## Cover Page
AER Rule | Field Name | Value(s)
1 | Constrained connection point ID | Loganlea
2 | Constraint primary driver | Asset condition
3 | Constraint investment type | Asset renewal
4 | Constrained connection point latitude (decimal degrees) | -27.664
| Constrained connection point longitude (decimal degrees) | 153.131
5 | Affect on residential customers
| Annual Energy | Not available
| Maximum Demand | Not available
6,7 | Effect on industrial and commercial customers
| Annual Energy | Not available
| Maximum Demand | Not available
8 | Load profile (maximum day, MVA)
50% PoE
Load profile (minimum day, MVA)
Minimum demand data (MVA)
| Max. demand, maximum demand day (MVA) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| 10% PoE | 605.381 | 612.549 | 579.408 | 555.774 | 619.217 | 562.778 | 612.769 | 580.005 | 564.836 | 581.866 | 611.467
| 50% PoE | 571.902 | 610.726 | 607.768 | 606.76 | 605.988 | 616.996 | 616.782 | 603.267 | 596.381 | 593.839 | 592.598
9 | Max. demand, minimum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Maximum demand data | 257.389 | 247.262 | 249.378 | 261.814 | 261.981 | 262.319 | 262.849 | 263.825 | 269.491 | 267.12 | 269.659
10 | Load profile (maximum day, MW)
Load profile 50%
| Max. demand, maximum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| 10% PoE | 486.972 | 504.657 | 496.184 | 540.661 | 525.684 | 515.94 | 519.364 | 511.652 | 517.458 | 524.062 | 605.725
| 50% PoE | 438.594 | 460.143 | 439.961 | 484.978 | 489.689 | 491.753 | 494.104 | 471.642 | 499.824 | 496.81 | 492.662
11 | Load profile (minimum day, MW)
Minimum demand data (MW)
| Min. demand, minimum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Mininum demand data | 95.4 | 59.376 | 51.051 | 47.603 | 47.189 | 41.97 | 39.673 | 37.458 | 35.42 | 31.283 | 28.23
12 | Voltage Level (kV) | 275
13 | Maximum load at risk per year | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Load at risk (MW, peak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Load at risk (MVA, peak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Load duration curve
15 | Preferred investment | Loganlea 275kV primary plant replacement
16 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Capital cost ($m, nominal) | [7 empty] | 5
17 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Operating cost ($m, nominal) | [7 empty] | 0.1 | 0.1 | 0.1 | 0.1
18 | Preferred investment cost accuracy | 0.3
19 | Preferred investment proposed timing | 2028-06-30
20 | Demand reduction to defer the investment by 1 year
21 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Annual deferral value ($m, nominal)
22 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Load transfer capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Historic load trace
24 | Historic ratings
25 | Limitation asset | Primary plant
26 | Unplanned outages
27 | Maximum fault level (kA) | 15.5
28 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Economic cost ($m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | VCR ($m/MWh) | 0.04003
30 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Annual unserved energy (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 8. Load profile max (50% PoE)
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:30 | 229.137 | 240.597 | 252.47 | 252.543 | 238.569 | 247.589 | 246.986 | 255.295 | 240.02 | 245.724 | 251.139
1:00 | 222.003 | 232.062 | 242.145 | 242.221 | 230.109 | 241.895 | 220.997 | 247.887 | 245.219 | 240.715 | 240.79
1:30 | 239.094 | 224.624 | 237.373 | 248.085 | 223.035 | 233.1 | 212.409 | 241.507 | 234.829 | 237.781 | 237.906
2:00 | 209.919 | 218.437 | 230.889 | 229.789 | 218.028 | 227.666 | 223.617 | 238.482 | 227.662 | 229.937 | 230.003
2:30 | 221.558 | 216.117 | 226.386 | 226.377 | 216.894 | 238.843 | 220.5 | 233.601 | 224.577 | 226.032 | 225.001
3:00 | 234.609 | 229.177 | 225.829 | 225.836 | 215.44 | 235.988 | 220.162 | 230.705 | 222.676 | 225.414 | 225.469
3:30 | 218.709 | 235.501 | 225.538 | 225.568 | 214.938 | 217.982 | 220.478 | 230.031 | 223.806 | 224.642 | 225.145
4:00 | 231.813 | 224.389 | 223.896 | 223.838 | 221.661 | 238.59 | 220.211 | 228.83 | 225.973 | 224.982 | 225.041
4:30 | 231.91 | 232.472 | 226.585 | 226.565 | 221.134 | 229.36 | 226.779 | 241.769 | 233.542 | 226.555 | 226.518
5:00 | 233.236 | 224.761 | 231.383 | 231.461 | 229.574 | 216.174 | 235.019 | 238.632 | 232.16 | 230.967 | 231.107
5:30 | 223.872 | 226.613 | 239.356 | 238.893 | 231.914 | 218.148 | 224.796 | 250.657 | 239.117 | 238.985 | 239.131
6:00 | 240.632 | 225.992 | 246.806 | 246.826 | 233.002 | 218.644 | 244.338 | 248.779 | 254.302 | 248.269 | 239.493
6:30 | 220.964 | 217.19 | 258.387 | 259.665 | 258.35 | 225.102 | 261.082 | 265.617 | 273.086 | 259.764 | 259.935
7:00 | 223.619 | 229.46 | 272.33 | 272.13 | 279.811 | 236.239 | 264.004 | 274.517 | 344.768 | 271.542 | 272.012
7:30 | 225.928 | 222.004 | 285.29 | 284.783 | 275.102 | 240.32 | 307.631 | 300.065 | 596.381 | 283.722 | 283.754
8:00 | 224.127 | 224.925 | 283.661 | 280.964 | 262.62 | 233.22 | 296.14 | 296.648 | 319.961 | 279.821 | 277.609
8:30 | 223.427 | 242.719 | 267.807 | 267.514 | 231.744 | 232.796 | 273.682 | 288.258 | 286.45 | 259.183 | 258.533
9:00 | 224.462 | 235.929 | 290.209 | 288.83 | 213.641 | 232.609 | 255.88 | 290.008 | 242.397 | 272.069 | 271.376
9:30 | 226.434 | 247.994 | 290.601 | 288.958 | 202.296 | 255.335 | 235.347 | 292.9 | 211.374 | 281.122 | 280.328
10:00 | 225.767 | 223.199 | 295.854 | 294.168 | 193.521 | 220.521 | 207.436 | 291.463 | 187.062 | 282.93 | 281.714
10:30 | 232.891 | 216.12 | 297.757 | 295.927 | 203.141 | 230.387 | 210.5133 | 317.124 | 213.554 | 287.394 | 286.961
11:00 | 244.274 | 226.231 | 295.566 | 288.63 | 219.651 | 237.532 | 213.5907 | 303.449 | 197.434 | 276.928 | 275.341
11:30 | 242.62 | 235.301 | 296.318 | 294.53 | 231.045 | 241.586 | 216.668 | 603.267 | 197.732 | 283.974 | 283.353
12:00 | 243.391 | 239.787 | 305.157 | 302.796 | 229.057 | 232.154 | 218.889 | 306.926 | 194.501 | 292.378 | 291.282
12:30 | 242.875 | 239.86 | 299.617 | 303.4355 | 249.623 | 234.988 | 214.194 | 304.283 | 194.101 | 285.998 | 286.476
13:00 | 225.799 | 251.027 | 305.358 | 304.075 | 245.708 | 242.553 | 212.373 | 321.425 | 204.2 | 295.122 | 294.176
13:30 | 237.825 | 250.014 | 317.629 | 316.569 | 246.926 | 244.515 | 221.534 | 307.895 | 210.741 | 304.417 | 303.09
14:00 | 240.768 | 255.989 | 313.726 | 312.012 | 259.872 | 259.291 | 222.919 | 314.719 | 204.392 | 302.93 | 447.844
14:30 | 244.727 | 269.683 | 301.064 | 298.205 | 255.281 | 271.523 | 209.767 | 338.236 | 220.496 | 593.839 | 592.598
15:00 | 268.605 | 300.06 | 607.768 | 606.76 | 250.161 | 303.027 | 209.781 | 361.753 | 231.655 | 280.338 | 277.266
15:30 | 283.348 | 320.577 | 304.571 | 304.271 | 245.041 | 324.229 | 210.861 | 360.035 | 250.717 | 294.482 | 292.833
16:00 | 305.787 | 610.726 | 330.887 | 329.591 | 271.7 | 616.996 | 238.363 | 431.88 | 263.837 | 312.267 | 318.48
16:30 | 321.238 | 323.641 | 336.753 | 346.837 | 286.9735 | 338.43 | 263.366 | 451.135 | 310.18 | 327.4205 | 326.807
17:00 | 446.57 | 342.672 | 336.367 | 336.559 | 302.247 | 359.745 | 283.85 | 439.69 | 322.376 | 342.574 | 347.994
17:30 | 571.902 | 348.308 | 363.035 | 355.071 | 320.366 | 359.884 | 316.34 | 451.76 | 398.537 | 353.528 | 359.975
18:00 | 360.014 | 341.077 | 359.344 | 358.658 | 325.657 | 366.672 | 616.782 | 444.833 | 395.157 | 364.482 | 358.853
18:30 | 365.697 | 346.158 | 355.653 | 355.902 | 324.561 | 366.696 | 304.294 | 437.906 | 397.671 | 359.206 | 359.179
19:00 | 369.742 | 342.103 | 352.265 | 353.128 | 321.68 | 382.571 | 300.214 | 442.32 | 400.081 | 363.938 | 364.169
19:30 | 382.076 | 338.999 | 360.572 | 361.143 | 605.988 | 375.229 | 294.299 | 440.75 | 397.72 | 370.623 | 370.798
20:00 | 335.088 | 339.065 | 359.487 | 359.596 | 315.957 | 353.843 | 317.828 | 436.1965 | 405.844 | 367.857 | 368.182
20:30 | 325.118 | 341.146 | 355.685 | 355.978 | 295.6 | 373.927 | 321.97 | 431.643 | 406.111 | 369.023 | 364.535
21:00 | 311.349 | 369.07 | 380.39 | 380.593 | 283.9255 | 395.7255 | 299.9655 | 388.871 | 375.242 | 388.736 | 388.519
21:30 | 283.668 | 355.667 | 341.983 | 342.143 | 272.251 | 417.524 | 277.961 | 379.183 | 328.907 | 346.506 | 348.701
22:00 | 271.283 | 333.321 | 321.688 | 320.993 | 258.364 | 332.162 | 265.068 | 356.695 | 329.589 | 325.856 | 325.974
22:30 | 264.79 | 310.975 | 294.529 | 294.567 | 272.853 | 327.033 | 260.032 | 342.553 | 313.302 | 297.694 | 297.813
23:00 | 259.227 | 304.62 | 275.795 | 275.836 | 268.851 | 322.204 | 239.542 | 324.725 | 298.464 | 278.532 | 278.622
23:30 | 248.768 | 268.439 | 272.172 | 272.228 | 266.382 | 269.915 | 268.966 | 285.609 | 255.806 | 275.331 | 275.418
0:00 | 238.689 | 244.227 | 266.448 | 255.537 | 229.195 | 258.859 | 236.983 | 264.112 | 243.27 | 260.808 | 260.995

## 8. Load profile min
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:30 | 218.036 | 217.812 | 222.182 | 226.247 | 226.026 | 248.59 | 214.721 |  | 241.959 | 235.88 | 236.861
1:00 | 224.07 | 210.954 | 215.311 | 217.011 | 231.375 | 233 | 220.24 | 221.556 | 231.41 | 223.714 | 224.341
1:30 | 217.315 | 205.862 | 210.604 | 210.559 | 222.621 | 216.251 | 211.999 | 212.268 | 222.95 | 222.227 | 222.729
2:00 | 210.721 | 201.507 | 206.251 | 211.159 | 215.69 | 209.355 | 206.405 | 206.142 | 217.268 | 215.352 | 215.601
2:30 | 208.215 | 200.737 | 205.614 | 212.743 | 211.224 | 206.898 | 201.513 | 201.756 | 212.286 | 210.827 | 211.015
3:00 | 205.831 | 198.456 | 200.983 | 210.454 | 208.593 | 209.673 | 200.358 | 200.057 | 208.211 | 208.059 | 210.064
3:30 | 205.035 | 197.358 | 199.961 | 209.483 | 207.59 | 204.533 | 199.185 | 204.271 | 208.101 | 208.097 | 208.364
4:00 | 202.207 | 199.219 | 199.282 | 208.754 | 207.136 | 208.263 | 203.013 | 198.901 | 206.456 | 205.771 | 206.14
4:30 | 202.97 | 203.509 | 201.284 | 209.456 | 208.763 | 209.453 | 199.769 | 201.14 | 208.618 | 208 | 207.992
5:00 | 203.678 | 203.874 | 201.125 | 210.796 | 211.772 | 206.008 | 201.542 | 201.582 | 211.971 | 211.427 | 211.858
5:30 | 207.023 | 199.489 | 204.316 | 214.543 | 217.493 | 209.017 | 205.837 | 206.012 | 217.402 | 217.424 | 217.796
6:00 | 208.687 | 198.45 | 203.323 | 213.065 | 222.603 | 212.439 | 209.183 | 209.28 | 216.476 | 222.64 | 223.398
6:30 | 211.81 | 197.302 | 202.203 | 213.477 | 228.482 | 232.235 | 212.865 | 213.731 | 228.723 | 228.585 | 229.645
7:00 | 210.425 | 189.951 | 194.488 | 204.368 | 232.711 | 209.122 | 209.753 | 210.417 | 232.553 | 232.168 | 232.709
7:30 | 208.78 | 184.944 | 187.503 | 196.972 | 228.922 | 207.46 | 207.746 | 207.7 | 227.629 | 227.491 | 227.392
8:00 | 199.809 | 176.942 | 179.903 | 186.16 | 220.687 | 200.583 | 196.168 | 195.39 | 216.715 | 217.299 | 215.352
8:30 | 191.564 | 169.494 | 167.935 | 174.339 | 207.029 | 186.056 | 180.2005 | 173.0637 | 201.523 | 203.017 | 201.779
9:00 | 182.355 | 165.995 | 168.513 | 159.699 | 194.993 | 171.549 | 164.233 | 150.7373 | 188.33 | 186.04 | 182.918
9:30 | 172.932 | 162.496 | 160.77 | 145.059 | 180.581 | 144.804 | 130.492 | 128.411 | 168.545 | 166.709 | 152.358
10:00 | 167.027 | 128.342 | 130.774 | 130.419 | 146.253 | 135.276 | 131.866 | 124.65 | 132.171 | 133.593 | 134.07
10:30 | 141.394 | 128.458 | 102.565 | 99.803 | 139.763 | 126.975 | 94.072 | 91.234 | 127.554 | 131.562 | 127.149
11:00 | 137.522 | 78.308 | 84.562 | 84.664 | 127.422 | 119.23 | 56.278 | 53.96 | 112.7128 | 119.242 | 95.081
11:30 | 133.65 | 70.8105 | 66.559 | 83.792 | 127.1 | 66.941 | 125.946 | 118.928 | 97.8716 | 82.511 | 63.013
12:00 | 131.572 | 63.313 | 65.936 | 82.954 | 96.49 | 64.61 | 120.549 | 116.2615 | 83.0304 | 52.798 | 49.789
12:30 | 134.926 | 81.048 | 86.92 | 69.261 | 70.879 | 64.77 | 115.716 | 113.595 | 68.1892 | 59.297 | 56.758
13:00 | 138.365 | 98.783 | 107.904 | 91.7807 | 76.139 | 66.72 | 124.7 | 122.47 | 53.348 | 56.602 | 57.578
13:30 | 164.022 | 127.768 | 128.888 | 114.3003 | 100.4082 | 82.207 | 132.012 | 99.681 | 68.375 | 58.445 | 55.759
14:00 | 173.226 | 165.716 | 149.627 | 136.82 | 124.6775 | 112.629 | 93.939 | 76.892 | 122.442 | 122.834 | 121.951
14:30 | 181.588 | 169.232 | 170.366 | 168.316 | 148.9468 | 143.051 | 129.096 | 132.059 | 132.354 | 133.183 | 135.931
15:00 | 196.68 | 179.22 | 179.126 | 185.663 | 173.216 | 169.349 | 166.407 | 160.087 | 159.7595 | 166.425 | 165.044
15:30 | 214.77 | 194.697 | 196.853 | 199.266 | 192.209 | 195.647 | 189.329 | 188.115 | 187.165 | 184.436 | 184.677
16:00 | 235.517 | 215.366 | 217.236 | 221.224 | 209.71 | 215.296 | 206.734 | 211.5215 | 205.329 | 204.63 | 204.31
16:30 | 248.494 | 235.93 | 237.696 | 239.895 | 232.276 | 239.229 | 235.562 | 234.928 | 228.942 | 217.882 | 233.019
17:00 | 255.544 | 239.921 | 246.423 | 251.223 | 247.445 | 240.168 | 246.042 | 245.794 | 248.191 | 246.127 | 247.291
17:30 | 248.313 | 244.596 | 249.121 | 256.405 | 245.718 | 261.758 | 256.522 | 256.66 | 249.907 | 250.144 | 252.5
18:00 | 270.051 | 255.106 | 258.614 | 267.021 | 262.644 | 267.404 | 263.925 | 264.05 | 265.127 | 268.484 | 271.11
18:30 | 262.586 | 270.612 | 271.316 | 275.648 | 277.347 | 282.101 | 273.602 | 274.813 | 279.335 | 279.597 | 284.158
19:00 | 267.222 | 267.268 | 275.169 | 275.283 | 283.114 | 279.373 | 263.724 | 264.454 | 285.846 | 289.392 | 292.783
19:30 | 247.846 | 262.389 | 265.001 | 280.192 | 274.567 | 269.137 | 257.939 | 258.784 | 272.784 | 276.506 | 279.294
20:00 | 266.65 | 265.631 | 270.557 | 281.901 | 274.528 | 278.194 | 263.615 | 263.872 | 271.315 | 272.435 | 274.887
20:30 | 263.714 | 266.162 | 269.838 | 280.152 | 270.338 | 278.504 | 269.206 | 269.467 | 275.336 | 272.182 | 276.428
21:00 | 249.655 | 258.166 | 263.578 | 253.864 | 259.417 | 269.732 | 259.374 | 261.214 | 260.992 | 263.135 | 265.246
21:30 | 235.469 | 252.078 | 255.384 | 248.397 | 252.727 | 257.313 | 250.632 | 250.846 | 253.439 | 255.631 | 256.814
22:00 | 256.362 | 246.02 | 249.16 | 250.474 | 228.97 | 246.977 | 248.967 | 241.564 | 229.179 | 231.949 | 233.651
22:30 | 264.721 | 242.431 | 254.533 | 252.595 | 255.033 | 242.899 | 244.909 | 244.804 | 255.586 | 258.109 | 259.682
23:00 | 252.966 | 248.607 | 244.22 | 257.574 | 251.216 | 240.342 | 240.452 | 240.174 | 251.582 | 254.916 | 254.899
23:30 | 244.802 | 261.415 | 243.452 | 247.588 | 247.146 | 242.409 | 228.135 | 228.369 | 263.534 | 265.974 | 269.019
0:00 | 218.203 | 250.132 | 254.355 | 239.228 | 241.327 | 243.768 | 229.643 | 229.734 | 241.436 | 240.736 | 242.132

## 10. Load profile (50% PoE)
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:30 | 228.651 | 224.827 | 224.649 | 235.384 | 235.461 | 235.154 | 238.344 | 238.36 | 238.605 | 271.06 | 243.677
1:00 | 216.453 | 212.999 | 216.961 | 226.039 | 227.403 | 225.923 | 225.964 | 226.473 | 226.203 | 258.627 | 230.625
1:30 | 209.85 | 208.692 | 210.498 | 219.935 | 220.028 | 219.725 | 219.764 | 219.847 | 219.964 | 251.83 | 222.647
2:00 | 203.778 | 202.564 | 210.381 | 214.785 | 214.842 | 214.573 | 214.61 | 214.676 | 214.79 | 247.932 | 218.385
2:30 | 200.382 | 200.681 | 203.946 | 212.996 | 213.034 | 212.349 | 212.328 | 212.332 | 212.424 | 242.557 | 213.526
3:00 | 197.354 | 198.88 | 200.493 | 211.067 | 211.104 | 210.832 | 210.82 | 212.018 | 212.111 | 237.182 | 209.314
3:30 | 196.462 | 197.731 | 200.55 | 209.821 | 209.82 | 208.93 | 209.526 | 209.539 | 209.606 | 233.963 | 208.73
4:00 | 195.516 | 197.39 | 199.234 | 208.97 | 209.054 | 208.717 | 209.35 | 209.378 | 209.377 | 230.133 | 207.285
4:30 | 198.973 | 199.876 | 201.568 | 212.016 | 212.048 | 211.76 | 211.782 | 211.816 | 211.897 | 233.497 | 211.091
5:00 | 206.539 | 206.814 | 207.632 | 219.095 | 218.931 | 218.566 | 218.761 | 218.852 | 218.942 | 239.041 | 219.72
5:30 | 222.276 | 218.671 | 224.331 | 230.524 | 231.946 | 231.669 | 231.726 | 230.598 | 232 | 250.207 | 236.729
6:00 | 235.422 | 230.588 | 239.605 | 244.634 | 244.625 | 244.213 | 244.227 | 244.326 | 244.379 | 259.393 | 250.579
6:30 | 258.996 | 250.259 | 266.244 | 264.642 | 265.198 | 264.992 | 264.948 | 265.068 | 265.4 | 282.352 | 275.785
7:00 | 276.048 | 258.702 | 276.533 | 274.235 | 274.087 | 273.582 | 273.012 | 273.094 | 273.228 | 289.339 | 295.046
7:30 | 289.551 | 270.009 | 296.736 | 286.436 | 285.89 | 284.801 | 284.411 | 284.004 | 283.558 | 307.313 | 310.366
8:00 | 286.775 | 270.547 | 289.986 | 286.147 | 285.241 | 283.907 | 283.175 | 282.446 | 281.773 | 309.055 | 302.334
8:30 | 275.48 | 262.855 | 286.158 | 276.059 | 273.878 | 274.128 | 270.719 | 269.906 | 267.838 | 302.481 | 282.969
9:00 | 270.353 | 265.812 | 289.893 | 274.727 | 273.433 | 274.307 | 271.379 | 270.447 | 268.019 | 297.519 | 273.001
9:30 | 265.226 | 265.404 | 292.4113 | 278.371 | 276.803 | 274.486 | 267.676 | 269.542 | 267.608 | 301.908 | 262.899
10:00 | 262.756 | 267.097 | 294.9297 | 282.7135 | 277.652 | 273.802 | 272.639 | 269.391 | 265.283 | 308.585 | 252.057
10:30 | 269.181 | 272.159 | 297.448 | 287.056 | 285.743 | 278.275 | 277.703 | 278.669 | 275.905 | 315.262 | 259.183
11:00 | 279.287 | 276.7 | 307.192 | 291.3985 | 289.991 | 282.38 | 284.359 | 281.983 | 279.375 | 315.556 | 269.864
11:30 | 289.094 | 283.051 | 316.936 | 295.741 | 295.796 | 290.4635 | 290.812 | 291.826 | 289.284 | 323.054 | 282.823
12:00 | 298.397 | 286.14 | 331.19 | 307.0435 | 310.36 | 298.547 | 297.265 | 294.771 | 300.978 | 334.982 | 295.782
12:30 | 323.981 | 302.3785 | 340.019 | 318.346 | 316.653 | 315.5335 | 313.8775 | 309.742 | 310.442 | 345.377 | 321.1105
13:00 | 343.832 | 318.617 | 352.802 | 336.7613 | 334.891 | 332.52 | 330.49 | 323.094 | 319.906 | 362.9095 | 346.439
13:30 | 356.979 | 334.7885 | 369.732 | 355.1765 | 350.824 | 349.012 | 347.341 | 342.7815 | 340.1003 | 380.442 | 361.181
14:00 | 364.721 | 350.96 | 404.8465 | 373.5918 | 365.489 | 368.9523 | 363.648 | 362.469 | 360.2945 | 390.1393 | 375.923
14:30 | 376.1212 | 367.1315 | 439.961 | 392.007 | 381.998 | 388.8927 | 379.955 | 382.1565 | 380.4887 | 399.8367 | 393.5878
15:00 | 387.5214 | 383.303 | 426.922 | 410.4223 | 403.5362 | 408.833 | 396.262 | 401.844 | 400.683 | 409.534 | 411.2526
15:30 | 398.9216 | 399.3375 | 426.0872 | 428.8375 | 425.0744 | 428.7733 | 412.569 | 425.11 | 430.32 | 419.2313 | 428.9174
16:00 | 410.3218 | 415.372 | 425.2523 | 447.2527 | 446.6126 | 448.7137 | 428.876 | 448.376 | 444.2208 | 428.9287 | 446.5822
16:30 | 421.722 | 437.67 | 424.4175 | 465.668 | 468.1508 | 468.654 | 445.183 | 471.642 | 458.1216 | 438.626 | 464.247
17:00 | 430.158 | 448.9065 | 423.5827 | 472.1047 | 489.689 | 491.753 | 461.49 | 466.5316 | 472.0224 | 448.3233 | 471.3508
17:30 | 438.594 | 460.143 | 422.7478 | 478.5413 | 484.5132 | 482.8997 | 477.797 | 461.4211 | 485.9232 | 458.0207 | 478.4545
18:00 | 434.001 | 451.631 | 421.913 | 484.978 | 479.3373 | 474.0465 | 494.104 | 456.3107 | 499.824 | 467.718 | 485.5582
18:30 | 429.408 | 443.119 | 415.3 | 477.9265 | 474.1615 | 465.1932 | 480.7531 | 451.2002 | 495.148 | 477.4153 | 492.662
19:00 | 424.815 | 434.607 | 417.32 | 470.875 | 468.9857 | 456.34 | 467.4023 | 446.0898 | 490.472 | 487.1127
19:30 | 420.222 | 426.095 | 404.174 | 463.473 | 463.8098 | 447.4867 | 454.0514 | 440.9793 | 485.796 | 496.81 | 476.235
20:00 | 401.03 | 417.583 | 391.028 | 456.071 | 458.634 | 438.6335 | 440.7006 | 435.8689 | 472.551 | 481.0477 | 460.993
20:30 | 393.3 | 409.071 | 378.855 | 439.095 | 441.486 | 429.7803 | 427.3497 | 430.7584 | 450.231 | 465.2853 | 445.751
21:00 | 385.57 | 386.511 | 353.65 | 415.768 | 418.248 | 420.927 | 413.9989 | 425.648 | 427.911 | 449.523 | 426.421
21:30 | 356.08 | 366.5895 | 335.427 | 392.2723 | 394.675 | 398.638 | 400.648 | 402.456 | 404.452 | 419.6185 | 393.9865
22:00 | 330.812 | 346.668 | 319.843 | 368.7767 | 367.148 | 368.935 | 375.833 | 374.01 | 377.583 | 389.714 | 361.552
22:30 | 302.737 | 325.896 | 306.42 | 345.281 | 348.668 | 347.166 | 351.018 | 351.925 | 353.902 | 348.249 | 326.541
23:00 | 289.894 | 310.013 | 292.068 | 329.552 | 329.738 | 330.154 | 331.949 | 333.233 | 334.556 | 333.957 | 312.504
23:30 | 271.359 | 290.571 | 270.798 | 307.099 | 306.995 | 306.817 | 309.049 | 310.29 | 311.588 | 313.894 | 291.618
0:00 | 239.968 | 240.15 | 239.526 | 254.762 | 254.834 | 254.546 | 254.619 | 254.739 | 255.315 | 285.849 | 254.281

## 11. Load profile min
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:30 | 182.216 | 168.635 | 173.896 | 180.477 | 180.115 |  | 182.174 |  | 174.256 | 180.82 | 180.96
1:00 | 170.459 | 159.182 | 163.081 | 170.936 | 169.995 | 170.816 | 170.903 | 171.317 | 165.886 | 171.114 | 171.586
1:30 | 163.987 | 151.907 | 156.013 | 163.492 | 162.205 | 163.395 | 163.309 | 163.475 | 160.35 | 163.574 | 163.639
2:00 | 158.158 | 146.886 | 151.339 | 157.731 | 157.053 | 158.487 | 158.534 | 158.381 | 155.384 | 158.482 | 158.82
2:30 | 154.861 | 142.588 | 147.02 | 153.89 | 152.425 | 153.713 | 153.792 | 153.844 | 152.61 | 153.953 | 154.12
3:00 | 152.36 | 141.225 | 145.496 | 152.468 | 152.21 | 151.956 | 152.025 | 152.343 | 151.004 | 152.221 | 152.667
3:30 | 150.5 | 140.5 | 144.995 | 151.79 | 151.644 | 151.637 | 151.706 | 152.062 | 149.398 | 151.901 | 152.095
4:00 | 149.648 | 139.118 | 143.517 | 150.71 | 150.469 | 150.572 | 150.627 | 150.364 | 148.68 | 150.774 | 150.619
4:30 | 149.644 | 140.148 | 144.615 | 151.737 | 150.904 | 151.65 | 151.555 | 151.353 | 149.642 | 151.538 | 151.818
5:00 | 150.053 | 142.833 | 146.287 | 153.262 | 152.798 | 153.338 | 153.528 | 153.575 | 150.604 | 153.823 | 154.151
5:30 | 152.247 | 146.052 | 150.403 | 157.556 | 157.402 | 157.33 | 157.426 | 157.525 | 153.31 | 157.718 | 157.967
6:00 | 153.899 | 148.745 | 153.016 | 160.294 | 160.097 | 160.05 | 160.19 | 160.288 | 152.064 | 160.503 | 160.812
6:30 | 157.04 | 151.54 | 155.589 | 162.969 | 162.903 | 163.096 | 163.228 | 163.229 | 146.9765 | 163.136 | 163.88
7:00 | 155.638 | 149.14 | 152.681 | 159.717 | 159.01 | 159.315 | 159.247 | 159.401 | 141.889 | 159.878 | 159.342
7:30 | 155.809 | 144.743 | 147.483 | 153.925 | 152.725 | 153.124 | 152.66 | 152.371 | 131.904 | 151.181 | 151.021
8:00 | 146.669 | 135.95 | 138.25 | 143.908 | 140.2905 | 142.172 | 141.395 | 140.663 | 121.059 | 139.109 | 138.023
8:30 | 137.265 | 128.329 | 126.037 | 130.334 | 127.856 | 128.302 | 125.9535 | 124.3283 | 110.552 | 121.6465 | 120.504
9:00 | 127.476 | 115.8425 | 114.414 | 118.5047 | 113.8 | 116.948 | 110.512 | 107.9937 | 95.296 | 104.184 | 98.686
9:30 | 118.453 | 103.356 | 104.7207 | 106.6753 | 100.3525 | 96.517 | 93.807 | 91.659 | 80.04 | 91.499 | 88.076
10:00 | 114.488 | 94.752 | 95.0273 | 94.846 | 86.905 | 89.486 | 86.771 | 84.104 | 68.885 | 74.258 | 72.18
10:30 | 106.258 | 86.148 | 85.334 | 86.055 | 77.93 | 76.061 | 71.52 | 68.373 | 57.73 | 59.4715 | 56.284
11:00 | 101.3955 | 78.677 | 71.197 | 70.8 | 65.652 | 61.825 | 56.269 | 53.947 | 46.575 | 44.685 | 40.801
11:30 | 96.533 | 69.0265 | 64.4817 | 52.948 | 56.438 | 44.064 | 41.061 | 39.022 | 35.42 | 32.988 | 36.6107
12:00 | 95.4 | 59.376 | 57.7663 | 47.603 | 47.224 | 41.997 | 39.673 | 38.24 | 44.64 | 31.283 | 32.4203
12:30 | 100.032 | 59.754 | 51.051 | 48.077 | 47.189 | 41.97 | 39.958 | 37.458 | 53.86 | 31.378 | 28.23
13:00 | 103.084 | 61.44 | 56.293 | 55.4585 | 49.924 | 44.122 | 42.01 | 39.514 | 63.08 | 34.257 | 31.348
13:30 | 112.2 | 73.4555 | 65.411 | 62.84 | 59.633 | 54.459 | 48.697 | 55.235 | 72.3 | 48.696 | 38.44
14:00 | 117.98 | 85.471 | 84.759 | 80.8975 | 82.919 | 77.748 | 75.587 | 70.956 | 81.52 | 63.135 | 60.456
14:30 | 129.203 | 102.2205 | 99.347 | 98.955 | 99.962 | 99.069 | 92.525 | 90.627 | 101.1877 | 86.017 | 83.797
15:00 | 144.6 | 118.97 | 119.849 | 122.859 | 117.005 | 120.39 | 113.461 | 114.71 | 120.8553 | 108.14 | 109.2775
15:30 | 162.932 | 138.0665 | 135.423 | 143.358 | 139.097 | 141.711 | 139.88 | 138.793 | 140.523 | 136.208 | 134.758
16:00 | 183.152 | 157.163 | 158.267 | 163.857 | 162.298 | 165.252 | 160.189 | 163.265 | 164.4515 | 157.156 | 160.71
16:30 | 203.008 | 181.337 | 182.979 | 191.539 | 186.243 | 188.793 | 188.256 | 187.737 | 188.38 | 186.096 | 186.662
17:00 | 223.86 | 207.408 | 203.9805 | 216.458 | 220.293 | 215.645 | 212.3695 | 212.283 | 217.506 | 215.036 | 215.821
17:30 | 238.501 | 224.311 | 224.982 | 233.6315 | 236.6955 | 236.215 | 236.483 | 236.829 | 242.517 | 238.515 | 240.41
18:00 | 243.516 | 238.211 | 240.739 | 250.805 | 253.098 | 251.378 | 254.879 | 255.105 | 249.302 | 258.167 | 260.674
18:30 | 252.72 | 246.812 | 249.378 | 261.814 | 261.981 | 262.319 | 262.849 | 263.825 | 265.943 | 267.12 | 269.659
19:00 | 257.389 | 247.262 | 247.167 | 259.56 | 259.53 | 259.916 | 260.346 | 260.999 | 269.491 | 264.432 | 266.493
19:30 | 244.967 | 237.208 | 236.605 | 248.691 | 248.885 | 248.885 | 249.2 | 249.676 | 258.299 | 252.148 | 256.983
20:00 | 242.268 | 235.709 | 238.116 | 250.3 | 250.375 | 250.499 | 250.809 | 251.038 | 254.24 | 253.058 | 254.912
20:30 | 237.39 | 236.473 | 239.482 | 251.414 | 250.864 | 251.423 | 251.863 | 252.074 | 242.527 | 253.963 | 258.977
21:00 | 229.671 | 228.46 | 231.029 | 242.358 | 242.03 | 242.514 | 242.456 | 243.183 | 236.433 | 244.687 | 246.379
21:30 | 217.825 | 225.285 | 228.091 | 239.21 | 238.291 | 239.37 | 239.655 | 239.846 | 229.348 | 241.233 | 242.872
22:00 | 209.02 | 214.699 | 217.359 | 228.248 | 229.605 | 231.275 | 228.45 | 231.628 | 222.515 | 232.422 | 233.82
22:30 | 206.377 | 211.606 | 213.637 | 224.715 | 222.092 | 224.568 | 224.883 | 224.95 | 216.995 | 225.241 | 226.582
23:00 | 204.698 | 208.588 | 211.252 | 221.583 | 218.197 | 220.835 | 220.988 | 221.929 | 214.821 | 220.959 | 223.422
23:30 | 191.163 | 195.219 | 198.228 | 209.153 | 205.112 | 207.584 | 207.691 | 207.887 | 199.915 | 208.159 | 208.931
0:00 | 194.199 | 183.494 | 186.436 | 193.5 | 194.853 | 195.521 | 195.613 | 195.697 | 189.387 | 195.868 | 194.508

## 23. Historic load trace
Date/Time | Load (MVA) | Load (MW)
2017-03-01 00:30 | 191 | 191
2017-03-01 01:00 | 184 | 183
2017-03-01 01:30 | 177 | 175
2017-03-01 02:00 | 173 | 171
2017-03-01 02:30 | 169 | 167
2017-03-01 03:00 | 167 | 166
2017-03-01 03:30 | 167 | 166
2017-03-01 04:00 | 168 | 167
2017-03-01 04:30 | 172 | 170
2017-03-01 05:00 | 178 | 176
2017-03-01 05:30 | 191 | 190
2017-03-01 06:00 | 201 | 200
2017-03-01 06:30 | 224 | 223
2017-03-01 07:00 | 239 | 238
2017-03-01 07:30 | 252 | 250
2017-03-01 08:00 | 255 | 254
2017-03-01 08:30 | 255 | 254
2017-03-01 09:00 | 257 | 255
2017-03-01 09:30 | 262 | 259
2017-03-01 10:00 | 270 | 269
2017-03-01 10:30 | 279 | 278
2017-03-01 11:00 | 279 | 278
2017-03-01 11:30 | 278 | 277
2017-03-01 12:00 | 283 | 283
2017-03-01 12:30 | 286 | 286
2017-03-01 13:00 | 291 | 290
2017-03-01 13:30 | 298 | 297
2017-03-01 14:00 | 303 | 303
2017-03-01 14:30 | 308 | 308
2017-03-01 15:00 | 311 | 311
2017-03-01 15:30 | 320 | 320
2017-03-01 16:00 | 325 | 325
2017-03-01 16:30 | 328 | 328
2017-03-01 17:00 | 333 | 333
2017-03-01 17:30 | 330 | 330
2017-03-01 18:00 | 326 | 326
2017-03-01 18:30 | 320 | 320
2017-03-01 19:00 | 329 | 328
2017-03-01 19:30 | 324 | 323
2017-03-01 20:00 | 320 | 319
2017-03-01 20:30 | 313 | 313
2017-03-01 21:00 | 298 | 298
2017-03-01 21:30 | 284 | 284
2017-03-01 22:00 | 269 | 269
2017-03-01 22:30 | 257 | 257
2017-03-01 23:00 | 253 | 253
2017-03-01 23:30 | 236 | 235
2017-03-02 | 215 | 215
2017-03-02 00:30 | 204 | 204
2017-03-02 01:00 | 196 | 195
2017-03-02 01:30 | 189 | 188
2017-03-02 02:00 | 183 | 183
2017-03-02 02:30 | 181 | 180
2017-03-02 03:00 | 180 | 179
2017-03-02 03:30 | 179 | 179
2017-03-02 04:00 | 179 | 178
2017-03-02 04:30 | 182 | 181
2017-03-02 05:00 | 188 | 188
2017-03-02 05:30 | 203 | 201
2017-03-02 06:00 | 213 | 211
2017-03-02 06:30 | 232 | 231
2017-03-02 07:00 | 248 | 247
2017-03-02 07:30 | 263 | 261
2017-03-02 08:00 | 267 | 266
2017-03-02 08:30 | 270 | 270
2017-03-02 09:00 | 276 | 276
2017-03-02 09:30 | 286 | 286
2017-03-02 10:00 | 289 | 289
2017-03-02 10:30 | 292 | 292
2017-03-02 11:00 | 294 | 294
2017-03-02 11:30 | 299 | 299
2017-03-02 12:00 | 308 | 308
2017-03-02 12:30 | 310 | 310
2017-03-02 13:00 | 311 | 311
2017-03-02 13:30 | 316 | 315
2017-03-02 14:00 | 317 | 317
2017-03-02 14:30 | 321 | 321
2017-03-02 15:00 | 322 | 322
2017-03-02 15:30 | 326 | 326
2017-03-02 16:00 | 332 | 332
2017-03-02 16:30 | 334 | 334
2017-03-02 17:00 | 336 | 336
2017-03-02 17:30 | 338 | 338
2017-03-02 18:00 | 338 | 337
2017-03-02 18:30 | 335 | 335
2017-03-02 19:00 | 345 | 344
2017-03-02 19:30 | 341 | 341
2017-03-02 20:00 | 337 | 336
2017-03-02 20:30 | 329 | 328
2017-03-02 21:00 | 313 | 312
2017-03-02 21:30 | 296 | 296
2017-03-02 22:00 | 280 | 280
2017-03-02 22:30 | 266 | 266
2017-03-02 23:00 | 262 | 261
2017-03-02 23:30 | 242 | 242
2017-03-03 | 222 | 222
2017-03-03 00:30 | 210 | 208
2017-03-03 01:00 | 202 | 201
2017-03-03 01:30 | 193 | 192
2017-03-03 02:00 | 188 | 187
2017-03-03 02:30 | 184 | 183
2017-03-03 03:00 | 182 | 181
2017-03-03 03:30 | 181 | 181
2017-03-03 04:00 | 181 | 180
2017-03-03 04:30 | 184 | 183
2017-03-03 05:00 | 190 | 189
2017-03-03 05:30 | 202 | 201
2017-03-03 06:00 | 211 | 210
2017-03-03 06:30 | 232 | 230
2017-03-03 07:00 | 249 | 247
2017-03-03 07:30 | 264 | 263
2017-03-03 08:00 | 267 | 267
2017-03-03 08:30 | 269 | 268
2017-03-03 09:00 | 276 | 274
2017-03-03 09:30 | 284 | 283
2017-03-03 10:00 | 288 | 287
2017-03-03 10:30 | 290 | 290
2017-03-03 11:00 | 294 | 293
2017-03-03 11:30 | 301 | 300
2017-03-03 12:00 | 317 | 316
2017-03-03 12:30 | 324 | 323
2017-03-03 13:00 | 328 | 328
2017-03-03 13:30 | 320 | 320
2017-03-03 14:00 | 315 | 315
2017-03-03 14:30 | 320 | 320
2017-03-03 15:00 | 319 | 319
2017-03-03 15:30 | 318 | 318
2017-03-03 16:00 | 328 | 328
2017-03-03 16:30 | 336 | 336
2017-03-03 17:00 | 342 | 342
2017-03-03 17:30 | 339 | 339
2017-03-03 18:00 | 330 | 330
2017-03-03 18:30 | 325 | 325
2017-03-03 19:00 | 332 | 332
2017-03-03 19:30 | 327 | 327
2017-03-03 20:00 | 323 | 323
2017-03-03 20:30 | 316 | 316
2017-03-03 21:00 | 301 | 301
2017-03-03 21:30 | 290 | 289
2017-03-03 22:00 | 278 | 278
2017-03-03 22:30 | 268 | 267
2017-03-03 23:00 | 262 | 262
2017-03-03 23:30 | 245 | 244
2017-03-04 | 226 | 226
2017-03-04 00:30 | 211 | 211
2017-03-04 01:00 | 202 | 202
2017-03-04 01:30 | 195 | 195
2017-03-04 02:00 | 188 | 188
2017-03-04 02:30 | 184 | 184
2017-03-04 03:00 | 181 | 181
2017-03-04 03:30 | 179 | 179
2017-03-04 04:00 | 178 | 178
2017-03-04 04:30 | 178 | 178
2017-03-04 05:00 | 179 | 179
2017-03-04 05:30 | 183 | 183
2017-03-04 06:00 | 184 | 184
2017-03-04 06:30 | 190 | 190
2017-03-04 07:00 | 199 | 199
2017-03-04 07:30 | 206 | 206
2017-03-04 08:00 | 212 | 212
2017-03-04 08:30 | 215 | 215
2017-03-04 09:00 | 224 | 223
2017-03-04 09:30 | 235 | 235
2017-03-04 10:00 | 245 | 245
2017-03-04 10:30 | 252 | 252
2017-03-04 11:00 | 251 | 251
2017-03-04 11:30 | 254 | 254
2017-03-04 12:00 | 252 | 252
2017-03-04 12:30 | 245 | 244
2017-03-04 13:00 | 247 | 246
2017-03-04 13:30 | 255 | 254
2017-03-04 14:00 | 260 | 260
2017-03-04 14:30 | 273 | 273
2017-03-04 15:00 | 281 | 281
2017-03-04 15:30 | 285 | 285
2017-03-04 16:00 | 288 | 288
2017-03-04 16:30 | 291 | 291
2017-03-04 17:00 | 293 | 293
2017-03-04 17:30 | 289 | 289
2017-03-04 18:00 | 288 | 287
2017-03-04 18:30 | 291 | 291
2017-03-04 19:00 | 297 | 297
2017-03-04 19:30 | 293 | 293
2017-03-04 20:00 | 290 | 290
2017-03-04 20:30 | 283 | 283
2017-03-04 21:00 | 269 | 269
2017-03-04 21:30 | 261 | 261
2017-03-04 22:00 | 252 | 251
2017-03-04 22:30 | 244 | 244
2017-03-04 23:00 | 244 | 243
2017-03-04 23:30 | 229 | 229
2017-03-05 | 211 | 211
2017-03-05 00:30 | 200 | 199
2017-03-05 01:00 | 192 | 192
2017-03-05 01:30 | 184 | 183
2017-03-05 02:00 | 177 | 177
2017-03-05 02:30 | 173 | 173
2017-03-05 03:00 | 171 | 171
2017-03-05 03:30 | 170 | 170
2017-03-05 04:00 | 169 | 169
2017-03-05 04:30 | 168 | 168
2017-03-05 05:00 | 169 | 169
2017-03-05 05:30 | 171 | 171
2017-03-05 06:00 | 172 | 172
2017-03-05 06:30 | 176 | 176
2017-03-05 07:00 | 179 | 179
2017-03-05 07:30 | 182 | 181
2017-03-05 08:00 | 188 | 188
2017-03-05 08:30 | 202 | 201
2017-03-05 09:00 | 211 | 211
2017-03-05 09:30 | 211 | 211
2017-03-05 10:00 | 207 | 207
2017-03-05 10:30 | 212 | 212
2017-03-05 11:00 | 221 | 221
2017-03-05 11:30 | 229 | 229
2017-03-05 12:00 | 234 | 233
2017-03-05 12:30 | 238 | 238
2017-03-05 13:00 | 245 | 245
2017-03-05 13:30 | 253 | 252
2017-03-05 14:00 | 264 | 263
2017-03-05 14:30 | 274 | 274
2017-03-05 15:00 | 284 | 284
2017-03-05 15:30 | 299 | 299
2017-03-05 16:00 | 308 | 308
2017-03-05 16:30 | 315 | 315
2017-03-05 17:00 | 321 | 321
2017-03-05 17:30 | 325 | 324
2017-03-05 18:00 | 324 | 324
2017-03-05 18:30 | 326 | 325
2017-03-05 19:00 | 338 | 337
2017-03-05 19:30 | 333 | 333
2017-03-05 20:00 | 324 | 324
2017-03-05 20:30 | 315 | 315
2017-03-05 21:00 | 298 | 298
2017-03-05 21:30 | 285 | 285
2017-03-05 22:00 | 271 | 271
2017-03-05 22:30 | 257 | 257
2017-03-05 23:00 | 255 | 254
2017-03-05 23:30 | 238 | 237
2017-03-06 | 218 | 218
2017-03-06 00:30 | 204 | 203
2017-03-06 01:00 | 196 | 195
2017-03-06 01:30 | 187 | 187
2017-03-06 02:00 | 182 | 182
2017-03-06 02:30 | 179 | 178
2017-03-06 03:00 | 176 | 176
2017-03-06 03:30 | 175 | 175
2017-03-06 04:00 | 175 | 175
2017-03-06 04:30 | 178 | 178
2017-03-06 05:00 | 185 | 185
2017-03-06 05:30 | 198 | 197
2017-03-06 06:00 | 208 | 207
2017-03-06 06:30 | 229 | 228
2017-03-06 07:00 | 247 | 247
2017-03-06 07:30 | 264 | 263
2017-03-06 08:00 | 268 | 268
2017-03-06 08:30 | 268 | 268
2017-03-06 09:00 | 270 | 270
2017-03-06 09:30 | 277 | 276
2017-03-06 10:00 | 284 | 283
2017-03-06 10:30 | 288 | 286
2017-03-06 11:00 | 292 | 291
2017-03-06 11:30 | 297 | 296
2017-03-06 12:00 | 304 | 302
2017-03-06 12:30 | 310 | 308
2017-03-06 13:00 | 317 | 315
2017-03-06 13:30 | 321 | 319
2017-03-06 14:00 | 320 | 318
2017-03-06 14:30 | 318 | 317
2017-03-06 15:00 | 317 | 316
2017-03-06 15:30 | 321 | 320
2017-03-06 16:00 | 331 | 329
2017-03-06 16:30 | 340 | 339
2017-03-06 17:00 | 347 | 346
2017-03-06 17:30 | 344 | 343
2017-03-06 18:00 | 338 | 336
2017-03-06 18:30 | 335 | 333
2017-03-06 19:00 | 339 | 336
2017-03-06 19:30 | 330 | 328
2017-03-06 20:00 | 327 | 325
2017-03-06 20:30 | 317 | 316
2017-03-06 21:00 | 299 | 298
2017-03-06 21:30 | 285 | 284
2017-03-06 22:00 | 270 | 270
2017-03-06 22:30 | 257 | 257
2017-03-06 23:00 | 252 | 252
2017-03-06 23:30 | 234 | 234
2017-03-07 | 216 | 216
2017-03-07 00:30 | 205 | 204
2017-03-07 01:00 | 197 | 197
2017-03-07 01:30 | 188 | 188
2017-03-07 02:00 | 184 | 183
2017-03-07 02:30 | 181 | 180
2017-03-07 03:00 | 180 | 180
2017-03-07 03:30 | 178 | 178
2017-03-07 04:00 | 178 | 178
2017-03-07 04:30 | 182 | 182
2017-03-07 05:00 | 188 | 187
2017-03-07 05:30 | 200 | 200
2017-03-07 06:00 | 209 | 209
2017-03-07 06:30 | 229 | 228
2017-03-07 07:00 | 245 | 244
2017-03-07 07:30 | 257 | 256
2017-03-07 08:00 | 258 | 257
2017-03-07 08:30 | 257 | 256
2017-03-07 09:00 | 254 | 253
2017-03-07 09:30 | 255 | 255
2017-03-07 10:00 | 255 | 254
2017-03-07 10:30 | 255 | 254
2017-03-07 11:00 | 255 | 254
2017-03-07 11:30 | 255 | 254
2017-03-07 12:00 | 259 | 258
2017-03-07 12:30 | 262 | 262
2017-03-07 13:00 | 268 | 267
2017-03-07 13:30 | 278 | 278
2017-03-07 14:00 | 286 | 286
2017-03-07 14:30 | 291 | 291
2017-03-07 15:00 | 296 | 296
2017-03-07 15:30 | 301 | 301
2017-03-07 16:00 | 310 | 310
2017-03-07 16:30 | 320 | 320
2017-03-07 17:00 | 326 | 326
2017-03-07 17:30 | 323 | 323
2017-03-07 18:00 | 316 | 316
2017-03-07 18:30 | 312 | 312
2017-03-07 19:00 | 319 | 319
2017-03-07 19:30 | 312 | 312
2017-03-07 20:00 | 304 | 304
2017-03-07 20:30 | 294 | 294
2017-03-07 21:00 | 279 | 279
2017-03-07 21:30 | 266 | 266
2017-03-07 22:00 | 251 | 251
2017-03-07 22:30 | 239 | 238
2017-03-07 23:00 | 235 | 234
2017-03-07 23:30 | 217 | 217
2017-03-08 | 200 | 200
2017-03-08 00:30 | 188 | 188
2017-03-08 01:00 | 183 | 183
2017-03-08 01:30 | 176 | 176
2017-03-08 02:00 | 172 | 171
2017-03-08 02:30 | 168 | 168
2017-03-08 03:00 | 166 | 166
2017-03-08 03:30 | 166 | 166
2017-03-08 04:00 | 166 | 166
2017-03-08 04:30 | 170 | 170
2017-03-08 05:00 | 177 | 176
2017-03-08 05:30 | 189 | 189
2017-03-08 06:00 | 199 | 198
2017-03-08 06:30 | 218 | 218
2017-03-08 07:00 | 233 | 233
2017-03-08 07:30 | 244 | 243
2017-03-08 08:00 | 248 | 248
2017-03-08 08:30 | 249 | 248
2017-03-08 09:00 | 249 | 249
2017-03-08 09:30 | 250 | 250
2017-03-08 10:00 | 254 | 253
2017-03-08 10:30 | 250 | 249
2017-03-08 11:00 | 252 | 251
2017-03-08 11:30 | 242 | 242
2017-03-08 12:00 | 244 | 244
2017-03-08 12:30 | 248 | 247
2017-03-08 13:00 | 251 | 250
2017-03-08 13:30 | 254 | 253
2017-03-08 14:00 | 262 | 261
2017-03-08 14:30 | 269 | 269
2017-03-08 15:00 | 278 | 277
2017-03-08 15:30 | 287 | 286
2017-03-08 16:00 | 289 | 288
2017-03-08 16:30 | 292 | 291
2017-03-08 17:00 | 298 | 298
2017-03-08 17:30 | 295 | 295
2017-03-08 18:00 | 291 | 291
2017-03-08 18:30 | 291 | 291
2017-03-08 19:00 | 301 | 299
2017-03-08 19:30 | 294 | 293
2017-03-08 20:00 | 290 | 289
2017-03-08 20:30 | 282 | 281
2017-03-08 21:00 | 267 | 266
2017-03-08 21:30 | 254 | 254
2017-03-08 22:00 | 242 | 242
2017-03-08 22:30 | 233 | 233
2017-03-08 23:00 | 233 | 233
2017-03-08 23:30 | 217 | 217
2017-03-09 | 200 | 200
2017-03-09 00:30 | 189 | 188
2017-03-09 01:00 | 183 | 183
2017-03-09 01:30 | 176 | 176
2017-03-09 02:00 | 172 | 171
2017-03-09 02:30 | 168 | 168
2017-03-09 03:00 | 167 | 167
2017-03-09 03:30 | 167 | 167
2017-03-09 04:00 | 167 | 167
2017-03-09 04:30 | 170 | 170
2017-03-09 05:00 | 178 | 178
2017-03-09 05:30 | 191 | 190
2017-03-09 06:00 | 201 | 200
2017-03-09 06:30 | 222 | 222
2017-03-09 07:00 | 239 | 239
2017-03-09 07:30 | 247 | 247
2017-03-09 08:00 | 246 | 245
2017-03-09 08:30 | 243 | 242
2017-03-09 09:00 | 242 | 240
2017-03-09 09:30 | 243 | 240
2017-03-09 10:00 | 240 | 237
2017-03-09 10:30 | 235 | 232
2017-03-09 11:00 | 237 | 234
2017-03-09 11:30 | 243 | 240
2017-03-09 12:00 | 249 | 246
2017-03-09 12:30 | 253 | 249
2017-03-09 13:00 | 259 | 258
2017-03-09 13:30 | 260 | 260
2017-03-09 14:00 | 264 | 263
2017-03-09 14:30 | 270 | 269
2017-03-09 15:00 | 269 | 269
2017-03-09 15:30 | 275 | 274
2017-03-09 16:00 | 286 | 285
2017-03-09 16:30 | 295 | 294
2017-03-09 17:00 | 302 | 302
2017-03-09 17:30 | 303 | 303
2017-03-09 18:00 | 301 | 301
2017-03-09 18:30 | 303 | 303
2017-03-09 19:00 | 314 | 313
2017-03-09 19:30 | 309 | 308
2017-03-09 20:00 | 303 | 303
2017-03-09 20:30 | 296 | 296
2017-03-09 21:00 | 281 | 281
2017-03-09 21:30 | 264 | 264
2017-03-09 22:00 | 249 | 249
2017-03-09 22:30 | 236 | 236
2017-03-09 23:00 | 232 | 232
2017-03-09 23:30 | 216 | 216
2017-03-10 | 198 | 198
2017-03-10 00:30 | 187 | 187
2017-03-10 01:00 | 180 | 180
2017-03-10 01:30 | 172 | 172
2017-03-10 02:00 | 167 | 167
2017-03-10 02:30 | 165 | 165
2017-03-10 03:00 | 163 | 163
2017-03-10 03:30 | 163 | 163
2017-03-10 04:00 | 164 | 164
2017-03-10 04:30 | 167 | 167
2017-03-10 05:00 | 173 | 173
2017-03-10 05:30 | 186 | 186
2017-03-10 06:00 | 195 | 195
2017-03-10 06:30 | 215 | 214
2017-03-10 07:00 | 228 | 227
2017-03-10 07:30 | 237 | 235
2017-03-10 08:00 | 236 | 235
2017-03-10 08:30 | 231 | 230
2017-03-10 09:00 | 226 | 225
2017-03-10 09:30 | 225 | 224
2017-03-10 10:00 | 224 | 223
2017-03-10 10:30 | 225 | 223
2017-03-10 11:00 | 227 | 224
2017-03-10 11:30 | 231 | 228
2017-03-10 12:00 | 232 | 228
2017-03-10 12:30 | 235 | 232
2017-03-10 13:00 | 240 | 237
2017-03-10 13:30 | 246 | 243
2017-03-10 14:00 | 254 | 250
2017-03-10 14:30 | 261 | 257
2017-03-10 15:00 | 269 | 268
2017-03-10 15:30 | 277 | 276
2017-03-10 16:00 | 288 | 287
2017-03-10 16:30 | 297 | 297
2017-03-10 17:00 | 304 | 303
2017-03-10 17:30 | 300 | 300
2017-03-10 18:00 | 291 | 291
2017-03-10 18:30 | 286 | 286
2017-03-10 19:00 | 295 | 294
2017-03-10 19:30 | 289 | 288
2017-03-10 20:00 | 280 | 280
2017-03-10 20:30 | 272 | 272
2017-03-10 21:00 | 261 | 260
2017-03-10 21:30 | 250 | 249
2017-03-10 22:00 | 242 | 241
2017-03-10 22:30 | 235 | 235
2017-03-10 23:00 | 234 | 234
2017-03-10 23:30 | 218 | 218
2017-03-11 | 200 | 200
2017-03-11 00:30 | 188 | 188
2017-03-11 01:00 | 182 | 181
2017-03-11 01:30 | 174 | 173
2017-03-11 02:00 | 169 | 169
2017-03-11 02:30 | 166 | 166
2017-03-11 03:00 | 164 | 164
2017-03-11 03:30 | 164 | 163
2017-03-11 04:00 | 162 | 162
2017-03-11 04:30 | 162 | 162
2017-03-11 05:00 | 164 | 164
2017-03-11 05:30 | 168 | 168
2017-03-11 06:00 | 170 | 170
2017-03-11 06:30 | 175 | 174
2017-03-11 07:00 | 179 | 178
2017-03-11 07:30 | 186 | 186
2017-03-11 08:00 | 190 | 190
2017-03-11 08:30 | 194 | 194
2017-03-11 09:00 | 194 | 194
2017-03-11 09:30 | 193 | 193
2017-03-11 10:00 | 192 | 192
2017-03-11 10:30 | 194 | 193
2017-03-11 11:00 | 195 | 195
2017-03-11 11:30 | 198 | 198
2017-03-11 12:00 | 203 | 202
2017-03-11 12:30 | 205 | 204
2017-03-11 13:00 | 210 | 209
2017-03-11 13:30 | 215 | 215
2017-03-11 14:00 | 218 | 217
2017-03-11 14:30 | 221 | 219
2017-03-11 15:00 | 223 | 222
2017-03-11 15:30 | 230 | 229
2017-03-11 16:00 | 238 | 238
2017-03-11 16:30 | 247 | 246
2017-03-11 17:00 | 255 | 254
2017-03-11 17:30 | 257 | 257
2017-03-11 18:00 | 255 | 255
2017-03-11 18:30 | 259 | 259
2017-03-11 19:00 | 267 | 267
2017-03-11 19:30 | 262 | 262
2017-03-11 20:00 | 258 | 258
2017-03-11 20:30 | 251 | 250
2017-03-11 21:00 | 242 | 240
2017-03-11 21:30 | 234 | 233
2017-03-11 22:00 | 226 | 226
2017-03-11 22:30 | 222 | 222
2017-03-11 23:00 | 223 | 223
2017-03-11 23:30 | 210 | 210
2017-03-12 | 194 | 194
2017-03-12 00:30 | 184 | 184
2017-03-12 01:00 | 178 | 178
2017-03-12 01:30 | 171 | 171
2017-03-12 02:00 | 166 | 166
2017-03-12 02:30 | 163 | 162
2017-03-12 03:00 | 161 | 161
2017-03-12 03:30 | 160 | 160
2017-03-12 04:00 | 159 | 159
2017-03-12 04:30 | 158 | 158
2017-03-12 05:00 | 158 | 157
2017-03-12 05:30 | 160 | 159
2017-03-12 06:00 | 161 | 161
2017-03-12 06:30 | 164 | 163
2017-03-12 07:00 | 166 | 165
2017-03-12 07:30 | 173 | 173
2017-03-12 08:00 | 176 | 176
2017-03-12 08:30 | 183 | 183
2017-03-12 09:00 | 192 | 192
2017-03-12 09:30 | 198 | 197
2017-03-12 10:00 | 197 | 197
2017-03-12 10:30 | 198 | 198
2017-03-12 11:00 | 199 | 199
2017-03-12 11:30 | 202 | 202
2017-03-12 12:00 | 210 | 209
2017-03-12 12:30 | 215 | 215
2017-03-12 13:00 | 220 | 220
2017-03-12 13:30 | 229 | 229
2017-03-12 14:00 | 239 | 239
2017-03-12 14:30 | 249 | 249
2017-03-12 15:00 | 262 | 262
2017-03-12 15:30 | 275 | 274
2017-03-12 16:00 | 286 | 286
2017-03-12 16:30 | 294 | 293
2017-03-12 17:00 | 302 | 302
2017-03-12 17:30 | 303 | 303
2017-03-12 18:00 | 304 | 304
2017-03-12 18:30 | 309 | 309
2017-03-12 19:00 | 320 | 319
2017-03-12 19:30 | 313 | 312
2017-03-12 20:00 | 308 | 307
2017-03-12 20:30 | 300 | 300
2017-03-12 21:00 | 285 | 285
2017-03-12 21:30 | 274 | 274
2017-03-12 22:00 | 260 | 260
2017-03-12 22:30 | 251 | 251
2017-03-12 23:00 | 247 | 247
2017-03-12 23:30 | 231 | 230
2017-03-13 | 213 | 212
2017-03-13 00:30 | 201 | 201
2017-03-13 01:00 | 195 | 194
2017-03-13 01:30 | 188 | 188
2017-03-13 02:00 | 183 | 183
2017-03-13 02:30 | 180 | 180
2017-03-13 03:00 | 178 | 178
2017-03-13 03:30 | 177 | 177
2017-03-13 04:00 | 178 | 177
2017-03-13 04:30 | 181 | 181
2017-03-13 05:00 | 188 | 187
2017-03-13 05:30 | 201 | 200
2017-03-13 06:00 | 212 | 212
2017-03-13 06:30 | 232 | 232
2017-03-13 07:00 | 251 | 251
2017-03-13 07:30 | 274 | 274
2017-03-13 08:00 | 294 | 293
2017-03-13 08:30 | 303 | 302
2017-03-13 09:00 | 300 | 299
2017-03-13 09:30 | 298 | 298
2017-03-13 10:00 | 292 | 292
2017-03-13 10:30 | 281 | 281
2017-03-13 11:00 | 269 | 269
2017-03-13 11:30 | 274 | 274
2017-03-13 12:00 | 277 | 276
2017-03-13 12:30 | 267 | 267
2017-03-13 13:00 | 270 | 269
2017-03-13 13:30 | 280 | 279
2017-03-13 14:00 | 294 | 293
2017-03-13 14:30 | 298 | 297
2017-03-13 15:00 | 297 | 296
2017-03-13 15:30 | 298 | 297
2017-03-13 16:00 | 303 | 302
2017-03-13 16:30 | 305 | 304
2017-03-13 17:00 | 306 | 305
2017-03-13 17:30 | 304 | 303
2017-03-13 18:00 | 302 | 302
2017-03-13 18:30 | 306 | 304
2017-03-13 19:00 | 316 | 315
2017-03-13 19:30 | 310 | 310
2017-03-13 20:00 | 307 | 307
2017-03-13 20:30 | 298 | 298
2017-03-13 21:00 | 281 | 280
2017-03-13 21:30 | 268 | 268
2017-03-13 22:00 | 253 | 253
2017-03-13 22:30 | 242 | 242
2017-03-13 23:00 | 240 | 239
2017-03-13 23:30 | 225 | 224
2017-03-14 | 208 | 207
2017-03-14 00:30 | 197 | 196
2017-03-14 01:00 | 191 | 190
2017-03-14 01:30 | 183 | 183
2017-03-14 02:00 | 178 | 178
2017-03-14 02:30 | 175 | 175
2017-03-14 03:00 | 173 | 173
2017-03-14 03:30 | 173 | 173
2017-03-14 04:00 | 173 | 173
2017-03-14 04:30 | 177 | 176
2017-03-14 05:00 | 184 | 183
2017-03-14 05:30 | 198 | 198
2017-03-14 06:00 | 211 | 211
2017-03-14 06:30 | 233 | 233
2017-03-14 07:00 | 251 | 250
2017-03-14 07:30 | 269 | 268
2017-03-14 08:00 | 278 | 277
2017-03-14 08:30 | 278 | 277
2017-03-14 09:00 | 282 | 281
2017-03-14 09:30 | 290 | 289
2017-03-14 10:00 | 285 | 283
2017-03-14 10:30 | 278 | 276
2017-03-14 11:00 | 285 | 284
2017-03-14 11:30 | 305 | 304
2017-03-14 12:00 | 305 | 304
2017-03-14 12:30 | 287 | 287
2017-03-14 13:00 | 270 | 269
2017-03-14 13:30 | 273 | 272
2017-03-14 14:00 | 282 | 281
2017-03-14 14:30 | 277 | 276
2017-03-14 15:00 | 273 | 273
2017-03-14 15:30 | 275 | 275
2017-03-14 16:00 | 282 | 282
2017-03-14 16:30 | 295 | 295
2017-03-14 17:00 | 304 | 304
2017-03-14 17:30 | 304 | 304
2017-03-14 18:00 | 302 | 302
2017-03-14 18:30 | 304 | 304
2017-03-14 19:00 | 310 | 310
2017-03-14 19:30 | 303 | 303
2017-03-14 20:00 | 298 | 298
2017-03-14 20:30 | 293 | 292
2017-03-14 21:00 | 277 | 277
2017-03-14 21:30 | 265 | 265
2017-03-14 22:00 | 253 | 253
2017-03-14 22:30 | 245 | 244
2017-03-14 23:00 | 241 | 241
2017-03-14 23:30 | 224 | 223
2017-03-15 | 205 | 205
2017-03-15 00:30 | 196 | 196
2017-03-15 01:00 | 190 | 189
2017-03-15 01:30 | 181 | 181
2017-03-15 02:00 | 176 | 176
2017-03-15 02:30 | 174 | 174
2017-03-15 03:00 | 174 | 174
2017-03-15 03:30 | 174 | 174
2017-03-15 04:00 | 174 | 174
2017-03-15 04:30 | 177 | 177
2017-03-15 05:00 | 181 | 181
2017-03-15 05:30 | 195 | 195
2017-03-15 06:00 | 207 | 207
2017-03-15 06:30 | 229 | 229
2017-03-15 07:00 | 246 | 246
2017-03-15 07:30 | 260 | 259
2017-03-15 08:00 | 261 | 260
2017-03-15 08:30 | 265 | 263
2017-03-15 09:00 | 266 | 264
2017-03-15 09:30 | 269 | 267
2017-03-15 10:00 | 274 | 271
2017-03-15 10:30 | 275 | 273
2017-03-15 11:00 | 275 | 273
2017-03-15 11:30 | 273 | 271
2017-03-15 12:00 | 274 | 272
2017-03-15 12:30 | 274 | 272
2017-03-15 13:00 | 276 | 275
2017-03-15 13:30 | 279 | 278
2017-03-15 14:00 | 281 | 280
2017-03-15 14:30 | 285 | 284
2017-03-15 15:00 | 282 | 281
2017-03-15 15:30 | 286 | 285
2017-03-15 16:00 | 291 | 290
2017-03-15 16:30 | 293 | 292
2017-03-15 17:00 | 297 | 296
2017-03-15 17:30 | 298 | 296
2017-03-15 18:00 | 296 | 294
2017-03-15 18:30 | 300 | 297
2017-03-15 19:00 | 309 | 308
2017-03-15 19:30 | 302 | 300
2017-03-15 20:00 | 299 | 298
2017-03-15 20:30 | 290 | 290
2017-03-15 21:00 | 273 | 273
2017-03-15 21:30 | 259 | 259
2017-03-15 22:00 | 246 | 246
2017-03-15 22:30 | 235 | 234
2017-03-15 23:00 | 233 | 231
2017-03-15 23:30 | 216 | 215
2017-03-16 | 198 | 197
2017-03-16 00:30 | 186 | 186
2017-03-16 01:00 | 180 | 179
2017-03-16 01:30 | 172 | 172
2017-03-16 02:00 | 168 | 168
2017-03-16 02:30 | 164 | 164
2017-03-16 03:00 | 163 | 163
2017-03-16 03:30 | 162 | 162
2017-03-16 04:00 | 163 | 163
2017-03-16 04:30 | 167 | 167
2017-03-16 05:00 | 174 | 174
2017-03-16 05:30 | 187 | 187
2017-03-16 06:00 | 200 | 200
2017-03-16 06:30 | 220 | 220
2017-03-16 07:00 | 240 | 239
2017-03-16 07:30 | 257 | 256
2017-03-16 08:00 | 265 | 265
2017-03-16 08:30 | 263 | 263
2017-03-16 09:00 | 267 | 266
2017-03-16 09:30 | 267 | 266
2017-03-16 10:00 | 266 | 266
2017-03-16 10:30 | 266 | 265
2017-03-16 11:00 | 265 | 264
2017-03-16 11:30 | 262 | 261
2017-03-16 12:00 | 271 | 270
2017-03-16 12:30 | 284 | 283
2017-03-16 13:00 | 288 | 287
2017-03-16 13:30 | 292 | 291
2017-03-16 14:00 | 308 | 307
2017-03-16 14:30 | 315 | 313
2017-03-16 15:00 | 322 | 320
2017-03-16 15:30 | 321 | 319
2017-03-16 16:00 | 321 | 320
2017-03-16 16:30 | 325 | 324
2017-03-16 17:00 | 327 | 326
2017-03-16 17:30 | 326 | 325
2017-03-16 18:00 | 324 | 322
2017-03-16 18:30 | 327 | 325
2017-03-16 19:00 | 333 | 330
2017-03-16 19:30 | 325 | 323
2017-03-16 20:00 | 321 | 319
2017-03-16 20:30 | 312 | 311
2017-03-16 21:00 | 295 | 295
2017-03-16 21:30 | 277 | 277
2017-03-16 22:00 | 261 | 261
2017-03-16 22:30 | 249 | 249
2017-03-16 23:00 | 244 | 244
2017-03-16 23:30 | 225 | 224
2017-03-17 | 205 | 205
2017-03-17 00:30 | 193 | 192
2017-03-17 01:00 | 186 | 183
2017-03-17 01:30 | 178 | 175
2017-03-17 02:00 | 173 | 171
2017-03-17 02:30 | 170 | 168
2017-03-17 03:00 | 168 | 165
2017-03-17 03:30 | 167 | 164
2017-03-17 04:00 | 167 | 164
2017-03-17 04:30 | 169 | 167
2017-03-17 05:00 | 176 | 173
2017-03-17 05:30 | 188 | 187
2017-03-17 06:00 | 200 | 200
2017-03-17 06:30 | 218 | 218
2017-03-17 07:00 | 236 | 235
2017-03-17 07:30 | 251 | 251
2017-03-17 08:00 | 256 | 256
2017-03-17 08:30 | 256 | 256
2017-03-17 09:00 | 258 | 257
2017-03-17 09:30 | 261 | 261
2017-03-17 10:00 | 264 | 263
2017-03-17 10:30 | 269 | 269
2017-03-17 11:00 | 273 | 273
2017-03-17 11:30 | 278 | 278
2017-03-17 12:00 | 291 | 290
2017-03-17 12:30 | 307 | 306
2017-03-17 13:00 | 325 | 324
2017-03-17 13:30 | 340 | 339
2017-03-17 14:00 | 330 | 329
2017-03-17 14:30 | 320 | 319
2017-03-17 15:00 | 322 | 321
2017-03-17 15:30 | 320 | 319
2017-03-17 16:00 | 306 | 305
2017-03-17 16:30 | 298 | 297
2017-03-17 17:00 | 298 | 296
2017-03-17 17:30 | 295 | 293
2017-03-17 18:00 | 288 | 287
2017-03-17 18:30 | 287 | 285
2017-03-17 19:00 | 293 | 290
2017-03-17 19:30 | 286 | 284
2017-03-17 20:00 | 281 | 279
2017-03-17 20:30 | 276 | 274
2017-03-17 21:00 | 263 | 262
2017-03-17 21:30 | 251 | 248
2017-03-17 22:00 | 240 | 236
2017-03-17 22:30 | 231 | 227
2017-03-17 23:00 | 230 | 227
2017-03-17 23:30 | 215 | 211
2017-03-18 | 197 | 195
2017-03-18 00:30 | 185 | 183
2017-03-18 01:00 | 178 | 176
2017-03-18 01:30 | 170 | 168
2017-03-18 02:00 | 165 | 163
2017-03-18 02:30 | 162 | 160
2017-03-18 03:00 | 159 | 158
2017-03-18 03:30 | 159 | 157
2017-03-18 04:00 | 159 | 157
2017-03-18 04:30 | 159 | 157
2017-03-18 05:00 | 160 | 158
2017-03-18 05:30 | 165 | 163
2017-03-18 06:00 | 167 | 165
2017-03-18 06:30 | 174 | 172
2017-03-18 07:00 | 182 | 180
2017-03-18 07:30 | 203 | 202
2017-03-18 08:00 | 212 | 211
2017-03-18 08:30 | 219 | 218
2017-03-18 09:00 | 224 | 223
2017-03-18 09:30 | 223 | 223
2017-03-18 10:00 | 221 | 220
2017-03-18 10:30 | 222 | 222
2017-03-18 11:00 | 224 | 224
2017-03-18 11:30 | 235 | 235
2017-03-18 12:00 | 242 | 241
2017-03-18 12:30 | 234 | 233
2017-03-18 13:00 | 229 | 229
2017-03-18 13:30 | 238 | 237
2017-03-18 14:00 | 247 | 247
2017-03-18 14:30 | 257 | 256
2017-03-18 15:00 | 267 | 266
2017-03-18 15:30 | 277 | 277
2017-03-18 16:00 | 286 | 286
2017-03-18 16:30 | 290 | 290
2017-03-18 17:00 | 297 | 297
2017-03-18 17:30 | 297 | 297
2017-03-18 18:00 | 293 | 293
2017-03-18 18:30 | 298 | 297
2017-03-18 19:00 | 305 | 305
2017-03-18 19:30 | 298 | 298
2017-03-18 20:00 | 296 | 296
2017-03-18 20:30 | 291 | 291
2017-03-18 21:00 | 279 | 279
2017-03-18 21:30 | 271 | 271
2017-03-18 22:00 | 261 | 261
2017-03-18 22:30 | 251 | 251
2017-03-18 23:00 | 246 | 246
2017-03-18 23:30 | 229 | 228
2017-03-19 | 205 | 204
2017-03-19 00:30 | 193 | 192
2017-03-19 01:00 | 185 | 184
2017-03-19 01:30 | 176 | 175
2017-03-19 02:00 | 169 | 169
2017-03-19 02:30 | 166 | 165
2017-03-19 03:00 | 162 | 162
2017-03-19 03:30 | 160 | 160
2017-03-19 04:00 | 158 | 158
2017-03-19 04:30 | 158 | 158
2017-03-19 05:00 | 158 | 158
2017-03-19 05:30 | 160 | 160
2017-03-19 06:00 | 163 | 163
2017-03-19 06:30 | 167 | 167
2017-03-19 07:00 | 172 | 172
2017-03-19 07:30 | 182 | 181
2017-03-19 08:00 | 186 | 185
2017-03-19 08:30 | 194 | 192
2017-03-19 09:00 | 209 | 208
2017-03-19 09:30 | 223 | 221
2017-03-19 10:00 | 224 | 223
2017-03-19 10:30 | 218 | 217
2017-03-19 11:00 | 207 | 206
2017-03-19 11:30 | 210 | 208
2017-03-19 12:00 | 213 | 211
2017-03-19 12:30 | 218 | 216
2017-03-19 13:00 | 225 | 222
2017-03-19 13:30 | 227 | 225
2017-03-19 14:00 | 231 | 228
2017-03-19 14:30 | 237 | 234
2017-03-19 15:00 | 238 | 235
2017-03-19 15:30 | 247 | 243
2017-03-19 16:00 | 259 | 259
2017-03-19 16:30 | 269 | 269
2017-03-19 17:00 | 273 | 273
2017-03-19 17:30 | 277 | 277
2017-03-19 18:00 | 284 | 284
2017-03-19 18:30 | 292 | 292
2017-03-19 19:00 | 297 | 297
2017-03-19 19:30 | 287 | 287
2017-03-19 20:00 | 281 | 280
2017-03-19 20:30 | 274 | 273
2017-03-19 21:00 | 261 | 261
2017-03-19 21:30 | 251 | 250
2017-03-19 22:00 | 237 | 235
2017-03-19 22:30 | 227 | 226
2017-03-19 23:00 | 226 | 225
2017-03-19 23:30 | 212 | 211
2017-03-20 | 195 | 194
2017-03-20 00:30 | 184 | 183
2017-03-20 01:00 | 179 | 178
2017-03-20 01:30 | 173 | 173
2017-03-20 02:00 | 169 | 168
2017-03-20 02:30 | 166 | 166
2017-03-20 03:00 | 164 | 164
2017-03-20 03:30 | 163 | 163
2017-03-20 04:00 | 164 | 163
2017-03-20 04:30 | 167 | 167
2017-03-20 05:00 | 176 | 175
2017-03-20 05:30 | 190 | 189
2017-03-20 06:00 | 204 | 203
2017-03-20 06:30 | 228 | 227
2017-03-20 07:00 | 250 | 250
2017-03-20 07:30 | 266 | 266
2017-03-20 08:00 | 270 | 269
2017-03-20 08:30 | 281 | 281
2017-03-20 09:00 | 290 | 289
2017-03-20 09:30 | 301 | 300
2017-03-20 10:00 | 299 | 299
2017-03-20 10:30 | 295 | 294
2017-03-20 11:00 | 296 | 295
2017-03-20 11:30 | 296 | 295
2017-03-20 12:00 | 300 | 299
2017-03-20 12:30 | 308 | 308
2017-03-20 13:00 | 308 | 307
2017-03-20 13:30 | 301 | 301
2017-03-20 14:00 | 305 | 305
2017-03-20 14:30 | 304 | 304
2017-03-20 15:00 | 298 | 298
2017-03-20 15:30 | 298 | 298
2017-03-20 16:00 | 303 | 303
2017-03-20 16:30 | 307 | 307
2017-03-20 17:00 | 311 | 311
2017-03-20 17:30 | 311 | 311
2017-03-20 18:00 | 305 | 305
2017-03-20 18:30 | 308 | 308
2017-03-20 19:00 | 308 | 308
2017-03-20 19:30 | 298 | 297
2017-03-20 20:00 | 294 | 294
2017-03-20 20:30 | 287 | 287
2017-03-20 21:00 | 271 | 271
2017-03-20 21:30 | 258 | 258
2017-03-20 22:00 | 246 | 245
2017-03-20 22:30 | 234 | 234
2017-03-20 23:00 | 232 | 232
2017-03-20 23:30 | 220 | 220
2017-03-21 | 202 | 202
2017-03-21 00:30 | 189 | 189
2017-03-21 01:00 | 184 | 183
2017-03-21 01:30 | 176 | 176
2017-03-21 02:00 | 172 | 171
2017-03-21 02:30 | 170 | 170
2017-03-21 03:00 | 169 | 169
2017-03-21 03:30 | 168 | 168
2017-03-21 04:00 | 169 | 169
2017-03-21 04:30 | 172 | 172
2017-03-21 05:00 | 181 | 180
2017-03-21 05:30 | 195 | 194
2017-03-21 06:00 | 208 | 207
2017-03-21 06:30 | 230 | 228
2017-03-21 07:00 | 251 | 250
2017-03-21 07:30 | 270 | 267
2017-03-21 08:00 | 278 | 276
2017-03-21 08:30 | 279 | 279
2017-03-21 09:00 | 279 | 279
2017-03-21 09:30 | 282 | 282
2017-03-21 10:00 | 286 | 286
2017-03-21 10:30 | 285 | 285
2017-03-21 11:00 | 277 | 277
2017-03-21 11:30 | 279 | 279
2017-03-21 12:00 | 283 | 283
2017-03-21 12:30 | 289 | 289
2017-03-21 13:00 | 287 | 287
2017-03-21 13:30 | 289 | 289
2017-03-21 14:00 | 294 | 294
2017-03-21 14:30 | 295 | 295
2017-03-21 15:00 | 296 | 296
2017-03-21 15:30 | 300 | 300
2017-03-21 16:00 | 307 | 307
2017-03-21 16:30 | 312 | 312
2017-03-21 17:00 | 317 | 317
2017-03-21 17:30 | 317 | 317
2017-03-21 18:00 | 318 | 318
2017-03-21 18:30 | 324 | 324
2017-03-21 19:00 | 327 | 327
2017-03-21 19:30 | 320 | 320
2017-03-21 20:00 | 317 | 317
2017-03-21 20:30 | 310 | 309
2017-03-21 21:00 | 292 | 292
2017-03-21 21:30 | 279 | 279
2017-03-21 22:00 | 265 | 265
2017-03-21 22:30 | 253 | 253
2017-03-21 23:00 | 250 | 250
2017-03-21 23:30 | 232 | 231
2017-03-22 | 213 | 212
2017-03-22 00:30 | 200 | 199
2017-03-22 01:00 | 193 | 193
2017-03-22 01:30 | 186 | 186
2017-03-22 02:00 | 180 | 180
2017-03-22 02:30 | 178 | 178
2017-03-22 03:00 | 175 | 175
2017-03-22 03:30 | 175 | 174
2017-03-22 04:00 | 175 | 175
2017-03-22 04:30 | 180 | 179
2017-03-22 05:00 | 187 | 186
2017-03-22 05:30 | 201 | 199
2017-03-22 06:00 | 215 | 212
2017-03-22 06:30 | 238 | 238
2017-03-22 07:00 | 259 | 259
2017-03-22 07:30 | 277 | 277
2017-03-22 08:00 | 281 | 281
2017-03-22 08:30 | 281 | 281
2017-03-22 09:00 | 281 | 281
2017-03-22 09:30 | 285 | 284
2017-03-22 10:00 | 294 | 293
2017-03-22 10:30 | 293 | 293
2017-03-22 11:00 | 298 | 298
2017-03-22 11:30 | 300 | 300
2017-03-22 12:00 | 298 | 297
2017-03-22 12:30 | 302 | 301
2017-03-22 13:00 | 306 | 306
2017-03-22 13:30 | 310 | 310
2017-03-22 14:00 | 307 | 306
2017-03-22 14:30 | 303 | 303
2017-03-22 15:00 | 300 | 300
2017-03-22 15:30 | 299 | 299
2017-03-22 16:00 | 304 | 304
2017-03-22 16:30 | 310 | 310
2017-03-22 17:00 | 313 | 313
2017-03-22 17:30 | 312 | 312
2017-03-22 18:00 | 309 | 309
2017-03-22 18:30 | 312 | 312
2017-03-22 19:00 | 316 | 316
2017-03-22 19:30 | 307 | 307
2017-03-22 20:00 | 303 | 303
2017-03-22 20:30 | 296 | 296
2017-03-22 21:00 | 281 | 281
2017-03-22 21:30 | 268 | 268
2017-03-22 22:00 | 256 | 256
2017-03-22 22:30 | 244 | 244
2017-03-22 23:00 | 243 | 242
2017-03-22 23:30 | 226 | 226
2017-03-23 | 208 | 208
2017-03-23 00:30 | 196 | 196
2017-03-23 01:00 | 188 | 188
2017-03-23 01:30 | 181 | 181
2017-03-23 02:00 | 175 | 175
2017-03-23 02:30 | 173 | 173
2017-03-23 03:00 | 171 | 171
2017-03-23 03:30 | 172 | 172
2017-03-23 04:00 | 172 | 172
2017-03-23 04:30 | 175 | 175
2017-03-23 05:00 | 184 | 184
2017-03-23 05:30 | 198 | 198
2017-03-23 06:00 | 212 | 211
2017-03-23 06:30 | 233 | 231
2017-03-23 07:00 | 255 | 255
2017-03-23 07:30 | 274 | 274
2017-03-23 08:00 | 279 | 278
2017-03-23 08:30 | 279 | 279
2017-03-23 09:00 | 282 | 281
2017-03-23 09:30 | 287 | 287
2017-03-23 10:00 | 290 | 290
2017-03-23 10:30 | 290 | 290
2017-03-23 11:00 | 283 | 283
2017-03-23 11:30 | 282 | 282
2017-03-23 12:00 | 288 | 288
2017-03-23 12:30 | 290 | 290
2017-03-23 13:00 | 296 | 296
2017-03-23 13:30 | 294 | 294
2017-03-23 14:00 | 299 | 299
2017-03-23 14:30 | 306 | 306
2017-03-23 15:00 | 302 | 302
2017-03-23 15:30 | 305 | 305
2017-03-23 16:00 | 311 | 311
2017-03-23 16:30 | 317 | 317
2017-03-23 17:00 | 323 | 323
2017-03-23 17:30 | 324 | 324
2017-03-23 18:00 | 323 | 323
2017-03-23 18:30 | 327 | 327
2017-03-23 19:00 | 332 | 332
2017-03-23 19:30 | 325 | 325
2017-03-23 20:00 | 321 | 321
2017-03-23 20:30 | 314 | 313
2017-03-23 21:00 | 298 | 298
2017-03-23 21:30 | 281 | 281
2017-03-23 22:00 | 265 | 265
2017-03-23 22:30 | 254 | 254
2017-03-23 23:00 | 252 | 252
2017-03-23 23:30 | 235 | 235
2017-03-24 | 216 | 216
2017-03-24 00:30 | 202 | 202
2017-03-24 01:00 | 194 | 194
2017-03-24 01:30 | 187 | 187
2017-03-24 02:00 | 181 | 180
2017-03-24 02:30 | 178 | 178
2017-03-24 03:00 | 176 | 176
2017-03-24 03:30 | 174 | 174
2017-03-24 04:00 | 175 | 175
2017-03-24 04:30 | 179 | 178
2017-03-24 05:00 | 186 | 186
2017-03-24 05:30 | 199 | 198
2017-03-24 06:00 | 211 | 211
2017-03-24 06:30 | 232 | 232
2017-03-24 07:00 | 248 | 248
2017-03-24 07:30 | 264 | 262
2017-03-24 08:00 | 269 | 266
2017-03-24 08:30 | 273 | 269
2017-03-24 09:00 | 279 | 278
2017-03-24 09:30 | 282 | 281
2017-03-24 10:00 | 282 | 281
2017-03-24 10:30 | 282 | 281
2017-03-24 11:00 | 288 | 287
2017-03-24 11:30 | 294 | 293
2017-03-24 12:00 | 300 | 299
2017-03-24 12:30 | 299 | 299
2017-03-24 13:00 | 304 | 304
2017-03-24 13:30 | 303 | 303
2017-03-24 14:00 | 305 | 305
2017-03-24 14:30 | 302 | 302
2017-03-24 15:00 | 294 | 294
2017-03-24 15:30 | 293 | 293
2017-03-24 16:00 | 297 | 297
2017-03-24 16:30 | 306 | 305
2017-03-24 17:00 | 307 | 306
2017-03-24 17:30 | 301 | 301
2017-03-24 18:00 | 296 | 296
2017-03-24 18:30 | 298 | 298
2017-03-24 19:00 | 300 | 299
2017-03-24 19:30 | 291 | 291
2017-03-24 20:00 | 286 | 285
2017-03-24 20:30 | 279 | 279
2017-03-24 21:00 | 264 | 264
2017-03-24 21:30 | 254 | 254
2017-03-24 22:00 | 244 | 244
2017-03-24 22:30 | 235 | 235
2017-03-24 23:00 | 233 | 232
2017-03-24 23:30 | 219 | 219
2017-03-25 | 201 | 201
2017-03-25 00:30 | 190 | 190
2017-03-25 01:00 | 183 | 183
2017-03-25 01:30 | 176 | 176
2017-03-25 02:00 | 169 | 169
2017-03-25 02:30 | 166 | 166
2017-03-25 03:00 | 163 | 163
2017-03-25 03:30 | 162 | 162
2017-03-25 04:00 | 161 | 161
2017-03-25 04:30 | 162 | 162
2017-03-25 05:00 | 164 | 164
2017-03-25 05:30 | 168 | 168
2017-03-25 06:00 | 172 | 172
2017-03-25 06:30 | 180 | 180
2017-03-25 07:00 | 186 | 186
2017-03-25 07:30 | 193 | 193
2017-03-25 08:00 | 217 | 216
2017-03-25 08:30 | 224 | 224
2017-03-25 09:00 | 231 | 231
2017-03-25 09:30 | 238 | 238
2017-03-25 10:00 | 244 | 244
2017-03-25 10:30 | 228 | 228
2017-03-25 11:00 | 225 | 225
2017-03-25 11:30 | 225 | 225
2017-03-25 12:00 | 224 | 224
2017-03-25 12:30 | 220 | 220
2017-03-25 13:00 | 220 | 220
2017-03-25 13:30 | 220 | 220
2017-03-25 14:00 | 215 | 215
2017-03-25 14:30 | 218 | 218
2017-03-25 15:00 | 224 | 224
2017-03-25 15:30 | 233 | 232
2017-03-25 16:00 | 241 | 241
2017-03-25 16:30 | 246 | 246
2017-03-25 17:00 | 256 | 255
2017-03-25 17:30 | 251 | 251
2017-03-25 18:00 | 252 | 252
2017-03-25 18:30 | 262 | 262
2017-03-25 19:00 | 265 | 264
2017-03-25 19:30 | 257 | 257
2017-03-25 20:00 | 253 | 253
2017-03-25 20:30 | 248 | 248
2017-03-25 21:00 | 237 | 237
2017-03-25 21:30 | 230 | 229
2017-03-25 22:00 | 223 | 222
2017-03-25 22:30 | 218 | 218
2017-03-25 23:00 | 221 | 220
2017-03-25 23:30 | 207 | 207
2017-03-26 | 193 | 193
2017-03-26 00:30 | 181 | 181
2017-03-26 01:00 | 173 | 173
2017-03-26 01:30 | 166 | 166
2017-03-26 02:00 | 161 | 161
2017-03-26 02:30 | 157 | 157
2017-03-26 03:00 | 155 | 155
2017-03-26 03:30 | 153 | 153
2017-03-26 04:00 | 153 | 153
2017-03-26 04:30 | 152 | 152
2017-03-26 05:00 | 152 | 152
2017-03-26 05:30 | 153 | 153
2017-03-26 06:00 | 155 | 155
2017-03-26 06:30 | 159 | 159
2017-03-26 07:00 | 164 | 164
2017-03-26 07:30 | 169 | 169
2017-03-26 08:00 | 173 | 173
2017-03-26 08:30 | 179 | 179
2017-03-26 09:00 | 189 | 188
2017-03-26 09:30 | 199 | 198
2017-03-26 10:00 | 194 | 193
2017-03-26 10:30 | 193 | 192
2017-03-26 11:00 | 196 | 195
2017-03-26 11:30 | 194 | 193
2017-03-26 12:00 | 202 | 201
2017-03-26 12:30 | 209 | 208
2017-03-26 13:00 | 217 | 215
2017-03-26 13:30 | 227 | 226
2017-03-26 14:00 | 230 | 228
2017-03-26 14:30 | 233 | 232
2017-03-26 15:00 | 246 | 244
2017-03-26 15:30 | 259 | 256
2017-03-26 16:00 | 272 | 271
2017-03-26 16:30 | 282 | 281
2017-03-26 17:00 | 292 | 291
2017-03-26 17:30 | 295 | 295
2017-03-26 18:00 | 296 | 296
2017-03-26 18:30 | 305 | 305
2017-03-26 19:00 | 306 | 306
2017-03-26 19:30 | 296 | 296
2017-03-26 20:00 | 290 | 290
2017-03-26 20:30 | 281 | 281
2017-03-26 21:00 | 267 | 267
2017-03-26 21:30 | 255 | 255
2017-03-26 22:00 | 243 | 243
2017-03-26 22:30 | 232 | 232
2017-03-26 23:00 | 231 | 231
2017-03-26 23:30 | 217 | 217
2017-03-27 | 200 | 199
2017-03-27 00:30 | 189 | 189
2017-03-27 01:00 | 183 | 182
2017-03-27 01:30 | 176 | 176
2017-03-27 02:00 | 171 | 171
2017-03-27 02:30 | 168 | 168
2017-03-27 03:00 | 166 | 166
2017-03-27 03:30 | 165 | 165
2017-03-27 04:00 | 166 | 166
2017-03-27 04:30 | 169 | 169
2017-03-27 05:00 | 176 | 175
2017-03-27 05:30 | 190 | 189
2017-03-27 06:00 | 205 | 204
2017-03-27 06:30 | 227 | 225
2017-03-27 07:00 | 248 | 246
2017-03-27 07:30 | 263 | 263
2017-03-27 08:00 | 269 | 269
2017-03-27 08:30 | 272 | 272
2017-03-27 09:00 | 274 | 274
2017-03-27 09:30 | 278 | 277
2017-03-27 10:00 | 280 | 279
2017-03-27 10:30 | 279 | 277
2017-03-27 11:00 | 279 | 277
2017-03-27 11:30 | 277 | 274
2017-03-27 12:00 | 279 | 278
2017-03-27 12:30 | 283 | 282
2017-03-27 13:00 | 291 | 289
2017-03-27 13:30 | 296 | 294
2017-03-27 14:00 | 302 | 300
2017-03-27 14:30 | 302 | 300
2017-03-27 15:00 | 302 | 300
2017-03-27 15:30 | 307 | 305
2017-03-27 16:00 | 318 | 316
2017-03-27 16:30 | 322 | 320
2017-03-27 17:00 | 326 | 324
2017-03-27 17:30 | 323 | 322
2017-03-27 18:00 | 320 | 319
2017-03-27 18:30 | 322 | 321
2017-03-27 19:00 | 326 | 324
2017-03-27 19:30 | 313 | 312
2017-03-27 20:00 | 311 | 308
2017-03-27 20:30 | 301 | 299
2017-03-27 21:00 | 284 | 282
2017-03-27 21:30 | 269 | 268
2017-03-27 22:00 | 255 | 254
2017-03-27 22:30 | 244 | 243
2017-03-27 23:00 | 241 | 241
2017-03-27 23:30 | 225 | 225
2017-03-28 | 207 | 207
2017-03-28 00:30 | 194 | 193
2017-03-28 01:00 | 187 | 187
2017-03-28 01:30 | 180 | 179
2017-03-28 02:00 | 175 | 174
2017-03-28 02:30 | 171 | 171
2017-03-28 03:00 | 169 | 169
2017-03-28 03:30 | 169 | 169
2017-03-28 04:00 | 169 | 168
2017-03-28 04:30 | 173 | 172
2017-03-28 05:00 | 180 | 179
2017-03-28 05:30 | 193 | 193
2017-03-28 06:00 | 204 | 204
2017-03-28 06:30 | 224 | 224
2017-03-28 07:00 | 241 | 240
2017-03-28 07:30 | 252 | 252
2017-03-28 08:00 | 255 | 255
2017-03-28 08:30 | 255 | 254
2017-03-28 09:00 | 257 | 257
2017-03-28 09:30 | 262 | 262
2017-03-28 10:00 | 261 | 260
2017-03-28 10:30 | 261 | 260
2017-03-28 11:00 | 262 | 261
2017-03-28 11:30 | 265 | 263
2017-03-28 12:00 | 268 | 265
2017-03-28 12:30 | 272 | 269
2017-03-28 13:00 | 277 | 275
2017-03-28 13:30 | 286 | 284
2017-03-28 14:00 | 295 | 295
2017-03-28 14:30 | 302 | 301
2017-03-28 15:00 | 307 | 306
2017-03-28 15:30 | 314 | 314
2017-03-28 16:00 | 326 | 325
2017-03-28 16:30 | 333 | 333
2017-03-28 17:00 | 338 | 337
2017-03-28 17:30 | 332 | 332
2017-03-28 18:00 | 329 | 328
2017-03-28 18:30 | 332 | 331
2017-03-28 19:00 | 334 | 333
2017-03-28 19:30 | 323 | 323
2017-03-28 20:00 | 318 | 318
2017-03-28 20:30 | 308 | 308
2017-03-28 21:00 | 290 | 288
2017-03-28 21:30 | 276 | 273
2017-03-28 22:00 | 261 | 259
2017-03-28 22:30 | 248 | 247
2017-03-28 23:00 | 243 | 243
2017-03-28 23:30 | 225 | 225
2017-03-29 | 208 | 207
2017-03-29 00:30 | 195 | 194
2017-03-29 01:00 | 188 | 187
2017-03-29 01:30 | 181 | 179
2017-03-29 02:00 | 175 | 174
2017-03-29 02:30 | 171 | 170
2017-03-29 03:00 | 170 | 169
2017-03-29 03:30 | 168 | 167
2017-03-29 04:00 | 168 | 168
2017-03-29 04:30 | 172 | 171
2017-03-29 05:00 | 180 | 179
2017-03-29 05:30 | 195 | 193
2017-03-29 06:00 | 206 | 206
2017-03-29 06:30 | 226 | 226
2017-03-29 07:00 | 244 | 243
2017-03-29 07:30 | 260 | 258
2017-03-29 08:00 | 264 | 262
2017-03-29 08:30 | 271 | 268
2017-03-29 09:00 | 274 | 274
2017-03-29 09:30 | 286 | 286
2017-03-29 10:00 | 294 | 294
2017-03-29 10:30 | 295 | 295
2017-03-29 11:00 | 298 | 298
2017-03-29 11:30 | 302 | 302
2017-03-29 12:00 | 302 | 302
2017-03-29 12:30 | 297 | 297
2017-03-29 13:00 | 298 | 298
2017-03-29 13:30 | 305 | 304
2017-03-29 14:00 | 307 | 306
2017-03-29 14:30 | 315 | 314
2017-03-29 15:00 | 323 | 322
2017-03-29 15:30 | 321 | 321
2017-03-29 16:00 | 323 | 323
2017-03-29 16:30 | 326 | 326
2017-03-29 17:00 | 329 | 329
2017-03-29 17:30 | 328 | 328
2017-03-29 18:00 | 328 | 328
2017-03-29 18:30 | 329 | 329
2017-03-29 19:00 | 331 | 331
2017-03-29 19:30 | 323 | 322
2017-03-29 20:00 | 320 | 320
2017-03-29 20:30 | 313 | 313
2017-03-29 21:00 | 297 | 297
2017-03-29 21:30 | 283 | 283
2017-03-29 22:00 | 271 | 271
2017-03-29 22:30 | 262 | 262
2017-03-29 23:00 | 258 | 258
2017-03-29 23:30 | 240 | 240
2017-03-30 | 221 | 221
2017-03-30 00:30 | 207 | 206
2017-03-30 01:00 | 197 | 196
2017-03-30 01:30 | 192 | 191
2017-03-30 02:00 | 187 | 186
2017-03-30 02:30 | 184 | 183
2017-03-30 03:00 | 182 | 182
2017-03-30 03:30 | 181 | 180
2017-03-30 04:00 | 181 | 180
2017-03-30 04:30 | 186 | 185
2017-03-30 05:00 | 195 | 194
2017-03-30 05:30 | 210 | 209
2017-03-30 06:00 | 225 | 225
2017-03-30 06:30 | 251 | 250
2017-03-30 07:00 | 276 | 274
2017-03-30 07:30 | 300 | 299
2017-03-30 08:00 | 310 | 310
2017-03-30 08:30 | 316 | 316
2017-03-30 09:00 | 322 | 321
2017-03-30 09:30 | 325 | 325
2017-03-30 10:00 | 325 | 325
2017-03-30 10:30 | 321 | 321
2017-03-30 11:00 | 315 | 315
2017-03-30 11:30 | 301 | 301
2017-03-30 12:00 | 297 | 297
2017-03-30 12:30 | 300 | 300
2017-03-30 13:00 | 295 | 295
2017-03-30 13:30 | 289 | 289
2017-03-30 14:00 | 287 | 287
2017-03-30 14:30 | 285 | 285
2017-03-30 15:00 | 281 | 281
2017-03-30 15:30 | 279 | 279
2017-03-30 16:00 | 279 | 279
2017-03-30 16:30 | 281 | 281
2017-03-30 17:00 | 286 | 286
2017-03-30 17:30 | 289 | 289
2017-03-30 18:00 | 293 | 293
2017-03-30 18:30 | 295 | 294
2017-03-30 19:00 | 296 | 296
2017-03-30 19:30 | 285 | 285
2017-03-30 20:00 | 280 | 279
2017-03-30 20:30 | 270 | 270
2017-03-30 21:00 | 254 | 253
2017-03-30 21:30 | 238 | 237
2017-03-30 22:00 | 227 | 227
2017-03-30 22:30 | 220 | 219
2017-03-30 23:00 | 215 | 214
2017-03-30 23:30 | 201 | 200
2017-03-31 | 187 | 186
2017-03-31 00:30 | 174 | 174
2017-03-31 01:00 | 168 | 168
2017-03-31 01:30 | 161 | 161
2017-03-31 02:00 | 158 | 158
2017-03-31 02:30 | 158 | 157
2017-03-31 03:00 | 157 | 157
2017-03-31 03:30 | 155 | 155
2017-03-31 04:00 | 154 | 154
2017-03-31 04:30 | 156 | 156
2017-03-31 05:00 | 161 | 161
2017-03-31 05:30 | 172 | 171
2017-03-31 06:00 | 181 | 180
2017-03-31 06:30 | 194 | 193
2017-03-31 07:00 | 210 | 210
2017-03-31 07:30 | 224 | 224
2017-03-31 08:00 | 230 | 230
2017-03-31 08:30 | 230 | 230
2017-03-31 09:00 | 228 | 228
2017-03-31 09:30 | 224 | 223
2017-03-31 10:00 | 218 | 218
2017-03-31 10:30 | 219 | 218
2017-03-31 11:00 | 216 | 216
2017-03-31 11:30 | 215 | 215
2017-03-31 12:00 | 218 | 218
2017-03-31 12:30 | 223 | 223
2017-03-31 13:00 | 237 | 236
2017-03-31 13:30 | 251 | 250
2017-03-31 14:00 | 258 | 257
2017-03-31 14:30 | 260 | 259
2017-03-31 15:00 | 262 | 261
2017-03-31 15:30 | 259 | 259
2017-03-31 16:00 | 257 | 257
2017-03-31 16:30 | 255 | 255
2017-03-31 17:00 | 265 | 265
2017-03-31 17:30 | 265 | 265
2017-03-31 18:00 | 265 | 265
2017-03-31 18:30 | 268 | 268
2017-03-31 19:00 | 270 | 270
2017-03-31 19:30 | 263 | 263
2017-03-31 20:00 | 259 | 259
2017-03-31 20:30 | 255 | 254
2017-03-31 21:00 | 245 | 245
2017-03-31 21:30 | 236 | 236
2017-03-31 22:00 | 226 | 224
2017-03-31 22:30 | 223 | 222
2017-03-31 23:00 | 221 | 220
2017-03-31 23:30 | 205 | 205
2017-04-01 | 187 | 187
2017-04-01 00:30 | 173 | 173
2017-04-01 01:00 | 164 | 164
2017-04-01 01:30 | 158 | 158
2017-04-01 02:00 | 154 | 154
2017-04-01 02:30 | 150 | 150
2017-04-01 03:00 | 148 | 148
2017-04-01 03:30 | 148 | 148
2017-04-01 04:00 | 147 | 147
2017-04-01 04:30 | 148 | 148
2017-04-01 05:00 | 150 | 150
2017-04-01 05:30 | 156 | 155
2017-04-01 06:00 | 159 | 159
2017-04-01 06:30 | 163 | 163
2017-04-01 07:00 | 169 | 168
2017-04-01 07:30 | 175 | 174
2017-04-01 08:00 | 177 | 176
2017-04-01 08:30 | 181 | 179
2017-04-01 09:00 | 182 | 179
2017-04-01 09:30 | 181 | 178
2017-04-01 10:00 | 179 | 176
2017-04-01 10:30 | 176 | 174
2017-04-01 11:00 | 173 | 171
2017-04-01 11:30 | 171 | 168
2017-04-01 12:00 | 171 | 169
2017-04-01 12:30 | 172 | 170
2017-04-01 13:00 | 176 | 174
2017-04-01 13:30 | 182 | 179
2017-04-01 14:00 | 189 | 186
2017-04-01 14:30 | 199 | 196
2017-04-01 15:00 | 205 | 203
2017-04-01 15:30 | 212 | 211
2017-04-01 16:00 | 221 | 220
2017-04-01 16:30 | 230 | 229
2017-04-01 17:00 | 237 | 236
2017-04-01 17:30 | 236 | 235
2017-04-01 18:00 | 239 | 238
2017-04-01 18:30 | 246 | 245
2017-04-01 19:00 | 248 | 247
2017-04-01 19:30 | 242 | 241
2017-04-01 20:00 | 240 | 239
2017-04-01 20:30 | 234 | 233
2017-04-01 21:00 | 222 | 222
2017-04-01 21:30 | 217 | 216
2017-04-01 22:00 | 211 | 211
2017-04-01 22:30 | 211 | 211
2017-04-01 23:00 | 211 | 211
2017-04-01 23:30 | 199 | 198
2017-04-02 | 184 | 184
2017-04-02 00:30 | 170 | 170
2017-04-02 01:00 | 162 | 162
2017-04-02 01:30 | 156 | 156
2017-04-02 02:00 | 151 | 151
2017-04-02 02:30 | 148 | 148
2017-04-02 03:00 | 146 | 146
2017-04-02 03:30 | 145 | 145
2017-04-02 04:00 | 144 | 144
2017-04-02 04:30 | 143 | 143
2017-04-02 05:00 | 144 | 144
2017-04-02 05:30 | 147 | 147
2017-04-02 06:00 | 150 | 150
2017-04-02 06:30 | 153 | 152
2017-04-02 07:00 | 155 | 154
2017-04-02 07:30 | 159 | 159
2017-04-02 08:00 | 162 | 162
2017-04-02 08:30 | 171 | 171
2017-04-02 09:00 | 181 | 181
2017-04-02 09:30 | 189 | 189
2017-04-02 10:00 | 202 | 201
2017-04-02 10:30 | 204 | 203
2017-04-02 11:00 | 200 | 199
2017-04-02 11:30 | 187 | 187
2017-04-02 12:00 | 175 | 175
2017-04-02 12:30 | 170 | 170
2017-04-02 13:00 | 169 | 169
2017-04-02 13:30 | 173 | 173
2017-04-02 14:00 | 183 | 182
2017-04-02 14:30 | 187 | 187
2017-04-02 15:00 | 183 | 183
2017-04-02 15:30 | 190 | 189
2017-04-02 16:00 | 202 | 201
2017-04-02 16:30 | 217 | 216
2017-04-02 17:00 | 226 | 225
2017-04-02 17:30 | 233 | 232
2017-04-02 18:00 | 242 | 241
2017-04-02 18:30 | 253 | 251
2017-04-02 19:00 | 253 | 252
2017-04-02 19:30 | 243 | 242
2017-04-02 20:00 | 239 | 238
2017-04-02 20:30 | 235 | 234
2017-04-02 21:00 | 223 | 223
2017-04-02 21:30 | 216 | 215
2017-04-02 22:00 | 209 | 208
2017-04-02 22:30 | 207 | 207
2017-04-02 23:00 | 206 | 205
2017-04-02 23:30 | 194 | 194
2017-04-03 | 177 | 177
2017-04-03 00:30 | 162 | 162
2017-04-03 01:00 | 154 | 154
2017-04-03 01:30 | 149 | 149
2017-04-03 02:00 | 146 | 145
2017-04-03 02:30 | 144 | 144
2017-04-03 03:00 | 143 | 143
2017-04-03 03:30 | 143 | 143
2017-04-03 04:00 | 145 | 144
2017-04-03 04:30 | 149 | 148
2017-04-03 05:00 | 155 | 154
2017-04-03 05:30 | 169 | 167
2017-04-03 06:00 | 181 | 178
2017-04-03 06:30 | 197 | 195
2017-04-03 07:00 | 209 | 208
2017-04-03 07:30 | 217 | 216
2017-04-03 08:00 | 219 | 218
2017-04-03 08:30 | 218 | 217
2017-04-03 09:00 | 218 | 216
2017-04-03 09:30 | 227 | 225
2017-04-03 10:00 | 236 | 234
2017-04-03 10:30 | 227 | 224
2017-04-03 11:00 | 218 | 215
2017-04-03 11:30 | 223 | 222
2017-04-03 12:00 | 229 | 228
2017-04-03 12:30 | 229 | 228
2017-04-03 13:00 | 220 | 219
2017-04-03 13:30 | 219 | 218
2017-04-03 14:00 | 242 | 240
2017-04-03 14:30 | 244 | 243
2017-04-03 15:00 | 240 | 239
2017-04-03 15:30 | 236 | 235
2017-04-03 16:00 | 246 | 246
2017-04-03 16:30 | 256 | 255
2017-04-03 17:00 | 264 | 263
2017-04-03 17:30 | 269 | 269
2017-04-03 18:00 | 273 | 272
2017-04-03 18:30 | 277 | 276
2017-04-03 19:00 | 278 | 276
2017-04-03 19:30 | 268 | 265
2017-04-03 20:00 | 263 | 259
2017-04-03 20:30 | 257 | 254
2017-04-03 21:00 | 242 | 240
2017-04-03 21:30 | 233 | 232
2017-04-03 22:00 | 224 | 222
2017-04-03 22:30 | 220 | 218
2017-04-03 23:00 | 218 | 217
2017-04-03 23:30 | 204 | 203
2017-04-04 | 186 | 185
2017-04-04 00:30 | 171 | 170
2017-04-04 01:00 | 162 | 161
2017-04-04 01:30 | 157 | 157
2017-04-04 02:00 | 152 | 152
2017-04-04 02:30 | 150 | 150
2017-04-04 03:00 | 148 | 148
2017-04-04 03:30 | 144 | 144
2017-04-04 04:00 | 146 | 146
2017-04-04 04:30 | 151 | 151
2017-04-04 05:00 | 159 | 159
2017-04-04 05:30 | 173 | 172
2017-04-04 06:00 | 184 | 183
2017-04-04 06:30 | 201 | 199
2017-04-04 07:00 | 212 | 211
2017-04-04 07:30 | 219 | 219
2017-04-04 08:00 | 221 | 220
2017-04-04 08:30 | 220 | 218
2017-04-04 09:00 | 218 | 215
2017-04-04 09:30 | 214 | 211
2017-04-04 10:00 | 222 | 218
2017-04-04 10:30 | 239 | 235
2017-04-04 11:00 | 226 | 225
2017-04-04 11:30 | 230 | 229
2017-04-04 12:00 | 237 | 237
2017-04-04 12:30 | 226 | 225
2017-04-04 13:00 | 234 | 234
2017-04-04 13:30 | 238 | 238
2017-04-04 14:00 | 238 | 238
2017-04-04 14:30 | 243 | 243
2017-04-04 15:00 | 237 | 236
2017-04-04 15:30 | 240 | 239
2017-04-04 16:00 | 248 | 248
2017-04-04 16:30 | 261 | 260
2017-04-04 17:00 | 268 | 267
2017-04-04 17:30 | 269 | 269
2017-04-04 18:00 | 271 | 270
2017-04-04 18:30 | 278 | 277
2017-04-04 19:00 | 280 | 280
2017-04-04 19:30 | 271 | 271
2017-04-04 20:00 | 266 | 266
2017-04-04 20:30 | 261 | 261
2017-04-04 21:00 | 247 | 247
2017-04-04 21:30 | 236 | 236
2017-04-04 22:00 | 226 | 226
2017-04-04 22:30 | 221 | 220
2017-04-04 23:00 | 220 | 219
2017-04-04 23:30 | 206 | 205
2017-04-05 | 188 | 187
2017-04-05 00:30 | 172 | 171
2017-04-05 01:00 | 164 | 164
2017-04-05 01:30 | 158 | 158
2017-04-05 02:00 | 154 | 154
2017-04-05 02:30 | 152 | 151
2017-04-05 03:00 | 150 | 150
2017-04-05 03:30 | 151 | 151
2017-04-05 04:00 | 152 | 152
2017-04-05 04:30 | 155 | 155
2017-04-05 05:00 | 163 | 163
2017-04-05 05:30 | 177 | 177
2017-04-05 06:00 | 189 | 188
2017-04-05 06:30 | 205 | 204
2017-04-05 07:00 | 217 | 217
2017-04-05 07:30 | 220 | 219
2017-04-05 08:00 | 221 | 221
2017-04-05 08:30 | 228 | 228
2017-04-05 09:00 | 221 | 220
2017-04-05 09:30 | 223 | 221
2017-04-05 10:00 | 224 | 222
2017-04-05 10:30 | 221 | 219
2017-04-05 11:00 | 223 | 222
2017-04-05 11:30 | 224 | 222
2017-04-05 12:00 | 218 | 217
2017-04-05 12:30 | 216 | 215
2017-04-05 13:00 | 221 | 220
2017-04-05 13:30 | 223 | 222
2017-04-05 14:00 | 226 | 225
2017-04-05 14:30 | 233 | 231
2017-04-05 15:00 | 238 | 237
2017-04-05 15:30 | 247 | 246
2017-04-05 16:00 | 251 | 250
2017-04-05 16:30 | 255 | 255
2017-04-05 17:00 | 262 | 261
2017-04-05 17:30 | 268 | 268
2017-04-05 18:00 | 271 | 271
2017-04-05 18:30 | 275 | 274
2017-04-05 19:00 | 277 | 276
2017-04-05 19:30 | 269 | 267
2017-04-05 20:00 | 265 | 262
2017-04-05 20:30 | 259 | 257
2017-04-05 21:00 | 245 | 244
2017-04-05 21:30 | 242 | 242
2017-04-05 22:00 | 241 | 241
2017-04-05 22:30 | 237 | 237
2017-04-05 23:00 | 235 | 235
2017-04-05 23:30 | 220 | 219
2017-04-06 | 203 | 203
2017-04-06 00:30 | 186 | 186
2017-04-06 01:00 | 177 | 177
2017-04-06 01:30 | 172 | 171
2017-04-06 02:00 | 167 | 167
2017-04-06 02:30 | 158 | 158
2017-04-06 03:00 | 153 | 152
2017-04-06 03:30 | 153 | 152
2017-04-06 04:00 | 154 | 153
2017-04-06 04:30 | 158 | 157
2017-04-06 05:00 | 165 | 164
2017-04-06 05:30 | 179 | 177
2017-04-06 06:00 | 193 | 193
2017-04-06 06:30 | 209 | 209
2017-04-06 07:00 | 224 | 224
2017-04-06 07:30 | 235 | 235
2017-04-06 08:00 | 238 | 238
2017-04-06 08:30 | 238 | 237
2017-04-06 09:00 | 233 | 233
2017-04-06 09:30 | 242 | 242
2017-04-06 10:00 | 237 | 237
2017-04-06 10:30 | 243 | 243
2017-04-06 11:00 | 244 | 244
2017-04-06 11:30 | 239 | 239
2017-04-06 12:00 | 239 | 239
2017-04-06 12:30 | 237 | 237
2017-04-06 13:00 | 238 | 238
2017-04-06 13:30 | 240 | 240
2017-04-06 14:00 | 244 | 244
2017-04-06 14:30 | 248 | 248
2017-04-06 15:00 | 248 | 248
2017-04-06 15:30 | 251 | 251
2017-04-06 16:00 | 256 | 255
2017-04-06 16:30 | 257 | 257
2017-04-06 17:00 | 266 | 266
2017-04-06 17:30 | 271 | 271
2017-04-06 18:00 | 278 | 277
2017-04-06 18:30 | 281 | 281
2017-04-06 19:00 | 284 | 283
2017-04-06 19:30 | 275 | 275
2017-04-06 20:00 | 271 | 271
2017-04-06 20:30 | 264 | 264
2017-04-06 21:00 | 251 | 251
2017-04-06 21:30 | 238 | 238
2017-04-06 22:00 | 228 | 228
2017-04-06 22:30 | 224 | 224
2017-04-06 23:00 | 223 | 222
2017-04-06 23:30 | 209 | 208
2017-04-07 | 190 | 190
2017-04-07 00:30 | 174 | 174
2017-04-07 01:00 | 165 | 164
2017-04-07 01:30 | 159 | 159
2017-04-07 02:00 | 156 | 156
2017-04-07 02:30 | 154 | 154
2017-04-07 03:00 | 152 | 152
2017-04-07 03:30 | 153 | 152
2017-04-07 04:00 | 153 | 153
2017-04-07 04:30 | 157 | 157
2017-04-07 05:00 | 165 | 164
2017-04-07 05:30 | 177 | 176
2017-04-07 06:00 | 189 | 188
2017-04-07 06:30 | 204 | 203
2017-04-07 07:00 | 216 | 216
2017-04-07 07:30 | 225 | 223
2017-04-07 08:00 | 225 | 224
2017-04-07 08:30 | 222 | 220
2017-04-07 09:00 | 217 | 215
2017-04-07 09:30 | 216 | 214
2017-04-07 10:00 | 218 | 215
2017-04-07 10:30 | 216 | 213
2017-04-07 11:00 | 211 | 210
2017-04-07 11:30 | 206 | 205
2017-04-07 12:00 | 206 | 205
2017-04-07 12:30 | 207 | 207
2017-04-07 13:00 | 211 | 210
2017-04-07 13:30 | 209 | 208
2017-04-07 14:00 | 210 | 210
2017-04-07 14:30 | 215 | 214
2017-04-07 15:00 | 219 | 218
2017-04-07 15:30 | 222 | 221
2017-04-07 16:00 | 233 | 232
2017-04-07 16:30 | 242 | 241
2017-04-07 17:00 | 248 | 248
2017-04-07 17:30 | 250 | 250
2017-04-07 18:00 | 251 | 251
2017-04-07 18:30 | 256 | 255
2017-04-07 19:00 | 258 | 257
2017-04-07 19:30 | 249 | 249
2017-04-07 20:00 | 246 | 246
2017-04-07 20:30 | 240 | 240
2017-04-07 21:00 | 228 | 228
2017-04-07 21:30 | 221 | 221
2017-04-07 22:00 | 212 | 212
2017-04-07 22:30 | 210 | 210
2017-04-07 23:00 | 210 | 209
2017-04-07 23:30 | 196 | 196
2017-04-08 | 180 | 180
2017-04-08 00:30 | 166 | 166
2017-04-08 01:00 | 157 | 157
2017-04-08 01:30 | 150 | 150
2017-04-08 02:00 | 146 | 146
2017-04-08 02:30 | 143 | 143
2017-04-08 03:00 | 141 | 141
2017-04-08 03:30 | 139 | 139
2017-04-08 04:00 | 139 | 139
2017-04-08 04:30 | 141 | 141
2017-04-08 05:00 | 144 | 143
2017-04-08 05:30 | 148 | 148
2017-04-08 06:00 | 154 | 154
2017-04-08 06:30 | 163 | 163
2017-04-08 07:00 | 167 | 167
2017-04-08 07:30 | 172 | 172
2017-04-08 08:00 | 175 | 175
2017-04-08 08:30 | 176 | 176
2017-04-08 09:00 | 177 | 177
2017-04-08 09:30 | 177 | 177
2017-04-08 10:00 | 183 | 183
2017-04-08 10:30 | 178 | 178
2017-04-08 11:00 | 172 | 171
2017-04-08 11:30 | 174 | 174
2017-04-08 12:00 | 176 | 175
2017-04-08 12:30 | 176 | 176
2017-04-08 13:00 | 178 | 178
2017-04-08 13:30 | 180 | 180
2017-04-08 14:00 | 180 | 180
2017-04-08 14:30 | 175 | 174
2017-04-08 15:00 | 184 | 184
2017-04-08 15:30 | 195 | 194
2017-04-08 16:00 | 202 | 202
2017-04-08 16:30 | 208 | 207
2017-04-08 17:00 | 216 | 216
2017-04-08 17:30 | 218 | 218
2017-04-08 18:00 | 224 | 224
2017-04-08 18:30 | 233 | 232
2017-04-08 19:00 | 232 | 232
2017-04-08 19:30 | 226 | 225
2017-04-08 20:00 | 229 | 228
2017-04-08 20:30 | 235 | 235
2017-04-08 21:00 | 224 | 224
2017-04-08 21:30 | 216 | 215
2017-04-08 22:00 | 209 | 209
2017-04-08 22:30 | 208 | 208
2017-04-08 23:00 | 209 | 209
2017-04-08 23:30 | 185 | 185
2017-04-09 | 170 | 170
2017-04-09 00:30 | 159 | 158
2017-04-09 01:00 | 151 | 151
2017-04-09 01:30 | 146 | 145
2017-04-09 02:00 | 141 | 141
2017-04-09 02:30 | 139 | 138
2017-04-09 03:00 | 136 | 136
2017-04-09 03:30 | 137 | 136
2017-04-09 04:00 | 134 | 133
2017-04-09 04:30 | 133 | 133
2017-04-09 05:00 | 134 | 134
2017-04-09 05:30 | 137 | 136
2017-04-09 06:00 | 141 | 140
2017-04-09 06:30 | 144 | 144
2017-04-09 07:00 | 147 | 146
2017-04-09 07:30 | 151 | 151
2017-04-09 08:00 | 153 | 153
2017-04-09 08:30 | 156 | 156
2017-04-09 09:00 | 155 | 155
2017-04-09 09:30 | 155 | 155
2017-04-09 10:00 | 155 | 155
2017-04-09 10:30 | 159 | 159
2017-04-09 11:00 | 162 | 162
2017-04-09 11:30 | 162 | 161
2017-04-09 12:00 | 163 | 162
2017-04-09 12:30 | 169 | 168
2017-04-09 13:00 | 169 | 169
2017-04-09 13:30 | 173 | 173
2017-04-09 14:00 | 180 | 179
2017-04-09 14:30 | 184 | 183
2017-04-09 15:00 | 188 | 187
2017-04-09 15:30 | 194 | 193
2017-04-09 16:00 | 207 | 206
2017-04-09 16:30 | 214 | 213
2017-04-09 17:00 | 223 | 223
2017-04-09 17:30 | 230 | 229
2017-04-09 18:00 | 238 | 238
2017-04-09 18:30 | 250 | 250
2017-04-09 19:00 | 248 | 248
2017-04-09 19:30 | 240 | 240
2017-04-09 20:00 | 237 | 237
2017-04-09 20:30 | 232 | 232
2017-04-09 21:00 | 219 | 219
2017-04-09 21:30 | 210 | 210
2017-04-09 22:00 | 204 | 204
2017-04-09 22:30 | 202 | 201
2017-04-09 23:00 | 203 | 203
2017-04-09 23:30 | 191 | 191
2017-04-10 | 176 | 176
2017-04-10 00:30 | 162 | 162
2017-04-10 01:00 | 154 | 154
2017-04-10 01:30 | 150 | 150
2017-04-10 02:00 | 147 | 147
2017-04-10 02:30 | 146 | 146
2017-04-10 03:00 | 145 | 145
2017-04-10 03:30 | 145 | 145
2017-04-10 04:00 | 146 | 146
2017-04-10 04:30 | 150 | 150
2017-04-10 05:00 | 158 | 158
2017-04-10 05:30 | 171 | 171
2017-04-10 06:00 | 184 | 183
2017-04-10 06:30 | 200 | 199
2017-04-10 07:00 | 211 | 210
2017-04-10 07:30 | 221 | 220
2017-04-10 08:00 | 224 | 223
2017-04-10 08:30 | 223 | 222
2017-04-10 09:00 | 222 | 221
2017-04-10 09:30 | 220 | 219
2017-04-10 10:00 | 218 | 218
2017-04-10 10:30 | 223 | 223
2017-04-10 11:00 | 216 | 216
2017-04-10 11:30 | 217 | 217
2017-04-10 12:00 | 220 | 220
2017-04-10 12:30 | 220 | 220
2017-04-10 13:00 | 223 | 223
2017-04-10 13:30 | 224 | 224
2017-04-10 14:00 | 230 | 230
2017-04-10 14:30 | 236 | 236
2017-04-10 15:00 | 243 | 243
2017-04-10 15:30 | 251 | 250
2017-04-10 16:00 | 259 | 259
2017-04-10 16:30 | 266 | 266
2017-04-10 17:00 | 274 | 274
2017-04-10 17:30 | 274 | 274
2017-04-10 18:00 | 275 | 275
2017-04-10 18:30 | 279 | 279
2017-04-10 19:00 | 278 | 278
2017-04-10 19:30 | 268 | 267
2017-04-10 20:00 | 262 | 262
2017-04-10 20:30 | 258 | 258
2017-04-10 21:00 | 245 | 245
2017-04-10 21:30 | 234 | 234
2017-04-10 22:00 | 224 | 224
2017-04-10 22:30 | 220 | 220
2017-04-10 23:00 | 218 | 218
2017-04-10 23:30 | 203 | 203
2017-04-11 | 187 | 186
2017-04-11 00:30 | 169 | 169
2017-04-11 01:00 | 162 | 162
2017-04-11 01:30 | 155 | 155
2017-04-11 02:00 | 151 | 151
2017-04-11 02:30 | 148 | 148
2017-04-11 03:00 | 146 | 146
2017-04-11 03:30 | 146 | 146
2017-04-11 04:00 | 147 | 146
2017-04-11 04:30 | 150 | 150
2017-04-11 05:00 | 158 | 158
2017-04-11 05:30 | 172 | 172
2017-04-11 06:00 | 183 | 183
2017-04-11 06:30 | 200 | 199
2017-04-11 07:00 | 212 | 211
2017-04-11 07:30 | 219 | 218
2017-04-11 08:00 | 219 | 217
2017-04-11 08:30 | 215 | 213
2017-04-11 09:00 | 207 | 206
2017-04-11 09:30 | 203 | 203
2017-04-11 10:00 | 202 | 202
2017-04-11 10:30 | 194 | 194
2017-04-11 11:00 | 192 | 191
2017-04-11 11:30 | 190 | 189
2017-04-11 12:00 | 192 | 191
2017-04-11 12:30 | 195 | 195
2017-04-11 13:00 | 198 | 198
2017-04-11 13:30 | 202 | 202
2017-04-11 14:00 | 209 | 209
2017-04-11 14:30 | 216 | 216
2017-04-11 15:00 | 225 | 225
2017-04-11 15:30 | 233 | 233
2017-04-11 16:00 | 244 | 244
2017-04-11 16:30 | 253 | 253
2017-04-11 17:00 | 263 | 263
2017-04-11 17:30 | 268 | 268
2017-04-11 18:00 | 273 | 273
2017-04-11 18:30 | 277 | 277
2017-04-11 19:00 | 276 | 276
2017-04-11 19:30 | 268 | 268
2017-04-11 20:00 | 263 | 263
2017-04-11 20:30 | 259 | 259
2017-04-11 21:00 | 245 | 245
2017-04-11 21:30 | 234 | 234
2017-04-11 22:00 | 225 | 225
2017-04-11 22:30 | 220 | 220
2017-04-11 23:00 | 219 | 219
2017-04-11 23:30 | 206 | 205
2017-04-12 | 189 | 188
2017-04-12 00:30 | 174 | 173
2017-04-12 01:00 | 166 | 166
2017-04-12 01:30 | 160 | 160
2017-04-12 02:00 | 156 | 156
2017-04-12 02:30 | 153 | 153
2017-04-12 03:00 | 150 | 150
2017-04-12 03:30 | 150 | 150
2017-04-12 04:00 | 151 | 151
2017-04-12 04:30 | 156 | 156
2017-04-12 05:00 | 163 | 162
2017-04-12 05:30 | 175 | 175
2017-04-12 06:00 | 189 | 187
2017-04-12 06:30 | 204 | 203
2017-04-12 07:00 | 214 | 214
2017-04-12 07:30 | 222 | 222
2017-04-12 08:00 | 223 | 222
2017-04-12 08:30 | 219 | 219
2017-04-12 09:00 | 230 | 229
2017-04-12 09:30 | 212 | 211
2017-04-12 10:00 | 205 | 204
2017-04-12 10:30 | 215 | 215
2017-04-12 11:00 | 214 | 213
2017-04-12 11:30 | 214 | 214
2017-04-12 12:00 | 217 | 216
2017-04-12 12:30 | 220 | 220
2017-04-12 13:00 | 225 | 225
2017-04-12 13:30 | 232 | 232
2017-04-12 14:00 | 237 | 236
2017-04-12 14:30 | 242 | 241
2017-04-12 15:00 | 248 | 248
2017-04-12 15:30 | 256 | 256
2017-04-12 16:00 | 264 | 264
2017-04-12 16:30 | 269 | 269
2017-04-12 17:00 | 274 | 274
2017-04-12 17:30 | 275 | 275
2017-04-12 18:00 | 277 | 277
2017-04-12 18:30 | 280 | 279
2017-04-12 19:00 | 279 | 279
2017-04-12 19:30 | 271 | 270
2017-04-12 20:00 | 267 | 266
2017-04-12 20:30 | 262 | 261
2017-04-12 21:00 | 249 | 249
2017-04-12 21:30 | 239 | 239
2017-04-12 22:00 | 229 | 229
2017-04-12 22:30 | 225 | 225
2017-04-12 23:00 | 224 | 223
2017-04-12 23:30 | 207 | 207
2017-04-13 | 191 | 191
2017-04-13 00:30 | 175 | 175
2017-04-13 01:00 | 166 | 166
2017-04-13 01:30 | 161 | 161
2017-04-13 02:00 | 157 | 157
2017-04-13 02:30 | 155 | 155
2017-04-13 03:00 | 153 | 153
2017-04-13 03:30 | 153 | 153
2017-04-13 04:00 | 154 | 154
2017-04-13 04:30 | 158 | 158
2017-04-13 05:00 | 165 | 165
2017-04-13 05:30 | 177 | 177
2017-04-13 06:00 | 189 | 189
2017-04-13 06:30 | 204 | 204
2017-04-13 07:00 | 217 | 216
2017-04-13 07:30 | 224 | 224
2017-04-13 08:00 | 227 | 226
2017-04-13 08:30 | 227 | 227
2017-04-13 09:00 | 222 | 222
2017-04-13 09:30 | 219 | 219
2017-04-13 10:00 | 219 | 219
2017-04-13 10:30 | 219 | 219
2017-04-13 11:00 | 220 | 220
2017-04-13 11:30 | 220 | 220
2017-04-13 12:00 | 226 | 225
2017-04-13 12:30 | 231 | 231
2017-04-13 13:00 | 233 | 233
2017-04-13 13:30 | 235 | 234
2017-04-13 14:00 | 231 | 231
2017-04-13 14:30 | 233 | 233
2017-04-13 15:00 | 236 | 236
2017-04-13 15:30 | 242 | 242
2017-04-13 16:00 | 246 | 246
2017-04-13 16:30 | 252 | 252
2017-04-13 17:00 | 259 | 259
2017-04-13 17:30 | 262 | 262
2017-04-13 18:00 | 266 | 266
2017-04-13 18:30 | 269 | 269
2017-04-13 19:00 | 269 | 269
2017-04-13 19:30 | 263 | 263
2017-04-13 20:00 | 258 | 258
2017-04-13 20:30 | 254 | 253
2017-04-13 21:00 | 242 | 241
2017-04-13 21:30 | 230 | 229
2017-04-13 22:00 | 222 | 222
2017-04-13 22:30 | 218 | 218
2017-04-13 23:00 | 217 | 217
2017-04-13 23:30 | 203 | 203
2017-04-14 | 186 | 185
2017-04-14 00:30 | 170 | 170
2017-04-14 01:00 | 161 | 161
2017-04-14 01:30 | 155 | 155
2017-04-14 02:00 | 150 | 150
2017-04-14 02:30 | 147 | 147
2017-04-14 03:00 | 145 | 145
2017-04-14 03:30 | 144 | 144
2017-04-14 04:00 | 142 | 142
2017-04-14 04:30 | 142 | 142
2017-04-14 05:00 | 142 | 142
2017-04-14 05:30 | 145 | 145
2017-04-14 06:00 | 149 | 149
2017-04-14 06:30 | 153 | 153
2017-04-14 07:00 | 156 | 156
2017-04-14 07:30 | 162 | 161
2017-04-14 08:00 | 169 | 169
2017-04-14 08:30 | 168 | 168
2017-04-14 09:00 | 171 | 171
2017-04-14 09:30 | 174 | 173
2017-04-14 10:00 | 169 | 169
2017-04-14 10:30 | 166 | 166
2017-04-14 11:00 | 163 | 163
2017-04-14 11:30 | 159 | 159
2017-04-14 12:00 | 159 | 159
2017-04-14 12:30 | 156 | 156
2017-04-14 13:00 | 163 | 163
2017-04-14 13:30 | 162 | 162
2017-04-14 14:00 | 163 | 163
2017-04-14 14:30 | 162 | 162
2017-04-14 15:00 | 170 | 170
2017-04-14 15:30 | 179 | 179
2017-04-14 16:00 | 187 | 187
2017-04-14 16:30 | 194 | 194
2017-04-14 17:00 | 203 | 203
2017-04-14 17:30 | 211 | 211
2017-04-14 18:00 | 221 | 220
2017-04-14 18:30 | 227 | 227
2017-04-14 19:00 | 225 | 225
2017-04-14 19:30 | 216 | 216
2017-04-14 20:00 | 213 | 213
2017-04-14 20:30 | 210 | 210
2017-04-14 21:00 | 203 | 203
2017-04-14 21:30 | 197 | 197
2017-04-14 22:00 | 193 | 193
2017-04-14 22:30 | 194 | 194
2017-04-14 23:00 | 197 | 197
2017-04-14 23:30 | 187 | 187
2017-04-15 | 173 | 173
2017-04-15 00:30 | 160 | 160
2017-04-15 01:00 | 152 | 151
2017-04-15 01:30 | 146 | 145
2017-04-15 02:00 | 142 | 142
2017-04-15 02:30 | 141 | 140
2017-04-15 03:00 | 138 | 138
2017-04-15 03:30 | 138 | 137
2017-04-15 04:00 | 137 | 136
2017-04-15 04:30 | 138 | 138
2017-04-15 05:00 | 140 | 139
2017-04-15 05:30 | 143 | 142
2017-04-15 06:00 | 146 | 146
2017-04-15 06:30 | 151 | 150
2017-04-15 07:00 | 154 | 154
2017-04-15 07:30 | 158 | 158
2017-04-15 08:00 | 160 | 159
2017-04-15 08:30 | 163 | 163
2017-04-15 09:00 | 168 | 168
2017-04-15 09:30 | 170 | 169
2017-04-15 10:00 | 162 | 162
2017-04-15 10:30 | 157 | 157
2017-04-15 11:00 | 158 | 158
2017-04-15 11:30 | 160 | 160
2017-04-15 12:00 | 164 | 163
2017-04-15 12:30 | 162 | 162
2017-04-15 13:00 | 166 | 165
2017-04-15 13:30 | 166 | 166
2017-04-15 14:00 | 165 | 165
2017-04-15 14:30 | 171 | 170
2017-04-15 15:00 | 176 | 176
2017-04-15 15:30 | 187 | 186
2017-04-15 16:00 | 195 | 194
2017-04-15 16:30 | 201 | 201
2017-04-15 17:00 | 211 | 210
2017-04-15 17:30 | 215 | 214
2017-04-15 18:00 | 223 | 223
2017-04-15 18:30 | 229 | 229
2017-04-15 19:00 | 227 | 227
2017-04-15 19:30 | 221 | 221
2017-04-15 20:00 | 217 | 217
2017-04-15 20:30 | 216 | 215
2017-04-15 21:00 | 206 | 206
2017-04-15 21:30 | 201 | 200
2017-04-15 22:00 | 197 | 197
2017-04-15 22:30 | 197 | 197
2017-04-15 23:00 | 199 | 199
2017-04-15 23:30 | 188 | 188
2017-04-16 | 173 | 173
2017-04-16 00:30 | 160 | 160
2017-04-16 01:00 | 153 | 152
2017-04-16 01:30 | 147 | 147
2017-04-16 02:00 | 142 | 142
2017-04-16 02:30 | 140 | 140
2017-04-16 03:00 | 138 | 138
2017-04-16 03:30 | 138 | 138
2017-04-16 04:00 | 137 | 137
2017-04-16 04:30 | 136 | 136
2017-04-16 05:00 | 137 | 137
2017-04-16 05:30 | 140 | 140
2017-04-16 06:00 | 143 | 143
2017-04-16 06:30 | 147 | 147
2017-04-16 07:00 | 149 | 149
2017-04-16 07:30 | 153 | 153
2017-04-16 08:00 | 153 | 153
2017-04-16 08:30 | 155 | 154
2017-04-16 09:00 | 153 | 153
2017-04-16 09:30 | 161 | 160
2017-04-16 10:00 | 157 | 156
2017-04-16 10:30 | 159 | 158
2017-04-16 11:00 | 155 | 154
2017-04-16 11:30 | 156 | 155
2017-04-16 12:00 | 151 | 150
2017-04-16 12:30 | 152 | 151
2017-04-16 13:00 | 149 | 148
2017-04-16 13:30 | 151 | 150
2017-04-16 14:00 | 151 | 151
2017-04-16 14:30 | 154 | 153
2017-04-16 15:00 | 161 | 160
2017-04-16 15:30 | 171 | 169
2017-04-16 16:00 | 182 | 181
2017-04-16 16:30 | 194 | 192
2017-04-16 17:00 | 205 | 204
2017-04-16 17:30 | 210 | 210
2017-04-16 18:00 | 219 | 219
2017-04-16 18:30 | 225 | 224
2017-04-16 19:00 | 224 | 224
2017-04-16 19:30 | 218 | 217
2017-04-16 20:00 | 216 | 216
2017-04-16 20:30 | 214 | 213
2017-04-16 21:00 | 205 | 205
2017-04-16 21:30 | 199 | 199
2017-04-16 22:00 | 194 | 194
2017-04-16 22:30 | 194 | 194
2017-04-16 23:00 | 196 | 196
2017-04-16 23:30 | 185 | 185
2017-04-17 | 171 | 171
2017-04-17 00:30 | 158 | 158
2017-04-17 01:00 | 152 | 152
2017-04-17 01:30 | 147 | 146
2017-04-17 02:00 | 142 | 141
2017-04-17 02:30 | 140 | 140
2017-04-17 03:00 | 138 | 138
2017-04-17 03:30 | 137 | 137
2017-04-17 04:00 | 136 | 136
2017-04-17 04:30 | 137 | 137
2017-04-17 05:00 | 138 | 138
2017-04-17 05:30 | 142 | 142
2017-04-17 06:00 | 147 | 147
2017-04-17 06:30 | 151 | 151
2017-04-17 07:00 | 154 | 154
2017-04-17 07:30 | 158 | 158
2017-04-17 08:00 | 160 | 160
2017-04-17 08:30 | 163 | 163
2017-04-17 09:00 | 164 | 163
2017-04-17 09:30 | 165 | 164
2017-04-17 10:00 | 166 | 164
2017-04-17 10:30 | 166 | 165
2017-04-17 11:00 | 166 | 165
2017-04-17 11:30 | 167 | 166
2017-04-17 12:00 | 168 | 167
2017-04-17 12:30 | 173 | 172
2017-04-17 13:00 | 178 | 177
2017-04-17 13:30 | 183 | 182
2017-04-17 14:00 | 186 | 185
2017-04-17 14:30 | 188 | 188
2017-04-17 15:00 | 192 | 191
2017-04-17 15:30 | 202 | 201
2017-04-17 16:00 | 215 | 214
2017-04-17 16:30 | 224 | 223
2017-04-17 17:00 | 233 | 232
2017-04-17 17:30 | 239 | 238
2017-04-17 18:00 | 250 | 248
2017-04-17 18:30 | 251 | 250
2017-04-17 19:00 | 248 | 247
2017-04-17 19:30 | 239 | 239
2017-04-17 20:00 | 234 | 234
2017-04-17 20:30 | 231 | 230
2017-04-17 21:00 | 217 | 217
2017-04-17 21:30 | 210 | 210
2017-04-17 22:00 | 203 | 203
2017-04-17 22:30 | 201 | 200
2017-04-17 23:00 | 200 | 200
2017-04-17 23:30 | 190 | 190
2017-04-18 | 175 | 175
2017-04-18 00:30 | 160 | 160
2017-04-18 01:00 | 154 | 153
2017-04-18 01:30 | 149 | 148
2017-04-18 02:00 | 145 | 144
2017-04-18 02:30 | 143 | 143
2017-04-18 03:00 | 142 | 141
2017-04-18 03:30 | 142 | 141
2017-04-18 04:00 | 143 | 143
2017-04-18 04:30 | 148 | 147
2017-04-18 05:00 | 155 | 155
2017-04-18 05:30 | 169 | 169
2017-04-18 06:00 | 184 | 184
2017-04-18 06:30 | 205 | 205
2017-04-18 07:00 | 224 | 223
2017-04-18 07:30 | 233 | 232
2017-04-18 08:00 | 231 | 230
2017-04-18 08:30 | 227 | 225
2017-04-18 09:00 | 222 | 220
2017-04-18 09:30 | 222 | 220
2017-04-18 10:00 | 222 | 220
2017-04-18 10:30 | 222 | 219
2017-04-18 11:00 | 222 | 219
2017-04-18 11:30 | 221 | 219
2017-04-18 12:00 | 220 | 217
2017-04-18 12:30 | 220 | 218
2017-04-18 13:00 | 227 | 224
2017-04-18 13:30 | 229 | 226
2017-04-18 14:00 | 236 | 233
2017-04-18 14:30 | 246 | 244
2017-04-18 15:00 | 247 | 246
2017-04-18 15:30 | 249 | 248
2017-04-18 16:00 | 255 | 254
2017-04-18 16:30 | 260 | 259
2017-04-18 17:00 | 272 | 271
2017-04-18 17:30 | 278 | 277
2017-04-18 18:00 | 284 | 283
2017-04-18 18:30 | 283 | 282
2017-04-18 19:00 | 280 | 279
2017-04-18 19:30 | 271 | 270
2017-04-18 20:00 | 267 | 266
2017-04-18 20:30 | 262 | 261
2017-04-18 21:00 | 249 | 249
2017-04-18 21:30 | 237 | 236
2017-04-18 22:00 | 227 | 226
2017-04-18 22:30 | 222 | 221
2017-04-18 23:00 | 220 | 219
2017-04-18 23:30 | 205 | 205
2017-04-19 | 188 | 188
2017-04-19 00:30 | 174 | 173
2017-04-19 01:00 | 165 | 165
2017-04-19 01:30 | 160 | 160
2017-04-19 02:00 | 156 | 156
2017-04-19 02:30 | 153 | 153
2017-04-19 03:00 | 152 | 152
2017-04-19 03:30 | 152 | 152
2017-04-19 04:00 | 152 | 152
2017-04-19 04:30 | 156 | 156
2017-04-19 05:00 | 163 | 163
2017-04-19 05:30 | 176 | 176
2017-04-19 06:00 | 192 | 191
2017-04-19 06:30 | 211 | 210
2017-04-19 07:00 | 225 | 225
2017-04-19 07:30 | 235 | 234
2017-04-19 08:00 | 233 | 232
2017-04-19 08:30 | 225 | 224
2017-04-19 09:00 | 217 | 215
2017-04-19 09:30 | 216 | 214
2017-04-19 10:00 | 220 | 218
2017-04-19 10:30 | 223 | 221
2017-04-19 11:00 | 224 | 222
2017-04-19 11:30 | 223 | 222
2017-04-19 12:00 | 224 | 222
2017-04-19 12:30 | 214 | 213
2017-04-19 13:00 | 222 | 220
2017-04-19 13:30 | 219 | 217
2017-04-19 14:00 | 225 | 224
2017-04-19 14:30 | 229 | 229
2017-04-19 15:00 | 230 | 230
2017-04-19 15:30 | 239 | 239
2017-04-19 16:00 | 249 | 249
2017-04-19 16:30 | 260 | 260
2017-04-19 17:00 | 269 | 269
2017-04-19 17:30 | 273 | 273
2017-04-19 18:00 | 281 | 281
2017-04-19 18:30 | 282 | 282
2017-04-19 19:00 | 281 | 281
2017-04-19 19:30 | 272 | 272
2017-04-19 20:00 | 269 | 269
2017-04-19 20:30 | 265 | 265
2017-04-19 21:00 | 252 | 252
2017-04-19 21:30 | 239 | 238
2017-04-19 22:00 | 229 | 228
2017-04-19 22:30 | 223 | 223
2017-04-19 23:00 | 221 | 220
2017-04-19 23:30 | 206 | 206
2017-04-20 | 189 | 189
2017-04-20 00:30 | 173 | 173
2017-04-20 01:00 | 165 | 165
2017-04-20 01:30 | 159 | 159
2017-04-20 02:00 | 154 | 154
2017-04-20 02:30 | 153 | 153
2017-04-20 03:00 | 151 | 151
2017-04-20 03:30 | 151 | 151
2017-04-20 04:00 | 152 | 152
2017-04-20 04:30 | 156 | 156
2017-04-20 05:00 | 163 | 163
2017-04-20 05:30 | 176 | 176
2017-04-20 06:00 | 191 | 190
2017-04-20 06:30 | 210 | 209
2017-04-20 07:00 | 226 | 225
2017-04-20 07:30 | 238 | 236
2017-04-20 08:00 | 238 | 235
2017-04-20 08:30 | 233 | 229
2017-04-20 09:00 | 231 | 226
2017-04-20 09:30 | 228 | 225
2017-04-20 10:00 | 222 | 220
2017-04-20 10:30 | 219 | 219
2017-04-20 11:00 | 220 | 219
2017-04-20 11:30 | 215 | 214
2017-04-20 12:00 | 214 | 214
2017-04-20 12:30 | 215 | 214
2017-04-20 13:00 | 216 | 216
2017-04-20 13:30 | 223 | 223
2017-04-20 14:00 | 229 | 229
2017-04-20 14:30 | 239 | 239
2017-04-20 15:00 | 241 | 241
2017-04-20 15:30 | 241 | 241
2017-04-20 16:00 | 248 | 248
2017-04-20 16:30 | 259 | 258
2017-04-20 17:00 | 270 | 270
2017-04-20 17:30 | 278 | 277
2017-04-20 18:00 | 285 | 284
2017-04-20 18:30 | 285 | 285
2017-04-20 19:00 | 283 | 283
2017-04-20 19:30 | 276 | 276
2017-04-20 20:00 | 272 | 272
2017-04-20 20:30 | 268 | 268
2017-04-20 21:00 | 255 | 255
2017-04-20 21:30 | 242 | 242
2017-04-20 22:00 | 229 | 229
2017-04-20 22:30 | 224 | 224
2017-04-20 23:00 | 222 | 222
2017-04-20 23:30 | 207 | 207
2017-04-21 | 191 | 191
2017-04-21 00:30 | 174 | 174
2017-04-21 01:00 | 165 | 164
2017-04-21 01:30 | 159 | 159
2017-04-21 02:00 | 155 | 155
2017-04-21 02:30 | 153 | 153
2017-04-21 03:00 | 152 | 152
2017-04-21 03:30 | 152 | 152
2017-04-21 04:00 | 152 | 152
2017-04-21 04:30 | 156 | 156
2017-04-21 05:00 | 162 | 162
2017-04-21 05:30 | 174 | 174
2017-04-21 06:00 | 188 | 187
2017-04-21 06:30 | 207 | 206
2017-04-21 07:00 | 225 | 223
2017-04-21 07:30 | 236 | 236
2017-04-21 08:00 | 238 | 238
2017-04-21 08:30 | 232 | 232
2017-04-21 09:00 | 223 | 223
2017-04-21 09:30 | 220 | 220
2017-04-21 10:00 | 227 | 227
2017-04-21 10:30 | 230 | 230
2017-04-21 11:00 | 229 | 228
2017-04-21 11:30 | 226 | 225
2017-04-21 12:00 | 221 | 219
2017-04-21 12:30 | 221 | 219
2017-04-21 13:00 | 226 | 225
2017-04-21 13:30 | 233 | 232
2017-04-21 14:00 | 241 | 240
2017-04-21 14:30 | 241 | 239
2017-04-21 15:00 | 238 | 236
2017-04-21 15:30 | 242 | 240
2017-04-21 16:00 | 245 | 243
2017-04-21 16:30 | 251 | 250
2017-04-21 17:00 | 255 | 255
2017-04-21 17:30 | 258 | 258
2017-04-21 18:00 | 265 | 265
2017-04-21 18:30 | 263 | 263
2017-04-21 19:00 | 262 | 262
2017-04-21 19:30 | 255 | 254
2017-04-21 20:00 | 252 | 251
2017-04-21 20:30 | 249 | 249
2017-04-21 21:00 | 238 | 238
2017-04-21 21:30 | 229 | 229
2017-04-21 22:00 | 221 | 221
2017-04-21 22:30 | 218 | 218
2017-04-21 23:00 | 219 | 218
2017-04-21 23:30 | 205 | 204
2017-04-22 | 188 | 187
2017-04-22 00:30 | 173 | 173
2017-04-22 01:00 | 165 | 165
2017-04-22 01:30 | 157 | 157
2017-04-22 02:00 | 153 | 153
2017-04-22 02:30 | 149 | 149
2017-04-22 03:00 | 147 | 147
2017-04-22 03:30 | 147 | 147
2017-04-22 04:00 | 147 | 147
2017-04-22 04:30 | 147 | 147
2017-04-22 05:00 | 149 | 149
2017-04-22 05:30 | 154 | 154
2017-04-22 06:00 | 162 | 162
2017-04-22 06:30 | 171 | 171
2017-04-22 07:00 | 179 | 179
2017-04-22 07:30 | 191 | 191
2017-04-22 08:00 | 199 | 199
2017-04-22 08:30 | 207 | 206
2017-04-22 09:00 | 207 | 207
2017-04-22 09:30 | 207 | 206
2017-04-22 10:00 | 206 | 206
2017-04-22 10:30 | 205 | 204
2017-04-22 11:00 | 200 | 200
2017-04-22 11:30 | 191 | 191
2017-04-22 12:00 | 188 | 187
2017-04-22 12:30 | 182 | 182
2017-04-22 13:00 | 175 | 175
2017-04-22 13:30 | 175 | 175
2017-04-22 14:00 | 176 | 176
2017-04-22 14:30 | 181 | 181
2017-04-22 15:00 | 187 | 187
2017-04-22 15:30 | 192 | 192
2017-04-22 16:00 | 200 | 200
2017-04-22 16:30 | 211 | 210
2017-04-22 17:00 | 224 | 224
2017-04-22 17:30 | 228 | 227
2017-04-22 18:00 | 237 | 236
2017-04-22 18:30 | 238 | 237
2017-04-22 19:00 | 235 | 235
2017-04-22 19:30 | 229 | 229
2017-04-22 20:00 | 225 | 225
2017-04-22 20:30 | 221 | 221
2017-04-22 21:00 | 211 | 211
2017-04-22 21:30 | 204 | 203
2017-04-22 22:00 | 198 | 197
2017-04-22 22:30 | 198 | 198
2017-04-22 23:00 | 201 | 201
2017-04-22 23:30 | 190 | 190
2017-04-23 | 174 | 173
2017-04-23 00:30 | 159 | 159
2017-04-23 01:00 | 150 | 150
2017-04-23 01:30 | 143 | 143
2017-04-23 02:00 | 138 | 137
2017-04-23 02:30 | 135 | 135
2017-04-23 03:00 | 133 | 132
2017-04-23 03:30 | 131 | 131
2017-04-23 04:00 | 131 | 130
2017-04-23 04:30 | 131 | 131
2017-04-23 05:00 | 133 | 133
2017-04-23 05:30 | 135 | 135
2017-04-23 06:00 | 139 | 139
2017-04-23 06:30 | 144 | 144
2017-04-23 07:00 | 148 | 148
2017-04-23 07:30 | 152 | 152
2017-04-23 08:00 | 153 | 153
2017-04-23 08:30 | 154 | 154
2017-04-23 09:00 | 155 | 155
2017-04-23 09:30 | 154 | 154
2017-04-23 10:00 | 152 | 152
2017-04-23 10:30 | 156 | 155
2017-04-23 11:00 | 160 | 159
2017-04-23 11:30 | 163 | 162
2017-04-23 12:00 | 160 | 159
2017-04-23 12:30 | 159 | 158
2017-04-23 13:00 | 164 | 163
2017-04-23 13:30 | 164 | 163
2017-04-23 14:00 | 164 | 163
2017-04-23 14:30 | 168 | 166
2017-04-23 15:00 | 171 | 170
2017-04-23 15:30 | 179 | 178
2017-04-23 16:00 | 193 | 192
2017-04-23 16:30 | 206 | 205
2017-04-23 17:00 | 216 | 216
2017-04-23 17:30 | 226 | 226
2017-04-23 18:00 | 238 | 238
2017-04-23 18:30 | 244 | 244
2017-04-23 19:00 | 242 | 241
2017-04-23 19:30 | 234 | 234
2017-04-23 20:00 | 229 | 229
2017-04-23 20:30 | 227 | 227
2017-04-23 21:00 | 216 | 216
2017-04-23 21:30 | 205 | 205
2017-04-23 22:00 | 198 | 197
2017-04-23 22:30 | 196 | 195
2017-04-23 23:00 | 197 | 196
2017-04-23 23:30 | 184 | 183
2017-04-24 | 167 | 167
2017-04-24 00:30 | 154 | 153
2017-04-24 01:00 | 145 | 145
2017-04-24 01:30 | 140 | 139
2017-04-24 02:00 | 135 | 135
2017-04-24 02:30 | 133 | 133
2017-04-24 03:00 | 132 | 132
2017-04-24 03:30 | 132 | 132
2017-04-24 04:00 | 133 | 133
2017-04-24 04:30 | 137 | 137
2017-04-24 05:00 | 145 | 144
2017-04-24 05:30 | 163 | 162
2017-04-24 06:00 | 180 | 178
2017-04-24 06:30 | 193 | 191
2017-04-24 07:00 | 210 | 208
2017-04-24 07:30 | 221 | 219
2017-04-24 08:00 | 221 | 221
2017-04-24 08:30 | 215 | 214
2017-04-24 09:00 | 207 | 206
2017-04-24 09:30 | 204 | 203
2017-04-24 10:00 | 201 | 201
2017-04-24 10:30 | 203 | 203
2017-04-24 11:00 | 207 | 206
2017-04-24 11:30 | 207 | 207
2017-04-24 12:00 | 210 | 209
2017-04-24 12:30 | 213 | 213
2017-04-24 13:00 | 213 | 213
2017-04-24 13:30 | 216 | 216
2017-04-24 14:00 | 222 | 221
2017-04-24 14:30 | 229 | 228
2017-04-24 15:00 | 228 | 227
2017-04-24 15:30 | 229 | 228
2017-04-24 16:00 | 236 | 236
2017-04-24 16:30 | 245 | 245
2017-04-24 17:00 | 254 | 254
2017-04-24 17:30 | 258 | 258
2017-04-24 18:00 | 266 | 266
2017-04-24 18:30 | 263 | 263
2017-04-24 19:00 | 261 | 261
2017-04-24 19:30 | 253 | 253
2017-04-24 20:00 | 247 | 246
2017-04-24 20:30 | 241 | 241
2017-04-24 21:00 | 230 | 230
2017-04-24 21:30 | 220 | 218
2017-04-24 22:00 | 213 | 210
2017-04-24 22:30 | 208 | 205
2017-04-24 23:00 | 207 | 205
2017-04-24 23:30 | 194 | 193
2017-04-25 | 176 | 175
2017-04-25 00:30 | 159 | 159
2017-04-25 01:00 | 149 | 149
2017-04-25 01:30 | 144 | 143
2017-04-25 02:00 | 139 | 139
2017-04-25 02:30 | 135 | 135
2017-04-25 03:00 | 134 | 134
2017-04-25 03:30 | 134 | 134
2017-04-25 04:00 | 134 | 134
2017-04-25 04:30 | 135 | 135
2017-04-25 05:00 | 137 | 137
2017-04-25 05:30 | 139 | 139
2017-04-25 06:00 | 143 | 143
2017-04-25 06:30 | 148 | 148
2017-04-25 07:00 | 151 | 151
2017-04-25 07:30 | 155 | 155
2017-04-25 08:00 | 161 | 161
2017-04-25 08:30 | 160 | 160
2017-04-25 09:00 | 163 | 162
2017-04-25 09:30 | 174 | 173
2017-04-25 10:00 | 173 | 171
2017-04-25 10:30 | 172 | 170
2017-04-25 11:00 | 155 | 154
2017-04-25 11:30 | 154 | 152
2017-04-25 12:00 | 155 | 153
2017-04-25 12:30 | 157 | 156
2017-04-25 13:00 | 159 | 158
2017-04-25 13:30 | 160 | 160
2017-04-25 14:00 | 162 | 162
2017-04-25 14:30 | 168 | 167
2017-04-25 15:00 | 175 | 174
2017-04-25 15:30 | 181 | 180
2017-04-25 16:00 | 195 | 194
2017-04-25 16:30 | 208 | 207
2017-04-25 17:00 | 222 | 220
2017-04-25 17:30 | 228 | 228
2017-04-25 18:00 | 242 | 241
2017-04-25 18:30 | 245 | 245
2017-04-25 19:00 | 244 | 244
2017-04-25 19:30 | 238 | 237
2017-04-25 20:00 | 234 | 233
2017-04-25 20:30 | 232 | 231
2017-04-25 21:00 | 223 | 223
2017-04-25 21:30 | 215 | 214
2017-04-25 22:00 | 206 | 205
2017-04-25 22:30 | 202 | 201
2017-04-25 23:00 | 200 | 199
2017-04-25 23:30 | 188 | 187
2017-04-26 | 170 | 170
2017-04-26 00:30 | 157 | 157
2017-04-26 01:00 | 149 | 149
2017-04-26 01:30 | 143 | 143
2017-04-26 02:00 | 140 | 140
2017-04-26 02:30 | 138 | 137
2017-04-26 03:00 | 137 | 137
2017-04-26 03:30 | 137 | 137
2017-04-26 04:00 | 139 | 139
2017-04-26 04:30 | 145 | 145
2017-04-26 05:00 | 152 | 152
2017-04-26 05:30 | 165 | 165
2017-04-26 06:00 | 181 | 180
2017-04-26 06:30 | 203 | 202
2017-04-26 07:00 | 221 | 220
2017-04-26 07:30 | 230 | 229
2017-04-26 08:00 | 237 | 237
2017-04-26 08:30 | 233 | 233
2017-04-26 09:00 | 237 | 236
2017-04-26 09:30 | 248 | 246
2017-04-26 10:00 | 247 | 245
2017-04-26 10:30 | 240 | 238
2017-04-26 11:00 | 245 | 243
2017-04-26 11:30 | 252 | 249
2017-04-26 12:00 | 256 | 254
2017-04-26 12:30 | 257 | 255
2017-04-26 13:00 | 252 | 250
2017-04-26 13:30 | 248 | 246
2017-04-26 14:00 | 249 | 247
2017-04-26 14:30 | 254 | 252
2017-04-26 15:00 | 254 | 252
2017-04-26 15:30 | 248 | 246
2017-04-26 16:00 | 248 | 246
2017-04-26 16:30 | 257 | 256
2017-04-26 17:00 | 269 | 267
2017-04-26 17:30 | 279 | 277
2017-04-26 18:00 | 285 | 285
2017-04-26 18:30 | 279 | 279
2017-04-26 19:00 | 278 | 278
2017-04-26 19:30 | 270 | 270
2017-04-26 20:00 | 265 | 264
2017-04-26 20:30 | 261 | 259
2017-04-26 21:00 | 247 | 246
2017-04-26 21:30 | 233 | 233
2017-04-26 22:00 | 223 | 223
2017-04-26 22:30 | 218 | 218
2017-04-26 23:00 | 216 | 216
2017-04-26 23:30 | 202 | 202
2017-04-27 | 185 | 185
2017-04-27 00:30 | 168 | 168
2017-04-27 01:00 | 159 | 159
2017-04-27 01:30 | 153 | 153
2017-04-27 02:00 | 147 | 147
2017-04-27 02:30 | 146 | 146
2017-04-27 03:00 | 144 | 144
2017-04-27 03:30 | 146 | 146
2017-04-27 04:00 | 144 | 144
2017-04-27 04:30 | 148 | 148
2017-04-27 05:00 | 157 | 157
2017-04-27 05:30 | 171 | 171
2017-04-27 06:00 | 184 | 183
2017-04-27 06:30 | 205 | 203
2017-04-27 07:00 | 223 | 221
2017-04-27 07:30 | 232 | 231
2017-04-27 08:00 | 227 | 227
2017-04-27 08:30 | 216 | 216
2017-04-27 09:00 | 205 | 205
2017-04-27 09:30 | 200 | 199
2017-04-27 10:00 | 192 | 192
2017-04-27 10:30 | 187 | 186
2017-04-27 11:00 | 182 | 182
2017-04-27 11:30 | 180 | 180
2017-04-27 12:00 | 180 | 180
2017-04-27 12:30 | 180 | 180
2017-04-27 13:00 | 184 | 183
2017-04-27 13:30 | 188 | 187
2017-04-27 14:00 | 193 | 193
2017-04-27 14:30 | 200 | 200
2017-04-27 15:00 | 208 | 207
2017-04-27 15:30 | 217 | 217
2017-04-27 16:00 | 231 | 230
2017-04-27 16:30 | 243 | 242
2017-04-27 17:00 | 255 | 254
2017-04-27 17:30 | 264 | 263
2017-04-27 18:00 | 277 | 275
2017-04-27 18:30 | 278 | 277
2017-04-27 19:00 | 278 | 277
2017-04-27 19:30 | 272 | 271
2017-04-27 20:00 | 266 | 266
2017-04-27 20:30 | 262 | 261
2017-04-27 21:00 | 249 | 249
2017-04-27 21:30 | 235 | 235
2017-04-27 22:00 | 225 | 225
2017-04-27 22:30 | 219 | 219
2017-04-27 23:00 | 217 | 217
2017-04-27 23:30 | 203 | 203
2017-04-28 | 186 | 185
2017-04-28 00:30 | 169 | 168
2017-04-28 01:00 | 159 | 159
2017-04-28 01:30 | 153 | 153
2017-04-28 02:00 | 148 | 148
2017-04-28 02:30 | 145 | 145
2017-04-28 03:00 | 143 | 143
2017-04-28 03:30 | 145 | 145
2017-04-28 04:00 | 145 | 145
2017-04-28 04:30 | 149 | 149
2017-04-28 05:00 | 157 | 157
2017-04-28 05:30 | 170 | 170
2017-04-28 06:00 | 187 | 186
2017-04-28 06:30 | 208 | 207
2017-04-28 07:00 | 226 | 224
2017-04-28 07:30 | 237 | 237
2017-04-28 08:00 | 235 | 235
2017-04-28 08:30 | 224 | 223
2017-04-28 09:00 | 207 | 207
2017-04-28 09:30 | 198 | 198
2017-04-28 10:00 | 191 | 191
2017-04-28 10:30 | 187 | 187
2017-04-28 11:00 | 184 | 184
2017-04-28 11:30 | 183 | 182
2017-04-28 12:00 | 184 | 184
2017-04-28 12:30 | 191 | 191
2017-04-28 13:00 | 204 | 204
2017-04-28 13:30 | 214 | 213
2017-04-28 14:00 | 216 | 216
2017-04-28 14:30 | 217 | 217
2017-04-28 15:00 | 224 | 224
2017-04-28 15:30 | 230 | 230
2017-04-28 16:00 | 233 | 233
2017-04-28 16:30 | 242 | 242
2017-04-28 17:00 | 247 | 247
2017-04-28 17:30 | 253 | 253
2017-04-28 18:00 | 260 | 260
2017-04-28 18:30 | 258 | 258
2017-04-28 19:00 | 257 | 257
2017-04-28 19:30 | 251 | 251
2017-04-28 20:00 | 249 | 248
2017-04-28 20:30 | 248 | 247
2017-04-28 21:00 | 238 | 237
2017-04-28 21:30 | 227 | 226
2017-04-28 22:00 | 219 | 219
2017-04-28 22:30 | 216 | 215
2017-04-28 23:00 | 215 | 214
2017-04-28 23:30 | 202 | 201
2017-04-29 | 185 | 185
2017-04-29 00:30 | 169 | 169
2017-04-29 01:00 | 161 | 161
2017-04-29 01:30 | 153 | 153
2017-04-29 02:00 | 147 | 147
2017-04-29 02:30 | 145 | 145
2017-04-29 03:00 | 142 | 142
2017-04-29 03:30 | 142 | 142
2017-04-29 04:00 | 141 | 141
2017-04-29 04:30 | 141 | 141
2017-04-29 05:00 | 144 | 144
2017-04-29 05:30 | 149 | 149
2017-04-29 06:00 | 155 | 155
2017-04-29 06:30 | 164 | 164
2017-04-29 07:00 | 170 | 170
2017-04-29 07:30 | 176 | 176
2017-04-29 08:00 | 177 | 177
2017-04-29 08:30 | 177 | 177
2017-04-29 09:00 | 174 | 173
2017-04-29 09:30 | 169 | 168
2017-04-29 10:00 | 164 | 163
2017-04-29 10:30 | 159 | 157
2017-04-29 11:00 | 154 | 153
2017-04-29 11:30 | 148 | 147
2017-04-29 12:00 | 149 | 148
2017-04-29 12:30 | 148 | 147
2017-04-29 13:00 | 149 | 148
2017-04-29 13:30 | 153 | 151
2017-04-29 14:00 | 158 | 157
2017-04-29 14:30 | 165 | 164
2017-04-29 15:00 | 173 | 171
2017-04-29 15:30 | 181 | 179
2017-04-29 16:00 | 193 | 191
2017-04-29 16:30 | 204 | 202
2017-04-29 17:00 | 215 | 213
2017-04-29 17:30 | 222 | 220
2017-04-29 18:00 | 233 | 233
2017-04-29 18:30 | 233 | 233
2017-04-29 19:00 | 233 | 233
2017-04-29 19:30 | 227 | 227
2017-04-29 20:00 | 225 | 224
2017-04-29 20:30 | 222 | 220
2017-04-29 21:00 | 212 | 211
2017-04-29 21:30 | 204 | 203
2017-04-29 22:00 | 199 | 198
2017-04-29 22:30 | 198 | 197
2017-04-29 23:00 | 201 | 200
2017-04-29 23:30 | 189 | 189
2017-04-30 | 175 | 175
2017-04-30 00:30 | 161 | 161
2017-04-30 01:00 | 152 | 152
2017-04-30 01:30 | 145 | 145
2017-04-30 02:00 | 140 | 140
2017-04-30 02:30 | 138 | 138
2017-04-30 03:00 | 136 | 136
2017-04-30 03:30 | 135 | 135
2017-04-30 04:00 | 134 | 134
2017-04-30 04:30 | 135 | 134
2017-04-30 05:00 | 135 | 134
2017-04-30 05:30 | 138 | 137
2017-04-30 06:00 | 142 | 142
2017-04-30 06:30 | 146 | 146
2017-04-30 07:00 | 150 | 150
2017-04-30 07:30 | 155 | 154
2017-04-30 08:00 | 156 | 155
2017-04-30 08:30 | 156 | 155
2017-04-30 09:00 | 156 | 155
2017-04-30 09:30 | 154 | 153
2017-04-30 10:00 | 148 | 148
2017-04-30 10:30 | 147 | 147
2017-04-30 11:00 | 143 | 143
2017-04-30 11:30 | 145 | 145
2017-04-30 12:00 | 146 | 145
2017-04-30 12:30 | 145 | 145
2017-04-30 13:00 | 146 | 146
2017-04-30 13:30 | 149 | 148
2017-04-30 14:00 | 151 | 151
2017-04-30 14:30 | 157 | 156
2017-04-30 15:00 | 164 | 164
2017-04-30 15:30 | 174 | 173
2017-04-30 16:00 | 182 | 182
2017-04-30 16:30 | 193 | 192
2017-04-30 17:00 | 205 | 205
2017-04-30 17:30 | 214 | 214
2017-04-30 18:00 | 227 | 227
2017-04-30 18:30 | 229 | 229
2017-04-30 19:00 | 228 | 227
2017-04-30 19:30 | 221 | 221
2017-04-30 20:00 | 218 | 217
2017-04-30 20:30 | 215 | 215
2017-04-30 21:00 | 206 | 206
2017-04-30 21:30 | 201 | 201
2017-04-30 22:00 | 196 | 196
2017-04-30 22:30 | 195 | 195
2017-04-30 23:00 | 199 | 198
2017-04-30 23:30 | 187 | 187
2017-05-01 | 171 | 171
2017-05-01 00:30 | 157 | 157
2017-05-01 01:00 | 150 | 150
2017-05-01 01:30 | 144 | 144
2017-05-01 02:00 | 139 | 139
2017-05-01 02:30 | 136 | 136
2017-05-01 03:00 | 135 | 135
2017-05-01 03:30 | 135 | 135
2017-05-01 04:00 | 134 | 134
2017-05-01 04:30 | 133 | 133
2017-05-01 05:00 | 135 | 135
2017-05-01 05:30 | 139 | 139
2017-05-01 06:00 | 144 | 144
2017-05-01 06:30 | 149 | 149
2017-05-01 07:00 | 152 | 152
2017-05-01 07:30 | 156 | 156
2017-05-01 08:00 | 156 | 156
2017-05-01 08:30 | 157 | 157
2017-05-01 09:00 | 156 | 156
2017-05-01 09:30 | 155 | 155
2017-05-01 10:00 | 152 | 151
2017-05-01 10:30 | 150 | 149
2017-05-01 11:00 | 147 | 146
2017-05-01 11:30 | 148 | 147
2017-05-01 12:00 | 148 | 147
2017-05-01 12:30 | 151 | 150
2017-05-01 13:00 | 155 | 154
2017-05-01 13:30 | 159 | 158
2017-05-01 14:00 | 166 | 165
2017-05-01 14:30 | 166 | 165
2017-05-01 15:00 | 174 | 173
2017-05-01 15:30 | 181 | 179
2017-05-01 16:00 | 191 | 189
2017-05-01 16:30 | 206 | 204
2017-05-01 17:00 | 219 | 217
2017-05-01 17:30 | 233 | 232
2017-05-01 18:00 | 246 | 245
2017-05-01 18:30 | 245 | 244
2017-05-01 19:00 | 243 | 242
2017-05-01 19:30 | 236 | 235
2017-05-01 20:00 | 231 | 231
2017-05-01 20:30 | 228 | 227
2017-05-01 21:00 | 216 | 216
2017-05-01 21:30 | 208 | 207
2017-05-01 22:00 | 201 | 200
2017-05-01 22:30 | 198 | 198
2017-05-01 23:00 | 198 | 198
2017-05-01 23:30 | 187 | 187
2017-05-02 | 172 | 172
2017-05-02 00:30 | 158 | 158
2017-05-02 01:00 | 151 | 151
2017-05-02 01:30 | 146 | 146
2017-05-02 02:00 | 141 | 141
2017-05-02 02:30 | 139 | 139
2017-05-02 03:00 | 138 | 137
2017-05-02 03:30 | 137 | 137
2017-05-02 04:00 | 137 | 137
2017-05-02 04:30 | 143 | 143
2017-05-02 05:00 | 152 | 152
2017-05-02 05:30 | 167 | 166
2017-05-02 06:00 | 182 | 181
2017-05-02 06:30 | 205 | 203
2017-05-02 07:00 | 224 | 224
2017-05-02 07:30 | 235 | 235
2017-05-02 08:00 | 234 | 234
2017-05-02 08:30 | 223 | 223
2017-05-02 09:00 | 212 | 212
2017-05-02 09:30 | 203 | 203
2017-05-02 10:00 | 199 | 199
2017-05-02 10:30 | 198 | 197
2017-05-02 11:00 | 196 | 196
2017-05-02 11:30 | 199 | 199
2017-05-02 12:00 | 200 | 200
2017-05-02 12:30 | 206 | 205
2017-05-02 13:00 | 211 | 210
2017-05-02 13:30 | 217 | 216
2017-05-02 14:00 | 220 | 219
2017-05-02 14:30 | 226 | 225
2017-05-02 15:00 | 233 | 231
2017-05-02 15:30 | 243 | 242
2017-05-02 16:00 | 249 | 248
2017-05-02 16:30 | 258 | 257
2017-05-02 17:00 | 266 | 265
2017-05-02 17:30 | 276 | 275
2017-05-02 18:00 | 285 | 285
2017-05-02 18:30 | 279 | 279
2017-05-02 19:00 | 277 | 277
2017-05-02 19:30 | 271 | 271
2017-05-02 20:00 | 267 | 266
2017-05-02 20:30 | 259 | 259
2017-05-02 21:00 | 244 | 244
2017-05-02 21:30 | 232 | 232
2017-05-02 22:00 | 223 | 223
2017-05-02 22:30 | 218 | 218
2017-05-02 23:00 | 216 | 216
2017-05-02 23:30 | 202 | 202
2017-05-03 | 184 | 184
2017-05-03 00:30 | 169 | 169
2017-05-03 01:00 | 160 | 160
2017-05-03 01:30 | 153 | 153
2017-05-03 02:00 | 149 | 149
2017-05-03 02:30 | 147 | 147
2017-05-03 03:00 | 146 | 146
2017-05-03 03:30 | 146 | 146
2017-05-03 04:00 | 146 | 146
2017-05-03 04:30 | 151 | 151
2017-05-03 05:00 | 157 | 157
2017-05-03 05:30 | 172 | 171
2017-05-03 06:00 | 187 | 187
2017-05-03 06:30 | 209 | 208
2017-05-03 07:00 | 231 | 230
2017-05-03 07:30 | 239 | 239
2017-05-03 08:00 | 236 | 235
2017-05-03 08:30 | 227 | 227
2017-05-03 09:00 | 221 | 220
2017-05-03 09:30 | 218 | 217
2017-05-03 10:00 | 214 | 213
2017-05-03 10:30 | 212 | 211
2017-05-03 11:00 | 216 | 215
2017-05-03 11:30 | 218 | 217
2017-05-03 12:00 | 223 | 222
2017-05-03 12:30 | 226 | 226
2017-05-03 13:00 | 226 | 225
2017-05-03 13:30 | 234 | 234
2017-05-03 14:00 | 243 | 242
2017-05-03 14:30 | 250 | 250
2017-05-03 15:00 | 250 | 249
2017-05-03 15:30 | 246 | 245
2017-05-03 16:00 | 254 | 253
2017-05-03 16:30 | 262 | 261
2017-05-03 17:00 | 272 | 271
2017-05-03 17:30 | 278 | 277
2017-05-03 18:00 | 287 | 287
2017-05-03 18:30 | 285 | 284
2017-05-03 19:00 | 283 | 283
2017-05-03 19:30 | 276 | 275
2017-05-03 20:00 | 268 | 267
2017-05-03 20:30 | 263 | 263
2017-05-03 21:00 | 250 | 250
2017-05-03 21:30 | 236 | 236
2017-05-03 22:00 | 225 | 225
2017-05-03 22:30 | 216 | 216
2017-05-03 23:00 | 214 | 214
2017-05-03 23:30 | 199 | 199
2017-05-04 | 181 | 181
2017-05-04 00:30 | 166 | 166
2017-05-04 01:00 | 157 | 156
2017-05-04 01:30 | 151 | 150
2017-05-04 02:00 | 147 | 146
2017-05-04 02:30 | 147 | 146
2017-05-04 03:00 | 146 | 145
2017-05-04 03:30 | 146 | 145
2017-05-04 04:00 | 147 | 146
2017-05-04 04:30 | 152 | 151
2017-05-04 05:00 | 158 | 158
2017-05-04 05:30 | 172 | 172
2017-05-04 06:00 | 187 | 187
2017-05-04 06:30 | 208 | 208
2017-05-04 07:00 | 226 | 226
2017-05-04 07:30 | 238 | 238
2017-05-04 08:00 | 239 | 238
2017-05-04 08:30 | 235 | 233
2017-05-04 09:00 | 231 | 228
2017-05-04 09:30 | 227 | 225
2017-05-04 10:00 | 231 | 228
2017-05-04 10:30 | 232 | 228
2017-05-04 11:00 | 227 | 224
2017-05-04 11:30 | 232 | 228
2017-05-04 12:00 | 240 | 236
2017-05-04 12:30 | 242 | 238
2017-05-04 13:00 | 236 | 233
2017-05-04 13:30 | 233 | 229
2017-05-04 14:00 | 227 | 224
2017-05-04 14:30 | 234 | 231
2017-05-04 15:00 | 237 | 234
2017-05-04 15:30 | 243 | 240
2017-05-04 16:00 | 251 | 248
2017-05-04 16:30 | 255 | 252
2017-05-04 17:00 | 263 | 261
2017-05-04 17:30 | 274 | 273
2017-05-04 18:00 | 283 | 282
2017-05-04 18:30 | 281 | 280
2017-05-04 19:00 | 280 | 280
2017-05-04 19:30 | 274 | 273
2017-05-04 20:00 | 271 | 270
2017-05-04 20:30 | 268 | 267
2017-05-04 21:00 | 254 | 253
2017-05-04 21:30 | 240 | 239
2017-05-04 22:00 | 229 | 226
2017-05-04 22:30 | 224 | 220
2017-05-04 23:00 | 221 | 217
2017-05-04 23:30 | 206 | 203
2017-05-05 | 188 | 185
2017-05-05 00:30 | 171 | 170
2017-05-05 01:00 | 161 | 160
2017-05-05 01:30 | 155 | 154
2017-05-05 02:00 | 150 | 149
2017-05-05 02:30 | 148 | 147
2017-05-05 03:00 | 147 | 146
2017-05-05 03:30 | 147 | 146
2017-05-05 04:00 | 147 | 146
2017-05-05 04:30 | 152 | 151
2017-05-05 05:00 | 159 | 158
2017-05-05 05:30 | 173 | 171
2017-05-05 06:00 | 189 | 186
2017-05-05 06:30 | 208 | 208
2017-05-05 07:00 | 226 | 226
2017-05-05 07:30 | 236 | 236
2017-05-05 08:00 | 233 | 233
2017-05-05 08:30 | 223 | 223
2017-05-05 09:00 | 212 | 212
2017-05-05 09:30 | 207 | 207
2017-05-05 10:00 | 202 | 202
2017-05-05 10:30 | 200 | 200
2017-05-05 11:00 | 201 | 200
2017-05-05 11:30 | 196 | 196
2017-05-05 12:00 | 200 | 199
2017-05-05 12:30 | 202 | 202
2017-05-05 13:00 | 206 | 206
2017-05-05 13:30 | 207 | 207
2017-05-05 14:00 | 213 | 213
2017-05-05 14:30 | 218 | 218
2017-05-05 15:00 | 220 | 220
2017-05-05 15:30 | 221 | 221
2017-05-05 16:00 | 232 | 232
2017-05-05 16:30 | 241 | 241
2017-05-05 17:00 | 251 | 251
2017-05-05 17:30 | 259 | 258
2017-05-05 18:00 | 264 | 264
2017-05-05 18:30 | 261 | 260
2017-05-05 19:00 | 259 | 259
2017-05-05 19:30 | 253 | 253
2017-05-05 20:00 | 249 | 249
2017-05-05 20:30 | 246 | 246
2017-05-05 21:00 | 235 | 235
2017-05-05 21:30 | 226 | 226
2017-05-05 22:00 | 218 | 218
2017-05-05 22:30 | 216 | 216
2017-05-05 23:00 | 213 | 213
2017-05-05 23:30 | 200 | 200
2017-05-06 | 182 | 182
2017-05-06 00:30 | 167 | 166
2017-05-06 01:00 | 158 | 158
2017-05-06 01:30 | 151 | 150
2017-05-06 02:00 | 145 | 145
2017-05-06 02:30 | 142 | 142
2017-05-06 03:00 | 141 | 141
2017-05-06 03:30 | 141 | 140
2017-05-06 04:00 | 140 | 139
2017-05-06 04:30 | 143 | 142
2017-05-06 05:00 | 143 | 143
2017-05-06 05:30 | 149 | 148
2017-05-06 06:00 | 156 | 156
2017-05-06 06:30 | 162 | 161
2017-05-06 07:00 | 180 | 180
2017-05-06 07:30 | 191 | 191
2017-05-06 08:00 | 189 | 189
2017-05-06 08:30 | 181 | 181
2017-05-06 09:00 | 182 | 182
2017-05-06 09:30 | 182 | 181
2017-05-06 10:00 | 176 | 176
2017-05-06 10:30 | 174 | 174
2017-05-06 11:00 | 172 | 172
2017-05-06 11:30 | 168 | 168
2017-05-06 12:00 | 169 | 169
2017-05-06 12:30 | 162 | 162
2017-05-06 13:00 | 157 | 157
2017-05-06 13:30 | 159 | 159
2017-05-06 14:00 | 164 | 163
2017-05-06 14:30 | 166 | 166
2017-05-06 15:00 | 174 | 174
2017-05-06 15:30 | 182 | 181
2017-05-06 16:00 | 194 | 193
2017-05-06 16:30 | 205 | 205
2017-05-06 17:00 | 219 | 218
2017-05-06 17:30 | 227 | 226
2017-05-06 18:00 | 237 | 237
2017-05-06 18:30 | 236 | 236
2017-05-06 19:00 | 234 | 234
2017-05-06 19:30 | 228 | 228
2017-05-06 20:00 | 226 | 226
2017-05-06 20:30 | 223 | 223
2017-05-06 21:00 | 214 | 213
2017-05-06 21:30 | 207 | 206
2017-05-06 22:00 | 201 | 201
2017-05-06 22:30 | 201 | 200
2017-05-06 23:00 | 203 | 203
2017-05-06 23:30 | 192 | 192
2017-05-07 | 177 | 177
2017-05-07 00:30 | 163 | 163
2017-05-07 01:00 | 155 | 155
2017-05-07 01:30 | 147 | 147
2017-05-07 02:00 | 140 | 140
2017-05-07 02:30 | 138 | 138
2017-05-07 03:00 | 135 | 135
2017-05-07 03:30 | 134 | 134
2017-05-07 04:00 | 134 | 134
2017-05-07 04:30 | 134 | 134
2017-05-07 05:00 | 135 | 135
2017-05-07 05:30 | 138 | 138
2017-05-07 06:00 | 143 | 143
2017-05-07 06:30 | 147 | 147
2017-05-07 07:00 | 152 | 152
2017-05-07 07:30 | 159 | 159
2017-05-07 08:00 | 164 | 164
2017-05-07 08:30 | 168 | 168
2017-05-07 09:00 | 168 | 168
2017-05-07 09:30 | 164 | 164
2017-05-07 10:00 | 158 | 158
2017-05-07 10:30 | 154 | 154
2017-05-07 11:00 | 152 | 152
2017-05-07 11:30 | 150 | 150
2017-05-07 12:00 | 148 | 148
2017-05-07 12:30 | 149 | 149
2017-05-07 13:00 | 150 | 150
2017-05-07 13:30 | 154 | 154
2017-05-07 14:00 | 158 | 158
2017-05-07 14:30 | 165 | 165
2017-05-07 15:00 | 174 | 174
2017-05-07 15:30 | 185 | 185
2017-05-07 16:00 | 197 | 196
2017-05-07 16:30 | 211 | 211
2017-05-07 17:00 | 225 | 225
2017-05-07 17:30 | 235 | 234
2017-05-07 18:00 | 248 | 247
2017-05-07 18:30 | 247 | 246
2017-05-07 19:00 | 244 | 243
2017-05-07 19:30 | 236 | 236
2017-05-07 20:00 | 232 | 231
2017-05-07 20:30 | 229 | 228
2017-05-07 21:00 | 218 | 218
2017-05-07 21:30 | 209 | 209
2017-05-07 22:00 | 202 | 202
2017-05-07 22:30 | 199 | 199
2017-05-07 23:00 | 199 | 199
2017-05-07 23:30 | 188 | 188
2017-05-08 | 173 | 173
2017-05-08 00:30 | 160 | 159
2017-05-08 01:00 | 151 | 151
2017-05-08 01:30 | 146 | 145
2017-05-08 02:00 | 141 | 141
2017-05-08 02:30 | 140 | 140
2017-05-08 03:00 | 138 | 138
2017-05-08 03:30 | 138 | 138
2017-05-08 04:00 | 139 | 139
2017-05-08 04:30 | 144 | 144
2017-05-08 05:00 | 154 | 154
2017-05-08 05:30 | 168 | 167
2017-05-08 06:00 | 185 | 183
2017-05-08 06:30 | 208 | 208
2017-05-08 07:00 | 227 | 227
2017-05-08 07:30 | 243 | 242
2017-05-08 08:00 | 244 | 244
2017-05-08 08:30 | 240 | 240
2017-05-08 09:00 | 238 | 238
2017-05-08 09:30 | 238 | 238
2017-05-08 10:00 | 239 | 239
2017-05-08 10:30 | 232 | 232
2017-05-08 11:00 | 227 | 227
2017-05-08 11:30 | 239 | 239
2017-05-08 12:00 | 233 | 233
2017-05-08 12:30 | 233 | 233
2017-05-08 13:00 | 240 | 240
2017-05-08 13:30 | 239 | 239
2017-05-08 14:00 | 236 | 236
2017-05-08 14:30 | 238 | 238
2017-05-08 15:00 | 244 | 244
2017-05-08 15:30 | 250 | 250
2017-05-08 16:00 | 257 | 257
2017-05-08 16:30 | 262 | 262
2017-05-08 17:00 | 272 | 272
2017-05-08 17:30 | 282 | 282
2017-05-08 18:00 | 287 | 287
2017-05-08 18:30 | 282 | 282
2017-05-08 19:00 | 280 | 279
2017-05-08 19:30 | 271 | 271
2017-05-08 20:00 | 267 | 266
2017-05-08 20:30 | 262 | 261
2017-05-08 21:00 | 250 | 249
2017-05-08 21:30 | 238 | 237
2017-05-08 22:00 | 225 | 225
2017-05-08 22:30 | 219 | 219
2017-05-08 23:00 | 218 | 217
2017-05-08 23:30 | 204 | 204
2017-05-09 | 188 | 187
2017-05-09 00:30 | 171 | 171
2017-05-09 01:00 | 161 | 161
2017-05-09 01:30 | 154 | 154
2017-05-09 02:00 | 149 | 148
2017-05-09 02:30 | 148 | 148
2017-05-09 03:00 | 145 | 145
2017-05-09 03:30 | 145 | 145
2017-05-09 04:00 | 146 | 146
2017-05-09 04:30 | 151 | 151
2017-05-09 05:00 | 159 | 159
2017-05-09 05:30 | 173 | 172
2017-05-09 06:00 | 190 | 189
2017-05-09 06:30 | 212 | 211
2017-05-09 07:00 | 230 | 229
2017-05-09 07:30 | 247 | 247
2017-05-09 08:00 | 248 | 248
2017-05-09 08:30 | 240 | 240
2017-05-09 09:00 | 229 | 229
2017-05-09 09:30 | 221 | 221
2017-05-09 10:00 | 220 | 220
2017-05-09 10:30 | 219 | 219
2017-05-09 11:00 | 219 | 219
2017-05-09 11:30 | 213 | 213
2017-05-09 12:00 | 208 | 208
2017-05-09 12:30 | 208 | 208
2017-05-09 13:00 | 213 | 213
2017-05-09 13:30 | 215 | 215
2017-05-09 14:00 | 214 | 214
2017-05-09 14:30 | 217 | 217
2017-05-09 15:00 | 223 | 223
2017-05-09 15:30 | 230 | 230
2017-05-09 16:00 | 241 | 241
2017-05-09 16:30 | 254 | 254
2017-05-09 17:00 | 261 | 261
2017-05-09 17:30 | 272 | 272
2017-05-09 18:00 | 281 | 280
2017-05-09 18:30 | 275 | 275
2017-05-09 19:00 | 274 | 274
2017-05-09 19:30 | 267 | 267
2017-05-09 20:00 | 262 | 262
2017-05-09 20:30 | 262 | 262
2017-05-09 21:00 | 252 | 250
2017-05-09 21:30 | 240 | 239
2017-05-09 22:00 | 230 | 230
2017-05-09 22:30 | 225 | 224
2017-05-09 23:00 | 223 | 221
2017-05-09 23:30 | 209 | 208
2017-05-10 | 191 | 191
2017-05-10 00:30 | 175 | 174
2017-05-10 01:00 | 165 | 165
2017-05-10 01:30 | 158 | 158
2017-05-10 02:00 | 153 | 153
2017-05-10 02:30 | 151 | 151
2017-05-10 03:00 | 150 | 150
2017-05-10 03:30 | 150 | 150
2017-05-10 04:00 | 150 | 150
2017-05-10 04:30 | 155 | 154
2017-05-10 05:00 | 164 | 164
2017-05-10 05:30 | 177 | 176
2017-05-10 06:00 | 191 | 189
2017-05-10 06:30 | 216 | 216
2017-05-10 07:00 | 238 | 238
2017-05-10 07:30 | 256 | 256
2017-05-10 08:00 | 263 | 263
2017-05-10 08:30 | 257 | 256
2017-05-10 09:00 | 255 | 255
2017-05-10 09:30 | 258 | 258
2017-05-10 10:00 | 258 | 258
2017-05-10 10:30 | 260 | 260
2017-05-10 11:00 | 261 | 261
2017-05-10 11:30 | 260 | 260
2017-05-10 12:00 | 256 | 256
2017-05-10 12:30 | 254 | 254
2017-05-10 13:00 | 249 | 249
2017-05-10 13:30 | 251 | 251
2017-05-10 14:00 | 253 | 253
2017-05-10 14:30 | 254 | 254
2017-05-10 15:00 | 253 | 253
2017-05-10 15:30 | 256 | 255
2017-05-10 16:00 | 260 | 260
2017-05-10 16:30 | 267 | 267
2017-05-10 17:00 | 278 | 278
2017-05-10 17:30 | 290 | 290
2017-05-10 18:00 | 293 | 293
2017-05-10 18:30 | 288 | 288
2017-05-10 19:00 | 286 | 286
2017-05-10 19:30 | 279 | 279
2017-05-10 20:00 | 274 | 274
2017-05-10 20:30 | 272 | 272
2017-05-10 21:00 | 259 | 259
2017-05-10 21:30 | 248 | 248
2017-05-10 22:00 | 237 | 236
2017-05-10 22:30 | 227 | 227
2017-05-10 23:00 | 224 | 224
2017-05-10 23:30 | 211 | 210
2017-05-11 | 193 | 193
2017-05-11 00:30 | 177 | 176
2017-05-11 01:00 | 167 | 167
2017-05-11 01:30 | 160 | 160
2017-05-11 02:00 | 155 | 155
2017-05-11 02:30 | 151 | 151
2017-05-11 03:00 | 150 | 150
2017-05-11 03:30 | 150 | 150
2017-05-11 04:00 | 150 | 150
2017-05-11 04:30 | 156 | 156
2017-05-11 05:00 | 164 | 164
2017-05-11 05:30 | 180 | 179
2017-05-11 06:00 | 197 | 195
2017-05-11 06:30 | 220 | 219
2017-05-11 07:00 | 241 | 241
2017-05-11 07:30 | 251 | 251
2017-05-11 08:00 | 246 | 245
2017-05-11 08:30 | 234 | 234
2017-05-11 09:00 | 223 | 223
2017-05-11 09:30 | 214 | 214
2017-05-11 10:00 | 215 | 215
2017-05-11 10:30 | 228 | 228
2017-05-11 11:00 | 222 | 221
2017-05-11 11:30 | 213 | 213
2017-05-11 12:00 | 198 | 198
2017-05-11 12:30 | 197 | 197
2017-05-11 13:00 | 202 | 201
2017-05-11 13:30 | 205 | 205
2017-05-11 14:00 | 212 | 212
2017-05-11 14:30 | 216 | 216
2017-05-11 15:00 | 221 | 221
2017-05-11 15:30 | 230 | 230
2017-05-11 16:00 | 241 | 241
2017-05-11 16:30 | 250 | 250
2017-05-11 17:00 | 260 | 260
2017-05-11 17:30 | 271 | 271
2017-05-11 18:00 | 280 | 280
2017-05-11 18:30 | 279 | 279
2017-05-11 19:00 | 280 | 280
2017-05-11 19:30 | 275 | 275
2017-05-11 20:00 | 271 | 271
2017-05-11 20:30 | 270 | 270
2017-05-11 21:00 | 259 | 259
2017-05-11 21:30 | 247 | 246
2017-05-11 22:00 | 234 | 234
2017-05-11 22:30 | 229 | 229
2017-05-11 23:00 | 226 | 226
2017-05-11 23:30 | 211 | 211
2017-05-12 | 193 | 193
2017-05-12 00:30 | 176 | 176
2017-05-12 01:00 | 166 | 166
2017-05-12 01:30 | 159 | 159
2017-05-12 02:00 | 154 | 154
2017-05-12 02:30 | 151 | 151
2017-05-12 03:00 | 149 | 149
2017-05-12 03:30 | 149 | 149
2017-05-12 04:00 | 148 | 148
2017-05-12 04:30 | 152 | 152
2017-05-12 05:00 | 162 | 161
2017-05-12 05:30 | 177 | 176
2017-05-12 06:00 | 194 | 193
2017-05-12 06:30 | 217 | 215
2017-05-12 07:00 | 238 | 238
2017-05-12 07:30 | 253 | 253
2017-05-12 08:00 | 255 | 255
2017-05-12 08:30 | 250 | 250
2017-05-12 09:00 | 238 | 238
2017-05-12 09:30 | 227 | 227
2017-05-12 10:00 | 219 | 219
2017-05-12 10:30 | 216 | 216
2017-05-12 11:00 | 218 | 218
2017-05-12 11:30 | 207 | 207
2017-05-12 12:00 | 214 | 214
2017-05-12 12:30 | 226 | 226
2017-05-12 13:00 | 228 | 228
2017-05-12 13:30 | 227 | 227
2017-05-12 14:00 | 229 | 229
2017-05-12 14:30 | 226 | 226
2017-05-12 15:00 | 229 | 229
2017-05-12 15:30 | 233 | 233
2017-05-12 16:00 | 243 | 243
2017-05-12 16:30 | 252 | 252
2017-05-12 17:00 | 261 | 261
2017-05-12 17:30 | 267 | 267
2017-05-12 18:00 | 272 | 272
2017-05-12 18:30 | 267 | 267
2017-05-12 19:00 | 266 | 266
2017-05-12 19:30 | 260 | 260
2017-05-12 20:00 | 256 | 256
2017-05-12 20:30 | 254 | 254
2017-05-12 21:00 | 243 | 243
2017-05-12 21:30 | 233 | 233
2017-05-12 22:00 | 225 | 224
2017-05-12 22:30 | 223 | 222
2017-05-12 23:00 | 222 | 221
2017-05-12 23:30 | 208 | 207
2017-05-13 | 190 | 190
2017-05-13 00:30 | 174 | 174
2017-05-13 01:00 | 165 | 165
2017-05-13 01:30 | 158 | 158
2017-05-13 02:00 | 153 | 153
2017-05-13 02:30 | 149 | 149
2017-05-13 03:00 | 147 | 147
2017-05-13 03:30 | 146 | 146
2017-05-13 04:00 | 145 | 145
2017-05-13 04:30 | 146 | 146
2017-05-13 05:00 | 148 | 148
2017-05-13 05:30 | 153 | 153
2017-05-13 06:00 | 159 | 159
2017-05-13 06:30 | 169 | 168
2017-05-13 07:00 | 176 | 176
2017-05-13 07:30 | 187 | 187
2017-05-13 08:00 | 204 | 203
2017-05-13 08:30 | 214 | 214
2017-05-13 09:00 | 210 | 209
2017-05-13 09:30 | 206 | 205
2017-05-13 10:00 | 201 | 200
2017-05-13 10:30 | 195 | 194
2017-05-13 11:00 | 200 | 199
2017-05-13 11:30 | 212 | 210
2017-05-13 12:00 | 216 | 214
2017-05-13 12:30 | 215 | 214
2017-05-13 13:00 | 213 | 211
2017-05-13 13:30 | 214 | 213
2017-05-13 14:00 | 215 | 213
2017-05-13 14:30 | 219 | 218
2017-05-13 15:00 | 220 | 219
2017-05-13 15:30 | 220 | 219
2017-05-13 16:00 | 224 | 223
2017-05-13 16:30 | 231 | 230
2017-05-13 17:00 | 242 | 240
2017-05-13 17:30 | 252 | 251
2017-05-13 18:00 | 260 | 259
2017-05-13 18:30 | 259 | 259
2017-05-13 19:00 | 258 | 258
2017-05-13 19:30 | 251 | 251
2017-05-13 20:00 | 247 | 246
2017-05-13 20:30 | 243 | 242
2017-05-13 21:00 | 232 | 232
2017-05-13 21:30 | 224 | 223
2017-05-13 22:00 | 218 | 218
2017-05-13 22:30 | 216 | 216
2017-05-13 23:00 | 218 | 218
2017-05-13 23:30 | 207 | 207
2017-05-14 | 190 | 190
2017-05-14 00:30 | 174 | 174
2017-05-14 01:00 | 163 | 163
2017-05-14 01:30 | 155 | 155
2017-05-14 02:00 | 150 | 150
2017-05-14 02:30 | 146 | 146
2017-05-14 03:00 | 143 | 143
2017-05-14 03:30 | 142 | 142
2017-05-14 04:00 | 140 | 140
2017-05-14 04:30 | 141 | 141
2017-05-14 05:00 | 142 | 142
2017-05-14 05:30 | 146 | 146
2017-05-14 06:00 | 150 | 150
2017-05-14 06:30 | 157 | 157
2017-05-14 07:00 | 166 | 166
2017-05-14 07:30 | 179 | 179
2017-05-14 08:00 | 189 | 189
2017-05-14 08:30 | 201 | 200
2017-05-14 09:00 | 209 | 208
2017-05-14 09:30 | 204 | 203
2017-05-14 10:00 | 195 | 194
2017-05-14 10:30 | 197 | 196
2017-05-14 11:00 | 200 | 199
2017-05-14 11:30 | 205 | 204
2017-05-14 12:00 | 204 | 203
2017-05-14 12:30 | 197 | 196
2017-05-14 13:00 | 197 | 197
2017-05-14 13:30 | 202 | 201
2017-05-14 14:00 | 204 | 203
2017-05-14 14:30 | 203 | 202
2017-05-14 15:00 | 203 | 202
2017-05-14 15:30 | 210 | 209
2017-05-14 16:00 | 219 | 217
2017-05-14 16:30 | 230 | 228
2017-05-14 17:00 | 243 | 241
2017-05-14 17:30 | 254 | 253
2017-05-14 18:00 | 260 | 259
2017-05-14 18:30 | 258 | 257
2017-05-14 19:00 | 257 | 257
2017-05-14 19:30 | 251 | 250
2017-05-14 20:00 | 247 | 246
2017-05-14 20:30 | 246 | 245
2017-05-14 21:00 | 236 | 235
2017-05-14 21:30 | 227 | 227
2017-05-14 22:00 | 220 | 220
2017-05-14 22:30 | 216 | 216
2017-05-14 23:00 | 217 | 217
2017-05-14 23:30 | 205 | 205
2017-05-15 | 188 | 188
2017-05-15 00:30 | 173 | 173
2017-05-15 01:00 | 164 | 164
2017-05-15 01:30 | 157 | 157
2017-05-15 02:00 | 152 | 152
2017-05-15 02:30 | 149 | 149
2017-05-15 03:00 | 148 | 148
2017-05-15 03:30 | 147 | 147
2017-05-15 04:00 | 148 | 148
2017-05-15 04:30 | 153 | 153
2017-05-15 05:00 | 162 | 162
2017-05-15 05:30 | 179 | 179
2017-05-15 06:00 | 197 | 196
2017-05-15 06:30 | 223 | 223
2017-05-15 07:00 | 247 | 247
2017-05-15 07:30 | 264 | 264
2017-05-15 08:00 | 264 | 263
2017-05-15 08:30 | 255 | 255
2017-05-15 09:00 | 244 | 244
2017-05-15 09:30 | 236 | 235
2017-05-15 10:00 | 228 | 228
2017-05-15 10:30 | 222 | 222
2017-05-15 11:00 | 218 | 218
2017-05-15 11:30 | 217 | 217
2017-05-15 12:00 | 217 | 217
2017-05-15 12:30 | 218 | 218
2017-05-15 13:00 | 221 | 221
2017-05-15 13:30 | 231 | 230
2017-05-15 14:00 | 235 | 234
2017-05-15 14:30 | 241 | 241
2017-05-15 15:00 | 247 | 246
2017-05-15 15:30 | 254 | 254
2017-05-15 16:00 | 266 | 265
2017-05-15 16:30 | 276 | 275
2017-05-15 17:00 | 287 | 286
2017-05-15 17:30 | 299 | 299
2017-05-15 18:00 | 308 | 307
2017-05-15 18:30 | 302 | 301
2017-05-15 19:00 | 300 | 299
2017-05-15 19:30 | 293 | 292
2017-05-15 20:00 | 284 | 284
2017-05-15 20:30 | 279 | 279
2017-05-15 21:00 | 265 | 265
2017-05-15 21:30 | 254 | 254
2017-05-15 22:00 | 243 | 243
2017-05-15 22:30 | 235 | 234
2017-05-15 23:00 | 231 | 231
2017-05-15 23:30 | 216 | 216
2017-05-16 | 199 | 199
2017-05-16 00:30 | 182 | 182
2017-05-16 01:00 | 172 | 171
2017-05-16 01:30 | 164 | 164
2017-05-16 02:00 | 159 | 159
2017-05-16 02:30 | 157 | 157
2017-05-16 03:00 | 155 | 155
2017-05-16 03:30 | 157 | 157
2017-05-16 04:00 | 157 | 157
2017-05-16 04:30 | 163 | 163
2017-05-16 05:00 | 171 | 171
2017-05-16 05:30 | 187 | 186
2017-05-16 06:00 | 207 | 205
2017-05-16 06:30 | 232 | 230
2017-05-16 07:00 | 259 | 259
2017-05-16 07:30 | 283 | 283
2017-05-16 08:00 | 276 | 276
2017-05-16 08:30 | 261 | 261
2017-05-16 09:00 | 245 | 244
2017-05-16 09:30 | 234 | 234
2017-05-16 10:00 | 226 | 226
2017-05-16 10:30 | 221 | 221
2017-05-16 11:00 | 217 | 217
2017-05-16 11:30 | 216 | 215
2017-05-16 12:00 | 215 | 215
2017-05-16 12:30 | 216 | 215
2017-05-16 13:00 | 219 | 219
2017-05-16 13:30 | 225 | 225
2017-05-16 14:00 | 231 | 231
2017-05-16 14:30 | 237 | 237
2017-05-16 15:00 | 246 | 245
2017-05-16 15:30 | 258 | 258
2017-05-16 16:00 | 272 | 272
2017-05-16 16:30 | 283 | 283
2017-05-16 17:00 | 283 | 283
2017-05-16 17:30 | 294 | 294
2017-05-16 18:00 | 303 | 303
2017-05-16 18:30 | 296 | 296
2017-05-16 19:00 | 296 | 296
2017-05-16 19:30 | 291 | 291
2017-05-16 20:00 | 287 | 287
2017-05-16 20:30 | 284 | 284
2017-05-16 21:00 | 269 | 269
2017-05-16 21:30 | 257 | 257
2017-05-16 22:00 | 243 | 243
2017-05-16 22:30 | 235 | 235
2017-05-16 23:00 | 233 | 232
2017-05-16 23:30 | 218 | 218
2017-05-17 | 200 | 200
2017-05-17 00:30 | 183 | 183
2017-05-17 01:00 | 172 | 172
2017-05-17 01:30 | 166 | 166
2017-05-17 02:00 | 161 | 161
2017-05-17 02:30 | 158 | 158
2017-05-17 03:00 | 157 | 157
2017-05-17 03:30 | 156 | 156
2017-05-17 04:00 | 157 | 157
2017-05-17 04:30 | 162 | 162
2017-05-17 05:00 | 172 | 171
2017-05-17 05:30 | 188 | 188
2017-05-17 06:00 | 207 | 205
2017-05-17 06:30 | 231 | 231
2017-05-17 07:00 | 253 | 252
2017-05-17 07:30 | 265 | 265
2017-05-17 08:00 | 259 | 258
2017-05-17 08:30 | 246 | 245
2017-05-17 09:00 | 234 | 234
2017-05-17 09:30 | 225 | 225
2017-05-17 10:00 | 218 | 218
2017-05-17 10:30 | 215 | 214
2017-05-17 11:00 | 215 | 214
2017-05-17 11:30 | 221 | 221
2017-05-17 12:00 | 225 | 225
2017-05-17 12:30 | 227 | 226
2017-05-17 13:00 | 229 | 229
2017-05-17 13:30 | 232 | 231
2017-05-17 14:00 | 235 | 234
2017-05-17 14:30 | 239 | 239
2017-05-17 15:00 | 241 | 241
2017-05-17 15:30 | 247 | 246
2017-05-17 16:00 | 256 | 255
2017-05-17 16:30 | 267 | 266
2017-05-17 17:00 | 279 | 279
2017-05-17 17:30 | 292 | 292
2017-05-17 18:00 | 300 | 300
2017-05-17 18:30 | 293 | 293
2017-05-17 19:00 | 292 | 292
2017-05-17 19:30 | 285 | 285
2017-05-17 20:00 | 283 | 283
2017-05-17 20:30 | 280 | 280
2017-05-17 21:00 | 265 | 265
2017-05-17 21:30 | 253 | 253
2017-05-17 22:00 | 241 | 241
2017-05-17 22:30 | 233 | 233
2017-05-17 23:00 | 230 | 230
2017-05-17 23:30 | 215 | 215
2017-05-18 | 197 | 197
2017-05-18 00:30 | 181 | 181
2017-05-18 01:00 | 171 | 171
2017-05-18 01:30 | 164 | 164
2017-05-18 02:00 | 160 | 159
2017-05-18 02:30 | 158 | 157
2017-05-18 03:00 | 156 | 155
2017-05-18 03:30 | 156 | 155
2017-05-18 04:00 | 157 | 156
2017-05-18 04:30 | 163 | 163
2017-05-18 05:00 | 170 | 170
2017-05-18 05:30 | 185 | 185
2017-05-18 06:00 | 202 | 202
2017-05-18 06:30 | 226 | 226
2017-05-18 07:00 | 248 | 248
2017-05-18 07:30 | 270 | 270
2017-05-18 08:00 | 276 | 275
2017-05-18 08:30 | 270 | 269
2017-05-18 09:00 | 258 | 257
2017-05-18 09:30 | 249 | 249
2017-05-18 10:00 | 250 | 249
2017-05-18 10:30 | 252 | 251
2017-05-18 11:00 | 253 | 252
2017-05-18 11:30 | 246 | 245
2017-05-18 12:00 | 244 | 243
2017-05-18 12:30 | 234 | 234
2017-05-18 13:00 | 233 | 233
2017-05-18 13:30 | 242 | 241
2017-05-18 14:00 | 248 | 247
2017-05-18 14:30 | 250 | 248
2017-05-18 15:00 | 255 | 254
2017-05-18 15:30 | 260 | 259
2017-05-18 16:00 | 268 | 268
2017-05-18 16:30 | 276 | 276
2017-05-18 17:00 | 287 | 286
2017-05-18 17:30 | 300 | 299
2017-05-18 18:00 | 302 | 302
2017-05-18 18:30 | 296 | 296
2017-05-18 19:00 | 295 | 295
2017-05-18 19:30 | 289 | 289
2017-05-18 20:00 | 287 | 287
2017-05-18 20:30 | 283 | 282
2017-05-18 21:00 | 271 | 271
2017-05-18 21:30 | 257 | 257
2017-05-18 22:00 | 243 | 243
2017-05-18 22:30 | 238 | 238
2017-05-18 23:00 | 236 | 236
2017-05-18 23:30 | 222 | 222
2017-05-19 | 203 | 203
2017-05-19 00:30 | 185 | 185
2017-05-19 01:00 | 174 | 174
2017-05-19 01:30 | 167 | 167
2017-05-19 02:00 | 162 | 162
2017-05-19 02:30 | 159 | 159
2017-05-19 03:00 | 159 | 158
2017-05-19 03:30 | 159 | 158
2017-05-19 04:00 | 158 | 158
2017-05-19 04:30 | 163 | 162
2017-05-19 05:00 | 170 | 170
2017-05-19 05:30 | 184 | 184
2017-05-19 06:00 | 199 | 199
2017-05-19 06:30 | 226 | 225
2017-05-19 07:00 | 248 | 248
2017-05-19 07:30 | 270 | 269
2017-05-19 08:00 | 278 | 277
2017-05-19 08:30 | 280 | 279
2017-05-19 09:00 | 277 | 275
2017-05-19 09:30 | 273 | 272
2017-05-19 10:00 | 270 | 270
2017-05-19 10:30 | 270 | 270
2017-05-19 11:00 | 268 | 268
2017-05-19 11:30 | 266 | 265
2017-05-19 12:00 | 268 | 268
2017-05-19 12:30 | 271 | 270
2017-05-19 13:00 | 269 | 269
2017-05-19 13:30 | 265 | 264
2017-05-19 14:00 | 267 | 266
2017-05-19 14:30 | 269 | 269
2017-05-19 15:00 | 267 | 267
2017-05-19 15:30 | 269 | 269
2017-05-19 16:00 | 275 | 275
2017-05-19 16:30 | 283 | 282
2017-05-19 17:00 | 294 | 293
2017-05-19 17:30 | 300 | 300
2017-05-19 18:00 | 297 | 297
2017-05-19 18:30 | 289 | 289
2017-05-19 19:00 | 286 | 286
2017-05-19 19:30 | 279 | 279
2017-05-19 20:00 | 274 | 274
2017-05-19 20:30 | 271 | 270
2017-05-19 21:00 | 259 | 259
2017-05-19 21:30 | 249 | 249
2017-05-19 22:00 | 241 | 241
2017-05-19 22:30 | 239 | 239
2017-05-19 23:00 | 237 | 237
2017-05-19 23:30 | 222 | 222
2017-05-20 | 205 | 205
2017-05-20 00:30 | 186 | 186
2017-05-20 01:00 | 175 | 175
2017-05-20 01:30 | 167 | 167
2017-05-20 02:00 | 162 | 161
2017-05-20 02:30 | 158 | 158
2017-05-20 03:00 | 154 | 154
2017-05-20 03:30 | 154 | 154
2017-05-20 04:00 | 155 | 155
2017-05-20 04:30 | 155 | 155
2017-05-20 05:00 | 157 | 157
2017-05-20 05:30 | 162 | 162
2017-05-20 06:00 | 168 | 168
2017-05-20 06:30 | 178 | 178
2017-05-20 07:00 | 187 | 187
2017-05-20 07:30 | 197 | 197
2017-05-20 08:00 | 202 | 201
2017-05-20 08:30 | 205 | 204
2017-05-20 09:00 | 207 | 206
2017-05-20 09:30 | 203 | 203
2017-05-20 10:00 | 198 | 198
2017-05-20 10:30 | 198 | 198
2017-05-20 11:00 | 199 | 198
2017-05-20 11:30 | 198 | 198
2017-05-20 12:00 | 202 | 201
2017-05-20 12:30 | 205 | 205
2017-05-20 13:00 | 209 | 208
2017-05-20 13:30 | 201 | 201
2017-05-20 14:00 | 183 | 183
2017-05-20 14:30 | 186 | 186
2017-05-20 15:00 | 191 | 191
2017-05-20 15:30 | 196 | 196
2017-05-20 16:00 | 205 | 205
2017-05-20 16:30 | 215 | 215
2017-05-20 17:00 | 226 | 226
2017-05-20 17:30 | 236 | 235
2017-05-20 18:00 | 242 | 241
2017-05-20 18:30 | 240 | 239
2017-05-20 19:00 | 239 | 238
2017-05-20 19:30 | 234 | 233
2017-05-20 20:00 | 230 | 230
2017-05-20 20:30 | 228 | 228
2017-05-20 21:00 | 220 | 219
2017-05-20 21:30 | 213 | 212
2017-05-20 22:00 | 207 | 207
2017-05-20 22:30 | 207 | 207
2017-05-20 23:00 | 210 | 210
2017-05-20 23:30 | 199 | 199
2017-05-21 | 184 | 184
2017-05-21 00:30 | 169 | 169
2017-05-21 01:00 | 160 | 160
2017-05-21 01:30 | 152 | 152
2017-05-21 02:00 | 146 | 146
2017-05-21 02:30 | 143 | 143
2017-05-21 03:00 | 141 | 140
2017-05-21 03:30 | 140 | 140
2017-05-21 04:00 | 139 | 138
2017-05-21 04:30 | 138 | 138
2017-05-21 05:00 | 140 | 140
2017-05-21 05:30 | 143 | 143
2017-05-21 06:00 | 146 | 146
2017-05-21 06:30 | 151 | 151
2017-05-21 07:00 | 156 | 156
2017-05-21 07:30 | 164 | 164
2017-05-21 08:00 | 170 | 170
2017-05-21 08:30 | 175 | 175
2017-05-21 09:00 | 175 | 175
2017-05-21 09:30 | 175 | 175
2017-05-21 10:00 | 177 | 176
2017-05-21 10:30 | 177 | 176
2017-05-21 11:00 | 173 | 172
2017-05-21 11:30 | 168 | 167
2017-05-21 12:00 | 165 | 164
2017-05-21 12:30 | 162 | 161
2017-05-21 13:00 | 162 | 161
2017-05-21 13:30 | 165 | 164
2017-05-21 14:00 | 172 | 171
2017-05-21 14:30 | 177 | 175
2017-05-21 15:00 | 185 | 184
2017-05-21 15:30 | 194 | 193
2017-05-21 16:00 | 204 | 203
2017-05-21 16:30 | 215 | 213
2017-05-21 17:00 | 227 | 227
2017-05-21 17:30 | 242 | 241
2017-05-21 18:00 | 252 | 252
2017-05-21 18:30 | 248 | 248
2017-05-21 19:00 | 245 | 245
2017-05-21 19:30 | 239 | 238
2017-05-21 20:00 | 235 | 235
2017-05-21 20:30 | 233 | 233
2017-05-21 21:00 | 223 | 223
2017-05-21 21:30 | 214 | 214
2017-05-21 22:00 | 206 | 206
2017-05-21 22:30 | 203 | 203
2017-05-21 23:00 | 204 | 204
2017-05-21 23:30 | 192 | 192
2017-05-22 | 177 | 177
2017-05-22 00:30 | 163 | 163
2017-05-22 01:00 | 155 | 155
2017-05-22 01:30 | 149 | 149
2017-05-22 02:00 | 144 | 144
2017-05-22 02:30 | 142 | 141
2017-05-22 03:00 | 141 | 141
2017-05-22 03:30 | 141 | 141
2017-05-22 04:00 | 142 | 141
2017-05-22 04:30 | 147 | 147
2017-05-22 05:00 | 156 | 156
2017-05-22 05:30 | 170 | 170
2017-05-22 06:00 | 186 | 185
2017-05-22 06:30 | 209 | 208
2017-05-22 07:00 | 229 | 228
2017-05-22 07:30 | 243 | 243
2017-05-22 08:00 | 243 | 243
2017-05-22 08:30 | 235 | 235
2017-05-22 09:00 | 226 | 226
2017-05-22 09:30 | 221 | 221
2017-05-22 10:00 | 217 | 217
2017-05-22 10:30 | 216 | 216
2017-05-22 11:00 | 216 | 215
2017-05-22 11:30 | 217 | 217
2017-05-22 12:00 | 221 | 221
2017-05-22 12:30 | 224 | 224
2017-05-22 13:00 | 225 | 225
2017-05-22 13:30 | 229 | 229
2017-05-22 14:00 | 234 | 234
2017-05-22 14:30 | 237 | 236
2017-05-22 15:00 | 239 | 239
2017-05-22 15:30 | 246 | 246
2017-05-22 16:00 | 255 | 255
2017-05-22 16:30 | 264 | 264
2017-05-22 17:00 | 275 | 275
2017-05-22 17:30 | 287 | 287
2017-05-22 18:00 | 292 | 292
2017-05-22 18:30 | 285 | 285
2017-05-22 19:00 | 282 | 282
2017-05-22 19:30 | 274 | 274
2017-05-22 20:00 | 270 | 270
2017-05-22 20:30 | 265 | 265
2017-05-22 21:00 | 251 | 251
2017-05-22 21:30 | 239 | 239
2017-05-22 22:00 | 230 | 230
2017-05-22 22:30 | 225 | 224
2017-05-22 23:00 | 222 | 222
2017-05-22 23:30 | 209 | 208
2017-05-23 | 190 | 190
2017-05-23 00:30 | 175 | 174
2017-05-23 01:00 | 165 | 165
2017-05-23 01:30 | 159 | 159
2017-05-23 02:00 | 154 | 154
2017-05-23 02:30 | 151 | 151
2017-05-23 03:00 | 150 | 150
2017-05-23 03:30 | 150 | 150
2017-05-23 04:00 | 151 | 151
2017-05-23 04:30 | 155 | 155
2017-05-23 05:00 | 164 | 164
2017-05-23 05:30 | 178 | 177
2017-05-23 06:00 | 193 | 193
2017-05-23 06:30 | 216 | 216
2017-05-23 07:00 | 235 | 234
2017-05-23 07:30 | 243 | 243
2017-05-23 08:00 | 241 | 241
2017-05-23 08:30 | 232 | 232
2017-05-23 09:00 | 223 | 223
2017-05-23 09:30 | 218 | 218
2017-05-23 10:00 | 211 | 211
2017-05-23 10:30 | 208 | 207
2017-05-23 11:00 | 207 | 207
2017-05-23 11:30 | 208 | 207
2017-05-23 12:00 | 210 | 209
2017-05-23 12:30 | 213 | 213
2017-05-23 13:00 | 215 | 214
2017-05-23 13:30 | 220 | 219
2017-05-23 14:00 | 224 | 224
2017-05-23 14:30 | 230 | 230
2017-05-23 15:00 | 232 | 232
2017-05-23 15:30 | 238 | 238
2017-05-23 16:00 | 248 | 247
2017-05-23 16:30 | 256 | 256
2017-05-23 17:00 | 267 | 266
2017-05-23 17:30 | 278 | 278
2017-05-23 18:00 | 283 | 283
2017-05-23 18:30 | 276 | 275
2017-05-23 19:00 | 273 | 273
2017-05-23 19:30 | 268 | 266
2017-05-23 20:00 | 264 | 262
2017-05-23 20:30 | 259 | 258
2017-05-23 21:00 | 245 | 244
2017-05-23 21:30 | 234 | 234
2017-05-23 22:00 | 226 | 226
2017-05-23 22:30 | 221 | 221
2017-05-23 23:00 | 219 | 219
2017-05-23 23:30 | 205 | 205
2017-05-24 | 188 | 188
2017-05-24 00:30 | 173 | 173
2017-05-24 01:00 | 163 | 163
2017-05-24 01:30 | 156 | 156
2017-05-24 02:00 | 152 | 152
2017-05-24 02:30 | 150 | 150
2017-05-24 03:00 | 148 | 147
2017-05-24 03:30 | 149 | 149
2017-05-24 04:00 | 150 | 149
2017-05-24 04:30 | 153 | 153
2017-05-24 05:00 | 160 | 160
2017-05-24 05:30 | 175 | 175
2017-05-24 06:00 | 191 | 191
2017-05-24 06:30 | 214 | 214
2017-05-24 07:00 | 232 | 232
2017-05-24 07:30 | 246 | 246
2017-05-24 08:00 | 251 | 251
2017-05-24 08:30 | 245 | 245
2017-05-24 09:00 | 238 | 238
2017-05-24 09:30 | 232 | 232
2017-05-24 10:00 | 222 | 222
2017-05-24 10:30 | 213 | 212
2017-05-24 11:00 | 207 | 207
2017-05-24 11:30 | 204 | 204
2017-05-24 12:00 | 205 | 205
2017-05-24 12:30 | 207 | 207
2017-05-24 13:00 | 210 | 210
2017-05-24 13:30 | 216 | 216
2017-05-24 14:00 | 223 | 223
2017-05-24 14:30 | 229 | 229
2017-05-24 15:00 | 234 | 234
2017-05-24 15:30 | 241 | 241
2017-05-24 16:00 | 252 | 252
2017-05-24 16:30 | 262 | 262
2017-05-24 17:00 | 271 | 271
2017-05-24 17:30 | 282 | 282
2017-05-24 18:00 | 287 | 287
2017-05-24 18:30 | 280 | 280
2017-05-24 19:00 | 278 | 278
2017-05-24 19:30 | 270 | 270
2017-05-24 20:00 | 267 | 266
2017-05-24 20:30 | 264 | 264
2017-05-24 21:00 | 253 | 252
2017-05-24 21:30 | 242 | 242
2017-05-24 22:00 | 230 | 230
2017-05-24 22:30 | 222 | 221
2017-05-24 23:00 | 216 | 216
2017-05-24 23:30 | 201 | 201
2017-05-25 | 184 | 184
2017-05-25 00:30 | 167 | 167
2017-05-25 01:00 | 158 | 158
2017-05-25 01:30 | 151 | 151
2017-05-25 02:00 | 147 | 146
2017-05-25 02:30 | 145 | 144
2017-05-25 03:00 | 145 | 144
2017-05-25 03:30 | 144 | 144
2017-05-25 04:00 | 144 | 144
2017-05-25 04:30 | 149 | 149
2017-05-25 05:00 | 157 | 157
2017-05-25 05:30 | 169 | 169
2017-05-25 06:00 | 184 | 184
2017-05-25 06:30 | 208 | 207
2017-05-25 07:00 | 227 | 225
2017-05-25 07:30 | 237 | 236
2017-05-25 08:00 | 234 | 232
2017-05-25 08:30 | 223 | 222
2017-05-25 09:00 | 212 | 210
2017-05-25 09:30 | 205 | 203
2017-05-25 10:00 | 201 | 198
2017-05-25 10:30 | 196 | 193
2017-05-25 11:00 | 193 | 190
2017-05-25 11:30 | 192 | 189
2017-05-25 12:00 | 195 | 193
2017-05-25 12:30 | 199 | 197
2017-05-25 13:00 | 201 | 200
2017-05-25 13:30 | 208 | 206
2017-05-25 14:00 | 210 | 208
2017-05-25 14:30 | 215 | 213
2017-05-25 15:00 | 219 | 217
2017-05-25 15:30 | 225 | 224
2017-05-25 16:00 | 233 | 231
2017-05-25 16:30 | 243 | 241
2017-05-25 17:00 | 253 | 252
2017-05-25 17:30 | 265 | 263
2017-05-25 18:00 | 274 | 274
2017-05-25 18:30 | 269 | 269
2017-05-25 19:00 | 270 | 269
2017-05-25 19:30 | 264 | 264
2017-05-25 20:00 | 261 | 261
2017-05-25 20:30 | 257 | 257
2017-05-25 21:00 | 244 | 244
2017-05-25 21:30 | 230 | 230
2017-05-25 22:00 | 221 | 220
2017-05-25 22:30 | 215 | 215
2017-05-25 23:00 | 212 | 212
2017-05-25 23:30 | 200 | 200
2017-05-26 | 182 | 182
2017-05-26 00:30 | 167 | 166
2017-05-26 01:00 | 156 | 155
2017-05-26 01:30 | 149 | 149
2017-05-26 02:00 | 144 | 144
2017-05-26 02:30 | 142 | 142
2017-05-26 03:00 | 140 | 140
2017-05-26 03:30 | 141 | 141
2017-05-26 04:00 | 141 | 141
2017-05-26 04:30 | 146 | 146
2017-05-26 05:00 | 155 | 155
2017-05-26 05:30 | 170 | 169
2017-05-26 06:00 | 185 | 184
2017-05-26 06:30 | 209 | 207
2017-05-26 07:00 | 226 | 226
2017-05-26 07:30 | 238 | 238
2017-05-26 08:00 | 235 | 235
2017-05-26 08:30 | 226 | 226
2017-05-26 09:00 | 215 | 215
2017-05-26 09:30 | 206 | 206
2017-05-26 10:00 | 201 | 201
2017-05-26 10:30 | 197 | 197
2017-05-26 11:00 | 194 | 194
2017-05-26 11:30 | 194 | 193
2017-05-26 12:00 | 194 | 194
2017-05-26 12:30 | 196 | 196
2017-05-26 13:00 | 199 | 199
2017-05-26 13:30 | 203 | 203
2017-05-26 14:00 | 206 | 206
2017-05-26 14:30 | 211 | 211
2017-05-26 15:00 | 215 | 215
2017-05-26 15:30 | 221 | 221
2017-05-26 16:00 | 232 | 232
2017-05-26 16:30 | 241 | 240
2017-05-26 17:00 | 250 | 250
2017-05-26 17:30 | 259 | 259
2017-05-26 18:00 | 262 | 262
2017-05-26 18:30 | 256 | 255
2017-05-26 19:00 | 256 | 255
2017-05-26 19:30 | 249 | 249
2017-05-26 20:00 | 246 | 246
2017-05-26 20:30 | 244 | 244
2017-05-26 21:00 | 233 | 232
2017-05-26 21:30 | 222 | 222
2017-05-26 22:00 | 213 | 213
2017-05-26 22:30 | 209 | 209
2017-05-26 23:00 | 208 | 208
2017-05-26 23:30 | 197 | 197
2017-05-27 | 181 | 181
2017-05-27 00:30 | 165 | 164
2017-05-27 01:00 | 155 | 155
2017-05-27 01:30 | 148 | 148
2017-05-27 02:00 | 144 | 144
2017-05-27 02:30 | 141 | 141
2017-05-27 03:00 | 139 | 139
2017-05-27 03:30 | 138 | 138
2017-05-27 04:00 | 137 | 137
2017-05-27 04:30 | 138 | 138
2017-05-27 05:00 | 140 | 140
2017-05-27 05:30 | 145 | 145
2017-05-27 06:00 | 151 | 151
2017-05-27 06:30 | 161 | 161
2017-05-27 07:00 | 170 | 169
2017-05-27 07:30 | 179 | 178
2017-05-27 08:00 | 182 | 181
2017-05-27 08:30 | 183 | 182
2017-05-27 09:00 | 181 | 180
2017-05-27 09:30 | 176 | 175
2017-05-27 10:00 | 170 | 169
2017-05-27 10:30 | 167 | 166
2017-05-27 11:00 | 165 | 164
2017-05-27 11:30 | 166 | 164
2017-05-27 12:00 | 167 | 166
2017-05-27 12:30 | 163 | 162
2017-05-27 13:00 | 163 | 162
2017-05-27 13:30 | 163 | 162
2017-05-27 14:00 | 168 | 167
2017-05-27 14:30 | 172 | 170
2017-05-27 15:00 | 177 | 175
2017-05-27 15:30 | 186 | 184
2017-05-27 16:00 | 193 | 192
2017-05-27 16:30 | 205 | 203
2017-05-27 17:00 | 217 | 216
2017-05-27 17:30 | 227 | 226
2017-05-27 18:00 | 232 | 231
2017-05-27 18:30 | 228 | 228
2017-05-27 19:00 | 227 | 227
2017-05-27 19:30 | 222 | 222
2017-05-27 20:00 | 220 | 219
2017-05-27 20:30 | 221 | 220
2017-05-27 21:00 | 211 | 210
2017-05-27 21:30 | 202 | 202
2017-05-27 22:00 | 198 | 198
2017-05-27 22:30 | 197 | 197
2017-05-27 23:00 | 199 | 198
2017-05-27 23:30 | 188 | 188
2017-05-28 | 174 | 174
2017-05-28 00:30 | 160 | 160
2017-05-28 01:00 | 151 | 151
2017-05-28 01:30 | 144 | 144
2017-05-28 02:00 | 138 | 138
2017-05-28 02:30 | 135 | 135
2017-05-28 03:00 | 134 | 134
2017-05-28 03:30 | 138 | 138
2017-05-28 04:00 | 139 | 139
2017-05-28 04:30 | 139 | 139
2017-05-28 05:00 | 139 | 139
2017-05-28 05:30 | 143 | 143
2017-05-28 06:00 | 146 | 146
2017-05-28 06:30 | 152 | 152
2017-05-28 07:00 | 158 | 158
2017-05-28 07:30 | 165 | 165
2017-05-28 08:00 | 169 | 169
2017-05-28 08:30 | 171 | 171
2017-05-28 09:00 | 170 | 170
2017-05-28 09:30 | 168 | 168
2017-05-28 10:00 | 163 | 163
2017-05-28 10:30 | 159 | 159
2017-05-28 11:00 | 154 | 153
2017-05-28 11:30 | 152 | 152
2017-05-28 12:00 | 153 | 153
2017-05-28 12:30 | 154 | 154
2017-05-28 13:00 | 155 | 155
2017-05-28 13:30 | 160 | 159
2017-05-28 14:00 | 167 | 166
2017-05-28 14:30 | 174 | 173
2017-05-28 15:00 | 179 | 178
2017-05-28 15:30 | 186 | 185
2017-05-28 16:00 | 199 | 197
2017-05-28 16:30 | 213 | 211
2017-05-28 17:00 | 228 | 225
2017-05-28 17:30 | 243 | 242
2017-05-28 18:00 | 252 | 252
2017-05-28 18:30 | 247 | 247
2017-05-28 19:00 | 246 | 246
2017-05-28 19:30 | 239 | 239
2017-05-28 20:00 | 234 | 234
2017-05-28 20:30 | 232 | 231
2017-05-28 21:00 | 220 | 220
2017-05-28 21:30 | 213 | 213
2017-05-28 22:00 | 205 | 205
2017-05-28 22:30 | 202 | 201
2017-05-28 23:00 | 202 | 202
2017-05-28 23:30 | 192 | 192
2017-05-29 | 178 | 178
2017-05-29 00:30 | 163 | 163
2017-05-29 01:00 | 154 | 154
2017-05-29 01:30 | 148 | 148
2017-05-29 02:00 | 144 | 144
2017-05-29 02:30 | 142 | 142
2017-05-29 03:00 | 141 | 141
2017-05-29 03:30 | 140 | 140
2017-05-29 04:00 | 141 | 141
2017-05-29 04:30 | 147 | 147
2017-05-29 05:00 | 155 | 155
2017-05-29 05:30 | 170 | 170
2017-05-29 06:00 | 187 | 186
2017-05-29 06:30 | 213 | 213
2017-05-29 07:00 | 234 | 234
2017-05-29 07:30 | 247 | 247
2017-05-29 08:00 | 246 | 246
2017-05-29 08:30 | 237 | 237
2017-05-29 09:00 | 227 | 227
2017-05-29 09:30 | 219 | 219
2017-05-29 10:00 | 213 | 213
2017-05-29 10:30 | 207 | 207
2017-05-29 11:00 | 203 | 203
2017-05-29 11:30 | 202 | 202
2017-05-29 12:00 | 201 | 201
2017-05-29 12:30 | 202 | 202
2017-05-29 13:00 | 204 | 204
2017-05-29 13:30 | 210 | 210
2017-05-29 14:00 | 215 | 215
2017-05-29 14:30 | 220 | 220
2017-05-29 15:00 | 227 | 227
2017-05-29 15:30 | 234 | 234
2017-05-29 16:00 | 246 | 246
2017-05-29 16:30 | 256 | 256
2017-05-29 17:00 | 268 | 268
2017-05-29 17:30 | 282 | 282
2017-05-29 18:00 | 288 | 288
2017-05-29 18:30 | 282 | 281
2017-05-29 19:00 | 279 | 279
2017-05-29 19:30 | 272 | 271
2017-05-29 20:00 | 267 | 267
2017-05-29 20:30 | 263 | 263
2017-05-29 21:00 | 252 | 252
2017-05-29 21:30 | 241 | 241
2017-05-29 22:00 | 231 | 231
2017-05-29 22:30 | 223 | 223
2017-05-29 23:00 | 218 | 217
2017-05-29 23:30 | 206 | 205
2017-05-30 | 190 | 189
2017-05-30 00:30 | 173 | 173
2017-05-30 01:00 | 162 | 162
2017-05-30 01:30 | 156 | 156
2017-05-30 02:00 | 151 | 151
2017-05-30 02:30 | 149 | 149
2017-05-30 03:00 | 148 | 147
2017-05-30 03:30 | 147 | 147
2017-05-30 04:00 | 148 | 148
2017-05-30 04:30 | 154 | 154
2017-05-30 05:00 | 164 | 163
2017-05-30 05:30 | 178 | 177
2017-05-30 06:00 | 196 | 194
2017-05-30 06:30 | 222 | 222
2017-05-30 07:00 | 244 | 244
2017-05-30 07:30 | 267 | 267
2017-05-30 08:00 | 288 | 288
2017-05-30 08:30 | 269 | 269
2017-05-30 09:00 | 251 | 251
2017-05-30 09:30 | 238 | 238
2017-05-30 10:00 | 229 | 229
2017-05-30 10:30 | 222 | 221
2017-05-30 11:00 | 217 | 216
2017-05-30 11:30 | 215 | 215
2017-05-30 12:00 | 216 | 216
2017-05-30 12:30 | 218 | 218
2017-05-30 13:00 | 224 | 224
2017-05-30 13:30 | 214 | 214
2017-05-30 14:00 | 219 | 219
2017-05-30 14:30 | 225 | 225
2017-05-30 15:00 | 229 | 229
2017-05-30 15:30 | 236 | 236
2017-05-30 16:00 | 246 | 246
2017-05-30 16:30 | 258 | 258
2017-05-30 17:00 | 271 | 271
2017-05-30 17:30 | 287 | 287
2017-05-30 18:00 | 292 | 292
2017-05-30 18:30 | 286 | 286
2017-05-30 19:00 | 286 | 286
2017-05-30 19:30 | 279 | 279
2017-05-30 20:00 | 276 | 276
2017-05-30 20:30 | 272 | 272
2017-05-30 21:00 | 258 | 258
2017-05-30 21:30 | 244 | 243
2017-05-30 22:00 | 234 | 233
2017-05-30 22:30 | 228 | 227
2017-05-30 23:00 | 222 | 222
2017-05-30 23:30 | 209 | 209
2017-05-31 | 193 | 192
2017-05-31 00:30 | 177 | 177
2017-05-31 01:00 | 167 | 167
2017-05-31 01:30 | 159 | 159
2017-05-31 02:00 | 155 | 155
2017-05-31 02:30 | 152 | 152
2017-05-31 03:00 | 151 | 151
2017-05-31 03:30 | 151 | 151
2017-05-31 04:00 | 152 | 152
2017-05-31 04:30 | 158 | 158
2017-05-31 05:00 | 168 | 168
2017-05-31 05:30 | 184 | 183
2017-05-31 06:00 | 201 | 199
2017-05-31 06:30 | 229 | 228
2017-05-31 07:00 | 251 | 250
2017-05-31 07:30 | 258 | 257
2017-05-31 08:00 | 250 | 250
2017-05-31 08:30 | 237 | 237
2017-05-31 09:00 | 224 | 224
2017-05-31 09:30 | 213 | 213
2017-05-31 10:00 | 199 | 199
2017-05-31 10:30 | 194 | 192
2017-05-31 11:00 | 189 | 186
2017-05-31 11:30 | 183 | 181
2017-05-31 12:00 | 182 | 180
2017-05-31 12:30 | 186 | 184
2017-05-31 13:00 | 192 | 190
2017-05-31 13:30 | 195 | 193
2017-05-31 14:00 | 202 | 200
2017-05-31 14:30 | 208 | 206
2017-05-31 15:00 | 213 | 211
2017-05-31 15:30 | 223 | 220
2017-05-31 16:00 | 236 | 233
2017-05-31 16:30 | 250 | 248
2017-05-31 17:00 | 265 | 265
2017-05-31 17:30 | 282 | 281
2017-05-31 18:00 | 289 | 289
2017-05-31 18:30 | 288 | 287
2017-05-31 19:00 | 289 | 289
2017-05-31 19:30 | 284 | 284
2017-05-31 20:00 | 281 | 280
2017-05-31 20:30 | 278 | 278
2017-05-31 21:00 | 263 | 263
2017-05-31 21:30 | 253 | 253
2017-05-31 22:00 | 242 | 242
2017-05-31 22:30 | 237 | 236
2017-05-31 23:00 | 234 | 234
2017-05-31 23:30 | 220 | 220
2017-06-01 | 201 | 200
2017-06-01 00:30 | 183 | 183
2017-06-01 01:00 | 171 | 171
2017-06-01 01:30 | 163 | 163
2017-06-01 02:00 | 158 | 158
2017-06-01 02:30 | 155 | 155
2017-06-01 03:00 | 153 | 153
2017-06-01 03:30 | 154 | 154
2017-06-01 04:00 | 155 | 155
2017-06-01 04:30 | 161 | 161
2017-06-01 05:00 | 170 | 170
2017-06-01 05:30 | 187 | 187
2017-06-01 06:00 | 205 | 204
2017-06-01 06:30 | 233 | 232
2017-06-01 07:00 | 256 | 256
2017-06-01 07:30 | 273 | 273
2017-06-01 08:00 | 268 | 268
2017-06-01 08:30 | 254 | 254
2017-06-01 09:00 | 237 | 237
2017-06-01 09:30 | 225 | 224
2017-06-01 10:00 | 214 | 213
2017-06-01 10:30 | 205 | 205
2017-06-01 11:00 | 198 | 198
2017-06-01 11:30 | 194 | 194
2017-06-01 12:00 | 192 | 192
2017-06-01 12:30 | 193 | 192
2017-06-01 13:00 | 194 | 193
2017-06-01 13:30 | 200 | 198
2017-06-01 14:00 | 205 | 203
2017-06-01 14:30 | 210 | 208
2017-06-01 15:00 | 216 | 214
2017-06-01 15:30 | 224 | 223
2017-06-01 16:00 | 237 | 235
2017-06-01 16:30 | 250 | 249
2017-06-01 17:00 | 265 | 265
2017-06-01 17:30 | 281 | 280
2017-06-01 18:00 | 292 | 291
2017-06-01 18:30 | 292 | 292
2017-06-01 19:00 | 294 | 294
2017-06-01 19:30 | 291 | 290
2017-06-01 20:00 | 288 | 288
2017-06-01 20:30 | 285 | 284
2017-06-01 21:00 | 274 | 274
2017-06-01 21:30 | 260 | 260
2017-06-01 22:00 | 249 | 249
2017-06-01 22:30 | 241 | 241
2017-06-01 23:00 | 236 | 235
2017-06-01 23:30 | 222 | 221
2017-06-02 | 204 | 202
2017-06-02 00:30 | 186 | 186
2017-06-02 01:00 | 174 | 174
2017-06-02 01:30 | 166 | 166
2017-06-02 02:00 | 162 | 161
2017-06-02 02:30 | 158 | 157
2017-06-02 03:00 | 155 | 155
2017-06-02 03:30 | 156 | 155
2017-06-02 04:00 | 157 | 157
2017-06-02 04:30 | 163 | 162
2017-06-02 05:00 | 173 | 172
2017-06-02 05:30 | 190 | 188
2017-06-02 06:00 | 208 | 207
2017-06-02 06:30 | 237 | 237
2017-06-02 07:00 | 261 | 261
2017-06-02 07:30 | 276 | 276
2017-06-02 08:00 | 271 | 271
2017-06-02 08:30 | 256 | 256
2017-06-02 09:00 | 239 | 239
2017-06-02 09:30 | 226 | 226
2017-06-02 10:00 | 216 | 216
2017-06-02 10:30 | 206 | 206
2017-06-02 11:00 | 199 | 199
2017-06-02 11:30 | 195 | 195
2017-06-02 12:00 | 193 | 193
2017-06-02 12:30 | 192 | 191
2017-06-02 13:00 | 192 | 192
2017-06-02 13:30 | 195 | 195
2017-06-02 14:00 | 199 | 199
2017-06-02 14:30 | 204 | 204
2017-06-02 15:00 | 211 | 211
2017-06-02 15:30 | 219 | 219
2017-06-02 16:00 | 231 | 231
2017-06-02 16:30 | 244 | 244
2017-06-02 17:00 | 257 | 257
2017-06-02 17:30 | 270 | 270
2017-06-02 18:00 | 276 | 276
2017-06-02 18:30 | 273 | 273
2017-06-02 19:00 | 274 | 274
2017-06-02 19:30 | 271 | 271
2017-06-02 20:00 | 269 | 269
2017-06-02 20:30 | 268 | 268
2017-06-02 21:00 | 260 | 260
2017-06-02 21:30 | 249 | 249
2017-06-02 22:00 | 239 | 238
2017-06-02 22:30 | 234 | 233
2017-06-02 23:00 | 232 | 231
2017-06-02 23:30 | 219 | 219
2017-06-03 | 202 | 202
2017-06-03 00:30 | 185 | 185
2017-06-03 01:00 | 174 | 174
2017-06-03 01:30 | 165 | 165
2017-06-03 02:00 | 159 | 159
2017-06-03 02:30 | 157 | 156
2017-06-03 03:00 | 154 | 154
2017-06-03 03:30 | 154 | 153
2017-06-03 04:00 | 154 | 153
2017-06-03 04:30 | 156 | 155
2017-06-03 05:00 | 159 | 158
2017-06-03 05:30 | 167 | 166
2017-06-03 06:00 | 173 | 172
2017-06-03 06:30 | 185 | 184
2017-06-03 07:00 | 196 | 194
2017-06-03 07:30 | 207 | 205
2017-06-03 08:00 | 210 | 210
2017-06-03 08:30 | 211 | 211
2017-06-03 09:00 | 206 | 206
2017-06-03 09:30 | 198 | 198
2017-06-03 10:00 | 189 | 189
2017-06-03 10:30 | 180 | 180
2017-06-03 11:00 | 170 | 170
2017-06-03 11:30 | 163 | 161
2017-06-03 12:00 | 160 | 158
2017-06-03 12:30 | 158 | 157
2017-06-03 13:00 | 160 | 158
2017-06-03 13:30 | 162 | 160
2017-06-03 14:00 | 165 | 163
2017-06-03 14:30 | 171 | 169
2017-06-03 15:00 | 179 | 177
2017-06-03 15:30 | 190 | 188
2017-06-03 16:00 | 200 | 198
2017-06-03 16:30 | 212 | 210
2017-06-03 17:00 | 227 | 226
2017-06-03 17:30 | 241 | 240
2017-06-03 18:00 | 248 | 248
2017-06-03 18:30 | 246 | 246
2017-06-03 19:00 | 246 | 246
2017-06-03 19:30 | 243 | 243
2017-06-03 20:00 | 241 | 240
2017-06-03 20:30 | 242 | 242
2017-06-03 21:00 | 231 | 231
2017-06-03 21:30 | 222 | 222
2017-06-03 22:00 | 216 | 216
2017-06-03 22:30 | 215 | 215
2017-06-03 23:00 | 215 | 215
2017-06-03 23:30 | 205 | 205
2017-06-04 | 191 | 191
2017-06-04 00:30 | 176 | 176
2017-06-04 01:00 | 166 | 166
2017-06-04 01:30 | 159 | 159
2017-06-04 02:00 | 153 | 153
2017-06-04 02:30 | 149 | 149
2017-06-04 03:00 | 146 | 146
2017-06-04 03:30 | 145 | 145
2017-06-04 04:00 | 145 | 145
2017-06-04 04:30 | 145 | 145
2017-06-04 05:00 | 147 | 147
2017-06-04 05:30 | 151 | 151
2017-06-04 06:00 | 156 | 156
2017-06-04 06:30 | 164 | 164
2017-06-04 07:00 | 170 | 170
2017-06-04 07:30 | 178 | 177
2017-06-04 08:00 | 182 | 182
2017-06-04 08:30 | 184 | 184
2017-06-04 09:00 | 183 | 183
2017-06-04 09:30 | 178 | 178
2017-06-04 10:00 | 171 | 171
2017-06-04 10:30 | 164 | 164
2017-06-04 11:00 | 158 | 158
2017-06-04 11:30 | 154 | 154
2017-06-04 12:00 | 154 | 154
2017-06-04 12:30 | 155 | 155
2017-06-04 13:00 | 161 | 161
2017-06-04 13:30 | 160 | 160
2017-06-04 14:00 | 165 | 165
2017-06-04 14:30 | 172 | 172
2017-06-04 15:00 | 181 | 181
2017-06-04 15:30 | 193 | 192
2017-06-04 16:00 | 204 | 204
2017-06-04 16:30 | 217 | 216
2017-06-04 17:00 | 233 | 232
2017-06-04 17:30 | 248 | 248
2017-06-04 18:00 | 258 | 257
2017-06-04 18:30 | 256 | 255
2017-06-04 19:00 | 255 | 254
2017-06-04 19:30 | 250 | 250
2017-06-04 20:00 | 246 | 246
2017-06-04 20:30 | 246 | 245
2017-06-04 21:00 | 236 | 235
2017-06-04 21:30 | 227 | 226
2017-06-04 22:00 | 220 | 220
2017-06-04 22:30 | 215 | 215
2017-06-04 23:00 | 214 | 214
2017-06-04 23:30 | 203 | 203
2017-06-05 | 188 | 188
2017-06-05 00:30 | 174 | 174
2017-06-05 01:00 | 165 | 164
2017-06-05 01:30 | 159 | 158
2017-06-05 02:00 | 153 | 153
2017-06-05 02:30 | 150 | 149
2017-06-05 03:00 | 149 | 149
2017-06-05 03:30 | 149 | 149
2017-06-05 04:00 | 150 | 150
2017-06-05 04:30 | 157 | 157
2017-06-05 05:00 | 167 | 167
2017-06-05 05:30 | 183 | 182
2017-06-05 06:00 | 202 | 201
2017-06-05 06:30 | 230 | 230
2017-06-05 07:00 | 255 | 255
2017-06-05 07:30 | 269 | 269
2017-06-05 08:00 | 265 | 265
2017-06-05 08:30 | 250 | 250
2017-06-05 09:00 | 234 | 234
2017-06-05 09:30 | 223 | 223
2017-06-05 10:00 | 213 | 213
2017-06-05 10:30 | 204 | 204
2017-06-05 11:00 | 200 | 200
2017-06-05 11:30 | 197 | 197
2017-06-05 12:00 | 196 | 196
2017-06-05 12:30 | 196 | 196
2017-06-05 13:00 | 198 | 198
2017-06-05 13:30 | 202 | 202
2017-06-05 14:00 | 209 | 209
2017-06-05 14:30 | 216 | 216
2017-06-05 15:00 | 220 | 220
2017-06-05 15:30 | 228 | 228
2017-06-05 16:00 | 240 | 240
2017-06-05 16:30 | 252 | 252
2017-06-05 17:00 | 269 | 269
2017-06-05 17:30 | 288 | 287
2017-06-05 18:00 | 295 | 294
2017-06-05 18:30 | 289 | 289
2017-06-05 19:00 | 289 | 289
2017-06-05 19:30 | 284 | 284
2017-06-05 20:00 | 279 | 279
2017-06-05 20:30 | 277 | 277
2017-06-05 21:00 | 263 | 262
2017-06-05 21:30 | 251 | 250
2017-06-05 22:00 | 241 | 240
2017-06-05 22:30 | 232 | 231
2017-06-05 23:00 | 229 | 228
2017-06-05 23:30 | 215 | 215
2017-06-06 | 199 | 199
2017-06-06 00:30 | 182 | 182
2017-06-06 01:00 | 172 | 172
2017-06-06 01:30 | 164 | 164
2017-06-06 02:00 | 159 | 159
2017-06-06 02:30 | 156 | 156
2017-06-06 03:00 | 154 | 154
2017-06-06 03:30 | 154 | 154
2017-06-06 04:00 | 155 | 155
2017-06-06 04:30 | 162 | 162
2017-06-06 05:00 | 172 | 172
2017-06-06 05:30 | 187 | 187
2017-06-06 06:00 | 206 | 205
2017-06-06 06:30 | 234 | 233
2017-06-06 07:00 | 259 | 259
2017-06-06 07:30 | 275 | 275
2017-06-06 08:00 | 268 | 268
2017-06-06 08:30 | 251 | 251
2017-06-06 09:00 | 235 | 235
2017-06-06 09:30 | 224 | 224
2017-06-06 10:00 | 214 | 214
2017-06-06 10:30 | 205 | 205
2017-06-06 11:00 | 201 | 200
2017-06-06 11:30 | 197 | 196
2017-06-06 12:00 | 194 | 194
2017-06-06 12:30 | 199 | 199
2017-06-06 13:00 | 199 | 199
2017-06-06 13:30 | 199 | 199
2017-06-06 14:00 | 203 | 203
2017-06-06 14:30 | 207 | 207
2017-06-06 15:00 | 212 | 212
2017-06-06 15:30 | 221 | 221
2017-06-06 16:00 | 234 | 234
2017-06-06 16:30 | 249 | 249
2017-06-06 17:00 | 266 | 266
2017-06-06 17:30 | 284 | 284
2017-06-06 18:00 | 294 | 294
2017-06-06 18:30 | 292 | 292
2017-06-06 19:00 | 294 | 294
2017-06-06 19:30 | 291 | 291
2017-06-06 20:00 | 289 | 288
2017-06-06 20:30 | 288 | 288
2017-06-06 21:00 | 275 | 275
2017-06-06 21:30 | 262 | 262
2017-06-06 22:00 | 252 | 251
2017-06-06 22:30 | 244 | 243
2017-06-06 23:00 | 238 | 238
2017-06-06 23:30 | 224 | 224
2017-06-07 | 205 | 204
2017-06-07 00:30 | 187 | 187
2017-06-07 01:00 | 175 | 175
2017-06-07 01:30 | 168 | 167
2017-06-07 02:00 | 162 | 162
2017-06-07 02:30 | 159 | 159
2017-06-07 03:00 | 158 | 158
2017-06-07 03:30 | 158 | 157
2017-06-07 04:00 | 160 | 159
2017-06-07 04:30 | 167 | 167
2017-06-07 05:00 | 177 | 177
2017-06-07 05:30 | 196 | 196
2017-06-07 06:00 | 217 | 216
2017-06-07 06:30 | 249 | 248
2017-06-07 07:00 | 275 | 275
2017-06-07 07:30 | 290 | 290
2017-06-07 08:00 | 283 | 282
2017-06-07 08:30 | 264 | 264
2017-06-07 09:00 | 245 | 245
2017-06-07 09:30 | 229 | 229
2017-06-07 10:00 | 216 | 216
2017-06-07 10:30 | 206 | 206
2017-06-07 11:00 | 200 | 199
2017-06-07 11:30 | 192 | 192
2017-06-07 12:00 | 189 | 188
2017-06-07 12:30 | 190 | 190
2017-06-07 13:00 | 193 | 192
2017-06-07 13:30 | 195 | 194
2017-06-07 14:00 | 198 | 198
2017-06-07 14:30 | 204 | 203
2017-06-07 15:00 | 211 | 210
2017-06-07 15:30 | 221 | 219
2017-06-07 16:00 | 235 | 234
2017-06-07 16:30 | 251 | 250
2017-06-07 17:00 | 271 | 270
2017-06-07 17:30 | 293 | 293
2017-06-07 18:00 | 306 | 306
2017-06-07 18:30 | 305 | 305
2017-06-07 19:00 | 308 | 308
2017-06-07 19:30 | 304 | 304
2017-06-07 20:00 | 302 | 302
2017-06-07 20:30 | 300 | 300
2017-06-07 21:00 | 288 | 288
2017-06-07 21:30 | 273 | 273
2017-06-07 22:00 | 259 | 259
2017-06-07 22:30 | 250 | 250
2017-06-07 23:00 | 241 | 241
2017-06-07 23:30 | 226 | 226
2017-06-08 | 208 | 208
2017-06-08 00:30 | 190 | 190
2017-06-08 01:00 | 179 | 179
2017-06-08 01:30 | 171 | 171
2017-06-08 02:00 | 165 | 165
2017-06-08 02:30 | 163 | 162
2017-06-08 03:00 | 160 | 160
2017-06-08 03:30 | 160 | 160
2017-06-08 04:00 | 162 | 162
2017-06-08 04:30 | 169 | 169
2017-06-08 05:00 | 181 | 181
2017-06-08 05:30 | 199 | 199
2017-06-08 06:00 | 219 | 218
2017-06-08 06:30 | 250 | 249
2017-06-08 07:00 | 275 | 275
2017-06-08 07:30 | 293 | 293
2017-06-08 08:00 | 285 | 285
2017-06-08 08:30 | 268 | 268
2017-06-08 09:00 | 247 | 247
2017-06-08 09:30 | 231 | 231
2017-06-08 10:00 | 219 | 219
2017-06-08 10:30 | 210 | 210
2017-06-08 11:00 | 202 | 202
2017-06-08 11:30 | 196 | 196
2017-06-08 12:00 | 191 | 191
2017-06-08 12:30 | 191 | 190
2017-06-08 13:00 | 192 | 192
2017-06-08 13:30 | 196 | 195
2017-06-08 14:00 | 201 | 200
2017-06-08 14:30 | 206 | 205
2017-06-08 15:00 | 211 | 210
2017-06-08 15:30 | 220 | 219
2017-06-08 16:00 | 234 | 234
2017-06-08 16:30 | 249 | 248
2017-06-08 17:00 | 267 | 265
2017-06-08 17:30 | 287 | 286
2017-06-08 18:00 | 299 | 299
2017-06-08 18:30 | 298 | 298
2017-06-08 19:00 | 301 | 301
2017-06-08 19:30 | 299 | 299
2017-06-08 20:00 | 298 | 298
2017-06-08 20:30 | 298 | 298
2017-06-08 21:00 | 286 | 286
2017-06-08 21:30 | 272 | 272
2017-06-08 22:00 | 257 | 256
2017-06-08 22:30 | 248 | 248
2017-06-08 23:00 | 242 | 242
2017-06-08 23:30 | 228 | 228
2017-06-09 | 209 | 209
2017-06-09 00:30 | 191 | 191
2017-06-09 01:00 | 179 | 179
2017-06-09 01:30 | 171 | 171
2017-06-09 02:00 | 165 | 165
2017-06-09 02:30 | 161 | 161
2017-06-09 03:00 | 160 | 160
2017-06-09 03:30 | 160 | 160
2017-06-09 04:00 | 163 | 162
2017-06-09 04:30 | 168 | 168
2017-06-09 05:00 | 177 | 177
2017-06-09 05:30 | 195 | 195
2017-06-09 06:00 | 214 | 214
2017-06-09 06:30 | 243 | 242
2017-06-09 07:00 | 268 | 266
2017-06-09 07:30 | 285 | 284
2017-06-09 08:00 | 278 | 278
2017-06-09 08:30 | 260 | 260
2017-06-09 09:00 | 240 | 240
2017-06-09 09:30 | 224 | 224
2017-06-09 10:00 | 217 | 217
2017-06-09 10:30 | 210 | 210
2017-06-09 11:00 | 206 | 206
2017-06-09 11:30 | 210 | 209
2017-06-09 12:00 | 216 | 216
2017-06-09 12:30 | 218 | 218
2017-06-09 13:00 | 217 | 217
2017-06-09 13:30 | 227 | 227
2017-06-09 14:00 | 228 | 228
2017-06-09 14:30 | 231 | 231
2017-06-09 15:00 | 235 | 235
2017-06-09 15:30 | 239 | 239
2017-06-09 16:00 | 246 | 246
2017-06-09 16:30 | 256 | 256
2017-06-09 17:00 | 267 | 267
2017-06-09 17:30 | 278 | 278
2017-06-09 18:00 | 282 | 282
2017-06-09 18:30 | 278 | 278
2017-06-09 19:00 | 278 | 278
2017-06-09 19:30 | 274 | 274
2017-06-09 20:00 | 271 | 271
2017-06-09 20:30 | 269 | 269
2017-06-09 21:00 | 260 | 260
2017-06-09 21:30 | 250 | 250
2017-06-09 22:00 | 241 | 241
2017-06-09 22:30 | 237 | 236
2017-06-09 23:00 | 235 | 234
2017-06-09 23:30 | 220 | 220
2017-06-10 | 202 | 202
2017-06-10 00:30 | 186 | 186
2017-06-10 01:00 | 175 | 175
2017-06-10 01:30 | 166 | 166
2017-06-10 02:00 | 160 | 160
2017-06-10 02:30 | 157 | 157
2017-06-10 03:00 | 154 | 154
2017-06-10 03:30 | 153 | 152
2017-06-10 04:00 | 152 | 152
2017-06-10 04:30 | 155 | 154
2017-06-10 05:00 | 156 | 156
2017-06-10 05:30 | 161 | 161
2017-06-10 06:00 | 166 | 166
2017-06-10 06:30 | 177 | 177
2017-06-10 07:00 | 187 | 187
2017-06-10 07:30 | 195 | 195
2017-06-10 08:00 | 200 | 200
2017-06-10 08:30 | 203 | 203
2017-06-10 09:00 | 199 | 199
2017-06-10 09:30 | 193 | 193
2017-06-10 10:00 | 186 | 186
2017-06-10 10:30 | 183 | 182
2017-06-10 11:00 | 185 | 184
2017-06-10 11:30 | 185 | 185
2017-06-10 12:00 | 187 | 187
2017-06-10 12:30 | 189 | 188
2017-06-10 13:00 | 187 | 187
2017-06-10 13:30 | 184 | 183
2017-06-10 14:00 | 182 | 182
2017-06-10 14:30 | 184 | 184
2017-06-10 15:00 | 187 | 187
2017-06-10 15:30 | 192 | 192
2017-06-10 16:00 | 203 | 202
2017-06-10 16:30 | 214 | 214
2017-06-10 17:00 | 232 | 232
2017-06-10 17:30 | 247 | 246
2017-06-10 18:00 | 251 | 250
2017-06-10 18:30 | 248 | 248
2017-06-10 19:00 | 247 | 246
2017-06-10 19:30 | 242 | 242
2017-06-10 20:00 | 241 | 240
2017-06-10 20:30 | 240 | 239
2017-06-10 21:00 | 230 | 230
2017-06-10 21:30 | 223 | 223
2017-06-10 22:00 | 218 | 218
2017-06-10 22:30 | 217 | 217
2017-06-10 23:00 | 218 | 218
2017-06-10 23:30 | 206 | 206
2017-06-11 | 193 | 193
2017-06-11 00:30 | 179 | 179
2017-06-11 01:00 | 167 | 167
2017-06-11 01:30 | 158 | 158
2017-06-11 02:00 | 152 | 152
2017-06-11 02:30 | 150 | 149
2017-06-11 03:00 | 148 | 147
2017-06-11 03:30 | 146 | 146
2017-06-11 04:00 | 146 | 145
2017-06-11 04:30 | 146 | 145
2017-06-11 05:00 | 146 | 146
2017-06-11 05:30 | 150 | 149
2017-06-11 06:00 | 154 | 154
2017-06-11 06:30 | 160 | 160
2017-06-11 07:00 | 167 | 167
2017-06-11 07:30 | 178 | 178
2017-06-11 08:00 | 187 | 187
2017-06-11 08:30 | 199 | 199
2017-06-11 09:00 | 212 | 212
2017-06-11 09:30 | 215 | 215
2017-06-11 10:00 | 216 | 216
2017-06-11 10:30 | 216 | 216
2017-06-11 11:00 | 215 | 215
2017-06-11 11:30 | 214 | 214
2017-06-11 12:00 | 212 | 212
2017-06-11 12:30 | 213 | 213
2017-06-11 13:00 | 205 | 205
2017-06-11 13:30 | 209 | 209
2017-06-11 14:00 | 213 | 213
2017-06-11 14:30 | 215 | 215
2017-06-11 15:00 | 214 | 214
2017-06-11 15:30 | 216 | 216
2017-06-11 16:00 | 221 | 221
2017-06-11 16:30 | 231 | 231
2017-06-11 17:00 | 246 | 245
2017-06-11 17:30 | 263 | 263
2017-06-11 18:00 | 273 | 273
2017-06-11 18:30 | 271 | 271
2017-06-11 19:00 | 269 | 269
2017-06-11 19:30 | 263 | 263
2017-06-11 20:00 | 259 | 259
2017-06-11 20:30 | 256 | 256
2017-06-11 21:00 | 246 | 246
2017-06-11 21:30 | 237 | 236
2017-06-11 22:00 | 229 | 229
2017-06-11 22:30 | 224 | 223
2017-06-11 23:00 | 220 | 219
2017-06-11 23:30 | 208 | 208
2017-06-12 | 191 | 191
2017-06-12 00:30 | 176 | 176
2017-06-12 01:00 | 166 | 166
2017-06-12 01:30 | 159 | 158
2017-06-12 02:00 | 154 | 153
2017-06-12 02:30 | 150 | 149
2017-06-12 03:00 | 149 | 149
2017-06-12 03:30 | 150 | 150
2017-06-12 04:00 | 150 | 150
2017-06-12 04:30 | 154 | 154
2017-06-12 05:00 | 163 | 163
2017-06-12 05:30 | 178 | 178
2017-06-12 06:00 | 196 | 196
2017-06-12 06:30 | 226 | 225
2017-06-12 07:00 | 247 | 246
2017-06-12 07:30 | 265 | 263
2017-06-12 08:00 | 269 | 268
2017-06-12 08:30 | 261 | 260
2017-06-12 09:00 | 247 | 247
2017-06-12 09:30 | 241 | 241
2017-06-12 10:00 | 240 | 240
2017-06-12 10:30 | 238 | 238
2017-06-12 11:00 | 233 | 233
2017-06-12 11:30 | 229 | 229
2017-06-12 12:00 | 225 | 225
2017-06-12 12:30 | 225 | 225
2017-06-12 13:00 | 228 | 228
2017-06-12 13:30 | 237 | 237
2017-06-12 14:00 | 245 | 245
2017-06-12 14:30 | 244 | 244
2017-06-12 15:00 | 246 | 246
2017-06-12 15:30 | 249 | 249
2017-06-12 16:00 | 257 | 257
2017-06-12 16:30 | 268 | 268
2017-06-12 17:00 | 286 | 285
2017-06-12 17:30 | 303 | 303
2017-06-12 18:00 | 306 | 306
2017-06-12 18:30 | 301 | 301
2017-06-12 19:00 | 300 | 300
2017-06-12 19:30 | 295 | 295
2017-06-12 20:00 | 289 | 288
2017-06-12 20:30 | 287 | 285
2017-06-12 21:00 | 274 | 273
2017-06-12 21:30 | 260 | 259
2017-06-12 22:00 | 248 | 248
2017-06-12 22:30 | 239 | 239
2017-06-12 23:00 | 236 | 235
2017-06-12 23:30 | 223 | 222
2017-06-13 | 205 | 204
2017-06-13 00:30 | 188 | 188
2017-06-13 01:00 | 177 | 177
2017-06-13 01:30 | 168 | 168
2017-06-13 02:00 | 162 | 162
2017-06-13 02:30 | 160 | 160
2017-06-13 03:00 | 157 | 157
2017-06-13 03:30 | 157 | 157
2017-06-13 04:00 | 159 | 159
2017-06-13 04:30 | 164 | 164
2017-06-13 05:00 | 174 | 174
2017-06-13 05:30 | 187 | 187
2017-06-13 06:00 | 205 | 204
2017-06-13 06:30 | 233 | 231
2017-06-13 07:00 | 254 | 254
2017-06-13 07:30 | 275 | 275
2017-06-13 08:00 | 282 | 282
2017-06-13 08:30 | 279 | 278
2017-06-13 09:00 | 275 | 275
2017-06-13 09:30 | 275 | 275
2017-06-13 10:00 | 274 | 274
2017-06-13 10:30 | 274 | 274
2017-06-13 11:00 | 272 | 272
2017-06-13 11:30 | 271 | 271
2017-06-13 12:00 | 275 | 275
2017-06-13 12:30 | 280 | 280
2017-06-13 13:00 | 282 | 282
2017-06-13 13:30 | 284 | 284
2017-06-13 14:00 | 282 | 281
2017-06-13 14:30 | 277 | 277
2017-06-13 15:00 | 276 | 276
2017-06-13 15:30 | 277 | 277
2017-06-13 16:00 | 284 | 284
2017-06-13 16:30 | 294 | 293
2017-06-13 17:00 | 307 | 307
2017-06-13 17:30 | 322 | 322
2017-06-13 18:00 | 326 | 326
2017-06-13 18:30 | 321 | 321
2017-06-13 19:00 | 319 | 319
2017-06-13 19:30 | 311 | 311
2017-06-13 20:00 | 306 | 306
2017-06-13 20:30 | 303 | 303
2017-06-13 21:00 | 288 | 288
2017-06-13 21:30 | 273 | 273
2017-06-13 22:00 | 262 | 261
2017-06-13 22:30 | 252 | 251
2017-06-13 23:00 | 247 | 246
2017-06-13 23:30 | 232 | 232
2017-06-14 | 211 | 210
2017-06-14 00:30 | 193 | 193
2017-06-14 01:00 | 180 | 180
2017-06-14 01:30 | 174 | 174
2017-06-14 02:00 | 169 | 169
2017-06-14 02:30 | 166 | 166
2017-06-14 03:00 | 164 | 164
2017-06-14 03:30 | 164 | 164
2017-06-14 04:00 | 165 | 165
2017-06-14 04:30 | 166 | 166
2017-06-14 05:00 | 178 | 178
2017-06-14 05:30 | 190 | 190
2017-06-14 06:00 | 207 | 206
2017-06-14 06:30 | 235 | 235
2017-06-14 07:00 | 258 | 258
2017-06-14 07:30 | 277 | 277
2017-06-14 08:00 | 278 | 278
2017-06-14 08:30 | 270 | 270
2017-06-14 09:00 | 263 | 263
2017-06-14 09:30 | 262 | 262
2017-06-14 10:00 | 265 | 265
2017-06-14 10:30 | 264 | 264
2017-06-14 11:00 | 256 | 256
2017-06-14 11:30 | 249 | 249
2017-06-14 12:00 | 254 | 254
2017-06-14 12:30 | 254 | 254
2017-06-14 13:00 | 260 | 260
2017-06-14 13:30 | 260 | 260
2017-06-14 14:00 | 264 | 264
2017-06-14 14:30 | 266 | 266
2017-06-14 15:00 | 263 | 263
2017-06-14 15:30 | 265 | 265
2017-06-14 16:00 | 271 | 271
2017-06-14 16:30 | 282 | 282
2017-06-14 17:00 | 297 | 297
2017-06-14 17:30 | 312 | 311
2017-06-14 18:00 | 316 | 316
2017-06-14 18:30 | 311 | 311
2017-06-14 19:00 | 309 | 309
2017-06-14 19:30 | 302 | 302
2017-06-14 20:00 | 297 | 297
2017-06-14 20:30 | 294 | 294
2017-06-14 21:00 | 281 | 281
2017-06-14 21:30 | 266 | 266
2017-06-14 22:00 | 255 | 255
2017-06-14 22:30 | 247 | 246
2017-06-14 23:00 | 239 | 239
2017-06-14 23:30 | 225 | 225
2017-06-15 | 208 | 208
2017-06-15 00:30 | 189 | 189
2017-06-15 01:00 | 179 | 179
2017-06-15 01:30 | 169 | 169
2017-06-15 02:00 | 164 | 164
2017-06-15 02:30 | 161 | 160
2017-06-15 03:00 | 159 | 159
2017-06-15 03:30 | 159 | 159
2017-06-15 04:00 | 160 | 160
2017-06-15 04:30 | 166 | 166
2017-06-15 05:00 | 174 | 174
2017-06-15 05:30 | 189 | 188
2017-06-15 06:00 | 205 | 204
2017-06-15 06:30 | 231 | 229
2017-06-15 07:00 | 251 | 251
2017-06-15 07:30 | 268 | 267
2017-06-15 08:00 | 266 | 265
2017-06-15 08:30 | 259 | 257
2017-06-15 09:00 | 247 | 246
2017-06-15 09:30 | 236 | 235
2017-06-15 10:00 | 226 | 225
2017-06-15 10:30 | 222 | 221
2017-06-15 11:00 | 225 | 224
2017-06-15 11:30 | 233 | 232
2017-06-15 12:00 | 222 | 221
2017-06-15 12:30 | 223 | 222
2017-06-15 13:00 | 225 | 224
2017-06-15 13:30 | 229 | 227
2017-06-15 14:00 | 234 | 233
2017-06-15 14:30 | 238 | 236
2017-06-15 15:00 | 239 | 237
2017-06-15 15:30 | 243 | 242
2017-06-15 16:00 | 250 | 249
2017-06-15 16:30 | 262 | 261
2017-06-15 17:00 | 275 | 274
2017-06-15 17:30 | 290 | 290
2017-06-15 18:00 | 298 | 298
2017-06-15 18:30 | 295 | 295
2017-06-15 19:00 | 294 | 294
2017-06-15 19:30 | 289 | 289
2017-06-15 20:00 | 284 | 284
2017-06-15 20:30 | 284 | 284
2017-06-15 21:00 | 273 | 273
2017-06-15 21:30 | 259 | 259
2017-06-15 22:00 | 248 | 248
2017-06-15 22:30 | 243 | 243
2017-06-15 23:00 | 237 | 237
2017-06-15 23:30 | 223 | 223
2017-06-16 | 205 | 205
2017-06-16 00:30 | 189 | 189
2017-06-16 01:00 | 177 | 177
2017-06-16 01:30 | 168 | 168
2017-06-16 02:00 | 163 | 163
2017-06-16 02:30 | 161 | 160
2017-06-16 03:00 | 158 | 158
2017-06-16 03:30 | 159 | 158
2017-06-16 04:00 | 160 | 160
2017-06-16 04:30 | 165 | 165
2017-06-16 05:00 | 173 | 173
2017-06-16 05:30 | 187 | 187
2017-06-16 06:00 | 204 | 203
2017-06-16 06:30 | 228 | 227
2017-06-16 07:00 | 247 | 246
2017-06-16 07:30 | 263 | 262
2017-06-16 08:00 | 262 | 262
2017-06-16 08:30 | 248 | 248
2017-06-16 09:00 | 235 | 234
2017-06-16 09:30 | 228 | 228
2017-06-16 10:00 | 230 | 229
2017-06-16 10:30 | 230 | 230
2017-06-16 11:00 | 229 | 229
2017-06-16 11:30 | 227 | 227
2017-06-16 12:00 | 231 | 231
2017-06-16 12:30 | 236 | 236
2017-06-16 13:00 | 236 | 236
2017-06-16 13:30 | 218 | 218
2017-06-16 14:00 | 219 | 218
2017-06-16 14:30 | 230 | 230
2017-06-16 15:00 | 237 | 237
2017-06-16 15:30 | 240 | 240
2017-06-16 16:00 | 246 | 246
2017-06-16 16:30 | 254 | 253
2017-06-16 17:00 | 265 | 265
2017-06-16 17:30 | 277 | 277
2017-06-16 18:00 | 278 | 278
2017-06-16 18:30 | 273 | 273
2017-06-16 19:00 | 272 | 272
2017-06-16 19:30 | 265 | 265
2017-06-16 20:00 | 260 | 260
2017-06-16 20:30 | 259 | 259
2017-06-16 21:00 | 247 | 247
2017-06-16 21:30 | 237 | 236
2017-06-16 22:00 | 228 | 228
2017-06-16 22:30 | 223 | 222
2017-06-16 23:00 | 220 | 220
2017-06-16 23:30 | 209 | 209
2017-06-17 | 191 | 191
2017-06-17 00:30 | 175 | 175
2017-06-17 01:00 | 165 | 165
2017-06-17 01:30 | 156 | 155
2017-06-17 02:00 | 150 | 150
2017-06-17 02:30 | 146 | 146
2017-06-17 03:00 | 144 | 143
2017-06-17 03:30 | 142 | 141
2017-06-17 04:00 | 142 | 141
2017-06-17 04:30 | 142 | 142
2017-06-17 05:00 | 145 | 145
2017-06-17 05:30 | 150 | 150
2017-06-17 06:00 | 156 | 156
2017-06-17 06:30 | 167 | 167
2017-06-17 07:00 | 174 | 174
2017-06-17 07:30 | 185 | 185
2017-06-17 08:00 | 195 | 195
2017-06-17 08:30 | 202 | 202
2017-06-17 09:00 | 203 | 203
2017-06-17 09:30 | 199 | 199
2017-06-17 10:00 | 192 | 192
2017-06-17 10:30 | 192 | 192
2017-06-17 11:00 | 191 | 191
2017-06-17 11:30 | 193 | 192
2017-06-17 12:00 | 191 | 190
2017-06-17 12:30 | 184 | 184
2017-06-17 13:00 | 187 | 186
2017-06-17 13:30 | 186 | 185
2017-06-17 14:00 | 189 | 189
2017-06-17 14:30 | 192 | 192
2017-06-17 15:00 | 197 | 197
2017-06-17 15:30 | 200 | 200
2017-06-17 16:00 | 204 | 203
2017-06-17 16:30 | 213 | 212
2017-06-17 17:00 | 227 | 226
2017-06-17 17:30 | 241 | 240
2017-06-17 18:00 | 246 | 245
2017-06-17 18:30 | 243 | 242
2017-06-17 19:00 | 240 | 239
2017-06-17 19:30 | 232 | 231
2017-06-17 20:00 | 228 | 227
2017-06-17 20:30 | 228 | 227
2017-06-17 21:00 | 218 | 217
2017-06-17 21:30 | 212 | 211
2017-06-17 22:00 | 206 | 206
2017-06-17 22:30 | 205 | 205
2017-06-17 23:00 | 207 | 206
2017-06-17 23:30 | 197 | 197
2017-06-18 | 182 | 182
2017-06-18 00:30 | 167 | 167
2017-06-18 01:00 | 158 | 158
2017-06-18 01:30 | 150 | 149
2017-06-18 02:00 | 143 | 143
2017-06-18 02:30 | 140 | 140
2017-06-18 03:00 | 138 | 137
2017-06-18 03:30 | 137 | 136
2017-06-18 04:00 | 136 | 135
2017-06-18 04:30 | 136 | 135
2017-06-18 05:00 | 138 | 137
2017-06-18 05:30 | 141 | 141
2017-06-18 06:00 | 146 | 146
2017-06-18 06:30 | 153 | 152
2017-06-18 07:00 | 158 | 158
2017-06-18 07:30 | 167 | 167
2017-06-18 08:00 | 171 | 171
2017-06-18 08:30 | 174 | 174
2017-06-18 09:00 | 173 | 173
2017-06-18 09:30 | 171 | 171
2017-06-18 10:00 | 166 | 166
2017-06-18 10:30 | 161 | 161
2017-06-18 11:00 | 156 | 156
2017-06-18 11:30 | 151 | 151
2017-06-18 12:00 | 148 | 148
2017-06-18 12:30 | 147 | 147
2017-06-18 13:00 | 149 | 149
2017-06-18 13:30 | 153 | 153
2017-06-18 14:00 | 156 | 156
2017-06-18 14:30 | 160 | 160
2017-06-18 15:00 | 168 | 168
2017-06-18 15:30 | 177 | 177
2017-06-18 16:00 | 189 | 189
2017-06-18 16:30 | 204 | 204
2017-06-18 17:00 | 221 | 221
2017-06-18 17:30 | 240 | 239
2017-06-18 18:00 | 250 | 250
2017-06-18 18:30 | 249 | 249
2017-06-18 19:00 | 246 | 246
2017-06-18 19:30 | 240 | 240
2017-06-18 20:00 | 236 | 236
2017-06-18 20:30 | 236 | 236
2017-06-18 21:00 | 226 | 226
2017-06-18 21:30 | 217 | 217
2017-06-18 22:00 | 210 | 210
2017-06-18 22:30 | 207 | 207
2017-06-18 23:00 | 207 | 207
2017-06-18 23:30 | 195 | 195
2017-06-19 | 180 | 180
2017-06-19 00:30 | 165 | 165
2017-06-19 01:00 | 155 | 155
2017-06-19 01:30 | 149 | 148
2017-06-19 02:00 | 144 | 144
2017-06-19 02:30 | 141 | 141
2017-06-19 03:00 | 140 | 139
2017-06-19 03:30 | 140 | 139
2017-06-19 04:00 | 141 | 140
2017-06-19 04:30 | 146 | 146
2017-06-19 05:00 | 155 | 155
2017-06-19 05:30 | 171 | 171
2017-06-19 06:00 | 186 | 186
2017-06-19 06:30 | 213 | 212
2017-06-19 07:00 | 233 | 233
2017-06-19 07:30 | 251 | 251
2017-06-19 08:00 | 252 | 252
2017-06-19 08:30 | 243 | 243
2017-06-19 09:00 | 231 | 231
2017-06-19 09:30 | 222 | 222
2017-06-19 10:00 | 214 | 214
2017-06-19 10:30 | 207 | 207
2017-06-19 11:00 | 206 | 206
2017-06-19 11:30 | 208 | 208
2017-06-19 12:00 | 224 | 224
2017-06-19 12:30 | 236 | 236
2017-06-19 13:00 | 231 | 231
2017-06-19 13:30 | 227 | 227
2017-06-19 14:00 | 225 | 225
2017-06-19 14:30 | 229 | 229
2017-06-19 15:00 | 230 | 230
2017-06-19 15:30 | 237 | 237
2017-06-19 16:00 | 245 | 245
2017-06-19 16:30 | 258 | 258
2017-06-19 17:00 | 272 | 272
2017-06-19 17:30 | 288 | 287
2017-06-19 18:00 | 295 | 295
2017-06-19 18:30 | 291 | 291
2017-06-19 19:00 | 286 | 285
2017-06-19 19:30 | 277 | 276
2017-06-19 20:00 | 272 | 271
2017-06-19 20:30 | 271 | 270
2017-06-19 21:00 | 259 | 259
2017-06-19 21:30 | 246 | 246
2017-06-19 22:00 | 236 | 236
2017-06-19 22:30 | 228 | 228
2017-06-19 23:00 | 224 | 224
2017-06-19 23:30 | 210 | 209
2017-06-20 | 193 | 192
2017-06-20 00:30 | 176 | 176
2017-06-20 01:00 | 166 | 165
2017-06-20 01:30 | 158 | 158
2017-06-20 02:00 | 152 | 152
2017-06-20 02:30 | 150 | 150
2017-06-20 03:00 | 148 | 148
2017-06-20 03:30 | 147 | 147
2017-06-20 04:00 | 149 | 149
2017-06-20 04:30 | 154 | 153
2017-06-20 05:00 | 162 | 162
2017-06-20 05:30 | 177 | 176
2017-06-20 06:00 | 194 | 193
2017-06-20 06:30 | 218 | 217
2017-06-20 07:00 | 237 | 237
2017-06-20 07:30 | 252 | 252
2017-06-20 08:00 | 253 | 252
2017-06-20 08:30 | 248 | 247
2017-06-20 09:00 | 243 | 242
2017-06-20 09:30 | 239 | 238
2017-06-20 10:00 | 227 | 226
2017-06-20 10:30 | 224 | 224
2017-06-20 11:00 | 226 | 225
2017-06-20 11:30 | 224 | 223
2017-06-20 12:00 | 227 | 226
2017-06-20 12:30 | 224 | 223
2017-06-20 13:00 | 217 | 217
2017-06-20 13:30 | 226 | 226
2017-06-20 14:00 | 227 | 226
2017-06-20 14:30 | 232 | 231
2017-06-20 15:00 | 234 | 233
2017-06-20 15:30 | 239 | 238
2017-06-20 16:00 | 247 | 246
2017-06-20 16:30 | 258 | 257
2017-06-20 17:00 | 274 | 274
2017-06-20 17:30 | 290 | 290
2017-06-20 18:00 | 294 | 294
2017-06-20 18:30 | 288 | 288
2017-06-20 19:00 | 286 | 286
2017-06-20 19:30 | 279 | 279
2017-06-20 20:00 | 275 | 275
2017-06-20 20:30 | 274 | 274
2017-06-20 21:00 | 261 | 261
2017-06-20 21:30 | 248 | 247
2017-06-20 22:00 | 238 | 237
2017-06-20 22:30 | 230 | 230
2017-06-20 23:00 | 228 | 228
2017-06-20 23:30 | 214 | 214
2017-06-21 | 197 | 197
2017-06-21 00:30 | 183 | 183
2017-06-21 01:00 | 173 | 173
2017-06-21 01:30 | 164 | 164
2017-06-21 02:00 | 160 | 160
2017-06-21 02:30 | 158 | 158
2017-06-21 03:00 | 155 | 155
2017-06-21 03:30 | 156 | 156
2017-06-21 04:00 | 157 | 157
2017-06-21 04:30 | 163 | 163
2017-06-21 05:00 | 169 | 169
2017-06-21 05:30 | 183 | 183
2017-06-21 06:00 | 200 | 200
2017-06-21 06:30 | 228 | 228
2017-06-21 07:00 | 249 | 248
2017-06-21 07:30 | 276 | 276
2017-06-21 08:00 | 273 | 273
2017-06-21 08:30 | 258 | 258
2017-06-21 09:00 | 241 | 241
2017-06-21 09:30 | 229 | 228
2017-06-21 10:00 | 216 | 215
2017-06-21 10:30 | 208 | 207
2017-06-21 11:00 | 200 | 199
2017-06-21 11:30 | 197 | 196
2017-06-21 12:00 | 200 | 199
2017-06-21 12:30 | 206 | 205
2017-06-21 13:00 | 211 | 210
2017-06-21 13:30 | 210 | 209
2017-06-21 14:00 | 214 | 214
2017-06-21 14:30 | 219 | 218
2017-06-21 15:00 | 226 | 225
2017-06-21 15:30 | 232 | 232
2017-06-21 16:00 | 245 | 245
2017-06-21 16:30 | 247 | 247
2017-06-21 17:00 | 260 | 260
2017-06-21 17:30 | 278 | 278
2017-06-21 18:00 | 283 | 283
2017-06-21 18:30 | 281 | 281
2017-06-21 19:00 | 280 | 280
2017-06-21 19:30 | 274 | 274
2017-06-21 20:00 | 271 | 271
2017-06-21 20:30 | 269 | 269
2017-06-21 21:00 | 258 | 258
2017-06-21 21:30 | 245 | 245
2017-06-21 22:00 | 234 | 234
2017-06-21 22:30 | 229 | 229
2017-06-21 23:00 | 227 | 227
2017-06-21 23:30 | 214 | 214
2017-06-22 | 196 | 196
2017-06-22 00:30 | 178 | 178
2017-06-22 01:00 | 168 | 168
2017-06-22 01:30 | 162 | 162
2017-06-22 02:00 | 156 | 156
2017-06-22 02:30 | 153 | 153
2017-06-22 03:00 | 150 | 150
2017-06-22 03:30 | 150 | 149
2017-06-22 04:00 | 151 | 151
2017-06-22 04:30 | 155 | 155
2017-06-22 05:00 | 164 | 164
2017-06-22 05:30 | 179 | 179
2017-06-22 06:00 | 195 | 194
2017-06-22 06:30 | 220 | 219
2017-06-22 07:00 | 239 | 238
2017-06-22 07:30 | 266 | 264
2017-06-22 08:00 | 274 | 272
2017-06-22 08:30 | 265 | 263
2017-06-22 09:00 | 252 | 250
2017-06-22 09:30 | 239 | 238
2017-06-22 10:00 | 224 | 223
2017-06-22 10:30 | 213 | 212
2017-06-22 11:00 | 205 | 205
2017-06-22 11:30 | 203 | 202
2017-06-22 12:00 | 208 | 207
2017-06-22 12:30 | 212 | 211
2017-06-22 13:00 | 214 | 213
2017-06-22 13:30 | 219 | 218
2017-06-22 14:00 | 221 | 220
2017-06-22 14:30 | 224 | 223
2017-06-22 15:00 | 226 | 225
2017-06-22 15:30 | 232 | 231
2017-06-22 16:00 | 241 | 240
2017-06-22 16:30 | 252 | 250
2017-06-22 17:00 | 259 | 258
2017-06-22 17:30 | 273 | 273
2017-06-22 18:00 | 284 | 283
2017-06-22 18:30 | 283 | 283
2017-06-22 19:00 | 284 | 284
2017-06-22 19:30 | 281 | 281
2017-06-22 20:00 | 279 | 278
2017-06-22 20:30 | 279 | 278
2017-06-22 21:00 | 267 | 266
2017-06-22 21:30 | 254 | 253
2017-06-22 22:00 | 244 | 243
2017-06-22 22:30 | 236 | 236
2017-06-22 23:00 | 233 | 233
2017-06-22 23:30 | 220 | 220
2017-06-23 | 201 | 201
2017-06-23 00:30 | 184 | 184
2017-06-23 01:00 | 173 | 173
2017-06-23 01:30 | 165 | 165
2017-06-23 02:00 | 159 | 159
2017-06-23 02:30 | 156 | 156
2017-06-23 03:00 | 155 | 155
2017-06-23 03:30 | 155 | 155
2017-06-23 04:00 | 155 | 155
2017-06-23 04:30 | 160 | 160
2017-06-23 05:00 | 169 | 169
2017-06-23 05:30 | 187 | 186
2017-06-23 06:00 | 205 | 204
2017-06-23 06:30 | 231 | 231
2017-06-23 07:00 | 253 | 253
2017-06-23 07:30 | 269 | 269
2017-06-23 08:00 | 268 | 268
2017-06-23 08:30 | 269 | 269
2017-06-23 09:00 | 257 | 256
2017-06-23 09:30 | 246 | 246
2017-06-23 10:00 | 235 | 235
2017-06-23 10:30 | 223 | 223
2017-06-23 11:00 | 216 | 214
2017-06-23 11:30 | 210 | 208
2017-06-23 12:00 | 207 | 206
2017-06-23 12:30 | 206 | 204
2017-06-23 13:00 | 206 | 205
2017-06-23 13:30 | 209 | 208
2017-06-23 14:00 | 214 | 212
2017-06-23 14:30 | 218 | 217
2017-06-23 15:00 | 212 | 211
2017-06-23 15:30 | 218 | 217
2017-06-23 16:00 | 230 | 228
2017-06-23 16:30 | 241 | 239
2017-06-23 17:00 | 253 | 252
2017-06-23 17:30 | 266 | 265
2017-06-23 18:00 | 274 | 273
2017-06-23 18:30 | 271 | 270
2017-06-23 19:00 | 272 | 272
2017-06-23 19:30 | 270 | 270
2017-06-23 20:00 | 269 | 269
2017-06-23 20:30 | 269 | 268
2017-06-23 21:00 | 259 | 258
2017-06-23 21:30 | 248 | 247
2017-06-23 22:00 | 241 | 240
2017-06-23 22:30 | 234 | 234
2017-06-23 23:00 | 233 | 232
2017-06-23 23:30 | 219 | 219
2017-06-24 | 203 | 203
2017-06-24 00:30 | 186 | 186
2017-06-24 01:00 | 176 | 176
2017-06-24 01:30 | 167 | 167
2017-06-24 02:00 | 160 | 160
2017-06-24 02:30 | 157 | 157
2017-06-24 03:00 | 154 | 154
2017-06-24 03:30 | 153 | 153
2017-06-24 04:00 | 152 | 152
2017-06-24 04:30 | 154 | 154
2017-06-24 05:00 | 157 | 157
2017-06-24 05:30 | 164 | 164
2017-06-24 06:00 | 171 | 171
2017-06-24 06:30 | 182 | 181
2017-06-24 07:00 | 192 | 191
2017-06-24 07:30 | 205 | 204
2017-06-24 08:00 | 211 | 210
2017-06-24 08:30 | 214 | 212
2017-06-24 09:00 | 208 | 206
2017-06-24 09:30 | 200 | 198
2017-06-24 10:00 | 189 | 188
2017-06-24 10:30 | 180 | 179
2017-06-24 11:00 | 169 | 168
2017-06-24 11:30 | 162 | 161
2017-06-24 12:00 | 157 | 156
2017-06-24 12:30 | 154 | 154
2017-06-24 13:00 | 155 | 155
2017-06-24 13:30 | 156 | 156
2017-06-24 14:00 | 159 | 159
2017-06-24 14:30 | 165 | 164
2017-06-24 15:00 | 173 | 172
2017-06-24 15:30 | 182 | 181
2017-06-24 16:00 | 194 | 193
2017-06-24 16:30 | 206 | 206
2017-06-24 17:00 | 222 | 222
2017-06-24 17:30 | 235 | 234
2017-06-24 18:00 | 243 | 242
2017-06-24 18:30 | 243 | 243
2017-06-24 19:00 | 242 | 242
2017-06-24 19:30 | 237 | 237
2017-06-24 20:00 | 234 | 234
2017-06-24 20:30 | 232 | 232
2017-06-24 21:00 | 222 | 222
2017-06-24 21:30 | 215 | 215
2017-06-24 22:00 | 211 | 211
2017-06-24 22:30 | 209 | 209
2017-06-24 23:00 | 211 | 211
2017-06-24 23:30 | 201 | 201
2017-06-25 | 187 | 187
2017-06-25 00:30 | 172 | 172
2017-06-25 01:00 | 161 | 161
2017-06-25 01:30 | 153 | 153
2017-06-25 02:00 | 148 | 147
2017-06-25 02:30 | 144 | 143
2017-06-25 03:00 | 141 | 140
2017-06-25 03:30 | 139 | 139
2017-06-25 04:00 | 137 | 137
2017-06-25 04:30 | 137 | 137
2017-06-25 05:00 | 140 | 140
2017-06-25 05:30 | 144 | 144
2017-06-25 06:00 | 149 | 149
2017-06-25 06:30 | 158 | 157
2017-06-25 07:00 | 165 | 165
2017-06-25 07:30 | 175 | 175
2017-06-25 08:00 | 179 | 179
2017-06-25 08:30 | 182 | 182
2017-06-25 09:00 | 181 | 181
2017-06-25 09:30 | 176 | 176
2017-06-25 10:00 | 172 | 172
2017-06-25 10:30 | 163 | 163
2017-06-25 11:00 | 151 | 151
2017-06-25 11:30 | 146 | 146
2017-06-25 12:00 | 141 | 141
2017-06-25 12:30 | 140 | 140
2017-06-25 13:00 | 142 | 142
2017-06-25 13:30 | 143 | 143
2017-06-25 14:00 | 147 | 147
2017-06-25 14:30 | 152 | 152
2017-06-25 15:00 | 160 | 160
2017-06-25 15:30 | 171 | 171
2017-06-25 16:00 | 185 | 185
2017-06-25 16:30 | 199 | 199
2017-06-25 17:00 | 216 | 215
2017-06-25 17:30 | 233 | 233
2017-06-25 18:00 | 246 | 246
2017-06-25 18:30 | 246 | 245
2017-06-25 19:00 | 244 | 244
2017-06-25 19:30 | 240 | 240
2017-06-25 20:00 | 236 | 236
2017-06-25 20:30 | 235 | 235
2017-06-25 21:00 | 225 | 225
2017-06-25 21:30 | 217 | 217
2017-06-25 22:00 | 210 | 210
2017-06-25 22:30 | 207 | 207
2017-06-25 23:00 | 206 | 206
2017-06-25 23:30 | 196 | 196
2017-06-26 | 181 | 180
2017-06-26 00:30 | 166 | 165
2017-06-26 01:00 | 157 | 155
2017-06-26 01:30 | 150 | 148
2017-06-26 02:00 | 143 | 142
2017-06-26 02:30 | 139 | 139
2017-06-26 03:00 | 138 | 137
2017-06-26 03:30 | 138 | 137
2017-06-26 04:00 | 138 | 138
2017-06-26 04:30 | 143 | 143
2017-06-26 05:00 | 152 | 152
2017-06-26 05:30 | 169 | 169
2017-06-26 06:00 | 187 | 187
2017-06-26 06:30 | 211 | 211
2017-06-26 07:00 | 228 | 228
2017-06-26 07:30 | 244 | 243
2017-06-26 08:00 | 244 | 243
2017-06-26 08:30 | 238 | 237
2017-06-26 09:00 | 228 | 227
2017-06-26 09:30 | 218 | 217
2017-06-26 10:00 | 208 | 206
2017-06-26 10:30 | 200 | 199
2017-06-26 11:00 | 193 | 192
2017-06-26 11:30 | 188 | 187
2017-06-26 12:00 | 186 | 185
2017-06-26 12:30 | 186 | 186
2017-06-26 13:00 | 189 | 189
2017-06-26 13:30 | 193 | 192
2017-06-26 14:00 | 198 | 198
2017-06-26 14:30 | 203 | 203
2017-06-26 15:00 | 212 | 212
2017-06-26 15:30 | 219 | 219
2017-06-26 16:00 | 228 | 228
2017-06-26 16:30 | 240 | 240
2017-06-26 17:00 | 253 | 253
2017-06-26 17:30 | 268 | 268
2017-06-26 18:00 | 278 | 278
2017-06-26 18:30 | 273 | 273
2017-06-26 19:00 | 272 | 272
2017-06-26 19:30 | 268 | 267
2017-06-26 20:00 | 265 | 264
2017-06-26 20:30 | 261 | 261
2017-06-26 21:00 | 251 | 250
2017-06-26 21:30 | 239 | 238
2017-06-26 22:00 | 230 | 229
2017-06-26 22:30 | 224 | 223
2017-06-26 23:00 | 223 | 223
2017-06-26 23:30 | 210 | 210
2017-06-27 | 192 | 192
2017-06-27 00:30 | 175 | 175
2017-06-27 01:00 | 165 | 165
2017-06-27 01:30 | 157 | 157
2017-06-27 02:00 | 152 | 151
2017-06-27 02:30 | 148 | 148
2017-06-27 03:00 | 147 | 146
2017-06-27 03:30 | 147 | 147
2017-06-27 04:00 | 150 | 149
2017-06-27 04:30 | 154 | 154
2017-06-27 05:00 | 163 | 163
2017-06-27 05:30 | 179 | 179
2017-06-27 06:00 | 195 | 194
2017-06-27 06:30 | 217 | 216
2017-06-27 07:00 | 233 | 232
2017-06-27 07:30 | 246 | 246
2017-06-27 08:00 | 248 | 248
2017-06-27 08:30 | 249 | 249
2017-06-27 09:00 | 244 | 244
2017-06-27 09:30 | 233 | 233
2017-06-27 10:00 | 232 | 232
2017-06-27 10:30 | 219 | 219
2017-06-27 11:00 | 217 | 216
2017-06-27 11:30 | 217 | 216
2017-06-27 12:00 | 213 | 212
2017-06-27 12:30 | 219 | 218
2017-06-27 13:00 | 222 | 221
2017-06-27 13:30 | 221 | 220
2017-06-27 14:00 | 228 | 227
2017-06-27 14:30 | 222 | 221
2017-06-27 15:00 | 223 | 222
2017-06-27 15:30 | 232 | 231
2017-06-27 16:00 | 238 | 237
2017-06-27 16:30 | 245 | 244
2017-06-27 17:00 | 261 | 260
2017-06-27 17:30 | 279 | 278
2017-06-27 18:00 | 289 | 289
2017-06-27 18:30 | 284 | 284
2017-06-27 19:00 | 284 | 284
2017-06-27 19:30 | 279 | 279
2017-06-27 20:00 | 276 | 276
2017-06-27 20:30 | 274 | 274
2017-06-27 21:00 | 261 | 260
2017-06-27 21:30 | 249 | 248
2017-06-27 22:00 | 239 | 238
2017-06-27 22:30 | 229 | 228
2017-06-27 23:00 | 226 | 225
2017-06-27 23:30 | 212 | 212
2017-06-28 | 194 | 194
2017-06-28 00:30 | 176 | 176
2017-06-28 01:00 | 165 | 165
2017-06-28 01:30 | 157 | 157
2017-06-28 02:00 | 152 | 151
2017-06-28 02:30 | 148 | 148
2017-06-28 03:00 | 146 | 146
2017-06-28 03:30 | 146 | 145
2017-06-28 04:00 | 148 | 147
2017-06-28 04:30 | 151 | 151
2017-06-28 05:00 | 159 | 159
2017-06-28 05:30 | 173 | 173
2017-06-28 06:00 | 190 | 189
2017-06-28 06:30 | 211 | 211
2017-06-28 07:00 | 228 | 227
2017-06-28 07:30 | 242 | 241
2017-06-28 08:00 | 249 | 249
2017-06-28 08:30 | 246 | 246
2017-06-28 09:00 | 238 | 238
2017-06-28 09:30 | 229 | 229
2017-06-28 10:00 | 220 | 220
2017-06-28 10:30 | 212 | 212
2017-06-28 11:00 | 209 | 209
2017-06-28 11:30 | 209 | 209
2017-06-28 12:00 | 208 | 208
2017-06-28 12:30 | 208 | 208
2017-06-28 13:00 | 212 | 212
2017-06-28 13:30 | 215 | 215
2017-06-28 14:00 | 221 | 221
2017-06-28 14:30 | 222 | 222
2017-06-28 15:00 | 225 | 225
2017-06-28 15:30 | 227 | 227
2017-06-28 16:00 | 234 | 234
2017-06-28 16:30 | 245 | 245
2017-06-28 17:00 | 256 | 256
2017-06-28 17:30 | 270 | 270
2017-06-28 18:00 | 278 | 278
2017-06-28 18:30 | 272 | 272
2017-06-28 19:00 | 273 | 273
2017-06-28 19:30 | 268 | 268
2017-06-28 20:00 | 265 | 265
2017-06-28 20:30 | 264 | 264
2017-06-28 21:00 | 253 | 253
2017-06-28 21:30 | 242 | 242
2017-06-28 22:00 | 232 | 232
2017-06-28 22:30 | 227 | 227
2017-06-28 23:00 | 224 | 224
2017-06-28 23:30 | 210 | 209
2017-06-29 | 192 | 192
2017-06-29 00:30 | 177 | 177
2017-06-29 01:00 | 165 | 165
2017-06-29 01:30 | 159 | 159
2017-06-29 02:00 | 153 | 152
2017-06-29 02:30 | 149 | 149
2017-06-29 03:00 | 147 | 147
2017-06-29 03:30 | 147 | 147
2017-06-29 04:00 | 148 | 147
2017-06-29 04:30 | 153 | 153
2017-06-29 05:00 | 161 | 161
2017-06-29 05:30 | 175 | 175
2017-06-29 06:00 | 190 | 190
2017-06-29 06:30 | 213 | 213
2017-06-29 07:00 | 229 | 229
2017-06-29 07:30 | 240 | 240
2017-06-29 08:00 | 242 | 241
2017-06-29 08:30 | 241 | 241
2017-06-29 09:00 | 233 | 233
2017-06-29 09:30 | 225 | 225
2017-06-29 10:00 | 216 | 216
2017-06-29 10:30 | 211 | 211
2017-06-29 11:00 | 204 | 204
2017-06-29 11:30 | 200 | 200
2017-06-29 12:00 | 199 | 199
2017-06-29 12:30 | 198 | 198
2017-06-29 13:00 | 201 | 201
2017-06-29 13:30 | 203 | 203
2017-06-29 14:00 | 214 | 214
2017-06-29 14:30 | 219 | 219
2017-06-29 15:00 | 224 | 224
2017-06-29 15:30 | 228 | 228
2017-06-29 16:00 | 237 | 237
2017-06-29 16:30 | 246 | 246
2017-06-29 17:00 | 257 | 257
2017-06-29 17:30 | 272 | 272
2017-06-29 18:00 | 280 | 280
2017-06-29 18:30 | 277 | 277
2017-06-29 19:00 | 274 | 273
2017-06-29 19:30 | 269 | 269
2017-06-29 20:00 | 267 | 266
2017-06-29 20:30 | 264 | 264
2017-06-29 21:00 | 253 | 253
2017-06-29 21:30 | 239 | 239
2017-06-29 22:00 | 230 | 230
2017-06-29 22:30 | 225 | 225
2017-06-29 23:00 | 224 | 224
2017-06-29 23:30 | 211 | 210
2017-06-30 | 193 | 193
2017-06-30 00:30 | 177 | 176
2017-06-30 01:00 | 167 | 166
2017-06-30 01:30 | 157 | 157
2017-06-30 02:00 | 152 | 152
2017-06-30 02:30 | 149 | 149
2017-06-30 03:00 | 146 | 146
2017-06-30 03:30 | 146 | 145
2017-06-30 04:00 | 147 | 147
2017-06-30 04:30 | 149 | 149
2017-06-30 05:00 | 157 | 157
2017-06-30 05:30 | 170 | 170
2017-06-30 06:00 | 183 | 183
2017-06-30 06:30 | 202 | 202
2017-06-30 07:00 | 217 | 217
2017-06-30 07:30 | 232 | 232
2017-06-30 08:00 | 238 | 238
2017-06-30 08:30 | 240 | 240
2017-06-30 09:00 | 231 | 230
2017-06-30 09:30 | 218 | 218
2017-06-30 10:00 | 207 | 207
2017-06-30 10:30 | 203 | 202
2017-06-30 11:00 | 196 | 195
2017-06-30 11:30 | 190 | 189
2017-06-30 12:00 | 189 | 189
2017-06-30 12:30 | 191 | 190
2017-06-30 13:00 | 192 | 192
2017-06-30 13:30 | 194 | 193
2017-06-30 14:00 | 197 | 197
2017-06-30 14:30 | 202 | 201
2017-06-30 15:00 | 208 | 207
2017-06-30 15:30 | 215 | 215
2017-06-30 16:00 | 224 | 224
2017-06-30 16:30 | 234 | 234
2017-06-30 17:00 | 247 | 247
2017-06-30 17:30 | 259 | 259
2017-06-30 18:00 | 267 | 267
2017-06-30 18:30 | 263 | 263
2017-06-30 19:00 | 264 | 264
2017-06-30 19:30 | 261 | 260
2017-06-30 20:00 | 259 | 258
2017-06-30 20:30 | 257 | 257
2017-06-30 21:00 | 247 | 247
2017-06-30 21:30 | 239 | 238
2017-06-30 22:00 | 232 | 231
2017-06-30 22:30 | 229 | 228
2017-06-30 23:00 | 228 | 227
2017-06-30 23:30 | 215 | 214
2017-07-01 | 198 | 198
2017-07-01 00:30 | 181 | 181
2017-07-01 01:00 | 170 | 170
2017-07-01 01:30 | 162 | 162
2017-07-01 02:00 | 156 | 156
2017-07-01 02:30 | 152 | 152
2017-07-01 03:00 | 149 | 149
2017-07-01 03:30 | 148 | 148
2017-07-01 04:00 | 149 | 149
2017-07-01 04:30 | 150 | 150
2017-07-01 05:00 | 153 | 153
2017-07-01 05:30 | 162 | 162
2017-07-01 06:00 | 169 | 168
2017-07-01 06:30 | 181 | 180
2017-07-01 07:00 | 191 | 190
2017-07-01 07:30 | 204 | 204
2017-07-01 08:00 | 211 | 211
2017-07-01 08:30 | 212 | 212
2017-07-01 09:00 | 208 | 208
2017-07-01 09:30 | 200 | 200
2017-07-01 10:00 | 189 | 189
2017-07-01 10:30 | 178 | 178
2017-07-01 11:00 | 167 | 167
2017-07-01 11:30 | 159 | 158
2017-07-01 12:00 | 156 | 155
2017-07-01 12:30 | 153 | 152
2017-07-01 13:00 | 154 | 153
2017-07-01 13:30 | 155 | 154
2017-07-01 14:00 | 158 | 158
2017-07-01 14:30 | 164 | 163
2017-07-01 15:00 | 169 | 169
2017-07-01 15:30 | 176 | 176
2017-07-01 16:00 | 191 | 190
2017-07-01 16:30 | 206 | 205
2017-07-01 17:00 | 226 | 225
2017-07-01 17:30 | 244 | 244
2017-07-01 18:00 | 257 | 257
2017-07-01 18:30 | 260 | 260
2017-07-01 19:00 | 262 | 262
2017-07-01 19:30 | 261 | 261
2017-07-01 20:00 | 262 | 262
2017-07-01 20:30 | 262 | 262
2017-07-01 21:00 | 253 | 253
2017-07-01 21:30 | 244 | 244
2017-07-01 22:00 | 238 | 238
2017-07-01 22:30 | 234 | 234
2017-07-01 23:00 | 234 | 234
2017-07-01 23:30 | 222 | 222
2017-07-02 | 207 | 207
2017-07-02 00:30 | 188 | 188
2017-07-02 01:00 | 177 | 176
2017-07-02 01:30 | 167 | 167
2017-07-02 02:00 | 159 | 159
2017-07-02 02:30 | 155 | 155
2017-07-02 03:00 | 152 | 152
2017-07-02 03:30 | 151 | 151
2017-07-02 04:00 | 149 | 149
2017-07-02 04:30 | 149 | 149
2017-07-02 05:00 | 152 | 152
2017-07-02 05:30 | 156 | 156
2017-07-02 06:00 | 163 | 163
2017-07-02 06:30 | 173 | 172
2017-07-02 07:00 | 182 | 181
2017-07-02 07:30 | 194 | 193
2017-07-02 08:00 | 205 | 205
2017-07-02 08:30 | 211 | 210
2017-07-02 09:00 | 207 | 207
2017-07-02 09:30 | 198 | 198
2017-07-02 10:00 | 190 | 189
2017-07-02 10:30 | 175 | 175
2017-07-02 11:00 | 165 | 165
2017-07-02 11:30 | 153 | 153
2017-07-02 12:00 | 147 | 147
2017-07-02 12:30 | 143 | 143
2017-07-02 13:00 | 144 | 143
2017-07-02 13:30 | 145 | 144
2017-07-02 14:00 | 151 | 150
2017-07-02 14:30 | 157 | 157
2017-07-02 15:00 | 164 | 164
2017-07-02 15:30 | 174 | 173
2017-07-02 16:00 | 188 | 187
2017-07-02 16:30 | 204 | 203
2017-07-02 17:00 | 224 | 223
2017-07-02 17:30 | 247 | 245
2017-07-02 18:00 | 262 | 262
2017-07-02 18:30 | 264 | 264
2017-07-02 19:00 | 265 | 265
2017-07-02 19:30 | 261 | 261
2017-07-02 20:00 | 258 | 258
2017-07-02 20:30 | 259 | 259
2017-07-02 21:00 | 250 | 250
2017-07-02 21:30 | 240 | 240
2017-07-02 22:00 | 232 | 232
2017-07-02 22:30 | 226 | 226
2017-07-02 23:00 | 224 | 224
2017-07-02 23:30 | 211 | 211
2017-07-03 | 194 | 193
2017-07-03 00:30 | 179 | 179
2017-07-03 01:00 | 171 | 170
2017-07-03 01:30 | 164 | 164
2017-07-03 02:00 | 159 | 159
2017-07-03 02:30 | 157 | 157
2017-07-03 03:00 | 156 | 156
2017-07-03 03:30 | 156 | 156
2017-07-03 04:00 | 157 | 157
2017-07-03 04:30 | 163 | 163
2017-07-03 05:00 | 173 | 173
2017-07-03 05:30 | 188 | 187
2017-07-03 06:00 | 207 | 205
2017-07-03 06:30 | 233 | 232
2017-07-03 07:00 | 253 | 253
2017-07-03 07:30 | 270 | 270
2017-07-03 08:00 | 271 | 271
2017-07-03 08:30 | 266 | 266
2017-07-03 09:00 | 257 | 257
2017-07-03 09:30 | 244 | 244
2017-07-03 10:00 | 232 | 232
2017-07-03 10:30 | 221 | 220
2017-07-03 11:00 | 210 | 210
2017-07-03 11:30 | 203 | 203
2017-07-03 12:00 | 203 | 202
2017-07-03 12:30 | 203 | 203
2017-07-03 13:00 | 212 | 212
2017-07-03 13:30 | 218 | 218
2017-07-03 14:00 | 226 | 226
2017-07-03 14:30 | 231 | 231
2017-07-03 15:00 | 234 | 234
2017-07-03 15:30 | 234 | 234
2017-07-03 16:00 | 238 | 238
2017-07-03 16:30 | 254 | 254
2017-07-03 17:00 | 268 | 268
2017-07-03 17:30 | 284 | 283
2017-07-03 18:00 | 294 | 294
2017-07-03 18:30 | 291 | 291
2017-07-03 19:00 | 291 | 291
2017-07-03 19:30 | 285 | 284
2017-07-03 20:00 | 281 | 280
2017-07-03 20:30 | 278 | 278
2017-07-03 21:00 | 267 | 267
2017-07-03 21:30 | 253 | 253
2017-07-03 22:00 | 243 | 243
2017-07-03 22:30 | 235 | 235
2017-07-03 23:00 | 232 | 232
2017-07-03 23:30 | 221 | 221
2017-07-04 | 202 | 201
2017-07-04 00:30 | 184 | 184
2017-07-04 01:00 | 172 | 172
2017-07-04 01:30 | 163 | 163
2017-07-04 02:00 | 157 | 157
2017-07-04 02:30 | 153 | 152
2017-07-04 03:00 | 151 | 151
2017-07-04 03:30 | 152 | 151
2017-07-04 04:00 | 152 | 151
2017-07-04 04:30 | 156 | 156
2017-07-04 05:00 | 165 | 165
2017-07-04 05:30 | 180 | 180
2017-07-04 06:00 | 196 | 195
2017-07-04 06:30 | 217 | 216
2017-07-04 07:00 | 232 | 232
2017-07-04 07:30 | 246 | 246
2017-07-04 08:00 | 249 | 248
2017-07-04 08:30 | 245 | 244
2017-07-04 09:00 | 233 | 232
2017-07-04 09:30 | 237 | 237
2017-07-04 10:00 | 227 | 226
2017-07-04 10:30 | 218 | 218
2017-07-04 11:00 | 213 | 212
2017-07-04 11:30 | 209 | 209
2017-07-04 12:00 | 207 | 206
2017-07-04 12:30 | 208 | 208
2017-07-04 13:00 | 211 | 211
2017-07-04 13:30 | 214 | 213
2017-07-04 14:00 | 218 | 218
2017-07-04 14:30 | 225 | 224
2017-07-04 15:00 | 234 | 234
2017-07-04 15:30 | 239 | 238
2017-07-04 16:00 | 231 | 231
2017-07-04 16:30 | 242 | 241
2017-07-04 17:00 | 255 | 254
2017-07-04 17:30 | 270 | 270
2017-07-04 18:00 | 283 | 283
2017-07-04 18:30 | 278 | 278
2017-07-04 19:00 | 278 | 278
2017-07-04 19:30 | 271 | 270
2017-07-04 20:00 | 267 | 267
2017-07-04 20:30 | 265 | 265
2017-07-04 21:00 | 254 | 254
2017-07-04 21:30 | 244 | 244
2017-07-04 22:00 | 235 | 235
2017-07-04 22:30 | 230 | 230
2017-07-04 23:00 | 229 | 228
2017-07-04 23:30 | 216 | 215
2017-07-05 | 199 | 199
2017-07-05 00:30 | 179 | 179
2017-07-05 01:00 | 167 | 167
2017-07-05 01:30 | 161 | 160
2017-07-05 02:00 | 156 | 156
2017-07-05 02:30 | 152 | 151
2017-07-05 03:00 | 152 | 152
2017-07-05 03:30 | 152 | 151
2017-07-05 04:00 | 152 | 151
2017-07-05 04:30 | 156 | 156
2017-07-05 05:00 | 165 | 165
2017-07-05 05:30 | 179 | 179
2017-07-05 06:00 | 196 | 196
2017-07-05 06:30 | 220 | 219
2017-07-05 07:00 | 237 | 237
2017-07-05 07:30 | 251 | 251
2017-07-05 08:00 | 251 | 251
2017-07-05 08:30 | 246 | 246
2017-07-05 09:00 | 234 | 234
2017-07-05 09:30 | 223 | 223
2017-07-05 10:00 | 213 | 213
2017-07-05 10:30 | 207 | 207
2017-07-05 11:00 | 200 | 200
2017-07-05 11:30 | 195 | 195
2017-07-05 12:00 | 188 | 188
2017-07-05 12:30 | 187 | 187
2017-07-05 13:00 | 191 | 191
2017-07-05 13:30 | 197 | 197
2017-07-05 14:00 | 203 | 203
2017-07-05 14:30 | 205 | 205
2017-07-05 15:00 | 214 | 214
2017-07-05 15:30 | 225 | 224
2017-07-05 16:00 | 241 | 241
2017-07-05 16:30 | 253 | 253
2017-07-05 17:00 | 268 | 267
2017-07-05 17:30 | 278 | 278
2017-07-05 18:00 | 278 | 278
2017-07-05 18:30 | 274 | 274
2017-07-05 19:00 | 273 | 273
2017-07-05 19:30 | 268 | 268
2017-07-05 20:00 | 264 | 264
2017-07-05 20:30 | 264 | 264
2017-07-05 21:00 | 251 | 251
2017-07-05 21:30 | 240 | 240
2017-07-05 22:00 | 231 | 231
2017-07-05 22:30 | 224 | 224
2017-07-05 23:00 | 223 | 222
2017-07-05 23:30 | 212 | 212
2017-07-06 | 195 | 195
2017-07-06 00:30 | 179 | 179
2017-07-06 01:00 | 168 | 168
2017-07-06 01:30 | 161 | 160
2017-07-06 02:00 | 156 | 156
2017-07-06 02:30 | 156 | 156
2017-07-06 03:00 | 153 | 153
2017-07-06 03:30 | 153 | 153
2017-07-06 04:00 | 155 | 155
2017-07-06 04:30 | 160 | 160
2017-07-06 05:00 | 165 | 165
2017-07-06 05:30 | 179 | 179
2017-07-06 06:00 | 195 | 194
2017-07-06 06:30 | 213 | 213
2017-07-06 07:00 | 229 | 228
2017-07-06 07:30 | 245 | 243
2017-07-06 08:00 | 246 | 244
2017-07-06 08:30 | 241 | 241
2017-07-06 09:00 | 232 | 232
2017-07-06 09:30 | 220 | 220
2017-07-06 10:00 | 211 | 210
2017-07-06 10:30 | 202 | 202
2017-07-06 11:00 | 196 | 196
2017-07-06 11:30 | 192 | 192
2017-07-06 12:00 | 189 | 189
2017-07-06 12:30 | 189 | 189
2017-07-06 13:00 | 189 | 189
2017-07-06 13:30 | 193 | 193
2017-07-06 14:00 | 197 | 197
2017-07-06 14:30 | 203 | 203
2017-07-06 15:00 | 210 | 210
2017-07-06 15:30 | 219 | 219
2017-07-06 16:00 | 230 | 230
2017-07-06 16:30 | 241 | 241
2017-07-06 17:00 | 254 | 254
2017-07-06 17:30 | 268 | 268
2017-07-06 18:00 | 280 | 280
2017-07-06 18:30 | 279 | 279
2017-07-06 19:00 | 281 | 281
2017-07-06 19:30 | 277 | 277
2017-07-06 20:00 | 274 | 274
2017-07-06 20:30 | 274 | 274
2017-07-06 21:00 | 262 | 262
2017-07-06 21:30 | 252 | 252
2017-07-06 22:00 | 242 | 242
2017-07-06 22:30 | 233 | 233
2017-07-06 23:00 | 231 | 231
2017-07-06 23:30 | 219 | 219
2017-07-07 | 201 | 201
2017-07-07 00:30 | 184 | 184
2017-07-07 01:00 | 172 | 172
2017-07-07 01:30 | 163 | 163
2017-07-07 02:00 | 157 | 157
2017-07-07 02:30 | 154 | 154
2017-07-07 03:00 | 154 | 154
2017-07-07 03:30 | 153 | 153
2017-07-07 04:00 | 155 | 155
2017-07-07 04:30 | 159 | 158
2017-07-07 05:00 | 165 | 165
2017-07-07 05:30 | 178 | 177
2017-07-07 06:00 | 194 | 193
2017-07-07 06:30 | 216 | 214
2017-07-07 07:00 | 232 | 231
2017-07-07 07:30 | 251 | 250
2017-07-07 08:00 | 262 | 262
2017-07-07 08:30 | 265 | 264
2017-07-07 09:00 | 263 | 261
2017-07-07 09:30 | 269 | 266
2017-07-07 10:00 | 272 | 269
2017-07-07 10:30 | 267 | 264
2017-07-07 11:00 | 263 | 262
2017-07-07 11:30 | 262 | 261
2017-07-07 12:00 | 264 | 263
2017-07-07 12:30 | 266 | 266
2017-07-07 13:00 | 260 | 260
2017-07-07 13:30 | 256 | 256
2017-07-07 14:00 | 253 | 253
2017-07-07 14:30 | 251 | 251
2017-07-07 15:00 | 252 | 252
2017-07-07 15:30 | 256 | 255
2017-07-07 16:00 | 258 | 258
2017-07-07 16:30 | 263 | 263
2017-07-07 17:00 | 274 | 274
2017-07-07 17:30 | 289 | 289
2017-07-07 18:00 | 296 | 296
2017-07-07 18:30 | 292 | 291
2017-07-07 19:00 | 293 | 291
2017-07-07 19:30 | 287 | 285
2017-07-07 20:00 | 282 | 281
2017-07-07 20:30 | 279 | 278
2017-07-07 21:00 | 269 | 269
2017-07-07 21:30 | 259 | 258
2017-07-07 22:00 | 245 | 245
2017-07-07 22:30 | 238 | 238
2017-07-07 23:00 | 236 | 235
2017-07-07 23:30 | 223 | 223
2017-07-08 | 204 | 204
2017-07-08 00:30 | 187 | 187
2017-07-08 01:00 | 174 | 174
2017-07-08 01:30 | 165 | 165
2017-07-08 02:00 | 159 | 159
2017-07-08 02:30 | 154 | 154
2017-07-08 03:00 | 152 | 151
2017-07-08 03:30 | 150 | 150
2017-07-08 04:00 | 150 | 149
2017-07-08 04:30 | 150 | 149
2017-07-08 05:00 | 153 | 152
2017-07-08 05:30 | 160 | 160
2017-07-08 06:00 | 165 | 165
2017-07-08 06:30 | 175 | 175
2017-07-08 07:00 | 185 | 185
2017-07-08 07:30 | 196 | 196
2017-07-08 08:00 | 203 | 203
2017-07-08 08:30 | 205 | 205
2017-07-08 09:00 | 202 | 202
2017-07-08 09:30 | 194 | 194
2017-07-08 10:00 | 184 | 184
2017-07-08 10:30 | 177 | 177
2017-07-08 11:00 | 166 | 166
2017-07-08 11:30 | 159 | 159
2017-07-08 12:00 | 154 | 154
2017-07-08 12:30 | 149 | 149
2017-07-08 13:00 | 148 | 148
2017-07-08 13:30 | 149 | 148
2017-07-08 14:00 | 152 | 152
2017-07-08 14:30 | 156 | 156
2017-07-08 15:00 | 164 | 164
2017-07-08 15:30 | 173 | 173
2017-07-08 16:00 | 186 | 186
2017-07-08 16:30 | 200 | 200
2017-07-08 17:00 | 219 | 218
2017-07-08 17:30 | 234 | 233
2017-07-08 18:00 | 247 | 247
2017-07-08 18:30 | 250 | 250
2017-07-08 19:00 | 253 | 253
2017-07-08 19:30 | 250 | 250
2017-07-08 20:00 | 249 | 249
2017-07-08 20:30 | 251 | 251
2017-07-08 21:00 | 243 | 243
2017-07-08 21:30 | 235 | 235
2017-07-08 22:00 | 231 | 231
2017-07-08 22:30 | 231 | 231
2017-07-08 23:00 | 232 | 232
2017-07-08 23:30 | 221 | 221
2017-07-09 | 207 | 207
2017-07-09 00:30 | 191 | 191
2017-07-09 01:00 | 178 | 178
2017-07-09 01:30 | 169 | 169
2017-07-09 02:00 | 162 | 162
2017-07-09 02:30 | 158 | 158
2017-07-09 03:00 | 154 | 154
2017-07-09 03:30 | 153 | 153
2017-07-09 04:00 | 152 | 152
2017-07-09 04:30 | 152 | 152
2017-07-09 05:00 | 154 | 154
2017-07-09 05:30 | 158 | 158
2017-07-09 06:00 | 163 | 163
2017-07-09 06:30 | 172 | 172
2017-07-09 07:00 | 182 | 182
2017-07-09 07:30 | 196 | 196
2017-07-09 08:00 | 200 | 200
2017-07-09 08:30 | 202 | 202
2017-07-09 09:00 | 199 | 199
2017-07-09 09:30 | 196 | 196
2017-07-09 10:00 | 194 | 194
2017-07-09 10:30 | 180 | 180
2017-07-09 11:00 | 169 | 169
2017-07-09 11:30 | 158 | 157
2017-07-09 12:00 | 151 | 151
2017-07-09 12:30 | 148 | 148
2017-07-09 13:00 | 148 | 148
2017-07-09 13:30 | 150 | 150
2017-07-09 14:00 | 153 | 153
2017-07-09 14:30 | 159 | 159
2017-07-09 15:00 | 171 | 171
2017-07-09 15:30 | 183 | 183
2017-07-09 16:00 | 198 | 197
2017-07-09 16:30 | 215 | 215
2017-07-09 17:00 | 237 | 237
2017-07-09 17:30 | 253 | 253
2017-07-09 18:00 | 264 | 264
2017-07-09 18:30 | 267 | 267
2017-07-09 19:00 | 268 | 268
2017-07-09 19:30 | 266 | 266
2017-07-09 20:00 | 263 | 263
2017-07-09 20:30 | 263 | 262
2017-07-09 21:00 | 251 | 251
2017-07-09 21:30 | 242 | 242
2017-07-09 22:00 | 234 | 233
2017-07-09 22:30 | 227 | 227
2017-07-09 23:00 | 224 | 224
2017-07-09 23:30 | 211 | 211
2017-07-10 | 195 | 195
2017-07-10 00:30 | 180 | 180
2017-07-10 01:00 | 170 | 169
2017-07-10 01:30 | 166 | 164
2017-07-10 02:00 | 159 | 158
2017-07-10 02:30 | 154 | 153
2017-07-10 03:00 | 152 | 151
2017-07-10 03:30 | 151 | 149
2017-07-10 04:00 | 152 | 151
2017-07-10 04:30 | 159 | 158
2017-07-10 05:00 | 168 | 167
2017-07-10 05:30 | 183 | 183
2017-07-10 06:00 | 203 | 203
2017-07-10 06:30 | 232 | 232
2017-07-10 07:00 | 258 | 258
2017-07-10 07:30 | 280 | 280
2017-07-10 08:00 | 288 | 287
2017-07-10 08:30 | 273 | 272
2017-07-10 09:00 | 255 | 254
2017-07-10 09:30 | 246 | 246
2017-07-10 10:00 | 237 | 236
2017-07-10 10:30 | 241 | 241
2017-07-10 11:00 | 233 | 233
2017-07-10 11:30 | 217 | 217
2017-07-10 12:00 | 224 | 224
2017-07-10 12:30 | 219 | 219
2017-07-10 13:00 | 218 | 218
2017-07-10 13:30 | 214 | 214
2017-07-10 14:00 | 225 | 225
2017-07-10 14:30 | 233 | 232
2017-07-10 15:00 | 237 | 237
2017-07-10 15:30 | 246 | 245
2017-07-10 16:00 | 258 | 256
2017-07-10 16:30 | 271 | 269
2017-07-10 17:00 | 286 | 285
2017-07-10 17:30 | 302 | 302
2017-07-10 18:00 | 311 | 311
2017-07-10 18:30 | 308 | 307
2017-07-10 19:00 | 306 | 306
2017-07-10 19:30 | 301 | 301
2017-07-10 20:00 | 297 | 297
2017-07-10 20:30 | 292 | 292
2017-07-10 21:00 | 279 | 279
2017-07-10 21:30 | 264 | 264
2017-07-10 22:00 | 254 | 254
2017-07-10 22:30 | 244 | 243
2017-07-10 23:00 | 237 | 237
2017-07-10 23:30 | 221 | 220
2017-07-11 | 205 | 204
2017-07-11 00:30 | 188 | 187
2017-07-11 01:00 | 179 | 178
2017-07-11 01:30 | 172 | 172
2017-07-11 02:00 | 165 | 165
2017-07-11 02:30 | 159 | 159
2017-07-11 03:00 | 158 | 158
2017-07-11 03:30 | 157 | 157
2017-07-11 04:00 | 158 | 158
2017-07-11 04:30 | 163 | 163
2017-07-11 05:00 | 172 | 172
2017-07-11 05:30 | 186 | 185
2017-07-11 06:00 | 205 | 203
2017-07-11 06:30 | 231 | 230
2017-07-11 07:00 | 255 | 255
2017-07-11 07:30 | 276 | 276
2017-07-11 08:00 | 276 | 276
2017-07-11 08:30 | 263 | 263
2017-07-11 09:00 | 245 | 244
2017-07-11 09:30 | 233 | 233
2017-07-11 10:00 | 221 | 221
2017-07-11 10:30 | 210 | 210
2017-07-11 11:00 | 205 | 205
2017-07-11 11:30 | 202 | 202
2017-07-11 12:00 | 201 | 200
2017-07-11 12:30 | 202 | 201
2017-07-11 13:00 | 206 | 205
2017-07-11 13:30 | 210 | 209
2017-07-11 14:00 | 214 | 214
2017-07-11 14:30 | 218 | 218
2017-07-11 15:00 | 224 | 224
2017-07-11 15:30 | 223 | 223
2017-07-11 16:00 | 232 | 231
2017-07-11 16:30 | 245 | 244
2017-07-11 17:00 | 261 | 261
2017-07-11 17:30 | 279 | 279
2017-07-11 18:00 | 293 | 293
2017-07-11 18:30 | 293 | 293
2017-07-11 19:00 | 296 | 296
2017-07-11 19:30 | 292 | 292
2017-07-11 20:00 | 290 | 290
2017-07-11 20:30 | 289 | 289
2017-07-11 21:00 | 278 | 278
2017-07-11 21:30 | 265 | 265
2017-07-11 22:00 | 256 | 256
2017-07-11 22:30 | 247 | 246
2017-07-11 23:00 | 241 | 240
2017-07-11 23:30 | 226 | 226
2017-07-12 | 209 | 208
2017-07-12 00:30 | 192 | 192
2017-07-12 01:00 | 182 | 182
2017-07-12 01:30 | 173 | 173
2017-07-12 02:00 | 167 | 167
2017-07-12 02:30 | 165 | 164
2017-07-12 03:00 | 162 | 162
2017-07-12 03:30 | 161 | 161
2017-07-12 04:00 | 162 | 162
2017-07-12 04:30 | 168 | 168
2017-07-12 05:00 | 178 | 178
2017-07-12 05:30 | 193 | 193
2017-07-12 06:00 | 214 | 213
2017-07-12 06:30 | 243 | 242
2017-07-12 07:00 | 269 | 268
2017-07-12 07:30 | 290 | 290
2017-07-12 08:00 | 286 | 286
2017-07-12 08:30 | 270 | 270
2017-07-12 09:00 | 255 | 255
2017-07-12 09:30 | 240 | 240
2017-07-12 10:00 | 227 | 226
2017-07-12 10:30 | 216 | 216
2017-07-12 11:00 | 207 | 207
2017-07-12 11:30 | 200 | 199
2017-07-12 12:00 | 197 | 197
2017-07-12 12:30 | 201 | 201
2017-07-12 13:00 | 210 | 210
2017-07-12 13:30 | 217 | 217
2017-07-12 14:00 | 221 | 221
2017-07-12 14:30 | 223 | 223
2017-07-12 15:00 | 219 | 219
2017-07-12 15:30 | 226 | 226
2017-07-12 16:00 | 239 | 239
2017-07-12 16:30 | 250 | 250
2017-07-12 17:00 | 266 | 266
2017-07-12 17:30 | 288 | 288
2017-07-12 18:00 | 303 | 303
2017-07-12 18:30 | 304 | 304
2017-07-12 19:00 | 305 | 305
2017-07-12 19:30 | 300 | 300
2017-07-12 20:00 | 295 | 295
2017-07-12 20:30 | 296 | 295
2017-07-12 21:00 | 282 | 282
2017-07-12 21:30 | 271 | 271
2017-07-12 22:00 | 262 | 262
2017-07-12 22:30 | 259 | 259
2017-07-12 23:00 | 254 | 254
2017-07-12 23:30 | 238 | 238
2017-07-13 | 215 | 215
2017-07-13 00:30 | 196 | 196
2017-07-13 01:00 | 183 | 183
2017-07-13 01:30 | 177 | 177
2017-07-13 02:00 | 170 | 170
2017-07-13 02:30 | 166 | 166
2017-07-13 03:00 | 163 | 163
2017-07-13 03:30 | 162 | 162
2017-07-13 04:00 | 164 | 164
2017-07-13 04:30 | 168 | 168
2017-07-13 05:00 | 178 | 177
2017-07-13 05:30 | 194 | 193
2017-07-13 06:00 | 213 | 212
2017-07-13 06:30 | 241 | 240
2017-07-13 07:00 | 266 | 266
2017-07-13 07:30 | 288 | 288
2017-07-13 08:00 | 285 | 285
2017-07-13 08:30 | 267 | 267
2017-07-13 09:00 | 249 | 249
2017-07-13 09:30 | 234 | 234
2017-07-13 10:00 | 221 | 220
2017-07-13 10:30 | 210 | 209
2017-07-13 11:00 | 204 | 203
2017-07-13 11:30 | 199 | 199
2017-07-13 12:00 | 197 | 196
2017-07-13 12:30 | 202 | 202
2017-07-13 13:00 | 205 | 204
2017-07-13 13:30 | 208 | 208
2017-07-13 14:00 | 211 | 211
2017-07-13 14:30 | 215 | 214
2017-07-13 15:00 | 217 | 216
2017-07-13 15:30 | 225 | 224
2017-07-13 16:00 | 235 | 234
2017-07-13 16:30 | 248 | 247
2017-07-13 17:00 | 262 | 262
2017-07-13 17:30 | 280 | 279
2017-07-13 18:00 | 300 | 300
2017-07-13 18:30 | 303 | 303
2017-07-13 19:00 | 306 | 306
2017-07-13 19:30 | 304 | 304
2017-07-13 20:00 | 301 | 301
2017-07-13 20:30 | 302 | 302
2017-07-13 21:00 | 290 | 290
2017-07-13 21:30 | 275 | 275
2017-07-13 22:00 | 263 | 263
2017-07-13 22:30 | 255 | 255
2017-07-13 23:00 | 247 | 247
2017-07-13 23:30 | 231 | 231
2017-07-14 | 213 | 213
2017-07-14 00:30 | 196 | 196
2017-07-14 01:00 | 183 | 183
2017-07-14 01:30 | 175 | 175
2017-07-14 02:00 | 169 | 169
2017-07-14 02:30 | 164 | 164
2017-07-14 03:00 | 161 | 161
2017-07-14 03:30 | 162 | 162
2017-07-14 04:00 | 163 | 163
2017-07-14 04:30 | 169 | 169
2017-07-14 05:00 | 177 | 177
2017-07-14 05:30 | 194 | 194
2017-07-14 06:00 | 213 | 213
2017-07-14 06:30 | 244 | 244
2017-07-14 07:00 | 272 | 272
2017-07-14 07:30 | 291 | 291
2017-07-14 08:00 | 288 | 288
2017-07-14 08:30 | 271 | 271
2017-07-14 09:00 | 252 | 252
2017-07-14 09:30 | 236 | 236
2017-07-14 10:00 | 222 | 222
2017-07-14 10:30 | 212 | 212
2017-07-14 11:00 | 204 | 204
2017-07-14 11:30 | 197 | 197
2017-07-14 12:00 | 195 | 195
2017-07-14 12:30 | 194 | 194
2017-07-14 13:00 | 198 | 198
2017-07-14 13:30 | 203 | 202
2017-07-14 14:00 | 207 | 207
2017-07-14 14:30 | 211 | 210
2017-07-14 15:00 | 213 | 213
2017-07-14 15:30 | 218 | 217
2017-07-14 16:00 | 228 | 228
2017-07-14 16:30 | 242 | 241
2017-07-14 17:00 | 257 | 256
2017-07-14 17:30 | 269 | 269
2017-07-14 18:00 | 281 | 281
2017-07-14 18:30 | 281 | 281
2017-07-14 19:00 | 284 | 284
2017-07-14 19:30 | 281 | 280
2017-07-14 20:00 | 279 | 279
2017-07-14 20:30 | 278 | 278
2017-07-14 21:00 | 266 | 266
2017-07-14 21:30 | 256 | 256
2017-07-14 22:00 | 247 | 247
2017-07-14 22:30 | 241 | 241
2017-07-14 23:00 | 238 | 238
2017-07-14 23:30 | 225 | 225
2017-07-15 | 207 | 207
2017-07-15 00:30 | 191 | 191
2017-07-15 01:00 | 178 | 178
2017-07-15 01:30 | 168 | 168
2017-07-15 02:00 | 162 | 161
2017-07-15 02:30 | 158 | 158
2017-07-15 03:00 | 154 | 154
2017-07-15 03:30 | 153 | 153
2017-07-15 04:00 | 153 | 153
2017-07-15 04:30 | 153 | 153
2017-07-15 05:00 | 157 | 157
2017-07-15 05:30 | 163 | 163
2017-07-15 06:00 | 170 | 170
2017-07-15 06:30 | 181 | 181
2017-07-15 07:00 | 192 | 192
2017-07-15 07:30 | 205 | 205
2017-07-15 08:00 | 211 | 211
2017-07-15 08:30 | 210 | 210
2017-07-15 09:00 | 204 | 204
2017-07-15 09:30 | 194 | 194
2017-07-15 10:00 | 185 | 185
2017-07-15 10:30 | 176 | 176
2017-07-15 11:00 | 167 | 167
2017-07-15 11:30 | 160 | 160
2017-07-15 12:00 | 158 | 158
2017-07-15 12:30 | 155 | 155
2017-07-15 13:00 | 156 | 156
2017-07-15 13:30 | 159 | 159
2017-07-15 14:00 | 163 | 163
2017-07-15 14:30 | 167 | 167
2017-07-15 15:00 | 172 | 172
2017-07-15 15:30 | 182 | 182
2017-07-15 16:00 | 191 | 191
2017-07-15 16:30 | 205 | 205
2017-07-15 17:00 | 223 | 223
2017-07-15 17:30 | 235 | 235
2017-07-15 18:00 | 241 | 241
2017-07-15 18:30 | 243 | 243
2017-07-15 19:00 | 242 | 241
2017-07-15 19:30 | 236 | 236
2017-07-15 20:00 | 235 | 235
2017-07-15 20:30 | 235 | 234
2017-07-15 21:00 | 225 | 225
2017-07-15 21:30 | 218 | 217
2017-07-15 22:00 | 213 | 213
2017-07-15 22:30 | 212 | 212
2017-07-15 23:00 | 214 | 213
2017-07-15 23:30 | 203 | 203
2017-07-16 | 190 | 190
2017-07-16 00:30 | 174 | 174
2017-07-16 01:00 | 164 | 164
2017-07-16 01:30 | 155 | 155
2017-07-16 02:00 | 148 | 148
2017-07-16 02:30 | 144 | 144
2017-07-16 03:00 | 141 | 141
2017-07-16 03:30 | 141 | 141
2017-07-16 04:00 | 139 | 139
2017-07-16 04:30 | 139 | 139
2017-07-16 05:00 | 139 | 139
2017-07-16 05:30 | 143 | 143
2017-07-16 06:00 | 148 | 148
2017-07-16 06:30 | 155 | 155
2017-07-16 07:00 | 162 | 162
2017-07-16 07:30 | 171 | 171
2017-07-16 08:00 | 180 | 180
2017-07-16 08:30 | 184 | 184
2017-07-16 09:00 | 190 | 190
2017-07-16 09:30 | 186 | 186
2017-07-16 10:00 | 182 | 182
2017-07-16 10:30 | 185 | 185
2017-07-16 11:00 | 170 | 170
2017-07-16 11:30 | 163 | 162
2017-07-16 12:00 | 167 | 167
2017-07-16 12:30 | 165 | 165
2017-07-16 13:00 | 166 | 165
2017-07-16 13:30 | 162 | 162
2017-07-16 14:00 | 161 | 160
2017-07-16 14:30 | 163 | 162
2017-07-16 15:00 | 170 | 170
2017-07-16 15:30 | 178 | 178
2017-07-16 16:00 | 188 | 188
2017-07-16 16:30 | 203 | 203
2017-07-16 17:00 | 220 | 220
2017-07-16 17:30 | 236 | 236
2017-07-16 18:00 | 252 | 252
2017-07-16 18:30 | 255 | 255
2017-07-16 19:00 | 254 | 254
2017-07-16 19:30 | 249 | 249
2017-07-16 20:00 | 246 | 246
2017-07-16 20:30 | 247 | 247
2017-07-16 21:00 | 237 | 237
2017-07-16 21:30 | 227 | 227
2017-07-16 22:00 | 219 | 219
2017-07-16 22:30 | 215 | 215
2017-07-16 23:00 | 213 | 213
2017-07-16 23:30 | 203 | 203
2017-07-17 | 187 | 187
2017-07-17 00:30 | 173 | 173
2017-07-17 01:00 | 166 | 166
2017-07-17 01:30 | 160 | 160
2017-07-17 02:00 | 154 | 154
2017-07-17 02:30 | 151 | 151
2017-07-17 03:00 | 149 | 149
2017-07-17 03:30 | 148 | 148
2017-07-17 04:00 | 149 | 149
2017-07-17 04:30 | 151 | 151
2017-07-17 05:00 | 161 | 161
2017-07-17 05:30 | 179 | 178
2017-07-17 06:00 | 200 | 199
2017-07-17 06:30 | 229 | 229
2017-07-17 07:00 | 253 | 252
2017-07-17 07:30 | 271 | 269
2017-07-17 08:00 | 270 | 267
2017-07-17 08:30 | 256 | 253
2017-07-17 09:00 | 240 | 237
2017-07-17 09:30 | 228 | 226
2017-07-17 10:00 | 219 | 216
2017-07-17 10:30 | 210 | 207
2017-07-17 11:00 | 204 | 202
2017-07-17 11:30 | 203 | 201
2017-07-17 12:00 | 206 | 204
2017-07-17 12:30 | 209 | 206
2017-07-17 13:00 | 210 | 207
2017-07-17 13:30 | 212 | 211
2017-07-17 14:00 | 215 | 213
2017-07-17 14:30 | 217 | 216
2017-07-17 15:00 | 222 | 220
2017-07-17 15:30 | 228 | 227
2017-07-17 16:00 | 240 | 238
2017-07-17 16:30 | 251 | 250
2017-07-17 17:00 | 265 | 264
2017-07-17 17:30 | 278 | 278
2017-07-17 18:00 | 292 | 291
2017-07-17 18:30 | 292 | 291
2017-07-17 19:00 | 291 | 290
2017-07-17 19:30 | 285 | 284
2017-07-17 20:00 | 281 | 280
2017-07-17 20:30 | 279 | 279
2017-07-17 21:00 | 268 | 267
2017-07-17 21:30 | 254 | 253
2017-07-17 22:00 | 244 | 244
2017-07-17 22:30 | 236 | 236
2017-07-17 23:00 | 230 | 230
2017-07-17 23:30 | 215 | 215
2017-07-18 | 197 | 197
2017-07-18 00:30 | 178 | 178
2017-07-18 01:00 | 169 | 169
2017-07-18 01:30 | 162 | 162
2017-07-18 02:00 | 155 | 155
2017-07-18 02:30 | 151 | 151
2017-07-18 03:00 | 151 | 151
2017-07-18 03:30 | 150 | 150
2017-07-18 04:00 | 151 | 151
2017-07-18 04:30 | 156 | 156
2017-07-18 05:00 | 166 | 165
2017-07-18 05:30 | 180 | 179
2017-07-18 06:00 | 197 | 196
2017-07-18 06:30 | 221 | 221
2017-07-18 07:00 | 242 | 241
2017-07-18 07:30 | 260 | 259
2017-07-18 08:00 | 259 | 258
2017-07-18 08:30 | 246 | 246
2017-07-18 09:00 | 233 | 233
2017-07-18 09:30 | 219 | 219
2017-07-18 10:00 | 208 | 208
2017-07-18 10:30 | 200 | 200
2017-07-18 11:00 | 195 | 195
2017-07-18 11:30 | 192 | 192
2017-07-18 12:00 | 192 | 192
2017-07-18 12:30 | 192 | 192
2017-07-18 13:00 | 193 | 193
2017-07-18 13:30 | 198 | 198
2017-07-18 14:00 | 205 | 205
2017-07-18 14:30 | 210 | 210
2017-07-18 15:00 | 215 | 215
2017-07-18 15:30 | 222 | 222
2017-07-18 16:00 | 234 | 234
2017-07-18 16:30 | 246 | 246
2017-07-18 17:00 | 257 | 257
2017-07-18 17:30 | 269 | 269
2017-07-18 18:00 | 282 | 282
2017-07-18 18:30 | 281 | 281
2017-07-18 19:00 | 281 | 280
2017-07-18 19:30 | 274 | 274
2017-07-18 20:00 | 271 | 271
2017-07-18 20:30 | 269 | 269
2017-07-18 21:00 | 257 | 257
2017-07-18 21:30 | 246 | 246
2017-07-18 22:00 | 236 | 236
2017-07-18 22:30 | 228 | 228
2017-07-18 23:00 | 224 | 223
2017-07-18 23:30 | 210 | 210
2017-07-19 | 193 | 193
2017-07-19 00:30 | 179 | 178
2017-07-19 01:00 | 168 | 167
2017-07-19 01:30 | 162 | 160
2017-07-19 02:00 | 156 | 154
2017-07-19 02:30 | 150 | 150
2017-07-19 03:00 | 148 | 147
2017-07-19 03:30 | 148 | 148
2017-07-19 04:00 | 149 | 149
2017-07-19 04:30 | 154 | 154
2017-07-19 05:00 | 162 | 162
2017-07-19 05:30 | 177 | 177
2017-07-19 06:00 | 193 | 193
2017-07-19 06:30 | 217 | 217
2017-07-19 07:00 | 237 | 237
2017-07-19 07:30 | 258 | 257
2017-07-19 08:00 | 256 | 255
2017-07-19 08:30 | 242 | 241
2017-07-19 09:00 | 228 | 227
2017-07-19 09:30 | 215 | 214
2017-07-19 10:00 | 204 | 203
2017-07-19 10:30 | 198 | 197
2017-07-19 11:00 | 191 | 190
2017-07-19 11:30 | 188 | 187
2017-07-19 12:00 | 184 | 183
2017-07-19 12:30 | 179 | 179
2017-07-19 13:00 | 181 | 181
2017-07-19 13:30 | 184 | 184
2017-07-19 14:00 | 190 | 190
2017-07-19 14:30 | 200 | 200
2017-07-19 15:00 | 208 | 208
2017-07-19 15:30 | 218 | 218
2017-07-19 16:00 | 230 | 230
2017-07-19 16:30 | 244 | 244
2017-07-19 17:00 | 263 | 263
2017-07-19 17:30 | 281 | 281
2017-07-19 18:00 | 300 | 300
2017-07-19 18:30 | 304 | 303
2017-07-19 19:00 | 307 | 307
2017-07-19 19:30 | 308 | 308
2017-07-19 20:00 | 304 | 303
2017-07-19 20:30 | 299 | 298
2017-07-19 21:00 | 288 | 287
2017-07-19 21:30 | 274 | 272
2017-07-19 22:00 | 259 | 258
2017-07-19 22:30 | 245 | 245
2017-07-19 23:00 | 240 | 240
2017-07-19 23:30 | 225 | 225
2017-07-20 | 207 | 206
2017-07-20 00:30 | 190 | 189
2017-07-20 01:00 | 178 | 177
2017-07-20 01:30 | 169 | 168
2017-07-20 02:00 | 164 | 162
2017-07-20 02:30 | 162 | 160
2017-07-20 03:00 | 159 | 157
2017-07-20 03:30 | 160 | 159
2017-07-20 04:00 | 162 | 160
2017-07-20 04:30 | 167 | 165
2017-07-20 05:00 | 176 | 175
2017-07-20 05:30 | 192 | 191
2017-07-20 06:00 | 212 | 212
2017-07-20 06:30 | 245 | 245
2017-07-20 07:00 | 272 | 271
2017-07-20 07:30 | 289 | 288
2017-07-20 08:00 | 285 | 284
2017-07-20 08:30 | 288 | 287
2017-07-20 09:00 | 269 | 268
2017-07-20 09:30 | 253 | 253
2017-07-20 10:00 | 236 | 236
2017-07-20 10:30 | 225 | 224
2017-07-20 11:00 | 218 | 218
2017-07-20 11:30 | 212 | 212
2017-07-20 12:00 | 208 | 208
2017-07-20 12:30 | 206 | 206
2017-07-20 13:00 | 205 | 204
2017-07-20 13:30 | 205 | 205
2017-07-20 14:00 | 195 | 195
2017-07-20 14:30 | 195 | 195
2017-07-20 15:00 | 201 | 201
2017-07-20 15:30 | 211 | 211
2017-07-20 16:00 | 224 | 224
2017-07-20 16:30 | 239 | 239
2017-07-20 17:00 | 257 | 257
2017-07-20 17:30 | 275 | 275
2017-07-20 18:00 | 294 | 294
2017-07-20 18:30 | 299 | 299
2017-07-20 19:00 | 303 | 303
2017-07-20 19:30 | 299 | 299
2017-07-20 20:00 | 297 | 296
2017-07-20 20:30 | 294 | 294
2017-07-20 21:00 | 281 | 281
2017-07-20 21:30 | 265 | 265
2017-07-20 22:00 | 255 | 254
2017-07-20 22:30 | 246 | 246
2017-07-20 23:00 | 242 | 242
2017-07-20 23:30 | 227 | 227
2017-07-21 | 209 | 209
2017-07-21 00:30 | 190 | 190
2017-07-21 01:00 | 180 | 179
2017-07-21 01:30 | 171 | 170
2017-07-21 02:00 | 165 | 163
2017-07-21 02:30 | 161 | 160
2017-07-21 03:00 | 160 | 158
2017-07-21 03:30 | 160 | 159
2017-07-21 04:00 | 162 | 161
2017-07-21 04:30 | 168 | 167
2017-07-21 05:00 | 178 | 177
2017-07-21 05:30 | 194 | 194
2017-07-21 06:00 | 216 | 216
2017-07-21 06:30 | 249 | 249
2017-07-21 07:00 | 278 | 278
2017-07-21 07:30 | 297 | 297
2017-07-21 08:00 | 292 | 291
2017-07-21 08:30 | 273 | 273
2017-07-21 09:00 | 253 | 253
2017-07-21 09:30 | 234 | 234
2017-07-21 10:00 | 218 | 217
2017-07-21 10:30 | 205 | 204
2017-07-21 11:00 | 192 | 192
2017-07-21 11:30 | 185 | 184
2017-07-21 12:00 | 180 | 180
2017-07-21 12:30 | 175 | 175
2017-07-21 13:00 | 175 | 175
2017-07-21 13:30 | 177 | 177
2017-07-21 14:00 | 181 | 181
2017-07-21 14:30 | 187 | 187
2017-07-21 15:00 | 192 | 192
2017-07-21 15:30 | 200 | 200
2017-07-21 16:00 | 214 | 214
2017-07-21 16:30 | 230 | 230
2017-07-21 17:00 | 250 | 250
2017-07-21 17:30 | 267 | 267
2017-07-21 18:00 | 284 | 283
2017-07-21 18:30 | 289 | 288
2017-07-21 19:00 | 293 | 293
2017-07-21 19:30 | 291 | 291
2017-07-21 20:00 | 289 | 289
2017-07-21 20:30 | 289 | 289
2017-07-21 21:00 | 279 | 279
2017-07-21 21:30 | 270 | 269
2017-07-21 22:00 | 260 | 260
2017-07-21 22:30 | 252 | 252
2017-07-21 23:00 | 246 | 246
2017-07-21 23:30 | 233 | 233
2017-07-22 | 216 | 216
2017-07-22 00:30 | 197 | 197
2017-07-22 01:00 | 184 | 184
2017-07-22 01:30 | 175 | 175
2017-07-22 02:00 | 168 | 168
2017-07-22 02:30 | 164 | 163
2017-07-22 03:00 | 160 | 159
2017-07-22 03:30 | 158 | 157
2017-07-22 04:00 | 158 | 157
2017-07-22 04:30 | 158 | 157
2017-07-22 05:00 | 162 | 161
2017-07-22 05:30 | 169 | 168
2017-07-22 06:00 | 179 | 179
2017-07-22 06:30 | 194 | 194
2017-07-22 07:00 | 208 | 208
2017-07-22 07:30 | 223 | 223
2017-07-22 08:00 | 229 | 229
2017-07-22 08:30 | 228 | 228
2017-07-22 09:00 | 220 | 220
2017-07-22 09:30 | 207 | 207
2017-07-22 10:00 | 193 | 193
2017-07-22 10:30 | 179 | 179
2017-07-22 11:00 | 168 | 168
2017-07-22 11:30 | 157 | 157
2017-07-22 12:00 | 151 | 151
2017-07-22 12:30 | 147 | 146
2017-07-22 13:00 | 145 | 144
2017-07-22 13:30 | 146 | 146
2017-07-22 14:00 | 149 | 149
2017-07-22 14:30 | 153 | 152
2017-07-22 15:00 | 161 | 160
2017-07-22 15:30 | 170 | 170
2017-07-22 16:00 | 182 | 182
2017-07-22 16:30 | 197 | 197
2017-07-22 17:00 | 216 | 216
2017-07-22 17:30 | 231 | 231
2017-07-22 18:00 | 249 | 248
2017-07-22 18:30 | 255 | 255
2017-07-22 19:00 | 258 | 257
2017-07-22 19:30 | 256 | 255
2017-07-22 20:00 | 255 | 254
2017-07-22 20:30 | 256 | 255
2017-07-22 21:00 | 246 | 246
2017-07-22 21:30 | 240 | 239
2017-07-22 22:00 | 232 | 232
2017-07-22 22:30 | 227 | 227
2017-07-22 23:00 | 227 | 227
2017-07-22 23:30 | 216 | 216
2017-07-23 | 201 | 201
2017-07-23 00:30 | 185 | 185
2017-07-23 01:00 | 174 | 173
2017-07-23 01:30 | 164 | 164
2017-07-23 02:00 | 157 | 157
2017-07-23 02:30 | 152 | 152
2017-07-23 03:00 | 149 | 149
2017-07-23 03:30 | 147 | 147
2017-07-23 04:00 | 148 | 148
2017-07-23 04:30 | 149 | 148
2017-07-23 05:00 | 149 | 149
2017-07-23 05:30 | 154 | 154
2017-07-23 06:00 | 160 | 160
2017-07-23 06:30 | 167 | 167
2017-07-23 07:00 | 175 | 175
2017-07-23 07:30 | 186 | 186
2017-07-23 08:00 | 192 | 192
2017-07-23 08:30 | 193 | 193
2017-07-23 09:00 | 190 | 189
2017-07-23 09:30 | 181 | 180
2017-07-23 10:00 | 169 | 169
2017-07-23 10:30 | 160 | 160
2017-07-23 11:00 | 150 | 150
2017-07-23 11:30 | 142 | 142
2017-07-23 12:00 | 138 | 138
2017-07-23 12:30 | 135 | 135
2017-07-23 13:00 | 134 | 134
2017-07-23 13:30 | 136 | 136
2017-07-23 14:00 | 140 | 140
2017-07-23 14:30 | 146 | 146
2017-07-23 15:00 | 153 | 153
2017-07-23 15:30 | 164 | 164
2017-07-23 16:00 | 177 | 177
2017-07-23 16:30 | 192 | 191
2017-07-23 17:00 | 211 | 211
2017-07-23 17:30 | 230 | 229
2017-07-23 18:00 | 251 | 250
2017-07-23 18:30 | 259 | 258
2017-07-23 19:00 | 261 | 260
2017-07-23 19:30 | 258 | 258
2017-07-23 20:00 | 257 | 256
2017-07-23 20:30 | 257 | 257
2017-07-23 21:00 | 248 | 247
2017-07-23 21:30 | 238 | 238
2017-07-23 22:00 | 229 | 229
2017-07-23 22:30 | 222 | 222
2017-07-23 23:00 | 220 | 220
2017-07-23 23:30 | 210 | 210
2017-07-24 | 195 | 195
2017-07-24 00:30 | 180 | 179
2017-07-24 01:00 | 169 | 169
2017-07-24 01:30 | 161 | 161
2017-07-24 02:00 | 155 | 154
2017-07-24 02:30 | 151 | 151
2017-07-24 03:00 | 148 | 147
2017-07-24 03:30 | 150 | 150
2017-07-24 04:00 | 152 | 152
2017-07-24 04:30 | 159 | 159
2017-07-24 05:00 | 171 | 171
2017-07-24 05:30 | 192 | 191
2017-07-24 06:00 | 215 | 214
2017-07-24 06:30 | 250 | 249
2017-07-24 07:00 | 281 | 281
2017-07-24 07:30 | 303 | 302
2017-07-24 08:00 | 300 | 299
2017-07-24 08:30 | 281 | 281
2017-07-24 09:00 | 258 | 258
2017-07-24 09:30 | 241 | 241
2017-07-24 10:00 | 224 | 224
2017-07-24 10:30 | 213 | 212
2017-07-24 11:00 | 201 | 201
2017-07-24 11:30 | 192 | 191
2017-07-24 12:00 | 189 | 188
2017-07-24 12:30 | 186 | 185
2017-07-24 13:00 | 186 | 186
2017-07-24 13:30 | 188 | 188
2017-07-24 14:00 | 192 | 192
2017-07-24 14:30 | 197 | 196
2017-07-24 15:00 | 203 | 202
2017-07-24 15:30 | 211 | 211
2017-07-24 16:00 | 224 | 223
2017-07-24 16:30 | 238 | 237
2017-07-24 17:00 | 254 | 253
2017-07-24 17:30 | 270 | 270
2017-07-24 18:00 | 288 | 288
2017-07-24 18:30 | 292 | 292
2017-07-24 19:00 | 294 | 293
2017-07-24 19:30 | 290 | 289
2017-07-24 20:00 | 288 | 288
2017-07-24 20:30 | 286 | 286
2017-07-24 21:00 | 275 | 274
2017-07-24 21:30 | 263 | 262
2017-07-24 22:00 | 253 | 252
2017-07-24 22:30 | 244 | 244
2017-07-24 23:00 | 238 | 238
2017-07-24 23:30 | 223 | 223
2017-07-25 | 206 | 205
2017-07-25 00:30 | 189 | 188
2017-07-25 01:00 | 177 | 177
2017-07-25 01:30 | 169 | 169
2017-07-25 02:00 | 164 | 164
2017-07-25 02:30 | 162 | 161
2017-07-25 03:00 | 161 | 160
2017-07-25 03:30 | 161 | 160
2017-07-25 04:00 | 161 | 160
2017-07-25 04:30 | 168 | 167
2017-07-25 05:00 | 177 | 175
2017-07-25 05:30 | 200 | 197
2017-07-25 06:00 | 223 | 221
2017-07-25 06:30 | 253 | 252
2017-07-25 07:00 | 286 | 285
2017-07-25 07:30 | 306 | 305
2017-07-25 08:00 | 299 | 299
2017-07-25 08:30 | 278 | 278
2017-07-25 09:00 | 254 | 254
2017-07-25 09:30 | 235 | 235
2017-07-25 10:00 | 216 | 216
2017-07-25 10:30 | 204 | 204
2017-07-25 11:00 | 195 | 195
2017-07-25 11:30 | 188 | 187
2017-07-25 12:00 | 185 | 183
2017-07-25 12:30 | 183 | 181
2017-07-25 13:00 | 185 | 184
2017-07-25 13:30 | 187 | 186
2017-07-25 14:00 | 192 | 191
2017-07-25 14:30 | 197 | 196
2017-07-25 15:00 | 202 | 202
2017-07-25 15:30 | 212 | 211
2017-07-25 16:00 | 226 | 225
2017-07-25 16:30 | 240 | 239
2017-07-25 17:00 | 257 | 257
2017-07-25 17:30 | 274 | 274
2017-07-25 18:00 | 295 | 295
2017-07-25 18:30 | 302 | 302
2017-07-25 19:00 | 306 | 306
2017-07-25 19:30 | 304 | 304
2017-07-25 20:00 | 302 | 302
2017-07-25 20:30 | 302 | 301
2017-07-25 21:00 | 291 | 291
2017-07-25 21:30 | 277 | 277
2017-07-25 22:00 | 265 | 265
2017-07-25 22:30 | 254 | 254
2017-07-25 23:00 | 246 | 246
2017-07-25 23:30 | 232 | 232
2017-07-26 | 214 | 214
2017-07-26 00:30 | 196 | 196
2017-07-26 01:00 | 183 | 183
2017-07-26 01:30 | 176 | 176
2017-07-26 02:00 | 169 | 169
2017-07-26 02:30 | 166 | 166
2017-07-26 03:00 | 164 | 164
2017-07-26 03:30 | 164 | 164
2017-07-26 04:00 | 166 | 166
2017-07-26 04:30 | 173 | 173
2017-07-26 05:00 | 184 | 184
2017-07-26 05:30 | 204 | 203
2017-07-26 06:00 | 228 | 226
2017-07-26 06:30 | 262 | 262
2017-07-26 07:00 | 292 | 292
2017-07-26 07:30 | 311 | 311
2017-07-26 08:00 | 304 | 304
2017-07-26 08:30 | 283 | 283
2017-07-26 09:00 | 264 | 263
2017-07-26 09:30 | 245 | 245
2017-07-26 10:00 | 228 | 227
2017-07-26 10:30 | 211 | 210
2017-07-26 11:00 | 201 | 201
2017-07-26 11:30 | 194 | 194
2017-07-26 12:00 | 192 | 191
2017-07-26 12:30 | 189 | 188
2017-07-26 13:00 | 191 | 190
2017-07-26 13:30 | 193 | 192
2017-07-26 14:00 | 198 | 198
2017-07-26 14:30 | 204 | 203
2017-07-26 15:00 | 210 | 209
2017-07-26 15:30 | 219 | 219
2017-07-26 16:00 | 230 | 230
2017-07-26 16:30 | 244 | 243
2017-07-26 17:00 | 257 | 257
2017-07-26 17:30 | 273 | 272
2017-07-26 18:00 | 290 | 290
2017-07-26 18:30 | 291 | 291
2017-07-26 19:00 | 294 | 294
2017-07-26 19:30 | 293 | 293
2017-07-26 20:00 | 290 | 289
2017-07-26 20:30 | 290 | 289
2017-07-26 21:00 | 276 | 276
2017-07-26 21:30 | 264 | 264
2017-07-26 22:00 | 253 | 253
2017-07-26 22:30 | 245 | 245
2017-07-26 23:00 | 239 | 239
2017-07-26 23:30 | 225 | 225
2017-07-27 | 208 | 208
2017-07-27 00:30 | 191 | 191
2017-07-27 01:00 | 180 | 179
2017-07-27 01:30 | 170 | 170
2017-07-27 02:00 | 165 | 165
2017-07-27 02:30 | 160 | 160
2017-07-27 03:00 | 159 | 159
2017-07-27 03:30 | 158 | 158
2017-07-27 04:00 | 161 | 161
2017-07-27 04:30 | 168 | 168
2017-07-27 05:00 | 178 | 178
2017-07-27 05:30 | 197 | 196
2017-07-27 06:00 | 220 | 218
2017-07-27 06:30 | 251 | 250
2017-07-27 07:00 | 281 | 280
2017-07-27 07:30 | 298 | 298
2017-07-27 08:00 | 290 | 290
2017-07-27 08:30 | 267 | 267
2017-07-27 09:00 | 245 | 245
2017-07-27 09:30 | 230 | 230
2017-07-27 10:00 | 215 | 215
2017-07-27 10:30 | 203 | 203
2017-07-27 11:00 | 193 | 191
2017-07-27 11:30 | 189 | 187
2017-07-27 12:00 | 186 | 184
2017-07-27 12:30 | 184 | 182
2017-07-27 13:00 | 185 | 183
2017-07-27 13:30 | 187 | 186
2017-07-27 14:00 | 192 | 191
2017-07-27 14:30 | 198 | 197
2017-07-27 15:00 | 203 | 202
2017-07-27 15:30 | 212 | 212
2017-07-27 16:00 | 225 | 224
2017-07-27 16:30 | 240 | 239
2017-07-27 17:00 | 256 | 255
2017-07-27 17:30 | 269 | 269
2017-07-27 18:00 | 286 | 286
2017-07-27 18:30 | 292 | 292
2017-07-27 19:00 | 294 | 294
2017-07-27 19:30 | 291 | 291
2017-07-27 20:00 | 289 | 289
2017-07-27 20:30 | 290 | 289
2017-07-27 21:00 | 279 | 278
2017-07-27 21:30 | 265 | 265
2017-07-27 22:00 | 254 | 254
2017-07-27 22:30 | 247 | 247
2017-07-27 23:00 | 242 | 242
2017-07-27 23:30 | 227 | 227
2017-07-28 | 209 | 209
2017-07-28 00:30 | 192 | 192
2017-07-28 01:00 | 179 | 179
2017-07-28 01:30 | 171 | 171
2017-07-28 02:00 | 164 | 164
2017-07-28 02:30 | 161 | 161
2017-07-28 03:00 | 159 | 159
2017-07-28 03:30 | 159 | 158
2017-07-28 04:00 | 159 | 159
2017-07-28 04:30 | 166 | 165
2017-07-28 05:00 | 176 | 175
2017-07-28 05:30 | 194 | 192
2017-07-28 06:00 | 215 | 214
2017-07-28 06:30 | 247 | 245
2017-07-28 07:00 | 275 | 272
2017-07-28 07:30 | 292 | 292
2017-07-28 08:00 | 285 | 285
2017-07-28 08:30 | 266 | 266
2017-07-28 09:00 | 246 | 246
2017-07-28 09:30 | 231 | 231
2017-07-28 10:00 | 218 | 218
2017-07-28 10:30 | 211 | 211
2017-07-28 11:00 | 207 | 207
2017-07-28 11:30 | 198 | 198
2017-07-28 12:00 | 193 | 192
2017-07-28 12:30 | 187 | 187
2017-07-28 13:00 | 186 | 186
2017-07-28 13:30 | 188 | 188
2017-07-28 14:00 | 191 | 191
2017-07-28 14:30 | 195 | 195
2017-07-28 15:00 | 201 | 201
2017-07-28 15:30 | 210 | 210
2017-07-28 16:00 | 224 | 224
2017-07-28 16:30 | 238 | 238
2017-07-28 17:00 | 251 | 251
2017-07-28 17:30 | 259 | 259
2017-07-28 18:00 | 270 | 270
2017-07-28 18:30 | 271 | 271
2017-07-28 19:00 | 273 | 273
2017-07-28 19:30 | 269 | 268
2017-07-28 20:00 | 266 | 265
2017-07-28 20:30 | 266 | 266
2017-07-28 21:00 | 256 | 256
2017-07-28 21:30 | 246 | 246
2017-07-28 22:00 | 239 | 238
2017-07-28 22:30 | 232 | 232
2017-07-28 23:00 | 231 | 230
2017-07-28 23:30 | 219 | 218
2017-07-29 | 201 | 201
2017-07-29 00:30 | 185 | 184
2017-07-29 01:00 | 173 | 173
2017-07-29 01:30 | 164 | 164
2017-07-29 02:00 | 157 | 157
2017-07-29 02:30 | 154 | 154
2017-07-29 03:00 | 150 | 150
2017-07-29 03:30 | 148 | 148
2017-07-29 04:00 | 148 | 148
2017-07-29 04:30 | 150 | 150
2017-07-29 05:00 | 153 | 153
2017-07-29 05:30 | 160 | 160
2017-07-29 06:00 | 168 | 168
2017-07-29 06:30 | 181 | 181
2017-07-29 07:00 | 193 | 193
2017-07-29 07:30 | 206 | 206
2017-07-29 08:00 | 209 | 208
2017-07-29 08:30 | 206 | 206
2017-07-29 09:00 | 200 | 200
2017-07-29 09:30 | 189 | 188
2017-07-29 10:00 | 176 | 176
2017-07-29 10:30 | 165 | 165
2017-07-29 11:00 | 157 | 157
2017-07-29 11:30 | 150 | 150
2017-07-29 12:00 | 147 | 146
2017-07-29 12:30 | 144 | 144
2017-07-29 13:00 | 144 | 144
2017-07-29 13:30 | 145 | 145
2017-07-29 14:00 | 148 | 148
2017-07-29 14:30 | 152 | 152
2017-07-29 15:00 | 159 | 159
2017-07-29 15:30 | 168 | 168
2017-07-29 16:00 | 181 | 181
2017-07-29 16:30 | 195 | 195
2017-07-29 17:00 | 215 | 214
2017-07-29 17:30 | 226 | 226
2017-07-29 18:00 | 240 | 240
2017-07-29 18:30 | 247 | 247
2017-07-29 19:00 | 248 | 248
2017-07-29 19:30 | 246 | 246
2017-07-29 20:00 | 245 | 245
2017-07-29 20:30 | 245 | 245
2017-07-29 21:00 | 238 | 238
2017-07-29 21:30 | 231 | 231
2017-07-29 22:00 | 227 | 226
2017-07-29 22:30 | 225 | 224
2017-07-29 23:00 | 225 | 225
2017-07-29 23:30 | 215 | 215
2017-07-30 | 199 | 199
2017-07-30 00:30 | 183 | 183
2017-07-30 01:00 | 172 | 172
2017-07-30 01:30 | 164 | 164
2017-07-30 02:00 | 157 | 157
2017-07-30 02:30 | 153 | 153
2017-07-30 03:00 | 151 | 151
2017-07-30 03:30 | 150 | 150
2017-07-30 04:00 | 149 | 149
2017-07-30 04:30 | 150 | 150
2017-07-30 05:00 | 152 | 152
2017-07-30 05:30 | 157 | 157
2017-07-30 06:00 | 164 | 164
2017-07-30 06:30 | 172 | 172
2017-07-30 07:00 | 181 | 181
2017-07-30 07:30 | 192 | 191
2017-07-30 08:00 | 196 | 196
2017-07-30 08:30 | 196 | 196
2017-07-30 09:00 | 190 | 190
2017-07-30 09:30 | 183 | 183
2017-07-30 10:00 | 171 | 171
2017-07-30 10:30 | 160 | 159
2017-07-30 11:00 | 151 | 151
2017-07-30 11:30 | 145 | 145
2017-07-30 12:00 | 140 | 140
2017-07-30 12:30 | 138 | 138
2017-07-30 13:00 | 137 | 137
2017-07-30 13:30 | 140 | 139
2017-07-30 14:00 | 143 | 142
2017-07-30 14:30 | 149 | 149
2017-07-30 15:00 | 157 | 157
2017-07-30 15:30 | 168 | 168
2017-07-30 16:00 | 181 | 181
2017-07-30 16:30 | 198 | 198
2017-07-30 17:00 | 216 | 216
2017-07-30 17:30 | 232 | 232
2017-07-30 18:00 | 250 | 250
2017-07-30 18:30 | 258 | 258
2017-07-30 19:00 | 258 | 258
2017-07-30 19:30 | 254 | 254
2017-07-30 20:00 | 251 | 250
2017-07-30 20:30 | 250 | 250
2017-07-30 21:00 | 242 | 242
2017-07-30 21:30 | 231 | 231
2017-07-30 22:00 | 223 | 223
2017-07-30 22:30 | 218 | 217
2017-07-30 23:00 | 216 | 216
2017-07-30 23:30 | 206 | 205
2017-07-31 | 192 | 191
2017-07-31 00:30 | 177 | 176
2017-07-31 01:00 | 168 | 166
2017-07-31 01:30 | 160 | 158
2017-07-31 02:00 | 154 | 152
2017-07-31 02:30 | 151 | 149
2017-07-31 03:00 | 149 | 146
2017-07-31 03:30 | 149 | 146
2017-07-31 04:00 | 149 | 147
2017-07-31 04:30 | 156 | 154
2017-07-31 05:00 | 166 | 165
2017-07-31 05:30 | 182 | 182
2017-07-31 06:00 | 203 | 203
2017-07-31 06:30 | 231 | 230
2017-07-31 07:00 | 256 | 256
2017-07-31 07:30 | 273 | 273
2017-07-31 08:00 | 277 | 276
2017-07-31 08:30 | 266 | 266
2017-07-31 09:00 | 252 | 251
2017-07-31 09:30 | 238 | 238
2017-07-31 10:00 | 223 | 223
2017-07-31 10:30 | 207 | 207
2017-07-31 11:00 | 199 | 199
2017-07-31 11:30 | 193 | 193
2017-07-31 12:00 | 191 | 191
2017-07-31 12:30 | 191 | 191
2017-07-31 13:00 | 192 | 192
2017-07-31 13:30 | 195 | 195
2017-07-31 14:00 | 200 | 200
2017-07-31 14:30 | 207 | 207
2017-07-31 15:00 | 212 | 212
2017-07-31 15:30 | 220 | 220
2017-07-31 16:00 | 232 | 232
2017-07-31 16:30 | 244 | 244
2017-07-31 17:00 | 259 | 259
2017-07-31 17:30 | 274 | 274
2017-07-31 18:00 | 289 | 289
2017-07-31 18:30 | 291 | 291
2017-07-31 19:00 | 291 | 291
2017-07-31 19:30 | 284 | 284
2017-07-31 20:00 | 279 | 279
2017-07-31 20:30 | 277 | 277
2017-07-31 21:00 | 265 | 265
2017-07-31 21:30 | 252 | 252
2017-07-31 22:00 | 241 | 241
2017-07-31 22:30 | 234 | 233
2017-07-31 23:00 | 230 | 230
2017-07-31 23:30 | 216 | 216
2017-08-01 | 201 | 201
2017-08-01 00:30 | 185 | 184
2017-08-01 01:00 | 173 | 173
2017-08-01 01:30 | 167 | 166
2017-08-01 02:00 | 161 | 160
2017-08-01 02:30 | 158 | 157
2017-08-01 03:00 | 157 | 155
2017-08-01 03:30 | 157 | 155
2017-08-01 04:00 | 157 | 155
2017-08-01 04:30 | 163 | 162
2017-08-01 05:00 | 172 | 171
2017-08-01 05:30 | 189 | 189
2017-08-01 06:00 | 210 | 210
2017-08-01 06:30 | 237 | 237
2017-08-01 07:00 | 260 | 260
2017-08-01 07:30 | 275 | 275
2017-08-01 08:00 | 267 | 267
2017-08-01 08:30 | 251 | 250
2017-08-01 09:00 | 231 | 231
2017-08-01 09:30 | 218 | 218
2017-08-01 10:00 | 205 | 205
2017-08-01 10:30 | 197 | 197
2017-08-01 11:00 | 190 | 190
2017-08-01 11:30 | 185 | 185
2017-08-01 12:00 | 183 | 183
2017-08-01 12:30 | 181 | 181
2017-08-01 13:00 | 182 | 182
2017-08-01 13:30 | 186 | 186
2017-08-01 14:00 | 191 | 191
2017-08-01 14:30 | 197 | 197
2017-08-01 15:00 | 204 | 204
2017-08-01 15:30 | 213 | 213
2017-08-01 16:00 | 227 | 227
2017-08-01 16:30 | 242 | 242
2017-08-01 17:00 | 259 | 259
2017-08-01 17:30 | 275 | 275
2017-08-01 18:00 | 295 | 295
2017-08-01 18:30 | 301 | 300
2017-08-01 19:00 | 303 | 303
2017-08-01 19:30 | 298 | 297
2017-08-01 20:00 | 294 | 294
2017-08-01 20:30 | 294 | 293
2017-08-01 21:00 | 282 | 281
2017-08-01 21:30 | 268 | 266
2017-08-01 22:00 | 253 | 253
2017-08-01 22:30 | 245 | 244
2017-08-01 23:00 | 240 | 240
2017-08-01 23:30 | 226 | 226
2017-08-02 | 208 | 208
2017-08-02 00:30 | 191 | 191
2017-08-02 01:00 | 180 | 180
2017-08-02 01:30 | 172 | 172
2017-08-02 02:00 | 166 | 166
2017-08-02 02:30 | 162 | 162
2017-08-02 03:00 | 160 | 160
2017-08-02 03:30 | 161 | 161
2017-08-02 04:00 | 160 | 160
2017-08-02 04:30 | 166 | 166
2017-08-02 05:00 | 176 | 176
2017-08-02 05:30 | 196 | 195
2017-08-02 06:00 | 219 | 217
2017-08-02 06:30 | 252 | 252
2017-08-02 07:00 | 279 | 278
2017-08-02 07:30 | 296 | 295
2017-08-02 08:00 | 287 | 287
2017-08-02 08:30 | 266 | 266
2017-08-02 09:00 | 245 | 245
2017-08-02 09:30 | 227 | 227
2017-08-02 10:00 | 213 | 213
2017-08-02 10:30 | 203 | 203
2017-08-02 11:00 | 195 | 195
2017-08-02 11:30 | 191 | 191
2017-08-02 12:00 | 189 | 189
2017-08-02 12:30 | 190 | 190
2017-08-02 13:00 | 195 | 194
2017-08-02 13:30 | 198 | 198
2017-08-02 14:00 | 202 | 202
2017-08-02 14:30 | 207 | 207
2017-08-02 15:00 | 210 | 210
2017-08-02 15:30 | 218 | 218
2017-08-02 16:00 | 230 | 230
2017-08-02 16:30 | 245 | 245
2017-08-02 17:00 | 262 | 262
2017-08-02 17:30 | 278 | 277
2017-08-02 18:00 | 296 | 296
2017-08-02 18:30 | 304 | 303
2017-08-02 19:00 | 307 | 306
2017-08-02 19:30 | 302 | 301
2017-08-02 20:00 | 299 | 298
2017-08-02 20:30 | 297 | 296
2017-08-02 21:00 | 286 | 285
2017-08-02 21:30 | 273 | 271
2017-08-02 22:00 | 258 | 257
2017-08-02 22:30 | 248 | 247
2017-08-02 23:00 | 240 | 240
2017-08-02 23:30 | 224 | 224
2017-08-03 | 204 | 204
2017-08-03 00:30 | 185 | 185
2017-08-03 01:00 | 173 | 172
2017-08-03 01:30 | 165 | 164
2017-08-03 02:00 | 158 | 157
2017-08-03 02:30 | 155 | 154
2017-08-03 03:00 | 154 | 153
2017-08-03 03:30 | 156 | 155
2017-08-03 04:00 | 159 | 159
2017-08-03 04:30 | 165 | 165
2017-08-03 05:00 | 175 | 175
2017-08-03 05:30 | 192 | 192
2017-08-03 06:00 | 215 | 214
2017-08-03 06:30 | 246 | 245
2017-08-03 07:00 | 271 | 270
2017-08-03 07:30 | 288 | 288
2017-08-03 08:00 | 282 | 282
2017-08-03 08:30 | 266 | 266
2017-08-03 09:00 | 251 | 251
2017-08-03 09:30 | 235 | 234
2017-08-03 10:00 | 219 | 219
2017-08-03 10:30 | 209 | 209
2017-08-03 11:00 | 203 | 203
2017-08-03 11:30 | 204 | 204
2017-08-03 12:00 | 207 | 207
2017-08-03 12:30 | 215 | 215
2017-08-03 13:00 | 213 | 213
2017-08-03 13:30 | 214 | 214
2017-08-03 14:00 | 215 | 215
2017-08-03 14:30 | 215 | 215
2017-08-03 15:00 | 217 | 217
2017-08-03 15:30 | 223 | 223
2017-08-03 16:00 | 232 | 232
2017-08-03 16:30 | 243 | 243
2017-08-03 17:00 | 258 | 258
2017-08-03 17:30 | 277 | 276
2017-08-03 18:00 | 294 | 294
2017-08-03 18:30 | 300 | 299
2017-08-03 19:00 | 303 | 302
2017-08-03 19:30 | 299 | 298
2017-08-03 20:00 | 296 | 295
2017-08-03 20:30 | 295 | 294
2017-08-03 21:00 | 284 | 284
2017-08-03 21:30 | 271 | 270
2017-08-03 22:00 | 257 | 257
2017-08-03 22:30 | 247 | 247
2017-08-03 23:00 | 244 | 243
2017-08-03 23:30 | 230 | 230
2017-08-04 | 212 | 212
2017-08-04 00:30 | 193 | 193
2017-08-04 01:00 | 181 | 180
2017-08-04 01:30 | 173 | 172
2017-08-04 02:00 | 167 | 166
2017-08-04 02:30 | 163 | 163
2017-08-04 03:00 | 161 | 160
2017-08-04 03:30 | 161 | 160
2017-08-04 04:00 | 161 | 161
2017-08-04 04:30 | 166 | 166
2017-08-04 05:00 | 175 | 174
2017-08-04 05:30 | 190 | 190
2017-08-04 06:00 | 207 | 207
2017-08-04 06:30 | 233 | 233
2017-08-04 07:00 | 257 | 256
2017-08-04 07:30 | 272 | 272
2017-08-04 08:00 | 267 | 267
2017-08-04 08:30 | 252 | 252
2017-08-04 09:00 | 235 | 234
2017-08-04 09:30 | 220 | 220
2017-08-04 10:00 | 210 | 209
2017-08-04 10:30 | 202 | 201
2017-08-04 11:00 | 193 | 193
2017-08-04 11:30 | 185 | 185
2017-08-04 12:00 | 182 | 181
2017-08-04 12:30 | 181 | 181
2017-08-04 13:00 | 181 | 181
2017-08-04 13:30 | 183 | 182
2017-08-04 14:00 | 187 | 186
2017-08-04 14:30 | 193 | 193
2017-08-04 15:00 | 198 | 198
2017-08-04 15:30 | 209 | 209
2017-08-04 16:00 | 223 | 222
2017-08-04 16:30 | 236 | 236
2017-08-04 17:00 | 249 | 248
2017-08-04 17:30 | 258 | 257
2017-08-04 18:00 | 271 | 270
2017-08-04 18:30 | 275 | 274
2017-08-04 19:00 | 278 | 277
2017-08-04 19:30 | 275 | 274
2017-08-04 20:00 | 272 | 271
2017-08-04 20:30 | 272 | 272
2017-08-04 21:00 | 263 | 263
2017-08-04 21:30 | 254 | 254
2017-08-04 22:00 | 246 | 246
2017-08-04 22:30 | 242 | 242
2017-08-04 23:00 | 240 | 240
2017-08-04 23:30 | 228 | 228
2017-08-05 | 210 | 210
2017-08-05 00:30 | 193 | 193
2017-08-05 01:00 | 182 | 182
2017-08-05 01:30 | 174 | 174
2017-08-05 02:00 | 167 | 166
2017-08-05 02:30 | 164 | 164
2017-08-05 03:00 | 161 | 161
2017-08-05 03:30 | 159 | 159
2017-08-05 04:00 | 159 | 159
2017-08-05 04:30 | 160 | 160
2017-08-05 05:00 | 164 | 164
2017-08-05 05:30 | 169 | 169
2017-08-05 06:00 | 177 | 177
2017-08-05 06:30 | 189 | 189
2017-08-05 07:00 | 201 | 201
2017-08-05 07:30 | 211 | 211
2017-08-05 08:00 | 214 | 213
2017-08-05 08:30 | 211 | 211
2017-08-05 09:00 | 204 | 204
2017-08-05 09:30 | 193 | 193
2017-08-05 10:00 | 181 | 181
2017-08-05 10:30 | 170 | 170
2017-08-05 11:00 | 160 | 160
2017-08-05 11:30 | 152 | 152
2017-08-05 12:00 | 147 | 147
2017-08-05 12:30 | 143 | 142
2017-08-05 13:00 | 141 | 141
2017-08-05 13:30 | 143 | 142
2017-08-05 14:00 | 148 | 148
2017-08-05 14:30 | 152 | 152
2017-08-05 15:00 | 159 | 159
2017-08-05 15:30 | 171 | 170
2017-08-05 16:00 | 181 | 181
2017-08-05 16:30 | 196 | 196
2017-08-05 17:00 | 212 | 212
2017-08-05 17:30 | 223 | 223
2017-08-05 18:00 | 238 | 238
2017-08-05 18:30 | 246 | 246
2017-08-05 19:00 | 249 | 249
2017-08-05 19:30 | 248 | 248
2017-08-05 20:00 | 247 | 247
2017-08-05 20:30 | 249 | 249
2017-08-05 21:00 | 242 | 242
2017-08-05 21:30 | 235 | 235
2017-08-05 22:00 | 230 | 230
2017-08-05 22:30 | 227 | 227
2017-08-05 23:00 | 228 | 228
2017-08-05 23:30 | 218 | 218
2017-08-06 | 203 | 203
2017-08-06 00:30 | 188 | 188
2017-08-06 01:00 | 178 | 177
2017-08-06 01:30 | 170 | 169
2017-08-06 02:00 | 162 | 162
2017-08-06 02:30 | 158 | 158
2017-08-06 03:00 | 154 | 154
2017-08-06 03:30 | 153 | 153
2017-08-06 04:00 | 151 | 151
2017-08-06 04:30 | 152 | 152
2017-08-06 05:00 | 154 | 154
2017-08-06 05:30 | 159 | 159
2017-08-06 06:00 | 164 | 164
2017-08-06 06:30 | 173 | 173
2017-08-06 07:00 | 182 | 182
2017-08-06 07:30 | 195 | 194
2017-08-06 08:00 | 205 | 205
2017-08-06 08:30 | 209 | 208
2017-08-06 09:00 | 207 | 205
2017-08-06 09:30 | 191 | 190
2017-08-06 10:00 | 186 | 185
2017-08-06 10:30 | 176 | 175
2017-08-06 11:00 | 161 | 160
2017-08-06 11:30 | 155 | 154
2017-08-06 12:00 | 152 | 152
2017-08-06 12:30 | 148 | 147
2017-08-06 13:00 | 145 | 145
2017-08-06 13:30 | 147 | 146
2017-08-06 14:00 | 151 | 151
2017-08-06 14:30 | 158 | 157
2017-08-06 15:00 | 171 | 171
2017-08-06 15:30 | 184 | 184
2017-08-06 16:00 | 196 | 195
2017-08-06 16:30 | 209 | 209
2017-08-06 17:00 | 228 | 228
2017-08-06 17:30 | 245 | 245
2017-08-06 18:00 | 256 | 254
2017-08-06 18:30 | 258 | 256
2017-08-06 19:00 | 257 | 255
2017-08-06 19:30 | 253 | 250
2017-08-06 20:00 | 249 | 246
2017-08-06 20:30 | 247 | 245
2017-08-06 21:00 | 236 | 234
2017-08-06 21:30 | 226 | 225
2017-08-06 22:00 | 217 | 217
2017-08-06 22:30 | 213 | 212
2017-08-06 23:00 | 212 | 212
2017-08-06 23:30 | 203 | 202
2017-08-07 | 186 | 186
2017-08-07 00:30 | 172 | 172
2017-08-07 01:00 | 162 | 162
2017-08-07 01:30 | 156 | 156
2017-08-07 02:00 | 151 | 150
2017-08-07 02:30 | 147 | 147
2017-08-07 03:00 | 145 | 145
2017-08-07 03:30 | 145 | 145
2017-08-07 04:00 | 147 | 147
2017-08-07 04:30 | 151 | 151
2017-08-07 05:00 | 159 | 159
2017-08-07 05:30 | 175 | 174
2017-08-07 06:00 | 194 | 192
2017-08-07 06:30 | 217 | 216
2017-08-07 07:00 | 239 | 238
2017-08-07 07:30 | 257 | 255
2017-08-07 08:00 | 261 | 261
2017-08-07 08:30 | 248 | 248
2017-08-07 09:00 | 227 | 227
2017-08-07 09:30 | 217 | 217
2017-08-07 10:00 | 214 | 214
2017-08-07 10:30 | 211 | 211
2017-08-07 11:00 | 205 | 205
2017-08-07 11:30 | 197 | 197
2017-08-07 12:00 | 193 | 193
2017-08-07 12:30 | 191 | 191
2017-08-07 13:00 | 191 | 191
2017-08-07 13:30 | 193 | 193
2017-08-07 14:00 | 197 | 197
2017-08-07 14:30 | 202 | 202
2017-08-07 15:00 | 208 | 208
2017-08-07 15:30 | 217 | 217
2017-08-07 16:00 | 230 | 230
2017-08-07 16:30 | 243 | 243
2017-08-07 17:00 | 258 | 258
2017-08-07 17:30 | 269 | 269
2017-08-07 18:00 | 283 | 283
2017-08-07 18:30 | 288 | 287
2017-08-07 19:00 | 287 | 287
2017-08-07 19:30 | 281 | 280
2017-08-07 20:00 | 273 | 273
2017-08-07 20:30 | 273 | 273
2017-08-07 21:00 | 261 | 261
2017-08-07 21:30 | 250 | 250
2017-08-07 22:00 | 239 | 239
2017-08-07 22:30 | 232 | 232
2017-08-07 23:00 | 230 | 229
2017-08-07 23:30 | 216 | 216
2017-08-08 | 199 | 199
2017-08-08 00:30 | 183 | 183
2017-08-08 01:00 | 172 | 172
2017-08-08 01:30 | 165 | 165
2017-08-08 02:00 | 161 | 161
2017-08-08 02:30 | 157 | 157
2017-08-08 03:00 | 156 | 156
2017-08-08 03:30 | 156 | 156
2017-08-08 04:00 | 157 | 157
2017-08-08 04:30 | 162 | 162
2017-08-08 05:00 | 171 | 171
2017-08-08 05:30 | 189 | 188
2017-08-08 06:00 | 209 | 208
2017-08-08 06:30 | 239 | 239
2017-08-08 07:00 | 264 | 263
2017-08-08 07:30 | 279 | 279
2017-08-08 08:00 | 270 | 270
2017-08-08 08:30 | 252 | 252
2017-08-08 09:00 | 234 | 234
2017-08-08 09:30 | 219 | 218
2017-08-08 10:00 | 207 | 206
2017-08-08 10:30 | 197 | 196
2017-08-08 11:00 | 189 | 189
2017-08-08 11:30 | 181 | 181
2017-08-08 12:00 | 179 | 179
2017-08-08 12:30 | 177 | 177
2017-08-08 13:00 | 179 | 179
2017-08-08 13:30 | 181 | 181
2017-08-08 14:00 | 188 | 187
2017-08-08 14:30 | 193 | 193
2017-08-08 15:00 | 200 | 200
2017-08-08 15:30 | 211 | 210
2017-08-08 16:00 | 225 | 225
2017-08-08 16:30 | 241 | 241
2017-08-08 17:00 | 258 | 257
2017-08-08 17:30 | 272 | 272
2017-08-08 18:00 | 288 | 288
2017-08-08 18:30 | 294 | 294
2017-08-08 19:00 | 297 | 297
2017-08-08 19:30 | 292 | 292
2017-08-08 20:00 | 290 | 290
2017-08-08 20:30 | 290 | 290
2017-08-08 21:00 | 279 | 279
2017-08-08 21:30 | 268 | 268
2017-08-08 22:00 | 257 | 257
2017-08-08 22:30 | 246 | 246
2017-08-08 23:00 | 241 | 241
2017-08-08 23:30 | 226 | 226
2017-08-09 | 208 | 208
2017-08-09 00:30 | 192 | 192
2017-08-09 01:00 | 181 | 180
2017-08-09 01:30 | 172 | 172
2017-08-09 02:00 | 167 | 167
2017-08-09 02:30 | 164 | 164
2017-08-09 03:00 | 162 | 162
2017-08-09 03:30 | 163 | 163
2017-08-09 04:00 | 163 | 163
2017-08-09 04:30 | 170 | 170
2017-08-09 05:00 | 180 | 180
2017-08-09 05:30 | 199 | 198
2017-08-09 06:00 | 223 | 221
2017-08-09 06:30 | 255 | 255
2017-08-09 07:00 | 282 | 282
2017-08-09 07:30 | 295 | 295
2017-08-09 08:00 | 285 | 285
2017-08-09 08:30 | 263 | 263
2017-08-09 09:00 | 241 | 241
2017-08-09 09:30 | 223 | 223
2017-08-09 10:00 | 209 | 208
2017-08-09 10:30 | 198 | 197
2017-08-09 11:00 | 186 | 186
2017-08-09 11:30 | 180 | 180
2017-08-09 12:00 | 178 | 177
2017-08-09 12:30 | 176 | 176
2017-08-09 13:00 | 178 | 177
2017-08-09 13:30 | 179 | 179
2017-08-09 14:00 | 183 | 182
2017-08-09 14:30 | 189 | 189
2017-08-09 15:00 | 196 | 196
2017-08-09 15:30 | 208 | 207
2017-08-09 16:00 | 217 | 216
2017-08-09 16:30 | 233 | 232
2017-08-09 17:00 | 250 | 250
2017-08-09 17:30 | 263 | 263
2017-08-09 18:00 | 279 | 279
2017-08-09 18:30 | 288 | 288
2017-08-09 19:00 | 292 | 292
2017-08-09 19:30 | 288 | 288
2017-08-09 20:00 | 288 | 288
2017-08-09 20:30 | 289 | 289
2017-08-09 21:00 | 277 | 277
2017-08-09 21:30 | 266 | 266
2017-08-09 22:00 | 253 | 253
2017-08-09 22:30 | 242 | 242
2017-08-09 23:00 | 238 | 237
2017-08-09 23:30 | 222 | 222
2017-08-10 | 205 | 205
2017-08-10 00:30 | 187 | 187
2017-08-10 01:00 | 176 | 176
2017-08-10 01:30 | 169 | 169
2017-08-10 02:00 | 162 | 162
2017-08-10 02:30 | 159 | 159
2017-08-10 03:00 | 157 | 157
2017-08-10 03:30 | 158 | 158
2017-08-10 04:00 | 159 | 159
2017-08-10 04:30 | 165 | 165
2017-08-10 05:00 | 176 | 176
2017-08-10 05:30 | 196 | 195
2017-08-10 06:00 | 218 | 216
2017-08-10 06:30 | 251 | 250
2017-08-10 07:00 | 281 | 281
2017-08-10 07:30 | 295 | 295
2017-08-10 08:00 | 285 | 285
2017-08-10 08:30 | 263 | 262
2017-08-10 09:00 | 241 | 241
2017-08-10 09:30 | 225 | 224
2017-08-10 10:00 | 213 | 213
2017-08-10 10:30 | 200 | 200
2017-08-10 11:00 | 192 | 192
2017-08-10 11:30 | 185 | 185
2017-08-10 12:00 | 179 | 178
2017-08-10 12:30 | 179 | 179
2017-08-10 13:00 | 180 | 180
2017-08-10 13:30 | 184 | 184
2017-08-10 14:00 | 190 | 190
2017-08-10 14:30 | 196 | 196
2017-08-10 15:00 | 202 | 202
2017-08-10 15:30 | 211 | 210
2017-08-10 16:00 | 223 | 222
2017-08-10 16:30 | 236 | 236
2017-08-10 17:00 | 251 | 250
2017-08-10 17:30 | 262 | 262
2017-08-10 18:00 | 278 | 277
2017-08-10 18:30 | 283 | 283
2017-08-10 19:00 | 285 | 284
2017-08-10 19:30 | 280 | 280
2017-08-10 20:00 | 279 | 279
2017-08-10 20:30 | 278 | 278
2017-08-10 21:00 | 269 | 267
2017-08-10 21:30 | 256 | 255
2017-08-10 22:00 | 245 | 245
2017-08-10 22:30 | 237 | 237
2017-08-10 23:00 | 233 | 232
2017-08-10 23:30 | 219 | 218
2017-08-11 | 201 | 200
2017-08-11 00:30 | 183 | 183
2017-08-11 01:00 | 172 | 172
2017-08-11 01:30 | 165 | 165
2017-08-11 02:00 | 159 | 159
2017-08-11 02:30 | 156 | 156
2017-08-11 03:00 | 154 | 153
2017-08-11 03:30 | 154 | 153
2017-08-11 04:00 | 156 | 155
2017-08-11 04:30 | 161 | 161
2017-08-11 05:00 | 171 | 170
2017-08-11 05:30 | 187 | 185
2017-08-11 06:00 | 208 | 205
2017-08-11 06:30 | 235 | 234
2017-08-11 07:00 | 259 | 258
2017-08-11 07:30 | 271 | 271
2017-08-11 08:00 | 262 | 262
2017-08-11 08:30 | 245 | 245
2017-08-11 09:00 | 227 | 227
2017-08-11 09:30 | 212 | 212
2017-08-11 10:00 | 200 | 200
2017-08-11 10:30 | 192 | 192
2017-08-11 11:00 | 187 | 187
2017-08-11 11:30 | 183 | 183
2017-08-11 12:00 | 181 | 181
2017-08-11 12:30 | 180 | 180
2017-08-11 13:00 | 182 | 182
2017-08-11 13:30 | 184 | 184
2017-08-11 14:00 | 191 | 191
2017-08-11 14:30 | 197 | 197
2017-08-11 15:00 | 203 | 203
2017-08-11 15:30 | 212 | 212
2017-08-11 16:00 | 224 | 224
2017-08-11 16:30 | 235 | 235
2017-08-11 17:00 | 245 | 245
2017-08-11 17:30 | 252 | 252
2017-08-11 18:00 | 261 | 261
2017-08-11 18:30 | 264 | 264
2017-08-11 19:00 | 264 | 264
2017-08-11 19:30 | 258 | 258
2017-08-11 20:00 | 256 | 256
2017-08-11 20:30 | 256 | 256
2017-08-11 21:00 | 251 | 251
2017-08-11 21:30 | 242 | 242
2017-08-11 22:00 | 235 | 235
2017-08-11 22:30 | 230 | 229
2017-08-11 23:00 | 229 | 229
2017-08-11 23:30 | 218 | 217
2017-08-12 | 200 | 200
2017-08-12 00:30 | 184 | 184
2017-08-12 01:00 | 173 | 173
2017-08-12 01:30 | 160 | 160
2017-08-12 02:00 | 154 | 154
2017-08-12 02:30 | 150 | 150
2017-08-12 03:00 | 149 | 149
2017-08-12 03:30 | 148 | 148
2017-08-12 04:00 | 149 | 149
2017-08-12 04:30 | 150 | 150
2017-08-12 05:00 | 151 | 151
2017-08-12 05:30 | 157 | 157
2017-08-12 06:00 | 165 | 165
2017-08-12 06:30 | 173 | 173
2017-08-12 07:00 | 183 | 183
2017-08-12 07:30 | 191 | 190
2017-08-12 08:00 | 191 | 191
2017-08-12 08:30 | 189 | 189
2017-08-12 09:00 | 184 | 184
2017-08-12 09:30 | 176 | 175
2017-08-12 10:00 | 169 | 168
2017-08-12 10:30 | 182 | 181
2017-08-12 11:00 | 190 | 189
2017-08-12 11:30 | 173 | 173
2017-08-12 12:00 | 157 | 157
2017-08-12 12:30 | 165 | 164
2017-08-12 13:00 | 169 | 169
2017-08-12 13:30 | 169 | 168
2017-08-12 14:00 | 167 | 166
2017-08-12 14:30 | 164 | 163
2017-08-12 15:00 | 165 | 164
2017-08-12 15:30 | 175 | 174
2017-08-12 16:00 | 186 | 185
2017-08-12 16:30 | 198 | 197
2017-08-12 17:00 | 211 | 210
2017-08-12 17:30 | 217 | 216
2017-08-12 18:00 | 228 | 227
2017-08-12 18:30 | 233 | 233
2017-08-12 19:00 | 233 | 233
2017-08-12 19:30 | 227 | 227
2017-08-12 20:00 | 226 | 226
2017-08-12 20:30 | 227 | 227
2017-08-12 21:00 | 219 | 218
2017-08-12 21:30 | 212 | 212
2017-08-12 22:00 | 206 | 206
2017-08-12 22:30 | 206 | 206
2017-08-12 23:00 | 208 | 208
2017-08-12 23:30 | 198 | 198
2017-08-13 | 183 | 183
2017-08-13 00:30 | 168 | 168
2017-08-13 01:00 | 158 | 158
2017-08-13 01:30 | 150 | 150
2017-08-13 02:00 | 144 | 144
2017-08-13 02:30 | 141 | 141
2017-08-13 03:00 | 138 | 138
2017-08-13 03:30 | 137 | 137
2017-08-13 04:00 | 137 | 137
2017-08-13 04:30 | 136 | 136
2017-08-13 05:00 | 138 | 138
2017-08-13 05:30 | 142 | 142
2017-08-13 06:00 | 146 | 146
2017-08-13 06:30 | 152 | 152
2017-08-13 07:00 | 158 | 158
2017-08-13 07:30 | 166 | 166
2017-08-13 08:00 | 169 | 169
2017-08-13 08:30 | 171 | 171
2017-08-13 09:00 | 167 | 167
2017-08-13 09:30 | 161 | 161
2017-08-13 10:00 | 155 | 155
2017-08-13 10:30 | 149 | 149
2017-08-13 11:00 | 143 | 143
2017-08-13 11:30 | 141 | 141
2017-08-13 12:00 | 139 | 139
2017-08-13 12:30 | 135 | 135
2017-08-13 13:00 | 136 | 135
2017-08-13 13:30 | 137 | 137
2017-08-13 14:00 | 142 | 141
2017-08-13 14:30 | 148 | 147
2017-08-13 15:00 | 156 | 155
2017-08-13 15:30 | 165 | 164
2017-08-13 16:00 | 177 | 176
2017-08-13 16:30 | 190 | 189
2017-08-13 17:00 | 205 | 203
2017-08-13 17:30 | 217 | 216
2017-08-13 18:00 | 232 | 231
2017-08-13 18:30 | 240 | 239
2017-08-13 19:00 | 239 | 239
2017-08-13 19:30 | 232 | 232
2017-08-13 20:00 | 230 | 230
2017-08-13 20:30 | 233 | 232
2017-08-13 21:00 | 223 | 222
2017-08-13 21:30 | 214 | 214
2017-08-13 22:00 | 208 | 208
2017-08-13 22:30 | 205 | 205
2017-08-13 23:00 | 206 | 205
2017-08-13 23:30 | 193 | 193
2017-08-14 | 178 | 178
2017-08-14 00:30 | 163 | 163
2017-08-14 01:00 | 155 | 155
2017-08-14 01:30 | 148 | 148
2017-08-14 02:00 | 143 | 143
2017-08-14 02:30 | 139 | 139
2017-08-14 03:00 | 138 | 138
2017-08-14 03:30 | 138 | 138
2017-08-14 04:00 | 139 | 139
2017-08-14 04:30 | 143 | 143
2017-08-14 05:00 | 150 | 150
2017-08-14 05:30 | 163 | 162
2017-08-14 06:00 | 178 | 178
2017-08-14 06:30 | 199 | 198
2017-08-14 07:00 | 218 | 218
2017-08-14 07:30 | 229 | 229
2017-08-14 08:00 | 225 | 225
2017-08-14 08:30 | 217 | 217
2017-08-14 09:00 | 204 | 204
2017-08-14 09:30 | 201 | 201
2017-08-14 10:00 | 193 | 193
2017-08-14 10:30 | 181 | 181
2017-08-14 11:00 | 180 | 180
2017-08-14 11:30 | 180 | 180
2017-08-14 12:00 | 175 | 175
2017-08-14 12:30 | 174 | 174
2017-08-14 13:00 | 177 | 177
2017-08-14 13:30 | 188 | 188
2017-08-14 14:00 | 192 | 192
2017-08-14 14:30 | 200 | 200
2017-08-14 15:00 | 199 | 199
2017-08-14 15:30 | 201 | 201
2017-08-14 16:00 | 213 | 213
2017-08-14 16:30 | 227 | 227
2017-08-14 17:00 | 242 | 242
2017-08-14 17:30 | 254 | 254
2017-08-14 18:00 | 267 | 266
2017-08-14 18:30 | 271 | 271
2017-08-14 19:00 | 271 | 271
2017-08-14 19:30 | 262 | 261
2017-08-14 20:00 | 258 | 258
2017-08-14 20:30 | 257 | 257
2017-08-14 21:00 | 245 | 245
2017-08-14 21:30 | 234 | 234
2017-08-14 22:00 | 226 | 225
2017-08-14 22:30 | 218 | 218
2017-08-14 23:00 | 215 | 215
2017-08-14 23:30 | 203 | 203
2017-08-15 | 187 | 187
2017-08-15 00:30 | 170 | 170
2017-08-15 01:00 | 161 | 160
2017-08-15 01:30 | 154 | 154
2017-08-15 02:00 | 149 | 149
2017-08-15 02:30 | 147 | 146
2017-08-15 03:00 | 147 | 147
2017-08-15 03:30 | 148 | 147
2017-08-15 04:00 | 148 | 148
2017-08-15 04:30 | 152 | 152
2017-08-15 05:00 | 161 | 161
2017-08-15 05:30 | 175 | 175
2017-08-15 06:00 | 194 | 194
2017-08-15 06:30 | 220 | 220
2017-08-15 07:00 | 243 | 242
2017-08-15 07:30 | 255 | 255
2017-08-15 08:00 | 249 | 249
2017-08-15 08:30 | 233 | 233
2017-08-15 09:00 | 215 | 215
2017-08-15 09:30 | 204 | 204
2017-08-15 10:00 | 195 | 195
2017-08-15 10:30 | 188 | 188
2017-08-15 11:00 | 184 | 184
2017-08-15 11:30 | 181 | 181
2017-08-15 12:00 | 180 | 180
2017-08-15 12:30 | 180 | 180
2017-08-15 13:00 | 183 | 183
2017-08-15 13:30 | 187 | 187
2017-08-15 14:00 | 194 | 194
2017-08-15 14:30 | 201 | 199
2017-08-15 15:00 | 206 | 205
2017-08-15 15:30 | 214 | 212
2017-08-15 16:00 | 225 | 223
2017-08-15 16:30 | 237 | 236
2017-08-15 17:00 | 248 | 247
2017-08-15 17:30 | 258 | 256
2017-08-15 18:00 | 270 | 268
2017-08-15 18:30 | 276 | 275
2017-08-15 19:00 | 275 | 275
2017-08-15 19:30 | 267 | 267
2017-08-15 20:00 | 264 | 264
2017-08-15 20:30 | 262 | 262
2017-08-15 21:00 | 251 | 251
2017-08-15 21:30 | 241 | 241
2017-08-15 22:00 | 231 | 231
2017-08-15 22:30 | 225 | 225
2017-08-15 23:00 | 222 | 222
2017-08-15 23:30 | 207 | 206
2017-08-16 | 191 | 191
2017-08-16 00:30 | 174 | 174
2017-08-16 01:00 | 163 | 163
2017-08-16 01:30 | 157 | 157
2017-08-16 02:00 | 152 | 151
2017-08-16 02:30 | 150 | 149
2017-08-16 03:00 | 149 | 148
2017-08-16 03:30 | 150 | 149
2017-08-16 04:00 | 151 | 150
2017-08-16 04:30 | 154 | 153
2017-08-16 05:00 | 159 | 159
2017-08-16 05:30 | 168 | 168
2017-08-16 06:00 | 181 | 181
2017-08-16 06:30 | 196 | 196
2017-08-16 07:00 | 212 | 211
2017-08-16 07:30 | 223 | 221
2017-08-16 08:00 | 220 | 219
2017-08-16 08:30 | 212 | 211
2017-08-16 09:00 | 203 | 202
2017-08-16 09:30 | 194 | 193
2017-08-16 10:00 | 187 | 186
2017-08-16 10:30 | 182 | 181
2017-08-16 11:00 | 178 | 176
2017-08-16 11:30 | 177 | 175
2017-08-16 12:00 | 176 | 174
2017-08-16 12:30 | 177 | 175
2017-08-16 13:00 | 178 | 178
2017-08-16 13:30 | 182 | 182
2017-08-16 14:00 | 189 | 188
2017-08-16 14:30 | 195 | 194
2017-08-16 15:00 | 203 | 202
2017-08-16 15:30 | 212 | 211
2017-08-16 16:00 | 222 | 222
2017-08-16 16:30 | 233 | 233
2017-08-16 17:00 | 246 | 246
2017-08-16 17:30 | 254 | 254
2017-08-16 18:00 | 265 | 265
2017-08-16 18:30 | 269 | 269
2017-08-16 19:00 | 267 | 267
2017-08-16 19:30 | 260 | 260
2017-08-16 20:00 | 256 | 256
2017-08-16 20:30 | 254 | 254
2017-08-16 21:00 | 241 | 241
2017-08-16 21:30 | 230 | 230
2017-08-16 22:00 | 222 | 222
2017-08-16 22:30 | 215 | 215
2017-08-16 23:00 | 215 | 214
2017-08-16 23:30 | 204 | 204
2017-08-17 | 189 | 188
2017-08-17 00:30 | 173 | 172
2017-08-17 01:00 | 163 | 162
2017-08-17 01:30 | 157 | 155
2017-08-17 02:00 | 153 | 151
2017-08-17 02:30 | 151 | 149
2017-08-17 03:00 | 149 | 147
2017-08-17 03:30 | 148 | 147
2017-08-17 04:00 | 148 | 148
2017-08-17 04:30 | 152 | 152
2017-08-17 05:00 | 159 | 159
2017-08-17 05:30 | 173 | 173
2017-08-17 06:00 | 188 | 188
2017-08-17 06:30 | 209 | 209
2017-08-17 07:00 | 228 | 228
2017-08-17 07:30 | 239 | 239
2017-08-17 08:00 | 236 | 236
2017-08-17 08:30 | 227 | 227
2017-08-17 09:00 | 218 | 218
2017-08-17 09:30 | 211 | 210
2017-08-17 10:00 | 205 | 205
2017-08-17 10:30 | 202 | 202
2017-08-17 11:00 | 200 | 200
2017-08-17 11:30 | 199 | 199
2017-08-17 12:00 | 199 | 199
2017-08-17 12:30 | 201 | 201
2017-08-17 13:00 | 205 | 205
2017-08-17 13:30 | 210 | 210
2017-08-17 14:00 | 217 | 217
2017-08-17 14:30 | 226 | 226
2017-08-17 15:00 | 233 | 233
2017-08-17 15:30 | 240 | 240
2017-08-17 16:00 | 251 | 251
2017-08-17 16:30 | 261 | 261
2017-08-17 17:00 | 270 | 270
2017-08-17 17:30 | 274 | 273
2017-08-17 18:00 | 283 | 282
2017-08-17 18:30 | 287 | 287
2017-08-17 19:00 | 287 | 287
2017-08-17 19:30 | 279 | 279
2017-08-17 20:00 | 274 | 274
2017-08-17 20:30 | 270 | 270
2017-08-17 21:00 | 257 | 257
2017-08-17 21:30 | 244 | 244
2017-08-17 22:00 | 233 | 232
2017-08-17 22:30 | 227 | 227
2017-08-17 23:00 | 222 | 222
2017-08-17 23:30 | 207 | 206
2017-08-18 | 189 | 188
2017-08-18 00:30 | 172 | 172
2017-08-18 01:00 | 163 | 162
2017-08-18 01:30 | 157 | 156
2017-08-18 02:00 | 153 | 152
2017-08-18 02:30 | 150 | 149
2017-08-18 03:00 | 148 | 148
2017-08-18 03:30 | 148 | 147
2017-08-18 04:00 | 149 | 148
2017-08-18 04:30 | 153 | 152
2017-08-18 05:00 | 159 | 159
2017-08-18 05:30 | 172 | 172
2017-08-18 06:00 | 187 | 187
2017-08-18 06:30 | 208 | 207
2017-08-18 07:00 | 227 | 227
2017-08-18 07:30 | 238 | 238
2017-08-18 08:00 | 233 | 233
2017-08-18 08:30 | 222 | 222
2017-08-18 09:00 | 210 | 210
2017-08-18 09:30 | 200 | 200
2017-08-18 10:00 | 191 | 191
2017-08-18 10:30 | 184 | 182
2017-08-18 11:00 | 181 | 179
2017-08-18 11:30 | 177 | 175
2017-08-18 12:00 | 176 | 174
2017-08-18 12:30 | 175 | 173
2017-08-18 13:00 | 176 | 174
2017-08-18 13:30 | 180 | 178
2017-08-18 14:00 | 184 | 183
2017-08-18 14:30 | 189 | 188
2017-08-18 15:00 | 194 | 193
2017-08-18 15:30 | 203 | 203
2017-08-18 16:00 | 218 | 217
2017-08-18 16:30 | 230 | 230
2017-08-18 17:00 | 243 | 243
2017-08-18 17:30 | 251 | 250
2017-08-18 18:00 | 255 | 255
2017-08-18 18:30 | 259 | 259
2017-08-18 19:00 | 258 | 258
2017-08-18 19:30 | 252 | 251
2017-08-18 20:00 | 247 | 246
2017-08-18 20:30 | 246 | 245
2017-08-18 21:00 | 236 | 235
2017-08-18 21:30 | 227 | 226
2017-08-18 22:00 | 220 | 219
2017-08-18 22:30 | 217 | 216
2017-08-18 23:00 | 215 | 215
2017-08-18 23:30 | 205 | 205
2017-08-19 | 189 | 189
2017-08-19 00:30 | 173 | 173
2017-08-19 01:00 | 162 | 162
2017-08-19 01:30 | 154 | 154
2017-08-19 02:00 | 149 | 149
2017-08-19 02:30 | 146 | 145
2017-08-19 03:00 | 144 | 143
2017-08-19 03:30 | 142 | 142
2017-08-19 04:00 | 145 | 145
2017-08-19 04:30 | 147 | 147
2017-08-19 05:00 | 150 | 150
2017-08-19 05:30 | 156 | 156
2017-08-19 06:00 | 163 | 163
2017-08-19 06:30 | 172 | 172
2017-08-19 07:00 | 180 | 180
2017-08-19 07:30 | 187 | 187
2017-08-19 08:00 | 188 | 187
2017-08-19 08:30 | 187 | 186
2017-08-19 09:00 | 183 | 183
2017-08-19 09:30 | 176 | 176
2017-08-19 10:00 | 168 | 167
2017-08-19 10:30 | 158 | 158
2017-08-19 11:00 | 149 | 148
2017-08-19 11:30 | 142 | 141
2017-08-19 12:00 | 136 | 136
2017-08-19 12:30 | 132 | 132
2017-08-19 13:00 | 131 | 131
2017-08-19 13:30 | 133 | 133
2017-08-19 14:00 | 136 | 136
2017-08-19 14:30 | 142 | 142
2017-08-19 15:00 | 150 | 149
2017-08-19 15:30 | 158 | 158
2017-08-19 16:00 | 170 | 169
2017-08-19 16:30 | 185 | 184
2017-08-19 17:00 | 201 | 201
2017-08-19 17:30 | 213 | 213
2017-08-19 18:00 | 230 | 230
2017-08-19 18:30 | 243 | 243
2017-08-19 19:00 | 245 | 245
2017-08-19 19:30 | 242 | 242
2017-08-19 20:00 | 242 | 241
2017-08-19 20:30 | 241 | 241
2017-08-19 21:00 | 231 | 231
2017-08-19 21:30 | 224 | 223
2017-08-19 22:00 | 218 | 218
2017-08-19 22:30 | 218 | 218
2017-08-19 23:00 | 220 | 219
2017-08-19 23:30 | 210 | 210
2017-08-20 | 195 | 195
2017-08-20 00:30 | 179 | 179
2017-08-20 01:00 | 168 | 168
2017-08-20 01:30 | 160 | 159
2017-08-20 02:00 | 153 | 153
2017-08-20 02:30 | 149 | 149
2017-08-20 03:00 | 150 | 150
2017-08-20 03:30 | 151 | 150
2017-08-20 04:00 | 149 | 149
2017-08-20 04:30 | 150 | 150
2017-08-20 05:00 | 151 | 150
2017-08-20 05:30 | 152 | 151
2017-08-20 06:00 | 157 | 157
2017-08-20 06:30 | 164 | 163
2017-08-20 07:00 | 172 | 171
2017-08-20 07:30 | 178 | 178
2017-08-20 08:00 | 180 | 180
2017-08-20 08:30 | 179 | 179
2017-08-20 09:00 | 173 | 173
2017-08-20 09:30 | 166 | 166
2017-08-20 10:00 | 157 | 157
2017-08-20 10:30 | 149 | 149
2017-08-20 11:00 | 140 | 139
2017-08-20 11:30 | 133 | 132
2017-08-20 12:00 | 131 | 130
2017-08-20 12:30 | 128 | 128
2017-08-20 13:00 | 128 | 128
2017-08-20 13:30 | 131 | 131
2017-08-20 14:00 | 134 | 134
2017-08-20 14:30 | 140 | 140
2017-08-20 15:00 | 148 | 148
2017-08-20 15:30 | 158 | 158
2017-08-20 16:00 | 172 | 172
2017-08-20 16:30 | 188 | 188
2017-08-20 17:00 | 207 | 207
2017-08-20 17:30 | 223 | 223
2017-08-20 18:00 | 243 | 243
2017-08-20 18:30 | 255 | 255
2017-08-20 19:00 | 256 | 256
2017-08-20 19:30 | 252 | 252
2017-08-20 20:00 | 251 | 251
2017-08-20 20:30 | 250 | 250
2017-08-20 21:00 | 242 | 242
2017-08-20 21:30 | 231 | 231
2017-08-20 22:00 | 224 | 223
2017-08-20 22:30 | 219 | 219
2017-08-20 23:00 | 217 | 217
2017-08-20 23:30 | 205 | 205
2017-08-21 | 189 | 189
2017-08-21 00:30 | 175 | 175
2017-08-21 01:00 | 165 | 164
2017-08-21 01:30 | 157 | 157
2017-08-21 02:00 | 153 | 152
2017-08-21 02:30 | 150 | 149
2017-08-21 03:00 | 147 | 147
2017-08-21 03:30 | 147 | 147
2017-08-21 04:00 | 149 | 149
2017-08-21 04:30 | 154 | 154
2017-08-21 05:00 | 164 | 164
2017-08-21 05:30 | 184 | 183
2017-08-21 06:00 | 206 | 205
2017-08-21 06:30 | 237 | 237
2017-08-21 07:00 | 262 | 262
2017-08-21 07:30 | 271 | 270
2017-08-21 08:00 | 268 | 268
2017-08-21 08:30 | 250 | 250
2017-08-21 09:00 | 236 | 236
2017-08-21 09:30 | 227 | 227
2017-08-21 10:00 | 217 | 217
2017-08-21 10:30 | 201 | 201
2017-08-21 11:00 | 189 | 189
2017-08-21 11:30 | 185 | 185
2017-08-21 12:00 | 187 | 187
2017-08-21 12:30 | 187 | 187
2017-08-21 13:00 | 190 | 190
2017-08-21 13:30 | 198 | 198
2017-08-21 14:00 | 211 | 210
2017-08-21 14:30 | 206 | 204
2017-08-21 15:00 | 216 | 214
2017-08-21 15:30 | 230 | 229
2017-08-21 16:00 | 243 | 242
2017-08-21 16:30 | 254 | 254
2017-08-21 17:00 | 269 | 268
2017-08-21 17:30 | 283 | 282
2017-08-21 18:00 | 294 | 293
2017-08-21 18:30 | 294 | 294
2017-08-21 19:00 | 294 | 294
2017-08-21 19:30 | 288 | 287
2017-08-21 20:00 | 283 | 283
2017-08-21 20:30 | 282 | 282
2017-08-21 21:00 | 268 | 268
2017-08-21 21:30 | 255 | 255
2017-08-21 22:00 | 243 | 243
2017-08-21 22:30 | 235 | 235
2017-08-21 23:00 | 231 | 230
2017-08-21 23:30 | 218 | 217
2017-08-22 | 199 | 199
2017-08-22 00:30 | 184 | 184
2017-08-22 01:00 | 174 | 174
2017-08-22 01:30 | 165 | 165
2017-08-22 02:00 | 158 | 158
2017-08-22 02:30 | 154 | 154
2017-08-22 03:00 | 152 | 151
2017-08-22 03:30 | 152 | 152
2017-08-22 04:00 | 157 | 157
2017-08-22 04:30 | 163 | 163
2017-08-22 05:00 | 171 | 171
2017-08-22 05:30 | 186 | 186
2017-08-22 06:00 | 205 | 205
2017-08-22 06:30 | 230 | 229
2017-08-22 07:00 | 253 | 253
2017-08-22 07:30 | 262 | 262
2017-08-22 08:00 | 255 | 255
2017-08-22 08:30 | 242 | 242
2017-08-22 09:00 | 227 | 227
2017-08-22 09:30 | 217 | 217
2017-08-22 10:00 | 211 | 211
2017-08-22 10:30 | 207 | 207
2017-08-22 11:00 | 204 | 204
2017-08-22 11:30 | 198 | 198
2017-08-22 12:00 | 196 | 196
2017-08-22 12:30 | 194 | 194
2017-08-22 13:00 | 196 | 196
2017-08-22 13:30 | 202 | 202
2017-08-22 14:00 | 209 | 208
2017-08-22 14:30 | 211 | 211
2017-08-22 15:00 | 216 | 216
2017-08-22 15:30 | 225 | 225
2017-08-22 16:00 | 236 | 236
2017-08-22 16:30 | 248 | 248
2017-08-22 17:00 | 261 | 261
2017-08-22 17:30 | 274 | 274
2017-08-22 18:00 | 285 | 285
2017-08-22 18:30 | 290 | 290
2017-08-22 19:00 | 290 | 290
2017-08-22 19:30 | 282 | 281
2017-08-22 20:00 | 279 | 279
2017-08-22 20:30 | 277 | 277
2017-08-22 21:00 | 263 | 263
2017-08-22 21:30 | 251 | 251
2017-08-22 22:00 | 240 | 240
2017-08-22 22:30 | 234 | 234
2017-08-22 23:00 | 230 | 230
2017-08-22 23:30 | 215 | 215
2017-08-23 | 198 | 198
2017-08-23 00:30 | 183 | 183
2017-08-23 01:00 | 173 | 172
2017-08-23 01:30 | 165 | 164
2017-08-23 02:00 | 157 | 156
2017-08-23 02:30 | 153 | 153
2017-08-23 03:00 | 151 | 150
2017-08-23 03:30 | 148 | 148
2017-08-23 04:00 | 149 | 149
2017-08-23 04:30 | 153 | 153
2017-08-23 05:00 | 162 | 161
2017-08-23 05:30 | 177 | 177
2017-08-23 06:00 | 195 | 194
2017-08-23 06:30 | 214 | 214
2017-08-23 07:00 | 232 | 232
2017-08-23 07:30 | 248 | 248
2017-08-23 08:00 | 243 | 243
2017-08-23 08:30 | 208 | 208
2017-08-23 09:00 | 162 | 162
2017-08-23 09:30 | 156 | 156
2017-08-23 10:00 | 151 | 151
2017-08-23 10:30 | 150 | 150
2017-08-23 11:00 | 143 | 143
2017-08-23 11:30 | 137 | 137
2017-08-23 12:00 | 167 | 167
2017-08-23 12:30 | 189 | 189
2017-08-23 13:00 | 190 | 190
2017-08-23 13:30 | 195 | 195
2017-08-23 14:00 | 201 | 201
2017-08-23 14:30 | 209 | 209
2017-08-23 15:00 | 215 | 215
2017-08-23 15:30 | 223 | 223
2017-08-23 16:00 | 236 | 235
2017-08-23 16:30 | 248 | 247
2017-08-23 17:00 | 261 | 261
2017-08-23 17:30 | 273 | 273
2017-08-23 18:00 | 283 | 283
2017-08-23 18:30 | 287 | 287
2017-08-23 19:00 | 286 | 286
2017-08-23 19:30 | 278 | 278
2017-08-23 20:00 | 275 | 275
2017-08-23 20:30 | 273 | 273
2017-08-23 21:00 | 261 | 260
2017-08-23 21:30 | 248 | 248
2017-08-23 22:00 | 239 | 239
2017-08-23 22:30 | 232 | 232
2017-08-23 23:00 | 228 | 227
2017-08-23 23:30 | 215 | 214
2017-08-24 | 199 | 199
2017-08-24 00:30 | 182 | 182
2017-08-24 01:00 | 171 | 171
2017-08-24 01:30 | 163 | 163
2017-08-24 02:00 | 159 | 159
2017-08-24 02:30 | 156 | 156
2017-08-24 03:00 | 154 | 154
2017-08-24 03:30 | 154 | 154
2017-08-24 04:00 | 155 | 155
2017-08-24 04:30 | 159 | 159
2017-08-24 05:00 | 166 | 166
2017-08-24 05:30 | 183 | 182
2017-08-24 06:00 | 199 | 199
2017-08-24 06:30 | 220 | 220
2017-08-24 07:00 | 242 | 242
2017-08-24 07:30 | 259 | 259
2017-08-24 08:00 | 260 | 260
2017-08-24 08:30 | 258 | 258
2017-08-24 09:00 | 179 | 179
2017-08-24 09:30 | 167 | 167
2017-08-24 10:00 | 175 | 174
2017-08-24 10:30 | 179 | 179
2017-08-24 11:00 | 173 | 173
2017-08-24 11:30 | 162 | 162
2017-08-24 12:00 | 167 | 167
2017-08-24 12:30 | 205 | 205
2017-08-24 13:00 | 196 | 196
2017-08-24 13:30 | 199 | 199
2017-08-24 14:00 | 207 | 207
2017-08-24 14:30 | 213 | 213
2017-08-24 15:00 | 225 | 225
2017-08-24 15:30 | 247 | 247
2017-08-24 16:00 | 251 | 251
2017-08-24 16:30 | 259 | 259
2017-08-24 17:00 | 265 | 265
2017-08-24 17:30 | 269 | 269
2017-08-24 18:00 | 280 | 279
2017-08-24 18:30 | 287 | 287
2017-08-24 19:00 | 288 | 288
2017-08-24 19:30 | 282 | 282
2017-08-24 20:00 | 280 | 280
2017-08-24 20:30 | 279 | 279
2017-08-24 21:00 | 266 | 266
2017-08-24 21:30 | 253 | 252
2017-08-24 22:00 | 242 | 242
2017-08-24 22:30 | 237 | 237
2017-08-24 23:00 | 234 | 233
2017-08-24 23:30 | 220 | 220
2017-08-25 | 202 | 201
2017-08-25 00:30 | 185 | 184
2017-08-25 01:00 | 175 | 174
2017-08-25 01:30 | 166 | 166
2017-08-25 02:00 | 162 | 161
2017-08-25 02:30 | 158 | 158
2017-08-25 03:00 | 156 | 156
2017-08-25 03:30 | 157 | 156
2017-08-25 04:00 | 157 | 156
2017-08-25 04:30 | 161 | 160
2017-08-25 05:00 | 169 | 169
2017-08-25 05:30 | 184 | 184
2017-08-25 06:00 | 201 | 201
2017-08-25 06:30 | 225 | 224
2017-08-25 07:00 | 245 | 244
2017-08-25 07:30 | 255 | 255
2017-08-25 08:00 | 249 | 249
2017-08-25 08:30 | 234 | 234
2017-08-25 09:00 | 220 | 220
2017-08-25 09:30 | 209 | 209
2017-08-25 10:00 | 199 | 199
2017-08-25 10:30 | 193 | 193
2017-08-25 11:00 | 192 | 192
2017-08-25 11:30 | 191 | 191
2017-08-25 12:00 | 191 | 190
2017-08-25 12:30 | 193 | 193
2017-08-25 13:00 | 192 | 192
2017-08-25 13:30 | 197 | 197
2017-08-25 14:00 | 201 | 201
2017-08-25 14:30 | 203 | 203
2017-08-25 15:00 | 199 | 199
2017-08-25 15:30 | 206 | 206
2017-08-25 16:00 | 219 | 219
2017-08-25 16:30 | 236 | 235
2017-08-25 17:00 | 250 | 250
2017-08-25 17:30 | 257 | 257
2017-08-25 18:00 | 267 | 267
2017-08-25 18:30 | 273 | 273
2017-08-25 19:00 | 277 | 277
2017-08-25 19:30 | 272 | 272
2017-08-25 20:00 | 271 | 271
2017-08-25 20:30 | 271 | 271
2017-08-25 21:00 | 261 | 261
2017-08-25 21:30 | 252 | 252
2017-08-25 22:00 | 245 | 245
2017-08-25 22:30 | 240 | 239
2017-08-25 23:00 | 237 | 237
2017-08-25 23:30 | 224 | 224
2017-08-26 | 206 | 206
2017-08-26 00:30 | 190 | 190
2017-08-26 01:00 | 179 | 179
2017-08-26 01:30 | 171 | 170
2017-08-26 02:00 | 165 | 164
2017-08-26 02:30 | 160 | 159
2017-08-26 03:00 | 156 | 156
2017-08-26 03:30 | 155 | 155
2017-08-26 04:00 | 154 | 153
2017-08-26 04:30 | 156 | 156
2017-08-26 05:00 | 159 | 158
2017-08-26 05:30 | 167 | 167
2017-08-26 06:00 | 173 | 173
2017-08-26 06:30 | 183 | 183
2017-08-26 07:00 | 191 | 191
2017-08-26 07:30 | 197 | 197
2017-08-26 08:00 | 198 | 197
2017-08-26 08:30 | 195 | 195
2017-08-26 09:00 | 187 | 187
2017-08-26 09:30 | 179 | 179
2017-08-26 10:00 | 169 | 169
2017-08-26 10:30 | 161 | 161
2017-08-26 11:00 | 154 | 154
2017-08-26 11:30 | 149 | 149
2017-08-26 12:00 | 146 | 146
2017-08-26 12:30 | 145 | 145
2017-08-26 13:00 | 145 | 145
2017-08-26 13:30 | 147 | 147
2017-08-26 14:00 | 147 | 147
2017-08-26 14:30 | 151 | 151
2017-08-26 15:00 | 158 | 158
2017-08-26 15:30 | 166 | 166
2017-08-26 16:00 | 178 | 178
2017-08-26 16:30 | 192 | 192
2017-08-26 17:00 | 208 | 208
2017-08-26 17:30 | 219 | 219
2017-08-26 18:00 | 232 | 232
2017-08-26 18:30 | 242 | 242
2017-08-26 19:00 | 244 | 244
2017-08-26 19:30 | 239 | 239
2017-08-26 20:00 | 238 | 238
2017-08-26 20:30 | 238 | 237
2017-08-26 21:00 | 229 | 229
2017-08-26 21:30 | 222 | 222
2017-08-26 22:00 | 217 | 217
2017-08-26 22:30 | 216 | 216
2017-08-26 23:00 | 217 | 217
2017-08-26 23:30 | 207 | 207
2017-08-27 | 193 | 193
2017-08-27 00:30 | 178 | 178
2017-08-27 01:00 | 167 | 166
2017-08-27 01:30 | 159 | 159
2017-08-27 02:00 | 153 | 153
2017-08-27 02:30 | 149 | 149
2017-08-27 03:00 | 146 | 146
2017-08-27 03:30 | 143 | 143
2017-08-27 04:00 | 143 | 143
2017-08-27 04:30 | 143 | 143
2017-08-27 05:00 | 147 | 147
2017-08-27 05:30 | 151 | 151
2017-08-27 06:00 | 155 | 155
2017-08-27 06:30 | 159 | 159
2017-08-27 07:00 | 164 | 164
2017-08-27 07:30 | 170 | 170
2017-08-27 08:00 | 176 | 176
2017-08-27 08:30 | 173 | 173
2017-08-27 09:00 | 165 | 165
2017-08-27 09:30 | 171 | 171
2017-08-27 10:00 | 164 | 164
2017-08-27 10:30 | 155 | 155
2017-08-27 11:00 | 152 | 152
2017-08-27 11:30 | 156 | 155
2017-08-27 12:00 | 146 | 146
2017-08-27 12:30 | 148 | 148
2017-08-27 13:00 | 149 | 148
2017-08-27 13:30 | 156 | 156
2017-08-27 14:00 | 156 | 156
2017-08-27 14:30 | 157 | 157
2017-08-27 15:00 | 162 | 162
2017-08-27 15:30 | 170 | 170
2017-08-27 16:00 | 179 | 178
2017-08-27 16:30 | 191 | 190
2017-08-27 17:00 | 207 | 207
2017-08-27 17:30 | 220 | 219
2017-08-27 18:00 | 237 | 236
2017-08-27 18:30 | 248 | 248
2017-08-27 19:00 | 250 | 250
2017-08-27 19:30 | 244 | 244
2017-08-27 20:00 | 241 | 240
2017-08-27 20:30 | 242 | 241
2017-08-27 21:00 | 234 | 234
2017-08-27 21:30 | 224 | 224
2017-08-27 22:00 | 217 | 217
2017-08-27 22:30 | 213 | 213
2017-08-27 23:00 | 211 | 211
2017-08-27 23:30 | 201 | 201
2017-08-28 | 186 | 186
2017-08-28 00:30 | 172 | 172
2017-08-28 01:00 | 163 | 163
2017-08-28 01:30 | 157 | 156
2017-08-28 02:00 | 152 | 152
2017-08-28 02:30 | 148 | 148
2017-08-28 03:00 | 147 | 147
2017-08-28 03:30 | 147 | 147
2017-08-28 04:00 | 148 | 148
2017-08-28 04:30 | 155 | 155
2017-08-28 05:00 | 165 | 165
2017-08-28 05:30 | 184 | 183
2017-08-28 06:00 | 204 | 204
2017-08-28 06:30 | 232 | 232
2017-08-28 07:00 | 254 | 253
2017-08-28 07:30 | 263 | 262
2017-08-28 08:00 | 256 | 256
2017-08-28 08:30 | 238 | 238
2017-08-28 09:00 | 221 | 221
2017-08-28 09:30 | 207 | 206
2017-08-28 10:00 | 195 | 195
2017-08-28 10:30 | 186 | 185
2017-08-28 11:00 | 179 | 177
2017-08-28 11:30 | 174 | 172
2017-08-28 12:00 | 172 | 171
2017-08-28 12:30 | 171 | 170
2017-08-28 13:00 | 172 | 171
2017-08-28 13:30 | 175 | 174
2017-08-28 14:00 | 180 | 179
2017-08-28 14:30 | 186 | 185
2017-08-28 15:00 | 192 | 191
2017-08-28 15:30 | 203 | 201
2017-08-28 16:00 | 216 | 214
2017-08-28 16:30 | 233 | 231
2017-08-28 17:00 | 250 | 249
2017-08-28 17:30 | 265 | 264
2017-08-28 18:00 | 281 | 281
2017-08-28 18:30 | 292 | 292
2017-08-28 19:00 | 294 | 294
2017-08-28 19:30 | 285 | 285
2017-08-28 20:00 | 284 | 283
2017-08-28 20:30 | 282 | 282
2017-08-28 21:00 | 270 | 270
2017-08-28 21:30 | 256 | 255
2017-08-28 22:00 | 246 | 244
2017-08-28 22:30 | 238 | 237
2017-08-28 23:00 | 234 | 234
2017-08-28 23:30 | 221 | 220
2017-08-29 | 204 | 204
2017-08-29 00:30 | 188 | 188
2017-08-29 01:00 | 176 | 176
2017-08-29 01:30 | 169 | 169
2017-08-29 02:00 | 164 | 164
2017-08-29 02:30 | 160 | 160
2017-08-29 03:00 | 158 | 158
2017-08-29 03:30 | 157 | 157
2017-08-29 04:00 | 158 | 158
2017-08-29 04:30 | 163 | 163
2017-08-29 05:00 | 172 | 172
2017-08-29 05:30 | 189 | 188
2017-08-29 06:00 | 211 | 211
2017-08-29 06:30 | 240 | 240
2017-08-29 07:00 | 261 | 261
2017-08-29 07:30 | 272 | 272
2017-08-29 08:00 | 260 | 260
2017-08-29 08:30 | 240 | 240
2017-08-29 09:00 | 221 | 221
2017-08-29 09:30 | 208 | 208
2017-08-29 10:00 | 198 | 198
2017-08-29 10:30 | 188 | 188
2017-08-29 11:00 | 179 | 179
2017-08-29 11:30 | 174 | 174
2017-08-29 12:00 | 175 | 174
2017-08-29 12:30 | 172 | 172
2017-08-29 13:00 | 174 | 174
2017-08-29 13:30 | 177 | 177
2017-08-29 14:00 | 182 | 182
2017-08-29 14:30 | 188 | 188
2017-08-29 15:00 | 196 | 196
2017-08-29 15:30 | 204 | 204
2017-08-29 16:00 | 216 | 216
2017-08-29 16:30 | 231 | 231
2017-08-29 17:00 | 247 | 246
2017-08-29 17:30 | 260 | 260
2017-08-29 18:00 | 272 | 272
2017-08-29 18:30 | 283 | 283
2017-08-29 19:00 | 283 | 283
2017-08-29 19:30 | 277 | 276
2017-08-29 20:00 | 275 | 274
2017-08-29 20:30 | 275 | 273
2017-08-29 21:00 | 264 | 262
2017-08-29 21:30 | 253 | 253
2017-08-29 22:00 | 241 | 241
2017-08-29 22:30 | 234 | 234
2017-08-29 23:00 | 229 | 229
2017-08-29 23:30 | 216 | 216
2017-08-30 | 199 | 198
2017-08-30 00:30 | 183 | 181
2017-08-30 01:00 | 172 | 170
2017-08-30 01:30 | 163 | 162
2017-08-30 02:00 | 158 | 157
2017-08-30 02:30 | 155 | 154
2017-08-30 03:00 | 153 | 152
2017-08-30 03:30 | 154 | 153
2017-08-30 04:00 | 154 | 153
2017-08-30 04:30 | 159 | 158
2017-08-30 05:00 | 168 | 168
2017-08-30 05:30 | 184 | 184
2017-08-30 06:00 | 204 | 204
2017-08-30 06:30 | 230 | 230
2017-08-30 07:00 | 249 | 249
2017-08-30 07:30 | 255 | 255
2017-08-30 08:00 | 245 | 245
2017-08-30 08:30 | 208 | 208
2017-08-30 09:00 | 150 | 150
2017-08-30 09:30 | 142 | 142
2017-08-30 10:00 | 135 | 135
2017-08-30 10:30 | 133 | 133
2017-08-30 11:00 | 128 | 128
2017-08-30 11:30 | 140 | 140
2017-08-30 12:00 | 174 | 174
2017-08-30 12:30 | 172 | 172
2017-08-30 13:00 | 172 | 172
2017-08-30 13:30 | 176 | 176
2017-08-30 14:00 | 181 | 181
2017-08-30 14:30 | 186 | 186
2017-08-30 15:00 | 194 | 194
2017-08-30 15:30 | 203 | 203
2017-08-30 16:00 | 218 | 218
2017-08-30 16:30 | 232 | 232
2017-08-30 17:00 | 247 | 247
2017-08-30 17:30 | 257 | 257
2017-08-30 18:00 | 269 | 269
2017-08-30 18:30 | 279 | 279
2017-08-30 19:00 | 280 | 280
2017-08-30 19:30 | 274 | 274
2017-08-30 20:00 | 273 | 273
2017-08-30 20:30 | 272 | 272
2017-08-30 21:00 | 260 | 260
2017-08-30 21:30 | 250 | 250
2017-08-30 22:00 | 240 | 240
2017-08-30 22:30 | 233 | 233
2017-08-30 23:00 | 229 | 229
2017-08-30 23:30 | 215 | 215
2017-08-31 | 198 | 198
2017-08-31 00:30 | 182 | 182
2017-08-31 01:00 | 172 | 171
2017-08-31 01:30 | 165 | 164
2017-08-31 02:00 | 160 | 158
2017-08-31 02:30 | 157 | 155
2017-08-31 03:00 | 155 | 153
2017-08-31 03:30 | 155 | 153
2017-08-31 04:00 | 156 | 155
2017-08-31 04:30 | 161 | 159
2017-08-31 05:00 | 170 | 169
2017-08-31 05:30 | 186 | 186
2017-08-31 06:00 | 205 | 205
2017-08-31 06:30 | 230 | 230
2017-08-31 07:00 | 249 | 249
2017-08-31 07:30 | 257 | 256
2017-08-31 08:00 | 247 | 247
2017-08-31 08:30 | 229 | 229
2017-08-31 09:00 | 212 | 212
2017-08-31 09:30 | 200 | 200
2017-08-31 10:00 | 190 | 190
2017-08-31 10:30 | 183 | 183
2017-08-31 11:00 | 182 | 182
2017-08-31 11:30 | 180 | 180
2017-08-31 12:00 | 182 | 182
2017-08-31 12:30 | 186 | 186
2017-08-31 13:00 | 188 | 188
2017-08-31 13:30 | 190 | 190
2017-08-31 14:00 | 193 | 192
2017-08-31 14:30 | 199 | 199
2017-08-31 15:00 | 205 | 205
2017-08-31 15:30 | 211 | 211
2017-08-31 16:00 | 220 | 220
2017-08-31 16:30 | 232 | 232
2017-08-31 17:00 | 247 | 247
2017-08-31 17:30 | 258 | 258
2017-08-31 18:00 | 271 | 271
2017-08-31 18:30 | 280 | 280
2017-08-31 19:00 | 283 | 283
2017-08-31 19:30 | 278 | 278
2017-08-31 20:00 | 276 | 276
2017-08-31 20:30 | 274 | 274
2017-08-31 21:00 | 263 | 263
2017-08-31 21:30 | 251 | 251
2017-08-31 22:00 | 240 | 240
2017-08-31 22:30 | 236 | 235
2017-08-31 23:00 | 235 | 235
2017-08-31 23:30 | 221 | 221
2017-09-01 | 201 | 201
2017-09-01 00:30 | 184 | 184
2017-09-01 01:00 | 173 | 172
2017-09-01 01:30 | 167 | 166
2017-09-01 02:00 | 162 | 161
2017-09-01 02:30 | 159 | 158
2017-09-01 03:00 | 157 | 155
2017-09-01 03:30 | 157 | 155
2017-09-01 04:00 | 157 | 156
2017-09-01 04:30 | 162 | 161
2017-09-01 05:00 | 170 | 169
2017-09-01 05:30 | 184 | 184
2017-09-01 06:00 | 200 | 200
2017-09-01 06:30 | 223 | 222
2017-09-01 07:00 | 241 | 241
2017-09-01 07:30 | 249 | 249
2017-09-01 08:00 | 243 | 243
2017-09-01 08:30 | 219 | 218
2017-09-01 09:00 | 154 | 154
2017-09-01 09:30 | 145 | 145
2017-09-01 10:00 | 138 | 138
2017-09-01 10:30 | 134 | 134
2017-09-01 11:00 | 132 | 132
2017-09-01 11:30 | 128 | 128
2017-09-01 12:00 | 127 | 127
2017-09-01 12:30 | 140 | 140
2017-09-01 13:00 | 176 | 175
2017-09-01 13:30 | 177 | 176
2017-09-01 14:00 | 182 | 181
2017-09-01 14:30 | 187 | 186
2017-09-01 15:00 | 188 | 188
2017-09-01 15:30 | 197 | 197
2017-09-01 16:00 | 210 | 209
2017-09-01 16:30 | 224 | 223
2017-09-01 17:00 | 239 | 239
2017-09-01 17:30 | 247 | 247
2017-09-01 18:00 | 257 | 257
2017-09-01 18:30 | 264 | 264
2017-09-01 19:00 | 267 | 267
2017-09-01 19:30 | 261 | 261
2017-09-01 20:00 | 259 | 259
2017-09-01 20:30 | 258 | 258
2017-09-01 21:00 | 249 | 248
2017-09-01 21:30 | 240 | 239
2017-09-01 22:00 | 232 | 232
2017-09-01 22:30 | 228 | 228
2017-09-01 23:00 | 227 | 226
2017-09-01 23:30 | 215 | 214
2017-09-02 | 197 | 197
2017-09-02 00:30 | 181 | 181
2017-09-02 01:00 | 170 | 170
2017-09-02 01:30 | 162 | 162
2017-09-02 02:00 | 156 | 156
2017-09-02 02:30 | 154 | 153
2017-09-02 03:00 | 151 | 151
2017-09-02 03:30 | 150 | 150
2017-09-02 04:00 | 150 | 150
2017-09-02 04:30 | 150 | 150
2017-09-02 05:00 | 154 | 154
2017-09-02 05:30 | 161 | 161
2017-09-02 06:00 | 167 | 167
2017-09-02 06:30 | 176 | 176
2017-09-02 07:00 | 182 | 182
2017-09-02 07:30 | 189 | 188
2017-09-02 08:00 | 188 | 187
2017-09-02 08:30 | 184 | 183
2017-09-02 09:00 | 180 | 179
2017-09-02 09:30 | 172 | 171
2017-09-02 10:00 | 163 | 162
2017-09-02 10:30 | 156 | 155
2017-09-02 11:00 | 149 | 148
2017-09-02 11:30 | 145 | 145
2017-09-02 12:00 | 142 | 141
2017-09-02 12:30 | 138 | 137
2017-09-02 13:00 | 136 | 135
2017-09-02 13:30 | 136 | 135
2017-09-02 14:00 | 139 | 138
2017-09-02 14:30 | 144 | 144
2017-09-02 15:00 | 151 | 150
2017-09-02 15:30 | 161 | 161
2017-09-02 16:00 | 173 | 172
2017-09-02 16:30 | 187 | 187
2017-09-02 17:00 | 201 | 201
2017-09-02 17:30 | 209 | 209
2017-09-02 18:00 | 219 | 218
2017-09-02 18:30 | 232 | 231
2017-09-02 19:00 | 233 | 232
2017-09-02 19:30 | 228 | 227
2017-09-02 20:00 | 226 | 226
2017-09-02 20:30 | 226 | 226
2017-09-02 21:00 | 218 | 218
2017-09-02 21:30 | 212 | 211
2017-09-02 22:00 | 207 | 207
2017-09-02 22:30 | 206 | 206
2017-09-02 23:00 | 207 | 207
2017-09-02 23:30 | 197 | 197
2017-09-03 | 182 | 182
2017-09-03 00:30 | 169 | 168
2017-09-03 01:00 | 158 | 157
2017-09-03 01:30 | 150 | 149
2017-09-03 02:00 | 144 | 143
2017-09-03 02:30 | 140 | 140
2017-09-03 03:00 | 137 | 137
2017-09-03 03:30 | 136 | 136
2017-09-03 04:00 | 136 | 136
2017-09-03 04:30 | 137 | 137
2017-09-03 05:00 | 139 | 139
2017-09-03 05:30 | 141 | 141
2017-09-03 06:00 | 145 | 145
2017-09-03 06:30 | 149 | 149
2017-09-03 07:00 | 152 | 152
2017-09-03 07:30 | 156 | 156
2017-09-03 08:00 | 158 | 158
2017-09-03 08:30 | 158 | 158
2017-09-03 09:00 | 156 | 156
2017-09-03 09:30 | 152 | 152
2017-09-03 10:00 | 147 | 146
2017-09-03 10:30 | 142 | 141
2017-09-03 11:00 | 138 | 137
2017-09-03 11:30 | 132 | 131
2017-09-03 12:00 | 129 | 129
2017-09-03 12:30 | 127 | 126
2017-09-03 13:00 | 131 | 130
2017-09-03 13:30 | 133 | 132
2017-09-03 14:00 | 138 | 136
2017-09-03 14:30 | 143 | 142
2017-09-03 15:00 | 151 | 150
2017-09-03 15:30 | 162 | 161
2017-09-03 16:00 | 175 | 174
2017-09-03 16:30 | 187 | 186
2017-09-03 17:00 | 200 | 199
2017-09-03 17:30 | 210 | 210
2017-09-03 18:00 | 222 | 221
2017-09-03 18:30 | 233 | 232
2017-09-03 19:00 | 234 | 234
2017-09-03 19:30 | 229 | 229
2017-09-03 20:00 | 226 | 226
2017-09-03 20:30 | 225 | 225
2017-09-03 21:00 | 216 | 216
2017-09-03 21:30 | 208 | 208
2017-09-03 22:00 | 203 | 203
2017-09-03 22:30 | 199 | 199
2017-09-03 23:00 | 199 | 199
2017-09-03 23:30 | 189 | 188
2017-09-04 | 175 | 175
2017-09-04 00:30 | 161 | 160
2017-09-04 01:00 | 152 | 151
2017-09-04 01:30 | 146 | 145
2017-09-04 02:00 | 141 | 140
2017-09-04 02:30 | 138 | 137
2017-09-04 03:00 | 136 | 136
2017-09-04 03:30 | 137 | 137
2017-09-04 04:00 | 138 | 138
2017-09-04 04:30 | 142 | 142
2017-09-04 05:00 | 150 | 150
2017-09-04 05:30 | 165 | 165
2017-09-04 06:00 | 182 | 181
2017-09-04 06:30 | 202 | 201
2017-09-04 07:00 | 217 | 216
2017-09-04 07:30 | 226 | 226
2017-09-04 08:00 | 221 | 221
2017-09-04 08:30 | 211 | 211
2017-09-04 09:00 | 201 | 201
2017-09-04 09:30 | 196 | 196
2017-09-04 10:00 | 191 | 191
2017-09-04 10:30 | 188 | 188
2017-09-04 11:00 | 184 | 184
2017-09-04 11:30 | 184 | 183
2017-09-04 12:00 | 187 | 186
2017-09-04 12:30 | 189 | 189
2017-09-04 13:00 | 193 | 192
2017-09-04 13:30 | 200 | 199
2017-09-04 14:00 | 207 | 207
2017-09-04 14:30 | 216 | 215
2017-09-04 15:00 | 221 | 221
2017-09-04 15:30 | 229 | 229
2017-09-04 16:00 | 238 | 238
2017-09-04 16:30 | 249 | 249
2017-09-04 17:00 | 259 | 259
2017-09-04 17:30 | 264 | 264
2017-09-04 18:00 | 271 | 271
2017-09-04 18:30 | 277 | 277
2017-09-04 19:00 | 276 | 276
2017-09-04 19:30 | 268 | 267
2017-09-04 20:00 | 259 | 259
2017-09-04 20:30 | 257 | 256
2017-09-04 21:00 | 246 | 245
2017-09-04 21:30 | 233 | 232
2017-09-04 22:00 | 222 | 222
2017-09-04 22:30 | 217 | 217
2017-09-04 23:00 | 214 | 214
2017-09-04 23:30 | 202 | 202
2017-09-05 | 185 | 185
2017-09-05 00:30 | 170 | 170
2017-09-05 01:00 | 166 | 166
2017-09-05 01:30 | 160 | 160
2017-09-05 02:00 | 154 | 154
2017-09-05 02:30 | 152 | 151
2017-09-05 03:00 | 152 | 151
2017-09-05 03:30 | 147 | 147
2017-09-05 04:00 | 146 | 146
2017-09-05 04:30 | 151 | 150
2017-09-05 05:00 | 158 | 158
2017-09-05 05:30 | 171 | 171
2017-09-05 06:00 | 186 | 186
2017-09-05 06:30 | 209 | 209
2017-09-05 07:00 | 225 | 225
2017-09-05 07:30 | 231 | 231
2017-09-05 08:00 | 226 | 226
2017-09-05 08:30 | 212 | 211
2017-09-05 09:00 | 197 | 197
2017-09-05 09:30 | 186 | 186
2017-09-05 10:00 | 179 | 178
2017-09-05 10:30 | 175 | 174
2017-09-05 11:00 | 170 | 170
2017-09-05 11:30 | 168 | 168
2017-09-05 12:00 | 167 | 167
2017-09-05 12:30 | 169 | 169
2017-09-05 13:00 | 172 | 172
2017-09-05 13:30 | 177 | 177
2017-09-05 14:00 | 183 | 183
2017-09-05 14:30 | 190 | 190
2017-09-05 15:00 | 199 | 198
2017-09-05 15:30 | 209 | 209
2017-09-05 16:00 | 222 | 222
2017-09-05 16:30 | 234 | 234
2017-09-05 17:00 | 247 | 247
2017-09-05 17:30 | 253 | 253
2017-09-05 18:00 | 262 | 262
2017-09-05 18:30 | 269 | 269
2017-09-05 19:00 | 269 | 269
2017-09-05 19:30 | 261 | 261
2017-09-05 20:00 | 259 | 259
2017-09-05 20:30 | 257 | 257
2017-09-05 21:00 | 246 | 246
2017-09-05 21:30 | 235 | 235
2017-09-05 22:00 | 226 | 226
2017-09-05 22:30 | 218 | 218
2017-09-05 23:00 | 216 | 216
2017-09-05 23:30 | 204 | 204
2017-09-06 | 186 | 186
2017-09-06 00:30 | 170 | 170
2017-09-06 01:00 | 161 | 161
2017-09-06 01:30 | 154 | 154
2017-09-06 02:00 | 149 | 149
2017-09-06 02:30 | 147 | 147
2017-09-06 03:00 | 146 | 146
2017-09-06 03:30 | 148 | 148
2017-09-06 04:00 | 148 | 148
2017-09-06 04:30 | 153 | 153
2017-09-06 05:00 | 162 | 162
2017-09-06 05:30 | 177 | 177
2017-09-06 06:00 | 192 | 192
2017-09-06 06:30 | 216 | 216
2017-09-06 07:00 | 231 | 231
2017-09-06 07:30 | 238 | 238
2017-09-06 08:00 | 229 | 229
2017-09-06 08:30 | 215 | 215
2017-09-06 09:00 | 200 | 200
2017-09-06 09:30 | 191 | 190
2017-09-06 10:00 | 182 | 182
2017-09-06 10:30 | 176 | 175
2017-09-06 11:00 | 172 | 172
2017-09-06 11:30 | 170 | 169
2017-09-06 12:00 | 169 | 169
2017-09-06 12:30 | 170 | 170
2017-09-06 13:00 | 172 | 172
2017-09-06 13:30 | 176 | 176
2017-09-06 14:00 | 185 | 184
2017-09-06 14:30 | 192 | 191
2017-09-06 15:00 | 200 | 199
2017-09-06 15:30 | 210 | 210
2017-09-06 16:00 | 224 | 223
2017-09-06 16:30 | 237 | 236
2017-09-06 17:00 | 250 | 249
2017-09-06 17:30 | 259 | 257
2017-09-06 18:00 | 266 | 264
2017-09-06 18:30 | 274 | 273
2017-09-06 19:00 | 274 | 273
2017-09-06 19:30 | 268 | 267
2017-09-06 20:00 | 264 | 264
2017-09-06 20:30 | 263 | 262
2017-09-06 21:00 | 249 | 249
2017-09-06 21:30 | 238 | 238
2017-09-06 22:00 | 227 | 227
2017-09-06 22:30 | 222 | 222
2017-09-06 23:00 | 219 | 219
2017-09-06 23:30 | 205 | 205
2017-09-07 | 188 | 188
2017-09-07 00:30 | 173 | 173
2017-09-07 01:00 | 163 | 162
2017-09-07 01:30 | 157 | 157
2017-09-07 02:00 | 152 | 151
2017-09-07 02:30 | 149 | 148
2017-09-07 03:00 | 148 | 146
2017-09-07 03:30 | 148 | 147
2017-09-07 04:00 | 149 | 148
2017-09-07 04:30 | 154 | 153
2017-09-07 05:00 | 162 | 162
2017-09-07 05:30 | 179 | 178
2017-09-07 06:00 | 194 | 194
2017-09-07 06:30 | 216 | 216
2017-09-07 07:00 | 229 | 229
2017-09-07 07:30 | 236 | 236
2017-09-07 08:00 | 224 | 224
2017-09-07 08:30 | 211 | 211
2017-09-07 09:00 | 199 | 199
2017-09-07 09:30 | 185 | 185
2017-09-07 10:00 | 179 | 179
2017-09-07 10:30 | 174 | 174
2017-09-07 11:00 | 170 | 170
2017-09-07 11:30 | 172 | 172
2017-09-07 12:00 | 167 | 167
2017-09-07 12:30 | 168 | 168
2017-09-07 13:00 | 170 | 170
2017-09-07 13:30 | 175 | 175
2017-09-07 14:00 | 182 | 182
2017-09-07 14:30 | 189 | 189
2017-09-07 15:00 | 196 | 196
2017-09-07 15:30 | 206 | 206
2017-09-07 16:00 | 218 | 218
2017-09-07 16:30 | 232 | 231
2017-09-07 17:00 | 245 | 245
2017-09-07 17:30 | 257 | 257
2017-09-07 18:00 | 280 | 280
2017-09-07 18:30 | 289 | 289
2017-09-07 19:00 | 292 | 292
2017-09-07 19:30 | 285 | 285
2017-09-07 20:00 | 281 | 281
2017-09-07 20:30 | 265 | 264
2017-09-07 21:00 | 247 | 246
2017-09-07 21:30 | 236 | 235
2017-09-07 22:00 | 226 | 226
2017-09-07 22:30 | 221 | 221
2017-09-07 23:00 | 219 | 219
2017-09-07 23:30 | 206 | 206
2017-09-08 | 188 | 188
2017-09-08 00:30 | 174 | 174
2017-09-08 01:00 | 163 | 163
2017-09-08 01:30 | 156 | 156
2017-09-08 02:00 | 150 | 150
2017-09-08 02:30 | 148 | 148
2017-09-08 03:00 | 151 | 150
2017-09-08 03:30 | 148 | 148
2017-09-08 04:00 | 147 | 146
2017-09-08 04:30 | 152 | 152
2017-09-08 05:00 | 161 | 161
2017-09-08 05:30 | 176 | 176
2017-09-08 06:00 | 193 | 193
2017-09-08 06:30 | 217 | 217
2017-09-08 07:00 | 232 | 232
2017-09-08 07:30 | 242 | 242
2017-09-08 08:00 | 235 | 235
2017-09-08 08:30 | 218 | 218
2017-09-08 09:00 | 201 | 201
2017-09-08 09:30 | 188 | 188
2017-09-08 10:00 | 178 | 178
2017-09-08 10:30 | 173 | 173
2017-09-08 11:00 | 170 | 170
2017-09-08 11:30 | 167 | 167
2017-09-08 12:00 | 166 | 165
2017-09-08 12:30 | 166 | 165
2017-09-08 13:00 | 167 | 166
2017-09-08 13:30 | 170 | 170
2017-09-08 14:00 | 175 | 175
2017-09-08 14:30 | 181 | 181
2017-09-08 15:00 | 187 | 187
2017-09-08 15:30 | 197 | 197
2017-09-08 16:00 | 210 | 210
2017-09-08 16:30 | 221 | 221
2017-09-08 17:00 | 234 | 234
2017-09-08 17:30 | 239 | 239
2017-09-08 18:00 | 244 | 244
2017-09-08 18:30 | 251 | 251
2017-09-08 19:00 | 253 | 253
2017-09-08 19:30 | 248 | 248
2017-09-08 20:00 | 246 | 246
2017-09-08 20:30 | 264 | 264
2017-09-08 21:00 | 256 | 256
2017-09-08 21:30 | 247 | 247
2017-09-08 22:00 | 240 | 239
2017-09-08 22:30 | 237 | 237
2017-09-08 23:00 | 235 | 235
2017-09-08 23:30 | 222 | 222
2017-09-09 | 206 | 206
2017-09-09 00:30 | 190 | 190
2017-09-09 01:00 | 179 | 178
2017-09-09 01:30 | 171 | 171
2017-09-09 02:00 | 164 | 163
2017-09-09 02:30 | 161 | 161
2017-09-09 03:00 | 159 | 158
2017-09-09 03:30 | 157 | 156
2017-09-09 04:00 | 156 | 155
2017-09-09 04:30 | 157 | 156
2017-09-09 05:00 | 160 | 159
2017-09-09 05:30 | 167 | 167
2017-09-09 06:00 | 174 | 173
2017-09-09 06:30 | 183 | 183
2017-09-09 07:00 | 188 | 187
2017-09-09 07:30 | 190 | 190
2017-09-09 08:00 | 188 | 188
2017-09-09 08:30 | 185 | 185
2017-09-09 09:00 | 179 | 179
2017-09-09 09:30 | 172 | 172
2017-09-09 10:00 | 165 | 165
2017-09-09 10:30 | 158 | 158
2017-09-09 11:00 | 151 | 151
2017-09-09 11:30 | 147 | 147
2017-09-09 12:00 | 142 | 142
2017-09-09 12:30 | 139 | 139
2017-09-09 13:00 | 139 | 139
2017-09-09 13:30 | 142 | 142
2017-09-09 14:00 | 147 | 147
2017-09-09 14:30 | 155 | 155
2017-09-09 15:00 | 164 | 164
2017-09-09 15:30 | 174 | 174
2017-09-09 16:00 | 192 | 192
2017-09-09 16:30 | 206 | 206
2017-09-09 17:00 | 219 | 219
2017-09-09 17:30 | 229 | 229
2017-09-09 18:00 | 237 | 237
2017-09-09 18:30 | 248 | 248
2017-09-09 19:00 | 250 | 249
2017-09-09 19:30 | 241 | 241
2017-09-09 20:00 | 223 | 223
2017-09-09 20:30 | 223 | 222
2017-09-09 21:00 | 215 | 215
2017-09-09 21:30 | 207 | 207
2017-09-09 22:00 | 203 | 203
2017-09-09 22:30 | 202 | 202
2017-09-09 23:00 | 204 | 204
2017-09-09 23:30 | 195 | 195
2017-09-10 | 181 | 180
2017-09-10 00:30 | 168 | 166
2017-09-10 01:00 | 159 | 157
2017-09-10 01:30 | 151 | 148
2017-09-10 02:00 | 144 | 142
2017-09-10 02:30 | 139 | 138
2017-09-10 03:00 | 137 | 135
2017-09-10 03:30 | 136 | 134
2017-09-10 04:00 | 135 | 134
2017-09-10 04:30 | 134 | 133
2017-09-10 05:00 | 135 | 134
2017-09-10 05:30 | 140 | 139
2017-09-10 06:00 | 149 | 148
2017-09-10 06:30 | 150 | 149
2017-09-10 07:00 | 150 | 148
2017-09-10 07:30 | 148 | 147
2017-09-10 08:00 | 148 | 147
2017-09-10 08:30 | 148 | 147
2017-09-10 09:00 | 145 | 144
2017-09-10 09:30 | 140 | 140
2017-09-10 10:00 | 135 | 135
2017-09-10 10:30 | 131 | 130
2017-09-10 11:00 | 127 | 127
2017-09-10 11:30 | 123 | 123
2017-09-10 12:00 | 125 | 125
2017-09-10 12:30 | 121 | 121
2017-09-10 13:00 | 123 | 123
2017-09-10 13:30 | 126 | 126
2017-09-10 14:00 | 130 | 130
2017-09-10 14:30 | 135 | 135
2017-09-10 15:00 | 143 | 143
2017-09-10 15:30 | 154 | 154
2017-09-10 16:00 | 169 | 169
2017-09-10 16:30 | 184 | 184
2017-09-10 17:00 | 200 | 200
2017-09-10 17:30 | 213 | 213
2017-09-10 18:00 | 224 | 224
2017-09-10 18:30 | 237 | 237
2017-09-10 19:00 | 242 | 242
2017-09-10 19:30 | 235 | 234
2017-09-10 20:00 | 230 | 230
2017-09-10 20:30 | 230 | 230
2017-09-10 21:00 | 220 | 220
2017-09-10 21:30 | 212 | 211
2017-09-10 22:00 | 203 | 203
2017-09-10 22:30 | 201 | 200
2017-09-10 23:00 | 201 | 200
2017-09-10 23:30 | 191 | 190
2017-09-11 | 176 | 174
2017-09-11 00:30 | 161 | 160
2017-09-11 01:00 | 153 | 152
2017-09-11 01:30 | 148 | 146
2017-09-11 02:00 | 143 | 141
2017-09-11 02:30 | 141 | 139
2017-09-11 03:00 | 142 | 140
2017-09-11 03:30 | 144 | 142
2017-09-11 04:00 | 141 | 139
2017-09-11 04:30 | 146 | 144
2017-09-11 05:00 | 154 | 153
2017-09-11 05:30 | 169 | 168
2017-09-11 06:00 | 184 | 184
2017-09-11 06:30 | 204 | 204
2017-09-11 07:00 | 220 | 220
2017-09-11 07:30 | 227 | 227
2017-09-11 08:00 | 221 | 221
2017-09-11 08:30 | 208 | 208
2017-09-11 09:00 | 197 | 197
2017-09-11 09:30 | 188 | 188
2017-09-11 10:00 | 181 | 181
2017-09-11 10:30 | 177 | 177
2017-09-11 11:00 | 174 | 174
2017-09-11 11:30 | 172 | 172
2017-09-11 12:00 | 174 | 174
2017-09-11 12:30 | 175 | 175
2017-09-11 13:00 | 177 | 177
2017-09-11 13:30 | 183 | 182
2017-09-11 14:00 | 189 | 188
2017-09-11 14:30 | 195 | 194
2017-09-11 15:00 | 201 | 200
2017-09-11 15:30 | 209 | 209
2017-09-11 16:00 | 222 | 222
2017-09-11 16:30 | 235 | 235
2017-09-11 17:00 | 247 | 247
2017-09-11 17:30 | 255 | 255
2017-09-11 18:00 | 264 | 264
2017-09-11 18:30 | 272 | 272
2017-09-11 19:00 | 271 | 271
2017-09-11 19:30 | 262 | 262
2017-09-11 20:00 | 257 | 257
2017-09-11 20:30 | 255 | 255
2017-09-11 21:00 | 242 | 242
2017-09-11 21:30 | 231 | 231
2017-09-11 22:00 | 222 | 222
2017-09-11 22:30 | 216 | 216
2017-09-11 23:00 | 213 | 213
2017-09-11 23:30 | 201 | 201
2017-09-12 | 185 | 184
2017-09-12 00:30 | 171 | 170
2017-09-12 01:00 | 162 | 161
2017-09-12 01:30 | 156 | 154
2017-09-12 02:00 | 151 | 149
2017-09-12 02:30 | 148 | 146
2017-09-12 03:00 | 145 | 144
2017-09-12 03:30 | 145 | 143
2017-09-12 04:00 | 147 | 145
2017-09-12 04:30 | 151 | 150
2017-09-12 05:00 | 158 | 157
2017-09-12 05:30 | 172 | 172
2017-09-12 06:00 | 185 | 185
2017-09-12 06:30 | 203 | 203
2017-09-12 07:00 | 220 | 220
2017-09-12 07:30 | 228 | 228
2017-09-12 08:00 | 221 | 221
2017-09-12 08:30 | 208 | 208
2017-09-12 09:00 | 198 | 198
2017-09-12 09:30 | 189 | 189
2017-09-12 10:00 | 184 | 183
2017-09-12 10:30 | 182 | 182
2017-09-12 11:00 | 182 | 182
2017-09-12 11:30 | 180 | 180
2017-09-12 12:00 | 181 | 181
2017-09-12 12:30 | 184 | 184
2017-09-12 13:00 | 191 | 191
2017-09-12 13:30 | 196 | 196
2017-09-12 14:00 | 200 | 200
2017-09-12 14:30 | 207 | 207
2017-09-12 15:00 | 217 | 217
2017-09-12 15:30 | 221 | 220
2017-09-12 16:00 | 232 | 232
2017-09-12 16:30 | 244 | 244
2017-09-12 17:00 | 255 | 254
2017-09-12 17:30 | 261 | 260
2017-09-12 18:00 | 266 | 265
2017-09-12 18:30 | 273 | 273
2017-09-12 19:00 | 273 | 273
2017-09-12 19:30 | 264 | 264
2017-09-12 20:00 | 262 | 261
2017-09-12 20:30 | 258 | 258
2017-09-12 21:00 | 245 | 245
2017-09-12 21:30 | 235 | 235
2017-09-12 22:00 | 223 | 223
2017-09-12 22:30 | 218 | 218
2017-09-12 23:00 | 216 | 216
2017-09-12 23:30 | 203 | 203
2017-09-13 | 186 | 186
2017-09-13 00:30 | 171 | 170
2017-09-13 01:00 | 162 | 160
2017-09-13 01:30 | 156 | 154
2017-09-13 02:00 | 151 | 149
2017-09-13 02:30 | 149 | 146
2017-09-13 03:00 | 147 | 145
2017-09-13 03:30 | 147 | 145
2017-09-13 04:00 | 148 | 145
2017-09-13 04:30 | 152 | 150
2017-09-13 05:00 | 159 | 157
2017-09-13 05:30 | 171 | 170
2017-09-13 06:00 | 183 | 183
2017-09-13 06:30 | 205 | 204
2017-09-13 07:00 | 219 | 218
2017-09-13 07:30 | 229 | 228
2017-09-13 08:00 | 226 | 225
2017-09-13 08:30 | 214 | 214
2017-09-13 09:00 | 202 | 202
2017-09-13 09:30 | 195 | 195
2017-09-13 10:00 | 192 | 191
2017-09-13 10:30 | 188 | 188
2017-09-13 11:00 | 187 | 187
2017-09-13 11:30 | 186 | 186
2017-09-13 12:00 | 188 | 188
2017-09-13 12:30 | 189 | 189
2017-09-13 13:00 | 193 | 193
2017-09-13 13:30 | 197 | 197
2017-09-13 14:00 | 204 | 204
2017-09-13 14:30 | 211 | 211
2017-09-13 15:00 | 218 | 217
2017-09-13 15:30 | 227 | 227
2017-09-13 16:00 | 239 | 239
2017-09-13 16:30 | 248 | 248
2017-09-13 17:00 | 260 | 260
2017-09-13 17:30 | 265 | 265
2017-09-13 18:00 | 270 | 270
2017-09-13 18:30 | 276 | 276
2017-09-13 19:00 | 276 | 276
2017-09-13 19:30 | 267 | 266
2017-09-13 20:00 | 265 | 264
2017-09-13 20:30 | 261 | 260
2017-09-13 21:00 | 249 | 248
2017-09-13 21:30 | 237 | 237
2017-09-13 22:00 | 226 | 226
2017-09-13 22:30 | 221 | 221
2017-09-13 23:00 | 217 | 217
2017-09-13 23:30 | 204 | 204
2017-09-14 | 187 | 187
2017-09-14 00:30 | 170 | 170
2017-09-14 01:00 | 161 | 161
2017-09-14 01:30 | 154 | 154
2017-09-14 02:00 | 150 | 150
2017-09-14 02:30 | 148 | 148
2017-09-14 03:00 | 146 | 146
2017-09-14 03:30 | 146 | 146
2017-09-14 04:00 | 145 | 145
2017-09-14 04:30 | 150 | 150
2017-09-14 05:00 | 158 | 158
2017-09-14 05:30 | 172 | 171
2017-09-14 06:00 | 184 | 183
2017-09-14 06:30 | 203 | 203
2017-09-14 07:00 | 215 | 215
2017-09-14 07:30 | 233 | 233
2017-09-14 08:00 | 248 | 248
2017-09-14 08:30 | 254 | 254
2017-09-14 09:00 | 241 | 241
2017-09-14 09:30 | 228 | 227
2017-09-14 10:00 | 208 | 207
2017-09-14 10:30 | 187 | 187
2017-09-14 11:00 | 175 | 175
2017-09-14 11:30 | 172 | 172
2017-09-14 12:00 | 172 | 171
2017-09-14 12:30 | 171 | 170
2017-09-14 13:00 | 171 | 170
2017-09-14 13:30 | 170 | 170
2017-09-14 14:00 | 173 | 172
2017-09-14 14:30 | 179 | 179
2017-09-14 15:00 | 186 | 186
2017-09-14 15:30 | 197 | 196
2017-09-14 16:00 | 211 | 210
2017-09-14 16:30 | 224 | 224
2017-09-14 17:00 | 239 | 238
2017-09-14 17:30 | 248 | 247
2017-09-14 18:00 | 258 | 257
2017-09-14 18:30 | 270 | 270
2017-09-14 19:00 | 270 | 270
2017-09-14 19:30 | 263 | 263
2017-09-14 20:00 | 258 | 257
2017-09-14 20:30 | 257 | 256
2017-09-14 21:00 | 247 | 246
2017-09-14 21:30 | 234 | 233
2017-09-14 22:00 | 226 | 225
2017-09-14 22:30 | 220 | 220
2017-09-14 23:00 | 217 | 217
2017-09-14 23:30 | 204 | 204
2017-09-15 | 187 | 187
2017-09-15 00:30 | 171 | 170
2017-09-15 01:00 | 162 | 161
2017-09-15 01:30 | 154 | 154
2017-09-15 02:00 | 149 | 148
2017-09-15 02:30 | 147 | 147
2017-09-15 03:00 | 145 | 145
2017-09-15 03:30 | 147 | 147
2017-09-15 04:00 | 147 | 147
2017-09-15 04:30 | 154 | 154
2017-09-15 05:00 | 163 | 163
2017-09-15 05:30 | 179 | 178
2017-09-15 06:00 | 193 | 193
2017-09-15 06:30 | 214 | 213
2017-09-15 07:00 | 225 | 224
2017-09-15 07:30 | 230 | 229
2017-09-15 08:00 | 223 | 222
2017-09-15 08:30 | 214 | 213
2017-09-15 09:00 | 195 | 194
2017-09-15 09:30 | 183 | 183
2017-09-15 10:00 | 176 | 176
2017-09-15 10:30 | 170 | 169
2017-09-15 11:00 | 167 | 167
2017-09-15 11:30 | 165 | 165
2017-09-15 12:00 | 165 | 165
2017-09-15 12:30 | 164 | 164
2017-09-15 13:00 | 166 | 165
2017-09-15 13:30 | 169 | 168
2017-09-15 14:00 | 173 | 173
2017-09-15 14:30 | 179 | 178
2017-09-15 15:00 | 185 | 184
2017-09-15 15:30 | 193 | 192
2017-09-15 16:00 | 205 | 205
2017-09-15 16:30 | 218 | 217
2017-09-15 17:00 | 229 | 229
2017-09-15 17:30 | 235 | 235
2017-09-15 18:00 | 240 | 240
2017-09-15 18:30 | 253 | 253
2017-09-15 19:00 | 260 | 260
2017-09-15 19:30 | 256 | 256
2017-09-15 20:00 | 255 | 255
2017-09-15 20:30 | 254 | 253
2017-09-15 21:00 | 244 | 244
2017-09-15 21:30 | 235 | 235
2017-09-15 22:00 | 228 | 228
2017-09-15 22:30 | 226 | 226
2017-09-15 23:00 | 223 | 223
2017-09-15 23:30 | 212 | 212
2017-09-16 | 196 | 196
2017-09-16 00:30 | 181 | 181
2017-09-16 01:00 | 171 | 171
2017-09-16 01:30 | 164 | 164
2017-09-16 02:00 | 158 | 158
2017-09-16 02:30 | 154 | 154
2017-09-16 03:00 | 153 | 153
2017-09-16 03:30 | 152 | 152
2017-09-16 04:00 | 151 | 151
2017-09-16 04:30 | 152 | 152
2017-09-16 05:00 | 155 | 155
2017-09-16 05:30 | 162 | 162
2017-09-16 06:00 | 166 | 166
2017-09-16 06:30 | 174 | 174
2017-09-16 07:00 | 176 | 176
2017-09-16 07:30 | 177 | 177
2017-09-16 08:00 | 175 | 175
2017-09-16 08:30 | 172 | 172
2017-09-16 09:00 | 167 | 166
2017-09-16 09:30 | 161 | 160
2017-09-16 10:00 | 154 | 153
2017-09-16 10:30 | 147 | 146
2017-09-16 11:00 | 141 | 141
2017-09-16 11:30 | 136 | 136
2017-09-16 12:00 | 134 | 133
2017-09-16 12:30 | 132 | 132
2017-09-16 13:00 | 132 | 132
2017-09-16 13:30 | 135 | 134
2017-09-16 14:00 | 139 | 139
2017-09-16 14:30 | 145 | 144
2017-09-16 15:00 | 155 | 154
2017-09-16 15:30 | 164 | 164
2017-09-16 16:00 | 177 | 176
2017-09-16 16:30 | 192 | 191
2017-09-16 17:00 | 203 | 202
2017-09-16 17:30 | 211 | 210
2017-09-16 18:00 | 220 | 219
2017-09-16 18:30 | 232 | 231
2017-09-16 19:00 | 234 | 233
2017-09-16 19:30 | 228 | 228
2017-09-16 20:00 | 227 | 226
2017-09-16 20:30 | 225 | 224
2017-09-16 21:00 | 217 | 216
2017-09-16 21:30 | 209 | 209
2017-09-16 22:00 | 203 | 203
2017-09-16 22:30 | 203 | 203
2017-09-16 23:00 | 203 | 203
2017-09-16 23:30 | 194 | 194
2017-09-17 | 180 | 180
2017-09-17 00:30 | 166 | 166
2017-09-17 01:00 | 158 | 157
2017-09-17 01:30 | 151 | 150
2017-09-17 02:00 | 145 | 145
2017-09-17 02:30 | 142 | 141
2017-09-17 03:00 | 140 | 139
2017-09-17 03:30 | 139 | 139
2017-09-17 04:00 | 138 | 138
2017-09-17 04:30 | 139 | 138
2017-09-17 05:00 | 140 | 139
2017-09-17 05:30 | 143 | 143
2017-09-17 06:00 | 144 | 144
2017-09-17 06:30 | 148 | 148
2017-09-17 07:00 | 151 | 151
2017-09-17 07:30 | 154 | 153
2017-09-17 08:00 | 161 | 161
2017-09-17 08:30 | 162 | 162
2017-09-17 09:00 | 161 | 161
2017-09-17 09:30 | 162 | 162
2017-09-17 10:00 | 159 | 159
2017-09-17 10:30 | 151 | 151
2017-09-17 11:00 | 147 | 147
2017-09-17 11:30 | 143 | 143
2017-09-17 12:00 | 134 | 134
2017-09-17 12:30 | 136 | 136
2017-09-17 13:00 | 136 | 136
2017-09-17 13:30 | 136 | 136
2017-09-17 14:00 | 143 | 143
2017-09-17 14:30 | 147 | 147
2017-09-17 15:00 | 154 | 154
2017-09-17 15:30 | 163 | 163
2017-09-17 16:00 | 175 | 174
2017-09-17 16:30 | 186 | 185
2017-09-17 17:00 | 199 | 198
2017-09-17 17:30 | 210 | 209
2017-09-17 18:00 | 224 | 223
2017-09-17 18:30 | 237 | 236
2017-09-17 19:00 | 237 | 236
2017-09-17 19:30 | 230 | 229
2017-09-17 20:00 | 227 | 227
2017-09-17 20:30 | 226 | 226
2017-09-17 21:00 | 217 | 217
2017-09-17 21:30 | 210 | 210
2017-09-17 22:00 | 204 | 204
2017-09-17 22:30 | 202 | 202
2017-09-17 23:00 | 202 | 202
2017-09-17 23:30 | 192 | 192
2017-09-18 | 177 | 177
2017-09-18 00:30 | 163 | 163
2017-09-18 01:00 | 153 | 153
2017-09-18 01:30 | 147 | 147
2017-09-18 02:00 | 142 | 142
2017-09-18 02:30 | 141 | 141
2017-09-18 03:00 | 139 | 139
2017-09-18 03:30 | 139 | 139
2017-09-18 04:00 | 141 | 140
2017-09-18 04:30 | 144 | 144
2017-09-18 05:00 | 152 | 152
2017-09-18 05:30 | 167 | 167
2017-09-18 06:00 | 179 | 179
2017-09-18 06:30 | 196 | 195
2017-09-18 07:00 | 206 | 205
2017-09-18 07:30 | 212 | 211
2017-09-18 08:00 | 211 | 210
2017-09-18 08:30 | 207 | 206
2017-09-18 09:00 | 206 | 206
2017-09-18 09:30 | 208 | 207
2017-09-18 10:00 | 204 | 204
2017-09-18 10:30 | 195 | 195
2017-09-18 11:00 | 190 | 189
2017-09-18 11:30 | 185 | 185
2017-09-18 12:00 | 183 | 183
2017-09-18 12:30 | 181 | 181
2017-09-18 13:00 | 182 | 181
2017-09-18 13:30 | 185 | 185
2017-09-18 14:00 | 188 | 188
2017-09-18 14:30 | 193 | 193
2017-09-18 15:00 | 201 | 201
2017-09-18 15:30 | 210 | 210
2017-09-18 16:00 | 221 | 221
2017-09-18 16:30 | 233 | 233
2017-09-18 17:00 | 244 | 244
2017-09-18 17:30 | 253 | 252
2017-09-18 18:00 | 260 | 260
2017-09-18 18:30 | 269 | 269
2017-09-18 19:00 | 270 | 270
2017-09-18 19:30 | 262 | 262
2017-09-18 20:00 | 258 | 258
2017-09-18 20:30 | 253 | 253
2017-09-18 21:00 | 243 | 243
2017-09-18 21:30 | 233 | 233
2017-09-18 22:00 | 224 | 224
2017-09-18 22:30 | 219 | 218
2017-09-18 23:00 | 216 | 216
2017-09-18 23:30 | 203 | 202
2017-09-19 | 186 | 186
2017-09-19 00:30 | 170 | 169
2017-09-19 01:00 | 160 | 159
2017-09-19 01:30 | 154 | 152
2017-09-19 02:00 | 150 | 149
2017-09-19 02:30 | 145 | 145
2017-09-19 03:00 | 143 | 143
2017-09-19 03:30 | 143 | 143
2017-09-19 04:00 | 143 | 143
2017-09-19 04:30 | 149 | 149
2017-09-19 05:00 | 157 | 156
2017-09-19 05:30 | 171 | 170
2017-09-19 06:00 | 181 | 181
2017-09-19 06:30 | 196 | 195
2017-09-19 07:00 | 206 | 205
2017-09-19 07:30 | 211 | 211
2017-09-19 08:00 | 207 | 207
2017-09-19 08:30 | 203 | 203
2017-09-19 09:00 | 196 | 196
2017-09-19 09:30 | 191 | 191
2017-09-19 10:00 | 184 | 184
2017-09-19 10:30 | 180 | 180
2017-09-19 11:00 | 178 | 178
2017-09-19 11:30 | 178 | 178
2017-09-19 12:00 | 184 | 184
2017-09-19 12:30 | 185 | 185
2017-09-19 13:00 | 192 | 191
2017-09-19 13:30 | 196 | 196
2017-09-19 14:00 | 203 | 202
2017-09-19 14:30 | 210 | 209
2017-09-19 15:00 | 219 | 219
2017-09-19 15:30 | 228 | 228
2017-09-19 16:00 | 239 | 238
2017-09-19 16:30 | 247 | 247
2017-09-19 17:00 | 257 | 256
2017-09-19 17:30 | 263 | 262
2017-09-19 18:00 | 269 | 269
2017-09-19 18:30 | 276 | 276
2017-09-19 19:00 | 277 | 276
2017-09-19 19:30 | 268 | 268
2017-09-19 20:00 | 265 | 265
2017-09-19 20:30 | 262 | 262
2017-09-19 21:00 | 250 | 250
2017-09-19 21:30 | 239 | 239
2017-09-19 22:00 | 231 | 230
2017-09-19 22:30 | 225 | 225
2017-09-19 23:00 | 222 | 221
2017-09-19 23:30 | 209 | 208
2017-09-20 | 192 | 192
2017-09-20 00:30 | 176 | 176
2017-09-20 01:00 | 166 | 166
2017-09-20 01:30 | 160 | 159
2017-09-20 02:00 | 155 | 155
2017-09-20 02:30 | 153 | 152
2017-09-20 03:00 | 152 | 152
2017-09-20 03:30 | 152 | 152
2017-09-20 04:00 | 152 | 152
2017-09-20 04:30 | 154 | 154
2017-09-20 05:00 | 162 | 162
2017-09-20 05:30 | 174 | 174
2017-09-20 06:00 | 185 | 185
2017-09-20 06:30 | 200 | 200
2017-09-20 07:00 | 210 | 209
2017-09-20 07:30 | 217 | 216
2017-09-20 08:00 | 215 | 215
2017-09-20 08:30 | 212 | 211
2017-09-20 09:00 | 205 | 204
2017-09-20 09:30 | 197 | 196
2017-09-20 10:00 | 191 | 190
2017-09-20 10:30 | 187 | 186
2017-09-20 11:00 | 185 | 184
2017-09-20 11:30 | 185 | 183
2017-09-20 12:00 | 187 | 186
2017-09-20 12:30 | 189 | 189
2017-09-20 13:00 | 190 | 190
2017-09-20 13:30 | 192 | 192
2017-09-20 14:00 | 199 | 199
2017-09-20 14:30 | 204 | 204
2017-09-20 15:00 | 212 | 212
2017-09-20 15:30 | 220 | 220
2017-09-20 16:00 | 231 | 230
2017-09-20 16:30 | 240 | 240
2017-09-20 17:00 | 251 | 251
2017-09-20 17:30 | 257 | 257
2017-09-20 18:00 | 262 | 262
2017-09-20 18:30 | 269 | 269
2017-09-20 19:00 | 271 | 271
2017-09-20 19:30 | 263 | 263
2017-09-20 20:00 | 259 | 259
2017-09-20 20:30 | 256 | 256
2017-09-20 21:00 | 245 | 244
2017-09-20 21:30 | 235 | 235
2017-09-20 22:00 | 226 | 226
2017-09-20 22:30 | 221 | 221
2017-09-20 23:00 | 219 | 219
2017-09-20 23:30 | 205 | 205
2017-09-21 | 188 | 188
2017-09-21 00:30 | 172 | 172
2017-09-21 01:00 | 163 | 163
2017-09-21 01:30 | 156 | 156
2017-09-21 02:00 | 152 | 152
2017-09-21 02:30 | 150 | 149
2017-09-21 03:00 | 148 | 147
2017-09-21 03:30 | 148 | 147
2017-09-21 04:00 | 148 | 148
2017-09-21 04:30 | 152 | 152
2017-09-21 05:00 | 160 | 160
2017-09-21 05:30 | 173 | 173
2017-09-21 06:00 | 182 | 182
2017-09-21 06:30 | 196 | 196
2017-09-21 07:00 | 206 | 205
2017-09-21 07:30 | 214 | 214
2017-09-21 08:00 | 212 | 212
2017-09-21 08:30 | 209 | 208
2017-09-21 09:00 | 211 | 211
2017-09-21 09:30 | 220 | 219
2017-09-21 10:00 | 215 | 214
2017-09-21 10:30 | 208 | 207
2017-09-21 11:00 | 203 | 202
2017-09-21 11:30 | 199 | 198
2017-09-21 12:00 | 199 | 199
2017-09-21 12:30 | 200 | 200
2017-09-21 13:00 | 200 | 200
2017-09-21 13:30 | 202 | 202
2017-09-21 14:00 | 205 | 204
2017-09-21 14:30 | 209 | 208
2017-09-21 15:00 | 216 | 215
2017-09-21 15:30 | 222 | 222
2017-09-21 16:00 | 232 | 231
2017-09-21 16:30 | 241 | 241
2017-09-21 17:00 | 251 | 251
2017-09-21 17:30 | 257 | 256
2017-09-21 18:00 | 264 | 264
2017-09-21 18:30 | 273 | 272
2017-09-21 19:00 | 273 | 273
2017-09-21 19:30 | 266 | 266
2017-09-21 20:00 | 264 | 263
2017-09-21 20:30 | 261 | 260
2017-09-21 21:00 | 250 | 250
2017-09-21 21:30 | 238 | 237
2017-09-21 22:00 | 227 | 227
2017-09-21 22:30 | 222 | 222
2017-09-21 23:00 | 221 | 221
2017-09-21 23:30 | 206 | 205
2017-09-22 | 189 | 189
2017-09-22 00:30 | 174 | 174
2017-09-22 01:00 | 165 | 165
2017-09-22 01:30 | 159 | 159
2017-09-22 02:00 | 153 | 153
2017-09-22 02:30 | 151 | 151
2017-09-22 03:00 | 150 | 150
2017-09-22 03:30 | 151 | 151
2017-09-22 04:00 | 151 | 151
2017-09-22 04:30 | 154 | 154
2017-09-22 05:00 | 160 | 160
2017-09-22 05:30 | 173 | 172
2017-09-22 06:00 | 181 | 181
2017-09-22 06:30 | 196 | 195
2017-09-22 07:00 | 207 | 205
2017-09-22 07:30 | 216 | 215
2017-09-22 08:00 | 217 | 217
2017-09-22 08:30 | 216 | 215
2017-09-22 09:00 | 215 | 214
2017-09-22 09:30 | 214 | 213
2017-09-22 10:00 | 207 | 206
2017-09-22 10:30 | 202 | 200
2017-09-22 11:00 | 199 | 198
2017-09-22 11:30 | 199 | 198
2017-09-22 12:00 | 201 | 199
2017-09-22 12:30 | 203 | 201
2017-09-22 13:00 | 206 | 204
2017-09-22 13:30 | 208 | 206
2017-09-22 14:00 | 216 | 213
2017-09-22 14:30 | 224 | 222
2017-09-22 15:00 | 234 | 233
2017-09-22 15:30 | 249 | 249
2017-09-22 16:00 | 259 | 259
2017-09-22 16:30 | 259 | 259
2017-09-22 17:00 | 259 | 259
2017-09-22 17:30 | 256 | 256
2017-09-22 18:00 | 258 | 258
2017-09-22 18:30 | 260 | 260
2017-09-22 19:00 | 262 | 262
2017-09-22 19:30 | 254 | 254
2017-09-22 20:00 | 249 | 249
2017-09-22 20:30 | 243 | 242
2017-09-22 21:00 | 230 | 230
2017-09-22 21:30 | 220 | 220
2017-09-22 22:00 | 213 | 213
2017-09-22 22:30 | 211 | 211
2017-09-22 23:00 | 210 | 210
2017-09-22 23:30 | 199 | 199
2017-09-23 | 183 | 183
2017-09-23 00:30 | 167 | 167
2017-09-23 01:00 | 159 | 159
2017-09-23 01:30 | 153 | 153
2017-09-23 02:00 | 147 | 147
2017-09-23 02:30 | 145 | 145
2017-09-23 03:00 | 142 | 142
2017-09-23 03:30 | 141 | 141
2017-09-23 04:00 | 141 | 141
2017-09-23 04:30 | 141 | 141
2017-09-23 05:00 | 143 | 143
2017-09-23 05:30 | 148 | 148
2017-09-23 06:00 | 150 | 150
2017-09-23 06:30 | 155 | 155
2017-09-23 07:00 | 157 | 157
2017-09-23 07:30 | 160 | 160
2017-09-23 08:00 | 163 | 162
2017-09-23 08:30 | 165 | 164
2017-09-23 09:00 | 165 | 164
2017-09-23 09:30 | 163 | 161
2017-09-23 10:00 | 159 | 158
2017-09-23 10:30 | 155 | 154
2017-09-23 11:00 | 151 | 151
2017-09-23 11:30 | 151 | 150
2017-09-23 12:00 | 151 | 150
2017-09-23 12:30 | 152 | 151
2017-09-23 13:00 | 156 | 155
2017-09-23 13:30 | 161 | 160
2017-09-23 14:00 | 168 | 167
2017-09-23 14:30 | 174 | 173
2017-09-23 15:00 | 181 | 180
2017-09-23 15:30 | 191 | 190
2017-09-23 16:00 | 201 | 200
2017-09-23 16:30 | 211 | 210
2017-09-23 17:00 | 221 | 220
2017-09-23 17:30 | 222 | 221
2017-09-23 18:00 | 227 | 225
2017-09-23 18:30 | 238 | 237
2017-09-23 19:00 | 240 | 238
2017-09-23 19:30 | 233 | 232
2017-09-23 20:00 | 231 | 230
2017-09-23 20:30 | 228 | 227
2017-09-23 21:00 | 219 | 218
2017-09-23 21:30 | 209 | 209
2017-09-23 22:00 | 205 | 204
2017-09-23 22:30 | 204 | 203
2017-09-23 23:00 | 203 | 203
2017-09-23 23:30 | 192 | 192
2017-09-24 | 177 | 177
2017-09-24 00:30 | 163 | 163
2017-09-24 01:00 | 153 | 153
2017-09-24 01:30 | 147 | 147
2017-09-24 02:00 | 142 | 142
2017-09-24 02:30 | 140 | 140
2017-09-24 03:00 | 137 | 137
2017-09-24 03:30 | 136 | 136
2017-09-24 04:00 | 136 | 136
2017-09-24 04:30 | 135 | 135
2017-09-24 05:00 | 136 | 136
2017-09-24 05:30 | 138 | 138
2017-09-24 06:00 | 139 | 138
2017-09-24 06:30 | 142 | 141
2017-09-24 07:00 | 141 | 141
2017-09-24 07:30 | 144 | 143
2017-09-24 08:00 | 144 | 143
2017-09-24 08:30 | 145 | 144
2017-09-24 09:00 | 146 | 144
2017-09-24 09:30 | 148 | 146
2017-09-24 10:00 | 147 | 144
2017-09-24 10:30 | 147 | 144
2017-09-24 11:00 | 146 | 142
2017-09-24 11:30 | 146 | 142
2017-09-24 12:00 | 149 | 144
2017-09-24 12:30 | 153 | 148
2017-09-24 13:00 | 155 | 150
2017-09-24 13:30 | 161 | 155
2017-09-24 14:00 | 163 | 160
2017-09-24 14:30 | 170 | 167
2017-09-24 15:00 | 180 | 177
2017-09-24 15:30 | 191 | 191
2017-09-24 16:00 | 201 | 201
2017-09-24 16:30 | 212 | 212
2017-09-24 17:00 | 225 | 225
2017-09-24 17:30 | 228 | 228
2017-09-24 18:00 | 236 | 236
2017-09-24 18:30 | 248 | 248
2017-09-24 19:00 | 248 | 248
2017-09-24 19:30 | 241 | 241
2017-09-24 20:00 | 237 | 237
2017-09-24 20:30 | 231 | 231
2017-09-24 21:00 | 220 | 220
2017-09-24 21:30 | 211 | 211
2017-09-24 22:00 | 204 | 204
2017-09-24 22:30 | 200 | 200
2017-09-24 23:00 | 200 | 199
2017-09-24 23:30 | 188 | 188
2017-09-25 | 172 | 172
2017-09-25 00:30 | 158 | 158
2017-09-25 01:00 | 151 | 151
2017-09-25 01:30 | 147 | 147
2017-09-25 02:00 | 145 | 145
2017-09-25 02:30 | 143 | 143
2017-09-25 03:00 | 143 | 143
2017-09-25 03:30 | 144 | 144
2017-09-25 04:00 | 144 | 144
2017-09-25 04:30 | 147 | 147
2017-09-25 05:00 | 155 | 154
2017-09-25 05:30 | 167 | 167
2017-09-25 06:00 | 177 | 176
2017-09-25 06:30 | 193 | 192
2017-09-25 07:00 | 205 | 204
2017-09-25 07:30 | 218 | 217
2017-09-25 08:00 | 221 | 219
2017-09-25 08:30 | 221 | 220
2017-09-25 09:00 | 221 | 221
2017-09-25 09:30 | 219 | 219
2017-09-25 10:00 | 217 | 216
2017-09-25 10:30 | 215 | 215
2017-09-25 11:00 | 216 | 215
2017-09-25 11:30 | 220 | 219
2017-09-25 12:00 | 225 | 224
2017-09-25 12:30 | 230 | 229
2017-09-25 13:00 | 237 | 235
2017-09-25 13:30 | 245 | 244
2017-09-25 14:00 | 252 | 251
2017-09-25 14:30 | 260 | 258
2017-09-25 15:00 | 269 | 267
2017-09-25 15:30 | 277 | 275
2017-09-25 16:00 | 284 | 282
2017-09-25 16:30 | 292 | 290
2017-09-25 17:00 | 296 | 295
2017-09-25 17:30 | 295 | 294
2017-09-25 18:00 | 294 | 292
2017-09-25 18:30 | 296 | 295
2017-09-25 19:00 | 297 | 297
2017-09-25 19:30 | 288 | 288
2017-09-25 20:00 | 283 | 282
2017-09-25 20:30 | 275 | 275
2017-09-25 21:00 | 259 | 259
2017-09-25 21:30 | 247 | 247
2017-09-25 22:00 | 234 | 233
2017-09-25 22:30 | 227 | 226
2017-09-25 23:00 | 224 | 222
2017-09-25 23:30 | 209 | 208
2017-09-26 | 192 | 191
2017-09-26 00:30 | 176 | 176
2017-09-26 01:00 | 166 | 166
2017-09-26 01:30 | 161 | 160
2017-09-26 02:00 | 156 | 156
2017-09-26 02:30 | 155 | 155
2017-09-26 03:00 | 153 | 153
2017-09-26 03:30 | 153 | 153
2017-09-26 04:00 | 155 | 155
2017-09-26 04:30 | 159 | 158
2017-09-26 05:00 | 166 | 166
2017-09-26 05:30 | 178 | 177
2017-09-26 06:00 | 186 | 185
2017-09-26 06:30 | 202 | 200
2017-09-26 07:00 | 213 | 212
2017-09-26 07:30 | 223 | 223
2017-09-26 08:00 | 226 | 226
2017-09-26 08:30 | 228 | 228
2017-09-26 09:00 | 229 | 229
2017-09-26 09:30 | 230 | 230
2017-09-26 10:00 | 244 | 244
2017-09-26 10:30 | 255 | 255
2017-09-26 11:00 | 255 | 255
2017-09-26 11:30 | 228 | 228
2017-09-26 12:00 | 236 | 236
2017-09-26 12:30 | 222 | 222
2017-09-26 13:00 | 214 | 214
2017-09-26 13:30 | 223 | 223
2017-09-26 14:00 | 229 | 229
2017-09-26 14:30 | 235 | 235
2017-09-26 15:00 | 240 | 239
2017-09-26 15:30 | 250 | 250
2017-09-26 16:00 | 258 | 258
2017-09-26 16:30 | 265 | 265
2017-09-26 17:00 | 273 | 273
2017-09-26 17:30 | 276 | 276
2017-09-26 18:00 | 278 | 278
2017-09-26 18:30 | 286 | 286
2017-09-26 19:00 | 287 | 287
2017-09-26 19:30 | 277 | 277
2017-09-26 20:00 | 272 | 272
2017-09-26 20:30 | 267 | 267
2017-09-26 21:00 | 252 | 251
2017-09-26 21:30 | 242 | 241
2017-09-26 22:00 | 233 | 232
2017-09-26 22:30 | 226 | 226
2017-09-26 23:00 | 223 | 223
2017-09-26 23:30 | 211 | 210
2017-09-27 | 193 | 193
2017-09-27 00:30 | 178 | 178
2017-09-27 01:00 | 170 | 169
2017-09-27 01:30 | 163 | 163
2017-09-27 02:00 | 159 | 159
2017-09-27 02:30 | 157 | 157
2017-09-27 03:00 | 156 | 156
2017-09-27 03:30 | 156 | 156
2017-09-27 04:00 | 156 | 156
2017-09-27 04:30 | 159 | 159
2017-09-27 05:00 | 166 | 166
2017-09-27 05:30 | 179 | 179
2017-09-27 06:00 | 188 | 188
2017-09-27 06:30 | 208 | 207
2017-09-27 07:00 | 225 | 224
2017-09-27 07:30 | 234 | 234
2017-09-27 08:00 | 237 | 237
2017-09-27 08:30 | 241 | 241
2017-09-27 09:00 | 250 | 250
2017-09-27 09:30 | 251 | 250
2017-09-27 10:00 | 251 | 251
2017-09-27 10:30 | 243 | 243
2017-09-27 11:00 | 250 | 249
2017-09-27 11:30 | 253 | 253
2017-09-27 12:00 | 258 | 258
2017-09-27 12:30 | 256 | 255
2017-09-27 13:00 | 254 | 254
2017-09-27 13:30 | 256 | 256
2017-09-27 14:00 | 258 | 258
2017-09-27 14:30 | 262 | 262
2017-09-27 15:00 | 262 | 262
2017-09-27 15:30 | 261 | 261
2017-09-27 16:00 | 262 | 262
2017-09-27 16:30 | 267 | 267
2017-09-27 17:00 | 274 | 274
2017-09-27 17:30 | 277 | 277
2017-09-27 18:00 | 280 | 280
2017-09-27 18:30 | 284 | 284
2017-09-27 19:00 | 286 | 285
2017-09-27 19:30 | 278 | 278
2017-09-27 20:00 | 275 | 274
2017-09-27 20:30 | 270 | 269
2017-09-27 21:00 | 255 | 255
2017-09-27 21:30 | 244 | 243
2017-09-27 22:00 | 235 | 235
2017-09-27 22:30 | 231 | 231
2017-09-27 23:00 | 228 | 228
2017-09-27 23:30 | 216 | 216
2017-09-28 | 199 | 199
2017-09-28 00:30 | 183 | 183
2017-09-28 01:00 | 174 | 174
2017-09-28 01:30 | 168 | 168
2017-09-28 02:00 | 165 | 164
2017-09-28 02:30 | 160 | 159
2017-09-28 03:00 | 157 | 157
2017-09-28 03:30 | 159 | 159
2017-09-28 04:00 | 159 | 159
2017-09-28 04:30 | 162 | 162
2017-09-28 05:00 | 170 | 170
2017-09-28 05:30 | 180 | 180
2017-09-28 06:00 | 190 | 190
2017-09-28 06:30 | 206 | 205
2017-09-28 07:00 | 216 | 215
2017-09-28 07:30 | 225 | 224
2017-09-28 08:00 | 227 | 225
2017-09-28 08:30 | 227 | 225
2017-09-28 09:00 | 226 | 222
2017-09-28 09:30 | 223 | 219
2017-09-28 10:00 | 222 | 218
2017-09-28 10:30 | 223 | 220
2017-09-28 11:00 | 223 | 222
2017-09-28 11:30 | 226 | 225
2017-09-28 12:00 | 231 | 230
2017-09-28 12:30 | 241 | 238
2017-09-28 13:00 | 250 | 247
2017-09-28 13:30 | 259 | 259
2017-09-28 14:00 | 269 | 269
2017-09-28 14:30 | 279 | 279
2017-09-28 15:00 | 290 | 289
2017-09-28 15:30 | 302 | 302
2017-09-28 16:00 | 314 | 314
2017-09-28 16:30 | 323 | 323
2017-09-28 17:00 | 329 | 329
2017-09-28 17:30 | 324 | 324
2017-09-28 18:00 | 322 | 322
2017-09-28 18:30 | 326 | 326
2017-09-28 19:00 | 328 | 328
2017-09-28 19:30 | 318 | 318
2017-09-28 20:00 | 312 | 312
2017-09-28 20:30 | 302 | 302
2017-09-28 21:00 | 284 | 284
2017-09-28 21:30 | 268 | 268
2017-09-28 22:00 | 256 | 256
2017-09-28 22:30 | 246 | 246
2017-09-28 23:00 | 242 | 242
2017-09-28 23:30 | 224 | 224
2017-09-29 | 204 | 204
2017-09-29 00:30 | 188 | 188
2017-09-29 01:00 | 179 | 179
2017-09-29 01:30 | 171 | 171
2017-09-29 02:00 | 167 | 167
2017-09-29 02:30 | 165 | 165
2017-09-29 03:00 | 164 | 164
2017-09-29 03:30 | 164 | 164
2017-09-29 04:00 | 163 | 163
2017-09-29 04:30 | 167 | 167
2017-09-29 05:00 | 172 | 172
2017-09-29 05:30 | 182 | 182
2017-09-29 06:00 | 191 | 191
2017-09-29 06:30 | 206 | 205
2017-09-29 07:00 | 215 | 214
2017-09-29 07:30 | 226 | 225
2017-09-29 08:00 | 231 | 230
2017-09-29 08:30 | 234 | 234
2017-09-29 09:00 | 236 | 235
2017-09-29 09:30 | 238 | 237
2017-09-29 10:00 | 237 | 236
2017-09-29 10:30 | 240 | 239
2017-09-29 11:00 | 245 | 244
2017-09-29 11:30 | 247 | 246
2017-09-29 12:00 | 252 | 251
2017-09-29 12:30 | 258 | 257
2017-09-29 13:00 | 268 | 267
2017-09-29 13:30 | 277 | 276
2017-09-29 14:00 | 291 | 290
2017-09-29 14:30 | 306 | 305
2017-09-29 15:00 | 311 | 310
2017-09-29 15:30 | 318 | 317
2017-09-29 16:00 | 324 | 323
2017-09-29 16:30 | 327 | 326
2017-09-29 17:00 | 326 | 324
2017-09-29 17:30 | 317 | 316
2017-09-29 18:00 | 303 | 303
2017-09-29 18:30 | 303 | 303
2017-09-29 19:00 | 303 | 302
2017-09-29 19:30 | 292 | 291
2017-09-29 20:00 | 286 | 286
2017-09-29 20:30 | 279 | 279
2017-09-29 21:00 | 266 | 266
2017-09-29 21:30 | 254 | 253
2017-09-29 22:00 | 242 | 242
2017-09-29 22:30 | 237 | 236
2017-09-29 23:00 | 234 | 233
2017-09-29 23:30 | 217 | 216
2017-09-30 | 197 | 197
2017-09-30 00:30 | 182 | 182
2017-09-30 01:00 | 174 | 174
2017-09-30 01:30 | 167 | 167
2017-09-30 02:00 | 162 | 162
2017-09-30 02:30 | 158 | 158
2017-09-30 03:00 | 158 | 157
2017-09-30 03:30 | 156 | 156
2017-09-30 04:00 | 154 | 154
2017-09-30 04:30 | 152 | 152
2017-09-30 05:00 | 154 | 154
2017-09-30 05:30 | 157 | 157
2017-09-30 06:00 | 158 | 158
2017-09-30 06:30 | 163 | 162
2017-09-30 07:00 | 164 | 164
2017-09-30 07:30 | 168 | 168
2017-09-30 08:00 | 170 | 170
2017-09-30 08:30 | 175 | 174
2017-09-30 09:00 | 178 | 177
2017-09-30 09:30 | 188 | 187
2017-09-30 10:00 | 180 | 178
2017-09-30 10:30 | 184 | 182
2017-09-30 11:00 | 183 | 181
2017-09-30 11:30 | 179 | 177
2017-09-30 12:00 | 180 | 178
2017-09-30 12:30 | 184 | 182
2017-09-30 13:00 | 191 | 188
2017-09-30 13:30 | 198 | 195
2017-09-30 14:00 | 209 | 205
2017-09-30 14:30 | 217 | 214
2017-09-30 15:00 | 227 | 223
2017-09-30 15:30 | 233 | 233
2017-09-30 16:00 | 239 | 239
2017-09-30 16:30 | 241 | 241
2017-09-30 17:00 | 243 | 243
2017-09-30 17:30 | 237 | 237
2017-09-30 18:00 | 237 | 237
2017-09-30 18:30 | 244 | 244
2017-09-30 19:00 | 245 | 245
2017-09-30 19:30 | 237 | 237
2017-09-30 20:00 | 232 | 232
2017-09-30 20:30 | 229 | 228
2017-09-30 21:00 | 220 | 219
2017-09-30 21:30 | 214 | 213
2017-09-30 22:00 | 208 | 207
2017-09-30 22:30 | 206 | 205
2017-09-30 23:00 | 206 | 206
2017-09-30 23:30 | 193 | 193
2017-10-01 | 179 | 179
2017-10-01 00:30 | 165 | 165
2017-10-01 01:00 | 157 | 157
2017-10-01 01:30 | 152 | 152
2017-10-01 02:00 | 147 | 147
2017-10-01 02:30 | 145 | 145
2017-10-01 03:00 | 144 | 143
2017-10-01 03:30 | 143 | 143
2017-10-01 04:00 | 142 | 142
2017-10-01 04:30 | 141 | 141
2017-10-01 05:00 | 142 | 142
2017-10-01 05:30 | 144 | 144
2017-10-01 06:00 | 146 | 146
2017-10-01 06:30 | 151 | 150
2017-10-01 07:00 | 155 | 155
2017-10-01 07:30 | 163 | 163
2017-10-01 08:00 | 169 | 169
2017-10-01 08:30 | 176 | 176
2017-10-01 09:00 | 174 | 174
2017-10-01 09:30 | 169 | 169
2017-10-01 10:00 | 167 | 167
2017-10-01 10:30 | 175 | 175
2017-10-01 11:00 | 186 | 186
2017-10-01 11:30 | 191 | 190
2017-10-01 12:00 | 192 | 192
2017-10-01 12:30 | 193 | 192
2017-10-01 13:00 | 188 | 188
2017-10-01 13:30 | 182 | 182
2017-10-01 14:00 | 184 | 184
2017-10-01 14:30 | 187 | 186
2017-10-01 15:00 | 193 | 193
2017-10-01 15:30 | 199 | 198
2017-10-01 16:00 | 201 | 201
2017-10-01 16:30 | 206 | 206
2017-10-01 17:00 | 215 | 214
2017-10-01 17:30 | 220 | 219
2017-10-01 18:00 | 223 | 222
2017-10-01 18:30 | 224 | 223
2017-10-01 19:00 | 221 | 220
2017-10-01 19:30 | 213 | 213
2017-10-01 20:00 | 213 | 213
2017-10-01 20:30 | 210 | 210
2017-10-01 21:00 | 201 | 201
2017-10-01 21:30 | 196 | 196
2017-10-01 22:00 | 193 | 193
2017-10-01 22:30 | 192 | 192
2017-10-01 23:00 | 194 | 194
2017-10-01 23:30 | 185 | 185
2017-10-02 | 171 | 171
2017-10-02 00:30 | 158 | 158
2017-10-02 01:00 | 151 | 151
2017-10-02 01:30 | 146 | 146
2017-10-02 02:00 | 141 | 141
2017-10-02 02:30 | 138 | 138
2017-10-02 03:00 | 138 | 138
2017-10-02 03:30 | 137 | 137
2017-10-02 04:00 | 135 | 135
2017-10-02 04:30 | 136 | 136
2017-10-02 05:00 | 136 | 136
2017-10-02 05:30 | 142 | 142
2017-10-02 06:00 | 144 | 144
2017-10-02 06:30 | 150 | 150
2017-10-02 07:00 | 156 | 156
2017-10-02 07:30 | 166 | 166
2017-10-02 08:00 | 181 | 180
2017-10-02 08:30 | 194 | 193
2017-10-02 09:00 | 199 | 198
2017-10-02 09:30 | 203 | 202
2017-10-02 10:00 | 208 | 208
2017-10-02 10:30 | 208 | 208
2017-10-02 11:00 | 206 | 205
2017-10-02 11:30 | 203 | 202
2017-10-02 12:00 | 205 | 205
2017-10-02 12:30 | 201 | 200
2017-10-02 13:00 | 200 | 200
2017-10-02 13:30 | 197 | 197
2017-10-02 14:00 | 200 | 199
2017-10-02 14:30 | 203 | 203
2017-10-02 15:00 | 204 | 204
2017-10-02 15:30 | 210 | 209
2017-10-02 16:00 | 219 | 218
2017-10-02 16:30 | 226 | 225
2017-10-02 17:00 | 236 | 235
2017-10-02 17:30 | 241 | 240
2017-10-02 18:00 | 245 | 243
2017-10-02 18:30 | 248 | 248
2017-10-02 19:00 | 246 | 246
2017-10-02 19:30 | 238 | 238
2017-10-02 20:00 | 236 | 236
2017-10-02 20:30 | 233 | 233
2017-10-02 21:00 | 222 | 222
2017-10-02 21:30 | 214 | 214
2017-10-02 22:00 | 206 | 206
2017-10-02 22:30 | 201 | 201
2017-10-02 23:00 | 199 | 199
2017-10-02 23:30 | 189 | 189
2017-10-03 | 174 | 174
2017-10-03 00:30 | 162 | 162
2017-10-03 01:00 | 154 | 153
2017-10-03 01:30 | 147 | 147
2017-10-03 02:00 | 142 | 142
2017-10-03 02:30 | 140 | 140
2017-10-03 03:00 | 139 | 139
2017-10-03 03:30 | 139 | 139
2017-10-03 04:00 | 139 | 139
2017-10-03 04:30 | 144 | 144
2017-10-03 05:00 | 152 | 152
2017-10-03 05:30 | 167 | 166
2017-10-03 06:00 | 180 | 180
2017-10-03 06:30 | 205 | 203
2017-10-03 07:00 | 224 | 222
2017-10-03 07:30 | 238 | 237
2017-10-03 08:00 | 243 | 241
2017-10-03 08:30 | 240 | 238
2017-10-03 09:00 | 230 | 228
2017-10-03 09:30 | 223 | 222
2017-10-03 10:00 | 223 | 221
2017-10-03 10:30 | 219 | 217
2017-10-03 11:00 | 211 | 208
2017-10-03 11:30 | 208 | 205
2017-10-03 12:00 | 208 | 205
2017-10-03 12:30 | 211 | 208
2017-10-03 13:00 | 207 | 205
2017-10-03 13:30 | 205 | 204
2017-10-03 14:00 | 209 | 208
2017-10-03 14:30 | 216 | 215
2017-10-03 15:00 | 228 | 227
2017-10-03 15:30 | 239 | 239
2017-10-03 16:00 | 249 | 249
2017-10-03 16:30 | 256 | 256
2017-10-03 17:00 | 265 | 265
2017-10-03 17:30 | 269 | 269
2017-10-03 18:00 | 274 | 274
2017-10-03 18:30 | 279 | 279
2017-10-03 19:00 | 280 | 280
2017-10-03 19:30 | 271 | 271
2017-10-03 20:00 | 267 | 266
2017-10-03 20:30 | 261 | 260
2017-10-03 21:00 | 247 | 246
2017-10-03 21:30 | 237 | 236
2017-10-03 22:00 | 227 | 226
2017-10-03 22:30 | 221 | 220
2017-10-03 23:00 | 218 | 217
2017-10-03 23:30 | 205 | 204
2017-10-04 | 188 | 187
2017-10-04 00:30 | 173 | 172
2017-10-04 01:00 | 164 | 164
2017-10-04 01:30 | 159 | 158
2017-10-04 02:00 | 154 | 154
2017-10-04 02:30 | 152 | 152
2017-10-04 03:00 | 151 | 151
2017-10-04 03:30 | 150 | 150
2017-10-04 04:00 | 147 | 147
2017-10-04 04:30 | 153 | 153
2017-10-04 05:00 | 161 | 161
2017-10-04 05:30 | 173 | 173
2017-10-04 06:00 | 186 | 186
2017-10-04 06:30 | 207 | 206
2017-10-04 07:00 | 225 | 225
2017-10-04 07:30 | 238 | 238
2017-10-04 08:00 | 237 | 237
2017-10-04 08:30 | 231 | 231
2017-10-04 09:00 | 226 | 226
2017-10-04 09:30 | 224 | 224
2017-10-04 10:00 | 227 | 227
2017-10-04 10:30 | 239 | 239
2017-10-04 11:00 | 246 | 246
2017-10-04 11:30 | 237 | 236
2017-10-04 12:00 | 225 | 224
2017-10-04 12:30 | 223 | 222
2017-10-04 13:00 | 223 | 222
2017-10-04 13:30 | 227 | 226
2017-10-04 14:00 | 230 | 229
2017-10-04 14:30 | 235 | 234
2017-10-04 15:00 | 240 | 239
2017-10-04 15:30 | 245 | 245
2017-10-04 16:00 | 255 | 255
2017-10-04 16:30 | 264 | 264
2017-10-04 17:00 | 272 | 272
2017-10-04 17:30 | 274 | 274
2017-10-04 18:00 | 276 | 276
2017-10-04 18:30 | 285 | 285
2017-10-04 19:00 | 289 | 289
2017-10-04 19:30 | 280 | 280
2017-10-04 20:00 | 274 | 274
2017-10-04 20:30 | 269 | 269
2017-10-04 21:00 | 256 | 256
2017-10-04 21:30 | 246 | 246
2017-10-04 22:00 | 234 | 233
2017-10-04 22:30 | 227 | 225
2017-10-04 23:00 | 223 | 221
2017-10-04 23:30 | 210 | 208
2017-10-05 | 192 | 191
2017-10-05 00:30 | 176 | 176
2017-10-05 01:00 | 166 | 166
2017-10-05 01:30 | 160 | 160
2017-10-05 02:00 | 156 | 156
2017-10-05 02:30 | 153 | 153
2017-10-05 03:00 | 152 | 152
2017-10-05 03:30 | 152 | 152
2017-10-05 04:00 | 152 | 152
2017-10-05 04:30 | 156 | 156
2017-10-05 05:00 | 163 | 163
2017-10-05 05:30 | 175 | 175
2017-10-05 06:00 | 187 | 186
2017-10-05 06:30 | 204 | 203
2017-10-05 07:00 | 218 | 216
2017-10-05 07:30 | 224 | 224
2017-10-05 08:00 | 221 | 221
2017-10-05 08:30 | 217 | 217
2017-10-05 09:00 | 212 | 212
2017-10-05 09:30 | 216 | 215
2017-10-05 10:00 | 216 | 216
2017-10-05 10:30 | 216 | 215
2017-10-05 11:00 | 216 | 216
2017-10-05 11:30 | 215 | 214
2017-10-05 12:00 | 218 | 218
2017-10-05 12:30 | 220 | 219
2017-10-05 13:00 | 225 | 225
2017-10-05 13:30 | 234 | 234
2017-10-05 14:00 | 243 | 243
2017-10-05 14:30 | 251 | 250
2017-10-05 15:00 | 257 | 256
2017-10-05 15:30 | 263 | 263
2017-10-05 16:00 | 273 | 273
2017-10-05 16:30 | 281 | 281
2017-10-05 17:00 | 288 | 288
2017-10-05 17:30 | 288 | 288
2017-10-05 18:00 | 290 | 290
2017-10-05 18:30 | 297 | 296
2017-10-05 19:00 | 299 | 299
2017-10-05 19:30 | 291 | 291
2017-10-05 20:00 | 287 | 287
2017-10-05 20:30 | 282 | 282
2017-10-05 21:00 | 268 | 268
2017-10-05 21:30 | 255 | 255
2017-10-05 22:00 | 241 | 241
2017-10-05 22:30 | 235 | 234
2017-10-05 23:00 | 230 | 228
2017-10-05 23:30 | 216 | 214
2017-10-06 | 197 | 195
2017-10-06 00:30 | 181 | 180
2017-10-06 01:00 | 172 | 172
2017-10-06 01:30 | 165 | 165
2017-10-06 02:00 | 162 | 161
2017-10-06 02:30 | 160 | 159
2017-10-06 03:00 | 157 | 157
2017-10-06 03:30 | 157 | 157
2017-10-06 04:00 | 157 | 157
2017-10-06 04:30 | 160 | 160
2017-10-06 05:00 | 167 | 166
2017-10-06 05:30 | 179 | 178
2017-10-06 06:00 | 190 | 189
2017-10-06 06:30 | 208 | 206
2017-10-06 07:00 | 221 | 219
2017-10-06 07:30 | 231 | 230
2017-10-06 08:00 | 233 | 233
2017-10-06 08:30 | 231 | 231
2017-10-06 09:00 | 229 | 229
2017-10-06 09:30 | 231 | 231
2017-10-06 10:00 | 237 | 237
2017-10-06 10:30 | 236 | 235
2017-10-06 11:00 | 234 | 234
2017-10-06 11:30 | 234 | 234
2017-10-06 12:00 | 239 | 239
2017-10-06 12:30 | 245 | 245
2017-10-06 13:00 | 252 | 252
2017-10-06 13:30 | 262 | 262
2017-10-06 14:00 | 275 | 275
2017-10-06 14:30 | 300 | 300
2017-10-06 15:00 | 310 | 310
2017-10-06 15:30 | 292 | 292
2017-10-06 16:00 | 276 | 276
2017-10-06 16:30 | 271 | 271
2017-10-06 17:00 | 271 | 271
2017-10-06 17:30 | 276 | 276
2017-10-06 18:00 | 278 | 278
2017-10-06 18:30 | 281 | 281
2017-10-06 19:00 | 283 | 282
2017-10-06 19:30 | 274 | 272
2017-10-06 20:00 | 273 | 272
2017-10-06 20:30 | 268 | 267
2017-10-06 21:00 | 257 | 256
2017-10-06 21:30 | 245 | 245
2017-10-06 22:00 | 236 | 236
2017-10-06 22:30 | 231 | 231
2017-10-06 23:00 | 229 | 229
2017-10-06 23:30 | 214 | 214
2017-10-07 | 196 | 196
2017-10-07 00:30 | 182 | 182
2017-10-07 01:00 | 170 | 170
2017-10-07 01:30 | 165 | 165
2017-10-07 02:00 | 161 | 161
2017-10-07 02:30 | 157 | 157
2017-10-07 03:00 | 154 | 154
2017-10-07 03:30 | 152 | 152
2017-10-07 04:00 | 151 | 151
2017-10-07 04:30 | 151 | 151
2017-10-07 05:00 | 153 | 153
2017-10-07 05:30 | 157 | 157
2017-10-07 06:00 | 159 | 159
2017-10-07 06:30 | 167 | 167
2017-10-07 07:00 | 175 | 175
2017-10-07 07:30 | 187 | 187
2017-10-07 08:00 | 194 | 193
2017-10-07 08:30 | 199 | 198
2017-10-07 09:00 | 207 | 206
2017-10-07 09:30 | 208 | 207
2017-10-07 10:00 | 203 | 202
2017-10-07 10:30 | 198 | 197
2017-10-07 11:00 | 200 | 199
2017-10-07 11:30 | 201 | 200
2017-10-07 12:00 | 203 | 203
2017-10-07 12:30 | 196 | 196
2017-10-07 13:00 | 190 | 190
2017-10-07 13:30 | 197 | 196
2017-10-07 14:00 | 203 | 203
2017-10-07 14:30 | 208 | 208
2017-10-07 15:00 | 205 | 205
2017-10-07 15:30 | 204 | 204
2017-10-07 16:00 | 211 | 210
2017-10-07 16:30 | 213 | 213
2017-10-07 17:00 | 221 | 220
2017-10-07 17:30 | 224 | 223
2017-10-07 18:00 | 225 | 224
2017-10-07 18:30 | 233 | 231
2017-10-07 19:00 | 236 | 235
2017-10-07 19:30 | 229 | 228
2017-10-07 20:00 | 227 | 226
2017-10-07 20:30 | 225 | 223
2017-10-07 21:00 | 214 | 213
2017-10-07 21:30 | 208 | 207
2017-10-07 22:00 | 203 | 202
2017-10-07 22:30 | 201 | 200
2017-10-07 23:00 | 202 | 202
2017-10-07 23:30 | 193 | 192
2017-10-08 | 177 | 177
2017-10-08 00:30 | 164 | 164
2017-10-08 01:00 | 155 | 155
2017-10-08 01:30 | 149 | 149
2017-10-08 02:00 | 145 | 144
2017-10-08 02:30 | 141 | 141
2017-10-08 03:00 | 139 | 139
2017-10-08 03:30 | 138 | 138
2017-10-08 04:00 | 137 | 137
2017-10-08 04:30 | 137 | 137
2017-10-08 05:00 | 138 | 138
2017-10-08 05:30 | 140 | 140
2017-10-08 06:00 | 141 | 140
2017-10-08 06:30 | 145 | 145
2017-10-08 07:00 | 149 | 149
2017-10-08 07:30 | 154 | 154
2017-10-08 08:00 | 152 | 152
2017-10-08 08:30 | 153 | 153
2017-10-08 09:00 | 160 | 159
2017-10-08 09:30 | 169 | 168
2017-10-08 10:00 | 177 | 176
2017-10-08 10:30 | 181 | 180
2017-10-08 11:00 | 185 | 184
2017-10-08 11:30 | 182 | 180
2017-10-08 12:00 | 171 | 170
2017-10-08 12:30 | 171 | 169
2017-10-08 13:00 | 181 | 180
2017-10-08 13:30 | 186 | 185
2017-10-08 14:00 | 195 | 194
2017-10-08 14:30 | 200 | 199
2017-10-08 15:00 | 203 | 202
2017-10-08 15:30 | 203 | 202
2017-10-08 16:00 | 200 | 200
2017-10-08 16:30 | 204 | 203
2017-10-08 17:00 | 215 | 215
2017-10-08 17:30 | 220 | 219
2017-10-08 18:00 | 229 | 228
2017-10-08 18:30 | 247 | 245
2017-10-08 19:00 | 250 | 248
2017-10-08 19:30 | 242 | 241
2017-10-08 20:00 | 238 | 237
2017-10-08 20:30 | 235 | 234
2017-10-08 21:00 | 224 | 223
2017-10-08 21:30 | 215 | 214
2017-10-08 22:00 | 208 | 207
2017-10-08 22:30 | 204 | 203
2017-10-08 23:00 | 202 | 202
2017-10-08 23:30 | 190 | 190
2017-10-09 | 173 | 173
2017-10-09 00:30 | 159 | 159
2017-10-09 01:00 | 153 | 153
2017-10-09 01:30 | 149 | 148
2017-10-09 02:00 | 146 | 146
2017-10-09 02:30 | 144 | 144
2017-10-09 03:00 | 142 | 142
2017-10-09 03:30 | 144 | 144
2017-10-09 04:00 | 144 | 144
2017-10-09 04:30 | 148 | 148
2017-10-09 05:00 | 155 | 155
2017-10-09 05:30 | 167 | 167
2017-10-09 06:00 | 180 | 180
2017-10-09 06:30 | 203 | 203
2017-10-09 07:00 | 224 | 224
2017-10-09 07:30 | 242 | 242
2017-10-09 08:00 | 253 | 252
2017-10-09 08:30 | 256 | 255
2017-10-09 09:00 | 245 | 244
2017-10-09 09:30 | 231 | 230
2017-10-09 10:00 | 225 | 223
2017-10-09 10:30 | 225 | 223
2017-10-09 11:00 | 226 | 224
2017-10-09 11:30 | 225 | 222
2017-10-09 12:00 | 233 | 230
2017-10-09 12:30 | 246 | 243
2017-10-09 13:00 | 256 | 253
2017-10-09 13:30 | 257 | 256
2017-10-09 14:00 | 253 | 252
2017-10-09 14:30 | 265 | 263
2017-10-09 15:00 | 271 | 269
2017-10-09 15:30 | 282 | 281
2017-10-09 16:00 | 306 | 305
2017-10-09 16:30 | 304 | 303
2017-10-09 17:00 | 301 | 300
2017-10-09 17:30 | 302 | 301
2017-10-09 18:00 | 302 | 299
2017-10-09 18:30 | 310 | 308
2017-10-09 19:00 | 314 | 311
2017-10-09 19:30 | 302 | 300
2017-10-09 20:00 | 294 | 293
2017-10-09 20:30 | 287 | 286
2017-10-09 21:00 | 272 | 272
2017-10-09 21:30 | 258 | 258
2017-10-09 22:00 | 243 | 243
2017-10-09 22:30 | 236 | 235
2017-10-09 23:00 | 229 | 228
2017-10-09 23:30 | 215 | 214
2017-10-10 | 198 | 198
2017-10-10 00:30 | 182 | 182
2017-10-10 01:00 | 174 | 174
2017-10-10 01:30 | 169 | 169
2017-10-10 02:00 | 164 | 164
2017-10-10 02:30 | 163 | 163
2017-10-10 03:00 | 161 | 161
2017-10-10 03:30 | 162 | 162
2017-10-10 04:00 | 161 | 161
2017-10-10 04:30 | 165 | 165
2017-10-10 05:00 | 171 | 171
2017-10-10 05:30 | 183 | 182
2017-10-10 06:00 | 193 | 192
2017-10-10 06:30 | 211 | 210
2017-10-10 07:00 | 228 | 228
2017-10-10 07:30 | 243 | 243
2017-10-10 08:00 | 252 | 252
2017-10-10 08:30 | 255 | 255
2017-10-10 09:00 | 258 | 258
2017-10-10 09:30 | 263 | 263
2017-10-10 10:00 | 270 | 269
2017-10-10 10:30 | 274 | 274
2017-10-10 11:00 | 281 | 281
2017-10-10 11:30 | 290 | 289
2017-10-10 12:00 | 292 | 292
2017-10-10 12:30 | 293 | 292
2017-10-10 13:00 | 295 | 295
2017-10-10 13:30 | 294 | 294
2017-10-10 14:00 | 299 | 299
2017-10-10 14:30 | 304 | 304
2017-10-10 15:00 | 306 | 306
2017-10-10 15:30 | 312 | 312
2017-10-10 16:00 | 324 | 323
2017-10-10 16:30 | 330 | 330
2017-10-10 17:00 | 335 | 335
2017-10-10 17:30 | 330 | 330
2017-10-10 18:00 | 328 | 327
2017-10-10 18:30 | 329 | 329
2017-10-10 19:00 | 331 | 331
2017-10-10 19:30 | 321 | 321
2017-10-10 20:00 | 314 | 314
2017-10-10 20:30 | 305 | 305
2017-10-10 21:00 | 290 | 290
2017-10-10 21:30 | 278 | 278
2017-10-10 22:00 | 264 | 264
2017-10-10 22:30 | 253 | 253
2017-10-10 23:00 | 246 | 246
2017-10-10 23:30 | 229 | 228
2017-10-11 | 212 | 212
2017-10-11 00:30 | 196 | 196
2017-10-11 01:00 | 187 | 187
2017-10-11 01:30 | 180 | 180
2017-10-11 02:00 | 175 | 175
2017-10-11 02:30 | 173 | 173
2017-10-11 03:00 | 171 | 171
2017-10-11 03:30 | 169 | 169
2017-10-11 04:00 | 167 | 167
2017-10-11 04:30 | 174 | 174
2017-10-11 05:00 | 182 | 181
2017-10-11 05:30 | 193 | 193
2017-10-11 06:00 | 205 | 204
2017-10-11 06:30 | 225 | 224
2017-10-11 07:00 | 245 | 245
2017-10-11 07:30 | 266 | 266
2017-10-11 08:00 | 273 | 272
2017-10-11 08:30 | 275 | 274
2017-10-11 09:00 | 278 | 278
2017-10-11 09:30 | 280 | 279
2017-10-11 10:00 | 279 | 279
2017-10-11 10:30 | 283 | 282
2017-10-11 11:00 | 281 | 281
2017-10-11 11:30 | 274 | 273
2017-10-11 12:00 | 277 | 276
2017-10-11 12:30 | 275 | 275
2017-10-11 13:00 | 276 | 276
2017-10-11 13:30 | 286 | 286
2017-10-11 14:00 | 284 | 284
2017-10-11 14:30 | 277 | 276
2017-10-11 15:00 | 278 | 278
2017-10-11 15:30 | 281 | 281
2017-10-11 16:00 | 292 | 292
2017-10-11 16:30 | 297 | 297
2017-10-11 17:00 | 311 | 311
2017-10-11 17:30 | 307 | 307
2017-10-11 18:00 | 302 | 302
2017-10-11 18:30 | 307 | 307
2017-10-11 19:00 | 310 | 309
2017-10-11 19:30 | 300 | 300
2017-10-11 20:00 | 295 | 295
2017-10-11 20:30 | 290 | 290
2017-10-11 21:00 | 276 | 276
2017-10-11 21:30 | 264 | 264
2017-10-11 22:00 | 252 | 251
2017-10-11 22:30 | 244 | 244
2017-10-11 23:00 | 241 | 240
2017-10-11 23:30 | 226 | 225
2017-10-12 | 209 | 208
2017-10-12 00:30 | 192 | 191
2017-10-12 01:00 | 181 | 181
2017-10-12 01:30 | 174 | 174
2017-10-12 02:00 | 171 | 170
2017-10-12 02:30 | 169 | 169
2017-10-12 03:00 | 167 | 167
2017-10-12 03:30 | 166 | 166
2017-10-12 04:00 | 166 | 166
2017-10-12 04:30 | 169 | 169
2017-10-12 05:00 | 176 | 176
2017-10-12 05:30 | 190 | 189
2017-10-12 06:00 | 205 | 204
2017-10-12 06:30 | 228 | 226
2017-10-12 07:00 | 243 | 242
2017-10-12 07:30 | 265 | 264
2017-10-12 08:00 | 277 | 276
2017-10-12 08:30 | 278 | 277
2017-10-12 09:00 | 280 | 279
2017-10-12 09:30 | 279 | 278
2017-10-12 10:00 | 276 | 276
2017-10-12 10:30 | 278 | 278
2017-10-12 11:00 | 278 | 278
2017-10-12 11:30 | 275 | 275
2017-10-12 12:00 | 279 | 279
2017-10-12 12:30 | 278 | 278
2017-10-12 13:00 | 278 | 278
2017-10-12 13:30 | 280 | 280
2017-10-12 14:00 | 277 | 277
2017-10-12 14:30 | 277 | 277
2017-10-12 15:00 | 267 | 267
2017-10-12 15:30 | 277 | 276
2017-10-12 16:00 | 283 | 282
2017-10-12 16:30 | 286 | 286
2017-10-12 17:00 | 289 | 289
2017-10-12 17:30 | 289 | 289
2017-10-12 18:00 | 292 | 291
2017-10-12 18:30 | 299 | 298
2017-10-12 19:00 | 303 | 302
2017-10-12 19:30 | 295 | 295
2017-10-12 20:00 | 292 | 292
2017-10-12 20:30 | 286 | 286
2017-10-12 21:00 | 273 | 272
2017-10-12 21:30 | 259 | 259
2017-10-12 22:00 | 245 | 245
2017-10-12 22:30 | 238 | 238
2017-10-12 23:00 | 235 | 235
2017-10-12 23:30 | 219 | 219
2017-10-13 | 201 | 201
2017-10-13 00:30 | 184 | 184
2017-10-13 01:00 | 175 | 175
2017-10-13 01:30 | 167 | 167
2017-10-13 02:00 | 163 | 163
2017-10-13 02:30 | 160 | 160
2017-10-13 03:00 | 160 | 160
2017-10-13 03:30 | 160 | 160
2017-10-13 04:00 | 160 | 160
2017-10-13 04:30 | 165 | 165
2017-10-13 05:00 | 172 | 172
2017-10-13 05:30 | 185 | 185
2017-10-13 06:00 | 198 | 198
2017-10-13 06:30 | 219 | 218
2017-10-13 07:00 | 236 | 236
2017-10-13 07:30 | 248 | 248
2017-10-13 08:00 | 245 | 245
2017-10-13 08:30 | 240 | 240
2017-10-13 09:00 | 233 | 233
2017-10-13 09:30 | 237 | 237
2017-10-13 10:00 | 239 | 239
2017-10-13 10:30 | 243 | 243
2017-10-13 11:00 | 246 | 246
2017-10-13 11:30 | 251 | 251
2017-10-13 12:00 | 259 | 259
2017-10-13 12:30 | 261 | 261
2017-10-13 13:00 | 268 | 268
2017-10-13 13:30 | 273 | 273
2017-10-13 14:00 | 274 | 274
2017-10-13 14:30 | 275 | 275
2017-10-13 15:00 | 277 | 277
2017-10-13 15:30 | 288 | 287
2017-10-13 16:00 | 290 | 290
2017-10-13 16:30 | 295 | 295
2017-10-13 17:00 | 291 | 291
2017-10-13 17:30 | 289 | 289
2017-10-13 18:00 | 285 | 285
2017-10-13 18:30 | 286 | 286
2017-10-13 19:00 | 289 | 289
2017-10-13 19:30 | 280 | 280
2017-10-13 20:00 | 277 | 276
2017-10-13 20:30 | 270 | 269
2017-10-13 21:00 | 257 | 256
2017-10-13 21:30 | 248 | 248
2017-10-13 22:00 | 240 | 240
2017-10-13 22:30 | 235 | 235
2017-10-13 23:00 | 233 | 233
2017-10-13 23:30 | 219 | 219
2017-10-14 | 200 | 200
2017-10-14 00:30 | 186 | 185
2017-10-14 01:00 | 176 | 175
2017-10-14 01:30 | 169 | 169
2017-10-14 02:00 | 163 | 163
2017-10-14 02:30 | 160 | 160
2017-10-14 03:00 | 157 | 157
2017-10-14 03:30 | 156 | 156
2017-10-14 04:00 | 155 | 155
2017-10-14 04:30 | 155 | 155
2017-10-14 05:00 | 157 | 157
2017-10-14 05:30 | 160 | 160
2017-10-14 06:00 | 164 | 164
2017-10-14 06:30 | 172 | 172
2017-10-14 07:00 | 180 | 179
2017-10-14 07:30 | 189 | 188
2017-10-14 08:00 | 193 | 193
2017-10-14 08:30 | 198 | 197
2017-10-14 09:00 | 203 | 202
2017-10-14 09:30 | 201 | 200
2017-10-14 10:00 | 207 | 207
2017-10-14 10:30 | 207 | 207
2017-10-14 11:00 | 207 | 206
2017-10-14 11:30 | 199 | 199
2017-10-14 12:00 | 199 | 199
2017-10-14 12:30 | 209 | 209
2017-10-14 13:00 | 213 | 213
2017-10-14 13:30 | 210 | 210
2017-10-14 14:00 | 208 | 208
2017-10-14 14:30 | 209 | 209
2017-10-14 15:00 | 205 | 205
2017-10-14 15:30 | 207 | 206
2017-10-14 16:00 | 211 | 211
2017-10-14 16:30 | 220 | 220
2017-10-14 17:00 | 228 | 227
2017-10-14 17:30 | 230 | 229
2017-10-14 18:00 | 237 | 236
2017-10-14 18:30 | 244 | 243
2017-10-14 19:00 | 244 | 243
2017-10-14 19:30 | 236 | 236
2017-10-14 20:00 | 235 | 234
2017-10-14 20:30 | 231 | 230
2017-10-14 21:00 | 222 | 221
2017-10-14 21:30 | 214 | 213
2017-10-14 22:00 | 206 | 206
2017-10-14 22:30 | 205 | 204
2017-10-14 23:00 | 205 | 205
2017-10-14 23:30 | 195 | 195
2017-10-15 | 180 | 180
2017-10-15 00:30 | 166 | 166
2017-10-15 01:00 | 159 | 158
2017-10-15 01:30 | 152 | 152
2017-10-15 02:00 | 149 | 148
2017-10-15 02:30 | 145 | 145
2017-10-15 03:00 | 143 | 143
2017-10-15 03:30 | 143 | 142
2017-10-15 04:00 | 143 | 142
2017-10-15 04:30 | 143 | 142
2017-10-15 05:00 | 142 | 142
2017-10-15 05:30 | 143 | 142
2017-10-15 06:00 | 148 | 147
2017-10-15 06:30 | 155 | 155
2017-10-15 07:00 | 162 | 162
2017-10-15 07:30 | 171 | 171
2017-10-15 08:00 | 182 | 182
2017-10-15 08:30 | 193 | 193
2017-10-15 09:00 | 193 | 193
2017-10-15 09:30 | 184 | 184
2017-10-15 10:00 | 180 | 180
2017-10-15 10:30 | 193 | 192
2017-10-15 11:00 | 194 | 193
2017-10-15 11:30 | 196 | 195
2017-10-15 12:00 | 195 | 195
2017-10-15 12:30 | 202 | 202
2017-10-15 13:00 | 199 | 199
2017-10-15 13:30 | 200 | 200
2017-10-15 14:00 | 198 | 198
2017-10-15 14:30 | 203 | 202
2017-10-15 15:00 | 211 | 211
2017-10-15 15:30 | 215 | 215
2017-10-15 16:00 | 217 | 217
2017-10-15 16:30 | 224 | 224
2017-10-15 17:00 | 232 | 232
2017-10-15 17:30 | 236 | 236
2017-10-15 18:00 | 240 | 240
2017-10-15 18:30 | 249 | 249
2017-10-15 19:00 | 250 | 250
2017-10-15 19:30 | 242 | 242
2017-10-15 20:00 | 236 | 236
2017-10-15 20:30 | 234 | 234
2017-10-15 21:00 | 225 | 224
2017-10-15 21:30 | 215 | 215
2017-10-15 22:00 | 210 | 210
2017-10-15 22:30 | 206 | 206
2017-10-15 23:00 | 205 | 204
2017-10-15 23:30 | 195 | 195
2017-10-16 | 180 | 180
2017-10-16 00:30 | 167 | 167
2017-10-16 01:00 | 159 | 159
2017-10-16 01:30 | 153 | 153
2017-10-16 02:00 | 150 | 150
2017-10-16 02:30 | 149 | 148
2017-10-16 03:00 | 148 | 148
2017-10-16 03:30 | 146 | 146
2017-10-16 04:00 | 148 | 147
2017-10-16 04:30 | 151 | 151
2017-10-16 05:00 | 158 | 158
2017-10-16 05:30 | 170 | 170
2017-10-16 06:00 | 186 | 186
2017-10-16 06:30 | 209 | 208
2017-10-16 07:00 | 226 | 226
2017-10-16 07:30 | 241 | 241
2017-10-16 08:00 | 245 | 245
2017-10-16 08:30 | 253 | 253
2017-10-16 09:00 | 252 | 252
2017-10-16 09:30 | 250 | 249
2017-10-16 10:00 | 250 | 250
2017-10-16 10:30 | 253 | 253
2017-10-16 11:00 | 256 | 256
2017-10-16 11:30 | 245 | 245
2017-10-16 12:00 | 245 | 245
2017-10-16 12:30 | 248 | 248
2017-10-16 13:00 | 245 | 245
2017-10-16 13:30 | 249 | 249
2017-10-16 14:00 | 251 | 251
2017-10-16 14:30 | 252 | 252
2017-10-16 15:00 | 254 | 254
2017-10-16 15:30 | 255 | 255
2017-10-16 16:00 | 259 | 259
2017-10-16 16:30 | 265 | 265
2017-10-16 17:00 | 273 | 273
2017-10-16 17:30 | 276 | 276
2017-10-16 18:00 | 280 | 280
2017-10-16 18:30 | 284 | 284
2017-10-16 19:00 | 284 | 284
2017-10-16 19:30 | 274 | 274
2017-10-16 20:00 | 269 | 269
2017-10-16 20:30 | 266 | 266
2017-10-16 21:00 | 252 | 252
2017-10-16 21:30 | 240 | 239
2017-10-16 22:00 | 230 | 230
2017-10-16 22:30 | 225 | 224
2017-10-16 23:00 | 221 | 221
2017-10-16 23:30 | 209 | 209
2017-10-17 | 192 | 192
2017-10-17 00:30 | 177 | 177
2017-10-17 01:00 | 168 | 168
2017-10-17 01:30 | 161 | 161
2017-10-17 02:00 | 158 | 158
2017-10-17 02:30 | 156 | 156
2017-10-17 03:00 | 154 | 154
2017-10-17 03:30 | 155 | 155
2017-10-17 04:00 | 155 | 155
2017-10-17 04:30 | 162 | 162
2017-10-17 05:00 | 169 | 169
2017-10-17 05:30 | 180 | 180
2017-10-17 06:00 | 192 | 192
2017-10-17 06:30 | 214 | 213
2017-10-17 07:00 | 231 | 231
2017-10-17 07:30 | 249 | 249
2017-10-17 08:00 | 251 | 251
2017-10-17 08:30 | 255 | 255
2017-10-17 09:00 | 251 | 251
2017-10-17 09:30 | 252 | 252
2017-10-17 10:00 | 249 | 249
2017-10-17 10:30 | 246 | 246
2017-10-17 11:00 | 247 | 247
2017-10-17 11:30 | 253 | 253
2017-10-17 12:00 | 249 | 249
2017-10-17 12:30 | 253 | 253
2017-10-17 13:00 | 249 | 249
2017-10-17 13:30 | 251 | 251
2017-10-17 14:00 | 252 | 252
2017-10-17 14:30 | 250 | 250
2017-10-17 15:00 | 253 | 252
2017-10-17 15:30 | 253 | 253
2017-10-17 16:00 | 260 | 260
2017-10-17 16:30 | 269 | 269
2017-10-17 17:00 | 276 | 276
2017-10-17 17:30 | 280 | 280
2017-10-17 18:00 | 280 | 280
2017-10-17 18:30 | 285 | 285
2017-10-17 19:00 | 287 | 287
2017-10-17 19:30 | 278 | 278
2017-10-17 20:00 | 274 | 274
2017-10-17 20:30 | 271 | 271
2017-10-17 21:00 | 258 | 258
2017-10-17 21:30 | 246 | 246
2017-10-17 22:00 | 236 | 236
2017-10-17 22:30 | 230 | 230
2017-10-17 23:00 | 227 | 227
2017-10-17 23:30 | 213 | 213
2017-10-18 | 197 | 197
2017-10-18 00:30 | 180 | 180
2017-10-18 01:00 | 170 | 170
2017-10-18 01:30 | 163 | 163
2017-10-18 02:00 | 159 | 159
2017-10-18 02:30 | 158 | 158
2017-10-18 03:00 | 156 | 155
2017-10-18 03:30 | 153 | 152
2017-10-18 04:00 | 155 | 155
2017-10-18 04:30 | 159 | 159
2017-10-18 05:00 | 167 | 167
2017-10-18 05:30 | 180 | 180
2017-10-18 06:00 | 193 | 193
2017-10-18 06:30 | 214 | 213
2017-10-18 07:00 | 232 | 231
2017-10-18 07:30 | 244 | 243
2017-10-18 08:00 | 246 | 245
2017-10-18 08:30 | 243 | 242
2017-10-18 09:00 | 239 | 238
2017-10-18 09:30 | 236 | 234
2017-10-18 10:00 | 226 | 225
2017-10-18 10:30 | 229 | 228
2017-10-18 11:00 | 235 | 235
2017-10-18 11:30 | 231 | 230
2017-10-18 12:00 | 224 | 224
2017-10-18 12:30 | 223 | 223
2017-10-18 13:00 | 226 | 226
2017-10-18 13:30 | 225 | 225
2017-10-18 14:00 | 229 | 229
2017-10-18 14:30 | 230 | 230
2017-10-18 15:00 | 234 | 234
2017-10-18 15:30 | 235 | 235
2017-10-18 16:00 | 251 | 251
2017-10-18 16:30 | 259 | 259
2017-10-18 17:00 | 268 | 268
2017-10-18 17:30 | 273 | 273
2017-10-18 18:00 | 276 | 276
2017-10-18 18:30 | 282 | 281
2017-10-18 19:00 | 283 | 282
2017-10-18 19:30 | 275 | 274
2017-10-18 20:00 | 269 | 269
2017-10-18 20:30 | 266 | 266
2017-10-18 21:00 | 254 | 254
2017-10-18 21:30 | 243 | 242
2017-10-18 22:00 | 233 | 232
2017-10-18 22:30 | 229 | 228
2017-10-18 23:00 | 224 | 223
2017-10-18 23:30 | 210 | 210
2017-10-19 | 193 | 193
2017-10-19 00:30 | 176 | 176
2017-10-19 01:00 | 168 | 168
2017-10-19 01:30 | 161 | 161
2017-10-19 02:00 | 157 | 157
2017-10-19 02:30 | 155 | 154
2017-10-19 03:00 | 154 | 153
2017-10-19 03:30 | 155 | 154
2017-10-19 04:00 | 155 | 154
2017-10-19 04:30 | 159 | 159
2017-10-19 05:00 | 165 | 165
2017-10-19 05:30 | 176 | 176
2017-10-19 06:00 | 190 | 190
2017-10-19 06:30 | 206 | 205
2017-10-19 07:00 | 218 | 217
2017-10-19 07:30 | 230 | 230
2017-10-19 08:00 | 235 | 235
2017-10-19 08:30 | 236 | 236
2017-10-19 09:00 | 228 | 228
2017-10-19 09:30 | 229 | 228
2017-10-19 10:00 | 223 | 223
2017-10-19 10:30 | 223 | 222
2017-10-19 11:00 | 226 | 226
2017-10-19 11:30 | 221 | 221
2017-10-19 12:00 | 225 | 225
2017-10-19 12:30 | 224 | 224
2017-10-19 13:00 | 223 | 223
2017-10-19 13:30 | 223 | 223
2017-10-19 14:00 | 224 | 224
2017-10-19 14:30 | 224 | 224
2017-10-19 15:00 | 230 | 230
2017-10-19 15:30 | 237 | 237
2017-10-19 16:00 | 242 | 241
2017-10-19 16:30 | 248 | 248
2017-10-19 17:00 | 257 | 257
2017-10-19 17:30 | 261 | 261
2017-10-19 18:00 | 264 | 264
2017-10-19 18:30 | 273 | 273
2017-10-19 19:00 | 281 | 280
2017-10-19 19:30 | 274 | 274
2017-10-19 20:00 | 271 | 271
2017-10-19 20:30 | 268 | 268
2017-10-19 21:00 | 256 | 256
2017-10-19 21:30 | 245 | 245
2017-10-19 22:00 | 235 | 235
2017-10-19 22:30 | 229 | 229
2017-10-19 23:00 | 226 | 225
2017-10-19 23:30 | 212 | 212
2017-10-20 | 194 | 194
2017-10-20 00:30 | 178 | 178
2017-10-20 01:00 | 170 | 170
2017-10-20 01:30 | 162 | 162
2017-10-20 02:00 | 159 | 158
2017-10-20 02:30 | 156 | 156
2017-10-20 03:00 | 155 | 155
2017-10-20 03:30 | 156 | 156
2017-10-20 04:00 | 156 | 156
2017-10-20 04:30 | 159 | 159
2017-10-20 05:00 | 166 | 166
2017-10-20 05:30 | 177 | 177
2017-10-20 06:00 | 191 | 191
2017-10-20 06:30 | 208 | 208
2017-10-20 07:00 | 219 | 219
2017-10-20 07:30 | 224 | 224
2017-10-20 08:00 | 228 | 227
2017-10-20 08:30 | 227 | 226
2017-10-20 09:00 | 225 | 224
2017-10-20 09:30 | 230 | 229
2017-10-20 10:00 | 230 | 229
2017-10-20 10:30 | 231 | 230
2017-10-20 11:00 | 231 | 230
2017-10-20 11:30 | 225 | 224
2017-10-20 12:00 | 222 | 221
2017-10-20 12:30 | 224 | 223
2017-10-20 13:00 | 231 | 230
2017-10-20 13:30 | 231 | 230
2017-10-20 14:00 | 231 | 230
2017-10-20 14:30 | 230 | 229
2017-10-20 15:00 | 227 | 226
2017-10-20 15:30 | 226 | 225
2017-10-20 16:00 | 235 | 234
2017-10-20 16:30 | 245 | 245
2017-10-20 17:00 | 257 | 256
2017-10-20 17:30 | 255 | 254
2017-10-20 18:00 | 252 | 252
2017-10-20 18:30 | 258 | 258
2017-10-20 19:00 | 265 | 265
2017-10-20 19:30 | 258 | 258
2017-10-20 20:00 | 256 | 255
2017-10-20 20:30 | 253 | 252
2017-10-20 21:00 | 241 | 241
2017-10-20 21:30 | 231 | 231
2017-10-20 22:00 | 225 | 224
2017-10-20 22:30 | 221 | 221
2017-10-20 23:00 | 220 | 220
2017-10-20 23:30 | 206 | 206
2017-10-21 | 190 | 190
2017-10-21 00:30 | 175 | 175
2017-10-21 01:00 | 166 | 166
2017-10-21 01:30 | 160 | 160
2017-10-21 02:00 | 156 | 156
2017-10-21 02:30 | 153 | 152
2017-10-21 03:00 | 151 | 151
2017-10-21 03:30 | 150 | 150
2017-10-21 04:00 | 150 | 149
2017-10-21 04:30 | 150 | 150
2017-10-21 05:00 | 153 | 152
2017-10-21 05:30 | 156 | 155
2017-10-21 06:00 | 161 | 160
2017-10-21 06:30 | 171 | 171
2017-10-21 07:00 | 181 | 181
2017-10-21 07:30 | 193 | 193
2017-10-21 08:00 | 202 | 202
2017-10-21 08:30 | 214 | 214
2017-10-21 09:00 | 223 | 223
2017-10-21 09:30 | 230 | 230
2017-10-21 10:00 | 233 | 232
2017-10-21 10:30 | 229 | 229
2017-10-21 11:00 | 222 | 222
2017-10-21 11:30 | 217 | 217
2017-10-21 12:00 | 215 | 215
2017-10-21 12:30 | 217 | 216
2017-10-21 13:00 | 215 | 215
2017-10-21 13:30 | 214 | 214
2017-10-21 14:00 | 215 | 214
2017-10-21 14:30 | 213 | 213
2017-10-21 15:00 | 212 | 211
2017-10-21 15:30 | 213 | 213
2017-10-21 16:00 | 216 | 216
2017-10-21 16:30 | 220 | 220
2017-10-21 17:00 | 226 | 226
2017-10-21 17:30 | 228 | 227
2017-10-21 18:00 | 230 | 230
2017-10-21 18:30 | 239 | 238
2017-10-21 19:00 | 242 | 241
2017-10-21 19:30 | 235 | 235
2017-10-21 20:00 | 233 | 232
2017-10-21 20:30 | 229 | 229
2017-10-21 21:00 | 219 | 219
2017-10-21 21:30 | 214 | 213
2017-10-21 22:00 | 208 | 207
2017-10-21 22:30 | 207 | 207
2017-10-21 23:00 | 207 | 207
2017-10-21 23:30 | 198 | 198
2017-10-22 | 184 | 184
2017-10-22 00:30 | 169 | 169
2017-10-22 01:00 | 159 | 159
2017-10-22 01:30 | 152 | 152
2017-10-22 02:00 | 147 | 147
2017-10-22 02:30 | 143 | 143
2017-10-22 03:00 | 141 | 141
2017-10-22 03:30 | 141 | 141
2017-10-22 04:00 | 140 | 139
2017-10-22 04:30 | 140 | 140
2017-10-22 05:00 | 141 | 141
2017-10-22 05:30 | 139 | 139
2017-10-22 06:00 | 139 | 139
2017-10-22 06:30 | 140 | 139
2017-10-22 07:00 | 138 | 138
2017-10-22 07:30 | 138 | 138
2017-10-22 08:00 | 138 | 138
2017-10-22 08:30 | 138 | 138
2017-10-22 09:00 | 136 | 136
2017-10-22 09:30 | 135 | 135
2017-10-22 10:00 | 133 | 133
2017-10-22 10:30 | 132 | 132
2017-10-22 11:00 | 137 | 137
2017-10-22 11:30 | 141 | 141
2017-10-22 12:00 | 144 | 144
2017-10-22 12:30 | 144 | 144
2017-10-22 13:00 | 143 | 143
2017-10-22 13:30 | 143 | 143
2017-10-22 14:00 | 146 | 146
2017-10-22 14:30 | 152 | 152
2017-10-22 15:00 | 159 | 159
2017-10-22 15:30 | 168 | 168
2017-10-22 16:00 | 180 | 180
2017-10-22 16:30 | 190 | 190
2017-10-22 17:00 | 203 | 203
2017-10-22 17:30 | 211 | 211
2017-10-22 18:00 | 220 | 220
2017-10-22 18:30 | 235 | 234
2017-10-22 19:00 | 242 | 242
2017-10-22 19:30 | 236 | 236
2017-10-22 20:00 | 232 | 232
2017-10-22 20:30 | 230 | 230
2017-10-22 21:00 | 221 | 221
2017-10-22 21:30 | 212 | 212
2017-10-22 22:00 | 204 | 204
2017-10-22 22:30 | 201 | 201
2017-10-22 23:00 | 201 | 201
2017-10-22 23:30 | 191 | 191
2017-10-23 | 176 | 176
2017-10-23 00:30 | 163 | 162
2017-10-23 01:00 | 156 | 154
2017-10-23 01:30 | 150 | 149
2017-10-23 02:00 | 147 | 145
2017-10-23 02:30 | 145 | 143
2017-10-23 03:00 | 144 | 142
2017-10-23 03:30 | 144 | 142
2017-10-23 04:00 | 145 | 143
2017-10-23 04:30 | 150 | 148
2017-10-23 05:00 | 157 | 156
2017-10-23 05:30 | 168 | 167
2017-10-23 06:00 | 182 | 182
2017-10-23 06:30 | 204 | 204
2017-10-23 07:00 | 219 | 219
2017-10-23 07:30 | 224 | 224
2017-10-23 08:00 | 220 | 220
2017-10-23 08:30 | 218 | 217
2017-10-23 09:00 | 219 | 218
2017-10-23 09:30 | 239 | 238
2017-10-23 10:00 | 258 | 257
2017-10-23 10:30 | 257 | 256
2017-10-23 11:00 | 240 | 239
2017-10-23 11:30 | 230 | 229
2017-10-23 12:00 | 236 | 235
2017-10-23 12:30 | 228 | 227
2017-10-23 13:00 | 212 | 212
2017-10-23 13:30 | 204 | 203
2017-10-23 14:00 | 216 | 215
2017-10-23 14:30 | 223 | 223
2017-10-23 15:00 | 224 | 224
2017-10-23 15:30 | 237 | 237
2017-10-23 16:00 | 247 | 246
2017-10-23 16:30 | 250 | 250
2017-10-23 17:00 | 258 | 257
2017-10-23 17:30 | 262 | 261
2017-10-23 18:00 | 262 | 262
2017-10-23 18:30 | 271 | 270
2017-10-23 19:00 | 276 | 275
2017-10-23 19:30 | 267 | 267
2017-10-23 20:00 | 263 | 262
2017-10-23 20:30 | 260 | 259
2017-10-23 21:00 | 247 | 247
2017-10-23 21:30 | 235 | 234
2017-10-23 22:00 | 224 | 224
2017-10-23 22:30 | 217 | 217
2017-10-23 23:00 | 214 | 214
2017-10-23 23:30 | 203 | 203
2017-10-24 | 188 | 188
2017-10-24 00:30 | 172 | 172
2017-10-24 01:00 | 163 | 163
2017-10-24 01:30 | 157 | 156
2017-10-24 02:00 | 153 | 152
2017-10-24 02:30 | 151 | 151
2017-10-24 03:00 | 150 | 149
2017-10-24 03:30 | 150 | 149
2017-10-24 04:00 | 151 | 150
2017-10-24 04:30 | 155 | 155
2017-10-24 05:00 | 163 | 162
2017-10-24 05:30 | 174 | 174
2017-10-24 06:00 | 187 | 187
2017-10-24 06:30 | 203 | 203
2017-10-24 07:00 | 213 | 212
2017-10-24 07:30 | 217 | 217
2017-10-24 08:00 | 212 | 212
2017-10-24 08:30 | 210 | 209
2017-10-24 09:00 | 202 | 201
2017-10-24 09:30 | 204 | 202
2017-10-24 10:00 | 209 | 206
2017-10-24 10:30 | 205 | 203
2017-10-24 11:00 | 203 | 200
2017-10-24 11:30 | 204 | 201
2017-10-24 12:00 | 212 | 208
2017-10-24 12:30 | 217 | 213
2017-10-24 13:00 | 220 | 217
2017-10-24 13:30 | 219 | 217
2017-10-24 14:00 | 218 | 216
2017-10-24 14:30 | 221 | 219
2017-10-24 15:00 | 221 | 219
2017-10-24 15:30 | 228 | 227
2017-10-24 16:00 | 236 | 233
2017-10-24 16:30 | 243 | 242
2017-10-24 17:00 | 255 | 254
2017-10-24 17:30 | 262 | 261
2017-10-24 18:00 | 264 | 263
2017-10-24 18:30 | 273 | 273
2017-10-24 19:00 | 280 | 279
2017-10-24 19:30 | 269 | 269
2017-10-24 20:00 | 264 | 263
2017-10-24 20:30 | 259 | 258
2017-10-24 21:00 | 249 | 248
2017-10-24 21:30 | 238 | 237
2017-10-24 22:00 | 228 | 228
2017-10-24 22:30 | 221 | 221
2017-10-24 23:00 | 218 | 217
2017-10-24 23:30 | 205 | 204
2017-10-25 | 189 | 189
2017-10-25 00:30 | 174 | 174
2017-10-25 01:00 | 165 | 165
2017-10-25 01:30 | 158 | 158
2017-10-25 02:00 | 154 | 154
2017-10-25 02:30 | 151 | 151
2017-10-25 03:00 | 148 | 148
2017-10-25 03:30 | 147 | 147
2017-10-25 04:00 | 147 | 147
2017-10-25 04:30 | 152 | 152
2017-10-25 05:00 | 159 | 159
2017-10-25 05:30 | 172 | 172
2017-10-25 06:00 | 185 | 185
2017-10-25 06:30 | 200 | 200
2017-10-25 07:00 | 208 | 208
2017-10-25 07:30 | 216 | 216
2017-10-25 08:00 | 195 | 194
2017-10-25 08:30 | 185 | 184
2017-10-25 09:00 | 178 | 178
2017-10-25 09:30 | 174 | 174
2017-10-25 10:00 | 172 | 172
2017-10-25 10:30 | 171 | 171
2017-10-25 11:00 | 172 | 172
2017-10-25 11:30 | 172 | 172
2017-10-25 12:00 | 176 | 176
2017-10-25 12:30 | 180 | 180
2017-10-25 13:00 | 188 | 188
2017-10-25 13:30 | 199 | 199
2017-10-25 14:00 | 197 | 197
2017-10-25 14:30 | 205 | 205
2017-10-25 15:00 | 211 | 211
2017-10-25 15:30 | 220 | 219
2017-10-25 16:00 | 232 | 231
2017-10-25 16:30 | 259 | 259
2017-10-25 17:00 | 270 | 269
2017-10-25 17:30 | 274 | 274
2017-10-25 18:00 | 274 | 273
2017-10-25 18:30 | 278 | 278
2017-10-25 19:00 | 287 | 286
2017-10-25 19:30 | 278 | 277
2017-10-25 20:00 | 270 | 270
2017-10-25 20:30 | 266 | 266
2017-10-25 21:00 | 253 | 253
2017-10-25 21:30 | 241 | 241
2017-10-25 22:00 | 232 | 232
2017-10-25 22:30 | 226 | 225
2017-10-25 23:00 | 222 | 222
2017-10-25 23:30 | 207 | 207
2017-10-26 | 191 | 191
2017-10-26 00:30 | 177 | 176
2017-10-26 01:00 | 167 | 167
2017-10-26 01:30 | 162 | 161
2017-10-26 02:00 | 158 | 157
2017-10-26 02:30 | 156 | 154
2017-10-26 03:00 | 153 | 151
2017-10-26 03:30 | 152 | 150
2017-10-26 04:00 | 152 | 151
2017-10-26 04:30 | 157 | 156
2017-10-26 05:00 | 162 | 162
2017-10-26 05:30 | 171 | 171
2017-10-26 06:00 | 182 | 182
2017-10-26 06:30 | 195 | 195
2017-10-26 07:00 | 207 | 207
2017-10-26 07:30 | 216 | 216
2017-10-26 08:00 | 213 | 213
2017-10-26 08:30 | 209 | 209
2017-10-26 09:00 | 205 | 205
2017-10-26 09:30 | 204 | 204
2017-10-26 10:00 | 204 | 204
2017-10-26 10:30 | 206 | 206
2017-10-26 11:00 | 208 | 207
2017-10-26 11:30 | 211 | 211
2017-10-26 12:00 | 218 | 217
2017-10-26 12:30 | 225 | 224
2017-10-26 13:00 | 230 | 228
2017-10-26 13:30 | 239 | 237
2017-10-26 14:00 | 247 | 246
2017-10-26 14:30 | 261 | 259
2017-10-26 15:00 | 271 | 271
2017-10-26 15:30 | 282 | 280
2017-10-26 16:00 | 295 | 293
2017-10-26 16:30 | 303 | 302
2017-10-26 17:00 | 308 | 307
2017-10-26 17:30 | 309 | 308
2017-10-26 18:00 | 305 | 304
2017-10-26 18:30 | 298 | 297
2017-10-26 19:00 | 300 | 299
2017-10-26 19:30 | 292 | 292
2017-10-26 20:00 | 286 | 286
2017-10-26 20:30 | 280 | 279
2017-10-26 21:00 | 265 | 265
2017-10-26 21:30 | 251 | 250
2017-10-26 22:00 | 238 | 238
2017-10-26 22:30 | 231 | 231
2017-10-26 23:00 | 228 | 228
2017-10-26 23:30 | 215 | 215
2017-10-27 | 198 | 197
2017-10-27 00:30 | 182 | 181
2017-10-27 01:00 | 174 | 173
2017-10-27 01:30 | 168 | 168
2017-10-27 02:00 | 165 | 164
2017-10-27 02:30 | 163 | 162
2017-10-27 03:00 | 161 | 160
2017-10-27 03:30 | 161 | 160
2017-10-27 04:00 | 161 | 161
2017-10-27 04:30 | 163 | 162
2017-10-27 05:00 | 168 | 167
2017-10-27 05:30 | 174 | 173
2017-10-27 06:00 | 186 | 185
2017-10-27 06:30 | 202 | 202
2017-10-27 07:00 | 213 | 212
2017-10-27 07:30 | 220 | 220
2017-10-27 08:00 | 217 | 217
2017-10-27 08:30 | 211 | 211
2017-10-27 09:00 | 205 | 205
2017-10-27 09:30 | 201 | 201
2017-10-27 10:00 | 197 | 197
2017-10-27 10:30 | 197 | 196
2017-10-27 11:00 | 197 | 197
2017-10-27 11:30 | 197 | 197
2017-10-27 12:00 | 200 | 199
2017-10-27 12:30 | 202 | 201
2017-10-27 13:00 | 208 | 207
2017-10-27 13:30 | 213 | 213
2017-10-27 14:00 | 223 | 222
2017-10-27 14:30 | 234 | 232
2017-10-27 15:00 | 242 | 241
2017-10-27 15:30 | 252 | 251
2017-10-27 16:00 | 265 | 263
2017-10-27 16:30 | 274 | 273
2017-10-27 17:00 | 278 | 277
2017-10-27 17:30 | 275 | 274
2017-10-27 18:00 | 270 | 269
2017-10-27 18:30 | 268 | 267
2017-10-27 19:00 | 277 | 275
2017-10-27 19:30 | 272 | 270
2017-10-27 20:00 | 267 | 265
2017-10-27 20:30 | 263 | 261
2017-10-27 21:00 | 249 | 248
2017-10-27 21:30 | 239 | 238
2017-10-27 22:00 | 229 | 229
2017-10-27 22:30 | 222 | 222
2017-10-27 23:00 | 221 | 219
2017-10-27 23:30 | 207 | 206
2017-10-28 | 190 | 189
2017-10-28 00:30 | 174 | 174
2017-10-28 01:00 | 165 | 165
2017-10-28 01:30 | 159 | 159
2017-10-28 02:00 | 153 | 153
2017-10-28 02:30 | 151 | 151
2017-10-28 03:00 | 148 | 148
2017-10-28 03:30 | 147 | 147
2017-10-28 04:00 | 145 | 145
2017-10-28 04:30 | 146 | 146
2017-10-28 05:00 | 147 | 147
2017-10-28 05:30 | 147 | 147
2017-10-28 06:00 | 153 | 153
2017-10-28 06:30 | 154 | 154
2017-10-28 07:00 | 156 | 156
2017-10-28 07:30 | 163 | 162
2017-10-28 08:00 | 163 | 162
2017-10-28 08:30 | 168 | 166
2017-10-28 09:00 | 170 | 170
2017-10-28 09:30 | 169 | 169
2017-10-28 10:00 | 170 | 169
2017-10-28 10:30 | 172 | 171
2017-10-28 11:00 | 175 | 174
2017-10-28 11:30 | 179 | 178
2017-10-28 12:00 | 179 | 179
2017-10-28 12:30 | 185 | 184
2017-10-28 13:00 | 183 | 183
2017-10-28 13:30 | 187 | 186
2017-10-28 14:00 | 193 | 193
2017-10-28 14:30 | 196 | 196
2017-10-28 15:00 | 202 | 201
2017-10-28 15:30 | 215 | 214
2017-10-28 16:00 | 224 | 223
2017-10-28 16:30 | 228 | 228
2017-10-28 17:00 | 234 | 234
2017-10-28 17:30 | 233 | 233
2017-10-28 18:00 | 234 | 233
2017-10-28 18:30 | 244 | 243
2017-10-28 19:00 | 250 | 250
2017-10-28 19:30 | 244 | 243
2017-10-28 20:00 | 241 | 241
2017-10-28 20:30 | 237 | 237
2017-10-28 21:00 | 227 | 227
2017-10-28 21:30 | 221 | 220
2017-10-28 22:00 | 214 | 214
2017-10-28 22:30 | 211 | 211
2017-10-28 23:00 | 211 | 211
2017-10-28 23:30 | 200 | 200
2017-10-29 | 184 | 183
2017-10-29 00:30 | 170 | 169
2017-10-29 01:00 | 162 | 162
2017-10-29 01:30 | 156 | 156
2017-10-29 02:00 | 151 | 151
2017-10-29 02:30 | 148 | 148
2017-10-29 03:00 | 146 | 145
2017-10-29 03:30 | 142 | 142
2017-10-29 04:00 | 140 | 140
2017-10-29 04:30 | 143 | 143
2017-10-29 05:00 | 144 | 144
2017-10-29 05:30 | 144 | 144
2017-10-29 06:00 | 147 | 147
2017-10-29 06:30 | 147 | 147
2017-10-29 07:00 | 145 | 145
2017-10-29 07:30 | 148 | 147
2017-10-29 08:00 | 150 | 150
2017-10-29 08:30 | 157 | 156
2017-10-29 09:00 | 156 | 154
2017-10-29 09:30 | 163 | 160
2017-10-29 10:00 | 166 | 164
2017-10-29 10:30 | 170 | 166
2017-10-29 11:00 | 173 | 169
2017-10-29 11:30 | 178 | 176
2017-10-29 12:00 | 183 | 182
2017-10-29 12:30 | 191 | 189
2017-10-29 13:00 | 199 | 198
2017-10-29 13:30 | 208 | 207
2017-10-29 14:00 | 217 | 215
2017-10-29 14:30 | 226 | 224
2017-10-29 15:00 | 236 | 234
2017-10-29 15:30 | 247 | 246
2017-10-29 16:00 | 260 | 258
2017-10-29 16:30 | 272 | 271
2017-10-29 17:00 | 282 | 282
2017-10-29 17:30 | 279 | 279
2017-10-29 18:00 | 278 | 277
2017-10-29 18:30 | 285 | 284
2017-10-29 19:00 | 293 | 293
2017-10-29 19:30 | 274 | 274
2017-10-29 20:00 | 260 | 260
2017-10-29 20:30 | 250 | 250
2017-10-29 21:00 | 236 | 236
2017-10-29 21:30 | 226 | 225
2017-10-29 22:00 | 216 | 216
2017-10-29 22:30 | 212 | 212
2017-10-29 23:00 | 209 | 209
2017-10-29 23:30 | 198 | 198
2017-10-30 | 179 | 179
2017-10-30 00:30 | 166 | 166
2017-10-30 01:00 | 160 | 160
2017-10-30 01:30 | 156 | 156
2017-10-30 02:00 | 152 | 152
2017-10-30 02:30 | 151 | 151
2017-10-30 03:00 | 148 | 148
2017-10-30 03:30 | 148 | 148
2017-10-30 04:00 | 149 | 149
2017-10-30 04:30 | 153 | 152
2017-10-30 05:00 | 160 | 160
2017-10-30 05:30 | 171 | 170
2017-10-30 06:00 | 184 | 182
2017-10-30 06:30 | 204 | 203
2017-10-30 07:00 | 222 | 222
2017-10-30 07:30 | 237 | 236
2017-10-30 08:00 | 237 | 237
2017-10-30 08:30 | 238 | 237
2017-10-30 09:00 | 244 | 243
2017-10-30 09:30 | 249 | 248
2017-10-30 10:00 | 253 | 253
2017-10-30 10:30 | 261 | 261
2017-10-30 11:00 | 254 | 254
2017-10-30 11:30 | 262 | 262
2017-10-30 12:00 | 266 | 266
2017-10-30 12:30 | 265 | 265
2017-10-30 13:00 | 271 | 271
2017-10-30 13:30 | 278 | 278
2017-10-30 14:00 | 289 | 288
2017-10-30 14:30 | 310 | 310
2017-10-30 15:00 | 327 | 326
2017-10-30 15:30 | 326 | 326
2017-10-30 16:00 | 313 | 312
2017-10-30 16:30 | 308 | 308
2017-10-30 17:00 | 318 | 317
2017-10-30 17:30 | 320 | 320
2017-10-30 18:00 | 313 | 313
2017-10-30 18:30 | 313 | 312
2017-10-30 19:00 | 322 | 321
2017-10-30 19:30 | 313 | 312
2017-10-30 20:00 | 308 | 307
2017-10-30 20:30 | 301 | 300
2017-10-30 21:00 | 283 | 280
2017-10-30 21:30 | 268 | 266
2017-10-30 22:00 | 253 | 252
2017-10-30 22:30 | 244 | 243
2017-10-30 23:00 | 238 | 238
2017-10-30 23:30 | 221 | 221
2017-10-31 | 203 | 203
2017-10-31 00:30 | 187 | 187
2017-10-31 01:00 | 179 | 178
2017-10-31 01:30 | 174 | 173
2017-10-31 02:00 | 169 | 168
2017-10-31 02:30 | 166 | 165
2017-10-31 03:00 | 163 | 162
2017-10-31 03:30 | 163 | 162
2017-10-31 04:00 | 163 | 162
2017-10-31 04:30 | 166 | 165
2017-10-31 05:00 | 170 | 170
2017-10-31 05:30 | 180 | 179
2017-10-31 06:00 | 190 | 189
2017-10-31 06:30 | 207 | 205
2017-10-31 07:00 | 220 | 219
2017-10-31 07:30 | 231 | 231
2017-10-31 08:00 | 224 | 224
2017-10-31 08:30 | 224 | 224
2017-10-31 09:00 | 221 | 221
2017-10-31 09:30 | 216 | 216
2017-10-31 10:00 | 217 | 217
2017-10-31 10:30 | 214 | 214
2017-10-31 11:00 | 210 | 210
2017-10-31 11:30 | 210 | 210
2017-10-31 12:00 | 212 | 212
2017-10-31 12:30 | 222 | 222
2017-10-31 13:00 | 221 | 220
2017-10-31 13:30 | 222 | 222
2017-10-31 14:00 | 229 | 228
2017-10-31 14:30 | 237 | 236
2017-10-31 15:00 | 243 | 243
2017-10-31 15:30 | 252 | 252
2017-10-31 16:00 | 265 | 265
2017-10-31 16:30 | 277 | 276
2017-10-31 17:00 | 285 | 285
2017-10-31 17:30 | 283 | 283
2017-10-31 18:00 | 276 | 276
2017-10-31 18:30 | 274 | 274
2017-10-31 19:00 | 281 | 281
2017-10-31 19:30 | 273 | 272
2017-10-31 20:00 | 269 | 268
2017-10-31 20:30 | 266 | 266
2017-10-31 21:00 | 252 | 252
2017-10-31 21:30 | 240 | 240
2017-10-31 22:00 | 229 | 229
2017-10-31 22:30 | 222 | 222
2017-10-31 23:00 | 217 | 217
2017-10-31 23:30 | 198 | 198
2017-11-01 | 180 | 180
2017-11-01 00:30 | 165 | 165
2017-11-01 01:00 | 157 | 157
2017-11-01 01:30 | 154 | 154
2017-11-01 02:00 | 150 | 150
2017-11-01 02:30 | 147 | 147
2017-11-01 03:00 | 147 | 147
2017-11-01 03:30 | 147 | 146
2017-11-01 04:00 | 147 | 147
2017-11-01 04:30 | 151 | 151
2017-11-01 05:00 | 156 | 156
2017-11-01 05:30 | 166 | 166
2017-11-01 06:00 | 176 | 175
2017-11-01 06:30 | 196 | 194
2017-11-01 07:00 | 210 | 209
2017-11-01 07:30 | 218 | 218
2017-11-01 08:00 | 211 | 211
2017-11-01 08:30 | 205 | 205
2017-11-01 09:00 | 203 | 203
2017-11-01 09:30 | 211 | 211
2017-11-01 10:00 | 209 | 209
2017-11-01 10:30 | 209 | 209
2017-11-01 11:00 | 205 | 205
2017-11-01 11:30 | 209 | 209
2017-11-01 12:00 | 211 | 211
2017-11-01 12:30 | 213 | 213
2017-11-01 13:00 | 210 | 210
2017-11-01 13:30 | 208 | 208
2017-11-01 14:00 | 211 | 211
2017-11-01 14:30 | 216 | 216
2017-11-01 15:00 | 218 | 218
2017-11-01 15:30 | 225 | 225
2017-11-01 16:00 | 238 | 238
2017-11-01 16:30 | 249 | 249
2017-11-01 17:00 | 264 | 264
2017-11-01 17:30 | 272 | 272
2017-11-01 18:00 | 268 | 268
2017-11-01 18:30 | 271 | 271
2017-11-01 19:00 | 282 | 282
2017-11-01 19:30 | 275 | 275
2017-11-01 20:00 | 270 | 270
2017-11-01 20:30 | 265 | 265
2017-11-01 21:00 | 249 | 248
2017-11-01 21:30 | 237 | 236
2017-11-01 22:00 | 225 | 225
2017-11-01 22:30 | 218 | 218
2017-11-01 23:00 | 215 | 214
2017-11-01 23:30 | 203 | 203
2017-11-02 | 186 | 186
2017-11-02 00:30 | 170 | 170
2017-11-02 01:00 | 163 | 163
2017-11-02 01:30 | 159 | 159
2017-11-02 02:00 | 155 | 155
2017-11-02 02:30 | 152 | 152
2017-11-02 03:00 | 150 | 150
2017-11-02 03:30 | 150 | 150
2017-11-02 04:00 | 151 | 151
2017-11-02 04:30 | 155 | 155
2017-11-02 05:00 | 160 | 160
2017-11-02 05:30 | 170 | 170
2017-11-02 06:00 | 180 | 179
2017-11-02 06:30 | 194 | 193
2017-11-02 07:00 | 205 | 203
2017-11-02 07:30 | 213 | 212
2017-11-02 08:00 | 212 | 212
2017-11-02 08:30 | 209 | 209
2017-11-02 09:00 | 205 | 205
2017-11-02 09:30 | 207 | 207
2017-11-02 10:00 | 208 | 208
2017-11-02 10:30 | 210 | 210
2017-11-02 11:00 | 212 | 212
2017-11-02 11:30 | 212 | 212
2017-11-02 12:00 | 216 | 216
2017-11-02 12:30 | 218 | 218
2017-11-02 13:00 | 227 | 227
2017-11-02 13:30 | 234 | 233
2017-11-02 14:00 | 241 | 241
2017-11-02 14:30 | 240 | 240
2017-11-02 15:00 | 241 | 241
2017-11-02 15:30 | 245 | 245
2017-11-02 16:00 | 255 | 255
2017-11-02 16:30 | 266 | 266
2017-11-02 17:00 | 276 | 276
2017-11-02 17:30 | 277 | 277
2017-11-02 18:00 | 276 | 276
2017-11-02 18:30 | 280 | 279
2017-11-02 19:00 | 292 | 292
2017-11-02 19:30 | 285 | 285
2017-11-02 20:00 | 281 | 281
2017-11-02 20:30 | 275 | 275
2017-11-02 21:00 | 263 | 263
2017-11-02 21:30 | 248 | 248
2017-11-02 22:00 | 238 | 238
2017-11-02 22:30 | 231 | 231
2017-11-02 23:00 | 227 | 226
2017-11-02 23:30 | 210 | 210
2017-11-03 | 191 | 191
2017-11-03 00:30 | 177 | 177
2017-11-03 01:00 | 167 | 167
2017-11-03 01:30 | 161 | 161
2017-11-03 02:00 | 159 | 159
2017-11-03 02:30 | 156 | 156
2017-11-03 03:00 | 155 | 155
2017-11-03 03:30 | 156 | 156
2017-11-03 04:00 | 157 | 157
2017-11-03 04:30 | 160 | 160
2017-11-03 05:00 | 165 | 165
2017-11-03 05:30 | 174 | 174
2017-11-03 06:00 | 183 | 183
2017-11-03 06:30 | 199 | 198
2017-11-03 07:00 | 212 | 212
2017-11-03 07:30 | 224 | 224
2017-11-03 08:00 | 228 | 228
2017-11-03 08:30 | 229 | 229
2017-11-03 09:00 | 225 | 225
2017-11-03 09:30 | 224 | 223
2017-11-03 10:00 | 223 | 223
2017-11-03 10:30 | 224 | 224
2017-11-03 11:00 | 227 | 227
2017-11-03 11:30 | 230 | 230
2017-11-03 12:00 | 235 | 235
2017-11-03 12:30 | 240 | 240
2017-11-03 13:00 | 244 | 244
2017-11-03 13:30 | 241 | 241
2017-11-03 14:00 | 239 | 239
2017-11-03 14:30 | 246 | 246
2017-11-03 15:00 | 254 | 254
2017-11-03 15:30 | 260 | 260
2017-11-03 16:00 | 270 | 270
2017-11-03 16:30 | 277 | 277
2017-11-03 17:00 | 284 | 284
2017-11-03 17:30 | 282 | 282
2017-11-03 18:00 | 275 | 274
2017-11-03 18:30 | 273 | 272
2017-11-03 19:00 | 282 | 282
2017-11-03 19:30 | 276 | 276
2017-11-03 20:00 | 273 | 273
2017-11-03 20:30 | 265 | 264
2017-11-03 21:00 | 252 | 251
2017-11-03 21:30 | 241 | 241
2017-11-03 22:00 | 230 | 230
2017-11-03 22:30 | 226 | 226
2017-11-03 23:00 | 221 | 221
2017-11-03 23:30 | 209 | 209
2017-11-04 | 192 | 192
2017-11-04 00:30 | 178 | 177
2017-11-04 01:00 | 169 | 169
2017-11-04 01:30 | 163 | 163
2017-11-04 02:00 | 159 | 158
2017-11-04 02:30 | 156 | 156
2017-11-04 03:00 | 155 | 155
2017-11-04 03:30 | 153 | 153
2017-11-04 04:00 | 152 | 152
2017-11-04 04:30 | 154 | 154
2017-11-04 05:00 | 153 | 153
2017-11-04 05:30 | 155 | 155
2017-11-04 06:00 | 156 | 156
2017-11-04 06:30 | 162 | 162
2017-11-04 07:00 | 165 | 165
2017-11-04 07:30 | 171 | 170
2017-11-04 08:00 | 173 | 172
2017-11-04 08:30 | 177 | 176
2017-11-04 09:00 | 178 | 177
2017-11-04 09:30 | 176 | 175
2017-11-04 10:00 | 176 | 175
2017-11-04 10:30 | 177 | 175
2017-11-04 11:00 | 177 | 175
2017-11-04 11:30 | 181 | 179
2017-11-04 12:00 | 186 | 183
2017-11-04 12:30 | 188 | 186
2017-11-04 13:00 | 197 | 195
2017-11-04 13:30 | 202 | 200
2017-11-04 14:00 | 209 | 208
2017-11-04 14:30 | 212 | 212
2017-11-04 15:00 | 218 | 218
2017-11-04 15:30 | 226 | 225
2017-11-04 16:00 | 236 | 235
2017-11-04 16:30 | 245 | 244
2017-11-04 17:00 | 252 | 252
2017-11-04 17:30 | 250 | 250
2017-11-04 18:00 | 248 | 248
2017-11-04 18:30 | 253 | 252
2017-11-04 19:00 | 263 | 262
2017-11-04 19:30 | 256 | 256
2017-11-04 20:00 | 252 | 252
2017-11-04 20:30 | 247 | 246
2017-11-04 21:00 | 236 | 236
2017-11-04 21:30 | 228 | 228
2017-11-04 22:00 | 221 | 221
2017-11-04 22:30 | 218 | 218
2017-11-04 23:00 | 218 | 218
2017-11-04 23:30 | 207 | 207
2017-11-05 | 190 | 190
2017-11-05 00:30 | 176 | 176
2017-11-05 01:00 | 168 | 168
2017-11-05 01:30 | 163 | 162
2017-11-05 02:00 | 158 | 158
2017-11-05 02:30 | 156 | 156
2017-11-05 03:00 | 154 | 154
2017-11-05 03:30 | 153 | 153
2017-11-05 04:00 | 151 | 151
2017-11-05 04:30 | 150 | 150
2017-11-05 05:00 | 150 | 149
2017-11-05 05:30 | 150 | 149
2017-11-05 06:00 | 151 | 150
2017-11-05 06:30 | 154 | 153
2017-11-05 07:00 | 156 | 156
2017-11-05 07:30 | 162 | 162
2017-11-05 08:00 | 174 | 174
2017-11-05 08:30 | 179 | 179
2017-11-05 09:00 | 181 | 181
2017-11-05 09:30 | 184 | 184
2017-11-05 10:00 | 188 | 187
2017-11-05 10:30 | 185 | 184
2017-11-05 11:00 | 178 | 177
2017-11-05 11:30 | 185 | 184
2017-11-05 12:00 | 182 | 181
2017-11-05 12:30 | 179 | 178
2017-11-05 13:00 | 184 | 183
2017-11-05 13:30 | 192 | 190
2017-11-05 14:00 | 197 | 197
2017-11-05 14:30 | 204 | 204
2017-11-05 15:00 | 209 | 209
2017-11-05 15:30 | 219 | 219
2017-11-05 16:00 | 230 | 230
2017-11-05 16:30 | 239 | 239
2017-11-05 17:00 | 251 | 251
2017-11-05 17:30 | 256 | 256
2017-11-05 18:00 | 258 | 258
2017-11-05 18:30 | 263 | 263
2017-11-05 19:00 | 270 | 269
2017-11-05 19:30 | 262 | 262
2017-11-05 20:00 | 257 | 257
2017-11-05 20:30 | 253 | 252
2017-11-05 21:00 | 240 | 239
2017-11-05 21:30 | 229 | 229
2017-11-05 22:00 | 224 | 224
2017-11-05 22:30 | 220 | 220
2017-11-05 23:00 | 217 | 217
2017-11-05 23:30 | 204 | 204
2017-11-06 | 186 | 186
2017-11-06 00:30 | 172 | 172
2017-11-06 01:00 | 165 | 165
2017-11-06 01:30 | 161 | 161
2017-11-06 02:00 | 158 | 158
2017-11-06 02:30 | 156 | 156
2017-11-06 03:00 | 155 | 155
2017-11-06 03:30 | 152 | 152
2017-11-06 04:00 | 150 | 150
2017-11-06 04:30 | 156 | 156
2017-11-06 05:00 | 161 | 161
2017-11-06 05:30 | 172 | 172
2017-11-06 06:00 | 184 | 184
2017-11-06 06:30 | 208 | 207
2017-11-06 07:00 | 224 | 224
2017-11-06 07:30 | 233 | 232
2017-11-06 08:00 | 231 | 230
2017-11-06 08:30 | 237 | 237
2017-11-06 09:00 | 242 | 241
2017-11-06 09:30 | 247 | 246
2017-11-06 10:00 | 245 | 244
2017-11-06 10:30 | 234 | 233
2017-11-06 11:00 | 229 | 228
2017-11-06 11:30 | 244 | 242
2017-11-06 12:00 | 255 | 253
2017-11-06 12:30 | 245 | 243
2017-11-06 13:00 | 250 | 248
2017-11-06 13:30 | 259 | 257
2017-11-06 14:00 | 245 | 243
2017-11-06 14:30 | 251 | 250
2017-11-06 15:00 | 257 | 257
2017-11-06 15:30 | 264 | 264
2017-11-06 16:00 | 277 | 277
2017-11-06 16:30 | 287 | 287
2017-11-06 17:00 | 297 | 297
2017-11-06 17:30 | 298 | 298
2017-11-06 18:00 | 293 | 293
2017-11-06 18:30 | 296 | 296
2017-11-06 19:00 | 306 | 306
2017-11-06 19:30 | 297 | 296
2017-11-06 20:00 | 291 | 290
2017-11-06 20:30 | 285 | 285
2017-11-06 21:00 | 271 | 271
2017-11-06 21:30 | 257 | 257
2017-11-06 22:00 | 242 | 242
2017-11-06 22:30 | 232 | 232
2017-11-06 23:00 | 224 | 224
2017-11-06 23:30 | 206 | 206
2017-11-07 | 190 | 190
2017-11-07 00:30 | 176 | 176
2017-11-07 01:00 | 168 | 168
2017-11-07 01:30 | 163 | 163
2017-11-07 02:00 | 160 | 160
2017-11-07 02:30 | 158 | 158
2017-11-07 03:00 | 157 | 157
2017-11-07 03:30 | 156 | 156
2017-11-07 04:00 | 156 | 156
2017-11-07 04:30 | 160 | 160
2017-11-07 05:00 | 166 | 166
2017-11-07 05:30 | 176 | 176
2017-11-07 06:00 | 183 | 183
2017-11-07 06:30 | 203 | 202
2017-11-07 07:00 | 213 | 212
2017-11-07 07:30 | 223 | 223
2017-11-07 08:00 | 227 | 227
2017-11-07 08:30 | 226 | 225
2017-11-07 09:00 | 227 | 226
2017-11-07 09:30 | 229 | 229
2017-11-07 10:00 | 234 | 234
2017-11-07 10:30 | 241 | 241
2017-11-07 11:00 | 247 | 247
2017-11-07 11:30 | 248 | 248
2017-11-07 12:00 | 238 | 237
2017-11-07 12:30 | 226 | 226
2017-11-07 13:00 | 229 | 229
2017-11-07 13:30 | 230 | 230
2017-11-07 14:00 | 247 | 247
2017-11-07 14:30 | 246 | 246
2017-11-07 15:00 | 253 | 253
2017-11-07 15:30 | 256 | 255
2017-11-07 16:00 | 252 | 252
2017-11-07 16:30 | 256 | 255
2017-11-07 17:00 | 268 | 268
2017-11-07 17:30 | 270 | 270
2017-11-07 18:00 | 268 | 267
2017-11-07 18:30 | 270 | 269
2017-11-07 19:00 | 277 | 277
2017-11-07 19:30 | 270 | 269
2017-11-07 20:00 | 266 | 266
2017-11-07 20:30 | 264 | 264
2017-11-07 21:00 | 252 | 251
2017-11-07 21:30 | 238 | 238
2017-11-07 22:00 | 227 | 227
2017-11-07 22:30 | 221 | 221
2017-11-07 23:00 | 218 | 218
2017-11-07 23:30 | 204 | 204
2017-11-08 | 188 | 188
2017-11-08 00:30 | 174 | 174
2017-11-08 01:00 | 166 | 166
2017-11-08 01:30 | 161 | 161
2017-11-08 02:00 | 157 | 157
2017-11-08 02:30 | 154 | 154
2017-11-08 03:00 | 153 | 153
2017-11-08 03:30 | 154 | 154
2017-11-08 04:00 | 154 | 154
2017-11-08 04:30 | 158 | 158
2017-11-08 05:00 | 164 | 164
2017-11-08 05:30 | 174 | 174
2017-11-08 06:00 | 186 | 185
2017-11-08 06:30 | 203 | 201
2017-11-08 07:00 | 217 | 216
2017-11-08 07:30 | 226 | 225
2017-11-08 08:00 | 222 | 221
2017-11-08 08:30 | 217 | 216
2017-11-08 09:00 | 211 | 209
2017-11-08 09:30 | 208 | 207
2017-11-08 10:00 | 213 | 211
2017-11-08 10:30 | 212 | 210
2017-11-08 11:00 | 209 | 208
2017-11-08 11:30 | 217 | 216
2017-11-08 12:00 | 235 | 233
2017-11-08 12:30 | 228 | 227
2017-11-08 13:00 | 225 | 224
2017-11-08 13:30 | 235 | 234
2017-11-08 14:00 | 234 | 234
2017-11-08 14:30 | 234 | 233
2017-11-08 15:00 | 229 | 229
2017-11-08 15:30 | 233 | 233
2017-11-08 16:00 | 239 | 239
2017-11-08 16:30 | 241 | 241
2017-11-08 17:00 | 250 | 250
2017-11-08 17:30 | 257 | 257
2017-11-08 18:00 | 258 | 257
2017-11-08 18:30 | 261 | 260
2017-11-08 19:00 | 271 | 271
2017-11-08 19:30 | 265 | 264
2017-11-08 20:00 | 260 | 260
2017-11-08 20:30 | 256 | 256
2017-11-08 21:00 | 244 | 243
2017-11-08 21:30 | 233 | 232
2017-11-08 22:00 | 224 | 223
2017-11-08 22:30 | 217 | 216
2017-11-08 23:00 | 215 | 214
2017-11-08 23:30 | 201 | 201
2017-11-09 | 184 | 184
2017-11-09 00:30 | 168 | 168
2017-11-09 01:00 | 161 | 160
2017-11-09 01:30 | 155 | 155
2017-11-09 02:00 | 151 | 151
2017-11-09 02:30 | 149 | 149
2017-11-09 03:00 | 148 | 148
2017-11-09 03:30 | 149 | 149
2017-11-09 04:00 | 150 | 150
2017-11-09 04:30 | 155 | 155
2017-11-09 05:00 | 158 | 158
2017-11-09 05:30 | 169 | 169
2017-11-09 06:00 | 182 | 182
2017-11-09 06:30 | 196 | 196
2017-11-09 07:00 | 209 | 209
2017-11-09 07:30 | 216 | 216
2017-11-09 08:00 | 212 | 212
2017-11-09 08:30 | 207 | 206
2017-11-09 09:00 | 204 | 203
2017-11-09 09:30 | 212 | 211
2017-11-09 10:00 | 216 | 216
2017-11-09 10:30 | 212 | 211
2017-11-09 11:00 | 212 | 212
2017-11-09 11:30 | 216 | 215
2017-11-09 12:00 | 217 | 216
2017-11-09 12:30 | 219 | 219
2017-11-09 13:00 | 220 | 219
2017-11-09 13:30 | 207 | 206
2017-11-09 14:00 | 212 | 211
2017-11-09 14:30 | 221 | 220
2017-11-09 15:00 | 219 | 218
2017-11-09 15:30 | 222 | 221
2017-11-09 16:00 | 234 | 233
2017-11-09 16:30 | 244 | 243
2017-11-09 17:00 | 251 | 251
2017-11-09 17:30 | 256 | 255
2017-11-09 18:00 | 258 | 258
2017-11-09 18:30 | 266 | 266
2017-11-09 19:00 | 278 | 277
2017-11-09 19:30 | 272 | 272
2017-11-09 20:00 | 268 | 268
2017-11-09 20:30 | 262 | 262
2017-11-09 21:00 | 249 | 249
2017-11-09 21:30 | 236 | 236
2017-11-09 22:00 | 225 | 225
2017-11-09 22:30 | 218 | 218
2017-11-09 23:00 | 216 | 216
2017-11-09 23:30 | 202 | 202
2017-11-10 | 184 | 184
2017-11-10 00:30 | 170 | 170
2017-11-10 01:00 | 163 | 162
2017-11-10 01:30 | 157 | 157
2017-11-10 02:00 | 154 | 154
2017-11-10 02:30 | 151 | 150
2017-11-10 03:00 | 150 | 149
2017-11-10 03:30 | 151 | 150
2017-11-10 04:00 | 151 | 150
2017-11-10 04:30 | 155 | 154
2017-11-10 05:00 | 159 | 158
2017-11-10 05:30 | 169 | 168
2017-11-10 06:00 | 179 | 179
2017-11-10 06:30 | 194 | 194
2017-11-10 07:00 | 204 | 204
2017-11-10 07:30 | 212 | 212
2017-11-10 08:00 | 226 | 226
2017-11-10 08:30 | 221 | 221
2017-11-10 09:00 | 223 | 223
2017-11-10 09:30 | 223 | 223
2017-11-10 10:00 | 226 | 226
2017-11-10 10:30 | 217 | 216
2017-11-10 11:00 | 204 | 203
2017-11-10 11:30 | 212 | 212
2017-11-10 12:00 | 217 | 217
2017-11-10 12:30 | 211 | 210
2017-11-10 13:00 | 209 | 208
2017-11-10 13:30 | 208 | 207
2017-11-10 14:00 | 204 | 203
2017-11-10 14:30 | 206 | 205
2017-11-10 15:00 | 216 | 215
2017-11-10 15:30 | 219 | 218
2017-11-10 16:00 | 231 | 230
2017-11-10 16:30 | 237 | 236
2017-11-10 17:00 | 243 | 242
2017-11-10 17:30 | 245 | 244
2017-11-10 18:00 | 247 | 245
2017-11-10 18:30 | 250 | 249
2017-11-10 19:00 | 257 | 256
2017-11-10 19:30 | 252 | 250
2017-11-10 20:00 | 249 | 248
2017-11-10 20:30 | 241 | 241
2017-11-10 21:00 | 231 | 231
2017-11-10 21:30 | 221 | 221
2017-11-10 22:00 | 214 | 213
2017-11-10 22:30 | 211 | 211
2017-11-10 23:00 | 210 | 210
2017-11-10 23:30 | 198 | 198
2017-11-11 | 183 | 183
2017-11-11 00:30 | 167 | 167
2017-11-11 01:00 | 158 | 158
2017-11-11 01:30 | 153 | 153
2017-11-11 02:00 | 149 | 148
2017-11-11 02:30 | 147 | 147
2017-11-11 03:00 | 145 | 144
2017-11-11 03:30 | 145 | 144
2017-11-11 04:00 | 145 | 144
2017-11-11 04:30 | 145 | 145
2017-11-11 05:00 | 146 | 145
2017-11-11 05:30 | 148 | 147
2017-11-11 06:00 | 149 | 148
2017-11-11 06:30 | 154 | 153
2017-11-11 07:00 | 157 | 156
2017-11-11 07:30 | 160 | 160
2017-11-11 08:00 | 172 | 172
2017-11-11 08:30 | 180 | 180
2017-11-11 09:00 | 183 | 183
2017-11-11 09:30 | 174 | 173
2017-11-11 10:00 | 173 | 172
2017-11-11 10:30 | 171 | 170
2017-11-11 11:00 | 169 | 168
2017-11-11 11:30 | 160 | 159
2017-11-11 12:00 | 163 | 163
2017-11-11 12:30 | 164 | 163
2017-11-11 13:00 | 160 | 159
2017-11-11 13:30 | 154 | 153
2017-11-11 14:00 | 160 | 160
2017-11-11 14:30 | 170 | 169
2017-11-11 15:00 | 177 | 176
2017-11-11 15:30 | 173 | 173
2017-11-11 16:00 | 180 | 179
2017-11-11 16:30 | 191 | 191
2017-11-11 17:00 | 199 | 198
2017-11-11 17:30 | 208 | 208
2017-11-11 18:00 | 212 | 211
2017-11-11 18:30 | 218 | 218
2017-11-11 19:00 | 229 | 229
2017-11-11 19:30 | 226 | 226
2017-11-11 20:00 | 224 | 224
2017-11-11 20:30 | 222 | 221
2017-11-11 21:00 | 211 | 211
2017-11-11 21:30 | 205 | 204
2017-11-11 22:00 | 199 | 199
2017-11-11 22:30 | 198 | 198
2017-11-11 23:00 | 199 | 199
2017-11-11 23:30 | 189 | 188
2017-11-12 | 176 | 175
2017-11-12 00:30 | 162 | 161
2017-11-12 01:00 | 154 | 152
2017-11-12 01:30 | 148 | 146
2017-11-12 02:00 | 145 | 142
2017-11-12 02:30 | 142 | 140
2017-11-12 03:00 | 142 | 139
2017-11-12 03:30 | 140 | 137
2017-11-12 04:00 | 139 | 135
2017-11-12 04:30 | 140 | 137
2017-11-12 05:00 | 140 | 136
2017-11-12 05:30 | 141 | 137
2017-11-12 06:00 | 138 | 134
2017-11-12 06:30 | 136 | 131
2017-11-12 07:00 | 137 | 133
2017-11-12 07:30 | 139 | 136
2017-11-12 08:00 | 140 | 138
2017-11-12 08:30 | 146 | 145
2017-11-12 09:00 | 151 | 150
2017-11-12 09:30 | 151 | 150
2017-11-12 10:00 | 149 | 148
2017-11-12 10:30 | 145 | 145
2017-11-12 11:00 | 140 | 139
2017-11-12 11:30 | 136 | 136
2017-11-12 12:00 | 135 | 135
2017-11-12 12:30 | 132 | 131
2017-11-12 13:00 | 130 | 130
2017-11-12 13:30 | 134 | 133
2017-11-12 14:00 | 143 | 142
2017-11-12 14:30 | 147 | 146
2017-11-12 15:00 | 154 | 154
2017-11-12 15:30 | 163 | 163
2017-11-12 16:00 | 176 | 175
2017-11-12 16:30 | 189 | 189
2017-11-12 17:00 | 203 | 203
2017-11-12 17:30 | 211 | 211
2017-11-12 18:00 | 218 | 218
2017-11-12 18:30 | 228 | 228
2017-11-12 19:00 | 240 | 240
2017-11-12 19:30 | 237 | 237
2017-11-12 20:00 | 233 | 233
2017-11-12 20:30 | 231 | 230
2017-11-12 21:00 | 220 | 220
2017-11-12 21:30 | 211 | 210
2017-11-12 22:00 | 203 | 203
2017-11-12 22:30 | 199 | 199
2017-11-12 23:00 | 199 | 199
2017-11-12 23:30 | 189 | 189
2017-11-13 | 175 | 174
2017-11-13 00:30 | 162 | 160
2017-11-13 01:00 | 153 | 151
2017-11-13 01:30 | 149 | 147
2017-11-13 02:00 | 147 | 145
2017-11-13 02:30 | 145 | 142
2017-11-13 03:00 | 144 | 141
2017-11-13 03:30 | 145 | 142
2017-11-13 04:00 | 148 | 145
2017-11-13 04:30 | 152 | 150
2017-11-13 05:00 | 156 | 154
2017-11-13 05:30 | 165 | 164
2017-11-13 06:00 | 174 | 173
2017-11-13 06:30 | 188 | 188
2017-11-13 07:00 | 199 | 199
2017-11-13 07:30 | 207 | 207
2017-11-13 08:00 | 211 | 210
2017-11-13 08:30 | 211 | 211
2017-11-13 09:00 | 206 | 206
2017-11-13 09:30 | 204 | 203
2017-11-13 10:00 | 202 | 202
2017-11-13 10:30 | 202 | 202
2017-11-13 11:00 | 199 | 199
2017-11-13 11:30 | 197 | 197
2017-11-13 12:00 | 198 | 198
2017-11-13 12:30 | 196 | 196
2017-11-13 13:00 | 194 | 194
2017-11-13 13:30 | 194 | 194
2017-11-13 14:00 | 197 | 197
2017-11-13 14:30 | 201 | 201
2017-11-13 15:00 | 206 | 206
2017-11-13 15:30 | 214 | 214
2017-11-13 16:00 | 225 | 225
2017-11-13 16:30 | 237 | 237
2017-11-13 17:00 | 251 | 251
2017-11-13 17:30 | 255 | 255
2017-11-13 18:00 | 257 | 257
2017-11-13 18:30 | 260 | 260
2017-11-13 19:00 | 272 | 272
2017-11-13 19:30 | 267 | 267
2017-11-13 20:00 | 263 | 263
2017-11-13 20:30 | 256 | 256
2017-11-13 21:00 | 245 | 244
2017-11-13 21:30 | 234 | 233
2017-11-13 22:00 | 224 | 223
2017-11-13 22:30 | 217 | 217
2017-11-13 23:00 | 213 | 213
2017-11-13 23:30 | 200 | 200
2017-11-14 | 185 | 185
2017-11-14 00:30 | 171 | 170
2017-11-14 01:00 | 163 | 163
2017-11-14 01:30 | 157 | 157
2017-11-14 02:00 | 154 | 154
2017-11-14 02:30 | 152 | 152
2017-11-14 03:00 | 150 | 150
2017-11-14 03:30 | 151 | 151
2017-11-14 04:00 | 151 | 151
2017-11-14 04:30 | 156 | 156
2017-11-14 05:00 | 160 | 159
2017-11-14 05:30 | 170 | 169
2017-11-14 06:00 | 178 | 178
2017-11-14 06:30 | 192 | 192
2017-11-14 07:00 | 204 | 204
2017-11-14 07:30 | 209 | 209
2017-11-14 08:00 | 208 | 207
2017-11-14 08:30 | 206 | 206
2017-11-14 09:00 | 206 | 206
2017-11-14 09:30 | 204 | 204
2017-11-14 10:00 | 200 | 200
2017-11-14 10:30 | 198 | 198
2017-11-14 11:00 | 197 | 197
2017-11-14 11:30 | 196 | 196
2017-11-14 12:00 | 198 | 198
2017-11-14 12:30 | 199 | 199
2017-11-14 13:00 | 200 | 200
2017-11-14 13:30 | 201 | 201
2017-11-14 14:00 | 207 | 207
2017-11-14 14:30 | 209 | 209
2017-11-14 15:00 | 214 | 214
2017-11-14 15:30 | 222 | 222
2017-11-14 16:00 | 232 | 232
2017-11-14 16:30 | 243 | 243
2017-11-14 17:00 | 255 | 255
2017-11-14 17:30 | 259 | 259
2017-11-14 18:00 | 259 | 259
2017-11-14 18:30 | 261 | 261
2017-11-14 19:00 | 273 | 273
2017-11-14 19:30 | 268 | 268
2017-11-14 20:00 | 266 | 266
2017-11-14 20:30 | 261 | 260
2017-11-14 21:00 | 248 | 248
2017-11-14 21:30 | 238 | 237
2017-11-14 22:00 | 228 | 227
2017-11-14 22:30 | 216 | 216
2017-11-14 23:00 | 212 | 212
2017-11-14 23:30 | 198 | 198
2017-11-15 | 181 | 181
2017-11-15 00:30 | 164 | 164
2017-11-15 01:00 | 154 | 154
2017-11-15 01:30 | 150 | 150
2017-11-15 02:00 | 147 | 146
2017-11-15 02:30 | 144 | 143
2017-11-15 03:00 | 143 | 142
2017-11-15 03:30 | 145 | 144
2017-11-15 04:00 | 147 | 146
2017-11-15 04:30 | 151 | 151
2017-11-15 05:00 | 155 | 154
2017-11-15 05:30 | 164 | 164
2017-11-15 06:00 | 173 | 173
2017-11-15 06:30 | 187 | 187
2017-11-15 07:00 | 198 | 197
2017-11-15 07:30 | 203 | 203
2017-11-15 08:00 | 202 | 202
2017-11-15 08:30 | 204 | 204
2017-11-15 09:00 | 203 | 202
2017-11-15 09:30 | 200 | 199
2017-11-15 10:00 | 202 | 202
2017-11-15 10:30 | 206 | 205
2017-11-15 11:00 | 211 | 209
2017-11-15 11:30 | 210 | 209
2017-11-15 12:00 | 211 | 210
2017-11-15 12:30 | 215 | 214
2017-11-15 13:00 | 222 | 220
2017-11-15 13:30 | 234 | 232
2017-11-15 14:00 | 235 | 233
2017-11-15 14:30 | 239 | 237
2017-11-15 15:00 | 231 | 230
2017-11-15 15:30 | 222 | 222
2017-11-15 16:00 | 232 | 231
2017-11-15 16:30 | 240 | 240
2017-11-15 17:00 | 251 | 250
2017-11-15 17:30 | 254 | 253
2017-11-15 18:00 | 255 | 253
2017-11-15 18:30 | 257 | 255
2017-11-15 19:00 | 269 | 269
2017-11-15 19:30 | 264 | 264
2017-11-15 20:00 | 261 | 261
2017-11-15 20:30 | 257 | 257
2017-11-15 21:00 | 245 | 245
2017-11-15 21:30 | 233 | 233
2017-11-15 22:00 | 221 | 221
2017-11-15 22:30 | 212 | 212
2017-11-15 23:00 | 210 | 209
2017-11-15 23:30 | 197 | 197
2017-11-16 | 180 | 180
2017-11-16 00:30 | 165 | 165
2017-11-16 01:00 | 157 | 156
2017-11-16 01:30 | 152 | 152
2017-11-16 02:00 | 149 | 148
2017-11-16 02:30 | 146 | 146
2017-11-16 03:00 | 145 | 145
2017-11-16 03:30 | 146 | 146
2017-11-16 04:00 | 150 | 150
2017-11-16 04:30 | 155 | 155
2017-11-16 05:00 | 159 | 159
2017-11-16 05:30 | 168 | 168
2017-11-16 06:00 | 178 | 178
2017-11-16 06:30 | 192 | 192
2017-11-16 07:00 | 206 | 205
2017-11-16 07:30 | 216 | 216
2017-11-16 08:00 | 219 | 218
2017-11-16 08:30 | 221 | 221
2017-11-16 09:00 | 215 | 215
2017-11-16 09:30 | 219 | 219
2017-11-16 10:00 | 224 | 224
2017-11-16 10:30 | 219 | 219
2017-11-16 11:00 | 221 | 221
2017-11-16 11:30 | 223 | 223
2017-11-16 12:00 | 221 | 221
2017-11-16 12:30 | 219 | 219
2017-11-16 13:00 | 222 | 222
2017-11-16 13:30 | 226 | 226
2017-11-16 14:00 | 232 | 232
2017-11-16 14:30 | 239 | 239
2017-11-16 15:00 | 244 | 244
2017-11-16 15:30 | 246 | 246
2017-11-16 16:00 | 245 | 245
2017-11-16 16:30 | 251 | 251
2017-11-16 17:00 | 264 | 264
2017-11-16 17:30 | 265 | 265
2017-11-16 18:00 | 263 | 263
2017-11-16 18:30 | 266 | 266
2017-11-16 19:00 | 278 | 278
2017-11-16 19:30 | 274 | 274
2017-11-16 20:00 | 270 | 270
2017-11-16 20:30 | 264 | 263
2017-11-16 21:00 | 250 | 249
2017-11-16 21:30 | 237 | 236
2017-11-16 22:00 | 226 | 226
2017-11-16 22:30 | 221 | 220
2017-11-16 23:00 | 218 | 218
2017-11-16 23:30 | 205 | 204
2017-11-17 | 188 | 188
2017-11-17 00:30 | 172 | 172
2017-11-17 01:00 | 164 | 164
2017-11-17 01:30 | 159 | 158
2017-11-17 02:00 | 155 | 155
2017-11-17 02:30 | 153 | 153
2017-11-17 03:00 | 152 | 152
2017-11-17 03:30 | 153 | 152
2017-11-17 04:00 | 154 | 153
2017-11-17 04:30 | 157 | 157
2017-11-17 05:00 | 161 | 161
2017-11-17 05:30 | 170 | 170
2017-11-17 06:00 | 180 | 180
2017-11-17 06:30 | 195 | 195
2017-11-17 07:00 | 206 | 205
2017-11-17 07:30 | 220 | 220
2017-11-17 08:00 | 227 | 226
2017-11-17 08:30 | 228 | 228
2017-11-17 09:00 | 227 | 227
2017-11-17 09:30 | 226 | 226
2017-11-17 10:00 | 225 | 225
2017-11-17 10:30 | 221 | 221
2017-11-17 11:00 | 214 | 214
2017-11-17 11:30 | 208 | 208
2017-11-17 12:00 | 210 | 210
2017-11-17 12:30 | 213 | 213
2017-11-17 13:00 | 217 | 217
2017-11-17 13:30 | 219 | 219
2017-11-17 14:00 | 220 | 220
2017-11-17 14:30 | 221 | 221
2017-11-17 15:00 | 226 | 226
2017-11-17 15:30 | 231 | 231
2017-11-17 16:00 | 241 | 241
2017-11-17 16:30 | 247 | 247
2017-11-17 17:00 | 252 | 252
2017-11-17 17:30 | 251 | 251
2017-11-17 18:00 | 246 | 246
2017-11-17 18:30 | 246 | 245
2017-11-17 19:00 | 259 | 258
2017-11-17 19:30 | 255 | 254
2017-11-17 20:00 | 253 | 251
2017-11-17 20:30 | 248 | 247
2017-11-17 21:00 | 236 | 235
2017-11-17 21:30 | 225 | 225
2017-11-17 22:00 | 218 | 218
2017-11-17 22:30 | 215 | 214
2017-11-17 23:00 | 215 | 214
2017-11-17 23:30 | 202 | 202
2017-11-18 | 186 | 186
2017-11-18 00:30 | 171 | 171
2017-11-18 01:00 | 164 | 163
2017-11-18 01:30 | 157 | 157
2017-11-18 02:00 | 153 | 153
2017-11-18 02:30 | 151 | 150
2017-11-18 03:00 | 149 | 148
2017-11-18 03:30 | 148 | 148
2017-11-18 04:00 | 148 | 148
2017-11-18 04:30 | 149 | 149
2017-11-18 05:00 | 150 | 149
2017-11-18 05:30 | 151 | 150
2017-11-18 06:00 | 155 | 154
2017-11-18 06:30 | 162 | 162
2017-11-18 07:00 | 171 | 171
2017-11-18 07:30 | 179 | 179
2017-11-18 08:00 | 185 | 185
2017-11-18 08:30 | 200 | 199
2017-11-18 09:00 | 209 | 209
2017-11-18 09:30 | 217 | 216
2017-11-18 10:00 | 219 | 218
2017-11-18 10:30 | 217 | 216
2017-11-18 11:00 | 217 | 216
2017-11-18 11:30 | 215 | 214
2017-11-18 12:00 | 213 | 212
2017-11-18 12:30 | 209 | 208
2017-11-18 13:00 | 211 | 210
2017-11-18 13:30 | 210 | 210
2017-11-18 14:00 | 207 | 206
2017-11-18 14:30 | 206 | 206
2017-11-18 15:00 | 209 | 209
2017-11-18 15:30 | 210 | 210
2017-11-18 16:00 | 212 | 211
2017-11-18 16:30 | 213 | 213
2017-11-18 17:00 | 218 | 218
2017-11-18 17:30 | 218 | 217
2017-11-18 18:00 | 217 | 217
2017-11-18 18:30 | 222 | 222
2017-11-18 19:00 | 234 | 232
2017-11-18 19:30 | 229 | 228
2017-11-18 20:00 | 226 | 225
2017-11-18 20:30 | 223 | 223
2017-11-18 21:00 | 213 | 213
2017-11-18 21:30 | 206 | 206
2017-11-18 22:00 | 200 | 200
2017-11-18 22:30 | 199 | 199
2017-11-18 23:00 | 200 | 200
2017-11-18 23:30 | 190 | 190
2017-11-19 | 177 | 176
2017-11-19 00:30 | 162 | 162
2017-11-19 01:00 | 153 | 153
2017-11-19 01:30 | 147 | 147
2017-11-19 02:00 | 142 | 142
2017-11-19 02:30 | 139 | 139
2017-11-19 03:00 | 137 | 137
2017-11-19 03:30 | 137 | 136
2017-11-19 04:00 | 136 | 136
2017-11-19 04:30 | 135 | 134
2017-11-19 05:00 | 134 | 134
2017-11-19 05:30 | 134 | 134
2017-11-19 06:00 | 135 | 135
2017-11-19 06:30 | 135 | 135
2017-11-19 07:00 | 135 | 135
2017-11-19 07:30 | 141 | 141
2017-11-19 08:00 | 154 | 153
2017-11-19 08:30 | 169 | 168
2017-11-19 09:00 | 175 | 173
2017-11-19 09:30 | 176 | 174
2017-11-19 10:00 | 175 | 174
2017-11-19 10:30 | 168 | 167
2017-11-19 11:00 | 172 | 171
2017-11-19 11:30 | 177 | 176
2017-11-19 12:00 | 185 | 184
2017-11-19 12:30 | 187 | 186
2017-11-19 13:00 | 181 | 180
2017-11-19 13:30 | 173 | 173
2017-11-19 14:00 | 168 | 167
2017-11-19 14:30 | 165 | 165
2017-11-19 15:00 | 170 | 170
2017-11-19 15:30 | 174 | 174
2017-11-19 16:00 | 177 | 177
2017-11-19 16:30 | 189 | 188
2017-11-19 17:00 | 200 | 199
2017-11-19 17:30 | 207 | 206
2017-11-19 18:00 | 215 | 214
2017-11-19 18:30 | 226 | 225
2017-11-19 19:00 | 239 | 238
2017-11-19 19:30 | 236 | 235
2017-11-19 20:00 | 233 | 232
2017-11-19 20:30 | 230 | 230
2017-11-19 21:00 | 220 | 219
2017-11-19 21:30 | 209 | 209
2017-11-19 22:00 | 202 | 202
2017-11-19 22:30 | 198 | 198
2017-11-19 23:00 | 198 | 198
2017-11-19 23:30 | 188 | 188
2017-11-20 | 173 | 173
2017-11-20 00:30 | 160 | 160
2017-11-20 01:00 | 151 | 151
2017-11-20 01:30 | 146 | 145
2017-11-20 02:00 | 142 | 142
2017-11-20 02:30 | 140 | 140
2017-11-20 03:00 | 140 | 140
2017-11-20 03:30 | 140 | 140
2017-11-20 04:00 | 139 | 139
2017-11-20 04:30 | 145 | 145
2017-11-20 05:00 | 150 | 150
2017-11-20 05:30 | 161 | 161
2017-11-20 06:00 | 172 | 172
2017-11-20 06:30 | 190 | 189
2017-11-20 07:00 | 202 | 201
2017-11-20 07:30 | 208 | 208
2017-11-20 08:00 | 203 | 202
2017-11-20 08:30 | 199 | 198
2017-11-20 09:00 | 196 | 195
2017-11-20 09:30 | 196 | 195
2017-11-20 10:00 | 200 | 198
2017-11-20 10:30 | 200 | 199
2017-11-20 11:00 | 196 | 193
2017-11-20 11:30 | 196 | 193
2017-11-20 12:00 | 197 | 194
2017-11-20 12:30 | 199 | 196
2017-11-20 13:00 | 203 | 202
2017-11-20 13:30 | 205 | 205
2017-11-20 14:00 | 212 | 211
2017-11-20 14:30 | 218 | 218
2017-11-20 15:00 | 222 | 222
2017-11-20 15:30 | 226 | 226
2017-11-20 16:00 | 235 | 235
2017-11-20 16:30 | 248 | 247
2017-11-20 17:00 | 257 | 257
2017-11-20 17:30 | 260 | 260
2017-11-20 18:00 | 260 | 260
2017-11-20 18:30 | 266 | 266
2017-11-20 19:00 | 276 | 275
2017-11-20 19:30 | 267 | 267
2017-11-20 20:00 | 259 | 259
2017-11-20 20:30 | 255 | 255
2017-11-20 21:00 | 243 | 243
2017-11-20 21:30 | 231 | 231
2017-11-20 22:00 | 222 | 220
2017-11-20 22:30 | 216 | 214
2017-11-20 23:00 | 218 | 217
2017-11-20 23:30 | 207 | 206
2017-11-21 | 188 | 187
2017-11-21 00:30 | 169 | 169
2017-11-21 01:00 | 161 | 161
2017-11-21 01:30 | 156 | 156
2017-11-21 02:00 | 152 | 152
2017-11-21 02:30 | 149 | 149
2017-11-21 03:00 | 148 | 148
2017-11-21 03:30 | 149 | 149
2017-11-21 04:00 | 150 | 150
2017-11-21 04:30 | 154 | 154
2017-11-21 05:00 | 159 | 159
2017-11-21 05:30 | 168 | 168
2017-11-21 06:00 | 178 | 178
2017-11-21 06:30 | 193 | 192
2017-11-21 07:00 | 203 | 203
2017-11-21 07:30 | 211 | 210
2017-11-21 08:00 | 210 | 209
2017-11-21 08:30 | 214 | 214
2017-11-21 09:00 | 214 | 214
2017-11-21 09:30 | 211 | 209
2017-11-21 10:00 | 203 | 202
2017-11-21 10:30 | 202 | 200
2017-11-21 11:00 | 200 | 198
2017-11-21 11:30 | 207 | 204
2017-11-21 12:00 | 219 | 216
2017-11-21 12:30 | 219 | 216
2017-11-21 13:00 | 208 | 206
2017-11-21 13:30 | 206 | 204
2017-11-21 14:00 | 223 | 221
2017-11-21 14:30 | 227 | 225
2017-11-21 15:00 | 226 | 224
2017-11-21 15:30 | 223 | 222
2017-11-21 16:00 | 232 | 231
2017-11-21 16:30 | 240 | 240
2017-11-21 17:00 | 248 | 247
2017-11-21 17:30 | 253 | 252
2017-11-21 18:00 | 254 | 253
2017-11-21 18:30 | 258 | 256
2017-11-21 19:00 | 271 | 269
2017-11-21 19:30 | 267 | 265
2017-11-21 20:00 | 264 | 262
2017-11-21 20:30 | 260 | 258
2017-11-21 21:00 | 248 | 246
2017-11-21 21:30 | 236 | 235
2017-11-21 22:00 | 224 | 223
2017-11-21 22:30 | 218 | 217
2017-11-21 23:00 | 215 | 214
2017-11-21 23:30 | 202 | 201
2017-11-22 | 186 | 185
2017-11-22 00:30 | 171 | 171
2017-11-22 01:00 | 162 | 162
2017-11-22 01:30 | 156 | 156
2017-11-22 02:00 | 152 | 152
2017-11-22 02:30 | 148 | 148
2017-11-22 03:00 | 146 | 146
2017-11-22 03:30 | 146 | 146
2017-11-22 04:00 | 146 | 146
2017-11-22 04:30 | 148 | 148
2017-11-22 05:00 | 155 | 155
2017-11-22 05:30 | 167 | 167
2017-11-22 06:00 | 175 | 175
2017-11-22 06:30 | 192 | 192
2017-11-22 07:00 | 205 | 205
2017-11-22 07:30 | 213 | 213
2017-11-22 08:00 | 213 | 212
2017-11-22 08:30 | 214 | 214
2017-11-22 09:00 | 207 | 207
2017-11-22 09:30 | 207 | 207
2017-11-22 10:00 | 201 | 201
2017-11-22 10:30 | 200 | 200
2017-11-22 11:00 | 198 | 198
2017-11-22 11:30 | 201 | 201
2017-11-22 12:00 | 201 | 201
2017-11-22 12:30 | 202 | 202
2017-11-22 13:00 | 195 | 195
2017-11-22 13:30 | 199 | 198
2017-11-22 14:00 | 209 | 209
2017-11-22 14:30 | 216 | 216
2017-11-22 15:00 | 213 | 213
2017-11-22 15:30 | 221 | 221
2017-11-22 16:00 | 236 | 235
2017-11-22 16:30 | 245 | 244
2017-11-22 17:00 | 254 | 254
2017-11-22 17:30 | 258 | 258
2017-11-22 18:00 | 260 | 259
2017-11-22 18:30 | 260 | 260
2017-11-22 19:00 | 270 | 270
2017-11-22 19:30 | 266 | 266
2017-11-22 20:00 | 263 | 263
2017-11-22 20:30 | 256 | 256
2017-11-22 21:00 | 245 | 244
2017-11-22 21:30 | 232 | 232
2017-11-22 22:00 | 222 | 222
2017-11-22 22:30 | 216 | 216
2017-11-22 23:00 | 219 | 218
2017-11-22 23:30 | 208 | 207
2017-11-23 | 189 | 189
2017-11-23 00:30 | 170 | 170
2017-11-23 01:00 | 159 | 159
2017-11-23 01:30 | 154 | 154
2017-11-23 02:00 | 151 | 151
2017-11-23 02:30 | 149 | 149
2017-11-23 03:00 | 147 | 147
2017-11-23 03:30 | 148 | 148
2017-11-23 04:00 | 149 | 149
2017-11-23 04:30 | 153 | 153
2017-11-23 05:00 | 157 | 157
2017-11-23 05:30 | 167 | 167
2017-11-23 06:00 | 175 | 175
2017-11-23 06:30 | 190 | 189
2017-11-23 07:00 | 201 | 200
2017-11-23 07:30 | 211 | 210
2017-11-23 08:00 | 213 | 212
2017-11-23 08:30 | 216 | 216
2017-11-23 09:00 | 214 | 214
2017-11-23 09:30 | 214 | 214
2017-11-23 10:00 | 215 | 214
2017-11-23 10:30 | 209 | 208
2017-11-23 11:00 | 207 | 207
2017-11-23 11:30 | 210 | 209
2017-11-23 12:00 | 209 | 208
2017-11-23 12:30 | 208 | 207
2017-11-23 13:00 | 207 | 206
2017-11-23 13:30 | 210 | 209
2017-11-23 14:00 | 214 | 213
2017-11-23 14:30 | 218 | 217
2017-11-23 15:00 | 224 | 221
2017-11-23 15:30 | 230 | 227
2017-11-23 16:00 | 240 | 237
2017-11-23 16:30 | 248 | 246
2017-11-23 17:00 | 259 | 256
2017-11-23 17:30 | 264 | 261
2017-11-23 18:00 | 265 | 262
2017-11-23 18:30 | 265 | 262
2017-11-23 19:00 | 277 | 276
2017-11-23 19:30 | 275 | 274
2017-11-23 20:00 | 273 | 271
2017-11-23 20:30 | 268 | 266
2017-11-23 21:00 | 257 | 256
2017-11-23 21:30 | 243 | 242
2017-11-23 22:00 | 232 | 231
2017-11-23 22:30 | 226 | 225
2017-11-23 23:00 | 222 | 220
2017-11-23 23:30 | 209 | 207
2017-11-24 | 192 | 190
2017-11-24 00:30 | 175 | 174
2017-11-24 01:00 | 167 | 165
2017-11-24 01:30 | 161 | 160
2017-11-24 02:00 | 157 | 156
2017-11-24 02:30 | 153 | 152
2017-11-24 03:00 | 152 | 152
2017-11-24 03:30 | 152 | 152
2017-11-24 04:00 | 152 | 152
2017-11-24 04:30 | 156 | 156
2017-11-24 05:00 | 160 | 160
2017-11-24 05:30 | 169 | 169
2017-11-24 06:00 | 179 | 179
2017-11-24 06:30 | 194 | 193
2017-11-24 07:00 | 206 | 205
2017-11-24 07:30 | 212 | 211
2017-11-24 08:00 | 212 | 211
2017-11-24 08:30 | 211 | 210
2017-11-24 09:00 | 214 | 212
2017-11-24 09:30 | 213 | 211
2017-11-24 10:00 | 215 | 213
2017-11-24 10:30 | 217 | 214
2017-11-24 11:00 | 216 | 213
2017-11-24 11:30 | 218 | 214
2017-11-24 12:00 | 217 | 213
2017-11-24 12:30 | 216 | 212
2017-11-24 13:00 | 216 | 213
2017-11-24 13:30 | 221 | 217
2017-11-24 14:00 | 226 | 222
2017-11-24 14:30 | 231 | 227
2017-11-24 15:00 | 235 | 231
2017-11-24 15:30 | 241 | 237
2017-11-24 16:00 | 251 | 247
2017-11-24 16:30 | 261 | 260
2017-11-24 17:00 | 270 | 270
2017-11-24 17:30 | 269 | 269
2017-11-24 18:00 | 264 | 264
2017-11-24 18:30 | 260 | 260
2017-11-24 19:00 | 269 | 269
2017-11-24 19:30 | 268 | 268
2017-11-24 20:00 | 265 | 265
2017-11-24 20:30 | 258 | 258
2017-11-24 21:00 | 245 | 243
2017-11-24 21:30 | 234 | 234
2017-11-24 22:00 | 226 | 226
2017-11-24 22:30 | 221 | 220
2017-11-24 23:00 | 219 | 219
2017-11-24 23:30 | 207 | 207
2017-11-25 | 189 | 189
2017-11-25 00:30 | 175 | 175
2017-11-25 01:00 | 166 | 166
2017-11-25 01:30 | 160 | 160
2017-11-25 02:00 | 156 | 156
2017-11-25 02:30 | 153 | 153
2017-11-25 03:00 | 151 | 151
2017-11-25 03:30 | 151 | 151
2017-11-25 04:00 | 149 | 149
2017-11-25 04:30 | 149 | 149
2017-11-25 05:00 | 148 | 148
2017-11-25 05:30 | 150 | 150
2017-11-25 06:00 | 152 | 152
2017-11-25 06:30 | 157 | 157
2017-11-25 07:00 | 160 | 160
2017-11-25 07:30 | 166 | 165
2017-11-25 08:00 | 172 | 172
2017-11-25 08:30 | 179 | 179
2017-11-25 09:00 | 187 | 186
2017-11-25 09:30 | 190 | 190
2017-11-25 10:00 | 189 | 189
2017-11-25 10:30 | 186 | 186
2017-11-25 11:00 | 184 | 184
2017-11-25 11:30 | 183 | 183
2017-11-25 12:00 | 179 | 179
2017-11-25 12:30 | 181 | 181
2017-11-25 13:00 | 185 | 185
2017-11-25 13:30 | 185 | 184
2017-11-25 14:00 | 188 | 187
2017-11-25 14:30 | 196 | 195
2017-11-25 15:00 | 207 | 206
2017-11-25 15:30 | 217 | 216
2017-11-25 16:00 | 221 | 220
2017-11-25 16:30 | 229 | 228
2017-11-25 17:00 | 233 | 232
2017-11-25 17:30 | 230 | 230
2017-11-25 18:00 | 231 | 231
2017-11-25 18:30 | 233 | 233
2017-11-25 19:00 | 243 | 243
2017-11-25 19:30 | 243 | 243
2017-11-25 20:00 | 241 | 240
2017-11-25 20:30 | 237 | 237
2017-11-25 21:00 | 228 | 227
2017-11-25 21:30 | 220 | 219
2017-11-25 22:00 | 214 | 214
2017-11-25 22:30 | 212 | 212
2017-11-25 23:00 | 212 | 212
2017-11-25 23:30 | 201 | 201
2017-11-26 | 185 | 185
2017-11-26 00:30 | 171 | 171
2017-11-26 01:00 | 164 | 164
2017-11-26 01:30 | 157 | 157
2017-11-26 02:00 | 152 | 152
2017-11-26 02:30 | 150 | 149
2017-11-26 03:00 | 148 | 148
2017-11-26 03:30 | 147 | 146
2017-11-26 04:00 | 146 | 145
2017-11-26 04:30 | 145 | 145
2017-11-26 05:00 | 141 | 140
2017-11-26 05:30 | 142 | 141
2017-11-26 06:00 | 143 | 142
2017-11-26 06:30 | 143 | 142
2017-11-26 07:00 | 144 | 144
2017-11-26 07:30 | 151 | 151
2017-11-26 08:00 | 163 | 163
2017-11-26 08:30 | 173 | 173
2017-11-26 09:00 | 179 | 179
2017-11-26 09:30 | 177 | 177
2017-11-26 10:00 | 173 | 173
2017-11-26 10:30 | 171 | 171
2017-11-26 11:00 | 170 | 169
2017-11-26 11:30 | 168 | 168
2017-11-26 12:00 | 169 | 169
2017-11-26 12:30 | 172 | 171
2017-11-26 13:00 | 175 | 175
2017-11-26 13:30 | 179 | 178
2017-11-26 14:00 | 185 | 184
2017-11-26 14:30 | 191 | 190
2017-11-26 15:00 | 196 | 196
2017-11-26 15:30 | 206 | 205
2017-11-26 16:00 | 222 | 221
2017-11-26 16:30 | 233 | 233
2017-11-26 17:00 | 241 | 241
2017-11-26 17:30 | 246 | 246
2017-11-26 18:00 | 248 | 248
2017-11-26 18:30 | 250 | 250
2017-11-26 19:00 | 260 | 260
2017-11-26 19:30 | 258 | 258
2017-11-26 20:00 | 254 | 253
2017-11-26 20:30 | 250 | 248
2017-11-26 21:00 | 237 | 236
2017-11-26 21:30 | 227 | 226
2017-11-26 22:00 | 218 | 218
2017-11-26 22:30 | 212 | 212
2017-11-26 23:00 | 209 | 209
2017-11-26 23:30 | 197 | 197
2017-11-27 | 182 | 182
2017-11-27 00:30 | 168 | 168
2017-11-27 01:00 | 161 | 161
2017-11-27 01:30 | 156 | 156
2017-11-27 02:00 | 153 | 153
2017-11-27 02:30 | 151 | 151
2017-11-27 03:00 | 150 | 150
2017-11-27 03:30 | 150 | 150
2017-11-27 04:00 | 151 | 151
2017-11-27 04:30 | 155 | 155
2017-11-27 05:00 | 159 | 158
2017-11-27 05:30 | 168 | 168
2017-11-27 06:00 | 178 | 178
2017-11-27 06:30 | 199 | 198
2017-11-27 07:00 | 212 | 212
2017-11-27 07:30 | 227 | 227
2017-11-27 08:00 | 235 | 234
2017-11-27 08:30 | 241 | 241
2017-11-27 09:00 | 242 | 242
2017-11-27 09:30 | 241 | 240
2017-11-27 10:00 | 242 | 240
2017-11-27 10:30 | 245 | 243
2017-11-27 11:00 | 247 | 245
2017-11-27 11:30 | 248 | 245
2017-11-27 12:00 | 249 | 246
2017-11-27 12:30 | 245 | 243
2017-11-27 13:00 | 245 | 243
2017-11-27 13:30 | 247 | 244
2017-11-27 14:00 | 254 | 251
2017-11-27 14:30 | 260 | 257
2017-11-27 15:00 | 265 | 262
2017-11-27 15:30 | 271 | 269
2017-11-27 16:00 | 281 | 279
2017-11-27 16:30 | 290 | 289
2017-11-27 17:00 | 298 | 297
2017-11-27 17:30 | 297 | 297
2017-11-27 18:00 | 292 | 292
2017-11-27 18:30 | 288 | 287
2017-11-27 19:00 | 299 | 297
2017-11-27 19:30 | 296 | 296
2017-11-27 20:00 | 289 | 289
2017-11-27 20:30 | 282 | 282
2017-11-27 21:00 | 266 | 265
2017-11-27 21:30 | 254 | 253
2017-11-27 22:00 | 243 | 243
2017-11-27 22:30 | 234 | 234
2017-11-27 23:00 | 230 | 230
2017-11-27 23:30 | 216 | 216
2017-11-28 | 199 | 199
2017-11-28 00:30 | 185 | 185
2017-11-28 01:00 | 176 | 176
2017-11-28 01:30 | 171 | 171
2017-11-28 02:00 | 167 | 167
2017-11-28 02:30 | 165 | 165
2017-11-28 03:00 | 163 | 163
2017-11-28 03:30 | 163 | 163
2017-11-28 04:00 | 166 | 166
2017-11-28 04:30 | 172 | 172
2017-11-28 05:00 | 175 | 174
2017-11-28 05:30 | 185 | 185
2017-11-28 06:00 | 194 | 194
2017-11-28 06:30 | 209 | 209
2017-11-28 07:00 | 223 | 223
2017-11-28 07:30 | 239 | 238
2017-11-28 08:00 | 247 | 246
2017-11-28 08:30 | 250 | 249
2017-11-28 09:00 | 250 | 248
2017-11-28 09:30 | 256 | 254
2017-11-28 10:00 | 257 | 255
2017-11-28 10:30 | 257 | 255
2017-11-28 11:00 | 259 | 258
2017-11-28 11:30 | 263 | 263
2017-11-28 12:00 | 269 | 269
2017-11-28 12:30 | 280 | 279
2017-11-28 13:00 | 278 | 278
2017-11-28 13:30 | 284 | 284
2017-11-28 14:00 | 291 | 290
2017-11-28 14:30 | 291 | 291
2017-11-28 15:00 | 287 | 286
2017-11-28 15:30 | 290 | 290
2017-11-28 16:00 | 296 | 295
2017-11-28 16:30 | 306 | 306
2017-11-28 17:00 | 306 | 306
2017-11-28 17:30 | 306 | 306
2017-11-28 18:00 | 302 | 302
2017-11-28 18:30 | 301 | 300
2017-11-28 19:00 | 310 | 309
2017-11-28 19:30 | 306 | 303
2017-11-28 20:00 | 302 | 300
2017-11-28 20:30 | 295 | 294
2017-11-28 21:00 | 280 | 277
2017-11-28 21:30 | 264 | 262
2017-11-28 22:00 | 252 | 251
2017-11-28 22:30 | 243 | 242
2017-11-28 23:00 | 238 | 236
2017-11-28 23:30 | 224 | 222
2017-11-29 | 205 | 203
2017-11-29 00:30 | 189 | 188
2017-11-29 01:00 | 181 | 180
2017-11-29 01:30 | 175 | 174
2017-11-29 02:00 | 171 | 170
2017-11-29 02:30 | 169 | 169
2017-11-29 03:00 | 166 | 166
2017-11-29 03:30 | 166 | 166
2017-11-29 04:00 | 168 | 168
2017-11-29 04:30 | 171 | 170
2017-11-29 05:00 | 176 | 176
2017-11-29 05:30 | 187 | 187
2017-11-29 06:00 | 199 | 198
2017-11-29 06:30 | 222 | 221
2017-11-29 07:00 | 239 | 239
2017-11-29 07:30 | 262 | 262
2017-11-29 08:00 | 272 | 272
2017-11-29 08:30 | 277 | 277
2017-11-29 09:00 | 278 | 278
2017-11-29 09:30 | 283 | 283
2017-11-29 10:00 | 284 | 284
2017-11-29 10:30 | 285 | 285
2017-11-29 11:00 | 287 | 287
2017-11-29 11:30 | 286 | 286
2017-11-29 12:00 | 284 | 284
2017-11-29 12:30 | 282 | 282
2017-11-29 13:00 | 280 | 280
2017-11-29 13:30 | 277 | 277
2017-11-29 14:00 | 275 | 275
2017-11-29 14:30 | 270 | 270
2017-11-29 15:00 | 269 | 269
2017-11-29 15:30 | 271 | 271
2017-11-29 16:00 | 274 | 274
2017-11-29 16:30 | 278 | 278
2017-11-29 17:00 | 285 | 285
2017-11-29 17:30 | 285 | 285
2017-11-29 18:00 | 282 | 282
2017-11-29 18:30 | 282 | 282
2017-11-29 19:00 | 292 | 292
2017-11-29 19:30 | 286 | 286
2017-11-29 20:00 | 281 | 280
2017-11-29 20:30 | 274 | 274
2017-11-29 21:00 | 261 | 261
2017-11-29 21:30 | 249 | 249
2017-11-29 22:00 | 239 | 239
2017-11-29 22:30 | 230 | 230
2017-11-29 23:00 | 226 | 226
2017-11-29 23:30 | 215 | 215
2017-11-30 | 197 | 197
2017-11-30 00:30 | 181 | 181
2017-11-30 01:00 | 173 | 173
2017-11-30 01:30 | 168 | 168
2017-11-30 02:00 | 164 | 164
2017-11-30 02:30 | 161 | 161
2017-11-30 03:00 | 161 | 160
2017-11-30 03:30 | 160 | 160
2017-11-30 04:00 | 163 | 163
2017-11-30 04:30 | 169 | 169
2017-11-30 05:00 | 174 | 174
2017-11-30 05:30 | 182 | 182
2017-11-30 06:00 | 192 | 192
2017-11-30 06:30 | 196 | 196
2017-11-30 07:00 | 208 | 207
2017-11-30 07:30 | 221 | 221
2017-11-30 08:00 | 230 | 230
2017-11-30 08:30 | 228 | 228
2017-11-30 09:00 | 228 | 228
2017-11-30 09:30 | 238 | 237
2017-11-30 10:00 | 242 | 241
2017-11-30 10:30 | 237 | 237
2017-11-30 11:00 | 235 | 235
2017-11-30 11:30 | 229 | 229
2017-11-30 12:00 | 234 | 234
2017-11-30 12:30 | 244 | 243
2017-11-30 13:00 | 244 | 243
2017-11-30 13:30 | 245 | 244
2017-11-30 14:00 | 259 | 259
2017-11-30 14:30 | 260 | 260
2017-11-30 15:00 | 259 | 258
2017-11-30 15:30 | 255 | 254
2017-11-30 16:00 | 257 | 257
2017-11-30 16:30 | 262 | 261
2017-11-30 17:00 | 268 | 267
2017-11-30 17:30 | 267 | 267
2017-11-30 18:00 | 274 | 274
2017-11-30 18:30 | 283 | 283
2017-11-30 19:00 | 291 | 291
2017-11-30 19:30 | 289 | 289
2017-11-30 20:00 | 287 | 287
2017-11-30 20:30 | 282 | 282
2017-11-30 21:00 | 271 | 271
2017-11-30 21:30 | 256 | 256
2017-11-30 22:00 | 244 | 244
2017-11-30 22:30 | 235 | 235
2017-11-30 23:00 | 232 | 232
2017-11-30 23:30 | 216 | 216
2017-12-01 | 198 | 198
2017-12-01 00:30 | 182 | 181
2017-12-01 01:00 | 173 | 173
2017-12-01 01:30 | 169 | 168
2017-12-01 02:00 | 165 | 165
2017-12-01 02:30 | 163 | 163
2017-12-01 03:00 | 162 | 162
2017-12-01 03:30 | 162 | 162
2017-12-01 04:00 | 162 | 162
2017-12-01 04:30 | 166 | 166
2017-12-01 05:00 | 169 | 169
2017-12-01 05:30 | 179 | 178
2017-12-01 06:00 | 189 | 189
2017-12-01 06:30 | 208 | 206
2017-12-01 07:00 | 223 | 221
2017-12-01 07:30 | 235 | 235
2017-12-01 08:00 | 240 | 239
2017-12-01 08:30 | 241 | 240
2017-12-01 09:00 | 245 | 243
2017-12-01 09:30 | 247 | 247
2017-12-01 10:00 | 248 | 248
2017-12-01 10:30 | 248 | 248
2017-12-01 11:00 | 249 | 249
2017-12-01 11:30 | 245 | 245
2017-12-01 12:00 | 247 | 247
2017-12-01 12:30 | 248 | 248
2017-12-01 13:00 | 249 | 249
2017-12-01 13:30 | 251 | 251
2017-12-01 14:00 | 255 | 255
2017-12-01 14:30 | 257 | 257
2017-12-01 15:00 | 259 | 259
2017-12-01 15:30 | 267 | 267
2017-12-01 16:00 | 275 | 275
2017-12-01 16:30 | 281 | 281
2017-12-01 17:00 | 287 | 287
2017-12-01 17:30 | 284 | 284
2017-12-01 18:00 | 275 | 275
2017-12-01 18:30 | 271 | 270
2017-12-01 19:00 | 279 | 279
2017-12-01 19:30 | 280 | 279
2017-12-01 20:00 | 278 | 278
2017-12-01 20:30 | 272 | 271
2017-12-01 21:00 | 259 | 258
2017-12-01 21:30 | 249 | 248
2017-12-01 22:00 | 239 | 239
2017-12-01 22:30 | 235 | 235
2017-12-01 23:00 | 232 | 232
2017-12-01 23:30 | 217 | 217
2017-12-02 | 200 | 200
2017-12-02 00:30 | 185 | 185
2017-12-02 01:00 | 175 | 175
2017-12-02 01:30 | 169 | 169
2017-12-02 02:00 | 164 | 164
2017-12-02 02:30 | 161 | 161
2017-12-02 03:00 | 159 | 159
2017-12-02 03:30 | 159 | 159
2017-12-02 04:00 | 158 | 158
2017-12-02 04:30 | 158 | 158
2017-12-02 05:00 | 157 | 156
2017-12-02 05:30 | 160 | 159
2017-12-02 06:00 | 161 | 161
2017-12-02 06:30 | 166 | 166
2017-12-02 07:00 | 173 | 173
2017-12-02 07:30 | 183 | 183
2017-12-02 08:00 | 190 | 190
2017-12-02 08:30 | 198 | 197
2017-12-02 09:00 | 207 | 206
2017-12-02 09:30 | 214 | 212
2017-12-02 10:00 | 214 | 212
2017-12-02 10:30 | 213 | 211
2017-12-02 11:00 | 202 | 200
2017-12-02 11:30 | 197 | 195
2017-12-02 12:00 | 196 | 195
2017-12-02 12:30 | 195 | 193
2017-12-02 13:00 | 197 | 195
2017-12-02 13:30 | 202 | 200
2017-12-02 14:00 | 211 | 209
2017-12-02 14:30 | 229 | 228
2017-12-02 15:00 | 238 | 238
2017-12-02 15:30 | 236 | 236
2017-12-02 16:00 | 239 | 239
2017-12-02 16:30 | 248 | 248
2017-12-02 17:00 | 258 | 258
2017-12-02 17:30 | 259 | 259
2017-12-02 18:00 | 256 | 256
2017-12-02 18:30 | 258 | 258
2017-12-02 19:00 | 267 | 267
2017-12-02 19:30 | 265 | 265
2017-12-02 20:00 | 263 | 263
2017-12-02 20:30 | 260 | 260
2017-12-02 21:00 | 248 | 248
2017-12-02 21:30 | 241 | 241
2017-12-02 22:00 | 235 | 235
2017-12-02 22:30 | 231 | 231
2017-12-02 23:00 | 231 | 231
2017-12-02 23:30 | 219 | 219
2017-12-03 | 203 | 202
2017-12-03 00:30 | 185 | 185
2017-12-03 01:00 | 178 | 178
2017-12-03 01:30 | 171 | 171
2017-12-03 02:00 | 166 | 166
2017-12-03 02:30 | 163 | 163
2017-12-03 03:00 | 160 | 160
2017-12-03 03:30 | 160 | 159
2017-12-03 04:00 | 157 | 157
2017-12-03 04:30 | 156 | 156
2017-12-03 05:00 | 156 | 156
2017-12-03 05:30 | 155 | 155
2017-12-03 06:00 | 156 | 156
2017-12-03 06:30 | 157 | 157
2017-12-03 07:00 | 157 | 157
2017-12-03 07:30 | 167 | 167
2017-12-03 08:00 | 172 | 172
2017-12-03 08:30 | 174 | 173
2017-12-03 09:00 | 176 | 176
2017-12-03 09:30 | 184 | 183
2017-12-03 10:00 | 191 | 189
2017-12-03 10:30 | 197 | 195
2017-12-03 11:00 | 204 | 202
2017-12-03 11:30 | 204 | 203
2017-12-03 12:00 | 209 | 207
2017-12-03 12:30 | 218 | 216
2017-12-03 13:00 | 227 | 225
2017-12-03 13:30 | 231 | 230
2017-12-03 14:00 | 241 | 241
2017-12-03 14:30 | 247 | 247
2017-12-03 15:00 | 246 | 245
2017-12-03 15:30 | 249 | 249
2017-12-03 16:00 | 260 | 259
2017-12-03 16:30 | 275 | 275
2017-12-03 17:00 | 286 | 285
2017-12-03 17:30 | 289 | 288
2017-12-03 18:00 | 292 | 291
2017-12-03 18:30 | 289 | 288
2017-12-03 19:00 | 290 | 288
2017-12-03 19:30 | 288 | 288
2017-12-03 20:00 | 286 | 285
2017-12-03 20:30 | 280 | 279
2017-12-03 21:00 | 265 | 265
2017-12-03 21:30 | 253 | 253
2017-12-03 22:00 | 242 | 242
2017-12-03 22:30 | 235 | 235
2017-12-03 23:00 | 232 | 232
2017-12-03 23:30 | 214 | 214
2017-12-04 | 198 | 198
2017-12-04 00:30 | 184 | 184
2017-12-04 01:00 | 176 | 176
2017-12-04 01:30 | 171 | 171
2017-12-04 02:00 | 167 | 167
2017-12-04 02:30 | 164 | 164
2017-12-04 03:00 | 163 | 163
2017-12-04 03:30 | 163 | 163
2017-12-04 04:00 | 163 | 163
2017-12-04 04:30 | 167 | 167
2017-12-04 05:00 | 171 | 171
2017-12-04 05:30 | 180 | 180
2017-12-04 06:00 | 192 | 192
2017-12-04 06:30 | 210 | 210
2017-12-04 07:00 | 224 | 224
2017-12-04 07:30 | 241 | 241
2017-12-04 08:00 | 254 | 254
2017-12-04 08:30 | 263 | 263
2017-12-04 09:00 | 270 | 270
2017-12-04 09:30 | 280 | 279
2017-12-04 10:00 | 282 | 282
2017-12-04 10:30 | 285 | 285
2017-12-04 11:00 | 302 | 301
2017-12-04 11:30 | 307 | 307
2017-12-04 12:00 | 312 | 312
2017-12-04 12:30 | 312 | 312
2017-12-04 13:00 | 305 | 305
2017-12-04 13:30 | 296 | 296
2017-12-04 14:00 | 289 | 289
2017-12-04 14:30 | 284 | 284
2017-12-04 15:00 | 277 | 277
2017-12-04 15:30 | 275 | 275
2017-12-04 16:00 | 277 | 277
2017-12-04 16:30 | 278 | 278
2017-12-04 17:00 | 283 | 283
2017-12-04 17:30 | 283 | 283
2017-12-04 18:00 | 277 | 277
2017-12-04 18:30 | 272 | 271
2017-12-04 19:00 | 278 | 278
2017-12-04 19:30 | 277 | 277
2017-12-04 20:00 | 274 | 274
2017-12-04 20:30 | 268 | 268
2017-12-04 21:00 | 253 | 253
2017-12-04 21:30 | 241 | 241
2017-12-04 22:00 | 229 | 229
2017-12-04 22:30 | 223 | 222
2017-12-04 23:00 | 220 | 219
2017-12-04 23:30 | 207 | 207
2017-12-05 | 191 | 191
2017-12-05 00:30 | 177 | 177
2017-12-05 01:00 | 169 | 169
2017-12-05 01:30 | 163 | 163
2017-12-05 02:00 | 160 | 160
2017-12-05 02:30 | 158 | 158
2017-12-05 03:00 | 157 | 157
2017-12-05 03:30 | 157 | 157
2017-12-05 04:00 | 157 | 157
2017-12-05 04:30 | 161 | 161
2017-12-05 05:00 | 167 | 167
2017-12-05 05:30 | 176 | 176
2017-12-05 06:00 | 186 | 186
2017-12-05 06:30 | 201 | 201
2017-12-05 07:00 | 210 | 209
2017-12-05 07:30 | 225 | 225
2017-12-05 08:00 | 230 | 230
2017-12-05 08:30 | 246 | 245
2017-12-05 09:00 | 248 | 247
2017-12-05 09:30 | 244 | 243
2017-12-05 10:00 | 223 | 222
2017-12-05 10:30 | 237 | 235
2017-12-05 11:00 | 246 | 244
2017-12-05 11:30 | 221 | 219
2017-12-05 12:00 | 227 | 224
2017-12-05 12:30 | 242 | 239
2017-12-05 13:00 | 245 | 243
2017-12-05 13:30 | 243 | 241
2017-12-05 14:00 | 256 | 255
2017-12-05 14:30 | 257 | 257
2017-12-05 15:00 | 272 | 272
2017-12-05 15:30 | 285 | 284
2017-12-05 16:00 | 295 | 295
2017-12-05 16:30 | 301 | 301
2017-12-05 17:00 | 296 | 296
2017-12-05 17:30 | 298 | 298
2017-12-05 18:00 | 295 | 295
2017-12-05 18:30 | 292 | 291
2017-12-05 19:00 | 300 | 298
2017-12-05 19:30 | 300 | 299
2017-12-05 20:00 | 294 | 294
2017-12-05 20:30 | 287 | 286
2017-12-05 21:00 | 270 | 268
2017-12-05 21:30 | 257 | 256
2017-12-05 22:00 | 243 | 243
2017-12-05 22:30 | 234 | 233
2017-12-05 23:00 | 229 | 228
2017-12-05 23:30 | 214 | 214
2017-12-06 | 197 | 197
2017-12-06 00:30 | 180 | 180
2017-12-06 01:00 | 171 | 171
2017-12-06 01:30 | 166 | 166
2017-12-06 02:00 | 161 | 161
2017-12-06 02:30 | 157 | 157
2017-12-06 03:00 | 154 | 154
2017-12-06 03:30 | 153 | 153
2017-12-06 04:00 | 153 | 153
2017-12-06 04:30 | 157 | 157
2017-12-06 05:00 | 160 | 160
2017-12-06 05:30 | 169 | 169
2017-12-06 06:00 | 179 | 178
2017-12-06 06:30 | 195 | 193
2017-12-06 07:00 | 204 | 202
2017-12-06 07:30 | 211 | 210
2017-12-06 08:00 | 211 | 208
2017-12-06 08:30 | 210 | 208
2017-12-06 09:00 | 207 | 207
2017-12-06 09:30 | 206 | 206
2017-12-06 10:00 | 217 | 216
2017-12-06 10:30 | 216 | 216
2017-12-06 11:00 | 208 | 208
2017-12-06 11:30 | 207 | 207
2017-12-06 12:00 | 208 | 207
2017-12-06 12:30 | 210 | 209
2017-12-06 13:00 | 214 | 213
2017-12-06 13:30 | 222 | 221
2017-12-06 14:00 | 231 | 230
2017-12-06 14:30 | 239 | 238
2017-12-06 15:00 | 253 | 253
2017-12-06 15:30 | 265 | 265
2017-12-06 16:00 | 281 | 280
2017-12-06 16:30 | 294 | 294
2017-12-06 17:00 | 305 | 304
2017-12-06 17:30 | 307 | 306
2017-12-06 18:00 | 295 | 295
2017-12-06 18:30 | 288 | 287
2017-12-06 19:00 | 295 | 293
2017-12-06 19:30 | 297 | 295
2017-12-06 20:00 | 294 | 292
2017-12-06 20:30 | 285 | 284
2017-12-06 21:00 | 272 | 271
2017-12-06 21:30 | 257 | 257
2017-12-06 22:00 | 244 | 244
2017-12-06 22:30 | 236 | 236
2017-12-06 23:00 | 232 | 232
2017-12-06 23:30 | 217 | 217
2017-12-07 | 197 | 196
2017-12-07 00:30 | 181 | 180
2017-12-07 01:00 | 172 | 171
2017-12-07 01:30 | 166 | 165
2017-12-07 02:00 | 162 | 162
2017-12-07 02:30 | 159 | 159
2017-12-07 03:00 | 158 | 158
2017-12-07 03:30 | 157 | 157
2017-12-07 04:00 | 157 | 157
2017-12-07 04:30 | 159 | 159
2017-12-07 05:00 | 162 | 162
2017-12-07 05:30 | 171 | 171
2017-12-07 06:00 | 181 | 180
2017-12-07 06:30 | 195 | 193
2017-12-07 07:00 | 204 | 203
2017-12-07 07:30 | 215 | 214
2017-12-07 08:00 | 218 | 217
2017-12-07 08:30 | 219 | 219
2017-12-07 09:00 | 219 | 219
2017-12-07 09:30 | 221 | 220
2017-12-07 10:00 | 224 | 223
2017-12-07 10:30 | 225 | 224
2017-12-07 11:00 | 229 | 227
2017-12-07 11:30 | 235 | 235
2017-12-07 12:00 | 238 | 238
2017-12-07 12:30 | 242 | 242
2017-12-07 13:00 | 249 | 249
2017-12-07 13:30 | 258 | 258
2017-12-07 14:00 | 267 | 267
2017-12-07 14:30 | 277 | 277
2017-12-07 15:00 | 284 | 284
2017-12-07 15:30 | 294 | 294
2017-12-07 16:00 | 305 | 305
2017-12-07 16:30 | 315 | 315
2017-12-07 17:00 | 324 | 323
2017-12-07 17:30 | 322 | 322
2017-12-07 18:00 | 318 | 317
2017-12-07 18:30 | 311 | 310
2017-12-07 19:00 | 315 | 315
2017-12-07 19:30 | 317 | 317
2017-12-07 20:00 | 313 | 313
2017-12-07 20:30 | 306 | 305
2017-12-07 21:00 | 290 | 287
2017-12-07 21:30 | 273 | 271
2017-12-07 22:00 | 258 | 256
2017-12-07 22:30 | 248 | 247
2017-12-07 23:00 | 243 | 241
2017-12-07 23:30 | 226 | 224
2017-12-08 | 206 | 205
2017-12-08 00:30 | 191 | 190
2017-12-08 01:00 | 182 | 182
2017-12-08 01:30 | 176 | 176
2017-12-08 02:00 | 173 | 172
2017-12-08 02:30 | 170 | 170
2017-12-08 03:00 | 168 | 168
2017-12-08 03:30 | 168 | 167
2017-12-08 04:00 | 167 | 167
2017-12-08 04:30 | 170 | 170
2017-12-08 05:00 | 173 | 173
2017-12-08 05:30 | 182 | 182
2017-12-08 06:00 | 190 | 189
2017-12-08 06:30 | 207 | 206
2017-12-08 07:00 | 219 | 219
2017-12-08 07:30 | 232 | 232
2017-12-08 08:00 | 239 | 238
2017-12-08 08:30 | 244 | 243
2017-12-08 09:00 | 249 | 247
2017-12-08 09:30 | 255 | 254
2017-12-08 10:00 | 260 | 260
2017-12-08 10:30 | 270 | 270
2017-12-08 11:00 | 286 | 286
2017-12-08 11:30 | 308 | 308
2017-12-08 12:00 | 332 | 332
2017-12-08 12:30 | 344 | 344
2017-12-08 13:00 | 330 | 329
2017-12-08 13:30 | 300 | 300
2017-12-08 14:00 | 290 | 289
2017-12-08 14:30 | 286 | 284
2017-12-08 15:00 | 283 | 281
2017-12-08 15:30 | 279 | 277
2017-12-08 16:00 | 283 | 281
2017-12-08 16:30 | 284 | 282
2017-12-08 17:00 | 287 | 286
2017-12-08 17:30 | 285 | 283
2017-12-08 18:00 | 275 | 275
2017-12-08 18:30 | 265 | 265
2017-12-08 19:00 | 271 | 271
2017-12-08 19:30 | 268 | 268
2017-12-08 20:00 | 266 | 266
2017-12-08 20:30 | 261 | 261
2017-12-08 21:00 | 248 | 247
2017-12-08 21:30 | 239 | 238
2017-12-08 22:00 | 230 | 229
2017-12-08 22:30 | 225 | 225
2017-12-08 23:00 | 222 | 222
2017-12-08 23:30 | 209 | 208
2017-12-09 | 193 | 192
2017-12-09 00:30 | 178 | 178
2017-12-09 01:00 | 171 | 170
2017-12-09 01:30 | 166 | 165
2017-12-09 02:00 | 160 | 160
2017-12-09 02:30 | 157 | 157
2017-12-09 03:00 | 154 | 154
2017-12-09 03:30 | 153 | 153
2017-12-09 04:00 | 152 | 152
2017-12-09 04:30 | 152 | 152
2017-12-09 05:00 | 151 | 151
2017-12-09 05:30 | 152 | 152
2017-12-09 06:00 | 155 | 155
2017-12-09 06:30 | 162 | 162
2017-12-09 07:00 | 166 | 166
2017-12-09 07:30 | 171 | 170
2017-12-09 08:00 | 175 | 174
2017-12-09 08:30 | 180 | 178
2017-12-09 09:00 | 183 | 182
2017-12-09 09:30 | 182 | 181
2017-12-09 10:00 | 184 | 183
2017-12-09 10:30 | 187 | 185
2017-12-09 11:00 | 189 | 187
2017-12-09 11:30 | 195 | 195
2017-12-09 12:00 | 201 | 201
2017-12-09 12:30 | 205 | 205
2017-12-09 13:00 | 210 | 209
2017-12-09 13:30 | 216 | 216
2017-12-09 14:00 | 222 | 222
2017-12-09 14:30 | 228 | 228
2017-12-09 15:00 | 239 | 239
2017-12-09 15:30 | 247 | 247
2017-12-09 16:00 | 256 | 256
2017-12-09 16:30 | 266 | 266
2017-12-09 17:00 | 265 | 265
2017-12-09 17:30 | 259 | 258
2017-12-09 18:00 | 249 | 249
2017-12-09 18:30 | 244 | 244
2017-12-09 19:00 | 245 | 245
2017-12-09 19:30 | 242 | 242
2017-12-09 20:00 | 241 | 241
2017-12-09 20:30 | 238 | 238
2017-12-09 21:00 | 228 | 227
2017-12-09 21:30 | 220 | 219
2017-12-09 22:00 | 213 | 212
2017-12-09 22:30 | 210 | 209
2017-12-09 23:00 | 211 | 210
2017-12-09 23:30 | 199 | 199
2017-12-10 | 183 | 183
2017-12-10 00:30 | 168 | 168
2017-12-10 01:00 | 159 | 159
2017-12-10 01:30 | 154 | 154
2017-12-10 02:00 | 149 | 149
2017-12-10 02:30 | 146 | 146
2017-12-10 03:00 | 144 | 144
2017-12-10 03:30 | 143 | 143
2017-12-10 04:00 | 143 | 143
2017-12-10 04:30 | 143 | 143
2017-12-10 05:00 | 140 | 140
2017-12-10 05:30 | 141 | 141
2017-12-10 06:00 | 141 | 141
2017-12-10 06:30 | 143 | 142
2017-12-10 07:00 | 143 | 143
2017-12-10 07:30 | 145 | 145
2017-12-10 08:00 | 148 | 148
2017-12-10 08:30 | 154 | 154
2017-12-10 09:00 | 158 | 157
2017-12-10 09:30 | 162 | 161
2017-12-10 10:00 | 163 | 161
2017-12-10 10:30 | 166 | 164
2017-12-10 11:00 | 167 | 165
2017-12-10 11:30 | 168 | 166
2017-12-10 12:00 | 170 | 167
2017-12-10 12:30 | 171 | 168
2017-12-10 13:00 | 174 | 173
2017-12-10 13:30 | 179 | 177
2017-12-10 14:00 | 189 | 187
2017-12-10 14:30 | 199 | 197
2017-12-10 15:00 | 208 | 207
2017-12-10 15:30 | 214 | 213
2017-12-10 16:00 | 210 | 209
2017-12-10 16:30 | 212 | 211
2017-12-10 17:00 | 223 | 222
2017-12-10 17:30 | 228 | 228
2017-12-10 18:00 | 232 | 232
2017-12-10 18:30 | 234 | 234
2017-12-10 19:00 | 244 | 243
2017-12-10 19:30 | 248 | 247
2017-12-10 20:00 | 246 | 245
2017-12-10 20:30 | 240 | 240
2017-12-10 21:00 | 230 | 230
2017-12-10 21:30 | 222 | 222
2017-12-10 22:00 | 213 | 213
2017-12-10 22:30 | 208 | 208
2017-12-10 23:00 | 207 | 206
2017-12-10 23:30 | 193 | 193
2017-12-11 | 177 | 177
2017-12-11 00:30 | 163 | 163
2017-12-11 01:00 | 156 | 155
2017-12-11 01:30 | 152 | 151
2017-12-11 02:00 | 148 | 148
2017-12-11 02:30 | 149 | 148
2017-12-11 03:00 | 147 | 146
2017-12-11 03:30 | 147 | 146
2017-12-11 04:00 | 147 | 146
2017-12-11 04:30 | 150 | 150
2017-12-11 05:00 | 156 | 155
2017-12-11 05:30 | 165 | 164
2017-12-11 06:00 | 174 | 174
2017-12-11 06:30 | 190 | 190
2017-12-11 07:00 | 205 | 205
2017-12-11 07:30 | 215 | 215
2017-12-11 08:00 | 222 | 221
2017-12-11 08:30 | 225 | 225
2017-12-11 09:00 | 228 | 228
2017-12-11 09:30 | 235 | 235
2017-12-11 10:00 | 238 | 238
2017-12-11 10:30 | 241 | 241
2017-12-11 11:00 | 238 | 238
2017-12-11 11:30 | 234 | 234
2017-12-11 12:00 | 245 | 245
2017-12-11 12:30 | 247 | 247
2017-12-11 13:00 | 245 | 245
2017-12-11 13:30 | 243 | 243
2017-12-11 14:00 | 244 | 244
2017-12-11 14:30 | 247 | 247
2017-12-11 15:00 | 254 | 254
2017-12-11 15:30 | 261 | 261
2017-12-11 16:00 | 270 | 270
2017-12-11 16:30 | 279 | 279
2017-12-11 17:00 | 286 | 286
2017-12-11 17:30 | 288 | 288
2017-12-11 18:00 | 285 | 285
2017-12-11 18:30 | 282 | 282
2017-12-11 19:00 | 289 | 289
2017-12-11 19:30 | 290 | 290
2017-12-11 20:00 | 284 | 284
2017-12-11 20:30 | 276 | 276
2017-12-11 21:00 | 262 | 262
2017-12-11 21:30 | 247 | 247
2017-12-11 22:00 | 235 | 235
2017-12-11 22:30 | 228 | 227
2017-12-11 23:00 | 225 | 224
2017-12-11 23:30 | 209 | 209
2017-12-12 | 190 | 190
2017-12-12 00:30 | 175 | 175
2017-12-12 01:00 | 166 | 166
2017-12-12 01:30 | 160 | 159
2017-12-12 02:00 | 157 | 157
2017-12-12 02:30 | 155 | 155
2017-12-12 03:00 | 152 | 152
2017-12-12 03:30 | 154 | 154
2017-12-12 04:00 | 157 | 157
2017-12-12 04:30 | 160 | 159
2017-12-12 05:00 | 161 | 161
2017-12-12 05:30 | 171 | 170
2017-12-12 06:00 | 180 | 179
2017-12-12 06:30 | 193 | 192
2017-12-12 07:00 | 202 | 201
2017-12-12 07:30 | 212 | 211
2017-12-12 08:00 | 216 | 216
2017-12-12 08:30 | 222 | 222
2017-12-12 09:00 | 230 | 230
2017-12-12 09:30 | 240 | 240
2017-12-12 10:00 | 243 | 242
2017-12-12 10:30 | 232 | 232
2017-12-12 11:00 | 226 | 226
2017-12-12 11:30 | 226 | 226
2017-12-12 12:00 | 224 | 224
2017-12-12 12:30 | 220 | 220
2017-12-12 13:00 | 223 | 223
2017-12-12 13:30 | 228 | 228
2017-12-12 14:00 | 232 | 232
2017-12-12 14:30 | 237 | 237
2017-12-12 15:00 | 245 | 245
2017-12-12 15:30 | 255 | 255
2017-12-12 16:00 | 266 | 266
2017-12-12 16:30 | 275 | 274
2017-12-12 17:00 | 285 | 285
2017-12-12 17:30 | 287 | 287
2017-12-12 18:00 | 283 | 283
2017-12-12 18:30 | 280 | 279
2017-12-12 19:00 | 288 | 287
2017-12-12 19:30 | 288 | 288
2017-12-12 20:00 | 285 | 285
2017-12-12 20:30 | 277 | 277
2017-12-12 21:00 | 262 | 262
2017-12-12 21:30 | 249 | 249
2017-12-12 22:00 | 238 | 238
2017-12-12 22:30 | 230 | 230
2017-12-12 23:00 | 226 | 225
2017-12-12 23:30 | 210 | 210
2017-12-13 | 192 | 192
2017-12-13 00:30 | 178 | 178
2017-12-13 01:00 | 169 | 169
2017-12-13 01:30 | 164 | 163
2017-12-13 02:00 | 160 | 159
2017-12-13 02:30 | 155 | 155
2017-12-13 03:00 | 155 | 155
2017-12-13 03:30 | 155 | 155
2017-12-13 04:00 | 155 | 155
2017-12-13 04:30 | 159 | 159
2017-12-13 05:00 | 161 | 161
2017-12-13 05:30 | 171 | 171
2017-12-13 06:00 | 178 | 178
2017-12-13 06:30 | 190 | 190
2017-12-13 07:00 | 201 | 200
2017-12-13 07:30 | 212 | 211
2017-12-13 08:00 | 217 | 216
2017-12-13 08:30 | 228 | 226
2017-12-13 09:00 | 234 | 233
2017-12-13 09:30 | 237 | 235
2017-12-13 10:00 | 238 | 236
2017-12-13 10:30 | 237 | 236
2017-12-13 11:00 | 238 | 236
2017-12-13 11:30 | 239 | 237
2017-12-13 12:00 | 242 | 240
2017-12-13 12:30 | 244 | 244
2017-12-13 13:00 | 246 | 246
2017-12-13 13:30 | 252 | 252
2017-12-13 14:00 | 257 | 257
2017-12-13 14:30 | 262 | 262
2017-12-13 15:00 | 270 | 270
2017-12-13 15:30 | 279 | 279
2017-12-13 16:00 | 286 | 286
2017-12-13 16:30 | 293 | 293
2017-12-13 17:00 | 300 | 300
2017-12-13 17:30 | 301 | 301
2017-12-13 18:00 | 296 | 296
2017-12-13 18:30 | 292 | 292
2017-12-13 19:00 | 298 | 298
2017-12-13 19:30 | 300 | 300
2017-12-13 20:00 | 295 | 294
2017-12-13 20:30 | 287 | 287
2017-12-13 21:00 | 273 | 273
2017-12-13 21:30 | 259 | 259
2017-12-13 22:00 | 246 | 246
2017-12-13 22:30 | 236 | 235
2017-12-13 23:00 | 231 | 231
2017-12-13 23:30 | 215 | 214
2017-12-14 | 194 | 194
2017-12-14 00:30 | 179 | 179
2017-12-14 01:00 | 171 | 171
2017-12-14 01:30 | 165 | 165
2017-12-14 02:00 | 161 | 161
2017-12-14 02:30 | 158 | 158
2017-12-14 03:00 | 157 | 157
2017-12-14 03:30 | 157 | 157
2017-12-14 04:00 | 158 | 158
2017-12-14 04:30 | 161 | 161
2017-12-14 05:00 | 166 | 165
2017-12-14 05:30 | 174 | 174
2017-12-14 06:00 | 184 | 183
2017-12-14 06:30 | 197 | 197
2017-12-14 07:00 | 207 | 207
2017-12-14 07:30 | 223 | 222
2017-12-14 08:00 | 227 | 227
2017-12-14 08:30 | 234 | 234
2017-12-14 09:00 | 239 | 239
2017-12-14 09:30 | 241 | 241
2017-12-14 10:00 | 243 | 243
2017-12-14 10:30 | 243 | 243
2017-12-14 11:00 | 245 | 245
2017-12-14 11:30 | 249 | 248
2017-12-14 12:00 | 252 | 252
2017-12-14 12:30 | 253 | 253
2017-12-14 13:00 | 254 | 253
2017-12-14 13:30 | 260 | 260
2017-12-14 14:00 | 266 | 265
2017-12-14 14:30 | 272 | 271
2017-12-14 15:00 | 277 | 277
2017-12-14 15:30 | 284 | 283
2017-12-14 16:00 | 295 | 294
2017-12-14 16:30 | 304 | 304
2017-12-14 17:00 | 313 | 312
2017-12-14 17:30 | 313 | 312
2017-12-14 18:00 | 309 | 308
2017-12-14 18:30 | 304 | 303
2017-12-14 19:00 | 306 | 305
2017-12-14 19:30 | 310 | 307
2017-12-14 20:00 | 306 | 304
2017-12-14 20:30 | 298 | 295
2017-12-14 21:00 | 284 | 282
2017-12-14 21:30 | 268 | 267
2017-12-14 22:00 | 252 | 252
2017-12-14 22:30 | 245 | 245
2017-12-14 23:00 | 241 | 241
2017-12-14 23:30 | 225 | 225
2017-12-15 | 205 | 205
2017-12-15 00:30 | 187 | 187
2017-12-15 01:00 | 179 | 178
2017-12-15 01:30 | 170 | 170
2017-12-15 02:00 | 168 | 168
2017-12-15 02:30 | 165 | 165
2017-12-15 03:00 | 164 | 164
2017-12-15 03:30 | 163 | 163
2017-12-15 04:00 | 163 | 163
2017-12-15 04:30 | 167 | 167
2017-12-15 05:00 | 171 | 171
2017-12-15 05:30 | 178 | 178
2017-12-15 06:00 | 188 | 188
2017-12-15 06:30 | 197 | 197
2017-12-15 07:00 | 198 | 197
2017-12-15 07:30 | 209 | 208
2017-12-15 08:00 | 220 | 220
2017-12-15 08:30 | 226 | 226
2017-12-15 09:00 | 225 | 225
2017-12-15 09:30 | 226 | 226
2017-12-15 10:00 | 227 | 227
2017-12-15 10:30 | 228 | 228
2017-12-15 11:00 | 232 | 231
2017-12-15 11:30 | 234 | 234
2017-12-15 12:00 | 238 | 238
2017-12-15 12:30 | 240 | 239
2017-12-15 13:00 | 243 | 243
2017-12-15 13:30 | 244 | 243
2017-12-15 14:00 | 249 | 248
2017-12-15 14:30 | 255 | 254
2017-12-15 15:00 | 262 | 262
2017-12-15 15:30 | 271 | 270
2017-12-15 16:00 | 282 | 281
2017-12-15 16:30 | 309 | 308
2017-12-15 17:00 | 317 | 316
2017-12-15 17:30 | 317 | 316
2017-12-15 18:00 | 308 | 308
2017-12-15 18:30 | 297 | 296
2017-12-15 19:00 | 301 | 300
2017-12-15 19:30 | 301 | 300
2017-12-15 20:00 | 298 | 297
2017-12-15 20:30 | 290 | 290
2017-12-15 21:00 | 279 | 278
2017-12-15 21:30 | 268 | 268
2017-12-15 22:00 | 255 | 255
2017-12-15 22:30 | 248 | 247
2017-12-15 23:00 | 243 | 242
2017-12-15 23:30 | 226 | 226
2017-12-16 | 208 | 207
2017-12-16 00:30 | 192 | 191
2017-12-16 01:00 | 184 | 184
2017-12-16 01:30 | 178 | 178
2017-12-16 02:00 | 173 | 173
2017-12-16 02:30 | 170 | 170
2017-12-16 03:00 | 167 | 167
2017-12-16 03:30 | 165 | 165
2017-12-16 04:00 | 164 | 164
2017-12-16 04:30 | 165 | 165
2017-12-16 05:00 | 163 | 163
2017-12-16 05:30 | 163 | 163
2017-12-16 06:00 | 165 | 165
2017-12-16 06:30 | 172 | 172
2017-12-16 07:00 | 178 | 178
2017-12-16 07:30 | 186 | 186
2017-12-16 08:00 | 194 | 194
2017-12-16 08:30 | 203 | 201
2017-12-16 09:00 | 209 | 209
2017-12-16 09:30 | 213 | 213
2017-12-16 10:00 | 214 | 214
2017-12-16 10:30 | 218 | 218
2017-12-16 11:00 | 221 | 221
2017-12-16 11:30 | 224 | 224
2017-12-16 12:00 | 230 | 230
2017-12-16 12:30 | 233 | 232
2017-12-16 13:00 | 236 | 236
2017-12-16 13:30 | 241 | 241
2017-12-16 14:00 | 241 | 241
2017-12-16 14:30 | 245 | 245
2017-12-16 15:00 | 251 | 251
2017-12-16 15:30 | 255 | 255
2017-12-16 16:00 | 265 | 265
2017-12-16 16:30 | 272 | 272
2017-12-16 17:00 | 282 | 282
2017-12-16 17:30 | 279 | 279
2017-12-16 18:00 | 269 | 269
2017-12-16 18:30 | 266 | 266
2017-12-16 19:00 | 268 | 268
2017-12-16 19:30 | 271 | 270
2017-12-16 20:00 | 269 | 269
2017-12-16 20:30 | 262 | 262
2017-12-16 21:00 | 251 | 250
2017-12-16 21:30 | 244 | 244
2017-12-16 22:00 | 237 | 237
2017-12-16 22:30 | 231 | 231
2017-12-16 23:00 | 227 | 226
2017-12-16 23:30 | 212 | 212
2017-12-17 | 196 | 196
2017-12-17 00:30 | 181 | 181
2017-12-17 01:00 | 171 | 171
2017-12-17 01:30 | 165 | 165
2017-12-17 02:00 | 162 | 161
2017-12-17 02:30 | 158 | 158
2017-12-17 03:00 | 155 | 155
2017-12-17 03:30 | 154 | 154
2017-12-17 04:00 | 151 | 151
2017-12-17 04:30 | 150 | 150
2017-12-17 05:00 | 146 | 146
2017-12-17 05:30 | 146 | 146
2017-12-17 06:00 | 146 | 146
2017-12-17 06:30 | 150 | 150
2017-12-17 07:00 | 153 | 153
2017-12-17 07:30 | 159 | 159
2017-12-17 08:00 | 163 | 162
2017-12-17 08:30 | 168 | 167
2017-12-17 09:00 | 175 | 175
2017-12-17 09:30 | 183 | 182
2017-12-17 10:00 | 190 | 189
2017-12-17 10:30 | 196 | 195
2017-12-17 11:00 | 198 | 198
2017-12-17 11:30 | 204 | 204
2017-12-17 12:00 | 209 | 209
2017-12-17 12:30 | 213 | 213
2017-12-17 13:00 | 219 | 219
2017-12-17 13:30 | 222 | 222
2017-12-17 14:00 | 227 | 227
2017-12-17 14:30 | 234 | 233
2017-12-17 15:00 | 242 | 242
2017-12-17 15:30 | 249 | 248
2017-12-17 16:00 | 259 | 259
2017-12-17 16:30 | 267 | 266
2017-12-17 17:00 | 273 | 273
2017-12-17 17:30 | 273 | 273
2017-12-17 18:00 | 268 | 268
2017-12-17 18:30 | 266 | 266
2017-12-17 19:00 | 272 | 272
2017-12-17 19:30 | 271 | 271
2017-12-17 20:00 | 270 | 270
2017-12-17 20:30 | 264 | 264
2017-12-17 21:00 | 253 | 253
2017-12-17 21:30 | 245 | 244
2017-12-17 22:00 | 237 | 236
2017-12-17 22:30 | 230 | 229
2017-12-17 23:00 | 226 | 225
2017-12-17 23:30 | 208 | 208
2017-12-18 | 191 | 190
2017-12-18 00:30 | 179 | 179
2017-12-18 01:00 | 172 | 172
2017-12-18 01:30 | 167 | 167
2017-12-18 02:00 | 162 | 162
2017-12-18 02:30 | 159 | 159
2017-12-18 03:00 | 157 | 157
2017-12-18 03:30 | 157 | 157
2017-12-18 04:00 | 158 | 158
2017-12-18 04:30 | 161 | 161
2017-12-18 05:00 | 164 | 164
2017-12-18 05:30 | 174 | 174
2017-12-18 06:00 | 182 | 181
2017-12-18 06:30 | 198 | 197
2017-12-18 07:00 | 213 | 212
2017-12-18 07:30 | 227 | 227
2017-12-18 08:00 | 240 | 238
2017-12-18 08:30 | 248 | 246
2017-12-18 09:00 | 249 | 249
2017-12-18 09:30 | 251 | 251
2017-12-18 10:00 | 252 | 252
2017-12-18 10:30 | 251 | 251
2017-12-18 11:00 | 258 | 257
2017-12-18 11:30 | 260 | 259
2017-12-18 12:00 | 260 | 260
2017-12-18 12:30 | 262 | 262
2017-12-18 13:00 | 263 | 263
2017-12-18 13:30 | 265 | 265
2017-12-18 14:00 | 269 | 268
2017-12-18 14:30 | 276 | 275
2017-12-18 15:00 | 285 | 284
2017-12-18 15:30 | 294 | 294
2017-12-18 16:00 | 304 | 304
2017-12-18 16:30 | 311 | 311
2017-12-18 17:00 | 320 | 320
2017-12-18 17:30 | 319 | 319
2017-12-18 18:00 | 312 | 312
2017-12-18 18:30 | 306 | 305
2017-12-18 19:00 | 309 | 309
2017-12-18 19:30 | 308 | 308
2017-12-18 20:00 | 303 | 303
2017-12-18 20:30 | 295 | 295
2017-12-18 21:00 | 280 | 280
2017-12-18 21:30 | 268 | 268
2017-12-18 22:00 | 254 | 254
2017-12-18 22:30 | 246 | 246
2017-12-18 23:00 | 240 | 240
2017-12-18 23:30 | 223 | 223
2017-12-19 | 206 | 205
2017-12-19 00:30 | 190 | 189
2017-12-19 01:00 | 178 | 178
2017-12-19 01:30 | 173 | 173
2017-12-19 02:00 | 170 | 170
2017-12-19 02:30 | 167 | 167
2017-12-19 03:00 | 165 | 165
2017-12-19 03:30 | 165 | 165
2017-12-19 04:00 | 164 | 164
2017-12-19 04:30 | 167 | 167
2017-12-19 05:00 | 169 | 169
2017-12-19 05:30 | 176 | 176
2017-12-19 06:00 | 186 | 186
2017-12-19 06:30 | 199 | 199
2017-12-19 07:00 | 214 | 214
2017-12-19 07:30 | 227 | 227
2017-12-19 08:00 | 233 | 233
2017-12-19 08:30 | 238 | 237
2017-12-19 09:00 | 242 | 242
2017-12-19 09:30 | 244 | 243
2017-12-19 10:00 | 244 | 244
2017-12-19 10:30 | 247 | 247
2017-12-19 11:00 | 252 | 250
2017-12-19 11:30 | 256 | 255
2017-12-19 12:00 | 264 | 262
2017-12-19 12:30 | 272 | 270
2017-12-19 13:00 | 280 | 277
2017-12-19 13:30 | 289 | 286
2017-12-19 14:00 | 298 | 296
2017-12-19 14:30 | 306 | 304
2017-12-19 15:00 | 322 | 320
2017-12-19 15:30 | 345 | 344
2017-12-19 16:00 | 340 | 340
2017-12-19 16:30 | 333 | 333
2017-12-19 17:00 | 337 | 337
2017-12-19 17:30 | 338 | 338
2017-12-19 18:00 | 326 | 326
2017-12-19 18:30 | 315 | 315
2017-12-19 19:00 | 319 | 319
2017-12-19 19:30 | 321 | 320
2017-12-19 20:00 | 317 | 317
2017-12-19 20:30 | 307 | 307
2017-12-19 21:00 | 293 | 293
2017-12-19 21:30 | 280 | 280
2017-12-19 22:00 | 268 | 268
2017-12-19 22:30 | 258 | 258
2017-12-19 23:00 | 253 | 253
2017-12-19 23:30 | 234 | 234
2017-12-20 | 215 | 214
2017-12-20 00:30 | 197 | 197
2017-12-20 01:00 | 189 | 189
2017-12-20 01:30 | 183 | 183
2017-12-20 02:00 | 179 | 179
2017-12-20 02:30 | 176 | 176
2017-12-20 03:00 | 174 | 174
2017-12-20 03:30 | 173 | 173
2017-12-20 04:00 | 173 | 173
2017-12-20 04:30 | 175 | 175
2017-12-20 05:00 | 177 | 177
2017-12-20 05:30 | 185 | 185
2017-12-20 06:00 | 192 | 192
2017-12-20 06:30 | 205 | 205
2017-12-20 07:00 | 221 | 221
2017-12-20 07:30 | 240 | 240
2017-12-20 08:00 | 250 | 250
2017-12-20 08:30 | 261 | 261
2017-12-20 09:00 | 265 | 264
2017-12-20 09:30 | 266 | 266
2017-12-20 10:00 | 268 | 268
2017-12-20 10:30 | 271 | 271
2017-12-20 11:00 | 275 | 275
2017-12-20 11:30 | 281 | 281
2017-12-20 12:00 | 287 | 287
2017-12-20 12:30 | 293 | 293
2017-12-20 13:00 | 300 | 300
2017-12-20 13:30 | 307 | 307
2017-12-20 14:00 | 317 | 317
2017-12-20 14:30 | 325 | 325
2017-12-20 15:00 | 334 | 333
2017-12-20 15:30 | 342 | 341
2017-12-20 16:00 | 352 | 352
2017-12-20 16:30 | 363 | 363
2017-12-20 17:00 | 366 | 366
2017-12-20 17:30 | 361 | 361
2017-12-20 18:00 | 349 | 349
2017-12-20 18:30 | 336 | 336
2017-12-20 19:00 | 337 | 336
2017-12-20 19:30 | 338 | 338
2017-12-20 20:00 | 334 | 334
2017-12-20 20:30 | 326 | 326
2017-12-20 21:00 | 311 | 310
2017-12-20 21:30 | 298 | 297
2017-12-20 22:00 | 281 | 281
2017-12-20 22:30 | 273 | 272
2017-12-20 23:00 | 266 | 265
2017-12-20 23:30 | 246 | 246
2017-12-21 | 227 | 227
2017-12-21 00:30 | 210 | 209
2017-12-21 01:00 | 200 | 200
2017-12-21 01:30 | 194 | 194
2017-12-21 02:00 | 189 | 189
2017-12-21 02:30 | 185 | 185
2017-12-21 03:00 | 182 | 182
2017-12-21 03:30 | 180 | 180
2017-12-21 04:00 | 178 | 178
2017-12-21 04:30 | 181 | 181
2017-12-21 05:00 | 183 | 183
2017-12-21 05:30 | 190 | 190
2017-12-21 06:00 | 199 | 199
2017-12-21 06:30 | 213 | 213
2017-12-21 07:00 | 225 | 225
2017-12-21 07:30 | 240 | 238
2017-12-21 08:00 | 247 | 247
2017-12-21 08:30 | 258 | 258
2017-12-21 09:00 | 257 | 257
2017-12-21 09:30 | 266 | 266
2017-12-21 10:00 | 271 | 270
2017-12-21 10:30 | 278 | 278
2017-12-21 11:00 | 288 | 288
2017-12-21 11:30 | 294 | 293
2017-12-21 12:00 | 299 | 298
2017-12-21 12:30 | 307 | 306
2017-12-21 13:00 | 309 | 308
2017-12-21 13:30 | 316 | 315
2017-12-21 14:00 | 321 | 319
2017-12-21 14:30 | 334 | 333
2017-12-21 15:00 | 341 | 341
2017-12-21 15:30 | 340 | 340
2017-12-21 16:00 | 348 | 348
2017-12-21 16:30 | 342 | 341
2017-12-21 17:00 | 344 | 344
2017-12-21 17:30 | 330 | 330
2017-12-21 18:00 | 339 | 339
2017-12-21 18:30 | 337 | 337
2017-12-21 19:00 | 344 | 343
2017-12-21 19:30 | 346 | 345
2017-12-21 20:00 | 343 | 343
2017-12-21 20:30 | 336 | 336
2017-12-21 21:00 | 319 | 319
2017-12-21 21:30 | 305 | 305
2017-12-21 22:00 | 292 | 292
2017-12-21 22:30 | 280 | 280
2017-12-21 23:00 | 271 | 270
2017-12-21 23:30 | 251 | 250
2017-12-22 | 231 | 231
2017-12-22 00:30 | 212 | 211
2017-12-22 01:00 | 203 | 201
2017-12-22 01:30 | 195 | 194
2017-12-22 02:00 | 190 | 190
2017-12-22 02:30 | 188 | 187
2017-12-22 03:00 | 185 | 184
2017-12-22 03:30 | 183 | 183
2017-12-22 04:00 | 181 | 181
2017-12-22 04:30 | 183 | 183
2017-12-22 05:00 | 184 | 184
2017-12-22 05:30 | 191 | 191
2017-12-22 06:00 | 199 | 199
2017-12-22 06:30 | 212 | 212
2017-12-22 07:00 | 227 | 227
2017-12-22 07:30 | 243 | 243
2017-12-22 08:00 | 255 | 255
2017-12-22 08:30 | 256 | 256
2017-12-22 09:00 | 264 | 264
2017-12-22 09:30 | 263 | 263
2017-12-22 10:00 | 260 | 260
2017-12-22 10:30 | 252 | 252
2017-12-22 11:00 | 253 | 253
2017-12-22 11:30 | 254 | 254
2017-12-22 12:00 | 266 | 266
2017-12-22 12:30 | 280 | 280
2017-12-22 13:00 | 265 | 265
2017-12-22 13:30 | 264 | 264
2017-12-22 14:00 | 278 | 277
2017-12-22 14:30 | 292 | 291
2017-12-22 15:00 | 304 | 304
2017-12-22 15:30 | 304 | 303
2017-12-22 16:00 | 312 | 311
2017-12-22 16:30 | 316 | 315
2017-12-22 17:00 | 317 | 316
2017-12-22 17:30 | 310 | 310
2017-12-22 18:00 | 301 | 301
2017-12-22 18:30 | 295 | 295
2017-12-22 19:00 | 299 | 299
2017-12-22 19:30 | 298 | 298
2017-12-22 20:00 | 297 | 297
2017-12-22 20:30 | 291 | 291
2017-12-22 21:00 | 279 | 279
2017-12-22 21:30 | 270 | 270
2017-12-22 22:00 | 263 | 262
2017-12-22 22:30 | 256 | 256
2017-12-22 23:00 | 253 | 252
2017-12-22 23:30 | 236 | 236
2017-12-23 | 219 | 219
2017-12-23 00:30 | 202 | 202
2017-12-23 01:00 | 193 | 193
2017-12-23 01:30 | 187 | 186
2017-12-23 02:00 | 181 | 181
2017-12-23 02:30 | 178 | 178
2017-12-23 03:00 | 174 | 174
2017-12-23 03:30 | 172 | 172
2017-12-23 04:00 | 172 | 172
2017-12-23 04:30 | 171 | 171
2017-12-23 05:00 | 169 | 169
2017-12-23 05:30 | 168 | 168
2017-12-23 06:00 | 169 | 169
2017-12-23 06:30 | 174 | 174
2017-12-23 07:00 | 178 | 178
2017-12-23 07:30 | 184 | 183
2017-12-23 08:00 | 191 | 190
2017-12-23 08:30 | 204 | 202
2017-12-23 09:00 | 209 | 208
2017-12-23 09:30 | 216 | 215
2017-12-23 10:00 | 217 | 216
2017-12-23 10:30 | 223 | 221
2017-12-23 11:00 | 226 | 224
2017-12-23 11:30 | 232 | 231
2017-12-23 12:00 | 242 | 242
2017-12-23 12:30 | 245 | 245
2017-12-23 13:00 | 254 | 254
2017-12-23 13:30 | 257 | 257
2017-12-23 14:00 | 249 | 249
2017-12-23 14:30 | 254 | 254
2017-12-23 15:00 | 262 | 262
2017-12-23 15:30 | 274 | 274
2017-12-23 16:00 | 279 | 279
2017-12-23 16:30 | 284 | 284
2017-12-23 17:00 | 294 | 294
2017-12-23 17:30 | 295 | 295
2017-12-23 18:00 | 293 | 293
2017-12-23 18:30 | 291 | 291
2017-12-23 19:00 | 291 | 291
2017-12-23 19:30 | 292 | 292
2017-12-23 20:00 | 292 | 292
2017-12-23 20:30 | 284 | 284
2017-12-23 21:00 | 271 | 271
2017-12-23 21:30 | 262 | 261
2017-12-23 22:00 | 253 | 252
2017-12-23 22:30 | 242 | 242
2017-12-23 23:00 | 237 | 237
2017-12-23 23:30 | 219 | 219
2017-12-24 | 201 | 201
2017-12-24 00:30 | 185 | 185
2017-12-24 01:00 | 175 | 175
2017-12-24 01:30 | 168 | 168
2017-12-24 02:00 | 163 | 163
2017-12-24 02:30 | 160 | 160
2017-12-24 03:00 | 156 | 156
2017-12-24 03:30 | 154 | 154
2017-12-24 04:00 | 151 | 151
2017-12-24 04:30 | 150 | 150
2017-12-24 05:00 | 147 | 147
2017-12-24 05:30 | 146 | 146
2017-12-24 06:00 | 148 | 148
2017-12-24 06:30 | 153 | 153
2017-12-24 07:00 | 160 | 160
2017-12-24 07:30 | 167 | 167
2017-12-24 08:00 | 172 | 171
2017-12-24 08:30 | 179 | 178
2017-12-24 09:00 | 184 | 183
2017-12-24 09:30 | 191 | 190
2017-12-24 10:00 | 196 | 195
2017-12-24 10:30 | 204 | 202
2017-12-24 11:00 | 210 | 207
2017-12-24 11:30 | 217 | 214
2017-12-24 12:00 | 228 | 224
2017-12-24 12:30 | 236 | 235
2017-12-24 13:00 | 247 | 245
2017-12-24 13:30 | 254 | 252
2017-12-24 14:00 | 265 | 262
2017-12-24 14:30 | 274 | 273
2017-12-24 15:00 | 281 | 280
2017-12-24 15:30 | 291 | 290
2017-12-24 16:00 | 301 | 300
2017-12-24 16:30 | 308 | 307
2017-12-24 17:00 | 314 | 313
2017-12-24 17:30 | 313 | 312
2017-12-24 18:00 | 309 | 308
2017-12-24 18:30 | 298 | 298
2017-12-24 19:00 | 295 | 295
2017-12-24 19:30 | 296 | 295
2017-12-24 20:00 | 296 | 296
2017-12-24 20:30 | 289 | 289
2017-12-24 21:00 | 277 | 277
2017-12-24 21:30 | 269 | 269
2017-12-24 22:00 | 261 | 261
2017-12-24 22:30 | 255 | 254
2017-12-24 23:00 | 249 | 249
2017-12-24 23:30 | 228 | 228
2017-12-25 | 206 | 205
2017-12-25 00:30 | 188 | 187
2017-12-25 01:00 | 177 | 176
2017-12-25 01:30 | 169 | 169
2017-12-25 02:00 | 164 | 164
2017-12-25 02:30 | 159 | 159
2017-12-25 03:00 | 155 | 155
2017-12-25 03:30 | 152 | 152
2017-12-25 04:00 | 151 | 151
2017-12-25 04:30 | 151 | 151
2017-12-25 05:00 | 149 | 149
2017-12-25 05:30 | 148 | 148
2017-12-25 06:00 | 153 | 153
2017-12-25 06:30 | 162 | 162
2017-12-25 07:00 | 173 | 173
2017-12-25 07:30 | 186 | 185
2017-12-25 08:00 | 191 | 190
2017-12-25 08:30 | 196 | 195
2017-12-25 09:00 | 198 | 197
2017-12-25 09:30 | 201 | 201
2017-12-25 10:00 | 206 | 206
2017-12-25 10:30 | 208 | 208
2017-12-25 11:00 | 212 | 212
2017-12-25 11:30 | 216 | 216
2017-12-25 12:00 | 219 | 219
2017-12-25 12:30 | 223 | 223
2017-12-25 13:00 | 226 | 226
2017-12-25 13:30 | 231 | 230
2017-12-25 14:00 | 238 | 237
2017-12-25 14:30 | 247 | 246
2017-12-25 15:00 | 252 | 251
2017-12-25 15:30 | 261 | 260
2017-12-25 16:00 | 283 | 283
2017-12-25 16:30 | 288 | 288
2017-12-25 17:00 | 285 | 285
2017-12-25 17:30 | 279 | 279
2017-12-25 18:00 | 275 | 275
2017-12-25 18:30 | 270 | 270
2017-12-25 19:00 | 266 | 266
2017-12-25 19:30 | 251 | 251
2017-12-25 20:00 | 243 | 243
2017-12-25 20:30 | 235 | 233
2017-12-25 21:00 | 226 | 224
2017-12-25 21:30 | 220 | 219
2017-12-25 22:00 | 214 | 213
2017-12-25 22:30 | 210 | 210
2017-12-25 23:00 | 207 | 206
2017-12-25 23:30 | 188 | 188
2017-12-26 | 173 | 173
2017-12-26 00:30 | 161 | 161
2017-12-26 01:00 | 158 | 158
2017-12-26 01:30 | 155 | 154
2017-12-26 02:00 | 152 | 152
2017-12-26 02:30 | 150 | 150
2017-12-26 03:00 | 147 | 147
2017-12-26 03:30 | 147 | 146
2017-12-26 04:00 | 145 | 145
2017-12-26 04:30 | 147 | 146
2017-12-26 05:00 | 146 | 146
2017-12-26 05:30 | 143 | 143
2017-12-26 06:00 | 144 | 144
2017-12-26 06:30 | 152 | 152
2017-12-26 07:00 | 157 | 157
2017-12-26 07:30 | 166 | 165
2017-12-26 08:00 | 170 | 168
2017-12-26 08:30 | 174 | 172
2017-12-26 09:00 | 174 | 173
2017-12-26 09:30 | 178 | 177
2017-12-26 10:00 | 179 | 178
2017-12-26 10:30 | 182 | 181
2017-12-26 11:00 | 191 | 189
2017-12-26 11:30 | 194 | 193
2017-12-26 12:00 | 203 | 202
2017-12-26 12:30 | 199 | 199
2017-12-26 13:00 | 196 | 195
2017-12-26 13:30 | 200 | 198
2017-12-26 14:00 | 202 | 201
2017-12-26 14:30 | 208 | 206
2017-12-26 15:00 | 220 | 218
2017-12-26 15:30 | 246 | 246
2017-12-26 16:00 | 244 | 243
2017-12-26 16:30 | 247 | 247
2017-12-26 17:00 | 256 | 256
2017-12-26 17:30 | 258 | 258
2017-12-26 18:00 | 256 | 256
2017-12-26 18:30 | 253 | 253
2017-12-26 19:00 | 256 | 256
2017-12-26 19:30 | 250 | 250
2017-12-26 20:00 | 246 | 246
2017-12-26 20:30 | 240 | 239
2017-12-26 21:00 | 228 | 227
2017-12-26 21:30 | 220 | 219
2017-12-26 22:00 | 212 | 212
2017-12-26 22:30 | 210 | 209
2017-12-26 23:00 | 207 | 206
2017-12-26 23:30 | 193 | 193
2017-12-27 | 178 | 178
2017-12-27 00:30 | 165 | 165
2017-12-27 01:00 | 160 | 160
2017-12-27 01:30 | 159 | 159
2017-12-27 02:00 | 155 | 155
2017-12-27 02:30 | 155 | 155
2017-12-27 03:00 | 153 | 152
2017-12-27 03:30 | 152 | 152
2017-12-27 04:00 | 152 | 152
2017-12-27 04:30 | 154 | 153
2017-12-27 05:00 | 156 | 155
2017-12-27 05:30 | 158 | 158
2017-12-27 06:00 | 163 | 162
2017-12-27 06:30 | 172 | 171
2017-12-27 07:00 | 179 | 177
2017-12-27 07:30 | 186 | 185
2017-12-27 08:00 | 191 | 190
2017-12-27 08:30 | 197 | 197
2017-12-27 09:00 | 209 | 209
2017-12-27 09:30 | 216 | 216
2017-12-27 10:00 | 219 | 219
2017-12-27 10:30 | 218 | 218
2017-12-27 11:00 | 219 | 219
2017-12-27 11:30 | 220 | 220
2017-12-27 12:00 | 224 | 224
2017-12-27 12:30 | 230 | 230
2017-12-27 13:00 | 237 | 237
2017-12-27 13:30 | 244 | 244
2017-12-27 14:00 | 244 | 244
2017-12-27 14:30 | 245 | 245
2017-12-27 15:00 | 252 | 252
2017-12-27 15:30 | 258 | 258
2017-12-27 16:00 | 260 | 260
2017-12-27 16:30 | 272 | 272
2017-12-27 17:00 | 280 | 280
2017-12-27 17:30 | 280 | 280
2017-12-27 18:00 | 275 | 274
2017-12-27 18:30 | 267 | 267
2017-12-27 19:00 | 269 | 268
2017-12-27 19:30 | 270 | 270
2017-12-27 20:00 | 271 | 270
2017-12-27 20:30 | 265 | 265
2017-12-27 21:00 | 254 | 253
2017-12-27 21:30 | 243 | 243
2017-12-27 22:00 | 233 | 232
2017-12-27 22:30 | 227 | 226
2017-12-27 23:00 | 225 | 223
2017-12-27 23:30 | 210 | 209
2017-12-28 | 194 | 193
2017-12-28 00:30 | 179 | 179
2017-12-28 01:00 | 172 | 172
2017-12-28 01:30 | 167 | 167
2017-12-28 02:00 | 164 | 164
2017-12-28 02:30 | 161 | 161
2017-12-28 03:00 | 159 | 159
2017-12-28 03:30 | 158 | 158
2017-12-28 04:00 | 157 | 157
2017-12-28 04:30 | 158 | 158
2017-12-28 05:00 | 158 | 158
2017-12-28 05:30 | 162 | 162
2017-12-28 06:00 | 166 | 166
2017-12-28 06:30 | 174 | 174
2017-12-28 07:00 | 180 | 180
2017-12-28 07:30 | 187 | 186
2017-12-28 08:00 | 193 | 191
2017-12-28 08:30 | 201 | 199
2017-12-28 09:00 | 210 | 208
2017-12-28 09:30 | 219 | 217
2017-12-28 10:00 | 224 | 224
2017-12-28 10:30 | 224 | 224
2017-12-28 11:00 | 229 | 229
2017-12-28 11:30 | 233 | 233
2017-12-28 12:00 | 238 | 238
2017-12-28 12:30 | 242 | 242
2017-12-28 13:00 | 243 | 243
2017-12-28 13:30 | 244 | 244
2017-12-28 14:00 | 248 | 248
2017-12-28 14:30 | 251 | 251
2017-12-28 15:00 | 254 | 254
2017-12-28 15:30 | 258 | 258
2017-12-28 16:00 | 265 | 265
2017-12-28 16:30 | 267 | 267
2017-12-28 17:00 | 274 | 274
2017-12-28 17:30 | 278 | 278
2017-12-28 18:00 | 281 | 281
2017-12-28 18:30 | 279 | 279
2017-12-28 19:00 | 285 | 285
2017-12-28 19:30 | 288 | 288
2017-12-28 20:00 | 289 | 289
2017-12-28 20:30 | 282 | 282
2017-12-28 21:00 | 268 | 268
2017-12-28 21:30 | 255 | 255
2017-12-28 22:00 | 243 | 243
2017-12-28 22:30 | 235 | 235
2017-12-28 23:00 | 232 | 231
2017-12-28 23:30 | 215 | 215
2017-12-29 | 198 | 198
2017-12-29 00:30 | 185 | 185
2017-12-29 01:00 | 178 | 178
2017-12-29 01:30 | 173 | 173
2017-12-29 02:00 | 169 | 169
2017-12-29 02:30 | 166 | 166
2017-12-29 03:00 | 165 | 164
2017-12-29 03:30 | 164 | 164
2017-12-29 04:00 | 162 | 162
2017-12-29 04:30 | 163 | 163
2017-12-29 05:00 | 164 | 164
2017-12-29 05:30 | 166 | 166
2017-12-29 06:00 | 168 | 168
2017-12-29 06:30 | 171 | 171
2017-12-29 07:00 | 176 | 175
2017-12-29 07:30 | 194 | 193
2017-12-29 08:00 | 195 | 194
2017-12-29 08:30 | 200 | 200
2017-12-29 09:00 | 209 | 209
2017-12-29 09:30 | 217 | 216
2017-12-29 10:00 | 214 | 214
2017-12-29 10:30 | 214 | 213
2017-12-29 11:00 | 217 | 217
2017-12-29 11:30 | 216 | 216
2017-12-29 12:00 | 221 | 221
2017-12-29 12:30 | 222 | 222
2017-12-29 13:00 | 227 | 227
2017-12-29 13:30 | 237 | 237
2017-12-29 14:00 | 244 | 244
2017-12-29 14:30 | 253 | 253
2017-12-29 15:00 | 256 | 256
2017-12-29 15:30 | 261 | 261
2017-12-29 16:00 | 274 | 274
2017-12-29 16:30 | 284 | 284
2017-12-29 17:00 | 291 | 290
2017-12-29 17:30 | 296 | 296
2017-12-29 18:00 | 291 | 291
2017-12-29 18:30 | 282 | 282
2017-12-29 19:00 | 285 | 284
2017-12-29 19:30 | 288 | 287
2017-12-29 20:00 | 287 | 286
2017-12-29 20:30 | 280 | 280
2017-12-29 21:00 | 269 | 269
2017-12-29 21:30 | 260 | 260
2017-12-29 22:00 | 250 | 250
2017-12-29 22:30 | 244 | 244
2017-12-29 23:00 | 240 | 240
2017-12-29 23:30 | 222 | 222
2017-12-30 | 202 | 202
2017-12-30 00:30 | 188 | 188
2017-12-30 01:00 | 180 | 180
2017-12-30 01:30 | 174 | 174
2017-12-30 02:00 | 169 | 169
2017-12-30 02:30 | 166 | 166
2017-12-30 03:00 | 162 | 162
2017-12-30 03:30 | 160 | 160
2017-12-30 04:00 | 159 | 159
2017-12-30 04:30 | 158 | 158
2017-12-30 05:00 | 157 | 157
2017-12-30 05:30 | 156 | 156
2017-12-30 06:00 | 158 | 158
2017-12-30 06:30 | 161 | 161
2017-12-30 07:00 | 163 | 163
2017-12-30 07:30 | 170 | 170
2017-12-30 08:00 | 181 | 180
2017-12-30 08:30 | 190 | 189
2017-12-30 09:00 | 198 | 197
2017-12-30 09:30 | 195 | 195
2017-12-30 10:00 | 200 | 199
2017-12-30 10:30 | 217 | 216
2017-12-30 11:00 | 227 | 226
2017-12-30 11:30 | 228 | 227
2017-12-30 12:00 | 232 | 231
2017-12-30 12:30 | 243 | 243
2017-12-30 13:00 | 252 | 252
2017-12-30 13:30 | 253 | 253
2017-12-30 14:00 | 255 | 255
2017-12-30 14:30 | 253 | 253
2017-12-30 15:00 | 256 | 255
2017-12-30 15:30 | 262 | 262
2017-12-30 16:00 | 278 | 277
2017-12-30 16:30 | 289 | 289
2017-12-30 17:00 | 300 | 299
2017-12-30 17:30 | 302 | 301
2017-12-30 18:00 | 300 | 299
2017-12-30 18:30 | 299 | 299
2017-12-30 19:00 | 305 | 305
2017-12-30 19:30 | 307 | 306
2017-12-30 20:00 | 306 | 306
2017-12-30 20:30 | 299 | 299
2017-12-30 21:00 | 286 | 286
2017-12-30 21:30 | 276 | 276
2017-12-30 22:00 | 266 | 266
2017-12-30 22:30 | 260 | 260
2017-12-30 23:00 | 255 | 255
2017-12-30 23:30 | 236 | 236
2017-12-31 | 217 | 217
2017-12-31 00:30 | 202 | 201
2017-12-31 01:00 | 192 | 192
2017-12-31 01:30 | 187 | 187
2017-12-31 02:00 | 182 | 182
2017-12-31 02:30 | 178 | 178
2017-12-31 03:00 | 175 | 175
2017-12-31 03:30 | 174 | 174
2017-12-31 04:00 | 173 | 173
2017-12-31 04:30 | 169 | 169
2017-12-31 05:00 | 166 | 166
2017-12-31 05:30 | 165 | 165
2017-12-31 06:00 | 163 | 163
2017-12-31 06:30 | 166 | 166
2017-12-31 07:00 | 165 | 165
2017-12-31 07:30 | 168 | 168
2017-12-31 08:00 | 175 | 174
2017-12-31 08:30 | 185 | 184
2017-12-31 09:00 | 197 | 195
2017-12-31 09:30 | 206 | 204
2017-12-31 10:00 | 217 | 216
2017-12-31 10:30 | 230 | 229
2017-12-31 11:00 | 252 | 251
2017-12-31 11:30 | 265 | 265
2017-12-31 12:00 | 271 | 270
2017-12-31 12:30 | 275 | 274
2017-12-31 13:00 | 277 | 276
2017-12-31 13:30 | 287 | 286
2017-12-31 14:00 | 305 | 303
2017-12-31 14:30 | 308 | 306
2017-12-31 15:00 | 297 | 296
2017-12-31 15:30 | 285 | 285
2017-12-31 16:00 | 286 | 286
2017-12-31 16:30 | 275 | 275
2017-12-31 17:00 | 269 | 269
2017-12-31 17:30 | 264 | 264
2017-12-31 18:00 | 262 | 262
2017-12-31 18:30 | 259 | 259
2017-12-31 19:00 | 259 | 259
2017-12-31 19:30 | 261 | 261
2017-12-31 20:00 | 260 | 258
2017-12-31 20:30 | 255 | 253
2017-12-31 21:00 | 243 | 242
2017-12-31 21:30 | 238 | 237
2017-12-31 22:00 | 234 | 234
2017-12-31 22:30 | 233 | 233
2017-12-31 23:00 | 233 | 233
2017-12-31 23:30 | 221 | 221
2018-01-01 | 206 | 206
2018-01-01 00:30 | 193 | 193
2018-01-01 01:00 | 188 | 188
2018-01-01 01:30 | 184 | 184
2018-01-01 02:00 | 178 | 178
2018-01-01 02:30 | 174 | 174
2018-01-01 03:00 | 171 | 171
2018-01-01 03:30 | 167 | 167
2018-01-01 04:00 | 165 | 165
2018-01-01 04:30 | 163 | 163
2018-01-01 05:00 | 162 | 162
2018-01-01 05:30 | 161 | 160
2018-01-01 06:00 | 161 | 161
2018-01-01 06:30 | 165 | 165
2018-01-01 07:00 | 168 | 168
2018-01-01 07:30 | 174 | 174
2018-01-01 08:00 | 183 | 183
2018-01-01 08:30 | 204 | 204
2018-01-01 09:00 | 215 | 215
2018-01-01 09:30 | 219 | 219
2018-01-01 10:00 | 226 | 226
2018-01-01 10:30 | 238 | 238
2018-01-01 11:00 | 248 | 248
2018-01-01 11:30 | 249 | 249
2018-01-01 12:00 | 256 | 256
2018-01-01 12:30 | 256 | 256
2018-01-01 13:00 | 269 | 269
2018-01-01 13:30 | 288 | 288
2018-01-01 14:00 | 285 | 284
2018-01-01 14:30 | 289 | 288
2018-01-01 15:00 | 302 | 302
2018-01-01 15:30 | 302 | 302
2018-01-01 16:00 | 313 | 313
2018-01-01 16:30 | 316 | 316
2018-01-01 17:00 | 320 | 319
2018-01-01 17:30 | 322 | 322
2018-01-01 18:00 | 316 | 316
2018-01-01 18:30 | 300 | 299
2018-01-01 19:00 | 299 | 299
2018-01-01 19:30 | 297 | 297
2018-01-01 20:00 | 290 | 290
2018-01-01 20:30 | 281 | 280
2018-01-01 21:00 | 268 | 267
2018-01-01 21:30 | 258 | 256
2018-01-01 22:00 | 246 | 244
2018-01-01 22:30 | 241 | 240
2018-01-01 23:00 | 237 | 236
2018-01-01 23:30 | 223 | 221
2018-01-02 | 202 | 202
2018-01-02 00:30 | 186 | 186
2018-01-02 01:00 | 176 | 176
2018-01-02 01:30 | 169 | 169
2018-01-02 02:00 | 166 | 166
2018-01-02 02:30 | 165 | 165
2018-01-02 03:00 | 162 | 162
2018-01-02 03:30 | 161 | 161
2018-01-02 04:00 | 161 | 161
2018-01-02 04:30 | 164 | 164
2018-01-02 05:00 | 167 | 167
2018-01-02 05:30 | 171 | 171
2018-01-02 06:00 | 179 | 179
2018-01-02 06:30 | 196 | 196
2018-01-02 07:00 | 208 | 207
2018-01-02 07:30 | 225 | 223
2018-01-02 08:00 | 233 | 230
2018-01-02 08:30 | 241 | 240
2018-01-02 09:00 | 238 | 238
2018-01-02 09:30 | 245 | 244
2018-01-02 10:00 | 257 | 257
2018-01-02 10:30 | 268 | 268
2018-01-02 11:00 | 278 | 278
2018-01-02 11:30 | 275 | 275
2018-01-02 12:00 | 272 | 272
2018-01-02 12:30 | 268 | 268
2018-01-02 13:00 | 265 | 265
2018-01-02 13:30 | 278 | 278
2018-01-02 14:00 | 295 | 294
2018-01-02 14:30 | 311 | 311
2018-01-02 15:00 | 332 | 332
2018-01-02 15:30 | 330 | 329
2018-01-02 16:00 | 318 | 317
2018-01-02 16:30 | 304 | 304
2018-01-02 17:00 | 299 | 299
2018-01-02 17:30 | 297 | 296
2018-01-02 18:00 | 297 | 297
2018-01-02 18:30 | 295 | 295
2018-01-02 19:00 | 300 | 299
2018-01-02 19:30 | 291 | 291
2018-01-02 20:00 | 284 | 284
2018-01-02 20:30 | 275 | 275
2018-01-02 21:00 | 261 | 260
2018-01-02 21:30 | 251 | 250
2018-01-02 22:00 | 240 | 240
2018-01-02 22:30 | 235 | 235
2018-01-02 23:00 | 232 | 232
2018-01-02 23:30 | 216 | 216
2018-01-03 | 198 | 197
2018-01-03 00:30 | 183 | 183
2018-01-03 01:00 | 177 | 176
2018-01-03 01:30 | 171 | 171
2018-01-03 02:00 | 167 | 167
2018-01-03 02:30 | 164 | 164
2018-01-03 03:00 | 163 | 163
2018-01-03 03:30 | 161 | 161
2018-01-03 04:00 | 161 | 161
2018-01-03 04:30 | 163 | 163
2018-01-03 05:00 | 164 | 164
2018-01-03 05:30 | 169 | 169
2018-01-03 06:00 | 176 | 176
2018-01-03 06:30 | 188 | 187
2018-01-03 07:00 | 195 | 193
2018-01-03 07:30 | 202 | 201
2018-01-03 08:00 | 210 | 207
2018-01-03 08:30 | 214 | 214
2018-01-03 09:00 | 220 | 220
2018-01-03 09:30 | 224 | 224
2018-01-03 10:00 | 226 | 226
2018-01-03 10:30 | 227 | 227
2018-01-03 11:00 | 233 | 233
2018-01-03 11:30 | 241 | 241
2018-01-03 12:00 | 249 | 249
2018-01-03 12:30 | 256 | 255
2018-01-03 13:00 | 260 | 259
2018-01-03 13:30 | 281 | 280
2018-01-03 14:00 | 336 | 334
2018-01-03 14:30 | 327 | 327
2018-01-03 15:00 | 310 | 310
2018-01-03 15:30 | 294 | 294
2018-01-03 16:00 | 283 | 283
2018-01-03 16:30 | 275 | 275
2018-01-03 17:00 | 281 | 281
2018-01-03 17:30 | 287 | 287
2018-01-03 18:00 | 286 | 286
2018-01-03 18:30 | 284 | 283
2018-01-03 19:00 | 290 | 287
2018-01-03 19:30 | 292 | 289
2018-01-03 20:00 | 291 | 289
2018-01-03 20:30 | 282 | 280
2018-01-03 21:00 | 267 | 266
2018-01-03 21:30 | 252 | 252
2018-01-03 22:00 | 241 | 240
2018-01-03 22:30 | 232 | 232
2018-01-03 23:00 | 227 | 227
2018-01-03 23:30 | 214 | 214
2018-01-04 | 195 | 194
2018-01-04 00:30 | 180 | 179
2018-01-04 01:00 | 172 | 171
2018-01-04 01:30 | 166 | 166
2018-01-04 02:00 | 162 | 162
2018-01-04 02:30 | 158 | 158
2018-01-04 03:00 | 156 | 155
2018-01-04 03:30 | 155 | 155
2018-01-04 04:00 | 155 | 155
2018-01-04 04:30 | 157 | 157
2018-01-04 05:00 | 159 | 159
2018-01-04 05:30 | 164 | 164
2018-01-04 06:00 | 170 | 169
2018-01-04 06:30 | 183 | 182
2018-01-04 07:00 | 190 | 190
2018-01-04 07:30 | 200 | 199
2018-01-04 08:00 | 205 | 204
2018-01-04 08:30 | 214 | 213
2018-01-04 09:00 | 220 | 219
2018-01-04 09:30 | 225 | 225
2018-01-04 10:00 | 228 | 228
2018-01-04 10:30 | 236 | 236
2018-01-04 11:00 | 240 | 240
2018-01-04 11:30 | 240 | 240
2018-01-04 12:00 | 245 | 245
2018-01-04 12:30 | 254 | 254
2018-01-04 13:00 | 256 | 256
2018-01-04 13:30 | 260 | 259
2018-01-04 14:00 | 264 | 264
2018-01-04 14:30 | 266 | 266
2018-01-04 15:00 | 264 | 263
2018-01-04 15:30 | 259 | 259
2018-01-04 16:00 | 261 | 261
2018-01-04 16:30 | 268 | 268
2018-01-04 17:00 | 279 | 278
2018-01-04 17:30 | 284 | 283
2018-01-04 18:00 | 285 | 285
2018-01-04 18:30 | 281 | 281
2018-01-04 19:00 | 284 | 283
2018-01-04 19:30 | 286 | 285
2018-01-04 20:00 | 286 | 286
2018-01-04 20:30 | 279 | 278
2018-01-04 21:00 | 266 | 266
2018-01-04 21:30 | 253 | 253
2018-01-04 22:00 | 240 | 240
2018-01-04 22:30 | 233 | 231
2018-01-04 23:00 | 227 | 225
2018-01-04 23:30 | 212 | 211
2018-01-05 | 196 | 194
2018-01-05 00:30 | 181 | 179
2018-01-05 01:00 | 174 | 173
2018-01-05 01:30 | 170 | 169
2018-01-05 02:00 | 165 | 164
2018-01-05 02:30 | 163 | 162
2018-01-05 03:00 | 161 | 160
2018-01-05 03:30 | 159 | 159
2018-01-05 04:00 | 160 | 159
2018-01-05 04:30 | 162 | 161
2018-01-05 05:00 | 163 | 162
2018-01-05 05:30 | 168 | 167
2018-01-05 06:00 | 172 | 171
2018-01-05 06:30 | 186 | 184
2018-01-05 07:00 | 196 | 194
2018-01-05 07:30 | 209 | 206
2018-01-05 08:00 | 212 | 212
2018-01-05 08:30 | 220 | 220
2018-01-05 09:00 | 230 | 230
2018-01-05 09:30 | 249 | 249
2018-01-05 10:00 | 260 | 260
2018-01-05 10:30 | 252 | 252
2018-01-05 11:00 | 237 | 237
2018-01-05 11:30 | 242 | 242
2018-01-05 12:00 | 241 | 241
2018-01-05 12:30 | 244 | 244
2018-01-05 13:00 | 254 | 254
2018-01-05 13:30 | 257 | 257
2018-01-05 14:00 | 261 | 261
2018-01-05 14:30 | 263 | 263
2018-01-05 15:00 | 269 | 269
2018-01-05 15:30 | 277 | 277
2018-01-05 16:00 | 283 | 282
2018-01-05 16:30 | 291 | 291
2018-01-05 17:00 | 300 | 300
2018-01-05 17:30 | 292 | 291
2018-01-05 18:00 | 278 | 278
2018-01-05 18:30 | 275 | 275
2018-01-05 19:00 | 278 | 278
2018-01-05 19:30 | 281 | 281
2018-01-05 20:00 | 280 | 280
2018-01-05 20:30 | 274 | 274
2018-01-05 21:00 | 263 | 263
2018-01-05 21:30 | 254 | 254
2018-01-05 22:00 | 242 | 242
2018-01-05 22:30 | 236 | 236
2018-01-05 23:00 | 232 | 232
2018-01-05 23:30 | 215 | 214
2018-01-06 | 197 | 197
2018-01-06 00:30 | 184 | 184
2018-01-06 01:00 | 177 | 176
2018-01-06 01:30 | 171 | 171
2018-01-06 02:00 | 165 | 165
2018-01-06 02:30 | 162 | 162
2018-01-06 03:00 | 160 | 160
2018-01-06 03:30 | 158 | 158
2018-01-06 04:00 | 156 | 156
2018-01-06 04:30 | 155 | 155
2018-01-06 05:00 | 154 | 154
2018-01-06 05:30 | 152 | 152
2018-01-06 06:00 | 153 | 153
2018-01-06 06:30 | 157 | 157
2018-01-06 07:00 | 160 | 160
2018-01-06 07:30 | 167 | 167
2018-01-06 08:00 | 172 | 172
2018-01-06 08:30 | 178 | 178
2018-01-06 09:00 | 183 | 181
2018-01-06 09:30 | 189 | 187
2018-01-06 10:00 | 190 | 190
2018-01-06 10:30 | 192 | 192
2018-01-06 11:00 | 194 | 194
2018-01-06 11:30 | 199 | 199
2018-01-06 12:00 | 201 | 201
2018-01-06 12:30 | 205 | 205
2018-01-06 13:00 | 210 | 210
2018-01-06 13:30 | 217 | 217
2018-01-06 14:00 | 226 | 226
2018-01-06 14:30 | 234 | 234
2018-01-06 15:00 | 243 | 242
2018-01-06 15:30 | 251 | 251
2018-01-06 16:00 | 262 | 261
2018-01-06 16:30 | 273 | 272
2018-01-06 17:00 | 282 | 282
2018-01-06 17:30 | 283 | 282
2018-01-06 18:00 | 280 | 280
2018-01-06 18:30 | 276 | 276
2018-01-06 19:00 | 275 | 275
2018-01-06 19:30 | 275 | 275
2018-01-06 20:00 | 273 | 272
2018-01-06 20:30 | 265 | 265
2018-01-06 21:00 | 251 | 251
2018-01-06 21:30 | 242 | 242
2018-01-06 22:00 | 232 | 232
2018-01-06 22:30 | 227 | 227
2018-01-06 23:00 | 223 | 223
2018-01-06 23:30 | 206 | 206
2018-01-07 | 188 | 188
2018-01-07 00:30 | 175 | 175
2018-01-07 01:00 | 168 | 168
2018-01-07 01:30 | 162 | 162
2018-01-07 02:00 | 157 | 156
2018-01-07 02:30 | 153 | 153
2018-01-07 03:00 | 151 | 151
2018-01-07 03:30 | 150 | 150
2018-01-07 04:00 | 148 | 148
2018-01-07 04:30 | 146 | 146
2018-01-07 05:00 | 146 | 146
2018-01-07 05:30 | 146 | 145
2018-01-07 06:00 | 146 | 145
2018-01-07 06:30 | 148 | 147
2018-01-07 07:00 | 149 | 149
2018-01-07 07:30 | 153 | 153
2018-01-07 08:00 | 156 | 156
2018-01-07 08:30 | 164 | 164
2018-01-07 09:00 | 169 | 169
2018-01-07 09:30 | 175 | 174
2018-01-07 10:00 | 177 | 177
2018-01-07 10:30 | 181 | 181
2018-01-07 11:00 | 186 | 186
2018-01-07 11:30 | 192 | 192
2018-01-07 12:00 | 200 | 199
2018-01-07 12:30 | 206 | 205
2018-01-07 13:00 | 213 | 212
2018-01-07 13:30 | 220 | 220
2018-01-07 14:00 | 228 | 227
2018-01-07 14:30 | 240 | 239
2018-01-07 15:00 | 253 | 251
2018-01-07 15:30 | 264 | 262
2018-01-07 16:00 | 276 | 275
2018-01-07 16:30 | 287 | 286
2018-01-07 17:00 | 297 | 297
2018-01-07 17:30 | 303 | 300
2018-01-07 18:00 | 303 | 300
2018-01-07 18:30 | 300 | 297
2018-01-07 19:00 | 299 | 297
2018-01-07 19:30 | 299 | 296
2018-01-07 20:00 | 296 | 294
2018-01-07 20:30 | 286 | 284
2018-01-07 21:00 | 270 | 267
2018-01-07 21:30 | 257 | 254
2018-01-07 22:00 | 243 | 241
2018-01-07 22:30 | 233 | 232
2018-01-07 23:00 | 228 | 226
2018-01-07 23:30 | 211 | 210
2018-01-08 | 193 | 192
2018-01-08 00:30 | 180 | 180
2018-01-08 01:00 | 172 | 172
2018-01-08 01:30 | 167 | 167
2018-01-08 02:00 | 164 | 163
2018-01-08 02:30 | 160 | 160
2018-01-08 03:00 | 158 | 158
2018-01-08 03:30 | 158 | 158
2018-01-08 04:00 | 158 | 158
2018-01-08 04:30 | 160 | 160
2018-01-08 05:00 | 164 | 164
2018-01-08 05:30 | 171 | 171
2018-01-08 06:00 | 180 | 179
2018-01-08 06:30 | 197 | 196
2018-01-08 07:00 | 210 | 210
2018-01-08 07:30 | 224 | 224
2018-01-08 08:00 | 233 | 232
2018-01-08 08:30 | 239 | 238
2018-01-08 09:00 | 243 | 242
2018-01-08 09:30 | 249 | 246
2018-01-08 10:00 | 251 | 248
2018-01-08 10:30 | 254 | 251
2018-01-08 11:00 | 259 | 257
2018-01-08 11:30 | 263 | 262
2018-01-08 12:00 | 266 | 265
2018-01-08 12:30 | 276 | 275
2018-01-08 13:00 | 286 | 286
2018-01-08 13:30 | 298 | 298
2018-01-08 14:00 | 308 | 308
2018-01-08 14:30 | 316 | 316
2018-01-08 15:00 | 327 | 326
2018-01-08 15:30 | 335 | 335
2018-01-08 16:00 | 345 | 344
2018-01-08 16:30 | 352 | 352
2018-01-08 17:00 | 361 | 360
2018-01-08 17:30 | 360 | 360
2018-01-08 18:00 | 352 | 351
2018-01-08 18:30 | 340 | 340
2018-01-08 19:00 | 338 | 337
2018-01-08 19:30 | 336 | 335
2018-01-08 20:00 | 331 | 329
2018-01-08 20:30 | 321 | 320
2018-01-08 21:00 | 303 | 302
2018-01-08 21:30 | 288 | 288
2018-01-08 22:00 | 272 | 272
2018-01-08 22:30 | 264 | 264
2018-01-08 23:00 | 256 | 256
2018-01-08 23:30 | 236 | 236
2018-01-09 | 217 | 217
2018-01-09 00:30 | 200 | 200
2018-01-09 01:00 | 192 | 192
2018-01-09 01:30 | 187 | 187
2018-01-09 02:00 | 184 | 184
2018-01-09 02:30 | 181 | 181
2018-01-09 03:00 | 178 | 178
2018-01-09 03:30 | 176 | 176
2018-01-09 04:00 | 174 | 174
2018-01-09 04:30 | 177 | 177
2018-01-09 05:00 | 181 | 181
2018-01-09 05:30 | 187 | 187
2018-01-09 06:00 | 195 | 195
2018-01-09 06:30 | 211 | 211
2018-01-09 07:00 | 225 | 225
2018-01-09 07:30 | 239 | 238
2018-01-09 08:00 | 246 | 245
2018-01-09 08:30 | 252 | 250
2018-01-09 09:00 | 254 | 252
2018-01-09 09:30 | 259 | 257
2018-01-09 10:00 | 259 | 257
2018-01-09 10:30 | 260 | 260
2018-01-09 11:00 | 263 | 263
2018-01-09 11:30 | 269 | 268
2018-01-09 12:00 | 279 | 278
2018-01-09 12:30 | 289 | 289
2018-01-09 13:00 | 298 | 297
2018-01-09 13:30 | 305 | 304
2018-01-09 14:00 | 309 | 308
2018-01-09 14:30 | 319 | 317
2018-01-09 15:00 | 327 | 325
2018-01-09 15:30 | 336 | 335
2018-01-09 16:00 | 347 | 346
2018-01-09 16:30 | 354 | 354
2018-01-09 17:00 | 363 | 363
2018-01-09 17:30 | 361 | 361
2018-01-09 18:00 | 353 | 353
2018-01-09 18:30 | 340 | 340
2018-01-09 19:00 | 338 | 338
2018-01-09 19:30 | 336 | 336
2018-01-09 20:00 | 332 | 332
2018-01-09 20:30 | 320 | 320
2018-01-09 21:00 | 302 | 301
2018-01-09 21:30 | 286 | 286
2018-01-09 22:00 | 270 | 270
2018-01-09 22:30 | 257 | 257
2018-01-09 23:00 | 247 | 246
2018-01-09 23:30 | 230 | 230
2018-01-10 | 212 | 212
2018-01-10 00:30 | 197 | 196
2018-01-10 01:00 | 191 | 189
2018-01-10 01:30 | 185 | 184
2018-01-10 02:00 | 180 | 179
2018-01-10 02:30 | 177 | 176
2018-01-10 03:00 | 174 | 173
2018-01-10 03:30 | 172 | 172
2018-01-10 04:00 | 172 | 172
2018-01-10 04:30 | 173 | 173
2018-01-10 05:00 | 178 | 178
2018-01-10 05:30 | 187 | 186
2018-01-10 06:00 | 195 | 194
2018-01-10 06:30 | 211 | 211
2018-01-10 07:00 | 223 | 223
2018-01-10 07:30 | 239 | 237
2018-01-10 08:00 | 249 | 248
2018-01-10 08:30 | 257 | 257
2018-01-10 09:00 | 262 | 262
2018-01-10 09:30 | 267 | 266
2018-01-10 10:00 | 273 | 273
2018-01-10 10:30 | 286 | 285
2018-01-10 11:00 | 294 | 293
2018-01-10 11:30 | 295 | 295
2018-01-10 12:00 | 297 | 296
2018-01-10 12:30 | 296 | 296
2018-01-10 13:00 | 300 | 299
2018-01-10 13:30 | 305 | 305
2018-01-10 14:00 | 309 | 308
2018-01-10 14:30 | 317 | 316
2018-01-10 15:00 | 326 | 324
2018-01-10 15:30 | 336 | 334
2018-01-10 16:00 | 346 | 345
2018-01-10 16:30 | 355 | 354
2018-01-10 17:00 | 364 | 363
2018-01-10 17:30 | 364 | 364
2018-01-10 18:00 | 359 | 359
2018-01-10 18:30 | 345 | 344
2018-01-10 19:00 | 345 | 342
2018-01-10 19:30 | 345 | 343
2018-01-10 20:00 | 340 | 339
2018-01-10 20:30 | 330 | 329
2018-01-10 21:00 | 315 | 314
2018-01-10 21:30 | 299 | 299
2018-01-10 22:00 | 282 | 281
2018-01-10 22:30 | 270 | 268
2018-01-10 23:00 | 262 | 260
2018-01-10 23:30 | 241 | 241
2018-01-11 | 224 | 223
2018-01-11 00:30 | 207 | 206
2018-01-11 01:00 | 197 | 196
2018-01-11 01:30 | 190 | 190
2018-01-11 02:00 | 187 | 187
2018-01-11 02:30 | 184 | 184
2018-01-11 03:00 | 182 | 182
2018-01-11 03:30 | 182 | 181
2018-01-11 04:00 | 181 | 181
2018-01-11 04:30 | 181 | 181
2018-01-11 05:00 | 185 | 185
2018-01-11 05:30 | 192 | 192
2018-01-11 06:00 | 201 | 200
2018-01-11 06:30 | 216 | 216
2018-01-11 07:00 | 230 | 230
2018-01-11 07:30 | 249 | 249
2018-01-11 08:00 | 260 | 260
2018-01-11 08:30 | 268 | 267
2018-01-11 09:00 | 273 | 273
2018-01-11 09:30 | 278 | 278
2018-01-11 10:00 | 279 | 279
2018-01-11 10:30 | 284 | 283
2018-01-11 11:00 | 290 | 289
2018-01-11 11:30 | 299 | 299
2018-01-11 12:00 | 308 | 307
2018-01-11 12:30 | 308 | 307
2018-01-11 13:00 | 303 | 302
2018-01-11 13:30 | 311 | 309
2018-01-11 14:00 | 323 | 320
2018-01-11 14:30 | 338 | 337
2018-01-11 15:00 | 350 | 349
2018-01-11 15:30 | 351 | 350
2018-01-11 16:00 | 359 | 359
2018-01-11 16:30 | 361 | 361
2018-01-11 17:00 | 354 | 354
2018-01-11 17:30 | 360 | 358
2018-01-11 18:00 | 362 | 361
2018-01-11 18:30 | 352 | 352
2018-01-11 19:00 | 354 | 352
2018-01-11 19:30 | 356 | 354
2018-01-11 20:00 | 351 | 350
2018-01-11 20:30 | 342 | 341
2018-01-11 21:00 | 324 | 323
2018-01-11 21:30 | 305 | 305
2018-01-11 22:00 | 287 | 287
2018-01-11 22:30 | 274 | 274
2018-01-11 23:00 | 264 | 264
2018-01-11 23:30 | 247 | 247
2018-01-12 | 225 | 225
2018-01-12 00:30 | 209 | 208
2018-01-12 01:00 | 201 | 199
2018-01-12 01:30 | 194 | 193
2018-01-12 02:00 | 190 | 189
2018-01-12 02:30 | 188 | 187
2018-01-12 03:00 | 185 | 184
2018-01-12 03:30 | 184 | 184
2018-01-12 04:00 | 184 | 183
2018-01-12 04:30 | 186 | 185
2018-01-12 05:00 | 189 | 188
2018-01-12 05:30 | 196 | 196
2018-01-12 06:00 | 205 | 204
2018-01-12 06:30 | 221 | 220
2018-01-12 07:00 | 237 | 236
2018-01-12 07:30 | 254 | 253
2018-01-12 08:00 | 266 | 265
2018-01-12 08:30 | 275 | 275
2018-01-12 09:00 | 278 | 278
2018-01-12 09:30 | 286 | 285
2018-01-12 10:00 | 292 | 292
2018-01-12 10:30 | 291 | 291
2018-01-12 11:00 | 295 | 295
2018-01-12 11:30 | 296 | 296
2018-01-12 12:00 | 304 | 304
2018-01-12 12:30 | 308 | 308
2018-01-12 13:00 | 317 | 316
2018-01-12 13:30 | 323 | 322
2018-01-12 14:00 | 331 | 330
2018-01-12 14:30 | 339 | 338
2018-01-12 15:00 | 350 | 350
2018-01-12 15:30 | 361 | 361
2018-01-12 16:00 | 371 | 371
2018-01-12 16:30 | 379 | 379
2018-01-12 17:00 | 387 | 387
2018-01-12 17:30 | 385 | 385
2018-01-12 18:00 | 370 | 370
2018-01-12 18:30 | 355 | 355
2018-01-12 19:00 | 354 | 354
2018-01-12 19:30 | 353 | 353
2018-01-12 20:00 | 351 | 351
2018-01-12 20:30 | 341 | 341
2018-01-12 21:00 | 326 | 326
2018-01-12 21:30 | 312 | 312
2018-01-12 22:00 | 300 | 299
2018-01-12 22:30 | 289 | 288
2018-01-12 23:00 | 278 | 278
2018-01-12 23:30 | 255 | 253
2018-01-13 | 234 | 233
2018-01-13 00:30 | 218 | 217
2018-01-13 01:00 | 209 | 209
2018-01-13 01:30 | 201 | 201
2018-01-13 02:00 | 195 | 195
2018-01-13 02:30 | 191 | 191
2018-01-13 03:00 | 188 | 188
2018-01-13 03:30 | 186 | 186
2018-01-13 04:00 | 184 | 184
2018-01-13 04:30 | 184 | 184
2018-01-13 05:00 | 183 | 183
2018-01-13 05:30 | 182 | 182
2018-01-13 06:00 | 185 | 185
2018-01-13 06:30 | 193 | 193
2018-01-13 07:00 | 201 | 199
2018-01-13 07:30 | 211 | 210
2018-01-13 08:00 | 221 | 219
2018-01-13 08:30 | 234 | 230
2018-01-13 09:00 | 244 | 243
2018-01-13 09:30 | 254 | 253
2018-01-13 10:00 | 263 | 263
2018-01-13 10:30 | 272 | 272
2018-01-13 11:00 | 282 | 280
2018-01-13 11:30 | 289 | 288
2018-01-13 12:00 | 299 | 297
2018-01-13 12:30 | 309 | 308
2018-01-13 13:00 | 319 | 317
2018-01-13 13:30 | 330 | 329
2018-01-13 14:00 | 347 | 347
2018-01-13 14:30 | 353 | 352
2018-01-13 15:00 | 357 | 357
2018-01-13 15:30 | 368 | 368
2018-01-13 16:00 | 381 | 381
2018-01-13 16:30 | 388 | 388
2018-01-13 17:00 | 391 | 391
2018-01-13 17:30 | 385 | 385
2018-01-13 18:00 | 375 | 375
2018-01-13 18:30 | 363 | 363
2018-01-13 19:00 | 363 | 363
2018-01-13 19:30 | 363 | 362
2018-01-13 20:00 | 359 | 358
2018-01-13 20:30 | 347 | 347
2018-01-13 21:00 | 331 | 331
2018-01-13 21:30 | 321 | 321
2018-01-13 22:00 | 307 | 307
2018-01-13 22:30 | 299 | 299
2018-01-13 23:00 | 291 | 290
2018-01-13 23:30 | 270 | 268
2018-01-14 | 245 | 245
2018-01-14 00:30 | 226 | 226
2018-01-14 01:00 | 217 | 216
2018-01-14 01:30 | 209 | 208
2018-01-14 02:00 | 202 | 201
2018-01-14 02:30 | 198 | 197
2018-01-14 03:00 | 194 | 193
2018-01-14 03:30 | 190 | 190
2018-01-14 04:00 | 188 | 188
2018-01-14 04:30 | 187 | 187
2018-01-14 05:00 | 185 | 185
2018-01-14 05:30 | 182 | 182
2018-01-14 06:00 | 183 | 183
2018-01-14 06:30 | 187 | 187
2018-01-14 07:00 | 196 | 195
2018-01-14 07:30 | 208 | 207
2018-01-14 08:00 | 223 | 223
2018-01-14 08:30 | 239 | 238
2018-01-14 09:00 | 254 | 254
2018-01-14 09:30 | 273 | 273
2018-01-14 10:00 | 281 | 280
2018-01-14 10:30 | 289 | 289
2018-01-14 11:00 | 289 | 289
2018-01-14 11:30 | 290 | 289
2018-01-14 12:00 | 292 | 291
2018-01-14 12:30 | 303 | 302
2018-01-14 13:00 | 314 | 313
2018-01-14 13:30 | 323 | 322
2018-01-14 14:00 | 329 | 328
2018-01-14 14:30 | 335 | 334
2018-01-14 15:00 | 348 | 348
2018-01-14 15:30 | 351 | 351
2018-01-14 16:00 | 351 | 351
2018-01-14 16:30 | 349 | 349
2018-01-14 17:00 | 342 | 342
2018-01-14 17:30 | 323 | 323
2018-01-14 18:00 | 305 | 305
2018-01-14 18:30 | 290 | 290
2018-01-14 19:00 | 283 | 283
2018-01-14 19:30 | 277 | 274
2018-01-14 20:00 | 272 | 270
2018-01-14 20:30 | 263 | 261
2018-01-14 21:00 | 246 | 245
2018-01-14 21:30 | 234 | 233
2018-01-14 22:00 | 222 | 221
2018-01-14 22:30 | 216 | 215
2018-01-14 23:00 | 211 | 211
2018-01-14 23:30 | 196 | 195
2018-01-15 | 177 | 176
2018-01-15 00:30 | 163 | 163
2018-01-15 01:00 | 156 | 156
2018-01-15 01:30 | 153 | 153
2018-01-15 02:00 | 150 | 150
2018-01-15 02:30 | 148 | 148
2018-01-15 03:00 | 145 | 145
2018-01-15 03:30 | 145 | 145
2018-01-15 04:00 | 144 | 144
2018-01-15 04:30 | 149 | 148
2018-01-15 05:00 | 155 | 155
2018-01-15 05:30 | 164 | 164
2018-01-15 06:00 | 174 | 174
2018-01-15 06:30 | 191 | 189
2018-01-15 07:00 | 202 | 200
2018-01-15 07:30 | 212 | 209
2018-01-15 08:00 | 216 | 214
2018-01-15 08:30 | 218 | 216
2018-01-15 09:00 | 217 | 215
2018-01-15 09:30 | 216 | 214
2018-01-15 10:00 | 216 | 215
2018-01-15 10:30 | 216 | 215
2018-01-15 11:00 | 219 | 218
2018-01-15 11:30 | 222 | 221
2018-01-15 12:00 | 227 | 225
2018-01-15 12:30 | 233 | 233
2018-01-15 13:00 | 241 | 241
2018-01-15 13:30 | 242 | 242
2018-01-15 14:00 | 248 | 248
2018-01-15 14:30 | 253 | 253
2018-01-15 15:00 | 257 | 257
2018-01-15 15:30 | 263 | 262
2018-01-15 16:00 | 269 | 269
2018-01-15 16:30 | 274 | 274
2018-01-15 17:00 | 281 | 281
2018-01-15 17:30 | 281 | 281
2018-01-15 18:00 | 278 | 278
2018-01-15 18:30 | 273 | 273
2018-01-15 19:00 | 275 | 275
2018-01-15 19:30 | 276 | 276
2018-01-15 20:00 | 274 | 274
2018-01-15 20:30 | 265 | 265
2018-01-15 21:00 | 252 | 251
2018-01-15 21:30 | 240 | 238
2018-01-15 22:00 | 228 | 227
2018-01-15 22:30 | 220 | 219
2018-01-15 23:00 | 214 | 214
2018-01-15 23:30 | 199 | 199
2018-01-16 | 182 | 182
2018-01-16 00:30 | 168 | 168
2018-01-16 01:00 | 161 | 161
2018-01-16 01:30 | 156 | 156
2018-01-16 02:00 | 153 | 153
2018-01-16 02:30 | 152 | 152
2018-01-16 03:00 | 150 | 150
2018-01-16 03:30 | 150 | 150
2018-01-16 04:00 | 150 | 149
2018-01-16 04:30 | 152 | 152
2018-01-16 05:00 | 159 | 159
2018-01-16 05:30 | 166 | 166
2018-01-16 06:00 | 175 | 175
2018-01-16 06:30 | 188 | 187
2018-01-16 07:00 | 199 | 197
2018-01-16 07:30 | 208 | 207
2018-01-16 08:00 | 210 | 210
2018-01-16 08:30 | 212 | 212
2018-01-16 09:00 | 209 | 209
2018-01-16 09:30 | 205 | 205
2018-01-16 10:00 | 200 | 200
2018-01-16 10:30 | 202 | 202
2018-01-16 11:00 | 206 | 205
2018-01-16 11:30 | 212 | 211
2018-01-16 12:00 | 216 | 215
2018-01-16 12:30 | 219 | 217
2018-01-16 13:00 | 224 | 222
2018-01-16 13:30 | 228 | 227
2018-01-16 14:00 | 236 | 235
2018-01-16 14:30 | 241 | 240
2018-01-16 15:00 | 246 | 244
2018-01-16 15:30 | 252 | 251
2018-01-16 16:00 | 261 | 260
2018-01-16 16:30 | 270 | 269
2018-01-16 17:00 | 280 | 279
2018-01-16 17:30 | 283 | 283
2018-01-16 18:00 | 280 | 280
2018-01-16 18:30 | 273 | 273
2018-01-16 19:00 | 276 | 275
2018-01-16 19:30 | 279 | 278
2018-01-16 20:00 | 276 | 275
2018-01-16 20:30 | 268 | 267
2018-01-16 21:00 | 254 | 253
2018-01-16 21:30 | 241 | 240
2018-01-16 22:00 | 230 | 230
2018-01-16 22:30 | 222 | 222
2018-01-16 23:00 | 216 | 216
2018-01-16 23:30 | 202 | 202
2018-01-17 | 185 | 185
2018-01-17 00:30 | 172 | 171
2018-01-17 01:00 | 166 | 165
2018-01-17 01:30 | 161 | 161
2018-01-17 02:00 | 157 | 157
2018-01-17 02:30 | 155 | 155
2018-01-17 03:00 | 155 | 154
2018-01-17 03:30 | 154 | 154
2018-01-17 04:00 | 153 | 153
2018-01-17 04:30 | 156 | 156
2018-01-17 05:00 | 162 | 162
2018-01-17 05:30 | 169 | 169
2018-01-17 06:00 | 176 | 175
2018-01-17 06:30 | 191 | 189
2018-01-17 07:00 | 200 | 199
2018-01-17 07:30 | 209 | 208
2018-01-17 08:00 | 211 | 210
2018-01-17 08:30 | 211 | 211
2018-01-17 09:00 | 210 | 209
2018-01-17 09:30 | 210 | 209
2018-01-17 10:00 | 206 | 206
2018-01-17 10:30 | 205 | 204
2018-01-17 11:00 | 205 | 204
2018-01-17 11:30 | 208 | 207
2018-01-17 12:00 | 210 | 209
2018-01-17 12:30 | 214 | 212
2018-01-17 13:00 | 220 | 219
2018-01-17 13:30 | 228 | 226
2018-01-17 14:00 | 234 | 231
2018-01-17 14:30 | 242 | 240
2018-01-17 15:00 | 250 | 250
2018-01-17 15:30 | 257 | 257
2018-01-17 16:00 | 265 | 265
2018-01-17 16:30 | 274 | 274
2018-01-17 17:00 | 283 | 283
2018-01-17 17:30 | 288 | 288
2018-01-17 18:00 | 288 | 288
2018-01-17 18:30 | 281 | 281
2018-01-17 19:00 | 285 | 285
2018-01-17 19:30 | 288 | 288
2018-01-17 20:00 | 286 | 285
2018-01-17 20:30 | 278 | 278
2018-01-17 21:00 | 264 | 263
2018-01-17 21:30 | 253 | 252
2018-01-17 22:00 | 243 | 242
2018-01-17 22:30 | 233 | 232
2018-01-17 23:00 | 227 | 226
2018-01-17 23:30 | 211 | 211
2018-01-18 | 195 | 195
2018-01-18 00:30 | 181 | 181
2018-01-18 01:00 | 175 | 175
2018-01-18 01:30 | 170 | 170
2018-01-18 02:00 | 166 | 166
2018-01-18 02:30 | 164 | 164
2018-01-18 03:00 | 163 | 162
2018-01-18 03:30 | 163 | 162
2018-01-18 04:00 | 162 | 162
2018-01-18 04:30 | 165 | 165
2018-01-18 05:00 | 171 | 170
2018-01-18 05:30 | 179 | 178
2018-01-18 06:00 | 188 | 187
2018-01-18 06:30 | 203 | 200
2018-01-18 07:00 | 213 | 211
2018-01-18 07:30 | 223 | 221
2018-01-18 08:00 | 226 | 226
2018-01-18 08:30 | 229 | 229
2018-01-18 09:00 | 229 | 229
2018-01-18 09:30 | 225 | 225
2018-01-18 10:00 | 224 | 224
2018-01-18 10:30 | 226 | 226
2018-01-18 11:00 | 231 | 231
2018-01-18 11:30 | 235 | 234
2018-01-18 12:00 | 239 | 238
2018-01-18 12:30 | 242 | 242
2018-01-18 13:00 | 248 | 248
2018-01-18 13:30 | 255 | 255
2018-01-18 14:00 | 261 | 261
2018-01-18 14:30 | 266 | 266
2018-01-18 15:00 | 271 | 271
2018-01-18 15:30 | 274 | 274
2018-01-18 16:00 | 282 | 282
2018-01-18 16:30 | 292 | 292
2018-01-18 17:00 | 300 | 300
2018-01-18 17:30 | 301 | 301
2018-01-18 18:00 | 299 | 299
2018-01-18 18:30 | 292 | 292
2018-01-18 19:00 | 296 | 296
2018-01-18 19:30 | 299 | 299
2018-01-18 20:00 | 297 | 296
2018-01-18 20:30 | 288 | 288
2018-01-18 21:00 | 274 | 274
2018-01-18 21:30 | 259 | 259
2018-01-18 22:00 | 245 | 245
2018-01-18 22:30 | 235 | 235
2018-01-18 23:00 | 230 | 230
2018-01-18 23:30 | 214 | 214
2018-01-19 | 196 | 196
2018-01-19 00:30 | 181 | 181
2018-01-19 01:00 | 175 | 175
2018-01-19 01:30 | 170 | 169
2018-01-19 02:00 | 167 | 166
2018-01-19 02:30 | 162 | 162
2018-01-19 03:00 | 160 | 160
2018-01-19 03:30 | 159 | 159
2018-01-19 04:00 | 159 | 159
2018-01-19 04:30 | 161 | 161
2018-01-19 05:00 | 167 | 167
2018-01-19 05:30 | 174 | 174
2018-01-19 06:00 | 183 | 183
2018-01-19 06:30 | 196 | 196
2018-01-19 07:00 | 205 | 205
2018-01-19 07:30 | 215 | 215
2018-01-19 08:00 | 217 | 217
2018-01-19 08:30 | 219 | 219
2018-01-19 09:00 | 219 | 219
2018-01-19 09:30 | 217 | 217
2018-01-19 10:00 | 217 | 217
2018-01-19 10:30 | 218 | 218
2018-01-19 11:00 | 218 | 218
2018-01-19 11:30 | 221 | 221
2018-01-19 12:00 | 231 | 231
2018-01-19 12:30 | 235 | 235
2018-01-19 13:00 | 239 | 239
2018-01-19 13:30 | 251 | 251
2018-01-19 14:00 | 260 | 260
2018-01-19 14:30 | 270 | 269
2018-01-19 15:00 | 280 | 279
2018-01-19 15:30 | 289 | 289
2018-01-19 16:00 | 299 | 299
2018-01-19 16:30 | 309 | 309
2018-01-19 17:00 | 318 | 317
2018-01-19 17:30 | 315 | 315
2018-01-19 18:00 | 309 | 309
2018-01-19 18:30 | 300 | 300
2018-01-19 19:00 | 300 | 300
2018-01-19 19:30 | 301 | 301
2018-01-19 20:00 | 299 | 299
2018-01-19 20:30 | 283 | 283
2018-01-19 21:00 | 272 | 271
2018-01-19 21:30 | 261 | 261
2018-01-19 22:00 | 251 | 251
2018-01-19 22:30 | 240 | 240
2018-01-19 23:00 | 235 | 235
2018-01-19 23:30 | 217 | 217
2018-01-20 | 197 | 197
2018-01-20 00:30 | 182 | 182
2018-01-20 01:00 | 175 | 175
2018-01-20 01:30 | 171 | 171
2018-01-20 02:00 | 166 | 166
2018-01-20 02:30 | 162 | 162
2018-01-20 03:00 | 160 | 160
2018-01-20 03:30 | 158 | 158
2018-01-20 04:00 | 158 | 158
2018-01-20 04:30 | 158 | 158
2018-01-20 05:00 | 158 | 158
2018-01-20 05:30 | 159 | 159
2018-01-20 06:00 | 161 | 161
2018-01-20 06:30 | 165 | 165
2018-01-20 07:00 | 167 | 167
2018-01-20 07:30 | 173 | 173
2018-01-20 08:00 | 176 | 176
2018-01-20 08:30 | 180 | 179
2018-01-20 09:00 | 185 | 185
2018-01-20 09:30 | 183 | 183
2018-01-20 10:00 | 184 | 184
2018-01-20 10:30 | 186 | 186
2018-01-20 11:00 | 185 | 185
2018-01-20 11:30 | 187 | 187
2018-01-20 12:00 | 189 | 189
2018-01-20 12:30 | 193 | 193
2018-01-20 13:00 | 199 | 199
2018-01-20 13:30 | 205 | 205
2018-01-20 14:00 | 213 | 213
2018-01-20 14:30 | 223 | 223
2018-01-20 15:00 | 231 | 231
2018-01-20 15:30 | 240 | 240
2018-01-20 16:00 | 250 | 250
2018-01-20 16:30 | 260 | 259
2018-01-20 17:00 | 270 | 269
2018-01-20 17:30 | 271 | 270
2018-01-20 18:00 | 269 | 268
2018-01-20 18:30 | 266 | 266
2018-01-20 19:00 | 267 | 267
2018-01-20 19:30 | 269 | 269
2018-01-20 20:00 | 267 | 267
2018-01-20 20:30 | 261 | 261
2018-01-20 21:00 | 250 | 250
2018-01-20 21:30 | 241 | 241
2018-01-20 22:00 | 233 | 232
2018-01-20 22:30 | 227 | 227
2018-01-20 23:00 | 225 | 225
2018-01-20 23:30 | 210 | 210
2018-01-21 | 194 | 193
2018-01-21 00:30 | 176 | 176
2018-01-21 01:00 | 169 | 169
2018-01-21 01:30 | 163 | 163
2018-01-21 02:00 | 159 | 159
2018-01-21 02:30 | 156 | 156
2018-01-21 03:00 | 155 | 155
2018-01-21 03:30 | 154 | 154
2018-01-21 04:00 | 152 | 152
2018-01-21 04:30 | 150 | 150
2018-01-21 05:00 | 148 | 148
2018-01-21 05:30 | 148 | 148
2018-01-21 06:00 | 148 | 147
2018-01-21 06:30 | 150 | 150
2018-01-21 07:00 | 151 | 151
2018-01-21 07:30 | 158 | 158
2018-01-21 08:00 | 164 | 164
2018-01-21 08:30 | 172 | 171
2018-01-21 09:00 | 180 | 179
2018-01-21 09:30 | 197 | 196
2018-01-21 10:00 | 204 | 203
2018-01-21 10:30 | 199 | 199
2018-01-21 11:00 | 196 | 196
2018-01-21 11:30 | 197 | 197
2018-01-21 12:00 | 199 | 199
2018-01-21 12:30 | 205 | 205
2018-01-21 13:00 | 215 | 215
2018-01-21 13:30 | 218 | 218
2018-01-21 14:00 | 221 | 221
2018-01-21 14:30 | 232 | 232
2018-01-21 15:00 | 249 | 249
2018-01-21 15:30 | 254 | 254
2018-01-21 16:00 | 258 | 258
2018-01-21 16:30 | 262 | 262
2018-01-21 17:00 | 267 | 267
2018-01-21 17:30 | 269 | 269
2018-01-21 18:00 | 271 | 271
2018-01-21 18:30 | 273 | 273
2018-01-21 19:00 | 279 | 279
2018-01-21 19:30 | 283 | 283
2018-01-21 20:00 | 282 | 282
2018-01-21 20:30 | 276 | 276
2018-01-21 21:00 | 263 | 263
2018-01-21 21:30 | 252 | 252
2018-01-21 22:00 | 241 | 241
2018-01-21 22:30 | 231 | 231
2018-01-21 23:00 | 227 | 226
2018-01-21 23:30 | 211 | 210
2018-01-22 | 193 | 193
2018-01-22 00:30 | 179 | 179
2018-01-22 01:00 | 172 | 172
2018-01-22 01:30 | 168 | 168
2018-01-22 02:00 | 164 | 164
2018-01-22 02:30 | 162 | 162
2018-01-22 03:00 | 160 | 160
2018-01-22 03:30 | 160 | 160
2018-01-22 04:00 | 160 | 160
2018-01-22 04:30 | 164 | 164
2018-01-22 05:00 | 170 | 170
2018-01-22 05:30 | 178 | 178
2018-01-22 06:00 | 189 | 189
2018-01-22 06:30 | 210 | 209
2018-01-22 07:00 | 227 | 226
2018-01-22 07:30 | 245 | 245
2018-01-22 08:00 | 257 | 257
2018-01-22 08:30 | 261 | 261
2018-01-22 09:00 | 268 | 267
2018-01-22 09:30 | 271 | 270
2018-01-22 10:00 | 272 | 272
2018-01-22 10:30 | 271 | 270
2018-01-22 11:00 | 271 | 271
2018-01-22 11:30 | 272 | 272
2018-01-22 12:00 | 278 | 278
2018-01-22 12:30 | 282 | 282
2018-01-22 13:00 | 286 | 285
2018-01-22 13:30 | 294 | 294
2018-01-22 14:00 | 300 | 300
2018-01-22 14:30 | 305 | 304
2018-01-22 15:00 | 309 | 309
2018-01-22 15:30 | 314 | 314
2018-01-22 16:00 | 326 | 326
2018-01-22 16:30 | 335 | 334
2018-01-22 17:00 | 340 | 340
2018-01-22 17:30 | 339 | 338
2018-01-22 18:00 | 333 | 333
2018-01-22 18:30 | 323 | 323
2018-01-22 19:00 | 324 | 324
2018-01-22 19:30 | 325 | 325
2018-01-22 20:00 | 322 | 322
2018-01-22 20:30 | 314 | 314
2018-01-22 21:00 | 298 | 298
2018-01-22 21:30 | 282 | 282
2018-01-22 22:00 | 266 | 266
2018-01-22 22:30 | 255 | 255
2018-01-22 23:00 | 246 | 246
2018-01-22 23:30 | 227 | 227
2018-01-23 | 209 | 209
2018-01-23 00:30 | 195 | 194
2018-01-23 01:00 | 187 | 187
2018-01-23 01:30 | 180 | 180
2018-01-23 02:00 | 176 | 176
2018-01-23 02:30 | 173 | 173
2018-01-23 03:00 | 172 | 172
2018-01-23 03:30 | 172 | 172
2018-01-23 04:00 | 170 | 170
2018-01-23 04:30 | 173 | 173
2018-01-23 05:00 | 179 | 179
2018-01-23 05:30 | 187 | 187
2018-01-23 06:00 | 197 | 196
2018-01-23 06:30 | 213 | 211
2018-01-23 07:00 | 229 | 228
2018-01-23 07:30 | 245 | 244
2018-01-23 08:00 | 249 | 247
2018-01-23 08:30 | 252 | 251
2018-01-23 09:00 | 256 | 253
2018-01-23 09:30 | 265 | 263
2018-01-23 10:00 | 267 | 265
2018-01-23 10:30 | 272 | 269
2018-01-23 11:00 | 277 | 273
2018-01-23 11:30 | 279 | 275
2018-01-23 12:00 | 281 | 277
2018-01-23 12:30 | 287 | 282
2018-01-23 13:00 | 292 | 289
2018-01-23 13:30 | 298 | 297
2018-01-23 14:00 | 306 | 305
2018-01-23 14:30 | 312 | 311
2018-01-23 15:00 | 316 | 315
2018-01-23 15:30 | 324 | 323
2018-01-23 16:00 | 337 | 336
2018-01-23 16:30 | 349 | 347
2018-01-23 17:00 | 357 | 356
2018-01-23 17:30 | 357 | 356
2018-01-23 18:00 | 349 | 348
2018-01-23 18:30 | 339 | 337
2018-01-23 19:00 | 340 | 338
2018-01-23 19:30 | 341 | 339
2018-01-23 20:00 | 336 | 334
2018-01-23 20:30 | 326 | 325
2018-01-23 21:00 | 309 | 309
2018-01-23 21:30 | 292 | 291
2018-01-23 22:00 | 275 | 275
2018-01-23 22:30 | 262 | 262
2018-01-23 23:00 | 253 | 253
2018-01-23 23:30 | 233 | 232
2018-01-24 | 215 | 214
2018-01-24 00:30 | 201 | 199
2018-01-24 01:00 | 194 | 192
2018-01-24 01:30 | 188 | 186
2018-01-24 02:00 | 184 | 182
2018-01-24 02:30 | 181 | 179
2018-01-24 03:00 | 178 | 177
2018-01-24 03:30 | 178 | 177
2018-01-24 04:00 | 177 | 176
2018-01-24 04:30 | 179 | 178
2018-01-24 05:00 | 186 | 184
2018-01-24 05:30 | 195 | 193
2018-01-24 06:00 | 205 | 203
2018-01-24 06:30 | 223 | 223
2018-01-24 07:00 | 240 | 240
2018-01-24 07:30 | 258 | 258
2018-01-24 08:00 | 266 | 265
2018-01-24 08:30 | 272 | 272
2018-01-24 09:00 | 274 | 274
2018-01-24 09:30 | 283 | 283
2018-01-24 10:00 | 290 | 289
2018-01-24 10:30 | 293 | 293
2018-01-24 11:00 | 293 | 293
2018-01-24 11:30 | 289 | 289
2018-01-24 12:00 | 291 | 291
2018-01-24 12:30 | 299 | 299
2018-01-24 13:00 | 308 | 307
2018-01-24 13:30 | 309 | 309
2018-01-24 14:00 | 314 | 313
2018-01-24 14:30 | 320 | 320
2018-01-24 15:00 | 323 | 323
2018-01-24 15:30 | 330 | 330
2018-01-24 16:00 | 341 | 340
2018-01-24 16:30 | 349 | 349
2018-01-24 17:00 | 356 | 356
2018-01-24 17:30 | 355 | 355
2018-01-24 18:00 | 348 | 348
2018-01-24 18:30 | 339 | 339
2018-01-24 19:00 | 343 | 342
2018-01-24 19:30 | 344 | 343
2018-01-24 20:00 | 342 | 341
2018-01-24 20:30 | 333 | 332
2018-01-24 21:00 | 318 | 317
2018-01-24 21:30 | 303 | 303
2018-01-24 22:00 | 288 | 287
2018-01-24 22:30 | 273 | 273
2018-01-24 23:00 | 263 | 262
2018-01-24 23:30 | 244 | 243
2018-01-25 | 225 | 225
2018-01-25 00:30 | 210 | 209
2018-01-25 01:00 | 204 | 202
2018-01-25 01:30 | 198 | 196
2018-01-25 02:00 | 192 | 190
2018-01-25 02:30 | 190 | 188
2018-01-25 03:00 | 188 | 186
2018-01-25 03:30 | 187 | 185
2018-01-25 04:00 | 184 | 182
2018-01-25 04:30 | 187 | 186
2018-01-25 05:00 | 192 | 190
2018-01-25 05:30 | 201 | 199
2018-01-25 06:00 | 211 | 210
2018-01-25 06:30 | 231 | 231
2018-01-25 07:00 | 250 | 250
2018-01-25 07:30 | 270 | 270
2018-01-25 08:00 | 278 | 278
2018-01-25 08:30 | 282 | 282
2018-01-25 09:00 | 289 | 289
2018-01-25 09:30 | 296 | 295
2018-01-25 10:00 | 303 | 302
2018-01-25 10:30 | 307 | 306
2018-01-25 11:00 | 308 | 307
2018-01-25 11:30 | 314 | 313
2018-01-25 12:00 | 319 | 318
2018-01-25 12:30 | 319 | 317
2018-01-25 13:00 | 317 | 315
2018-01-25 13:30 | 322 | 321
2018-01-25 14:00 | 330 | 330
2018-01-25 14:30 | 336 | 336
2018-01-25 15:00 | 338 | 338
2018-01-25 15:30 | 342 | 342
2018-01-25 16:00 | 352 | 352
2018-01-25 16:30 | 360 | 360
2018-01-25 17:00 | 366 | 366
2018-01-25 17:30 | 362 | 362
2018-01-25 18:00 | 357 | 357
2018-01-25 18:30 | 349 | 349
2018-01-25 19:00 | 350 | 349
2018-01-25 19:30 | 352 | 352
2018-01-25 20:00 | 350 | 349
2018-01-25 20:30 | 341 | 341
2018-01-25 21:00 | 326 | 326
2018-01-25 21:30 | 309 | 309
2018-01-25 22:00 | 290 | 290
2018-01-25 22:30 | 278 | 278
2018-01-25 23:00 | 269 | 269
2018-01-25 23:30 | 249 | 249
2018-01-26 | 228 | 227
2018-01-26 00:30 | 212 | 210
2018-01-26 01:00 | 203 | 201
2018-01-26 01:30 | 196 | 194
2018-01-26 02:00 | 191 | 189
2018-01-26 02:30 | 186 | 185
2018-01-26 03:00 | 182 | 180
2018-01-26 03:30 | 180 | 179
2018-01-26 04:00 | 178 | 177
2018-01-26 04:30 | 177 | 176
2018-01-26 05:00 | 178 | 177
2018-01-26 05:30 | 176 | 175
2018-01-26 06:00 | 180 | 180
2018-01-26 06:30 | 186 | 185
2018-01-26 07:00 | 191 | 190
2018-01-26 07:30 | 202 | 201
2018-01-26 08:00 | 214 | 213
2018-01-26 08:30 | 226 | 225
2018-01-26 09:00 | 233 | 233
2018-01-26 09:30 | 240 | 240
2018-01-26 10:00 | 249 | 249
2018-01-26 10:30 | 259 | 259
2018-01-26 11:00 | 260 | 260
2018-01-26 11:30 | 265 | 265
2018-01-26 12:00 | 271 | 271
2018-01-26 12:30 | 275 | 275
2018-01-26 13:00 | 277 | 277
2018-01-26 13:30 | 274 | 274
2018-01-26 14:00 | 271 | 271
2018-01-26 14:30 | 274 | 274
2018-01-26 15:00 | 280 | 280
2018-01-26 15:30 | 289 | 289
2018-01-26 16:00 | 299 | 299
2018-01-26 16:30 | 311 | 310
2018-01-26 17:00 | 320 | 320
2018-01-26 17:30 | 323 | 323
2018-01-26 18:00 | 321 | 321
2018-01-26 18:30 | 316 | 316
2018-01-26 19:00 | 316 | 316
2018-01-26 19:30 | 320 | 318
2018-01-26 20:00 | 318 | 317
2018-01-26 20:30 | 311 | 310
2018-01-26 21:00 | 299 | 299
2018-01-26 21:30 | 289 | 289
2018-01-26 22:00 | 278 | 278
2018-01-26 22:30 | 269 | 268
2018-01-26 23:00 | 262 | 262
2018-01-26 23:30 | 243 | 243
2018-01-27 | 225 | 225
2018-01-27 00:30 | 209 | 208
2018-01-27 01:00 | 202 | 201
2018-01-27 01:30 | 196 | 196
2018-01-27 02:00 | 192 | 192
2018-01-27 02:30 | 189 | 188
2018-01-27 03:00 | 186 | 186
2018-01-27 03:30 | 184 | 183
2018-01-27 04:00 | 182 | 182
2018-01-27 04:30 | 182 | 182
2018-01-27 05:00 | 183 | 182
2018-01-27 05:30 | 184 | 184
2018-01-27 06:00 | 185 | 185
2018-01-27 06:30 | 190 | 190
2018-01-27 07:00 | 196 | 195
2018-01-27 07:30 | 206 | 204
2018-01-27 08:00 | 213 | 213
2018-01-27 08:30 | 227 | 226
2018-01-27 09:00 | 237 | 235
2018-01-27 09:30 | 241 | 240
2018-01-27 10:00 | 243 | 242
2018-01-27 10:30 | 248 | 247
2018-01-27 11:00 | 251 | 250
2018-01-27 11:30 | 251 | 249
2018-01-27 12:00 | 248 | 246
2018-01-27 12:30 | 251 | 249
2018-01-27 13:00 | 256 | 254
2018-01-27 13:30 | 258 | 256
2018-01-27 14:00 | 266 | 266
2018-01-27 14:30 | 272 | 272
2018-01-27 15:00 | 279 | 279
2018-01-27 15:30 | 285 | 285
2018-01-27 16:00 | 295 | 295
2018-01-27 16:30 | 304 | 304
2018-01-27 17:00 | 312 | 312
2018-01-27 17:30 | 312 | 311
2018-01-27 18:00 | 307 | 307
2018-01-27 18:30 | 304 | 304
2018-01-27 19:00 | 305 | 305
2018-01-27 19:30 | 307 | 306
2018-01-27 20:00 | 305 | 304
2018-01-27 20:30 | 298 | 298
2018-01-27 21:00 | 286 | 286
2018-01-27 21:30 | 276 | 276
2018-01-27 22:00 | 266 | 266
2018-01-27 22:30 | 258 | 258
2018-01-27 23:00 | 251 | 251
2018-01-27 23:30 | 235 | 235
2018-01-28 | 217 | 217
2018-01-28 00:30 | 201 | 201
2018-01-28 01:00 | 194 | 193
2018-01-28 01:30 | 187 | 187
2018-01-28 02:00 | 180 | 179
2018-01-28 02:30 | 176 | 176
2018-01-28 03:00 | 172 | 172
2018-01-28 03:30 | 170 | 170
2018-01-28 04:00 | 168 | 168
2018-01-28 04:30 | 168 | 168
2018-01-28 05:00 | 168 | 168
2018-01-28 05:30 | 168 | 168
2018-01-28 06:00 | 168 | 168
2018-01-28 06:30 | 170 | 170
2018-01-28 07:00 | 174 | 174
2018-01-28 07:30 | 183 | 183
2018-01-28 08:00 | 191 | 190
2018-01-28 08:30 | 200 | 199
2018-01-28 09:00 | 209 | 208
2018-01-28 09:30 | 210 | 209
2018-01-28 10:00 | 214 | 213
2018-01-28 10:30 | 213 | 211
2018-01-28 11:00 | 214 | 213
2018-01-28 11:30 | 209 | 209
2018-01-28 12:00 | 215 | 215
2018-01-28 12:30 | 225 | 225
2018-01-28 13:00 | 228 | 228
2018-01-28 13:30 | 238 | 238
2018-01-28 14:00 | 236 | 236
2018-01-28 14:30 | 234 | 234
2018-01-28 15:00 | 236 | 236
2018-01-28 15:30 | 248 | 248
2018-01-28 16:00 | 255 | 254
2018-01-28 16:30 | 260 | 260
2018-01-28 17:00 | 270 | 270
2018-01-28 17:30 | 273 | 273
2018-01-28 18:00 | 280 | 279
2018-01-28 18:30 | 282 | 282
2018-01-28 19:00 | 287 | 287
2018-01-28 19:30 | 289 | 289
2018-01-28 20:00 | 288 | 288
2018-01-28 20:30 | 281 | 281
2018-01-28 21:00 | 268 | 268
2018-01-28 21:30 | 257 | 257
2018-01-28 22:00 | 245 | 245
2018-01-28 22:30 | 236 | 236
2018-01-28 23:00 | 230 | 229
2018-01-28 23:30 | 214 | 214
2018-01-29 | 195 | 195
2018-01-29 00:30 | 183 | 183
2018-01-29 01:00 | 176 | 176
2018-01-29 01:30 | 171 | 171
2018-01-29 02:00 | 168 | 168
2018-01-29 02:30 | 167 | 167
2018-01-29 03:00 | 165 | 165
2018-01-29 03:30 | 163 | 163
2018-01-29 04:00 | 163 | 163
2018-01-29 04:30 | 166 | 166
2018-01-29 05:00 | 175 | 175
2018-01-29 05:30 | 186 | 185
2018-01-29 06:00 | 197 | 196
2018-01-29 06:30 | 218 | 218
2018-01-29 07:00 | 238 | 237
2018-01-29 07:30 | 256 | 256
2018-01-29 08:00 | 264 | 264
2018-01-29 08:30 | 264 | 264
2018-01-29 09:00 | 267 | 267
2018-01-29 09:30 | 275 | 275
2018-01-29 10:00 | 290 | 290
2018-01-29 10:30 | 310 | 309
2018-01-29 11:00 | 304 | 304
2018-01-29 11:30 | 297 | 297
2018-01-29 12:00 | 280 | 280
2018-01-29 12:30 | 279 | 279
2018-01-29 13:00 | 283 | 283
2018-01-29 13:30 | 294 | 293
2018-01-29 14:00 | 298 | 297
2018-01-29 14:30 | 305 | 305
2018-01-29 15:00 | 308 | 308
2018-01-29 15:30 | 306 | 306
2018-01-29 16:00 | 318 | 318
2018-01-29 16:30 | 328 | 328
2018-01-29 17:00 | 338 | 337
2018-01-29 17:30 | 337 | 336
2018-01-29 18:00 | 332 | 332
2018-01-29 18:30 | 324 | 324
2018-01-29 19:00 | 328 | 328
2018-01-29 19:30 | 325 | 325
2018-01-29 20:00 | 322 | 321
2018-01-29 20:30 | 314 | 314
2018-01-29 21:00 | 299 | 299
2018-01-29 21:30 | 281 | 281
2018-01-29 22:00 | 269 | 269
2018-01-29 22:30 | 258 | 258
2018-01-29 23:00 | 251 | 251
2018-01-29 23:30 | 233 | 233
2018-01-30 | 216 | 216
2018-01-30 00:30 | 200 | 200
2018-01-30 01:00 | 192 | 192
2018-01-30 01:30 | 187 | 187
2018-01-30 02:00 | 184 | 183
2018-01-30 02:30 | 180 | 180
2018-01-30 03:00 | 179 | 179
2018-01-30 03:30 | 179 | 179
2018-01-30 04:00 | 178 | 178
2018-01-30 04:30 | 181 | 181
2018-01-30 05:00 | 188 | 188
2018-01-30 05:30 | 199 | 199
2018-01-30 06:00 | 209 | 209
2018-01-30 06:30 | 228 | 228
2018-01-30 07:00 | 246 | 246
2018-01-30 07:30 | 260 | 260
2018-01-30 08:00 | 268 | 267
2018-01-30 08:30 | 271 | 271
2018-01-30 09:00 | 290 | 290
2018-01-30 09:30 | 306 | 306
2018-01-30 10:00 | 306 | 306
2018-01-30 10:30 | 286 | 286
2018-01-30 11:00 | 284 | 284
2018-01-30 11:30 | 283 | 283
2018-01-30 12:00 | 293 | 292
2018-01-30 12:30 | 296 | 295
2018-01-30 13:00 | 294 | 293
2018-01-30 13:30 | 302 | 301
2018-01-30 14:00 | 312 | 312
2018-01-30 14:30 | 318 | 318
2018-01-30 15:00 | 325 | 325
2018-01-30 15:30 | 336 | 336
2018-01-30 16:00 | 353 | 353
2018-01-30 16:30 | 357 | 356
2018-01-30 17:00 | 356 | 356
2018-01-30 17:30 | 353 | 353
2018-01-30 18:00 | 348 | 348
2018-01-30 18:30 | 344 | 344
2018-01-30 19:00 | 345 | 345
2018-01-30 19:30 | 347 | 347
2018-01-30 20:00 | 344 | 344
2018-01-30 20:30 | 332 | 332
2018-01-30 21:00 | 316 | 315
2018-01-30 21:30 | 300 | 299
2018-01-30 22:00 | 285 | 285
2018-01-30 22:30 | 271 | 271
2018-01-30 23:00 | 259 | 257
2018-01-30 23:30 | 240 | 238
2018-01-31 | 222 | 221
2018-01-31 00:30 | 207 | 206
2018-01-31 01:00 | 200 | 199
2018-01-31 01:30 | 191 | 190
2018-01-31 02:00 | 187 | 186
2018-01-31 02:30 | 183 | 182
2018-01-31 03:00 | 182 | 181
2018-01-31 03:30 | 180 | 180
2018-01-31 04:00 | 176 | 176
2018-01-31 04:30 | 180 | 180
2018-01-31 05:00 | 188 | 187
2018-01-31 05:30 | 194 | 194
2018-01-31 06:00 | 210 | 209
2018-01-31 06:30 | 231 | 231
2018-01-31 07:00 | 247 | 246
2018-01-31 07:30 | 263 | 262
2018-01-31 08:00 | 267 | 266
2018-01-31 08:30 | 271 | 271
2018-01-31 09:00 | 270 | 270
2018-01-31 09:30 | 275 | 275
2018-01-31 10:00 | 279 | 279
2018-01-31 10:30 | 283 | 282
2018-01-31 11:00 | 296 | 296
2018-01-31 11:30 | 306 | 306
2018-01-31 12:00 | 316 | 316
2018-01-31 12:30 | 327 | 327
2018-01-31 13:00 | 335 | 335
2018-01-31 13:30 | 344 | 344
2018-01-31 14:00 | 354 | 354
2018-01-31 14:30 | 360 | 360
2018-01-31 15:00 | 362 | 362
2018-01-31 15:30 | 371 | 371
2018-01-31 16:00 | 385 | 385
2018-01-31 16:30 | 397 | 397
2018-01-31 17:00 | 397 | 397
2018-01-31 17:30 | 385 | 385
2018-01-31 18:00 | 374 | 374
2018-01-31 18:30 | 365 | 365
2018-01-31 19:00 | 366 | 366
2018-01-31 19:30 | 356 | 356
2018-01-31 20:00 | 346 | 346
2018-01-31 20:30 | 332 | 331
2018-01-31 21:00 | 314 | 313
2018-01-31 21:30 | 299 | 299
2018-01-31 22:00 | 284 | 283
2018-01-31 22:30 | 270 | 270
2018-01-31 23:00 | 261 | 261
2018-01-31 23:30 | 242 | 242
2018-02-01 | 222 | 221
2018-02-01 00:30 | 207 | 206
2018-02-01 01:00 | 201 | 200
2018-02-01 01:30 | 194 | 194
2018-02-01 02:00 | 190 | 190
2018-02-01 02:30 | 188 | 187
2018-02-01 03:00 | 186 | 185
2018-02-01 03:30 | 186 | 185
2018-02-01 04:00 | 185 | 184
2018-02-01 04:30 | 187 | 187
2018-02-01 05:00 | 194 | 193
2018-02-01 05:30 | 205 | 204
2018-02-01 06:00 | 215 | 215
2018-02-01 06:30 | 234 | 234
2018-02-01 07:00 | 248 | 248
2018-02-01 07:30 | 263 | 262
2018-02-01 08:00 | 270 | 269
2018-02-01 08:30 | 273 | 273
2018-02-01 09:00 | 272 | 271
2018-02-01 09:30 | 271 | 270
2018-02-01 10:00 | 267 | 266
2018-02-01 10:30 | 258 | 257
2018-02-01 11:00 | 250 | 250
2018-02-01 11:30 | 262 | 262
2018-02-01 12:00 | 270 | 270
2018-02-01 12:30 | 266 | 266
2018-02-01 13:00 | 257 | 257
2018-02-01 13:30 | 257 | 256
2018-02-01 14:00 | 269 | 269
2018-02-01 14:30 | 268 | 268
2018-02-01 15:00 | 270 | 270
2018-02-01 15:30 | 267 | 267
2018-02-01 16:00 | 276 | 276
2018-02-01 16:30 | 278 | 278
2018-02-01 17:00 | 282 | 281
2018-02-01 17:30 | 281 | 281
2018-02-01 18:00 | 280 | 280
2018-02-01 18:30 | 279 | 279
2018-02-01 19:00 | 286 | 286
2018-02-01 19:30 | 283 | 283
2018-02-01 20:00 | 279 | 279
2018-02-01 20:30 | 273 | 272
2018-02-01 21:00 | 262 | 261
2018-02-01 21:30 | 248 | 248
2018-02-01 22:00 | 238 | 237
2018-02-01 22:30 | 229 | 229
2018-02-01 23:00 | 226 | 226
2018-02-01 23:30 | 213 | 213
2018-02-02 | 196 | 196
2018-02-02 00:30 | 181 | 181
2018-02-02 01:00 | 174 | 174
2018-02-02 01:30 | 169 | 169
2018-02-02 02:00 | 166 | 166
2018-02-02 02:30 | 163 | 163
2018-02-02 03:00 | 160 | 160
2018-02-02 03:30 | 160 | 160
2018-02-02 04:00 | 159 | 159
2018-02-02 04:30 | 161 | 161
2018-02-02 05:00 | 166 | 166
2018-02-02 05:30 | 179 | 179
2018-02-02 06:00 | 190 | 189
2018-02-02 06:30 | 211 | 210
2018-02-02 07:00 | 232 | 231
2018-02-02 07:30 | 250 | 250
2018-02-02 08:00 | 253 | 253
2018-02-02 08:30 | 250 | 249
2018-02-02 09:00 | 243 | 243
2018-02-02 09:30 | 252 | 252
2018-02-02 10:00 | 253 | 253
2018-02-02 10:30 | 249 | 248
2018-02-02 11:00 | 251 | 251
2018-02-02 11:30 | 244 | 244
2018-02-02 12:00 | 240 | 240
2018-02-02 12:30 | 246 | 246
2018-02-02 13:00 | 243 | 243
2018-02-02 13:30 | 238 | 238
2018-02-02 14:00 | 236 | 236
2018-02-02 14:30 | 242 | 242
2018-02-02 15:00 | 245 | 245
2018-02-02 15:30 | 244 | 244
2018-02-02 16:00 | 248 | 248
2018-02-02 16:30 | 254 | 254
2018-02-02 17:00 | 256 | 256
2018-02-02 17:30 | 254 | 253
2018-02-02 18:00 | 252 | 252
2018-02-02 18:30 | 249 | 249
2018-02-02 19:00 | 257 | 257
2018-02-02 19:30 | 256 | 256
2018-02-02 20:00 | 254 | 254
2018-02-02 20:30 | 250 | 250
2018-02-02 21:00 | 238 | 237
2018-02-02 21:30 | 228 | 227
2018-02-02 22:00 | 219 | 219
2018-02-02 22:30 | 215 | 214
2018-02-02 23:00 | 213 | 213
2018-02-02 23:30 | 201 | 201
2018-02-03 | 184 | 184
2018-02-03 00:30 | 170 | 170
2018-02-03 01:00 | 162 | 162
2018-02-03 01:30 | 157 | 157
2018-02-03 02:00 | 153 | 153
2018-02-03 02:30 | 150 | 150
2018-02-03 03:00 | 148 | 148
2018-02-03 03:30 | 147 | 147
2018-02-03 04:00 | 147 | 147
2018-02-03 04:30 | 147 | 147
2018-02-03 05:00 | 149 | 148
2018-02-03 05:30 | 153 | 153
2018-02-03 06:00 | 155 | 155
2018-02-03 06:30 | 162 | 162
2018-02-03 07:00 | 170 | 170
2018-02-03 07:30 | 183 | 183
2018-02-03 08:00 | 189 | 189
2018-02-03 08:30 | 200 | 199
2018-02-03 09:00 | 206 | 205
2018-02-03 09:30 | 210 | 209
2018-02-03 10:00 | 211 | 211
2018-02-03 10:30 | 211 | 211
2018-02-03 11:00 | 210 | 209
2018-02-03 11:30 | 206 | 205
2018-02-03 12:00 | 212 | 211
2018-02-03 12:30 | 210 | 210
2018-02-03 13:00 | 210 | 209
2018-02-03 13:30 | 213 | 213
2018-02-03 14:00 | 212 | 211
2018-02-03 14:30 | 210 | 210
2018-02-03 15:00 | 211 | 211
2018-02-03 15:30 | 210 | 210
2018-02-03 16:00 | 208 | 208
2018-02-03 16:30 | 210 | 209
2018-02-03 17:00 | 214 | 214
2018-02-03 17:30 | 214 | 214
2018-02-03 18:00 | 215 | 215
2018-02-03 18:30 | 219 | 219
2018-02-03 19:00 | 226 | 226
2018-02-03 19:30 | 230 | 229
2018-02-03 20:00 | 228 | 228
2018-02-03 20:30 | 224 | 224
2018-02-03 21:00 | 213 | 213
2018-02-03 21:30 | 204 | 204
2018-02-03 22:00 | 200 | 200
2018-02-03 22:30 | 200 | 200
2018-02-03 23:00 | 200 | 200
2018-02-03 23:30 | 190 | 190
2018-02-04 | 175 | 174
2018-02-04 00:30 | 160 | 160
2018-02-04 01:00 | 154 | 154
2018-02-04 01:30 | 149 | 148
2018-02-04 02:00 | 144 | 143
2018-02-04 02:30 | 142 | 141
2018-02-04 03:00 | 140 | 139
2018-02-04 03:30 | 139 | 138
2018-02-04 04:00 | 139 | 138
2018-02-04 04:30 | 139 | 138
2018-02-04 05:00 | 140 | 139
2018-02-04 05:30 | 140 | 139
2018-02-04 06:00 | 142 | 141
2018-02-04 06:30 | 147 | 146
2018-02-04 07:00 | 150 | 149
2018-02-04 07:30 | 153 | 153
2018-02-04 08:00 | 157 | 157
2018-02-04 08:30 | 157 | 157
2018-02-04 09:00 | 159 | 159
2018-02-04 09:30 | 162 | 162
2018-02-04 10:00 | 162 | 162
2018-02-04 10:30 | 159 | 159
2018-02-04 11:00 | 163 | 163
2018-02-04 11:30 | 163 | 163
2018-02-04 12:00 | 160 | 160
2018-02-04 12:30 | 158 | 158
2018-02-04 13:00 | 156 | 155
2018-02-04 13:30 | 157 | 156
2018-02-04 14:00 | 153 | 152
2018-02-04 14:30 | 154 | 154
2018-02-04 15:00 | 158 | 158
2018-02-04 15:30 | 168 | 167
2018-02-04 16:00 | 181 | 180
2018-02-04 16:30 | 194 | 194
2018-02-04 17:00 | 209 | 208
2018-02-04 17:30 | 218 | 217
2018-02-04 18:00 | 225 | 225
2018-02-04 18:30 | 231 | 231
2018-02-04 19:00 | 241 | 240
2018-02-04 19:30 | 247 | 247
2018-02-04 20:00 | 244 | 244
2018-02-04 20:30 | 239 | 239
2018-02-04 21:00 | 228 | 228
2018-02-04 21:30 | 216 | 216
2018-02-04 22:00 | 208 | 208
2018-02-04 22:30 | 205 | 204
2018-02-04 23:00 | 203 | 203
2018-02-04 23:30 | 191 | 191
2018-02-05 | 176 | 176
2018-02-05 00:30 | 163 | 163
2018-02-05 01:00 | 155 | 155
2018-02-05 01:30 | 151 | 150
2018-02-05 02:00 | 147 | 147
2018-02-05 02:30 | 146 | 146
2018-02-05 03:00 | 144 | 144
2018-02-05 03:30 | 145 | 145
2018-02-05 04:00 | 146 | 146
2018-02-05 04:30 | 150 | 149
2018-02-05 05:00 | 157 | 157
2018-02-05 05:30 | 167 | 167
2018-02-05 06:00 | 178 | 178
2018-02-05 06:30 | 198 | 197
2018-02-05 07:00 | 212 | 211
2018-02-05 07:30 | 221 | 220
2018-02-05 08:00 | 220 | 218
2018-02-05 08:30 | 218 | 217
2018-02-05 09:00 | 215 | 214
2018-02-05 09:30 | 218 | 217
2018-02-05 10:00 | 215 | 215
2018-02-05 10:30 | 210 | 210
2018-02-05 11:00 | 208 | 208
2018-02-05 11:30 | 207 | 206
2018-02-05 12:00 | 210 | 209
2018-02-05 12:30 | 212 | 211
2018-02-05 13:00 | 218 | 217
2018-02-05 13:30 | 226 | 225
2018-02-05 14:00 | 233 | 232
2018-02-05 14:30 | 237 | 235
2018-02-05 15:00 | 243 | 241
2018-02-05 15:30 | 252 | 250
2018-02-05 16:00 | 262 | 260
2018-02-05 16:30 | 272 | 270
2018-02-05 17:00 | 276 | 275
2018-02-05 17:30 | 275 | 275
2018-02-05 18:00 | 272 | 272
2018-02-05 18:30 | 271 | 271
2018-02-05 19:00 | 278 | 277
2018-02-05 19:30 | 277 | 276
2018-02-05 20:00 | 274 | 274
2018-02-05 20:30 | 269 | 269
2018-02-05 21:00 | 257 | 255
2018-02-05 21:30 | 245 | 243
2018-02-05 22:00 | 234 | 233
2018-02-05 22:30 | 224 | 223
2018-02-05 23:00 | 219 | 219
2018-02-05 23:30 | 205 | 205
2018-02-06 | 192 | 192
2018-02-06 00:30 | 178 | 178
2018-02-06 01:00 | 169 | 169
2018-02-06 01:30 | 162 | 162
2018-02-06 02:00 | 158 | 158
2018-02-06 02:30 | 157 | 157
2018-02-06 03:00 | 155 | 155
2018-02-06 03:30 | 155 | 155
2018-02-06 04:00 | 155 | 155
2018-02-06 04:30 | 159 | 159
2018-02-06 05:00 | 166 | 166
2018-02-06 05:30 | 176 | 176
2018-02-06 06:00 | 187 | 187
2018-02-06 06:30 | 204 | 204
2018-02-06 07:00 | 219 | 219
2018-02-06 07:30 | 232 | 230
2018-02-06 08:00 | 227 | 226
2018-02-06 08:30 | 226 | 226
2018-02-06 09:00 | 227 | 227
2018-02-06 09:30 | 236 | 236
2018-02-06 10:00 | 230 | 230
2018-02-06 10:30 | 221 | 221
2018-02-06 11:00 | 221 | 220
2018-02-06 11:30 | 223 | 223
2018-02-06 12:00 | 225 | 225
2018-02-06 12:30 | 226 | 225
2018-02-06 13:00 | 227 | 227
2018-02-06 13:30 | 234 | 233
2018-02-06 14:00 | 238 | 237
2018-02-06 14:30 | 242 | 241
2018-02-06 15:00 | 246 | 245
2018-02-06 15:30 | 259 | 259
2018-02-06 16:00 | 270 | 269
2018-02-06 16:30 | 269 | 268
2018-02-06 17:00 | 271 | 271
2018-02-06 17:30 | 276 | 276
2018-02-06 18:00 | 276 | 276
2018-02-06 18:30 | 274 | 274
2018-02-06 19:00 | 283 | 282
2018-02-06 19:30 | 284 | 283
2018-02-06 20:00 | 281 | 280
2018-02-06 20:30 | 274 | 274
2018-02-06 21:00 | 256 | 256
2018-02-06 21:30 | 242 | 242
2018-02-06 22:00 | 231 | 231
2018-02-06 22:30 | 223 | 223
2018-02-06 23:00 | 220 | 220
2018-02-06 23:30 | 208 | 208
2018-02-07 | 191 | 191
2018-02-07 00:30 | 177 | 177
2018-02-07 01:00 | 169 | 169
2018-02-07 01:30 | 165 | 165
2018-02-07 02:00 | 161 | 161
2018-02-07 02:30 | 159 | 159
2018-02-07 03:00 | 159 | 159
2018-02-07 03:30 | 158 | 158
2018-02-07 04:00 | 158 | 158
2018-02-07 04:30 | 163 | 163
2018-02-07 05:00 | 170 | 170
2018-02-07 05:30 | 180 | 180
2018-02-07 06:00 | 191 | 191
2018-02-07 06:30 | 208 | 207
2018-02-07 07:00 | 224 | 224
2018-02-07 07:30 | 237 | 237
2018-02-07 08:00 | 235 | 235
2018-02-07 08:30 | 228 | 228
2018-02-07 09:00 | 226 | 226
2018-02-07 09:30 | 228 | 228
2018-02-07 10:00 | 222 | 222
2018-02-07 10:30 | 222 | 222
2018-02-07 11:00 | 220 | 220
2018-02-07 11:30 | 217 | 217
2018-02-07 12:00 | 217 | 217
2018-02-07 12:30 | 217 | 217
2018-02-07 13:00 | 220 | 220
2018-02-07 13:30 | 219 | 219
2018-02-07 14:00 | 222 | 222
2018-02-07 14:30 | 227 | 227
2018-02-07 15:00 | 231 | 231
2018-02-07 15:30 | 238 | 238
2018-02-07 16:00 | 251 | 251
2018-02-07 16:30 | 266 | 266
2018-02-07 17:00 | 278 | 278
2018-02-07 17:30 | 284 | 284
2018-02-07 18:00 | 280 | 280
2018-02-07 18:30 | 281 | 281
2018-02-07 19:00 | 288 | 288
2018-02-07 19:30 | 290 | 290
2018-02-07 20:00 | 287 | 287
2018-02-07 20:30 | 281 | 281
2018-02-07 21:00 | 266 | 265
2018-02-07 21:30 | 253 | 252
2018-02-07 22:00 | 241 | 240
2018-02-07 22:30 | 231 | 231
2018-02-07 23:00 | 226 | 226
2018-02-07 23:30 | 211 | 210
2018-02-08 | 192 | 192
2018-02-08 00:30 | 176 | 176
2018-02-08 01:00 | 169 | 169
2018-02-08 01:30 | 164 | 164
2018-02-08 02:00 | 160 | 160
2018-02-08 02:30 | 158 | 158
2018-02-08 03:00 | 158 | 157
2018-02-08 03:30 | 158 | 158
2018-02-08 04:00 | 158 | 158
2018-02-08 04:30 | 161 | 161
2018-02-08 05:00 | 171 | 171
2018-02-08 05:30 | 182 | 182
2018-02-08 06:00 | 192 | 192
2018-02-08 06:30 | 211 | 211
2018-02-08 07:00 | 226 | 225
2018-02-08 07:30 | 239 | 238
2018-02-08 08:00 | 239 | 238
2018-02-08 08:30 | 230 | 229
2018-02-08 09:00 | 231 | 229
2018-02-08 09:30 | 241 | 240
2018-02-08 10:00 | 242 | 241
2018-02-08 10:30 | 243 | 242
2018-02-08 11:00 | 238 | 237
2018-02-08 11:30 | 236 | 235
2018-02-08 12:00 | 239 | 238
2018-02-08 12:30 | 230 | 230
2018-02-08 13:00 | 225 | 224
2018-02-08 13:30 | 229 | 228
2018-02-08 14:00 | 229 | 229
2018-02-08 14:30 | 232 | 231
2018-02-08 15:00 | 235 | 234
2018-02-08 15:30 | 243 | 242
2018-02-08 16:00 | 257 | 256
2018-02-08 16:30 | 269 | 268
2018-02-08 17:00 | 276 | 275
2018-02-08 17:30 | 279 | 279
2018-02-08 18:00 | 279 | 279
2018-02-08 18:30 | 279 | 279
2018-02-08 19:00 | 287 | 287
2018-02-08 19:30 | 290 | 289
2018-02-08 20:00 | 287 | 287
2018-02-08 20:30 | 279 | 279
2018-02-08 21:00 | 265 | 265
2018-02-08 21:30 | 252 | 252
2018-02-08 22:00 | 241 | 241
2018-02-08 22:30 | 232 | 232
2018-02-08 23:00 | 227 | 227
2018-02-08 23:30 | 212 | 212
2018-02-09 | 196 | 195
2018-02-09 00:30 | 179 | 179
2018-02-09 01:00 | 172 | 172
2018-02-09 01:30 | 167 | 167
2018-02-09 02:00 | 163 | 163
2018-02-09 02:30 | 161 | 161
2018-02-09 03:00 | 160 | 160
2018-02-09 03:30 | 159 | 159
2018-02-09 04:00 | 159 | 159
2018-02-09 04:30 | 161 | 161
2018-02-09 05:00 | 169 | 169
2018-02-09 05:30 | 179 | 179
2018-02-09 06:00 | 189 | 189
2018-02-09 06:30 | 205 | 205
2018-02-09 07:00 | 216 | 215
2018-02-09 07:30 | 223 | 223
2018-02-09 08:00 | 222 | 221
2018-02-09 08:30 | 219 | 219
2018-02-09 09:00 | 217 | 217
2018-02-09 09:30 | 221 | 221
2018-02-09 10:00 | 225 | 224
2018-02-09 10:30 | 224 | 223
2018-02-09 11:00 | 223 | 222
2018-02-09 11:30 | 221 | 220
2018-02-09 12:00 | 222 | 221
2018-02-09 12:30 | 225 | 224
2018-02-09 13:00 | 230 | 229
2018-02-09 13:30 | 235 | 233
2018-02-09 14:00 | 243 | 241
2018-02-09 14:30 | 251 | 249
2018-02-09 15:00 | 258 | 255
2018-02-09 15:30 | 268 | 265
2018-02-09 16:00 | 284 | 283
2018-02-09 16:30 | 296 | 296
2018-02-09 17:00 | 307 | 307
2018-02-09 17:30 | 308 | 308
2018-02-09 18:00 | 301 | 301
2018-02-09 18:30 | 293 | 293
2018-02-09 19:00 | 297 | 296
2018-02-09 19:30 | 298 | 298
2018-02-09 20:00 | 295 | 294
2018-02-09 20:30 | 287 | 287
2018-02-09 21:00 | 274 | 274
2018-02-09 21:30 | 259 | 259
2018-02-09 22:00 | 247 | 247
2018-02-09 22:30 | 239 | 238
2018-02-09 23:00 | 233 | 233
2018-02-09 23:30 | 216 | 216
2018-02-10 | 198 | 198
2018-02-10 00:30 | 180 | 180
2018-02-10 01:00 | 174 | 174
2018-02-10 01:30 | 168 | 168
2018-02-10 02:00 | 163 | 163
2018-02-10 02:30 | 160 | 160
2018-02-10 03:00 | 158 | 158
2018-02-10 03:30 | 157 | 157
2018-02-10 04:00 | 155 | 155
2018-02-10 04:30 | 156 | 156
2018-02-10 05:00 | 159 | 159
2018-02-10 05:30 | 162 | 162
2018-02-10 06:00 | 161 | 161
2018-02-10 06:30 | 167 | 167
2018-02-10 07:00 | 173 | 173
2018-02-10 07:30 | 183 | 183
2018-02-10 08:00 | 181 | 180
2018-02-10 08:30 | 185 | 184
2018-02-10 09:00 | 187 | 186
2018-02-10 09:30 | 188 | 187
2018-02-10 10:00 | 186 | 185
2018-02-10 10:30 | 187 | 186
2018-02-10 11:00 | 191 | 190
2018-02-10 11:30 | 194 | 193
2018-02-10 12:00 | 200 | 199
2018-02-10 12:30 | 207 | 206
2018-02-10 13:00 | 217 | 216
2018-02-10 13:30 | 228 | 226
2018-02-10 14:00 | 241 | 241
2018-02-10 14:30 | 253 | 253
2018-02-10 15:00 | 265 | 265
2018-02-10 15:30 | 278 | 278
2018-02-10 16:00 | 293 | 293
2018-02-10 16:30 | 303 | 303
2018-02-10 17:00 | 311 | 311
2018-02-10 17:30 | 313 | 313
2018-02-10 18:00 | 306 | 306
2018-02-10 18:30 | 299 | 299
2018-02-10 19:00 | 300 | 299
2018-02-10 19:30 | 294 | 294
2018-02-10 20:00 | 289 | 289
2018-02-10 20:30 | 281 | 281
2018-02-10 21:00 | 267 | 266
2018-02-10 21:30 | 257 | 257
2018-02-10 22:00 | 247 | 247
2018-02-10 22:30 | 242 | 242
2018-02-10 23:00 | 238 | 238
2018-02-10 23:30 | 222 | 222
2018-02-11 | 203 | 203
2018-02-11 00:30 | 186 | 186
2018-02-11 01:00 | 179 | 178
2018-02-11 01:30 | 173 | 173
2018-02-11 02:00 | 168 | 168
2018-02-11 02:30 | 164 | 164
2018-02-11 03:00 | 161 | 161
2018-02-11 03:30 | 159 | 159
2018-02-11 04:00 | 158 | 158
2018-02-11 04:30 | 158 | 158
2018-02-11 05:00 | 157 | 157
2018-02-11 05:30 | 157 | 157
2018-02-11 06:00 | 157 | 156
2018-02-11 06:30 | 159 | 159
2018-02-11 07:00 | 162 | 162
2018-02-11 07:30 | 169 | 169
2018-02-11 08:00 | 175 | 175
2018-02-11 08:30 | 183 | 182
2018-02-11 09:00 | 189 | 188
2018-02-11 09:30 | 196 | 196
2018-02-11 10:00 | 204 | 204
2018-02-11 10:30 | 216 | 216
2018-02-11 11:00 | 227 | 227
2018-02-11 11:30 | 239 | 239
2018-02-11 12:00 | 251 | 250
2018-02-11 12:30 | 263 | 263
2018-02-11 13:00 | 277 | 276
2018-02-11 13:30 | 290 | 290
2018-02-11 14:00 | 304 | 303
2018-02-11 14:30 | 319 | 317
2018-02-11 15:00 | 330 | 329
2018-02-11 15:30 | 343 | 343
2018-02-11 16:00 | 359 | 359
2018-02-11 16:30 | 377 | 377
2018-02-11 17:00 | 383 | 383
2018-02-11 17:30 | 380 | 380
2018-02-11 18:00 | 373 | 373
2018-02-11 18:30 | 295 | 293
2018-02-11 19:00 | 255 | 254
2018-02-11 19:30 | 242 | 242
2018-02-11 20:00 | 236 | 236
2018-02-11 20:30 | 229 | 228
2018-02-11 21:00 | 215 | 214
2018-02-11 21:30 | 202 | 202
2018-02-11 22:00 | 192 | 192
2018-02-11 22:30 | 186 | 185
2018-02-11 23:00 | 180 | 179
2018-02-11 23:30 | 168 | 168
2018-02-12 | 159 | 159
2018-02-12 00:30 | 155 | 154
2018-02-12 01:00 | 149 | 148
2018-02-12 01:30 | 146 | 146
2018-02-12 02:00 | 142 | 142
2018-02-12 02:30 | 143 | 143
2018-02-12 03:00 | 143 | 143
2018-02-12 03:30 | 144 | 144
2018-02-12 04:00 | 143 | 143
2018-02-12 04:30 | 148 | 148
2018-02-12 05:00 | 155 | 155
2018-02-12 05:30 | 165 | 165
2018-02-12 06:00 | 178 | 177
2018-02-12 06:30 | 202 | 202
2018-02-12 07:00 | 218 | 218
2018-02-12 07:30 | 235 | 235
2018-02-12 08:00 | 245 | 245
2018-02-12 08:30 | 250 | 250
2018-02-12 09:00 | 257 | 257
2018-02-12 09:30 | 265 | 265
2018-02-12 10:00 | 272 | 272
2018-02-12 10:30 | 279 | 279
2018-02-12 11:00 | 286 | 286
2018-02-12 11:30 | 296 | 296
2018-02-12 12:00 | 305 | 304
2018-02-12 12:30 | 314 | 313
2018-02-12 13:00 | 324 | 323
2018-02-12 13:30 | 334 | 333
2018-02-12 14:00 | 346 | 345
2018-02-12 14:30 | 356 | 355
2018-02-12 15:00 | 361 | 360
2018-02-12 15:30 | 374 | 373
2018-02-12 16:00 | 394 | 392
2018-02-12 16:30 | 410 | 410
2018-02-12 17:00 | 422 | 421
2018-02-12 17:30 | 423 | 423
2018-02-12 18:00 | 415 | 415
2018-02-12 18:30 | 407 | 407
2018-02-12 19:00 | 413 | 412
2018-02-12 19:30 | 411 | 411
2018-02-12 20:00 | 405 | 404
2018-02-12 20:30 | 390 | 389
2018-02-12 21:00 | 370 | 369
2018-02-12 21:30 | 347 | 347
2018-02-12 22:00 | 328 | 328
2018-02-12 22:30 | 313 | 313
2018-02-12 23:00 | 301 | 300
2018-02-12 23:30 | 281 | 281
2018-02-13 | 261 | 261
2018-02-13 00:30 | 243 | 243
2018-02-13 01:00 | 235 | 235
2018-02-13 01:30 | 229 | 229
2018-02-13 02:00 | 225 | 225
2018-02-13 02:30 | 222 | 222
2018-02-13 03:00 | 220 | 220
2018-02-13 03:30 | 219 | 219
2018-02-13 04:00 | 219 | 219
2018-02-13 04:30 | 222 | 222
2018-02-13 05:00 | 228 | 228
2018-02-13 05:30 | 240 | 240
2018-02-13 06:00 | 252 | 252
2018-02-13 06:30 | 275 | 274
2018-02-13 07:00 | 295 | 294
2018-02-13 07:30 | 318 | 317
2018-02-13 08:00 | 327 | 326
2018-02-13 08:30 | 344 | 343
2018-02-13 09:00 | 346 | 345
2018-02-13 09:30 | 334 | 334
2018-02-13 10:00 | 326 | 326
2018-02-13 10:30 | 332 | 331
2018-02-13 11:00 | 340 | 340
2018-02-13 11:30 | 346 | 345
2018-02-13 12:00 | 349 | 348
2018-02-13 12:30 | 354 | 353
2018-02-13 13:00 | 364 | 363
2018-02-13 13:30 | 371 | 371
2018-02-13 14:00 | 377 | 376
2018-02-13 14:30 | 383 | 382
2018-02-13 15:00 | 391 | 390
2018-02-13 15:30 | 405 | 403
2018-02-13 16:00 | 422 | 422
2018-02-13 16:30 | 441 | 441
2018-02-13 17:00 | 437 | 437
2018-02-13 17:30 | 424 | 424
2018-02-13 18:00 | 415 | 415
2018-02-13 18:30 | 406 | 406
2018-02-13 19:00 | 412 | 412
2018-02-13 19:30 | 393 | 393
2018-02-13 20:00 | 373 | 372
2018-02-13 20:30 | 345 | 345
2018-02-13 21:00 | 319 | 319
2018-02-13 21:30 | 301 | 300
2018-02-13 22:00 | 286 | 285
2018-02-13 22:30 | 268 | 268
2018-02-13 23:00 | 258 | 258
2018-02-13 23:30 | 237 | 236
2018-02-14 | 218 | 216
2018-02-14 00:30 | 203 | 202
2018-02-14 01:00 | 195 | 195
2018-02-14 01:30 | 189 | 189
2018-02-14 02:00 | 186 | 185
2018-02-14 02:30 | 183 | 182
2018-02-14 03:00 | 180 | 180
2018-02-14 03:30 | 180 | 179
2018-02-14 04:00 | 179 | 179
2018-02-14 04:30 | 181 | 181
2018-02-14 05:00 | 188 | 187
2018-02-14 05:30 | 198 | 197
2018-02-14 06:00 | 209 | 208
2018-02-14 06:30 | 229 | 228
2018-02-14 07:00 | 249 | 248
2018-02-14 07:30 | 265 | 264
2018-02-14 08:00 | 273 | 272
2018-02-14 08:30 | 277 | 277
2018-02-14 09:00 | 281 | 281
2018-02-14 09:30 | 289 | 288
2018-02-14 10:00 | 295 | 293
2018-02-14 10:30 | 304 | 303
2018-02-14 11:00 | 313 | 312
2018-02-14 11:30 | 320 | 320
2018-02-14 12:00 | 332 | 331
2018-02-14 12:30 | 343 | 342
2018-02-14 13:00 | 357 | 357
2018-02-14 13:30 | 371 | 370
2018-02-14 14:00 | 382 | 382
2018-02-14 14:30 | 389 | 389
2018-02-14 15:00 | 389 | 389
2018-02-14 15:30 | 402 | 402
2018-02-14 16:00 | 422 | 422
2018-02-14 16:30 | 438 | 438
2018-02-14 17:00 | 445 | 445
2018-02-14 17:30 | 443 | 443
2018-02-14 18:00 | 433 | 433
2018-02-14 18:30 | 420 | 420
2018-02-14 19:00 | 420 | 419
2018-02-14 19:30 | 413 | 413
2018-02-14 20:00 | 399 | 399
2018-02-14 20:30 | 396 | 395
2018-02-14 21:00 | 398 | 397
2018-02-14 21:30 | 374 | 373
2018-02-14 22:00 | 348 | 348
2018-02-14 22:30 | 314 | 314
2018-02-14 23:00 | 299 | 299
2018-02-14 23:30 | 283 | 282
2018-02-15 | 267 | 267
2018-02-15 00:30 | 249 | 249
2018-02-15 01:00 | 234 | 234
2018-02-15 01:30 | 227 | 225
2018-02-15 02:00 | 238 | 236
2018-02-15 02:30 | 230 | 230
2018-02-15 03:00 | 222 | 222
2018-02-15 03:30 | 215 | 215
2018-02-15 04:00 | 212 | 212
2018-02-15 04:30 | 213 | 213
2018-02-15 05:00 | 217 | 217
2018-02-15 05:30 | 227 | 227
2018-02-15 06:00 | 242 | 242
2018-02-15 06:30 | 262 | 261
2018-02-15 07:00 | 282 | 282
2018-02-15 07:30 | 303 | 303
2018-02-15 08:00 | 315 | 315
2018-02-15 08:30 | 322 | 321
2018-02-15 09:00 | 330 | 329
2018-02-15 09:30 | 341 | 340
2018-02-15 10:00 | 351 | 351
2018-02-15 10:30 | 354 | 353
2018-02-15 11:00 | 360 | 359
2018-02-15 11:30 | 356 | 356
2018-02-15 12:00 | 363 | 363
2018-02-15 12:30 | 371 | 371
2018-02-15 13:00 | 382 | 381
2018-02-15 13:30 | 391 | 391
2018-02-15 14:00 | 399 | 399
2018-02-15 14:30 | 407 | 407
2018-02-15 15:00 | 408 | 408
2018-02-15 15:30 | 424 | 424
2018-02-15 16:00 | 439 | 439
2018-02-15 16:30 | 430 | 430
2018-02-15 17:00 | 421 | 421
2018-02-15 17:30 | 413 | 413
2018-02-15 18:00 | 410 | 410
2018-02-15 18:30 | 398 | 397
2018-02-15 19:00 | 400 | 400
2018-02-15 19:30 | 397 | 396
2018-02-15 20:00 | 393 | 393
2018-02-15 20:30 | 398 | 398
2018-02-15 21:00 | 389 | 388
2018-02-15 21:30 | 357 | 356
2018-02-15 22:00 | 338 | 337
2018-02-15 22:30 | 308 | 307
2018-02-15 23:00 | 294 | 294
2018-02-15 23:30 | 278 | 277
2018-02-16 | 262 | 261
2018-02-16 00:30 | 244 | 244
2018-02-16 01:00 | 230 | 229
2018-02-16 01:30 | 222 | 222
2018-02-16 02:00 | 231 | 230
2018-02-16 02:30 | 225 | 225
2018-02-16 03:00 | 214 | 214
2018-02-16 03:30 | 210 | 210
2018-02-16 04:00 | 209 | 209
2018-02-16 04:30 | 210 | 210
2018-02-16 05:00 | 217 | 217
2018-02-16 05:30 | 230 | 230
2018-02-16 06:00 | 239 | 239
2018-02-16 06:30 | 262 | 262
2018-02-16 07:00 | 286 | 285
2018-02-16 07:30 | 307 | 306
2018-02-16 08:00 | 319 | 319
2018-02-16 08:30 | 326 | 326
2018-02-16 09:00 | 331 | 331
2018-02-16 09:30 | 334 | 334
2018-02-16 10:00 | 335 | 334
2018-02-16 10:30 | 335 | 335
2018-02-16 11:00 | 345 | 344
2018-02-16 11:30 | 357 | 357
2018-02-16 12:00 | 363 | 362
2018-02-16 12:30 | 363 | 363
2018-02-16 13:00 | 370 | 370
2018-02-16 13:30 | 378 | 378
2018-02-16 14:00 | 380 | 380
2018-02-16 14:30 | 387 | 386
2018-02-16 15:00 | 412 | 411
2018-02-16 15:30 | 415 | 415
2018-02-16 16:00 | 419 | 418
2018-02-16 16:30 | 413 | 412
2018-02-16 17:00 | 416 | 416
2018-02-16 17:30 | 391 | 391
2018-02-16 18:00 | 369 | 368
2018-02-16 18:30 | 348 | 348
2018-02-16 19:00 | 346 | 346
2018-02-16 19:30 | 343 | 342
2018-02-16 20:00 | 341 | 339
2018-02-16 20:30 | 329 | 328
2018-02-16 21:00 | 313 | 312
2018-02-16 21:30 | 296 | 296
2018-02-16 22:00 | 284 | 284
2018-02-16 22:30 | 276 | 276
2018-02-16 23:00 | 270 | 270
2018-02-16 23:30 | 252 | 252
2018-02-17 | 232 | 232
2018-02-17 00:30 | 216 | 216
2018-02-17 01:00 | 208 | 208
2018-02-17 01:30 | 203 | 203
2018-02-17 02:00 | 197 | 197
2018-02-17 02:30 | 194 | 194
2018-02-17 03:00 | 192 | 191
2018-02-17 03:30 | 190 | 190
2018-02-17 04:00 | 190 | 189
2018-02-17 04:30 | 189 | 188
2018-02-17 05:00 | 189 | 189
2018-02-17 05:30 | 192 | 192
2018-02-17 06:00 | 192 | 192
2018-02-17 06:30 | 200 | 200
2018-02-17 07:00 | 207 | 206
2018-02-17 07:30 | 220 | 220
2018-02-17 08:00 | 232 | 232
2018-02-17 08:30 | 243 | 243
2018-02-17 09:00 | 251 | 251
2018-02-17 09:30 | 252 | 252
2018-02-17 10:00 | 251 | 251
2018-02-17 10:30 | 253 | 253
2018-02-17 11:00 | 259 | 259
2018-02-17 11:30 | 261 | 261
2018-02-17 12:00 | 262 | 262
2018-02-17 12:30 | 262 | 262
2018-02-17 13:00 | 267 | 267
2018-02-17 13:30 | 272 | 272
2018-02-17 14:00 | 274 | 274
2018-02-17 14:30 | 281 | 281
2018-02-17 15:00 | 283 | 283
2018-02-17 15:30 | 294 | 294
2018-02-17 16:00 | 304 | 304
2018-02-17 16:30 | 307 | 307
2018-02-17 17:00 | 314 | 314
2018-02-17 17:30 | 311 | 311
2018-02-17 18:00 | 308 | 308
2018-02-17 18:30 | 304 | 304
2018-02-17 19:00 | 309 | 309
2018-02-17 19:30 | 307 | 307
2018-02-17 20:00 | 305 | 305
2018-02-17 20:30 | 296 | 296
2018-02-17 21:00 | 284 | 284
2018-02-17 21:30 | 271 | 271
2018-02-17 22:00 | 262 | 262
2018-02-17 22:30 | 256 | 256
2018-02-17 23:00 | 252 | 252
2018-02-17 23:30 | 238 | 238
2018-02-18 | 220 | 220
2018-02-18 00:30 | 205 | 204
2018-02-18 01:00 | 195 | 194
2018-02-18 01:30 | 188 | 188
2018-02-18 02:00 | 183 | 182
2018-02-18 02:30 | 178 | 178
2018-02-18 03:00 | 174 | 174
2018-02-18 03:30 | 172 | 172
2018-02-18 04:00 | 170 | 170
2018-02-18 04:30 | 169 | 168
2018-02-18 05:00 | 169 | 168
2018-02-18 05:30 | 168 | 168
2018-02-18 06:00 | 166 | 165
2018-02-18 06:30 | 168 | 168
2018-02-18 07:00 | 175 | 175
2018-02-18 07:30 | 180 | 180
2018-02-18 08:00 | 184 | 184
2018-02-18 08:30 | 193 | 192
2018-02-18 09:00 | 201 | 200
2018-02-18 09:30 | 211 | 210
2018-02-18 10:00 | 214 | 214
2018-02-18 10:30 | 218 | 217
2018-02-18 11:00 | 222 | 222
2018-02-18 11:30 | 228 | 228
2018-02-18 12:00 | 233 | 233
2018-02-18 12:30 | 238 | 238
2018-02-18 13:00 | 245 | 245
2018-02-18 13:30 | 251 | 250
2018-02-18 14:00 | 260 | 260
2018-02-18 14:30 | 268 | 268
2018-02-18 15:00 | 277 | 277
2018-02-18 15:30 | 290 | 289
2018-02-18 16:00 | 301 | 301
2018-02-18 16:30 | 308 | 308
2018-02-18 17:00 | 317 | 316
2018-02-18 17:30 | 317 | 317
2018-02-18 18:00 | 315 | 315
2018-02-18 18:30 | 311 | 310
2018-02-18 19:00 | 317 | 316
2018-02-18 19:30 | 312 | 311
2018-02-18 20:00 | 305 | 304
2018-02-18 20:30 | 293 | 292
2018-02-18 21:00 | 277 | 277
2018-02-18 21:30 | 263 | 263
2018-02-18 22:00 | 250 | 250
2018-02-18 22:30 | 242 | 242
2018-02-18 23:00 | 235 | 235
2018-02-18 23:30 | 222 | 222
2018-02-19 | 203 | 203
2018-02-19 00:30 | 187 | 187
2018-02-19 01:00 | 178 | 178
2018-02-19 01:30 | 174 | 174
2018-02-19 02:00 | 170 | 170
2018-02-19 02:30 | 166 | 166
2018-02-19 03:00 | 165 | 165
2018-02-19 03:30 | 164 | 164
2018-02-19 04:00 | 165 | 165
2018-02-19 04:30 | 167 | 167
2018-02-19 05:00 | 173 | 173
2018-02-19 05:30 | 185 | 185
2018-02-19 06:00 | 197 | 197
2018-02-19 06:30 | 219 | 219
2018-02-19 07:00 | 236 | 235
2018-02-19 07:30 | 250 | 248
2018-02-19 08:00 | 254 | 254
2018-02-19 08:30 | 255 | 255
2018-02-19 09:00 | 255 | 255
2018-02-19 09:30 | 256 | 256
2018-02-19 10:00 | 258 | 258
2018-02-19 10:30 | 258 | 258
2018-02-19 11:00 | 263 | 263
2018-02-19 11:30 | 267 | 266
2018-02-19 12:00 | 271 | 271
2018-02-19 12:30 | 277 | 276
2018-02-19 13:00 | 284 | 284
2018-02-19 13:30 | 294 | 293
2018-02-19 14:00 | 304 | 303
2018-02-19 14:30 | 314 | 313
2018-02-19 15:00 | 320 | 319
2018-02-19 15:30 | 333 | 332
2018-02-19 16:00 | 349 | 348
2018-02-19 16:30 | 360 | 360
2018-02-19 17:00 | 372 | 372
2018-02-19 17:30 | 369 | 369
2018-02-19 18:00 | 356 | 356
2018-02-19 18:30 | 350 | 349
2018-02-19 19:00 | 355 | 353
2018-02-19 19:30 | 349 | 348
2018-02-19 20:00 | 342 | 342
2018-02-19 20:30 | 332 | 331
2018-02-19 21:00 | 315 | 314
2018-02-19 21:30 | 300 | 300
2018-02-19 22:00 | 283 | 283
2018-02-19 22:30 | 269 | 268
2018-02-19 23:00 | 260 | 259
2018-02-19 23:30 | 240 | 240
2018-02-20 | 222 | 222
2018-02-20 00:30 | 206 | 206
2018-02-20 01:00 | 199 | 198
2018-02-20 01:30 | 193 | 193
2018-02-20 02:00 | 188 | 188
2018-02-20 02:30 | 185 | 185
2018-02-20 03:00 | 183 | 182
2018-02-20 03:30 | 183 | 182
2018-02-20 04:00 | 183 | 182
2018-02-20 04:30 | 185 | 185
2018-02-20 05:00 | 193 | 192
2018-02-20 05:30 | 205 | 204
2018-02-20 06:00 | 211 | 211
2018-02-20 06:30 | 232 | 232
2018-02-20 07:00 | 248 | 247
2018-02-20 07:30 | 268 | 267
2018-02-20 08:00 | 276 | 276
2018-02-20 08:30 | 275 | 275
2018-02-20 09:00 | 274 | 274
2018-02-20 09:30 | 271 | 270
2018-02-20 10:00 | 273 | 272
2018-02-20 10:30 | 280 | 280
2018-02-20 11:00 | 275 | 275
2018-02-20 11:30 | 278 | 278
2018-02-20 12:00 | 278 | 278
2018-02-20 12:30 | 271 | 271
2018-02-20 13:00 | 273 | 273
2018-02-20 13:30 | 274 | 274
2018-02-20 14:00 | 282 | 282
2018-02-20 14:30 | 282 | 282
2018-02-20 15:00 | 283 | 283
2018-02-20 15:30 | 288 | 288
2018-02-20 16:00 | 300 | 300
2018-02-20 16:30 | 308 | 308
2018-02-20 17:00 | 316 | 316
2018-02-20 17:30 | 319 | 319
2018-02-20 18:00 | 312 | 312
2018-02-20 18:30 | 309 | 308
2018-02-20 19:00 | 316 | 316
2018-02-20 19:30 | 313 | 313
2018-02-20 20:00 | 308 | 308
2018-02-20 20:30 | 300 | 300
2018-02-20 21:00 | 284 | 284
2018-02-20 21:30 | 272 | 272
2018-02-20 22:00 | 260 | 260
2018-02-20 22:30 | 250 | 250
2018-02-20 23:00 | 240 | 240
2018-02-20 23:30 | 225 | 224
2018-02-21 | 208 | 208
2018-02-21 00:30 | 195 | 194
2018-02-21 01:00 | 189 | 189
2018-02-21 01:30 | 183 | 183
2018-02-21 02:00 | 180 | 180
2018-02-21 02:30 | 178 | 178
2018-02-21 03:00 | 178 | 178
2018-02-21 03:30 | 179 | 179
2018-02-21 04:00 | 179 | 179
2018-02-21 04:30 | 182 | 182
2018-02-21 05:00 | 188 | 188
2018-02-21 05:30 | 201 | 200
2018-02-21 06:00 | 211 | 210
2018-02-21 06:30 | 231 | 231
2018-02-21 07:00 | 250 | 250
2018-02-21 07:30 | 264 | 263
2018-02-21 08:00 | 268 | 267
2018-02-21 08:30 | 267 | 266
2018-02-21 09:00 | 271 | 270
2018-02-21 09:30 | 277 | 277
2018-02-21 10:00 | 280 | 280
2018-02-21 10:30 | 271 | 270
2018-02-21 11:00 | 259 | 259
2018-02-21 11:30 | 258 | 258
2018-02-21 12:00 | 259 | 259
2018-02-21 12:30 | 268 | 268
2018-02-21 13:00 | 264 | 263
2018-02-21 13:30 | 254 | 254
2018-02-21 14:00 | 255 | 255
2018-02-21 14:30 | 262 | 262
2018-02-21 15:00 | 262 | 262
2018-02-21 15:30 | 264 | 264
2018-02-21 16:00 | 268 | 268
2018-02-21 16:30 | 278 | 278
2018-02-21 17:00 | 284 | 284
2018-02-21 17:30 | 283 | 283
2018-02-21 18:00 | 279 | 279
2018-02-21 18:30 | 276 | 276
2018-02-21 19:00 | 286 | 286
2018-02-21 19:30 | 284 | 284
2018-02-21 20:00 | 280 | 280
2018-02-21 20:30 | 272 | 272
2018-02-21 21:00 | 260 | 260
2018-02-21 21:30 | 250 | 250
2018-02-21 22:00 | 239 | 239
2018-02-21 22:30 | 229 | 227
2018-02-21 23:00 | 225 | 223
2018-02-21 23:30 | 210 | 209
2018-02-22 | 193 | 192
2018-02-22 00:30 | 180 | 179
2018-02-22 01:00 | 173 | 172
2018-02-22 01:30 | 168 | 167
2018-02-22 02:00 | 164 | 163
2018-02-22 02:30 | 163 | 163
2018-02-22 03:00 | 162 | 162
2018-02-22 03:30 | 162 | 162
2018-02-22 04:00 | 163 | 163
2018-02-22 04:30 | 166 | 166
2018-02-22 05:00 | 173 | 173
2018-02-22 05:30 | 186 | 186
2018-02-22 06:00 | 199 | 198
2018-02-22 06:30 | 218 | 217
2018-02-22 07:00 | 236 | 236
2018-02-22 07:30 | 257 | 257
2018-02-22 08:00 | 259 | 259
2018-02-22 08:30 | 253 | 253
2018-02-22 09:00 | 253 | 253
2018-02-22 09:30 | 258 | 257
2018-02-22 10:00 | 253 | 252
2018-02-22 10:30 | 256 | 255
2018-02-22 11:00 | 266 | 266
2018-02-22 11:30 | 262 | 262
2018-02-22 12:00 | 260 | 260
2018-02-22 12:30 | 257 | 257
2018-02-22 13:00 | 257 | 257
2018-02-22 13:30 | 256 | 256
2018-02-22 14:00 | 259 | 259
2018-02-22 14:30 | 261 | 261
2018-02-22 15:00 | 258 | 258
2018-02-22 15:30 | 263 | 263
2018-02-22 16:00 | 272 | 272
2018-02-22 16:30 | 275 | 275
2018-02-22 17:00 | 277 | 277
2018-02-22 17:30 | 278 | 278
2018-02-22 18:00 | 279 | 279
2018-02-22 18:30 | 280 | 280
2018-02-22 19:00 | 290 | 290
2018-02-22 19:30 | 286 | 286
2018-02-22 20:00 | 284 | 284
2018-02-22 20:30 | 280 | 280
2018-02-22 21:00 | 267 | 267
2018-02-22 21:30 | 252 | 252
2018-02-22 22:00 | 240 | 239
2018-02-22 22:30 | 234 | 233
2018-02-22 23:00 | 230 | 230
2018-02-22 23:30 | 215 | 215
2018-02-23 | 198 | 198
2018-02-23 00:30 | 184 | 184
2018-02-23 01:00 | 178 | 178
2018-02-23 01:30 | 172 | 172
2018-02-23 02:00 | 169 | 169
2018-02-23 02:30 | 168 | 168
2018-02-23 03:00 | 168 | 167
2018-02-23 03:30 | 168 | 167
2018-02-23 04:00 | 169 | 169
2018-02-23 04:30 | 173 | 173
2018-02-23 05:00 | 180 | 180
2018-02-23 05:30 | 193 | 193
2018-02-23 06:00 | 207 | 206
2018-02-23 06:30 | 228 | 227
2018-02-23 07:00 | 249 | 249
2018-02-23 07:30 | 272 | 272
2018-02-23 08:00 | 282 | 282
2018-02-23 08:30 | 285 | 285
2018-02-23 09:00 | 291 | 291
2018-02-23 09:30 | 293 | 293
2018-02-23 10:00 | 294 | 294
2018-02-23 10:30 | 293 | 293
2018-02-23 11:00 | 286 | 286
2018-02-23 11:30 | 285 | 285
2018-02-23 12:00 | 286 | 286
2018-02-23 12:30 | 286 | 286
2018-02-23 13:00 | 289 | 289
2018-02-23 13:30 | 287 | 287
2018-02-23 14:00 | 287 | 287
2018-02-23 14:30 | 285 | 285
2018-02-23 15:00 | 280 | 280
2018-02-23 15:30 | 279 | 279
2018-02-23 16:00 | 281 | 281
2018-02-23 16:30 | 284 | 284
2018-02-23 17:00 | 288 | 288
2018-02-23 17:30 | 289 | 288
2018-02-23 18:00 | 282 | 282
2018-02-23 18:30 | 280 | 280
2018-02-23 19:00 | 289 | 289
2018-02-23 19:30 | 283 | 283
2018-02-23 20:00 | 277 | 277
2018-02-23 20:30 | 272 | 270
2018-02-23 21:00 | 260 | 258
2018-02-23 21:30 | 250 | 249
2018-02-23 22:00 | 243 | 243
2018-02-23 22:30 | 237 | 237
2018-02-23 23:00 | 236 | 235
2018-02-23 23:30 | 223 | 222
2018-02-24 | 206 | 205
2018-02-24 00:30 | 192 | 191
2018-02-24 01:00 | 183 | 183
2018-02-24 01:30 | 178 | 178
2018-02-24 02:00 | 174 | 174
2018-02-24 02:30 | 169 | 169
2018-02-24 03:00 | 167 | 167
2018-02-24 03:30 | 167 | 167
2018-02-24 04:00 | 166 | 166
2018-02-24 04:30 | 166 | 166
2018-02-24 05:00 | 170 | 170
2018-02-24 05:30 | 174 | 174
2018-02-24 06:00 | 178 | 178
2018-02-24 06:30 | 185 | 185
2018-02-24 07:00 | 193 | 193
2018-02-24 07:30 | 200 | 200
2018-02-24 08:00 | 214 | 213
2018-02-24 08:30 | 221 | 220
2018-02-24 09:00 | 225 | 224
2018-02-24 09:30 | 174 | 173
2018-02-24 10:00 | 169 | 167
2018-02-24 10:30 | 175 | 173
2018-02-24 11:00 | 175 | 173
2018-02-24 11:30 | 174 | 172
2018-02-24 12:00 | 173 | 172
2018-02-24 12:30 | 163 | 162
2018-02-24 13:00 | 156 | 155
2018-02-24 13:30 | 163 | 162
2018-02-24 14:00 | 169 | 168
2018-02-24 14:30 | 167 | 166
2018-02-24 15:00 | 186 | 185
2018-02-24 15:30 | 236 | 236
2018-02-24 16:00 | 258 | 257
2018-02-24 16:30 | 263 | 262
2018-02-24 17:00 | 267 | 266
2018-02-24 17:30 | 271 | 270
2018-02-24 18:00 | 269 | 269
2018-02-24 18:30 | 270 | 270
2018-02-24 19:00 | 278 | 277
2018-02-24 19:30 | 274 | 273
2018-02-24 20:00 | 271 | 270
2018-02-24 20:30 | 266 | 266
2018-02-24 21:00 | 257 | 257
2018-02-24 21:30 | 250 | 250
2018-02-24 22:00 | 243 | 243
2018-02-24 22:30 | 240 | 240
2018-02-24 23:00 | 238 | 238
2018-02-24 23:30 | 224 | 224
2018-02-25 | 207 | 207
2018-02-25 00:30 | 192 | 192
2018-02-25 01:00 | 183 | 183
2018-02-25 01:30 | 177 | 177
2018-02-25 02:00 | 173 | 173
2018-02-25 02:30 | 168 | 168
2018-02-25 03:00 | 166 | 166
2018-02-25 03:30 | 164 | 164
2018-02-25 04:00 | 163 | 163
2018-02-25 04:30 | 163 | 163
2018-02-25 05:00 | 163 | 163
2018-02-25 05:30 | 166 | 166
2018-02-25 06:00 | 166 | 166
2018-02-25 06:30 | 170 | 170
2018-02-25 07:00 | 173 | 173
2018-02-25 07:30 | 180 | 180
2018-02-25 08:00 | 188 | 188
2018-02-25 08:30 | 198 | 198
2018-02-25 09:00 | 208 | 208
2018-02-25 09:30 | 215 | 214
2018-02-25 10:00 | 217 | 215
2018-02-25 10:30 | 224 | 222
2018-02-25 11:00 | 231 | 229
2018-02-25 11:30 | 239 | 237
2018-02-25 12:00 | 255 | 254
2018-02-25 12:30 | 259 | 259
2018-02-25 13:00 | 261 | 261
2018-02-25 13:30 | 267 | 267
2018-02-25 14:00 | 279 | 279
2018-02-25 14:30 | 290 | 289
2018-02-25 15:00 | 290 | 289
2018-02-25 15:30 | 290 | 290
2018-02-25 16:00 | 316 | 316
2018-02-25 16:30 | 320 | 320
2018-02-25 17:00 | 322 | 322
2018-02-25 17:30 | 319 | 319
2018-02-25 18:00 | 313 | 313
2018-02-25 18:30 | 312 | 312
2018-02-25 19:00 | 322 | 321
2018-02-25 19:30 | 317 | 317
2018-02-25 20:00 | 312 | 312
2018-02-25 20:30 | 304 | 304
2018-02-25 21:00 | 289 | 288
2018-02-25 21:30 | 277 | 277
2018-02-25 22:00 | 262 | 262
2018-02-25 22:30 | 253 | 253
2018-02-25 23:00 | 247 | 247
2018-02-25 23:30 | 231 | 231
2018-02-26 | 213 | 213
2018-02-26 00:30 | 198 | 198
2018-02-26 01:00 | 190 | 190
2018-02-26 01:30 | 185 | 185
2018-02-26 02:00 | 182 | 182
2018-02-26 02:30 | 180 | 179
2018-02-26 03:00 | 177 | 177
2018-02-26 03:30 | 177 | 177
2018-02-26 04:00 | 177 | 176
2018-02-26 04:30 | 179 | 178
2018-02-26 05:00 | 185 | 185
2018-02-26 05:30 | 199 | 199
2018-02-26 06:00 | 210 | 210
2018-02-26 06:30 | 233 | 233
2018-02-26 07:00 | 251 | 251
2018-02-26 07:30 | 268 | 268
2018-02-26 08:00 | 277 | 277
2018-02-26 08:30 | 281 | 280
2018-02-26 09:00 | 284 | 282
2018-02-26 09:30 | 291 | 290
2018-02-26 10:00 | 299 | 299
2018-02-26 10:30 | 306 | 306
2018-02-26 11:00 | 314 | 314
2018-02-26 11:30 | 316 | 316
2018-02-26 12:00 | 318 | 318
2018-02-26 12:30 | 324 | 323
2018-02-26 13:00 | 331 | 331
2018-02-26 13:30 | 343 | 342
2018-02-26 14:00 | 356 | 355
2018-02-26 14:30 | 365 | 365
2018-02-26 15:00 | 372 | 372
2018-02-26 15:30 | 379 | 379
2018-02-26 16:00 | 395 | 395
2018-02-26 16:30 | 411 | 411
2018-02-26 17:00 | 422 | 422
2018-02-26 17:30 | 423 | 423
2018-02-26 18:00 | 415 | 415
2018-02-26 18:30 | 404 | 404
2018-02-26 19:00 | 403 | 403
2018-02-26 19:30 | 383 | 382
2018-02-26 20:00 | 356 | 356
2018-02-26 20:30 | 329 | 329
2018-02-26 21:00 | 308 | 308
2018-02-26 21:30 | 289 | 289
2018-02-26 22:00 | 276 | 276
2018-02-26 22:30 | 264 | 264
2018-02-26 23:00 | 254 | 254
2018-02-26 23:30 | 236 | 236
2018-02-27 | 217 | 216
2018-02-27 00:30 | 200 | 200
2018-02-27 01:00 | 192 | 192
2018-02-27 01:30 | 186 | 185
2018-02-27 02:00 | 182 | 181
2018-02-27 02:30 | 180 | 179
2018-02-27 03:00 | 178 | 177
2018-02-27 03:30 | 177 | 176
2018-02-27 04:00 | 177 | 176
2018-02-27 04:30 | 180 | 179
2018-02-27 05:00 | 188 | 187
2018-02-27 05:30 | 201 | 200
2018-02-27 06:00 | 211 | 211
2018-02-27 06:30 | 231 | 231
2018-02-27 07:00 | 249 | 248
2018-02-27 07:30 | 263 | 263
2018-02-27 08:00 | 268 | 268
2018-02-27 08:30 | 269 | 269
2018-02-27 09:00 | 273 | 273
2018-02-27 09:30 | 272 | 272
2018-02-27 10:00 | 271 | 271
2018-02-27 10:30 | 265 | 265
2018-02-27 11:00 | 262 | 262
2018-02-27 11:30 | 265 | 265
2018-02-27 12:00 | 260 | 260
2018-02-27 12:30 | 255 | 255
2018-02-27 13:00 | 253 | 253
2018-02-27 13:30 | 257 | 257
2018-02-27 14:00 | 268 | 268
2018-02-27 14:30 | 277 | 277
2018-02-27 15:00 | 283 | 283
2018-02-27 15:30 | 285 | 285
2018-02-27 16:00 | 293 | 293
2018-02-27 16:30 | 297 | 297
2018-02-27 17:00 | 299 | 299
2018-02-27 17:30 | 298 | 298
2018-02-27 18:00 | 295 | 294
2018-02-27 18:30 | 294 | 293
2018-02-27 19:00 | 301 | 301
2018-02-27 19:30 | 296 | 295
2018-02-27 20:00 | 291 | 290
2018-02-27 20:30 | 283 | 282
2018-02-27 21:00 | 266 | 266
2018-02-27 21:30 | 255 | 255
2018-02-27 22:00 | 244 | 244
2018-02-27 22:30 | 235 | 235
2018-02-27 23:00 | 230 | 230
2018-02-27 23:30 | 215 | 214
2018-02-28 | 198 | 197
2018-02-28 00:30 | 183 | 182
2018-02-28 01:00 | 177 | 175
2018-02-28 01:30 | 172 | 170
2018-02-28 02:00 | 169 | 166
2018-02-28 02:30 | 166 | 163
2018-02-28 03:00 | 164 | 161
2018-02-28 03:30 | 165 | 162
2018-02-28 04:00 | 165 | 163
2018-02-28 04:30 | 168 | 166
2018-02-28 05:00 | 173 | 171
2018-02-28 05:30 | 183 | 182
2018-02-28 06:00 | 193 | 192
2018-02-28 06:30 | 211 | 211
2018-02-28 07:00 | 225 | 225
2018-02-28 07:30 | 233 | 233
2018-02-28 08:00 | 234 | 234
2018-02-28 08:30 | 233 | 233
2018-02-28 09:00 | 230 | 229
2018-02-28 09:30 | 229 | 228
2018-02-28 10:00 | 231 | 230
2018-02-28 10:30 | 236 | 234
2018-02-28 11:00 | 238 | 236
2018-02-28 11:30 | 240 | 239
2018-02-28 12:00 | 243 | 242
2018-02-28 12:30 | 248 | 247
2018-02-28 13:00 | 251 | 249
2018-02-28 13:30 | 254 | 252
2018-02-28 14:00 | 262 | 261
2018-02-28 14:30 | 268 | 268
2018-02-28 15:00 | 271 | 271
2018-02-28 15:30 | 280 | 280
2018-02-28 16:00 | 292 | 291
2018-02-28 16:30 | 303 | 303
2018-02-28 17:00 | 314 | 313
2018-02-28 17:30 | 315 | 315
2018-02-28 18:00 | 310 | 310
2018-02-28 18:30 | 306 | 306
2018-02-28 19:00 | 316 | 316
2018-02-28 19:30 | 312 | 312
2018-02-28 20:00 | 306 | 306
2018-02-28 20:30 | 296 | 296
2018-02-28 21:00 | 279 | 278
2018-02-28 21:30 | 267 | 267
2018-02-28 22:00 | 254 | 254
2018-02-28 22:30 | 243 | 243
2018-02-28 23:00 | 237 | 236
2018-02-28 23:30 | 218 | 218
2018-03-01 | 199 | 199
2018-03-01 00:30 | 184 | 184
2018-03-01 01:00 | 175 | 175
2018-03-01 01:30 | 171 | 171
2018-03-01 02:00 | 168 | 168
2018-03-01 02:30 | 168 | 168
2018-03-01 03:00 | 166 | 166
2018-03-01 03:30 | 166 | 166
2018-03-01 04:00 | 166 | 166
2018-03-01 04:30 | 169 | 169
2018-03-01 05:00 | 176 | 176
2018-03-01 05:30 | 188 | 188
2018-03-01 06:00 | 197 | 197
2018-03-01 06:30 | 217 | 216
2018-03-01 07:00 | 231 | 230
2018-03-01 07:30 | 241 | 241
2018-03-01 08:00 | 242 | 241
2018-03-01 08:30 | 240 | 240
2018-03-01 09:00 | 240 | 239
2018-03-01 09:30 | 242 | 241
2018-03-01 10:00 | 248 | 247
2018-03-01 10:30 | 251 | 251
2018-03-01 11:00 | 260 | 260
2018-03-01 11:30 | 268 | 268
2018-03-01 12:00 | 278 | 278
2018-03-01 12:30 | 292 | 291
2018-03-01 13:00 | 309 | 309
2018-03-01 13:30 | 323 | 323
2018-03-01 14:00 | 338 | 338
2018-03-01 14:30 | 350 | 349
2018-03-01 15:00 | 365 | 365
2018-03-01 15:30 | 378 | 378
2018-03-01 16:00 | 396 | 396
2018-03-01 16:30 | 406 | 406
2018-03-01 17:00 | 415 | 414
2018-03-01 17:30 | 415 | 415
2018-03-01 18:00 | 411 | 411
2018-03-01 18:30 | 403 | 402
2018-03-01 19:00 | 411 | 410
2018-03-01 19:30 | 404 | 404
2018-03-01 20:00 | 395 | 395
2018-03-01 20:30 | 381 | 381
2018-03-01 21:00 | 356 | 356
2018-03-01 21:30 | 332 | 332
2018-03-01 22:00 | 310 | 310
2018-03-01 22:30 | 292 | 292
2018-03-01 23:00 | 280 | 280
2018-03-01 23:30 | 259 | 259
2018-03-02 | 240 | 238
2018-03-02 00:30 | 222 | 221
2018-03-02 01:00 | 212 | 211
2018-03-02 01:30 | 205 | 205
2018-03-02 02:00 | 200 | 200
2018-03-02 02:30 | 198 | 198
2018-03-02 03:00 | 197 | 196
2018-03-02 03:30 | 195 | 194
2018-03-02 04:00 | 195 | 194
2018-03-02 04:30 | 197 | 196
2018-03-02 05:00 | 203 | 201
2018-03-02 05:30 | 215 | 213
2018-03-02 06:00 | 223 | 223
2018-03-02 06:30 | 241 | 241
2018-03-02 07:00 | 258 | 258
2018-03-02 07:30 | 272 | 272
2018-03-02 08:00 | 276 | 276
2018-03-02 08:30 | 278 | 278
2018-03-02 09:00 | 282 | 281
2018-03-02 09:30 | 288 | 288
2018-03-02 10:00 | 289 | 289
2018-03-02 10:30 | 295 | 294
2018-03-02 11:00 | 308 | 307
2018-03-02 11:30 | 313 | 312
2018-03-02 12:00 | 313 | 312
2018-03-02 12:30 | 306 | 305
2018-03-02 13:00 | 305 | 305
2018-03-02 13:30 | 319 | 318
2018-03-02 14:00 | 319 | 318
2018-03-02 14:30 | 315 | 315
2018-03-02 15:00 | 307 | 307
2018-03-02 15:30 | 298 | 298
2018-03-02 16:00 | 316 | 316
2018-03-02 16:30 | 324 | 323
2018-03-02 17:00 | 321 | 321
2018-03-02 17:30 | 314 | 314
2018-03-02 18:00 | 306 | 306
2018-03-02 18:30 | 302 | 302
2018-03-02 19:00 | 310 | 309
2018-03-02 19:30 | 305 | 304
2018-03-02 20:00 | 300 | 300
2018-03-02 20:30 | 295 | 294
2018-03-02 21:00 | 284 | 283
2018-03-02 21:30 | 274 | 273
2018-03-02 22:00 | 265 | 265
2018-03-02 22:30 | 260 | 260
2018-03-02 23:00 | 252 | 251
2018-03-02 23:30 | 236 | 235
2018-03-03 | 219 | 218
2018-03-03 00:30 | 205 | 205
2018-03-03 01:00 | 197 | 197
2018-03-03 01:30 | 191 | 191
2018-03-03 02:00 | 187 | 187
2018-03-03 02:30 | 184 | 184
2018-03-03 03:00 | 181 | 181
2018-03-03 03:30 | 180 | 180
2018-03-03 04:00 | 178 | 178
2018-03-03 04:30 | 178 | 178
2018-03-03 05:00 | 180 | 180
2018-03-03 05:30 | 183 | 183
2018-03-03 06:00 | 187 | 187
2018-03-03 06:30 | 194 | 194
2018-03-03 07:00 | 200 | 200
2018-03-03 07:30 | 209 | 208
2018-03-03 08:00 | 215 | 214
2018-03-03 08:30 | 224 | 224
2018-03-03 09:00 | 232 | 232
2018-03-03 09:30 | 237 | 237
2018-03-03 10:00 | 243 | 243
2018-03-03 10:30 | 253 | 252
2018-03-03 11:00 | 259 | 259
2018-03-03 11:30 | 258 | 258
2018-03-03 12:00 | 252 | 252
2018-03-03 12:30 | 253 | 252
2018-03-03 13:00 | 252 | 252
2018-03-03 13:30 | 266 | 266
2018-03-03 14:00 | 270 | 270
2018-03-03 14:30 | 268 | 268
2018-03-03 15:00 | 279 | 279
2018-03-03 15:30 | 286 | 286
2018-03-03 16:00 | 292 | 292
2018-03-03 16:30 | 301 | 301
2018-03-03 17:00 | 309 | 309
2018-03-03 17:30 | 310 | 310
2018-03-03 18:00 | 308 | 307
2018-03-03 18:30 | 309 | 308
2018-03-03 19:00 | 317 | 317
2018-03-03 19:30 | 311 | 311
2018-03-03 20:00 | 305 | 305
2018-03-03 20:30 | 298 | 298
2018-03-03 21:00 | 285 | 285
2018-03-03 21:30 | 276 | 276
2018-03-03 22:00 | 268 | 268
2018-03-03 22:30 | 263 | 263
2018-03-03 23:00 | 260 | 260
2018-03-03 23:30 | 245 | 244
2018-03-04 | 226 | 226
2018-03-04 00:30 | 209 | 209
2018-03-04 01:00 | 202 | 202
2018-03-04 01:30 | 195 | 195
2018-03-04 02:00 | 190 | 190
2018-03-04 02:30 | 185 | 184
2018-03-04 03:00 | 181 | 180
2018-03-04 03:30 | 177 | 177
2018-03-04 04:00 | 174 | 173
2018-03-04 04:30 | 172 | 172
2018-03-04 05:00 | 172 | 172
2018-03-04 05:30 | 174 | 174
2018-03-04 06:00 | 173 | 173
2018-03-04 06:30 | 174 | 173
2018-03-04 07:00 | 182 | 182
2018-03-04 07:30 | 186 | 186
2018-03-04 08:00 | 190 | 189
2018-03-04 08:30 | 199 | 198
2018-03-04 09:00 | 208 | 207
2018-03-04 09:30 | 216 | 215
2018-03-04 10:00 | 219 | 217
2018-03-04 10:30 | 229 | 228
2018-03-04 11:00 | 236 | 236
2018-03-04 11:30 | 241 | 241
2018-03-04 12:00 | 251 | 251
2018-03-04 12:30 | 263 | 263
2018-03-04 13:00 | 278 | 278
2018-03-04 13:30 | 295 | 295
2018-03-04 14:00 | 310 | 310
2018-03-04 14:30 | 331 | 331
2018-03-04 15:00 | 345 | 345
2018-03-04 15:30 | 348 | 348
2018-03-04 16:00 | 348 | 348
2018-03-04 16:30 | 356 | 356
2018-03-04 17:00 | 363 | 363
2018-03-04 17:30 | 364 | 364
2018-03-04 18:00 | 364 | 364
2018-03-04 18:30 | 366 | 366
2018-03-04 19:00 | 368 | 368
2018-03-04 19:30 | 357 | 357
2018-03-04 20:00 | 348 | 348
2018-03-04 20:30 | 333 | 333
2018-03-04 21:00 | 316 | 316
2018-03-04 21:30 | 300 | 300
2018-03-04 22:00 | 286 | 286
2018-03-04 22:30 | 274 | 274
2018-03-04 23:00 | 263 | 263
2018-03-04 23:30 | 245 | 245
2018-03-05 | 226 | 226
2018-03-05 00:30 | 211 | 211
2018-03-05 01:00 | 204 | 204
2018-03-05 01:30 | 198 | 198
2018-03-05 02:00 | 194 | 194
2018-03-05 02:30 | 189 | 188
2018-03-05 03:00 | 187 | 186
2018-03-05 03:30 | 186 | 186
2018-03-05 04:00 | 185 | 184
2018-03-05 04:30 | 187 | 186
2018-03-05 05:00 | 193 | 192
2018-03-05 05:30 | 206 | 205
2018-03-05 06:00 | 219 | 218
2018-03-05 06:30 | 241 | 240
2018-03-05 07:00 | 263 | 261
2018-03-05 07:30 | 284 | 284
2018-03-05 08:00 | 293 | 293
2018-03-05 08:30 | 296 | 296
2018-03-05 09:00 | 292 | 292
2018-03-05 09:30 | 293 | 293
2018-03-05 10:00 | 297 | 297
2018-03-05 10:30 | 298 | 298
2018-03-05 11:00 | 297 | 297
2018-03-05 11:30 | 295 | 295
2018-03-05 12:00 | 292 | 292
2018-03-05 12:30 | 293 | 293
2018-03-05 13:00 | 296 | 296
2018-03-05 13:30 | 295 | 295
2018-03-05 14:00 | 302 | 302
2018-03-05 14:30 | 305 | 304
2018-03-05 15:00 | 308 | 308
2018-03-05 15:30 | 320 | 319
2018-03-05 16:00 | 329 | 328
2018-03-05 16:30 | 332 | 332
2018-03-05 17:00 | 337 | 337
2018-03-05 17:30 | 338 | 338
2018-03-05 18:00 | 337 | 336
2018-03-05 18:30 | 337 | 336
2018-03-05 19:00 | 344 | 343
2018-03-05 19:30 | 334 | 333
2018-03-05 20:00 | 328 | 327
2018-03-05 20:30 | 318 | 317
2018-03-05 21:00 | 303 | 303
2018-03-05 21:30 | 288 | 288
2018-03-05 22:00 | 276 | 276
2018-03-05 22:30 | 265 | 265
2018-03-05 23:00 | 257 | 257
2018-03-05 23:30 | 240 | 240
2018-03-06 | 222 | 221
2018-03-06 00:30 | 204 | 204
2018-03-06 01:00 | 192 | 192
2018-03-06 01:30 | 183 | 183
2018-03-06 02:00 | 180 | 180
2018-03-06 02:30 | 177 | 177
2018-03-06 03:00 | 175 | 175
2018-03-06 03:30 | 175 | 175
2018-03-06 04:00 | 175 | 175
2018-03-06 04:30 | 177 | 177
2018-03-06 05:00 | 184 | 184
2018-03-06 05:30 | 197 | 196
2018-03-06 06:00 | 209 | 208
2018-03-06 06:30 | 230 | 229
2018-03-06 07:00 | 253 | 253
2018-03-06 07:30 | 272 | 271
2018-03-06 08:00 | 277 | 277
2018-03-06 08:30 | 278 | 278
2018-03-06 09:00 | 279 | 279
2018-03-06 09:30 | 284 | 284
2018-03-06 10:00 | 287 | 287
2018-03-06 10:30 | 284 | 284
2018-03-06 11:00 | 282 | 282
2018-03-06 11:30 | 274 | 274
2018-03-06 12:00 | 268 | 268
2018-03-06 12:30 | 264 | 264
2018-03-06 13:00 | 266 | 265
2018-03-06 13:30 | 267 | 267
2018-03-06 14:00 | 271 | 271
2018-03-06 14:30 | 273 | 272
2018-03-06 15:00 | 268 | 268
2018-03-06 15:30 | 265 | 264
2018-03-06 16:00 | 269 | 269
2018-03-06 16:30 | 275 | 274
2018-03-06 17:00 | 277 | 277
2018-03-06 17:30 | 278 | 277
2018-03-06 18:00 | 276 | 275
2018-03-06 18:30 | 277 | 277
2018-03-06 19:00 | 281 | 281
2018-03-06 19:30 | 274 | 274
2018-03-06 20:00 | 267 | 267
2018-03-06 20:30 | 261 | 261
2018-03-06 21:00 | 247 | 247
2018-03-06 21:30 | 237 | 237
2018-03-06 22:00 | 228 | 228
2018-03-06 22:30 | 221 | 221
2018-03-06 23:00 | 216 | 216
2018-03-06 23:30 | 203 | 203
2018-03-07 | 188 | 187
2018-03-07 00:30 | 172 | 172
2018-03-07 01:00 | 165 | 165
2018-03-07 01:30 | 159 | 159
2018-03-07 02:00 | 158 | 158
2018-03-07 02:30 | 156 | 156
2018-03-07 03:00 | 156 | 156
2018-03-07 03:30 | 156 | 156
2018-03-07 04:00 | 156 | 156
2018-03-07 04:30 | 161 | 160
2018-03-07 05:00 | 168 | 168
2018-03-07 05:30 | 181 | 181
2018-03-07 06:00 | 193 | 193
2018-03-07 06:30 | 216 | 215
2018-03-07 07:00 | 238 | 236
2018-03-07 07:30 | 255 | 252
2018-03-07 08:00 | 262 | 261
2018-03-07 08:30 | 264 | 263
2018-03-07 09:00 | 261 | 261
2018-03-07 09:30 | 266 | 265
2018-03-07 10:00 | 265 | 265
2018-03-07 10:30 | 255 | 255
2018-03-07 11:00 | 244 | 244
2018-03-07 11:30 | 254 | 254
2018-03-07 12:00 | 259 | 259
2018-03-07 12:30 | 249 | 249
2018-03-07 13:00 | 238 | 238
2018-03-07 13:30 | 231 | 231
2018-03-07 14:00 | 232 | 232
2018-03-07 14:30 | 232 | 232
2018-03-07 15:00 | 236 | 235
2018-03-07 15:30 | 239 | 238
2018-03-07 16:00 | 248 | 247
2018-03-07 16:30 | 261 | 261
2018-03-07 17:00 | 272 | 272
2018-03-07 17:30 | 274 | 274
2018-03-07 18:00 | 277 | 277
2018-03-07 18:30 | 279 | 279
2018-03-07 19:00 | 286 | 286
2018-03-07 19:30 | 279 | 279
2018-03-07 20:00 | 273 | 273
2018-03-07 20:30 | 267 | 267
2018-03-07 21:00 | 253 | 253
2018-03-07 21:30 | 244 | 243
2018-03-07 22:00 | 234 | 234
2018-03-07 22:30 | 226 | 226
2018-03-07 23:00 | 219 | 219
2018-03-07 23:30 | 207 | 206
2018-03-08 | 189 | 189
2018-03-08 00:30 | 174 | 174
2018-03-08 01:00 | 167 | 167
2018-03-08 01:30 | 162 | 161
2018-03-08 02:00 | 158 | 158
2018-03-08 02:30 | 155 | 155
2018-03-08 03:00 | 155 | 155
2018-03-08 03:30 | 155 | 155
2018-03-08 04:00 | 157 | 156
2018-03-08 04:30 | 161 | 161
2018-03-08 05:00 | 167 | 167
2018-03-08 05:30 | 180 | 180
2018-03-08 06:00 | 193 | 193
2018-03-08 06:30 | 214 | 213
2018-03-08 07:00 | 231 | 231
2018-03-08 07:30 | 244 | 243
2018-03-08 08:00 | 244 | 244
2018-03-08 08:30 | 241 | 241
2018-03-08 09:00 | 242 | 242
2018-03-08 09:30 | 239 | 239
2018-03-08 10:00 | 233 | 233
2018-03-08 10:30 | 237 | 237
2018-03-08 11:00 | 237 | 237
2018-03-08 11:30 | 234 | 234
2018-03-08 12:00 | 236 | 236
2018-03-08 12:30 | 245 | 244
2018-03-08 13:00 | 239 | 239
2018-03-08 13:30 | 234 | 233
2018-03-08 14:00 | 237 | 237
2018-03-08 14:30 | 236 | 236
2018-03-08 15:00 | 236 | 236
2018-03-08 15:30 | 241 | 241
2018-03-08 16:00 | 248 | 248
2018-03-08 16:30 | 255 | 255
2018-03-08 17:00 | 266 | 266
2018-03-08 17:30 | 270 | 270
2018-03-08 18:00 | 270 | 270
2018-03-08 18:30 | 274 | 274
2018-03-08 19:00 | 285 | 285
2018-03-08 19:30 | 279 | 279
2018-03-08 20:00 | 274 | 274
2018-03-08 20:30 | 268 | 268
2018-03-08 21:00 | 256 | 256
2018-03-08 21:30 | 243 | 241
2018-03-08 22:00 | 231 | 230
2018-03-08 22:30 | 223 | 222
2018-03-08 23:00 | 219 | 218
2018-03-08 23:30 | 206 | 205
2018-03-09 | 189 | 189
2018-03-09 00:30 | 174 | 174
2018-03-09 01:00 | 166 | 166
2018-03-09 01:30 | 162 | 161
2018-03-09 02:00 | 159 | 158
2018-03-09 02:30 | 157 | 157
2018-03-09 03:00 | 155 | 155
2018-03-09 03:30 | 156 | 156
2018-03-09 04:00 | 156 | 156
2018-03-09 04:30 | 160 | 160
2018-03-09 05:00 | 166 | 166
2018-03-09 05:30 | 178 | 178
2018-03-09 06:00 | 189 | 189
2018-03-09 06:30 | 208 | 207
2018-03-09 07:00 | 224 | 223
2018-03-09 07:30 | 240 | 238
2018-03-09 08:00 | 240 | 238
2018-03-09 08:30 | 233 | 232
2018-03-09 09:00 | 223 | 222
2018-03-09 09:30 | 229 | 228
2018-03-09 10:00 | 224 | 223
2018-03-09 10:30 | 221 | 220
2018-03-09 11:00 | 216 | 215
2018-03-09 11:30 | 221 | 220
2018-03-09 12:00 | 226 | 225
2018-03-09 12:30 | 221 | 220
2018-03-09 13:00 | 219 | 218
2018-03-09 13:30 | 219 | 218
2018-03-09 14:00 | 225 | 224
2018-03-09 14:30 | 225 | 224
2018-03-09 15:00 | 219 | 218
2018-03-09 15:30 | 229 | 229
2018-03-09 16:00 | 239 | 239
2018-03-09 16:30 | 252 | 251
2018-03-09 17:00 | 260 | 259
2018-03-09 17:30 | 258 | 258
2018-03-09 18:00 | 255 | 255
2018-03-09 18:30 | 257 | 257
2018-03-09 19:00 | 268 | 268
2018-03-09 19:30 | 261 | 261
2018-03-09 20:00 | 257 | 257
2018-03-09 20:30 | 254 | 254
2018-03-09 21:00 | 244 | 244
2018-03-09 21:30 | 234 | 234
2018-03-09 22:00 | 225 | 225
2018-03-09 22:30 | 220 | 220
2018-03-09 23:00 | 216 | 216
2018-03-09 23:30 | 203 | 203
2018-03-10 | 187 | 187
2018-03-10 00:30 | 173 | 173
2018-03-10 01:00 | 166 | 166
2018-03-10 01:30 | 161 | 161
2018-03-10 02:00 | 157 | 157
2018-03-10 02:30 | 155 | 154
2018-03-10 03:00 | 153 | 152
2018-03-10 03:30 | 152 | 152
2018-03-10 04:00 | 152 | 152
2018-03-10 04:30 | 152 | 152
2018-03-10 05:00 | 154 | 153
2018-03-10 05:30 | 159 | 158
2018-03-10 06:00 | 162 | 161
2018-03-10 06:30 | 170 | 169
2018-03-10 07:00 | 175 | 175
2018-03-10 07:30 | 186 | 186
2018-03-10 08:00 | 188 | 188
2018-03-10 08:30 | 181 | 181
2018-03-10 09:00 | 192 | 192
2018-03-10 09:30 | 194 | 194
2018-03-10 10:00 | 207 | 207
2018-03-10 10:30 | 202 | 202
2018-03-10 11:00 | 182 | 182
2018-03-10 11:30 | 186 | 186
2018-03-10 12:00 | 181 | 181
2018-03-10 12:30 | 178 | 178
2018-03-10 13:00 | 179 | 179
2018-03-10 13:30 | 189 | 189
2018-03-10 14:00 | 187 | 187
2018-03-10 14:30 | 185 | 185
2018-03-10 15:00 | 194 | 194
2018-03-10 15:30 | 208 | 208
2018-03-10 16:00 | 212 | 212
2018-03-10 16:30 | 217 | 217
2018-03-10 17:00 | 226 | 226
2018-03-10 17:30 | 229 | 228
2018-03-10 18:00 | 229 | 229
2018-03-10 18:30 | 235 | 235
2018-03-10 19:00 | 241 | 241
2018-03-10 19:30 | 236 | 236
2018-03-10 20:00 | 233 | 233
2018-03-10 20:30 | 228 | 228
2018-03-10 21:00 | 218 | 218
2018-03-10 21:30 | 211 | 211
2018-03-10 22:00 | 206 | 206
2018-03-10 22:30 | 205 | 205
2018-03-10 23:00 | 205 | 205
2018-03-10 23:30 | 194 | 194
2018-03-11 | 180 | 180
2018-03-11 00:30 | 167 | 167
2018-03-11 01:00 | 159 | 158
2018-03-11 01:30 | 155 | 154
2018-03-11 02:00 | 149 | 149
2018-03-11 02:30 | 148 | 148
2018-03-11 03:00 | 146 | 146
2018-03-11 03:30 | 145 | 145
2018-03-11 04:00 | 145 | 145
2018-03-11 04:30 | 145 | 145
2018-03-11 05:00 | 145 | 145
2018-03-11 05:30 | 148 | 148
2018-03-11 06:00 | 149 | 149
2018-03-11 06:30 | 153 | 153
2018-03-11 07:00 | 156 | 156
2018-03-11 07:30 | 163 | 163
2018-03-11 08:00 | 165 | 165
2018-03-11 08:30 | 169 | 169
2018-03-11 09:00 | 180 | 179
2018-03-11 09:30 | 195 | 193
2018-03-11 10:00 | 192 | 191
2018-03-11 10:30 | 184 | 183
2018-03-11 11:00 | 187 | 185
2018-03-11 11:30 | 182 | 181
2018-03-11 12:00 | 171 | 170
2018-03-11 12:30 | 172 | 171
2018-03-11 13:00 | 194 | 192
2018-03-11 13:30 | 189 | 188
2018-03-11 14:00 | 191 | 189
2018-03-11 14:30 | 197 | 196
2018-03-11 15:00 | 193 | 192
2018-03-11 15:30 | 195 | 193
2018-03-11 16:00 | 205 | 203
2018-03-11 16:30 | 214 | 213
2018-03-11 17:00 | 220 | 219
2018-03-11 17:30 | 226 | 224
2018-03-11 18:00 | 233 | 231
2018-03-11 18:30 | 243 | 241
2018-03-11 19:00 | 253 | 251
2018-03-11 19:30 | 244 | 244
2018-03-11 20:00 | 239 | 239
2018-03-11 20:30 | 234 | 233
2018-03-11 21:00 | 225 | 224
2018-03-11 21:30 | 217 | 216
2018-03-11 22:00 | 209 | 208
2018-03-11 22:30 | 206 | 205
2018-03-11 23:00 | 203 | 203
2018-03-11 23:30 | 194 | 194
2018-03-12 | 178 | 178
2018-03-12 00:30 | 164 | 164
2018-03-12 01:00 | 157 | 157
2018-03-12 01:30 | 154 | 154
2018-03-12 02:00 | 150 | 150
2018-03-12 02:30 | 148 | 148
2018-03-12 03:00 | 146 | 146
2018-03-12 03:30 | 147 | 147
2018-03-12 04:00 | 149 | 149
2018-03-12 04:30 | 153 | 153
2018-03-12 05:00 | 160 | 160
2018-03-12 05:30 | 174 | 174
2018-03-12 06:00 | 185 | 184
2018-03-12 06:30 | 207 | 206
2018-03-12 07:00 | 226 | 226
2018-03-12 07:30 | 236 | 236
2018-03-12 08:00 | 234 | 233
2018-03-12 08:30 | 224 | 224
2018-03-12 09:00 | 216 | 216
2018-03-12 09:30 | 216 | 215
2018-03-12 10:00 | 231 | 230
2018-03-12 10:30 | 238 | 238
2018-03-12 11:00 | 241 | 241
2018-03-12 11:30 | 241 | 241
2018-03-12 12:00 | 240 | 240
2018-03-12 12:30 | 241 | 241
2018-03-12 13:00 | 241 | 241
2018-03-12 13:30 | 245 | 245
2018-03-12 14:00 | 249 | 249
2018-03-12 14:30 | 257 | 257
2018-03-12 15:00 | 244 | 243
2018-03-12 15:30 | 250 | 250
2018-03-12 16:00 | 263 | 263
2018-03-12 16:30 | 273 | 273
2018-03-12 17:00 | 283 | 283
2018-03-12 17:30 | 288 | 288
2018-03-12 18:00 | 287 | 287
2018-03-12 18:30 | 289 | 289
2018-03-12 19:00 | 298 | 298
2018-03-12 19:30 | 290 | 290
2018-03-12 20:00 | 284 | 284
2018-03-12 20:30 | 277 | 277
2018-03-12 21:00 | 261 | 260
2018-03-12 21:30 | 250 | 249
2018-03-12 22:00 | 239 | 239
2018-03-12 22:30 | 231 | 231
2018-03-12 23:00 | 226 | 225
2018-03-12 23:30 | 210 | 209
2018-03-13 | 194 | 193
2018-03-13 00:30 | 178 | 178
2018-03-13 01:00 | 170 | 170
2018-03-13 01:30 | 165 | 165
2018-03-13 02:00 | 162 | 162
2018-03-13 02:30 | 160 | 160
2018-03-13 03:00 | 159 | 159
2018-03-13 03:30 | 159 | 159
2018-03-13 04:00 | 159 | 159
2018-03-13 04:30 | 163 | 162
2018-03-13 05:00 | 170 | 169
2018-03-13 05:30 | 183 | 182
2018-03-13 06:00 | 194 | 193
2018-03-13 06:30 | 212 | 211
2018-03-13 07:00 | 227 | 227
2018-03-13 07:30 | 238 | 238
2018-03-13 08:00 | 236 | 236
2018-03-13 08:30 | 245 | 245
2018-03-13 09:00 | 249 | 249
2018-03-13 09:30 | 260 | 259
2018-03-13 10:00 | 267 | 266
2018-03-13 10:30 | 271 | 271
2018-03-13 11:00 | 274 | 274
2018-03-13 11:30 | 275 | 275
2018-03-13 12:00 | 271 | 270
2018-03-13 12:30 | 265 | 265
2018-03-13 13:00 | 271 | 271
2018-03-13 13:30 | 276 | 276
2018-03-13 14:00 | 272 | 271
2018-03-13 14:30 | 272 | 271
2018-03-13 15:00 | 277 | 277
2018-03-13 15:30 | 282 | 281
2018-03-13 16:00 | 284 | 284
2018-03-13 16:30 | 292 | 292
2018-03-13 17:00 | 300 | 300
2018-03-13 17:30 | 303 | 303
2018-03-13 18:00 | 304 | 304
2018-03-13 18:30 | 307 | 307
2018-03-13 19:00 | 315 | 315
2018-03-13 19:30 | 308 | 308
2018-03-13 20:00 | 303 | 303
2018-03-13 20:30 | 293 | 293
2018-03-13 21:00 | 280 | 280
2018-03-13 21:30 | 269 | 269
2018-03-13 22:00 | 258 | 258
2018-03-13 22:30 | 250 | 250
2018-03-13 23:00 | 246 | 246
2018-03-13 23:30 | 231 | 231
2018-03-14 | 211 | 211
2018-03-14 00:30 | 195 | 195
2018-03-14 01:00 | 187 | 187
2018-03-14 01:30 | 182 | 182
2018-03-14 02:00 | 179 | 179
2018-03-14 02:30 | 178 | 178
2018-03-14 03:00 | 176 | 176
2018-03-14 03:30 | 175 | 175
2018-03-14 04:00 | 175 | 175
2018-03-14 04:30 | 179 | 178
2018-03-14 05:00 | 186 | 186
2018-03-14 05:30 | 200 | 199
2018-03-14 06:00 | 215 | 215
2018-03-14 06:30 | 234 | 234
2018-03-14 07:00 | 252 | 252
2018-03-14 07:30 | 268 | 268
2018-03-14 08:00 | 264 | 264
2018-03-14 08:30 | 257 | 257
2018-03-14 09:00 | 249 | 248
2018-03-14 09:30 | 254 | 253
2018-03-14 10:00 | 250 | 249
2018-03-14 10:30 | 248 | 246
2018-03-14 11:00 | 250 | 249
2018-03-14 11:30 | 246 | 245
2018-03-14 12:00 | 244 | 242
2018-03-14 12:30 | 231 | 230
2018-03-14 13:00 | 234 | 232
2018-03-14 13:30 | 235 | 233
2018-03-14 14:00 | 233 | 231
2018-03-14 14:30 | 238 | 236
2018-03-14 15:00 | 242 | 240
2018-03-14 15:30 | 248 | 246
2018-03-14 16:00 | 258 | 256
2018-03-14 16:30 | 270 | 269
2018-03-14 17:00 | 281 | 279
2018-03-14 17:30 | 283 | 282
2018-03-14 18:00 | 281 | 280
2018-03-14 18:30 | 284 | 284
2018-03-14 19:00 | 294 | 293
2018-03-14 19:30 | 286 | 285
2018-03-14 20:00 | 281 | 280
2018-03-14 20:30 | 275 | 274
2018-03-14 21:00 | 262 | 261
2018-03-14 21:30 | 252 | 251
2018-03-14 22:00 | 242 | 241
2018-03-14 22:30 | 232 | 232
2018-03-14 23:00 | 228 | 227
2018-03-14 23:30 | 214 | 214
2018-03-15 | 196 | 196
2018-03-15 00:30 | 181 | 181
2018-03-15 01:00 | 174 | 174
2018-03-15 01:30 | 168 | 168
2018-03-15 02:00 | 165 | 165
2018-03-15 02:30 | 163 | 163
2018-03-15 03:00 | 162 | 162
2018-03-15 03:30 | 161 | 161
2018-03-15 04:00 | 161 | 161
2018-03-15 04:30 | 165 | 165
2018-03-15 05:00 | 171 | 171
2018-03-15 05:30 | 185 | 185
2018-03-15 06:00 | 198 | 198
2018-03-15 06:30 | 218 | 217
2018-03-15 07:00 | 234 | 233
2018-03-15 07:30 | 247 | 246
2018-03-15 08:00 | 252 | 251
2018-03-15 08:30 | 248 | 247
2018-03-15 09:00 | 238 | 238
2018-03-15 09:30 | 234 | 234
2018-03-15 10:00 | 225 | 225
2018-03-15 10:30 | 225 | 224
2018-03-15 11:00 | 228 | 228
2018-03-15 11:30 | 233 | 233
2018-03-15 12:00 | 235 | 235
2018-03-15 12:30 | 239 | 239
2018-03-15 13:00 | 242 | 242
2018-03-15 13:30 | 246 | 246
2018-03-15 14:00 | 248 | 248
2018-03-15 14:30 | 253 | 253
2018-03-15 15:00 | 257 | 257
2018-03-15 15:30 | 260 | 260
2018-03-15 16:00 | 272 | 272
2018-03-15 16:30 | 283 | 283
2018-03-15 17:00 | 294 | 294
2018-03-15 17:30 | 296 | 296
2018-03-15 18:00 | 295 | 294
2018-03-15 18:30 | 296 | 296
2018-03-15 19:00 | 305 | 304
2018-03-15 19:30 | 297 | 296
2018-03-15 20:00 | 291 | 290
2018-03-15 20:30 | 284 | 284
2018-03-15 21:00 | 269 | 269
2018-03-15 21:30 | 254 | 254
2018-03-15 22:00 | 242 | 242
2018-03-15 22:30 | 233 | 233
2018-03-15 23:00 | 228 | 228
2018-03-15 23:30 | 212 | 212
2018-03-16 | 195 | 195
2018-03-16 00:30 | 180 | 180
2018-03-16 01:00 | 171 | 171
2018-03-16 01:30 | 166 | 166
2018-03-16 02:00 | 163 | 163
2018-03-16 02:30 | 160 | 160
2018-03-16 03:00 | 159 | 159
2018-03-16 03:30 | 159 | 159
2018-03-16 04:00 | 160 | 160
2018-03-16 04:30 | 162 | 162
2018-03-16 05:00 | 169 | 169
2018-03-16 05:30 | 182 | 182
2018-03-16 06:00 | 192 | 192
2018-03-16 06:30 | 210 | 209
2018-03-16 07:00 | 227 | 226
2018-03-16 07:30 | 239 | 238
2018-03-16 08:00 | 236 | 236
2018-03-16 08:30 | 232 | 232
2018-03-16 09:00 | 228 | 228
2018-03-16 09:30 | 226 | 226
2018-03-16 10:00 | 224 | 224
2018-03-16 10:30 | 223 | 223
2018-03-16 11:00 | 222 | 222
2018-03-16 11:30 | 225 | 224
2018-03-16 12:00 | 227 | 227
2018-03-16 12:30 | 232 | 231
2018-03-16 13:00 | 238 | 237
2018-03-16 13:30 | 245 | 245
2018-03-16 14:00 | 251 | 251
2018-03-16 14:30 | 258 | 258
2018-03-16 15:00 | 262 | 262
2018-03-16 15:30 | 271 | 271
2018-03-16 16:00 | 284 | 284
2018-03-16 16:30 | 295 | 295
2018-03-16 17:00 | 303 | 303
2018-03-16 17:30 | 303 | 303
2018-03-16 18:00 | 296 | 295
2018-03-16 18:30 | 291 | 291
2018-03-16 19:00 | 298 | 298
2018-03-16 19:30 | 289 | 289
2018-03-16 20:00 | 283 | 283
2018-03-16 20:30 | 279 | 278
2018-03-16 21:00 | 265 | 265
2018-03-16 21:30 | 254 | 253
2018-03-16 22:00 | 244 | 243
2018-03-16 22:30 | 238 | 237
2018-03-16 23:00 | 233 | 232
2018-03-16 23:30 | 218 | 218
2018-03-17 | 198 | 198
2018-03-17 00:30 | 184 | 184
2018-03-17 01:00 | 176 | 176
2018-03-17 01:30 | 170 | 170
2018-03-17 02:00 | 166 | 166
2018-03-17 02:30 | 163 | 163
2018-03-17 03:00 | 161 | 161
2018-03-17 03:30 | 159 | 158
2018-03-17 04:00 | 158 | 158
2018-03-17 04:30 | 158 | 157
2018-03-17 05:00 | 159 | 159
2018-03-17 05:30 | 163 | 163
2018-03-17 06:00 | 166 | 166
2018-03-17 06:30 | 171 | 171
2018-03-17 07:00 | 177 | 177
2018-03-17 07:30 | 182 | 182
2018-03-17 08:00 | 200 | 199
2018-03-17 08:30 | 203 | 202
2018-03-17 09:00 | 204 | 203
2018-03-17 09:30 | 205 | 204
2018-03-17 10:00 | 203 | 202
2018-03-17 10:30 | 201 | 201
2018-03-17 11:00 | 201 | 201
2018-03-17 11:30 | 203 | 203
2018-03-17 12:00 | 206 | 206
2018-03-17 12:30 | 211 | 211
2018-03-17 13:00 | 217 | 217
2018-03-17 13:30 | 224 | 224
2018-03-17 14:00 | 233 | 232
2018-03-17 14:30 | 241 | 240
2018-03-17 15:00 | 251 | 250
2018-03-17 15:30 | 263 | 262
2018-03-17 16:00 | 274 | 273
2018-03-17 16:30 | 278 | 276
2018-03-17 17:00 | 277 | 275
2018-03-17 17:30 | 277 | 276
2018-03-17 18:00 | 273 | 272
2018-03-17 18:30 | 277 | 273
2018-03-17 19:00 | 284 | 280
2018-03-17 19:30 | 274 | 271
2018-03-17 20:00 | 267 | 265
2018-03-17 20:30 | 261 | 259
2018-03-17 21:00 | 248 | 246
2018-03-17 21:30 | 239 | 238
2018-03-17 22:00 | 232 | 231
2018-03-17 22:30 | 227 | 226
2018-03-17 23:00 | 224 | 223
2018-03-17 23:30 | 211 | 211
2018-03-18 | 195 | 195
2018-03-18 00:30 | 180 | 180
2018-03-18 01:00 | 172 | 172
2018-03-18 01:30 | 167 | 167
2018-03-18 02:00 | 162 | 162
2018-03-18 02:30 | 160 | 159
2018-03-18 03:00 | 157 | 157
2018-03-18 03:30 | 156 | 156
2018-03-18 04:00 | 155 | 155
2018-03-18 04:30 | 155 | 155
2018-03-18 05:00 | 156 | 155
2018-03-18 05:30 | 158 | 157
2018-03-18 06:00 | 158 | 158
2018-03-18 06:30 | 161 | 161
2018-03-18 07:00 | 164 | 164
2018-03-18 07:30 | 170 | 170
2018-03-18 08:00 | 174 | 174
2018-03-18 08:30 | 178 | 178
2018-03-18 09:00 | 180 | 180
2018-03-18 09:30 | 187 | 186
2018-03-18 10:00 | 195 | 194
2018-03-18 10:30 | 198 | 196
2018-03-18 11:00 | 196 | 194
2018-03-18 11:30 | 197 | 195
2018-03-18 12:00 | 203 | 201
2018-03-18 12:30 | 209 | 207
2018-03-18 13:00 | 214 | 214
2018-03-18 13:30 | 220 | 220
2018-03-18 14:00 | 229 | 229
2018-03-18 14:30 | 237 | 237
2018-03-18 15:00 | 249 | 248
2018-03-18 15:30 | 262 | 261
2018-03-18 16:00 | 274 | 274
2018-03-18 16:30 | 286 | 285
2018-03-18 17:00 | 296 | 295
2018-03-18 17:30 | 301 | 301
2018-03-18 18:00 | 301 | 300
2018-03-18 18:30 | 305 | 303
2018-03-18 19:00 | 312 | 310
2018-03-18 19:30 | 300 | 299
2018-03-18 20:00 | 292 | 291
2018-03-18 20:30 | 282 | 282
2018-03-18 21:00 | 267 | 266
2018-03-18 21:30 | 255 | 255
2018-03-18 22:00 | 244 | 243
2018-03-18 22:30 | 236 | 235
2018-03-18 23:00 | 231 | 231
2018-03-18 23:30 | 216 | 216
2018-03-19 | 199 | 199
2018-03-19 00:30 | 185 | 185
2018-03-19 01:00 | 178 | 178
2018-03-19 01:30 | 172 | 172
2018-03-19 02:00 | 169 | 169
2018-03-19 02:30 | 167 | 167
2018-03-19 03:00 | 166 | 166
2018-03-19 03:30 | 165 | 165
2018-03-19 04:00 | 165 | 165
2018-03-19 04:30 | 168 | 168
2018-03-19 05:00 | 176 | 176
2018-03-19 05:30 | 189 | 189
2018-03-19 06:00 | 201 | 201
2018-03-19 06:30 | 223 | 222
2018-03-19 07:00 | 239 | 238
2018-03-19 07:30 | 252 | 250
2018-03-19 08:00 | 256 | 256
2018-03-19 08:30 | 258 | 257
2018-03-19 09:00 | 260 | 260
2018-03-19 09:30 | 264 | 263
2018-03-19 10:00 | 265 | 264
2018-03-19 10:30 | 269 | 268
2018-03-19 11:00 | 274 | 273
2018-03-19 11:30 | 277 | 276
2018-03-19 12:00 | 279 | 279
2018-03-19 12:30 | 282 | 282
2018-03-19 13:00 | 291 | 291
2018-03-19 13:30 | 297 | 296
2018-03-19 14:00 | 306 | 305
2018-03-19 14:30 | 314 | 313
2018-03-19 15:00 | 319 | 318
2018-03-19 15:30 | 327 | 326
2018-03-19 16:00 | 342 | 341
2018-03-19 16:30 | 353 | 353
2018-03-19 17:00 | 362 | 361
2018-03-19 17:30 | 360 | 359
2018-03-19 18:00 | 352 | 352
2018-03-19 18:30 | 352 | 351
2018-03-19 19:00 | 358 | 357
2018-03-19 19:30 | 346 | 346
2018-03-19 20:00 | 338 | 337
2018-03-19 20:30 | 329 | 329
2018-03-19 21:00 | 312 | 312
2018-03-19 21:30 | 295 | 295
2018-03-19 22:00 | 282 | 282
2018-03-19 22:30 | 271 | 271
2018-03-19 23:00 | 263 | 262
2018-03-19 23:30 | 241 | 241
2018-03-20 | 223 | 222
2018-03-20 00:30 | 206 | 205
2018-03-20 01:00 | 197 | 196
2018-03-20 01:30 | 190 | 189
2018-03-20 02:00 | 185 | 185
2018-03-20 02:30 | 181 | 181
2018-03-20 03:00 | 180 | 180
2018-03-20 03:30 | 179 | 179
2018-03-20 04:00 | 178 | 178
2018-03-20 04:30 | 182 | 181
2018-03-20 05:00 | 189 | 188
2018-03-20 05:30 | 201 | 200
2018-03-20 06:00 | 212 | 211
2018-03-20 06:30 | 230 | 229
2018-03-20 07:00 | 247 | 245
2018-03-20 07:30 | 260 | 259
2018-03-20 08:00 | 262 | 262
2018-03-20 08:30 | 263 | 262
2018-03-20 09:00 | 265 | 264
2018-03-20 09:30 | 267 | 267
2018-03-20 10:00 | 267 | 266
2018-03-20 10:30 | 266 | 265
2018-03-20 11:00 | 266 | 265
2018-03-20 11:30 | 264 | 262
2018-03-20 12:00 | 261 | 260
2018-03-20 12:30 | 262 | 261
2018-03-20 13:00 | 266 | 265
2018-03-20 13:30 | 272 | 270
2018-03-20 14:00 | 278 | 277
2018-03-20 14:30 | 281 | 280
2018-03-20 15:00 | 284 | 282
2018-03-20 15:30 | 292 | 291
2018-03-20 16:00 | 305 | 305
2018-03-20 16:30 | 313 | 313
2018-03-20 17:00 | 317 | 317
2018-03-20 17:30 | 321 | 321
2018-03-20 18:00 | 317 | 317
2018-03-20 18:30 | 318 | 318
2018-03-20 19:00 | 324 | 324
2018-03-20 19:30 | 316 | 316
2018-03-20 20:00 | 311 | 311
2018-03-20 20:30 | 301 | 301
2018-03-20 21:00 | 286 | 286
2018-03-20 21:30 | 273 | 272
2018-03-20 22:00 | 262 | 262
2018-03-20 22:30 | 252 | 252
2018-03-20 23:00 | 245 | 245
2018-03-20 23:30 | 230 | 230
2018-03-21 | 210 | 209
2018-03-21 00:30 | 195 | 195
2018-03-21 01:00 | 187 | 187
2018-03-21 01:30 | 183 | 183
2018-03-21 02:00 | 179 | 179
2018-03-21 02:30 | 177 | 177
2018-03-21 03:00 | 177 | 177
2018-03-21 03:30 | 177 | 177
2018-03-21 04:00 | 176 | 176
2018-03-21 04:30 | 178 | 178
2018-03-21 05:00 | 184 | 184
2018-03-21 05:30 | 198 | 198
2018-03-21 06:00 | 210 | 209
2018-03-21 06:30 | 231 | 229
2018-03-21 07:00 | 249 | 247
2018-03-21 07:30 | 260 | 257
2018-03-21 08:00 | 266 | 266
2018-03-21 08:30 | 267 | 267
2018-03-21 09:00 | 271 | 271
2018-03-21 09:30 | 268 | 267
2018-03-21 10:00 | 279 | 278
2018-03-21 10:30 | 273 | 273
2018-03-21 11:00 | 257 | 257
2018-03-21 11:30 | 268 | 268
2018-03-21 12:00 | 268 | 268
2018-03-21 12:30 | 271 | 271
2018-03-21 13:00 | 271 | 271
2018-03-21 13:30 | 266 | 265
2018-03-21 14:00 | 263 | 263
2018-03-21 14:30 | 258 | 258
2018-03-21 15:00 | 266 | 266
2018-03-21 15:30 | 278 | 278
2018-03-21 16:00 | 281 | 281
2018-03-21 16:30 | 287 | 287
2018-03-21 17:00 | 291 | 291
2018-03-21 17:30 | 296 | 296
2018-03-21 18:00 | 296 | 296
2018-03-21 18:30 | 298 | 298
2018-03-21 19:00 | 302 | 302
2018-03-21 19:30 | 295 | 295
2018-03-21 20:00 | 289 | 289
2018-03-21 20:30 | 282 | 282
2018-03-21 21:00 | 268 | 268
2018-03-21 21:30 | 257 | 256
2018-03-21 22:00 | 249 | 248
2018-03-21 22:30 | 242 | 242
2018-03-21 23:00 | 238 | 237
2018-03-21 23:30 | 223 | 223
2018-03-22 | 206 | 206
2018-03-22 00:30 | 191 | 191
2018-03-22 01:00 | 183 | 182
2018-03-22 01:30 | 178 | 177
2018-03-22 02:00 | 175 | 174
2018-03-22 02:30 | 171 | 170
2018-03-22 03:00 | 170 | 170
2018-03-22 03:30 | 170 | 169
2018-03-22 04:00 | 169 | 168
2018-03-22 04:30 | 172 | 171
2018-03-22 05:00 | 178 | 177
2018-03-22 05:30 | 192 | 190
2018-03-22 06:00 | 205 | 203
2018-03-22 06:30 | 228 | 227
2018-03-22 07:00 | 244 | 244
2018-03-22 07:30 | 255 | 254
2018-03-22 08:00 | 255 | 254
2018-03-22 08:30 | 259 | 259
2018-03-22 09:00 | 259 | 259
2018-03-22 09:30 | 247 | 247
2018-03-22 10:00 | 248 | 248
2018-03-22 10:30 | 254 | 254
2018-03-22 11:00 | 261 | 261
2018-03-22 11:30 | 249 | 249
2018-03-22 12:00 | 247 | 247
2018-03-22 12:30 | 238 | 238
2018-03-22 13:00 | 243 | 243
2018-03-22 13:30 | 239 | 239
2018-03-22 14:00 | 244 | 244
2018-03-22 14:30 | 248 | 248
2018-03-22 15:00 | 256 | 256
2018-03-22 15:30 | 266 | 266
2018-03-22 16:00 | 275 | 275
2018-03-22 16:30 | 284 | 284
2018-03-22 17:00 | 292 | 292
2018-03-22 17:30 | 292 | 292
2018-03-22 18:00 | 294 | 293
2018-03-22 18:30 | 299 | 299
2018-03-22 19:00 | 304 | 304
2018-03-22 19:30 | 296 | 296
2018-03-22 20:00 | 292 | 292
2018-03-22 20:30 | 287 | 287
2018-03-22 21:00 | 274 | 274
2018-03-22 21:30 | 258 | 258
2018-03-22 22:00 | 246 | 245
2018-03-22 22:30 | 239 | 237
2018-03-22 23:00 | 234 | 231
2018-03-22 23:30 | 218 | 216
2018-03-23 | 200 | 199
2018-03-23 00:30 | 182 | 182
2018-03-23 01:00 | 176 | 176
2018-03-23 01:30 | 171 | 170
2018-03-23 02:00 | 168 | 167
2018-03-23 02:30 | 166 | 166
2018-03-23 03:00 | 163 | 163
2018-03-23 03:30 | 165 | 165
2018-03-23 04:00 | 164 | 164
2018-03-23 04:30 | 168 | 168
2018-03-23 05:00 | 175 | 174
2018-03-23 05:30 | 187 | 186
2018-03-23 06:00 | 200 | 198
2018-03-23 06:30 | 218 | 217
2018-03-23 07:00 | 235 | 235
2018-03-23 07:30 | 246 | 246
2018-03-23 08:00 | 248 | 247
2018-03-23 08:30 | 247 | 247
2018-03-23 09:00 | 243 | 243
2018-03-23 09:30 | 245 | 245
2018-03-23 10:00 | 256 | 255
2018-03-23 10:30 | 248 | 247
2018-03-23 11:00 | 243 | 243
2018-03-23 11:30 | 241 | 241
2018-03-23 12:00 | 243 | 243
2018-03-23 12:30 | 234 | 234
2018-03-23 13:00 | 236 | 236
2018-03-23 13:30 | 239 | 239
2018-03-23 14:00 | 240 | 240
2018-03-23 14:30 | 243 | 242
2018-03-23 15:00 | 249 | 249
2018-03-23 15:30 | 255 | 255
2018-03-23 16:00 | 266 | 265
2018-03-23 16:30 | 276 | 276
2018-03-23 17:00 | 284 | 284
2018-03-23 17:30 | 282 | 282
2018-03-23 18:00 | 277 | 277
2018-03-23 18:30 | 281 | 281
2018-03-23 19:00 | 285 | 285
2018-03-23 19:30 | 278 | 277
2018-03-23 20:00 | 274 | 274
2018-03-23 20:30 | 269 | 269
2018-03-23 21:00 | 256 | 256
2018-03-23 21:30 | 246 | 246
2018-03-23 22:00 | 238 | 237
2018-03-23 22:30 | 233 | 233
2018-03-23 23:00 | 230 | 229
2018-03-23 23:30 | 215 | 215
2018-03-24 | 197 | 196
2018-03-24 00:30 | 183 | 182
2018-03-24 01:00 | 177 | 176
2018-03-24 01:30 | 171 | 170
2018-03-24 02:00 | 167 | 166
2018-03-24 02:30 | 164 | 163
2018-03-24 03:00 | 162 | 162
2018-03-24 03:30 | 160 | 160
2018-03-24 04:00 | 160 | 159
2018-03-24 04:30 | 160 | 159
2018-03-24 05:00 | 162 | 162
2018-03-24 05:30 | 167 | 166
2018-03-24 06:00 | 170 | 170
2018-03-24 06:30 | 176 | 176
2018-03-24 07:00 | 183 | 182
2018-03-24 07:30 | 190 | 189
2018-03-24 08:00 | 193 | 192
2018-03-24 08:30 | 198 | 198
2018-03-24 09:00 | 205 | 205
2018-03-24 09:30 | 205 | 205
2018-03-24 10:00 | 203 | 203
2018-03-24 10:30 | 208 | 208
2018-03-24 11:00 | 209 | 209
2018-03-24 11:30 | 208 | 207
2018-03-24 12:00 | 205 | 205
2018-03-24 12:30 | 200 | 200
2018-03-24 13:00 | 195 | 195
2018-03-24 13:30 | 196 | 196
2018-03-24 14:00 | 194 | 194
2018-03-24 14:30 | 203 | 203
2018-03-24 15:00 | 213 | 213
2018-03-24 15:30 | 222 | 222
2018-03-24 16:00 | 233 | 233
2018-03-24 16:30 | 243 | 242
2018-03-24 17:00 | 246 | 246
2018-03-24 17:30 | 248 | 248
2018-03-24 18:00 | 252 | 252
2018-03-24 18:30 | 259 | 259
2018-03-24 19:00 | 262 | 262
2018-03-24 19:30 | 255 | 255
2018-03-24 20:00 | 252 | 251
2018-03-24 20:30 | 246 | 246
2018-03-24 21:00 | 235 | 234
2018-03-24 21:30 | 227 | 227
2018-03-24 22:00 | 221 | 221
2018-03-24 22:30 | 217 | 217
2018-03-24 23:00 | 217 | 216
2018-03-24 23:30 | 204 | 204
2018-03-25 | 188 | 188
2018-03-25 00:30 | 174 | 174
2018-03-25 01:00 | 166 | 166
2018-03-25 01:30 | 161 | 161
2018-03-25 02:00 | 158 | 158
2018-03-25 02:30 | 158 | 158
2018-03-25 03:00 | 157 | 156
2018-03-25 03:30 | 156 | 155
2018-03-25 04:00 | 154 | 153
2018-03-25 04:30 | 151 | 151
2018-03-25 05:00 | 150 | 150
2018-03-25 05:30 | 153 | 153
2018-03-25 06:00 | 155 | 155
2018-03-25 06:30 | 157 | 157
2018-03-25 07:00 | 161 | 161
2018-03-25 07:30 | 168 | 168
2018-03-25 08:00 | 172 | 172
2018-03-25 08:30 | 176 | 175
2018-03-25 09:00 | 180 | 179
2018-03-25 09:30 | 190 | 188
2018-03-25 10:00 | 199 | 197
2018-03-25 10:30 | 204 | 203
2018-03-25 11:00 | 206 | 205
2018-03-25 11:30 | 201 | 200
2018-03-25 12:00 | 199 | 198
2018-03-25 12:30 | 205 | 203
2018-03-25 13:00 | 203 | 202
2018-03-25 13:30 | 212 | 211
2018-03-25 14:00 | 214 | 213
2018-03-25 14:30 | 211 | 210
2018-03-25 15:00 | 212 | 212
2018-03-25 15:30 | 227 | 226
2018-03-25 16:00 | 238 | 237
2018-03-25 16:30 | 245 | 244
2018-03-25 17:00 | 252 | 251
2018-03-25 17:30 | 256 | 255
2018-03-25 18:00 | 260 | 259
2018-03-25 18:30 | 269 | 268
2018-03-25 19:00 | 273 | 272
2018-03-25 19:30 | 265 | 264
2018-03-25 20:00 | 261 | 260
2018-03-25 20:30 | 257 | 256
2018-03-25 21:00 | 245 | 244
2018-03-25 21:30 | 236 | 235
2018-03-25 22:00 | 228 | 228
2018-03-25 22:30 | 225 | 224
2018-03-25 23:00 | 224 | 223
2018-03-25 23:30 | 210 | 210
2018-03-26 | 195 | 195
2018-03-26 00:30 | 181 | 181
2018-03-26 01:00 | 174 | 174
2018-03-26 01:30 | 170 | 170
2018-03-26 02:00 | 167 | 167
2018-03-26 02:30 | 166 | 166
2018-03-26 03:00 | 165 | 165
2018-03-26 03:30 | 164 | 164
2018-03-26 04:00 | 165 | 165
2018-03-26 04:30 | 169 | 169
2018-03-26 05:00 | 176 | 176
2018-03-26 05:30 | 190 | 190
2018-03-26 06:00 | 203 | 202
2018-03-26 06:30 | 223 | 222
2018-03-26 07:00 | 240 | 240
2018-03-26 07:30 | 254 | 254
2018-03-26 08:00 | 257 | 257
2018-03-26 08:30 | 256 | 256
2018-03-26 09:00 | 256 | 256
2018-03-26 09:30 | 263 | 263
2018-03-26 10:00 | 269 | 269
2018-03-26 10:30 | 277 | 277
2018-03-26 11:00 | 276 | 276
2018-03-26 11:30 | 273 | 273
2018-03-26 12:00 | 279 | 278
2018-03-26 12:30 | 284 | 284
2018-03-26 13:00 | 287 | 287
2018-03-26 13:30 | 292 | 291
2018-03-26 14:00 | 296 | 296
2018-03-26 14:30 | 303 | 303
2018-03-26 15:00 | 310 | 309
2018-03-26 15:30 | 314 | 313
2018-03-26 16:00 | 321 | 320
2018-03-26 16:30 | 326 | 326
2018-03-26 17:00 | 333 | 333
2018-03-26 17:30 | 335 | 335
2018-03-26 18:00 | 334 | 334
2018-03-26 18:30 | 337 | 337
2018-03-26 19:00 | 338 | 338
2018-03-26 19:30 | 328 | 328
2018-03-26 20:00 | 321 | 321
2018-03-26 20:30 | 312 | 312
2018-03-26 21:00 | 295 | 295
2018-03-26 21:30 | 279 | 279
2018-03-26 22:00 | 268 | 267
2018-03-26 22:30 | 259 | 258
2018-03-26 23:00 | 251 | 251
2018-03-26 23:30 | 235 | 235
2018-03-27 | 218 | 217
2018-03-27 00:30 | 202 | 202
2018-03-27 01:00 | 194 | 194
2018-03-27 01:30 | 188 | 188
2018-03-27 02:00 | 184 | 184
2018-03-27 02:30 | 182 | 182
2018-03-27 03:00 | 180 | 180
2018-03-27 03:30 | 179 | 179
2018-03-27 04:00 | 179 | 179
2018-03-27 04:30 | 182 | 182
2018-03-27 05:00 | 189 | 189
2018-03-27 05:30 | 204 | 204
2018-03-27 06:00 | 218 | 218
2018-03-27 06:30 | 239 | 239
2018-03-27 07:00 | 258 | 258
2018-03-27 07:30 | 278 | 278
2018-03-27 08:00 | 287 | 287
2018-03-27 08:30 | 289 | 289
2018-03-27 09:00 | 292 | 292
2018-03-27 09:30 | 298 | 297
2018-03-27 10:00 | 299 | 299
2018-03-27 10:30 | 297 | 297
2018-03-27 11:00 | 297 | 297
2018-03-27 11:30 | 296 | 296
2018-03-27 12:00 | 304 | 304
2018-03-27 12:30 | 302 | 301
2018-03-27 13:00 | 293 | 293
2018-03-27 13:30 | 274 | 274
2018-03-27 14:00 | 267 | 267
2018-03-27 14:30 | 272 | 272
2018-03-27 15:00 | 282 | 281
2018-03-27 15:30 | 294 | 293
2018-03-27 16:00 | 303 | 301
2018-03-27 16:30 | 311 | 310
2018-03-27 17:00 | 315 | 314
2018-03-27 17:30 | 314 | 314
2018-03-27 18:00 | 312 | 312
2018-03-27 18:30 | 315 | 314
2018-03-27 19:00 | 316 | 316
2018-03-27 19:30 | 305 | 304
2018-03-27 20:00 | 301 | 300
2018-03-27 20:30 | 294 | 293
2018-03-27 21:00 | 280 | 280
2018-03-27 21:30 | 266 | 266
2018-03-27 22:00 | 255 | 255
2018-03-27 22:30 | 248 | 247
2018-03-27 23:00 | 241 | 240
2018-03-27 23:30 | 226 | 225
2018-03-28 | 208 | 207
2018-03-28 00:30 | 193 | 193
2018-03-28 01:00 | 187 | 186
2018-03-28 01:30 | 181 | 181
2018-03-28 02:00 | 178 | 177
2018-03-28 02:30 | 175 | 175
2018-03-28 03:00 | 172 | 172
2018-03-28 03:30 | 172 | 172
2018-03-28 04:00 | 172 | 172
2018-03-28 04:30 | 175 | 175
2018-03-28 05:00 | 185 | 185
2018-03-28 05:30 | 197 | 196
2018-03-28 06:00 | 209 | 209
2018-03-28 06:30 | 227 | 227
2018-03-28 07:00 | 243 | 243
2018-03-28 07:30 | 253 | 253
2018-03-28 08:00 | 254 | 254
2018-03-28 08:30 | 255 | 255
2018-03-28 09:00 | 255 | 254
2018-03-28 09:30 | 252 | 251
2018-03-28 10:00 | 252 | 251
2018-03-28 10:30 | 252 | 252
2018-03-28 11:00 | 252 | 251
2018-03-28 11:30 | 251 | 250
2018-03-28 12:00 | 252 | 251
2018-03-28 12:30 | 253 | 252
2018-03-28 13:00 | 257 | 256
2018-03-28 13:30 | 261 | 259
2018-03-28 14:00 | 270 | 268
2018-03-28 14:30 | 278 | 276
2018-03-28 15:00 | 286 | 284
2018-03-28 15:30 | 296 | 295
2018-03-28 16:00 | 306 | 305
2018-03-28 16:30 | 315 | 315
2018-03-28 17:00 | 322 | 321
2018-03-28 17:30 | 321 | 320
2018-03-28 18:00 | 315 | 315
2018-03-28 18:30 | 318 | 318
2018-03-28 19:00 | 320 | 320
2018-03-28 19:30 | 309 | 309
2018-03-28 20:00 | 303 | 303
2018-03-28 20:30 | 295 | 295
2018-03-28 21:00 | 278 | 278
2018-03-28 21:30 | 265 | 265
2018-03-28 22:00 | 255 | 254
2018-03-28 22:30 | 246 | 246
2018-03-28 23:00 | 241 | 241
2018-03-28 23:30 | 225 | 225
2018-03-29 | 207 | 207
2018-03-29 00:30 | 192 | 192
2018-03-29 01:00 | 185 | 185
2018-03-29 01:30 | 180 | 180
2018-03-29 02:00 | 175 | 175
2018-03-29 02:30 | 173 | 173
2018-03-29 03:00 | 172 | 172
2018-03-29 03:30 | 172 | 172
2018-03-29 04:00 | 172 | 172
2018-03-29 04:30 | 176 | 176
2018-03-29 05:00 | 184 | 184
2018-03-29 05:30 | 197 | 197
2018-03-29 06:00 | 211 | 211
2018-03-29 06:30 | 230 | 230
2018-03-29 07:00 | 250 | 250
2018-03-29 07:30 | 267 | 267
2018-03-29 08:00 | 269 | 269
2018-03-29 08:30 | 268 | 268
2018-03-29 09:00 | 271 | 270
2018-03-29 09:30 | 274 | 273
2018-03-29 10:00 | 269 | 268
2018-03-29 10:30 | 270 | 269
2018-03-29 11:00 | 267 | 266
2018-03-29 11:30 | 266 | 265
2018-03-29 12:00 | 271 | 269
2018-03-29 12:30 | 271 | 270
2018-03-29 13:00 | 271 | 269
2018-03-29 13:30 | 272 | 271
2018-03-29 14:00 | 273 | 271
2018-03-29 14:30 | 277 | 275
2018-03-29 15:00 | 281 | 280
2018-03-29 15:30 | 280 | 279
2018-03-29 16:00 | 281 | 280
2018-03-29 16:30 | 287 | 287
2018-03-29 17:00 | 293 | 293
2018-03-29 17:30 | 294 | 294
2018-03-29 18:00 | 295 | 295
2018-03-29 18:30 | 299 | 298
2018-03-29 19:00 | 301 | 300
2018-03-29 19:30 | 293 | 292
2018-03-29 20:00 | 289 | 288
2018-03-29 20:30 | 283 | 282
2018-03-29 21:00 | 269 | 268
2018-03-29 21:30 | 257 | 257
2018-03-29 22:00 | 246 | 246
2018-03-29 22:30 | 240 | 240
2018-03-29 23:00 | 236 | 236
2018-03-29 23:30 | 221 | 221
2018-03-30 | 204 | 204
2018-03-30 00:30 | 189 | 188
2018-03-30 01:00 | 179 | 178
2018-03-30 01:30 | 173 | 172
2018-03-30 02:00 | 168 | 167
2018-03-30 02:30 | 165 | 164
2018-03-30 03:00 | 163 | 162
2018-03-30 03:30 | 162 | 160
2018-03-30 04:00 | 160 | 159
2018-03-30 04:30 | 159 | 158
2018-03-30 05:00 | 159 | 158
2018-03-30 05:30 | 161 | 160
2018-03-30 06:00 | 164 | 163
2018-03-30 06:30 | 169 | 167
2018-03-30 07:00 | 174 | 173
2018-03-30 07:30 | 179 | 179
2018-03-30 08:00 | 181 | 181
2018-03-30 08:30 | 188 | 188
2018-03-30 09:00 | 192 | 191
2018-03-30 09:30 | 194 | 194
2018-03-30 10:00 | 193 | 192
2018-03-30 10:30 | 199 | 199
2018-03-30 11:00 | 199 | 199
2018-03-30 11:30 | 192 | 192
2018-03-30 12:00 | 192 | 192
2018-03-30 12:30 | 196 | 196
2018-03-30 13:00 | 195 | 195
2018-03-30 13:30 | 195 | 195
2018-03-30 14:00 | 198 | 198
2018-03-30 14:30 | 208 | 208
2018-03-30 15:00 | 214 | 213
2018-03-30 15:30 | 216 | 216
2018-03-30 16:00 | 223 | 223
2018-03-30 16:30 | 230 | 230
2018-03-30 17:00 | 237 | 237
2018-03-30 17:30 | 242 | 242
2018-03-30 18:00 | 247 | 247
2018-03-30 18:30 | 256 | 256
2018-03-30 19:00 | 260 | 260
2018-03-30 19:30 | 252 | 252
2018-03-30 20:00 | 248 | 248
2018-03-30 20:30 | 243 | 243
2018-03-30 21:00 | 232 | 232
2018-03-30 21:30 | 226 | 226
2018-03-30 22:00 | 221 | 221
2018-03-30 22:30 | 218 | 218
2018-03-30 23:00 | 217 | 217
2018-03-30 23:30 | 205 | 205
2018-03-31 | 190 | 189
2018-03-31 00:30 | 176 | 175
2018-03-31 01:00 | 170 | 168
2018-03-31 01:30 | 165 | 163
2018-03-31 02:00 | 161 | 159
2018-03-31 02:30 | 159 | 158
2018-03-31 03:00 | 157 | 155
2018-03-31 03:30 | 156 | 154
2018-03-31 04:00 | 156 | 154
2018-03-31 04:30 | 156 | 154
2018-03-31 05:00 | 157 | 155
2018-03-31 05:30 | 160 | 159
2018-03-31 06:00 | 163 | 162
2018-03-31 06:30 | 167 | 166
2018-03-31 07:00 | 169 | 168
2018-03-31 07:30 | 174 | 173
2018-03-31 08:00 | 177 | 177
2018-03-31 08:30 | 183 | 183
2018-03-31 09:00 | 189 | 189
2018-03-31 09:30 | 195 | 195
2018-03-31 10:00 | 188 | 188
2018-03-31 10:30 | 182 | 182
2018-03-31 11:00 | 179 | 179
2018-03-31 11:30 | 178 | 178
2018-03-31 12:00 | 178 | 178
2018-03-31 12:30 | 178 | 178
2018-03-31 13:00 | 180 | 180
2018-03-31 13:30 | 185 | 185
2018-03-31 14:00 | 191 | 191
2018-03-31 14:30 | 198 | 198
2018-03-31 15:00 | 207 | 207
2018-03-31 15:30 | 215 | 215
2018-03-31 16:00 | 225 | 225
2018-03-31 16:30 | 233 | 233
2018-03-31 17:00 | 243 | 242
2018-03-31 17:30 | 244 | 244
2018-03-31 18:00 | 246 | 246
2018-03-31 18:30 | 253 | 253
2018-03-31 19:00 | 255 | 255
2018-03-31 19:30 | 247 | 247
2018-03-31 20:00 | 244 | 244
2018-03-31 20:30 | 239 | 239
2018-03-31 21:00 | 229 | 229
2018-03-31 21:30 | 223 | 223
2018-03-31 22:00 | 217 | 217
2018-03-31 22:30 | 215 | 215
2018-03-31 23:00 | 215 | 215
2018-03-31 23:30 | 202 | 202
2018-04-01 | 187 | 187
2018-04-01 00:30 | 174 | 174
2018-04-01 01:00 | 167 | 166
2018-04-01 01:30 | 164 | 162
2018-04-01 02:00 | 159 | 158
2018-04-01 02:30 | 157 | 156
2018-04-01 03:00 | 155 | 153
2018-04-01 03:30 | 154 | 152
2018-04-01 04:00 | 152 | 150
2018-04-01 04:30 | 151 | 149
2018-04-01 05:00 | 151 | 149
2018-04-01 05:30 | 155 | 153
2018-04-01 06:00 | 156 | 154
2018-04-01 06:30 | 159 | 157
2018-04-01 07:00 | 161 | 159
2018-04-01 07:30 | 165 | 164
2018-04-01 08:00 | 166 | 165
2018-04-01 08:30 | 168 | 168
2018-04-01 09:00 | 172 | 172
2018-04-01 09:30 | 183 | 183
2018-04-01 10:00 | 185 | 185
2018-04-01 10:30 | 184 | 184
2018-04-01 11:00 | 182 | 182
2018-04-01 11:30 | 181 | 181
2018-04-01 12:00 | 179 | 179
2018-04-01 12:30 | 176 | 176
2018-04-01 13:00 | 176 | 176
2018-04-01 13:30 | 180 | 180
2018-04-01 14:00 | 186 | 186
2018-04-01 14:30 | 195 | 195
2018-04-01 15:00 | 203 | 203
2018-04-01 15:30 | 212 | 212
2018-04-01 16:00 | 222 | 221
2018-04-01 16:30 | 230 | 229
2018-04-01 17:00 | 239 | 238
2018-04-01 17:30 | 242 | 241
2018-04-01 18:00 | 244 | 243
2018-04-01 18:30 | 252 | 252
2018-04-01 19:00 | 253 | 253
2018-04-01 19:30 | 247 | 246
2018-04-01 20:00 | 244 | 243
2018-04-01 20:30 | 240 | 240
2018-04-01 21:00 | 230 | 230
2018-04-01 21:30 | 224 | 224
2018-04-01 22:00 | 218 | 218
2018-04-01 22:30 | 216 | 216
2018-04-01 23:00 | 215 | 215
2018-04-01 23:30 | 203 | 203
2018-04-02 | 188 | 188
2018-04-02 00:30 | 175 | 175
2018-04-02 01:00 | 169 | 168
2018-04-02 01:30 | 164 | 163
2018-04-02 02:00 | 160 | 159
2018-04-02 02:30 | 158 | 156
2018-04-02 03:00 | 156 | 154
2018-04-02 03:30 | 155 | 154
2018-04-02 04:00 | 154 | 153
2018-04-02 04:30 | 154 | 153
2018-04-02 05:00 | 156 | 155
2018-04-02 05:30 | 159 | 158
2018-04-02 06:00 | 162 | 162
2018-04-02 06:30 | 167 | 166
2018-04-02 07:00 | 169 | 169
2018-04-02 07:30 | 175 | 175
2018-04-02 08:00 | 178 | 178
2018-04-02 08:30 | 182 | 182
2018-04-02 09:00 | 190 | 190
2018-04-02 09:30 | 197 | 196
2018-04-02 10:00 | 199 | 198
2018-04-02 10:30 | 197 | 196
2018-04-02 11:00 | 199 | 198
2018-04-02 11:30 | 200 | 200
2018-04-02 12:00 | 199 | 198
2018-04-02 12:30 | 198 | 197
2018-04-02 13:00 | 200 | 199
2018-04-02 13:30 | 202 | 201
2018-04-02 14:00 | 209 | 208
2018-04-02 14:30 | 214 | 213
2018-04-02 15:00 | 220 | 219
2018-04-02 15:30 | 229 | 227
2018-04-02 16:00 | 242 | 241
2018-04-02 16:30 | 255 | 255
2018-04-02 17:00 | 266 | 266
2018-04-02 17:30 | 271 | 270
2018-04-02 18:00 | 273 | 273
2018-04-02 18:30 | 279 | 279
2018-04-02 19:00 | 279 | 279
2018-04-02 19:30 | 269 | 268
2018-04-02 20:00 | 265 | 264
2018-04-02 20:30 | 255 | 255
2018-04-02 21:00 | 243 | 243
2018-04-02 21:30 | 233 | 233
2018-04-02 22:00 | 224 | 224
2018-04-02 22:30 | 219 | 219
2018-04-02 23:00 | 217 | 217
2018-04-02 23:30 | 204 | 204
2018-04-03 | 188 | 188
2018-04-03 00:30 | 174 | 174
2018-04-03 01:00 | 167 | 167
2018-04-03 01:30 | 161 | 161
2018-04-03 02:00 | 158 | 158
2018-04-03 02:30 | 156 | 156
2018-04-03 03:00 | 156 | 155
2018-04-03 03:30 | 155 | 155
2018-04-03 04:00 | 156 | 156
2018-04-03 04:30 | 160 | 160
2018-04-03 05:00 | 167 | 167
2018-04-03 05:30 | 179 | 179
2018-04-03 06:00 | 190 | 190
2018-04-03 06:30 | 209 | 209
2018-04-03 07:00 | 224 | 224
2018-04-03 07:30 | 234 | 233
2018-04-03 08:00 | 238 | 237
2018-04-03 08:30 | 250 | 249
2018-04-03 09:00 | 259 | 259
2018-04-03 09:30 | 253 | 252
2018-04-03 10:00 | 245 | 245
2018-04-03 10:30 | 239 | 239
2018-04-03 11:00 | 237 | 237
2018-04-03 11:30 | 234 | 233
2018-04-03 12:00 | 232 | 231
2018-04-03 12:30 | 234 | 233
2018-04-03 13:00 | 232 | 232
2018-04-03 13:30 | 238 | 237
2018-04-03 14:00 | 243 | 242
2018-04-03 14:30 | 248 | 247
2018-04-03 15:00 | 252 | 251
2018-04-03 15:30 | 261 | 260
2018-04-03 16:00 | 271 | 271
2018-04-03 16:30 | 280 | 280
2018-04-03 17:00 | 288 | 288
2018-04-03 17:30 | 290 | 290
2018-04-03 18:00 | 290 | 290
2018-04-03 18:30 | 295 | 295
2018-04-03 19:00 | 295 | 295
2018-04-03 19:30 | 285 | 285
2018-04-03 20:00 | 278 | 278
2018-04-03 20:30 | 272 | 272
2018-04-03 21:00 | 257 | 256
2018-04-03 21:30 | 246 | 246
2018-04-03 22:00 | 236 | 236
2018-04-03 22:30 | 228 | 227
2018-04-03 23:00 | 225 | 224
2018-04-03 23:30 | 212 | 211
2018-04-04 | 195 | 195
2018-04-04 00:30 | 180 | 180
2018-04-04 01:00 | 174 | 174
2018-04-04 01:30 | 169 | 169
2018-04-04 02:00 | 167 | 167
2018-04-04 02:30 | 165 | 165
2018-04-04 03:00 | 163 | 163
2018-04-04 03:30 | 163 | 163
2018-04-04 04:00 | 165 | 165
2018-04-04 04:30 | 168 | 168
2018-04-04 05:00 | 174 | 174
2018-04-04 05:30 | 185 | 185
2018-04-04 06:00 | 200 | 199
2018-04-04 06:30 | 216 | 215
2018-04-04 07:00 | 229 | 228
2018-04-04 07:30 | 247 | 245
2018-04-04 08:00 | 256 | 254
2018-04-04 08:30 | 265 | 265
2018-04-04 09:00 | 267 | 267
2018-04-04 09:30 | 265 | 265
2018-04-04 10:00 | 256 | 256
2018-04-04 10:30 | 247 | 247
2018-04-04 11:00 | 242 | 242
2018-04-04 11:30 | 247 | 246
2018-04-04 12:00 | 260 | 260
2018-04-04 12:30 | 252 | 251
2018-04-04 13:00 | 243 | 242
2018-04-04 13:30 | 244 | 244
2018-04-04 14:00 | 248 | 248
2018-04-04 14:30 | 252 | 252
2018-04-04 15:00 | 261 | 261
2018-04-04 15:30 | 263 | 262
2018-04-04 16:00 | 267 | 267
2018-04-04 16:30 | 273 | 273
2018-04-04 17:00 | 278 | 278
2018-04-04 17:30 | 280 | 280
2018-04-04 18:00 | 283 | 283
2018-04-04 18:30 | 289 | 289
2018-04-04 19:00 | 289 | 289
2018-04-04 19:30 | 280 | 280
2018-04-04 20:00 | 274 | 274
2018-04-04 20:30 | 267 | 267
2018-04-04 21:00 | 256 | 256
2018-04-04 21:30 | 247 | 247
2018-04-04 22:00 | 237 | 237
2018-04-04 22:30 | 233 | 233
2018-04-04 23:00 | 232 | 232
2018-04-04 23:30 | 218 | 218
2018-04-05 | 201 | 200
2018-04-05 00:30 | 186 | 185
2018-04-05 01:00 | 176 | 176
2018-04-05 01:30 | 171 | 171
2018-04-05 02:00 | 167 | 166
2018-04-05 02:30 | 163 | 163
2018-04-05 03:00 | 162 | 162
2018-04-05 03:30 | 161 | 161
2018-04-05 04:00 | 162 | 162
2018-04-05 04:30 | 166 | 166
2018-04-05 05:00 | 172 | 171
2018-04-05 05:30 | 183 | 182
2018-04-05 06:00 | 193 | 193
2018-04-05 06:30 | 208 | 207
2018-04-05 07:00 | 220 | 219
2018-04-05 07:30 | 235 | 235
2018-04-05 08:00 | 241 | 240
2018-04-05 08:30 | 240 | 239
2018-04-05 09:00 | 237 | 236
2018-04-05 09:30 | 236 | 235
2018-04-05 10:00 | 233 | 232
2018-04-05 10:30 | 227 | 227
2018-04-05 11:00 | 228 | 228
2018-04-05 11:30 | 233 | 232
2018-04-05 12:00 | 240 | 240
2018-04-05 12:30 | 237 | 237
2018-04-05 13:00 | 236 | 236
2018-04-05 13:30 | 246 | 246
2018-04-05 14:00 | 248 | 248
2018-04-05 14:30 | 258 | 258
2018-04-05 15:00 | 251 | 251
2018-04-05 15:30 | 254 | 254
2018-04-05 16:00 | 264 | 264
2018-04-05 16:30 | 268 | 267
2018-04-05 17:00 | 273 | 273
2018-04-05 17:30 | 277 | 277
2018-04-05 18:00 | 281 | 281
2018-04-05 18:30 | 286 | 286
2018-04-05 19:00 | 286 | 286
2018-04-05 19:30 | 275 | 275
2018-04-05 20:00 | 272 | 272
2018-04-05 20:30 | 266 | 266
2018-04-05 21:00 | 255 | 255
2018-04-05 21:30 | 244 | 244
2018-04-05 22:00 | 234 | 234
2018-04-05 22:30 | 225 | 224
2018-04-05 23:00 | 222 | 221
2018-04-05 23:30 | 209 | 208
2018-04-06 | 192 | 192
2018-04-06 00:30 | 176 | 176
2018-04-06 01:00 | 169 | 169
2018-04-06 01:30 | 164 | 164
2018-04-06 02:00 | 160 | 160
2018-04-06 02:30 | 157 | 157
2018-04-06 03:00 | 154 | 154
2018-04-06 03:30 | 155 | 155
2018-04-06 04:00 | 156 | 156
2018-04-06 04:30 | 158 | 158
2018-04-06 05:00 | 165 | 165
2018-04-06 05:30 | 176 | 176
2018-04-06 06:00 | 186 | 186
2018-04-06 06:30 | 202 | 201
2018-04-06 07:00 | 216 | 216
2018-04-06 07:30 | 224 | 224
2018-04-06 08:00 | 226 | 226
2018-04-06 08:30 | 225 | 225
2018-04-06 09:00 | 227 | 226
2018-04-06 09:30 | 228 | 228
2018-04-06 10:00 | 232 | 231
2018-04-06 10:30 | 228 | 227
2018-04-06 11:00 | 223 | 222
2018-04-06 11:30 | 217 | 217
2018-04-06 12:00 | 211 | 211
2018-04-06 12:30 | 209 | 208
2018-04-06 13:00 | 211 | 210
2018-04-06 13:30 | 217 | 216
2018-04-06 14:00 | 222 | 222
2018-04-06 14:30 | 230 | 230
2018-04-06 15:00 | 241 | 241
2018-04-06 15:30 | 252 | 252
2018-04-06 16:00 | 261 | 261
2018-04-06 16:30 | 269 | 269
2018-04-06 17:00 | 275 | 275
2018-04-06 17:30 | 274 | 274
2018-04-06 18:00 | 273 | 272
2018-04-06 18:30 | 277 | 276
2018-04-06 19:00 | 277 | 276
2018-04-06 19:30 | 269 | 268
2018-04-06 20:00 | 264 | 264
2018-04-06 20:30 | 258 | 258
2018-04-06 21:00 | 245 | 245
2018-04-06 21:30 | 237 | 237
2018-04-06 22:00 | 229 | 229
2018-04-06 22:30 | 224 | 224
2018-04-06 23:00 | 224 | 224
2018-04-06 23:30 | 211 | 211
2018-04-07 | 193 | 193
2018-04-07 00:30 | 179 | 179
2018-04-07 01:00 | 171 | 171
2018-04-07 01:30 | 165 | 165
2018-04-07 02:00 | 161 | 161
2018-04-07 02:30 | 157 | 157
2018-04-07 03:00 | 155 | 155
2018-04-07 03:30 | 153 | 153
2018-04-07 04:00 | 153 | 153
2018-04-07 04:30 | 154 | 153
2018-04-07 05:00 | 156 | 155
2018-04-07 05:30 | 160 | 160
2018-04-07 06:00 | 164 | 164
2018-04-07 06:30 | 169 | 168
2018-04-07 07:00 | 172 | 171
2018-04-07 07:30 | 177 | 177
2018-04-07 08:00 | 179 | 178
2018-04-07 08:30 | 179 | 179
2018-04-07 09:00 | 182 | 181
2018-04-07 09:30 | 186 | 186
2018-04-07 10:00 | 184 | 184
2018-04-07 10:30 | 181 | 180
2018-04-07 11:00 | 184 | 183
2018-04-07 11:30 | 180 | 180
2018-04-07 12:00 | 178 | 178
2018-04-07 12:30 | 179 | 179
2018-04-07 13:00 | 179 | 179
2018-04-07 13:30 | 182 | 182
2018-04-07 14:00 | 184 | 184
2018-04-07 14:30 | 192 | 192
2018-04-07 15:00 | 198 | 198
2018-04-07 15:30 | 206 | 206
2018-04-07 16:00 | 213 | 213
2018-04-07 16:30 | 223 | 223
2018-04-07 17:00 | 234 | 234
2018-04-07 17:30 | 235 | 235
2018-04-07 18:00 | 240 | 240
2018-04-07 18:30 | 250 | 250
2018-04-07 19:00 | 249 | 249
2018-04-07 19:30 | 241 | 240
2018-04-07 20:00 | 238 | 237
2018-04-07 20:30 | 234 | 233
2018-04-07 21:00 | 224 | 224
2018-04-07 21:30 | 218 | 217
2018-04-07 22:00 | 212 | 212
2018-04-07 22:30 | 211 | 210
2018-04-07 23:00 | 211 | 211
2018-04-07 23:30 | 198 | 198
2018-04-08 | 183 | 183
2018-04-08 00:30 | 169 | 169
2018-04-08 01:00 | 161 | 161
2018-04-08 01:30 | 156 | 156
2018-04-08 02:00 | 152 | 152
2018-04-08 02:30 | 149 | 149
2018-04-08 03:00 | 148 | 147
2018-04-08 03:30 | 145 | 145
2018-04-08 04:00 | 144 | 144
2018-04-08 04:30 | 144 | 144
2018-04-08 05:00 | 144 | 144
2018-04-08 05:30 | 148 | 148
2018-04-08 06:00 | 151 | 151
2018-04-08 06:30 | 154 | 154
2018-04-08 07:00 | 158 | 158
2018-04-08 07:30 | 163 | 163
2018-04-08 08:00 | 166 | 166
2018-04-08 08:30 | 171 | 170
2018-04-08 09:00 | 163 | 163
2018-04-08 09:30 | 160 | 159
2018-04-08 10:00 | 163 | 162
2018-04-08 10:30 | 168 | 168
2018-04-08 11:00 | 174 | 173
2018-04-08 11:30 | 172 | 172
2018-04-08 12:00 | 170 | 169
2018-04-08 12:30 | 164 | 164
2018-04-08 13:00 | 164 | 164
2018-04-08 13:30 | 168 | 168
2018-04-08 14:00 | 173 | 172
2018-04-08 14:30 | 181 | 180
2018-04-08 15:00 | 192 | 191
2018-04-08 15:30 | 201 | 200
2018-04-08 16:00 | 213 | 213
2018-04-08 16:30 | 224 | 223
2018-04-08 17:00 | 236 | 236
2018-04-08 17:30 | 243 | 243
2018-04-08 18:00 | 250 | 249
2018-04-08 18:30 | 262 | 262
2018-04-08 19:00 | 260 | 260
2018-04-08 19:30 | 251 | 251
2018-04-08 20:00 | 247 | 247
2018-04-08 20:30 | 242 | 242
2018-04-08 21:00 | 232 | 232
2018-04-08 21:30 | 222 | 222
2018-04-08 22:00 | 213 | 213
2018-04-08 22:30 | 210 | 210
2018-04-08 23:00 | 210 | 210
2018-04-08 23:30 | 199 | 199
2018-04-09 | 185 | 185
2018-04-09 00:30 | 172 | 172
2018-04-09 01:00 | 164 | 164
2018-04-09 01:30 | 160 | 160
2018-04-09 02:00 | 156 | 155
2018-04-09 02:30 | 154 | 153
2018-04-09 03:00 | 152 | 152
2018-04-09 03:30 | 152 | 152
2018-04-09 04:00 | 153 | 153
2018-04-09 04:30 | 157 | 157
2018-04-09 05:00 | 164 | 164
2018-04-09 05:30 | 176 | 176
2018-04-09 06:00 | 187 | 187
2018-04-09 06:30 | 203 | 203
2018-04-09 07:00 | 216 | 215
2018-04-09 07:30 | 222 | 221
2018-04-09 08:00 | 224 | 223
2018-04-09 08:30 | 224 | 223
2018-04-09 09:00 | 222 | 221
2018-04-09 09:30 | 221 | 220
2018-04-09 10:00 | 219 | 219
2018-04-09 10:30 | 223 | 223
2018-04-09 11:00 | 221 | 221
2018-04-09 11:30 | 218 | 218
2018-04-09 12:00 | 219 | 219
2018-04-09 12:30 | 222 | 222
2018-04-09 13:00 | 227 | 226
2018-04-09 13:30 | 233 | 232
2018-04-09 14:00 | 240 | 240
2018-04-09 14:30 | 249 | 249
2018-04-09 15:00 | 258 | 258
2018-04-09 15:30 | 269 | 269
2018-04-09 16:00 | 281 | 281
2018-04-09 16:30 | 290 | 290
2018-04-09 17:00 | 298 | 298
2018-04-09 17:30 | 298 | 298
2018-04-09 18:00 | 298 | 297
2018-04-09 18:30 | 300 | 300
2018-04-09 19:00 | 297 | 296
2018-04-09 19:30 | 284 | 284
2018-04-09 20:00 | 277 | 277
2018-04-09 20:30 | 271 | 271
2018-04-09 21:00 | 258 | 258
2018-04-09 21:30 | 246 | 246
2018-04-09 22:00 | 237 | 237
2018-04-09 22:30 | 230 | 230
2018-04-09 23:00 | 228 | 227
2018-04-09 23:30 | 214 | 214
2018-04-10 | 199 | 198
2018-04-10 00:30 | 182 | 182
2018-04-10 01:00 | 174 | 174
2018-04-10 01:30 | 168 | 168
2018-04-10 02:00 | 165 | 164
2018-04-10 02:30 | 162 | 162
2018-04-10 03:00 | 160 | 159
2018-04-10 03:30 | 161 | 160
2018-04-10 04:00 | 161 | 161
2018-04-10 04:30 | 164 | 164
2018-04-10 05:00 | 170 | 170
2018-04-10 05:30 | 181 | 181
2018-04-10 06:00 | 190 | 190
2018-04-10 06:30 | 206 | 206
2018-04-10 07:00 | 216 | 216
2018-04-10 07:30 | 223 | 223
2018-04-10 08:00 | 222 | 222
2018-04-10 08:30 | 222 | 222
2018-04-10 09:00 | 220 | 220
2018-04-10 09:30 | 218 | 217
2018-04-10 10:00 | 218 | 218
2018-04-10 10:30 | 221 | 221
2018-04-10 11:00 | 225 | 225
2018-04-10 11:30 | 230 | 230
2018-04-10 12:00 | 234 | 234
2018-04-10 12:30 | 235 | 234
2018-04-10 13:00 | 235 | 235
2018-04-10 13:30 | 240 | 240
2018-04-10 14:00 | 252 | 252
2018-04-10 14:30 | 261 | 261
2018-04-10 15:00 | 271 | 270
2018-04-10 15:30 | 276 | 276
2018-04-10 16:00 | 279 | 279
2018-04-10 16:30 | 283 | 283
2018-04-10 17:00 | 290 | 290
2018-04-10 17:30 | 289 | 289
2018-04-10 18:00 | 290 | 290
2018-04-10 18:30 | 294 | 294
2018-04-10 19:00 | 293 | 293
2018-04-10 19:30 | 283 | 283
2018-04-10 20:00 | 276 | 276
2018-04-10 20:30 | 271 | 271
2018-04-10 21:00 | 258 | 258
2018-04-10 21:30 | 247 | 247
2018-04-10 22:00 | 238 | 238
2018-04-10 22:30 | 233 | 232
2018-04-10 23:00 | 232 | 230
2018-04-10 23:30 | 216 | 215
2018-04-11 | 200 | 200
2018-04-11 00:30 | 185 | 185
2018-04-11 01:00 | 177 | 177
2018-04-11 01:30 | 172 | 172
2018-04-11 02:00 | 168 | 168
2018-04-11 02:30 | 164 | 164
2018-04-11 03:00 | 163 | 163
2018-04-11 03:30 | 163 | 163
2018-04-11 04:00 | 164 | 164
2018-04-11 04:30 | 168 | 168
2018-04-11 05:00 | 174 | 174
2018-04-11 05:30 | 184 | 183
2018-04-11 06:00 | 194 | 193
2018-04-11 06:30 | 208 | 208
2018-04-11 07:00 | 219 | 219
2018-04-11 07:30 | 231 | 231
2018-04-11 08:00 | 236 | 235
2018-04-11 08:30 | 237 | 237
2018-04-11 09:00 | 234 | 233
2018-04-11 09:30 | 229 | 228
2018-04-11 10:00 | 224 | 224
2018-04-11 10:30 | 223 | 223
2018-04-11 11:00 | 224 | 223
2018-04-11 11:30 | 219 | 219
2018-04-11 12:00 | 221 | 220
2018-04-11 12:30 | 220 | 220
2018-04-11 13:00 | 220 | 220
2018-04-11 13:30 | 222 | 221
2018-04-11 14:00 | 226 | 225
2018-04-11 14:30 | 233 | 232
2018-04-11 15:00 | 240 | 239
2018-04-11 15:30 | 250 | 249
2018-04-11 16:00 | 259 | 258
2018-04-11 16:30 | 265 | 264
2018-04-11 17:00 | 265 | 264
2018-04-11 17:30 | 264 | 263
2018-04-11 18:00 | 271 | 269
2018-04-11 18:30 | 280 | 277
2018-04-11 19:00 | 279 | 277
2018-04-11 19:30 | 272 | 269
2018-04-11 20:00 | 268 | 265
2018-04-11 20:30 | 263 | 261
2018-04-11 21:00 | 251 | 248
2018-04-11 21:30 | 239 | 237
2018-04-11 22:00 | 230 | 227
2018-04-11 22:30 | 222 | 221
2018-04-11 23:00 | 220 | 219
2018-04-11 23:30 | 207 | 206
2018-04-12 | 189 | 189
2018-04-12 00:30 | 176 | 176
2018-04-12 01:00 | 169 | 169
2018-04-12 01:30 | 164 | 164
2018-04-12 02:00 | 159 | 159
2018-04-12 02:30 | 157 | 157
2018-04-12 03:00 | 156 | 156
2018-04-12 03:30 | 156 | 155
2018-04-12 04:00 | 157 | 156
2018-04-12 04:30 | 160 | 160
2018-04-12 05:00 | 165 | 165
2018-04-12 05:30 | 178 | 178
2018-04-12 06:00 | 191 | 191
2018-04-12 06:30 | 206 | 205
2018-04-12 07:00 | 218 | 217
2018-04-12 07:30 | 226 | 226
2018-04-12 08:00 | 231 | 231
2018-04-12 08:30 | 232 | 232
2018-04-12 09:00 | 228 | 228
2018-04-12 09:30 | 226 | 225
2018-04-12 10:00 | 227 | 226
2018-04-12 10:30 | 229 | 229
2018-04-12 11:00 | 237 | 237
2018-04-12 11:30 | 238 | 238
2018-04-12 12:00 | 231 | 231
2018-04-12 12:30 | 230 | 230
2018-04-12 13:00 | 232 | 232
2018-04-12 13:30 | 234 | 234
2018-04-12 14:00 | 237 | 237
2018-04-12 14:30 | 243 | 243
2018-04-12 15:00 | 244 | 243
2018-04-12 15:30 | 251 | 251
2018-04-12 16:00 | 260 | 260
2018-04-12 16:30 | 261 | 261
2018-04-12 17:00 | 270 | 269
2018-04-12 17:30 | 274 | 274
2018-04-12 18:00 | 281 | 281
2018-04-12 18:30 | 284 | 284
2018-04-12 19:00 | 283 | 283
2018-04-12 19:30 | 274 | 274
2018-04-12 20:00 | 268 | 267
2018-04-12 20:30 | 263 | 262
2018-04-12 21:00 | 251 | 249
2018-04-12 21:30 | 237 | 236
2018-04-12 22:00 | 227 | 226
2018-04-12 22:30 | 223 | 222
2018-04-12 23:00 | 221 | 220
2018-04-12 23:30 | 209 | 208
2018-04-13 | 192 | 192
2018-04-13 00:30 | 177 | 177
2018-04-13 01:00 | 170 | 170
2018-04-13 01:30 | 164 | 164
2018-04-13 02:00 | 160 | 160
2018-04-13 02:30 | 154 | 154
2018-04-13 03:00 | 154 | 154
2018-04-13 03:30 | 154 | 154
2018-04-13 04:00 | 156 | 156
2018-04-13 04:30 | 158 | 158
2018-04-13 05:00 | 164 | 164
2018-04-13 05:30 | 176 | 176
2018-04-13 06:00 | 188 | 187
2018-04-13 06:30 | 204 | 204
2018-04-13 07:00 | 215 | 215
2018-04-13 07:30 | 226 | 225
2018-04-13 08:00 | 235 | 235
2018-04-13 08:30 | 235 | 235
2018-04-13 09:00 | 230 | 230
2018-04-13 09:30 | 228 | 228
2018-04-13 10:00 | 228 | 228
2018-04-13 10:30 | 226 | 226
2018-04-13 11:00 | 224 | 224
2018-04-13 11:30 | 221 | 221
2018-04-13 12:00 | 222 | 222
2018-04-13 12:30 | 218 | 218
2018-04-13 13:00 | 223 | 223
2018-04-13 13:30 | 232 | 232
2018-04-13 14:00 | 235 | 235
2018-04-13 14:30 | 234 | 234
2018-04-13 15:00 | 241 | 241
2018-04-13 15:30 | 249 | 249
2018-04-13 16:00 | 258 | 258
2018-04-13 16:30 | 270 | 270
2018-04-13 17:00 | 272 | 272
2018-04-13 17:30 | 270 | 270
2018-04-13 18:00 | 272 | 272
2018-04-13 18:30 | 274 | 274
2018-04-13 19:00 | 273 | 273
2018-04-13 19:30 | 265 | 265
2018-04-13 20:00 | 262 | 261
2018-04-13 20:30 | 257 | 257
2018-04-13 21:00 | 246 | 246
2018-04-13 21:30 | 237 | 237
2018-04-13 22:00 | 229 | 229
2018-04-13 22:30 | 226 | 226
2018-04-13 23:00 | 222 | 222
2018-04-13 23:30 | 208 | 208
2018-04-14 | 194 | 194
2018-04-14 00:30 | 179 | 179
2018-04-14 01:00 | 172 | 172
2018-04-14 01:30 | 166 | 166
2018-04-14 02:00 | 162 | 161
2018-04-14 02:30 | 157 | 156
2018-04-14 03:00 | 154 | 153
2018-04-14 03:30 | 151 | 151
2018-04-14 04:00 | 148 | 148
2018-04-14 04:30 | 150 | 149
2018-04-14 05:00 | 150 | 150
2018-04-14 05:30 | 153 | 153
2018-04-14 06:00 | 158 | 158
2018-04-14 06:30 | 167 | 167
2018-04-14 07:00 | 172 | 172
2018-04-14 07:30 | 175 | 175
2018-04-14 08:00 | 178 | 178
2018-04-14 08:30 | 190 | 189
2018-04-14 09:00 | 197 | 196
2018-04-14 09:30 | 213 | 212
2018-04-14 10:00 | 222 | 222
2018-04-14 10:30 | 221 | 221
2018-04-14 11:00 | 223 | 223
2018-04-14 11:30 | 223 | 223
2018-04-14 12:00 | 218 | 218
2018-04-14 12:30 | 202 | 202
2018-04-14 13:00 | 209 | 209
2018-04-14 13:30 | 212 | 212
2018-04-14 14:00 | 204 | 204
2018-04-14 14:30 | 185 | 185
2018-04-14 15:00 | 193 | 193
2018-04-14 15:30 | 201 | 201
2018-04-14 16:00 | 214 | 214
2018-04-14 16:30 | 224 | 224
2018-04-14 17:00 | 235 | 235
2018-04-14 17:30 | 240 | 240
2018-04-14 18:00 | 246 | 245
2018-04-14 18:30 | 252 | 251
2018-04-14 19:00 | 252 | 252
2018-04-14 19:30 | 244 | 244
2018-04-14 20:00 | 243 | 243
2018-04-14 20:30 | 243 | 243
2018-04-14 21:00 | 233 | 233
2018-04-14 21:30 | 225 | 225
2018-04-14 22:00 | 216 | 215
2018-04-14 22:30 | 214 | 213
2018-04-14 23:00 | 214 | 214
2018-04-14 23:30 | 205 | 204
2018-04-15 | 189 | 189
2018-04-15 00:30 | 174 | 174
2018-04-15 01:00 | 166 | 166
2018-04-15 01:30 | 161 | 161
2018-04-15 02:00 | 154 | 154
2018-04-15 02:30 | 150 | 149
2018-04-15 03:00 | 143 | 143
2018-04-15 03:30 | 141 | 140
2018-04-15 04:00 | 142 | 141
2018-04-15 04:30 | 142 | 142
2018-04-15 05:00 | 144 | 144
2018-04-15 05:30 | 148 | 148
2018-04-15 06:00 | 151 | 150
2018-04-15 06:30 | 158 | 157
2018-04-15 07:00 | 159 | 159
2018-04-15 07:30 | 162 | 162
2018-04-15 08:00 | 163 | 163
2018-04-15 08:30 | 166 | 166
2018-04-15 09:00 | 168 | 168
2018-04-15 09:30 | 168 | 167
2018-04-15 10:00 | 169 | 168
2018-04-15 10:30 | 168 | 167
2018-04-15 11:00 | 168 | 167
2018-04-15 11:30 | 171 | 170
2018-04-15 12:00 | 175 | 174
2018-04-15 12:30 | 180 | 178
2018-04-15 13:00 | 189 | 189
2018-04-15 13:30 | 200 | 200
2018-04-15 14:00 | 214 | 214
2018-04-15 14:30 | 229 | 228
2018-04-15 15:00 | 236 | 235
2018-04-15 15:30 | 247 | 247
2018-04-15 16:00 | 259 | 259
2018-04-15 16:30 | 268 | 268
2018-04-15 17:00 | 277 | 277
2018-04-15 17:30 | 280 | 280
2018-04-15 18:00 | 286 | 286
2018-04-15 18:30 | 294 | 294
2018-04-15 19:00 | 291 | 291
2018-04-15 19:30 | 279 | 279
2018-04-15 20:00 | 272 | 271
2018-04-15 20:30 | 265 | 264
2018-04-15 21:00 | 249 | 249
2018-04-15 21:30 | 238 | 237
2018-04-15 22:00 | 225 | 225
2018-04-15 22:30 | 223 | 223
2018-04-15 23:00 | 221 | 221
2018-04-15 23:30 | 207 | 207
2018-04-16 | 190 | 190
2018-04-16 00:30 | 175 | 175
2018-04-16 01:00 | 168 | 167
2018-04-16 01:30 | 159 | 159
2018-04-16 02:00 | 154 | 154
2018-04-16 02:30 | 154 | 154
2018-04-16 03:00 | 153 | 152
2018-04-16 03:30 | 152 | 152
2018-04-16 04:00 | 151 | 151
2018-04-16 04:30 | 155 | 155
2018-04-16 05:00 | 161 | 161
2018-04-16 05:30 | 173 | 173
2018-04-16 06:00 | 184 | 184
2018-04-16 06:30 | 200 | 200
2018-04-16 07:00 | 211 | 211
2018-04-16 07:30 | 219 | 218
2018-04-16 08:00 | 218 | 218
2018-04-16 08:30 | 218 | 217
2018-04-16 09:00 | 216 | 215
2018-04-16 09:30 | 215 | 215
2018-04-16 10:00 | 214 | 214
2018-04-16 10:30 | 214 | 213
2018-04-16 11:00 | 215 | 214
2018-04-16 11:30 | 216 | 215
2018-04-16 12:00 | 220 | 219
2018-04-16 12:30 | 223 | 222
2018-04-16 13:00 | 229 | 228
2018-04-16 13:30 | 237 | 236
2018-04-16 14:00 | 246 | 245
2018-04-16 14:30 | 257 | 256
2018-04-16 15:00 | 271 | 271
2018-04-16 15:30 | 283 | 283
2018-04-16 16:00 | 294 | 293
2018-04-16 16:30 | 302 | 302
2018-04-16 17:00 | 309 | 309
2018-04-16 17:30 | 307 | 307
2018-04-16 18:00 | 309 | 309
2018-04-16 18:30 | 309 | 309
2018-04-16 19:00 | 305 | 305
2018-04-16 19:30 | 294 | 294
2018-04-16 20:00 | 290 | 290
2018-04-16 20:30 | 281 | 281
2018-04-16 21:00 | 264 | 263
2018-04-16 21:30 | 251 | 251
2018-04-16 22:00 | 241 | 241
2018-04-16 22:30 | 232 | 232
2018-04-16 23:00 | 226 | 226
2018-04-16 23:30 | 212 | 212
2018-04-17 | 195 | 194
2018-04-17 00:30 | 178 | 178
2018-04-17 01:00 | 169 | 169
2018-04-17 01:30 | 163 | 163
2018-04-17 02:00 | 159 | 159
2018-04-17 02:30 | 156 | 156
2018-04-17 03:00 | 155 | 155
2018-04-17 03:30 | 155 | 155
2018-04-17 04:00 | 155 | 155
2018-04-17 04:30 | 159 | 159
2018-04-17 05:00 | 166 | 166
2018-04-17 05:30 | 178 | 178
2018-04-17 06:00 | 191 | 191
2018-04-17 06:30 | 209 | 208
2018-04-17 07:00 | 223 | 223
2018-04-17 07:30 | 230 | 230
2018-04-17 08:00 | 225 | 225
2018-04-17 08:30 | 219 | 219
2018-04-17 09:00 | 212 | 212
2018-04-17 09:30 | 210 | 210
2018-04-17 10:00 | 208 | 208
2018-04-17 10:30 | 208 | 207
2018-04-17 11:00 | 209 | 208
2018-04-17 11:30 | 210 | 209
2018-04-17 12:00 | 216 | 216
2018-04-17 12:30 | 221 | 221
2018-04-17 13:00 | 229 | 229
2018-04-17 13:30 | 238 | 238
2018-04-17 14:00 | 248 | 248
2018-04-17 14:30 | 258 | 258
2018-04-17 15:00 | 265 | 264
2018-04-17 15:30 | 273 | 273
2018-04-17 16:00 | 283 | 282
2018-04-17 16:30 | 291 | 291
2018-04-17 17:00 | 297 | 297
2018-04-17 17:30 | 296 | 296
2018-04-17 18:00 | 301 | 301
2018-04-17 18:30 | 301 | 301
2018-04-17 19:00 | 299 | 298
2018-04-17 19:30 | 287 | 287
2018-04-17 20:00 | 282 | 282
2018-04-17 20:30 | 275 | 274
2018-04-17 21:00 | 261 | 261
2018-04-17 21:30 | 250 | 250
2018-04-17 22:00 | 240 | 240
2018-04-17 22:30 | 231 | 231
2018-04-17 23:00 | 227 | 226
2018-04-17 23:30 | 212 | 212
2018-04-18 | 194 | 194
2018-04-18 00:30 | 180 | 180
2018-04-18 01:00 | 171 | 171
2018-04-18 01:30 | 167 | 167
2018-04-18 02:00 | 162 | 162
2018-04-18 02:30 | 161 | 161
2018-04-18 03:00 | 159 | 159
2018-04-18 03:30 | 158 | 158
2018-04-18 04:00 | 159 | 159
2018-04-18 04:30 | 162 | 162
2018-04-18 05:00 | 169 | 169
2018-04-18 05:30 | 182 | 182
2018-04-18 06:00 | 196 | 196
2018-04-18 06:30 | 215 | 215
2018-04-18 07:00 | 241 | 241
2018-04-18 07:30 | 272 | 271
2018-04-18 08:00 | 273 | 273
2018-04-18 08:30 | 269 | 269
2018-04-18 09:00 | 276 | 276
2018-04-18 09:30 | 279 | 279
2018-04-18 10:00 | 271 | 271
2018-04-18 10:30 | 266 | 266
2018-04-18 11:00 | 271 | 271
2018-04-18 11:30 | 268 | 268
2018-04-18 12:00 | 268 | 268
2018-04-18 12:30 | 263 | 263
2018-04-18 13:00 | 255 | 255
2018-04-18 13:30 | 250 | 250
2018-04-18 14:00 | 241 | 241
2018-04-18 14:30 | 241 | 241
2018-04-18 15:00 | 247 | 247
2018-04-18 15:30 | 255 | 255
2018-04-18 16:00 | 252 | 251
2018-04-18 16:30 | 262 | 262
2018-04-18 17:00 | 272 | 272
2018-04-18 17:30 | 275 | 275
2018-04-18 18:00 | 281 | 281
2018-04-18 18:30 | 281 | 281
2018-04-18 19:00 | 280 | 280
2018-04-18 19:30 | 271 | 270
2018-04-18 20:00 | 265 | 265
2018-04-18 20:30 | 258 | 257
2018-04-18 21:00 | 245 | 245
2018-04-18 21:30 | 236 | 236
2018-04-18 22:00 | 226 | 226
2018-04-18 22:30 | 220 | 220
2018-04-18 23:00 | 216 | 216
2018-04-18 23:30 | 203 | 203
2018-04-19 | 186 | 186
2018-04-19 00:30 | 171 | 171
2018-04-19 01:00 | 163 | 163
2018-04-19 01:30 | 158 | 158
2018-04-19 02:00 | 154 | 154
2018-04-19 02:30 | 152 | 152
2018-04-19 03:00 | 149 | 149
2018-04-19 03:30 | 150 | 149
2018-04-19 04:00 | 150 | 150
2018-04-19 04:30 | 155 | 155
2018-04-19 05:00 | 163 | 163
2018-04-19 05:30 | 176 | 176
2018-04-19 06:00 | 190 | 190
2018-04-19 06:30 | 210 | 210
2018-04-19 07:00 | 227 | 227
2018-04-19 07:30 | 235 | 235
2018-04-19 08:00 | 234 | 234
2018-04-19 08:30 | 229 | 228
2018-04-19 09:00 | 221 | 221
2018-04-19 09:30 | 211 | 211
2018-04-19 10:00 | 211 | 211
2018-04-19 10:30 | 217 | 217
2018-04-19 11:00 | 219 | 219
2018-04-19 11:30 | 214 | 213
2018-04-19 12:00 | 222 | 222
2018-04-19 12:30 | 231 | 230
2018-04-19 13:00 | 234 | 233
2018-04-19 13:30 | 235 | 234
2018-04-19 14:00 | 236 | 235
2018-04-19 14:30 | 239 | 238
2018-04-19 15:00 | 246 | 246
2018-04-19 15:30 | 255 | 255
2018-04-19 16:00 | 258 | 258
2018-04-19 16:30 | 267 | 267
2018-04-19 17:00 | 274 | 274
2018-04-19 17:30 | 277 | 277
2018-04-19 18:00 | 285 | 285
2018-04-19 18:30 | 285 | 285
2018-04-19 19:00 | 284 | 284
2018-04-19 19:30 | 275 | 275
2018-04-19 20:00 | 271 | 270
2018-04-19 20:30 | 266 | 266
2018-04-19 21:00 | 255 | 255
2018-04-19 21:30 | 241 | 241
2018-04-19 22:00 | 230 | 229
2018-04-19 22:30 | 223 | 223
2018-04-19 23:00 | 220 | 220
2018-04-19 23:30 | 206 | 206
2018-04-20 | 190 | 190
2018-04-20 00:30 | 175 | 175
2018-04-20 01:00 | 165 | 165
2018-04-20 01:30 | 160 | 159
2018-04-20 02:00 | 156 | 156
2018-04-20 02:30 | 154 | 154
2018-04-20 03:00 | 154 | 154
2018-04-20 03:30 | 155 | 154
2018-04-20 04:00 | 155 | 155
2018-04-20 04:30 | 160 | 160
2018-04-20 05:00 | 164 | 164
2018-04-20 05:30 | 176 | 176
2018-04-20 06:00 | 190 | 190
2018-04-20 06:30 | 208 | 208
2018-04-20 07:00 | 227 | 226
2018-04-20 07:30 | 238 | 237
2018-04-20 08:00 | 234 | 233
2018-04-20 08:30 | 232 | 231
2018-04-20 09:00 | 229 | 229
2018-04-20 09:30 | 229 | 229
2018-04-20 10:00 | 233 | 233
2018-04-20 10:30 | 234 | 234
2018-04-20 11:00 | 234 | 234
2018-04-20 11:30 | 237 | 237
2018-04-20 12:00 | 246 | 246
2018-04-20 12:30 | 252 | 252
2018-04-20 13:00 | 258 | 258
2018-04-20 13:30 | 262 | 262
2018-04-20 14:00 | 266 | 266
2018-04-20 14:30 | 267 | 267
2018-04-20 15:00 | 266 | 266
2018-04-20 15:30 | 268 | 267
2018-04-20 16:00 | 273 | 272
2018-04-20 16:30 | 275 | 274
2018-04-20 17:00 | 275 | 275
2018-04-20 17:30 | 272 | 272
2018-04-20 18:00 | 272 | 271
2018-04-20 18:30 | 266 | 266
2018-04-20 19:00 | 265 | 265
2018-04-20 19:30 | 257 | 257
2018-04-20 20:00 | 253 | 253
2018-04-20 20:30 | 249 | 249
2018-04-20 21:00 | 237 | 237
2018-04-20 21:30 | 227 | 226
2018-04-20 22:00 | 219 | 218
2018-04-20 22:30 | 215 | 215
2018-04-20 23:00 | 213 | 212
2018-04-20 23:30 | 200 | 200
2018-04-21 | 184 | 184
2018-04-21 00:30 | 170 | 170
2018-04-21 01:00 | 162 | 162
2018-04-21 01:30 | 157 | 156
2018-04-21 02:00 | 153 | 152
2018-04-21 02:30 | 149 | 149
2018-04-21 03:00 | 147 | 147
2018-04-21 03:30 | 147 | 146
2018-04-21 04:00 | 144 | 144
2018-04-21 04:30 | 143 | 143
2018-04-21 05:00 | 145 | 145
2018-04-21 05:30 | 150 | 150
2018-04-21 06:00 | 157 | 157
2018-04-21 06:30 | 165 | 165
2018-04-21 07:00 | 174 | 174
2018-04-21 07:30 | 181 | 181
2018-04-21 08:00 | 180 | 180
2018-04-21 08:30 | 179 | 178
2018-04-21 09:00 | 178 | 177
2018-04-21 09:30 | 176 | 174
2018-04-21 10:00 | 175 | 173
2018-04-21 10:30 | 177 | 175
2018-04-21 11:00 | 183 | 181
2018-04-21 11:30 | 182 | 180
2018-04-21 12:00 | 178 | 178
2018-04-21 12:30 | 180 | 179
2018-04-21 13:00 | 181 | 181
2018-04-21 13:30 | 188 | 188
2018-04-21 14:00 | 191 | 191
2018-04-21 14:30 | 197 | 197
2018-04-21 15:00 | 204 | 204
2018-04-21 15:30 | 206 | 206
2018-04-21 16:00 | 209 | 209
2018-04-21 16:30 | 217 | 217
2018-04-21 17:00 | 225 | 225
2018-04-21 17:30 | 227 | 227
2018-04-21 18:00 | 236 | 236
2018-04-21 18:30 | 239 | 238
2018-04-21 19:00 | 237 | 236
2018-04-21 19:30 | 228 | 228
2018-04-21 20:00 | 225 | 224
2018-04-21 20:30 | 223 | 222
2018-04-21 21:00 | 213 | 212
2018-04-21 21:30 | 205 | 205
2018-04-21 22:00 | 200 | 200
2018-04-21 22:30 | 198 | 198
2018-04-21 23:00 | 199 | 199
2018-04-21 23:30 | 191 | 191
2018-04-22 | 174 | 174
2018-04-22 00:30 | 160 | 160
2018-04-22 01:00 | 151 | 151
2018-04-22 01:30 | 144 | 143
2018-04-22 02:00 | 140 | 140
2018-04-22 02:30 | 138 | 138
2018-04-22 03:00 | 137 | 137
2018-04-22 03:30 | 135 | 135
2018-04-22 04:00 | 134 | 134
2018-04-22 04:30 | 134 | 134
2018-04-22 05:00 | 135 | 135
2018-04-22 05:30 | 139 | 139
2018-04-22 06:00 | 143 | 142
2018-04-22 06:30 | 147 | 146
2018-04-22 07:00 | 151 | 151
2018-04-22 07:30 | 153 | 153
2018-04-22 08:00 | 155 | 154
2018-04-22 08:30 | 160 | 159
2018-04-22 09:00 | 162 | 160
2018-04-22 09:30 | 177 | 175
2018-04-22 10:00 | 179 | 176
2018-04-22 10:30 | 172 | 170
2018-04-22 11:00 | 156 | 154
2018-04-22 11:30 | 173 | 170
2018-04-22 12:00 | 166 | 163
2018-04-22 12:30 | 156 | 153
2018-04-22 13:00 | 160 | 157
2018-04-22 13:30 | 164 | 161
2018-04-22 14:00 | 172 | 168
2018-04-22 14:30 | 172 | 169
2018-04-22 15:00 | 178 | 175
2018-04-22 15:30 | 190 | 186
2018-04-22 16:00 | 202 | 199
2018-04-22 16:30 | 216 | 212
2018-04-22 17:00 | 230 | 227
2018-04-22 17:30 | 239 | 238
2018-04-22 18:00 | 250 | 249
2018-04-22 18:30 | 251 | 251
2018-04-22 19:00 | 246 | 246
2018-04-22 19:30 | 237 | 237
2018-04-22 20:00 | 234 | 234
2018-04-22 20:30 | 231 | 231
2018-04-22 21:00 | 220 | 220
2018-04-22 21:30 | 210 | 208
2018-04-22 22:00 | 202 | 201
2018-04-22 22:30 | 198 | 196
2018-04-22 23:00 | 197 | 196
2018-04-22 23:30 | 186 | 185
2018-04-23 | 171 | 171
2018-04-23 00:30 | 158 | 157
2018-04-23 01:00 | 148 | 148
2018-04-23 01:30 | 143 | 143
2018-04-23 02:00 | 140 | 139
2018-04-23 02:30 | 137 | 137
2018-04-23 03:00 | 135 | 135
2018-04-23 03:30 | 137 | 137
2018-04-23 04:00 | 138 | 137
2018-04-23 04:30 | 143 | 142
2018-04-23 05:00 | 151 | 151
2018-04-23 05:30 | 166 | 165
2018-04-23 06:00 | 181 | 179
2018-04-23 06:30 | 201 | 200
2018-04-23 07:00 | 218 | 218
2018-04-23 07:30 | 229 | 228
2018-04-23 08:00 | 224 | 224
2018-04-23 08:30 | 215 | 215
2018-04-23 09:00 | 208 | 208
2018-04-23 09:30 | 202 | 202
2018-04-23 10:00 | 200 | 200
2018-04-23 10:30 | 199 | 199
2018-04-23 11:00 | 201 | 201
2018-04-23 11:30 | 207 | 207
2018-04-23 12:00 | 211 | 210
2018-04-23 12:30 | 214 | 214
2018-04-23 13:00 | 221 | 221
2018-04-23 13:30 | 230 | 230
2018-04-23 14:00 | 239 | 239
2018-04-23 14:30 | 245 | 245
2018-04-23 15:00 | 241 | 241
2018-04-23 15:30 | 241 | 241
2018-04-23 16:00 | 252 | 252
2018-04-23 16:30 | 260 | 260
2018-04-23 17:00 | 270 | 270
2018-04-23 17:30 | 277 | 277
2018-04-23 18:00 | 286 | 286
2018-04-23 18:30 | 284 | 284
2018-04-23 19:00 | 281 | 281
2018-04-23 19:30 | 270 | 270
2018-04-23 20:00 | 265 | 265
2018-04-23 20:30 | 261 | 260
2018-04-23 21:00 | 248 | 248
2018-04-23 21:30 | 237 | 237
2018-04-23 22:00 | 226 | 226
2018-04-23 22:30 | 219 | 217
2018-04-23 23:00 | 216 | 215
2018-04-23 23:30 | 202 | 202
2018-04-24 | 186 | 186
2018-04-24 00:30 | 171 | 171
2018-04-24 01:00 | 162 | 162
2018-04-24 01:30 | 158 | 157
2018-04-24 02:00 | 154 | 153
2018-04-24 02:30 | 150 | 150
2018-04-24 03:00 | 149 | 149
2018-04-24 03:30 | 150 | 150
2018-04-24 04:00 | 150 | 150
2018-04-24 04:30 | 155 | 155
2018-04-24 05:00 | 163 | 162
2018-04-24 05:30 | 176 | 176
2018-04-24 06:00 | 191 | 189
2018-04-24 06:30 | 211 | 209
2018-04-24 07:00 | 226 | 226
2018-04-24 07:30 | 233 | 232
2018-04-24 08:00 | 229 | 228
2018-04-24 08:30 | 221 | 220
2018-04-24 09:00 | 212 | 211
2018-04-24 09:30 | 207 | 206
2018-04-24 10:00 | 203 | 201
2018-04-24 10:30 | 199 | 197
2018-04-24 11:00 | 198 | 196
2018-04-24 11:30 | 196 | 195
2018-04-24 12:00 | 198 | 198
2018-04-24 12:30 | 206 | 206
2018-04-24 13:00 | 217 | 216
2018-04-24 13:30 | 225 | 224
2018-04-24 14:00 | 224 | 223
2018-04-24 14:30 | 227 | 227
2018-04-24 15:00 | 235 | 235
2018-04-24 15:30 | 244 | 243
2018-04-24 16:00 | 251 | 251
2018-04-24 16:30 | 258 | 258
2018-04-24 17:00 | 265 | 264
2018-04-24 17:30 | 269 | 269
2018-04-24 18:00 | 275 | 275
2018-04-24 18:30 | 272 | 272
2018-04-24 19:00 | 269 | 269
2018-04-24 19:30 | 262 | 262
2018-04-24 20:00 | 258 | 258
2018-04-24 20:30 | 254 | 253
2018-04-24 21:00 | 242 | 242
2018-04-24 21:30 | 232 | 232
2018-04-24 22:00 | 225 | 225
2018-04-24 22:30 | 219 | 218
2018-04-24 23:00 | 216 | 216
2018-04-24 23:30 | 202 | 202
2018-04-25 | 186 | 186
2018-04-25 00:30 | 170 | 170
2018-04-25 01:00 | 161 | 161
2018-04-25 01:30 | 156 | 156
2018-04-25 02:00 | 151 | 151
2018-04-25 02:30 | 148 | 148
2018-04-25 03:00 | 147 | 147
2018-04-25 03:30 | 146 | 146
2018-04-25 04:00 | 145 | 145
2018-04-25 04:30 | 145 | 145
2018-04-25 05:00 | 146 | 146
2018-04-25 05:30 | 147 | 147
2018-04-25 06:00 | 151 | 151
2018-04-25 06:30 | 157 | 157
2018-04-25 07:00 | 161 | 161
2018-04-25 07:30 | 164 | 164
2018-04-25 08:00 | 162 | 162
2018-04-25 08:30 | 161 | 161
2018-04-25 09:00 | 158 | 158
2018-04-25 09:30 | 156 | 156
2018-04-25 10:00 | 154 | 154
2018-04-25 10:30 | 152 | 152
2018-04-25 11:00 | 153 | 152
2018-04-25 11:30 | 154 | 152
2018-04-25 12:00 | 156 | 155
2018-04-25 12:30 | 160 | 158
2018-04-25 13:00 | 163 | 161
2018-04-25 13:30 | 170 | 168
2018-04-25 14:00 | 178 | 176
2018-04-25 14:30 | 183 | 181
2018-04-25 15:00 | 185 | 184
2018-04-25 15:30 | 188 | 186
2018-04-25 16:00 | 201 | 199
2018-04-25 16:30 | 214 | 211
2018-04-25 17:00 | 225 | 224
2018-04-25 17:30 | 234 | 234
2018-04-25 18:00 | 247 | 247
2018-04-25 18:30 | 250 | 249
2018-04-25 19:00 | 249 | 249
2018-04-25 19:30 | 241 | 241
2018-04-25 20:00 | 238 | 238
2018-04-25 20:30 | 235 | 235
2018-04-25 21:00 | 223 | 223
2018-04-25 21:30 | 212 | 211
2018-04-25 22:00 | 204 | 204
2018-04-25 22:30 | 201 | 201
2018-04-25 23:00 | 200 | 200
2018-04-25 23:30 | 188 | 188
2018-04-26 | 173 | 173
2018-04-26 00:30 | 162 | 162
2018-04-26 01:00 | 154 | 154
2018-04-26 01:30 | 150 | 150
2018-04-26 02:00 | 147 | 146
2018-04-26 02:30 | 145 | 145
2018-04-26 03:00 | 144 | 144
2018-04-26 03:30 | 142 | 142
2018-04-26 04:00 | 142 | 142
2018-04-26 04:30 | 146 | 146
2018-04-26 05:00 | 155 | 155
2018-04-26 05:30 | 170 | 170
2018-04-26 06:00 | 185 | 184
2018-04-26 06:30 | 205 | 204
2018-04-26 07:00 | 220 | 219
2018-04-26 07:30 | 232 | 231
2018-04-26 08:00 | 231 | 231
2018-04-26 08:30 | 223 | 223
2018-04-26 09:00 | 218 | 218
2018-04-26 09:30 | 216 | 216
2018-04-26 10:00 | 214 | 214
2018-04-26 10:30 | 212 | 212
2018-04-26 11:00 | 212 | 212
2018-04-26 11:30 | 212 | 212
2018-04-26 12:00 | 214 | 214
2018-04-26 12:30 | 216 | 216
2018-04-26 13:00 | 220 | 220
2018-04-26 13:30 | 223 | 223
2018-04-26 14:00 | 232 | 232
2018-04-26 14:30 | 236 | 236
2018-04-26 15:00 | 243 | 243
2018-04-26 15:30 | 250 | 250
2018-04-26 16:00 | 257 | 257
2018-04-26 16:30 | 266 | 266
2018-04-26 17:00 | 274 | 274
2018-04-26 17:30 | 276 | 276
2018-04-26 18:00 | 284 | 284
2018-04-26 18:30 | 283 | 283
2018-04-26 19:00 | 283 | 283
2018-04-26 19:30 | 275 | 275
2018-04-26 20:00 | 271 | 271
2018-04-26 20:30 | 267 | 267
2018-04-26 21:00 | 257 | 256
2018-04-26 21:30 | 240 | 240
2018-04-26 22:00 | 229 | 227
2018-04-26 22:30 | 222 | 221
2018-04-26 23:00 | 217 | 216
2018-04-26 23:30 | 204 | 203
2018-04-27 | 188 | 187
2018-04-27 00:30 | 173 | 173
2018-04-27 01:00 | 164 | 164
2018-04-27 01:30 | 158 | 158
2018-04-27 02:00 | 155 | 155
2018-04-27 02:30 | 153 | 153
2018-04-27 03:00 | 151 | 151
2018-04-27 03:30 | 151 | 151
2018-04-27 04:00 | 151 | 151
2018-04-27 04:30 | 155 | 155
2018-04-27 05:00 | 162 | 162
2018-04-27 05:30 | 174 | 174
2018-04-27 06:00 | 187 | 186
2018-04-27 06:30 | 207 | 206
2018-04-27 07:00 | 222 | 222
2018-04-27 07:30 | 234 | 234
2018-04-27 08:00 | 232 | 232
2018-04-27 08:30 | 226 | 225
2018-04-27 09:00 | 217 | 217
2018-04-27 09:30 | 210 | 210
2018-04-27 10:00 | 206 | 205
2018-04-27 10:30 | 204 | 204
2018-04-27 11:00 | 204 | 204
2018-04-27 11:30 | 205 | 205
2018-04-27 12:00 | 204 | 204
2018-04-27 12:30 | 209 | 209
2018-04-27 13:00 | 207 | 207
2018-04-27 13:30 | 210 | 210
2018-04-27 14:00 | 219 | 219
2018-04-27 14:30 | 225 | 225
2018-04-27 15:00 | 232 | 232
2018-04-27 15:30 | 241 | 241
2018-04-27 16:00 | 249 | 249
2018-04-27 16:30 | 251 | 251
2018-04-27 17:00 | 258 | 257
2018-04-27 17:30 | 261 | 261
2018-04-27 18:00 | 266 | 266
2018-04-27 18:30 | 263 | 263
2018-04-27 19:00 | 261 | 260
2018-04-27 19:30 | 253 | 252
2018-04-27 20:00 | 250 | 250
2018-04-27 20:30 | 247 | 246
2018-04-27 21:00 | 235 | 234
2018-04-27 21:30 | 224 | 223
2018-04-27 22:00 | 216 | 215
2018-04-27 22:30 | 211 | 210
2018-04-27 23:00 | 209 | 208
2018-04-27 23:30 | 197 | 197
2018-04-28 | 181 | 181
2018-04-28 00:30 | 166 | 166
2018-04-28 01:00 | 158 | 158
2018-04-28 01:30 | 153 | 153
2018-04-28 02:00 | 148 | 148
2018-04-28 02:30 | 145 | 145
2018-04-28 03:00 | 143 | 143
2018-04-28 03:30 | 142 | 142
2018-04-28 04:00 | 141 | 141
2018-04-28 04:30 | 142 | 142
2018-04-28 05:00 | 143 | 143
2018-04-28 05:30 | 148 | 148
2018-04-28 06:00 | 153 | 153
2018-04-28 06:30 | 161 | 161
2018-04-28 07:00 | 167 | 166
2018-04-28 07:30 | 173 | 173
2018-04-28 08:00 | 176 | 176
2018-04-28 08:30 | 180 | 179
2018-04-28 09:00 | 185 | 183
2018-04-28 09:30 | 180 | 179
2018-04-28 10:00 | 182 | 181
2018-04-28 10:30 | 192 | 190
2018-04-28 11:00 | 173 | 171
2018-04-28 11:30 | 157 | 155
2018-04-28 12:00 | 153 | 152
2018-04-28 12:30 | 158 | 157
2018-04-28 13:00 | 165 | 164
2018-04-28 13:30 | 161 | 159
2018-04-28 14:00 | 175 | 173
2018-04-28 14:30 | 182 | 181
2018-04-28 15:00 | 190 | 189
2018-04-28 15:30 | 193 | 191
2018-04-28 16:00 | 199 | 197
2018-04-28 16:30 | 206 | 205
2018-04-28 17:00 | 218 | 217
2018-04-28 17:30 | 227 | 227
2018-04-28 18:00 | 235 | 235
2018-04-28 18:30 | 236 | 236
2018-04-28 19:00 | 234 | 234
2018-04-28 19:30 | 227 | 227
2018-04-28 20:00 | 224 | 224
2018-04-28 20:30 | 221 | 221
2018-04-28 21:00 | 210 | 209
2018-04-28 21:30 | 203 | 202
2018-04-28 22:00 | 198 | 197
2018-04-28 22:30 | 197 | 197
2018-04-28 23:00 | 198 | 197
2018-04-28 23:30 | 188 | 187
2018-04-29 | 173 | 173
2018-04-29 00:30 | 160 | 160
2018-04-29 01:00 | 151 | 151
2018-04-29 01:30 | 146 | 146
2018-04-29 02:00 | 140 | 140
2018-04-29 02:30 | 138 | 138
2018-04-29 03:00 | 135 | 135
2018-04-29 03:30 | 135 | 135
2018-04-29 04:00 | 135 | 135
2018-04-29 04:30 | 134 | 134
2018-04-29 05:00 | 136 | 135
2018-04-29 05:30 | 137 | 137
2018-04-29 06:00 | 141 | 141
2018-04-29 06:30 | 146 | 146
2018-04-29 07:00 | 150 | 150
2018-04-29 07:30 | 153 | 152
2018-04-29 08:00 | 153 | 153
2018-04-29 08:30 | 154 | 154
2018-04-29 09:00 | 152 | 151
2018-04-29 09:30 | 149 | 148
2018-04-29 10:00 | 144 | 142
2018-04-29 10:30 | 143 | 141
2018-04-29 11:00 | 151 | 148
2018-04-29 11:30 | 159 | 157
2018-04-29 12:00 | 159 | 157
2018-04-29 12:30 | 153 | 151
2018-04-29 13:00 | 148 | 146
2018-04-29 13:30 | 149 | 147
2018-04-29 14:00 | 157 | 155
2018-04-29 14:30 | 168 | 166
2018-04-29 15:00 | 176 | 173
2018-04-29 15:30 | 183 | 181
2018-04-29 16:00 | 195 | 192
2018-04-29 16:30 | 205 | 203
2018-04-29 17:00 | 217 | 215
2018-04-29 17:30 | 230 | 228
2018-04-29 18:00 | 243 | 241
2018-04-29 18:30 | 245 | 243
2018-04-29 19:00 | 241 | 240
2018-04-29 19:30 | 231 | 231
2018-04-29 20:00 | 229 | 228
2018-04-29 20:30 | 226 | 225
2018-04-29 21:00 | 217 | 216
2018-04-29 21:30 | 210 | 209
2018-04-29 22:00 | 202 | 202
2018-04-29 22:30 | 197 | 197
2018-04-29 23:00 | 196 | 196
2018-04-29 23:30 | 186 | 186
2018-04-30 | 170 | 170
2018-04-30 00:30 | 158 | 158
2018-04-30 01:00 | 149 | 149
2018-04-30 01:30 | 144 | 144
2018-04-30 02:00 | 141 | 141
2018-04-30 02:30 | 139 | 139
2018-04-30 03:00 | 137 | 137
2018-04-30 03:30 | 139 | 139
2018-04-30 04:00 | 139 | 139
2018-04-30 04:30 | 143 | 143
2018-04-30 05:00 | 153 | 152
2018-04-30 05:30 | 166 | 166
2018-04-30 06:00 | 182 | 181
2018-04-30 06:30 | 203 | 203
2018-04-30 07:00 | 223 | 221
2018-04-30 07:30 | 231 | 230
2018-04-30 08:00 | 226 | 225
2018-04-30 08:30 | 215 | 214
2018-04-30 09:00 | 205 | 204
2018-04-30 09:30 | 198 | 197
2018-04-30 10:00 | 192 | 191
2018-04-30 10:30 | 190 | 189
2018-04-30 11:00 | 189 | 187
2018-04-30 11:30 | 193 | 191
2018-04-30 12:00 | 197 | 196
2018-04-30 12:30 | 196 | 194
2018-04-30 13:00 | 203 | 201
2018-04-30 13:30 | 213 | 211
2018-04-30 14:00 | 220 | 218
2018-04-30 14:30 | 228 | 226
2018-04-30 15:00 | 224 | 223
2018-04-30 15:30 | 220 | 219
2018-04-30 16:00 | 231 | 230
2018-04-30 16:30 | 243 | 242
2018-04-30 17:00 | 259 | 257
2018-04-30 17:30 | 268 | 267
2018-04-30 18:00 | 279 | 279
2018-04-30 18:30 | 278 | 278
2018-04-30 19:00 | 275 | 275
2018-04-30 19:30 | 266 | 266
2018-04-30 20:00 | 262 | 262
2018-04-30 20:30 | 258 | 258
2018-04-30 21:00 | 243 | 243
2018-04-30 21:30 | 231 | 230
2018-04-30 22:00 | 222 | 222
2018-04-30 22:30 | 215 | 215
2018-04-30 23:00 | 212 | 212
2018-04-30 23:30 | 199 | 199
2018-05-01 | 183 | 183
2018-05-01 00:30 | 167 | 167
2018-05-01 01:00 | 158 | 158
2018-05-01 01:30 | 153 | 153
2018-05-01 02:00 | 149 | 149
2018-05-01 02:30 | 147 | 147
2018-05-01 03:00 | 146 | 146
2018-05-01 03:30 | 146 | 146
2018-05-01 04:00 | 146 | 146
2018-05-01 04:30 | 150 | 150
2018-05-01 05:00 | 156 | 156
2018-05-01 05:30 | 170 | 170
2018-05-01 06:00 | 185 | 185
2018-05-01 06:30 | 206 | 206
2018-05-01 07:00 | 226 | 226
2018-05-01 07:30 | 238 | 238
2018-05-01 08:00 | 236 | 235
2018-05-01 08:30 | 230 | 230
2018-05-01 09:00 | 231 | 230
2018-05-01 09:30 | 225 | 225
2018-05-01 10:00 | 217 | 216
2018-05-01 10:30 | 220 | 220
2018-05-01 11:00 | 229 | 228
2018-05-01 11:30 | 234 | 234
2018-05-01 12:00 | 223 | 223
2018-05-01 12:30 | 219 | 218
2018-05-01 13:00 | 217 | 217
2018-05-01 13:30 | 225 | 224
2018-05-01 14:00 | 231 | 231
2018-05-01 14:30 | 230 | 230
2018-05-01 15:00 | 234 | 233
2018-05-01 15:30 | 243 | 243
2018-05-01 16:00 | 255 | 255
2018-05-01 16:30 | 267 | 266
2018-05-01 17:00 | 279 | 279
2018-05-01 17:30 | 290 | 290
2018-05-01 18:00 | 298 | 298
2018-05-01 18:30 | 295 | 295
2018-05-01 19:00 | 292 | 292
2018-05-01 19:30 | 284 | 284
2018-05-01 20:00 | 277 | 277
2018-05-01 20:30 | 274 | 273
2018-05-01 21:00 | 261 | 260
2018-05-01 21:30 | 249 | 249
2018-05-01 22:00 | 241 | 241
2018-05-01 22:30 | 232 | 232
2018-05-01 23:00 | 228 | 228
2018-05-01 23:30 | 214 | 214
2018-05-02 | 196 | 196
2018-05-02 00:30 | 181 | 181
2018-05-02 01:00 | 172 | 172
2018-05-02 01:30 | 167 | 167
2018-05-02 02:00 | 162 | 162
2018-05-02 02:30 | 161 | 161
2018-05-02 03:00 | 159 | 159
2018-05-02 03:30 | 160 | 160
2018-05-02 04:00 | 160 | 160
2018-05-02 04:30 | 165 | 165
2018-05-02 05:00 | 173 | 173
2018-05-02 05:30 | 187 | 187
2018-05-02 06:00 | 203 | 203
2018-05-02 06:30 | 226 | 225
2018-05-02 07:00 | 247 | 246
2018-05-02 07:30 | 262 | 261
2018-05-02 08:00 | 265 | 263
2018-05-02 08:30 | 259 | 258
2018-05-02 09:00 | 237 | 235
2018-05-02 09:30 | 226 | 225
2018-05-02 10:00 | 224 | 222
2018-05-02 10:30 | 246 | 244
2018-05-02 11:00 | 244 | 243
2018-05-02 11:30 | 231 | 231
2018-05-02 12:00 | 231 | 230
2018-05-02 12:30 | 228 | 227
2018-05-02 13:00 | 232 | 232
2018-05-02 13:30 | 241 | 240
2018-05-02 14:00 | 230 | 230
2018-05-02 14:30 | 237 | 236
2018-05-02 15:00 | 249 | 248
2018-05-02 15:30 | 253 | 253
2018-05-02 16:00 | 265 | 264
2018-05-02 16:30 | 276 | 275
2018-05-02 17:00 | 290 | 289
2018-05-02 17:30 | 297 | 297
2018-05-02 18:00 | 302 | 302
2018-05-02 18:30 | 300 | 299
2018-05-02 19:00 | 296 | 295
2018-05-02 19:30 | 287 | 287
2018-05-02 20:00 | 282 | 282
2018-05-02 20:30 | 279 | 279
2018-05-02 21:00 | 265 | 265
2018-05-02 21:30 | 251 | 250
2018-05-02 22:00 | 243 | 242
2018-05-02 22:30 | 234 | 234
2018-05-02 23:00 | 229 | 229
2018-05-02 23:30 | 218 | 218
2018-05-03 | 202 | 202
2018-05-03 00:30 | 185 | 185
2018-05-03 01:00 | 177 | 177
2018-05-03 01:30 | 171 | 171
2018-05-03 02:00 | 166 | 166
2018-05-03 02:30 | 164 | 163
2018-05-03 03:00 | 164 | 164
2018-05-03 03:30 | 162 | 162
2018-05-03 04:00 | 162 | 162
2018-05-03 04:30 | 166 | 165
2018-05-03 05:00 | 174 | 174
2018-05-03 05:30 | 188 | 188
2018-05-03 06:00 | 202 | 202
2018-05-03 06:30 | 223 | 222
2018-05-03 07:00 | 241 | 240
2018-05-03 07:30 | 253 | 253
2018-05-03 08:00 | 253 | 253
2018-05-03 08:30 | 247 | 247
2018-05-03 09:00 | 236 | 236
2018-05-03 09:30 | 232 | 232
2018-05-03 10:00 | 231 | 231
2018-05-03 10:30 | 228 | 228
2018-05-03 11:00 | 232 | 231
2018-05-03 11:30 | 233 | 232
2018-05-03 12:00 | 238 | 237
2018-05-03 12:30 | 245 | 245
2018-05-03 13:00 | 245 | 244
2018-05-03 13:30 | 247 | 247
2018-05-03 14:00 | 251 | 250
2018-05-03 14:30 | 254 | 254
2018-05-03 15:00 | 264 | 263
2018-05-03 15:30 | 263 | 263
2018-05-03 16:00 | 267 | 267
2018-05-03 16:30 | 273 | 273
2018-05-03 17:00 | 285 | 285
2018-05-03 17:30 | 295 | 295
2018-05-03 18:00 | 307 | 307
2018-05-03 18:30 | 302 | 302
2018-05-03 19:00 | 300 | 299
2018-05-03 19:30 | 289 | 289
2018-05-03 20:00 | 286 | 286
2018-05-03 20:30 | 279 | 279
2018-05-03 21:00 | 264 | 262
2018-05-03 21:30 | 251 | 249
2018-05-03 22:00 | 239 | 238
2018-05-03 22:30 | 232 | 231
2018-05-03 23:00 | 230 | 229
2018-05-03 23:30 | 217 | 216
2018-05-04 | 199 | 199
2018-05-04 00:30 | 183 | 183
2018-05-04 01:00 | 172 | 172
2018-05-04 01:30 | 166 | 166
2018-05-04 02:00 | 162 | 162
2018-05-04 02:30 | 160 | 160
2018-05-04 03:00 | 159 | 159
2018-05-04 03:30 | 159 | 159
2018-05-04 04:00 | 160 | 159
2018-05-04 04:30 | 165 | 165
2018-05-04 05:00 | 172 | 172
2018-05-04 05:30 | 186 | 186
2018-05-04 06:00 | 200 | 200
2018-05-04 06:30 | 220 | 219
2018-05-04 07:00 | 241 | 241
2018-05-04 07:30 | 253 | 253
2018-05-04 08:00 | 250 | 250
2018-05-04 08:30 | 243 | 243
2018-05-04 09:00 | 232 | 232
2018-05-04 09:30 | 225 | 225
2018-05-04 10:00 | 219 | 218
2018-05-04 10:30 | 217 | 216
2018-05-04 11:00 | 216 | 215
2018-05-04 11:30 | 219 | 219
2018-05-04 12:00 | 225 | 225
2018-05-04 12:30 | 222 | 221
2018-05-04 13:00 | 224 | 224
2018-05-04 13:30 | 226 | 225
2018-05-04 14:00 | 235 | 235
2018-05-04 14:30 | 243 | 243
2018-05-04 15:00 | 249 | 249
2018-05-04 15:30 | 257 | 257
2018-05-04 16:00 | 269 | 269
2018-05-04 16:30 | 277 | 277
2018-05-04 17:00 | 284 | 284
2018-05-04 17:30 | 287 | 287
2018-05-04 18:00 | 290 | 290
2018-05-04 18:30 | 283 | 283
2018-05-04 19:00 | 280 | 280
2018-05-04 19:30 | 273 | 273
2018-05-04 20:00 | 269 | 269
2018-05-04 20:30 | 266 | 266
2018-05-04 21:00 | 255 | 255
2018-05-04 21:30 | 245 | 245
2018-05-04 22:00 | 236 | 235
2018-05-04 22:30 | 231 | 231
2018-05-04 23:00 | 230 | 229
2018-05-04 23:30 | 215 | 215
2018-05-05 | 196 | 196
2018-05-05 00:30 | 181 | 181
2018-05-05 01:00 | 173 | 173
2018-05-05 01:30 | 167 | 167
2018-05-05 02:00 | 161 | 161
2018-05-05 02:30 | 158 | 157
2018-05-05 03:00 | 157 | 156
2018-05-05 03:30 | 156 | 155
2018-05-05 04:00 | 155 | 155
2018-05-05 04:30 | 156 | 156
2018-05-05 05:00 | 157 | 157
2018-05-05 05:30 | 162 | 162
2018-05-05 06:00 | 168 | 168
2018-05-05 06:30 | 176 | 176
2018-05-05 07:00 | 182 | 182
2018-05-05 07:30 | 189 | 189
2018-05-05 08:00 | 192 | 191
2018-05-05 08:30 | 193 | 192
2018-05-05 09:00 | 192 | 191
2018-05-05 09:30 | 189 | 188
2018-05-05 10:00 | 184 | 184
2018-05-05 10:30 | 182 | 182
2018-05-05 11:00 | 180 | 179
2018-05-05 11:30 | 175 | 175
2018-05-05 12:00 | 175 | 175
2018-05-05 12:30 | 172 | 172
2018-05-05 13:00 | 172 | 171
2018-05-05 13:30 | 177 | 176
2018-05-05 14:00 | 184 | 184
2018-05-05 14:30 | 192 | 192
2018-05-05 15:00 | 202 | 202
2018-05-05 15:30 | 208 | 208
2018-05-05 16:00 | 219 | 219
2018-05-05 16:30 | 229 | 229
2018-05-05 17:00 | 241 | 241
2018-05-05 17:30 | 246 | 245
2018-05-05 18:00 | 253 | 252
2018-05-05 18:30 | 250 | 249
2018-05-05 19:00 | 247 | 247
2018-05-05 19:30 | 240 | 240
2018-05-05 20:00 | 237 | 237
2018-05-05 20:30 | 236 | 235
2018-05-05 21:00 | 226 | 225
2018-05-05 21:30 | 219 | 219
2018-05-05 22:00 | 213 | 213
2018-05-05 22:30 | 212 | 211
2018-05-05 23:00 | 212 | 212
2018-05-05 23:30 | 202 | 202
2018-05-06 | 187 | 187
2018-05-06 00:30 | 173 | 173
2018-05-06 01:00 | 164 | 163
2018-05-06 01:30 | 158 | 157
2018-05-06 02:00 | 152 | 152
2018-05-06 02:30 | 150 | 150
2018-05-06 03:00 | 149 | 149
2018-05-06 03:30 | 147 | 147
2018-05-06 04:00 | 147 | 147
2018-05-06 04:30 | 147 | 146
2018-05-06 05:00 | 147 | 147
2018-05-06 05:30 | 151 | 151
2018-05-06 06:00 | 155 | 155
2018-05-06 06:30 | 160 | 160
2018-05-06 07:00 | 163 | 163
2018-05-06 07:30 | 167 | 167
2018-05-06 08:00 | 167 | 167
2018-05-06 08:30 | 167 | 167
2018-05-06 09:00 | 165 | 165
2018-05-06 09:30 | 161 | 161
2018-05-06 10:00 | 157 | 157
2018-05-06 10:30 | 154 | 154
2018-05-06 11:00 | 148 | 148
2018-05-06 11:30 | 145 | 144
2018-05-06 12:00 | 146 | 145
2018-05-06 12:30 | 148 | 147
2018-05-06 13:00 | 151 | 150
2018-05-06 13:30 | 156 | 155
2018-05-06 14:00 | 159 | 158
2018-05-06 14:30 | 167 | 166
2018-05-06 15:00 | 174 | 173
2018-05-06 15:30 | 179 | 178
2018-05-06 16:00 | 190 | 188
2018-05-06 16:30 | 200 | 199
2018-05-06 17:00 | 212 | 211
2018-05-06 17:30 | 222 | 221
2018-05-06 18:00 | 232 | 231
2018-05-06 18:30 | 232 | 230
2018-05-06 19:00 | 229 | 228
2018-05-06 19:30 | 221 | 220
2018-05-06 20:00 | 218 | 218
2018-05-06 20:30 | 216 | 216
2018-05-06 21:00 | 206 | 206
2018-05-06 21:30 | 201 | 201
2018-05-06 22:00 | 196 | 196
2018-05-06 22:30 | 196 | 196
2018-05-06 23:00 | 197 | 197
2018-05-06 23:30 | 188 | 188
2018-05-07 | 173 | 173
2018-05-07 00:30 | 159 | 159
2018-05-07 01:00 | 153 | 152
2018-05-07 01:30 | 147 | 147
2018-05-07 02:00 | 143 | 143
2018-05-07 02:30 | 139 | 139
2018-05-07 03:00 | 139 | 139
2018-05-07 03:30 | 138 | 138
2018-05-07 04:00 | 136 | 136
2018-05-07 04:30 | 134 | 134
2018-05-07 05:00 | 137 | 137
2018-05-07 05:30 | 142 | 142
2018-05-07 06:00 | 148 | 147
2018-05-07 06:30 | 154 | 153
2018-05-07 07:00 | 157 | 156
2018-05-07 07:30 | 162 | 162
2018-05-07 08:00 | 169 | 168
2018-05-07 08:30 | 176 | 175
2018-05-07 09:00 | 177 | 176
2018-05-07 09:30 | 180 | 178
2018-05-07 10:00 | 188 | 187
2018-05-07 10:30 | 177 | 177
2018-05-07 11:00 | 180 | 180
2018-05-07 11:30 | 185 | 185
2018-05-07 12:00 | 186 | 185
2018-05-07 12:30 | 186 | 186
2018-05-07 13:00 | 186 | 186
2018-05-07 13:30 | 191 | 191
2018-05-07 14:00 | 202 | 202
2018-05-07 14:30 | 209 | 209
2018-05-07 15:00 | 210 | 210
2018-05-07 15:30 | 214 | 213
2018-05-07 16:00 | 221 | 221
2018-05-07 16:30 | 229 | 228
2018-05-07 17:00 | 242 | 242
2018-05-07 17:30 | 256 | 256
2018-05-07 18:00 | 259 | 259
2018-05-07 18:30 | 254 | 254
2018-05-07 19:00 | 249 | 249
2018-05-07 19:30 | 243 | 243
2018-05-07 20:00 | 240 | 240
2018-05-07 20:30 | 238 | 238
2018-05-07 21:00 | 227 | 225
2018-05-07 21:30 | 217 | 214
2018-05-07 22:00 | 209 | 207
2018-05-07 22:30 | 203 | 202
2018-05-07 23:00 | 202 | 201
2018-05-07 23:30 | 190 | 189
2018-05-08 | 174 | 173
2018-05-08 00:30 | 162 | 161
2018-05-08 01:00 | 155 | 155
2018-05-08 01:30 | 149 | 149
2018-05-08 02:00 | 145 | 145
2018-05-08 02:30 | 143 | 143
2018-05-08 03:00 | 141 | 141
2018-05-08 03:30 | 142 | 142
2018-05-08 04:00 | 144 | 144
2018-05-08 04:30 | 150 | 150
2018-05-08 05:00 | 158 | 158
2018-05-08 05:30 | 172 | 171
2018-05-08 06:00 | 188 | 186
2018-05-08 06:30 | 213 | 212
2018-05-08 07:00 | 234 | 233
2018-05-08 07:30 | 251 | 249
2018-05-08 08:00 | 255 | 253
2018-05-08 08:30 | 265 | 263
2018-05-08 09:00 | 262 | 260
2018-05-08 09:30 | 260 | 260
2018-05-08 10:00 | 258 | 257
2018-05-08 10:30 | 257 | 256
2018-05-08 11:00 | 262 | 261
2018-05-08 11:30 | 257 | 256
2018-05-08 12:00 | 252 | 251
2018-05-08 12:30 | 257 | 255
2018-05-08 13:00 | 257 | 256
2018-05-08 13:30 | 264 | 263
2018-05-08 14:00 | 270 | 268
2018-05-08 14:30 | 275 | 274
2018-05-08 15:00 | 272 | 271
2018-05-08 15:30 | 263 | 263
2018-05-08 16:00 | 260 | 259
2018-05-08 16:30 | 267 | 266
2018-05-08 17:00 | 277 | 277
2018-05-08 17:30 | 289 | 287
2018-05-08 18:00 | 293 | 291
2018-05-08 18:30 | 287 | 286
2018-05-08 19:00 | 285 | 284
2018-05-08 19:30 | 276 | 274
2018-05-08 20:00 | 273 | 271
2018-05-08 20:30 | 269 | 267
2018-05-08 21:00 | 254 | 253
2018-05-08 21:30 | 241 | 240
2018-05-08 22:00 | 231 | 231
2018-05-08 22:30 | 224 | 222
2018-05-08 23:00 | 221 | 217
2018-05-08 23:30 | 208 | 206
2018-05-09 | 192 | 190
2018-05-09 00:30 | 175 | 173
2018-05-09 01:00 | 166 | 165
2018-05-09 01:30 | 159 | 159
2018-05-09 02:00 | 156 | 155
2018-05-09 02:30 | 154 | 153
2018-05-09 03:00 | 152 | 152
2018-05-09 03:30 | 152 | 152
2018-05-09 04:00 | 153 | 152
2018-05-09 04:30 | 157 | 157
2018-05-09 05:00 | 166 | 165
2018-05-09 05:30 | 179 | 177
2018-05-09 06:00 | 194 | 194
2018-05-09 06:30 | 216 | 216
2018-05-09 07:00 | 235 | 235
2018-05-09 07:30 | 243 | 243
2018-05-09 08:00 | 241 | 241
2018-05-09 08:30 | 229 | 228
2018-05-09 09:00 | 214 | 214
2018-05-09 09:30 | 206 | 206
2018-05-09 10:00 | 200 | 200
2018-05-09 10:30 | 196 | 196
2018-05-09 11:00 | 193 | 193
2018-05-09 11:30 | 190 | 190
2018-05-09 12:00 | 194 | 194
2018-05-09 12:30 | 196 | 196
2018-05-09 13:00 | 198 | 198
2018-05-09 13:30 | 203 | 203
2018-05-09 14:00 | 212 | 211
2018-05-09 14:30 | 225 | 225
2018-05-09 15:00 | 231 | 231
2018-05-09 15:30 | 240 | 240
2018-05-09 16:00 | 253 | 253
2018-05-09 16:30 | 263 | 263
2018-05-09 17:00 | 274 | 274
2018-05-09 17:30 | 282 | 281
2018-05-09 18:00 | 290 | 290
2018-05-09 18:30 | 286 | 285
2018-05-09 19:00 | 283 | 282
2018-05-09 19:30 | 273 | 273
2018-05-09 20:00 | 271 | 271
2018-05-09 20:30 | 269 | 268
2018-05-09 21:00 | 255 | 255
2018-05-09 21:30 | 242 | 241
2018-05-09 22:00 | 230 | 228
2018-05-09 22:30 | 223 | 221
2018-05-09 23:00 | 219 | 217
2018-05-09 23:30 | 207 | 206
2018-05-10 | 189 | 188
2018-05-10 00:30 | 172 | 172
2018-05-10 01:00 | 164 | 164
2018-05-10 01:30 | 159 | 159
2018-05-10 02:00 | 155 | 155
2018-05-10 02:30 | 154 | 154
2018-05-10 03:00 | 152 | 152
2018-05-10 03:30 | 152 | 152
2018-05-10 04:00 | 152 | 152
2018-05-10 04:30 | 157 | 157
2018-05-10 05:00 | 164 | 164
2018-05-10 05:30 | 179 | 178
2018-05-10 06:00 | 193 | 192
2018-05-10 06:30 | 212 | 211
2018-05-10 07:00 | 230 | 229
2018-05-10 07:30 | 235 | 235
2018-05-10 08:00 | 195 | 195
2018-05-10 08:30 | 187 | 187
2018-05-10 09:00 | 177 | 177
2018-05-10 09:30 | 171 | 171
2018-05-10 10:00 | 167 | 166
2018-05-10 10:30 | 162 | 162
2018-05-10 11:00 | 159 | 159
2018-05-10 11:30 | 157 | 157
2018-05-10 12:00 | 158 | 158
2018-05-10 12:30 | 160 | 160
2018-05-10 13:00 | 163 | 163
2018-05-10 13:30 | 168 | 168
2018-05-10 14:00 | 173 | 173
2018-05-10 14:30 | 180 | 180
2018-05-10 15:00 | 226 | 225
2018-05-10 15:30 | 235 | 235
2018-05-10 16:00 | 247 | 247
2018-05-10 16:30 | 258 | 258
2018-05-10 17:00 | 268 | 267
2018-05-10 17:30 | 275 | 275
2018-05-10 18:00 | 287 | 286
2018-05-10 18:30 | 284 | 283
2018-05-10 19:00 | 282 | 282
2018-05-10 19:30 | 275 | 275
2018-05-10 20:00 | 272 | 272
2018-05-10 20:30 | 270 | 270
2018-05-10 21:00 | 259 | 259
2018-05-10 21:30 | 244 | 243
2018-05-10 22:00 | 232 | 232
2018-05-10 22:30 | 225 | 225
2018-05-10 23:00 | 221 | 221
2018-05-10 23:30 | 208 | 208
2018-05-11 | 191 | 190
2018-05-11 00:30 | 175 | 175
2018-05-11 01:00 | 164 | 164
2018-05-11 01:30 | 159 | 159
2018-05-11 02:00 | 155 | 155
2018-05-11 02:30 | 152 | 152
2018-05-11 03:00 | 151 | 151
2018-05-11 03:30 | 152 | 151
2018-05-11 04:00 | 152 | 152
2018-05-11 04:30 | 157 | 157
2018-05-11 05:00 | 163 | 163
2018-05-11 05:30 | 176 | 176
2018-05-11 06:00 | 190 | 190
2018-05-11 06:30 | 210 | 209
2018-05-11 07:00 | 229 | 228
2018-05-11 07:30 | 239 | 239
2018-05-11 08:00 | 234 | 234
2018-05-11 08:30 | 224 | 224
2018-05-11 09:00 | 215 | 215
2018-05-11 09:30 | 204 | 204
2018-05-11 10:00 | 194 | 193
2018-05-11 10:30 | 188 | 187
2018-05-11 11:00 | 182 | 182
2018-05-11 11:30 | 178 | 177
2018-05-11 12:00 | 177 | 177
2018-05-11 12:30 | 176 | 175
2018-05-11 13:00 | 177 | 177
2018-05-11 13:30 | 179 | 179
2018-05-11 14:00 | 185 | 185
2018-05-11 14:30 | 194 | 194
2018-05-11 15:00 | 201 | 201
2018-05-11 15:30 | 212 | 212
2018-05-11 16:00 | 226 | 226
2018-05-11 16:30 | 241 | 240
2018-05-11 17:00 | 253 | 253
2018-05-11 17:30 | 262 | 261
2018-05-11 18:00 | 269 | 269
2018-05-11 18:30 | 264 | 264
2018-05-11 19:00 | 265 | 264
2018-05-11 19:30 | 260 | 259
2018-05-11 20:00 | 260 | 259
2018-05-11 20:30 | 260 | 258
2018-05-11 21:00 | 249 | 248
2018-05-11 21:30 | 240 | 239
2018-05-11 22:00 | 233 | 232
2018-05-11 22:30 | 226 | 226
2018-05-11 23:00 | 223 | 223
2018-05-11 23:30 | 211 | 211
2018-05-12 | 194 | 194
2018-05-12 00:30 | 179 | 179
2018-05-12 01:00 | 172 | 172
2018-05-12 01:30 | 165 | 165
2018-05-12 02:00 | 160 | 159
2018-05-12 02:30 | 156 | 155
2018-05-12 03:00 | 154 | 154
2018-05-12 03:30 | 154 | 154
2018-05-12 04:00 | 154 | 154
2018-05-12 04:30 | 155 | 154
2018-05-12 05:00 | 157 | 156
2018-05-12 05:30 | 162 | 162
2018-05-12 06:00 | 169 | 169
2018-05-12 06:30 | 176 | 176
2018-05-12 07:00 | 186 | 186
2018-05-12 07:30 | 193 | 193
2018-05-12 08:00 | 193 | 193
2018-05-12 08:30 | 191 | 191
2018-05-12 09:00 | 185 | 185
2018-05-12 09:30 | 177 | 177
2018-05-12 10:00 | 168 | 168
2018-05-12 10:30 | 159 | 159
2018-05-12 11:00 | 152 | 152
2018-05-12 11:30 | 146 | 146
2018-05-12 12:00 | 142 | 142
2018-05-12 12:30 | 140 | 140
2018-05-12 13:00 | 141 | 141
2018-05-12 13:30 | 144 | 144
2018-05-12 14:00 | 150 | 150
2018-05-12 14:30 | 158 | 158
2018-05-12 15:00 | 167 | 167
2018-05-12 15:30 | 178 | 178
2018-05-12 16:00 | 191 | 191
2018-05-12 16:30 | 204 | 204
2018-05-12 17:00 | 218 | 218
2018-05-12 17:30 | 229 | 229
2018-05-12 18:00 | 242 | 241
2018-05-12 18:30 | 242 | 241
2018-05-12 19:00 | 243 | 242
2018-05-12 19:30 | 237 | 236
2018-05-12 20:00 | 234 | 233
2018-05-12 20:30 | 232 | 231
2018-05-12 21:00 | 223 | 223
2018-05-12 21:30 | 216 | 216
2018-05-12 22:00 | 212 | 212
2018-05-12 22:30 | 210 | 210
2018-05-12 23:00 | 211 | 211
2018-05-12 23:30 | 202 | 202
2018-05-13 | 187 | 187
2018-05-13 00:30 | 173 | 173
2018-05-13 01:00 | 162 | 162
2018-05-13 01:30 | 153 | 153
2018-05-13 02:00 | 147 | 147
2018-05-13 02:30 | 144 | 144
2018-05-13 03:00 | 142 | 142
2018-05-13 03:30 | 142 | 142
2018-05-13 04:00 | 141 | 141
2018-05-13 04:30 | 141 | 141
2018-05-13 05:00 | 142 | 142
2018-05-13 05:30 | 146 | 146
2018-05-13 06:00 | 151 | 151
2018-05-13 06:30 | 159 | 159
2018-05-13 07:00 | 166 | 166
2018-05-13 07:30 | 174 | 174
2018-05-13 08:00 | 175 | 175
2018-05-13 08:30 | 173 | 173
2018-05-13 09:00 | 169 | 169
2018-05-13 09:30 | 163 | 163
2018-05-13 10:00 | 156 | 156
2018-05-13 10:30 | 147 | 147
2018-05-13 11:00 | 141 | 141
2018-05-13 11:30 | 136 | 136
2018-05-13 12:00 | 132 | 132
2018-05-13 12:30 | 131 | 131
2018-05-13 13:00 | 132 | 132
2018-05-13 13:30 | 135 | 135
2018-05-13 14:00 | 141 | 140
2018-05-13 14:30 | 149 | 148
2018-05-13 15:00 | 159 | 159
2018-05-13 15:30 | 171 | 171
2018-05-13 16:00 | 188 | 188
2018-05-13 16:30 | 203 | 203
2018-05-13 17:00 | 219 | 218
2018-05-13 17:30 | 231 | 230
2018-05-13 18:00 | 239 | 239
2018-05-13 18:30 | 239 | 239
2018-05-13 19:00 | 239 | 238
2018-05-13 19:30 | 234 | 233
2018-05-13 20:00 | 233 | 232
2018-05-13 20:30 | 231 | 231
2018-05-13 21:00 | 223 | 222
2018-05-13 21:30 | 213 | 213
2018-05-13 22:00 | 207 | 207
2018-05-13 22:30 | 202 | 202
2018-05-13 23:00 | 200 | 200
2018-05-13 23:30 | 190 | 190
2018-05-14 | 176 | 175
2018-05-14 00:30 | 163 | 163
2018-05-14 01:00 | 154 | 154
2018-05-14 01:30 | 148 | 148
2018-05-14 02:00 | 144 | 144
2018-05-14 02:30 | 141 | 141
2018-05-14 03:00 | 142 | 142
2018-05-14 03:30 | 143 | 143
2018-05-14 04:00 | 144 | 144
2018-05-14 04:30 | 148 | 148
2018-05-14 05:00 | 158 | 158
2018-05-14 05:30 | 174 | 173
2018-05-14 06:00 | 191 | 190
2018-05-14 06:30 | 216 | 215
2018-05-14 07:00 | 237 | 237
2018-05-14 07:30 | 246 | 246
2018-05-14 08:00 | 239 | 239
2018-05-14 08:30 | 225 | 225
2018-05-14 09:00 | 210 | 210
2018-05-14 09:30 | 199 | 199
2018-05-14 10:00 | 191 | 191
2018-05-14 10:30 | 186 | 186
2018-05-14 11:00 | 182 | 182
2018-05-14 11:30 | 179 | 179
2018-05-14 12:00 | 180 | 180
2018-05-14 12:30 | 182 | 182
2018-05-14 13:00 | 185 | 185
2018-05-14 13:30 | 192 | 192
2018-05-14 14:00 | 204 | 204
2018-05-14 14:30 | 211 | 211
2018-05-14 15:00 | 215 | 215
2018-05-14 15:30 | 226 | 226
2018-05-14 16:00 | 238 | 238
2018-05-14 16:30 | 248 | 248
2018-05-14 17:00 | 262 | 262
2018-05-14 17:30 | 274 | 274
2018-05-14 18:00 | 282 | 282
2018-05-14 18:30 | 276 | 276
2018-05-14 19:00 | 273 | 273
2018-05-14 19:30 | 266 | 266
2018-05-14 20:00 | 262 | 262
2018-05-14 20:30 | 260 | 260
2018-05-14 21:00 | 247 | 247
2018-05-14 21:30 | 235 | 234
2018-05-14 22:00 | 226 | 225
2018-05-14 22:30 | 218 | 218
2018-05-14 23:00 | 216 | 216
2018-05-14 23:30 | 204 | 204
2018-05-15 | 187 | 187
2018-05-15 00:30 | 172 | 172
2018-05-15 01:00 | 162 | 162
2018-05-15 01:30 | 157 | 156
2018-05-15 02:00 | 152 | 152
2018-05-15 02:30 | 150 | 150
2018-05-15 03:00 | 149 | 149
2018-05-15 03:30 | 149 | 148
2018-05-15 04:00 | 149 | 149
2018-05-15 04:30 | 154 | 154
2018-05-15 05:00 | 163 | 163
2018-05-15 05:30 | 178 | 178
2018-05-15 06:00 | 195 | 195
2018-05-15 06:30 | 220 | 220
2018-05-15 07:00 | 243 | 243
2018-05-15 07:30 | 251 | 251
2018-05-15 08:00 | 244 | 244
2018-05-15 08:30 | 229 | 228
2018-05-15 09:00 | 212 | 212
2018-05-15 09:30 | 201 | 201
2018-05-15 10:00 | 193 | 192
2018-05-15 10:30 | 186 | 186
2018-05-15 11:00 | 182 | 181
2018-05-15 11:30 | 179 | 178
2018-05-15 12:00 | 179 | 179
2018-05-15 12:30 | 182 | 181
2018-05-15 13:00 | 184 | 183
2018-05-15 13:30 | 191 | 190
2018-05-15 14:00 | 198 | 196
2018-05-15 14:30 | 204 | 202
2018-05-15 15:00 | 210 | 208
2018-05-15 15:30 | 220 | 218
2018-05-15 16:00 | 232 | 231
2018-05-15 16:30 | 244 | 243
2018-05-15 17:00 | 258 | 257
2018-05-15 17:30 | 271 | 269
2018-05-15 18:00 | 281 | 280
2018-05-15 18:30 | 276 | 276
2018-05-15 19:00 | 276 | 276
2018-05-15 19:30 | 269 | 269
2018-05-15 20:00 | 266 | 266
2018-05-15 20:30 | 265 | 265
2018-05-15 21:00 | 251 | 251
2018-05-15 21:30 | 237 | 236
2018-05-15 22:00 | 228 | 227
2018-05-15 22:30 | 221 | 221
2018-05-15 23:00 | 218 | 218
2018-05-15 23:30 | 206 | 206
2018-05-16 | 189 | 189
2018-05-16 00:30 | 173 | 173
2018-05-16 01:00 | 165 | 165
2018-05-16 01:30 | 157 | 157
2018-05-16 02:00 | 154 | 154
2018-05-16 02:30 | 152 | 151
2018-05-16 03:00 | 150 | 150
2018-05-16 03:30 | 151 | 151
2018-05-16 04:00 | 152 | 152
2018-05-16 04:30 | 156 | 156
2018-05-16 05:00 | 165 | 165
2018-05-16 05:30 | 181 | 181
2018-05-16 06:00 | 199 | 198
2018-05-16 06:30 | 225 | 225
2018-05-16 07:00 | 245 | 245
2018-05-16 07:30 | 253 | 253
2018-05-16 08:00 | 246 | 246
2018-05-16 08:30 | 232 | 232
2018-05-16 09:00 | 217 | 217
2018-05-16 09:30 | 205 | 205
2018-05-16 10:00 | 194 | 194
2018-05-16 10:30 | 189 | 189
2018-05-16 11:00 | 184 | 184
2018-05-16 11:30 | 182 | 182
2018-05-16 12:00 | 184 | 184
2018-05-16 12:30 | 185 | 185
2018-05-16 13:00 | 186 | 186
2018-05-16 13:30 | 189 | 189
2018-05-16 14:00 | 198 | 198
2018-05-16 14:30 | 204 | 203
2018-05-16 15:00 | 210 | 210
2018-05-16 15:30 | 219 | 219
2018-05-16 16:00 | 232 | 232
2018-05-16 16:30 | 243 | 243
2018-05-16 17:00 | 258 | 258
2018-05-16 17:30 | 271 | 271
2018-05-16 18:00 | 280 | 280
2018-05-16 18:30 | 276 | 276
2018-05-16 19:00 | 275 | 275
2018-05-16 19:30 | 269 | 269
2018-05-16 20:00 | 265 | 265
2018-05-16 20:30 | 264 | 264
2018-05-16 21:00 | 253 | 252
2018-05-16 21:30 | 240 | 238
2018-05-16 22:00 | 230 | 229
2018-05-16 22:30 | 222 | 221
2018-05-16 23:00 | 219 | 218
2018-05-16 23:30 | 207 | 206
2018-05-17 | 189 | 189
2018-05-17 00:30 | 174 | 174
2018-05-17 01:00 | 164 | 164
2018-05-17 01:30 | 158 | 158
2018-05-17 02:00 | 154 | 154
2018-05-17 02:30 | 152 | 152
2018-05-17 03:00 | 150 | 150
2018-05-17 03:30 | 151 | 151
2018-05-17 04:00 | 152 | 152
2018-05-17 04:30 | 157 | 157
2018-05-17 05:00 | 165 | 165
2018-05-17 05:30 | 182 | 182
2018-05-17 06:00 | 199 | 198
2018-05-17 06:30 | 224 | 224
2018-05-17 07:00 | 244 | 244
2018-05-17 07:30 | 255 | 255
2018-05-17 08:00 | 248 | 248
2018-05-17 08:30 | 234 | 234
2018-05-17 09:00 | 219 | 218
2018-05-17 09:30 | 207 | 206
2018-05-17 10:00 | 199 | 198
2018-05-17 10:30 | 195 | 194
2018-05-17 11:00 | 197 | 195
2018-05-17 11:30 | 201 | 200
2018-05-17 12:00 | 208 | 206
2018-05-17 12:30 | 214 | 213
2018-05-17 13:00 | 217 | 216
2018-05-17 13:30 | 226 | 224
2018-05-17 14:00 | 227 | 226
2018-05-17 14:30 | 226 | 224
2018-05-17 15:00 | 227 | 226
2018-05-17 15:30 | 226 | 225
2018-05-17 16:00 | 233 | 232
2018-05-17 16:30 | 244 | 243
2018-05-17 17:00 | 259 | 258
2018-05-17 17:30 | 273 | 273
2018-05-17 18:00 | 285 | 285
2018-05-17 18:30 | 281 | 281
2018-05-17 19:00 | 280 | 280
2018-05-17 19:30 | 274 | 274
2018-05-17 20:00 | 271 | 271
2018-05-17 20:30 | 271 | 271
2018-05-17 21:00 | 259 | 259
2018-05-17 21:30 | 246 | 245
2018-05-17 22:00 | 232 | 231
2018-05-17 22:30 | 225 | 225
2018-05-17 23:00 | 221 | 221
2018-05-17 23:30 | 209 | 209
2018-05-18 | 192 | 192
2018-05-18 00:30 | 175 | 175
2018-05-18 01:00 | 166 | 166
2018-05-18 01:30 | 159 | 159
2018-05-18 02:00 | 155 | 155
2018-05-18 02:30 | 152 | 152
2018-05-18 03:00 | 152 | 152
2018-05-18 03:30 | 152 | 152
2018-05-18 04:00 | 153 | 153
2018-05-18 04:30 | 161 | 161
2018-05-18 05:00 | 169 | 169
2018-05-18 05:30 | 183 | 183
2018-05-18 06:00 | 200 | 200
2018-05-18 06:30 | 223 | 222
2018-05-18 07:00 | 247 | 247
2018-05-18 07:30 | 260 | 260
2018-05-18 08:00 | 252 | 251
2018-05-18 08:30 | 238 | 237
2018-05-18 09:00 | 223 | 222
2018-05-18 09:30 | 212 | 211
2018-05-18 10:00 | 199 | 199
2018-05-18 10:30 | 194 | 194
2018-05-18 11:00 | 190 | 189
2018-05-18 11:30 | 187 | 187
2018-05-18 12:00 | 188 | 188
2018-05-18 12:30 | 188 | 188
2018-05-18 13:00 | 192 | 192
2018-05-18 13:30 | 196 | 195
2018-05-18 14:00 | 200 | 199
2018-05-18 14:30 | 205 | 205
2018-05-18 15:00 | 211 | 211
2018-05-18 15:30 | 220 | 219
2018-05-18 16:00 | 232 | 231
2018-05-18 16:30 | 245 | 244
2018-05-18 17:00 | 257 | 256
2018-05-18 17:30 | 265 | 264
2018-05-18 18:00 | 269 | 268
2018-05-18 18:30 | 264 | 263
2018-05-18 19:00 | 262 | 262
2018-05-18 19:30 | 257 | 257
2018-05-18 20:00 | 256 | 255
2018-05-18 20:30 | 254 | 254
2018-05-18 21:00 | 245 | 245
2018-05-18 21:30 | 234 | 234
2018-05-18 22:00 | 225 | 225
2018-05-18 22:30 | 223 | 222
2018-05-18 23:00 | 222 | 221
2018-05-18 23:30 | 211 | 210
2018-05-19 | 194 | 194
2018-05-19 00:30 | 182 | 182
2018-05-19 01:00 | 171 | 171
2018-05-19 01:30 | 163 | 163
2018-05-19 02:00 | 156 | 156
2018-05-19 02:30 | 153 | 153
2018-05-19 03:00 | 151 | 150
2018-05-19 03:30 | 151 | 151
2018-05-19 04:00 | 150 | 150
2018-05-19 04:30 | 152 | 152
2018-05-19 05:00 | 156 | 155
2018-05-19 05:30 | 161 | 161
2018-05-19 06:00 | 167 | 167
2018-05-19 06:30 | 178 | 178
2018-05-19 07:00 | 186 | 186
2018-05-19 07:30 | 194 | 194
2018-05-19 08:00 | 197 | 196
2018-05-19 08:30 | 194 | 194
2018-05-19 09:00 | 188 | 188
2018-05-19 09:30 | 181 | 181
2018-05-19 10:00 | 173 | 173
2018-05-19 10:30 | 165 | 165
2018-05-19 11:00 | 158 | 158
2018-05-19 11:30 | 152 | 152
2018-05-19 12:00 | 148 | 148
2018-05-19 12:30 | 148 | 148
2018-05-19 13:00 | 148 | 148
2018-05-19 13:30 | 151 | 151
2018-05-19 14:00 | 157 | 157
2018-05-19 14:30 | 164 | 164
2018-05-19 15:00 | 174 | 174
2018-05-19 15:30 | 185 | 185
2018-05-19 16:00 | 198 | 198
2018-05-19 16:30 | 211 | 211
2018-05-19 17:00 | 225 | 224
2018-05-19 17:30 | 235 | 234
2018-05-19 18:00 | 242 | 240
2018-05-19 18:30 | 240 | 239
2018-05-19 19:00 | 239 | 238
2018-05-19 19:30 | 233 | 232
2018-05-19 20:00 | 232 | 231
2018-05-19 20:30 | 230 | 230
2018-05-19 21:00 | 220 | 219
2018-05-19 21:30 | 213 | 212
2018-05-19 22:00 | 210 | 210
2018-05-19 22:30 | 211 | 211
2018-05-19 23:00 | 215 | 214
2018-05-19 23:30 | 205 | 205
2018-05-20 | 188 | 188
2018-05-20 00:30 | 173 | 173
2018-05-20 01:00 | 164 | 164
2018-05-20 01:30 | 157 | 157
2018-05-20 02:00 | 151 | 151
2018-05-20 02:30 | 148 | 148
2018-05-20 03:00 | 147 | 146
2018-05-20 03:30 | 146 | 145
2018-05-20 04:00 | 145 | 144
2018-05-20 04:30 | 145 | 145
2018-05-20 05:00 | 147 | 147
2018-05-20 05:30 | 150 | 150
2018-05-20 06:00 | 155 | 155
2018-05-20 06:30 | 161 | 160
2018-05-20 07:00 | 166 | 166
2018-05-20 07:30 | 171 | 171
2018-05-20 08:00 | 171 | 171
2018-05-20 08:30 | 170 | 170
2018-05-20 09:00 | 166 | 166
2018-05-20 09:30 | 161 | 161
2018-05-20 10:00 | 155 | 154
2018-05-20 10:30 | 148 | 148
2018-05-20 11:00 | 143 | 143
2018-05-20 11:30 | 138 | 138
2018-05-20 12:00 | 136 | 136
2018-05-20 12:30 | 136 | 136
2018-05-20 13:00 | 138 | 138
2018-05-20 13:30 | 141 | 141
2018-05-20 14:00 | 147 | 147
2018-05-20 14:30 | 155 | 155
2018-05-20 15:00 | 166 | 166
2018-05-20 15:30 | 178 | 178
2018-05-20 16:00 | 193 | 193
2018-05-20 16:30 | 207 | 207
2018-05-20 17:00 | 224 | 223
2018-05-20 17:30 | 240 | 238
2018-05-20 18:00 | 249 | 248
2018-05-20 18:30 | 246 | 246
2018-05-20 19:00 | 245 | 244
2018-05-20 19:30 | 239 | 239
2018-05-20 20:00 | 237 | 236
2018-05-20 20:30 | 236 | 236
2018-05-20 21:00 | 227 | 226
2018-05-20 21:30 | 218 | 217
2018-05-20 22:00 | 210 | 210
2018-05-20 22:30 | 207 | 207
2018-05-20 23:00 | 206 | 206
2018-05-20 23:30 | 196 | 196
2018-05-21 | 181 | 181
2018-05-21 00:30 | 169 | 169
2018-05-21 01:00 | 160 | 160
2018-05-21 01:30 | 155 | 154
2018-05-21 02:00 | 150 | 150
2018-05-21 02:30 | 148 | 147
2018-05-21 03:00 | 146 | 146
2018-05-21 03:30 | 149 | 149
2018-05-21 04:00 | 150 | 149
2018-05-21 04:30 | 156 | 156
2018-05-21 05:00 | 166 | 166
2018-05-21 05:30 | 182 | 182
2018-05-21 06:00 | 202 | 201
2018-05-21 06:30 | 228 | 227
2018-05-21 07:00 | 250 | 249
2018-05-21 07:30 | 262 | 260
2018-05-21 08:00 | 254 | 253
2018-05-21 08:30 | 237 | 236
2018-05-21 09:00 | 219 | 219
2018-05-21 09:30 | 207 | 206
2018-05-21 10:00 | 196 | 196
2018-05-21 10:30 | 189 | 189
2018-05-21 11:00 | 184 | 184
2018-05-21 11:30 | 182 | 181
2018-05-21 12:00 | 183 | 181
2018-05-21 12:30 | 185 | 183
2018-05-21 13:00 | 188 | 186
2018-05-21 13:30 | 193 | 191
2018-05-21 14:00 | 200 | 197
2018-05-21 14:30 | 207 | 205
2018-05-21 15:00 | 214 | 212
2018-05-21 15:30 | 225 | 225
2018-05-21 16:00 | 239 | 239
2018-05-21 16:30 | 251 | 251
2018-05-21 17:00 | 265 | 265
2018-05-21 17:30 | 280 | 280
2018-05-21 18:00 | 289 | 289
2018-05-21 18:30 | 283 | 283
2018-05-21 19:00 | 281 | 281
2018-05-21 19:30 | 273 | 273
2018-05-21 20:00 | 271 | 271
2018-05-21 20:30 | 270 | 269
2018-05-21 21:00 | 257 | 257
2018-05-21 21:30 | 244 | 244
2018-05-21 22:00 | 236 | 236
2018-05-21 22:30 | 228 | 228
2018-05-21 23:00 | 223 | 223
2018-05-21 23:30 | 211 | 210
2018-05-22 | 195 | 195
2018-05-22 00:30 | 181 | 181
2018-05-22 01:00 | 171 | 171
2018-05-22 01:30 | 164 | 164
2018-05-22 02:00 | 161 | 161
2018-05-22 02:30 | 158 | 158
2018-05-22 03:00 | 157 | 156
2018-05-22 03:30 | 157 | 157
2018-05-22 04:00 | 158 | 158
2018-05-22 04:30 | 165 | 165
2018-05-22 05:00 | 174 | 174
2018-05-22 05:30 | 191 | 191
2018-05-22 06:00 | 209 | 209
2018-05-22 06:30 | 237 | 237
2018-05-22 07:00 | 260 | 259
2018-05-22 07:30 | 270 | 270
2018-05-22 08:00 | 261 | 261
2018-05-22 08:30 | 242 | 242
2018-05-22 09:00 | 223 | 223
2018-05-22 09:30 | 211 | 211
2018-05-22 10:00 | 199 | 199
2018-05-22 10:30 | 191 | 190
2018-05-22 11:00 | 184 | 184
2018-05-22 11:30 | 179 | 178
2018-05-22 12:00 | 177 | 176
2018-05-22 12:30 | 179 | 178
2018-05-22 13:00 | 182 | 181
2018-05-22 13:30 | 186 | 186
2018-05-22 14:00 | 193 | 193
2018-05-22 14:30 | 202 | 202
2018-05-22 15:00 | 211 | 210
2018-05-22 15:30 | 221 | 221
2018-05-22 16:00 | 234 | 234
2018-05-22 16:30 | 248 | 248
2018-05-22 17:00 | 262 | 262
2018-05-22 17:30 | 275 | 275
2018-05-22 18:00 | 287 | 286
2018-05-22 18:30 | 282 | 282
2018-05-22 19:00 | 282 | 282
2018-05-22 19:30 | 275 | 275
2018-05-22 20:00 | 273 | 271
2018-05-22 20:30 | 274 | 273
2018-05-22 21:00 | 261 | 260
2018-05-22 21:30 | 248 | 247
2018-05-22 22:00 | 236 | 236
2018-05-22 22:30 | 230 | 229
2018-05-22 23:00 | 224 | 224
2018-05-22 23:30 | 213 | 213
2018-05-23 | 196 | 196
2018-05-23 00:30 | 181 | 181
2018-05-23 01:00 | 171 | 171
2018-05-23 01:30 | 166 | 166
2018-05-23 02:00 | 161 | 161
2018-05-23 02:30 | 156 | 156
2018-05-23 03:00 | 155 | 155
2018-05-23 03:30 | 156 | 155
2018-05-23 04:00 | 157 | 157
2018-05-23 04:30 | 162 | 162
2018-05-23 05:00 | 171 | 171
2018-05-23 05:30 | 188 | 188
2018-05-23 06:00 | 205 | 205
2018-05-23 06:30 | 233 | 233
2018-05-23 07:00 | 256 | 256
2018-05-23 07:30 | 265 | 265
2018-05-23 08:00 | 258 | 258
2018-05-23 08:30 | 245 | 245
2018-05-23 09:00 | 228 | 228
2018-05-23 09:30 | 216 | 216
2018-05-23 10:00 | 204 | 204
2018-05-23 10:30 | 198 | 198
2018-05-23 11:00 | 198 | 198
2018-05-23 11:30 | 200 | 200
2018-05-23 12:00 | 203 | 203
2018-05-23 12:30 | 208 | 208
2018-05-23 13:00 | 207 | 207
2018-05-23 13:30 | 206 | 206
2018-05-23 14:00 | 209 | 209
2018-05-23 14:30 | 218 | 217
2018-05-23 15:00 | 216 | 216
2018-05-23 15:30 | 223 | 222
2018-05-23 16:00 | 235 | 235
2018-05-23 16:30 | 246 | 246
2018-05-23 17:00 | 260 | 260
2018-05-23 17:30 | 274 | 273
2018-05-23 18:00 | 281 | 280
2018-05-23 18:30 | 276 | 276
2018-05-23 19:00 | 276 | 276
2018-05-23 19:30 | 269 | 269
2018-05-23 20:00 | 267 | 266
2018-05-23 20:30 | 265 | 265
2018-05-23 21:00 | 254 | 253
2018-05-23 21:30 | 243 | 242
2018-05-23 22:00 | 232 | 232
2018-05-23 22:30 | 227 | 226
2018-05-23 23:00 | 223 | 222
2018-05-23 23:30 | 211 | 211
2018-05-24 | 193 | 193
2018-05-24 00:30 | 178 | 178
2018-05-24 01:00 | 168 | 168
2018-05-24 01:30 | 162 | 162
2018-05-24 02:00 | 158 | 158
2018-05-24 02:30 | 154 | 154
2018-05-24 03:00 | 154 | 154
2018-05-24 03:30 | 155 | 155
2018-05-24 04:00 | 155 | 155
2018-05-24 04:30 | 161 | 161
2018-05-24 05:00 | 170 | 170
2018-05-24 05:30 | 186 | 186
2018-05-24 06:00 | 203 | 203
2018-05-24 06:30 | 235 | 235
2018-05-24 07:00 | 266 | 265
2018-05-24 07:30 | 277 | 276
2018-05-24 08:00 | 267 | 267
2018-05-24 08:30 | 250 | 249
2018-05-24 09:00 | 232 | 231
2018-05-24 09:30 | 220 | 219
2018-05-24 10:00 | 211 | 211
2018-05-24 10:30 | 205 | 205
2018-05-24 11:00 | 203 | 203
2018-05-24 11:30 | 204 | 203
2018-05-24 12:00 | 208 | 206
2018-05-24 12:30 | 207 | 206
2018-05-24 13:00 | 226 | 225
2018-05-24 13:30 | 231 | 230
2018-05-24 14:00 | 244 | 243
2018-05-24 14:30 | 250 | 250
2018-05-24 15:00 | 227 | 227
2018-05-24 15:30 | 228 | 227
2018-05-24 16:00 | 241 | 241
2018-05-24 16:30 | 254 | 254
2018-05-24 17:00 | 266 | 266
2018-05-24 17:30 | 279 | 279
2018-05-24 18:00 | 287 | 287
2018-05-24 18:30 | 284 | 284
2018-05-24 19:00 | 284 | 284
2018-05-24 19:30 | 277 | 277
2018-05-24 20:00 | 275 | 275
2018-05-24 20:30 | 273 | 273
2018-05-24 21:00 | 264 | 263
2018-05-24 21:30 | 250 | 250
2018-05-24 22:00 | 239 | 239
2018-05-24 22:30 | 233 | 233
2018-05-24 23:00 | 228 | 227
2018-05-24 23:30 | 214 | 213
2018-05-25 | 197 | 196
2018-05-25 00:30 | 180 | 179
2018-05-25 01:00 | 169 | 169
2018-05-25 01:30 | 163 | 163
2018-05-25 02:00 | 159 | 159
2018-05-25 02:30 | 156 | 156
2018-05-25 03:00 | 154 | 154
2018-05-25 03:30 | 155 | 155
2018-05-25 04:00 | 155 | 155
2018-05-25 04:30 | 161 | 161
2018-05-25 05:00 | 170 | 170
2018-05-25 05:30 | 186 | 185
2018-05-25 06:00 | 202 | 200
2018-05-25 06:30 | 227 | 227
2018-05-25 07:00 | 247 | 247
2018-05-25 07:30 | 259 | 259
2018-05-25 08:00 | 259 | 259
2018-05-25 08:30 | 253 | 253
2018-05-25 09:00 | 244 | 244
2018-05-25 09:30 | 232 | 231
2018-05-25 10:00 | 222 | 222
2018-05-25 10:30 | 219 | 219
2018-05-25 11:00 | 205 | 205
2018-05-25 11:30 | 205 | 205
2018-05-25 12:00 | 204 | 204
2018-05-25 12:30 | 199 | 199
2018-05-25 13:00 | 200 | 200
2018-05-25 13:30 | 204 | 204
2018-05-25 14:00 | 212 | 212
2018-05-25 14:30 | 220 | 220
2018-05-25 15:00 | 226 | 226
2018-05-25 15:30 | 233 | 233
2018-05-25 16:00 | 240 | 239
2018-05-25 16:30 | 248 | 247
2018-05-25 17:00 | 260 | 259
2018-05-25 17:30 | 271 | 271
2018-05-25 18:00 | 274 | 273
2018-05-25 18:30 | 267 | 267
2018-05-25 19:00 | 267 | 267
2018-05-25 19:30 | 260 | 260
2018-05-25 20:00 | 258 | 258
2018-05-25 20:30 | 256 | 256
2018-05-25 21:00 | 245 | 243
2018-05-25 21:30 | 234 | 233
2018-05-25 22:00 | 226 | 225
2018-05-25 22:30 | 222 | 222
2018-05-25 23:00 | 221 | 220
2018-05-25 23:30 | 209 | 209
2018-05-26 | 193 | 193
2018-05-26 00:30 | 177 | 177
2018-05-26 01:00 | 167 | 167
2018-05-26 01:30 | 161 | 161
2018-05-26 02:00 | 156 | 155
2018-05-26 02:30 | 153 | 152
2018-05-26 03:00 | 150 | 150
2018-05-26 03:30 | 149 | 148
2018-05-26 04:00 | 149 | 148
2018-05-26 04:30 | 150 | 149
2018-05-26 05:00 | 153 | 152
2018-05-26 05:30 | 160 | 159
2018-05-26 06:00 | 166 | 165
2018-05-26 06:30 | 175 | 174
2018-05-26 07:00 | 183 | 182
2018-05-26 07:30 | 192 | 190
2018-05-26 08:00 | 194 | 194
2018-05-26 08:30 | 193 | 193
2018-05-26 09:00 | 193 | 193
2018-05-26 09:30 | 198 | 197
2018-05-26 10:00 | 194 | 194
2018-05-26 10:30 | 183 | 183
2018-05-26 11:00 | 172 | 172
2018-05-26 11:30 | 167 | 167
2018-05-26 12:00 | 164 | 164
2018-05-26 12:30 | 166 | 166
2018-05-26 13:00 | 165 | 165
2018-05-26 13:30 | 179 | 179
2018-05-26 14:00 | 192 | 191
2018-05-26 14:30 | 200 | 199
2018-05-26 15:00 | 203 | 202
2018-05-26 15:30 | 204 | 204
2018-05-26 16:00 | 212 | 212
2018-05-26 16:30 | 223 | 222
2018-05-26 17:00 | 235 | 234
2018-05-26 17:30 | 247 | 247
2018-05-26 18:00 | 249 | 249
2018-05-26 18:30 | 248 | 248
2018-05-26 19:00 | 245 | 245
2018-05-26 19:30 | 239 | 238
2018-05-26 20:00 | 237 | 237
2018-05-26 20:30 | 237 | 236
2018-05-26 21:00 | 228 | 227
2018-05-26 21:30 | 219 | 219
2018-05-26 22:00 | 214 | 214
2018-05-26 22:30 | 211 | 211
2018-05-26 23:00 | 212 | 212
2018-05-26 23:30 | 203 | 203
2018-05-27 | 188 | 188
2018-05-27 00:30 | 174 | 174
2018-05-27 01:00 | 164 | 164
2018-05-27 01:30 | 157 | 157
2018-05-27 02:00 | 152 | 152
2018-05-27 02:30 | 148 | 148
2018-05-27 03:00 | 145 | 145
2018-05-27 03:30 | 143 | 143
2018-05-27 04:00 | 143 | 143
2018-05-27 04:30 | 143 | 143
2018-05-27 05:00 | 145 | 145
2018-05-27 05:30 | 148 | 148
2018-05-27 06:00 | 152 | 152
2018-05-27 06:30 | 159 | 159
2018-05-27 07:00 | 165 | 165
2018-05-27 07:30 | 173 | 173
2018-05-27 08:00 | 177 | 177
2018-05-27 08:30 | 182 | 181
2018-05-27 09:00 | 183 | 183
2018-05-27 09:30 | 180 | 180
2018-05-27 10:00 | 173 | 172
2018-05-27 10:30 | 165 | 164
2018-05-27 11:00 | 176 | 175
2018-05-27 11:30 | 178 | 177
2018-05-27 12:00 | 170 | 170
2018-05-27 12:30 | 170 | 169
2018-05-27 13:00 | 169 | 168
2018-05-27 13:30 | 170 | 169
2018-05-27 14:00 | 169 | 168
2018-05-27 14:30 | 183 | 182
2018-05-27 15:00 | 183 | 182
2018-05-27 15:30 | 183 | 182
2018-05-27 16:00 | 198 | 197
2018-05-27 16:30 | 214 | 214
2018-05-27 17:00 | 232 | 231
2018-05-27 17:30 | 249 | 248
2018-05-27 18:00 | 256 | 256
2018-05-27 18:30 | 255 | 254
2018-05-27 19:00 | 251 | 251
2018-05-27 19:30 | 245 | 244
2018-05-27 20:00 | 244 | 243
2018-05-27 20:30 | 243 | 242
2018-05-27 21:00 | 232 | 232
2018-05-27 21:30 | 222 | 222
2018-05-27 22:00 | 214 | 214
2018-05-27 22:30 | 210 | 210
2018-05-27 23:00 | 210 | 210
2018-05-27 23:30 | 199 | 199
2018-05-28 | 184 | 184
2018-05-28 00:30 | 170 | 170
2018-05-28 01:00 | 161 | 161
2018-05-28 01:30 | 156 | 155
2018-05-28 02:00 | 151 | 150
2018-05-28 02:30 | 148 | 147
2018-05-28 03:00 | 147 | 146
2018-05-28 03:30 | 147 | 146
2018-05-28 04:00 | 148 | 147
2018-05-28 04:30 | 154 | 153
2018-05-28 05:00 | 163 | 163
2018-05-28 05:30 | 177 | 177
2018-05-28 06:00 | 193 | 193
2018-05-28 06:30 | 218 | 217
2018-05-28 07:00 | 237 | 237
2018-05-28 07:30 | 254 | 253
2018-05-28 08:00 | 253 | 251
2018-05-28 08:30 | 242 | 241
2018-05-28 09:00 | 227 | 226
2018-05-28 09:30 | 218 | 217
2018-05-28 10:00 | 215 | 214
2018-05-28 10:30 | 216 | 214
2018-05-28 11:00 | 219 | 217
2018-05-28 11:30 | 217 | 215
2018-05-28 12:00 | 224 | 222
2018-05-28 12:30 | 220 | 218
2018-05-28 13:00 | 216 | 214
2018-05-28 13:30 | 225 | 224
2018-05-28 14:00 | 236 | 235
2018-05-28 14:30 | 240 | 239
2018-05-28 15:00 | 241 | 240
2018-05-28 15:30 | 245 | 244
2018-05-28 16:00 | 252 | 251
2018-05-28 16:30 | 263 | 263
2018-05-28 17:00 | 279 | 279
2018-05-28 17:30 | 296 | 295
2018-05-28 18:00 | 298 | 298
2018-05-28 18:30 | 291 | 291
2018-05-28 19:00 | 288 | 287
2018-05-28 19:30 | 280 | 279
2018-05-28 20:00 | 275 | 275
2018-05-28 20:30 | 273 | 272
2018-05-28 21:00 | 262 | 261
2018-05-28 21:30 | 248 | 248
2018-05-28 22:00 | 238 | 238
2018-05-28 22:30 | 230 | 230
2018-05-28 23:00 | 228 | 227
2018-05-28 23:30 | 216 | 216
2018-05-29 | 200 | 199
2018-05-29 00:30 | 183 | 183
2018-05-29 01:00 | 172 | 172
2018-05-29 01:30 | 164 | 164
2018-05-29 02:00 | 159 | 159
2018-05-29 02:30 | 157 | 157
2018-05-29 03:00 | 156 | 156
2018-05-29 03:30 | 156 | 156
2018-05-29 04:00 | 157 | 157
2018-05-29 04:30 | 163 | 163
2018-05-29 05:00 | 171 | 171
2018-05-29 05:30 | 186 | 185
2018-05-29 06:00 | 203 | 201
2018-05-29 06:30 | 227 | 227
2018-05-29 07:00 | 244 | 243
2018-05-29 07:30 | 257 | 256
2018-05-29 08:00 | 256 | 256
2018-05-29 08:30 | 259 | 259
2018-05-29 09:00 | 247 | 247
2018-05-29 09:30 | 238 | 238
2018-05-29 10:00 | 233 | 233
2018-05-29 10:30 | 223 | 223
2018-05-29 11:00 | 221 | 221
2018-05-29 11:30 | 229 | 229
2018-05-29 12:00 | 236 | 236
2018-05-29 12:30 | 247 | 246
2018-05-29 13:00 | 253 | 252
2018-05-29 13:30 | 248 | 248
2018-05-29 14:00 | 245 | 245
2018-05-29 14:30 | 240 | 240
2018-05-29 15:00 | 249 | 249
2018-05-29 15:30 | 254 | 254
2018-05-29 16:00 | 265 | 265
2018-05-29 16:30 | 277 | 277
2018-05-29 17:00 | 290 | 290
2018-05-29 17:30 | 304 | 304
2018-05-29 18:00 | 312 | 312
2018-05-29 18:30 | 307 | 306
2018-05-29 19:00 | 306 | 306
2018-05-29 19:30 | 300 | 299
2018-05-29 20:00 | 297 | 296
2018-05-29 20:30 | 293 | 293
2018-05-29 21:00 | 278 | 277
2018-05-29 21:30 | 263 | 263
2018-05-29 22:00 | 251 | 251
2018-05-29 22:30 | 244 | 244
2018-05-29 23:00 | 242 | 242
2018-05-29 23:30 | 228 | 228
2018-05-30 | 210 | 210
2018-05-30 00:30 | 193 | 193
2018-05-30 01:00 | 181 | 181
2018-05-30 01:30 | 175 | 175
2018-05-30 02:00 | 171 | 170
2018-05-30 02:30 | 167 | 167
2018-05-30 03:00 | 165 | 165
2018-05-30 03:30 | 165 | 165
2018-05-30 04:00 | 166 | 166
2018-05-30 04:30 | 173 | 172
2018-05-30 05:00 | 182 | 182
2018-05-30 05:30 | 198 | 198
2018-05-30 06:00 | 215 | 215
2018-05-30 06:30 | 243 | 241
2018-05-30 07:00 | 267 | 267
2018-05-30 07:30 | 280 | 280
2018-05-30 08:00 | 277 | 277
2018-05-30 08:30 | 263 | 262
2018-05-30 09:00 | 247 | 247
2018-05-30 09:30 | 235 | 235
2018-05-30 10:00 | 222 | 222
2018-05-30 10:30 | 212 | 212
2018-05-30 11:00 | 206 | 205
2018-05-30 11:30 | 204 | 203
2018-05-30 12:00 | 204 | 203
2018-05-30 12:30 | 206 | 205
2018-05-30 13:00 | 208 | 207
2018-05-30 13:30 | 214 | 213
2018-05-30 14:00 | 221 | 219
2018-05-30 14:30 | 232 | 230
2018-05-30 15:00 | 241 | 241
2018-05-30 15:30 | 250 | 249
2018-05-30 16:00 | 260 | 260
2018-05-30 16:30 | 274 | 274
2018-05-30 17:00 | 288 | 288
2018-05-30 17:30 | 302 | 302
2018-05-30 18:00 | 307 | 306
2018-05-30 18:30 | 300 | 300
2018-05-30 19:00 | 299 | 299
2018-05-30 19:30 | 291 | 290
2018-05-30 20:00 | 289 | 287
2018-05-30 20:30 | 287 | 285
2018-05-30 21:00 | 274 | 273
2018-05-30 21:30 | 262 | 261
2018-05-30 22:00 | 250 | 250
2018-05-30 22:30 | 243 | 242
2018-05-30 23:00 | 239 | 238
2018-05-30 23:30 | 227 | 226
2018-05-31 | 209 | 209
2018-05-31 00:30 | 193 | 193
2018-05-31 01:00 | 182 | 182
2018-05-31 01:30 | 175 | 175
2018-05-31 02:00 | 170 | 170
2018-05-31 02:30 | 169 | 169
2018-05-31 03:00 | 167 | 167
2018-05-31 03:30 | 168 | 168
2018-05-31 04:00 | 170 | 170
2018-05-31 04:30 | 177 | 177
2018-05-31 05:00 | 187 | 187
2018-05-31 05:30 | 205 | 204
2018-05-31 06:00 | 225 | 223
2018-05-31 06:30 | 256 | 256
2018-05-31 07:00 | 284 | 284
2018-05-31 07:30 | 297 | 297
2018-05-31 08:00 | 289 | 289
2018-05-31 08:30 | 271 | 271
2018-05-31 09:00 | 252 | 252
2018-05-31 09:30 | 235 | 235
2018-05-31 10:00 | 220 | 219
2018-05-31 10:30 | 209 | 208
2018-05-31 11:00 | 201 | 201
2018-05-31 11:30 | 195 | 194
2018-05-31 12:00 | 192 | 192
2018-05-31 12:30 | 193 | 192
2018-05-31 13:00 | 195 | 194
2018-05-31 13:30 | 200 | 199
2018-05-31 14:00 | 208 | 207
2018-05-31 14:30 | 215 | 215
2018-05-31 15:00 | 224 | 223
2018-05-31 15:30 | 235 | 235
2018-05-31 16:00 | 251 | 250
2018-05-31 16:30 | 266 | 266
2018-05-31 17:00 | 283 | 283
2018-05-31 17:30 | 302 | 301
2018-05-31 18:00 | 313 | 313
2018-05-31 18:30 | 314 | 314
2018-05-31 19:00 | 316 | 315
2018-05-31 19:30 | 312 | 311
2018-05-31 20:00 | 308 | 308
2018-05-31 20:30 | 307 | 306
2018-05-31 21:00 | 295 | 295
2018-05-31 21:30 | 281 | 281
2018-05-31 22:00 | 268 | 268
2018-05-31 22:30 | 259 | 259
2018-05-31 23:00 | 253 | 253
2018-05-31 23:30 | 237 | 237
2018-06-01 | 220 | 220
2018-06-01 00:30 | 202 | 202
2018-06-01 01:00 | 190 | 190
2018-06-01 01:30 | 182 | 182
2018-06-01 02:00 | 178 | 178
2018-06-01 02:30 | 175 | 175
2018-06-01 03:00 | 173 | 173
2018-06-01 03:30 | 173 | 173
2018-06-01 04:00 | 174 | 174
2018-06-01 04:30 | 182 | 182
2018-06-01 05:00 | 193 | 193
2018-06-01 05:30 | 211 | 210
2018-06-01 06:00 | 232 | 230
2018-06-01 06:30 | 264 | 263
2018-06-01 07:00 | 292 | 291
2018-06-01 07:30 | 309 | 308
2018-06-01 08:00 | 300 | 300
2018-06-01 08:30 | 279 | 279
2018-06-01 09:00 | 260 | 260
2018-06-01 09:30 | 243 | 242
2018-06-01 10:00 | 225 | 225
2018-06-01 10:30 | 213 | 213
2018-06-01 11:00 | 206 | 205
2018-06-01 11:30 | 199 | 198
2018-06-01 12:00 | 195 | 195
2018-06-01 12:30 | 194 | 193
2018-06-01 13:00 | 193 | 193
2018-06-01 13:30 | 197 | 197
2018-06-01 14:00 | 203 | 202
2018-06-01 14:30 | 210 | 210
2018-06-01 15:00 | 218 | 218
2018-06-01 15:30 | 228 | 228
2018-06-01 16:00 | 244 | 243
2018-06-01 16:30 | 259 | 258
2018-06-01 17:00 | 275 | 274
2018-06-01 17:30 | 291 | 289
2018-06-01 18:00 | 299 | 297
2018-06-01 18:30 | 297 | 296
2018-06-01 19:00 | 300 | 299
2018-06-01 19:30 | 293 | 293
2018-06-01 20:00 | 293 | 292
2018-06-01 20:30 | 292 | 291
2018-06-01 21:00 | 283 | 282
2018-06-01 21:30 | 271 | 271
2018-06-01 22:00 | 261 | 261
2018-06-01 22:30 | 256 | 256
2018-06-01 23:00 | 251 | 251
2018-06-01 23:30 | 238 | 238
2018-06-02 | 220 | 220
2018-06-02 00:30 | 202 | 202
2018-06-02 01:00 | 190 | 190
2018-06-02 01:30 | 181 | 181
2018-06-02 02:00 | 175 | 175
2018-06-02 02:30 | 172 | 172
2018-06-02 03:00 | 169 | 169
2018-06-02 03:30 | 169 | 168
2018-06-02 04:00 | 169 | 169
2018-06-02 04:30 | 171 | 171
2018-06-02 05:00 | 175 | 175
2018-06-02 05:30 | 184 | 183
2018-06-02 06:00 | 193 | 193
2018-06-02 06:30 | 207 | 206
2018-06-02 07:00 | 220 | 219
2018-06-02 07:30 | 233 | 232
2018-06-02 08:00 | 236 | 236
2018-06-02 08:30 | 231 | 231
2018-06-02 09:00 | 222 | 222
2018-06-02 09:30 | 211 | 211
2018-06-02 10:00 | 198 | 198
2018-06-02 10:30 | 184 | 183
2018-06-02 11:00 | 174 | 173
2018-06-02 11:30 | 165 | 164
2018-06-02 12:00 | 160 | 159
2018-06-02 12:30 | 157 | 156
2018-06-02 13:00 | 157 | 156
2018-06-02 13:30 | 160 | 159
2018-06-02 14:00 | 165 | 164
2018-06-02 14:30 | 173 | 172
2018-06-02 15:00 | 183 | 182
2018-06-02 15:30 | 195 | 194
2018-06-02 16:00 | 208 | 208
2018-06-02 16:30 | 224 | 223
2018-06-02 17:00 | 244 | 243
2018-06-02 17:30 | 261 | 260
2018-06-02 18:00 | 269 | 267
2018-06-02 18:30 | 268 | 266
2018-06-02 19:00 | 269 | 267
2018-06-02 19:30 | 264 | 263
2018-06-02 20:00 | 265 | 263
2018-06-02 20:30 | 265 | 263
2018-06-02 21:00 | 254 | 253
2018-06-02 21:30 | 245 | 244
2018-06-02 22:00 | 238 | 238
2018-06-02 22:30 | 236 | 236
2018-06-02 23:00 | 236 | 235
2018-06-02 23:30 | 225 | 225
2018-06-03 | 208 | 208
2018-06-03 00:30 | 192 | 192
2018-06-03 01:00 | 182 | 181
2018-06-03 01:30 | 173 | 173
2018-06-03 02:00 | 166 | 166
2018-06-03 02:30 | 163 | 162
2018-06-03 03:00 | 160 | 159
2018-06-03 03:30 | 158 | 158
2018-06-03 04:00 | 158 | 158
2018-06-03 04:30 | 160 | 160
2018-06-03 05:00 | 162 | 162
2018-06-03 05:30 | 167 | 167
2018-06-03 06:00 | 172 | 172
2018-06-03 06:30 | 180 | 180
2018-06-03 07:00 | 189 | 189
2018-06-03 07:30 | 198 | 198
2018-06-03 08:00 | 201 | 201
2018-06-03 08:30 | 201 | 201
2018-06-03 09:00 | 197 | 197
2018-06-03 09:30 | 190 | 189
2018-06-03 10:00 | 180 | 180
2018-06-03 10:30 | 171 | 171
2018-06-03 11:00 | 163 | 162
2018-06-03 11:30 | 154 | 154
2018-06-03 12:00 | 146 | 146
2018-06-03 12:30 | 147 | 147
2018-06-03 13:00 | 149 | 148
2018-06-03 13:30 | 153 | 153
2018-06-03 14:00 | 162 | 162
2018-06-03 14:30 | 170 | 169
2018-06-03 15:00 | 178 | 178
2018-06-03 15:30 | 188 | 188
2018-06-03 16:00 | 202 | 200
2018-06-03 16:30 | 214 | 214
2018-06-03 17:00 | 232 | 231
2018-06-03 17:30 | 250 | 248
2018-06-03 18:00 | 257 | 255
2018-06-03 18:30 | 254 | 252
2018-06-03 19:00 | 252 | 251
2018-06-03 19:30 | 246 | 245
2018-06-03 20:00 | 244 | 243
2018-06-03 20:30 | 244 | 243
2018-06-03 21:00 | 233 | 233
2018-06-03 21:30 | 223 | 223
2018-06-03 22:00 | 216 | 216
2018-06-03 22:30 | 213 | 213
2018-06-03 23:00 | 211 | 211
2018-06-03 23:30 | 200 | 200
2018-06-04 | 185 | 184
2018-06-04 00:30 | 172 | 172
2018-06-04 01:00 | 163 | 162
2018-06-04 01:30 | 157 | 157
2018-06-04 02:00 | 152 | 152
2018-06-04 02:30 | 150 | 150
2018-06-04 03:00 | 148 | 148
2018-06-04 03:30 | 148 | 148
2018-06-04 04:00 | 150 | 150
2018-06-04 04:30 | 157 | 157
2018-06-04 05:00 | 168 | 168
2018-06-04 05:30 | 187 | 186
2018-06-04 06:00 | 205 | 203
2018-06-04 06:30 | 234 | 233
2018-06-04 07:00 | 256 | 255
2018-06-04 07:30 | 270 | 270
2018-06-04 08:00 | 263 | 263
2018-06-04 08:30 | 246 | 246
2018-06-04 09:00 | 227 | 227
2018-06-04 09:30 | 213 | 213
2018-06-04 10:00 | 202 | 202
2018-06-04 10:30 | 194 | 194
2018-06-04 11:00 | 191 | 191
2018-06-04 11:30 | 188 | 188
2018-06-04 12:00 | 189 | 189
2018-06-04 12:30 | 191 | 191
2018-06-04 13:00 | 196 | 196
2018-06-04 13:30 | 203 | 203
2018-06-04 14:00 | 210 | 210
2018-06-04 14:30 | 219 | 219
2018-06-04 15:00 | 223 | 223
2018-06-04 15:30 | 230 | 230
2018-06-04 16:00 | 244 | 244
2018-06-04 16:30 | 258 | 258
2018-06-04 17:00 | 271 | 271
2018-06-04 17:30 | 289 | 289
2018-06-04 18:00 | 297 | 297
2018-06-04 18:30 | 291 | 291
2018-06-04 19:00 | 291 | 290
2018-06-04 19:30 | 284 | 284
2018-06-04 20:00 | 281 | 281
2018-06-04 20:30 | 280 | 279
2018-06-04 21:00 | 269 | 266
2018-06-04 21:30 | 257 | 255
2018-06-04 22:00 | 244 | 242
2018-06-04 22:30 | 236 | 235
2018-06-04 23:00 | 232 | 231
2018-06-04 23:30 | 220 | 219
2018-06-05 | 202 | 202
2018-06-05 00:30 | 185 | 185
2018-06-05 01:00 | 174 | 174
2018-06-05 01:30 | 168 | 168
2018-06-05 02:00 | 163 | 163
2018-06-05 02:30 | 159 | 159
2018-06-05 03:00 | 158 | 158
2018-06-05 03:30 | 158 | 158
2018-06-05 04:00 | 160 | 160
2018-06-05 04:30 | 168 | 167
2018-06-05 05:00 | 176 | 176
2018-06-05 05:30 | 194 | 193
2018-06-05 06:00 | 214 | 211
2018-06-05 06:30 | 243 | 243
2018-06-05 07:00 | 267 | 266
2018-06-05 07:30 | 279 | 277
2018-06-05 08:00 | 272 | 269
2018-06-05 08:30 | 254 | 251
2018-06-05 09:00 | 237 | 232
2018-06-05 09:30 | 223 | 217
2018-06-05 10:00 | 205 | 204
2018-06-05 10:30 | 196 | 196
2018-06-05 11:00 | 190 | 190
2018-06-05 11:30 | 185 | 185
2018-06-05 12:00 | 187 | 187
2018-06-05 12:30 | 191 | 191
2018-06-05 13:00 | 196 | 195
2018-06-05 13:30 | 199 | 199
2018-06-05 14:00 | 203 | 203
2018-06-05 14:30 | 207 | 207
2018-06-05 15:00 | 215 | 214
2018-06-05 15:30 | 225 | 224
2018-06-05 16:00 | 239 | 239
2018-06-05 16:30 | 254 | 254
2018-06-05 17:00 | 266 | 266
2018-06-05 17:30 | 278 | 277
2018-06-05 18:00 | 285 | 285
2018-06-05 18:30 | 288 | 287
2018-06-05 19:00 | 283 | 282
2018-06-05 19:30 | 276 | 276
2018-06-05 20:00 | 284 | 283
2018-06-05 20:30 | 285 | 284
2018-06-05 21:00 | 271 | 270
2018-06-05 21:30 | 257 | 257
2018-06-05 22:00 | 246 | 246
2018-06-05 22:30 | 238 | 238
2018-06-05 23:00 | 233 | 233
2018-06-05 23:30 | 221 | 221
2018-06-06 | 204 | 204
2018-06-06 00:30 | 186 | 186
2018-06-06 01:00 | 175 | 175
2018-06-06 01:30 | 167 | 167
2018-06-06 02:00 | 163 | 163
2018-06-06 02:30 | 159 | 159
2018-06-06 03:00 | 157 | 157
2018-06-06 03:30 | 157 | 157
2018-06-06 04:00 | 158 | 158
2018-06-06 04:30 | 165 | 165
2018-06-06 05:00 | 176 | 176
2018-06-06 05:30 | 194 | 193
2018-06-06 06:00 | 212 | 211
2018-06-06 06:30 | 240 | 238
2018-06-06 07:00 | 264 | 264
2018-06-06 07:30 | 279 | 279
2018-06-06 08:00 | 271 | 271
2018-06-06 08:30 | 254 | 254
2018-06-06 09:00 | 235 | 234
2018-06-06 09:30 | 224 | 224
2018-06-06 10:00 | 206 | 206
2018-06-06 10:30 | 197 | 196
2018-06-06 11:00 | 191 | 191
2018-06-06 11:30 | 190 | 190
2018-06-06 12:00 | 194 | 193
2018-06-06 12:30 | 208 | 207
2018-06-06 13:00 | 218 | 218
2018-06-06 13:30 | 218 | 217
2018-06-06 14:00 | 221 | 220
2018-06-06 14:30 | 220 | 219
2018-06-06 15:00 | 225 | 225
2018-06-06 15:30 | 233 | 232
2018-06-06 16:00 | 241 | 241
2018-06-06 16:30 | 254 | 254
2018-06-06 17:00 | 274 | 274
2018-06-06 17:30 | 290 | 290
2018-06-06 18:00 | 297 | 296
2018-06-06 18:30 | 294 | 294
2018-06-06 19:00 | 294 | 293
2018-06-06 19:30 | 288 | 287
2018-06-06 20:00 | 284 | 284
2018-06-06 20:30 | 281 | 280
2018-06-06 21:00 | 268 | 267
2018-06-06 21:30 | 257 | 257
2018-06-06 22:00 | 246 | 246
2018-06-06 22:30 | 240 | 240
2018-06-06 23:00 | 237 | 237
2018-06-06 23:30 | 223 | 223
2018-06-07 | 207 | 206
2018-06-07 00:30 | 189 | 188
2018-06-07 01:00 | 175 | 175
2018-06-07 01:30 | 167 | 167
2018-06-07 02:00 | 163 | 163
2018-06-07 02:30 | 160 | 160
2018-06-07 03:00 | 158 | 158
2018-06-07 03:30 | 158 | 158
2018-06-07 04:00 | 160 | 159
2018-06-07 04:30 | 165 | 164
2018-06-07 05:00 | 175 | 175
2018-06-07 05:30 | 191 | 189
2018-06-07 06:00 | 207 | 205
2018-06-07 06:30 | 233 | 233
2018-06-07 07:00 | 257 | 257
2018-06-07 07:30 | 275 | 275
2018-06-07 08:00 | 283 | 282
2018-06-07 08:30 | 282 | 282
2018-06-07 09:00 | 278 | 277
2018-06-07 09:30 | 276 | 275
2018-06-07 10:00 | 267 | 267
2018-06-07 10:30 | 253 | 252
2018-06-07 11:00 | 232 | 232
2018-06-07 11:30 | 222 | 222
2018-06-07 12:00 | 221 | 221
2018-06-07 12:30 | 223 | 223
2018-06-07 13:00 | 231 | 231
2018-06-07 13:30 | 241 | 241
2018-06-07 14:00 | 231 | 231
2018-06-07 14:30 | 224 | 223
2018-06-07 15:00 | 230 | 229
2018-06-07 15:30 | 238 | 237
2018-06-07 16:00 | 248 | 247
2018-06-07 16:30 | 258 | 257
2018-06-07 17:00 | 275 | 273
2018-06-07 17:30 | 284 | 282
2018-06-07 18:00 | 292 | 291
2018-06-07 18:30 | 290 | 290
2018-06-07 19:00 | 290 | 290
2018-06-07 19:30 | 284 | 284
2018-06-07 20:00 | 294 | 291
2018-06-07 20:30 | 292 | 291
2018-06-07 21:00 | 279 | 278
2018-06-07 21:30 | 263 | 262
2018-06-07 22:00 | 248 | 248
2018-06-07 22:30 | 242 | 241
2018-06-07 23:00 | 238 | 237
2018-06-07 23:30 | 223 | 223
2018-06-08 | 205 | 204
2018-06-08 00:30 | 189 | 189
2018-06-08 01:00 | 177 | 177
2018-06-08 01:30 | 169 | 169
2018-06-08 02:00 | 163 | 163
2018-06-08 02:30 | 160 | 160
2018-06-08 03:00 | 158 | 158
2018-06-08 03:30 | 159 | 159
2018-06-08 04:00 | 160 | 160
2018-06-08 04:30 | 166 | 166
2018-06-08 05:00 | 174 | 174
2018-06-08 05:30 | 189 | 188
2018-06-08 06:00 | 205 | 205
2018-06-08 06:30 | 232 | 230
2018-06-08 07:00 | 256 | 256
2018-06-08 07:30 | 271 | 271
2018-06-08 08:00 | 269 | 269
2018-06-08 08:30 | 262 | 262
2018-06-08 09:00 | 254 | 253
2018-06-08 09:30 | 244 | 244
2018-06-08 10:00 | 241 | 240
2018-06-08 10:30 | 233 | 231
2018-06-08 11:00 | 224 | 222
2018-06-08 11:30 | 226 | 224
2018-06-08 12:00 | 223 | 221
2018-06-08 12:30 | 212 | 211
2018-06-08 13:00 | 212 | 211
2018-06-08 13:30 | 215 | 214
2018-06-08 14:00 | 221 | 220
2018-06-08 14:30 | 231 | 230
2018-06-08 15:00 | 231 | 231
2018-06-08 15:30 | 239 | 238
2018-06-08 16:00 | 253 | 253
2018-06-08 16:30 | 265 | 264
2018-06-08 17:00 | 280 | 280
2018-06-08 17:30 | 290 | 290
2018-06-08 18:00 | 291 | 290
2018-06-08 18:30 | 287 | 287
2018-06-08 19:00 | 286 | 286
2018-06-08 19:30 | 279 | 279
2018-06-08 20:00 | 278 | 278
2018-06-08 20:30 | 276 | 276
2018-06-08 21:00 | 262 | 262
2018-06-08 21:30 | 250 | 250
2018-06-08 22:00 | 241 | 241
2018-06-08 22:30 | 234 | 234
2018-06-08 23:00 | 233 | 230
2018-06-08 23:30 | 220 | 219
2018-06-09 | 203 | 202
2018-06-09 00:30 | 187 | 186
2018-06-09 01:00 | 176 | 176
2018-06-09 01:30 | 165 | 164
2018-06-09 02:00 | 158 | 158
2018-06-09 02:30 | 155 | 155
2018-06-09 03:00 | 153 | 152
2018-06-09 03:30 | 151 | 151
2018-06-09 04:00 | 150 | 150
2018-06-09 04:30 | 152 | 152
2018-06-09 05:00 | 154 | 154
2018-06-09 05:30 | 160 | 160
2018-06-09 06:00 | 166 | 166
2018-06-09 06:30 | 178 | 178
2018-06-09 07:00 | 188 | 187
2018-06-09 07:30 | 200 | 199
2018-06-09 08:00 | 209 | 209
2018-06-09 08:30 | 213 | 213
2018-06-09 09:00 | 218 | 217
2018-06-09 09:30 | 211 | 211
2018-06-09 10:00 | 210 | 210
2018-06-09 10:30 | 202 | 202
2018-06-09 11:00 | 200 | 200
2018-06-09 11:30 | 201 | 201
2018-06-09 12:00 | 190 | 190
2018-06-09 12:30 | 185 | 184
2018-06-09 13:00 | 177 | 177
2018-06-09 13:30 | 175 | 175
2018-06-09 14:00 | 176 | 175
2018-06-09 14:30 | 182 | 182
2018-06-09 15:00 | 187 | 187
2018-06-09 15:30 | 189 | 189
2018-06-09 16:00 | 199 | 199
2018-06-09 16:30 | 213 | 213
2018-06-09 17:00 | 229 | 228
2018-06-09 17:30 | 244 | 243
2018-06-09 18:00 | 251 | 251
2018-06-09 18:30 | 249 | 249
2018-06-09 19:00 | 249 | 249
2018-06-09 19:30 | 245 | 245
2018-06-09 20:00 | 242 | 241
2018-06-09 20:30 | 241 | 240
2018-06-09 21:00 | 230 | 229
2018-06-09 21:30 | 222 | 221
2018-06-09 22:00 | 217 | 216
2018-06-09 22:30 | 214 | 214
2018-06-09 23:00 | 215 | 215
2018-06-09 23:30 | 206 | 205
2018-06-10 | 191 | 191
2018-06-10 00:30 | 176 | 176
2018-06-10 01:00 | 166 | 166
2018-06-10 01:30 | 158 | 158
2018-06-10 02:00 | 151 | 150
2018-06-10 02:30 | 147 | 146
2018-06-10 03:00 | 143 | 143
2018-06-10 03:30 | 142 | 142
2018-06-10 04:00 | 141 | 141
2018-06-10 04:30 | 143 | 143
2018-06-10 05:00 | 145 | 145
2018-06-10 05:30 | 149 | 149
2018-06-10 06:00 | 152 | 152
2018-06-10 06:30 | 159 | 159
2018-06-10 07:00 | 165 | 165
2018-06-10 07:30 | 174 | 174
2018-06-10 08:00 | 181 | 180
2018-06-10 08:30 | 185 | 185
2018-06-10 09:00 | 180 | 179
2018-06-10 09:30 | 177 | 176
2018-06-10 10:00 | 172 | 171
2018-06-10 10:30 | 169 | 168
2018-06-10 11:00 | 163 | 163
2018-06-10 11:30 | 165 | 165
2018-06-10 12:00 | 165 | 165
2018-06-10 12:30 | 157 | 157
2018-06-10 13:00 | 157 | 157
2018-06-10 13:30 | 153 | 153
2018-06-10 14:00 | 160 | 160
2018-06-10 14:30 | 179 | 179
2018-06-10 15:00 | 191 | 191
2018-06-10 15:30 | 196 | 196
2018-06-10 16:00 | 203 | 203
2018-06-10 16:30 | 217 | 217
2018-06-10 17:00 | 235 | 235
2018-06-10 17:30 | 255 | 254
2018-06-10 18:00 | 260 | 259
2018-06-10 18:30 | 257 | 256
2018-06-10 19:00 | 256 | 254
2018-06-10 19:30 | 250 | 248
2018-06-10 20:00 | 248 | 246
2018-06-10 20:30 | 246 | 245
2018-06-10 21:00 | 236 | 235
2018-06-10 21:30 | 225 | 225
2018-06-10 22:00 | 218 | 218
2018-06-10 22:30 | 215 | 214
2018-06-10 23:00 | 214 | 214
2018-06-10 23:30 | 203 | 203
2018-06-11 | 187 | 187
2018-06-11 00:30 | 173 | 173
2018-06-11 01:00 | 164 | 164
2018-06-11 01:30 | 158 | 158
2018-06-11 02:00 | 152 | 152
2018-06-11 02:30 | 149 | 149
2018-06-11 03:00 | 148 | 148
2018-06-11 03:30 | 148 | 148
2018-06-11 04:00 | 150 | 150
2018-06-11 04:30 | 157 | 156
2018-06-11 05:00 | 168 | 167
2018-06-11 05:30 | 186 | 184
2018-06-11 06:00 | 202 | 201
2018-06-11 06:30 | 229 | 227
2018-06-11 07:00 | 253 | 253
2018-06-11 07:30 | 269 | 269
2018-06-11 08:00 | 263 | 263
2018-06-11 08:30 | 246 | 246
2018-06-11 09:00 | 230 | 230
2018-06-11 09:30 | 218 | 218
2018-06-11 10:00 | 206 | 206
2018-06-11 10:30 | 197 | 197
2018-06-11 11:00 | 191 | 191
2018-06-11 11:30 | 187 | 187
2018-06-11 12:00 | 186 | 186
2018-06-11 12:30 | 187 | 187
2018-06-11 13:00 | 192 | 192
2018-06-11 13:30 | 197 | 197
2018-06-11 14:00 | 203 | 203
2018-06-11 14:30 | 209 | 209
2018-06-11 15:00 | 216 | 216
2018-06-11 15:30 | 227 | 227
2018-06-11 16:00 | 241 | 241
2018-06-11 16:30 | 254 | 254
2018-06-11 17:00 | 270 | 270
2018-06-11 17:30 | 288 | 288
2018-06-11 18:00 | 298 | 298
2018-06-11 18:30 | 294 | 294
2018-06-11 19:00 | 293 | 293
2018-06-11 19:30 | 287 | 287
2018-06-11 20:00 | 287 | 286
2018-06-11 20:30 | 287 | 286
2018-06-11 21:00 | 274 | 271
2018-06-11 21:30 | 261 | 258
2018-06-11 22:00 | 249 | 247
2018-06-11 22:30 | 240 | 239
2018-06-11 23:00 | 236 | 235
2018-06-11 23:30 | 221 | 221
2018-06-12 | 204 | 204
2018-06-12 00:30 | 188 | 188
2018-06-12 01:00 | 177 | 177
2018-06-12 01:30 | 170 | 170
2018-06-12 02:00 | 165 | 165
2018-06-12 02:30 | 162 | 162
2018-06-12 03:00 | 161 | 161
2018-06-12 03:30 | 161 | 161
2018-06-12 04:00 | 163 | 163
2018-06-12 04:30 | 169 | 169
2018-06-12 05:00 | 181 | 181
2018-06-12 05:30 | 198 | 198
2018-06-12 06:00 | 219 | 218
2018-06-12 06:30 | 248 | 246
2018-06-12 07:00 | 274 | 273
2018-06-12 07:30 | 290 | 289
2018-06-12 08:00 | 286 | 286
2018-06-12 08:30 | 266 | 266
2018-06-12 09:00 | 246 | 246
2018-06-12 09:30 | 244 | 244
2018-06-12 10:00 | 231 | 231
2018-06-12 10:30 | 212 | 212
2018-06-12 11:00 | 201 | 201
2018-06-12 11:30 | 193 | 193
2018-06-12 12:00 | 193 | 192
2018-06-12 12:30 | 193 | 192
2018-06-12 13:00 | 197 | 196
2018-06-12 13:30 | 207 | 206
2018-06-12 14:00 | 214 | 214
2018-06-12 14:30 | 224 | 223
2018-06-12 15:00 | 225 | 225
2018-06-12 15:30 | 232 | 232
2018-06-12 16:00 | 242 | 242
2018-06-12 16:30 | 256 | 256
2018-06-12 17:00 | 275 | 274
2018-06-12 17:30 | 295 | 293
2018-06-12 18:00 | 304 | 304
2018-06-12 18:30 | 300 | 299
2018-06-12 19:00 | 301 | 301
2018-06-12 19:30 | 294 | 294
2018-06-12 20:00 | 293 | 293
2018-06-12 20:30 | 292 | 291
2018-06-12 21:00 | 278 | 276
2018-06-12 21:30 | 264 | 263
2018-06-12 22:00 | 251 | 250
2018-06-12 22:30 | 243 | 242
2018-06-12 23:00 | 238 | 237
2018-06-12 23:30 | 222 | 221
2018-06-13 | 205 | 204
2018-06-13 00:30 | 189 | 189
2018-06-13 01:00 | 178 | 178
2018-06-13 01:30 | 171 | 171
2018-06-13 02:00 | 166 | 165
2018-06-13 02:30 | 163 | 162
2018-06-13 03:00 | 162 | 161
2018-06-13 03:30 | 162 | 161
2018-06-13 04:00 | 164 | 163
2018-06-13 04:30 | 170 | 169
2018-06-13 05:00 | 182 | 180
2018-06-13 05:30 | 200 | 197
2018-06-13 06:00 | 220 | 217
2018-06-13 06:30 | 248 | 248
2018-06-13 07:00 | 273 | 273
2018-06-13 07:30 | 286 | 286
2018-06-13 08:00 | 280 | 280
2018-06-13 08:30 | 264 | 264
2018-06-13 09:00 | 248 | 248
2018-06-13 09:30 | 231 | 231
2018-06-13 10:00 | 220 | 219
2018-06-13 10:30 | 221 | 221
2018-06-13 11:00 | 220 | 220
2018-06-13 11:30 | 223 | 223
2018-06-13 12:00 | 222 | 222
2018-06-13 12:30 | 226 | 226
2018-06-13 13:00 | 230 | 230
2018-06-13 13:30 | 223 | 223
2018-06-13 14:00 | 235 | 235
2018-06-13 14:30 | 240 | 240
2018-06-13 15:00 | 228 | 228
2018-06-13 15:30 | 236 | 236
2018-06-13 16:00 | 254 | 254
2018-06-13 16:30 | 266 | 266
2018-06-13 17:00 | 282 | 282
2018-06-13 17:30 | 296 | 295
2018-06-13 18:00 | 298 | 297
2018-06-13 18:30 | 291 | 291
2018-06-13 19:00 | 292 | 292
2018-06-13 19:30 | 286 | 286
2018-06-13 20:00 | 282 | 282
2018-06-13 20:30 | 278 | 278
2018-06-13 21:00 | 266 | 266
2018-06-13 21:30 | 254 | 254
2018-06-13 22:00 | 243 | 242
2018-06-13 22:30 | 235 | 235
2018-06-13 23:00 | 231 | 231
2018-06-13 23:30 | 218 | 217
2018-06-14 | 200 | 200
2018-06-14 00:30 | 184 | 183
2018-06-14 01:00 | 173 | 173
2018-06-14 01:30 | 165 | 165
2018-06-14 02:00 | 159 | 159
2018-06-14 02:30 | 156 | 156
2018-06-14 03:00 | 155 | 155
2018-06-14 03:30 | 156 | 156
2018-06-14 04:00 | 157 | 156
2018-06-14 04:30 | 162 | 161
2018-06-14 05:00 | 171 | 171
2018-06-14 05:30 | 186 | 186
2018-06-14 06:00 | 203 | 203
2018-06-14 06:30 | 229 | 229
2018-06-14 07:00 | 250 | 249
2018-06-14 07:30 | 264 | 264
2018-06-14 08:00 | 258 | 257
2018-06-14 08:30 | 245 | 244
2018-06-14 09:00 | 235 | 235
2018-06-14 09:30 | 225 | 224
2018-06-14 10:00 | 218 | 217
2018-06-14 10:30 | 220 | 219
2018-06-14 11:00 | 222 | 221
2018-06-14 11:30 | 210 | 209
2018-06-14 12:00 | 209 | 209
2018-06-14 12:30 | 211 | 211
2018-06-14 13:00 | 201 | 201
2018-06-14 13:30 | 206 | 206
2018-06-14 14:00 | 219 | 218
2018-06-14 14:30 | 228 | 227
2018-06-14 15:00 | 229 | 228
2018-06-14 15:30 | 236 | 235
2018-06-14 16:00 | 250 | 250
2018-06-14 16:30 | 260 | 260
2018-06-14 17:00 | 271 | 271
2018-06-14 17:30 | 285 | 285
2018-06-14 18:00 | 290 | 290
2018-06-14 18:30 | 287 | 287
2018-06-14 19:00 | 286 | 286
2018-06-14 19:30 | 281 | 281
2018-06-14 20:00 | 280 | 280
2018-06-14 20:30 | 278 | 278
2018-06-14 21:00 | 266 | 266
2018-06-14 21:30 | 252 | 252
2018-06-14 22:00 | 242 | 242
2018-06-14 22:30 | 235 | 235
2018-06-14 23:00 | 232 | 232
2018-06-14 23:30 | 219 | 218
2018-06-15 | 201 | 201
2018-06-15 00:30 | 186 | 185
2018-06-15 01:00 | 175 | 174
2018-06-15 01:30 | 168 | 167
2018-06-15 02:00 | 163 | 162
2018-06-15 02:30 | 161 | 160
2018-06-15 03:00 | 160 | 159
2018-06-15 03:30 | 160 | 159
2018-06-15 04:00 | 160 | 160
2018-06-15 04:30 | 166 | 165
2018-06-15 05:00 | 175 | 175
2018-06-15 05:30 | 190 | 190
2018-06-15 06:00 | 207 | 207
2018-06-15 06:30 | 235 | 234
2018-06-15 07:00 | 258 | 256
2018-06-15 07:30 | 278 | 277
2018-06-15 08:00 | 275 | 275
2018-06-15 08:30 | 260 | 260
2018-06-15 09:00 | 241 | 241
2018-06-15 09:30 | 224 | 224
2018-06-15 10:00 | 208 | 208
2018-06-15 10:30 | 197 | 197
2018-06-15 11:00 | 191 | 191
2018-06-15 11:30 | 185 | 185
2018-06-15 12:00 | 183 | 182
2018-06-15 12:30 | 181 | 181
2018-06-15 13:00 | 181 | 181
2018-06-15 13:30 | 183 | 183
2018-06-15 14:00 | 190 | 190
2018-06-15 14:30 | 197 | 197
2018-06-15 15:00 | 205 | 205
2018-06-15 15:30 | 215 | 215
2018-06-15 16:00 | 229 | 229
2018-06-15 16:30 | 242 | 241
2018-06-15 17:00 | 256 | 256
2018-06-15 17:30 | 269 | 269
2018-06-15 18:00 | 276 | 276
2018-06-15 18:30 | 273 | 273
2018-06-15 19:00 | 274 | 274
2018-06-15 19:30 | 270 | 270
2018-06-15 20:00 | 270 | 270
2018-06-15 20:30 | 271 | 271
2018-06-15 21:00 | 263 | 263
2018-06-15 21:30 | 253 | 253
2018-06-15 22:00 | 245 | 245
2018-06-15 22:30 | 241 | 240
2018-06-15 23:00 | 238 | 238
2018-06-15 23:30 | 226 | 225
2018-06-16 | 209 | 208
2018-06-16 00:30 | 192 | 192
2018-06-16 01:00 | 181 | 181
2018-06-16 01:30 | 174 | 173
2018-06-16 02:00 | 167 | 167
2018-06-16 02:30 | 164 | 163
2018-06-16 03:00 | 162 | 162
2018-06-16 03:30 | 160 | 160
2018-06-16 04:00 | 160 | 160
2018-06-16 04:30 | 163 | 162
2018-06-16 05:00 | 167 | 166
2018-06-16 05:30 | 175 | 173
2018-06-16 06:00 | 185 | 183
2018-06-16 06:30 | 199 | 196
2018-06-16 07:00 | 210 | 207
2018-06-16 07:30 | 225 | 225
2018-06-16 08:00 | 228 | 228
2018-06-16 08:30 | 226 | 226
2018-06-16 09:00 | 216 | 216
2018-06-16 09:30 | 205 | 204
2018-06-16 10:00 | 188 | 188
2018-06-16 10:30 | 175 | 175
2018-06-16 11:00 | 163 | 163
2018-06-16 11:30 | 154 | 154
2018-06-16 12:00 | 149 | 149
2018-06-16 12:30 | 145 | 145
2018-06-16 13:00 | 145 | 145
2018-06-16 13:30 | 148 | 148
2018-06-16 14:00 | 155 | 155
2018-06-16 14:30 | 162 | 162
2018-06-16 15:00 | 170 | 170
2018-06-16 15:30 | 179 | 179
2018-06-16 16:00 | 192 | 192
2018-06-16 16:30 | 209 | 209
2018-06-16 17:00 | 227 | 226
2018-06-16 17:30 | 245 | 245
2018-06-16 18:00 | 254 | 253
2018-06-16 18:30 | 254 | 253
2018-06-16 19:00 | 255 | 254
2018-06-16 19:30 | 252 | 251
2018-06-16 20:00 | 252 | 252
2018-06-16 20:30 | 251 | 251
2018-06-16 21:00 | 243 | 243
2018-06-16 21:30 | 236 | 236
2018-06-16 22:00 | 230 | 230
2018-06-16 22:30 | 228 | 228
2018-06-16 23:00 | 228 | 228
2018-06-16 23:30 | 218 | 218
2018-06-17 | 203 | 203
2018-06-17 00:30 | 189 | 188
2018-06-17 01:00 | 177 | 177
2018-06-17 01:30 | 169 | 169
2018-06-17 02:00 | 162 | 162
2018-06-17 02:30 | 157 | 157
2018-06-17 03:00 | 155 | 155
2018-06-17 03:30 | 155 | 154
2018-06-17 04:00 | 154 | 153
2018-06-17 04:30 | 154 | 154
2018-06-17 05:00 | 155 | 155
2018-06-17 05:30 | 160 | 160
2018-06-17 06:00 | 167 | 167
2018-06-17 06:30 | 176 | 176
2018-06-17 07:00 | 187 | 186
2018-06-17 07:30 | 201 | 201
2018-06-17 08:00 | 204 | 203
2018-06-17 08:30 | 202 | 202
2018-06-17 09:00 | 197 | 196
2018-06-17 09:30 | 188 | 188
2018-06-17 10:00 | 177 | 177
2018-06-17 10:30 | 167 | 166
2018-06-17 11:00 | 158 | 158
2018-06-17 11:30 | 149 | 149
2018-06-17 12:00 | 145 | 144
2018-06-17 12:30 | 142 | 142
2018-06-17 13:00 | 142 | 142
2018-06-17 13:30 | 145 | 145
2018-06-17 14:00 | 151 | 151
2018-06-17 14:30 | 158 | 158
2018-06-17 15:00 | 168 | 168
2018-06-17 15:30 | 181 | 181
2018-06-17 16:00 | 199 | 198
2018-06-17 16:30 | 218 | 217
2018-06-17 17:00 | 242 | 241
2018-06-17 17:30 | 269 | 269
2018-06-17 18:00 | 284 | 284
2018-06-17 18:30 | 285 | 285
2018-06-17 19:00 | 286 | 286
2018-06-17 19:30 | 283 | 283
2018-06-17 20:00 | 282 | 282
2018-06-17 20:30 | 283 | 282
2018-06-17 21:00 | 270 | 269
2018-06-17 21:30 | 258 | 257
2018-06-17 22:00 | 246 | 246
2018-06-17 22:30 | 237 | 237
2018-06-17 23:00 | 233 | 233
2018-06-17 23:30 | 219 | 219
2018-06-18 | 202 | 202
2018-06-18 00:30 | 188 | 187
2018-06-18 01:00 | 179 | 178
2018-06-18 01:30 | 172 | 171
2018-06-18 02:00 | 168 | 166
2018-06-18 02:30 | 164 | 162
2018-06-18 03:00 | 161 | 160
2018-06-18 03:30 | 162 | 161
2018-06-18 04:00 | 162 | 161
2018-06-18 04:30 | 169 | 168
2018-06-18 05:00 | 181 | 181
2018-06-18 05:30 | 201 | 201
2018-06-18 06:00 | 225 | 224
2018-06-18 06:30 | 258 | 258
2018-06-18 07:00 | 292 | 291
2018-06-18 07:30 | 311 | 310
2018-06-18 08:00 | 305 | 304
2018-06-18 08:30 | 284 | 283
2018-06-18 09:00 | 261 | 261
2018-06-18 09:30 | 245 | 245
2018-06-18 10:00 | 228 | 228
2018-06-18 10:30 | 217 | 217
2018-06-18 11:00 | 206 | 206
2018-06-18 11:30 | 199 | 199
2018-06-18 12:00 | 196 | 196
2018-06-18 12:30 | 194 | 194
2018-06-18 13:00 | 194 | 194
2018-06-18 13:30 | 196 | 196
2018-06-18 14:00 | 202 | 202
2018-06-18 14:30 | 208 | 208
2018-06-18 15:00 | 217 | 217
2018-06-18 15:30 | 228 | 228
2018-06-18 16:00 | 245 | 245
2018-06-18 16:30 | 266 | 266
2018-06-18 17:00 | 294 | 294
2018-06-18 17:30 | 322 | 322
2018-06-18 18:00 | 337 | 336
2018-06-18 18:30 | 337 | 337
2018-06-18 19:00 | 338 | 338
2018-06-18 19:30 | 331 | 331
2018-06-18 20:00 | 329 | 329
2018-06-18 20:30 | 327 | 327
2018-06-18 21:00 | 314 | 313
2018-06-18 21:30 | 296 | 296
2018-06-18 22:00 | 280 | 280
2018-06-18 22:30 | 266 | 266
2018-06-18 23:00 | 257 | 256
2018-06-18 23:30 | 240 | 240
2018-06-19 | 222 | 222
2018-06-19 00:30 | 204 | 204
2018-06-19 01:00 | 192 | 191
2018-06-19 01:30 | 183 | 182
2018-06-19 02:00 | 176 | 176
2018-06-19 02:30 | 173 | 173
2018-06-19 03:00 | 171 | 171
2018-06-19 03:30 | 171 | 171
2018-06-19 04:00 | 173 | 173
2018-06-19 04:30 | 180 | 180
2018-06-19 05:00 | 192 | 192
2018-06-19 05:30 | 213 | 213
2018-06-19 06:00 | 237 | 236
2018-06-19 06:30 | 272 | 271
2018-06-19 07:00 | 305 | 305
2018-06-19 07:30 | 323 | 323
2018-06-19 08:00 | 315 | 314
2018-06-19 08:30 | 292 | 291
2018-06-19 09:00 | 268 | 267
2018-06-19 09:30 | 244 | 244
2018-06-19 10:00 | 229 | 229
2018-06-19 10:30 | 215 | 214
2018-06-19 11:00 | 205 | 204
2018-06-19 11:30 | 195 | 195
2018-06-19 12:00 | 192 | 192
2018-06-19 12:30 | 190 | 190
2018-06-19 13:00 | 193 | 193
2018-06-19 13:30 | 195 | 194
2018-06-19 14:00 | 201 | 200
2018-06-19 14:30 | 208 | 207
2018-06-19 15:00 | 213 | 212
2018-06-19 15:30 | 223 | 222
2018-06-19 16:00 | 240 | 239
2018-06-19 16:30 | 259 | 258
2018-06-19 17:00 | 283 | 282
2018-06-19 17:30 | 312 | 312
2018-06-19 18:00 | 329 | 329
2018-06-19 18:30 | 331 | 331
2018-06-19 19:00 | 334 | 334
2018-06-19 19:30 | 328 | 328
2018-06-19 20:00 | 326 | 325
2018-06-19 20:30 | 325 | 325
2018-06-19 21:00 | 311 | 311
2018-06-19 21:30 | 296 | 296
2018-06-19 22:00 | 278 | 278
2018-06-19 22:30 | 267 | 266
2018-06-19 23:00 | 258 | 258
2018-06-19 23:30 | 243 | 243
2018-06-20 | 223 | 223
2018-06-20 00:30 | 205 | 205
2018-06-20 01:00 | 194 | 194
2018-06-20 01:30 | 184 | 184
2018-06-20 02:00 | 178 | 178
2018-06-20 02:30 | 174 | 174
2018-06-20 03:00 | 171 | 171
2018-06-20 03:30 | 171 | 171
2018-06-20 04:00 | 174 | 174
2018-06-20 04:30 | 182 | 182
2018-06-20 05:00 | 194 | 194
2018-06-20 05:30 | 214 | 213
2018-06-20 06:00 | 238 | 236
2018-06-20 06:30 | 271 | 269
2018-06-20 07:00 | 301 | 300
2018-06-20 07:30 | 322 | 322
2018-06-20 08:00 | 314 | 314
2018-06-20 08:30 | 292 | 292
2018-06-20 09:00 | 268 | 268
2018-06-20 09:30 | 244 | 244
2018-06-20 10:00 | 229 | 229
2018-06-20 10:30 | 215 | 215
2018-06-20 11:00 | 204 | 202
2018-06-20 11:30 | 201 | 198
2018-06-20 12:00 | 199 | 198
2018-06-20 12:30 | 203 | 202
2018-06-20 13:00 | 201 | 200
2018-06-20 13:30 | 214 | 213
2018-06-20 14:00 | 220 | 219
2018-06-20 14:30 | 224 | 223
2018-06-20 15:00 | 224 | 223
2018-06-20 15:30 | 229 | 228
2018-06-20 16:00 | 245 | 245
2018-06-20 16:30 | 257 | 256
2018-06-20 17:00 | 276 | 275
2018-06-20 17:30 | 299 | 298
2018-06-20 18:00 | 312 | 312
2018-06-20 18:30 | 311 | 310
2018-06-20 19:00 | 314 | 314
2018-06-20 19:30 | 309 | 309
2018-06-20 20:00 | 309 | 308
2018-06-20 20:30 | 309 | 307
2018-06-20 21:00 | 297 | 296
2018-06-20 21:30 | 281 | 281
2018-06-20 22:00 | 267 | 267
2018-06-20 22:30 | 257 | 257
2018-06-20 23:00 | 250 | 250
2018-06-20 23:30 | 236 | 235
2018-06-21 | 216 | 216
2018-06-21 00:30 | 199 | 198
2018-06-21 01:00 | 187 | 187
2018-06-21 01:30 | 179 | 179
2018-06-21 02:00 | 172 | 172
2018-06-21 02:30 | 169 | 169
2018-06-21 03:00 | 167 | 167
2018-06-21 03:30 | 167 | 167
2018-06-21 04:00 | 168 | 168
2018-06-21 04:30 | 174 | 174
2018-06-21 05:00 | 186 | 186
2018-06-21 05:30 | 206 | 206
2018-06-21 06:00 | 229 | 228
2018-06-21 06:30 | 261 | 260
2018-06-21 07:00 | 291 | 291
2018-06-21 07:30 | 309 | 309
2018-06-21 08:00 | 301 | 301
2018-06-21 08:30 | 282 | 282
2018-06-21 09:00 | 260 | 260
2018-06-21 09:30 | 242 | 242
2018-06-21 10:00 | 226 | 225
2018-06-21 10:30 | 215 | 215
2018-06-21 11:00 | 209 | 209
2018-06-21 11:30 | 201 | 201
2018-06-21 12:00 | 200 | 200
2018-06-21 12:30 | 207 | 207
2018-06-21 13:00 | 208 | 208
2018-06-21 13:30 | 216 | 215
2018-06-21 14:00 | 229 | 229
2018-06-21 14:30 | 233 | 233
2018-06-21 15:00 | 231 | 230
2018-06-21 15:30 | 234 | 233
2018-06-21 16:00 | 246 | 245
2018-06-21 16:30 | 258 | 258
2018-06-21 17:00 | 276 | 275
2018-06-21 17:30 | 297 | 296
2018-06-21 18:00 | 312 | 310
2018-06-21 18:30 | 313 | 311
2018-06-21 19:00 | 313 | 312
2018-06-21 19:30 | 309 | 308
2018-06-21 20:00 | 307 | 306
2018-06-21 20:30 | 308 | 307
2018-06-21 21:00 | 295 | 295
2018-06-21 21:30 | 279 | 279
2018-06-21 22:00 | 265 | 265
2018-06-21 22:30 | 257 | 257
2018-06-21 23:00 | 252 | 251
2018-06-21 23:30 | 238 | 237
2018-06-22 | 219 | 219
2018-06-22 00:30 | 200 | 200
2018-06-22 01:00 | 187 | 187
2018-06-22 01:30 | 179 | 179
2018-06-22 02:00 | 173 | 173
2018-06-22 02:30 | 170 | 169
2018-06-22 03:00 | 168 | 167
2018-06-22 03:30 | 168 | 167
2018-06-22 04:00 | 169 | 168
2018-06-22 04:30 | 175 | 174
2018-06-22 05:00 | 185 | 185
2018-06-22 05:30 | 203 | 203
2018-06-22 06:00 | 224 | 223
2018-06-22 06:30 | 256 | 256
2018-06-22 07:00 | 284 | 284
2018-06-22 07:30 | 302 | 302
2018-06-22 08:00 | 296 | 296
2018-06-22 08:30 | 277 | 277
2018-06-22 09:00 | 252 | 252
2018-06-22 09:30 | 233 | 233
2018-06-22 10:00 | 219 | 218
2018-06-22 10:30 | 208 | 208
2018-06-22 11:00 | 199 | 198
2018-06-22 11:30 | 190 | 189
2018-06-22 12:00 | 188 | 187
2018-06-22 12:30 | 186 | 186
2018-06-22 13:00 | 188 | 188
2018-06-22 13:30 | 192 | 191
2018-06-22 14:00 | 198 | 198
2018-06-22 14:30 | 202 | 202
2018-06-22 15:00 | 208 | 207
2018-06-22 15:30 | 216 | 216
2018-06-22 16:00 | 230 | 230
2018-06-22 16:30 | 245 | 245
2018-06-22 17:00 | 263 | 262
2018-06-22 17:30 | 280 | 277
2018-06-22 18:00 | 288 | 284
2018-06-22 18:30 | 286 | 282
2018-06-22 19:00 | 289 | 285
2018-06-22 19:30 | 286 | 282
2018-06-22 20:00 | 285 | 280
2018-06-22 20:30 | 285 | 280
2018-06-22 21:00 | 276 | 270
2018-06-22 21:30 | 267 | 263
2018-06-22 22:00 | 257 | 253
2018-06-22 22:30 | 251 | 247
2018-06-22 23:00 | 247 | 243
2018-06-22 23:30 | 232 | 230
2018-06-23 | 214 | 213
2018-06-23 00:30 | 196 | 195
2018-06-23 01:00 | 184 | 183
2018-06-23 01:30 | 176 | 176
2018-06-23 02:00 | 170 | 169
2018-06-23 02:30 | 165 | 165
2018-06-23 03:00 | 163 | 162
2018-06-23 03:30 | 162 | 160
2018-06-23 04:00 | 162 | 161
2018-06-23 04:30 | 163 | 162
2018-06-23 05:00 | 167 | 166
2018-06-23 05:30 | 175 | 173
2018-06-23 06:00 | 184 | 182
2018-06-23 06:30 | 198 | 195
2018-06-23 07:00 | 208 | 208
2018-06-23 07:30 | 222 | 222
2018-06-23 08:00 | 227 | 226
2018-06-23 08:30 | 227 | 227
2018-06-23 09:00 | 219 | 219
2018-06-23 09:30 | 211 | 211
2018-06-23 10:00 | 198 | 197
2018-06-23 10:30 | 189 | 187
2018-06-23 11:00 | 175 | 175
2018-06-23 11:30 | 165 | 165
2018-06-23 12:00 | 159 | 159
2018-06-23 12:30 | 152 | 152
2018-06-23 13:00 | 153 | 153
2018-06-23 13:30 | 155 | 155
2018-06-23 14:00 | 159 | 159
2018-06-23 14:30 | 166 | 166
2018-06-23 15:00 | 173 | 173
2018-06-23 15:30 | 182 | 182
2018-06-23 16:00 | 196 | 196
2018-06-23 16:30 | 206 | 206
2018-06-23 17:00 | 227 | 227
2018-06-23 17:30 | 244 | 244
2018-06-23 18:00 | 254 | 254
2018-06-23 18:30 | 257 | 257
2018-06-23 19:00 | 258 | 258
2018-06-23 19:30 | 255 | 255
2018-06-23 20:00 | 256 | 256
2018-06-23 20:30 | 257 | 257
2018-06-23 21:00 | 250 | 250
2018-06-23 21:30 | 240 | 240
2018-06-23 22:00 | 235 | 235
2018-06-23 22:30 | 233 | 232
2018-06-23 23:00 | 231 | 231
2018-06-23 23:30 | 220 | 220
2018-06-24 | 205 | 205
2018-06-24 00:30 | 190 | 190
2018-06-24 01:00 | 179 | 179
2018-06-24 01:30 | 171 | 171
2018-06-24 02:00 | 164 | 164
2018-06-24 02:30 | 160 | 160
2018-06-24 03:00 | 157 | 157
2018-06-24 03:30 | 156 | 156
2018-06-24 04:00 | 155 | 154
2018-06-24 04:30 | 156 | 156
2018-06-24 05:00 | 158 | 158
2018-06-24 05:30 | 164 | 164
2018-06-24 06:00 | 169 | 169
2018-06-24 06:30 | 179 | 179
2018-06-24 07:00 | 188 | 188
2018-06-24 07:30 | 200 | 200
2018-06-24 08:00 | 206 | 206
2018-06-24 08:30 | 206 | 205
2018-06-24 09:00 | 200 | 200
2018-06-24 09:30 | 189 | 189
2018-06-24 10:00 | 179 | 179
2018-06-24 10:30 | 168 | 168
2018-06-24 11:00 | 158 | 158
2018-06-24 11:30 | 151 | 151
2018-06-24 12:00 | 147 | 146
2018-06-24 12:30 | 145 | 145
2018-06-24 13:00 | 145 | 145
2018-06-24 13:30 | 147 | 147
2018-06-24 14:00 | 153 | 153
2018-06-24 14:30 | 159 | 159
2018-06-24 15:00 | 170 | 170
2018-06-24 15:30 | 181 | 181
2018-06-24 16:00 | 195 | 195
2018-06-24 16:30 | 211 | 211
2018-06-24 17:00 | 233 | 233
2018-06-24 17:30 | 254 | 254
2018-06-24 18:00 | 270 | 270
2018-06-24 18:30 | 273 | 272
2018-06-24 19:00 | 272 | 272
2018-06-24 19:30 | 268 | 268
2018-06-24 20:00 | 270 | 270
2018-06-24 20:30 | 269 | 269
2018-06-24 21:00 | 258 | 257
2018-06-24 21:30 | 249 | 248
2018-06-24 22:00 | 240 | 240
2018-06-24 22:30 | 235 | 234
2018-06-24 23:00 | 232 | 231
2018-06-24 23:30 | 218 | 218
2018-06-25 | 201 | 201
2018-06-25 00:30 | 186 | 185
2018-06-25 01:00 | 176 | 176
2018-06-25 01:30 | 170 | 170
2018-06-25 02:00 | 163 | 163
2018-06-25 02:30 | 159 | 159
2018-06-25 03:00 | 157 | 157
2018-06-25 03:30 | 156 | 156
2018-06-25 04:00 | 158 | 158
2018-06-25 04:30 | 166 | 166
2018-06-25 05:00 | 176 | 176
2018-06-25 05:30 | 196 | 194
2018-06-25 06:00 | 217 | 216
2018-06-25 06:30 | 247 | 246
2018-06-25 07:00 | 273 | 273
2018-06-25 07:30 | 294 | 294
2018-06-25 08:00 | 296 | 296
2018-06-25 08:30 | 285 | 284
2018-06-25 09:00 | 274 | 273
2018-06-25 09:30 | 261 | 260
2018-06-25 10:00 | 242 | 242
2018-06-25 10:30 | 229 | 229
2018-06-25 11:00 | 215 | 215
2018-06-25 11:30 | 202 | 200
2018-06-25 12:00 | 201 | 198
2018-06-25 12:30 | 205 | 204
2018-06-25 13:00 | 212 | 211
2018-06-25 13:30 | 213 | 212
2018-06-25 14:00 | 214 | 213
2018-06-25 14:30 | 218 | 217
2018-06-25 15:00 | 223 | 222
2018-06-25 15:30 | 231 | 230
2018-06-25 16:00 | 244 | 243
2018-06-25 16:30 | 257 | 256
2018-06-25 17:00 | 275 | 275
2018-06-25 17:30 | 298 | 297
2018-06-25 18:00 | 311 | 311
2018-06-25 18:30 | 308 | 308
2018-06-25 19:00 | 306 | 306
2018-06-25 19:30 | 300 | 300
2018-06-25 20:00 | 297 | 297
2018-06-25 20:30 | 295 | 295
2018-06-25 21:00 | 281 | 281
2018-06-25 21:30 | 267 | 267
2018-06-25 22:00 | 255 | 255
2018-06-25 22:30 | 246 | 245
2018-06-25 23:00 | 238 | 237
2018-06-25 23:30 | 223 | 223
2018-06-26 | 206 | 206
2018-06-26 00:30 | 190 | 190
2018-06-26 01:00 | 179 | 179
2018-06-26 01:30 | 170 | 170
2018-06-26 02:00 | 164 | 164
2018-06-26 02:30 | 161 | 161
2018-06-26 03:00 | 160 | 159
2018-06-26 03:30 | 160 | 160
2018-06-26 04:00 | 161 | 161
2018-06-26 04:30 | 167 | 167
2018-06-26 05:00 | 178 | 178
2018-06-26 05:30 | 194 | 194
2018-06-26 06:00 | 211 | 211
2018-06-26 06:30 | 240 | 239
2018-06-26 07:00 | 262 | 262
2018-06-26 07:30 | 276 | 275
2018-06-26 08:00 | 271 | 271
2018-06-26 08:30 | 259 | 259
2018-06-26 09:00 | 249 | 249
2018-06-26 09:30 | 239 | 239
2018-06-26 10:00 | 221 | 221
2018-06-26 10:30 | 213 | 213
2018-06-26 11:00 | 210 | 210
2018-06-26 11:30 | 209 | 209
2018-06-26 12:00 | 212 | 212
2018-06-26 12:30 | 206 | 206
2018-06-26 13:00 | 209 | 209
2018-06-26 13:30 | 217 | 217
2018-06-26 14:00 | 218 | 218
2018-06-26 14:30 | 229 | 229
2018-06-26 15:00 | 234 | 234
2018-06-26 15:30 | 241 | 241
2018-06-26 16:00 | 249 | 249
2018-06-26 16:30 | 263 | 263
2018-06-26 17:00 | 280 | 280
2018-06-26 17:30 | 301 | 301
2018-06-26 18:00 | 307 | 307
2018-06-26 18:30 | 303 | 302
2018-06-26 19:00 | 302 | 302
2018-06-26 19:30 | 296 | 296
2018-06-26 20:00 | 292 | 292
2018-06-26 20:30 | 290 | 290
2018-06-26 21:00 | 277 | 277
2018-06-26 21:30 | 263 | 263
2018-06-26 22:00 | 249 | 248
2018-06-26 22:30 | 239 | 238
2018-06-26 23:00 | 234 | 233
2018-06-26 23:30 | 221 | 221
2018-06-27 | 204 | 204
2018-06-27 00:30 | 190 | 190
2018-06-27 01:00 | 178 | 178
2018-06-27 01:30 | 170 | 170
2018-06-27 02:00 | 163 | 163
2018-06-27 02:30 | 159 | 159
2018-06-27 03:00 | 158 | 157
2018-06-27 03:30 | 158 | 157
2018-06-27 04:00 | 159 | 158
2018-06-27 04:30 | 165 | 164
2018-06-27 05:00 | 174 | 173
2018-06-27 05:30 | 189 | 188
2018-06-27 06:00 | 207 | 205
2018-06-27 06:30 | 232 | 231
2018-06-27 07:00 | 255 | 254
2018-06-27 07:30 | 274 | 274
2018-06-27 08:00 | 280 | 279
2018-06-27 08:30 | 276 | 276
2018-06-27 09:00 | 266 | 266
2018-06-27 09:30 | 258 | 257
2018-06-27 10:00 | 259 | 259
2018-06-27 10:30 | 264 | 263
2018-06-27 11:00 | 264 | 264
2018-06-27 11:30 | 264 | 264
2018-06-27 12:00 | 264 | 263
2018-06-27 12:30 | 263 | 263
2018-06-27 13:00 | 265 | 264
2018-06-27 13:30 | 262 | 262
2018-06-27 14:00 | 261 | 261
2018-06-27 14:30 | 262 | 262
2018-06-27 15:00 | 261 | 261
2018-06-27 15:30 | 267 | 267
2018-06-27 16:00 | 279 | 279
2018-06-27 16:30 | 288 | 288
2018-06-27 17:00 | 301 | 300
2018-06-27 17:30 | 316 | 315
2018-06-27 18:00 | 320 | 320
2018-06-27 18:30 | 318 | 317
2018-06-27 19:00 | 318 | 318
2018-06-27 19:30 | 310 | 310
2018-06-27 20:00 | 306 | 306
2018-06-27 20:30 | 304 | 304
2018-06-27 21:00 | 288 | 288
2018-06-27 21:30 | 272 | 271
2018-06-27 22:00 | 259 | 259
2018-06-27 22:30 | 248 | 248
2018-06-27 23:00 | 242 | 242
2018-06-27 23:30 | 229 | 229
2018-06-28 | 212 | 211
2018-06-28 00:30 | 195 | 194
2018-06-28 01:00 | 182 | 181
2018-06-28 01:30 | 172 | 172
2018-06-28 02:00 | 166 | 166
2018-06-28 02:30 | 162 | 162
2018-06-28 03:00 | 160 | 160
2018-06-28 03:30 | 161 | 161
2018-06-28 04:00 | 161 | 161
2018-06-28 04:30 | 166 | 165
2018-06-28 05:00 | 175 | 175
2018-06-28 05:30 | 192 | 192
2018-06-28 06:00 | 209 | 209
2018-06-28 06:30 | 235 | 234
2018-06-28 07:00 | 256 | 255
2018-06-28 07:30 | 274 | 272
2018-06-28 08:00 | 274 | 274
2018-06-28 08:30 | 267 | 267
2018-06-28 09:00 | 257 | 257
2018-06-28 09:30 | 247 | 247
2018-06-28 10:00 | 239 | 239
2018-06-28 10:30 | 231 | 231
2018-06-28 11:00 | 220 | 220
2018-06-28 11:30 | 218 | 218
2018-06-28 12:00 | 223 | 223
2018-06-28 12:30 | 227 | 227
2018-06-28 13:00 | 223 | 223
2018-06-28 13:30 | 218 | 218
2018-06-28 14:00 | 221 | 221
2018-06-28 14:30 | 223 | 223
2018-06-28 15:00 | 225 | 225
2018-06-28 15:30 | 234 | 234
2018-06-28 16:00 | 245 | 245
2018-06-28 16:30 | 255 | 255
2018-06-28 17:00 | 271 | 271
2018-06-28 17:30 | 286 | 286
2018-06-28 18:00 | 297 | 297
2018-06-28 18:30 | 299 | 299
2018-06-28 19:00 | 299 | 299
2018-06-28 19:30 | 293 | 293
2018-06-28 20:00 | 291 | 291
2018-06-28 20:30 | 292 | 292
2018-06-28 21:00 | 281 | 281
2018-06-28 21:30 | 267 | 267
2018-06-28 22:00 | 256 | 256
2018-06-28 22:30 | 249 | 249
2018-06-28 23:00 | 245 | 244
2018-06-28 23:30 | 227 | 227
2018-06-29 | 210 | 210
2018-06-29 00:30 | 192 | 192
2018-06-29 01:00 | 181 | 181
2018-06-29 01:30 | 174 | 173
2018-06-29 02:00 | 169 | 168
2018-06-29 02:30 | 165 | 164
2018-06-29 03:00 | 164 | 163
2018-06-29 03:30 | 164 | 162
2018-06-29 04:00 | 164 | 163
2018-06-29 04:30 | 169 | 168
2018-06-29 05:00 | 178 | 177
2018-06-29 05:30 | 194 | 194
2018-06-29 06:00 | 209 | 209
2018-06-29 06:30 | 231 | 230
2018-06-29 07:00 | 255 | 255
2018-06-29 07:30 | 274 | 274
2018-06-29 08:00 | 278 | 278
2018-06-29 08:30 | 272 | 272
2018-06-29 09:00 | 260 | 260
2018-06-29 09:30 | 251 | 251
2018-06-29 10:00 | 242 | 242
2018-06-29 10:30 | 231 | 230
2018-06-29 11:00 | 211 | 210
2018-06-29 11:30 | 198 | 196
2018-06-29 12:00 | 190 | 188
2018-06-29 12:30 | 187 | 185
2018-06-29 13:00 | 188 | 187
2018-06-29 13:30 | 191 | 189
2018-06-29 14:00 | 195 | 193
2018-06-29 14:30 | 201 | 199
2018-06-29 15:00 | 208 | 206
2018-06-29 15:30 | 218 | 215
2018-06-29 16:00 | 229 | 227
2018-06-29 16:30 | 240 | 240
2018-06-29 17:00 | 253 | 253
2018-06-29 17:30 | 266 | 266
2018-06-29 18:00 | 272 | 272
2018-06-29 18:30 | 271 | 271
2018-06-29 19:00 | 271 | 271
2018-06-29 19:30 | 266 | 266
2018-06-29 20:00 | 266 | 266
2018-06-29 20:30 | 266 | 266
2018-06-29 21:00 | 256 | 254
2018-06-29 21:30 | 247 | 245
2018-06-29 22:00 | 237 | 236
2018-06-29 22:30 | 231 | 231
2018-06-29 23:00 | 227 | 227
2018-06-29 23:30 | 214 | 214
2018-06-30 | 198 | 198
2018-06-30 00:30 | 181 | 181
2018-06-30 01:00 | 171 | 171
2018-06-30 01:30 | 163 | 163
2018-06-30 02:00 | 156 | 156
2018-06-30 02:30 | 153 | 153
2018-06-30 03:00 | 150 | 149
2018-06-30 03:30 | 150 | 149
2018-06-30 04:00 | 148 | 147
2018-06-30 04:30 | 148 | 148
2018-06-30 05:00 | 152 | 151
2018-06-30 05:30 | 158 | 158
2018-06-30 06:00 | 165 | 165
2018-06-30 06:30 | 176 | 176
2018-06-30 07:00 | 185 | 185
2018-06-30 07:30 | 195 | 195
2018-06-30 08:00 | 201 | 201
2018-06-30 08:30 | 205 | 205
2018-06-30 09:00 | 209 | 209
2018-06-30 09:30 | 207 | 207
2018-06-30 10:00 | 198 | 198
2018-06-30 10:30 | 193 | 193
2018-06-30 11:00 | 181 | 181
2018-06-30 11:30 | 171 | 171
2018-06-30 12:00 | 168 | 168
2018-06-30 12:30 | 159 | 159
2018-06-30 13:00 | 155 | 155
2018-06-30 13:30 | 156 | 156
2018-06-30 14:00 | 164 | 164
2018-06-30 14:30 | 169 | 169
2018-06-30 15:00 | 177 | 177
2018-06-30 15:30 | 184 | 184
2018-06-30 16:00 | 192 | 192
2018-06-30 16:30 | 203 | 203
2018-06-30 17:00 | 221 | 220
2018-06-30 17:30 | 234 | 233
2018-06-30 18:00 | 238 | 237
2018-06-30 18:30 | 237 | 236
2018-06-30 19:00 | 237 | 236
2018-06-30 19:30 | 231 | 230
2018-06-30 20:00 | 229 | 228
2018-06-30 20:30 | 228 | 228
2018-06-30 21:00 | 219 | 218
2018-06-30 21:30 | 213 | 212
2018-06-30 22:00 | 208 | 208
2018-06-30 22:30 | 206 | 206
2018-06-30 23:00 | 208 | 208
2018-06-30 23:30 | 197 | 197
2018-07-01 | 183 | 183
2018-07-01 00:30 | 170 | 169
2018-07-01 01:00 | 160 | 160
2018-07-01 01:30 | 155 | 154
2018-07-01 02:00 | 154 | 153
2018-07-01 02:30 | 150 | 149
2018-07-01 03:00 | 147 | 146
2018-07-01 03:30 | 146 | 145
2018-07-01 04:00 | 145 | 145
2018-07-01 04:30 | 145 | 144
2018-07-01 05:00 | 147 | 146
2018-07-01 05:30 | 150 | 149
2018-07-01 06:00 | 154 | 153
2018-07-01 06:30 | 161 | 161
2018-07-01 07:00 | 166 | 166
2018-07-01 07:30 | 177 | 176
2018-07-01 08:00 | 184 | 184
2018-07-01 08:30 | 190 | 190
2018-07-01 09:00 | 193 | 193
2018-07-01 09:30 | 196 | 196
2018-07-01 10:00 | 192 | 192
2018-07-01 10:30 | 191 | 191
2018-07-01 11:00 | 189 | 189
2018-07-01 11:30 | 191 | 191
2018-07-01 12:00 | 197 | 197
2018-07-01 12:30 | 195 | 195
2018-07-01 13:00 | 188 | 188
2018-07-01 13:30 | 191 | 191
2018-07-01 14:00 | 199 | 199
2018-07-01 14:30 | 207 | 207
2018-07-01 15:00 | 208 | 207
2018-07-01 15:30 | 210 | 210
2018-07-01 16:00 | 213 | 213
2018-07-01 16:30 | 221 | 220
2018-07-01 17:00 | 235 | 234
2018-07-01 17:30 | 250 | 249
2018-07-01 18:00 | 260 | 260
2018-07-01 18:30 | 258 | 258
2018-07-01 19:00 | 256 | 256
2018-07-01 19:30 | 249 | 249
2018-07-01 20:00 | 245 | 244
2018-07-01 20:30 | 245 | 244
2018-07-01 21:00 | 236 | 235
2018-07-01 21:30 | 226 | 226
2018-07-01 22:00 | 219 | 219
2018-07-01 22:30 | 215 | 215
2018-07-01 23:00 | 214 | 213
2018-07-01 23:30 | 202 | 202
2018-07-02 | 186 | 186
2018-07-02 00:30 | 172 | 172
2018-07-02 01:00 | 164 | 163
2018-07-02 01:30 | 157 | 157
2018-07-02 02:00 | 152 | 152
2018-07-02 02:30 | 150 | 149
2018-07-02 03:00 | 148 | 147
2018-07-02 03:30 | 148 | 147
2018-07-02 04:00 | 148 | 147
2018-07-02 04:30 | 154 | 153
2018-07-02 05:00 | 162 | 162
2018-07-02 05:30 | 177 | 177
2018-07-02 06:00 | 192 | 192
2018-07-02 06:30 | 214 | 213
2018-07-02 07:00 | 231 | 230
2018-07-02 07:30 | 248 | 247
2018-07-02 08:00 | 252 | 252
2018-07-02 08:30 | 251 | 251
2018-07-02 09:00 | 243 | 243
2018-07-02 09:30 | 233 | 233
2018-07-02 10:00 | 221 | 221
2018-07-02 10:30 | 218 | 218
2018-07-02 11:00 | 206 | 206
2018-07-02 11:30 | 209 | 209
2018-07-02 12:00 | 210 | 210
2018-07-02 12:30 | 212 | 212
2018-07-02 13:00 | 217 | 217
2018-07-02 13:30 | 221 | 221
2018-07-02 14:00 | 220 | 220
2018-07-02 14:30 | 230 | 229
2018-07-02 15:00 | 225 | 225
2018-07-02 15:30 | 231 | 230
2018-07-02 16:00 | 248 | 248
2018-07-02 16:30 | 258 | 258
2018-07-02 17:00 | 277 | 276
2018-07-02 17:30 | 291 | 291
2018-07-02 18:00 | 295 | 295
2018-07-02 18:30 | 290 | 289
2018-07-02 19:00 | 288 | 288
2018-07-02 19:30 | 281 | 280
2018-07-02 20:00 | 275 | 275
2018-07-02 20:30 | 273 | 273
2018-07-02 21:00 | 262 | 262
2018-07-02 21:30 | 251 | 251
2018-07-02 22:00 | 240 | 240
2018-07-02 22:30 | 231 | 231
2018-07-02 23:00 | 228 | 228
2018-07-02 23:30 | 217 | 217
2018-07-03 | 202 | 202
2018-07-03 00:30 | 185 | 185
2018-07-03 01:00 | 175 | 175
2018-07-03 01:30 | 169 | 168
2018-07-03 02:00 | 163 | 163
2018-07-03 02:30 | 160 | 160
2018-07-03 03:00 | 158 | 157
2018-07-03 03:30 | 158 | 158
2018-07-03 04:00 | 158 | 158
2018-07-03 04:30 | 163 | 163
2018-07-03 05:00 | 172 | 172
2018-07-03 05:30 | 187 | 187
2018-07-03 06:00 | 201 | 201
2018-07-03 06:30 | 224 | 222
2018-07-03 07:00 | 240 | 239
2018-07-03 07:30 | 253 | 253
2018-07-03 08:00 | 253 | 253
2018-07-03 08:30 | 246 | 246
2018-07-03 09:00 | 235 | 235
2018-07-03 09:30 | 223 | 223
2018-07-03 10:00 | 212 | 212
2018-07-03 10:30 | 203 | 203
2018-07-03 11:00 | 196 | 196
2018-07-03 11:30 | 191 | 190
2018-07-03 12:00 | 191 | 191
2018-07-03 12:30 | 190 | 190
2018-07-03 13:00 | 194 | 193
2018-07-03 13:30 | 202 | 202
2018-07-03 14:00 | 213 | 213
2018-07-03 14:30 | 215 | 215
2018-07-03 15:00 | 218 | 217
2018-07-03 15:30 | 225 | 225
2018-07-03 16:00 | 237 | 237
2018-07-03 16:30 | 249 | 249
2018-07-03 17:00 | 264 | 264
2018-07-03 17:30 | 278 | 278
2018-07-03 18:00 | 290 | 290
2018-07-03 18:30 | 288 | 288
2018-07-03 19:00 | 289 | 288
2018-07-03 19:30 | 282 | 282
2018-07-03 20:00 | 281 | 281
2018-07-03 20:30 | 279 | 279
2018-07-03 21:00 | 267 | 267
2018-07-03 21:30 | 255 | 255
2018-07-03 22:00 | 246 | 245
2018-07-03 22:30 | 240 | 239
2018-07-03 23:00 | 232 | 232
2018-07-03 23:30 | 218 | 218
2018-07-04 | 202 | 202
2018-07-04 00:30 | 186 | 186
2018-07-04 01:00 | 175 | 175
2018-07-04 01:30 | 167 | 167
2018-07-04 02:00 | 162 | 162
2018-07-04 02:30 | 158 | 158
2018-07-04 03:00 | 156 | 155
2018-07-04 03:30 | 155 | 155
2018-07-04 04:00 | 156 | 156
2018-07-04 04:30 | 161 | 160
2018-07-04 05:00 | 169 | 169
2018-07-04 05:30 | 184 | 184
2018-07-04 06:00 | 198 | 198
2018-07-04 06:30 | 218 | 217
2018-07-04 07:00 | 234 | 232
2018-07-04 07:30 | 251 | 251
2018-07-04 08:00 | 255 | 255
2018-07-04 08:30 | 254 | 253
2018-07-04 09:00 | 244 | 244
2018-07-04 09:30 | 230 | 230
2018-07-04 10:00 | 215 | 214
2018-07-04 10:30 | 212 | 210
2018-07-04 11:00 | 216 | 213
2018-07-04 11:30 | 206 | 204
2018-07-04 12:00 | 201 | 199
2018-07-04 12:30 | 196 | 194
2018-07-04 13:00 | 194 | 191
2018-07-04 13:30 | 198 | 195
2018-07-04 14:00 | 202 | 200
2018-07-04 14:30 | 210 | 208
2018-07-04 15:00 | 219 | 216
2018-07-04 15:30 | 228 | 226
2018-07-04 16:00 | 237 | 237
2018-07-04 16:30 | 249 | 249
2018-07-04 17:00 | 260 | 260
2018-07-04 17:30 | 273 | 272
2018-07-04 18:00 | 283 | 282
2018-07-04 18:30 | 280 | 279
2018-07-04 19:00 | 280 | 280
2018-07-04 19:30 | 274 | 274
2018-07-04 20:00 | 271 | 271
2018-07-04 20:30 | 270 | 270
2018-07-04 21:00 | 260 | 260
2018-07-04 21:30 | 252 | 252
2018-07-04 22:00 | 242 | 242
2018-07-04 22:30 | 235 | 235
2018-07-04 23:00 | 229 | 229
2018-07-04 23:30 | 217 | 216
2018-07-05 | 199 | 199
2018-07-05 00:30 | 183 | 183
2018-07-05 01:00 | 174 | 174
2018-07-05 01:30 | 167 | 166
2018-07-05 02:00 | 162 | 162
2018-07-05 02:30 | 158 | 158
2018-07-05 03:00 | 156 | 156
2018-07-05 03:30 | 156 | 156
2018-07-05 04:00 | 157 | 156
2018-07-05 04:30 | 160 | 160
2018-07-05 05:00 | 169 | 169
2018-07-05 05:30 | 182 | 182
2018-07-05 06:00 | 195 | 195
2018-07-05 06:30 | 215 | 214
2018-07-05 07:00 | 230 | 229
2018-07-05 07:30 | 246 | 246
2018-07-05 08:00 | 248 | 248
2018-07-05 08:30 | 245 | 245
2018-07-05 09:00 | 236 | 236
2018-07-05 09:30 | 232 | 232
2018-07-05 10:00 | 237 | 237
2018-07-05 10:30 | 241 | 241
2018-07-05 11:00 | 236 | 236
2018-07-05 11:30 | 231 | 231
2018-07-05 12:00 | 235 | 235
2018-07-05 12:30 | 232 | 232
2018-07-05 13:00 | 237 | 237
2018-07-05 13:30 | 235 | 235
2018-07-05 14:00 | 235 | 235
2018-07-05 14:30 | 244 | 244
2018-07-05 15:00 | 248 | 248
2018-07-05 15:30 | 249 | 249
2018-07-05 16:00 | 252 | 252
2018-07-05 16:30 | 259 | 259
2018-07-05 17:00 | 270 | 270
2018-07-05 17:30 | 281 | 281
2018-07-05 18:00 | 289 | 289
2018-07-05 18:30 | 286 | 286
2018-07-05 19:00 | 286 | 286
2018-07-05 19:30 | 279 | 279
2018-07-05 20:00 | 276 | 276
2018-07-05 20:30 | 274 | 274
2018-07-05 21:00 | 263 | 263
2018-07-05 21:30 | 248 | 246
2018-07-05 22:00 | 238 | 238
2018-07-05 22:30 | 232 | 232
2018-07-05 23:00 | 228 | 228
2018-07-05 23:30 | 216 | 216
2018-07-06 | 200 | 200
2018-07-06 00:30 | 183 | 183
2018-07-06 01:00 | 172 | 172
2018-07-06 01:30 | 165 | 165
2018-07-06 02:00 | 160 | 160
2018-07-06 02:30 | 158 | 158
2018-07-06 03:00 | 156 | 156
2018-07-06 03:30 | 156 | 156
2018-07-06 04:00 | 155 | 155
2018-07-06 04:30 | 160 | 160
2018-07-06 05:00 | 166 | 166
2018-07-06 05:30 | 179 | 179
2018-07-06 06:00 | 191 | 191
2018-07-06 06:30 | 211 | 210
2018-07-06 07:00 | 225 | 223
2018-07-06 07:30 | 237 | 237
2018-07-06 08:00 | 241 | 241
2018-07-06 08:30 | 240 | 239
2018-07-06 09:00 | 234 | 233
2018-07-06 09:30 | 230 | 230
2018-07-06 10:00 | 236 | 236
2018-07-06 10:30 | 240 | 240
2018-07-06 11:00 | 237 | 236
2018-07-06 11:30 | 227 | 227
2018-07-06 12:00 | 228 | 227
2018-07-06 12:30 | 228 | 228
2018-07-06 13:00 | 225 | 224
2018-07-06 13:30 | 218 | 217
2018-07-06 14:00 | 228 | 227
2018-07-06 14:30 | 233 | 232
2018-07-06 15:00 | 231 | 230
2018-07-06 15:30 | 239 | 238
2018-07-06 16:00 | 245 | 244
2018-07-06 16:30 | 253 | 251
2018-07-06 17:00 | 262 | 261
2018-07-06 17:30 | 269 | 267
2018-07-06 18:00 | 271 | 270
2018-07-06 18:30 | 266 | 266
2018-07-06 19:00 | 266 | 265
2018-07-06 19:30 | 259 | 258
2018-07-06 20:00 | 257 | 256
2018-07-06 20:30 | 256 | 255
2018-07-06 21:00 | 247 | 246
2018-07-06 21:30 | 238 | 237
2018-07-06 22:00 | 230 | 230
2018-07-06 22:30 | 228 | 227
2018-07-06 23:00 | 226 | 225
2018-07-06 23:30 | 214 | 214
2018-07-07 | 198 | 198
2018-07-07 00:30 | 182 | 182
2018-07-07 01:00 | 172 | 171
2018-07-07 01:30 | 165 | 165
2018-07-07 02:00 | 158 | 158
2018-07-07 02:30 | 155 | 155
2018-07-07 03:00 | 152 | 152
2018-07-07 03:30 | 150 | 150
2018-07-07 04:00 | 149 | 149
2018-07-07 04:30 | 151 | 151
2018-07-07 05:00 | 151 | 151
2018-07-07 05:30 | 156 | 156
2018-07-07 06:00 | 161 | 161
2018-07-07 06:30 | 170 | 170
2018-07-07 07:00 | 176 | 176
2018-07-07 07:30 | 187 | 186
2018-07-07 08:00 | 195 | 195
2018-07-07 08:30 | 203 | 202
2018-07-07 09:00 | 209 | 208
2018-07-07 09:30 | 210 | 209
2018-07-07 10:00 | 212 | 211
2018-07-07 10:30 | 214 | 213
2018-07-07 11:00 | 206 | 206
2018-07-07 11:30 | 196 | 195
2018-07-07 12:00 | 186 | 186
2018-07-07 12:30 | 197 | 197
2018-07-07 13:00 | 203 | 203
2018-07-07 13:30 | 204 | 203
2018-07-07 14:00 | 194 | 194
2018-07-07 14:30 | 190 | 190
2018-07-07 15:00 | 181 | 181
2018-07-07 15:30 | 187 | 187
2018-07-07 16:00 | 197 | 197
2018-07-07 16:30 | 205 | 205
2018-07-07 17:00 | 223 | 222
2018-07-07 17:30 | 232 | 232
2018-07-07 18:00 | 242 | 241
2018-07-07 18:30 | 240 | 239
2018-07-07 19:00 | 238 | 237
2018-07-07 19:30 | 230 | 230
2018-07-07 20:00 | 229 | 228
2018-07-07 20:30 | 230 | 230
2018-07-07 21:00 | 221 | 221
2018-07-07 21:30 | 214 | 214
2018-07-07 22:00 | 210 | 210
2018-07-07 22:30 | 210 | 210
2018-07-07 23:00 | 210 | 210
2018-07-07 23:30 | 202 | 202
2018-07-08 | 188 | 188
2018-07-08 00:30 | 173 | 173
2018-07-08 01:00 | 163 | 163
2018-07-08 01:30 | 156 | 156
2018-07-08 02:00 | 150 | 150
2018-07-08 02:30 | 146 | 146
2018-07-08 03:00 | 144 | 144
2018-07-08 03:30 | 142 | 142
2018-07-08 04:00 | 141 | 141
2018-07-08 04:30 | 141 | 141
2018-07-08 05:00 | 143 | 143
2018-07-08 05:30 | 147 | 147
2018-07-08 06:00 | 153 | 153
2018-07-08 06:30 | 162 | 162
2018-07-08 07:00 | 170 | 170
2018-07-08 07:30 | 179 | 178
2018-07-08 08:00 | 182 | 181
2018-07-08 08:30 | 183 | 182
2018-07-08 09:00 | 179 | 179
2018-07-08 09:30 | 171 | 171
2018-07-08 10:00 | 162 | 161
2018-07-08 10:30 | 151 | 151
2018-07-08 11:00 | 142 | 141
2018-07-08 11:30 | 135 | 135
2018-07-08 12:00 | 133 | 133
2018-07-08 12:30 | 131 | 130
2018-07-08 13:00 | 130 | 129
2018-07-08 13:30 | 133 | 133
2018-07-08 14:00 | 137 | 137
2018-07-08 14:30 | 145 | 145
2018-07-08 15:00 | 155 | 155
2018-07-08 15:30 | 168 | 167
2018-07-08 16:00 | 184 | 183
2018-07-08 16:30 | 201 | 200
2018-07-08 17:00 | 222 | 221
2018-07-08 17:30 | 244 | 243
2018-07-08 18:00 | 261 | 259
2018-07-08 18:30 | 265 | 263
2018-07-08 19:00 | 266 | 265
2018-07-08 19:30 | 262 | 261
2018-07-08 20:00 | 262 | 260
2018-07-08 20:30 | 262 | 260
2018-07-08 21:00 | 252 | 251
2018-07-08 21:30 | 243 | 242
2018-07-08 22:00 | 233 | 232
2018-07-08 22:30 | 228 | 228
2018-07-08 23:00 | 224 | 223
2018-07-08 23:30 | 212 | 212
2018-07-09 | 196 | 196
2018-07-09 00:30 | 180 | 180
2018-07-09 01:00 | 171 | 171
2018-07-09 01:30 | 164 | 164
2018-07-09 02:00 | 158 | 158
2018-07-09 02:30 | 155 | 154
2018-07-09 03:00 | 152 | 152
2018-07-09 03:30 | 153 | 152
2018-07-09 04:00 | 156 | 156
2018-07-09 04:30 | 169 | 169
2018-07-09 05:00 | 180 | 178
2018-07-09 05:30 | 199 | 196
2018-07-09 06:00 | 218 | 215
2018-07-09 06:30 | 241 | 241
2018-07-09 07:00 | 263 | 263
2018-07-09 07:30 | 279 | 279
2018-07-09 08:00 | 277 | 277
2018-07-09 08:30 | 269 | 269
2018-07-09 09:00 | 253 | 253
2018-07-09 09:30 | 237 | 237
2018-07-09 10:00 | 219 | 219
2018-07-09 10:30 | 205 | 205
2018-07-09 11:00 | 193 | 193
2018-07-09 11:30 | 187 | 186
2018-07-09 12:00 | 180 | 180
2018-07-09 12:30 | 178 | 177
2018-07-09 13:00 | 176 | 175
2018-07-09 13:30 | 180 | 179
2018-07-09 14:00 | 185 | 184
2018-07-09 14:30 | 198 | 198
2018-07-09 15:00 | 210 | 209
2018-07-09 15:30 | 221 | 221
2018-07-09 16:00 | 233 | 232
2018-07-09 16:30 | 242 | 242
2018-07-09 17:00 | 259 | 259
2018-07-09 17:30 | 281 | 281
2018-07-09 18:00 | 298 | 298
2018-07-09 18:30 | 301 | 301
2018-07-09 19:00 | 302 | 302
2018-07-09 19:30 | 297 | 297
2018-07-09 20:00 | 296 | 296
2018-07-09 20:30 | 294 | 294
2018-07-09 21:00 | 282 | 282
2018-07-09 21:30 | 269 | 269
2018-07-09 22:00 | 255 | 255
2018-07-09 22:30 | 246 | 246
2018-07-09 23:00 | 240 | 240
2018-07-09 23:30 | 226 | 226
2018-07-10 | 209 | 209
2018-07-10 00:30 | 191 | 191
2018-07-10 01:00 | 180 | 180
2018-07-10 01:30 | 171 | 171
2018-07-10 02:00 | 165 | 164
2018-07-10 02:30 | 161 | 160
2018-07-10 03:00 | 158 | 158
2018-07-10 03:30 | 160 | 159
2018-07-10 04:00 | 161 | 161
2018-07-10 04:30 | 166 | 166
2018-07-10 05:00 | 176 | 176
2018-07-10 05:30 | 196 | 196
2018-07-10 06:00 | 221 | 221
2018-07-10 06:30 | 241 | 241
2018-07-10 07:00 | 263 | 263
2018-07-10 07:30 | 279 | 279
2018-07-10 08:00 | 283 | 283
2018-07-10 08:30 | 278 | 278
2018-07-10 09:00 | 269 | 269
2018-07-10 09:30 | 250 | 250
2018-07-10 10:00 | 228 | 228
2018-07-10 10:30 | 211 | 211
2018-07-10 11:00 | 194 | 194
2018-07-10 11:30 | 188 | 188
2018-07-10 12:00 | 185 | 185
2018-07-10 12:30 | 187 | 187
2018-07-10 13:00 | 192 | 192
2018-07-10 13:30 | 192 | 192
2018-07-10 14:00 | 199 | 199
2018-07-10 14:30 | 206 | 205
2018-07-10 15:00 | 214 | 213
2018-07-10 15:30 | 218 | 217
2018-07-10 16:00 | 229 | 229
2018-07-10 16:30 | 244 | 244
2018-07-10 17:00 | 262 | 262
2018-07-10 17:30 | 281 | 280
2018-07-10 18:00 | 294 | 294
2018-07-10 18:30 | 295 | 294
2018-07-10 19:00 | 296 | 295
2018-07-10 19:30 | 290 | 289
2018-07-10 20:00 | 290 | 290
2018-07-10 20:30 | 291 | 290
2018-07-10 21:00 | 279 | 279
2018-07-10 21:30 | 266 | 266
2018-07-10 22:00 | 255 | 255
2018-07-10 22:30 | 245 | 245
2018-07-10 23:00 | 239 | 239
2018-07-10 23:30 | 225 | 225
2018-07-11 | 208 | 208
2018-07-11 00:30 | 190 | 190
2018-07-11 01:00 | 178 | 178
2018-07-11 01:30 | 170 | 170
2018-07-11 02:00 | 164 | 164
2018-07-11 02:30 | 160 | 160
2018-07-11 03:00 | 159 | 159
2018-07-11 03:30 | 158 | 158
2018-07-11 04:00 | 159 | 159
2018-07-11 04:30 | 166 | 165
2018-07-11 05:00 | 176 | 175
2018-07-11 05:30 | 194 | 193
2018-07-11 06:00 | 213 | 211
2018-07-11 06:30 | 239 | 239
2018-07-11 07:00 | 261 | 261
2018-07-11 07:30 | 279 | 279
2018-07-11 08:00 | 278 | 277
2018-07-11 08:30 | 265 | 265
2018-07-11 09:00 | 249 | 249
2018-07-11 09:30 | 237 | 237
2018-07-11 10:00 | 221 | 221
2018-07-11 10:30 | 205 | 204
2018-07-11 11:00 | 199 | 199
2018-07-11 11:30 | 203 | 203
2018-07-11 12:00 | 202 | 202
2018-07-11 12:30 | 209 | 209
2018-07-11 13:00 | 215 | 215
2018-07-11 13:30 | 220 | 220
2018-07-11 14:00 | 224 | 224
2018-07-11 14:30 | 238 | 238
2018-07-11 15:00 | 244 | 244
2018-07-11 15:30 | 247 | 247
2018-07-11 16:00 | 251 | 251
2018-07-11 16:30 | 261 | 260
2018-07-11 17:00 | 273 | 273
2018-07-11 17:30 | 288 | 288
2018-07-11 18:00 | 298 | 298
2018-07-11 18:30 | 298 | 298
2018-07-11 19:00 | 299 | 299
2018-07-11 19:30 | 292 | 292
2018-07-11 20:00 | 290 | 290
2018-07-11 20:30 | 288 | 287
2018-07-11 21:00 | 275 | 274
2018-07-11 21:30 | 263 | 263
2018-07-11 22:00 | 250 | 250
2018-07-11 22:30 | 246 | 246
2018-07-11 23:00 | 246 | 245
2018-07-11 23:30 | 231 | 231
2018-07-12 | 206 | 206
2018-07-12 00:30 | 187 | 187
2018-07-12 01:00 | 174 | 174
2018-07-12 01:30 | 167 | 166
2018-07-12 02:00 | 160 | 160
2018-07-12 02:30 | 156 | 156
2018-07-12 03:00 | 154 | 153
2018-07-12 03:30 | 154 | 153
2018-07-12 04:00 | 155 | 154
2018-07-12 04:30 | 160 | 160
2018-07-12 05:00 | 169 | 169
2018-07-12 05:30 | 184 | 184
2018-07-12 06:00 | 199 | 199
2018-07-12 06:30 | 219 | 219
2018-07-12 07:00 | 238 | 237
2018-07-12 07:30 | 255 | 254
2018-07-12 08:00 | 260 | 260
2018-07-12 08:30 | 265 | 264
2018-07-12 09:00 | 261 | 259
2018-07-12 09:30 | 254 | 252
2018-07-12 10:00 | 237 | 236
2018-07-12 10:30 | 213 | 212
2018-07-12 11:00 | 199 | 199
2018-07-12 11:30 | 190 | 190
2018-07-12 12:00 | 188 | 187
2018-07-12 12:30 | 192 | 190
2018-07-12 13:00 | 199 | 198
2018-07-12 13:30 | 205 | 205
2018-07-12 14:00 | 212 | 212
2018-07-12 14:30 | 216 | 215
2018-07-12 15:00 | 218 | 217
2018-07-12 15:30 | 221 | 220
2018-07-12 16:00 | 228 | 227
2018-07-12 16:30 | 239 | 238
2018-07-12 17:00 | 253 | 252
2018-07-12 17:30 | 269 | 268
2018-07-12 18:00 | 285 | 283
2018-07-12 18:30 | 287 | 287
2018-07-12 19:00 | 287 | 287
2018-07-12 19:30 | 283 | 283
2018-07-12 20:00 | 285 | 284
2018-07-12 20:30 | 286 | 285
2018-07-12 21:00 | 275 | 274
2018-07-12 21:30 | 263 | 263
2018-07-12 22:00 | 249 | 249
2018-07-12 22:30 | 243 | 243
2018-07-12 23:00 | 237 | 237
2018-07-12 23:30 | 224 | 224
2018-07-13 | 208 | 208
2018-07-13 00:30 | 188 | 187
2018-07-13 01:00 | 176 | 175
2018-07-13 01:30 | 168 | 167
2018-07-13 02:00 | 163 | 162
2018-07-13 02:30 | 160 | 159
2018-07-13 03:00 | 158 | 157
2018-07-13 03:30 | 158 | 157
2018-07-13 04:00 | 159 | 158
2018-07-13 04:30 | 162 | 161
2018-07-13 05:00 | 173 | 171
2018-07-13 05:30 | 189 | 186
2018-07-13 06:00 | 205 | 205
2018-07-13 06:30 | 229 | 228
2018-07-13 07:00 | 248 | 247
2018-07-13 07:30 | 262 | 260
2018-07-13 08:00 | 261 | 259
2018-07-13 08:30 | 252 | 250
2018-07-13 09:00 | 241 | 239
2018-07-13 09:30 | 223 | 223
2018-07-13 10:00 | 207 | 206
2018-07-13 10:30 | 195 | 194
2018-07-13 11:00 | 186 | 186
2018-07-13 11:30 | 178 | 176
2018-07-13 12:00 | 175 | 169
2018-07-13 12:30 | 172 | 167
2018-07-13 13:00 | 173 | 168
2018-07-13 13:30 | 175 | 170
2018-07-13 14:00 | 179 | 174
2018-07-13 14:30 | 186 | 181
2018-07-13 15:00 | 192 | 188
2018-07-13 15:30 | 204 | 199
2018-07-13 16:00 | 218 | 213
2018-07-13 16:30 | 231 | 227
2018-07-13 17:00 | 247 | 244
2018-07-13 17:30 | 264 | 264
2018-07-13 18:00 | 280 | 278
2018-07-13 18:30 | 284 | 283
2018-07-13 19:00 | 290 | 290
2018-07-13 19:30 | 289 | 289
2018-07-13 20:00 | 293 | 293
2018-07-13 20:30 | 295 | 295
2018-07-13 21:00 | 286 | 286
2018-07-13 21:30 | 276 | 276
2018-07-13 22:00 | 267 | 267
2018-07-13 22:30 | 262 | 261
2018-07-13 23:00 | 257 | 257
2018-07-13 23:30 | 241 | 241
2018-07-14 | 221 | 221
2018-07-14 00:30 | 201 | 200
2018-07-14 01:00 | 188 | 187
2018-07-14 01:30 | 179 | 177
2018-07-14 02:00 | 172 | 171
2018-07-14 02:30 | 167 | 166
2018-07-14 03:00 | 164 | 163
2018-07-14 03:30 | 162 | 162
2018-07-14 04:00 | 161 | 160
2018-07-14 04:30 | 164 | 163
2018-07-14 05:00 | 168 | 167
2018-07-14 05:30 | 178 | 176
2018-07-14 06:00 | 188 | 186
2018-07-14 06:30 | 203 | 200
2018-07-14 07:00 | 218 | 217
2018-07-14 07:30 | 233 | 233
2018-07-14 08:00 | 240 | 240
2018-07-14 08:30 | 240 | 240
2018-07-14 09:00 | 233 | 232
2018-07-14 09:30 | 218 | 218
2018-07-14 10:00 | 202 | 201
2018-07-14 10:30 | 182 | 182
2018-07-14 11:00 | 170 | 170
2018-07-14 11:30 | 159 | 159
2018-07-14 12:00 | 149 | 149
2018-07-14 12:30 | 144 | 144
2018-07-14 13:00 | 142 | 142
2018-07-14 13:30 | 144 | 144
2018-07-14 14:00 | 147 | 146
2018-07-14 14:30 | 153 | 153
2018-07-14 15:00 | 161 | 161
2018-07-14 15:30 | 172 | 172
2018-07-14 16:00 | 187 | 187
2018-07-14 16:30 | 205 | 205
2018-07-14 17:00 | 228 | 228
2018-07-14 17:30 | 250 | 250
2018-07-14 18:00 | 267 | 267
2018-07-14 18:30 | 275 | 275
2018-07-14 19:00 | 279 | 278
2018-07-14 19:30 | 278 | 277
2018-07-14 20:00 | 279 | 278
2018-07-14 20:30 | 281 | 280
2018-07-14 21:00 | 273 | 273
2018-07-14 21:30 | 264 | 263
2018-07-14 22:00 | 256 | 256
2018-07-14 22:30 | 250 | 250
2018-07-14 23:00 | 247 | 247
2018-07-14 23:30 | 237 | 237
2018-07-15 | 221 | 220
2018-07-15 00:30 | 204 | 203
2018-07-15 01:00 | 192 | 191
2018-07-15 01:30 | 182 | 182
2018-07-15 02:00 | 174 | 173
2018-07-15 02:30 | 170 | 169
2018-07-15 03:00 | 166 | 165
2018-07-15 03:30 | 163 | 163
2018-07-15 04:00 | 163 | 163
2018-07-15 04:30 | 168 | 167
2018-07-15 05:00 | 171 | 171
2018-07-15 05:30 | 173 | 173
2018-07-15 06:00 | 180 | 179
2018-07-15 06:30 | 190 | 190
2018-07-15 07:00 | 202 | 202
2018-07-15 07:30 | 217 | 217
2018-07-15 08:00 | 227 | 227
2018-07-15 08:30 | 229 | 228
2018-07-15 09:00 | 222 | 222
2018-07-15 09:30 | 212 | 210
2018-07-15 10:00 | 198 | 196
2018-07-15 10:30 | 183 | 181
2018-07-15 11:00 | 167 | 166
2018-07-15 11:30 | 154 | 154
2018-07-15 12:00 | 145 | 145
2018-07-15 12:30 | 140 | 140
2018-07-15 13:00 | 138 | 138
2018-07-15 13:30 | 140 | 140
2018-07-15 14:00 | 144 | 144
2018-07-15 14:30 | 150 | 150
2018-07-15 15:00 | 160 | 160
2018-07-15 15:30 | 173 | 173
2018-07-15 16:00 | 190 | 189
2018-07-15 16:30 | 210 | 210
2018-07-15 17:00 | 236 | 236
2018-07-15 17:30 | 262 | 262
2018-07-15 18:00 | 283 | 283
2018-07-15 18:30 | 290 | 290
2018-07-15 19:00 | 292 | 292
2018-07-15 19:30 | 289 | 289
2018-07-15 20:00 | 289 | 289
2018-07-15 20:30 | 290 | 290
2018-07-15 21:00 | 278 | 278
2018-07-15 21:30 | 264 | 264
2018-07-15 22:00 | 253 | 252
2018-07-15 22:30 | 242 | 241
2018-07-15 23:00 | 236 | 236
2018-07-15 23:30 | 224 | 223
2018-07-16 | 207 | 206
2018-07-16 00:30 | 193 | 191
2018-07-16 01:00 | 181 | 180
2018-07-16 01:30 | 174 | 174
2018-07-16 02:00 | 168 | 167
2018-07-16 02:30 | 164 | 163
2018-07-16 03:00 | 161 | 161
2018-07-16 03:30 | 160 | 160
2018-07-16 04:00 | 162 | 162
2018-07-16 04:30 | 168 | 168
2018-07-16 05:00 | 179 | 179
2018-07-16 05:30 | 200 | 199
2018-07-16 06:00 | 223 | 221
2018-07-16 06:30 | 260 | 258
2018-07-16 07:00 | 291 | 290
2018-07-16 07:30 | 310 | 310
2018-07-16 08:00 | 300 | 300
2018-07-16 08:30 | 278 | 278
2018-07-16 09:00 | 256 | 256
2018-07-16 09:30 | 241 | 241
2018-07-16 10:00 | 225 | 224
2018-07-16 10:30 | 209 | 209
2018-07-16 11:00 | 195 | 195
2018-07-16 11:30 | 185 | 185
2018-07-16 12:00 | 180 | 180
2018-07-16 12:30 | 178 | 178
2018-07-16 13:00 | 179 | 179
2018-07-16 13:30 | 182 | 181
2018-07-16 14:00 | 187 | 186
2018-07-16 14:30 | 194 | 194
2018-07-16 15:00 | 206 | 206
2018-07-16 15:30 | 215 | 215
2018-07-16 16:00 | 228 | 228
2018-07-16 16:30 | 246 | 246
2018-07-16 17:00 | 266 | 266
2018-07-16 17:30 | 285 | 284
2018-07-16 18:00 | 304 | 303
2018-07-16 18:30 | 307 | 307
2018-07-16 19:00 | 310 | 310
2018-07-16 19:30 | 307 | 307
2018-07-16 20:00 | 307 | 307
2018-07-16 20:30 | 308 | 308
2018-07-16 21:00 | 296 | 296
2018-07-16 21:30 | 282 | 282
2018-07-16 22:00 | 266 | 266
2018-07-16 22:30 | 257 | 256
2018-07-16 23:00 | 250 | 250
2018-07-16 23:30 | 234 | 234
2018-07-17 | 217 | 215
2018-07-17 00:30 | 199 | 199
2018-07-17 01:00 | 188 | 188
2018-07-17 01:30 | 181 | 181
2018-07-17 02:00 | 175 | 174
2018-07-17 02:30 | 170 | 170
2018-07-17 03:00 | 169 | 168
2018-07-17 03:30 | 168 | 168
2018-07-17 04:00 | 170 | 170
2018-07-17 04:30 | 177 | 177
2018-07-17 05:00 | 190 | 190
2018-07-17 05:30 | 213 | 211
2018-07-17 06:00 | 237 | 236
2018-07-17 06:30 | 273 | 273
2018-07-17 07:00 | 306 | 306
2018-07-17 07:30 | 323 | 323
2018-07-17 08:00 | 314 | 314
2018-07-17 08:30 | 290 | 290
2018-07-17 09:00 | 263 | 262
2018-07-17 09:30 | 242 | 242
2018-07-17 10:00 | 222 | 222
2018-07-17 10:30 | 205 | 205
2018-07-17 11:00 | 195 | 195
2018-07-17 11:30 | 187 | 187
2018-07-17 12:00 | 186 | 186
2018-07-17 12:30 | 181 | 181
2018-07-17 13:00 | 184 | 184
2018-07-17 13:30 | 190 | 190
2018-07-17 14:00 | 187 | 187
2018-07-17 14:30 | 192 | 192
2018-07-17 15:00 | 199 | 199
2018-07-17 15:30 | 209 | 209
2018-07-17 16:00 | 225 | 225
2018-07-17 16:30 | 242 | 242
2018-07-17 17:00 | 262 | 262
2018-07-17 17:30 | 283 | 283
2018-07-17 18:00 | 305 | 304
2018-07-17 18:30 | 309 | 308
2018-07-17 19:00 | 315 | 314
2018-07-17 19:30 | 313 | 312
2018-07-17 20:00 | 314 | 313
2018-07-17 20:30 | 315 | 313
2018-07-17 21:00 | 304 | 303
2018-07-17 21:30 | 290 | 290
2018-07-17 22:00 | 274 | 274
2018-07-17 22:30 | 263 | 262
2018-07-17 23:00 | 254 | 254
2018-07-17 23:30 | 239 | 239
2018-07-18 | 221 | 220
2018-07-18 00:30 | 202 | 202
2018-07-18 01:00 | 190 | 189
2018-07-18 01:30 | 181 | 180
2018-07-18 02:00 | 175 | 174
2018-07-18 02:30 | 171 | 170
2018-07-18 03:00 | 169 | 168
2018-07-18 03:30 | 169 | 168
2018-07-18 04:00 | 171 | 170
2018-07-18 04:30 | 178 | 177
2018-07-18 05:00 | 190 | 190
2018-07-18 05:30 | 212 | 212
2018-07-18 06:00 | 237 | 237
2018-07-18 06:30 | 275 | 274
2018-07-18 07:00 | 312 | 312
2018-07-18 07:30 | 333 | 333
2018-07-18 08:00 | 323 | 323
2018-07-18 08:30 | 290 | 290
2018-07-18 09:00 | 196 | 195
2018-07-18 09:30 | 181 | 180
2018-07-18 10:00 | 167 | 167
2018-07-18 10:30 | 156 | 155
2018-07-18 11:00 | 147 | 147
2018-07-18 11:30 | 140 | 140
2018-07-18 12:00 | 136 | 136
2018-07-18 12:30 | 186 | 186
2018-07-18 13:00 | 189 | 186
2018-07-18 13:30 | 192 | 189
2018-07-18 14:00 | 195 | 192
2018-07-18 14:30 | 202 | 199
2018-07-18 15:00 | 210 | 207
2018-07-18 15:30 | 220 | 216
2018-07-18 16:00 | 235 | 234
2018-07-18 16:30 | 251 | 251
2018-07-18 17:00 | 269 | 269
2018-07-18 17:30 | 288 | 287
2018-07-18 18:00 | 308 | 308
2018-07-18 18:30 | 313 | 313
2018-07-18 19:00 | 320 | 320
2018-07-18 19:30 | 318 | 318
2018-07-18 20:00 | 318 | 318
2018-07-18 20:30 | 321 | 321
2018-07-18 21:00 | 309 | 308
2018-07-18 21:30 | 295 | 294
2018-07-18 22:00 | 281 | 281
2018-07-18 22:30 | 270 | 269
2018-07-18 23:00 | 261 | 260
2018-07-18 23:30 | 247 | 246
2018-07-19 | 229 | 228
2018-07-19 00:30 | 211 | 211
2018-07-19 01:00 | 198 | 198
2018-07-19 01:30 | 190 | 190
2018-07-19 02:00 | 183 | 183
2018-07-19 02:30 | 180 | 180
2018-07-19 03:00 | 178 | 178
2018-07-19 03:30 | 179 | 179
2018-07-19 04:00 | 180 | 180
2018-07-19 04:30 | 189 | 189
2018-07-19 05:00 | 200 | 200
2018-07-19 05:30 | 222 | 221
2018-07-19 06:00 | 247 | 247
2018-07-19 06:30 | 282 | 281
2018-07-19 07:00 | 314 | 314
2018-07-19 07:30 | 335 | 335
2018-07-19 08:00 | 327 | 327
2018-07-19 08:30 | 301 | 301
2018-07-19 09:00 | 201 | 201
2018-07-19 09:30 | 185 | 185
2018-07-19 10:00 | 169 | 169
2018-07-19 10:30 | 157 | 157
2018-07-19 11:00 | 148 | 146
2018-07-19 11:30 | 140 | 138
2018-07-19 12:00 | 136 | 134
2018-07-19 12:30 | 144 | 142
2018-07-19 13:00 | 188 | 187
2018-07-19 13:30 | 190 | 189
2018-07-19 14:00 | 195 | 194
2018-07-19 14:30 | 201 | 200
2018-07-19 15:00 | 208 | 207
2018-07-19 15:30 | 218 | 216
2018-07-19 16:00 | 231 | 229
2018-07-19 16:30 | 248 | 246
2018-07-19 17:00 | 267 | 265
2018-07-19 17:30 | 285 | 283
2018-07-19 18:00 | 304 | 302
2018-07-19 18:30 | 310 | 309
2018-07-19 19:00 | 314 | 313
2018-07-19 19:30 | 312 | 311
2018-07-19 20:00 | 312 | 311
2018-07-19 20:30 | 313 | 312
2018-07-19 21:00 | 302 | 302
2018-07-19 21:30 | 287 | 287
2018-07-19 22:00 | 272 | 272
2018-07-19 22:30 | 262 | 261
2018-07-19 23:00 | 255 | 255
2018-07-19 23:30 | 240 | 239
2018-07-20 | 220 | 218
2018-07-20 00:30 | 201 | 200
2018-07-20 01:00 | 190 | 188
2018-07-20 01:30 | 181 | 180
2018-07-20 02:00 | 175 | 174
2018-07-20 02:30 | 171 | 170
2018-07-20 03:00 | 169 | 168
2018-07-20 03:30 | 169 | 169
2018-07-20 04:00 | 170 | 169
2018-07-20 04:30 | 177 | 176
2018-07-20 05:00 | 187 | 186
2018-07-20 05:30 | 206 | 205
2018-07-20 06:00 | 228 | 226
2018-07-20 06:30 | 259 | 259
2018-07-20 07:00 | 285 | 284
2018-07-20 07:30 | 303 | 301
2018-07-20 08:00 | 309 | 308
2018-07-20 08:30 | 288 | 288
2018-07-20 09:00 | 256 | 256
2018-07-20 09:30 | 172 | 172
2018-07-20 10:00 | 163 | 163
2018-07-20 10:30 | 153 | 153
2018-07-20 11:00 | 145 | 145
2018-07-20 11:30 | 140 | 139
2018-07-20 12:00 | 169 | 168
2018-07-20 12:30 | 213 | 212
2018-07-20 13:00 | 229 | 227
2018-07-20 13:30 | 209 | 208
2018-07-20 14:00 | 226 | 224
2018-07-20 14:30 | 249 | 247
2018-07-20 15:00 | 246 | 244
2018-07-20 15:30 | 234 | 232
2018-07-20 16:00 | 239 | 238
2018-07-20 16:30 | 249 | 248
2018-07-20 17:00 | 260 | 258
2018-07-20 17:30 | 272 | 271
2018-07-20 18:00 | 286 | 286
2018-07-20 18:30 | 287 | 287
2018-07-20 19:00 | 287 | 287
2018-07-20 19:30 | 282 | 282
2018-07-20 20:00 | 282 | 282
2018-07-20 20:30 | 282 | 282
2018-07-20 21:00 | 272 | 272
2018-07-20 21:30 | 263 | 263
2018-07-20 22:00 | 252 | 252
2018-07-20 22:30 | 247 | 247
2018-07-20 23:00 | 244 | 244
2018-07-20 23:30 | 231 | 231
2018-07-21 | 213 | 212
2018-07-21 00:30 | 196 | 196
2018-07-21 01:00 | 184 | 184
2018-07-21 01:30 | 175 | 175
2018-07-21 02:00 | 169 | 169
2018-07-21 02:30 | 165 | 165
2018-07-21 03:00 | 163 | 163
2018-07-21 03:30 | 162 | 162
2018-07-21 04:00 | 162 | 162
2018-07-21 04:30 | 162 | 162
2018-07-21 05:00 | 167 | 167
2018-07-21 05:30 | 174 | 174
2018-07-21 06:00 | 183 | 183
2018-07-21 06:30 | 197 | 197
2018-07-21 07:00 | 211 | 211
2018-07-21 07:30 | 223 | 223
2018-07-21 08:00 | 225 | 225
2018-07-21 08:30 | 223 | 223
2018-07-21 09:00 | 214 | 214
2018-07-21 09:30 | 202 | 202
2018-07-21 10:00 | 189 | 189
2018-07-21 10:30 | 175 | 175
2018-07-21 11:00 | 164 | 164
2018-07-21 11:30 | 154 | 154
2018-07-21 12:00 | 148 | 147
2018-07-21 12:30 | 143 | 143
2018-07-21 13:00 | 143 | 142
2018-07-21 13:30 | 144 | 144
2018-07-21 14:00 | 149 | 149
2018-07-21 14:30 | 156 | 156
2018-07-21 15:00 | 164 | 164
2018-07-21 15:30 | 176 | 176
2018-07-21 16:00 | 191 | 191
2018-07-21 16:30 | 208 | 208
2018-07-21 17:00 | 230 | 230
2018-07-21 17:30 | 250 | 250
2018-07-21 18:00 | 269 | 269
2018-07-21 18:30 | 277 | 276
2018-07-21 19:00 | 280 | 279
2018-07-21 19:30 | 278 | 276
2018-07-21 20:00 | 280 | 278
2018-07-21 20:30 | 281 | 280
2018-07-21 21:00 | 273 | 272
2018-07-21 21:30 | 265 | 264
2018-07-21 22:00 | 260 | 259
2018-07-21 22:30 | 256 | 255
2018-07-21 23:00 | 252 | 251
2018-07-21 23:30 | 240 | 239
2018-07-22 | 225 | 224
2018-07-22 00:30 | 207 | 207
2018-07-22 01:00 | 194 | 194
2018-07-22 01:30 | 184 | 184
2018-07-22 02:00 | 177 | 177
2018-07-22 02:30 | 173 | 172
2018-07-22 03:00 | 168 | 167
2018-07-22 03:30 | 165 | 165
2018-07-22 04:00 | 162 | 162
2018-07-22 04:30 | 162 | 162
2018-07-22 05:00 | 163 | 163
2018-07-22 05:30 | 168 | 168
2018-07-22 06:00 | 175 | 175
2018-07-22 06:30 | 187 | 186
2018-07-22 07:00 | 197 | 197
2018-07-22 07:30 | 209 | 208
2018-07-22 08:00 | 213 | 213
2018-07-22 08:30 | 213 | 213
2018-07-22 09:00 | 208 | 208
2018-07-22 09:30 | 198 | 198
2018-07-22 10:00 | 190 | 190
2018-07-22 10:30 | 174 | 174
2018-07-22 11:00 | 161 | 161
2018-07-22 11:30 | 151 | 151
2018-07-22 12:00 | 149 | 149
2018-07-22 12:30 | 153 | 153
2018-07-22 13:00 | 151 | 151
2018-07-22 13:30 | 151 | 151
2018-07-22 14:00 | 153 | 153
2018-07-22 14:30 | 160 | 159
2018-07-22 15:00 | 169 | 169
2018-07-22 15:30 | 180 | 180
2018-07-22 16:00 | 194 | 194
2018-07-22 16:30 | 213 | 213
2018-07-22 17:00 | 235 | 235
2018-07-22 17:30 | 254 | 254
2018-07-22 18:00 | 277 | 276
2018-07-22 18:30 | 285 | 283
2018-07-22 19:00 | 286 | 284
2018-07-22 19:30 | 283 | 281
2018-07-22 20:00 | 283 | 281
2018-07-22 20:30 | 284 | 283
2018-07-22 21:00 | 273 | 273
2018-07-22 21:30 | 260 | 260
2018-07-22 22:00 | 250 | 250
2018-07-22 22:30 | 241 | 241
2018-07-22 23:00 | 236 | 236
2018-07-22 23:30 | 223 | 223
2018-07-23 | 205 | 205
2018-07-23 00:30 | 189 | 189
2018-07-23 01:00 | 178 | 178
2018-07-23 01:30 | 172 | 172
2018-07-23 02:00 | 165 | 165
2018-07-23 02:30 | 162 | 162
2018-07-23 03:00 | 161 | 160
2018-07-23 03:30 | 161 | 160
2018-07-23 04:00 | 162 | 162
2018-07-23 04:30 | 170 | 169
2018-07-23 05:00 | 181 | 181
2018-07-23 05:30 | 203 | 203
2018-07-23 06:00 | 226 | 226
2018-07-23 06:30 | 261 | 260
2018-07-23 07:00 | 292 | 292
2018-07-23 07:30 | 312 | 312
2018-07-23 08:00 | 304 | 304
2018-07-23 08:30 | 282 | 282
2018-07-23 09:00 | 255 | 255
2018-07-23 09:30 | 234 | 234
2018-07-23 10:00 | 217 | 216
2018-07-23 10:30 | 204 | 203
2018-07-23 11:00 | 193 | 193
2018-07-23 11:30 | 187 | 186
2018-07-23 12:00 | 187 | 186
2018-07-23 12:30 | 189 | 189
2018-07-23 13:00 | 188 | 188
2018-07-23 13:30 | 192 | 192
2018-07-23 14:00 | 197 | 197
2018-07-23 14:30 | 204 | 204
2018-07-23 15:00 | 208 | 208
2018-07-23 15:30 | 214 | 214
2018-07-23 16:00 | 227 | 227
2018-07-23 16:30 | 244 | 244
2018-07-23 17:00 | 261 | 261
2018-07-23 17:30 | 283 | 283
2018-07-23 18:00 | 306 | 305
2018-07-23 18:30 | 311 | 310
2018-07-23 19:00 | 312 | 311
2018-07-23 19:30 | 309 | 308
2018-07-23 20:00 | 308 | 307
2018-07-23 20:30 | 308 | 307
2018-07-23 21:00 | 294 | 292
2018-07-23 21:30 | 277 | 276
2018-07-23 22:00 | 264 | 263
2018-07-23 22:30 | 253 | 253
2018-07-23 23:00 | 246 | 246
2018-07-23 23:30 | 231 | 230
2018-07-24 | 214 | 214
2018-07-24 00:30 | 197 | 197
2018-07-24 01:00 | 185 | 185
2018-07-24 01:30 | 175 | 175
2018-07-24 02:00 | 169 | 169
2018-07-24 02:30 | 166 | 166
2018-07-24 03:00 | 164 | 164
2018-07-24 03:30 | 163 | 163
2018-07-24 04:00 | 165 | 164
2018-07-24 04:30 | 172 | 172
2018-07-24 05:00 | 185 | 185
2018-07-24 05:30 | 205 | 204
2018-07-24 06:00 | 230 | 227
2018-07-24 06:30 | 265 | 264
2018-07-24 07:00 | 295 | 295
2018-07-24 07:30 | 313 | 313
2018-07-24 08:00 | 304 | 304
2018-07-24 08:30 | 281 | 280
2018-07-24 09:00 | 254 | 254
2018-07-24 09:30 | 233 | 233
2018-07-24 10:00 | 212 | 212
2018-07-24 10:30 | 200 | 199
2018-07-24 11:00 | 189 | 189
2018-07-24 11:30 | 181 | 181
2018-07-24 12:00 | 176 | 176
2018-07-24 12:30 | 173 | 173
2018-07-24 13:00 | 173 | 173
2018-07-24 13:30 | 177 | 177
2018-07-24 14:00 | 182 | 182
2018-07-24 14:30 | 190 | 190
2018-07-24 15:00 | 197 | 197
2018-07-24 15:30 | 206 | 206
2018-07-24 16:00 | 224 | 223
2018-07-24 16:30 | 238 | 237
2018-07-24 17:00 | 254 | 253
2018-07-24 17:30 | 271 | 269
2018-07-24 18:00 | 289 | 287
2018-07-24 18:30 | 291 | 290
2018-07-24 19:00 | 292 | 290
2018-07-24 19:30 | 289 | 289
2018-07-24 20:00 | 289 | 289
2018-07-24 20:30 | 287 | 287
2018-07-24 21:00 | 276 | 276
2018-07-24 21:30 | 264 | 264
2018-07-24 22:00 | 254 | 254
2018-07-24 22:30 | 246 | 246
2018-07-24 23:00 | 240 | 240
2018-07-24 23:30 | 222 | 222
2018-07-25 | 206 | 206
2018-07-25 00:30 | 189 | 189
2018-07-25 01:00 | 178 | 178
2018-07-25 01:30 | 169 | 169
2018-07-25 02:00 | 163 | 163
2018-07-25 02:30 | 160 | 160
2018-07-25 03:00 | 158 | 158
2018-07-25 03:30 | 158 | 158
2018-07-25 04:00 | 161 | 161
2018-07-25 04:30 | 168 | 168
2018-07-25 05:00 | 179 | 179
2018-07-25 05:30 | 199 | 198
2018-07-25 06:00 | 220 | 220
2018-07-25 06:30 | 252 | 251
2018-07-25 07:00 | 278 | 278
2018-07-25 07:30 | 294 | 293
2018-07-25 08:00 | 295 | 295
2018-07-25 08:30 | 267 | 267
2018-07-25 09:00 | 198 | 198
2018-07-25 09:30 | 192 | 192
2018-07-25 10:00 | 184 | 184
2018-07-25 10:30 | 173 | 173
2018-07-25 11:00 | 162 | 162
2018-07-25 11:30 | 149 | 149
2018-07-25 12:00 | 193 | 193
2018-07-25 12:30 | 191 | 191
2018-07-25 13:00 | 191 | 191
2018-07-25 13:30 | 206 | 206
2018-07-25 14:00 | 220 | 219
2018-07-25 14:30 | 220 | 220
2018-07-25 15:00 | 224 | 224
2018-07-25 15:30 | 230 | 230
2018-07-25 16:00 | 242 | 242
2018-07-25 16:30 | 249 | 249
2018-07-25 17:00 | 264 | 264
2018-07-25 17:30 | 280 | 280
2018-07-25 18:00 | 295 | 295
2018-07-25 18:30 | 296 | 296
2018-07-25 19:00 | 296 | 296
2018-07-25 19:30 | 291 | 291
2018-07-25 20:00 | 290 | 290
2018-07-25 20:30 | 288 | 288
2018-07-25 21:00 | 277 | 277
2018-07-25 21:30 | 263 | 262
2018-07-25 22:00 | 248 | 248
2018-07-25 22:30 | 240 | 239
2018-07-25 23:00 | 234 | 234
2018-07-25 23:30 | 220 | 220
2018-07-26 | 203 | 203
2018-07-26 00:30 | 185 | 185
2018-07-26 01:00 | 173 | 173
2018-07-26 01:30 | 166 | 165
2018-07-26 02:00 | 159 | 159
2018-07-26 02:30 | 156 | 155
2018-07-26 03:00 | 154 | 154
2018-07-26 03:30 | 154 | 154
2018-07-26 04:00 | 155 | 154
2018-07-26 04:30 | 159 | 159
2018-07-26 05:00 | 168 | 168
2018-07-26 05:30 | 185 | 185
2018-07-26 06:00 | 203 | 202
2018-07-26 06:30 | 232 | 232
2018-07-26 07:00 | 254 | 254
2018-07-26 07:30 | 272 | 272
2018-07-26 08:00 | 267 | 267
2018-07-26 08:30 | 213 | 213
2018-07-26 09:00 | 165 | 165
2018-07-26 09:30 | 154 | 154
2018-07-26 10:00 | 146 | 146
2018-07-26 10:30 | 140 | 140
2018-07-26 11:00 | 132 | 132
2018-07-26 11:30 | 148 | 144
2018-07-26 12:00 | 181 | 177
2018-07-26 12:30 | 181 | 177
2018-07-26 13:00 | 183 | 179
2018-07-26 13:30 | 187 | 183
2018-07-26 14:00 | 191 | 187
2018-07-26 14:30 | 199 | 194
2018-07-26 15:00 | 206 | 201
2018-07-26 15:30 | 213 | 211
2018-07-26 16:00 | 226 | 225
2018-07-26 16:30 | 239 | 238
2018-07-26 17:00 | 252 | 251
2018-07-26 17:30 | 265 | 265
2018-07-26 18:00 | 280 | 280
2018-07-26 18:30 | 280 | 280
2018-07-26 19:00 | 281 | 281
2018-07-26 19:30 | 278 | 277
2018-07-26 20:00 | 277 | 276
2018-07-26 20:30 | 276 | 275
2018-07-26 21:00 | 267 | 266
2018-07-26 21:30 | 253 | 253
2018-07-26 22:00 | 242 | 242
2018-07-26 22:30 | 236 | 236
2018-07-26 23:00 | 232 | 232
2018-07-26 23:30 | 219 | 219
2018-07-27 | 199 | 199
2018-07-27 00:30 | 181 | 181
2018-07-27 01:00 | 171 | 170
2018-07-27 01:30 | 164 | 163
2018-07-27 02:00 | 155 | 154
2018-07-27 02:30 | 149 | 149
2018-07-27 03:00 | 147 | 147
2018-07-27 03:30 | 151 | 151
2018-07-27 04:00 | 154 | 154
2018-07-27 04:30 | 158 | 158
2018-07-27 05:00 | 167 | 166
2018-07-27 05:30 | 185 | 184
2018-07-27 06:00 | 203 | 202
2018-07-27 06:30 | 229 | 227
2018-07-27 07:00 | 254 | 252
2018-07-27 07:30 | 269 | 268
2018-07-27 08:00 | 262 | 261
2018-07-27 08:30 | 203 | 202
2018-07-27 09:00 | 163 | 162
2018-07-27 09:30 | 151 | 151
2018-07-27 10:00 | 143 | 143
2018-07-27 10:30 | 136 | 136
2018-07-27 11:00 | 131 | 131
2018-07-27 11:30 | 177 | 177
2018-07-27 12:00 | 175 | 175
2018-07-27 12:30 | 170 | 170
2018-07-27 13:00 | 174 | 174
2018-07-27 13:30 | 176 | 175
2018-07-27 14:00 | 178 | 177
2018-07-27 14:30 | 186 | 186
2018-07-27 15:00 | 191 | 191
2018-07-27 15:30 | 198 | 198
2018-07-27 16:00 | 216 | 216
2018-07-27 16:30 | 230 | 229
2018-07-27 17:00 | 245 | 244
2018-07-27 17:30 | 254 | 253
2018-07-27 18:00 | 264 | 262
2018-07-27 18:30 | 262 | 261
2018-07-27 19:00 | 263 | 262
2018-07-27 19:30 | 257 | 257
2018-07-27 20:00 | 256 | 255
2018-07-27 20:30 | 255 | 254
2018-07-27 21:00 | 245 | 244
2018-07-27 21:30 | 236 | 236
2018-07-27 22:00 | 227 | 226
2018-07-27 22:30 | 219 | 218
2018-07-27 23:00 | 219 | 217
2018-07-27 23:30 | 206 | 205
2018-07-28 | 189 | 189
2018-07-28 00:30 | 174 | 174
2018-07-28 01:00 | 164 | 164
2018-07-28 01:30 | 156 | 156
2018-07-28 02:00 | 151 | 151
2018-07-28 02:30 | 147 | 147
2018-07-28 03:00 | 145 | 145
2018-07-28 03:30 | 144 | 144
2018-07-28 04:00 | 143 | 142
2018-07-28 04:30 | 145 | 144
2018-07-28 05:00 | 147 | 146
2018-07-28 05:30 | 154 | 154
2018-07-28 06:00 | 162 | 161
2018-07-28 06:30 | 173 | 171
2018-07-28 07:00 | 181 | 180
2018-07-28 07:30 | 189 | 188
2018-07-28 08:00 | 192 | 190
2018-07-28 08:30 | 189 | 186
2018-07-28 09:00 | 184 | 182
2018-07-28 09:30 | 176 | 174
2018-07-28 10:00 | 166 | 164
2018-07-28 10:30 | 158 | 156
2018-07-28 11:00 | 152 | 151
2018-07-28 11:30 | 147 | 146
2018-07-28 12:00 | 145 | 143
2018-07-28 12:30 | 142 | 139
2018-07-28 13:00 | 143 | 140
2018-07-28 13:30 | 145 | 142
2018-07-28 14:00 | 149 | 146
2018-07-28 14:30 | 157 | 155
2018-07-28 15:00 | 167 | 164
2018-07-28 15:30 | 174 | 171
2018-07-28 16:00 | 187 | 184
2018-07-28 16:30 | 199 | 197
2018-07-28 17:00 | 214 | 214
2018-07-28 17:30 | 222 | 221
2018-07-28 18:00 | 232 | 232
2018-07-28 18:30 | 235 | 235
2018-07-28 19:00 | 236 | 236
2018-07-28 19:30 | 230 | 230
2018-07-28 20:00 | 227 | 226
2018-07-28 20:30 | 226 | 225
2018-07-28 21:00 | 217 | 216
2018-07-28 21:30 | 210 | 210
2018-07-28 22:00 | 205 | 205
2018-07-28 22:30 | 202 | 202
2018-07-28 23:00 | 205 | 205
2018-07-28 23:30 | 194 | 194
2018-07-29 | 181 | 181
2018-07-29 00:30 | 168 | 168
2018-07-29 01:00 | 158 | 158
2018-07-29 01:30 | 151 | 151
2018-07-29 02:00 | 145 | 145
2018-07-29 02:30 | 142 | 142
2018-07-29 03:00 | 138 | 138
2018-07-29 03:30 | 137 | 137
2018-07-29 04:00 | 136 | 136
2018-07-29 04:30 | 137 | 136
2018-07-29 05:00 | 138 | 138
2018-07-29 05:30 | 142 | 142
2018-07-29 06:00 | 146 | 146
2018-07-29 06:30 | 154 | 154
2018-07-29 07:00 | 160 | 160
2018-07-29 07:30 | 170 | 170
2018-07-29 08:00 | 175 | 175
2018-07-29 08:30 | 177 | 177
2018-07-29 09:00 | 175 | 175
2018-07-29 09:30 | 167 | 167
2018-07-29 10:00 | 155 | 155
2018-07-29 10:30 | 148 | 148
2018-07-29 11:00 | 140 | 140
2018-07-29 11:30 | 135 | 135
2018-07-29 12:00 | 131 | 131
2018-07-29 12:30 | 127 | 127
2018-07-29 13:00 | 130 | 130
2018-07-29 13:30 | 128 | 128
2018-07-29 14:00 | 138 | 138
2018-07-29 14:30 | 146 | 145
2018-07-29 15:00 | 157 | 156
2018-07-29 15:30 | 170 | 170
2018-07-29 16:00 | 186 | 185
2018-07-29 16:30 | 200 | 199
2018-07-29 17:00 | 215 | 214
2018-07-29 17:30 | 230 | 228
2018-07-29 18:00 | 244 | 242
2018-07-29 18:30 | 247 | 245
2018-07-29 19:00 | 244 | 243
2018-07-29 19:30 | 237 | 236
2018-07-29 20:00 | 234 | 233
2018-07-29 20:30 | 233 | 232
2018-07-29 21:00 | 222 | 221
2018-07-29 21:30 | 213 | 213
2018-07-29 22:00 | 206 | 206
2018-07-29 22:30 | 202 | 202
2018-07-29 23:00 | 200 | 200
2018-07-29 23:30 | 189 | 189
2018-07-30 | 176 | 176
2018-07-30 00:30 | 161 | 161
2018-07-30 01:00 | 152 | 152
2018-07-30 01:30 | 145 | 145
2018-07-30 02:00 | 140 | 139
2018-07-30 02:30 | 138 | 138
2018-07-30 03:00 | 138 | 138
2018-07-30 03:30 | 139 | 139
2018-07-30 04:00 | 140 | 140
2018-07-30 04:30 | 145 | 145
2018-07-30 05:00 | 154 | 154
2018-07-30 05:30 | 171 | 169
2018-07-30 06:00 | 188 | 186
2018-07-30 06:30 | 210 | 208
2018-07-30 07:00 | 232 | 230
2018-07-30 07:30 | 247 | 247
2018-07-30 08:00 | 240 | 240
2018-07-30 08:30 | 229 | 229
2018-07-30 09:00 | 215 | 215
2018-07-30 09:30 | 203 | 202
2018-07-30 10:00 | 192 | 192
2018-07-30 10:30 | 184 | 183
2018-07-30 11:00 | 177 | 176
2018-07-30 11:30 | 171 | 169
2018-07-30 12:00 | 169 | 168
2018-07-30 12:30 | 169 | 168
2018-07-30 13:00 | 166 | 166
2018-07-30 13:30 | 170 | 170
2018-07-30 14:00 | 176 | 176
2018-07-30 14:30 | 182 | 182
2018-07-30 15:00 | 191 | 191
2018-07-30 15:30 | 202 | 202
2018-07-30 16:00 | 218 | 218
2018-07-30 16:30 | 231 | 231
2018-07-30 17:00 | 247 | 247
2018-07-30 17:30 | 262 | 261
2018-07-30 18:00 | 277 | 276
2018-07-30 18:30 | 279 | 277
2018-07-30 19:00 | 279 | 278
2018-07-30 19:30 | 273 | 272
2018-07-30 20:00 | 269 | 269
2018-07-30 20:30 | 268 | 268
2018-07-30 21:00 | 257 | 257
2018-07-30 21:30 | 246 | 244
2018-07-30 22:00 | 238 | 235
2018-07-30 22:30 | 229 | 227
2018-07-30 23:00 | 224 | 222
2018-07-30 23:30 | 211 | 210
2018-07-31 | 193 | 192
2018-07-31 00:30 | 177 | 177
2018-07-31 01:00 | 168 | 167
2018-07-31 01:30 | 162 | 161
2018-07-31 02:00 | 157 | 157
2018-07-31 02:30 | 154 | 153
2018-07-31 03:00 | 153 | 152
2018-07-31 03:30 | 155 | 154
2018-07-31 04:00 | 155 | 154
2018-07-31 04:30 | 161 | 160
2018-07-31 05:00 | 172 | 170
2018-07-31 05:30 | 192 | 190
2018-07-31 06:00 | 215 | 213
2018-07-31 06:30 | 245 | 245
2018-07-31 07:00 | 274 | 274
2018-07-31 07:30 | 287 | 286
2018-07-31 08:00 | 276 | 275
2018-07-31 08:30 | 254 | 254
2018-07-31 09:00 | 231 | 231
2018-07-31 09:30 | 213 | 213
2018-07-31 10:00 | 198 | 198
2018-07-31 10:30 | 186 | 186
2018-07-31 11:00 | 177 | 177
2018-07-31 11:30 | 170 | 170
2018-07-31 12:00 | 165 | 165
2018-07-31 12:30 | 162 | 162
2018-07-31 13:00 | 164 | 164
2018-07-31 13:30 | 166 | 166
2018-07-31 14:00 | 172 | 172
2018-07-31 14:30 | 182 | 182
2018-07-31 15:00 | 192 | 192
2018-07-31 15:30 | 202 | 202
2018-07-31 16:00 | 217 | 217
2018-07-31 16:30 | 232 | 232
2018-07-31 17:00 | 249 | 249
2018-07-31 17:30 | 264 | 264
2018-07-31 18:00 | 281 | 281
2018-07-31 18:30 | 288 | 287
2018-07-31 19:00 | 290 | 290
2018-07-31 19:30 | 288 | 287
2018-07-31 20:00 | 287 | 287
2018-07-31 20:30 | 287 | 286
2018-07-31 21:00 | 277 | 276
2018-07-31 21:30 | 263 | 263
2018-07-31 22:00 | 253 | 253
2018-07-31 22:30 | 244 | 242
2018-07-31 23:00 | 236 | 234
2018-07-31 23:30 | 221 | 220
2018-08-01 | 205 | 204
2018-08-01 00:30 | 188 | 188
2018-08-01 01:00 | 178 | 178
2018-08-01 01:30 | 169 | 169
2018-08-01 02:00 | 163 | 163
2018-08-01 02:30 | 161 | 161
2018-08-01 03:00 | 159 | 159
2018-08-01 03:30 | 160 | 160
2018-08-01 04:00 | 161 | 161
2018-08-01 04:30 | 168 | 168
2018-08-01 05:00 | 179 | 179
2018-08-01 05:30 | 201 | 200
2018-08-01 06:00 | 222 | 221
2018-08-01 06:30 | 256 | 256
2018-08-01 07:00 | 287 | 286
2018-08-01 07:30 | 301 | 300
2018-08-01 08:00 | 289 | 289
2018-08-01 08:30 | 264 | 264
2018-08-01 09:00 | 241 | 240
2018-08-01 09:30 | 224 | 223
2018-08-01 10:00 | 207 | 207
2018-08-01 10:30 | 191 | 191
2018-08-01 11:00 | 181 | 180
2018-08-01 11:30 | 173 | 172
2018-08-01 12:00 | 169 | 169
2018-08-01 12:30 | 168 | 167
2018-08-01 13:00 | 168 | 167
2018-08-01 13:30 | 171 | 170
2018-08-01 14:00 | 177 | 176
2018-08-01 14:30 | 185 | 185
2018-08-01 15:00 | 193 | 192
2018-08-01 15:30 | 200 | 199
2018-08-01 16:00 | 213 | 212
2018-08-01 16:30 | 228 | 228
2018-08-01 17:00 | 244 | 244
2018-08-01 17:30 | 260 | 260
2018-08-01 18:00 | 282 | 282
2018-08-01 18:30 | 290 | 290
2018-08-01 19:00 | 293 | 293
2018-08-01 19:30 | 291 | 291
2018-08-01 20:00 | 290 | 289
2018-08-01 20:30 | 291 | 291
2018-08-01 21:00 | 280 | 280
2018-08-01 21:30 | 267 | 267
2018-08-01 22:00 | 255 | 254
2018-08-01 22:30 | 246 | 245
2018-08-01 23:00 | 239 | 239
2018-08-01 23:30 | 221 | 221
2018-08-02 | 205 | 205
2018-08-02 00:30 | 189 | 189
2018-08-02 01:00 | 179 | 178
2018-08-02 01:30 | 171 | 171
2018-08-02 02:00 | 165 | 165
2018-08-02 02:30 | 163 | 163
2018-08-02 03:00 | 161 | 161
2018-08-02 03:30 | 162 | 162
2018-08-02 04:00 | 163 | 163
2018-08-02 04:30 | 170 | 169
2018-08-02 05:00 | 180 | 180
2018-08-02 05:30 | 200 | 200
2018-08-02 06:00 | 223 | 222
2018-08-02 06:30 | 256 | 255
2018-08-02 07:00 | 283 | 282
2018-08-02 07:30 | 296 | 295
2018-08-02 08:00 | 285 | 285
2018-08-02 08:30 | 263 | 263
2018-08-02 09:00 | 239 | 239
2018-08-02 09:30 | 220 | 220
2018-08-02 10:00 | 203 | 203
2018-08-02 10:30 | 189 | 188
2018-08-02 11:00 | 181 | 181
2018-08-02 11:30 | 175 | 175
2018-08-02 12:00 | 172 | 171
2018-08-02 12:30 | 174 | 173
2018-08-02 13:00 | 175 | 174
2018-08-02 13:30 | 177 | 176
2018-08-02 14:00 | 180 | 179
2018-08-02 14:30 | 185 | 184
2018-08-02 15:00 | 192 | 191
2018-08-02 15:30 | 202 | 202
2018-08-02 16:00 | 216 | 216
2018-08-02 16:30 | 231 | 230
2018-08-02 17:00 | 248 | 248
2018-08-02 17:30 | 263 | 263
2018-08-02 18:00 | 282 | 282
2018-08-02 18:30 | 288 | 288
2018-08-02 19:00 | 291 | 291
2018-08-02 19:30 | 288 | 288
2018-08-02 20:00 | 286 | 286
2018-08-02 20:30 | 286 | 286
2018-08-02 21:00 | 276 | 276
2018-08-02 21:30 | 262 | 262
2018-08-02 22:00 | 250 | 250
2018-08-02 22:30 | 241 | 240
2018-08-02 23:00 | 234 | 234
2018-08-02 23:30 | 219 | 219
2018-08-03 | 201 | 201
2018-08-03 00:30 | 185 | 185
2018-08-03 01:00 | 173 | 173
2018-08-03 01:30 | 166 | 166
2018-08-03 02:00 | 161 | 161
2018-08-03 02:30 | 157 | 157
2018-08-03 03:00 | 155 | 155
2018-08-03 03:30 | 155 | 155
2018-08-03 04:00 | 157 | 157
2018-08-03 04:30 | 163 | 163
2018-08-03 05:00 | 173 | 173
2018-08-03 05:30 | 190 | 189
2018-08-03 06:00 | 209 | 208
2018-08-03 06:30 | 238 | 237
2018-08-03 07:00 | 264 | 264
2018-08-03 07:30 | 273 | 273
2018-08-03 08:00 | 268 | 267
2018-08-03 08:30 | 248 | 248
2018-08-03 09:00 | 226 | 226
2018-08-03 09:30 | 209 | 209
2018-08-03 10:00 | 196 | 196
2018-08-03 10:30 | 186 | 185
2018-08-03 11:00 | 179 | 177
2018-08-03 11:30 | 178 | 176
2018-08-03 12:00 | 178 | 176
2018-08-03 12:30 | 174 | 172
2018-08-03 13:00 | 179 | 177
2018-08-03 13:30 | 178 | 177
2018-08-03 14:00 | 180 | 179
2018-08-03 14:30 | 183 | 181
2018-08-03 15:00 | 189 | 187
2018-08-03 15:30 | 196 | 195
2018-08-03 16:00 | 210 | 209
2018-08-03 16:30 | 224 | 223
2018-08-03 17:00 | 238 | 238
2018-08-03 17:30 | 249 | 247
2018-08-03 18:00 | 262 | 261
2018-08-03 18:30 | 264 | 264
2018-08-03 19:00 | 266 | 266
2018-08-03 19:30 | 261 | 261
2018-08-03 20:00 | 260 | 260
2018-08-03 20:30 | 259 | 259
2018-08-03 21:00 | 249 | 248
2018-08-03 21:30 | 240 | 239
2018-08-03 22:00 | 232 | 231
2018-08-03 22:30 | 228 | 228
2018-08-03 23:00 | 223 | 222
2018-08-03 23:30 | 210 | 210
2018-08-04 | 194 | 194
2018-08-04 00:30 | 178 | 178
2018-08-04 01:00 | 168 | 168
2018-08-04 01:30 | 160 | 160
2018-08-04 02:00 | 155 | 155
2018-08-04 02:30 | 151 | 151
2018-08-04 03:00 | 148 | 148
2018-08-04 03:30 | 148 | 148
2018-08-04 04:00 | 147 | 147
2018-08-04 04:30 | 145 | 145
2018-08-04 05:00 | 149 | 149
2018-08-04 05:30 | 155 | 155
2018-08-04 06:00 | 162 | 162
2018-08-04 06:30 | 173 | 173
2018-08-04 07:00 | 183 | 182
2018-08-04 07:30 | 192 | 191
2018-08-04 08:00 | 193 | 193
2018-08-04 08:30 | 190 | 189
2018-08-04 09:00 | 182 | 181
2018-08-04 09:30 | 172 | 171
2018-08-04 10:00 | 163 | 162
2018-08-04 10:30 | 153 | 153
2018-08-04 11:00 | 145 | 145
2018-08-04 11:30 | 139 | 138
2018-08-04 12:00 | 134 | 134
2018-08-04 12:30 | 129 | 129
2018-08-04 13:00 | 128 | 127
2018-08-04 13:30 | 134 | 134
2018-08-04 14:00 | 138 | 138
2018-08-04 14:30 | 145 | 144
2018-08-04 15:00 | 152 | 152
2018-08-04 15:30 | 164 | 164
2018-08-04 16:00 | 177 | 176
2018-08-04 16:30 | 190 | 189
2018-08-04 17:00 | 205 | 205
2018-08-04 17:30 | 215 | 215
2018-08-04 18:00 | 227 | 227
2018-08-04 18:30 | 232 | 232
2018-08-04 19:00 | 233 | 233
2018-08-04 19:30 | 228 | 228
2018-08-04 20:00 | 228 | 228
2018-08-04 20:30 | 227 | 227
2018-08-04 21:00 | 219 | 217
2018-08-04 21:30 | 212 | 210
2018-08-04 22:00 | 207 | 206
2018-08-04 22:30 | 206 | 205
2018-08-04 23:00 | 205 | 205
2018-08-04 23:30 | 196 | 195
2018-08-05 | 183 | 182
2018-08-05 00:30 | 168 | 168
2018-08-05 01:00 | 160 | 160
2018-08-05 01:30 | 152 | 152
2018-08-05 02:00 | 147 | 147
2018-08-05 02:30 | 144 | 143
2018-08-05 03:00 | 140 | 140
2018-08-05 03:30 | 137 | 136
2018-08-05 04:00 | 136 | 135
2018-08-05 04:30 | 136 | 135
2018-08-05 05:00 | 138 | 138
2018-08-05 05:30 | 145 | 145
2018-08-05 06:00 | 149 | 148
2018-08-05 06:30 | 160 | 159
2018-08-05 07:00 | 165 | 164
2018-08-05 07:30 | 174 | 173
2018-08-05 08:00 | 176 | 174
2018-08-05 08:30 | 174 | 173
2018-08-05 09:00 | 169 | 167
2018-08-05 09:30 | 161 | 159
2018-08-05 10:00 | 150 | 148
2018-08-05 10:30 | 142 | 141
2018-08-05 11:00 | 130 | 129
2018-08-05 11:30 | 125 | 123
2018-08-05 12:00 | 124 | 122
2018-08-05 12:30 | 122 | 121
2018-08-05 13:00 | 122 | 120
2018-08-05 13:30 | 127 | 125
2018-08-05 14:00 | 131 | 130
2018-08-05 14:30 | 139 | 138
2018-08-05 15:00 | 147 | 145
2018-08-05 15:30 | 157 | 155
2018-08-05 16:00 | 172 | 171
2018-08-05 16:30 | 188 | 187
2018-08-05 17:00 | 206 | 205
2018-08-05 17:30 | 221 | 219
2018-08-05 18:00 | 235 | 234
2018-08-05 18:30 | 242 | 242
2018-08-05 19:00 | 242 | 242
2018-08-05 19:30 | 234 | 234
2018-08-05 20:00 | 233 | 233
2018-08-05 20:30 | 232 | 232
2018-08-05 21:00 | 221 | 219
2018-08-05 21:30 | 212 | 210
2018-08-05 22:00 | 205 | 203
2018-08-05 22:30 | 199 | 199
2018-08-05 23:00 | 200 | 199
2018-08-05 23:30 | 195 | 195
2018-08-06 | 181 | 181
2018-08-06 00:30 | 168 | 168
2018-08-06 01:00 | 159 | 159
2018-08-06 01:30 | 153 | 153
2018-08-06 02:00 | 148 | 148
2018-08-06 02:30 | 145 | 145
2018-08-06 03:00 | 144 | 144
2018-08-06 03:30 | 145 | 145
2018-08-06 04:00 | 145 | 145
2018-08-06 04:30 | 149 | 149
2018-08-06 05:00 | 160 | 160
2018-08-06 05:30 | 177 | 176
2018-08-06 06:00 | 195 | 194
2018-08-06 06:30 | 221 | 221
2018-08-06 07:00 | 242 | 241
2018-08-06 07:30 | 256 | 256
2018-08-06 08:00 | 250 | 250
2018-08-06 08:30 | 235 | 234
2018-08-06 09:00 | 219 | 218
2018-08-06 09:30 | 208 | 208
2018-08-06 10:00 | 199 | 199
2018-08-06 10:30 | 190 | 190
2018-08-06 11:00 | 182 | 182
2018-08-06 11:30 | 177 | 177
2018-08-06 12:00 | 176 | 176
2018-08-06 12:30 | 178 | 178
2018-08-06 13:00 | 181 | 180
2018-08-06 13:30 | 185 | 185
2018-08-06 14:00 | 192 | 191
2018-08-06 14:30 | 201 | 200
2018-08-06 15:00 | 209 | 209
2018-08-06 15:30 | 223 | 223
2018-08-06 16:00 | 242 | 242
2018-08-06 16:30 | 251 | 251
2018-08-06 17:00 | 265 | 265
2018-08-06 17:30 | 278 | 278
2018-08-06 18:00 | 287 | 287
2018-08-06 18:30 | 282 | 282
2018-08-06 19:00 | 281 | 280
2018-08-06 19:30 | 271 | 271
2018-08-06 20:00 | 269 | 269
2018-08-06 20:30 | 266 | 266
2018-08-06 21:00 | 252 | 251
2018-08-06 21:30 | 239 | 238
2018-08-06 22:00 | 228 | 227
2018-08-06 22:30 | 222 | 222
2018-08-06 23:00 | 217 | 217
2018-08-06 23:30 | 205 | 205
2018-08-07 | 189 | 189
2018-08-07 00:30 | 173 | 173
2018-08-07 01:00 | 164 | 164
2018-08-07 01:30 | 156 | 156
2018-08-07 02:00 | 149 | 149
2018-08-07 02:30 | 147 | 147
2018-08-07 03:00 | 142 | 142
2018-08-07 03:30 | 142 | 142
2018-08-07 04:00 | 143 | 143
2018-08-07 04:30 | 147 | 147
2018-08-07 05:00 | 157 | 157
2018-08-07 05:30 | 173 | 173
2018-08-07 06:00 | 189 | 187
2018-08-07 06:30 | 213 | 213
2018-08-07 07:00 | 233 | 233
2018-08-07 07:30 | 245 | 245
2018-08-07 08:00 | 246 | 246
2018-08-07 08:30 | 235 | 235
2018-08-07 09:00 | 218 | 217
2018-08-07 09:30 | 209 | 208
2018-08-07 10:00 | 196 | 196
2018-08-07 10:30 | 176 | 176
2018-08-07 11:00 | 174 | 174
2018-08-07 11:30 | 171 | 171
2018-08-07 12:00 | 170 | 168
2018-08-07 12:30 | 172 | 170
2018-08-07 13:00 | 189 | 187
2018-08-07 13:30 | 193 | 191
2018-08-07 14:00 | 192 | 190
2018-08-07 14:30 | 195 | 193
2018-08-07 15:00 | 193 | 191
2018-08-07 15:30 | 206 | 204
2018-08-07 16:00 | 216 | 215
2018-08-07 16:30 | 224 | 223
2018-08-07 17:00 | 241 | 239
2018-08-07 17:30 | 259 | 257
2018-08-07 18:00 | 278 | 277
2018-08-07 18:30 | 283 | 283
2018-08-07 19:00 | 285 | 285
2018-08-07 19:30 | 281 | 281
2018-08-07 20:00 | 279 | 278
2018-08-07 20:30 | 279 | 279
2018-08-07 21:00 | 270 | 270
2018-08-07 21:30 | 256 | 256
2018-08-07 22:00 | 246 | 246
2018-08-07 22:30 | 237 | 237
2018-08-07 23:00 | 230 | 230
2018-08-07 23:30 | 215 | 215
2018-08-08 | 198 | 197
2018-08-08 00:30 | 182 | 182
2018-08-08 01:00 | 172 | 172
2018-08-08 01:30 | 166 | 166
2018-08-08 02:00 | 160 | 160
2018-08-08 02:30 | 158 | 158
2018-08-08 03:00 | 155 | 155
2018-08-08 03:30 | 157 | 157
2018-08-08 04:00 | 159 | 159
2018-08-08 04:30 | 164 | 164
2018-08-08 05:00 | 174 | 173
2018-08-08 05:30 | 196 | 194
2018-08-08 06:00 | 218 | 216
2018-08-08 06:30 | 249 | 248
2018-08-08 07:00 | 276 | 276
2018-08-08 07:30 | 287 | 286
2018-08-08 08:00 | 274 | 274
2018-08-08 08:30 | 250 | 250
2018-08-08 09:00 | 226 | 226
2018-08-08 09:30 | 209 | 208
2018-08-08 10:00 | 193 | 193
2018-08-08 10:30 | 181 | 180
2018-08-08 11:00 | 172 | 170
2018-08-08 11:30 | 165 | 163
2018-08-08 12:00 | 161 | 159
2018-08-08 12:30 | 160 | 158
2018-08-08 13:00 | 162 | 160
2018-08-08 13:30 | 165 | 162
2018-08-08 14:00 | 169 | 167
2018-08-08 14:30 | 175 | 174
2018-08-08 15:00 | 182 | 181
2018-08-08 15:30 | 193 | 192
2018-08-08 16:00 | 209 | 208
2018-08-08 16:30 | 225 | 225
2018-08-08 17:00 | 244 | 244
2018-08-08 17:30 | 261 | 261
2018-08-08 18:00 | 280 | 280
2018-08-08 18:30 | 288 | 288
2018-08-08 19:00 | 292 | 292
2018-08-08 19:30 | 289 | 289
2018-08-08 20:00 | 290 | 288
2018-08-08 20:30 | 292 | 291
2018-08-08 21:00 | 281 | 278
2018-08-08 21:30 | 268 | 265
2018-08-08 22:00 | 256 | 254
2018-08-08 22:30 | 246 | 244
2018-08-08 23:00 | 240 | 238
2018-08-08 23:30 | 224 | 223
2018-08-09 | 207 | 206
2018-08-09 00:30 | 189 | 189
2018-08-09 01:00 | 178 | 178
2018-08-09 01:30 | 169 | 169
2018-08-09 02:00 | 163 | 163
2018-08-09 02:30 | 160 | 160
2018-08-09 03:00 | 157 | 156
2018-08-09 03:30 | 161 | 160
2018-08-09 04:00 | 163 | 163
2018-08-09 04:30 | 170 | 170
2018-08-09 05:00 | 183 | 182
2018-08-09 05:30 | 203 | 201
2018-08-09 06:00 | 228 | 224
2018-08-09 06:30 | 259 | 259
2018-08-09 07:00 | 288 | 287
2018-08-09 07:30 | 301 | 301
2018-08-09 08:00 | 288 | 288
2018-08-09 08:30 | 264 | 264
2018-08-09 09:00 | 238 | 238
2018-08-09 09:30 | 218 | 218
2018-08-09 10:00 | 202 | 202
2018-08-09 10:30 | 190 | 190
2018-08-09 11:00 | 179 | 179
2018-08-09 11:30 | 169 | 169
2018-08-09 12:00 | 164 | 164
2018-08-09 12:30 | 164 | 164
2018-08-09 13:00 | 163 | 162
2018-08-09 13:30 | 171 | 170
2018-08-09 14:00 | 172 | 171
2018-08-09 14:30 | 181 | 181
2018-08-09 15:00 | 189 | 189
2018-08-09 15:30 | 199 | 199
2018-08-09 16:00 | 215 | 215
2018-08-09 16:30 | 230 | 229
2018-08-09 17:00 | 245 | 245
2018-08-09 17:30 | 260 | 260
2018-08-09 18:00 | 280 | 280
2018-08-09 18:30 | 288 | 287
2018-08-09 19:00 | 291 | 291
2018-08-09 19:30 | 288 | 288
2018-08-09 20:00 | 289 | 288
2018-08-09 20:30 | 289 | 289
2018-08-09 21:00 | 278 | 278
2018-08-09 21:30 | 265 | 265
2018-08-09 22:00 | 252 | 252
2018-08-09 22:30 | 245 | 244
2018-08-09 23:00 | 238 | 238
2018-08-09 23:30 | 223 | 223
2018-08-10 | 205 | 204
2018-08-10 00:30 | 188 | 187
2018-08-10 01:00 | 177 | 176
2018-08-10 01:30 | 169 | 168
2018-08-10 02:00 | 163 | 163
2018-08-10 02:30 | 160 | 160
2018-08-10 03:00 | 158 | 158
2018-08-10 03:30 | 159 | 159
2018-08-10 04:00 | 161 | 160
2018-08-10 04:30 | 168 | 168
2018-08-10 05:00 | 179 | 178
2018-08-10 05:30 | 197 | 196
2018-08-10 06:00 | 216 | 216
2018-08-10 06:30 | 247 | 246
2018-08-10 07:00 | 272 | 271
2018-08-10 07:30 | 284 | 281
2018-08-10 08:00 | 273 | 271
2018-08-10 08:30 | 250 | 249
2018-08-10 09:00 | 226 | 226
2018-08-10 09:30 | 207 | 207
2018-08-10 10:00 | 194 | 193
2018-08-10 10:30 | 184 | 184
2018-08-10 11:00 | 176 | 175
2018-08-10 11:30 | 173 | 173
2018-08-10 12:00 | 171 | 171
2018-08-10 12:30 | 165 | 165
2018-08-10 13:00 | 165 | 165
2018-08-10 13:30 | 165 | 165
2018-08-10 14:00 | 166 | 166
2018-08-10 14:30 | 172 | 172
2018-08-10 15:00 | 176 | 176
2018-08-10 15:30 | 187 | 187
2018-08-10 16:00 | 204 | 203
2018-08-10 16:30 | 220 | 218
2018-08-10 17:00 | 235 | 234
2018-08-10 17:30 | 247 | 247
2018-08-10 18:00 | 260 | 260
2018-08-10 18:30 | 266 | 266
2018-08-10 19:00 | 268 | 268
2018-08-10 19:30 | 265 | 265
2018-08-10 20:00 | 264 | 264
2018-08-10 20:30 | 265 | 264
2018-08-10 21:00 | 256 | 256
2018-08-10 21:30 | 246 | 246
2018-08-10 22:00 | 237 | 237
2018-08-10 22:30 | 231 | 230
2018-08-10 23:00 | 225 | 224
2018-08-10 23:30 | 212 | 211
2018-08-11 | 194 | 194
2018-08-11 00:30 | 178 | 178
2018-08-11 01:00 | 167 | 167
2018-08-11 01:30 | 159 | 159
2018-08-11 02:00 | 152 | 152
2018-08-11 02:30 | 149 | 149
2018-08-11 03:00 | 146 | 146
2018-08-11 03:30 | 145 | 145
2018-08-11 04:00 | 146 | 145
2018-08-11 04:30 | 147 | 147
2018-08-11 05:00 | 150 | 150
2018-08-11 05:30 | 157 | 157
2018-08-11 06:00 | 164 | 164
2018-08-11 06:30 | 174 | 174
2018-08-11 07:00 | 185 | 185
2018-08-11 07:30 | 195 | 195
2018-08-11 08:00 | 200 | 200
2018-08-11 08:30 | 203 | 203
2018-08-11 09:00 | 198 | 198
2018-08-11 09:30 | 190 | 190
2018-08-11 10:00 | 171 | 171
2018-08-11 10:30 | 154 | 154
2018-08-11 11:00 | 144 | 144
2018-08-11 11:30 | 138 | 138
2018-08-11 12:00 | 131 | 131
2018-08-11 12:30 | 129 | 129
2018-08-11 13:00 | 129 | 129
2018-08-11 13:30 | 129 | 129
2018-08-11 14:00 | 135 | 135
2018-08-11 14:30 | 138 | 138
2018-08-11 15:00 | 147 | 147
2018-08-11 15:30 | 156 | 156
2018-08-11 16:00 | 170 | 170
2018-08-11 16:30 | 183 | 183
2018-08-11 17:00 | 201 | 201
2018-08-11 17:30 | 210 | 210
2018-08-11 18:00 | 223 | 223
2018-08-11 18:30 | 229 | 229
2018-08-11 19:00 | 230 | 230
2018-08-11 19:30 | 226 | 226
2018-08-11 20:00 | 225 | 225
2018-08-11 20:30 | 224 | 224
2018-08-11 21:00 | 218 | 217
2018-08-11 21:30 | 211 | 211
2018-08-11 22:00 | 204 | 204
2018-08-11 22:30 | 204 | 204
2018-08-11 23:00 | 204 | 204
2018-08-11 23:30 | 195 | 194
2018-08-12 | 180 | 180
2018-08-12 00:30 | 168 | 167
2018-08-12 01:00 | 158 | 157
2018-08-12 01:30 | 151 | 150
2018-08-12 02:00 | 145 | 144
2018-08-12 02:30 | 141 | 140
2018-08-12 03:00 | 138 | 137
2018-08-12 03:30 | 137 | 136
2018-08-12 04:00 | 137 | 136
2018-08-12 04:30 | 136 | 136
2018-08-12 05:00 | 138 | 137
2018-08-12 05:30 | 142 | 141
2018-08-12 06:00 | 147 | 146
2018-08-12 06:30 | 153 | 153
2018-08-12 07:00 | 159 | 158
2018-08-12 07:30 | 164 | 163
2018-08-12 08:00 | 164 | 164
2018-08-12 08:30 | 163 | 163
2018-08-12 09:00 | 159 | 159
2018-08-12 09:30 | 152 | 152
2018-08-12 10:00 | 144 | 144
2018-08-12 10:30 | 136 | 136
2018-08-12 11:00 | 129 | 129
2018-08-12 11:30 | 122 | 122
2018-08-12 12:00 | 120 | 120
2018-08-12 12:30 | 118 | 118
2018-08-12 13:00 | 117 | 117
2018-08-12 13:30 | 119 | 119
2018-08-12 14:00 | 123 | 122
2018-08-12 14:30 | 130 | 130
2018-08-12 15:00 | 139 | 139
2018-08-12 15:30 | 151 | 151
2018-08-12 16:00 | 165 | 165
2018-08-12 16:30 | 182 | 182
2018-08-12 17:00 | 202 | 201
2018-08-12 17:30 | 217 | 217
2018-08-12 18:00 | 233 | 233
2018-08-12 18:30 | 242 | 242
2018-08-12 19:00 | 244 | 244
2018-08-12 19:30 | 240 | 240
2018-08-12 20:00 | 240 | 240
2018-08-12 20:30 | 242 | 241
2018-08-12 21:00 | 235 | 234
2018-08-12 21:30 | 227 | 226
2018-08-12 22:00 | 220 | 219
2018-08-12 22:30 | 215 | 214
2018-08-12 23:00 | 213 | 213
2018-08-12 23:30 | 202 | 202
2018-08-13 | 186 | 186
2018-08-13 00:30 | 172 | 172
2018-08-13 01:00 | 159 | 159
2018-08-13 01:30 | 154 | 154
2018-08-13 02:00 | 150 | 150
2018-08-13 02:30 | 150 | 150
2018-08-13 03:00 | 148 | 148
2018-08-13 03:30 | 148 | 148
2018-08-13 04:00 | 150 | 150
2018-08-13 04:30 | 156 | 156
2018-08-13 05:00 | 164 | 164
2018-08-13 05:30 | 179 | 178
2018-08-13 06:00 | 199 | 197
2018-08-13 06:30 | 225 | 224
2018-08-13 07:00 | 246 | 244
2018-08-13 07:30 | 257 | 256
2018-08-13 08:00 | 251 | 251
2018-08-13 08:30 | 235 | 235
2018-08-13 09:00 | 217 | 217
2018-08-13 09:30 | 199 | 199
2018-08-13 10:00 | 184 | 184
2018-08-13 10:30 | 172 | 171
2018-08-13 11:00 | 161 | 160
2018-08-13 11:30 | 156 | 155
2018-08-13 12:00 | 154 | 153
2018-08-13 12:30 | 152 | 151
2018-08-13 13:00 | 149 | 149
2018-08-13 13:30 | 150 | 149
2018-08-13 14:00 | 157 | 156
2018-08-13 14:30 | 162 | 161
2018-08-13 15:00 | 172 | 171
2018-08-13 15:30 | 182 | 182
2018-08-13 16:00 | 197 | 196
2018-08-13 16:30 | 213 | 213
2018-08-13 17:00 | 235 | 235
2018-08-13 17:30 | 256 | 255
2018-08-13 18:00 | 278 | 277
2018-08-13 18:30 | 287 | 287
2018-08-13 19:00 | 290 | 290
2018-08-13 19:30 | 287 | 286
2018-08-13 20:00 | 287 | 286
2018-08-13 20:30 | 287 | 287
2018-08-13 21:00 | 276 | 273
2018-08-13 21:30 | 265 | 262
2018-08-13 22:00 | 251 | 250
2018-08-13 22:30 | 242 | 241
2018-08-13 23:00 | 236 | 235
2018-08-13 23:30 | 222 | 221
2018-08-14 | 206 | 206
2018-08-14 00:30 | 187 | 187
2018-08-14 01:00 | 177 | 176
2018-08-14 01:30 | 169 | 169
2018-08-14 02:00 | 164 | 164
2018-08-14 02:30 | 158 | 158
2018-08-14 03:00 | 157 | 157
2018-08-14 03:30 | 160 | 160
2018-08-14 04:00 | 163 | 163
2018-08-14 04:30 | 170 | 169
2018-08-14 05:00 | 181 | 180
2018-08-14 05:30 | 203 | 202
2018-08-14 06:00 | 226 | 223
2018-08-14 06:30 | 259 | 259
2018-08-14 07:00 | 289 | 289
2018-08-14 07:30 | 301 | 301
2018-08-14 08:00 | 290 | 290
2018-08-14 08:30 | 266 | 266
2018-08-14 09:00 | 240 | 239
2018-08-14 09:30 | 215 | 215
2018-08-14 10:00 | 199 | 199
2018-08-14 10:30 | 186 | 186
2018-08-14 11:00 | 172 | 172
2018-08-14 11:30 | 171 | 169
2018-08-14 12:00 | 166 | 165
2018-08-14 12:30 | 163 | 162
2018-08-14 13:00 | 164 | 162
2018-08-14 13:30 | 166 | 165
2018-08-14 14:00 | 170 | 169
2018-08-14 14:30 | 178 | 177
2018-08-14 15:00 | 185 | 184
2018-08-14 15:30 | 196 | 195
2018-08-14 16:00 | 209 | 208
2018-08-14 16:30 | 223 | 222
2018-08-14 17:00 | 239 | 238
2018-08-14 17:30 | 253 | 253
2018-08-14 18:00 | 271 | 271
2018-08-14 18:30 | 280 | 279
2018-08-14 19:00 | 281 | 281
2018-08-14 19:30 | 279 | 278
2018-08-14 20:00 | 278 | 277
2018-08-14 20:30 | 279 | 278
2018-08-14 21:00 | 268 | 267
2018-08-14 21:30 | 255 | 254
2018-08-14 22:00 | 245 | 244
2018-08-14 22:30 | 238 | 238
2018-08-14 23:00 | 233 | 232
2018-08-14 23:30 | 217 | 217
2018-08-15 | 200 | 200
2018-08-15 00:30 | 185 | 185
2018-08-15 01:00 | 174 | 174
2018-08-15 01:30 | 164 | 164
2018-08-15 02:00 | 159 | 159
2018-08-15 02:30 | 158 | 158
2018-08-15 03:00 | 157 | 157
2018-08-15 03:30 | 158 | 158
2018-08-15 04:00 | 159 | 159
2018-08-15 04:30 | 163 | 163
2018-08-15 05:00 | 170 | 170
2018-08-15 05:30 | 183 | 183
2018-08-15 06:00 | 198 | 197
2018-08-15 06:30 | 222 | 222
2018-08-15 07:00 | 244 | 244
2018-08-15 07:30 | 255 | 255
2018-08-15 08:00 | 250 | 250
2018-08-15 08:30 | 234 | 234
2018-08-15 09:00 | 215 | 214
2018-08-15 09:30 | 198 | 197
2018-08-15 10:00 | 185 | 183
2018-08-15 10:30 | 174 | 172
2018-08-15 11:00 | 160 | 160
2018-08-15 11:30 | 153 | 153
2018-08-15 12:00 | 150 | 150
2018-08-15 12:30 | 147 | 147
2018-08-15 13:00 | 148 | 148
2018-08-15 13:30 | 152 | 151
2018-08-15 14:00 | 155 | 155
2018-08-15 14:30 | 161 | 161
2018-08-15 15:00 | 170 | 170
2018-08-15 15:30 | 183 | 183
2018-08-15 16:00 | 197 | 197
2018-08-15 16:30 | 213 | 213
2018-08-15 17:00 | 229 | 228
2018-08-15 17:30 | 240 | 240
2018-08-15 18:00 | 254 | 254
2018-08-15 18:30 | 260 | 260
2018-08-15 19:00 | 262 | 261
2018-08-15 19:30 | 258 | 258
2018-08-15 20:00 | 257 | 257
2018-08-15 20:30 | 256 | 255
2018-08-15 21:00 | 246 | 245
2018-08-15 21:30 | 235 | 235
2018-08-15 22:00 | 226 | 226
2018-08-15 22:30 | 220 | 220
2018-08-15 23:00 | 218 | 217
2018-08-15 23:30 | 206 | 206
2018-08-16 | 190 | 190
2018-08-16 00:30 | 175 | 175
2018-08-16 01:00 | 167 | 167
2018-08-16 01:30 | 160 | 159
2018-08-16 02:00 | 154 | 154
2018-08-16 02:30 | 151 | 151
2018-08-16 03:00 | 146 | 146
2018-08-16 03:30 | 148 | 148
2018-08-16 04:00 | 151 | 151
2018-08-16 04:30 | 159 | 159
2018-08-16 05:00 | 169 | 169
2018-08-16 05:30 | 187 | 186
2018-08-16 06:00 | 205 | 204
2018-08-16 06:30 | 231 | 231
2018-08-16 07:00 | 260 | 260
2018-08-16 07:30 | 266 | 266
2018-08-16 08:00 | 255 | 255
2018-08-16 08:30 | 235 | 234
2018-08-16 09:00 | 213 | 213
2018-08-16 09:30 | 196 | 195
2018-08-16 10:00 | 182 | 182
2018-08-16 10:30 | 171 | 171
2018-08-16 11:00 | 165 | 165
2018-08-16 11:30 | 161 | 161
2018-08-16 12:00 | 160 | 159
2018-08-16 12:30 | 161 | 160
2018-08-16 13:00 | 164 | 164
2018-08-16 13:30 | 167 | 167
2018-08-16 14:00 | 174 | 174
2018-08-16 14:30 | 187 | 187
2018-08-16 15:00 | 196 | 196
2018-08-16 15:30 | 205 | 205
2018-08-16 16:00 | 219 | 219
2018-08-16 16:30 | 232 | 232
2018-08-16 17:00 | 247 | 247
2018-08-16 17:30 | 257 | 257
2018-08-16 18:00 | 270 | 270
2018-08-16 18:30 | 278 | 278
2018-08-16 19:00 | 278 | 278
2018-08-16 19:30 | 273 | 273
2018-08-16 20:00 | 270 | 270
2018-08-16 20:30 | 266 | 266
2018-08-16 21:00 | 255 | 255
2018-08-16 21:30 | 243 | 243
2018-08-16 22:00 | 233 | 233
2018-08-16 22:30 | 228 | 227
2018-08-16 23:00 | 221 | 220
2018-08-16 23:30 | 208 | 207
2018-08-17 | 190 | 190
2018-08-17 00:30 | 174 | 174
2018-08-17 01:00 | 164 | 164
2018-08-17 01:30 | 158 | 158
2018-08-17 02:00 | 154 | 154
2018-08-17 02:30 | 151 | 151
2018-08-17 03:00 | 149 | 149
2018-08-17 03:30 | 150 | 149
2018-08-17 04:00 | 150 | 150
2018-08-17 04:30 | 156 | 156
2018-08-17 05:00 | 166 | 165
2018-08-17 05:30 | 184 | 183
2018-08-17 06:00 | 204 | 202
2018-08-17 06:30 | 233 | 232
2018-08-17 07:00 | 255 | 254
2018-08-17 07:30 | 264 | 264
2018-08-17 08:00 | 253 | 252
2018-08-17 08:30 | 234 | 234
2018-08-17 09:00 | 218 | 215
2018-08-17 09:30 | 202 | 199
2018-08-17 10:00 | 188 | 185
2018-08-17 10:30 | 180 | 178
2018-08-17 11:00 | 176 | 173
2018-08-17 11:30 | 173 | 169
2018-08-17 12:00 | 172 | 168
2018-08-17 12:30 | 170 | 167
2018-08-17 13:00 | 166 | 162
2018-08-17 13:30 | 168 | 165
2018-08-17 14:00 | 174 | 170
2018-08-17 14:30 | 181 | 177
2018-08-17 15:00 | 187 | 184
2018-08-17 15:30 | 197 | 194
2018-08-17 16:00 | 212 | 211
2018-08-17 16:30 | 226 | 226
2018-08-17 17:00 | 237 | 237
2018-08-17 17:30 | 244 | 244
2018-08-17 18:00 | 252 | 252
2018-08-17 18:30 | 255 | 255
2018-08-17 19:00 | 256 | 256
2018-08-17 19:30 | 251 | 251
2018-08-17 20:00 | 248 | 248
2018-08-17 20:30 | 249 | 249
2018-08-17 21:00 | 241 | 241
2018-08-17 21:30 | 232 | 232
2018-08-17 22:00 | 225 | 225
2018-08-17 22:30 | 220 | 220
2018-08-17 23:00 | 218 | 217
2018-08-17 23:30 | 207 | 206
2018-08-18 | 191 | 191
2018-08-18 00:30 | 176 | 176
2018-08-18 01:00 | 165 | 165
2018-08-18 01:30 | 158 | 158
2018-08-18 02:00 | 152 | 152
2018-08-18 02:30 | 146 | 146
2018-08-18 03:00 | 144 | 144
2018-08-18 03:30 | 144 | 144
2018-08-18 04:00 | 147 | 147
2018-08-18 04:30 | 147 | 146
2018-08-18 05:00 | 149 | 149
2018-08-18 05:30 | 157 | 157
2018-08-18 06:00 | 167 | 167
2018-08-18 06:30 | 175 | 174
2018-08-18 07:00 | 184 | 183
2018-08-18 07:30 | 189 | 188
2018-08-18 08:00 | 187 | 186
2018-08-18 08:30 | 182 | 180
2018-08-18 09:00 | 174 | 172
2018-08-18 09:30 | 163 | 162
2018-08-18 10:00 | 149 | 148
2018-08-18 10:30 | 141 | 140
2018-08-18 11:00 | 137 | 136
2018-08-18 11:30 | 130 | 129
2018-08-18 12:00 | 124 | 123
2018-08-18 12:30 | 122 | 121
2018-08-18 13:00 | 122 | 121
2018-08-18 13:30 | 125 | 124
2018-08-18 14:00 | 131 | 129
2018-08-18 14:30 | 138 | 136
2018-08-18 15:00 | 146 | 145
2018-08-18 15:30 | 158 | 157
2018-08-18 16:00 | 172 | 170
2018-08-18 16:30 | 186 | 184
2018-08-18 17:00 | 199 | 197
2018-08-18 17:30 | 207 | 205
2018-08-18 18:00 | 218 | 215
2018-08-18 18:30 | 224 | 223
2018-08-18 19:00 | 225 | 224
2018-08-18 19:30 | 220 | 219
2018-08-18 20:00 | 219 | 219
2018-08-18 20:30 | 218 | 218
2018-08-18 21:00 | 212 | 211
2018-08-18 21:30 | 205 | 204
2018-08-18 22:00 | 201 | 201
2018-08-18 22:30 | 200 | 200
2018-08-18 23:00 | 200 | 200
2018-08-18 23:30 | 190 | 190
2018-08-19 | 179 | 179
2018-08-19 00:30 | 165 | 165
2018-08-19 01:00 | 156 | 156
2018-08-19 01:30 | 148 | 148
2018-08-19 02:00 | 140 | 140
2018-08-19 02:30 | 136 | 136
2018-08-19 03:00 | 136 | 136
2018-08-19 03:30 | 134 | 134
2018-08-19 04:00 | 133 | 133
2018-08-19 04:30 | 135 | 134
2018-08-19 05:00 | 136 | 135
2018-08-19 05:30 | 142 | 141
2018-08-19 06:00 | 149 | 148
2018-08-19 06:30 | 156 | 155
2018-08-19 07:00 | 161 | 160
2018-08-19 07:30 | 164 | 163
2018-08-19 08:00 | 163 | 161
2018-08-19 08:30 | 159 | 157
2018-08-19 09:00 | 152 | 150
2018-08-19 09:30 | 144 | 143
2018-08-19 10:00 | 137 | 135
2018-08-19 10:30 | 129 | 127
2018-08-19 11:00 | 121 | 120
2018-08-19 11:30 | 115 | 113
2018-08-19 12:00 | 111 | 109
2018-08-19 12:30 | 109 | 107
2018-08-19 13:00 | 110 | 108
2018-08-19 13:30 | 112 | 111
2018-08-19 14:00 | 118 | 116
2018-08-19 14:30 | 122 | 120
2018-08-19 15:00 | 134 | 132
2018-08-19 15:30 | 147 | 146
2018-08-19 16:00 | 163 | 161
2018-08-19 16:30 | 181 | 179
2018-08-19 17:00 | 200 | 199
2018-08-19 17:30 | 216 | 215
2018-08-19 18:00 | 237 | 236
2018-08-19 18:30 | 251 | 248
2018-08-19 19:00 | 252 | 249
2018-08-19 19:30 | 247 | 245
2018-08-19 20:00 | 246 | 244
2018-08-19 20:30 | 247 | 245
2018-08-19 21:00 | 238 | 236
2018-08-19 21:30 | 227 | 226
2018-08-19 22:00 | 218 | 217
2018-08-19 22:30 | 212 | 211
2018-08-19 23:00 | 207 | 207
2018-08-19 23:30 | 196 | 196
2018-08-20 | 180 | 180
2018-08-20 00:30 | 166 | 166
2018-08-20 01:00 | 158 | 158
2018-08-20 01:30 | 151 | 151
2018-08-20 02:00 | 145 | 145
2018-08-20 02:30 | 143 | 143
2018-08-20 03:00 | 141 | 141
2018-08-20 03:30 | 142 | 142
2018-08-20 04:00 | 144 | 144
2018-08-20 04:30 | 151 | 151
2018-08-20 05:00 | 162 | 161
2018-08-20 05:30 | 182 | 181
2018-08-20 06:00 | 202 | 200
2018-08-20 06:30 | 232 | 229
2018-08-20 07:00 | 255 | 255
2018-08-20 07:30 | 264 | 264
2018-08-20 08:00 | 251 | 251
2018-08-20 08:30 | 233 | 233
2018-08-20 09:00 | 212 | 212
2018-08-20 09:30 | 195 | 195
2018-08-20 10:00 | 186 | 186
2018-08-20 10:30 | 179 | 179
2018-08-20 11:00 | 171 | 171
2018-08-20 11:30 | 164 | 164
2018-08-20 12:00 | 157 | 157
2018-08-20 12:30 | 155 | 155
2018-08-20 13:00 | 155 | 154
2018-08-20 13:30 | 159 | 157
2018-08-20 14:00 | 165 | 163
2018-08-20 14:30 | 173 | 170
2018-08-20 15:00 | 181 | 178
2018-08-20 15:30 | 192 | 190
2018-08-20 16:00 | 209 | 208
2018-08-20 16:30 | 226 | 226
2018-08-20 17:00 | 246 | 246
2018-08-20 17:30 | 266 | 265
2018-08-20 18:00 | 287 | 286
2018-08-20 18:30 | 297 | 296
2018-08-20 19:00 | 300 | 299
2018-08-20 19:30 | 296 | 295
2018-08-20 20:00 | 296 | 295
2018-08-20 20:30 | 295 | 295
2018-08-20 21:00 | 285 | 285
2018-08-20 21:30 | 272 | 272
2018-08-20 22:00 | 257 | 257
2018-08-20 22:30 | 249 | 249
2018-08-20 23:00 | 242 | 242
2018-08-20 23:30 | 227 | 227
2018-08-21 | 210 | 210
2018-08-21 00:30 | 192 | 191
2018-08-21 01:00 | 179 | 179
2018-08-21 01:30 | 173 | 172
2018-08-21 02:00 | 168 | 167
2018-08-21 02:30 | 165 | 165
2018-08-21 03:00 | 162 | 162
2018-08-21 03:30 | 162 | 162
2018-08-21 04:00 | 165 | 165
2018-08-21 04:30 | 173 | 173
2018-08-21 05:00 | 186 | 185
2018-08-21 05:30 | 209 | 208
2018-08-21 06:00 | 235 | 235
2018-08-21 06:30 | 271 | 270
2018-08-21 07:00 | 298 | 298
2018-08-21 07:30 | 306 | 306
2018-08-21 08:00 | 290 | 289
2018-08-21 08:30 | 261 | 261
2018-08-21 09:00 | 234 | 234
2018-08-21 09:30 | 214 | 213
2018-08-21 10:00 | 196 | 196
2018-08-21 10:30 | 182 | 182
2018-08-21 11:00 | 172 | 172
2018-08-21 11:30 | 165 | 164
2018-08-21 12:00 | 162 | 160
2018-08-21 12:30 | 161 | 158
2018-08-21 13:00 | 161 | 159
2018-08-21 13:30 | 163 | 161
2018-08-21 14:00 | 168 | 166
2018-08-21 14:30 | 174 | 173
2018-08-21 15:00 | 183 | 182
2018-08-21 15:30 | 194 | 193
2018-08-21 16:00 | 210 | 208
2018-08-21 16:30 | 226 | 225
2018-08-21 17:00 | 243 | 242
2018-08-21 17:30 | 261 | 260
2018-08-21 18:00 | 280 | 280
2018-08-21 18:30 | 290 | 290
2018-08-21 19:00 | 295 | 295
2018-08-21 19:30 | 293 | 293
2018-08-21 20:00 | 293 | 292
2018-08-21 20:30 | 293 | 293
2018-08-21 21:00 | 283 | 282
2018-08-21 21:30 | 270 | 270
2018-08-21 22:00 | 258 | 258
2018-08-21 22:30 | 248 | 248
2018-08-21 23:00 | 241 | 241
2018-08-21 23:30 | 223 | 223
2018-08-22 | 206 | 206
2018-08-22 00:30 | 190 | 190
2018-08-22 01:00 | 178 | 178
2018-08-22 01:30 | 171 | 171
2018-08-22 02:00 | 164 | 164
2018-08-22 02:30 | 162 | 162
2018-08-22 03:00 | 160 | 160
2018-08-22 03:30 | 161 | 161
2018-08-22 04:00 | 162 | 162
2018-08-22 04:30 | 171 | 170
2018-08-22 05:00 | 184 | 183
2018-08-22 05:30 | 204 | 203
2018-08-22 06:00 | 229 | 229
2018-08-22 06:30 | 261 | 259
2018-08-22 07:00 | 286 | 286
2018-08-22 07:30 | 292 | 292
2018-08-22 08:00 | 275 | 275
2018-08-22 08:30 | 248 | 248
2018-08-22 09:00 | 223 | 222
2018-08-22 09:30 | 203 | 203
2018-08-22 10:00 | 185 | 185
2018-08-22 10:30 | 175 | 174
2018-08-22 11:00 | 167 | 166
2018-08-22 11:30 | 162 | 161
2018-08-22 12:00 | 158 | 157
2018-08-22 12:30 | 157 | 156
2018-08-22 13:00 | 158 | 157
2018-08-22 13:30 | 162 | 161
2018-08-22 14:00 | 167 | 166
2018-08-22 14:30 | 174 | 173
2018-08-22 15:00 | 181 | 180
2018-08-22 15:30 | 191 | 191
2018-08-22 16:00 | 207 | 206
2018-08-22 16:30 | 222 | 222
2018-08-22 17:00 | 240 | 239
2018-08-22 17:30 | 254 | 253
2018-08-22 18:00 | 270 | 269
2018-08-22 18:30 | 278 | 277
2018-08-22 19:00 | 283 | 283
2018-08-22 19:30 | 278 | 278
2018-08-22 20:00 | 278 | 277
2018-08-22 20:30 | 278 | 278
2018-08-22 21:00 | 269 | 269
2018-08-22 21:30 | 256 | 256
2018-08-22 22:00 | 248 | 247
2018-08-22 22:30 | 239 | 239
2018-08-22 23:00 | 233 | 233
2018-08-22 23:30 | 219 | 219
2018-08-23 | 203 | 202
2018-08-23 00:30 | 185 | 185
2018-08-23 01:00 | 174 | 174
2018-08-23 01:30 | 167 | 167
2018-08-23 02:00 | 161 | 161
2018-08-23 02:30 | 157 | 157
2018-08-23 03:00 | 156 | 156
2018-08-23 03:30 | 156 | 156
2018-08-23 04:00 | 157 | 157
2018-08-23 04:30 | 166 | 166
2018-08-23 05:00 | 177 | 176
2018-08-23 05:30 | 197 | 195
2018-08-23 06:00 | 220 | 219
2018-08-23 06:30 | 251 | 251
2018-08-23 07:00 | 275 | 275
2018-08-23 07:30 | 279 | 278
2018-08-23 08:00 | 265 | 265
2018-08-23 08:30 | 241 | 241
2018-08-23 09:00 | 218 | 218
2018-08-23 09:30 | 200 | 200
2018-08-23 10:00 | 186 | 186
2018-08-23 10:30 | 178 | 178
2018-08-23 11:00 | 177 | 177
2018-08-23 11:30 | 174 | 173
2018-08-23 12:00 | 176 | 174
2018-08-23 12:30 | 174 | 172
2018-08-23 13:00 | 172 | 170
2018-08-23 13:30 | 173 | 171
2018-08-23 14:00 | 177 | 175
2018-08-23 14:30 | 183 | 181
2018-08-23 15:00 | 189 | 187
2018-08-23 15:30 | 196 | 194
2018-08-23 16:00 | 208 | 206
2018-08-23 16:30 | 221 | 219
2018-08-23 17:00 | 239 | 239
2018-08-23 17:30 | 252 | 252
2018-08-23 18:00 | 270 | 270
2018-08-23 18:30 | 280 | 279
2018-08-23 19:00 | 285 | 285
2018-08-23 19:30 | 280 | 279
2018-08-23 20:00 | 280 | 279
2018-08-23 20:30 | 280 | 279
2018-08-23 21:00 | 269 | 269
2018-08-23 21:30 | 256 | 256
2018-08-23 22:00 | 243 | 243
2018-08-23 22:30 | 235 | 234
2018-08-23 23:00 | 228 | 227
2018-08-23 23:30 | 214 | 213
2018-08-24 | 197 | 197
2018-08-24 00:30 | 183 | 183
2018-08-24 01:00 | 173 | 173
2018-08-24 01:30 | 165 | 165
2018-08-24 02:00 | 159 | 159
2018-08-24 02:30 | 156 | 156
2018-08-24 03:00 | 153 | 153
2018-08-24 03:30 | 153 | 153
2018-08-24 04:00 | 156 | 156
2018-08-24 04:30 | 161 | 161
2018-08-24 05:00 | 173 | 172
2018-08-24 05:30 | 190 | 189
2018-08-24 06:00 | 211 | 209
2018-08-24 06:30 | 237 | 237
2018-08-24 07:00 | 257 | 257
2018-08-24 07:30 | 262 | 262
2018-08-24 08:00 | 250 | 250
2018-08-24 08:30 | 230 | 230
2018-08-24 09:00 | 210 | 209
2018-08-24 09:30 | 195 | 194
2018-08-24 10:00 | 189 | 188
2018-08-24 10:30 | 190 | 189
2018-08-24 11:00 | 191 | 190
2018-08-24 11:30 | 194 | 194
2018-08-24 12:00 | 195 | 195
2018-08-24 12:30 | 194 | 194
2018-08-24 13:00 | 196 | 195
2018-08-24 13:30 | 190 | 189
2018-08-24 14:00 | 191 | 191
2018-08-24 14:30 | 192 | 191
2018-08-24 15:00 | 201 | 200
2018-08-24 15:30 | 206 | 205
2018-08-24 16:00 | 218 | 218
2018-08-24 16:30 | 232 | 231
2018-08-24 17:00 | 245 | 244
2018-08-24 17:30 | 255 | 254
2018-08-24 18:00 | 265 | 264
2018-08-24 18:30 | 268 | 266
2018-08-24 19:00 | 269 | 268
2018-08-24 19:30 | 264 | 263
2018-08-24 20:00 | 262 | 262
2018-08-24 20:30 | 261 | 260
2018-08-24 21:00 | 250 | 250
2018-08-24 21:30 | 240 | 240
2018-08-24 22:00 | 229 | 229
2018-08-24 22:30 | 226 | 225
2018-08-24 23:00 | 223 | 223
2018-08-24 23:30 | 209 | 209
2018-08-25 | 193 | 193
2018-08-25 00:30 | 177 | 177
2018-08-25 01:00 | 167 | 167
2018-08-25 01:30 | 160 | 160
2018-08-25 02:00 | 154 | 154
2018-08-25 02:30 | 149 | 149
2018-08-25 03:00 | 147 | 146
2018-08-25 03:30 | 146 | 146
2018-08-25 04:00 | 145 | 145
2018-08-25 04:30 | 146 | 146
2018-08-25 05:00 | 149 | 149
2018-08-25 05:30 | 154 | 154
2018-08-25 06:00 | 161 | 161
2018-08-25 06:30 | 170 | 170
2018-08-25 07:00 | 179 | 179
2018-08-25 07:30 | 187 | 187
2018-08-25 08:00 | 186 | 186
2018-08-25 08:30 | 183 | 183
2018-08-25 09:00 | 175 | 175
2018-08-25 09:30 | 167 | 167
2018-08-25 10:00 | 158 | 158
2018-08-25 10:30 | 151 | 151
2018-08-25 11:00 | 149 | 149
2018-08-25 11:30 | 150 | 150
2018-08-25 12:00 | 149 | 149
2018-08-25 12:30 | 149 | 149
2018-08-25 13:00 | 152 | 152
2018-08-25 13:30 | 159 | 159
2018-08-25 14:00 | 158 | 157
2018-08-25 14:30 | 160 | 159
2018-08-25 15:00 | 159 | 158
2018-08-25 15:30 | 164 | 163
2018-08-25 16:00 | 176 | 176
2018-08-25 16:30 | 194 | 193
2018-08-25 17:00 | 209 | 208
2018-08-25 17:30 | 218 | 217
2018-08-25 18:00 | 232 | 230
2018-08-25 18:30 | 238 | 238
2018-08-25 19:00 | 242 | 241
2018-08-25 19:30 | 237 | 236
2018-08-25 20:00 | 236 | 235
2018-08-25 20:30 | 236 | 235
2018-08-25 21:00 | 228 | 227
2018-08-25 21:30 | 221 | 221
2018-08-25 22:00 | 217 | 217
2018-08-25 22:30 | 216 | 215
2018-08-25 23:00 | 215 | 214
2018-08-25 23:30 | 206 | 205
2018-08-26 | 191 | 191
2018-08-26 00:30 | 176 | 176
2018-08-26 01:00 | 166 | 166
2018-08-26 01:30 | 157 | 157
2018-08-26 02:00 | 151 | 151
2018-08-26 02:30 | 147 | 146
2018-08-26 03:00 | 144 | 143
2018-08-26 03:30 | 143 | 142
2018-08-26 04:00 | 142 | 142
2018-08-26 04:30 | 142 | 142
2018-08-26 05:00 | 141 | 141
2018-08-26 05:30 | 145 | 145
2018-08-26 06:00 | 151 | 151
2018-08-26 06:30 | 155 | 155
2018-08-26 07:00 | 161 | 161
2018-08-26 07:30 | 170 | 170
2018-08-26 08:00 | 180 | 180
2018-08-26 08:30 | 193 | 192
2018-08-26 09:00 | 198 | 197
2018-08-26 09:30 | 206 | 205
2018-08-26 10:00 | 210 | 209
2018-08-26 10:30 | 213 | 212
2018-08-26 11:00 | 223 | 222
2018-08-26 11:30 | 212 | 212
2018-08-26 12:00 | 198 | 198
2018-08-26 12:30 | 196 | 196
2018-08-26 13:00 | 199 | 199
2018-08-26 13:30 | 192 | 192
2018-08-26 14:00 | 176 | 176
2018-08-26 14:30 | 181 | 181
2018-08-26 15:00 | 176 | 176
2018-08-26 15:30 | 191 | 191
2018-08-26 16:00 | 198 | 198
2018-08-26 16:30 | 200 | 200
2018-08-26 17:00 | 219 | 219
2018-08-26 17:30 | 234 | 234
2018-08-26 18:00 | 250 | 249
2018-08-26 18:30 | 263 | 263
2018-08-26 19:00 | 263 | 263
2018-08-26 19:30 | 259 | 258
2018-08-26 20:00 | 255 | 255
2018-08-26 20:30 | 254 | 254
2018-08-26 21:00 | 245 | 245
2018-08-26 21:30 | 235 | 235
2018-08-26 22:00 | 222 | 222
2018-08-26 22:30 | 214 | 214
2018-08-26 23:00 | 210 | 210
2018-08-26 23:30 | 197 | 197
2018-08-27 | 182 | 182
2018-08-27 00:30 | 168 | 168
2018-08-27 01:00 | 158 | 158
2018-08-27 01:30 | 149 | 149
2018-08-27 02:00 | 146 | 146
2018-08-27 02:30 | 143 | 143
2018-08-27 03:00 | 140 | 140
2018-08-27 03:30 | 141 | 141
2018-08-27 04:00 | 142 | 142
2018-08-27 04:30 | 149 | 149
2018-08-27 05:00 | 160 | 159
2018-08-27 05:30 | 177 | 177
2018-08-27 06:00 | 197 | 196
2018-08-27 06:30 | 223 | 223
2018-08-27 07:00 | 244 | 244
2018-08-27 07:30 | 251 | 251
2018-08-27 08:00 | 242 | 242
2018-08-27 08:30 | 224 | 224
2018-08-27 09:00 | 205 | 204
2018-08-27 09:30 | 191 | 190
2018-08-27 10:00 | 178 | 178
2018-08-27 10:30 | 170 | 169
2018-08-27 11:00 | 163 | 163
2018-08-27 11:30 | 160 | 160
2018-08-27 12:00 | 159 | 159
2018-08-27 12:30 | 159 | 159
2018-08-27 13:00 | 164 | 164
2018-08-27 13:30 | 170 | 170
2018-08-27 14:00 | 173 | 173
2018-08-27 14:30 | 179 | 179
2018-08-27 15:00 | 185 | 185
2018-08-27 15:30 | 195 | 195
2018-08-27 16:00 | 208 | 208
2018-08-27 16:30 | 223 | 223
2018-08-27 17:00 | 240 | 240
2018-08-27 17:30 | 257 | 257
2018-08-27 18:00 | 274 | 274
2018-08-27 18:30 | 284 | 283
2018-08-27 19:00 | 285 | 285
2018-08-27 19:30 | 279 | 279
2018-08-27 20:00 | 276 | 276
2018-08-27 20:30 | 276 | 275
2018-08-27 21:00 | 264 | 262
2018-08-27 21:30 | 250 | 249
2018-08-27 22:00 | 239 | 237
2018-08-27 22:30 | 231 | 230
2018-08-27 23:00 | 226 | 225
2018-08-27 23:30 | 211 | 211
2018-08-28 | 195 | 195
2018-08-28 00:30 | 179 | 179
2018-08-28 01:00 | 168 | 168
2018-08-28 01:30 | 161 | 161
2018-08-28 02:00 | 156 | 156
2018-08-28 02:30 | 154 | 153
2018-08-28 03:00 | 152 | 152
2018-08-28 03:30 | 153 | 153
2018-08-28 04:00 | 154 | 154
2018-08-28 04:30 | 159 | 159
2018-08-28 05:00 | 168 | 168
2018-08-28 05:30 | 185 | 184
2018-08-28 06:00 | 204 | 202
2018-08-28 06:30 | 230 | 228
2018-08-28 07:00 | 250 | 250
2018-08-28 07:30 | 257 | 257
2018-08-28 08:00 | 245 | 245
2018-08-28 08:30 | 226 | 226
2018-08-28 09:00 | 204 | 204
2018-08-28 09:30 | 188 | 188
2018-08-28 10:00 | 176 | 175
2018-08-28 10:30 | 172 | 171
2018-08-28 11:00 | 175 | 174
2018-08-28 11:30 | 173 | 171
2018-08-28 12:00 | 173 | 172
2018-08-28 12:30 | 172 | 171
2018-08-28 13:00 | 175 | 173
2018-08-28 13:30 | 176 | 175
2018-08-28 14:00 | 177 | 177
2018-08-28 14:30 | 181 | 181
2018-08-28 15:00 | 188 | 187
2018-08-28 15:30 | 198 | 198
2018-08-28 16:00 | 213 | 212
2018-08-28 16:30 | 228 | 227
2018-08-28 17:00 | 244 | 244
2018-08-28 17:30 | 256 | 256
2018-08-28 18:00 | 272 | 271
2018-08-28 18:30 | 282 | 282
2018-08-28 19:00 | 285 | 284
2018-08-28 19:30 | 280 | 280
2018-08-28 20:00 | 277 | 277
2018-08-28 20:30 | 278 | 277
2018-08-28 21:00 | 267 | 266
2018-08-28 21:30 | 255 | 254
2018-08-28 22:00 | 244 | 244
2018-08-28 22:30 | 236 | 236
2018-08-28 23:00 | 231 | 231
2018-08-28 23:30 | 217 | 217
2018-08-29 | 199 | 199
2018-08-29 00:30 | 182 | 181
2018-08-29 01:00 | 172 | 171
2018-08-29 01:30 | 164 | 162
2018-08-29 02:00 | 156 | 155
2018-08-29 02:30 | 153 | 152
2018-08-29 03:00 | 152 | 151
2018-08-29 03:30 | 151 | 151
2018-08-29 04:00 | 153 | 153
2018-08-29 04:30 | 156 | 156
2018-08-29 05:00 | 167 | 167
2018-08-29 05:30 | 184 | 184
2018-08-29 06:00 | 207 | 206
2018-08-29 06:30 | 234 | 233
2018-08-29 07:00 | 253 | 252
2018-08-29 07:30 | 261 | 260
2018-08-29 08:00 | 247 | 247
2018-08-29 08:30 | 228 | 228
2018-08-29 09:00 | 206 | 205
2018-08-29 09:30 | 186 | 186
2018-08-29 10:00 | 172 | 172
2018-08-29 10:30 | 164 | 164
2018-08-29 11:00 | 156 | 156
2018-08-29 11:30 | 151 | 150
2018-08-29 12:00 | 151 | 150
2018-08-29 12:30 | 148 | 147
2018-08-29 13:00 | 147 | 146
2018-08-29 13:30 | 152 | 151
2018-08-29 14:00 | 159 | 158
2018-08-29 14:30 | 166 | 166
2018-08-29 15:00 | 174 | 174
2018-08-29 15:30 | 184 | 183
2018-08-29 16:00 | 200 | 200
2018-08-29 16:30 | 216 | 216
2018-08-29 17:00 | 235 | 234
2018-08-29 17:30 | 248 | 247
2018-08-29 18:00 | 263 | 262
2018-08-29 18:30 | 277 | 277
2018-08-29 19:00 | 280 | 280
2018-08-29 19:30 | 275 | 275
2018-08-29 20:00 | 272 | 272
2018-08-29 20:30 | 274 | 274
2018-08-29 21:00 | 265 | 264
2018-08-29 21:30 | 253 | 251
2018-08-29 22:00 | 241 | 240
2018-08-29 22:30 | 232 | 232
2018-08-29 23:00 | 228 | 228
2018-08-29 23:30 | 213 | 213
2018-08-30 | 197 | 197
2018-08-30 00:30 | 183 | 183
2018-08-30 01:00 | 173 | 172
2018-08-30 01:30 | 166 | 165
2018-08-30 02:00 | 160 | 159
2018-08-30 02:30 | 155 | 155
2018-08-30 03:00 | 152 | 152
2018-08-30 03:30 | 152 | 151
2018-08-30 04:00 | 152 | 151
2018-08-30 04:30 | 157 | 157
2018-08-30 05:00 | 168 | 168
2018-08-30 05:30 | 189 | 189
2018-08-30 06:00 | 211 | 210
2018-08-30 06:30 | 240 | 240
2018-08-30 07:00 | 262 | 261
2018-08-30 07:30 | 266 | 266
2018-08-30 08:00 | 251 | 251
2018-08-30 08:30 | 228 | 228
2018-08-30 09:00 | 212 | 212
2018-08-30 09:30 | 195 | 195
2018-08-30 10:00 | 180 | 180
2018-08-30 10:30 | 170 | 169
2018-08-30 11:00 | 165 | 164
2018-08-30 11:30 | 162 | 160
2018-08-30 12:00 | 162 | 160
2018-08-30 12:30 | 163 | 162
2018-08-30 13:00 | 165 | 164
2018-08-30 13:30 | 171 | 169
2018-08-30 14:00 | 176 | 175
2018-08-30 14:30 | 183 | 182
2018-08-30 15:00 | 187 | 187
2018-08-30 15:30 | 195 | 195
2018-08-30 16:00 | 210 | 210
2018-08-30 16:30 | 223 | 223
2018-08-30 17:00 | 238 | 237
2018-08-30 17:30 | 254 | 254
2018-08-30 18:00 | 270 | 270
2018-08-30 18:30 | 282 | 281
2018-08-30 19:00 | 285 | 285
2018-08-30 19:30 | 281 | 281
2018-08-30 20:00 | 281 | 280
2018-08-30 20:30 | 280 | 280
2018-08-30 21:00 | 269 | 269
2018-08-30 21:30 | 253 | 251
2018-08-30 22:00 | 239 | 238
2018-08-30 22:30 | 232 | 231
2018-08-30 23:00 | 227 | 226
2018-08-30 23:30 | 213 | 213
2018-08-31 | 196 | 196
2018-08-31 00:30 | 180 | 180
2018-08-31 01:00 | 170 | 170
2018-08-31 01:30 | 162 | 162
2018-08-31 02:00 | 156 | 156
2018-08-31 02:30 | 153 | 153
2018-08-31 03:00 | 152 | 152
2018-08-31 03:30 | 152 | 152
2018-08-31 04:00 | 152 | 152
2018-08-31 04:30 | 157 | 156
2018-08-31 05:00 | 165 | 165
2018-08-31 05:30 | 179 | 179
2018-08-31 06:00 | 196 | 196
2018-08-31 06:30 | 221 | 220
2018-08-31 07:00 | 237 | 235
2018-08-31 07:30 | 242 | 241
2018-08-31 08:00 | 231 | 231
2018-08-31 08:30 | 213 | 212
2018-08-31 09:00 | 195 | 195
2018-08-31 09:30 | 182 | 182
2018-08-31 10:00 | 171 | 171
2018-08-31 10:30 | 164 | 164
2018-08-31 11:00 | 160 | 160
2018-08-31 11:30 | 158 | 157
2018-08-31 12:00 | 153 | 152
2018-08-31 12:30 | 150 | 150
2018-08-31 13:00 | 149 | 149
2018-08-31 13:30 | 151 | 150
2018-08-31 14:00 | 157 | 155
2018-08-31 14:30 | 164 | 163
2018-08-31 15:00 | 169 | 167
2018-08-31 15:30 | 179 | 178
2018-08-31 16:00 | 194 | 193
2018-08-31 16:30 | 210 | 209
2018-08-31 17:00 | 225 | 224
2018-08-31 17:30 | 234 | 233
2018-08-31 18:00 | 243 | 241
2018-08-31 18:30 | 249 | 248
2018-08-31 19:00 | 251 | 250
2018-08-31 19:30 | 246 | 245
2018-08-31 20:00 | 243 | 242
2018-08-31 20:30 | 241 | 240
2018-08-31 21:00 | 233 | 231
2018-08-31 21:30 | 223 | 221
2018-08-31 22:00 | 215 | 214
2018-08-31 22:30 | 213 | 211
2018-08-31 23:00 | 211 | 210
2018-08-31 23:30 | 200 | 199
2018-09-01 | 185 | 184
2018-09-01 00:30 | 169 | 168
2018-09-01 01:00 | 158 | 158
2018-09-01 01:30 | 151 | 151
2018-09-01 02:00 | 146 | 145
2018-09-01 02:30 | 143 | 142
2018-09-01 03:00 | 141 | 139
2018-09-01 03:30 | 141 | 140
2018-09-01 04:00 | 140 | 139
2018-09-01 04:30 | 141 | 140
2018-09-01 05:00 | 143 | 141
2018-09-01 05:30 | 148 | 147
2018-09-01 06:00 | 152 | 151
2018-09-01 06:30 | 159 | 158
2018-09-01 07:00 | 164 | 162
2018-09-01 07:30 | 168 | 166
2018-09-01 08:00 | 163 | 163
2018-09-01 08:30 | 173 | 172
2018-09-01 09:00 | 171 | 171
2018-09-01 09:30 | 158 | 158
2018-09-01 10:00 | 147 | 147
2018-09-01 10:30 | 149 | 148
2018-09-01 11:00 | 151 | 150
2018-09-01 11:30 | 133 | 132
2018-09-01 12:00 | 119 | 119
2018-09-01 12:30 | 117 | 116
2018-09-01 13:00 | 116 | 116
2018-09-01 13:30 | 116 | 115
2018-09-01 14:00 | 122 | 121
2018-09-01 14:30 | 130 | 129
2018-09-01 15:00 | 142 | 141
2018-09-01 15:30 | 153 | 152
2018-09-01 16:00 | 164 | 164
2018-09-01 16:30 | 179 | 178
2018-09-01 17:00 | 193 | 192
2018-09-01 17:30 | 200 | 200
2018-09-01 18:00 | 211 | 211
2018-09-01 18:30 | 224 | 223
2018-09-01 19:00 | 226 | 225
2018-09-01 19:30 | 220 | 220
2018-09-01 20:00 | 220 | 219
2018-09-01 20:30 | 220 | 220
2018-09-01 21:00 | 212 | 212
2018-09-01 21:30 | 204 | 204
2018-09-01 22:00 | 199 | 199
2018-09-01 22:30 | 199 | 199
2018-09-01 23:00 | 199 | 198
2018-09-01 23:30 | 189 | 189
2018-09-02 | 175 | 175
2018-09-02 00:30 | 161 | 161
2018-09-02 01:00 | 152 | 152
2018-09-02 01:30 | 145 | 145
2018-09-02 02:00 | 139 | 139
2018-09-02 02:30 | 136 | 136
2018-09-02 03:00 | 135 | 135
2018-09-02 03:30 | 133 | 133
2018-09-02 04:00 | 133 | 132
2018-09-02 04:30 | 133 | 133
2018-09-02 05:00 | 133 | 133
2018-09-02 05:30 | 138 | 138
2018-09-02 06:00 | 142 | 141
2018-09-02 06:30 | 146 | 146
2018-09-02 07:00 | 149 | 149
2018-09-02 07:30 | 151 | 150
2018-09-02 08:00 | 150 | 149
2018-09-02 08:30 | 147 | 146
2018-09-02 09:00 | 142 | 141
2018-09-02 09:30 | 135 | 134
2018-09-02 10:00 | 128 | 126
2018-09-02 10:30 | 122 | 120
2018-09-02 11:00 | 116 | 114
2018-09-02 11:30 | 111 | 110
2018-09-02 12:00 | 109 | 107
2018-09-02 12:30 | 106 | 105
2018-09-02 13:00 | 107 | 105
2018-09-02 13:30 | 109 | 108
2018-09-02 14:00 | 115 | 114
2018-09-02 14:30 | 124 | 122
2018-09-02 15:00 | 132 | 131
2018-09-02 15:30 | 143 | 143
2018-09-02 16:00 | 158 | 158
2018-09-02 16:30 | 173 | 173
2018-09-02 17:00 | 190 | 190
2018-09-02 17:30 | 204 | 204
2018-09-02 18:00 | 217 | 217
2018-09-02 18:30 | 231 | 230
2018-09-02 19:00 | 233 | 233
2018-09-02 19:30 | 228 | 228
2018-09-02 20:00 | 227 | 226
2018-09-02 20:30 | 227 | 226
2018-09-02 21:00 | 218 | 218
2018-09-02 21:30 | 209 | 209
2018-09-02 22:00 | 201 | 201
2018-09-02 22:30 | 197 | 197
2018-09-02 23:00 | 195 | 195
2018-09-02 23:30 | 185 | 185
2018-09-03 | 172 | 172
2018-09-03 00:30 | 160 | 159
2018-09-03 01:00 | 151 | 150
2018-09-03 01:30 | 144 | 143
2018-09-03 02:00 | 139 | 139
2018-09-03 02:30 | 136 | 136
2018-09-03 03:00 | 135 | 135
2018-09-03 03:30 | 134 | 134
2018-09-03 04:00 | 136 | 136
2018-09-03 04:30 | 141 | 141
2018-09-03 05:00 | 150 | 150
2018-09-03 05:30 | 166 | 166
2018-09-03 06:00 | 184 | 183
2018-09-03 06:30 | 206 | 206
2018-09-03 07:00 | 226 | 225
2018-09-03 07:30 | 238 | 237
2018-09-03 08:00 | 235 | 234
2018-09-03 08:30 | 227 | 226
2018-09-03 09:00 | 213 | 212
2018-09-03 09:30 | 203 | 202
2018-09-03 10:00 | 199 | 198
2018-09-03 10:30 | 198 | 197
2018-09-03 11:00 | 199 | 198
2018-09-03 11:30 | 204 | 203
2018-09-03 12:00 | 208 | 206
2018-09-03 12:30 | 214 | 213
2018-09-03 13:00 | 209 | 208
2018-09-03 13:30 | 200 | 199
2018-09-03 14:00 | 205 | 204
2018-09-03 14:30 | 213 | 212
2018-09-03 15:00 | 214 | 213
2018-09-03 15:30 | 218 | 217
2018-09-03 16:00 | 223 | 222
2018-09-03 16:30 | 232 | 231
2018-09-03 17:00 | 249 | 248
2018-09-03 17:30 | 263 | 261
2018-09-03 18:00 | 276 | 275
2018-09-03 18:30 | 286 | 286
2018-09-03 19:00 | 287 | 287
2018-09-03 19:30 | 280 | 279
2018-09-03 20:00 | 274 | 274
2018-09-03 20:30 | 272 | 272
2018-09-03 21:00 | 264 | 264
2018-09-03 21:30 | 248 | 248
2018-09-03 22:00 | 234 | 234
2018-09-03 22:30 | 227 | 226
2018-09-03 23:00 | 221 | 221
2018-09-03 23:30 | 207 | 207
2018-09-04 | 191 | 191
2018-09-04 00:30 | 175 | 175
2018-09-04 01:00 | 164 | 164
2018-09-04 01:30 | 158 | 158
2018-09-04 02:00 | 151 | 151
2018-09-04 02:30 | 148 | 148
2018-09-04 03:00 | 146 | 146
2018-09-04 03:30 | 147 | 147
2018-09-04 04:00 | 147 | 147
2018-09-04 04:30 | 152 | 152
2018-09-04 05:00 | 162 | 161
2018-09-04 05:30 | 178 | 178
2018-09-04 06:00 | 194 | 193
2018-09-04 06:30 | 220 | 219
2018-09-04 07:00 | 243 | 243
2018-09-04 07:30 | 255 | 255
2018-09-04 08:00 | 250 | 250
2018-09-04 08:30 | 238 | 238
2018-09-04 09:00 | 225 | 225
2018-09-04 09:30 | 219 | 219
2018-09-04 10:00 | 205 | 205
2018-09-04 10:30 | 183 | 183
2018-09-04 11:00 | 175 | 175
2018-09-04 11:30 | 176 | 176
2018-09-04 12:00 | 177 | 177
2018-09-04 12:30 | 184 | 184
2018-09-04 13:00 | 185 | 185
2018-09-04 13:30 | 190 | 190
2018-09-04 14:00 | 200 | 200
2018-09-04 14:30 | 199 | 199
2018-09-04 15:00 | 201 | 201
2018-09-04 15:30 | 214 | 214
2018-09-04 16:00 | 224 | 224
2018-09-04 16:30 | 237 | 237
2018-09-04 17:00 | 252 | 252
2018-09-04 17:30 | 267 | 267
2018-09-04 18:00 | 284 | 284
2018-09-04 18:30 | 292 | 292
2018-09-04 19:00 | 292 | 292
2018-09-04 19:30 | 285 | 285
2018-09-04 20:00 | 280 | 280
2018-09-04 20:30 | 279 | 279
2018-09-04 21:00 | 264 | 264
2018-09-04 21:30 | 249 | 249
2018-09-04 22:00 | 237 | 237
2018-09-04 22:30 | 229 | 229
2018-09-04 23:00 | 222 | 222
2018-09-04 23:30 | 209 | 209
2018-09-05 | 192 | 192
2018-09-05 00:30 | 176 | 176
2018-09-05 01:00 | 166 | 166
2018-09-05 01:30 | 159 | 158
2018-09-05 02:00 | 153 | 153
2018-09-05 02:30 | 150 | 150
2018-09-05 03:00 | 147 | 147
2018-09-05 03:30 | 148 | 148
2018-09-05 04:00 | 148 | 148
2018-09-05 04:30 | 153 | 153
2018-09-05 05:00 | 162 | 162
2018-09-05 05:30 | 178 | 177
2018-09-05 06:00 | 197 | 196
2018-09-05 06:30 | 223 | 221
2018-09-05 07:00 | 242 | 241
2018-09-05 07:30 | 251 | 251
2018-09-05 08:00 | 247 | 247
2018-09-05 08:30 | 224 | 224
2018-09-05 09:00 | 202 | 202
2018-09-05 09:30 | 191 | 190
2018-09-05 10:00 | 191 | 191
2018-09-05 10:30 | 189 | 189
2018-09-05 11:00 | 184 | 184
2018-09-05 11:30 | 179 | 179
2018-09-05 12:00 | 175 | 175
2018-09-05 12:30 | 176 | 176
2018-09-05 13:00 | 179 | 179
2018-09-05 13:30 | 187 | 187
2018-09-05 14:00 | 201 | 201
2018-09-05 14:30 | 212 | 212
2018-09-05 15:00 | 205 | 205
2018-09-05 15:30 | 202 | 202
2018-09-05 16:00 | 215 | 215
2018-09-05 16:30 | 222 | 222
2018-09-05 17:00 | 238 | 238
2018-09-05 17:30 | 251 | 251
2018-09-05 18:00 | 265 | 265
2018-09-05 18:30 | 277 | 276
2018-09-05 19:00 | 279 | 278
2018-09-05 19:30 | 273 | 273
2018-09-05 20:00 | 273 | 272
2018-09-05 20:30 | 271 | 270
2018-09-05 21:00 | 258 | 258
2018-09-05 21:30 | 246 | 246
2018-09-05 22:00 | 236 | 236
2018-09-05 22:30 | 225 | 224
2018-09-05 23:00 | 216 | 215
2018-09-05 23:30 | 204 | 204
2018-09-06 | 188 | 188
2018-09-06 00:30 | 172 | 172
2018-09-06 01:00 | 161 | 161
2018-09-06 01:30 | 154 | 154
2018-09-06 02:00 | 148 | 148
2018-09-06 02:30 | 145 | 145
2018-09-06 03:00 | 143 | 143
2018-09-06 03:30 | 143 | 143
2018-09-06 04:00 | 144 | 144
2018-09-06 04:30 | 149 | 149
2018-09-06 05:00 | 158 | 158
2018-09-06 05:30 | 175 | 175
2018-09-06 06:00 | 190 | 190
2018-09-06 06:30 | 214 | 214
2018-09-06 07:00 | 232 | 232
2018-09-06 07:30 | 239 | 239
2018-09-06 08:00 | 231 | 231
2018-09-06 08:30 | 216 | 216
2018-09-06 09:00 | 198 | 198
2018-09-06 09:30 | 197 | 197
2018-09-06 10:00 | 201 | 201
2018-09-06 10:30 | 200 | 200
2018-09-06 11:00 | 202 | 201
2018-09-06 11:30 | 202 | 202
2018-09-06 12:00 | 204 | 204
2018-09-06 12:30 | 202 | 202
2018-09-06 13:00 | 198 | 198
2018-09-06 13:30 | 192 | 192
2018-09-06 14:00 | 190 | 190
2018-09-06 14:30 | 193 | 193
2018-09-06 15:00 | 196 | 196
2018-09-06 15:30 | 200 | 200
2018-09-06 16:00 | 208 | 208
2018-09-06 16:30 | 219 | 219
2018-09-06 17:00 | 234 | 234
2018-09-06 17:30 | 247 | 246
2018-09-06 18:00 | 261 | 260
2018-09-06 18:30 | 271 | 271
2018-09-06 19:00 | 277 | 277
2018-09-06 19:30 | 272 | 271
2018-09-06 20:00 | 270 | 269
2018-09-06 20:30 | 270 | 270
2018-09-06 21:00 | 259 | 258
2018-09-06 21:30 | 243 | 242
2018-09-06 22:00 | 232 | 231
2018-09-06 22:30 | 225 | 224
2018-09-06 23:00 | 221 | 220
2018-09-06 23:30 | 205 | 205
2018-09-07 | 188 | 187
2018-09-07 00:30 | 171 | 171
2018-09-07 01:00 | 161 | 161
2018-09-07 01:30 | 153 | 153
2018-09-07 02:00 | 147 | 147
2018-09-07 02:30 | 144 | 144
2018-09-07 03:00 | 141 | 141
2018-09-07 03:30 | 142 | 142
2018-09-07 04:00 | 143 | 143
2018-09-07 04:30 | 149 | 149
2018-09-07 05:00 | 158 | 158
2018-09-07 05:30 | 174 | 174
2018-09-07 06:00 | 189 | 189
2018-09-07 06:30 | 210 | 210
2018-09-07 07:00 | 225 | 225
2018-09-07 07:30 | 228 | 228
2018-09-07 08:00 | 229 | 229
2018-09-07 08:30 | 221 | 221
2018-09-07 09:00 | 198 | 197
2018-09-07 09:30 | 191 | 189
2018-09-07 10:00 | 188 | 187
2018-09-07 10:30 | 180 | 178
2018-09-07 11:00 | 175 | 174
2018-09-07 11:30 | 172 | 170
2018-09-07 12:00 | 174 | 173
2018-09-07 12:30 | 177 | 176
2018-09-07 13:00 | 170 | 169
2018-09-07 13:30 | 163 | 161
2018-09-07 14:00 | 168 | 166
2018-09-07 14:30 | 170 | 169
2018-09-07 15:00 | 178 | 177
2018-09-07 15:30 | 189 | 188
2018-09-07 16:00 | 207 | 206
2018-09-07 16:30 | 214 | 212
2018-09-07 17:00 | 228 | 227
2018-09-07 17:30 | 238 | 236
2018-09-07 18:00 | 245 | 243
2018-09-07 18:30 | 249 | 247
2018-09-07 19:00 | 251 | 249
2018-09-07 19:30 | 247 | 245
2018-09-07 20:00 | 244 | 242
2018-09-07 20:30 | 243 | 240
2018-09-07 21:00 | 232 | 231
2018-09-07 21:30 | 222 | 222
2018-09-07 22:00 | 213 | 213
2018-09-07 22:30 | 214 | 214
2018-09-07 23:00 | 212 | 212
2018-09-07 23:30 | 201 | 201
2018-09-08 | 186 | 186
2018-09-08 00:30 | 171 | 170
2018-09-08 01:00 | 161 | 160
2018-09-08 01:30 | 155 | 154
2018-09-08 02:00 | 148 | 148
2018-09-08 02:30 | 144 | 144
2018-09-08 03:00 | 142 | 142
2018-09-08 03:30 | 141 | 141
2018-09-08 04:00 | 142 | 142
2018-09-08 04:30 | 141 | 141
2018-09-08 05:00 | 143 | 143
2018-09-08 05:30 | 148 | 148
2018-09-08 06:00 | 152 | 152
2018-09-08 06:30 | 159 | 159
2018-09-08 07:00 | 169 | 169
2018-09-08 07:30 | 180 | 180
2018-09-08 08:00 | 188 | 188
2018-09-08 08:30 | 193 | 193
2018-09-08 09:00 | 199 | 199
2018-09-08 09:30 | 195 | 195
2018-09-08 10:00 | 199 | 199
2018-09-08 10:30 | 197 | 196
2018-09-08 11:00 | 187 | 187
2018-09-08 11:30 | 166 | 165
2018-09-08 12:00 | 155 | 155
2018-09-08 12:30 | 144 | 144
2018-09-08 13:00 | 155 | 154
2018-09-08 13:30 | 167 | 167
2018-09-08 14:00 | 184 | 184
2018-09-08 14:30 | 186 | 186
2018-09-08 15:00 | 188 | 187
2018-09-08 15:30 | 184 | 184
2018-09-08 16:00 | 189 | 189
2018-09-08 16:30 | 202 | 202
2018-09-08 17:00 | 212 | 212
2018-09-08 17:30 | 214 | 213
2018-09-08 18:00 | 221 | 220
2018-09-08 18:30 | 233 | 233
2018-09-08 19:00 | 236 | 235
2018-09-08 19:30 | 229 | 228
2018-09-08 20:00 | 224 | 223
2018-09-08 20:30 | 222 | 222
2018-09-08 21:00 | 213 | 213
2018-09-08 21:30 | 206 | 206
2018-09-08 22:00 | 201 | 201
2018-09-08 22:30 | 200 | 200
2018-09-08 23:00 | 200 | 200
2018-09-08 23:30 | 192 | 192
2018-09-09 | 177 | 177
2018-09-09 00:30 | 163 | 162
2018-09-09 01:00 | 152 | 152
2018-09-09 01:30 | 146 | 146
2018-09-09 02:00 | 140 | 139
2018-09-09 02:30 | 138 | 137
2018-09-09 03:00 | 136 | 135
2018-09-09 03:30 | 134 | 133
2018-09-09 04:00 | 134 | 133
2018-09-09 04:30 | 134 | 133
2018-09-09 05:00 | 135 | 134
2018-09-09 05:30 | 137 | 136
2018-09-09 06:00 | 138 | 137
2018-09-09 06:30 | 141 | 141
2018-09-09 07:00 | 143 | 143
2018-09-09 07:30 | 143 | 143
2018-09-09 08:00 | 142 | 142
2018-09-09 08:30 | 139 | 139
2018-09-09 09:00 | 137 | 137
2018-09-09 09:30 | 133 | 133
2018-09-09 10:00 | 128 | 128
2018-09-09 10:30 | 123 | 123
2018-09-09 11:00 | 118 | 118
2018-09-09 11:30 | 117 | 117
2018-09-09 12:00 | 113 | 112
2018-09-09 12:30 | 113 | 112
2018-09-09 13:00 | 114 | 113
2018-09-09 13:30 | 115 | 115
2018-09-09 14:00 | 120 | 120
2018-09-09 14:30 | 126 | 126
2018-09-09 15:00 | 141 | 141
2018-09-09 15:30 | 155 | 155
2018-09-09 16:00 | 171 | 170
2018-09-09 16:30 | 187 | 186
2018-09-09 17:00 | 203 | 202
2018-09-09 17:30 | 215 | 215
2018-09-09 18:00 | 228 | 227
2018-09-09 18:30 | 243 | 241
2018-09-09 19:00 | 244 | 243
2018-09-09 19:30 | 237 | 236
2018-09-09 20:00 | 234 | 233
2018-09-09 20:30 | 234 | 233
2018-09-09 21:00 | 224 | 223
2018-09-09 21:30 | 214 | 214
2018-09-09 22:00 | 207 | 207
2018-09-09 22:30 | 203 | 203
2018-09-09 23:00 | 201 | 201
2018-09-09 23:30 | 191 | 191
2018-09-10 | 178 | 178
2018-09-10 00:30 | 165 | 165
2018-09-10 01:00 | 156 | 155
2018-09-10 01:30 | 150 | 149
2018-09-10 02:00 | 145 | 144
2018-09-10 02:30 | 143 | 142
2018-09-10 03:00 | 141 | 141
2018-09-10 03:30 | 141 | 141
2018-09-10 04:00 | 143 | 143
2018-09-10 04:30 | 148 | 148
2018-09-10 05:00 | 156 | 156
2018-09-10 05:30 | 172 | 172
2018-09-10 06:00 | 188 | 188
2018-09-10 06:30 | 212 | 211
2018-09-10 07:00 | 226 | 225
2018-09-10 07:30 | 231 | 230
2018-09-10 08:00 | 222 | 221
2018-09-10 08:30 | 206 | 205
2018-09-10 09:00 | 190 | 190
2018-09-10 09:30 | 179 | 178
2018-09-10 10:00 | 170 | 170
2018-09-10 10:30 | 164 | 164
2018-09-10 11:00 | 160 | 159
2018-09-10 11:30 | 157 | 156
2018-09-10 12:00 | 157 | 156
2018-09-10 12:30 | 158 | 157
2018-09-10 13:00 | 160 | 159
2018-09-10 13:30 | 164 | 163
2018-09-10 14:00 | 168 | 168
2018-09-10 14:30 | 176 | 175
2018-09-10 15:00 | 183 | 182
2018-09-10 15:30 | 194 | 193
2018-09-10 16:00 | 209 | 208
2018-09-10 16:30 | 226 | 225
2018-09-10 17:00 | 242 | 242
2018-09-10 17:30 | 254 | 253
2018-09-10 18:00 | 266 | 266
2018-09-10 18:30 | 274 | 274
2018-09-10 19:00 | 275 | 275
2018-09-10 19:30 | 270 | 269
2018-09-10 20:00 | 263 | 263
2018-09-10 20:30 | 260 | 260
2018-09-10 21:00 | 249 | 249
2018-09-10 21:30 | 238 | 238
2018-09-10 22:00 | 229 | 228
2018-09-10 22:30 | 223 | 223
2018-09-10 23:00 | 215 | 215
2018-09-10 23:30 | 205 | 205
2018-09-11 | 189 | 189
2018-09-11 00:30 | 173 | 173
2018-09-11 01:00 | 164 | 164
2018-09-11 01:30 | 158 | 158
2018-09-11 02:00 | 153 | 153
2018-09-11 02:30 | 150 | 150
2018-09-11 03:00 | 148 | 148
2018-09-11 03:30 | 150 | 150
2018-09-11 04:00 | 149 | 148
2018-09-11 04:30 | 155 | 155
2018-09-11 05:00 | 163 | 163
2018-09-11 05:30 | 178 | 178
2018-09-11 06:00 | 195 | 194
2018-09-11 06:30 | 216 | 215
2018-09-11 07:00 | 232 | 231
2018-09-11 07:30 | 239 | 238
2018-09-11 08:00 | 230 | 230
2018-09-11 08:30 | 215 | 214
2018-09-11 09:00 | 198 | 197
2018-09-11 09:30 | 186 | 186
2018-09-11 10:00 | 178 | 176
2018-09-11 10:30 | 172 | 170
2018-09-11 11:00 | 171 | 169
2018-09-11 11:30 | 169 | 168
2018-09-11 12:00 | 169 | 168
2018-09-11 12:30 | 169 | 168
2018-09-11 13:00 | 173 | 172
2018-09-11 13:30 | 179 | 178
2018-09-11 14:00 | 185 | 184
2018-09-11 14:30 | 191 | 189
2018-09-11 15:00 | 193 | 192
2018-09-11 15:30 | 200 | 199
2018-09-11 16:00 | 213 | 212
2018-09-11 16:30 | 229 | 228
2018-09-11 17:00 | 244 | 243
2018-09-11 17:30 | 254 | 254
2018-09-11 18:00 | 266 | 266
2018-09-11 18:30 | 273 | 273
2018-09-11 19:00 | 274 | 274
2018-09-11 19:30 | 267 | 267
2018-09-11 20:00 | 264 | 264
2018-09-11 20:30 | 262 | 262
2018-09-11 21:00 | 251 | 250
2018-09-11 21:30 | 236 | 236
2018-09-11 22:00 | 227 | 226
2018-09-11 22:30 | 220 | 220
2018-09-11 23:00 | 216 | 216
2018-09-11 23:30 | 204 | 204
2018-09-12 | 190 | 189
2018-09-12 00:30 | 174 | 173
2018-09-12 01:00 | 165 | 164
2018-09-12 01:30 | 159 | 158
2018-09-12 02:00 | 154 | 153
2018-09-12 02:30 | 151 | 149
2018-09-12 03:00 | 150 | 148
2018-09-12 03:30 | 150 | 149
2018-09-12 04:00 | 149 | 149
2018-09-12 04:30 | 154 | 154
2018-09-12 05:00 | 162 | 162
2018-09-12 05:30 | 178 | 178
2018-09-12 06:00 | 193 | 192
2018-09-12 06:30 | 211 | 211
2018-09-12 07:00 | 226 | 226
2018-09-12 07:30 | 212 | 212
2018-09-12 08:00 | 190 | 190
2018-09-12 08:30 | 178 | 178
2018-09-12 09:00 | 170 | 170
2018-09-12 09:30 | 161 | 161
2018-09-12 10:00 | 158 | 158
2018-09-12 10:30 | 164 | 163
2018-09-12 11:00 | 157 | 157
2018-09-12 11:30 | 151 | 150
2018-09-12 12:00 | 149 | 149
2018-09-12 12:30 | 150 | 150
2018-09-12 13:00 | 148 | 147
2018-09-12 13:30 | 149 | 149
2018-09-12 14:00 | 152 | 152
2018-09-12 14:30 | 155 | 154
2018-09-12 15:00 | 159 | 158
2018-09-12 15:30 | 165 | 165
2018-09-12 16:00 | 178 | 178
2018-09-12 16:30 | 191 | 190
2018-09-12 17:00 | 203 | 203
2018-09-12 17:30 | 212 | 212
2018-09-12 18:00 | 222 | 222
2018-09-12 18:30 | 229 | 229
2018-09-12 19:00 | 231 | 231
2018-09-12 19:30 | 226 | 226
2018-09-12 20:00 | 223 | 223
2018-09-12 20:30 | 220 | 220
2018-09-12 21:00 | 212 | 212
2018-09-12 21:30 | 204 | 203
2018-09-12 22:00 | 194 | 194
2018-09-12 22:30 | 188 | 188
2018-09-12 23:00 | 185 | 184
2018-09-12 23:30 | 174 | 174
2018-09-13 | 161 | 161
2018-09-13 00:30 | 147 | 147
2018-09-13 01:00 | 139 | 139
2018-09-13 01:30 | 133 | 133
2018-09-13 02:00 | 128 | 128
2018-09-13 02:30 | 124 | 123
2018-09-13 03:00 | 122 | 122
2018-09-13 03:30 | 125 | 124
2018-09-13 04:00 | 125 | 124
2018-09-13 04:30 | 128 | 128
2018-09-13 05:00 | 135 | 135
2018-09-13 05:30 | 148 | 148
2018-09-13 06:00 | 159 | 159
2018-09-13 06:30 | 179 | 179
2018-09-13 07:00 | 192 | 192
2018-09-13 07:30 | 195 | 195
2018-09-13 08:00 | 188 | 188
2018-09-13 08:30 | 176 | 176
2018-09-13 09:00 | 163 | 163
2018-09-13 09:30 | 153 | 153
2018-09-13 10:00 | 147 | 147
2018-09-13 10:30 | 143 | 143
2018-09-13 11:00 | 139 | 139
2018-09-13 11:30 | 138 | 138
2018-09-13 12:00 | 139 | 139
2018-09-13 12:30 | 139 | 139
2018-09-13 13:00 | 141 | 141
2018-09-13 13:30 | 145 | 145
2018-09-13 14:00 | 151 | 151
2018-09-13 14:30 | 156 | 156
2018-09-13 15:00 | 163 | 163
2018-09-13 15:30 | 171 | 171
2018-09-13 16:00 | 183 | 183
2018-09-13 16:30 | 195 | 195
2018-09-13 17:00 | 206 | 206
2018-09-13 17:30 | 213 | 213
2018-09-13 18:00 | 222 | 222
2018-09-13 18:30 | 230 | 230
2018-09-13 19:00 | 232 | 232
2018-09-13 19:30 | 227 | 227
2018-09-13 20:00 | 225 | 225
2018-09-13 20:30 | 223 | 223
2018-09-13 21:00 | 214 | 214
2018-09-13 21:30 | 204 | 204
2018-09-13 22:00 | 195 | 195
2018-09-13 22:30 | 188 | 187
2018-09-13 23:00 | 185 | 184
2018-09-13 23:30 | 173 | 172
2018-09-14 | 159 | 159
2018-09-14 00:30 | 145 | 145
2018-09-14 01:00 | 136 | 136
2018-09-14 01:30 | 131 | 131
2018-09-14 02:00 | 127 | 127
2018-09-14 02:30 | 125 | 125
2018-09-14 03:00 | 124 | 124
2018-09-14 03:30 | 124 | 124
2018-09-14 04:00 | 125 | 125
2018-09-14 04:30 | 128 | 128
2018-09-14 05:00 | 133 | 133
2018-09-14 05:30 | 145 | 145
2018-09-14 06:00 | 155 | 155
2018-09-14 06:30 | 169 | 169
2018-09-14 07:00 | 182 | 181
2018-09-14 07:30 | 187 | 187
2018-09-14 08:00 | 181 | 181
2018-09-14 08:30 | 176 | 176
2018-09-14 09:00 | 191 | 191
2018-09-14 09:30 | 193 | 193
2018-09-14 10:00 | 192 | 191
2018-09-14 10:30 | 184 | 184
2018-09-14 11:00 | 179 | 179
2018-09-14 11:30 | 173 | 173
2018-09-14 12:00 | 168 | 167
2018-09-14 12:30 | 169 | 169
2018-09-14 13:00 | 171 | 170
2018-09-14 13:30 | 170 | 169
2018-09-14 14:00 | 173 | 173
2018-09-14 14:30 | 179 | 179
2018-09-14 15:00 | 186 | 185
2018-09-14 15:30 | 195 | 195
2018-09-14 16:00 | 209 | 208
2018-09-14 16:30 | 222 | 222
2018-09-14 17:00 | 237 | 236
2018-09-14 17:30 | 243 | 242
2018-09-14 18:00 | 245 | 245
2018-09-14 18:30 | 252 | 252
2018-09-14 19:00 | 254 | 254
2018-09-14 19:30 | 245 | 245
2018-09-14 20:00 | 243 | 243
2018-09-14 20:30 | 243 | 243
2018-09-14 21:00 | 234 | 232
2018-09-14 21:30 | 224 | 222
2018-09-14 22:00 | 216 | 215
2018-09-14 22:30 | 212 | 211
2018-09-14 23:00 | 210 | 209
2018-09-14 23:30 | 199 | 199
2018-09-15 | 183 | 183
2018-09-15 00:30 | 168 | 168
2018-09-15 01:00 | 158 | 158
2018-09-15 01:30 | 152 | 152
2018-09-15 02:00 | 144 | 144
2018-09-15 02:30 | 140 | 140
2018-09-15 03:00 | 138 | 138
2018-09-15 03:30 | 139 | 139
2018-09-15 04:00 | 139 | 139
2018-09-15 04:30 | 138 | 138
2018-09-15 05:00 | 140 | 140
2018-09-15 05:30 | 147 | 147
2018-09-15 06:00 | 148 | 148
2018-09-15 06:30 | 155 | 155
2018-09-15 07:00 | 158 | 158
2018-09-15 07:30 | 158 | 158
2018-09-15 08:00 | 157 | 157
2018-09-15 08:30 | 156 | 156
2018-09-15 09:00 | 152 | 152
2018-09-15 09:30 | 145 | 145
2018-09-15 10:00 | 138 | 138
2018-09-15 10:30 | 130 | 130
2018-09-15 11:00 | 127 | 127
2018-09-15 11:30 | 122 | 122
2018-09-15 12:00 | 119 | 119
2018-09-15 12:30 | 117 | 117
2018-09-15 13:00 | 120 | 120
2018-09-15 13:30 | 122 | 122
2018-09-15 14:00 | 130 | 130
2018-09-15 14:30 | 138 | 137
2018-09-15 15:00 | 145 | 144
2018-09-15 15:30 | 156 | 156
2018-09-15 16:00 | 173 | 172
2018-09-15 16:30 | 186 | 185
2018-09-15 17:00 | 200 | 199
2018-09-15 17:30 | 206 | 205
2018-09-15 18:00 | 215 | 214
2018-09-15 18:30 | 227 | 225
2018-09-15 19:00 | 229 | 228
2018-09-15 19:30 | 223 | 222
2018-09-15 20:00 | 222 | 221
2018-09-15 20:30 | 220 | 219
2018-09-15 21:00 | 210 | 209
2018-09-15 21:30 | 203 | 203
2018-09-15 22:00 | 198 | 198
2018-09-15 22:30 | 199 | 198
2018-09-15 23:00 | 197 | 197
2018-09-15 23:30 | 187 | 186
2018-09-16 | 173 | 173
2018-09-16 00:30 | 159 | 159
2018-09-16 01:00 | 150 | 150
2018-09-16 01:30 | 144 | 144
2018-09-16 02:00 | 138 | 137
2018-09-16 02:30 | 134 | 134
2018-09-16 03:00 | 132 | 132
2018-09-16 03:30 | 130 | 130
2018-09-16 04:00 | 130 | 130
2018-09-16 04:30 | 132 | 131
2018-09-16 05:00 | 131 | 131
2018-09-16 05:30 | 133 | 133
2018-09-16 06:00 | 136 | 135
2018-09-16 06:30 | 139 | 139
2018-09-16 07:00 | 140 | 140
2018-09-16 07:30 | 139 | 139
2018-09-16 08:00 | 138 | 138
2018-09-16 08:30 | 140 | 140
2018-09-16 09:00 | 138 | 138
2018-09-16 09:30 | 136 | 136
2018-09-16 10:00 | 147 | 147
2018-09-16 10:30 | 148 | 147
2018-09-16 11:00 | 129 | 129
2018-09-16 11:30 | 124 | 123
2018-09-16 12:00 | 120 | 120
2018-09-16 12:30 | 121 | 121
2018-09-16 13:00 | 125 | 125
2018-09-16 13:30 | 128 | 128
2018-09-16 14:00 | 133 | 133
2018-09-16 14:30 | 132 | 132
2018-09-16 15:00 | 140 | 140
2018-09-16 15:30 | 150 | 150
2018-09-16 16:00 | 165 | 165
2018-09-16 16:30 | 179 | 178
2018-09-16 17:00 | 195 | 195
2018-09-16 17:30 | 208 | 207
2018-09-16 18:00 | 223 | 222
2018-09-16 18:30 | 239 | 239
2018-09-16 19:00 | 240 | 240
2018-09-16 19:30 | 234 | 234
2018-09-16 20:00 | 230 | 230
2018-09-16 20:30 | 227 | 227
2018-09-16 21:00 | 216 | 215
2018-09-16 21:30 | 205 | 205
2018-09-16 22:00 | 197 | 197
2018-09-16 22:30 | 194 | 193
2018-09-16 23:00 | 192 | 192
2018-09-16 23:30 | 182 | 182
2018-09-17 | 169 | 169
2018-09-17 00:30 | 155 | 155
2018-09-17 01:00 | 148 | 147
2018-09-17 01:30 | 142 | 142
2018-09-17 02:00 | 138 | 138
2018-09-17 02:30 | 137 | 136
2018-09-17 03:00 | 136 | 135
2018-09-17 03:30 | 135 | 134
2018-09-17 04:00 | 136 | 135
2018-09-17 04:30 | 140 | 140
2018-09-17 05:00 | 149 | 149
2018-09-17 05:30 | 164 | 164
2018-09-17 06:00 | 176 | 176
2018-09-17 06:30 | 197 | 197
2018-09-17 07:00 | 211 | 210
2018-09-17 07:30 | 214 | 213
2018-09-17 08:00 | 206 | 206
2018-09-17 08:30 | 191 | 191
2018-09-17 09:00 | 178 | 178
2018-09-17 09:30 | 167 | 167
2018-09-17 10:00 | 160 | 158
2018-09-17 10:30 | 156 | 153
2018-09-17 11:00 | 155 | 151
2018-09-17 11:30 | 156 | 153
2018-09-17 12:00 | 159 | 156
2018-09-17 12:30 | 164 | 160
2018-09-17 13:00 | 162 | 159
2018-09-17 13:30 | 171 | 168
2018-09-17 14:00 | 176 | 173
2018-09-17 14:30 | 184 | 180
2018-09-17 15:00 | 187 | 183
2018-09-17 15:30 | 194 | 190
2018-09-17 16:00 | 205 | 203
2018-09-17 16:30 | 222 | 221
2018-09-17 17:00 | 239 | 238
2018-09-17 17:30 | 250 | 250
2018-09-17 18:00 | 260 | 260
2018-09-17 18:30 | 271 | 271
2018-09-17 19:00 | 273 | 273
2018-09-17 19:30 | 265 | 264
2018-09-17 20:00 | 261 | 260
2018-09-17 20:30 | 257 | 257
2018-09-17 21:00 | 245 | 245
2018-09-17 21:30 | 235 | 235
2018-09-17 22:00 | 223 | 222
2018-09-17 22:30 | 217 | 216
2018-09-17 23:00 | 213 | 212
2018-09-17 23:30 | 201 | 201
2018-09-18 | 186 | 186
2018-09-18 00:30 | 171 | 171
2018-09-18 01:00 | 162 | 161
2018-09-18 01:30 | 156 | 155
2018-09-18 02:00 | 152 | 152
2018-09-18 02:30 | 149 | 149
2018-09-18 03:00 | 148 | 148
2018-09-18 03:30 | 147 | 147
2018-09-18 04:00 | 149 | 149
2018-09-18 04:30 | 153 | 153
2018-09-18 05:00 | 159 | 159
2018-09-18 05:30 | 176 | 175
2018-09-18 06:00 | 190 | 190
2018-09-18 06:30 | 211 | 211
2018-09-18 07:00 | 222 | 222
2018-09-18 07:30 | 226 | 226
2018-09-18 08:00 | 215 | 215
2018-09-18 08:30 | 204 | 204
2018-09-18 09:00 | 196 | 196
2018-09-18 09:30 | 193 | 193
2018-09-18 10:00 | 197 | 197
2018-09-18 10:30 | 197 | 197
2018-09-18 11:00 | 198 | 198
2018-09-18 11:30 | 193 | 192
2018-09-18 12:00 | 186 | 186
2018-09-18 12:30 | 183 | 183
2018-09-18 13:00 | 179 | 179
2018-09-18 13:30 | 178 | 177
2018-09-18 14:00 | 179 | 179
2018-09-18 14:30 | 184 | 184
2018-09-18 15:00 | 186 | 186
2018-09-18 15:30 | 192 | 192
2018-09-18 16:00 | 205 | 205
2018-09-18 16:30 | 220 | 220
2018-09-18 17:00 | 237 | 237
2018-09-18 17:30 | 247 | 247
2018-09-18 18:00 | 256 | 255
2018-09-18 18:30 | 268 | 268
2018-09-18 19:00 | 270 | 269
2018-09-18 19:30 | 264 | 264
2018-09-18 20:00 | 259 | 259
2018-09-18 20:30 | 258 | 258
2018-09-18 21:00 | 248 | 248
2018-09-18 21:30 | 235 | 234
2018-09-18 22:00 | 225 | 224
2018-09-18 22:30 | 219 | 218
2018-09-18 23:00 | 215 | 214
2018-09-18 23:30 | 202 | 201
2018-09-19 | 185 | 185
2018-09-19 00:30 | 171 | 171
2018-09-19 01:00 | 161 | 161
2018-09-19 01:30 | 154 | 154
2018-09-19 02:00 | 149 | 149
2018-09-19 02:30 | 147 | 147
2018-09-19 03:00 | 147 | 147
2018-09-19 03:30 | 147 | 147
2018-09-19 04:00 | 147 | 147
2018-09-19 04:30 | 151 | 151
2018-09-19 05:00 | 159 | 159
2018-09-19 05:30 | 174 | 173
2018-09-19 06:00 | 185 | 184
2018-09-19 06:30 | 204 | 202
2018-09-19 07:00 | 217 | 214
2018-09-19 07:30 | 220 | 219
2018-09-19 08:00 | 210 | 209
2018-09-19 08:30 | 147 | 146
2018-09-19 09:00 | 128 | 127
2018-09-19 09:30 | 122 | 122
2018-09-19 10:00 | 116 | 116
2018-09-19 10:30 | 112 | 112
2018-09-19 11:00 | 109 | 109
2018-09-19 11:30 | 108 | 107
2018-09-19 12:00 | 107 | 107
2018-09-19 12:30 | 107 | 107
2018-09-19 13:00 | 109 | 109
2018-09-19 13:30 | 111 | 111
2018-09-19 14:00 | 117 | 117
2018-09-19 14:30 | 176 | 175
2018-09-19 15:00 | 184 | 184
2018-09-19 15:30 | 194 | 194
2018-09-19 16:00 | 209 | 209
2018-09-19 16:30 | 222 | 222
2018-09-19 17:00 | 239 | 239
2018-09-19 17:30 | 248 | 248
2018-09-19 18:00 | 255 | 255
2018-09-19 18:30 | 265 | 265
2018-09-19 19:00 | 267 | 267
2018-09-19 19:30 | 260 | 260
2018-09-19 20:00 | 256 | 256
2018-09-19 20:30 | 254 | 254
2018-09-19 21:00 | 241 | 240
2018-09-19 21:30 | 230 | 229
2018-09-19 22:00 | 220 | 219
2018-09-19 22:30 | 213 | 212
2018-09-19 23:00 | 209 | 208
2018-09-19 23:30 | 196 | 195
2018-09-20 | 186 | 186
2018-09-20 00:30 | 171 | 171
2018-09-20 01:00 | 162 | 162
2018-09-20 01:30 | 156 | 156
2018-09-20 02:00 | 151 | 151
2018-09-20 02:30 | 149 | 149
2018-09-20 03:00 | 147 | 147
2018-09-20 03:30 | 148 | 148
2018-09-20 04:00 | 148 | 148
2018-09-20 04:30 | 153 | 153
2018-09-20 05:00 | 160 | 160
2018-09-20 05:30 | 174 | 173
2018-09-20 06:00 | 186 | 185
2018-09-20 06:30 | 204 | 202
2018-09-20 07:00 | 217 | 216
2018-09-20 07:30 | 220 | 220
2018-09-20 08:00 | 212 | 212
2018-09-20 08:30 | 201 | 201
2018-09-20 09:00 | 193 | 193
2018-09-20 09:30 | 188 | 188
2018-09-20 10:00 | 190 | 190
2018-09-20 10:30 | 192 | 191
2018-09-20 11:00 | 186 | 186
2018-09-20 11:30 | 181 | 181
2018-09-20 12:00 | 181 | 181
2018-09-20 12:30 | 189 | 188
2018-09-20 13:00 | 196 | 195
2018-09-20 13:30 | 201 | 200
2018-09-20 14:00 | 208 | 207
2018-09-20 14:30 | 205 | 204
2018-09-20 15:00 | 203 | 203
2018-09-20 15:30 | 208 | 207
2018-09-20 16:00 | 221 | 220
2018-09-20 16:30 | 235 | 234
2018-09-20 17:00 | 247 | 247
2018-09-20 17:30 | 255 | 255
2018-09-20 18:00 | 263 | 263
2018-09-20 18:30 | 273 | 272
2018-09-20 19:00 | 275 | 275
2018-09-20 19:30 | 268 | 267
2018-09-20 20:00 | 264 | 264
2018-09-20 20:30 | 262 | 261
2018-09-20 21:00 | 250 | 250
2018-09-20 21:30 | 235 | 234
2018-09-20 22:00 | 228 | 226
2018-09-20 22:30 | 222 | 221
2018-09-20 23:00 | 217 | 217
2018-09-20 23:30 | 205 | 205
2018-09-21 | 189 | 189
2018-09-21 00:30 | 172 | 172
2018-09-21 01:00 | 162 | 162
2018-09-21 01:30 | 156 | 156
2018-09-21 02:00 | 152 | 152
2018-09-21 02:30 | 150 | 150
2018-09-21 03:00 | 149 | 149
2018-09-21 03:30 | 149 | 149
2018-09-21 04:00 | 150 | 150
2018-09-21 04:30 | 154 | 153
2018-09-21 05:00 | 160 | 160
2018-09-21 05:30 | 174 | 174
2018-09-21 06:00 | 186 | 186
2018-09-21 06:30 | 201 | 200
2018-09-21 07:00 | 212 | 211
2018-09-21 07:30 | 219 | 217
2018-09-21 08:00 | 212 | 210
2018-09-21 08:30 | 200 | 197
2018-09-21 09:00 | 186 | 184
2018-09-21 09:30 | 178 | 176
2018-09-21 10:00 | 170 | 167
2018-09-21 10:30 | 166 | 163
2018-09-21 11:00 | 165 | 161
2018-09-21 11:30 | 162 | 159
2018-09-21 12:00 | 164 | 161
2018-09-21 12:30 | 168 | 164
2018-09-21 13:00 | 173 | 170
2018-09-21 13:30 | 172 | 169
2018-09-21 14:00 | 173 | 170
2018-09-21 14:30 | 179 | 176
2018-09-21 15:00 | 184 | 181
2018-09-21 15:30 | 192 | 189
2018-09-21 16:00 | 206 | 203
2018-09-21 16:30 | 219 | 217
2018-09-21 17:00 | 234 | 234
2018-09-21 17:30 | 241 | 241
2018-09-21 18:00 | 246 | 246
2018-09-21 18:30 | 256 | 255
2018-09-21 19:00 | 259 | 259
2018-09-21 19:30 | 255 | 252
2018-09-21 20:00 | 252 | 249
2018-09-21 20:30 | 250 | 247
2018-09-21 21:00 | 241 | 239
2018-09-21 21:30 | 231 | 229
2018-09-21 22:00 | 222 | 221
2018-09-21 22:30 | 221 | 220
2018-09-21 23:00 | 218 | 217
2018-09-21 23:30 | 205 | 205
2018-09-22 | 190 | 190
2018-09-22 00:30 | 173 | 173
2018-09-22 01:00 | 163 | 163
2018-09-22 01:30 | 157 | 157
2018-09-22 02:00 | 152 | 151
2018-09-22 02:30 | 148 | 148
2018-09-22 03:00 | 147 | 146
2018-09-22 03:30 | 146 | 146
2018-09-22 04:00 | 145 | 145
2018-09-22 04:30 | 146 | 146
2018-09-22 05:00 | 149 | 149
2018-09-22 05:30 | 154 | 154
2018-09-22 06:00 | 157 | 157
2018-09-22 06:30 | 164 | 164
2018-09-22 07:00 | 166 | 166
2018-09-22 07:30 | 168 | 167
2018-09-22 08:00 | 166 | 166
2018-09-22 08:30 | 163 | 162
2018-09-22 09:00 | 155 | 155
2018-09-22 09:30 | 150 | 150
2018-09-22 10:00 | 154 | 154
2018-09-22 10:30 | 157 | 157
2018-09-22 11:00 | 154 | 154
2018-09-22 11:30 | 149 | 149
2018-09-22 12:00 | 148 | 147
2018-09-22 12:30 | 140 | 140
2018-09-22 13:00 | 134 | 133
2018-09-22 13:30 | 134 | 134
2018-09-22 14:00 | 134 | 134
2018-09-22 14:30 | 136 | 136
2018-09-22 15:00 | 142 | 142
2018-09-22 15:30 | 151 | 151
2018-09-22 16:00 | 165 | 165
2018-09-22 16:30 | 181 | 181
2018-09-22 17:00 | 197 | 197
2018-09-22 17:30 | 204 | 203
2018-09-22 18:00 | 211 | 211
2018-09-22 18:30 | 224 | 224
2018-09-22 19:00 | 227 | 227
2018-09-22 19:30 | 223 | 223
2018-09-22 20:00 | 221 | 221
2018-09-22 20:30 | 218 | 218
2018-09-22 21:00 | 208 | 208
2018-09-22 21:30 | 201 | 201
2018-09-22 22:00 | 197 | 196
2018-09-22 22:30 | 195 | 195
2018-09-22 23:00 | 194 | 194
2018-09-22 23:30 | 185 | 185
2018-09-23 | 173 | 173
2018-09-23 00:30 | 160 | 160
2018-09-23 01:00 | 151 | 151
2018-09-23 01:30 | 145 | 145
2018-09-23 02:00 | 140 | 140
2018-09-23 02:30 | 136 | 135
2018-09-23 03:00 | 135 | 135
2018-09-23 03:30 | 133 | 132
2018-09-23 04:00 | 133 | 132
2018-09-23 04:30 | 133 | 132
2018-09-23 05:00 | 134 | 133
2018-09-23 05:30 | 137 | 137
2018-09-23 06:00 | 139 | 138
2018-09-23 06:30 | 141 | 140
2018-09-23 07:00 | 139 | 139
2018-09-23 07:30 | 138 | 138
2018-09-23 08:00 | 136 | 135
2018-09-23 08:30 | 133 | 133
2018-09-23 09:00 | 129 | 129
2018-09-23 09:30 | 125 | 125
2018-09-23 10:00 | 120 | 120
2018-09-23 10:30 | 117 | 117
2018-09-23 11:00 | 113 | 113
2018-09-23 11:30 | 110 | 110
2018-09-23 12:00 | 110 | 110
2018-09-23 12:30 | 111 | 111
2018-09-23 13:00 | 113 | 113
2018-09-23 13:30 | 116 | 116
2018-09-23 14:00 | 123 | 123
2018-09-23 14:30 | 128 | 128
2018-09-23 15:00 | 137 | 137
2018-09-23 15:30 | 148 | 148
2018-09-23 16:00 | 162 | 162
2018-09-23 16:30 | 177 | 177
2018-09-23 17:00 | 193 | 192
2018-09-23 17:30 | 205 | 204
2018-09-23 18:00 | 216 | 215
2018-09-23 18:30 | 231 | 231
2018-09-23 19:00 | 234 | 234
2018-09-23 19:30 | 226 | 226
2018-09-23 20:00 | 223 | 223
2018-09-23 20:30 | 219 | 219
2018-09-23 21:00 | 210 | 210
2018-09-23 21:30 | 202 | 202
2018-09-23 22:00 | 195 | 195
2018-09-23 22:30 | 192 | 191
2018-09-23 23:00 | 191 | 191
2018-09-23 23:30 | 181 | 181
2018-09-24 | 167 | 167
2018-09-24 00:30 | 154 | 154
2018-09-24 01:00 | 146 | 146
2018-09-24 01:30 | 140 | 140
2018-09-24 02:00 | 137 | 137
2018-09-24 02:30 | 135 | 135
2018-09-24 03:00 | 134 | 134
2018-09-24 03:30 | 135 | 135
2018-09-24 04:00 | 136 | 136
2018-09-24 04:30 | 140 | 140
2018-09-24 05:00 | 147 | 147
2018-09-24 05:30 | 161 | 161
2018-09-24 06:00 | 170 | 170
2018-09-24 06:30 | 185 | 184
2018-09-24 07:00 | 193 | 193
2018-09-24 07:30 | 195 | 195
2018-09-24 08:00 | 191 | 191
2018-09-24 08:30 | 189 | 189
2018-09-24 09:00 | 191 | 191
2018-09-24 09:30 | 189 | 189
2018-09-24 10:00 | 186 | 186
2018-09-24 10:30 | 185 | 185
2018-09-24 11:00 | 183 | 183
2018-09-24 11:30 | 180 | 179
2018-09-24 12:00 | 189 | 188
2018-09-24 12:30 | 199 | 199
2018-09-24 13:00 | 212 | 212
2018-09-24 13:30 | 217 | 216
2018-09-24 14:00 | 214 | 213
2018-09-24 14:30 | 204 | 204
2018-09-24 15:00 | 196 | 196
2018-09-24 15:30 | 201 | 201
2018-09-24 16:00 | 213 | 213
2018-09-24 16:30 | 226 | 226
2018-09-24 17:00 | 239 | 239
2018-09-24 17:30 | 248 | 248
2018-09-24 18:00 | 257 | 257
2018-09-24 18:30 | 265 | 265
2018-09-24 19:00 | 266 | 266
2018-09-24 19:30 | 258 | 258
2018-09-24 20:00 | 253 | 253
2018-09-24 20:30 | 251 | 251
2018-09-24 21:00 | 240 | 240
2018-09-24 21:30 | 228 | 228
2018-09-24 22:00 | 219 | 219
2018-09-24 22:30 | 212 | 212
2018-09-24 23:00 | 207 | 207
2018-09-24 23:30 | 196 | 196
2018-09-25 | 181 | 181
2018-09-25 00:30 | 167 | 167
2018-09-25 01:00 | 158 | 158
2018-09-25 01:30 | 151 | 151
2018-09-25 02:00 | 147 | 147
2018-09-25 02:30 | 145 | 145
2018-09-25 03:00 | 143 | 143
2018-09-25 03:30 | 143 | 143
2018-09-25 04:00 | 144 | 144
2018-09-25 04:30 | 148 | 148
2018-09-25 05:00 | 155 | 155
2018-09-25 05:30 | 167 | 167
2018-09-25 06:00 | 178 | 178
2018-09-25 06:30 | 195 | 195
2018-09-25 07:00 | 212 | 212
2018-09-25 07:30 | 224 | 224
2018-09-25 08:00 | 231 | 231
2018-09-25 08:30 | 235 | 235
2018-09-25 09:00 | 225 | 225
2018-09-25 09:30 | 209 | 208
2018-09-25 10:00 | 192 | 192
2018-09-25 10:30 | 190 | 190
2018-09-25 11:00 | 202 | 202
2018-09-25 11:30 | 218 | 217
2018-09-25 12:00 | 223 | 223
2018-09-25 12:30 | 227 | 226
2018-09-25 13:00 | 221 | 221
2018-09-25 13:30 | 212 | 212
2018-09-25 14:00 | 212 | 212
2018-09-25 14:30 | 219 | 218
2018-09-25 15:00 | 218 | 217
2018-09-25 15:30 | 227 | 227
2018-09-25 16:00 | 235 | 234
2018-09-25 16:30 | 241 | 241
2018-09-25 17:00 | 252 | 252
2018-09-25 17:30 | 260 | 260
2018-09-25 18:00 | 265 | 265
2018-09-25 18:30 | 271 | 270
2018-09-25 19:00 | 272 | 272
2018-09-25 19:30 | 262 | 262
2018-09-25 20:00 | 259 | 256
2018-09-25 20:30 | 256 | 253
2018-09-25 21:00 | 243 | 241
2018-09-25 21:30 | 232 | 230
2018-09-25 22:00 | 222 | 221
2018-09-25 22:30 | 216 | 215
2018-09-25 23:00 | 213 | 212
2018-09-25 23:30 | 200 | 200
2018-09-26 | 183 | 183
2018-09-26 00:30 | 167 | 167
2018-09-26 01:00 | 158 | 158
2018-09-26 01:30 | 154 | 154
2018-09-26 02:00 | 152 | 152
2018-09-26 02:30 | 149 | 149
2018-09-26 03:00 | 145 | 145
2018-09-26 03:30 | 144 | 143
2018-09-26 04:00 | 143 | 143
2018-09-26 04:30 | 148 | 148
2018-09-26 05:00 | 156 | 155
2018-09-26 05:30 | 169 | 169
2018-09-26 06:00 | 178 | 178
2018-09-26 06:30 | 193 | 193
2018-09-26 07:00 | 206 | 205
2018-09-26 07:30 | 206 | 206
2018-09-26 08:00 | 195 | 195
2018-09-26 08:30 | 188 | 188
2018-09-26 09:00 | 187 | 186
2018-09-26 09:30 | 192 | 192
2018-09-26 10:00 | 197 | 197
2018-09-26 10:30 | 197 | 197
2018-09-26 11:00 | 194 | 194
2018-09-26 11:30 | 193 | 193
2018-09-26 12:00 | 187 | 187
2018-09-26 12:30 | 176 | 176
2018-09-26 13:00 | 187 | 187
2018-09-26 13:30 | 181 | 181
2018-09-26 14:00 | 179 | 179
2018-09-26 14:30 | 195 | 195
2018-09-26 15:00 | 203 | 203
2018-09-26 15:30 | 199 | 199
2018-09-26 16:00 | 203 | 203
2018-09-26 16:30 | 218 | 218
2018-09-26 17:00 | 231 | 231
2018-09-26 17:30 | 240 | 240
2018-09-26 18:00 | 247 | 247
2018-09-26 18:30 | 257 | 257
2018-09-26 19:00 | 260 | 260
2018-09-26 19:30 | 251 | 249
2018-09-26 20:00 | 248 | 245
2018-09-26 20:30 | 247 | 246
2018-09-26 21:00 | 235 | 235
2018-09-26 21:30 | 224 | 224
2018-09-26 22:00 | 215 | 215
2018-09-26 22:30 | 211 | 211
2018-09-26 23:00 | 209 | 209
2018-09-26 23:30 | 197 | 197
2018-09-27 | 182 | 181
2018-09-27 00:30 | 167 | 167
2018-09-27 01:00 | 159 | 158
2018-09-27 01:30 | 152 | 151
2018-09-27 02:00 | 149 | 148
2018-09-27 02:30 | 147 | 145
2018-09-27 03:00 | 145 | 144
2018-09-27 03:30 | 145 | 144
2018-09-27 04:00 | 146 | 145
2018-09-27 04:30 | 151 | 150
2018-09-27 05:00 | 158 | 157
2018-09-27 05:30 | 169 | 169
2018-09-27 06:00 | 179 | 179
2018-09-27 06:30 | 193 | 193
2018-09-27 07:00 | 204 | 204
2018-09-27 07:30 | 216 | 216
2018-09-27 08:00 | 218 | 218
2018-09-27 08:30 | 217 | 217
2018-09-27 09:00 | 215 | 214
2018-09-27 09:30 | 215 | 215
2018-09-27 10:00 | 214 | 214
2018-09-27 10:30 | 216 | 216
2018-09-27 11:00 | 223 | 222
2018-09-27 11:30 | 227 | 227
2018-09-27 12:00 | 229 | 229
2018-09-27 12:30 | 228 | 228
2018-09-27 13:00 | 220 | 220
2018-09-27 13:30 | 207 | 207
2018-09-27 14:00 | 203 | 203
2018-09-27 14:30 | 192 | 192
2018-09-27 15:00 | 201 | 201
2018-09-27 15:30 | 209 | 209
2018-09-27 16:00 | 215 | 215
2018-09-27 16:30 | 228 | 228
2018-09-27 17:00 | 240 | 240
2018-09-27 17:30 | 249 | 249
2018-09-27 18:00 | 257 | 257
2018-09-27 18:30 | 269 | 269
2018-09-27 19:00 | 271 | 271
2018-09-27 19:30 | 264 | 264
2018-09-27 20:00 | 260 | 259
2018-09-27 20:30 | 257 | 256
2018-09-27 21:00 | 247 | 245
2018-09-27 21:30 | 234 | 234
2018-09-27 22:00 | 224 | 224
2018-09-27 22:30 | 219 | 218
2018-09-27 23:00 | 214 | 212
2018-09-27 23:30 | 202 | 200
2018-09-28 | 185 | 183
2018-09-28 00:30 | 169 | 168
2018-09-28 01:00 | 159 | 159
2018-09-28 01:30 | 151 | 151
2018-09-28 02:00 | 147 | 147
2018-09-28 02:30 | 145 | 145
2018-09-28 03:00 | 143 | 143
2018-09-28 03:30 | 144 | 144
2018-09-28 04:00 | 144 | 144
2018-09-28 04:30 | 147 | 147
2018-09-28 05:00 | 153 | 153
2018-09-28 05:30 | 165 | 165
2018-09-28 06:00 | 174 | 174
2018-09-28 06:30 | 188 | 188
2018-09-28 07:00 | 197 | 196
2018-09-28 07:30 | 201 | 201
2018-09-28 08:00 | 198 | 198
2018-09-28 08:30 | 198 | 197
2018-09-28 09:00 | 196 | 195
2018-09-28 09:30 | 201 | 200
2018-09-28 10:00 | 201 | 199
2018-09-28 10:30 | 193 | 192
2018-09-28 11:00 | 186 | 184
2018-09-28 11:30 | 181 | 180
2018-09-28 12:00 | 181 | 180
2018-09-28 12:30 | 181 | 180
2018-09-28 13:00 | 181 | 180
2018-09-28 13:30 | 181 | 180
2018-09-28 14:00 | 184 | 183
2018-09-28 14:30 | 190 | 189
2018-09-28 15:00 | 196 | 195
2018-09-28 15:30 | 205 | 204
2018-09-28 16:00 | 216 | 215
2018-09-28 16:30 | 226 | 226
2018-09-28 17:00 | 237 | 237
2018-09-28 17:30 | 241 | 241
2018-09-28 18:00 | 244 | 244
2018-09-28 18:30 | 251 | 251
2018-09-28 19:00 | 254 | 254
2018-09-28 19:30 | 248 | 248
2018-09-28 20:00 | 243 | 243
2018-09-28 20:30 | 240 | 240
2018-09-28 21:00 | 231 | 231
2018-09-28 21:30 | 221 | 221
2018-09-28 22:00 | 214 | 214
2018-09-28 22:30 | 210 | 210
2018-09-28 23:00 | 207 | 207
2018-09-28 23:30 | 196 | 196
2018-09-29 | 182 | 182
2018-09-29 00:30 | 168 | 167
2018-09-29 01:00 | 159 | 158
2018-09-29 01:30 | 152 | 151
2018-09-29 02:00 | 148 | 147
2018-09-29 02:30 | 145 | 144
2018-09-29 03:00 | 142 | 141
2018-09-29 03:30 | 141 | 141
2018-09-29 04:00 | 140 | 140
2018-09-29 04:30 | 140 | 140
2018-09-29 05:00 | 142 | 142
2018-09-29 05:30 | 146 | 145
2018-09-29 06:00 | 147 | 147
2018-09-29 06:30 | 150 | 150
2018-09-29 07:00 | 151 | 151
2018-09-29 07:30 | 152 | 152
2018-09-29 08:00 | 152 | 152
2018-09-29 08:30 | 153 | 153
2018-09-29 09:00 | 152 | 152
2018-09-29 09:30 | 149 | 148
2018-09-29 10:00 | 143 | 143
2018-09-29 10:30 | 139 | 138
2018-09-29 11:00 | 136 | 135
2018-09-29 11:30 | 134 | 133
2018-09-29 12:00 | 133 | 133
2018-09-29 12:30 | 137 | 137
2018-09-29 13:00 | 141 | 140
2018-09-29 13:30 | 144 | 144
2018-09-29 14:00 | 147 | 147
2018-09-29 14:30 | 157 | 157
2018-09-29 15:00 | 187 | 186
2018-09-29 15:30 | 199 | 198
2018-09-29 16:00 | 206 | 206
2018-09-29 16:30 | 208 | 207
2018-09-29 17:00 | 207 | 207
2018-09-29 17:30 | 207 | 207
2018-09-29 18:00 | 211 | 211
2018-09-29 18:30 | 222 | 221
2018-09-29 19:00 | 223 | 222
2018-09-29 19:30 | 215 | 215
2018-09-29 20:00 | 212 | 212
2018-09-29 20:30 | 211 | 210
2018-09-29 21:00 | 203 | 202
2018-09-29 21:30 | 198 | 197
2018-09-29 22:00 | 192 | 192
2018-09-29 22:30 | 191 | 190
2018-09-29 23:00 | 191 | 190
2018-09-29 23:30 | 180 | 180
2018-09-30 | 167 | 167
2018-09-30 00:30 | 154 | 154
2018-09-30 01:00 | 147 | 147
2018-09-30 01:30 | 142 | 142
2018-09-30 02:00 | 137 | 136
2018-09-30 02:30 | 135 | 135
2018-09-30 03:00 | 133 | 133
2018-09-30 03:30 | 132 | 132
2018-09-30 04:00 | 132 | 132
2018-09-30 04:30 | 131 | 131
2018-09-30 05:00 | 130 | 129
2018-09-30 05:30 | 133 | 133
2018-09-30 06:00 | 133 | 133
2018-09-30 06:30 | 137 | 137
2018-09-30 07:00 | 145 | 145
2018-09-30 07:30 | 157 | 156
2018-09-30 08:00 | 166 | 166
2018-09-30 08:30 | 177 | 177
2018-09-30 09:00 | 189 | 189
2018-09-30 09:30 | 193 | 193
2018-09-30 10:00 | 195 | 195
2018-09-30 10:30 | 199 | 199
2018-09-30 11:00 | 201 | 201
2018-09-30 11:30 | 205 | 205
2018-09-30 12:00 | 207 | 207
2018-09-30 12:30 | 204 | 204
2018-09-30 13:00 | 194 | 193
2018-09-30 13:30 | 168 | 168
2018-09-30 14:00 | 149 | 149
2018-09-30 14:30 | 146 | 146
2018-09-30 15:00 | 158 | 158
2018-09-30 15:30 | 161 | 161
2018-09-30 16:00 | 161 | 161
2018-09-30 16:30 | 171 | 171
2018-09-30 17:00 | 188 | 188
2018-09-30 17:30 | 197 | 197
2018-09-30 18:00 | 207 | 207
2018-09-30 18:30 | 221 | 221
2018-09-30 19:00 | 226 | 226
2018-09-30 19:30 | 218 | 218
2018-09-30 20:00 | 214 | 214
2018-09-30 20:30 | 212 | 212
2018-09-30 21:00 | 205 | 205
2018-09-30 21:30 | 198 | 198
2018-09-30 22:00 | 194 | 194
2018-09-30 22:30 | 194 | 194
2018-09-30 23:00 | 194 | 194
2018-09-30 23:30 | 184 | 184
2018-10-01 | 171 | 170
2018-10-01 00:30 | 157 | 156
2018-10-01 01:00 | 147 | 146
2018-10-01 01:30 | 141 | 140
2018-10-01 02:00 | 137 | 135
2018-10-01 02:30 | 135 | 133
2018-10-01 03:00 | 133 | 132
2018-10-01 03:30 | 133 | 132
2018-10-01 04:00 | 133 | 132
2018-10-01 04:30 | 134 | 132
2018-10-01 05:00 | 136 | 135
2018-10-01 05:30 | 140 | 139
2018-10-01 06:00 | 141 | 139
2018-10-01 06:30 | 143 | 142
2018-10-01 07:00 | 140 | 139
2018-10-01 07:30 | 138 | 137
2018-10-01 08:00 | 134 | 133
2018-10-01 08:30 | 130 | 129
2018-10-01 09:00 | 126 | 126
2018-10-01 09:30 | 123 | 123
2018-10-01 10:00 | 122 | 122
2018-10-01 10:30 | 123 | 123
2018-10-01 11:00 | 122 | 122
2018-10-01 11:30 | 118 | 118
2018-10-01 12:00 | 121 | 121
2018-10-01 12:30 | 126 | 126
2018-10-01 13:00 | 129 | 129
2018-10-01 13:30 | 127 | 127
2018-10-01 14:00 | 128 | 128
2018-10-01 14:30 | 130 | 130
2018-10-01 15:00 | 138 | 138
2018-10-01 15:30 | 150 | 150
2018-10-01 16:00 | 164 | 164
2018-10-01 16:30 | 179 | 179
2018-10-01 17:00 | 196 | 196
2018-10-01 17:30 | 209 | 208
2018-10-01 18:00 | 219 | 218
2018-10-01 18:30 | 234 | 233
2018-10-01 19:00 | 237 | 237
2018-10-01 19:30 | 230 | 230
2018-10-01 20:00 | 226 | 226
2018-10-01 20:30 | 223 | 223
2018-10-01 21:00 | 214 | 214
2018-10-01 21:30 | 206 | 206
2018-10-01 22:00 | 199 | 199
2018-10-01 22:30 | 196 | 195
2018-10-01 23:00 | 195 | 195
2018-10-01 23:30 | 185 | 185
2018-10-02 | 172 | 171
2018-10-02 00:30 | 159 | 158
2018-10-02 01:00 | 150 | 149
2018-10-02 01:30 | 144 | 143
2018-10-02 02:00 | 140 | 140
2018-10-02 02:30 | 137 | 136
2018-10-02 03:00 | 136 | 135
2018-10-02 03:30 | 136 | 135
2018-10-02 04:00 | 137 | 136
2018-10-02 04:30 | 141 | 140
2018-10-02 05:00 | 149 | 149
2018-10-02 05:30 | 161 | 161
2018-10-02 06:00 | 172 | 172
2018-10-02 06:30 | 184 | 184
2018-10-02 07:00 | 189 | 189
2018-10-02 07:30 | 193 | 192
2018-10-02 08:00 | 187 | 187
2018-10-02 08:30 | 179 | 178
2018-10-02 09:00 | 173 | 172
2018-10-02 09:30 | 174 | 172
2018-10-02 10:00 | 176 | 175
2018-10-02 10:30 | 174 | 173
2018-10-02 11:00 | 174 | 173
2018-10-02 11:30 | 170 | 169
2018-10-02 12:00 | 169 | 168
2018-10-02 12:30 | 165 | 164
2018-10-02 13:00 | 162 | 161
2018-10-02 13:30 | 161 | 160
2018-10-02 14:00 | 163 | 162
2018-10-02 14:30 | 174 | 173
2018-10-02 15:00 | 181 | 180
2018-10-02 15:30 | 191 | 190
2018-10-02 16:00 | 203 | 202
2018-10-02 16:30 | 218 | 217
2018-10-02 17:00 | 233 | 233
2018-10-02 17:30 | 242 | 242
2018-10-02 18:00 | 249 | 249
2018-10-02 18:30 | 262 | 260
2018-10-02 19:00 | 266 | 264
2018-10-02 19:30 | 258 | 256
2018-10-02 20:00 | 254 | 251
2018-10-02 20:30 | 250 | 248
2018-10-02 21:00 | 240 | 238
2018-10-02 21:30 | 230 | 229
2018-10-02 22:00 | 221 | 220
2018-10-02 22:30 | 217 | 216
2018-10-02 23:00 | 212 | 212
2018-10-02 23:30 | 200 | 200
2018-10-03 | 184 | 184
2018-10-03 00:30 | 169 | 169
2018-10-03 01:00 | 160 | 160
2018-10-03 01:30 | 154 | 154
2018-10-03 02:00 | 150 | 150
2018-10-03 02:30 | 148 | 148
2018-10-03 03:00 | 146 | 146
2018-10-03 03:30 | 147 | 146
2018-10-03 04:00 | 148 | 148
2018-10-03 04:30 | 151 | 151
2018-10-03 05:00 | 159 | 159
2018-10-03 05:30 | 171 | 170
2018-10-03 06:00 | 181 | 180
2018-10-03 06:30 | 193 | 193
2018-10-03 07:00 | 197 | 197
2018-10-03 07:30 | 200 | 199
2018-10-03 08:00 | 193 | 192
2018-10-03 08:30 | 187 | 186
2018-10-03 09:00 | 181 | 180
2018-10-03 09:30 | 178 | 176
2018-10-03 10:00 | 175 | 173
2018-10-03 10:30 | 171 | 169
2018-10-03 11:00 | 168 | 166
2018-10-03 11:30 | 164 | 162
2018-10-03 12:00 | 162 | 160
2018-10-03 12:30 | 164 | 161
2018-10-03 13:00 | 164 | 161
2018-10-03 13:30 | 167 | 164
2018-10-03 14:00 | 173 | 172
2018-10-03 14:30 | 183 | 182
2018-10-03 15:00 | 192 | 192
2018-10-03 15:30 | 203 | 203
2018-10-03 16:00 | 216 | 216
2018-10-03 16:30 | 229 | 229
2018-10-03 17:00 | 245 | 245
2018-10-03 17:30 | 250 | 250
2018-10-03 18:00 | 256 | 256
2018-10-03 18:30 | 267 | 267
2018-10-03 19:00 | 272 | 272
2018-10-03 19:30 | 263 | 263
2018-10-03 20:00 | 258 | 258
2018-10-03 20:30 | 257 | 257
2018-10-03 21:00 | 246 | 246
2018-10-03 21:30 | 234 | 234
2018-10-03 22:00 | 222 | 221
2018-10-03 22:30 | 216 | 215
2018-10-03 23:00 | 212 | 212
2018-10-03 23:30 | 200 | 200
2018-10-04 | 184 | 184
2018-10-04 00:30 | 169 | 169
2018-10-04 01:00 | 160 | 160
2018-10-04 01:30 | 153 | 153
2018-10-04 02:00 | 148 | 148
2018-10-04 02:30 | 146 | 145
2018-10-04 03:00 | 143 | 142
2018-10-04 03:30 | 142 | 142
2018-10-04 04:00 | 141 | 141
2018-10-04 04:30 | 145 | 144
2018-10-04 05:00 | 151 | 151
2018-10-04 05:30 | 162 | 162
2018-10-04 06:00 | 171 | 171
2018-10-04 06:30 | 184 | 184
2018-10-04 07:00 | 188 | 188
2018-10-04 07:30 | 192 | 192
2018-10-04 08:00 | 187 | 187
2018-10-04 08:30 | 179 | 179
2018-10-04 09:00 | 172 | 172
2018-10-04 09:30 | 165 | 165
2018-10-04 10:00 | 159 | 159
2018-10-04 10:30 | 159 | 159
2018-10-04 11:00 | 154 | 154
2018-10-04 11:30 | 154 | 154
2018-10-04 12:00 | 155 | 155
2018-10-04 12:30 | 158 | 158
2018-10-04 13:00 | 160 | 160
2018-10-04 13:30 | 164 | 164
2018-10-04 14:00 | 175 | 175
2018-10-04 14:30 | 183 | 183
2018-10-04 15:00 | 191 | 191
2018-10-04 15:30 | 201 | 201
2018-10-04 16:00 | 213 | 213
2018-10-04 16:30 | 226 | 226
2018-10-04 17:00 | 238 | 238
2018-10-04 17:30 | 249 | 249
2018-10-04 18:00 | 254 | 254
2018-10-04 18:30 | 265 | 265
2018-10-04 19:00 | 267 | 267
2018-10-04 19:30 | 260 | 260
2018-10-04 20:00 | 255 | 255
2018-10-04 20:30 | 250 | 250
2018-10-04 21:00 | 238 | 238
2018-10-04 21:30 | 227 | 227
2018-10-04 22:00 | 219 | 219
2018-10-04 22:30 | 212 | 211
2018-10-04 23:00 | 209 | 209
2018-10-04 23:30 | 197 | 196
2018-10-05 | 181 | 181
2018-10-05 00:30 | 165 | 165
2018-10-05 01:00 | 156 | 156
2018-10-05 01:30 | 150 | 150
2018-10-05 02:00 | 146 | 146
2018-10-05 02:30 | 144 | 143
2018-10-05 03:00 | 141 | 141
2018-10-05 03:30 | 142 | 142
2018-10-05 04:00 | 142 | 142
2018-10-05 04:30 | 144 | 144
2018-10-05 05:00 | 152 | 151
2018-10-05 05:30 | 162 | 162
2018-10-05 06:00 | 169 | 169
2018-10-05 06:30 | 185 | 185
2018-10-05 07:00 | 194 | 194
2018-10-05 07:30 | 200 | 199
2018-10-05 08:00 | 196 | 196
2018-10-05 08:30 | 191 | 191
2018-10-05 09:00 | 189 | 189
2018-10-05 09:30 | 195 | 195
2018-10-05 10:00 | 201 | 201
2018-10-05 10:30 | 210 | 210
2018-10-05 11:00 | 209 | 209
2018-10-05 11:30 | 203 | 203
2018-10-05 12:00 | 201 | 200
2018-10-05 12:30 | 202 | 201
2018-10-05 13:00 | 213 | 213
2018-10-05 13:30 | 221 | 221
2018-10-05 14:00 | 222 | 222
2018-10-05 14:30 | 228 | 227
2018-10-05 15:00 | 232 | 232
2018-10-05 15:30 | 234 | 234
2018-10-05 16:00 | 238 | 238
2018-10-05 16:30 | 238 | 238
2018-10-05 17:00 | 240 | 239
2018-10-05 17:30 | 238 | 237
2018-10-05 18:00 | 239 | 238
2018-10-05 18:30 | 248 | 247
2018-10-05 19:00 | 251 | 251
2018-10-05 19:30 | 246 | 245
2018-10-05 20:00 | 237 | 237
2018-10-05 20:30 | 235 | 235
2018-10-05 21:00 | 226 | 226
2018-10-05 21:30 | 218 | 218
2018-10-05 22:00 | 210 | 210
2018-10-05 22:30 | 208 | 208
2018-10-05 23:00 | 206 | 206
2018-10-05 23:30 | 194 | 194
2018-10-06 | 179 | 178
2018-10-06 00:30 | 165 | 164
2018-10-06 01:00 | 156 | 156
2018-10-06 01:30 | 150 | 150
2018-10-06 02:00 | 144 | 143
2018-10-06 02:30 | 140 | 139
2018-10-06 03:00 | 138 | 137
2018-10-06 03:30 | 138 | 137
2018-10-06 04:00 | 138 | 137
2018-10-06 04:30 | 138 | 137
2018-10-06 05:00 | 140 | 139
2018-10-06 05:30 | 144 | 143
2018-10-06 06:00 | 147 | 145
2018-10-06 06:30 | 155 | 154
2018-10-06 07:00 | 161 | 160
2018-10-06 07:30 | 164 | 164
2018-10-06 08:00 | 165 | 165
2018-10-06 08:30 | 178 | 178
2018-10-06 09:00 | 183 | 183
2018-10-06 09:30 | 187 | 187
2018-10-06 10:00 | 185 | 185
2018-10-06 10:30 | 178 | 178
2018-10-06 11:00 | 179 | 179
2018-10-06 11:30 | 180 | 180
2018-10-06 12:00 | 181 | 181
2018-10-06 12:30 | 188 | 188
2018-10-06 13:00 | 192 | 192
2018-10-06 13:30 | 189 | 189
2018-10-06 14:00 | 182 | 182
2018-10-06 14:30 | 174 | 174
2018-10-06 15:00 | 176 | 176
2018-10-06 15:30 | 182 | 182
2018-10-06 16:00 | 194 | 194
2018-10-06 16:30 | 203 | 203
2018-10-06 17:00 | 214 | 214
2018-10-06 17:30 | 219 | 219
2018-10-06 18:00 | 221 | 221
2018-10-06 18:30 | 230 | 229
2018-10-06 19:00 | 233 | 232
2018-10-06 19:30 | 225 | 225
2018-10-06 20:00 | 221 | 221
2018-10-06 20:30 | 220 | 219
2018-10-06 21:00 | 210 | 209
2018-10-06 21:30 | 202 | 202
2018-10-06 22:00 | 196 | 196
2018-10-06 22:30 | 196 | 196
2018-10-06 23:00 | 196 | 196
2018-10-06 23:30 | 187 | 187
2018-10-07 | 173 | 173
2018-10-07 00:30 | 159 | 159
2018-10-07 01:00 | 150 | 150
2018-10-07 01:30 | 144 | 143
2018-10-07 02:00 | 139 | 138
2018-10-07 02:30 | 136 | 135
2018-10-07 03:00 | 134 | 133
2018-10-07 03:30 | 133 | 132
2018-10-07 04:00 | 132 | 132
2018-10-07 04:30 | 132 | 132
2018-10-07 05:00 | 133 | 133
2018-10-07 05:30 | 135 | 135
2018-10-07 06:00 | 134 | 134
2018-10-07 06:30 | 135 | 134
2018-10-07 07:00 | 133 | 133
2018-10-07 07:30 | 132 | 132
2018-10-07 08:00 | 129 | 129
2018-10-07 08:30 | 129 | 129
2018-10-07 09:00 | 129 | 129
2018-10-07 09:30 | 135 | 135
2018-10-07 10:00 | 138 | 137
2018-10-07 10:30 | 137 | 136
2018-10-07 11:00 | 146 | 146
2018-10-07 11:30 | 150 | 150
2018-10-07 12:00 | 156 | 155
2018-10-07 12:30 | 159 | 158
2018-10-07 13:00 | 151 | 151
2018-10-07 13:30 | 143 | 142
2018-10-07 14:00 | 145 | 145
2018-10-07 14:30 | 152 | 151
2018-10-07 15:00 | 155 | 155
2018-10-07 15:30 | 160 | 160
2018-10-07 16:00 | 171 | 170
2018-10-07 16:30 | 182 | 181
2018-10-07 17:00 | 198 | 196
2018-10-07 17:30 | 209 | 208
2018-10-07 18:00 | 217 | 216
2018-10-07 18:30 | 232 | 231
2018-10-07 19:00 | 237 | 236
2018-10-07 19:30 | 229 | 228
2018-10-07 20:00 | 226 | 226
2018-10-07 20:30 | 224 | 223
2018-10-07 21:00 | 215 | 214
2018-10-07 21:30 | 205 | 204
2018-10-07 22:00 | 198 | 198
2018-10-07 22:30 | 194 | 194
2018-10-07 23:00 | 191 | 191
2018-10-07 23:30 | 182 | 182
2018-10-08 | 168 | 168
2018-10-08 00:30 | 155 | 155
2018-10-08 01:00 | 146 | 146
2018-10-08 01:30 | 141 | 140
2018-10-08 02:00 | 136 | 135
2018-10-08 02:30 | 133 | 132
2018-10-08 03:00 | 131 | 130
2018-10-08 03:30 | 131 | 130
2018-10-08 04:00 | 132 | 131
2018-10-08 04:30 | 137 | 137
2018-10-08 05:00 | 144 | 144
2018-10-08 05:30 | 157 | 157
2018-10-08 06:00 | 169 | 169
2018-10-08 06:30 | 185 | 185
2018-10-08 07:00 | 193 | 192
2018-10-08 07:30 | 200 | 200
2018-10-08 08:00 | 194 | 194
2018-10-08 08:30 | 189 | 188
2018-10-08 09:00 | 189 | 188
2018-10-08 09:30 | 185 | 184
2018-10-08 10:00 | 177 | 175
2018-10-08 10:30 | 170 | 168
2018-10-08 11:00 | 169 | 167
2018-10-08 11:30 | 172 | 169
2018-10-08 12:00 | 174 | 172
2018-10-08 12:30 | 176 | 173
2018-10-08 13:00 | 184 | 181
2018-10-08 13:30 | 199 | 197
2018-10-08 14:00 | 223 | 223
2018-10-08 14:30 | 217 | 217
2018-10-08 15:00 | 198 | 198
2018-10-08 15:30 | 205 | 205
2018-10-08 16:00 | 220 | 220
2018-10-08 16:30 | 234 | 234
2018-10-08 17:00 | 251 | 251
2018-10-08 17:30 | 261 | 261
2018-10-08 18:00 | 264 | 264
2018-10-08 18:30 | 270 | 269
2018-10-08 19:00 | 270 | 270
2018-10-08 19:30 | 260 | 260
2018-10-08 20:00 | 255 | 255
2018-10-08 20:30 | 252 | 252
2018-10-08 21:00 | 240 | 240
2018-10-08 21:30 | 227 | 227
2018-10-08 22:00 | 216 | 216
2018-10-08 22:30 | 210 | 210
2018-10-08 23:00 | 204 | 204
2018-10-08 23:30 | 192 | 192
2018-10-09 | 176 | 176
2018-10-09 00:30 | 162 | 162
2018-10-09 01:00 | 153 | 153
2018-10-09 01:30 | 147 | 147
2018-10-09 02:00 | 144 | 144
2018-10-09 02:30 | 142 | 142
2018-10-09 03:00 | 139 | 139
2018-10-09 03:30 | 140 | 140
2018-10-09 04:00 | 141 | 140
2018-10-09 04:30 | 144 | 144
2018-10-09 05:00 | 151 | 151
2018-10-09 05:30 | 162 | 162
2018-10-09 06:00 | 175 | 175
2018-10-09 06:30 | 190 | 189
2018-10-09 07:00 | 198 | 197
2018-10-09 07:30 | 203 | 202
2018-10-09 08:00 | 200 | 199
2018-10-09 08:30 | 196 | 195
2018-10-09 09:00 | 191 | 191
2018-10-09 09:30 | 195 | 194
2018-10-09 10:00 | 196 | 196
2018-10-09 10:30 | 204 | 203
2018-10-09 11:00 | 202 | 201
2018-10-09 11:30 | 197 | 196
2018-10-09 12:00 | 186 | 184
2018-10-09 12:30 | 178 | 177
2018-10-09 13:00 | 176 | 175
2018-10-09 13:30 | 182 | 181
2018-10-09 14:00 | 195 | 193
2018-10-09 14:30 | 201 | 198
2018-10-09 15:00 | 218 | 214
2018-10-09 15:30 | 235 | 235
2018-10-09 16:00 | 240 | 240
2018-10-09 16:30 | 246 | 246
2018-10-09 17:00 | 255 | 255
2018-10-09 17:30 | 263 | 263
2018-10-09 18:00 | 265 | 265
2018-10-09 18:30 | 268 | 268
2018-10-09 19:00 | 268 | 268
2018-10-09 19:30 | 260 | 260
2018-10-09 20:00 | 256 | 256
2018-10-09 20:30 | 252 | 252
2018-10-09 21:00 | 239 | 237
2018-10-09 21:30 | 226 | 225
2018-10-09 22:00 | 215 | 214
2018-10-09 22:30 | 210 | 209
2018-10-09 23:00 | 206 | 205
2018-10-09 23:30 | 193 | 192
2018-10-10 | 177 | 177
2018-10-10 00:30 | 163 | 163
2018-10-10 01:00 | 153 | 153
2018-10-10 01:30 | 147 | 147
2018-10-10 02:00 | 143 | 142
2018-10-10 02:30 | 141 | 141
2018-10-10 03:00 | 140 | 140
2018-10-10 03:30 | 140 | 140
2018-10-10 04:00 | 141 | 141
2018-10-10 04:30 | 145 | 145
2018-10-10 05:00 | 152 | 152
2018-10-10 05:30 | 162 | 162
2018-10-10 06:00 | 174 | 174
2018-10-10 06:30 | 191 | 191
2018-10-10 07:00 | 202 | 202
2018-10-10 07:30 | 206 | 206
2018-10-10 08:00 | 202 | 202
2018-10-10 08:30 | 194 | 194
2018-10-10 09:00 | 185 | 185
2018-10-10 09:30 | 183 | 180
2018-10-10 10:00 | 179 | 176
2018-10-10 10:30 | 178 | 175
2018-10-10 11:00 | 177 | 174
2018-10-10 11:30 | 173 | 169
2018-10-10 12:00 | 178 | 174
2018-10-10 12:30 | 181 | 176
2018-10-10 13:00 | 186 | 182
2018-10-10 13:30 | 196 | 191
2018-10-10 14:00 | 205 | 203
2018-10-10 14:30 | 215 | 214
2018-10-10 15:00 | 228 | 227
2018-10-10 15:30 | 241 | 241
2018-10-10 16:00 | 256 | 256
2018-10-10 16:30 | 265 | 264
2018-10-10 17:00 | 271 | 270
2018-10-10 17:30 | 273 | 273
2018-10-10 18:00 | 275 | 275
2018-10-10 18:30 | 281 | 281
2018-10-10 19:00 | 283 | 283
2018-10-10 19:30 | 274 | 274
2018-10-10 20:00 | 269 | 269
2018-10-10 20:30 | 264 | 264
2018-10-10 21:00 | 251 | 251
2018-10-10 21:30 | 236 | 236
2018-10-10 22:00 | 222 | 222
2018-10-10 22:30 | 216 | 215
2018-10-10 23:00 | 210 | 210
2018-10-10 23:30 | 196 | 195
2018-10-11 | 180 | 180
2018-10-11 00:30 | 166 | 166
2018-10-11 01:00 | 157 | 157
2018-10-11 01:30 | 152 | 151
2018-10-11 02:00 | 148 | 148
2018-10-11 02:30 | 147 | 147
2018-10-11 03:00 | 147 | 146
2018-10-11 03:30 | 147 | 146
2018-10-11 04:00 | 147 | 147
2018-10-11 04:30 | 150 | 150
2018-10-11 05:00 | 157 | 157
2018-10-11 05:30 | 167 | 167
2018-10-11 06:00 | 175 | 175
2018-10-11 06:30 | 192 | 192
2018-10-11 07:00 | 206 | 205
2018-10-11 07:30 | 215 | 214
2018-10-11 08:00 | 212 | 212
2018-10-11 08:30 | 207 | 207
2018-10-11 09:00 | 197 | 197
2018-10-11 09:30 | 196 | 196
2018-10-11 10:00 | 199 | 199
2018-10-11 10:30 | 213 | 213
2018-10-11 11:00 | 232 | 232
2018-10-11 11:30 | 238 | 237
2018-10-11 12:00 | 242 | 242
2018-10-11 12:30 | 247 | 247
2018-10-11 13:00 | 256 | 256
2018-10-11 13:30 | 252 | 251
2018-10-11 14:00 | 214 | 214
2018-10-11 14:30 | 210 | 210
2018-10-11 15:00 | 228 | 228
2018-10-11 15:30 | 232 | 232
2018-10-11 16:00 | 237 | 237
2018-10-11 16:30 | 245 | 245
2018-10-11 17:00 | 252 | 252
2018-10-11 17:30 | 257 | 257
2018-10-11 18:00 | 260 | 260
2018-10-11 18:30 | 268 | 268
2018-10-11 19:00 | 270 | 270
2018-10-11 19:30 | 265 | 265
2018-10-11 20:00 | 263 | 263
2018-10-11 20:30 | 260 | 259
2018-10-11 21:00 | 246 | 246
2018-10-11 21:30 | 233 | 233
2018-10-11 22:00 | 220 | 219
2018-10-11 22:30 | 214 | 213
2018-10-11 23:00 | 208 | 208
2018-10-11 23:30 | 196 | 195
2018-10-12 | 178 | 178
2018-10-12 00:30 | 164 | 164
2018-10-12 01:00 | 155 | 155
2018-10-12 01:30 | 149 | 148
2018-10-12 02:00 | 145 | 145
2018-10-12 02:30 | 143 | 142
2018-10-12 03:00 | 141 | 140
2018-10-12 03:30 | 141 | 141
2018-10-12 04:00 | 142 | 142
2018-10-12 04:30 | 146 | 145
2018-10-12 05:00 | 152 | 152
2018-10-12 05:30 | 164 | 164
2018-10-12 06:00 | 174 | 174
2018-10-12 06:30 | 192 | 192
2018-10-12 07:00 | 201 | 201
2018-10-12 07:30 | 212 | 212
2018-10-12 08:00 | 216 | 216
2018-10-12 08:30 | 225 | 224
2018-10-12 09:00 | 224 | 223
2018-10-12 09:30 | 218 | 217
2018-10-12 10:00 | 219 | 218
2018-10-12 10:30 | 215 | 213
2018-10-12 11:00 | 213 | 212
2018-10-12 11:30 | 212 | 211
2018-10-12 12:00 | 218 | 216
2018-10-12 12:30 | 228 | 227
2018-10-12 13:00 | 228 | 227
2018-10-12 13:30 | 223 | 223
2018-10-12 14:00 | 231 | 230
2018-10-12 14:30 | 234 | 233
2018-10-12 15:00 | 233 | 232
2018-10-12 15:30 | 231 | 230
2018-10-12 16:00 | 234 | 233
2018-10-12 16:30 | 241 | 241
2018-10-12 17:00 | 251 | 251
2018-10-12 17:30 | 253 | 252
2018-10-12 18:00 | 253 | 252
2018-10-12 18:30 | 256 | 255
2018-10-12 19:00 | 258 | 257
2018-10-12 19:30 | 250 | 250
2018-10-12 20:00 | 247 | 246
2018-10-12 20:30 | 243 | 242
2018-10-12 21:00 | 233 | 232
2018-10-12 21:30 | 224 | 223
2018-10-12 22:00 | 215 | 215
2018-10-12 22:30 | 209 | 209
2018-10-12 23:00 | 206 | 206
2018-10-12 23:30 | 195 | 195
2018-10-13 | 180 | 180
2018-10-13 00:30 | 166 | 166
2018-10-13 01:00 | 155 | 155
2018-10-13 01:30 | 149 | 149
2018-10-13 02:00 | 144 | 143
2018-10-13 02:30 | 142 | 141
2018-10-13 03:00 | 139 | 139
2018-10-13 03:30 | 138 | 137
2018-10-13 04:00 | 138 | 137
2018-10-13 04:30 | 138 | 138
2018-10-13 05:00 | 140 | 139
2018-10-13 05:30 | 143 | 143
2018-10-13 06:00 | 145 | 145
2018-10-13 06:30 | 155 | 155
2018-10-13 07:00 | 165 | 164
2018-10-13 07:30 | 175 | 174
2018-10-13 08:00 | 178 | 177
2018-10-13 08:30 | 190 | 189
2018-10-13 09:00 | 208 | 208
2018-10-13 09:30 | 216 | 215
2018-10-13 10:00 | 215 | 214
2018-10-13 10:30 | 213 | 212
2018-10-13 11:00 | 209 | 209
2018-10-13 11:30 | 205 | 205
2018-10-13 12:00 | 199 | 198
2018-10-13 12:30 | 195 | 195
2018-10-13 13:00 | 194 | 194
2018-10-13 13:30 | 192 | 192
2018-10-13 14:00 | 191 | 191
2018-10-13 14:30 | 193 | 193
2018-10-13 15:00 | 193 | 193
2018-10-13 15:30 | 198 | 198
2018-10-13 16:00 | 203 | 203
2018-10-13 16:30 | 208 | 208
2018-10-13 17:00 | 216 | 216
2018-10-13 17:30 | 221 | 220
2018-10-13 18:00 | 227 | 226
2018-10-13 18:30 | 235 | 234
2018-10-13 19:00 | 237 | 237
2018-10-13 19:30 | 232 | 231
2018-10-13 20:00 | 228 | 228
2018-10-13 20:30 | 224 | 224
2018-10-13 21:00 | 215 | 215
2018-10-13 21:30 | 207 | 207
2018-10-13 22:00 | 202 | 202
2018-10-13 22:30 | 200 | 200
2018-10-13 23:00 | 199 | 199
2018-10-13 23:30 | 190 | 190
2018-10-14 | 176 | 176
2018-10-14 00:30 | 162 | 161
2018-10-14 01:00 | 153 | 152
2018-10-14 01:30 | 146 | 145
2018-10-14 02:00 | 141 | 140
2018-10-14 02:30 | 138 | 137
2018-10-14 03:00 | 136 | 134
2018-10-14 03:30 | 135 | 133
2018-10-14 04:00 | 134 | 132
2018-10-14 04:30 | 134 | 132
2018-10-14 05:00 | 134 | 133
2018-10-14 05:30 | 136 | 135
2018-10-14 06:00 | 135 | 135
2018-10-14 06:30 | 139 | 139
2018-10-14 07:00 | 141 | 141
2018-10-14 07:30 | 147 | 147
2018-10-14 08:00 | 157 | 157
2018-10-14 08:30 | 170 | 170
2018-10-14 09:00 | 181 | 181
2018-10-14 09:30 | 187 | 187
2018-10-14 10:00 | 195 | 194
2018-10-14 10:30 | 196 | 195
2018-10-14 11:00 | 194 | 194
2018-10-14 11:30 | 198 | 197
2018-10-14 12:00 | 202 | 201
2018-10-14 12:30 | 200 | 199
2018-10-14 13:00 | 194 | 193
2018-10-14 13:30 | 192 | 191
2018-10-14 14:00 | 193 | 192
2018-10-14 14:30 | 193 | 192
2018-10-14 15:00 | 194 | 193
2018-10-14 15:30 | 196 | 195
2018-10-14 16:00 | 204 | 203
2018-10-14 16:30 | 216 | 216
2018-10-14 17:00 | 227 | 227
2018-10-14 17:30 | 236 | 236
2018-10-14 18:00 | 243 | 243
2018-10-14 18:30 | 254 | 253
2018-10-14 19:00 | 255 | 255
2018-10-14 19:30 | 248 | 247
2018-10-14 20:00 | 243 | 242
2018-10-14 20:30 | 242 | 241
2018-10-14 21:00 | 232 | 232
2018-10-14 21:30 | 221 | 221
2018-10-14 22:00 | 212 | 212
2018-10-14 22:30 | 208 | 208
2018-10-14 23:00 | 205 | 204
2018-10-14 23:30 | 195 | 195
2018-10-15 | 182 | 182
2018-10-15 00:30 | 170 | 170
2018-10-15 01:00 | 160 | 160
2018-10-15 01:30 | 153 | 153
2018-10-15 02:00 | 148 | 148
2018-10-15 02:30 | 145 | 145
2018-10-15 03:00 | 142 | 142
2018-10-15 03:30 | 143 | 142
2018-10-15 04:00 | 144 | 144
2018-10-15 04:30 | 149 | 149
2018-10-15 05:00 | 157 | 157
2018-10-15 05:30 | 170 | 169
2018-10-15 06:00 | 183 | 182
2018-10-15 06:30 | 206 | 204
2018-10-15 07:00 | 230 | 229
2018-10-15 07:30 | 249 | 249
2018-10-15 08:00 | 254 | 254
2018-10-15 08:30 | 251 | 251
2018-10-15 09:00 | 246 | 245
2018-10-15 09:30 | 244 | 244
2018-10-15 10:00 | 240 | 240
2018-10-15 10:30 | 239 | 238
2018-10-15 11:00 | 239 | 238
2018-10-15 11:30 | 249 | 249
2018-10-15 12:00 | 247 | 246
2018-10-15 12:30 | 237 | 237
2018-10-15 13:00 | 226 | 226
2018-10-15 13:30 | 224 | 224
2018-10-15 14:00 | 227 | 227
2018-10-15 14:30 | 237 | 237
2018-10-15 15:00 | 235 | 234
2018-10-15 15:30 | 235 | 235
2018-10-15 16:00 | 241 | 241
2018-10-15 16:30 | 249 | 249
2018-10-15 17:00 | 260 | 259
2018-10-15 17:30 | 264 | 264
2018-10-15 18:00 | 272 | 272
2018-10-15 18:30 | 283 | 282
2018-10-15 19:00 | 287 | 287
2018-10-15 19:30 | 278 | 278
2018-10-15 20:00 | 273 | 273
2018-10-15 20:30 | 270 | 270
2018-10-15 21:00 | 258 | 258
2018-10-15 21:30 | 244 | 244
2018-10-15 22:00 | 233 | 233
2018-10-15 22:30 | 224 | 224
2018-10-15 23:00 | 220 | 220
2018-10-15 23:30 | 208 | 208
2018-10-16 | 191 | 191
2018-10-16 00:30 | 176 | 176
2018-10-16 01:00 | 168 | 168
2018-10-16 01:30 | 160 | 160
2018-10-16 02:00 | 155 | 155
2018-10-16 02:30 | 153 | 153
2018-10-16 03:00 | 151 | 151
2018-10-16 03:30 | 151 | 151
2018-10-16 04:00 | 151 | 151
2018-10-16 04:30 | 157 | 157
2018-10-16 05:00 | 163 | 163
2018-10-16 05:30 | 174 | 173
2018-10-16 06:00 | 187 | 186
2018-10-16 06:30 | 208 | 206
2018-10-16 07:00 | 221 | 221
2018-10-16 07:30 | 233 | 233
2018-10-16 08:00 | 234 | 233
2018-10-16 08:30 | 227 | 227
2018-10-16 09:00 | 224 | 224
2018-10-16 09:30 | 222 | 221
2018-10-16 10:00 | 217 | 217
2018-10-16 10:30 | 211 | 211
2018-10-16 11:00 | 207 | 206
2018-10-16 11:30 | 205 | 204
2018-10-16 12:00 | 205 | 204
2018-10-16 12:30 | 198 | 198
2018-10-16 13:00 | 195 | 194
2018-10-16 13:30 | 202 | 201
2018-10-16 14:00 | 209 | 208
2018-10-16 14:30 | 215 | 214
2018-10-16 15:00 | 218 | 217
2018-10-16 15:30 | 225 | 224
2018-10-16 16:00 | 240 | 239
2018-10-16 16:30 | 248 | 247
2018-10-16 17:00 | 259 | 258
2018-10-16 17:30 | 265 | 264
2018-10-16 18:00 | 272 | 271
2018-10-16 18:30 | 280 | 279
2018-10-16 19:00 | 283 | 282
2018-10-16 19:30 | 274 | 274
2018-10-16 20:00 | 269 | 269
2018-10-16 20:30 | 266 | 265
2018-10-16 21:00 | 252 | 252
2018-10-16 21:30 | 240 | 240
2018-10-16 22:00 | 230 | 230
2018-10-16 22:30 | 224 | 224
2018-10-16 23:00 | 218 | 218
2018-10-16 23:30 | 204 | 203
2018-10-17 | 188 | 188
2018-10-17 00:30 | 173 | 173
2018-10-17 01:00 | 164 | 164
2018-10-17 01:30 | 158 | 158
2018-10-17 02:00 | 154 | 154
2018-10-17 02:30 | 153 | 152
2018-10-17 03:00 | 151 | 150
2018-10-17 03:30 | 151 | 150
2018-10-17 04:00 | 152 | 151
2018-10-17 04:30 | 155 | 154
2018-10-17 05:00 | 163 | 161
2018-10-17 05:30 | 174 | 172
2018-10-17 06:00 | 185 | 183
2018-10-17 06:30 | 200 | 200
2018-10-17 07:00 | 214 | 213
2018-10-17 07:30 | 223 | 222
2018-10-17 08:00 | 226 | 225
2018-10-17 08:30 | 225 | 223
2018-10-17 09:00 | 223 | 221
2018-10-17 09:30 | 221 | 218
2018-10-17 10:00 | 219 | 218
2018-10-17 10:30 | 218 | 218
2018-10-17 11:00 | 220 | 219
2018-10-17 11:30 | 213 | 213
2018-10-17 12:00 | 211 | 211
2018-10-17 12:30 | 211 | 211
2018-10-17 13:00 | 210 | 210
2018-10-17 13:30 | 208 | 207
2018-10-17 14:00 | 211 | 210
2018-10-17 14:30 | 217 | 217
2018-10-17 15:00 | 221 | 221
2018-10-17 15:30 | 228 | 228
2018-10-17 16:00 | 238 | 238
2018-10-17 16:30 | 246 | 246
2018-10-17 17:00 | 257 | 257
2018-10-17 17:30 | 261 | 260
2018-10-17 18:00 | 263 | 263
2018-10-17 18:30 | 272 | 271
2018-10-17 19:00 | 276 | 276
2018-10-17 19:30 | 268 | 268
2018-10-17 20:00 | 263 | 263
2018-10-17 20:30 | 260 | 259
2018-10-17 21:00 | 247 | 245
2018-10-17 21:30 | 236 | 234
2018-10-17 22:00 | 225 | 224
2018-10-17 22:30 | 219 | 218
2018-10-17 23:00 | 214 | 213
2018-10-17 23:30 | 201 | 201
2018-10-18 | 186 | 186
2018-10-18 00:30 | 171 | 171
2018-10-18 01:00 | 160 | 160
2018-10-18 01:30 | 153 | 153
2018-10-18 02:00 | 148 | 148
2018-10-18 02:30 | 149 | 149
2018-10-18 03:00 | 148 | 148
2018-10-18 03:30 | 150 | 150
2018-10-18 04:00 | 153 | 153
2018-10-18 04:30 | 156 | 156
2018-10-18 05:00 | 162 | 162
2018-10-18 05:30 | 171 | 171
2018-10-18 06:00 | 184 | 183
2018-10-18 06:30 | 202 | 201
2018-10-18 07:00 | 219 | 217
2018-10-18 07:30 | 234 | 233
2018-10-18 08:00 | 233 | 232
2018-10-18 08:30 | 228 | 228
2018-10-18 09:00 | 225 | 225
2018-10-18 09:30 | 223 | 223
2018-10-18 10:00 | 222 | 222
2018-10-18 10:30 | 218 | 218
2018-10-18 11:00 | 216 | 216
2018-10-18 11:30 | 210 | 210
2018-10-18 12:00 | 220 | 220
2018-10-18 12:30 | 227 | 227
2018-10-18 13:00 | 225 | 224
2018-10-18 13:30 | 222 | 222
2018-10-18 14:00 | 231 | 230
2018-10-18 14:30 | 241 | 241
2018-10-18 15:00 | 245 | 245
2018-10-18 15:30 | 243 | 243
2018-10-18 16:00 | 240 | 240
2018-10-18 16:30 | 245 | 245
2018-10-18 17:00 | 254 | 254
2018-10-18 17:30 | 262 | 262
2018-10-18 18:00 | 271 | 271
2018-10-18 18:30 | 276 | 276
2018-10-18 19:00 | 277 | 277
2018-10-18 19:30 | 273 | 273
2018-10-18 20:00 | 266 | 266
2018-10-18 20:30 | 263 | 263
2018-10-18 21:00 | 249 | 248
2018-10-18 21:30 | 236 | 235
2018-10-18 22:00 | 224 | 223
2018-10-18 22:30 | 223 | 222
2018-10-18 23:00 | 218 | 217
2018-10-18 23:30 | 204 | 203
2018-10-19 | 187 | 187
2018-10-19 00:30 | 171 | 171
2018-10-19 01:00 | 161 | 161
2018-10-19 01:30 | 155 | 155
2018-10-19 02:00 | 151 | 151
2018-10-19 02:30 | 149 | 149
2018-10-19 03:00 | 147 | 146
2018-10-19 03:30 | 148 | 147
2018-10-19 04:00 | 147 | 147
2018-10-19 04:30 | 152 | 152
2018-10-19 05:00 | 158 | 158
2018-10-19 05:30 | 168 | 167
2018-10-19 06:00 | 174 | 174
2018-10-19 06:30 | 188 | 188
2018-10-19 07:00 | 199 | 198
2018-10-19 07:30 | 206 | 206
2018-10-19 08:00 | 207 | 207
2018-10-19 08:30 | 204 | 204
2018-10-19 09:00 | 202 | 202
2018-10-19 09:30 | 200 | 200
2018-10-19 10:00 | 198 | 198
2018-10-19 10:30 | 206 | 206
2018-10-19 11:00 | 210 | 210
2018-10-19 11:30 | 216 | 216
2018-10-19 12:00 | 218 | 218
2018-10-19 12:30 | 213 | 213
2018-10-19 13:00 | 214 | 214
2018-10-19 13:30 | 218 | 218
2018-10-19 14:00 | 219 | 218
2018-10-19 14:30 | 209 | 209
2018-10-19 15:00 | 199 | 199
2018-10-19 15:30 | 204 | 204
2018-10-19 16:00 | 218 | 218
2018-10-19 16:30 | 232 | 232
2018-10-19 17:00 | 242 | 242
2018-10-19 17:30 | 243 | 243
2018-10-19 18:00 | 243 | 243
2018-10-19 18:30 | 248 | 248
2018-10-19 19:00 | 256 | 256
2018-10-19 19:30 | 250 | 250
2018-10-19 20:00 | 247 | 247
2018-10-19 20:30 | 242 | 242
2018-10-19 21:00 | 231 | 230
2018-10-19 21:30 | 221 | 220
2018-10-19 22:00 | 213 | 212
2018-10-19 22:30 | 209 | 209
2018-10-19 23:00 | 206 | 206
2018-10-19 23:30 | 194 | 194
2018-10-20 | 178 | 178
2018-10-20 00:30 | 164 | 164
2018-10-20 01:00 | 155 | 155
2018-10-20 01:30 | 149 | 149
2018-10-20 02:00 | 145 | 144
2018-10-20 02:30 | 142 | 142
2018-10-20 03:00 | 141 | 140
2018-10-20 03:30 | 139 | 139
2018-10-20 04:00 | 140 | 139
2018-10-20 04:30 | 140 | 140
2018-10-20 05:00 | 142 | 142
2018-10-20 05:30 | 143 | 142
2018-10-20 06:00 | 145 | 144
2018-10-20 06:30 | 147 | 147
2018-10-20 07:00 | 148 | 148
2018-10-20 07:30 | 151 | 151
2018-10-20 08:00 | 157 | 157
2018-10-20 08:30 | 168 | 168
2018-10-20 09:00 | 168 | 168
2018-10-20 09:30 | 168 | 168
2018-10-20 10:00 | 163 | 163
2018-10-20 10:30 | 160 | 159
2018-10-20 11:00 | 154 | 153
2018-10-20 11:30 | 147 | 147
2018-10-20 12:00 | 144 | 143
2018-10-20 12:30 | 147 | 147
2018-10-20 13:00 | 149 | 149
2018-10-20 13:30 | 147 | 147
2018-10-20 14:00 | 146 | 146
2018-10-20 14:30 | 152 | 151
2018-10-20 15:00 | 160 | 159
2018-10-20 15:30 | 172 | 171
2018-10-20 16:00 | 184 | 184
2018-10-20 16:30 | 198 | 197
2018-10-20 17:00 | 212 | 211
2018-10-20 17:30 | 216 | 215
2018-10-20 18:00 | 221 | 220
2018-10-20 18:30 | 230 | 229
2018-10-20 19:00 | 236 | 235
2018-10-20 19:30 | 231 | 229
2018-10-20 20:00 | 228 | 227
2018-10-20 20:30 | 225 | 224
2018-10-20 21:00 | 214 | 213
2018-10-20 21:30 | 204 | 204
2018-10-20 22:00 | 199 | 199
2018-10-20 22:30 | 197 | 197
2018-10-20 23:00 | 195 | 195
2018-10-20 23:30 | 186 | 186
2018-10-21 | 173 | 173
2018-10-21 00:30 | 159 | 159
2018-10-21 01:00 | 150 | 150
2018-10-21 01:30 | 144 | 144
2018-10-21 02:00 | 139 | 139
2018-10-21 02:30 | 137 | 137
2018-10-21 03:00 | 135 | 135
2018-10-21 03:30 | 135 | 135
2018-10-21 04:00 | 133 | 133
2018-10-21 04:30 | 135 | 135
2018-10-21 05:00 | 136 | 135
2018-10-21 05:30 | 135 | 134
2018-10-21 06:00 | 136 | 136
2018-10-21 06:30 | 138 | 138
2018-10-21 07:00 | 139 | 139
2018-10-21 07:30 | 140 | 140
2018-10-21 08:00 | 152 | 151
2018-10-21 08:30 | 158 | 156
2018-10-21 09:00 | 155 | 153
2018-10-21 09:30 | 145 | 143
2018-10-21 10:00 | 141 | 139
2018-10-21 10:30 | 143 | 139
2018-10-21 11:00 | 145 | 141
2018-10-21 11:30 | 153 | 152
2018-10-21 12:00 | 159 | 157
2018-10-21 12:30 | 164 | 162
2018-10-21 13:00 | 165 | 164
2018-10-21 13:30 | 165 | 163
2018-10-21 14:00 | 199 | 198
2018-10-21 14:30 | 224 | 223
2018-10-21 15:00 | 225 | 224
2018-10-21 15:30 | 224 | 223
2018-10-21 16:00 | 221 | 220
2018-10-21 16:30 | 219 | 219
2018-10-21 17:00 | 221 | 220
2018-10-21 17:30 | 214 | 214
2018-10-21 18:00 | 215 | 214
2018-10-21 18:30 | 226 | 225
2018-10-21 19:00 | 233 | 232
2018-10-21 19:30 | 227 | 226
2018-10-21 20:00 | 224 | 223
2018-10-21 20:30 | 220 | 220
2018-10-21 21:00 | 211 | 210
2018-10-21 21:30 | 202 | 202
2018-10-21 22:00 | 196 | 196
2018-10-21 22:30 | 193 | 193
2018-10-21 23:00 | 191 | 191
2018-10-21 23:30 | 182 | 182
2018-10-22 | 167 | 167
2018-10-22 00:30 | 154 | 154
2018-10-22 01:00 | 145 | 145
2018-10-22 01:30 | 140 | 140
2018-10-22 02:00 | 137 | 137
2018-10-22 02:30 | 135 | 135
2018-10-22 03:00 | 134 | 134
2018-10-22 03:30 | 136 | 136
2018-10-22 04:00 | 136 | 136
2018-10-22 04:30 | 140 | 139
2018-10-22 05:00 | 148 | 147
2018-10-22 05:30 | 157 | 157
2018-10-22 06:00 | 167 | 166
2018-10-22 06:30 | 178 | 177
2018-10-22 07:00 | 185 | 183
2018-10-22 07:30 | 188 | 187
2018-10-22 08:00 | 186 | 185
2018-10-22 08:30 | 185 | 183
2018-10-22 09:00 | 183 | 181
2018-10-22 09:30 | 183 | 181
2018-10-22 10:00 | 183 | 181
2018-10-22 10:30 | 187 | 187
2018-10-22 11:00 | 191 | 189
2018-10-22 11:30 | 193 | 191
2018-10-22 12:00 | 197 | 194
2018-10-22 12:30 | 202 | 199
2018-10-22 13:00 | 204 | 201
2018-10-22 13:30 | 210 | 207
2018-10-22 14:00 | 220 | 220
2018-10-22 14:30 | 224 | 223
2018-10-22 15:00 | 225 | 224
2018-10-22 15:30 | 227 | 227
2018-10-22 16:00 | 233 | 233
2018-10-22 16:30 | 243 | 243
2018-10-22 17:00 | 254 | 254
2018-10-22 17:30 | 259 | 259
2018-10-22 18:00 | 261 | 261
2018-10-22 18:30 | 267 | 267
2018-10-22 19:00 | 274 | 274
2018-10-22 19:30 | 265 | 265
2018-10-22 20:00 | 260 | 260
2018-10-22 20:30 | 256 | 256
2018-10-22 21:00 | 244 | 244
2018-10-22 21:30 | 230 | 230
2018-10-22 22:00 | 218 | 218
2018-10-22 22:30 | 211 | 210
2018-10-22 23:00 | 207 | 207
2018-10-22 23:30 | 196 | 196
2018-10-23 | 180 | 180
2018-10-23 00:30 | 165 | 165
2018-10-23 01:00 | 156 | 156
2018-10-23 01:30 | 151 | 151
2018-10-23 02:00 | 146 | 146
2018-10-23 02:30 | 144 | 144
2018-10-23 03:00 | 142 | 142
2018-10-23 03:30 | 143 | 143
2018-10-23 04:00 | 143 | 143
2018-10-23 04:30 | 147 | 147
2018-10-23 05:00 | 154 | 154
2018-10-23 05:30 | 164 | 164
2018-10-23 06:00 | 173 | 173
2018-10-23 06:30 | 187 | 186
2018-10-23 07:00 | 198 | 196
2018-10-23 07:30 | 204 | 202
2018-10-23 08:00 | 202 | 199
2018-10-23 08:30 | 195 | 193
2018-10-23 09:00 | 190 | 188
2018-10-23 09:30 | 190 | 187
2018-10-23 10:00 | 189 | 186
2018-10-23 10:30 | 188 | 185
2018-10-23 11:00 | 188 | 184
2018-10-23 11:30 | 187 | 187
2018-10-23 12:00 | 190 | 190
2018-10-23 12:30 | 194 | 194
2018-10-23 13:00 | 199 | 198
2018-10-23 13:30 | 205 | 204
2018-10-23 14:00 | 213 | 212
2018-10-23 14:30 | 219 | 218
2018-10-23 15:00 | 224 | 224
2018-10-23 15:30 | 232 | 232
2018-10-23 16:00 | 246 | 245
2018-10-23 16:30 | 257 | 257
2018-10-23 17:00 | 266 | 266
2018-10-23 17:30 | 269 | 269
2018-10-23 18:00 | 269 | 268
2018-10-23 18:30 | 273 | 272
2018-10-23 19:00 | 280 | 278
2018-10-23 19:30 | 270 | 269
2018-10-23 20:00 | 265 | 264
2018-10-23 20:30 | 259 | 258
2018-10-23 21:00 | 245 | 243
2018-10-23 21:30 | 234 | 231
2018-10-23 22:00 | 221 | 219
2018-10-23 22:30 | 215 | 213
2018-10-23 23:00 | 209 | 208
2018-10-23 23:30 | 195 | 195
2018-10-24 | 180 | 180
2018-10-24 00:30 | 165 | 165
2018-10-24 01:00 | 157 | 157
2018-10-24 01:30 | 152 | 152
2018-10-24 02:00 | 148 | 148
2018-10-24 02:30 | 147 | 147
2018-10-24 03:00 | 145 | 145
2018-10-24 03:30 | 145 | 145
2018-10-24 04:00 | 146 | 146
2018-10-24 04:30 | 149 | 149
2018-10-24 05:00 | 155 | 155
2018-10-24 05:30 | 164 | 164
2018-10-24 06:00 | 172 | 172
2018-10-24 06:30 | 187 | 186
2018-10-24 07:00 | 199 | 198
2018-10-24 07:30 | 208 | 208
2018-10-24 08:00 | 206 | 206
2018-10-24 08:30 | 202 | 202
2018-10-24 09:00 | 196 | 196
2018-10-24 09:30 | 192 | 192
2018-10-24 10:00 | 192 | 192
2018-10-24 10:30 | 193 | 192
2018-10-24 11:00 | 195 | 195
2018-10-24 11:30 | 199 | 198
2018-10-24 12:00 | 207 | 205
2018-10-24 12:30 | 213 | 211
2018-10-24 13:00 | 220 | 219
2018-10-24 13:30 | 235 | 233
2018-10-24 14:00 | 248 | 246
2018-10-24 14:30 | 259 | 258
2018-10-24 15:00 | 259 | 258
2018-10-24 15:30 | 264 | 263
2018-10-24 16:00 | 279 | 278
2018-10-24 16:30 | 293 | 292
2018-10-24 17:00 | 297 | 296
2018-10-24 17:30 | 295 | 295
2018-10-24 18:00 | 288 | 288
2018-10-24 18:30 | 291 | 289
2018-10-24 19:00 | 295 | 294
2018-10-24 19:30 | 286 | 286
2018-10-24 20:00 | 281 | 280
2018-10-24 20:30 | 275 | 274
2018-10-24 21:00 | 263 | 262
2018-10-24 21:30 | 249 | 248
2018-10-24 22:00 | 235 | 234
2018-10-24 22:30 | 228 | 225
2018-10-24 23:00 | 221 | 219
2018-10-24 23:30 | 206 | 205
2018-10-25 | 188 | 187
2018-10-25 00:30 | 174 | 173
2018-10-25 01:00 | 165 | 165
2018-10-25 01:30 | 160 | 160
2018-10-25 02:00 | 155 | 155
2018-10-25 02:30 | 153 | 153
2018-10-25 03:00 | 151 | 151
2018-10-25 03:30 | 150 | 150
2018-10-25 04:00 | 151 | 150
2018-10-25 04:30 | 153 | 153
2018-10-25 05:00 | 159 | 158
2018-10-25 05:30 | 167 | 167
2018-10-25 06:00 | 176 | 175
2018-10-25 06:30 | 195 | 193
2018-10-25 07:00 | 211 | 209
2018-10-25 07:30 | 221 | 220
2018-10-25 08:00 | 221 | 220
2018-10-25 08:30 | 220 | 219
2018-10-25 09:00 | 219 | 218
2018-10-25 09:30 | 223 | 221
2018-10-25 10:00 | 225 | 224
2018-10-25 10:30 | 233 | 232
2018-10-25 11:00 | 234 | 233
2018-10-25 11:30 | 221 | 221
2018-10-25 12:00 | 213 | 212
2018-10-25 12:30 | 215 | 214
2018-10-25 13:00 | 218 | 217
2018-10-25 13:30 | 222 | 221
2018-10-25 14:00 | 230 | 229
2018-10-25 14:30 | 237 | 235
2018-10-25 15:00 | 239 | 238
2018-10-25 15:30 | 250 | 248
2018-10-25 16:00 | 261 | 260
2018-10-25 16:30 | 271 | 270
2018-10-25 17:00 | 280 | 280
2018-10-25 17:30 | 282 | 282
2018-10-25 18:00 | 283 | 282
2018-10-25 18:30 | 288 | 288
2018-10-25 19:00 | 294 | 293
2018-10-25 19:30 | 283 | 282
2018-10-25 20:00 | 276 | 276
2018-10-25 20:30 | 269 | 268
2018-10-25 21:00 | 261 | 261
2018-10-25 21:30 | 244 | 244
2018-10-25 22:00 | 231 | 231
2018-10-25 22:30 | 222 | 221
2018-10-25 23:00 | 215 | 214
2018-10-25 23:30 | 201 | 200
2018-10-26 | 185 | 185
2018-10-26 00:30 | 169 | 169
2018-10-26 01:00 | 161 | 161
2018-10-26 01:30 | 156 | 156
2018-10-26 02:00 | 153 | 153
2018-10-26 02:30 | 151 | 151
2018-10-26 03:00 | 150 | 150
2018-10-26 03:30 | 150 | 150
2018-10-26 04:00 | 151 | 151
2018-10-26 04:30 | 154 | 154
2018-10-26 05:00 | 158 | 158
2018-10-26 05:30 | 167 | 167
2018-10-26 06:00 | 176 | 176
2018-10-26 06:30 | 190 | 190
2018-10-26 07:00 | 201 | 201
2018-10-26 07:30 | 209 | 209
2018-10-26 08:00 | 207 | 207
2018-10-26 08:30 | 205 | 205
2018-10-26 09:00 | 208 | 207
2018-10-26 09:30 | 208 | 208
2018-10-26 10:00 | 206 | 206
2018-10-26 10:30 | 208 | 208
2018-10-26 11:00 | 212 | 212
2018-10-26 11:30 | 216 | 216
2018-10-26 12:00 | 225 | 225
2018-10-26 12:30 | 230 | 230
2018-10-26 13:00 | 242 | 242
2018-10-26 13:30 | 251 | 251
2018-10-26 14:00 | 261 | 261
2018-10-26 14:30 | 273 | 273
2018-10-26 15:00 | 285 | 285
2018-10-26 15:30 | 294 | 294
2018-10-26 16:00 | 309 | 309
2018-10-26 16:30 | 319 | 319
2018-10-26 17:00 | 324 | 324
2018-10-26 17:30 | 316 | 316
2018-10-26 18:00 | 301 | 301
2018-10-26 18:30 | 294 | 294
2018-10-26 19:00 | 296 | 296
2018-10-26 19:30 | 286 | 286
2018-10-26 20:00 | 279 | 279
2018-10-26 20:30 | 271 | 271
2018-10-26 21:00 | 254 | 254
2018-10-26 21:30 | 241 | 241
2018-10-26 22:00 | 231 | 231
2018-10-26 22:30 | 226 | 226
2018-10-26 23:00 | 221 | 221
2018-10-26 23:30 | 208 | 208
2018-10-27 | 193 | 192
2018-10-27 00:30 | 179 | 178
2018-10-27 01:00 | 171 | 170
2018-10-27 01:30 | 165 | 165
2018-10-27 02:00 | 159 | 159
2018-10-27 02:30 | 155 | 155
2018-10-27 03:00 | 152 | 152
2018-10-27 03:30 | 151 | 151
2018-10-27 04:00 | 150 | 150
2018-10-27 04:30 | 151 | 151
2018-10-27 05:00 | 151 | 151
2018-10-27 05:30 | 152 | 152
2018-10-27 06:00 | 153 | 153
2018-10-27 06:30 | 155 | 155
2018-10-27 07:00 | 156 | 156
2018-10-27 07:30 | 159 | 159
2018-10-27 08:00 | 161 | 161
2018-10-27 08:30 | 163 | 163
2018-10-27 09:00 | 164 | 164
2018-10-27 09:30 | 163 | 163
2018-10-27 10:00 | 162 | 162
2018-10-27 10:30 | 163 | 163
2018-10-27 11:00 | 162 | 162
2018-10-27 11:30 | 161 | 161
2018-10-27 12:00 | 160 | 160
2018-10-27 12:30 | 163 | 162
2018-10-27 13:00 | 165 | 164
2018-10-27 13:30 | 169 | 169
2018-10-27 14:00 | 173 | 173
2018-10-27 14:30 | 181 | 180
2018-10-27 15:00 | 191 | 191
2018-10-27 15:30 | 201 | 201
2018-10-27 16:00 | 213 | 213
2018-10-27 16:30 | 223 | 223
2018-10-27 17:00 | 233 | 233
2018-10-27 17:30 | 233 | 233
2018-10-27 18:00 | 232 | 232
2018-10-27 18:30 | 238 | 238
2018-10-27 19:00 | 246 | 246
2018-10-27 19:30 | 241 | 240
2018-10-27 20:00 | 236 | 236
2018-10-27 20:30 | 231 | 231
2018-10-27 21:00 | 220 | 219
2018-10-27 21:30 | 212 | 211
2018-10-27 22:00 | 205 | 205
2018-10-27 22:30 | 203 | 203
2018-10-27 23:00 | 202 | 202
2018-10-27 23:30 | 191 | 191
2018-10-28 | 177 | 177
2018-10-28 00:30 | 164 | 164
2018-10-28 01:00 | 156 | 156
2018-10-28 01:30 | 150 | 150
2018-10-28 02:00 | 146 | 145
2018-10-28 02:30 | 144 | 143
2018-10-28 03:00 | 142 | 141
2018-10-28 03:30 | 140 | 140
2018-10-28 04:00 | 140 | 139
2018-10-28 04:30 | 140 | 139
2018-10-28 05:00 | 139 | 139
2018-10-28 05:30 | 138 | 138
2018-10-28 06:00 | 137 | 137
2018-10-28 06:30 | 132 | 132
2018-10-28 07:00 | 139 | 139
2018-10-28 07:30 | 148 | 148
2018-10-28 08:00 | 149 | 149
2018-10-28 08:30 | 162 | 162
2018-10-28 09:00 | 165 | 165
2018-10-28 09:30 | 157 | 156
2018-10-28 10:00 | 190 | 189
2018-10-28 10:30 | 152 | 152
2018-10-28 11:00 | 131 | 131
2018-10-28 11:30 | 132 | 132
2018-10-28 12:00 | 138 | 137
2018-10-28 12:30 | 146 | 145
2018-10-28 13:00 | 152 | 151
2018-10-28 13:30 | 156 | 156
2018-10-28 14:00 | 162 | 162
2018-10-28 14:30 | 177 | 176
2018-10-28 15:00 | 197 | 196
2018-10-28 15:30 | 204 | 203
2018-10-28 16:00 | 209 | 208
2018-10-28 16:30 | 215 | 214
2018-10-28 17:00 | 223 | 222
2018-10-28 17:30 | 226 | 225
2018-10-28 18:00 | 233 | 232
2018-10-28 18:30 | 242 | 240
2018-10-28 19:00 | 245 | 244
2018-10-28 19:30 | 236 | 236
2018-10-28 20:00 | 231 | 230
2018-10-28 20:30 | 226 | 226
2018-10-28 21:00 | 215 | 215
2018-10-28 21:30 | 207 | 207
2018-10-28 22:00 | 198 | 198
2018-10-28 22:30 | 194 | 194
2018-10-28 23:00 | 193 | 192
2018-10-28 23:30 | 182 | 182
2018-10-29 | 169 | 168
2018-10-29 00:30 | 156 | 155
2018-10-29 01:00 | 148 | 148
2018-10-29 01:30 | 143 | 143
2018-10-29 02:00 | 140 | 139
2018-10-29 02:30 | 140 | 139
2018-10-29 03:00 | 139 | 138
2018-10-29 03:30 | 139 | 138
2018-10-29 04:00 | 140 | 139
2018-10-29 04:30 | 144 | 143
2018-10-29 05:00 | 151 | 150
2018-10-29 05:30 | 161 | 161
2018-10-29 06:00 | 175 | 175
2018-10-29 06:30 | 198 | 198
2018-10-29 07:00 | 216 | 216
2018-10-29 07:30 | 231 | 229
2018-10-29 08:00 | 237 | 237
2018-10-29 08:30 | 231 | 230
2018-10-29 09:00 | 228 | 228
2018-10-29 09:30 | 230 | 229
2018-10-29 10:00 | 229 | 228
2018-10-29 10:30 | 225 | 224
2018-10-29 11:00 | 231 | 230
2018-10-29 11:30 | 235 | 233
2018-10-29 12:00 | 241 | 239
2018-10-29 12:30 | 245 | 244
2018-10-29 13:00 | 246 | 245
2018-10-29 13:30 | 245 | 243
2018-10-29 14:00 | 240 | 239
2018-10-29 14:30 | 237 | 236
2018-10-29 15:00 | 237 | 237
2018-10-29 15:30 | 240 | 239
2018-10-29 16:00 | 246 | 245
2018-10-29 16:30 | 250 | 249
2018-10-29 17:00 | 255 | 255
2018-10-29 17:30 | 256 | 256
2018-10-29 18:00 | 256 | 255
2018-10-29 18:30 | 260 | 259
2018-10-29 19:00 | 265 | 264
2018-10-29 19:30 | 257 | 256
2018-10-29 20:00 | 252 | 251
2018-10-29 20:30 | 248 | 247
2018-10-29 21:00 | 237 | 235
2018-10-29 21:30 | 224 | 223
2018-10-29 22:00 | 217 | 216
2018-10-29 22:30 | 211 | 211
2018-10-29 23:00 | 208 | 208
2018-10-29 23:30 | 196 | 196
2018-10-30 | 181 | 181
2018-10-30 00:30 | 166 | 166
2018-10-30 01:00 | 158 | 158
2018-10-30 01:30 | 152 | 152
2018-10-30 02:00 | 148 | 148
2018-10-30 02:30 | 146 | 146
2018-10-30 03:00 | 145 | 145
2018-10-30 03:30 | 146 | 146
2018-10-30 04:00 | 146 | 146
2018-10-30 04:30 | 149 | 149
2018-10-30 05:00 | 154 | 154
2018-10-30 05:30 | 165 | 165
2018-10-30 06:00 | 173 | 173
2018-10-30 06:30 | 187 | 186
2018-10-30 07:00 | 196 | 195
2018-10-30 07:30 | 198 | 197
2018-10-30 08:00 | 194 | 193
2018-10-30 08:30 | 194 | 192
2018-10-30 09:00 | 197 | 196
2018-10-30 09:30 | 202 | 200
2018-10-30 10:00 | 203 | 200
2018-10-30 10:30 | 203 | 200
2018-10-30 11:00 | 199 | 196
2018-10-30 11:30 | 195 | 193
2018-10-30 12:00 | 196 | 194
2018-10-30 12:30 | 198 | 196
2018-10-30 13:00 | 200 | 198
2018-10-30 13:30 | 199 | 196
2018-10-30 14:00 | 198 | 196
2018-10-30 14:30 | 195 | 193
2018-10-30 15:00 | 196 | 193
2018-10-30 15:30 | 204 | 202
2018-10-30 16:00 | 217 | 216
2018-10-30 16:30 | 231 | 229
2018-10-30 17:00 | 245 | 243
2018-10-30 17:30 | 251 | 250
2018-10-30 18:00 | 252 | 251
2018-10-30 18:30 | 258 | 257
2018-10-30 19:00 | 270 | 268
2018-10-30 19:30 | 263 | 261
2018-10-30 20:00 | 257 | 257
2018-10-30 20:30 | 252 | 251
2018-10-30 21:00 | 241 | 240
2018-10-30 21:30 | 230 | 229
2018-10-30 22:00 | 219 | 219
2018-10-30 22:30 | 212 | 212
2018-10-30 23:00 | 208 | 208
2018-10-30 23:30 | 196 | 196
2018-10-31 | 180 | 180
2018-10-31 00:30 | 166 | 166
2018-10-31 01:00 | 158 | 158
2018-10-31 01:30 | 153 | 153
2018-10-31 02:00 | 149 | 149
2018-10-31 02:30 | 147 | 147
2018-10-31 03:00 | 145 | 145
2018-10-31 03:30 | 145 | 145
2018-10-31 04:00 | 146 | 146
2018-10-31 04:30 | 150 | 150
2018-10-31 05:00 | 156 | 156
2018-10-31 05:30 | 166 | 166
2018-10-31 06:00 | 175 | 175
2018-10-31 06:30 | 190 | 189
2018-10-31 07:00 | 201 | 199
2018-10-31 07:30 | 201 | 200
2018-10-31 08:00 | 196 | 194
2018-10-31 08:30 | 190 | 188
2018-10-31 09:00 | 188 | 186
2018-10-31 09:30 | 192 | 190
2018-10-31 10:00 | 186 | 186
2018-10-31 10:30 | 177 | 176
2018-10-31 11:00 | 173 | 173
2018-10-31 11:30 | 175 | 174
2018-10-31 12:00 | 177 | 177
2018-10-31 12:30 | 181 | 180
2018-10-31 13:00 | 187 | 186
2018-10-31 13:30 | 192 | 191
2018-10-31 14:00 | 200 | 198
2018-10-31 14:30 | 210 | 210
2018-10-31 15:00 | 219 | 218
2018-10-31 15:30 | 231 | 230
2018-10-31 16:00 | 247 | 246
2018-10-31 16:30 | 259 | 258
2018-10-31 17:00 | 269 | 268
2018-10-31 17:30 | 270 | 269
2018-10-31 18:00 | 264 | 264
2018-10-31 18:30 | 265 | 265
2018-10-31 19:00 | 275 | 274
2018-10-31 19:30 | 269 | 268
2018-10-31 20:00 | 265 | 265
2018-10-31 20:30 | 261 | 261
2018-10-31 21:00 | 249 | 249
2018-10-31 21:30 | 237 | 237
2018-10-31 22:00 | 227 | 227
2018-10-31 22:30 | 218 | 218
2018-10-31 23:00 | 212 | 212
2018-10-31 23:30 | 200 | 200
2018-11-01 | 184 | 184
2018-11-01 00:30 | 169 | 169
2018-11-01 01:00 | 159 | 159
2018-11-01 01:30 | 153 | 153
2018-11-01 02:00 | 148 | 148
2018-11-01 02:30 | 145 | 145
2018-11-01 03:00 | 144 | 144
2018-11-01 03:30 | 144 | 144
2018-11-01 04:00 | 147 | 147
2018-11-01 04:30 | 152 | 152
2018-11-01 05:00 | 157 | 157
2018-11-01 05:30 | 166 | 166
2018-11-01 06:00 | 175 | 175
2018-11-01 06:30 | 189 | 188
2018-11-01 07:00 | 199 | 197
2018-11-01 07:30 | 204 | 204
2018-11-01 08:00 | 202 | 202
2018-11-01 08:30 | 203 | 203
2018-11-01 09:00 | 199 | 199
2018-11-01 09:30 | 197 | 196
2018-11-01 10:00 | 195 | 194
2018-11-01 10:30 | 189 | 189
2018-11-01 11:00 | 186 | 186
2018-11-01 11:30 | 185 | 185
2018-11-01 12:00 | 187 | 187
2018-11-01 12:30 | 190 | 189
2018-11-01 13:00 | 193 | 193
2018-11-01 13:30 | 198 | 198
2018-11-01 14:00 | 206 | 206
2018-11-01 14:30 | 216 | 215
2018-11-01 15:00 | 224 | 223
2018-11-01 15:30 | 233 | 232
2018-11-01 16:00 | 247 | 246
2018-11-01 16:30 | 260 | 259
2018-11-01 17:00 | 271 | 270
2018-11-01 17:30 | 274 | 273
2018-11-01 18:00 | 273 | 273
2018-11-01 18:30 | 276 | 276
2018-11-01 19:00 | 287 | 286
2018-11-01 19:30 | 280 | 279
2018-11-01 20:00 | 273 | 273
2018-11-01 20:30 | 267 | 267
2018-11-01 21:00 | 255 | 255
2018-11-01 21:30 | 241 | 241
2018-11-01 22:00 | 229 | 229
2018-11-01 22:30 | 223 | 222
2018-11-01 23:00 | 218 | 217
2018-11-01 23:30 | 202 | 202
2018-11-02 | 185 | 185
2018-11-02 00:30 | 170 | 170
2018-11-02 01:00 | 161 | 161
2018-11-02 01:30 | 156 | 156
2018-11-02 02:00 | 152 | 152
2018-11-02 02:30 | 151 | 151
2018-11-02 03:00 | 150 | 150
2018-11-02 03:30 | 151 | 150
2018-11-02 04:00 | 151 | 151
2018-11-02 04:30 | 154 | 154
2018-11-02 05:00 | 160 | 160
2018-11-02 05:30 | 169 | 168
2018-11-02 06:00 | 177 | 176
2018-11-02 06:30 | 194 | 192
2018-11-02 07:00 | 204 | 203
2018-11-02 07:30 | 210 | 209
2018-11-02 08:00 | 212 | 211
2018-11-02 08:30 | 211 | 210
2018-11-02 09:00 | 202 | 201
2018-11-02 09:30 | 198 | 197
2018-11-02 10:00 | 194 | 192
2018-11-02 10:30 | 184 | 183
2018-11-02 11:00 | 178 | 176
2018-11-02 11:30 | 176 | 174
2018-11-02 12:00 | 179 | 176
2018-11-02 12:30 | 181 | 179
2018-11-02 13:00 | 183 | 181
2018-11-02 13:30 | 192 | 189
2018-11-02 14:00 | 200 | 197
2018-11-02 14:30 | 208 | 205
2018-11-02 15:00 | 215 | 212
2018-11-02 15:30 | 225 | 222
2018-11-02 16:00 | 241 | 238
2018-11-02 16:30 | 254 | 251
2018-11-02 17:00 | 264 | 263
2018-11-02 17:30 | 263 | 263
2018-11-02 18:00 | 257 | 257
2018-11-02 18:30 | 258 | 257
2018-11-02 19:00 | 267 | 265
2018-11-02 19:30 | 259 | 258
2018-11-02 20:00 | 253 | 252
2018-11-02 20:30 | 249 | 249
2018-11-02 21:00 | 238 | 237
2018-11-02 21:30 | 227 | 227
2018-11-02 22:00 | 218 | 218
2018-11-02 22:30 | 214 | 212
2018-11-02 23:00 | 211 | 209
2018-11-02 23:30 | 197 | 196
2018-11-03 | 180 | 180
2018-11-03 00:30 | 166 | 166
2018-11-03 01:00 | 158 | 157
2018-11-03 01:30 | 153 | 153
2018-11-03 02:00 | 148 | 148
2018-11-03 02:30 | 144 | 144
2018-11-03 03:00 | 145 | 145
2018-11-03 03:30 | 144 | 144
2018-11-03 04:00 | 145 | 145
2018-11-03 04:30 | 145 | 145
2018-11-03 05:00 | 146 | 146
2018-11-03 05:30 | 147 | 147
2018-11-03 06:00 | 146 | 146
2018-11-03 06:30 | 147 | 147
2018-11-03 07:00 | 146 | 146
2018-11-03 07:30 | 148 | 147
2018-11-03 08:00 | 149 | 149
2018-11-03 08:30 | 151 | 150
2018-11-03 09:00 | 150 | 148
2018-11-03 09:30 | 149 | 147
2018-11-03 10:00 | 148 | 146
2018-11-03 10:30 | 146 | 143
2018-11-03 11:00 | 146 | 143
2018-11-03 11:30 | 146 | 143
2018-11-03 12:00 | 150 | 147
2018-11-03 12:30 | 155 | 152
2018-11-03 13:00 | 159 | 156
2018-11-03 13:30 | 166 | 165
2018-11-03 14:00 | 177 | 175
2018-11-03 14:30 | 190 | 188
2018-11-03 15:00 | 202 | 201
2018-11-03 15:30 | 214 | 212
2018-11-03 16:00 | 223 | 223
2018-11-03 16:30 | 233 | 233
2018-11-03 17:00 | 242 | 242
2018-11-03 17:30 | 242 | 241
2018-11-03 18:00 | 237 | 237
2018-11-03 18:30 | 243 | 243
2018-11-03 19:00 | 254 | 254
2018-11-03 19:30 | 250 | 249
2018-11-03 20:00 | 245 | 244
2018-11-03 20:30 | 239 | 239
2018-11-03 21:00 | 226 | 226
2018-11-03 21:30 | 217 | 217
2018-11-03 22:00 | 210 | 210
2018-11-03 22:30 | 208 | 207
2018-11-03 23:00 | 203 | 203
2018-11-03 23:30 | 193 | 193
2018-11-04 | 178 | 178
2018-11-04 00:30 | 165 | 165
2018-11-04 01:00 | 156 | 156
2018-11-04 01:30 | 151 | 150
2018-11-04 02:00 | 145 | 145
2018-11-04 02:30 | 143 | 143
2018-11-04 03:00 | 141 | 141
2018-11-04 03:30 | 139 | 139
2018-11-04 04:00 | 138 | 138
2018-11-04 04:30 | 138 | 138
2018-11-04 05:00 | 137 | 137
2018-11-04 05:30 | 137 | 137
2018-11-04 06:00 | 135 | 135
2018-11-04 06:30 | 135 | 135
2018-11-04 07:00 | 133 | 133
2018-11-04 07:30 | 135 | 135
2018-11-04 08:00 | 135 | 135
2018-11-04 08:30 | 140 | 140
2018-11-04 09:00 | 145 | 144
2018-11-04 09:30 | 149 | 148
2018-11-04 10:00 | 154 | 152
2018-11-04 10:30 | 160 | 159
2018-11-04 11:00 | 167 | 165
2018-11-04 11:30 | 175 | 173
2018-11-04 12:00 | 182 | 179
2018-11-04 12:30 | 189 | 186
2018-11-04 13:00 | 201 | 197
2018-11-04 13:30 | 207 | 205
2018-11-04 14:00 | 217 | 217
2018-11-04 14:30 | 229 | 229
2018-11-04 15:00 | 239 | 239
2018-11-04 15:30 | 252 | 252
2018-11-04 16:00 | 265 | 265
2018-11-04 16:30 | 277 | 277
2018-11-04 17:00 | 278 | 278
2018-11-04 17:30 | 280 | 279
2018-11-04 18:00 | 279 | 278
2018-11-04 18:30 | 282 | 281
2018-11-04 19:00 | 290 | 289
2018-11-04 19:30 | 282 | 282
2018-11-04 20:00 | 276 | 275
2018-11-04 20:30 | 270 | 269
2018-11-04 21:00 | 254 | 254
2018-11-04 21:30 | 240 | 240
2018-11-04 22:00 | 230 | 230
2018-11-04 22:30 | 221 | 221
2018-11-04 23:00 | 213 | 213
2018-11-04 23:30 | 202 | 201
2018-11-05 | 185 | 185
2018-11-05 00:30 | 171 | 171
2018-11-05 01:00 | 163 | 163
2018-11-05 01:30 | 158 | 158
2018-11-05 02:00 | 154 | 153
2018-11-05 02:30 | 152 | 151
2018-11-05 03:00 | 150 | 149
2018-11-05 03:30 | 149 | 149
2018-11-05 04:00 | 150 | 150
2018-11-05 04:30 | 155 | 155
2018-11-05 05:00 | 160 | 160
2018-11-05 05:30 | 171 | 171
2018-11-05 06:00 | 183 | 183
2018-11-05 06:30 | 204 | 203
2018-11-05 07:00 | 221 | 220
2018-11-05 07:30 | 236 | 234
2018-11-05 08:00 | 241 | 241
2018-11-05 08:30 | 242 | 241
2018-11-05 09:00 | 235 | 234
2018-11-05 09:30 | 235 | 235
2018-11-05 10:00 | 238 | 237
2018-11-05 10:30 | 244 | 244
2018-11-05 11:00 | 248 | 247
2018-11-05 11:30 | 254 | 254
2018-11-05 12:00 | 263 | 262
2018-11-05 12:30 | 272 | 271
2018-11-05 13:00 | 281 | 280
2018-11-05 13:30 | 292 | 291
2018-11-05 14:00 | 301 | 300
2018-11-05 14:30 | 313 | 313
2018-11-05 15:00 | 322 | 322
2018-11-05 15:30 | 329 | 329
2018-11-05 16:00 | 344 | 343
2018-11-05 16:30 | 357 | 357
2018-11-05 17:00 | 366 | 366
2018-11-05 17:30 | 361 | 361
2018-11-05 18:00 | 349 | 349
2018-11-05 18:30 | 344 | 344
2018-11-05 19:00 | 351 | 351
2018-11-05 19:30 | 340 | 339
2018-11-05 20:00 | 330 | 329
2018-11-05 20:30 | 318 | 317
2018-11-05 21:00 | 300 | 299
2018-11-05 21:30 | 280 | 280
2018-11-05 22:00 | 265 | 265
2018-11-05 22:30 | 255 | 254
2018-11-05 23:00 | 243 | 243
2018-11-05 23:30 | 225 | 225
2018-11-06 | 208 | 208
2018-11-06 00:30 | 191 | 191
2018-11-06 01:00 | 182 | 182
2018-11-06 01:30 | 177 | 177
2018-11-06 02:00 | 173 | 173
2018-11-06 02:30 | 170 | 170
2018-11-06 03:00 | 168 | 168
2018-11-06 03:30 | 168 | 168
2018-11-06 04:00 | 168 | 168
2018-11-06 04:30 | 172 | 172
2018-11-06 05:00 | 177 | 177
2018-11-06 05:30 | 190 | 189
2018-11-06 06:00 | 202 | 202
2018-11-06 06:30 | 225 | 223
2018-11-06 07:00 | 245 | 244
2018-11-06 07:30 | 263 | 262
2018-11-06 08:00 | 267 | 267
2018-11-06 08:30 | 265 | 265
2018-11-06 09:00 | 257 | 257
2018-11-06 09:30 | 262 | 262
2018-11-06 10:00 | 263 | 262
2018-11-06 10:30 | 272 | 270
2018-11-06 11:00 | 278 | 276
2018-11-06 11:30 | 284 | 283
2018-11-06 12:00 | 294 | 292
2018-11-06 12:30 | 310 | 309
2018-11-06 13:00 | 311 | 310
2018-11-06 13:30 | 315 | 314
2018-11-06 14:00 | 332 | 330
2018-11-06 14:30 | 336 | 335
2018-11-06 15:00 | 344 | 343
2018-11-06 15:30 | 360 | 358
2018-11-06 16:00 | 373 | 370
2018-11-06 16:30 | 362 | 360
2018-11-06 17:00 | 359 | 357
2018-11-06 17:30 | 355 | 353
2018-11-06 18:00 | 347 | 346
2018-11-06 18:30 | 339 | 338
2018-11-06 19:00 | 338 | 337
2018-11-06 19:30 | 324 | 323
2018-11-06 20:00 | 309 | 308
2018-11-06 20:30 | 314 | 313
2018-11-06 21:00 | 308 | 308
2018-11-06 21:30 | 285 | 285
2018-11-06 22:00 | 281 | 281
2018-11-06 22:30 | 257 | 256
2018-11-06 23:00 | 242 | 242
2018-11-06 23:30 | 230 | 230
2018-11-07 | 218 | 218
2018-11-07 00:30 | 209 | 209
2018-11-07 01:00 | 204 | 204
2018-11-07 01:30 | 191 | 190
2018-11-07 02:00 | 181 | 180
2018-11-07 02:30 | 175 | 175
2018-11-07 03:00 | 172 | 172
2018-11-07 03:30 | 171 | 171
2018-11-07 04:00 | 171 | 171
2018-11-07 04:30 | 173 | 173
2018-11-07 05:00 | 177 | 177
2018-11-07 05:30 | 188 | 188
2018-11-07 06:00 | 199 | 198
2018-11-07 06:30 | 219 | 218
2018-11-07 07:00 | 238 | 238
2018-11-07 07:30 | 249 | 249
2018-11-07 08:00 | 253 | 253
2018-11-07 08:30 | 254 | 252
2018-11-07 09:00 | 253 | 251
2018-11-07 09:30 | 254 | 253
2018-11-07 10:00 | 255 | 253
2018-11-07 10:30 | 261 | 260
2018-11-07 11:00 | 262 | 261
2018-11-07 11:30 | 266 | 266
2018-11-07 12:00 | 274 | 273
2018-11-07 12:30 | 281 | 280
2018-11-07 13:00 | 288 | 287
2018-11-07 13:30 | 297 | 296
2018-11-07 14:00 | 317 | 316
2018-11-07 14:30 | 321 | 321
2018-11-07 15:00 | 319 | 319
2018-11-07 15:30 | 332 | 332
2018-11-07 16:00 | 348 | 348
2018-11-07 16:30 | 357 | 357
2018-11-07 17:00 | 365 | 365
2018-11-07 17:30 | 361 | 361
2018-11-07 18:00 | 351 | 351
2018-11-07 18:30 | 343 | 343
2018-11-07 19:00 | 349 | 348
2018-11-07 19:30 | 334 | 333
2018-11-07 20:00 | 327 | 326
2018-11-07 20:30 | 319 | 316
2018-11-07 21:00 | 299 | 297
2018-11-07 21:30 | 283 | 281
2018-11-07 22:00 | 272 | 267
2018-11-07 22:30 | 262 | 257
2018-11-07 23:00 | 253 | 248
2018-11-07 23:30 | 231 | 227
2018-11-08 | 211 | 208
2018-11-08 00:30 | 194 | 190
2018-11-08 01:00 | 183 | 181
2018-11-08 01:30 | 179 | 177
2018-11-08 02:00 | 174 | 171
2018-11-08 02:30 | 172 | 169
2018-11-08 03:00 | 171 | 168
2018-11-08 03:30 | 171 | 168
2018-11-08 04:00 | 172 | 169
2018-11-08 04:30 | 175 | 172
2018-11-08 05:00 | 180 | 179
2018-11-08 05:30 | 188 | 187
2018-11-08 06:00 | 201 | 200
2018-11-08 06:30 | 225 | 224
2018-11-08 07:00 | 247 | 246
2018-11-08 07:30 | 264 | 264
2018-11-08 08:00 | 272 | 271
2018-11-08 08:30 | 274 | 273
2018-11-08 09:00 | 265 | 264
2018-11-08 09:30 | 272 | 271
2018-11-08 10:00 | 269 | 269
2018-11-08 10:30 | 265 | 265
2018-11-08 11:00 | 259 | 259
2018-11-08 11:30 | 253 | 253
2018-11-08 12:00 | 236 | 236
2018-11-08 12:30 | 225 | 225
2018-11-08 13:00 | 209 | 209
2018-11-08 13:30 | 217 | 217
2018-11-08 14:00 | 218 | 218
2018-11-08 14:30 | 210 | 210
2018-11-08 15:00 | 194 | 194
2018-11-08 15:30 | 207 | 207
2018-11-08 16:00 | 226 | 226
2018-11-08 16:30 | 239 | 239
2018-11-08 17:00 | 249 | 249
2018-11-08 17:30 | 254 | 254
2018-11-08 18:00 | 257 | 257
2018-11-08 18:30 | 260 | 260
2018-11-08 19:00 | 272 | 272
2018-11-08 19:30 | 267 | 267
2018-11-08 20:00 | 262 | 262
2018-11-08 20:30 | 258 | 258
2018-11-08 21:00 | 247 | 247
2018-11-08 21:30 | 232 | 232
2018-11-08 22:00 | 222 | 221
2018-11-08 22:30 | 215 | 215
2018-11-08 23:00 | 210 | 210
2018-11-08 23:30 | 197 | 197
2018-11-09 | 181 | 181
2018-11-09 00:30 | 167 | 167
2018-11-09 01:00 | 159 | 159
2018-11-09 01:30 | 154 | 154
2018-11-09 02:00 | 149 | 149
2018-11-09 02:30 | 148 | 148
2018-11-09 03:00 | 146 | 146
2018-11-09 03:30 | 146 | 146
2018-11-09 04:00 | 146 | 146
2018-11-09 04:30 | 151 | 151
2018-11-09 05:00 | 155 | 155
2018-11-09 05:30 | 164 | 164
2018-11-09 06:00 | 173 | 173
2018-11-09 06:30 | 186 | 186
2018-11-09 07:00 | 194 | 193
2018-11-09 07:30 | 199 | 198
2018-11-09 08:00 | 195 | 193
2018-11-09 08:30 | 187 | 185
2018-11-09 09:00 | 182 | 180
2018-11-09 09:30 | 183 | 181
2018-11-09 10:00 | 185 | 182
2018-11-09 10:30 | 193 | 191
2018-11-09 11:00 | 201 | 198
2018-11-09 11:30 | 198 | 195
2018-11-09 12:00 | 193 | 190
2018-11-09 12:30 | 190 | 187
2018-11-09 13:00 | 189 | 186
2018-11-09 13:30 | 186 | 184
2018-11-09 14:00 | 196 | 193
2018-11-09 14:30 | 192 | 190
2018-11-09 15:00 | 190 | 188
2018-11-09 15:30 | 199 | 198
2018-11-09 16:00 | 211 | 209
2018-11-09 16:30 | 221 | 219
2018-11-09 17:00 | 228 | 227
2018-11-09 17:30 | 234 | 232
2018-11-09 18:00 | 235 | 234
2018-11-09 18:30 | 238 | 237
2018-11-09 19:00 | 249 | 247
2018-11-09 19:30 | 245 | 244
2018-11-09 20:00 | 242 | 241
2018-11-09 20:30 | 239 | 237
2018-11-09 21:00 | 229 | 228
2018-11-09 21:30 | 218 | 218
2018-11-09 22:00 | 210 | 210
2018-11-09 22:30 | 206 | 206
2018-11-09 23:00 | 203 | 203
2018-11-09 23:30 | 192 | 192
2018-11-10 | 176 | 176
2018-11-10 00:30 | 163 | 163
2018-11-10 01:00 | 155 | 155
2018-11-10 01:30 | 150 | 150
2018-11-10 02:00 | 145 | 145
2018-11-10 02:30 | 144 | 143
2018-11-10 03:00 | 142 | 141
2018-11-10 03:30 | 141 | 140
2018-11-10 04:00 | 140 | 139
2018-11-10 04:30 | 140 | 139
2018-11-10 05:00 | 139 | 138
2018-11-10 05:30 | 141 | 139
2018-11-10 06:00 | 141 | 139
2018-11-10 06:30 | 141 | 140
2018-11-10 07:00 | 139 | 139
2018-11-10 07:30 | 139 | 139
2018-11-10 08:00 | 138 | 137
2018-11-10 08:30 | 139 | 139
2018-11-10 09:00 | 149 | 149
2018-11-10 09:30 | 153 | 153
2018-11-10 10:00 | 156 | 155
2018-11-10 10:30 | 152 | 151
2018-11-10 11:00 | 148 | 147
2018-11-10 11:30 | 143 | 142
2018-11-10 12:00 | 141 | 141
2018-11-10 12:30 | 143 | 142
2018-11-10 13:00 | 152 | 151
2018-11-10 13:30 | 155 | 155
2018-11-10 14:00 | 158 | 158
2018-11-10 14:30 | 154 | 154
2018-11-10 15:00 | 161 | 161
2018-11-10 15:30 | 166 | 166
2018-11-10 16:00 | 180 | 180
2018-11-10 16:30 | 193 | 193
2018-11-10 17:00 | 204 | 204
2018-11-10 17:30 | 209 | 209
2018-11-10 18:00 | 212 | 211
2018-11-10 18:30 | 218 | 218
2018-11-10 19:00 | 231 | 230
2018-11-10 19:30 | 228 | 227
2018-11-10 20:00 | 224 | 223
2018-11-10 20:30 | 221 | 220
2018-11-10 21:00 | 211 | 210
2018-11-10 21:30 | 203 | 203
2018-11-10 22:00 | 198 | 198
2018-11-10 22:30 | 196 | 196
2018-11-10 23:00 | 193 | 193
2018-11-10 23:30 | 184 | 184
2018-11-11 | 170 | 170
2018-11-11 00:30 | 157 | 157
2018-11-11 01:00 | 150 | 149
2018-11-11 01:30 | 145 | 144
2018-11-11 02:00 | 141 | 140
2018-11-11 02:30 | 139 | 138
2018-11-11 03:00 | 137 | 136
2018-11-11 03:30 | 135 | 134
2018-11-11 04:00 | 135 | 134
2018-11-11 04:30 | 135 | 134
2018-11-11 05:00 | 135 | 133
2018-11-11 05:30 | 136 | 134
2018-11-11 06:00 | 134 | 132
2018-11-11 06:30 | 132 | 130
2018-11-11 07:00 | 130 | 128
2018-11-11 07:30 | 131 | 129
2018-11-11 08:00 | 131 | 131
2018-11-11 08:30 | 134 | 134
2018-11-11 09:00 | 130 | 130
2018-11-11 09:30 | 129 | 129
2018-11-11 10:00 | 130 | 130
2018-11-11 10:30 | 134 | 134
2018-11-11 11:00 | 137 | 137
2018-11-11 11:30 | 135 | 135
2018-11-11 12:00 | 128 | 128
2018-11-11 12:30 | 127 | 127
2018-11-11 13:00 | 130 | 130
2018-11-11 13:30 | 134 | 134
2018-11-11 14:00 | 141 | 141
2018-11-11 14:30 | 150 | 150
2018-11-11 15:00 | 162 | 161
2018-11-11 15:30 | 172 | 171
2018-11-11 16:00 | 185 | 185
2018-11-11 16:30 | 199 | 198
2018-11-11 17:00 | 214 | 213
2018-11-11 17:30 | 221 | 220
2018-11-11 18:00 | 226 | 225
2018-11-11 18:30 | 233 | 232
2018-11-11 19:00 | 245 | 244
2018-11-11 19:30 | 241 | 241
2018-11-11 20:00 | 237 | 237
2018-11-11 20:30 | 233 | 233
2018-11-11 21:00 | 219 | 219
2018-11-11 21:30 | 209 | 209
2018-11-11 22:00 | 200 | 200
2018-11-11 22:30 | 196 | 196
2018-11-11 23:00 | 193 | 193
2018-11-11 23:30 | 182 | 182
2018-11-12 | 168 | 168
2018-11-12 00:30 | 156 | 156
2018-11-12 01:00 | 149 | 149
2018-11-12 01:30 | 145 | 144
2018-11-12 02:00 | 141 | 141
2018-11-12 02:30 | 140 | 139
2018-11-12 03:00 | 140 | 139
2018-11-12 03:30 | 140 | 139
2018-11-12 04:00 | 141 | 140
2018-11-12 04:30 | 145 | 144
2018-11-12 05:00 | 150 | 149
2018-11-12 05:30 | 160 | 159
2018-11-12 06:00 | 168 | 168
2018-11-12 06:30 | 181 | 181
2018-11-12 07:00 | 191 | 191
2018-11-12 07:30 | 198 | 198
2018-11-12 08:00 | 196 | 196
2018-11-12 08:30 | 193 | 193
2018-11-12 09:00 | 189 | 189
2018-11-12 09:30 | 185 | 185
2018-11-12 10:00 | 183 | 183
2018-11-12 10:30 | 185 | 185
2018-11-12 11:00 | 186 | 186
2018-11-12 11:30 | 181 | 181
2018-11-12 12:00 | 181 | 181
2018-11-12 12:30 | 183 | 183
2018-11-12 13:00 | 187 | 187
2018-11-12 13:30 | 191 | 191
2018-11-12 14:00 | 195 | 195
2018-11-12 14:30 | 201 | 201
2018-11-12 15:00 | 207 | 207
2018-11-12 15:30 | 214 | 214
2018-11-12 16:00 | 230 | 230
2018-11-12 16:30 | 242 | 242
2018-11-12 17:00 | 255 | 254
2018-11-12 17:30 | 259 | 259
2018-11-12 18:00 | 266 | 266
2018-11-12 18:30 | 269 | 269
2018-11-12 19:00 | 279 | 279
2018-11-12 19:30 | 273 | 273
2018-11-12 20:00 | 267 | 266
2018-11-12 20:30 | 261 | 261
2018-11-12 21:00 | 250 | 250
2018-11-12 21:30 | 238 | 238
2018-11-12 22:00 | 228 | 228
2018-11-12 22:30 | 219 | 218
2018-11-12 23:00 | 215 | 214
2018-11-12 23:30 | 201 | 201
2018-11-13 | 186 | 186
2018-11-13 00:30 | 171 | 171
2018-11-13 01:00 | 164 | 163
2018-11-13 01:30 | 159 | 159
2018-11-13 02:00 | 156 | 156
2018-11-13 02:30 | 155 | 155
2018-11-13 03:00 | 153 | 153
2018-11-13 03:30 | 153 | 153
2018-11-13 04:00 | 153 | 153
2018-11-13 04:30 | 157 | 157
2018-11-13 05:00 | 161 | 161
2018-11-13 05:30 | 171 | 171
2018-11-13 06:00 | 181 | 181
2018-11-13 06:30 | 197 | 197
2018-11-13 07:00 | 202 | 202
2018-11-13 07:30 | 204 | 204
2018-11-13 08:00 | 204 | 204
2018-11-13 08:30 | 208 | 208
2018-11-13 09:00 | 213 | 213
2018-11-13 09:30 | 212 | 212
2018-11-13 10:00 | 207 | 207
2018-11-13 10:30 | 197 | 197
2018-11-13 11:00 | 195 | 195
2018-11-13 11:30 | 195 | 195
2018-11-13 12:00 | 194 | 194
2018-11-13 12:30 | 194 | 193
2018-11-13 13:00 | 194 | 194
2018-11-13 13:30 | 193 | 193
2018-11-13 14:00 | 197 | 197
2018-11-13 14:30 | 206 | 206
2018-11-13 15:00 | 214 | 214
2018-11-13 15:30 | 226 | 226
2018-11-13 16:00 | 243 | 242
2018-11-13 16:30 | 251 | 251
2018-11-13 17:00 | 262 | 261
2018-11-13 17:30 | 268 | 268
2018-11-13 18:00 | 265 | 265
2018-11-13 18:30 | 268 | 268
2018-11-13 19:00 | 279 | 279
2018-11-13 19:30 | 274 | 274
2018-11-13 20:00 | 269 | 269
2018-11-13 20:30 | 263 | 263
2018-11-13 21:00 | 252 | 252
2018-11-13 21:30 | 239 | 239
2018-11-13 22:00 | 228 | 228
2018-11-13 22:30 | 220 | 219
2018-11-13 23:00 | 215 | 214
2018-11-13 23:30 | 201 | 201
2018-11-14 | 185 | 185
2018-11-14 00:30 | 172 | 172
2018-11-14 01:00 | 163 | 163
2018-11-14 01:30 | 159 | 159
2018-11-14 02:00 | 156 | 156
2018-11-14 02:30 | 154 | 153
2018-11-14 03:00 | 152 | 152
2018-11-14 03:30 | 152 | 152
2018-11-14 04:00 | 153 | 152
2018-11-14 04:30 | 154 | 154
2018-11-14 05:00 | 158 | 157
2018-11-14 05:30 | 165 | 165
2018-11-14 06:00 | 172 | 172
2018-11-14 06:30 | 187 | 187
2018-11-14 07:00 | 197 | 197
2018-11-14 07:30 | 210 | 208
2018-11-14 08:00 | 210 | 208
2018-11-14 08:30 | 209 | 207
2018-11-14 09:00 | 209 | 207
2018-11-14 09:30 | 214 | 213
2018-11-14 10:00 | 217 | 217
2018-11-14 10:30 | 216 | 216
2018-11-14 11:00 | 215 | 214
2018-11-14 11:30 | 210 | 209
2018-11-14 12:00 | 220 | 219
2018-11-14 12:30 | 225 | 225
2018-11-14 13:00 | 224 | 224
2018-11-14 13:30 | 235 | 235
2018-11-14 14:00 | 237 | 236
2018-11-14 14:30 | 243 | 243
2018-11-14 15:00 | 236 | 236
2018-11-14 15:30 | 246 | 246
2018-11-14 16:00 | 248 | 248
2018-11-14 16:30 | 264 | 264
2018-11-14 17:00 | 273 | 273
2018-11-14 17:30 | 273 | 273
2018-11-14 18:00 | 273 | 273
2018-11-14 18:30 | 276 | 276
2018-11-14 19:00 | 286 | 286
2018-11-14 19:30 | 281 | 281
2018-11-14 20:00 | 277 | 276
2018-11-14 20:30 | 273 | 273
2018-11-14 21:00 | 260 | 258
2018-11-14 21:30 | 248 | 244
2018-11-14 22:00 | 236 | 233
2018-11-14 22:30 | 229 | 226
2018-11-14 23:00 | 224 | 222
2018-11-14 23:30 | 208 | 207
2018-11-15 | 192 | 191
2018-11-15 00:30 | 177 | 177
2018-11-15 01:00 | 170 | 170
2018-11-15 01:30 | 164 | 164
2018-11-15 02:00 | 161 | 161
2018-11-15 02:30 | 158 | 158
2018-11-15 03:00 | 158 | 158
2018-11-15 03:30 | 157 | 157
2018-11-15 04:00 | 157 | 157
2018-11-15 04:30 | 161 | 161
2018-11-15 05:00 | 165 | 165
2018-11-15 05:30 | 174 | 174
2018-11-15 06:00 | 183 | 182
2018-11-15 06:30 | 196 | 195
2018-11-15 07:00 | 211 | 211
2018-11-15 07:30 | 224 | 224
2018-11-15 08:00 | 229 | 228
2018-11-15 08:30 | 225 | 224
2018-11-15 09:00 | 217 | 216
2018-11-15 09:30 | 219 | 218
2018-11-15 10:00 | 220 | 219
2018-11-15 10:30 | 220 | 219
2018-11-15 11:00 | 221 | 221
2018-11-15 11:30 | 220 | 219
2018-11-15 12:00 | 221 | 221
2018-11-15 12:30 | 224 | 224
2018-11-15 13:00 | 226 | 226
2018-11-15 13:30 | 233 | 232
2018-11-15 14:00 | 246 | 245
2018-11-15 14:30 | 257 | 255
2018-11-15 15:00 | 260 | 259
2018-11-15 15:30 | 259 | 258
2018-11-15 16:00 | 270 | 268
2018-11-15 16:30 | 281 | 280
2018-11-15 17:00 | 293 | 291
2018-11-15 17:30 | 291 | 290
2018-11-15 18:00 | 284 | 284
2018-11-15 18:30 | 282 | 282
2018-11-15 19:00 | 289 | 289
2018-11-15 19:30 | 285 | 285
2018-11-15 20:00 | 281 | 281
2018-11-15 20:30 | 276 | 276
2018-11-15 21:00 | 262 | 262
2018-11-15 21:30 | 249 | 249
2018-11-15 22:00 | 239 | 239
2018-11-15 22:30 | 232 | 232
2018-11-15 23:00 | 225 | 224
2018-11-15 23:30 | 210 | 210
2018-11-16 | 192 | 192
2018-11-16 00:30 | 176 | 176
2018-11-16 01:00 | 168 | 168
2018-11-16 01:30 | 162 | 162
2018-11-16 02:00 | 159 | 158
2018-11-16 02:30 | 156 | 156
2018-11-16 03:00 | 155 | 155
2018-11-16 03:30 | 154 | 154
2018-11-16 04:00 | 154 | 154
2018-11-16 04:30 | 157 | 157
2018-11-16 05:00 | 161 | 161
2018-11-16 05:30 | 171 | 171
2018-11-16 06:00 | 180 | 180
2018-11-16 06:30 | 196 | 194
2018-11-16 07:00 | 210 | 208
2018-11-16 07:30 | 220 | 220
2018-11-16 08:00 | 227 | 227
2018-11-16 08:30 | 226 | 226
2018-11-16 09:00 | 222 | 221
2018-11-16 09:30 | 223 | 223
2018-11-16 10:00 | 222 | 222
2018-11-16 10:30 | 220 | 220
2018-11-16 11:00 | 223 | 223
2018-11-16 11:30 | 228 | 228
2018-11-16 12:00 | 232 | 232
2018-11-16 12:30 | 235 | 235
2018-11-16 13:00 | 233 | 233
2018-11-16 13:30 | 238 | 238
2018-11-16 14:00 | 244 | 244
2018-11-16 14:30 | 246 | 246
2018-11-16 15:00 | 252 | 252
2018-11-16 15:30 | 259 | 259
2018-11-16 16:00 | 273 | 273
2018-11-16 16:30 | 283 | 283
2018-11-16 17:00 | 292 | 292
2018-11-16 17:30 | 289 | 289
2018-11-16 18:00 | 280 | 279
2018-11-16 18:30 | 274 | 274
2018-11-16 19:00 | 282 | 282
2018-11-16 19:30 | 278 | 278
2018-11-16 20:00 | 274 | 274
2018-11-16 20:30 | 270 | 270
2018-11-16 21:00 | 255 | 255
2018-11-16 21:30 | 243 | 242
2018-11-16 22:00 | 234 | 233
2018-11-16 22:30 | 229 | 229
2018-11-16 23:00 | 225 | 225
2018-11-16 23:30 | 211 | 211
2018-11-17 | 195 | 195
2018-11-17 00:30 | 181 | 181
2018-11-17 01:00 | 172 | 172
2018-11-17 01:30 | 165 | 165
2018-11-17 02:00 | 161 | 161
2018-11-17 02:30 | 158 | 158
2018-11-17 03:00 | 154 | 154
2018-11-17 03:30 | 153 | 153
2018-11-17 04:00 | 152 | 152
2018-11-17 04:30 | 153 | 153
2018-11-17 05:00 | 152 | 152
2018-11-17 05:30 | 153 | 153
2018-11-17 06:00 | 155 | 155
2018-11-17 06:30 | 159 | 159
2018-11-17 07:00 | 165 | 164
2018-11-17 07:30 | 172 | 171
2018-11-17 08:00 | 177 | 177
2018-11-17 08:30 | 191 | 191
2018-11-17 09:00 | 197 | 197
2018-11-17 09:30 | 197 | 197
2018-11-17 10:00 | 186 | 186
2018-11-17 10:30 | 187 | 187
2018-11-17 11:00 | 190 | 189
2018-11-17 11:30 | 183 | 183
2018-11-17 12:00 | 183 | 183
2018-11-17 12:30 | 201 | 200
2018-11-17 13:00 | 207 | 207
2018-11-17 13:30 | 193 | 193
2018-11-17 14:00 | 201 | 201
2018-11-17 14:30 | 209 | 209
2018-11-17 15:00 | 245 | 245
2018-11-17 15:30 | 258 | 257
2018-11-17 16:00 | 256 | 255
2018-11-17 16:30 | 254 | 254
2018-11-17 17:00 | 251 | 251
2018-11-17 17:30 | 246 | 246
2018-11-17 18:00 | 243 | 243
2018-11-17 18:30 | 244 | 244
2018-11-17 19:00 | 247 | 247
2018-11-17 19:30 | 238 | 237
2018-11-17 20:00 | 232 | 232
2018-11-17 20:30 | 227 | 227
2018-11-17 21:00 | 216 | 215
2018-11-17 21:30 | 209 | 207
2018-11-17 22:00 | 203 | 202
2018-11-17 22:30 | 201 | 200
2018-11-17 23:00 | 200 | 199
2018-11-17 23:30 | 189 | 188
2018-11-18 | 174 | 174
2018-11-18 00:30 | 161 | 161
2018-11-18 01:00 | 153 | 153
2018-11-18 01:30 | 149 | 148
2018-11-18 02:00 | 145 | 144
2018-11-18 02:30 | 142 | 141
2018-11-18 03:00 | 140 | 140
2018-11-18 03:30 | 139 | 138
2018-11-18 04:00 | 137 | 137
2018-11-18 04:30 | 138 | 137
2018-11-18 05:00 | 137 | 136
2018-11-18 05:30 | 137 | 136
2018-11-18 06:00 | 137 | 136
2018-11-18 06:30 | 140 | 139
2018-11-18 07:00 | 142 | 141
2018-11-18 07:30 | 145 | 145
2018-11-18 08:00 | 158 | 158
2018-11-18 08:30 | 165 | 165
2018-11-18 09:00 | 167 | 167
2018-11-18 09:30 | 163 | 162
2018-11-18 10:00 | 165 | 165
2018-11-18 10:30 | 168 | 168
2018-11-18 11:00 | 164 | 164
2018-11-18 11:30 | 167 | 166
2018-11-18 12:00 | 170 | 170
2018-11-18 12:30 | 169 | 169
2018-11-18 13:00 | 164 | 164
2018-11-18 13:30 | 168 | 168
2018-11-18 14:00 | 167 | 167
2018-11-18 14:30 | 165 | 165
2018-11-18 15:00 | 172 | 172
2018-11-18 15:30 | 179 | 179
2018-11-18 16:00 | 190 | 190
2018-11-18 16:30 | 195 | 195
2018-11-18 17:00 | 202 | 202
2018-11-18 17:30 | 211 | 211
2018-11-18 18:00 | 219 | 219
2018-11-18 18:30 | 228 | 228
2018-11-18 19:00 | 237 | 237
2018-11-18 19:30 | 233 | 233
2018-11-18 20:00 | 230 | 230
2018-11-18 20:30 | 226 | 226
2018-11-18 21:00 | 214 | 214
2018-11-18 21:30 | 204 | 204
2018-11-18 22:00 | 196 | 196
2018-11-18 22:30 | 192 | 192
2018-11-18 23:00 | 191 | 191
2018-11-18 23:30 | 181 | 181
2018-11-19 | 166 | 166
2018-11-19 00:30 | 154 | 153
2018-11-19 01:00 | 147 | 146
2018-11-19 01:30 | 142 | 142
2018-11-19 02:00 | 141 | 140
2018-11-19 02:30 | 140 | 139
2018-11-19 03:00 | 137 | 136
2018-11-19 03:30 | 137 | 136
2018-11-19 04:00 | 139 | 138
2018-11-19 04:30 | 143 | 143
2018-11-19 05:00 | 149 | 148
2018-11-19 05:30 | 158 | 158
2018-11-19 06:00 | 165 | 165
2018-11-19 06:30 | 180 | 180
2018-11-19 07:00 | 192 | 192
2018-11-19 07:30 | 200 | 200
2018-11-19 08:00 | 197 | 197
2018-11-19 08:30 | 191 | 191
2018-11-19 09:00 | 191 | 191
2018-11-19 09:30 | 197 | 197
2018-11-19 10:00 | 199 | 199
2018-11-19 10:30 | 199 | 199
2018-11-19 11:00 | 205 | 204
2018-11-19 11:30 | 202 | 202
2018-11-19 12:00 | 201 | 201
2018-11-19 12:30 | 202 | 202
2018-11-19 13:00 | 199 | 199
2018-11-19 13:30 | 202 | 201
2018-11-19 14:00 | 209 | 209
2018-11-19 14:30 | 212 | 211
2018-11-19 15:00 | 211 | 211
2018-11-19 15:30 | 219 | 219
2018-11-19 16:00 | 233 | 232
2018-11-19 16:30 | 244 | 244
2018-11-19 17:00 | 255 | 254
2018-11-19 17:30 | 259 | 258
2018-11-19 18:00 | 260 | 260
2018-11-19 18:30 | 260 | 260
2018-11-19 19:00 | 271 | 271
2018-11-19 19:30 | 267 | 267
2018-11-19 20:00 | 263 | 263
2018-11-19 20:30 | 257 | 257
2018-11-19 21:00 | 244 | 243
2018-11-19 21:30 | 233 | 231
2018-11-19 22:00 | 222 | 221
2018-11-19 22:30 | 216 | 216
2018-11-19 23:00 | 211 | 211
2018-11-19 23:30 | 197 | 197
2018-11-20 | 182 | 182
2018-11-20 00:30 | 168 | 168
2018-11-20 01:00 | 160 | 160
2018-11-20 01:30 | 155 | 154
2018-11-20 02:00 | 151 | 151
2018-11-20 02:30 | 149 | 149
2018-11-20 03:00 | 147 | 147
2018-11-20 03:30 | 147 | 147
2018-11-20 04:00 | 148 | 148
2018-11-20 04:30 | 152 | 152
2018-11-20 05:00 | 156 | 156
2018-11-20 05:30 | 166 | 166
2018-11-20 06:00 | 173 | 173
2018-11-20 06:30 | 187 | 186
2018-11-20 07:00 | 197 | 196
2018-11-20 07:30 | 202 | 201
2018-11-20 08:00 | 196 | 195
2018-11-20 08:30 | 194 | 192
2018-11-20 09:00 | 194 | 191
2018-11-20 09:30 | 196 | 195
2018-11-20 10:00 | 198 | 196
2018-11-20 10:30 | 190 | 188
2018-11-20 11:00 | 186 | 184
2018-11-20 11:30 | 187 | 184
2018-11-20 12:00 | 192 | 189
2018-11-20 12:30 | 195 | 192
2018-11-20 13:00 | 200 | 197
2018-11-20 13:30 | 203 | 200
2018-11-20 14:00 | 209 | 208
2018-11-20 14:30 | 216 | 216
2018-11-20 15:00 | 223 | 222
2018-11-20 15:30 | 232 | 231
2018-11-20 16:00 | 249 | 248
2018-11-20 16:30 | 266 | 265
2018-11-20 17:00 | 270 | 269
2018-11-20 17:30 | 275 | 274
2018-11-20 18:00 | 274 | 274
2018-11-20 18:30 | 274 | 274
2018-11-20 19:00 | 286 | 284
2018-11-20 19:30 | 281 | 280
2018-11-20 20:00 | 275 | 275
2018-11-20 20:30 | 269 | 269
2018-11-20 21:00 | 257 | 257
2018-11-20 21:30 | 245 | 245
2018-11-20 22:00 | 231 | 231
2018-11-20 22:30 | 224 | 224
2018-11-20 23:00 | 218 | 218
2018-11-20 23:30 | 205 | 205
2018-11-21 | 190 | 189
2018-11-21 00:30 | 174 | 174
2018-11-21 01:00 | 167 | 167
2018-11-21 01:30 | 161 | 161
2018-11-21 02:00 | 158 | 158
2018-11-21 02:30 | 155 | 155
2018-11-21 03:00 | 155 | 154
2018-11-21 03:30 | 154 | 154
2018-11-21 04:00 | 155 | 155
2018-11-21 04:30 | 159 | 158
2018-11-21 05:00 | 162 | 162
2018-11-21 05:30 | 172 | 172
2018-11-21 06:00 | 181 | 181
2018-11-21 06:30 | 196 | 195
2018-11-21 07:00 | 206 | 205
2018-11-21 07:30 | 213 | 212
2018-11-21 08:00 | 213 | 211
2018-11-21 08:30 | 212 | 209
2018-11-21 09:00 | 209 | 207
2018-11-21 09:30 | 210 | 207
2018-11-21 10:00 | 211 | 208
2018-11-21 10:30 | 214 | 211
2018-11-21 11:00 | 218 | 215
2018-11-21 11:30 | 224 | 222
2018-11-21 12:00 | 227 | 224
2018-11-21 12:30 | 231 | 229
2018-11-21 13:00 | 240 | 238
2018-11-21 13:30 | 253 | 253
2018-11-21 14:00 | 265 | 265
2018-11-21 14:30 | 285 | 285
2018-11-21 15:00 | 292 | 292
2018-11-21 15:30 | 298 | 298
2018-11-21 16:00 | 314 | 314
2018-11-21 16:30 | 315 | 315
2018-11-21 17:00 | 319 | 319
2018-11-21 17:30 | 317 | 317
2018-11-21 18:00 | 313 | 313
2018-11-21 18:30 | 314 | 314
2018-11-21 19:00 | 321 | 321
2018-11-21 19:30 | 316 | 316
2018-11-21 20:00 | 307 | 307
2018-11-21 20:30 | 300 | 300
2018-11-21 21:00 | 286 | 286
2018-11-21 21:30 | 272 | 272
2018-11-21 22:00 | 260 | 260
2018-11-21 22:30 | 250 | 249
2018-11-21 23:00 | 239 | 239
2018-11-21 23:30 | 225 | 225
2018-11-22 | 208 | 208
2018-11-22 00:30 | 194 | 194
2018-11-22 01:00 | 186 | 185
2018-11-22 01:30 | 179 | 178
2018-11-22 02:00 | 172 | 172
2018-11-22 02:30 | 169 | 169
2018-11-22 03:00 | 168 | 168
2018-11-22 03:30 | 167 | 167
2018-11-22 04:00 | 167 | 167
2018-11-22 04:30 | 171 | 171
2018-11-22 05:00 | 174 | 174
2018-11-22 05:30 | 183 | 183
2018-11-22 06:00 | 195 | 195
2018-11-22 06:30 | 215 | 215
2018-11-22 07:00 | 235 | 235
2018-11-22 07:30 | 280 | 279
2018-11-22 08:00 | 294 | 294
2018-11-22 08:30 | 289 | 288
2018-11-22 09:00 | 291 | 290
2018-11-22 09:30 | 294 | 293
2018-11-22 10:00 | 292 | 290
2018-11-22 10:30 | 302 | 299
2018-11-22 11:00 | 336 | 334
2018-11-22 11:30 | 350 | 350
2018-11-22 12:00 | 333 | 333
2018-11-22 12:30 | 309 | 308
2018-11-22 13:00 | 273 | 272
2018-11-22 13:30 | 256 | 254
2018-11-22 14:00 | 254 | 252
2018-11-22 14:30 | 270 | 267
2018-11-22 15:00 | 270 | 267
2018-11-22 15:30 | 274 | 271
2018-11-22 16:00 | 263 | 261
2018-11-22 16:30 | 287 | 287
2018-11-22 17:00 | 299 | 299
2018-11-22 17:30 | 305 | 305
2018-11-22 18:00 | 304 | 304
2018-11-22 18:30 | 302 | 302
2018-11-22 19:00 | 314 | 314
2018-11-22 19:30 | 312 | 312
2018-11-22 20:00 | 306 | 306
2018-11-22 20:30 | 297 | 297
2018-11-22 21:00 | 281 | 280
2018-11-22 21:30 | 263 | 262
2018-11-22 22:00 | 248 | 245
2018-11-22 22:30 | 239 | 237
2018-11-22 23:00 | 231 | 229
2018-11-22 23:30 | 216 | 214
2018-11-23 | 198 | 197
2018-11-23 00:30 | 181 | 180
2018-11-23 01:00 | 172 | 172
2018-11-23 01:30 | 165 | 165
2018-11-23 02:00 | 160 | 160
2018-11-23 02:30 | 158 | 158
2018-11-23 03:00 | 156 | 156
2018-11-23 03:30 | 156 | 156
2018-11-23 04:00 | 157 | 157
2018-11-23 04:30 | 159 | 159
2018-11-23 05:00 | 161 | 161
2018-11-23 05:30 | 169 | 169
2018-11-23 06:00 | 177 | 176
2018-11-23 06:30 | 190 | 190
2018-11-23 07:00 | 197 | 196
2018-11-23 07:30 | 202 | 201
2018-11-23 08:00 | 198 | 197
2018-11-23 08:30 | 192 | 190
2018-11-23 09:00 | 185 | 184
2018-11-23 09:30 | 180 | 178
2018-11-23 10:00 | 178 | 176
2018-11-23 10:30 | 176 | 173
2018-11-23 11:00 | 176 | 173
2018-11-23 11:30 | 175 | 172
2018-11-23 12:00 | 177 | 174
2018-11-23 12:30 | 180 | 177
2018-11-23 13:00 | 184 | 181
2018-11-23 13:30 | 189 | 186
2018-11-23 14:00 | 197 | 194
2018-11-23 14:30 | 207 | 204
2018-11-23 15:00 | 214 | 214
2018-11-23 15:30 | 226 | 226
2018-11-23 16:00 | 243 | 243
2018-11-23 16:30 | 258 | 258
2018-11-23 17:00 | 270 | 270
2018-11-23 17:30 | 273 | 273
2018-11-23 18:00 | 269 | 268
2018-11-23 18:30 | 265 | 264
2018-11-23 19:00 | 274 | 274
2018-11-23 19:30 | 272 | 272
2018-11-23 20:00 | 269 | 269
2018-11-23 20:30 | 262 | 261
2018-11-23 21:00 | 251 | 251
2018-11-23 21:30 | 236 | 236
2018-11-23 22:00 | 226 | 226
2018-11-23 22:30 | 221 | 221
2018-11-23 23:00 | 218 | 217
2018-11-23 23:30 | 203 | 203
2018-11-24 | 185 | 185
2018-11-24 00:30 | 171 | 170
2018-11-24 01:00 | 163 | 162
2018-11-24 01:30 | 156 | 156
2018-11-24 02:00 | 152 | 151
2018-11-24 02:30 | 150 | 149
2018-11-24 03:00 | 148 | 148
2018-11-24 03:30 | 146 | 146
2018-11-24 04:00 | 146 | 146
2018-11-24 04:30 | 146 | 146
2018-11-24 05:00 | 144 | 144
2018-11-24 05:30 | 145 | 145
2018-11-24 06:00 | 145 | 145
2018-11-24 06:30 | 147 | 147
2018-11-24 07:00 | 150 | 150
2018-11-24 07:30 | 152 | 152
2018-11-24 08:00 | 144 | 144
2018-11-24 08:30 | 145 | 144
2018-11-24 09:00 | 143 | 142
2018-11-24 09:30 | 140 | 139
2018-11-24 10:00 | 137 | 135
2018-11-24 10:30 | 134 | 132
2018-11-24 11:00 | 131 | 129
2018-11-24 11:30 | 131 | 129
2018-11-24 12:00 | 130 | 128
2018-11-24 12:30 | 132 | 130
2018-11-24 13:00 | 135 | 133
2018-11-24 13:30 | 139 | 137
2018-11-24 14:00 | 147 | 144
2018-11-24 14:30 | 158 | 155
2018-11-24 15:00 | 170 | 168
2018-11-24 15:30 | 183 | 182
2018-11-24 16:00 | 199 | 197
2018-11-24 16:30 | 213 | 212
2018-11-24 17:00 | 228 | 227
2018-11-24 17:30 | 235 | 235
2018-11-24 18:00 | 237 | 236
2018-11-24 18:30 | 239 | 239
2018-11-24 19:00 | 250 | 250
2018-11-24 19:30 | 248 | 248
2018-11-24 20:00 | 243 | 243
2018-11-24 20:30 | 236 | 236
2018-11-24 21:00 | 224 | 223
2018-11-24 21:30 | 216 | 215
2018-11-24 22:00 | 209 | 209
2018-11-24 22:30 | 206 | 206
2018-11-24 23:00 | 204 | 204
2018-11-24 23:30 | 192 | 192
2018-11-25 | 178 | 178
2018-11-25 00:30 | 164 | 164
2018-11-25 01:00 | 155 | 155
2018-11-25 01:30 | 150 | 150
2018-11-25 02:00 | 147 | 147
2018-11-25 02:30 | 144 | 144
2018-11-25 03:00 | 143 | 143
2018-11-25 03:30 | 141 | 141
2018-11-25 04:00 | 140 | 140
2018-11-25 04:30 | 140 | 140
2018-11-25 05:00 | 138 | 138
2018-11-25 05:30 | 136 | 136
2018-11-25 06:00 | 134 | 134
2018-11-25 06:30 | 134 | 133
2018-11-25 07:00 | 132 | 132
2018-11-25 07:30 | 134 | 133
2018-11-25 08:00 | 134 | 133
2018-11-25 08:30 | 136 | 134
2018-11-25 09:00 | 148 | 146
2018-11-25 09:30 | 171 | 170
2018-11-25 10:00 | 149 | 148
2018-11-25 10:30 | 144 | 142
2018-11-25 11:00 | 168 | 166
2018-11-25 11:30 | 186 | 184
2018-11-25 12:00 | 163 | 161
2018-11-25 12:30 | 161 | 159
2018-11-25 13:00 | 176 | 175
2018-11-25 13:30 | 193 | 192
2018-11-25 14:00 | 212 | 212
2018-11-25 14:30 | 211 | 211
2018-11-25 15:00 | 221 | 221
2018-11-25 15:30 | 245 | 245
2018-11-25 16:00 | 229 | 229
2018-11-25 16:30 | 236 | 236
2018-11-25 17:00 | 253 | 253
2018-11-25 17:30 | 260 | 260
2018-11-25 18:00 | 264 | 264
2018-11-25 18:30 | 265 | 265
2018-11-25 19:00 | 272 | 272
2018-11-25 19:30 | 270 | 270
2018-11-25 20:00 | 266 | 266
2018-11-25 20:30 | 260 | 260
2018-11-25 21:00 | 247 | 247
2018-11-25 21:30 | 236 | 236
2018-11-25 22:00 | 226 | 226
2018-11-25 22:30 | 219 | 219
2018-11-25 23:00 | 214 | 214
2018-11-25 23:30 | 200 | 200
2018-11-26 | 184 | 184
2018-11-26 00:30 | 170 | 170
2018-11-26 01:00 | 161 | 161
2018-11-26 01:30 | 157 | 156
2018-11-26 02:00 | 152 | 152
2018-11-26 02:30 | 150 | 150
2018-11-26 03:00 | 148 | 148
2018-11-26 03:30 | 148 | 148
2018-11-26 04:00 | 148 | 148
2018-11-26 04:30 | 152 | 152
2018-11-26 05:00 | 156 | 155
2018-11-26 05:30 | 166 | 165
2018-11-26 06:00 | 174 | 174
2018-11-26 06:30 | 189 | 189
2018-11-26 07:00 | 202 | 201
2018-11-26 07:30 | 210 | 209
2018-11-26 08:00 | 210 | 209
2018-11-26 08:30 | 208 | 207
2018-11-26 09:00 | 207 | 207
2018-11-26 09:30 | 210 | 209
2018-11-26 10:00 | 210 | 209
2018-11-26 10:30 | 213 | 211
2018-11-26 11:00 | 217 | 215
2018-11-26 11:30 | 222 | 219
2018-11-26 12:00 | 227 | 224
2018-11-26 12:30 | 232 | 229
2018-11-26 13:00 | 241 | 237
2018-11-26 13:30 | 250 | 246
2018-11-26 14:00 | 259 | 256
2018-11-26 14:30 | 268 | 268
2018-11-26 15:00 | 275 | 275
2018-11-26 15:30 | 285 | 284
2018-11-26 16:00 | 298 | 298
2018-11-26 16:30 | 308 | 308
2018-11-26 17:00 | 316 | 316
2018-11-26 17:30 | 315 | 315
2018-11-26 18:00 | 307 | 307
2018-11-26 18:30 | 301 | 300
2018-11-26 19:00 | 308 | 307
2018-11-26 19:30 | 303 | 303
2018-11-26 20:00 | 294 | 293
2018-11-26 20:30 | 287 | 286
2018-11-26 21:00 | 270 | 270
2018-11-26 21:30 | 255 | 255
2018-11-26 22:00 | 241 | 241
2018-11-26 22:30 | 232 | 232
2018-11-26 23:00 | 226 | 225
2018-11-26 23:30 | 211 | 210
2018-11-27 | 195 | 195
2018-11-27 00:30 | 179 | 179
2018-11-27 01:00 | 171 | 171
2018-11-27 01:30 | 166 | 166
2018-11-27 02:00 | 162 | 162
2018-11-27 02:30 | 159 | 159
2018-11-27 03:00 | 157 | 157
2018-11-27 03:30 | 157 | 157
2018-11-27 04:00 | 157 | 157
2018-11-27 04:30 | 161 | 161
2018-11-27 05:00 | 163 | 163
2018-11-27 05:30 | 172 | 172
2018-11-27 06:00 | 183 | 183
2018-11-27 06:30 | 192 | 192
2018-11-27 07:00 | 209 | 207
2018-11-27 07:30 | 219 | 218
2018-11-27 08:00 | 228 | 227
2018-11-27 08:30 | 237 | 237
2018-11-27 09:00 | 236 | 235
2018-11-27 09:30 | 242 | 242
2018-11-27 10:00 | 238 | 237
2018-11-27 10:30 | 237 | 237
2018-11-27 11:00 | 244 | 243
2018-11-27 11:30 | 253 | 252
2018-11-27 12:00 | 258 | 257
2018-11-27 12:30 | 255 | 255
2018-11-27 13:00 | 247 | 246
2018-11-27 13:30 | 231 | 231
2018-11-27 14:00 | 240 | 240
2018-11-27 14:30 | 244 | 243
2018-11-27 15:00 | 235 | 235
2018-11-27 15:30 | 251 | 251
2018-11-27 16:00 | 271 | 270
2018-11-27 16:30 | 285 | 285
2018-11-27 17:00 | 297 | 296
2018-11-27 17:30 | 301 | 301
2018-11-27 18:00 | 300 | 299
2018-11-27 18:30 | 299 | 298
2018-11-27 19:00 | 311 | 311
2018-11-27 19:30 | 309 | 308
2018-11-27 20:00 | 303 | 303
2018-11-27 20:30 | 297 | 297
2018-11-27 21:00 | 285 | 285
2018-11-27 21:30 | 273 | 272
2018-11-27 22:00 | 258 | 257
2018-11-27 22:30 | 250 | 250
2018-11-27 23:00 | 244 | 244
2018-11-27 23:30 | 229 | 229
2018-11-28 | 210 | 210
2018-11-28 00:30 | 195 | 194
2018-11-28 01:00 | 186 | 186
2018-11-28 01:30 | 179 | 179
2018-11-28 02:00 | 174 | 174
2018-11-28 02:30 | 172 | 172
2018-11-28 03:00 | 170 | 170
2018-11-28 03:30 | 170 | 170
2018-11-28 04:00 | 172 | 172
2018-11-28 04:30 | 176 | 176
2018-11-28 05:00 | 180 | 180
2018-11-28 05:30 | 187 | 187
2018-11-28 06:00 | 200 | 200
2018-11-28 06:30 | 219 | 217
2018-11-28 07:00 | 239 | 239
2018-11-28 07:30 | 261 | 261
2018-11-28 08:00 | 267 | 266
2018-11-28 08:30 | 268 | 267
2018-11-28 09:00 | 265 | 263
2018-11-28 09:30 | 266 | 264
2018-11-28 10:00 | 262 | 260
2018-11-28 10:30 | 267 | 267
2018-11-28 11:00 | 283 | 283
2018-11-28 11:30 | 300 | 300
2018-11-28 12:00 | 315 | 315
2018-11-28 12:30 | 346 | 346
2018-11-28 13:00 | 324 | 324
2018-11-28 13:30 | 313 | 313
2018-11-28 14:00 | 316 | 316
2018-11-28 14:30 | 316 | 316
2018-11-28 15:00 | 320 | 320
2018-11-28 15:30 | 326 | 326
2018-11-28 16:00 | 343 | 343
2018-11-28 16:30 | 356 | 356
2018-11-28 17:00 | 372 | 372
2018-11-28 17:30 | 373 | 373
2018-11-28 18:00 | 363 | 363
2018-11-28 18:30 | 354 | 354
2018-11-28 19:00 | 357 | 356
2018-11-28 19:30 | 350 | 350
2018-11-28 20:00 | 340 | 340
2018-11-28 20:30 | 327 | 327
2018-11-28 21:00 | 306 | 306
2018-11-28 21:30 | 289 | 289
2018-11-28 22:00 | 272 | 272
2018-11-28 22:30 | 261 | 260
2018-11-28 23:00 | 250 | 249
2018-11-28 23:30 | 229 | 229
2018-11-29 | 215 | 214
2018-11-29 00:30 | 200 | 200
2018-11-29 01:00 | 191 | 191
2018-11-29 01:30 | 184 | 184
2018-11-29 02:00 | 178 | 178
2018-11-29 02:30 | 176 | 176
2018-11-29 03:00 | 173 | 173
2018-11-29 03:30 | 172 | 172
2018-11-29 04:00 | 171 | 171
2018-11-29 04:30 | 174 | 174
2018-11-29 05:00 | 176 | 176
2018-11-29 05:30 | 185 | 185
2018-11-29 06:00 | 194 | 194
2018-11-29 06:30 | 211 | 210
2018-11-29 07:00 | 221 | 219
2018-11-29 07:30 | 229 | 228
2018-11-29 08:00 | 228 | 228
2018-11-29 08:30 | 226 | 226
2018-11-29 09:00 | 225 | 224
2018-11-29 09:30 | 225 | 225
2018-11-29 10:00 | 226 | 226
2018-11-29 10:30 | 230 | 229
2018-11-29 11:00 | 234 | 234
2018-11-29 11:30 | 240 | 239
2018-11-29 12:00 | 247 | 246
2018-11-29 12:30 | 256 | 255
2018-11-29 13:00 | 270 | 269
2018-11-29 13:30 | 283 | 282
2018-11-29 14:00 | 296 | 296
2018-11-29 14:30 | 305 | 305
2018-11-29 15:00 | 310 | 309
2018-11-29 15:30 | 313 | 313
2018-11-29 16:00 | 319 | 318
2018-11-29 16:30 | 325 | 325
2018-11-29 17:00 | 330 | 330
2018-11-29 17:30 | 330 | 330
2018-11-29 18:00 | 325 | 325
2018-11-29 18:30 | 319 | 319
2018-11-29 19:00 | 326 | 326
2018-11-29 19:30 | 323 | 323
2018-11-29 20:00 | 317 | 317
2018-11-29 20:30 | 309 | 309
2018-11-29 21:00 | 295 | 295
2018-11-29 21:30 | 278 | 278
2018-11-29 22:00 | 261 | 261
2018-11-29 22:30 | 254 | 254
2018-11-29 23:00 | 245 | 245
2018-11-29 23:30 | 228 | 227
2018-11-30 | 210 | 210
2018-11-30 00:30 | 194 | 194
2018-11-30 01:00 | 185 | 185
2018-11-30 01:30 | 179 | 179
2018-11-30 02:00 | 175 | 174
2018-11-30 02:30 | 172 | 172
2018-11-30 03:00 | 171 | 171
2018-11-30 03:30 | 170 | 170
2018-11-30 04:00 | 170 | 170
2018-11-30 04:30 | 172 | 172
2018-11-30 05:00 | 175 | 175
2018-11-30 05:30 | 184 | 184
2018-11-30 06:00 | 192 | 192
2018-11-30 06:30 | 208 | 208
2018-11-30 07:00 | 220 | 220
2018-11-30 07:30 | 227 | 227
2018-11-30 08:00 | 227 | 227
2018-11-30 08:30 | 226 | 225
2018-11-30 09:00 | 222 | 220
2018-11-30 09:30 | 222 | 221
2018-11-30 10:00 | 222 | 221
2018-11-30 10:30 | 225 | 224
2018-11-30 11:00 | 229 | 229
2018-11-30 11:30 | 251 | 251
2018-11-30 12:00 | 280 | 280
2018-11-30 12:30 | 266 | 265
2018-11-30 13:00 | 256 | 255
2018-11-30 13:30 | 276 | 276
2018-11-30 14:00 | 276 | 276
2018-11-30 14:30 | 271 | 271
2018-11-30 15:00 | 281 | 281
2018-11-30 15:30 | 284 | 284
2018-11-30 16:00 | 294 | 294
2018-11-30 16:30 | 305 | 305
2018-11-30 17:00 | 315 | 314
2018-11-30 17:30 | 314 | 313
2018-11-30 18:00 | 307 | 306
2018-11-30 18:30 | 299 | 299
2018-11-30 19:00 | 306 | 306
2018-11-30 19:30 | 305 | 305
2018-11-30 20:00 | 301 | 301
2018-11-30 20:30 | 292 | 292
2018-11-30 21:00 | 279 | 279
2018-11-30 21:30 | 269 | 269
2018-11-30 22:00 | 258 | 258
2018-11-30 22:30 | 252 | 252
2018-11-30 23:00 | 246 | 246
2018-11-30 23:30 | 231 | 231
2018-12-01 | 213 | 213
2018-12-01 00:30 | 194 | 194
2018-12-01 01:00 | 185 | 185
2018-12-01 01:30 | 177 | 177
2018-12-01 02:00 | 171 | 171
2018-12-01 02:30 | 167 | 166
2018-12-01 03:00 | 163 | 163
2018-12-01 03:30 | 162 | 162
2018-12-01 04:00 | 163 | 162
2018-12-01 04:30 | 161 | 161
2018-12-01 05:00 | 157 | 157
2018-12-01 05:30 | 159 | 159
2018-12-01 06:00 | 162 | 162
2018-12-01 06:30 | 168 | 168
2018-12-01 07:00 | 173 | 173
2018-12-01 07:30 | 179 | 179
2018-12-01 08:00 | 182 | 181
2018-12-01 08:30 | 187 | 186
2018-12-01 09:00 | 191 | 189
2018-12-01 09:30 | 195 | 194
2018-12-01 10:00 | 201 | 201
2018-12-01 10:30 | 206 | 206
2018-12-01 11:00 | 212 | 212
2018-12-01 11:30 | 219 | 219
2018-12-01 12:00 | 226 | 226
2018-12-01 12:30 | 234 | 234
2018-12-01 13:00 | 244 | 244
2018-12-01 13:30 | 256 | 255
2018-12-01 14:00 | 268 | 267
2018-12-01 14:30 | 279 | 277
2018-12-01 15:00 | 289 | 288
2018-12-01 15:30 | 301 | 300
2018-12-01 16:00 | 317 | 317
2018-12-01 16:30 | 328 | 328
2018-12-01 17:00 | 337 | 337
2018-12-01 17:30 | 335 | 335
2018-12-01 18:00 | 328 | 328
2018-12-01 18:30 | 324 | 323
2018-12-01 19:00 | 326 | 326
2018-12-01 19:30 | 324 | 324
2018-12-01 20:00 | 320 | 320
2018-12-01 20:30 | 311 | 310
2018-12-01 21:00 | 293 | 293
2018-12-01 21:30 | 281 | 280
2018-12-01 22:00 | 270 | 270
2018-12-01 22:30 | 264 | 264
2018-12-01 23:00 | 257 | 257
2018-12-01 23:30 | 240 | 239
2018-12-02 | 223 | 222
2018-12-02 00:30 | 207 | 206
2018-12-02 01:00 | 195 | 195
2018-12-02 01:30 | 188 | 187
2018-12-02 02:00 | 182 | 181
2018-12-02 02:30 | 177 | 177
2018-12-02 03:00 | 174 | 174
2018-12-02 03:30 | 172 | 171
2018-12-02 04:00 | 170 | 170
2018-12-02 04:30 | 169 | 168
2018-12-02 05:00 | 167 | 165
2018-12-02 05:30 | 166 | 165
2018-12-02 06:00 | 162 | 162
2018-12-02 06:30 | 165 | 165
2018-12-02 07:00 | 167 | 167
2018-12-02 07:30 | 174 | 174
2018-12-02 08:00 | 179 | 178
2018-12-02 08:30 | 187 | 186
2018-12-02 09:00 | 195 | 195
2018-12-02 09:30 | 208 | 208
2018-12-02 10:00 | 213 | 213
2018-12-02 10:30 | 226 | 226
2018-12-02 11:00 | 237 | 237
2018-12-02 11:30 | 249 | 249
2018-12-02 12:00 | 268 | 267
2018-12-02 12:30 | 281 | 281
2018-12-02 13:00 | 290 | 290
2018-12-02 13:30 | 311 | 310
2018-12-02 14:00 | 318 | 317
2018-12-02 14:30 | 330 | 329
2018-12-02 15:00 | 347 | 347
2018-12-02 15:30 | 361 | 361
2018-12-02 16:00 | 369 | 368
2018-12-02 16:30 | 372 | 372
2018-12-02 17:00 | 384 | 384
2018-12-02 17:30 | 382 | 382
2018-12-02 18:00 | 382 | 382
2018-12-02 18:30 | 380 | 380
2018-12-02 19:00 | 383 | 382
2018-12-02 19:30 | 380 | 380
2018-12-02 20:00 | 370 | 370
2018-12-02 20:30 | 356 | 356
2018-12-02 21:00 | 336 | 335
2018-12-02 21:30 | 316 | 315
2018-12-02 22:00 | 295 | 294
2018-12-02 22:30 | 283 | 282
2018-12-02 23:00 | 272 | 271
2018-12-02 23:30 | 249 | 249
2018-12-03 | 230 | 229
2018-12-03 00:30 | 215 | 214
2018-12-03 01:00 | 204 | 203
2018-12-03 01:30 | 195 | 194
2018-12-03 02:00 | 190 | 189
2018-12-03 02:30 | 187 | 186
2018-12-03 03:00 | 182 | 182
2018-12-03 03:30 | 182 | 181
2018-12-03 04:00 | 183 | 183
2018-12-03 04:30 | 185 | 185
2018-12-03 05:00 | 187 | 187
2018-12-03 05:30 | 198 | 198
2018-12-03 06:00 | 207 | 207
2018-12-03 06:30 | 226 | 225
2018-12-03 07:00 | 241 | 240
2018-12-03 07:30 | 254 | 254
2018-12-03 08:00 | 259 | 259
2018-12-03 08:30 | 262 | 262
2018-12-03 09:00 | 262 | 262
2018-12-03 09:30 | 265 | 264
2018-12-03 10:00 | 267 | 266
2018-12-03 10:30 | 267 | 267
2018-12-03 11:00 | 271 | 271
2018-12-03 11:30 | 275 | 275
2018-12-03 12:00 | 280 | 280
2018-12-03 12:30 | 295 | 295
2018-12-03 13:00 | 290 | 290
2018-12-03 13:30 | 288 | 288
2018-12-03 14:00 | 288 | 288
2018-12-03 14:30 | 298 | 298
2018-12-03 15:00 | 306 | 305
2018-12-03 15:30 | 316 | 316
2018-12-03 16:00 | 326 | 326
2018-12-03 16:30 | 331 | 331
2018-12-03 17:00 | 336 | 336
2018-12-03 17:30 | 333 | 333
2018-12-03 18:00 | 326 | 326
2018-12-03 18:30 | 319 | 319
2018-12-03 19:00 | 324 | 324
2018-12-03 19:30 | 319 | 319
2018-12-03 20:00 | 310 | 310
2018-12-03 20:30 | 300 | 300
2018-12-03 21:00 | 285 | 284
2018-12-03 21:30 | 268 | 268
2018-12-03 22:00 | 255 | 255
2018-12-03 22:30 | 245 | 245
2018-12-03 23:00 | 238 | 237
2018-12-03 23:30 | 220 | 220
2018-12-04 | 202 | 202
2018-12-04 00:30 | 187 | 187
2018-12-04 01:00 | 179 | 179
2018-12-04 01:30 | 174 | 174
2018-12-04 02:00 | 170 | 170
2018-12-04 02:30 | 167 | 167
2018-12-04 03:00 | 166 | 165
2018-12-04 03:30 | 166 | 166
2018-12-04 04:00 | 165 | 165
2018-12-04 04:30 | 168 | 168
2018-12-04 05:00 | 171 | 171
2018-12-04 05:30 | 179 | 179
2018-12-04 06:00 | 188 | 188
2018-12-04 06:30 | 205 | 205
2018-12-04 07:00 | 215 | 214
2018-12-04 07:30 | 231 | 230
2018-12-04 08:00 | 233 | 233
2018-12-04 08:30 | 244 | 244
2018-12-04 09:00 | 248 | 248
2018-12-04 09:30 | 252 | 252
2018-12-04 10:00 | 253 | 253
2018-12-04 10:30 | 260 | 260
2018-12-04 11:00 | 254 | 254
2018-12-04 11:30 | 267 | 267
2018-12-04 12:00 | 261 | 261
2018-12-04 12:30 | 252 | 252
2018-12-04 13:00 | 270 | 270
2018-12-04 13:30 | 293 | 293
2018-12-04 14:00 | 301 | 301
2018-12-04 14:30 | 312 | 311
2018-12-04 15:00 | 312 | 311
2018-12-04 15:30 | 310 | 310
2018-12-04 16:00 | 308 | 307
2018-12-04 16:30 | 308 | 307
2018-12-04 17:00 | 310 | 309
2018-12-04 17:30 | 306 | 306
2018-12-04 18:00 | 300 | 300
2018-12-04 18:30 | 299 | 299
2018-12-04 19:00 | 305 | 305
2018-12-04 19:30 | 300 | 300
2018-12-04 20:00 | 296 | 296
2018-12-04 20:30 | 290 | 290
2018-12-04 21:00 | 278 | 278
2018-12-04 21:30 | 263 | 263
2018-12-04 22:00 | 250 | 250
2018-12-04 22:30 | 243 | 243
2018-12-04 23:00 | 233 | 233
2018-12-04 23:30 | 216 | 216
2018-12-05 | 200 | 199
2018-12-05 00:30 | 185 | 185
2018-12-05 01:00 | 178 | 178
2018-12-05 01:30 | 172 | 172
2018-12-05 02:00 | 168 | 168
2018-12-05 02:30 | 165 | 165
2018-12-05 03:00 | 163 | 163
2018-12-05 03:30 | 163 | 163
2018-12-05 04:00 | 163 | 163
2018-12-05 04:30 | 167 | 167
2018-12-05 05:00 | 171 | 171
2018-12-05 05:30 | 182 | 182
2018-12-05 06:00 | 190 | 190
2018-12-05 06:30 | 203 | 202
2018-12-05 07:00 | 215 | 215
2018-12-05 07:30 | 229 | 228
2018-12-05 08:00 | 232 | 232
2018-12-05 08:30 | 233 | 233
2018-12-05 09:00 | 227 | 227
2018-12-05 09:30 | 234 | 233
2018-12-05 10:00 | 236 | 236
2018-12-05 10:30 | 244 | 243
2018-12-05 11:00 | 249 | 248
2018-12-05 11:30 | 245 | 244
2018-12-05 12:00 | 241 | 241
2018-12-05 12:30 | 252 | 252
2018-12-05 13:00 | 260 | 259
2018-12-05 13:30 | 250 | 249
2018-12-05 14:00 | 247 | 247
2018-12-05 14:30 | 251 | 251
2018-12-05 15:00 | 247 | 247
2018-12-05 15:30 | 241 | 241
2018-12-05 16:00 | 251 | 251
2018-12-05 16:30 | 255 | 255
2018-12-05 17:00 | 263 | 263
2018-12-05 17:30 | 267 | 267
2018-12-05 18:00 | 267 | 267
2018-12-05 18:30 | 267 | 267
2018-12-05 19:00 | 279 | 279
2018-12-05 19:30 | 280 | 280
2018-12-05 20:00 | 277 | 277
2018-12-05 20:30 | 272 | 272
2018-12-05 21:00 | 259 | 259
2018-12-05 21:30 | 244 | 244
2018-12-05 22:00 | 233 | 232
2018-12-05 22:30 | 227 | 226
2018-12-05 23:00 | 222 | 221
2018-12-05 23:30 | 207 | 207
2018-12-06 | 191 | 191
2018-12-06 00:30 | 176 | 176
2018-12-06 01:00 | 167 | 167
2018-12-06 01:30 | 162 | 161
2018-12-06 02:00 | 158 | 158
2018-12-06 02:30 | 156 | 156
2018-12-06 03:00 | 154 | 154
2018-12-06 03:30 | 154 | 154
2018-12-06 04:00 | 156 | 156
2018-12-06 04:30 | 160 | 159
2018-12-06 05:00 | 163 | 163
2018-12-06 05:30 | 174 | 174
2018-12-06 06:00 | 184 | 184
2018-12-06 06:30 | 198 | 197
2018-12-06 07:00 | 210 | 209
2018-12-06 07:30 | 223 | 222
2018-12-06 08:00 | 229 | 228
2018-12-06 08:30 | 225 | 225
2018-12-06 09:00 | 215 | 215
2018-12-06 09:30 | 224 | 224
2018-12-06 10:00 | 223 | 223
2018-12-06 10:30 | 223 | 223
2018-12-06 11:00 | 220 | 220
2018-12-06 11:30 | 208 | 208
2018-12-06 12:00 | 204 | 204
2018-12-06 12:30 | 204 | 204
2018-12-06 13:00 | 202 | 202
2018-12-06 13:30 | 203 | 203
2018-12-06 14:00 | 205 | 205
2018-12-06 14:30 | 210 | 210
2018-12-06 15:00 | 212 | 212
2018-12-06 15:30 | 221 | 221
2018-12-06 16:00 | 234 | 234
2018-12-06 16:30 | 245 | 245
2018-12-06 17:00 | 257 | 257
2018-12-06 17:30 | 261 | 261
2018-12-06 18:00 | 263 | 263
2018-12-06 18:30 | 264 | 264
2018-12-06 19:00 | 274 | 274
2018-12-06 19:30 | 277 | 277
2018-12-06 20:00 | 274 | 274
2018-12-06 20:30 | 276 | 275
2018-12-06 21:00 | 264 | 264
2018-12-06 21:30 | 250 | 250
2018-12-06 22:00 | 237 | 237
2018-12-06 22:30 | 232 | 232
2018-12-06 23:00 | 225 | 224
2018-12-06 23:30 | 210 | 210
2018-12-07 | 194 | 194
2018-12-07 00:30 | 179 | 179
2018-12-07 01:00 | 171 | 171
2018-12-07 01:30 | 166 | 165
2018-12-07 02:00 | 162 | 162
2018-12-07 02:30 | 160 | 160
2018-12-07 03:00 | 159 | 159
2018-12-07 03:30 | 160 | 159
2018-12-07 04:00 | 160 | 159
2018-12-07 04:30 | 162 | 162
2018-12-07 05:00 | 166 | 166
2018-12-07 05:30 | 174 | 174
2018-12-07 06:00 | 182 | 182
2018-12-07 06:30 | 197 | 197
2018-12-07 07:00 | 212 | 211
2018-12-07 07:30 | 219 | 219
2018-12-07 08:00 | 228 | 228
2018-12-07 08:30 | 231 | 231
2018-12-07 09:00 | 231 | 231
2018-12-07 09:30 | 230 | 230
2018-12-07 10:00 | 228 | 228
2018-12-07 10:30 | 236 | 236
2018-12-07 11:00 | 236 | 236
2018-12-07 11:30 | 229 | 229
2018-12-07 12:00 | 227 | 227
2018-12-07 12:30 | 216 | 216
2018-12-07 13:00 | 222 | 222
2018-12-07 13:30 | 234 | 234
2018-12-07 14:00 | 233 | 233
2018-12-07 14:30 | 237 | 237
2018-12-07 15:00 | 236 | 236
2018-12-07 15:30 | 233 | 233
2018-12-07 16:00 | 233 | 233
2018-12-07 16:30 | 234 | 234
2018-12-07 17:00 | 248 | 248
2018-12-07 17:30 | 254 | 254
2018-12-07 18:00 | 252 | 252
2018-12-07 18:30 | 250 | 250
2018-12-07 19:00 | 259 | 259
2018-12-07 19:30 | 261 | 260
2018-12-07 20:00 | 259 | 259
2018-12-07 20:30 | 256 | 256
2018-12-07 21:00 | 247 | 247
2018-12-07 21:30 | 239 | 239
2018-12-07 22:00 | 230 | 229
2018-12-07 22:30 | 226 | 225
2018-12-07 23:00 | 222 | 222
2018-12-07 23:30 | 209 | 209
2018-12-08 | 194 | 194
2018-12-08 00:30 | 180 | 180
2018-12-08 01:00 | 171 | 171
2018-12-08 01:30 | 165 | 165
2018-12-08 02:00 | 160 | 160
2018-12-08 02:30 | 158 | 158
2018-12-08 03:00 | 157 | 156
2018-12-08 03:30 | 155 | 155
2018-12-08 04:00 | 156 | 155
2018-12-08 04:30 | 156 | 156
2018-12-08 05:00 | 157 | 157
2018-12-08 05:30 | 159 | 159
2018-12-08 06:00 | 163 | 163
2018-12-08 06:30 | 172 | 172
2018-12-08 07:00 | 179 | 179
2018-12-08 07:30 | 186 | 186
2018-12-08 08:00 | 192 | 191
2018-12-08 08:30 | 194 | 194
2018-12-08 09:00 | 195 | 195
2018-12-08 09:30 | 196 | 195
2018-12-08 10:00 | 192 | 192
2018-12-08 10:30 | 194 | 194
2018-12-08 11:00 | 200 | 199
2018-12-08 11:30 | 204 | 203
2018-12-08 12:00 | 203 | 203
2018-12-08 12:30 | 204 | 204
2018-12-08 13:00 | 209 | 208
2018-12-08 13:30 | 211 | 211
2018-12-08 14:00 | 205 | 205
2018-12-08 14:30 | 199 | 199
2018-12-08 15:00 | 198 | 197
2018-12-08 15:30 | 199 | 199
2018-12-08 16:00 | 198 | 197
2018-12-08 16:30 | 199 | 199
2018-12-08 17:00 | 207 | 207
2018-12-08 17:30 | 210 | 210
2018-12-08 18:00 | 212 | 212
2018-12-08 18:30 | 219 | 219
2018-12-08 19:00 | 230 | 230
2018-12-08 19:30 | 233 | 233
2018-12-08 20:00 | 231 | 231
2018-12-08 20:30 | 229 | 228
2018-12-08 21:00 | 220 | 220
2018-12-08 21:30 | 213 | 213
2018-12-08 22:00 | 208 | 208
2018-12-08 22:30 | 207 | 207
2018-12-08 23:00 | 207 | 207
2018-12-08 23:30 | 195 | 195
2018-12-09 | 181 | 181
2018-12-09 00:30 | 167 | 167
2018-12-09 01:00 | 159 | 159
2018-12-09 01:30 | 155 | 155
2018-12-09 02:00 | 150 | 149
2018-12-09 02:30 | 148 | 147
2018-12-09 03:00 | 146 | 146
2018-12-09 03:30 | 145 | 144
2018-12-09 04:00 | 144 | 143
2018-12-09 04:30 | 144 | 143
2018-12-09 05:00 | 141 | 140
2018-12-09 05:30 | 142 | 142
2018-12-09 06:00 | 140 | 140
2018-12-09 06:30 | 140 | 140
2018-12-09 07:00 | 141 | 141
2018-12-09 07:30 | 145 | 145
2018-12-09 08:00 | 147 | 147
2018-12-09 08:30 | 159 | 158
2018-12-09 09:00 | 159 | 159
2018-12-09 09:30 | 158 | 157
2018-12-09 10:00 | 157 | 157
2018-12-09 10:30 | 155 | 155
2018-12-09 11:00 | 157 | 157
2018-12-09 11:30 | 154 | 154
2018-12-09 12:00 | 161 | 161
2018-12-09 12:30 | 175 | 174
2018-12-09 13:00 | 173 | 173
2018-12-09 13:30 | 174 | 174
2018-12-09 14:00 | 180 | 180
2018-12-09 14:30 | 185 | 184
2018-12-09 15:00 | 186 | 185
2018-12-09 15:30 | 190 | 190
2018-12-09 16:00 | 200 | 200
2018-12-09 16:30 | 212 | 212
2018-12-09 17:00 | 222 | 221
2018-12-09 17:30 | 233 | 233
2018-12-09 18:00 | 238 | 238
2018-12-09 18:30 | 243 | 243
2018-12-09 19:00 | 252 | 252
2018-12-09 19:30 | 256 | 256
2018-12-09 20:00 | 254 | 254
2018-12-09 20:30 | 249 | 249
2018-12-09 21:00 | 238 | 238
2018-12-09 21:30 | 230 | 230
2018-12-09 22:00 | 219 | 218
2018-12-09 22:30 | 215 | 215
2018-12-09 23:00 | 213 | 213
2018-12-09 23:30 | 200 | 200
2018-12-10 | 184 | 184
2018-12-10 00:30 | 171 | 171
2018-12-10 01:00 | 164 | 164
2018-12-10 01:30 | 159 | 159
2018-12-10 02:00 | 155 | 155
2018-12-10 02:30 | 154 | 153
2018-12-10 03:00 | 153 | 152
2018-12-10 03:30 | 152 | 152
2018-12-10 04:00 | 152 | 152
2018-12-10 04:30 | 157 | 157
2018-12-10 05:00 | 161 | 161
2018-12-10 05:30 | 171 | 171
2018-12-10 06:00 | 181 | 181
2018-12-10 06:30 | 198 | 198
2018-12-10 07:00 | 212 | 212
2018-12-10 07:30 | 225 | 225
2018-12-10 08:00 | 233 | 233
2018-12-10 08:30 | 236 | 236
2018-12-10 09:00 | 235 | 235
2018-12-10 09:30 | 233 | 233
2018-12-10 10:00 | 232 | 232
2018-12-10 10:30 | 236 | 236
2018-12-10 11:00 | 239 | 239
2018-12-10 11:30 | 240 | 240
2018-12-10 12:00 | 242 | 242
2018-12-10 12:30 | 246 | 246
2018-12-10 13:00 | 245 | 245
2018-12-10 13:30 | 251 | 251
2018-12-10 14:00 | 259 | 259
2018-12-10 14:30 | 265 | 265
2018-12-10 15:00 | 267 | 267
2018-12-10 15:30 | 292 | 292
2018-12-10 16:00 | 297 | 297
2018-12-10 16:30 | 295 | 294
2018-12-10 17:00 | 305 | 305
2018-12-10 17:30 | 310 | 310
2018-12-10 18:00 | 306 | 306
2018-12-10 18:30 | 304 | 304
2018-12-10 19:00 | 308 | 308
2018-12-10 19:30 | 308 | 308
2018-12-10 20:00 | 303 | 303
2018-12-10 20:30 | 295 | 295
2018-12-10 21:00 | 280 | 280
2018-12-10 21:30 | 266 | 266
2018-12-10 22:00 | 253 | 253
2018-12-10 22:30 | 241 | 241
2018-12-10 23:00 | 235 | 234
2018-12-10 23:30 | 219 | 219
2018-12-11 | 200 | 200
2018-12-11 00:30 | 185 | 185
2018-12-11 01:00 | 176 | 176
2018-12-11 01:30 | 170 | 170
2018-12-11 02:00 | 166 | 166
2018-12-11 02:30 | 163 | 163
2018-12-11 03:00 | 162 | 162
2018-12-11 03:30 | 161 | 161
2018-12-11 04:00 | 162 | 162
2018-12-11 04:30 | 166 | 166
2018-12-11 05:00 | 169 | 169
2018-12-11 05:30 | 177 | 177
2018-12-11 06:00 | 185 | 185
2018-12-11 06:30 | 200 | 200
2018-12-11 07:00 | 213 | 213
2018-12-11 07:30 | 225 | 225
2018-12-11 08:00 | 230 | 230
2018-12-11 08:30 | 234 | 233
2018-12-11 09:00 | 235 | 234
2018-12-11 09:30 | 237 | 236
2018-12-11 10:00 | 235 | 235
2018-12-11 10:30 | 235 | 234
2018-12-11 11:00 | 237 | 237
2018-12-11 11:30 | 243 | 243
2018-12-11 12:00 | 241 | 240
2018-12-11 12:30 | 249 | 248
2018-12-11 13:00 | 249 | 248
2018-12-11 13:30 | 258 | 257
2018-12-11 14:00 | 260 | 259
2018-12-11 14:30 | 274 | 273
2018-12-11 15:00 | 268 | 267
2018-12-11 15:30 | 277 | 276
2018-12-11 16:00 | 298 | 296
2018-12-11 16:30 | 316 | 314
2018-12-11 17:00 | 312 | 311
2018-12-11 17:30 | 303 | 302
2018-12-11 18:00 | 305 | 305
2018-12-11 18:30 | 302 | 302
2018-12-11 19:00 | 309 | 309
2018-12-11 19:30 | 310 | 309
2018-12-11 20:00 | 306 | 306
2018-12-11 20:30 | 298 | 297
2018-12-11 21:00 | 283 | 283
2018-12-11 21:30 | 270 | 270
2018-12-11 22:00 | 254 | 254
2018-12-11 22:30 | 246 | 245
2018-12-11 23:00 | 238 | 237
2018-12-11 23:30 | 222 | 221
2018-12-12 | 202 | 202
2018-12-12 00:30 | 186 | 186
2018-12-12 01:00 | 177 | 177
2018-12-12 01:30 | 171 | 171
2018-12-12 02:00 | 167 | 167
2018-12-12 02:30 | 165 | 164
2018-12-12 03:00 | 164 | 164
2018-12-12 03:30 | 164 | 164
2018-12-12 04:00 | 163 | 163
2018-12-12 04:30 | 167 | 167
2018-12-12 05:00 | 170 | 170
2018-12-12 05:30 | 180 | 180
2018-12-12 06:00 | 188 | 187
2018-12-12 06:30 | 203 | 202
2018-12-12 07:00 | 213 | 212
2018-12-12 07:30 | 228 | 228
2018-12-12 08:00 | 232 | 231
2018-12-12 08:30 | 236 | 235
2018-12-12 09:00 | 236 | 235
2018-12-12 09:30 | 233 | 233
2018-12-12 10:00 | 234 | 234
2018-12-12 10:30 | 236 | 236
2018-12-12 11:00 | 235 | 235
2018-12-12 11:30 | 232 | 232
2018-12-12 12:00 | 233 | 233
2018-12-12 12:30 | 238 | 238
2018-12-12 13:00 | 242 | 242
2018-12-12 13:30 | 245 | 245
2018-12-12 14:00 | 249 | 249
2018-12-12 14:30 | 257 | 257
2018-12-12 15:00 | 265 | 265
2018-12-12 15:30 | 278 | 278
2018-12-12 16:00 | 291 | 291
2018-12-12 16:30 | 303 | 303
2018-12-12 17:00 | 313 | 313
2018-12-12 17:30 | 316 | 316
2018-12-12 18:00 | 311 | 311
2018-12-12 18:30 | 303 | 303
2018-12-12 19:00 | 310 | 310
2018-12-12 19:30 | 308 | 308
2018-12-12 20:00 | 305 | 305
2018-12-12 20:30 | 299 | 299
2018-12-12 21:00 | 287 | 287
2018-12-12 21:30 | 273 | 273
2018-12-12 22:00 | 260 | 259
2018-12-12 22:30 | 252 | 251
2018-12-12 23:00 | 243 | 243
2018-12-12 23:30 | 224 | 224
2018-12-13 | 204 | 204
2018-12-13 00:30 | 189 | 189
2018-12-13 01:00 | 180 | 180
2018-12-13 01:30 | 173 | 173
2018-12-13 02:00 | 171 | 171
2018-12-13 02:30 | 169 | 169
2018-12-13 03:00 | 167 | 167
2018-12-13 03:30 | 167 | 167
2018-12-13 04:00 | 166 | 166
2018-12-13 04:30 | 170 | 170
2018-12-13 05:00 | 173 | 173
2018-12-13 05:30 | 181 | 181
2018-12-13 06:00 | 190 | 190
2018-12-13 06:30 | 207 | 206
2018-12-13 07:00 | 220 | 219
2018-12-13 07:30 | 232 | 232
2018-12-13 08:00 | 238 | 238
2018-12-13 08:30 | 240 | 239
2018-12-13 09:00 | 233 | 232
2018-12-13 09:30 | 232 | 232
2018-12-13 10:00 | 240 | 239
2018-12-13 10:30 | 243 | 243
2018-12-13 11:00 | 240 | 240
2018-12-13 11:30 | 231 | 231
2018-12-13 12:00 | 239 | 238
2018-12-13 12:30 | 249 | 248
2018-12-13 13:00 | 265 | 265
2018-12-13 13:30 | 275 | 275
2018-12-13 14:00 | 279 | 279
2018-12-13 14:30 | 281 | 281
2018-12-13 15:00 | 279 | 279
2018-12-13 15:30 | 290 | 290
2018-12-13 16:00 | 303 | 303
2018-12-13 16:30 | 316 | 315
2018-12-13 17:00 | 326 | 325
2018-12-13 17:30 | 319 | 319
2018-12-13 18:00 | 319 | 319
2018-12-13 18:30 | 317 | 317
2018-12-13 19:00 | 325 | 324
2018-12-13 19:30 | 323 | 323
2018-12-13 20:00 | 318 | 318
2018-12-13 20:30 | 311 | 311
2018-12-13 21:00 | 299 | 299
2018-12-13 21:30 | 283 | 283
2018-12-13 22:00 | 269 | 269
2018-12-13 22:30 | 262 | 262
2018-12-13 23:00 | 255 | 255
2018-12-13 23:30 | 238 | 238
2018-12-14 | 218 | 217
2018-12-14 00:30 | 202 | 201
2018-12-14 01:00 | 193 | 193
2018-12-14 01:30 | 188 | 188
2018-12-14 02:00 | 184 | 184
2018-12-14 02:30 | 181 | 181
2018-12-14 03:00 | 177 | 177
2018-12-14 03:30 | 177 | 176
2018-12-14 04:00 | 177 | 176
2018-12-14 04:30 | 179 | 179
2018-12-14 05:00 | 184 | 183
2018-12-14 05:30 | 192 | 192
2018-12-14 06:00 | 202 | 201
2018-12-14 06:30 | 223 | 223
2018-12-14 07:00 | 242 | 242
2018-12-14 07:30 | 265 | 265
2018-12-14 08:00 | 279 | 279
2018-12-14 08:30 | 292 | 292
2018-12-14 09:00 | 291 | 291
2018-12-14 09:30 | 279 | 279
2018-12-14 10:00 | 271 | 271
2018-12-14 10:30 | 259 | 259
2018-12-14 11:00 | 249 | 249
2018-12-14 11:30 | 242 | 242
2018-12-14 12:00 | 250 | 250
2018-12-14 12:30 | 259 | 258
2018-12-14 13:00 | 263 | 263
2018-12-14 13:30 | 281 | 281
2018-12-14 14:00 | 295 | 295
2018-12-14 14:30 | 299 | 299
2018-12-14 15:00 | 301 | 301
2018-12-14 15:30 | 308 | 308
2018-12-14 16:00 | 327 | 326
2018-12-14 16:30 | 330 | 329
2018-12-14 17:00 | 327 | 327
2018-12-14 17:30 | 317 | 317
2018-12-14 18:00 | 304 | 304
2018-12-14 18:30 | 307 | 307
2018-12-14 19:00 | 313 | 312
2018-12-14 19:30 | 312 | 311
2018-12-14 20:00 | 310 | 309
2018-12-14 20:30 | 303 | 303
2018-12-14 21:00 | 290 | 290
2018-12-14 21:30 | 278 | 278
2018-12-14 22:00 | 266 | 266
2018-12-14 22:30 | 258 | 258
2018-12-14 23:00 | 252 | 251
2018-12-14 23:30 | 237 | 237
2018-12-15 | 218 | 218
2018-12-15 00:30 | 201 | 201
2018-12-15 01:00 | 193 | 192
2018-12-15 01:30 | 186 | 185
2018-12-15 02:00 | 180 | 179
2018-12-15 02:30 | 175 | 175
2018-12-15 03:00 | 172 | 172
2018-12-15 03:30 | 171 | 171
2018-12-15 04:00 | 171 | 170
2018-12-15 04:30 | 171 | 170
2018-12-15 05:00 | 171 | 171
2018-12-15 05:30 | 172 | 171
2018-12-15 06:00 | 176 | 175
2018-12-15 06:30 | 180 | 180
2018-12-15 07:00 | 185 | 185
2018-12-15 07:30 | 198 | 196
2018-12-15 08:00 | 203 | 202
2018-12-15 08:30 | 210 | 210
2018-12-15 09:00 | 209 | 209
2018-12-15 09:30 | 206 | 206
2018-12-15 10:00 | 208 | 207
2018-12-15 10:30 | 215 | 215
2018-12-15 11:00 | 225 | 225
2018-12-15 11:30 | 239 | 239
2018-12-15 12:00 | 244 | 243
2018-12-15 12:30 | 238 | 238
2018-12-15 13:00 | 245 | 244
2018-12-15 13:30 | 249 | 249
2018-12-15 14:00 | 252 | 251
2018-12-15 14:30 | 256 | 255
2018-12-15 15:00 | 269 | 268
2018-12-15 15:30 | 272 | 272
2018-12-15 16:00 | 276 | 276
2018-12-15 16:30 | 284 | 284
2018-12-15 17:00 | 296 | 296
2018-12-15 17:30 | 299 | 299
2018-12-15 18:00 | 295 | 295
2018-12-15 18:30 | 294 | 294
2018-12-15 19:00 | 295 | 294
2018-12-15 19:30 | 291 | 290
2018-12-15 20:00 | 287 | 285
2018-12-15 20:30 | 280 | 278
2018-12-15 21:00 | 267 | 266
2018-12-15 21:30 | 259 | 259
2018-12-15 22:00 | 251 | 251
2018-12-15 22:30 | 247 | 247
2018-12-15 23:00 | 243 | 243
2018-12-15 23:30 | 226 | 226
2018-12-16 | 210 | 210
2018-12-16 00:30 | 195 | 195
2018-12-16 01:00 | 185 | 185
2018-12-16 01:30 | 180 | 180
2018-12-16 02:00 | 175 | 175
2018-12-16 02:30 | 171 | 171
2018-12-16 03:00 | 168 | 168
2018-12-16 03:30 | 167 | 167
2018-12-16 04:00 | 166 | 166
2018-12-16 04:30 | 165 | 165
2018-12-16 05:00 | 165 | 165
2018-12-16 05:30 | 165 | 165
2018-12-16 06:00 | 168 | 168
2018-12-16 06:30 | 174 | 174
2018-12-16 07:00 | 179 | 179
2018-12-16 07:30 | 191 | 191
2018-12-16 08:00 | 203 | 202
2018-12-16 08:30 | 214 | 213
2018-12-16 09:00 | 219 | 217
2018-12-16 09:30 | 232 | 230
2018-12-16 10:00 | 240 | 238
2018-12-16 10:30 | 239 | 238
2018-12-16 11:00 | 237 | 236
2018-12-16 11:30 | 233 | 233
2018-12-16 12:00 | 227 | 227
2018-12-16 12:30 | 228 | 228
2018-12-16 13:00 | 226 | 226
2018-12-16 13:30 | 223 | 223
2018-12-16 14:00 | 220 | 220
2018-12-16 14:30 | 223 | 223
2018-12-16 15:00 | 229 | 228
2018-12-16 15:30 | 234 | 234
2018-12-16 16:00 | 239 | 239
2018-12-16 16:30 | 243 | 243
2018-12-16 17:00 | 246 | 245
2018-12-16 17:30 | 252 | 252
2018-12-16 18:00 | 256 | 255
2018-12-16 18:30 | 258 | 257
2018-12-16 19:00 | 262 | 261
2018-12-16 19:30 | 254 | 253
2018-12-16 20:00 | 253 | 252
2018-12-16 20:30 | 249 | 248
2018-12-16 21:00 | 238 | 238
2018-12-16 21:30 | 229 | 229
2018-12-16 22:00 | 219 | 219
2018-12-16 22:30 | 216 | 216
2018-12-16 23:00 | 214 | 214
2018-12-16 23:30 | 201 | 201
2018-12-17 | 186 | 186
2018-12-17 00:30 | 173 | 173
2018-12-17 01:00 | 166 | 166
2018-12-17 01:30 | 162 | 162
2018-12-17 02:00 | 162 | 162
2018-12-17 02:30 | 156 | 156
2018-12-17 03:00 | 155 | 155
2018-12-17 03:30 | 154 | 154
2018-12-17 04:00 | 155 | 155
2018-12-17 04:30 | 159 | 159
2018-12-17 05:00 | 165 | 165
2018-12-17 05:30 | 175 | 175
2018-12-17 06:00 | 185 | 185
2018-12-17 06:30 | 203 | 202
2018-12-17 07:00 | 214 | 213
2018-12-17 07:30 | 228 | 228
2018-12-17 08:00 | 242 | 242
2018-12-17 08:30 | 255 | 255
2018-12-17 09:00 | 258 | 257
2018-12-17 09:30 | 261 | 260
2018-12-17 10:00 | 260 | 259
2018-12-17 10:30 | 248 | 248
2018-12-17 11:00 | 249 | 249
2018-12-17 11:30 | 256 | 255
2018-12-17 12:00 | 258 | 258
2018-12-17 12:30 | 263 | 262
2018-12-17 13:00 | 267 | 267
2018-12-17 13:30 | 260 | 260
2018-12-17 14:00 | 264 | 264
2018-12-17 14:30 | 270 | 270
2018-12-17 15:00 | 275 | 275
2018-12-17 15:30 | 277 | 277
2018-12-17 16:00 | 281 | 281
2018-12-17 16:30 | 284 | 284
2018-12-17 17:00 | 286 | 285
2018-12-17 17:30 | 287 | 286
2018-12-17 18:00 | 284 | 283
2018-12-17 18:30 | 283 | 283
2018-12-17 19:00 | 290 | 290
2018-12-17 19:30 | 291 | 291
2018-12-17 20:00 | 289 | 289
2018-12-17 20:30 | 283 | 283
2018-12-17 21:00 | 269 | 269
2018-12-17 21:30 | 253 | 253
2018-12-17 22:00 | 242 | 242
2018-12-17 22:30 | 237 | 237
2018-12-17 23:00 | 231 | 231
2018-12-17 23:30 | 216 | 216
2018-12-18 | 199 | 198
2018-12-18 00:30 | 186 | 185
2018-12-18 01:00 | 175 | 175
2018-12-18 01:30 | 171 | 170
2018-12-18 02:00 | 168 | 167
2018-12-18 02:30 | 165 | 164
2018-12-18 03:00 | 164 | 163
2018-12-18 03:30 | 164 | 163
2018-12-18 04:00 | 165 | 164
2018-12-18 04:30 | 168 | 167
2018-12-18 05:00 | 172 | 171
2018-12-18 05:30 | 182 | 181
2018-12-18 06:00 | 189 | 188
2018-12-18 06:30 | 203 | 201
2018-12-18 07:00 | 214 | 213
2018-12-18 07:30 | 226 | 224
2018-12-18 08:00 | 236 | 233
2018-12-18 08:30 | 246 | 243
2018-12-18 09:00 | 247 | 246
2018-12-18 09:30 | 245 | 244
2018-12-18 10:00 | 242 | 241
2018-12-18 10:30 | 243 | 242
2018-12-18 11:00 | 241 | 240
2018-12-18 11:30 | 245 | 244
2018-12-18 12:00 | 251 | 250
2018-12-18 12:30 | 257 | 257
2018-12-18 13:00 | 267 | 267
2018-12-18 13:30 | 269 | 269
2018-12-18 14:00 | 276 | 276
2018-12-18 14:30 | 280 | 280
2018-12-18 15:00 | 283 | 283
2018-12-18 15:30 | 288 | 288
2018-12-18 16:00 | 295 | 295
2018-12-18 16:30 | 304 | 304
2018-12-18 17:00 | 317 | 317
2018-12-18 17:30 | 321 | 320
2018-12-18 18:00 | 319 | 319
2018-12-18 18:30 | 314 | 313
2018-12-18 19:00 | 318 | 317
2018-12-18 19:30 | 320 | 319
2018-12-18 20:00 | 315 | 315
2018-12-18 20:30 | 307 | 307
2018-12-18 21:00 | 295 | 294
2018-12-18 21:30 | 281 | 281
2018-12-18 22:00 | 269 | 268
2018-12-18 22:30 | 257 | 257
2018-12-18 23:00 | 251 | 251
2018-12-18 23:30 | 236 | 236
2018-12-19 | 215 | 215
2018-12-19 00:30 | 199 | 198
2018-12-19 01:00 | 189 | 189
2018-12-19 01:30 | 183 | 183
2018-12-19 02:00 | 180 | 180
2018-12-19 02:30 | 178 | 178
2018-12-19 03:00 | 176 | 176
2018-12-19 03:30 | 175 | 175
2018-12-19 04:00 | 173 | 173
2018-12-19 04:30 | 176 | 176
2018-12-19 05:00 | 179 | 179
2018-12-19 05:30 | 187 | 187
2018-12-19 06:00 | 194 | 194
2018-12-19 06:30 | 210 | 210
2018-12-19 07:00 | 225 | 225
2018-12-19 07:30 | 239 | 239
2018-12-19 08:00 | 246 | 246
2018-12-19 08:30 | 253 | 253
2018-12-19 09:00 | 255 | 254
2018-12-19 09:30 | 253 | 253
2018-12-19 10:00 | 253 | 253
2018-12-19 10:30 | 259 | 258
2018-12-19 11:00 | 261 | 260
2018-12-19 11:30 | 266 | 265
2018-12-19 12:00 | 269 | 268
2018-12-19 12:30 | 275 | 274
2018-12-19 13:00 | 279 | 278
2018-12-19 13:30 | 284 | 283
2018-12-19 14:00 | 292 | 291
2018-12-19 14:30 | 300 | 299
2018-12-19 15:00 | 309 | 308
2018-12-19 15:30 | 316 | 316
2018-12-19 16:00 | 326 | 325
2018-12-19 16:30 | 332 | 332
2018-12-19 17:00 | 342 | 342
2018-12-19 17:30 | 342 | 342
2018-12-19 18:00 | 340 | 340
2018-12-19 18:30 | 335 | 335
2018-12-19 19:00 | 337 | 337
2018-12-19 19:30 | 336 | 336
2018-12-19 20:00 | 331 | 331
2018-12-19 20:30 | 322 | 322
2018-12-19 21:00 | 307 | 307
2018-12-19 21:30 | 291 | 291
2018-12-19 22:00 | 276 | 276
2018-12-19 22:30 | 263 | 262
2018-12-19 23:00 | 255 | 254
2018-12-19 23:30 | 236 | 235
2018-12-20 | 217 | 216
2018-12-20 00:30 | 199 | 199
2018-12-20 01:00 | 190 | 190
2018-12-20 01:30 | 183 | 183
2018-12-20 02:00 | 180 | 180
2018-12-20 02:30 | 177 | 177
2018-12-20 03:00 | 176 | 176
2018-12-20 03:30 | 176 | 176
2018-12-20 04:00 | 176 | 176
2018-12-20 04:30 | 178 | 178
2018-12-20 05:00 | 181 | 181
2018-12-20 05:30 | 189 | 189
2018-12-20 06:00 | 199 | 198
2018-12-20 06:30 | 215 | 214
2018-12-20 07:00 | 232 | 232
2018-12-20 07:30 | 242 | 242
2018-12-20 08:00 | 253 | 252
2018-12-20 08:30 | 257 | 256
2018-12-20 09:00 | 258 | 256
2018-12-20 09:30 | 258 | 257
2018-12-20 10:00 | 259 | 259
2018-12-20 10:30 | 263 | 262
2018-12-20 11:00 | 269 | 268
2018-12-20 11:30 | 276 | 275
2018-12-20 12:00 | 288 | 286
2018-12-20 12:30 | 297 | 295
2018-12-20 13:00 | 305 | 303
2018-12-20 13:30 | 319 | 318
2018-12-20 14:00 | 330 | 330
2018-12-20 14:30 | 340 | 340
2018-12-20 15:00 | 353 | 352
2018-12-20 15:30 | 367 | 366
2018-12-20 16:00 | 382 | 381
2018-12-20 16:30 | 393 | 392
2018-12-20 17:00 | 403 | 402
2018-12-20 17:30 | 400 | 400
2018-12-20 18:00 | 394 | 394
2018-12-20 18:30 | 386 | 386
2018-12-20 19:00 | 383 | 382
2018-12-20 19:30 | 378 | 378
2018-12-20 20:00 | 370 | 370
2018-12-20 20:30 | 360 | 360
2018-12-20 21:00 | 342 | 342
2018-12-20 21:30 | 327 | 326
2018-12-20 22:00 | 311 | 310
2018-12-20 22:30 | 297 | 297
2018-12-20 23:00 | 287 | 287
2018-12-20 23:30 | 263 | 263
2018-12-21 | 242 | 242
2018-12-21 00:30 | 223 | 223
2018-12-21 01:00 | 211 | 211
2018-12-21 01:30 | 204 | 204
2018-12-21 02:00 | 199 | 199
2018-12-21 02:30 | 196 | 196
2018-12-21 03:00 | 197 | 197
2018-12-21 03:30 | 198 | 198
2018-12-21 04:00 | 193 | 193
2018-12-21 04:30 | 191 | 191
2018-12-21 05:00 | 192 | 192
2018-12-21 05:30 | 199 | 199
2018-12-21 06:00 | 208 | 207
2018-12-21 06:30 | 226 | 225
2018-12-21 07:00 | 239 | 238
2018-12-21 07:30 | 246 | 246
2018-12-21 08:00 | 190 | 190
2018-12-21 08:30 | 198 | 197
2018-12-21 09:00 | 210 | 209
2018-12-21 09:30 | 211 | 210
2018-12-21 10:00 | 208 | 207
2018-12-21 10:30 | 214 | 212
2018-12-21 11:00 | 306 | 304
2018-12-21 11:30 | 323 | 321
2018-12-21 12:00 | 331 | 330
2018-12-21 12:30 | 339 | 339
2018-12-21 13:00 | 347 | 347
2018-12-21 13:30 | 356 | 356
2018-12-21 14:00 | 366 | 366
2018-12-21 14:30 | 379 | 379
2018-12-21 15:00 | 394 | 394
2018-12-21 15:30 | 408 | 408
2018-12-21 16:00 | 430 | 429
2018-12-21 16:30 | 445 | 443
2018-12-21 17:00 | 443 | 442
2018-12-21 17:30 | 419 | 419
2018-12-21 18:00 | 371 | 371
2018-12-21 18:30 | 331 | 331
2018-12-21 19:00 | 316 | 316
2018-12-21 19:30 | 307 | 307
2018-12-21 20:00 | 296 | 296
2018-12-21 20:30 | 299 | 299
2018-12-21 21:00 | 294 | 294
2018-12-21 21:30 | 276 | 276
2018-12-21 22:00 | 263 | 263
2018-12-21 22:30 | 243 | 243
2018-12-21 23:00 | 242 | 242
2018-12-21 23:30 | 233 | 233
2018-12-22 | 221 | 221
2018-12-22 00:30 | 211 | 211
2018-12-22 01:00 | 207 | 206
2018-12-22 01:30 | 195 | 195
2018-12-22 02:00 | 188 | 188
2018-12-22 02:30 | 184 | 184
2018-12-22 03:00 | 180 | 180
2018-12-22 03:30 | 176 | 176
2018-12-22 04:00 | 175 | 175
2018-12-22 04:30 | 175 | 175
2018-12-22 05:00 | 176 | 176
2018-12-22 05:30 | 176 | 176
2018-12-22 06:00 | 178 | 178
2018-12-22 06:30 | 185 | 185
2018-12-22 07:00 | 194 | 194
2018-12-22 07:30 | 201 | 200
2018-12-22 08:00 | 199 | 198
2018-12-22 08:30 | 209 | 209
2018-12-22 09:00 | 222 | 222
2018-12-22 09:30 | 234 | 234
2018-12-22 10:00 | 227 | 227
2018-12-22 10:30 | 224 | 224
2018-12-22 11:00 | 226 | 225
2018-12-22 11:30 | 232 | 232
2018-12-22 12:00 | 245 | 244
2018-12-22 12:30 | 259 | 258
2018-12-22 13:00 | 279 | 279
2018-12-22 13:30 | 294 | 292
2018-12-22 14:00 | 305 | 304
2018-12-22 14:30 | 317 | 317
2018-12-22 15:00 | 329 | 329
2018-12-22 15:30 | 341 | 341
2018-12-22 16:00 | 356 | 356
2018-12-22 16:30 | 356 | 356
2018-12-22 17:00 | 344 | 344
2018-12-22 17:30 | 317 | 317
2018-12-22 18:00 | 291 | 291
2018-12-22 18:30 | 280 | 280
2018-12-22 19:00 | 278 | 278
2018-12-22 19:30 | 275 | 275
2018-12-22 20:00 | 271 | 271
2018-12-22 20:30 | 263 | 263
2018-12-22 21:00 | 250 | 250
2018-12-22 21:30 | 240 | 240
2018-12-22 22:00 | 230 | 230
2018-12-22 22:30 | 227 | 227
2018-12-22 23:00 | 222 | 222
2018-12-22 23:30 | 207 | 207
2018-12-23 | 190 | 190
2018-12-23 00:30 | 178 | 178
2018-12-23 01:00 | 171 | 170
2018-12-23 01:30 | 166 | 165
2018-12-23 02:00 | 162 | 161
2018-12-23 02:30 | 160 | 159
2018-12-23 03:00 | 158 | 157
2018-12-23 03:30 | 157 | 156
2018-12-23 04:00 | 156 | 154
2018-12-23 04:30 | 155 | 153
2018-12-23 05:00 | 153 | 151
2018-12-23 05:30 | 152 | 149
2018-12-23 06:00 | 151 | 148
2018-12-23 06:30 | 150 | 148
2018-12-23 07:00 | 148 | 146
2018-12-23 07:30 | 149 | 147
2018-12-23 08:00 | 148 | 147
2018-12-23 08:30 | 148 | 148
2018-12-23 09:00 | 151 | 151
2018-12-23 09:30 | 153 | 153
2018-12-23 10:00 | 154 | 154
2018-12-23 10:30 | 155 | 155
2018-12-23 11:00 | 161 | 161
2018-12-23 11:30 | 165 | 164
2018-12-23 12:00 | 163 | 163
2018-12-23 12:30 | 163 | 163
2018-12-23 13:00 | 165 | 164
2018-12-23 13:30 | 164 | 164
2018-12-23 14:00 | 164 | 164
2018-12-23 14:30 | 168 | 168
2018-12-23 15:00 | 176 | 176
2018-12-23 15:30 | 181 | 181
2018-12-23 16:00 | 191 | 191
2018-12-23 16:30 | 204 | 204
2018-12-23 17:00 | 216 | 216
2018-12-23 17:30 | 224 | 224
2018-12-23 18:00 | 229 | 229
2018-12-23 18:30 | 232 | 232
2018-12-23 19:00 | 239 | 239
2018-12-23 19:30 | 244 | 244
2018-12-23 20:00 | 244 | 243
2018-12-23 20:30 | 240 | 239
2018-12-23 21:00 | 230 | 229
2018-12-23 21:30 | 222 | 222
2018-12-23 22:00 | 215 | 215
2018-12-23 22:30 | 213 | 213
2018-12-23 23:00 | 210 | 210
2018-12-23 23:30 | 198 | 198
2018-12-24 | 183 | 183
2018-12-24 00:30 | 170 | 170
2018-12-24 01:00 | 163 | 163
2018-12-24 01:30 | 158 | 158
2018-12-24 02:00 | 155 | 155
2018-12-24 02:30 | 152 | 152
2018-12-24 03:00 | 150 | 149
2018-12-24 03:30 | 148 | 148
2018-12-24 04:00 | 148 | 148
2018-12-24 04:30 | 151 | 151
2018-12-24 05:00 | 152 | 152
2018-12-24 05:30 | 156 | 156
2018-12-24 06:00 | 159 | 159
2018-12-24 06:30 | 167 | 167
2018-12-24 07:00 | 168 | 168
2018-12-24 07:30 | 173 | 173
2018-12-24 08:00 | 178 | 178
2018-12-24 08:30 | 180 | 179
2018-12-24 09:00 | 188 | 187
2018-12-24 09:30 | 194 | 194
2018-12-24 10:00 | 194 | 194
2018-12-24 10:30 | 195 | 195
2018-12-24 11:00 | 196 | 196
2018-12-24 11:30 | 196 | 196
2018-12-24 12:00 | 188 | 188
2018-12-24 12:30 | 181 | 181
2018-12-24 13:00 | 179 | 179
2018-12-24 13:30 | 182 | 182
2018-12-24 14:00 | 183 | 183
2018-12-24 14:30 | 186 | 186
2018-12-24 15:00 | 193 | 193
2018-12-24 15:30 | 202 | 202
2018-12-24 16:00 | 216 | 216
2018-12-24 16:30 | 229 | 229
2018-12-24 17:00 | 243 | 242
2018-12-24 17:30 | 248 | 248
2018-12-24 18:00 | 246 | 246
2018-12-24 18:30 | 242 | 241
2018-12-24 19:00 | 244 | 244
2018-12-24 19:30 | 245 | 245
2018-12-24 20:00 | 244 | 244
2018-12-24 20:30 | 240 | 240
2018-12-24 21:00 | 230 | 230
2018-12-24 21:30 | 223 | 223
2018-12-24 22:00 | 218 | 218
2018-12-24 22:30 | 214 | 214
2018-12-24 23:00 | 211 | 211
2018-12-24 23:30 | 198 | 198
2018-12-25 | 181 | 181
2018-12-25 00:30 | 166 | 165
2018-12-25 01:00 | 154 | 152
2018-12-25 01:30 | 147 | 144
2018-12-25 02:00 | 142 | 139
2018-12-25 02:30 | 139 | 136
2018-12-25 03:00 | 134 | 133
2018-12-25 03:30 | 133 | 131
2018-12-25 04:00 | 132 | 131
2018-12-25 04:30 | 131 | 131
2018-12-25 05:00 | 130 | 129
2018-12-25 05:30 | 133 | 133
2018-12-25 06:00 | 133 | 132
2018-12-25 06:30 | 134 | 133
2018-12-25 07:00 | 131 | 131
2018-12-25 07:30 | 131 | 131
2018-12-25 08:00 | 128 | 128
2018-12-25 08:30 | 129 | 129
2018-12-25 09:00 | 133 | 133
2018-12-25 09:30 | 137 | 137
2018-12-25 10:00 | 141 | 141
2018-12-25 10:30 | 144 | 144
2018-12-25 11:00 | 144 | 144
2018-12-25 11:30 | 136 | 136
2018-12-25 12:00 | 137 | 136
2018-12-25 12:30 | 136 | 135
2018-12-25 13:00 | 130 | 130
2018-12-25 13:30 | 131 | 130
2018-12-25 14:00 | 134 | 134
2018-12-25 14:30 | 138 | 138
2018-12-25 15:00 | 145 | 145
2018-12-25 15:30 | 155 | 154
2018-12-25 16:00 | 166 | 165
2018-12-25 16:30 | 181 | 180
2018-12-25 17:00 | 194 | 192
2018-12-25 17:30 | 201 | 199
2018-12-25 18:00 | 201 | 200
2018-12-25 18:30 | 202 | 201
2018-12-25 19:00 | 205 | 204
2018-12-25 19:30 | 210 | 209
2018-12-25 20:00 | 213 | 212
2018-12-25 20:30 | 211 | 210
2018-12-25 21:00 | 204 | 203
2018-12-25 21:30 | 199 | 198
2018-12-25 22:00 | 194 | 194
2018-12-25 22:30 | 193 | 193
2018-12-25 23:00 | 191 | 191
2018-12-25 23:30 | 180 | 180
2018-12-26 | 166 | 166
2018-12-26 00:30 | 155 | 155
2018-12-26 01:00 | 147 | 147
2018-12-26 01:30 | 143 | 143
2018-12-26 02:00 | 139 | 139
2018-12-26 02:30 | 138 | 138
2018-12-26 03:00 | 136 | 136
2018-12-26 03:30 | 136 | 135
2018-12-26 04:00 | 135 | 135
2018-12-26 04:30 | 134 | 133
2018-12-26 05:00 | 132 | 131
2018-12-26 05:30 | 134 | 133
2018-12-26 06:00 | 132 | 131
2018-12-26 06:30 | 132 | 131
2018-12-26 07:00 | 131 | 131
2018-12-26 07:30 | 132 | 132
2018-12-26 08:00 | 131 | 131
2018-12-26 08:30 | 136 | 136
2018-12-26 09:00 | 143 | 143
2018-12-26 09:30 | 142 | 142
2018-12-26 10:00 | 139 | 138
2018-12-26 10:30 | 140 | 139
2018-12-26 11:00 | 138 | 137
2018-12-26 11:30 | 133 | 133
2018-12-26 12:00 | 133 | 132
2018-12-26 12:30 | 131 | 130
2018-12-26 13:00 | 132 | 131
2018-12-26 13:30 | 137 | 135
2018-12-26 14:00 | 142 | 141
2018-12-26 14:30 | 151 | 150
2018-12-26 15:00 | 161 | 160
2018-12-26 15:30 | 174 | 173
2018-12-26 16:00 | 187 | 186
2018-12-26 16:30 | 201 | 200
2018-12-26 17:00 | 215 | 214
2018-12-26 17:30 | 222 | 221
2018-12-26 18:00 | 224 | 223
2018-12-26 18:30 | 224 | 223
2018-12-26 19:00 | 227 | 226
2018-12-26 19:30 | 231 | 230
2018-12-26 20:00 | 232 | 231
2018-12-26 20:30 | 228 | 227
2018-12-26 21:00 | 219 | 219
2018-12-26 21:30 | 212 | 212
2018-12-26 22:00 | 205 | 205
2018-12-26 22:30 | 201 | 201
2018-12-26 23:00 | 198 | 198
2018-12-26 23:30 | 185 | 185
2018-12-27 | 171 | 171
2018-12-27 00:30 | 158 | 158
2018-12-27 01:00 | 151 | 150
2018-12-27 01:30 | 147 | 146
2018-12-27 02:00 | 144 | 143
2018-12-27 02:30 | 142 | 141
2018-12-27 03:00 | 141 | 140
2018-12-27 03:30 | 141 | 140
2018-12-27 04:00 | 141 | 140
2018-12-27 04:30 | 142 | 141
2018-12-27 05:00 | 143 | 142
2018-12-27 05:30 | 148 | 146
2018-12-27 06:00 | 150 | 149
2018-12-27 06:30 | 155 | 154
2018-12-27 07:00 | 158 | 157
2018-12-27 07:30 | 162 | 162
2018-12-27 08:00 | 162 | 162
2018-12-27 08:30 | 166 | 166
2018-12-27 09:00 | 172 | 172
2018-12-27 09:30 | 175 | 175
2018-12-27 10:00 | 175 | 175
2018-12-27 10:30 | 177 | 176
2018-12-27 11:00 | 174 | 174
2018-12-27 11:30 | 172 | 171
2018-12-27 12:00 | 171 | 170
2018-12-27 12:30 | 174 | 172
2018-12-27 13:00 | 178 | 177
2018-12-27 13:30 | 182 | 181
2018-12-27 14:00 | 188 | 186
2018-12-27 14:30 | 194 | 193
2018-12-27 15:00 | 203 | 202
2018-12-27 15:30 | 215 | 213
2018-12-27 16:00 | 226 | 225
2018-12-27 16:30 | 240 | 240
2018-12-27 17:00 | 255 | 255
2018-12-27 17:30 | 262 | 262
2018-12-27 18:00 | 263 | 263
2018-12-27 18:30 | 260 | 260
2018-12-27 19:00 | 261 | 261
2018-12-27 19:30 | 264 | 263
2018-12-27 20:00 | 261 | 261
2018-12-27 20:30 | 256 | 256
2018-12-27 21:00 | 245 | 245
2018-12-27 21:30 | 233 | 233
2018-12-27 22:00 | 222 | 221
2018-12-27 22:30 | 217 | 217
2018-12-27 23:00 | 212 | 212
2018-12-27 23:30 | 199 | 199
2018-12-28 | 183 | 183
2018-12-28 00:30 | 170 | 170
2018-12-28 01:00 | 163 | 163
2018-12-28 01:30 | 157 | 157
2018-12-28 02:00 | 154 | 154
2018-12-28 02:30 | 151 | 151
2018-12-28 03:00 | 149 | 149
2018-12-28 03:30 | 148 | 148
2018-12-28 04:00 | 147 | 147
2018-12-28 04:30 | 149 | 149
2018-12-28 05:00 | 149 | 149
2018-12-28 05:30 | 152 | 152
2018-12-28 06:00 | 154 | 154
2018-12-28 06:30 | 160 | 160
2018-12-28 07:00 | 164 | 164
2018-12-28 07:30 | 171 | 171
2018-12-28 08:00 | 176 | 175
2018-12-28 08:30 | 185 | 185
2018-12-28 09:00 | 186 | 186
2018-12-28 09:30 | 188 | 188
2018-12-28 10:00 | 186 | 186
2018-12-28 10:30 | 186 | 186
2018-12-28 11:00 | 182 | 182
2018-12-28 11:30 | 182 | 182
2018-12-28 12:00 | 184 | 184
2018-12-28 12:30 | 187 | 187
2018-12-28 13:00 | 192 | 192
2018-12-28 13:30 | 196 | 196
2018-12-28 14:00 | 202 | 201
2018-12-28 14:30 | 210 | 210
2018-12-28 15:00 | 218 | 218
2018-12-28 15:30 | 227 | 226
2018-12-28 16:00 | 238 | 237
2018-12-28 16:30 | 250 | 249
2018-12-28 17:00 | 260 | 259
2018-12-28 17:30 | 263 | 263
2018-12-28 18:00 | 261 | 261
2018-12-28 18:30 | 257 | 257
2018-12-28 19:00 | 258 | 258
2018-12-28 19:30 | 260 | 260
2018-12-28 20:00 | 260 | 259
2018-12-28 20:30 | 254 | 253
2018-12-28 21:00 | 242 | 241
2018-12-28 21:30 | 232 | 231
2018-12-28 22:00 | 223 | 223
2018-12-28 22:30 | 219 | 219
2018-12-28 23:00 | 215 | 215
2018-12-28 23:30 | 201 | 201
2018-12-29 | 184 | 184
2018-12-29 00:30 | 171 | 171
2018-12-29 01:00 | 163 | 163
2018-12-29 01:30 | 158 | 158
2018-12-29 02:00 | 154 | 154
2018-12-29 02:30 | 152 | 151
2018-12-29 03:00 | 150 | 150
2018-12-29 03:30 | 149 | 149
2018-12-29 04:00 | 147 | 147
2018-12-29 04:30 | 148 | 147
2018-12-29 05:00 | 147 | 146
2018-12-29 05:30 | 147 | 146
2018-12-29 06:00 | 147 | 146
2018-12-29 06:30 | 149 | 148
2018-12-29 07:00 | 152 | 151
2018-12-29 07:30 | 158 | 157
2018-12-29 08:00 | 156 | 156
2018-12-29 08:30 | 158 | 158
2018-12-29 09:00 | 162 | 162
2018-12-29 09:30 | 165 | 165
2018-12-29 10:00 | 163 | 162
2018-12-29 10:30 | 163 | 162
2018-12-29 11:00 | 164 | 163
2018-12-29 11:30 | 161 | 160
2018-12-29 12:00 | 164 | 163
2018-12-29 12:30 | 168 | 166
2018-12-29 13:00 | 175 | 173
2018-12-29 13:30 | 182 | 180
2018-12-29 14:00 | 188 | 186
2018-12-29 14:30 | 197 | 195
2018-12-29 15:00 | 206 | 205
2018-12-29 15:30 | 217 | 217
2018-12-29 16:00 | 229 | 229
2018-12-29 16:30 | 242 | 242
2018-12-29 17:00 | 251 | 251
2018-12-29 17:30 | 256 | 256
2018-12-29 18:00 | 256 | 256
2018-12-29 18:30 | 258 | 258
2018-12-29 19:00 | 264 | 264
2018-12-29 19:30 | 268 | 268
2018-12-29 20:00 | 269 | 269
2018-12-29 20:30 | 264 | 264
2018-12-29 21:00 | 253 | 253
2018-12-29 21:30 | 245 | 245
2018-12-29 22:00 | 238 | 238
2018-12-29 22:30 | 233 | 233
2018-12-29 23:00 | 225 | 225
2018-12-29 23:30 | 211 | 211
2018-12-30 | 196 | 195
2018-12-30 00:30 | 181 | 181
2018-12-30 01:00 | 174 | 174
2018-12-30 01:30 | 169 | 169
2018-12-30 02:00 | 164 | 164
2018-12-30 02:30 | 160 | 160
2018-12-30 03:00 | 158 | 158
2018-12-30 03:30 | 156 | 156
2018-12-30 04:00 | 155 | 154
2018-12-30 04:30 | 153 | 153
2018-12-30 05:00 | 152 | 151
2018-12-30 05:30 | 151 | 150
2018-12-30 06:00 | 149 | 148
2018-12-30 06:30 | 148 | 148
2018-12-30 07:00 | 150 | 150
2018-12-30 07:30 | 155 | 155
2018-12-30 08:00 | 159 | 159
2018-12-30 08:30 | 162 | 162
2018-12-30 09:00 | 165 | 165
2018-12-30 09:30 | 167 | 167
2018-12-30 10:00 | 169 | 168
2018-12-30 10:30 | 172 | 171
2018-12-30 11:00 | 174 | 173
2018-12-30 11:30 | 175 | 174
2018-12-30 12:00 | 177 | 176
2018-12-30 12:30 | 181 | 179
2018-12-30 13:00 | 183 | 183
2018-12-30 13:30 | 187 | 187
2018-12-30 14:00 | 192 | 192
2018-12-30 14:30 | 201 | 201
2018-12-30 15:00 | 211 | 211
2018-12-30 15:30 | 223 | 223
2018-12-30 16:00 | 237 | 237
2018-12-30 16:30 | 251 | 251
2018-12-30 17:00 | 265 | 264
2018-12-30 17:30 | 272 | 272
2018-12-30 18:00 | 276 | 275
2018-12-30 18:30 | 274 | 274
2018-12-30 19:00 | 274 | 273
2018-12-30 19:30 | 275 | 274
2018-12-30 20:00 | 274 | 273
2018-12-30 20:30 | 268 | 267
2018-12-30 21:00 | 254 | 253
2018-12-30 21:30 | 242 | 241
2018-12-30 22:00 | 232 | 231
2018-12-30 22:30 | 227 | 226
2018-12-30 23:00 | 223 | 222
2018-12-30 23:30 | 207 | 206
2018-12-31 | 190 | 190
2018-12-31 00:30 | 176 | 176
2018-12-31 01:00 | 168 | 168
2018-12-31 01:30 | 163 | 163
2018-12-31 02:00 | 161 | 161
2018-12-31 02:30 | 163 | 163
2018-12-31 03:00 | 160 | 160
2018-12-31 03:30 | 159 | 159
2018-12-31 04:00 | 158 | 158
2018-12-31 04:30 | 159 | 159
2018-12-31 05:00 | 160 | 160
2018-12-31 05:30 | 162 | 162
2018-12-31 06:00 | 165 | 165
2018-12-31 06:30 | 172 | 172
2018-12-31 07:00 | 179 | 178
2018-12-31 07:30 | 186 | 185
2018-12-31 08:00 | 191 | 191
2018-12-31 08:30 | 196 | 196
2018-12-31 09:00 | 198 | 198
2018-12-31 09:30 | 202 | 202
2018-12-31 10:00 | 204 | 204
2018-12-31 10:30 | 208 | 208
2018-12-31 11:00 | 206 | 206
2018-12-31 11:30 | 208 | 207
2018-12-31 12:00 | 207 | 206
2018-12-31 12:30 | 208 | 207
2018-12-31 13:00 | 213 | 212
2018-12-31 13:30 | 217 | 215
2018-12-31 14:00 | 223 | 222
2018-12-31 14:30 | 233 | 231
2018-12-31 15:00 | 245 | 243
2018-12-31 15:30 | 257 | 255
2018-12-31 16:00 | 271 | 268
2018-12-31 16:30 | 286 | 284
2018-12-31 17:00 | 299 | 299
2018-12-31 17:30 | 303 | 303
2018-12-31 18:00 | 297 | 297
2018-12-31 18:30 | 285 | 285
2018-12-31 19:00 | 282 | 282
2018-12-31 19:30 | 279 | 279
2018-12-31 20:00 | 274 | 274
2018-12-31 20:30 | 265 | 265
2018-12-31 21:00 | 252 | 252
2018-12-31 21:30 | 243 | 243
2018-12-31 22:00 | 238 | 237
2018-12-31 22:30 | 237 | 237
2018-12-31 23:00 | 232 | 232
2018-12-31 23:30 | 220 | 220
2019-01-01 | 205 | 205
2019-01-01 00:30 | 191 | 191
2019-01-01 01:00 | 186 | 185
2019-01-01 01:30 | 182 | 181
2019-01-01 02:00 | 177 | 177
2019-01-01 02:30 | 173 | 172
2019-01-01 03:00 | 169 | 169
2019-01-01 03:30 | 166 | 166
2019-01-01 04:00 | 163 | 163
2019-01-01 04:30 | 162 | 162
2019-01-01 05:00 | 159 | 159
2019-01-01 05:30 | 157 | 156
2019-01-01 06:00 | 156 | 155
2019-01-01 06:30 | 157 | 157
2019-01-01 07:00 | 158 | 158
2019-01-01 07:30 | 162 | 162
2019-01-01 08:00 | 166 | 166
2019-01-01 08:30 | 170 | 170
2019-01-01 09:00 | 172 | 171
2019-01-01 09:30 | 171 | 171
2019-01-01 10:00 | 172 | 171
2019-01-01 10:30 | 178 | 176
2019-01-01 11:00 | 181 | 180
2019-01-01 11:30 | 186 | 186
2019-01-01 12:00 | 194 | 193
2019-01-01 12:30 | 199 | 198
2019-01-01 13:00 | 205 | 205
2019-01-01 13:30 | 210 | 210
2019-01-01 14:00 | 218 | 217
2019-01-01 14:30 | 226 | 226
2019-01-01 15:00 | 236 | 236
2019-01-01 15:30 | 247 | 247
2019-01-01 16:00 | 264 | 263
2019-01-01 16:30 | 275 | 274
2019-01-01 17:00 | 276 | 275
2019-01-01 17:30 | 286 | 285
2019-01-01 18:00 | 287 | 287
2019-01-01 18:30 | 279 | 279
2019-01-01 19:00 | 279 | 279
2019-01-01 19:30 | 278 | 277
2019-01-01 20:00 | 277 | 275
2019-01-01 20:30 | 270 | 268
2019-01-01 21:00 | 256 | 255
2019-01-01 21:30 | 246 | 245
2019-01-01 22:00 | 236 | 235
2019-01-01 22:30 | 231 | 230
2019-01-01 23:00 | 225 | 225
2019-01-01 23:30 | 211 | 211
2019-01-02 | 195 | 195
2019-01-02 00:30 | 181 | 181
2019-01-02 01:00 | 174 | 174
2019-01-02 01:30 | 170 | 170
2019-01-02 02:00 | 166 | 166
2019-01-02 02:30 | 163 | 163
2019-01-02 03:00 | 162 | 162
2019-01-02 03:30 | 161 | 160
2019-01-02 04:00 | 160 | 160
2019-01-02 04:30 | 162 | 161
2019-01-02 05:00 | 163 | 163
2019-01-02 05:30 | 167 | 167
2019-01-02 06:00 | 171 | 171
2019-01-02 06:30 | 183 | 183
2019-01-02 07:00 | 189 | 189
2019-01-02 07:30 | 199 | 199
2019-01-02 08:00 | 208 | 208
2019-01-02 08:30 | 218 | 218
2019-01-02 09:00 | 225 | 224
2019-01-02 09:30 | 228 | 228
2019-01-02 10:00 | 227 | 227
2019-01-02 10:30 | 231 | 231
2019-01-02 11:00 | 232 | 231
2019-01-02 11:30 | 235 | 235
2019-01-02 12:00 | 240 | 240
2019-01-02 12:30 | 244 | 243
2019-01-02 13:00 | 250 | 250
2019-01-02 13:30 | 255 | 254
2019-01-02 14:00 | 259 | 258
2019-01-02 14:30 | 268 | 267
2019-01-02 15:00 | 276 | 275
2019-01-02 15:30 | 288 | 286
2019-01-02 16:00 | 298 | 296
2019-01-02 16:30 | 305 | 303
2019-01-02 17:00 | 315 | 314
2019-01-02 17:30 | 318 | 318
2019-01-02 18:00 | 314 | 314
2019-01-02 18:30 | 306 | 306
2019-01-02 19:00 | 307 | 307
2019-01-02 19:30 | 307 | 307
2019-01-02 20:00 | 304 | 304
2019-01-02 20:30 | 296 | 296
2019-01-02 21:00 | 284 | 284
2019-01-02 21:30 | 271 | 271
2019-01-02 22:00 | 260 | 260
2019-01-02 22:30 | 252 | 251
2019-01-02 23:00 | 244 | 244
2019-01-02 23:30 | 226 | 226
2019-01-03 | 208 | 207
2019-01-03 00:30 | 193 | 192
2019-01-03 01:00 | 184 | 184
2019-01-03 01:30 | 179 | 179
2019-01-03 02:00 | 175 | 175
2019-01-03 02:30 | 173 | 172
2019-01-03 03:00 | 170 | 170
2019-01-03 03:30 | 170 | 170
2019-01-03 04:00 | 169 | 169
2019-01-03 04:30 | 170 | 170
2019-01-03 05:00 | 172 | 172
2019-01-03 05:30 | 177 | 177
2019-01-03 06:00 | 181 | 181
2019-01-03 06:30 | 191 | 190
2019-01-03 07:00 | 201 | 200
2019-01-03 07:30 | 218 | 217
2019-01-03 08:00 | 224 | 223
2019-01-03 08:30 | 224 | 224
2019-01-03 09:00 | 219 | 219
2019-01-03 09:30 | 227 | 227
2019-01-03 10:00 | 237 | 237
2019-01-03 10:30 | 248 | 248
2019-01-03 11:00 | 266 | 266
2019-01-03 11:30 | 276 | 275
2019-01-03 12:00 | 275 | 274
2019-01-03 12:30 | 255 | 254
2019-01-03 13:00 | 244 | 244
2019-01-03 13:30 | 254 | 254
2019-01-03 14:00 | 252 | 252
2019-01-03 14:30 | 254 | 254
2019-01-03 15:00 | 266 | 266
2019-01-03 15:30 | 272 | 272
2019-01-03 16:00 | 276 | 275
2019-01-03 16:30 | 283 | 283
2019-01-03 17:00 | 297 | 297
2019-01-03 17:30 | 304 | 304
2019-01-03 18:00 | 306 | 305
2019-01-03 18:30 | 304 | 304
2019-01-03 19:00 | 307 | 307
2019-01-03 19:30 | 310 | 310
2019-01-03 20:00 | 310 | 310
2019-01-03 20:30 | 304 | 304
2019-01-03 21:00 | 293 | 293
2019-01-03 21:30 | 279 | 279
2019-01-03 22:00 | 267 | 267
2019-01-03 22:30 | 259 | 259
2019-01-03 23:00 | 252 | 252
2019-01-03 23:30 | 238 | 238
2019-01-04 | 221 | 220
2019-01-04 00:30 | 202 | 202
2019-01-04 01:00 | 192 | 192
2019-01-04 01:30 | 187 | 187
2019-01-04 02:00 | 183 | 183
2019-01-04 02:30 | 180 | 180
2019-01-04 03:00 | 178 | 178
2019-01-04 03:30 | 177 | 177
2019-01-04 04:00 | 177 | 177
2019-01-04 04:30 | 177 | 177
2019-01-04 05:00 | 179 | 179
2019-01-04 05:30 | 183 | 183
2019-01-04 06:00 | 187 | 187
2019-01-04 06:30 | 199 | 199
2019-01-04 07:00 | 210 | 209
2019-01-04 07:30 | 222 | 221
2019-01-04 08:00 | 232 | 232
2019-01-04 08:30 | 240 | 240
2019-01-04 09:00 | 242 | 242
2019-01-04 09:30 | 241 | 241
2019-01-04 10:00 | 236 | 236
2019-01-04 10:30 | 231 | 231
2019-01-04 11:00 | 227 | 227
2019-01-04 11:30 | 226 | 226
2019-01-04 12:00 | 232 | 232
2019-01-04 12:30 | 234 | 234
2019-01-04 13:00 | 241 | 241
2019-01-04 13:30 | 250 | 249
2019-01-04 14:00 | 257 | 256
2019-01-04 14:30 | 267 | 266
2019-01-04 15:00 | 275 | 274
2019-01-04 15:30 | 281 | 280
2019-01-04 16:00 | 292 | 291
2019-01-04 16:30 | 306 | 304
2019-01-04 17:00 | 316 | 314
2019-01-04 17:30 | 317 | 316
2019-01-04 18:00 | 312 | 311
2019-01-04 18:30 | 303 | 303
2019-01-04 19:00 | 305 | 305
2019-01-04 19:30 | 308 | 307
2019-01-04 20:00 | 306 | 306
2019-01-04 20:30 | 299 | 299
2019-01-04 21:00 | 288 | 287
2019-01-04 21:30 | 276 | 276
2019-01-04 22:00 | 265 | 265
2019-01-04 22:30 | 258 | 258
2019-01-04 23:00 | 250 | 250
2019-01-04 23:30 | 234 | 234
2019-01-05 | 217 | 217
2019-01-05 00:30 | 200 | 200
2019-01-05 01:00 | 191 | 191
2019-01-05 01:30 | 184 | 184
2019-01-05 02:00 | 179 | 179
2019-01-05 02:30 | 175 | 175
2019-01-05 03:00 | 172 | 172
2019-01-05 03:30 | 170 | 170
2019-01-05 04:00 | 169 | 169
2019-01-05 04:30 | 167 | 167
2019-01-05 05:00 | 166 | 166
2019-01-05 05:30 | 164 | 164
2019-01-05 06:00 | 163 | 163
2019-01-05 06:30 | 166 | 166
2019-01-05 07:00 | 171 | 171
2019-01-05 07:30 | 177 | 176
2019-01-05 08:00 | 185 | 183
2019-01-05 08:30 | 195 | 193
2019-01-05 09:00 | 196 | 195
2019-01-05 09:30 | 200 | 199
2019-01-05 10:00 | 205 | 204
2019-01-05 10:30 | 209 | 207
2019-01-05 11:00 | 213 | 211
2019-01-05 11:30 | 213 | 210
2019-01-05 12:00 | 213 | 210
2019-01-05 12:30 | 215 | 212
2019-01-05 13:00 | 219 | 217
2019-01-05 13:30 | 229 | 229
2019-01-05 14:00 | 238 | 237
2019-01-05 14:30 | 245 | 244
2019-01-05 15:00 | 253 | 252
2019-01-05 15:30 | 263 | 263
2019-01-05 16:00 | 269 | 269
2019-01-05 16:30 | 278 | 277
2019-01-05 17:00 | 289 | 289
2019-01-05 17:30 | 292 | 292
2019-01-05 18:00 | 286 | 286
2019-01-05 18:30 | 286 | 286
2019-01-05 19:00 | 289 | 289
2019-01-05 19:30 | 291 | 291
2019-01-05 20:00 | 291 | 291
2019-01-05 20:30 | 284 | 284
2019-01-05 21:00 | 273 | 273
2019-01-05 21:30 | 264 | 264
2019-01-05 22:00 | 256 | 255
2019-01-05 22:30 | 251 | 251
2019-01-05 23:00 | 247 | 246
2019-01-05 23:30 | 231 | 231
2019-01-06 | 215 | 215
2019-01-06 00:30 | 200 | 200
2019-01-06 01:00 | 192 | 192
2019-01-06 01:30 | 185 | 185
2019-01-06 02:00 | 180 | 180
2019-01-06 02:30 | 176 | 176
2019-01-06 03:00 | 174 | 174
2019-01-06 03:30 | 172 | 172
2019-01-06 04:00 | 171 | 171
2019-01-06 04:30 | 170 | 170
2019-01-06 05:00 | 169 | 169
2019-01-06 05:30 | 167 | 167
2019-01-06 06:00 | 166 | 165
2019-01-06 06:30 | 165 | 165
2019-01-06 07:00 | 166 | 166
2019-01-06 07:30 | 176 | 176
2019-01-06 08:00 | 180 | 180
2019-01-06 08:30 | 180 | 180
2019-01-06 09:00 | 184 | 184
2019-01-06 09:30 | 189 | 189
2019-01-06 10:00 | 197 | 197
2019-01-06 10:30 | 207 | 207
2019-01-06 11:00 | 217 | 217
2019-01-06 11:30 | 218 | 218
2019-01-06 12:00 | 223 | 223
2019-01-06 12:30 | 230 | 229
2019-01-06 13:00 | 235 | 235
2019-01-06 13:30 | 243 | 243
2019-01-06 14:00 | 248 | 248
2019-01-06 14:30 | 251 | 251
2019-01-06 15:00 | 259 | 259
2019-01-06 15:30 | 268 | 268
2019-01-06 16:00 | 277 | 277
2019-01-06 16:30 | 277 | 277
2019-01-06 17:00 | 286 | 286
2019-01-06 17:30 | 292 | 292
2019-01-06 18:00 | 294 | 294
2019-01-06 18:30 | 296 | 296
2019-01-06 19:00 | 300 | 300
2019-01-06 19:30 | 302 | 301
2019-01-06 20:00 | 301 | 301
2019-01-06 20:30 | 293 | 293
2019-01-06 21:00 | 280 | 280
2019-01-06 21:30 | 269 | 269
2019-01-06 22:00 | 258 | 258
2019-01-06 22:30 | 251 | 251
2019-01-06 23:00 | 246 | 246
2019-01-06 23:30 | 231 | 231
2019-01-07 | 213 | 213
2019-01-07 00:30 | 199 | 199
2019-01-07 01:00 | 192 | 191
2019-01-07 01:30 | 187 | 186
2019-01-07 02:00 | 184 | 183
2019-01-07 02:30 | 179 | 179
2019-01-07 03:00 | 178 | 178
2019-01-07 03:30 | 177 | 177
2019-01-07 04:00 | 177 | 177
2019-01-07 04:30 | 179 | 179
2019-01-07 05:00 | 184 | 184
2019-01-07 05:30 | 190 | 190
2019-01-07 06:00 | 199 | 199
2019-01-07 06:30 | 216 | 216
2019-01-07 07:00 | 232 | 231
2019-01-07 07:30 | 250 | 249
2019-01-07 08:00 | 260 | 260
2019-01-07 08:30 | 267 | 267
2019-01-07 09:00 | 270 | 270
2019-01-07 09:30 | 268 | 268
2019-01-07 10:00 | 266 | 266
2019-01-07 10:30 | 265 | 265
2019-01-07 11:00 | 262 | 262
2019-01-07 11:30 | 262 | 262
2019-01-07 12:00 | 262 | 262
2019-01-07 12:30 | 273 | 273
2019-01-07 13:00 | 288 | 287
2019-01-07 13:30 | 304 | 304
2019-01-07 14:00 | 312 | 312
2019-01-07 14:30 | 315 | 315
2019-01-07 15:00 | 307 | 307
2019-01-07 15:30 | 310 | 310
2019-01-07 16:00 | 313 | 313
2019-01-07 16:30 | 311 | 310
2019-01-07 17:00 | 312 | 311
2019-01-07 17:30 | 310 | 309
2019-01-07 18:00 | 307 | 305
2019-01-07 18:30 | 298 | 298
2019-01-07 19:00 | 303 | 302
2019-01-07 19:30 | 304 | 304
2019-01-07 20:00 | 303 | 303
2019-01-07 20:30 | 298 | 298
2019-01-07 21:00 | 286 | 286
2019-01-07 21:30 | 275 | 275
2019-01-07 22:00 | 261 | 261
2019-01-07 22:30 | 252 | 252
2019-01-07 23:00 | 247 | 247
2019-01-07 23:30 | 233 | 233
2019-01-08 | 217 | 217
2019-01-08 00:30 | 201 | 201
2019-01-08 01:00 | 192 | 192
2019-01-08 01:30 | 187 | 187
2019-01-08 02:00 | 183 | 183
2019-01-08 02:30 | 180 | 180
2019-01-08 03:00 | 179 | 179
2019-01-08 03:30 | 179 | 179
2019-01-08 04:00 | 178 | 178
2019-01-08 04:30 | 180 | 180
2019-01-08 05:00 | 184 | 184
2019-01-08 05:30 | 191 | 191
2019-01-08 06:00 | 199 | 199
2019-01-08 06:30 | 218 | 218
2019-01-08 07:00 | 234 | 233
2019-01-08 07:30 | 250 | 249
2019-01-08 08:00 | 261 | 261
2019-01-08 08:30 | 269 | 269
2019-01-08 09:00 | 268 | 268
2019-01-08 09:30 | 267 | 267
2019-01-08 10:00 | 271 | 271
2019-01-08 10:30 | 263 | 263
2019-01-08 11:00 | 256 | 256
2019-01-08 11:30 | 258 | 258
2019-01-08 12:00 | 255 | 255
2019-01-08 12:30 | 263 | 263
2019-01-08 13:00 | 271 | 271
2019-01-08 13:30 | 278 | 278
2019-01-08 14:00 | 285 | 285
2019-01-08 14:30 | 282 | 281
2019-01-08 15:00 | 280 | 280
2019-01-08 15:30 | 286 | 286
2019-01-08 16:00 | 291 | 291
2019-01-08 16:30 | 298 | 298
2019-01-08 17:00 | 305 | 305
2019-01-08 17:30 | 311 | 311
2019-01-08 18:00 | 312 | 312
2019-01-08 18:30 | 307 | 307
2019-01-08 19:00 | 311 | 311
2019-01-08 19:30 | 311 | 311
2019-01-08 20:00 | 310 | 310
2019-01-08 20:30 | 303 | 303
2019-01-08 21:00 | 291 | 290
2019-01-08 21:30 | 278 | 278
2019-01-08 22:00 | 265 | 265
2019-01-08 22:30 | 257 | 257
2019-01-08 23:00 | 250 | 250
2019-01-08 23:30 | 233 | 233
2019-01-09 | 217 | 216
2019-01-09 00:30 | 203 | 203
2019-01-09 01:00 | 195 | 195
2019-01-09 01:30 | 188 | 188
2019-01-09 02:00 | 185 | 185
2019-01-09 02:30 | 182 | 182
2019-01-09 03:00 | 181 | 181
2019-01-09 03:30 | 179 | 179
2019-01-09 04:00 | 178 | 178
2019-01-09 04:30 | 181 | 181
2019-01-09 05:00 | 185 | 184
2019-01-09 05:30 | 191 | 191
2019-01-09 06:00 | 196 | 196
2019-01-09 06:30 | 211 | 211
2019-01-09 07:00 | 224 | 223
2019-01-09 07:30 | 249 | 249
2019-01-09 08:00 | 274 | 273
2019-01-09 08:30 | 284 | 284
2019-01-09 09:00 | 283 | 283
2019-01-09 09:30 | 281 | 281
2019-01-09 10:00 | 285 | 285
2019-01-09 10:30 | 289 | 288
2019-01-09 11:00 | 288 | 288
2019-01-09 11:30 | 287 | 287
2019-01-09 12:00 | 282 | 282
2019-01-09 12:30 | 278 | 278
2019-01-09 13:00 | 285 | 285
2019-01-09 13:30 | 292 | 291
2019-01-09 14:00 | 289 | 288
2019-01-09 14:30 | 290 | 290
2019-01-09 15:00 | 296 | 296
2019-01-09 15:30 | 304 | 304
2019-01-09 16:00 | 312 | 312
2019-01-09 16:30 | 315 | 315
2019-01-09 17:00 | 324 | 324
2019-01-09 17:30 | 324 | 324
2019-01-09 18:00 | 320 | 319
2019-01-09 18:30 | 317 | 317
2019-01-09 19:00 | 323 | 323
2019-01-09 19:30 | 325 | 325
2019-01-09 20:00 | 323 | 323
2019-01-09 20:30 | 317 | 317
2019-01-09 21:00 | 304 | 304
2019-01-09 21:30 | 292 | 292
2019-01-09 22:00 | 279 | 279
2019-01-09 22:30 | 268 | 268
2019-01-09 23:00 | 260 | 260
2019-01-09 23:30 | 244 | 244
2019-01-10 | 225 | 225
2019-01-10 00:30 | 209 | 209
2019-01-10 01:00 | 201 | 201
2019-01-10 01:30 | 196 | 196
2019-01-10 02:00 | 191 | 191
2019-01-10 02:30 | 188 | 188
2019-01-10 03:00 | 186 | 186
2019-01-10 03:30 | 185 | 185
2019-01-10 04:00 | 185 | 185
2019-01-10 04:30 | 188 | 187
2019-01-10 05:00 | 191 | 191
2019-01-10 05:30 | 198 | 198
2019-01-10 06:00 | 205 | 205
2019-01-10 06:30 | 223 | 223
2019-01-10 07:00 | 238 | 238
2019-01-10 07:30 | 256 | 255
2019-01-10 08:00 | 255 | 254
2019-01-10 08:30 | 256 | 255
2019-01-10 09:00 | 276 | 276
2019-01-10 09:30 | 279 | 278
2019-01-10 10:00 | 284 | 284
2019-01-10 10:30 | 285 | 284
2019-01-10 11:00 | 279 | 278
2019-01-10 11:30 | 288 | 288
2019-01-10 12:00 | 295 | 294
2019-01-10 12:30 | 291 | 291
2019-01-10 13:00 | 295 | 295
2019-01-10 13:30 | 297 | 297
2019-01-10 14:00 | 295 | 295
2019-01-10 14:30 | 279 | 279
2019-01-10 15:00 | 282 | 282
2019-01-10 15:30 | 293 | 293
2019-01-10 16:00 | 304 | 304
2019-01-10 16:30 | 317 | 317
2019-01-10 17:00 | 328 | 328
2019-01-10 17:30 | 333 | 332
2019-01-10 18:00 | 333 | 333
2019-01-10 18:30 | 329 | 329
2019-01-10 19:00 | 331 | 331
2019-01-10 19:30 | 334 | 334
2019-01-10 20:00 | 333 | 333
2019-01-10 20:30 | 324 | 324
2019-01-10 21:00 | 311 | 311
2019-01-10 21:30 | 294 | 294
2019-01-10 22:00 | 280 | 280
2019-01-10 22:30 | 268 | 268
2019-01-10 23:00 | 258 | 258
2019-01-10 23:30 | 241 | 241
2019-01-11 | 223 | 222
2019-01-11 00:30 | 204 | 204
2019-01-11 01:00 | 196 | 195
2019-01-11 01:30 | 190 | 190
2019-01-11 02:00 | 185 | 185
2019-01-11 02:30 | 183 | 183
2019-01-11 03:00 | 179 | 179
2019-01-11 03:30 | 177 | 177
2019-01-11 04:00 | 176 | 176
2019-01-11 04:30 | 179 | 179
2019-01-11 05:00 | 183 | 183
2019-01-11 05:30 | 190 | 190
2019-01-11 06:00 | 196 | 196
2019-01-11 06:30 | 212 | 211
2019-01-11 07:00 | 225 | 224
2019-01-11 07:30 | 237 | 236
2019-01-11 08:00 | 245 | 245
2019-01-11 08:30 | 254 | 253
2019-01-11 09:00 | 256 | 256
2019-01-11 09:30 | 258 | 257
2019-01-11 10:00 | 257 | 257
2019-01-11 10:30 | 255 | 255
2019-01-11 11:00 | 255 | 255
2019-01-11 11:30 | 256 | 256
2019-01-11 12:00 | 256 | 256
2019-01-11 12:30 | 258 | 258
2019-01-11 13:00 | 261 | 261
2019-01-11 13:30 | 266 | 265
2019-01-11 14:00 | 271 | 271
2019-01-11 14:30 | 277 | 277
2019-01-11 15:00 | 284 | 284
2019-01-11 15:30 | 292 | 291
2019-01-11 16:00 | 302 | 302
2019-01-11 16:30 | 312 | 311
2019-01-11 17:00 | 322 | 321
2019-01-11 17:30 | 323 | 323
2019-01-11 18:00 | 319 | 319
2019-01-11 18:30 | 311 | 311
2019-01-11 19:00 | 311 | 311
2019-01-11 19:30 | 311 | 311
2019-01-11 20:00 | 309 | 309
2019-01-11 20:30 | 300 | 299
2019-01-11 21:00 | 287 | 286
2019-01-11 21:30 | 274 | 274
2019-01-11 22:00 | 262 | 262
2019-01-11 22:30 | 254 | 254
2019-01-11 23:00 | 245 | 245
2019-01-11 23:30 | 227 | 227
2019-01-12 | 209 | 209
2019-01-12 00:30 | 195 | 195
2019-01-12 01:00 | 186 | 186
2019-01-12 01:30 | 181 | 180
2019-01-12 02:00 | 175 | 174
2019-01-12 02:30 | 171 | 171
2019-01-12 03:00 | 168 | 167
2019-01-12 03:30 | 166 | 165
2019-01-12 04:00 | 165 | 164
2019-01-12 04:30 | 163 | 162
2019-01-12 05:00 | 163 | 162
2019-01-12 05:30 | 163 | 162
2019-01-12 06:00 | 164 | 162
2019-01-12 06:30 | 167 | 166
2019-01-12 07:00 | 169 | 168
2019-01-12 07:30 | 174 | 173
2019-01-12 08:00 | 177 | 177
2019-01-12 08:30 | 187 | 187
2019-01-12 09:00 | 192 | 192
2019-01-12 09:30 | 192 | 192
2019-01-12 10:00 | 190 | 190
2019-01-12 10:30 | 186 | 186
2019-01-12 11:00 | 184 | 184
2019-01-12 11:30 | 186 | 186
2019-01-12 12:00 | 190 | 190
2019-01-12 12:30 | 192 | 192
2019-01-12 13:00 | 198 | 198
2019-01-12 13:30 | 205 | 204
2019-01-12 14:00 | 213 | 213
2019-01-12 14:30 | 220 | 220
2019-01-12 15:00 | 232 | 232
2019-01-12 15:30 | 243 | 243
2019-01-12 16:00 | 256 | 256
2019-01-12 16:30 | 267 | 267
2019-01-12 17:00 | 280 | 280
2019-01-12 17:30 | 280 | 279
2019-01-12 18:00 | 281 | 281
2019-01-12 18:30 | 278 | 278
2019-01-12 19:00 | 280 | 280
2019-01-12 19:30 | 282 | 282
2019-01-12 20:00 | 281 | 281
2019-01-12 20:30 | 274 | 274
2019-01-12 21:00 | 261 | 261
2019-01-12 21:30 | 251 | 251
2019-01-12 22:00 | 242 | 242
2019-01-12 22:30 | 237 | 237
2019-01-12 23:00 | 232 | 232
2019-01-12 23:30 | 218 | 218
2019-01-13 | 202 | 202
2019-01-13 00:30 | 189 | 189
2019-01-13 01:00 | 182 | 181
2019-01-13 01:30 | 176 | 176
2019-01-13 02:00 | 170 | 169
2019-01-13 02:30 | 167 | 166
2019-01-13 03:00 | 165 | 163
2019-01-13 03:30 | 164 | 163
2019-01-13 04:00 | 164 | 163
2019-01-13 04:30 | 163 | 162
2019-01-13 05:00 | 162 | 161
2019-01-13 05:30 | 161 | 159
2019-01-13 06:00 | 160 | 158
2019-01-13 06:30 | 160 | 158
2019-01-13 07:00 | 161 | 160
2019-01-13 07:30 | 165 | 165
2019-01-13 08:00 | 166 | 166
2019-01-13 08:30 | 175 | 175
2019-01-13 09:00 | 179 | 179
2019-01-13 09:30 | 185 | 185
2019-01-13 10:00 | 189 | 189
2019-01-13 10:30 | 191 | 191
2019-01-13 11:00 | 192 | 191
2019-01-13 11:30 | 195 | 195
2019-01-13 12:00 | 199 | 199
2019-01-13 12:30 | 204 | 204
2019-01-13 13:00 | 209 | 209
2019-01-13 13:30 | 215 | 214
2019-01-13 14:00 | 223 | 223
2019-01-13 14:30 | 229 | 229
2019-01-13 15:00 | 238 | 238
2019-01-13 15:30 | 249 | 249
2019-01-13 16:00 | 261 | 261
2019-01-13 16:30 | 272 | 272
2019-01-13 17:00 | 285 | 284
2019-01-13 17:30 | 292 | 291
2019-01-13 18:00 | 295 | 294
2019-01-13 18:30 | 294 | 294
2019-01-13 19:00 | 294 | 294
2019-01-13 19:30 | 295 | 294
2019-01-13 20:00 | 292 | 292
2019-01-13 20:30 | 284 | 284
2019-01-13 21:00 | 271 | 271
2019-01-13 21:30 | 260 | 260
2019-01-13 22:00 | 249 | 249
2019-01-13 22:30 | 244 | 243
2019-01-13 23:00 | 235 | 235
2019-01-13 23:30 | 219 | 219
2019-01-14 | 202 | 202
2019-01-14 00:30 | 189 | 189
2019-01-14 01:00 | 182 | 182
2019-01-14 01:30 | 177 | 177
2019-01-14 02:00 | 173 | 173
2019-01-14 02:30 | 171 | 171
2019-01-14 03:00 | 169 | 169
2019-01-14 03:30 | 168 | 168
2019-01-14 04:00 | 168 | 168
2019-01-14 04:30 | 172 | 172
2019-01-14 05:00 | 176 | 176
2019-01-14 05:30 | 185 | 185
2019-01-14 06:00 | 193 | 193
2019-01-14 06:30 | 211 | 210
2019-01-14 07:00 | 224 | 223
2019-01-14 07:30 | 238 | 238
2019-01-14 08:00 | 245 | 245
2019-01-14 08:30 | 249 | 249
2019-01-14 09:00 | 255 | 255
2019-01-14 09:30 | 281 | 281
2019-01-14 10:00 | 282 | 282
2019-01-14 10:30 | 280 | 280
2019-01-14 11:00 | 277 | 277
2019-01-14 11:30 | 278 | 278
2019-01-14 12:00 | 280 | 280
2019-01-14 12:30 | 284 | 284
2019-01-14 13:00 | 292 | 292
2019-01-14 13:30 | 301 | 300
2019-01-14 14:00 | 312 | 311
2019-01-14 14:30 | 322 | 322
2019-01-14 15:00 | 335 | 335
2019-01-14 15:30 | 322 | 322
2019-01-14 16:00 | 326 | 326
2019-01-14 16:30 | 334 | 334
2019-01-14 17:00 | 345 | 344
2019-01-14 17:30 | 346 | 345
2019-01-14 18:00 | 341 | 341
2019-01-14 18:30 | 335 | 335
2019-01-14 19:00 | 336 | 336
2019-01-14 19:30 | 336 | 336
2019-01-14 20:00 | 333 | 333
2019-01-14 20:30 | 323 | 323
2019-01-14 21:00 | 306 | 306
2019-01-14 21:30 | 292 | 292
2019-01-14 22:00 | 278 | 278
2019-01-14 22:30 | 267 | 267
2019-01-14 23:00 | 257 | 257
2019-01-14 23:30 | 238 | 238
2019-01-15 | 216 | 216
2019-01-15 00:30 | 199 | 199
2019-01-15 01:00 | 190 | 190
2019-01-15 01:30 | 184 | 184
2019-01-15 02:00 | 179 | 179
2019-01-15 02:30 | 177 | 177
2019-01-15 03:00 | 175 | 175
2019-01-15 03:30 | 174 | 174
2019-01-15 04:00 | 174 | 173
2019-01-15 04:30 | 176 | 176
2019-01-15 05:00 | 180 | 180
2019-01-15 05:30 | 188 | 187
2019-01-15 06:00 | 194 | 194
2019-01-15 06:30 | 213 | 213
2019-01-15 07:00 | 225 | 225
2019-01-15 07:30 | 239 | 239
2019-01-15 08:00 | 248 | 248
2019-01-15 08:30 | 255 | 255
2019-01-15 09:00 | 259 | 259
2019-01-15 09:30 | 263 | 262
2019-01-15 10:00 | 264 | 264
2019-01-15 10:30 | 264 | 263
2019-01-15 11:00 | 264 | 263
2019-01-15 11:30 | 266 | 265
2019-01-15 12:00 | 274 | 273
2019-01-15 12:30 | 280 | 278
2019-01-15 13:00 | 287 | 286
2019-01-15 13:30 | 292 | 291
2019-01-15 14:00 | 300 | 300
2019-01-15 14:30 | 310 | 310
2019-01-15 15:00 | 318 | 318
2019-01-15 15:30 | 327 | 327
2019-01-15 16:00 | 341 | 341
2019-01-15 16:30 | 355 | 355
2019-01-15 17:00 | 365 | 365
2019-01-15 17:30 | 366 | 366
2019-01-15 18:00 | 361 | 361
2019-01-15 18:30 | 350 | 350
2019-01-15 19:00 | 346 | 345
2019-01-15 19:30 | 345 | 344
2019-01-15 20:00 | 342 | 341
2019-01-15 20:30 | 327 | 327
2019-01-15 21:00 | 307 | 307
2019-01-15 21:30 | 291 | 291
2019-01-15 22:00 | 277 | 277
2019-01-15 22:30 | 265 | 265
2019-01-15 23:00 | 255 | 255
2019-01-15 23:30 | 236 | 236
2019-01-16 | 217 | 217
2019-01-16 00:30 | 203 | 203
2019-01-16 01:00 | 195 | 195
2019-01-16 01:30 | 188 | 188
2019-01-16 02:00 | 184 | 184
2019-01-16 02:30 | 181 | 181
2019-01-16 03:00 | 180 | 180
2019-01-16 03:30 | 180 | 180
2019-01-16 04:00 | 179 | 178
2019-01-16 04:30 | 181 | 181
2019-01-16 05:00 | 184 | 184
2019-01-16 05:30 | 191 | 191
2019-01-16 06:00 | 199 | 199
2019-01-16 06:30 | 215 | 215
2019-01-16 07:00 | 232 | 232
2019-01-16 07:30 | 244 | 244
2019-01-16 08:00 | 249 | 249
2019-01-16 08:30 | 252 | 252
2019-01-16 09:00 | 256 | 255
2019-01-16 09:30 | 254 | 254
2019-01-16 10:00 | 255 | 254
2019-01-16 10:30 | 258 | 257
2019-01-16 11:00 | 263 | 261
2019-01-16 11:30 | 268 | 267
2019-01-16 12:00 | 277 | 275
2019-01-16 12:30 | 286 | 285
2019-01-16 13:00 | 295 | 295
2019-01-16 13:30 | 305 | 305
2019-01-16 14:00 | 316 | 316
2019-01-16 14:30 | 325 | 325
2019-01-16 15:00 | 336 | 336
2019-01-16 15:30 | 345 | 345
2019-01-16 16:00 | 355 | 355
2019-01-16 16:30 | 367 | 367
2019-01-16 17:00 | 380 | 380
2019-01-16 17:30 | 379 | 378
2019-01-16 18:00 | 374 | 373
2019-01-16 18:30 | 364 | 364
2019-01-16 19:00 | 363 | 363
2019-01-16 19:30 | 361 | 361
2019-01-16 20:00 | 363 | 363
2019-01-16 20:30 | 356 | 355
2019-01-16 21:00 | 336 | 335
2019-01-16 21:30 | 319 | 318
2019-01-16 22:00 | 300 | 298
2019-01-16 22:30 | 284 | 283
2019-01-16 23:00 | 271 | 271
2019-01-16 23:30 | 248 | 248
2019-01-17 | 228 | 228
2019-01-17 00:30 | 212 | 212
2019-01-17 01:00 | 204 | 203
2019-01-17 01:30 | 198 | 197
2019-01-17 02:00 | 192 | 191
2019-01-17 02:30 | 189 | 188
2019-01-17 03:00 | 185 | 185
2019-01-17 03:30 | 184 | 184
2019-01-17 04:00 | 182 | 182
2019-01-17 04:30 | 184 | 184
2019-01-17 05:00 | 189 | 189
2019-01-17 05:30 | 195 | 195
2019-01-17 06:00 | 203 | 202
2019-01-17 06:30 | 220 | 220
2019-01-17 07:00 | 235 | 234
2019-01-17 07:30 | 250 | 250
2019-01-17 08:00 | 260 | 260
2019-01-17 08:30 | 265 | 265
2019-01-17 09:00 | 270 | 270
2019-01-17 09:30 | 272 | 272
2019-01-17 10:00 | 267 | 267
2019-01-17 10:30 | 271 | 271
2019-01-17 11:00 | 275 | 274
2019-01-17 11:30 | 275 | 274
2019-01-17 12:00 | 279 | 278
2019-01-17 12:30 | 282 | 281
2019-01-17 13:00 | 286 | 285
2019-01-17 13:30 | 297 | 297
2019-01-17 14:00 | 307 | 307
2019-01-17 14:30 | 315 | 315
2019-01-17 15:00 | 324 | 324
2019-01-17 15:30 | 331 | 331
2019-01-17 16:00 | 344 | 344
2019-01-17 16:30 | 355 | 355
2019-01-17 17:00 | 366 | 366
2019-01-17 17:30 | 368 | 368
2019-01-17 18:00 | 362 | 361
2019-01-17 18:30 | 352 | 352
2019-01-17 19:00 | 349 | 349
2019-01-17 19:30 | 346 | 346
2019-01-17 20:00 | 342 | 342
2019-01-17 20:30 | 331 | 331
2019-01-17 21:00 | 318 | 317
2019-01-17 21:30 | 299 | 298
2019-01-17 22:00 | 284 | 284
2019-01-17 22:30 | 274 | 274
2019-01-17 23:00 | 263 | 263
2019-01-17 23:30 | 243 | 243
2019-01-18 | 222 | 222
2019-01-18 00:30 | 208 | 208
2019-01-18 01:00 | 199 | 199
2019-01-18 01:30 | 194 | 194
2019-01-18 02:00 | 188 | 188
2019-01-18 02:30 | 185 | 184
2019-01-18 03:00 | 182 | 182
2019-01-18 03:30 | 181 | 181
2019-01-18 04:00 | 181 | 180
2019-01-18 04:30 | 182 | 182
2019-01-18 05:00 | 187 | 187
2019-01-18 05:30 | 194 | 194
2019-01-18 06:00 | 203 | 203
2019-01-18 06:30 | 221 | 221
2019-01-18 07:00 | 230 | 230
2019-01-18 07:30 | 243 | 242
2019-01-18 08:00 | 250 | 250
2019-01-18 08:30 | 260 | 260
2019-01-18 09:00 | 266 | 265
2019-01-18 09:30 | 268 | 267
2019-01-18 10:00 | 271 | 269
2019-01-18 10:30 | 271 | 269
2019-01-18 11:00 | 271 | 269
2019-01-18 11:30 | 269 | 266
2019-01-18 12:00 | 271 | 269
2019-01-18 12:30 | 272 | 270
2019-01-18 13:00 | 279 | 276
2019-01-18 13:30 | 287 | 284
2019-01-18 14:00 | 296 | 292
2019-01-18 14:30 | 306 | 303
2019-01-18 15:00 | 315 | 312
2019-01-18 15:30 | 327 | 327
2019-01-18 16:00 | 340 | 339
2019-01-18 16:30 | 353 | 352
2019-01-18 17:00 | 364 | 363
2019-01-18 17:30 | 365 | 364
2019-01-18 18:00 | 357 | 357
2019-01-18 18:30 | 346 | 345
2019-01-18 19:00 | 343 | 342
2019-01-18 19:30 | 342 | 340
2019-01-18 20:00 | 337 | 336
2019-01-18 20:30 | 327 | 325
2019-01-18 21:00 | 309 | 308
2019-01-18 21:30 | 297 | 296
2019-01-18 22:00 | 284 | 283
2019-01-18 22:30 | 276 | 276
2019-01-18 23:00 | 264 | 264
2019-01-18 23:30 | 244 | 244
2019-01-19 | 224 | 223
2019-01-19 00:30 | 209 | 208
2019-01-19 01:00 | 200 | 199
2019-01-19 01:30 | 193 | 193
2019-01-19 02:00 | 188 | 187
2019-01-19 02:30 | 184 | 183
2019-01-19 03:00 | 180 | 179
2019-01-19 03:30 | 179 | 178
2019-01-19 04:00 | 176 | 176
2019-01-19 04:30 | 175 | 175
2019-01-19 05:00 | 175 | 175
2019-01-19 05:30 | 174 | 174
2019-01-19 06:00 | 174 | 174
2019-01-19 06:30 | 178 | 178
2019-01-19 07:00 | 179 | 178
2019-01-19 07:30 | 185 | 184
2019-01-19 08:00 | 194 | 193
2019-01-19 08:30 | 204 | 203
2019-01-19 09:00 | 208 | 207
2019-01-19 09:30 | 210 | 210
2019-01-19 10:00 | 208 | 208
2019-01-19 10:30 | 219 | 219
2019-01-19 11:00 | 218 | 218
2019-01-19 11:30 | 231 | 231
2019-01-19 12:00 | 246 | 246
2019-01-19 12:30 | 250 | 250
2019-01-19 13:00 | 250 | 250
2019-01-19 13:30 | 249 | 248
2019-01-19 14:00 | 254 | 253
2019-01-19 14:30 | 265 | 264
2019-01-19 15:00 | 280 | 280
2019-01-19 15:30 | 294 | 293
2019-01-19 16:00 | 309 | 307
2019-01-19 16:30 | 322 | 320
2019-01-19 17:00 | 334 | 334
2019-01-19 17:30 | 337 | 336
2019-01-19 18:00 | 333 | 333
2019-01-19 18:30 | 330 | 329
2019-01-19 19:00 | 327 | 327
2019-01-19 19:30 | 324 | 324
2019-01-19 20:00 | 320 | 320
2019-01-19 20:30 | 310 | 310
2019-01-19 21:00 | 295 | 295
2019-01-19 21:30 | 283 | 282
2019-01-19 22:00 | 270 | 268
2019-01-19 22:30 | 264 | 260
2019-01-19 23:00 | 256 | 253
2019-01-19 23:30 | 239 | 237
2019-01-20 | 222 | 220
2019-01-20 00:30 | 206 | 205
2019-01-20 01:00 | 198 | 197
2019-01-20 01:30 | 190 | 190
2019-01-20 02:00 | 185 | 185
2019-01-20 02:30 | 181 | 180
2019-01-20 03:00 | 178 | 177
2019-01-20 03:30 | 175 | 175
2019-01-20 04:00 | 174 | 174
2019-01-20 04:30 | 173 | 173
2019-01-20 05:00 | 173 | 173
2019-01-20 05:30 | 173 | 173
2019-01-20 06:00 | 173 | 173
2019-01-20 06:30 | 177 | 177
2019-01-20 07:00 | 178 | 178
2019-01-20 07:30 | 183 | 183
2019-01-20 08:00 | 187 | 187
2019-01-20 08:30 | 194 | 193
2019-01-20 09:00 | 198 | 197
2019-01-20 09:30 | 203 | 203
2019-01-20 10:00 | 207 | 207
2019-01-20 10:30 | 211 | 210
2019-01-20 11:00 | 211 | 211
2019-01-20 11:30 | 215 | 215
2019-01-20 12:00 | 223 | 223
2019-01-20 12:30 | 234 | 234
2019-01-20 13:00 | 248 | 248
2019-01-20 13:30 | 259 | 259
2019-01-20 14:00 | 265 | 265
2019-01-20 14:30 | 270 | 270
2019-01-20 15:00 | 280 | 279
2019-01-20 15:30 | 291 | 290
2019-01-20 16:00 | 303 | 303
2019-01-20 16:30 | 316 | 316
2019-01-20 17:00 | 330 | 329
2019-01-20 17:30 | 333 | 332
2019-01-20 18:00 | 336 | 335
2019-01-20 18:30 | 334 | 333
2019-01-20 19:00 | 332 | 331
2019-01-20 19:30 | 333 | 329
2019-01-20 20:00 | 330 | 327
2019-01-20 20:30 | 321 | 318
2019-01-20 21:00 | 303 | 302
2019-01-20 21:30 | 289 | 288
2019-01-20 22:00 | 276 | 275
2019-01-20 22:30 | 266 | 265
2019-01-20 23:00 | 256 | 255
2019-01-20 23:30 | 238 | 237
2019-01-21 | 219 | 219
2019-01-21 00:30 | 205 | 205
2019-01-21 01:00 | 199 | 199
2019-01-21 01:30 | 195 | 195
2019-01-21 02:00 | 191 | 191
2019-01-21 02:30 | 188 | 188
2019-01-21 03:00 | 186 | 185
2019-01-21 03:30 | 186 | 185
2019-01-21 04:00 | 185 | 185
2019-01-21 04:30 | 187 | 186
2019-01-21 05:00 | 193 | 193
2019-01-21 05:30 | 202 | 202
2019-01-21 06:00 | 210 | 210
2019-01-21 06:30 | 231 | 231
2019-01-21 07:00 | 248 | 248
2019-01-21 07:30 | 265 | 265
2019-01-21 08:00 | 293 | 292
2019-01-21 08:30 | 308 | 308
2019-01-21 09:00 | 310 | 309
2019-01-21 09:30 | 312 | 312
2019-01-21 10:00 | 309 | 308
2019-01-21 10:30 | 308 | 308
2019-01-21 11:00 | 310 | 310
2019-01-21 11:30 | 314 | 314
2019-01-21 12:00 | 320 | 320
2019-01-21 12:30 | 326 | 326
2019-01-21 13:00 | 335 | 335
2019-01-21 13:30 | 344 | 344
2019-01-21 14:00 | 352 | 352
2019-01-21 14:30 | 361 | 361
2019-01-21 15:00 | 370 | 369
2019-01-21 15:30 | 381 | 380
2019-01-21 16:00 | 392 | 392
2019-01-21 16:30 | 403 | 403
2019-01-21 17:00 | 413 | 413
2019-01-21 17:30 | 410 | 410
2019-01-21 18:00 | 402 | 402
2019-01-21 18:30 | 391 | 391
2019-01-21 19:00 | 389 | 389
2019-01-21 19:30 | 387 | 387
2019-01-21 20:00 | 382 | 382
2019-01-21 20:30 | 372 | 372
2019-01-21 21:00 | 352 | 352
2019-01-21 21:30 | 334 | 334
2019-01-21 22:00 | 317 | 317
2019-01-21 22:30 | 304 | 304
2019-01-21 23:00 | 290 | 290
2019-01-21 23:30 | 267 | 267
2019-01-22 | 244 | 244
2019-01-22 00:30 | 226 | 225
2019-01-22 01:00 | 216 | 215
2019-01-22 01:30 | 209 | 209
2019-01-22 02:00 | 204 | 204
2019-01-22 02:30 | 200 | 200
2019-01-22 03:00 | 197 | 197
2019-01-22 03:30 | 197 | 197
2019-01-22 04:00 | 196 | 196
2019-01-22 04:30 | 199 | 199
2019-01-22 05:00 | 205 | 205
2019-01-22 05:30 | 212 | 211
2019-01-22 06:00 | 221 | 221
2019-01-22 06:30 | 239 | 239
2019-01-22 07:00 | 256 | 255
2019-01-22 07:30 | 271 | 270
2019-01-22 08:00 | 286 | 286
2019-01-22 08:30 | 298 | 298
2019-01-22 09:00 | 303 | 303
2019-01-22 09:30 | 310 | 310
2019-01-22 10:00 | 288 | 288
2019-01-22 10:30 | 289 | 289
2019-01-22 11:00 | 292 | 292
2019-01-22 11:30 | 296 | 296
2019-01-22 12:00 | 298 | 298
2019-01-22 12:30 | 304 | 304
2019-01-22 13:00 | 311 | 310
2019-01-22 13:30 | 317 | 316
2019-01-22 14:00 | 325 | 324
2019-01-22 14:30 | 334 | 334
2019-01-22 15:00 | 339 | 339
2019-01-22 15:30 | 347 | 347
2019-01-22 16:00 | 360 | 360
2019-01-22 16:30 | 367 | 367
2019-01-22 17:00 | 374 | 374
2019-01-22 17:30 | 373 | 373
2019-01-22 18:00 | 353 | 353
2019-01-22 18:30 | 344 | 344
2019-01-22 19:00 | 346 | 346
2019-01-22 19:30 | 346 | 345
2019-01-22 20:00 | 339 | 339
2019-01-22 20:30 | 327 | 327
2019-01-22 21:00 | 308 | 308
2019-01-22 21:30 | 291 | 290
2019-01-22 22:00 | 277 | 274
2019-01-22 22:30 | 261 | 260
2019-01-22 23:00 | 247 | 247
2019-01-22 23:30 | 229 | 229
2019-01-23 | 213 | 213
2019-01-23 00:30 | 199 | 198
2019-01-23 01:00 | 190 | 189
2019-01-23 01:30 | 182 | 182
2019-01-23 02:00 | 178 | 178
2019-01-23 02:30 | 177 | 176
2019-01-23 03:00 | 174 | 174
2019-01-23 03:30 | 173 | 173
2019-01-23 04:00 | 172 | 172
2019-01-23 04:30 | 175 | 175
2019-01-23 05:00 | 180 | 180
2019-01-23 05:30 | 187 | 187
2019-01-23 06:00 | 195 | 195
2019-01-23 06:30 | 210 | 210
2019-01-23 07:00 | 223 | 223
2019-01-23 07:30 | 240 | 239
2019-01-23 08:00 | 252 | 250
2019-01-23 08:30 | 261 | 261
2019-01-23 09:00 | 268 | 268
2019-01-23 09:30 | 266 | 266
2019-01-23 10:00 | 267 | 267
2019-01-23 10:30 | 272 | 272
2019-01-23 11:00 | 276 | 276
2019-01-23 11:30 | 279 | 278
2019-01-23 12:00 | 291 | 290
2019-01-23 12:30 | 298 | 298
2019-01-23 13:00 | 303 | 303
2019-01-23 13:30 | 313 | 313
2019-01-23 14:00 | 322 | 322
2019-01-23 14:30 | 331 | 331
2019-01-23 15:00 | 341 | 341
2019-01-23 15:30 | 352 | 352
2019-01-23 16:00 | 369 | 369
2019-01-23 16:30 | 382 | 382
2019-01-23 17:00 | 384 | 384
2019-01-23 17:30 | 377 | 377
2019-01-23 18:00 | 366 | 365
2019-01-23 18:30 | 354 | 354
2019-01-23 19:00 | 352 | 352
2019-01-23 19:30 | 349 | 348
2019-01-23 20:00 | 343 | 343
2019-01-23 20:30 | 333 | 333
2019-01-23 21:00 | 315 | 315
2019-01-23 21:30 | 297 | 297
2019-01-23 22:00 | 281 | 281
2019-01-23 22:30 | 270 | 270
2019-01-23 23:00 | 258 | 258
2019-01-23 23:30 | 239 | 239
2019-01-24 | 221 | 221
2019-01-24 00:30 | 206 | 206
2019-01-24 01:00 | 198 | 198
2019-01-24 01:30 | 191 | 191
2019-01-24 02:00 | 186 | 186
2019-01-24 02:30 | 183 | 183
2019-01-24 03:00 | 180 | 180
2019-01-24 03:30 | 179 | 179
2019-01-24 04:00 | 177 | 177
2019-01-24 04:30 | 179 | 179
2019-01-24 05:00 | 182 | 182
2019-01-24 05:30 | 190 | 190
2019-01-24 06:00 | 197 | 197
2019-01-24 06:30 | 214 | 213
2019-01-24 07:00 | 228 | 228
2019-01-24 07:30 | 243 | 242
2019-01-24 08:00 | 251 | 251
2019-01-24 08:30 | 262 | 260
2019-01-24 09:00 | 267 | 266
2019-01-24 09:30 | 273 | 273
2019-01-24 10:00 | 279 | 279
2019-01-24 10:30 | 286 | 286
2019-01-24 11:00 | 289 | 289
2019-01-24 11:30 | 300 | 300
2019-01-24 12:00 | 307 | 307
2019-01-24 12:30 | 310 | 310
2019-01-24 13:00 | 314 | 314
2019-01-24 13:30 | 312 | 312
2019-01-24 14:00 | 319 | 318
2019-01-24 14:30 | 330 | 329
2019-01-24 15:00 | 339 | 339
2019-01-24 15:30 | 346 | 346
2019-01-24 16:00 | 357 | 356
2019-01-24 16:30 | 360 | 360
2019-01-24 17:00 | 366 | 366
2019-01-24 17:30 | 368 | 368
2019-01-24 18:00 | 367 | 367
2019-01-24 18:30 | 359 | 359
2019-01-24 19:00 | 356 | 356
2019-01-24 19:30 | 358 | 358
2019-01-24 20:00 | 354 | 354
2019-01-24 20:30 | 342 | 342
2019-01-24 21:00 | 327 | 326
2019-01-24 21:30 | 308 | 307
2019-01-24 22:00 | 293 | 290
2019-01-24 22:30 | 276 | 276
2019-01-24 23:00 | 260 | 260
2019-01-24 23:30 | 240 | 240
2019-01-25 | 223 | 222
2019-01-25 00:30 | 210 | 209
2019-01-25 01:00 | 203 | 202
2019-01-25 01:30 | 196 | 196
2019-01-25 02:00 | 192 | 191
2019-01-25 02:30 | 188 | 188
2019-01-25 03:00 | 186 | 185
2019-01-25 03:30 | 184 | 184
2019-01-25 04:00 | 183 | 183
2019-01-25 04:30 | 183 | 183
2019-01-25 05:00 | 188 | 187
2019-01-25 05:30 | 196 | 196
2019-01-25 06:00 | 206 | 206
2019-01-25 06:30 | 222 | 222
2019-01-25 07:00 | 235 | 235
2019-01-25 07:30 | 252 | 252
2019-01-25 08:00 | 264 | 264
2019-01-25 08:30 | 276 | 276
2019-01-25 09:00 | 284 | 284
2019-01-25 09:30 | 284 | 284
2019-01-25 10:00 | 286 | 285
2019-01-25 10:30 | 294 | 294
2019-01-25 11:00 | 290 | 289
2019-01-25 11:30 | 276 | 276
2019-01-25 12:00 | 280 | 280
2019-01-25 12:30 | 288 | 288
2019-01-25 13:00 | 294 | 293
2019-01-25 13:30 | 303 | 303
2019-01-25 14:00 | 309 | 308
2019-01-25 14:30 | 320 | 320
2019-01-25 15:00 | 329 | 329
2019-01-25 15:30 | 336 | 336
2019-01-25 16:00 | 344 | 344
2019-01-25 16:30 | 351 | 351
2019-01-25 17:00 | 361 | 361
2019-01-25 17:30 | 360 | 360
2019-01-25 18:00 | 354 | 354
2019-01-25 18:30 | 345 | 345
2019-01-25 19:00 | 343 | 343
2019-01-25 19:30 | 343 | 343
2019-01-25 20:00 | 339 | 338
2019-01-25 20:30 | 324 | 324
2019-01-25 21:00 | 310 | 310
2019-01-25 21:30 | 295 | 295
2019-01-25 22:00 | 281 | 281
2019-01-25 22:30 | 271 | 271
2019-01-25 23:00 | 260 | 260
2019-01-25 23:30 | 238 | 238
2019-01-26 | 220 | 220
2019-01-26 00:30 | 206 | 206
2019-01-26 01:00 | 196 | 196
2019-01-26 01:30 | 190 | 189
2019-01-26 02:00 | 184 | 183
2019-01-26 02:30 | 180 | 179
2019-01-26 03:00 | 176 | 176
2019-01-26 03:30 | 174 | 173
2019-01-26 04:00 | 170 | 170
2019-01-26 04:30 | 170 | 170
2019-01-26 05:00 | 171 | 171
2019-01-26 05:30 | 171 | 171
2019-01-26 06:00 | 172 | 172
2019-01-26 06:30 | 176 | 176
2019-01-26 07:00 | 180 | 180
2019-01-26 07:30 | 188 | 188
2019-01-26 08:00 | 193 | 192
2019-01-26 08:30 | 199 | 198
2019-01-26 09:00 | 206 | 204
2019-01-26 09:30 | 212 | 212
2019-01-26 10:00 | 210 | 210
2019-01-26 10:30 | 209 | 209
2019-01-26 11:00 | 212 | 212
2019-01-26 11:30 | 217 | 217
2019-01-26 12:00 | 221 | 221
2019-01-26 12:30 | 222 | 222
2019-01-26 13:00 | 225 | 224
2019-01-26 13:30 | 229 | 229
2019-01-26 14:00 | 234 | 233
2019-01-26 14:30 | 240 | 239
2019-01-26 15:00 | 251 | 250
2019-01-26 15:30 | 262 | 262
2019-01-26 16:00 | 277 | 277
2019-01-26 16:30 | 286 | 286
2019-01-26 17:00 | 298 | 298
2019-01-26 17:30 | 300 | 300
2019-01-26 18:00 | 296 | 296
2019-01-26 18:30 | 292 | 292
2019-01-26 19:00 | 289 | 289
2019-01-26 19:30 | 288 | 288
2019-01-26 20:00 | 284 | 283
2019-01-26 20:30 | 274 | 274
2019-01-26 21:00 | 262 | 260
2019-01-26 21:30 | 253 | 252
2019-01-26 22:00 | 243 | 242
2019-01-26 22:30 | 238 | 237
2019-01-26 23:00 | 232 | 230
2019-01-26 23:30 | 216 | 215
2019-01-27 | 200 | 199
2019-01-27 00:30 | 185 | 185
2019-01-27 01:00 | 177 | 177
2019-01-27 01:30 | 172 | 172
2019-01-27 02:00 | 167 | 167
2019-01-27 02:30 | 163 | 163
2019-01-27 03:00 | 160 | 160
2019-01-27 03:30 | 158 | 158
2019-01-27 04:00 | 157 | 157
2019-01-27 04:30 | 156 | 156
2019-01-27 05:00 | 155 | 155
2019-01-27 05:30 | 154 | 154
2019-01-27 06:00 | 153 | 152
2019-01-27 06:30 | 154 | 154
2019-01-27 07:00 | 155 | 155
2019-01-27 07:30 | 160 | 160
2019-01-27 08:00 | 164 | 164
2019-01-27 08:30 | 172 | 171
2019-01-27 09:00 | 176 | 175
2019-01-27 09:30 | 179 | 178
2019-01-27 10:00 | 180 | 178
2019-01-27 10:30 | 177 | 175
2019-01-27 11:00 | 179 | 177
2019-01-27 11:30 | 183 | 180
2019-01-27 12:00 | 190 | 187
2019-01-27 12:30 | 194 | 192
2019-01-27 13:00 | 203 | 201
2019-01-27 13:30 | 212 | 209
2019-01-27 14:00 | 223 | 221
2019-01-27 14:30 | 233 | 233
2019-01-27 15:00 | 245 | 244
2019-01-27 15:30 | 256 | 255
2019-01-27 16:00 | 269 | 269
2019-01-27 16:30 | 282 | 282
2019-01-27 17:00 | 292 | 292
2019-01-27 17:30 | 297 | 297
2019-01-27 18:00 | 296 | 296
2019-01-27 18:30 | 294 | 294
2019-01-27 19:00 | 292 | 291
2019-01-27 19:30 | 291 | 291
2019-01-27 20:00 | 289 | 289
2019-01-27 20:30 | 279 | 279
2019-01-27 21:00 | 267 | 266
2019-01-27 21:30 | 258 | 257
2019-01-27 22:00 | 248 | 248
2019-01-27 22:30 | 242 | 242
2019-01-27 23:00 | 234 | 234
2019-01-27 23:30 | 216 | 216
2019-01-28 | 200 | 199
2019-01-28 00:30 | 186 | 185
2019-01-28 01:00 | 179 | 178
2019-01-28 01:30 | 173 | 173
2019-01-28 02:00 | 167 | 167
2019-01-28 02:30 | 165 | 165
2019-01-28 03:00 | 163 | 163
2019-01-28 03:30 | 163 | 163
2019-01-28 04:00 | 161 | 161
2019-01-28 04:30 | 159 | 159
2019-01-28 05:00 | 160 | 160
2019-01-28 05:30 | 163 | 163
2019-01-28 06:00 | 162 | 162
2019-01-28 06:30 | 164 | 164
2019-01-28 07:00 | 169 | 169
2019-01-28 07:30 | 178 | 177
2019-01-28 08:00 | 186 | 184
2019-01-28 08:30 | 193 | 192
2019-01-28 09:00 | 198 | 196
2019-01-28 09:30 | 201 | 199
2019-01-28 10:00 | 205 | 201
2019-01-28 10:30 | 207 | 206
2019-01-28 11:00 | 210 | 208
2019-01-28 11:30 | 212 | 210
2019-01-28 12:00 | 214 | 212
2019-01-28 12:30 | 218 | 216
2019-01-28 13:00 | 227 | 224
2019-01-28 13:30 | 234 | 233
2019-01-28 14:00 | 244 | 242
2019-01-28 14:30 | 255 | 254
2019-01-28 15:00 | 265 | 264
2019-01-28 15:30 | 277 | 276
2019-01-28 16:00 | 291 | 289
2019-01-28 16:30 | 307 | 305
2019-01-28 17:00 | 320 | 318
2019-01-28 17:30 | 328 | 326
2019-01-28 18:00 | 327 | 324
2019-01-28 18:30 | 322 | 319
2019-01-28 19:00 | 321 | 318
2019-01-28 19:30 | 323 | 319
2019-01-28 20:00 | 319 | 316
2019-01-28 20:30 | 308 | 306
2019-01-28 21:00 | 292 | 290
2019-01-28 21:30 | 278 | 276
2019-01-28 22:00 | 265 | 264
2019-01-28 22:30 | 253 | 253
2019-01-28 23:00 | 242 | 241
2019-01-28 23:30 | 225 | 224
2019-01-29 | 209 | 208
2019-01-29 00:30 | 193 | 192
2019-01-29 01:00 | 188 | 187
2019-01-29 01:30 | 182 | 182
2019-01-29 02:00 | 178 | 178
2019-01-29 02:30 | 176 | 176
2019-01-29 03:00 | 173 | 173
2019-01-29 03:30 | 172 | 172
2019-01-29 04:00 | 171 | 171
2019-01-29 04:30 | 174 | 173
2019-01-29 05:00 | 178 | 178
2019-01-29 05:30 | 186 | 186
2019-01-29 06:00 | 195 | 194
2019-01-29 06:30 | 216 | 215
2019-01-29 07:00 | 234 | 233
2019-01-29 07:30 | 250 | 250
2019-01-29 08:00 | 260 | 260
2019-01-29 08:30 | 268 | 267
2019-01-29 09:00 | 271 | 270
2019-01-29 09:30 | 276 | 276
2019-01-29 10:00 | 280 | 280
2019-01-29 10:30 | 280 | 280
2019-01-29 11:00 | 277 | 277
2019-01-29 11:30 | 278 | 278
2019-01-29 12:00 | 283 | 282
2019-01-29 12:30 | 283 | 283
2019-01-29 13:00 | 287 | 286
2019-01-29 13:30 | 293 | 292
2019-01-29 14:00 | 292 | 292
2019-01-29 14:30 | 297 | 296
2019-01-29 15:00 | 304 | 303
2019-01-29 15:30 | 315 | 314
2019-01-29 16:00 | 330 | 329
2019-01-29 16:30 | 343 | 342
2019-01-29 17:00 | 360 | 359
2019-01-29 17:30 | 363 | 362
2019-01-29 18:00 | 357 | 357
2019-01-29 18:30 | 348 | 348
2019-01-29 19:00 | 351 | 350
2019-01-29 19:30 | 349 | 349
2019-01-29 20:00 | 344 | 344
2019-01-29 20:30 | 331 | 331
2019-01-29 21:00 | 314 | 314
2019-01-29 21:30 | 297 | 297
2019-01-29 22:00 | 281 | 281
2019-01-29 22:30 | 268 | 268
2019-01-29 23:00 | 255 | 255
2019-01-29 23:30 | 234 | 234
2019-01-30 | 217 | 217
2019-01-30 00:30 | 203 | 203
2019-01-30 01:00 | 196 | 196
2019-01-30 01:30 | 191 | 190
2019-01-30 02:00 | 187 | 186
2019-01-30 02:30 | 184 | 183
2019-01-30 03:00 | 181 | 181
2019-01-30 03:30 | 180 | 180
2019-01-30 04:00 | 179 | 179
2019-01-30 04:30 | 182 | 182
2019-01-30 05:00 | 187 | 187
2019-01-30 05:30 | 196 | 196
2019-01-30 06:00 | 204 | 204
2019-01-30 06:30 | 223 | 222
2019-01-30 07:00 | 241 | 240
2019-01-30 07:30 | 259 | 259
2019-01-30 08:00 | 270 | 270
2019-01-30 08:30 | 282 | 282
2019-01-30 09:00 | 283 | 283
2019-01-30 09:30 | 279 | 279
2019-01-30 10:00 | 268 | 268
2019-01-30 10:30 | 261 | 261
2019-01-30 11:00 | 263 | 263
2019-01-30 11:30 | 270 | 269
2019-01-30 12:00 | 281 | 280
2019-01-30 12:30 | 289 | 288
2019-01-30 13:00 | 293 | 292
2019-01-30 13:30 | 299 | 299
2019-01-30 14:00 | 312 | 311
2019-01-30 14:30 | 319 | 318
2019-01-30 15:00 | 321 | 320
2019-01-30 15:30 | 328 | 327
2019-01-30 16:00 | 335 | 335
2019-01-30 16:30 | 344 | 343
2019-01-30 17:00 | 352 | 351
2019-01-30 17:30 | 346 | 346
2019-01-30 18:00 | 339 | 339
2019-01-30 18:30 | 331 | 330
2019-01-30 19:00 | 338 | 336
2019-01-30 19:30 | 341 | 341
2019-01-30 20:00 | 336 | 336
2019-01-30 20:30 | 325 | 325
2019-01-30 21:00 | 311 | 310
2019-01-30 21:30 | 295 | 295
2019-01-30 22:00 | 278 | 277
2019-01-30 22:30 | 266 | 265
2019-01-30 23:00 | 253 | 253
2019-01-30 23:30 | 233 | 233
2019-01-31 | 214 | 214
2019-01-31 00:30 | 200 | 200
2019-01-31 01:00 | 193 | 193
2019-01-31 01:30 | 188 | 188
2019-01-31 02:00 | 184 | 184
2019-01-31 02:30 | 181 | 181
2019-01-31 03:00 | 179 | 179
2019-01-31 03:30 | 178 | 178
2019-01-31 04:00 | 177 | 177
2019-01-31 04:30 | 179 | 179
2019-01-31 05:00 | 184 | 184
2019-01-31 05:30 | 192 | 192
2019-01-31 06:00 | 199 | 199
2019-01-31 06:30 | 216 | 216
2019-01-31 07:00 | 231 | 229
2019-01-31 07:30 | 248 | 248
2019-01-31 08:00 | 256 | 255
2019-01-31 08:30 | 261 | 260
2019-01-31 09:00 | 266 | 265
2019-01-31 09:30 | 271 | 270
2019-01-31 10:00 | 274 | 274
2019-01-31 10:30 | 278 | 278
2019-01-31 11:00 | 280 | 279
2019-01-31 11:30 | 282 | 281
2019-01-31 12:00 | 286 | 285
2019-01-31 12:30 | 291 | 289
2019-01-31 13:00 | 299 | 297
2019-01-31 13:30 | 306 | 305
2019-01-31 14:00 | 311 | 311
2019-01-31 14:30 | 316 | 316
2019-01-31 15:00 | 327 | 327
2019-01-31 15:30 | 331 | 331
2019-01-31 16:00 | 341 | 341
2019-01-31 16:30 | 358 | 358
2019-01-31 17:00 | 365 | 365
2019-01-31 17:30 | 361 | 361
2019-01-31 18:00 | 362 | 362
2019-01-31 18:30 | 355 | 355
2019-01-31 19:00 | 357 | 357
2019-01-31 19:30 | 356 | 356
2019-01-31 20:00 | 351 | 351
2019-01-31 20:30 | 340 | 339
2019-01-31 21:00 | 321 | 321
2019-01-31 21:30 | 302 | 302
2019-01-31 22:00 | 283 | 283
2019-01-31 22:30 | 270 | 270
2019-01-31 23:00 | 258 | 258
2019-01-31 23:30 | 239 | 239
2019-02-01 | 221 | 221
2019-02-01 00:30 | 205 | 204
2019-02-01 01:00 | 196 | 196
2019-02-01 01:30 | 190 | 190
2019-02-01 02:00 | 185 | 185
2019-02-01 02:30 | 181 | 180
2019-02-01 03:00 | 178 | 178
2019-02-01 03:30 | 178 | 177
2019-02-01 04:00 | 176 | 175
2019-02-01 04:30 | 177 | 176
2019-02-01 05:00 | 181 | 181
2019-02-01 05:30 | 189 | 189
2019-02-01 06:00 | 195 | 195
2019-02-01 06:30 | 213 | 213
2019-02-01 07:00 | 227 | 227
2019-02-01 07:30 | 239 | 239
2019-02-01 08:00 | 249 | 249
2019-02-01 08:30 | 252 | 252
2019-02-01 09:00 | 255 | 255
2019-02-01 09:30 | 259 | 259
2019-02-01 10:00 | 261 | 261
2019-02-01 10:30 | 263 | 263
2019-02-01 11:00 | 266 | 266
2019-02-01 11:30 | 265 | 265
2019-02-01 12:00 | 267 | 267
2019-02-01 12:30 | 272 | 271
2019-02-01 13:00 | 278 | 278
2019-02-01 13:30 | 283 | 283
2019-02-01 14:00 | 290 | 290
2019-02-01 14:30 | 308 | 308
2019-02-01 15:00 | 309 | 309
2019-02-01 15:30 | 317 | 317
2019-02-01 16:00 | 331 | 330
2019-02-01 16:30 | 336 | 336
2019-02-01 17:00 | 336 | 336
2019-02-01 17:30 | 325 | 325
2019-02-01 18:00 | 313 | 313
2019-02-01 18:30 | 305 | 305
2019-02-01 19:00 | 310 | 309
2019-02-01 19:30 | 310 | 310
2019-02-01 20:00 | 304 | 304
2019-02-01 20:30 | 298 | 298
2019-02-01 21:00 | 287 | 287
2019-02-01 21:30 | 278 | 278
2019-02-01 22:00 | 266 | 265
2019-02-01 22:30 | 257 | 256
2019-02-01 23:00 | 247 | 245
2019-02-01 23:30 | 224 | 224
2019-02-02 | 207 | 207
2019-02-02 00:30 | 193 | 192
2019-02-02 01:00 | 186 | 185
2019-02-02 01:30 | 180 | 179
2019-02-02 02:00 | 175 | 173
2019-02-02 02:30 | 172 | 170
2019-02-02 03:00 | 169 | 167
2019-02-02 03:30 | 168 | 165
2019-02-02 04:00 | 166 | 163
2019-02-02 04:30 | 166 | 163
2019-02-02 05:00 | 166 | 163
2019-02-02 05:30 | 167 | 164
2019-02-02 06:00 | 167 | 164
2019-02-02 06:30 | 172 | 169
2019-02-02 07:00 | 174 | 172
2019-02-02 07:30 | 178 | 177
2019-02-02 08:00 | 186 | 185
2019-02-02 08:30 | 200 | 200
2019-02-02 09:00 | 198 | 198
2019-02-02 09:30 | 198 | 197
2019-02-02 10:00 | 201 | 200
2019-02-02 10:30 | 201 | 200
2019-02-02 11:00 | 202 | 201
2019-02-02 11:30 | 191 | 190
2019-02-02 12:00 | 204 | 203
2019-02-02 12:30 | 211 | 210
2019-02-02 13:00 | 209 | 208
2019-02-02 13:30 | 211 | 210
2019-02-02 14:00 | 226 | 224
2019-02-02 14:30 | 231 | 230
2019-02-02 15:00 | 225 | 224
2019-02-02 15:30 | 236 | 234
2019-02-02 16:00 | 248 | 246
2019-02-02 16:30 | 250 | 250
2019-02-02 17:00 | 261 | 261
2019-02-02 17:30 | 266 | 266
2019-02-02 18:00 | 262 | 262
2019-02-02 18:30 | 266 | 266
2019-02-02 19:00 | 272 | 272
2019-02-02 19:30 | 274 | 274
2019-02-02 20:00 | 271 | 271
2019-02-02 20:30 | 264 | 264
2019-02-02 21:00 | 253 | 253
2019-02-02 21:30 | 245 | 245
2019-02-02 22:00 | 236 | 236
2019-02-02 22:30 | 231 | 231
2019-02-02 23:00 | 226 | 226
2019-02-02 23:30 | 209 | 209
2019-02-03 | 192 | 192
2019-02-03 00:30 | 178 | 178
2019-02-03 01:00 | 171 | 171
2019-02-03 01:30 | 166 | 166
2019-02-03 02:00 | 161 | 161
2019-02-03 02:30 | 158 | 158
2019-02-03 03:00 | 154 | 154
2019-02-03 03:30 | 154 | 154
2019-02-03 04:00 | 152 | 152
2019-02-03 04:30 | 152 | 152
2019-02-03 05:00 | 152 | 151
2019-02-03 05:30 | 151 | 150
2019-02-03 06:00 | 150 | 150
2019-02-03 06:30 | 155 | 155
2019-02-03 07:00 | 158 | 158
2019-02-03 07:30 | 162 | 162
2019-02-03 08:00 | 165 | 165
2019-02-03 08:30 | 172 | 172
2019-02-03 09:00 | 177 | 176
2019-02-03 09:30 | 183 | 183
2019-02-03 10:00 | 188 | 188
2019-02-03 10:30 | 194 | 193
2019-02-03 11:00 | 190 | 189
2019-02-03 11:30 | 184 | 184
2019-02-03 12:00 | 188 | 187
2019-02-03 12:30 | 179 | 178
2019-02-03 13:00 | 174 | 173
2019-02-03 13:30 | 176 | 175
2019-02-03 14:00 | 184 | 184
2019-02-03 14:30 | 192 | 191
2019-02-03 15:00 | 204 | 203
2019-02-03 15:30 | 217 | 215
2019-02-03 16:00 | 232 | 230
2019-02-03 16:30 | 245 | 243
2019-02-03 17:00 | 255 | 252
2019-02-03 17:30 | 263 | 263
2019-02-03 18:00 | 265 | 265
2019-02-03 18:30 | 267 | 267
2019-02-03 19:00 | 273 | 273
2019-02-03 19:30 | 276 | 275
2019-02-03 20:00 | 272 | 272
2019-02-03 20:30 | 265 | 264
2019-02-03 21:00 | 253 | 253
2019-02-03 21:30 | 241 | 241
2019-02-03 22:00 | 231 | 231
2019-02-03 22:30 | 226 | 226
2019-02-03 23:00 | 219 | 218
2019-02-03 23:30 | 202 | 201
2019-02-04 | 185 | 185
2019-02-04 00:30 | 171 | 171
2019-02-04 01:00 | 165 | 165
2019-02-04 01:30 | 162 | 162
2019-02-04 02:00 | 158 | 158
2019-02-04 02:30 | 155 | 155
2019-02-04 03:00 | 153 | 153
2019-02-04 03:30 | 155 | 155
2019-02-04 04:00 | 158 | 158
2019-02-04 04:30 | 162 | 162
2019-02-04 05:00 | 168 | 168
2019-02-04 05:30 | 177 | 177
2019-02-04 06:00 | 186 | 186
2019-02-04 06:30 | 207 | 206
2019-02-04 07:00 | 225 | 224
2019-02-04 07:30 | 244 | 244
2019-02-04 08:00 | 247 | 247
2019-02-04 08:30 | 249 | 249
2019-02-04 09:00 | 253 | 253
2019-02-04 09:30 | 252 | 252
2019-02-04 10:00 | 247 | 247
2019-02-04 10:30 | 242 | 242
2019-02-04 11:00 | 235 | 235
2019-02-04 11:30 | 230 | 230
2019-02-04 12:00 | 231 | 231
2019-02-04 12:30 | 236 | 236
2019-02-04 13:00 | 243 | 243
2019-02-04 13:30 | 246 | 246
2019-02-04 14:00 | 251 | 251
2019-02-04 14:30 | 255 | 254
2019-02-04 15:00 | 258 | 258
2019-02-04 15:30 | 267 | 266
2019-02-04 16:00 | 287 | 286
2019-02-04 16:30 | 298 | 297
2019-02-04 17:00 | 308 | 307
2019-02-04 17:30 | 311 | 311
2019-02-04 18:00 | 310 | 310
2019-02-04 18:30 | 305 | 305
2019-02-04 19:00 | 307 | 307
2019-02-04 19:30 | 310 | 310
2019-02-04 20:00 | 306 | 306
2019-02-04 20:30 | 298 | 298
2019-02-04 21:00 | 284 | 284
2019-02-04 21:30 | 269 | 269
2019-02-04 22:00 | 258 | 258
2019-02-04 22:30 | 248 | 248
2019-02-04 23:00 | 238 | 238
2019-02-04 23:30 | 220 | 220
2019-02-05 | 201 | 200
2019-02-05 00:30 | 187 | 186
2019-02-05 01:00 | 179 | 179
2019-02-05 01:30 | 174 | 174
2019-02-05 02:00 | 170 | 170
2019-02-05 02:30 | 168 | 168
2019-02-05 03:00 | 166 | 166
2019-02-05 03:30 | 165 | 165
2019-02-05 04:00 | 166 | 166
2019-02-05 04:30 | 168 | 168
2019-02-05 05:00 | 174 | 174
2019-02-05 05:30 | 183 | 183
2019-02-05 06:00 | 192 | 191
2019-02-05 06:30 | 210 | 208
2019-02-05 07:00 | 227 | 226
2019-02-05 07:30 | 240 | 240
2019-02-05 08:00 | 246 | 246
2019-02-05 08:30 | 250 | 250
2019-02-05 09:00 | 255 | 255
2019-02-05 09:30 | 250 | 250
2019-02-05 10:00 | 240 | 240
2019-02-05 10:30 | 237 | 237
2019-02-05 11:00 | 239 | 239
2019-02-05 11:30 | 238 | 238
2019-02-05 12:00 | 239 | 239
2019-02-05 12:30 | 241 | 240
2019-02-05 13:00 | 253 | 252
2019-02-05 13:30 | 267 | 266
2019-02-05 14:00 | 277 | 276
2019-02-05 14:30 | 276 | 275
2019-02-05 15:00 | 278 | 278
2019-02-05 15:30 | 285 | 285
2019-02-05 16:00 | 285 | 284
2019-02-05 16:30 | 298 | 298
2019-02-05 17:00 | 310 | 310
2019-02-05 17:30 | 307 | 307
2019-02-05 18:00 | 303 | 303
2019-02-05 18:30 | 300 | 300
2019-02-05 19:00 | 305 | 304
2019-02-05 19:30 | 301 | 301
2019-02-05 20:00 | 296 | 296
2019-02-05 20:30 | 288 | 286
2019-02-05 21:00 | 274 | 273
2019-02-05 21:30 | 261 | 260
2019-02-05 22:00 | 251 | 250
2019-02-05 22:30 | 244 | 244
2019-02-05 23:00 | 235 | 233
2019-02-05 23:30 | 218 | 217
2019-02-06 | 201 | 200
2019-02-06 00:30 | 188 | 188
2019-02-06 01:00 | 183 | 182
2019-02-06 01:30 | 177 | 176
2019-02-06 02:00 | 173 | 172
2019-02-06 02:30 | 172 | 171
2019-02-06 03:00 | 168 | 168
2019-02-06 03:30 | 168 | 167
2019-02-06 04:00 | 169 | 168
2019-02-06 04:30 | 171 | 170
2019-02-06 05:00 | 178 | 176
2019-02-06 05:30 | 188 | 187
2019-02-06 06:00 | 197 | 196
2019-02-06 06:30 | 217 | 217
2019-02-06 07:00 | 235 | 235
2019-02-06 07:30 | 251 | 251
2019-02-06 08:00 | 252 | 252
2019-02-06 08:30 | 247 | 247
2019-02-06 09:00 | 243 | 242
2019-02-06 09:30 | 248 | 247
2019-02-06 10:00 | 243 | 243
2019-02-06 10:30 | 256 | 256
2019-02-06 11:00 | 253 | 253
2019-02-06 11:30 | 259 | 259
2019-02-06 12:00 | 255 | 255
2019-02-06 12:30 | 251 | 251
2019-02-06 13:00 | 248 | 248
2019-02-06 13:30 | 240 | 240
2019-02-06 14:00 | 252 | 252
2019-02-06 14:30 | 256 | 256
2019-02-06 15:00 | 258 | 258
2019-02-06 15:30 | 264 | 264
2019-02-06 16:00 | 279 | 279
2019-02-06 16:30 | 291 | 290
2019-02-06 17:00 | 301 | 301
2019-02-06 17:30 | 301 | 301
2019-02-06 18:00 | 302 | 301
2019-02-06 18:30 | 297 | 297
2019-02-06 19:00 | 303 | 303
2019-02-06 19:30 | 304 | 304
2019-02-06 20:00 | 300 | 300
2019-02-06 20:30 | 291 | 291
2019-02-06 21:00 | 283 | 283
2019-02-06 21:30 | 269 | 269
2019-02-06 22:00 | 259 | 258
2019-02-06 22:30 | 249 | 248
2019-02-06 23:00 | 238 | 238
2019-02-06 23:30 | 222 | 222
2019-02-07 | 204 | 204
2019-02-07 00:30 | 190 | 190
2019-02-07 01:00 | 183 | 183
2019-02-07 01:30 | 178 | 178
2019-02-07 02:00 | 174 | 174
2019-02-07 02:30 | 171 | 171
2019-02-07 03:00 | 170 | 170
2019-02-07 03:30 | 170 | 170
2019-02-07 04:00 | 169 | 169
2019-02-07 04:30 | 172 | 172
2019-02-07 05:00 | 177 | 177
2019-02-07 05:30 | 187 | 186
2019-02-07 06:00 | 194 | 194
2019-02-07 06:30 | 210 | 209
2019-02-07 07:00 | 227 | 225
2019-02-07 07:30 | 242 | 241
2019-02-07 08:00 | 251 | 251
2019-02-07 08:30 | 247 | 246
2019-02-07 09:00 | 249 | 248
2019-02-07 09:30 | 246 | 246
2019-02-07 10:00 | 243 | 242
2019-02-07 10:30 | 244 | 243
2019-02-07 11:00 | 244 | 244
2019-02-07 11:30 | 261 | 260
2019-02-07 12:00 | 264 | 263
2019-02-07 12:30 | 255 | 254
2019-02-07 13:00 | 259 | 258
2019-02-07 13:30 | 270 | 269
2019-02-07 14:00 | 282 | 281
2019-02-07 14:30 | 279 | 277
2019-02-07 15:00 | 274 | 273
2019-02-07 15:30 | 295 | 294
2019-02-07 16:00 | 296 | 295
2019-02-07 16:30 | 294 | 294
2019-02-07 17:00 | 295 | 294
2019-02-07 17:30 | 294 | 294
2019-02-07 18:00 | 296 | 296
2019-02-07 18:30 | 297 | 297
2019-02-07 19:00 | 304 | 304
2019-02-07 19:30 | 305 | 304
2019-02-07 20:00 | 303 | 303
2019-02-07 20:30 | 296 | 296
2019-02-07 21:00 | 283 | 283
2019-02-07 21:30 | 267 | 267
2019-02-07 22:00 | 253 | 253
2019-02-07 22:30 | 245 | 245
2019-02-07 23:00 | 236 | 236
2019-02-07 23:30 | 220 | 219
2019-02-08 | 203 | 203
2019-02-08 00:30 | 189 | 189
2019-02-08 01:00 | 182 | 182
2019-02-08 01:30 | 178 | 178
2019-02-08 02:00 | 175 | 174
2019-02-08 02:30 | 172 | 172
2019-02-08 03:00 | 171 | 170
2019-02-08 03:30 | 170 | 170
2019-02-08 04:00 | 171 | 170
2019-02-08 04:30 | 173 | 173
2019-02-08 05:00 | 178 | 178
2019-02-08 05:30 | 189 | 189
2019-02-08 06:00 | 197 | 197
2019-02-08 06:30 | 218 | 218
2019-02-08 07:00 | 237 | 237
2019-02-08 07:30 | 253 | 253
2019-02-08 08:00 | 260 | 260
2019-02-08 08:30 | 263 | 262
2019-02-08 09:00 | 263 | 263
2019-02-08 09:30 | 263 | 263
2019-02-08 10:00 | 255 | 255
2019-02-08 10:30 | 251 | 251
2019-02-08 11:00 | 246 | 246
2019-02-08 11:30 | 243 | 243
2019-02-08 12:00 | 249 | 249
2019-02-08 12:30 | 253 | 253
2019-02-08 13:00 | 253 | 253
2019-02-08 13:30 | 255 | 255
2019-02-08 14:00 | 261 | 261
2019-02-08 14:30 | 268 | 267
2019-02-08 15:00 | 273 | 272
2019-02-08 15:30 | 282 | 282
2019-02-08 16:00 | 300 | 299
2019-02-08 16:30 | 306 | 305
2019-02-08 17:00 | 313 | 312
2019-02-08 17:30 | 314 | 313
2019-02-08 18:00 | 308 | 308
2019-02-08 18:30 | 302 | 302
2019-02-08 19:00 | 306 | 305
2019-02-08 19:30 | 307 | 307
2019-02-08 20:00 | 305 | 305
2019-02-08 20:30 | 298 | 298
2019-02-08 21:00 | 286 | 286
2019-02-08 21:30 | 274 | 274
2019-02-08 22:00 | 264 | 264
2019-02-08 22:30 | 257 | 257
2019-02-08 23:00 | 249 | 249
2019-02-08 23:30 | 231 | 231
2019-02-09 | 211 | 211
2019-02-09 00:30 | 196 | 196
2019-02-09 01:00 | 187 | 187
2019-02-09 01:30 | 180 | 180
2019-02-09 02:00 | 173 | 173
2019-02-09 02:30 | 171 | 171
2019-02-09 03:00 | 171 | 171
2019-02-09 03:30 | 169 | 169
2019-02-09 04:00 | 165 | 165
2019-02-09 04:30 | 163 | 163
2019-02-09 05:00 | 164 | 164
2019-02-09 05:30 | 165 | 165
2019-02-09 06:00 | 166 | 166
2019-02-09 06:30 | 169 | 169
2019-02-09 07:00 | 173 | 173
2019-02-09 07:30 | 180 | 180
2019-02-09 08:00 | 186 | 185
2019-02-09 08:30 | 200 | 199
2019-02-09 09:00 | 204 | 202
2019-02-09 09:30 | 206 | 204
2019-02-09 10:00 | 212 | 209
2019-02-09 10:30 | 212 | 210
2019-02-09 11:00 | 220 | 218
2019-02-09 11:30 | 224 | 222
2019-02-09 12:00 | 224 | 222
2019-02-09 12:30 | 227 | 224
2019-02-09 13:00 | 235 | 235
2019-02-09 13:30 | 240 | 240
2019-02-09 14:00 | 247 | 246
2019-02-09 14:30 | 254 | 254
2019-02-09 15:00 | 265 | 264
2019-02-09 15:30 | 274 | 273
2019-02-09 16:00 | 285 | 284
2019-02-09 16:30 | 299 | 299
2019-02-09 17:00 | 308 | 307
2019-02-09 17:30 | 313 | 313
2019-02-09 18:00 | 312 | 312
2019-02-09 18:30 | 311 | 311
2019-02-09 19:00 | 311 | 311
2019-02-09 19:30 | 310 | 310
2019-02-09 20:00 | 305 | 305
2019-02-09 20:30 | 297 | 297
2019-02-09 21:00 | 284 | 284
2019-02-09 21:30 | 274 | 273
2019-02-09 22:00 | 264 | 263
2019-02-09 22:30 | 258 | 257
2019-02-09 23:00 | 247 | 247
2019-02-09 23:30 | 226 | 226
2019-02-10 | 209 | 208
2019-02-10 00:30 | 193 | 193
2019-02-10 01:00 | 184 | 184
2019-02-10 01:30 | 178 | 178
2019-02-10 02:00 | 173 | 173
2019-02-10 02:30 | 169 | 169
2019-02-10 03:00 | 165 | 165
2019-02-10 03:30 | 163 | 163
2019-02-10 04:00 | 160 | 160
2019-02-10 04:30 | 158 | 158
2019-02-10 05:00 | 157 | 157
2019-02-10 05:30 | 157 | 157
2019-02-10 06:00 | 157 | 157
2019-02-10 06:30 | 159 | 159
2019-02-10 07:00 | 160 | 160
2019-02-10 07:30 | 165 | 165
2019-02-10 08:00 | 169 | 169
2019-02-10 08:30 | 176 | 175
2019-02-10 09:00 | 190 | 188
2019-02-10 09:30 | 203 | 201
2019-02-10 10:00 | 219 | 219
2019-02-10 10:30 | 226 | 226
2019-02-10 11:00 | 224 | 224
2019-02-10 11:30 | 227 | 227
2019-02-10 12:00 | 229 | 229
2019-02-10 12:30 | 231 | 231
2019-02-10 13:00 | 235 | 235
2019-02-10 13:30 | 241 | 241
2019-02-10 14:00 | 248 | 248
2019-02-10 14:30 | 256 | 255
2019-02-10 15:00 | 264 | 263
2019-02-10 15:30 | 273 | 272
2019-02-10 16:00 | 285 | 284
2019-02-10 16:30 | 292 | 291
2019-02-10 17:00 | 294 | 294
2019-02-10 17:30 | 301 | 300
2019-02-10 18:00 | 300 | 299
2019-02-10 18:30 | 300 | 298
2019-02-10 19:00 | 303 | 301
2019-02-10 19:30 | 299 | 297
2019-02-10 20:00 | 294 | 292
2019-02-10 20:30 | 286 | 284
2019-02-10 21:00 | 271 | 271
2019-02-10 21:30 | 260 | 260
2019-02-10 22:00 | 251 | 250
2019-02-10 22:30 | 243 | 243
2019-02-10 23:00 | 236 | 235
2019-02-10 23:30 | 219 | 219
2019-02-11 | 202 | 201
2019-02-11 00:30 | 189 | 188
2019-02-11 01:00 | 181 | 181
2019-02-11 01:30 | 177 | 177
2019-02-11 02:00 | 173 | 173
2019-02-11 02:30 | 171 | 171
2019-02-11 03:00 | 169 | 169
2019-02-11 03:30 | 168 | 168
2019-02-11 04:00 | 168 | 168
2019-02-11 04:30 | 170 | 170
2019-02-11 05:00 | 177 | 177
2019-02-11 05:30 | 190 | 189
2019-02-11 06:00 | 199 | 198
2019-02-11 06:30 | 220 | 220
2019-02-11 07:00 | 240 | 240
2019-02-11 07:30 | 268 | 268
2019-02-11 08:00 | 269 | 268
2019-02-11 08:30 | 272 | 272
2019-02-11 09:00 | 280 | 279
2019-02-11 09:30 | 289 | 287
2019-02-11 10:00 | 276 | 275
2019-02-11 10:30 | 272 | 270
2019-02-11 11:00 | 271 | 270
2019-02-11 11:30 | 279 | 277
2019-02-11 12:00 | 284 | 284
2019-02-11 12:30 | 287 | 287
2019-02-11 13:00 | 301 | 301
2019-02-11 13:30 | 312 | 312
2019-02-11 14:00 | 314 | 314
2019-02-11 14:30 | 317 | 317
2019-02-11 15:00 | 324 | 324
2019-02-11 15:30 | 335 | 335
2019-02-11 16:00 | 355 | 355
2019-02-11 16:30 | 369 | 368
2019-02-11 17:00 | 381 | 380
2019-02-11 17:30 | 383 | 382
2019-02-11 18:00 | 377 | 376
2019-02-11 18:30 | 367 | 366
2019-02-11 19:00 | 364 | 364
2019-02-11 19:30 | 361 | 361
2019-02-11 20:00 | 354 | 354
2019-02-11 20:30 | 341 | 341
2019-02-11 21:00 | 322 | 322
2019-02-11 21:30 | 308 | 308
2019-02-11 22:00 | 292 | 292
2019-02-11 22:30 | 279 | 279
2019-02-11 23:00 | 268 | 268
2019-02-11 23:30 | 250 | 250
2019-02-12 | 233 | 233
2019-02-12 00:30 | 218 | 218
2019-02-12 01:00 | 208 | 208
2019-02-12 01:30 | 202 | 202
2019-02-12 02:00 | 197 | 196
2019-02-12 02:30 | 196 | 196
2019-02-12 03:00 | 194 | 194
2019-02-12 03:30 | 192 | 192
2019-02-12 04:00 | 191 | 191
2019-02-12 04:30 | 194 | 194
2019-02-12 05:00 | 201 | 200
2019-02-12 05:30 | 212 | 211
2019-02-12 06:00 | 220 | 219
2019-02-12 06:30 | 244 | 244
2019-02-12 07:00 | 263 | 263
2019-02-12 07:30 | 277 | 277
2019-02-12 08:00 | 283 | 283
2019-02-12 08:30 | 285 | 285
2019-02-12 09:00 | 293 | 293
2019-02-12 09:30 | 306 | 306
2019-02-12 10:00 | 310 | 310
2019-02-12 10:30 | 315 | 315
2019-02-12 11:00 | 323 | 322
2019-02-12 11:30 | 331 | 331
2019-02-12 12:00 | 343 | 342
2019-02-12 12:30 | 356 | 355
2019-02-12 13:00 | 369 | 369
2019-02-12 13:30 | 385 | 383
2019-02-12 14:00 | 400 | 397
2019-02-12 14:30 | 398 | 395
2019-02-12 15:00 | 403 | 400
2019-02-12 15:30 | 415 | 412
2019-02-12 16:00 | 429 | 426
2019-02-12 16:30 | 442 | 441
2019-02-12 17:00 | 454 | 453
2019-02-12 17:30 | 456 | 455
2019-02-12 18:00 | 451 | 450
2019-02-12 18:30 | 440 | 438
2019-02-12 19:00 | 440 | 439
2019-02-12 19:30 | 438 | 437
2019-02-12 20:00 | 430 | 429
2019-02-12 20:30 | 416 | 416
2019-02-12 21:00 | 397 | 397
2019-02-12 21:30 | 377 | 377
2019-02-12 22:00 | 358 | 358
2019-02-12 22:30 | 338 | 338
2019-02-12 23:00 | 320 | 320
2019-02-12 23:30 | 296 | 296
2019-02-13 | 272 | 271
2019-02-13 00:30 | 254 | 253
2019-02-13 01:00 | 244 | 242
2019-02-13 01:30 | 236 | 235
2019-02-13 02:00 | 229 | 229
2019-02-13 02:30 | 224 | 224
2019-02-13 03:00 | 219 | 219
2019-02-13 03:30 | 214 | 214
2019-02-13 04:00 | 211 | 210
2019-02-13 04:30 | 211 | 210
2019-02-13 05:00 | 216 | 215
2019-02-13 05:30 | 225 | 224
2019-02-13 06:00 | 233 | 232
2019-02-13 06:30 | 255 | 254
2019-02-13 07:00 | 274 | 272
2019-02-13 07:30 | 294 | 293
2019-02-13 08:00 | 303 | 302
2019-02-13 08:30 | 310 | 310
2019-02-13 09:00 | 315 | 314
2019-02-13 09:30 | 323 | 321
2019-02-13 10:00 | 331 | 330
2019-02-13 10:30 | 340 | 339
2019-02-13 11:00 | 349 | 348
2019-02-13 11:30 | 357 | 356
2019-02-13 12:00 | 371 | 369
2019-02-13 12:30 | 380 | 379
2019-02-13 13:00 | 390 | 388
2019-02-13 13:30 | 400 | 400
2019-02-13 14:00 | 410 | 410
2019-02-13 14:30 | 422 | 422
2019-02-13 15:00 | 430 | 430
2019-02-13 15:30 | 441 | 441
2019-02-13 16:00 | 460 | 459
2019-02-13 16:30 | 464 | 463
2019-02-13 17:00 | 478 | 476
2019-02-13 17:30 | 477 | 477
2019-02-13 18:00 | 473 | 472
2019-02-13 18:30 | 459 | 459
2019-02-13 19:00 | 455 | 455
2019-02-13 19:30 | 447 | 447
2019-02-13 20:00 | 431 | 430
2019-02-13 20:30 | 429 | 429
2019-02-13 21:00 | 415 | 415
2019-02-13 21:30 | 387 | 386
2019-02-13 22:00 | 365 | 365
2019-02-13 22:30 | 328 | 327
2019-02-13 23:00 | 313 | 312
2019-02-13 23:30 | 296 | 296
2019-02-14 | 281 | 280
2019-02-14 00:30 | 269 | 269
2019-02-14 01:00 | 261 | 261
2019-02-14 01:30 | 242 | 242
2019-02-14 02:00 | 230 | 229
2019-02-14 02:30 | 224 | 220
2019-02-14 03:00 | 219 | 216
2019-02-14 03:30 | 217 | 213
2019-02-14 04:00 | 214 | 211
2019-02-14 04:30 | 215 | 212
2019-02-14 05:00 | 222 | 218
2019-02-14 05:30 | 232 | 228
2019-02-14 06:00 | 239 | 236
2019-02-14 06:30 | 265 | 261
2019-02-14 07:00 | 281 | 277
2019-02-14 07:30 | 293 | 290
2019-02-14 08:00 | 303 | 300
2019-02-14 08:30 | 310 | 308
2019-02-14 09:00 | 311 | 310
2019-02-14 09:30 | 316 | 313
2019-02-14 10:00 | 314 | 312
2019-02-14 10:30 | 313 | 310
2019-02-14 11:00 | 311 | 310
2019-02-14 11:30 | 311 | 310
2019-02-14 12:00 | 312 | 311
2019-02-14 12:30 | 309 | 308
2019-02-14 13:00 | 320 | 318
2019-02-14 13:30 | 328 | 326
2019-02-14 14:00 | 335 | 333
2019-02-14 14:30 | 340 | 338
2019-02-14 15:00 | 338 | 336
2019-02-14 15:30 | 333 | 331
2019-02-14 16:00 | 335 | 334
2019-02-14 16:30 | 336 | 335
2019-02-14 17:00 | 337 | 337
2019-02-14 17:30 | 331 | 330
2019-02-14 18:00 | 328 | 327
2019-02-14 18:30 | 321 | 320
2019-02-14 19:00 | 326 | 325
2019-02-14 19:30 | 325 | 324
2019-02-14 20:00 | 320 | 320
2019-02-14 20:30 | 310 | 310
2019-02-14 21:00 | 296 | 296
2019-02-14 21:30 | 282 | 281
2019-02-14 22:00 | 268 | 267
2019-02-14 22:30 | 255 | 255
2019-02-14 23:00 | 245 | 245
2019-02-14 23:30 | 228 | 228
2019-02-15 | 212 | 212
2019-02-15 00:30 | 199 | 199
2019-02-15 01:00 | 192 | 192
2019-02-15 01:30 | 187 | 187
2019-02-15 02:00 | 183 | 183
2019-02-15 02:30 | 181 | 180
2019-02-15 03:00 | 179 | 179
2019-02-15 03:30 | 178 | 178
2019-02-15 04:00 | 178 | 178
2019-02-15 04:30 | 180 | 180
2019-02-15 05:00 | 186 | 186
2019-02-15 05:30 | 198 | 198
2019-02-15 06:00 | 207 | 207
2019-02-15 06:30 | 225 | 225
2019-02-15 07:00 | 238 | 238
2019-02-15 07:30 | 249 | 249
2019-02-15 08:00 | 252 | 252
2019-02-15 08:30 | 246 | 246
2019-02-15 09:00 | 249 | 249
2019-02-15 09:30 | 252 | 252
2019-02-15 10:00 | 253 | 253
2019-02-15 10:30 | 251 | 251
2019-02-15 11:00 | 251 | 251
2019-02-15 11:30 | 255 | 255
2019-02-15 12:00 | 262 | 262
2019-02-15 12:30 | 264 | 263
2019-02-15 13:00 | 262 | 262
2019-02-15 13:30 | 261 | 261
2019-02-15 14:00 | 263 | 263
2019-02-15 14:30 | 270 | 270
2019-02-15 15:00 | 274 | 274
2019-02-15 15:30 | 279 | 279
2019-02-15 16:00 | 293 | 293
2019-02-15 16:30 | 304 | 304
2019-02-15 17:00 | 314 | 314
2019-02-15 17:30 | 316 | 315
2019-02-15 18:00 | 306 | 306
2019-02-15 18:30 | 298 | 298
2019-02-15 19:00 | 301 | 301
2019-02-15 19:30 | 297 | 297
2019-02-15 20:00 | 294 | 294
2019-02-15 20:30 | 284 | 284
2019-02-15 21:00 | 273 | 273
2019-02-15 21:30 | 263 | 262
2019-02-15 22:00 | 254 | 253
2019-02-15 22:30 | 248 | 248
2019-02-15 23:00 | 238 | 238
2019-02-15 23:30 | 221 | 221
2019-02-16 | 203 | 203
2019-02-16 00:30 | 190 | 190
2019-02-16 01:00 | 183 | 183
2019-02-16 01:30 | 177 | 177
2019-02-16 02:00 | 172 | 172
2019-02-16 02:30 | 169 | 169
2019-02-16 03:00 | 167 | 167
2019-02-16 03:30 | 165 | 165
2019-02-16 04:00 | 164 | 164
2019-02-16 04:30 | 163 | 163
2019-02-16 05:00 | 164 | 164
2019-02-16 05:30 | 168 | 168
2019-02-16 06:00 | 167 | 167
2019-02-16 06:30 | 173 | 173
2019-02-16 07:00 | 176 | 176
2019-02-16 07:30 | 180 | 180
2019-02-16 08:00 | 184 | 183
2019-02-16 08:30 | 191 | 191
2019-02-16 09:00 | 193 | 192
2019-02-16 09:30 | 197 | 195
2019-02-16 10:00 | 202 | 202
2019-02-16 10:30 | 197 | 196
2019-02-16 11:00 | 190 | 189
2019-02-16 11:30 | 194 | 193
2019-02-16 12:00 | 199 | 198
2019-02-16 12:30 | 210 | 209
2019-02-16 13:00 | 208 | 207
2019-02-16 13:30 | 216 | 214
2019-02-16 14:00 | 217 | 216
2019-02-16 14:30 | 220 | 219
2019-02-16 15:00 | 225 | 224
2019-02-16 15:30 | 227 | 226
2019-02-16 16:00 | 236 | 234
2019-02-16 16:30 | 242 | 241
2019-02-16 17:00 | 253 | 252
2019-02-16 17:30 | 256 | 255
2019-02-16 18:00 | 257 | 256
2019-02-16 18:30 | 259 | 258
2019-02-16 19:00 | 268 | 266
2019-02-16 19:30 | 268 | 266
2019-02-16 20:00 | 265 | 263
2019-02-16 20:30 | 259 | 258
2019-02-16 21:00 | 248 | 247
2019-02-16 21:30 | 239 | 238
2019-02-16 22:00 | 231 | 230
2019-02-16 22:30 | 228 | 227
2019-02-16 23:00 | 225 | 224
2019-02-16 23:30 | 210 | 209
2019-02-17 | 195 | 194
2019-02-17 00:30 | 181 | 180
2019-02-17 01:00 | 174 | 173
2019-02-17 01:30 | 169 | 169
2019-02-17 02:00 | 164 | 163
2019-02-17 02:30 | 161 | 160
2019-02-17 03:00 | 158 | 158
2019-02-17 03:30 | 157 | 156
2019-02-17 04:00 | 156 | 156
2019-02-17 04:30 | 155 | 155
2019-02-17 05:00 | 156 | 155
2019-02-17 05:30 | 157 | 157
2019-02-17 06:00 | 156 | 156
2019-02-17 06:30 | 158 | 157
2019-02-17 07:00 | 158 | 157
2019-02-17 07:30 | 160 | 160
2019-02-17 08:00 | 161 | 160
2019-02-17 08:30 | 163 | 161
2019-02-17 09:00 | 167 | 164
2019-02-17 09:30 | 174 | 170
2019-02-17 10:00 | 179 | 174
2019-02-17 10:30 | 181 | 176
2019-02-17 11:00 | 180 | 175
2019-02-17 11:30 | 182 | 179
2019-02-17 12:00 | 185 | 181
2019-02-17 12:30 | 186 | 182
2019-02-17 13:00 | 186 | 182
2019-02-17 13:30 | 192 | 187
2019-02-17 14:00 | 200 | 194
2019-02-17 14:30 | 205 | 204
2019-02-17 15:00 | 214 | 214
2019-02-17 15:30 | 226 | 226
2019-02-17 16:00 | 242 | 242
2019-02-17 16:30 | 255 | 255
2019-02-17 17:00 | 267 | 267
2019-02-17 17:30 | 276 | 275
2019-02-17 18:00 | 280 | 280
2019-02-17 18:30 | 281 | 281
2019-02-17 19:00 | 288 | 288
2019-02-17 19:30 | 287 | 287
2019-02-17 20:00 | 282 | 281
2019-02-17 20:30 | 274 | 274
2019-02-17 21:00 | 260 | 260
2019-02-17 21:30 | 246 | 246
2019-02-17 22:00 | 236 | 236
2019-02-17 22:30 | 230 | 230
2019-02-17 23:00 | 223 | 223
2019-02-17 23:30 | 208 | 208
2019-02-18 | 191 | 190
2019-02-18 00:30 | 179 | 177
2019-02-18 01:00 | 172 | 170
2019-02-18 01:30 | 169 | 166
2019-02-18 02:00 | 165 | 162
2019-02-18 02:30 | 164 | 161
2019-02-18 03:00 | 163 | 160
2019-02-18 03:30 | 163 | 160
2019-02-18 04:00 | 163 | 160
2019-02-18 04:30 | 166 | 164
2019-02-18 05:00 | 172 | 170
2019-02-18 05:30 | 183 | 182
2019-02-18 06:00 | 193 | 193
2019-02-18 06:30 | 211 | 211
2019-02-18 07:00 | 224 | 224
2019-02-18 07:30 | 237 | 236
2019-02-18 08:00 | 236 | 235
2019-02-18 08:30 | 236 | 236
2019-02-18 09:00 | 248 | 248
2019-02-18 09:30 | 265 | 263
2019-02-18 10:00 | 263 | 262
2019-02-18 10:30 | 261 | 259
2019-02-18 11:00 | 251 | 250
2019-02-18 11:30 | 249 | 247
2019-02-18 12:00 | 252 | 250
2019-02-18 12:30 | 253 | 252
2019-02-18 13:00 | 256 | 254
2019-02-18 13:30 | 263 | 261
2019-02-18 14:00 | 270 | 268
2019-02-18 14:30 | 278 | 276
2019-02-18 15:00 | 285 | 284
2019-02-18 15:30 | 294 | 294
2019-02-18 16:00 | 310 | 309
2019-02-18 16:30 | 325 | 325
2019-02-18 17:00 | 339 | 338
2019-02-18 17:30 | 343 | 343
2019-02-18 18:00 | 340 | 340
2019-02-18 18:30 | 332 | 332
2019-02-18 19:00 | 337 | 336
2019-02-18 19:30 | 334 | 333
2019-02-18 20:00 | 328 | 327
2019-02-18 20:30 | 316 | 315
2019-02-18 21:00 | 298 | 297
2019-02-18 21:30 | 282 | 282
2019-02-18 22:00 | 267 | 267
2019-02-18 22:30 | 257 | 257
2019-02-18 23:00 | 247 | 247
2019-02-18 23:30 | 230 | 230
2019-02-19 | 212 | 212
2019-02-19 00:30 | 198 | 197
2019-02-19 01:00 | 191 | 190
2019-02-19 01:30 | 185 | 184
2019-02-19 02:00 | 182 | 181
2019-02-19 02:30 | 180 | 178
2019-02-19 03:00 | 178 | 177
2019-02-19 03:30 | 178 | 176
2019-02-19 04:00 | 177 | 175
2019-02-19 04:30 | 180 | 178
2019-02-19 05:00 | 185 | 184
2019-02-19 05:30 | 197 | 196
2019-02-19 06:00 | 204 | 203
2019-02-19 06:30 | 221 | 221
2019-02-19 07:00 | 235 | 234
2019-02-19 07:30 | 245 | 243
2019-02-19 08:00 | 246 | 246
2019-02-19 08:30 | 245 | 244
2019-02-19 09:00 | 245 | 245
2019-02-19 09:30 | 247 | 247
2019-02-19 10:00 | 250 | 249
2019-02-19 10:30 | 252 | 252
2019-02-19 11:00 | 255 | 254
2019-02-19 11:30 | 261 | 260
2019-02-19 12:00 | 270 | 269
2019-02-19 12:30 | 280 | 280
2019-02-19 13:00 | 292 | 290
2019-02-19 13:30 | 303 | 303
2019-02-19 14:00 | 314 | 314
2019-02-19 14:30 | 327 | 327
2019-02-19 15:00 | 339 | 339
2019-02-19 15:30 | 352 | 352
2019-02-19 16:00 | 373 | 373
2019-02-19 16:30 | 389 | 389
2019-02-19 17:00 | 401 | 400
2019-02-19 17:30 | 401 | 401
2019-02-19 18:00 | 393 | 393
2019-02-19 18:30 | 382 | 382
2019-02-19 19:00 | 382 | 382
2019-02-19 19:30 | 378 | 378
2019-02-19 20:00 | 369 | 369
2019-02-19 20:30 | 354 | 354
2019-02-19 21:00 | 334 | 334
2019-02-19 21:30 | 315 | 315
2019-02-19 22:00 | 298 | 298
2019-02-19 22:30 | 284 | 284
2019-02-19 23:00 | 270 | 269
2019-02-19 23:30 | 249 | 249
2019-02-20 | 231 | 231
2019-02-20 00:30 | 216 | 216
2019-02-20 01:00 | 208 | 208
2019-02-20 01:30 | 202 | 202
2019-02-20 02:00 | 196 | 196
2019-02-20 02:30 | 192 | 192
2019-02-20 03:00 | 190 | 190
2019-02-20 03:30 | 190 | 190
2019-02-20 04:00 | 190 | 190
2019-02-20 04:30 | 193 | 193
2019-02-20 05:00 | 199 | 199
2019-02-20 05:30 | 211 | 210
2019-02-20 06:00 | 220 | 219
2019-02-20 06:30 | 240 | 240
2019-02-20 07:00 | 254 | 254
2019-02-20 07:30 | 254 | 254
2019-02-20 08:00 | 261 | 260
2019-02-20 08:30 | 263 | 263
2019-02-20 09:00 | 260 | 260
2019-02-20 09:30 | 258 | 258
2019-02-20 10:00 | 257 | 257
2019-02-20 10:30 | 257 | 257
2019-02-20 11:00 | 261 | 261
2019-02-20 11:30 | 266 | 265
2019-02-20 12:00 | 274 | 273
2019-02-20 12:30 | 281 | 280
2019-02-20 13:00 | 290 | 289
2019-02-20 13:30 | 300 | 300
2019-02-20 14:00 | 311 | 311
2019-02-20 14:30 | 322 | 322
2019-02-20 15:00 | 330 | 329
2019-02-20 15:30 | 340 | 340
2019-02-20 16:00 | 357 | 357
2019-02-20 16:30 | 376 | 375
2019-02-20 17:00 | 397 | 396
2019-02-20 17:30 | 397 | 396
2019-02-20 18:00 | 389 | 388
2019-02-20 18:30 | 380 | 378
2019-02-20 19:00 | 385 | 382
2019-02-20 19:30 | 381 | 379
2019-02-20 20:00 | 373 | 372
2019-02-20 20:30 | 362 | 361
2019-02-20 21:00 | 346 | 346
2019-02-20 21:30 | 329 | 329
2019-02-20 22:00 | 313 | 313
2019-02-20 22:30 | 300 | 300
2019-02-20 23:00 | 288 | 288
2019-02-20 23:30 | 266 | 266
2019-02-21 | 244 | 243
2019-02-21 00:30 | 227 | 226
2019-02-21 01:00 | 215 | 214
2019-02-21 01:30 | 207 | 206
2019-02-21 02:00 | 203 | 202
2019-02-21 02:30 | 199 | 199
2019-02-21 03:00 | 197 | 196
2019-02-21 03:30 | 196 | 195
2019-02-21 04:00 | 194 | 194
2019-02-21 04:30 | 196 | 196
2019-02-21 05:00 | 201 | 201
2019-02-21 05:30 | 214 | 214
2019-02-21 06:00 | 223 | 222
2019-02-21 06:30 | 244 | 243
2019-02-21 07:00 | 261 | 260
2019-02-21 07:30 | 265 | 265
2019-02-21 08:00 | 271 | 271
2019-02-21 08:30 | 281 | 281
2019-02-21 09:00 | 277 | 277
2019-02-21 09:30 | 271 | 271
2019-02-21 10:00 | 273 | 273
2019-02-21 10:30 | 280 | 280
2019-02-21 11:00 | 295 | 295
2019-02-21 11:30 | 292 | 291
2019-02-21 12:00 | 292 | 291
2019-02-21 12:30 | 276 | 276
2019-02-21 13:00 | 282 | 282
2019-02-21 13:30 | 292 | 292
2019-02-21 14:00 | 299 | 299
2019-02-21 14:30 | 304 | 304
2019-02-21 15:00 | 308 | 308
2019-02-21 15:30 | 321 | 321
2019-02-21 16:00 | 339 | 339
2019-02-21 16:30 | 354 | 354
2019-02-21 17:00 | 365 | 365
2019-02-21 17:30 | 383 | 382
2019-02-21 18:00 | 380 | 379
2019-02-21 18:30 | 372 | 370
2019-02-21 19:00 | 377 | 377
2019-02-21 19:30 | 373 | 372
2019-02-21 20:00 | 366 | 365
2019-02-21 20:30 | 353 | 353
2019-02-21 21:00 | 333 | 333
2019-02-21 21:30 | 311 | 311
2019-02-21 22:00 | 293 | 293
2019-02-21 22:30 | 282 | 281
2019-02-21 23:00 | 270 | 270
2019-02-21 23:30 | 251 | 250
2019-02-22 | 232 | 231
2019-02-22 00:30 | 214 | 214
2019-02-22 01:00 | 207 | 207
2019-02-22 01:30 | 201 | 201
2019-02-22 02:00 | 196 | 196
2019-02-22 02:30 | 193 | 193
2019-02-22 03:00 | 191 | 191
2019-02-22 03:30 | 190 | 189
2019-02-22 04:00 | 189 | 189
2019-02-22 04:30 | 192 | 192
2019-02-22 05:00 | 198 | 198
2019-02-22 05:30 | 210 | 209
2019-02-22 06:00 | 217 | 216
2019-02-22 06:30 | 235 | 235
2019-02-22 07:00 | 248 | 248
2019-02-22 07:30 | 261 | 261
2019-02-22 08:00 | 267 | 267
2019-02-22 08:30 | 267 | 267
2019-02-22 09:00 | 260 | 259
2019-02-22 09:30 | 264 | 264
2019-02-22 10:00 | 264 | 264
2019-02-22 10:30 | 263 | 263
2019-02-22 11:00 | 259 | 259
2019-02-22 11:30 | 249 | 249
2019-02-22 12:00 | 261 | 261
2019-02-22 12:30 | 295 | 294
2019-02-22 13:00 | 290 | 290
2019-02-22 13:30 | 263 | 263
2019-02-22 14:00 | 243 | 243
2019-02-22 14:30 | 236 | 236
2019-02-22 15:00 | 240 | 240
2019-02-22 15:30 | 255 | 255
2019-02-22 16:00 | 269 | 269
2019-02-22 16:30 | 272 | 272
2019-02-22 17:00 | 283 | 283
2019-02-22 17:30 | 281 | 281
2019-02-22 18:00 | 273 | 273
2019-02-22 18:30 | 267 | 267
2019-02-22 19:00 | 273 | 272
2019-02-22 19:30 | 269 | 269
2019-02-22 20:00 | 263 | 263
2019-02-22 20:30 | 257 | 257
2019-02-22 21:00 | 245 | 245
2019-02-22 21:30 | 233 | 232
2019-02-22 22:00 | 223 | 221
2019-02-22 22:30 | 217 | 216
2019-02-22 23:00 | 211 | 210
2019-02-22 23:30 | 196 | 196
2019-02-23 | 180 | 180
2019-02-23 00:30 | 167 | 167
2019-02-23 01:00 | 162 | 161
2019-02-23 01:30 | 158 | 158
2019-02-23 02:00 | 153 | 153
2019-02-23 02:30 | 151 | 151
2019-02-23 03:00 | 149 | 149
2019-02-23 03:30 | 149 | 149
2019-02-23 04:00 | 148 | 148
2019-02-23 04:30 | 147 | 147
2019-02-23 05:00 | 148 | 148
2019-02-23 05:30 | 152 | 152
2019-02-23 06:00 | 152 | 152
2019-02-23 06:30 | 156 | 156
2019-02-23 07:00 | 161 | 161
2019-02-23 07:30 | 164 | 164
2019-02-23 08:00 | 161 | 161
2019-02-23 08:30 | 162 | 162
2019-02-23 09:00 | 164 | 163
2019-02-23 09:30 | 167 | 167
2019-02-23 10:00 | 171 | 170
2019-02-23 10:30 | 169 | 168
2019-02-23 11:00 | 163 | 163
2019-02-23 11:30 | 169 | 169
2019-02-23 12:00 | 167 | 167
2019-02-23 12:30 | 168 | 167
2019-02-23 13:00 | 176 | 175
2019-02-23 13:30 | 182 | 181
2019-02-23 14:00 | 183 | 182
2019-02-23 14:30 | 185 | 184
2019-02-23 15:00 | 192 | 191
2019-02-23 15:30 | 202 | 200
2019-02-23 16:00 | 216 | 215
2019-02-23 16:30 | 221 | 220
2019-02-23 17:00 | 230 | 228
2019-02-23 17:30 | 234 | 233
2019-02-23 18:00 | 236 | 235
2019-02-23 18:30 | 239 | 238
2019-02-23 19:00 | 248 | 246
2019-02-23 19:30 | 245 | 244
2019-02-23 20:00 | 240 | 239
2019-02-23 20:30 | 234 | 233
2019-02-23 21:00 | 225 | 224
2019-02-23 21:30 | 217 | 216
2019-02-23 22:00 | 209 | 208
2019-02-23 22:30 | 204 | 204
2019-02-23 23:00 | 201 | 201
2019-02-23 23:30 | 189 | 189
2019-02-24 | 174 | 174
2019-02-24 00:30 | 163 | 163
2019-02-24 01:00 | 156 | 156
2019-02-24 01:30 | 152 | 152
2019-02-24 02:00 | 148 | 147
2019-02-24 02:30 | 146 | 145
2019-02-24 03:00 | 144 | 143
2019-02-24 03:30 | 143 | 142
2019-02-24 04:00 | 141 | 140
2019-02-24 04:30 | 140 | 140
2019-02-24 05:00 | 141 | 141
2019-02-24 05:30 | 147 | 147
2019-02-24 06:00 | 147 | 147
2019-02-24 06:30 | 149 | 149
2019-02-24 07:00 | 149 | 149
2019-02-24 07:30 | 151 | 151
2019-02-24 08:00 | 152 | 151
2019-02-24 08:30 | 158 | 157
2019-02-24 09:00 | 171 | 170
2019-02-24 09:30 | 177 | 175
2019-02-24 10:00 | 189 | 187
2019-02-24 10:30 | 180 | 178
2019-02-24 11:00 | 174 | 172
2019-02-24 11:30 | 172 | 170
2019-02-24 12:00 | 164 | 162
2019-02-24 12:30 | 162 | 161
2019-02-24 13:00 | 159 | 159
2019-02-24 13:30 | 152 | 151
2019-02-24 14:00 | 160 | 160
2019-02-24 14:30 | 174 | 173
2019-02-24 15:00 | 178 | 177
2019-02-24 15:30 | 187 | 186
2019-02-24 16:00 | 201 | 201
2019-02-24 16:30 | 212 | 212
2019-02-24 17:00 | 225 | 225
2019-02-24 17:30 | 232 | 232
2019-02-24 18:00 | 238 | 238
2019-02-24 18:30 | 243 | 243
2019-02-24 19:00 | 251 | 251
2019-02-24 19:30 | 248 | 248
2019-02-24 20:00 | 242 | 242
2019-02-24 20:30 | 235 | 235
2019-02-24 21:00 | 226 | 226
2019-02-24 21:30 | 217 | 217
2019-02-24 22:00 | 209 | 209
2019-02-24 22:30 | 206 | 206
2019-02-24 23:00 | 202 | 202
2019-02-24 23:30 | 191 | 190
2019-02-25 | 176 | 175
2019-02-25 00:30 | 163 | 162
2019-02-25 01:00 | 156 | 156
2019-02-25 01:30 | 153 | 153
2019-02-25 02:00 | 150 | 150
2019-02-25 02:30 | 149 | 149
2019-02-25 03:00 | 148 | 148
2019-02-25 03:30 | 149 | 149
2019-02-25 04:00 | 150 | 149
2019-02-25 04:30 | 153 | 153
2019-02-25 05:00 | 158 | 158
2019-02-25 05:30 | 171 | 171
2019-02-25 06:00 | 181 | 181
2019-02-25 06:30 | 201 | 200
2019-02-25 07:00 | 213 | 213
2019-02-25 07:30 | 224 | 224
2019-02-25 08:00 | 225 | 225
2019-02-25 08:30 | 226 | 225
2019-02-25 09:00 | 218 | 218
2019-02-25 09:30 | 219 | 219
2019-02-25 10:00 | 217 | 216
2019-02-25 10:30 | 216 | 215
2019-02-25 11:00 | 211 | 211
2019-02-25 11:30 | 212 | 212
2019-02-25 12:00 | 209 | 208
2019-02-25 12:30 | 214 | 213
2019-02-25 13:00 | 211 | 211
2019-02-25 13:30 | 219 | 219
2019-02-25 14:00 | 218 | 218
2019-02-25 14:30 | 224 | 224
2019-02-25 15:00 | 226 | 226
2019-02-25 15:30 | 232 | 232
2019-02-25 16:00 | 236 | 235
2019-02-25 16:30 | 242 | 242
2019-02-25 17:00 | 255 | 255
2019-02-25 17:30 | 262 | 262
2019-02-25 18:00 | 263 | 263
2019-02-25 18:30 | 262 | 262
2019-02-25 19:00 | 269 | 269
2019-02-25 19:30 | 266 | 266
2019-02-25 20:00 | 261 | 261
2019-02-25 20:30 | 255 | 255
2019-02-25 21:00 | 243 | 242
2019-02-25 21:30 | 231 | 231
2019-02-25 22:00 | 221 | 221
2019-02-25 22:30 | 215 | 215
2019-02-25 23:00 | 209 | 209
2019-02-25 23:30 | 196 | 196
2019-02-26 | 181 | 181
2019-02-26 00:30 | 169 | 168
2019-02-26 01:00 | 162 | 161
2019-02-26 01:30 | 159 | 158
2019-02-26 02:00 | 156 | 155
2019-02-26 02:30 | 154 | 153
2019-02-26 03:00 | 153 | 151
2019-02-26 03:30 | 153 | 152
2019-02-26 04:00 | 153 | 152
2019-02-26 04:30 | 156 | 155
2019-02-26 05:00 | 162 | 161
2019-02-26 05:30 | 173 | 172
2019-02-26 06:00 | 181 | 180
2019-02-26 06:30 | 198 | 198
2019-02-26 07:00 | 212 | 211
2019-02-26 07:30 | 224 | 223
2019-02-26 08:00 | 223 | 223
2019-02-26 08:30 | 222 | 222
2019-02-26 09:00 | 216 | 216
2019-02-26 09:30 | 207 | 207
2019-02-26 10:00 | 216 | 216
2019-02-26 10:30 | 216 | 215
2019-02-26 11:00 | 215 | 214
2019-02-26 11:30 | 215 | 215
2019-02-26 12:00 | 221 | 221
2019-02-26 12:30 | 216 | 216
2019-02-26 13:00 | 209 | 209
2019-02-26 13:30 | 210 | 210
2019-02-26 14:00 | 207 | 207
2019-02-26 14:30 | 212 | 211
2019-02-26 15:00 | 214 | 214
2019-02-26 15:30 | 220 | 220
2019-02-26 16:00 | 227 | 227
2019-02-26 16:30 | 239 | 239
2019-02-26 17:00 | 250 | 250
2019-02-26 17:30 | 258 | 258
2019-02-26 18:00 | 257 | 257
2019-02-26 18:30 | 258 | 258
2019-02-26 19:00 | 270 | 270
2019-02-26 19:30 | 268 | 267
2019-02-26 20:00 | 262 | 262
2019-02-26 20:30 | 256 | 256
2019-02-26 21:00 | 244 | 244
2019-02-26 21:30 | 233 | 233
2019-02-26 22:00 | 224 | 224
2019-02-26 22:30 | 218 | 218
2019-02-26 23:00 | 212 | 211
2019-02-26 23:30 | 198 | 197
2019-02-27 | 183 | 182
2019-02-27 00:30 | 168 | 168
2019-02-27 01:00 | 160 | 160
2019-02-27 01:30 | 156 | 156
2019-02-27 02:00 | 152 | 152
2019-02-27 02:30 | 151 | 151
2019-02-27 03:00 | 151 | 150
2019-02-27 03:30 | 151 | 150
2019-02-27 04:00 | 151 | 150
2019-02-27 04:30 | 154 | 154
2019-02-27 05:00 | 161 | 161
2019-02-27 05:30 | 172 | 172
2019-02-27 06:00 | 181 | 181
2019-02-27 06:30 | 197 | 197
2019-02-27 07:00 | 208 | 207
2019-02-27 07:30 | 214 | 212
2019-02-27 08:00 | 219 | 216
2019-02-27 08:30 | 216 | 214
2019-02-27 09:00 | 219 | 216
2019-02-27 09:30 | 217 | 214
2019-02-27 10:00 | 219 | 215
2019-02-27 10:30 | 212 | 208
2019-02-27 11:00 | 213 | 213
2019-02-27 11:30 | 221 | 220
2019-02-27 12:00 | 221 | 220
2019-02-27 12:30 | 220 | 219
2019-02-27 13:00 | 219 | 218
2019-02-27 13:30 | 218 | 217
2019-02-27 14:00 | 218 | 217
2019-02-27 14:30 | 222 | 221
2019-02-27 15:00 | 222 | 221
2019-02-27 15:30 | 227 | 226
2019-02-27 16:00 | 234 | 233
2019-02-27 16:30 | 242 | 241
2019-02-27 17:00 | 252 | 251
2019-02-27 17:30 | 254 | 254
2019-02-27 18:00 | 256 | 256
2019-02-27 18:30 | 258 | 258
2019-02-27 19:00 | 269 | 268
2019-02-27 19:30 | 265 | 264
2019-02-27 20:00 | 261 | 261
2019-02-27 20:30 | 255 | 254
2019-02-27 21:00 | 243 | 242
2019-02-27 21:30 | 233 | 233
2019-02-27 22:00 | 224 | 224
2019-02-27 22:30 | 218 | 218
2019-02-27 23:00 | 212 | 212
2019-02-27 23:30 | 198 | 198
2019-02-28 | 181 | 181
2019-02-28 00:30 | 168 | 168
2019-02-28 01:00 | 161 | 161
2019-02-28 01:30 | 155 | 155
2019-02-28 02:00 | 151 | 151
2019-02-28 02:30 | 148 | 148
2019-02-28 03:00 | 148 | 148
2019-02-28 03:30 | 148 | 148
2019-02-28 04:00 | 148 | 148
2019-02-28 04:30 | 153 | 152
2019-02-28 05:00 | 158 | 158
2019-02-28 05:30 | 171 | 171
2019-02-28 06:00 | 180 | 179
2019-02-28 06:30 | 196 | 195
2019-02-28 07:00 | 207 | 206
2019-02-28 07:30 | 218 | 217
2019-02-28 08:00 | 226 | 226
2019-02-28 08:30 | 226 | 226
2019-02-28 09:00 | 220 | 220
2019-02-28 09:30 | 213 | 212
2019-02-28 10:00 | 214 | 213
2019-02-28 10:30 | 216 | 215
2019-02-28 11:00 | 203 | 202
2019-02-28 11:30 | 199 | 198
2019-02-28 12:00 | 199 | 198
2019-02-28 12:30 | 194 | 193
2019-02-28 13:00 | 205 | 204
2019-02-28 13:30 | 204 | 203
2019-02-28 14:00 | 209 | 207
2019-02-28 14:30 | 214 | 212
2019-02-28 15:00 | 217 | 215
2019-02-28 15:30 | 218 | 217
2019-02-28 16:00 | 222 | 221
2019-02-28 16:30 | 228 | 227
2019-02-28 17:00 | 239 | 238
2019-02-28 17:30 | 244 | 243
2019-02-28 18:00 | 248 | 247
2019-02-28 18:30 | 253 | 252
2019-02-28 19:00 | 264 | 263
2019-02-28 19:30 | 261 | 260
2019-02-28 20:00 | 255 | 254
2019-02-28 20:30 | 250 | 249
2019-02-28 21:00 | 239 | 239
2019-02-28 21:30 | 227 | 227
2019-02-28 22:00 | 215 | 215
2019-02-28 22:30 | 210 | 210
2019-02-28 23:00 | 204 | 204
2019-02-28 23:30 | 188 | 188
2019-03-01 | 174 | 174
2019-03-01 00:30 | 163 | 163
2019-03-01 01:00 | 156 | 156
2019-03-01 01:30 | 151 | 151
2019-03-01 02:00 | 146 | 146
2019-03-01 02:30 | 145 | 145
2019-03-01 03:00 | 145 | 145
2019-03-01 03:30 | 146 | 146
2019-03-01 04:00 | 146 | 145
2019-03-01 04:30 | 149 | 149
2019-03-01 05:00 | 156 | 155
2019-03-01 05:30 | 167 | 166
2019-03-01 06:00 | 177 | 175
2019-03-01 06:30 | 197 | 195
2019-03-01 07:00 | 210 | 210
2019-03-01 07:30 | 220 | 219
2019-03-01 08:00 | 220 | 220
2019-03-01 08:30 | 214 | 214
2019-03-01 09:00 | 217 | 217
2019-03-01 09:30 | 216 | 216
2019-03-01 10:00 | 218 | 218
2019-03-01 10:30 | 211 | 210
2019-03-01 11:00 | 209 | 209
2019-03-01 11:30 | 209 | 208
2019-03-01 12:00 | 210 | 209
2019-03-01 12:30 | 209 | 209
2019-03-01 13:00 | 209 | 209
2019-03-01 13:30 | 209 | 208
2019-03-01 14:00 | 212 | 212
2019-03-01 14:30 | 218 | 218
2019-03-01 15:00 | 220 | 220
2019-03-01 15:30 | 224 | 224
2019-03-01 16:00 | 228 | 228
2019-03-01 16:30 | 238 | 238
2019-03-01 17:00 | 246 | 246
2019-03-01 17:30 | 243 | 243
2019-03-01 18:00 | 242 | 242
2019-03-01 18:30 | 243 | 243
2019-03-01 19:00 | 253 | 253
2019-03-01 19:30 | 250 | 250
2019-03-01 20:00 | 243 | 243
2019-03-01 20:30 | 239 | 239
2019-03-01 21:00 | 230 | 230
2019-03-01 21:30 | 219 | 219
2019-03-01 22:00 | 208 | 208
2019-03-01 22:30 | 203 | 203
2019-03-01 23:00 | 199 | 199
2019-03-01 23:30 | 186 | 186
2019-03-02 | 172 | 172
2019-03-02 00:30 | 159 | 159
2019-03-02 01:00 | 152 | 152
2019-03-02 01:30 | 147 | 147
2019-03-02 02:00 | 144 | 144
2019-03-02 02:30 | 141 | 141
2019-03-02 03:00 | 139 | 139
2019-03-02 03:30 | 137 | 137
2019-03-02 04:00 | 137 | 137
2019-03-02 04:30 | 137 | 137
2019-03-02 05:00 | 138 | 138
2019-03-02 05:30 | 142 | 142
2019-03-02 06:00 | 145 | 145
2019-03-02 06:30 | 152 | 152
2019-03-02 07:00 | 159 | 158
2019-03-02 07:30 | 167 | 166
2019-03-02 08:00 | 177 | 176
2019-03-02 08:30 | 180 | 179
2019-03-02 09:00 | 178 | 176
2019-03-02 09:30 | 173 | 172
2019-03-02 10:00 | 176 | 175
2019-03-02 10:30 | 169 | 168
2019-03-02 11:00 | 165 | 165
2019-03-02 11:30 | 159 | 158
2019-03-02 12:00 | 155 | 155
2019-03-02 12:30 | 157 | 157
2019-03-02 13:00 | 152 | 152
2019-03-02 13:30 | 157 | 157
2019-03-02 14:00 | 172 | 171
2019-03-02 14:30 | 165 | 165
2019-03-02 15:00 | 172 | 171
2019-03-02 15:30 | 184 | 183
2019-03-02 16:00 | 187 | 187
2019-03-02 16:30 | 191 | 190
2019-03-02 17:00 | 203 | 203
2019-03-02 17:30 | 206 | 206
2019-03-02 18:00 | 210 | 210
2019-03-02 18:30 | 217 | 217
2019-03-02 19:00 | 226 | 225
2019-03-02 19:30 | 222 | 221
2019-03-02 20:00 | 218 | 218
2019-03-02 20:30 | 217 | 216
2019-03-02 21:00 | 207 | 206
2019-03-02 21:30 | 198 | 197
2019-03-02 22:00 | 192 | 192
2019-03-02 22:30 | 191 | 191
2019-03-02 23:00 | 190 | 190
2019-03-02 23:30 | 179 | 179
2019-03-03 | 166 | 166
2019-03-03 00:30 | 153 | 153
2019-03-03 01:00 | 145 | 145
2019-03-03 01:30 | 140 | 140
2019-03-03 02:00 | 137 | 136
2019-03-03 02:30 | 134 | 133
2019-03-03 03:00 | 133 | 132
2019-03-03 03:30 | 135 | 134
2019-03-03 04:00 | 135 | 134
2019-03-03 04:30 | 134 | 133
2019-03-03 05:00 | 136 | 135
2019-03-03 05:30 | 138 | 138
2019-03-03 06:00 | 139 | 138
2019-03-03 06:30 | 141 | 140
2019-03-03 07:00 | 144 | 144
2019-03-03 07:30 | 150 | 150
2019-03-03 08:00 | 154 | 154
2019-03-03 08:30 | 161 | 161
2019-03-03 09:00 | 161 | 161
2019-03-03 09:30 | 164 | 163
2019-03-03 10:00 | 158 | 158
2019-03-03 10:30 | 160 | 160
2019-03-03 11:00 | 162 | 161
2019-03-03 11:30 | 165 | 164
2019-03-03 12:00 | 160 | 160
2019-03-03 12:30 | 152 | 152
2019-03-03 13:00 | 148 | 147
2019-03-03 13:30 | 153 | 153
2019-03-03 14:00 | 160 | 160
2019-03-03 14:30 | 162 | 162
2019-03-03 15:00 | 174 | 173
2019-03-03 15:30 | 181 | 180
2019-03-03 16:00 | 192 | 191
2019-03-03 16:30 | 201 | 201
2019-03-03 17:00 | 215 | 215
2019-03-03 17:30 | 224 | 223
2019-03-03 18:00 | 230 | 229
2019-03-03 18:30 | 238 | 237
2019-03-03 19:00 | 249 | 248
2019-03-03 19:30 | 244 | 243
2019-03-03 20:00 | 238 | 238
2019-03-03 20:30 | 234 | 233
2019-03-03 21:00 | 224 | 223
2019-03-03 21:30 | 215 | 214
2019-03-03 22:00 | 207 | 207
2019-03-03 22:30 | 203 | 203
2019-03-03 23:00 | 198 | 198
2019-03-03 23:30 | 186 | 186
2019-03-04 | 172 | 172
2019-03-04 00:30 | 160 | 160
2019-03-04 01:00 | 154 | 153
2019-03-04 01:30 | 149 | 149
2019-03-04 02:00 | 146 | 146
2019-03-04 02:30 | 145 | 144
2019-03-04 03:00 | 144 | 143
2019-03-04 03:30 | 144 | 143
2019-03-04 04:00 | 144 | 144
2019-03-04 04:30 | 147 | 147
2019-03-04 05:00 | 153 | 153
2019-03-04 05:30 | 168 | 168
2019-03-04 06:00 | 181 | 181
2019-03-04 06:30 | 201 | 200
2019-03-04 07:00 | 213 | 212
2019-03-04 07:30 | 224 | 223
2019-03-04 08:00 | 227 | 227
2019-03-04 08:30 | 228 | 228
2019-03-04 09:00 | 229 | 229
2019-03-04 09:30 | 232 | 231
2019-03-04 10:00 | 227 | 226
2019-03-04 10:30 | 228 | 228
2019-03-04 11:00 | 226 | 226
2019-03-04 11:30 | 226 | 226
2019-03-04 12:00 | 226 | 225
2019-03-04 12:30 | 225 | 225
2019-03-04 13:00 | 224 | 224
2019-03-04 13:30 | 225 | 225
2019-03-04 14:00 | 227 | 227
2019-03-04 14:30 | 232 | 231
2019-03-04 15:00 | 235 | 235
2019-03-04 15:30 | 244 | 244
2019-03-04 16:00 | 258 | 258
2019-03-04 16:30 | 272 | 272
2019-03-04 17:00 | 280 | 280
2019-03-04 17:30 | 285 | 285
2019-03-04 18:00 | 284 | 284
2019-03-04 18:30 | 284 | 284
2019-03-04 19:00 | 294 | 293
2019-03-04 19:30 | 288 | 288
2019-03-04 20:00 | 282 | 282
2019-03-04 20:30 | 274 | 274
2019-03-04 21:00 | 260 | 259
2019-03-04 21:30 | 248 | 247
2019-03-04 22:00 | 237 | 237
2019-03-04 22:30 | 230 | 229
2019-03-04 23:00 | 223 | 222
2019-03-04 23:30 | 208 | 207
2019-03-05 | 191 | 191
2019-03-05 00:30 | 177 | 177
2019-03-05 01:00 | 170 | 170
2019-03-05 01:30 | 165 | 165
2019-03-05 02:00 | 162 | 162
2019-03-05 02:30 | 161 | 161
2019-03-05 03:00 | 160 | 160
2019-03-05 03:30 | 160 | 160
2019-03-05 04:00 | 159 | 159
2019-03-05 04:30 | 162 | 162
2019-03-05 05:00 | 169 | 169
2019-03-05 05:30 | 181 | 181
2019-03-05 06:00 | 191 | 191
2019-03-05 06:30 | 210 | 209
2019-03-05 07:00 | 220 | 220
2019-03-05 07:30 | 232 | 231
2019-03-05 08:00 | 236 | 236
2019-03-05 08:30 | 238 | 238
2019-03-05 09:00 | 236 | 235
2019-03-05 09:30 | 234 | 234
2019-03-05 10:00 | 230 | 230
2019-03-05 10:30 | 228 | 228
2019-03-05 11:00 | 227 | 226
2019-03-05 11:30 | 225 | 225
2019-03-05 12:00 | 231 | 231
2019-03-05 12:30 | 234 | 234
2019-03-05 13:00 | 230 | 230
2019-03-05 13:30 | 232 | 232
2019-03-05 14:00 | 241 | 241
2019-03-05 14:30 | 249 | 249
2019-03-05 15:00 | 252 | 252
2019-03-05 15:30 | 254 | 254
2019-03-05 16:00 | 263 | 263
2019-03-05 16:30 | 280 | 280
2019-03-05 17:00 | 290 | 290
2019-03-05 17:30 | 292 | 292
2019-03-05 18:00 | 288 | 288
2019-03-05 18:30 | 290 | 290
2019-03-05 19:00 | 301 | 300
2019-03-05 19:30 | 295 | 295
2019-03-05 20:00 | 289 | 289
2019-03-05 20:30 | 282 | 281
2019-03-05 21:00 | 268 | 267
2019-03-05 21:30 | 255 | 253
2019-03-05 22:00 | 245 | 243
2019-03-05 22:30 | 237 | 235
2019-03-05 23:00 | 228 | 226
2019-03-05 23:30 | 212 | 211
2019-03-06 | 196 | 195
2019-03-06 00:30 | 181 | 181
2019-03-06 01:00 | 175 | 175
2019-03-06 01:30 | 169 | 169
2019-03-06 02:00 | 166 | 166
2019-03-06 02:30 | 164 | 164
2019-03-06 03:00 | 162 | 162
2019-03-06 03:30 | 163 | 163
2019-03-06 04:00 | 161 | 161
2019-03-06 04:30 | 164 | 164
2019-03-06 05:00 | 169 | 169
2019-03-06 05:30 | 182 | 182
2019-03-06 06:00 | 192 | 191
2019-03-06 06:30 | 211 | 210
2019-03-06 07:00 | 223 | 222
2019-03-06 07:30 | 232 | 231
2019-03-06 08:00 | 248 | 248
2019-03-06 08:30 | 257 | 257
2019-03-06 09:00 | 259 | 258
2019-03-06 09:30 | 264 | 264
2019-03-06 10:00 | 265 | 265
2019-03-06 10:30 | 268 | 268
2019-03-06 11:00 | 271 | 271
2019-03-06 11:30 | 271 | 271
2019-03-06 12:00 | 275 | 274
2019-03-06 12:30 | 281 | 280
2019-03-06 13:00 | 287 | 286
2019-03-06 13:30 | 298 | 298
2019-03-06 14:00 | 307 | 307
2019-03-06 14:30 | 313 | 312
2019-03-06 15:00 | 321 | 320
2019-03-06 15:30 | 331 | 330
2019-03-06 16:00 | 348 | 348
2019-03-06 16:30 | 353 | 353
2019-03-06 17:00 | 349 | 349
2019-03-06 17:30 | 351 | 351
2019-03-06 18:00 | 346 | 346
2019-03-06 18:30 | 342 | 342
2019-03-06 19:00 | 351 | 350
2019-03-06 19:30 | 345 | 345
2019-03-06 20:00 | 338 | 338
2019-03-06 20:30 | 327 | 327
2019-03-06 21:00 | 310 | 310
2019-03-06 21:30 | 296 | 295
2019-03-06 22:00 | 281 | 280
2019-03-06 22:30 | 270 | 269
2019-03-06 23:00 | 260 | 258
2019-03-06 23:30 | 240 | 239
2019-03-07 | 222 | 221
2019-03-07 00:30 | 206 | 205
2019-03-07 01:00 | 198 | 197
2019-03-07 01:30 | 190 | 190
2019-03-07 02:00 | 185 | 185
2019-03-07 02:30 | 182 | 182
2019-03-07 03:00 | 179 | 179
2019-03-07 03:30 | 178 | 178
2019-03-07 04:00 | 176 | 176
2019-03-07 04:30 | 179 | 178
2019-03-07 05:00 | 183 | 183
2019-03-07 05:30 | 196 | 195
2019-03-07 06:00 | 205 | 204
2019-03-07 06:30 | 222 | 221
2019-03-07 07:00 | 249 | 247
2019-03-07 07:30 | 267 | 267
2019-03-07 08:00 | 275 | 275
2019-03-07 08:30 | 274 | 274
2019-03-07 09:00 | 277 | 277
2019-03-07 09:30 | 278 | 278
2019-03-07 10:00 | 285 | 285
2019-03-07 10:30 | 288 | 288
2019-03-07 11:00 | 298 | 298
2019-03-07 11:30 | 300 | 300
2019-03-07 12:00 | 295 | 295
2019-03-07 12:30 | 292 | 292
2019-03-07 13:00 | 296 | 296
2019-03-07 13:30 | 307 | 307
2019-03-07 14:00 | 312 | 312
2019-03-07 14:30 | 319 | 319
2019-03-07 15:00 | 327 | 327
2019-03-07 15:30 | 333 | 333
2019-03-07 16:00 | 347 | 347
2019-03-07 16:30 | 362 | 362
2019-03-07 17:00 | 372 | 372
2019-03-07 17:30 | 367 | 367
2019-03-07 18:00 | 363 | 362
2019-03-07 18:30 | 361 | 361
2019-03-07 19:00 | 367 | 367
2019-03-07 19:30 | 358 | 358
2019-03-07 20:00 | 347 | 346
2019-03-07 20:30 | 337 | 337
2019-03-07 21:00 | 322 | 322
2019-03-07 21:30 | 304 | 303
2019-03-07 22:00 | 284 | 284
2019-03-07 22:30 | 271 | 270
2019-03-07 23:00 | 260 | 260
2019-03-07 23:30 | 241 | 241
2019-03-08 | 222 | 221
2019-03-08 00:30 | 205 | 205
2019-03-08 01:00 | 195 | 195
2019-03-08 01:30 | 190 | 190
2019-03-08 02:00 | 186 | 186
2019-03-08 02:30 | 183 | 183
2019-03-08 03:00 | 182 | 182
2019-03-08 03:30 | 182 | 182
2019-03-08 04:00 | 181 | 181
2019-03-08 04:30 | 185 | 185
2019-03-08 05:00 | 190 | 190
2019-03-08 05:30 | 202 | 202
2019-03-08 06:00 | 214 | 213
2019-03-08 06:30 | 233 | 232
2019-03-08 07:00 | 249 | 249
2019-03-08 07:30 | 264 | 264
2019-03-08 08:00 | 272 | 272
2019-03-08 08:30 | 272 | 272
2019-03-08 09:00 | 270 | 269
2019-03-08 09:30 | 269 | 269
2019-03-08 10:00 | 270 | 270
2019-03-08 10:30 | 272 | 271
2019-03-08 11:00 | 267 | 266
2019-03-08 11:30 | 267 | 267
2019-03-08 12:00 | 270 | 270
2019-03-08 12:30 | 271 | 271
2019-03-08 13:00 | 277 | 277
2019-03-08 13:30 | 275 | 275
2019-03-08 14:00 | 268 | 268
2019-03-08 14:30 | 267 | 267
2019-03-08 15:00 | 267 | 267
2019-03-08 15:30 | 267 | 267
2019-03-08 16:00 | 275 | 275
2019-03-08 16:30 | 285 | 284
2019-03-08 17:00 | 294 | 294
2019-03-08 17:30 | 294 | 294
2019-03-08 18:00 | 288 | 288
2019-03-08 18:30 | 286 | 286
2019-03-08 19:00 | 294 | 293
2019-03-08 19:30 | 288 | 288
2019-03-08 20:00 | 283 | 283
2019-03-08 20:30 | 276 | 276
2019-03-08 21:00 | 263 | 263
2019-03-08 21:30 | 254 | 254
2019-03-08 22:00 | 241 | 241
2019-03-08 22:30 | 234 | 234
2019-03-08 23:00 | 227 | 227
2019-03-08 23:30 | 212 | 212
2019-03-09 | 196 | 196
2019-03-09 00:30 | 181 | 181
2019-03-09 01:00 | 174 | 174
2019-03-09 01:30 | 168 | 168
2019-03-09 02:00 | 163 | 163
2019-03-09 02:30 | 161 | 161
2019-03-09 03:00 | 159 | 159
2019-03-09 03:30 | 158 | 158
2019-03-09 04:00 | 158 | 158
2019-03-09 04:30 | 158 | 158
2019-03-09 05:00 | 160 | 160
2019-03-09 05:30 | 163 | 163
2019-03-09 06:00 | 165 | 165
2019-03-09 06:30 | 171 | 171
2019-03-09 07:00 | 176 | 176
2019-03-09 07:30 | 181 | 181
2019-03-09 08:00 | 182 | 181
2019-03-09 08:30 | 186 | 185
2019-03-09 09:00 | 189 | 188
2019-03-09 09:30 | 194 | 193
2019-03-09 10:00 | 199 | 197
2019-03-09 10:30 | 202 | 201
2019-03-09 11:00 | 204 | 204
2019-03-09 11:30 | 203 | 203
2019-03-09 12:00 | 206 | 206
2019-03-09 12:30 | 210 | 210
2019-03-09 13:00 | 213 | 213
2019-03-09 13:30 | 221 | 221
2019-03-09 14:00 | 228 | 228
2019-03-09 14:30 | 234 | 234
2019-03-09 15:00 | 244 | 243
2019-03-09 15:30 | 254 | 253
2019-03-09 16:00 | 266 | 265
2019-03-09 16:30 | 278 | 277
2019-03-09 17:00 | 290 | 289
2019-03-09 17:30 | 292 | 291
2019-03-09 18:00 | 287 | 287
2019-03-09 18:30 | 286 | 286
2019-03-09 19:00 | 291 | 290
2019-03-09 19:30 | 285 | 284
2019-03-09 20:00 | 279 | 278
2019-03-09 20:30 | 272 | 271
2019-03-09 21:00 | 260 | 259
2019-03-09 21:30 | 247 | 247
2019-03-09 22:00 | 238 | 238
2019-03-09 22:30 | 233 | 233
2019-03-09 23:00 | 228 | 228
2019-03-09 23:30 | 213 | 213
2019-03-10 | 197 | 196
2019-03-10 00:30 | 182 | 182
2019-03-10 01:00 | 174 | 174
2019-03-10 01:30 | 169 | 169
2019-03-10 02:00 | 164 | 164
2019-03-10 02:30 | 161 | 161
2019-03-10 03:00 | 159 | 159
2019-03-10 03:30 | 159 | 159
2019-03-10 04:00 | 157 | 157
2019-03-10 04:30 | 157 | 157
2019-03-10 05:00 | 157 | 157
2019-03-10 05:30 | 158 | 158
2019-03-10 06:00 | 158 | 158
2019-03-10 06:30 | 160 | 160
2019-03-10 07:00 | 161 | 161
2019-03-10 07:30 | 165 | 165
2019-03-10 08:00 | 167 | 167
2019-03-10 08:30 | 171 | 171
2019-03-10 09:00 | 178 | 177
2019-03-10 09:30 | 184 | 183
2019-03-10 10:00 | 186 | 184
2019-03-10 10:30 | 189 | 189
2019-03-10 11:00 | 189 | 189
2019-03-10 11:30 | 191 | 191
2019-03-10 12:00 | 197 | 197
2019-03-10 12:30 | 208 | 207
2019-03-10 13:00 | 220 | 219
2019-03-10 13:30 | 234 | 233
2019-03-10 14:00 | 238 | 238
2019-03-10 14:30 | 248 | 247
2019-03-10 15:00 | 258 | 256
2019-03-10 15:30 | 271 | 269
2019-03-10 16:00 | 287 | 285
2019-03-10 16:30 | 298 | 297
2019-03-10 17:00 | 311 | 309
2019-03-10 17:30 | 317 | 315
2019-03-10 18:00 | 314 | 313
2019-03-10 18:30 | 315 | 314
2019-03-10 19:00 | 320 | 318
2019-03-10 19:30 | 308 | 307
2019-03-10 20:00 | 300 | 298
2019-03-10 20:30 | 291 | 290
2019-03-10 21:00 | 276 | 275
2019-03-10 21:30 | 264 | 263
2019-03-10 22:00 | 250 | 250
2019-03-10 22:30 | 242 | 242
2019-03-10 23:00 | 235 | 235
2019-03-10 23:30 | 220 | 220
2019-03-11 | 203 | 203
2019-03-11 00:30 | 188 | 188
2019-03-11 01:00 | 182 | 181
2019-03-11 01:30 | 176 | 176
2019-03-11 02:00 | 173 | 173
2019-03-11 02:30 | 170 | 170
2019-03-11 03:00 | 168 | 168
2019-03-11 03:30 | 166 | 166
2019-03-11 04:00 | 170 | 170
2019-03-11 04:30 | 173 | 173
2019-03-11 05:00 | 178 | 177
2019-03-11 05:30 | 191 | 191
2019-03-11 06:00 | 202 | 201
2019-03-11 06:30 | 224 | 223
2019-03-11 07:00 | 240 | 239
2019-03-11 07:30 | 255 | 254
2019-03-11 08:00 | 262 | 262
2019-03-11 08:30 | 264 | 263
2019-03-11 09:00 | 267 | 267
2019-03-11 09:30 | 273 | 272
2019-03-11 10:00 | 278 | 277
2019-03-11 10:30 | 285 | 285
2019-03-11 11:00 | 299 | 298
2019-03-11 11:30 | 305 | 304
2019-03-11 12:00 | 316 | 316
2019-03-11 12:30 | 325 | 325
2019-03-11 13:00 | 336 | 336
2019-03-11 13:30 | 350 | 349
2019-03-11 14:00 | 383 | 382
2019-03-11 14:30 | 387 | 387
2019-03-11 15:00 | 376 | 376
2019-03-11 15:30 | 373 | 373
2019-03-11 16:00 | 368 | 368
2019-03-11 16:30 | 373 | 372
2019-03-11 17:00 | 379 | 378
2019-03-11 17:30 | 377 | 377
2019-03-11 18:00 | 370 | 370
2019-03-11 18:30 | 366 | 366
2019-03-11 19:00 | 367 | 367
2019-03-11 19:30 | 357 | 357
2019-03-11 20:00 | 347 | 347
2019-03-11 20:30 | 336 | 336
2019-03-11 21:00 | 318 | 318
2019-03-11 21:30 | 300 | 300
2019-03-11 22:00 | 284 | 282
2019-03-11 22:30 | 272 | 270
2019-03-11 23:00 | 258 | 257
2019-03-11 23:30 | 238 | 237
2019-03-12 | 220 | 219
2019-03-12 00:30 | 205 | 204
2019-03-12 01:00 | 196 | 196
2019-03-12 01:30 | 190 | 190
2019-03-12 02:00 | 186 | 186
2019-03-12 02:30 | 182 | 182
2019-03-12 03:00 | 180 | 179
2019-03-12 03:30 | 179 | 179
2019-03-12 04:00 | 178 | 178
2019-03-12 04:30 | 181 | 181
2019-03-12 05:00 | 190 | 189
2019-03-12 05:30 | 202 | 201
2019-03-12 06:00 | 213 | 211
2019-03-12 06:30 | 234 | 233
2019-03-12 07:00 | 254 | 254
2019-03-12 07:30 | 271 | 270
2019-03-12 08:00 | 272 | 272
2019-03-12 08:30 | 279 | 279
2019-03-12 09:00 | 280 | 280
2019-03-12 09:30 | 277 | 277
2019-03-12 10:00 | 278 | 278
2019-03-12 10:30 | 286 | 285
2019-03-12 11:00 | 295 | 295
2019-03-12 11:30 | 306 | 305
2019-03-12 12:00 | 321 | 320
2019-03-12 12:30 | 342 | 341
2019-03-12 13:00 | 346 | 346
2019-03-12 13:30 | 349 | 349
2019-03-12 14:00 | 355 | 355
2019-03-12 14:30 | 362 | 362
2019-03-12 15:00 | 367 | 367
2019-03-12 15:30 | 381 | 381
2019-03-12 16:00 | 393 | 392
2019-03-12 16:30 | 395 | 394
2019-03-12 17:00 | 405 | 403
2019-03-12 17:30 | 409 | 408
2019-03-12 18:00 | 407 | 407
2019-03-12 18:30 | 404 | 403
2019-03-12 19:00 | 408 | 406
2019-03-12 19:30 | 396 | 395
2019-03-12 20:00 | 378 | 378
2019-03-12 20:30 | 376 | 376
2019-03-12 21:00 | 364 | 364
2019-03-12 21:30 | 338 | 338
2019-03-12 22:00 | 318 | 318
2019-03-12 22:30 | 285 | 284
2019-03-12 23:00 | 270 | 269
2019-03-12 23:30 | 253 | 252
2019-03-13 | 237 | 236
2019-03-13 00:30 | 225 | 224
2019-03-13 01:00 | 221 | 220
2019-03-13 01:30 | 208 | 208
2019-03-13 02:00 | 197 | 197
2019-03-13 02:30 | 192 | 192
2019-03-13 03:00 | 188 | 188
2019-03-13 03:30 | 186 | 186
2019-03-13 04:00 | 185 | 185
2019-03-13 04:30 | 186 | 186
2019-03-13 05:00 | 190 | 190
2019-03-13 05:30 | 199 | 199
2019-03-13 06:00 | 208 | 208
2019-03-13 06:30 | 228 | 227
2019-03-13 07:00 | 246 | 245
2019-03-13 07:30 | 258 | 257
2019-03-13 08:00 | 261 | 261
2019-03-13 08:30 | 260 | 260
2019-03-13 09:00 | 261 | 260
2019-03-13 09:30 | 264 | 264
2019-03-13 10:00 | 268 | 267
2019-03-13 10:30 | 275 | 275
2019-03-13 11:00 | 283 | 283
2019-03-13 11:30 | 292 | 292
2019-03-13 12:00 | 303 | 303
2019-03-13 12:30 | 311 | 311
2019-03-13 13:00 | 320 | 320
2019-03-13 13:30 | 325 | 325
2019-03-13 14:00 | 330 | 329
2019-03-13 14:30 | 333 | 333
2019-03-13 15:00 | 338 | 337
2019-03-13 15:30 | 345 | 345
2019-03-13 16:00 | 355 | 355
2019-03-13 16:30 | 365 | 365
2019-03-13 17:00 | 373 | 372
2019-03-13 17:30 | 371 | 371
2019-03-13 18:00 | 362 | 362
2019-03-13 18:30 | 354 | 353
2019-03-13 19:00 | 357 | 357
2019-03-13 19:30 | 347 | 347
2019-03-13 20:00 | 338 | 338
2019-03-13 20:30 | 327 | 327
2019-03-13 21:00 | 308 | 308
2019-03-13 21:30 | 293 | 293
2019-03-13 22:00 | 278 | 278
2019-03-13 22:30 | 269 | 268
2019-03-13 23:00 | 256 | 256
2019-03-13 23:30 | 237 | 237
2019-03-14 | 219 | 219
2019-03-14 00:30 | 206 | 206
2019-03-14 01:00 | 199 | 199
2019-03-14 01:30 | 194 | 193
2019-03-14 02:00 | 189 | 188
2019-03-14 02:30 | 185 | 184
2019-03-14 03:00 | 183 | 182
2019-03-14 03:30 | 182 | 182
2019-03-14 04:00 | 181 | 180
2019-03-14 04:30 | 184 | 183
2019-03-14 05:00 | 189 | 188
2019-03-14 05:30 | 200 | 199
2019-03-14 06:00 | 209 | 209
2019-03-14 06:30 | 228 | 228
2019-03-14 07:00 | 241 | 241
2019-03-14 07:30 | 255 | 255
2019-03-14 08:00 | 260 | 260
2019-03-14 08:30 | 267 | 267
2019-03-14 09:00 | 268 | 268
2019-03-14 09:30 | 272 | 272
2019-03-14 10:00 | 273 | 273
2019-03-14 10:30 | 275 | 275
2019-03-14 11:00 | 275 | 274
2019-03-14 11:30 | 284 | 284
2019-03-14 12:00 | 296 | 295
2019-03-14 12:30 | 291 | 290
2019-03-14 13:00 | 302 | 302
2019-03-14 13:30 | 307 | 306
2019-03-14 14:00 | 317 | 316
2019-03-14 14:30 | 319 | 319
2019-03-14 15:00 | 316 | 316
2019-03-14 15:30 | 321 | 320
2019-03-14 16:00 | 322 | 322
2019-03-14 16:30 | 335 | 335
2019-03-14 17:00 | 340 | 340
2019-03-14 17:30 | 336 | 336
2019-03-14 18:00 | 337 | 335
2019-03-14 18:30 | 340 | 338
2019-03-14 19:00 | 349 | 346
2019-03-14 19:30 | 341 | 340
2019-03-14 20:00 | 334 | 333
2019-03-14 20:30 | 324 | 323
2019-03-14 21:00 | 302 | 301
2019-03-14 21:30 | 280 | 280
2019-03-14 22:00 | 259 | 259
2019-03-14 22:30 | 244 | 244
2019-03-14 23:00 | 232 | 231
2019-03-14 23:30 | 215 | 215
2019-03-15 | 199 | 199
2019-03-15 00:30 | 185 | 185
2019-03-15 01:00 | 177 | 177
2019-03-15 01:30 | 172 | 172
2019-03-15 02:00 | 168 | 168
2019-03-15 02:30 | 165 | 165
2019-03-15 03:00 | 163 | 163
2019-03-15 03:30 | 163 | 163
2019-03-15 04:00 | 164 | 163
2019-03-15 04:30 | 167 | 166
2019-03-15 05:00 | 172 | 172
2019-03-15 05:30 | 185 | 184
2019-03-15 06:00 | 195 | 193
2019-03-15 06:30 | 212 | 212
2019-03-15 07:00 | 225 | 225
2019-03-15 07:30 | 235 | 235
2019-03-15 08:00 | 237 | 237
2019-03-15 08:30 | 234 | 234
2019-03-15 09:00 | 234 | 234
2019-03-15 09:30 | 237 | 237
2019-03-15 10:00 | 239 | 239
2019-03-15 10:30 | 242 | 242
2019-03-15 11:00 | 247 | 247
2019-03-15 11:30 | 255 | 254
2019-03-15 12:00 | 273 | 272
2019-03-15 12:30 | 293 | 292
2019-03-15 13:00 | 307 | 305
2019-03-15 13:30 | 313 | 313
2019-03-15 14:00 | 340 | 340
2019-03-15 14:30 | 349 | 349
2019-03-15 15:00 | 350 | 350
2019-03-15 15:30 | 347 | 347
2019-03-15 16:00 | 345 | 345
2019-03-15 16:30 | 340 | 340
2019-03-15 17:00 | 326 | 326
2019-03-15 17:30 | 300 | 300
2019-03-15 18:00 | 280 | 280
2019-03-15 18:30 | 275 | 274
2019-03-15 19:00 | 268 | 268
2019-03-15 19:30 | 258 | 258
2019-03-15 20:00 | 254 | 254
2019-03-15 20:30 | 247 | 247
2019-03-15 21:00 | 235 | 235
2019-03-15 21:30 | 224 | 224
2019-03-15 22:00 | 217 | 217
2019-03-15 22:30 | 212 | 212
2019-03-15 23:00 | 207 | 207
2019-03-15 23:30 | 193 | 193
2019-03-16 | 179 | 178
2019-03-16 00:30 | 167 | 166
2019-03-16 01:00 | 161 | 160
2019-03-16 01:30 | 158 | 157
2019-03-16 02:00 | 155 | 154
2019-03-16 02:30 | 154 | 153
2019-03-16 03:00 | 153 | 152
2019-03-16 03:30 | 152 | 151
2019-03-16 04:00 | 152 | 151
2019-03-16 04:30 | 152 | 151
2019-03-16 05:00 | 153 | 152
2019-03-16 05:30 | 156 | 155
2019-03-16 06:00 | 160 | 159
2019-03-16 06:30 | 165 | 164
2019-03-16 07:00 | 171 | 170
2019-03-16 07:30 | 181 | 181
2019-03-16 08:00 | 188 | 188
2019-03-16 08:30 | 204 | 204
2019-03-16 09:00 | 206 | 206
2019-03-16 09:30 | 193 | 193
2019-03-16 10:00 | 197 | 197
2019-03-16 10:30 | 209 | 209
2019-03-16 11:00 | 208 | 208
2019-03-16 11:30 | 208 | 208
2019-03-16 12:00 | 207 | 206
2019-03-16 12:30 | 207 | 207
2019-03-16 13:00 | 205 | 205
2019-03-16 13:30 | 209 | 208
2019-03-16 14:00 | 201 | 201
2019-03-16 14:30 | 194 | 194
2019-03-16 15:00 | 200 | 200
2019-03-16 15:30 | 195 | 194
2019-03-16 16:00 | 211 | 211
2019-03-16 16:30 | 222 | 221
2019-03-16 17:00 | 227 | 226
2019-03-16 17:30 | 229 | 228
2019-03-16 18:00 | 228 | 227
2019-03-16 18:30 | 234 | 233
2019-03-16 19:00 | 242 | 241
2019-03-16 19:30 | 236 | 234
2019-03-16 20:00 | 232 | 231
2019-03-16 20:30 | 228 | 226
2019-03-16 21:00 | 218 | 217
2019-03-16 21:30 | 211 | 211
2019-03-16 22:00 | 205 | 205
2019-03-16 22:30 | 204 | 203
2019-03-16 23:00 | 203 | 203
2019-03-16 23:30 | 191 | 191
2019-03-17 | 178 | 178
2019-03-17 00:30 | 165 | 165
2019-03-17 01:00 | 158 | 158
2019-03-17 01:30 | 154 | 154
2019-03-17 02:00 | 150 | 150
2019-03-17 02:30 | 147 | 147
2019-03-17 03:00 | 145 | 145
2019-03-17 03:30 | 143 | 143
2019-03-17 04:00 | 143 | 143
2019-03-17 04:30 | 142 | 142
2019-03-17 05:00 | 144 | 144
2019-03-17 05:30 | 146 | 146
2019-03-17 06:00 | 148 | 148
2019-03-17 06:30 | 149 | 149
2019-03-17 07:00 | 147 | 147
2019-03-17 07:30 | 156 | 156
2019-03-17 08:00 | 166 | 166
2019-03-17 08:30 | 177 | 176
2019-03-17 09:00 | 180 | 179
2019-03-17 09:30 | 189 | 188
2019-03-17 10:00 | 183 | 182
2019-03-17 10:30 | 178 | 178
2019-03-17 11:00 | 185 | 184
2019-03-17 11:30 | 180 | 180
2019-03-17 12:00 | 179 | 178
2019-03-17 12:30 | 191 | 191
2019-03-17 13:00 | 194 | 194
2019-03-17 13:30 | 199 | 199
2019-03-17 14:00 | 194 | 194
2019-03-17 14:30 | 187 | 187
2019-03-17 15:00 | 199 | 199
2019-03-17 15:30 | 225 | 225
2019-03-17 16:00 | 241 | 240
2019-03-17 16:30 | 246 | 246
2019-03-17 17:00 | 254 | 254
2019-03-17 17:30 | 260 | 259
2019-03-17 18:00 | 257 | 256
2019-03-17 18:30 | 255 | 255
2019-03-17 19:00 | 254 | 253
2019-03-17 19:30 | 245 | 244
2019-03-17 20:00 | 240 | 239
2019-03-17 20:30 | 235 | 235
2019-03-17 21:00 | 224 | 224
2019-03-17 21:30 | 216 | 216
2019-03-17 22:00 | 208 | 208
2019-03-17 22:30 | 204 | 204
2019-03-17 23:00 | 200 | 199
2019-03-17 23:30 | 189 | 188
2019-03-18 | 176 | 174
2019-03-18 00:30 | 164 | 163
2019-03-18 01:00 | 158 | 155
2019-03-18 01:30 | 153 | 151
2019-03-18 02:00 | 151 | 148
2019-03-18 02:30 | 149 | 146
2019-03-18 03:00 | 148 | 145
2019-03-18 03:30 | 148 | 145
2019-03-18 04:00 | 149 | 146
2019-03-18 04:30 | 152 | 149
2019-03-18 05:00 | 158 | 155
2019-03-18 05:30 | 169 | 168
2019-03-18 06:00 | 180 | 180
2019-03-18 06:30 | 199 | 199
2019-03-18 07:00 | 213 | 213
2019-03-18 07:30 | 225 | 225
2019-03-18 08:00 | 225 | 225
2019-03-18 08:30 | 220 | 220
2019-03-18 09:00 | 215 | 215
2019-03-18 09:30 | 218 | 218
2019-03-18 10:00 | 221 | 220
2019-03-18 10:30 | 227 | 226
2019-03-18 11:00 | 229 | 229
2019-03-18 11:30 | 233 | 232
2019-03-18 12:00 | 232 | 232
2019-03-18 12:30 | 235 | 235
2019-03-18 13:00 | 252 | 252
2019-03-18 13:30 | 293 | 293
2019-03-18 14:00 | 313 | 313
2019-03-18 14:30 | 300 | 300
2019-03-18 15:00 | 271 | 271
2019-03-18 15:30 | 249 | 249
2019-03-18 16:00 | 258 | 258
2019-03-18 16:30 | 274 | 274
2019-03-18 17:00 | 281 | 281
2019-03-18 17:30 | 289 | 289
2019-03-18 18:00 | 289 | 289
2019-03-18 18:30 | 290 | 290
2019-03-18 19:00 | 295 | 295
2019-03-18 19:30 | 285 | 285
2019-03-18 20:00 | 277 | 277
2019-03-18 20:30 | 269 | 268
2019-03-18 21:00 | 254 | 254
2019-03-18 21:30 | 241 | 241
2019-03-18 22:00 | 231 | 231
2019-03-18 22:30 | 225 | 225
2019-03-18 23:00 | 216 | 215
2019-03-18 23:30 | 200 | 200
2019-03-19 | 184 | 184
2019-03-19 00:30 | 171 | 171
2019-03-19 01:00 | 164 | 164
2019-03-19 01:30 | 159 | 158
2019-03-19 02:00 | 157 | 156
2019-03-19 02:30 | 154 | 153
2019-03-19 03:00 | 154 | 152
2019-03-19 03:30 | 154 | 153
2019-03-19 04:00 | 154 | 152
2019-03-19 04:30 | 156 | 155
2019-03-19 05:00 | 162 | 161
2019-03-19 05:30 | 174 | 174
2019-03-19 06:00 | 184 | 184
2019-03-19 06:30 | 202 | 202
2019-03-19 07:00 | 217 | 217
2019-03-19 07:30 | 225 | 225
2019-03-19 08:00 | 221 | 221
2019-03-19 08:30 | 217 | 217
2019-03-19 09:00 | 211 | 211
2019-03-19 09:30 | 209 | 209
2019-03-19 10:00 | 208 | 207
2019-03-19 10:30 | 209 | 208
2019-03-19 11:00 | 213 | 213
2019-03-19 11:30 | 217 | 217
2019-03-19 12:00 | 224 | 224
2019-03-19 12:30 | 231 | 231
2019-03-19 13:00 | 240 | 240
2019-03-19 13:30 | 250 | 250
2019-03-19 14:00 | 262 | 261
2019-03-19 14:30 | 275 | 275
2019-03-19 15:00 | 289 | 288
2019-03-19 15:30 | 304 | 303
2019-03-19 16:00 | 320 | 319
2019-03-19 16:30 | 326 | 325
2019-03-19 17:00 | 336 | 335
2019-03-19 17:30 | 336 | 335
2019-03-19 18:00 | 330 | 330
2019-03-19 18:30 | 330 | 329
2019-03-19 19:00 | 335 | 335
2019-03-19 19:30 | 326 | 325
2019-03-19 20:00 | 318 | 318
2019-03-19 20:30 | 306 | 306
2019-03-19 21:00 | 290 | 290
2019-03-19 21:30 | 275 | 275
2019-03-19 22:00 | 257 | 257
2019-03-19 22:30 | 246 | 246
2019-03-19 23:00 | 235 | 234
2019-03-19 23:30 | 218 | 217
2019-03-20 | 201 | 200
2019-03-20 00:30 | 186 | 185
2019-03-20 01:00 | 177 | 177
2019-03-20 01:30 | 173 | 173
2019-03-20 02:00 | 167 | 167
2019-03-20 02:30 | 164 | 164
2019-03-20 03:00 | 163 | 163
2019-03-20 03:30 | 162 | 162
2019-03-20 04:00 | 162 | 162
2019-03-20 04:30 | 165 | 165
2019-03-20 05:00 | 171 | 171
2019-03-20 05:30 | 183 | 183
2019-03-20 06:00 | 193 | 193
2019-03-20 06:30 | 212 | 211
2019-03-20 07:00 | 224 | 224
2019-03-20 07:30 | 234 | 234
2019-03-20 08:00 | 234 | 233
2019-03-20 08:30 | 231 | 230
2019-03-20 09:00 | 230 | 228
2019-03-20 09:30 | 233 | 230
2019-03-20 10:00 | 241 | 238
2019-03-20 10:30 | 247 | 243
2019-03-20 11:00 | 242 | 240
2019-03-20 11:30 | 241 | 240
2019-03-20 12:00 | 250 | 249
2019-03-20 12:30 | 280 | 278
2019-03-20 13:00 | 286 | 286
2019-03-20 13:30 | 291 | 291
2019-03-20 14:00 | 293 | 293
2019-03-20 14:30 | 310 | 310
2019-03-20 15:00 | 323 | 323
2019-03-20 15:30 | 330 | 330
2019-03-20 16:00 | 332 | 332
2019-03-20 16:30 | 323 | 323
2019-03-20 17:00 | 329 | 329
2019-03-20 17:30 | 332 | 332
2019-03-20 18:00 | 331 | 331
2019-03-20 18:30 | 329 | 329
2019-03-20 19:00 | 334 | 334
2019-03-20 19:30 | 326 | 326
2019-03-20 20:00 | 319 | 319
2019-03-20 20:30 | 312 | 311
2019-03-20 21:00 | 295 | 295
2019-03-20 21:30 | 279 | 279
2019-03-20 22:00 | 265 | 265
2019-03-20 22:30 | 255 | 255
2019-03-20 23:00 | 243 | 242
2019-03-20 23:30 | 226 | 225
2019-03-21 | 208 | 208
2019-03-21 00:30 | 195 | 195
2019-03-21 01:00 | 187 | 187
2019-03-21 01:30 | 180 | 180
2019-03-21 02:00 | 175 | 175
2019-03-21 02:30 | 173 | 173
2019-03-21 03:00 | 170 | 170
2019-03-21 03:30 | 171 | 171
2019-03-21 04:00 | 170 | 170
2019-03-21 04:30 | 173 | 173
2019-03-21 05:00 | 179 | 179
2019-03-21 05:30 | 191 | 191
2019-03-21 06:00 | 203 | 203
2019-03-21 06:30 | 220 | 219
2019-03-21 07:00 | 237 | 237
2019-03-21 07:30 | 250 | 250
2019-03-21 08:00 | 254 | 254
2019-03-21 08:30 | 259 | 259
2019-03-21 09:00 | 262 | 262
2019-03-21 09:30 | 259 | 258
2019-03-21 10:00 | 251 | 250
2019-03-21 10:30 | 250 | 250
2019-03-21 11:00 | 255 | 254
2019-03-21 11:30 | 258 | 258
2019-03-21 12:00 | 261 | 261
2019-03-21 12:30 | 263 | 263
2019-03-21 13:00 | 271 | 271
2019-03-21 13:30 | 280 | 280
2019-03-21 14:00 | 293 | 293
2019-03-21 14:30 | 301 | 301
2019-03-21 15:00 | 306 | 306
2019-03-21 15:30 | 318 | 318
2019-03-21 16:00 | 328 | 328
2019-03-21 16:30 | 327 | 327
2019-03-21 17:00 | 340 | 340
2019-03-21 17:30 | 332 | 332
2019-03-21 18:00 | 329 | 329
2019-03-21 18:30 | 329 | 329
2019-03-21 19:00 | 331 | 331
2019-03-21 19:30 | 323 | 323
2019-03-21 20:00 | 317 | 317
2019-03-21 20:30 | 310 | 310
2019-03-21 21:00 | 296 | 296
2019-03-21 21:30 | 279 | 279
2019-03-21 22:00 | 263 | 262
2019-03-21 22:30 | 253 | 252
2019-03-21 23:00 | 244 | 243
2019-03-21 23:30 | 227 | 226
2019-03-22 | 211 | 211
2019-03-22 00:30 | 198 | 197
2019-03-22 01:00 | 188 | 188
2019-03-22 01:30 | 183 | 183
2019-03-22 02:00 | 179 | 179
2019-03-22 02:30 | 176 | 176
2019-03-22 03:00 | 173 | 173
2019-03-22 03:30 | 173 | 173
2019-03-22 04:00 | 173 | 173
2019-03-22 04:30 | 174 | 174
2019-03-22 05:00 | 181 | 181
2019-03-22 05:30 | 193 | 193
2019-03-22 06:00 | 205 | 204
2019-03-22 06:30 | 225 | 225
2019-03-22 07:00 | 240 | 240
2019-03-22 07:30 | 255 | 254
2019-03-22 08:00 | 261 | 261
2019-03-22 08:30 | 262 | 262
2019-03-22 09:00 | 266 | 266
2019-03-22 09:30 | 269 | 268
2019-03-22 10:00 | 264 | 264
2019-03-22 10:30 | 257 | 257
2019-03-22 11:00 | 257 | 257
2019-03-22 11:30 | 262 | 262
2019-03-22 12:00 | 268 | 268
2019-03-22 12:30 | 277 | 276
2019-03-22 13:00 | 275 | 275
2019-03-22 13:30 | 272 | 272
2019-03-22 14:00 | 263 | 263
2019-03-22 14:30 | 283 | 282
2019-03-22 15:00 | 287 | 287
2019-03-22 15:30 | 302 | 302
2019-03-22 16:00 | 311 | 311
2019-03-22 16:30 | 317 | 317
2019-03-22 17:00 | 314 | 314
2019-03-22 17:30 | 309 | 309
2019-03-22 18:00 | 305 | 305
2019-03-22 18:30 | 306 | 306
2019-03-22 19:00 | 307 | 307
2019-03-22 19:30 | 300 | 300
2019-03-22 20:00 | 294 | 294
2019-03-22 20:30 | 289 | 289
2019-03-22 21:00 | 276 | 276
2019-03-22 21:30 | 265 | 265
2019-03-22 22:00 | 255 | 254
2019-03-22 22:30 | 246 | 246
2019-03-22 23:00 | 238 | 238
2019-03-22 23:30 | 222 | 222
2019-03-23 | 207 | 207
2019-03-23 00:30 | 192 | 192
2019-03-23 01:00 | 184 | 184
2019-03-23 01:30 | 178 | 178
2019-03-23 02:00 | 173 | 173
2019-03-23 02:30 | 169 | 169
2019-03-23 03:00 | 167 | 167
2019-03-23 03:30 | 166 | 166
2019-03-23 04:00 | 165 | 165
2019-03-23 04:30 | 164 | 164
2019-03-23 05:00 | 165 | 165
2019-03-23 05:30 | 170 | 170
2019-03-23 06:00 | 173 | 173
2019-03-23 06:30 | 179 | 179
2019-03-23 07:00 | 183 | 183
2019-03-23 07:30 | 189 | 189
2019-03-23 08:00 | 195 | 194
2019-03-23 08:30 | 198 | 198
2019-03-23 09:00 | 204 | 204
2019-03-23 09:30 | 207 | 207
2019-03-23 10:00 | 209 | 209
2019-03-23 10:30 | 210 | 210
2019-03-23 11:00 | 209 | 209
2019-03-23 11:30 | 210 | 209
2019-03-23 12:00 | 214 | 213
2019-03-23 12:30 | 221 | 220
2019-03-23 13:00 | 232 | 231
2019-03-23 13:30 | 246 | 245
2019-03-23 14:00 | 260 | 260
2019-03-23 14:30 | 273 | 273
2019-03-23 15:00 | 288 | 287
2019-03-23 15:30 | 302 | 302
2019-03-23 16:00 | 316 | 316
2019-03-23 16:30 | 328 | 328
2019-03-23 17:00 | 336 | 336
2019-03-23 17:30 | 332 | 332
2019-03-23 18:00 | 326 | 326
2019-03-23 18:30 | 327 | 327
2019-03-23 19:00 | 328 | 328
2019-03-23 19:30 | 318 | 317
2019-03-23 20:00 | 309 | 309
2019-03-23 20:30 | 300 | 300
2019-03-23 21:00 | 286 | 286
2019-03-23 21:30 | 275 | 275
2019-03-23 22:00 | 264 | 263
2019-03-23 22:30 | 256 | 255
2019-03-23 23:00 | 246 | 246
2019-03-23 23:30 | 231 | 231
2019-03-24 | 215 | 215
2019-03-24 00:30 | 200 | 199
2019-03-24 01:00 | 191 | 191
2019-03-24 01:30 | 183 | 183
2019-03-24 02:00 | 177 | 177
2019-03-24 02:30 | 173 | 173
2019-03-24 03:00 | 169 | 169
2019-03-24 03:30 | 166 | 166
2019-03-24 04:00 | 164 | 164
2019-03-24 04:30 | 162 | 162
2019-03-24 05:00 | 162 | 162
2019-03-24 05:30 | 164 | 164
2019-03-24 06:00 | 165 | 165
2019-03-24 06:30 | 168 | 168
2019-03-24 07:00 | 170 | 170
2019-03-24 07:30 | 174 | 173
2019-03-24 08:00 | 176 | 176
2019-03-24 08:30 | 182 | 181
2019-03-24 09:00 | 186 | 185
2019-03-24 09:30 | 192 | 191
2019-03-24 10:00 | 198 | 197
2019-03-24 10:30 | 207 | 205
2019-03-24 11:00 | 215 | 213
2019-03-24 11:30 | 225 | 222
2019-03-24 12:00 | 237 | 233
2019-03-24 12:30 | 248 | 244
2019-03-24 13:00 | 262 | 260
2019-03-24 13:30 | 274 | 272
2019-03-24 14:00 | 290 | 288
2019-03-24 14:30 | 305 | 305
2019-03-24 15:00 | 319 | 319
2019-03-24 15:30 | 335 | 334
2019-03-24 16:00 | 348 | 348
2019-03-24 16:30 | 359 | 359
2019-03-24 17:00 | 369 | 369
2019-03-24 17:30 | 369 | 369
2019-03-24 18:00 | 363 | 363
2019-03-24 18:30 | 366 | 365
2019-03-24 19:00 | 366 | 365
2019-03-24 19:30 | 351 | 351
2019-03-24 20:00 | 338 | 338
2019-03-24 20:30 | 324 | 324
2019-03-24 21:00 | 305 | 304
2019-03-24 21:30 | 289 | 288
2019-03-24 22:00 | 271 | 270
2019-03-24 22:30 | 256 | 256
2019-03-24 23:00 | 246 | 246
2019-03-24 23:30 | 229 | 229
2019-03-25 | 213 | 212
2019-03-25 00:30 | 198 | 198
2019-03-25 01:00 | 191 | 190
2019-03-25 01:30 | 185 | 184
2019-03-25 02:00 | 178 | 178
2019-03-25 02:30 | 176 | 176
2019-03-25 03:00 | 174 | 174
2019-03-25 03:30 | 172 | 172
2019-03-25 04:00 | 172 | 172
2019-03-25 04:30 | 175 | 174
2019-03-25 05:00 | 180 | 180
2019-03-25 05:30 | 192 | 192
2019-03-25 06:00 | 206 | 206
2019-03-25 06:30 | 226 | 226
2019-03-25 07:00 | 241 | 241
2019-03-25 07:30 | 254 | 254
2019-03-25 08:00 | 262 | 262
2019-03-25 08:30 | 265 | 265
2019-03-25 09:00 | 258 | 258
2019-03-25 09:30 | 259 | 259
2019-03-25 10:00 | 260 | 260
2019-03-25 10:30 | 264 | 264
2019-03-25 11:00 | 269 | 269
2019-03-25 11:30 | 279 | 279
2019-03-25 12:00 | 285 | 284
2019-03-25 12:30 | 301 | 300
2019-03-25 13:00 | 300 | 299
2019-03-25 13:30 | 313 | 312
2019-03-25 14:00 | 331 | 330
2019-03-25 14:30 | 354 | 353
2019-03-25 15:00 | 367 | 367
2019-03-25 15:30 | 366 | 366
2019-03-25 16:00 | 368 | 368
2019-03-25 16:30 | 360 | 360
2019-03-25 17:00 | 368 | 368
2019-03-25 17:30 | 371 | 371
2019-03-25 18:00 | 367 | 367
2019-03-25 18:30 | 367 | 367
2019-03-25 19:00 | 366 | 366
2019-03-25 19:30 | 353 | 353
2019-03-25 20:00 | 344 | 344
2019-03-25 20:30 | 332 | 332
2019-03-25 21:00 | 315 | 315
2019-03-25 21:30 | 296 | 296
2019-03-25 22:00 | 281 | 281
2019-03-25 22:30 | 271 | 271
2019-03-25 23:00 | 260 | 260
2019-03-25 23:30 | 242 | 242
2019-03-26 | 225 | 225
2019-03-26 00:30 | 210 | 210
2019-03-26 01:00 | 201 | 201
2019-03-26 01:30 | 196 | 196
2019-03-26 02:00 | 193 | 192
2019-03-26 02:30 | 190 | 189
2019-03-26 03:00 | 185 | 185
2019-03-26 03:30 | 184 | 184
2019-03-26 04:00 | 183 | 183
2019-03-26 04:30 | 185 | 185
2019-03-26 05:00 | 191 | 191
2019-03-26 05:30 | 203 | 202
2019-03-26 06:00 | 214 | 212
2019-03-26 06:30 | 235 | 235
2019-03-26 07:00 | 250 | 250
2019-03-26 07:30 | 268 | 268
2019-03-26 08:00 | 271 | 271
2019-03-26 08:30 | 273 | 273
2019-03-26 09:00 | 273 | 272
2019-03-26 09:30 | 279 | 279
2019-03-26 10:00 | 273 | 273
2019-03-26 10:30 | 278 | 278
2019-03-26 11:00 | 285 | 285
2019-03-26 11:30 | 298 | 298
2019-03-26 12:00 | 294 | 293
2019-03-26 12:30 | 292 | 292
2019-03-26 13:00 | 297 | 297
2019-03-26 13:30 | 315 | 314
2019-03-26 14:00 | 315 | 314
2019-03-26 14:30 | 318 | 317
2019-03-26 15:00 | 330 | 329
2019-03-26 15:30 | 332 | 331
2019-03-26 16:00 | 337 | 336
2019-03-26 16:30 | 337 | 336
2019-03-26 17:00 | 339 | 339
2019-03-26 17:30 | 340 | 340
2019-03-26 18:00 | 340 | 340
2019-03-26 18:30 | 340 | 340
2019-03-26 19:00 | 342 | 342
2019-03-26 19:30 | 333 | 333
2019-03-26 20:00 | 326 | 326
2019-03-26 20:30 | 317 | 317
2019-03-26 21:00 | 301 | 301
2019-03-26 21:30 | 288 | 287
2019-03-26 22:00 | 272 | 272
2019-03-26 22:30 | 264 | 263
2019-03-26 23:00 | 250 | 250
2019-03-26 23:30 | 233 | 232
2019-03-27 | 215 | 215
2019-03-27 00:30 | 202 | 201
2019-03-27 01:00 | 195 | 194
2019-03-27 01:30 | 190 | 189
2019-03-27 02:00 | 185 | 184
2019-03-27 02:30 | 181 | 181
2019-03-27 03:00 | 180 | 179
2019-03-27 03:30 | 180 | 179
2019-03-27 04:00 | 180 | 179
2019-03-27 04:30 | 182 | 182
2019-03-27 05:00 | 188 | 188
2019-03-27 05:30 | 199 | 199
2019-03-27 06:00 | 212 | 211
2019-03-27 06:30 | 228 | 227
2019-03-27 07:00 | 241 | 241
2019-03-27 07:30 | 257 | 256
2019-03-27 08:00 | 262 | 261
2019-03-27 08:30 | 264 | 263
2019-03-27 09:00 | 265 | 265
2019-03-27 09:30 | 266 | 266
2019-03-27 10:00 | 262 | 262
2019-03-27 10:30 | 262 | 262
2019-03-27 11:00 | 263 | 263
2019-03-27 11:30 | 263 | 263
2019-03-27 12:00 | 267 | 267
2019-03-27 12:30 | 266 | 266
2019-03-27 13:00 | 265 | 265
2019-03-27 13:30 | 267 | 267
2019-03-27 14:00 | 264 | 264
2019-03-27 14:30 | 265 | 265
2019-03-27 15:00 | 263 | 263
2019-03-27 15:30 | 262 | 262
2019-03-27 16:00 | 266 | 265
2019-03-27 16:30 | 268 | 268
2019-03-27 17:00 | 272 | 272
2019-03-27 17:30 | 273 | 273
2019-03-27 18:00 | 274 | 274
2019-03-27 18:30 | 273 | 273
2019-03-27 19:00 | 272 | 271
2019-03-27 19:30 | 263 | 263
2019-03-27 20:00 | 259 | 258
2019-03-27 20:30 | 253 | 252
2019-03-27 21:00 | 240 | 240
2019-03-27 21:30 | 229 | 229
2019-03-27 22:00 | 221 | 221
2019-03-27 22:30 | 214 | 214
2019-03-27 23:00 | 208 | 208
2019-03-27 23:30 | 197 | 197
2019-03-28 | 182 | 182
2019-03-28 00:30 | 169 | 169
2019-03-28 01:00 | 161 | 160
2019-03-28 01:30 | 155 | 155
2019-03-28 02:00 | 151 | 151
2019-03-28 02:30 | 148 | 148
2019-03-28 03:00 | 147 | 147
2019-03-28 03:30 | 148 | 148
2019-03-28 04:00 | 150 | 149
2019-03-28 04:30 | 153 | 153
2019-03-28 05:00 | 159 | 159
2019-03-28 05:30 | 171 | 171
2019-03-28 06:00 | 183 | 183
2019-03-28 06:30 | 202 | 202
2019-03-28 07:00 | 220 | 219
2019-03-28 07:30 | 229 | 228
2019-03-28 08:00 | 229 | 227
2019-03-28 08:30 | 220 | 219
2019-03-28 09:00 | 217 | 215
2019-03-28 09:30 | 218 | 216
2019-03-28 10:00 | 223 | 221
2019-03-28 10:30 | 226 | 224
2019-03-28 11:00 | 229 | 229
2019-03-28 11:30 | 236 | 235
2019-03-28 12:00 | 231 | 231
2019-03-28 12:30 | 230 | 229
2019-03-28 13:00 | 239 | 239
2019-03-28 13:30 | 241 | 240
2019-03-28 14:00 | 234 | 234
2019-03-28 14:30 | 239 | 238
2019-03-28 15:00 | 236 | 236
2019-03-28 15:30 | 232 | 232
2019-03-28 16:00 | 235 | 235
2019-03-28 16:30 | 242 | 242
2019-03-28 17:00 | 252 | 252
2019-03-28 17:30 | 257 | 257
2019-03-28 18:00 | 262 | 262
2019-03-28 18:30 | 269 | 269
2019-03-28 19:00 | 273 | 272
2019-03-28 19:30 | 264 | 264
2019-03-28 20:00 | 260 | 260
2019-03-28 20:30 | 257 | 257
2019-03-28 21:00 | 244 | 244
2019-03-28 21:30 | 230 | 229
2019-03-28 22:00 | 220 | 219
2019-03-28 22:30 | 214 | 214
2019-03-28 23:00 | 208 | 208
2019-03-28 23:30 | 195 | 194
2019-03-29 | 180 | 180
2019-03-29 00:30 | 166 | 166
2019-03-29 01:00 | 159 | 159
2019-03-29 01:30 | 154 | 154
2019-03-29 02:00 | 151 | 151
2019-03-29 02:30 | 150 | 150
2019-03-29 03:00 | 148 | 148
2019-03-29 03:30 | 148 | 148
2019-03-29 04:00 | 149 | 149
2019-03-29 04:30 | 153 | 153
2019-03-29 05:00 | 159 | 159
2019-03-29 05:30 | 170 | 170
2019-03-29 06:00 | 182 | 181
2019-03-29 06:30 | 199 | 199
2019-03-29 07:00 | 212 | 211
2019-03-29 07:30 | 222 | 221
2019-03-29 08:00 | 220 | 219
2019-03-29 08:30 | 222 | 220
2019-03-29 09:00 | 222 | 220
2019-03-29 09:30 | 223 | 222
2019-03-29 10:00 | 220 | 219
2019-03-29 10:30 | 219 | 219
2019-03-29 11:00 | 215 | 214
2019-03-29 11:30 | 215 | 214
2019-03-29 12:00 | 214 | 214
2019-03-29 12:30 | 216 | 216
2019-03-29 13:00 | 219 | 219
2019-03-29 13:30 | 228 | 228
2019-03-29 14:00 | 231 | 231
2019-03-29 14:30 | 237 | 237
2019-03-29 15:00 | 238 | 238
2019-03-29 15:30 | 248 | 248
2019-03-29 16:00 | 258 | 258
2019-03-29 16:30 | 268 | 268
2019-03-29 17:00 | 278 | 278
2019-03-29 17:30 | 278 | 278
2019-03-29 18:00 | 275 | 275
2019-03-29 18:30 | 276 | 276
2019-03-29 19:00 | 277 | 277
2019-03-29 19:30 | 271 | 271
2019-03-29 20:00 | 267 | 267
2019-03-29 20:30 | 263 | 263
2019-03-29 21:00 | 252 | 252
2019-03-29 21:30 | 243 | 243
2019-03-29 22:00 | 234 | 234
2019-03-29 22:30 | 230 | 230
2019-03-29 23:00 | 225 | 225
2019-03-29 23:30 | 209 | 209
2019-03-30 | 192 | 192
2019-03-30 00:30 | 178 | 178
2019-03-30 01:00 | 171 | 171
2019-03-30 01:30 | 165 | 165
2019-03-30 02:00 | 161 | 161
2019-03-30 02:30 | 160 | 160
2019-03-30 03:00 | 159 | 159
2019-03-30 03:30 | 156 | 156
2019-03-30 04:00 | 155 | 155
2019-03-30 04:30 | 157 | 157
2019-03-30 05:00 | 158 | 158
2019-03-30 05:30 | 160 | 160
2019-03-30 06:00 | 163 | 163
2019-03-30 06:30 | 170 | 170
2019-03-30 07:00 | 177 | 177
2019-03-30 07:30 | 186 | 186
2019-03-30 08:00 | 192 | 192
2019-03-30 08:30 | 202 | 202
2019-03-30 09:00 | 209 | 209
2019-03-30 09:30 | 210 | 210
2019-03-30 10:00 | 215 | 215
2019-03-30 10:30 | 230 | 230
2019-03-30 11:00 | 218 | 218
2019-03-30 11:30 | 221 | 221
2019-03-30 12:00 | 231 | 231
2019-03-30 12:30 | 233 | 233
2019-03-30 13:00 | 232 | 232
2019-03-30 13:30 | 238 | 238
2019-03-30 14:00 | 242 | 242
2019-03-30 14:30 | 234 | 234
2019-03-30 15:00 | 237 | 237
2019-03-30 15:30 | 240 | 240
2019-03-30 16:00 | 236 | 236
2019-03-30 16:30 | 236 | 236
2019-03-30 17:00 | 239 | 239
2019-03-30 17:30 | 239 | 239
2019-03-30 18:00 | 232 | 232
2019-03-30 18:30 | 239 | 239
2019-03-30 19:00 | 241 | 241
2019-03-30 19:30 | 234 | 234
2019-03-30 20:00 | 230 | 229
2019-03-30 20:30 | 223 | 223
2019-03-30 21:00 | 212 | 211
2019-03-30 21:30 | 206 | 206
2019-03-30 22:00 | 200 | 199
2019-03-30 22:30 | 198 | 198
2019-03-30 23:00 | 196 | 196
2019-03-30 23:30 | 184 | 184
2019-03-31 | 171 | 171
2019-03-31 00:30 | 159 | 159
2019-03-31 01:00 | 151 | 150
2019-03-31 01:30 | 145 | 144
2019-03-31 02:00 | 139 | 139
2019-03-31 02:30 | 137 | 136
2019-03-31 03:00 | 135 | 134
2019-03-31 03:30 | 133 | 132
2019-03-31 04:00 | 132 | 131
2019-03-31 04:30 | 133 | 132
2019-03-31 05:00 | 133 | 132
2019-03-31 05:30 | 133 | 133
2019-03-31 06:00 | 136 | 135
2019-03-31 06:30 | 139 | 138
2019-03-31 07:00 | 138 | 137
2019-03-31 07:30 | 137 | 136
2019-03-31 08:00 | 133 | 132
2019-03-31 08:30 | 130 | 130
2019-03-31 09:00 | 124 | 124
2019-03-31 09:30 | 119 | 118
2019-03-31 10:00 | 113 | 113
2019-03-31 10:30 | 108 | 108
2019-03-31 11:00 | 104 | 104
2019-03-31 11:30 | 102 | 102
2019-03-31 12:00 | 102 | 102
2019-03-31 12:30 | 104 | 104
2019-03-31 13:00 | 107 | 107
2019-03-31 13:30 | 112 | 112
2019-03-31 14:00 | 120 | 120
2019-03-31 14:30 | 128 | 128
2019-03-31 15:00 | 139 | 139
2019-03-31 15:30 | 151 | 151
2019-03-31 16:00 | 166 | 166
2019-03-31 16:30 | 181 | 180
2019-03-31 17:00 | 198 | 198
2019-03-31 17:30 | 211 | 211
2019-03-31 18:00 | 218 | 218
2019-03-31 18:30 | 230 | 230
2019-03-31 19:00 | 232 | 232
2019-03-31 19:30 | 222 | 222
2019-03-31 20:00 | 215 | 215
2019-03-31 20:30 | 210 | 209
2019-03-31 21:00 | 199 | 199
2019-03-31 21:30 | 191 | 191
2019-03-31 22:00 | 183 | 183
2019-03-31 22:30 | 181 | 181
2019-03-31 23:00 | 178 | 178
2019-03-31 23:30 | 167 | 167
2019-04-01 | 154 | 154
2019-04-01 00:30 | 143 | 142
2019-04-01 01:00 | 137 | 136
2019-04-01 01:30 | 133 | 132
2019-04-01 02:00 | 131 | 130
2019-04-01 02:30 | 129 | 128
2019-04-01 03:00 | 130 | 129
2019-04-01 03:30 | 130 | 129
2019-04-01 04:00 | 130 | 129
2019-04-01 04:30 | 135 | 134
2019-04-01 05:00 | 142 | 142
2019-04-01 05:30 | 155 | 155
2019-04-01 06:00 | 167 | 167
2019-04-01 06:30 | 184 | 184
2019-04-01 07:00 | 196 | 196
2019-04-01 07:30 | 199 | 199
2019-04-01 08:00 | 193 | 193
2019-04-01 08:30 | 184 | 184
2019-04-01 09:00 | 176 | 176
2019-04-01 09:30 | 171 | 171
2019-04-01 10:00 | 167 | 166
2019-04-01 10:30 | 170 | 169
2019-04-01 11:00 | 169 | 169
2019-04-01 11:30 | 169 | 169
2019-04-01 12:00 | 168 | 167
2019-04-01 12:30 | 169 | 168
2019-04-01 13:00 | 173 | 173
2019-04-01 13:30 | 179 | 179
2019-04-01 14:00 | 194 | 192
2019-04-01 14:30 | 204 | 202
2019-04-01 15:00 | 204 | 203
2019-04-01 15:30 | 207 | 206
2019-04-01 16:00 | 218 | 217
2019-04-01 16:30 | 230 | 229
2019-04-01 17:00 | 241 | 240
2019-04-01 17:30 | 247 | 246
2019-04-01 18:00 | 249 | 248
2019-04-01 18:30 | 255 | 254
2019-04-01 19:00 | 256 | 255
2019-04-01 19:30 | 247 | 247
2019-04-01 20:00 | 241 | 240
2019-04-01 20:30 | 236 | 235
2019-04-01 21:00 | 223 | 222
2019-04-01 21:30 | 212 | 212
2019-04-01 22:00 | 204 | 204
2019-04-01 22:30 | 199 | 199
2019-04-01 23:00 | 195 | 195
2019-04-01 23:30 | 183 | 183
2019-04-02 | 169 | 169
2019-04-02 00:30 | 155 | 155
2019-04-02 01:00 | 148 | 147
2019-04-02 01:30 | 144 | 144
2019-04-02 02:00 | 141 | 141
2019-04-02 02:30 | 140 | 139
2019-04-02 03:00 | 138 | 138
2019-04-02 03:30 | 138 | 137
2019-04-02 04:00 | 138 | 137
2019-04-02 04:30 | 143 | 142
2019-04-02 05:00 | 149 | 149
2019-04-02 05:30 | 160 | 160
2019-04-02 06:00 | 169 | 169
2019-04-02 06:30 | 188 | 188
2019-04-02 07:00 | 202 | 201
2019-04-02 07:30 | 212 | 210
2019-04-02 08:00 | 208 | 206
2019-04-02 08:30 | 200 | 197
2019-04-02 09:00 | 187 | 185
2019-04-02 09:30 | 180 | 179
2019-04-02 10:00 | 185 | 185
2019-04-02 10:30 | 201 | 200
2019-04-02 11:00 | 206 | 204
2019-04-02 11:30 | 202 | 201
2019-04-02 12:00 | 206 | 205
2019-04-02 12:30 | 198 | 197
2019-04-02 13:00 | 191 | 190
2019-04-02 13:30 | 193 | 192
2019-04-02 14:00 | 201 | 200
2019-04-02 14:30 | 212 | 211
2019-04-02 15:00 | 212 | 212
2019-04-02 15:30 | 216 | 216
2019-04-02 16:00 | 226 | 226
2019-04-02 16:30 | 241 | 240
2019-04-02 17:00 | 247 | 247
2019-04-02 17:30 | 252 | 251
2019-04-02 18:00 | 256 | 255
2019-04-02 18:30 | 261 | 260
2019-04-02 19:00 | 262 | 261
2019-04-02 19:30 | 253 | 253
2019-04-02 20:00 | 247 | 247
2019-04-02 20:30 | 243 | 243
2019-04-02 21:00 | 231 | 230
2019-04-02 21:30 | 219 | 219
2019-04-02 22:00 | 210 | 210
2019-04-02 22:30 | 204 | 204
2019-04-02 23:00 | 198 | 197
2019-04-02 23:30 | 185 | 185
2019-04-03 | 171 | 171
2019-04-03 00:30 | 159 | 158
2019-04-03 01:00 | 151 | 151
2019-04-03 01:30 | 146 | 146
2019-04-03 02:00 | 143 | 143
2019-04-03 02:30 | 142 | 141
2019-04-03 03:00 | 140 | 140
2019-04-03 03:30 | 140 | 140
2019-04-03 04:00 | 141 | 141
2019-04-03 04:30 | 145 | 145
2019-04-03 05:00 | 151 | 151
2019-04-03 05:30 | 164 | 163
2019-04-03 06:00 | 176 | 175
2019-04-03 06:30 | 196 | 195
2019-04-03 07:00 | 208 | 207
2019-04-03 07:30 | 217 | 216
2019-04-03 08:00 | 221 | 220
2019-04-03 08:30 | 205 | 205
2019-04-03 09:00 | 195 | 194
2019-04-03 09:30 | 206 | 206
2019-04-03 10:00 | 212 | 212
2019-04-03 10:30 | 211 | 211
2019-04-03 11:00 | 203 | 203
2019-04-03 11:30 | 195 | 195
2019-04-03 12:00 | 193 | 193
2019-04-03 12:30 | 194 | 194
2019-04-03 13:00 | 200 | 200
2019-04-03 13:30 | 201 | 201
2019-04-03 14:00 | 208 | 208
2019-04-03 14:30 | 215 | 215
2019-04-03 15:00 | 226 | 225
2019-04-03 15:30 | 227 | 227
2019-04-03 16:00 | 235 | 234
2019-04-03 16:30 | 240 | 240
2019-04-03 17:00 | 251 | 251
2019-04-03 17:30 | 253 | 253
2019-04-03 18:00 | 257 | 256
2019-04-03 18:30 | 260 | 260
2019-04-03 19:00 | 260 | 260
2019-04-03 19:30 | 252 | 252
2019-04-03 20:00 | 247 | 247
2019-04-03 20:30 | 244 | 244
2019-04-03 21:00 | 230 | 230
2019-04-03 21:30 | 218 | 218
2019-04-03 22:00 | 208 | 208
2019-04-03 22:30 | 203 | 203
2019-04-03 23:00 | 199 | 199
2019-04-03 23:30 | 186 | 186
2019-04-04 | 171 | 171
2019-04-04 00:30 | 158 | 158
2019-04-04 01:00 | 151 | 151
2019-04-04 01:30 | 146 | 146
2019-04-04 02:00 | 142 | 141
2019-04-04 02:30 | 139 | 139
2019-04-04 03:00 | 139 | 138
2019-04-04 03:30 | 139 | 138
2019-04-04 04:00 | 141 | 140
2019-04-04 04:30 | 146 | 145
2019-04-04 05:00 | 152 | 151
2019-04-04 05:30 | 164 | 164
2019-04-04 06:00 | 175 | 175
2019-04-04 06:30 | 192 | 192
2019-04-04 07:00 | 205 | 204
2019-04-04 07:30 | 208 | 208
2019-04-04 08:00 | 205 | 205
2019-04-04 08:30 | 197 | 197
2019-04-04 09:00 | 195 | 194
2019-04-04 09:30 | 192 | 192
2019-04-04 10:00 | 184 | 183
2019-04-04 10:30 | 179 | 178
2019-04-04 11:00 | 176 | 175
2019-04-04 11:30 | 173 | 173
2019-04-04 12:00 | 175 | 175
2019-04-04 12:30 | 179 | 178
2019-04-04 13:00 | 186 | 185
2019-04-04 13:30 | 188 | 188
2019-04-04 14:00 | 193 | 193
2019-04-04 14:30 | 196 | 196
2019-04-04 15:00 | 203 | 203
2019-04-04 15:30 | 218 | 218
2019-04-04 16:00 | 229 | 229
2019-04-04 16:30 | 239 | 239
2019-04-04 17:00 | 250 | 250
2019-04-04 17:30 | 253 | 253
2019-04-04 18:00 | 256 | 256
2019-04-04 18:30 | 262 | 261
2019-04-04 19:00 | 263 | 263
2019-04-04 19:30 | 254 | 254
2019-04-04 20:00 | 249 | 248
2019-04-04 20:30 | 246 | 242
2019-04-04 21:00 | 235 | 231
2019-04-04 21:30 | 221 | 218
2019-04-04 22:00 | 209 | 208
2019-04-04 22:30 | 205 | 203
2019-04-04 23:00 | 200 | 199
2019-04-04 23:30 | 186 | 185
2019-04-05 | 171 | 171
2019-04-05 00:30 | 160 | 160
2019-04-05 01:00 | 154 | 154
2019-04-05 01:30 | 147 | 147
2019-04-05 02:00 | 144 | 144
2019-04-05 02:30 | 142 | 142
2019-04-05 03:00 | 140 | 140
2019-04-05 03:30 | 140 | 140
2019-04-05 04:00 | 141 | 141
2019-04-05 04:30 | 146 | 146
2019-04-05 05:00 | 151 | 151
2019-04-05 05:30 | 163 | 163
2019-04-05 06:00 | 176 | 175
2019-04-05 06:30 | 193 | 192
2019-04-05 07:00 | 207 | 205
2019-04-05 07:30 | 211 | 210
2019-04-05 08:00 | 206 | 205
2019-04-05 08:30 | 198 | 197
2019-04-05 09:00 | 190 | 189
2019-04-05 09:30 | 183 | 181
2019-04-05 10:00 | 179 | 177
2019-04-05 10:30 | 177 | 175
2019-04-05 11:00 | 175 | 173
2019-04-05 11:30 | 174 | 171
2019-04-05 12:00 | 175 | 173
2019-04-05 12:30 | 172 | 170
2019-04-05 13:00 | 172 | 170
2019-04-05 13:30 | 178 | 176
2019-04-05 14:00 | 183 | 180
2019-04-05 14:30 | 194 | 191
2019-04-05 15:00 | 209 | 205
2019-04-05 15:30 | 217 | 214
2019-04-05 16:00 | 227 | 226
2019-04-05 16:30 | 236 | 236
2019-04-05 17:00 | 241 | 241
2019-04-05 17:30 | 243 | 242
2019-04-05 18:00 | 244 | 244
2019-04-05 18:30 | 247 | 246
2019-04-05 19:00 | 249 | 248
2019-04-05 19:30 | 241 | 241
2019-04-05 20:00 | 237 | 237
2019-04-05 20:30 | 234 | 234
2019-04-05 21:00 | 220 | 219
2019-04-05 21:30 | 211 | 211
2019-04-05 22:00 | 205 | 204
2019-04-05 22:30 | 205 | 205
2019-04-05 23:00 | 202 | 201
2019-04-05 23:30 | 189 | 189
2019-04-06 | 175 | 175
2019-04-06 00:30 | 163 | 163
2019-04-06 01:00 | 156 | 156
2019-04-06 01:30 | 152 | 151
2019-04-06 02:00 | 147 | 147
2019-04-06 02:30 | 146 | 146
2019-04-06 03:00 | 144 | 143
2019-04-06 03:30 | 143 | 142
2019-04-06 04:00 | 141 | 141
2019-04-06 04:30 | 142 | 142
2019-04-06 05:00 | 143 | 143
2019-04-06 05:30 | 147 | 147
2019-04-06 06:00 | 151 | 151
2019-04-06 06:30 | 159 | 159
2019-04-06 07:00 | 161 | 161
2019-04-06 07:30 | 163 | 162
2019-04-06 08:00 | 163 | 163
2019-04-06 08:30 | 162 | 162
2019-04-06 09:00 | 159 | 159
2019-04-06 09:30 | 156 | 156
2019-04-06 10:00 | 153 | 152
2019-04-06 10:30 | 151 | 151
2019-04-06 11:00 | 150 | 150
2019-04-06 11:30 | 149 | 149
2019-04-06 12:00 | 149 | 149
2019-04-06 12:30 | 148 | 148
2019-04-06 13:00 | 147 | 147
2019-04-06 13:30 | 153 | 153
2019-04-06 14:00 | 158 | 158
2019-04-06 14:30 | 166 | 166
2019-04-06 15:00 | 173 | 173
2019-04-06 15:30 | 181 | 181
2019-04-06 16:00 | 193 | 193
2019-04-06 16:30 | 205 | 204
2019-04-06 17:00 | 217 | 217
2019-04-06 17:30 | 223 | 223
2019-04-06 18:00 | 226 | 226
2019-04-06 18:30 | 235 | 234
2019-04-06 19:00 | 235 | 234
2019-04-06 19:30 | 228 | 227
2019-04-06 20:00 | 223 | 223
2019-04-06 20:30 | 218 | 218
2019-04-06 21:00 | 209 | 209
2019-04-06 21:30 | 202 | 202
2019-04-06 22:00 | 196 | 196
2019-04-06 22:30 | 194 | 194
2019-04-06 23:00 | 193 | 193
2019-04-06 23:30 | 184 | 184
2019-04-07 | 171 | 171
2019-04-07 00:30 | 159 | 158
2019-04-07 01:00 | 152 | 152
2019-04-07 01:30 | 147 | 147
2019-04-07 02:00 | 143 | 142
2019-04-07 02:30 | 141 | 141
2019-04-07 03:00 | 139 | 139
2019-04-07 03:30 | 137 | 137
2019-04-07 04:00 | 137 | 137
2019-04-07 04:30 | 137 | 137
2019-04-07 05:00 | 138 | 138
2019-04-07 05:30 | 140 | 140
2019-04-07 06:00 | 143 | 143
2019-04-07 06:30 | 145 | 145
2019-04-07 07:00 | 146 | 146
2019-04-07 07:30 | 148 | 148
2019-04-07 08:00 | 146 | 146
2019-04-07 08:30 | 145 | 145
2019-04-07 09:00 | 142 | 142
2019-04-07 09:30 | 139 | 139
2019-04-07 10:00 | 138 | 138
2019-04-07 10:30 | 138 | 138
2019-04-07 11:00 | 137 | 136
2019-04-07 11:30 | 138 | 137
2019-04-07 12:00 | 139 | 138
2019-04-07 12:30 | 142 | 141
2019-04-07 13:00 | 148 | 148
2019-04-07 13:30 | 157 | 156
2019-04-07 14:00 | 162 | 161
2019-04-07 14:30 | 169 | 168
2019-04-07 15:00 | 177 | 176
2019-04-07 15:30 | 189 | 188
2019-04-07 16:00 | 201 | 200
2019-04-07 16:30 | 212 | 212
2019-04-07 17:00 | 224 | 223
2019-04-07 17:30 | 231 | 230
2019-04-07 18:00 | 237 | 236
2019-04-07 18:30 | 248 | 248
2019-04-07 19:00 | 247 | 247
2019-04-07 19:30 | 237 | 237
2019-04-07 20:00 | 231 | 231
2019-04-07 20:30 | 224 | 224
2019-04-07 21:00 | 213 | 212
2019-04-07 21:30 | 206 | 206
2019-04-07 22:00 | 199 | 199
2019-04-07 22:30 | 197 | 196
2019-04-07 23:00 | 193 | 193
2019-04-07 23:30 | 182 | 182
2019-04-08 | 168 | 168
2019-04-08 00:30 | 157 | 156
2019-04-08 01:00 | 150 | 150
2019-04-08 01:30 | 146 | 146
2019-04-08 02:00 | 143 | 143
2019-04-08 02:30 | 141 | 141
2019-04-08 03:00 | 140 | 140
2019-04-08 03:30 | 141 | 140
2019-04-08 04:00 | 141 | 140
2019-04-08 04:30 | 145 | 145
2019-04-08 05:00 | 150 | 150
2019-04-08 05:30 | 162 | 162
2019-04-08 06:00 | 172 | 172
2019-04-08 06:30 | 188 | 188
2019-04-08 07:00 | 199 | 198
2019-04-08 07:30 | 205 | 204
2019-04-08 08:00 | 203 | 203
2019-04-08 08:30 | 201 | 201
2019-04-08 09:00 | 204 | 204
2019-04-08 09:30 | 210 | 209
2019-04-08 10:00 | 207 | 206
2019-04-08 10:30 | 206 | 206
2019-04-08 11:00 | 198 | 198
2019-04-08 11:30 | 190 | 190
2019-04-08 12:00 | 189 | 189
2019-04-08 12:30 | 191 | 191
2019-04-08 13:00 | 196 | 196
2019-04-08 13:30 | 204 | 203
2019-04-08 14:00 | 212 | 211
2019-04-08 14:30 | 223 | 223
2019-04-08 15:00 | 235 | 235
2019-04-08 15:30 | 247 | 247
2019-04-08 16:00 | 259 | 259
2019-04-08 16:30 | 269 | 269
2019-04-08 17:00 | 279 | 279
2019-04-08 17:30 | 280 | 280
2019-04-08 18:00 | 279 | 279
2019-04-08 18:30 | 284 | 283
2019-04-08 19:00 | 281 | 281
2019-04-08 19:30 | 269 | 269
2019-04-08 20:00 | 263 | 262
2019-04-08 20:30 | 256 | 256
2019-04-08 21:00 | 243 | 243
2019-04-08 21:30 | 232 | 232
2019-04-08 22:00 | 225 | 225
2019-04-08 22:30 | 219 | 219
2019-04-08 23:00 | 214 | 214
2019-04-08 23:30 | 196 | 195
2019-04-09 | 181 | 180
2019-04-09 00:30 | 168 | 167
2019-04-09 01:00 | 161 | 160
2019-04-09 01:30 | 156 | 155
2019-04-09 02:00 | 151 | 151
2019-04-09 02:30 | 150 | 150
2019-04-09 03:00 | 148 | 148
2019-04-09 03:30 | 149 | 148
2019-04-09 04:00 | 149 | 149
2019-04-09 04:30 | 152 | 152
2019-04-09 05:00 | 157 | 157
2019-04-09 05:30 | 169 | 168
2019-04-09 06:00 | 179 | 178
2019-04-09 06:30 | 197 | 194
2019-04-09 07:00 | 205 | 203
2019-04-09 07:30 | 210 | 209
2019-04-09 08:00 | 207 | 206
2019-04-09 08:30 | 207 | 205
2019-04-09 09:00 | 204 | 203
2019-04-09 09:30 | 202 | 202
2019-04-09 10:00 | 202 | 202
2019-04-09 10:30 | 196 | 196
2019-04-09 11:00 | 198 | 197
2019-04-09 11:30 | 192 | 191
2019-04-09 12:00 | 198 | 197
2019-04-09 12:30 | 200 | 199
2019-04-09 13:00 | 207 | 205
2019-04-09 13:30 | 215 | 213
2019-04-09 14:00 | 230 | 229
2019-04-09 14:30 | 239 | 239
2019-04-09 15:00 | 242 | 242
2019-04-09 15:30 | 258 | 257
2019-04-09 16:00 | 266 | 266
2019-04-09 16:30 | 272 | 272
2019-04-09 17:00 | 278 | 278
2019-04-09 17:30 | 280 | 280
2019-04-09 18:00 | 283 | 283
2019-04-09 18:30 | 284 | 284
2019-04-09 19:00 | 282 | 282
2019-04-09 19:30 | 273 | 272
2019-04-09 20:00 | 268 | 267
2019-04-09 20:30 | 261 | 261
2019-04-09 21:00 | 249 | 248
2019-04-09 21:30 | 237 | 237
2019-04-09 22:00 | 228 | 227
2019-04-09 22:30 | 223 | 223
2019-04-09 23:00 | 217 | 217
2019-04-09 23:30 | 202 | 201
2019-04-10 | 187 | 186
2019-04-10 00:30 | 173 | 173
2019-04-10 01:00 | 165 | 165
2019-04-10 01:30 | 160 | 159
2019-04-10 02:00 | 156 | 156
2019-04-10 02:30 | 155 | 154
2019-04-10 03:00 | 153 | 153
2019-04-10 03:30 | 153 | 152
2019-04-10 04:00 | 153 | 152
2019-04-10 04:30 | 156 | 156
2019-04-10 05:00 | 162 | 162
2019-04-10 05:30 | 173 | 173
2019-04-10 06:00 | 184 | 183
2019-04-10 06:30 | 200 | 198
2019-04-10 07:00 | 209 | 209
2019-04-10 07:30 | 216 | 216
2019-04-10 08:00 | 218 | 218
2019-04-10 08:30 | 218 | 218
2019-04-10 09:00 | 212 | 212
2019-04-10 09:30 | 212 | 212
2019-04-10 10:00 | 212 | 212
2019-04-10 10:30 | 215 | 215
2019-04-10 11:00 | 211 | 211
2019-04-10 11:30 | 207 | 207
2019-04-10 12:00 | 206 | 206
2019-04-10 12:30 | 207 | 207
2019-04-10 13:00 | 209 | 209
2019-04-10 13:30 | 216 | 216
2019-04-10 14:00 | 217 | 217
2019-04-10 14:30 | 223 | 223
2019-04-10 15:00 | 235 | 235
2019-04-10 15:30 | 237 | 237
2019-04-10 16:00 | 242 | 242
2019-04-10 16:30 | 251 | 251
2019-04-10 17:00 | 259 | 259
2019-04-10 17:30 | 264 | 264
2019-04-10 18:00 | 269 | 269
2019-04-10 18:30 | 269 | 269
2019-04-10 19:00 | 267 | 267
2019-04-10 19:30 | 258 | 258
2019-04-10 20:00 | 253 | 253
2019-04-10 20:30 | 249 | 249
2019-04-10 21:00 | 238 | 238
2019-04-10 21:30 | 228 | 228
2019-04-10 22:00 | 219 | 219
2019-04-10 22:30 | 214 | 214
2019-04-10 23:00 | 211 | 211
2019-04-10 23:30 | 197 | 197
2019-04-11 | 182 | 181
2019-04-11 00:30 | 167 | 167
2019-04-11 01:00 | 159 | 158
2019-04-11 01:30 | 152 | 151
2019-04-11 02:00 | 147 | 147
2019-04-11 02:30 | 144 | 144
2019-04-11 03:00 | 143 | 143
2019-04-11 03:30 | 143 | 143
2019-04-11 04:00 | 144 | 144
2019-04-11 04:30 | 147 | 147
2019-04-11 05:00 | 153 | 153
2019-04-11 05:30 | 164 | 164
2019-04-11 06:00 | 175 | 175
2019-04-11 06:30 | 190 | 189
2019-04-11 07:00 | 201 | 199
2019-04-11 07:30 | 207 | 207
2019-04-11 08:00 | 203 | 203
2019-04-11 08:30 | 199 | 199
2019-04-11 09:00 | 197 | 197
2019-04-11 09:30 | 195 | 195
2019-04-11 10:00 | 207 | 207
2019-04-11 10:30 | 207 | 207
2019-04-11 11:00 | 195 | 195
2019-04-11 11:30 | 182 | 182
2019-04-11 12:00 | 178 | 177
2019-04-11 12:30 | 180 | 180
2019-04-11 13:00 | 188 | 188
2019-04-11 13:30 | 196 | 196
2019-04-11 14:00 | 197 | 197
2019-04-11 14:30 | 198 | 198
2019-04-11 15:00 | 207 | 207
2019-04-11 15:30 | 217 | 217
2019-04-11 16:00 | 222 | 222
2019-04-11 16:30 | 231 | 231
2019-04-11 17:00 | 245 | 245
2019-04-11 17:30 | 249 | 249
2019-04-11 18:00 | 256 | 256
2019-04-11 18:30 | 259 | 259
2019-04-11 19:00 | 258 | 258
2019-04-11 19:30 | 250 | 250
2019-04-11 20:00 | 247 | 247
2019-04-11 20:30 | 243 | 243
2019-04-11 21:00 | 232 | 232
2019-04-11 21:30 | 221 | 220
2019-04-11 22:00 | 210 | 210
2019-04-11 22:30 | 205 | 204
2019-04-11 23:00 | 202 | 201
2019-04-11 23:30 | 191 | 191
2019-04-12 | 176 | 176
2019-04-12 00:30 | 162 | 162
2019-04-12 01:00 | 153 | 153
2019-04-12 01:30 | 147 | 146
2019-04-12 02:00 | 144 | 144
2019-04-12 02:30 | 143 | 143
2019-04-12 03:00 | 140 | 140
2019-04-12 03:30 | 140 | 140
2019-04-12 04:00 | 140 | 140
2019-04-12 04:30 | 145 | 145
2019-04-12 05:00 | 149 | 149
2019-04-12 05:30 | 160 | 160
2019-04-12 06:00 | 170 | 170
2019-04-12 06:30 | 184 | 183
2019-04-12 07:00 | 194 | 193
2019-04-12 07:30 | 199 | 198
2019-04-12 08:00 | 201 | 201
2019-04-12 08:30 | 198 | 198
2019-04-12 09:00 | 190 | 190
2019-04-12 09:30 | 186 | 186
2019-04-12 10:00 | 191 | 191
2019-04-12 10:30 | 201 | 201
2019-04-12 11:00 | 202 | 201
2019-04-12 11:30 | 203 | 203
2019-04-12 12:00 | 203 | 203
2019-04-12 12:30 | 193 | 193
2019-04-12 13:00 | 198 | 198
2019-04-12 13:30 | 201 | 201
2019-04-12 14:00 | 207 | 207
2019-04-12 14:30 | 216 | 214
2019-04-12 15:00 | 211 | 210
2019-04-12 15:30 | 210 | 209
2019-04-12 16:00 | 216 | 215
2019-04-12 16:30 | 224 | 223
2019-04-12 17:00 | 235 | 234
2019-04-12 17:30 | 238 | 238
2019-04-12 18:00 | 241 | 240
2019-04-12 18:30 | 241 | 241
2019-04-12 19:00 | 242 | 241
2019-04-12 19:30 | 235 | 235
2019-04-12 20:00 | 231 | 230
2019-04-12 20:30 | 226 | 226
2019-04-12 21:00 | 218 | 217
2019-04-12 21:30 | 207 | 207
2019-04-12 22:00 | 200 | 200
2019-04-12 22:30 | 198 | 198
2019-04-12 23:00 | 196 | 196
2019-04-12 23:30 | 185 | 185
2019-04-13 | 172 | 172
2019-04-13 00:30 | 157 | 157
2019-04-13 01:00 | 150 | 150
2019-04-13 01:30 | 144 | 144
2019-04-13 02:00 | 139 | 139
2019-04-13 02:30 | 136 | 136
2019-04-13 03:00 | 137 | 137
2019-04-13 03:30 | 135 | 135
2019-04-13 04:00 | 136 | 136
2019-04-13 04:30 | 134 | 134
2019-04-13 05:00 | 135 | 135
2019-04-13 05:30 | 140 | 140
2019-04-13 06:00 | 145 | 145
2019-04-13 06:30 | 149 | 149
2019-04-13 07:00 | 153 | 153
2019-04-13 07:30 | 155 | 155
2019-04-13 08:00 | 155 | 155
2019-04-13 08:30 | 152 | 152
2019-04-13 09:00 | 150 | 149
2019-04-13 09:30 | 147 | 147
2019-04-13 10:00 | 147 | 146
2019-04-13 10:30 | 148 | 146
2019-04-13 11:00 | 146 | 145
2019-04-13 11:30 | 144 | 142
2019-04-13 12:00 | 135 | 134
2019-04-13 12:30 | 135 | 133
2019-04-13 13:00 | 132 | 131
2019-04-13 13:30 | 134 | 133
2019-04-13 14:00 | 142 | 141
2019-04-13 14:30 | 150 | 149
2019-04-13 15:00 | 157 | 155
2019-04-13 15:30 | 167 | 166
2019-04-13 16:00 | 176 | 175
2019-04-13 16:30 | 188 | 186
2019-04-13 17:00 | 199 | 197
2019-04-13 17:30 | 206 | 204
2019-04-13 18:00 | 215 | 213
2019-04-13 18:30 | 222 | 219
2019-04-13 19:00 | 221 | 218
2019-04-13 19:30 | 213 | 211
2019-04-13 20:00 | 211 | 209
2019-04-13 20:30 | 207 | 205
2019-04-13 21:00 | 198 | 197
2019-04-13 21:30 | 192 | 191
2019-04-13 22:00 | 188 | 187
2019-04-13 22:30 | 186 | 185
2019-04-13 23:00 | 185 | 184
2019-04-13 23:30 | 176 | 176
2019-04-14 | 162 | 162
2019-04-14 00:30 | 151 | 151
2019-04-14 01:00 | 145 | 144
2019-04-14 01:30 | 141 | 140
2019-04-14 02:00 | 138 | 137
2019-04-14 02:30 | 134 | 133
2019-04-14 03:00 | 132 | 131
2019-04-14 03:30 | 131 | 131
2019-04-14 04:00 | 129 | 129
2019-04-14 04:30 | 129 | 129
2019-04-14 05:00 | 130 | 130
2019-04-14 05:30 | 134 | 134
2019-04-14 06:00 | 136 | 136
2019-04-14 06:30 | 139 | 139
2019-04-14 07:00 | 139 | 139
2019-04-14 07:30 | 139 | 138
2019-04-14 08:00 | 139 | 138
2019-04-14 08:30 | 142 | 141
2019-04-14 09:00 | 144 | 143
2019-04-14 09:30 | 146 | 145
2019-04-14 10:00 | 139 | 138
2019-04-14 10:30 | 144 | 144
2019-04-14 11:00 | 147 | 146
2019-04-14 11:30 | 141 | 140
2019-04-14 12:00 | 143 | 142
2019-04-14 12:30 | 141 | 141
2019-04-14 13:00 | 138 | 137
2019-04-14 13:30 | 139 | 138
2019-04-14 14:00 | 145 | 143
2019-04-14 14:30 | 153 | 152
2019-04-14 15:00 | 156 | 155
2019-04-14 15:30 | 169 | 168
2019-04-14 16:00 | 183 | 183
2019-04-14 16:30 | 191 | 191
2019-04-14 17:00 | 202 | 202
2019-04-14 17:30 | 212 | 212
2019-04-14 18:00 | 223 | 222
2019-04-14 18:30 | 228 | 227
2019-04-14 19:00 | 225 | 225
2019-04-14 19:30 | 217 | 217
2019-04-14 20:00 | 214 | 214
2019-04-14 20:30 | 211 | 211
2019-04-14 21:00 | 201 | 201
2019-04-14 21:30 | 196 | 196
2019-04-14 22:00 | 190 | 190
2019-04-14 22:30 | 187 | 187
2019-04-14 23:00 | 185 | 185
2019-04-14 23:30 | 174 | 174
2019-04-15 | 160 | 160
2019-04-15 00:30 | 149 | 149
2019-04-15 01:00 | 142 | 142
2019-04-15 01:30 | 139 | 139
2019-04-15 02:00 | 137 | 136
2019-04-15 02:30 | 137 | 136
2019-04-15 03:00 | 135 | 135
2019-04-15 03:30 | 136 | 135
2019-04-15 04:00 | 137 | 136
2019-04-15 04:30 | 138 | 137
2019-04-15 05:00 | 143 | 142
2019-04-15 05:30 | 154 | 154
2019-04-15 06:00 | 167 | 167
2019-04-15 06:30 | 182 | 182
2019-04-15 07:00 | 193 | 193
2019-04-15 07:30 | 201 | 201
2019-04-15 08:00 | 204 | 203
2019-04-15 08:30 | 199 | 199
2019-04-15 09:00 | 188 | 187
2019-04-15 09:30 | 182 | 182
2019-04-15 10:00 | 183 | 182
2019-04-15 10:30 | 179 | 179
2019-04-15 11:00 | 186 | 185
2019-04-15 11:30 | 190 | 189
2019-04-15 12:00 | 196 | 195
2019-04-15 12:30 | 197 | 196
2019-04-15 13:00 | 198 | 197
2019-04-15 13:30 | 199 | 198
2019-04-15 14:00 | 203 | 202
2019-04-15 14:30 | 200 | 198
2019-04-15 15:00 | 209 | 208
2019-04-15 15:30 | 221 | 220
2019-04-15 16:00 | 230 | 229
2019-04-15 16:30 | 235 | 234
2019-04-15 17:00 | 242 | 241
2019-04-15 17:30 | 247 | 246
2019-04-15 18:00 | 254 | 252
2019-04-15 18:30 | 256 | 255
2019-04-15 19:00 | 252 | 251
2019-04-15 19:30 | 241 | 240
2019-04-15 20:00 | 237 | 236
2019-04-15 20:30 | 232 | 231
2019-04-15 21:00 | 221 | 221
2019-04-15 21:30 | 210 | 210
2019-04-15 22:00 | 202 | 202
2019-04-15 22:30 | 199 | 199
2019-04-15 23:00 | 195 | 195
2019-04-15 23:30 | 185 | 185
2019-04-16 | 172 | 172
2019-04-16 00:30 | 158 | 157
2019-04-16 01:00 | 150 | 148
2019-04-16 01:30 | 146 | 144
2019-04-16 02:00 | 143 | 141
2019-04-16 02:30 | 141 | 139
2019-04-16 03:00 | 141 | 139
2019-04-16 03:30 | 141 | 138
2019-04-16 04:00 | 141 | 138
2019-04-16 04:30 | 144 | 142
2019-04-16 05:00 | 150 | 148
2019-04-16 05:30 | 160 | 160
2019-04-16 06:00 | 170 | 170
2019-04-16 06:30 | 183 | 183
2019-04-16 07:00 | 194 | 194
2019-04-16 07:30 | 196 | 195
2019-04-16 08:00 | 196 | 195
2019-04-16 08:30 | 195 | 194
2019-04-16 09:00 | 188 | 187
2019-04-16 09:30 | 183 | 182
2019-04-16 10:00 | 182 | 180
2019-04-16 10:30 | 188 | 186
2019-04-16 11:00 | 188 | 186
2019-04-16 11:30 | 193 | 191
2019-04-16 12:00 | 189 | 187
2019-04-16 12:30 | 191 | 189
2019-04-16 13:00 | 186 | 184
2019-04-16 13:30 | 186 | 184
2019-04-16 14:00 | 200 | 198
2019-04-16 14:30 | 204 | 203
2019-04-16 15:00 | 214 | 214
2019-04-16 15:30 | 218 | 218
2019-04-16 16:00 | 218 | 218
2019-04-16 16:30 | 231 | 231
2019-04-16 17:00 | 241 | 241
2019-04-16 17:30 | 246 | 246
2019-04-16 18:00 | 253 | 253
2019-04-16 18:30 | 256 | 256
2019-04-16 19:00 | 253 | 253
2019-04-16 19:30 | 245 | 245
2019-04-16 20:00 | 242 | 242
2019-04-16 20:30 | 239 | 239
2019-04-16 21:00 | 228 | 228
2019-04-16 21:30 | 218 | 218
2019-04-16 22:00 | 210 | 210
2019-04-16 22:30 | 207 | 206
2019-04-16 23:00 | 205 | 204
2019-04-16 23:30 | 191 | 191
2019-04-17 | 175 | 175
2019-04-17 00:30 | 165 | 165
2019-04-17 01:00 | 158 | 157
2019-04-17 01:30 | 150 | 150
2019-04-17 02:00 | 145 | 145
2019-04-17 02:30 | 144 | 144
2019-04-17 03:00 | 142 | 142
2019-04-17 03:30 | 143 | 143
2019-04-17 04:00 | 143 | 143
2019-04-17 04:30 | 146 | 146
2019-04-17 05:00 | 152 | 152
2019-04-17 05:30 | 164 | 163
2019-04-17 06:00 | 174 | 174
2019-04-17 06:30 | 190 | 189
2019-04-17 07:00 | 200 | 198
2019-04-17 07:30 | 203 | 202
2019-04-17 08:00 | 199 | 198
2019-04-17 08:30 | 195 | 194
2019-04-17 09:00 | 194 | 192
2019-04-17 09:30 | 188 | 186
2019-04-17 10:00 | 193 | 190
2019-04-17 10:30 | 202 | 199
2019-04-17 11:00 | 197 | 197
2019-04-17 11:30 | 196 | 196
2019-04-17 12:00 | 196 | 196
2019-04-17 12:30 | 192 | 192
2019-04-17 13:00 | 190 | 190
2019-04-17 13:30 | 195 | 194
2019-04-17 14:00 | 192 | 192
2019-04-17 14:30 | 203 | 203
2019-04-17 15:00 | 209 | 209
2019-04-17 15:30 | 217 | 216
2019-04-17 16:00 | 226 | 226
2019-04-17 16:30 | 235 | 235
2019-04-17 17:00 | 247 | 247
2019-04-17 17:30 | 252 | 252
2019-04-17 18:00 | 257 | 256
2019-04-17 18:30 | 259 | 258
2019-04-17 19:00 | 257 | 257
2019-04-17 19:30 | 248 | 248
2019-04-17 20:00 | 243 | 243
2019-04-17 20:30 | 239 | 239
2019-04-17 21:00 | 229 | 228
2019-04-17 21:30 | 218 | 218
2019-04-17 22:00 | 208 | 207
2019-04-17 22:30 | 206 | 205
2019-04-17 23:00 | 202 | 201
2019-04-17 23:30 | 189 | 189
2019-04-18 | 175 | 175
2019-04-18 00:30 | 161 | 161
2019-04-18 01:00 | 152 | 152
2019-04-18 01:30 | 148 | 148
2019-04-18 02:00 | 145 | 145
2019-04-18 02:30 | 143 | 142
2019-04-18 03:00 | 141 | 141
2019-04-18 03:30 | 141 | 141
2019-04-18 04:00 | 142 | 142
2019-04-18 04:30 | 146 | 145
2019-04-18 05:00 | 150 | 150
2019-04-18 05:30 | 162 | 161
2019-04-18 06:00 | 173 | 172
2019-04-18 06:30 | 187 | 187
2019-04-18 07:00 | 201 | 200
2019-04-18 07:30 | 208 | 208
2019-04-18 08:00 | 208 | 208
2019-04-18 08:30 | 205 | 205
2019-04-18 09:00 | 197 | 197
2019-04-18 09:30 | 189 | 189
2019-04-18 10:00 | 187 | 187
2019-04-18 10:30 | 191 | 191
2019-04-18 11:00 | 196 | 196
2019-04-18 11:30 | 192 | 192
2019-04-18 12:00 | 190 | 190
2019-04-18 12:30 | 192 | 192
2019-04-18 13:00 | 192 | 192
2019-04-18 13:30 | 196 | 196
2019-04-18 14:00 | 201 | 201
2019-04-18 14:30 | 208 | 208
2019-04-18 15:00 | 216 | 216
2019-04-18 15:30 | 218 | 218
2019-04-18 16:00 | 226 | 226
2019-04-18 16:30 | 234 | 234
2019-04-18 17:00 | 244 | 244
2019-04-18 17:30 | 246 | 246
2019-04-18 18:00 | 250 | 250
2019-04-18 18:30 | 251 | 251
2019-04-18 19:00 | 250 | 250
2019-04-18 19:30 | 244 | 244
2019-04-18 20:00 | 242 | 242
2019-04-18 20:30 | 239 | 239
2019-04-18 21:00 | 227 | 227
2019-04-18 21:30 | 216 | 215
2019-04-18 22:00 | 206 | 205
2019-04-18 22:30 | 204 | 204
2019-04-18 23:00 | 201 | 200
2019-04-18 23:30 | 188 | 188
2019-04-19 | 174 | 174
2019-04-19 00:30 | 160 | 160
2019-04-19 01:00 | 152 | 152
2019-04-19 01:30 | 147 | 147
2019-04-19 02:00 | 143 | 142
2019-04-19 02:30 | 139 | 138
2019-04-19 03:00 | 137 | 137
2019-04-19 03:30 | 136 | 136
2019-04-19 04:00 | 136 | 135
2019-04-19 04:30 | 135 | 134
2019-04-19 05:00 | 135 | 134
2019-04-19 05:30 | 137 | 136
2019-04-19 06:00 | 140 | 139
2019-04-19 06:30 | 145 | 144
2019-04-19 07:00 | 149 | 148
2019-04-19 07:30 | 151 | 150
2019-04-19 08:00 | 151 | 151
2019-04-19 08:30 | 155 | 155
2019-04-19 09:00 | 152 | 152
2019-04-19 09:30 | 149 | 149
2019-04-19 10:00 | 143 | 143
2019-04-19 10:30 | 143 | 143
2019-04-19 11:00 | 139 | 139
2019-04-19 11:30 | 136 | 136
2019-04-19 12:00 | 146 | 146
2019-04-19 12:30 | 149 | 149
2019-04-19 13:00 | 138 | 138
2019-04-19 13:30 | 141 | 141
2019-04-19 14:00 | 151 | 151
2019-04-19 14:30 | 156 | 156
2019-04-19 15:00 | 163 | 163
2019-04-19 15:30 | 173 | 173
2019-04-19 16:00 | 177 | 177
2019-04-19 16:30 | 184 | 183
2019-04-19 17:00 | 197 | 197
2019-04-19 17:30 | 205 | 204
2019-04-19 18:00 | 212 | 211
2019-04-19 18:30 | 216 | 216
2019-04-19 19:00 | 214 | 214
2019-04-19 19:30 | 207 | 206
2019-04-19 20:00 | 206 | 205
2019-04-19 20:30 | 202 | 202
2019-04-19 21:00 | 195 | 195
2019-04-19 21:30 | 189 | 189
2019-04-19 22:00 | 184 | 184
2019-04-19 22:30 | 185 | 185
2019-04-19 23:00 | 185 | 185
2019-04-19 23:30 | 175 | 175
2019-04-20 | 162 | 162
2019-04-20 00:30 | 151 | 151
2019-04-20 01:00 | 144 | 144
2019-04-20 01:30 | 139 | 138
2019-04-20 02:00 | 136 | 135
2019-04-20 02:30 | 134 | 133
2019-04-20 03:00 | 132 | 131
2019-04-20 03:30 | 132 | 131
2019-04-20 04:00 | 132 | 130
2019-04-20 04:30 | 131 | 130
2019-04-20 05:00 | 133 | 132
2019-04-20 05:30 | 136 | 135
2019-04-20 06:00 | 140 | 139
2019-04-20 06:30 | 144 | 143
2019-04-20 07:00 | 148 | 147
2019-04-20 07:30 | 151 | 151
2019-04-20 08:00 | 153 | 153
2019-04-20 08:30 | 156 | 156
2019-04-20 09:00 | 157 | 157
2019-04-20 09:30 | 159 | 159
2019-04-20 10:00 | 166 | 166
2019-04-20 10:30 | 173 | 172
2019-04-20 11:00 | 163 | 163
2019-04-20 11:30 | 155 | 155
2019-04-20 12:00 | 164 | 164
2019-04-20 12:30 | 153 | 153
2019-04-20 13:00 | 153 | 153
2019-04-20 13:30 | 153 | 153
2019-04-20 14:00 | 161 | 161
2019-04-20 14:30 | 164 | 164
2019-04-20 15:00 | 172 | 172
2019-04-20 15:30 | 186 | 186
2019-04-20 16:00 | 188 | 188
2019-04-20 16:30 | 191 | 191
2019-04-20 17:00 | 203 | 203
2019-04-20 17:30 | 211 | 210
2019-04-20 18:00 | 220 | 220
2019-04-20 18:30 | 223 | 222
2019-04-20 19:00 | 220 | 220
2019-04-20 19:30 | 215 | 214
2019-04-20 20:00 | 209 | 209
2019-04-20 20:30 | 206 | 206
2019-04-20 21:00 | 197 | 197
2019-04-20 21:30 | 192 | 192
2019-04-20 22:00 | 187 | 187
2019-04-20 22:30 | 187 | 187
2019-04-20 23:00 | 187 | 187
2019-04-20 23:30 | 177 | 177
2019-04-21 | 163 | 163
2019-04-21 00:30 | 152 | 151
2019-04-21 01:00 | 146 | 145
2019-04-21 01:30 | 142 | 141
2019-04-21 02:00 | 137 | 136
2019-04-21 02:30 | 134 | 134
2019-04-21 03:00 | 132 | 132
2019-04-21 03:30 | 131 | 131
2019-04-21 04:00 | 131 | 131
2019-04-21 04:30 | 131 | 131
2019-04-21 05:00 | 131 | 131
2019-04-21 05:30 | 133 | 133
2019-04-21 06:00 | 135 | 135
2019-04-21 06:30 | 138 | 138
2019-04-21 07:00 | 141 | 141
2019-04-21 07:30 | 141 | 141
2019-04-21 08:00 | 143 | 143
2019-04-21 08:30 | 145 | 145
2019-04-21 09:00 | 148 | 148
2019-04-21 09:30 | 150 | 150
2019-04-21 10:00 | 146 | 146
2019-04-21 10:30 | 151 | 151
2019-04-21 11:00 | 151 | 151
2019-04-21 11:30 | 135 | 135
2019-04-21 12:00 | 132 | 132
2019-04-21 12:30 | 132 | 132
2019-04-21 13:00 | 135 | 135
2019-04-21 13:30 | 131 | 131
2019-04-21 14:00 | 133 | 133
2019-04-21 14:30 | 139 | 139
2019-04-21 15:00 | 142 | 142
2019-04-21 15:30 | 154 | 154
2019-04-21 16:00 | 173 | 173
2019-04-21 16:30 | 189 | 189
2019-04-21 17:00 | 201 | 201
2019-04-21 17:30 | 206 | 205
2019-04-21 18:00 | 211 | 211
2019-04-21 18:30 | 211 | 211
2019-04-21 19:00 | 209 | 209
2019-04-21 19:30 | 204 | 204
2019-04-21 20:00 | 203 | 203
2019-04-21 20:30 | 202 | 201
2019-04-21 21:00 | 194 | 194
2019-04-21 21:30 | 189 | 189
2019-04-21 22:00 | 184 | 184
2019-04-21 22:30 | 184 | 184
2019-04-21 23:00 | 184 | 184
2019-04-21 23:30 | 175 | 175
2019-04-22 | 162 | 162
2019-04-22 00:30 | 151 | 151
2019-04-22 01:00 | 144 | 144
2019-04-22 01:30 | 140 | 139
2019-04-22 02:00 | 136 | 135
2019-04-22 02:30 | 134 | 133
2019-04-22 03:00 | 133 | 132
2019-04-22 03:30 | 133 | 132
2019-04-22 04:00 | 133 | 132
2019-04-22 04:30 | 133 | 132
2019-04-22 05:00 | 133 | 132
2019-04-22 05:30 | 136 | 136
2019-04-22 06:00 | 140 | 139
2019-04-22 06:30 | 143 | 143
2019-04-22 07:00 | 146 | 145
2019-04-22 07:30 | 150 | 150
2019-04-22 08:00 | 151 | 151
2019-04-22 08:30 | 156 | 156
2019-04-22 09:00 | 164 | 164
2019-04-22 09:30 | 159 | 159
2019-04-22 10:00 | 151 | 151
2019-04-22 10:30 | 159 | 159
2019-04-22 11:00 | 163 | 163
2019-04-22 11:30 | 156 | 156
2019-04-22 12:00 | 162 | 162
2019-04-22 12:30 | 169 | 169
2019-04-22 13:00 | 168 | 167
2019-04-22 13:30 | 169 | 168
2019-04-22 14:00 | 168 | 168
2019-04-22 14:30 | 173 | 173
2019-04-22 15:00 | 181 | 181
2019-04-22 15:30 | 188 | 187
2019-04-22 16:00 | 195 | 195
2019-04-22 16:30 | 206 | 205
2019-04-22 17:00 | 218 | 217
2019-04-22 17:30 | 228 | 227
2019-04-22 18:00 | 238 | 238
2019-04-22 18:30 | 237 | 237
2019-04-22 19:00 | 233 | 232
2019-04-22 19:30 | 224 | 224
2019-04-22 20:00 | 221 | 221
2019-04-22 20:30 | 219 | 219
2019-04-22 21:00 | 209 | 209
2019-04-22 21:30 | 200 | 200
2019-04-22 22:00 | 193 | 193
2019-04-22 22:30 | 191 | 191
2019-04-22 23:00 | 189 | 189
2019-04-22 23:30 | 179 | 179
2019-04-23 | 165 | 165
2019-04-23 00:30 | 153 | 153
2019-04-23 01:00 | 146 | 145
2019-04-23 01:30 | 141 | 141
2019-04-23 02:00 | 138 | 138
2019-04-23 02:30 | 136 | 136
2019-04-23 03:00 | 135 | 135
2019-04-23 03:30 | 136 | 136
2019-04-23 04:00 | 137 | 136
2019-04-23 04:30 | 140 | 140
2019-04-23 05:00 | 146 | 146
2019-04-23 05:30 | 158 | 158
2019-04-23 06:00 | 169 | 169
2019-04-23 06:30 | 187 | 187
2019-04-23 07:00 | 203 | 202
2019-04-23 07:30 | 213 | 213
2019-04-23 08:00 | 217 | 217
2019-04-23 08:30 | 217 | 216
2019-04-23 09:00 | 214 | 214
2019-04-23 09:30 | 214 | 214
2019-04-23 10:00 | 216 | 216
2019-04-23 10:30 | 208 | 208
2019-04-23 11:00 | 198 | 198
2019-04-23 11:30 | 201 | 201
2019-04-23 12:00 | 201 | 200
2019-04-23 12:30 | 199 | 199
2019-04-23 13:00 | 198 | 197
2019-04-23 13:30 | 199 | 199
2019-04-23 14:00 | 207 | 205
2019-04-23 14:30 | 211 | 209
2019-04-23 15:00 | 220 | 218
2019-04-23 15:30 | 231 | 230
2019-04-23 16:00 | 237 | 235
2019-04-23 16:30 | 245 | 243
2019-04-23 17:00 | 253 | 251
2019-04-23 17:30 | 260 | 259
2019-04-23 18:00 | 266 | 266
2019-04-23 18:30 | 262 | 262
2019-04-23 19:00 | 259 | 259
2019-04-23 19:30 | 251 | 251
2019-04-23 20:00 | 247 | 247
2019-04-23 20:30 | 245 | 244
2019-04-23 21:00 | 230 | 230
2019-04-23 21:30 | 219 | 219
2019-04-23 22:00 | 211 | 211
2019-04-23 22:30 | 206 | 206
2019-04-23 23:00 | 203 | 203
2019-04-23 23:30 | 191 | 191
2019-04-24 | 176 | 176
2019-04-24 00:30 | 163 | 163
2019-04-24 01:00 | 155 | 155
2019-04-24 01:30 | 150 | 150
2019-04-24 02:00 | 146 | 146
2019-04-24 02:30 | 144 | 144
2019-04-24 03:00 | 143 | 142
2019-04-24 03:30 | 143 | 143
2019-04-24 04:00 | 144 | 144
2019-04-24 04:30 | 147 | 146
2019-04-24 05:00 | 152 | 152
2019-04-24 05:30 | 163 | 163
2019-04-24 06:00 | 174 | 174
2019-04-24 06:30 | 191 | 190
2019-04-24 07:00 | 203 | 202
2019-04-24 07:30 | 211 | 211
2019-04-24 08:00 | 208 | 208
2019-04-24 08:30 | 206 | 206
2019-04-24 09:00 | 203 | 203
2019-04-24 09:30 | 196 | 196
2019-04-24 10:00 | 190 | 190
2019-04-24 10:30 | 184 | 184
2019-04-24 11:00 | 181 | 181
2019-04-24 11:30 | 180 | 180
2019-04-24 12:00 | 186 | 186
2019-04-24 12:30 | 184 | 184
2019-04-24 13:00 | 184 | 184
2019-04-24 13:30 | 184 | 184
2019-04-24 14:00 | 191 | 191
2019-04-24 14:30 | 197 | 197
2019-04-24 15:00 | 208 | 208
2019-04-24 15:30 | 225 | 225
2019-04-24 16:00 | 233 | 232
2019-04-24 16:30 | 239 | 237
2019-04-24 17:00 | 248 | 247
2019-04-24 17:30 | 253 | 253
2019-04-24 18:00 | 259 | 258
2019-04-24 18:30 | 256 | 255
2019-04-24 19:00 | 254 | 253
2019-04-24 19:30 | 243 | 243
2019-04-24 20:00 | 240 | 240
2019-04-24 20:30 | 235 | 234
2019-04-24 21:00 | 225 | 224
2019-04-24 21:30 | 216 | 215
2019-04-24 22:00 | 208 | 208
2019-04-24 22:30 | 206 | 205
2019-04-24 23:00 | 203 | 203
2019-04-24 23:30 | 190 | 190
2019-04-25 | 175 | 175
2019-04-25 00:30 | 161 | 161
2019-04-25 01:00 | 153 | 153
2019-04-25 01:30 | 148 | 148
2019-04-25 02:00 | 144 | 143
2019-04-25 02:30 | 141 | 140
2019-04-25 03:00 | 139 | 138
2019-04-25 03:30 | 139 | 139
2019-04-25 04:00 | 138 | 138
2019-04-25 04:30 | 139 | 139
2019-04-25 05:00 | 139 | 139
2019-04-25 05:30 | 142 | 142
2019-04-25 06:00 | 145 | 145
2019-04-25 06:30 | 149 | 149
2019-04-25 07:00 | 151 | 151
2019-04-25 07:30 | 154 | 154
2019-04-25 08:00 | 148 | 148
2019-04-25 08:30 | 147 | 147
2019-04-25 09:00 | 152 | 152
2019-04-25 09:30 | 155 | 155
2019-04-25 10:00 | 157 | 156
2019-04-25 10:30 | 138 | 137
2019-04-25 11:00 | 136 | 135
2019-04-25 11:30 | 143 | 142
2019-04-25 12:00 | 143 | 142
2019-04-25 12:30 | 143 | 142
2019-04-25 13:00 | 144 | 143
2019-04-25 13:30 | 150 | 149
2019-04-25 14:00 | 154 | 152
2019-04-25 14:30 | 157 | 156
2019-04-25 15:00 | 163 | 162
2019-04-25 15:30 | 170 | 169
2019-04-25 16:00 | 180 | 179
2019-04-25 16:30 | 192 | 192
2019-04-25 17:00 | 205 | 204
2019-04-25 17:30 | 216 | 215
2019-04-25 18:00 | 226 | 225
2019-04-25 18:30 | 229 | 228
2019-04-25 19:00 | 228 | 227
2019-04-25 19:30 | 221 | 221
2019-04-25 20:00 | 217 | 217
2019-04-25 20:30 | 214 | 214
2019-04-25 21:00 | 204 | 204
2019-04-25 21:30 | 198 | 198
2019-04-25 22:00 | 191 | 191
2019-04-25 22:30 | 190 | 190
2019-04-25 23:00 | 189 | 189
2019-04-25 23:30 | 178 | 178
2019-04-26 | 165 | 165
2019-04-26 00:30 | 154 | 154
2019-04-26 01:00 | 147 | 147
2019-04-26 01:30 | 142 | 142
2019-04-26 02:00 | 140 | 140
2019-04-26 02:30 | 138 | 138
2019-04-26 03:00 | 138 | 137
2019-04-26 03:30 | 138 | 137
2019-04-26 04:00 | 138 | 137
2019-04-26 04:30 | 140 | 140
2019-04-26 05:00 | 146 | 146
2019-04-26 05:30 | 157 | 156
2019-04-26 06:00 | 167 | 167
2019-04-26 06:30 | 183 | 183
2019-04-26 07:00 | 195 | 195
2019-04-26 07:30 | 201 | 201
2019-04-26 08:00 | 204 | 203
2019-04-26 08:30 | 196 | 196
2019-04-26 09:00 | 194 | 194
2019-04-26 09:30 | 187 | 187
2019-04-26 10:00 | 191 | 191
2019-04-26 10:30 | 196 | 196
2019-04-26 11:00 | 192 | 192
2019-04-26 11:30 | 192 | 192
2019-04-26 12:00 | 188 | 188
2019-04-26 12:30 | 190 | 190
2019-04-26 13:00 | 195 | 195
2019-04-26 13:30 | 191 | 191
2019-04-26 14:00 | 182 | 182
2019-04-26 14:30 | 195 | 195
2019-04-26 15:00 | 210 | 210
2019-04-26 15:30 | 202 | 202
2019-04-26 16:00 | 221 | 221
2019-04-26 16:30 | 232 | 232
2019-04-26 17:00 | 236 | 236
2019-04-26 17:30 | 242 | 242
2019-04-26 18:00 | 248 | 247
2019-04-26 18:30 | 245 | 244
2019-04-26 19:00 | 243 | 242
2019-04-26 19:30 | 235 | 234
2019-04-26 20:00 | 232 | 231
2019-04-26 20:30 | 229 | 228
2019-04-26 21:00 | 219 | 218
2019-04-26 21:30 | 210 | 210
2019-04-26 22:00 | 203 | 203
2019-04-26 22:30 | 201 | 201
2019-04-26 23:00 | 199 | 198
2019-04-26 23:30 | 187 | 187
2019-04-27 | 173 | 173
2019-04-27 00:30 | 160 | 160
2019-04-27 01:00 | 152 | 152
2019-04-27 01:30 | 147 | 147
2019-04-27 02:00 | 141 | 141
2019-04-27 02:30 | 138 | 137
2019-04-27 03:00 | 135 | 135
2019-04-27 03:30 | 133 | 133
2019-04-27 04:00 | 131 | 131
2019-04-27 04:30 | 132 | 132
2019-04-27 05:00 | 133 | 133
2019-04-27 05:30 | 138 | 138
2019-04-27 06:00 | 143 | 142
2019-04-27 06:30 | 148 | 148
2019-04-27 07:00 | 153 | 153
2019-04-27 07:30 | 155 | 155
2019-04-27 08:00 | 154 | 153
2019-04-27 08:30 | 154 | 153
2019-04-27 09:00 | 150 | 149
2019-04-27 09:30 | 146 | 145
2019-04-27 10:00 | 140 | 140
2019-04-27 10:30 | 137 | 137
2019-04-27 11:00 | 139 | 139
2019-04-27 11:30 | 143 | 142
2019-04-27 12:00 | 139 | 139
2019-04-27 12:30 | 140 | 139
2019-04-27 13:00 | 145 | 145
2019-04-27 13:30 | 149 | 149
2019-04-27 14:00 | 153 | 153
2019-04-27 14:30 | 153 | 153
2019-04-27 15:00 | 163 | 162
2019-04-27 15:30 | 174 | 173
2019-04-27 16:00 | 185 | 184
2019-04-27 16:30 | 197 | 196
2019-04-27 17:00 | 208 | 207
2019-04-27 17:30 | 214 | 213
2019-04-27 18:00 | 220 | 220
2019-04-27 18:30 | 221 | 221
2019-04-27 19:00 | 218 | 218
2019-04-27 19:30 | 212 | 212
2019-04-27 20:00 | 209 | 209
2019-04-27 20:30 | 207 | 206
2019-04-27 21:00 | 198 | 197
2019-04-27 21:30 | 191 | 190
2019-04-27 22:00 | 186 | 186
2019-04-27 22:30 | 186 | 186
2019-04-27 23:00 | 185 | 185
2019-04-27 23:30 | 176 | 176
2019-04-28 | 163 | 163
2019-04-28 00:30 | 151 | 151
2019-04-28 01:00 | 144 | 143
2019-04-28 01:30 | 138 | 137
2019-04-28 02:00 | 133 | 133
2019-04-28 02:30 | 131 | 131
2019-04-28 03:00 | 129 | 129
2019-04-28 03:30 | 128 | 128
2019-04-28 04:00 | 128 | 128
2019-04-28 04:30 | 128 | 128
2019-04-28 05:00 | 129 | 129
2019-04-28 05:30 | 131 | 131
2019-04-28 06:00 | 134 | 134
2019-04-28 06:30 | 137 | 137
2019-04-28 07:00 | 138 | 138
2019-04-28 07:30 | 139 | 139
2019-04-28 08:00 | 137 | 137
2019-04-28 08:30 | 136 | 136
2019-04-28 09:00 | 132 | 132
2019-04-28 09:30 | 130 | 130
2019-04-28 10:00 | 127 | 126
2019-04-28 10:30 | 126 | 125
2019-04-28 11:00 | 127 | 126
2019-04-28 11:30 | 128 | 127
2019-04-28 12:00 | 128 | 127
2019-04-28 12:30 | 131 | 130
2019-04-28 13:00 | 133 | 132
2019-04-28 13:30 | 138 | 137
2019-04-28 14:00 | 143 | 141
2019-04-28 14:30 | 150 | 148
2019-04-28 15:00 | 161 | 159
2019-04-28 15:30 | 173 | 171
2019-04-28 16:00 | 187 | 185
2019-04-28 16:30 | 200 | 198
2019-04-28 17:00 | 214 | 212
2019-04-28 17:30 | 223 | 223
2019-04-28 18:00 | 233 | 233
2019-04-28 18:30 | 236 | 236
2019-04-28 19:00 | 231 | 231
2019-04-28 19:30 | 222 | 222
2019-04-28 20:00 | 218 | 218
2019-04-28 20:30 | 214 | 214
2019-04-28 21:00 | 203 | 203
2019-04-28 21:30 | 194 | 194
2019-04-28 22:00 | 186 | 186
2019-04-28 22:30 | 184 | 184
2019-04-28 23:00 | 182 | 182
2019-04-28 23:30 | 171 | 171
2019-04-29 | 159 | 158
2019-04-29 00:30 | 147 | 147
2019-04-29 01:00 | 141 | 141
2019-04-29 01:30 | 137 | 136
2019-04-29 02:00 | 133 | 133
2019-04-29 02:30 | 131 | 131
2019-04-29 03:00 | 130 | 130
2019-04-29 03:30 | 130 | 130
2019-04-29 04:00 | 131 | 131
2019-04-29 04:30 | 135 | 135
2019-04-29 05:00 | 143 | 143
2019-04-29 05:30 | 155 | 154
2019-04-29 06:00 | 169 | 167
2019-04-29 06:30 | 188 | 186
2019-04-29 07:00 | 204 | 203
2019-04-29 07:30 | 212 | 212
2019-04-29 08:00 | 213 | 213
2019-04-29 08:30 | 147 | 147
2019-04-29 09:00 | 142 | 141
2019-04-29 09:30 | 142 | 141
2019-04-29 10:00 | 140 | 140
2019-04-29 10:30 | 134 | 134
2019-04-29 11:00 | 133 | 133
2019-04-29 11:30 | 133 | 133
2019-04-29 12:00 | 130 | 130
2019-04-29 12:30 | 125 | 125
2019-04-29 13:00 | 126 | 126
2019-04-29 13:30 | 128 | 128
2019-04-29 14:00 | 133 | 133
2019-04-29 14:30 | 136 | 135
2019-04-29 15:00 | 140 | 139
2019-04-29 15:30 | 147 | 146
2019-04-29 16:00 | 154 | 154
2019-04-29 16:30 | 162 | 162
2019-04-29 17:00 | 171 | 170
2019-04-29 17:30 | 177 | 176
2019-04-29 18:00 | 184 | 183
2019-04-29 18:30 | 180 | 180
2019-04-29 19:00 | 178 | 177
2019-04-29 19:30 | 172 | 172
2019-04-29 20:00 | 170 | 169
2019-04-29 20:30 | 167 | 167
2019-04-29 21:00 | 159 | 159
2019-04-29 21:30 | 151 | 150
2019-04-29 22:00 | 145 | 144
2019-04-29 22:30 | 142 | 141
2019-04-29 23:00 | 139 | 138
2019-04-29 23:30 | 131 | 130
2019-04-30 | 120 | 120
2019-04-30 00:30 | 111 | 111
2019-04-30 01:00 | 106 | 106
2019-04-30 01:30 | 103 | 103
2019-04-30 02:00 | 100 | 100
2019-04-30 02:30 | 98 | 98
2019-04-30 03:00 | 98 | 97
2019-04-30 03:30 | 98 | 97
2019-04-30 04:00 | 99 | 98
2019-04-30 04:30 | 101 | 101
2019-04-30 05:00 | 106 | 105
2019-04-30 05:30 | 115 | 113
2019-04-30 06:00 | 124 | 122
2019-04-30 06:30 | 137 | 135
2019-04-30 07:00 | 149 | 147
2019-04-30 07:30 | 154 | 153
2019-04-30 08:00 | 152 | 150
2019-04-30 08:30 | 147 | 145
2019-04-30 09:00 | 144 | 142
2019-04-30 09:30 | 138 | 135
2019-04-30 10:00 | 132 | 130
2019-04-30 10:30 | 139 | 137
2019-04-30 11:00 | 144 | 142
2019-04-30 11:30 | 145 | 143
2019-04-30 12:00 | 151 | 148
2019-04-30 12:30 | 150 | 147
2019-04-30 13:00 | 145 | 143
2019-04-30 13:30 | 148 | 145
2019-04-30 14:00 | 153 | 151
2019-04-30 14:30 | 157 | 154
2019-04-30 15:00 | 153 | 151
2019-04-30 15:30 | 157 | 155
2019-04-30 16:00 | 162 | 160
2019-04-30 16:30 | 169 | 167
2019-04-30 17:00 | 175 | 175
2019-04-30 17:30 | 182 | 182
2019-04-30 18:00 | 185 | 185
2019-04-30 18:30 | 181 | 181
2019-04-30 19:00 | 179 | 179
2019-04-30 19:30 | 174 | 174
2019-04-30 20:00 | 172 | 172
2019-04-30 20:30 | 170 | 169
2019-04-30 21:00 | 162 | 162
2019-04-30 21:30 | 154 | 154
2019-04-30 22:00 | 146 | 145
2019-04-30 22:30 | 142 | 141
2019-04-30 23:00 | 140 | 139
2019-04-30 23:30 | 132 | 132
2019-05-01 | 122 | 121
2019-05-01 00:30 | 113 | 113
2019-05-01 01:00 | 107 | 107
2019-05-01 01:30 | 103 | 103
2019-05-01 02:00 | 101 | 101
2019-05-01 02:30 | 100 | 100
2019-05-01 03:00 | 99 | 99
2019-05-01 03:30 | 100 | 100
2019-05-01 04:00 | 100 | 100
2019-05-01 04:30 | 102 | 102
2019-05-01 05:00 | 106 | 106
2019-05-01 05:30 | 115 | 115
2019-05-01 06:00 | 124 | 123
2019-05-01 06:30 | 138 | 136
2019-05-01 07:00 | 150 | 150
2019-05-01 07:30 | 157 | 157
2019-05-01 08:00 | 158 | 158
2019-05-01 08:30 | 152 | 152
2019-05-01 09:00 | 146 | 146
2019-05-01 09:30 | 142 | 142
2019-05-01 10:00 | 142 | 142
2019-05-01 10:30 | 141 | 140
2019-05-01 11:00 | 138 | 138
2019-05-01 11:30 | 134 | 134
2019-05-01 12:00 | 133 | 132
2019-05-01 12:30 | 136 | 136
2019-05-01 13:00 | 138 | 138
2019-05-01 13:30 | 132 | 131
2019-05-01 14:00 | 134 | 133
2019-05-01 14:30 | 140 | 140
2019-05-01 15:00 | 145 | 145
2019-05-01 15:30 | 152 | 152
2019-05-01 16:00 | 161 | 161
2019-05-01 16:30 | 168 | 168
2019-05-01 17:00 | 176 | 175
2019-05-01 17:30 | 180 | 180
2019-05-01 18:00 | 186 | 186
2019-05-01 18:30 | 183 | 183
2019-05-01 19:00 | 181 | 181
2019-05-01 19:30 | 176 | 176
2019-05-01 20:00 | 173 | 173
2019-05-01 20:30 | 170 | 170
2019-05-01 21:00 | 164 | 164
2019-05-01 21:30 | 156 | 156
2019-05-01 22:00 | 150 | 150
2019-05-01 22:30 | 146 | 146
2019-05-01 23:00 | 142 | 141
2019-05-01 23:30 | 134 | 133
2019-05-02 | 123 | 122
2019-05-02 00:30 | 114 | 114
2019-05-02 01:00 | 109 | 109
2019-05-02 01:30 | 105 | 105
2019-05-02 02:00 | 102 | 102
2019-05-02 02:30 | 101 | 101
2019-05-02 03:00 | 100 | 100
2019-05-02 03:30 | 100 | 100
2019-05-02 04:00 | 100 | 100
2019-05-02 04:30 | 103 | 103
2019-05-02 05:00 | 107 | 107
2019-05-02 05:30 | 116 | 116
2019-05-02 06:00 | 124 | 124
2019-05-02 06:30 | 137 | 136
2019-05-02 07:00 | 146 | 145
2019-05-02 07:30 | 150 | 149
2019-05-02 08:00 | 146 | 145
2019-05-02 08:30 | 141 | 140
2019-05-02 09:00 | 138 | 137
2019-05-02 09:30 | 140 | 138
2019-05-02 10:00 | 143 | 140
2019-05-02 10:30 | 143 | 139
2019-05-02 11:00 | 146 | 142
2019-05-02 11:30 | 145 | 141
2019-05-02 12:00 | 144 | 140
2019-05-02 12:30 | 144 | 140
2019-05-02 13:00 | 142 | 139
2019-05-02 13:30 | 146 | 142
2019-05-02 14:00 | 146 | 142
2019-05-02 14:30 | 148 | 144
2019-05-02 15:00 | 149 | 146
2019-05-02 15:30 | 154 | 151
2019-05-02 16:00 | 163 | 160
2019-05-02 16:30 | 166 | 163
2019-05-02 17:00 | 173 | 170
2019-05-02 17:30 | 179 | 176
2019-05-02 18:00 | 184 | 181
2019-05-02 18:30 | 183 | 180
2019-05-02 19:00 | 181 | 179
2019-05-02 19:30 | 176 | 174
2019-05-02 20:00 | 175 | 172
2019-05-02 20:30 | 171 | 169
2019-05-02 21:00 | 164 | 162
2019-05-02 21:30 | 156 | 154
2019-05-02 22:00 | 149 | 148
2019-05-02 22:30 | 146 | 145
2019-05-02 23:00 | 143 | 142
2019-05-02 23:30 | 134 | 134
2019-05-03 | 123 | 123
2019-05-03 00:30 | 113 | 113
2019-05-03 01:00 | 107 | 106
2019-05-03 01:30 | 102 | 101
2019-05-03 02:00 | 98 | 98
2019-05-03 02:30 | 98 | 98
2019-05-03 03:00 | 100 | 100
2019-05-03 03:30 | 99 | 99
2019-05-03 04:00 | 100 | 100
2019-05-03 04:30 | 102 | 102
2019-05-03 05:00 | 106 | 106
2019-05-03 05:30 | 115 | 114
2019-05-03 06:00 | 124 | 122
2019-05-03 06:30 | 135 | 134
2019-05-03 07:00 | 145 | 144
2019-05-03 07:30 | 149 | 147
2019-05-03 08:00 | 151 | 150
2019-05-03 08:30 | 148 | 147
2019-05-03 09:00 | 143 | 142
2019-05-03 09:30 | 140 | 139
2019-05-03 10:00 | 137 | 136
2019-05-03 10:30 | 148 | 147
2019-05-03 11:00 | 152 | 150
2019-05-03 11:30 | 147 | 145
2019-05-03 12:00 | 150 | 148
2019-05-03 12:30 | 152 | 150
2019-05-03 13:00 | 150 | 148
2019-05-03 13:30 | 148 | 146
2019-05-03 14:00 | 143 | 141
2019-05-03 14:30 | 146 | 145
2019-05-03 15:00 | 153 | 151
2019-05-03 15:30 | 158 | 156
2019-05-03 16:00 | 165 | 163
2019-05-03 16:30 | 169 | 167
2019-05-03 17:00 | 174 | 172
2019-05-03 17:30 | 177 | 175
2019-05-03 18:00 | 178 | 175
2019-05-03 18:30 | 174 | 172
2019-05-03 19:00 | 172 | 170
2019-05-03 19:30 | 168 | 166
2019-05-03 20:00 | 166 | 163
2019-05-03 20:30 | 163 | 161
2019-05-03 21:00 | 157 | 155
2019-05-03 21:30 | 151 | 149
2019-05-03 22:00 | 146 | 144
2019-05-03 22:30 | 145 | 143
2019-05-03 23:00 | 143 | 141
2019-05-03 23:30 | 134 | 133
2019-05-04 | 124 | 123
2019-05-04 00:30 | 114 | 114
2019-05-04 01:00 | 109 | 109
2019-05-04 01:30 | 105 | 105
2019-05-04 02:00 | 102 | 102
2019-05-04 02:30 | 100 | 100
2019-05-04 03:00 | 99 | 99
2019-05-04 03:30 | 99 | 99
2019-05-04 04:00 | 99 | 98
2019-05-04 04:30 | 99 | 99
2019-05-04 05:00 | 100 | 99
2019-05-04 05:30 | 103 | 103
2019-05-04 06:00 | 107 | 106
2019-05-04 06:30 | 113 | 112
2019-05-04 07:00 | 116 | 115
2019-05-04 07:30 | 124 | 122
2019-05-04 08:00 | 127 | 127
2019-05-04 08:30 | 133 | 132
2019-05-04 09:00 | 137 | 136
2019-05-04 09:30 | 138 | 137
2019-05-04 10:00 | 140 | 139
2019-05-04 10:30 | 137 | 136
2019-05-04 11:00 | 139 | 138
2019-05-04 11:30 | 137 | 136
2019-05-04 12:00 | 129 | 128
2019-05-04 12:30 | 136 | 135
2019-05-04 13:00 | 137 | 136
2019-05-04 13:30 | 136 | 136
2019-05-04 14:00 | 140 | 139
2019-05-04 14:30 | 147 | 146
2019-05-04 15:00 | 145 | 145
2019-05-04 15:30 | 139 | 139
2019-05-04 16:00 | 138 | 138
2019-05-04 16:30 | 142 | 142
2019-05-04 17:00 | 147 | 147
2019-05-04 17:30 | 152 | 151
2019-05-04 18:00 | 156 | 155
2019-05-04 18:30 | 155 | 154
2019-05-04 19:00 | 154 | 153
2019-05-04 19:30 | 149 | 148
2019-05-04 20:00 | 147 | 146
2019-05-04 20:30 | 146 | 145
2019-05-04 21:00 | 140 | 139
2019-05-04 21:30 | 135 | 135
2019-05-04 22:00 | 131 | 131
2019-05-04 22:30 | 131 | 131
2019-05-04 23:00 | 130 | 130
2019-05-04 23:30 | 123 | 123
2019-05-05 | 115 | 115
2019-05-05 00:30 | 107 | 107
2019-05-05 01:00 | 102 | 102
2019-05-05 01:30 | 98 | 98
2019-05-05 02:00 | 95 | 95
2019-05-05 02:30 | 93 | 93
2019-05-05 03:00 | 92 | 92
2019-05-05 03:30 | 91 | 91
2019-05-05 04:00 | 91 | 91
2019-05-05 04:30 | 91 | 91
2019-05-05 05:00 | 92 | 92
2019-05-05 05:30 | 94 | 93
2019-05-05 06:00 | 96 | 96
2019-05-05 06:30 | 99 | 98
2019-05-05 07:00 | 101 | 101
2019-05-05 07:30 | 102 | 102
2019-05-05 08:00 | 100 | 100
2019-05-05 08:30 | 98 | 98
2019-05-05 09:00 | 94 | 94
2019-05-05 09:30 | 90 | 90
2019-05-05 10:00 | 86 | 85
2019-05-05 10:30 | 81 | 81
2019-05-05 11:00 | 77 | 76
2019-05-05 11:30 | 74 | 74
2019-05-05 12:00 | 72 | 72
2019-05-05 12:30 | 73 | 72
2019-05-05 13:00 | 74 | 73
2019-05-05 13:30 | 77 | 77
2019-05-05 14:00 | 82 | 81
2019-05-05 14:30 | 88 | 88
2019-05-05 15:00 | 96 | 96
2019-05-05 15:30 | 106 | 105
2019-05-05 16:00 | 115 | 115
2019-05-05 16:30 | 125 | 125
2019-05-05 17:00 | 136 | 135
2019-05-05 17:30 | 142 | 142
2019-05-05 18:00 | 150 | 149
2019-05-05 18:30 | 151 | 150
2019-05-05 19:00 | 149 | 148
2019-05-05 19:30 | 143 | 143
2019-05-05 20:00 | 141 | 141
2019-05-05 20:30 | 141 | 140
2019-05-05 21:00 | 135 | 134
2019-05-05 21:30 | 131 | 130
2019-05-05 22:00 | 127 | 127
2019-05-05 22:30 | 128 | 128
2019-05-05 23:00 | 127 | 127
2019-05-05 23:30 | 121 | 121
2019-05-06 | 112 | 112
2019-05-06 00:30 | 104 | 104
2019-05-06 01:00 | 99 | 99
2019-05-06 01:30 | 96 | 95
2019-05-06 02:00 | 93 | 92
2019-05-06 02:30 | 91 | 91
2019-05-06 03:00 | 89 | 89
2019-05-06 03:30 | 89 | 89
2019-05-06 04:00 | 89 | 89
2019-05-06 04:30 | 89 | 89
2019-05-06 05:00 | 90 | 90
2019-05-06 05:30 | 93 | 93
2019-05-06 06:00 | 95 | 95
2019-05-06 06:30 | 98 | 98
2019-05-06 07:00 | 101 | 101
2019-05-06 07:30 | 101 | 101
2019-05-06 08:00 | 98 | 98
2019-05-06 08:30 | 96 | 96
2019-05-06 09:00 | 93 | 93
2019-05-06 09:30 | 89 | 89
2019-05-06 10:00 | 84 | 84
2019-05-06 10:30 | 80 | 80
2019-05-06 11:00 | 76 | 76
2019-05-06 11:30 | 74 | 74
2019-05-06 12:00 | 73 | 73
2019-05-06 12:30 | 73 | 73
2019-05-06 13:00 | 75 | 74
2019-05-06 13:30 | 78 | 78
2019-05-06 14:00 | 83 | 83
2019-05-06 14:30 | 90 | 90
2019-05-06 15:00 | 98 | 97
2019-05-06 15:30 | 106 | 106
2019-05-06 16:00 | 117 | 116
2019-05-06 16:30 | 131 | 131
2019-05-06 17:00 | 143 | 143
2019-05-06 17:30 | 152 | 152
2019-05-06 18:00 | 160 | 160
2019-05-06 18:30 | 160 | 160
2019-05-06 19:00 | 158 | 158
2019-05-06 19:30 | 153 | 153
2019-05-06 20:00 | 152 | 152
2019-05-06 20:30 | 151 | 151
2019-05-06 21:00 | 140 | 140
2019-05-06 21:30 | 134 | 134
2019-05-06 22:00 | 130 | 130
2019-05-06 22:30 | 129 | 129
2019-05-06 23:00 | 128 | 128
2019-05-06 23:30 | 122 | 122
2019-05-07 | 113 | 113
2019-05-07 00:30 | 105 | 105
2019-05-07 01:00 | 100 | 100
2019-05-07 01:30 | 97 | 96
2019-05-07 02:00 | 94 | 93
2019-05-07 02:30 | 93 | 92
2019-05-07 03:00 | 92 | 91
2019-05-07 03:30 | 92 | 91
2019-05-07 04:00 | 91 | 91
2019-05-07 04:30 | 93 | 93
2019-05-07 05:00 | 98 | 97
2019-05-07 05:30 | 106 | 106
2019-05-07 06:00 | 116 | 116
2019-05-07 06:30 | 130 | 130
2019-05-07 07:00 | 142 | 141
2019-05-07 07:30 | 145 | 144
2019-05-07 08:00 | 142 | 141
2019-05-07 08:30 | 132 | 131
2019-05-07 09:00 | 121 | 120
2019-05-07 09:30 | 113 | 112
2019-05-07 10:00 | 109 | 108
2019-05-07 10:30 | 106 | 105
2019-05-07 11:00 | 102 | 102
2019-05-07 11:30 | 100 | 100
2019-05-07 12:00 | 101 | 101
2019-05-07 12:30 | 102 | 102
2019-05-07 13:00 | 106 | 106
2019-05-07 13:30 | 109 | 109
2019-05-07 14:00 | 115 | 114
2019-05-07 14:30 | 121 | 121
2019-05-07 15:00 | 126 | 126
2019-05-07 15:30 | 133 | 133
2019-05-07 16:00 | 143 | 143
2019-05-07 16:30 | 153 | 152
2019-05-07 17:00 | 162 | 162
2019-05-07 17:30 | 168 | 167
2019-05-07 18:00 | 175 | 174
2019-05-07 18:30 | 176 | 175
2019-05-07 19:00 | 176 | 176
2019-05-07 19:30 | 171 | 170
2019-05-07 20:00 | 170 | 169
2019-05-07 20:30 | 167 | 166
2019-05-07 21:00 | 159 | 159
2019-05-07 21:30 | 153 | 153
2019-05-07 22:00 | 146 | 146
2019-05-07 22:30 | 142 | 142
2019-05-07 23:00 | 139 | 139
2019-05-07 23:30 | 131 | 131
2019-05-08 | 121 | 121
2019-05-08 00:30 | 113 | 113
2019-05-08 01:00 | 107 | 107
2019-05-08 01:30 | 103 | 103
2019-05-08 02:00 | 101 | 100
2019-05-08 02:30 | 99 | 99
2019-05-08 03:00 | 99 | 98
2019-05-08 03:30 | 99 | 98
2019-05-08 04:00 | 99 | 99
2019-05-08 04:30 | 102 | 102
2019-05-08 05:00 | 107 | 107
2019-05-08 05:30 | 116 | 116
2019-05-08 06:00 | 125 | 125
2019-05-08 06:30 | 138 | 137
2019-05-08 07:00 | 149 | 148
2019-05-08 07:30 | 152 | 151
2019-05-08 08:00 | 146 | 145
2019-05-08 08:30 | 137 | 136
2019-05-08 09:00 | 128 | 127
2019-05-08 09:30 | 123 | 122
2019-05-08 10:00 | 117 | 117
2019-05-08 10:30 | 113 | 113
2019-05-08 11:00 | 111 | 111
2019-05-08 11:30 | 109 | 109
2019-05-08 12:00 | 110 | 110
2019-05-08 12:30 | 110 | 110
2019-05-08 13:00 | 112 | 112
2019-05-08 13:30 | 117 | 117
2019-05-08 14:00 | 123 | 123
2019-05-08 14:30 | 129 | 128
2019-05-08 15:00 | 135 | 135
2019-05-08 15:30 | 144 | 144
2019-05-08 16:00 | 155 | 155
2019-05-08 16:30 | 164 | 164
2019-05-08 17:00 | 173 | 173
2019-05-08 17:30 | 179 | 178
2019-05-08 18:00 | 184 | 184
2019-05-08 18:30 | 181 | 181
2019-05-08 19:00 | 181 | 181
2019-05-08 19:30 | 176 | 176
2019-05-08 20:00 | 174 | 174
2019-05-08 20:30 | 172 | 172
2019-05-08 21:00 | 165 | 165
2019-05-08 21:30 | 157 | 157
2019-05-08 22:00 | 150 | 150
2019-05-08 22:30 | 147 | 146
2019-05-08 23:00 | 144 | 143
2019-05-08 23:30 | 133 | 133
2019-05-09 | 123 | 123
2019-05-09 00:30 | 114 | 114
2019-05-09 01:00 | 109 | 109
2019-05-09 01:30 | 105 | 105
2019-05-09 02:00 | 102 | 102
2019-05-09 02:30 | 101 | 101
2019-05-09 03:00 | 100 | 100
2019-05-09 03:30 | 101 | 100
2019-05-09 04:00 | 101 | 101
2019-05-09 04:30 | 103 | 103
2019-05-09 05:00 | 107 | 107
2019-05-09 05:30 | 116 | 116
2019-05-09 06:00 | 126 | 126
2019-05-09 06:30 | 139 | 139
2019-05-09 07:00 | 151 | 151
2019-05-09 07:30 | 155 | 154
2019-05-09 08:00 | 148 | 147
2019-05-09 08:30 | 137 | 136
2019-05-09 09:00 | 127 | 126
2019-05-09 09:30 | 120 | 119
2019-05-09 10:00 | 114 | 113
2019-05-09 10:30 | 110 | 109
2019-05-09 11:00 | 108 | 107
2019-05-09 11:30 | 105 | 104
2019-05-09 12:00 | 105 | 104
2019-05-09 12:30 | 106 | 106
2019-05-09 13:00 | 109 | 109
2019-05-09 13:30 | 113 | 112
2019-05-09 14:00 | 119 | 118
2019-05-09 14:30 | 125 | 125
2019-05-09 15:00 | 132 | 132
2019-05-09 15:30 | 140 | 139
2019-05-09 16:00 | 150 | 150
2019-05-09 16:30 | 160 | 159
2019-05-09 17:00 | 169 | 169
2019-05-09 17:30 | 174 | 174
2019-05-09 18:00 | 183 | 183
2019-05-09 18:30 | 181 | 181
2019-05-09 19:00 | 181 | 181
2019-05-09 19:30 | 176 | 176
2019-05-09 20:00 | 174 | 174
2019-05-09 20:30 | 173 | 173
2019-05-09 21:00 | 166 | 166
2019-05-09 21:30 | 157 | 157
2019-05-09 22:00 | 148 | 148
2019-05-09 22:30 | 145 | 145
2019-05-09 23:00 | 141 | 141
2019-05-09 23:30 | 132 | 132
2019-05-10 | 123 | 123
2019-05-10 00:30 | 114 | 114
2019-05-10 01:00 | 108 | 108
2019-05-10 01:30 | 105 | 104
2019-05-10 02:00 | 102 | 102
2019-05-10 02:30 | 101 | 101
2019-05-10 03:00 | 99 | 99
2019-05-10 03:30 | 100 | 100
2019-05-10 04:00 | 101 | 100
2019-05-10 04:30 | 103 | 103
2019-05-10 05:00 | 108 | 108
2019-05-10 05:30 | 116 | 116
2019-05-10 06:00 | 125 | 125
2019-05-10 06:30 | 138 | 138
2019-05-10 07:00 | 150 | 149
2019-05-10 07:30 | 159 | 158
2019-05-10 08:00 | 157 | 155
2019-05-10 08:30 | 148 | 147
2019-05-10 09:00 | 140 | 139
2019-05-10 09:30 | 130 | 129
2019-05-10 10:00 | 131 | 130
2019-05-10 10:30 | 134 | 132
2019-05-10 11:00 | 130 | 129
2019-05-10 11:30 | 126 | 125
2019-05-10 12:00 | 121 | 120
2019-05-10 12:30 | 118 | 117
2019-05-10 13:00 | 123 | 121
2019-05-10 13:30 | 138 | 135
2019-05-10 14:00 | 138 | 137
2019-05-10 14:30 | 141 | 140
2019-05-10 15:00 | 153 | 151
2019-05-10 15:30 | 163 | 161
2019-05-10 16:00 | 165 | 164
2019-05-10 16:30 | 169 | 168
2019-05-10 17:00 | 176 | 174
2019-05-10 17:30 | 180 | 178
2019-05-10 18:00 | 182 | 180
2019-05-10 18:30 | 178 | 176
2019-05-10 19:00 | 176 | 175
2019-05-10 19:30 | 171 | 170
2019-05-10 20:00 | 168 | 167
2019-05-10 20:30 | 165 | 164
2019-05-10 21:00 | 157 | 156
2019-05-10 21:30 | 151 | 150
2019-05-10 22:00 | 145 | 145
2019-05-10 22:30 | 144 | 144
2019-05-10 23:00 | 142 | 141
2019-05-10 23:30 | 133 | 133
2019-05-11 | 123 | 123
2019-05-11 00:30 | 114 | 114
2019-05-11 01:00 | 108 | 108
2019-05-11 01:30 | 104 | 104
2019-05-11 02:00 | 101 | 101
2019-05-11 02:30 | 98 | 98
2019-05-11 03:00 | 97 | 97
2019-05-11 03:30 | 97 | 97
2019-05-11 04:00 | 97 | 97
2019-05-11 04:30 | 98 | 98
2019-05-11 05:00 | 99 | 99
2019-05-11 05:30 | 103 | 103
2019-05-11 06:00 | 106 | 106
2019-05-11 06:30 | 111 | 111
2019-05-11 07:00 | 116 | 115
2019-05-11 07:30 | 117 | 117
2019-05-11 08:00 | 116 | 115
2019-05-11 08:30 | 114 | 113
2019-05-11 09:00 | 109 | 108
2019-05-11 09:30 | 102 | 102
2019-05-11 10:00 | 97 | 97
2019-05-11 10:30 | 92 | 92
2019-05-11 11:00 | 86 | 86
2019-05-11 11:30 | 83 | 83
2019-05-11 12:00 | 81 | 80
2019-05-11 12:30 | 80 | 80
2019-05-11 13:00 | 81 | 81
2019-05-11 13:30 | 83 | 83
2019-05-11 14:00 | 87 | 87
2019-05-11 14:30 | 93 | 93
2019-05-11 15:00 | 101 | 101
2019-05-11 15:30 | 110 | 110
2019-05-11 16:00 | 121 | 120
2019-05-11 16:30 | 131 | 131
2019-05-11 17:00 | 142 | 142
2019-05-11 17:30 | 149 | 149
2019-05-11 18:00 | 155 | 155
2019-05-11 18:30 | 155 | 155
2019-05-11 19:00 | 155 | 155
2019-05-11 19:30 | 151 | 151
2019-05-11 20:00 | 150 | 150
2019-05-11 20:30 | 150 | 150
2019-05-11 21:00 | 144 | 144
2019-05-11 21:30 | 140 | 140
2019-05-11 22:00 | 136 | 136
2019-05-11 22:30 | 136 | 136
2019-05-11 23:00 | 136 | 136
2019-05-11 23:30 | 130 | 130
2019-05-12 | 122 | 122
2019-05-12 00:30 | 113 | 112
2019-05-12 01:00 | 108 | 107
2019-05-12 01:30 | 102 | 102
2019-05-12 02:00 | 98 | 98
2019-05-12 02:30 | 96 | 96
2019-05-12 03:00 | 95 | 94
2019-05-12 03:30 | 94 | 94
2019-05-12 04:00 | 94 | 94
2019-05-12 04:30 | 95 | 95
2019-05-12 05:00 | 96 | 96
2019-05-12 05:30 | 99 | 98
2019-05-12 06:00 | 102 | 101
2019-05-12 06:30 | 105 | 105
2019-05-12 07:00 | 110 | 110
2019-05-12 07:30 | 115 | 115
2019-05-12 08:00 | 117 | 117
2019-05-12 08:30 | 120 | 120
2019-05-12 09:00 | 116 | 116
2019-05-12 09:30 | 110 | 110
2019-05-12 10:00 | 104 | 104
2019-05-12 10:30 | 101 | 101
2019-05-12 11:00 | 92 | 92
2019-05-12 11:30 | 85 | 85
2019-05-12 12:00 | 85 | 85
2019-05-12 12:30 | 88 | 88
2019-05-12 13:00 | 92 | 92
2019-05-12 13:30 | 95 | 95
2019-05-12 14:00 | 96 | 96
2019-05-12 14:30 | 97 | 97
2019-05-12 15:00 | 104 | 104
2019-05-12 15:30 | 111 | 111
2019-05-12 16:00 | 120 | 120
2019-05-12 16:30 | 130 | 130
2019-05-12 17:00 | 142 | 142
2019-05-12 17:30 | 150 | 150
2019-05-12 18:00 | 156 | 156
2019-05-12 18:30 | 156 | 156
2019-05-12 19:00 | 155 | 155
2019-05-12 19:30 | 151 | 151
2019-05-12 20:00 | 150 | 150
2019-05-12 20:30 | 150 | 150
2019-05-12 21:00 | 144 | 144
2019-05-12 21:30 | 139 | 139
2019-05-12 22:00 | 134 | 134
2019-05-12 22:30 | 133 | 133
2019-05-12 23:00 | 132 | 132
2019-05-12 23:30 | 125 | 125
2019-05-13 | 116 | 116
2019-05-13 00:30 | 109 | 108
2019-05-13 01:00 | 103 | 102
2019-05-13 01:30 | 100 | 99
2019-05-13 02:00 | 98 | 96
2019-05-13 02:30 | 96 | 95
2019-05-13 03:00 | 95 | 94
2019-05-13 03:30 | 96 | 95
2019-05-13 04:00 | 97 | 95
2019-05-13 04:30 | 100 | 99
2019-05-13 05:00 | 105 | 104
2019-05-13 05:30 | 112 | 112
2019-05-13 06:00 | 121 | 121
2019-05-13 06:30 | 133 | 133
2019-05-13 07:00 | 144 | 144
2019-05-13 07:30 | 153 | 153
2019-05-13 08:00 | 156 | 155
2019-05-13 08:30 | 153 | 153
2019-05-13 09:00 | 151 | 151
2019-05-13 09:30 | 149 | 148
2019-05-13 10:00 | 143 | 142
2019-05-13 10:30 | 135 | 134
2019-05-13 11:00 | 133 | 132
2019-05-13 11:30 | 130 | 129
2019-05-13 12:00 | 128 | 128
2019-05-13 12:30 | 130 | 130
2019-05-13 13:00 | 137 | 136
2019-05-13 13:30 | 139 | 137
2019-05-13 14:00 | 147 | 145
2019-05-13 14:30 | 147 | 145
2019-05-13 15:00 | 145 | 144
2019-05-13 15:30 | 148 | 146
2019-05-13 16:00 | 154 | 152
2019-05-13 16:30 | 161 | 159
2019-05-13 17:00 | 169 | 167
2019-05-13 17:30 | 177 | 177
2019-05-13 18:00 | 183 | 183
2019-05-13 18:30 | 180 | 180
2019-05-13 19:00 | 178 | 177
2019-05-13 19:30 | 172 | 171
2019-05-13 20:00 | 169 | 168
2019-05-13 20:30 | 167 | 166
2019-05-13 21:00 | 159 | 158
2019-05-13 21:30 | 152 | 151
2019-05-13 22:00 | 145 | 142
2019-05-13 22:30 | 142 | 140
2019-05-13 23:00 | 140 | 137
2019-05-13 23:30 | 135 | 133
2019-05-14 | 126 | 124
2019-05-14 00:30 | 116 | 115
2019-05-14 01:00 | 110 | 109
2019-05-14 01:30 | 107 | 106
2019-05-14 02:00 | 103 | 103
2019-05-14 02:30 | 102 | 102
2019-05-14 03:00 | 102 | 101
2019-05-14 03:30 | 101 | 100
2019-05-14 04:00 | 102 | 101
2019-05-14 04:30 | 106 | 105
2019-05-14 05:00 | 110 | 109
2019-05-14 05:30 | 119 | 117
2019-05-14 06:00 | 129 | 127
2019-05-14 06:30 | 142 | 139
2019-05-14 07:00 | 153 | 151
2019-05-14 07:30 | 160 | 158
2019-05-14 08:00 | 159 | 157
2019-05-14 08:30 | 156 | 153
2019-05-14 09:00 | 149 | 147
2019-05-14 09:30 | 142 | 140
2019-05-14 10:00 | 138 | 135
2019-05-14 10:30 | 131 | 129
2019-05-14 11:00 | 124 | 122
2019-05-14 11:30 | 120 | 118
2019-05-14 12:00 | 118 | 116
2019-05-14 12:30 | 120 | 118
2019-05-14 13:00 | 127 | 125
2019-05-14 13:30 | 130 | 127
2019-05-14 14:00 | 140 | 137
2019-05-14 14:30 | 147 | 144
2019-05-14 15:00 | 150 | 148
2019-05-14 15:30 | 155 | 153
2019-05-14 16:00 | 162 | 159
2019-05-14 16:30 | 166 | 164
2019-05-14 17:00 | 174 | 173
2019-05-14 17:30 | 182 | 181
2019-05-14 18:00 | 187 | 186
2019-05-14 18:30 | 183 | 183
2019-05-14 19:00 | 182 | 182
2019-05-14 19:30 | 177 | 177
2019-05-14 20:00 | 174 | 174
2019-05-14 20:30 | 172 | 172
2019-05-14 21:00 | 165 | 164
2019-05-14 21:30 | 157 | 157
2019-05-14 22:00 | 150 | 148
2019-05-14 22:30 | 147 | 145
2019-05-14 23:00 | 144 | 142
2019-05-14 23:30 | 135 | 133
2019-05-15 | 125 | 124
2019-05-15 00:30 | 116 | 114
2019-05-15 01:00 | 111 | 108
2019-05-15 01:30 | 107 | 105
2019-05-15 02:00 | 105 | 102
2019-05-15 02:30 | 103 | 101
2019-05-15 03:00 | 102 | 100
2019-05-15 03:30 | 103 | 101
2019-05-15 04:00 | 103 | 100
2019-05-15 04:30 | 106 | 104
2019-05-15 05:00 | 111 | 108
2019-05-15 05:30 | 121 | 117
2019-05-15 06:00 | 129 | 126
2019-05-15 06:30 | 141 | 141
2019-05-15 07:00 | 153 | 152
2019-05-15 07:30 | 160 | 158
2019-05-15 08:00 | 160 | 158
2019-05-15 08:30 | 155 | 153
2019-05-15 09:00 | 146 | 145
2019-05-15 09:30 | 142 | 142
2019-05-15 10:00 | 138 | 137
2019-05-15 10:30 | 136 | 135
2019-05-15 11:00 | 132 | 131
2019-05-15 11:30 | 131 | 131
2019-05-15 12:00 | 134 | 133
2019-05-15 12:30 | 140 | 139
2019-05-15 13:00 | 144 | 143
2019-05-15 13:30 | 142 | 141
2019-05-15 14:00 | 143 | 142
2019-05-15 14:30 | 149 | 148
2019-05-15 15:00 | 151 | 150
2019-05-15 15:30 | 154 | 153
2019-05-15 16:00 | 161 | 160
2019-05-15 16:30 | 168 | 167
2019-05-15 17:00 | 176 | 175
2019-05-15 17:30 | 184 | 183
2019-05-15 18:00 | 187 | 186
2019-05-15 18:30 | 185 | 184
2019-05-15 19:00 | 183 | 183
2019-05-15 19:30 | 178 | 177
2019-05-15 20:00 | 176 | 175
2019-05-15 20:30 | 174 | 174
2019-05-15 21:00 | 167 | 166
2019-05-15 21:30 | 158 | 158
2019-05-15 22:00 | 151 | 150
2019-05-15 22:30 | 148 | 147
2019-05-15 23:00 | 144 | 143
2019-05-15 23:30 | 135 | 134
2019-05-16 | 123 | 123
2019-05-16 00:30 | 113 | 112
2019-05-16 01:00 | 106 | 106
2019-05-16 01:30 | 103 | 103
2019-05-16 02:00 | 100 | 100
2019-05-16 02:30 | 99 | 99
2019-05-16 03:00 | 98 | 97
2019-05-16 03:30 | 99 | 98
2019-05-16 04:00 | 99 | 98
2019-05-16 04:30 | 102 | 102
2019-05-16 05:00 | 106 | 105
2019-05-16 05:30 | 115 | 114
2019-05-16 06:00 | 125 | 124
2019-05-16 06:30 | 137 | 136
2019-05-16 07:00 | 148 | 145
2019-05-16 07:30 | 153 | 150
2019-05-16 08:00 | 148 | 146
2019-05-16 08:30 | 141 | 139
2019-05-16 09:00 | 140 | 137
2019-05-16 09:30 | 138 | 136
2019-05-16 10:00 | 135 | 132
2019-05-16 10:30 | 131 | 129
2019-05-16 11:00 | 129 | 127
2019-05-16 11:30 | 126 | 124
2019-05-16 12:00 | 128 | 125
2019-05-16 12:30 | 130 | 127
2019-05-16 13:00 | 132 | 129
2019-05-16 13:30 | 133 | 130
2019-05-16 14:00 | 136 | 133
2019-05-16 14:30 | 141 | 137
2019-05-16 15:00 | 145 | 142
2019-05-16 15:30 | 150 | 147
2019-05-16 16:00 | 158 | 156
2019-05-16 16:30 | 166 | 165
2019-05-16 17:00 | 174 | 173
2019-05-16 17:30 | 182 | 181
2019-05-16 18:00 | 186 | 185
2019-05-16 18:30 | 183 | 183
2019-05-16 19:00 | 182 | 182
2019-05-16 19:30 | 178 | 177
2019-05-16 20:00 | 175 | 175
2019-05-16 20:30 | 173 | 173
2019-05-16 21:00 | 166 | 166
2019-05-16 21:30 | 158 | 158
2019-05-16 22:00 | 151 | 151
2019-05-16 22:30 | 149 | 149
2019-05-16 23:00 | 146 | 146
2019-05-16 23:30 | 136 | 135
2019-05-17 | 126 | 126
2019-05-17 00:30 | 115 | 115
2019-05-17 01:00 | 109 | 109
2019-05-17 01:30 | 105 | 105
2019-05-17 02:00 | 103 | 103
2019-05-17 02:30 | 101 | 101
2019-05-17 03:00 | 100 | 100
2019-05-17 03:30 | 101 | 101
2019-05-17 04:00 | 101 | 101
2019-05-17 04:30 | 104 | 104
2019-05-17 05:00 | 108 | 108
2019-05-17 05:30 | 116 | 116
2019-05-17 06:00 | 125 | 125
2019-05-17 06:30 | 139 | 138
2019-05-17 07:00 | 151 | 151
2019-05-17 07:30 | 161 | 160
2019-05-17 08:00 | 164 | 164
2019-05-17 08:30 | 164 | 163
2019-05-17 09:00 | 159 | 159
2019-05-17 09:30 | 154 | 154
2019-05-17 10:00 | 152 | 152
2019-05-17 10:30 | 150 | 149
2019-05-17 11:00 | 203 | 203
2019-05-17 11:30 | 204 | 204
2019-05-17 12:00 | 210 | 210
2019-05-17 12:30 | 214 | 213
2019-05-17 13:00 | 212 | 212
2019-05-17 13:30 | 212 | 211
2019-05-17 14:00 | 207 | 207
2019-05-17 14:30 | 207 | 206
2019-05-17 15:00 | 205 | 205
2019-05-17 15:30 | 210 | 210
2019-05-17 16:00 | 225 | 224
2019-05-17 16:30 | 237 | 237
2019-05-17 17:00 | 245 | 245
2019-05-17 17:30 | 254 | 254
2019-05-17 18:00 | 256 | 256
2019-05-17 18:30 | 254 | 254
2019-05-17 19:00 | 251 | 251
2019-05-17 19:30 | 246 | 246
2019-05-17 20:00 | 244 | 244
2019-05-17 20:30 | 242 | 242
2019-05-17 21:00 | 231 | 231
2019-05-17 21:30 | 220 | 220
2019-05-17 22:00 | 213 | 213
2019-05-17 22:30 | 210 | 210
2019-05-17 23:00 | 208 | 207
2019-05-17 23:30 | 198 | 198
2019-05-18 | 186 | 185
2019-05-18 00:30 | 169 | 168
2019-05-18 01:00 | 160 | 159
2019-05-18 01:30 | 155 | 153
2019-05-18 02:00 | 150 | 147
2019-05-18 02:30 | 147 | 144
2019-05-18 03:00 | 145 | 142
2019-05-18 03:30 | 144 | 141
2019-05-18 04:00 | 144 | 141
2019-05-18 04:30 | 146 | 143
2019-05-18 05:00 | 147 | 145
2019-05-18 05:30 | 151 | 149
2019-05-18 06:00 | 157 | 155
2019-05-18 06:30 | 165 | 164
2019-05-18 07:00 | 173 | 172
2019-05-18 07:30 | 180 | 180
2019-05-18 08:00 | 183 | 183
2019-05-18 08:30 | 185 | 185
2019-05-18 09:00 | 183 | 183
2019-05-18 09:30 | 177 | 177
2019-05-18 10:00 | 181 | 180
2019-05-18 10:30 | 177 | 176
2019-05-18 11:00 | 167 | 167
2019-05-18 11:30 | 159 | 159
2019-05-18 12:00 | 156 | 156
2019-05-18 12:30 | 155 | 155
2019-05-18 13:00 | 152 | 152
2019-05-18 13:30 | 159 | 159
2019-05-18 14:00 | 177 | 177
2019-05-18 14:30 | 181 | 181
2019-05-18 15:00 | 181 | 181
2019-05-18 15:30 | 183 | 183
2019-05-18 16:00 | 189 | 189
2019-05-18 16:30 | 201 | 201
2019-05-18 17:00 | 213 | 213
2019-05-18 17:30 | 222 | 222
2019-05-18 18:00 | 228 | 228
2019-05-18 18:30 | 227 | 227
2019-05-18 19:00 | 225 | 225
2019-05-18 19:30 | 219 | 219
2019-05-18 20:00 | 218 | 218
2019-05-18 20:30 | 216 | 216
2019-05-18 21:00 | 208 | 208
2019-05-18 21:30 | 201 | 201
2019-05-18 22:00 | 197 | 197
2019-05-18 22:30 | 198 | 197
2019-05-18 23:00 | 198 | 197
2019-05-18 23:30 | 189 | 188
2019-05-19 | 176 | 175
2019-05-19 00:30 | 164 | 162
2019-05-19 01:00 | 155 | 153
2019-05-19 01:30 | 149 | 146
2019-05-19 02:00 | 143 | 140
2019-05-19 02:30 | 141 | 137
2019-05-19 03:00 | 139 | 137
2019-05-19 03:30 | 136 | 135
2019-05-19 04:00 | 136 | 134
2019-05-19 04:30 | 136 | 134
2019-05-19 05:00 | 137 | 136
2019-05-19 05:30 | 140 | 139
2019-05-19 06:00 | 144 | 143
2019-05-19 06:30 | 149 | 148
2019-05-19 07:00 | 153 | 152
2019-05-19 07:30 | 159 | 159
2019-05-19 08:00 | 161 | 161
2019-05-19 08:30 | 159 | 159
2019-05-19 09:00 | 157 | 156
2019-05-19 09:30 | 154 | 154
2019-05-19 10:00 | 145 | 145
2019-05-19 10:30 | 141 | 141
2019-05-19 11:00 | 141 | 141
2019-05-19 11:30 | 139 | 139
2019-05-19 12:00 | 137 | 137
2019-05-19 12:30 | 137 | 137
2019-05-19 13:00 | 140 | 140
2019-05-19 13:30 | 140 | 140
2019-05-19 14:00 | 149 | 149
2019-05-19 14:30 | 159 | 159
2019-05-19 15:00 | 168 | 168
2019-05-19 15:30 | 180 | 180
2019-05-19 16:00 | 190 | 190
2019-05-19 16:30 | 201 | 201
2019-05-19 17:00 | 216 | 216
2019-05-19 17:30 | 230 | 230
2019-05-19 18:00 | 241 | 241
2019-05-19 18:30 | 239 | 239
2019-05-19 19:00 | 236 | 236
2019-05-19 19:30 | 230 | 229
2019-05-19 20:00 | 225 | 225
2019-05-19 20:30 | 221 | 221
2019-05-19 21:00 | 212 | 212
2019-05-19 21:30 | 204 | 203
2019-05-19 22:00 | 197 | 197
2019-05-19 22:30 | 194 | 194
2019-05-19 23:00 | 191 | 191
2019-05-19 23:30 | 182 | 181
2019-05-20 | 170 | 169
2019-05-20 00:30 | 157 | 157
2019-05-20 01:00 | 150 | 149
2019-05-20 01:30 | 145 | 144
2019-05-20 02:00 | 141 | 140
2019-05-20 02:30 | 139 | 137
2019-05-20 03:00 | 138 | 137
2019-05-20 03:30 | 139 | 137
2019-05-20 04:00 | 139 | 138
2019-05-20 04:30 | 144 | 142
2019-05-20 05:00 | 150 | 150
2019-05-20 05:30 | 163 | 163
2019-05-20 06:00 | 177 | 177
2019-05-20 06:30 | 196 | 196
2019-05-20 07:00 | 217 | 217
2019-05-20 07:30 | 231 | 230
2019-05-20 08:00 | 234 | 234
2019-05-20 08:30 | 226 | 226
2019-05-20 09:00 | 221 | 220
2019-05-20 09:30 | 224 | 224
2019-05-20 10:00 | 229 | 229
2019-05-20 10:30 | 195 | 195
2019-05-20 11:00 | 150 | 150
2019-05-20 11:30 | 146 | 146
2019-05-20 12:00 | 150 | 150
2019-05-20 12:30 | 155 | 155
2019-05-20 13:00 | 150 | 150
2019-05-20 13:30 | 151 | 150
2019-05-20 14:00 | 150 | 150
2019-05-20 14:30 | 154 | 154
2019-05-20 15:00 | 156 | 156
2019-05-20 15:30 | 164 | 164
2019-05-20 16:00 | 168 | 168
2019-05-20 16:30 | 173 | 173
2019-05-20 17:00 | 184 | 184
2019-05-20 17:30 | 193 | 193
2019-05-20 18:00 | 197 | 197
2019-05-20 18:30 | 193 | 193
2019-05-20 19:00 | 191 | 191
2019-05-20 19:30 | 184 | 184
2019-05-20 20:00 | 180 | 179
2019-05-20 20:30 | 177 | 177
2019-05-20 21:00 | 169 | 169
2019-05-20 21:30 | 161 | 161
2019-05-20 22:00 | 154 | 154
2019-05-20 22:30 | 151 | 151
2019-05-20 23:00 | 146 | 146
2019-05-20 23:30 | 137 | 137
2019-05-21 | 127 | 127
2019-05-21 00:30 | 118 | 118
2019-05-21 01:00 | 111 | 111
2019-05-21 01:30 | 107 | 107
2019-05-21 02:00 | 104 | 104
2019-05-21 02:30 | 103 | 103
2019-05-21 03:00 | 102 | 102
2019-05-21 03:30 | 102 | 102
2019-05-21 04:00 | 103 | 103
2019-05-21 04:30 | 106 | 106
2019-05-21 05:00 | 110 | 110
2019-05-21 05:30 | 119 | 119
2019-05-21 06:00 | 129 | 129
2019-05-21 06:30 | 143 | 143
2019-05-21 07:00 | 158 | 158
2019-05-21 07:30 | 167 | 167
2019-05-21 08:00 | 163 | 163
2019-05-21 08:30 | 156 | 156
2019-05-21 09:00 | 147 | 147
2019-05-21 09:30 | 141 | 141
2019-05-21 10:00 | 136 | 136
2019-05-21 10:30 | 131 | 130
2019-05-21 11:00 | 131 | 131
2019-05-21 11:30 | 129 | 129
2019-05-21 12:00 | 130 | 130
2019-05-21 12:30 | 128 | 128
2019-05-21 13:00 | 129 | 129
2019-05-21 13:30 | 130 | 130
2019-05-21 14:00 | 134 | 134
2019-05-21 14:30 | 139 | 139
2019-05-21 15:00 | 146 | 146
2019-05-21 15:30 | 153 | 153
2019-05-21 16:00 | 162 | 162
2019-05-21 16:30 | 171 | 171
2019-05-21 17:00 | 178 | 178
2019-05-21 17:30 | 185 | 185
2019-05-21 18:00 | 190 | 189
2019-05-21 18:30 | 186 | 186
2019-05-21 19:00 | 184 | 184
2019-05-21 19:30 | 179 | 179
2019-05-21 20:00 | 177 | 177
2019-05-21 20:30 | 175 | 175
2019-05-21 21:00 | 168 | 168
2019-05-21 21:30 | 160 | 160
2019-05-21 22:00 | 152 | 152
2019-05-21 22:30 | 148 | 148
2019-05-21 23:00 | 145 | 145
2019-05-21 23:30 | 137 | 137
2019-05-22 | 126 | 126
2019-05-22 00:30 | 117 | 116
2019-05-22 01:00 | 111 | 111
2019-05-22 01:30 | 107 | 107
2019-05-22 02:00 | 105 | 104
2019-05-22 02:30 | 103 | 102
2019-05-22 03:00 | 102 | 102
2019-05-22 03:30 | 102 | 102
2019-05-22 04:00 | 102 | 102
2019-05-22 04:30 | 106 | 106
2019-05-22 05:00 | 110 | 110
2019-05-22 05:30 | 120 | 120
2019-05-22 06:00 | 129 | 129
2019-05-22 06:30 | 144 | 144
2019-05-22 07:00 | 158 | 158
2019-05-22 07:30 | 164 | 164
2019-05-22 08:00 | 159 | 159
2019-05-22 08:30 | 151 | 151
2019-05-22 09:00 | 142 | 142
2019-05-22 09:30 | 136 | 136
2019-05-22 10:00 | 135 | 135
2019-05-22 10:30 | 142 | 142
2019-05-22 11:00 | 152 | 152
2019-05-22 11:30 | 154 | 154
2019-05-22 12:00 | 152 | 152
2019-05-22 12:30 | 147 | 147
2019-05-22 13:00 | 146 | 146
2019-05-22 13:30 | 146 | 146
2019-05-22 14:00 | 147 | 147
2019-05-22 14:30 | 151 | 151
2019-05-22 15:00 | 153 | 153
2019-05-22 15:30 | 156 | 156
2019-05-22 16:00 | 161 | 161
2019-05-22 16:30 | 169 | 168
2019-05-22 17:00 | 178 | 178
2019-05-22 17:30 | 187 | 186
2019-05-22 18:00 | 190 | 190
2019-05-22 18:30 | 187 | 186
2019-05-22 19:00 | 185 | 185
2019-05-22 19:30 | 180 | 180
2019-05-22 20:00 | 178 | 178
2019-05-22 20:30 | 176 | 176
2019-05-22 21:00 | 169 | 169
2019-05-22 21:30 | 161 | 161
2019-05-22 22:00 | 152 | 151
2019-05-22 22:30 | 149 | 148
2019-05-22 23:00 | 146 | 146
2019-05-22 23:30 | 138 | 138
2019-05-23 | 129 | 129
2019-05-23 00:30 | 118 | 118
2019-05-23 01:00 | 113 | 113
2019-05-23 01:30 | 108 | 108
2019-05-23 02:00 | 104 | 104
2019-05-23 02:30 | 103 | 103
2019-05-23 03:00 | 102 | 102
2019-05-23 03:30 | 103 | 103
2019-05-23 04:00 | 103 | 103
2019-05-23 04:30 | 106 | 106
2019-05-23 05:00 | 111 | 111
2019-05-23 05:30 | 121 | 121
2019-05-23 06:00 | 132 | 131
2019-05-23 06:30 | 146 | 145
2019-05-23 07:00 | 159 | 158
2019-05-23 07:30 | 166 | 164
2019-05-23 08:00 | 160 | 159
2019-05-23 08:30 | 153 | 152
2019-05-23 09:00 | 146 | 145
2019-05-23 09:30 | 141 | 140
2019-05-23 10:00 | 133 | 132
2019-05-23 10:30 | 128 | 127
2019-05-23 11:00 | 131 | 130
2019-05-23 11:30 | 136 | 134
2019-05-23 12:00 | 137 | 135
2019-05-23 12:30 | 134 | 132
2019-05-23 13:00 | 133 | 132
2019-05-23 13:30 | 133 | 132
2019-05-23 14:00 | 137 | 135
2019-05-23 14:30 | 143 | 141
2019-05-23 15:00 | 146 | 145
2019-05-23 15:30 | 151 | 149
2019-05-23 16:00 | 159 | 157
2019-05-23 16:30 | 167 | 164
2019-05-23 17:00 | 174 | 173
2019-05-23 17:30 | 182 | 180
2019-05-23 18:00 | 188 | 186
2019-05-23 18:30 | 186 | 184
2019-05-23 19:00 | 185 | 184
2019-05-23 19:30 | 180 | 179
2019-05-23 20:00 | 179 | 176
2019-05-23 20:30 | 177 | 176
2019-05-23 21:00 | 170 | 168
2019-05-23 21:30 | 161 | 160
2019-05-23 22:00 | 154 | 153
2019-05-23 22:30 | 151 | 150
2019-05-23 23:00 | 148 | 148
2019-05-23 23:30 | 140 | 140
2019-05-24 | 130 | 130
2019-05-24 00:30 | 118 | 118
2019-05-24 01:00 | 112 | 112
2019-05-24 01:30 | 108 | 108
2019-05-24 02:00 | 105 | 105
2019-05-24 02:30 | 103 | 103
2019-05-24 03:00 | 102 | 102
2019-05-24 03:30 | 103 | 103
2019-05-24 04:00 | 103 | 103
2019-05-24 04:30 | 106 | 106
2019-05-24 05:00 | 111 | 111
2019-05-24 05:30 | 120 | 120
2019-05-24 06:00 | 130 | 130
2019-05-24 06:30 | 145 | 144
2019-05-24 07:00 | 157 | 157
2019-05-24 07:30 | 163 | 162
2019-05-24 08:00 | 159 | 158
2019-05-24 08:30 | 153 | 152
2019-05-24 09:00 | 141 | 140
2019-05-24 09:30 | 134 | 133
2019-05-24 10:00 | 129 | 128
2019-05-24 10:30 | 125 | 124
2019-05-24 11:00 | 122 | 121
2019-05-24 11:30 | 124 | 123
2019-05-24 12:00 | 128 | 127
2019-05-24 12:30 | 125 | 125
2019-05-24 13:00 | 127 | 127
2019-05-24 13:30 | 133 | 132
2019-05-24 14:00 | 138 | 137
2019-05-24 14:30 | 143 | 142
2019-05-24 15:00 | 142 | 141
2019-05-24 15:30 | 146 | 146
2019-05-24 16:00 | 153 | 152
2019-05-24 16:30 | 161 | 160
2019-05-24 17:00 | 171 | 170
2019-05-24 17:30 | 177 | 175
2019-05-24 18:00 | 179 | 177
2019-05-24 18:30 | 176 | 174
2019-05-24 19:00 | 174 | 173
2019-05-24 19:30 | 171 | 169
2019-05-24 20:00 | 170 | 167
2019-05-24 20:30 | 168 | 166
2019-05-24 21:00 | 161 | 159
2019-05-24 21:30 | 154 | 153
2019-05-24 22:00 | 149 | 148
2019-05-24 22:30 | 147 | 146
2019-05-24 23:00 | 145 | 145
2019-05-24 23:30 | 137 | 137
2019-05-25 | 127 | 127
2019-05-25 00:30 | 118 | 118
2019-05-25 01:00 | 111 | 111
2019-05-25 01:30 | 107 | 107
2019-05-25 02:00 | 103 | 103
2019-05-25 02:30 | 102 | 102
2019-05-25 03:00 | 100 | 100
2019-05-25 03:30 | 100 | 100
2019-05-25 04:00 | 100 | 100
2019-05-25 04:30 | 101 | 101
2019-05-25 05:00 | 102 | 102
2019-05-25 05:30 | 105 | 105
2019-05-25 06:00 | 109 | 109
2019-05-25 06:30 | 115 | 115
2019-05-25 07:00 | 120 | 120
2019-05-25 07:30 | 124 | 124
2019-05-25 08:00 | 124 | 123
2019-05-25 08:30 | 122 | 121
2019-05-25 09:00 | 117 | 117
2019-05-25 09:30 | 112 | 112
2019-05-25 10:00 | 108 | 108
2019-05-25 10:30 | 103 | 102
2019-05-25 11:00 | 100 | 99
2019-05-25 11:30 | 96 | 96
2019-05-25 12:00 | 95 | 94
2019-05-25 12:30 | 99 | 99
2019-05-25 13:00 | 102 | 102
2019-05-25 13:30 | 107 | 106
2019-05-25 14:00 | 105 | 105
2019-05-25 14:30 | 111 | 111
2019-05-25 15:00 | 118 | 117
2019-05-25 15:30 | 125 | 124
2019-05-25 16:00 | 132 | 131
2019-05-25 16:30 | 141 | 139
2019-05-25 17:00 | 150 | 149
2019-05-25 17:30 | 159 | 157
2019-05-25 18:00 | 161 | 160
2019-05-25 18:30 | 158 | 158
2019-05-25 19:00 | 157 | 157
2019-05-25 19:30 | 153 | 152
2019-05-25 20:00 | 152 | 151
2019-05-25 20:30 | 151 | 151
2019-05-25 21:00 | 145 | 145
2019-05-25 21:30 | 140 | 140
2019-05-25 22:00 | 137 | 137
2019-05-25 22:30 | 137 | 137
2019-05-25 23:00 | 136 | 136
2019-05-25 23:30 | 130 | 130
2019-05-26 | 122 | 122
2019-05-26 00:30 | 113 | 113
2019-05-26 01:00 | 106 | 106
2019-05-26 01:30 | 102 | 102
2019-05-26 02:00 | 98 | 98
2019-05-26 02:30 | 96 | 96
2019-05-26 03:00 | 95 | 95
2019-05-26 03:30 | 94 | 94
2019-05-26 04:00 | 94 | 94
2019-05-26 04:30 | 94 | 94
2019-05-26 05:00 | 95 | 95
2019-05-26 05:30 | 97 | 97
2019-05-26 06:00 | 100 | 100
2019-05-26 06:30 | 105 | 105
2019-05-26 07:00 | 108 | 108
2019-05-26 07:30 | 113 | 113
2019-05-26 08:00 | 117 | 117
2019-05-26 08:30 | 127 | 126
2019-05-26 09:00 | 124 | 124
2019-05-26 09:30 | 119 | 119
2019-05-26 10:00 | 111 | 111
2019-05-26 10:30 | 105 | 105
2019-05-26 11:00 | 100 | 100
2019-05-26 11:30 | 97 | 97
2019-05-26 12:00 | 96 | 95
2019-05-26 12:30 | 95 | 95
2019-05-26 13:00 | 92 | 92
2019-05-26 13:30 | 101 | 101
2019-05-26 14:00 | 117 | 117
2019-05-26 14:30 | 128 | 127
2019-05-26 15:00 | 131 | 130
2019-05-26 15:30 | 128 | 127
2019-05-26 16:00 | 131 | 130
2019-05-26 16:30 | 143 | 143
2019-05-26 17:00 | 154 | 154
2019-05-26 17:30 | 164 | 164
2019-05-26 18:00 | 170 | 170
2019-05-26 18:30 | 167 | 167
2019-05-26 19:00 | 166 | 166
2019-05-26 19:30 | 160 | 160
2019-05-26 20:00 | 158 | 158
2019-05-26 20:30 | 157 | 157
2019-05-26 21:00 | 149 | 149
2019-05-26 21:30 | 142 | 142
2019-05-26 22:00 | 138 | 138
2019-05-26 22:30 | 136 | 136
2019-05-26 23:00 | 135 | 135
2019-05-26 23:30 | 128 | 128
2019-05-27 | 119 | 119
2019-05-27 00:30 | 111 | 111
2019-05-27 01:00 | 105 | 105
2019-05-27 01:30 | 101 | 101
2019-05-27 02:00 | 98 | 98
2019-05-27 02:30 | 96 | 96
2019-05-27 03:00 | 96 | 96
2019-05-27 03:30 | 97 | 97
2019-05-27 04:00 | 97 | 97
2019-05-27 04:30 | 101 | 101
2019-05-27 05:00 | 107 | 106
2019-05-27 05:30 | 118 | 116
2019-05-27 06:00 | 128 | 127
2019-05-27 06:30 | 143 | 141
2019-05-27 07:00 | 155 | 154
2019-05-27 07:30 | 162 | 161
2019-05-27 08:00 | 159 | 157
2019-05-27 08:30 | 148 | 147
2019-05-27 09:00 | 140 | 139
2019-05-27 09:30 | 134 | 133
2019-05-27 10:00 | 127 | 126
2019-05-27 10:30 | 125 | 124
2019-05-27 11:00 | 121 | 120
2019-05-27 11:30 | 119 | 118
2019-05-27 12:00 | 117 | 115
2019-05-27 12:30 | 117 | 115
2019-05-27 13:00 | 119 | 117
2019-05-27 13:30 | 123 | 122
2019-05-27 14:00 | 128 | 127
2019-05-27 14:30 | 135 | 133
2019-05-27 15:00 | 140 | 138
2019-05-27 15:30 | 147 | 146
2019-05-27 16:00 | 157 | 156
2019-05-27 16:30 | 166 | 165
2019-05-27 17:00 | 177 | 177
2019-05-27 17:30 | 186 | 186
2019-05-27 18:00 | 190 | 190
2019-05-27 18:30 | 187 | 187
2019-05-27 19:00 | 184 | 184
2019-05-27 19:30 | 180 | 180
2019-05-27 20:00 | 176 | 176
2019-05-27 20:30 | 174 | 174
2019-05-27 21:00 | 166 | 166
2019-05-27 21:30 | 158 | 158
2019-05-27 22:00 | 150 | 149
2019-05-27 22:30 | 146 | 145
2019-05-27 23:00 | 143 | 142
2019-05-27 23:30 | 135 | 134
2019-05-28 | 125 | 124
2019-05-28 00:30 | 114 | 114
2019-05-28 01:00 | 109 | 109
2019-05-28 01:30 | 106 | 106
2019-05-28 02:00 | 103 | 103
2019-05-28 02:30 | 101 | 100
2019-05-28 03:00 | 101 | 100
2019-05-28 03:30 | 102 | 101
2019-05-28 04:00 | 102 | 102
2019-05-28 04:30 | 106 | 105
2019-05-28 05:00 | 111 | 110
2019-05-28 05:30 | 122 | 120
2019-05-28 06:00 | 133 | 130
2019-05-28 06:30 | 149 | 147
2019-05-28 07:00 | 163 | 161
2019-05-28 07:30 | 170 | 170
2019-05-28 08:00 | 164 | 164
2019-05-28 08:30 | 152 | 152
2019-05-28 09:00 | 140 | 140
2019-05-28 09:30 | 132 | 132
2019-05-28 10:00 | 124 | 124
2019-05-28 10:30 | 118 | 118
2019-05-28 11:00 | 113 | 113
2019-05-28 11:30 | 109 | 109
2019-05-28 12:00 | 108 | 108
2019-05-28 12:30 | 109 | 108
2019-05-28 13:00 | 110 | 110
2019-05-28 13:30 | 113 | 113
2019-05-28 14:00 | 119 | 119
2019-05-28 14:30 | 125 | 125
2019-05-28 15:00 | 132 | 132
2019-05-28 15:30 | 141 | 141
2019-05-28 16:00 | 151 | 151
2019-05-28 16:30 | 163 | 163
2019-05-28 17:00 | 175 | 174
2019-05-28 17:30 | 186 | 186
2019-05-28 18:00 | 192 | 192
2019-05-28 18:30 | 190 | 189
2019-05-28 19:00 | 190 | 190
2019-05-28 19:30 | 186 | 186
2019-05-28 20:00 | 184 | 184
2019-05-28 20:30 | 182 | 181
2019-05-28 21:00 | 175 | 173
2019-05-28 21:30 | 166 | 165
2019-05-28 22:00 | 159 | 158
2019-05-28 22:30 | 153 | 152
2019-05-28 23:00 | 149 | 149
2019-05-28 23:30 | 141 | 141
2019-05-29 | 131 | 131
2019-05-29 00:30 | 121 | 121
2019-05-29 01:00 | 115 | 114
2019-05-29 01:30 | 110 | 110
2019-05-29 02:00 | 107 | 107
2019-05-29 02:30 | 105 | 105
2019-05-29 03:00 | 104 | 104
2019-05-29 03:30 | 105 | 105
2019-05-29 04:00 | 105 | 105
2019-05-29 04:30 | 110 | 109
2019-05-29 05:00 | 116 | 115
2019-05-29 05:30 | 126 | 126
2019-05-29 06:00 | 139 | 137
2019-05-29 06:30 | 157 | 154
2019-05-29 07:00 | 174 | 171
2019-05-29 07:30 | 182 | 181
2019-05-29 08:00 | 174 | 174
2019-05-29 08:30 | 161 | 161
2019-05-29 09:00 | 146 | 146
2019-05-29 09:30 | 135 | 135
2019-05-29 10:00 | 124 | 124
2019-05-29 10:30 | 117 | 116
2019-05-29 11:00 | 111 | 110
2019-05-29 11:30 | 107 | 106
2019-05-29 12:00 | 106 | 105
2019-05-29 12:30 | 105 | 104
2019-05-29 13:00 | 108 | 106
2019-05-29 13:30 | 110 | 109
2019-05-29 14:00 | 115 | 114
2019-05-29 14:30 | 123 | 121
2019-05-29 15:00 | 130 | 128
2019-05-29 15:30 | 140 | 139
2019-05-29 16:00 | 152 | 151
2019-05-29 16:30 | 164 | 164
2019-05-29 17:00 | 176 | 176
2019-05-29 17:30 | 186 | 185
2019-05-29 18:00 | 193 | 191
2019-05-29 18:30 | 192 | 190
2019-05-29 19:00 | 192 | 190
2019-05-29 19:30 | 188 | 187
2019-05-29 20:00 | 186 | 184
2019-05-29 20:30 | 185 | 184
2019-05-29 21:00 | 178 | 177
2019-05-29 21:30 | 169 | 169
2019-05-29 22:00 | 162 | 161
2019-05-29 22:30 | 157 | 156
2019-05-29 23:00 | 153 | 153
2019-05-29 23:30 | 144 | 144
2019-05-30 | 133 | 133
2019-05-30 00:30 | 123 | 123
2019-05-30 01:00 | 116 | 116
2019-05-30 01:30 | 112 | 112
2019-05-30 02:00 | 109 | 109
2019-05-30 02:30 | 107 | 107
2019-05-30 03:00 | 106 | 106
2019-05-30 03:30 | 107 | 107
2019-05-30 04:00 | 108 | 108
2019-05-30 04:30 | 112 | 112
2019-05-30 05:00 | 117 | 117
2019-05-30 05:30 | 129 | 129
2019-05-30 06:00 | 141 | 140
2019-05-30 06:30 | 160 | 159
2019-05-30 07:00 | 177 | 176
2019-05-30 07:30 | 186 | 185
2019-05-30 08:00 | 179 | 178
2019-05-30 08:30 | 164 | 164
2019-05-30 09:00 | 149 | 149
2019-05-30 09:30 | 137 | 137
2019-05-30 10:00 | 126 | 125
2019-05-30 10:30 | 119 | 118
2019-05-30 11:00 | 114 | 113
2019-05-30 11:30 | 109 | 109
2019-05-30 12:00 | 108 | 107
2019-05-30 12:30 | 108 | 107
2019-05-30 13:00 | 110 | 109
2019-05-30 13:30 | 113 | 113
2019-05-30 14:00 | 118 | 118
2019-05-30 14:30 | 124 | 124
2019-05-30 15:00 | 131 | 131
2019-05-30 15:30 | 140 | 139
2019-05-30 16:00 | 151 | 151
2019-05-30 16:30 | 161 | 161
2019-05-30 17:00 | 174 | 173
2019-05-30 17:30 | 185 | 184
2019-05-30 18:00 | 194 | 194
2019-05-30 18:30 | 193 | 193
2019-05-30 19:00 | 195 | 195
2019-05-30 19:30 | 192 | 192
2019-05-30 20:00 | 191 | 191
2019-05-30 20:30 | 191 | 191
2019-05-30 21:00 | 184 | 184
2019-05-30 21:30 | 175 | 175
2019-05-30 22:00 | 167 | 167
2019-05-30 22:30 | 162 | 161
2019-05-30 23:00 | 155 | 155
2019-05-30 23:30 | 145 | 145
2019-05-31 | 135 | 135
2019-05-31 00:30 | 124 | 124
2019-05-31 01:00 | 118 | 118
2019-05-31 01:30 | 114 | 114
2019-05-31 02:00 | 111 | 111
2019-05-31 02:30 | 110 | 109
2019-05-31 03:00 | 109 | 109
2019-05-31 03:30 | 110 | 109
2019-05-31 04:00 | 110 | 110
2019-05-31 04:30 | 115 | 115
2019-05-31 05:00 | 122 | 122
2019-05-31 05:30 | 135 | 134
2019-05-31 06:00 | 148 | 148
2019-05-31 06:30 | 170 | 168
2019-05-31 07:00 | 189 | 187
2019-05-31 07:30 | 199 | 198
2019-05-31 08:00 | 192 | 191
2019-05-31 08:30 | 172 | 172
2019-05-31 09:00 | 156 | 156
2019-05-31 09:30 | 143 | 143
2019-05-31 10:00 | 135 | 135
2019-05-31 10:30 | 126 | 126
2019-05-31 11:00 | 117 | 116
2019-05-31 11:30 | 111 | 110
2019-05-31 12:00 | 108 | 107
2019-05-31 12:30 | 107 | 106
2019-05-31 13:00 | 109 | 108
2019-05-31 13:30 | 114 | 114
2019-05-31 14:00 | 113 | 113
2019-05-31 14:30 | 122 | 122
2019-05-31 15:00 | 131 | 131
2019-05-31 15:30 | 139 | 139
2019-05-31 16:00 | 155 | 154
2019-05-31 16:30 | 167 | 167
2019-05-31 17:00 | 182 | 181
2019-05-31 17:30 | 194 | 193
2019-05-31 18:00 | 202 | 200
2019-05-31 18:30 | 201 | 199
2019-05-31 19:00 | 203 | 201
2019-05-31 19:30 | 201 | 199
2019-05-31 20:00 | 202 | 199
2019-05-31 20:30 | 202 | 199
2019-05-31 21:00 | 196 | 194
2019-05-31 21:30 | 188 | 186
2019-05-31 22:00 | 181 | 179
2019-05-31 22:30 | 176 | 175
2019-05-31 23:00 | 170 | 169
2019-05-31 23:30 | 159 | 159
2019-06-01 | 147 | 145
2019-06-01 00:30 | 135 | 133
2019-06-01 01:00 | 127 | 126
2019-06-01 01:30 | 122 | 120
2019-06-01 02:00 | 119 | 116
2019-06-01 02:30 | 117 | 113
2019-06-01 03:00 | 116 | 112
2019-06-01 03:30 | 116 | 112
2019-06-01 04:00 | 116 | 112
2019-06-01 04:30 | 118 | 114
2019-06-01 05:00 | 121 | 117
2019-06-01 05:30 | 127 | 122
2019-06-01 06:00 | 133 | 127
2019-06-01 06:30 | 143 | 137
2019-06-01 07:00 | 149 | 146
2019-06-01 07:30 | 155 | 154
2019-06-01 08:00 | 156 | 155
2019-06-01 08:30 | 151 | 150
2019-06-01 09:00 | 143 | 143
2019-06-01 09:30 | 132 | 131
2019-06-01 10:00 | 121 | 121
2019-06-01 10:30 | 112 | 112
2019-06-01 11:00 | 104 | 104
2019-06-01 11:30 | 100 | 100
2019-06-01 12:00 | 97 | 97
2019-06-01 12:30 | 98 | 98
2019-06-01 13:00 | 105 | 105
2019-06-01 13:30 | 115 | 115
2019-06-01 14:00 | 124 | 124
2019-06-01 14:30 | 124 | 124
2019-06-01 15:00 | 127 | 127
2019-06-01 15:30 | 134 | 134
2019-06-01 16:00 | 140 | 140
2019-06-01 16:30 | 149 | 148
2019-06-01 17:00 | 161 | 160
2019-06-01 17:30 | 170 | 168
2019-06-01 18:00 | 171 | 170
2019-06-01 18:30 | 169 | 168
2019-06-01 19:00 | 168 | 167
2019-06-01 19:30 | 165 | 164
2019-06-01 20:00 | 163 | 162
2019-06-01 20:30 | 162 | 161
2019-06-01 21:00 | 155 | 155
2019-06-01 21:30 | 150 | 150
2019-06-01 22:00 | 146 | 146
2019-06-01 22:30 | 144 | 143
2019-06-01 23:00 | 142 | 142
2019-06-01 23:30 | 135 | 135
2019-06-02 | 126 | 126
2019-06-02 00:30 | 116 | 116
2019-06-02 01:00 | 109 | 109
2019-06-02 01:30 | 104 | 103
2019-06-02 02:00 | 99 | 99
2019-06-02 02:30 | 96 | 96
2019-06-02 03:00 | 94 | 94
2019-06-02 03:30 | 93 | 93
2019-06-02 04:00 | 93 | 93
2019-06-02 04:30 | 93 | 93
2019-06-02 05:00 | 94 | 94
2019-06-02 05:30 | 97 | 97
2019-06-02 06:00 | 101 | 101
2019-06-02 06:30 | 105 | 105
2019-06-02 07:00 | 108 | 108
2019-06-02 07:30 | 113 | 112
2019-06-02 08:00 | 115 | 115
2019-06-02 08:30 | 115 | 114
2019-06-02 09:00 | 117 | 116
2019-06-02 09:30 | 119 | 118
2019-06-02 10:00 | 124 | 124
2019-06-02 10:30 | 126 | 125
2019-06-02 11:00 | 109 | 108
2019-06-02 11:30 | 104 | 103
2019-06-02 12:00 | 107 | 106
2019-06-02 12:30 | 110 | 110
2019-06-02 13:00 | 116 | 115
2019-06-02 13:30 | 128 | 127
2019-06-02 14:00 | 133 | 132
2019-06-02 14:30 | 129 | 128
2019-06-02 15:00 | 123 | 122
2019-06-02 15:30 | 124 | 123
2019-06-02 16:00 | 132 | 131
2019-06-02 16:30 | 144 | 143
2019-06-02 17:00 | 158 | 157
2019-06-02 17:30 | 171 | 170
2019-06-02 18:00 | 176 | 174
2019-06-02 18:30 | 175 | 173
2019-06-02 19:00 | 174 | 172
2019-06-02 19:30 | 169 | 168
2019-06-02 20:00 | 167 | 166
2019-06-02 20:30 | 166 | 165
2019-06-02 21:00 | 158 | 157
2019-06-02 21:30 | 152 | 151
2019-06-02 22:00 | 146 | 146
2019-06-02 22:30 | 142 | 142
2019-06-02 23:00 | 139 | 139
2019-06-02 23:30 | 132 | 132
2019-06-03 | 123 | 123
2019-06-03 00:30 | 114 | 114
2019-06-03 01:00 | 107 | 107
2019-06-03 01:30 | 103 | 103
2019-06-03 02:00 | 100 | 100
2019-06-03 02:30 | 99 | 99
2019-06-03 03:00 | 98 | 98
2019-06-03 03:30 | 98 | 98
2019-06-03 04:00 | 99 | 99
2019-06-03 04:30 | 102 | 102
2019-06-03 05:00 | 107 | 107
2019-06-03 05:30 | 118 | 117
2019-06-03 06:00 | 129 | 128
2019-06-03 06:30 | 147 | 146
2019-06-03 07:00 | 161 | 161
2019-06-03 07:30 | 169 | 169
2019-06-03 08:00 | 167 | 167
2019-06-03 08:30 | 158 | 158
2019-06-03 09:00 | 149 | 149
2019-06-03 09:30 | 140 | 140
2019-06-03 10:00 | 131 | 131
2019-06-03 10:30 | 124 | 124
2019-06-03 11:00 | 119 | 119
2019-06-03 11:30 | 122 | 122
2019-06-03 12:00 | 121 | 121
2019-06-03 12:30 | 120 | 120
2019-06-03 13:00 | 119 | 119
2019-06-03 13:30 | 123 | 123
2019-06-03 14:00 | 127 | 127
2019-06-03 14:30 | 130 | 130
2019-06-03 15:00 | 135 | 135
2019-06-03 15:30 | 142 | 142
2019-06-03 16:00 | 155 | 154
2019-06-03 16:30 | 167 | 167
2019-06-03 17:00 | 180 | 180
2019-06-03 17:30 | 192 | 192
2019-06-03 18:00 | 198 | 197
2019-06-03 18:30 | 196 | 196
2019-06-03 19:00 | 196 | 195
2019-06-03 19:30 | 190 | 189
2019-06-03 20:00 | 188 | 188
2019-06-03 20:30 | 187 | 186
2019-06-03 21:00 | 180 | 179
2019-06-03 21:30 | 172 | 172
2019-06-03 22:00 | 164 | 164
2019-06-03 22:30 | 160 | 160
2019-06-03 23:00 | 156 | 156
2019-06-03 23:30 | 146 | 146
2019-06-04 | 135 | 135
2019-06-04 00:30 | 125 | 125
2019-06-04 01:00 | 118 | 118
2019-06-04 01:30 | 114 | 114
2019-06-04 02:00 | 110 | 110
2019-06-04 02:30 | 108 | 108
2019-06-04 03:00 | 108 | 108
2019-06-04 03:30 | 108 | 108
2019-06-04 04:00 | 109 | 109
2019-06-04 04:30 | 114 | 113
2019-06-04 05:00 | 121 | 120
2019-06-04 05:30 | 134 | 132
2019-06-04 06:00 | 148 | 146
2019-06-04 06:30 | 168 | 167
2019-06-04 07:00 | 186 | 185
2019-06-04 07:30 | 195 | 195
2019-06-04 08:00 | 189 | 189
2019-06-04 08:30 | 174 | 174
2019-06-04 09:00 | 158 | 158
2019-06-04 09:30 | 144 | 144
2019-06-04 10:00 | 134 | 134
2019-06-04 10:30 | 130 | 130
2019-06-04 11:00 | 125 | 125
2019-06-04 11:30 | 120 | 120
2019-06-04 12:00 | 118 | 118
2019-06-04 12:30 | 118 | 118
2019-06-04 13:00 | 118 | 118
2019-06-04 13:30 | 120 | 120
2019-06-04 14:00 | 122 | 122
2019-06-04 14:30 | 128 | 128
2019-06-04 15:00 | 133 | 133
2019-06-04 15:30 | 143 | 143
2019-06-04 16:00 | 160 | 160
2019-06-04 16:30 | 178 | 177
2019-06-04 17:00 | 197 | 197
2019-06-04 17:30 | 216 | 215
2019-06-04 18:00 | 217 | 216
2019-06-04 18:30 | 217 | 217
2019-06-04 19:00 | 221 | 221
2019-06-04 19:30 | 222 | 221
2019-06-04 20:00 | 220 | 220
2019-06-04 20:30 | 217 | 217
2019-06-04 21:00 | 207 | 207
2019-06-04 21:30 | 196 | 196
2019-06-04 22:00 | 185 | 185
2019-06-04 22:30 | 177 | 177
2019-06-04 23:00 | 169 | 168
2019-06-04 23:30 | 156 | 156
2019-06-05 | 145 | 145
2019-06-05 00:30 | 134 | 134
2019-06-05 01:00 | 126 | 126
2019-06-05 01:30 | 121 | 121
2019-06-05 02:00 | 117 | 117
2019-06-05 02:30 | 115 | 114
2019-06-05 03:00 | 114 | 113
2019-06-05 03:30 | 114 | 113
2019-06-05 04:00 | 115 | 114
2019-06-05 04:30 | 119 | 118
2019-06-05 05:00 | 125 | 125
2019-06-05 05:30 | 137 | 137
2019-06-05 06:00 | 151 | 150
2019-06-05 06:30 | 174 | 174
2019-06-05 07:00 | 192 | 192
2019-06-05 07:30 | 199 | 199
2019-06-05 08:00 | 191 | 190
2019-06-05 08:30 | 175 | 175
2019-06-05 09:00 | 159 | 159
2019-06-05 09:30 | 146 | 146
2019-06-05 10:00 | 137 | 137
2019-06-05 10:30 | 129 | 129
2019-06-05 11:00 | 122 | 122
2019-06-05 11:30 | 116 | 116
2019-06-05 12:00 | 115 | 115
2019-06-05 12:30 | 116 | 116
2019-06-05 13:00 | 119 | 118
2019-06-05 13:30 | 125 | 124
2019-06-05 14:00 | 131 | 131
2019-06-05 14:30 | 138 | 138
2019-06-05 15:00 | 138 | 138
2019-06-05 15:30 | 143 | 143
2019-06-05 16:00 | 154 | 153
2019-06-05 16:30 | 164 | 164
2019-06-05 17:00 | 176 | 176
2019-06-05 17:30 | 193 | 193
2019-06-05 18:00 | 201 | 201
2019-06-05 18:30 | 201 | 201
2019-06-05 19:00 | 202 | 202
2019-06-05 19:30 | 198 | 198
2019-06-05 20:00 | 196 | 196
2019-06-05 20:30 | 194 | 194
2019-06-05 21:00 | 187 | 187
2019-06-05 21:30 | 181 | 181
2019-06-05 22:00 | 173 | 173
2019-06-05 22:30 | 166 | 166
2019-06-05 23:00 | 163 | 163
2019-06-05 23:30 | 151 | 151
2019-06-06 | 140 | 140
2019-06-06 00:30 | 130 | 130
2019-06-06 01:00 | 122 | 122
2019-06-06 01:30 | 117 | 117
2019-06-06 02:00 | 113 | 113
2019-06-06 02:30 | 111 | 111
2019-06-06 03:00 | 110 | 110
2019-06-06 03:30 | 110 | 110
2019-06-06 04:00 | 111 | 111
2019-06-06 04:30 | 115 | 115
2019-06-06 05:00 | 121 | 121
2019-06-06 05:30 | 133 | 133
2019-06-06 06:00 | 146 | 146
2019-06-06 06:30 | 166 | 166
2019-06-06 07:00 | 182 | 182
2019-06-06 07:30 | 192 | 191
2019-06-06 08:00 | 185 | 184
2019-06-06 08:30 | 169 | 168
2019-06-06 09:00 | 154 | 153
2019-06-06 09:30 | 144 | 142
2019-06-06 10:00 | 132 | 131
2019-06-06 10:30 | 125 | 124
2019-06-06 11:00 | 124 | 123
2019-06-06 11:30 | 125 | 124
2019-06-06 12:00 | 120 | 120
2019-06-06 12:30 | 122 | 122
2019-06-06 13:00 | 127 | 126
2019-06-06 13:30 | 126 | 126
2019-06-06 14:00 | 131 | 131
2019-06-06 14:30 | 137 | 137
2019-06-06 15:00 | 144 | 144
2019-06-06 15:30 | 151 | 150
2019-06-06 16:00 | 159 | 159
2019-06-06 16:30 | 168 | 168
2019-06-06 17:00 | 181 | 181
2019-06-06 17:30 | 194 | 194
2019-06-06 18:00 | 200 | 200
2019-06-06 18:30 | 200 | 200
2019-06-06 19:00 | 202 | 202
2019-06-06 19:30 | 200 | 200
2019-06-06 20:00 | 198 | 198
2019-06-06 20:30 | 199 | 199
2019-06-06 21:00 | 195 | 195
2019-06-06 21:30 | 185 | 185
2019-06-06 22:00 | 176 | 175
2019-06-06 22:30 | 167 | 166
2019-06-06 23:00 | 161 | 161
2019-06-06 23:30 | 151 | 151
2019-06-07 | 140 | 140
2019-06-07 00:30 | 129 | 129
2019-06-07 01:00 | 122 | 122
2019-06-07 01:30 | 117 | 117
2019-06-07 02:00 | 114 | 114
2019-06-07 02:30 | 111 | 111
2019-06-07 03:00 | 110 | 110
2019-06-07 03:30 | 110 | 109
2019-06-07 04:00 | 111 | 111
2019-06-07 04:30 | 114 | 114
2019-06-07 05:00 | 120 | 120
2019-06-07 05:30 | 132 | 131
2019-06-07 06:00 | 144 | 144
2019-06-07 06:30 | 164 | 163
2019-06-07 07:00 | 180 | 180
2019-06-07 07:30 | 189 | 189
2019-06-07 08:00 | 186 | 186
2019-06-07 08:30 | 174 | 174
2019-06-07 09:00 | 157 | 157
2019-06-07 09:30 | 145 | 145
2019-06-07 10:00 | 136 | 136
2019-06-07 10:30 | 131 | 130
2019-06-07 11:00 | 129 | 129
2019-06-07 11:30 | 129 | 129
2019-06-07 12:00 | 131 | 130
2019-06-07 12:30 | 140 | 140
2019-06-07 13:00 | 153 | 153
2019-06-07 13:30 | 153 | 153
2019-06-07 14:00 | 153 | 153
2019-06-07 14:30 | 155 | 155
2019-06-07 15:00 | 155 | 155
2019-06-07 15:30 | 158 | 158
2019-06-07 16:00 | 163 | 163
2019-06-07 16:30 | 169 | 169
2019-06-07 17:00 | 179 | 179
2019-06-07 17:30 | 190 | 189
2019-06-07 18:00 | 193 | 193
2019-06-07 18:30 | 192 | 192
2019-06-07 19:00 | 196 | 196
2019-06-07 19:30 | 193 | 193
2019-06-07 20:00 | 190 | 190
2019-06-07 20:30 | 186 | 186
2019-06-07 21:00 | 178 | 177
2019-06-07 21:30 | 172 | 171
2019-06-07 22:00 | 166 | 165
2019-06-07 22:30 | 161 | 161
2019-06-07 23:00 | 156 | 156
2019-06-07 23:30 | 147 | 147
2019-06-08 | 136 | 136
2019-06-08 00:30 | 126 | 126
2019-06-08 01:00 | 120 | 120
2019-06-08 01:30 | 115 | 115
2019-06-08 02:00 | 110 | 110
2019-06-08 02:30 | 108 | 108
2019-06-08 03:00 | 106 | 106
2019-06-08 03:30 | 105 | 105
2019-06-08 04:00 | 104 | 104
2019-06-08 04:30 | 104 | 104
2019-06-08 05:00 | 106 | 106
2019-06-08 05:30 | 109 | 109
2019-06-08 06:00 | 114 | 114
2019-06-08 06:30 | 122 | 121
2019-06-08 07:00 | 127 | 127
2019-06-08 07:30 | 135 | 134
2019-06-08 08:00 | 139 | 138
2019-06-08 08:30 | 146 | 145
2019-06-08 09:00 | 147 | 145
2019-06-08 09:30 | 146 | 145
2019-06-08 10:00 | 149 | 147
2019-06-08 10:30 | 150 | 149
2019-06-08 11:00 | 150 | 149
2019-06-08 11:30 | 150 | 149
2019-06-08 12:00 | 151 | 151
2019-06-08 12:30 | 150 | 150
2019-06-08 13:00 | 146 | 146
2019-06-08 13:30 | 149 | 149
2019-06-08 14:00 | 151 | 150
2019-06-08 14:30 | 153 | 152
2019-06-08 15:00 | 155 | 154
2019-06-08 15:30 | 158 | 157
2019-06-08 16:00 | 161 | 160
2019-06-08 16:30 | 164 | 164
2019-06-08 17:00 | 173 | 172
2019-06-08 17:30 | 181 | 181
2019-06-08 18:00 | 182 | 182
2019-06-08 18:30 | 181 | 181
2019-06-08 19:00 | 179 | 179
2019-06-08 19:30 | 174 | 174
2019-06-08 20:00 | 172 | 172
2019-06-08 20:30 | 171 | 170
2019-06-08 21:00 | 164 | 164
2019-06-08 21:30 | 159 | 159
2019-06-08 22:00 | 153 | 153
2019-06-08 22:30 | 150 | 149
2019-06-08 23:00 | 148 | 148
2019-06-08 23:30 | 140 | 140
2019-06-09 | 131 | 131
2019-06-09 00:30 | 121 | 120
2019-06-09 01:00 | 114 | 114
2019-06-09 01:30 | 108 | 108
2019-06-09 02:00 | 103 | 103
2019-06-09 02:30 | 100 | 100
2019-06-09 03:00 | 99 | 99
2019-06-09 03:30 | 98 | 98
2019-06-09 04:00 | 99 | 98
2019-06-09 04:30 | 98 | 98
2019-06-09 05:00 | 99 | 98
2019-06-09 05:30 | 101 | 101
2019-06-09 06:00 | 105 | 104
2019-06-09 06:30 | 110 | 109
2019-06-09 07:00 | 114 | 114
2019-06-09 07:30 | 119 | 119
2019-06-09 08:00 | 119 | 119
2019-06-09 08:30 | 120 | 120
2019-06-09 09:00 | 121 | 121
2019-06-09 09:30 | 119 | 119
2019-06-09 10:00 | 111 | 111
2019-06-09 10:30 | 103 | 103
2019-06-09 11:00 | 97 | 96
2019-06-09 11:30 | 93 | 92
2019-06-09 12:00 | 91 | 90
2019-06-09 12:30 | 92 | 92
2019-06-09 13:00 | 99 | 99
2019-06-09 13:30 | 106 | 106
2019-06-09 14:00 | 112 | 112
2019-06-09 14:30 | 114 | 114
2019-06-09 15:00 | 117 | 117
2019-06-09 15:30 | 123 | 123
2019-06-09 16:00 | 134 | 134
2019-06-09 16:30 | 145 | 145
2019-06-09 17:00 | 157 | 157
2019-06-09 17:30 | 169 | 169
2019-06-09 18:00 | 176 | 176
2019-06-09 18:30 | 176 | 175
2019-06-09 19:00 | 174 | 174
2019-06-09 19:30 | 170 | 170
2019-06-09 20:00 | 169 | 168
2019-06-09 20:30 | 168 | 168
2019-06-09 21:00 | 162 | 162
2019-06-09 21:30 | 155 | 155
2019-06-09 22:00 | 150 | 150
2019-06-09 22:30 | 146 | 146
2019-06-09 23:00 | 144 | 144
2019-06-09 23:30 | 136 | 136
2019-06-10 | 127 | 126
2019-06-10 00:30 | 118 | 117
2019-06-10 01:00 | 111 | 111
2019-06-10 01:30 | 107 | 107
2019-06-10 02:00 | 103 | 103
2019-06-10 02:30 | 101 | 100
2019-06-10 03:00 | 99 | 99
2019-06-10 03:30 | 99 | 99
2019-06-10 04:00 | 100 | 100
2019-06-10 04:30 | 104 | 104
2019-06-10 05:00 | 111 | 111
2019-06-10 05:30 | 122 | 121
2019-06-10 06:00 | 133 | 132
2019-06-10 06:30 | 151 | 150
2019-06-10 07:00 | 165 | 164
2019-06-10 07:30 | 176 | 176
2019-06-10 08:00 | 174 | 174
2019-06-10 08:30 | 162 | 162
2019-06-10 09:00 | 151 | 151
2019-06-10 09:30 | 142 | 142
2019-06-10 10:00 | 135 | 134
2019-06-10 10:30 | 128 | 128
2019-06-10 11:00 | 123 | 123
2019-06-10 11:30 | 119 | 119
2019-06-10 12:00 | 118 | 117
2019-06-10 12:30 | 118 | 118
2019-06-10 13:00 | 119 | 119
2019-06-10 13:30 | 124 | 124
2019-06-10 14:00 | 129 | 129
2019-06-10 14:30 | 135 | 135
2019-06-10 15:00 | 140 | 140
2019-06-10 15:30 | 147 | 147
2019-06-10 16:00 | 158 | 157
2019-06-10 16:30 | 169 | 168
2019-06-10 17:00 | 179 | 178
2019-06-10 17:30 | 189 | 189
2019-06-10 18:00 | 195 | 194
2019-06-10 18:30 | 192 | 191
2019-06-10 19:00 | 190 | 190
2019-06-10 19:30 | 185 | 185
2019-06-10 20:00 | 183 | 183
2019-06-10 20:30 | 181 | 181
2019-06-10 21:00 | 173 | 172
2019-06-10 21:30 | 166 | 165
2019-06-10 22:00 | 159 | 159
2019-06-10 22:30 | 154 | 153
2019-06-10 23:00 | 150 | 149
2019-06-10 23:30 | 141 | 141
2019-06-11 | 130 | 130
2019-06-11 00:30 | 121 | 121
2019-06-11 01:00 | 114 | 114
2019-06-11 01:30 | 110 | 110
2019-06-11 02:00 | 106 | 106
2019-06-11 02:30 | 105 | 104
2019-06-11 03:00 | 104 | 103
2019-06-11 03:30 | 104 | 104
2019-06-11 04:00 | 105 | 105
2019-06-11 04:30 | 108 | 108
2019-06-11 05:00 | 114 | 114
2019-06-11 05:30 | 125 | 124
2019-06-11 06:00 | 136 | 136
2019-06-11 06:30 | 154 | 152
2019-06-11 07:00 | 168 | 167
2019-06-11 07:30 | 177 | 175
2019-06-11 08:00 | 171 | 170
2019-06-11 08:30 | 157 | 156
2019-06-11 09:00 | 145 | 144
2019-06-11 09:30 | 137 | 135
2019-06-11 10:00 | 129 | 127
2019-06-11 10:30 | 123 | 121
2019-06-11 11:00 | 119 | 117
2019-06-11 11:30 | 117 | 115
2019-06-11 12:00 | 116 | 113
2019-06-11 12:30 | 117 | 114
2019-06-11 13:00 | 118 | 116
2019-06-11 13:30 | 123 | 120
2019-06-11 14:00 | 129 | 126
2019-06-11 14:30 | 135 | 132
2019-06-11 15:00 | 140 | 136
2019-06-11 15:30 | 148 | 145
2019-06-11 16:00 | 157 | 154
2019-06-11 16:30 | 166 | 164
2019-06-11 17:00 | 176 | 174
2019-06-11 17:30 | 187 | 184
2019-06-11 18:00 | 193 | 189
2019-06-11 18:30 | 189 | 187
2019-06-11 19:00 | 189 | 187
2019-06-11 19:30 | 184 | 182
2019-06-11 20:00 | 183 | 181
2019-06-11 20:30 | 181 | 179
2019-06-11 21:00 | 173 | 172
2019-06-11 21:30 | 165 | 164
2019-06-11 22:00 | 158 | 158
2019-06-11 22:30 | 154 | 153
2019-06-11 23:00 | 149 | 149
2019-06-11 23:30 | 140 | 140
2019-06-12 | 130 | 129
2019-06-12 00:30 | 120 | 120
2019-06-12 01:00 | 114 | 114
2019-06-12 01:30 | 109 | 109
2019-06-12 02:00 | 107 | 106
2019-06-12 02:30 | 105 | 104
2019-06-12 03:00 | 105 | 103
2019-06-12 03:30 | 105 | 104
2019-06-12 04:00 | 105 | 104
2019-06-12 04:30 | 109 | 108
2019-06-12 05:00 | 115 | 114
2019-06-12 05:30 | 127 | 125
2019-06-12 06:00 | 139 | 137
2019-06-12 06:30 | 157 | 153
2019-06-12 07:00 | 171 | 168
2019-06-12 07:30 | 180 | 179
2019-06-12 08:00 | 175 | 175
2019-06-12 08:30 | 163 | 163
2019-06-12 09:00 | 150 | 150
2019-06-12 09:30 | 142 | 142
2019-06-12 10:00 | 136 | 136
2019-06-12 10:30 | 129 | 129
2019-06-12 11:00 | 129 | 129
2019-06-12 11:30 | 132 | 132
2019-06-12 12:00 | 137 | 137
2019-06-12 12:30 | 136 | 136
2019-06-12 13:00 | 136 | 136
2019-06-12 13:30 | 136 | 136
2019-06-12 14:00 | 140 | 140
2019-06-12 14:30 | 145 | 145
2019-06-12 15:00 | 146 | 146
2019-06-12 15:30 | 150 | 150
2019-06-12 16:00 | 159 | 159
2019-06-12 16:30 | 168 | 168
2019-06-12 17:00 | 177 | 177
2019-06-12 17:30 | 188 | 187
2019-06-12 18:00 | 194 | 193
2019-06-12 18:30 | 192 | 191
2019-06-12 19:00 | 191 | 191
2019-06-12 19:30 | 187 | 187
2019-06-12 20:00 | 185 | 185
2019-06-12 20:30 | 184 | 184
2019-06-12 21:00 | 178 | 178
2019-06-12 21:30 | 170 | 170
2019-06-12 22:00 | 162 | 162
2019-06-12 22:30 | 156 | 155
2019-06-12 23:00 | 152 | 152
2019-06-12 23:30 | 143 | 143
2019-06-13 | 132 | 132
2019-06-13 00:30 | 122 | 122
2019-06-13 01:00 | 116 | 116
2019-06-13 01:30 | 111 | 111
2019-06-13 02:00 | 107 | 107
2019-06-13 02:30 | 105 | 105
2019-06-13 03:00 | 105 | 104
2019-06-13 03:30 | 104 | 104
2019-06-13 04:00 | 106 | 105
2019-06-13 04:30 | 109 | 108
2019-06-13 05:00 | 114 | 113
2019-06-13 05:30 | 125 | 123
2019-06-13 06:00 | 136 | 134
2019-06-13 06:30 | 151 | 151
2019-06-13 07:00 | 165 | 164
2019-06-13 07:30 | 174 | 173
2019-06-13 08:00 | 172 | 170
2019-06-13 08:30 | 161 | 160
2019-06-13 09:00 | 153 | 152
2019-06-13 09:30 | 143 | 142
2019-06-13 10:00 | 136 | 136
2019-06-13 10:30 | 138 | 137
2019-06-13 11:00 | 132 | 131
2019-06-13 11:30 | 123 | 122
2019-06-13 12:00 | 122 | 121
2019-06-13 12:30 | 135 | 134
2019-06-13 13:00 | 144 | 142
2019-06-13 13:30 | 145 | 144
2019-06-13 14:00 | 143 | 142
2019-06-13 14:30 | 145 | 144
2019-06-13 15:00 | 145 | 143
2019-06-13 15:30 | 150 | 148
2019-06-13 16:00 | 159 | 158
2019-06-13 16:30 | 166 | 165
2019-06-13 17:00 | 176 | 175
2019-06-13 17:30 | 187 | 185
2019-06-13 18:00 | 192 | 190
2019-06-13 18:30 | 191 | 189
2019-06-13 19:00 | 191 | 190
2019-06-13 19:30 | 187 | 185
2019-06-13 20:00 | 185 | 184
2019-06-13 20:30 | 184 | 183
2019-06-13 21:00 | 178 | 177
2019-06-13 21:30 | 169 | 169
2019-06-13 22:00 | 161 | 161
2019-06-13 22:30 | 156 | 156
2019-06-13 23:00 | 152 | 152
2019-06-13 23:30 | 143 | 143
2019-06-14 | 132 | 132
2019-06-14 00:30 | 121 | 121
2019-06-14 01:00 | 115 | 115
2019-06-14 01:30 | 110 | 110
2019-06-14 02:00 | 108 | 107
2019-06-14 02:30 | 105 | 105
2019-06-14 03:00 | 104 | 104
2019-06-14 03:30 | 104 | 104
2019-06-14 04:00 | 104 | 104
2019-06-14 04:30 | 108 | 108
2019-06-14 05:00 | 113 | 113
2019-06-14 05:30 | 123 | 122
2019-06-14 06:00 | 135 | 134
2019-06-14 06:30 | 151 | 150
2019-06-14 07:00 | 165 | 164
2019-06-14 07:30 | 174 | 173
2019-06-14 08:00 | 170 | 169
2019-06-14 08:30 | 163 | 161
2019-06-14 09:00 | 149 | 148
2019-06-14 09:30 | 141 | 141
2019-06-14 10:00 | 136 | 136
2019-06-14 10:30 | 128 | 128
2019-06-14 11:00 | 123 | 122
2019-06-14 11:30 | 121 | 120
2019-06-14 12:00 | 122 | 121
2019-06-14 12:30 | 121 | 120
2019-06-14 13:00 | 123 | 122
2019-06-14 13:30 | 128 | 127
2019-06-14 14:00 | 135 | 134
2019-06-14 14:30 | 138 | 137
2019-06-14 15:00 | 142 | 141
2019-06-14 15:30 | 149 | 147
2019-06-14 16:00 | 160 | 158
2019-06-14 16:30 | 168 | 166
2019-06-14 17:00 | 176 | 174
2019-06-14 17:30 | 182 | 179
2019-06-14 18:00 | 183 | 181
2019-06-14 18:30 | 178 | 177
2019-06-14 19:00 | 178 | 176
2019-06-14 19:30 | 174 | 173
2019-06-14 20:00 | 172 | 171
2019-06-14 20:30 | 171 | 170
2019-06-14 21:00 | 164 | 163
2019-06-14 21:30 | 159 | 158
2019-06-14 22:00 | 153 | 152
2019-06-14 22:30 | 150 | 149
2019-06-14 23:00 | 146 | 146
2019-06-14 23:30 | 138 | 137
2019-06-15 | 127 | 127
2019-06-15 00:30 | 117 | 117
2019-06-15 01:00 | 111 | 110
2019-06-15 01:30 | 106 | 106
2019-06-15 02:00 | 102 | 102
2019-06-15 02:30 | 100 | 100
2019-06-15 03:00 | 99 | 99
2019-06-15 03:30 | 98 | 98
2019-06-15 04:00 | 98 | 98
2019-06-15 04:30 | 99 | 99
2019-06-15 05:00 | 100 | 100
2019-06-15 05:30 | 103 | 103
2019-06-15 06:00 | 108 | 108
2019-06-15 06:30 | 115 | 115
2019-06-15 07:00 | 120 | 120
2019-06-15 07:30 | 127 | 127
2019-06-15 08:00 | 125 | 124
2019-06-15 08:30 | 124 | 123
2019-06-15 09:00 | 123 | 122
2019-06-15 09:30 | 120 | 119
2019-06-15 10:00 | 115 | 114
2019-06-15 10:30 | 113 | 112
2019-06-15 11:00 | 111 | 110
2019-06-15 11:30 | 107 | 107
2019-06-15 12:00 | 103 | 102
2019-06-15 12:30 | 101 | 101
2019-06-15 13:00 | 102 | 102
2019-06-15 13:30 | 108 | 108
2019-06-15 14:00 | 113 | 112
2019-06-15 14:30 | 118 | 117
2019-06-15 15:00 | 120 | 119
2019-06-15 15:30 | 127 | 126
2019-06-15 16:00 | 136 | 135
2019-06-15 16:30 | 144 | 143
2019-06-15 17:00 | 152 | 150
2019-06-15 17:30 | 160 | 158
2019-06-15 18:00 | 161 | 160
2019-06-15 18:30 | 159 | 159
2019-06-15 19:00 | 159 | 158
2019-06-15 19:30 | 155 | 154
2019-06-15 20:00 | 154 | 153
2019-06-15 20:30 | 153 | 152
2019-06-15 21:00 | 146 | 146
2019-06-15 21:30 | 142 | 142
2019-06-15 22:00 | 139 | 139
2019-06-15 22:30 | 138 | 138
2019-06-15 23:00 | 137 | 137
2019-06-15 23:30 | 131 | 131
2019-06-16 | 121 | 121
2019-06-16 00:30 | 112 | 112
2019-06-16 01:00 | 106 | 106
2019-06-16 01:30 | 102 | 102
2019-06-16 02:00 | 98 | 98
2019-06-16 02:30 | 95 | 95
2019-06-16 03:00 | 94 | 94
2019-06-16 03:30 | 94 | 94
2019-06-16 04:00 | 94 | 93
2019-06-16 04:30 | 94 | 94
2019-06-16 05:00 | 95 | 94
2019-06-16 05:30 | 97 | 97
2019-06-16 06:00 | 100 | 99
2019-06-16 06:30 | 104 | 104
2019-06-16 07:00 | 107 | 107
2019-06-16 07:30 | 113 | 112
2019-06-16 08:00 | 116 | 115
2019-06-16 08:30 | 118 | 118
2019-06-16 09:00 | 124 | 124
2019-06-16 09:30 | 134 | 134
2019-06-16 10:00 | 139 | 139
2019-06-16 10:30 | 140 | 140
2019-06-16 11:00 | 138 | 138
2019-06-16 11:30 | 129 | 129
2019-06-16 12:00 | 118 | 117
2019-06-16 12:30 | 123 | 123
2019-06-16 13:00 | 117 | 117
2019-06-16 13:30 | 118 | 118
2019-06-16 14:00 | 119 | 119
2019-06-16 14:30 | 127 | 127
2019-06-16 15:00 | 135 | 135
2019-06-16 15:30 | 145 | 145
2019-06-16 16:00 | 154 | 153
2019-06-16 16:30 | 158 | 158
2019-06-16 17:00 | 164 | 164
2019-06-16 17:30 | 171 | 171
2019-06-16 18:00 | 173 | 173
2019-06-16 18:30 | 172 | 172
2019-06-16 19:00 | 171 | 171
2019-06-16 19:30 | 166 | 166
2019-06-16 20:00 | 164 | 164
2019-06-16 20:30 | 163 | 163
2019-06-16 21:00 | 156 | 156
2019-06-16 21:30 | 149 | 149
2019-06-16 22:00 | 144 | 144
2019-06-16 22:30 | 140 | 140
2019-06-16 23:00 | 138 | 138
2019-06-16 23:30 | 130 | 130
2019-06-17 | 121 | 121
2019-06-17 00:30 | 112 | 112
2019-06-17 01:00 | 106 | 106
2019-06-17 01:30 | 102 | 102
2019-06-17 02:00 | 99 | 98
2019-06-17 02:30 | 97 | 96
2019-06-17 03:00 | 96 | 95
2019-06-17 03:30 | 96 | 96
2019-06-17 04:00 | 97 | 96
2019-06-17 04:30 | 100 | 100
2019-06-17 05:00 | 106 | 105
2019-06-17 05:30 | 117 | 115
2019-06-17 06:00 | 128 | 126
2019-06-17 06:30 | 145 | 143
2019-06-17 07:00 | 158 | 156
2019-06-17 07:30 | 170 | 168
2019-06-17 08:00 | 170 | 170
2019-06-17 08:30 | 158 | 158
2019-06-17 09:00 | 144 | 144
2019-06-17 09:30 | 136 | 135
2019-06-17 10:00 | 129 | 128
2019-06-17 10:30 | 122 | 122
2019-06-17 11:00 | 117 | 116
2019-06-17 11:30 | 113 | 113
2019-06-17 12:00 | 111 | 111
2019-06-17 12:30 | 112 | 111
2019-06-17 13:00 | 112 | 112
2019-06-17 13:30 | 116 | 115
2019-06-17 14:00 | 121 | 120
2019-06-17 14:30 | 126 | 126
2019-06-17 15:00 | 132 | 132
2019-06-17 15:30 | 141 | 141
2019-06-17 16:00 | 152 | 152
2019-06-17 16:30 | 162 | 162
2019-06-17 17:00 | 175 | 175
2019-06-17 17:30 | 189 | 188
2019-06-17 18:00 | 196 | 195
2019-06-17 18:30 | 194 | 194
2019-06-17 19:00 | 195 | 195
2019-06-17 19:30 | 191 | 191
2019-06-17 20:00 | 189 | 188
2019-06-17 20:30 | 189 | 188
2019-06-17 21:00 | 182 | 181
2019-06-17 21:30 | 173 | 173
2019-06-17 22:00 | 165 | 165
2019-06-17 22:30 | 160 | 160
2019-06-17 23:00 | 156 | 156
2019-06-17 23:30 | 145 | 144
2019-06-18 | 134 | 134
2019-06-18 00:30 | 124 | 124
2019-06-18 01:00 | 118 | 117
2019-06-18 01:30 | 113 | 113
2019-06-18 02:00 | 109 | 109
2019-06-18 02:30 | 107 | 107
2019-06-18 03:00 | 107 | 106
2019-06-18 03:30 | 107 | 107
2019-06-18 04:00 | 108 | 108
2019-06-18 04:30 | 111 | 111
2019-06-18 05:00 | 118 | 118
2019-06-18 05:30 | 131 | 130
2019-06-18 06:00 | 145 | 143
2019-06-18 06:30 | 166 | 164
2019-06-18 07:00 | 186 | 185
2019-06-18 07:30 | 196 | 194
2019-06-18 08:00 | 189 | 188
2019-06-18 08:30 | 173 | 173
2019-06-18 09:00 | 157 | 157
2019-06-18 09:30 | 143 | 143
2019-06-18 10:00 | 132 | 131
2019-06-18 10:30 | 125 | 124
2019-06-18 11:00 | 118 | 117
2019-06-18 11:30 | 113 | 112
2019-06-18 12:00 | 111 | 110
2019-06-18 12:30 | 111 | 110
2019-06-18 13:00 | 112 | 111
2019-06-18 13:30 | 116 | 114
2019-06-18 14:00 | 120 | 118
2019-06-18 14:30 | 126 | 124
2019-06-18 15:00 | 132 | 131
2019-06-18 15:30 | 141 | 139
2019-06-18 16:00 | 153 | 151
2019-06-18 16:30 | 163 | 161
2019-06-18 17:00 | 175 | 175
2019-06-18 17:30 | 187 | 187
2019-06-18 18:00 | 195 | 195
2019-06-18 18:30 | 193 | 193
2019-06-18 19:00 | 194 | 194
2019-06-18 19:30 | 191 | 191
2019-06-18 20:00 | 189 | 189
2019-06-18 20:30 | 188 | 188
2019-06-18 21:00 | 181 | 181
2019-06-18 21:30 | 173 | 173
2019-06-18 22:00 | 166 | 166
2019-06-18 22:30 | 161 | 161
2019-06-18 23:00 | 154 | 154
2019-06-18 23:30 | 145 | 144
2019-06-19 | 134 | 134
2019-06-19 00:30 | 124 | 124
2019-06-19 01:00 | 117 | 117
2019-06-19 01:30 | 112 | 112
2019-06-19 02:00 | 109 | 109
2019-06-19 02:30 | 107 | 106
2019-06-19 03:00 | 106 | 106
2019-06-19 03:30 | 106 | 106
2019-06-19 04:00 | 108 | 107
2019-06-19 04:30 | 112 | 112
2019-06-19 05:00 | 119 | 119
2019-06-19 05:30 | 131 | 131
2019-06-19 06:00 | 145 | 145
2019-06-19 06:30 | 165 | 164
2019-06-19 07:00 | 183 | 182
2019-06-19 07:30 | 193 | 193
2019-06-19 08:00 | 185 | 185
2019-06-19 08:30 | 171 | 171
2019-06-19 09:00 | 156 | 156
2019-06-19 09:30 | 145 | 145
2019-06-19 10:00 | 135 | 135
2019-06-19 10:30 | 128 | 128
2019-06-19 11:00 | 122 | 122
2019-06-19 11:30 | 117 | 117
2019-06-19 12:00 | 114 | 114
2019-06-19 12:30 | 114 | 114
2019-06-19 13:00 | 115 | 115
2019-06-19 13:30 | 118 | 118
2019-06-19 14:00 | 124 | 124
2019-06-19 14:30 | 131 | 131
2019-06-19 15:00 | 137 | 137
2019-06-19 15:30 | 145 | 145
2019-06-19 16:00 | 155 | 155
2019-06-19 16:30 | 164 | 164
2019-06-19 17:00 | 175 | 175
2019-06-19 17:30 | 186 | 186
2019-06-19 18:00 | 195 | 194
2019-06-19 18:30 | 194 | 194
2019-06-19 19:00 | 194 | 194
2019-06-19 19:30 | 191 | 191
2019-06-19 20:00 | 189 | 188
2019-06-19 20:30 | 187 | 187
2019-06-19 21:00 | 179 | 179
2019-06-19 21:30 | 170 | 170
2019-06-19 22:00 | 163 | 162
2019-06-19 22:30 | 157 | 157
2019-06-19 23:00 | 153 | 152
2019-06-19 23:30 | 144 | 144
2019-06-20 | 132 | 132
2019-06-20 00:30 | 123 | 123
2019-06-20 01:00 | 116 | 116
2019-06-20 01:30 | 111 | 111
2019-06-20 02:00 | 107 | 107
2019-06-20 02:30 | 106 | 106
2019-06-20 03:00 | 105 | 104
2019-06-20 03:30 | 106 | 105
2019-06-20 04:00 | 106 | 106
2019-06-20 04:30 | 109 | 109
2019-06-20 05:00 | 115 | 115
2019-06-20 05:30 | 126 | 126
2019-06-20 06:00 | 138 | 138
2019-06-20 06:30 | 156 | 155
2019-06-20 07:00 | 172 | 170
2019-06-20 07:30 | 181 | 179
2019-06-20 08:00 | 176 | 174
2019-06-20 08:30 | 166 | 165
2019-06-20 09:00 | 158 | 157
2019-06-20 09:30 | 153 | 152
2019-06-20 10:00 | 150 | 150
2019-06-20 10:30 | 148 | 147
2019-06-20 11:00 | 149 | 148
2019-06-20 11:30 | 140 | 139
2019-06-20 12:00 | 140 | 139
2019-06-20 12:30 | 144 | 143
2019-06-20 13:00 | 147 | 146
2019-06-20 13:30 | 151 | 149
2019-06-20 14:00 | 156 | 155
2019-06-20 14:30 | 160 | 159
2019-06-20 15:00 | 162 | 160
2019-06-20 15:30 | 163 | 162
2019-06-20 16:00 | 167 | 166
2019-06-20 16:30 | 173 | 172
2019-06-20 17:00 | 182 | 181
2019-06-20 17:30 | 193 | 191
2019-06-20 18:00 | 200 | 197
2019-06-20 18:30 | 199 | 197
2019-06-20 19:00 | 200 | 197
2019-06-20 19:30 | 195 | 193
2019-06-20 20:00 | 192 | 190
2019-06-20 20:30 | 191 | 189
2019-06-20 21:00 | 183 | 181
2019-06-20 21:30 | 173 | 172
2019-06-20 22:00 | 164 | 163
2019-06-20 22:30 | 159 | 158
2019-06-20 23:00 | 154 | 154
2019-06-20 23:30 | 145 | 144
2019-06-21 | 133 | 133
2019-06-21 00:30 | 122 | 122
2019-06-21 01:00 | 116 | 116
2019-06-21 01:30 | 111 | 110
2019-06-21 02:00 | 107 | 107
2019-06-21 02:30 | 105 | 105
2019-06-21 03:00 | 104 | 104
2019-06-21 03:30 | 105 | 104
2019-06-21 04:00 | 105 | 104
2019-06-21 04:30 | 107 | 107
2019-06-21 05:00 | 113 | 113
2019-06-21 05:30 | 122 | 122
2019-06-21 06:00 | 133 | 133
2019-06-21 06:30 | 150 | 150
2019-06-21 07:00 | 165 | 165
2019-06-21 07:30 | 175 | 175
2019-06-21 08:00 | 175 | 175
2019-06-21 08:30 | 169 | 169
2019-06-21 09:00 | 160 | 160
2019-06-21 09:30 | 151 | 151
2019-06-21 10:00 | 140 | 140
2019-06-21 10:30 | 128 | 128
2019-06-21 11:00 | 121 | 121
2019-06-21 11:30 | 119 | 119
2019-06-21 12:00 | 169 | 169
2019-06-21 12:30 | 174 | 174
2019-06-21 13:00 | 175 | 174
2019-06-21 13:30 | 176 | 176
2019-06-21 14:00 | 177 | 177
2019-06-21 14:30 | 184 | 183
2019-06-21 15:00 | 190 | 190
2019-06-21 15:30 | 199 | 199
2019-06-21 16:00 | 212 | 212
2019-06-21 16:30 | 225 | 225
2019-06-21 17:00 | 241 | 241
2019-06-21 17:30 | 254 | 254
2019-06-21 18:00 | 261 | 261
2019-06-21 18:30 | 260 | 260
2019-06-21 19:00 | 261 | 261
2019-06-21 19:30 | 257 | 257
2019-06-21 20:00 | 255 | 255
2019-06-21 20:30 | 255 | 255
2019-06-21 21:00 | 247 | 247
2019-06-21 21:30 | 237 | 237
2019-06-21 22:00 | 228 | 228
2019-06-21 22:30 | 224 | 223
2019-06-21 23:00 | 220 | 219
2019-06-21 23:30 | 208 | 208
2019-06-22 | 192 | 192
2019-06-22 00:30 | 178 | 177
2019-06-22 01:00 | 168 | 168
2019-06-22 01:30 | 161 | 161
2019-06-22 02:00 | 156 | 155
2019-06-22 02:30 | 153 | 152
2019-06-22 03:00 | 149 | 149
2019-06-22 03:30 | 149 | 148
2019-06-22 04:00 | 149 | 148
2019-06-22 04:30 | 151 | 150
2019-06-22 05:00 | 154 | 153
2019-06-22 05:30 | 160 | 159
2019-06-22 06:00 | 167 | 167
2019-06-22 06:30 | 179 | 179
2019-06-22 07:00 | 192 | 192
2019-06-22 07:30 | 204 | 204
2019-06-22 08:00 | 205 | 204
2019-06-22 08:30 | 201 | 201
2019-06-22 09:00 | 191 | 191
2019-06-22 09:30 | 181 | 181
2019-06-22 10:00 | 168 | 168
2019-06-22 10:30 | 156 | 156
2019-06-22 11:00 | 146 | 146
2019-06-22 11:30 | 138 | 137
2019-06-22 12:00 | 132 | 132
2019-06-22 12:30 | 127 | 127
2019-06-22 13:00 | 129 | 128
2019-06-22 13:30 | 132 | 131
2019-06-22 14:00 | 135 | 135
2019-06-22 14:30 | 146 | 146
2019-06-22 15:00 | 154 | 154
2019-06-22 15:30 | 165 | 165
2019-06-22 16:00 | 181 | 181
2019-06-22 16:30 | 199 | 199
2019-06-22 17:00 | 220 | 220
2019-06-22 17:30 | 239 | 238
2019-06-22 18:00 | 250 | 249
2019-06-22 18:30 | 252 | 251
2019-06-22 19:00 | 253 | 252
2019-06-22 19:30 | 250 | 249
2019-06-22 20:00 | 251 | 250
2019-06-22 20:30 | 252 | 251
2019-06-22 21:00 | 244 | 243
2019-06-22 21:30 | 236 | 236
2019-06-22 22:00 | 229 | 229
2019-06-22 22:30 | 225 | 225
2019-06-22 23:00 | 222 | 222
2019-06-22 23:30 | 211 | 211
2019-06-23 | 197 | 197
2019-06-23 00:30 | 182 | 182
2019-06-23 01:00 | 173 | 172
2019-06-23 01:30 | 164 | 164
2019-06-23 02:00 | 158 | 158
2019-06-23 02:30 | 154 | 154
2019-06-23 03:00 | 152 | 151
2019-06-23 03:30 | 151 | 150
2019-06-23 04:00 | 151 | 150
2019-06-23 04:30 | 151 | 150
2019-06-23 05:00 | 153 | 152
2019-06-23 05:30 | 158 | 158
2019-06-23 06:00 | 164 | 164
2019-06-23 06:30 | 174 | 173
2019-06-23 07:00 | 183 | 183
2019-06-23 07:30 | 195 | 195
2019-06-23 08:00 | 199 | 199
2019-06-23 08:30 | 198 | 198
2019-06-23 09:00 | 192 | 192
2019-06-23 09:30 | 187 | 187
2019-06-23 10:00 | 185 | 185
2019-06-23 10:30 | 176 | 176
2019-06-23 11:00 | 162 | 162
2019-06-23 11:30 | 146 | 146
2019-06-23 12:00 | 135 | 134
2019-06-23 12:30 | 131 | 130
2019-06-23 13:00 | 136 | 135
2019-06-23 13:30 | 148 | 147
2019-06-23 14:00 | 157 | 156
2019-06-23 14:30 | 160 | 160
2019-06-23 15:00 | 172 | 172
2019-06-23 15:30 | 184 | 184
2019-06-23 16:00 | 197 | 197
2019-06-23 16:30 | 212 | 212
2019-06-23 17:00 | 235 | 234
2019-06-23 17:30 | 258 | 256
2019-06-23 18:00 | 270 | 268
2019-06-23 18:30 | 270 | 268
2019-06-23 19:00 | 269 | 267
2019-06-23 19:30 | 265 | 263
2019-06-23 20:00 | 263 | 261
2019-06-23 20:30 | 259 | 258
2019-06-23 21:00 | 249 | 248
2019-06-23 21:30 | 239 | 238
2019-06-23 22:00 | 228 | 227
2019-06-23 22:30 | 220 | 220
2019-06-23 23:00 | 214 | 214
2019-06-23 23:30 | 202 | 202
2019-06-24 | 187 | 187
2019-06-24 00:30 | 173 | 173
2019-06-24 01:00 | 165 | 164
2019-06-24 01:30 | 158 | 157
2019-06-24 02:00 | 153 | 152
2019-06-24 02:30 | 150 | 149
2019-06-24 03:00 | 148 | 147
2019-06-24 03:30 | 148 | 147
2019-06-24 04:00 | 150 | 148
2019-06-24 04:30 | 156 | 155
2019-06-24 05:00 | 165 | 165
2019-06-24 05:30 | 182 | 182
2019-06-24 06:00 | 200 | 200
2019-06-24 06:30 | 228 | 228
2019-06-24 07:00 | 256 | 255
2019-06-24 07:30 | 274 | 274
2019-06-24 08:00 | 268 | 268
2019-06-24 08:30 | 249 | 249
2019-06-24 09:00 | 229 | 229
2019-06-24 09:30 | 213 | 213
2019-06-24 10:00 | 198 | 198
2019-06-24 10:30 | 184 | 183
2019-06-24 11:00 | 175 | 175
2019-06-24 11:30 | 169 | 168
2019-06-24 12:00 | 166 | 166
2019-06-24 12:30 | 168 | 167
2019-06-24 13:00 | 170 | 169
2019-06-24 13:30 | 174 | 173
2019-06-24 14:00 | 178 | 178
2019-06-24 14:30 | 187 | 187
2019-06-24 15:00 | 197 | 197
2019-06-24 15:30 | 210 | 209
2019-06-24 16:00 | 227 | 226
2019-06-24 16:30 | 246 | 246
2019-06-24 17:00 | 271 | 271
2019-06-24 17:30 | 295 | 295
2019-06-24 18:00 | 309 | 308
2019-06-24 18:30 | 308 | 308
2019-06-24 19:00 | 308 | 308
2019-06-24 19:30 | 302 | 302
2019-06-24 20:00 | 299 | 299
2019-06-24 20:30 | 296 | 296
2019-06-24 21:00 | 283 | 283
2019-06-24 21:30 | 266 | 266
2019-06-24 22:00 | 252 | 252
2019-06-24 22:30 | 242 | 241
2019-06-24 23:00 | 231 | 230
2019-06-24 23:30 | 215 | 215
2019-06-25 | 199 | 199
2019-06-25 00:30 | 184 | 184
2019-06-25 01:00 | 174 | 173
2019-06-25 01:30 | 166 | 166
2019-06-25 02:00 | 161 | 160
2019-06-25 02:30 | 157 | 156
2019-06-25 03:00 | 155 | 154
2019-06-25 03:30 | 154 | 154
2019-06-25 04:00 | 155 | 155
2019-06-25 04:30 | 160 | 160
2019-06-25 05:00 | 169 | 169
2019-06-25 05:30 | 185 | 184
2019-06-25 06:00 | 202 | 201
2019-06-25 06:30 | 229 | 228
2019-06-25 07:00 | 253 | 253
2019-06-25 07:30 | 273 | 273
2019-06-25 08:00 | 268 | 268
2019-06-25 08:30 | 254 | 254
2019-06-25 09:00 | 242 | 242
2019-06-25 09:30 | 226 | 226
2019-06-25 10:00 | 214 | 214
2019-06-25 10:30 | 214 | 213
2019-06-25 11:00 | 209 | 209
2019-06-25 11:30 | 202 | 202
2019-06-25 12:00 | 199 | 198
2019-06-25 12:30 | 217 | 217
2019-06-25 13:00 | 224 | 224
2019-06-25 13:30 | 222 | 222
2019-06-25 14:00 | 227 | 227
2019-06-25 14:30 | 227 | 227
2019-06-25 15:00 | 223 | 223
2019-06-25 15:30 | 230 | 230
2019-06-25 16:00 | 244 | 244
2019-06-25 16:30 | 259 | 259
2019-06-25 17:00 | 277 | 277
2019-06-25 17:30 | 297 | 297
2019-06-25 18:00 | 309 | 308
2019-06-25 18:30 | 307 | 306
2019-06-25 19:00 | 305 | 305
2019-06-25 19:30 | 298 | 297
2019-06-25 20:00 | 294 | 294
2019-06-25 20:30 | 291 | 290
2019-06-25 21:00 | 282 | 281
2019-06-25 21:30 | 262 | 262
2019-06-25 22:00 | 248 | 247
2019-06-25 22:30 | 238 | 238
2019-06-25 23:00 | 229 | 229
2019-06-25 23:30 | 213 | 213
2019-06-26 | 197 | 197
2019-06-26 00:30 | 182 | 182
2019-06-26 01:00 | 172 | 171
2019-06-26 01:30 | 164 | 164
2019-06-26 02:00 | 158 | 158
2019-06-26 02:30 | 154 | 154
2019-06-26 03:00 | 152 | 152
2019-06-26 03:30 | 153 | 153
2019-06-26 04:00 | 153 | 153
2019-06-26 04:30 | 158 | 158
2019-06-26 05:00 | 166 | 166
2019-06-26 05:30 | 181 | 181
2019-06-26 06:00 | 198 | 197
2019-06-26 06:30 | 225 | 225
2019-06-26 07:00 | 248 | 248
2019-06-26 07:30 | 267 | 267
2019-06-26 08:00 | 271 | 271
2019-06-26 08:30 | 265 | 265
2019-06-26 09:00 | 251 | 251
2019-06-26 09:30 | 248 | 248
2019-06-26 10:00 | 242 | 242
2019-06-26 10:30 | 239 | 239
2019-06-26 11:00 | 246 | 246
2019-06-26 11:30 | 251 | 251
2019-06-26 12:00 | 250 | 250
2019-06-26 12:30 | 250 | 250
2019-06-26 13:00 | 249 | 249
2019-06-26 13:30 | 253 | 253
2019-06-26 14:00 | 255 | 255
2019-06-26 14:30 | 255 | 255
2019-06-26 15:00 | 253 | 253
2019-06-26 15:30 | 256 | 256
2019-06-26 16:00 | 267 | 267
2019-06-26 16:30 | 278 | 278
2019-06-26 17:00 | 294 | 293
2019-06-26 17:30 | 307 | 306
2019-06-26 18:00 | 312 | 311
2019-06-26 18:30 | 308 | 307
2019-06-26 19:00 | 305 | 305
2019-06-26 19:30 | 297 | 297
2019-06-26 20:00 | 293 | 293
2019-06-26 20:30 | 289 | 289
2019-06-26 21:00 | 276 | 276
2019-06-26 21:30 | 259 | 259
2019-06-26 22:00 | 247 | 246
2019-06-26 22:30 | 236 | 236
2019-06-26 23:00 | 228 | 228
2019-06-26 23:30 | 214 | 214
2019-06-27 | 198 | 198
2019-06-27 00:30 | 182 | 182
2019-06-27 01:00 | 171 | 171
2019-06-27 01:30 | 164 | 164
2019-06-27 02:00 | 158 | 157
2019-06-27 02:30 | 155 | 154
2019-06-27 03:00 | 153 | 152
2019-06-27 03:30 | 153 | 152
2019-06-27 04:00 | 155 | 154
2019-06-27 04:30 | 159 | 158
2019-06-27 05:00 | 166 | 166
2019-06-27 05:30 | 181 | 181
2019-06-27 06:00 | 198 | 198
2019-06-27 06:30 | 222 | 222
2019-06-27 07:00 | 246 | 245
2019-06-27 07:30 | 260 | 260
2019-06-27 08:00 | 258 | 258
2019-06-27 08:30 | 244 | 244
2019-06-27 09:00 | 227 | 227
2019-06-27 09:30 | 217 | 217
2019-06-27 10:00 | 204 | 203
2019-06-27 10:30 | 195 | 194
2019-06-27 11:00 | 189 | 189
2019-06-27 11:30 | 184 | 183
2019-06-27 12:00 | 181 | 181
2019-06-27 12:30 | 185 | 185
2019-06-27 13:00 | 182 | 182
2019-06-27 13:30 | 187 | 187
2019-06-27 14:00 | 196 | 196
2019-06-27 14:30 | 201 | 201
2019-06-27 15:00 | 203 | 203
2019-06-27 15:30 | 214 | 213
2019-06-27 16:00 | 228 | 227
2019-06-27 16:30 | 239 | 239
2019-06-27 17:00 | 254 | 254
2019-06-27 17:30 | 273 | 273
2019-06-27 18:00 | 284 | 284
2019-06-27 18:30 | 284 | 284
2019-06-27 19:00 | 285 | 285
2019-06-27 19:30 | 280 | 280
2019-06-27 20:00 | 278 | 278
2019-06-27 20:30 | 277 | 277
2019-06-27 21:00 | 267 | 267
2019-06-27 21:30 | 256 | 256
2019-06-27 22:00 | 244 | 244
2019-06-27 22:30 | 236 | 235
2019-06-27 23:00 | 228 | 227
2019-06-27 23:30 | 210 | 210
2019-06-28 | 195 | 195
2019-06-28 00:30 | 180 | 179
2019-06-28 01:00 | 169 | 169
2019-06-28 01:30 | 162 | 162
2019-06-28 02:00 | 157 | 157
2019-06-28 02:30 | 153 | 153
2019-06-28 03:00 | 150 | 150
2019-06-28 03:30 | 150 | 150
2019-06-28 04:00 | 152 | 152
2019-06-28 04:30 | 156 | 156
2019-06-28 05:00 | 164 | 163
2019-06-28 05:30 | 176 | 176
2019-06-28 06:00 | 191 | 191
2019-06-28 06:30 | 215 | 214
2019-06-28 07:00 | 236 | 235
2019-06-28 07:30 | 252 | 251
2019-06-28 08:00 | 248 | 248
2019-06-28 08:30 | 239 | 239
2019-06-28 09:00 | 239 | 239
2019-06-28 09:30 | 220 | 220
2019-06-28 10:00 | 193 | 193
2019-06-28 10:30 | 188 | 188
2019-06-28 11:00 | 191 | 191
2019-06-28 11:30 | 180 | 180
2019-06-28 12:00 | 169 | 169
2019-06-28 12:30 | 171 | 171
2019-06-28 13:00 | 176 | 176
2019-06-28 13:30 | 185 | 185
2019-06-28 14:00 | 186 | 186
2019-06-28 14:30 | 192 | 192
2019-06-28 15:00 | 206 | 206
2019-06-28 15:30 | 205 | 205
2019-06-28 16:00 | 211 | 210
2019-06-28 16:30 | 222 | 222
2019-06-28 17:00 | 237 | 237
2019-06-28 17:30 | 252 | 251
2019-06-28 18:00 | 260 | 260
2019-06-28 18:30 | 258 | 258
2019-06-28 19:00 | 260 | 260
2019-06-28 19:30 | 255 | 255
2019-06-28 20:00 | 254 | 254
2019-06-28 20:30 | 253 | 252
2019-06-28 21:00 | 244 | 244
2019-06-28 21:30 | 235 | 234
2019-06-28 22:00 | 225 | 225
2019-06-28 22:30 | 218 | 218
2019-06-28 23:00 | 213 | 212
2019-06-28 23:30 | 200 | 200
2019-06-29 | 186 | 185
2019-06-29 00:30 | 172 | 171
2019-06-29 01:00 | 161 | 161
2019-06-29 01:30 | 154 | 153
2019-06-29 02:00 | 147 | 147
2019-06-29 02:30 | 144 | 144
2019-06-29 03:00 | 142 | 142
2019-06-29 03:30 | 140 | 140
2019-06-29 04:00 | 139 | 139
2019-06-29 04:30 | 139 | 139
2019-06-29 05:00 | 142 | 142
2019-06-29 05:30 | 148 | 148
2019-06-29 06:00 | 154 | 154
2019-06-29 06:30 | 164 | 164
2019-06-29 07:00 | 173 | 173
2019-06-29 07:30 | 184 | 184
2019-06-29 08:00 | 190 | 189
2019-06-29 08:30 | 189 | 188
2019-06-29 09:00 | 184 | 183
2019-06-29 09:30 | 181 | 180
2019-06-29 10:00 | 172 | 172
2019-06-29 10:30 | 164 | 164
2019-06-29 11:00 | 159 | 158
2019-06-29 11:30 | 156 | 156
2019-06-29 12:00 | 157 | 157
2019-06-29 12:30 | 153 | 153
2019-06-29 13:00 | 146 | 146
2019-06-29 13:30 | 149 | 149
2019-06-29 14:00 | 159 | 158
2019-06-29 14:30 | 160 | 160
2019-06-29 15:00 | 163 | 163
2019-06-29 15:30 | 172 | 171
2019-06-29 16:00 | 183 | 183
2019-06-29 16:30 | 195 | 194
2019-06-29 17:00 | 211 | 209
2019-06-29 17:30 | 223 | 223
2019-06-29 18:00 | 231 | 230
2019-06-29 18:30 | 231 | 230
2019-06-29 19:00 | 230 | 230
2019-06-29 19:30 | 225 | 225
2019-06-29 20:00 | 225 | 224
2019-06-29 20:30 | 225 | 224
2019-06-29 21:00 | 216 | 216
2019-06-29 21:30 | 209 | 209
2019-06-29 22:00 | 204 | 204
2019-06-29 22:30 | 200 | 200
2019-06-29 23:00 | 202 | 202
2019-06-29 23:30 | 192 | 192
2019-06-30 | 178 | 178
2019-06-30 00:30 | 164 | 163
2019-06-30 01:00 | 154 | 153
2019-06-30 01:30 | 146 | 146
2019-06-30 02:00 | 140 | 140
2019-06-30 02:30 | 135 | 135
2019-06-30 03:00 | 133 | 133
2019-06-30 03:30 | 133 | 132
2019-06-30 04:00 | 131 | 131
2019-06-30 04:30 | 130 | 130
2019-06-30 05:00 | 132 | 132
2019-06-30 05:30 | 135 | 135
2019-06-30 06:00 | 140 | 140
2019-06-30 06:30 | 148 | 148
2019-06-30 07:00 | 154 | 154
2019-06-30 07:30 | 164 | 164
2019-06-30 08:00 | 165 | 165
2019-06-30 08:30 | 165 | 165
2019-06-30 09:00 | 160 | 160
2019-06-30 09:30 | 154 | 154
2019-06-30 10:00 | 145 | 145
2019-06-30 10:30 | 137 | 137
2019-06-30 11:00 | 129 | 128
2019-06-30 11:30 | 123 | 123
2019-06-30 12:00 | 120 | 119
2019-06-30 12:30 | 118 | 118
2019-06-30 13:00 | 120 | 120
2019-06-30 13:30 | 123 | 123
2019-06-30 14:00 | 129 | 129
2019-06-30 14:30 | 136 | 136
2019-06-30 15:00 | 145 | 145
2019-06-30 15:30 | 157 | 157
2019-06-30 16:00 | 171 | 171
2019-06-30 16:30 | 186 | 186
2019-06-30 17:00 | 204 | 204
2019-06-30 17:30 | 220 | 220
2019-06-30 18:00 | 232 | 231
2019-06-30 18:30 | 231 | 231
2019-06-30 19:00 | 230 | 229
2019-06-30 19:30 | 225 | 225
2019-06-30 20:00 | 223 | 222
2019-06-30 20:30 | 222 | 222
2019-06-30 21:00 | 213 | 213
2019-06-30 21:30 | 207 | 207
2019-06-30 22:00 | 201 | 200
2019-06-30 22:30 | 195 | 195
2019-06-30 23:00 | 192 | 192
2019-06-30 23:30 | 183 | 183
2019-07-01 | 170 | 170
2019-07-01 00:30 | 156 | 156
2019-07-01 01:00 | 147 | 146
2019-07-01 01:30 | 141 | 140
2019-07-01 02:00 | 135 | 135
2019-07-01 02:30 | 132 | 132
2019-07-01 03:00 | 131 | 131
2019-07-01 03:30 | 132 | 132
2019-07-01 04:00 | 133 | 133
2019-07-01 04:30 | 138 | 138
2019-07-01 05:00 | 146 | 146
2019-07-01 05:30 | 162 | 161
2019-07-01 06:00 | 177 | 176
2019-07-01 06:30 | 196 | 195
2019-07-01 07:00 | 214 | 214
2019-07-01 07:30 | 226 | 226
2019-07-01 08:00 | 224 | 223
2019-07-01 08:30 | 216 | 215
2019-07-01 09:00 | 204 | 203
2019-07-01 09:30 | 194 | 192
2019-07-01 10:00 | 185 | 182
2019-07-01 10:30 | 178 | 176
2019-07-01 11:00 | 174 | 172
2019-07-01 11:30 | 177 | 174
2019-07-01 12:00 | 202 | 199
2019-07-01 12:30 | 214 | 211
2019-07-01 13:00 | 207 | 206
2019-07-01 13:30 | 196 | 195
2019-07-01 14:00 | 188 | 187
2019-07-01 14:30 | 190 | 189
2019-07-01 15:00 | 200 | 199
2019-07-01 15:30 | 216 | 215
2019-07-01 16:00 | 230 | 229
2019-07-01 16:30 | 240 | 239
2019-07-01 17:00 | 257 | 255
2019-07-01 17:30 | 270 | 268
2019-07-01 18:00 | 275 | 275
2019-07-01 18:30 | 268 | 268
2019-07-01 19:00 | 265 | 265
2019-07-01 19:30 | 258 | 258
2019-07-01 20:00 | 260 | 260
2019-07-01 20:30 | 260 | 260
2019-07-01 21:00 | 247 | 246
2019-07-01 21:30 | 236 | 235
2019-07-01 22:00 | 225 | 225
2019-07-01 22:30 | 218 | 218
2019-07-01 23:00 | 213 | 213
2019-07-01 23:30 | 202 | 202
2019-07-02 | 187 | 187
2019-07-02 00:30 | 174 | 174
2019-07-02 01:00 | 165 | 164
2019-07-02 01:30 | 158 | 158
2019-07-02 02:00 | 150 | 150
2019-07-02 02:30 | 145 | 145
2019-07-02 03:00 | 142 | 142
2019-07-02 03:30 | 142 | 142
2019-07-02 04:00 | 142 | 142
2019-07-02 04:30 | 148 | 148
2019-07-02 05:00 | 154 | 154
2019-07-02 05:30 | 168 | 168
2019-07-02 06:00 | 182 | 182
2019-07-02 06:30 | 201 | 201
2019-07-02 07:00 | 219 | 219
2019-07-02 07:30 | 232 | 232
2019-07-02 08:00 | 233 | 233
2019-07-02 08:30 | 221 | 221
2019-07-02 09:00 | 208 | 208
2019-07-02 09:30 | 204 | 204
2019-07-02 10:00 | 190 | 189
2019-07-02 10:30 | 179 | 179
2019-07-02 11:00 | 170 | 170
2019-07-02 11:30 | 165 | 164
2019-07-02 12:00 | 166 | 165
2019-07-02 12:30 | 169 | 168
2019-07-02 13:00 | 172 | 172
2019-07-02 13:30 | 180 | 179
2019-07-02 14:00 | 186 | 185
2019-07-02 14:30 | 195 | 193
2019-07-02 15:00 | 201 | 199
2019-07-02 15:30 | 209 | 207
2019-07-02 16:00 | 219 | 218
2019-07-02 16:30 | 231 | 229
2019-07-02 17:00 | 244 | 243
2019-07-02 17:30 | 257 | 256
2019-07-02 18:00 | 265 | 265
2019-07-02 18:30 | 263 | 262
2019-07-02 19:00 | 265 | 264
2019-07-02 19:30 | 262 | 261
2019-07-02 20:00 | 261 | 260
2019-07-02 20:30 | 259 | 258
2019-07-02 21:00 | 249 | 248
2019-07-02 21:30 | 239 | 238
2019-07-02 22:00 | 230 | 229
2019-07-02 22:30 | 224 | 223
2019-07-02 23:00 | 219 | 219
2019-07-02 23:30 | 207 | 207
2019-07-03 | 191 | 191
2019-07-03 00:30 | 176 | 176
2019-07-03 01:00 | 167 | 166
2019-07-03 01:30 | 160 | 160
2019-07-03 02:00 | 154 | 154
2019-07-03 02:30 | 151 | 151
2019-07-03 03:00 | 150 | 150
2019-07-03 03:30 | 150 | 150
2019-07-03 04:00 | 150 | 150
2019-07-03 04:30 | 154 | 154
2019-07-03 05:00 | 162 | 162
2019-07-03 05:30 | 177 | 177
2019-07-03 06:00 | 192 | 192
2019-07-03 06:30 | 212 | 212
2019-07-03 07:00 | 230 | 229
2019-07-03 07:30 | 244 | 244
2019-07-03 08:00 | 240 | 240
2019-07-03 08:30 | 231 | 231
2019-07-03 09:00 | 219 | 218
2019-07-03 09:30 | 207 | 207
2019-07-03 10:00 | 193 | 193
2019-07-03 10:30 | 189 | 189
2019-07-03 11:00 | 190 | 190
2019-07-03 11:30 | 189 | 188
2019-07-03 12:00 | 183 | 183
2019-07-03 12:30 | 181 | 181
2019-07-03 13:00 | 181 | 180
2019-07-03 13:30 | 180 | 179
2019-07-03 14:00 | 186 | 185
2019-07-03 14:30 | 194 | 193
2019-07-03 15:00 | 203 | 202
2019-07-03 15:30 | 210 | 208
2019-07-03 16:00 | 219 | 218
2019-07-03 16:30 | 231 | 231
2019-07-03 17:00 | 247 | 247
2019-07-03 17:30 | 264 | 264
2019-07-03 18:00 | 274 | 274
2019-07-03 18:30 | 271 | 271
2019-07-03 19:00 | 271 | 271
2019-07-03 19:30 | 263 | 263
2019-07-03 20:00 | 260 | 260
2019-07-03 20:30 | 257 | 257
2019-07-03 21:00 | 249 | 249
2019-07-03 21:30 | 239 | 239
2019-07-03 22:00 | 229 | 229
2019-07-03 22:30 | 221 | 221
2019-07-03 23:00 | 217 | 217
2019-07-03 23:30 | 204 | 204
2019-07-04 | 188 | 187
2019-07-04 00:30 | 173 | 173
2019-07-04 01:00 | 163 | 163
2019-07-04 01:30 | 158 | 157
2019-07-04 02:00 | 153 | 152
2019-07-04 02:30 | 150 | 149
2019-07-04 03:00 | 148 | 147
2019-07-04 03:30 | 149 | 148
2019-07-04 04:00 | 149 | 148
2019-07-04 04:30 | 153 | 152
2019-07-04 05:00 | 159 | 159
2019-07-04 05:30 | 172 | 172
2019-07-04 06:00 | 185 | 185
2019-07-04 06:30 | 205 | 205
2019-07-04 07:00 | 220 | 219
2019-07-04 07:30 | 232 | 231
2019-07-04 08:00 | 232 | 231
2019-07-04 08:30 | 230 | 228
2019-07-04 09:00 | 223 | 221
2019-07-04 09:30 | 212 | 210
2019-07-04 10:00 | 201 | 200
2019-07-04 10:30 | 194 | 193
2019-07-04 11:00 | 194 | 192
2019-07-04 11:30 | 187 | 185
2019-07-04 12:00 | 185 | 183
2019-07-04 12:30 | 184 | 183
2019-07-04 13:00 | 185 | 184
2019-07-04 13:30 | 194 | 192
2019-07-04 14:00 | 206 | 205
2019-07-04 14:30 | 210 | 210
2019-07-04 15:00 | 218 | 217
2019-07-04 15:30 | 222 | 222
2019-07-04 16:00 | 226 | 226
2019-07-04 16:30 | 234 | 234
2019-07-04 17:00 | 247 | 247
2019-07-04 17:30 | 261 | 260
2019-07-04 18:00 | 273 | 271
2019-07-04 18:30 | 271 | 270
2019-07-04 19:00 | 271 | 270
2019-07-04 19:30 | 266 | 265
2019-07-04 20:00 | 262 | 262
2019-07-04 20:30 | 261 | 260
2019-07-04 21:00 | 250 | 250
2019-07-04 21:30 | 239 | 239
2019-07-04 22:00 | 230 | 229
2019-07-04 22:30 | 224 | 224
2019-07-04 23:00 | 220 | 220
2019-07-04 23:30 | 207 | 207
2019-07-05 | 191 | 191
2019-07-05 00:30 | 177 | 176
2019-07-05 01:00 | 167 | 167
2019-07-05 01:30 | 160 | 159
2019-07-05 02:00 | 155 | 154
2019-07-05 02:30 | 152 | 151
2019-07-05 03:00 | 150 | 149
2019-07-05 03:30 | 149 | 148
2019-07-05 04:00 | 150 | 149
2019-07-05 04:30 | 155 | 154
2019-07-05 05:00 | 160 | 160
2019-07-05 05:30 | 172 | 171
2019-07-05 06:00 | 184 | 184
2019-07-05 06:30 | 203 | 203
2019-07-05 07:00 | 217 | 217
2019-07-05 07:30 | 229 | 228
2019-07-05 08:00 | 231 | 231
2019-07-05 08:30 | 229 | 229
2019-07-05 09:00 | 222 | 222
2019-07-05 09:30 | 213 | 213
2019-07-05 10:00 | 203 | 203
2019-07-05 10:30 | 200 | 200
2019-07-05 11:00 | 199 | 199
2019-07-05 11:30 | 192 | 192
2019-07-05 12:00 | 198 | 198
2019-07-05 12:30 | 204 | 204
2019-07-05 13:00 | 212 | 212
2019-07-05 13:30 | 207 | 207
2019-07-05 14:00 | 199 | 199
2019-07-05 14:30 | 210 | 210
2019-07-05 15:00 | 216 | 215
2019-07-05 15:30 | 220 | 220
2019-07-05 16:00 | 226 | 226
2019-07-05 16:30 | 235 | 235
2019-07-05 17:00 | 247 | 247
2019-07-05 17:30 | 261 | 260
2019-07-05 18:00 | 267 | 267
2019-07-05 18:30 | 264 | 264
2019-07-05 19:00 | 264 | 264
2019-07-05 19:30 | 258 | 258
2019-07-05 20:00 | 257 | 257
2019-07-05 20:30 | 254 | 254
2019-07-05 21:00 | 245 | 244
2019-07-05 21:30 | 236 | 236
2019-07-05 22:00 | 228 | 228
2019-07-05 22:30 | 223 | 222
2019-07-05 23:00 | 218 | 218
2019-07-05 23:30 | 205 | 205
2019-07-06 | 187 | 187
2019-07-06 00:30 | 173 | 172
2019-07-06 01:00 | 162 | 162
2019-07-06 01:30 | 155 | 154
2019-07-06 02:00 | 148 | 147
2019-07-06 02:30 | 145 | 143
2019-07-06 03:00 | 140 | 139
2019-07-06 03:30 | 140 | 139
2019-07-06 04:00 | 139 | 138
2019-07-06 04:30 | 140 | 138
2019-07-06 05:00 | 142 | 141
2019-07-06 05:30 | 153 | 152
2019-07-06 06:00 | 154 | 153
2019-07-06 06:30 | 161 | 161
2019-07-06 07:00 | 167 | 167
2019-07-06 07:30 | 176 | 176
2019-07-06 08:00 | 185 | 185
2019-07-06 08:30 | 194 | 194
2019-07-06 09:00 | 202 | 202
2019-07-06 09:30 | 199 | 199
2019-07-06 10:00 | 183 | 183
2019-07-06 10:30 | 173 | 173
2019-07-06 11:00 | 165 | 165
2019-07-06 11:30 | 162 | 162
2019-07-06 12:00 | 163 | 163
2019-07-06 12:30 | 159 | 158
2019-07-06 13:00 | 169 | 169
2019-07-06 13:30 | 176 | 176
2019-07-06 14:00 | 175 | 175
2019-07-06 14:30 | 177 | 177
2019-07-06 15:00 | 173 | 173
2019-07-06 15:30 | 185 | 185
2019-07-06 16:00 | 196 | 196
2019-07-06 16:30 | 208 | 208
2019-07-06 17:00 | 223 | 223
2019-07-06 17:30 | 235 | 235
2019-07-06 18:00 | 238 | 237
2019-07-06 18:30 | 236 | 236
2019-07-06 19:00 | 236 | 236
2019-07-06 19:30 | 231 | 231
2019-07-06 20:00 | 230 | 228
2019-07-06 20:30 | 230 | 228
2019-07-06 21:00 | 220 | 219
2019-07-06 21:30 | 214 | 213
2019-07-06 22:00 | 208 | 207
2019-07-06 22:30 | 204 | 203
2019-07-06 23:00 | 202 | 201
2019-07-06 23:30 | 192 | 192
2019-07-07 | 178 | 178
2019-07-07 00:30 | 164 | 164
2019-07-07 01:00 | 154 | 153
2019-07-07 01:30 | 147 | 146
2019-07-07 02:00 | 142 | 140
2019-07-07 02:30 | 139 | 137
2019-07-07 03:00 | 136 | 134
2019-07-07 03:30 | 135 | 133
2019-07-07 04:00 | 134 | 133
2019-07-07 04:30 | 134 | 133
2019-07-07 05:00 | 136 | 134
2019-07-07 05:30 | 139 | 137
2019-07-07 06:00 | 142 | 141
2019-07-07 06:30 | 148 | 147
2019-07-07 07:00 | 153 | 152
2019-07-07 07:30 | 161 | 160
2019-07-07 08:00 | 166 | 165
2019-07-07 08:30 | 170 | 170
2019-07-07 09:00 | 169 | 169
2019-07-07 09:30 | 168 | 168
2019-07-07 10:00 | 159 | 159
2019-07-07 10:30 | 150 | 150
2019-07-07 11:00 | 148 | 148
2019-07-07 11:30 | 146 | 146
2019-07-07 12:00 | 154 | 154
2019-07-07 12:30 | 154 | 153
2019-07-07 13:00 | 155 | 155
2019-07-07 13:30 | 160 | 160
2019-07-07 14:00 | 165 | 165
2019-07-07 14:30 | 170 | 170
2019-07-07 15:00 | 175 | 175
2019-07-07 15:30 | 178 | 178
2019-07-07 16:00 | 188 | 188
2019-07-07 16:30 | 198 | 198
2019-07-07 17:00 | 213 | 213
2019-07-07 17:30 | 231 | 231
2019-07-07 18:00 | 241 | 241
2019-07-07 18:30 | 241 | 241
2019-07-07 19:00 | 241 | 241
2019-07-07 19:30 | 235 | 235
2019-07-07 20:00 | 236 | 236
2019-07-07 20:30 | 238 | 238
2019-07-07 21:00 | 229 | 229
2019-07-07 21:30 | 221 | 221
2019-07-07 22:00 | 214 | 214
2019-07-07 22:30 | 209 | 209
2019-07-07 23:00 | 206 | 205
2019-07-07 23:30 | 195 | 194
2019-07-08 | 180 | 179
2019-07-08 00:30 | 166 | 166
2019-07-08 01:00 | 157 | 157
2019-07-08 01:30 | 151 | 150
2019-07-08 02:00 | 146 | 145
2019-07-08 02:30 | 143 | 142
2019-07-08 03:00 | 140 | 140
2019-07-08 03:30 | 140 | 140
2019-07-08 04:00 | 140 | 140
2019-07-08 04:30 | 146 | 146
2019-07-08 05:00 | 154 | 154
2019-07-08 05:30 | 168 | 167
2019-07-08 06:00 | 182 | 181
2019-07-08 06:30 | 202 | 201
2019-07-08 07:00 | 218 | 217
2019-07-08 07:30 | 235 | 235
2019-07-08 08:00 | 236 | 236
2019-07-08 08:30 | 240 | 240
2019-07-08 09:00 | 242 | 242
2019-07-08 09:30 | 243 | 243
2019-07-08 10:00 | 232 | 232
2019-07-08 10:30 | 216 | 216
2019-07-08 11:00 | 209 | 209
2019-07-08 11:30 | 220 | 220
2019-07-08 12:00 | 223 | 223
2019-07-08 12:30 | 228 | 228
2019-07-08 13:00 | 244 | 243
2019-07-08 13:30 | 240 | 240
2019-07-08 14:00 | 232 | 232
2019-07-08 14:30 | 228 | 228
2019-07-08 15:00 | 231 | 231
2019-07-08 15:30 | 233 | 233
2019-07-08 16:00 | 234 | 234
2019-07-08 16:30 | 242 | 242
2019-07-08 17:00 | 261 | 261
2019-07-08 17:30 | 280 | 280
2019-07-08 18:00 | 295 | 295
2019-07-08 18:30 | 294 | 294
2019-07-08 19:00 | 292 | 292
2019-07-08 19:30 | 284 | 283
2019-07-08 20:00 | 281 | 280
2019-07-08 20:30 | 277 | 277
2019-07-08 21:00 | 266 | 266
2019-07-08 21:30 | 255 | 255
2019-07-08 22:00 | 241 | 240
2019-07-08 22:30 | 232 | 232
2019-07-08 23:00 | 226 | 226
2019-07-08 23:30 | 213 | 213
2019-07-09 | 197 | 197
2019-07-09 00:30 | 182 | 182
2019-07-09 01:00 | 172 | 172
2019-07-09 01:30 | 164 | 164
2019-07-09 02:00 | 158 | 158
2019-07-09 02:30 | 155 | 155
2019-07-09 03:00 | 153 | 153
2019-07-09 03:30 | 154 | 154
2019-07-09 04:00 | 154 | 154
2019-07-09 04:30 | 159 | 159
2019-07-09 05:00 | 167 | 167
2019-07-09 05:30 | 180 | 180
2019-07-09 06:00 | 195 | 195
2019-07-09 06:30 | 219 | 217
2019-07-09 07:00 | 237 | 235
2019-07-09 07:30 | 248 | 247
2019-07-09 08:00 | 244 | 243
2019-07-09 08:30 | 235 | 234
2019-07-09 09:00 | 220 | 220
2019-07-09 09:30 | 205 | 205
2019-07-09 10:00 | 192 | 192
2019-07-09 10:30 | 182 | 181
2019-07-09 11:00 | 174 | 174
2019-07-09 11:30 | 169 | 168
2019-07-09 12:00 | 165 | 165
2019-07-09 12:30 | 165 | 165
2019-07-09 13:00 | 168 | 167
2019-07-09 13:30 | 175 | 175
2019-07-09 14:00 | 181 | 180
2019-07-09 14:30 | 190 | 189
2019-07-09 15:00 | 198 | 197
2019-07-09 15:30 | 208 | 207
2019-07-09 16:00 | 220 | 219
2019-07-09 16:30 | 233 | 232
2019-07-09 17:00 | 249 | 249
2019-07-09 17:30 | 263 | 263
2019-07-09 18:00 | 276 | 276
2019-07-09 18:30 | 275 | 275
2019-07-09 19:00 | 276 | 276
2019-07-09 19:30 | 270 | 270
2019-07-09 20:00 | 269 | 268
2019-07-09 20:30 | 266 | 266
2019-07-09 21:00 | 255 | 254
2019-07-09 21:30 | 243 | 243
2019-07-09 22:00 | 232 | 231
2019-07-09 22:30 | 224 | 224
2019-07-09 23:00 | 221 | 221
2019-07-09 23:30 | 211 | 211
2019-07-10 | 192 | 192
2019-07-10 00:30 | 174 | 174
2019-07-10 01:00 | 163 | 163
2019-07-10 01:30 | 156 | 156
2019-07-10 02:00 | 151 | 151
2019-07-10 02:30 | 148 | 148
2019-07-10 03:00 | 146 | 146
2019-07-10 03:30 | 146 | 146
2019-07-10 04:00 | 146 | 146
2019-07-10 04:30 | 151 | 151
2019-07-10 05:00 | 159 | 159
2019-07-10 05:30 | 174 | 174
2019-07-10 06:00 | 190 | 189
2019-07-10 06:30 | 213 | 212
2019-07-10 07:00 | 232 | 232
2019-07-10 07:30 | 243 | 243
2019-07-10 08:00 | 243 | 243
2019-07-10 08:30 | 236 | 236
2019-07-10 09:00 | 220 | 219
2019-07-10 09:30 | 203 | 203
2019-07-10 10:00 | 188 | 188
2019-07-10 10:30 | 176 | 175
2019-07-10 11:00 | 163 | 163
2019-07-10 11:30 | 159 | 158
2019-07-10 12:00 | 158 | 157
2019-07-10 12:30 | 151 | 151
2019-07-10 13:00 | 151 | 151
2019-07-10 13:30 | 155 | 155
2019-07-10 14:00 | 160 | 160
2019-07-10 14:30 | 169 | 168
2019-07-10 15:00 | 179 | 178
2019-07-10 15:30 | 191 | 191
2019-07-10 16:00 | 206 | 205
2019-07-10 16:30 | 221 | 220
2019-07-10 17:00 | 239 | 238
2019-07-10 17:30 | 254 | 254
2019-07-10 18:00 | 268 | 268
2019-07-10 18:30 | 269 | 269
2019-07-10 19:00 | 272 | 272
2019-07-10 19:30 | 269 | 268
2019-07-10 20:00 | 270 | 270
2019-07-10 20:30 | 268 | 267
2019-07-10 21:00 | 257 | 257
2019-07-10 21:30 | 250 | 249
2019-07-10 22:00 | 238 | 238
2019-07-10 22:30 | 232 | 232
2019-07-10 23:00 | 227 | 227
2019-07-10 23:30 | 214 | 214
2019-07-11 | 196 | 196
2019-07-11 00:30 | 182 | 181
2019-07-11 01:00 | 169 | 169
2019-07-11 01:30 | 161 | 161
2019-07-11 02:00 | 155 | 155
2019-07-11 02:30 | 152 | 152
2019-07-11 03:00 | 150 | 150
2019-07-11 03:30 | 151 | 151
2019-07-11 04:00 | 152 | 152
2019-07-11 04:30 | 157 | 157
2019-07-11 05:00 | 166 | 166
2019-07-11 05:30 | 182 | 182
2019-07-11 06:00 | 198 | 198
2019-07-11 06:30 | 222 | 221
2019-07-11 07:00 | 242 | 241
2019-07-11 07:30 | 255 | 254
2019-07-11 08:00 | 253 | 253
2019-07-11 08:30 | 236 | 236
2019-07-11 09:00 | 216 | 216
2019-07-11 09:30 | 197 | 197
2019-07-11 10:00 | 180 | 179
2019-07-11 10:30 | 171 | 170
2019-07-11 11:00 | 164 | 164
2019-07-11 11:30 | 154 | 154
2019-07-11 12:00 | 146 | 145
2019-07-11 12:30 | 144 | 143
2019-07-11 13:00 | 149 | 149
2019-07-11 13:30 | 155 | 155
2019-07-11 14:00 | 161 | 161
2019-07-11 14:30 | 170 | 169
2019-07-11 15:00 | 180 | 179
2019-07-11 15:30 | 199 | 198
2019-07-11 16:00 | 214 | 213
2019-07-11 16:30 | 223 | 223
2019-07-11 17:00 | 237 | 236
2019-07-11 17:30 | 254 | 254
2019-07-11 18:00 | 270 | 269
2019-07-11 18:30 | 271 | 270
2019-07-11 19:00 | 272 | 271
2019-07-11 19:30 | 269 | 269
2019-07-11 20:00 | 268 | 267
2019-07-11 20:30 | 266 | 266
2019-07-11 21:00 | 259 | 259
2019-07-11 21:30 | 247 | 246
2019-07-11 22:00 | 235 | 235
2019-07-11 22:30 | 229 | 229
2019-07-11 23:00 | 224 | 224
2019-07-11 23:30 | 211 | 211
2019-07-12 | 195 | 195
2019-07-12 00:30 | 180 | 180
2019-07-12 01:00 | 168 | 168
2019-07-12 01:30 | 161 | 161
2019-07-12 02:00 | 155 | 155
2019-07-12 02:30 | 152 | 152
2019-07-12 03:00 | 151 | 151
2019-07-12 03:30 | 151 | 151
2019-07-12 04:00 | 152 | 152
2019-07-12 04:30 | 158 | 158
2019-07-12 05:00 | 166 | 166
2019-07-12 05:30 | 181 | 181
2019-07-12 06:00 | 198 | 197
2019-07-12 06:30 | 223 | 222
2019-07-12 07:00 | 241 | 241
2019-07-12 07:30 | 256 | 256
2019-07-12 08:00 | 252 | 252
2019-07-12 08:30 | 241 | 241
2019-07-12 09:00 | 222 | 222
2019-07-12 09:30 | 204 | 203
2019-07-12 10:00 | 186 | 186
2019-07-12 10:30 | 171 | 171
2019-07-12 11:00 | 162 | 162
2019-07-12 11:30 | 153 | 153
2019-07-12 12:00 | 148 | 148
2019-07-12 12:30 | 147 | 145
2019-07-12 13:00 | 147 | 146
2019-07-12 13:30 | 159 | 157
2019-07-12 14:00 | 162 | 160
2019-07-12 14:30 | 166 | 164
2019-07-12 15:00 | 174 | 173
2019-07-12 15:30 | 183 | 183
2019-07-12 16:00 | 199 | 198
2019-07-12 16:30 | 212 | 212
2019-07-12 17:00 | 230 | 230
2019-07-12 17:30 | 250 | 249
2019-07-12 18:00 | 258 | 258
2019-07-12 18:30 | 254 | 254
2019-07-12 19:00 | 257 | 257
2019-07-12 19:30 | 255 | 255
2019-07-12 20:00 | 254 | 254
2019-07-12 20:30 | 256 | 255
2019-07-12 21:00 | 254 | 254
2019-07-12 21:30 | 241 | 241
2019-07-12 22:00 | 231 | 230
2019-07-12 22:30 | 222 | 222
2019-07-12 23:00 | 218 | 218
2019-07-12 23:30 | 205 | 205
2019-07-13 | 190 | 190
2019-07-13 00:30 | 176 | 176
2019-07-13 01:00 | 164 | 164
2019-07-13 01:30 | 158 | 158
2019-07-13 02:00 | 151 | 151
2019-07-13 02:30 | 146 | 146
2019-07-13 03:00 | 143 | 143
2019-07-13 03:30 | 143 | 143
2019-07-13 04:00 | 142 | 142
2019-07-13 04:30 | 144 | 144
2019-07-13 05:00 | 145 | 145
2019-07-13 05:30 | 152 | 152
2019-07-13 06:00 | 159 | 159
2019-07-13 06:30 | 170 | 170
2019-07-13 07:00 | 179 | 179
2019-07-13 07:30 | 188 | 188
2019-07-13 08:00 | 196 | 196
2019-07-13 08:30 | 196 | 196
2019-07-13 09:00 | 188 | 188
2019-07-13 09:30 | 178 | 178
2019-07-13 10:00 | 170 | 170
2019-07-13 10:30 | 154 | 154
2019-07-13 11:00 | 141 | 141
2019-07-13 11:30 | 138 | 138
2019-07-13 12:00 | 131 | 131
2019-07-13 12:30 | 130 | 130
2019-07-13 13:00 | 130 | 130
2019-07-13 13:30 | 130 | 130
2019-07-13 14:00 | 133 | 133
2019-07-13 14:30 | 143 | 142
2019-07-13 15:00 | 148 | 148
2019-07-13 15:30 | 160 | 160
2019-07-13 16:00 | 176 | 175
2019-07-13 16:30 | 193 | 193
2019-07-13 17:00 | 210 | 209
2019-07-13 17:30 | 227 | 227
2019-07-13 18:00 | 238 | 238
2019-07-13 18:30 | 241 | 240
2019-07-13 19:00 | 240 | 240
2019-07-13 19:30 | 232 | 232
2019-07-13 20:00 | 229 | 229
2019-07-13 20:30 | 230 | 230
2019-07-13 21:00 | 223 | 223
2019-07-13 21:30 | 217 | 217
2019-07-13 22:00 | 212 | 212
2019-07-13 22:30 | 208 | 208
2019-07-13 23:00 | 206 | 205
2019-07-13 23:30 | 196 | 196
2019-07-14 | 183 | 183
2019-07-14 00:30 | 169 | 169
2019-07-14 01:00 | 159 | 159
2019-07-14 01:30 | 151 | 151
2019-07-14 02:00 | 145 | 145
2019-07-14 02:30 | 142 | 142
2019-07-14 03:00 | 139 | 139
2019-07-14 03:30 | 138 | 138
2019-07-14 04:00 | 138 | 138
2019-07-14 04:30 | 139 | 139
2019-07-14 05:00 | 141 | 140
2019-07-14 05:30 | 146 | 146
2019-07-14 06:00 | 152 | 152
2019-07-14 06:30 | 163 | 162
2019-07-14 07:00 | 170 | 169
2019-07-14 07:30 | 179 | 178
2019-07-14 08:00 | 182 | 181
2019-07-14 08:30 | 181 | 179
2019-07-14 09:00 | 172 | 171
2019-07-14 09:30 | 162 | 161
2019-07-14 10:00 | 152 | 151
2019-07-14 10:30 | 140 | 139
2019-07-14 11:00 | 128 | 128
2019-07-14 11:30 | 119 | 119
2019-07-14 12:00 | 113 | 113
2019-07-14 12:30 | 111 | 110
2019-07-14 13:00 | 110 | 109
2019-07-14 13:30 | 113 | 112
2019-07-14 14:00 | 120 | 119
2019-07-14 14:30 | 127 | 126
2019-07-14 15:00 | 138 | 138
2019-07-14 15:30 | 153 | 152
2019-07-14 16:00 | 172 | 171
2019-07-14 16:30 | 194 | 194
2019-07-14 17:00 | 221 | 221
2019-07-14 17:30 | 247 | 247
2019-07-14 18:00 | 270 | 269
2019-07-14 18:30 | 279 | 278
2019-07-14 19:00 | 280 | 280
2019-07-14 19:30 | 278 | 278
2019-07-14 20:00 | 278 | 278
2019-07-14 20:30 | 280 | 280
2019-07-14 21:00 | 270 | 270
2019-07-14 21:30 | 258 | 258
2019-07-14 22:00 | 246 | 246
2019-07-14 22:30 | 236 | 236
2019-07-14 23:00 | 229 | 228
2019-07-14 23:30 | 216 | 216
2019-07-15 | 204 | 204
2019-07-15 00:30 | 186 | 186
2019-07-15 01:00 | 174 | 173
2019-07-15 01:30 | 165 | 165
2019-07-15 02:00 | 159 | 159
2019-07-15 02:30 | 154 | 154
2019-07-15 03:00 | 155 | 155
2019-07-15 03:30 | 159 | 159
2019-07-15 04:00 | 157 | 157
2019-07-15 04:30 | 162 | 162
2019-07-15 05:00 | 173 | 173
2019-07-15 05:30 | 193 | 193
2019-07-15 06:00 | 216 | 214
2019-07-15 06:30 | 246 | 246
2019-07-15 07:00 | 277 | 277
2019-07-15 07:30 | 300 | 299
2019-07-15 08:00 | 289 | 289
2019-07-15 08:30 | 265 | 265
2019-07-15 09:00 | 242 | 242
2019-07-15 09:30 | 221 | 221
2019-07-15 10:00 | 202 | 202
2019-07-15 10:30 | 188 | 188
2019-07-15 11:00 | 176 | 175
2019-07-15 11:30 | 166 | 166
2019-07-15 12:00 | 162 | 162
2019-07-15 12:30 | 160 | 160
2019-07-15 13:00 | 156 | 156
2019-07-15 13:30 | 158 | 157
2019-07-15 14:00 | 162 | 162
2019-07-15 14:30 | 170 | 170
2019-07-15 15:00 | 180 | 180
2019-07-15 15:30 | 198 | 198
2019-07-15 16:00 | 214 | 214
2019-07-15 16:30 | 230 | 230
2019-07-15 17:00 | 255 | 254
2019-07-15 17:30 | 284 | 283
2019-07-15 18:00 | 312 | 312
2019-07-15 18:30 | 316 | 316
2019-07-15 19:00 | 315 | 314
2019-07-15 19:30 | 309 | 309
2019-07-15 20:00 | 307 | 306
2019-07-15 20:30 | 308 | 306
2019-07-15 21:00 | 294 | 293
2019-07-15 21:30 | 279 | 279
2019-07-15 22:00 | 264 | 264
2019-07-15 22:30 | 258 | 258
2019-07-15 23:00 | 250 | 250
2019-07-15 23:30 | 234 | 233
2019-07-16 | 213 | 213
2019-07-16 00:30 | 191 | 190
2019-07-16 01:00 | 178 | 178
2019-07-16 01:30 | 171 | 170
2019-07-16 02:00 | 170 | 169
2019-07-16 02:30 | 170 | 170
2019-07-16 03:00 | 167 | 167
2019-07-16 03:30 | 163 | 163
2019-07-16 04:00 | 163 | 163
2019-07-16 04:30 | 170 | 170
2019-07-16 05:00 | 181 | 181
2019-07-16 05:30 | 201 | 200
2019-07-16 06:00 | 225 | 223
2019-07-16 06:30 | 258 | 258
2019-07-16 07:00 | 291 | 290
2019-07-16 07:30 | 307 | 307
2019-07-16 08:00 | 298 | 297
2019-07-16 08:30 | 270 | 270
2019-07-16 09:00 | 241 | 241
2019-07-16 09:30 | 219 | 219
2019-07-16 10:00 | 198 | 197
2019-07-16 10:30 | 183 | 182
2019-07-16 11:00 | 173 | 172
2019-07-16 11:30 | 171 | 170
2019-07-16 12:00 | 163 | 162
2019-07-16 12:30 | 155 | 154
2019-07-16 13:00 | 153 | 152
2019-07-16 13:30 | 156 | 155
2019-07-16 14:00 | 161 | 161
2019-07-16 14:30 | 168 | 168
2019-07-16 15:00 | 184 | 184
2019-07-16 15:30 | 192 | 191
2019-07-16 16:00 | 206 | 205
2019-07-16 16:30 | 224 | 223
2019-07-16 17:00 | 246 | 246
2019-07-16 17:30 | 269 | 269
2019-07-16 18:00 | 292 | 291
2019-07-16 18:30 | 299 | 297
2019-07-16 19:00 | 305 | 303
2019-07-16 19:30 | 304 | 302
2019-07-16 20:00 | 305 | 303
2019-07-16 20:30 | 304 | 303
2019-07-16 21:00 | 292 | 290
2019-07-16 21:30 | 277 | 276
2019-07-16 22:00 | 263 | 262
2019-07-16 22:30 | 251 | 250
2019-07-16 23:00 | 240 | 240
2019-07-16 23:30 | 223 | 223
2019-07-17 | 205 | 205
2019-07-17 00:30 | 188 | 188
2019-07-17 01:00 | 179 | 179
2019-07-17 01:30 | 171 | 171
2019-07-17 02:00 | 169 | 168
2019-07-17 02:30 | 168 | 168
2019-07-17 03:00 | 166 | 166
2019-07-17 03:30 | 167 | 167
2019-07-17 04:00 | 169 | 169
2019-07-17 04:30 | 176 | 175
2019-07-17 05:00 | 187 | 187
2019-07-17 05:30 | 207 | 206
2019-07-17 06:00 | 228 | 227
2019-07-17 06:30 | 260 | 259
2019-07-17 07:00 | 292 | 291
2019-07-17 07:30 | 309 | 308
2019-07-17 08:00 | 298 | 297
2019-07-17 08:30 | 271 | 271
2019-07-17 09:00 | 240 | 240
2019-07-17 09:30 | 217 | 215
2019-07-17 10:00 | 196 | 195
2019-07-17 10:30 | 181 | 181
2019-07-17 11:00 | 174 | 173
2019-07-17 11:30 | 165 | 164
2019-07-17 12:00 | 160 | 159
2019-07-17 12:30 | 158 | 157
2019-07-17 13:00 | 158 | 157
2019-07-17 13:30 | 161 | 161
2019-07-17 14:00 | 168 | 168
2019-07-17 14:30 | 177 | 176
2019-07-17 15:00 | 185 | 185
2019-07-17 15:30 | 197 | 197
2019-07-17 16:00 | 212 | 211
2019-07-17 16:30 | 228 | 227
2019-07-17 17:00 | 249 | 248
2019-07-17 17:30 | 267 | 266
2019-07-17 18:00 | 286 | 286
2019-07-17 18:30 | 291 | 291
2019-07-17 19:00 | 295 | 295
2019-07-17 19:30 | 292 | 292
2019-07-17 20:00 | 292 | 292
2019-07-17 20:30 | 293 | 293
2019-07-17 21:00 | 283 | 283
2019-07-17 21:30 | 271 | 271
2019-07-17 22:00 | 259 | 259
2019-07-17 22:30 | 249 | 249
2019-07-17 23:00 | 242 | 242
2019-07-17 23:30 | 225 | 225
2019-07-18 | 208 | 207
2019-07-18 00:30 | 192 | 192
2019-07-18 01:00 | 182 | 181
2019-07-18 01:30 | 174 | 173
2019-07-18 02:00 | 169 | 169
2019-07-18 02:30 | 165 | 165
2019-07-18 03:00 | 163 | 163
2019-07-18 03:30 | 163 | 163
2019-07-18 04:00 | 164 | 164
2019-07-18 04:30 | 171 | 170
2019-07-18 05:00 | 182 | 181
2019-07-18 05:30 | 202 | 201
2019-07-18 06:00 | 225 | 222
2019-07-18 06:30 | 256 | 254
2019-07-18 07:00 | 285 | 285
2019-07-18 07:30 | 301 | 300
2019-07-18 08:00 | 287 | 286
2019-07-18 08:30 | 260 | 260
2019-07-18 09:00 | 236 | 235
2019-07-18 09:30 | 218 | 218
2019-07-18 10:00 | 197 | 197
2019-07-18 10:30 | 184 | 181
2019-07-18 11:00 | 172 | 169
2019-07-18 11:30 | 163 | 160
2019-07-18 12:00 | 158 | 155
2019-07-18 12:30 | 156 | 153
2019-07-18 13:00 | 156 | 154
2019-07-18 13:30 | 161 | 158
2019-07-18 14:00 | 166 | 164
2019-07-18 14:30 | 175 | 172
2019-07-18 15:00 | 183 | 180
2019-07-18 15:30 | 195 | 192
2019-07-18 16:00 | 211 | 210
2019-07-18 16:30 | 228 | 227
2019-07-18 17:00 | 248 | 247
2019-07-18 17:30 | 268 | 267
2019-07-18 18:00 | 288 | 287
2019-07-18 18:30 | 293 | 293
2019-07-18 19:00 | 298 | 298
2019-07-18 19:30 | 297 | 297
2019-07-18 20:00 | 298 | 298
2019-07-18 20:30 | 299 | 299
2019-07-18 21:00 | 290 | 290
2019-07-18 21:30 | 278 | 278
2019-07-18 22:00 | 266 | 266
2019-07-18 22:30 | 255 | 255
2019-07-18 23:00 | 247 | 247
2019-07-18 23:30 | 231 | 230
2019-07-19 | 211 | 211
2019-07-19 00:30 | 196 | 195
2019-07-19 01:00 | 186 | 186
2019-07-19 01:30 | 177 | 176
2019-07-19 02:00 | 171 | 171
2019-07-19 02:30 | 168 | 167
2019-07-19 03:00 | 166 | 166
2019-07-19 03:30 | 166 | 165
2019-07-19 04:00 | 167 | 167
2019-07-19 04:30 | 174 | 173
2019-07-19 05:00 | 184 | 184
2019-07-19 05:30 | 204 | 204
2019-07-19 06:00 | 226 | 225
2019-07-19 06:30 | 257 | 256
2019-07-19 07:00 | 288 | 285
2019-07-19 07:30 | 308 | 307
2019-07-19 08:00 | 296 | 295
2019-07-19 08:30 | 269 | 269
2019-07-19 09:00 | 241 | 240
2019-07-19 09:30 | 219 | 218
2019-07-19 10:00 | 205 | 201
2019-07-19 10:30 | 190 | 186
2019-07-19 11:00 | 176 | 174
2019-07-19 11:30 | 165 | 164
2019-07-19 12:00 | 159 | 158
2019-07-19 12:30 | 156 | 154
2019-07-19 13:00 | 156 | 153
2019-07-19 13:30 | 157 | 155
2019-07-19 14:00 | 162 | 160
2019-07-19 14:30 | 170 | 168
2019-07-19 15:00 | 178 | 176
2019-07-19 15:30 | 190 | 188
2019-07-19 16:00 | 206 | 203
2019-07-19 16:30 | 223 | 222
2019-07-19 17:00 | 244 | 242
2019-07-19 17:30 | 258 | 256
2019-07-19 18:00 | 273 | 270
2019-07-19 18:30 | 277 | 275
2019-07-19 19:00 | 281 | 279
2019-07-19 19:30 | 279 | 277
2019-07-19 20:00 | 280 | 278
2019-07-19 20:30 | 282 | 280
2019-07-19 21:00 | 274 | 272
2019-07-19 21:30 | 265 | 263
2019-07-19 22:00 | 256 | 254
2019-07-19 22:30 | 249 | 246
2019-07-19 23:00 | 243 | 240
2019-07-19 23:30 | 229 | 227
2019-07-20 | 212 | 211
2019-07-20 00:30 | 196 | 195
2019-07-20 01:00 | 184 | 183
2019-07-20 01:30 | 176 | 175
2019-07-20 02:00 | 169 | 168
2019-07-20 02:30 | 164 | 164
2019-07-20 03:00 | 162 | 162
2019-07-20 03:30 | 161 | 161
2019-07-20 04:00 | 161 | 161
2019-07-20 04:30 | 162 | 162
2019-07-20 05:00 | 165 | 165
2019-07-20 05:30 | 172 | 172
2019-07-20 06:00 | 182 | 181
2019-07-20 06:30 | 196 | 195
2019-07-20 07:00 | 209 | 208
2019-07-20 07:30 | 223 | 221
2019-07-20 08:00 | 224 | 224
2019-07-20 08:30 | 219 | 219
2019-07-20 09:00 | 207 | 207
2019-07-20 09:30 | 194 | 194
2019-07-20 10:00 | 178 | 177
2019-07-20 10:30 | 164 | 163
2019-07-20 11:00 | 150 | 150
2019-07-20 11:30 | 141 | 141
2019-07-20 12:00 | 135 | 134
2019-07-20 12:30 | 131 | 130
2019-07-20 13:00 | 131 | 131
2019-07-20 13:30 | 134 | 133
2019-07-20 14:00 | 142 | 142
2019-07-20 14:30 | 149 | 149
2019-07-20 15:00 | 158 | 157
2019-07-20 15:30 | 168 | 167
2019-07-20 16:00 | 182 | 181
2019-07-20 16:30 | 198 | 196
2019-07-20 17:00 | 217 | 215
2019-07-20 17:30 | 233 | 233
2019-07-20 18:00 | 247 | 247
2019-07-20 18:30 | 251 | 251
2019-07-20 19:00 | 254 | 253
2019-07-20 19:30 | 250 | 249
2019-07-20 20:00 | 249 | 248
2019-07-20 20:30 | 248 | 248
2019-07-20 21:00 | 241 | 240
2019-07-20 21:30 | 234 | 233
2019-07-20 22:00 | 228 | 228
2019-07-20 22:30 | 223 | 221
2019-07-20 23:00 | 220 | 218
2019-07-20 23:30 | 209 | 207
2019-07-21 | 194 | 193
2019-07-21 00:30 | 179 | 178
2019-07-21 01:00 | 167 | 167
2019-07-21 01:30 | 160 | 160
2019-07-21 02:00 | 154 | 154
2019-07-21 02:30 | 149 | 149
2019-07-21 03:00 | 146 | 146
2019-07-21 03:30 | 145 | 145
2019-07-21 04:00 | 144 | 144
2019-07-21 04:30 | 144 | 144
2019-07-21 05:00 | 149 | 148
2019-07-21 05:30 | 154 | 152
2019-07-21 06:00 | 160 | 159
2019-07-21 06:30 | 170 | 168
2019-07-21 07:00 | 179 | 177
2019-07-21 07:30 | 189 | 187
2019-07-21 08:00 | 191 | 188
2019-07-21 08:30 | 183 | 183
2019-07-21 09:00 | 173 | 173
2019-07-21 09:30 | 162 | 162
2019-07-21 10:00 | 148 | 148
2019-07-21 10:30 | 136 | 136
2019-07-21 11:00 | 125 | 125
2019-07-21 11:30 | 118 | 118
2019-07-21 12:00 | 114 | 113
2019-07-21 12:30 | 110 | 109
2019-07-21 13:00 | 110 | 110
2019-07-21 13:30 | 114 | 113
2019-07-21 14:00 | 122 | 121
2019-07-21 14:30 | 130 | 130
2019-07-21 15:00 | 138 | 138
2019-07-21 15:30 | 150 | 150
2019-07-21 16:00 | 166 | 166
2019-07-21 16:30 | 194 | 194
2019-07-21 17:00 | 215 | 214
2019-07-21 17:30 | 231 | 230
2019-07-21 18:00 | 247 | 246
2019-07-21 18:30 | 253 | 252
2019-07-21 19:00 | 260 | 258
2019-07-21 19:30 | 257 | 256
2019-07-21 20:00 | 253 | 252
2019-07-21 20:30 | 251 | 250
2019-07-21 21:00 | 241 | 241
2019-07-21 21:30 | 232 | 232
2019-07-21 22:00 | 223 | 222
2019-07-21 22:30 | 215 | 214
2019-07-21 23:00 | 209 | 209
2019-07-21 23:30 | 196 | 196
2019-07-22 | 182 | 182
2019-07-22 00:30 | 169 | 169
2019-07-22 01:00 | 160 | 160
2019-07-22 01:30 | 155 | 154
2019-07-22 02:00 | 153 | 153
2019-07-22 02:30 | 149 | 149
2019-07-22 03:00 | 143 | 143
2019-07-22 03:30 | 142 | 142
2019-07-22 04:00 | 144 | 144
2019-07-22 04:30 | 151 | 151
2019-07-22 05:00 | 167 | 167
2019-07-22 05:30 | 183 | 182
2019-07-22 06:00 | 199 | 198
2019-07-22 06:30 | 230 | 230
2019-07-22 07:00 | 255 | 255
2019-07-22 07:30 | 274 | 274
2019-07-22 08:00 | 269 | 269
2019-07-22 08:30 | 251 | 251
2019-07-22 09:00 | 227 | 226
2019-07-22 09:30 | 204 | 204
2019-07-22 10:00 | 184 | 184
2019-07-22 10:30 | 172 | 172
2019-07-22 11:00 | 163 | 163
2019-07-22 11:30 | 163 | 163
2019-07-22 12:00 | 158 | 158
2019-07-22 12:30 | 154 | 154
2019-07-22 13:00 | 158 | 157
2019-07-22 13:30 | 166 | 165
2019-07-22 14:00 | 166 | 165
2019-07-22 14:30 | 169 | 168
2019-07-22 15:00 | 183 | 182
2019-07-22 15:30 | 198 | 197
2019-07-22 16:00 | 211 | 210
2019-07-22 16:30 | 224 | 224
2019-07-22 17:00 | 244 | 242
2019-07-22 17:30 | 262 | 262
2019-07-22 18:00 | 278 | 278
2019-07-22 18:30 | 279 | 279
2019-07-22 19:00 | 280 | 280
2019-07-22 19:30 | 275 | 275
2019-07-22 20:00 | 272 | 272
2019-07-22 20:30 | 271 | 271
2019-07-22 21:00 | 260 | 260
2019-07-22 21:30 | 249 | 249
2019-07-22 22:00 | 239 | 239
2019-07-22 22:30 | 229 | 229
2019-07-22 23:00 | 221 | 221
2019-07-22 23:30 | 209 | 208
2019-07-23 | 193 | 193
2019-07-23 00:30 | 179 | 179
2019-07-23 01:00 | 169 | 169
2019-07-23 01:30 | 161 | 161
2019-07-23 02:00 | 156 | 156
2019-07-23 02:30 | 153 | 153
2019-07-23 03:00 | 152 | 152
2019-07-23 03:30 | 152 | 152
2019-07-23 04:00 | 152 | 152
2019-07-23 04:30 | 158 | 158
2019-07-23 05:00 | 167 | 167
2019-07-23 05:30 | 183 | 183
2019-07-23 06:00 | 204 | 202
2019-07-23 06:30 | 233 | 232
2019-07-23 07:00 | 255 | 255
2019-07-23 07:30 | 270 | 269
2019-07-23 08:00 | 260 | 260
2019-07-23 08:30 | 239 | 239
2019-07-23 09:00 | 216 | 216
2019-07-23 09:30 | 201 | 200
2019-07-23 10:00 | 185 | 184
2019-07-23 10:30 | 173 | 172
2019-07-23 11:00 | 164 | 164
2019-07-23 11:30 | 158 | 158
2019-07-23 12:00 | 155 | 155
2019-07-23 12:30 | 156 | 155
2019-07-23 13:00 | 159 | 158
2019-07-23 13:30 | 164 | 163
2019-07-23 14:00 | 171 | 170
2019-07-23 14:30 | 178 | 177
2019-07-23 15:00 | 187 | 186
2019-07-23 15:30 | 198 | 197
2019-07-23 16:00 | 212 | 212
2019-07-23 16:30 | 228 | 228
2019-07-23 17:00 | 244 | 244
2019-07-23 17:30 | 258 | 258
2019-07-23 18:00 | 273 | 272
2019-07-23 18:30 | 274 | 273
2019-07-23 19:00 | 275 | 274
2019-07-23 19:30 | 270 | 270
2019-07-23 20:00 | 268 | 268
2019-07-23 20:30 | 267 | 267
2019-07-23 21:00 | 257 | 256
2019-07-23 21:30 | 245 | 245
2019-07-23 22:00 | 236 | 235
2019-07-23 22:30 | 229 | 229
2019-07-23 23:00 | 223 | 223
2019-07-23 23:30 | 210 | 210
2019-07-24 | 194 | 194
2019-07-24 00:30 | 180 | 179
2019-07-24 01:00 | 170 | 170
2019-07-24 01:30 | 163 | 163
2019-07-24 02:00 | 158 | 158
2019-07-24 02:30 | 155 | 155
2019-07-24 03:00 | 153 | 153
2019-07-24 03:30 | 153 | 153
2019-07-24 04:00 | 155 | 155
2019-07-24 04:30 | 161 | 161
2019-07-24 05:00 | 171 | 171
2019-07-24 05:30 | 188 | 188
2019-07-24 06:00 | 209 | 208
2019-07-24 06:30 | 239 | 236
2019-07-24 07:00 | 265 | 265
2019-07-24 07:30 | 279 | 279
2019-07-24 08:00 | 266 | 266
2019-07-24 08:30 | 242 | 242
2019-07-24 09:00 | 219 | 219
2019-07-24 09:30 | 200 | 200
2019-07-24 10:00 | 183 | 182
2019-07-24 10:30 | 171 | 170
2019-07-24 11:00 | 161 | 160
2019-07-24 11:30 | 154 | 153
2019-07-24 12:00 | 150 | 149
2019-07-24 12:30 | 150 | 149
2019-07-24 13:00 | 151 | 150
2019-07-24 13:30 | 157 | 156
2019-07-24 14:00 | 163 | 162
2019-07-24 14:30 | 173 | 172
2019-07-24 15:00 | 183 | 182
2019-07-24 15:30 | 195 | 193
2019-07-24 16:00 | 211 | 210
2019-07-24 16:30 | 227 | 226
2019-07-24 17:00 | 244 | 243
2019-07-24 17:30 | 257 | 257
2019-07-24 18:00 | 271 | 271
2019-07-24 18:30 | 274 | 274
2019-07-24 19:00 | 277 | 277
2019-07-24 19:30 | 273 | 273
2019-07-24 20:00 | 272 | 272
2019-07-24 20:30 | 272 | 272
2019-07-24 21:00 | 263 | 263
2019-07-24 21:30 | 253 | 253
2019-07-24 22:00 | 243 | 243
2019-07-24 22:30 | 234 | 234
2019-07-24 23:00 | 226 | 226
2019-07-24 23:30 | 213 | 213
2019-07-25 | 197 | 197
2019-07-25 00:30 | 182 | 182
2019-07-25 01:00 | 172 | 172
2019-07-25 01:30 | 164 | 164
2019-07-25 02:00 | 158 | 158
2019-07-25 02:30 | 155 | 155
2019-07-25 03:00 | 154 | 154
2019-07-25 03:30 | 155 | 155
2019-07-25 04:00 | 156 | 156
2019-07-25 04:30 | 162 | 162
2019-07-25 05:00 | 171 | 171
2019-07-25 05:30 | 188 | 188
2019-07-25 06:00 | 207 | 207
2019-07-25 06:30 | 236 | 235
2019-07-25 07:00 | 262 | 262
2019-07-25 07:30 | 277 | 277
2019-07-25 08:00 | 269 | 269
2019-07-25 08:30 | 249 | 249
2019-07-25 09:00 | 225 | 224
2019-07-25 09:30 | 205 | 204
2019-07-25 10:00 | 188 | 188
2019-07-25 10:30 | 178 | 178
2019-07-25 11:00 | 173 | 173
2019-07-25 11:30 | 172 | 172
2019-07-25 12:00 | 172 | 172
2019-07-25 12:30 | 172 | 172
2019-07-25 13:00 | 176 | 175
2019-07-25 13:30 | 181 | 181
2019-07-25 14:00 | 186 | 186
2019-07-25 14:30 | 189 | 189
2019-07-25 15:00 | 195 | 195
2019-07-25 15:30 | 200 | 200
2019-07-25 16:00 | 215 | 215
2019-07-25 16:30 | 227 | 227
2019-07-25 17:00 | 242 | 242
2019-07-25 17:30 | 257 | 257
2019-07-25 18:00 | 272 | 272
2019-07-25 18:30 | 275 | 275
2019-07-25 19:00 | 276 | 276
2019-07-25 19:30 | 271 | 271
2019-07-25 20:00 | 270 | 270
2019-07-25 20:30 | 268 | 268
2019-07-25 21:00 | 258 | 256
2019-07-25 21:30 | 245 | 244
2019-07-25 22:00 | 233 | 233
2019-07-25 22:30 | 225 | 225
2019-07-25 23:00 | 219 | 219
2019-07-25 23:30 | 205 | 205
2019-07-26 | 188 | 188
2019-07-26 00:30 | 173 | 173
2019-07-26 01:00 | 164 | 164
2019-07-26 01:30 | 158 | 157
2019-07-26 02:00 | 151 | 151
2019-07-26 02:30 | 148 | 148
2019-07-26 03:00 | 146 | 146
2019-07-26 03:30 | 146 | 146
2019-07-26 04:00 | 147 | 147
2019-07-26 04:30 | 152 | 152
2019-07-26 05:00 | 161 | 161
2019-07-26 05:30 | 176 | 176
2019-07-26 06:00 | 196 | 195
2019-07-26 06:30 | 223 | 222
2019-07-26 07:00 | 246 | 246
2019-07-26 07:30 | 261 | 261
2019-07-26 08:00 | 251 | 251
2019-07-26 08:30 | 233 | 233
2019-07-26 09:00 | 221 | 221
2019-07-26 09:30 | 202 | 201
2019-07-26 10:00 | 181 | 181
2019-07-26 10:30 | 168 | 168
2019-07-26 11:00 | 167 | 166
2019-07-26 11:30 | 168 | 167
2019-07-26 12:00 | 170 | 169
2019-07-26 12:30 | 166 | 166
2019-07-26 13:00 | 172 | 172
2019-07-26 13:30 | 175 | 174
2019-07-26 14:00 | 181 | 180
2019-07-26 14:30 | 182 | 181
2019-07-26 15:00 | 198 | 198
2019-07-26 15:30 | 200 | 199
2019-07-26 16:00 | 195 | 194
2019-07-26 16:30 | 207 | 207
2019-07-26 17:00 | 227 | 227
2019-07-26 17:30 | 245 | 244
2019-07-26 18:00 | 257 | 256
2019-07-26 18:30 | 258 | 257
2019-07-26 19:00 | 259 | 258
2019-07-26 19:30 | 254 | 253
2019-07-26 20:00 | 254 | 253
2019-07-26 20:30 | 253 | 252
2019-07-26 21:00 | 244 | 243
2019-07-26 21:30 | 235 | 234
2019-07-26 22:00 | 226 | 226
2019-07-26 22:30 | 221 | 221
2019-07-26 23:00 | 216 | 216
2019-07-26 23:30 | 203 | 203
2019-07-27 | 187 | 187
2019-07-27 00:30 | 172 | 171
2019-07-27 01:00 | 162 | 162
2019-07-27 01:30 | 155 | 154
2019-07-27 02:00 | 148 | 147
2019-07-27 02:30 | 145 | 143
2019-07-27 03:00 | 142 | 141
2019-07-27 03:30 | 142 | 140
2019-07-27 04:00 | 142 | 140
2019-07-27 04:30 | 143 | 142
2019-07-27 05:00 | 145 | 144
2019-07-27 05:30 | 152 | 151
2019-07-27 06:00 | 160 | 159
2019-07-27 06:30 | 170 | 170
2019-07-27 07:00 | 179 | 178
2019-07-27 07:30 | 186 | 186
2019-07-27 08:00 | 187 | 187
2019-07-27 08:30 | 183 | 183
2019-07-27 09:00 | 174 | 174
2019-07-27 09:30 | 164 | 164
2019-07-27 10:00 | 151 | 151
2019-07-27 10:30 | 139 | 139
2019-07-27 11:00 | 130 | 130
2019-07-27 11:30 | 126 | 125
2019-07-27 12:00 | 121 | 121
2019-07-27 12:30 | 118 | 118
2019-07-27 13:00 | 119 | 118
2019-07-27 13:30 | 123 | 123
2019-07-27 14:00 | 126 | 125
2019-07-27 14:30 | 133 | 132
2019-07-27 15:00 | 141 | 141
2019-07-27 15:30 | 155 | 155
2019-07-27 16:00 | 170 | 170
2019-07-27 16:30 | 183 | 183
2019-07-27 17:00 | 199 | 199
2019-07-27 17:30 | 210 | 210
2019-07-27 18:00 | 222 | 221
2019-07-27 18:30 | 225 | 224
2019-07-27 19:00 | 226 | 225
2019-07-27 19:30 | 221 | 221
2019-07-27 20:00 | 222 | 221
2019-07-27 20:30 | 222 | 221
2019-07-27 21:00 | 214 | 213
2019-07-27 21:30 | 208 | 207
2019-07-27 22:00 | 203 | 203
2019-07-27 22:30 | 202 | 202
2019-07-27 23:00 | 200 | 200
2019-07-27 23:30 | 191 | 191
2019-07-28 | 177 | 177
2019-07-28 00:30 | 163 | 163
2019-07-28 01:00 | 154 | 154
2019-07-28 01:30 | 146 | 146
2019-07-28 02:00 | 140 | 140
2019-07-28 02:30 | 137 | 135
2019-07-28 03:00 | 133 | 132
2019-07-28 03:30 | 134 | 133
2019-07-28 04:00 | 132 | 131
2019-07-28 04:30 | 133 | 132
2019-07-28 05:00 | 134 | 132
2019-07-28 05:30 | 138 | 137
2019-07-28 06:00 | 144 | 143
2019-07-28 06:30 | 151 | 150
2019-07-28 07:00 | 157 | 157
2019-07-28 07:30 | 163 | 163
2019-07-28 08:00 | 163 | 163
2019-07-28 08:30 | 161 | 160
2019-07-28 09:00 | 154 | 154
2019-07-28 09:30 | 146 | 146
2019-07-28 10:00 | 138 | 138
2019-07-28 10:30 | 130 | 130
2019-07-28 11:00 | 126 | 126
2019-07-28 11:30 | 124 | 124
2019-07-28 12:00 | 128 | 128
2019-07-28 12:30 | 124 | 124
2019-07-28 13:00 | 126 | 126
2019-07-28 13:30 | 134 | 134
2019-07-28 14:00 | 144 | 144
2019-07-28 14:30 | 157 | 157
2019-07-28 15:00 | 163 | 163
2019-07-28 15:30 | 169 | 169
2019-07-28 16:00 | 177 | 177
2019-07-28 16:30 | 188 | 188
2019-07-28 17:00 | 206 | 206
2019-07-28 17:30 | 222 | 222
2019-07-28 18:00 | 237 | 237
2019-07-28 18:30 | 242 | 242
2019-07-28 19:00 | 241 | 241
2019-07-28 19:30 | 235 | 235
2019-07-28 20:00 | 234 | 234
2019-07-28 20:30 | 234 | 234
2019-07-28 21:00 | 223 | 223
2019-07-28 21:30 | 214 | 214
2019-07-28 22:00 | 207 | 207
2019-07-28 22:30 | 200 | 200
2019-07-28 23:00 | 196 | 196
2019-07-28 23:30 | 185 | 185
2019-07-29 | 172 | 171
2019-07-29 00:30 | 159 | 158
2019-07-29 01:00 | 151 | 150
2019-07-29 01:30 | 145 | 144
2019-07-29 02:00 | 139 | 138
2019-07-29 02:30 | 137 | 136
2019-07-29 03:00 | 136 | 135
2019-07-29 03:30 | 136 | 135
2019-07-29 04:00 | 137 | 136
2019-07-29 04:30 | 143 | 142
2019-07-29 05:00 | 151 | 150
2019-07-29 05:30 | 166 | 166
2019-07-29 06:00 | 184 | 184
2019-07-29 06:30 | 210 | 209
2019-07-29 07:00 | 234 | 233
2019-07-29 07:30 | 246 | 244
2019-07-29 08:00 | 241 | 239
2019-07-29 08:30 | 224 | 223
2019-07-29 09:00 | 204 | 203
2019-07-29 09:30 | 188 | 188
2019-07-29 10:00 | 174 | 173
2019-07-29 10:30 | 165 | 164
2019-07-29 11:00 | 158 | 158
2019-07-29 11:30 | 163 | 162
2019-07-29 12:00 | 166 | 165
2019-07-29 12:30 | 165 | 164
2019-07-29 13:00 | 166 | 165
2019-07-29 13:30 | 168 | 167
2019-07-29 14:00 | 177 | 175
2019-07-29 14:30 | 186 | 184
2019-07-29 15:00 | 195 | 194
2019-07-29 15:30 | 201 | 200
2019-07-29 16:00 | 214 | 213
2019-07-29 16:30 | 225 | 224
2019-07-29 17:00 | 241 | 241
2019-07-29 17:30 | 258 | 258
2019-07-29 18:00 | 272 | 272
2019-07-29 18:30 | 274 | 274
2019-07-29 19:00 | 274 | 274
2019-07-29 19:30 | 268 | 268
2019-07-29 20:00 | 265 | 265
2019-07-29 20:30 | 262 | 261
2019-07-29 21:00 | 251 | 249
2019-07-29 21:30 | 240 | 239
2019-07-29 22:00 | 231 | 230
2019-07-29 22:30 | 222 | 222
2019-07-29 23:00 | 216 | 216
2019-07-29 23:30 | 204 | 204
2019-07-30 | 188 | 188
2019-07-30 00:30 | 174 | 173
2019-07-30 01:00 | 164 | 164
2019-07-30 01:30 | 158 | 157
2019-07-30 02:00 | 150 | 150
2019-07-30 02:30 | 147 | 146
2019-07-30 03:00 | 145 | 144
2019-07-30 03:30 | 147 | 146
2019-07-30 04:00 | 147 | 146
2019-07-30 04:30 | 151 | 151
2019-07-30 05:00 | 160 | 160
2019-07-30 05:30 | 178 | 178
2019-07-30 06:00 | 197 | 196
2019-07-30 06:30 | 226 | 226
2019-07-30 07:00 | 248 | 248
2019-07-30 07:30 | 262 | 261
2019-07-30 08:00 | 251 | 251
2019-07-30 08:30 | 231 | 231
2019-07-30 09:00 | 209 | 209
2019-07-30 09:30 | 193 | 193
2019-07-30 10:00 | 177 | 177
2019-07-30 10:30 | 167 | 167
2019-07-30 11:00 | 159 | 159
2019-07-30 11:30 | 158 | 157
2019-07-30 12:00 | 157 | 157
2019-07-30 12:30 | 158 | 158
2019-07-30 13:00 | 165 | 165
2019-07-30 13:30 | 168 | 168
2019-07-30 14:00 | 173 | 173
2019-07-30 14:30 | 183 | 183
2019-07-30 15:00 | 191 | 191
2019-07-30 15:30 | 201 | 201
2019-07-30 16:00 | 217 | 217
2019-07-30 16:30 | 234 | 234
2019-07-30 17:00 | 252 | 252
2019-07-30 17:30 | 264 | 264
2019-07-30 18:00 | 275 | 275
2019-07-30 18:30 | 276 | 276
2019-07-30 19:00 | 276 | 276
2019-07-30 19:30 | 270 | 270
2019-07-30 20:00 | 265 | 265
2019-07-30 20:30 | 263 | 261
2019-07-30 21:00 | 252 | 251
2019-07-30 21:30 | 239 | 239
2019-07-30 22:00 | 230 | 229
2019-07-30 22:30 | 222 | 222
2019-07-30 23:00 | 217 | 217
2019-07-30 23:30 | 204 | 204
2019-07-31 | 190 | 190
2019-07-31 00:30 | 176 | 175
2019-07-31 01:00 | 167 | 167
2019-07-31 01:30 | 160 | 160
2019-07-31 02:00 | 154 | 153
2019-07-31 02:30 | 151 | 150
2019-07-31 03:00 | 149 | 148
2019-07-31 03:30 | 150 | 150
2019-07-31 04:00 | 151 | 150
2019-07-31 04:30 | 156 | 156
2019-07-31 05:00 | 165 | 165
2019-07-31 05:30 | 181 | 181
2019-07-31 06:00 | 199 | 199
2019-07-31 06:30 | 226 | 226
2019-07-31 07:00 | 250 | 248
2019-07-31 07:30 | 262 | 262
2019-07-31 08:00 | 252 | 252
2019-07-31 08:30 | 234 | 234
2019-07-31 09:00 | 214 | 214
2019-07-31 09:30 | 198 | 198
2019-07-31 10:00 | 184 | 183
2019-07-31 10:30 | 174 | 173
2019-07-31 11:00 | 170 | 170
2019-07-31 11:30 | 170 | 170
2019-07-31 12:00 | 170 | 170
2019-07-31 12:30 | 171 | 171
2019-07-31 13:00 | 175 | 175
2019-07-31 13:30 | 181 | 181
2019-07-31 14:00 | 189 | 189
2019-07-31 14:30 | 200 | 200
2019-07-31 15:00 | 200 | 200
2019-07-31 15:30 | 207 | 207
2019-07-31 16:00 | 216 | 216
2019-07-31 16:30 | 226 | 226
2019-07-31 17:00 | 243 | 243
2019-07-31 17:30 | 260 | 260
2019-07-31 18:00 | 277 | 277
2019-07-31 18:30 | 280 | 280
2019-07-31 19:00 | 282 | 282
2019-07-31 19:30 | 277 | 277
2019-07-31 20:00 | 274 | 274
2019-07-31 20:30 | 273 | 273
2019-07-31 21:00 | 264 | 264
2019-07-31 21:30 | 254 | 254
2019-07-31 22:00 | 242 | 242
2019-07-31 22:30 | 232 | 231
2019-07-31 23:00 | 226 | 226
2019-07-31 23:30 | 212 | 212
2019-08-01 | 196 | 196
2019-08-01 00:30 | 181 | 181
2019-08-01 01:00 | 171 | 171
2019-08-01 01:30 | 164 | 164
2019-08-01 02:00 | 157 | 157
2019-08-01 02:30 | 154 | 154
2019-08-01 03:00 | 153 | 153
2019-08-01 03:30 | 153 | 153
2019-08-01 04:00 | 154 | 153
2019-08-01 04:30 | 159 | 158
2019-08-01 05:00 | 167 | 167
2019-08-01 05:30 | 182 | 182
2019-08-01 06:00 | 200 | 200
2019-08-01 06:30 | 226 | 225
2019-08-01 07:00 | 248 | 247
2019-08-01 07:30 | 261 | 261
2019-08-01 08:00 | 259 | 259
2019-08-01 08:30 | 243 | 243
2019-08-01 09:00 | 220 | 219
2019-08-01 09:30 | 205 | 205
2019-08-01 10:00 | 198 | 198
2019-08-01 10:30 | 197 | 197
2019-08-01 11:00 | 199 | 199
2019-08-01 11:30 | 202 | 202
2019-08-01 12:00 | 213 | 213
2019-08-01 12:30 | 214 | 214
2019-08-01 13:00 | 205 | 205
2019-08-01 13:30 | 197 | 197
2019-08-01 14:00 | 197 | 197
2019-08-01 14:30 | 198 | 198
2019-08-01 15:00 | 205 | 205
2019-08-01 15:30 | 211 | 211
2019-08-01 16:00 | 230 | 230
2019-08-01 16:30 | 239 | 239
2019-08-01 17:00 | 255 | 255
2019-08-01 17:30 | 268 | 268
2019-08-01 18:00 | 283 | 282
2019-08-01 18:30 | 288 | 287
2019-08-01 19:00 | 291 | 291
2019-08-01 19:30 | 288 | 287
2019-08-01 20:00 | 287 | 286
2019-08-01 20:30 | 287 | 286
2019-08-01 21:00 | 277 | 277
2019-08-01 21:30 | 263 | 262
2019-08-01 22:00 | 248 | 248
2019-08-01 22:30 | 235 | 235
2019-08-01 23:00 | 225 | 225
2019-08-01 23:30 | 209 | 209
2019-08-02 | 193 | 193
2019-08-02 00:30 | 176 | 176
2019-08-02 01:00 | 167 | 166
2019-08-02 01:30 | 160 | 159
2019-08-02 02:00 | 154 | 154
2019-08-02 02:30 | 152 | 151
2019-08-02 03:00 | 150 | 150
2019-08-02 03:30 | 151 | 150
2019-08-02 04:00 | 151 | 150
2019-08-02 04:30 | 155 | 155
2019-08-02 05:00 | 163 | 163
2019-08-02 05:30 | 179 | 179
2019-08-02 06:00 | 198 | 198
2019-08-02 06:30 | 225 | 225
2019-08-02 07:00 | 252 | 250
2019-08-02 07:30 | 264 | 264
2019-08-02 08:00 | 253 | 253
2019-08-02 08:30 | 234 | 234
2019-08-02 09:00 | 210 | 210
2019-08-02 09:30 | 193 | 193
2019-08-02 10:00 | 179 | 179
2019-08-02 10:30 | 168 | 167
2019-08-02 11:00 | 163 | 163
2019-08-02 11:30 | 171 | 170
2019-08-02 12:00 | 167 | 167
2019-08-02 12:30 | 168 | 167
2019-08-02 13:00 | 168 | 168
2019-08-02 13:30 | 170 | 170
2019-08-02 14:00 | 172 | 171
2019-08-02 14:30 | 175 | 175
2019-08-02 15:00 | 180 | 180
2019-08-02 15:30 | 190 | 190
2019-08-02 16:00 | 208 | 208
2019-08-02 16:30 | 224 | 223
2019-08-02 17:00 | 239 | 238
2019-08-02 17:30 | 250 | 249
2019-08-02 18:00 | 262 | 261
2019-08-02 18:30 | 264 | 264
2019-08-02 19:00 | 266 | 266
2019-08-02 19:30 | 262 | 262
2019-08-02 20:00 | 261 | 261
2019-08-02 20:30 | 263 | 263
2019-08-02 21:00 | 252 | 252
2019-08-02 21:30 | 242 | 242
2019-08-02 22:00 | 234 | 234
2019-08-02 22:30 | 230 | 230
2019-08-02 23:00 | 225 | 224
2019-08-02 23:30 | 209 | 209
2019-08-03 | 193 | 193
2019-08-03 00:30 | 178 | 178
2019-08-03 01:00 | 167 | 166
2019-08-03 01:30 | 159 | 159
2019-08-03 02:00 | 152 | 152
2019-08-03 02:30 | 148 | 148
2019-08-03 03:00 | 145 | 145
2019-08-03 03:30 | 143 | 143
2019-08-03 04:00 | 143 | 143
2019-08-03 04:30 | 146 | 146
2019-08-03 05:00 | 148 | 148
2019-08-03 05:30 | 153 | 153
2019-08-03 06:00 | 161 | 161
2019-08-03 06:30 | 173 | 173
2019-08-03 07:00 | 185 | 185
2019-08-03 07:30 | 192 | 192
2019-08-03 08:00 | 190 | 189
2019-08-03 08:30 | 184 | 183
2019-08-03 09:00 | 174 | 174
2019-08-03 09:30 | 162 | 161
2019-08-03 10:00 | 148 | 148
2019-08-03 10:30 | 136 | 136
2019-08-03 11:00 | 127 | 126
2019-08-03 11:30 | 123 | 123
2019-08-03 12:00 | 122 | 122
2019-08-03 12:30 | 123 | 122
2019-08-03 13:00 | 124 | 124
2019-08-03 13:30 | 126 | 126
2019-08-03 14:00 | 130 | 130
2019-08-03 14:30 | 140 | 140
2019-08-03 15:00 | 146 | 146
2019-08-03 15:30 | 153 | 153
2019-08-03 16:00 | 166 | 166
2019-08-03 16:30 | 182 | 182
2019-08-03 17:00 | 199 | 199
2019-08-03 17:30 | 212 | 212
2019-08-03 18:00 | 225 | 225
2019-08-03 18:30 | 232 | 232
2019-08-03 19:00 | 233 | 233
2019-08-03 19:30 | 230 | 230
2019-08-03 20:00 | 230 | 229
2019-08-03 20:30 | 229 | 229
2019-08-03 21:00 | 223 | 223
2019-08-03 21:30 | 217 | 216
2019-08-03 22:00 | 212 | 211
2019-08-03 22:30 | 209 | 209
2019-08-03 23:00 | 207 | 207
2019-08-03 23:30 | 197 | 197
2019-08-04 | 182 | 182
2019-08-04 00:30 | 169 | 168
2019-08-04 01:00 | 159 | 158
2019-08-04 01:30 | 152 | 151
2019-08-04 02:00 | 145 | 144
2019-08-04 02:30 | 141 | 141
2019-08-04 03:00 | 139 | 139
2019-08-04 03:30 | 138 | 138
2019-08-04 04:00 | 136 | 136
2019-08-04 04:30 | 138 | 138
2019-08-04 05:00 | 140 | 140
2019-08-04 05:30 | 145 | 145
2019-08-04 06:00 | 151 | 151
2019-08-04 06:30 | 159 | 159
2019-08-04 07:00 | 167 | 167
2019-08-04 07:30 | 173 | 173
2019-08-04 08:00 | 176 | 176
2019-08-04 08:30 | 180 | 180
2019-08-04 09:00 | 171 | 171
2019-08-04 09:30 | 160 | 160
2019-08-04 10:00 | 149 | 149
2019-08-04 10:30 | 138 | 138
2019-08-04 11:00 | 128 | 127
2019-08-04 11:30 | 118 | 117
2019-08-04 12:00 | 107 | 106
2019-08-04 12:30 | 104 | 103
2019-08-04 13:00 | 105 | 104
2019-08-04 13:30 | 109 | 108
2019-08-04 14:00 | 116 | 115
2019-08-04 14:30 | 122 | 121
2019-08-04 15:00 | 132 | 132
2019-08-04 15:30 | 145 | 145
2019-08-04 16:00 | 160 | 160
2019-08-04 16:30 | 179 | 179
2019-08-04 17:00 | 201 | 201
2019-08-04 17:30 | 219 | 219
2019-08-04 18:00 | 237 | 236
2019-08-04 18:30 | 245 | 244
2019-08-04 19:00 | 244 | 243
2019-08-04 19:30 | 241 | 240
2019-08-04 20:00 | 239 | 238
2019-08-04 20:30 | 239 | 238
2019-08-04 21:00 | 230 | 229
2019-08-04 21:30 | 220 | 220
2019-08-04 22:00 | 212 | 212
2019-08-04 22:30 | 206 | 206
2019-08-04 23:00 | 201 | 201
2019-08-04 23:30 | 190 | 190
2019-08-05 | 176 | 176
2019-08-05 00:30 | 164 | 164
2019-08-05 01:00 | 161 | 161
2019-08-05 01:30 | 155 | 155
2019-08-05 02:00 | 146 | 146
2019-08-05 02:30 | 142 | 142
2019-08-05 03:00 | 141 | 141
2019-08-05 03:30 | 141 | 141
2019-08-05 04:00 | 143 | 143
2019-08-05 04:30 | 149 | 149
2019-08-05 05:00 | 158 | 158
2019-08-05 05:30 | 175 | 174
2019-08-05 06:00 | 194 | 194
2019-08-05 06:30 | 223 | 223
2019-08-05 07:00 | 247 | 245
2019-08-05 07:30 | 258 | 257
2019-08-05 08:00 | 248 | 246
2019-08-05 08:30 | 237 | 236
2019-08-05 09:00 | 210 | 209
2019-08-05 09:30 | 192 | 191
2019-08-05 10:00 | 176 | 175
2019-08-05 10:30 | 167 | 167
2019-08-05 11:00 | 164 | 163
2019-08-05 11:30 | 163 | 162
2019-08-05 12:00 | 157 | 157
2019-08-05 12:30 | 155 | 155
2019-08-05 13:00 | 154 | 154
2019-08-05 13:30 | 158 | 157
2019-08-05 14:00 | 163 | 162
2019-08-05 14:30 | 173 | 171
2019-08-05 15:00 | 178 | 177
2019-08-05 15:30 | 189 | 188
2019-08-05 16:00 | 203 | 202
2019-08-05 16:30 | 219 | 218
2019-08-05 17:00 | 236 | 236
2019-08-05 17:30 | 252 | 252
2019-08-05 18:00 | 269 | 269
2019-08-05 18:30 | 275 | 274
2019-08-05 19:00 | 277 | 276
2019-08-05 19:30 | 271 | 270
2019-08-05 20:00 | 269 | 267
2019-08-05 20:30 | 268 | 267
2019-08-05 21:00 | 257 | 257
2019-08-05 21:30 | 245 | 244
2019-08-05 22:00 | 233 | 233
2019-08-05 22:30 | 224 | 223
2019-08-05 23:00 | 220 | 219
2019-08-05 23:30 | 208 | 206
2019-08-06 | 191 | 191
2019-08-06 00:30 | 176 | 175
2019-08-06 01:00 | 165 | 165
2019-08-06 01:30 | 161 | 161
2019-08-06 02:00 | 156 | 156
2019-08-06 02:30 | 153 | 153
2019-08-06 03:00 | 153 | 153
2019-08-06 03:30 | 150 | 150
2019-08-06 04:00 | 151 | 150
2019-08-06 04:30 | 157 | 157
2019-08-06 05:00 | 167 | 166
2019-08-06 05:30 | 186 | 184
2019-08-06 06:00 | 211 | 210
2019-08-06 06:30 | 240 | 239
2019-08-06 07:00 | 265 | 264
2019-08-06 07:30 | 273 | 273
2019-08-06 08:00 | 262 | 262
2019-08-06 08:30 | 240 | 240
2019-08-06 09:00 | 216 | 216
2019-08-06 09:30 | 197 | 197
2019-08-06 10:00 | 183 | 182
2019-08-06 10:30 | 171 | 169
2019-08-06 11:00 | 163 | 161
2019-08-06 11:30 | 156 | 154
2019-08-06 12:00 | 153 | 152
2019-08-06 12:30 | 154 | 152
2019-08-06 13:00 | 159 | 158
2019-08-06 13:30 | 167 | 165
2019-08-06 14:00 | 175 | 173
2019-08-06 14:30 | 178 | 177
2019-08-06 15:00 | 183 | 182
2019-08-06 15:30 | 193 | 191
2019-08-06 16:00 | 207 | 206
2019-08-06 16:30 | 222 | 221
2019-08-06 17:00 | 240 | 239
2019-08-06 17:30 | 255 | 254
2019-08-06 18:00 | 272 | 270
2019-08-06 18:30 | 277 | 275
2019-08-06 19:00 | 279 | 277
2019-08-06 19:30 | 273 | 272
2019-08-06 20:00 | 271 | 270
2019-08-06 20:30 | 271 | 270
2019-08-06 21:00 | 260 | 259
2019-08-06 21:30 | 248 | 247
2019-08-06 22:00 | 237 | 236
2019-08-06 22:30 | 229 | 228
2019-08-06 23:00 | 223 | 223
2019-08-06 23:30 | 210 | 209
2019-08-07 | 194 | 194
2019-08-07 00:30 | 179 | 179
2019-08-07 01:00 | 170 | 169
2019-08-07 01:30 | 163 | 163
2019-08-07 02:00 | 158 | 158
2019-08-07 02:30 | 154 | 154
2019-08-07 03:00 | 152 | 152
2019-08-07 03:30 | 153 | 152
2019-08-07 04:00 | 154 | 152
2019-08-07 04:30 | 159 | 158
2019-08-07 05:00 | 166 | 166
2019-08-07 05:30 | 182 | 182
2019-08-07 06:00 | 199 | 199
2019-08-07 06:30 | 226 | 226
2019-08-07 07:00 | 249 | 249
2019-08-07 07:30 | 268 | 267
2019-08-07 08:00 | 273 | 270
2019-08-07 08:30 | 268 | 265
2019-08-07 09:00 | 257 | 255
2019-08-07 09:30 | 248 | 246
2019-08-07 10:00 | 235 | 233
2019-08-07 10:30 | 218 | 217
2019-08-07 11:00 | 197 | 197
2019-08-07 11:30 | 182 | 182
2019-08-07 12:00 | 181 | 181
2019-08-07 12:30 | 175 | 175
2019-08-07 13:00 | 187 | 186
2019-08-07 13:30 | 202 | 201
2019-08-07 14:00 | 216 | 215
2019-08-07 14:30 | 221 | 220
2019-08-07 15:00 | 226 | 225
2019-08-07 15:30 | 231 | 231
2019-08-07 16:00 | 240 | 239
2019-08-07 16:30 | 248 | 247
2019-08-07 17:00 | 262 | 261
2019-08-07 17:30 | 273 | 272
2019-08-07 18:00 | 283 | 282
2019-08-07 18:30 | 285 | 285
2019-08-07 19:00 | 285 | 285
2019-08-07 19:30 | 278 | 278
2019-08-07 20:00 | 276 | 276
2019-08-07 20:30 | 274 | 274
2019-08-07 21:00 | 264 | 264
2019-08-07 21:30 | 252 | 252
2019-08-07 22:00 | 240 | 240
2019-08-07 22:30 | 232 | 232
2019-08-07 23:00 | 225 | 225
2019-08-07 23:30 | 210 | 210
2019-08-08 | 194 | 194
2019-08-08 00:30 | 178 | 178
2019-08-08 01:00 | 168 | 168
2019-08-08 01:30 | 161 | 161
2019-08-08 02:00 | 156 | 156
2019-08-08 02:30 | 152 | 152
2019-08-08 03:00 | 151 | 150
2019-08-08 03:30 | 150 | 150
2019-08-08 04:00 | 151 | 150
2019-08-08 04:30 | 156 | 155
2019-08-08 05:00 | 164 | 164
2019-08-08 05:30 | 178 | 178
2019-08-08 06:00 | 195 | 195
2019-08-08 06:30 | 221 | 221
2019-08-08 07:00 | 243 | 243
2019-08-08 07:30 | 251 | 250
2019-08-08 08:00 | 242 | 242
2019-08-08 08:30 | 224 | 224
2019-08-08 09:00 | 207 | 207
2019-08-08 09:30 | 215 | 215
2019-08-08 10:00 | 208 | 208
2019-08-08 10:30 | 178 | 177
2019-08-08 11:00 | 156 | 155
2019-08-08 11:30 | 147 | 147
2019-08-08 12:00 | 143 | 143
2019-08-08 12:30 | 144 | 144
2019-08-08 13:00 | 146 | 145
2019-08-08 13:30 | 156 | 155
2019-08-08 14:00 | 161 | 161
2019-08-08 14:30 | 165 | 165
2019-08-08 15:00 | 176 | 176
2019-08-08 15:30 | 198 | 198
2019-08-08 16:00 | 211 | 211
2019-08-08 16:30 | 224 | 224
2019-08-08 17:00 | 234 | 234
2019-08-08 17:30 | 245 | 245
2019-08-08 18:00 | 260 | 259
2019-08-08 18:30 | 265 | 264
2019-08-08 19:00 | 265 | 265
2019-08-08 19:30 | 258 | 258
2019-08-08 20:00 | 256 | 256
2019-08-08 20:30 | 254 | 254
2019-08-08 21:00 | 243 | 243
2019-08-08 21:30 | 231 | 230
2019-08-08 22:00 | 220 | 220
2019-08-08 22:30 | 213 | 213
2019-08-08 23:00 | 208 | 208
2019-08-08 23:30 | 195 | 195
2019-08-09 | 180 | 180
2019-08-09 00:30 | 167 | 167
2019-08-09 01:00 | 158 | 158
2019-08-09 01:30 | 151 | 151
2019-08-09 02:00 | 145 | 145
2019-08-09 02:30 | 143 | 142
2019-08-09 03:00 | 141 | 141
2019-08-09 03:30 | 143 | 142
2019-08-09 04:00 | 143 | 143
2019-08-09 04:30 | 147 | 147
2019-08-09 05:00 | 155 | 155
2019-08-09 05:30 | 172 | 172
2019-08-09 06:00 | 187 | 187
2019-08-09 06:30 | 210 | 209
2019-08-09 07:00 | 229 | 228
2019-08-09 07:30 | 238 | 236
2019-08-09 08:00 | 227 | 225
2019-08-09 08:30 | 206 | 206
2019-08-09 09:00 | 187 | 186
2019-08-09 09:30 | 173 | 172
2019-08-09 10:00 | 159 | 158
2019-08-09 10:30 | 148 | 148
2019-08-09 11:00 | 141 | 141
2019-08-09 11:30 | 135 | 134
2019-08-09 12:00 | 132 | 132
2019-08-09 12:30 | 131 | 130
2019-08-09 13:00 | 131 | 131
2019-08-09 13:30 | 134 | 134
2019-08-09 14:00 | 141 | 141
2019-08-09 14:30 | 149 | 148
2019-08-09 15:00 | 160 | 159
2019-08-09 15:30 | 170 | 170
2019-08-09 16:00 | 186 | 186
2019-08-09 16:30 | 203 | 203
2019-08-09 17:00 | 221 | 220
2019-08-09 17:30 | 232 | 232
2019-08-09 18:00 | 247 | 247
2019-08-09 18:30 | 253 | 253
2019-08-09 19:00 | 254 | 254
2019-08-09 19:30 | 248 | 248
2019-08-09 20:00 | 245 | 245
2019-08-09 20:30 | 246 | 246
2019-08-09 21:00 | 239 | 239
2019-08-09 21:30 | 230 | 230
2019-08-09 22:00 | 221 | 220
2019-08-09 22:30 | 217 | 217
2019-08-09 23:00 | 210 | 209
2019-08-09 23:30 | 198 | 197
2019-08-10 | 183 | 183
2019-08-10 00:30 | 168 | 168
2019-08-10 01:00 | 158 | 158
2019-08-10 01:30 | 151 | 151
2019-08-10 02:00 | 144 | 144
2019-08-10 02:30 | 141 | 141
2019-08-10 03:00 | 139 | 138
2019-08-10 03:30 | 137 | 137
2019-08-10 04:00 | 137 | 136
2019-08-10 04:30 | 138 | 137
2019-08-10 05:00 | 141 | 140
2019-08-10 05:30 | 146 | 146
2019-08-10 06:00 | 153 | 153
2019-08-10 06:30 | 162 | 162
2019-08-10 07:00 | 171 | 171
2019-08-10 07:30 | 175 | 175
2019-08-10 08:00 | 171 | 171
2019-08-10 08:30 | 167 | 167
2019-08-10 09:00 | 156 | 156
2019-08-10 09:30 | 146 | 146
2019-08-10 10:00 | 134 | 134
2019-08-10 10:30 | 124 | 124
2019-08-10 11:00 | 115 | 115
2019-08-10 11:30 | 107 | 107
2019-08-10 12:00 | 101 | 101
2019-08-10 12:30 | 99 | 99
2019-08-10 13:00 | 99 | 99
2019-08-10 13:30 | 101 | 101
2019-08-10 14:00 | 107 | 107
2019-08-10 14:30 | 115 | 115
2019-08-10 15:00 | 126 | 126
2019-08-10 15:30 | 139 | 139
2019-08-10 16:00 | 156 | 156
2019-08-10 16:30 | 175 | 175
2019-08-10 17:00 | 194 | 194
2019-08-10 17:30 | 207 | 207
2019-08-10 18:00 | 223 | 222
2019-08-10 18:30 | 231 | 231
2019-08-10 19:00 | 232 | 232
2019-08-10 19:30 | 229 | 229
2019-08-10 20:00 | 226 | 225
2019-08-10 20:30 | 227 | 226
2019-08-10 21:00 | 220 | 220
2019-08-10 21:30 | 215 | 214
2019-08-10 22:00 | 207 | 207
2019-08-10 22:30 | 203 | 203
2019-08-10 23:00 | 202 | 202
2019-08-10 23:30 | 192 | 192
2019-08-11 | 178 | 178
2019-08-11 00:30 | 166 | 166
2019-08-11 01:00 | 157 | 156
2019-08-11 01:30 | 149 | 148
2019-08-11 02:00 | 143 | 142
2019-08-11 02:30 | 140 | 139
2019-08-11 03:00 | 136 | 135
2019-08-11 03:30 | 135 | 135
2019-08-11 04:00 | 134 | 134
2019-08-11 04:30 | 135 | 135
2019-08-11 05:00 | 137 | 137
2019-08-11 05:30 | 142 | 142
2019-08-11 06:00 | 147 | 147
2019-08-11 06:30 | 156 | 156
2019-08-11 07:00 | 164 | 164
2019-08-11 07:30 | 167 | 167
2019-08-11 08:00 | 166 | 166
2019-08-11 08:30 | 163 | 163
2019-08-11 09:00 | 154 | 154
2019-08-11 09:30 | 144 | 144
2019-08-11 10:00 | 132 | 132
2019-08-11 10:30 | 121 | 121
2019-08-11 11:00 | 111 | 111
2019-08-11 11:30 | 103 | 103
2019-08-11 12:00 | 98 | 98
2019-08-11 12:30 | 97 | 97
2019-08-11 13:00 | 97 | 97
2019-08-11 13:30 | 99 | 99
2019-08-11 14:00 | 104 | 104
2019-08-11 14:30 | 112 | 112
2019-08-11 15:00 | 124 | 124
2019-08-11 15:30 | 140 | 140
2019-08-11 16:00 | 158 | 158
2019-08-11 16:30 | 178 | 177
2019-08-11 17:00 | 200 | 200
2019-08-11 17:30 | 219 | 219
2019-08-11 18:00 | 240 | 239
2019-08-11 18:30 | 250 | 250
2019-08-11 19:00 | 252 | 251
2019-08-11 19:30 | 249 | 248
2019-08-11 20:00 | 248 | 247
2019-08-11 20:30 | 248 | 248
2019-08-11 21:00 | 239 | 239
2019-08-11 21:30 | 231 | 230
2019-08-11 22:00 | 220 | 220
2019-08-11 22:30 | 213 | 213
2019-08-11 23:00 | 206 | 206
2019-08-11 23:30 | 195 | 195
2019-08-12 | 180 | 180
2019-08-12 00:30 | 166 | 166
2019-08-12 01:00 | 157 | 156
2019-08-12 01:30 | 150 | 149
2019-08-12 02:00 | 144 | 144
2019-08-12 02:30 | 141 | 141
2019-08-12 03:00 | 139 | 139
2019-08-12 03:30 | 140 | 140
2019-08-12 04:00 | 141 | 141
2019-08-12 04:30 | 147 | 147
2019-08-12 05:00 | 155 | 155
2019-08-12 05:30 | 169 | 169
2019-08-12 06:00 | 186 | 185
2019-08-12 06:30 | 208 | 208
2019-08-12 07:00 | 227 | 227
2019-08-12 07:30 | 234 | 234
2019-08-12 08:00 | 225 | 224
2019-08-12 08:30 | 211 | 211
2019-08-12 09:00 | 192 | 192
2019-08-12 09:30 | 177 | 177
2019-08-12 10:00 | 162 | 162
2019-08-12 10:30 | 148 | 148
2019-08-12 11:00 | 137 | 137
2019-08-12 11:30 | 131 | 131
2019-08-12 12:00 | 127 | 127
2019-08-12 12:30 | 125 | 125
2019-08-12 13:00 | 126 | 126
2019-08-12 13:30 | 130 | 130
2019-08-12 14:00 | 136 | 136
2019-08-12 14:30 | 144 | 144
2019-08-12 15:00 | 154 | 154
2019-08-12 15:30 | 167 | 167
2019-08-12 16:00 | 186 | 186
2019-08-12 16:30 | 206 | 206
2019-08-12 17:00 | 230 | 229
2019-08-12 17:30 | 248 | 248
2019-08-12 18:00 | 271 | 270
2019-08-12 18:30 | 282 | 280
2019-08-12 19:00 | 284 | 282
2019-08-12 19:30 | 279 | 277
2019-08-12 20:00 | 279 | 277
2019-08-12 20:30 | 280 | 279
2019-08-12 21:00 | 267 | 267
2019-08-12 21:30 | 253 | 253
2019-08-12 22:00 | 241 | 240
2019-08-12 22:30 | 232 | 232
2019-08-12 23:00 | 225 | 225
2019-08-12 23:30 | 211 | 211
2019-08-13 | 195 | 195
2019-08-13 00:30 | 180 | 180
2019-08-13 01:00 | 171 | 171
2019-08-13 01:30 | 164 | 164
2019-08-13 02:00 | 157 | 157
2019-08-13 02:30 | 154 | 154
2019-08-13 03:00 | 152 | 152
2019-08-13 03:30 | 153 | 153
2019-08-13 04:00 | 154 | 154
2019-08-13 04:30 | 161 | 161
2019-08-13 05:00 | 171 | 170
2019-08-13 05:30 | 190 | 189
2019-08-13 06:00 | 211 | 210
2019-08-13 06:30 | 243 | 242
2019-08-13 07:00 | 269 | 269
2019-08-13 07:30 | 279 | 279
2019-08-13 08:00 | 266 | 266
2019-08-13 08:30 | 240 | 240
2019-08-13 09:00 | 217 | 217
2019-08-13 09:30 | 199 | 198
2019-08-13 10:00 | 181 | 180
2019-08-13 10:30 | 168 | 168
2019-08-13 11:00 | 161 | 160
2019-08-13 11:30 | 155 | 154
2019-08-13 12:00 | 157 | 156
2019-08-13 12:30 | 164 | 163
2019-08-13 13:00 | 163 | 163
2019-08-13 13:30 | 165 | 164
2019-08-13 14:00 | 171 | 170
2019-08-13 14:30 | 176 | 176
2019-08-13 15:00 | 184 | 184
2019-08-13 15:30 | 192 | 191
2019-08-13 16:00 | 204 | 204
2019-08-13 16:30 | 217 | 217
2019-08-13 17:00 | 236 | 236
2019-08-13 17:30 | 254 | 253
2019-08-13 18:00 | 274 | 274
2019-08-13 18:30 | 279 | 279
2019-08-13 19:00 | 285 | 284
2019-08-13 19:30 | 281 | 281
2019-08-13 20:00 | 280 | 279
2019-08-13 20:30 | 279 | 278
2019-08-13 21:00 | 266 | 266
2019-08-13 21:30 | 255 | 255
2019-08-13 22:00 | 244 | 244
2019-08-13 22:30 | 235 | 235
2019-08-13 23:00 | 229 | 227
2019-08-13 23:30 | 214 | 213
2019-08-14 | 196 | 196
2019-08-14 00:30 | 181 | 181
2019-08-14 01:00 | 171 | 171
2019-08-14 01:30 | 165 | 164
2019-08-14 02:00 | 158 | 157
2019-08-14 02:30 | 155 | 154
2019-08-14 03:00 | 153 | 153
2019-08-14 03:30 | 153 | 153
2019-08-14 04:00 | 154 | 154
2019-08-14 04:30 | 158 | 158
2019-08-14 05:00 | 165 | 164
2019-08-14 05:30 | 177 | 176
2019-08-14 06:00 | 192 | 190
2019-08-14 06:30 | 213 | 213
2019-08-14 07:00 | 232 | 231
2019-08-14 07:30 | 243 | 242
2019-08-14 08:00 | 236 | 235
2019-08-14 08:30 | 221 | 220
2019-08-14 09:00 | 201 | 200
2019-08-14 09:30 | 186 | 186
2019-08-14 10:00 | 176 | 175
2019-08-14 10:30 | 172 | 172
2019-08-14 11:00 | 166 | 166
2019-08-14 11:30 | 167 | 167
2019-08-14 12:00 | 167 | 167
2019-08-14 12:30 | 170 | 169
2019-08-14 13:00 | 178 | 178
2019-08-14 13:30 | 185 | 185
2019-08-14 14:00 | 181 | 181
2019-08-14 14:30 | 183 | 183
2019-08-14 15:00 | 190 | 190
2019-08-14 15:30 | 201 | 201
2019-08-14 16:00 | 212 | 212
2019-08-14 16:30 | 219 | 219
2019-08-14 17:00 | 230 | 230
2019-08-14 17:30 | 244 | 244
2019-08-14 18:00 | 263 | 262
2019-08-14 18:30 | 273 | 273
2019-08-14 19:00 | 276 | 276
2019-08-14 19:30 | 273 | 273
2019-08-14 20:00 | 273 | 273
2019-08-14 20:30 | 273 | 273
2019-08-14 21:00 | 262 | 262
2019-08-14 21:30 | 250 | 250
2019-08-14 22:00 | 240 | 239
2019-08-14 22:30 | 229 | 229
2019-08-14 23:00 | 222 | 222
2019-08-14 23:30 | 210 | 210
2019-08-15 | 193 | 193
2019-08-15 00:30 | 179 | 179
2019-08-15 01:00 | 169 | 169
2019-08-15 01:30 | 161 | 161
2019-08-15 02:00 | 156 | 156
2019-08-15 02:30 | 153 | 152
2019-08-15 03:00 | 151 | 151
2019-08-15 03:30 | 153 | 152
2019-08-15 04:00 | 154 | 153
2019-08-15 04:30 | 160 | 159
2019-08-15 05:00 | 170 | 169
2019-08-15 05:30 | 189 | 187
2019-08-15 06:00 | 210 | 206
2019-08-15 06:30 | 238 | 238
2019-08-15 07:00 | 263 | 263
2019-08-15 07:30 | 272 | 271
2019-08-15 08:00 | 257 | 257
2019-08-15 08:30 | 232 | 232
2019-08-15 09:00 | 208 | 208
2019-08-15 09:30 | 188 | 188
2019-08-15 10:00 | 171 | 171
2019-08-15 10:30 | 160 | 157
2019-08-15 11:00 | 150 | 148
2019-08-15 11:30 | 144 | 142
2019-08-15 12:00 | 143 | 140
2019-08-15 12:30 | 145 | 143
2019-08-15 13:00 | 150 | 149
2019-08-15 13:30 | 156 | 156
2019-08-15 14:00 | 159 | 159
2019-08-15 14:30 | 163 | 163
2019-08-15 15:00 | 170 | 170
2019-08-15 15:30 | 182 | 181
2019-08-15 16:00 | 196 | 196
2019-08-15 16:30 | 212 | 212
2019-08-15 17:00 | 232 | 231
2019-08-15 17:30 | 246 | 245
2019-08-15 18:00 | 265 | 262
2019-08-15 18:30 | 274 | 271
2019-08-15 19:00 | 277 | 274
2019-08-15 19:30 | 273 | 271
2019-08-15 20:00 | 272 | 270
2019-08-15 20:30 | 272 | 269
2019-08-15 21:00 | 261 | 259
2019-08-15 21:30 | 250 | 248
2019-08-15 22:00 | 238 | 237
2019-08-15 22:30 | 230 | 230
2019-08-15 23:00 | 223 | 222
2019-08-15 23:30 | 209 | 209
2019-08-16 | 192 | 192
2019-08-16 00:30 | 177 | 176
2019-08-16 01:00 | 167 | 167
2019-08-16 01:30 | 160 | 160
2019-08-16 02:00 | 155 | 155
2019-08-16 02:30 | 151 | 151
2019-08-16 03:00 | 149 | 149
2019-08-16 03:30 | 151 | 150
2019-08-16 04:00 | 151 | 150
2019-08-16 04:30 | 157 | 156
2019-08-16 05:00 | 166 | 164
2019-08-16 05:30 | 182 | 180
2019-08-16 06:00 | 199 | 198
2019-08-16 06:30 | 222 | 222
2019-08-16 07:00 | 243 | 242
2019-08-16 07:30 | 255 | 255
2019-08-16 08:00 | 250 | 250
2019-08-16 08:30 | 235 | 235
2019-08-16 09:00 | 209 | 209
2019-08-16 09:30 | 187 | 186
2019-08-16 10:00 | 170 | 169
2019-08-16 10:30 | 158 | 157
2019-08-16 11:00 | 149 | 148
2019-08-16 11:30 | 143 | 142
2019-08-16 12:00 | 140 | 139
2019-08-16 12:30 | 139 | 138
2019-08-16 13:00 | 140 | 140
2019-08-16 13:30 | 147 | 147
2019-08-16 14:00 | 157 | 156
2019-08-16 14:30 | 166 | 166
2019-08-16 15:00 | 173 | 173
2019-08-16 15:30 | 182 | 181
2019-08-16 16:00 | 194 | 193
2019-08-16 16:30 | 210 | 210
2019-08-16 17:00 | 226 | 226
2019-08-16 17:30 | 237 | 237
2019-08-16 18:00 | 247 | 247
2019-08-16 18:30 | 251 | 251
2019-08-16 19:00 | 252 | 252
2019-08-16 19:30 | 249 | 249
2019-08-16 20:00 | 248 | 247
2019-08-16 20:30 | 246 | 246
2019-08-16 21:00 | 238 | 238
2019-08-16 21:30 | 231 | 231
2019-08-16 22:00 | 223 | 223
2019-08-16 22:30 | 218 | 218
2019-08-16 23:00 | 215 | 215
2019-08-16 23:30 | 203 | 203
2019-08-17 | 188 | 187
2019-08-17 00:30 | 173 | 172
2019-08-17 01:00 | 164 | 163
2019-08-17 01:30 | 156 | 155
2019-08-17 02:00 | 149 | 148
2019-08-17 02:30 | 145 | 144
2019-08-17 03:00 | 143 | 142
2019-08-17 03:30 | 141 | 141
2019-08-17 04:00 | 140 | 140
2019-08-17 04:30 | 142 | 142
2019-08-17 05:00 | 144 | 144
2019-08-17 05:30 | 151 | 151
2019-08-17 06:00 | 158 | 158
2019-08-17 06:30 | 168 | 168
2019-08-17 07:00 | 177 | 177
2019-08-17 07:30 | 181 | 181
2019-08-17 08:00 | 176 | 176
2019-08-17 08:30 | 170 | 170
2019-08-17 09:00 | 160 | 160
2019-08-17 09:30 | 147 | 147
2019-08-17 10:00 | 136 | 136
2019-08-17 10:30 | 124 | 123
2019-08-17 11:00 | 115 | 115
2019-08-17 11:30 | 110 | 110
2019-08-17 12:00 | 106 | 106
2019-08-17 12:30 | 104 | 103
2019-08-17 13:00 | 103 | 103
2019-08-17 13:30 | 107 | 107
2019-08-17 14:00 | 112 | 112
2019-08-17 14:30 | 120 | 120
2019-08-17 15:00 | 130 | 130
2019-08-17 15:30 | 144 | 144
2019-08-17 16:00 | 160 | 160
2019-08-17 16:30 | 176 | 175
2019-08-17 17:00 | 193 | 193
2019-08-17 17:30 | 203 | 203
2019-08-17 18:00 | 213 | 213
2019-08-17 18:30 | 221 | 221
2019-08-17 19:00 | 223 | 223
2019-08-17 19:30 | 217 | 217
2019-08-17 20:00 | 216 | 216
2019-08-17 20:30 | 216 | 215
2019-08-17 21:00 | 208 | 208
2019-08-17 21:30 | 203 | 203
2019-08-17 22:00 | 198 | 198
2019-08-17 22:30 | 197 | 197
2019-08-17 23:00 | 195 | 195
2019-08-17 23:30 | 186 | 186
2019-08-18 | 173 | 173
2019-08-18 00:30 | 161 | 160
2019-08-18 01:00 | 152 | 152
2019-08-18 01:30 | 146 | 145
2019-08-18 02:00 | 141 | 139
2019-08-18 02:30 | 138 | 136
2019-08-18 03:00 | 135 | 133
2019-08-18 03:30 | 134 | 132
2019-08-18 04:00 | 133 | 131
2019-08-18 04:30 | 134 | 132
2019-08-18 05:00 | 135 | 133
2019-08-18 05:30 | 139 | 137
2019-08-18 06:00 | 144 | 142
2019-08-18 06:30 | 148 | 146
2019-08-18 07:00 | 152 | 150
2019-08-18 07:30 | 153 | 152
2019-08-18 08:00 | 149 | 148
2019-08-18 08:30 | 144 | 143
2019-08-18 09:00 | 140 | 138
2019-08-18 09:30 | 134 | 132
2019-08-18 10:00 | 128 | 127
2019-08-18 10:30 | 134 | 133
2019-08-18 11:00 | 130 | 130
2019-08-18 11:30 | 129 | 128
2019-08-18 12:00 | 125 | 124
2019-08-18 12:30 | 123 | 122
2019-08-18 13:00 | 118 | 118
2019-08-18 13:30 | 120 | 119
2019-08-18 14:00 | 125 | 125
2019-08-18 14:30 | 129 | 129
2019-08-18 15:00 | 137 | 137
2019-08-18 15:30 | 151 | 151
2019-08-18 16:00 | 166 | 164
2019-08-18 16:30 | 183 | 182
2019-08-18 17:00 | 202 | 202
2019-08-18 17:30 | 218 | 217
2019-08-18 18:00 | 233 | 233
2019-08-18 18:30 | 242 | 242
2019-08-18 19:00 | 241 | 241
2019-08-18 19:30 | 235 | 235
2019-08-18 20:00 | 232 | 232
2019-08-18 20:30 | 232 | 231
2019-08-18 21:00 | 223 | 223
2019-08-18 21:30 | 215 | 215
2019-08-18 22:00 | 208 | 208
2019-08-18 22:30 | 203 | 203
2019-08-18 23:00 | 200 | 200
2019-08-18 23:30 | 191 | 190
2019-08-19 | 178 | 176
2019-08-19 00:30 | 167 | 164
2019-08-19 01:00 | 159 | 156
2019-08-19 01:30 | 153 | 149
2019-08-19 02:00 | 148 | 144
2019-08-19 02:30 | 146 | 141
2019-08-19 03:00 | 144 | 140
2019-08-19 03:30 | 144 | 141
2019-08-19 04:00 | 143 | 141
2019-08-19 04:30 | 147 | 146
2019-08-19 05:00 | 156 | 155
2019-08-19 05:30 | 171 | 170
2019-08-19 06:00 | 187 | 187
2019-08-19 06:30 | 211 | 211
2019-08-19 07:00 | 229 | 229
2019-08-19 07:30 | 242 | 242
2019-08-19 08:00 | 236 | 236
2019-08-19 08:30 | 217 | 217
2019-08-19 09:00 | 194 | 194
2019-08-19 09:30 | 177 | 177
2019-08-19 10:00 | 166 | 166
2019-08-19 10:30 | 157 | 157
2019-08-19 11:00 | 152 | 152
2019-08-19 11:30 | 147 | 146
2019-08-19 12:00 | 145 | 145
2019-08-19 12:30 | 146 | 146
2019-08-19 13:00 | 149 | 149
2019-08-19 13:30 | 155 | 155
2019-08-19 14:00 | 164 | 163
2019-08-19 14:30 | 172 | 171
2019-08-19 15:00 | 179 | 179
2019-08-19 15:30 | 190 | 189
2019-08-19 16:00 | 205 | 205
2019-08-19 16:30 | 220 | 220
2019-08-19 17:00 | 237 | 237
2019-08-19 17:30 | 250 | 249
2019-08-19 18:00 | 265 | 263
2019-08-19 18:30 | 270 | 269
2019-08-19 19:00 | 271 | 270
2019-08-19 19:30 | 265 | 264
2019-08-19 20:00 | 259 | 259
2019-08-19 20:30 | 259 | 258
2019-08-19 21:00 | 247 | 247
2019-08-19 21:30 | 235 | 235
2019-08-19 22:00 | 225 | 225
2019-08-19 22:30 | 219 | 219
2019-08-19 23:00 | 215 | 215
2019-08-19 23:30 | 204 | 204
2019-08-20 | 189 | 189
2019-08-20 00:30 | 176 | 175
2019-08-20 01:00 | 167 | 166
2019-08-20 01:30 | 161 | 160
2019-08-20 02:00 | 155 | 155
2019-08-20 02:30 | 150 | 150
2019-08-20 03:00 | 149 | 149
2019-08-20 03:30 | 148 | 148
2019-08-20 04:00 | 148 | 148
2019-08-20 04:30 | 153 | 153
2019-08-20 05:00 | 161 | 161
2019-08-20 05:30 | 177 | 177
2019-08-20 06:00 | 197 | 196
2019-08-20 06:30 | 222 | 221
2019-08-20 07:00 | 243 | 242
2019-08-20 07:30 | 248 | 248
2019-08-20 08:00 | 234 | 234
2019-08-20 08:30 | 213 | 213
2019-08-20 09:00 | 191 | 191
2019-08-20 09:30 | 174 | 174
2019-08-20 10:00 | 160 | 160
2019-08-20 10:30 | 149 | 149
2019-08-20 11:00 | 141 | 141
2019-08-20 11:30 | 135 | 134
2019-08-20 12:00 | 132 | 132
2019-08-20 12:30 | 131 | 131
2019-08-20 13:00 | 131 | 131
2019-08-20 13:30 | 135 | 135
2019-08-20 14:00 | 142 | 142
2019-08-20 14:30 | 150 | 150
2019-08-20 15:00 | 160 | 160
2019-08-20 15:30 | 173 | 173
2019-08-20 16:00 | 191 | 191
2019-08-20 16:30 | 210 | 210
2019-08-20 17:00 | 231 | 231
2019-08-20 17:30 | 249 | 249
2019-08-20 18:00 | 266 | 265
2019-08-20 18:30 | 278 | 278
2019-08-20 19:00 | 282 | 281
2019-08-20 19:30 | 276 | 276
2019-08-20 20:00 | 276 | 276
2019-08-20 20:30 | 276 | 276
2019-08-20 21:00 | 266 | 266
2019-08-20 21:30 | 254 | 254
2019-08-20 22:00 | 244 | 243
2019-08-20 22:30 | 236 | 235
2019-08-20 23:00 | 229 | 228
2019-08-20 23:30 | 215 | 215
2019-08-21 | 199 | 199
2019-08-21 00:30 | 183 | 183
2019-08-21 01:00 | 174 | 174
2019-08-21 01:30 | 166 | 166
2019-08-21 02:00 | 161 | 161
2019-08-21 02:30 | 158 | 158
2019-08-21 03:00 | 157 | 157
2019-08-21 03:30 | 158 | 158
2019-08-21 04:00 | 159 | 159
2019-08-21 04:30 | 164 | 164
2019-08-21 05:00 | 176 | 176
2019-08-21 05:30 | 195 | 194
2019-08-21 06:00 | 217 | 216
2019-08-21 06:30 | 246 | 244
2019-08-21 07:00 | 270 | 269
2019-08-21 07:30 | 274 | 274
2019-08-21 08:00 | 256 | 256
2019-08-21 08:30 | 228 | 228
2019-08-21 09:00 | 201 | 201
2019-08-21 09:30 | 181 | 181
2019-08-21 10:00 | 165 | 164
2019-08-21 10:30 | 153 | 152
2019-08-21 11:00 | 144 | 143
2019-08-21 11:30 | 137 | 137
2019-08-21 12:00 | 134 | 134
2019-08-21 12:30 | 133 | 132
2019-08-21 13:00 | 135 | 135
2019-08-21 13:30 | 139 | 138
2019-08-21 14:00 | 146 | 145
2019-08-21 14:30 | 156 | 155
2019-08-21 15:00 | 166 | 165
2019-08-21 15:30 | 178 | 177
2019-08-21 16:00 | 196 | 195
2019-08-21 16:30 | 213 | 212
2019-08-21 17:00 | 231 | 231
2019-08-21 17:30 | 243 | 243
2019-08-21 18:00 | 257 | 256
2019-08-21 18:30 | 266 | 265
2019-08-21 19:00 | 268 | 268
2019-08-21 19:30 | 262 | 262
2019-08-21 20:00 | 260 | 260
2019-08-21 20:30 | 259 | 258
2019-08-21 21:00 | 248 | 247
2019-08-21 21:30 | 239 | 238
2019-08-21 22:00 | 228 | 228
2019-08-21 22:30 | 221 | 221
2019-08-21 23:00 | 216 | 216
2019-08-21 23:30 | 203 | 203
2019-08-22 | 187 | 187
2019-08-22 00:30 | 173 | 173
2019-08-22 01:00 | 165 | 164
2019-08-22 01:30 | 158 | 158
2019-08-22 02:00 | 153 | 152
2019-08-22 02:30 | 150 | 149
2019-08-22 03:00 | 149 | 148
2019-08-22 03:30 | 151 | 150
2019-08-22 04:00 | 151 | 151
2019-08-22 04:30 | 155 | 155
2019-08-22 05:00 | 164 | 164
2019-08-22 05:30 | 180 | 180
2019-08-22 06:00 | 199 | 199
2019-08-22 06:30 | 223 | 223
2019-08-22 07:00 | 241 | 240
2019-08-22 07:30 | 242 | 241
2019-08-22 08:00 | 227 | 226
2019-08-22 08:30 | 207 | 207
2019-08-22 09:00 | 186 | 185
2019-08-22 09:30 | 170 | 169
2019-08-22 10:00 | 156 | 156
2019-08-22 10:30 | 146 | 145
2019-08-22 11:00 | 139 | 139
2019-08-22 11:30 | 133 | 133
2019-08-22 12:00 | 131 | 131
2019-08-22 12:30 | 130 | 129
2019-08-22 13:00 | 133 | 133
2019-08-22 13:30 | 138 | 138
2019-08-22 14:00 | 145 | 145
2019-08-22 14:30 | 154 | 154
2019-08-22 15:00 | 162 | 162
2019-08-22 15:30 | 177 | 176
2019-08-22 16:00 | 195 | 194
2019-08-22 16:30 | 212 | 212
2019-08-22 17:00 | 230 | 229
2019-08-22 17:30 | 242 | 242
2019-08-22 18:00 | 257 | 257
2019-08-22 18:30 | 265 | 265
2019-08-22 19:00 | 268 | 268
2019-08-22 19:30 | 262 | 262
2019-08-22 20:00 | 257 | 257
2019-08-22 20:30 | 257 | 256
2019-08-22 21:00 | 247 | 247
2019-08-22 21:30 | 235 | 235
2019-08-22 22:00 | 225 | 225
2019-08-22 22:30 | 218 | 218
2019-08-22 23:00 | 212 | 212
2019-08-22 23:30 | 199 | 199
2019-08-23 | 183 | 182
2019-08-23 00:30 | 170 | 169
2019-08-23 01:00 | 161 | 159
2019-08-23 01:30 | 154 | 152
2019-08-23 02:00 | 149 | 146
2019-08-23 02:30 | 146 | 145
2019-08-23 03:00 | 144 | 143
2019-08-23 03:30 | 146 | 145
2019-08-23 04:00 | 146 | 145
2019-08-23 04:30 | 150 | 150
2019-08-23 05:00 | 158 | 158
2019-08-23 05:30 | 173 | 173
2019-08-23 06:00 | 189 | 189
2019-08-23 06:30 | 211 | 211
2019-08-23 07:00 | 231 | 231
2019-08-23 07:30 | 239 | 239
2019-08-23 08:00 | 229 | 229
2019-08-23 08:30 | 210 | 210
2019-08-23 09:00 | 190 | 190
2019-08-23 09:30 | 175 | 175
2019-08-23 10:00 | 161 | 161
2019-08-23 10:30 | 153 | 152
2019-08-23 11:00 | 143 | 142
2019-08-23 11:30 | 136 | 135
2019-08-23 12:00 | 133 | 132
2019-08-23 12:30 | 134 | 133
2019-08-23 13:00 | 135 | 135
2019-08-23 13:30 | 138 | 137
2019-08-23 14:00 | 145 | 144
2019-08-23 14:30 | 152 | 152
2019-08-23 15:00 | 161 | 160
2019-08-23 15:30 | 171 | 171
2019-08-23 16:00 | 189 | 188
2019-08-23 16:30 | 205 | 205
2019-08-23 17:00 | 224 | 223
2019-08-23 17:30 | 238 | 237
2019-08-23 18:00 | 250 | 248
2019-08-23 18:30 | 255 | 253
2019-08-23 19:00 | 255 | 254
2019-08-23 19:30 | 252 | 251
2019-08-23 20:00 | 251 | 249
2019-08-23 20:30 | 249 | 248
2019-08-23 21:00 | 239 | 238
2019-08-23 21:30 | 230 | 230
2019-08-23 22:00 | 221 | 221
2019-08-23 22:30 | 217 | 217
2019-08-23 23:00 | 214 | 214
2019-08-23 23:30 | 203 | 203
2019-08-24 | 188 | 188
2019-08-24 00:30 | 175 | 175
2019-08-24 01:00 | 164 | 164
2019-08-24 01:30 | 158 | 157
2019-08-24 02:00 | 152 | 151
2019-08-24 02:30 | 148 | 147
2019-08-24 03:00 | 144 | 144
2019-08-24 03:30 | 144 | 144
2019-08-24 04:00 | 144 | 144
2019-08-24 04:30 | 146 | 146
2019-08-24 05:00 | 149 | 149
2019-08-24 05:30 | 156 | 156
2019-08-24 06:00 | 163 | 163
2019-08-24 06:30 | 172 | 172
2019-08-24 07:00 | 179 | 179
2019-08-24 07:30 | 181 | 181
2019-08-24 08:00 | 179 | 179
2019-08-24 08:30 | 174 | 174
2019-08-24 09:00 | 160 | 160
2019-08-24 09:30 | 147 | 147
2019-08-24 10:00 | 136 | 135
2019-08-24 10:30 | 130 | 130
2019-08-24 11:00 | 128 | 128
2019-08-24 11:30 | 127 | 127
2019-08-24 12:00 | 123 | 123
2019-08-24 12:30 | 118 | 118
2019-08-24 13:00 | 119 | 119
2019-08-24 13:30 | 117 | 117
2019-08-24 14:00 | 117 | 116
2019-08-24 14:30 | 120 | 119
2019-08-24 15:00 | 127 | 126
2019-08-24 15:30 | 139 | 139
2019-08-24 16:00 | 154 | 154
2019-08-24 16:30 | 170 | 170
2019-08-24 17:00 | 189 | 189
2019-08-24 17:30 | 201 | 201
2019-08-24 18:00 | 215 | 214
2019-08-24 18:30 | 226 | 225
2019-08-24 19:00 | 228 | 228
2019-08-24 19:30 | 223 | 223
2019-08-24 20:00 | 222 | 221
2019-08-24 20:30 | 222 | 222
2019-08-24 21:00 | 216 | 215
2019-08-24 21:30 | 208 | 208
2019-08-24 22:00 | 203 | 203
2019-08-24 22:30 | 201 | 201
2019-08-24 23:00 | 199 | 199
2019-08-24 23:30 | 190 | 190
2019-08-25 | 177 | 177
2019-08-25 00:30 | 164 | 164
2019-08-25 01:00 | 155 | 154
2019-08-25 01:30 | 148 | 147
2019-08-25 02:00 | 142 | 141
2019-08-25 02:30 | 137 | 137
2019-08-25 03:00 | 135 | 135
2019-08-25 03:30 | 135 | 135
2019-08-25 04:00 | 135 | 135
2019-08-25 04:30 | 135 | 135
2019-08-25 05:00 | 138 | 138
2019-08-25 05:30 | 143 | 143
2019-08-25 06:00 | 148 | 148
2019-08-25 06:30 | 153 | 153
2019-08-25 07:00 | 157 | 157
2019-08-25 07:30 | 157 | 157
2019-08-25 08:00 | 154 | 154
2019-08-25 08:30 | 150 | 150
2019-08-25 09:00 | 141 | 141
2019-08-25 09:30 | 132 | 132
2019-08-25 10:00 | 122 | 121
2019-08-25 10:30 | 114 | 113
2019-08-25 11:00 | 107 | 106
2019-08-25 11:30 | 101 | 100
2019-08-25 12:00 | 98 | 96
2019-08-25 12:30 | 98 | 96
2019-08-25 13:00 | 99 | 97
2019-08-25 13:30 | 103 | 102
2019-08-25 14:00 | 109 | 108
2019-08-25 14:30 | 115 | 115
2019-08-25 15:00 | 124 | 124
2019-08-25 15:30 | 140 | 139
2019-08-25 16:00 | 154 | 154
2019-08-25 16:30 | 171 | 171
2019-08-25 17:00 | 194 | 194
2019-08-25 17:30 | 210 | 210
2019-08-25 18:00 | 225 | 225
2019-08-25 18:30 | 238 | 237
2019-08-25 19:00 | 239 | 238
2019-08-25 19:30 | 232 | 232
2019-08-25 20:00 | 229 | 229
2019-08-25 20:30 | 227 | 227
2019-08-25 21:00 | 218 | 218
2019-08-25 21:30 | 209 | 209
2019-08-25 22:00 | 201 | 201
2019-08-25 22:30 | 194 | 194
2019-08-25 23:00 | 190 | 190
2019-08-25 23:30 | 180 | 179
2019-08-26 | 168 | 167
2019-08-26 00:30 | 156 | 155
2019-08-26 01:00 | 149 | 148
2019-08-26 01:30 | 142 | 141
2019-08-26 02:00 | 137 | 135
2019-08-26 02:30 | 135 | 133
2019-08-26 03:00 | 134 | 132
2019-08-26 03:30 | 134 | 132
2019-08-26 04:00 | 135 | 133
2019-08-26 04:30 | 140 | 138
2019-08-26 05:00 | 148 | 147
2019-08-26 05:30 | 164 | 164
2019-08-26 06:00 | 181 | 181
2019-08-26 06:30 | 204 | 204
2019-08-26 07:00 | 222 | 222
2019-08-26 07:30 | 228 | 228
2019-08-26 08:00 | 218 | 217
2019-08-26 08:30 | 200 | 200
2019-08-26 09:00 | 181 | 181
2019-08-26 09:30 | 167 | 167
2019-08-26 10:00 | 158 | 158
2019-08-26 10:30 | 151 | 151
2019-08-26 11:00 | 145 | 145
2019-08-26 11:30 | 141 | 140
2019-08-26 12:00 | 140 | 140
2019-08-26 12:30 | 141 | 141
2019-08-26 13:00 | 145 | 145
2019-08-26 13:30 | 155 | 154
2019-08-26 14:00 | 168 | 168
2019-08-26 14:30 | 181 | 181
2019-08-26 15:00 | 190 | 190
2019-08-26 15:30 | 201 | 201
2019-08-26 16:00 | 214 | 214
2019-08-26 16:30 | 224 | 224
2019-08-26 17:00 | 236 | 236
2019-08-26 17:30 | 250 | 250
2019-08-26 18:00 | 262 | 262
2019-08-26 18:30 | 269 | 269
2019-08-26 19:00 | 271 | 271
2019-08-26 19:30 | 265 | 264
2019-08-26 20:00 | 262 | 261
2019-08-26 20:30 | 258 | 257
2019-08-26 21:00 | 247 | 246
2019-08-26 21:30 | 236 | 236
2019-08-26 22:00 | 226 | 226
2019-08-26 22:30 | 218 | 218
2019-08-26 23:00 | 210 | 210
2019-08-26 23:30 | 200 | 199
2019-08-27 | 187 | 186
2019-08-27 00:30 | 172 | 171
2019-08-27 01:00 | 162 | 161
2019-08-27 01:30 | 155 | 154
2019-08-27 02:00 | 152 | 151
2019-08-27 02:30 | 149 | 148
2019-08-27 03:00 | 148 | 147
2019-08-27 03:30 | 148 | 147
2019-08-27 04:00 | 148 | 147
2019-08-27 04:30 | 152 | 151
2019-08-27 05:00 | 159 | 159
2019-08-27 05:30 | 175 | 175
2019-08-27 06:00 | 190 | 190
2019-08-27 06:30 | 212 | 212
2019-08-27 07:00 | 231 | 231
2019-08-27 07:30 | 249 | 249
2019-08-27 08:00 | 248 | 248
2019-08-27 08:30 | 240 | 239
2019-08-27 09:00 | 225 | 225
2019-08-27 09:30 | 214 | 213
2019-08-27 10:00 | 199 | 198
2019-08-27 10:30 | 185 | 184
2019-08-27 11:00 | 178 | 177
2019-08-27 11:30 | 176 | 175
2019-08-27 12:00 | 173 | 172
2019-08-27 12:30 | 173 | 172
2019-08-27 13:00 | 171 | 170
2019-08-27 13:30 | 174 | 173
2019-08-27 14:00 | 186 | 184
2019-08-27 14:30 | 190 | 189
2019-08-27 15:00 | 192 | 190
2019-08-27 15:30 | 201 | 199
2019-08-27 16:00 | 220 | 219
2019-08-27 16:30 | 224 | 223
2019-08-27 17:00 | 239 | 238
2019-08-27 17:30 | 253 | 252
2019-08-27 18:00 | 263 | 262
2019-08-27 18:30 | 269 | 268
2019-08-27 19:00 | 270 | 270
2019-08-27 19:30 | 265 | 264
2019-08-27 20:00 | 263 | 262
2019-08-27 20:30 | 261 | 260
2019-08-27 21:00 | 250 | 249
2019-08-27 21:30 | 237 | 237
2019-08-27 22:00 | 227 | 226
2019-08-27 22:30 | 219 | 219
2019-08-27 23:00 | 214 | 214
2019-08-27 23:30 | 203 | 203
2019-08-28 | 187 | 187
2019-08-28 00:30 | 173 | 173
2019-08-28 01:00 | 165 | 164
2019-08-28 01:30 | 158 | 158
2019-08-28 02:00 | 153 | 153
2019-08-28 02:30 | 150 | 150
2019-08-28 03:00 | 148 | 148
2019-08-28 03:30 | 146 | 146
2019-08-28 04:00 | 146 | 146
2019-08-28 04:30 | 151 | 151
2019-08-28 05:00 | 158 | 158
2019-08-28 05:30 | 171 | 171
2019-08-28 06:00 | 186 | 186
2019-08-28 06:30 | 204 | 204
2019-08-28 07:00 | 217 | 217
2019-08-28 07:30 | 222 | 222
2019-08-28 08:00 | 216 | 216
2019-08-28 08:30 | 208 | 208
2019-08-28 09:00 | 204 | 204
2019-08-28 09:30 | 211 | 211
2019-08-28 10:00 | 212 | 212
2019-08-28 10:30 | 208 | 208
2019-08-28 11:00 | 205 | 205
2019-08-28 11:30 | 223 | 222
2019-08-28 12:00 | 223 | 223
2019-08-28 12:30 | 204 | 204
2019-08-28 13:00 | 204 | 204
2019-08-28 13:30 | 215 | 215
2019-08-28 14:00 | 222 | 222
2019-08-28 14:30 | 225 | 225
2019-08-28 15:00 | 228 | 227
2019-08-28 15:30 | 229 | 229
2019-08-28 16:00 | 234 | 234
2019-08-28 16:30 | 238 | 238
2019-08-28 17:00 | 246 | 246
2019-08-28 17:30 | 255 | 255
2019-08-28 18:00 | 266 | 266
2019-08-28 18:30 | 273 | 273
2019-08-28 19:00 | 275 | 275
2019-08-28 19:30 | 270 | 270
2019-08-28 20:00 | 268 | 268
2019-08-28 20:30 | 264 | 264
2019-08-28 21:00 | 254 | 253
2019-08-28 21:30 | 243 | 242
2019-08-28 22:00 | 231 | 231
2019-08-28 22:30 | 222 | 221
2019-08-28 23:00 | 215 | 215
2019-08-28 23:30 | 202 | 202
2019-08-29 | 187 | 187
2019-08-29 00:30 | 175 | 174
2019-08-29 01:00 | 165 | 165
2019-08-29 01:30 | 159 | 159
2019-08-29 02:00 | 154 | 153
2019-08-29 02:30 | 150 | 149
2019-08-29 03:00 | 148 | 147
2019-08-29 03:30 | 147 | 146
2019-08-29 04:00 | 148 | 147
2019-08-29 04:30 | 153 | 152
2019-08-29 05:00 | 160 | 160
2019-08-29 05:30 | 175 | 175
2019-08-29 06:00 | 190 | 190
2019-08-29 06:30 | 212 | 212
2019-08-29 07:00 | 233 | 232
2019-08-29 07:30 | 249 | 249
2019-08-29 08:00 | 252 | 252
2019-08-29 08:30 | 246 | 246
2019-08-29 09:00 | 232 | 232
2019-08-29 09:30 | 234 | 234
2019-08-29 10:00 | 236 | 236
2019-08-29 10:30 | 225 | 225
2019-08-29 11:00 | 215 | 215
2019-08-29 11:30 | 216 | 215
2019-08-29 12:00 | 222 | 222
2019-08-29 12:30 | 223 | 223
2019-08-29 13:00 | 230 | 230
2019-08-29 13:30 | 233 | 233
2019-08-29 14:00 | 236 | 236
2019-08-29 14:30 | 236 | 236
2019-08-29 15:00 | 234 | 234
2019-08-29 15:30 | 235 | 235
2019-08-29 16:00 | 239 | 239
2019-08-29 16:30 | 245 | 245
2019-08-29 17:00 | 258 | 258
2019-08-29 17:30 | 266 | 266
2019-08-29 18:00 | 276 | 276
2019-08-29 18:30 | 275 | 275
2019-08-29 19:00 | 274 | 274
2019-08-29 19:30 | 269 | 269
2019-08-29 20:00 | 277 | 277
2019-08-29 20:30 | 278 | 278
2019-08-29 21:00 | 272 | 271
2019-08-29 21:30 | 255 | 255
2019-08-29 22:00 | 244 | 244
2019-08-29 22:30 | 237 | 236
2019-08-29 23:00 | 230 | 229
2019-08-29 23:30 | 215 | 214
2019-08-30 | 195 | 195
2019-08-30 00:30 | 180 | 180
2019-08-30 01:00 | 169 | 168
2019-08-30 01:30 | 165 | 165
2019-08-30 02:00 | 159 | 158
2019-08-30 02:30 | 154 | 154
2019-08-30 03:00 | 151 | 151
2019-08-30 03:30 | 152 | 152
2019-08-30 04:00 | 152 | 152
2019-08-30 04:30 | 155 | 155
2019-08-30 05:00 | 160 | 160
2019-08-30 05:30 | 172 | 172
2019-08-30 06:00 | 185 | 184
2019-08-30 06:30 | 205 | 205
2019-08-30 07:00 | 219 | 219
2019-08-30 07:30 | 223 | 223
2019-08-30 08:00 | 213 | 213
2019-08-30 08:30 | 197 | 196
2019-08-30 09:00 | 178 | 178
2019-08-30 09:30 | 166 | 166
2019-08-30 10:00 | 156 | 155
2019-08-30 10:30 | 151 | 150
2019-08-30 11:00 | 153 | 153
2019-08-30 11:30 | 155 | 155
2019-08-30 12:00 | 156 | 156
2019-08-30 12:30 | 157 | 157
2019-08-30 13:00 | 154 | 154
2019-08-30 13:30 | 162 | 162
2019-08-30 14:00 | 155 | 154
2019-08-30 14:30 | 158 | 157
2019-08-30 15:00 | 162 | 162
2019-08-30 15:30 | 170 | 170
2019-08-30 16:00 | 187 | 187
2019-08-30 16:30 | 202 | 201
2019-08-30 17:00 | 218 | 218
2019-08-30 17:30 | 231 | 231
2019-08-30 18:00 | 243 | 243
2019-08-30 18:30 | 251 | 251
2019-08-30 19:00 | 255 | 255
2019-08-30 19:30 | 250 | 250
2019-08-30 20:00 | 249 | 249
2019-08-30 20:30 | 249 | 249
2019-08-30 21:00 | 238 | 238
2019-08-30 21:30 | 229 | 229
2019-08-30 22:00 | 221 | 221
2019-08-30 22:30 | 217 | 217
2019-08-30 23:00 | 213 | 213
2019-08-30 23:30 | 202 | 202
2019-08-31 | 188 | 188
2019-08-31 00:30 | 171 | 171
2019-08-31 01:00 | 159 | 159
2019-08-31 01:30 | 153 | 152
2019-08-31 02:00 | 146 | 145
2019-08-31 02:30 | 143 | 142
2019-08-31 03:00 | 140 | 138
2019-08-31 03:30 | 139 | 138
2019-08-31 04:00 | 137 | 137
2019-08-31 04:30 | 139 | 139
2019-08-31 05:00 | 142 | 142
2019-08-31 05:30 | 148 | 148
2019-08-31 06:00 | 153 | 153
2019-08-31 06:30 | 161 | 161
2019-08-31 07:00 | 164 | 164
2019-08-31 07:30 | 165 | 165
2019-08-31 08:00 | 159 | 159
2019-08-31 08:30 | 151 | 151
2019-08-31 09:00 | 142 | 142
2019-08-31 09:30 | 133 | 133
2019-08-31 10:00 | 122 | 122
2019-08-31 10:30 | 113 | 113
2019-08-31 11:00 | 105 | 105
2019-08-31 11:30 | 102 | 102
2019-08-31 12:00 | 104 | 104
2019-08-31 12:30 | 108 | 107
2019-08-31 13:00 | 108 | 108
2019-08-31 13:30 | 107 | 107
2019-08-31 14:00 | 106 | 105
2019-08-31 14:30 | 114 | 114
2019-08-31 15:00 | 126 | 125
2019-08-31 15:30 | 136 | 136
2019-08-31 16:00 | 149 | 149
2019-08-31 16:30 | 166 | 166
2019-08-31 17:00 | 186 | 186
2019-08-31 17:30 | 199 | 199
2019-08-31 18:00 | 212 | 212
2019-08-31 18:30 | 224 | 224
2019-08-31 19:00 | 226 | 226
2019-08-31 19:30 | 222 | 222
2019-08-31 20:00 | 222 | 222
2019-08-31 20:30 | 220 | 220
2019-08-31 21:00 | 213 | 213
2019-08-31 21:30 | 206 | 206
2019-08-31 22:00 | 200 | 199
2019-08-31 22:30 | 197 | 196
2019-08-31 23:00 | 195 | 195
2019-08-31 23:30 | 186 | 185
2019-09-01 | 173 | 172
2019-09-01 00:30 | 159 | 158
2019-09-01 01:00 | 150 | 149
2019-09-01 01:30 | 143 | 141
2019-09-01 02:00 | 138 | 136
2019-09-01 02:30 | 134 | 131
2019-09-01 03:00 | 132 | 129
2019-09-01 03:30 | 131 | 128
2019-09-01 04:00 | 130 | 127
2019-09-01 04:30 | 132 | 129
2019-09-01 05:00 | 134 | 131
2019-09-01 05:30 | 138 | 135
2019-09-01 06:00 | 142 | 140
2019-09-01 06:30 | 149 | 146
2019-09-01 07:00 | 152 | 150
2019-09-01 07:30 | 151 | 149
2019-09-01 08:00 | 146 | 144
2019-09-01 08:30 | 140 | 137
2019-09-01 09:00 | 133 | 130
2019-09-01 09:30 | 125 | 123
2019-09-01 10:00 | 115 | 112
2019-09-01 10:30 | 107 | 103
2019-09-01 11:00 | 99 | 95
2019-09-01 11:30 | 93 | 89
2019-09-01 12:00 | 89 | 85
2019-09-01 12:30 | 88 | 83
2019-09-01 13:00 | 87 | 83
2019-09-01 13:30 | 90 | 86
2019-09-01 14:00 | 98 | 94
2019-09-01 14:30 | 106 | 103
2019-09-01 15:00 | 117 | 115
2019-09-01 15:30 | 128 | 126
2019-09-01 16:00 | 146 | 144
2019-09-01 16:30 | 166 | 164
2019-09-01 17:00 | 185 | 183
2019-09-01 17:30 | 197 | 197
2019-09-01 18:00 | 210 | 210
2019-09-01 18:30 | 222 | 222
2019-09-01 19:00 | 224 | 223
2019-09-01 19:30 | 220 | 219
2019-09-01 20:00 | 218 | 218
2019-09-01 20:30 | 219 | 219
2019-09-01 21:00 | 213 | 213
2019-09-01 21:30 | 203 | 203
2019-09-01 22:00 | 196 | 196
2019-09-01 22:30 | 189 | 189
2019-09-01 23:00 | 186 | 186
2019-09-01 23:30 | 177 | 177
2019-09-02 | 165 | 164
2019-09-02 00:30 | 152 | 151
2019-09-02 01:00 | 143 | 142
2019-09-02 01:30 | 137 | 137
2019-09-02 02:00 | 135 | 134
2019-09-02 02:30 | 132 | 132
2019-09-02 03:00 | 130 | 130
2019-09-02 03:30 | 130 | 130
2019-09-02 04:00 | 131 | 131
2019-09-02 04:30 | 137 | 137
2019-09-02 05:00 | 147 | 147
2019-09-02 05:30 | 162 | 162
2019-09-02 06:00 | 177 | 177
2019-09-02 06:30 | 200 | 200
2019-09-02 07:00 | 215 | 215
2019-09-02 07:30 | 219 | 218
2019-09-02 08:00 | 208 | 207
2019-09-02 08:30 | 189 | 189
2019-09-02 09:00 | 171 | 171
2019-09-02 09:30 | 158 | 158
2019-09-02 10:00 | 145 | 144
2019-09-02 10:30 | 136 | 135
2019-09-02 11:00 | 129 | 129
2019-09-02 11:30 | 128 | 127
2019-09-02 12:00 | 129 | 128
2019-09-02 12:30 | 131 | 130
2019-09-02 13:00 | 134 | 133
2019-09-02 13:30 | 138 | 137
2019-09-02 14:00 | 147 | 146
2019-09-02 14:30 | 156 | 155
2019-09-02 15:00 | 167 | 166
2019-09-02 15:30 | 181 | 179
2019-09-02 16:00 | 199 | 197
2019-09-02 16:30 | 214 | 212
2019-09-02 17:00 | 233 | 233
2019-09-02 17:30 | 245 | 245
2019-09-02 18:00 | 255 | 255
2019-09-02 18:30 | 262 | 262
2019-09-02 19:00 | 262 | 262
2019-09-02 19:30 | 255 | 255
2019-09-02 20:00 | 251 | 251
2019-09-02 20:30 | 247 | 247
2019-09-02 21:00 | 235 | 234
2019-09-02 21:30 | 224 | 222
2019-09-02 22:00 | 213 | 212
2019-09-02 22:30 | 209 | 208
2019-09-02 23:00 | 208 | 207
2019-09-02 23:30 | 196 | 195
2019-09-03 | 180 | 180
2019-09-03 00:30 | 168 | 168
2019-09-03 01:00 | 160 | 160
2019-09-03 01:30 | 154 | 154
2019-09-03 02:00 | 150 | 150
2019-09-03 02:30 | 147 | 147
2019-09-03 03:00 | 146 | 146
2019-09-03 03:30 | 148 | 147
2019-09-03 04:00 | 148 | 148
2019-09-03 04:30 | 154 | 153
2019-09-03 05:00 | 161 | 160
2019-09-03 05:30 | 178 | 176
2019-09-03 06:00 | 195 | 192
2019-09-03 06:30 | 217 | 217
2019-09-03 07:00 | 230 | 230
2019-09-03 07:30 | 230 | 230
2019-09-03 08:00 | 218 | 217
2019-09-03 08:30 | 199 | 198
2019-09-03 09:00 | 180 | 179
2019-09-03 09:30 | 163 | 163
2019-09-03 10:00 | 152 | 152
2019-09-03 10:30 | 146 | 145
2019-09-03 11:00 | 141 | 140
2019-09-03 11:30 | 138 | 137
2019-09-03 12:00 | 138 | 137
2019-09-03 12:30 | 138 | 136
2019-09-03 13:00 | 140 | 138
2019-09-03 13:30 | 144 | 144
2019-09-03 14:00 | 151 | 150
2019-09-03 14:30 | 160 | 160
2019-09-03 15:00 | 169 | 169
2019-09-03 15:30 | 181 | 181
2019-09-03 16:00 | 197 | 197
2019-09-03 16:30 | 214 | 214
2019-09-03 17:00 | 232 | 232
2019-09-03 17:30 | 244 | 244
2019-09-03 18:00 | 255 | 255
2019-09-03 18:30 | 264 | 263
2019-09-03 19:00 | 265 | 264
2019-09-03 19:30 | 259 | 258
2019-09-03 20:00 | 255 | 255
2019-09-03 20:30 | 253 | 253
2019-09-03 21:00 | 242 | 241
2019-09-03 21:30 | 232 | 232
2019-09-03 22:00 | 222 | 222
2019-09-03 22:30 | 216 | 216
2019-09-03 23:00 | 209 | 209
2019-09-03 23:30 | 197 | 197
2019-09-04 | 183 | 183
2019-09-04 00:30 | 170 | 169
2019-09-04 01:00 | 160 | 160
2019-09-04 01:30 | 155 | 154
2019-09-04 02:00 | 151 | 151
2019-09-04 02:30 | 149 | 148
2019-09-04 03:00 | 148 | 147
2019-09-04 03:30 | 149 | 148
2019-09-04 04:00 | 150 | 149
2019-09-04 04:30 | 154 | 154
2019-09-04 05:00 | 162 | 161
2019-09-04 05:30 | 176 | 176
2019-09-04 06:00 | 193 | 193
2019-09-04 06:30 | 213 | 213
2019-09-04 07:00 | 231 | 231
2019-09-04 07:30 | 231 | 231
2019-09-04 08:00 | 217 | 217
2019-09-04 08:30 | 196 | 196
2019-09-04 09:00 | 177 | 177
2019-09-04 09:30 | 163 | 163
2019-09-04 10:00 | 153 | 152
2019-09-04 10:30 | 150 | 148
2019-09-04 11:00 | 148 | 146
2019-09-04 11:30 | 146 | 145
2019-09-04 12:00 | 148 | 147
2019-09-04 12:30 | 151 | 150
2019-09-04 13:00 | 158 | 157
2019-09-04 13:30 | 167 | 165
2019-09-04 14:00 | 174 | 172
2019-09-04 14:30 | 185 | 185
2019-09-04 15:00 | 195 | 195
2019-09-04 15:30 | 206 | 206
2019-09-04 16:00 | 220 | 220
2019-09-04 16:30 | 233 | 233
2019-09-04 17:00 | 246 | 246
2019-09-04 17:30 | 254 | 253
2019-09-04 18:00 | 260 | 260
2019-09-04 18:30 | 267 | 267
2019-09-04 19:00 | 267 | 267
2019-09-04 19:30 | 259 | 259
2019-09-04 20:00 | 255 | 255
2019-09-04 20:30 | 252 | 252
2019-09-04 21:00 | 242 | 241
2019-09-04 21:30 | 231 | 230
2019-09-04 22:00 | 221 | 220
2019-09-04 22:30 | 213 | 212
2019-09-04 23:00 | 208 | 207
2019-09-04 23:30 | 193 | 193
2019-09-05 | 176 | 176
2019-09-05 00:30 | 162 | 162
2019-09-05 01:00 | 154 | 154
2019-09-05 01:30 | 148 | 148
2019-09-05 02:00 | 144 | 143
2019-09-05 02:30 | 143 | 142
2019-09-05 03:00 | 141 | 140
2019-09-05 03:30 | 141 | 141
2019-09-05 04:00 | 142 | 141
2019-09-05 04:30 | 146 | 146
2019-09-05 05:00 | 153 | 153
2019-09-05 05:30 | 168 | 168
2019-09-05 06:00 | 182 | 182
2019-09-05 06:30 | 202 | 202
2019-09-05 07:00 | 216 | 216
2019-09-05 07:30 | 215 | 215
2019-09-05 08:00 | 203 | 202
2019-09-05 08:30 | 187 | 186
2019-09-05 09:00 | 172 | 171
2019-09-05 09:30 | 159 | 159
2019-09-05 10:00 | 153 | 152
2019-09-05 10:30 | 149 | 148
2019-09-05 11:00 | 144 | 143
2019-09-05 11:30 | 144 | 142
2019-09-05 12:00 | 147 | 144
2019-09-05 12:30 | 151 | 148
2019-09-05 13:00 | 157 | 154
2019-09-05 13:30 | 162 | 161
2019-09-05 14:00 | 172 | 171
2019-09-05 14:30 | 181 | 180
2019-09-05 15:00 | 192 | 189
2019-09-05 15:30 | 204 | 201
2019-09-05 16:00 | 219 | 218
2019-09-05 16:30 | 233 | 233
2019-09-05 17:00 | 246 | 246
2019-09-05 17:30 | 251 | 251
2019-09-05 18:00 | 258 | 257
2019-09-05 18:30 | 265 | 265
2019-09-05 19:00 | 266 | 265
2019-09-05 19:30 | 257 | 257
2019-09-05 20:00 | 255 | 254
2019-09-05 20:30 | 249 | 249
2019-09-05 21:00 | 240 | 240
2019-09-05 21:30 | 229 | 229
2019-09-05 22:00 | 217 | 217
2019-09-05 22:30 | 213 | 213
2019-09-05 23:00 | 209 | 209
2019-09-05 23:30 | 195 | 195
2019-09-06 | 178 | 178
2019-09-06 00:30 | 164 | 164
2019-09-06 01:00 | 155 | 155
2019-09-06 01:30 | 149 | 149
2019-09-06 02:00 | 145 | 145
2019-09-06 02:30 | 143 | 143
2019-09-06 03:00 | 141 | 141
2019-09-06 03:30 | 143 | 143
2019-09-06 04:00 | 143 | 143
2019-09-06 04:30 | 148 | 148
2019-09-06 05:00 | 154 | 154
2019-09-06 05:30 | 168 | 167
2019-09-06 06:00 | 182 | 181
2019-09-06 06:30 | 200 | 199
2019-09-06 07:00 | 212 | 210
2019-09-06 07:30 | 218 | 218
2019-09-06 08:00 | 211 | 211
2019-09-06 08:30 | 192 | 191
2019-09-06 09:00 | 176 | 176
2019-09-06 09:30 | 169 | 169
2019-09-06 10:00 | 166 | 166
2019-09-06 10:30 | 161 | 161
2019-09-06 11:00 | 158 | 158
2019-09-06 11:30 | 150 | 150
2019-09-06 12:00 | 153 | 153
2019-09-06 12:30 | 156 | 156
2019-09-06 13:00 | 161 | 161
2019-09-06 13:30 | 169 | 169
2019-09-06 14:00 | 179 | 178
2019-09-06 14:30 | 188 | 187
2019-09-06 15:00 | 199 | 198
2019-09-06 15:30 | 211 | 211
2019-09-06 16:00 | 228 | 228
2019-09-06 16:30 | 242 | 242
2019-09-06 17:00 | 253 | 252
2019-09-06 17:30 | 254 | 254
2019-09-06 18:00 | 255 | 254
2019-09-06 18:30 | 257 | 257
2019-09-06 19:00 | 255 | 255
2019-09-06 19:30 | 246 | 246
2019-09-06 20:00 | 243 | 243
2019-09-06 20:30 | 240 | 240
2019-09-06 21:00 | 228 | 228
2019-09-06 21:30 | 220 | 220
2019-09-06 22:00 | 211 | 211
2019-09-06 22:30 | 207 | 207
2019-09-06 23:00 | 200 | 200
2019-09-06 23:30 | 188 | 188
2019-09-07 | 174 | 174
2019-09-07 00:30 | 161 | 161
2019-09-07 01:00 | 154 | 154
2019-09-07 01:30 | 148 | 148
2019-09-07 02:00 | 144 | 143
2019-09-07 02:30 | 141 | 140
2019-09-07 03:00 | 138 | 137
2019-09-07 03:30 | 136 | 136
2019-09-07 04:00 | 136 | 136
2019-09-07 04:30 | 136 | 136
2019-09-07 05:00 | 137 | 137
2019-09-07 05:30 | 141 | 141
2019-09-07 06:00 | 144 | 144
2019-09-07 06:30 | 149 | 149
2019-09-07 07:00 | 149 | 149
2019-09-07 07:30 | 150 | 149
2019-09-07 08:00 | 146 | 146
2019-09-07 08:30 | 144 | 143
2019-09-07 09:00 | 135 | 135
2019-09-07 09:30 | 128 | 128
2019-09-07 10:00 | 117 | 117
2019-09-07 10:30 | 112 | 111
2019-09-07 11:00 | 104 | 104
2019-09-07 11:30 | 100 | 99
2019-09-07 12:00 | 95 | 95
2019-09-07 12:30 | 96 | 96
2019-09-07 13:00 | 97 | 97
2019-09-07 13:30 | 102 | 102
2019-09-07 14:00 | 109 | 109
2019-09-07 14:30 | 118 | 118
2019-09-07 15:00 | 128 | 128
2019-09-07 15:30 | 142 | 142
2019-09-07 16:00 | 157 | 157
2019-09-07 16:30 | 173 | 172
2019-09-07 17:00 | 188 | 187
2019-09-07 17:30 | 197 | 196
2019-09-07 18:00 | 205 | 204
2019-09-07 18:30 | 215 | 215
2019-09-07 19:00 | 216 | 216
2019-09-07 19:30 | 210 | 210
2019-09-07 20:00 | 207 | 207
2019-09-07 20:30 | 205 | 205
2019-09-07 21:00 | 197 | 197
2019-09-07 21:30 | 191 | 191
2019-09-07 22:00 | 186 | 186
2019-09-07 22:30 | 185 | 185
2019-09-07 23:00 | 185 | 185
2019-09-07 23:30 | 175 | 175
2019-09-08 | 162 | 162
2019-09-08 00:30 | 150 | 150
2019-09-08 01:00 | 143 | 143
2019-09-08 01:30 | 137 | 137
2019-09-08 02:00 | 131 | 131
2019-09-08 02:30 | 128 | 127
2019-09-08 03:00 | 126 | 126
2019-09-08 03:30 | 126 | 126
2019-09-08 04:00 | 125 | 125
2019-09-08 04:30 | 125 | 125
2019-09-08 05:00 | 126 | 126
2019-09-08 05:30 | 130 | 130
2019-09-08 06:00 | 133 | 133
2019-09-08 06:30 | 136 | 135
2019-09-08 07:00 | 134 | 133
2019-09-08 07:30 | 132 | 132
2019-09-08 08:00 | 128 | 128
2019-09-08 08:30 | 123 | 123
2019-09-08 09:00 | 117 | 117
2019-09-08 09:30 | 109 | 109
2019-09-08 10:00 | 102 | 101
2019-09-08 10:30 | 95 | 94
2019-09-08 11:00 | 88 | 88
2019-09-08 11:30 | 86 | 85
2019-09-08 12:00 | 84 | 83
2019-09-08 12:30 | 84 | 83
2019-09-08 13:00 | 85 | 84
2019-09-08 13:30 | 90 | 89
2019-09-08 14:00 | 96 | 96
2019-09-08 14:30 | 107 | 106
2019-09-08 15:00 | 119 | 118
2019-09-08 15:30 | 134 | 133
2019-09-08 16:00 | 152 | 151
2019-09-08 16:30 | 171 | 170
2019-09-08 17:00 | 189 | 188
2019-09-08 17:30 | 199 | 199
2019-09-08 18:00 | 214 | 213
2019-09-08 18:30 | 227 | 226
2019-09-08 19:00 | 228 | 227
2019-09-08 19:30 | 220 | 220
2019-09-08 20:00 | 216 | 216
2019-09-08 20:30 | 216 | 215
2019-09-08 21:00 | 207 | 207
2019-09-08 21:30 | 199 | 199
2019-09-08 22:00 | 192 | 192
2019-09-08 22:30 | 189 | 189
2019-09-08 23:00 | 185 | 185
2019-09-08 23:30 | 175 | 174
2019-09-09 | 162 | 162
2019-09-09 00:30 | 151 | 150
2019-09-09 01:00 | 143 | 142
2019-09-09 01:30 | 137 | 136
2019-09-09 02:00 | 132 | 132
2019-09-09 02:30 | 130 | 130
2019-09-09 03:00 | 129 | 128
2019-09-09 03:30 | 129 | 128
2019-09-09 04:00 | 131 | 131
2019-09-09 04:30 | 135 | 135
2019-09-09 05:00 | 142 | 142
2019-09-09 05:30 | 156 | 156
2019-09-09 06:00 | 171 | 171
2019-09-09 06:30 | 189 | 189
2019-09-09 07:00 | 202 | 202
2019-09-09 07:30 | 205 | 205
2019-09-09 08:00 | 195 | 194
2019-09-09 08:30 | 182 | 181
2019-09-09 09:00 | 166 | 165
2019-09-09 09:30 | 154 | 153
2019-09-09 10:00 | 140 | 140
2019-09-09 10:30 | 132 | 132
2019-09-09 11:00 | 126 | 126
2019-09-09 11:30 | 122 | 122
2019-09-09 12:00 | 121 | 121
2019-09-09 12:30 | 122 | 122
2019-09-09 13:00 | 123 | 123
2019-09-09 13:30 | 128 | 128
2019-09-09 14:00 | 135 | 135
2019-09-09 14:30 | 145 | 144
2019-09-09 15:00 | 155 | 155
2019-09-09 15:30 | 169 | 169
2019-09-09 16:00 | 188 | 188
2019-09-09 16:30 | 207 | 207
2019-09-09 17:00 | 226 | 226
2019-09-09 17:30 | 241 | 240
2019-09-09 18:00 | 253 | 252
2019-09-09 18:30 | 264 | 264
2019-09-09 19:00 | 264 | 264
2019-09-09 19:30 | 258 | 258
2019-09-09 20:00 | 255 | 255
2019-09-09 20:30 | 253 | 253
2019-09-09 21:00 | 243 | 243
2019-09-09 21:30 | 232 | 232
2019-09-09 22:00 | 218 | 218
2019-09-09 22:30 | 210 | 210
2019-09-09 23:00 | 205 | 205
2019-09-09 23:30 | 195 | 195
2019-09-10 | 181 | 181
2019-09-10 00:30 | 167 | 166
2019-09-10 01:00 | 157 | 157
2019-09-10 01:30 | 151 | 151
2019-09-10 02:00 | 147 | 147
2019-09-10 02:30 | 147 | 146
2019-09-10 03:00 | 144 | 143
2019-09-10 03:30 | 144 | 143
2019-09-10 04:00 | 146 | 145
2019-09-10 04:30 | 151 | 151
2019-09-10 05:00 | 159 | 158
2019-09-10 05:30 | 173 | 173
2019-09-10 06:00 | 187 | 187
2019-09-10 06:30 | 209 | 209
2019-09-10 07:00 | 220 | 220
2019-09-10 07:30 | 224 | 223
2019-09-10 08:00 | 213 | 212
2019-09-10 08:30 | 194 | 193
2019-09-10 09:00 | 175 | 175
2019-09-10 09:30 | 160 | 160
2019-09-10 10:00 | 147 | 147
2019-09-10 10:30 | 141 | 141
2019-09-10 11:00 | 134 | 134
2019-09-10 11:30 | 131 | 130
2019-09-10 12:00 | 132 | 131
2019-09-10 12:30 | 137 | 136
2019-09-10 13:00 | 151 | 150
2019-09-10 13:30 | 156 | 155
2019-09-10 14:00 | 159 | 159
2019-09-10 14:30 | 161 | 161
2019-09-10 15:00 | 164 | 164
2019-09-10 15:30 | 179 | 179
2019-09-10 16:00 | 196 | 196
2019-09-10 16:30 | 213 | 213
2019-09-10 17:00 | 231 | 230
2019-09-10 17:30 | 247 | 247
2019-09-10 18:00 | 261 | 261
2019-09-10 18:30 | 269 | 269
2019-09-10 19:00 | 271 | 271
2019-09-10 19:30 | 264 | 263
2019-09-10 20:00 | 259 | 259
2019-09-10 20:30 | 258 | 258
2019-09-10 21:00 | 248 | 248
2019-09-10 21:30 | 238 | 237
2019-09-10 22:00 | 226 | 226
2019-09-10 22:30 | 217 | 217
2019-09-10 23:00 | 211 | 211
2019-09-10 23:30 | 199 | 199
2019-09-11 | 184 | 183
2019-09-11 00:30 | 171 | 170
2019-09-11 01:00 | 161 | 160
2019-09-11 01:30 | 156 | 154
2019-09-11 02:00 | 152 | 150
2019-09-11 02:30 | 149 | 147
2019-09-11 03:00 | 147 | 145
2019-09-11 03:30 | 148 | 146
2019-09-11 04:00 | 149 | 146
2019-09-11 04:30 | 154 | 152
2019-09-11 05:00 | 162 | 160
2019-09-11 05:30 | 177 | 176
2019-09-11 06:00 | 191 | 191
2019-09-11 06:30 | 211 | 211
2019-09-11 07:00 | 220 | 220
2019-09-11 07:30 | 224 | 223
2019-09-11 08:00 | 211 | 211
2019-09-11 08:30 | 191 | 191
2019-09-11 09:00 | 172 | 172
2019-09-11 09:30 | 163 | 163
2019-09-11 10:00 | 169 | 169
2019-09-11 10:30 | 184 | 184
2019-09-11 11:00 | 185 | 185
2019-09-11 11:30 | 178 | 178
2019-09-11 12:00 | 177 | 177
2019-09-11 12:30 | 169 | 169
2019-09-11 13:00 | 156 | 156
2019-09-11 13:30 | 151 | 150
2019-09-11 14:00 | 160 | 159
2019-09-11 14:30 | 173 | 173
2019-09-11 15:00 | 179 | 178
2019-09-11 15:30 | 184 | 183
2019-09-11 16:00 | 195 | 194
2019-09-11 16:30 | 209 | 209
2019-09-11 17:00 | 227 | 227
2019-09-11 17:30 | 242 | 241
2019-09-11 18:00 | 256 | 256
2019-09-11 18:30 | 269 | 269
2019-09-11 19:00 | 271 | 271
2019-09-11 19:30 | 265 | 265
2019-09-11 20:00 | 261 | 261
2019-09-11 20:30 | 260 | 260
2019-09-11 21:00 | 251 | 251
2019-09-11 21:30 | 240 | 240
2019-09-11 22:00 | 228 | 228
2019-09-11 22:30 | 218 | 217
2019-09-11 23:00 | 212 | 211
2019-09-11 23:30 | 201 | 200
2019-09-12 | 185 | 185
2019-09-12 00:30 | 170 | 170
2019-09-12 01:00 | 162 | 162
2019-09-12 01:30 | 155 | 154
2019-09-12 02:00 | 150 | 150
2019-09-12 02:30 | 148 | 147
2019-09-12 03:00 | 147 | 146
2019-09-12 03:30 | 147 | 147
2019-09-12 04:00 | 148 | 147
2019-09-12 04:30 | 154 | 153
2019-09-12 05:00 | 162 | 161
2019-09-12 05:30 | 177 | 177
2019-09-12 06:00 | 191 | 191
2019-09-12 06:30 | 213 | 213
2019-09-12 07:00 | 223 | 223
2019-09-12 07:30 | 224 | 224
2019-09-12 08:00 | 212 | 212
2019-09-12 08:30 | 192 | 192
2019-09-12 09:00 | 173 | 173
2019-09-12 09:30 | 157 | 157
2019-09-12 10:00 | 148 | 148
2019-09-12 10:30 | 141 | 140
2019-09-12 11:00 | 133 | 132
2019-09-12 11:30 | 127 | 126
2019-09-12 12:00 | 127 | 126
2019-09-12 12:30 | 126 | 126
2019-09-12 13:00 | 130 | 129
2019-09-12 13:30 | 134 | 133
2019-09-12 14:00 | 141 | 140
2019-09-12 14:30 | 150 | 150
2019-09-12 15:00 | 161 | 161
2019-09-12 15:30 | 174 | 174
2019-09-12 16:00 | 193 | 192
2019-09-12 16:30 | 210 | 210
2019-09-12 17:00 | 227 | 227
2019-09-12 17:30 | 237 | 237
2019-09-12 18:00 | 248 | 248
2019-09-12 18:30 | 260 | 260
2019-09-12 19:00 | 263 | 262
2019-09-12 19:30 | 259 | 258
2019-09-12 20:00 | 258 | 257
2019-09-12 20:30 | 257 | 257
2019-09-12 21:00 | 247 | 246
2019-09-12 21:30 | 236 | 235
2019-09-12 22:00 | 224 | 224
2019-09-12 22:30 | 217 | 217
2019-09-12 23:00 | 213 | 213
2019-09-12 23:30 | 201 | 201
2019-09-13 | 186 | 186
2019-09-13 00:30 | 171 | 171
2019-09-13 01:00 | 161 | 161
2019-09-13 01:30 | 155 | 155
2019-09-13 02:00 | 151 | 150
2019-09-13 02:30 | 148 | 147
2019-09-13 03:00 | 146 | 145
2019-09-13 03:30 | 148 | 147
2019-09-13 04:00 | 148 | 147
2019-09-13 04:30 | 153 | 152
2019-09-13 05:00 | 159 | 159
2019-09-13 05:30 | 174 | 174
2019-09-13 06:00 | 188 | 188
2019-09-13 06:30 | 208 | 208
2019-09-13 07:00 | 219 | 219
2019-09-13 07:30 | 221 | 220
2019-09-13 08:00 | 207 | 207
2019-09-13 08:30 | 188 | 187
2019-09-13 09:00 | 168 | 168
2019-09-13 09:30 | 155 | 155
2019-09-13 10:00 | 145 | 145
2019-09-13 10:30 | 140 | 139
2019-09-13 11:00 | 136 | 135
2019-09-13 11:30 | 133 | 132
2019-09-13 12:00 | 133 | 132
2019-09-13 12:30 | 135 | 134
2019-09-13 13:00 | 137 | 136
2019-09-13 13:30 | 142 | 141
2019-09-13 14:00 | 150 | 150
2019-09-13 14:30 | 159 | 159
2019-09-13 15:00 | 169 | 169
2019-09-13 15:30 | 180 | 180
2019-09-13 16:00 | 195 | 195
2019-09-13 16:30 | 211 | 211
2019-09-13 17:00 | 226 | 225
2019-09-13 17:30 | 235 | 234
2019-09-13 18:00 | 240 | 239
2019-09-13 18:30 | 246 | 244
2019-09-13 19:00 | 248 | 247
2019-09-13 19:30 | 244 | 243
2019-09-13 20:00 | 240 | 239
2019-09-13 20:30 | 239 | 238
2019-09-13 21:00 | 228 | 228
2019-09-13 21:30 | 220 | 220
2019-09-13 22:00 | 212 | 212
2019-09-13 22:30 | 208 | 208
2019-09-13 23:00 | 206 | 205
2019-09-13 23:30 | 195 | 194
2019-09-14 | 181 | 180
2019-09-14 00:30 | 167 | 166
2019-09-14 01:00 | 158 | 158
2019-09-14 01:30 | 153 | 152
2019-09-14 02:00 | 147 | 146
2019-09-14 02:30 | 144 | 143
2019-09-14 03:00 | 141 | 140
2019-09-14 03:30 | 141 | 140
2019-09-14 04:00 | 141 | 140
2019-09-14 04:30 | 141 | 140
2019-09-14 05:00 | 143 | 142
2019-09-14 05:30 | 148 | 147
2019-09-14 06:00 | 152 | 151
2019-09-14 06:30 | 159 | 158
2019-09-14 07:00 | 161 | 160
2019-09-14 07:30 | 167 | 166
2019-09-14 08:00 | 159 | 159
2019-09-14 08:30 | 152 | 151
2019-09-14 09:00 | 141 | 140
2019-09-14 09:30 | 128 | 127
2019-09-14 10:00 | 117 | 116
2019-09-14 10:30 | 108 | 108
2019-09-14 11:00 | 101 | 100
2019-09-14 11:30 | 96 | 96
2019-09-14 12:00 | 93 | 93
2019-09-14 12:30 | 91 | 91
2019-09-14 13:00 | 95 | 95
2019-09-14 13:30 | 102 | 102
2019-09-14 14:00 | 109 | 109
2019-09-14 14:30 | 120 | 120
2019-09-14 15:00 | 136 | 136
2019-09-14 15:30 | 153 | 153
2019-09-14 16:00 | 175 | 175
2019-09-14 16:30 | 193 | 193
2019-09-14 17:00 | 207 | 207
2019-09-14 17:30 | 217 | 217
2019-09-14 18:00 | 226 | 225
2019-09-14 18:30 | 238 | 237
2019-09-14 19:00 | 235 | 235
2019-09-14 19:30 | 229 | 229
2019-09-14 20:00 | 226 | 226
2019-09-14 20:30 | 224 | 224
2019-09-14 21:00 | 216 | 216
2019-09-14 21:30 | 209 | 209
2019-09-14 22:00 | 202 | 202
2019-09-14 22:30 | 200 | 200
2019-09-14 23:00 | 199 | 199
2019-09-14 23:30 | 188 | 187
2019-09-15 | 176 | 175
2019-09-15 00:30 | 161 | 161
2019-09-15 01:00 | 156 | 155
2019-09-15 01:30 | 148 | 147
2019-09-15 02:00 | 144 | 143
2019-09-15 02:30 | 139 | 138
2019-09-15 03:00 | 137 | 136
2019-09-15 03:30 | 136 | 135
2019-09-15 04:00 | 135 | 135
2019-09-15 04:30 | 137 | 136
2019-09-15 05:00 | 137 | 137
2019-09-15 05:30 | 142 | 141
2019-09-15 06:00 | 144 | 144
2019-09-15 06:30 | 149 | 148
2019-09-15 07:00 | 146 | 145
2019-09-15 07:30 | 145 | 144
2019-09-15 08:00 | 139 | 139
2019-09-15 08:30 | 133 | 132
2019-09-15 09:00 | 125 | 124
2019-09-15 09:30 | 118 | 118
2019-09-15 10:00 | 108 | 108
2019-09-15 10:30 | 100 | 100
2019-09-15 11:00 | 93 | 92
2019-09-15 11:30 | 89 | 88
2019-09-15 12:00 | 86 | 86
2019-09-15 12:30 | 86 | 86
2019-09-15 13:00 | 86 | 86
2019-09-15 13:30 | 92 | 92
2019-09-15 14:00 | 100 | 100
2019-09-15 14:30 | 111 | 111
2019-09-15 15:00 | 125 | 125
2019-09-15 15:30 | 142 | 142
2019-09-15 16:00 | 159 | 159
2019-09-15 16:30 | 172 | 172
2019-09-15 17:00 | 192 | 191
2019-09-15 17:30 | 205 | 205
2019-09-15 18:00 | 215 | 215
2019-09-15 18:30 | 231 | 230
2019-09-15 19:00 | 232 | 231
2019-09-15 19:30 | 225 | 225
2019-09-15 20:00 | 223 | 222
2019-09-15 20:30 | 221 | 220
2019-09-15 21:00 | 212 | 212
2019-09-15 21:30 | 203 | 203
2019-09-15 22:00 | 195 | 195
2019-09-15 22:30 | 191 | 191
2019-09-15 23:00 | 188 | 188
2019-09-15 23:30 | 178 | 178
2019-09-16 | 165 | 165
2019-09-16 00:30 | 154 | 153
2019-09-16 01:00 | 147 | 146
2019-09-16 01:30 | 141 | 140
2019-09-16 02:00 | 137 | 135
2019-09-16 02:30 | 134 | 133
2019-09-16 03:00 | 134 | 132
2019-09-16 03:30 | 136 | 134
2019-09-16 04:00 | 137 | 135
2019-09-16 04:30 | 140 | 138
2019-09-16 05:00 | 146 | 145
2019-09-16 05:30 | 162 | 161
2019-09-16 06:00 | 174 | 173
2019-09-16 06:30 | 191 | 191
2019-09-16 07:00 | 201 | 201
2019-09-16 07:30 | 204 | 204
2019-09-16 08:00 | 194 | 193
2019-09-16 08:30 | 178 | 178
2019-09-16 09:00 | 164 | 164
2019-09-16 09:30 | 152 | 152
2019-09-16 10:00 | 145 | 145
2019-09-16 10:30 | 140 | 140
2019-09-16 11:00 | 140 | 140
2019-09-16 11:30 | 138 | 138
2019-09-16 12:00 | 139 | 139
2019-09-16 12:30 | 141 | 141
2019-09-16 13:00 | 144 | 144
2019-09-16 13:30 | 151 | 150
2019-09-16 14:00 | 159 | 159
2019-09-16 14:30 | 169 | 169
2019-09-16 15:00 | 179 | 179
2019-09-16 15:30 | 191 | 191
2019-09-16 16:00 | 208 | 207
2019-09-16 16:30 | 223 | 222
2019-09-16 17:00 | 240 | 238
2019-09-16 17:30 | 250 | 249
2019-09-16 18:00 | 258 | 257
2019-09-16 18:30 | 268 | 266
2019-09-16 19:00 | 270 | 268
2019-09-16 19:30 | 261 | 260
2019-09-16 20:00 | 255 | 254
2019-09-16 20:30 | 252 | 250
2019-09-16 21:00 | 240 | 238
2019-09-16 21:30 | 227 | 227
2019-09-16 22:00 | 216 | 216
2019-09-16 22:30 | 211 | 211
2019-09-16 23:00 | 206 | 206
2019-09-16 23:30 | 194 | 194
2019-09-17 | 180 | 180
2019-09-17 00:30 | 167 | 167
2019-09-17 01:00 | 158 | 158
2019-09-17 01:30 | 151 | 151
2019-09-17 02:00 | 147 | 147
2019-09-17 02:30 | 145 | 145
2019-09-17 03:00 | 143 | 143
2019-09-17 03:30 | 145 | 145
2019-09-17 04:00 | 146 | 146
2019-09-17 04:30 | 149 | 149
2019-09-17 05:00 | 156 | 156
2019-09-17 05:30 | 169 | 169
2019-09-17 06:00 | 179 | 179
2019-09-17 06:30 | 194 | 193
2019-09-17 07:00 | 208 | 207
2019-09-17 07:30 | 209 | 208
2019-09-17 08:00 | 198 | 198
2019-09-17 08:30 | 182 | 181
2019-09-17 09:00 | 176 | 175
2019-09-17 09:30 | 171 | 169
2019-09-17 10:00 | 163 | 161
2019-09-17 10:30 | 154 | 153
2019-09-17 11:00 | 148 | 147
2019-09-17 11:30 | 149 | 148
2019-09-17 12:00 | 150 | 149
2019-09-17 12:30 | 154 | 153
2019-09-17 13:00 | 157 | 157
2019-09-17 13:30 | 163 | 163
2019-09-17 14:00 | 170 | 170
2019-09-17 14:30 | 178 | 178
2019-09-17 15:00 | 197 | 197
2019-09-17 15:30 | 222 | 222
2019-09-17 16:00 | 236 | 236
2019-09-17 16:30 | 248 | 248
2019-09-17 17:00 | 260 | 260
2019-09-17 17:30 | 264 | 264
2019-09-17 18:00 | 267 | 267
2019-09-17 18:30 | 264 | 264
2019-09-17 19:00 | 263 | 262
2019-09-17 19:30 | 255 | 254
2019-09-17 20:00 | 251 | 251
2019-09-17 20:30 | 248 | 248
2019-09-17 21:00 | 237 | 237
2019-09-17 21:30 | 227 | 226
2019-09-17 22:00 | 216 | 216
2019-09-17 22:30 | 208 | 208
2019-09-17 23:00 | 204 | 204
2019-09-17 23:30 | 192 | 192
2019-09-18 | 177 | 177
2019-09-18 00:30 | 164 | 164
2019-09-18 01:00 | 155 | 154
2019-09-18 01:30 | 151 | 150
2019-09-18 02:00 | 148 | 147
2019-09-18 02:30 | 145 | 144
2019-09-18 03:00 | 143 | 142
2019-09-18 03:30 | 145 | 144
2019-09-18 04:00 | 146 | 145
2019-09-18 04:30 | 150 | 149
2019-09-18 05:00 | 156 | 156
2019-09-18 05:30 | 170 | 170
2019-09-18 06:00 | 181 | 181
2019-09-18 06:30 | 198 | 198
2019-09-18 07:00 | 205 | 205
2019-09-18 07:30 | 204 | 203
2019-09-18 08:00 | 193 | 192
2019-09-18 08:30 | 177 | 176
2019-09-18 09:00 | 159 | 159
2019-09-18 09:30 | 148 | 147
2019-09-18 10:00 | 137 | 136
2019-09-18 10:30 | 132 | 131
2019-09-18 11:00 | 128 | 127
2019-09-18 11:30 | 124 | 123
2019-09-18 12:00 | 125 | 124
2019-09-18 12:30 | 127 | 126
2019-09-18 13:00 | 131 | 131
2019-09-18 13:30 | 136 | 136
2019-09-18 14:00 | 145 | 144
2019-09-18 14:30 | 155 | 154
2019-09-18 15:00 | 164 | 164
2019-09-18 15:30 | 178 | 177
2019-09-18 16:00 | 197 | 197
2019-09-18 16:30 | 214 | 214
2019-09-18 17:00 | 232 | 232
2019-09-18 17:30 | 244 | 244
2019-09-18 18:00 | 252 | 251
2019-09-18 18:30 | 261 | 261
2019-09-18 19:00 | 264 | 264
2019-09-18 19:30 | 257 | 257
2019-09-18 20:00 | 253 | 253
2019-09-18 20:30 | 250 | 250
2019-09-18 21:00 | 240 | 240
2019-09-18 21:30 | 229 | 229
2019-09-18 22:00 | 216 | 216
2019-09-18 22:30 | 209 | 209
2019-09-18 23:00 | 204 | 204
2019-09-18 23:30 | 191 | 191
2019-09-19 | 177 | 177
2019-09-19 00:30 | 164 | 163
2019-09-19 01:00 | 155 | 154
2019-09-19 01:30 | 150 | 149
2019-09-19 02:00 | 144 | 143
2019-09-19 02:30 | 141 | 140
2019-09-19 03:00 | 141 | 140
2019-09-19 03:30 | 141 | 140
2019-09-19 04:00 | 143 | 142
2019-09-19 04:30 | 147 | 146
2019-09-19 05:00 | 154 | 153
2019-09-19 05:30 | 167 | 167
2019-09-19 06:00 | 178 | 178
2019-09-19 06:30 | 193 | 193
2019-09-19 07:00 | 201 | 201
2019-09-19 07:30 | 202 | 201
2019-09-19 08:00 | 191 | 190
2019-09-19 08:30 | 175 | 175
2019-09-19 09:00 | 162 | 161
2019-09-19 09:30 | 151 | 150
2019-09-19 10:00 | 141 | 141
2019-09-19 10:30 | 137 | 137
2019-09-19 11:00 | 134 | 134
2019-09-19 11:30 | 132 | 131
2019-09-19 12:00 | 132 | 131
2019-09-19 12:30 | 133 | 133
2019-09-19 13:00 | 139 | 139
2019-09-19 13:30 | 142 | 141
2019-09-19 14:00 | 148 | 147
2019-09-19 14:30 | 156 | 155
2019-09-19 15:00 | 165 | 165
2019-09-19 15:30 | 179 | 178
2019-09-19 16:00 | 195 | 195
2019-09-19 16:30 | 212 | 211
2019-09-19 17:00 | 228 | 227
2019-09-19 17:30 | 238 | 237
2019-09-19 18:00 | 246 | 245
2019-09-19 18:30 | 256 | 255
2019-09-19 19:00 | 258 | 256
2019-09-19 19:30 | 251 | 250
2019-09-19 20:00 | 247 | 245
2019-09-19 20:30 | 245 | 243
2019-09-19 21:00 | 235 | 234
2019-09-19 21:30 | 224 | 223
2019-09-19 22:00 | 214 | 213
2019-09-19 22:30 | 209 | 208
2019-09-19 23:00 | 204 | 204
2019-09-19 23:30 | 192 | 192
2019-09-20 | 176 | 176
2019-09-20 00:30 | 163 | 162
2019-09-20 01:00 | 155 | 155
2019-09-20 01:30 | 150 | 149
2019-09-20 02:00 | 145 | 144
2019-09-20 02:30 | 142 | 141
2019-09-20 03:00 | 140 | 140
2019-09-20 03:30 | 141 | 141
2019-09-20 04:00 | 142 | 142
2019-09-20 04:30 | 146 | 146
2019-09-20 05:00 | 153 | 153
2019-09-20 05:30 | 166 | 166
2019-09-20 06:00 | 177 | 177
2019-09-20 06:30 | 192 | 191
2019-09-20 07:00 | 198 | 198
2019-09-20 07:30 | 198 | 198
2019-09-20 08:00 | 189 | 188
2019-09-20 08:30 | 176 | 176
2019-09-20 09:00 | 167 | 166
2019-09-20 09:30 | 165 | 164
2019-09-20 10:00 | 170 | 169
2019-09-20 10:30 | 167 | 166
2019-09-20 11:00 | 164 | 162
2019-09-20 11:30 | 166 | 164
2019-09-20 12:00 | 164 | 162
2019-09-20 12:30 | 160 | 158
2019-09-20 13:00 | 163 | 161
2019-09-20 13:30 | 167 | 166
2019-09-20 14:00 | 168 | 166
2019-09-20 14:30 | 170 | 168
2019-09-20 15:00 | 177 | 176
2019-09-20 15:30 | 188 | 187
2019-09-20 16:00 | 200 | 200
2019-09-20 16:30 | 212 | 212
2019-09-20 17:00 | 225 | 225
2019-09-20 17:30 | 233 | 232
2019-09-20 18:00 | 237 | 237
2019-09-20 18:30 | 243 | 243
2019-09-20 19:00 | 246 | 245
2019-09-20 19:30 | 238 | 237
2019-09-20 20:00 | 234 | 234
2019-09-20 20:30 | 230 | 230
2019-09-20 21:00 | 221 | 221
2019-09-20 21:30 | 213 | 213
2019-09-20 22:00 | 205 | 205
2019-09-20 22:30 | 202 | 202
2019-09-20 23:00 | 199 | 199
2019-09-20 23:30 | 188 | 188
2019-09-21 | 174 | 174
2019-09-21 00:30 | 160 | 160
2019-09-21 01:00 | 152 | 152
2019-09-21 01:30 | 146 | 146
2019-09-21 02:00 | 142 | 142
2019-09-21 02:30 | 138 | 138
2019-09-21 03:00 | 136 | 136
2019-09-21 03:30 | 134 | 134
2019-09-21 04:00 | 135 | 135
2019-09-21 04:30 | 137 | 137
2019-09-21 05:00 | 138 | 138
2019-09-21 05:30 | 142 | 142
2019-09-21 06:00 | 143 | 143
2019-09-21 06:30 | 148 | 148
2019-09-21 07:00 | 151 | 151
2019-09-21 07:30 | 155 | 155
2019-09-21 08:00 | 152 | 152
2019-09-21 08:30 | 153 | 153
2019-09-21 09:00 | 153 | 153
2019-09-21 09:30 | 150 | 149
2019-09-21 10:00 | 146 | 145
2019-09-21 10:30 | 138 | 137
2019-09-21 11:00 | 129 | 128
2019-09-21 11:30 | 120 | 119
2019-09-21 12:00 | 118 | 117
2019-09-21 12:30 | 113 | 112
2019-09-21 13:00 | 107 | 107
2019-09-21 13:30 | 109 | 108
2019-09-21 14:00 | 115 | 114
2019-09-21 14:30 | 122 | 122
2019-09-21 15:00 | 131 | 131
2019-09-21 15:30 | 143 | 142
2019-09-21 16:00 | 160 | 159
2019-09-21 16:30 | 176 | 175
2019-09-21 17:00 | 190 | 190
2019-09-21 17:30 | 199 | 199
2019-09-21 18:00 | 207 | 207
2019-09-21 18:30 | 221 | 221
2019-09-21 19:00 | 223 | 223
2019-09-21 19:30 | 218 | 218
2019-09-21 20:00 | 213 | 213
2019-09-21 20:30 | 211 | 210
2019-09-21 21:00 | 201 | 201
2019-09-21 21:30 | 195 | 195
2019-09-21 22:00 | 189 | 189
2019-09-21 22:30 | 187 | 187
2019-09-21 23:00 | 187 | 187
2019-09-21 23:30 | 177 | 177
2019-09-22 | 166 | 165
2019-09-22 00:30 | 154 | 153
2019-09-22 01:00 | 147 | 146
2019-09-22 01:30 | 140 | 139
2019-09-22 02:00 | 135 | 134
2019-09-22 02:30 | 132 | 131
2019-09-22 03:00 | 129 | 129
2019-09-22 03:30 | 129 | 129
2019-09-22 04:00 | 129 | 129
2019-09-22 04:30 | 129 | 129
2019-09-22 05:00 | 130 | 130
2019-09-22 05:30 | 133 | 133
2019-09-22 06:00 | 133 | 133
2019-09-22 06:30 | 137 | 136
2019-09-22 07:00 | 141 | 141
2019-09-22 07:30 | 143 | 143
2019-09-22 08:00 | 146 | 146
2019-09-22 08:30 | 146 | 146
2019-09-22 09:00 | 140 | 140
2019-09-22 09:30 | 140 | 140
2019-09-22 10:00 | 134 | 134
2019-09-22 10:30 | 124 | 124
2019-09-22 11:00 | 120 | 120
2019-09-22 11:30 | 113 | 113
2019-09-22 12:00 | 106 | 105
2019-09-22 12:30 | 100 | 100
2019-09-22 13:00 | 101 | 101
2019-09-22 13:30 | 103 | 103
2019-09-22 14:00 | 110 | 109
2019-09-22 14:30 | 119 | 118
2019-09-22 15:00 | 130 | 129
2019-09-22 15:30 | 142 | 142
2019-09-22 16:00 | 159 | 158
2019-09-22 16:30 | 176 | 175
2019-09-22 17:00 | 194 | 193
2019-09-22 17:30 | 204 | 204
2019-09-22 18:00 | 214 | 214
2019-09-22 18:30 | 228 | 227
2019-09-22 19:00 | 229 | 228
2019-09-22 19:30 | 221 | 221
2019-09-22 20:00 | 217 | 217
2019-09-22 20:30 | 214 | 214
2019-09-22 21:00 | 203 | 203
2019-09-22 21:30 | 196 | 196
2019-09-22 22:00 | 189 | 189
2019-09-22 22:30 | 187 | 187
2019-09-22 23:00 | 185 | 185
2019-09-22 23:30 | 174 | 174
2019-09-23 | 161 | 161
2019-09-23 00:30 | 150 | 149
2019-09-23 01:00 | 142 | 141
2019-09-23 01:30 | 137 | 136
2019-09-23 02:00 | 135 | 134
2019-09-23 02:30 | 134 | 132
2019-09-23 03:00 | 133 | 131
2019-09-23 03:30 | 132 | 131
2019-09-23 04:00 | 132 | 131
2019-09-23 04:30 | 136 | 134
2019-09-23 05:00 | 142 | 142
2019-09-23 05:30 | 154 | 153
2019-09-23 06:00 | 162 | 162
2019-09-23 06:30 | 172 | 172
2019-09-23 07:00 | 180 | 180
2019-09-23 07:30 | 182 | 182
2019-09-23 08:00 | 176 | 176
2019-09-23 08:30 | 171 | 170
2019-09-23 09:00 | 163 | 163
2019-09-23 09:30 | 157 | 156
2019-09-23 10:00 | 151 | 150
2019-09-23 10:30 | 148 | 148
2019-09-23 11:00 | 145 | 144
2019-09-23 11:30 | 143 | 142
2019-09-23 12:00 | 145 | 145
2019-09-23 12:30 | 150 | 149
2019-09-23 13:00 | 155 | 154
2019-09-23 13:30 | 165 | 164
2019-09-23 14:00 | 178 | 177
2019-09-23 14:30 | 197 | 196
2019-09-23 15:00 | 213 | 212
2019-09-23 15:30 | 217 | 217
2019-09-23 16:00 | 225 | 225
2019-09-23 16:30 | 236 | 236
2019-09-23 17:00 | 247 | 247
2019-09-23 17:30 | 251 | 251
2019-09-23 18:00 | 254 | 254
2019-09-23 18:30 | 261 | 261
2019-09-23 19:00 | 262 | 262
2019-09-23 19:30 | 252 | 252
2019-09-23 20:00 | 246 | 246
2019-09-23 20:30 | 241 | 240
2019-09-23 21:00 | 228 | 227
2019-09-23 21:30 | 218 | 218
2019-09-23 22:00 | 208 | 207
2019-09-23 22:30 | 202 | 202
2019-09-23 23:00 | 198 | 198
2019-09-23 23:30 | 186 | 186
2019-09-24 | 172 | 172
2019-09-24 00:30 | 158 | 158
2019-09-24 01:00 | 150 | 150
2019-09-24 01:30 | 145 | 144
2019-09-24 02:00 | 141 | 140
2019-09-24 02:30 | 138 | 137
2019-09-24 03:00 | 138 | 137
2019-09-24 03:30 | 138 | 137
2019-09-24 04:00 | 139 | 138
2019-09-24 04:30 | 142 | 141
2019-09-24 05:00 | 147 | 146
2019-09-24 05:30 | 158 | 158
2019-09-24 06:00 | 166 | 165
2019-09-24 06:30 | 178 | 178
2019-09-24 07:00 | 183 | 183
2019-09-24 07:30 | 184 | 184
2019-09-24 08:00 | 176 | 176
2019-09-24 08:30 | 173 | 173
2019-09-24 09:00 | 167 | 166
2019-09-24 09:30 | 162 | 162
2019-09-24 10:00 | 154 | 154
2019-09-24 10:30 | 149 | 149
2019-09-24 11:00 | 148 | 148
2019-09-24 11:30 | 151 | 150
2019-09-24 12:00 | 149 | 149
2019-09-24 12:30 | 149 | 148
2019-09-24 13:00 | 152 | 151
2019-09-24 13:30 | 160 | 160
2019-09-24 14:00 | 162 | 162
2019-09-24 14:30 | 169 | 168
2019-09-24 15:00 | 185 | 184
2019-09-24 15:30 | 194 | 193
2019-09-24 16:00 | 209 | 208
2019-09-24 16:30 | 216 | 216
2019-09-24 17:00 | 228 | 227
2019-09-24 17:30 | 236 | 235
2019-09-24 18:00 | 244 | 243
2019-09-24 18:30 | 251 | 249
2019-09-24 19:00 | 249 | 248
2019-09-24 19:30 | 241 | 241
2019-09-24 20:00 | 237 | 236
2019-09-24 20:30 | 233 | 233
2019-09-24 21:00 | 222 | 221
2019-09-24 21:30 | 212 | 212
2019-09-24 22:00 | 204 | 202
2019-09-24 22:30 | 199 | 198
2019-09-24 23:00 | 196 | 195
2019-09-24 23:30 | 184 | 183
2019-09-25 | 169 | 169
2019-09-25 00:30 | 155 | 155
2019-09-25 01:00 | 147 | 147
2019-09-25 01:30 | 142 | 142
2019-09-25 02:00 | 138 | 138
2019-09-25 02:30 | 136 | 136
2019-09-25 03:00 | 135 | 135
2019-09-25 03:30 | 135 | 135
2019-09-25 04:00 | 136 | 136
2019-09-25 04:30 | 139 | 139
2019-09-25 05:00 | 145 | 145
2019-09-25 05:30 | 157 | 157
2019-09-25 06:00 | 164 | 164
2019-09-25 06:30 | 181 | 181
2019-09-25 07:00 | 186 | 186
2019-09-25 07:30 | 193 | 193
2019-09-25 08:00 | 196 | 196
2019-09-25 08:30 | 199 | 199
2019-09-25 09:00 | 203 | 203
2019-09-25 09:30 | 201 | 201
2019-09-25 10:00 | 197 | 197
2019-09-25 10:30 | 188 | 188
2019-09-25 11:00 | 181 | 181
2019-09-25 11:30 | 171 | 170
2019-09-25 12:00 | 179 | 178
2019-09-25 12:30 | 182 | 182
2019-09-25 13:00 | 174 | 174
2019-09-25 13:30 | 179 | 179
2019-09-25 14:00 | 180 | 180
2019-09-25 14:30 | 182 | 182
2019-09-25 15:00 | 189 | 189
2019-09-25 15:30 | 200 | 200
2019-09-25 16:00 | 208 | 208
2019-09-25 16:30 | 222 | 222
2019-09-25 17:00 | 237 | 237
2019-09-25 17:30 | 245 | 245
2019-09-25 18:00 | 251 | 251
2019-09-25 18:30 | 256 | 256
2019-09-25 19:00 | 254 | 253
2019-09-25 19:30 | 245 | 244
2019-09-25 20:00 | 239 | 239
2019-09-25 20:30 | 238 | 237
2019-09-25 21:00 | 227 | 226
2019-09-25 21:30 | 218 | 218
2019-09-25 22:00 | 209 | 209
2019-09-25 22:30 | 204 | 204
2019-09-25 23:00 | 202 | 202
2019-09-25 23:30 | 189 | 189
2019-09-26 | 174 | 174
2019-09-26 00:30 | 161 | 160
2019-09-26 01:00 | 152 | 152
2019-09-26 01:30 | 148 | 148
2019-09-26 02:00 | 144 | 144
2019-09-26 02:30 | 141 | 141
2019-09-26 03:00 | 139 | 139
2019-09-26 03:30 | 139 | 139
2019-09-26 04:00 | 141 | 141
2019-09-26 04:30 | 143 | 143
2019-09-26 05:00 | 150 | 150
2019-09-26 05:30 | 160 | 160
2019-09-26 06:00 | 168 | 168
2019-09-26 06:30 | 185 | 185
2019-09-26 07:00 | 196 | 196
2019-09-26 07:30 | 203 | 203
2019-09-26 08:00 | 207 | 207
2019-09-26 08:30 | 214 | 213
2019-09-26 09:00 | 207 | 207
2019-09-26 09:30 | 211 | 211
2019-09-26 10:00 | 204 | 204
2019-09-26 10:30 | 190 | 190
2019-09-26 11:00 | 177 | 177
2019-09-26 11:30 | 173 | 173
2019-09-26 12:00 | 173 | 173
2019-09-26 12:30 | 169 | 169
2019-09-26 13:00 | 170 | 170
2019-09-26 13:30 | 195 | 194
2019-09-26 14:00 | 199 | 199
2019-09-26 14:30 | 182 | 182
2019-09-26 15:00 | 176 | 176
2019-09-26 15:30 | 184 | 184
2019-09-26 16:00 | 197 | 196
2019-09-26 16:30 | 212 | 211
2019-09-26 17:00 | 227 | 226
2019-09-26 17:30 | 235 | 235
2019-09-26 18:00 | 244 | 244
2019-09-26 18:30 | 254 | 254
2019-09-26 19:00 | 256 | 256
2019-09-26 19:30 | 249 | 249
2019-09-26 20:00 | 247 | 246
2019-09-26 20:30 | 243 | 243
2019-09-26 21:00 | 233 | 233
2019-09-26 21:30 | 220 | 219
2019-09-26 22:00 | 211 | 210
2019-09-26 22:30 | 205 | 205
2019-09-26 23:00 | 201 | 201
2019-09-26 23:30 | 189 | 189
2019-09-27 | 174 | 174
2019-09-27 00:30 | 159 | 159
2019-09-27 01:00 | 151 | 151
2019-09-27 01:30 | 146 | 145
2019-09-27 02:00 | 142 | 141
2019-09-27 02:30 | 140 | 139
2019-09-27 03:00 | 138 | 137
2019-09-27 03:30 | 139 | 138
2019-09-27 04:00 | 139 | 139
2019-09-27 04:30 | 142 | 142
2019-09-27 05:00 | 148 | 148
2019-09-27 05:30 | 158 | 158
2019-09-27 06:00 | 165 | 165
2019-09-27 06:30 | 176 | 176
2019-09-27 07:00 | 182 | 182
2019-09-27 07:30 | 188 | 186
2019-09-27 08:00 | 181 | 179
2019-09-27 08:30 | 176 | 174
2019-09-27 09:00 | 170 | 167
2019-09-27 09:30 | 163 | 159
2019-09-27 10:00 | 156 | 152
2019-09-27 10:30 | 150 | 147
2019-09-27 11:00 | 147 | 145
2019-09-27 11:30 | 153 | 152
2019-09-27 12:00 | 159 | 158
2019-09-27 12:30 | 152 | 151
2019-09-27 13:00 | 153 | 152
2019-09-27 13:30 | 152 | 152
2019-09-27 14:00 | 157 | 156
2019-09-27 14:30 | 161 | 161
2019-09-27 15:00 | 174 | 173
2019-09-27 15:30 | 186 | 185
2019-09-27 16:00 | 201 | 201
2019-09-27 16:30 | 213 | 212
2019-09-27 17:00 | 226 | 225
2019-09-27 17:30 | 226 | 226
2019-09-27 18:00 | 232 | 232
2019-09-27 18:30 | 240 | 239
2019-09-27 19:00 | 241 | 240
2019-09-27 19:30 | 235 | 234
2019-09-27 20:00 | 231 | 230
2019-09-27 20:30 | 225 | 225
2019-09-27 21:00 | 216 | 216
2019-09-27 21:30 | 208 | 208
2019-09-27 22:00 | 202 | 202
2019-09-27 22:30 | 200 | 200
2019-09-27 23:00 | 197 | 197
2019-09-27 23:30 | 185 | 185
2019-09-28 | 170 | 170
2019-09-28 00:30 | 155 | 155
2019-09-28 01:00 | 147 | 147
2019-09-28 01:30 | 142 | 141
2019-09-28 02:00 | 137 | 136
2019-09-28 02:30 | 134 | 133
2019-09-28 03:00 | 133 | 132
2019-09-28 03:30 | 133 | 133
2019-09-28 04:00 | 133 | 132
2019-09-28 04:30 | 133 | 132
2019-09-28 05:00 | 134 | 134
2019-09-28 05:30 | 137 | 137
2019-09-28 06:00 | 139 | 139
2019-09-28 06:30 | 144 | 144
2019-09-28 07:00 | 142 | 141
2019-09-28 07:30 | 139 | 139
2019-09-28 08:00 | 133 | 133
2019-09-28 08:30 | 130 | 130
2019-09-28 09:00 | 126 | 126
2019-09-28 09:30 | 121 | 121
2019-09-28 10:00 | 115 | 115
2019-09-28 10:30 | 112 | 112
2019-09-28 11:00 | 109 | 109
2019-09-28 11:30 | 108 | 108
2019-09-28 12:00 | 112 | 112
2019-09-28 12:30 | 119 | 119
2019-09-28 13:00 | 127 | 126
2019-09-28 13:30 | 140 | 140
2019-09-28 14:00 | 152 | 151
2019-09-28 14:30 | 163 | 163
2019-09-28 15:00 | 171 | 171
2019-09-28 15:30 | 169 | 168
2019-09-28 16:00 | 179 | 179
2019-09-28 16:30 | 194 | 193
2019-09-28 17:00 | 207 | 207
2019-09-28 17:30 | 212 | 211
2019-09-28 18:00 | 214 | 214
2019-09-28 18:30 | 225 | 224
2019-09-28 19:00 | 227 | 226
2019-09-28 19:30 | 219 | 219
2019-09-28 20:00 | 215 | 215
2019-09-28 20:30 | 211 | 211
2019-09-28 21:00 | 203 | 203
2019-09-28 21:30 | 196 | 196
2019-09-28 22:00 | 190 | 189
2019-09-28 22:30 | 187 | 187
2019-09-28 23:00 | 185 | 185
2019-09-28 23:30 | 175 | 175
2019-09-29 | 162 | 161
2019-09-29 00:30 | 150 | 149
2019-09-29 01:00 | 142 | 142
2019-09-29 01:30 | 137 | 136
2019-09-29 02:00 | 133 | 132
2019-09-29 02:30 | 130 | 128
2019-09-29 03:00 | 127 | 126
2019-09-29 03:30 | 125 | 124
2019-09-29 04:00 | 124 | 124
2019-09-29 04:30 | 126 | 126
2019-09-29 05:00 | 126 | 126
2019-09-29 05:30 | 129 | 129
2019-09-29 06:00 | 129 | 129
2019-09-29 06:30 | 128 | 128
2019-09-29 07:00 | 125 | 125
2019-09-29 07:30 | 121 | 121
2019-09-29 08:00 | 115 | 115
2019-09-29 08:30 | 112 | 111
2019-09-29 09:00 | 105 | 104
2019-09-29 09:30 | 100 | 99
2019-09-29 10:00 | 95 | 94
2019-09-29 10:30 | 91 | 91
2019-09-29 11:00 | 88 | 88
2019-09-29 11:30 | 86 | 86
2019-09-29 12:00 | 86 | 86
2019-09-29 12:30 | 87 | 87
2019-09-29 13:00 | 90 | 90
2019-09-29 13:30 | 96 | 96
2019-09-29 14:00 | 103 | 103
2019-09-29 14:30 | 112 | 112
2019-09-29 15:00 | 124 | 124
2019-09-29 15:30 | 139 | 139
2019-09-29 16:00 | 156 | 155
2019-09-29 16:30 | 174 | 174
2019-09-29 17:00 | 189 | 189
2019-09-29 17:30 | 202 | 202
2019-09-29 18:00 | 211 | 211
2019-09-29 18:30 | 224 | 223
2019-09-29 19:00 | 225 | 225
2019-09-29 19:30 | 219 | 219
2019-09-29 20:00 | 215 | 215
2019-09-29 20:30 | 211 | 211
2019-09-29 21:00 | 203 | 203
2019-09-29 21:30 | 194 | 194
2019-09-29 22:00 | 188 | 188
2019-09-29 22:30 | 184 | 184
2019-09-29 23:00 | 181 | 181
2019-09-29 23:30 | 171 | 171
2019-09-30 | 158 | 158
2019-09-30 00:30 | 146 | 146
2019-09-30 01:00 | 139 | 138
2019-09-30 01:30 | 134 | 134
2019-09-30 02:00 | 132 | 131
2019-09-30 02:30 | 129 | 128
2019-09-30 03:00 | 128 | 128
2019-09-30 03:30 | 130 | 129
2019-09-30 04:00 | 131 | 130
2019-09-30 04:30 | 134 | 134
2019-09-30 05:00 | 139 | 139
2019-09-30 05:30 | 150 | 150
2019-09-30 06:00 | 158 | 158
2019-09-30 06:30 | 169 | 169
2019-09-30 07:00 | 177 | 177
2019-09-30 07:30 | 181 | 181
2019-09-30 08:00 | 177 | 177
2019-09-30 08:30 | 173 | 173
2019-09-30 09:00 | 165 | 165
2019-09-30 09:30 | 163 | 163
2019-09-30 10:00 | 163 | 163
2019-09-30 10:30 | 161 | 161
2019-09-30 11:00 | 162 | 162
2019-09-30 11:30 | 160 | 159
2019-09-30 12:00 | 157 | 156
2019-09-30 12:30 | 157 | 156
2019-09-30 13:00 | 159 | 158
2019-09-30 13:30 | 163 | 163
2019-09-30 14:00 | 168 | 168
2019-09-30 14:30 | 177 | 177
2019-09-30 15:00 | 189 | 188
2019-09-30 15:30 | 200 | 200
2019-09-30 16:00 | 213 | 213
2019-09-30 16:30 | 225 | 225
2019-09-30 17:00 | 238 | 238
2019-09-30 17:30 | 245 | 245
2019-09-30 18:00 | 251 | 251
2019-09-30 18:30 | 258 | 258
2019-09-30 19:00 | 260 | 260
2019-09-30 19:30 | 252 | 251
2019-09-30 20:00 | 247 | 246
2019-09-30 20:30 | 241 | 241
2019-09-30 21:00 | 229 | 229
2019-09-30 21:30 | 218 | 218
2019-09-30 22:00 | 207 | 207
2019-09-30 22:30 | 201 | 201
2019-09-30 23:00 | 199 | 198
2019-09-30 23:30 | 186 | 186
2019-10-01 | 171 | 171
2019-10-01 00:30 | 158 | 158
2019-10-01 01:00 | 150 | 150
2019-10-01 01:30 | 146 | 146
2019-10-01 02:00 | 142 | 142
2019-10-01 02:30 | 139 | 139
2019-10-01 03:00 | 138 | 138
2019-10-01 03:30 | 138 | 138
2019-10-01 04:00 | 138 | 138
2019-10-01 04:30 | 142 | 141
2019-10-01 05:00 | 148 | 148
2019-10-01 05:30 | 157 | 157
2019-10-01 06:00 | 164 | 164
2019-10-01 06:30 | 175 | 175
2019-10-01 07:00 | 187 | 186
2019-10-01 07:30 | 188 | 188
2019-10-01 08:00 | 184 | 183
2019-10-01 08:30 | 182 | 182
2019-10-01 09:00 | 184 | 184
2019-10-01 09:30 | 181 | 181
2019-10-01 10:00 | 181 | 181
2019-10-01 10:30 | 182 | 182
2019-10-01 11:00 | 169 | 169
2019-10-01 11:30 | 162 | 161
2019-10-01 12:00 | 164 | 164
2019-10-01 12:30 | 163 | 163
2019-10-01 13:00 | 159 | 159
2019-10-01 13:30 | 153 | 153
2019-10-01 14:00 | 156 | 156
2019-10-01 14:30 | 167 | 167
2019-10-01 15:00 | 175 | 175
2019-10-01 15:30 | 184 | 184
2019-10-01 16:00 | 196 | 196
2019-10-01 16:30 | 207 | 207
2019-10-01 17:00 | 225 | 225
2019-10-01 17:30 | 238 | 238
2019-10-01 18:00 | 246 | 246
2019-10-01 18:30 | 257 | 257
2019-10-01 19:00 | 258 | 258
2019-10-01 19:30 | 250 | 250
2019-10-01 20:00 | 243 | 242
2019-10-01 20:30 | 240 | 239
2019-10-01 21:00 | 230 | 229
2019-10-01 21:30 | 219 | 219
2019-10-01 22:00 | 211 | 210
2019-10-01 22:30 | 205 | 205
2019-10-01 23:00 | 201 | 201
2019-10-01 23:30 | 188 | 188
2019-10-02 | 175 | 175
2019-10-02 00:30 | 162 | 162
2019-10-02 01:00 | 155 | 154
2019-10-02 01:30 | 149 | 148
2019-10-02 02:00 | 145 | 144
2019-10-02 02:30 | 144 | 143
2019-10-02 03:00 | 142 | 141
2019-10-02 03:30 | 144 | 143
2019-10-02 04:00 | 143 | 142
2019-10-02 04:30 | 145 | 144
2019-10-02 05:00 | 150 | 150
2019-10-02 05:30 | 160 | 160
2019-10-02 06:00 | 169 | 168
2019-10-02 06:30 | 178 | 178
2019-10-02 07:00 | 181 | 181
2019-10-02 07:30 | 178 | 178
2019-10-02 08:00 | 173 | 173
2019-10-02 08:30 | 170 | 170
2019-10-02 09:00 | 170 | 169
2019-10-02 09:30 | 168 | 168
2019-10-02 10:00 | 162 | 162
2019-10-02 10:30 | 159 | 159
2019-10-02 11:00 | 152 | 152
2019-10-02 11:30 | 147 | 147
2019-10-02 12:00 | 143 | 143
2019-10-02 12:30 | 143 | 143
2019-10-02 13:00 | 143 | 143
2019-10-02 13:30 | 140 | 140
2019-10-02 14:00 | 145 | 145
2019-10-02 14:30 | 153 | 153
2019-10-02 15:00 | 162 | 162
2019-10-02 15:30 | 178 | 178
2019-10-02 16:00 | 195 | 195
2019-10-02 16:30 | 211 | 211
2019-10-02 17:00 | 229 | 228
2019-10-02 17:30 | 241 | 240
2019-10-02 18:00 | 249 | 249
2019-10-02 18:30 | 261 | 261
2019-10-02 19:00 | 265 | 264
2019-10-02 19:30 | 257 | 256
2019-10-02 20:00 | 250 | 249
2019-10-02 20:30 | 247 | 247
2019-10-02 21:00 | 236 | 235
2019-10-02 21:30 | 227 | 226
2019-10-02 22:00 | 217 | 217
2019-10-02 22:30 | 211 | 211
2019-10-02 23:00 | 208 | 208
2019-10-02 23:30 | 196 | 196
2019-10-03 | 179 | 179
2019-10-03 00:30 | 165 | 164
2019-10-03 01:00 | 156 | 156
2019-10-03 01:30 | 150 | 149
2019-10-03 02:00 | 145 | 144
2019-10-03 02:30 | 142 | 141
2019-10-03 03:00 | 141 | 140
2019-10-03 03:30 | 140 | 140
2019-10-03 04:00 | 142 | 141
2019-10-03 04:30 | 147 | 146
2019-10-03 05:00 | 152 | 152
2019-10-03 05:30 | 162 | 162
2019-10-03 06:00 | 171 | 171
2019-10-03 06:30 | 179 | 179
2019-10-03 07:00 | 180 | 180
2019-10-03 07:30 | 178 | 178
2019-10-03 08:00 | 169 | 169
2019-10-03 08:30 | 160 | 159
2019-10-03 09:00 | 150 | 149
2019-10-03 09:30 | 140 | 140
2019-10-03 10:00 | 133 | 132
2019-10-03 10:30 | 128 | 127
2019-10-03 11:00 | 127 | 125
2019-10-03 11:30 | 124 | 123
2019-10-03 12:00 | 126 | 125
2019-10-03 12:30 | 125 | 124
2019-10-03 13:00 | 130 | 128
2019-10-03 13:30 | 136 | 134
2019-10-03 14:00 | 142 | 142
2019-10-03 14:30 | 150 | 150
2019-10-03 15:00 | 161 | 161
2019-10-03 15:30 | 175 | 175
2019-10-03 16:00 | 191 | 191
2019-10-03 16:30 | 208 | 208
2019-10-03 17:00 | 226 | 226
2019-10-03 17:30 | 238 | 238
2019-10-03 18:00 | 245 | 245
2019-10-03 18:30 | 257 | 257
2019-10-03 19:00 | 261 | 261
2019-10-03 19:30 | 253 | 253
2019-10-03 20:00 | 248 | 248
2019-10-03 20:30 | 245 | 245
2019-10-03 21:00 | 234 | 234
2019-10-03 21:30 | 222 | 222
2019-10-03 22:00 | 213 | 213
2019-10-03 22:30 | 209 | 208
2019-10-03 23:00 | 202 | 202
2019-10-03 23:30 | 190 | 190
2019-10-04 | 176 | 176
2019-10-04 00:30 | 162 | 162
2019-10-04 01:00 | 153 | 152
2019-10-04 01:30 | 148 | 147
2019-10-04 02:00 | 144 | 143
2019-10-04 02:30 | 142 | 142
2019-10-04 03:00 | 141 | 140
2019-10-04 03:30 | 143 | 142
2019-10-04 04:00 | 143 | 142
2019-10-04 04:30 | 147 | 147
2019-10-04 05:00 | 153 | 153
2019-10-04 05:30 | 162 | 162
2019-10-04 06:00 | 168 | 168
2019-10-04 06:30 | 175 | 175
2019-10-04 07:00 | 176 | 176
2019-10-04 07:30 | 176 | 176
2019-10-04 08:00 | 168 | 167
2019-10-04 08:30 | 160 | 160
2019-10-04 09:00 | 150 | 149
2019-10-04 09:30 | 142 | 141
2019-10-04 10:00 | 137 | 136
2019-10-04 10:30 | 134 | 133
2019-10-04 11:00 | 131 | 129
2019-10-04 11:30 | 129 | 127
2019-10-04 12:00 | 128 | 128
2019-10-04 12:30 | 130 | 130
2019-10-04 13:00 | 131 | 131
2019-10-04 13:30 | 136 | 136
2019-10-04 14:00 | 144 | 143
2019-10-04 14:30 | 153 | 153
2019-10-04 15:00 | 164 | 164
2019-10-04 15:30 | 178 | 177
2019-10-04 16:00 | 194 | 194
2019-10-04 16:30 | 209 | 209
2019-10-04 17:00 | 226 | 225
2019-10-04 17:30 | 235 | 235
2019-10-04 18:00 | 238 | 238
2019-10-04 18:30 | 249 | 248
2019-10-04 19:00 | 250 | 250
2019-10-04 19:30 | 244 | 244
2019-10-04 20:00 | 241 | 241
2019-10-04 20:30 | 238 | 237
2019-10-04 21:00 | 224 | 224
2019-10-04 21:30 | 217 | 216
2019-10-04 22:00 | 210 | 210
2019-10-04 22:30 | 206 | 206
2019-10-04 23:00 | 203 | 203
2019-10-04 23:30 | 191 | 191
2019-10-05 | 176 | 176
2019-10-05 00:30 | 162 | 162
2019-10-05 01:00 | 154 | 153
2019-10-05 01:30 | 148 | 147
2019-10-05 02:00 | 143 | 142
2019-10-05 02:30 | 140 | 139
2019-10-05 03:00 | 139 | 138
2019-10-05 03:30 | 139 | 138
2019-10-05 04:00 | 139 | 138
2019-10-05 04:30 | 139 | 138
2019-10-05 05:00 | 141 | 140
2019-10-05 05:30 | 143 | 142
2019-10-05 06:00 | 143 | 142
2019-10-05 06:30 | 143 | 142
2019-10-05 07:00 | 139 | 138
2019-10-05 07:30 | 134 | 133
2019-10-05 08:00 | 129 | 128
2019-10-05 08:30 | 124 | 124
2019-10-05 09:00 | 118 | 118
2019-10-05 09:30 | 112 | 112
2019-10-05 10:00 | 105 | 105
2019-10-05 10:30 | 101 | 101
2019-10-05 11:00 | 100 | 100
2019-10-05 11:30 | 99 | 99
2019-10-05 12:00 | 99 | 99
2019-10-05 12:30 | 100 | 100
2019-10-05 13:00 | 104 | 104
2019-10-05 13:30 | 115 | 115
2019-10-05 14:00 | 124 | 124
2019-10-05 14:30 | 133 | 133
2019-10-05 15:00 | 145 | 145
2019-10-05 15:30 | 156 | 156
2019-10-05 16:00 | 166 | 166
2019-10-05 16:30 | 182 | 182
2019-10-05 17:00 | 193 | 193
2019-10-05 17:30 | 201 | 201
2019-10-05 18:00 | 208 | 208
2019-10-05 18:30 | 220 | 219
2019-10-05 19:00 | 223 | 223
2019-10-05 19:30 | 217 | 216
2019-10-05 20:00 | 214 | 213
2019-10-05 20:30 | 210 | 210
2019-10-05 21:00 | 202 | 202
2019-10-05 21:30 | 196 | 196
2019-10-05 22:00 | 191 | 191
2019-10-05 22:30 | 189 | 189
2019-10-05 23:00 | 188 | 187
2019-10-05 23:30 | 179 | 178
2019-10-06 | 168 | 166
2019-10-06 00:30 | 155 | 153
2019-10-06 01:00 | 148 | 145
2019-10-06 01:30 | 143 | 140
2019-10-06 02:00 | 139 | 136
2019-10-06 02:30 | 137 | 133
2019-10-06 03:00 | 136 | 132
2019-10-06 03:30 | 135 | 132
2019-10-06 04:00 | 132 | 130
2019-10-06 04:30 | 132 | 130
2019-10-06 05:00 | 133 | 131
2019-10-06 05:30 | 133 | 131
2019-10-06 06:00 | 133 | 130
2019-10-06 06:30 | 130 | 127
2019-10-06 07:00 | 128 | 125
2019-10-06 07:30 | 127 | 125
2019-10-06 08:00 | 120 | 118
2019-10-06 08:30 | 116 | 115
2019-10-06 09:00 | 111 | 110
2019-10-06 09:30 | 112 | 111
2019-10-06 10:00 | 112 | 112
2019-10-06 10:30 | 108 | 107
2019-10-06 11:00 | 103 | 103
2019-10-06 11:30 | 93 | 92
2019-10-06 12:00 | 87 | 87
2019-10-06 12:30 | 85 | 85
2019-10-06 13:00 | 91 | 91
2019-10-06 13:30 | 97 | 97
2019-10-06 14:00 | 105 | 105
2019-10-06 14:30 | 116 | 116
2019-10-06 15:00 | 130 | 130
2019-10-06 15:30 | 146 | 146
2019-10-06 16:00 | 163 | 163
2019-10-06 16:30 | 179 | 179
2019-10-06 17:00 | 195 | 195
2019-10-06 17:30 | 202 | 202
2019-10-06 18:00 | 209 | 209
2019-10-06 18:30 | 222 | 222
2019-10-06 19:00 | 223 | 223
2019-10-06 19:30 | 215 | 215
2019-10-06 20:00 | 213 | 213
2019-10-06 20:30 | 209 | 209
2019-10-06 21:00 | 200 | 200
2019-10-06 21:30 | 196 | 195
2019-10-06 22:00 | 191 | 190
2019-10-06 22:30 | 189 | 189
2019-10-06 23:00 | 188 | 188
2019-10-06 23:30 | 179 | 177
2019-10-07 | 167 | 165
2019-10-07 00:30 | 155 | 152
2019-10-07 01:00 | 148 | 144
2019-10-07 01:30 | 143 | 140
2019-10-07 02:00 | 141 | 137
2019-10-07 02:30 | 137 | 135
2019-10-07 03:00 | 134 | 132
2019-10-07 03:30 | 134 | 132
2019-10-07 04:00 | 133 | 132
2019-10-07 04:30 | 132 | 131
2019-10-07 05:00 | 134 | 132
2019-10-07 05:30 | 136 | 134
2019-10-07 06:00 | 136 | 134
2019-10-07 06:30 | 135 | 133
2019-10-07 07:00 | 133 | 132
2019-10-07 07:30 | 131 | 130
2019-10-07 08:00 | 126 | 125
2019-10-07 08:30 | 124 | 124
2019-10-07 09:00 | 120 | 120
2019-10-07 09:30 | 118 | 118
2019-10-07 10:00 | 117 | 117
2019-10-07 10:30 | 117 | 117
2019-10-07 11:00 | 117 | 117
2019-10-07 11:30 | 121 | 121
2019-10-07 12:00 | 128 | 128
2019-10-07 12:30 | 137 | 137
2019-10-07 13:00 | 151 | 151
2019-10-07 13:30 | 161 | 161
2019-10-07 14:00 | 169 | 169
2019-10-07 14:30 | 186 | 186
2019-10-07 15:00 | 206 | 204
2019-10-07 15:30 | 222 | 219
2019-10-07 16:00 | 234 | 232
2019-10-07 16:30 | 245 | 243
2019-10-07 17:00 | 255 | 253
2019-10-07 17:30 | 259 | 257
2019-10-07 18:00 | 260 | 258
2019-10-07 18:30 | 268 | 266
2019-10-07 19:00 | 269 | 267
2019-10-07 19:30 | 259 | 257
2019-10-07 20:00 | 252 | 250
2019-10-07 20:30 | 246 | 244
2019-10-07 21:00 | 232 | 231
2019-10-07 21:30 | 223 | 222
2019-10-07 22:00 | 212 | 212
2019-10-07 22:30 | 205 | 205
2019-10-07 23:00 | 199 | 199
2019-10-07 23:30 | 188 | 188
2019-10-08 | 175 | 175
2019-10-08 00:30 | 161 | 161
2019-10-08 01:00 | 153 | 153
2019-10-08 01:30 | 147 | 147
2019-10-08 02:00 | 144 | 144
2019-10-08 02:30 | 142 | 142
2019-10-08 03:00 | 141 | 141
2019-10-08 03:30 | 141 | 141
2019-10-08 04:00 | 143 | 143
2019-10-08 04:30 | 146 | 146
2019-10-08 05:00 | 152 | 152
2019-10-08 05:30 | 163 | 163
2019-10-08 06:00 | 175 | 175
2019-10-08 06:30 | 191 | 191
2019-10-08 07:00 | 204 | 204
2019-10-08 07:30 | 210 | 210
2019-10-08 08:00 | 205 | 205
2019-10-08 08:30 | 199 | 199
2019-10-08 09:00 | 189 | 189
2019-10-08 09:30 | 187 | 187
2019-10-08 10:00 | 185 | 185
2019-10-08 10:30 | 190 | 190
2019-10-08 11:00 | 200 | 200
2019-10-08 11:30 | 202 | 201
2019-10-08 12:00 | 204 | 203
2019-10-08 12:30 | 217 | 216
2019-10-08 13:00 | 250 | 250
2019-10-08 13:30 | 257 | 257
2019-10-08 14:00 | 271 | 271
2019-10-08 14:30 | 278 | 278
2019-10-08 15:00 | 284 | 284
2019-10-08 15:30 | 282 | 282
2019-10-08 16:00 | 281 | 280
2019-10-08 16:30 | 288 | 288
2019-10-08 17:00 | 296 | 296
2019-10-08 17:30 | 303 | 302
2019-10-08 18:00 | 305 | 305
2019-10-08 18:30 | 309 | 309
2019-10-08 19:00 | 310 | 310
2019-10-08 19:30 | 297 | 296
2019-10-08 20:00 | 289 | 289
2019-10-08 20:30 | 277 | 277
2019-10-08 21:00 | 266 | 266
2019-10-08 21:30 | 254 | 253
2019-10-08 22:00 | 241 | 240
2019-10-08 22:30 | 231 | 230
2019-10-08 23:00 | 220 | 220
2019-10-08 23:30 | 204 | 204
2019-10-09 | 188 | 188
2019-10-09 00:30 | 174 | 174
2019-10-09 01:00 | 165 | 165
2019-10-09 01:30 | 160 | 160
2019-10-09 02:00 | 156 | 156
2019-10-09 02:30 | 152 | 152
2019-10-09 03:00 | 151 | 150
2019-10-09 03:30 | 150 | 149
2019-10-09 04:00 | 151 | 150
2019-10-09 04:30 | 154 | 153
2019-10-09 05:00 | 160 | 160
2019-10-09 05:30 | 170 | 170
2019-10-09 06:00 | 178 | 178
2019-10-09 06:30 | 191 | 191
2019-10-09 07:00 | 198 | 198
2019-10-09 07:30 | 201 | 201
2019-10-09 08:00 | 201 | 200
2019-10-09 08:30 | 189 | 187
2019-10-09 09:00 | 177 | 175
2019-10-09 09:30 | 171 | 170
2019-10-09 10:00 | 173 | 171
2019-10-09 10:30 | 172 | 170
2019-10-09 11:00 | 163 | 161
2019-10-09 11:30 | 159 | 157
2019-10-09 12:00 | 154 | 153
2019-10-09 12:30 | 151 | 149
2019-10-09 13:00 | 150 | 149
2019-10-09 13:30 | 151 | 149
2019-10-09 14:00 | 156 | 155
2019-10-09 14:30 | 165 | 165
2019-10-09 15:00 | 176 | 176
2019-10-09 15:30 | 189 | 188
2019-10-09 16:00 | 203 | 203
2019-10-09 16:30 | 219 | 217
2019-10-09 17:00 | 234 | 233
2019-10-09 17:30 | 245 | 244
2019-10-09 18:00 | 252 | 250
2019-10-09 18:30 | 261 | 260
2019-10-09 19:00 | 263 | 263
2019-10-09 19:30 | 256 | 256
2019-10-09 20:00 | 252 | 251
2019-10-09 20:30 | 248 | 248
2019-10-09 21:00 | 237 | 236
2019-10-09 21:30 | 225 | 225
2019-10-09 22:00 | 215 | 215
2019-10-09 22:30 | 209 | 209
2019-10-09 23:00 | 205 | 204
2019-10-09 23:30 | 191 | 191
2019-10-10 | 177 | 177
2019-10-10 00:30 | 167 | 166
2019-10-10 01:00 | 158 | 158
2019-10-10 01:30 | 153 | 152
2019-10-10 02:00 | 150 | 149
2019-10-10 02:30 | 148 | 147
2019-10-10 03:00 | 145 | 145
2019-10-10 03:30 | 146 | 145
2019-10-10 04:00 | 147 | 147
2019-10-10 04:30 | 151 | 151
2019-10-10 05:00 | 158 | 158
2019-10-10 05:30 | 169 | 169
2019-10-10 06:00 | 176 | 176
2019-10-10 06:30 | 187 | 187
2019-10-10 07:00 | 194 | 194
2019-10-10 07:30 | 199 | 198
2019-10-10 08:00 | 189 | 188
2019-10-10 08:30 | 174 | 173
2019-10-10 09:00 | 166 | 165
2019-10-10 09:30 | 167 | 165
2019-10-10 10:00 | 172 | 170
2019-10-10 10:30 | 173 | 171
2019-10-10 11:00 | 174 | 171
2019-10-10 11:30 | 170 | 167
2019-10-10 12:00 | 176 | 175
2019-10-10 12:30 | 174 | 174
2019-10-10 13:00 | 182 | 182
2019-10-10 13:30 | 176 | 176
2019-10-10 14:00 | 170 | 170
2019-10-10 14:30 | 178 | 178
2019-10-10 15:00 | 196 | 195
2019-10-10 15:30 | 212 | 212
2019-10-10 16:00 | 212 | 212
2019-10-10 16:30 | 229 | 229
2019-10-10 17:00 | 241 | 241
2019-10-10 17:30 | 251 | 251
2019-10-10 18:00 | 257 | 257
2019-10-10 18:30 | 267 | 267
2019-10-10 19:00 | 270 | 270
2019-10-10 19:30 | 264 | 264
2019-10-10 20:00 | 260 | 260
2019-10-10 20:30 | 256 | 256
2019-10-10 21:00 | 245 | 244
2019-10-10 21:30 | 232 | 232
2019-10-10 22:00 | 222 | 222
2019-10-10 22:30 | 215 | 215
2019-10-10 23:00 | 210 | 210
2019-10-10 23:30 | 199 | 199
2019-10-11 | 183 | 183
2019-10-11 00:30 | 170 | 170
2019-10-11 01:00 | 161 | 161
2019-10-11 01:30 | 157 | 156
2019-10-11 02:00 | 153 | 152
2019-10-11 02:30 | 150 | 150
2019-10-11 03:00 | 148 | 148
2019-10-11 03:30 | 148 | 148
2019-10-11 04:00 | 148 | 148
2019-10-11 04:30 | 152 | 152
2019-10-11 05:00 | 160 | 160
2019-10-11 05:30 | 171 | 171
2019-10-11 06:00 | 180 | 180
2019-10-11 06:30 | 191 | 190
2019-10-11 07:00 | 197 | 197
2019-10-11 07:30 | 200 | 200
2019-10-11 08:00 | 195 | 194
2019-10-11 08:30 | 188 | 188
2019-10-11 09:00 | 177 | 176
2019-10-11 09:30 | 167 | 167
2019-10-11 10:00 | 169 | 168
2019-10-11 10:30 | 192 | 191
2019-10-11 11:00 | 205 | 203
2019-10-11 11:30 | 203 | 203
2019-10-11 12:00 | 194 | 194
2019-10-11 12:30 | 199 | 199
2019-10-11 13:00 | 201 | 201
2019-10-11 13:30 | 190 | 190
2019-10-11 14:00 | 171 | 171
2019-10-11 14:30 | 157 | 157
2019-10-11 15:00 | 183 | 183
2019-10-11 15:30 | 215 | 215
2019-10-11 16:00 | 224 | 224
2019-10-11 16:30 | 232 | 232
2019-10-11 17:00 | 240 | 240
2019-10-11 17:30 | 241 | 241
2019-10-11 18:00 | 244 | 244
2019-10-11 18:30 | 250 | 250
2019-10-11 19:00 | 254 | 254
2019-10-11 19:30 | 247 | 247
2019-10-11 20:00 | 244 | 244
2019-10-11 20:30 | 242 | 242
2019-10-11 21:00 | 231 | 231
2019-10-11 21:30 | 222 | 222
2019-10-11 22:00 | 214 | 214
2019-10-11 22:30 | 211 | 211
2019-10-11 23:00 | 208 | 208
2019-10-11 23:30 | 197 | 197
2019-10-12 | 185 | 184
2019-10-12 00:30 | 170 | 170
2019-10-12 01:00 | 161 | 160
2019-10-12 01:30 | 155 | 154
2019-10-12 02:00 | 150 | 149
2019-10-12 02:30 | 146 | 144
2019-10-12 03:00 | 143 | 142
2019-10-12 03:30 | 143 | 142
2019-10-12 04:00 | 144 | 143
2019-10-12 04:30 | 144 | 142
2019-10-12 05:00 | 145 | 143
2019-10-12 05:30 | 149 | 148
2019-10-12 06:00 | 154 | 152
2019-10-12 06:30 | 163 | 161
2019-10-12 07:00 | 173 | 173
2019-10-12 07:30 | 187 | 187
2019-10-12 08:00 | 198 | 198
2019-10-12 08:30 | 205 | 205
2019-10-12 09:00 | 208 | 208
2019-10-12 09:30 | 214 | 214
2019-10-12 10:00 | 211 | 210
2019-10-12 10:30 | 215 | 215
2019-10-12 11:00 | 220 | 220
2019-10-12 11:30 | 216 | 216
2019-10-12 12:00 | 214 | 214
2019-10-12 12:30 | 201 | 201
2019-10-12 13:00 | 169 | 169
2019-10-12 13:30 | 135 | 135
2019-10-12 14:00 | 122 | 121
2019-10-12 14:30 | 133 | 132
2019-10-12 15:00 | 141 | 140
2019-10-12 15:30 | 139 | 138
2019-10-12 16:00 | 156 | 155
2019-10-12 16:30 | 172 | 172
2019-10-12 17:00 | 192 | 192
2019-10-12 17:30 | 205 | 205
2019-10-12 18:00 | 216 | 216
2019-10-12 18:30 | 232 | 232
2019-10-12 19:00 | 242 | 241
2019-10-12 19:30 | 238 | 236
2019-10-12 20:00 | 235 | 234
2019-10-12 20:30 | 231 | 230
2019-10-12 21:00 | 219 | 219
2019-10-12 21:30 | 213 | 213
2019-10-12 22:00 | 208 | 208
2019-10-12 22:30 | 205 | 205
2019-10-12 23:00 | 203 | 203
2019-10-12 23:30 | 193 | 192
2019-10-13 | 180 | 178
2019-10-13 00:30 | 167 | 165
2019-10-13 01:00 | 158 | 155
2019-10-13 01:30 | 149 | 147
2019-10-13 02:00 | 143 | 142
2019-10-13 02:30 | 140 | 138
2019-10-13 03:00 | 138 | 136
2019-10-13 03:30 | 137 | 135
2019-10-13 04:00 | 137 | 135
2019-10-13 04:30 | 137 | 135
2019-10-13 05:00 | 138 | 136
2019-10-13 05:30 | 139 | 136
2019-10-13 06:00 | 139 | 137
2019-10-13 06:30 | 135 | 132
2019-10-13 07:00 | 128 | 126
2019-10-13 07:30 | 124 | 122
2019-10-13 08:00 | 117 | 115
2019-10-13 08:30 | 111 | 109
2019-10-13 09:00 | 104 | 102
2019-10-13 09:30 | 99 | 97
2019-10-13 10:00 | 95 | 94
2019-10-13 10:30 | 96 | 96
2019-10-13 11:00 | 104 | 103
2019-10-13 11:30 | 112 | 112
2019-10-13 12:00 | 126 | 126
2019-10-13 12:30 | 131 | 130
2019-10-13 13:00 | 133 | 133
2019-10-13 13:30 | 137 | 137
2019-10-13 14:00 | 139 | 139
2019-10-13 14:30 | 135 | 135
2019-10-13 15:00 | 135 | 134
2019-10-13 15:30 | 145 | 145
2019-10-13 16:00 | 160 | 160
2019-10-13 16:30 | 175 | 175
2019-10-13 17:00 | 193 | 193
2019-10-13 17:30 | 207 | 207
2019-10-13 18:00 | 220 | 220
2019-10-13 18:30 | 236 | 236
2019-10-13 19:00 | 242 | 242
2019-10-13 19:30 | 236 | 236
2019-10-13 20:00 | 231 | 231
2019-10-13 20:30 | 229 | 229
2019-10-13 21:00 | 219 | 219
2019-10-13 21:30 | 209 | 209
2019-10-13 22:00 | 200 | 200
2019-10-13 22:30 | 196 | 195
2019-10-13 23:00 | 193 | 192
2019-10-13 23:30 | 183 | 182
2019-10-14 | 169 | 168
2019-10-14 00:30 | 156 | 155
2019-10-14 01:00 | 149 | 148
2019-10-14 01:30 | 144 | 142
2019-10-14 02:00 | 139 | 138
2019-10-14 02:30 | 138 | 136
2019-10-14 03:00 | 137 | 135
2019-10-14 03:30 | 137 | 135
2019-10-14 04:00 | 137 | 136
2019-10-14 04:30 | 142 | 141
2019-10-14 05:00 | 150 | 149
2019-10-14 05:30 | 161 | 160
2019-10-14 06:00 | 171 | 170
2019-10-14 06:30 | 183 | 183
2019-10-14 07:00 | 189 | 189
2019-10-14 07:30 | 191 | 191
2019-10-14 08:00 | 179 | 179
2019-10-14 08:30 | 172 | 172
2019-10-14 09:00 | 169 | 168
2019-10-14 09:30 | 158 | 158
2019-10-14 10:00 | 159 | 158
2019-10-14 10:30 | 161 | 160
2019-10-14 11:00 | 161 | 159
2019-10-14 11:30 | 160 | 159
2019-10-14 12:00 | 155 | 154
2019-10-14 12:30 | 154 | 154
2019-10-14 13:00 | 156 | 156
2019-10-14 13:30 | 158 | 158
2019-10-14 14:00 | 163 | 163
2019-10-14 14:30 | 167 | 166
2019-10-14 15:00 | 174 | 173
2019-10-14 15:30 | 186 | 185
2019-10-14 16:00 | 203 | 202
2019-10-14 16:30 | 219 | 219
2019-10-14 17:00 | 236 | 236
2019-10-14 17:30 | 244 | 244
2019-10-14 18:00 | 251 | 251
2019-10-14 18:30 | 263 | 263
2019-10-14 19:00 | 268 | 267
2019-10-14 19:30 | 258 | 257
2019-10-14 20:00 | 251 | 250
2019-10-14 20:30 | 247 | 246
2019-10-14 21:00 | 236 | 235
2019-10-14 21:30 | 224 | 224
2019-10-14 22:00 | 213 | 213
2019-10-14 22:30 | 207 | 207
2019-10-14 23:00 | 202 | 202
2019-10-14 23:30 | 190 | 190
2019-10-15 | 173 | 173
2019-10-15 00:30 | 160 | 160
2019-10-15 01:00 | 152 | 151
2019-10-15 01:30 | 147 | 146
2019-10-15 02:00 | 143 | 143
2019-10-15 02:30 | 141 | 140
2019-10-15 03:00 | 140 | 139
2019-10-15 03:30 | 138 | 137
2019-10-15 04:00 | 138 | 138
2019-10-15 04:30 | 144 | 144
2019-10-15 05:00 | 151 | 151
2019-10-15 05:30 | 162 | 162
2019-10-15 06:00 | 173 | 173
2019-10-15 06:30 | 191 | 191
2019-10-15 07:00 | 204 | 204
2019-10-15 07:30 | 218 | 217
2019-10-15 08:00 | 222 | 222
2019-10-15 08:30 | 219 | 219
2019-10-15 09:00 | 215 | 215
2019-10-15 09:30 | 205 | 205
2019-10-15 10:00 | 201 | 201
2019-10-15 10:30 | 199 | 199
2019-10-15 11:00 | 198 | 198
2019-10-15 11:30 | 196 | 196
2019-10-15 12:00 | 193 | 193
2019-10-15 12:30 | 187 | 187
2019-10-15 13:00 | 185 | 185
2019-10-15 13:30 | 191 | 191
2019-10-15 14:00 | 192 | 192
2019-10-15 14:30 | 201 | 201
2019-10-15 15:00 | 204 | 204
2019-10-15 15:30 | 202 | 202
2019-10-15 16:00 | 212 | 212
2019-10-15 16:30 | 225 | 225
2019-10-15 17:00 | 241 | 241
2019-10-15 17:30 | 250 | 250
2019-10-15 18:00 | 255 | 255
2019-10-15 18:30 | 266 | 266
2019-10-15 19:00 | 272 | 272
2019-10-15 19:30 | 264 | 264
2019-10-15 20:00 | 258 | 258
2019-10-15 20:30 | 253 | 253
2019-10-15 21:00 | 241 | 241
2019-10-15 21:30 | 230 | 230
2019-10-15 22:00 | 219 | 219
2019-10-15 22:30 | 212 | 212
2019-10-15 23:00 | 208 | 208
2019-10-15 23:30 | 195 | 195
2019-10-16 | 180 | 179
2019-10-16 00:30 | 165 | 164
2019-10-16 01:00 | 156 | 156
2019-10-16 01:30 | 151 | 151
2019-10-16 02:00 | 148 | 147
2019-10-16 02:30 | 146 | 145
2019-10-16 03:00 | 144 | 143
2019-10-16 03:30 | 144 | 143
2019-10-16 04:00 | 145 | 144
2019-10-16 04:30 | 148 | 147
2019-10-16 05:00 | 154 | 154
2019-10-16 05:30 | 163 | 163
2019-10-16 06:00 | 172 | 172
2019-10-16 06:30 | 187 | 187
2019-10-16 07:00 | 202 | 202
2019-10-16 07:30 | 211 | 210
2019-10-16 08:00 | 208 | 207
2019-10-16 08:30 | 200 | 199
2019-10-16 09:00 | 185 | 185
2019-10-16 09:30 | 194 | 193
2019-10-16 10:00 | 187 | 186
2019-10-16 10:30 | 178 | 177
2019-10-16 11:00 | 180 | 178
2019-10-16 11:30 | 172 | 172
2019-10-16 12:00 | 165 | 165
2019-10-16 12:30 | 163 | 163
2019-10-16 13:00 | 163 | 163
2019-10-16 13:30 | 169 | 169
2019-10-16 14:00 | 180 | 178
2019-10-16 14:30 | 190 | 188
2019-10-16 15:00 | 202 | 200
2019-10-16 15:30 | 214 | 212
2019-10-16 16:00 | 231 | 229
2019-10-16 16:30 | 246 | 244
2019-10-16 17:00 | 259 | 257
2019-10-16 17:30 | 264 | 262
2019-10-16 18:00 | 266 | 264
2019-10-16 18:30 | 274 | 272
2019-10-16 19:00 | 280 | 278
2019-10-16 19:30 | 271 | 270
2019-10-16 20:00 | 265 | 264
2019-10-16 20:30 | 260 | 259
2019-10-16 21:00 | 248 | 247
2019-10-16 21:30 | 235 | 235
2019-10-16 22:00 | 223 | 223
2019-10-16 22:30 | 217 | 217
2019-10-16 23:00 | 211 | 211
2019-10-16 23:30 | 199 | 199
2019-10-17 | 183 | 183
2019-10-17 00:30 | 168 | 168
2019-10-17 01:00 | 160 | 160
2019-10-17 01:30 | 155 | 154
2019-10-17 02:00 | 150 | 150
2019-10-17 02:30 | 148 | 148
2019-10-17 03:00 | 147 | 147
2019-10-17 03:30 | 147 | 147
2019-10-17 04:00 | 147 | 147
2019-10-17 04:30 | 150 | 150
2019-10-17 05:00 | 158 | 158
2019-10-17 05:30 | 167 | 167
2019-10-17 06:00 | 172 | 172
2019-10-17 06:30 | 190 | 190
2019-10-17 07:00 | 196 | 195
2019-10-17 07:30 | 202 | 201
2019-10-17 08:00 | 194 | 193
2019-10-17 08:30 | 187 | 186
2019-10-17 09:00 | 182 | 180
2019-10-17 09:30 | 180 | 177
2019-10-17 10:00 | 180 | 177
2019-10-17 10:30 | 185 | 182
2019-10-17 11:00 | 172 | 168
2019-10-17 11:30 | 172 | 168
2019-10-17 12:00 | 176 | 172
2019-10-17 12:30 | 179 | 175
2019-10-17 13:00 | 184 | 180
2019-10-17 13:30 | 191 | 187
2019-10-17 14:00 | 200 | 196
2019-10-17 14:30 | 213 | 211
2019-10-17 15:00 | 234 | 233
2019-10-17 15:30 | 255 | 254
2019-10-17 16:00 | 269 | 269
2019-10-17 16:30 | 278 | 277
2019-10-17 17:00 | 265 | 265
2019-10-17 17:30 | 252 | 252
2019-10-17 18:00 | 252 | 252
2019-10-17 18:30 | 260 | 259
2019-10-17 19:00 | 268 | 268
2019-10-17 19:30 | 262 | 262
2019-10-17 20:00 | 258 | 258
2019-10-17 20:30 | 254 | 254
2019-10-17 21:00 | 242 | 241
2019-10-17 21:30 | 230 | 229
2019-10-17 22:00 | 220 | 219
2019-10-17 22:30 | 214 | 213
2019-10-17 23:00 | 205 | 205
2019-10-17 23:30 | 193 | 193
2019-10-18 | 179 | 179
2019-10-18 00:30 | 167 | 167
2019-10-18 01:00 | 158 | 158
2019-10-18 01:30 | 153 | 153
2019-10-18 02:00 | 149 | 149
2019-10-18 02:30 | 147 | 146
2019-10-18 03:00 | 145 | 145
2019-10-18 03:30 | 145 | 145
2019-10-18 04:00 | 145 | 145
2019-10-18 04:30 | 149 | 149
2019-10-18 05:00 | 156 | 156
2019-10-18 05:30 | 163 | 163
2019-10-18 06:00 | 171 | 171
2019-10-18 06:30 | 180 | 180
2019-10-18 07:00 | 191 | 191
2019-10-18 07:30 | 190 | 190
2019-10-18 08:00 | 182 | 182
2019-10-18 08:30 | 186 | 186
2019-10-18 09:00 | 163 | 163
2019-10-18 09:30 | 158 | 157
2019-10-18 10:00 | 156 | 155
2019-10-18 10:30 | 154 | 153
2019-10-18 11:00 | 149 | 148
2019-10-18 11:30 | 148 | 147
2019-10-18 12:00 | 148 | 147
2019-10-18 12:30 | 149 | 148
2019-10-18 13:00 | 151 | 150
2019-10-18 13:30 | 155 | 155
2019-10-18 14:00 | 160 | 160
2019-10-18 14:30 | 171 | 171
2019-10-18 15:00 | 178 | 177
2019-10-18 15:30 | 191 | 190
2019-10-18 16:00 | 207 | 206
2019-10-18 16:30 | 225 | 225
2019-10-18 17:00 | 240 | 239
2019-10-18 17:30 | 244 | 244
2019-10-18 18:00 | 243 | 243
2019-10-18 18:30 | 250 | 249
2019-10-18 19:00 | 256 | 256
2019-10-18 19:30 | 250 | 250
2019-10-18 20:00 | 246 | 245
2019-10-18 20:30 | 242 | 242
2019-10-18 21:00 | 231 | 231
2019-10-18 21:30 | 222 | 222
2019-10-18 22:00 | 214 | 214
2019-10-18 22:30 | 210 | 210
2019-10-18 23:00 | 206 | 206
2019-10-18 23:30 | 194 | 194
2019-10-19 | 179 | 179
2019-10-19 00:30 | 166 | 166
2019-10-19 01:00 | 159 | 159
2019-10-19 01:30 | 153 | 153
2019-10-19 02:00 | 149 | 149
2019-10-19 02:30 | 147 | 147
2019-10-19 03:00 | 147 | 147
2019-10-19 03:30 | 147 | 147
2019-10-19 04:00 | 146 | 146
2019-10-19 04:30 | 146 | 146
2019-10-19 05:00 | 148 | 148
2019-10-19 05:30 | 149 | 149
2019-10-19 06:00 | 150 | 150
2019-10-19 06:30 | 154 | 154
2019-10-19 07:00 | 160 | 160
2019-10-19 07:30 | 161 | 161
2019-10-19 08:00 | 160 | 160
2019-10-19 08:30 | 167 | 167
2019-10-19 09:00 | 172 | 172
2019-10-19 09:30 | 192 | 192
2019-10-19 10:00 | 200 | 200
2019-10-19 10:30 | 197 | 197
2019-10-19 11:00 | 181 | 180
2019-10-19 11:30 | 192 | 192
2019-10-19 12:00 | 205 | 205
2019-10-19 12:30 | 197 | 197
2019-10-19 13:00 | 150 | 149
2019-10-19 13:30 | 124 | 123
2019-10-19 14:00 | 133 | 132
2019-10-19 14:30 | 146 | 146
2019-10-19 15:00 | 158 | 157
2019-10-19 15:30 | 169 | 169
2019-10-19 16:00 | 193 | 193
2019-10-19 16:30 | 208 | 208
2019-10-19 17:00 | 215 | 214
2019-10-19 17:30 | 219 | 218
2019-10-19 18:00 | 225 | 225
2019-10-19 18:30 | 235 | 234
2019-10-19 19:00 | 241 | 240
2019-10-19 19:30 | 236 | 235
2019-10-19 20:00 | 232 | 231
2019-10-19 20:30 | 228 | 227
2019-10-19 21:00 | 217 | 217
2019-10-19 21:30 | 210 | 210
2019-10-19 22:00 | 203 | 203
2019-10-19 22:30 | 201 | 201
2019-10-19 23:00 | 200 | 200
2019-10-19 23:30 | 189 | 189
2019-10-20 | 175 | 175
2019-10-20 00:30 | 163 | 162
2019-10-20 01:00 | 155 | 155
2019-10-20 01:30 | 149 | 149
2019-10-20 02:00 | 144 | 144
2019-10-20 02:30 | 141 | 141
2019-10-20 03:00 | 139 | 139
2019-10-20 03:30 | 138 | 138
2019-10-20 04:00 | 138 | 138
2019-10-20 04:30 | 138 | 138
2019-10-20 05:00 | 138 | 138
2019-10-20 05:30 | 138 | 138
2019-10-20 06:00 | 136 | 136
2019-10-20 06:30 | 133 | 133
2019-10-20 07:00 | 130 | 130
2019-10-20 07:30 | 129 | 129
2019-10-20 08:00 | 123 | 123
2019-10-20 08:30 | 119 | 118
2019-10-20 09:00 | 114 | 113
2019-10-20 09:30 | 111 | 110
2019-10-20 10:00 | 108 | 107
2019-10-20 10:30 | 103 | 103
2019-10-20 11:00 | 101 | 101
2019-10-20 11:30 | 100 | 100
2019-10-20 12:00 | 101 | 101
2019-10-20 12:30 | 104 | 104
2019-10-20 13:00 | 105 | 105
2019-10-20 13:30 | 110 | 110
2019-10-20 14:00 | 118 | 118
2019-10-20 14:30 | 128 | 128
2019-10-20 15:00 | 139 | 139
2019-10-20 15:30 | 149 | 149
2019-10-20 16:00 | 164 | 164
2019-10-20 16:30 | 180 | 180
2019-10-20 17:00 | 198 | 198
2019-10-20 17:30 | 212 | 212
2019-10-20 18:00 | 223 | 223
2019-10-20 18:30 | 234 | 234
2019-10-20 19:00 | 239 | 239
2019-10-20 19:30 | 231 | 231
2019-10-20 20:00 | 226 | 226
2019-10-20 20:30 | 224 | 224
2019-10-20 21:00 | 213 | 213
2019-10-20 21:30 | 205 | 205
2019-10-20 22:00 | 199 | 198
2019-10-20 22:30 | 195 | 195
2019-10-20 23:00 | 193 | 192
2019-10-20 23:30 | 182 | 182
2019-10-21 | 170 | 170
2019-10-21 00:30 | 158 | 157
2019-10-21 01:00 | 150 | 149
2019-10-21 01:30 | 145 | 144
2019-10-21 02:00 | 141 | 140
2019-10-21 02:30 | 139 | 138
2019-10-21 03:00 | 138 | 138
2019-10-21 03:30 | 139 | 139
2019-10-21 04:00 | 139 | 139
2019-10-21 04:30 | 143 | 143
2019-10-21 05:00 | 149 | 149
2019-10-21 05:30 | 157 | 157
2019-10-21 06:00 | 163 | 162
2019-10-21 06:30 | 170 | 170
2019-10-21 07:00 | 172 | 172
2019-10-21 07:30 | 173 | 173
2019-10-21 08:00 | 169 | 168
2019-10-21 08:30 | 173 | 173
2019-10-21 09:00 | 175 | 175
2019-10-21 09:30 | 169 | 169
2019-10-21 10:00 | 163 | 163
2019-10-21 10:30 | 158 | 158
2019-10-21 11:00 | 157 | 157
2019-10-21 11:30 | 153 | 153
2019-10-21 12:00 | 146 | 146
2019-10-21 12:30 | 144 | 144
2019-10-21 13:00 | 141 | 141
2019-10-21 13:30 | 144 | 144
2019-10-21 14:00 | 148 | 148
2019-10-21 14:30 | 157 | 157
2019-10-21 15:00 | 166 | 166
2019-10-21 15:30 | 178 | 178
2019-10-21 16:00 | 192 | 192
2019-10-21 16:30 | 209 | 208
2019-10-21 17:00 | 228 | 227
2019-10-21 17:30 | 239 | 239
2019-10-21 18:00 | 245 | 245
2019-10-21 18:30 | 254 | 254
2019-10-21 19:00 | 261 | 261
2019-10-21 19:30 | 253 | 253
2019-10-21 20:00 | 247 | 247
2019-10-21 20:30 | 243 | 242
2019-10-21 21:00 | 232 | 231
2019-10-21 21:30 | 220 | 220
2019-10-21 22:00 | 209 | 209
2019-10-21 22:30 | 204 | 204
2019-10-21 23:00 | 199 | 199
2019-10-21 23:30 | 186 | 186
2019-10-22 | 170 | 170
2019-10-22 00:30 | 157 | 157
2019-10-22 01:00 | 150 | 150
2019-10-22 01:30 | 145 | 145
2019-10-22 02:00 | 142 | 142
2019-10-22 02:30 | 139 | 139
2019-10-22 03:00 | 139 | 139
2019-10-22 03:30 | 140 | 140
2019-10-22 04:00 | 140 | 140
2019-10-22 04:30 | 145 | 145
2019-10-22 05:00 | 152 | 152
2019-10-22 05:30 | 160 | 160
2019-10-22 06:00 | 167 | 167
2019-10-22 06:30 | 177 | 177
2019-10-22 07:00 | 185 | 184
2019-10-22 07:30 | 190 | 188
2019-10-22 08:00 | 182 | 181
2019-10-22 08:30 | 171 | 170
2019-10-22 09:00 | 175 | 175
2019-10-22 09:30 | 184 | 183
2019-10-22 10:00 | 171 | 171
2019-10-22 10:30 | 167 | 167
2019-10-22 11:00 | 163 | 163
2019-10-22 11:30 | 167 | 167
2019-10-22 12:00 | 170 | 170
2019-10-22 12:30 | 161 | 161
2019-10-22 13:00 | 152 | 152
2019-10-22 13:30 | 151 | 151
2019-10-22 14:00 | 155 | 155
2019-10-22 14:30 | 164 | 164
2019-10-22 15:00 | 173 | 173
2019-10-22 15:30 | 184 | 184
2019-10-22 16:00 | 201 | 201
2019-10-22 16:30 | 216 | 216
2019-10-22 17:00 | 234 | 234
2019-10-22 17:30 | 244 | 244
2019-10-22 18:00 | 249 | 249
2019-10-22 18:30 | 258 | 258
2019-10-22 19:00 | 265 | 265
2019-10-22 19:30 | 257 | 257
2019-10-22 20:00 | 251 | 251
2019-10-22 20:30 | 247 | 247
2019-10-22 21:00 | 233 | 233
2019-10-22 21:30 | 222 | 222
2019-10-22 22:00 | 212 | 212
2019-10-22 22:30 | 206 | 206
2019-10-22 23:00 | 201 | 201
2019-10-22 23:30 | 187 | 187
2019-10-23 | 173 | 173
2019-10-23 00:30 | 161 | 161
2019-10-23 01:00 | 152 | 152
2019-10-23 01:30 | 148 | 148
2019-10-23 02:00 | 145 | 144
2019-10-23 02:30 | 142 | 141
2019-10-23 03:00 | 142 | 141
2019-10-23 03:30 | 142 | 141
2019-10-23 04:00 | 142 | 141
2019-10-23 04:30 | 144 | 143
2019-10-23 05:00 | 150 | 150
2019-10-23 05:30 | 160 | 159
2019-10-23 06:00 | 167 | 167
2019-10-23 06:30 | 176 | 176
2019-10-23 07:00 | 180 | 180
2019-10-23 07:30 | 181 | 181
2019-10-23 08:00 | 174 | 173
2019-10-23 08:30 | 171 | 170
2019-10-23 09:00 | 163 | 162
2019-10-23 09:30 | 154 | 152
2019-10-23 10:00 | 144 | 142
2019-10-23 10:30 | 139 | 137
2019-10-23 11:00 | 137 | 135
2019-10-23 11:30 | 135 | 132
2019-10-23 12:00 | 135 | 132
2019-10-23 12:30 | 138 | 135
2019-10-23 13:00 | 141 | 138
2019-10-23 13:30 | 146 | 143
2019-10-23 14:00 | 154 | 151
2019-10-23 14:30 | 162 | 161
2019-10-23 15:00 | 171 | 169
2019-10-23 15:30 | 185 | 183
2019-10-23 16:00 | 203 | 201
2019-10-23 16:30 | 221 | 220
2019-10-23 17:00 | 239 | 238
2019-10-23 17:30 | 249 | 247
2019-10-23 18:00 | 252 | 251
2019-10-23 18:30 | 260 | 259
2019-10-23 19:00 | 269 | 267
2019-10-23 19:30 | 261 | 260
2019-10-23 20:00 | 256 | 255
2019-10-23 20:30 | 251 | 250
2019-10-23 21:00 | 239 | 238
2019-10-23 21:30 | 227 | 227
2019-10-23 22:00 | 216 | 216
2019-10-23 22:30 | 209 | 209
2019-10-23 23:00 | 204 | 204
2019-10-23 23:30 | 190 | 190
2019-10-24 | 175 | 175
2019-10-24 00:30 | 162 | 161
2019-10-24 01:00 | 154 | 153
2019-10-24 01:30 | 150 | 149
2019-10-24 02:00 | 146 | 145
2019-10-24 02:30 | 144 | 144
2019-10-24 03:00 | 143 | 142
2019-10-24 03:30 | 143 | 143
2019-10-24 04:00 | 144 | 143
2019-10-24 04:30 | 148 | 148
2019-10-24 05:00 | 154 | 153
2019-10-24 05:30 | 163 | 163
2019-10-24 06:00 | 170 | 170
2019-10-24 06:30 | 180 | 180
2019-10-24 07:00 | 184 | 184
2019-10-24 07:30 | 185 | 185
2019-10-24 08:00 | 175 | 175
2019-10-24 08:30 | 163 | 163
2019-10-24 09:00 | 154 | 154
2019-10-24 09:30 | 147 | 147
2019-10-24 10:00 | 141 | 141
2019-10-24 10:30 | 139 | 139
2019-10-24 11:00 | 137 | 137
2019-10-24 11:30 | 137 | 137
2019-10-24 12:00 | 139 | 139
2019-10-24 12:30 | 140 | 140
2019-10-24 13:00 | 142 | 142
2019-10-24 13:30 | 146 | 146
2019-10-24 14:00 | 155 | 155
2019-10-24 14:30 | 168 | 167
2019-10-24 15:00 | 177 | 177
2019-10-24 15:30 | 191 | 191
2019-10-24 16:00 | 209 | 209
2019-10-24 16:30 | 225 | 225
2019-10-24 17:00 | 241 | 241
2019-10-24 17:30 | 249 | 249
2019-10-24 18:00 | 253 | 253
2019-10-24 18:30 | 261 | 261
2019-10-24 19:00 | 269 | 269
2019-10-24 19:30 | 261 | 261
2019-10-24 20:00 | 256 | 256
2019-10-24 20:30 | 253 | 253
2019-10-24 21:00 | 238 | 238
2019-10-24 21:30 | 229 | 229
2019-10-24 22:00 | 218 | 218
2019-10-24 22:30 | 212 | 212
2019-10-24 23:00 | 206 | 206
2019-10-24 23:30 | 193 | 193
2019-10-25 | 179 | 178
2019-10-25 00:30 | 166 | 166
2019-10-25 01:00 | 157 | 157
2019-10-25 01:30 | 152 | 152
2019-10-25 02:00 | 148 | 148
2019-10-25 02:30 | 147 | 147
2019-10-25 03:00 | 147 | 147
2019-10-25 03:30 | 147 | 147
2019-10-25 04:00 | 148 | 148
2019-10-25 04:30 | 152 | 152
2019-10-25 05:00 | 156 | 156
2019-10-25 05:30 | 164 | 164
2019-10-25 06:00 | 169 | 169
2019-10-25 06:30 | 178 | 177
2019-10-25 07:00 | 182 | 181
2019-10-25 07:30 | 182 | 180
2019-10-25 08:00 | 174 | 174
2019-10-25 08:30 | 167 | 166
2019-10-25 09:00 | 157 | 156
2019-10-25 09:30 | 150 | 149
2019-10-25 10:00 | 145 | 143
2019-10-25 10:30 | 144 | 142
2019-10-25 11:00 | 142 | 141
2019-10-25 11:30 | 141 | 141
2019-10-25 12:00 | 142 | 142
2019-10-25 12:30 | 144 | 144
2019-10-25 13:00 | 148 | 147
2019-10-25 13:30 | 153 | 151
2019-10-25 14:00 | 159 | 158
2019-10-25 14:30 | 170 | 169
2019-10-25 15:00 | 180 | 179
2019-10-25 15:30 | 191 | 191
2019-10-25 16:00 | 207 | 207
2019-10-25 16:30 | 224 | 223
2019-10-25 17:00 | 239 | 238
2019-10-25 17:30 | 245 | 244
2019-10-25 18:00 | 245 | 245
2019-10-25 18:30 | 251 | 250
2019-10-25 19:00 | 259 | 258
2019-10-25 19:30 | 252 | 252
2019-10-25 20:00 | 249 | 248
2019-10-25 20:30 | 244 | 244
2019-10-25 21:00 | 233 | 233
2019-10-25 21:30 | 223 | 223
2019-10-25 22:00 | 215 | 215
2019-10-25 22:30 | 211 | 211
2019-10-25 23:00 | 208 | 208
2019-10-25 23:30 | 196 | 196
2019-10-26 | 181 | 180
2019-10-26 00:30 | 170 | 169
2019-10-26 01:00 | 165 | 165
2019-10-26 01:30 | 161 | 160
2019-10-26 02:00 | 155 | 155
2019-10-26 02:30 | 152 | 151
2019-10-26 03:00 | 150 | 150
2019-10-26 03:30 | 149 | 149
2019-10-26 04:00 | 149 | 149
2019-10-26 04:30 | 149 | 149
2019-10-26 05:00 | 149 | 149
2019-10-26 05:30 | 150 | 150
2019-10-26 06:00 | 150 | 150
2019-10-26 06:30 | 149 | 148
2019-10-26 07:00 | 145 | 145
2019-10-26 07:30 | 144 | 143
2019-10-26 08:00 | 140 | 139
2019-10-26 08:30 | 135 | 135
2019-10-26 09:00 | 129 | 129
2019-10-26 09:30 | 128 | 127
2019-10-26 10:00 | 123 | 122
2019-10-26 10:30 | 118 | 118
2019-10-26 11:00 | 116 | 116
2019-10-26 11:30 | 114 | 114
2019-10-26 12:00 | 116 | 115
2019-10-26 12:30 | 114 | 114
2019-10-26 13:00 | 118 | 118
2019-10-26 13:30 | 124 | 124
2019-10-26 14:00 | 132 | 132
2019-10-26 14:30 | 143 | 143
2019-10-26 15:00 | 155 | 155
2019-10-26 15:30 | 170 | 169
2019-10-26 16:00 | 187 | 186
2019-10-26 16:30 | 203 | 203
2019-10-26 17:00 | 221 | 220
2019-10-26 17:30 | 229 | 227
2019-10-26 18:00 | 232 | 231
2019-10-26 18:30 | 241 | 239
2019-10-26 19:00 | 249 | 249
2019-10-26 19:30 | 242 | 242
2019-10-26 20:00 | 235 | 234
2019-10-26 20:30 | 232 | 232
2019-10-26 21:00 | 223 | 223
2019-10-26 21:30 | 216 | 216
2019-10-26 22:00 | 208 | 208
2019-10-26 22:30 | 205 | 205
2019-10-26 23:00 | 201 | 200
2019-10-26 23:30 | 187 | 187
2019-10-27 | 173 | 172
2019-10-27 00:30 | 161 | 159
2019-10-27 01:00 | 153 | 151
2019-10-27 01:30 | 147 | 145
2019-10-27 02:00 | 141 | 140
2019-10-27 02:30 | 139 | 138
2019-10-27 03:00 | 137 | 135
2019-10-27 03:30 | 136 | 135
2019-10-27 04:00 | 136 | 134
2019-10-27 04:30 | 136 | 134
2019-10-27 05:00 | 136 | 134
2019-10-27 05:30 | 136 | 134
2019-10-27 06:00 | 132 | 130
2019-10-27 06:30 | 129 | 127
2019-10-27 07:00 | 125 | 124
2019-10-27 07:30 | 123 | 122
2019-10-27 08:00 | 119 | 118
2019-10-27 08:30 | 119 | 119
2019-10-27 09:00 | 117 | 117
2019-10-27 09:30 | 115 | 115
2019-10-27 10:00 | 114 | 114
2019-10-27 10:30 | 113 | 113
2019-10-27 11:00 | 113 | 113
2019-10-27 11:30 | 114 | 114
2019-10-27 12:00 | 116 | 116
2019-10-27 12:30 | 117 | 117
2019-10-27 13:00 | 120 | 120
2019-10-27 13:30 | 126 | 125
2019-10-27 14:00 | 133 | 133
2019-10-27 14:30 | 143 | 143
2019-10-27 15:00 | 156 | 156
2019-10-27 15:30 | 174 | 174
2019-10-27 16:00 | 188 | 187
2019-10-27 16:30 | 199 | 198
2019-10-27 17:00 | 216 | 216
2019-10-27 17:30 | 226 | 226
2019-10-27 18:00 | 233 | 233
2019-10-27 18:30 | 243 | 243
2019-10-27 19:00 | 251 | 251
2019-10-27 19:30 | 244 | 244
2019-10-27 20:00 | 239 | 239
2019-10-27 20:30 | 234 | 234
2019-10-27 21:00 | 223 | 223
2019-10-27 21:30 | 216 | 215
2019-10-27 22:00 | 206 | 206
2019-10-27 22:30 | 203 | 202
2019-10-27 23:00 | 197 | 196
2019-10-27 23:30 | 187 | 186
2019-10-28 | 176 | 175
2019-10-28 00:30 | 163 | 162
2019-10-28 01:00 | 154 | 153
2019-10-28 01:30 | 148 | 147
2019-10-28 02:00 | 144 | 143
2019-10-28 02:30 | 142 | 142
2019-10-28 03:00 | 141 | 141
2019-10-28 03:30 | 142 | 142
2019-10-28 04:00 | 148 | 148
2019-10-28 04:30 | 151 | 151
2019-10-28 05:00 | 158 | 158
2019-10-28 05:30 | 168 | 168
2019-10-28 06:00 | 181 | 181
2019-10-28 06:30 | 198 | 198
2019-10-28 07:00 | 213 | 212
2019-10-28 07:30 | 220 | 220
2019-10-28 08:00 | 218 | 218
2019-10-28 08:30 | 218 | 217
2019-10-28 09:00 | 213 | 211
2019-10-28 09:30 | 205 | 203
2019-10-28 10:00 | 206 | 203
2019-10-28 10:30 | 204 | 201
2019-10-28 11:00 | 192 | 190
2019-10-28 11:30 | 197 | 194
2019-10-28 12:00 | 202 | 199
2019-10-28 12:30 | 207 | 203
2019-10-28 13:00 | 206 | 203
2019-10-28 13:30 | 213 | 211
2019-10-28 14:00 | 201 | 199
2019-10-28 14:30 | 211 | 210
2019-10-28 15:00 | 210 | 209
2019-10-28 15:30 | 221 | 220
2019-10-28 16:00 | 230 | 229
2019-10-28 16:30 | 244 | 243
2019-10-28 17:00 | 258 | 257
2019-10-28 17:30 | 263 | 263
2019-10-28 18:00 | 269 | 268
2019-10-28 18:30 | 275 | 273
2019-10-28 19:00 | 280 | 278
2019-10-28 19:30 | 270 | 269
2019-10-28 20:00 | 265 | 263
2019-10-28 20:30 | 258 | 257
2019-10-28 21:00 | 245 | 244
2019-10-28 21:30 | 234 | 233
2019-10-28 22:00 | 222 | 222
2019-10-28 22:30 | 216 | 216
2019-10-28 23:00 | 212 | 212
2019-10-28 23:30 | 199 | 199
2019-10-29 | 182 | 182
2019-10-29 00:30 | 168 | 168
2019-10-29 01:00 | 160 | 160
2019-10-29 01:30 | 156 | 156
2019-10-29 02:00 | 152 | 152
2019-10-29 02:30 | 150 | 149
2019-10-29 03:00 | 149 | 149
2019-10-29 03:30 | 149 | 149
2019-10-29 04:00 | 149 | 149
2019-10-29 04:30 | 153 | 153
2019-10-29 05:00 | 159 | 159
2019-10-29 05:30 | 166 | 166
2019-10-29 06:00 | 173 | 173
2019-10-29 06:30 | 185 | 185
2019-10-29 07:00 | 194 | 193
2019-10-29 07:30 | 203 | 203
2019-10-29 08:00 | 198 | 198
2019-10-29 08:30 | 191 | 191
2019-10-29 09:00 | 181 | 181
2019-10-29 09:30 | 174 | 174
2019-10-29 10:00 | 172 | 172
2019-10-29 10:30 | 173 | 173
2019-10-29 11:00 | 171 | 171
2019-10-29 11:30 | 167 | 167
2019-10-29 12:00 | 168 | 168
2019-10-29 12:30 | 166 | 166
2019-10-29 13:00 | 167 | 167
2019-10-29 13:30 | 168 | 168
2019-10-29 14:00 | 174 | 174
2019-10-29 14:30 | 184 | 184
2019-10-29 15:00 | 195 | 194
2019-10-29 15:30 | 205 | 205
2019-10-29 16:00 | 223 | 223
2019-10-29 16:30 | 241 | 241
2019-10-29 17:00 | 257 | 257
2019-10-29 17:30 | 260 | 260
2019-10-29 18:00 | 265 | 265
2019-10-29 18:30 | 271 | 270
2019-10-29 19:00 | 278 | 277
2019-10-29 19:30 | 272 | 271
2019-10-29 20:00 | 265 | 265
2019-10-29 20:30 | 261 | 261
2019-10-29 21:00 | 248 | 248
2019-10-29 21:30 | 237 | 237
2019-10-29 22:00 | 226 | 226
2019-10-29 22:30 | 221 | 221
2019-10-29 23:00 | 214 | 214
2019-10-29 23:30 | 199 | 199
2019-10-30 | 184 | 184
2019-10-30 00:30 | 167 | 167
2019-10-30 01:00 | 161 | 161
2019-10-30 01:30 | 156 | 156
2019-10-30 02:00 | 152 | 152
2019-10-30 02:30 | 149 | 149
2019-10-30 03:00 | 148 | 148
2019-10-30 03:30 | 148 | 148
2019-10-30 04:00 | 148 | 148
2019-10-30 04:30 | 154 | 153
2019-10-30 05:00 | 159 | 159
2019-10-30 05:30 | 166 | 166
2019-10-30 06:00 | 173 | 172
2019-10-30 06:30 | 185 | 183
2019-10-30 07:00 | 203 | 201
2019-10-30 07:30 | 218 | 218
2019-10-30 08:00 | 222 | 222
2019-10-30 08:30 | 209 | 209
2019-10-30 09:00 | 221 | 221
2019-10-30 09:30 | 220 | 220
2019-10-30 10:00 | 208 | 208
2019-10-30 10:30 | 214 | 214
2019-10-30 11:00 | 212 | 212
2019-10-30 11:30 | 212 | 212
2019-10-30 12:00 | 208 | 208
2019-10-30 12:30 | 202 | 202
2019-10-30 13:00 | 200 | 199
2019-10-30 13:30 | 222 | 222
2019-10-30 14:00 | 232 | 231
2019-10-30 14:30 | 236 | 235
2019-10-30 15:00 | 235 | 235
2019-10-30 15:30 | 226 | 226
2019-10-30 16:00 | 225 | 225
2019-10-30 16:30 | 231 | 231
2019-10-30 17:00 | 245 | 245
2019-10-30 17:30 | 252 | 252
2019-10-30 18:00 | 257 | 257
2019-10-30 18:30 | 264 | 264
2019-10-30 19:00 | 268 | 268
2019-10-30 19:30 | 263 | 263
2019-10-30 20:00 | 257 | 257
2019-10-30 20:30 | 250 | 250
2019-10-30 21:00 | 237 | 236
2019-10-30 21:30 | 228 | 227
2019-10-30 22:00 | 217 | 217
2019-10-30 22:30 | 210 | 210
2019-10-30 23:00 | 207 | 206
2019-10-30 23:30 | 192 | 192
2019-10-31 | 177 | 177
2019-10-31 00:30 | 164 | 163
2019-10-31 01:00 | 155 | 155
2019-10-31 01:30 | 150 | 150
2019-10-31 02:00 | 147 | 147
2019-10-31 02:30 | 144 | 144
2019-10-31 03:00 | 145 | 145
2019-10-31 03:30 | 144 | 144
2019-10-31 04:00 | 145 | 145
2019-10-31 04:30 | 150 | 150
2019-10-31 05:00 | 160 | 160
2019-10-31 05:30 | 169 | 169
2019-10-31 06:00 | 174 | 173
2019-10-31 06:30 | 184 | 183
2019-10-31 07:00 | 196 | 195
2019-10-31 07:30 | 200 | 200
2019-10-31 08:00 | 193 | 193
2019-10-31 08:30 | 191 | 191
2019-10-31 09:00 | 188 | 188
2019-10-31 09:30 | 186 | 186
2019-10-31 10:00 | 185 | 185
2019-10-31 10:30 | 181 | 180
2019-10-31 11:00 | 177 | 176
2019-10-31 11:30 | 172 | 172
2019-10-31 12:00 | 170 | 169
2019-10-31 12:30 | 169 | 169
2019-10-31 13:00 | 168 | 168
2019-10-31 13:30 | 172 | 172
2019-10-31 14:00 | 175 | 175
2019-10-31 14:30 | 183 | 183
2019-10-31 15:00 | 196 | 195
2019-10-31 15:30 | 210 | 209
2019-10-31 16:00 | 222 | 221
2019-10-31 16:30 | 235 | 235
2019-10-31 17:00 | 250 | 250
2019-10-31 17:30 | 254 | 254
2019-10-31 18:00 | 256 | 256
2019-10-31 18:30 | 260 | 259
2019-10-31 19:00 | 268 | 268
2019-10-31 19:30 | 263 | 262
2019-10-31 20:00 | 258 | 258
2019-10-31 20:30 | 256 | 255
2019-10-31 21:00 | 246 | 245
2019-10-31 21:30 | 235 | 235
2019-10-31 22:00 | 223 | 221
2019-10-31 22:30 | 217 | 215
2019-10-31 23:00 | 211 | 210
2019-10-31 23:30 | 197 | 196
2019-11-01 | 181 | 181
2019-11-01 00:30 | 168 | 168
2019-11-01 01:00 | 161 | 161
2019-11-01 01:30 | 155 | 155
2019-11-01 02:00 | 152 | 152
2019-11-01 02:30 | 150 | 150
2019-11-01 03:00 | 148 | 148
2019-11-01 03:30 | 149 | 149
2019-11-01 04:00 | 149 | 149
2019-11-01 04:30 | 153 | 153
2019-11-01 05:00 | 158 | 158
2019-11-01 05:30 | 165 | 165
2019-11-01 06:00 | 172 | 172
2019-11-01 06:30 | 189 | 188
2019-11-01 07:00 | 205 | 204
2019-11-01 07:30 | 218 | 218
2019-11-01 08:00 | 220 | 220
2019-11-01 08:30 | 209 | 209
2019-11-01 09:00 | 212 | 211
2019-11-01 09:30 | 216 | 215
2019-11-01 10:00 | 212 | 212
2019-11-01 10:30 | 211 | 210
2019-11-01 11:00 | 208 | 208
2019-11-01 11:30 | 198 | 197
2019-11-01 12:00 | 190 | 189
2019-11-01 12:30 | 199 | 199
2019-11-01 13:00 | 207 | 207
2019-11-01 13:30 | 208 | 207
2019-11-01 14:00 | 208 | 207
2019-11-01 14:30 | 214 | 213
2019-11-01 15:00 | 216 | 215
2019-11-01 15:30 | 220 | 219
2019-11-01 16:00 | 227 | 227
2019-11-01 16:30 | 235 | 235
2019-11-01 17:00 | 243 | 243
2019-11-01 17:30 | 244 | 244
2019-11-01 18:00 | 243 | 242
2019-11-01 18:30 | 246 | 246
2019-11-01 19:00 | 256 | 255
2019-11-01 19:30 | 251 | 250
2019-11-01 20:00 | 248 | 248
2019-11-01 20:30 | 242 | 242
2019-11-01 21:00 | 230 | 230
2019-11-01 21:30 | 222 | 221
2019-11-01 22:00 | 214 | 213
2019-11-01 22:30 | 209 | 209
2019-11-01 23:00 | 206 | 206
2019-11-01 23:30 | 194 | 194
2019-11-02 | 179 | 179
2019-11-02 00:30 | 166 | 166
2019-11-02 01:00 | 158 | 158
2019-11-02 01:30 | 153 | 152
2019-11-02 02:00 | 149 | 149
2019-11-02 02:30 | 147 | 146
2019-11-02 03:00 | 144 | 144
2019-11-02 03:30 | 144 | 144
2019-11-02 04:00 | 143 | 143
2019-11-02 04:30 | 144 | 143
2019-11-02 05:00 | 146 | 146
2019-11-02 05:30 | 147 | 147
2019-11-02 06:00 | 146 | 146
2019-11-02 06:30 | 147 | 147
2019-11-02 07:00 | 146 | 146
2019-11-02 07:30 | 148 | 148
2019-11-02 08:00 | 153 | 153
2019-11-02 08:30 | 157 | 157
2019-11-02 09:00 | 164 | 164
2019-11-02 09:30 | 173 | 173
2019-11-02 10:00 | 174 | 174
2019-11-02 10:30 | 167 | 167
2019-11-02 11:00 | 176 | 175
2019-11-02 11:30 | 186 | 185
2019-11-02 12:00 | 173 | 172
2019-11-02 12:30 | 171 | 171
2019-11-02 13:00 | 165 | 165
2019-11-02 13:30 | 172 | 172
2019-11-02 14:00 | 167 | 167
2019-11-02 14:30 | 160 | 160
2019-11-02 15:00 | 163 | 163
2019-11-02 15:30 | 174 | 174
2019-11-02 16:00 | 187 | 187
2019-11-02 16:30 | 195 | 195
2019-11-02 17:00 | 204 | 204
2019-11-02 17:30 | 211 | 211
2019-11-02 18:00 | 217 | 217
2019-11-02 18:30 | 227 | 227
2019-11-02 19:00 | 237 | 237
2019-11-02 19:30 | 232 | 231
2019-11-02 20:00 | 228 | 227
2019-11-02 20:30 | 225 | 224
2019-11-02 21:00 | 215 | 215
2019-11-02 21:30 | 207 | 207
2019-11-02 22:00 | 203 | 203
2019-11-02 22:30 | 201 | 201
2019-11-02 23:00 | 199 | 199
2019-11-02 23:30 | 190 | 189
2019-11-03 | 176 | 175
2019-11-03 00:30 | 164 | 163
2019-11-03 01:00 | 156 | 155
2019-11-03 01:30 | 150 | 149
2019-11-03 02:00 | 146 | 145
2019-11-03 02:30 | 143 | 143
2019-11-03 03:00 | 141 | 141
2019-11-03 03:30 | 140 | 140
2019-11-03 04:00 | 139 | 139
2019-11-03 04:30 | 139 | 139
2019-11-03 05:00 | 139 | 139
2019-11-03 05:30 | 139 | 138
2019-11-03 06:00 | 136 | 135
2019-11-03 06:30 | 134 | 134
2019-11-03 07:00 | 131 | 131
2019-11-03 07:30 | 135 | 135
2019-11-03 08:00 | 138 | 138
2019-11-03 08:30 | 146 | 146
2019-11-03 09:00 | 156 | 156
2019-11-03 09:30 | 163 | 162
2019-11-03 10:00 | 152 | 151
2019-11-03 10:30 | 146 | 146
2019-11-03 11:00 | 133 | 133
2019-11-03 11:30 | 131 | 130
2019-11-03 12:00 | 131 | 130
2019-11-03 12:30 | 124 | 124
2019-11-03 13:00 | 122 | 121
2019-11-03 13:30 | 126 | 125
2019-11-03 14:00 | 130 | 129
2019-11-03 14:30 | 139 | 139
2019-11-03 15:00 | 152 | 152
2019-11-03 15:30 | 164 | 164
2019-11-03 16:00 | 179 | 178
2019-11-03 16:30 | 193 | 193
2019-11-03 17:00 | 212 | 212
2019-11-03 17:30 | 225 | 224
2019-11-03 18:00 | 234 | 233
2019-11-03 18:30 | 244 | 244
2019-11-03 19:00 | 253 | 252
2019-11-03 19:30 | 246 | 246
2019-11-03 20:00 | 241 | 241
2019-11-03 20:30 | 237 | 237
2019-11-03 21:00 | 226 | 226
2019-11-03 21:30 | 217 | 217
2019-11-03 22:00 | 209 | 209
2019-11-03 22:30 | 205 | 204
2019-11-03 23:00 | 201 | 201
2019-11-03 23:30 | 190 | 190
2019-11-04 | 176 | 175
2019-11-04 00:30 | 165 | 163
2019-11-04 01:00 | 158 | 156
2019-11-04 01:30 | 153 | 153
2019-11-04 02:00 | 149 | 149
2019-11-04 02:30 | 147 | 147
2019-11-04 03:00 | 147 | 147
2019-11-04 03:30 | 147 | 147
2019-11-04 04:00 | 148 | 148
2019-11-04 04:30 | 152 | 152
2019-11-04 05:00 | 158 | 158
2019-11-04 05:30 | 166 | 166
2019-11-04 06:00 | 176 | 176
2019-11-04 06:30 | 187 | 187
2019-11-04 07:00 | 194 | 194
2019-11-04 07:30 | 208 | 207
2019-11-04 08:00 | 224 | 223
2019-11-04 08:30 | 238 | 237
2019-11-04 09:00 | 231 | 231
2019-11-04 09:30 | 203 | 203
2019-11-04 10:00 | 185 | 184
2019-11-04 10:30 | 191 | 190
2019-11-04 11:00 | 207 | 207
2019-11-04 11:30 | 208 | 208
2019-11-04 12:00 | 218 | 218
2019-11-04 12:30 | 234 | 234
2019-11-04 13:00 | 246 | 246
2019-11-04 13:30 | 245 | 244
2019-11-04 14:00 | 252 | 251
2019-11-04 14:30 | 242 | 242
2019-11-04 15:00 | 248 | 248
2019-11-04 15:30 | 267 | 266
2019-11-04 16:00 | 288 | 287
2019-11-04 16:30 | 294 | 293
2019-11-04 17:00 | 293 | 292
2019-11-04 17:30 | 296 | 295
2019-11-04 18:00 | 296 | 296
2019-11-04 18:30 | 298 | 298
2019-11-04 19:00 | 305 | 305
2019-11-04 19:30 | 298 | 297
2019-11-04 20:00 | 290 | 289
2019-11-04 20:30 | 283 | 283
2019-11-04 21:00 | 268 | 268
2019-11-04 21:30 | 255 | 255
2019-11-04 22:00 | 243 | 243
2019-11-04 22:30 | 235 | 235
2019-11-04 23:00 | 229 | 229
2019-11-04 23:30 | 215 | 215
2019-11-05 | 196 | 196
2019-11-05 00:30 | 182 | 182
2019-11-05 01:00 | 174 | 174
2019-11-05 01:30 | 169 | 169
2019-11-05 02:00 | 165 | 165
2019-11-05 02:30 | 163 | 163
2019-11-05 03:00 | 162 | 161
2019-11-05 03:30 | 162 | 162
2019-11-05 04:00 | 162 | 162
2019-11-05 04:30 | 165 | 165
2019-11-05 05:00 | 170 | 169
2019-11-05 05:30 | 176 | 176
2019-11-05 06:00 | 181 | 181
2019-11-05 06:30 | 191 | 191
2019-11-05 07:00 | 197 | 197
2019-11-05 07:30 | 201 | 201
2019-11-05 08:00 | 195 | 194
2019-11-05 08:30 | 188 | 188
2019-11-05 09:00 | 181 | 181
2019-11-05 09:30 | 178 | 178
2019-11-05 10:00 | 180 | 180
2019-11-05 10:30 | 188 | 188
2019-11-05 11:00 | 194 | 194
2019-11-05 11:30 | 191 | 191
2019-11-05 12:00 | 185 | 184
2019-11-05 12:30 | 189 | 189
2019-11-05 13:00 | 174 | 174
2019-11-05 13:30 | 173 | 173
2019-11-05 14:00 | 175 | 175
2019-11-05 14:30 | 180 | 180
2019-11-05 15:00 | 190 | 190
2019-11-05 15:30 | 203 | 203
2019-11-05 16:00 | 222 | 221
2019-11-05 16:30 | 239 | 238
2019-11-05 17:00 | 255 | 254
2019-11-05 17:30 | 263 | 262
2019-11-05 18:00 | 264 | 264
2019-11-05 18:30 | 267 | 267
2019-11-05 19:00 | 277 | 276
2019-11-05 19:30 | 270 | 269
2019-11-05 20:00 | 263 | 262
2019-11-05 20:30 | 258 | 257
2019-11-05 21:00 | 247 | 244
2019-11-05 21:30 | 234 | 233
2019-11-05 22:00 | 223 | 223
2019-11-05 22:30 | 215 | 215
2019-11-05 23:00 | 210 | 210
2019-11-05 23:30 | 198 | 198
2019-11-06 | 183 | 183
2019-11-06 00:30 | 170 | 170
2019-11-06 01:00 | 162 | 162
2019-11-06 01:30 | 158 | 157
2019-11-06 02:00 | 154 | 153
2019-11-06 02:30 | 153 | 152
2019-11-06 03:00 | 152 | 151
2019-11-06 03:30 | 153 | 152
2019-11-06 04:00 | 154 | 153
2019-11-06 04:30 | 157 | 156
2019-11-06 05:00 | 162 | 161
2019-11-06 05:30 | 169 | 168
2019-11-06 06:00 | 174 | 173
2019-11-06 06:30 | 182 | 180
2019-11-06 07:00 | 185 | 185
2019-11-06 07:30 | 187 | 186
2019-11-06 08:00 | 180 | 179
2019-11-06 08:30 | 170 | 168
2019-11-06 09:00 | 160 | 158
2019-11-06 09:30 | 154 | 152
2019-11-06 10:00 | 150 | 148
2019-11-06 10:30 | 150 | 147
2019-11-06 11:00 | 151 | 148
2019-11-06 11:30 | 150 | 149
2019-11-06 12:00 | 153 | 153
2019-11-06 12:30 | 156 | 156
2019-11-06 13:00 | 161 | 160
2019-11-06 13:30 | 170 | 168
2019-11-06 14:00 | 178 | 176
2019-11-06 14:30 | 187 | 185
2019-11-06 15:00 | 197 | 194
2019-11-06 15:30 | 208 | 206
2019-11-06 16:00 | 224 | 222
2019-11-06 16:30 | 240 | 237
2019-11-06 17:00 | 256 | 254
2019-11-06 17:30 | 263 | 263
2019-11-06 18:00 | 264 | 264
2019-11-06 18:30 | 268 | 268
2019-11-06 19:00 | 279 | 278
2019-11-06 19:30 | 273 | 272
2019-11-06 20:00 | 267 | 267
2019-11-06 20:30 | 262 | 262
2019-11-06 21:00 | 250 | 250
2019-11-06 21:30 | 238 | 238
2019-11-06 22:00 | 225 | 224
2019-11-06 22:30 | 219 | 218
2019-11-06 23:00 | 213 | 213
2019-11-06 23:30 | 201 | 201
2019-11-07 | 186 | 186
2019-11-07 00:30 | 175 | 174
2019-11-07 01:00 | 167 | 166
2019-11-07 01:30 | 162 | 161
2019-11-07 02:00 | 158 | 157
2019-11-07 02:30 | 157 | 156
2019-11-07 03:00 | 156 | 155
2019-11-07 03:30 | 156 | 155
2019-11-07 04:00 | 156 | 155
2019-11-07 04:30 | 160 | 159
2019-11-07 05:00 | 165 | 164
2019-11-07 05:30 | 172 | 171
2019-11-07 06:00 | 176 | 175
2019-11-07 06:30 | 183 | 182
2019-11-07 07:00 | 187 | 186
2019-11-07 07:30 | 189 | 189
2019-11-07 08:00 | 180 | 179
2019-11-07 08:30 | 171 | 170
2019-11-07 09:00 | 164 | 163
2019-11-07 09:30 | 163 | 161
2019-11-07 10:00 | 162 | 161
2019-11-07 10:30 | 164 | 162
2019-11-07 11:00 | 167 | 165
2019-11-07 11:30 | 171 | 169
2019-11-07 12:00 | 178 | 177
2019-11-07 12:30 | 185 | 184
2019-11-07 13:00 | 194 | 191
2019-11-07 13:30 | 204 | 201
2019-11-07 14:00 | 216 | 213
2019-11-07 14:30 | 229 | 226
2019-11-07 15:00 | 241 | 239
2019-11-07 15:30 | 254 | 254
2019-11-07 16:00 | 276 | 275
2019-11-07 16:30 | 288 | 287
2019-11-07 17:00 | 297 | 296
2019-11-07 17:30 | 298 | 297
2019-11-07 18:00 | 298 | 296
2019-11-07 18:30 | 297 | 296
2019-11-07 19:00 | 304 | 303
2019-11-07 19:30 | 295 | 294
2019-11-07 20:00 | 287 | 287
2019-11-07 20:30 | 280 | 280
2019-11-07 21:00 | 265 | 265
2019-11-07 21:30 | 252 | 252
2019-11-07 22:00 | 240 | 240
2019-11-07 22:30 | 232 | 231
2019-11-07 23:00 | 225 | 224
2019-11-07 23:30 | 206 | 206
2019-11-08 | 189 | 189
2019-11-08 00:30 | 177 | 176
2019-11-08 01:00 | 169 | 169
2019-11-08 01:30 | 163 | 163
2019-11-08 02:00 | 161 | 161
2019-11-08 02:30 | 159 | 159
2019-11-08 03:00 | 158 | 158
2019-11-08 03:30 | 158 | 158
2019-11-08 04:00 | 158 | 157
2019-11-08 04:30 | 160 | 160
2019-11-08 05:00 | 164 | 164
2019-11-08 05:30 | 172 | 171
2019-11-08 06:00 | 175 | 175
2019-11-08 06:30 | 183 | 183
2019-11-08 07:00 | 189 | 189
2019-11-08 07:30 | 193 | 192
2019-11-08 08:00 | 189 | 188
2019-11-08 08:30 | 183 | 183
2019-11-08 09:00 | 181 | 181
2019-11-08 09:30 | 189 | 189
2019-11-08 10:00 | 192 | 191
2019-11-08 10:30 | 198 | 197
2019-11-08 11:00 | 206 | 205
2019-11-08 11:30 | 215 | 213
2019-11-08 12:00 | 226 | 224
2019-11-08 12:30 | 234 | 233
2019-11-08 13:00 | 245 | 244
2019-11-08 13:30 | 255 | 255
2019-11-08 14:00 | 268 | 268
2019-11-08 14:30 | 280 | 280
2019-11-08 15:00 | 292 | 292
2019-11-08 15:30 | 305 | 305
2019-11-08 16:00 | 325 | 324
2019-11-08 16:30 | 342 | 340
2019-11-08 17:00 | 354 | 353
2019-11-08 17:30 | 352 | 350
2019-11-08 18:00 | 340 | 340
2019-11-08 18:30 | 332 | 331
2019-11-08 19:00 | 335 | 334
2019-11-08 19:30 | 325 | 325
2019-11-08 20:00 | 316 | 316
2019-11-08 20:30 | 307 | 307
2019-11-08 21:00 | 293 | 293
2019-11-08 21:30 | 278 | 278
2019-11-08 22:00 | 266 | 265
2019-11-08 22:30 | 255 | 254
2019-11-08 23:00 | 244 | 244
2019-11-08 23:30 | 229 | 228
2019-11-09 | 212 | 211
2019-11-09 00:30 | 197 | 195
2019-11-09 01:00 | 185 | 185
2019-11-09 01:30 | 179 | 179
2019-11-09 02:00 | 173 | 173
2019-11-09 02:30 | 168 | 168
2019-11-09 03:00 | 168 | 168
2019-11-09 03:30 | 167 | 166
2019-11-09 04:00 | 166 | 165
2019-11-09 04:30 | 165 | 164
2019-11-09 05:00 | 164 | 163
2019-11-09 05:30 | 163 | 163
2019-11-09 06:00 | 161 | 161
2019-11-09 06:30 | 162 | 162
2019-11-09 07:00 | 162 | 162
2019-11-09 07:30 | 161 | 161
2019-11-09 08:00 | 158 | 158
2019-11-09 08:30 | 160 | 160
2019-11-09 09:00 | 161 | 160
2019-11-09 09:30 | 159 | 159
2019-11-09 10:00 | 156 | 156
2019-11-09 10:30 | 155 | 155
2019-11-09 11:00 | 154 | 154
2019-11-09 11:30 | 150 | 150
2019-11-09 12:00 | 150 | 150
2019-11-09 12:30 | 154 | 153
2019-11-09 13:00 | 162 | 162
2019-11-09 13:30 | 168 | 168
2019-11-09 14:00 | 178 | 178
2019-11-09 14:30 | 189 | 188
2019-11-09 15:00 | 200 | 200
2019-11-09 15:30 | 214 | 213
2019-11-09 16:00 | 224 | 223
2019-11-09 16:30 | 232 | 232
2019-11-09 17:00 | 243 | 243
2019-11-09 17:30 | 245 | 244
2019-11-09 18:00 | 244 | 244
2019-11-09 18:30 | 248 | 248
2019-11-09 19:00 | 257 | 257
2019-11-09 19:30 | 251 | 251
2019-11-09 20:00 | 244 | 244
2019-11-09 20:30 | 241 | 241
2019-11-09 21:00 | 231 | 230
2019-11-09 21:30 | 222 | 221
2019-11-09 22:00 | 216 | 216
2019-11-09 22:30 | 213 | 212
2019-11-09 23:00 | 209 | 209
2019-11-09 23:30 | 200 | 200
2019-11-10 | 187 | 187
2019-11-10 00:30 | 174 | 174
2019-11-10 01:00 | 167 | 166
2019-11-10 01:30 | 161 | 161
2019-11-10 02:00 | 157 | 156
2019-11-10 02:30 | 153 | 152
2019-11-10 03:00 | 150 | 149
2019-11-10 03:30 | 150 | 149
2019-11-10 04:00 | 149 | 148
2019-11-10 04:30 | 149 | 148
2019-11-10 05:00 | 147 | 147
2019-11-10 05:30 | 146 | 146
2019-11-10 06:00 | 141 | 141
2019-11-10 06:30 | 137 | 136
2019-11-10 07:00 | 130 | 130
2019-11-10 07:30 | 126 | 125
2019-11-10 08:00 | 121 | 121
2019-11-10 08:30 | 119 | 119
2019-11-10 09:00 | 115 | 115
2019-11-10 09:30 | 112 | 112
2019-11-10 10:00 | 109 | 109
2019-11-10 10:30 | 108 | 108
2019-11-10 11:00 | 107 | 107
2019-11-10 11:30 | 108 | 108
2019-11-10 12:00 | 112 | 111
2019-11-10 12:30 | 119 | 119
2019-11-10 13:00 | 127 | 127
2019-11-10 13:30 | 138 | 138
2019-11-10 14:00 | 151 | 151
2019-11-10 14:30 | 165 | 165
2019-11-10 15:00 | 180 | 180
2019-11-10 15:30 | 196 | 196
2019-11-10 16:00 | 212 | 212
2019-11-10 16:30 | 228 | 228
2019-11-10 17:00 | 242 | 241
2019-11-10 17:30 | 251 | 251
2019-11-10 18:00 | 255 | 255
2019-11-10 18:30 | 259 | 259
2019-11-10 19:00 | 267 | 267
2019-11-10 19:30 | 260 | 260
2019-11-10 20:00 | 253 | 253
2019-11-10 20:30 | 246 | 245
2019-11-10 21:00 | 234 | 233
2019-11-10 21:30 | 225 | 225
2019-11-10 22:00 | 215 | 215
2019-11-10 22:30 | 209 | 209
2019-11-10 23:00 | 204 | 204
2019-11-10 23:30 | 190 | 190
2019-11-11 | 179 | 179
2019-11-11 00:30 | 165 | 165
2019-11-11 01:00 | 159 | 159
2019-11-11 01:30 | 155 | 155
2019-11-11 02:00 | 152 | 152
2019-11-11 02:30 | 149 | 149
2019-11-11 03:00 | 150 | 149
2019-11-11 03:30 | 150 | 150
2019-11-11 04:00 | 150 | 150
2019-11-11 04:30 | 152 | 152
2019-11-11 05:00 | 156 | 156
2019-11-11 05:30 | 167 | 167
2019-11-11 06:00 | 173 | 173
2019-11-11 06:30 | 186 | 186
2019-11-11 07:00 | 195 | 195
2019-11-11 07:30 | 204 | 204
2019-11-11 08:00 | 203 | 202
2019-11-11 08:30 | 200 | 200
2019-11-11 09:00 | 203 | 203
2019-11-11 09:30 | 206 | 206
2019-11-11 10:00 | 203 | 203
2019-11-11 10:30 | 198 | 198
2019-11-11 11:00 | 193 | 193
2019-11-11 11:30 | 192 | 192
2019-11-11 12:00 | 193 | 193
2019-11-11 12:30 | 193 | 193
2019-11-11 13:00 | 200 | 200
2019-11-11 13:30 | 206 | 206
2019-11-11 14:00 | 214 | 213
2019-11-11 14:30 | 220 | 220
2019-11-11 15:00 | 228 | 228
2019-11-11 15:30 | 237 | 237
2019-11-11 16:00 | 249 | 249
2019-11-11 16:30 | 260 | 260
2019-11-11 17:00 | 271 | 271
2019-11-11 17:30 | 272 | 272
2019-11-11 18:00 | 273 | 273
2019-11-11 18:30 | 275 | 275
2019-11-11 19:00 | 283 | 283
2019-11-11 19:30 | 277 | 277
2019-11-11 20:00 | 271 | 271
2019-11-11 20:30 | 265 | 265
2019-11-11 21:00 | 253 | 253
2019-11-11 21:30 | 241 | 241
2019-11-11 22:00 | 228 | 228
2019-11-11 22:30 | 220 | 220
2019-11-11 23:00 | 216 | 216
2019-11-11 23:30 | 202 | 202
2019-11-12 | 186 | 186
2019-11-12 00:30 | 173 | 173
2019-11-12 01:00 | 166 | 166
2019-11-12 01:30 | 161 | 161
2019-11-12 02:00 | 158 | 158
2019-11-12 02:30 | 156 | 156
2019-11-12 03:00 | 155 | 155
2019-11-12 03:30 | 155 | 155
2019-11-12 04:00 | 155 | 155
2019-11-12 04:30 | 159 | 159
2019-11-12 05:00 | 163 | 163
2019-11-12 05:30 | 171 | 171
2019-11-12 06:00 | 177 | 176
2019-11-12 06:30 | 190 | 189
2019-11-12 07:00 | 198 | 197
2019-11-12 07:30 | 203 | 203
2019-11-12 08:00 | 201 | 200
2019-11-12 08:30 | 193 | 193
2019-11-12 09:00 | 189 | 189
2019-11-12 09:30 | 187 | 187
2019-11-12 10:00 | 185 | 185
2019-11-12 10:30 | 188 | 188
2019-11-12 11:00 | 190 | 190
2019-11-12 11:30 | 195 | 194
2019-11-12 12:00 | 202 | 201
2019-11-12 12:30 | 208 | 208
2019-11-12 13:00 | 216 | 215
2019-11-12 13:30 | 223 | 222
2019-11-12 14:00 | 233 | 232
2019-11-12 14:30 | 246 | 244
2019-11-12 15:00 | 257 | 255
2019-11-12 15:30 | 270 | 268
2019-11-12 16:00 | 286 | 285
2019-11-12 16:30 | 302 | 302
2019-11-12 17:00 | 314 | 314
2019-11-12 17:30 | 316 | 315
2019-11-12 18:00 | 311 | 310
2019-11-12 18:30 | 305 | 303
2019-11-12 19:00 | 313 | 312
2019-11-12 19:30 | 305 | 304
2019-11-12 20:00 | 296 | 296
2019-11-12 20:30 | 290 | 289
2019-11-12 21:00 | 274 | 274
2019-11-12 21:30 | 261 | 261
2019-11-12 22:00 | 247 | 247
2019-11-12 22:30 | 238 | 238
2019-11-12 23:00 | 230 | 229
2019-11-12 23:30 | 212 | 212
2019-11-13 | 194 | 194
2019-11-13 00:30 | 181 | 181
2019-11-13 01:00 | 174 | 173
2019-11-13 01:30 | 168 | 168
2019-11-13 02:00 | 165 | 164
2019-11-13 02:30 | 162 | 161
2019-11-13 03:00 | 160 | 159
2019-11-13 03:30 | 160 | 159
2019-11-13 04:00 | 161 | 160
2019-11-13 04:30 | 163 | 163
2019-11-13 05:00 | 166 | 165
2019-11-13 05:30 | 172 | 172
2019-11-13 06:00 | 178 | 178
2019-11-13 06:30 | 192 | 192
2019-11-13 07:00 | 202 | 202
2019-11-13 07:30 | 209 | 209
2019-11-13 08:00 | 209 | 209
2019-11-13 08:30 | 205 | 205
2019-11-13 09:00 | 203 | 203
2019-11-13 09:30 | 203 | 203
2019-11-13 10:00 | 208 | 207
2019-11-13 10:30 | 208 | 208
2019-11-13 11:00 | 208 | 208
2019-11-13 11:30 | 208 | 208
2019-11-13 12:00 | 209 | 209
2019-11-13 12:30 | 212 | 212
2019-11-13 13:00 | 216 | 215
2019-11-13 13:30 | 222 | 222
2019-11-13 14:00 | 230 | 230
2019-11-13 14:30 | 237 | 237
2019-11-13 15:00 | 241 | 241
2019-11-13 15:30 | 248 | 248
2019-11-13 16:00 | 258 | 258
2019-11-13 16:30 | 267 | 266
2019-11-13 17:00 | 278 | 276
2019-11-13 17:30 | 278 | 277
2019-11-13 18:00 | 277 | 276
2019-11-13 18:30 | 276 | 275
2019-11-13 19:00 | 285 | 284
2019-11-13 19:30 | 277 | 276
2019-11-13 20:00 | 272 | 271
2019-11-13 20:30 | 266 | 265
2019-11-13 21:00 | 256 | 255
2019-11-13 21:30 | 242 | 242
2019-11-13 22:00 | 231 | 231
2019-11-13 22:30 | 224 | 224
2019-11-13 23:00 | 219 | 218
2019-11-13 23:30 | 203 | 203
2019-11-14 | 188 | 188
2019-11-14 00:30 | 174 | 174
2019-11-14 01:00 | 167 | 167
2019-11-14 01:30 | 163 | 163
2019-11-14 02:00 | 161 | 160
2019-11-14 02:30 | 159 | 158
2019-11-14 03:00 | 157 | 157
2019-11-14 03:30 | 158 | 157
2019-11-14 04:00 | 157 | 157
2019-11-14 04:30 | 161 | 160
2019-11-14 05:00 | 164 | 164
2019-11-14 05:30 | 172 | 172
2019-11-14 06:00 | 176 | 176
2019-11-14 06:30 | 188 | 188
2019-11-14 07:00 | 196 | 196
2019-11-14 07:30 | 201 | 201
2019-11-14 08:00 | 196 | 196
2019-11-14 08:30 | 196 | 195
2019-11-14 09:00 | 187 | 187
2019-11-14 09:30 | 182 | 181
2019-11-14 10:00 | 177 | 177
2019-11-14 10:30 | 179 | 178
2019-11-14 11:00 | 179 | 178
2019-11-14 11:30 | 180 | 179
2019-11-14 12:00 | 184 | 183
2019-11-14 12:30 | 190 | 189
2019-11-14 13:00 | 196 | 195
2019-11-14 13:30 | 204 | 202
2019-11-14 14:00 | 213 | 211
2019-11-14 14:30 | 225 | 223
2019-11-14 15:00 | 233 | 232
2019-11-14 15:30 | 244 | 243
2019-11-14 16:00 | 259 | 258
2019-11-14 16:30 | 272 | 271
2019-11-14 17:00 | 282 | 281
2019-11-14 17:30 | 285 | 284
2019-11-14 18:00 | 285 | 285
2019-11-14 18:30 | 285 | 284
2019-11-14 19:00 | 295 | 294
2019-11-14 19:30 | 289 | 288
2019-11-14 20:00 | 283 | 282
2019-11-14 20:30 | 275 | 274
2019-11-14 21:00 | 263 | 262
2019-11-14 21:30 | 251 | 250
2019-11-14 22:00 | 241 | 240
2019-11-14 22:30 | 234 | 234
2019-11-14 23:00 | 229 | 229
2019-11-14 23:30 | 214 | 214
2019-11-15 | 199 | 199
2019-11-15 00:30 | 184 | 184
2019-11-15 01:00 | 176 | 176
2019-11-15 01:30 | 171 | 171
2019-11-15 02:00 | 168 | 168
2019-11-15 02:30 | 167 | 167
2019-11-15 03:00 | 165 | 165
2019-11-15 03:30 | 166 | 165
2019-11-15 04:00 | 166 | 166
2019-11-15 04:30 | 168 | 168
2019-11-15 05:00 | 171 | 171
2019-11-15 05:30 | 178 | 178
2019-11-15 06:00 | 184 | 184
2019-11-15 06:30 | 198 | 198
2019-11-15 07:00 | 208 | 207
2019-11-15 07:30 | 217 | 216
2019-11-15 08:00 | 219 | 219
2019-11-15 08:30 | 219 | 218
2019-11-15 09:00 | 215 | 215
2019-11-15 09:30 | 211 | 211
2019-11-15 10:00 | 209 | 209
2019-11-15 10:30 | 214 | 214
2019-11-15 11:00 | 219 | 219
2019-11-15 11:30 | 222 | 221
2019-11-15 12:00 | 228 | 227
2019-11-15 12:30 | 235 | 235
2019-11-15 13:00 | 246 | 245
2019-11-15 13:30 | 258 | 257
2019-11-15 14:00 | 271 | 270
2019-11-15 14:30 | 281 | 281
2019-11-15 15:00 | 290 | 290
2019-11-15 15:30 | 301 | 301
2019-11-15 16:00 | 316 | 316
2019-11-15 16:30 | 327 | 326
2019-11-15 17:00 | 334 | 333
2019-11-15 17:30 | 330 | 330
2019-11-15 18:00 | 320 | 320
2019-11-15 18:30 | 312 | 312
2019-11-15 19:00 | 317 | 317
2019-11-15 19:30 | 310 | 310
2019-11-15 20:00 | 303 | 303
2019-11-15 20:30 | 296 | 295
2019-11-15 21:00 | 279 | 278
2019-11-15 21:30 | 267 | 267
2019-11-15 22:00 | 254 | 253
2019-11-15 22:30 | 246 | 246
2019-11-15 23:00 | 239 | 239
2019-11-15 23:30 | 223 | 222
2019-11-16 | 205 | 205
2019-11-16 00:30 | 191 | 191
2019-11-16 01:00 | 184 | 184
2019-11-16 01:30 | 178 | 177
2019-11-16 02:00 | 173 | 172
2019-11-16 02:30 | 170 | 169
2019-11-16 03:00 | 167 | 166
2019-11-16 03:30 | 167 | 166
2019-11-16 04:00 | 166 | 164
2019-11-16 04:30 | 166 | 165
2019-11-16 05:00 | 162 | 161
2019-11-16 05:30 | 161 | 161
2019-11-16 06:00 | 160 | 159
2019-11-16 06:30 | 161 | 161
2019-11-16 07:00 | 161 | 161
2019-11-16 07:30 | 163 | 163
2019-11-16 08:00 | 164 | 164
2019-11-16 08:30 | 170 | 169
2019-11-16 09:00 | 175 | 174
2019-11-16 09:30 | 179 | 178
2019-11-16 10:00 | 184 | 183
2019-11-16 10:30 | 191 | 191
2019-11-16 11:00 | 200 | 200
2019-11-16 11:30 | 210 | 209
2019-11-16 12:00 | 220 | 218
2019-11-16 12:30 | 230 | 229
2019-11-16 13:00 | 245 | 245
2019-11-16 13:30 | 264 | 263
2019-11-16 14:00 | 281 | 281
2019-11-16 14:30 | 288 | 288
2019-11-16 15:00 | 298 | 298
2019-11-16 15:30 | 307 | 307
2019-11-16 16:00 | 317 | 317
2019-11-16 16:30 | 322 | 322
2019-11-16 17:00 | 330 | 330
2019-11-16 17:30 | 328 | 328
2019-11-16 18:00 | 321 | 321
2019-11-16 18:30 | 317 | 317
2019-11-16 19:00 | 319 | 319
2019-11-16 19:30 | 310 | 310
2019-11-16 20:00 | 298 | 297
2019-11-16 20:30 | 286 | 286
2019-11-16 21:00 | 272 | 272
2019-11-16 21:30 | 259 | 258
2019-11-16 22:00 | 246 | 246
2019-11-16 22:30 | 240 | 240
2019-11-16 23:00 | 231 | 231
2019-11-16 23:30 | 215 | 215
2019-11-17 | 198 | 198
2019-11-17 00:30 | 185 | 185
2019-11-17 01:00 | 174 | 174
2019-11-17 01:30 | 168 | 168
2019-11-17 02:00 | 162 | 162
2019-11-17 02:30 | 159 | 158
2019-11-17 03:00 | 156 | 156
2019-11-17 03:30 | 154 | 154
2019-11-17 04:00 | 153 | 152
2019-11-17 04:30 | 153 | 152
2019-11-17 05:00 | 151 | 150
2019-11-17 05:30 | 149 | 148
2019-11-17 06:00 | 145 | 144
2019-11-17 06:30 | 144 | 143
2019-11-17 07:00 | 143 | 143
2019-11-17 07:30 | 145 | 145
2019-11-17 08:00 | 142 | 142
2019-11-17 08:30 | 139 | 139
2019-11-17 09:00 | 145 | 145
2019-11-17 09:30 | 148 | 147
2019-11-17 10:00 | 153 | 153
2019-11-17 10:30 | 160 | 160
2019-11-17 11:00 | 169 | 168
2019-11-17 11:30 | 178 | 178
2019-11-17 12:00 | 190 | 189
2019-11-17 12:30 | 233 | 232
2019-11-17 13:00 | 224 | 224
2019-11-17 13:30 | 247 | 246
2019-11-17 14:00 | 229 | 227
2019-11-17 14:30 | 246 | 243
2019-11-17 15:00 | 227 | 226
2019-11-17 15:30 | 235 | 234
2019-11-17 16:00 | 248 | 247
2019-11-17 16:30 | 265 | 265
2019-11-17 17:00 | 277 | 277
2019-11-17 17:30 | 284 | 284
2019-11-17 18:00 | 287 | 286
2019-11-17 18:30 | 290 | 289
2019-11-17 19:00 | 298 | 298
2019-11-17 19:30 | 292 | 291
2019-11-17 20:00 | 283 | 282
2019-11-17 20:30 | 274 | 272
2019-11-17 21:00 | 259 | 258
2019-11-17 21:30 | 247 | 246
2019-11-17 22:00 | 232 | 231
2019-11-17 22:30 | 223 | 222
2019-11-17 23:00 | 216 | 216
2019-11-17 23:30 | 202 | 202
2019-11-18 | 186 | 186
2019-11-18 00:30 | 174 | 174
2019-11-18 01:00 | 166 | 166
2019-11-18 01:30 | 162 | 161
2019-11-18 02:00 | 158 | 158
2019-11-18 02:30 | 157 | 157
2019-11-18 03:00 | 155 | 155
2019-11-18 03:30 | 155 | 155
2019-11-18 04:00 | 155 | 155
2019-11-18 04:30 | 159 | 159
2019-11-18 05:00 | 162 | 162
2019-11-18 05:30 | 169 | 169
2019-11-18 06:00 | 175 | 174
2019-11-18 06:30 | 187 | 187
2019-11-18 07:00 | 198 | 197
2019-11-18 07:30 | 206 | 205
2019-11-18 08:00 | 207 | 206
2019-11-18 08:30 | 205 | 203
2019-11-18 09:00 | 196 | 196
2019-11-18 09:30 | 190 | 190
2019-11-18 10:00 | 183 | 183
2019-11-18 10:30 | 177 | 177
2019-11-18 11:00 | 180 | 180
2019-11-18 11:30 | 179 | 179
2019-11-18 12:00 | 178 | 178
2019-11-18 12:30 | 179 | 179
2019-11-18 13:00 | 181 | 181
2019-11-18 13:30 | 186 | 186
2019-11-18 14:00 | 196 | 195
2019-11-18 14:30 | 205 | 205
2019-11-18 15:00 | 214 | 214
2019-11-18 15:30 | 227 | 227
2019-11-18 16:00 | 244 | 243
2019-11-18 16:30 | 259 | 258
2019-11-18 17:00 | 273 | 273
2019-11-18 17:30 | 278 | 278
2019-11-18 18:00 | 278 | 278
2019-11-18 18:30 | 279 | 279
2019-11-18 19:00 | 286 | 286
2019-11-18 19:30 | 278 | 278
2019-11-18 20:00 | 270 | 270
2019-11-18 20:30 | 263 | 263
2019-11-18 21:00 | 247 | 247
2019-11-18 21:30 | 233 | 232
2019-11-18 22:00 | 221 | 220
2019-11-18 22:30 | 215 | 215
2019-11-18 23:00 | 209 | 209
2019-11-18 23:30 | 194 | 194
2019-11-19 | 179 | 179
2019-11-19 00:30 | 167 | 167
2019-11-19 01:00 | 160 | 160
2019-11-19 01:30 | 156 | 156
2019-11-19 02:00 | 154 | 153
2019-11-19 02:30 | 152 | 151
2019-11-19 03:00 | 152 | 151
2019-11-19 03:30 | 152 | 151
2019-11-19 04:00 | 152 | 152
2019-11-19 04:30 | 155 | 155
2019-11-19 05:00 | 159 | 159
2019-11-19 05:30 | 168 | 168
2019-11-19 06:00 | 175 | 175
2019-11-19 06:30 | 188 | 187
2019-11-19 07:00 | 196 | 196
2019-11-19 07:30 | 200 | 200
2019-11-19 08:00 | 195 | 195
2019-11-19 08:30 | 190 | 190
2019-11-19 09:00 | 181 | 181
2019-11-19 09:30 | 177 | 177
2019-11-19 10:00 | 174 | 174
2019-11-19 10:30 | 173 | 173
2019-11-19 11:00 | 177 | 177
2019-11-19 11:30 | 182 | 182
2019-11-19 12:00 | 190 | 189
2019-11-19 12:30 | 199 | 198
2019-11-19 13:00 | 209 | 209
2019-11-19 13:30 | 222 | 221
2019-11-19 14:00 | 237 | 236
2019-11-19 14:30 | 251 | 250
2019-11-19 15:00 | 264 | 264
2019-11-19 15:30 | 277 | 277
2019-11-19 16:00 | 294 | 294
2019-11-19 16:30 | 309 | 309
2019-11-19 17:00 | 323 | 323
2019-11-19 17:30 | 321 | 321
2019-11-19 18:00 | 318 | 318
2019-11-19 18:30 | 314 | 313
2019-11-19 19:00 | 321 | 321
2019-11-19 19:30 | 312 | 312
2019-11-19 20:00 | 305 | 304
2019-11-19 20:30 | 297 | 297
2019-11-19 21:00 | 281 | 281
2019-11-19 21:30 | 266 | 266
2019-11-19 22:00 | 253 | 253
2019-11-19 22:30 | 242 | 242
2019-11-19 23:00 | 234 | 234
2019-11-19 23:30 | 219 | 219
2019-11-20 | 203 | 203
2019-11-20 00:30 | 190 | 190
2019-11-20 01:00 | 183 | 183
2019-11-20 01:30 | 179 | 179
2019-11-20 02:00 | 175 | 175
2019-11-20 02:30 | 172 | 172
2019-11-20 03:00 | 170 | 170
2019-11-20 03:30 | 171 | 171
2019-11-20 04:00 | 171 | 171
2019-11-20 04:30 | 174 | 174
2019-11-20 05:00 | 176 | 176
2019-11-20 05:30 | 184 | 184
2019-11-20 06:00 | 190 | 190
2019-11-20 06:30 | 203 | 203
2019-11-20 07:00 | 212 | 212
2019-11-20 07:30 | 220 | 218
2019-11-20 08:00 | 218 | 216
2019-11-20 08:30 | 217 | 214
2019-11-20 09:00 | 218 | 218
2019-11-20 09:30 | 221 | 221
2019-11-20 10:00 | 223 | 223
2019-11-20 10:30 | 228 | 228
2019-11-20 11:00 | 235 | 235
2019-11-20 11:30 | 243 | 243
2019-11-20 12:00 | 253 | 253
2019-11-20 12:30 | 263 | 262
2019-11-20 13:00 | 275 | 275
2019-11-20 13:30 | 287 | 287
2019-11-20 14:00 | 299 | 299
2019-11-20 14:30 | 313 | 313
2019-11-20 15:00 | 322 | 322
2019-11-20 15:30 | 333 | 333
2019-11-20 16:00 | 347 | 347
2019-11-20 16:30 | 358 | 358
2019-11-20 17:00 | 362 | 361
2019-11-20 17:30 | 357 | 357
2019-11-20 18:00 | 348 | 348
2019-11-20 18:30 | 341 | 341
2019-11-20 19:00 | 344 | 344
2019-11-20 19:30 | 336 | 336
2019-11-20 20:00 | 328 | 328
2019-11-20 20:30 | 319 | 319
2019-11-20 21:00 | 301 | 301
2019-11-20 21:30 | 285 | 285
2019-11-20 22:00 | 267 | 267
2019-11-20 22:30 | 258 | 258
2019-11-20 23:00 | 249 | 248
2019-11-20 23:30 | 228 | 228
2019-11-21 | 209 | 208
2019-11-21 00:30 | 196 | 196
2019-11-21 01:00 | 190 | 189
2019-11-21 01:30 | 184 | 184
2019-11-21 02:00 | 180 | 180
2019-11-21 02:30 | 178 | 177
2019-11-21 03:00 | 176 | 176
2019-11-21 03:30 | 175 | 175
2019-11-21 04:00 | 174 | 174
2019-11-21 04:30 | 176 | 176
2019-11-21 05:00 | 178 | 178
2019-11-21 05:30 | 186 | 186
2019-11-21 06:00 | 193 | 193
2019-11-21 06:30 | 208 | 208
2019-11-21 07:00 | 220 | 219
2019-11-21 07:30 | 225 | 224
2019-11-21 08:00 | 222 | 221
2019-11-21 08:30 | 221 | 221
2019-11-21 09:00 | 219 | 219
2019-11-21 09:30 | 218 | 218
2019-11-21 10:00 | 213 | 213
2019-11-21 10:30 | 210 | 210
2019-11-21 11:00 | 210 | 210
2019-11-21 11:30 | 209 | 209
2019-11-21 12:00 | 210 | 210
2019-11-21 12:30 | 214 | 214
2019-11-21 13:00 | 219 | 219
2019-11-21 13:30 | 226 | 226
2019-11-21 14:00 | 236 | 236
2019-11-21 14:30 | 248 | 247
2019-11-21 15:00 | 258 | 257
2019-11-21 15:30 | 268 | 267
2019-11-21 16:00 | 279 | 279
2019-11-21 16:30 | 290 | 289
2019-11-21 17:00 | 299 | 299
2019-11-21 17:30 | 300 | 300
2019-11-21 18:00 | 299 | 299
2019-11-21 18:30 | 297 | 297
2019-11-21 19:00 | 304 | 304
2019-11-21 19:30 | 298 | 298
2019-11-21 20:00 | 292 | 292
2019-11-21 20:30 | 284 | 284
2019-11-21 21:00 | 271 | 271
2019-11-21 21:30 | 257 | 257
2019-11-21 22:00 | 241 | 241
2019-11-21 22:30 | 232 | 232
2019-11-21 23:00 | 224 | 224
2019-11-21 23:30 | 209 | 209
2019-11-22 | 191 | 191
2019-11-22 00:30 | 180 | 180
2019-11-22 01:00 | 172 | 172
2019-11-22 01:30 | 168 | 168
2019-11-22 02:00 | 164 | 164
2019-11-22 02:30 | 161 | 160
2019-11-22 03:00 | 159 | 158
2019-11-22 03:30 | 159 | 158
2019-11-22 04:00 | 159 | 158
2019-11-22 04:30 | 164 | 163
2019-11-22 05:00 | 167 | 166
2019-11-22 05:30 | 174 | 174
2019-11-22 06:00 | 178 | 178
2019-11-22 06:30 | 188 | 188
2019-11-22 07:00 | 197 | 197
2019-11-22 07:30 | 205 | 205
2019-11-22 08:00 | 205 | 204
2019-11-22 08:30 | 202 | 201
2019-11-22 09:00 | 196 | 195
2019-11-22 09:30 | 193 | 192
2019-11-22 10:00 | 193 | 192
2019-11-22 10:30 | 193 | 191
2019-11-22 11:00 | 192 | 190
2019-11-22 11:30 | 195 | 195
2019-11-22 12:00 | 198 | 198
2019-11-22 12:30 | 200 | 200
2019-11-22 13:00 | 206 | 206
2019-11-22 13:30 | 211 | 211
2019-11-22 14:00 | 220 | 220
2019-11-22 14:30 | 229 | 229
2019-11-22 15:00 | 242 | 241
2019-11-22 15:30 | 253 | 253
2019-11-22 16:00 | 272 | 272
2019-11-22 16:30 | 289 | 289
2019-11-22 17:00 | 298 | 298
2019-11-22 17:30 | 298 | 298
2019-11-22 18:00 | 292 | 291
2019-11-22 18:30 | 285 | 284
2019-11-22 19:00 | 290 | 290
2019-11-22 19:30 | 284 | 283
2019-11-22 20:00 | 279 | 279
2019-11-22 20:30 | 271 | 271
2019-11-22 21:00 | 259 | 259
2019-11-22 21:30 | 248 | 248
2019-11-22 22:00 | 237 | 237
2019-11-22 22:30 | 230 | 229
2019-11-22 23:00 | 225 | 224
2019-11-22 23:30 | 209 | 209
2019-11-23 | 193 | 193
2019-11-23 00:30 | 181 | 181
2019-11-23 01:00 | 175 | 174
2019-11-23 01:30 | 169 | 168
2019-11-23 02:00 | 165 | 164
2019-11-23 02:30 | 161 | 159
2019-11-23 03:00 | 159 | 158
2019-11-23 03:30 | 159 | 157
2019-11-23 04:00 | 157 | 155
2019-11-23 04:30 | 157 | 155
2019-11-23 05:00 | 156 | 154
2019-11-23 05:30 | 157 | 154
2019-11-23 06:00 | 155 | 152
2019-11-23 06:30 | 155 | 153
2019-11-23 07:00 | 155 | 154
2019-11-23 07:30 | 159 | 159
2019-11-23 08:00 | 167 | 166
2019-11-23 08:30 | 167 | 167
2019-11-23 09:00 | 164 | 163
2019-11-23 09:30 | 154 | 153
2019-11-23 10:00 | 146 | 146
2019-11-23 10:30 | 139 | 139
2019-11-23 11:00 | 139 | 139
2019-11-23 11:30 | 139 | 139
2019-11-23 12:00 | 142 | 142
2019-11-23 12:30 | 146 | 146
2019-11-23 13:00 | 152 | 151
2019-11-23 13:30 | 158 | 158
2019-11-23 14:00 | 168 | 167
2019-11-23 14:30 | 178 | 178
2019-11-23 15:00 | 191 | 191
2019-11-23 15:30 | 205 | 205
2019-11-23 16:00 | 219 | 219
2019-11-23 16:30 | 234 | 234
2019-11-23 17:00 | 247 | 247
2019-11-23 17:30 | 250 | 250
2019-11-23 18:00 | 251 | 251
2019-11-23 18:30 | 252 | 252
2019-11-23 19:00 | 258 | 257
2019-11-23 19:30 | 254 | 254
2019-11-23 20:00 | 250 | 250
2019-11-23 20:30 | 243 | 243
2019-11-23 21:00 | 233 | 233
2019-11-23 21:30 | 225 | 225
2019-11-23 22:00 | 216 | 216
2019-11-23 22:30 | 216 | 216
2019-11-23 23:00 | 212 | 211
2019-11-23 23:30 | 199 | 198
2019-11-24 | 184 | 182
2019-11-24 00:30 | 173 | 170
2019-11-24 01:00 | 166 | 163
2019-11-24 01:30 | 161 | 157
2019-11-24 02:00 | 157 | 153
2019-11-24 02:30 | 156 | 151
2019-11-24 03:00 | 154 | 148
2019-11-24 03:30 | 152 | 147
2019-11-24 04:00 | 151 | 145
2019-11-24 04:30 | 151 | 145
2019-11-24 05:00 | 148 | 143
2019-11-24 05:30 | 147 | 143
2019-11-24 06:00 | 144 | 139
2019-11-24 06:30 | 141 | 137
2019-11-24 07:00 | 136 | 133
2019-11-24 07:30 | 134 | 131
2019-11-24 08:00 | 134 | 132
2019-11-24 08:30 | 143 | 142
2019-11-24 09:00 | 146 | 145
2019-11-24 09:30 | 146 | 146
2019-11-24 10:00 | 147 | 147
2019-11-24 10:30 | 147 | 147
2019-11-24 11:00 | 147 | 147
2019-11-24 11:30 | 144 | 144
2019-11-24 12:00 | 146 | 146
2019-11-24 12:30 | 147 | 147
2019-11-24 13:00 | 152 | 152
2019-11-24 13:30 | 161 | 161
2019-11-24 14:00 | 176 | 176
2019-11-24 14:30 | 198 | 198
2019-11-24 15:00 | 214 | 214
2019-11-24 15:30 | 221 | 221
2019-11-24 16:00 | 230 | 230
2019-11-24 16:30 | 224 | 224
2019-11-24 17:00 | 234 | 234
2019-11-24 17:30 | 244 | 244
2019-11-24 18:00 | 249 | 249
2019-11-24 18:30 | 254 | 254
2019-11-24 19:00 | 264 | 264
2019-11-24 19:30 | 260 | 259
2019-11-24 20:00 | 253 | 253
2019-11-24 20:30 | 247 | 247
2019-11-24 21:00 | 235 | 235
2019-11-24 21:30 | 225 | 225
2019-11-24 22:00 | 215 | 215
2019-11-24 22:30 | 209 | 209
2019-11-24 23:00 | 204 | 204
2019-11-24 23:30 | 191 | 191
2019-11-25 | 177 | 176
2019-11-25 00:30 | 166 | 165
2019-11-25 01:00 | 160 | 158
2019-11-25 01:30 | 156 | 154
2019-11-25 02:00 | 153 | 151
2019-11-25 02:30 | 150 | 149
2019-11-25 03:00 | 149 | 148
2019-11-25 03:30 | 150 | 149
2019-11-25 04:00 | 149 | 149
2019-11-25 04:30 | 154 | 153
2019-11-25 05:00 | 156 | 156
2019-11-25 05:30 | 166 | 166
2019-11-25 06:00 | 177 | 177
2019-11-25 06:30 | 189 | 189
2019-11-25 07:00 | 201 | 201
2019-11-25 07:30 | 212 | 212
2019-11-25 08:00 | 216 | 216
2019-11-25 08:30 | 215 | 215
2019-11-25 09:00 | 215 | 215
2019-11-25 09:30 | 216 | 216
2019-11-25 10:00 | 210 | 210
2019-11-25 10:30 | 207 | 207
2019-11-25 11:00 | 196 | 196
2019-11-25 11:30 | 191 | 191
2019-11-25 12:00 | 193 | 192
2019-11-25 12:30 | 200 | 200
2019-11-25 13:00 | 208 | 208
2019-11-25 13:30 | 214 | 214
2019-11-25 14:00 | 223 | 223
2019-11-25 14:30 | 231 | 231
2019-11-25 15:00 | 242 | 242
2019-11-25 15:30 | 256 | 256
2019-11-25 16:00 | 271 | 270
2019-11-25 16:30 | 286 | 286
2019-11-25 17:00 | 300 | 299
2019-11-25 17:30 | 303 | 303
2019-11-25 18:00 | 303 | 303
2019-11-25 18:30 | 300 | 300
2019-11-25 19:00 | 307 | 307
2019-11-25 19:30 | 301 | 301
2019-11-25 20:00 | 295 | 295
2019-11-25 20:30 | 287 | 287
2019-11-25 21:00 | 272 | 271
2019-11-25 21:30 | 259 | 259
2019-11-25 22:00 | 246 | 246
2019-11-25 22:30 | 238 | 238
2019-11-25 23:00 | 231 | 231
2019-11-25 23:30 | 213 | 212
2019-11-26 | 197 | 197
2019-11-26 00:30 | 185 | 185
2019-11-26 01:00 | 178 | 178
2019-11-26 01:30 | 174 | 174
2019-11-26 02:00 | 171 | 171
2019-11-26 02:30 | 169 | 169
2019-11-26 03:00 | 167 | 167
2019-11-26 03:30 | 168 | 168
2019-11-26 04:00 | 167 | 167
2019-11-26 04:30 | 171 | 171
2019-11-26 05:00 | 174 | 173
2019-11-26 05:30 | 180 | 180
2019-11-26 06:00 | 185 | 185
2019-11-26 06:30 | 199 | 199
2019-11-26 07:00 | 211 | 210
2019-11-26 07:30 | 224 | 223
2019-11-26 08:00 | 223 | 223
2019-11-26 08:30 | 220 | 220
2019-11-26 09:00 | 227 | 227
2019-11-26 09:30 | 227 | 227
2019-11-26 10:00 | 218 | 218
2019-11-26 10:30 | 210 | 210
2019-11-26 11:00 | 209 | 209
2019-11-26 11:30 | 211 | 211
2019-11-26 12:00 | 210 | 210
2019-11-26 12:30 | 206 | 205
2019-11-26 13:00 | 213 | 213
2019-11-26 13:30 | 224 | 224
2019-11-26 14:00 | 238 | 237
2019-11-26 14:30 | 250 | 250
2019-11-26 15:00 | 261 | 261
2019-11-26 15:30 | 276 | 276
2019-11-26 16:00 | 295 | 295
2019-11-26 16:30 | 313 | 313
2019-11-26 17:00 | 324 | 324
2019-11-26 17:30 | 325 | 325
2019-11-26 18:00 | 321 | 321
2019-11-26 18:30 | 316 | 316
2019-11-26 19:00 | 323 | 322
2019-11-26 19:30 | 316 | 316
2019-11-26 20:00 | 308 | 308
2019-11-26 20:30 | 302 | 302
2019-11-26 21:00 | 288 | 288
2019-11-26 21:30 | 273 | 273
2019-11-26 22:00 | 259 | 259
2019-11-26 22:30 | 249 | 249
2019-11-26 23:00 | 240 | 240
2019-11-26 23:30 | 222 | 221
2019-11-27 | 205 | 204
2019-11-27 00:30 | 192 | 192
2019-11-27 01:00 | 185 | 185
2019-11-27 01:30 | 180 | 180
2019-11-27 02:00 | 175 | 175
2019-11-27 02:30 | 171 | 171
2019-11-27 03:00 | 170 | 170
2019-11-27 03:30 | 169 | 169
2019-11-27 04:00 | 168 | 168
2019-11-27 04:30 | 172 | 172
2019-11-27 05:00 | 175 | 175
2019-11-27 05:30 | 181 | 180
2019-11-27 06:00 | 186 | 186
2019-11-27 06:30 | 205 | 205
2019-11-27 07:00 | 214 | 214
2019-11-27 07:30 | 224 | 223
2019-11-27 08:00 | 226 | 226
2019-11-27 08:30 | 226 | 226
2019-11-27 09:00 | 229 | 228
2019-11-27 09:30 | 233 | 232
2019-11-27 10:00 | 238 | 236
2019-11-27 10:30 | 241 | 240
2019-11-27 11:00 | 239 | 237
2019-11-27 11:30 | 236 | 234
2019-11-27 12:00 | 240 | 238
2019-11-27 12:30 | 245 | 244
2019-11-27 13:00 | 248 | 247
2019-11-27 13:30 | 248 | 248
2019-11-27 14:00 | 256 | 256
2019-11-27 14:30 | 265 | 264
2019-11-27 15:00 | 269 | 269
2019-11-27 15:30 | 279 | 279
2019-11-27 16:00 | 288 | 288
2019-11-27 16:30 | 289 | 289
2019-11-27 17:00 | 293 | 293
2019-11-27 17:30 | 291 | 291
2019-11-27 18:00 | 287 | 286
2019-11-27 18:30 | 284 | 283
2019-11-27 19:00 | 290 | 289
2019-11-27 19:30 | 284 | 283
2019-11-27 20:00 | 278 | 277
2019-11-27 20:30 | 271 | 271
2019-11-27 21:00 | 260 | 260
2019-11-27 21:30 | 249 | 249
2019-11-27 22:00 | 237 | 237
2019-11-27 22:30 | 230 | 230
2019-11-27 23:00 | 223 | 223
2019-11-27 23:30 | 209 | 208
2019-11-28 | 192 | 192
2019-11-28 00:30 | 178 | 178
2019-11-28 01:00 | 172 | 172
2019-11-28 01:30 | 169 | 169
2019-11-28 02:00 | 166 | 165
2019-11-28 02:30 | 163 | 163
2019-11-28 03:00 | 163 | 162
2019-11-28 03:30 | 163 | 163
2019-11-28 04:00 | 163 | 163
2019-11-28 04:30 | 166 | 166
2019-11-28 05:00 | 170 | 170
2019-11-28 05:30 | 180 | 179
2019-11-28 06:00 | 188 | 188
2019-11-28 06:30 | 203 | 203
2019-11-28 07:00 | 219 | 219
2019-11-28 07:30 | 234 | 234
2019-11-28 08:00 | 244 | 244
2019-11-28 08:30 | 246 | 245
2019-11-28 09:00 | 237 | 237
2019-11-28 09:30 | 233 | 232
2019-11-28 10:00 | 228 | 228
2019-11-28 10:30 | 229 | 228
2019-11-28 11:00 | 227 | 226
2019-11-28 11:30 | 216 | 216
2019-11-28 12:00 | 224 | 223
2019-11-28 12:30 | 242 | 241
2019-11-28 13:00 | 252 | 251
2019-11-28 13:30 | 254 | 252
2019-11-28 14:00 | 247 | 245
2019-11-28 14:30 | 238 | 237
2019-11-28 15:00 | 244 | 243
2019-11-28 15:30 | 256 | 255
2019-11-28 16:00 | 267 | 267
2019-11-28 16:30 | 281 | 281
2019-11-28 17:00 | 294 | 293
2019-11-28 17:30 | 298 | 298
2019-11-28 18:00 | 299 | 298
2019-11-28 18:30 | 300 | 300
2019-11-28 19:00 | 307 | 307
2019-11-28 19:30 | 305 | 305
2019-11-28 20:00 | 300 | 300
2019-11-28 20:30 | 293 | 293
2019-11-28 21:00 | 278 | 278
2019-11-28 21:30 | 265 | 265
2019-11-28 22:00 | 250 | 250
2019-11-28 22:30 | 242 | 242
2019-11-28 23:00 | 234 | 233
2019-11-28 23:30 | 219 | 218
2019-11-29 | 201 | 200
2019-11-29 00:30 | 186 | 186
2019-11-29 01:00 | 179 | 179
2019-11-29 01:30 | 174 | 174
2019-11-29 02:00 | 171 | 171
2019-11-29 02:30 | 168 | 168
2019-11-29 03:00 | 168 | 168
2019-11-29 03:30 | 168 | 168
2019-11-29 04:00 | 168 | 168
2019-11-29 04:30 | 171 | 171
2019-11-29 05:00 | 174 | 174
2019-11-29 05:30 | 181 | 181
2019-11-29 06:00 | 188 | 188
2019-11-29 06:30 | 205 | 205
2019-11-29 07:00 | 221 | 221
2019-11-29 07:30 | 235 | 233
2019-11-29 08:00 | 245 | 245
2019-11-29 08:30 | 250 | 250
2019-11-29 09:00 | 246 | 246
2019-11-29 09:30 | 243 | 242
2019-11-29 10:00 | 240 | 240
2019-11-29 10:30 | 232 | 231
2019-11-29 11:00 | 227 | 226
2019-11-29 11:30 | 224 | 223
2019-11-29 12:00 | 222 | 221
2019-11-29 12:30 | 223 | 222
2019-11-29 13:00 | 227 | 226
2019-11-29 13:30 | 236 | 235
2019-11-29 14:00 | 247 | 246
2019-11-29 14:30 | 256 | 256
2019-11-29 15:00 | 267 | 267
2019-11-29 15:30 | 279 | 279
2019-11-29 16:00 | 297 | 297
2019-11-29 16:30 | 309 | 308
2019-11-29 17:00 | 317 | 317
2019-11-29 17:30 | 315 | 315
2019-11-29 18:00 | 307 | 307
2019-11-29 18:30 | 301 | 301
2019-11-29 19:00 | 306 | 306
2019-11-29 19:30 | 303 | 303
2019-11-29 20:00 | 298 | 298
2019-11-29 20:30 | 286 | 286
2019-11-29 21:00 | 274 | 273
2019-11-29 21:30 | 263 | 263
2019-11-29 22:00 | 252 | 252
2019-11-29 22:30 | 244 | 243
2019-11-29 23:00 | 238 | 237
2019-11-29 23:30 | 221 | 220
2019-11-30 | 204 | 204
2019-11-30 00:30 | 191 | 191
2019-11-30 01:00 | 184 | 184
2019-11-30 01:30 | 178 | 178
2019-11-30 02:00 | 173 | 173
2019-11-30 02:30 | 170 | 170
2019-11-30 03:00 | 168 | 168
2019-11-30 03:30 | 167 | 167
2019-11-30 04:00 | 166 | 166
2019-11-30 04:30 | 166 | 166
2019-11-30 05:00 | 163 | 163
2019-11-30 05:30 | 163 | 162
2019-11-30 06:00 | 162 | 162
2019-11-30 06:30 | 165 | 165
2019-11-30 07:00 | 164 | 164
2019-11-30 07:30 | 166 | 166
2019-11-30 08:00 | 168 | 168
2019-11-30 08:30 | 172 | 172
2019-11-30 09:00 | 175 | 174
2019-11-30 09:30 | 178 | 177
2019-11-30 10:00 | 183 | 181
2019-11-30 10:30 | 188 | 186
2019-11-30 11:00 | 195 | 192
2019-11-30 11:30 | 201 | 199
2019-11-30 12:00 | 206 | 206
2019-11-30 12:30 | 211 | 211
2019-11-30 13:00 | 227 | 226
2019-11-30 13:30 | 232 | 231
2019-11-30 14:00 | 231 | 231
2019-11-30 14:30 | 241 | 240
2019-11-30 15:00 | 253 | 253
2019-11-30 15:30 | 265 | 264
2019-11-30 16:00 | 278 | 277
2019-11-30 16:30 | 291 | 291
2019-11-30 17:00 | 304 | 304
2019-11-30 17:30 | 296 | 296
2019-11-30 18:00 | 288 | 288
2019-11-30 18:30 | 288 | 288
2019-11-30 19:00 | 293 | 293
2019-11-30 19:30 | 291 | 291
2019-11-30 20:00 | 286 | 286
2019-11-30 20:30 | 276 | 276
2019-11-30 21:00 | 264 | 264
2019-11-30 21:30 | 256 | 256
2019-11-30 22:00 | 248 | 248
2019-11-30 22:30 | 241 | 241
2019-11-30 23:00 | 232 | 232
2019-11-30 23:30 | 219 | 219
2019-12-01 | 203 | 202
2019-12-01 00:30 | 189 | 189
2019-12-01 01:00 | 180 | 180
2019-12-01 01:30 | 174 | 174
2019-12-01 02:00 | 170 | 169
2019-12-01 02:30 | 167 | 167
2019-12-01 03:00 | 164 | 164
2019-12-01 03:30 | 163 | 163
2019-12-01 04:00 | 162 | 162
2019-12-01 04:30 | 163 | 163
2019-12-01 05:00 | 160 | 160
2019-12-01 05:30 | 159 | 159
2019-12-01 06:00 | 157 | 157
2019-12-01 06:30 | 159 | 159
2019-12-01 07:00 | 157 | 157
2019-12-01 07:30 | 166 | 166
2019-12-01 08:00 | 166 | 165
2019-12-01 08:30 | 188 | 188
2019-12-01 09:00 | 176 | 176
2019-12-01 09:30 | 173 | 172
2019-12-01 10:00 | 173 | 172
2019-12-01 10:30 | 173 | 172
2019-12-01 11:00 | 181 | 180
2019-12-01 11:30 | 197 | 196
2019-12-01 12:00 | 206 | 204
2019-12-01 12:30 | 218 | 216
2019-12-01 13:00 | 216 | 214
2019-12-01 13:30 | 247 | 246
2019-12-01 14:00 | 283 | 282
2019-12-01 14:30 | 286 | 286
2019-12-01 15:00 | 241 | 241
2019-12-01 15:30 | 245 | 245
2019-12-01 16:00 | 262 | 262
2019-12-01 16:30 | 269 | 269
2019-12-01 17:00 | 277 | 277
2019-12-01 17:30 | 272 | 272
2019-12-01 18:00 | 269 | 269
2019-12-01 18:30 | 275 | 275
2019-12-01 19:00 | 281 | 281
2019-12-01 19:30 | 278 | 278
2019-12-01 20:00 | 274 | 274
2019-12-01 20:30 | 266 | 266
2019-12-01 21:00 | 253 | 253
2019-12-01 21:30 | 241 | 241
2019-12-01 22:00 | 231 | 231
2019-12-01 22:30 | 222 | 221
2019-12-01 23:00 | 215 | 215
2019-12-01 23:30 | 205 | 205
2019-12-02 | 190 | 190
2019-12-02 00:30 | 178 | 178
2019-12-02 01:00 | 173 | 173
2019-12-02 01:30 | 167 | 167
2019-12-02 02:00 | 164 | 164
2019-12-02 02:30 | 163 | 163
2019-12-02 03:00 | 159 | 159
2019-12-02 03:30 | 159 | 159
2019-12-02 04:00 | 159 | 159
2019-12-02 04:30 | 162 | 162
2019-12-02 05:00 | 166 | 166
2019-12-02 05:30 | 174 | 174
2019-12-02 06:00 | 184 | 184
2019-12-02 06:30 | 196 | 195
2019-12-02 07:00 | 207 | 206
2019-12-02 07:30 | 216 | 215
2019-12-02 08:00 | 217 | 215
2019-12-02 08:30 | 215 | 212
2019-12-02 09:00 | 210 | 207
2019-12-02 09:30 | 203 | 201
2019-12-02 10:00 | 197 | 196
2019-12-02 10:30 | 193 | 193
2019-12-02 11:00 | 193 | 193
2019-12-02 11:30 | 196 | 196
2019-12-02 12:00 | 202 | 201
2019-12-02 12:30 | 210 | 209
2019-12-02 13:00 | 217 | 216
2019-12-02 13:30 | 228 | 227
2019-12-02 14:00 | 240 | 239
2019-12-02 14:30 | 251 | 251
2019-12-02 15:00 | 264 | 264
2019-12-02 15:30 | 279 | 279
2019-12-02 16:00 | 299 | 298
2019-12-02 16:30 | 316 | 315
2019-12-02 17:00 | 325 | 324
2019-12-02 17:30 | 338 | 337
2019-12-02 18:00 | 337 | 337
2019-12-02 18:30 | 331 | 331
2019-12-02 19:00 | 336 | 335
2019-12-02 19:30 | 332 | 332
2019-12-02 20:00 | 325 | 325
2019-12-02 20:30 | 314 | 313
2019-12-02 21:00 | 296 | 295
2019-12-02 21:30 | 279 | 278
2019-12-02 22:00 | 261 | 261
2019-12-02 22:30 | 249 | 249
2019-12-02 23:00 | 241 | 241
2019-12-02 23:30 | 224 | 223
2019-12-03 | 204 | 204
2019-12-03 00:30 | 190 | 189
2019-12-03 01:00 | 181 | 181
2019-12-03 01:30 | 175 | 175
2019-12-03 02:00 | 170 | 170
2019-12-03 02:30 | 166 | 166
2019-12-03 03:00 | 165 | 165
2019-12-03 03:30 | 164 | 164
2019-12-03 04:00 | 163 | 163
2019-12-03 04:30 | 166 | 166
2019-12-03 05:00 | 167 | 167
2019-12-03 05:30 | 174 | 174
2019-12-03 06:00 | 178 | 178
2019-12-03 06:30 | 189 | 188
2019-12-03 07:00 | 200 | 198
2019-12-03 07:30 | 206 | 206
2019-12-03 08:00 | 204 | 204
2019-12-03 08:30 | 204 | 204
2019-12-03 09:00 | 204 | 204
2019-12-03 09:30 | 203 | 202
2019-12-03 10:00 | 201 | 201
2019-12-03 10:30 | 204 | 203
2019-12-03 11:00 | 206 | 205
2019-12-03 11:30 | 210 | 209
2019-12-03 12:00 | 215 | 215
2019-12-03 12:30 | 222 | 222
2019-12-03 13:00 | 233 | 232
2019-12-03 13:30 | 243 | 243
2019-12-03 14:00 | 256 | 256
2019-12-03 14:30 | 271 | 270
2019-12-03 15:00 | 277 | 275
2019-12-03 15:30 | 292 | 291
2019-12-03 16:00 | 311 | 309
2019-12-03 16:30 | 327 | 326
2019-12-03 17:00 | 340 | 340
2019-12-03 17:30 | 344 | 344
2019-12-03 18:00 | 340 | 340
2019-12-03 18:30 | 333 | 333
2019-12-03 19:00 | 337 | 337
2019-12-03 19:30 | 335 | 335
2019-12-03 20:00 | 329 | 329
2019-12-03 20:30 | 318 | 318
2019-12-03 21:00 | 300 | 300
2019-12-03 21:30 | 279 | 279
2019-12-03 22:00 | 262 | 262
2019-12-03 22:30 | 250 | 250
2019-12-03 23:00 | 238 | 238
2019-12-03 23:30 | 219 | 218
2019-12-04 | 201 | 200
2019-12-04 00:30 | 187 | 187
2019-12-04 01:00 | 179 | 179
2019-12-04 01:30 | 173 | 172
2019-12-04 02:00 | 168 | 168
2019-12-04 02:30 | 165 | 165
2019-12-04 03:00 | 163 | 163
2019-12-04 03:30 | 163 | 163
2019-12-04 04:00 | 161 | 161
2019-12-04 04:30 | 163 | 163
2019-12-04 05:00 | 166 | 166
2019-12-04 05:30 | 173 | 172
2019-12-04 06:00 | 178 | 177
2019-12-04 06:30 | 187 | 186
2019-12-04 07:00 | 200 | 199
2019-12-04 07:30 | 216 | 215
2019-12-04 08:00 | 211 | 209
2019-12-04 08:30 | 209 | 206
2019-12-04 09:00 | 206 | 206
2019-12-04 09:30 | 206 | 206
2019-12-04 10:00 | 207 | 206
2019-12-04 10:30 | 212 | 211
2019-12-04 11:00 | 220 | 219
2019-12-04 11:30 | 227 | 225
2019-12-04 12:00 | 237 | 234
2019-12-04 12:30 | 245 | 241
2019-12-04 13:00 | 253 | 253
2019-12-04 13:30 | 260 | 260
2019-12-04 14:00 | 268 | 268
2019-12-04 14:30 | 271 | 271
2019-12-04 15:00 | 270 | 270
2019-12-04 15:30 | 282 | 281
2019-12-04 16:00 | 297 | 296
2019-12-04 16:30 | 310 | 310
2019-12-04 17:00 | 322 | 322
2019-12-04 17:30 | 324 | 324
2019-12-04 18:00 | 319 | 319
2019-12-04 18:30 | 313 | 313
2019-12-04 19:00 | 316 | 316
2019-12-04 19:30 | 313 | 312
2019-12-04 20:00 | 307 | 305
2019-12-04 20:30 | 298 | 297
2019-12-04 21:00 | 282 | 281
2019-12-04 21:30 | 269 | 268
2019-12-04 22:00 | 253 | 253
2019-12-04 22:30 | 243 | 243
2019-12-04 23:00 | 233 | 233
2019-12-04 23:30 | 215 | 214
2019-12-05 | 198 | 197
2019-12-05 00:30 | 184 | 184
2019-12-05 01:00 | 176 | 176
2019-12-05 01:30 | 171 | 170
2019-12-05 02:00 | 167 | 166
2019-12-05 02:30 | 163 | 163
2019-12-05 03:00 | 161 | 161
2019-12-05 03:30 | 162 | 162
2019-12-05 04:00 | 161 | 161
2019-12-05 04:30 | 163 | 163
2019-12-05 05:00 | 165 | 165
2019-12-05 05:30 | 172 | 172
2019-12-05 06:00 | 175 | 175
2019-12-05 06:30 | 185 | 184
2019-12-05 07:00 | 192 | 190
2019-12-05 07:30 | 196 | 194
2019-12-05 08:00 | 193 | 192
2019-12-05 08:30 | 195 | 193
2019-12-05 09:00 | 196 | 194
2019-12-05 09:30 | 201 | 201
2019-12-05 10:00 | 203 | 203
2019-12-05 10:30 | 210 | 210
2019-12-05 11:00 | 217 | 217
2019-12-05 11:30 | 224 | 224
2019-12-05 12:00 | 233 | 233
2019-12-05 12:30 | 243 | 243
2019-12-05 13:00 | 254 | 254
2019-12-05 13:30 | 268 | 267
2019-12-05 14:00 | 281 | 280
2019-12-05 14:30 | 295 | 294
2019-12-05 15:00 | 307 | 307
2019-12-05 15:30 | 324 | 323
2019-12-05 16:00 | 340 | 340
2019-12-05 16:30 | 354 | 353
2019-12-05 17:00 | 363 | 363
2019-12-05 17:30 | 363 | 363
2019-12-05 18:00 | 357 | 357
2019-12-05 18:30 | 348 | 348
2019-12-05 19:00 | 348 | 348
2019-12-05 19:30 | 344 | 344
2019-12-05 20:00 | 336 | 336
2019-12-05 20:30 | 325 | 325
2019-12-05 21:00 | 309 | 309
2019-12-05 21:30 | 292 | 292
2019-12-05 22:00 | 276 | 275
2019-12-05 22:30 | 265 | 264
2019-12-05 23:00 | 253 | 252
2019-12-05 23:30 | 231 | 230
2019-12-06 | 211 | 211
2019-12-06 00:30 | 196 | 195
2019-12-06 01:00 | 187 | 186
2019-12-06 01:30 | 181 | 181
2019-12-06 02:00 | 175 | 175
2019-12-06 02:30 | 172 | 171
2019-12-06 03:00 | 170 | 169
2019-12-06 03:30 | 169 | 169
2019-12-06 04:00 | 168 | 167
2019-12-06 04:30 | 169 | 169
2019-12-06 05:00 | 171 | 170
2019-12-06 05:30 | 177 | 176
2019-12-06 06:00 | 181 | 180
2019-12-06 06:30 | 192 | 191
2019-12-06 07:00 | 199 | 198
2019-12-06 07:30 | 207 | 206
2019-12-06 08:00 | 209 | 209
2019-12-06 08:30 | 211 | 211
2019-12-06 09:00 | 216 | 216
2019-12-06 09:30 | 224 | 223
2019-12-06 10:00 | 231 | 230
2019-12-06 10:30 | 241 | 240
2019-12-06 11:00 | 252 | 251
2019-12-06 11:30 | 262 | 261
2019-12-06 12:00 | 274 | 272
2019-12-06 12:30 | 282 | 280
2019-12-06 13:00 | 297 | 297
2019-12-06 13:30 | 309 | 309
2019-12-06 14:00 | 322 | 322
2019-12-06 14:30 | 332 | 332
2019-12-06 15:00 | 344 | 343
2019-12-06 15:30 | 358 | 358
2019-12-06 16:00 | 378 | 377
2019-12-06 16:30 | 387 | 386
2019-12-06 17:00 | 388 | 387
2019-12-06 17:30 | 390 | 389
2019-12-06 18:00 | 384 | 383
2019-12-06 18:30 | 370 | 370
2019-12-06 19:00 | 366 | 366
2019-12-06 19:30 | 364 | 363
2019-12-06 20:00 | 363 | 363
2019-12-06 20:30 | 367 | 367
2019-12-06 21:00 | 345 | 345
2019-12-06 21:30 | 336 | 336
2019-12-06 22:00 | 326 | 325
2019-12-06 22:30 | 312 | 312
2019-12-06 23:00 | 287 | 287
2019-12-06 23:30 | 266 | 266
2019-12-07 | 247 | 247
2019-12-07 00:30 | 229 | 229
2019-12-07 01:00 | 218 | 217
2019-12-07 01:30 | 207 | 207
2019-12-07 02:00 | 198 | 198
2019-12-07 02:30 | 193 | 193
2019-12-07 03:00 | 190 | 190
2019-12-07 03:30 | 188 | 188
2019-12-07 04:00 | 186 | 186
2019-12-07 04:30 | 184 | 184
2019-12-07 05:00 | 181 | 180
2019-12-07 05:30 | 180 | 180
2019-12-07 06:00 | 179 | 178
2019-12-07 06:30 | 180 | 180
2019-12-07 07:00 | 182 | 182
2019-12-07 07:30 | 188 | 188
2019-12-07 08:00 | 194 | 193
2019-12-07 08:30 | 206 | 206
2019-12-07 09:00 | 219 | 217
2019-12-07 09:30 | 230 | 228
2019-12-07 10:00 | 242 | 242
2019-12-07 10:30 | 253 | 253
2019-12-07 11:00 | 263 | 263
2019-12-07 11:30 | 274 | 274
2019-12-07 12:00 | 285 | 285
2019-12-07 12:30 | 295 | 295
2019-12-07 13:00 | 305 | 305
2019-12-07 13:30 | 310 | 309
2019-12-07 14:00 | 316 | 315
2019-12-07 14:30 | 322 | 321
2019-12-07 15:00 | 328 | 327
2019-12-07 15:30 | 336 | 335
2019-12-07 16:00 | 342 | 342
2019-12-07 16:30 | 346 | 346
2019-12-07 17:00 | 351 | 351
2019-12-07 17:30 | 345 | 345
2019-12-07 18:00 | 335 | 335
2019-12-07 18:30 | 328 | 328
2019-12-07 19:00 | 325 | 325
2019-12-07 19:30 | 319 | 319
2019-12-07 20:00 | 311 | 311
2019-12-07 20:30 | 301 | 301
2019-12-07 21:00 | 286 | 286
2019-12-07 21:30 | 274 | 274
2019-12-07 22:00 | 261 | 261
2019-12-07 22:30 | 252 | 252
2019-12-07 23:00 | 244 | 244
2019-12-07 23:30 | 229 | 228
2019-12-08 | 213 | 212
2019-12-08 00:30 | 199 | 198
2019-12-08 01:00 | 191 | 191
2019-12-08 01:30 | 185 | 185
2019-12-08 02:00 | 179 | 179
2019-12-08 02:30 | 176 | 176
2019-12-08 03:00 | 173 | 173
2019-12-08 03:30 | 172 | 171
2019-12-08 04:00 | 170 | 170
2019-12-08 04:30 | 170 | 170
2019-12-08 05:00 | 167 | 167
2019-12-08 05:30 | 165 | 165
2019-12-08 06:00 | 165 | 164
2019-12-08 06:30 | 167 | 167
2019-12-08 07:00 | 170 | 170
2019-12-08 07:30 | 176 | 176
2019-12-08 08:00 | 177 | 177
2019-12-08 08:30 | 187 | 186
2019-12-08 09:00 | 187 | 187
2019-12-08 09:30 | 188 | 188
2019-12-08 10:00 | 203 | 202
2019-12-08 10:30 | 205 | 204
2019-12-08 11:00 | 199 | 197
2019-12-08 11:30 | 195 | 193
2019-12-08 12:00 | 195 | 193
2019-12-08 12:30 | 191 | 189
2019-12-08 13:00 | 193 | 191
2019-12-08 13:30 | 200 | 197
2019-12-08 14:00 | 211 | 209
2019-12-08 14:30 | 222 | 220
2019-12-08 15:00 | 235 | 233
2019-12-08 15:30 | 248 | 245
2019-12-08 16:00 | 263 | 263
2019-12-08 16:30 | 276 | 275
2019-12-08 17:00 | 285 | 285
2019-12-08 17:30 | 287 | 287
2019-12-08 18:00 | 287 | 287
2019-12-08 18:30 | 288 | 288
2019-12-08 19:00 | 293 | 293
2019-12-08 19:30 | 292 | 291
2019-12-08 20:00 | 288 | 288
2019-12-08 20:30 | 282 | 282
2019-12-08 21:00 | 269 | 269
2019-12-08 21:30 | 257 | 256
2019-12-08 22:00 | 245 | 245
2019-12-08 22:30 | 239 | 239
2019-12-08 23:00 | 234 | 234
2019-12-08 23:30 | 221 | 220
2019-12-09 | 206 | 205
2019-12-09 00:30 | 193 | 193
2019-12-09 01:00 | 186 | 186
2019-12-09 01:30 | 180 | 180
2019-12-09 02:00 | 176 | 176
2019-12-09 02:30 | 173 | 173
2019-12-09 03:00 | 171 | 171
2019-12-09 03:30 | 172 | 172
2019-12-09 04:00 | 172 | 172
2019-12-09 04:30 | 174 | 174
2019-12-09 05:00 | 177 | 177
2019-12-09 05:30 | 184 | 184
2019-12-09 06:00 | 191 | 191
2019-12-09 06:30 | 206 | 205
2019-12-09 07:00 | 219 | 217
2019-12-09 07:30 | 231 | 229
2019-12-09 08:00 | 237 | 236
2019-12-09 08:30 | 242 | 242
2019-12-09 09:00 | 248 | 248
2019-12-09 09:30 | 255 | 255
2019-12-09 10:00 | 258 | 258
2019-12-09 10:30 | 263 | 263
2019-12-09 11:00 | 269 | 269
2019-12-09 11:30 | 270 | 269
2019-12-09 12:00 | 274 | 273
2019-12-09 12:30 | 277 | 276
2019-12-09 13:00 | 283 | 282
2019-12-09 13:30 | 291 | 289
2019-12-09 14:00 | 300 | 299
2019-12-09 14:30 | 310 | 310
2019-12-09 15:00 | 314 | 314
2019-12-09 15:30 | 323 | 323
2019-12-09 16:00 | 338 | 338
2019-12-09 16:30 | 348 | 348
2019-12-09 17:00 | 352 | 351
2019-12-09 17:30 | 353 | 352
2019-12-09 18:00 | 349 | 348
2019-12-09 18:30 | 341 | 341
2019-12-09 19:00 | 340 | 340
2019-12-09 19:30 | 346 | 346
2019-12-09 20:00 | 342 | 341
2019-12-09 20:30 | 331 | 330
2019-12-09 21:00 | 314 | 314
2019-12-09 21:30 | 299 | 299
2019-12-09 22:00 | 280 | 280
2019-12-09 22:30 | 267 | 267
2019-12-09 23:00 | 257 | 257
2019-12-09 23:30 | 241 | 241
2019-12-10 | 221 | 220
2019-12-10 00:30 | 207 | 207
2019-12-10 01:00 | 198 | 198
2019-12-10 01:30 | 193 | 193
2019-12-10 02:00 | 189 | 189
2019-12-10 02:30 | 186 | 186
2019-12-10 03:00 | 185 | 185
2019-12-10 03:30 | 184 | 184
2019-12-10 04:00 | 182 | 182
2019-12-10 04:30 | 185 | 185
2019-12-10 05:00 | 187 | 187
2019-12-10 05:30 | 194 | 194
2019-12-10 06:00 | 200 | 200
2019-12-10 06:30 | 215 | 215
2019-12-10 07:00 | 228 | 227
2019-12-10 07:30 | 245 | 245
2019-12-10 08:00 | 256 | 256
2019-12-10 08:30 | 266 | 266
2019-12-10 09:00 | 274 | 273
2019-12-10 09:30 | 274 | 273
2019-12-10 10:00 | 268 | 267
2019-12-10 10:30 | 270 | 270
2019-12-10 11:00 | 261 | 260
2019-12-10 11:30 | 260 | 259
2019-12-10 12:00 | 271 | 270
2019-12-10 12:30 | 281 | 280
2019-12-10 13:00 | 293 | 293
2019-12-10 13:30 | 306 | 306
2019-12-10 14:00 | 317 | 317
2019-12-10 14:30 | 329 | 329
2019-12-10 15:00 | 340 | 340
2019-12-10 15:30 | 353 | 352
2019-12-10 16:00 | 370 | 369
2019-12-10 16:30 | 383 | 383
2019-12-10 17:00 | 390 | 390
2019-12-10 17:30 | 387 | 387
2019-12-10 18:00 | 381 | 381
2019-12-10 18:30 | 370 | 370
2019-12-10 19:00 | 369 | 369
2019-12-10 19:30 | 363 | 363
2019-12-10 20:00 | 355 | 354
2019-12-10 20:30 | 346 | 345
2019-12-10 21:00 | 325 | 325
2019-12-10 21:30 | 311 | 310
2019-12-10 22:00 | 292 | 291
2019-12-10 22:30 | 279 | 278
2019-12-10 23:00 | 267 | 267
2019-12-10 23:30 | 249 | 248
2019-12-11 | 230 | 230
2019-12-11 00:30 | 214 | 214
2019-12-11 01:00 | 206 | 206
2019-12-11 01:30 | 201 | 201
2019-12-11 02:00 | 195 | 195
2019-12-11 02:30 | 191 | 190
2019-12-11 03:00 | 189 | 188
2019-12-11 03:30 | 187 | 186
2019-12-11 04:00 | 186 | 185
2019-12-11 04:30 | 188 | 187
2019-12-11 05:00 | 189 | 188
2019-12-11 05:30 | 197 | 196
2019-12-11 06:00 | 204 | 203
2019-12-11 06:30 | 219 | 218
2019-12-11 07:00 | 234 | 234
2019-12-11 07:30 | 247 | 247
2019-12-11 08:00 | 252 | 251
2019-12-11 08:30 | 254 | 253
2019-12-11 09:00 | 257 | 256
2019-12-11 09:30 | 263 | 262
2019-12-11 10:00 | 269 | 268
2019-12-11 10:30 | 274 | 274
2019-12-11 11:00 | 283 | 281
2019-12-11 11:30 | 292 | 292
2019-12-11 12:00 | 304 | 304
2019-12-11 12:30 | 314 | 314
2019-12-11 13:00 | 332 | 332
2019-12-11 13:30 | 343 | 343
2019-12-11 14:00 | 357 | 357
2019-12-11 14:30 | 363 | 363
2019-12-11 15:00 | 370 | 370
2019-12-11 15:30 | 374 | 373
2019-12-11 16:00 | 393 | 392
2019-12-11 16:30 | 392 | 392
2019-12-11 17:00 | 385 | 385
2019-12-11 17:30 | 372 | 372
2019-12-11 18:00 | 358 | 358
2019-12-11 18:30 | 356 | 356
2019-12-11 19:00 | 363 | 363
2019-12-11 19:30 | 360 | 359
2019-12-11 20:00 | 349 | 349
2019-12-11 20:30 | 339 | 339
2019-12-11 21:00 | 325 | 325
2019-12-11 21:30 | 310 | 309
2019-12-11 22:00 | 293 | 291
2019-12-11 22:30 | 268 | 268
2019-12-11 23:00 | 247 | 247
2019-12-11 23:30 | 225 | 225
2019-12-12 | 207 | 207
2019-12-12 00:30 | 193 | 193
2019-12-12 01:00 | 185 | 185
2019-12-12 01:30 | 181 | 181
2019-12-12 02:00 | 178 | 178
2019-12-12 02:30 | 175 | 175
2019-12-12 03:00 | 174 | 174
2019-12-12 03:30 | 175 | 175
2019-12-12 04:00 | 174 | 174
2019-12-12 04:30 | 176 | 176
2019-12-12 05:00 | 178 | 178
2019-12-12 05:30 | 185 | 185
2019-12-12 06:00 | 194 | 194
2019-12-12 06:30 | 208 | 208
2019-12-12 07:00 | 220 | 219
2019-12-12 07:30 | 223 | 223
2019-12-12 08:00 | 226 | 226
2019-12-12 08:30 | 231 | 231
2019-12-12 09:00 | 236 | 236
2019-12-12 09:30 | 240 | 240
2019-12-12 10:00 | 241 | 241
2019-12-12 10:30 | 245 | 245
2019-12-12 11:00 | 252 | 252
2019-12-12 11:30 | 258 | 258
2019-12-12 12:00 | 263 | 263
2019-12-12 12:30 | 269 | 269
2019-12-12 13:00 | 276 | 276
2019-12-12 13:30 | 287 | 287
2019-12-12 14:00 | 298 | 297
2019-12-12 14:30 | 307 | 307
2019-12-12 15:00 | 317 | 317
2019-12-12 15:30 | 332 | 331
2019-12-12 16:00 | 343 | 343
2019-12-12 16:30 | 370 | 369
2019-12-12 17:00 | 377 | 376
2019-12-12 17:30 | 367 | 367
2019-12-12 18:00 | 352 | 352
2019-12-12 18:30 | 333 | 333
2019-12-12 19:00 | 341 | 341
2019-12-12 19:30 | 350 | 349
2019-12-12 20:00 | 346 | 345
2019-12-12 20:30 | 337 | 336
2019-12-12 21:00 | 323 | 322
2019-12-12 21:30 | 307 | 305
2019-12-12 22:00 | 292 | 287
2019-12-12 22:30 | 279 | 275
2019-12-12 23:00 | 268 | 265
2019-12-12 23:30 | 245 | 243
2019-12-13 | 226 | 225
2019-12-13 00:30 | 212 | 211
2019-12-13 01:00 | 204 | 203
2019-12-13 01:30 | 199 | 199
2019-12-13 02:00 | 193 | 192
2019-12-13 02:30 | 189 | 188
2019-12-13 03:00 | 189 | 188
2019-12-13 03:30 | 189 | 188
2019-12-13 04:00 | 191 | 191
2019-12-13 04:30 | 195 | 194
2019-12-13 05:00 | 197 | 196
2019-12-13 05:30 | 204 | 203
2019-12-13 06:00 | 212 | 210
2019-12-13 06:30 | 226 | 224
2019-12-13 07:00 | 238 | 236
2019-12-13 07:30 | 259 | 258
2019-12-13 08:00 | 264 | 264
2019-12-13 08:30 | 273 | 272
2019-12-13 09:00 | 300 | 300
2019-12-13 09:30 | 317 | 317
2019-12-13 10:00 | 309 | 309
2019-12-13 10:30 | 292 | 292
2019-12-13 11:00 | 282 | 282
2019-12-13 11:30 | 291 | 291
2019-12-13 12:00 | 293 | 293
2019-12-13 12:30 | 297 | 297
2019-12-13 13:00 | 306 | 305
2019-12-13 13:30 | 310 | 310
2019-12-13 14:00 | 296 | 296
2019-12-13 14:30 | 295 | 295
2019-12-13 15:00 | 311 | 311
2019-12-13 15:30 | 322 | 322
2019-12-13 16:00 | 304 | 304
2019-12-13 16:30 | 271 | 270
2019-12-13 17:00 | 275 | 275
2019-12-13 17:30 | 276 | 275
2019-12-13 18:00 | 282 | 282
2019-12-13 18:30 | 283 | 282
2019-12-13 19:00 | 289 | 289
2019-12-13 19:30 | 290 | 289
2019-12-13 20:00 | 286 | 286
2019-12-13 20:30 | 280 | 280
2019-12-13 21:00 | 270 | 270
2019-12-13 21:30 | 258 | 258
2019-12-13 22:00 | 247 | 247
2019-12-13 22:30 | 241 | 241
2019-12-13 23:00 | 236 | 236
2019-12-13 23:30 | 222 | 222
2019-12-14 | 206 | 206
2019-12-14 00:30 | 193 | 193
2019-12-14 01:00 | 185 | 185
2019-12-14 01:30 | 179 | 178
2019-12-14 02:00 | 175 | 174
2019-12-14 02:30 | 173 | 171
2019-12-14 03:00 | 171 | 169
2019-12-14 03:30 | 169 | 168
2019-12-14 04:00 | 166 | 166
2019-12-14 04:30 | 167 | 167
2019-12-14 05:00 | 167 | 166
2019-12-14 05:30 | 167 | 167
2019-12-14 06:00 | 169 | 168
2019-12-14 06:30 | 174 | 174
2019-12-14 07:00 | 176 | 176
2019-12-14 07:30 | 177 | 177
2019-12-14 08:00 | 184 | 184
2019-12-14 08:30 | 200 | 199
2019-12-14 09:00 | 204 | 204
2019-12-14 09:30 | 193 | 193
2019-12-14 10:00 | 187 | 187
2019-12-14 10:30 | 189 | 188
2019-12-14 11:00 | 187 | 186
2019-12-14 11:30 | 189 | 189
2019-12-14 12:00 | 193 | 193
2019-12-14 12:30 | 199 | 199
2019-12-14 13:00 | 209 | 209
2019-12-14 13:30 | 222 | 222
2019-12-14 14:00 | 235 | 235
2019-12-14 14:30 | 247 | 247
2019-12-14 15:00 | 260 | 260
2019-12-14 15:30 | 272 | 272
2019-12-14 16:00 | 289 | 288
2019-12-14 16:30 | 302 | 301
2019-12-14 17:00 | 314 | 313
2019-12-14 17:30 | 316 | 315
2019-12-14 18:00 | 310 | 309
2019-12-14 18:30 | 308 | 307
2019-12-14 19:00 | 310 | 308
2019-12-14 19:30 | 309 | 307
2019-12-14 20:00 | 305 | 304
2019-12-14 20:30 | 298 | 297
2019-12-14 21:00 | 285 | 284
2019-12-14 21:30 | 276 | 276
2019-12-14 22:00 | 265 | 265
2019-12-14 22:30 | 260 | 260
2019-12-14 23:00 | 255 | 255
2019-12-14 23:30 | 239 | 239
2019-12-15 | 220 | 220
2019-12-15 00:30 | 204 | 203
2019-12-15 01:00 | 196 | 195
2019-12-15 01:30 | 189 | 189
2019-12-15 02:00 | 185 | 184
2019-12-15 02:30 | 180 | 180
2019-12-15 03:00 | 177 | 177
2019-12-15 03:30 | 176 | 175
2019-12-15 04:00 | 173 | 172
2019-12-15 04:30 | 171 | 171
2019-12-15 05:00 | 167 | 167
2019-12-15 05:30 | 167 | 167
2019-12-15 06:00 | 164 | 164
2019-12-15 06:30 | 164 | 164
2019-12-15 07:00 | 164 | 164
2019-12-15 07:30 | 170 | 170
2019-12-15 08:00 | 176 | 176
2019-12-15 08:30 | 184 | 184
2019-12-15 09:00 | 193 | 193
2019-12-15 09:30 | 198 | 197
2019-12-15 10:00 | 202 | 201
2019-12-15 10:30 | 209 | 207
2019-12-15 11:00 | 216 | 213
2019-12-15 11:30 | 223 | 219
2019-12-15 12:00 | 234 | 230
2019-12-15 12:30 | 240 | 236
2019-12-15 13:00 | 250 | 245
2019-12-15 13:30 | 260 | 255
2019-12-15 14:00 | 271 | 267
2019-12-15 14:30 | 287 | 285
2019-12-15 15:00 | 305 | 303
2019-12-15 15:30 | 306 | 305
2019-12-15 16:00 | 315 | 315
2019-12-15 16:30 | 336 | 335
2019-12-15 17:00 | 341 | 340
2019-12-15 17:30 | 338 | 337
2019-12-15 18:00 | 335 | 334
2019-12-15 18:30 | 334 | 333
2019-12-15 19:00 | 336 | 335
2019-12-15 19:30 | 329 | 328
2019-12-15 20:00 | 322 | 321
2019-12-15 20:30 | 311 | 310
2019-12-15 21:00 | 295 | 294
2019-12-15 21:30 | 282 | 281
2019-12-15 22:00 | 269 | 269
2019-12-15 22:30 | 264 | 262
2019-12-15 23:00 | 258 | 256
2019-12-15 23:30 | 242 | 240
2019-12-16 | 225 | 223
2019-12-16 00:30 | 211 | 210
2019-12-16 01:00 | 206 | 200
2019-12-16 01:30 | 200 | 195
2019-12-16 02:00 | 196 | 191
2019-12-16 02:30 | 192 | 187
2019-12-16 03:00 | 189 | 184
2019-12-16 03:30 | 188 | 184
2019-12-16 04:00 | 188 | 184
2019-12-16 04:30 | 191 | 187
2019-12-16 05:00 | 192 | 188
2019-12-16 05:30 | 200 | 196
2019-12-16 06:00 | 210 | 205
2019-12-16 06:30 | 226 | 225
2019-12-16 07:00 | 242 | 240
2019-12-16 07:30 | 254 | 254
2019-12-16 08:00 | 257 | 257
2019-12-16 08:30 | 263 | 263
2019-12-16 09:00 | 275 | 274
2019-12-16 09:30 | 288 | 288
2019-12-16 10:00 | 294 | 293
2019-12-16 10:30 | 304 | 303
2019-12-16 11:00 | 316 | 315
2019-12-16 11:30 | 325 | 324
2019-12-16 12:00 | 337 | 335
2019-12-16 12:30 | 350 | 347
2019-12-16 13:00 | 361 | 359
2019-12-16 13:30 | 374 | 371
2019-12-16 14:00 | 389 | 388
2019-12-16 14:30 | 405 | 403
2019-12-16 15:00 | 419 | 417
2019-12-16 15:30 | 412 | 411
2019-12-16 16:00 | 396 | 396
2019-12-16 16:30 | 394 | 394
2019-12-16 17:00 | 397 | 397
2019-12-16 17:30 | 389 | 389
2019-12-16 18:00 | 379 | 378
2019-12-16 18:30 | 360 | 359
2019-12-16 19:00 | 350 | 349
2019-12-16 19:30 | 337 | 337
2019-12-16 20:00 | 320 | 320
2019-12-16 20:30 | 321 | 321
2019-12-16 21:00 | 310 | 310
2019-12-16 21:30 | 284 | 283
2019-12-16 22:00 | 266 | 266
2019-12-16 22:30 | 240 | 240
2019-12-16 23:00 | 232 | 231
2019-12-16 23:30 | 219 | 218
2019-12-17 | 205 | 205
2019-12-17 00:30 | 191 | 191
2019-12-17 01:00 | 182 | 182
2019-12-17 01:30 | 177 | 177
2019-12-17 02:00 | 174 | 174
2019-12-17 02:30 | 176 | 176
2019-12-17 03:00 | 179 | 179
2019-12-17 03:30 | 173 | 173
2019-12-17 04:00 | 168 | 167
2019-12-17 04:30 | 169 | 169
2019-12-17 05:00 | 170 | 170
2019-12-17 05:30 | 176 | 176
2019-12-17 06:00 | 180 | 180
2019-12-17 06:30 | 192 | 192
2019-12-17 07:00 | 200 | 199
2019-12-17 07:30 | 206 | 205
2019-12-17 08:00 | 208 | 208
2019-12-17 08:30 | 208 | 207
2019-12-17 09:00 | 208 | 207
2019-12-17 09:30 | 209 | 208
2019-12-17 10:00 | 211 | 211
2019-12-17 10:30 | 210 | 210
2019-12-17 11:00 | 206 | 206
2019-12-17 11:30 | 197 | 197
2019-12-17 12:00 | 197 | 197
2019-12-17 12:30 | 197 | 197
2019-12-17 13:00 | 199 | 199
2019-12-17 13:30 | 203 | 203
2019-12-17 14:00 | 210 | 210
2019-12-17 14:30 | 220 | 220
2019-12-17 15:00 | 228 | 228
2019-12-17 15:30 | 240 | 240
2019-12-17 16:00 | 253 | 253
2019-12-17 16:30 | 265 | 265
2019-12-17 17:00 | 279 | 279
2019-12-17 17:30 | 285 | 285
2019-12-17 18:00 | 286 | 285
2019-12-17 18:30 | 281 | 281
2019-12-17 19:00 | 284 | 284
2019-12-17 19:30 | 284 | 284
2019-12-17 20:00 | 281 | 281
2019-12-17 20:30 | 274 | 274
2019-12-17 21:00 | 261 | 261
2019-12-17 21:30 | 247 | 247
2019-12-17 22:00 | 235 | 234
2019-12-17 22:30 | 226 | 225
2019-12-17 23:00 | 219 | 219
2019-12-17 23:30 | 204 | 204
2019-12-18 | 188 | 188
2019-12-18 00:30 | 175 | 175
2019-12-18 01:00 | 169 | 169
2019-12-18 01:30 | 163 | 163
2019-12-18 02:00 | 159 | 159
2019-12-18 02:30 | 158 | 157
2019-12-18 03:00 | 157 | 157
2019-12-18 03:30 | 158 | 157
2019-12-18 04:00 | 157 | 157
2019-12-18 04:30 | 160 | 160
2019-12-18 05:00 | 163 | 163
2019-12-18 05:30 | 169 | 168
2019-12-18 06:00 | 173 | 173
2019-12-18 06:30 | 187 | 187
2019-12-18 07:00 | 194 | 194
2019-12-18 07:30 | 195 | 195
2019-12-18 08:00 | 196 | 196
2019-12-18 08:30 | 199 | 199
2019-12-18 09:00 | 192 | 192
2019-12-18 09:30 | 188 | 188
2019-12-18 10:00 | 186 | 186
2019-12-18 10:30 | 181 | 181
2019-12-18 11:00 | 175 | 175
2019-12-18 11:30 | 172 | 171
2019-12-18 12:00 | 174 | 174
2019-12-18 12:30 | 177 | 176
2019-12-18 13:00 | 183 | 182
2019-12-18 13:30 | 189 | 188
2019-12-18 14:00 | 198 | 196
2019-12-18 14:30 | 207 | 205
2019-12-18 15:00 | 217 | 216
2019-12-18 15:30 | 228 | 227
2019-12-18 16:00 | 242 | 241
2019-12-18 16:30 | 255 | 254
2019-12-18 17:00 | 267 | 266
2019-12-18 17:30 | 271 | 270
2019-12-18 18:00 | 270 | 270
2019-12-18 18:30 | 268 | 267
2019-12-18 19:00 | 278 | 277
2019-12-18 19:30 | 278 | 277
2019-12-18 20:00 | 272 | 272
2019-12-18 20:30 | 264 | 264
2019-12-18 21:00 | 251 | 250
2019-12-18 21:30 | 241 | 241
2019-12-18 22:00 | 230 | 229
2019-12-18 22:30 | 223 | 222
2019-12-18 23:00 | 217 | 217
2019-12-18 23:30 | 201 | 201
2019-12-19 | 185 | 185
2019-12-19 00:30 | 173 | 173
2019-12-19 01:00 | 166 | 166
2019-12-19 01:30 | 162 | 162
2019-12-19 02:00 | 158 | 157
2019-12-19 02:30 | 156 | 155
2019-12-19 03:00 | 154 | 154
2019-12-19 03:30 | 155 | 155
2019-12-19 04:00 | 155 | 154
2019-12-19 04:30 | 157 | 157
2019-12-19 05:00 | 159 | 159
2019-12-19 05:30 | 164 | 164
2019-12-19 06:00 | 168 | 168
2019-12-19 06:30 | 177 | 177
2019-12-19 07:00 | 181 | 181
2019-12-19 07:30 | 189 | 187
2019-12-19 08:00 | 186 | 185
2019-12-19 08:30 | 186 | 186
2019-12-19 09:00 | 190 | 190
2019-12-19 09:30 | 190 | 190
2019-12-19 10:00 | 189 | 189
2019-12-19 10:30 | 187 | 187
2019-12-19 11:00 | 185 | 185
2019-12-19 11:30 | 187 | 187
2019-12-19 12:00 | 191 | 191
2019-12-19 12:30 | 195 | 195
2019-12-19 13:00 | 201 | 201
2019-12-19 13:30 | 211 | 211
2019-12-19 14:00 | 218 | 218
2019-12-19 14:30 | 230 | 229
2019-12-19 15:00 | 241 | 241
2019-12-19 15:30 | 253 | 253
2019-12-19 16:00 | 271 | 270
2019-12-19 16:30 | 286 | 285
2019-12-19 17:00 | 297 | 297
2019-12-19 17:30 | 302 | 301
2019-12-19 18:00 | 302 | 302
2019-12-19 18:30 | 296 | 296
2019-12-19 19:00 | 299 | 298
2019-12-19 19:30 | 298 | 297
2019-12-19 20:00 | 293 | 292
2019-12-19 20:30 | 285 | 284
2019-12-19 21:00 | 272 | 272
2019-12-19 21:30 | 258 | 258
2019-12-19 22:00 | 246 | 246
2019-12-19 22:30 | 237 | 237
2019-12-19 23:00 | 229 | 229
2019-12-19 23:30 | 211 | 211
2019-12-20 | 193 | 193
2019-12-20 00:30 | 179 | 178
2019-12-20 01:00 | 171 | 171
2019-12-20 01:30 | 166 | 166
2019-12-20 02:00 | 163 | 163
2019-12-20 02:30 | 159 | 159
2019-12-20 03:00 | 157 | 157
2019-12-20 03:30 | 157 | 157
2019-12-20 04:00 | 157 | 157
2019-12-20 04:30 | 159 | 159
2019-12-20 05:00 | 162 | 162
2019-12-20 05:30 | 167 | 167
2019-12-20 06:00 | 170 | 170
2019-12-20 06:30 | 178 | 177
2019-12-20 07:00 | 186 | 186
2019-12-20 07:30 | 191 | 191
2019-12-20 08:00 | 191 | 190
2019-12-20 08:30 | 193 | 191
2019-12-20 09:00 | 192 | 192
2019-12-20 09:30 | 190 | 190
2019-12-20 10:00 | 193 | 193
2019-12-20 10:30 | 197 | 196
2019-12-20 11:00 | 205 | 204
2019-12-20 11:30 | 215 | 214
2019-12-20 12:00 | 224 | 223
2019-12-20 12:30 | 232 | 231
2019-12-20 13:00 | 243 | 242
2019-12-20 13:30 | 258 | 257
2019-12-20 14:00 | 268 | 267
2019-12-20 14:30 | 274 | 274
2019-12-20 15:00 | 278 | 278
2019-12-20 15:30 | 286 | 285
2019-12-20 16:00 | 295 | 295
2019-12-20 16:30 | 303 | 303
2019-12-20 17:00 | 309 | 309
2019-12-20 17:30 | 309 | 309
2019-12-20 18:00 | 305 | 305
2019-12-20 18:30 | 298 | 298
2019-12-20 19:00 | 300 | 300
2019-12-20 19:30 | 300 | 300
2019-12-20 20:00 | 297 | 297
2019-12-20 20:30 | 290 | 290
2019-12-20 21:00 | 278 | 278
2019-12-20 21:30 | 267 | 267
2019-12-20 22:00 | 257 | 257
2019-12-20 22:30 | 250 | 249
2019-12-20 23:00 | 240 | 240
2019-12-20 23:30 | 225 | 225
2019-12-21 | 208 | 208
2019-12-21 00:30 | 192 | 192
2019-12-21 01:00 | 185 | 184
2019-12-21 01:30 | 178 | 178
2019-12-21 02:00 | 173 | 173
2019-12-21 02:30 | 171 | 170
2019-12-21 03:00 | 169 | 168
2019-12-21 03:30 | 168 | 167
2019-12-21 04:00 | 167 | 166
2019-12-21 04:30 | 166 | 165
2019-12-21 05:00 | 165 | 163
2019-12-21 05:30 | 163 | 162
2019-12-21 06:00 | 161 | 160
2019-12-21 06:30 | 160 | 160
2019-12-21 07:00 | 161 | 161
2019-12-21 07:30 | 165 | 165
2019-12-21 08:00 | 169 | 169
2019-12-21 08:30 | 172 | 172
2019-12-21 09:00 | 169 | 169
2019-12-21 09:30 | 168 | 168
2019-12-21 10:00 | 169 | 169
2019-12-21 10:30 | 173 | 173
2019-12-21 11:00 | 179 | 178
2019-12-21 11:30 | 185 | 184
2019-12-21 12:00 | 192 | 192
2019-12-21 12:30 | 201 | 199
2019-12-21 13:00 | 210 | 210
2019-12-21 13:30 | 221 | 220
2019-12-21 14:00 | 233 | 231
2019-12-21 14:30 | 246 | 245
2019-12-21 15:00 | 258 | 257
2019-12-21 15:30 | 269 | 269
2019-12-21 16:00 | 282 | 281
2019-12-21 16:30 | 290 | 289
2019-12-21 17:00 | 302 | 301
2019-12-21 17:30 | 304 | 303
2019-12-21 18:00 | 302 | 301
2019-12-21 18:30 | 299 | 299
2019-12-21 19:00 | 299 | 298
2019-12-21 19:30 | 298 | 296
2019-12-21 20:00 | 293 | 292
2019-12-21 20:30 | 283 | 283
2019-12-21 21:00 | 269 | 269
2019-12-21 21:30 | 260 | 260
2019-12-21 22:00 | 247 | 247
2019-12-21 22:30 | 240 | 240
2019-12-21 23:00 | 234 | 234
2019-12-21 23:30 | 215 | 215
2019-12-22 | 199 | 198
2019-12-22 00:30 | 184 | 184
2019-12-22 01:00 | 176 | 176
2019-12-22 01:30 | 170 | 170
2019-12-22 02:00 | 167 | 167
2019-12-22 02:30 | 162 | 162
2019-12-22 03:00 | 159 | 158
2019-12-22 03:30 | 158 | 158
2019-12-22 04:00 | 157 | 157
2019-12-22 04:30 | 156 | 156
2019-12-22 05:00 | 154 | 154
2019-12-22 05:30 | 153 | 153
2019-12-22 06:00 | 152 | 152
2019-12-22 06:30 | 150 | 150
2019-12-22 07:00 | 152 | 152
2019-12-22 07:30 | 153 | 153
2019-12-22 08:00 | 156 | 155
2019-12-22 08:30 | 165 | 165
2019-12-22 09:00 | 168 | 168
2019-12-22 09:30 | 172 | 172
2019-12-22 10:00 | 176 | 176
2019-12-22 10:30 | 181 | 181
2019-12-22 11:00 | 184 | 184
2019-12-22 11:30 | 188 | 188
2019-12-22 12:00 | 197 | 196
2019-12-22 12:30 | 205 | 204
2019-12-22 13:00 | 214 | 213
2019-12-22 13:30 | 223 | 222
2019-12-22 14:00 | 230 | 230
2019-12-22 14:30 | 238 | 238
2019-12-22 15:00 | 248 | 247
2019-12-22 15:30 | 257 | 257
2019-12-22 16:00 | 267 | 267
2019-12-22 16:30 | 272 | 271
2019-12-22 17:00 | 278 | 277
2019-12-22 17:30 | 279 | 278
2019-12-22 18:00 | 279 | 279
2019-12-22 18:30 | 277 | 277
2019-12-22 19:00 | 280 | 280
2019-12-22 19:30 | 278 | 277
2019-12-22 20:00 | 276 | 275
2019-12-22 20:30 | 269 | 269
2019-12-22 21:00 | 258 | 258
2019-12-22 21:30 | 251 | 251
2019-12-22 22:00 | 242 | 242
2019-12-22 22:30 | 237 | 236
2019-12-22 23:00 | 229 | 229
2019-12-22 23:30 | 213 | 212
2019-12-23 | 199 | 199
2019-12-23 00:30 | 185 | 185
2019-12-23 01:00 | 177 | 177
2019-12-23 01:30 | 174 | 174
2019-12-23 02:00 | 167 | 167
2019-12-23 02:30 | 165 | 165
2019-12-23 03:00 | 163 | 163
2019-12-23 03:30 | 162 | 162
2019-12-23 04:00 | 162 | 162
2019-12-23 04:30 | 163 | 163
2019-12-23 05:00 | 166 | 166
2019-12-23 05:30 | 171 | 171
2019-12-23 06:00 | 178 | 178
2019-12-23 06:30 | 192 | 192
2019-12-23 07:00 | 203 | 203
2019-12-23 07:30 | 214 | 213
2019-12-23 08:00 | 219 | 218
2019-12-23 08:30 | 222 | 221
2019-12-23 09:00 | 221 | 219
2019-12-23 09:30 | 217 | 216
2019-12-23 10:00 | 215 | 214
2019-12-23 10:30 | 216 | 214
2019-12-23 11:00 | 214 | 212
2019-12-23 11:30 | 213 | 211
2019-12-23 12:00 | 215 | 212
2019-12-23 12:30 | 223 | 220
2019-12-23 13:00 | 228 | 226
2019-12-23 13:30 | 234 | 232
2019-12-23 14:00 | 244 | 243
2019-12-23 14:30 | 257 | 255
2019-12-23 15:00 | 272 | 269
2019-12-23 15:30 | 288 | 284
2019-12-23 16:00 | 295 | 293
2019-12-23 16:30 | 300 | 299
2019-12-23 17:00 | 308 | 307
2019-12-23 17:30 | 311 | 311
2019-12-23 18:00 | 312 | 312
2019-12-23 18:30 | 312 | 311
2019-12-23 19:00 | 315 | 315
2019-12-23 19:30 | 313 | 313
2019-12-23 20:00 | 310 | 310
2019-12-23 20:30 | 303 | 303
2019-12-23 21:00 | 292 | 292
2019-12-23 21:30 | 283 | 283
2019-12-23 22:00 | 274 | 274
2019-12-23 22:30 | 267 | 267
2019-12-23 23:00 | 260 | 260
2019-12-23 23:30 | 243 | 243
2019-12-24 | 223 | 223
2019-12-24 00:30 | 206 | 206
2019-12-24 01:00 | 197 | 197
2019-12-24 01:30 | 190 | 190
2019-12-24 02:00 | 187 | 187
2019-12-24 02:30 | 183 | 183
2019-12-24 03:00 | 182 | 182
2019-12-24 03:30 | 181 | 180
2019-12-24 04:00 | 180 | 179
2019-12-24 04:30 | 181 | 181
2019-12-24 05:00 | 184 | 183
2019-12-24 05:30 | 189 | 189
2019-12-24 06:00 | 193 | 193
2019-12-24 06:30 | 204 | 204
2019-12-24 07:00 | 216 | 216
2019-12-24 07:30 | 230 | 229
2019-12-24 08:00 | 236 | 236
2019-12-24 08:30 | 246 | 245
2019-12-24 09:00 | 254 | 254
2019-12-24 09:30 | 253 | 252
2019-12-24 10:00 | 255 | 255
2019-12-24 10:30 | 257 | 256
2019-12-24 11:00 | 270 | 270
2019-12-24 11:30 | 253 | 252
2019-12-24 12:00 | 240 | 240
2019-12-24 12:30 | 242 | 242
2019-12-24 13:00 | 252 | 252
2019-12-24 13:30 | 258 | 257
2019-12-24 14:00 | 259 | 258
2019-12-24 14:30 | 267 | 266
2019-12-24 15:00 | 270 | 269
2019-12-24 15:30 | 267 | 266
2019-12-24 16:00 | 283 | 282
2019-12-24 16:30 | 300 | 299
2019-12-24 17:00 | 304 | 303
2019-12-24 17:30 | 306 | 305
2019-12-24 18:00 | 303 | 302
2019-12-24 18:30 | 292 | 292
2019-12-24 19:00 | 290 | 289
2019-12-24 19:30 | 282 | 282
2019-12-24 20:00 | 269 | 269
2019-12-24 20:30 | 262 | 262
2019-12-24 21:00 | 250 | 248
2019-12-24 21:30 | 242 | 241
2019-12-24 22:00 | 236 | 236
2019-12-24 22:30 | 233 | 232
2019-12-24 23:00 | 228 | 227
2019-12-24 23:30 | 213 | 213
2019-12-25 | 196 | 196
2019-12-25 00:30 | 183 | 182
2019-12-25 01:00 | 173 | 173
2019-12-25 01:30 | 166 | 166
2019-12-25 02:00 | 159 | 159
2019-12-25 02:30 | 154 | 154
2019-12-25 03:00 | 153 | 152
2019-12-25 03:30 | 151 | 151
2019-12-25 04:00 | 149 | 149
2019-12-25 04:30 | 149 | 149
2019-12-25 05:00 | 149 | 149
2019-12-25 05:30 | 150 | 149
2019-12-25 06:00 | 151 | 150
2019-12-25 06:30 | 157 | 156
2019-12-25 07:00 | 165 | 165
2019-12-25 07:30 | 178 | 178
2019-12-25 08:00 | 180 | 180
2019-12-25 08:30 | 180 | 180
2019-12-25 09:00 | 177 | 177
2019-12-25 09:30 | 179 | 179
2019-12-25 10:00 | 188 | 188
2019-12-25 10:30 | 199 | 199
2019-12-25 11:00 | 195 | 194
2019-12-25 11:30 | 176 | 176
2019-12-25 12:00 | 170 | 170
2019-12-25 12:30 | 166 | 166
2019-12-25 13:00 | 150 | 150
2019-12-25 13:30 | 140 | 140
2019-12-25 14:00 | 147 | 147
2019-12-25 14:30 | 149 | 149
2019-12-25 15:00 | 142 | 142
2019-12-25 15:30 | 153 | 153
2019-12-25 16:00 | 161 | 161
2019-12-25 16:30 | 170 | 169
2019-12-25 17:00 | 183 | 182
2019-12-25 17:30 | 190 | 189
2019-12-25 18:00 | 193 | 193
2019-12-25 18:30 | 197 | 197
2019-12-25 19:00 | 204 | 204
2019-12-25 19:30 | 210 | 209
2019-12-25 20:00 | 213 | 213
2019-12-25 20:30 | 213 | 212
2019-12-25 21:00 | 207 | 207
2019-12-25 21:30 | 204 | 203
2019-12-25 22:00 | 200 | 200
2019-12-25 22:30 | 199 | 199
2019-12-25 23:00 | 200 | 200
2019-12-25 23:30 | 192 | 192
2019-12-26 | 178 | 178
2019-12-26 00:30 | 167 | 167
2019-12-26 01:00 | 160 | 160
2019-12-26 01:30 | 154 | 154
2019-12-26 02:00 | 152 | 151
2019-12-26 02:30 | 150 | 150
2019-12-26 03:00 | 149 | 149
2019-12-26 03:30 | 148 | 148
2019-12-26 04:00 | 147 | 147
2019-12-26 04:30 | 147 | 147
2019-12-26 05:00 | 145 | 145
2019-12-26 05:30 | 144 | 144
2019-12-26 06:00 | 143 | 143
2019-12-26 06:30 | 144 | 143
2019-12-26 07:00 | 143 | 143
2019-12-26 07:30 | 149 | 149
2019-12-26 08:00 | 158 | 158
2019-12-26 08:30 | 166 | 166
2019-12-26 09:00 | 176 | 176
2019-12-26 09:30 | 179 | 179
2019-12-26 10:00 | 173 | 172
2019-12-26 10:30 | 165 | 164
2019-12-26 11:00 | 142 | 142
2019-12-26 11:30 | 129 | 129
2019-12-26 12:00 | 127 | 127
2019-12-26 12:30 | 131 | 130
2019-12-26 13:00 | 134 | 134
2019-12-26 13:30 | 140 | 139
2019-12-26 14:00 | 145 | 144
2019-12-26 14:30 | 149 | 148
2019-12-26 15:00 | 156 | 155
2019-12-26 15:30 | 166 | 165
2019-12-26 16:00 | 178 | 177
2019-12-26 16:30 | 191 | 189
2019-12-26 17:00 | 207 | 206
2019-12-26 17:30 | 219 | 218
2019-12-26 18:00 | 224 | 224
2019-12-26 18:30 | 224 | 224
2019-12-26 19:00 | 229 | 228
2019-12-26 19:30 | 233 | 232
2019-12-26 20:00 | 234 | 233
2019-12-26 20:30 | 230 | 230
2019-12-26 21:00 | 220 | 219
2019-12-26 21:30 | 214 | 214
2019-12-26 22:00 | 214 | 214
2019-12-26 22:30 | 210 | 210
2019-12-26 23:00 | 207 | 207
2019-12-26 23:30 | 195 | 195
2019-12-27 | 180 | 180
2019-12-27 00:30 | 168 | 168
2019-12-27 01:00 | 162 | 162
2019-12-27 01:30 | 157 | 157
2019-12-27 02:00 | 153 | 153
2019-12-27 02:30 | 151 | 151
2019-12-27 03:00 | 150 | 150
2019-12-27 03:30 | 149 | 149
2019-12-27 04:00 | 149 | 148
2019-12-27 04:30 | 150 | 150
2019-12-27 05:00 | 151 | 151
2019-12-27 05:30 | 153 | 152
2019-12-27 06:00 | 152 | 152
2019-12-27 06:30 | 156 | 156
2019-12-27 07:00 | 158 | 158
2019-12-27 07:30 | 159 | 159
2019-12-27 08:00 | 157 | 157
2019-12-27 08:30 | 170 | 169
2019-12-27 09:00 | 179 | 178
2019-12-27 09:30 | 179 | 177
2019-12-27 10:00 | 173 | 171
2019-12-27 10:30 | 175 | 173
2019-12-27 11:00 | 173 | 172
2019-12-27 11:30 | 168 | 166
2019-12-27 12:00 | 164 | 163
2019-12-27 12:30 | 161 | 160
2019-12-27 13:00 | 167 | 165
2019-12-27 13:30 | 166 | 164
2019-12-27 14:00 | 168 | 166
2019-12-27 14:30 | 170 | 168
2019-12-27 15:00 | 176 | 174
2019-12-27 15:30 | 188 | 186
2019-12-27 16:00 | 201 | 199
2019-12-27 16:30 | 215 | 213
2019-12-27 17:00 | 231 | 228
2019-12-27 17:30 | 238 | 238
2019-12-27 18:00 | 240 | 239
2019-12-27 18:30 | 240 | 240
2019-12-27 19:00 | 246 | 246
2019-12-27 19:30 | 248 | 248
2019-12-27 20:00 | 246 | 246
2019-12-27 20:30 | 242 | 242
2019-12-27 21:00 | 230 | 230
2019-12-27 21:30 | 223 | 222
2019-12-27 22:00 | 214 | 213
2019-12-27 22:30 | 209 | 209
2019-12-27 23:00 | 206 | 206
2019-12-27 23:30 | 193 | 193
2019-12-28 | 178 | 178
2019-12-28 00:30 | 166 | 166
2019-12-28 01:00 | 160 | 159
2019-12-28 01:30 | 154 | 154
2019-12-28 02:00 | 149 | 149
2019-12-28 02:30 | 147 | 147
2019-12-28 03:00 | 145 | 145
2019-12-28 03:30 | 144 | 144
2019-12-28 04:00 | 144 | 144
2019-12-28 04:30 | 145 | 145
2019-12-28 05:00 | 144 | 144
2019-12-28 05:30 | 145 | 145
2019-12-28 06:00 | 148 | 148
2019-12-28 06:30 | 148 | 148
2019-12-28 07:00 | 147 | 147
2019-12-28 07:30 | 153 | 153
2019-12-28 08:00 | 159 | 159
2019-12-28 08:30 | 159 | 158
2019-12-28 09:00 | 160 | 159
2019-12-28 09:30 | 162 | 161
2019-12-28 10:00 | 151 | 150
2019-12-28 10:30 | 144 | 142
2019-12-28 11:00 | 133 | 131
2019-12-28 11:30 | 130 | 128
2019-12-28 12:00 | 133 | 131
2019-12-28 12:30 | 135 | 133
2019-12-28 13:00 | 144 | 142
2019-12-28 13:30 | 148 | 147
2019-12-28 14:00 | 150 | 149
2019-12-28 14:30 | 157 | 156
2019-12-28 15:00 | 165 | 164
2019-12-28 15:30 | 176 | 175
2019-12-28 16:00 | 191 | 190
2019-12-28 16:30 | 202 | 201
2019-12-28 17:00 | 218 | 217
2019-12-28 17:30 | 225 | 224
2019-12-28 18:00 | 229 | 228
2019-12-28 18:30 | 236 | 234
2019-12-28 19:00 | 243 | 241
2019-12-28 19:30 | 247 | 245
2019-12-28 20:00 | 247 | 245
2019-12-28 20:30 | 243 | 241
2019-12-28 21:00 | 233 | 232
2019-12-28 21:30 | 226 | 225
2019-12-28 22:00 | 217 | 217
2019-12-28 22:30 | 214 | 214
2019-12-28 23:00 | 210 | 210
2019-12-28 23:30 | 198 | 198
2019-12-29 | 182 | 182
2019-12-29 00:30 | 170 | 170
2019-12-29 01:00 | 163 | 163
2019-12-29 01:30 | 158 | 158
2019-12-29 02:00 | 154 | 154
2019-12-29 02:30 | 151 | 150
2019-12-29 03:00 | 148 | 148
2019-12-29 03:30 | 147 | 147
2019-12-29 04:00 | 146 | 146
2019-12-29 04:30 | 146 | 146
2019-12-29 05:00 | 144 | 144
2019-12-29 05:30 | 143 | 143
2019-12-29 06:00 | 140 | 140
2019-12-29 06:30 | 139 | 139
2019-12-29 07:00 | 135 | 135
2019-12-29 07:30 | 132 | 132
2019-12-29 08:00 | 133 | 133
2019-12-29 08:30 | 132 | 131
2019-12-29 09:00 | 127 | 126
2019-12-29 09:30 | 124 | 123
2019-12-29 10:00 | 121 | 120
2019-12-29 10:30 | 120 | 119
2019-12-29 11:00 | 118 | 117
2019-12-29 11:30 | 118 | 117
2019-12-29 12:00 | 120 | 119
2019-12-29 12:30 | 124 | 122
2019-12-29 13:00 | 130 | 128
2019-12-29 13:30 | 138 | 136
2019-12-29 14:00 | 147 | 145
2019-12-29 14:30 | 159 | 157
2019-12-29 15:00 | 171 | 170
2019-12-29 15:30 | 181 | 179
2019-12-29 16:00 | 197 | 195
2019-12-29 16:30 | 214 | 212
2019-12-29 17:00 | 231 | 229
2019-12-29 17:30 | 241 | 241
2019-12-29 18:00 | 246 | 246
2019-12-29 18:30 | 249 | 249
2019-12-29 19:00 | 252 | 252
2019-12-29 19:30 | 253 | 253
2019-12-29 20:00 | 252 | 252
2019-12-29 20:30 | 244 | 243
2019-12-29 21:00 | 234 | 232
2019-12-29 21:30 | 226 | 225
2019-12-29 22:00 | 220 | 220
2019-12-29 22:30 | 216 | 216
2019-12-29 23:00 | 211 | 211
2019-12-29 23:30 | 197 | 197
2019-12-30 | 181 | 181
2019-12-30 00:30 | 170 | 170
2019-12-30 01:00 | 163 | 163
2019-12-30 01:30 | 158 | 158
2019-12-30 02:00 | 156 | 155
2019-12-30 02:30 | 154 | 154
2019-12-30 03:00 | 152 | 152
2019-12-30 03:30 | 151 | 151
2019-12-30 04:00 | 151 | 150
2019-12-30 04:30 | 153 | 152
2019-12-30 05:00 | 153 | 152
2019-12-30 05:30 | 155 | 155
2019-12-30 06:00 | 157 | 157
2019-12-30 06:30 | 162 | 162
2019-12-30 07:00 | 165 | 165
2019-12-30 07:30 | 167 | 166
2019-12-30 08:00 | 171 | 170
2019-12-30 08:30 | 177 | 176
2019-12-30 09:00 | 178 | 177
2019-12-30 09:30 | 178 | 178
2019-12-30 10:00 | 182 | 182
2019-12-30 10:30 | 187 | 187
2019-12-30 11:00 | 184 | 184
2019-12-30 11:30 | 173 | 173
2019-12-30 12:00 | 171 | 171
2019-12-30 12:30 | 173 | 173
2019-12-30 13:00 | 174 | 174
2019-12-30 13:30 | 179 | 179
2019-12-30 14:00 | 187 | 187
2019-12-30 14:30 | 198 | 198
2019-12-30 15:00 | 209 | 209
2019-12-30 15:30 | 225 | 225
2019-12-30 16:00 | 243 | 242
2019-12-30 16:30 | 259 | 258
2019-12-30 17:00 | 278 | 276
2019-12-30 17:30 | 285 | 284
2019-12-30 18:00 | 285 | 284
2019-12-30 18:30 | 284 | 283
2019-12-30 19:00 | 290 | 289
2019-12-30 19:30 | 291 | 290
2019-12-30 20:00 | 288 | 287
2019-12-30 20:30 | 281 | 279
2019-12-30 21:00 | 269 | 265
2019-12-30 21:30 | 258 | 254
2019-12-30 22:00 | 246 | 243
2019-12-30 22:30 | 238 | 236
2019-12-30 23:00 | 229 | 228
2019-12-30 23:30 | 211 | 210
2019-12-31 | 195 | 194
2019-12-31 00:30 | 180 | 180
2019-12-31 01:00 | 172 | 172
2019-12-31 01:30 | 167 | 167
2019-12-31 02:00 | 164 | 164
2019-12-31 02:30 | 162 | 162
2019-12-31 03:00 | 159 | 159
2019-12-31 03:30 | 158 | 158
2019-12-31 04:00 | 158 | 158
2019-12-31 04:30 | 160 | 160
2019-12-31 05:00 | 159 | 159
2019-12-31 05:30 | 160 | 160
2019-12-31 06:00 | 162 | 162
2019-12-31 06:30 | 167 | 167
2019-12-31 07:00 | 171 | 171
2019-12-31 07:30 | 182 | 182
2019-12-31 08:00 | 191 | 191
2019-12-31 08:30 | 188 | 187
2019-12-31 09:00 | 189 | 189
2019-12-31 09:30 | 196 | 196
2019-12-31 10:00 | 197 | 197
2019-12-31 10:30 | 196 | 196
2019-12-31 11:00 | 199 | 199
2019-12-31 11:30 | 207 | 206
2019-12-31 12:00 | 201 | 201
2019-12-31 12:30 | 194 | 194
2019-12-31 13:00 | 196 | 195
2019-12-31 13:30 | 200 | 200
2019-12-31 14:00 | 210 | 210
2019-12-31 14:30 | 219 | 219
2019-12-31 15:00 | 226 | 225
2019-12-31 15:30 | 234 | 233
2019-12-31 16:00 | 245 | 244
2019-12-31 16:30 | 257 | 256
2019-12-31 17:00 | 268 | 268
2019-12-31 17:30 | 273 | 273
2019-12-31 18:00 | 269 | 269
2019-12-31 18:30 | 262 | 261
2019-12-31 19:00 | 260 | 259
2019-12-31 19:30 | 257 | 257
2019-12-31 20:00 | 253 | 253
2019-12-31 20:30 | 245 | 244
2019-12-31 21:00 | 233 | 232
2019-12-31 21:30 | 225 | 224
2019-12-31 22:00 | 219 | 218
2019-12-31 22:30 | 216 | 216
2019-12-31 23:00 | 214 | 214
2019-12-31 23:30 | 201 | 201
2020-01-01 | 187 | 187
2020-01-01 00:30 | 176 | 176
2020-01-01 01:00 | 170 | 170
2020-01-01 01:30 | 166 | 166
2020-01-01 02:00 | 162 | 162
2020-01-01 02:30 | 158 | 158
2020-01-01 03:00 | 156 | 156
2020-01-01 03:30 | 157 | 157
2020-01-01 04:00 | 155 | 155
2020-01-01 04:30 | 153 | 153
2020-01-01 05:00 | 151 | 151
2020-01-01 05:30 | 148 | 148
2020-01-01 06:00 | 142 | 142
2020-01-01 06:30 | 142 | 141
2020-01-01 07:00 | 140 | 140
2020-01-01 07:30 | 139 | 139
2020-01-01 08:00 | 141 | 141
2020-01-01 08:30 | 144 | 144
2020-01-01 09:00 | 143 | 143
2020-01-01 09:30 | 143 | 143
2020-01-01 10:00 | 144 | 144
2020-01-01 10:30 | 143 | 143
2020-01-01 11:00 | 143 | 143
2020-01-01 11:30 | 145 | 145
2020-01-01 12:00 | 152 | 152
2020-01-01 12:30 | 160 | 160
2020-01-01 13:00 | 168 | 168
2020-01-01 13:30 | 177 | 177
2020-01-01 14:00 | 187 | 187
2020-01-01 14:30 | 198 | 198
2020-01-01 15:00 | 211 | 210
2020-01-01 15:30 | 223 | 222
2020-01-01 16:00 | 239 | 238
2020-01-01 16:30 | 254 | 254
2020-01-01 17:00 | 273 | 271
2020-01-01 17:30 | 283 | 282
2020-01-01 18:00 | 287 | 285
2020-01-01 18:30 | 286 | 285
2020-01-01 19:00 | 287 | 286
2020-01-01 19:30 | 286 | 285
2020-01-01 20:00 | 284 | 283
2020-01-01 20:30 | 275 | 275
2020-01-01 21:00 | 263 | 262
2020-01-01 21:30 | 253 | 253
2020-01-01 22:00 | 240 | 240
2020-01-01 22:30 | 234 | 234
2020-01-01 23:00 | 227 | 227
2020-01-01 23:30 | 212 | 212
2020-01-02 | 196 | 196
2020-01-02 00:30 | 184 | 182
2020-01-02 01:00 | 177 | 175
2020-01-02 01:30 | 172 | 169
2020-01-02 02:00 | 168 | 165
2020-01-02 02:30 | 166 | 163
2020-01-02 03:00 | 164 | 160
2020-01-02 03:30 | 163 | 159
2020-01-02 04:00 | 162 | 158
2020-01-02 04:30 | 164 | 160
2020-01-02 05:00 | 165 | 162
2020-01-02 05:30 | 169 | 165
2020-01-02 06:00 | 171 | 168
2020-01-02 06:30 | 177 | 175
2020-01-02 07:00 | 180 | 180
2020-01-02 07:30 | 191 | 190
2020-01-02 08:00 | 199 | 198
2020-01-02 08:30 | 204 | 202
2020-01-02 09:00 | 206 | 204
2020-01-02 09:30 | 211 | 208
2020-01-02 10:00 | 211 | 208
2020-01-02 10:30 | 211 | 208
2020-01-02 11:00 | 214 | 211
2020-01-02 11:30 | 216 | 215
2020-01-02 12:00 | 218 | 217
2020-01-02 12:30 | 223 | 221
2020-01-02 13:00 | 229 | 227
2020-01-02 13:30 | 235 | 234
2020-01-02 14:00 | 244 | 243
2020-01-02 14:30 | 255 | 253
2020-01-02 15:00 | 267 | 266
2020-01-02 15:30 | 280 | 279
2020-01-02 16:00 | 295 | 293
2020-01-02 16:30 | 309 | 307
2020-01-02 17:00 | 323 | 323
2020-01-02 17:30 | 329 | 329
2020-01-02 18:00 | 330 | 330
2020-01-02 18:30 | 323 | 323
2020-01-02 19:00 | 318 | 318
2020-01-02 19:30 | 319 | 319
2020-01-02 20:00 | 315 | 315
2020-01-02 20:30 | 305 | 305
2020-01-02 21:00 | 288 | 288
2020-01-02 21:30 | 272 | 272
2020-01-02 22:00 | 258 | 258
2020-01-02 22:30 | 249 | 249
2020-01-02 23:00 | 241 | 241
2020-01-02 23:30 | 225 | 223
2020-01-03 | 205 | 204
2020-01-03 00:30 | 189 | 189
2020-01-03 01:00 | 181 | 181
2020-01-03 01:30 | 176 | 175
2020-01-03 02:00 | 172 | 171
2020-01-03 02:30 | 169 | 168
2020-01-03 03:00 | 167 | 166
2020-01-03 03:30 | 167 | 165
2020-01-03 04:00 | 166 | 164
2020-01-03 04:30 | 167 | 165
2020-01-03 05:00 | 167 | 166
2020-01-03 05:30 | 168 | 167
2020-01-03 06:00 | 169 | 169
2020-01-03 06:30 | 177 | 176
2020-01-03 07:00 | 181 | 181
2020-01-03 07:30 | 188 | 188
2020-01-03 08:00 | 196 | 196
2020-01-03 08:30 | 201 | 201
2020-01-03 09:00 | 202 | 202
2020-01-03 09:30 | 200 | 200
2020-01-03 10:00 | 200 | 199
2020-01-03 10:30 | 204 | 203
2020-01-03 11:00 | 205 | 203
2020-01-03 11:30 | 203 | 202
2020-01-03 12:00 | 210 | 208
2020-01-03 12:30 | 218 | 214
2020-01-03 13:00 | 223 | 219
2020-01-03 13:30 | 232 | 227
2020-01-03 14:00 | 239 | 234
2020-01-03 14:30 | 250 | 245
2020-01-03 15:00 | 263 | 257
2020-01-03 15:30 | 277 | 271
2020-01-03 16:00 | 290 | 288
2020-01-03 16:30 | 303 | 302
2020-01-03 17:00 | 316 | 314
2020-01-03 17:30 | 319 | 318
2020-01-03 18:00 | 316 | 315
2020-01-03 18:30 | 307 | 307
2020-01-03 19:00 | 306 | 305
2020-01-03 19:30 | 303 | 303
2020-01-03 20:00 | 300 | 300
2020-01-03 20:30 | 291 | 291
2020-01-03 21:00 | 277 | 277
2020-01-03 21:30 | 267 | 267
2020-01-03 22:00 | 255 | 255
2020-01-03 22:30 | 248 | 248
2020-01-03 23:00 | 240 | 240
2020-01-03 23:30 | 222 | 222
2020-01-04 | 204 | 203
2020-01-04 00:30 | 190 | 190
2020-01-04 01:00 | 182 | 182
2020-01-04 01:30 | 176 | 176
2020-01-04 02:00 | 170 | 170
2020-01-04 02:30 | 167 | 167
2020-01-04 03:00 | 165 | 165
2020-01-04 03:30 | 164 | 163
2020-01-04 04:00 | 162 | 162
2020-01-04 04:30 | 162 | 162
2020-01-04 05:00 | 160 | 160
2020-01-04 05:30 | 158 | 158
2020-01-04 06:00 | 155 | 155
2020-01-04 06:30 | 155 | 155
2020-01-04 07:00 | 153 | 153
2020-01-04 07:30 | 154 | 154
2020-01-04 08:00 | 157 | 157
2020-01-04 08:30 | 163 | 163
2020-01-04 09:00 | 160 | 160
2020-01-04 09:30 | 159 | 159
2020-01-04 10:00 | 159 | 158
2020-01-04 10:30 | 162 | 162
2020-01-04 11:00 | 165 | 165
2020-01-04 11:30 | 171 | 171
2020-01-04 12:00 | 178 | 178
2020-01-04 12:30 | 185 | 185
2020-01-04 13:00 | 194 | 194
2020-01-04 13:30 | 204 | 203
2020-01-04 14:00 | 214 | 214
2020-01-04 14:30 | 226 | 225
2020-01-04 15:00 | 238 | 237
2020-01-04 15:30 | 250 | 249
2020-01-04 16:00 | 262 | 261
2020-01-04 16:30 | 284 | 283
2020-01-04 17:00 | 298 | 296
2020-01-04 17:30 | 291 | 290
2020-01-04 18:00 | 289 | 289
2020-01-04 18:30 | 292 | 290
2020-01-04 19:00 | 295 | 293
2020-01-04 19:30 | 288 | 287
2020-01-04 20:00 | 283 | 282
2020-01-04 20:30 | 281 | 280
2020-01-04 21:00 | 269 | 268
2020-01-04 21:30 | 259 | 257
2020-01-04 22:00 | 248 | 247
2020-01-04 22:30 | 242 | 241
2020-01-04 23:00 | 234 | 233
2020-01-04 23:30 | 216 | 216
2020-01-05 | 198 | 198
2020-01-05 00:30 | 184 | 184
2020-01-05 01:00 | 177 | 176
2020-01-05 01:30 | 172 | 172
2020-01-05 02:00 | 167 | 166
2020-01-05 02:30 | 164 | 163
2020-01-05 03:00 | 160 | 159
2020-01-05 03:30 | 158 | 157
2020-01-05 04:00 | 156 | 155
2020-01-05 04:30 | 155 | 154
2020-01-05 05:00 | 153 | 152
2020-01-05 05:30 | 152 | 150
2020-01-05 06:00 | 148 | 146
2020-01-05 06:30 | 145 | 143
2020-01-05 07:00 | 143 | 141
2020-01-05 07:30 | 150 | 149
2020-01-05 08:00 | 147 | 147
2020-01-05 08:30 | 149 | 149
2020-01-05 09:00 | 153 | 153
2020-01-05 09:30 | 155 | 155
2020-01-05 10:00 | 156 | 156
2020-01-05 10:30 | 158 | 157
2020-01-05 11:00 | 161 | 160
2020-01-05 11:30 | 166 | 166
2020-01-05 12:00 | 176 | 175
2020-01-05 12:30 | 186 | 185
2020-01-05 13:00 | 198 | 197
2020-01-05 13:30 | 210 | 209
2020-01-05 14:00 | 223 | 221
2020-01-05 14:30 | 234 | 232
2020-01-05 15:00 | 243 | 242
2020-01-05 15:30 | 255 | 254
2020-01-05 16:00 | 268 | 266
2020-01-05 16:30 | 278 | 277
2020-01-05 17:00 | 291 | 291
2020-01-05 17:30 | 295 | 295
2020-01-05 18:00 | 296 | 296
2020-01-05 18:30 | 296 | 296
2020-01-05 19:00 | 296 | 296
2020-01-05 19:30 | 295 | 295
2020-01-05 20:00 | 290 | 290
2020-01-05 20:30 | 283 | 283
2020-01-05 21:00 | 270 | 270
2020-01-05 21:30 | 260 | 259
2020-01-05 22:00 | 248 | 247
2020-01-05 22:30 | 241 | 240
2020-01-05 23:00 | 235 | 233
2020-01-05 23:30 | 219 | 217
2020-01-06 | 202 | 200
2020-01-06 00:30 | 185 | 185
2020-01-06 01:00 | 177 | 177
2020-01-06 01:30 | 173 | 173
2020-01-06 02:00 | 169 | 169
2020-01-06 02:30 | 166 | 166
2020-01-06 03:00 | 163 | 162
2020-01-06 03:30 | 163 | 162
2020-01-06 04:00 | 163 | 163
2020-01-06 04:30 | 165 | 165
2020-01-06 05:00 | 168 | 168
2020-01-06 05:30 | 175 | 175
2020-01-06 06:00 | 180 | 180
2020-01-06 06:30 | 192 | 192
2020-01-06 07:00 | 202 | 201
2020-01-06 07:30 | 214 | 214
2020-01-06 08:00 | 216 | 216
2020-01-06 08:30 | 223 | 223
2020-01-06 09:00 | 228 | 228
2020-01-06 09:30 | 229 | 229
2020-01-06 10:00 | 231 | 230
2020-01-06 10:30 | 238 | 237
2020-01-06 11:00 | 244 | 243
2020-01-06 11:30 | 249 | 247
2020-01-06 12:00 | 250 | 250
2020-01-06 12:30 | 262 | 261
2020-01-06 13:00 | 271 | 271
2020-01-06 13:30 | 276 | 276
2020-01-06 14:00 | 282 | 282
2020-01-06 14:30 | 290 | 289
2020-01-06 15:00 | 298 | 297
2020-01-06 15:30 | 306 | 305
2020-01-06 16:00 | 315 | 314
2020-01-06 16:30 | 327 | 325
2020-01-06 17:00 | 333 | 332
2020-01-06 17:30 | 331 | 330
2020-01-06 18:00 | 325 | 325
2020-01-06 18:30 | 317 | 317
2020-01-06 19:00 | 322 | 322
2020-01-06 19:30 | 323 | 322
2020-01-06 20:00 | 317 | 317
2020-01-06 20:30 | 307 | 307
2020-01-06 21:00 | 292 | 292
2020-01-06 21:30 | 281 | 280
2020-01-06 22:00 | 268 | 267
2020-01-06 22:30 | 259 | 258
2020-01-06 23:00 | 251 | 250
2020-01-06 23:30 | 234 | 233
2020-01-07 | 218 | 215
2020-01-07 00:30 | 200 | 199
2020-01-07 01:00 | 189 | 189
2020-01-07 01:30 | 184 | 184
2020-01-07 02:00 | 180 | 180
2020-01-07 02:30 | 179 | 179
2020-01-07 03:00 | 177 | 177
2020-01-07 03:30 | 178 | 177
2020-01-07 04:00 | 172 | 171
2020-01-07 04:30 | 178 | 177
2020-01-07 05:00 | 182 | 182
2020-01-07 05:30 | 187 | 187
2020-01-07 06:00 | 191 | 191
2020-01-07 06:30 | 204 | 204
2020-01-07 07:00 | 216 | 216
2020-01-07 07:30 | 234 | 234
2020-01-07 08:00 | 248 | 247
2020-01-07 08:30 | 255 | 253
2020-01-07 09:00 | 254 | 252
2020-01-07 09:30 | 255 | 253
2020-01-07 10:00 | 253 | 252
2020-01-07 10:30 | 262 | 260
2020-01-07 11:00 | 269 | 266
2020-01-07 11:30 | 265 | 263
2020-01-07 12:00 | 262 | 260
2020-01-07 12:30 | 257 | 255
2020-01-07 13:00 | 255 | 252
2020-01-07 13:30 | 258 | 257
2020-01-07 14:00 | 267 | 266
2020-01-07 14:30 | 278 | 277
2020-01-07 15:00 | 281 | 280
2020-01-07 15:30 | 285 | 284
2020-01-07 16:00 | 294 | 294
2020-01-07 16:30 | 306 | 306
2020-01-07 17:00 | 322 | 321
2020-01-07 17:30 | 327 | 327
2020-01-07 18:00 | 327 | 326
2020-01-07 18:30 | 323 | 322
2020-01-07 19:00 | 324 | 322
2020-01-07 19:30 | 322 | 320
2020-01-07 20:00 | 319 | 314
2020-01-07 20:30 | 308 | 304
2020-01-07 21:00 | 291 | 288
2020-01-07 21:30 | 276 | 274
2020-01-07 22:00 | 261 | 259
2020-01-07 22:30 | 250 | 249
2020-01-07 23:00 | 240 | 239
2020-01-07 23:30 | 224 | 223
2020-01-08 | 205 | 205
2020-01-08 00:30 | 192 | 191
2020-01-08 01:00 | 182 | 182
2020-01-08 01:30 | 177 | 177
2020-01-08 02:00 | 173 | 173
2020-01-08 02:30 | 171 | 171
2020-01-08 03:00 | 169 | 169
2020-01-08 03:30 | 168 | 168
2020-01-08 04:00 | 168 | 168
2020-01-08 04:30 | 171 | 170
2020-01-08 05:00 | 175 | 174
2020-01-08 05:30 | 181 | 180
2020-01-08 06:00 | 186 | 186
2020-01-08 06:30 | 198 | 196
2020-01-08 07:00 | 205 | 204
2020-01-08 07:30 | 213 | 212
2020-01-08 08:00 | 220 | 220
2020-01-08 08:30 | 229 | 229
2020-01-08 09:00 | 228 | 228
2020-01-08 09:30 | 231 | 231
2020-01-08 10:00 | 233 | 232
2020-01-08 10:30 | 237 | 236
2020-01-08 11:00 | 238 | 238
2020-01-08 11:30 | 240 | 240
2020-01-08 12:00 | 243 | 243
2020-01-08 12:30 | 249 | 249
2020-01-08 13:00 | 256 | 256
2020-01-08 13:30 | 262 | 262
2020-01-08 14:00 | 271 | 270
2020-01-08 14:30 | 280 | 280
2020-01-08 15:00 | 292 | 291
2020-01-08 15:30 | 309 | 307
2020-01-08 16:00 | 321 | 320
2020-01-08 16:30 | 334 | 332
2020-01-08 17:00 | 346 | 344
2020-01-08 17:30 | 348 | 346
2020-01-08 18:00 | 344 | 343
2020-01-08 18:30 | 336 | 335
2020-01-08 19:00 | 337 | 336
2020-01-08 19:30 | 333 | 332
2020-01-08 20:00 | 327 | 326
2020-01-08 20:30 | 316 | 316
2020-01-08 21:00 | 300 | 300
2020-01-08 21:30 | 285 | 284
2020-01-08 22:00 | 269 | 269
2020-01-08 22:30 | 258 | 256
2020-01-08 23:00 | 247 | 246
2020-01-08 23:30 | 230 | 229
2020-01-09 | 212 | 211
2020-01-09 00:30 | 197 | 196
2020-01-09 01:00 | 188 | 187
2020-01-09 01:30 | 181 | 181
2020-01-09 02:00 | 177 | 177
2020-01-09 02:30 | 176 | 176
2020-01-09 03:00 | 173 | 172
2020-01-09 03:30 | 174 | 174
2020-01-09 04:00 | 173 | 172
2020-01-09 04:30 | 175 | 174
2020-01-09 05:00 | 178 | 178
2020-01-09 05:30 | 183 | 183
2020-01-09 06:00 | 190 | 189
2020-01-09 06:30 | 203 | 201
2020-01-09 07:00 | 212 | 212
2020-01-09 07:30 | 221 | 221
2020-01-09 08:00 | 226 | 226
2020-01-09 08:30 | 234 | 234
2020-01-09 09:00 | 238 | 238
2020-01-09 09:30 | 241 | 240
2020-01-09 10:00 | 239 | 238
2020-01-09 10:30 | 235 | 234
2020-01-09 11:00 | 239 | 238
2020-01-09 11:30 | 245 | 243
2020-01-09 12:00 | 249 | 247
2020-01-09 12:30 | 254 | 252
2020-01-09 13:00 | 263 | 260
2020-01-09 13:30 | 271 | 268
2020-01-09 14:00 | 279 | 276
2020-01-09 14:30 | 289 | 286
2020-01-09 15:00 | 298 | 295
2020-01-09 15:30 | 310 | 306
2020-01-09 16:00 | 328 | 325
2020-01-09 16:30 | 350 | 350
2020-01-09 17:00 | 352 | 352
2020-01-09 17:30 | 349 | 349
2020-01-09 18:00 | 344 | 344
2020-01-09 18:30 | 339 | 338
2020-01-09 19:00 | 340 | 338
2020-01-09 19:30 | 337 | 335
2020-01-09 20:00 | 331 | 331
2020-01-09 20:30 | 322 | 322
2020-01-09 21:00 | 307 | 306
2020-01-09 21:30 | 293 | 293
2020-01-09 22:00 | 279 | 279
2020-01-09 22:30 | 270 | 270
2020-01-09 23:00 | 260 | 260
2020-01-09 23:30 | 239 | 238
2020-01-10 | 222 | 221
2020-01-10 00:30 | 209 | 208
2020-01-10 01:00 | 200 | 200
2020-01-10 01:30 | 195 | 195
2020-01-10 02:00 | 190 | 190
2020-01-10 02:30 | 187 | 187
2020-01-10 03:00 | 186 | 186
2020-01-10 03:30 | 184 | 184
2020-01-10 04:00 | 184 | 184
2020-01-10 04:30 | 185 | 185
2020-01-10 05:00 | 188 | 188
2020-01-10 05:30 | 194 | 194
2020-01-10 06:00 | 199 | 199
2020-01-10 06:30 | 211 | 211
2020-01-10 07:00 | 221 | 220
2020-01-10 07:30 | 236 | 236
2020-01-10 08:00 | 244 | 243
2020-01-10 08:30 | 257 | 257
2020-01-10 09:00 | 258 | 258
2020-01-10 09:30 | 257 | 256
2020-01-10 10:00 | 252 | 251
2020-01-10 10:30 | 250 | 250
2020-01-10 11:00 | 246 | 246
2020-01-10 11:30 | 250 | 250
2020-01-10 12:00 | 254 | 254
2020-01-10 12:30 | 260 | 260
2020-01-10 13:00 | 268 | 268
2020-01-10 13:30 | 274 | 274
2020-01-10 14:00 | 283 | 283
2020-01-10 14:30 | 295 | 295
2020-01-10 15:00 | 305 | 305
2020-01-10 15:30 | 319 | 318
2020-01-10 16:00 | 332 | 332
2020-01-10 16:30 | 347 | 347
2020-01-10 17:00 | 360 | 360
2020-01-10 17:30 | 356 | 356
2020-01-10 18:00 | 350 | 350
2020-01-10 18:30 | 342 | 342
2020-01-10 19:00 | 341 | 341
2020-01-10 19:30 | 341 | 341
2020-01-10 20:00 | 337 | 337
2020-01-10 20:30 | 328 | 328
2020-01-10 21:00 | 315 | 314
2020-01-10 21:30 | 304 | 303
2020-01-10 22:00 | 290 | 289
2020-01-10 22:30 | 278 | 278
2020-01-10 23:00 | 270 | 270
2020-01-10 23:30 | 252 | 252
2020-01-11 | 231 | 231
2020-01-11 00:30 | 217 | 217
2020-01-11 01:00 | 210 | 210
2020-01-11 01:30 | 204 | 204
2020-01-11 02:00 | 198 | 198
2020-01-11 02:30 | 194 | 194
2020-01-11 03:00 | 190 | 190
2020-01-11 03:30 | 189 | 189
2020-01-11 04:00 | 187 | 187
2020-01-11 04:30 | 185 | 185
2020-01-11 05:00 | 183 | 183
2020-01-11 05:30 | 183 | 182
2020-01-11 06:00 | 182 | 182
2020-01-11 06:30 | 185 | 185
2020-01-11 07:00 | 187 | 187
2020-01-11 07:30 | 187 | 186
2020-01-11 08:00 | 188 | 187
2020-01-11 08:30 | 195 | 194
2020-01-11 09:00 | 203 | 202
2020-01-11 09:30 | 220 | 219
2020-01-11 10:00 | 223 | 221
2020-01-11 10:30 | 221 | 219
2020-01-11 11:00 | 226 | 223
2020-01-11 11:30 | 227 | 224
2020-01-11 12:00 | 254 | 251
2020-01-11 12:30 | 306 | 305
2020-01-11 13:00 | 321 | 321
2020-01-11 13:30 | 311 | 311
2020-01-11 14:00 | 303 | 303
2020-01-11 14:30 | 299 | 299
2020-01-11 15:00 | 302 | 302
2020-01-11 15:30 | 302 | 302
2020-01-11 16:00 | 306 | 305
2020-01-11 16:30 | 303 | 302
2020-01-11 17:00 | 310 | 310
2020-01-11 17:30 | 311 | 310
2020-01-11 18:00 | 309 | 309
2020-01-11 18:30 | 308 | 308
2020-01-11 19:00 | 311 | 310
2020-01-11 19:30 | 304 | 304
2020-01-11 20:00 | 299 | 298
2020-01-11 20:30 | 291 | 291
2020-01-11 21:00 | 279 | 279
2020-01-11 21:30 | 270 | 270
2020-01-11 22:00 | 259 | 259
2020-01-11 22:30 | 253 | 252
2020-01-11 23:00 | 247 | 246
2020-01-11 23:30 | 232 | 232
2020-01-12 | 215 | 215
2020-01-12 00:30 | 202 | 202
2020-01-12 01:00 | 195 | 194
2020-01-12 01:30 | 189 | 188
2020-01-12 02:00 | 184 | 183
2020-01-12 02:30 | 181 | 180
2020-01-12 03:00 | 179 | 178
2020-01-12 03:30 | 177 | 176
2020-01-12 04:00 | 175 | 174
2020-01-12 04:30 | 174 | 174
2020-01-12 05:00 | 173 | 173
2020-01-12 05:30 | 173 | 173
2020-01-12 06:00 | 173 | 173
2020-01-12 06:30 | 177 | 176
2020-01-12 07:00 | 180 | 180
2020-01-12 07:30 | 185 | 185
2020-01-12 08:00 | 186 | 186
2020-01-12 08:30 | 176 | 176
2020-01-12 09:00 | 176 | 176
2020-01-12 09:30 | 182 | 182
2020-01-12 10:00 | 180 | 180
2020-01-12 10:30 | 171 | 170
2020-01-12 11:00 | 176 | 175
2020-01-12 11:30 | 195 | 193
2020-01-12 12:00 | 212 | 211
2020-01-12 12:30 | 208 | 208
2020-01-12 13:00 | 218 | 218
2020-01-12 13:30 | 219 | 219
2020-01-12 14:00 | 229 | 229
2020-01-12 14:30 | 226 | 226
2020-01-12 15:00 | 214 | 214
2020-01-12 15:30 | 216 | 216
2020-01-12 16:00 | 226 | 226
2020-01-12 16:30 | 231 | 231
2020-01-12 17:00 | 237 | 237
2020-01-12 17:30 | 242 | 242
2020-01-12 18:00 | 249 | 249
2020-01-12 18:30 | 253 | 253
2020-01-12 19:00 | 257 | 257
2020-01-12 19:30 | 255 | 255
2020-01-12 20:00 | 253 | 253
2020-01-12 20:30 | 248 | 248
2020-01-12 21:00 | 237 | 237
2020-01-12 21:30 | 229 | 229
2020-01-12 22:00 | 222 | 222
2020-01-12 22:30 | 218 | 218
2020-01-12 23:00 | 213 | 213
2020-01-12 23:30 | 202 | 201
2020-01-13 | 186 | 186
2020-01-13 00:30 | 175 | 175
2020-01-13 01:00 | 169 | 169
2020-01-13 01:30 | 165 | 165
2020-01-13 02:00 | 164 | 164
2020-01-13 02:30 | 160 | 160
2020-01-13 03:00 | 159 | 158
2020-01-13 03:30 | 160 | 159
2020-01-13 04:00 | 160 | 159
2020-01-13 04:30 | 163 | 163
2020-01-13 05:00 | 169 | 169
2020-01-13 05:30 | 177 | 177
2020-01-13 06:00 | 184 | 184
2020-01-13 06:30 | 197 | 197
2020-01-13 07:00 | 208 | 208
2020-01-13 07:30 | 218 | 218
2020-01-13 08:00 | 229 | 229
2020-01-13 08:30 | 239 | 239
2020-01-13 09:00 | 236 | 236
2020-01-13 09:30 | 237 | 237
2020-01-13 10:00 | 240 | 240
2020-01-13 10:30 | 244 | 244
2020-01-13 11:00 | 245 | 244
2020-01-13 11:30 | 240 | 240
2020-01-13 12:00 | 235 | 235
2020-01-13 12:30 | 235 | 235
2020-01-13 13:00 | 228 | 227
2020-01-13 13:30 | 234 | 234
2020-01-13 14:00 | 237 | 237
2020-01-13 14:30 | 242 | 242
2020-01-13 15:00 | 245 | 245
2020-01-13 15:30 | 246 | 246
2020-01-13 16:00 | 261 | 260
2020-01-13 16:30 | 272 | 272
2020-01-13 17:00 | 280 | 280
2020-01-13 17:30 | 281 | 280
2020-01-13 18:00 | 282 | 282
2020-01-13 18:30 | 281 | 281
2020-01-13 19:00 | 285 | 285
2020-01-13 19:30 | 286 | 285
2020-01-13 20:00 | 283 | 283
2020-01-13 20:30 | 276 | 276
2020-01-13 21:00 | 264 | 264
2020-01-13 21:30 | 253 | 253
2020-01-13 22:00 | 240 | 240
2020-01-13 22:30 | 233 | 233
2020-01-13 23:00 | 226 | 226
2020-01-13 23:30 | 211 | 211
2020-01-14 | 195 | 195
2020-01-14 00:30 | 183 | 182
2020-01-14 01:00 | 176 | 174
2020-01-14 01:30 | 170 | 169
2020-01-14 02:00 | 168 | 166
2020-01-14 02:30 | 166 | 165
2020-01-14 03:00 | 165 | 164
2020-01-14 03:30 | 165 | 164
2020-01-14 04:00 | 166 | 164
2020-01-14 04:30 | 169 | 167
2020-01-14 05:00 | 173 | 172
2020-01-14 05:30 | 180 | 179
2020-01-14 06:00 | 187 | 186
2020-01-14 06:30 | 202 | 202
2020-01-14 07:00 | 216 | 216
2020-01-14 07:30 | 227 | 226
2020-01-14 08:00 | 235 | 234
2020-01-14 08:30 | 236 | 236
2020-01-14 09:00 | 233 | 231
2020-01-14 09:30 | 229 | 227
2020-01-14 10:00 | 224 | 222
2020-01-14 10:30 | 218 | 216
2020-01-14 11:00 | 227 | 226
2020-01-14 11:30 | 221 | 219
2020-01-14 12:00 | 234 | 233
2020-01-14 12:30 | 248 | 248
2020-01-14 13:00 | 249 | 249
2020-01-14 13:30 | 251 | 250
2020-01-14 14:00 | 248 | 248
2020-01-14 14:30 | 259 | 259
2020-01-14 15:00 | 272 | 272
2020-01-14 15:30 | 276 | 275
2020-01-14 16:00 | 282 | 281
2020-01-14 16:30 | 296 | 295
2020-01-14 17:00 | 301 | 300
2020-01-14 17:30 | 301 | 301
2020-01-14 18:00 | 301 | 301
2020-01-14 18:30 | 300 | 300
2020-01-14 19:00 | 303 | 303
2020-01-14 19:30 | 305 | 305
2020-01-14 20:00 | 303 | 303
2020-01-14 20:30 | 294 | 294
2020-01-14 21:00 | 282 | 282
2020-01-14 21:30 | 270 | 270
2020-01-14 22:00 | 257 | 257
2020-01-14 22:30 | 246 | 246
2020-01-14 23:00 | 237 | 237
2020-01-14 23:30 | 221 | 221
2020-01-15 | 206 | 205
2020-01-15 00:30 | 193 | 192
2020-01-15 01:00 | 186 | 185
2020-01-15 01:30 | 181 | 179
2020-01-15 02:00 | 177 | 175
2020-01-15 02:30 | 174 | 173
2020-01-15 03:00 | 171 | 171
2020-01-15 03:30 | 171 | 171
2020-01-15 04:00 | 171 | 170
2020-01-15 04:30 | 173 | 173
2020-01-15 05:00 | 179 | 179
2020-01-15 05:30 | 187 | 187
2020-01-15 06:00 | 196 | 196
2020-01-15 06:30 | 210 | 210
2020-01-15 07:00 | 220 | 220
2020-01-15 07:30 | 247 | 246
2020-01-15 08:00 | 259 | 259
2020-01-15 08:30 | 274 | 274
2020-01-15 09:00 | 279 | 279
2020-01-15 09:30 | 272 | 272
2020-01-15 10:00 | 261 | 261
2020-01-15 10:30 | 266 | 266
2020-01-15 11:00 | 276 | 276
2020-01-15 11:30 | 257 | 257
2020-01-15 12:00 | 256 | 256
2020-01-15 12:30 | 264 | 264
2020-01-15 13:00 | 272 | 272
2020-01-15 13:30 | 247 | 247
2020-01-15 14:00 | 249 | 249
2020-01-15 14:30 | 258 | 258
2020-01-15 15:00 | 258 | 258
2020-01-15 15:30 | 272 | 272
2020-01-15 16:00 | 287 | 287
2020-01-15 16:30 | 301 | 301
2020-01-15 17:00 | 314 | 314
2020-01-15 17:30 | 319 | 319
2020-01-15 18:00 | 319 | 319
2020-01-15 18:30 | 314 | 314
2020-01-15 19:00 | 318 | 317
2020-01-15 19:30 | 318 | 318
2020-01-15 20:00 | 315 | 315
2020-01-15 20:30 | 307 | 307
2020-01-15 21:00 | 294 | 294
2020-01-15 21:30 | 281 | 281
2020-01-15 22:00 | 267 | 267
2020-01-15 22:30 | 257 | 257
2020-01-15 23:00 | 247 | 247
2020-01-15 23:30 | 228 | 228
2020-01-16 | 211 | 211
2020-01-16 00:30 | 197 | 196
2020-01-16 01:00 | 189 | 189
2020-01-16 01:30 | 183 | 183
2020-01-16 02:00 | 179 | 179
2020-01-16 02:30 | 177 | 176
2020-01-16 03:00 | 176 | 175
2020-01-16 03:30 | 175 | 174
2020-01-16 04:00 | 175 | 175
2020-01-16 04:30 | 178 | 178
2020-01-16 05:00 | 182 | 181
2020-01-16 05:30 | 188 | 187
2020-01-16 06:00 | 191 | 191
2020-01-16 06:30 | 203 | 203
2020-01-16 07:00 | 216 | 215
2020-01-16 07:30 | 229 | 229
2020-01-16 08:00 | 239 | 239
2020-01-16 08:30 | 269 | 269
2020-01-16 09:00 | 278 | 278
2020-01-16 09:30 | 290 | 290
2020-01-16 10:00 | 287 | 287
2020-01-16 10:30 | 291 | 291
2020-01-16 11:00 | 301 | 301
2020-01-16 11:30 | 307 | 307
2020-01-16 12:00 | 300 | 300
2020-01-16 12:30 | 292 | 291
2020-01-16 13:00 | 288 | 288
2020-01-16 13:30 | 282 | 282
2020-01-16 14:00 | 286 | 286
2020-01-16 14:30 | 285 | 285
2020-01-16 15:00 | 280 | 279
2020-01-16 15:30 | 280 | 279
2020-01-16 16:00 | 282 | 281
2020-01-16 16:30 | 287 | 286
2020-01-16 17:00 | 293 | 292
2020-01-16 17:30 | 294 | 293
2020-01-16 18:00 | 297 | 296
2020-01-16 18:30 | 297 | 297
2020-01-16 19:00 | 303 | 303
2020-01-16 19:30 | 302 | 301
2020-01-16 20:00 | 300 | 299
2020-01-16 20:30 | 292 | 292
2020-01-16 21:00 | 280 | 280
2020-01-16 21:30 | 268 | 268
2020-01-16 22:00 | 254 | 254
2020-01-16 22:30 | 245 | 245
2020-01-16 23:00 | 238 | 238
2020-01-16 23:30 | 223 | 223
2020-01-17 | 207 | 207
2020-01-17 00:30 | 195 | 194
2020-01-17 01:00 | 186 | 185
2020-01-17 01:30 | 182 | 181
2020-01-17 02:00 | 177 | 176
2020-01-17 02:30 | 176 | 174
2020-01-17 03:00 | 174 | 172
2020-01-17 03:30 | 174 | 172
2020-01-17 04:00 | 174 | 172
2020-01-17 04:30 | 177 | 175
2020-01-17 05:00 | 182 | 181
2020-01-17 05:30 | 190 | 189
2020-01-17 06:00 | 196 | 195
2020-01-17 06:30 | 206 | 206
2020-01-17 07:00 | 214 | 214
2020-01-17 07:30 | 228 | 228
2020-01-17 08:00 | 241 | 240
2020-01-17 08:30 | 248 | 246
2020-01-17 09:00 | 251 | 250
2020-01-17 09:30 | 255 | 254
2020-01-17 10:00 | 256 | 254
2020-01-17 10:30 | 251 | 249
2020-01-17 11:00 | 258 | 258
2020-01-17 11:30 | 254 | 254
2020-01-17 12:00 | 248 | 248
2020-01-17 12:30 | 257 | 257
2020-01-17 13:00 | 264 | 263
2020-01-17 13:30 | 252 | 251
2020-01-17 14:00 | 260 | 259
2020-01-17 14:30 | 264 | 262
2020-01-17 15:00 | 280 | 279
2020-01-17 15:30 | 297 | 297
2020-01-17 16:00 | 299 | 298
2020-01-17 16:30 | 297 | 296
2020-01-17 17:00 | 305 | 304
2020-01-17 17:30 | 304 | 304
2020-01-17 18:00 | 301 | 301
2020-01-17 18:30 | 297 | 297
2020-01-17 19:00 | 302 | 302
2020-01-17 19:30 | 302 | 302
2020-01-17 20:00 | 300 | 300
2020-01-17 20:30 | 294 | 294
2020-01-17 21:00 | 284 | 284
2020-01-17 21:30 | 273 | 273
2020-01-17 22:00 | 263 | 262
2020-01-17 22:30 | 259 | 259
2020-01-17 23:00 | 249 | 249
2020-01-17 23:30 | 232 | 232
2020-01-18 | 215 | 215
2020-01-18 00:30 | 201 | 201
2020-01-18 01:00 | 193 | 193
2020-01-18 01:30 | 188 | 188
2020-01-18 02:00 | 182 | 181
2020-01-18 02:30 | 178 | 177
2020-01-18 03:00 | 174 | 173
2020-01-18 03:30 | 172 | 172
2020-01-18 04:00 | 172 | 172
2020-01-18 04:30 | 173 | 173
2020-01-18 05:00 | 174 | 174
2020-01-18 05:30 | 178 | 178
2020-01-18 06:00 | 181 | 181
2020-01-18 06:30 | 188 | 188
2020-01-18 07:00 | 194 | 194
2020-01-18 07:30 | 197 | 197
2020-01-18 08:00 | 198 | 197
2020-01-18 08:30 | 196 | 195
2020-01-18 09:00 | 196 | 196
2020-01-18 09:30 | 186 | 186
2020-01-18 10:00 | 185 | 185
2020-01-18 10:30 | 179 | 179
2020-01-18 11:00 | 188 | 188
2020-01-18 11:30 | 189 | 189
2020-01-18 12:00 | 188 | 188
2020-01-18 12:30 | 192 | 192
2020-01-18 13:00 | 204 | 204
2020-01-18 13:30 | 207 | 207
2020-01-18 14:00 | 207 | 207
2020-01-18 14:30 | 197 | 197
2020-01-18 15:00 | 205 | 205
2020-01-18 15:30 | 213 | 213
2020-01-18 16:00 | 225 | 223
2020-01-18 16:30 | 240 | 239
2020-01-18 17:00 | 254 | 252
2020-01-18 17:30 | 259 | 259
2020-01-18 18:00 | 263 | 262
2020-01-18 18:30 | 267 | 267
2020-01-18 19:00 | 272 | 272
2020-01-18 19:30 | 275 | 274
2020-01-18 20:00 | 273 | 273
2020-01-18 20:30 | 268 | 268
2020-01-18 21:00 | 257 | 257
2020-01-18 21:30 | 250 | 249
2020-01-18 22:00 | 243 | 242
2020-01-18 22:30 | 238 | 237
2020-01-18 23:00 | 232 | 232
2020-01-18 23:30 | 220 | 220
2020-01-19 | 205 | 205
2020-01-19 00:30 | 191 | 191
2020-01-19 01:00 | 183 | 183
2020-01-19 01:30 | 178 | 178
2020-01-19 02:00 | 173 | 173
2020-01-19 02:30 | 169 | 169
2020-01-19 03:00 | 167 | 167
2020-01-19 03:30 | 166 | 166
2020-01-19 04:00 | 165 | 165
2020-01-19 04:30 | 165 | 164
2020-01-19 05:00 | 164 | 164
2020-01-19 05:30 | 164 | 163
2020-01-19 06:00 | 163 | 162
2020-01-19 06:30 | 162 | 161
2020-01-19 07:00 | 160 | 160
2020-01-19 07:30 | 167 | 167
2020-01-19 08:00 | 170 | 170
2020-01-19 08:30 | 178 | 178
2020-01-19 09:00 | 177 | 176
2020-01-19 09:30 | 188 | 188
2020-01-19 10:00 | 208 | 207
2020-01-19 10:30 | 202 | 201
2020-01-19 11:00 | 197 | 196
2020-01-19 11:30 | 199 | 198
2020-01-19 12:00 | 216 | 215
2020-01-19 12:30 | 228 | 226
2020-01-19 13:00 | 227 | 225
2020-01-19 13:30 | 217 | 216
2020-01-19 14:00 | 222 | 220
2020-01-19 14:30 | 243 | 241
2020-01-19 15:00 | 257 | 256
2020-01-19 15:30 | 265 | 265
2020-01-19 16:00 | 278 | 278
2020-01-19 16:30 | 294 | 293
2020-01-19 17:00 | 309 | 307
2020-01-19 17:30 | 308 | 307
2020-01-19 18:00 | 307 | 306
2020-01-19 18:30 | 310 | 309
2020-01-19 19:00 | 316 | 315
2020-01-19 19:30 | 319 | 319
2020-01-19 20:00 | 319 | 319
2020-01-19 20:30 | 311 | 311
2020-01-19 21:00 | 297 | 296
2020-01-19 21:30 | 286 | 286
2020-01-19 22:00 | 274 | 274
2020-01-19 22:30 | 265 | 264
2020-01-19 23:00 | 258 | 257
2020-01-19 23:30 | 241 | 241
2020-01-20 | 223 | 223
2020-01-20 00:30 | 209 | 209
2020-01-20 01:00 | 202 | 202
2020-01-20 01:30 | 197 | 197
2020-01-20 02:00 | 193 | 193
2020-01-20 02:30 | 191 | 191
2020-01-20 03:00 | 190 | 190
2020-01-20 03:30 | 190 | 190
2020-01-20 04:00 | 190 | 190
2020-01-20 04:30 | 193 | 192
2020-01-20 05:00 | 198 | 198
2020-01-20 05:30 | 207 | 207
2020-01-20 06:00 | 215 | 215
2020-01-20 06:30 | 233 | 233
2020-01-20 07:00 | 249 | 249
2020-01-20 07:30 | 265 | 265
2020-01-20 08:00 | 273 | 273
2020-01-20 08:30 | 280 | 280
2020-01-20 09:00 | 283 | 283
2020-01-20 09:30 | 287 | 286
2020-01-20 10:00 | 292 | 291
2020-01-20 10:30 | 303 | 303
2020-01-20 11:00 | 308 | 308
2020-01-20 11:30 | 314 | 314
2020-01-20 12:00 | 320 | 319
2020-01-20 12:30 | 324 | 324
2020-01-20 13:00 | 331 | 331
2020-01-20 13:30 | 350 | 349
2020-01-20 14:00 | 357 | 356
2020-01-20 14:30 | 389 | 387
2020-01-20 15:00 | 421 | 418
2020-01-20 15:30 | 411 | 410
2020-01-20 16:00 | 381 | 381
2020-01-20 16:30 | 366 | 366
2020-01-20 17:00 | 351 | 351
2020-01-20 17:30 | 348 | 347
2020-01-20 18:00 | 346 | 346
2020-01-20 18:30 | 342 | 341
2020-01-20 19:00 | 343 | 343
2020-01-20 19:30 | 343 | 343
2020-01-20 20:00 | 337 | 337
2020-01-20 20:30 | 325 | 325
2020-01-20 21:00 | 310 | 310
2020-01-20 21:30 | 295 | 295
2020-01-20 22:00 | 279 | 279
2020-01-20 22:30 | 268 | 267
2020-01-20 23:00 | 257 | 255
2020-01-20 23:30 | 244 | 243
2020-01-21 | 228 | 228
2020-01-21 00:30 | 216 | 215
2020-01-21 01:00 | 209 | 209
2020-01-21 01:30 | 206 | 205
2020-01-21 02:00 | 202 | 202
2020-01-21 02:30 | 199 | 199
2020-01-21 03:00 | 199 | 199
2020-01-21 03:30 | 197 | 197
2020-01-21 04:00 | 197 | 197
2020-01-21 04:30 | 201 | 200
2020-01-21 05:00 | 205 | 204
2020-01-21 05:30 | 214 | 213
2020-01-21 06:00 | 224 | 223
2020-01-21 06:30 | 243 | 241
2020-01-21 07:00 | 256 | 255
2020-01-21 07:30 | 258 | 257
2020-01-21 08:00 | 270 | 269
2020-01-21 08:30 | 267 | 267
2020-01-21 09:00 | 264 | 264
2020-01-21 09:30 | 267 | 267
2020-01-21 10:00 | 271 | 271
2020-01-21 10:30 | 277 | 277
2020-01-21 11:00 | 287 | 287
2020-01-21 11:30 | 298 | 298
2020-01-21 12:00 | 311 | 310
2020-01-21 12:30 | 326 | 325
2020-01-21 13:00 | 339 | 339
2020-01-21 13:30 | 348 | 348
2020-01-21 14:00 | 352 | 352
2020-01-21 14:30 | 375 | 375
2020-01-21 15:00 | 388 | 387
2020-01-21 15:30 | 404 | 403
2020-01-21 16:00 | 427 | 425
2020-01-21 16:30 | 436 | 434
2020-01-21 17:00 | 423 | 421
2020-01-21 17:30 | 411 | 411
2020-01-21 18:00 | 410 | 410
2020-01-21 18:30 | 398 | 398
2020-01-21 19:00 | 394 | 394
2020-01-21 19:30 | 390 | 390
2020-01-21 20:00 | 381 | 381
2020-01-21 20:30 | 369 | 369
2020-01-21 21:00 | 350 | 350
2020-01-21 21:30 | 330 | 330
2020-01-21 22:00 | 311 | 311
2020-01-21 22:30 | 296 | 296
2020-01-21 23:00 | 283 | 283
2020-01-21 23:30 | 262 | 262
2020-01-22 | 241 | 240
2020-01-22 00:30 | 224 | 224
2020-01-22 01:00 | 215 | 215
2020-01-22 01:30 | 208 | 208
2020-01-22 02:00 | 203 | 202
2020-01-22 02:30 | 199 | 199
2020-01-22 03:00 | 196 | 195
2020-01-22 03:30 | 194 | 194
2020-01-22 04:00 | 192 | 192
2020-01-22 04:30 | 194 | 194
2020-01-22 05:00 | 198 | 198
2020-01-22 05:30 | 205 | 204
2020-01-22 06:00 | 212 | 212
2020-01-22 06:30 | 230 | 230
2020-01-22 07:00 | 245 | 244
2020-01-22 07:30 | 258 | 255
2020-01-22 08:00 | 267 | 266
2020-01-22 08:30 | 274 | 273
2020-01-22 09:00 | 287 | 286
2020-01-22 09:30 | 292 | 292
2020-01-22 10:00 | 290 | 290
2020-01-22 10:30 | 296 | 296
2020-01-22 11:00 | 299 | 299
2020-01-22 11:30 | 306 | 306
2020-01-22 12:00 | 318 | 317
2020-01-22 12:30 | 330 | 328
2020-01-22 13:00 | 338 | 337
2020-01-22 13:30 | 350 | 350
2020-01-22 14:00 | 367 | 367
2020-01-22 14:30 | 375 | 374
2020-01-22 15:00 | 392 | 391
2020-01-22 15:30 | 400 | 399
2020-01-22 16:00 | 439 | 437
2020-01-22 16:30 | 445 | 445
2020-01-22 17:00 | 439 | 439
2020-01-22 17:30 | 435 | 435
2020-01-22 18:00 | 431 | 430
2020-01-22 18:30 | 423 | 422
2020-01-22 19:00 | 425 | 424
2020-01-22 19:30 | 418 | 418
2020-01-22 20:00 | 410 | 410
2020-01-22 20:30 | 396 | 396
2020-01-22 21:00 | 377 | 377
2020-01-22 21:30 | 357 | 356
2020-01-22 22:00 | 334 | 334
2020-01-22 22:30 | 317 | 317
2020-01-22 23:00 | 302 | 302
2020-01-22 23:30 | 282 | 282
2020-01-23 | 263 | 263
2020-01-23 00:30 | 246 | 245
2020-01-23 01:00 | 238 | 237
2020-01-23 01:30 | 232 | 231
2020-01-23 02:00 | 227 | 226
2020-01-23 02:30 | 223 | 222
2020-01-23 03:00 | 220 | 219
2020-01-23 03:30 | 219 | 218
2020-01-23 04:00 | 217 | 217
2020-01-23 04:30 | 219 | 219
2020-01-23 05:00 | 224 | 224
2020-01-23 05:30 | 232 | 231
2020-01-23 06:00 | 241 | 240
2020-01-23 06:30 | 258 | 256
2020-01-23 07:00 | 272 | 271
2020-01-23 07:30 | 297 | 296
2020-01-23 08:00 | 308 | 308
2020-01-23 08:30 | 318 | 316
2020-01-23 09:00 | 320 | 319
2020-01-23 09:30 | 322 | 320
2020-01-23 10:00 | 324 | 322
2020-01-23 10:30 | 328 | 326
2020-01-23 11:00 | 324 | 322
2020-01-23 11:30 | 340 | 338
2020-01-23 12:00 | 345 | 342
2020-01-23 12:30 | 351 | 349
2020-01-23 13:00 | 323 | 321
2020-01-23 13:30 | 295 | 294
2020-01-23 14:00 | 321 | 320
2020-01-23 14:30 | 335 | 334
2020-01-23 15:00 | 337 | 336
2020-01-23 15:30 | 356 | 355
2020-01-23 16:00 | 366 | 364
2020-01-23 16:30 | 370 | 368
2020-01-23 17:00 | 371 | 370
2020-01-23 17:30 | 376 | 375
2020-01-23 18:00 | 376 | 376
2020-01-23 18:30 | 376 | 376
2020-01-23 19:00 | 375 | 375
2020-01-23 19:30 | 372 | 372
2020-01-23 20:00 | 368 | 368
2020-01-23 20:30 | 357 | 357
2020-01-23 21:00 | 349 | 349
2020-01-23 21:30 | 332 | 331
2020-01-23 22:00 | 315 | 314
2020-01-23 22:30 | 304 | 303
2020-01-23 23:00 | 293 | 292
2020-01-23 23:30 | 269 | 269
2020-01-24 | 250 | 249
2020-01-24 00:30 | 236 | 235
2020-01-24 01:00 | 229 | 227
2020-01-24 01:30 | 221 | 220
2020-01-24 02:00 | 217 | 216
2020-01-24 02:30 | 214 | 212
2020-01-24 03:00 | 211 | 209
2020-01-24 03:30 | 209 | 209
2020-01-24 04:00 | 208 | 207
2020-01-24 04:30 | 210 | 210
2020-01-24 05:00 | 215 | 215
2020-01-24 05:30 | 221 | 221
2020-01-24 06:00 | 228 | 228
2020-01-24 06:30 | 242 | 242
2020-01-24 07:00 | 261 | 261
2020-01-24 07:30 | 276 | 276
2020-01-24 08:00 | 279 | 279
2020-01-24 08:30 | 290 | 290
2020-01-24 09:00 | 321 | 320
2020-01-24 09:30 | 330 | 329
2020-01-24 10:00 | 342 | 341
2020-01-24 10:30 | 354 | 353
2020-01-24 11:00 | 357 | 356
2020-01-24 11:30 | 372 | 371
2020-01-24 12:00 | 371 | 370
2020-01-24 12:30 | 348 | 348
2020-01-24 13:00 | 358 | 357
2020-01-24 13:30 | 381 | 381
2020-01-24 14:00 | 392 | 392
2020-01-24 14:30 | 394 | 394
2020-01-24 15:00 | 392 | 392
2020-01-24 15:30 | 404 | 404
2020-01-24 16:00 | 416 | 415
2020-01-24 16:30 | 421 | 421
2020-01-24 17:00 | 435 | 435
2020-01-24 17:30 | 431 | 429
2020-01-24 18:00 | 421 | 420
2020-01-24 18:30 | 409 | 408
2020-01-24 19:00 | 406 | 404
2020-01-24 19:30 | 402 | 401
2020-01-24 20:00 | 394 | 393
2020-01-24 20:30 | 382 | 382
2020-01-24 21:00 | 366 | 366
2020-01-24 21:30 | 352 | 351
2020-01-24 22:00 | 335 | 334
2020-01-24 22:30 | 322 | 321
2020-01-24 23:00 | 310 | 309
2020-01-24 23:30 | 288 | 288
2020-01-25 | 268 | 268
2020-01-25 00:30 | 249 | 249
2020-01-25 01:00 | 240 | 240
2020-01-25 01:30 | 233 | 233
2020-01-25 02:00 | 227 | 227
2020-01-25 02:30 | 224 | 223
2020-01-25 03:00 | 221 | 221
2020-01-25 03:30 | 220 | 220
2020-01-25 04:00 | 218 | 218
2020-01-25 04:30 | 216 | 216
2020-01-25 05:00 | 216 | 216
2020-01-25 05:30 | 213 | 213
2020-01-25 06:00 | 213 | 213
2020-01-25 06:30 | 217 | 217
2020-01-25 07:00 | 219 | 219
2020-01-25 07:30 | 231 | 231
2020-01-25 08:00 | 247 | 247
2020-01-25 08:30 | 265 | 265
2020-01-25 09:00 | 276 | 275
2020-01-25 09:30 | 281 | 281
2020-01-25 10:00 | 273 | 273
2020-01-25 10:30 | 271 | 270
2020-01-25 11:00 | 270 | 270
2020-01-25 11:30 | 282 | 281
2020-01-25 12:00 | 288 | 287
2020-01-25 12:30 | 292 | 290
2020-01-25 13:00 | 330 | 328
2020-01-25 13:30 | 352 | 350
2020-01-25 14:00 | 347 | 346
2020-01-25 14:30 | 339 | 339
2020-01-25 15:00 | 330 | 330
2020-01-25 15:30 | 324 | 324
2020-01-25 16:00 | 322 | 322
2020-01-25 16:30 | 322 | 322
2020-01-25 17:00 | 321 | 321
2020-01-25 17:30 | 314 | 314
2020-01-25 18:00 | 313 | 313
2020-01-25 18:30 | 314 | 314
2020-01-25 19:00 | 319 | 319
2020-01-25 19:30 | 320 | 320
2020-01-25 20:00 | 318 | 318
2020-01-25 20:30 | 310 | 310
2020-01-25 21:00 | 298 | 298
2020-01-25 21:30 | 291 | 291
2020-01-25 22:00 | 280 | 280
2020-01-25 22:30 | 274 | 274
2020-01-25 23:00 | 266 | 266
2020-01-25 23:30 | 248 | 247
2020-01-26 | 230 | 230
2020-01-26 00:30 | 216 | 216
2020-01-26 01:00 | 207 | 207
2020-01-26 01:30 | 200 | 200
2020-01-26 02:00 | 194 | 194
2020-01-26 02:30 | 191 | 191
2020-01-26 03:00 | 188 | 188
2020-01-26 03:30 | 186 | 185
2020-01-26 04:00 | 184 | 184
2020-01-26 04:30 | 183 | 183
2020-01-26 05:00 | 183 | 182
2020-01-26 05:30 | 180 | 180
2020-01-26 06:00 | 179 | 179
2020-01-26 06:30 | 181 | 181
2020-01-26 07:00 | 184 | 184
2020-01-26 07:30 | 187 | 187
2020-01-26 08:00 | 187 | 187
2020-01-26 08:30 | 195 | 195
2020-01-26 09:00 | 202 | 201
2020-01-26 09:30 | 210 | 208
2020-01-26 10:00 | 210 | 209
2020-01-26 10:30 | 211 | 209
2020-01-26 11:00 | 211 | 209
2020-01-26 11:30 | 213 | 211
2020-01-26 12:00 | 223 | 222
2020-01-26 12:30 | 223 | 221
2020-01-26 13:00 | 221 | 219
2020-01-26 13:30 | 228 | 226
2020-01-26 14:00 | 237 | 235
2020-01-26 14:30 | 244 | 243
2020-01-26 15:00 | 252 | 252
2020-01-26 15:30 | 261 | 261
2020-01-26 16:00 | 272 | 272
2020-01-26 16:30 | 280 | 280
2020-01-26 17:00 | 292 | 291
2020-01-26 17:30 | 300 | 300
2020-01-26 18:00 | 304 | 303
2020-01-26 18:30 | 307 | 306
2020-01-26 19:00 | 310 | 310
2020-01-26 19:30 | 311 | 311
2020-01-26 20:00 | 310 | 309
2020-01-26 20:30 | 303 | 302
2020-01-26 21:00 | 292 | 291
2020-01-26 21:30 | 282 | 281
2020-01-26 22:00 | 272 | 271
2020-01-26 22:30 | 266 | 266
2020-01-26 23:00 | 260 | 258
2020-01-26 23:30 | 243 | 242
2020-01-27 | 224 | 223
2020-01-27 00:30 | 209 | 209
2020-01-27 01:00 | 200 | 200
2020-01-27 01:30 | 193 | 193
2020-01-27 02:00 | 189 | 189
2020-01-27 02:30 | 185 | 185
2020-01-27 03:00 | 183 | 183
2020-01-27 03:30 | 182 | 182
2020-01-27 04:00 | 181 | 181
2020-01-27 04:30 | 181 | 181
2020-01-27 05:00 | 181 | 181
2020-01-27 05:30 | 181 | 180
2020-01-27 06:00 | 180 | 179
2020-01-27 06:30 | 184 | 184
2020-01-27 07:00 | 186 | 186
2020-01-27 07:30 | 191 | 191
2020-01-27 08:00 | 196 | 195
2020-01-27 08:30 | 202 | 202
2020-01-27 09:00 | 206 | 206
2020-01-27 09:30 | 207 | 207
2020-01-27 10:00 | 214 | 214
2020-01-27 10:30 | 215 | 215
2020-01-27 11:00 | 219 | 219
2020-01-27 11:30 | 221 | 221
2020-01-27 12:00 | 223 | 223
2020-01-27 12:30 | 231 | 231
2020-01-27 13:00 | 239 | 238
2020-01-27 13:30 | 249 | 249
2020-01-27 14:00 | 257 | 257
2020-01-27 14:30 | 267 | 266
2020-01-27 15:00 | 281 | 281
2020-01-27 15:30 | 291 | 291
2020-01-27 16:00 | 303 | 303
2020-01-27 16:30 | 319 | 319
2020-01-27 17:00 | 331 | 331
2020-01-27 17:30 | 340 | 340
2020-01-27 18:00 | 343 | 343
2020-01-27 18:30 | 342 | 342
2020-01-27 19:00 | 342 | 342
2020-01-27 19:30 | 340 | 340
2020-01-27 20:00 | 334 | 334
2020-01-27 20:30 | 324 | 324
2020-01-27 21:00 | 308 | 308
2020-01-27 21:30 | 294 | 294
2020-01-27 22:00 | 279 | 279
2020-01-27 22:30 | 269 | 269
2020-01-27 23:00 | 261 | 260
2020-01-27 23:30 | 242 | 242
2020-01-28 | 221 | 221
2020-01-28 00:30 | 207 | 207
2020-01-28 01:00 | 199 | 199
2020-01-28 01:30 | 194 | 194
2020-01-28 02:00 | 190 | 190
2020-01-28 02:30 | 188 | 188
2020-01-28 03:00 | 186 | 186
2020-01-28 03:30 | 187 | 186
2020-01-28 04:00 | 186 | 186
2020-01-28 04:30 | 189 | 188
2020-01-28 05:00 | 194 | 194
2020-01-28 05:30 | 204 | 204
2020-01-28 06:00 | 215 | 215
2020-01-28 06:30 | 236 | 235
2020-01-28 07:00 | 253 | 251
2020-01-28 07:30 | 269 | 268
2020-01-28 08:00 | 279 | 279
2020-01-28 08:30 | 285 | 285
2020-01-28 09:00 | 286 | 286
2020-01-28 09:30 | 294 | 293
2020-01-28 10:00 | 294 | 293
2020-01-28 10:30 | 294 | 293
2020-01-28 11:00 | 294 | 293
2020-01-28 11:30 | 287 | 286
2020-01-28 12:00 | 288 | 287
2020-01-28 12:30 | 298 | 297
2020-01-28 13:00 | 303 | 302
2020-01-28 13:30 | 312 | 311
2020-01-28 14:00 | 320 | 319
2020-01-28 14:30 | 309 | 308
2020-01-28 15:00 | 311 | 310
2020-01-28 15:30 | 320 | 319
2020-01-28 16:00 | 341 | 339
2020-01-28 16:30 | 361 | 361
2020-01-28 17:00 | 376 | 376
2020-01-28 17:30 | 380 | 380
2020-01-28 18:00 | 384 | 384
2020-01-28 18:30 | 380 | 379
2020-01-28 19:00 | 377 | 377
2020-01-28 19:30 | 375 | 375
2020-01-28 20:00 | 369 | 369
2020-01-28 20:30 | 357 | 357
2020-01-28 21:00 | 339 | 338
2020-01-28 21:30 | 319 | 319
2020-01-28 22:00 | 300 | 299
2020-01-28 22:30 | 283 | 283
2020-01-28 23:00 | 272 | 272
2020-01-28 23:30 | 253 | 253
2020-01-29 | 231 | 231
2020-01-29 00:30 | 217 | 217
2020-01-29 01:00 | 209 | 209
2020-01-29 01:30 | 203 | 203
2020-01-29 02:00 | 200 | 200
2020-01-29 02:30 | 197 | 197
2020-01-29 03:00 | 194 | 194
2020-01-29 03:30 | 194 | 194
2020-01-29 04:00 | 193 | 193
2020-01-29 04:30 | 196 | 196
2020-01-29 05:00 | 201 | 201
2020-01-29 05:30 | 210 | 210
2020-01-29 06:00 | 220 | 219
2020-01-29 06:30 | 240 | 240
2020-01-29 07:00 | 258 | 257
2020-01-29 07:30 | 273 | 273
2020-01-29 08:00 | 277 | 276
2020-01-29 08:30 | 276 | 275
2020-01-29 09:00 | 273 | 272
2020-01-29 09:30 | 278 | 276
2020-01-29 10:00 | 281 | 278
2020-01-29 10:30 | 284 | 283
2020-01-29 11:00 | 290 | 288
2020-01-29 11:30 | 297 | 296
2020-01-29 12:00 | 308 | 306
2020-01-29 12:30 | 319 | 318
2020-01-29 13:00 | 336 | 333
2020-01-29 13:30 | 354 | 351
2020-01-29 14:00 | 359 | 358
2020-01-29 14:30 | 361 | 360
2020-01-29 15:00 | 369 | 368
2020-01-29 15:30 | 383 | 382
2020-01-29 16:00 | 408 | 407
2020-01-29 16:30 | 428 | 427
2020-01-29 17:00 | 446 | 445
2020-01-29 17:30 | 451 | 450
2020-01-29 18:00 | 445 | 445
2020-01-29 18:30 | 434 | 433
2020-01-29 19:00 | 432 | 431
2020-01-29 19:30 | 425 | 425
2020-01-29 20:00 | 415 | 415
2020-01-29 20:30 | 400 | 400
2020-01-29 21:00 | 378 | 378
2020-01-29 21:30 | 357 | 356
2020-01-29 22:00 | 333 | 333
2020-01-29 22:30 | 315 | 315
2020-01-29 23:00 | 302 | 302
2020-01-29 23:30 | 280 | 280
2020-01-30 | 259 | 258
2020-01-30 00:30 | 243 | 242
2020-01-30 01:00 | 233 | 233
2020-01-30 01:30 | 224 | 224
2020-01-30 02:00 | 219 | 219
2020-01-30 02:30 | 215 | 215
2020-01-30 03:00 | 211 | 211
2020-01-30 03:30 | 209 | 209
2020-01-30 04:00 | 208 | 208
2020-01-30 04:30 | 209 | 209
2020-01-30 05:00 | 214 | 214
2020-01-30 05:30 | 221 | 221
2020-01-30 06:00 | 231 | 230
2020-01-30 06:30 | 250 | 250
2020-01-30 07:00 | 267 | 266
2020-01-30 07:30 | 283 | 282
2020-01-30 08:00 | 294 | 293
2020-01-30 08:30 | 303 | 302
2020-01-30 09:00 | 301 | 301
2020-01-30 09:30 | 314 | 313
2020-01-30 10:00 | 319 | 317
2020-01-30 10:30 | 316 | 315
2020-01-30 11:00 | 319 | 317
2020-01-30 11:30 | 326 | 324
2020-01-30 12:00 | 328 | 326
2020-01-30 12:30 | 333 | 333
2020-01-30 13:00 | 335 | 334
2020-01-30 13:30 | 331 | 331
2020-01-30 14:00 | 335 | 335
2020-01-30 14:30 | 346 | 345
2020-01-30 15:00 | 359 | 359
2020-01-30 15:30 | 374 | 373
2020-01-30 16:00 | 388 | 387
2020-01-30 16:30 | 401 | 401
2020-01-30 17:00 | 413 | 413
2020-01-30 17:30 | 411 | 410
2020-01-30 18:00 | 403 | 403
2020-01-30 18:30 | 396 | 395
2020-01-30 19:00 | 392 | 391
2020-01-30 19:30 | 403 | 403
2020-01-30 20:00 | 399 | 398
2020-01-30 20:30 | 381 | 381
2020-01-30 21:00 | 357 | 356
2020-01-30 21:30 | 330 | 329
2020-01-30 22:00 | 309 | 309
2020-01-30 22:30 | 293 | 293
2020-01-30 23:00 | 280 | 280
2020-01-30 23:30 | 259 | 259
2020-01-31 | 238 | 237
2020-01-31 00:30 | 223 | 223
2020-01-31 01:00 | 214 | 214
2020-01-31 01:30 | 208 | 208
2020-01-31 02:00 | 203 | 203
2020-01-31 02:30 | 200 | 200
2020-01-31 03:00 | 198 | 197
2020-01-31 03:30 | 197 | 197
2020-01-31 04:00 | 197 | 197
2020-01-31 04:30 | 198 | 198
2020-01-31 05:00 | 203 | 203
2020-01-31 05:30 | 211 | 210
2020-01-31 06:00 | 220 | 220
2020-01-31 06:30 | 239 | 238
2020-01-31 07:00 | 254 | 253
2020-01-31 07:30 | 269 | 268
2020-01-31 08:00 | 275 | 274
2020-01-31 08:30 | 280 | 279
2020-01-31 09:00 | 286 | 285
2020-01-31 09:30 | 287 | 286
2020-01-31 10:00 | 287 | 286
2020-01-31 10:30 | 293 | 291
2020-01-31 11:00 | 297 | 295
2020-01-31 11:30 | 295 | 293
2020-01-31 12:00 | 300 | 299
2020-01-31 12:30 | 302 | 302
2020-01-31 13:00 | 301 | 301
2020-01-31 13:30 | 304 | 304
2020-01-31 14:00 | 312 | 312
2020-01-31 14:30 | 321 | 321
2020-01-31 15:00 | 325 | 325
2020-01-31 15:30 | 332 | 331
2020-01-31 16:00 | 338 | 337
2020-01-31 16:30 | 355 | 354
2020-01-31 17:00 | 374 | 374
2020-01-31 17:30 | 373 | 373
2020-01-31 18:00 | 372 | 372
2020-01-31 18:30 | 362 | 361
2020-01-31 19:00 | 362 | 362
2020-01-31 19:30 | 357 | 357
2020-01-31 20:00 | 360 | 360
2020-01-31 20:30 | 349 | 349
2020-01-31 21:00 | 329 | 329
2020-01-31 21:30 | 315 | 315
2020-01-31 22:00 | 298 | 298
2020-01-31 22:30 | 288 | 288
2020-01-31 23:00 | 278 | 277
2020-01-31 23:30 | 257 | 257
2020-02-01 | 238 | 238
2020-02-01 00:30 | 223 | 223
2020-02-01 01:00 | 215 | 214
2020-02-01 01:30 | 207 | 207
2020-02-01 02:00 | 201 | 201
2020-02-01 02:30 | 197 | 197
2020-02-01 03:00 | 194 | 194
2020-02-01 03:30 | 192 | 192
2020-02-01 04:00 | 190 | 190
2020-02-01 04:30 | 190 | 190
2020-02-01 05:00 | 189 | 189
2020-02-01 05:30 | 189 | 189
2020-02-01 06:00 | 188 | 188
2020-02-01 06:30 | 192 | 192
2020-02-01 07:00 | 193 | 193
2020-02-01 07:30 | 199 | 199
2020-02-01 08:00 | 205 | 205
2020-02-01 08:30 | 216 | 215
2020-02-01 09:00 | 221 | 220
2020-02-01 09:30 | 223 | 222
2020-02-01 10:00 | 226 | 225
2020-02-01 10:30 | 232 | 230
2020-02-01 11:00 | 241 | 238
2020-02-01 11:30 | 249 | 247
2020-02-01 12:00 | 259 | 259
2020-02-01 12:30 | 265 | 264
2020-02-01 13:00 | 272 | 271
2020-02-01 13:30 | 280 | 279
2020-02-01 14:00 | 289 | 288
2020-02-01 14:30 | 297 | 295
2020-02-01 15:00 | 302 | 300
2020-02-01 15:30 | 312 | 310
2020-02-01 16:00 | 322 | 320
2020-02-01 16:30 | 336 | 334
2020-02-01 17:00 | 350 | 348
2020-02-01 17:30 | 358 | 356
2020-02-01 18:00 | 357 | 355
2020-02-01 18:30 | 350 | 349
2020-02-01 19:00 | 351 | 349
2020-02-01 19:30 | 349 | 348
2020-02-01 20:00 | 342 | 341
2020-02-01 20:30 | 333 | 332
2020-02-01 21:00 | 315 | 315
2020-02-01 21:30 | 301 | 301
2020-02-01 22:00 | 289 | 289
2020-02-01 22:30 | 280 | 280
2020-02-01 23:00 | 271 | 271
2020-02-01 23:30 | 253 | 252
2020-02-02 | 235 | 234
2020-02-02 00:30 | 219 | 219
2020-02-02 01:00 | 210 | 210
2020-02-02 01:30 | 202 | 202
2020-02-02 02:00 | 196 | 196
2020-02-02 02:30 | 193 | 193
2020-02-02 03:00 | 190 | 189
2020-02-02 03:30 | 187 | 187
2020-02-02 04:00 | 184 | 184
2020-02-02 04:30 | 183 | 183
2020-02-02 05:00 | 182 | 181
2020-02-02 05:30 | 180 | 180
2020-02-02 06:00 | 178 | 178
2020-02-02 06:30 | 178 | 178
2020-02-02 07:00 | 177 | 177
2020-02-02 07:30 | 179 | 179
2020-02-02 08:00 | 181 | 181
2020-02-02 08:30 | 185 | 185
2020-02-02 09:00 | 190 | 189
2020-02-02 09:30 | 191 | 190
2020-02-02 10:00 | 195 | 193
2020-02-02 10:30 | 201 | 199
2020-02-02 11:00 | 209 | 209
2020-02-02 11:30 | 216 | 216
2020-02-02 12:00 | 227 | 226
2020-02-02 12:30 | 238 | 238
2020-02-02 13:00 | 251 | 250
2020-02-02 13:30 | 266 | 264
2020-02-02 14:00 | 281 | 280
2020-02-02 14:30 | 297 | 295
2020-02-02 15:00 | 313 | 311
2020-02-02 15:30 | 331 | 329
2020-02-02 16:00 | 349 | 349
2020-02-02 16:30 | 365 | 365
2020-02-02 17:00 | 382 | 381
2020-02-02 17:30 | 391 | 390
2020-02-02 18:00 | 394 | 393
2020-02-02 18:30 | 388 | 387
2020-02-02 19:00 | 379 | 379
2020-02-02 19:30 | 388 | 388
2020-02-02 20:00 | 384 | 384
2020-02-02 20:30 | 372 | 371
2020-02-02 21:00 | 354 | 354
2020-02-02 21:30 | 336 | 336
2020-02-02 22:00 | 316 | 316
2020-02-02 22:30 | 302 | 302
2020-02-02 23:00 | 290 | 290
2020-02-02 23:30 | 268 | 268
2020-02-03 | 249 | 249
2020-02-03 00:30 | 234 | 233
2020-02-03 01:00 | 225 | 224
2020-02-03 01:30 | 217 | 216
2020-02-03 02:00 | 211 | 211
2020-02-03 02:30 | 208 | 208
2020-02-03 03:00 | 205 | 205
2020-02-03 03:30 | 204 | 204
2020-02-03 04:00 | 202 | 202
2020-02-03 04:30 | 204 | 204
2020-02-03 05:00 | 210 | 209
2020-02-03 05:30 | 218 | 218
2020-02-03 06:00 | 229 | 228
2020-02-03 06:30 | 252 | 251
2020-02-03 07:00 | 270 | 270
2020-02-03 07:30 | 285 | 285
2020-02-03 08:00 | 290 | 289
2020-02-03 08:30 | 290 | 289
2020-02-03 09:00 | 292 | 290
2020-02-03 09:30 | 298 | 297
2020-02-03 10:00 | 301 | 301
2020-02-03 10:30 | 311 | 310
2020-02-03 11:00 | 322 | 322
2020-02-03 11:30 | 326 | 326
2020-02-03 12:00 | 335 | 335
2020-02-03 12:30 | 347 | 346
2020-02-03 13:00 | 358 | 357
2020-02-03 13:30 | 369 | 367
2020-02-03 14:00 | 383 | 381
2020-02-03 14:30 | 395 | 394
2020-02-03 15:00 | 408 | 407
2020-02-03 15:30 | 423 | 423
2020-02-03 16:00 | 447 | 445
2020-02-03 16:30 | 469 | 467
2020-02-03 17:00 | 478 | 477
2020-02-03 17:30 | 482 | 480
2020-02-03 18:00 | 478 | 477
2020-02-03 18:30 | 466 | 466
2020-02-03 19:00 | 463 | 462
2020-02-03 19:30 | 456 | 455
2020-02-03 20:00 | 448 | 448
2020-02-03 20:30 | 435 | 435
2020-02-03 21:00 | 408 | 408
2020-02-03 21:30 | 385 | 383
2020-02-03 22:00 | 355 | 355
2020-02-03 22:30 | 340 | 339
2020-02-03 23:00 | 319 | 317
2020-02-03 23:30 | 290 | 290
2020-02-04 | 268 | 267
2020-02-04 00:30 | 243 | 243
2020-02-04 01:00 | 233 | 232
2020-02-04 01:30 | 225 | 225
2020-02-04 02:00 | 219 | 219
2020-02-04 02:30 | 216 | 216
2020-02-04 03:00 | 213 | 213
2020-02-04 03:30 | 213 | 213
2020-02-04 04:00 | 212 | 212
2020-02-04 04:30 | 214 | 214
2020-02-04 05:00 | 220 | 220
2020-02-04 05:30 | 231 | 230
2020-02-04 06:00 | 237 | 236
2020-02-04 06:30 | 253 | 251
2020-02-04 07:00 | 268 | 268
2020-02-04 07:30 | 288 | 288
2020-02-04 08:00 | 302 | 301
2020-02-04 08:30 | 325 | 324
2020-02-04 09:00 | 339 | 339
2020-02-04 09:30 | 320 | 320
2020-02-04 10:00 | 307 | 307
2020-02-04 10:30 | 313 | 313
2020-02-04 11:00 | 319 | 319
2020-02-04 11:30 | 311 | 311
2020-02-04 12:00 | 302 | 302
2020-02-04 12:30 | 302 | 302
2020-02-04 13:00 | 322 | 322
2020-02-04 13:30 | 320 | 320
2020-02-04 14:00 | 312 | 312
2020-02-04 14:30 | 322 | 321
2020-02-04 15:00 | 324 | 324
2020-02-04 15:30 | 322 | 322
2020-02-04 16:00 | 306 | 306
2020-02-04 16:30 | 299 | 299
2020-02-04 17:00 | 302 | 302
2020-02-04 17:30 | 299 | 299
2020-02-04 18:00 | 295 | 295
2020-02-04 18:30 | 292 | 291
2020-02-04 19:00 | 298 | 297
2020-02-04 19:30 | 293 | 292
2020-02-04 20:00 | 289 | 289
2020-02-04 20:30 | 281 | 281
2020-02-04 21:00 | 267 | 267
2020-02-04 21:30 | 256 | 256
2020-02-04 22:00 | 246 | 246
2020-02-04 22:30 | 238 | 238
2020-02-04 23:00 | 232 | 232
2020-02-04 23:30 | 217 | 217
2020-02-05 | 201 | 201
2020-02-05 00:30 | 189 | 188
2020-02-05 01:00 | 182 | 182
2020-02-05 01:30 | 178 | 178
2020-02-05 02:00 | 175 | 174
2020-02-05 02:30 | 173 | 173
2020-02-05 03:00 | 173 | 173
2020-02-05 03:30 | 173 | 173
2020-02-05 04:00 | 173 | 173
2020-02-05 04:30 | 176 | 175
2020-02-05 05:00 | 182 | 182
2020-02-05 05:30 | 195 | 195
2020-02-05 06:00 | 206 | 206
2020-02-05 06:30 | 228 | 227
2020-02-05 07:00 | 242 | 241
2020-02-05 07:30 | 263 | 262
2020-02-05 08:00 | 284 | 284
2020-02-05 08:30 | 296 | 296
2020-02-05 09:00 | 304 | 303
2020-02-05 09:30 | 313 | 312
2020-02-05 10:00 | 311 | 310
2020-02-05 10:30 | 305 | 304
2020-02-05 11:00 | 279 | 279
2020-02-05 11:30 | 253 | 253
2020-02-05 12:00 | 283 | 282
2020-02-05 12:30 | 294 | 293
2020-02-05 13:00 | 291 | 290
2020-02-05 13:30 | 298 | 297
2020-02-05 14:00 | 290 | 289
2020-02-05 14:30 | 279 | 279
2020-02-05 15:00 | 281 | 281
2020-02-05 15:30 | 278 | 278
2020-02-05 16:00 | 269 | 269
2020-02-05 16:30 | 271 | 271
2020-02-05 17:00 | 286 | 286
2020-02-05 17:30 | 289 | 289
2020-02-05 18:00 | 288 | 288
2020-02-05 18:30 | 285 | 285
2020-02-05 19:00 | 291 | 291
2020-02-05 19:30 | 287 | 287
2020-02-05 20:00 | 282 | 282
2020-02-05 20:30 | 275 | 275
2020-02-05 21:00 | 262 | 262
2020-02-05 21:30 | 251 | 248
2020-02-05 22:00 | 241 | 238
2020-02-05 22:30 | 235 | 233
2020-02-05 23:00 | 229 | 228
2020-02-05 23:30 | 213 | 212
2020-02-06 | 196 | 196
2020-02-06 00:30 | 183 | 183
2020-02-06 01:00 | 177 | 177
2020-02-06 01:30 | 172 | 172
2020-02-06 02:00 | 169 | 169
2020-02-06 02:30 | 167 | 167
2020-02-06 03:00 | 167 | 167
2020-02-06 03:30 | 169 | 169
2020-02-06 04:00 | 169 | 169
2020-02-06 04:30 | 172 | 172
2020-02-06 05:00 | 179 | 179
2020-02-06 05:30 | 192 | 192
2020-02-06 06:00 | 203 | 202
2020-02-06 06:30 | 224 | 222
2020-02-06 07:00 | 246 | 246
2020-02-06 07:30 | 267 | 266
2020-02-06 08:00 | 271 | 270
2020-02-06 08:30 | 269 | 268
2020-02-06 09:00 | 273 | 272
2020-02-06 09:30 | 279 | 278
2020-02-06 10:00 | 273 | 272
2020-02-06 10:30 | 265 | 264
2020-02-06 11:00 | 263 | 263
2020-02-06 11:30 | 254 | 253
2020-02-06 12:00 | 239 | 238
2020-02-06 12:30 | 234 | 234
2020-02-06 13:00 | 256 | 255
2020-02-06 13:30 | 266 | 265
2020-02-06 14:00 | 272 | 271
2020-02-06 14:30 | 272 | 272
2020-02-06 15:00 | 270 | 270
2020-02-06 15:30 | 269 | 269
2020-02-06 16:00 | 278 | 278
2020-02-06 16:30 | 285 | 285
2020-02-06 17:00 | 291 | 291
2020-02-06 17:30 | 294 | 293
2020-02-06 18:00 | 291 | 291
2020-02-06 18:30 | 290 | 290
2020-02-06 19:00 | 295 | 295
2020-02-06 19:30 | 290 | 290
2020-02-06 20:00 | 287 | 287
2020-02-06 20:30 | 281 | 281
2020-02-06 21:00 | 269 | 269
2020-02-06 21:30 | 256 | 256
2020-02-06 22:00 | 246 | 245
2020-02-06 22:30 | 239 | 238
2020-02-06 23:00 | 232 | 232
2020-02-06 23:30 | 217 | 217
2020-02-07 | 200 | 200
2020-02-07 00:30 | 187 | 187
2020-02-07 01:00 | 178 | 178
2020-02-07 01:30 | 174 | 173
2020-02-07 02:00 | 171 | 170
2020-02-07 02:30 | 170 | 170
2020-02-07 03:00 | 168 | 168
2020-02-07 03:30 | 170 | 170
2020-02-07 04:00 | 170 | 170
2020-02-07 04:30 | 174 | 173
2020-02-07 05:00 | 180 | 180
2020-02-07 05:30 | 193 | 193
2020-02-07 06:00 | 204 | 204
2020-02-07 06:30 | 228 | 228
2020-02-07 07:00 | 249 | 248
2020-02-07 07:30 | 263 | 263
2020-02-07 08:00 | 265 | 264
2020-02-07 08:30 | 255 | 255
2020-02-07 09:00 | 242 | 242
2020-02-07 09:30 | 226 | 226
2020-02-07 10:00 | 225 | 225
2020-02-07 10:30 | 241 | 241
2020-02-07 11:00 | 242 | 242
2020-02-07 11:30 | 238 | 237
2020-02-07 12:00 | 241 | 241
2020-02-07 12:30 | 236 | 236
2020-02-07 13:00 | 236 | 236
2020-02-07 13:30 | 237 | 237
2020-02-07 14:00 | 249 | 248
2020-02-07 14:30 | 265 | 265
2020-02-07 15:00 | 274 | 273
2020-02-07 15:30 | 283 | 282
2020-02-07 16:00 | 292 | 291
2020-02-07 16:30 | 298 | 297
2020-02-07 17:00 | 301 | 301
2020-02-07 17:30 | 305 | 305
2020-02-07 18:00 | 306 | 306
2020-02-07 18:30 | 303 | 303
2020-02-07 19:00 | 308 | 307
2020-02-07 19:30 | 306 | 306
2020-02-07 20:00 | 302 | 302
2020-02-07 20:30 | 294 | 294
2020-02-07 21:00 | 283 | 283
2020-02-07 21:30 | 272 | 272
2020-02-07 22:00 | 262 | 262
2020-02-07 22:30 | 255 | 255
2020-02-07 23:00 | 248 | 247
2020-02-07 23:30 | 232 | 232
2020-02-08 | 214 | 214
2020-02-08 00:30 | 199 | 199
2020-02-08 01:00 | 190 | 190
2020-02-08 01:30 | 185 | 185
2020-02-08 02:00 | 180 | 180
2020-02-08 02:30 | 176 | 176
2020-02-08 03:00 | 174 | 174
2020-02-08 03:30 | 174 | 174
2020-02-08 04:00 | 173 | 173
2020-02-08 04:30 | 174 | 174
2020-02-08 05:00 | 175 | 175
2020-02-08 05:30 | 179 | 179
2020-02-08 06:00 | 181 | 181
2020-02-08 06:30 | 189 | 189
2020-02-08 07:00 | 193 | 193
2020-02-08 07:30 | 205 | 205
2020-02-08 08:00 | 221 | 221
2020-02-08 08:30 | 238 | 237
2020-02-08 09:00 | 242 | 241
2020-02-08 09:30 | 233 | 233
2020-02-08 10:00 | 215 | 215
2020-02-08 10:30 | 201 | 200
2020-02-08 11:00 | 211 | 211
2020-02-08 11:30 | 213 | 213
2020-02-08 12:00 | 220 | 220
2020-02-08 12:30 | 223 | 223
2020-02-08 13:00 | 216 | 216
2020-02-08 13:30 | 228 | 228
2020-02-08 14:00 | 232 | 232
2020-02-08 14:30 | 242 | 242
2020-02-08 15:00 | 242 | 242
2020-02-08 15:30 | 250 | 250
2020-02-08 16:00 | 256 | 256
2020-02-08 16:30 | 257 | 257
2020-02-08 17:00 | 270 | 270
2020-02-08 17:30 | 273 | 273
2020-02-08 18:00 | 274 | 274
2020-02-08 18:30 | 278 | 278
2020-02-08 19:00 | 286 | 286
2020-02-08 19:30 | 284 | 284
2020-02-08 20:00 | 280 | 280
2020-02-08 20:30 | 274 | 274
2020-02-08 21:00 | 264 | 263
2020-02-08 21:30 | 256 | 256
2020-02-08 22:00 | 249 | 249
2020-02-08 22:30 | 246 | 246
2020-02-08 23:00 | 243 | 243
2020-02-08 23:30 | 231 | 231
2020-02-09 | 212 | 212
2020-02-09 00:30 | 198 | 198
2020-02-09 01:00 | 190 | 190
2020-02-09 01:30 | 184 | 184
2020-02-09 02:00 | 179 | 179
2020-02-09 02:30 | 175 | 174
2020-02-09 03:00 | 171 | 171
2020-02-09 03:30 | 170 | 170
2020-02-09 04:00 | 170 | 170
2020-02-09 04:30 | 169 | 169
2020-02-09 05:00 | 170 | 170
2020-02-09 05:30 | 171 | 171
2020-02-09 06:00 | 171 | 171
2020-02-09 06:30 | 177 | 177
2020-02-09 07:00 | 180 | 180
2020-02-09 07:30 | 182 | 182
2020-02-09 08:00 | 189 | 189
2020-02-09 08:30 | 196 | 196
2020-02-09 09:00 | 188 | 188
2020-02-09 09:30 | 184 | 184
2020-02-09 10:00 | 209 | 209
2020-02-09 10:30 | 240 | 239
2020-02-09 11:00 | 259 | 259
2020-02-09 11:30 | 269 | 269
2020-02-09 12:00 | 263 | 262
2020-02-09 12:30 | 234 | 232
2020-02-09 13:00 | 189 | 184
2020-02-09 13:30 | 190 | 185
2020-02-09 14:00 | 213 | 211
2020-02-09 14:30 | 221 | 218
2020-02-09 15:00 | 237 | 236
2020-02-09 15:30 | 261 | 260
2020-02-09 16:00 | 266 | 266
2020-02-09 16:30 | 267 | 266
2020-02-09 17:00 | 274 | 274
2020-02-09 17:30 | 283 | 283
2020-02-09 18:00 | 283 | 283
2020-02-09 18:30 | 288 | 287
2020-02-09 19:00 | 297 | 297
2020-02-09 19:30 | 298 | 298
2020-02-09 20:00 | 294 | 294
2020-02-09 20:30 | 287 | 287
2020-02-09 21:00 | 275 | 275
2020-02-09 21:30 | 264 | 264
2020-02-09 22:00 | 252 | 252
2020-02-09 22:30 | 246 | 246
2020-02-09 23:00 | 241 | 240
2020-02-09 23:30 | 227 | 226
2020-02-10 | 210 | 210
2020-02-10 00:30 | 196 | 196
2020-02-10 01:00 | 189 | 189
2020-02-10 01:30 | 186 | 186
2020-02-10 02:00 | 183 | 183
2020-02-10 02:30 | 180 | 179
2020-02-10 03:00 | 177 | 177
2020-02-10 03:30 | 176 | 176
2020-02-10 04:00 | 176 | 176
2020-02-10 04:30 | 179 | 179
2020-02-10 05:00 | 185 | 185
2020-02-10 05:30 | 198 | 198
2020-02-10 06:00 | 209 | 209
2020-02-10 06:30 | 230 | 230
2020-02-10 07:00 | 247 | 247
2020-02-10 07:30 | 261 | 260
2020-02-10 08:00 | 264 | 263
2020-02-10 08:30 | 262 | 261
2020-02-10 09:00 | 260 | 260
2020-02-10 09:30 | 263 | 262
2020-02-10 10:00 | 271 | 271
2020-02-10 10:30 | 284 | 283
2020-02-10 11:00 | 287 | 285
2020-02-10 11:30 | 276 | 274
2020-02-10 12:00 | 279 | 277
2020-02-10 12:30 | 283 | 281
2020-02-10 13:00 | 282 | 280
2020-02-10 13:30 | 278 | 275
2020-02-10 14:00 | 271 | 269
2020-02-10 14:30 | 287 | 284
2020-02-10 15:00 | 305 | 303
2020-02-10 15:30 | 331 | 330
2020-02-10 16:00 | 360 | 360
2020-02-10 16:30 | 359 | 359
2020-02-10 17:00 | 356 | 356
2020-02-10 17:30 | 359 | 359
2020-02-10 18:00 | 358 | 358
2020-02-10 18:30 | 351 | 351
2020-02-10 19:00 | 355 | 355
2020-02-10 19:30 | 349 | 349
2020-02-10 20:00 | 341 | 341
2020-02-10 20:30 | 331 | 331
2020-02-10 21:00 | 313 | 312
2020-02-10 21:30 | 297 | 296
2020-02-10 22:00 | 284 | 284
2020-02-10 22:30 | 271 | 269
2020-02-10 23:00 | 261 | 259
2020-02-10 23:30 | 243 | 241
2020-02-11 | 224 | 223
2020-02-11 00:30 | 209 | 209
2020-02-11 01:00 | 200 | 200
2020-02-11 01:30 | 194 | 194
2020-02-11 02:00 | 191 | 191
2020-02-11 02:30 | 189 | 188
2020-02-11 03:00 | 186 | 186
2020-02-11 03:30 | 187 | 186
2020-02-11 04:00 | 186 | 186
2020-02-11 04:30 | 189 | 189
2020-02-11 05:00 | 194 | 194
2020-02-11 05:30 | 205 | 205
2020-02-11 06:00 | 216 | 216
2020-02-11 06:30 | 235 | 234
2020-02-11 07:00 | 257 | 256
2020-02-11 07:30 | 276 | 276
2020-02-11 08:00 | 279 | 279
2020-02-11 08:30 | 274 | 274
2020-02-11 09:00 | 269 | 269
2020-02-11 09:30 | 271 | 271
2020-02-11 10:00 | 269 | 269
2020-02-11 10:30 | 284 | 284
2020-02-11 11:00 | 283 | 283
2020-02-11 11:30 | 291 | 291
2020-02-11 12:00 | 301 | 301
2020-02-11 12:30 | 289 | 289
2020-02-11 13:00 | 291 | 291
2020-02-11 13:30 | 304 | 303
2020-02-11 14:00 | 313 | 313
2020-02-11 14:30 | 313 | 313
2020-02-11 15:00 | 314 | 313
2020-02-11 15:30 | 315 | 315
2020-02-11 16:00 | 336 | 336
2020-02-11 16:30 | 357 | 356
2020-02-11 17:00 | 359 | 358
2020-02-11 17:30 | 358 | 358
2020-02-11 18:00 | 364 | 363
2020-02-11 18:30 | 365 | 364
2020-02-11 19:00 | 375 | 373
2020-02-11 19:30 | 369 | 368
2020-02-11 20:00 | 360 | 358
2020-02-11 20:30 | 348 | 347
2020-02-11 21:00 | 330 | 329
2020-02-11 21:30 | 313 | 313
2020-02-11 22:00 | 298 | 298
2020-02-11 22:30 | 284 | 283
2020-02-11 23:00 | 273 | 271
2020-02-11 23:30 | 254 | 252
2020-02-12 | 233 | 233
2020-02-12 00:30 | 217 | 217
2020-02-12 01:00 | 208 | 208
2020-02-12 01:30 | 203 | 203
2020-02-12 02:00 | 199 | 198
2020-02-12 02:30 | 195 | 195
2020-02-12 03:00 | 193 | 193
2020-02-12 03:30 | 192 | 192
2020-02-12 04:00 | 192 | 192
2020-02-12 04:30 | 196 | 196
2020-02-12 05:00 | 202 | 202
2020-02-12 05:30 | 215 | 214
2020-02-12 06:00 | 225 | 225
2020-02-12 06:30 | 248 | 247
2020-02-12 07:00 | 269 | 269
2020-02-12 07:30 | 292 | 291
2020-02-12 08:00 | 306 | 305
2020-02-12 08:30 | 312 | 312
2020-02-12 09:00 | 306 | 305
2020-02-12 09:30 | 294 | 294
2020-02-12 10:00 | 290 | 290
2020-02-12 10:30 | 302 | 302
2020-02-12 11:00 | 306 | 306
2020-02-12 11:30 | 296 | 296
2020-02-12 12:00 | 273 | 273
2020-02-12 12:30 | 276 | 276
2020-02-12 13:00 | 291 | 291
2020-02-12 13:30 | 294 | 294
2020-02-12 14:00 | 301 | 301
2020-02-12 14:30 | 298 | 298
2020-02-12 15:00 | 300 | 300
2020-02-12 15:30 | 304 | 304
2020-02-12 16:00 | 312 | 312
2020-02-12 16:30 | 322 | 322
2020-02-12 17:00 | 332 | 332
2020-02-12 17:30 | 332 | 332
2020-02-12 18:00 | 329 | 329
2020-02-12 18:30 | 326 | 326
2020-02-12 19:00 | 328 | 328
2020-02-12 19:30 | 321 | 321
2020-02-12 20:00 | 315 | 315
2020-02-12 20:30 | 309 | 309
2020-02-12 21:00 | 292 | 292
2020-02-12 21:30 | 280 | 280
2020-02-12 22:00 | 269 | 268
2020-02-12 22:30 | 260 | 259
2020-02-12 23:00 | 255 | 253
2020-02-12 23:30 | 235 | 235
2020-02-13 | 218 | 218
2020-02-13 00:30 | 203 | 203
2020-02-13 01:00 | 193 | 193
2020-02-13 01:30 | 188 | 188
2020-02-13 02:00 | 185 | 185
2020-02-13 02:30 | 183 | 183
2020-02-13 03:00 | 182 | 182
2020-02-13 03:30 | 183 | 183
2020-02-13 04:00 | 184 | 184
2020-02-13 04:30 | 186 | 186
2020-02-13 05:00 | 193 | 192
2020-02-13 05:30 | 206 | 206
2020-02-13 06:00 | 216 | 216
2020-02-13 06:30 | 237 | 236
2020-02-13 07:00 | 259 | 258
2020-02-13 07:30 | 275 | 273
2020-02-13 08:00 | 281 | 280
2020-02-13 08:30 | 281 | 280
2020-02-13 09:00 | 282 | 282
2020-02-13 09:30 | 290 | 289
2020-02-13 10:00 | 293 | 292
2020-02-13 10:30 | 292 | 291
2020-02-13 11:00 | 288 | 288
2020-02-13 11:30 | 287 | 286
2020-02-13 12:00 | 291 | 290
2020-02-13 12:30 | 297 | 296
2020-02-13 13:00 | 299 | 299
2020-02-13 13:30 | 302 | 301
2020-02-13 14:00 | 295 | 295
2020-02-13 14:30 | 287 | 287
2020-02-13 15:00 | 287 | 287
2020-02-13 15:30 | 293 | 293
2020-02-13 16:00 | 295 | 295
2020-02-13 16:30 | 298 | 297
2020-02-13 17:00 | 302 | 302
2020-02-13 17:30 | 302 | 301
2020-02-13 18:00 | 305 | 305
2020-02-13 18:30 | 307 | 307
2020-02-13 19:00 | 315 | 314
2020-02-13 19:30 | 309 | 308
2020-02-13 20:00 | 304 | 304
2020-02-13 20:30 | 298 | 298
2020-02-13 21:00 | 285 | 285
2020-02-13 21:30 | 272 | 272
2020-02-13 22:00 | 259 | 259
2020-02-13 22:30 | 252 | 252
2020-02-13 23:00 | 246 | 246
2020-02-13 23:30 | 232 | 231
2020-02-14 | 213 | 213
2020-02-14 00:30 | 200 | 200
2020-02-14 01:00 | 191 | 191
2020-02-14 01:30 | 185 | 185
2020-02-14 02:00 | 181 | 180
2020-02-14 02:30 | 177 | 177
2020-02-14 03:00 | 175 | 175
2020-02-14 03:30 | 176 | 175
2020-02-14 04:00 | 176 | 176
2020-02-14 04:30 | 180 | 180
2020-02-14 05:00 | 185 | 185
2020-02-14 05:30 | 196 | 196
2020-02-14 06:00 | 207 | 207
2020-02-14 06:30 | 225 | 225
2020-02-14 07:00 | 241 | 240
2020-02-14 07:30 | 252 | 249
2020-02-14 08:00 | 246 | 243
2020-02-14 08:30 | 244 | 241
2020-02-14 09:00 | 238 | 237
2020-02-14 09:30 | 235 | 234
2020-02-14 10:00 | 236 | 235
2020-02-14 10:30 | 236 | 235
2020-02-14 11:00 | 240 | 238
2020-02-14 11:30 | 250 | 248
2020-02-14 12:00 | 254 | 252
2020-02-14 12:30 | 254 | 253
2020-02-14 13:00 | 265 | 264
2020-02-14 13:30 | 283 | 281
2020-02-14 14:00 | 299 | 296
2020-02-14 14:30 | 308 | 305
2020-02-14 15:00 | 304 | 301
2020-02-14 15:30 | 306 | 304
2020-02-14 16:00 | 314 | 311
2020-02-14 16:30 | 327 | 324
2020-02-14 17:00 | 336 | 334
2020-02-14 17:30 | 335 | 333
2020-02-14 18:00 | 330 | 328
2020-02-14 18:30 | 324 | 323
2020-02-14 19:00 | 327 | 326
2020-02-14 19:30 | 326 | 325
2020-02-14 20:00 | 320 | 319
2020-02-14 20:30 | 311 | 311
2020-02-14 21:00 | 298 | 298
2020-02-14 21:30 | 285 | 285
2020-02-14 22:00 | 275 | 275
2020-02-14 22:30 | 268 | 268
2020-02-14 23:00 | 261 | 261
2020-02-14 23:30 | 244 | 243
2020-02-15 | 225 | 224
2020-02-15 00:30 | 210 | 209
2020-02-15 01:00 | 200 | 200
2020-02-15 01:30 | 195 | 195
2020-02-15 02:00 | 190 | 190
2020-02-15 02:30 | 186 | 186
2020-02-15 03:00 | 185 | 185
2020-02-15 03:30 | 183 | 183
2020-02-15 04:00 | 181 | 181
2020-02-15 04:30 | 181 | 181
2020-02-15 05:00 | 181 | 181
2020-02-15 05:30 | 183 | 183
2020-02-15 06:00 | 184 | 184
2020-02-15 06:30 | 188 | 188
2020-02-15 07:00 | 194 | 194
2020-02-15 07:30 | 199 | 198
2020-02-15 08:00 | 205 | 203
2020-02-15 08:30 | 211 | 211
2020-02-15 09:00 | 207 | 207
2020-02-15 09:30 | 212 | 211
2020-02-15 10:00 | 222 | 222
2020-02-15 10:30 | 230 | 229
2020-02-15 11:00 | 235 | 235
2020-02-15 11:30 | 237 | 237
2020-02-15 12:00 | 242 | 242
2020-02-15 12:30 | 256 | 256
2020-02-15 13:00 | 267 | 267
2020-02-15 13:30 | 267 | 267
2020-02-15 14:00 | 275 | 274
2020-02-15 14:30 | 282 | 282
2020-02-15 15:00 | 296 | 296
2020-02-15 15:30 | 314 | 313
2020-02-15 16:00 | 332 | 332
2020-02-15 16:30 | 347 | 347
2020-02-15 17:00 | 361 | 361
2020-02-15 17:30 | 366 | 366
2020-02-15 18:00 | 367 | 367
2020-02-15 18:30 | 367 | 367
2020-02-15 19:00 | 368 | 367
2020-02-15 19:30 | 366 | 366
2020-02-15 20:00 | 360 | 360
2020-02-15 20:30 | 350 | 350
2020-02-15 21:00 | 334 | 333
2020-02-15 21:30 | 321 | 321
2020-02-15 22:00 | 305 | 305
2020-02-15 22:30 | 293 | 293
2020-02-15 23:00 | 283 | 282
2020-02-15 23:30 | 266 | 265
2020-02-16 | 247 | 246
2020-02-16 00:30 | 231 | 230
2020-02-16 01:00 | 220 | 219
2020-02-16 01:30 | 211 | 211
2020-02-16 02:00 | 205 | 205
2020-02-16 02:30 | 200 | 200
2020-02-16 03:00 | 197 | 197
2020-02-16 03:30 | 194 | 194
2020-02-16 04:00 | 192 | 192
2020-02-16 04:30 | 190 | 190
2020-02-16 05:00 | 190 | 190
2020-02-16 05:30 | 190 | 190
2020-02-16 06:00 | 188 | 188
2020-02-16 06:30 | 190 | 190
2020-02-16 07:00 | 191 | 191
2020-02-16 07:30 | 196 | 195
2020-02-16 08:00 | 204 | 203
2020-02-16 08:30 | 214 | 212
2020-02-16 09:00 | 224 | 224
2020-02-16 09:30 | 233 | 233
2020-02-16 10:00 | 240 | 240
2020-02-16 10:30 | 248 | 248
2020-02-16 11:00 | 255 | 254
2020-02-16 11:30 | 260 | 259
2020-02-16 12:00 | 268 | 267
2020-02-16 12:30 | 274 | 273
2020-02-16 13:00 | 280 | 279
2020-02-16 13:30 | 288 | 286
2020-02-16 14:00 | 295 | 293
2020-02-16 14:30 | 306 | 305
2020-02-16 15:00 | 320 | 320
2020-02-16 15:30 | 336 | 336
2020-02-16 16:00 | 351 | 351
2020-02-16 16:30 | 367 | 367
2020-02-16 17:00 | 381 | 381
2020-02-16 17:30 | 388 | 388
2020-02-16 18:00 | 387 | 387
2020-02-16 18:30 | 383 | 383
2020-02-16 19:00 | 384 | 384
2020-02-16 19:30 | 379 | 379
2020-02-16 20:00 | 370 | 370
2020-02-16 20:30 | 357 | 357
2020-02-16 21:00 | 334 | 334
2020-02-16 21:30 | 317 | 317
2020-02-16 22:00 | 299 | 299
2020-02-16 22:30 | 285 | 285
2020-02-16 23:00 | 274 | 274
2020-02-16 23:30 | 255 | 255
2020-02-17 | 234 | 234
2020-02-17 00:30 | 219 | 218
2020-02-17 01:00 | 210 | 210
2020-02-17 01:30 | 204 | 204
2020-02-17 02:00 | 201 | 200
2020-02-17 02:30 | 199 | 198
2020-02-17 03:00 | 196 | 195
2020-02-17 03:30 | 197 | 196
2020-02-17 04:00 | 197 | 196
2020-02-17 04:30 | 198 | 197
2020-02-17 05:00 | 203 | 202
2020-02-17 05:30 | 214 | 213
2020-02-17 06:00 | 225 | 225
2020-02-17 06:30 | 246 | 245
2020-02-17 07:00 | 263 | 262
2020-02-17 07:30 | 280 | 280
2020-02-17 08:00 | 287 | 287
2020-02-17 08:30 | 288 | 288
2020-02-17 09:00 | 286 | 286
2020-02-17 09:30 | 288 | 288
2020-02-17 10:00 | 289 | 289
2020-02-17 10:30 | 295 | 294
2020-02-17 11:00 | 296 | 296
2020-02-17 11:30 | 299 | 298
2020-02-17 12:00 | 303 | 302
2020-02-17 12:30 | 302 | 301
2020-02-17 13:00 | 307 | 307
2020-02-17 13:30 | 315 | 315
2020-02-17 14:00 | 323 | 323
2020-02-17 14:30 | 332 | 332
2020-02-17 15:00 | 339 | 339
2020-02-17 15:30 | 352 | 352
2020-02-17 16:00 | 372 | 372
2020-02-17 16:30 | 391 | 390
2020-02-17 17:00 | 407 | 407
2020-02-17 17:30 | 412 | 412
2020-02-17 18:00 | 410 | 410
2020-02-17 18:30 | 403 | 403
2020-02-17 19:00 | 406 | 406
2020-02-17 19:30 | 399 | 399
2020-02-17 20:00 | 388 | 388
2020-02-17 20:30 | 374 | 374
2020-02-17 21:00 | 353 | 353
2020-02-17 21:30 | 330 | 329
2020-02-17 22:00 | 311 | 311
2020-02-17 22:30 | 295 | 295
2020-02-17 23:00 | 282 | 282
2020-02-17 23:30 | 263 | 262
2020-02-18 | 244 | 243
2020-02-18 00:30 | 227 | 227
2020-02-18 01:00 | 218 | 218
2020-02-18 01:30 | 211 | 211
2020-02-18 02:00 | 207 | 207
2020-02-18 02:30 | 204 | 203
2020-02-18 03:00 | 201 | 201
2020-02-18 03:30 | 200 | 200
2020-02-18 04:00 | 198 | 198
2020-02-18 04:30 | 201 | 201
2020-02-18 05:00 | 206 | 206
2020-02-18 05:30 | 217 | 217
2020-02-18 06:00 | 227 | 227
2020-02-18 06:30 | 246 | 246
2020-02-18 07:00 | 266 | 266
2020-02-18 07:30 | 278 | 278
2020-02-18 08:00 | 279 | 279
2020-02-18 08:30 | 280 | 280
2020-02-18 09:00 | 287 | 287
2020-02-18 09:30 | 290 | 290
2020-02-18 10:00 | 292 | 292
2020-02-18 10:30 | 294 | 294
2020-02-18 11:00 | 296 | 296
2020-02-18 11:30 | 298 | 298
2020-02-18 12:00 | 305 | 304
2020-02-18 12:30 | 315 | 315
2020-02-18 13:00 | 321 | 321
2020-02-18 13:30 | 329 | 328
2020-02-18 14:00 | 341 | 341
2020-02-18 14:30 | 350 | 350
2020-02-18 15:00 | 355 | 355
2020-02-18 15:30 | 368 | 367
2020-02-18 16:00 | 392 | 391
2020-02-18 16:30 | 414 | 412
2020-02-18 17:00 | 434 | 434
2020-02-18 17:30 | 441 | 441
2020-02-18 18:00 | 440 | 440
2020-02-18 18:30 | 432 | 431
2020-02-18 19:00 | 437 | 436
2020-02-18 19:30 | 432 | 432
2020-02-18 20:00 | 421 | 421
2020-02-18 20:30 | 405 | 405
2020-02-18 21:00 | 382 | 382
2020-02-18 21:30 | 362 | 362
2020-02-18 22:00 | 341 | 341
2020-02-18 22:30 | 324 | 324
2020-02-18 23:00 | 309 | 308
2020-02-18 23:30 | 285 | 285
2020-02-19 | 265 | 265
2020-02-19 00:30 | 247 | 246
2020-02-19 01:00 | 238 | 237
2020-02-19 01:30 | 231 | 230
2020-02-19 02:00 | 227 | 226
2020-02-19 02:30 | 223 | 223
2020-02-19 03:00 | 221 | 220
2020-02-19 03:30 | 219 | 219
2020-02-19 04:00 | 218 | 218
2020-02-19 04:30 | 221 | 220
2020-02-19 05:00 | 224 | 224
2020-02-19 05:30 | 235 | 234
2020-02-19 06:00 | 244 | 243
2020-02-19 06:30 | 262 | 261
2020-02-19 07:00 | 281 | 280
2020-02-19 07:30 | 302 | 301
2020-02-19 08:00 | 304 | 304
2020-02-19 08:30 | 290 | 290
2020-02-19 09:00 | 285 | 285
2020-02-19 09:30 | 292 | 291
2020-02-19 10:00 | 294 | 293
2020-02-19 10:30 | 296 | 296
2020-02-19 11:00 | 305 | 304
2020-02-19 11:30 | 318 | 317
2020-02-19 12:00 | 326 | 325
2020-02-19 12:30 | 334 | 332
2020-02-19 13:00 | 351 | 348
2020-02-19 13:30 | 373 | 373
2020-02-19 14:00 | 378 | 378
2020-02-19 14:30 | 386 | 385
2020-02-19 15:00 | 393 | 392
2020-02-19 15:30 | 404 | 403
2020-02-19 16:00 | 432 | 430
2020-02-19 16:30 | 448 | 446
2020-02-19 17:00 | 474 | 472
2020-02-19 17:30 | 485 | 484
2020-02-19 18:00 | 480 | 478
2020-02-19 18:30 | 466 | 465
2020-02-19 19:00 | 466 | 465
2020-02-19 19:30 | 454 | 454
2020-02-19 20:00 | 436 | 436
2020-02-19 20:30 | 424 | 424
2020-02-19 21:00 | 398 | 398
2020-02-19 21:30 | 363 | 362
2020-02-19 22:00 | 340 | 339
2020-02-19 22:30 | 306 | 306
2020-02-19 23:00 | 292 | 292
2020-02-19 23:30 | 276 | 276
2020-02-20 | 257 | 256
2020-02-20 00:30 | 246 | 245
2020-02-20 01:00 | 242 | 241
2020-02-20 01:30 | 230 | 229
2020-02-20 02:00 | 220 | 219
2020-02-20 02:30 | 214 | 214
2020-02-20 03:00 | 211 | 211
2020-02-20 03:30 | 209 | 209
2020-02-20 04:00 | 207 | 207
2020-02-20 04:30 | 209 | 209
2020-02-20 05:00 | 213 | 213
2020-02-20 05:30 | 223 | 222
2020-02-20 06:00 | 232 | 231
2020-02-20 06:30 | 252 | 252
2020-02-20 07:00 | 268 | 268
2020-02-20 07:30 | 279 | 279
2020-02-20 08:00 | 279 | 279
2020-02-20 08:30 | 274 | 273
2020-02-20 09:00 | 273 | 273
2020-02-20 09:30 | 270 | 270
2020-02-20 10:00 | 267 | 267
2020-02-20 10:30 | 269 | 269
2020-02-20 11:00 | 271 | 270
2020-02-20 11:30 | 277 | 277
2020-02-20 12:00 | 284 | 283
2020-02-20 12:30 | 289 | 288
2020-02-20 13:00 | 300 | 299
2020-02-20 13:30 | 312 | 311
2020-02-20 14:00 | 322 | 321
2020-02-20 14:30 | 329 | 328
2020-02-20 15:00 | 338 | 336
2020-02-20 15:30 | 352 | 352
2020-02-20 16:00 | 371 | 371
2020-02-20 16:30 | 388 | 388
2020-02-20 17:00 | 403 | 403
2020-02-20 17:30 | 407 | 407
2020-02-20 18:00 | 403 | 403
2020-02-20 18:30 | 393 | 393
2020-02-20 19:00 | 397 | 396
2020-02-20 19:30 | 390 | 389
2020-02-20 20:00 | 380 | 380
2020-02-20 20:30 | 366 | 366
2020-02-20 21:00 | 346 | 346
2020-02-20 21:30 | 324 | 324
2020-02-20 22:00 | 304 | 304
2020-02-20 22:30 | 291 | 290
2020-02-20 23:00 | 277 | 277
2020-02-20 23:30 | 254 | 254
2020-02-21 | 236 | 236
2020-02-21 00:30 | 220 | 220
2020-02-21 01:00 | 212 | 212
2020-02-21 01:30 | 205 | 205
2020-02-21 02:00 | 201 | 201
2020-02-21 02:30 | 198 | 198
2020-02-21 03:00 | 195 | 195
2020-02-21 03:30 | 195 | 195
2020-02-21 04:00 | 195 | 195
2020-02-21 04:30 | 198 | 198
2020-02-21 05:00 | 202 | 202
2020-02-21 05:30 | 213 | 212
2020-02-21 06:00 | 220 | 220
2020-02-21 06:30 | 238 | 237
2020-02-21 07:00 | 253 | 253
2020-02-21 07:30 | 265 | 265
2020-02-21 08:00 | 267 | 266
2020-02-21 08:30 | 266 | 264
2020-02-21 09:00 | 268 | 267
2020-02-21 09:30 | 270 | 269
2020-02-21 10:00 | 267 | 266
2020-02-21 10:30 | 264 | 262
2020-02-21 11:00 | 267 | 266
2020-02-21 11:30 | 268 | 267
2020-02-21 12:00 | 268 | 268
2020-02-21 12:30 | 269 | 269
2020-02-21 13:00 | 273 | 273
2020-02-21 13:30 | 273 | 273
2020-02-21 14:00 | 280 | 280
2020-02-21 14:30 | 288 | 288
2020-02-21 15:00 | 298 | 298
2020-02-21 15:30 | 312 | 311
2020-02-21 16:00 | 330 | 329
2020-02-21 16:30 | 344 | 343
2020-02-21 17:00 | 351 | 350
2020-02-21 17:30 | 350 | 350
2020-02-21 18:00 | 345 | 344
2020-02-21 18:30 | 338 | 338
2020-02-21 19:00 | 342 | 342
2020-02-21 19:30 | 338 | 338
2020-02-21 20:00 | 332 | 331
2020-02-21 20:30 | 322 | 322
2020-02-21 21:00 | 307 | 307
2020-02-21 21:30 | 294 | 294
2020-02-21 22:00 | 281 | 280
2020-02-21 22:30 | 273 | 273
2020-02-21 23:00 | 264 | 263
2020-02-21 23:30 | 246 | 246
2020-02-22 | 227 | 227
2020-02-22 00:30 | 213 | 213
2020-02-22 01:00 | 204 | 204
2020-02-22 01:30 | 199 | 198
2020-02-22 02:00 | 194 | 194
2020-02-22 02:30 | 191 | 190
2020-02-22 03:00 | 188 | 187
2020-02-22 03:30 | 186 | 185
2020-02-22 04:00 | 185 | 183
2020-02-22 04:30 | 183 | 182
2020-02-22 05:00 | 185 | 184
2020-02-22 05:30 | 187 | 186
2020-02-22 06:00 | 188 | 187
2020-02-22 06:30 | 195 | 195
2020-02-22 07:00 | 198 | 198
2020-02-22 07:30 | 201 | 201
2020-02-22 08:00 | 201 | 201
2020-02-22 08:30 | 217 | 217
2020-02-22 09:00 | 210 | 210
2020-02-22 09:30 | 214 | 214
2020-02-22 10:00 | 205 | 205
2020-02-22 10:30 | 208 | 208
2020-02-22 11:00 | 215 | 215
2020-02-22 11:30 | 206 | 206
2020-02-22 12:00 | 210 | 210
2020-02-22 12:30 | 216 | 216
2020-02-22 13:00 | 220 | 220
2020-02-22 13:30 | 229 | 229
2020-02-22 14:00 | 237 | 237
2020-02-22 14:30 | 233 | 233
2020-02-22 15:00 | 222 | 222
2020-02-22 15:30 | 224 | 224
2020-02-22 16:00 | 233 | 233
2020-02-22 16:30 | 246 | 246
2020-02-22 17:00 | 251 | 250
2020-02-22 17:30 | 253 | 253
2020-02-22 18:00 | 259 | 258
2020-02-22 18:30 | 265 | 265
2020-02-22 19:00 | 277 | 276
2020-02-22 19:30 | 274 | 273
2020-02-22 20:00 | 270 | 269
2020-02-22 20:30 | 266 | 265
2020-02-22 21:00 | 256 | 256
2020-02-22 21:30 | 251 | 250
2020-02-22 22:00 | 243 | 243
2020-02-22 22:30 | 240 | 240
2020-02-22 23:00 | 237 | 237
2020-02-22 23:30 | 223 | 223
2020-02-23 | 208 | 207
2020-02-23 00:30 | 195 | 194
2020-02-23 01:00 | 188 | 187
2020-02-23 01:30 | 183 | 182
2020-02-23 02:00 | 178 | 177
2020-02-23 02:30 | 174 | 173
2020-02-23 03:00 | 172 | 172
2020-02-23 03:30 | 172 | 171
2020-02-23 04:00 | 169 | 168
2020-02-23 04:30 | 168 | 168
2020-02-23 05:00 | 169 | 168
2020-02-23 05:30 | 171 | 170
2020-02-23 06:00 | 171 | 170
2020-02-23 06:30 | 175 | 174
2020-02-23 07:00 | 173 | 172
2020-02-23 07:30 | 173 | 173
2020-02-23 08:00 | 178 | 178
2020-02-23 08:30 | 187 | 187
2020-02-23 09:00 | 197 | 197
2020-02-23 09:30 | 199 | 199
2020-02-23 10:00 | 200 | 200
2020-02-23 10:30 | 215 | 215
2020-02-23 11:00 | 219 | 218
2020-02-23 11:30 | 209 | 208
2020-02-23 12:00 | 209 | 209
2020-02-23 12:30 | 208 | 208
2020-02-23 13:00 | 205 | 205
2020-02-23 13:30 | 212 | 212
2020-02-23 14:00 | 219 | 219
2020-02-23 14:30 | 225 | 225
2020-02-23 15:00 | 222 | 222
2020-02-23 15:30 | 227 | 226
2020-02-23 16:00 | 234 | 234
2020-02-23 16:30 | 235 | 235
2020-02-23 17:00 | 243 | 243
2020-02-23 17:30 | 251 | 250
2020-02-23 18:00 | 259 | 258
2020-02-23 18:30 | 265 | 264
2020-02-23 19:00 | 274 | 273
2020-02-23 19:30 | 269 | 268
2020-02-23 20:00 | 265 | 264
2020-02-23 20:30 | 259 | 258
2020-02-23 21:00 | 248 | 247
2020-02-23 21:30 | 239 | 239
2020-02-23 22:00 | 229 | 229
2020-02-23 22:30 | 224 | 224
2020-02-23 23:00 | 220 | 220
2020-02-23 23:30 | 208 | 208
2020-02-24 | 193 | 193
2020-02-24 00:30 | 181 | 180
2020-02-24 01:00 | 174 | 174
2020-02-24 01:30 | 170 | 170
2020-02-24 02:00 | 167 | 166
2020-02-24 02:30 | 165 | 165
2020-02-24 03:00 | 164 | 164
2020-02-24 03:30 | 165 | 165
2020-02-24 04:00 | 166 | 166
2020-02-24 04:30 | 169 | 169
2020-02-24 05:00 | 176 | 176
2020-02-24 05:30 | 191 | 191
2020-02-24 06:00 | 202 | 202
2020-02-24 06:30 | 223 | 222
2020-02-24 07:00 | 240 | 239
2020-02-24 07:30 | 259 | 258
2020-02-24 08:00 | 265 | 264
2020-02-24 08:30 | 257 | 257
2020-02-24 09:00 | 256 | 255
2020-02-24 09:30 | 269 | 267
2020-02-24 10:00 | 282 | 280
2020-02-24 10:30 | 287 | 287
2020-02-24 11:00 | 274 | 274
2020-02-24 11:30 | 242 | 242
2020-02-24 12:00 | 257 | 257
2020-02-24 12:30 | 265 | 265
2020-02-24 13:00 | 253 | 253
2020-02-24 13:30 | 244 | 244
2020-02-24 14:00 | 241 | 241
2020-02-24 14:30 | 242 | 242
2020-02-24 15:00 | 248 | 248
2020-02-24 15:30 | 257 | 257
2020-02-24 16:00 | 277 | 277
2020-02-24 16:30 | 285 | 285
2020-02-24 17:00 | 297 | 297
2020-02-24 17:30 | 303 | 303
2020-02-24 18:00 | 307 | 307
2020-02-24 18:30 | 309 | 309
2020-02-24 19:00 | 317 | 317
2020-02-24 19:30 | 309 | 309
2020-02-24 20:00 | 302 | 302
2020-02-24 20:30 | 292 | 291
2020-02-24 21:00 | 277 | 276
2020-02-24 21:30 | 263 | 262
2020-02-24 22:00 | 252 | 251
2020-02-24 22:30 | 244 | 244
2020-02-24 23:00 | 238 | 237
2020-02-24 23:30 | 223 | 223
2020-02-25 | 206 | 206
2020-02-25 00:30 | 192 | 191
2020-02-25 01:00 | 184 | 184
2020-02-25 01:30 | 180 | 180
2020-02-25 02:00 | 176 | 176
2020-02-25 02:30 | 174 | 173
2020-02-25 03:00 | 172 | 171
2020-02-25 03:30 | 171 | 171
2020-02-25 04:00 | 172 | 172
2020-02-25 04:30 | 176 | 176
2020-02-25 05:00 | 183 | 183
2020-02-25 05:30 | 195 | 195
2020-02-25 06:00 | 206 | 206
2020-02-25 06:30 | 223 | 223
2020-02-25 07:00 | 235 | 234
2020-02-25 07:30 | 242 | 241
2020-02-25 08:00 | 239 | 238
2020-02-25 08:30 | 234 | 234
2020-02-25 09:00 | 234 | 234
2020-02-25 09:30 | 245 | 245
2020-02-25 10:00 | 244 | 244
2020-02-25 10:30 | 244 | 243
2020-02-25 11:00 | 247 | 246
2020-02-25 11:30 | 253 | 252
2020-02-25 12:00 | 260 | 259
2020-02-25 12:30 | 263 | 263
2020-02-25 13:00 | 270 | 270
2020-02-25 13:30 | 275 | 275
2020-02-25 14:00 | 282 | 282
2020-02-25 14:30 | 287 | 287
2020-02-25 15:00 | 290 | 290
2020-02-25 15:30 | 299 | 299
2020-02-25 16:00 | 303 | 303
2020-02-25 16:30 | 306 | 306
2020-02-25 17:00 | 315 | 314
2020-02-25 17:30 | 321 | 321
2020-02-25 18:00 | 323 | 323
2020-02-25 18:30 | 322 | 322
2020-02-25 19:00 | 331 | 330
2020-02-25 19:30 | 326 | 326
2020-02-25 20:00 | 321 | 321
2020-02-25 20:30 | 313 | 313
2020-02-25 21:00 | 296 | 296
2020-02-25 21:30 | 283 | 283
2020-02-25 22:00 | 270 | 270
2020-02-25 22:30 | 259 | 258
2020-02-25 23:00 | 251 | 251
2020-02-25 23:30 | 234 | 234
2020-02-26 | 215 | 215
2020-02-26 00:30 | 200 | 200
2020-02-26 01:00 | 192 | 192
2020-02-26 01:30 | 186 | 186
2020-02-26 02:00 | 183 | 183
2020-02-26 02:30 | 180 | 180
2020-02-26 03:00 | 178 | 178
2020-02-26 03:30 | 178 | 178
2020-02-26 04:00 | 179 | 179
2020-02-26 04:30 | 182 | 182
2020-02-26 05:00 | 188 | 188
2020-02-26 05:30 | 201 | 201
2020-02-26 06:00 | 212 | 212
2020-02-26 06:30 | 233 | 232
2020-02-26 07:00 | 245 | 243
2020-02-26 07:30 | 250 | 249
2020-02-26 08:00 | 247 | 247
2020-02-26 08:30 | 246 | 244
2020-02-26 09:00 | 249 | 246
2020-02-26 09:30 | 258 | 255
2020-02-26 10:00 | 260 | 260
2020-02-26 10:30 | 270 | 270
2020-02-26 11:00 | 282 | 281
2020-02-26 11:30 | 287 | 286
2020-02-26 12:00 | 279 | 278
2020-02-26 12:30 | 279 | 278
2020-02-26 13:00 | 293 | 291
2020-02-26 13:30 | 306 | 305
2020-02-26 14:00 | 315 | 313
2020-02-26 14:30 | 327 | 324
2020-02-26 15:00 | 333 | 331
2020-02-26 15:30 | 346 | 343
2020-02-26 16:00 | 363 | 360
2020-02-26 16:30 | 378 | 374
2020-02-26 17:00 | 383 | 382
2020-02-26 17:30 | 381 | 380
2020-02-26 18:00 | 376 | 376
2020-02-26 18:30 | 375 | 375
2020-02-26 19:00 | 386 | 385
2020-02-26 19:30 | 380 | 380
2020-02-26 20:00 | 373 | 373
2020-02-26 20:30 | 364 | 364
2020-02-26 21:00 | 344 | 344
2020-02-26 21:30 | 329 | 329
2020-02-26 22:00 | 311 | 310
2020-02-26 22:30 | 298 | 298
2020-02-26 23:00 | 287 | 286
2020-02-26 23:30 | 268 | 266
2020-02-27 | 247 | 246
2020-02-27 00:30 | 230 | 230
2020-02-27 01:00 | 221 | 218
2020-02-27 01:30 | 214 | 211
2020-02-27 02:00 | 209 | 206
2020-02-27 02:30 | 204 | 202
2020-02-27 03:00 | 202 | 199
2020-02-27 03:30 | 201 | 199
2020-02-27 04:00 | 200 | 198
2020-02-27 04:30 | 204 | 201
2020-02-27 05:00 | 210 | 207
2020-02-27 05:30 | 224 | 220
2020-02-27 06:00 | 232 | 230
2020-02-27 06:30 | 252 | 251
2020-02-27 07:00 | 268 | 268
2020-02-27 07:30 | 285 | 285
2020-02-27 08:00 | 287 | 286
2020-02-27 08:30 | 296 | 295
2020-02-27 09:00 | 337 | 337
2020-02-27 09:30 | 348 | 348
2020-02-27 10:00 | 343 | 342
2020-02-27 10:30 | 332 | 332
2020-02-27 11:00 | 306 | 306
2020-02-27 11:30 | 298 | 298
2020-02-27 12:00 | 292 | 292
2020-02-27 12:30 | 269 | 269
2020-02-27 13:00 | 287 | 287
2020-02-27 13:30 | 300 | 300
2020-02-27 14:00 | 310 | 310
2020-02-27 14:30 | 303 | 303
2020-02-27 15:00 | 290 | 290
2020-02-27 15:30 | 283 | 282
2020-02-27 16:00 | 290 | 290
2020-02-27 16:30 | 310 | 310
2020-02-27 17:00 | 335 | 335
2020-02-27 17:30 | 332 | 332
2020-02-27 18:00 | 328 | 328
2020-02-27 18:30 | 328 | 328
2020-02-27 19:00 | 336 | 335
2020-02-27 19:30 | 329 | 329
2020-02-27 20:00 | 320 | 320
2020-02-27 20:30 | 309 | 309
2020-02-27 21:00 | 292 | 292
2020-02-27 21:30 | 276 | 276
2020-02-27 22:00 | 260 | 260
2020-02-27 22:30 | 252 | 252
2020-02-27 23:00 | 243 | 243
2020-02-27 23:30 | 226 | 225
2020-02-28 | 207 | 206
2020-02-28 00:30 | 192 | 190
2020-02-28 01:00 | 185 | 183
2020-02-28 01:30 | 179 | 178
2020-02-28 02:00 | 175 | 174
2020-02-28 02:30 | 173 | 172
2020-02-28 03:00 | 171 | 170
2020-02-28 03:30 | 170 | 169
2020-02-28 04:00 | 171 | 170
2020-02-28 04:30 | 174 | 173
2020-02-28 05:00 | 180 | 179
2020-02-28 05:30 | 193 | 191
2020-02-28 06:00 | 201 | 199
2020-02-28 06:30 | 219 | 215
2020-02-28 07:00 | 234 | 228
2020-02-28 07:30 | 241 | 237
2020-02-28 08:00 | 237 | 234
2020-02-28 08:30 | 232 | 229
2020-02-28 09:00 | 229 | 227
2020-02-28 09:30 | 229 | 227
2020-02-28 10:00 | 230 | 227
2020-02-28 10:30 | 233 | 231
2020-02-28 11:00 | 240 | 239
2020-02-28 11:30 | 251 | 249
2020-02-28 12:00 | 255 | 252
2020-02-28 12:30 | 262 | 259
2020-02-28 13:00 | 269 | 265
2020-02-28 13:30 | 284 | 281
2020-02-28 14:00 | 303 | 302
2020-02-28 14:30 | 324 | 323
2020-02-28 15:00 | 350 | 348
2020-02-28 15:30 | 352 | 350
2020-02-28 16:00 | 349 | 348
2020-02-28 16:30 | 341 | 341
2020-02-28 17:00 | 341 | 340
2020-02-28 17:30 | 335 | 335
2020-02-28 18:00 | 329 | 329
2020-02-28 18:30 | 327 | 327
2020-02-28 19:00 | 335 | 334
2020-02-28 19:30 | 331 | 331
2020-02-28 20:00 | 326 | 326
2020-02-28 20:30 | 319 | 319
2020-02-28 21:00 | 306 | 306
2020-02-28 21:30 | 294 | 293
2020-02-28 22:00 | 282 | 281
2020-02-28 22:30 | 273 | 272
2020-02-28 23:00 | 262 | 262
2020-02-28 23:30 | 242 | 242
2020-02-29 | 223 | 223
2020-02-29 00:30 | 207 | 207
2020-02-29 01:00 | 198 | 198
2020-02-29 01:30 | 191 | 191
2020-02-29 02:00 | 186 | 186
2020-02-29 02:30 | 181 | 181
2020-02-29 03:00 | 179 | 179
2020-02-29 03:30 | 178 | 178
2020-02-29 04:00 | 176 | 176
2020-02-29 04:30 | 176 | 176
2020-02-29 05:00 | 176 | 176
2020-02-29 05:30 | 180 | 180
2020-02-29 06:00 | 180 | 180
2020-02-29 06:30 | 185 | 185
2020-02-29 07:00 | 185 | 185
2020-02-29 07:30 | 188 | 188
2020-02-29 08:00 | 192 | 192
2020-02-29 08:30 | 203 | 202
2020-02-29 09:00 | 205 | 205
2020-02-29 09:30 | 208 | 208
2020-02-29 10:00 | 205 | 204
2020-02-29 10:30 | 191 | 191
2020-02-29 11:00 | 195 | 195
2020-02-29 11:30 | 202 | 201
2020-02-29 12:00 | 208 | 207
2020-02-29 12:30 | 218 | 217
2020-02-29 13:00 | 231 | 230
2020-02-29 13:30 | 237 | 236
2020-02-29 14:00 | 233 | 232
2020-02-29 14:30 | 213 | 213
2020-02-29 15:00 | 216 | 216
2020-02-29 15:30 | 235 | 235
2020-02-29 16:00 | 252 | 251
2020-02-29 16:30 | 264 | 263
2020-02-29 17:00 | 279 | 278
2020-02-29 17:30 | 285 | 284
2020-02-29 18:00 | 284 | 284
2020-02-29 18:30 | 286 | 286
2020-02-29 19:00 | 294 | 293
2020-02-29 19:30 | 289 | 289
2020-02-29 20:00 | 283 | 283
2020-02-29 20:30 | 276 | 276
2020-02-29 21:00 | 263 | 263
2020-02-29 21:30 | 253 | 253
2020-02-29 22:00 | 243 | 243
2020-02-29 22:30 | 238 | 238
2020-02-29 23:00 | 233 | 233
2020-02-29 23:30 | 218 | 218
2020-03-01 | 203 | 203
Formulas:
Date/Time = [Date/Time, row above]+30/24/60

## 24. Historic ratings
PQ Rating (MVA) |  | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer | 2019 Winter | 2019/20 Summer
|  | 314 | 314 | 314 | 314 | 314 | 314
Transformers | H022T01 | 105 | 105 | 105 | 105 | 105 | 105
| H022T02 | 84 | 84 | 84 | 84 | 84 | 84
| H022T03 | 125 | 125 | 125 | 125 | 125 | 125

## 26. Unplanned outages
Unplanned Outage Date/Time | Element Affected | Element Type | Outage Cause | Outage Duration (mins) | Customer Outage Duration (mins) | MW Lost (Instantaneous) | MW Minutes
2017-08-18 07:10 | H022 110KV 7 CAPACITOR | CAPACITOR | HV Equipment malfunction or failure | 483.3333
2017-10-29 19:20 | 0792 - H022 Loganlea to H003 Belmont | FEEDER | Storm | 0.13333
2018-01-16 09:20 | 0792 - H022 Loganlea to H003 Belmont | FEEDER | HV Maint | 237.2
2018-05-10 07:27 | 8813 - H022 Loganlea to S003 Greenbank | FEEDER | HV Maint | 423.1
2018-08-17 16:02 | H022 110KV 4 CAPACITOR | CAPACITOR | HV Equipment malfunction or failure | 8665.85
2018-11-15 10:18 | H022 110KV 4 CAPACITOR | CAPACITOR | Sec Maint | 165.4333