## Cover Page
AER Rule | Field Name | Value(s)
1 | Constrained connection point ID | Mackay
2 | Constraint primary driver | Asset condition
3 | Constraint investment type | Asset renewal
4 | Constrained connection point latitude (decimal degrees) | -21.145
| Constrained connection point longitude (decimal degrees) | 149.159
5 | Affect on residential customers
| Annual Energy | Not available
| Maximum Demand | Not available
6,7 | Effect on industrial and commercial customers
| Annual Energy | Not available
| Maximum Demand | Not available
8 | Load profile (maximum day, MVA)
50% PoE
Load profile (minimum day, MVA)
Minimum demand data (MVA)
| Max. demand, maximum demand day (MVA) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| 10% PoE | 152.3014 | 149.908 | 149.2876 | 149.8817 | 150.7692 | 150.8565 | 150.2813 | 150.2224 | 150.2834 | 150.2981 | 150.0195
| 50% PoE | 144.831 | 142.555 | 141.965 | 142.53 | 143.374 | 143.457 | 142.91 | 142.854 | 142.912 | 142.926 | 142.661
9 | Max. demand, minimum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Maximum demand data | 47.515 | 47.531 | 47.548 | 47.565 | 47.597 | 47.627 | 47.651 | 47.679 | 47.71 | 47.781 | 47.791
10 | Load profile (maximum day, MW)
Load profile 50%
| Max. demand, maximum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| 10% PoE | 108.8354 | 107.1255 | 106.6817 | 107.1066 | 107.7407 | 107.8027 | 107.3926 | 107.3505 | 107.3937 | 107.4042 | 107.2044
| 50% PoE | 103.497 | 101.871 | 101.449 | 101.853 | 102.456 | 102.515 | 102.125 | 102.085 | 102.126 | 102.136 | 101.946
11 | Load profile (minimum day, MW)
Minimum demand data (MW)
| Min. demand, minimum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Mininum demand data | 1.476 | 1.475 | 1.442 | 1.422 | 1.402 | 1.382 | 1.364 | 1.344 | 1.321 | 1.294 | 1.277
12 | Voltage Level (kV) | 132/33
13 | Maximum load at risk per year | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Load at risk (MW, peak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1 | 8.9
| Load at risk (MVA, peak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 9.8
14 | Load duration curve
15 | Preferred investment | Mackay 132_33kV transformer replacement
16 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Capital cost ($m, nominal) | [9 empty] | 5
17 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Operating cost ($m, nominal) | [9 empty] | 0.1 | 0.1
18 | Preferred investment cost accuracy | 0.3
19 | Preferred investment proposed timing | 2030-06-30
20 | Demand reduction to defer the investment by 1 year
21 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Annual deferral value ($m, nominal)
22 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Load transfer capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Historic load trace
24 | Historic ratings
25 | Limitation asset | 132/33kV transformer
26 | Unplanned outages
27 | Maximum fault level (kA) | 6.8
28 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Economic cost ($m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | VCR ($m/MWh) | 0.04003
30 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Annual unserved energy (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 8. Load profile max (50% PoE)
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:30 | 72.345 | 72.349 | 72.353 | 72.357 | 72.365 | 72.374 | 72.379 | 72.386 | 72.393 | 72.41 | 72.412
1:00 | 70.239 | 70.242 | 70.247 | 70.251 | 70.259 | 70.266 | 70.272 | 70.278 | 70.285 | 70.302 | 70.303
1:30 | 70.059 | 70.063 | 70.068 | 70.072 | 70.079 | 70.087 | 70.092 | 70.099 | 70.105 | 70.122 | 70.124
2:00 | 68.719 | 68.723 | 68.727 | 68.731 | 68.739 | 68.747 | 68.751 | 68.758 | 68.764 | 68.781 | 68.782
2:30 | 68.248 | 68.253 | 68.258 | 68.263 | 68.272 | 68.281 | 68.286 | 68.294 | 68.302 | 68.322 | 68.322
3:00 | 67.661 | 67.663 | 67.667 | 67.67 | 67.677 | 67.683 | 67.687 | 67.692 | 67.697 | 67.711 | 67.711
3:30 | 66.289 | 66.294 | 66.299 | 66.304 | 66.313 | 66.323 | 66.329 | 66.337 | 66.345 | 66.365 | 66.366
4:00 | 64.826 | 64.832 | 64.838 | 64.844 | 64.855 | 64.865 | 64.872 | 64.881 | 64.89 | 64.914 | 64.915
4:30 | 65.137 | 65.143 | 65.149 | 65.154 | 65.166 | 65.176 | 65.183 | 65.191 | 65.2 | 65.223 | 65.224
5:00 | 66.403 | 66.407 | 66.411 | 66.415 | 66.422 | 66.429 | 66.435 | 66.441 | 66.448 | 66.465 | 66.468
5:30 | 69.577 | 69.58 | 69.583 | 69.587 | 69.593 | 69.6 | 69.605 | 69.612 | 69.619 | 69.636 | 69.641
6:00 | 72.665 | 72.668 | 72.672 | 72.676 | 72.684 | 72.692 | 72.7 | 72.71 | 72.722 | 72.745 | 72.758
6:30 | 83.424 | 83.38 | 83.354 | 83.341 | 83.335 | 83.329 | 83.324 | 83.321 | 83.317 | 83.331 | 83.329
7:00 | 90.755 | 90.646 | 90.573 | 90.526 | 90.48 | 90.437 | 90.4 | 90.362 | 90.319 | 90.269 | 90.252
7:30 | 102.253 | 102.029 | 101.872 | 101.77 | 101.665 | 101.563 | 101.476 | 101.386 | 101.28 | 101.143 | 101.094
8:00 | 108.015 | 107.614 | 107.336 | 107.159 | 106.976 | 106.8 | 106.647 | 106.486 | 106.298 | 106.065 | 105.967
8:30 | 109.559 | 108.834 | 108.325 | 107.998 | 107.649 | 107.313 | 107.017 | 106.704 | 106.334 | 105.856 | 105.648
9:00 | 113.714 | 112.788 | 112.132 | 111.706 | 111.246 | 110.799 | 110.408 | 109.989 | 109.493 | 108.832 | 108.546
9:30 | 116.787 | 115.763 | 115.042 | 114.575 | 114.073 | 113.588 | 113.155 | 112.693 | 112.14 | 111.422 | 111.083
10:00 | 118.091 | 116.927 | 116.11 | 115.585 | 115.032 | 114.495 | 114.01 | 113.494 | 112.871 | 112.091 | 111.691
10:30 | 119.954 | 118.689 | 117.807 | 117.246 | 116.663 | 116.096 | 115.578 | 115.031 | 114.365 | 113.556 | 113.115
11:00 | 123.865 | 122.558 | 121.653 | 121.082 | 120.498 | 119.93 | 119.407 | 118.857 | 118.183 | 117.394 | 116.938
11:30 | 124.863 | 123.595 | 122.73 | 122.199 | 121.684 | 121.182 | 120.706 | 120.214 | 119.599 | 118.962 | 118.512
12:00 | 128.004 | 126.703 | 125.817 | 125.27 | 124.744 | 124.23 | 123.742 | 123.236 | 122.605 | 121.952 | 121.49
12:30 | 132.152 | 131.022 | 130.249 | 129.771 | 129.306 | 128.853 | 128.424 | 127.979 | 127.426 | 126.842 | 126.441
13:00 | 132.723 | 131.748 | 131.083 | 130.673 | 130.276 | 129.888 | 129.522 | 129.142 | 128.669 | 128.175 | 127.831
13:30 | 135.515 | 134.394 | 133.621 | 133.139 | 132.657 | 132.189 | 131.752 | 131.295 | 130.732 | 130.104 | 129.708
14:00 | 134.157 | 133.108 | 132.394 | 131.958 | 131.542 | 131.135 | 130.746 | 130.344 | 129.842 | 129.336 | 128.962
14:30 | 138.737 | 137.862 | 137.266 | 136.902 | 136.554 | 136.214 | 135.89 | 135.555 | 135.137 | 134.714 | 134.403
15:00 | 138.053 | 137.397 | 136.952 | 136.681 | 136.426 | 136.178 | 135.939 | 135.694 | 135.386 | 135.086 | 134.854
15:30 | 133.762 | 133.008 | 132.498 | 132.188 | 131.899 | 131.616 | 131.346 | 131.069 | 130.719 | 130.382 | 130.121
16:00 | 144.831 | 142.555 | 141.965 | 142.53 | 143.374 | 143.457 | 142.91 | 142.854 | 142.912 | 142.926 | 142.661
16:30 | 140.377 | 138.368 | 137.936 | 138.58 | 139.505 | 139.686 | 139.243 | 139.284 | 139.455 | 139.622 | 139.435
17:00 | 135.192 | 133.356 | 133.018 | 133.696 | 134.666 | 134.913 | 134.546 | 134.656 | 134.899 | 135.196 | 135.054
17:30 | 130.319 | 128.746 | 128.553 | 129.289 | 130.294 | 130.598 | 130.309 | 130.483 | 130.809 | 131.155 | 131.1
18:00 | 128.757 | 127.446 | 127.413 | 128.235 | 129.334 | 129.745 | 129.562 | 129.839 | 130.284 | 130.804 | 130.821
18:30 | 119.97 | 118.919 | 119.03 | 119.907 | 121.066 | 121.568 | 121.484 | 121.847 | 122.385 | 123.063 | 123.132
19:00 | 131.07 | 129.882 | 129.932 | 130.805 | 131.954 | 132.415 | 132.273 | 132.59 | 133.084 | 133.671 | 133.705
19:30 | 135.366 | 134.124 | 134.144 | 135.004 | 136.141 | 136.584 | 136.418 | 136.713 | 137.182 | 137.735 | 137.747
20:00 | 129.406 | 128.224 | 128.256 | 129.095 | 130.201 | 130.636 | 130.479 | 130.769 | 131.227 | 131.768 | 131.78
20:30 | 117.473 | 116.406 | 116.462 | 117.265 | 118.309 | 118.719 | 118.577 | 118.852 | 119.291 | 119.777 | 119.804
21:00 | 108.378 | 108.398 | 108.42 | 108.443 | 108.483 | 108.522 | 108.549 | 108.583 | 108.618 | 108.707 | 108.713
21:30 | 106.138 | 106.158 | 106.18 | 106.201 | 106.241 | 106.279 | 106.307 | 106.341 | 106.375 | 106.462 | 106.468
22:00 | 109.915 | 109.933 | 109.952 | 109.972 | 110.007 | 110.042 | 110.066 | 110.096 | 110.126 | 110.205 | 110.21
22:30 | 95.363 | 95.378 | 95.395 | 95.412 | 95.441 | 95.469 | 95.49 | 95.514 | 95.541 | 95.606 | 95.609
23:00 | 88.542 | 88.556 | 88.573 | 88.589 | 88.618 | 88.646 | 88.666 | 88.69 | 88.716 | 88.78 | 88.783
23:30 | 80.591 | 80.598 | 80.607 | 80.615 | 80.63 | 80.645 | 80.656 | 80.668 | 80.681 | 80.715 | 80.717
0:00 | 75.484 | 75.488 | 75.493 | 75.497 | 75.506 | 75.514 | 75.52 | 75.526 | 75.533 | 75.552 | 75.553

## 8. Load profile min
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:30 | 41.86 | 41.867 | 41.874 | 41.881 | 41.895 | 41.908 | 41.917 | 41.928 | 41.939 | 41.968 | 41.97
1:00 | 40.356 | 40.363 | 40.37 | 40.377 | 40.39 | 40.402 | 40.411 | 40.421 | 40.432 | 40.46 | 40.462
1:30 | 40.533 | 40.54 | 40.547 | 40.554 | 40.568 | 40.58 | 40.589 | 40.599 | 40.61 | 40.639 | 40.64
2:00 | 39.641 | 39.648 | 39.655 | 39.663 | 39.676 | 39.689 | 39.697 | 39.708 | 39.72 | 39.749 | 39.749
2:30 | 39.77 | 39.777 | 39.784 | 39.793 | 39.806 | 39.819 | 39.828 | 39.84 | 39.851 | 39.881 | 39.882
3:00 | 38.877 | 38.88 | 38.885 | 38.889 | 38.896 | 38.904 | 38.908 | 38.914 | 38.921 | 38.937 | 38.938
3:30 | 38.117 | 38.122 | 38.126 | 38.13 | 38.137 | 38.144 | 38.148 | 38.155 | 38.161 | 38.177 | 38.177
4:00 | 38.796 | 38.799 | 38.803 | 38.807 | 38.814 | 38.82 | 38.825 | 38.831 | 38.837 | 38.852 | 38.852
4:30 | 37.774 | 37.777 | 37.781 | 37.784 | 37.791 | 37.798 | 37.803 | 37.809 | 37.815 | 37.83 | 37.831
5:00 | 37.967 | 37.975 | 37.983 | 37.991 | 38.006 | 38.021 | 38.031 | 38.045 | 38.057 | 38.091 | 38.094
5:30 | 38.555 | 38.564 | 38.572 | 38.582 | 38.599 | 38.615 | 38.628 | 38.643 | 38.659 | 38.699 | 38.704
6:00 | 39.269 | 39.278 | 39.288 | 39.298 | 39.315 | 39.334 | 39.348 | 39.366 | 39.387 | 39.433 | 39.445
6:30 | 41.802 | 41.81 | 41.82 | 41.83 | 41.849 | 41.867 | 41.883 | 41.903 | 41.925 | 41.974 | 41.99
7:00 | 42.333 | 42.337 | 42.342 | 42.347 | 42.357 | 42.369 | 42.38 | 42.393 | 42.412 | 42.443 | 42.463
7:30 | 44.995 | 44.991 | 44.987 | 44.984 | 44.98 | 44.976 | 44.978 | 44.981 | 44.989 | 44.99 | 45.013
8:00 | 44.111 | 44.041 | 43.992 | 43.96 | 43.926 | 43.894 | 43.873 | 43.851 | 43.831 | 43.799 | 43.811
8:30 | 43.705 | 43.48 | 43.316 | 43.207 | 43.08 | 42.959 | 42.862 | 42.756 | 42.639 | 42.456 | 42.415
9:00 | 43.394 | 42.943 | 42.62 | 42.409 | 42.174 | 41.947 | 41.753 | 41.544 | 41.301 | 40.959 | 40.835
9:30 | 43.608 | 42.973 | 42.521 | 42.226 | 41.901 | 41.587 | 41.312 | 41.017 | 40.666 | 40.189 | 39.985
10:00 | 40.838 | 40.04 | 39.479 | 39.118 | 38.735 | 38.361 | 38.027 | 37.67 | 37.241 | 36.694 | 36.423
10:30 | 39.211 | 38.6 | 37.964 | 37.559 | 37.141 | 36.734 | 36.362 | 35.969 | 35.491 | 34.915 | 34.596
11:00 | 37.496 | 36.861 | 36.18 | 35.75 | 35.311 | 34.884 | 34.49 | 34.077 | 33.57 | 32.977 | 32.633
11:30 | 35.82 | 35.45 | 34.716 | 34.256 | 33.795 | 33.344 | 32.925 | 32.488 | 31.949 | 31.337 | 30.964
12:00 | 38.268 | 37.453 | 36.691 | 36.214 | 35.737 | 35.271 | 34.838 | 34.384 | 33.826 | 33.197 | 32.808
12:30 | 8.953 | 8.711 | 8.544 | 8.44 | 8.334 | 8.233 | 8.137 | 8.037 | 7.914 | 7.775 | 7.69
13:00 | 2.066 | 2.063 | 2.018 | 1.99 | 1.962 | 1.934 | 1.909 | 1.881 | 1.848 | 1.811 | 1.787
13:30 | 2.123 | 2.13 | 2.088 | 2.061 | 2.036 | 2.011 | 1.988 | 1.964 | 1.933 | 1.902 | 1.88
14:00 | 2.11 | 2.088 | 2.053 | 2.032 | 2.011 | 1.991 | 1.972 | 1.952 | 1.928 | 1.903 | 1.885
14:30 | 2.236 | 2.276 | 2.239 | 2.216 | 2.194 | 2.174 | 2.154 | 2.133 | 2.107 | 2.081 | 2.061
15:00 | 2.32 | 2.281 | 2.254 | 2.239 | 2.225 | 2.21 | 2.196 | 2.182 | 2.164 | 2.147 | 2.133
15:30 | 2.256 | 2.229 | 2.211 | 2.2 | 2.19 | 2.179 | 2.17 | 2.16 | 2.148 | 2.136 | 2.126
16:00 | 2.37 | 2.351 | 2.338 | 2.33 | 2.323 | 2.314 | 2.308 | 2.301 | 2.293 | 2.284 | 2.277
16:30 | 2.277 | 2.267 | 2.26 | 2.256 | 2.253 | 2.25 | 2.247 | 2.244 | 2.24 | 2.237 | 2.235
17:00 | 2.327 | 2.322 | 2.319 | 2.317 | 2.316 | 2.314 | 2.314 | 2.313 | 2.312 | 2.313 | 2.312
17:30 | 2.235 | 2.235 | 2.237 | 2.238 | 2.24 | 2.243 | 2.246 | 2.247 | 2.25 | 2.256 | 2.257
18:00 | 2.203 | 2.204 | 2.205 | 2.206 | 2.208 | 2.211 | 2.213 | 2.214 | 2.217 | 2.222 | 2.223
18:30 | 38.592 | 38.61 | 38.629 | 38.649 | 38.685 | 38.721 | 38.747 | 38.781 | 38.816 | 38.899 | 38.911
19:00 | 66.492 | 66.514 | 66.537 | 66.561 | 66.605 | 66.648 | 66.681 | 66.721 | 66.764 | 66.864 | 66.877
19:30 | 63.586 | 63.611 | 63.64 | 63.668 | 63.719 | 63.768 | 63.804 | 63.849 | 63.894 | 64.009 | 64.018
20:00 | 61.095 | 61.12 | 61.148 | 61.177 | 61.228 | 61.277 | 61.312 | 61.356 | 61.4 | 61.513 | 61.52
20:30 | 57.834 | 57.854 | 57.875 | 57.897 | 57.936 | 57.973 | 57.999 | 58.033 | 58.067 | 58.153 | 58.158
21:00 | 55.573 | 55.592 | 55.614 | 55.635 | 55.672 | 55.709 | 55.735 | 55.768 | 55.801 | 55.885 | 55.891
21:30 | 53.677 | 53.691 | 53.706 | 53.723 | 53.751 | 53.779 | 53.798 | 53.822 | 53.846 | 53.91 | 53.914
22:00 | 51.243 | 51.258 | 51.273 | 51.288 | 51.316 | 51.344 | 51.364 | 51.387 | 51.412 | 51.475 | 51.478
22:30 | 47.377 | 47.391 | 47.406 | 47.421 | 47.449 | 47.475 | 47.493 | 47.517 | 47.541 | 47.601 | 47.604
23:00 | 44.967 | 44.977 | 44.987 | 44.998 | 45.016 | 45.033 | 45.046 | 45.062 | 45.078 | 45.119 | 45.122
23:30 | 42.759 | 42.769 | 42.779 | 42.789 | 42.807 | 42.825 | 42.836 | 42.852 | 42.867 | 42.867 | 42.909
0:00 | 44.214 | 44.221 | 44.229 | 44.236 | 44.25 | 44.262 | 44.271 | 44.282 | 44.293 | 44.323 | 44.325

## 10. Load profile (50% PoE)
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:30 | 51.698 | 51.701 | 51.704 | 51.707 | 51.713 | 51.719 | 51.723 | 51.727 | 51.732 | 51.745 | 51.746
1:00 | 50.193 | 50.196 | 50.199 | 50.202 | 50.208 | 50.213 | 50.217 | 50.221 | 50.226 | 50.238 | 50.239
1:30 | 50.065 | 50.068 | 50.071 | 50.074 | 50.079 | 50.085 | 50.088 | 50.093 | 50.098 | 50.11 | 50.111
2:00 | 49.107 | 49.11 | 49.113 | 49.116 | 49.121 | 49.127 | 49.13 | 49.135 | 49.139 | 49.152 | 49.152
2:30 | 48.771 | 48.774 | 48.778 | 48.781 | 48.788 | 48.794 | 48.798 | 48.804 | 48.809 | 48.823 | 48.824
3:00 | 48.351 | 48.353 | 48.355 | 48.358 | 48.362 | 48.367 | 48.369 | 48.373 | 48.377 | 48.387 | 48.387
3:30 | 47.371 | 47.374 | 47.378 | 47.382 | 47.388 | 47.395 | 47.399 | 47.405 | 47.41 | 47.425 | 47.426
4:00 | 46.325 | 46.329 | 46.334 | 46.338 | 46.346 | 46.353 | 46.358 | 46.365 | 46.371 | 46.388 | 46.389
4:30 | 46.548 | 46.552 | 46.556 | 46.56 | 46.568 | 46.575 | 46.58 | 46.586 | 46.592 | 46.609 | 46.61
5:00 | 47.452 | 47.455 | 47.458 | 47.461 | 47.466 | 47.471 | 47.475 | 47.48 | 47.485 | 47.497 | 47.498
5:30 | 49.72 | 49.722 | 49.725 | 49.727 | 49.732 | 49.737 | 49.74 | 49.745 | 49.75 | 49.762 | 49.766
6:00 | 51.927 | 51.929 | 51.932 | 51.935 | 51.941 | 51.946 | 51.952 | 51.959 | 51.968 | 51.984 | 51.993
6:30 | 59.615 | 59.584 | 59.565 | 59.556 | 59.552 | 59.548 | 59.544 | 59.542 | 59.539 | 59.549 | 59.548
7:00 | 64.854 | 64.777 | 64.724 | 64.691 | 64.658 | 64.627 | 64.6 | 64.573 | 64.543 | 64.507 | 64.495
7:30 | 73.071 | 72.911 | 72.798 | 72.726 | 72.651 | 72.578 | 72.516 | 72.451 | 72.375 | 72.278 | 72.243
8:00 | 77.188 | 76.902 | 76.703 | 76.577 | 76.446 | 76.32 | 76.211 | 76.096 | 75.961 | 75.795 | 75.725
8:30 | 78.292 | 77.774 | 77.41 | 77.176 | 76.927 | 76.687 | 76.475 | 76.252 | 75.987 | 75.646 | 75.497
9:00 | 81.261 | 80.599 | 80.131 | 79.826 | 79.497 | 79.178 | 78.898 | 78.599 | 78.244 | 77.772 | 77.568
9:30 | 83.457 | 82.725 | 82.21 | 81.876 | 81.518 | 81.171 | 80.861 | 80.531 | 80.136 | 79.623 | 79.381
10:00 | 84.389 | 83.557 | 82.973 | 82.598 | 82.203 | 81.819 | 81.472 | 81.104 | 80.659 | 80.101 | 79.815
10:30 | 85.72 | 84.816 | 84.186 | 83.785 | 83.368 | 82.963 | 82.593 | 82.202 | 81.726 | 81.148 | 80.833
11:00 | 88.515 | 87.581 | 86.934 | 86.526 | 86.109 | 85.703 | 85.329 | 84.936 | 84.455 | 83.891 | 83.565
11:30 | 89.228 | 88.322 | 87.704 | 87.324 | 86.957 | 86.598 | 86.258 | 85.906 | 85.466 | 85.011 | 84.69
12:00 | 91.473 | 90.543 | 89.91 | 89.519 | 89.143 | 88.776 | 88.427 | 88.065 | 87.615 | 87.148 | 86.818
12:30 | 94.437 | 93.629 | 93.077 | 92.736 | 92.403 | 92.079 | 91.773 | 91.455 | 91.06 | 90.642 | 90.356
13:00 | 94.845 | 94.148 | 93.673 | 93.38 | 93.096 | 92.819 | 92.557 | 92.286 | 91.948 | 91.595 | 91.349
13:30 | 96.84 | 96.039 | 95.487 | 95.142 | 94.798 | 94.463 | 94.151 | 93.825 | 93.422 | 92.973 | 92.691
14:00 | 95.87 | 95.12 | 94.61 | 94.298 | 94.001 | 93.71 | 93.432 | 93.145 | 92.786 | 92.425 | 92.157
14:30 | 99.143 | 98.517 | 98.092 | 97.831 | 97.582 | 97.34 | 97.108 | 96.869 | 96.57 | 96.268 | 96.046
15:00 | 98.654 | 98.185 | 97.867 | 97.673 | 97.491 | 97.314 | 97.143 | 96.968 | 96.748 | 96.533 | 96.368
15:30 | 95.587 | 95.049 | 94.684 | 94.463 | 94.256 | 94.054 | 93.861 | 93.663 | 93.413 | 93.172 | 92.986
16:00 | 103.497 | 101.871 | 101.449 | 101.853 | 102.456 | 102.515 | 102.125 | 102.085 | 102.126 | 102.136 | 101.946
16:30 | 100.315 | 98.879 | 98.57 | 99.03 | 99.691 | 99.82 | 99.504 | 99.533 | 99.656 | 99.775 | 99.641
17:00 | 96.609 | 95.297 | 95.056 | 95.54 | 96.233 | 96.41 | 96.148 | 96.226 | 96.4 | 96.612 | 96.511
17:30 | 93.127 | 92.003 | 91.865 | 92.391 | 93.109 | 93.326 | 93.12 | 93.244 | 93.477 | 93.724 | 93.685
18:00 | 92.011 | 91.074 | 91.05 | 91.638 | 92.423 | 92.717 | 92.586 | 92.784 | 93.102 | 93.473 | 93.486
18:30 | 85.732 | 84.981 | 85.06 | 85.686 | 86.515 | 86.873 | 86.813 | 87.073 | 87.457 | 87.942 | 87.991
19:00 | 93.664 | 92.815 | 92.85 | 93.474 | 94.296 | 94.625 | 94.523 | 94.75 | 95.103 | 95.522 | 95.547
19:30 | 96.733 | 95.846 | 95.86 | 96.475 | 97.288 | 97.604 | 97.485 | 97.696 | 98.031 | 98.426 | 98.435
20:00 | 92.475 | 91.63 | 91.653 | 92.252 | 93.043 | 93.353 | 93.241 | 93.449 | 93.776 | 94.162 | 94.171
20:30 | 83.947 | 83.185 | 83.225 | 83.799 | 84.545 | 84.838 | 84.736 | 84.933 | 85.247 | 85.594 | 85.613
21:00 | 77.448 | 77.462 | 77.478 | 77.494 | 77.523 | 77.551 | 77.57 | 77.594 | 77.619 | 77.683 | 77.687
21:30 | 75.847 | 75.861 | 75.877 | 75.892 | 75.921 | 75.948 | 75.968 | 75.992 | 76.016 | 76.079 | 76.083
22:00 | 78.546 | 78.559 | 78.573 | 78.587 | 78.612 | 78.637 | 78.654 | 78.675 | 78.697 | 78.754 | 78.757
22:30 | 68.147 | 68.158 | 68.17 | 68.182 | 68.203 | 68.223 | 68.238 | 68.255 | 68.274 | 68.321 | 68.323
23:00 | 63.273 | 63.283 | 63.295 | 63.306 | 63.327 | 63.347 | 63.361 | 63.379 | 63.397 | 63.443 | 63.445
23:30 | 57.591 | 57.596 | 57.602 | 57.608 | 57.619 | 57.63 | 57.637 | 57.646 | 57.655 | 57.68 | 57.681
0:00 | 53.941 | 53.944 | 53.948 | 53.951 | 53.957 | 53.963 | 53.967 | 53.972 | 53.977 | 53.99 | 53.991

## 11. Load profile min
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:30 | 29.914 | 29.918 | 29.924 | 29.929 | 29.938 | 29.948 | 29.954 | 29.962 | 29.97 | 29.991 | 29.992
1:00 | 28.839 | 28.843 | 28.848 | 28.854 | 28.863 | 28.872 | 28.878 | 28.885 | 28.893 | 28.913 | 28.914
1:30 | 28.965 | 28.97 | 28.975 | 28.98 | 28.99 | 28.999 | 29.005 | 29.013 | 29.02 | 29.041 | 29.042
2:00 | 28.328 | 28.333 | 28.338 | 28.344 | 28.353 | 28.362 | 28.368 | 28.376 | 28.384 | 28.405 | 28.405
2:30 | 28.42 | 28.425 | 28.43 | 28.436 | 28.446 | 28.455 | 28.461 | 28.47 | 28.478 | 28.499 | 28.5
3:00 | 27.782 | 27.784 | 27.787 | 27.79 | 27.795 | 27.801 | 27.804 | 27.808 | 27.813 | 27.825 | 27.825
3:30 | 27.239 | 27.242 | 27.245 | 27.248 | 27.253 | 27.258 | 27.261 | 27.266 | 27.27 | 27.282 | 27.282
4:00 | 27.724 | 27.726 | 27.729 | 27.732 | 27.737 | 27.741 | 27.745 | 27.749 | 27.753 | 27.764 | 27.764
4:30 | 26.993 | 26.996 | 26.999 | 27.001 | 27.006 | 27.011 | 27.014 | 27.019 | 27.023 | 27.034 | 27.034
5:00 | 27.131 | 27.137 | 27.143 | 27.149 | 27.16 | 27.17 | 27.177 | 27.187 | 27.196 | 27.22 | 27.222
5:30 | 27.552 | 27.558 | 27.564 | 27.571 | 27.583 | 27.595 | 27.604 | 27.614 | 27.626 | 27.654 | 27.658
6:00 | 28.062 | 28.068 | 28.075 | 28.082 | 28.095 | 28.108 | 28.119 | 28.131 | 28.146 | 28.179 | 28.188
6:30 | 29.872 | 29.878 | 29.885 | 29.892 | 29.906 | 29.919 | 29.93 | 29.944 | 29.96 | 29.995 | 30.006
7:00 | 30.252 | 30.254 | 30.258 | 30.262 | 30.269 | 30.277 | 30.285 | 30.295 | 30.308 | 30.33 | 30.345
7:30 | 32.154 | 32.151 | 32.148 | 32.146 | 32.143 | 32.14 | 32.142 | 32.144 | 32.15 | 32.15 | 32.167
8:00 | 31.522 | 31.472 | 31.437 | 31.414 | 31.39 | 31.367 | 31.352 | 31.336 | 31.322 | 31.299 | 31.308
8:30 | 31.232 | 31.071 | 30.954 | 30.876 | 30.785 | 30.699 | 30.629 | 30.554 | 30.47 | 30.339 | 30.31
9:00 | 31.01 | 30.687 | 30.457 | 30.306 | 30.138 | 29.975 | 29.837 | 29.688 | 29.514 | 29.27 | 29.181
9:30 | 31.163 | 30.709 | 30.386 | 30.175 | 29.943 | 29.719 | 29.522 | 29.311 | 29.06 | 28.72 | 28.574
10:00 | 29.183 | 28.613 | 28.212 | 27.954 | 27.68 | 27.413 | 27.174 | 26.919 | 26.613 | 26.222 | 26.028
10:30 | 28.021 | 27.584 | 27.129 | 26.84 | 26.541 | 26.251 | 25.985 | 25.704 | 25.362 | 24.95 | 24.723
11:00 | 26.795 | 26.341 | 25.855 | 25.547 | 25.234 | 24.928 | 24.647 | 24.352 | 23.99 | 23.566 | 23.32
11:30 | 25.597 | 25.333 | 24.808 | 24.48 | 24.15 | 23.828 | 23.529 | 23.216 | 22.831 | 22.394 | 22.127
12:00 | 27.347 | 26.764 | 26.22 | 25.879 | 25.538 | 25.205 | 24.895 | 24.571 | 24.172 | 23.723 | 23.445
12:30 | 6.398 | 6.225 | 6.106 | 6.031 | 5.956 | 5.883 | 5.815 | 5.743 | 5.656 | 5.556 | 5.495
13:00 | 1.476 | 1.475 | 1.442 | 1.422 | 1.402 | 1.382 | 1.364 | 1.344 | 1.321 | 1.294 | 1.277
13:30 | 1.517 | 1.522 | 1.492 | 1.473 | 1.455 | 1.437 | 1.421 | 1.403 | 1.382 | 1.359 | 1.343
14:00 | 1.508 | 1.492 | 1.467 | 1.452 | 1.437 | 1.423 | 1.409 | 1.395 | 1.378 | 1.36 | 1.347
14:30 | 1.598 | 1.627 | 1.6 | 1.584 | 1.568 | 1.553 | 1.539 | 1.524 | 1.506 | 1.487 | 1.473
15:00 | 1.658 | 1.63 | 1.611 | 1.6 | 1.59 | 1.579 | 1.569 | 1.559 | 1.546 | 1.534 | 1.524
15:30 | 1.612 | 1.593 | 1.58 | 1.572 | 1.565 | 1.557 | 1.551 | 1.544 | 1.535 | 1.526 | 1.519
16:00 | 1.694 | 1.68 | 1.671 | 1.665 | 1.66 | 1.654 | 1.649 | 1.644 | 1.638 | 1.632 | 1.627
16:30 | 1.627 | 1.62 | 1.615 | 1.612 | 1.61 | 1.608 | 1.606 | 1.604 | 1.601 | 1.599 | 1.597
17:00 | 1.663 | 1.659 | 1.657 | 1.655 | 1.655 | 1.654 | 1.654 | 1.653 | 1.652 | 1.653 | 1.652
17:30 | 1.597 | 1.597 | 1.598 | 1.599 | 1.601 | 1.603 | 1.605 | 1.606 | 1.608 | 1.612 | 1.613
18:00 | 1.574 | 1.575 | 1.576 | 1.577 | 1.578 | 1.58 | 1.581 | 1.582 | 1.584 | 1.588 | 1.588
18:30 | 27.578 | 27.591 | 27.605 | 27.619 | 27.645 | 27.67 | 27.689 | 27.713 | 27.738 | 27.797 | 27.806
19:00 | 47.515 | 47.531 | 47.548 | 47.565 | 47.597 | 47.627 | 47.651 | 47.679 | 47.71 | 47.781 | 47.791
19:30 | 45.439 | 45.457 | 45.478 | 45.498 | 45.534 | 45.569 | 45.595 | 45.627 | 45.659 | 45.741 | 45.748
20:00 | 43.659 | 43.677 | 43.697 | 43.718 | 43.754 | 43.789 | 43.814 | 43.845 | 43.877 | 43.958 | 43.963
20:30 | 41.329 | 41.343 | 41.358 | 41.374 | 41.401 | 41.428 | 41.447 | 41.471 | 41.495 | 41.557 | 41.56
21:00 | 39.713 | 39.726 | 39.742 | 39.757 | 39.784 | 39.81 | 39.829 | 39.852 | 39.876 | 39.936 | 39.94
21:30 | 38.358 | 38.368 | 38.379 | 38.391 | 38.411 | 38.431 | 38.444 | 38.462 | 38.479 | 38.525 | 38.527
22:00 | 36.618 | 36.629 | 36.64 | 36.651 | 36.671 | 36.691 | 36.705 | 36.722 | 36.739 | 36.784 | 36.787
22:30 | 33.856 | 33.866 | 33.877 | 33.888 | 33.907 | 33.926 | 33.939 | 33.956 | 33.973 | 34.016 | 34.018
23:00 | 32.134 | 32.141 | 32.148 | 32.156 | 32.169 | 32.181 | 32.19 | 32.202 | 32.213 | 32.242 | 32.244
23:30 | 30.556 | 30.563 | 30.57 | 30.577 | 30.59 | 30.603 | 30.611 | 30.622 | 30.633 | 30.633 | 30.663
0:00 | 31.596 | 31.601 | 31.606 | 31.611 | 31.621 | 31.63 | 31.636 | 31.644 | 31.652 | 31.673 | 31.675

## 23. Historic load trace
Date/Time | Load (MVA) | Load (MW)
2017-03-01 00:30 | 45.46 | 43.62
2017-03-01 01:00 | 44.24 | 42.33
2017-03-01 01:30 | 43.28 | 41.32
2017-03-01 02:00 | 42.59 | 40.58
2017-03-01 02:30 | 41.65 | 39.54
2017-03-01 03:00 | 41.11 | 38.94
2017-03-01 03:30 | 41.27 | 39.12
2017-03-01 04:00 | 41.33 | 39.19
2017-03-01 04:30 | 42.31 | 40.26
2017-03-01 05:00 | 43.07 | 41.08
2017-03-01 05:30 | 45.14 | 43.33
2017-03-01 06:00 | 47.62 | 46.22
2017-03-01 06:30 | 52.55 | 51.24
2017-03-01 07:00 | 58.28 | 56.97
2017-03-01 07:30 | 74.48 | 64.45
2017-03-01 08:00 | 77.55 | 68.04
2017-03-01 08:30 | 79.33 | 70.76
2017-03-01 09:00 | 81.34 | 72.86
2017-03-01 09:30 | 82.34 | 73.92
2017-03-01 10:00 | 82.49 | 74.08
2017-03-01 10:30 | 83.14 | 74.76
2017-03-01 11:00 | 84.1 | 75.74
2017-03-01 11:30 | 83.95 | 75.56
2017-03-01 12:00 | 84.88 | 76.57
2017-03-01 12:30 | 85.61 | 77.4
2017-03-01 13:00 | 86.07 | 77.91
2017-03-01 13:30 | 86.78 | 78.67
2017-03-01 14:00 | 87.06 | 79.01
2017-03-01 14:30 | 87.89 | 79.89
2017-03-01 15:00 | 88.28 | 80.33
2017-03-01 15:30 | 87.84 | 79.89
2017-03-01 16:00 | 87.57 | 79.75
2017-03-01 16:30 | 87.43 | 79.78
2017-03-01 17:00 | 86.17 | 78.51
2017-03-01 17:30 | 83.91 | 76.2
2017-03-01 18:00 | 81.39 | 73.66
2017-03-01 18:30 | 79.72 | 71.95
2017-03-01 19:00 | 80.79 | 73.18
2017-03-01 19:30 | 80.71 | 73.04
2017-03-01 20:00 | 78.73 | 70.33
2017-03-01 20:30 | 76.57 | 67.91
2017-03-01 21:00 | 74.04 | 65.09
2017-03-01 21:30 | 71.41 | 62.14
2017-03-01 22:00 | 69.33 | 58.67
2017-03-01 22:30 | 67.09 | 55.61
2017-03-01 23:00 | 65.87 | 54.26
2017-03-01 23:30 | 62.38 | 49.96
2017-03-02 | 60.76 | 47.95
2017-03-02 00:30 | 60.12 | 47.1
2017-03-02 01:00 | 58.85 | 45.43
2017-03-02 01:30 | 58.19 | 44.59
2017-03-02 02:00 | 57.65 | 43.92
2017-03-02 02:30 | 56.91 | 43.09
2017-03-02 03:00 | 56.15 | 42.05
2017-03-02 03:30 | 56.2 | 42.11
2017-03-02 04:00 | 56.12 | 42.01
2017-03-02 04:30 | 56.92 | 43.03
2017-03-02 05:00 | 57.68 | 44
2017-03-02 05:30 | 59.15 | 45.84
2017-03-02 06:00 | 61.68 | 48.97
2017-03-02 06:30 | 66.52 | 54.63
2017-03-02 07:00 | 62.3 | 60.81
2017-03-02 07:30 | 68.3 | 67.54
2017-03-02 08:00 | 70.65 | 69.93
2017-03-02 08:30 | 73.73 | 72.96
2017-03-02 09:00 | 76.4 | 75.59
2017-03-02 09:30 | 86.1 | 78.42
2017-03-02 10:00 | 87.6 | 79.65
2017-03-02 10:30 | 87.37 | 79.26
2017-03-02 11:00 | 88.71 | 80.77
2017-03-02 11:30 | 85.25 | 76.97
2017-03-02 12:00 | 83.36 | 74.87
2017-03-02 12:30 | 85.6 | 77.37
2017-03-02 13:00 | 84.33 | 75.93
2017-03-02 13:30 | 84.91 | 76.64
2017-03-02 14:00 | 86.9 | 78.85
2017-03-02 14:30 | 87.81 | 79.89
2017-03-02 15:00 | 87.81 | 79.89
2017-03-02 15:30 | 87.47 | 79.55
2017-03-02 16:00 | 88.05 | 80.25
2017-03-02 16:30 | 87.92 | 80.23
2017-03-02 17:00 | 86.3 | 78.68
2017-03-02 17:30 | 83.32 | 75.63
2017-03-02 18:00 | 81.87 | 74.22
2017-03-02 18:30 | 80.72 | 73.05
2017-03-02 19:00 | 81.52 | 74
2017-03-02 19:30 | 81.09 | 73.51
2017-03-02 20:00 | 75.73 | 71.28
2017-03-02 20:30 | 69.58 | 68.6
2017-03-02 21:00 | 66.67 | 65.84
2017-03-02 21:30 | 62.98 | 62.07
2017-03-02 22:00 | 59.55 | 58.35
2017-03-02 22:30 | 56.61 | 55.34
2017-03-02 23:00 | 55.67 | 54.48
2017-03-02 23:30 | 51.46 | 50.2
2017-03-03 | 48.98 | 47.67
2017-03-03 00:30 | 47.69 | 46.37
2017-03-03 01:00 | 46.22 | 44.87
2017-03-03 01:30 | 44.97 | 43.6
2017-03-03 02:00 | 44.14 | 42.76
2017-03-03 02:30 | 43.21 | 41.83
2017-03-03 03:00 | 43.09 | 41.7
2017-03-03 03:30 | 42.75 | 41.35
2017-03-03 04:00 | 42.69 | 41.15
2017-03-03 04:30 | 43.55 | 41.97
2017-03-03 05:00 | 44.42 | 42.86
2017-03-03 05:30 | 46.6 | 45.05
2017-03-03 06:00 | 49.56 | 48.03
2017-03-03 06:30 | 54.77 | 53.35
2017-03-03 07:00 | 59.38 | 58.06
2017-03-03 07:30 | 70.38 | 65.03
2017-03-03 08:00 | 79.73 | 69.79
2017-03-03 08:30 | 82.86 | 73.51
2017-03-03 09:00 | 84.52 | 75.75
2017-03-03 09:30 | 85.93 | 77.3
2017-03-03 10:00 | 86.22 | 77.68
2017-03-03 10:30 | 86.34 | 77.94
2017-03-03 11:00 | 86.86 | 78.55
2017-03-03 11:30 | 87.39 | 79.12
2017-03-03 12:00 | 88.75 | 80.61
2017-03-03 12:30 | 88.89 | 80.62
2017-03-03 13:00 | 88.51 | 80.4
2017-03-03 13:30 | 88.75 | 80.68
2017-03-03 14:00 | 88.85 | 80.85
2017-03-03 14:30 | 88.31 | 80.17
2017-03-03 15:00 | 88.04 | 79.96
2017-03-03 15:30 | 84.87 | 76.41
2017-03-03 16:00 | 87.49 | 79.61
2017-03-03 16:30 | 88.85 | 81.23
2017-03-03 17:00 | 81.09 | 77.94
2017-03-03 17:30 | 74.66 | 74.04
2017-03-03 18:00 | 71.91 | 71.15
2017-03-03 18:30 | 70.06 | 69.1
2017-03-03 19:00 | 71.16 | 70.27
2017-03-03 19:30 | 70.36 | 69.38
2017-03-03 20:00 | 68.61 | 67.48
2017-03-03 20:30 | 66.43 | 65.58
2017-03-03 21:00 | 63.95 | 62.93
2017-03-03 21:30 | 61.23 | 60.06
2017-03-03 22:00 | 58.48 | 57.29
2017-03-03 22:30 | 55.63 | 54.43
2017-03-03 23:00 | 54.76 | 53.55
2017-03-03 23:30 | 51.15 | 49.89
2017-03-04 | 48.92 | 47.63
2017-03-04 00:30 | 47.49 | 46.2
2017-03-04 01:00 | 45.97 | 44.5
2017-03-04 01:30 | 45.4 | 43.87
2017-03-04 02:00 | 44.76 | 43.21
2017-03-04 02:30 | 44.07 | 42.5
2017-03-04 03:00 | 43.27 | 41.68
2017-03-04 03:30 | 42.76 | 41.16
2017-03-04 04:00 | 42.22 | 40.61
2017-03-04 04:30 | 42.27 | 40.66
2017-03-04 05:00 | 42.51 | 40.91
2017-03-04 05:30 | 43.34 | 41.74
2017-03-04 06:00 | 44.2 | 42.65
2017-03-04 06:30 | 46.79 | 45.28
2017-03-04 07:00 | 48.68 | 47.2
2017-03-04 07:30 | 51.96 | 50.5
2017-03-04 08:00 | 54.91 | 52.98
2017-03-04 08:30 | 61.59 | 56.2
2017-03-04 09:00 | 63 | 57.72
2017-03-04 09:30 | 63.55 | 58.29
2017-03-04 10:00 | 63.35 | 58.04
2017-03-04 10:30 | 63.24 | 57.89
2017-03-04 11:00 | 64.44 | 59.19
2017-03-04 11:30 | 64.01 | 58.71
2017-03-04 12:00 | 63.56 | 58.23
2017-03-04 12:30 | 63.56 | 58.29
2017-03-04 13:00 | 61.8 | 56.36
2017-03-04 13:30 | 61.42 | 55.95
2017-03-04 14:00 | 63.22 | 57.83
2017-03-04 14:30 | 62.94 | 57.54
2017-03-04 15:00 | 63.27 | 57.95
2017-03-04 15:30 | 62.41 | 57.03
2017-03-04 16:00 | 63.85 | 58.62
2017-03-04 16:30 | 64.04 | 58.91
2017-03-04 17:00 | 62.17 | 56.96
2017-03-04 17:30 | 62.27 | 57.11
2017-03-04 18:00 | 62.75 | 57.65
2017-03-04 18:30 | 62.87 | 57.79
2017-03-04 19:00 | 64.79 | 59.82
2017-03-04 19:30 | 64.43 | 59.45
2017-03-04 20:00 | 62.84 | 57.74
2017-03-04 20:30 | 60.97 | 55.71
2017-03-04 21:00 | 59.44 | 54.03
2017-03-04 21:30 | 58 | 52.51
2017-03-04 22:00 | 56.76 | 51.15
2017-03-04 22:30 | 54.9 | 49.09
2017-03-04 23:00 | 54.63 | 48.84
2017-03-04 23:30 | 51.2 | 45.04
2017-03-05 | 49.34 | 42.97
2017-03-05 00:30 | 48.47 | 42
2017-03-05 01:00 | 47.07 | 40.37
2017-03-05 01:30 | 46.36 | 39.53
2017-03-05 02:00 | 45.63 | 38.71
2017-03-05 02:30 | 45.21 | 38.26
2017-03-05 03:00 | 44.98 | 38
2017-03-05 03:30 | 40.86 | 37.56
2017-03-05 04:00 | 37.3 | 37.25
2017-03-05 04:30 | 37.32 | 37.27
2017-03-05 05:00 | 37.34 | 37.29
2017-03-05 05:30 | 37.52 | 37.47
2017-03-05 06:00 | 38.29 | 38.23
2017-03-05 06:30 | 38.44 | 38.39
2017-03-05 07:00 | 39.69 | 39.63
2017-03-05 07:30 | 41.35 | 41.26
2017-03-05 08:00 | 43.93 | 43.76
2017-03-05 08:30 | 45.8 | 45.5
2017-03-05 09:00 | 48.53 | 48.01
2017-03-05 09:30 | 50.84 | 50.12
2017-03-05 10:00 | 52.73 | 51.89
2017-03-05 10:30 | 58.51 | 53.42
2017-03-05 11:00 | 60.63 | 55.05
2017-03-05 11:30 | 61.3 | 55.8
2017-03-05 12:00 | 62.4 | 56.97
2017-03-05 12:30 | 62.93 | 57.56
2017-03-05 13:00 | 64.01 | 58.72
2017-03-05 13:30 | 64.99 | 59.82
2017-03-05 14:00 | 64.75 | 59.58
2017-03-05 14:30 | 65.03 | 60.53
2017-03-05 15:00 | 65.68 | 61.71
2017-03-05 15:30 | 65.91 | 61.99
2017-03-05 16:00 | 67.04 | 63.2
2017-03-05 16:30 | 67.29 | 63.51
2017-03-05 17:00 | 67.02 | 63.26
2017-03-05 17:30 | 69.18 | 65.56
2017-03-05 18:00 | 69.6 | 66.05
2017-03-05 18:30 | 69.35 | 65.78
2017-03-05 19:00 | 70.6 | 67.04
2017-03-05 19:30 | 70.32 | 66.74
2017-03-05 20:00 | 68.08 | 64.42
2017-03-05 20:30 | 65.4 | 61.61
2017-03-05 21:00 | 63.09 | 59.17
2017-03-05 21:30 | 56.72 | 55.76
2017-03-05 22:00 | 54.14 | 52.98
2017-03-05 22:30 | 51.73 | 50.32
2017-03-05 23:00 | 51.18 | 49.64
2017-03-05 23:30 | 47.49 | 45.51
2017-03-06 | 46.07 | 43.18
2017-03-06 00:30 | 47.39 | 42.2
2017-03-06 01:00 | 40.61 | 40.55
2017-03-06 01:30 | 40.21 | 40.15
2017-03-06 02:00 | 40.01 | 39.95
2017-03-06 02:30 | 39.35 | 39.29
2017-03-06 03:00 | 39.33 | 39.27
2017-03-06 03:30 | 39.13 | 39.07
2017-03-06 04:00 | 39.33 | 39.27
2017-03-06 04:30 | 40.19 | 40.11
2017-03-06 05:00 | 41.23 | 41.13
2017-03-06 05:30 | 43.6 | 43.4
2017-03-06 06:00 | 47.12 | 46.69
2017-03-06 06:30 | 57.64 | 52.21
2017-03-06 07:00 | 62.96 | 57.82
2017-03-06 07:30 | 69.42 | 65.48
2017-03-06 08:00 | 73.76 | 70.21
2017-03-06 08:30 | 76.91 | 73.37
2017-03-06 09:00 | 79.17 | 75.59
2017-03-06 09:30 | 81.04 | 77.53
2017-03-06 10:00 | 83.04 | 79.55
2017-03-06 10:30 | 85.78 | 82.34
2017-03-06 11:00 | 86.57 | 83.15
2017-03-06 11:30 | 88.18 | 84.7
2017-03-06 12:00 | 89.34 | 85.92
2017-03-06 12:30 | 90.26 | 86.88
2017-03-06 13:00 | 90.45 | 87.08
2017-03-06 13:30 | 92.17 | 88.87
2017-03-06 14:00 | 92.11 | 88.81
2017-03-06 14:30 | 91.58 | 88.24
2017-03-06 15:00 | 91.28 | 87.97
2017-03-06 15:30 | 90.72 | 87.42
2017-03-06 16:00 | 91.18 | 87.96
2017-03-06 16:30 | 89.95 | 86.77
2017-03-06 17:00 | 88.59 | 85.49
2017-03-06 17:30 | 86.31 | 83.26
2017-03-06 18:00 | 83.63 | 80.64
2017-03-06 18:30 | 81.46 | 78.5
2017-03-06 19:00 | 81.47 | 78.51
2017-03-06 19:30 | 79.59 | 76.59
2017-03-06 20:00 | 79.01 | 76.01
2017-03-06 20:30 | 76.41 | 73.36
2017-03-06 21:00 | 68.26 | 67.6
2017-03-06 21:30 | 64.92 | 64.24
2017-03-06 22:00 | 60.94 | 60.51
2017-03-06 22:30 | 57.23 | 57.05
2017-03-06 23:00 | 54.27 | 54.15
2017-03-06 23:30 | 51.05 | 50.98
2017-03-07 | 49 | 48.94
2017-03-07 00:30 | 47.92 | 47.87
2017-03-07 01:00 | 46.34 | 46.3
2017-03-07 01:30 | 45.66 | 45.62
2017-03-07 02:00 | 44.94 | 44.91
2017-03-07 02:30 | 43.52 | 43.49
2017-03-07 03:00 | 42.99 | 42.97
2017-03-07 03:30 | 42.72 | 42.7
2017-03-07 04:00 | 42.7 | 42.68
2017-03-07 04:30 | 43.51 | 43.49
2017-03-07 05:00 | 44.65 | 44.62
2017-03-07 05:30 | 47.35 | 47.29
2017-03-07 06:00 | 50.73 | 50.58
2017-03-07 06:30 | 56.45 | 55.99
2017-03-07 07:00 | 63.61 | 61.72
2017-03-07 07:30 | 74.05 | 69.44
2017-03-07 08:00 | 77.08 | 72.68
2017-03-07 08:30 | 80.9 | 77.31
2017-03-07 09:00 | 84.88 | 81.36
2017-03-07 09:30 | 87.12 | 83.66
2017-03-07 10:00 | 88.95 | 85.56
2017-03-07 10:30 | 88.18 | 84.68
2017-03-07 11:00 | 89.72 | 86.27
2017-03-07 11:30 | 90.72 | 87.28
2017-03-07 12:00 | 91.95 | 88.54
2017-03-07 12:30 | 95.33 | 89.59
2017-03-07 13:00 | 98.7 | 91.25
2017-03-07 13:30 | 95.41 | 87.75
2017-03-07 14:00 | 95.77 | 88.16
2017-03-07 14:30 | 95.04 | 87.33
2017-03-07 15:00 | 95.08 | 87.45
2017-03-07 15:30 | 95.67 | 88.12
2017-03-07 16:00 | 95.55 | 88.09
2017-03-07 16:30 | 95.08 | 87.72
2017-03-07 17:00 | 93.7 | 86.4
2017-03-07 17:30 | 89.05 | 81.57
2017-03-07 18:00 | 77.37 | 75.68
2017-03-07 18:30 | 73.21 | 72.45
2017-03-07 19:00 | 71.8 | 71.01
2017-03-07 19:30 | 68.89 | 68.21
2017-03-07 20:00 | 65.44 | 64.67
2017-03-07 20:30 | 62.15 | 61.27
2017-03-07 21:00 | 59.15 | 58.09
2017-03-07 21:30 | 56.68 | 55.3
2017-03-07 22:00 | 52.33 | 50.24
2017-03-07 22:30 | 46.97 | 46.91
2017-03-07 23:00 | 48.55 | 47.94
2017-03-07 23:30 | 45.53 | 44.17
2017-03-08 | 43.7 | 42.31
2017-03-08 00:30 | 43.06 | 41.67
2017-03-08 01:00 | 41.73 | 40.3
2017-03-08 01:30 | 40.87 | 39.44
2017-03-08 02:00 | 40.45 | 39
2017-03-08 02:30 | 39.73 | 38.29
2017-03-08 03:00 | 39.41 | 37.96
2017-03-08 03:30 | 39.63 | 38.18
2017-03-08 04:00 | 39.58 | 38.14
2017-03-08 04:30 | 40.37 | 38.94
2017-03-08 05:00 | 41.1 | 39.68
2017-03-08 05:30 | 43.16 | 41.75
2017-03-08 06:00 | 46.42 | 45.03
2017-03-08 06:30 | 51.49 | 50.13
2017-03-08 07:00 | 57.12 | 55.76
2017-03-08 07:30 | 63.82 | 62.57
2017-03-08 08:00 | 70.74 | 66.55
2017-03-08 08:30 | 70.81 | 66.13
2017-03-08 09:00 | 71.51 | 67.4
2017-03-08 09:30 | 72.29 | 68.43
2017-03-08 10:00 | 69.53 | 65.47
2017-03-08 10:30 | 70.07 | 65.95
2017-03-08 11:00 | 71.84 | 67.79
2017-03-08 11:30 | 73.17 | 69.19
2017-03-08 12:00 | 73.99 | 70.02
2017-03-08 12:30 | 81.79 | 78.24
2017-03-08 13:00 | 81.62 | 78.06
2017-03-08 13:30 | 82.71 | 79.19
2017-03-08 14:00 | 83.73 | 80.25
2017-03-08 14:30 | 84.36 | 80.91
2017-03-08 15:00 | 83.7 | 80.24
2017-03-08 15:30 | 84.33 | 80.94
2017-03-08 16:00 | 83.81 | 80.49
2017-03-08 16:30 | 82.41 | 79.16
2017-03-08 17:00 | 79.67 | 76.41
2017-03-08 17:30 | 75.92 | 72.66
2017-03-08 18:00 | 73.89 | 70.66
2017-03-08 18:30 | 72.07 | 68.85
2017-03-08 19:00 | 72.13 | 68.76
2017-03-08 19:30 | 70.04 | 66.56
2017-03-08 20:00 | 67.96 | 64.39
2017-03-08 20:30 | 65.59 | 61.93
2017-03-08 21:00 | 62.73 | 58.93
2017-03-08 21:30 | 58.22 | 55.65
2017-03-08 22:00 | 52.26 | 51.85
2017-03-08 22:30 | 49.11 | 49.05
2017-03-08 23:00 | 48.16 | 48.11
2017-03-08 23:30 | 43.5 | 43.47
2017-03-09 | 41.68 | 41.65
2017-03-09 00:30 | 40.7 | 40.68
2017-03-09 01:00 | 39.76 | 39.74
2017-03-09 01:30 | 39.19 | 39.16
2017-03-09 02:00 | 38.32 | 38.29
2017-03-09 02:30 | 37.64 | 37.6
2017-03-09 03:00 | 37.51 | 37.47
2017-03-09 03:30 | 37.31 | 37.26
2017-03-09 04:00 | 37.06 | 37
2017-03-09 04:30 | 37.32 | 37.28
2017-03-09 05:00 | 38.14 | 38.11
2017-03-09 05:30 | 40.34 | 40.31
2017-03-09 06:00 | 42.94 | 42.89
2017-03-09 06:30 | 47.71 | 47.54
2017-03-09 07:00 | 55.16 | 52.93
2017-03-09 07:30 | 64.21 | 59.19
2017-03-09 08:00 | 66.64 | 61.78
2017-03-09 08:30 | 67.96 | 63.83
2017-03-09 09:00 | 69.4 | 65.56
2017-03-09 09:30 | 70.19 | 66.4
2017-03-09 10:00 | 69.99 | 66.19
2017-03-09 10:30 | 70.43 | 66.63
2017-03-09 11:00 | 70.28 | 66.49
2017-03-09 11:30 | 69.17 | 65.28
2017-03-09 12:00 | 67.43 | 63.41
2017-03-09 12:30 | 66.2 | 62.09
2017-03-09 13:00 | 68.42 | 64.48
2017-03-09 13:30 | 68.9 | 65
2017-03-09 14:00 | 69.37 | 65.49
2017-03-09 14:30 | 68.72 | 64.89
2017-03-09 15:00 | 66.93 | 63.04
2017-03-09 15:30 | 64.03 | 60.47
2017-03-09 16:00 | 60.36 | 59.89
2017-03-09 16:30 | 60.99 | 60.34
2017-03-09 17:00 | 59.88 | 58.85
2017-03-09 17:30 | 57.52 | 56.41
2017-03-09 18:00 | 56.91 | 55.86
2017-03-09 18:30 | 56.67 | 55.33
2017-03-09 19:00 | 57.67 | 56.47
2017-03-09 19:30 | 57.03 | 55.75
2017-03-09 20:00 | 55.14 | 53.66
2017-03-09 20:30 | 53.6 | 51.82
2017-03-09 21:00 | 52.17 | 50.15
2017-03-09 21:30 | 49.47 | 46.89
2017-03-09 22:00 | 47.1 | 44.03
2017-03-09 22:30 | 45.26 | 41.9
2017-03-09 23:00 | 43.73 | 41.77
2017-03-09 23:30 | 40.42 | 38.22
2017-03-10 | 38.65 | 36.31
2017-03-10 00:30 | 37.82 | 35.38
2017-03-10 01:00 | 36.42 | 33.84
2017-03-10 01:30 | 36.15 | 33.54
2017-03-10 02:00 | 35.67 | 33
2017-03-10 02:30 | 34.75 | 31.95
2017-03-10 03:00 | 34.61 | 31.78
2017-03-10 03:30 | 34.61 | 31.77
2017-03-10 04:00 | 34.5 | 31.64
2017-03-10 04:30 | 34.87 | 32.07
2017-03-10 05:00 | 35.83 | 33.15
2017-03-10 05:30 | 37.71 | 35.27
2017-03-10 06:00 | 39.98 | 37.79
2017-03-10 06:30 | 43.66 | 41.8
2017-03-10 07:00 | 48.6 | 47.15
2017-03-10 07:30 | 53.64 | 52.21
2017-03-10 08:00 | 56.2 | 54.73
2017-03-10 08:30 | 57.91 | 57.05
2017-03-10 09:00 | 60.04 | 59.21
2017-03-10 09:30 | 61.82 | 60.96
2017-03-10 10:00 | 62.9 | 62.03
2017-03-10 10:30 | 64.47 | 63.6
2017-03-10 11:00 | 65.08 | 64.17
2017-03-10 11:30 | 66 | 65.09
2017-03-10 12:00 | 67.27 | 66.36
2017-03-10 12:30 | 67.38 | 66.48
2017-03-10 13:00 | 67.4 | 66.49
2017-03-10 13:30 | 67.1 | 66.21
2017-03-10 14:00 | 67.58 | 66.71
2017-03-10 14:30 | 67.25 | 66.39
2017-03-10 15:00 | 67.3 | 66.46
2017-03-10 15:30 | 66.36 | 65.54
2017-03-10 16:00 | 66.88 | 66.1
2017-03-10 16:30 | 67.43 | 66.71
2017-03-10 17:00 | 65.67 | 64.94
2017-03-10 17:30 | 64.1 | 63.19
2017-03-10 18:00 | 61.55 | 60.59
2017-03-10 18:30 | 59.59 | 58.56
2017-03-10 19:00 | 60.64 | 59.68
2017-03-10 19:30 | 60.23 | 59.24
2017-03-10 20:00 | 57.84 | 56.66
2017-03-10 20:30 | 56.37 | 54.89
2017-03-10 21:00 | 53.48 | 51.13
2017-03-10 21:30 | 51.25 | 48.71
2017-03-10 22:00 | 49.57 | 46.87
2017-03-10 22:30 | 47.25 | 44.29
2017-03-10 23:00 | 45.75 | 43.04
2017-03-10 23:30 | 42.58 | 39.57
2017-03-11 | 40.26 | 37.33
2017-03-11 00:30 | 38.5 | 36.44
2017-03-11 01:00 | 36.48 | 34.68
2017-03-11 01:30 | 35.74 | 33.96
2017-03-11 02:00 | 35.37 | 33.59
2017-03-11 02:30 | 34.95 | 33.16
2017-03-11 03:00 | 34.45 | 32.64
2017-03-11 03:30 | 34.44 | 32.65
2017-03-11 04:00 | 34.66 | 32.88
2017-03-11 04:30 | 35.1 | 33.34
2017-03-11 05:00 | 34.74 | 32.95
2017-03-11 05:30 | 35.38 | 33.59
2017-03-11 06:00 | 35.7 | 33.93
2017-03-11 06:30 | 37.76 | 36.06
2017-03-11 07:00 | 39.65 | 37.98
2017-03-11 07:30 | 42.82 | 41.19
2017-03-11 08:00 | 45.06 | 43.41
2017-03-11 08:30 | 48.53 | 46.89
2017-03-11 09:00 | 50.67 | 49.01
2017-03-11 09:30 | 52.47 | 50.81
2017-03-11 10:00 | 54.73 | 51.61
2017-03-11 10:30 | 57.69 | 51.67
2017-03-11 11:00 | 57.95 | 51.91
2017-03-11 11:30 | 57.61 | 51.55
2017-03-11 12:00 | 58.32 | 52.19
2017-03-11 12:30 | 57.66 | 51.56
2017-03-11 13:00 | 57.75 | 51.69
2017-03-11 13:30 | 57.66 | 51.62
2017-03-11 14:00 | 53.26 | 50.82
2017-03-11 14:30 | 51.27 | 50.93
2017-03-11 15:00 | 52.03 | 51.69
2017-03-11 15:30 | 52.55 | 52.21
2017-03-11 16:00 | 53.75 | 53.39
2017-03-11 16:30 | 54.35 | 53.88
2017-03-11 17:00 | 54.28 | 53.69
2017-03-11 17:30 | 55.44 | 54.82
2017-03-11 18:00 | 55.61 | 54.89
2017-03-11 18:30 | 55.88 | 55.12
2017-03-11 19:00 | 56.49 | 55.89
2017-03-11 19:30 | 56.25 | 55.64
2017-03-11 20:00 | 54.44 | 53.74
2017-03-11 20:30 | 52.72 | 51.85
2017-03-11 21:00 | 50.87 | 49.83
2017-03-11 21:30 | 49.26 | 48.02
2017-03-11 22:00 | 47.59 | 46.05
2017-03-11 22:30 | 46.14 | 44.32
2017-03-11 23:00 | 46.27 | 44.32
2017-03-11 23:30 | 40.63 | 40.53
2017-03-12 | 38.73 | 38.66
2017-03-12 00:30 | 37.83 | 37.76
2017-03-12 01:00 | 36.16 | 36.11
2017-03-12 01:30 | 35.63 | 35.57
2017-03-12 02:00 | 35 | 34.95
2017-03-12 02:30 | 34.56 | 34.51
2017-03-12 03:00 | 34.23 | 34.19
2017-03-12 03:30 | 33.97 | 33.93
2017-03-12 04:00 | 33.63 | 33.59
2017-03-12 04:30 | 33.48 | 33.44
2017-03-12 05:00 | 33.53 | 33.49
2017-03-12 05:30 | 34.01 | 33.96
2017-03-12 06:00 | 34.15 | 34.11
2017-03-12 06:30 | 34.37 | 34.34
2017-03-12 07:00 | 35.41 | 35.37
2017-03-12 07:30 | 36.94 | 36.88
2017-03-12 08:00 | 38.17 | 38.08
2017-03-12 08:30 | 40.72 | 40.48
2017-03-12 09:00 | 42.99 | 42.56
2017-03-12 09:30 | 45.09 | 44.52
2017-03-12 10:00 | 49.77 | 46.2
2017-03-12 10:30 | 53.58 | 47.35
2017-03-12 11:00 | 54.07 | 47.87
2017-03-12 11:30 | 54.06 | 48.96
2017-03-12 12:00 | 54.05 | 49.22
2017-03-12 12:30 | 55.01 | 50.31
2017-03-12 13:00 | 55.21 | 50.54
2017-03-12 13:30 | 55.35 | 50.68
2017-03-12 14:00 | 55.28 | 50.61
2017-03-12 14:30 | 55.31 | 50.71
2017-03-12 15:00 | 56.07 | 51.53
2017-03-12 15:30 | 56.65 | 52.2
2017-03-12 16:00 | 57.41 | 53.03
2017-03-12 16:30 | 58.11 | 53.85
2017-03-12 17:00 | 58 | 53.75
2017-03-12 17:30 | 58.98 | 54.87
2017-03-12 18:00 | 59.87 | 55.87
2017-03-12 18:30 | 59.76 | 55.76
2017-03-12 19:00 | 61.64 | 57.75
2017-03-12 19:30 | 61.15 | 57.24
2017-03-12 20:00 | 59.2 | 55.14
2017-03-12 20:30 | 57.11 | 52.9
2017-03-12 21:00 | 54.89 | 50.54
2017-03-12 21:30 | 50.57 | 48.15
2017-03-12 22:00 | 47.53 | 45.58
2017-03-12 22:30 | 45.52 | 43.29
2017-03-12 23:00 | 44.98 | 42.49
2017-03-12 23:30 | 42 | 39.05
2017-03-13 | 40.16 | 37.09
2017-03-13 00:30 | 36.23 | 36.18
2017-03-13 01:00 | 35.04 | 35
2017-03-13 01:30 | 34.38 | 34.34
2017-03-13 02:00 | 34.04 | 34
2017-03-13 02:30 | 33.86 | 33.83
2017-03-13 03:00 | 33.45 | 33.41
2017-03-13 03:30 | 33.44 | 33.4
2017-03-13 04:00 | 33.55 | 33.52
2017-03-13 04:30 | 34.08 | 34.04
2017-03-13 05:00 | 35.07 | 35.02
2017-03-13 05:30 | 37.21 | 37.13
2017-03-13 06:00 | 40.34 | 40.18
2017-03-13 06:30 | 45.54 | 45.13
2017-03-13 07:00 | 54.64 | 50.61
2017-03-13 07:30 | 61.7 | 57.45
2017-03-13 08:00 | 65.23 | 61.31
2017-03-13 08:30 | 68.11 | 64.3
2017-03-13 09:00 | 70.87 | 67.09
2017-03-13 09:30 | 73.05 | 69.29
2017-03-13 10:00 | 74.31 | 70.55
2017-03-13 10:30 | 75.55 | 71.82
2017-03-13 11:00 | 77.16 | 73.44
2017-03-13 11:30 | 78.41 | 74.74
2017-03-13 12:00 | 79.66 | 76.04
2017-03-13 12:30 | 81.14 | 77.57
2017-03-13 13:00 | 81.14 | 77.58
2017-03-13 13:30 | 82.06 | 78.5
2017-03-13 14:00 | 82.88 | 79.39
2017-03-13 14:30 | 83.52 | 80.04
2017-03-13 15:00 | 83.74 | 80.26
2017-03-13 15:30 | 83.41 | 79.98
2017-03-13 16:00 | 84.18 | 80.86
2017-03-13 16:30 | 84.52 | 81.29
2017-03-13 17:00 | 82.67 | 79.46
2017-03-13 17:30 | 79.51 | 76.37
2017-03-13 18:00 | 77 | 73.89
2017-03-13 18:30 | 75.03 | 71.96
2017-03-13 19:00 | 75.94 | 72.9
2017-03-13 19:30 | 74.95 | 71.88
2017-03-13 20:00 | 72.5 | 69.37
2017-03-13 20:30 | 69.6 | 66.39
2017-03-13 21:00 | 66.92 | 63.61
2017-03-13 21:30 | 63.1 | 60.24
2017-03-13 22:00 | 58.62 | 56.21
2017-03-13 22:30 | 53.02 | 52.87
2017-03-13 23:00 | 51.59 | 51.57
2017-03-13 23:30 | 47.75 | 47.71
2017-03-14 | 45.47 | 45.39
2017-03-14 00:30 | 44.14 | 44
2017-03-14 01:00 | 42.85 | 42.67
2017-03-14 01:30 | 42.24 | 42.04
2017-03-14 02:00 | 41.75 | 41.5
2017-03-14 02:30 | 41.21 | 40.9
2017-03-14 03:00 | 40.53 | 40.41
2017-03-14 03:30 | 40.26 | 40.24
2017-03-14 04:00 | 40.44 | 40.41
2017-03-14 04:30 | 41.03 | 41.01
2017-03-14 05:00 | 41.32 | 41.3
2017-03-14 05:30 | 43.84 | 43.8
2017-03-14 06:00 | 47.17 | 47.08
2017-03-14 06:30 | 55.48 | 53.18
2017-03-14 07:00 | 63.78 | 58.89
2017-03-14 07:30 | 69.75 | 66
2017-03-14 08:00 | 73.29 | 69.69
2017-03-14 08:30 | 78.03 | 74.48
2017-03-14 09:00 | 80.24 | 76.68
2017-03-14 09:30 | 77.45 | 75.94
2017-03-14 10:00 | 78.1 | 77.91
2017-03-14 10:30 | 78.82 | 78.59
2017-03-14 11:00 | 81.05 | 79.53
2017-03-14 11:30 | 82.97 | 79.35
2017-03-14 12:00 | 85.43 | 81.91
2017-03-14 12:30 | 94.92 | 84.79
2017-03-14 13:00 | 98.25 | 84.55
2017-03-14 13:30 | 99.54 | 85.91
2017-03-14 14:00 | 92.16 | 84.13
2017-03-14 14:30 | 93.84 | 90.03
2017-03-14 15:00 | 92.02 | 88.18
2017-03-14 15:30 | 89.68 | 85.81
2017-03-14 16:00 | 86.99 | 84.31
2017-03-14 16:30 | 84.5 | 83.63
2017-03-14 17:00 | 81.72 | 80.9
2017-03-14 17:30 | 77.83 | 76.58
2017-03-14 18:00 | 75.46 | 73.94
2017-03-14 18:30 | 75 | 73.41
2017-03-14 19:00 | 76.27 | 74.73
2017-03-14 19:30 | 74.67 | 73.05
2017-03-14 20:00 | 72.23 | 70.5
2017-03-14 20:30 | 70.39 | 68.57
2017-03-14 21:00 | 67.67 | 65.69
2017-03-14 21:30 | 71.04 | 61.74
2017-03-14 22:00 | 68.83 | 58.48
2017-03-14 22:30 | 66.42 | 55.3
2017-03-14 23:00 | 65.6 | 54.17
2017-03-14 23:30 | 62.23 | 49.69
2017-03-15 | 60.62 | 47.45
2017-03-15 00:30 | 60 | 46.51
2017-03-15 01:00 | 58.75 | 44.77
2017-03-15 01:30 | 58.22 | 44.02
2017-03-15 02:00 | 57.61 | 43.08
2017-03-15 02:30 | 57.01 | 42.09
2017-03-15 03:00 | 55.95 | 41.46
2017-03-15 03:30 | 55.72 | 41.16
2017-03-15 04:00 | 55.65 | 41.07
2017-03-15 04:30 | 56.06 | 41.71
2017-03-15 05:00 | 56.74 | 42.77
2017-03-15 05:30 | 58.27 | 45.18
2017-03-15 06:00 | 60.63 | 48.61
2017-03-15 06:30 | 64.59 | 54.14
2017-03-15 07:00 | 60.69 | 59.5
2017-03-15 07:30 | 67.6 | 66.47
2017-03-15 08:00 | 72 | 70.52
2017-03-15 08:30 | 75.16 | 73.78
2017-03-15 09:00 | 76.54 | 75.41
2017-03-15 09:30 | 76.8 | 75.72
2017-03-15 10:00 | 77.9 | 76.84
2017-03-15 10:30 | 78.17 | 77.15
2017-03-15 11:00 | 79.83 | 78.88
2017-03-15 11:30 | 80.78 | 79.87
2017-03-15 12:00 | 81.65 | 80.78
2017-03-15 12:30 | 83.23 | 82.38
2017-03-15 13:00 | 84.97 | 84.16
2017-03-15 13:30 | 84.96 | 84.15
2017-03-15 14:00 | 85.34 | 84.53
2017-03-15 14:30 | 85.91 | 85.12
2017-03-15 15:00 | 85.87 | 85.06
2017-03-15 15:30 | 86.15 | 85.31
2017-03-15 16:00 | 85.84 | 84.94
2017-03-15 16:30 | 83.83 | 82.82
2017-03-15 17:00 | 79.56 | 78.35
2017-03-15 17:30 | 74.12 | 72.74
2017-03-15 18:00 | 74.85 | 69.66
2017-03-15 18:30 | 78.91 | 68.35
2017-03-15 19:00 | 78.82 | 68.22
2017-03-15 19:30 | 77 | 65.94
2017-03-15 20:00 | 75.24 | 63.67
2017-03-15 20:30 | 73.94 | 61.93
2017-03-15 21:00 | 71.72 | 59.26
2017-03-15 21:30 | 67.04 | 55.93
2017-03-15 22:00 | 64.86 | 53.24
2017-03-15 22:30 | 61.9 | 49.54
2017-03-15 23:00 | 59.98 | 47.35
2017-03-15 23:30 | 57.71 | 44.24
2017-03-16 | 56.09 | 41.86
2017-03-16 00:30 | 55.23 | 40.6
2017-03-16 01:00 | 54.25 | 38.99
2017-03-16 01:30 | 53.61 | 38.07
2017-03-16 02:00 | 53.4 | 37.74
2017-03-16 02:30 | 52.8 | 36.99
2017-03-16 03:00 | 51.75 | 36.24
2017-03-16 03:30 | 51.82 | 36.32
2017-03-16 04:00 | 51.83 | 36.32
2017-03-16 04:30 | 52.44 | 37.31
2017-03-16 05:00 | 52.83 | 37.98
2017-03-16 05:30 | 54.54 | 40.73
2017-03-16 06:00 | 56.44 | 43.65
2017-03-16 06:30 | 58.97 | 49.12
2017-03-16 07:00 | 56.33 | 55.02
2017-03-16 07:30 | 62.75 | 61.62
2017-03-16 08:00 | 66.63 | 65.44
2017-03-16 08:30 | 70.1 | 68.5
2017-03-16 09:00 | 72.9 | 71.67
2017-03-16 09:30 | 74.42 | 73.25
2017-03-16 10:00 | 74.86 | 73.74
2017-03-16 10:30 | 75.54 | 74.46
2017-03-16 11:00 | 77.21 | 76.2
2017-03-16 11:30 | 78.93 | 77.97
2017-03-16 12:00 | 79.76 | 78.82
2017-03-16 12:30 | 80.67 | 79.75
2017-03-16 13:00 | 81.16 | 80.26
2017-03-16 13:30 | 82.23 | 81.35
2017-03-16 14:00 | 83.11 | 82.24
2017-03-16 14:30 | 83.67 | 82.81
2017-03-16 15:00 | 83.35 | 82.48
2017-03-16 15:30 | 83.43 | 82.53
2017-03-16 16:00 | 84.11 | 83.19
2017-03-16 16:30 | 84.1 | 83.11
2017-03-16 17:00 | 83.66 | 82.6
2017-03-16 17:30 | 79.54 | 78.28
2017-03-16 18:00 | 76.95 | 75.52
2017-03-16 18:30 | 76.79 | 75.3
2017-03-16 19:00 | 77.72 | 76.26
2017-03-16 19:30 | 76.29 | 74.78
2017-03-16 20:00 | 76.56 | 75.03
2017-03-16 20:30 | 72.96 | 71.26
2017-03-16 21:00 | 70.09 | 68.25
2017-03-16 21:30 | 67.95 | 63.86
2017-03-16 22:00 | 65.06 | 59.37
2017-03-16 22:30 | 61.33 | 55.82
2017-03-16 23:00 | 58.72 | 52.75
2017-03-16 23:30 | 55.88 | 49.42
2017-03-17 | 54.11 | 47.29
2017-03-17 00:30 | 52.93 | 45.81
2017-03-17 01:00 | 51.44 | 43.97
2017-03-17 01:30 | 50.73 | 43.1
2017-03-17 02:00 | 49.68 | 42.35
2017-03-17 02:30 | 49.1 | 41.63
2017-03-17 03:00 | 48.73 | 41.15
2017-03-17 03:30 | 48.31 | 40.6
2017-03-17 04:00 | 48.36 | 40.64
2017-03-17 04:30 | 48.64 | 41.05
2017-03-17 05:00 | 49.12 | 41.66
2017-03-17 05:30 | 51.02 | 44.12
2017-03-17 06:00 | 53.48 | 47.17
2017-03-17 06:30 | 57.81 | 52.39
2017-03-17 07:00 | 62.39 | 57.79
2017-03-17 07:30 | 67.01 | 65.26
2017-03-17 08:00 | 69.4 | 69.38
2017-03-17 08:30 | 72.27 | 72.26
2017-03-17 09:00 | 75.06 | 75.02
2017-03-17 09:30 | 76.63 | 76.57
2017-03-17 10:00 | 78.06 | 77.98
2017-03-17 10:30 | 79.79 | 79.66
2017-03-17 11:00 | 80.21 | 80.05
2017-03-17 11:30 | 81.49 | 81.3
2017-03-17 12:00 | 82.22 | 81.98
2017-03-17 12:30 | 83.94 | 83.68
2017-03-17 13:00 | 83.71 | 83.48
2017-03-17 13:30 | 83.82 | 83.61
2017-03-17 14:00 | 83.97 | 83.77
2017-03-17 14:30 | 83.7 | 83.54
2017-03-17 15:00 | 83.04 | 82.92
2017-03-17 15:30 | 82.54 | 82.48
2017-03-17 16:00 | 82.75 | 82.71
2017-03-17 16:30 | 83.48 | 83.46
2017-03-17 17:00 | 80.75 | 80.73
2017-03-17 17:30 | 78.74 | 78.61
2017-03-17 18:00 | 76.24 | 75.06
2017-03-17 18:30 | 74.47 | 72.81
2017-03-17 19:00 | 75.37 | 73.76
2017-03-17 19:30 | 74.23 | 72.57
2017-03-17 20:00 | 72.24 | 70.49
2017-03-17 20:30 | 70.28 | 68.42
2017-03-17 21:00 | 75.55 | 65.11
2017-03-17 21:30 | 74.36 | 62.41
2017-03-17 22:00 | 71.54 | 59.31
2017-03-17 22:30 | 67.43 | 56.23
2017-03-17 23:00 | 66.59 | 55.11
2017-03-17 23:30 | 62.65 | 50.56
2017-03-18 | 60.38 | 47.99
2017-03-18 00:30 | 59.18 | 46.29
2017-03-18 01:00 | 57.76 | 44.31
2017-03-18 01:30 | 57.13 | 43.39
2017-03-18 02:00 | 56.42 | 42.28
2017-03-18 02:30 | 55.77 | 41.3
2017-03-18 03:00 | 54.68 | 40.03
2017-03-18 03:30 | 53.56 | 39.06
2017-03-18 04:00 | 53.18 | 38.45
2017-03-18 04:30 | 53.24 | 38.56
2017-03-18 05:00 | 53.34 | 38.68
2017-03-18 05:30 | 53.77 | 39.43
2017-03-18 06:00 | 54.18 | 40.11
2017-03-18 06:30 | 55.1 | 41.5
2017-03-18 07:00 | 56.71 | 43.94
2017-03-18 07:30 | 54.44 | 46.93
2017-03-18 08:00 | 51.19 | 49.84
2017-03-18 08:30 | 54.43 | 53.01
2017-03-18 09:00 | 57.23 | 55.68
2017-03-18 09:30 | 59.54 | 57.71
2017-03-18 10:00 | 61.06 | 59.04
2017-03-18 10:30 | 62.82 | 60.59
2017-03-18 11:00 | 64.68 | 62.28
2017-03-18 11:30 | 64.33 | 62.51
2017-03-18 12:00 | 62.44 | 62.42
2017-03-18 12:30 | 62.98 | 62.96
2017-03-18 13:00 | 63.12 | 63.1
2017-03-18 13:30 | 65.81 | 65.78
2017-03-18 14:00 | 67.55 | 67.12
2017-03-18 14:30 | 67.35 | 65.83
2017-03-18 15:00 | 64.3 | 62.68
2017-03-18 15:30 | 64.43 | 62.78
2017-03-18 16:00 | 64.22 | 62.54
2017-03-18 16:30 | 63.38 | 61.62
2017-03-18 17:00 | 60.49 | 58.55
2017-03-18 17:30 | 59.5 | 57.47
2017-03-18 18:00 | 59.16 | 57.09
2017-03-18 18:30 | 59.36 | 57.32
2017-03-18 19:00 | 59.26 | 57.25
2017-03-18 19:30 | 58.05 | 55.96
2017-03-18 20:00 | 56.14 | 53.93
2017-03-18 20:30 | 62.01 | 51.83
2017-03-18 21:00 | 63.76 | 50.06
2017-03-18 21:30 | 62.53 | 48.33
2017-03-18 22:00 | 61.79 | 47.08
2017-03-18 22:30 | 60.52 | 45.21
2017-03-18 23:00 | 58.97 | 45.16
2017-03-18 23:30 | 55.32 | 41.75
2017-03-19 | 54.24 | 40.09
2017-03-19 00:30 | 53.78 | 39.31
2017-03-19 01:00 | 52.73 | 37.73
2017-03-19 01:30 | 52.39 | 37.19
2017-03-19 02:00 | 52.2 | 36.86
2017-03-19 02:30 | 51.88 | 36.33
2017-03-19 03:00 | 51.67 | 35.94
2017-03-19 03:30 | 51.58 | 35.77
2017-03-19 04:00 | 51.37 | 35.44
2017-03-19 04:30 | 51.47 | 35.7
2017-03-19 05:00 | 51.49 | 35.71
2017-03-19 05:30 | 51.86 | 36.38
2017-03-19 06:00 | 51.93 | 36.48
2017-03-19 06:30 | 52.16 | 36.71
2017-03-19 07:00 | 53 | 38.05
2017-03-19 07:30 | 54.39 | 40.32
2017-03-19 08:00 | 56.2 | 42.92
2017-03-19 08:30 | 57.91 | 45.53
2017-03-19 09:00 | 57.95 | 45.87
2017-03-19 09:30 | 55.4 | 48.72
2017-03-19 10:00 | 52.26 | 50.93
2017-03-19 10:30 | 55.03 | 53.69
2017-03-19 11:00 | 58.5 | 57.25
2017-03-19 11:30 | 59.24 | 58
2017-03-19 12:00 | 58.25 | 57.02
2017-03-19 12:30 | 59.14 | 57.94
2017-03-19 13:00 | 58.6 | 57.41
2017-03-19 13:30 | 57.39 | 56.2
2017-03-19 14:00 | 54.69 | 53.44
2017-03-19 14:30 | 54.04 | 52.77
2017-03-19 15:00 | 54.43 | 53.18
2017-03-19 15:30 | 55.67 | 54.45
2017-03-19 16:00 | 57.1 | 55.92
2017-03-19 16:30 | 58.6 | 57.43
2017-03-19 17:00 | 57.54 | 56.32
2017-03-19 17:30 | 58.37 | 57.17
2017-03-19 18:00 | 59.56 | 58.38
2017-03-19 18:30 | 60.99 | 59.86
2017-03-19 19:00 | 61.91 | 60.82
2017-03-19 19:30 | 60.67 | 59.54
2017-03-19 20:00 | 58.64 | 57.45
2017-03-19 20:30 | 55.88 | 54.57
2017-03-19 21:00 | 53.7 | 52.3
2017-03-19 21:30 | 51.52 | 50
2017-03-19 22:00 | 49.24 | 47.59
2017-03-19 22:30 | 47.16 | 45.37
2017-03-19 23:00 | 46.73 | 44.9
2017-03-19 23:30 | 43.03 | 40.95
2017-03-20 | 41.72 | 39.54
2017-03-20 00:30 | 41.19 | 38.93
2017-03-20 01:00 | 40.04 | 37.69
2017-03-20 01:30 | 39.68 | 37.3
2017-03-20 02:00 | 39.13 | 36.71
2017-03-20 02:30 | 38.87 | 36.41
2017-03-20 03:00 | 38.63 | 36.16
2017-03-20 03:30 | 38.69 | 36.21
2017-03-20 04:00 | 38.53 | 36.03
2017-03-20 04:30 | 39.51 | 37.13
2017-03-20 05:00 | 40.53 | 38.26
2017-03-20 05:30 | 43.16 | 41.17
2017-03-20 06:00 | 46.49 | 44.79
2017-03-20 06:30 | 52.33 | 50.93
2017-03-20 07:00 | 57.72 | 56.48
2017-03-20 07:30 | 64.48 | 63.29
2017-03-20 08:00 | 67.92 | 66.8
2017-03-20 08:30 | 70.86 | 69.49
2017-03-20 09:00 | 74.07 | 72.21
2017-03-20 09:30 | 76.89 | 74.75
2017-03-20 10:00 | 76.84 | 74.65
2017-03-20 10:30 | 75.09 | 72.65
2017-03-20 11:00 | 75.34 | 72.69
2017-03-20 11:30 | 75.76 | 72.99
2017-03-20 12:00 | 78.04 | 75.26
2017-03-20 12:30 | 79.1 | 76.56
2017-03-20 13:00 | 77.2 | 74.83
2017-03-20 13:30 | 78.72 | 76.4
2017-03-20 14:00 | 77.17 | 75.15
2017-03-20 14:30 | 75.43 | 73.49
2017-03-20 15:00 | 72.96 | 71.23
2017-03-20 15:30 | 70.09 | 68.56
2017-03-20 16:00 | 67.57 | 66.07
2017-03-20 16:30 | 66.88 | 65.43
2017-03-20 17:00 | 64.63 | 63.2
2017-03-20 17:30 | 62.42 | 61.04
2017-03-20 18:00 | 61.87 | 60.56
2017-03-20 18:30 | 62.43 | 61.06
2017-03-20 19:00 | 61.91 | 60.49
2017-03-20 19:30 | 59.57 | 58.06
2017-03-20 20:00 | 56.93 | 55.29
2017-03-20 20:30 | 54.63 | 52.86
2017-03-20 21:00 | 52.54 | 50.63
2017-03-20 21:30 | 50.24 | 48.17
2017-03-20 22:00 | 48.39 | 46.17
2017-03-20 22:30 | 54.52 | 43.62
2017-03-20 23:00 | 58.01 | 43.39
2017-03-20 23:30 | 55.56 | 39.8
2017-03-21 | 54.26 | 37.79
2017-03-21 00:30 | 53.37 | 36.9
2017-03-21 01:00 | 52.11 | 35.58
2017-03-21 01:30 | 51.61 | 34.82
2017-03-21 02:00 | 51.47 | 34.57
2017-03-21 02:30 | 51.15 | 34.28
2017-03-21 03:00 | 50.22 | 33.61
2017-03-21 03:30 | 50.14 | 33.43
2017-03-21 04:00 | 50.28 | 33.61
2017-03-21 04:30 | 50.96 | 34.82
2017-03-21 05:00 | 51.54 | 35.82
2017-03-21 05:30 | 53.06 | 38.35
2017-03-21 06:00 | 54.8 | 41.22
2017-03-21 06:30 | 58.82 | 47.15
2017-03-21 07:00 | 55.39 | 53.56
2017-03-21 07:30 | 60.71 | 59.54
2017-03-21 08:00 | 61.85 | 60.71
2017-03-21 08:30 | 64.9 | 63.59
2017-03-21 09:00 | 66.95 | 65.25
2017-03-21 09:30 | 68.01 | 66.06
2017-03-21 10:00 | 70.72 | 68.62
2017-03-21 10:30 | 71.12 | 69.06
2017-03-21 11:00 | 70.26 | 68.03
2017-03-21 11:30 | 72.85 | 70.4
2017-03-21 12:00 | 72.32 | 70.7
2017-03-21 12:30 | 73.36 | 72.16
2017-03-21 13:00 | 72.69 | 71.48
2017-03-21 13:30 | 73.84 | 72.65
2017-03-21 14:00 | 74.41 | 73.23
2017-03-21 14:30 | 73.42 | 72.21
2017-03-21 15:00 | 73.19 | 71.94
2017-03-21 15:30 | 72.65 | 71.34
2017-03-21 16:00 | 71.46 | 70.02
2017-03-21 16:30 | 69.84 | 68.24
2017-03-21 17:00 | 67.71 | 65.94
2017-03-21 17:30 | 65.71 | 63.73
2017-03-21 18:00 | 71.3 | 61.54
2017-03-21 18:30 | 72.79 | 60.64
2017-03-21 19:00 | 73.22 | 61.23
2017-03-21 19:30 | 72.12 | 59.77
2017-03-21 20:00 | 70.46 | 57.55
2017-03-21 20:30 | 68.88 | 55.4
2017-03-21 21:00 | 67.61 | 53.6
2017-03-21 21:30 | 65.73 | 50.96
2017-03-21 22:00 | 62.56 | 48.64
2017-03-21 22:30 | 58.98 | 46.02
2017-03-21 23:00 | 58.55 | 45.31
2017-03-21 23:30 | 55.73 | 41.28
2017-03-22 | 54.23 | 39.04
2017-03-22 00:30 | 53.84 | 38.32
2017-03-22 01:00 | 53 | 37.04
2017-03-22 01:30 | 52.58 | 36.32
2017-03-22 02:00 | 51.9 | 35.62
2017-03-22 02:30 | 51.05 | 34.96
2017-03-22 03:00 | 50.76 | 34.55
2017-03-22 03:30 | 50.87 | 34.71
2017-03-22 04:00 | 51.02 | 34.92
2017-03-22 04:30 | 51.55 | 35.88
2017-03-22 05:00 | 51.96 | 36.57
2017-03-22 05:30 | 53.36 | 38.86
2017-03-22 06:00 | 55.47 | 42.16
2017-03-22 06:30 | 59.23 | 47.61
2017-03-22 07:00 | 55.54 | 53.74
2017-03-22 07:30 | 60.67 | 59.43
2017-03-22 08:00 | 64.48 | 63.23
2017-03-22 08:30 | 67.32 | 65.76
2017-03-22 09:00 | 69.07 | 67.64
2017-03-22 09:30 | 70.04 | 68.67
2017-03-22 10:00 | 69.69 | 69.19
2017-03-22 10:30 | 69.87 | 69.86
2017-03-22 11:00 | 71.72 | 71.37
2017-03-22 11:30 | 73.36 | 72.23
2017-03-22 12:00 | 74.09 | 72.99
2017-03-22 12:30 | 74.49 | 73.39
2017-03-22 13:00 | 74.93 | 73.84
2017-03-22 13:30 | 75.8 | 74.72
2017-03-22 14:00 | 77.16 | 76.12
2017-03-22 14:30 | 77.73 | 76.71
2017-03-22 15:00 | 78.51 | 77.51
2017-03-22 15:30 | 78.52 | 77.45
2017-03-22 16:00 | 77.42 | 76.27
2017-03-22 16:30 | 76.41 | 75.16
2017-03-22 17:00 | 74.88 | 73.5
2017-03-22 17:30 | 72.05 | 70.45
2017-03-22 18:00 | 70.03 | 68.24
2017-03-22 18:30 | 72.02 | 67.32
2017-03-22 19:00 | 73.89 | 68.41
2017-03-22 19:30 | 72.34 | 66.65
2017-03-22 20:00 | 70.62 | 64.69
2017-03-22 20:30 | 68.54 | 62.27
2017-03-22 21:00 | 66.51 | 59.89
2017-03-22 21:30 | 72.25 | 56.9
2017-03-22 22:00 | 75.13 | 53.84
2017-03-22 22:30 | 71.54 | 51.09
2017-03-22 23:00 | 69.57 | 49.77
2017-03-22 23:30 | 67.18 | 46.08
2017-03-23 | 65.51 | 43.29
2017-03-23 00:30 | 65.01 | 42.27
2017-03-23 01:00 | 64.18 | 40.85
2017-03-23 01:30 | 63.81 | 40.21
2017-03-23 02:00 | 63.48 | 39.58
2017-03-23 02:30 | 62.86 | 38.98
2017-03-23 03:00 | 62.14 | 38.38
2017-03-23 03:30 | 61.95 | 37.98
2017-03-23 04:00 | 62.1 | 38.26
2017-03-23 04:30 | 62.47 | 39.02
2017-03-23 05:00 | 63.12 | 40.28
2017-03-23 05:30 | 59.02 | 42.72
2017-03-23 06:00 | 58.83 | 46.03
2017-03-23 06:30 | 63.23 | 52.16
2017-03-23 07:00 | 62.25 | 57.82
2017-03-23 07:30 | 65.4 | 64.31
2017-03-23 08:00 | 68.97 | 67.86
2017-03-23 08:30 | 71.19 | 69.92
2017-03-23 09:00 | 72.33 | 70.94
2017-03-23 09:30 | 72.73 | 71.37
2017-03-23 10:00 | 71.83 | 70.43
2017-03-23 10:30 | 72.78 | 71.43
2017-03-23 11:00 | 72.89 | 71.54
2017-03-23 11:30 | 72.8 | 71.45
2017-03-23 12:00 | 72.59 | 71.23
2017-03-23 12:30 | 72.44 | 71.05
2017-03-23 13:00 | 70.57 | 69.13
2017-03-23 13:30 | 69.13 | 67.67
2017-03-23 14:00 | 69.29 | 67.85
2017-03-23 14:30 | 69.62 | 68.18
2017-03-23 15:00 | 69.88 | 68.41
2017-03-23 15:30 | 69.69 | 68.16
2017-03-23 16:00 | 69.43 | 67.84
2017-03-23 16:30 | 69.07 | 67.4
2017-03-23 17:00 | 68.65 | 65.74
2017-03-23 17:30 | 74.97 | 63.71
2017-03-23 18:00 | 74.51 | 62.9
2017-03-23 18:30 | 74.22 | 62.48
2017-03-23 19:00 | 73.6 | 61.62
2017-03-23 19:30 | 71.88 | 59.44
2017-03-23 20:00 | 69.43 | 57.44
2017-03-23 20:30 | 67.15 | 56.2
2017-03-23 21:00 | 66.18 | 54.86
2017-03-23 21:30 | 63.38 | 51.18
2017-03-23 22:00 | 61.25 | 48.24
2017-03-23 22:30 | 60.01 | 46.37
2017-03-23 23:00 | 59.78 | 46.01
2017-03-23 23:30 | 56.98 | 42.05
2017-03-24 | 55.4 | 39.58
2017-03-24 00:30 | 54.81 | 38.83
2017-03-24 01:00 | 53.11 | 37.14
2017-03-24 01:30 | 52.99 | 36.87
2017-03-24 02:00 | 52.42 | 36.01
2017-03-24 02:30 | 52.35 | 35.81
2017-03-24 03:00 | 52.09 | 35.36
2017-03-24 03:30 | 52.05 | 35.21
2017-03-24 04:00 | 52.15 | 35.42
2017-03-24 04:30 | 52.71 | 36.38
2017-03-24 05:00 | 53.4 | 37.51
2017-03-24 05:30 | 54.94 | 40.02
2017-03-24 06:00 | 56.94 | 43.13
2017-03-24 06:30 | 61.21 | 49.39
2017-03-24 07:00 | 67.51 | 54.95
2017-03-24 07:30 | 72.11 | 60.26
2017-03-24 08:00 | 75.37 | 64.56
2017-03-24 08:30 | 76.3 | 65.97
2017-03-24 09:00 | 76.53 | 66.43
2017-03-24 09:30 | 76.61 | 66.78
2017-03-24 10:00 | 76.78 | 67.14
2017-03-24 10:30 | 77.2 | 67.93
2017-03-24 11:00 | 79.29 | 70.52
2017-03-24 11:30 | 78.58 | 71.61
2017-03-24 12:00 | 77.34 | 73.38
2017-03-24 12:30 | 78.22 | 74.25
2017-03-24 13:00 | 77.73 | 73.41
2017-03-24 13:30 | 78.07 | 73.76
2017-03-24 14:00 | 78.45 | 74.12
2017-03-24 14:30 | 78.14 | 73.75
2017-03-24 15:00 | 77.75 | 73.31
2017-03-24 15:30 | 77.51 | 72.9
2017-03-24 16:00 | 77.66 | 72.87
2017-03-24 16:30 | 77.62 | 72.72
2017-03-24 17:00 | 75.57 | 70.28
2017-03-24 17:30 | 72.25 | 66.52
2017-03-24 18:00 | 69.76 | 63.79
2017-03-24 18:30 | 69.29 | 63.18
2017-03-24 19:00 | 70.04 | 64.03
2017-03-24 19:30 | 69.18 | 63.01
2017-03-24 20:00 | 67.71 | 61.28
2017-03-24 20:30 | 65.84 | 59.07
2017-03-24 21:00 | 68.25 | 56.7
2017-03-24 21:30 | 68.8 | 55.18
2017-03-24 22:00 | 66.96 | 52.57
2017-03-24 22:30 | 63.27 | 49.06
2017-03-24 23:00 | 59.33 | 47.87
2017-03-24 23:30 | 50.86 | 45.02
2017-03-25 | 48.8 | 42.54
2017-03-25 00:30 | 47.33 | 40.72
2017-03-25 01:00 | 46.14 | 39.25
2017-03-25 01:30 | 45.86 | 38.89
2017-03-25 02:00 | 45.2 | 38.07
2017-03-25 02:30 | 45.05 | 37.87
2017-03-25 03:00 | 44.41 | 37.03
2017-03-25 03:30 | 44.19 | 36.74
2017-03-25 04:00 | 44.13 | 36.66
2017-03-25 04:30 | 44.27 | 36.86
2017-03-25 05:00 | 44.49 | 37.15
2017-03-25 05:30 | 45.14 | 38.02
2017-03-25 06:00 | 45.8 | 38.89
2017-03-25 06:30 | 47.24 | 40.69
2017-03-25 07:00 | 48.8 | 42.6
2017-03-25 07:30 | 47.59 | 45.67
2017-03-25 08:00 | 50.53 | 49.19
2017-03-25 08:30 | 53.47 | 52.25
2017-03-25 09:00 | 55.89 | 54.49
2017-03-25 09:30 | 57.5 | 55.97
2017-03-25 10:00 | 57.47 | 56.5
2017-03-25 10:30 | 58.42 | 57.46
2017-03-25 11:00 | 57.73 | 56.74
2017-03-25 11:30 | 57.4 | 56.39
2017-03-25 12:00 | 55.58 | 54.56
2017-03-25 12:30 | 55.81 | 54.39
2017-03-25 13:00 | 54.83 | 52.94
2017-03-25 13:30 | 53.35 | 51.37
2017-03-25 14:00 | 53.54 | 51.53
2017-03-25 14:30 | 50.95 | 48.81
2017-03-25 15:00 | 53.41 | 51.37
2017-03-25 15:30 | 53.12 | 51.02
2017-03-25 16:00 | 53.82 | 51.74
2017-03-25 16:30 | 55.09 | 53.03
2017-03-25 17:00 | 54.45 | 52.31
2017-03-25 17:30 | 55.39 | 53.26
2017-03-25 18:00 | 56.46 | 54.35
2017-03-25 18:30 | 56.97 | 54.89
2017-03-25 19:00 | 58.61 | 56.65
2017-03-25 19:30 | 57.58 | 55.56
2017-03-25 20:00 | 53.62 | 51.54
2017-03-25 20:30 | 53.15 | 51.15
2017-03-25 21:00 | 51.12 | 49.72
2017-03-25 21:30 | 49.79 | 48.31
2017-03-25 22:00 | 48.26 | 46.69
2017-03-25 22:30 | 47.17 | 45.54
2017-03-25 23:00 | 46.96 | 45.3
2017-03-25 23:30 | 43.7 | 41.84
2017-03-26 | 41.64 | 39.63
2017-03-26 00:30 | 41.2 | 39.13
2017-03-26 01:00 | 39.8 | 37.63
2017-03-26 01:30 | 39.54 | 37.35
2017-03-26 02:00 | 38.81 | 36.55
2017-03-26 02:30 | 38.4 | 36.1
2017-03-26 03:00 | 38.07 | 35.75
2017-03-26 03:30 | 38.05 | 35.71
2017-03-26 04:00 | 37.77 | 35.4
2017-03-26 04:30 | 37.71 | 35.35
2017-03-26 05:00 | 37.77 | 35.42
2017-03-26 05:30 | 38.1 | 35.78
2017-03-26 06:00 | 38.8 | 36.56
2017-03-26 06:30 | 39.48 | 37.26
2017-03-26 07:00 | 40.55 | 38.41
2017-03-26 07:30 | 42.6 | 40.64
2017-03-26 08:00 | 44.33 | 42.49
2017-03-26 08:30 | 45.61 | 43.9
2017-03-26 09:00 | 48.33 | 46.79
2017-03-26 09:30 | 47.67 | 46.15
2017-03-26 10:00 | 50.07 | 48.68
2017-03-26 10:30 | 51.39 | 50.08
2017-03-26 11:00 | 52.27 | 51.01
2017-03-26 11:30 | 51.95 | 50.68
2017-03-26 12:00 | 49.12 | 47.77
2017-03-26 12:30 | 51.1 | 49.8
2017-03-26 13:00 | 51.39 | 50.11
2017-03-26 13:30 | 52.99 | 51.75
2017-03-26 14:00 | 53.38 | 52.14
2017-03-26 14:30 | 51.73 | 50.74
2017-03-26 15:00 | 50.5 | 50
2017-03-26 15:30 | 49.63 | 49.12
2017-03-26 16:00 | 51.57 | 51.1
2017-03-26 16:30 | 50.52 | 50.15
2017-03-26 17:00 | 49.05 | 48.75
2017-03-26 17:30 | 50.27 | 50.02
2017-03-26 18:00 | 51.89 | 51.64
2017-03-26 18:30 | 52.72 | 52.41
2017-03-26 19:00 | 53.03 | 52.72
2017-03-26 19:30 | 51.45 | 51.17
2017-03-26 20:00 | 49.55 | 49.3
2017-03-26 20:30 | 47.68 | 47.48
2017-03-26 21:00 | 46.15 | 45.98
2017-03-26 21:30 | 44.81 | 44.67
2017-03-26 22:00 | 43.39 | 43.29
2017-03-26 22:30 | 41.39 | 41.31
2017-03-26 23:00 | 41.93 | 41.86
2017-03-26 23:30 | 38.47 | 38.4
2017-03-27 | 37.18 | 37.12
2017-03-27 00:30 | 36.89 | 36.84
2017-03-27 01:00 | 35.5 | 35.45
2017-03-27 01:30 | 35.08 | 35.03
2017-03-27 02:00 | 34.94 | 34.9
2017-03-27 02:30 | 34.81 | 34.76
2017-03-27 03:00 | 34.33 | 34.28
2017-03-27 03:30 | 34.55 | 34.5
2017-03-27 04:00 | 34.9 | 34.85
2017-03-27 04:30 | 35.54 | 35.48
2017-03-27 05:00 | 37.04 | 36.97
2017-03-27 05:30 | 39.51 | 39.39
2017-03-27 06:00 | 43.04 | 42.75
2017-03-27 06:30 | 50.06 | 49.36
2017-03-27 07:00 | 56.02 | 55.35
2017-03-27 07:30 | 63.03 | 62.06
2017-03-27 08:00 | 68.15 | 67.28
2017-03-27 08:30 | 71.84 | 70.55
2017-03-27 09:00 | 76.75 | 72.82
2017-03-27 09:30 | 77.75 | 72.93
2017-03-27 10:00 | 78.04 | 73.21
2017-03-27 10:30 | 76.49 | 71.59
2017-03-27 11:00 | 74.75 | 69.74
2017-03-27 11:30 | 73.18 | 68.08
2017-03-27 12:00 | 72.41 | 68.07
2017-03-27 12:30 | 67.71 | 67.51
2017-03-27 13:00 | 61.75 | 59.89
2017-03-27 13:30 | 60.58 | 58.49
2017-03-27 14:00 | 57.31 | 54.96
2017-03-27 14:30 | 55.15 | 52.73
2017-03-27 15:00 | 53.27 | 50.82
2017-03-27 15:30 | 51.35 | 48.98
2017-03-27 16:00 | 51.35 | 48.97
2017-03-27 16:30 | 51.95 | 49.57
2017-03-27 17:00 | 51.22 | 48.76
2017-03-27 17:30 | 54.67 | 48.67
2017-03-27 18:00 | 57.03 | 50.02
2017-03-27 18:30 | 57.38 | 50.43
2017-03-27 19:00 | 57.25 | 50.25
2017-03-27 19:30 | 55.46 | 48.1
2017-03-27 20:00 | 54.37 | 46.75
2017-03-27 20:30 | 53.09 | 45.14
2017-03-27 21:00 | 52.33 | 44.18
2017-03-27 21:30 | 51.14 | 42.69
2017-03-27 22:00 | 49.54 | 40.73
2017-03-27 22:30 | 45.83 | 38.63
2017-03-27 23:00 | 46.1 | 38.93
2017-03-27 23:30 | 43.89 | 36.2
2017-03-28 | 42.59 | 34.54
2017-03-28 00:30 | 42.32 | 34.13
2017-03-28 01:00 | 41.32 | 32.84
2017-03-28 01:30 | 40.73 | 32.02
2017-03-28 02:00 | 39.84 | 30.81
2017-03-28 02:30 | 39.85 | 30.83
2017-03-28 03:00 | 39.75 | 30.68
2017-03-28 03:30 | 39.15 | 29.75
2017-03-28 04:00 | 39.41 | 30.15
2017-03-28 04:30 | 39.34 | 30.07
2017-03-28 05:00 | 39.56 | 30.4
2017-03-28 05:30 | 39.63 | 30.5
2017-03-28 06:00 | 39.09 | 30.68
2017-03-28 06:30 | 39.64 | 31.4
2017-03-28 07:00 | 41.37 | 33.75
2017-03-28 07:30 | 42.85 | 35.67
2017-03-28 08:00 | 41.88 | 34.5
2017-03-28 08:30 | 42.68 | 35.53
2017-03-28 09:00 | 43.76 | 36.86
2017-03-28 09:30 | 42.69 | 35.53
2017-03-28 10:00 | 41.01 | 33.37
2017-03-28 10:30 | 41.22 | 33.63
2017-03-28 11:00 | 41.16 | 33.55
2017-03-28 11:30 | 40.64 | 32.9
2017-03-28 12:00 | 40.34 | 32.49
2017-03-28 12:30 | 40.19 | 32.27
2017-03-28 13:00 | 37.47 | 28.67
2017-03-28 13:30 | 36.59 | 27.42
2017-03-28 14:00 | 35.66 | 26.06
2017-03-28 14:30 | 35.06 | 24.78
2017-03-28 15:00 | 34.99 | 24.79
2017-03-28 15:30 | 35.11 | 24.93
2017-03-28 16:00 | 35.38 | 25.34
2017-03-28 16:30 | 36.34 | 26.69
2017-03-28 17:00 | 37.5 | 28.34
2017-03-28 17:30 | 37.96 | 28.95
2017-03-28 18:00 | 38.63 | 29.87
2017-03-28 18:30 | 39.04 | 30.4
2017-03-28 19:00 | 39 | 30.34
2017-03-28 19:30 | 37.74 | 28.64
2017-03-28 20:00 | 37.24 | 27.9
2017-03-28 20:30 | 36.76 | 27.23
2017-03-28 21:00 | 36.25 | 26.47
2017-03-28 21:30 | 35.7 | 25.63
2017-03-28 22:00 | 35.31 | 25.03
2017-03-28 22:30 | 34.8 | 24.24
2017-03-28 23:00 | 35.2 | 24.81
2017-03-28 23:30 | 34 | 22.96
2017-03-29 | 33.26 | 21.72
2017-03-29 00:30 | 32.83 | 20.98
2017-03-29 01:00 | 32.41 | 20.28
2017-03-29 01:30 | 31.64 | 18.89
2017-03-29 02:00 | 31.38 | 18.4
2017-03-29 02:30 | 31 | 17.66
2017-03-29 03:00 | 30.86 | 17.33
2017-03-29 03:30 | 30.35 | 16.37
2017-03-29 04:00 | 30.15 | 15.89
2017-03-29 04:30 | 30.27 | 16.23
2017-03-29 05:00 | 30.3 | 16.38
2017-03-29 05:30 | 30.52 | 16.87
2017-03-29 06:00 | 30.91 | 17.67
2017-03-29 06:30 | 31.8 | 19.5
2017-03-29 07:00 | 32.6 | 21.05
2017-03-29 07:30 | 34.18 | 23.84
2017-03-29 08:00 | 35.84 | 26.45
2017-03-29 08:30 | 36.98 | 28.15
2017-03-29 09:00 | 37.63 | 29.15
2017-03-29 09:30 | 37.77 | 29.34
2017-03-29 10:00 | 38.09 | 29.81
2017-03-29 10:30 | 38.83 | 30.8
2017-03-29 11:00 | 38.44 | 30.28
2017-03-29 11:30 | 37.32 | 28.63
2017-03-29 12:00 | 36.64 | 27.61
2017-03-29 12:30 | 37 | 28.11
2017-03-29 13:00 | 37.16 | 28.34
2017-03-29 13:30 | 37.25 | 28.55
2017-03-29 14:00 | 36.83 | 27.96
2017-03-29 14:30 | 36.78 | 27.85
2017-03-29 15:00 | 35.77 | 26.43
2017-03-29 15:30 | 35.08 | 25.41
2017-03-29 16:00 | 35.37 | 25.84
2017-03-29 16:30 | 36.46 | 27.26
2017-03-29 17:00 | 36.48 | 27.23
2017-03-29 17:30 | 40.38 | 32.43
2017-03-29 18:00 | 40.42 | 32.51
2017-03-29 18:30 | 39.56 | 31.37
2017-03-29 19:00 | 36.94 | 27.62
2017-03-29 19:30 | 37.43 | 28.38
2017-03-29 20:00 | 38.66 | 30.06
2017-03-29 20:30 | 37.01 | 27.79
2017-03-29 21:00 | 36.45 | 27.04
2017-03-29 21:30 | 35.77 | 26.05
2017-03-29 22:00 | 35.25 | 25.2
2017-03-29 22:30 | 34.63 | 24.3
2017-03-29 23:00 | 34.39 | 23.92
2017-03-29 23:30 | 33.52 | 22.57
2017-03-30 | 33.14 | 21.91
2017-03-30 00:30 | 32.95 | 21.55
2017-03-30 01:00 | 32.57 | 20.88
2017-03-30 01:30 | 32.36 | 20.54
2017-03-30 02:00 | 32.05 | 19.96
2017-03-30 02:30 | 31.87 | 19.65
2017-03-30 03:00 | 31.83 | 19.58
2017-03-30 03:30 | 31.78 | 19.51
2017-03-30 04:00 | 31.88 | 19.7
2017-03-30 04:30 | 32.06 | 20.02
2017-03-30 05:00 | 32.34 | 20.54
2017-03-30 05:30 | 32.57 | 20.99
2017-03-30 06:00 | 33.53 | 22.66
2017-03-30 06:30 | 34.96 | 24.98
2017-03-30 07:00 | 36.76 | 27.77
2017-03-30 07:30 | 39.34 | 31.52
2017-03-30 08:00 | 42.48 | 35.8
2017-03-30 08:30 | 45.5 | 39.68
2017-03-30 09:00 | 46.15 | 43.04
2017-03-30 09:30 | 46.73 | 44.35
2017-03-30 10:00 | 47.39 | 44.93
2017-03-30 10:30 | 47.91 | 45.34
2017-03-30 11:00 | 48.86 | 46.21
2017-03-30 11:30 | 49.47 | 46.68
2017-03-30 12:00 | 49.39 | 46.51
2017-03-30 12:30 | 49.72 | 47.07
2017-03-30 13:00 | 48.8 | 47.19
2017-03-30 13:30 | 49.44 | 47.76
2017-03-30 14:00 | 49.71 | 48.03
2017-03-30 14:30 | 51.89 | 50.21
2017-03-30 15:00 | 53.3 | 51.54
2017-03-30 15:30 | 53.14 | 51.46
2017-03-30 16:00 | 52.62 | 51.05
2017-03-30 16:30 | 54.4 | 53.01
2017-03-30 17:00 | 53.54 | 52.38
2017-03-30 17:30 | 51.39 | 50.46
2017-03-30 18:00 | 48.82 | 48.2
2017-03-30 18:30 | 47.9 | 47.35
2017-03-30 19:00 | 50.06 | 49.48
2017-03-30 19:30 | 51.61 | 51.05
2017-03-30 20:00 | 51.27 | 50.75
2017-03-30 20:30 | 48.78 | 48.34
2017-03-30 21:00 | 47.67 | 47.28
2017-03-30 21:30 | 45.17 | 44.87
2017-03-30 22:00 | 40.67 | 40.49
2017-03-30 22:30 | 38.67 | 38.56
2017-03-30 23:00 | 38.06 | 37.89
2017-03-30 23:30 | 35.28 | 34.83
2017-03-31 | 32.84 | 32.44
2017-03-31 00:30 | 30.95 | 30.62
2017-03-31 01:00 | 29.58 | 29.3
2017-03-31 01:30 | 28.6 | 28.36
2017-03-31 02:00 | 28.89 | 27.72
2017-03-31 02:30 | 29.79 | 26.82
2017-03-31 03:00 | 29.43 | 26.42
2017-03-31 03:30 | 29.23 | 26.18
2017-03-31 04:00 | 29.09 | 26.01
2017-03-31 04:30 | 29.35 | 26.32
2017-03-31 05:00 | 29.54 | 26.55
2017-03-31 05:30 | 30.21 | 27.34
2017-03-31 06:00 | 31.59 | 28.96
2017-03-31 06:30 | 34.59 | 32.36
2017-03-31 07:00 | 37.55 | 35.67
2017-03-31 07:30 | 41.72 | 39.93
2017-03-31 08:00 | 44.92 | 42.86
2017-03-31 08:30 | 47.82 | 45.36
2017-03-31 09:00 | 50.3 | 47.62
2017-03-31 09:30 | 49.75 | 48.04
2017-03-31 10:00 | 49.98 | 48.21
2017-03-31 10:30 | 51.21 | 49.35
2017-03-31 11:00 | 52.74 | 50.77
2017-03-31 11:30 | 53.85 | 51.63
2017-03-31 12:00 | 53.82 | 51.57
2017-03-31 12:30 | 53.5 | 51.35
2017-03-31 13:00 | 54.89 | 52.68
2017-03-31 13:30 | 55.33 | 53.1
2017-03-31 14:00 | 55.05 | 52.85
2017-03-31 14:30 | 54.1 | 52.02
2017-03-31 15:00 | 53.92 | 51.93
2017-03-31 15:30 | 52.82 | 51.01
2017-03-31 16:00 | 52.99 | 51.38
2017-03-31 16:30 | 55.49 | 54.14
2017-03-31 17:00 | 54.82 | 53.65
2017-03-31 17:30 | 54.63 | 53.65
2017-03-31 18:00 | 53.49 | 52.57
2017-03-31 18:30 | 52.69 | 51.41
2017-03-31 19:00 | 53.89 | 52.59
2017-03-31 19:30 | 50.79 | 49.62
2017-03-31 20:00 | 47.86 | 46.81
2017-03-31 20:30 | 45.28 | 44.37
2017-03-31 21:00 | 42.94 | 42.15
2017-03-31 21:30 | 40.83 | 40.2
2017-03-31 22:00 | 39.13 | 38.61
2017-03-31 22:30 | 37.44 | 37.01
2017-03-31 23:00 | 39.09 | 38.7
2017-03-31 23:30 | 35.71 | 35.41
2017-04-01 | 33.37 | 33.13
2017-04-01 00:30 | 31.94 | 31.74
2017-04-01 01:00 | 30.05 | 29.89
2017-04-01 01:30 | 28.85 | 28.71
2017-04-01 02:00 | 28.07 | 27.95
2017-04-01 02:30 | 27.51 | 27.41
2017-04-01 03:00 | 27.18 | 27.09
2017-04-01 03:30 | 26.86 | 26.77
2017-04-01 04:00 | 26.49 | 26.44
2017-04-01 04:30 | 26.56 | 26.5
2017-04-01 05:00 | 26.81 | 26.74
2017-04-01 05:30 | 27.72 | 27.61
2017-04-01 06:00 | 28.57 | 28.44
2017-04-01 06:30 | 29.68 | 29.55
2017-04-01 07:00 | 30.76 | 30.62
2017-04-01 07:30 | 32.64 | 32.38
2017-04-01 08:00 | 34.56 | 34.16
2017-04-01 08:30 | 36.73 | 36.09
2017-04-01 09:00 | 38.74 | 37.82
2017-04-01 09:30 | 39.88 | 38.73
2017-04-01 10:00 | 39.91 | 39.06
2017-04-01 10:30 | 40.54 | 40.13
2017-04-01 11:00 | 40.56 | 40.24
2017-04-01 11:30 | 40.53 | 40.24
2017-04-01 12:00 | 41.36 | 41.09
2017-04-01 12:30 | 41.69 | 41.4
2017-04-01 13:00 | 41.66 | 41.37
2017-04-01 13:30 | 42.7 | 42.41
2017-04-01 14:00 | 43.18 | 42.88
2017-04-01 14:30 | 43.13 | 42.78
2017-04-01 15:00 | 43.52 | 43.18
2017-04-01 15:30 | 44.02 | 43.65
2017-04-01 16:00 | 45.34 | 44.96
2017-04-01 16:30 | 46.14 | 45.65
2017-04-01 17:00 | 45.88 | 45.25
2017-04-01 17:30 | 46.86 | 46.18
2017-04-01 18:00 | 47.5 | 46.75
2017-04-01 18:30 | 48.86 | 48.21
2017-04-01 19:00 | 49.65 | 49.09
2017-04-01 19:30 | 48.77 | 48.18
2017-04-01 20:00 | 47.11 | 46.45
2017-04-01 20:30 | 45.45 | 44.64
2017-04-01 21:00 | 44.15 | 43.23
2017-04-01 21:30 | 43.14 | 42.07
2017-04-01 22:00 | 41.93 | 40.66
2017-04-01 22:30 | 40.94 | 39.45
2017-04-01 23:00 | 41.31 | 39.71
2017-04-01 23:30 | 38.23 | 36.21
2017-04-02 | 34.73 | 34.13
2017-04-02 00:30 | 33.49 | 33.27
2017-04-02 01:00 | 32.22 | 32.01
2017-04-02 01:30 | 31.4 | 31.2
2017-04-02 02:00 | 30.87 | 30.7
2017-04-02 02:30 | 30.53 | 30.37
2017-04-02 03:00 | 30.08 | 29.93
2017-04-02 03:30 | 29.84 | 29.72
2017-04-02 04:00 | 29.52 | 29.4
2017-04-02 04:30 | 29.63 | 29.52
2017-04-02 05:00 | 29.63 | 29.51
2017-04-02 05:30 | 30.29 | 30.15
2017-04-02 06:00 | 30.7 | 30.54
2017-04-02 06:30 | 30.88 | 30.76
2017-04-02 07:00 | 31.91 | 31.78
2017-04-02 07:30 | 33.5 | 33.31
2017-04-02 08:00 | 35.15 | 34.9
2017-04-02 08:30 | 37.61 | 37.16
2017-04-02 09:00 | 39.77 | 38.55
2017-04-02 09:30 | 48 | 41.38
2017-04-02 10:00 | 49.86 | 43.46
2017-04-02 10:30 | 50.74 | 44.45
2017-04-02 11:00 | 50.47 | 44.07
2017-04-02 11:30 | 50.15 | 43.71
2017-04-02 12:00 | 50.08 | 43.65
2017-04-02 12:30 | 50.99 | 44.7
2017-04-02 13:00 | 49.57 | 43.09
2017-04-02 13:30 | 49.46 | 42.94
2017-04-02 14:00 | 49.12 | 42.53
2017-04-02 14:30 | 49.35 | 42.8
2017-04-02 15:00 | 50.51 | 44.11
2017-04-02 15:30 | 50.94 | 44.67
2017-04-02 16:00 | 51.13 | 44.89
2017-04-02 16:30 | 52.25 | 46.24
2017-04-02 17:00 | 52.66 | 46.71
2017-04-02 17:30 | 54.52 | 48.85
2017-04-02 18:00 | 56.25 | 50.8
2017-04-02 18:30 | 57.84 | 52.56
2017-04-02 19:00 | 59.44 | 54.31
2017-04-02 19:30 | 57.5 | 52.2
2017-04-02 20:00 | 55.51 | 49.97
2017-04-02 20:30 | 53.56 | 47.83
2017-04-02 21:00 | 52.29 | 46.41
2017-04-02 21:30 | 50.71 | 44.67
2017-04-02 22:00 | 48.97 | 42.74
2017-04-02 22:30 | 47.55 | 41.11
2017-04-02 23:00 | 47.51 | 41.12
2017-04-02 23:30 | 44.37 | 37.46
2017-04-03 | 43.05 | 35.89
2017-04-03 00:30 | 42.66 | 35.46
2017-04-03 01:00 | 41.39 | 33.92
2017-04-03 01:30 | 41 | 33.44
2017-04-03 02:00 | 40.88 | 33.33
2017-04-03 02:30 | 40.73 | 33.17
2017-04-03 03:00 | 40.59 | 32.94
2017-04-03 03:30 | 40.42 | 32.75
2017-04-03 04:00 | 40.46 | 32.81
2017-04-03 04:30 | 41.16 | 33.65
2017-04-03 05:00 | 42.04 | 34.65
2017-04-03 05:30 | 44.13 | 37.08
2017-04-03 06:00 | 47.04 | 40.28
2017-04-03 06:30 | 51.35 | 45.05
2017-04-03 07:00 | 55.77 | 49.95
2017-04-03 07:30 | 58.95 | 55.19
2017-04-03 08:00 | 59.98 | 58.52
2017-04-03 08:30 | 61.78 | 60.67
2017-04-03 09:00 | 63.14 | 62.21
2017-04-03 09:30 | 63.25 | 62.3
2017-04-03 10:00 | 62.19 | 61.23
2017-04-03 10:30 | 61.82 | 60.83
2017-04-03 11:00 | 61.52 | 60.48
2017-04-03 11:30 | 61.88 | 60.84
2017-04-03 12:00 | 62.02 | 60.98
2017-04-03 12:30 | 62.97 | 61.95
2017-04-03 13:00 | 63.32 | 62.32
2017-04-03 13:30 | 65.05 | 64.05
2017-04-03 14:00 | 65.03 | 64.02
2017-04-03 14:30 | 64.42 | 63.43
2017-04-03 15:00 | 64.35 | 63.37
2017-04-03 15:30 | 64.28 | 63.32
2017-04-03 16:00 | 64.44 | 63.52
2017-04-03 16:30 | 64.73 | 63.87
2017-04-03 17:00 | 63.46 | 62.64
2017-04-03 17:30 | 60.78 | 59.99
2017-04-03 18:00 | 59.6 | 58.64
2017-04-03 18:30 | 60.16 | 59.14
2017-04-03 19:00 | 60.56 | 59.48
2017-04-03 19:30 | 58.59 | 57.32
2017-04-03 20:00 | 56.88 | 55.06
2017-04-03 20:30 | 54.99 | 52.71
2017-04-03 21:00 | 52.58 | 50.12
2017-04-03 21:30 | 51.13 | 48.55
2017-04-03 22:00 | 49.04 | 46.2
2017-04-03 22:30 | 46.82 | 43.76
2017-04-03 23:00 | 45.11 | 43.28
2017-04-03 23:30 | 41.28 | 39.38
2017-04-04 | 39.18 | 37.13
2017-04-04 00:30 | 38.34 | 36.21
2017-04-04 01:00 | 37.11 | 34.88
2017-04-04 01:30 | 36.38 | 34.08
2017-04-04 02:00 | 36.23 | 33.9
2017-04-04 02:30 | 35.46 | 33.21
2017-04-04 03:00 | 34.93 | 32.79
2017-04-04 03:30 | 34.91 | 32.77
2017-04-04 04:00 | 35.39 | 33.29
2017-04-04 04:30 | 36 | 33.98
2017-04-04 05:00 | 36.68 | 34.72
2017-04-04 05:30 | 38.71 | 36.95
2017-04-04 06:00 | 41.25 | 39.68
2017-04-04 06:30 | 45.84 | 44.25
2017-04-04 07:00 | 50.93 | 49.21
2017-04-04 07:30 | 56.08 | 54.46
2017-04-04 08:00 | 58.52 | 56.89
2017-04-04 08:30 | 60.28 | 59.39
2017-04-04 09:00 | 61.09 | 60.17
2017-04-04 09:30 | 61.75 | 60.81
2017-04-04 10:00 | 62.34 | 61.38
2017-04-04 10:30 | 63.28 | 62.29
2017-04-04 11:00 | 63.72 | 62.73
2017-04-04 11:30 | 64.11 | 63.12
2017-04-04 12:00 | 64.54 | 63.54
2017-04-04 12:30 | 65.01 | 64.03
2017-04-04 13:00 | 65.38 | 64.39
2017-04-04 13:30 | 66.98 | 66.02
2017-04-04 14:00 | 66.91 | 65.95
2017-04-04 14:30 | 66.71 | 65.76
2017-04-04 15:00 | 66.56 | 65.61
2017-04-04 15:30 | 66.34 | 65.41
2017-04-04 16:00 | 66.82 | 65.93
2017-04-04 16:30 | 66.31 | 65.46
2017-04-04 17:00 | 65.74 | 64.93
2017-04-04 17:30 | 63.2 | 62.44
2017-04-04 18:00 | 63.05 | 62.26
2017-04-04 18:30 | 63.69 | 62.89
2017-04-04 19:00 | 63.3 | 62.45
2017-04-04 19:30 | 59.77 | 58.74
2017-04-04 20:00 | 58.14 | 57
2017-04-04 20:30 | 56.37 | 54.96
2017-04-04 21:00 | 54.69 | 53.01
2017-04-04 21:30 | 52.89 | 50.6
2017-04-04 22:00 | 49.6 | 48.01
2017-04-04 22:30 | 47.7 | 46.01
2017-04-04 23:00 | 47.42 | 45.69
2017-04-04 23:30 | 43.81 | 41.86
2017-04-05 | 41.2 | 39.3
2017-04-05 00:30 | 40.35 | 38.42
2017-04-05 01:00 | 38.56 | 36.47
2017-04-05 01:30 | 37.9 | 35.77
2017-04-05 02:00 | 37.55 | 35.4
2017-04-05 02:30 | 37.18 | 35.12
2017-04-05 03:00 | 36.37 | 34.43
2017-04-05 03:30 | 36.23 | 34.27
2017-04-05 04:00 | 36.33 | 34.37
2017-04-05 04:30 | 37.06 | 35.16
2017-04-05 05:00 | 37.63 | 35.76
2017-04-05 05:30 | 39.57 | 37.87
2017-04-05 06:00 | 43.01 | 41.46
2017-04-05 06:30 | 48.22 | 46.38
2017-04-05 07:00 | 51.6 | 49.83
2017-04-05 07:30 | 57.02 | 55.39
2017-04-05 08:00 | 59.72 | 58.41
2017-04-05 08:30 | 62.32 | 61.44
2017-04-05 09:00 | 60.5 | 59.56
2017-04-05 09:30 | 61.58 | 60.69
2017-04-05 10:00 | 60.18 | 59.26
2017-04-05 10:30 | 58.92 | 57.92
2017-04-05 11:00 | 59.83 | 58.82
2017-04-05 11:30 | 60.32 | 59.28
2017-04-05 12:00 | 62.33 | 61.32
2017-04-05 12:30 | 64.46 | 63.5
2017-04-05 13:00 | 62.11 | 61.14
2017-04-05 13:30 | 63.95 | 63.01
2017-04-05 14:00 | 64.1 | 63.17
2017-04-05 14:30 | 64 | 63.09
2017-04-05 15:00 | 63.7 | 62.8
2017-04-05 15:30 | 62.74 | 61.86
2017-04-05 16:00 | 61.28 | 60.44
2017-04-05 16:30 | 60.8 | 59.99
2017-04-05 17:00 | 59.63 | 58.82
2017-04-05 17:30 | 57.6 | 56.57
2017-04-05 18:00 | 56.37 | 54.73
2017-04-05 18:30 | 56.13 | 54.09
2017-04-05 19:00 | 55.2 | 53.45
2017-04-05 19:30 | 52.85 | 50.98
2017-04-05 20:00 | 51.28 | 49.31
2017-04-05 20:30 | 49.25 | 47.13
2017-04-05 21:00 | 47.56 | 45.32
2017-04-05 21:30 | 45.75 | 43.35
2017-04-05 22:00 | 44.03 | 41.46
2017-04-05 22:30 | 42.8 | 40.08
2017-04-05 23:00 | 41.5 | 39.63
2017-04-05 23:30 | 37.79 | 35.92
2017-04-06 | 36.09 | 34.09
2017-04-06 00:30 | 35.21 | 33.1
2017-04-06 01:00 | 33.89 | 31.67
2017-04-06 01:30 | 33.2 | 30.92
2017-04-06 02:00 | 32.85 | 30.54
2017-04-06 02:30 | 32.75 | 30.4
2017-04-06 03:00 | 32.38 | 29.98
2017-04-06 03:30 | 32.27 | 29.86
2017-04-06 04:00 | 32.34 | 29.95
2017-04-06 04:30 | 33.41 | 31.14
2017-04-06 05:00 | 34.29 | 32.11
2017-04-06 05:30 | 36.22 | 34.26
2017-04-06 06:00 | 38.82 | 37.1
2017-04-06 06:30 | 44.22 | 42.45
2017-04-06 07:00 | 48.28 | 46.46
2017-04-06 07:30 | 53.44 | 51.79
2017-04-06 08:00 | 56.17 | 55.17
2017-04-06 08:30 | 57.85 | 57.01
2017-04-06 09:00 | 58.61 | 57.74
2017-04-06 09:30 | 58.39 | 57.46
2017-04-06 10:00 | 59.21 | 58.27
2017-04-06 10:30 | 60.19 | 59.23
2017-04-06 11:00 | 59.59 | 58.59
2017-04-06 11:30 | 60.23 | 59.21
2017-04-06 12:00 | 61.62 | 60.62
2017-04-06 12:30 | 63.3 | 62.33
2017-04-06 13:00 | 62.34 | 61.36
2017-04-06 13:30 | 62.42 | 61.43
2017-04-06 14:00 | 62.74 | 61.75
2017-04-06 14:30 | 64.02 | 63.06
2017-04-06 15:00 | 64.53 | 63.62
2017-04-06 15:30 | 61.77 | 60.82
2017-04-06 16:00 | 62.49 | 61.6
2017-04-06 16:30 | 43.8 | 43.21
2017-04-06 17:00 | 57.35 | 56.64
2017-04-06 17:30 | 57.96 | 57.09
2017-04-06 18:00 | 58.12 | 57.15
2017-04-06 18:30 | 59.19 | 58.21
2017-04-06 19:00 | 59.05 | 57.99
2017-04-06 19:30 | 56.77 | 55.48
2017-04-06 20:00 | 54.61 | 53.16
2017-04-06 20:30 | 52.24 | 50.97
2017-04-06 21:00 | 50.55 | 49.25
2017-04-06 21:30 | 48.13 | 46.8
2017-04-06 22:00 | 45.35 | 43.99
2017-04-06 22:30 | 43.82 | 42.44
2017-04-06 23:00 | 43.74 | 42.38
2017-04-06 23:30 | 39.88 | 38.45
2017-04-07 | 37.55 | 36.03
2017-04-07 00:30 | 36.7 | 34.94
2017-04-07 01:00 | 35.19 | 33.38
2017-04-07 01:30 | 34.27 | 32.42
2017-04-07 02:00 | 33.58 | 31.7
2017-04-07 02:30 | 33.37 | 31.4
2017-04-07 03:00 | 33.45 | 31.32
2017-04-07 03:30 | 33.27 | 31.13
2017-04-07 04:00 | 33.52 | 31.38
2017-04-07 04:30 | 33.77 | 31.64
2017-04-07 05:00 | 34.93 | 32.84
2017-04-07 05:30 | 37.43 | 35.42
2017-04-07 06:00 | 40.32 | 38.37
2017-04-07 06:30 | 44.88 | 42.99
2017-04-07 07:00 | 48.71 | 47.09
2017-04-07 07:30 | 53.11 | 51.66
2017-04-07 08:00 | 40.05 | 38.1
2017-04-07 08:30 | 58.44 | 56.96
2017-04-07 09:00 | 59.75 | 58.2
2017-04-07 09:30 | 60.42 | 58.64
2017-04-07 10:00 | 59.97 | 58.06
2017-04-07 10:30 | 66.02 | 59.34
2017-04-07 11:00 | 70.78 | 58.92
2017-04-07 11:30 | 71.44 | 59.67
2017-04-07 12:00 | 72.45 | 60.83
2017-04-07 12:30 | 71.06 | 59.17
2017-04-07 13:00 | 72.08 | 60.42
2017-04-07 13:30 | 71.79 | 60.1
2017-04-07 14:00 | 72.28 | 60.66
2017-04-07 14:30 | 71.25 | 59.5
2017-04-07 15:00 | 69.94 | 58.07
2017-04-07 15:30 | 70.69 | 59.02
2017-04-07 16:00 | 70.13 | 58.52
2017-04-07 16:30 | 70.41 | 59.01
2017-04-07 17:00 | 68.44 | 56.81
2017-04-07 17:30 | 66.95 | 55.21
2017-04-07 18:00 | 65.8 | 53.97
2017-04-07 18:30 | 66.35 | 54.77
2017-04-07 19:00 | 66.28 | 54.71
2017-04-07 19:30 | 64.53 | 52.58
2017-04-07 20:00 | 63.29 | 51.06
2017-04-07 20:30 | 61.94 | 49.4
2017-04-07 21:00 | 54.65 | 47.54
2017-04-07 21:30 | 51.23 | 45.33
2017-04-07 22:00 | 49.53 | 43.45
2017-04-07 22:30 | 48.06 | 41.79
2017-04-07 23:00 | 47.9 | 41.71
2017-04-07 23:30 | 44.67 | 37.84
2017-04-08 | 43.27 | 35.97
2017-04-08 00:30 | 42.61 | 34.93
2017-04-08 01:00 | 41.23 | 33.06
2017-04-08 01:30 | 40.6 | 32.28
2017-04-08 02:00 | 40.25 | 31.9
2017-04-08 02:30 | 40.02 | 31.6
2017-04-08 03:00 | 39.69 | 31.15
2017-04-08 03:30 | 39.47 | 30.91
2017-04-08 04:00 | 39.38 | 30.79
2017-04-08 04:30 | 39.58 | 31.02
2017-04-08 05:00 | 40.07 | 31.63
2017-04-08 05:30 | 41.22 | 32.99
2017-04-08 06:00 | 42.08 | 33.99
2017-04-08 06:30 | 42.94 | 35.03
2017-04-08 07:00 | 44.47 | 36.86
2017-04-08 07:30 | 46.76 | 39.38
2017-04-08 08:00 | 48.76 | 41.6
2017-04-08 08:30 | 50.82 | 43.83
2017-04-08 09:00 | 51.69 | 44.75
2017-04-08 09:30 | 52.18 | 45.24
2017-04-08 10:00 | 51.83 | 44.84
2017-04-08 10:30 | 51.55 | 44.48
2017-04-08 11:00 | 51.23 | 44.07
2017-04-08 11:30 | 51.05 | 43.77
2017-04-08 12:00 | 50.36 | 43.04
2017-04-08 12:30 | 49.77 | 42.4
2017-04-08 13:00 | 49.3 | 41.86
2017-04-08 13:30 | 48.86 | 41.42
2017-04-08 14:00 | 48.59 | 41.13
2017-04-08 14:30 | 48.42 | 40.99
2017-04-08 15:00 | 48.66 | 41.3
2017-04-08 15:30 | 48.9 | 41.69
2017-04-08 16:00 | 49.93 | 42.94
2017-04-08 16:30 | 50.57 | 43.75
2017-04-08 17:00 | 50.8 | 44.04
2017-04-08 17:30 | 51.46 | 44.9
2017-04-08 18:00 | 52.64 | 46.24
2017-04-08 18:30 | 54.01 | 47.77
2017-04-08 19:00 | 54.42 | 48.27
2017-04-08 19:30 | 52.99 | 46.64
2017-04-08 20:00 | 51.9 | 45.38
2017-04-08 20:30 | 50.47 | 43.77
2017-04-08 21:00 | 49.38 | 42.55
2017-04-08 21:30 | 47.9 | 40.87
2017-04-08 22:00 | 46.94 | 39.74
2017-04-08 22:30 | 45.91 | 38.6
2017-04-08 23:00 | 46.38 | 39.17
2017-04-08 23:30 | 43.4 | 35.73
2017-04-09 | 41.9 | 33.91
2017-04-09 00:30 | 41.4 | 33.29
2017-04-09 01:00 | 40.17 | 31.76
2017-04-09 01:30 | 39.56 | 31.01
2017-04-09 02:00 | 39.1 | 30.43
2017-04-09 02:30 | 38.9 | 30.22
2017-04-09 03:00 | 38.76 | 30.05
2017-04-09 03:30 | 38.47 | 29.68
2017-04-09 04:00 | 38.52 | 29.75
2017-04-09 04:30 | 38.79 | 30.07
2017-04-09 05:00 | 38.92 | 30.2
2017-04-09 05:30 | 39.17 | 30.52
2017-04-09 06:00 | 39.52 | 30.96
2017-04-09 06:30 | 33.2 | 30.99
2017-04-09 07:00 | 33.72 | 31.65
2017-04-09 07:30 | 35.29 | 33.28
2017-04-09 08:00 | 37.34 | 35.35
2017-04-09 08:30 | 38.85 | 36.87
2017-04-09 09:00 | 39.91 | 37.93
2017-04-09 09:30 | 40.55 | 38.56
2017-04-09 10:00 | 40.92 | 38.91
2017-04-09 10:30 | 40.71 | 38.65
2017-04-09 11:00 | 40.84 | 38.74
2017-04-09 11:30 | 40.73 | 38.62
2017-04-09 12:00 | 40.97 | 38.88
2017-04-09 12:30 | 41.77 | 39.72
2017-04-09 13:00 | 41.23 | 39.14
2017-04-09 13:30 | 41.75 | 39.68
2017-04-09 14:00 | 42.26 | 40.22
2017-04-09 14:30 | 42.62 | 40.62
2017-04-09 15:00 | 43.28 | 41.32
2017-04-09 15:30 | 44.05 | 42.12
2017-04-09 16:00 | 44.82 | 42.97
2017-04-09 16:30 | 46.06 | 44.27
2017-04-09 17:00 | 46.38 | 44.63
2017-04-09 17:30 | 45.04 | 43.35
2017-04-09 18:00 | 49.01 | 47.39
2017-04-09 18:30 | 51.57 | 50.01
2017-04-09 19:00 | 52.64 | 51.09
2017-04-09 19:30 | 50.73 | 49.13
2017-04-09 20:00 | 49.27 | 47.62
2017-04-09 20:30 | 47.61 | 45.93
2017-04-09 21:00 | 46.07 | 44.35
2017-04-09 21:30 | 44.13 | 42.37
2017-04-09 22:00 | 42.37 | 40.55
2017-04-09 22:30 | 40.76 | 38.9
2017-04-09 23:00 | 40.82 | 39
2017-04-09 23:30 | 37.84 | 35.89
2017-04-10 | 36.31 | 34.29
2017-04-10 00:30 | 35.48 | 33.45
2017-04-10 01:00 | 34.54 | 32.45
2017-04-10 01:30 | 34.18 | 32.06
2017-04-10 02:00 | 34.1 | 31.98
2017-04-10 02:30 | 33.8 | 31.68
2017-04-10 03:00 | 33.41 | 31.26
2017-04-10 03:30 | 33.16 | 31.02
2017-04-10 04:00 | 33.05 | 30.9
2017-04-10 04:30 | 33.44 | 31.3
2017-04-10 05:00 | 34.45 | 32.34
2017-04-10 05:30 | 36.29 | 34.24
2017-04-10 06:00 | 39.39 | 37.42
2017-04-10 06:30 | 43.94 | 42.04
2017-04-10 07:00 | 47.42 | 45.56
2017-04-10 07:30 | 53.17 | 51.8
2017-04-10 08:00 | 56.08 | 55.12
2017-04-10 08:30 | 58.5 | 57.59
2017-04-10 09:00 | 60.14 | 59.2
2017-04-10 09:30 | 60.42 | 59.46
2017-04-10 10:00 | 60.58 | 59.61
2017-04-10 10:30 | 60.44 | 59.46
2017-04-10 11:00 | 61.07 | 60.07
2017-04-10 11:30 | 61.38 | 60.36
2017-04-10 12:00 | 61.71 | 60.68
2017-04-10 12:30 | 62.14 | 61.14
2017-04-10 13:00 | 62.79 | 61.8
2017-04-10 13:30 | 63.14 | 62.15
2017-04-10 14:00 | 62.97 | 61.97
2017-04-10 14:30 | 63.03 | 62.05
2017-04-10 15:00 | 63.36 | 62.39
2017-04-10 15:30 | 63.86 | 62.91
2017-04-10 16:00 | 63.75 | 62.84
2017-04-10 16:30 | 63.9 | 63.06
2017-04-10 17:00 | 62.76 | 61.94
2017-04-10 17:30 | 60.72 | 59.93
2017-04-10 18:00 | 59.47 | 58.55
2017-04-10 18:30 | 60.64 | 59.69
2017-04-10 19:00 | 61.02 | 60.04
2017-04-10 19:30 | 58.38 | 57.2
2017-04-10 20:00 | 56.14 | 54.69
2017-04-10 20:30 | 53.61 | 52.18
2017-04-10 21:00 | 51.17 | 49.88
2017-04-10 21:30 | 49.1 | 47.79
2017-04-10 22:00 | 46.97 | 45.62
2017-04-10 22:30 | 44.48 | 43.09
2017-04-10 23:00 | 44.54 | 43.16
2017-04-10 23:30 | 40.73 | 39.27
2017-04-11 | 38.31 | 36.8
2017-04-11 00:30 | 37.23 | 35.6
2017-04-11 01:00 | 35.83 | 34.02
2017-04-11 01:30 | 34.96 | 33.03
2017-04-11 02:00 | 34.67 | 32.57
2017-04-11 02:30 | 33.95 | 31.82
2017-04-11 03:00 | 33.39 | 31.24
2017-04-11 03:30 | 33.43 | 31.29
2017-04-11 04:00 | 33.82 | 31.69
2017-04-11 04:30 | 34.25 | 32.14
2017-04-11 05:00 | 34.75 | 32.67
2017-04-11 05:30 | 36.53 | 34.48
2017-04-11 06:00 | 38.92 | 36.94
2017-04-11 06:30 | 43.39 | 41.5
2017-04-11 07:00 | 47.24 | 45.43
2017-04-11 07:30 | 52.38 | 50.79
2017-04-11 08:00 | 54.7 | 53.23
2017-04-11 08:30 | 56.41 | 54.89
2017-04-11 09:00 | 57.49 | 55.92
2017-04-11 09:30 | 57.09 | 55.5
2017-04-11 10:00 | 56.65 | 55.01
2017-04-11 10:30 | 56.98 | 55.15
2017-04-11 11:00 | 57.95 | 55.87
2017-04-11 11:30 | 58.47 | 56.27
2017-04-11 12:00 | 59.05 | 56.8
2017-04-11 12:30 | 59.88 | 57.61
2017-04-11 13:00 | 59.61 | 57.39
2017-04-11 13:30 | 60.01 | 57.76
2017-04-11 14:00 | 60.67 | 58.33
2017-04-11 14:30 | 60.99 | 58.7
2017-04-11 15:00 | 61.19 | 59.03
2017-04-11 15:30 | 60.37 | 58.53
2017-04-11 16:00 | 59.75 | 58.17
2017-04-11 16:30 | 59.79 | 58.32
2017-04-11 17:00 | 58.34 | 56.93
2017-04-11 17:30 | 56.42 | 55.06
2017-04-11 18:00 | 54.92 | 53.61
2017-04-11 18:30 | 56.37 | 55.12
2017-04-11 19:00 | 56.32 | 55.08
2017-04-11 19:30 | 53.34 | 52.06
2017-04-11 20:00 | 51.19 | 49.89
2017-04-11 20:30 | 49.44 | 48.12
2017-04-11 21:00 | 47.47 | 46.14
2017-04-11 21:30 | 45.01 | 43.65
2017-04-11 22:00 | 42.68 | 41.29
2017-04-11 22:30 | 41.33 | 39.92
2017-04-11 23:00 | 41.32 | 39.93
2017-04-11 23:30 | 37.56 | 35.95
2017-04-12 | 35.38 | 33.59
2017-04-12 00:30 | 34.81 | 32.76
2017-04-12 01:00 | 33.29 | 31.16
2017-04-12 01:30 | 32.44 | 30.26
2017-04-12 02:00 | 32.3 | 30.11
2017-04-12 02:30 | 31.77 | 29.58
2017-04-12 03:00 | 31.35 | 29.14
2017-04-12 03:30 | 31.29 | 29.08
2017-04-12 04:00 | 31.59 | 29.39
2017-04-12 04:30 | 31.81 | 29.61
2017-04-12 05:00 | 32.49 | 30.32
2017-04-12 05:30 | 34.76 | 32.7
2017-04-12 06:00 | 37.45 | 35.43
2017-04-12 06:30 | 41.93 | 40.02
2017-04-12 07:00 | 45.3 | 43.43
2017-04-12 07:30 | 49.81 | 48.12
2017-04-12 08:00 | 51.89 | 50.24
2017-04-12 08:30 | 53.64 | 52.12
2017-04-12 09:00 | 55.15 | 53.59
2017-04-12 09:30 | 55.64 | 54.06
2017-04-12 10:00 | 55.79 | 54.17
2017-04-12 10:30 | 56.55 | 54.8
2017-04-12 11:00 | 57.95 | 55.87
2017-04-12 11:30 | 58.55 | 56.29
2017-04-12 12:00 | 59.31 | 56.91
2017-04-12 12:30 | 59.59 | 57.21
2017-04-12 13:00 | 59.44 | 57.16
2017-04-12 13:30 | 60.45 | 58.08
2017-04-12 14:00 | 61.67 | 59.27
2017-04-12 14:30 | 61.89 | 59.52
2017-04-12 15:00 | 62.49 | 60.13
2017-04-12 15:30 | 62.25 | 60.16
2017-04-12 16:00 | 61.7 | 59.92
2017-04-12 16:30 | 61.45 | 59.99
2017-04-12 17:00 | 59.68 | 58.26
2017-04-12 17:30 | 57.4 | 56.05
2017-04-12 18:00 | 56.3 | 55
2017-04-12 18:30 | 57.24 | 55.99
2017-04-12 19:00 | 57.15 | 55.91
2017-04-12 19:30 | 54.46 | 53.18
2017-04-12 20:00 | 52.33 | 51.02
2017-04-12 20:30 | 50.49 | 49.17
2017-04-12 21:00 | 48.69 | 47.35
2017-04-12 21:30 | 46.47 | 45.1
2017-04-12 22:00 | 43.97 | 42.46
2017-04-12 22:30 | 42.73 | 41.13
2017-04-12 23:00 | 42.64 | 41.05
2017-04-12 23:30 | 38.97 | 37.27
2017-04-13 | 36.87 | 35.11
2017-04-13 00:30 | 36.02 | 34.24
2017-04-13 01:00 | 34.48 | 32.63
2017-04-13 01:30 | 33.39 | 31.31
2017-04-13 02:00 | 33.12 | 30.95
2017-04-13 02:30 | 32.66 | 30.49
2017-04-13 03:00 | 32.3 | 30.11
2017-04-13 03:30 | 32.23 | 30.04
2017-04-13 04:00 | 32.35 | 30.17
2017-04-13 04:30 | 32.67 | 30.5
2017-04-13 05:00 | 33.98 | 31.87
2017-04-13 05:30 | 36.26 | 34.21
2017-04-13 06:00 | 39.21 | 37.22
2017-04-13 06:30 | 43.26 | 41.36
2017-04-13 07:00 | 46.63 | 44.76
2017-04-13 07:30 | 50.74 | 49.05
2017-04-13 08:00 | 53.73 | 52.24
2017-04-13 08:30 | 57.24 | 55.75
2017-04-13 09:00 | 58.67 | 57.13
2017-04-13 09:30 | 59.04 | 57.38
2017-04-13 10:00 | 60.11 | 58.67
2017-04-13 10:30 | 60.65 | 59.67
2017-04-13 11:00 | 60.79 | 59.79
2017-04-13 11:30 | 60.93 | 59.93
2017-04-13 12:00 | 60.59 | 59.57
2017-04-13 12:30 | 60.65 | 59.65
2017-04-13 13:00 | 60.09 | 59.08
2017-04-13 13:30 | 60.37 | 59.36
2017-04-13 14:00 | 60.69 | 59.7
2017-04-13 14:30 | 61.2 | 60.22
2017-04-13 15:00 | 61.74 | 60.78
2017-04-13 15:30 | 60.94 | 60.01
2017-04-13 16:00 | 60 | 59.11
2017-04-13 16:30 | 59.31 | 58.48
2017-04-13 17:00 | 57.84 | 57.01
2017-04-13 17:30 | 56.12 | 55.08
2017-04-13 18:00 | 55.32 | 54.01
2017-04-13 18:30 | 56.77 | 55.47
2017-04-13 19:00 | 56.77 | 55.37
2017-04-13 19:30 | 54.52 | 52.86
2017-04-13 20:00 | 53.33 | 51.48
2017-04-13 20:30 | 51.89 | 49.72
2017-04-13 21:00 | 50.64 | 48.16
2017-04-13 21:30 | 48.42 | 45.41
2017-04-13 22:00 | 50.09 | 42.24
2017-04-13 22:30 | 48.85 | 40.95
2017-04-13 23:00 | 48.82 | 41.07
2017-04-13 23:30 | 45.92 | 37.37
2017-04-14 | 44.27 | 35.15
2017-04-14 00:30 | 41.63 | 33.48
2017-04-14 01:00 | 39.35 | 31.58
2017-04-14 01:30 | 38.79 | 30.84
2017-04-14 02:00 | 38.39 | 30.31
2017-04-14 02:30 | 37.97 | 29.72
2017-04-14 03:00 | 37.77 | 29.46
2017-04-14 03:30 | 37.58 | 29.19
2017-04-14 04:00 | 37.55 | 29.16
2017-04-14 04:30 | 37.54 | 29.13
2017-04-14 05:00 | 37.77 | 29.46
2017-04-14 05:30 | 38.08 | 29.89
2017-04-14 06:00 | 38.5 | 30.48
2017-04-14 06:30 | 39.22 | 31.42
2017-04-14 07:00 | 39.81 | 32.2
2017-04-14 07:30 | 37.22 | 34.3
2017-04-14 08:00 | 34.42 | 33.89
2017-04-14 08:30 | 36.81 | 36.19
2017-04-14 09:00 | 37.54 | 36.75
2017-04-14 09:30 | 37.69 | 36.79
2017-04-14 10:00 | 37.62 | 36.63
2017-04-14 10:30 | 39.02 | 38
2017-04-14 11:00 | 38.27 | 37.28
2017-04-14 11:30 | 37.85 | 36.75
2017-04-14 12:00 | 37.14 | 36
2017-04-14 12:30 | 37.07 | 35.96
2017-04-14 13:00 | 37.03 | 35.88
2017-04-14 13:30 | 37.1 | 35.96
2017-04-14 14:00 | 37.07 | 35.98
2017-04-14 14:30 | 37.72 | 36.63
2017-04-14 15:00 | 38.24 | 37.15
2017-04-14 15:30 | 39.09 | 38.04
2017-04-14 16:00 | 40.28 | 39.36
2017-04-14 16:30 | 43.33 | 42.51
2017-04-14 17:00 | 42.75 | 41.98
2017-04-14 17:30 | 42.99 | 42.33
2017-04-14 18:00 | 43.59 | 43.01
2017-04-14 18:30 | 45.53 | 44.89
2017-04-14 19:00 | 45.83 | 45.22
2017-04-14 19:30 | 43.96 | 43.4
2017-04-14 20:00 | 42.41 | 41.87
2017-04-14 20:30 | 40.86 | 40.39
2017-04-14 21:00 | 39.63 | 39.2
2017-04-14 21:30 | 38.29 | 37.91
2017-04-14 22:00 | 36.85 | 36.54
2017-04-14 22:30 | 36.26 | 35.99
2017-04-14 23:00 | 36.31 | 36.08
2017-04-14 23:30 | 33.24 | 33.05
2017-04-15 | 31.65 | 31.51
2017-04-15 00:30 | 31.43 | 31.31
2017-04-15 01:00 | 30.1 | 29.99
2017-04-15 01:30 | 29.41 | 29.3
2017-04-15 02:00 | 29.11 | 28.99
2017-04-15 02:30 | 28.62 | 28.52
2017-04-15 03:00 | 28.41 | 28.31
2017-04-15 03:30 | 27.5 | 27.39
2017-04-15 04:00 | 26.97 | 26.86
2017-04-15 04:30 | 28.32 | 28.22
2017-04-15 05:00 | 28.42 | 28.32
2017-04-15 05:30 | 28.87 | 28.76
2017-04-15 06:00 | 29.61 | 29.49
2017-04-15 06:30 | 30.11 | 30.01
2017-04-15 07:00 | 31.37 | 31.26
2017-04-15 07:30 | 32.93 | 32.74
2017-04-15 08:00 | 34.67 | 34.36
2017-04-15 08:30 | 36.67 | 36.17
2017-04-15 09:00 | 38.11 | 37.4
2017-04-15 09:30 | 38.3 | 37.43
2017-04-15 10:00 | 38.6 | 37.59
2017-04-15 10:30 | 38.91 | 37.74
2017-04-15 11:00 | 38.78 | 37.52
2017-04-15 11:30 | 38.89 | 37.56
2017-04-15 12:00 | 39.15 | 37.8
2017-04-15 12:30 | 39.44 | 38.16
2017-04-15 13:00 | 38.98 | 37.65
2017-04-15 13:30 | 38.68 | 37.36
2017-04-15 14:00 | 38.85 | 37.65
2017-04-15 14:30 | 39.19 | 38.06
2017-04-15 15:00 | 39.76 | 38.67
2017-04-15 15:30 | 40.68 | 39.67
2017-04-15 16:00 | 42.25 | 41.38
2017-04-15 16:30 | 43.6 | 42.92
2017-04-15 17:00 | 41.89 | 41.35
2017-04-15 17:30 | 42.15 | 41.63
2017-04-15 18:00 | 43.19 | 42.67
2017-04-15 18:30 | 44.39 | 43.78
2017-04-15 19:00 | 44.63 | 44.01
2017-04-15 19:30 | 43.1 | 42.5
2017-04-15 20:00 | 41.81 | 41.25
2017-04-15 20:30 | 40.33 | 39.82
2017-04-15 21:00 | 39.24 | 38.75
2017-04-15 21:30 | 37.81 | 37.39
2017-04-15 22:00 | 36.77 | 36.41
2017-04-15 22:30 | 36.13 | 35.82
2017-04-15 23:00 | 36.32 | 36.05
2017-04-15 23:30 | 33.35 | 33.13
2017-04-16 | 31.85 | 31.69
2017-04-16 00:30 | 31.18 | 31.06
2017-04-16 01:00 | 29.75 | 29.63
2017-04-16 01:30 | 29.25 | 29.14
2017-04-16 02:00 | 28.92 | 28.81
2017-04-16 02:30 | 28.69 | 28.58
2017-04-16 03:00 | 28.62 | 28.51
2017-04-16 03:30 | 28.29 | 28.18
2017-04-16 04:00 | 28.35 | 28.25
2017-04-16 04:30 | 28.13 | 28.03
2017-04-16 05:00 | 28.28 | 28.17
2017-04-16 05:30 | 28.33 | 28.22
2017-04-16 06:00 | 29.01 | 28.9
2017-04-16 06:30 | 29.15 | 29.06
2017-04-16 07:00 | 29.77 | 29.68
2017-04-16 07:30 | 31.16 | 31.04
2017-04-16 08:00 | 32.98 | 32.78
2017-04-16 08:30 | 34.12 | 33.81
2017-04-16 09:00 | 35.59 | 35.09
2017-04-16 09:30 | 36.25 | 35.64
2017-04-16 10:00 | 36.24 | 35.54
2017-04-16 10:30 | 38.11 | 37.36
2017-04-16 11:00 | 37.52 | 36.74
2017-04-16 11:30 | 36.18 | 35.28
2017-04-16 12:00 | 37.38 | 36.5
2017-04-16 12:30 | 36.68 | 35.78
2017-04-16 13:00 | 36.04 | 35.11
2017-04-16 13:30 | 36.59 | 35.65
2017-04-16 14:00 | 37.58 | 36.67
2017-04-16 14:30 | 39.65 | 38.98
2017-04-16 15:00 | 38.9 | 38.25
2017-04-16 15:30 | 37.71 | 37.08
2017-04-16 16:00 | 38.2 | 37.53
2017-04-16 16:30 | 39.51 | 38.96
2017-04-16 17:00 | 39.57 | 39.07
2017-04-16 17:30 | 40.33 | 39.89
2017-04-16 18:00 | 41.64 | 41.2
2017-04-16 18:30 | 43.81 | 43.29
2017-04-16 19:00 | 44.05 | 43.52
2017-04-16 19:30 | 42.44 | 41.93
2017-04-16 20:00 | 41.4 | 40.93
2017-04-16 20:30 | 39.91 | 39.51
2017-04-16 21:00 | 39.04 | 38.65
2017-04-16 21:30 | 37.3 | 36.97
2017-04-16 22:00 | 36.01 | 35.74
2017-04-16 22:30 | 35.18 | 34.95
2017-04-16 23:00 | 35.39 | 35.2
2017-04-16 23:30 | 32.49 | 32.34
2017-04-17 | 30.68 | 30.58
2017-04-17 00:30 | 30.15 | 30.05
2017-04-17 01:00 | 28.91 | 28.81
2017-04-17 01:30 | 28.23 | 28.13
2017-04-17 02:00 | 28.31 | 28.21
2017-04-17 02:30 | 28.2 | 28.12
2017-04-17 03:00 | 27.86 | 27.77
2017-04-17 03:30 | 27.79 | 27.69
2017-04-17 04:00 | 27.95 | 27.86
2017-04-17 04:30 | 28.05 | 27.95
2017-04-17 05:00 | 28.33 | 28.22
2017-04-17 05:30 | 28.75 | 28.64
2017-04-17 06:00 | 29.71 | 29.57
2017-04-17 06:30 | 31.16 | 31
2017-04-17 07:00 | 32.04 | 31.88
2017-04-17 07:30 | 34.47 | 34.21
2017-04-17 08:00 | 36.24 | 35.91
2017-04-17 08:30 | 37.66 | 37.19
2017-04-17 09:00 | 39.86 | 39.32
2017-04-17 09:30 | 41.13 | 40.57
2017-04-17 10:00 | 40.6 | 39.96
2017-04-17 10:30 | 40.48 | 39.68
2017-04-17 11:00 | 39.83 | 38.83
2017-04-17 11:30 | 42.07 | 40.99
2017-04-17 12:00 | 42.05 | 41.02
2017-04-17 12:30 | 41.89 | 40.85
2017-04-17 13:00 | 40.34 | 39.12
2017-04-17 13:30 | 41.56 | 40.49
2017-04-17 14:00 | 40.48 | 39.38
2017-04-17 14:30 | 42.92 | 41.98
2017-04-17 15:00 | 42.25 | 41.44
2017-04-17 15:30 | 41.45 | 40.62
2017-04-17 16:00 | 42.85 | 42.1
2017-04-17 16:30 | 44.98 | 44.3
2017-04-17 17:00 | 44.92 | 44.27
2017-04-17 17:30 | 45.64 | 45.06
2017-04-17 18:00 | 47.07 | 46.47
2017-04-17 18:30 | 49.22 | 48.6
2017-04-17 19:00 | 47.82 | 47.27
2017-04-17 19:30 | 45.16 | 44.66
2017-04-17 20:00 | 43.44 | 43
2017-04-17 20:30 | 41.68 | 41.29
2017-04-17 21:00 | 40.03 | 39.66
2017-04-17 21:30 | 38.51 | 38.18
2017-04-17 22:00 | 37.05 | 36.77
2017-04-17 22:30 | 35.57 | 35.34
2017-04-17 23:00 | 36 | 35.78
2017-04-17 23:30 | 33.11 | 32.92
2017-04-18 | 31.54 | 31.39
2017-04-18 00:30 | 30.77 | 30.65
2017-04-18 01:00 | 29.52 | 29.41
2017-04-18 01:30 | 29.23 | 29.12
2017-04-18 02:00 | 29.17 | 29.06
2017-04-18 02:30 | 29.13 | 29.02
2017-04-18 03:00 | 29.06 | 28.95
2017-04-18 03:30 | 29.13 | 29.02
2017-04-18 04:00 | 29.18 | 29.07
2017-04-18 04:30 | 29.71 | 29.59
2017-04-18 05:00 | 31.14 | 30.98
2017-04-18 05:30 | 33.67 | 33.38
2017-04-18 06:00 | 36.41 | 35.93
2017-04-18 06:30 | 41.32 | 40.5
2017-04-18 07:00 | 46.36 | 45.19
2017-04-18 07:30 | 51.95 | 50.91
2017-04-18 08:00 | 55.09 | 53.11
2017-04-18 08:30 | 60.36 | 54.49
2017-04-18 09:00 | 60.89 | 55.11
2017-04-18 09:30 | 61.07 | 55.26
2017-04-18 10:00 | 60.94 | 55.07
2017-04-18 10:30 | 62.07 | 56.21
2017-04-18 11:00 | 61.97 | 56.11
2017-04-18 11:30 | 62.79 | 56.96
2017-04-18 12:00 | 63 | 57.17
2017-04-18 12:30 | 63.58 | 58.37
2017-04-18 13:00 | 62.96 | 58.34
2017-04-18 13:30 | 64.07 | 59.52
2017-04-18 14:00 | 64.41 | 59.88
2017-04-18 14:30 | 64.66 | 60.16
2017-04-18 15:00 | 64.52 | 60.07
2017-04-18 15:30 | 64.15 | 59.73
2017-04-18 16:00 | 64.14 | 59.84
2017-04-18 16:30 | 64.36 | 60.18
2017-04-18 17:00 | 62.7 | 58.52
2017-04-18 17:30 | 56.96 | 56.15
2017-04-18 18:00 | 56.81 | 55.64
2017-04-18 18:30 | 58.37 | 57.19
2017-04-18 19:00 | 58.16 | 56.87
2017-04-18 19:30 | 55.55 | 53.97
2017-04-18 20:00 | 53.59 | 51.71
2017-04-18 20:30 | 51.57 | 49.32
2017-04-18 21:00 | 49.89 | 47.28
2017-04-18 21:30 | 47.29 | 45.07
2017-04-18 22:00 | 42.62 | 42.6
2017-04-18 22:30 | 41.12 | 41.03
2017-04-18 23:00 | 40.94 | 40.86
2017-04-18 23:30 | 37.4 | 37.34
2017-04-19 | 35.42 | 35.37
2017-04-19 00:30 | 34.29 | 34.25
2017-04-19 01:00 | 32.98 | 32.87
2017-04-19 01:30 | 32.56 | 32.25
2017-04-19 02:00 | 32.22 | 31.94
2017-04-19 02:30 | 31.45 | 31.21
2017-04-19 03:00 | 31.15 | 30.93
2017-04-19 03:30 | 31.09 | 30.87
2017-04-19 04:00 | 30.94 | 30.74
2017-04-19 04:30 | 32.03 | 31.78
2017-04-19 05:00 | 33 | 32.71
2017-04-19 05:30 | 35.66 | 35.22
2017-04-19 06:00 | 38.91 | 38.23
2017-04-19 06:30 | 44.31 | 43.21
2017-04-19 07:00 | 49.66 | 48.74
2017-04-19 07:30 | 57.85 | 54.78
2017-04-19 08:00 | 60.71 | 57.26
2017-04-19 08:30 | 58.31 | 58.13
2017-04-19 09:00 | 59.05 | 59
2017-04-19 09:30 | 59.16 | 59.14
2017-04-19 10:00 | 58.85 | 58.83
2017-04-19 10:30 | 59.67 | 59.66
2017-04-19 11:00 | 59.37 | 59.35
2017-04-19 11:30 | 59.1 | 59.07
2017-04-19 12:00 | 59.23 | 59.2
2017-04-19 12:30 | 59.94 | 59.92
2017-04-19 13:00 | 60.88 | 60.86
2017-04-19 13:30 | 59.98 | 59.96
2017-04-19 14:00 | 60.4 | 60.37
2017-04-19 14:30 | 60.12 | 60.1
2017-04-19 15:00 | 60.22 | 60.2
2017-04-19 15:30 | 59.62 | 59.6
2017-04-19 16:00 | 59.84 | 59.79
2017-04-19 16:30 | 59.94 | 59.79
2017-04-19 17:00 | 58.72 | 58.38
2017-04-19 17:30 | 57.43 | 56.69
2017-04-19 18:00 | 57.48 | 56.46
2017-04-19 18:30 | 59.09 | 58.08
2017-04-19 19:00 | 58.72 | 57.56
2017-04-19 19:30 | 55.99 | 54.56
2017-04-19 20:00 | 53.69 | 51.93
2017-04-19 20:30 | 51.6 | 49.47
2017-04-19 21:00 | 49.77 | 47.18
2017-04-19 21:30 | 48.48 | 45.48
2017-04-19 22:00 | 43.43 | 43.08
2017-04-19 22:30 | 41.16 | 41.13
2017-04-19 23:00 | 41.04 | 41.01
2017-04-19 23:30 | 37.45 | 37.37
2017-04-20 | 35.51 | 35.44
2017-04-20 00:30 | 34.27 | 34.23
2017-04-20 01:00 | 32.88 | 32.84
2017-04-20 01:30 | 31.88 | 31.85
2017-04-20 02:00 | 31.56 | 31.53
2017-04-20 02:30 | 31.32 | 31.09
2017-04-20 03:00 | 31.16 | 30.94
2017-04-20 03:30 | 30.92 | 30.71
2017-04-20 04:00 | 31.57 | 31.36
2017-04-20 04:30 | 32.18 | 31.94
2017-04-20 05:00 | 33.02 | 32.72
2017-04-20 05:30 | 35.39 | 34.97
2017-04-20 06:00 | 38.89 | 38.22
2017-04-20 06:30 | 44.18 | 43.1
2017-04-20 07:00 | 49.02 | 47.93
2017-04-20 07:30 | 54.28 | 53.52
2017-04-20 08:00 | 56.96 | 56.25
2017-04-20 08:30 | 58.26 | 57.24
2017-04-20 09:00 | 61.92 | 58.37
2017-04-20 09:30 | 64.36 | 58.84
2017-04-20 10:00 | 63.92 | 58.34
2017-04-20 10:30 | 63.29 | 57.55
2017-04-20 11:00 | 62.96 | 57.19
2017-04-20 11:30 | 64.05 | 58.28
2017-04-20 12:00 | 64.28 | 58.54
2017-04-20 12:30 | 67.95 | 62.64
2017-04-20 13:00 | 66.61 | 61.26
2017-04-20 13:30 | 65.72 | 60.25
2017-04-20 14:00 | 65.36 | 59.86
2017-04-20 14:30 | 65.28 | 59.76
2017-04-20 15:00 | 65.02 | 59.51
2017-04-20 15:30 | 64.58 | 59.12
2017-04-20 16:00 | 64.35 | 58.94
2017-04-20 16:30 | 63.48 | 58.11
2017-04-20 17:00 | 62.83 | 57.47
2017-04-20 17:30 | 60.96 | 55.62
2017-04-20 18:00 | 61.42 | 56.21
2017-04-20 18:30 | 63.37 | 58.4
2017-04-20 19:00 | 62.47 | 57.44
2017-04-20 19:30 | 59.89 | 54.7
2017-04-20 20:00 | 57.58 | 52.2
2017-04-20 20:30 | 56.2 | 50.73
2017-04-20 21:00 | 54.58 | 48.97
2017-04-20 21:30 | 51.58 | 45.72
2017-04-20 22:00 | 48.52 | 42.3
2017-04-20 22:30 | 46.95 | 40.54
2017-04-20 23:00 | 43.71 | 40.37
2017-04-20 23:30 | 36.48 | 36.41
2017-04-21 | 34.58 | 34.53
2017-04-21 00:30 | 33.45 | 33.42
2017-04-21 01:00 | 31.96 | 31.93
2017-04-21 01:30 | 31.33 | 31.31
2017-04-21 02:00 | 31 | 30.83
2017-04-21 02:30 | 30.55 | 30.38
2017-04-21 03:00 | 30.26 | 30.08
2017-04-21 03:30 | 30.47 | 30.3
2017-04-21 04:00 | 30.63 | 30.46
2017-04-21 04:30 | 31.6 | 31.37
2017-04-21 05:00 | 31.01 | 30.65
2017-04-21 05:30 | 35.4 | 34.93
2017-04-21 06:00 | 38.48 | 37.8
2017-04-21 06:30 | 43 | 41.98
2017-04-21 07:00 | 47.8 | 46.63
2017-04-21 07:30 | 52.28 | 51.91
2017-04-21 08:00 | 54.82 | 54.23
2017-04-21 08:30 | 56.06 | 55.75
2017-04-21 09:00 | 57.91 | 57.73
2017-04-21 09:30 | 58.25 | 58.12
2017-04-21 10:00 | 57.25 | 57.16
2017-04-21 10:30 | 59.66 | 59.61
2017-04-21 11:00 | 59.06 | 59.03
2017-04-21 11:30 | 57.35 | 57.32
2017-04-21 12:00 | 57.79 | 57.77
2017-04-21 12:30 | 58.91 | 58.89
2017-04-21 13:00 | 58.35 | 58.3
2017-04-21 13:30 | 59.65 | 59.61
2017-04-21 14:00 | 57.77 | 57.68
2017-04-21 14:30 | 56.76 | 56.63
2017-04-21 15:00 | 55.41 | 55.27
2017-04-21 15:30 | 54.85 | 54.63
2017-04-21 16:00 | 54.64 | 54.26
2017-04-21 16:30 | 55.39 | 54.76
2017-04-21 17:00 | 54.06 | 53.24
2017-04-21 17:30 | 54.12 | 52.97
2017-04-21 18:00 | 54 | 52.54
2017-04-21 18:30 | 54.69 | 53.18
2017-04-21 19:00 | 54.46 | 52.8
2017-04-21 19:30 | 52.48 | 50.44
2017-04-21 20:00 | 51.11 | 48.79
2017-04-21 20:30 | 49.51 | 46.8
2017-04-21 21:00 | 47.5 | 44.54
2017-04-21 21:30 | 42.27 | 42.11
2017-04-21 22:00 | 40.77 | 40.57
2017-04-21 22:30 | 39.99 | 39.48
2017-04-21 23:00 | 39.82 | 39.39
2017-04-21 23:30 | 36.7 | 36.34
2017-04-22 | 34.54 | 34.26
2017-04-22 00:30 | 33.94 | 33.68
2017-04-22 01:00 | 32.29 | 32.07
2017-04-22 01:30 | 31.14 | 30.96
2017-04-22 02:00 | 31.04 | 30.86
2017-04-22 02:30 | 30.57 | 30.41
2017-04-22 03:00 | 30.06 | 29.93
2017-04-22 03:30 | 29.79 | 29.66
2017-04-22 04:00 | 30.15 | 30.02
2017-04-22 04:30 | 30.22 | 30.07
2017-04-22 05:00 | 30.88 | 30.71
2017-04-22 05:30 | 32.07 | 31.83
2017-04-22 06:00 | 33.07 | 32.78
2017-04-22 06:30 | 35.11 | 34.72
2017-04-22 07:00 | 36.71 | 36.31
2017-04-22 07:30 | 39.68 | 39.11
2017-04-22 08:00 | 42.55 | 41.82
2017-04-22 08:30 | 43.62 | 42.86
2017-04-22 09:00 | 44.96 | 44.41
2017-04-22 09:30 | 43.65 | 43.18
2017-04-22 10:00 | 44.52 | 44.23
2017-04-22 10:30 | 43.92 | 43.7
2017-04-22 11:00 | 45.61 | 45.47
2017-04-22 11:30 | 46.05 | 45.88
2017-04-22 12:00 | 43.55 | 43.36
2017-04-22 12:30 | 42.23 | 41.97
2017-04-22 13:00 | 43.3 | 43.02
2017-04-22 13:30 | 42.34 | 41.99
2017-04-22 14:00 | 41.84 | 41.44
2017-04-22 14:30 | 42.52 | 42.02
2017-04-22 15:00 | 41.44 | 40.88
2017-04-22 15:30 | 42.03 | 41.45
2017-04-22 16:00 | 43.31 | 42.7
2017-04-22 16:30 | 44.61 | 43.93
2017-04-22 17:00 | 44.68 | 43.79
2017-04-22 17:30 | 45.1 | 44.11
2017-04-22 18:00 | 46.94 | 46.09
2017-04-22 18:30 | 49.62 | 48.93
2017-04-22 19:00 | 48.93 | 48.18
2017-04-22 19:30 | 46.8 | 45.96
2017-04-22 20:00 | 45.4 | 44.46
2017-04-22 20:30 | 43.86 | 42.74
2017-04-22 21:00 | 42.72 | 41.45
2017-04-22 21:30 | 40.41 | 39.89
2017-04-22 22:00 | 39.06 | 38.65
2017-04-22 22:30 | 37.61 | 37.25
2017-04-22 23:00 | 36.61 | 36.32
2017-04-22 23:30 | 34.99 | 34.73
2017-04-23 | 34.54 | 34.31
2017-04-23 00:30 | 32.93 | 32.76
2017-04-23 01:00 | 31.19 | 31.04
2017-04-23 01:30 | 30.54 | 30.4
2017-04-23 02:00 | 30.06 | 29.94
2017-04-23 02:30 | 29.64 | 29.52
2017-04-23 03:00 | 29.47 | 29.36
2017-04-23 03:30 | 29.24 | 29.14
2017-04-23 04:00 | 29.13 | 29.02
2017-04-23 04:30 | 29.49 | 29.38
2017-04-23 05:00 | 29.57 | 29.46
2017-04-23 05:30 | 30.04 | 29.91
2017-04-23 06:00 | 30.96 | 30.8
2017-04-23 06:30 | 31.82 | 31.67
2017-04-23 07:00 | 31.97 | 31.85
2017-04-23 07:30 | 34.57 | 34.39
2017-04-23 08:00 | 36.29 | 36.08
2017-04-23 08:30 | 38.88 | 38.55
2017-04-23 09:00 | 40.89 | 40.46
2017-04-23 09:30 | 41.95 | 41.47
2017-04-23 10:00 | 43.24 | 42.7
2017-04-23 10:30 | 41.19 | 40.49
2017-04-23 11:00 | 41.07 | 40.14
2017-04-23 11:30 | 44.82 | 43.95
2017-04-23 12:00 | 43.6 | 42.81
2017-04-23 12:30 | 40.94 | 40.1
2017-04-23 13:00 | 40.79 | 39.91
2017-04-23 13:30 | 41.11 | 40.25
2017-04-23 14:00 | 42.08 | 41.23
2017-04-23 14:30 | 40.47 | 39.65
2017-04-23 15:00 | 40.46 | 39.65
2017-04-23 15:30 | 41.18 | 40.42
2017-04-23 16:00 | 41.44 | 40.76
2017-04-23 16:30 | 42.64 | 42.02
2017-04-23 17:00 | 43.16 | 42.58
2017-04-23 17:30 | 44.49 | 43.96
2017-04-23 18:00 | 46.54 | 46
2017-04-23 18:30 | 49.74 | 49.06
2017-04-23 19:00 | 49.02 | 48.37
2017-04-23 19:30 | 46.63 | 46.02
2017-04-23 20:00 | 44.76 | 44.21
2017-04-23 20:30 | 42.97 | 42.49
2017-04-23 21:00 | 41.46 | 41
2017-04-23 21:30 | 39.63 | 39.22
2017-04-23 22:00 | 37.99 | 37.65
2017-04-23 22:30 | 36.93 | 36.64
2017-04-23 23:00 | 37.39 | 37.13
2017-04-23 23:30 | 33.8 | 33.6
2017-04-24 | 32.34 | 32.17
2017-04-24 00:30 | 32.01 | 31.86
2017-04-24 01:00 | 30.46 | 30.33
2017-04-24 01:30 | 30.02 | 29.88
2017-04-24 02:00 | 29.74 | 29.62
2017-04-24 02:30 | 29.37 | 29.26
2017-04-24 03:00 | 29.33 | 29.23
2017-04-24 03:30 | 29.64 | 29.53
2017-04-24 04:00 | 29.54 | 29.43
2017-04-24 04:30 | 30.19 | 30.05
2017-04-24 05:00 | 31.18 | 31.01
2017-04-24 05:30 | 33.91 | 33.6
2017-04-24 06:00 | 37.58 | 37.05
2017-04-24 06:30 | 42.59 | 41.75
2017-04-24 07:00 | 47.35 | 46.14
2017-04-24 07:30 | 53.43 | 52.01
2017-04-24 08:00 | 54.93 | 54.64
2017-04-24 08:30 | 55.4 | 55.28
2017-04-24 09:00 | 56.57 | 56.54
2017-04-24 09:30 | 57.17 | 57.03
2017-04-24 10:00 | 57.54 | 57.37
2017-04-24 10:30 | 58.59 | 58.49
2017-04-24 11:00 | 57.99 | 57.95
2017-04-24 11:30 | 57.44 | 57.42
2017-04-24 12:00 | 58.67 | 58.66
2017-04-24 12:30 | 59.04 | 59.01
2017-04-24 13:00 | 58.32 | 58.28
2017-04-24 13:30 | 58.2 | 58.18
2017-04-24 14:00 | 59.32 | 59.3
2017-04-24 14:30 | 59.14 | 59.09
2017-04-24 15:00 | 58.52 | 58.45
2017-04-24 15:30 | 58.14 | 58.02
2017-04-24 16:00 | 57.46 | 57.23
2017-04-24 16:30 | 56.74 | 56.33
2017-04-24 17:00 | 56.01 | 55.43
2017-04-24 17:30 | 55.02 | 53.98
2017-04-24 18:00 | 54.96 | 53.5
2017-04-24 18:30 | 54.73 | 54.52
2017-04-24 19:00 | 53.97 | 53.72
2017-04-24 19:30 | 51.1 | 50.75
2017-04-24 20:00 | 49.19 | 48.72
2017-04-24 20:30 | 47.34 | 46.76
2017-04-24 21:00 | 45.61 | 44.88
2017-04-24 21:30 | 43.42 | 42.7
2017-04-24 22:00 | 41.57 | 40.95
2017-04-24 22:30 | 39.5 | 38.99
2017-04-24 23:00 | 39.55 | 39.12
2017-04-24 23:30 | 35.63 | 35.3
2017-04-25 | 33.27 | 33.03
2017-04-25 00:30 | 31.82 | 31.64
2017-04-25 01:00 | 30.33 | 30.18
2017-04-25 01:30 | 29.54 | 29.39
2017-04-25 02:00 | 29.23 | 29.1
2017-04-25 02:30 | 28.57 | 28.46
2017-04-25 03:00 | 28.34 | 28.24
2017-04-25 03:30 | 28.24 | 28.14
2017-04-25 04:00 | 28.52 | 28.42
2017-04-25 04:30 | 28.97 | 28.86
2017-04-25 05:00 | 29.07 | 28.96
2017-04-25 05:30 | 29.33 | 29.22
2017-04-25 06:00 | 30.58 | 30.41
2017-04-25 06:30 | 31.6 | 31.46
2017-04-25 07:00 | 32.78 | 32.63
2017-04-25 07:30 | 34.13 | 33.92
2017-04-25 08:00 | 34.71 | 34.38
2017-04-25 08:30 | 35.32 | 34.84
2017-04-25 09:00 | 35.92 | 35.25
2017-04-25 09:30 | 36.79 | 36.04
2017-04-25 10:00 | 37.01 | 36.12
2017-04-25 10:30 | 37.11 | 36.11
2017-04-25 11:00 | 37.51 | 36.44
2017-04-25 11:30 | 37.35 | 36.18
2017-04-25 12:00 | 37.59 | 36.4
2017-04-25 12:30 | 37.96 | 36.75
2017-04-25 13:00 | 37.62 | 36.42
2017-04-25 13:30 | 37.48 | 36.24
2017-04-25 14:00 | 37.89 | 36.6
2017-04-25 14:30 | 38.22 | 36.98
2017-04-25 15:00 | 38.82 | 37.65
2017-04-25 15:30 | 39.61 | 38.5
2017-04-25 16:00 | 40.62 | 39.63
2017-04-25 16:30 | 42.96 | 42.05
2017-04-25 17:00 | 43.34 | 42.56
2017-04-25 17:30 | 44.79 | 44.07
2017-04-25 18:00 | 47.37 | 46.62
2017-04-25 18:30 | 50.34 | 49.54
2017-04-25 19:00 | 50.19 | 49.42
2017-04-25 19:30 | 47.07 | 46.4
2017-04-25 20:00 | 45.24 | 44.58
2017-04-25 20:30 | 43.72 | 43.11
2017-04-25 21:00 | 41.94 | 41.36
2017-04-25 21:30 | 40.08 | 39.55
2017-04-25 22:00 | 38.06 | 37.66
2017-04-25 22:30 | 36.6 | 36.28
2017-04-25 23:00 | 37.1 | 36.82
2017-04-25 23:30 | 33.2 | 33
2017-04-26 | 31.93 | 31.73
2017-04-26 00:30 | 31.27 | 31.11
2017-04-26 01:00 | 30.13 | 29.97
2017-04-26 01:30 | 29.81 | 29.68
2017-04-26 02:00 | 29.39 | 29.27
2017-04-26 02:30 | 28.77 | 28.66
2017-04-26 03:00 | 29.12 | 29
2017-04-26 03:30 | 29.25 | 29.13
2017-04-26 04:00 | 28.91 | 28.8
2017-04-26 04:30 | 29.45 | 29.33
2017-04-26 05:00 | 30.76 | 30.58
2017-04-26 05:30 | 33.6 | 33.26
2017-04-26 06:00 | 37.04 | 36.48
2017-04-26 06:30 | 42.46 | 41.52
2017-04-26 07:00 | 47.67 | 46.06
2017-04-26 07:30 | 56.74 | 50.76
2017-04-26 08:00 | 57.85 | 53.14
2017-04-26 08:30 | 58.04 | 53.9
2017-04-26 09:00 | 55.16 | 54.93
2017-04-26 09:30 | 55.7 | 55.6
2017-04-26 10:00 | 56.17 | 56.13
2017-04-26 10:30 | 56.64 | 56.62
2017-04-26 11:00 | 57.37 | 57.36
2017-04-26 11:30 | 57.78 | 57.75
2017-04-26 12:00 | 58.75 | 58.72
2017-04-26 12:30 | 59.62 | 59.58
2017-04-26 13:00 | 59.78 | 59.75
2017-04-26 13:30 | 59.61 | 59.57
2017-04-26 14:00 | 61.16 | 61.12
2017-04-26 14:30 | 61.5 | 61.45
2017-04-26 15:00 | 60.99 | 60.96
2017-04-26 15:30 | 61.58 | 61.55
2017-04-26 16:00 | 61.07 | 61.05
2017-04-26 16:30 | 60.82 | 60.74
2017-04-26 17:00 | 59.91 | 59.69
2017-04-26 17:30 | 58.04 | 57.52
2017-04-26 18:00 | 58.32 | 57.48
2017-04-26 18:30 | 58.9 | 58.86
2017-04-26 19:00 | 57.29 | 57.22
2017-04-26 19:30 | 54.19 | 54.06
2017-04-26 20:00 | 52.02 | 51.81
2017-04-26 20:30 | 49.47 | 49.1
2017-04-26 21:00 | 47.73 | 47.08
2017-04-26 21:30 | 45.31 | 44.46
2017-04-26 22:00 | 43.18 | 42.41
2017-04-26 22:30 | 40.67 | 40.06
2017-04-26 23:00 | 40.59 | 40.05
2017-04-26 23:30 | 37.27 | 36.78
2017-04-27 | 35 | 34.56
2017-04-27 00:30 | 33.45 | 33.15
2017-04-27 01:00 | 31.94 | 31.7
2017-04-27 01:30 | 31.46 | 31.24
2017-04-27 02:00 | 30.98 | 30.78
2017-04-27 02:30 | 30.51 | 30.33
2017-04-27 03:00 | 29.37 | 29.24
2017-04-27 03:30 | 30.37 | 30.2
2017-04-27 04:00 | 30.5 | 30.3
2017-04-27 04:30 | 31.27 | 31.04
2017-04-27 05:00 | 32.43 | 32.16
2017-04-27 05:30 | 35.04 | 34.6
2017-04-27 06:00 | 38.24 | 37.61
2017-04-27 06:30 | 43.16 | 42.16
2017-04-27 07:00 | 50.16 | 46.88
2017-04-27 07:30 | 57.7 | 51.89
2017-04-27 08:00 | 59.84 | 54.36
2017-04-27 08:30 | 61.51 | 56
2017-04-27 09:00 | 62.52 | 56.97
2017-04-27 09:30 | 62.72 | 57.15
2017-04-27 10:00 | 63.52 | 57.96
2017-04-27 10:30 | 64.3 | 58.78
2017-04-27 11:00 | 65.21 | 59.68
2017-04-27 11:30 | 64.16 | 58.53
2017-04-27 12:00 | 64.73 | 59.13
2017-04-27 12:30 | 65.16 | 59.57
2017-04-27 13:00 | 65.46 | 59.96
2017-04-27 13:30 | 65.18 | 59.66
2017-04-27 14:00 | 65.29 | 59.76
2017-04-27 14:30 | 65.48 | 60.02
2017-04-27 15:00 | 64.15 | 58.6
2017-04-27 15:30 | 63.89 | 58.36
2017-04-27 16:00 | 64.05 | 59.46
2017-04-27 16:30 | 62.95 | 58.75
2017-04-27 17:00 | 60.84 | 56.87
2017-04-27 17:30 | 55.91 | 55
2017-04-27 18:00 | 56.01 | 54.85
2017-04-27 18:30 | 57.89 | 56.61
2017-04-27 19:00 | 57.43 | 56.01
2017-04-27 19:30 | 54.65 | 52.86
2017-04-27 20:00 | 52.89 | 51.35
2017-04-27 20:30 | 49.49 | 48.98
2017-04-27 21:00 | 47.4 | 46.74
2017-04-27 21:30 | 43.83 | 43.11
2017-04-27 22:00 | 40.88 | 40.32
2017-04-27 22:30 | 39.33 | 38.86
2017-04-27 23:00 | 39.29 | 38.86
2017-04-27 23:30 | 35.29 | 34.95
2017-04-28 | 33.35 | 33.05
2017-04-28 00:30 | 31.81 | 31.61
2017-04-28 01:00 | 30.38 | 30.2
2017-04-28 01:30 | 29.46 | 29.31
2017-04-28 02:00 | 28.75 | 28.63
2017-04-28 02:30 | 28.32 | 28.2
2017-04-28 03:00 | 28.05 | 27.94
2017-04-28 03:30 | 28.1 | 27.99
2017-04-28 04:00 | 28.12 | 28.01
2017-04-28 04:30 | 28.99 | 28.86
2017-04-28 05:00 | 30.59 | 30.4
2017-04-28 05:30 | 33 | 32.7
2017-04-28 06:00 | 35.86 | 35.41
2017-04-28 06:30 | 40.11 | 39.45
2017-04-28 07:00 | 44.81 | 43.84
2017-04-28 07:30 | 48.39 | 48.16
2017-04-28 08:00 | 49.45 | 49.25
2017-04-28 08:30 | 48.91 | 48.54
2017-04-28 09:00 | 48.65 | 48.05
2017-04-28 09:30 | 47.32 | 46.7
2017-04-28 10:00 | 46.26 | 45.53
2017-04-28 10:30 | 46.65 | 45.23
2017-04-28 11:00 | 47.29 | 45.56
2017-04-28 11:30 | 47.49 | 45.75
2017-04-28 12:00 | 47.41 | 45.66
2017-04-28 12:30 | 48.15 | 46.41
2017-04-28 13:00 | 47.96 | 46.22
2017-04-28 13:30 | 47.8 | 46.06
2017-04-28 14:00 | 48.13 | 46.43
2017-04-28 14:30 | 48.26 | 46.56
2017-04-28 15:00 | 48.36 | 46.69
2017-04-28 15:30 | 48.29 | 46.67
2017-04-28 16:00 | 48.65 | 47.1
2017-04-28 16:30 | 49.81 | 48.36
2017-04-28 17:00 | 49.5 | 48.08
2017-04-28 17:30 | 48.91 | 47.56
2017-04-28 18:00 | 49.13 | 47.84
2017-04-28 18:30 | 50.06 | 48.75
2017-04-28 19:00 | 49.11 | 47.69
2017-04-28 19:30 | 46.94 | 45.48
2017-04-28 20:00 | 45.58 | 44.09
2017-04-28 20:30 | 43.4 | 41.78
2017-04-28 21:00 | 41.93 | 40.15
2017-04-28 21:30 | 39.92 | 38.08
2017-04-28 22:00 | 38.16 | 36.26
2017-04-28 22:30 | 37.17 | 35.26
2017-04-28 23:00 | 37.7 | 35.84
2017-04-28 23:30 | 34.06 | 32.04
2017-04-29 | 32.34 | 30.25
2017-04-29 00:30 | 31.47 | 29.34
2017-04-29 01:00 | 29.95 | 27.73
2017-04-29 01:30 | 29.56 | 27.29
2017-04-29 02:00 | 29.13 | 26.85
2017-04-29 02:30 | 28.11 | 26.47
2017-04-29 03:00 | 26.27 | 26.24
2017-04-29 03:30 | 28.18 | 26.21
2017-04-29 04:00 | 28.61 | 26.32
2017-04-29 04:30 | 28.84 | 26.55
2017-04-29 05:00 | 29.37 | 27.11
2017-04-29 05:30 | 30.59 | 28.4
2017-04-29 06:00 | 31.4 | 29.24
2017-04-29 06:30 | 33.1 | 31.05
2017-04-29 07:00 | 34.96 | 33
2017-04-29 07:30 | 36.92 | 35.02
2017-04-29 08:00 | 36.71 | 34.74
2017-04-29 08:30 | 38.34 | 36.42
2017-04-29 09:00 | 38.49 | 36.55
2017-04-29 09:30 | 38.15 | 36.15
2017-04-29 10:00 | 38.18 | 36.13
2017-04-29 10:30 | 38.24 | 36.13
2017-04-29 11:00 | 37.82 | 35.63
2017-04-29 11:30 | 37.88 | 35.68
2017-04-29 12:00 | 37.69 | 35.47
2017-04-29 12:30 | 36.99 | 34.75
2017-04-29 13:00 | 36.82 | 34.59
2017-04-29 13:30 | 36.62 | 34.38
2017-04-29 14:00 | 36.34 | 34.1
2017-04-29 14:30 | 35.69 | 33.45
2017-04-29 15:00 | 36.88 | 34.69
2017-04-29 15:30 | 37.4 | 35.28
2017-04-29 16:00 | 38.49 | 36.46
2017-04-29 16:30 | 40.62 | 38.73
2017-04-29 17:00 | 40.68 | 38.83
2017-04-29 17:30 | 42.35 | 40.58
2017-04-29 18:00 | 43.71 | 42
2017-04-29 18:30 | 45.18 | 43.5
2017-04-29 19:00 | 44.64 | 42.94
2017-04-29 19:30 | 42.83 | 41.06
2017-04-29 20:00 | 41.62 | 39.81
2017-04-29 20:30 | 40.06 | 38.21
2017-04-29 21:00 | 39.13 | 37.25
2017-04-29 21:30 | 37.7 | 35.77
2017-04-29 22:00 | 36.94 | 34.99
2017-04-29 22:30 | 35.88 | 33.9
2017-04-29 23:00 | 36.27 | 34.34
2017-04-29 23:30 | 33.46 | 31.38
2017-04-30 | 31.92 | 29.78
2017-04-30 00:30 | 31.14 | 28.98
2017-04-30 01:00 | 30.67 | 28.45
2017-04-30 01:30 | 29.48 | 27.21
2017-04-30 02:00 | 29.47 | 27.2
2017-04-30 02:30 | 29.09 | 26.79
2017-04-30 03:00 | 28.96 | 26.65
2017-04-30 03:30 | 28.88 | 26.57
2017-04-30 04:00 | 28.8 | 26.49
2017-04-30 04:30 | 28.87 | 26.55
2017-04-30 05:00 | 29.06 | 26.75
2017-04-30 05:30 | 29.53 | 27.25
2017-04-30 06:00 | 30.07 | 27.81
2017-04-30 06:30 | 31.39 | 29.22
2017-04-30 07:00 | 31.97 | 29.87
2017-04-30 07:30 | 33.71 | 31.71
2017-04-30 08:00 | 35.57 | 33.64
2017-04-30 08:30 | 36.71 | 34.78
2017-04-30 09:00 | 38.53 | 36.65
2017-04-30 09:30 | 39.5 | 37.62
2017-04-30 10:00 | 39.68 | 37.77
2017-04-30 10:30 | 38.49 | 36.47
2017-04-30 11:00 | 38.03 | 35.94
2017-04-30 11:30 | 37.62 | 35.49
2017-04-30 12:00 | 36.96 | 34.78
2017-04-30 12:30 | 36.79 | 34.62
2017-04-30 13:00 | 36.49 | 34.29
2017-04-30 13:30 | 36.61 | 34.44
2017-04-30 14:00 | 37.02 | 34.85
2017-04-30 14:30 | 36.91 | 34.77
2017-04-30 15:00 | 36.8 | 34.68
2017-04-30 15:30 | 37.74 | 35.7
2017-04-30 16:00 | 39.16 | 37.2
2017-04-30 16:30 | 40.39 | 38.52
2017-04-30 17:00 | 40.2 | 38.37
2017-04-30 17:30 | 41.82 | 40.06
2017-04-30 18:00 | 43.42 | 41.72
2017-04-30 18:30 | 45.81 | 44.19
2017-04-30 19:00 | 45.14 | 43.5
2017-04-30 19:30 | 43.09 | 41.36
2017-04-30 20:00 | 41.61 | 39.83
2017-04-30 20:30 | 39.69 | 37.86
2017-04-30 21:00 | 38.3 | 36.42
2017-04-30 21:30 | 37.18 | 35.26
2017-04-30 22:00 | 37 | 35.09
2017-04-30 22:30 | 36.5 | 34.58
2017-04-30 23:00 | 36.29 | 34.39
2017-04-30 23:30 | 33.22 | 31.17
2017-05-01 | 32.07 | 29.96
2017-05-01 00:30 | 31.36 | 29.21
2017-05-01 01:00 | 30.14 | 27.9
2017-05-01 01:30 | 29.61 | 27.34
2017-05-01 02:00 | 29.27 | 26.98
2017-05-01 02:30 | 28.9 | 26.59
2017-05-01 03:00 | 28.55 | 26.21
2017-05-01 03:30 | 28.42 | 26.09
2017-05-01 04:00 | 28.61 | 26.28
2017-05-01 04:30 | 28.78 | 26.47
2017-05-01 05:00 | 28.99 | 26.68
2017-05-01 05:30 | 29.6 | 27.32
2017-05-01 06:00 | 30.22 | 27.96
2017-05-01 06:30 | 31.27 | 29.1
2017-05-01 07:00 | 32.09 | 29.99
2017-05-01 07:30 | 33.1 | 31.02
2017-05-01 08:00 | 34.81 | 32.82
2017-05-01 08:30 | 36.77 | 34.83
2017-05-01 09:00 | 37.34 | 35.39
2017-05-01 09:30 | 38.76 | 36.84
2017-05-01 10:00 | 38.71 | 36.76
2017-05-01 10:30 | 40.22 | 38.32
2017-05-01 11:00 | 40.31 | 38.38
2017-05-01 11:30 | 40.67 | 38.73
2017-05-01 12:00 | 41.04 | 39.1
2017-05-01 12:30 | 41.15 | 39.21
2017-05-01 13:00 | 41.14 | 39.21
2017-05-01 13:30 | 40.9 | 38.98
2017-05-01 14:00 | 41.82 | 39.94
2017-05-01 14:30 | 40.69 | 38.77
2017-05-01 15:00 | 40.03 | 38.09
2017-05-01 15:30 | 40.29 | 38.37
2017-05-01 16:00 | 40.92 | 39.04
2017-05-01 16:30 | 43 | 41.22
2017-05-01 17:00 | 43.54 | 41.8
2017-05-01 17:30 | 45.2 | 43.53
2017-05-01 18:00 | 47.63 | 46.04
2017-05-01 18:30 | 49.76 | 48.21
2017-05-01 19:00 | 48.76 | 47.2
2017-05-01 19:30 | 45.98 | 44.34
2017-05-01 20:00 | 44.59 | 42.9
2017-05-01 20:30 | 42.72 | 40.98
2017-05-01 21:00 | 41.09 | 39.3
2017-05-01 21:30 | 39.32 | 37.48
2017-05-01 22:00 | 37.67 | 35.77
2017-05-01 22:30 | 36.28 | 34.34
2017-05-01 23:00 | 36.67 | 34.77
2017-05-01 23:30 | 33.7 | 31.65
2017-05-02 | 32.23 | 30.1
2017-05-02 00:30 | 31.74 | 29.59
2017-05-02 01:00 | 30.65 | 28.44
2017-05-02 01:30 | 30.22 | 27.97
2017-05-02 02:00 | 30.07 | 27.81
2017-05-02 02:30 | 29.99 | 27.73
2017-05-02 03:00 | 29.63 | 27.35
2017-05-02 03:30 | 29.67 | 27.39
2017-05-02 04:00 | 29.62 | 27.34
2017-05-02 04:30 | 30.38 | 28.15
2017-05-02 05:00 | 31.43 | 29.25
2017-05-02 05:30 | 34.11 | 32.04
2017-05-02 06:00 | 37.35 | 35.36
2017-05-02 06:30 | 41.54 | 39.68
2017-05-02 07:00 | 46.14 | 44.36
2017-05-02 07:30 | 51.04 | 49.45
2017-05-02 08:00 | 53.98 | 52.39
2017-05-02 08:30 | 55.33 | 53.82
2017-05-02 09:00 | 55.6 | 54.22
2017-05-02 09:30 | 55.42 | 54.5
2017-05-02 10:00 | 55.41 | 54.46
2017-05-02 10:30 | 56.04 | 55.08
2017-05-02 11:00 | 56.32 | 55.34
2017-05-02 11:30 | 56.13 | 55.14
2017-05-02 12:00 | 56.74 | 55.73
2017-05-02 12:30 | 57.12 | 56.12
2017-05-02 13:00 | 57.18 | 56.19
2017-05-02 13:30 | 57.31 | 56.32
2017-05-02 14:00 | 57.98 | 56.98
2017-05-02 14:30 | 58.49 | 57.52
2017-05-02 15:00 | 58.55 | 57.6
2017-05-02 15:30 | 59.28 | 58.36
2017-05-02 16:00 | 60.01 | 59.12
2017-05-02 16:30 | 60.02 | 59.19
2017-05-02 17:00 | 58.3 | 57.49
2017-05-02 17:30 | 56.85 | 55.87
2017-05-02 18:00 | 57.18 | 56.24
2017-05-02 18:30 | 58.7 | 57.79
2017-05-02 19:00 | 57.84 | 56.94
2017-05-02 19:30 | 53.7 | 52.77
2017-05-02 20:00 | 50.93 | 49.97
2017-05-02 20:30 | 48.33 | 47.35
2017-05-02 21:00 | 46.2 | 45.13
2017-05-02 21:30 | 44.08 | 42.84
2017-05-02 22:00 | 42.11 | 40.61
2017-05-02 22:30 | 41.35 | 38.61
2017-05-02 23:00 | 40.4 | 38.58
2017-05-02 23:30 | 36.84 | 34.89
2017-05-03 | 34.77 | 32.72
2017-05-03 00:30 | 33.72 | 31.63
2017-05-03 01:00 | 32.22 | 30.05
2017-05-03 01:30 | 31.88 | 29.69
2017-05-03 02:00 | 31.42 | 29.2
2017-05-03 02:30 | 31.05 | 28.83
2017-05-03 03:00 | 30.74 | 28.51
2017-05-03 03:30 | 30.72 | 28.49
2017-05-03 04:00 | 30.91 | 28.7
2017-05-03 04:30 | 31.52 | 29.33
2017-05-03 05:00 | 32.64 | 30.49
2017-05-03 05:30 | 35.17 | 33.13
2017-05-03 06:00 | 38.11 | 36.16
2017-05-03 06:30 | 42.51 | 40.68
2017-05-03 07:00 | 47.8 | 46.07
2017-05-03 07:30 | 54.37 | 52.92
2017-05-03 08:00 | 57.42 | 56.09
2017-05-03 08:30 | 59.3 | 57.94
2017-05-03 09:00 | 61.33 | 59.94
2017-05-03 09:30 | 67.12 | 59.42
2017-05-03 10:00 | 70.96 | 59.48
2017-05-03 10:30 | 72.26 | 60.94
2017-05-03 11:00 | 71.8 | 60.24
2017-05-03 11:30 | 71.41 | 59.77
2017-05-03 12:00 | 70.44 | 58.57
2017-05-03 12:30 | 70.41 | 58.65
2017-05-03 13:00 | 70.13 | 58.32
2017-05-03 13:30 | 70.09 | 58.47
2017-05-03 14:00 | 69.5 | 59.16
2017-05-03 14:30 | 70 | 59.73
2017-05-03 15:00 | 69.76 | 59.49
2017-05-03 15:30 | 63.58 | 59.55
2017-05-03 16:00 | 60.66 | 59.79
2017-05-03 16:30 | 60.41 | 59.59
2017-05-03 17:00 | 59.08 | 58.3
2017-05-03 17:30 | 57.41 | 56.44
2017-05-03 18:00 | 58.07 | 57
2017-05-03 18:30 | 59.54 | 58.42
2017-05-03 19:00 | 58.5 | 57.19
2017-05-03 19:30 | 55.45 | 54
2017-05-03 20:00 | 52.79 | 51.86
2017-05-03 20:30 | 50.61 | 49.68
2017-05-03 21:00 | 48.43 | 47.47
2017-05-03 21:30 | 46.58 | 45.29
2017-05-03 22:00 | 44.7 | 42.96
2017-05-03 22:30 | 42.94 | 41.14
2017-05-03 23:00 | 42.75 | 40.98
2017-05-03 23:30 | 39.35 | 37.45
2017-05-04 | 37.34 | 35.38
2017-05-04 00:30 | 36.48 | 34.48
2017-05-04 01:00 | 35 | 32.93
2017-05-04 01:30 | 34.27 | 32.16
2017-05-04 02:00 | 34.21 | 32.11
2017-05-04 02:30 | 33.56 | 31.42
2017-05-04 03:00 | 33.53 | 31.39
2017-05-04 03:30 | 33.66 | 31.53
2017-05-04 04:00 | 33.87 | 31.76
2017-05-04 04:30 | 34.68 | 32.59
2017-05-04 05:00 | 35.81 | 33.76
2017-05-04 05:30 | 38.29 | 36.31
2017-05-04 06:00 | 41.49 | 39.57
2017-05-04 06:30 | 46.63 | 44.83
2017-05-04 07:00 | 51.15 | 49.58
2017-05-04 07:30 | 57.07 | 55.69
2017-05-04 08:00 | 58.45 | 57.1
2017-05-04 08:30 | 59.72 | 58.33
2017-05-04 09:00 | 59.97 | 58.55
2017-05-04 09:30 | 60.14 | 59.03
2017-05-04 10:00 | 59.56 | 58.66
2017-05-04 10:30 | 59.16 | 58.22
2017-05-04 11:00 | 59.22 | 58.27
2017-05-04 11:30 | 60.44 | 59.49
2017-05-04 12:00 | 60.07 | 59.11
2017-05-04 12:30 | 60.26 | 59.3
2017-05-04 13:00 | 59.17 | 58.19
2017-05-04 13:30 | 59.19 | 58.2
2017-05-04 14:00 | 59.54 | 58.54
2017-05-04 14:30 | 58.37 | 57.38
2017-05-04 15:00 | 59.09 | 58.14
2017-05-04 15:30 | 58.44 | 57.5
2017-05-04 16:00 | 58.94 | 58.04
2017-05-04 16:30 | 58.47 | 57.64
2017-05-04 17:00 | 56.96 | 56.12
2017-05-04 17:30 | 55.77 | 54.76
2017-05-04 18:00 | 56.79 | 55.71
2017-05-04 18:30 | 58.89 | 57.82
2017-05-04 19:00 | 57.82 | 56.61
2017-05-04 19:30 | 55.51 | 54.07
2017-05-04 20:00 | 53.69 | 52
2017-05-04 20:30 | 50.68 | 49.45
2017-05-04 21:00 | 48.4 | 47.44
2017-05-04 21:30 | 46.06 | 45
2017-05-04 22:00 | 43.43 | 42.18
2017-05-04 22:30 | 41.63 | 40.23
2017-05-04 23:00 | 41.47 | 39.94
2017-05-04 23:30 | 38.35 | 36.2
2017-05-05 | 36.56 | 34.55
2017-05-05 00:30 | 35.01 | 32.96
2017-05-05 01:00 | 33.48 | 31.35
2017-05-05 01:30 | 33.06 | 30.9
2017-05-05 02:00 | 32.48 | 30.31
2017-05-05 02:30 | 32.33 | 30.16
2017-05-05 03:00 | 31.75 | 29.55
2017-05-05 03:30 | 32.4 | 30.23
2017-05-05 04:00 | 32.66 | 30.5
2017-05-05 04:30 | 33.27 | 31.12
2017-05-05 05:00 | 34.19 | 32.09
2017-05-05 05:30 | 36.68 | 34.66
2017-05-05 06:00 | 39.67 | 37.73
2017-05-05 06:30 | 44.6 | 42.76
2017-05-05 07:00 | 48.91 | 47.27
2017-05-05 07:30 | 53.74 | 52.54
2017-05-05 08:00 | 55.72 | 54.89
2017-05-05 08:30 | 56.01 | 55.51
2017-05-05 09:00 | 55.95 | 55.62
2017-05-05 09:30 | 55.75 | 55.5
2017-05-05 10:00 | 56.87 | 56.66
2017-05-05 10:30 | 56.34 | 56.18
2017-05-05 11:00 | 56.32 | 56.23
2017-05-05 11:30 | 55.17 | 55.11
2017-05-05 12:00 | 57.68 | 57.63
2017-05-05 12:30 | 58.4 | 58.3
2017-05-05 13:00 | 56.93 | 56.79
2017-05-05 13:30 | 56.81 | 56.65
2017-05-05 14:00 | 56.78 | 56.6
2017-05-05 14:30 | 55.19 | 54.97
2017-05-05 15:00 | 54.26 | 54.01
2017-05-05 15:30 | 53.29 | 52.89
2017-05-05 16:00 | 53.7 | 53.17
2017-05-05 16:30 | 53.53 | 53.17
2017-05-05 17:00 | 53.01 | 52.6
2017-05-05 17:30 | 52.41 | 51.67
2017-05-05 18:00 | 52.62 | 51.97
2017-05-05 18:30 | 53.12 | 52.82
2017-05-05 19:00 | 51.77 | 51.39
2017-05-05 19:30 | 49.53 | 49.01
2017-05-05 20:00 | 47.91 | 47.25
2017-05-05 20:30 | 45.8 | 44.93
2017-05-05 21:00 | 45.41 | 42.76
2017-05-05 21:30 | 43.13 | 41.26
2017-05-05 22:00 | 41.26 | 39.49
2017-05-05 22:30 | 40.5 | 38.67
2017-05-05 23:00 | 40.42 | 38.55
2017-05-05 23:30 | 37.41 | 35.32
2017-05-06 | 35.6 | 33.34
2017-05-06 00:30 | 34.56 | 32.16
2017-05-06 01:00 | 32.97 | 30.41
2017-05-06 01:30 | 32.11 | 29.46
2017-05-06 02:00 | 31.94 | 29.24
2017-05-06 02:30 | 31.5 | 28.75
2017-05-06 03:00 | 31.31 | 28.53
2017-05-06 03:30 | 30.79 | 27.91
2017-05-06 04:00 | 30.69 | 27.8
2017-05-06 04:30 | 31.08 | 28.26
2017-05-06 05:00 | 31.49 | 28.73
2017-05-06 05:30 | 32.4 | 29.77
2017-05-06 06:00 | 33.19 | 30.69
2017-05-06 06:30 | 34.83 | 32.51
2017-05-06 07:00 | 36.32 | 34.13
2017-05-06 07:30 | 39.18 | 37.27
2017-05-06 08:00 | 41.69 | 40
2017-05-06 08:30 | 43.33 | 41.76
2017-05-06 09:00 | 44.29 | 42.81
2017-05-06 09:30 | 43.35 | 41.85
2017-05-06 10:00 | 43.26 | 41.66
2017-05-06 10:30 | 42.96 | 41.25
2017-05-06 11:00 | 42.73 | 40.95
2017-05-06 11:30 | 43.27 | 41.44
2017-05-06 12:00 | 44.08 | 42.33
2017-05-06 12:30 | 42.7 | 40.98
2017-05-06 13:00 | 42.28 | 40.58
2017-05-06 13:30 | 40.64 | 38.89
2017-05-06 14:00 | 40.56 | 38.83
2017-05-06 14:30 | 41 | 39.34
2017-05-06 15:00 | 41.38 | 39.78
2017-05-06 15:30 | 43.38 | 41.88
2017-05-06 16:00 | 42.98 | 41.45
2017-05-06 16:30 | 43.39 | 41.84
2017-05-06 17:00 | 43.62 | 42.04
2017-05-06 17:30 | 44.94 | 43.42
2017-05-06 18:00 | 47.04 | 45.63
2017-05-06 18:30 | 48.46 | 47.13
2017-05-06 19:00 | 47.03 | 45.63
2017-05-06 19:30 | 45.14 | 43.64
2017-05-06 20:00 | 44.02 | 42.47
2017-05-06 20:30 | 42.8 | 41.17
2017-05-06 21:00 | 41.73 | 40.03
2017-05-06 21:30 | 40.6 | 38.81
2017-05-06 22:00 | 39.59 | 37.71
2017-05-06 22:30 | 38.76 | 36.81
2017-05-06 23:00 | 39.07 | 37.1
2017-05-06 23:30 | 36.12 | 33.92
2017-05-07 | 34.77 | 32.42
2017-05-07 00:30 | 34.15 | 31.71
2017-05-07 01:00 | 33.07 | 30.51
2017-05-07 01:30 | 32.29 | 29.66
2017-05-07 02:00 | 31.89 | 29.19
2017-05-07 02:30 | 31.53 | 28.78
2017-05-07 03:00 | 31.42 | 28.66
2017-05-07 03:30 | 31.24 | 28.43
2017-05-07 04:00 | 31.16 | 28.35
2017-05-07 04:30 | 31.44 | 28.67
2017-05-07 05:00 | 31.48 | 28.72
2017-05-07 05:30 | 31.86 | 29.16
2017-05-07 06:00 | 32.37 | 29.71
2017-05-07 06:30 | 33.02 | 30.43
2017-05-07 07:00 | 33.64 | 31.09
2017-05-07 07:30 | 35.17 | 32.8
2017-05-07 08:00 | 36.89 | 34.69
2017-05-07 08:30 | 38.38 | 36.32
2017-05-07 09:00 | 38.6 | 36.64
2017-05-07 09:30 | 39.22 | 37.35
2017-05-07 10:00 | 39.06 | 37.23
2017-05-07 10:30 | 39.75 | 38.02
2017-05-07 11:00 | 39.38 | 37.67
2017-05-07 11:30 | 38.69 | 36.96
2017-05-07 12:00 | 38.31 | 36.56
2017-05-07 12:30 | 38.31 | 36.54
2017-05-07 13:00 | 37.43 | 35.6
2017-05-07 13:30 | 37.53 | 35.7
2017-05-07 14:00 | 37.64 | 35.8
2017-05-07 14:30 | 37.7 | 35.84
2017-05-07 15:00 | 37.96 | 36.11
2017-05-07 15:30 | 38.64 | 36.79
2017-05-07 16:00 | 39.85 | 38.05
2017-05-07 16:30 | 41.55 | 39.81
2017-05-07 17:00 | 42.22 | 40.5
2017-05-07 17:30 | 44.22 | 42.58
2017-05-07 18:00 | 46.96 | 45.5
2017-05-07 18:30 | 49.32 | 47.96
2017-05-07 19:00 | 48.7 | 47.32
2017-05-07 19:30 | 46.09 | 44.57
2017-05-07 20:00 | 44.12 | 42.5
2017-05-07 20:30 | 42.38 | 40.64
2017-05-07 21:00 | 40.85 | 39.01
2017-05-07 21:30 | 39.31 | 37.34
2017-05-07 22:00 | 37.89 | 35.78
2017-05-07 22:30 | 36.63 | 34.4
2017-05-07 23:00 | 37.13 | 34.91
2017-05-07 23:30 | 34.07 | 31.57
2017-05-08 | 32.85 | 30.21
2017-05-08 00:30 | 32.04 | 29.29
2017-05-08 01:00 | 30.85 | 27.95
2017-05-08 01:30 | 30.77 | 27.86
2017-05-08 02:00 | 30.67 | 27.76
2017-05-08 02:30 | 30.78 | 27.88
2017-05-08 03:00 | 31 | 28.15
2017-05-08 03:30 | 30.93 | 28.06
2017-05-08 04:00 | 31.1 | 28.25
2017-05-08 04:30 | 31.97 | 29.26
2017-05-08 05:00 | 32.94 | 30.35
2017-05-08 05:30 | 35.29 | 33.02
2017-05-08 06:00 | 38.1 | 36.11
2017-05-08 06:30 | 42.42 | 40.82
2017-05-08 07:00 | 46.35 | 44.91
2017-05-08 07:30 | 51.58 | 50.31
2017-05-08 08:00 | 54.17 | 52.91
2017-05-08 08:30 | 56.74 | 55.6
2017-05-08 09:00 | 56.2 | 54.91
2017-05-08 09:30 | 55.95 | 54.03
2017-05-08 10:00 | 56.06 | 54.18
2017-05-08 10:30 | 56.6 | 54.76
2017-05-08 11:00 | 57.11 | 55.33
2017-05-08 11:30 | 57.52 | 55.79
2017-05-08 12:00 | 56.96 | 55.21
2017-05-08 12:30 | 56.49 | 54.72
2017-05-08 13:00 | 57.7 | 55.98
2017-05-08 13:30 | 57.84 | 56.13
2017-05-08 14:00 | 58.02 | 56.36
2017-05-08 14:30 | 54.45 | 52.83
2017-05-08 15:00 | 52.57 | 51.5
2017-05-08 15:30 | 59.69 | 58.03
2017-05-08 16:00 | 59.37 | 57.62
2017-05-08 16:30 | 58.69 | 56.81
2017-05-08 17:00 | 58.08 | 56.09
2017-05-08 17:30 | 57.67 | 55.55
2017-05-08 18:00 | 58.57 | 56.45
2017-05-08 18:30 | 59.13 | 57
2017-05-08 19:00 | 57.43 | 55.19
2017-05-08 19:30 | 54.55 | 52.09
2017-05-08 20:00 | 51.74 | 49.05
2017-05-08 20:30 | 49.45 | 46.15
2017-05-08 21:00 | 59.55 | 44.19
2017-05-08 21:30 | 55.29 | 42.26
2017-05-08 22:00 | 42.88 | 39.91
2017-05-08 22:30 | 38.29 | 38.22
2017-05-08 23:00 | 38.43 | 38.33
2017-05-08 23:30 | 34.94 | 34.77
2017-05-09 | 33.2 | 32.92
2017-05-09 00:30 | 32.33 | 32.09
2017-05-09 01:00 | 30.85 | 30.62
2017-05-09 01:30 | 30.36 | 30.13
2017-05-09 02:00 | 30.23 | 30.02
2017-05-09 02:30 | 29.89 | 29.7
2017-05-09 03:00 | 29.81 | 29.63
2017-05-09 03:30 | 29.49 | 29.34
2017-05-09 04:00 | 29.88 | 29.7
2017-05-09 04:30 | 30.57 | 30.35
2017-05-09 05:00 | 32.1 | 31.84
2017-05-09 05:30 | 34.57 | 34.15
2017-05-09 06:00 | 37.8 | 37.16
2017-05-09 06:30 | 42.76 | 41.79
2017-05-09 07:00 | 47.54 | 46.71
2017-05-09 07:30 | 53.75 | 53.22
2017-05-09 08:00 | 56.98 | 56.34
2017-05-09 08:30 | 57.87 | 56.95
2017-05-09 09:00 | 59.22 | 58.19
2017-05-09 09:30 | 56.64 | 56.4
2017-05-09 10:00 | 56.58 | 56.42
2017-05-09 10:30 | 57.27 | 57.18
2017-05-09 11:00 | 57.92 | 57.88
2017-05-09 11:30 | 59.53 | 59.48
2017-05-09 12:00 | 59.67 | 59.62
2017-05-09 12:30 | 56.91 | 56.82
2017-05-09 13:00 | 58.21 | 58.13
2017-05-09 13:30 | 59.25 | 59.16
2017-05-09 14:00 | 59.06 | 58.96
2017-05-09 14:30 | 58.82 | 58.69
2017-05-09 15:00 | 57.41 | 57.23
2017-05-09 15:30 | 55.02 | 54.65
2017-05-09 16:00 | 54.64 | 54.1
2017-05-09 16:30 | 55.73 | 54.12
2017-05-09 17:00 | 55.23 | 53.02
2017-05-09 17:30 | 54.95 | 52.62
2017-05-09 18:00 | 55.83 | 53.52
2017-05-09 18:30 | 55.76 | 53.39
2017-05-09 19:00 | 54.45 | 51.98
2017-05-09 19:30 | 51.94 | 49.27
2017-05-09 20:00 | 53.08 | 46.85
2017-05-09 20:30 | 55.13 | 44.81
2017-05-09 21:00 | 46.94 | 45.06
2017-05-09 21:30 | 44.72 | 42.67
2017-05-09 22:00 | 42.42 | 40.19
2017-05-09 22:30 | 40.9 | 38.52
2017-05-09 23:00 | 40.89 | 38.45
2017-05-09 23:30 | 36.91 | 34.76
2017-05-10 | 35.09 | 32.8
2017-05-10 00:30 | 34.19 | 31.79
2017-05-10 01:00 | 32.88 | 30.35
2017-05-10 01:30 | 32.54 | 29.97
2017-05-10 02:00 | 32.16 | 29.54
2017-05-10 02:30 | 31.81 | 29.14
2017-05-10 03:00 | 31.38 | 28.64
2017-05-10 03:30 | 31.41 | 28.66
2017-05-10 04:00 | 31.61 | 28.91
2017-05-10 04:30 | 32.47 | 29.88
2017-05-10 05:00 | 33.54 | 31.08
2017-05-10 05:30 | 35.43 | 33.2
2017-05-10 06:00 | 38.03 | 36.07
2017-05-10 06:30 | 42.74 | 41.15
2017-05-10 07:00 | 47.62 | 46.18
2017-05-10 07:30 | 53.87 | 52.62
2017-05-10 08:00 | 55.94 | 54.71
2017-05-10 08:30 | 57 | 55.85
2017-05-10 09:00 | 56.62 | 55.48
2017-05-10 09:30 | 57.1 | 55.24
2017-05-10 10:00 | 56.76 | 54.74
2017-05-10 10:30 | 56.03 | 54.03
2017-05-10 11:00 | 56.89 | 54.94
2017-05-10 11:30 | 56.85 | 54.9
2017-05-10 12:00 | 56.8 | 54.87
2017-05-10 12:30 | 56.16 | 54.18
2017-05-10 13:00 | 55.5 | 53.49
2017-05-10 13:30 | 55.85 | 53.87
2017-05-10 14:00 | 55.51 | 53.52
2017-05-10 14:30 | 51.58 | 49.49
2017-05-10 15:00 | 55.76 | 53.76
2017-05-10 15:30 | 54.19 | 52.03
2017-05-10 16:00 | 54.02 | 51.78
2017-05-10 16:30 | 55.04 | 52.74
2017-05-10 17:00 | 54.63 | 52.25
2017-05-10 17:30 | 64.07 | 51.69
2017-05-10 18:00 | 61.02 | 53.99
2017-05-10 18:30 | 56.55 | 54.91
2017-05-10 19:00 | 55.11 | 53.4
2017-05-10 19:30 | 52.4 | 50.55
2017-05-10 20:00 | 50.27 | 48.26
2017-05-10 20:30 | 48.32 | 46.16
2017-05-10 21:00 | 46.28 | 43.98
2017-05-10 21:30 | 44.58 | 42.12
2017-05-10 22:00 | 42.36 | 39.67
2017-05-10 22:30 | 40.2 | 37.33
2017-05-10 23:00 | 39.79 | 37.14
2017-05-10 23:30 | 36.61 | 33.68
2017-05-11 | 34.2 | 31.57
2017-05-11 00:30 | 33.51 | 30.97
2017-05-11 01:00 | 31.96 | 29.22
2017-05-11 01:30 | 31.37 | 28.57
2017-05-11 02:00 | 30.94 | 28.08
2017-05-11 02:30 | 30.85 | 27.97
2017-05-11 03:00 | 30.72 | 27.79
2017-05-11 03:30 | 30.65 | 27.7
2017-05-11 04:00 | 31.02 | 28.12
2017-05-11 04:30 | 31.62 | 28.81
2017-05-11 05:00 | 32.89 | 30.24
2017-05-11 05:30 | 35.07 | 32.71
2017-05-11 06:00 | 37.44 | 35.33
2017-05-11 06:30 | 41.92 | 40.17
2017-05-11 07:00 | 46.57 | 45.13
2017-05-11 07:30 | 51.06 | 49.71
2017-05-11 08:00 | 51.67 | 50.36
2017-05-11 08:30 | 50.81 | 49.52
2017-05-11 09:00 | 50.97 | 49.36
2017-05-11 09:30 | 49.89 | 48.25
2017-05-11 10:00 | 49.25 | 47.61
2017-05-11 10:30 | 49.76 | 48.2
2017-05-11 11:00 | 49.62 | 48.09
2017-05-11 11:30 | 49.69 | 48.21
2017-05-11 12:00 | 50.43 | 49
2017-05-11 12:30 | 51.08 | 49.66
2017-05-11 13:00 | 50.48 | 49.04
2017-05-11 13:30 | 50.66 | 49.25
2017-05-11 14:00 | 51.49 | 50.14
2017-05-11 14:30 | 51.99 | 50.65
2017-05-11 15:00 | 52.4 | 51.05
2017-05-11 15:30 | 52.44 | 51.04
2017-05-11 16:00 | 53.04 | 51.62
2017-05-11 16:30 | 53.09 | 51.56
2017-05-11 17:00 | 52.31 | 50.65
2017-05-11 17:30 | 52.11 | 50.35
2017-05-11 18:00 | 54.32 | 52.62
2017-05-11 18:30 | 56.18 | 54.53
2017-05-11 19:00 | 55.26 | 53.54
2017-05-11 19:30 | 52.27 | 50.39
2017-05-11 20:00 | 50.27 | 48.26
2017-05-11 20:30 | 48.22 | 46.06
2017-05-11 21:00 | 46.83 | 44.56
2017-05-11 21:30 | 44.56 | 42.08
2017-05-11 22:00 | 41.68 | 38.93
2017-05-11 22:30 | 39.76 | 37.12
2017-05-11 23:00 | 39.87 | 37.21
2017-05-11 23:30 | 36.82 | 33.87
2017-05-12 | 34.85 | 31.9
2017-05-12 00:30 | 33.33 | 30.6
2017-05-12 01:00 | 31.5 | 28.7
2017-05-12 01:30 | 31.27 | 28.44
2017-05-12 02:00 | 30.88 | 28
2017-05-12 02:30 | 30.93 | 28.04
2017-05-12 03:00 | 30.75 | 27.86
2017-05-12 03:30 | 30.67 | 27.75
2017-05-12 04:00 | 31.13 | 28.28
2017-05-12 04:30 | 31.8 | 29.06
2017-05-12 05:00 | 33.01 | 30.45
2017-05-12 05:30 | 35.36 | 33.1
2017-05-12 06:00 | 37.92 | 35.92
2017-05-12 06:30 | 42.57 | 40.96
2017-05-12 07:00 | 46.7 | 45.24
2017-05-12 07:30 | 52.01 | 50.67
2017-05-12 08:00 | 55.05 | 53.57
2017-05-12 08:30 | 55.89 | 54.49
2017-05-12 09:00 | 55.71 | 54.36
2017-05-12 09:30 | 55.63 | 54.3
2017-05-12 10:00 | 55.25 | 53.91
2017-05-12 10:30 | 53.15 | 51.8
2017-05-12 11:00 | 54.54 | 53.29
2017-05-12 11:30 | 54.04 | 52.79
2017-05-12 12:00 | 55.52 | 54.29
2017-05-12 12:30 | 56.12 | 54.88
2017-05-12 13:00 | 54.26 | 52.95
2017-05-12 13:30 | 53.28 | 51.95
2017-05-12 14:00 | 53.44 | 52.1
2017-05-12 14:30 | 53.88 | 52.5
2017-05-12 15:00 | 55.36 | 53.98
2017-05-12 15:30 | 53.83 | 52.35
2017-05-12 16:00 | 53.59 | 52.06
2017-05-12 16:30 | 54.04 | 52.46
2017-05-12 17:00 | 52.86 | 51.18
2017-05-12 17:30 | 51.14 | 49.3
2017-05-12 18:00 | 53.89 | 52.16
2017-05-12 18:30 | 53.81 | 52.05
2017-05-12 19:00 | 52.42 | 50.56
2017-05-12 19:30 | 49.92 | 47.89
2017-05-12 20:00 | 48.3 | 46.18
2017-05-12 20:30 | 46.17 | 44.16
2017-05-12 21:00 | 44.05 | 42.02
2017-05-12 21:30 | 42.1 | 40.07
2017-05-12 22:00 | 40.49 | 38.32
2017-05-12 22:30 | 39.12 | 36.8
2017-05-12 23:00 | 38.61 | 36.21
2017-05-12 23:30 | 35.99 | 33.32
2017-05-13 | 33.9 | 30.98
2017-05-13 00:30 | 33.33 | 30.64
2017-05-13 01:00 | 31.65 | 28.85
2017-05-13 01:30 | 31.02 | 28.14
2017-05-13 02:00 | 30.41 | 27.45
2017-05-13 02:30 | 30.2 | 27.19
2017-05-13 03:00 | 30.17 | 27.16
2017-05-13 03:30 | 29.86 | 26.79
2017-05-13 04:00 | 29.66 | 26.58
2017-05-13 04:30 | 30.11 | 27.11
2017-05-13 05:00 | 30.64 | 27.72
2017-05-13 05:30 | 32.16 | 29.46
2017-05-13 06:00 | 32.89 | 30.32
2017-05-13 06:30 | 35.04 | 32.74
2017-05-13 07:00 | 36.92 | 34.77
2017-05-13 07:30 | 39.43 | 37.5
2017-05-13 08:00 | 41.61 | 39.85
2017-05-13 08:30 | 43.76 | 42.15
2017-05-13 09:00 | 45.48 | 43.99
2017-05-13 09:30 | 45.73 | 44.31
2017-05-13 10:00 | 44.81 | 43.32
2017-05-13 10:30 | 44.56 | 42.9
2017-05-13 11:00 | 43.61 | 41.93
2017-05-13 11:30 | 43.82 | 42.18
2017-05-13 12:00 | 42.58 | 40.87
2017-05-13 12:30 | 41.78 | 39.98
2017-05-13 13:00 | 41.29 | 39.45
2017-05-13 13:30 | 40.77 | 38.89
2017-05-13 14:00 | 40.85 | 38.95
2017-05-13 14:30 | 41.24 | 39.29
2017-05-13 15:00 | 41.22 | 39.27
2017-05-13 15:30 | 41.6 | 39.64
2017-05-13 16:00 | 42.14 | 40.2
2017-05-13 16:30 | 42.94 | 41.01
2017-05-13 17:00 | 42.64 | 40.66
2017-05-13 17:30 | 44.09 | 42.18
2017-05-13 18:00 | 46.53 | 44.8
2017-05-13 18:30 | 48.05 | 46.4
2017-05-13 19:00 | 46.89 | 45.17
2017-05-13 19:30 | 44.96 | 43.13
2017-05-13 20:00 | 43.33 | 41.39
2017-05-13 20:30 | 41.65 | 39.6
2017-05-13 21:00 | 40.39 | 38.24
2017-05-13 21:30 | 39.61 | 37.37
2017-05-13 22:00 | 38.21 | 35.82
2017-05-13 22:30 | 37.16 | 34.66
2017-05-13 23:00 | 37.65 | 35.16
2017-05-13 23:30 | 34.99 | 32.23
2017-05-14 | 33.09 | 30.34
2017-05-14 00:30 | 32.34 | 29.62
2017-05-14 01:00 | 31.18 | 28.33
2017-05-14 01:30 | 30.8 | 27.91
2017-05-14 02:00 | 30.26 | 27.3
2017-05-14 02:30 | 30.13 | 27.15
2017-05-14 03:00 | 29.83 | 26.78
2017-05-14 03:30 | 29.46 | 26.34
2017-05-14 04:00 | 29.54 | 26.44
2017-05-14 04:30 | 29.61 | 26.54
2017-05-14 05:00 | 30.09 | 27.09
2017-05-14 05:30 | 30.6 | 27.69
2017-05-14 06:00 | 31.14 | 28.3
2017-05-14 06:30 | 31.75 | 28.95
2017-05-14 07:00 | 32.45 | 29.67
2017-05-14 07:30 | 34.22 | 31.67
2017-05-14 08:00 | 35.6 | 33.22
2017-05-14 08:30 | 36.7 | 34.47
2017-05-14 09:00 | 37.61 | 35.51
2017-05-14 09:30 | 38.1 | 36.12
2017-05-14 10:00 | 38.71 | 36.82
2017-05-14 10:30 | 38.78 | 36.95
2017-05-14 11:00 | 38.43 | 36.49
2017-05-14 11:30 | 38.14 | 36.02
2017-05-14 12:00 | 38.09 | 35.97
2017-05-14 12:30 | 38.12 | 36
2017-05-14 13:00 | 37.58 | 35.42
2017-05-14 13:30 | 37.24 | 35.06
2017-05-14 14:00 | 37.65 | 35.5
2017-05-14 14:30 | 37.83 | 35.66
2017-05-14 15:00 | 38.33 | 36.18
2017-05-14 15:30 | 38.95 | 36.82
2017-05-14 16:00 | 40.04 | 37.95
2017-05-14 16:30 | 41.59 | 39.55
2017-05-14 17:00 | 42 | 39.98
2017-05-14 17:30 | 44.14 | 42.23
2017-05-14 18:00 | 46.62 | 44.88
2017-05-14 18:30 | 48.7 | 47.07
2017-05-14 19:00 | 47.48 | 45.77
2017-05-14 19:30 | 45.33 | 43.49
2017-05-14 20:00 | 43.61 | 41.66
2017-05-14 20:30 | 41.86 | 39.78
2017-05-14 21:00 | 40.75 | 38.57
2017-05-14 21:30 | 38.96 | 36.61
2017-05-14 22:00 | 37.6 | 35.07
2017-05-14 22:30 | 36.19 | 33.51
2017-05-14 23:00 | 36.69 | 34.03
2017-05-14 23:30 | 33.79 | 30.97
2017-05-15 | 31.96 | 29.19
2017-05-15 00:30 | 31.45 | 28.6
2017-05-15 01:00 | 30.32 | 27.33
2017-05-15 01:30 | 30 | 26.98
2017-05-15 02:00 | 29.84 | 26.76
2017-05-15 02:30 | 29.79 | 26.7
2017-05-15 03:00 | 29.64 | 26.55
2017-05-15 03:30 | 29.81 | 26.75
2017-05-15 04:00 | 29.92 | 26.87
2017-05-15 04:30 | 30.58 | 27.63
2017-05-15 05:00 | 31.77 | 29
2017-05-15 05:30 | 34.08 | 31.65
2017-05-15 06:00 | 36.74 | 34.62
2017-05-15 06:30 | 41.54 | 39.86
2017-05-15 07:00 | 45.83 | 44.39
2017-05-15 07:30 | 50.28 | 48.94
2017-05-15 08:00 | 52.94 | 51.54
2017-05-15 08:30 | 53.66 | 52.2
2017-05-15 09:00 | 53.3 | 51.89
2017-05-15 09:30 | 53.32 | 51.97
2017-05-15 10:00 | 53.43 | 52.13
2017-05-15 10:30 | 54.11 | 52.87
2017-05-15 11:00 | 54.52 | 53.32
2017-05-15 11:30 | 55.47 | 54.32
2017-05-15 12:00 | 56.96 | 55.67
2017-05-15 12:30 | 57.73 | 56.16
2017-05-15 13:00 | 57.53 | 55.96
2017-05-15 13:30 | 57.78 | 56.19
2017-05-15 14:00 | 57.51 | 55.93
2017-05-15 14:30 | 57.86 | 56.3
2017-05-15 15:00 | 57.98 | 56.41
2017-05-15 15:30 | 58.06 | 56.11
2017-05-15 16:00 | 58.41 | 56.42
2017-05-15 16:30 | 58.48 | 56.38
2017-05-15 17:00 | 57.91 | 55.68
2017-05-15 17:30 | 55.91 | 53.98
2017-05-15 18:00 | 55.85 | 54.29
2017-05-15 18:30 | 57.26 | 55.74
2017-05-15 19:00 | 55.89 | 54.28
2017-05-15 19:30 | 52.52 | 50.74
2017-05-15 20:00 | 50.67 | 48.77
2017-05-15 20:30 | 48.49 | 46.43
2017-05-15 21:00 | 46.29 | 44.05
2017-05-15 21:30 | 44.51 | 42.12
2017-05-15 22:00 | 41.64 | 39.22
2017-05-15 22:30 | 39.67 | 37.11
2017-05-15 23:00 | 39.85 | 37.27
2017-05-15 23:30 | 36.64 | 33.73
2017-05-16 | 34.62 | 31.65
2017-05-16 00:30 | 33.77 | 30.91
2017-05-16 01:00 | 32.64 | 29.65
2017-05-16 01:30 | 31.79 | 28.69
2017-05-16 02:00 | 31.64 | 28.51
2017-05-16 02:30 | 30.76 | 27.8
2017-05-16 03:00 | 30.18 | 27.23
2017-05-16 03:30 | 30.13 | 27.16
2017-05-16 04:00 | 30.43 | 27.51
2017-05-16 04:30 | 31.26 | 28.49
2017-05-16 05:00 | 32.4 | 29.78
2017-05-16 05:30 | 34.48 | 32.13
2017-05-16 06:00 | 37.45 | 35.42
2017-05-16 06:30 | 41.51 | 39.84
2017-05-16 07:00 | 46.4 | 44.97
2017-05-16 07:30 | 51.44 | 49.96
2017-05-16 08:00 | 53.86 | 51.35
2017-05-16 08:30 | 54.64 | 52.2
2017-05-16 09:00 | 55.96 | 53.72
2017-05-16 09:30 | 56.36 | 54.24
2017-05-16 10:00 | 56.67 | 54.6
2017-05-16 10:30 | 58.12 | 56.19
2017-05-16 11:00 | 57.79 | 55.9
2017-05-16 11:30 | 57.51 | 55.62
2017-05-16 12:00 | 58.75 | 56.94
2017-05-16 12:30 | 59.64 | 57.88
2017-05-16 13:00 | 59.16 | 57.39
2017-05-16 13:30 | 59.33 | 57.57
2017-05-16 14:00 | 59.91 | 58.18
2017-05-16 14:30 | 60.19 | 58.47
2017-05-16 15:00 | 60.72 | 59.01
2017-05-16 15:30 | 60.96 | 59.21
2017-05-16 16:00 | 61.26 | 59.44
2017-05-16 16:30 | 61.24 | 59.3
2017-05-16 17:00 | 59.86 | 57.75
2017-05-16 17:30 | 57.23 | 54.82
2017-05-16 18:00 | 58.06 | 55.61
2017-05-16 18:30 | 59.35 | 56.78
2017-05-16 19:00 | 57.89 | 54.93
2017-05-16 19:30 | 55.08 | 51.58
2017-05-16 20:00 | 54.01 | 49.35
2017-05-16 20:30 | 55.31 | 46.91
2017-05-16 21:00 | 53.8 | 44.95
2017-05-16 21:30 | 50.25 | 41.82
2017-05-16 22:00 | 47.14 | 39.62
2017-05-16 22:30 | 45.57 | 37.86
2017-05-16 23:00 | 45.67 | 37.87
2017-05-16 23:30 | 42.62 | 34.13
2017-05-17 | 40.52 | 31.95
2017-05-17 00:30 | 40.11 | 31.34
2017-05-17 01:00 | 38.95 | 29.78
2017-05-17 01:30 | 38.5 | 29.11
2017-05-17 02:00 | 38.18 | 28.68
2017-05-17 02:30 | 37.84 | 28.17
2017-05-17 03:00 | 36.95 | 27.74
2017-05-17 03:30 | 36.87 | 27.6
2017-05-17 04:00 | 37.01 | 27.78
2017-05-17 04:30 | 37.66 | 28.75
2017-05-17 05:00 | 38.38 | 29.78
2017-05-17 05:30 | 40.46 | 32.66
2017-05-17 06:00 | 42.87 | 35.87
2017-05-17 06:30 | 41.46 | 40.5
2017-05-17 07:00 | 46.24 | 45.15
2017-05-17 07:30 | 51.24 | 50.46
2017-05-17 08:00 | 52.69 | 52.29
2017-05-17 08:30 | 52.62 | 52.49
2017-05-17 09:00 | 52.97 | 52.69
2017-05-17 09:30 | 52.83 | 52.46
2017-05-17 10:00 | 53.48 | 52.92
2017-05-17 10:30 | 55 | 54.3
2017-05-17 11:00 | 54.99 | 54.24
2017-05-17 11:30 | 55.94 | 54.98
2017-05-17 12:00 | 55.78 | 54.8
2017-05-17 12:30 | 56.05 | 55.13
2017-05-17 13:00 | 55.8 | 54.95
2017-05-17 13:30 | 56.13 | 55.22
2017-05-17 14:00 | 57.17 | 56.21
2017-05-17 14:30 | 56.65 | 55.77
2017-05-17 15:00 | 56.07 | 55.3
2017-05-17 15:30 | 55.99 | 55.37
2017-05-17 16:00 | 55.98 | 55.51
2017-05-17 16:30 | 56.28 | 55.98
2017-05-17 17:00 | 54.97 | 54.84
2017-05-17 17:30 | 54.79 | 54.73
2017-05-17 18:00 | 55.82 | 55.79
2017-05-17 18:30 | 56.49 | 56.47
2017-05-17 19:00 | 54.73 | 54.71
2017-05-17 19:30 | 51.88 | 51.86
2017-05-17 20:00 | 49.98 | 49.94
2017-05-17 20:30 | 48.11 | 48.04
2017-05-17 21:00 | 46.18 | 46.07
2017-05-17 21:30 | 44.29 | 44.07
2017-05-17 22:00 | 42 | 41.65
2017-05-17 22:30 | 41.47 | 39.96
2017-05-17 23:00 | 47.73 | 39.67
2017-05-17 23:30 | 44.96 | 36.17
2017-05-18 | 42.95 | 33.9
2017-05-18 00:30 | 40.36 | 32.2
2017-05-18 01:00 | 39.29 | 30.85
2017-05-18 01:30 | 38.65 | 30.04
2017-05-18 02:00 | 38.7 | 30.04
2017-05-18 02:30 | 38.43 | 29.62
2017-05-18 03:00 | 38.1 | 29.11
2017-05-18 03:30 | 38.23 | 29.27
2017-05-18 04:00 | 38.06 | 29.03
2017-05-18 04:30 | 38.57 | 29.82
2017-05-18 05:00 | 39.75 | 31.43
2017-05-18 05:30 | 41.2 | 33.42
2017-05-18 06:00 | 43.53 | 36.57
2017-05-18 06:30 | 48.06 | 42.23
2017-05-18 07:00 | 49.93 | 47.54
2017-05-18 07:30 | 54.24 | 53.71
2017-05-18 08:00 | 62.4 | 56.71
2017-05-18 08:30 | 63.79 | 57.67
2017-05-18 09:00 | 64.18 | 58.03
2017-05-18 09:30 | 64.67 | 58.64
2017-05-18 10:00 | 65.09 | 59.15
2017-05-18 10:30 | 65.83 | 60.02
2017-05-18 11:00 | 66.29 | 60.58
2017-05-18 11:30 | 67.07 | 61.49
2017-05-18 12:00 | 66.04 | 60.34
2017-05-18 12:30 | 65.94 | 60.18
2017-05-18 13:00 | 65.67 | 59.85
2017-05-18 13:30 | 65.33 | 59.49
2017-05-18 14:00 | 65.55 | 59.73
2017-05-18 14:30 | 65.05 | 59.12
2017-05-18 15:00 | 64.74 | 58.73
2017-05-18 15:30 | 63.85 | 57.61
2017-05-18 16:00 | 63.43 | 57.07
2017-05-18 16:30 | 63.44 | 56.9
2017-05-18 17:00 | 62.59 | 55.83
2017-05-18 17:30 | 62.67 | 55.83
2017-05-18 18:00 | 63.84 | 57.12
2017-05-18 18:30 | 61.52 | 54.25
2017-05-18 19:00 | 59.96 | 52.38
2017-05-18 19:30 | 58.34 | 50.39
2017-05-18 20:00 | 57.1 | 48.82
2017-05-18 20:30 | 55.45 | 46.73
2017-05-18 21:00 | 55.05 | 46.29
2017-05-18 21:30 | 46.75 | 44.54
2017-05-18 22:00 | 43.74 | 41.39
2017-05-18 22:30 | 41.22 | 38.96
2017-05-18 23:00 | 40.53 | 38.19
2017-05-18 23:30 | 36.47 | 34.44
2017-05-19 | 34.82 | 32.67
2017-05-19 00:30 | 34.03 | 31.78
2017-05-19 01:00 | 32.79 | 30.42
2017-05-19 01:30 | 32.2 | 29.77
2017-05-19 02:00 | 31.81 | 29.34
2017-05-19 02:30 | 31.51 | 28.98
2017-05-19 03:00 | 31.46 | 28.93
2017-05-19 03:30 | 31.27 | 28.71
2017-05-19 04:00 | 31.54 | 29.02
2017-05-19 04:30 | 32.15 | 29.71
2017-05-19 05:00 | 32.83 | 30.47
2017-05-19 05:30 | 35.12 | 33.01
2017-05-19 06:00 | 37.92 | 36.1
2017-05-19 06:30 | 43.14 | 41.47
2017-05-19 07:00 | 47.84 | 46.15
2017-05-19 07:30 | 53.35 | 52.38
2017-05-19 08:00 | 56.26 | 55.17
2017-05-19 08:30 | 59.21 | 57.14
2017-05-19 09:00 | 59.39 | 57.36
2017-05-19 09:30 | 59.74 | 57.75
2017-05-19 10:00 | 59.69 | 57.72
2017-05-19 10:30 | 60.14 | 58.24
2017-05-19 11:00 | 59.86 | 57.95
2017-05-19 11:30 | 59.71 | 57.8
2017-05-19 12:00 | 58.16 | 56.15
2017-05-19 12:30 | 59.91 | 57.96
2017-05-19 13:00 | 58.85 | 56.84
2017-05-19 13:30 | 58.31 | 56.44
2017-05-19 14:00 | 57.32 | 55.46
2017-05-19 14:30 | 58.02 | 56.04
2017-05-19 15:00 | 56.91 | 54.74
2017-05-19 15:30 | 55.66 | 53.36
2017-05-19 16:00 | 55.34 | 52.98
2017-05-19 16:30 | 56.06 | 53.64
2017-05-19 17:00 | 56.32 | 53.69
2017-05-19 17:30 | 55.97 | 52.81
2017-05-19 18:00 | 56.45 | 53.08
2017-05-19 18:30 | 56.41 | 52.8
2017-05-19 19:00 | 55.56 | 51.69
2017-05-19 19:30 | 53.03 | 48.58
2017-05-19 20:00 | 51.31 | 46.31
2017-05-19 20:30 | 49.95 | 44.4
2017-05-19 21:00 | 51.7 | 42.19
2017-05-19 21:30 | 42.31 | 40.15
2017-05-19 22:00 | 40.43 | 38.1
2017-05-19 22:30 | 38.93 | 36.64
2017-05-19 23:00 | 39.42 | 37.25
2017-05-19 23:30 | 36.4 | 33.98
2017-05-20 | 34.25 | 31.88
2017-05-20 00:30 | 33.32 | 30.92
2017-05-20 01:00 | 32.14 | 29.63
2017-05-20 01:30 | 31.33 | 28.73
2017-05-20 02:00 | 30.75 | 28.08
2017-05-20 02:30 | 30.33 | 27.6
2017-05-20 03:00 | 30 | 27.21
2017-05-20 03:30 | 29.74 | 26.91
2017-05-20 04:00 | 29.95 | 27.16
2017-05-20 04:30 | 30.05 | 27.28
2017-05-20 05:00 | 30.57 | 27.88
2017-05-20 05:30 | 31.62 | 29.07
2017-05-20 06:00 | 32.67 | 30.26
2017-05-20 06:30 | 34.45 | 32.23
2017-05-20 07:00 | 35.99 | 33.88
2017-05-20 07:30 | 40.26 | 38.49
2017-05-20 08:00 | 42.41 | 40.8
2017-05-20 08:30 | 45.21 | 43.5
2017-05-20 09:00 | 47.05 | 45.35
2017-05-20 09:30 | 47.48 | 45.89
2017-05-20 10:00 | 47.16 | 45.52
2017-05-20 10:30 | 46.99 | 45.29
2017-05-20 11:00 | 45.57 | 43.82
2017-05-20 11:30 | 44.49 | 42.7
2017-05-20 12:00 | 43.66 | 41.84
2017-05-20 12:30 | 43.43 | 41.64
2017-05-20 13:00 | 42.5 | 40.67
2017-05-20 13:30 | 41.67 | 39.82
2017-05-20 14:00 | 41.43 | 39.6
2017-05-20 14:30 | 41.33 | 39.51
2017-05-20 15:00 | 41.69 | 39.9
2017-05-20 15:30 | 41.99 | 40.24
2017-05-20 16:00 | 42.96 | 41.27
2017-05-20 16:30 | 44.11 | 42.52
2017-05-20 17:00 | 44.37 | 42.83
2017-05-20 17:30 | 45.68 | 44.21
2017-05-20 18:00 | 48.24 | 46.82
2017-05-20 18:30 | 49.61 | 48.22
2017-05-20 19:00 | 48.14 | 46.73
2017-05-20 19:30 | 45.86 | 44.38
2017-05-20 20:00 | 44.1 | 42.58
2017-05-20 20:30 | 42.52 | 40.96
2017-05-20 21:00 | 41.13 | 39.54
2017-05-20 21:30 | 39.76 | 38.14
2017-05-20 22:00 | 38.53 | 36.89
2017-05-20 22:30 | 37.4 | 35.73
2017-05-20 23:00 | 37.88 | 36.26
2017-05-20 23:30 | 34.69 | 32.94
2017-05-21 | 32.95 | 30.99
2017-05-21 00:30 | 32.79 | 30.7
2017-05-21 01:00 | 31.46 | 29.27
2017-05-21 01:30 | 30.93 | 28.7
2017-05-21 02:00 | 30.52 | 28.28
2017-05-21 02:30 | 30.25 | 27.99
2017-05-21 03:00 | 29.9 | 27.62
2017-05-21 03:30 | 29.44 | 27.18
2017-05-21 04:00 | 29.38 | 27.12
2017-05-21 04:30 | 29.6 | 27.34
2017-05-21 05:00 | 29.87 | 27.62
2017-05-21 05:30 | 30.54 | 28.33
2017-05-21 06:00 | 31.02 | 28.85
2017-05-21 06:30 | 31.93 | 29.82
2017-05-21 07:00 | 32.34 | 30.29
2017-05-21 07:30 | 33.92 | 31.93
2017-05-21 08:00 | 35.7 | 33.77
2017-05-21 08:30 | 37.73 | 35.84
2017-05-21 09:00 | 39.74 | 37.91
2017-05-21 09:30 | 39.92 | 38.06
2017-05-21 10:00 | 39.72 | 37.81
2017-05-21 10:30 | 39.69 | 37.73
2017-05-21 11:00 | 39.47 | 37.69
2017-05-21 11:30 | 39.03 | 37.24
2017-05-21 12:00 | 38.78 | 36.96
2017-05-21 12:30 | 39.39 | 37.6
2017-05-21 13:00 | 38.78 | 36.97
2017-05-21 13:30 | 38.7 | 36.89
2017-05-21 14:00 | 38.98 | 37.19
2017-05-21 14:30 | 39.05 | 37.29
2017-05-21 15:00 | 39.19 | 37.45
2017-05-21 15:30 | 39.78 | 38.07
2017-05-21 16:00 | 41.04 | 39.41
2017-05-21 16:30 | 42.68 | 41.14
2017-05-21 17:00 | 42.76 | 41.24
2017-05-21 17:30 | 45.41 | 43.98
2017-05-21 18:00 | 48.68 | 47.32
2017-05-21 18:30 | 51.14 | 49.83
2017-05-21 19:00 | 50.15 | 48.81
2017-05-21 19:30 | 47.11 | 45.71
2017-05-21 20:00 | 45 | 43.54
2017-05-21 20:30 | 43.11 | 41.62
2017-05-21 21:00 | 41.38 | 39.86
2017-05-21 21:30 | 39.47 | 37.9
2017-05-21 22:00 | 37.7 | 36.07
2017-05-21 22:30 | 36.29 | 34.61
2017-05-21 23:00 | 36.41 | 34.78
2017-05-21 23:30 | 33.56 | 31.8
2017-05-22 | 32.03 | 30.01
2017-05-22 00:30 | 31.59 | 29.45
2017-05-22 01:00 | 30.41 | 28.18
2017-05-22 01:30 | 30.25 | 28.02
2017-05-22 02:00 | 30.19 | 27.96
2017-05-22 02:30 | 30 | 27.75
2017-05-22 03:00 | 29.81 | 27.56
2017-05-22 03:30 | 29.79 | 27.53
2017-05-22 04:00 | 29.95 | 27.7
2017-05-22 04:30 | 30.67 | 28.46
2017-05-22 05:00 | 31.68 | 29.51
2017-05-22 05:30 | 34.44 | 32.36
2017-05-22 06:00 | 37.51 | 35.52
2017-05-22 06:30 | 41.97 | 40.1
2017-05-22 07:00 | 46.86 | 45.14
2017-05-22 07:30 | 52.62 | 51.09
2017-05-22 08:00 | 55.12 | 54.01
2017-05-22 08:30 | 56.79 | 55.48
2017-05-22 09:00 | 56.79 | 55.75
2017-05-22 09:30 | 55.9 | 54.88
2017-05-22 10:00 | 56.38 | 55.41
2017-05-22 10:30 | 57.27 | 56.45
2017-05-22 11:00 | 57.36 | 56.52
2017-05-22 11:30 | 57.53 | 56.68
2017-05-22 12:00 | 56.9 | 56.02
2017-05-22 12:30 | 59.16 | 58.34
2017-05-22 13:00 | 58.51 | 57.68
2017-05-22 13:30 | 58.84 | 58.01
2017-05-22 14:00 | 60.24 | 59.43
2017-05-22 14:30 | 59.57 | 58.77
2017-05-22 15:00 | 59.01 | 58.23
2017-05-22 15:30 | 57.87 | 57.05
2017-05-22 16:00 | 58.29 | 57.38
2017-05-22 16:30 | 59.41 | 58.38
2017-05-22 17:00 | 58.4 | 57.1
2017-05-22 17:30 | 57.92 | 56.02
2017-05-22 18:00 | 59.02 | 56.9
2017-05-22 18:30 | 60.06 | 57.73
2017-05-22 19:00 | 56.96 | 56.05
2017-05-22 19:30 | 54.2 | 53.2
2017-05-22 20:00 | 52.16 | 51.07
2017-05-22 20:30 | 49.72 | 48.35
2017-05-22 21:00 | 46.93 | 45.45
2017-05-22 21:30 | 44.75 | 43.23
2017-05-22 22:00 | 43.07 | 41.5
2017-05-22 22:30 | 40.66 | 39.05
2017-05-22 23:00 | 41.41 | 39.82
2017-05-22 23:30 | 38.04 | 36.35
2017-05-23 | 36.15 | 34.39
2017-05-23 00:30 | 35.24 | 33.44
2017-05-23 01:00 | 33.67 | 31.62
2017-05-23 01:30 | 32.78 | 30.6
2017-05-23 02:00 | 32.35 | 30.17
2017-05-23 02:30 | 32.07 | 29.89
2017-05-23 03:00 | 31.66 | 29.46
2017-05-23 03:30 | 32.19 | 29.99
2017-05-23 04:00 | 32.68 | 30.5
2017-05-23 04:30 | 33.05 | 30.88
2017-05-23 05:00 | 33.62 | 31.49
2017-05-23 05:30 | 36.7 | 34.68
2017-05-23 06:00 | 39.74 | 37.79
2017-05-23 06:30 | 44.84 | 43.6
2017-05-23 07:00 | 49.28 | 48.18
2017-05-23 07:30 | 55.43 | 53.58
2017-05-23 08:00 | 56.99 | 55.56
2017-05-23 08:30 | 57.31 | 56.26
2017-05-23 09:00 | 57.82 | 56.93
2017-05-23 09:30 | 57.79 | 56.97
2017-05-23 10:00 | 57.05 | 56.22
2017-05-23 10:30 | 57.42 | 56.6
2017-05-23 11:00 | 57.88 | 57.04
2017-05-23 11:30 | 58.31 | 57.45
2017-05-23 12:00 | 58.75 | 57.92
2017-05-23 12:30 | 59.13 | 58.32
2017-05-23 13:00 | 58.12 | 57.29
2017-05-23 13:30 | 57.94 | 57.09
2017-05-23 14:00 | 58.13 | 57.29
2017-05-23 14:30 | 58.75 | 57.93
2017-05-23 15:00 | 58.42 | 57.61
2017-05-23 15:30 | 57.71 | 56.88
2017-05-23 16:00 | 58.98 | 58.08
2017-05-23 16:30 | 58.9 | 57.78
2017-05-23 17:00 | 57.73 | 56.19
2017-05-23 17:30 | 56.76 | 54.62
2017-05-23 18:00 | 57.53 | 55.73
2017-05-23 18:30 | 58.09 | 56.26
2017-05-23 19:00 | 56.74 | 54.81
2017-05-23 19:30 | 53.57 | 51.45
2017-05-23 20:00 | 51.52 | 49.27
2017-05-23 20:30 | 49.76 | 47.34
2017-05-23 21:00 | 47.53 | 44.92
2017-05-23 21:30 | 44.92 | 42.51
2017-05-23 22:00 | 42.16 | 40.3
2017-05-23 22:30 | 40.5 | 38.51
2017-05-23 23:00 | 40.61 | 38.6
2017-05-23 23:30 | 36.83 | 34.51
2017-05-24 | 35 | 32.5
2017-05-24 00:30 | 33.81 | 31.46
2017-05-24 01:00 | 32.71 | 30.33
2017-05-24 01:30 | 32.05 | 29.61
2017-05-24 02:00 | 31.78 | 29.3
2017-05-24 02:30 | 31.07 | 28.48
2017-05-24 03:00 | 30.74 | 28.09
2017-05-24 03:30 | 30.89 | 28.25
2017-05-24 04:00 | 28.98 | 28.38
2017-05-24 04:30 | 29.08 | 28.95
2017-05-24 05:00 | 30.51 | 30.34
2017-05-24 05:30 | 32.92 | 32.68
2017-05-24 06:00 | 36.29 | 35.85
2017-05-24 06:30 | 41.2 | 40.48
2017-05-24 07:00 | 45.89 | 44.85
2017-05-24 07:30 | 51.13 | 50.22
2017-05-24 08:00 | 52.83 | 52.3
2017-05-24 08:30 | 53.69 | 53.44
2017-05-24 09:00 | 54.05 | 53.71
2017-05-24 09:30 | 53.31 | 52.91
2017-05-24 10:00 | 53.92 | 53.4
2017-05-24 10:30 | 54.75 | 54.07
2017-05-24 11:00 | 55.26 | 54.48
2017-05-24 11:30 | 55.11 | 54.2
2017-05-24 12:00 | 55.17 | 54.21
2017-05-24 12:30 | 55.16 | 54.32
2017-05-24 13:00 | 55.01 | 54.15
2017-05-24 13:30 | 55.07 | 54.17
2017-05-24 14:00 | 56.04 | 55.08
2017-05-24 14:30 | 56.49 | 55.55
2017-05-24 15:00 | 56.24 | 55.39
2017-05-24 15:30 | 56.21 | 55.48
2017-05-24 16:00 | 56.56 | 56.01
2017-05-24 16:30 | 56.52 | 56.21
2017-05-24 17:00 | 54.78 | 54.65
2017-05-24 17:30 | 53.86 | 53.82
2017-05-24 18:00 | 55.42 | 55.4
2017-05-24 18:30 | 56.4 | 56.38
2017-05-24 19:00 | 54.69 | 54.67
2017-05-24 19:30 | 51.58 | 51.55
2017-05-24 20:00 | 49.42 | 49.35
2017-05-24 20:30 | 46.77 | 46.62
2017-05-24 21:00 | 44.41 | 44.24
2017-05-24 21:30 | 42.19 | 42.08
2017-05-24 22:00 | 40.02 | 39.95
2017-05-24 22:30 | 37.74 | 37.69
2017-05-24 23:00 | 37.74 | 37.7
2017-05-24 23:30 | 33.97 | 33.95
2017-05-25 | 31.92 | 31.88
2017-05-25 00:30 | 30.82 | 30.69
2017-05-25 01:00 | 29.56 | 29.44
2017-05-25 01:30 | 28.81 | 28.7
2017-05-25 02:00 | 28.39 | 28.28
2017-05-25 02:30 | 27.72 | 27.63
2017-05-25 03:00 | 27.54 | 27.46
2017-05-25 03:30 | 27.79 | 27.7
2017-05-25 04:00 | 27.73 | 27.64
2017-05-25 04:30 | 28.8 | 28.71
2017-05-25 05:00 | 30.21 | 30.1
2017-05-25 05:30 | 32.98 | 32.75
2017-05-25 06:00 | 36.25 | 35.84
2017-05-25 06:30 | 41.91 | 41.17
2017-05-25 07:00 | 46.62 | 45.62
2017-05-25 07:30 | 49.96 | 49.85
2017-05-25 08:00 | 52.13 | 51.87
2017-05-25 08:30 | 51.8 | 51.4
2017-05-25 09:00 | 51.47 | 51.34
2017-05-25 09:30 | 50.79 | 50.6
2017-05-25 10:00 | 50.47 | 50.22
2017-05-25 10:30 | 51.58 | 51.16
2017-05-25 11:00 | 51.67 | 51.16
2017-05-25 11:30 | 52.35 | 51.71
2017-05-25 12:00 | 52.86 | 52.17
2017-05-25 12:30 | 53.61 | 52.93
2017-05-25 13:00 | 53.37 | 52.73
2017-05-25 13:30 | 53.74 | 53.03
2017-05-25 14:00 | 54.86 | 54.11
2017-05-25 14:30 | 56.33 | 55.6
2017-05-25 15:00 | 57.62 | 56.86
2017-05-25 15:30 | 55.45 | 54.87
2017-05-25 16:00 | 55.73 | 55.29
2017-05-25 16:30 | 55.16 | 54.94
2017-05-25 17:00 | 53.95 | 53.85
2017-05-25 17:30 | 53.58 | 53.55
2017-05-25 18:00 | 55.39 | 55.36
2017-05-25 18:30 | 56.48 | 56.46
2017-05-25 19:00 | 55.07 | 55.05
2017-05-25 19:30 | 51.83 | 51.78
2017-05-25 20:00 | 49.85 | 49.76
2017-05-25 20:30 | 47.79 | 47.63
2017-05-25 21:00 | 45.67 | 45.5
2017-05-25 21:30 | 42.02 | 41.94
2017-05-25 22:00 | 39.24 | 39.19
2017-05-25 22:30 | 37.32 | 37.28
2017-05-25 23:00 | 37.39 | 37.36
2017-05-25 23:30 | 33.68 | 33.66
2017-05-26 | 31.56 | 31.5
2017-05-26 00:30 | 31.1 | 30.99
2017-05-26 01:00 | 29.51 | 29.41
2017-05-26 01:30 | 28.79 | 28.69
2017-05-26 02:00 | 28.38 | 28.29
2017-05-26 02:30 | 27.48 | 27.4
2017-05-26 03:00 | 27.46 | 27.39
2017-05-26 03:30 | 27.72 | 27.64
2017-05-26 04:00 | 27.89 | 27.81
2017-05-26 04:30 | 28.69 | 28.6
2017-05-26 05:00 | 28.4 | 28.32
2017-05-26 05:30 | 32.4 | 32.19
2017-05-26 06:00 | 35.64 | 35.29
2017-05-26 06:30 | 40.51 | 39.91
2017-05-26 07:00 | 43.96 | 43.16
2017-05-26 07:30 | 48.59 | 48.12
2017-05-26 08:00 | 50.3 | 49.73
2017-05-26 08:30 | 50.6 | 50.4
2017-05-26 09:00 | 50.46 | 50.35
2017-05-26 09:30 | 48.44 | 48.3
2017-05-26 10:00 | 51.69 | 51.35
2017-05-26 10:30 | 52.37 | 51.89
2017-05-26 11:00 | 52.33 | 51.76
2017-05-26 11:30 | 52.4 | 51.75
2017-05-26 12:00 | 53.13 | 52.46
2017-05-26 12:30 | 53.78 | 53.09
2017-05-26 13:00 | 53.3 | 52.59
2017-05-26 13:30 | 53.1 | 52.35
2017-05-26 14:00 | 53.35 | 52.57
2017-05-26 14:30 | 52.91 | 51.95
2017-05-26 15:00 | 53.06 | 52.03
2017-05-26 15:30 | 52.54 | 51.17
2017-05-26 16:00 | 53.1 | 51.43
2017-05-26 16:30 | 55.03 | 53.18
2017-05-26 17:00 | 53.71 | 51.31
2017-05-26 17:30 | 56.31 | 49.34
2017-05-26 18:00 | 57.32 | 50.95
2017-05-26 18:30 | 58.63 | 52.55
2017-05-26 19:00 | 57.2 | 50.83
2017-05-26 19:30 | 54.87 | 48.03
2017-05-26 20:00 | 53.34 | 46.17
2017-05-26 20:30 | 51.67 | 44.04
2017-05-26 21:00 | 49.88 | 41.76
2017-05-26 21:30 | 44.12 | 39.79
2017-05-26 22:00 | 40.17 | 38.09
2017-05-26 22:30 | 38.48 | 36.23
2017-05-26 23:00 | 38.53 | 36.23
2017-05-26 23:30 | 35.44 | 32.85
2017-05-27 | 33.87 | 31.1
2017-05-27 00:30 | 32.74 | 30.04
2017-05-27 01:00 | 31.33 | 28.65
2017-05-27 01:30 | 19.95 | 15.61
2017-05-27 02:00 | 30.15 | 27.3
2017-05-27 02:30 | 29.95 | 27.07
2017-05-27 03:00 | 29.62 | 26.68
2017-05-27 03:30 | 29.21 | 26.19
2017-05-27 04:00 | 29.32 | 26.33
2017-05-27 04:30 | 29.65 | 26.71
2017-05-27 05:00 | 30.24 | 27.41
2017-05-27 05:30 | 31.44 | 28.8
2017-05-27 06:00 | 32.61 | 30.14
2017-05-27 06:30 | 34.3 | 32.01
2017-05-27 07:00 | 35.44 | 33.22
2017-05-27 07:30 | 38.07 | 36.07
2017-05-27 08:00 | 38.99 | 37.08
2017-05-27 08:30 | 40.73 | 38.99
2017-05-27 09:00 | 42.11 | 40.51
2017-05-27 09:30 | 41.22 | 39.62
2017-05-27 10:00 | 41.14 | 39.58
2017-05-27 10:30 | 42.43 | 40.75
2017-05-27 11:00 | 41.46 | 39.75
2017-05-27 11:30 | 40.99 | 39.27
2017-05-27 12:00 | 40.7 | 38.97
2017-05-27 12:30 | 40.54 | 39.53
2017-05-27 13:00 | 38.74 | 38.42
2017-05-27 13:30 | 37.97 | 37.66
2017-05-27 14:00 | 38.06 | 37.78
2017-05-27 14:30 | 37.91 | 37.66
2017-05-27 15:00 | 38.44 | 38.22
2017-05-27 15:30 | 38.73 | 38.55
2017-05-27 16:00 | 39.53 | 39.4
2017-05-27 16:30 | 40.98 | 40.9
2017-05-27 17:00 | 40.88 | 40.82
2017-05-27 17:30 | 42.79 | 42.73
2017-05-27 18:00 | 45.57 | 45.5
2017-05-27 18:30 | 46.21 | 46.14
2017-05-27 19:00 | 44.64 | 44.58
2017-05-27 19:30 | 42.74 | 42.68
2017-05-27 20:00 | 41.17 | 41.12
2017-05-27 20:30 | 39.03 | 38.99
2017-05-27 21:00 | 37.84 | 37.81
2017-05-27 21:30 | 36.41 | 36.38
2017-05-27 22:00 | 35.41 | 35.38
2017-05-27 22:30 | 34.32 | 34.29
2017-05-27 23:00 | 32.3 | 32.24
2017-05-27 23:30 | 29.33 | 29.17
2017-05-28 | 29.83 | 29.64
2017-05-28 00:30 | 29.33 | 29.14
2017-05-28 01:00 | 27.65 | 27.59
2017-05-28 01:30 | 26.89 | 26.83
2017-05-28 02:00 | 26.43 | 26.37
2017-05-28 02:30 | 26.18 | 26.13
2017-05-28 03:00 | 26.06 | 26.01
2017-05-28 03:30 | 26.04 | 25.99
2017-05-28 04:00 | 25.91 | 25.86
2017-05-28 04:30 | 26.08 | 26.03
2017-05-28 05:00 | 26.41 | 26.36
2017-05-28 05:30 | 26.89 | 26.83
2017-05-28 06:00 | 27.41 | 27.34
2017-05-28 06:30 | 28.62 | 28.55
2017-05-28 07:00 | 29.66 | 29.61
2017-05-28 07:30 | 30.88 | 30.82
2017-05-28 08:00 | 31.78 | 31.71
2017-05-28 08:30 | 32.9 | 32.8
2017-05-28 09:00 | 34.06 | 33.9
2017-05-28 09:30 | 35.02 | 34.73
2017-05-28 10:00 | 36.06 | 35.64
2017-05-28 10:30 | 36.59 | 36.41
2017-05-28 11:00 | 36.5 | 36.41
2017-05-28 11:30 | 35.69 | 35.59
2017-05-28 12:00 | 35.47 | 35.35
2017-05-28 12:30 | 35.54 | 35.45
2017-05-28 13:00 | 35.34 | 35.23
2017-05-28 13:30 | 34.96 | 34.85
2017-05-28 14:00 | 35.23 | 35.13
2017-05-28 14:30 | 35.31 | 35.23
2017-05-28 15:00 | 35.74 | 35.66
2017-05-28 15:30 | 36.43 | 36.37
2017-05-28 16:00 | 37.78 | 37.72
2017-05-28 16:30 | 39.85 | 39.8
2017-05-28 17:00 | 40.09 | 40.05
2017-05-28 17:30 | 42.39 | 42.34
2017-05-28 18:00 | 45.84 | 45.78
2017-05-28 18:30 | 47.66 | 47.6
2017-05-28 19:00 | 46.13 | 46.08
2017-05-28 19:30 | 43.2 | 43.16
2017-05-28 20:00 | 41.28 | 41.24
2017-05-28 20:30 | 39.34 | 39.3
2017-05-28 21:00 | 37.67 | 37.65
2017-05-28 21:30 | 35.87 | 35.84
2017-05-28 22:00 | 34.02 | 33.97
2017-05-28 22:30 | 32.94 | 32.88
2017-05-28 23:00 | 33.27 | 33.2
2017-05-28 23:30 | 30.1 | 30.02
2017-05-29 | 28.71 | 28.64
2017-05-29 00:30 | 28.23 | 28.16
2017-05-29 01:00 | 27.13 | 27.07
2017-05-29 01:30 | 26.44 | 26.38
2017-05-29 02:00 | 26.25 | 26.2
2017-05-29 02:30 | 26.28 | 26.22
2017-05-29 03:00 | 26.31 | 26.26
2017-05-29 03:30 | 26.35 | 26.29
2017-05-29 04:00 | 26.4 | 26.35
2017-05-29 04:30 | 26.95 | 26.9
2017-05-29 05:00 | 28.3 | 28.23
2017-05-29 05:30 | 30.91 | 30.81
2017-05-29 06:00 | 34.62 | 34.37
2017-05-29 06:30 | 39.56 | 39.06
2017-05-29 07:00 | 44 | 43.25
2017-05-29 07:30 | 51.23 | 48.45
2017-05-29 08:00 | 56.04 | 50.14
2017-05-29 08:30 | 56.73 | 51.13
2017-05-29 09:00 | 56.75 | 51.34
2017-05-29 09:30 | 56.96 | 51.47
2017-05-29 10:00 | 57.02 | 51.49
2017-05-29 10:30 | 57.86 | 52.35
2017-05-29 11:00 | 57.93 | 52.34
2017-05-29 11:30 | 58.3 | 52.72
2017-05-29 12:00 | 58.56 | 52.98
2017-05-29 12:30 | 58.83 | 53.32
2017-05-29 13:00 | 58.67 | 53.14
2017-05-29 13:30 | 59.07 | 53.47
2017-05-29 14:00 | 60.24 | 54.5
2017-05-29 14:30 | 61.13 | 55.49
2017-05-29 15:00 | 60.87 | 55.27
2017-05-29 15:30 | 59.12 | 53.36
2017-05-29 16:00 | 60.03 | 54.5
2017-05-29 16:30 | 59.94 | 54.87
2017-05-29 17:00 | 58.73 | 53.7
2017-05-29 17:30 | 58.4 | 53.45
2017-05-29 18:00 | 59.51 | 54.79
2017-05-29 18:30 | 59.16 | 54.46
2017-05-29 19:00 | 57.51 | 52.71
2017-05-29 19:30 | 54.3 | 49.24
2017-05-29 20:00 | 52.37 | 47.11
2017-05-29 20:30 | 50.05 | 44.6
2017-05-29 21:00 | 43.54 | 42.14
2017-05-29 21:30 | 40.94 | 40.36
2017-05-29 22:00 | 38.88 | 38.13
2017-05-29 22:30 | 36.72 | 35.85
2017-05-29 23:00 | 34.31 | 33.99
2017-05-29 23:30 | 33.06 | 32.63
2017-05-30 | 32.34 | 32.2
2017-05-30 00:30 | 30.7 | 30.66
2017-05-30 01:00 | 29.3 | 29.2
2017-05-30 01:30 | 28.5 | 28.39
2017-05-30 02:00 | 28.12 | 28.02
2017-05-30 02:30 | 27.52 | 27.43
2017-05-30 03:00 | 27.18 | 27.1
2017-05-30 03:30 | 27.22 | 27.14
2017-05-30 04:00 | 27.51 | 27.43
2017-05-30 04:30 | 28.18 | 28.09
2017-05-30 05:00 | 29.66 | 29.56
2017-05-30 05:30 | 32.49 | 32.29
2017-05-30 06:00 | 35.47 | 35.13
2017-05-30 06:30 | 41.06 | 40.34
2017-05-30 07:00 | 45.84 | 44.72
2017-05-30 07:30 | 52.08 | 50.57
2017-05-30 08:00 | 53.76 | 52.28
2017-05-30 08:30 | 55 | 53.67
2017-05-30 09:00 | 54.53 | 53.08
2017-05-30 09:30 | 55.03 | 53.55
2017-05-30 10:00 | 56.39 | 54.9
2017-05-30 10:30 | 56.33 | 54.8
2017-05-30 11:00 | 57.42 | 55.9
2017-05-30 11:30 | 56.69 | 55.09
2017-05-30 12:00 | 56.21 | 54.49
2017-05-30 12:30 | 65.92 | 54.95
2017-05-30 13:00 | 67.72 | 55.75
2017-05-30 13:30 | 64.28 | 57.01
2017-05-30 14:00 | 56.91 | 56.02
2017-05-30 14:30 | 57.45 | 56.56
2017-05-30 15:00 | 57.56 | 56.64
2017-05-30 15:30 | 56.65 | 55.62
2017-05-30 16:00 | 56.48 | 55.3
2017-05-30 16:30 | 55.92 | 54.26
2017-05-30 17:00 | 55.34 | 53.11
2017-05-30 17:30 | 55.49 | 52.7
2017-05-30 18:00 | 57.2 | 54.41
2017-05-30 18:30 | 57.77 | 54.62
2017-05-30 19:00 | 56.88 | 53.5
2017-05-30 19:30 | 54.16 | 50.3
2017-05-30 20:00 | 52.36 | 47.92
2017-05-30 20:30 | 50.71 | 45.66
2017-05-30 21:00 | 49.24 | 43.56
2017-05-30 21:30 | 47.93 | 41.59
2017-05-30 22:00 | 44.46 | 39.17
2017-05-30 22:30 | 39.45 | 36.68
2017-05-30 23:00 | 39.33 | 36.79
2017-05-30 23:30 | 36.16 | 33.4
2017-05-31 | 34.61 | 31.79
2017-05-31 00:30 | 33.57 | 31.09
2017-05-31 01:00 | 32.22 | 29.77
2017-05-31 01:30 | 31.74 | 29.25
2017-05-31 02:00 | 31.38 | 28.85
2017-05-31 02:30 | 31.01 | 28.41
2017-05-31 03:00 | 30.79 | 28.16
2017-05-31 03:30 | 30.76 | 28.12
2017-05-31 04:00 | 30.99 | 28.37
2017-05-31 04:30 | 31.66 | 29.13
2017-05-31 05:00 | 32.73 | 30.33
2017-05-31 05:30 | 34.97 | 32.83
2017-05-31 06:00 | 37.77 | 35.92
2017-05-31 06:30 | 42.01 | 41.08
2017-05-31 07:00 | 46.58 | 45.4
2017-05-31 07:30 | 55.59 | 50.49
2017-05-31 08:00 | 58.59 | 53.3
2017-05-31 08:30 | 59.92 | 54.87
2017-05-31 09:00 | 59.08 | 53.84
2017-05-31 09:30 | 58.68 | 53.29
2017-05-31 10:00 | 58.88 | 53.48
2017-05-31 10:30 | 59.45 | 54.03
2017-05-31 11:00 | 59.25 | 53.72
2017-05-31 11:30 | 58.82 | 53.15
2017-05-31 12:00 | 61.22 | 55.88
2017-05-31 12:30 | 60.65 | 55.27
2017-05-31 13:00 | 59.37 | 53.89
2017-05-31 13:30 | 59.3 | 53.75
2017-05-31 14:00 | 59.8 | 54.31
2017-05-31 14:30 | 60.76 | 55.38
2017-05-31 15:00 | 60.73 | 55.4
2017-05-31 15:30 | 59.63 | 54.24
2017-05-31 16:00 | 59.48 | 54.21
2017-05-31 16:30 | 58.91 | 53.75
2017-05-31 17:00 | 57.73 | 52.57
2017-05-31 17:30 | 57.57 | 52.55
2017-05-31 18:00 | 59.32 | 54.51
2017-05-31 18:30 | 59.04 | 54.29
2017-05-31 19:00 | 57.47 | 52.62
2017-05-31 19:30 | 54.8 | 49.7
2017-05-31 20:00 | 52.23 | 46.92
2017-05-31 20:30 | 47.54 | 44.34
2017-05-31 21:00 | 42.09 | 41.68
2017-05-31 21:30 | 40.72 | 40.18
2017-05-31 22:00 | 38.82 | 38.11
2017-05-31 22:30 | 37.8 | 37.04
2017-05-31 23:00 | 37.46 | 37.2
2017-05-31 23:30 | 33.81 | 33.4
2017-06-01 | 31.1 | 31
2017-06-01 00:30 | 30.14 | 30.08
2017-06-01 01:00 | 28.5 | 28.41
2017-06-01 01:30 | 27.93 | 27.83
2017-06-01 02:00 | 28.01 | 27.92
2017-06-01 02:30 | 27.64 | 27.55
2017-06-01 03:00 | 27.01 | 26.93
2017-06-01 03:30 | 26.84 | 26.77
2017-06-01 04:00 | 26.9 | 26.83
2017-06-01 04:30 | 27.78 | 27.7
2017-06-01 05:00 | 29.38 | 29.29
2017-06-01 05:30 | 31.85 | 31.7
2017-06-01 06:00 | 34.6 | 34.33
2017-06-01 06:30 | 39.96 | 39.39
2017-06-01 07:00 | 44.11 | 43.34
2017-06-01 07:30 | 49.88 | 49.57
2017-06-01 08:00 | 48.75 | 48.53
2017-06-01 08:30 | 40.66 | 39.33
2017-06-01 09:00 | 40.31 | 38.24
2017-06-01 09:30 | 39.55 | 36.61
2017-06-01 10:00 | 39.45 | 36.15
2017-06-01 10:30 | 38.87 | 35.52
2017-06-01 11:00 | 38.91 | 35.6
2017-06-01 11:30 | 40.32 | 37.19
2017-06-01 12:00 | 39.07 | 35.82
2017-06-01 12:30 | 38.43 | 35.11
2017-06-01 13:00 | 38.59 | 35.31
2017-06-01 13:30 | 39.62 | 36.44
2017-06-01 14:00 | 40.22 | 37.1
2017-06-01 14:30 | 40.12 | 36.98
2017-06-01 15:00 | 39.66 | 36.44
2017-06-01 15:30 | 43.32 | 40.35
2017-06-01 16:00 | 51.96 | 49.38
2017-06-01 16:30 | 52.27 | 49.2
2017-06-01 17:00 | 52.37 | 48.77
2017-06-01 17:30 | 53.3 | 49.16
2017-06-01 18:00 | 56.68 | 53.11
2017-06-01 18:30 | 57.76 | 54.03
2017-06-01 19:00 | 56.75 | 52.78
2017-06-01 19:30 | 54.98 | 50.62
2017-06-01 20:00 | 53.25 | 48.43
2017-06-01 20:30 | 51.82 | 46.52
2017-06-01 21:00 | 50.43 | 44.62
2017-06-01 21:30 | 49.97 | 42.01
2017-06-01 22:00 | 45.91 | 38.94
2017-06-01 22:30 | 38.99 | 36.17
2017-06-01 23:00 | 38.73 | 36.19
2017-06-01 23:30 | 35.51 | 32.64
2017-06-02 | 33.5 | 30.6
2017-06-02 00:30 | 32.4 | 29.55
2017-06-02 01:00 | 31.28 | 28.31
2017-06-02 01:30 | 30.35 | 27.66
2017-06-02 02:00 | 30.23 | 27.52
2017-06-02 02:30 | 30.3 | 27.56
2017-06-02 03:00 | 30.06 | 27.29
2017-06-02 03:30 | 29.93 | 27.1
2017-06-02 04:00 | 30.26 | 27.48
2017-06-02 04:30 | 30.88 | 28.23
2017-06-02 05:00 | 31.78 | 29.25
2017-06-02 05:30 | 33.93 | 31.65
2017-06-02 06:00 | 36.8 | 34.84
2017-06-02 06:30 | 41.93 | 40.1
2017-06-02 07:00 | 45.95 | 44.19
2017-06-02 07:30 | 51.03 | 49.55
2017-06-02 08:00 | 53.88 | 52.54
2017-06-02 08:30 | 54.19 | 52.9
2017-06-02 09:00 | 54.51 | 53.31
2017-06-02 09:30 | 54.27 | 53.04
2017-06-02 10:00 | 54.01 | 52.77
2017-06-02 10:30 | 52 | 50.7
2017-06-02 11:00 | 52.6 | 51.29
2017-06-02 11:30 | 51.59 | 50.24
2017-06-02 12:00 | 53.85 | 52.55
2017-06-02 12:30 | 54.69 | 53.43
2017-06-02 13:00 | 52.05 | 50.74
2017-06-02 13:30 | 52.33 | 51.04
2017-06-02 14:00 | 53.38 | 52.14
2017-06-02 14:30 | 51.96 | 50.71
2017-06-02 15:00 | 51.14 | 49.89
2017-06-02 15:30 | 50.79 | 49.58
2017-06-02 16:00 | 50.32 | 49.13
2017-06-02 16:30 | 51.16 | 50.03
2017-06-02 17:00 | 50.35 | 49.23
2017-06-02 17:30 | 50.63 | 49.56
2017-06-02 18:00 | 52.34 | 51.29
2017-06-02 18:30 | 52.35 | 51.34
2017-06-02 19:00 | 50.9 | 49.79
2017-06-02 19:30 | 48.44 | 47.21
2017-06-02 20:00 | 46.75 | 45.5
2017-06-02 20:30 | 45.03 | 43.76
2017-06-02 21:00 | 42.98 | 41.66
2017-06-02 21:30 | 41.15 | 39.81
2017-06-02 22:00 | 39.3 | 37.8
2017-06-02 22:30 | 38 | 36.4
2017-06-02 23:00 | 37.42 | 35.81
2017-06-02 23:30 | 34.45 | 32.51
2017-06-03 | 32.63 | 30.59
2017-06-03 00:30 | 31.56 | 29.48
2017-06-03 01:00 | 30.69 | 28.54
2017-06-03 01:30 | 30.14 | 27.95
2017-06-03 02:00 | 29.66 | 27.45
2017-06-03 02:30 | 29.72 | 27.52
2017-06-03 03:00 | 29.25 | 27.02
2017-06-03 03:30 | 28.96 | 26.72
2017-06-03 04:00 | 28.86 | 26.61
2017-06-03 04:30 | 29.38 | 27.16
2017-06-03 05:00 | 29.81 | 27.61
2017-06-03 05:30 | 30.68 | 28.54
2017-06-03 06:00 | 32.07 | 29.98
2017-06-03 06:30 | 34.31 | 32.31
2017-06-03 07:00 | 35.52 | 33.59
2017-06-03 07:30 | 37.01 | 35.14
2017-06-03 08:00 | 38.89 | 37.05
2017-06-03 08:30 | 40.45 | 38.63
2017-06-03 09:00 | 41.25 | 39.37
2017-06-03 09:30 | 40.65 | 38.74
2017-06-03 10:00 | 40.33 | 38.36
2017-06-03 10:30 | 40.09 | 38.08
2017-06-03 11:00 | 39.06 | 36.98
2017-06-03 11:30 | 38.6 | 36.49
2017-06-03 12:00 | 37.91 | 35.78
2017-06-03 12:30 | 37.21 | 35.06
2017-06-03 13:00 | 36.62 | 34.44
2017-06-03 13:30 | 36.11 | 33.91
2017-06-03 14:00 | 36.35 | 34.18
2017-06-03 14:30 | 36.41 | 34.28
2017-06-03 15:00 | 36.48 | 34.36
2017-06-03 15:30 | 36.61 | 34.55
2017-06-03 16:00 | 37.67 | 35.69
2017-06-03 16:30 | 39.88 | 38.03
2017-06-03 17:00 | 40.66 | 38.86
2017-06-03 17:30 | 42.37 | 40.67
2017-06-03 18:00 | 45.85 | 44.23
2017-06-03 18:30 | 47.05 | 45.47
2017-06-03 19:00 | 45.72 | 44.1
2017-06-03 19:30 | 43.57 | 41.87
2017-06-03 20:00 | 41.95 | 40.21
2017-06-03 20:30 | 40.23 | 38.44
2017-06-03 21:00 | 39.13 | 37.31
2017-06-03 21:30 | 37.78 | 35.92
2017-06-03 22:00 | 36.74 | 34.84
2017-06-03 22:30 | 35.81 | 33.89
2017-06-03 23:00 | 36.17 | 34.29
2017-06-03 23:30 | 33.43 | 31.41
2017-06-04 | 31.8 | 29.7
2017-06-04 00:30 | 31.43 | 29.33
2017-06-04 01:00 | 30.46 | 28.3
2017-06-04 01:30 | 29.71 | 27.49
2017-06-04 02:00 | 29.52 | 27.29
2017-06-04 02:30 | 29.3 | 27.05
2017-06-04 03:00 | 28.91 | 26.66
2017-06-04 03:30 | 28.81 | 26.56
2017-06-04 04:00 | 28.79 | 26.54
2017-06-04 04:30 | 28.76 | 26.5
2017-06-04 05:00 | 29.44 | 27.22
2017-06-04 05:30 | 29.95 | 27.76
2017-06-04 06:00 | 30.93 | 28.79
2017-06-04 06:30 | 31.98 | 29.93
2017-06-04 07:00 | 32.46 | 30.46
2017-06-04 07:30 | 34.17 | 32.24
2017-06-04 08:00 | 34.98 | 33.07
2017-06-04 08:30 | 35.36 | 33.45
2017-06-04 09:00 | 35.77 | 33.84
2017-06-04 09:30 | 36.16 | 34.22
2017-06-04 10:00 | 35.99 | 34
2017-06-04 10:30 | 36 | 33.97
2017-06-04 11:00 | 36.14 | 34.08
2017-06-04 11:30 | 36.05 | 33.96
2017-06-04 12:00 | 35.48 | 33.33
2017-06-04 12:30 | 37.41 | 35.39
2017-06-04 13:00 | 36.25 | 34.17
2017-06-04 13:30 | 35.4 | 33.26
2017-06-04 14:00 | 35.72 | 33.59
2017-06-04 14:30 | 35.72 | 33.61
2017-06-04 15:00 | 36.11 | 34.04
2017-06-04 15:30 | 36.99 | 34.97
2017-06-04 16:00 | 38.31 | 36.37
2017-06-04 16:30 | 40.53 | 38.73
2017-06-04 17:00 | 41.18 | 39.44
2017-06-04 17:30 | 43.77 | 42.12
2017-06-04 18:00 | 47.54 | 45.96
2017-06-04 18:30 | 49.23 | 47.71
2017-06-04 19:00 | 48.01 | 46.46
2017-06-04 19:30 | 45.41 | 43.78
2017-06-04 20:00 | 42.99 | 41.32
2017-06-04 20:30 | 40.98 | 39.26
2017-06-04 21:00 | 39.81 | 38.04
2017-06-04 21:30 | 38.2 | 36.38
2017-06-04 22:00 | 36.73 | 34.86
2017-06-04 22:30 | 35.46 | 33.53
2017-06-04 23:00 | 35.62 | 33.73
2017-06-04 23:30 | 32.91 | 30.87
2017-06-05 | 31.53 | 29.41
2017-06-05 00:30 | 31.03 | 28.9
2017-06-05 01:00 | 29.82 | 27.6
2017-06-05 01:30 | 29.72 | 27.5
2017-06-05 02:00 | 29.7 | 27.47
2017-06-05 02:30 | 29.45 | 27.23
2017-06-05 03:00 | 29.4 | 27.17
2017-06-05 03:30 | 29.36 | 27.12
2017-06-05 04:00 | 29.73 | 27.52
2017-06-05 04:30 | 30.61 | 28.44
2017-06-05 05:00 | 31.76 | 29.65
2017-06-05 05:30 | 34.39 | 32.38
2017-06-05 06:00 | 37.03 | 35.12
2017-06-05 06:30 | 41.98 | 40.21
2017-06-05 07:00 | 45.85 | 44.13
2017-06-05 07:30 | 50.15 | 48.73
2017-06-05 08:00 | 51.65 | 50.34
2017-06-05 08:30 | 51.46 | 50.06
2017-06-05 09:00 | 51.5 | 48.85
2017-06-05 09:30 | 50.53 | 47.92
2017-06-05 10:00 | 49.48 | 46.87
2017-06-05 10:30 | 49.94 | 47.44
2017-06-05 11:00 | 49.8 | 47.34
2017-06-05 11:30 | 49.52 | 47.08
2017-06-05 12:00 | 49.94 | 47.56
2017-06-05 12:30 | 50 | 47.6
2017-06-05 13:00 | 49.42 | 46.98
2017-06-05 13:30 | 49.34 | 46.92
2017-06-05 14:00 | 50.22 | 47.85
2017-06-05 14:30 | 50.59 | 48.24
2017-06-05 15:00 | 50.48 | 48.1
2017-06-05 15:30 | 50.91 | 48.47
2017-06-05 16:00 | 51.07 | 48.56
2017-06-05 16:30 | 52.66 | 50.02
2017-06-05 17:00 | 53.06 | 49.91
2017-06-05 17:30 | 54.28 | 50.6
2017-06-05 18:00 | 56.48 | 52.98
2017-06-05 18:30 | 56.42 | 53.35
2017-06-05 19:00 | 53.8 | 51.61
2017-06-05 19:30 | 50.89 | 48.52
2017-06-05 20:00 | 48.62 | 46.07
2017-06-05 20:30 | 46.62 | 43.89
2017-06-05 21:00 | 45.11 | 42.22
2017-06-05 21:30 | 43.15 | 40.02
2017-06-05 22:00 | 39.79 | 37.16
2017-06-05 22:30 | 37.59 | 35.33
2017-06-05 23:00 | 37.49 | 35.5
2017-06-05 23:30 | 34.49 | 32.26
2017-06-06 | 33.26 | 30.92
2017-06-06 00:30 | 32.55 | 30.1
2017-06-06 01:00 | 31.4 | 28.83
2017-06-06 01:30 | 30.75 | 28.1
2017-06-06 02:00 | 30.31 | 27.6
2017-06-06 02:30 | 29.99 | 27.22
2017-06-06 03:00 | 29.92 | 27.12
2017-06-06 03:30 | 29.77 | 26.92
2017-06-06 04:00 | 29.8 | 26.96
2017-06-06 04:30 | 30.52 | 27.78
2017-06-06 05:00 | 31.57 | 29.01
2017-06-06 05:30 | 33.92 | 31.64
2017-06-06 06:00 | 36.62 | 34.61
2017-06-06 06:30 | 41.62 | 39.85
2017-06-06 07:00 | 45.48 | 43.74
2017-06-06 07:30 | 51.17 | 49.64
2017-06-06 08:00 | 53.35 | 51.88
2017-06-06 08:30 | 53.57 | 52.08
2017-06-06 09:00 | 53.37 | 52.12
2017-06-06 09:30 | 53.28 | 52.04
2017-06-06 10:00 | 51.96 | 50.66
2017-06-06 10:30 | 50.83 | 49.46
2017-06-06 11:00 | 51.91 | 50.52
2017-06-06 11:30 | 51.94 | 50.53
2017-06-06 12:00 | 51.86 | 50.44
2017-06-06 12:30 | 50.48 | 49.05
2017-06-06 13:00 | 51.51 | 50.1
2017-06-06 13:30 | 51.31 | 49.9
2017-06-06 14:00 | 51.03 | 49.6
2017-06-06 14:30 | 51.44 | 50.05
2017-06-06 15:00 | 49.89 | 48.47
2017-06-06 15:30 | 48.65 | 47.22
2017-06-06 16:00 | 49.07 | 47.7
2017-06-06 16:30 | 50.04 | 48.79
2017-06-06 17:00 | 49.79 | 48.6
2017-06-06 17:30 | 50.12 | 49
2017-06-06 18:00 | 51.96 | 50.9
2017-06-06 18:30 | 53.23 | 52.22
2017-06-06 19:00 | 51.91 | 50.89
2017-06-06 19:30 | 48.98 | 47.92
2017-06-06 20:00 | 46.78 | 45.69
2017-06-06 20:30 | 44.71 | 43.6
2017-06-06 21:00 | 42.25 | 41.11
2017-06-06 21:30 | 40.14 | 38.69
2017-06-06 22:00 | 38.33 | 36.71
2017-06-06 22:30 | 36.41 | 34.72
2017-06-06 23:00 | 36.84 | 34.95
2017-06-06 23:30 | 33.49 | 31.43
2017-06-07 | 31.71 | 29.55
2017-06-07 00:30 | 30.96 | 28.75
2017-06-07 01:00 | 29.7 | 27.42
2017-06-07 01:30 | 28.99 | 26.66
2017-06-07 02:00 | 28.49 | 26.13
2017-06-07 02:30 | 28.29 | 25.93
2017-06-07 03:00 | 28.17 | 25.81
2017-06-07 03:30 | 28.02 | 25.64
2017-06-07 04:00 | 28.14 | 25.79
2017-06-07 04:30 | 28.71 | 26.4
2017-06-07 05:00 | 29.88 | 27.63
2017-06-07 05:30 | 32.69 | 30.6
2017-06-07 06:00 | 35.93 | 33.96
2017-06-07 06:30 | 41.46 | 39.64
2017-06-07 07:00 | 45.59 | 43.9
2017-06-07 07:30 | 49.69 | 48.22
2017-06-07 08:00 | 50.41 | 48.91
2017-06-07 08:30 | 49.88 | 48.76
2017-06-07 09:00 | 49.73 | 47.41
2017-06-07 09:30 | 48.69 | 45.74
2017-06-07 10:00 | 47.7 | 44.87
2017-06-07 10:30 | 47.68 | 44.95
2017-06-07 11:00 | 47.07 | 44.34
2017-06-07 11:30 | 47.04 | 44.36
2017-06-07 12:00 | 47.55 | 44.95
2017-06-07 12:30 | 48.06 | 45.46
2017-06-07 13:00 | 47.31 | 44.66
2017-06-07 13:30 | 46.97 | 44.65
2017-06-07 14:00 | 47.83 | 45.52
2017-06-07 14:30 | 49.48 | 47.12
2017-06-07 15:00 | 48.24 | 45.97
2017-06-07 15:30 | 48.51 | 46.23
2017-06-07 16:00 | 49.41 | 47.09
2017-06-07 16:30 | 51.15 | 48.34
2017-06-07 17:00 | 51.95 | 48.67
2017-06-07 17:30 | 52.91 | 49.08
2017-06-07 18:00 | 55.62 | 51.99
2017-06-07 18:30 | 57.12 | 53.52
2017-06-07 19:00 | 55.9 | 51.97
2017-06-07 19:30 | 53.4 | 49.02
2017-06-07 20:00 | 49.62 | 46.85
2017-06-07 20:30 | 47.52 | 44.89
2017-06-07 21:00 | 45.76 | 42.95
2017-06-07 21:30 | 43.72 | 40.66
2017-06-07 22:00 | 41.49 | 38.09
2017-06-07 22:30 | 38.51 | 35.77
2017-06-07 23:00 | 38.08 | 36.14
2017-06-07 23:30 | 35.21 | 33.04
2017-06-08 | 33.48 | 31.16
2017-06-08 00:30 | 32.88 | 30.46
2017-06-08 01:00 | 31.95 | 29.46
2017-06-08 01:30 | 31.08 | 28.49
2017-06-08 02:00 | 30.45 | 27.75
2017-06-08 02:30 | 30.11 | 27.33
2017-06-08 03:00 | 29.44 | 26.6
2017-06-08 03:30 | 29.57 | 26.73
2017-06-08 04:00 | 30.02 | 27.22
2017-06-08 04:30 | 30.7 | 28
2017-06-08 05:00 | 32.15 | 29.65
2017-06-08 05:30 | 34.45 | 32.19
2017-06-08 06:00 | 37.85 | 35.91
2017-06-08 06:30 | 43.83 | 42.12
2017-06-08 07:00 | 48.08 | 46.45
2017-06-08 07:30 | 52.93 | 51.54
2017-06-08 08:00 | 53.31 | 52.43
2017-06-08 08:30 | 53.03 | 52.79
2017-06-08 09:00 | 50.53 | 50.27
2017-06-08 09:30 | 47.68 | 47.66
2017-06-08 10:00 | 46.39 | 46.37
2017-06-08 10:30 | 45.74 | 45.68
2017-06-08 11:00 | 45.17 | 45.07
2017-06-08 11:30 | 44.88 | 44.77
2017-06-08 12:00 | 44.53 | 44.37
2017-06-08 12:30 | 44.65 | 44.52
2017-06-08 13:00 | 44.11 | 43.99
2017-06-08 13:30 | 44.52 | 44.36
2017-06-08 14:00 | 45.02 | 44.85
2017-06-08 14:30 | 45.66 | 45.51
2017-06-08 15:00 | 45.56 | 45.44
2017-06-08 15:30 | 45.44 | 45.37
2017-06-08 16:00 | 46.47 | 46.42
2017-06-08 16:30 | 47.97 | 47.94
2017-06-08 17:00 | 47.63 | 47.61
2017-06-08 17:30 | 48.83 | 48.76
2017-06-08 18:00 | 53.15 | 53.08
2017-06-08 18:30 | 55.21 | 55.13
2017-06-08 19:00 | 53.72 | 53.61
2017-06-08 19:30 | 50.92 | 50.72
2017-06-08 20:00 | 49.36 | 49.11
2017-06-08 20:30 | 47.46 | 47.34
2017-06-08 21:00 | 45.11 | 45.04
2017-06-08 21:30 | 42.13 | 42.07
2017-06-08 22:00 | 39.31 | 39.17
2017-06-08 22:30 | 37.73 | 37.49
2017-06-08 23:00 | 37.28 | 37.08
2017-06-08 23:30 | 33.94 | 33.77
2017-06-09 | 31.59 | 31.46
2017-06-09 00:30 | 31.06 | 30.96
2017-06-09 01:00 | 29.45 | 29.36
2017-06-09 01:30 | 28.86 | 28.79
2017-06-09 02:00 | 28.56 | 28.51
2017-06-09 02:30 | 28.05 | 28.03
2017-06-09 03:00 | 28.08 | 28.06
2017-06-09 03:30 | 28.5 | 28.47
2017-06-09 04:00 | 28.16 | 28.14
2017-06-09 04:30 | 28.71 | 28.69
2017-06-09 05:00 | 30.04 | 30
2017-06-09 05:30 | 33.09 | 33
2017-06-09 06:00 | 36.93 | 36.72
2017-06-09 06:30 | 42.85 | 42.35
2017-06-09 07:00 | 47.56 | 46.82
2017-06-09 07:30 | 52.89 | 52.72
2017-06-09 08:00 | 53.62 | 53.49
2017-06-09 08:30 | 52.3 | 52.1
2017-06-09 09:00 | 50.03 | 49.74
2017-06-09 09:30 | 47.89 | 47.57
2017-06-09 10:00 | 45.87 | 45.6
2017-06-09 10:30 | 45.4 | 45.35
2017-06-09 11:00 | 44.67 | 44.59
2017-06-09 11:30 | 43.97 | 43.88
2017-06-09 12:00 | 43.61 | 43.49
2017-06-09 12:30 | 44.13 | 44.02
2017-06-09 13:00 | 43.33 | 43.24
2017-06-09 13:30 | 43.16 | 43.06
2017-06-09 14:00 | 43.26 | 43.18
2017-06-09 14:30 | 43.07 | 43.02
2017-06-09 15:00 | 42.67 | 42.65
2017-06-09 15:30 | 42.51 | 42.5
2017-06-09 16:00 | 43.4 | 43.39
2017-06-09 16:30 | 45.59 | 45.55
2017-06-09 17:00 | 45.73 | 45.64
2017-06-09 17:30 | 46.59 | 46.39
2017-06-09 18:00 | 49.24 | 49.07
2017-06-09 18:30 | 49.73 | 49.54
2017-06-09 19:00 | 48.89 | 48.65
2017-06-09 19:30 | 46.33 | 46.31
2017-06-09 20:00 | 44.28 | 44.23
2017-06-09 20:30 | 42.32 | 42.22
2017-06-09 21:00 | 40.69 | 40.57
2017-06-09 21:30 | 38.64 | 38.63
2017-06-09 22:00 | 36.61 | 36.6
2017-06-09 22:30 | 35.12 | 35.09
2017-06-09 23:00 | 35.22 | 35.16
2017-06-09 23:30 | 32.28 | 32.23
2017-06-10 | 30.49 | 30.46
2017-06-10 00:30 | 30.19 | 30.16
2017-06-10 01:00 | 28.43 | 28.41
2017-06-10 01:30 | 28.11 | 28.09
2017-06-10 02:00 | 27.47 | 27.45
2017-06-10 02:30 | 27.51 | 27.49
2017-06-10 03:00 | 26.52 | 26.5
2017-06-10 03:30 | 26.31 | 26.29
2017-06-10 04:00 | 26.22 | 26.2
2017-06-10 04:30 | 26.77 | 26.75
2017-06-10 05:00 | 27.29 | 27.27
2017-06-10 05:30 | 29.02 | 29
2017-06-10 06:00 | 30.82 | 30.77
2017-06-10 06:30 | 33.04 | 32.95
2017-06-10 07:00 | 34.85 | 34.75
2017-06-10 07:30 | 38.16 | 38
2017-06-10 08:00 | 39.9 | 39.67
2017-06-10 08:30 | 41.81 | 41.5
2017-06-10 09:00 | 42.01 | 41.64
2017-06-10 09:30 | 41.97 | 41.55
2017-06-10 10:00 | 40.87 | 40.42
2017-06-10 10:30 | 39.31 | 38.8
2017-06-10 11:00 | 40.08 | 39.47
2017-06-10 11:30 | 38.34 | 37.71
2017-06-10 12:00 | 36.08 | 35.41
2017-06-10 12:30 | 35.9 | 35.3
2017-06-10 13:00 | 36.07 | 35.54
2017-06-10 13:30 | 36.15 | 35.63
2017-06-10 14:00 | 34.93 | 34.43
2017-06-10 14:30 | 34.97 | 34.48
2017-06-10 15:00 | 35.12 | 34.65
2017-06-10 15:30 | 35.22 | 34.8
2017-06-10 16:00 | 36.87 | 36.49
2017-06-10 16:30 | 38.6 | 38.29
2017-06-10 17:00 | 38.86 | 38.58
2017-06-10 17:30 | 40.74 | 40.5
2017-06-10 18:00 | 44.2 | 43.85
2017-06-10 18:30 | 45.05 | 44.68
2017-06-10 19:00 | 43.31 | 42.99
2017-06-10 19:30 | 41.04 | 40.74
2017-06-10 20:00 | 39.43 | 39.18
2017-06-10 20:30 | 37.7 | 37.49
2017-06-10 21:00 | 36.43 | 36.25
2017-06-10 21:30 | 35.07 | 34.94
2017-06-10 22:00 | 33.6 | 33.51
2017-06-10 22:30 | 32.76 | 32.68
2017-06-10 23:00 | 33.28 | 33.22
2017-06-10 23:30 | 30.35 | 30.32
2017-06-11 | 28.7 | 28.67
2017-06-11 00:30 | 28.4 | 28.37
2017-06-11 01:00 | 27.24 | 27.21
2017-06-11 01:30 | 26.36 | 26.33
2017-06-11 02:00 | 25.7 | 25.67
2017-06-11 02:30 | 25.52 | 25.49
2017-06-11 03:00 | 25.63 | 25.6
2017-06-11 03:30 | 25.61 | 25.58
2017-06-11 04:00 | 25.41 | 25.38
2017-06-11 04:30 | 25.73 | 25.7
2017-06-11 05:00 | 25.49 | 25.46
2017-06-11 05:30 | 26.44 | 26.41
2017-06-11 06:00 | 27.1 | 27.07
2017-06-11 06:30 | 28.48 | 28.45
2017-06-11 07:00 | 28.78 | 28.75
2017-06-11 07:30 | 30.14 | 30.11
2017-06-11 08:00 | 32.18 | 32.15
2017-06-11 08:30 | 35.02 | 34.97
2017-06-11 09:00 | 36.8 | 36.73
2017-06-11 09:30 | 38.41 | 38.3
2017-06-11 10:00 | 38.9 | 38.79
2017-06-11 10:30 | 39.66 | 39.5
2017-06-11 11:00 | 39.76 | 39.58
2017-06-11 11:30 | 38.97 | 38.77
2017-06-11 12:00 | 38.66 | 38.47
2017-06-11 12:30 | 39.58 | 39.4
2017-06-11 13:00 | 39.74 | 39.56
2017-06-11 13:30 | 39.48 | 39.3
2017-06-11 14:00 | 37.47 | 37.31
2017-06-11 14:30 | 37.45 | 37.29
2017-06-11 15:00 | 38.02 | 37.86
2017-06-11 15:30 | 37.42 | 37.28
2017-06-11 16:00 | 38.11 | 37.99
2017-06-11 16:30 | 40.27 | 40.13
2017-06-11 17:00 | 40.67 | 40.52
2017-06-11 17:30 | 43.77 | 43.54
2017-06-11 18:00 | 47.56 | 47.17
2017-06-11 18:30 | 48.77 | 47.15
2017-06-11 19:00 | 47.36 | 45.68
2017-06-11 19:30 | 44.79 | 43.03
2017-06-11 20:00 | 42.54 | 40.71
2017-06-11 20:30 | 40.34 | 38.32
2017-06-11 21:00 | 39.32 | 37.22
2017-06-11 21:30 | 37.54 | 35.28
2017-06-11 22:00 | 35.93 | 33.49
2017-06-11 22:30 | 34.43 | 31.87
2017-06-11 23:00 | 34.91 | 32.38
2017-06-11 23:30 | 32.29 | 29.47
2017-06-12 | 30.81 | 27.79
2017-06-12 00:30 | 30.64 | 27.57
2017-06-12 01:00 | 29.43 | 26.22
2017-06-12 01:30 | 29.05 | 25.81
2017-06-12 02:00 | 29.31 | 26.07
2017-06-12 02:30 | 29.36 | 26.12
2017-06-12 03:00 | 29.1 | 25.85
2017-06-12 03:30 | 28.99 | 25.71
2017-06-12 04:00 | 28.86 | 25.56
2017-06-12 04:30 | 29.41 | 26.22
2017-06-12 05:00 | 30.79 | 27.82
2017-06-12 05:30 | 33.24 | 30.64
2017-06-12 06:00 | 36.27 | 34.01
2017-06-12 06:30 | 40.78 | 38.96
2017-06-12 07:00 | 44.27 | 42.72
2017-06-12 07:30 | 50.11 | 48.73
2017-06-12 08:00 | 52.6 | 51.31
2017-06-12 08:30 | 53.63 | 52.34
2017-06-12 09:00 | 53.02 | 51.42
2017-06-12 09:30 | 51.65 | 50
2017-06-12 10:00 | 50.64 | 48.99
2017-06-12 10:30 | 49.08 | 48.4
2017-06-12 11:00 | 48.37 | 48.21
2017-06-12 11:30 | 49.39 | 49.17
2017-06-12 12:00 | 50.62 | 50.37
2017-06-12 12:30 | 50.14 | 49.93
2017-06-12 13:00 | 49.15 | 48.93
2017-06-12 13:30 | 48.85 | 48.59
2017-06-12 14:00 | 48.97 | 48.72
2017-06-12 14:30 | 49.09 | 48.86
2017-06-12 15:00 | 47.88 | 47.69
2017-06-12 15:30 | 48.08 | 47.97
2017-06-12 16:00 | 48.71 | 48.66
2017-06-12 16:30 | 49.01 | 48.99
2017-06-12 17:00 | 48.78 | 48.76
2017-06-12 17:30 | 49.06 | 49
2017-06-12 18:00 | 51.97 | 51.91
2017-06-12 18:30 | 52.94 | 52.86
2017-06-12 19:00 | 50.71 | 50.58
2017-06-12 19:30 | 48.56 | 48.37
2017-06-12 20:00 | 46.69 | 46.43
2017-06-12 20:30 | 44.58 | 44.22
2017-06-12 21:00 | 42.58 | 42.13
2017-06-12 21:30 | 40.64 | 40.03
2017-06-12 22:00 | 38.57 | 37.72
2017-06-12 22:30 | 37.16 | 36.15
2017-06-12 23:00 | 35.91 | 35.76
2017-06-12 23:30 | 33.34 | 33.31
2017-06-13 | 30.56 | 30.51
2017-06-13 00:30 | 29.96 | 29.89
2017-06-13 01:00 | 28.78 | 28.69
2017-06-13 01:30 | 28.16 | 28.06
2017-06-13 02:00 | 27.05 | 26.98
2017-06-13 02:30 | 26.46 | 26.38
2017-06-13 03:00 | 25.91 | 25.85
2017-06-13 03:30 | 26.24 | 26.17
2017-06-13 04:00 | 27.85 | 27.79
2017-06-13 04:30 | 27.82 | 27.76
2017-06-13 05:00 | 29.01 | 28.94
2017-06-13 05:30 | 31.42 | 31.31
2017-06-13 06:00 | 34.59 | 34.38
2017-06-13 06:30 | 40.13 | 39.65
2017-06-13 07:00 | 44.55 | 43.83
2017-06-13 07:30 | 49.42 | 48.88
2017-06-13 08:00 | 50.7 | 50.1
2017-06-13 08:30 | 50.44 | 50.09
2017-06-13 09:00 | 48.96 | 48.58
2017-06-13 09:30 | 47.36 | 47.24
2017-06-13 10:00 | 46.65 | 46.59
2017-06-13 10:30 | 47.26 | 47.15
2017-06-13 11:00 | 46.84 | 46.67
2017-06-13 11:30 | 46.2 | 46.01
2017-06-13 12:00 | 46.19 | 45.98
2017-06-13 12:30 | 46.73 | 46.51
2017-06-13 13:00 | 46.54 | 46.33
2017-06-13 13:30 | 46.9 | 46.65
2017-06-13 14:00 | 47.26 | 46.99
2017-06-13 14:30 | 47.17 | 46.93
2017-06-13 15:00 | 46.87 | 46.69
2017-06-13 15:30 | 48.21 | 48.07
2017-06-13 16:00 | 50.07 | 50.01
2017-06-13 16:30 | 51.3 | 51.27
2017-06-13 17:00 | 50.52 | 50.51
2017-06-13 17:30 | 51.62 | 51.57
2017-06-13 18:00 | 53.42 | 53.38
2017-06-13 18:30 | 53.93 | 53.86
2017-06-13 19:00 | 52.57 | 52.47
2017-06-13 19:30 | 48.89 | 48.71
2017-06-13 20:00 | 46.73 | 46.48
2017-06-13 20:30 | 45.15 | 44.8
2017-06-13 21:00 | 43 | 42.52
2017-06-13 21:30 | 40.93 | 40.32
2017-06-13 22:00 | 38.64 | 37.77
2017-06-13 22:30 | 36.83 | 36.08
2017-06-13 23:00 | 36.37 | 36.05
2017-06-13 23:30 | 33.12 | 32.68
2017-06-14 | 30.95 | 30.86
2017-06-14 00:30 | 29.88 | 29.8
2017-06-14 01:00 | 28.67 | 28.58
2017-06-14 01:30 | 27.71 | 27.6
2017-06-14 02:00 | 27.25 | 27.13
2017-06-14 02:30 | 26.63 | 26.56
2017-06-14 03:00 | 26.08 | 26.03
2017-06-14 03:30 | 26.2 | 26.15
2017-06-14 04:00 | 26.88 | 26.82
2017-06-14 04:30 | 27.46 | 27.39
2017-06-14 05:00 | 28.66 | 28.58
2017-06-14 05:30 | 31.51 | 31.4
2017-06-14 06:00 | 34.9 | 34.71
2017-06-14 06:30 | 40.65 | 40.16
2017-06-14 07:00 | 45.69 | 44.93
2017-06-14 07:30 | 52.21 | 51.78
2017-06-14 08:00 | 53.85 | 53.21
2017-06-14 08:30 | 53.7 | 53.33
2017-06-14 09:00 | 52.64 | 52.22
2017-06-14 09:30 | 50.94 | 50.76
2017-06-14 10:00 | 49.04 | 48.94
2017-06-14 10:30 | 48.57 | 48.43
2017-06-14 11:00 | 48.36 | 48.16
2017-06-14 11:30 | 50.59 | 50.36
2017-06-14 12:00 | 49.38 | 49.12
2017-06-14 12:30 | 48.76 | 48.6
2017-06-14 13:00 | 49.59 | 49.46
2017-06-14 13:30 | 48.91 | 48.76
2017-06-14 14:00 | 49.98 | 49.81
2017-06-14 14:30 | 49.65 | 49.47
2017-06-14 15:00 | 48.55 | 48.36
2017-06-14 15:30 | 49.17 | 49
2017-06-14 16:00 | 49.24 | 49.14
2017-06-14 16:30 | 50.21 | 50.17
2017-06-14 17:00 | 49.54 | 49.52
2017-06-14 17:30 | 50.2 | 50.14
2017-06-14 18:00 | 52.81 | 52.76
2017-06-14 18:30 | 54.09 | 54.04
2017-06-14 19:00 | 52.88 | 52.79
2017-06-14 19:30 | 49.38 | 49.23
2017-06-14 20:00 | 47.23 | 47.02
2017-06-14 20:30 | 45.34 | 45.05
2017-06-14 21:00 | 43.59 | 43.22
2017-06-14 21:30 | 41.1 | 40.56
2017-06-14 22:00 | 39.2 | 38.46
2017-06-14 22:30 | 37.63 | 36.74
2017-06-14 23:00 | 36.78 | 36.17
2017-06-14 23:30 | 33.09 | 32.84
2017-06-15 | 30.56 | 30.51
2017-06-15 00:30 | 29.7 | 29.63
2017-06-15 01:00 | 28.13 | 28.04
2017-06-15 01:30 | 27.73 | 27.62
2017-06-15 02:00 | 27.15 | 27.02
2017-06-15 02:30 | 26.69 | 26.59
2017-06-15 03:00 | 26.25 | 26.18
2017-06-15 03:30 | 26.15 | 26.09
2017-06-15 04:00 | 26.73 | 26.66
2017-06-15 04:30 | 27.54 | 27.46
2017-06-15 05:00 | 28.94 | 28.84
2017-06-15 05:30 | 31.4 | 31.24
2017-06-15 06:00 | 34.92 | 34.64
2017-06-15 06:30 | 40.51 | 39.93
2017-06-15 07:00 | 45.2 | 44.48
2017-06-15 07:30 | 51.47 | 51.02
2017-06-15 08:00 | 54.08 | 53.8
2017-06-15 08:30 | 53.44 | 53.03
2017-06-15 09:00 | 51.32 | 51.07
2017-06-15 09:30 | 49.4 | 49.32
2017-06-15 10:00 | 48.54 | 48.39
2017-06-15 10:30 | 48.83 | 48.63
2017-06-15 11:00 | 49.22 | 48.91
2017-06-15 11:30 | 49.13 | 48.81
2017-06-15 12:00 | 49.13 | 48.77
2017-06-15 12:30 | 49.38 | 49.04
2017-06-15 13:00 | 48.84 | 48.48
2017-06-15 13:30 | 49.1 | 48.71
2017-06-15 14:00 | 49.66 | 49.26
2017-06-15 14:30 | 49.93 | 49.56
2017-06-15 15:00 | 49.91 | 49.6
2017-06-15 15:30 | 50.38 | 50.1
2017-06-15 16:00 | 50.55 | 50.39
2017-06-15 16:30 | 50.87 | 50.81
2017-06-15 17:00 | 50.49 | 50.46
2017-06-15 17:30 | 50.45 | 50.43
2017-06-15 18:00 | 53.02 | 53
2017-06-15 18:30 | 55 | 54.97
2017-06-15 19:00 | 53.53 | 53.48
2017-06-15 19:30 | 50.29 | 50.19
2017-06-15 20:00 | 48.36 | 48.24
2017-06-15 20:30 | 46.62 | 46.42
2017-06-15 21:00 | 44.89 | 44.59
2017-06-15 21:30 | 42.29 | 41.85
2017-06-15 22:00 | 39.29 | 39.16
2017-06-15 22:30 | 37.5 | 37.45
2017-06-15 23:00 | 37.19 | 37.16
2017-06-15 23:30 | 33.92 | 33.9
2017-06-16 | 31.87 | 31.77
2017-06-16 00:30 | 30.84 | 30.71
2017-06-16 01:00 | 29.23 | 29.11
2017-06-16 01:30 | 28.67 | 28.56
2017-06-16 02:00 | 27.69 | 27.59
2017-06-16 02:30 | 27.02 | 26.94
2017-06-16 03:00 | 26.77 | 26.7
2017-06-16 03:30 | 26.75 | 26.68
2017-06-16 04:00 | 26.88 | 26.81
2017-06-16 04:30 | 27.71 | 27.63
2017-06-16 05:00 | 29.38 | 29.25
2017-06-16 05:30 | 32.05 | 31.84
2017-06-16 06:00 | 35.57 | 35.17
2017-06-16 06:30 | 41.31 | 40.56
2017-06-16 07:00 | 45.42 | 44.71
2017-06-16 07:30 | 50.25 | 49.97
2017-06-16 08:00 | 51.1 | 50.84
2017-06-16 08:30 | 52.19 | 51.84
2017-06-16 09:00 | 52.09 | 51.93
2017-06-16 09:30 | 50.58 | 50.38
2017-06-16 10:00 | 49.94 | 49.71
2017-06-16 10:30 | 49.8 | 49.48
2017-06-16 11:00 | 51.13 | 50.76
2017-06-16 11:30 | 50.52 | 50.15
2017-06-16 12:00 | 49.71 | 49.32
2017-06-16 12:30 | 50.17 | 49.77
2017-06-16 13:00 | 50.36 | 49.96
2017-06-16 13:30 | 49.96 | 49.59
2017-06-16 14:00 | 49.74 | 49.4
2017-06-16 14:30 | 48.58 | 48.33
2017-06-16 15:00 | 48.53 | 48.33
2017-06-16 15:30 | 48.41 | 48.28
2017-06-16 16:00 | 48.82 | 48.75
2017-06-16 16:30 | 50.42 | 50.39
2017-06-16 17:00 | 49.52 | 49.5
2017-06-16 17:30 | 49.68 | 49.64
2017-06-16 18:00 | 51.71 | 51.66
2017-06-16 18:30 | 51.82 | 51.77
2017-06-16 19:00 | 50.54 | 50.46
2017-06-16 19:30 | 47.96 | 47.8
2017-06-16 20:00 | 45.79 | 45.55
2017-06-16 20:30 | 43.33 | 42.99
2017-06-16 21:00 | 42.07 | 41.62
2017-06-16 21:30 | 39.6 | 39.47
2017-06-16 22:00 | 37.55 | 37.51
2017-06-16 22:30 | 36 | 35.98
2017-06-16 23:00 | 36.22 | 36.19
2017-06-16 23:30 | 33.31 | 33.28
2017-06-17 | 30.92 | 30.84
2017-06-17 00:30 | 30.11 | 30.02
2017-06-17 01:00 | 28.51 | 28.43
2017-06-17 01:30 | 27.92 | 27.84
2017-06-17 02:00 | 27.58 | 27.51
2017-06-17 02:30 | 27.19 | 27.12
2017-06-17 03:00 | 26.62 | 26.56
2017-06-17 03:30 | 26.29 | 26.23
2017-06-17 04:00 | 26.39 | 26.33
2017-06-17 04:30 | 26.88 | 26.82
2017-06-17 05:00 | 27.21 | 27.14
2017-06-17 05:30 | 28.79 | 28.71
2017-06-17 06:00 | 30.24 | 30.13
2017-06-17 06:30 | 31.74 | 31.6
2017-06-17 07:00 | 33.05 | 32.91
2017-06-17 07:30 | 35.8 | 35.6
2017-06-17 08:00 | 37.86 | 37.5
2017-06-17 08:30 | 39.49 | 39.01
2017-06-17 09:00 | 40.44 | 39.79
2017-06-17 09:30 | 40.32 | 39.55
2017-06-17 10:00 | 39.97 | 39.09
2017-06-17 10:30 | 39.93 | 39.47
2017-06-17 11:00 | 39.47 | 39.14
2017-06-17 11:30 | 38.33 | 37.98
2017-06-17 12:00 | 37.54 | 37.16
2017-06-17 12:30 | 36.15 | 35.88
2017-06-17 13:00 | 35.6 | 35.36
2017-06-17 13:30 | 34.73 | 34.52
2017-06-17 14:00 | 34.61 | 34.43
2017-06-17 14:30 | 34.63 | 34.5
2017-06-17 15:00 | 35.39 | 35.28
2017-06-17 15:30 | 36.25 | 36.17
2017-06-17 16:00 | 37.26 | 37.17
2017-06-17 16:30 | 39.11 | 39.03
2017-06-17 17:00 | 39.76 | 39.7
2017-06-17 17:30 | 41.82 | 41.76
2017-06-17 18:00 | 44.56 | 44.49
2017-06-17 18:30 | 45.79 | 45.7
2017-06-17 19:00 | 44.24 | 44.17
2017-06-17 19:30 | 41.74 | 41.67
2017-06-17 20:00 | 39.93 | 39.88
2017-06-17 20:30 | 38.26 | 38.22
2017-06-17 21:00 | 36.57 | 36.53
2017-06-17 21:30 | 35.27 | 35.24
2017-06-17 22:00 | 34.18 | 34.15
2017-06-17 22:30 | 33.05 | 33.02
2017-06-17 23:00 | 33.77 | 33.73
2017-06-17 23:30 | 30.29 | 30.2
2017-06-18 | 29.08 | 28.94
2017-06-18 00:30 | 28.58 | 28.4
2017-06-18 01:00 | 27.17 | 26.97
2017-06-18 01:30 | 26.58 | 26.36
2017-06-18 02:00 | 26.22 | 25.98
2017-06-18 02:30 | 26.11 | 25.84
2017-06-18 03:00 | 25.95 | 25.67
2017-06-18 03:30 | 25.59 | 25.29
2017-06-18 04:00 | 25.93 | 25.62
2017-06-18 04:30 | 26.08 | 25.76
2017-06-18 05:00 | 26.16 | 25.85
2017-06-18 05:30 | 26.94 | 26.68
2017-06-18 06:00 | 27.77 | 27.57
2017-06-18 06:30 | 28.2 | 28
2017-06-18 07:00 | 28.99 | 28.77
2017-06-18 07:30 | 30.49 | 30.31
2017-06-18 08:00 | 31.7 | 31.58
2017-06-18 08:30 | 32.92 | 32.85
2017-06-18 09:00 | 33.51 | 33.48
2017-06-18 09:30 | 33.78 | 33.75
2017-06-18 10:00 | 34.31 | 34.27
2017-06-18 10:30 | 33.83 | 33.78
2017-06-18 11:00 | 33.42 | 33.36
2017-06-18 11:30 | 33.07 | 33
2017-06-18 12:00 | 32.83 | 32.75
2017-06-18 12:30 | 33.35 | 33.27
2017-06-18 13:00 | 32.52 | 32.43
2017-06-18 13:30 | 32.55 | 32.47
2017-06-18 14:00 | 32.86 | 32.77
2017-06-18 14:30 | 32.73 | 32.66
2017-06-18 15:00 | 33.32 | 33.25
2017-06-18 15:30 | 33.51 | 33.45
2017-06-18 16:00 | 34.95 | 34.91
2017-06-18 16:30 | 37.93 | 37.89
2017-06-18 17:00 | 38.13 | 38.09
2017-06-18 17:30 | 40.72 | 40.68
2017-06-18 18:00 | 44.58 | 44.52
2017-06-18 18:30 | 45.26 | 45.2
2017-06-18 19:00 | 45.52 | 45.47
2017-06-18 19:30 | 42.67 | 42.62
2017-06-18 20:00 | 40.21 | 40.17
2017-06-18 20:30 | 39 | 38.96
2017-06-18 21:00 | 37.44 | 37.41
2017-06-18 21:30 | 35.15 | 35.12
2017-06-18 22:00 | 34 | 33.97
2017-06-18 22:30 | 32.07 | 32.03
2017-06-18 23:00 | 32.17 | 32.12
2017-06-18 23:30 | 29.68 | 29.59
2017-06-19 | 27.95 | 27.87
2017-06-19 00:30 | 27.87 | 27.81
2017-06-19 01:00 | 26.74 | 26.67
2017-06-19 01:30 | 26.51 | 26.45
2017-06-19 02:00 | 26.66 | 26.59
2017-06-19 02:30 | 26.27 | 26.2
2017-06-19 03:00 | 26.12 | 26.05
2017-06-19 03:30 | 26.43 | 26.36
2017-06-19 04:00 | 26.62 | 26.56
2017-06-19 04:30 | 27.29 | 27.23
2017-06-19 05:00 | 28.18 | 28.09
2017-06-19 05:30 | 31.09 | 30.96
2017-06-19 06:00 | 34.56 | 34.26
2017-06-19 06:30 | 39.63 | 39.11
2017-06-19 07:00 | 44.09 | 43.33
2017-06-19 07:30 | 48.52 | 48.37
2017-06-19 08:00 | 50.9 | 50.76
2017-06-19 08:30 | 51.08 | 50.78
2017-06-19 09:00 | 50.39 | 50.24
2017-06-19 09:30 | 48.42 | 48.34
2017-06-19 10:00 | 48.15 | 48.05
2017-06-19 10:30 | 48.87 | 48.67
2017-06-19 11:00 | 48.67 | 48.38
2017-06-19 11:30 | 48.65 | 48.3
2017-06-19 12:00 | 48.83 | 48.44
2017-06-19 12:30 | 48.98 | 48.59
2017-06-19 13:00 | 48.85 | 48.45
2017-06-19 13:30 | 49.19 | 48.8
2017-06-19 14:00 | 49 | 48.59
2017-06-19 14:30 | 48.81 | 48.39
2017-06-19 15:00 | 48.63 | 48.26
2017-06-19 15:30 | 48.51 | 48.25
2017-06-19 16:00 | 48.44 | 48.32
2017-06-19 16:30 | 49.45 | 49.4
2017-06-19 17:00 | 49.84 | 49.82
2017-06-19 17:30 | 49.52 | 49.49
2017-06-19 18:00 | 51.77 | 51.75
2017-06-19 18:30 | 52.87 | 52.82
2017-06-19 19:00 | 52.01 | 51.94
2017-06-19 19:30 | 49.02 | 48.9
2017-06-19 20:00 | 46.64 | 46.46
2017-06-19 20:30 | 44.72 | 44.44
2017-06-19 21:00 | 42.56 | 42.16
2017-06-19 21:30 | 40.14 | 39.54
2017-06-19 22:00 | 38.31 | 37.56
2017-06-19 22:30 | 36.68 | 35.79
2017-06-19 23:00 | 36.65 | 35.64
2017-06-19 23:30 | 32.76 | 32.11
2017-06-20 | 30.82 | 30.34
2017-06-20 00:30 | 30.42 | 29.82
2017-06-20 01:00 | 28.23 | 28.06
2017-06-20 01:30 | 28.26 | 28.15
2017-06-20 02:00 | 27.55 | 27.45
2017-06-20 02:30 | 26.75 | 26.66
2017-06-20 03:00 | 26.18 | 26.11
2017-06-20 03:30 | 26.82 | 26.75
2017-06-20 04:00 | 27.11 | 27.04
2017-06-20 04:30 | 28 | 27.91
2017-06-20 05:00 | 29.12 | 29.02
2017-06-20 05:30 | 31.87 | 31.7
2017-06-20 06:00 | 35.15 | 34.85
2017-06-20 06:30 | 40.55 | 39.92
2017-06-20 07:00 | 44.62 | 44.21
2017-06-20 07:30 | 50.18 | 50.09
2017-06-20 08:00 | 51.14 | 50.95
2017-06-20 08:30 | 51.63 | 51.29
2017-06-20 09:00 | 50.59 | 50.39
2017-06-20 09:30 | 49.32 | 49.23
2017-06-20 10:00 | 48.17 | 48.07
2017-06-20 10:30 | 48.66 | 48.44
2017-06-20 11:00 | 48.45 | 48.18
2017-06-20 11:30 | 48.22 | 47.89
2017-06-20 12:00 | 48.35 | 47.98
2017-06-20 12:30 | 49.5 | 49.16
2017-06-20 13:00 | 48.5 | 48.25
2017-06-20 13:30 | 48.48 | 48.18
2017-06-20 14:00 | 49.04 | 48.71
2017-06-20 14:30 | 47.8 | 47.5
2017-06-20 15:00 | 47.04 | 46.78
2017-06-20 15:30 | 47.23 | 47.07
2017-06-20 16:00 | 48.34 | 48.26
2017-06-20 16:30 | 50.23 | 50.18
2017-06-20 17:00 | 49.87 | 49.84
2017-06-20 17:30 | 49.89 | 49.86
2017-06-20 18:00 | 51.5 | 51.47
2017-06-20 18:30 | 52.85 | 52.81
2017-06-20 19:00 | 51.59 | 51.52
2017-06-20 19:30 | 48.83 | 48.73
2017-06-20 20:00 | 47 | 46.87
2017-06-20 20:30 | 44.7 | 44.46
2017-06-20 21:00 | 43.15 | 42.85
2017-06-20 21:30 | 41.52 | 41.13
2017-06-20 22:00 | 39.2 | 38.6
2017-06-20 22:30 | 37.83 | 37.08
2017-06-20 23:00 | 37.65 | 36.79
2017-06-20 23:30 | 34.46 | 33.34
2017-06-21 | 31.39 | 30.68
2017-06-21 00:30 | 30.94 | 30.41
2017-06-21 01:00 | 29.39 | 28.84
2017-06-21 01:30 | 28.73 | 28.16
2017-06-21 02:00 | 28.37 | 27.75
2017-06-21 02:30 | 27.69 | 27.55
2017-06-21 03:00 | 27.47 | 27.39
2017-06-21 03:30 | 27.43 | 27.35
2017-06-21 04:00 | 27.44 | 27.35
2017-06-21 04:30 | 28.85 | 28.76
2017-06-21 05:00 | 29.72 | 29.62
2017-06-21 05:30 | 32.34 | 32.16
2017-06-21 06:00 | 34.95 | 34.63
2017-06-21 06:30 | 41.13 | 40.43
2017-06-21 07:00 | 44.86 | 44.56
2017-06-21 07:30 | 49.22 | 49.12
2017-06-21 08:00 | 50.75 | 50.54
2017-06-21 08:30 | 51.24 | 50.87
2017-06-21 09:00 | 50.52 | 50.36
2017-06-21 09:30 | 49.18 | 49.07
2017-06-21 10:00 | 49.25 | 49.1
2017-06-21 10:30 | 49.18 | 48.96
2017-06-21 11:00 | 48.37 | 48.08
2017-06-21 11:30 | 48.35 | 48
2017-06-21 12:00 | 48.26 | 47.89
2017-06-21 12:30 | 48.42 | 48.05
2017-06-21 13:00 | 47.43 | 47.1
2017-06-21 13:30 | 47.32 | 46.99
2017-06-21 14:00 | 48.15 | 47.79
2017-06-21 14:30 | 47.42 | 47.13
2017-06-21 15:00 | 47.29 | 47.08
2017-06-21 15:30 | 48.24 | 48.08
2017-06-21 16:00 | 48.19 | 48.09
2017-06-21 16:30 | 49.39 | 49.34
2017-06-21 17:00 | 49.76 | 49.73
2017-06-21 17:30 | 49.89 | 49.87
2017-06-21 18:00 | 50.95 | 50.93
2017-06-21 18:30 | 52.22 | 52.18
2017-06-21 19:00 | 51.1 | 51.04
2017-06-21 19:30 | 47.61 | 47.49
2017-06-21 20:00 | 45.6 | 45.45
2017-06-21 20:30 | 43.66 | 43.4
2017-06-21 21:00 | 41.36 | 40.98
2017-06-21 21:30 | 40.11 | 39.65
2017-06-21 22:00 | 38.59 | 37.97
2017-06-21 22:30 | 37.77 | 37.05
2017-06-21 23:00 | 37.24 | 37.19
2017-06-21 23:30 | 34.14 | 34.02
2017-06-22 | 32.29 | 32.06
2017-06-22 00:30 | 30.8 | 30.64
2017-06-22 01:00 | 29.56 | 29.42
2017-06-22 01:30 | 28.64 | 28.49
2017-06-22 02:00 | 27.82 | 27.7
2017-06-22 02:30 | 27.7 | 27.58
2017-06-22 03:00 | 27.04 | 26.93
2017-06-22 03:30 | 27.57 | 27.48
2017-06-22 04:00 | 27.6 | 27.5
2017-06-22 04:30 | 27.2 | 27.11
2017-06-22 05:00 | 28.1 | 28
2017-06-22 05:30 | 29.68 | 29.52
2017-06-22 06:00 | 30.66 | 30.46
2017-06-22 06:30 | 33.45 | 33.15
2017-06-22 07:00 | 35.07 | 34.77
2017-06-22 07:30 | 37.05 | 36.72
2017-06-22 08:00 | 38.14 | 37.71
2017-06-22 08:30 | 40.29 | 39.69
2017-06-22 09:00 | 40.83 | 40.06
2017-06-22 09:30 | 40.22 | 39.4
2017-06-22 10:00 | 40.41 | 39.38
2017-06-22 10:30 | 40.07 | 38.93
2017-06-22 11:00 | 39.75 | 38.42
2017-06-22 11:30 | 38.73 | 37.34
2017-06-22 12:00 | 38.02 | 37.44
2017-06-22 12:30 | 38.21 | 37.81
2017-06-22 13:00 | 36.52 | 36.08
2017-06-22 13:30 | 35.91 | 35.53
2017-06-22 14:00 | 36.85 | 36.47
2017-06-22 14:30 | 36.76 | 36.43
2017-06-22 15:00 | 36.84 | 36.52
2017-06-22 15:30 | 37.33 | 37.06
2017-06-22 16:00 | 37.75 | 37.55
2017-06-22 16:30 | 39.45 | 39.32
2017-06-22 17:00 | 39.88 | 39.79
2017-06-22 17:30 | 42.12 | 42.05
2017-06-22 18:00 | 45.69 | 45.58
2017-06-22 18:30 | 47.99 | 47.88
2017-06-22 19:00 | 46.61 | 46.52
2017-06-22 19:30 | 43.94 | 43.87
2017-06-22 20:00 | 42.63 | 42.56
2017-06-22 20:30 | 40.95 | 40.9
2017-06-22 21:00 | 38.93 | 38.89
2017-06-22 21:30 | 36.9 | 36.86
2017-06-22 22:00 | 35.27 | 35.24
2017-06-22 22:30 | 33.31 | 33.28
2017-06-22 23:00 | 33.47 | 33.44
2017-06-22 23:30 | 30.05 | 29.97
2017-06-23 | 28.68 | 28.6
2017-06-23 00:30 | 28.18 | 28.09
2017-06-23 01:00 | 27.01 | 26.92
2017-06-23 01:30 | 26.3 | 26.21
2017-06-23 02:00 | 25.93 | 25.85
2017-06-23 02:30 | 26.35 | 26.28
2017-06-23 03:00 | 26.23 | 26.16
2017-06-23 03:30 | 26.27 | 26.19
2017-06-23 04:00 | 25.93 | 25.86
2017-06-23 04:30 | 26.15 | 26.08
2017-06-23 05:00 | 27.06 | 26.97
2017-06-23 05:30 | 29.76 | 29.61
2017-06-23 06:00 | 32.25 | 32.03
2017-06-23 06:30 | 36.37 | 35.95
2017-06-23 07:00 | 40.04 | 39.4
2017-06-23 07:30 | 45.21 | 44.66
2017-06-23 08:00 | 48.49 | 48.02
2017-06-23 08:30 | 50.63 | 49.95
2017-06-23 09:00 | 50.13 | 49.47
2017-06-23 09:30 | 50 | 49.69
2017-06-23 10:00 | 50.35 | 50.03
2017-06-23 10:30 | 52.11 | 51.75
2017-06-23 11:00 | 50.62 | 50.22
2017-06-23 11:30 | 49.51 | 49
2017-06-23 12:00 | 48.26 | 47.69
2017-06-23 12:30 | 49.26 | 48.73
2017-06-23 13:00 | 50.2 | 49.74
2017-06-23 13:30 | 48.57 | 48.11
2017-06-23 14:00 | 47.84 | 47.4
2017-06-23 14:30 | 47.82 | 47.44
2017-06-23 15:00 | 47.35 | 47.02
2017-06-23 15:30 | 46.65 | 46.41
2017-06-23 16:00 | 46.95 | 46.77
2017-06-23 16:30 | 47.79 | 47.65
2017-06-23 17:00 | 47.82 | 47.71
2017-06-23 17:30 | 47.98 | 47.94
2017-06-23 18:00 | 49.8 | 49.75
2017-06-23 18:30 | 50.67 | 50.63
2017-06-23 19:00 | 49.69 | 49.66
2017-06-23 19:30 | 47.18 | 47.15
2017-06-23 20:00 | 45.23 | 45.21
2017-06-23 20:30 | 43.43 | 43.41
2017-06-23 21:00 | 41.98 | 41.95
2017-06-23 21:30 | 39.82 | 39.75
2017-06-23 22:00 | 37.9 | 37.77
2017-06-23 22:30 | 36.22 | 35.99
2017-06-23 23:00 | 36.4 | 36.14
2017-06-23 23:30 | 33.59 | 33.22
2017-06-24 | 31.53 | 31.34
2017-06-24 00:30 | 30.64 | 30.52
2017-06-24 01:00 | 28.86 | 28.75
2017-06-24 01:30 | 28.28 | 28.18
2017-06-24 02:00 | 27.72 | 27.62
2017-06-24 02:30 | 27.49 | 27.4
2017-06-24 03:00 | 27.05 | 26.96
2017-06-24 03:30 | 27.05 | 26.97
2017-06-24 04:00 | 27.28 | 27.2
2017-06-24 04:30 | 27.65 | 27.56
2017-06-24 05:00 | 28.01 | 27.91
2017-06-24 05:30 | 29.3 | 29.18
2017-06-24 06:00 | 30.46 | 30.31
2017-06-24 06:30 | 32.37 | 32.18
2017-06-24 07:00 | 33.38 | 33.19
2017-06-24 07:30 | 35.81 | 35.57
2017-06-24 08:00 | 37.85 | 37.53
2017-06-24 08:30 | 40.25 | 39.83
2017-06-24 09:00 | 42.4 | 41.83
2017-06-24 09:30 | 43.22 | 42.59
2017-06-24 10:00 | 43.36 | 42.67
2017-06-24 10:30 | 42.93 | 42.21
2017-06-24 11:00 | 42.09 | 41.33
2017-06-24 11:30 | 41.25 | 40.41
2017-06-24 12:00 | 40.27 | 39.39
2017-06-24 12:30 | 38.38 | 37.52
2017-06-24 13:00 | 37.41 | 36.53
2017-06-24 13:30 | 37.04 | 36.18
2017-06-24 14:00 | 36.95 | 36.19
2017-06-24 14:30 | 36.08 | 35.35
2017-06-24 15:00 | 36.58 | 35.85
2017-06-24 15:30 | 37 | 36.33
2017-06-24 16:00 | 37.49 | 36.89
2017-06-24 16:30 | 39.26 | 38.76
2017-06-24 17:00 | 39.38 | 38.95
2017-06-24 17:30 | 41.2 | 40.8
2017-06-24 18:00 | 44.06 | 43.58
2017-06-24 18:30 | 46.11 | 45.53
2017-06-24 19:00 | 45.02 | 44.44
2017-06-24 19:30 | 42.41 | 41.91
2017-06-24 20:00 | 40.4 | 39.98
2017-06-24 20:30 | 39.1 | 38.73
2017-06-24 21:00 | 37.91 | 37.57
2017-06-24 21:30 | 36.68 | 36.38
2017-06-24 22:00 | 35.51 | 35.28
2017-06-24 22:30 | 34.47 | 34.28
2017-06-24 23:00 | 34.84 | 34.68
2017-06-24 23:30 | 31.93 | 31.82
2017-06-25 | 29.7 | 29.62
2017-06-25 00:30 | 28.36 | 28.3
2017-06-25 01:00 | 27.02 | 26.96
2017-06-25 01:30 | 26.54 | 26.48
2017-06-25 02:00 | 25.54 | 25.48
2017-06-25 02:30 | 26.02 | 25.97
2017-06-25 03:00 | 26.05 | 25.99
2017-06-25 03:30 | 25.8 | 25.74
2017-06-25 04:00 | 26.06 | 26.02
2017-06-25 04:30 | 26.94 | 26.88
2017-06-25 05:00 | 27.44 | 27.38
2017-06-25 05:30 | 28.13 | 28.07
2017-06-25 06:00 | 28.72 | 28.65
2017-06-25 06:30 | 29.81 | 29.74
2017-06-25 07:00 | 30.11 | 30.06
2017-06-25 07:30 | 31.69 | 31.65
2017-06-25 08:00 | 32.88 | 32.85
2017-06-25 08:30 | 33.23 | 33.19
2017-06-25 09:00 | 33.13 | 33.04
2017-06-25 09:30 | 32.69 | 32.58
2017-06-25 10:00 | 32.84 | 32.66
2017-06-25 10:30 | 32.12 | 31.88
2017-06-25 11:00 | 32.01 | 31.71
2017-06-25 11:30 | 31.5 | 31.14
2017-06-25 12:00 | 31.17 | 30.75
2017-06-25 12:30 | 31.23 | 30.86
2017-06-25 13:00 | 30.83 | 30.42
2017-06-25 13:30 | 30.55 | 30.12
2017-06-25 14:00 | 30.63 | 30.24
2017-06-25 14:30 | 31.01 | 30.65
2017-06-25 15:00 | 31.7 | 31.33
2017-06-25 15:30 | 32.43 | 32.13
2017-06-25 16:00 | 33.93 | 33.66
2017-06-25 16:30 | 35.61 | 35.39
2017-06-25 17:00 | 36.65 | 36.43
2017-06-25 17:30 | 39.35 | 39.16
2017-06-25 18:00 | 43.13 | 42.83
2017-06-25 18:30 | 45.41 | 45.06
2017-06-25 19:00 | 48.79 | 44.25
2017-06-25 19:30 | 48.29 | 41.75
2017-06-25 20:00 | 46.3 | 39.42
2017-06-25 20:30 | 44.6 | 37.46
2017-06-25 21:00 | 43.56 | 36.26
2017-06-25 21:30 | 42.09 | 34.53
2017-06-25 22:00 | 40.75 | 32.92
2017-06-25 22:30 | 39.72 | 31.66
2017-06-25 23:00 | 39.7 | 31.68
2017-06-25 23:30 | 37.48 | 28.9
2017-06-26 | 36.27 | 27.37
2017-06-26 00:30 | 35.94 | 26.92
2017-06-26 01:00 | 35.12 | 25.77
2017-06-26 01:30 | 35.08 | 25.76
2017-06-26 02:00 | 34.92 | 25.56
2017-06-26 02:30 | 34.36 | 24.77
2017-06-26 03:00 | 34.25 | 24.64
2017-06-26 03:30 | 34.38 | 24.79
2017-06-26 04:00 | 34.73 | 25.29
2017-06-26 04:30 | 35.26 | 25.97
2017-06-26 05:00 | 36.89 | 28.05
2017-06-26 05:30 | 38.48 | 30.02
2017-06-26 06:00 | 42.4 | 34.78
2017-06-26 06:30 | 46.02 | 38.91
2017-06-26 07:00 | 48.62 | 41.84
2017-06-26 07:30 | 52.82 | 46.72
2017-06-26 08:00 | 54.08 | 48.17
2017-06-26 08:30 | 54.83 | 48.91
2017-06-26 09:00 | 52.44 | 49.12
2017-06-26 09:30 | 51.17 | 48.53
2017-06-26 10:00 | 51.47 | 49.14
2017-06-26 10:30 | 50.6 | 48.59
2017-06-26 11:00 | 50.03 | 48.22
2017-06-26 11:30 | 49.9 | 48.29
2017-06-26 12:00 | 49.64 | 48.19
2017-06-26 12:30 | 49.74 | 48.26
2017-06-26 13:00 | 49.19 | 47.6
2017-06-26 13:30 | 49.51 | 48.07
2017-06-26 14:00 | 49.77 | 48.39
2017-06-26 14:30 | 49.88 | 48.48
2017-06-26 15:00 | 50.03 | 48.55
2017-06-26 15:30 | 50.34 | 48.74
2017-06-26 16:00 | 50.66 | 48.73
2017-06-26 16:30 | 52.07 | 49.63
2017-06-26 17:00 | 51.76 | 48.7
2017-06-26 17:30 | 52.28 | 48.61
2017-06-26 18:00 | 54.59 | 50.99
2017-06-26 18:30 | 56.04 | 52.43
2017-06-26 19:00 | 55.26 | 51.32
2017-06-26 19:30 | 52.56 | 47.99
2017-06-26 20:00 | 51.16 | 46.04
2017-06-26 20:30 | 51.16 | 43.43
2017-06-26 21:00 | 50.38 | 41.23
2017-06-26 21:30 | 48.88 | 39.25
2017-06-26 22:00 | 46.91 | 36.65
2017-06-26 22:30 | 45.32 | 34.87
2017-06-26 23:00 | 37.4 | 34.95
2017-06-26 23:30 | 32.6 | 32.19
2017-06-27 | 30.41 | 30.32
2017-06-27 00:30 | 29.32 | 29.24
2017-06-27 01:00 | 27.88 | 27.79
2017-06-27 01:30 | 27.27 | 27.18
2017-06-27 02:00 | 26.97 | 26.88
2017-06-27 02:30 | 26.65 | 26.57
2017-06-27 03:00 | 25.79 | 25.72
2017-06-27 03:30 | 26.16 | 26.1
2017-06-27 04:00 | 26.36 | 26.3
2017-06-27 04:30 | 27.21 | 27.12
2017-06-27 05:00 | 28.36 | 28.28
2017-06-27 05:30 | 31.25 | 31.09
2017-06-27 06:00 | 34.12 | 33.84
2017-06-27 06:30 | 39.92 | 39.3
2017-06-27 07:00 | 43.36 | 42.81
2017-06-27 07:30 | 47.95 | 47.87
2017-06-27 08:00 | 50.12 | 49.95
2017-06-27 08:30 | 51.43 | 51.09
2017-06-27 09:00 | 51.23 | 51.06
2017-06-27 09:30 | 50.99 | 50.87
2017-06-27 10:00 | 50.74 | 50.6
2017-06-27 10:30 | 50.88 | 50.67
2017-06-27 11:00 | 50.6 | 50.29
2017-06-27 11:30 | 52.44 | 52.12
2017-06-27 12:00 | 51.18 | 50.77
2017-06-27 12:30 | 51.14 | 50.74
2017-06-27 13:00 | 50.41 | 50.05
2017-06-27 13:30 | 52.53 | 52.14
2017-06-27 14:00 | 51.85 | 51.47
2017-06-27 14:30 | 51.15 | 50.77
2017-06-27 15:00 | 51.66 | 51.05
2017-06-27 15:30 | 53.04 | 51.7
2017-06-27 16:00 | 52.79 | 51.48
2017-06-27 16:30 | 52.89 | 51.67
2017-06-27 17:00 | 52.23 | 51.06
2017-06-27 17:30 | 52.06 | 50.95
2017-06-27 18:00 | 53.3 | 52.25
2017-06-27 18:30 | 54.17 | 53.15
2017-06-27 19:00 | 52.92 | 51.89
2017-06-27 19:30 | 49.87 | 48.8
2017-06-27 20:00 | 47.81 | 46.7
2017-06-27 20:30 | 45.34 | 44.21
2017-06-27 21:00 | 43.98 | 42.81
2017-06-27 21:30 | 42.07 | 40.89
2017-06-27 22:00 | 39.17 | 37.93
2017-06-27 22:30 | 36.98 | 35.73
2017-06-27 23:00 | 36.32 | 35.84
2017-06-27 23:30 | 32.78 | 32.53
2017-06-28 | 31.05 | 30.69
2017-06-28 00:30 | 30.66 | 30.24
2017-06-28 01:00 | 29.31 | 28.78
2017-06-28 01:30 | 28.17 | 28.13
2017-06-28 02:00 | 28.01 | 27.97
2017-06-28 02:30 | 27.59 | 27.51
2017-06-28 03:00 | 27.11 | 27.02
2017-06-28 03:30 | 27.49 | 27.39
2017-06-28 04:00 | 27.65 | 27.55
2017-06-28 04:30 | 27.97 | 27.86
2017-06-28 05:00 | 28.98 | 28.86
2017-06-28 05:30 | 33.04 | 32.72
2017-06-28 06:00 | 35.69 | 35.22
2017-06-28 06:30 | 42.06 | 40.55
2017-06-28 07:00 | 50.68 | 43.97
2017-06-28 07:30 | 54.06 | 48.24
2017-06-28 08:00 | 55.89 | 50.24
2017-06-28 08:30 | 57.76 | 52.44
2017-06-28 09:00 | 59.85 | 54.71
2017-06-28 09:30 | 59.32 | 54.13
2017-06-28 10:00 | 58.93 | 53.61
2017-06-28 10:30 | 59.86 | 54.59
2017-06-28 11:00 | 58.84 | 53.43
2017-06-28 11:30 | 58.13 | 52.59
2017-06-28 12:00 | 57.98 | 52.38
2017-06-28 12:30 | 57.91 | 52.3
2017-06-28 13:00 | 57.66 | 52.04
2017-06-28 13:30 | 57.83 | 52.22
2017-06-28 14:00 | 57.65 | 52.07
2017-06-28 14:30 | 58.35 | 52.82
2017-06-28 15:00 | 57.6 | 52.05
2017-06-28 15:30 | 58.28 | 52.85
2017-06-28 16:00 | 58.59 | 53.27
2017-06-28 16:30 | 58.05 | 52.82
2017-06-28 17:00 | 56.67 | 51.45
2017-06-28 17:30 | 56.25 | 51.16
2017-06-28 18:00 | 57.84 | 52.93
2017-06-28 18:30 | 58.34 | 53.55
2017-06-28 19:00 | 57.05 | 52.17
2017-06-28 19:30 | 54.11 | 48.97
2017-06-28 20:00 | 52.04 | 46.69
2017-06-28 20:30 | 49.82 | 44.31
2017-06-28 21:00 | 48.56 | 42.9
2017-06-28 21:30 | 46.17 | 40.25
2017-06-28 22:00 | 38.73 | 38.04
2017-06-28 22:30 | 37.23 | 36.52
2017-06-28 23:00 | 37.18 | 36.4
2017-06-28 23:30 | 34.01 | 32.99
2017-06-29 | 31.44 | 30.68
2017-06-29 00:30 | 29.79 | 29.75
2017-06-29 01:00 | 28.4 | 28.36
2017-06-29 01:30 | 27.86 | 27.82
2017-06-29 02:00 | 27.1 | 27.01
2017-06-29 02:30 | 26.89 | 26.79
2017-06-29 03:00 | 26.65 | 26.55
2017-06-29 03:30 | 26.65 | 26.55
2017-06-29 04:00 | 26.67 | 26.58
2017-06-29 04:30 | 27.87 | 27.77
2017-06-29 05:00 | 29.08 | 28.93
2017-06-29 05:30 | 31.86 | 31.56
2017-06-29 06:00 | 35.12 | 34.62
2017-06-29 06:30 | 40.47 | 39.55
2017-06-29 07:00 | 49.72 | 43.31
2017-06-29 07:30 | 54.38 | 48.68
2017-06-29 08:00 | 56.58 | 51.04
2017-06-29 08:30 | 58.25 | 53.01
2017-06-29 09:00 | 59.07 | 53.9
2017-06-29 09:30 | 58.98 | 53.82
2017-06-29 10:00 | 57.62 | 52.26
2017-06-29 10:30 | 58.52 | 53.17
2017-06-29 11:00 | 59.41 | 54.15
2017-06-29 11:30 | 60.59 | 55.44
2017-06-29 12:00 | 59.7 | 54.46
2017-06-29 12:30 | 58.17 | 52.77
2017-06-29 13:00 | 57.84 | 52.45
2017-06-29 13:30 | 57.83 | 52.43
2017-06-29 14:00 | 58.55 | 53.26
2017-06-29 14:30 | 58.57 | 53.26
2017-06-29 15:00 | 58.63 | 53.4
2017-06-29 15:30 | 58.28 | 53.03
2017-06-29 16:00 | 57.37 | 52.11
2017-06-29 16:30 | 57.02 | 51.89
2017-06-29 17:00 | 55.66 | 50.54
2017-06-29 17:30 | 55.44 | 50.4
2017-06-29 18:00 | 57.69 | 52.91
2017-06-29 18:30 | 58.74 | 54.01
2017-06-29 19:00 | 57.62 | 52.79
2017-06-29 19:30 | 54.82 | 49.75
2017-06-29 20:00 | 52.7 | 47.42
2017-06-29 20:30 | 51.01 | 45.59
2017-06-29 21:00 | 49.34 | 43.77
2017-06-29 21:30 | 47.06 | 41.24
2017-06-29 22:00 | 38.96 | 38.05
2017-06-29 22:30 | 37.25 | 36.53
2017-06-29 23:00 | 37.06 | 36.24
2017-06-29 23:30 | 33.96 | 32.91
2017-06-30 | 31.6 | 31.16
2017-06-30 00:30 | 30.72 | 30.31
2017-06-30 01:00 | 30.12 | 29.7
2017-06-30 01:30 | 29.04 | 28.62
2017-06-30 02:00 | 27.63 | 27.57
2017-06-30 02:30 | 27.14 | 27.04
2017-06-30 03:00 | 26.85 | 26.75
2017-06-30 03:30 | 26.85 | 26.75
2017-06-30 04:00 | 27.13 | 27.03
2017-06-30 04:30 | 27.68 | 27.57
2017-06-30 05:00 | 28.74 | 28.61
2017-06-30 05:30 | 31.57 | 31.29
2017-06-30 06:00 | 35 | 34.51
2017-06-30 06:30 | 40.93 | 39.34
2017-06-30 07:00 | 49.57 | 43.06
2017-06-30 07:30 | 53.13 | 47.28
2017-06-30 08:00 | 56.06 | 50.42
2017-06-30 08:30 | 58.5 | 53.28
2017-06-30 09:00 | 59.66 | 54.56
2017-06-30 09:30 | 59.94 | 54.85
2017-06-30 10:00 | 58.97 | 53.78
2017-06-30 10:30 | 58.06 | 52.77
2017-06-30 11:00 | 58.14 | 52.78
2017-06-30 11:30 | 58.84 | 53.53
2017-06-30 12:00 | 58.55 | 53.23
2017-06-30 12:30 | 58.37 | 53.04
2017-06-30 13:00 | 56.67 | 51.14
2017-06-30 13:30 | 56.32 | 50.78
2017-06-30 14:00 | 55.62 | 50.1
2017-06-30 14:30 | 54.46 | 48.88
2017-06-30 15:00 | 54.93 | 49.42
2017-06-30 15:30 | 54.83 | 49.39
2017-06-30 16:00 | 53.42 | 47.92
2017-06-30 16:30 | 54.17 | 48.81
2017-06-30 17:00 | 53.58 | 48.27
2017-06-30 17:30 | 53.33 | 48.14
2017-06-30 18:00 | 54.86 | 49.81
2017-06-30 18:30 | 55.59 | 50.65
2017-06-30 19:00 | 54.8 | 49.82
2017-06-30 19:30 | 52.69 | 47.5
2017-06-30 20:00 | 51.23 | 45.88
2017-06-30 20:30 | 48.84 | 43.27
2017-06-30 21:00 | 47.82 | 42.08
2017-06-30 21:30 | 46.14 | 39.83
2017-06-30 22:00 | 44.19 | 37.61
2017-06-30 22:30 | 38.47 | 35.64
2017-06-30 23:00 | 36.1 | 35.81
2017-06-30 23:30 | 33.22 | 32.82
2017-07-01 | 30.82 | 30.63
2017-07-01 00:30 | 29.72 | 29.65
2017-07-01 01:00 | 28.25 | 28.16
2017-07-01 01:30 | 27.72 | 27.62
2017-07-01 02:00 | 27.02 | 26.94
2017-07-01 02:30 | 26.81 | 26.73
2017-07-01 03:00 | 25.86 | 25.78
2017-07-01 03:30 | 25.65 | 25.57
2017-07-01 04:00 | 25.62 | 25.55
2017-07-01 04:30 | 25.99 | 25.9
2017-07-01 05:00 | 26.45 | 26.36
2017-07-01 05:30 | 27.67 | 27.57
2017-07-01 06:00 | 28.39 | 28.29
2017-07-01 06:30 | 30.28 | 30.13
2017-07-01 07:00 | 31.52 | 31.37
2017-07-01 07:30 | 33.77 | 33.58
2017-07-01 08:00 | 35.94 | 35.65
2017-07-01 08:30 | 37.98 | 37.59
2017-07-01 09:00 | 39.85 | 39.35
2017-07-01 09:30 | 46.59 | 41.26
2017-07-01 10:00 | 47.93 | 41.04
2017-07-01 10:30 | 48.02 | 41.15
2017-07-01 11:00 | 47.47 | 40.49
2017-07-01 11:30 | 45.31 | 37.9
2017-07-01 12:00 | 46.33 | 39.11
2017-07-01 12:30 | 45.92 | 38.7
2017-07-01 13:00 | 45.04 | 37.73
2017-07-01 13:30 | 45.3 | 37.84
2017-07-01 14:00 | 44.54 | 36.96
2017-07-01 14:30 | 44.89 | 37.49
2017-07-01 15:00 | 44.62 | 37.15
2017-07-01 15:30 | 44.43 | 36.94
2017-07-01 16:00 | 45.05 | 37.69
2017-07-01 16:30 | 46.6 | 39.58
2017-07-01 17:00 | 46.29 | 39.26
2017-07-01 17:30 | 47.62 | 40.8
2017-07-01 18:00 | 50.11 | 43.66
2017-07-01 18:30 | 50.5 | 44.12
2017-07-01 19:00 | 49.58 | 43.06
2017-07-01 19:30 | 47.84 | 41.03
2017-07-01 20:00 | 46.51 | 39.47
2017-07-01 20:30 | 46.24 | 39.18
2017-07-01 21:00 | 44.65 | 37.33
2017-07-01 21:30 | 43.36 | 35.8
2017-07-01 22:00 | 42.11 | 34.29
2017-07-01 22:30 | 41.78 | 33.92
2017-07-01 23:00 | 41.64 | 33.8
2017-07-01 23:30 | 39.05 | 30.58
2017-07-02 | 38.16 | 29.41
2017-07-02 00:30 | 37.41 | 28.54
2017-07-02 01:00 | 36.57 | 27.45
2017-07-02 01:30 | 36.03 | 26.72
2017-07-02 02:00 | 35.79 | 26.47
2017-07-02 02:30 | 35.93 | 26.86
2017-07-02 03:00 | 34.83 | 25.39
2017-07-02 03:30 | 34.9 | 25.49
2017-07-02 04:00 | 34.93 | 25.5
2017-07-02 04:30 | 35.9 | 26.81
2017-07-02 05:00 | 35.3 | 25.96
2017-07-02 05:30 | 35.7 | 26.51
2017-07-02 06:00 | 36.09 | 27.03
2017-07-02 06:30 | 37.26 | 28.52
2017-07-02 07:00 | 37.49 | 28.85
2017-07-02 07:30 | 38.85 | 30.58
2017-07-02 08:00 | 39.89 | 31.91
2017-07-02 08:30 | 41.42 | 33.78
2017-07-02 09:00 | 42.75 | 35.35
2017-07-02 09:30 | 43.56 | 36.3
2017-07-02 10:00 | 43.71 | 36.39
2017-07-02 10:30 | 44.06 | 36.77
2017-07-02 11:00 | 43.47 | 36.05
2017-07-02 11:30 | 41.72 | 33.86
2017-07-02 12:00 | 41.67 | 33.77
2017-07-02 12:30 | 40.99 | 32.96
2017-07-02 13:00 | 40.04 | 31.73
2017-07-02 13:30 | 40.47 | 32.27
2017-07-02 14:00 | 39.64 | 31.31
2017-07-02 14:30 | 41.68 | 33.83
2017-07-02 15:00 | 43.28 | 35.79
2017-07-02 15:30 | 44.92 | 37.78
2017-07-02 16:00 | 45.22 | 38.19
2017-07-02 16:30 | 46.32 | 39.51
2017-07-02 17:00 | 45.87 | 39.02
2017-07-02 17:30 | 47.44 | 40.8
2017-07-02 18:00 | 49.48 | 43.13
2017-07-02 18:30 | 49.88 | 43.63
2017-07-02 19:00 | 49.09 | 42.72
2017-07-02 19:30 | 47.95 | 41.36
2017-07-02 20:00 | 46.07 | 39.22
2017-07-02 20:30 | 44.87 | 37.79
2017-07-02 21:00 | 43.57 | 36.28
2017-07-02 21:30 | 42.42 | 34.97
2017-07-02 22:00 | 41.41 | 33.72
2017-07-02 22:30 | 39.98 | 31.96
2017-07-02 23:00 | 41.29 | 33.65
2017-07-02 23:30 | 39.68 | 31.56
2017-07-03 | 38.51 | 30.08
2017-07-03 00:30 | 38.04 | 29.5
2017-07-03 01:00 | 37.21 | 28.44
2017-07-03 01:30 | 36.76 | 27.89
2017-07-03 02:00 | 35.69 | 26.61
2017-07-03 02:30 | 35.57 | 26.44
2017-07-03 03:00 | 35.47 | 26.31
2017-07-03 03:30 | 34.91 | 25.54
2017-07-03 04:00 | 36 | 26.98
2017-07-03 04:30 | 36.43 | 27.54
2017-07-03 05:00 | 37.29 | 28.57
2017-07-03 05:30 | 38.99 | 30.63
2017-07-03 06:00 | 41.41 | 33.51
2017-07-03 06:30 | 45.21 | 37.93
2017-07-03 07:00 | 48.1 | 41.25
2017-07-03 07:30 | 52.55 | 46.47
2017-07-03 08:00 | 52.27 | 48.8
2017-07-03 08:30 | 52.13 | 50.61
2017-07-03 09:00 | 52.87 | 51.43
2017-07-03 09:30 | 52.81 | 51.43
2017-07-03 10:00 | 53.06 | 51.16
2017-07-03 10:30 | 53.87 | 51.55
2017-07-03 11:00 | 53.63 | 51.36
2017-07-03 11:30 | 53.07 | 50.78
2017-07-03 12:00 | 53.27 | 51.01
2017-07-03 12:30 | 54.14 | 51.93
2017-07-03 13:00 | 53.55 | 51.32
2017-07-03 13:30 | 53.94 | 51.75
2017-07-03 14:00 | 54.33 | 52.18
2017-07-03 14:30 | 54.09 | 51.87
2017-07-03 15:00 | 54.36 | 52.13
2017-07-03 15:30 | 54.34 | 52.06
2017-07-03 16:00 | 54.12 | 51.76
2017-07-03 16:30 | 55.28 | 52.88
2017-07-03 17:00 | 54.43 | 51.81
2017-07-03 17:30 | 53.94 | 50.72
2017-07-03 18:00 | 55.99 | 52.72
2017-07-03 18:30 | 57.41 | 54.17
2017-07-03 19:00 | 55.61 | 52.59
2017-07-03 19:30 | 52.33 | 49.95
2017-07-03 20:00 | 49.93 | 47.39
2017-07-03 20:30 | 47.93 | 45.45
2017-07-03 21:00 | 45.11 | 43.37
2017-07-03 21:30 | 43.32 | 41.45
2017-07-03 22:00 | 41.55 | 39.53
2017-07-03 22:30 | 40.14 | 38
2017-07-03 23:00 | 39.62 | 37.54
2017-07-03 23:30 | 36.5 | 34.38
2017-07-04 | 34.28 | 31.98
2017-07-04 00:30 | 33.46 | 31.04
2017-07-04 01:00 | 32.36 | 29.81
2017-07-04 01:30 | 31.63 | 28.99
2017-07-04 02:00 | 31.03 | 28.31
2017-07-04 02:30 | 30.54 | 27.73
2017-07-04 03:00 | 30.48 | 27.66
2017-07-04 03:30 | 30.37 | 27.53
2017-07-04 04:00 | 30.48 | 27.62
2017-07-04 04:30 | 30.86 | 28.06
2017-07-04 05:00 | 31.86 | 29.2
2017-07-04 05:30 | 34.44 | 32.14
2017-07-04 06:00 | 37.12 | 35.1
2017-07-04 06:30 | 41.64 | 39.85
2017-07-04 07:00 | 44.98 | 43.12
2017-07-04 07:30 | 49.13 | 47.48
2017-07-04 08:00 | 51.45 | 49.85
2017-07-04 08:30 | 52.71 | 51.22
2017-07-04 09:00 | 53.32 | 51.96
2017-07-04 09:30 | 52.38 | 51
2017-07-04 10:00 | 52.48 | 51.06
2017-07-04 10:30 | 53.51 | 52.06
2017-07-04 11:00 | 53.97 | 52.52
2017-07-04 11:30 | 53.58 | 52.1
2017-07-04 12:00 | 53.42 | 51.91
2017-07-04 12:30 | 53.73 | 52.24
2017-07-04 13:00 | 53.28 | 51.8
2017-07-04 13:30 | 53.36 | 51.86
2017-07-04 14:00 | 53.45 | 51.94
2017-07-04 14:30 | 53.35 | 51.85
2017-07-04 15:00 | 53.56 | 52.09
2017-07-04 15:30 | 54.16 | 52.72
2017-07-04 16:00 | 54.74 | 53.38
2017-07-04 16:30 | 54.61 | 53.3
2017-07-04 17:00 | 53.36 | 52.09
2017-07-04 17:30 | 53.12 | 51.92
2017-07-04 18:00 | 54.52 | 53.39
2017-07-04 18:30 | 56.25 | 55.17
2017-07-04 19:00 | 54.96 | 53.88
2017-07-04 19:30 | 52.04 | 50.92
2017-07-04 20:00 | 49.77 | 48.61
2017-07-04 20:30 | 47.49 | 46.31
2017-07-04 21:00 | 45.81 | 44.62
2017-07-04 21:30 | 43.62 | 42.39
2017-07-04 22:00 | 41.7 | 40.45
2017-07-04 22:30 | 39.45 | 38.13
2017-07-04 23:00 | 39.19 | 37.96
2017-07-04 23:30 | 34.59 | 34.21
2017-07-05 | 32.75 | 32.34
2017-07-05 00:30 | 31.08 | 31
2017-07-05 01:00 | 29.92 | 29.87
2017-07-05 01:30 | 28.84 | 28.77
2017-07-05 02:00 | 28.36 | 28.26
2017-07-05 02:30 | 27.75 | 27.66
2017-07-05 03:00 | 27.38 | 27.3
2017-07-05 03:30 | 27.53 | 27.45
2017-07-05 04:00 | 27.91 | 27.83
2017-07-05 04:30 | 28.43 | 28.34
2017-07-05 05:00 | 29.52 | 29.41
2017-07-05 05:30 | 32.33 | 32.14
2017-07-05 06:00 | 35.67 | 35.28
2017-07-05 06:30 | 40.76 | 40.05
2017-07-05 07:00 | 43.86 | 43.35
2017-07-05 07:30 | 48.41 | 48.12
2017-07-05 08:00 | 50.1 | 49.92
2017-07-05 08:30 | 51.71 | 51.4
2017-07-05 09:00 | 51.61 | 51.43
2017-07-05 09:30 | 50.83 | 50.74
2017-07-05 10:00 | 51.23 | 51.09
2017-07-05 10:30 | 53.07 | 52.82
2017-07-05 11:00 | 51.92 | 51.6
2017-07-05 11:30 | 52.98 | 52.57
2017-07-05 12:00 | 52.4 | 51.96
2017-07-05 12:30 | 52.37 | 51.92
2017-07-05 13:00 | 51.74 | 51.3
2017-07-05 13:30 | 52.05 | 51.57
2017-07-05 14:00 | 52.97 | 52.44
2017-07-05 14:30 | 53.99 | 53.45
2017-07-05 15:00 | 53.1 | 52.64
2017-07-05 15:30 | 53.55 | 53.2
2017-07-05 16:00 | 53.99 | 53.78
2017-07-05 16:30 | 53.26 | 53.17
2017-07-05 17:00 | 53.2 | 53.15
2017-07-05 17:30 | 52.25 | 52.23
2017-07-05 18:00 | 53.31 | 53.3
2017-07-05 18:30 | 54.62 | 54.6
2017-07-05 19:00 | 53.92 | 53.89
2017-07-05 19:30 | 50.97 | 50.91
2017-07-05 20:00 | 48.14 | 48.02
2017-07-05 20:30 | 46.84 | 46.67
2017-07-05 21:00 | 44.9 | 44.64
2017-07-05 21:30 | 43.01 | 42.63
2017-07-05 22:00 | 40.99 | 40.46
2017-07-05 22:30 | 39.47 | 38.79
2017-07-05 23:00 | 38.71 | 38.41
2017-07-05 23:30 | 34.97 | 34.68
2017-07-06 | 33.52 | 33.19
2017-07-06 00:30 | 32.13 | 32.09
2017-07-06 01:00 | 30.84 | 30.81
2017-07-06 01:30 | 29.95 | 29.91
2017-07-06 02:00 | 29.48 | 29.43
2017-07-06 02:30 | 28.68 | 28.6
2017-07-06 03:00 | 28.41 | 28.3
2017-07-06 03:30 | 28.02 | 27.92
2017-07-06 04:00 | 28.29 | 28.19
2017-07-06 04:30 | 29.3 | 29.19
2017-07-06 05:00 | 30.61 | 30.5
2017-07-06 05:30 | 33.44 | 33.19
2017-07-06 06:00 | 36.46 | 36.05
2017-07-06 06:30 | 41.36 | 40.66
2017-07-06 07:00 | 44.6 | 44.08
2017-07-06 07:30 | 48.66 | 48.12
2017-07-06 08:00 | 50.05 | 49.31
2017-07-06 08:30 | 50.99 | 50.67
2017-07-06 09:00 | 51.21 | 51.13
2017-07-06 09:30 | 50.52 | 50.41
2017-07-06 10:00 | 50.37 | 50.17
2017-07-06 10:30 | 52.17 | 51.83
2017-07-06 11:00 | 53.01 | 52.58
2017-07-06 11:30 | 53.41 | 52.88
2017-07-06 12:00 | 52.65 | 52.08
2017-07-06 12:30 | 53.11 | 52.54
2017-07-06 13:00 | 52.74 | 52.13
2017-07-06 13:30 | 53.53 | 52.99
2017-07-06 14:00 | 53.27 | 52.62
2017-07-06 14:30 | 53.46 | 52.85
2017-07-06 15:00 | 53.69 | 53.12
2017-07-06 15:30 | 53.62 | 53.13
2017-07-06 16:00 | 53.27 | 52.93
2017-07-06 16:30 | 53.69 | 53.53
2017-07-06 17:00 | 52.6 | 52.54
2017-07-06 17:30 | 51.95 | 51.92
2017-07-06 18:00 | 53.62 | 53.6
2017-07-06 18:30 | 55.33 | 55.31
2017-07-06 19:00 | 54.07 | 54.05
2017-07-06 19:30 | 51.74 | 51.71
2017-07-06 20:00 | 49.27 | 49.2
2017-07-06 20:30 | 48.09 | 47.99
2017-07-06 21:00 | 46.64 | 46.51
2017-07-06 21:30 | 43.93 | 43.69
2017-07-06 22:00 | 42.11 | 41.75
2017-07-06 22:30 | 40.76 | 40.25
2017-07-06 23:00 | 41.19 | 40.57
2017-07-06 23:30 | 38.24 | 37.92
2017-07-07 | 36.27 | 36.13
2017-07-07 00:30 | 34.63 | 34.6
2017-07-07 01:00 | 32.21 | 32.18
2017-07-07 01:30 | 31.08 | 31.06
2017-07-07 02:00 | 30.52 | 30.49
2017-07-07 02:30 | 29.5 | 29.4
2017-07-07 03:00 | 29.61 | 29.5
2017-07-07 03:30 | 29.68 | 29.57
2017-07-07 04:00 | 28.93 | 28.83
2017-07-07 04:30 | 30.21 | 30.07
2017-07-07 05:00 | 31.29 | 31.12
2017-07-07 05:30 | 33.25 | 32.99
2017-07-07 06:00 | 36.19 | 35.77
2017-07-07 06:30 | 40.93 | 40.22
2017-07-07 07:00 | 43.75 | 43.23
2017-07-07 07:30 | 47.07 | 46.7
2017-07-07 08:00 | 49.41 | 49.18
2017-07-07 08:30 | 51.8 | 51.59
2017-07-07 09:00 | 52.37 | 52.22
2017-07-07 09:30 | 52.53 | 52.31
2017-07-07 10:00 | 52.5 | 52.22
2017-07-07 10:30 | 52.93 | 52.51
2017-07-07 11:00 | 53.57 | 53
2017-07-07 11:30 | 54.51 | 53.87
2017-07-07 12:00 | 56.24 | 55.54
2017-07-07 12:30 | 56.59 | 55.88
2017-07-07 13:00 | 55.65 | 55
2017-07-07 13:30 | 54.71 | 53.94
2017-07-07 14:00 | 55.3 | 54.62
2017-07-07 14:30 | 54.42 | 53.84
2017-07-07 15:00 | 54.33 | 53.86
2017-07-07 15:30 | 53.83 | 53.51
2017-07-07 16:00 | 52.9 | 52.72
2017-07-07 16:30 | 54.01 | 53.95
2017-07-07 17:00 | 53.51 | 53.46
2017-07-07 17:30 | 53.64 | 53.62
2017-07-07 18:00 | 53.16 | 53.14
2017-07-07 18:30 | 53.14 | 53.12
2017-07-07 19:00 | 51 | 50.97
2017-07-07 19:30 | 48.29 | 48.22
2017-07-07 20:00 | 46.45 | 46.34
2017-07-07 20:30 | 44.44 | 44.26
2017-07-07 21:00 | 43.02 | 42.78
2017-07-07 21:30 | 41.66 | 41.35
2017-07-07 22:00 | 40.58 | 40.13
2017-07-07 22:30 | 38.92 | 38.31
2017-07-07 23:00 | 38.08 | 37.89
2017-07-07 23:30 | 34.68 | 34.64
2017-07-08 | 32.75 | 32.72
2017-07-08 00:30 | 31.43 | 31.38
2017-07-08 01:00 | 29.84 | 29.75
2017-07-08 01:30 | 29.19 | 29.08
2017-07-08 02:00 | 28.49 | 28.38
2017-07-08 02:30 | 28.12 | 28.01
2017-07-08 03:00 | 27.93 | 27.83
2017-07-08 03:30 | 27.33 | 27.24
2017-07-08 04:00 | 27.52 | 27.43
2017-07-08 04:30 | 28.01 | 27.92
2017-07-08 05:00 | 29.09 | 28.99
2017-07-08 05:30 | 29.77 | 29.66
2017-07-08 06:00 | 30.61 | 30.45
2017-07-08 06:30 | 32.6 | 32.36
2017-07-08 07:00 | 33.25 | 33.03
2017-07-08 07:30 | 35.62 | 35.32
2017-07-08 08:00 | 37.94 | 37.55
2017-07-08 08:30 | 40.37 | 39.78
2017-07-08 09:00 | 41.61 | 40.83
2017-07-08 09:30 | 42.57 | 41.67
2017-07-08 10:00 | 42.66 | 42.32
2017-07-08 10:30 | 42.49 | 42.07
2017-07-08 11:00 | 42.91 | 42.4
2017-07-08 11:30 | 42.78 | 42.22
2017-07-08 12:00 | 40.92 | 40.41
2017-07-08 12:30 | 40.43 | 39.98
2017-07-08 13:00 | 39.45 | 39
2017-07-08 13:30 | 38.36 | 37.93
2017-07-08 14:00 | 37.97 | 37.63
2017-07-08 14:30 | 37.99 | 37.68
2017-07-08 15:00 | 37.93 | 37.67
2017-07-08 15:30 | 38.69 | 38.45
2017-07-08 16:00 | 39.73 | 39.56
2017-07-08 16:30 | 40.99 | 40.88
2017-07-08 17:00 | 41.25 | 41.17
2017-07-08 17:30 | 42.61 | 42.54
2017-07-08 18:00 | 44.73 | 44.65
2017-07-08 18:30 | 47.18 | 47.05
2017-07-08 19:00 | 45.33 | 45.23
2017-07-08 19:30 | 43.64 | 43.53
2017-07-08 20:00 | 41.92 | 41.82
2017-07-08 20:30 | 40.12 | 40.05
2017-07-08 21:00 | 39.31 | 39.24
2017-07-08 21:30 | 38.2 | 38.14
2017-07-08 22:00 | 37.32 | 37.27
2017-07-08 22:30 | 35.95 | 35.91
2017-07-08 23:00 | 36.16 | 36.14
2017-07-08 23:30 | 33.6 | 33.57
2017-07-09 | 31.91 | 31.88
2017-07-09 00:30 | 31.48 | 31.44
2017-07-09 01:00 | 30.57 | 30.49
2017-07-09 01:30 | 29.47 | 29.35
2017-07-09 02:00 | 28.75 | 28.63
2017-07-09 02:30 | 28.57 | 28.45
2017-07-09 03:00 | 28.34 | 28.23
2017-07-09 03:30 | 28.03 | 27.94
2017-07-09 04:00 | 28.87 | 28.77
2017-07-09 04:30 | 28.49 | 28.38
2017-07-09 05:00 | 28.57 | 28.46
2017-07-09 05:30 | 28.38 | 28.29
2017-07-09 06:00 | 29.72 | 29.6
2017-07-09 06:30 | 30.7 | 30.56
2017-07-09 07:00 | 30.52 | 30.42
2017-07-09 07:30 | 31.54 | 31.44
2017-07-09 08:00 | 33.45 | 33.31
2017-07-09 08:30 | 36.01 | 35.79
2017-07-09 09:00 | 35.82 | 35.55
2017-07-09 09:30 | 35.74 | 35.41
2017-07-09 10:00 | 36.53 | 36.1
2017-07-09 10:30 | 36.98 | 36.42
2017-07-09 11:00 | 35.94 | 35.68
2017-07-09 11:30 | 35.15 | 35.04
2017-07-09 12:00 | 35.48 | 35.35
2017-07-09 12:30 | 36.08 | 35.95
2017-07-09 13:00 | 35.62 | 35.48
2017-07-09 13:30 | 35.26 | 35.14
2017-07-09 14:00 | 35.38 | 35.26
2017-07-09 14:30 | 35.36 | 35.26
2017-07-09 15:00 | 35.56 | 35.47
2017-07-09 15:30 | 35.5 | 35.42
2017-07-09 16:00 | 36.57 | 36.51
2017-07-09 16:30 | 38.74 | 38.69
2017-07-09 17:00 | 39.32 | 39.28
2017-07-09 17:30 | 41.49 | 41.44
2017-07-09 18:00 | 44.5 | 44.44
2017-07-09 18:30 | 47.42 | 47.34
2017-07-09 19:00 | 46.51 | 46.44
2017-07-09 19:30 | 43.61 | 43.55
2017-07-09 20:00 | 41.19 | 41.14
2017-07-09 20:30 | 39.38 | 39.34
2017-07-09 21:00 | 37.74 | 37.7
2017-07-09 21:30 | 35.88 | 35.85
2017-07-09 22:00 | 34.42 | 34.39
2017-07-09 22:30 | 32.51 | 32.47
2017-07-09 23:00 | 32.98 | 32.92
2017-07-09 23:30 | 30.13 | 30.05
2017-07-10 | 29.09 | 29
2017-07-10 00:30 | 28.46 | 28.36
2017-07-10 01:00 | 27.04 | 26.94
2017-07-10 01:30 | 26.83 | 26.73
2017-07-10 02:00 | 26.17 | 26.09
2017-07-10 02:30 | 26.45 | 26.35
2017-07-10 03:00 | 26.65 | 26.55
2017-07-10 03:30 | 26.92 | 26.81
2017-07-10 04:00 | 26.66 | 26.56
2017-07-10 04:30 | 27.72 | 27.6
2017-07-10 05:00 | 28.94 | 28.81
2017-07-10 05:30 | 31.8 | 31.56
2017-07-10 06:00 | 35.07 | 34.64
2017-07-10 06:30 | 40.52 | 39.72
2017-07-10 07:00 | 44.95 | 43.86
2017-07-10 07:30 | 51.72 | 50.74
2017-07-10 08:00 | 53.1 | 52.62
2017-07-10 08:30 | 56.79 | 56.56
2017-07-10 09:00 | 58.24 | 57.83
2017-07-10 09:30 | 58.73 | 58.22
2017-07-10 10:00 | 59.2 | 58.53
2017-07-10 10:30 | 59.39 | 58.59
2017-07-10 11:00 | 58.86 | 57.93
2017-07-10 11:30 | 58.72 | 57.68
2017-07-10 12:00 | 58.45 | 57.38
2017-07-10 12:30 | 60.57 | 59.51
2017-07-10 13:00 | 58.8 | 57.71
2017-07-10 13:30 | 62 | 58.63
2017-07-10 14:00 | 63.88 | 58.27
2017-07-10 14:30 | 63.46 | 57.82
2017-07-10 15:00 | 64.29 | 58.78
2017-07-10 15:30 | 64.11 | 58.63
2017-07-10 16:00 | 64.07 | 58.64
2017-07-10 16:30 | 64.25 | 59.07
2017-07-10 17:00 | 63.77 | 58.64
2017-07-10 17:30 | 62.69 | 57.64
2017-07-10 18:00 | 63.39 | 58.53
2017-07-10 18:30 | 65.04 | 60.34
2017-07-10 19:00 | 63.6 | 58.88
2017-07-10 19:30 | 60.45 | 55.48
2017-07-10 20:00 | 57.74 | 52.53
2017-07-10 20:30 | 51.74 | 49.84
2017-07-10 21:00 | 47.5 | 47.33
2017-07-10 21:30 | 45.18 | 44.93
2017-07-10 22:00 | 42.93 | 42.6
2017-07-10 22:30 | 41.26 | 40.81
2017-07-10 23:00 | 40.66 | 40.04
2017-07-10 23:30 | 37.52 | 36.76
2017-07-11 | 35.79 | 34.88
2017-07-11 00:30 | 34.54 | 34.09
2017-07-11 01:00 | 32.57 | 32.45
2017-07-11 01:30 | 31.68 | 31.53
2017-07-11 02:00 | 30.93 | 30.74
2017-07-11 02:30 | 30.24 | 30.08
2017-07-11 03:00 | 29.66 | 29.53
2017-07-11 03:30 | 29.27 | 29.15
2017-07-11 04:00 | 29.53 | 29.41
2017-07-11 04:30 | 30.7 | 30.55
2017-07-11 05:00 | 32.21 | 32.01
2017-07-11 05:30 | 35.26 | 34.94
2017-07-11 06:00 | 38 | 37.47
2017-07-11 06:30 | 43.83 | 42.9
2017-07-11 07:00 | 48.62 | 47.79
2017-07-11 07:30 | 53.84 | 53.44
2017-07-11 08:00 | 55.86 | 55.47
2017-07-11 08:30 | 57.23 | 57.02
2017-07-11 09:00 | 57.55 | 57.18
2017-07-11 09:30 | 57.99 | 57.48
2017-07-11 10:00 | 58.4 | 57.76
2017-07-11 10:30 | 58.78 | 58.01
2017-07-11 11:00 | 58.19 | 57.29
2017-07-11 11:30 | 57.51 | 56.52
2017-07-11 12:00 | 57.39 | 56.36
2017-07-11 12:30 | 57.5 | 56.44
2017-07-11 13:00 | 57.24 | 56.19
2017-07-11 13:30 | 56.66 | 55.63
2017-07-11 14:00 | 56.78 | 55.71
2017-07-11 14:30 | 57.17 | 56.17
2017-07-11 15:00 | 56.36 | 55.51
2017-07-11 15:30 | 56.44 | 55.75
2017-07-11 16:00 | 57.37 | 56.84
2017-07-11 16:30 | 57.27 | 57
2017-07-11 17:00 | 56.11 | 55.97
2017-07-11 17:30 | 54.88 | 54.84
2017-07-11 18:00 | 56.72 | 56.7
2017-07-11 18:30 | 59.09 | 59.07
2017-07-11 19:00 | 58.31 | 58.29
2017-07-11 19:30 | 55.05 | 55.04
2017-07-11 20:00 | 52.6 | 52.58
2017-07-11 20:30 | 49.85 | 49.77
2017-07-11 21:00 | 47.73 | 47.61
2017-07-11 21:30 | 45.14 | 44.91
2017-07-11 22:00 | 43.32 | 43
2017-07-11 22:30 | 41.51 | 41.08
2017-07-11 23:00 | 39.67 | 39.17
2017-07-11 23:30 | 37.75 | 36.99
2017-07-12 | 35.86 | 34.89
2017-07-12 00:30 | 42.11 | 33.84
2017-07-12 01:00 | 41.13 | 32.16
2017-07-12 01:30 | 39.82 | 31.09
2017-07-12 02:00 | 38.79 | 30.41
2017-07-12 02:30 | 38.47 | 30.06
2017-07-12 03:00 | 38.52 | 30.08
2017-07-12 03:30 | 38.44 | 29.99
2017-07-12 04:00 | 38.6 | 30.24
2017-07-12 04:30 | 39.36 | 31.29
2017-07-12 05:00 | 40.02 | 32.14
2017-07-12 05:30 | 41.97 | 34.81
2017-07-12 06:00 | 43.25 | 37.99
2017-07-12 06:30 | 44.59 | 43.52
2017-07-12 07:00 | 48.04 | 47.27
2017-07-12 07:30 | 53.23 | 52.91
2017-07-12 08:00 | 55.47 | 55.16
2017-07-12 08:30 | 55.32 | 55.15
2017-07-12 09:00 | 54.27 | 54.05
2017-07-12 09:30 | 52.99 | 52.74
2017-07-12 10:00 | 52.78 | 52.48
2017-07-12 10:30 | 52.91 | 52.49
2017-07-12 11:00 | 52.12 | 51.65
2017-07-12 11:30 | 52.35 | 51.81
2017-07-12 12:00 | 52.72 | 52.1
2017-07-12 12:30 | 52.3 | 51.71
2017-07-12 13:00 | 51.69 | 51.17
2017-07-12 13:30 | 52.91 | 52.31
2017-07-12 14:00 | 53.37 | 52.73
2017-07-12 14:30 | 52.73 | 52.1
2017-07-12 15:00 | 52.51 | 51.98
2017-07-12 15:30 | 53.04 | 52.58
2017-07-12 16:00 | 52.96 | 52.68
2017-07-12 16:30 | 54.13 | 54.01
2017-07-12 17:00 | 54.03 | 53.97
2017-07-12 17:30 | 53.37 | 53.34
2017-07-12 18:00 | 55.41 | 55.39
2017-07-12 18:30 | 57.85 | 57.83
2017-07-12 19:00 | 56.73 | 56.71
2017-07-12 19:30 | 53.92 | 53.9
2017-07-12 20:00 | 51.09 | 51.05
2017-07-12 20:30 | 48.56 | 48.46
2017-07-12 21:00 | 45.84 | 45.67
2017-07-12 21:30 | 44.57 | 44.35
2017-07-12 22:00 | 42.05 | 41.69
2017-07-12 22:30 | 41.54 | 41.15
2017-07-12 23:00 | 41.9 | 41.36
2017-07-12 23:30 | 38.73 | 38.07
2017-07-13 | 40.99 | 34.93
2017-07-13 00:30 | 42.75 | 34.14
2017-07-13 01:00 | 40.8 | 32.11
2017-07-13 01:30 | 39.8 | 31
2017-07-13 02:00 | 39.6 | 31
2017-07-13 02:30 | 38.81 | 30.44
2017-07-13 03:00 | 38.2 | 29.6
2017-07-13 03:30 | 38.08 | 29.42
2017-07-13 04:00 | 38.82 | 30.5
2017-07-13 04:30 | 39.13 | 30.94
2017-07-13 05:00 | 40.42 | 32.73
2017-07-13 05:30 | 42.11 | 35.01
2017-07-13 06:00 | 44.1 | 37.55
2017-07-13 06:30 | 45.46 | 42.82
2017-07-13 07:00 | 47.83 | 47.03
2017-07-13 07:30 | 53.4 | 53.16
2017-07-13 08:00 | 56.19 | 55.75
2017-07-13 08:30 | 56.48 | 56.27
2017-07-13 09:00 | 55.63 | 55.39
2017-07-13 09:30 | 54.25 | 53.93
2017-07-13 10:00 | 54 | 53.6
2017-07-13 10:30 | 53.99 | 53.5
2017-07-13 11:00 | 54.04 | 53.47
2017-07-13 11:30 | 53.91 | 53.3
2017-07-13 12:00 | 53.75 | 53.06
2017-07-13 12:30 | 53.55 | 52.91
2017-07-13 13:00 | 51.58 | 51
2017-07-13 13:30 | 51.49 | 50.91
2017-07-13 14:00 | 52.37 | 51.82
2017-07-13 14:30 | 51.87 | 51.32
2017-07-13 15:00 | 52.99 | 52.49
2017-07-13 15:30 | 54.47 | 54.05
2017-07-13 16:00 | 55.06 | 54.76
2017-07-13 16:30 | 55.79 | 55.65
2017-07-13 17:00 | 54.7 | 54.65
2017-07-13 17:30 | 54.47 | 54.45
2017-07-13 18:00 | 57.83 | 57.81
2017-07-13 18:30 | 59.41 | 59.39
2017-07-13 19:00 | 58.14 | 58.13
2017-07-13 19:30 | 55.12 | 55.09
2017-07-13 20:00 | 52.99 | 52.95
2017-07-13 20:30 | 51.79 | 51.74
2017-07-13 21:00 | 49.85 | 49.77
2017-07-13 21:30 | 46.35 | 46.16
2017-07-13 22:00 | 42.96 | 42.64
2017-07-13 22:30 | 41.3 | 40.9
2017-07-13 23:00 | 41.04 | 40.56
2017-07-13 23:30 | 37.94 | 36.97
2017-07-14 | 37.28 | 34.32
2017-07-14 00:30 | 36.29 | 33.45
2017-07-14 01:00 | 35.15 | 32.47
2017-07-14 01:30 | 34.73 | 32.1
2017-07-14 02:00 | 34.05 | 31.34
2017-07-14 02:30 | 33.61 | 30.83
2017-07-14 03:00 | 32.98 | 30.22
2017-07-14 03:30 | 32.08 | 29.48
2017-07-14 04:00 | 32.16 | 29.56
2017-07-14 04:30 | 34.04 | 31.66
2017-07-14 05:00 | 35.63 | 33.41
2017-07-14 05:30 | 37.62 | 35.59
2017-07-14 06:00 | 40.19 | 38.4
2017-07-14 06:30 | 45.19 | 43.75
2017-07-14 07:00 | 50.3 | 48.92
2017-07-14 07:30 | 55.31 | 53.99
2017-07-14 08:00 | 56.52 | 55.2
2017-07-14 08:30 | 59.23 | 57.07
2017-07-14 09:00 | 58.66 | 56.46
2017-07-14 09:30 | 58.61 | 56.44
2017-07-14 10:00 | 57.45 | 55.26
2017-07-14 10:30 | 56.1 | 53.91
2017-07-14 11:00 | 54.63 | 52.44
2017-07-14 11:30 | 56.16 | 54.06
2017-07-14 12:00 | 55.79 | 53.68
2017-07-14 12:30 | 55.2 | 53.05
2017-07-14 13:00 | 53.85 | 51.66
2017-07-14 13:30 | 53.54 | 51.31
2017-07-14 14:00 | 53.26 | 51.01
2017-07-14 14:30 | 53.22 | 50.93
2017-07-14 15:00 | 53.05 | 50.72
2017-07-14 15:30 | 53.32 | 50.95
2017-07-14 16:00 | 53.6 | 51.14
2017-07-14 16:30 | 54.46 | 51.95
2017-07-14 17:00 | 54.26 | 51.59
2017-07-14 17:30 | 54.21 | 50.9
2017-07-14 18:00 | 56.47 | 53.22
2017-07-14 18:30 | 57.76 | 54.54
2017-07-14 19:00 | 57.08 | 53.6
2017-07-14 19:30 | 53.72 | 50.81
2017-07-14 20:00 | 51.3 | 48.47
2017-07-14 20:30 | 49.85 | 46.67
2017-07-14 21:00 | 48.5 | 45.04
2017-07-14 21:30 | 47.27 | 43.46
2017-07-14 22:00 | 43.95 | 40.9
2017-07-14 22:30 | 40.79 | 38.66
2017-07-14 23:00 | 40.99 | 38.86
2017-07-14 23:30 | 37.91 | 35.54
2017-07-15 | 36.02 | 33.69
2017-07-15 00:30 | 35.13 | 32.8
2017-07-15 01:00 | 31.58 | 28.79
2017-07-15 01:30 | 30.94 | 28.13
2017-07-15 02:00 | 30.48 | 27.6
2017-07-15 02:30 | 30.36 | 27.47
2017-07-15 03:00 | 30.04 | 27.1
2017-07-15 03:30 | 29.54 | 26.54
2017-07-15 04:00 | 29.61 | 26.61
2017-07-15 04:30 | 29.91 | 26.97
2017-07-15 05:00 | 30.89 | 28.12
2017-07-15 05:30 | 32.03 | 29.45
2017-07-15 06:00 | 33.22 | 30.78
2017-07-15 06:30 | 35.57 | 33.39
2017-07-15 07:00 | 36.87 | 34.78
2017-07-15 07:30 | 39.62 | 37.71
2017-07-15 08:00 | 42 | 40.28
2017-07-15 08:30 | 44.11 | 42.53
2017-07-15 09:00 | 44.12 | 42.61
2017-07-15 09:30 | 44.94 | 43.5
2017-07-15 10:00 | 46.42 | 44.58
2017-07-15 10:30 | 46.46 | 44.58
2017-07-15 11:00 | 46.28 | 44.61
2017-07-15 11:30 | 44.55 | 42.82
2017-07-15 12:00 | 41.63 | 39.78
2017-07-15 12:30 | 40.73 | 38.87
2017-07-15 13:00 | 39.32 | 37.39
2017-07-15 13:30 | 38.34 | 36.36
2017-07-15 14:00 | 37.92 | 35.96
2017-07-15 14:30 | 37.88 | 35.93
2017-07-15 15:00 | 38.36 | 36.47
2017-07-15 15:30 | 38.82 | 36.98
2017-07-15 16:00 | 40.12 | 38.36
2017-07-15 16:30 | 42.28 | 40.63
2017-07-15 17:00 | 42.64 | 41.04
2017-07-15 17:30 | 44.72 | 43.2
2017-07-15 18:00 | 47.71 | 46.26
2017-07-15 18:30 | 50.33 | 48.93
2017-07-15 19:00 | 48.98 | 47.55
2017-07-15 19:30 | 46.72 | 45.22
2017-07-15 20:00 | 44.92 | 43.38
2017-07-15 20:30 | 43.56 | 41.98
2017-07-15 21:00 | 42.31 | 40.69
2017-07-15 21:30 | 40.9 | 39.26
2017-07-15 22:00 | 39.08 | 37.4
2017-07-15 22:30 | 37.85 | 36.15
2017-07-15 23:00 | 38.72 | 37.07
2017-07-15 23:30 | 35.83 | 33.92
2017-07-16 | 34.72 | 32.66
2017-07-16 00:30 | 33.87 | 31.77
2017-07-16 01:00 | 31.8 | 29.58
2017-07-16 01:30 | 31.07 | 28.79
2017-07-16 02:00 | 30.52 | 28.21
2017-07-16 02:30 | 30.21 | 27.88
2017-07-16 03:00 | 28.54 | 27.69
2017-07-16 03:30 | 27.58 | 27.52
2017-07-16 04:00 | 27.38 | 27.32
2017-07-16 04:30 | 27.49 | 27.43
2017-07-16 05:00 | 27.88 | 27.83
2017-07-16 05:30 | 28.25 | 28.2
2017-07-16 06:00 | 29.1 | 29.03
2017-07-16 06:30 | 30.3 | 30.23
2017-07-16 07:00 | 30.54 | 30.49
2017-07-16 07:30 | 31.82 | 31.76
2017-07-16 08:00 | 33.54 | 33.47
2017-07-16 08:30 | 35.34 | 35.25
2017-07-16 09:00 | 36.35 | 36.21
2017-07-16 09:30 | 36.71 | 36.5
2017-07-16 10:00 | 37.44 | 37.1
2017-07-16 10:30 | 37.96 | 37.54
2017-07-16 11:00 | 37.23 | 36.72
2017-07-16 11:30 | 36.24 | 35.7
2017-07-16 12:00 | 35.91 | 35.32
2017-07-16 12:30 | 35.79 | 35.24
2017-07-16 13:00 | 34.51 | 33.95
2017-07-16 13:30 | 34.24 | 33.67
2017-07-16 14:00 | 34.2 | 33.66
2017-07-16 14:30 | 34.15 | 33.65
2017-07-16 15:00 | 34.34 | 33.88
2017-07-16 15:30 | 34.98 | 34.59
2017-07-16 16:00 | 36.38 | 36.05
2017-07-16 16:30 | 38.74 | 38.44
2017-07-16 17:00 | 39.98 | 39.71
2017-07-16 17:30 | 42.7 | 42.42
2017-07-16 18:00 | 46.51 | 46.14
2017-07-16 18:30 | 50.26 | 49.78
2017-07-16 19:00 | 49.65 | 49.15
2017-07-16 19:30 | 47.16 | 46.68
2017-07-16 20:00 | 44.44 | 44.04
2017-07-16 20:30 | 42.83 | 42.46
2017-07-16 21:00 | 41.44 | 41.1
2017-07-16 21:30 | 39.32 | 39.07
2017-07-16 22:00 | 37.09 | 36.9
2017-07-16 22:30 | 35 | 34.85
2017-07-16 23:00 | 35.75 | 35.63
2017-07-16 23:30 | 32.68 | 32.57
2017-07-17 | 31.38 | 31.28
2017-07-17 00:30 | 30.57 | 30.47
2017-07-17 01:00 | 29.37 | 29.28
2017-07-17 01:30 | 28.53 | 28.44
2017-07-17 02:00 | 27.98 | 27.89
2017-07-17 02:30 | 27.72 | 27.64
2017-07-17 03:00 | 27.77 | 27.68
2017-07-17 03:30 | 27.96 | 27.88
2017-07-17 04:00 | 28.55 | 28.46
2017-07-17 04:30 | 29.51 | 29.41
2017-07-17 05:00 | 30.75 | 30.64
2017-07-17 05:30 | 33.3 | 33.11
2017-07-17 06:00 | 37.06 | 36.7
2017-07-17 06:30 | 42.97 | 42.3
2017-07-17 07:00 | 47.62 | 46.67
2017-07-17 07:30 | 52.33 | 51.87
2017-07-17 08:00 | 53.4 | 53.18
2017-07-17 08:30 | 53.92 | 53.52
2017-07-17 09:00 | 52.71 | 52.34
2017-07-17 09:30 | 51.83 | 51.65
2017-07-17 10:00 | 50.85 | 50.61
2017-07-17 10:30 | 52.78 | 52.41
2017-07-17 11:00 | 52.09 | 51.61
2017-07-17 11:30 | 51.47 | 50.89
2017-07-17 12:00 | 52.12 | 51.45
2017-07-17 12:30 | 51.75 | 51.14
2017-07-17 13:00 | 51.71 | 51.06
2017-07-17 13:30 | 52.77 | 52.08
2017-07-17 14:00 | 52.66 | 52.01
2017-07-17 14:30 | 52.98 | 52.38
2017-07-17 15:00 | 52.94 | 52.43
2017-07-17 15:30 | 52.84 | 52.42
2017-07-17 16:00 | 53.07 | 52.82
2017-07-17 16:30 | 53.24 | 53.14
2017-07-17 17:00 | 52.65 | 52.6
2017-07-17 17:30 | 53.61 | 53.59
2017-07-17 18:00 | 54.45 | 54.43
2017-07-17 18:30 | 57.2 | 57.16
2017-07-17 19:00 | 56.46 | 56.4
2017-07-17 19:30 | 53.47 | 53.42
2017-07-17 20:00 | 50.41 | 50.38
2017-07-17 20:30 | 47.76 | 47.73
2017-07-17 21:00 | 45.42 | 45.4
2017-07-17 21:30 | 43 | 42.96
2017-07-17 22:00 | 40.53 | 40.43
2017-07-17 22:30 | 39.19 | 39.01
2017-07-17 23:00 | 38.58 | 38.33
2017-07-17 23:30 | 35.12 | 34.8
2017-07-18 | 32.98 | 32.89
2017-07-18 00:30 | 32.07 | 31.95
2017-07-18 01:00 | 30.36 | 30.25
2017-07-18 01:30 | 29.67 | 29.56
2017-07-18 02:00 | 29 | 28.89
2017-07-18 02:30 | 28.49 | 28.39
2017-07-18 03:00 | 27.85 | 27.76
2017-07-18 03:30 | 28.1 | 28
2017-07-18 04:00 | 28.57 | 28.47
2017-07-18 04:30 | 29.62 | 29.52
2017-07-18 05:00 | 30.89 | 30.78
2017-07-18 05:30 | 33.87 | 33.64
2017-07-18 06:00 | 36.88 | 36.48
2017-07-18 06:30 | 42.85 | 42.11
2017-07-18 07:00 | 47.49 | 46.5
2017-07-18 07:30 | 53.61 | 53.19
2017-07-18 08:00 | 54.9 | 54.61
2017-07-18 08:30 | 55.97 | 55.43
2017-07-18 09:00 | 55.35 | 55.01
2017-07-18 09:30 | 53.99 | 53.73
2017-07-18 10:00 | 53.18 | 52.8
2017-07-18 10:30 | 54.44 | 53.91
2017-07-18 11:00 | 54.62 | 53.91
2017-07-18 11:30 | 56.08 | 55.21
2017-07-18 12:00 | 54.04 | 53.22
2017-07-18 12:30 | 54.44 | 53.69
2017-07-18 13:00 | 54.43 | 53.67
2017-07-18 13:30 | 54.1 | 53.27
2017-07-18 14:00 | 54.49 | 53.66
2017-07-18 14:30 | 53.88 | 53.15
2017-07-18 15:00 | 53.94 | 53.21
2017-07-18 15:30 | 54.63 | 54.03
2017-07-18 16:00 | 54.99 | 54.63
2017-07-18 16:30 | 55.5 | 55.31
2017-07-18 17:00 | 55.18 | 55.11
2017-07-18 17:30 | 54.96 | 54.93
2017-07-18 18:00 | 56.23 | 56.21
2017-07-18 18:30 | 58.75 | 58.73
2017-07-18 19:00 | 58.06 | 58.04
2017-07-18 19:30 | 54.18 | 54.14
2017-07-18 20:00 | 51.27 | 51.19
2017-07-18 20:30 | 48.95 | 48.8
2017-07-18 21:00 | 46.86 | 46.64
2017-07-18 21:30 | 44.46 | 44.37
2017-07-18 22:00 | 42.02 | 41.97
2017-07-18 22:30 | 39.58 | 39.47
2017-07-18 23:00 | 39.6 | 39.44
2017-07-18 23:30 | 35.05 | 35
2017-07-19 | 33.44 | 33.41
2017-07-19 00:30 | 32.97 | 32.94
2017-07-19 01:00 | 30.9 | 30.81
2017-07-19 01:30 | 29.98 | 29.85
2017-07-19 02:00 | 29.41 | 29.3
2017-07-19 02:30 | 29.35 | 29.25
2017-07-19 03:00 | 28.49 | 28.39
2017-07-19 03:30 | 28.37 | 28.27
2017-07-19 04:00 | 29.08 | 28.98
2017-07-19 04:30 | 30.03 | 29.93
2017-07-19 05:00 | 31.08 | 30.97
2017-07-19 05:30 | 33.71 | 33.52
2017-07-19 06:00 | 36.7 | 36.39
2017-07-19 06:30 | 42.84 | 42.19
2017-07-19 07:00 | 48.3 | 47.54
2017-07-19 07:30 | 53.82 | 53.21
2017-07-19 08:00 | 55.89 | 55.31
2017-07-19 08:30 | 55.33 | 55.07
2017-07-19 09:00 | 54.05 | 53.89
2017-07-19 09:30 | 52.99 | 52.77
2017-07-19 10:00 | 52 | 51.71
2017-07-19 10:30 | 52.82 | 52.37
2017-07-19 11:00 | 52.93 | 52.37
2017-07-19 11:30 | 53.67 | 52.98
2017-07-19 12:00 | 53.91 | 53.15
2017-07-19 12:30 | 54.18 | 53.48
2017-07-19 13:00 | 53.84 | 53.17
2017-07-19 13:30 | 55.06 | 54.34
2017-07-19 14:00 | 55.33 | 54.51
2017-07-19 14:30 | 54.97 | 54.28
2017-07-19 15:00 | 55.14 | 54.54
2017-07-19 15:30 | 55.18 | 54.74
2017-07-19 16:00 | 56.09 | 55.74
2017-07-19 16:30 | 55.45 | 55.3
2017-07-19 17:00 | 54.65 | 54.58
2017-07-19 17:30 | 54.3 | 54.27
2017-07-19 18:00 | 54.76 | 54.74
2017-07-19 18:30 | 57.41 | 57.4
2017-07-19 19:00 | 56.97 | 56.94
2017-07-19 19:30 | 53.3 | 53.24
2017-07-19 20:00 | 50.66 | 50.53
2017-07-19 20:30 | 48.27 | 48.08
2017-07-19 21:00 | 45.85 | 45.7
2017-07-19 21:30 | 42.96 | 42.88
2017-07-19 22:00 | 40.21 | 40.15
2017-07-19 22:30 | 38.08 | 38.04
2017-07-19 23:00 | 37.85 | 37.82
2017-07-19 23:30 | 34.32 | 34.26
2017-07-20 | 33.19 | 33.08
2017-07-20 00:30 | 32.45 | 32.36
2017-07-20 01:00 | 30.23 | 30.13
2017-07-20 01:30 | 29.26 | 29.16
2017-07-20 02:00 | 28.51 | 28.42
2017-07-20 02:30 | 27.7 | 27.63
2017-07-20 03:00 | 27.67 | 27.61
2017-07-20 03:30 | 27.69 | 27.63
2017-07-20 04:00 | 27.77 | 27.7
2017-07-20 04:30 | 28.92 | 28.85
2017-07-20 05:00 | 30.61 | 30.53
2017-07-20 05:30 | 33.84 | 33.72
2017-07-20 06:00 | 37.3 | 37.08
2017-07-20 06:30 | 42.98 | 42.52
2017-07-20 07:00 | 48.21 | 47.51
2017-07-20 07:30 | 54.39 | 53.9
2017-07-20 08:00 | 54.84 | 54.31
2017-07-20 08:30 | 53.45 | 52.69
2017-07-20 09:00 | 52.04 | 51.11
2017-07-20 09:30 | 50.5 | 49.42
2017-07-20 10:00 | 48.65 | 47.9
2017-07-20 10:30 | 48.1 | 47.59
2017-07-20 11:00 | 47.57 | 47.42
2017-07-20 11:30 | 47.95 | 47.77
2017-07-20 12:00 | 48.34 | 48.15
2017-07-20 12:30 | 47.98 | 47.82
2017-07-20 13:00 | 47.6 | 47.43
2017-07-20 13:30 | 47.63 | 47.44
2017-07-20 14:00 | 47.17 | 46.99
2017-07-20 14:30 | 47.29 | 47.12
2017-07-20 15:00 | 47.91 | 47.75
2017-07-20 15:30 | 49.35 | 49.24
2017-07-20 16:00 | 50.71 | 50.65
2017-07-20 16:30 | 50.4 | 50.37
2017-07-20 17:00 | 50.02 | 50
2017-07-20 17:30 | 50.71 | 50.63
2017-07-20 18:00 | 53.36 | 53.28
2017-07-20 18:30 | 57.05 | 57
2017-07-20 19:00 | 56.85 | 56.77
2017-07-20 19:30 | 54.1 | 53.97
2017-07-20 20:00 | 51.75 | 51.57
2017-07-20 20:30 | 50.11 | 49.85
2017-07-20 21:00 | 48.17 | 47.95
2017-07-20 21:30 | 45.26 | 45.2
2017-07-20 22:00 | 42.14 | 42.09
2017-07-20 22:30 | 40.21 | 40.13
2017-07-20 23:00 | 39.55 | 39.35
2017-07-20 23:30 | 35.67 | 35.51
2017-07-21 | 33.95 | 33.82
2017-07-21 00:30 | 32.92 | 32.81
2017-07-21 01:00 | 31.32 | 31.2
2017-07-21 01:30 | 30.43 | 30.33
2017-07-21 02:00 | 29.7 | 29.61
2017-07-21 02:30 | 29.52 | 29.44
2017-07-21 03:00 | 29.02 | 28.95
2017-07-21 03:30 | 29 | 28.93
2017-07-21 04:00 | 29.18 | 29.11
2017-07-21 04:30 | 30.21 | 30.13
2017-07-21 05:00 | 31.99 | 31.89
2017-07-21 05:30 | 35.12 | 35
2017-07-21 06:00 | 38.54 | 38.29
2017-07-21 06:30 | 44.77 | 44.23
2017-07-21 07:00 | 50.04 | 49.35
2017-07-21 07:30 | 55.12 | 54.69
2017-07-21 08:00 | 55.52 | 54.92
2017-07-21 08:30 | 54.48 | 53.89
2017-07-21 09:00 | 52.27 | 51.95
2017-07-21 09:30 | 49.74 | 49.44
2017-07-21 10:00 | 47.7 | 47.57
2017-07-21 10:30 | 46.81 | 46.74
2017-07-21 11:00 | 46.33 | 46.26
2017-07-21 11:30 | 45.66 | 45.56
2017-07-21 12:00 | 45.39 | 45.3
2017-07-21 12:30 | 46.07 | 45.99
2017-07-21 13:00 | 44.92 | 44.84
2017-07-21 13:30 | 44.92 | 44.84
2017-07-21 14:00 | 44.83 | 44.76
2017-07-21 14:30 | 44.33 | 44.27
2017-07-21 15:00 | 44.57 | 44.52
2017-07-21 15:30 | 44.77 | 44.73
2017-07-21 16:00 | 45.51 | 45.48
2017-07-21 16:30 | 46.97 | 46.93
2017-07-21 17:00 | 47.34 | 47.25
2017-07-21 17:30 | 48.12 | 47.98
2017-07-21 18:00 | 50.21 | 50.06
2017-07-21 18:30 | 52.87 | 52.68
2017-07-21 19:00 | 52.7 | 52.54
2017-07-21 19:30 | 49.79 | 49.68
2017-07-21 20:00 | 47.23 | 47.15
2017-07-21 20:30 | 45.68 | 45.62
2017-07-21 21:00 | 44.14 | 44.09
2017-07-21 21:30 | 42.42 | 42.37
2017-07-21 22:00 | 40.27 | 40.23
2017-07-21 22:30 | 38.59 | 38.56
2017-07-21 23:00 | 38.93 | 38.91
2017-07-21 23:30 | 35.39 | 35.29
2017-07-22 | 33.93 | 33.83
2017-07-22 00:30 | 32.42 | 32.34
2017-07-22 01:00 | 30.62 | 30.53
2017-07-22 01:30 | 29.93 | 29.86
2017-07-22 02:00 | 29.31 | 29.24
2017-07-22 02:30 | 28.49 | 28.43
2017-07-22 03:00 | 28.42 | 28.36
2017-07-22 03:30 | 27.88 | 27.82
2017-07-22 04:00 | 28.06 | 28
2017-07-22 04:30 | 28.61 | 28.55
2017-07-22 05:00 | 29.31 | 29.24
2017-07-22 05:30 | 30.27 | 30.2
2017-07-22 06:00 | 31.88 | 31.8
2017-07-22 06:30 | 35.49 | 35.38
2017-07-22 07:00 | 37.23 | 37.13
2017-07-22 07:30 | 39.75 | 39.63
2017-07-22 08:00 | 40.71 | 40.51
2017-07-22 08:30 | 41.4 | 41.13
2017-07-22 09:00 | 40.88 | 40.53
2017-07-22 09:30 | 39.6 | 39.21
2017-07-22 10:00 | 38.56 | 38.08
2017-07-22 10:30 | 37.57 | 37.01
2017-07-22 11:00 | 36.48 | 35.84
2017-07-22 11:30 | 35.93 | 35.19
2017-07-22 12:00 | 34.81 | 34.09
2017-07-22 12:30 | 34.72 | 34.08
2017-07-22 13:00 | 33.67 | 33.04
2017-07-22 13:30 | 33.77 | 33.1
2017-07-22 14:00 | 32.26 | 31.68
2017-07-22 14:30 | 31.66 | 31.12
2017-07-22 15:00 | 32 | 31.53
2017-07-22 15:30 | 32.79 | 32.36
2017-07-22 16:00 | 34.21 | 33.85
2017-07-22 16:30 | 36.06 | 35.78
2017-07-22 17:00 | 37.17 | 36.94
2017-07-22 17:30 | 39.41 | 39.18
2017-07-22 18:00 | 42.1 | 41.83
2017-07-22 18:30 | 44.4 | 44.06
2017-07-22 19:00 | 43.6 | 43.28
2017-07-22 19:30 | 41.33 | 41.06
2017-07-22 20:00 | 40.24 | 40
2017-07-22 20:30 | 38.65 | 38.45
2017-07-22 21:00 | 37.2 | 37.04
2017-07-22 21:30 | 36.11 | 35.99
2017-07-22 22:00 | 34.9 | 34.79
2017-07-22 22:30 | 33.81 | 33.72
2017-07-22 23:00 | 34.38 | 34.29
2017-07-22 23:30 | 31.74 | 31.66
2017-07-23 | 30.46 | 30.39
2017-07-23 00:30 | 29.1 | 29.04
2017-07-23 01:00 | 27.3 | 27.24
2017-07-23 01:30 | 26.46 | 26.41
2017-07-23 02:00 | 26.33 | 26.27
2017-07-23 02:30 | 25.93 | 25.88
2017-07-23 03:00 | 25.26 | 25.21
2017-07-23 03:30 | 25.08 | 25.03
2017-07-23 04:00 | 25.52 | 25.47
2017-07-23 04:30 | 25.62 | 25.57
2017-07-23 05:00 | 25.87 | 25.82
2017-07-23 05:30 | 26.71 | 26.66
2017-07-23 06:00 | 27.33 | 27.28
2017-07-23 06:30 | 28.49 | 28.43
2017-07-23 07:00 | 28.97 | 28.92
2017-07-23 07:30 | 30.7 | 30.65
2017-07-23 08:00 | 32.02 | 31.96
2017-07-23 08:30 | 33.9 | 33.83
2017-07-23 09:00 | 34.75 | 34.67
2017-07-23 09:30 | 33.89 | 33.79
2017-07-23 10:00 | 33.6 | 33.46
2017-07-23 10:30 | 32.93 | 32.7
2017-07-23 11:00 | 32.57 | 32.3
2017-07-23 11:30 | 32.75 | 32.42
2017-07-23 12:00 | 32.7 | 32.35
2017-07-23 12:30 | 32.69 | 32.34
2017-07-23 13:00 | 32.17 | 31.77
2017-07-23 13:30 | 32.11 | 31.72
2017-07-23 14:00 | 31.98 | 31.61
2017-07-23 14:30 | 32 | 31.68
2017-07-23 15:00 | 32.78 | 32.48
2017-07-23 15:30 | 33.51 | 33.23
2017-07-23 16:00 | 34.87 | 34.59
2017-07-23 16:30 | 36.58 | 36.35
2017-07-23 17:00 | 37.56 | 37.34
2017-07-23 17:30 | 40.88 | 40.64
2017-07-23 18:00 | 44.05 | 43.75
2017-07-23 18:30 | 47.39 | 47.01
2017-07-23 19:00 | 46.89 | 46.51
2017-07-23 19:30 | 44.21 | 43.88
2017-07-23 20:00 | 41.93 | 41.63
2017-07-23 20:30 | 39.96 | 39.71
2017-07-23 21:00 | 38.22 | 38.02
2017-07-23 21:30 | 36.09 | 35.96
2017-07-23 22:00 | 34.11 | 33.99
2017-07-23 22:30 | 32.62 | 32.51
2017-07-23 23:00 | 32.92 | 32.83
2017-07-23 23:30 | 29.9 | 29.81
2017-07-24 | 28.33 | 28.25
2017-07-24 00:30 | 28.1 | 28.02
2017-07-24 01:00 | 26.66 | 26.59
2017-07-24 01:30 | 25.88 | 25.82
2017-07-24 02:00 | 25.95 | 25.88
2017-07-24 02:30 | 25.55 | 25.49
2017-07-24 03:00 | 25.41 | 25.35
2017-07-24 03:30 | 25.72 | 25.66
2017-07-24 04:00 | 26.46 | 26.4
2017-07-24 04:30 | 27.02 | 26.95
2017-07-24 05:00 | 28.37 | 28.3
2017-07-24 05:30 | 31.37 | 31.25
2017-07-24 06:00 | 34.58 | 34.38
2017-07-24 06:30 | 39.94 | 39.48
2017-07-24 07:00 | 44.68 | 43.99
2017-07-24 07:30 | 49.62 | 49.03
2017-07-24 08:00 | 51.22 | 50.64
2017-07-24 08:30 | 51.23 | 50.43
2017-07-24 09:00 | 50.07 | 49.43
2017-07-24 09:30 | 49.4 | 48.91
2017-07-24 10:00 | 49.12 | 48.51
2017-07-24 10:30 | 49.26 | 48.54
2017-07-24 11:00 | 49.59 | 48.68
2017-07-24 11:30 | 49.46 | 49.11
2017-07-24 12:00 | 49.78 | 49.4
2017-07-24 12:30 | 49.57 | 49.28
2017-07-24 13:00 | 48.59 | 48.28
2017-07-24 13:30 | 48.48 | 48.18
2017-07-24 14:00 | 49.15 | 48.82
2017-07-24 14:30 | 49.16 | 48.88
2017-07-24 15:00 | 49.25 | 49
2017-07-24 15:30 | 49.82 | 49.64
2017-07-24 16:00 | 50.06 | 49.95
2017-07-24 16:30 | 49.99 | 49.94
2017-07-24 17:00 | 49.64 | 49.61
2017-07-24 17:30 | 49.87 | 49.82
2017-07-24 18:00 | 51.96 | 51.89
2017-07-24 18:30 | 53.9 | 53.83
2017-07-24 19:00 | 53.13 | 53.03
2017-07-24 19:30 | 50.42 | 50.26
2017-07-24 20:00 | 47.82 | 47.58
2017-07-24 20:30 | 45.61 | 45.25
2017-07-24 21:00 | 43.62 | 43.16
2017-07-24 21:30 | 41.01 | 40.64
2017-07-24 22:00 | 38.65 | 38.43
2017-07-24 22:30 | 36.39 | 36.3
2017-07-24 23:00 | 36.4 | 36.31
2017-07-24 23:30 | 33.47 | 33.33
2017-07-25 | 30.94 | 30.83
2017-07-25 00:30 | 30.29 | 30.18
2017-07-25 01:00 | 28.98 | 28.87
2017-07-25 01:30 | 28.34 | 28.25
2017-07-25 02:00 | 28.2 | 28.1
2017-07-25 02:30 | 27.87 | 27.78
2017-07-25 03:00 | 28.07 | 28
2017-07-25 03:30 | 27.99 | 27.93
2017-07-25 04:00 | 28.09 | 28.02
2017-07-25 04:30 | 29.47 | 29.39
2017-07-25 05:00 | 30.41 | 30.33
2017-07-25 05:30 | 33.54 | 33.41
2017-07-25 06:00 | 37.12 | 36.88
2017-07-25 06:30 | 42.46 | 41.96
2017-07-25 07:00 | 47.76 | 46.99
2017-07-25 07:30 | 53.69 | 53.15
2017-07-25 08:00 | 54.07 | 53.44
2017-07-25 08:30 | 53.13 | 52.37
2017-07-25 09:00 | 51.99 | 51.09
2017-07-25 09:30 | 50.33 | 49.9
2017-07-25 10:00 | 49.91 | 49.68
2017-07-25 10:30 | 49.64 | 49.48
2017-07-25 11:00 | 49.26 | 49.06
2017-07-25 11:30 | 49.01 | 48.74
2017-07-25 12:00 | 49.7 | 49.38
2017-07-25 12:30 | 49.24 | 49.02
2017-07-25 13:00 | 48.7 | 48.48
2017-07-25 13:30 | 49.06 | 48.8
2017-07-25 14:00 | 47.88 | 47.6
2017-07-25 14:30 | 47.9 | 47.66
2017-07-25 15:00 | 48.3 | 48.09
2017-07-25 15:30 | 48.85 | 48.69
2017-07-25 16:00 | 49.43 | 49.33
2017-07-25 16:30 | 49.61 | 49.56
2017-07-25 17:00 | 49.79 | 49.77
2017-07-25 17:30 | 49.83 | 49.78
2017-07-25 18:00 | 51.29 | 51.21
2017-07-25 18:30 | 54.22 | 54.17
2017-07-25 19:00 | 54.29 | 54.21
2017-07-25 19:30 | 51.14 | 51.01
2017-07-25 20:00 | 48.31 | 48.12
2017-07-25 20:30 | 46.24 | 45.94
2017-07-25 21:00 | 44.07 | 43.67
2017-07-25 21:30 | 42.12 | 41.56
2017-07-25 22:00 | 42.17 | 39.05
2017-07-25 22:30 | 45.55 | 36.85
2017-07-25 23:00 | 45.11 | 36.84
2017-07-25 23:30 | 41.91 | 33.21
2017-07-26 | 39.64 | 31.38
2017-07-26 00:30 | 39.44 | 31.05
2017-07-26 01:00 | 38.39 | 29.63
2017-07-26 01:30 | 38.02 | 29.11
2017-07-26 02:00 | 37.5 | 28.35
2017-07-26 02:30 | 37.47 | 28.24
2017-07-26 03:00 | 37.08 | 27.62
2017-07-26 03:30 | 36.78 | 27.2
2017-07-26 04:00 | 36.95 | 27.47
2017-07-26 04:30 | 37.76 | 28.57
2017-07-26 05:00 | 38.55 | 29.69
2017-07-26 05:30 | 40.97 | 33.03
2017-07-26 06:00 | 43.56 | 36.4
2017-07-26 06:30 | 47.6 | 41.48
2017-07-26 07:00 | 51.3 | 46.54
2017-07-26 07:30 | 53.43 | 52.74
2017-07-26 08:00 | 53.59 | 52.94
2017-07-26 08:30 | 53.58 | 52.99
2017-07-26 09:00 | 51.94 | 51.83
2017-07-26 09:30 | 50.71 | 50.64
2017-07-26 10:00 | 49.46 | 49.33
2017-07-26 10:30 | 49.35 | 49.17
2017-07-26 11:00 | 49.24 | 49.01
2017-07-26 11:30 | 49.48 | 49.14
2017-07-26 12:00 | 49.78 | 49.37
2017-07-26 12:30 | 49.88 | 49.48
2017-07-26 13:00 | 49.25 | 48.9
2017-07-26 13:30 | 49.16 | 48.79
2017-07-26 14:00 | 48.91 | 48.59
2017-07-26 14:30 | 48.71 | 48.4
2017-07-26 15:00 | 49 | 48.73
2017-07-26 15:30 | 48.33 | 48.19
2017-07-26 16:00 | 48.7 | 48.63
2017-07-26 16:30 | 49.42 | 49.38
2017-07-26 17:00 | 49.46 | 49.44
2017-07-26 17:30 | 49.92 | 49.88
2017-07-26 18:00 | 51.37 | 51.3
2017-07-26 18:30 | 54.01 | 53.96
2017-07-26 19:00 | 53.4 | 53.3
2017-07-26 19:30 | 51.45 | 51.31
2017-07-26 20:00 | 48.45 | 48.23
2017-07-26 20:30 | 46.13 | 45.82
2017-07-26 21:00 | 44.31 | 43.91
2017-07-26 21:30 | 41.94 | 41.38
2017-07-26 22:00 | 39.17 | 38.98
2017-07-26 22:30 | 37.74 | 37.66
2017-07-26 23:00 | 37.51 | 37.46
2017-07-26 23:30 | 33.76 | 33.6
2017-07-27 | 31.45 | 31.33
2017-07-27 00:30 | 30.87 | 30.76
2017-07-27 01:00 | 29.47 | 29.38
2017-07-27 01:30 | 28.77 | 28.66
2017-07-27 02:00 | 28.12 | 28.03
2017-07-27 02:30 | 27.96 | 27.87
2017-07-27 03:00 | 28.36 | 28.28
2017-07-27 03:30 | 27.77 | 27.7
2017-07-27 04:00 | 28.21 | 28.13
2017-07-27 04:30 | 29.37 | 29.29
2017-07-27 05:00 | 30.65 | 30.57
2017-07-27 05:30 | 33.41 | 33.26
2017-07-27 06:00 | 37.02 | 36.71
2017-07-27 06:30 | 42.21 | 41.61
2017-07-27 07:00 | 47 | 46.17
2017-07-27 07:30 | 52.11 | 51.47
2017-07-27 08:00 | 52.44 | 52.07
2017-07-27 08:30 | 51.52 | 51.26
2017-07-27 09:00 | 49.93 | 49.57
2017-07-27 09:30 | 47.85 | 47.72
2017-07-27 10:00 | 47.43 | 47.35
2017-07-27 10:30 | 47.71 | 47.58
2017-07-27 11:00 | 47.33 | 47.13
2017-07-27 11:30 | 47.25 | 47
2017-07-27 12:00 | 47.8 | 47.5
2017-07-27 12:30 | 48.31 | 48.04
2017-07-27 13:00 | 48.46 | 48.19
2017-07-27 13:30 | 49.33 | 49.01
2017-07-27 14:00 | 47.94 | 47.63
2017-07-27 14:30 | 48.11 | 47.83
2017-07-27 15:00 | 48.51 | 48.25
2017-07-27 15:30 | 48.29 | 48.11
2017-07-27 16:00 | 49.07 | 48.94
2017-07-27 16:30 | 47.74 | 47.7
2017-07-27 17:00 | 47.74 | 47.71
2017-07-27 17:30 | 47.78 | 47.72
2017-07-27 18:00 | 49.93 | 49.85
2017-07-27 18:30 | 52.14 | 52.05
2017-07-27 19:00 | 52 | 51.88
2017-07-27 19:30 | 49.28 | 49.08
2017-07-27 20:00 | 46.81 | 46.53
2017-07-27 20:30 | 44.98 | 44.6
2017-07-27 21:00 | 44.1 | 43.1
2017-07-27 21:30 | 42.53 | 39.85
2017-07-27 22:00 | 40.44 | 37.54
2017-07-27 22:30 | 38.23 | 35.43
2017-07-27 23:00 | 37.51 | 35.06
2017-07-27 23:30 | 33.99 | 31.49
2017-07-28 | 32.66 | 30.04
2017-07-28 00:30 | 31.85 | 29.09
2017-07-28 01:00 | 30.68 | 27.79
2017-07-28 01:30 | 29.91 | 26.91
2017-07-28 02:00 | 29.22 | 26.11
2017-07-28 02:30 | 28.82 | 25.61
2017-07-28 03:00 | 28.86 | 25.64
2017-07-28 03:30 | 28.79 | 25.55
2017-07-28 04:00 | 29.21 | 26.03
2017-07-28 04:30 | 29.71 | 26.62
2017-07-28 05:00 | 30.86 | 27.95
2017-07-28 05:30 | 33.35 | 30.8
2017-07-28 06:00 | 36.31 | 34.08
2017-07-28 06:30 | 41.04 | 39.24
2017-07-28 07:00 | 45.66 | 44.16
2017-07-28 07:30 | 52.12 | 50.76
2017-07-28 08:00 | 52.52 | 51.22
2017-07-28 08:30 | 51.53 | 50.26
2017-07-28 09:00 | 49.93 | 48.61
2017-07-28 09:30 | 48.76 | 47.25
2017-07-28 10:00 | 47.86 | 46.08
2017-07-28 10:30 | 47.94 | 46.24
2017-07-28 11:00 | 48.7 | 47.06
2017-07-28 11:30 | 48.38 | 46.78
2017-07-28 12:00 | 48.96 | 47.4
2017-07-28 12:30 | 49.61 | 48.05
2017-07-28 13:00 | 49.34 | 47.77
2017-07-28 13:30 | 48.85 | 47.25
2017-07-28 14:00 | 48.94 | 47.34
2017-07-28 14:30 | 48.95 | 47.32
2017-07-28 15:00 | 48.49 | 46.8
2017-07-28 15:30 | 48.43 | 46.7
2017-07-28 16:00 | 48.2 | 46.41
2017-07-28 16:30 | 49.23 | 47.41
2017-07-28 17:00 | 48.8 | 46.85
2017-07-28 17:30 | 48.92 | 46.9
2017-07-28 18:00 | 50.34 | 48.37
2017-07-28 18:30 | 51.71 | 49.82
2017-07-28 19:00 | 51.37 | 49.43
2017-07-28 19:30 | 49.07 | 47.01
2017-07-28 20:00 | 47.27 | 45.06
2017-07-28 20:30 | 45.58 | 43.22
2017-07-28 21:00 | 43.61 | 41.35
2017-07-28 21:30 | 42.17 | 39.82
2017-07-28 22:00 | 40.49 | 37.95
2017-07-28 22:30 | 39.33 | 36.64
2017-07-28 23:00 | 39.23 | 36.6
2017-07-28 23:30 | 35.46 | 32.99
2017-07-29 | 34.63 | 32.18
2017-07-29 00:30 | 33.62 | 31.04
2017-07-29 01:00 | 31.94 | 29.2
2017-07-29 01:30 | 31.17 | 28.33
2017-07-29 02:00 | 30.5 | 27.57
2017-07-29 02:30 | 30.34 | 27.38
2017-07-29 03:00 | 30.22 | 27.24
2017-07-29 03:30 | 29.91 | 26.85
2017-07-29 04:00 | 29.76 | 26.65
2017-07-29 04:30 | 29.88 | 26.79
2017-07-29 05:00 | 30.27 | 27.24
2017-07-29 05:30 | 30.95 | 28.02
2017-07-29 06:00 | 32.08 | 29.31
2017-07-29 06:30 | 34.03 | 31.51
2017-07-29 07:00 | 35.7 | 33.31
2017-07-29 07:30 | 37.69 | 35.49
2017-07-29 08:00 | 38.75 | 36.68
2017-07-29 08:30 | 40 | 38.06
2017-07-29 09:00 | 40.79 | 38.94
2017-07-29 09:30 | 40.13 | 38.28
2017-07-29 10:00 | 39.29 | 37.43
2017-07-29 10:30 | 38.89 | 37.08
2017-07-29 11:00 | 38.21 | 36.41
2017-07-29 11:30 | 37.79 | 35.72
2017-07-29 12:00 | 37.21 | 35.05
2017-07-29 12:30 | 37.14 | 34.94
2017-07-29 13:00 | 36.35 | 34.1
2017-07-29 13:30 | 35.43 | 33.08
2017-07-29 14:00 | 35.63 | 33.28
2017-07-29 14:30 | 35.85 | 33.51
2017-07-29 15:00 | 36.3 | 33.98
2017-07-29 15:30 | 36.53 | 34.19
2017-07-29 16:00 | 37.91 | 35.64
2017-07-29 16:30 | 39.94 | 37.77
2017-07-29 17:00 | 40.39 | 38.23
2017-07-29 17:30 | 42.53 | 40.47
2017-07-29 18:00 | 44.38 | 42.45
2017-07-29 18:30 | 46.45 | 44.67
2017-07-29 19:00 | 45.83 | 44.01
2017-07-29 19:30 | 44.1 | 42.18
2017-07-29 20:00 | 42.06 | 40
2017-07-29 20:30 | 40.8 | 38.64
2017-07-29 21:00 | 39.59 | 37.31
2017-07-29 21:30 | 38.67 | 36.29
2017-07-29 22:00 | 37.34 | 34.8
2017-07-29 22:30 | 36.85 | 34.21
2017-07-29 23:00 | 36.92 | 34.33
2017-07-29 23:30 | 33.57 | 30.97
2017-07-30 | 32.24 | 29.48
2017-07-30 00:30 | 31.75 | 28.91
2017-07-30 01:00 | 30.6 | 27.62
2017-07-30 01:30 | 29.7 | 26.58
2017-07-30 02:00 | 29.46 | 26.29
2017-07-30 02:30 | 29.21 | 26.01
2017-07-30 03:00 | 29.05 | 25.83
2017-07-30 03:30 | 29.03 | 25.78
2017-07-30 04:00 | 29.18 | 25.96
2017-07-30 04:30 | 29.07 | 25.84
2017-07-30 05:00 | 29.33 | 26.13
2017-07-30 05:30 | 29.98 | 26.9
2017-07-30 06:00 | 31.06 | 28.13
2017-07-30 06:30 | 31.97 | 29.12
2017-07-30 07:00 | 32.43 | 29.59
2017-07-30 07:30 | 33.56 | 30.84
2017-07-30 08:00 | 34.51 | 31.91
2017-07-30 08:30 | 35.36 | 32.88
2017-07-30 09:00 | 35.86 | 33.49
2017-07-30 09:30 | 35.7 | 33.35
2017-07-30 10:00 | 35.72 | 33.44
2017-07-30 10:30 | 34.23 | 31.88
2017-07-30 11:00 | 34.16 | 31.83
2017-07-30 11:30 | 33.49 | 31.14
2017-07-30 12:00 | 33.05 | 30.69
2017-07-30 12:30 | 33.99 | 31.7
2017-07-30 13:00 | 33.65 | 31.35
2017-07-30 13:30 | 34.1 | 31.85
2017-07-30 14:00 | 34.03 | 31.79
2017-07-30 14:30 | 34.23 | 31.98
2017-07-30 15:00 | 34.72 | 32.49
2017-07-30 15:30 | 36.77 | 34.68
2017-07-30 16:00 | 37.69 | 35.64
2017-07-30 16:30 | 39.16 | 37.17
2017-07-30 17:00 | 39.41 | 37.43
2017-07-30 17:30 | 41.93 | 40.11
2017-07-30 18:00 | 44.9 | 43.25
2017-07-30 18:30 | 48.31 | 46.86
2017-07-30 19:00 | 48.14 | 46.68
2017-07-30 19:30 | 45.44 | 43.84
2017-07-30 20:00 | 43.22 | 41.52
2017-07-30 20:30 | 41.05 | 39.19
2017-07-30 21:00 | 39.87 | 37.92
2017-07-30 21:30 | 38.16 | 36.07
2017-07-30 22:00 | 36.51 | 34.26
2017-07-30 22:30 | 35.17 | 32.79
2017-07-30 23:00 | 35.61 | 33.25
2017-07-30 23:30 | 33 | 30.37
2017-07-31 | 31.63 | 28.84
2017-07-31 00:30 | 31.14 | 28.26
2017-07-31 01:00 | 30.23 | 27.23
2017-07-31 01:30 | 29.83 | 26.78
2017-07-31 02:00 | 29.52 | 26.42
2017-07-31 02:30 | 29.42 | 26.27
2017-07-31 03:00 | 29.45 | 26.31
2017-07-31 03:30 | 29.45 | 26.32
2017-07-31 04:00 | 29.67 | 26.55
2017-07-31 04:30 | 30.35 | 27.34
2017-07-31 05:00 | 31.46 | 28.62
2017-07-31 05:30 | 33.85 | 31.35
2017-07-31 06:00 | 36.5 | 34.29
2017-07-31 06:30 | 41.14 | 39.36
2017-07-31 07:00 | 45.31 | 43.81
2017-07-31 07:30 | 50.64 | 49.24
2017-07-31 08:00 | 52.11 | 50.82
2017-07-31 08:30 | 52.35 | 51.1
2017-07-31 09:00 | 52.17 | 50.82
2017-07-31 09:30 | 51.72 | 50.34
2017-07-31 10:00 | 52.21 | 50.86
2017-07-31 10:30 | 51.34 | 50
2017-07-31 11:00 | 49.76 | 48.43
2017-07-31 11:30 | 50.92 | 49.56
2017-07-31 12:00 | 51.85 | 50.43
2017-07-31 12:30 | 51.24 | 49.82
2017-07-31 13:00 | 50.25 | 48.79
2017-07-31 13:30 | 49.81 | 48.38
2017-07-31 14:00 | 50.59 | 49.18
2017-07-31 14:30 | 50.87 | 49.45
2017-07-31 15:00 | 50.36 | 48.89
2017-07-31 15:30 | 50.97 | 49.47
2017-07-31 16:00 | 51.21 | 49.65
2017-07-31 16:30 | 51.84 | 50.21
2017-07-31 17:00 | 52.14 | 50.47
2017-07-31 17:30 | 51.79 | 49.98
2017-07-31 18:00 | 53.78 | 52
2017-07-31 18:30 | 55.3 | 53.57
2017-07-31 19:00 | 54.53 | 52.74
2017-07-31 19:30 | 51.55 | 49.6
2017-07-31 20:00 | 49.3 | 47.21
2017-07-31 20:30 | 47.21 | 44.94
2017-07-31 21:00 | 45.4 | 42.96
2017-07-31 21:30 | 42.77 | 40.17
2017-07-31 22:00 | 39.01 | 36.35
2017-07-31 22:30 | 37.31 | 34.44
2017-07-31 23:00 | 37.07 | 34.27
2017-07-31 23:30 | 33.41 | 30.73
2017-08-01 | 31.82 | 29.1
2017-08-01 00:30 | 31.3 | 28.49
2017-08-01 01:00 | 30.18 | 27.23
2017-08-01 01:30 | 29.54 | 26.5
2017-08-01 02:00 | 29.12 | 26
2017-08-01 02:30 | 28.99 | 25.82
2017-08-01 03:00 | 28.79 | 25.56
2017-08-01 03:30 | 28.86 | 25.61
2017-08-01 04:00 | 29 | 25.78
2017-08-01 04:30 | 29.92 | 26.84
2017-08-01 05:00 | 30.83 | 27.89
2017-08-01 05:30 | 33.09 | 30.46
2017-08-01 06:00 | 35.63 | 33.32
2017-08-01 06:30 | 40.04 | 38.16
2017-08-01 07:00 | 44.36 | 42.78
2017-08-01 07:30 | 49.98 | 48.59
2017-08-01 08:00 | 51.33 | 50
2017-08-01 08:30 | 50.52 | 49.22
2017-08-01 09:00 | 49.22 | 47.88
2017-08-01 09:30 | 48.1 | 46.61
2017-08-01 10:00 | 47.53 | 46.03
2017-08-01 10:30 | 48.19 | 46.76
2017-08-01 11:00 | 48.21 | 46.8
2017-08-01 11:30 | 48.57 | 47.01
2017-08-01 12:00 | 48.53 | 46.99
2017-08-01 12:30 | 48.46 | 46.89
2017-08-01 13:00 | 47.92 | 46.33
2017-08-01 13:30 | 48 | 46.43
2017-08-01 14:00 | 48.15 | 46.62
2017-08-01 14:30 | 48.52 | 46.91
2017-08-01 15:00 | 48.98 | 47.39
2017-08-01 15:30 | 50.13 | 48.57
2017-08-01 16:00 | 51.2 | 49.64
2017-08-01 16:30 | 51.81 | 50.18
2017-08-01 17:00 | 51.76 | 50.07
2017-08-01 17:30 | 51.95 | 50.16
2017-08-01 18:00 | 53.08 | 51.3
2017-08-01 18:30 | 55.92 | 54.28
2017-08-01 19:00 | 56.98 | 55.35
2017-08-01 19:30 | 53.35 | 51.56
2017-08-01 20:00 | 50.83 | 48.89
2017-08-01 20:30 | 49.12 | 47.04
2017-08-01 21:00 | 46.73 | 44.47
2017-08-01 21:30 | 44.05 | 41.55
2017-08-01 22:00 | 41.44 | 38.69
2017-08-01 22:30 | 40.16 | 37.29
2017-08-01 23:00 | 39.37 | 36.93
2017-08-01 23:30 | 36.32 | 33.75
2017-08-02 | 34.55 | 31.79
2017-08-02 00:30 | 33.76 | 30.86
2017-08-02 01:00 | 32.34 | 29.28
2017-08-02 01:30 | 31.52 | 28.44
2017-08-02 02:00 | 30.81 | 27.96
2017-08-02 02:30 | 30.45 | 27.53
2017-08-02 03:00 | 30.19 | 27.22
2017-08-02 03:30 | 30.35 | 27.37
2017-08-02 04:00 | 30.78 | 27.86
2017-08-02 04:30 | 31.33 | 28.5
2017-08-02 05:00 | 32.3 | 29.62
2017-08-02 05:30 | 34.88 | 32.5
2017-08-02 06:00 | 37.66 | 35.57
2017-08-02 06:30 | 42.87 | 41.2
2017-08-02 07:00 | 46.88 | 45.46
2017-08-02 07:30 | 51.89 | 50.54
2017-08-02 08:00 | 52.78 | 51.51
2017-08-02 08:30 | 53.76 | 53.02
2017-08-02 09:00 | 52.25 | 51.78
2017-08-02 09:30 | 51.92 | 50.62
2017-08-02 10:00 | 51.15 | 49.65
2017-08-02 10:30 | 51.53 | 49.96
2017-08-02 11:00 | 52.22 | 50.63
2017-08-02 11:30 | 52.25 | 50.77
2017-08-02 12:00 | 52.01 | 50.49
2017-08-02 12:30 | 52.1 | 50.45
2017-08-02 13:00 | 51.47 | 49.8
2017-08-02 13:30 | 52.13 | 50.41
2017-08-02 14:00 | 52.33 | 50.62
2017-08-02 14:30 | 52.31 | 50.72
2017-08-02 15:00 | 51.8 | 50.33
2017-08-02 15:30 | 51.11 | 49.66
2017-08-02 16:00 | 51.14 | 49.78
2017-08-02 16:30 | 51.1 | 49.83
2017-08-02 17:00 | 50.21 | 48.98
2017-08-02 17:30 | 50.32 | 49.17
2017-08-02 18:00 | 51.63 | 50.55
2017-08-02 18:30 | 53.16 | 52.12
2017-08-02 19:00 | 53.09 | 52.05
2017-08-02 19:30 | 50.49 | 49.41
2017-08-02 20:00 | 47.94 | 46.83
2017-08-02 20:30 | 45.7 | 44.57
2017-08-02 21:00 | 43.6 | 42.43
2017-08-02 21:30 | 41.35 | 40.17
2017-08-02 22:00 | 39.47 | 37.81
2017-08-02 22:30 | 38.56 | 35.66
2017-08-02 23:00 | 38.34 | 35.41
2017-08-02 23:30 | 34.77 | 31.83
2017-08-03 | 33.83 | 30.77
2017-08-03 00:30 | 32.67 | 29.54
2017-08-03 01:00 | 30.58 | 27.82
2017-08-03 01:30 | 29.94 | 27.23
2017-08-03 02:00 | 29.72 | 26.95
2017-08-03 02:30 | 29.27 | 26.44
2017-08-03 03:00 | 28.85 | 25.95
2017-08-03 03:30 | 28.9 | 25.99
2017-08-03 04:00 | 29.29 | 26.45
2017-08-03 04:30 | 29.92 | 27.16
2017-08-03 05:00 | 31.04 | 28.43
2017-08-03 05:30 | 33.42 | 31.13
2017-08-03 06:00 | 36.15 | 34.15
2017-08-03 06:30 | 41.03 | 39.3
2017-08-03 07:00 | 45.71 | 43.33
2017-08-03 07:30 | 51.09 | 48.9
2017-08-03 08:00 | 53.19 | 51.17
2017-08-03 08:30 | 56.39 | 54.27
2017-08-03 09:00 | 56.85 | 54.64
2017-08-03 09:30 | 55.1 | 52.83
2017-08-03 10:00 | 53.68 | 51.42
2017-08-03 10:30 | 55.07 | 52.96
2017-08-03 11:00 | 56.71 | 54.7
2017-08-03 11:30 | 54.72 | 52.63
2017-08-03 12:00 | 54.85 | 52.81
2017-08-03 12:30 | 54.6 | 52.52
2017-08-03 13:00 | 53.83 | 51.72
2017-08-03 13:30 | 54.28 | 52.22
2017-08-03 14:00 | 54.33 | 52.27
2017-08-03 14:30 | 54.49 | 52.42
2017-08-03 15:00 | 54.48 | 52.37
2017-08-03 15:30 | 54.38 | 52.21
2017-08-03 16:00 | 54.6 | 52.38
2017-08-03 16:30 | 54.05 | 51.68
2017-08-03 17:00 | 53.87 | 51.32
2017-08-03 17:30 | 53.93 | 50.6
2017-08-03 18:00 | 55.36 | 51.72
2017-08-03 18:30 | 57.7 | 54.37
2017-08-03 19:00 | 58.02 | 54.69
2017-08-03 19:30 | 55.46 | 51.41
2017-08-03 20:00 | 53.47 | 49.06
2017-08-03 20:30 | 52.27 | 47.47
2017-08-03 21:00 | 49.22 | 45.74
2017-08-03 21:30 | 44.46 | 42.15
2017-08-03 22:00 | 42.29 | 39.8
2017-08-03 22:30 | 40.12 | 37.41
2017-08-03 23:00 | 40.18 | 37.43
2017-08-03 23:30 | 36.99 | 34.05
2017-08-04 | 34.61 | 31.93
2017-08-04 00:30 | 34.36 | 31.75
2017-08-04 01:00 | 32.44 | 29.99
2017-08-04 01:30 | 31.57 | 29.03
2017-08-04 02:00 | 29.25 | 26.96
2017-08-04 02:30 | 28.8 | 25.94
2017-08-04 03:00 | 30.52 | 27.79
2017-08-04 03:30 | 29.79 | 26.97
2017-08-04 04:00 | 29.54 | 26.71
2017-08-04 04:30 | 29.77 | 27.01
2017-08-04 05:00 | 30.81 | 28.19
2017-08-04 05:30 | 32.89 | 30.54
2017-08-04 06:00 | 36.31 | 34.27
2017-08-04 06:30 | 40.22 | 38.55
2017-08-04 07:00 | 44.25 | 42.49
2017-08-04 07:30 | 48.48 | 46.97
2017-08-04 08:00 | 49.28 | 47.89
2017-08-04 08:30 | 49.37 | 47.94
2017-08-04 09:00 | 48.67 | 47.33
2017-08-04 09:30 | 48.47 | 47.09
2017-08-04 10:00 | 48.59 | 47.18
2017-08-04 10:30 | 49.87 | 48.45
2017-08-04 11:00 | 50.22 | 48.77
2017-08-04 11:30 | 49.49 | 48
2017-08-04 12:00 | 49.49 | 47.96
2017-08-04 12:30 | 50.42 | 48.92
2017-08-04 13:00 | 49.94 | 48.43
2017-08-04 13:30 | 49.92 | 48.41
2017-08-04 14:00 | 49.84 | 48.36
2017-08-04 14:30 | 49.64 | 48.19
2017-08-04 15:00 | 49.5 | 48.07
2017-08-04 15:30 | 49.41 | 48.01
2017-08-04 16:00 | 49.67 | 48.34
2017-08-04 16:30 | 49.74 | 48.47
2017-08-04 17:00 | 48.97 | 47.72
2017-08-04 17:30 | 48.12 | 46.94
2017-08-04 18:00 | 48.8 | 47.67
2017-08-04 18:30 | 50.79 | 49.7
2017-08-04 19:00 | 49.88 | 48.8
2017-08-04 19:30 | 47.53 | 46.42
2017-08-04 20:00 | 45.45 | 44.3
2017-08-04 20:30 | 43.17 | 41.89
2017-08-04 21:00 | 41.33 | 39.93
2017-08-04 21:30 | 40 | 38.58
2017-08-04 22:00 | 39.72 | 38.33
2017-08-04 22:30 | 39.02 | 37.57
2017-08-04 23:00 | 38.54 | 36.97
2017-08-04 23:30 | 36.12 | 34.37
2017-08-05 | 34.5 | 32.54
2017-08-05 00:30 | 32.97 | 30.93
2017-08-05 01:00 | 31.11 | 28.93
2017-08-05 01:30 | 30.34 | 28.12
2017-08-05 02:00 | 29.81 | 27.57
2017-08-05 02:30 | 30.08 | 27.86
2017-08-05 03:00 | 29.16 | 26.89
2017-08-05 03:30 | 28.66 | 26.33
2017-08-05 04:00 | 27.8 | 25.4
2017-08-05 04:30 | 27.89 | 25.51
2017-08-05 05:00 | 28.42 | 26.08
2017-08-05 05:30 | 29.31 | 27.04
2017-08-05 06:00 | 30.79 | 28.6
2017-08-05 06:30 | 32.81 | 30.71
2017-08-05 07:00 | 33.58 | 31.5
2017-08-05 07:30 | 35.73 | 33.73
2017-08-05 08:00 | 37.5 | 35.56
2017-08-05 08:30 | 39.76 | 37.89
2017-08-05 09:00 | 41.41 | 39.58
2017-08-05 09:30 | 40.53 | 38.62
2017-08-05 10:00 | 39.49 | 37.51
2017-08-05 10:30 | 39.91 | 38.11
2017-08-05 11:00 | 40.57 | 38.77
2017-08-05 11:30 | 40.71 | 38.9
2017-08-05 12:00 | 39.94 | 38.11
2017-08-05 12:30 | 39.69 | 37.89
2017-08-05 13:00 | 37.67 | 35.77
2017-08-05 13:30 | 36.44 | 34.47
2017-08-05 14:00 | 37.23 | 35.33
2017-08-05 14:30 | 37.71 | 35.86
2017-08-05 15:00 | 38.02 | 36.21
2017-08-05 15:30 | 37.99 | 36.19
2017-08-05 16:00 | 38.86 | 37.12
2017-08-05 16:30 | 39.66 | 38.01
2017-08-05 17:00 | 40.27 | 38.67
2017-08-05 17:30 | 42.7 | 41.18
2017-08-05 18:00 | 44.66 | 43.2
2017-08-05 18:30 | 45.93 | 44.5
2017-08-05 19:00 | 44.92 | 43.46
2017-08-05 19:30 | 42.91 | 41.38
2017-08-05 20:00 | 41.6 | 40.01
2017-08-05 20:30 | 40.25 | 38.64
2017-08-05 21:00 | 39.12 | 37.49
2017-08-05 21:30 | 37.26 | 35.56
2017-08-05 22:00 | 36.36 | 34.66
2017-08-05 22:30 | 34.83 | 33.08
2017-08-05 23:00 | 34.97 | 33.25
2017-08-05 23:30 | 32.62 | 30.79
2017-08-06 | 31.14 | 29.25
2017-08-06 00:30 | 30.57 | 28.47
2017-08-06 01:00 | 29.55 | 27.28
2017-08-06 01:30 | 29.01 | 26.7
2017-08-06 02:00 | 28.66 | 26.33
2017-08-06 02:30 | 28.71 | 26.39
2017-08-06 03:00 | 28.03 | 25.65
2017-08-06 03:30 | 28 | 25.64
2017-08-06 04:00 | 28.15 | 25.79
2017-08-06 04:30 | 27.97 | 25.6
2017-08-06 05:00 | 28.2 | 25.82
2017-08-06 05:30 | 28.59 | 26.27
2017-08-06 06:00 | 29.43 | 27.14
2017-08-06 06:30 | 30.78 | 28.58
2017-08-06 07:00 | 30.82 | 28.65
2017-08-06 07:30 | 32.2 | 30.11
2017-08-06 08:00 | 33.7 | 31.7
2017-08-06 08:30 | 36.09 | 34.17
2017-08-06 09:00 | 38.88 | 37.05
2017-08-06 09:30 | 38.76 | 36.88
2017-08-06 10:00 | 39.8 | 37.93
2017-08-06 10:30 | 40.17 | 38.3
2017-08-06 11:00 | 38.75 | 36.77
2017-08-06 11:30 | 39.97 | 38.06
2017-08-06 12:00 | 39.95 | 38.21
2017-08-06 12:30 | 38.49 | 36.78
2017-08-06 13:00 | 36.74 | 34.93
2017-08-06 13:30 | 37.05 | 35.23
2017-08-06 14:00 | 36.67 | 34.84
2017-08-06 14:30 | 37.23 | 35.45
2017-08-06 15:00 | 38.18 | 36.46
2017-08-06 15:30 | 36.31 | 34.53
2017-08-06 16:00 | 39.04 | 37.4
2017-08-06 16:30 | 40.77 | 39.21
2017-08-06 17:00 | 40.74 | 39.19
2017-08-06 17:30 | 43.49 | 42.03
2017-08-06 18:00 | 46.08 | 44.7
2017-08-06 18:30 | 47.53 | 46.18
2017-08-06 19:00 | 46.7 | 45.32
2017-08-06 19:30 | 44.52 | 43.11
2017-08-06 20:00 | 42.14 | 40.65
2017-08-06 20:30 | 40.9 | 39.39
2017-08-06 21:00 | 38.96 | 37.39
2017-08-06 21:30 | 36.89 | 35.26
2017-08-06 22:00 | 35.55 | 33.85
2017-08-06 22:30 | 34.09 | 32.35
2017-08-06 23:00 | 34.4 | 32.69
2017-08-06 23:30 | 31.63 | 29.8
2017-08-07 | 30.43 | 28.35
2017-08-07 00:30 | 30.39 | 28.21
2017-08-07 01:00 | 29.09 | 26.82
2017-08-07 01:30 | 28.15 | 25.8
2017-08-07 02:00 | 28 | 25.63
2017-08-07 02:30 | 28.27 | 25.93
2017-08-07 03:00 | 28.16 | 25.81
2017-08-07 03:30 | 28.37 | 26.03
2017-08-07 04:00 | 28.15 | 25.78
2017-08-07 04:30 | 29.23 | 26.97
2017-08-07 05:00 | 29.98 | 27.75
2017-08-07 05:30 | 32.71 | 30.59
2017-08-07 06:00 | 35.87 | 33.86
2017-08-07 06:30 | 40.59 | 38.7
2017-08-07 07:00 | 45.1 | 43.32
2017-08-07 07:30 | 50.63 | 49.02
2017-08-07 08:00 | 52.52 | 51.13
2017-08-07 08:30 | 54.15 | 52.66
2017-08-07 09:00 | 55.78 | 53.57
2017-08-07 09:30 | 55.51 | 53.29
2017-08-07 10:00 | 54.54 | 52.3
2017-08-07 10:30 | 55.67 | 53.54
2017-08-07 11:00 | 56.13 | 54.04
2017-08-07 11:30 | 56.21 | 54.16
2017-08-07 12:00 | 54.72 | 52.63
2017-08-07 12:30 | 54.31 | 52.24
2017-08-07 13:00 | 52 | 49.84
2017-08-07 13:30 | 53.05 | 51.01
2017-08-07 14:00 | 54.02 | 52.06
2017-08-07 14:30 | 54.28 | 52.35
2017-08-07 15:00 | 55.12 | 53.2
2017-08-07 15:30 | 54.85 | 52.87
2017-08-07 16:00 | 54.68 | 52.61
2017-08-07 16:30 | 55.78 | 53.67
2017-08-07 17:00 | 54.24 | 51.98
2017-08-07 17:30 | 53.74 | 50.97
2017-08-07 18:00 | 54.31 | 51.17
2017-08-07 18:30 | 55.92 | 52.98
2017-08-07 19:00 | 55.94 | 52.8
2017-08-07 19:30 | 53.54 | 49.86
2017-08-07 20:00 | 51.79 | 47.7
2017-08-07 20:30 | 49.97 | 45.3
2017-08-07 21:00 | 48.34 | 43.07
2017-08-07 21:30 | 46.64 | 40.5
2017-08-07 22:00 | 44.99 | 37.94
2017-08-07 22:30 | 43.9 | 36.18
2017-08-07 23:00 | 41.58 | 35.67
2017-08-07 23:30 | 39.27 | 32.57
2017-08-08 | 37.96 | 30.57
2017-08-08 00:30 | 35.72 | 30.18
2017-08-08 01:00 | 33.29 | 28.76
2017-08-08 01:30 | 32.33 | 28.28
2017-08-08 02:00 | 31.77 | 27.62
2017-08-08 02:30 | 31.49 | 27.22
2017-08-08 03:00 | 31.52 | 27.23
2017-08-08 03:30 | 31.35 | 27.02
2017-08-08 04:00 | 31.5 | 27.18
2017-08-08 04:30 | 32.04 | 27.8
2017-08-08 05:00 | 32.88 | 28.82
2017-08-08 05:30 | 34.84 | 31.14
2017-08-08 06:00 | 37.66 | 34.41
2017-08-08 06:30 | 41.26 | 38.49
2017-08-08 07:00 | 45.34 | 42.99
2017-08-08 07:30 | 50.45 | 48.34
2017-08-08 08:00 | 50.72 | 48.68
2017-08-08 08:30 | 51.52 | 49.36
2017-08-08 09:00 | 50.78 | 48.4
2017-08-08 09:30 | 49.18 | 46.7
2017-08-08 10:00 | 48.43 | 45.97
2017-08-08 10:30 | 48.33 | 45.9
2017-08-08 11:00 | 48.63 | 46.28
2017-08-08 11:30 | 48.38 | 46.06
2017-08-08 12:00 | 48.16 | 45.85
2017-08-08 12:30 | 48.4 | 46.09
2017-08-08 13:00 | 48.13 | 45.82
2017-08-08 13:30 | 48.54 | 46.25
2017-08-08 14:00 | 48.68 | 46.4
2017-08-08 14:30 | 48.42 | 46.09
2017-08-08 15:00 | 48.63 | 46.31
2017-08-08 15:30 | 49.99 | 47.66
2017-08-08 16:00 | 50.98 | 48.64
2017-08-08 16:30 | 51.55 | 49.14
2017-08-08 17:00 | 51.27 | 48.64
2017-08-08 17:30 | 51.15 | 47.56
2017-08-08 18:00 | 52.85 | 48.88
2017-08-08 18:30 | 55.54 | 51.87
2017-08-08 19:00 | 55.94 | 52.27
2017-08-08 19:30 | 53.08 | 48.83
2017-08-08 20:00 | 50.9 | 46.14
2017-08-08 20:30 | 49.82 | 44.2
2017-08-08 21:00 | 48.14 | 42.06
2017-08-08 21:30 | 46.41 | 39.56
2017-08-08 22:00 | 43.28 | 37.3
2017-08-08 22:30 | 40.36 | 34.89
2017-08-08 23:00 | 39.15 | 34.81
2017-08-08 23:30 | 34.31 | 31.44
2017-08-09 | 33.35 | 30.68
2017-08-09 00:30 | 34.26 | 31.65
2017-08-09 01:00 | 31.67 | 29.07
2017-08-09 01:30 | 30.65 | 28.08
2017-08-09 02:00 | 30.23 | 27.6
2017-08-09 02:30 | 29.68 | 26.95
2017-08-09 03:00 | 27.17 | 26.66
2017-08-09 03:30 | 26.68 | 26.6
2017-08-09 04:00 | 27.07 | 26.99
2017-08-09 04:30 | 27.28 | 27.2
2017-08-09 05:00 | 28.32 | 28.23
2017-08-09 05:30 | 31.01 | 30.87
2017-08-09 06:00 | 34.76 | 34.49
2017-08-09 06:30 | 39.9 | 39.36
2017-08-09 07:00 | 46.14 | 43.75
2017-08-09 07:30 | 54.72 | 48.82
2017-08-09 08:00 | 55.72 | 49.93
2017-08-09 08:30 | 54.84 | 48.93
2017-08-09 09:00 | 52.91 | 47.21
2017-08-09 09:30 | 51.91 | 46.17
2017-08-09 10:00 | 50.65 | 44.69
2017-08-09 10:30 | 50.18 | 44.1
2017-08-09 11:00 | 51.24 | 45.21
2017-08-09 11:30 | 51.72 | 45.71
2017-08-09 12:00 | 52.08 | 46.08
2017-08-09 12:30 | 52.54 | 46.64
2017-08-09 13:00 | 51.66 | 45.68
2017-08-09 13:30 | 51.88 | 45.84
2017-08-09 14:00 | 52.69 | 46.79
2017-08-09 14:30 | 52.68 | 46.76
2017-08-09 15:00 | 52.93 | 47.08
2017-08-09 15:30 | 52.77 | 46.96
2017-08-09 16:00 | 52.68 | 46.94
2017-08-09 16:30 | 46.12 | 41.73
2017-08-09 17:00 | 53.04 | 47.65
2017-08-09 17:30 | 53.16 | 47.95
2017-08-09 18:00 | 54.34 | 49.33
2017-08-09 18:30 | 56.45 | 51.58
2017-08-09 19:00 | 56.52 | 51.63
2017-08-09 19:30 | 53.68 | 48.56
2017-08-09 20:00 | 51.47 | 46.12
2017-08-09 20:30 | 47 | 44.04
2017-08-09 21:00 | 43.19 | 42.04
2017-08-09 21:30 | 40.78 | 39.62
2017-08-09 22:00 | 38.25 | 36.98
2017-08-09 22:30 | 36.53 | 35.13
2017-08-09 23:00 | 36.44 | 35.01
2017-08-09 23:30 | 33.47 | 31.96
2017-08-10 | 32.08 | 30.36
2017-08-10 00:30 | 31.34 | 29.37
2017-08-10 01:00 | 29.98 | 27.77
2017-08-10 01:30 | 29.47 | 27.23
2017-08-10 02:00 | 28.95 | 26.66
2017-08-10 02:30 | 28.95 | 26.68
2017-08-10 03:00 | 28.64 | 26.36
2017-08-10 03:30 | 28.56 | 26.29
2017-08-10 04:00 | 28.66 | 26.41
2017-08-10 04:30 | 29.37 | 27.17
2017-08-10 05:00 | 30.44 | 28.29
2017-08-10 05:30 | 33.33 | 31.31
2017-08-10 06:00 | 36.36 | 34.46
2017-08-10 06:30 | 41.25 | 39.49
2017-08-10 07:00 | 46.18 | 44.54
2017-08-10 07:30 | 50.87 | 49.44
2017-08-10 08:00 | 52.37 | 50.95
2017-08-10 08:30 | 53.71 | 52.27
2017-08-10 09:00 | 52.55 | 51.02
2017-08-10 09:30 | 50.62 | 49.05
2017-08-10 10:00 | 50.3 | 48.8
2017-08-10 10:30 | 50.34 | 48.87
2017-08-10 11:00 | 50.17 | 48.65
2017-08-10 11:30 | 49.67 | 48.1
2017-08-10 12:00 | 50.27 | 48.7
2017-08-10 12:30 | 49.38 | 47.79
2017-08-10 13:00 | 49.86 | 48.27
2017-08-10 13:30 | 51.38 | 49.84
2017-08-10 14:00 | 51.87 | 50.32
2017-08-10 14:30 | 51.64 | 50.27
2017-08-10 15:00 | 51.59 | 50.25
2017-08-10 15:30 | 51.24 | 49.9
2017-08-10 16:00 | 52.12 | 50.84
2017-08-10 16:30 | 52.46 | 51.24
2017-08-10 17:00 | 51.88 | 50.71
2017-08-10 17:30 | 50.66 | 49.55
2017-08-10 18:00 | 52.06 | 50.99
2017-08-10 18:30 | 53.93 | 52.92
2017-08-10 19:00 | 53.51 | 52.51
2017-08-10 19:30 | 51.43 | 50.39
2017-08-10 20:00 | 49.17 | 47.97
2017-08-10 20:30 | 47.66 | 46.41
2017-08-10 21:00 | 45.65 | 44.37
2017-08-10 21:30 | 43.02 | 41.7
2017-08-10 22:00 | 40.79 | 39.41
2017-08-10 22:30 | 38.77 | 37.38
2017-08-10 23:00 | 38.05 | 36.68
2017-08-10 23:30 | 34.98 | 33.52
2017-08-11 | 33.17 | 31.46
2017-08-11 00:30 | 32.08 | 30.27
2017-08-11 01:00 | 30.92 | 29.03
2017-08-11 01:30 | 30.25 | 28.33
2017-08-11 02:00 | 29.68 | 27.73
2017-08-11 02:30 | 29.67 | 27.44
2017-08-11 03:00 | 29.74 | 27.51
2017-08-11 03:30 | 29.75 | 27.52
2017-08-11 04:00 | 30.02 | 27.81
2017-08-11 04:30 | 30.63 | 28.45
2017-08-11 05:00 | 31.97 | 29.87
2017-08-11 05:30 | 34.29 | 32.27
2017-08-11 06:00 | 36.81 | 34.87
2017-08-11 06:30 | 41.62 | 39.77
2017-08-11 07:00 | 45.26 | 43.59
2017-08-11 07:30 | 50.3 | 48.8
2017-08-11 08:00 | 52.35 | 50.84
2017-08-11 08:30 | 53 | 51.51
2017-08-11 09:00 | 52.56 | 51.13
2017-08-11 09:30 | 50.99 | 49.49
2017-08-11 10:00 | 50.21 | 48.65
2017-08-11 10:30 | 50.64 | 49.03
2017-08-11 11:00 | 52.11 | 50.53
2017-08-11 11:30 | 52.16 | 50.56
2017-08-11 12:00 | 50.69 | 49.02
2017-08-11 12:30 | 51.7 | 50.09
2017-08-11 13:00 | 51.3 | 49.68
2017-08-11 13:30 | 50.83 | 49.21
2017-08-11 14:00 | 50.86 | 49.25
2017-08-11 14:30 | 50.52 | 48.94
2017-08-11 15:00 | 49.75 | 48.18
2017-08-11 15:30 | 48.95 | 47.39
2017-08-11 16:00 | 49.89 | 48.4
2017-08-11 16:30 | 50.58 | 49.18
2017-08-11 17:00 | 49.79 | 48.44
2017-08-11 17:30 | 49.35 | 48.06
2017-08-11 18:00 | 50.13 | 48.91
2017-08-11 18:30 | 51.82 | 50.62
2017-08-11 19:00 | 51.43 | 50.25
2017-08-11 19:30 | 48.75 | 47.53
2017-08-11 20:00 | 46.9 | 45.64
2017-08-11 20:30 | 44.78 | 43.48
2017-08-11 21:00 | 43.28 | 41.97
2017-08-11 21:30 | 40.9 | 39.54
2017-08-11 22:00 | 39.45 | 38
2017-08-11 22:30 | 37.7 | 36.11
2017-08-11 23:00 | 37.95 | 36.4
2017-08-11 23:30 | 34.54 | 32.83
2017-08-12 | 33.15 | 31.15
2017-08-12 00:30 | 32.4 | 30.38
2017-08-12 01:00 | 31.05 | 28.93
2017-08-12 01:30 | 30.15 | 27.96
2017-08-12 02:00 | 29.34 | 27.12
2017-08-12 02:30 | 29.19 | 26.96
2017-08-12 03:00 | 29.64 | 27.39
2017-08-12 03:30 | 29.09 | 26.82
2017-08-12 04:00 | 28.84 | 26.6
2017-08-12 04:30 | 29.32 | 27.11
2017-08-12 05:00 | 29.69 | 27.49
2017-08-12 05:30 | 31.1 | 28.96
2017-08-12 06:00 | 31.96 | 29.87
2017-08-12 06:30 | 33.62 | 31.59
2017-08-12 07:00 | 35.04 | 33.1
2017-08-12 07:30 | 37.08 | 35.22
2017-08-12 08:00 | 38.07 | 36.23
2017-08-12 08:30 | 39.32 | 37.5
2017-08-12 09:00 | 39.42 | 37.55
2017-08-12 09:30 | 39.68 | 37.77
2017-08-12 10:00 | 39.28 | 37.31
2017-08-12 10:30 | 39.69 | 37.88
2017-08-12 11:00 | 39.24 | 37.43
2017-08-12 11:30 | 38.74 | 36.9
2017-08-12 12:00 | 38.38 | 36.52
2017-08-12 12:30 | 38.13 | 36.28
2017-08-12 13:00 | 37.29 | 35.41
2017-08-12 13:30 | 35.87 | 33.96
2017-08-12 14:00 | 36.61 | 34.74
2017-08-12 14:30 | 36.05 | 34.18
2017-08-12 15:00 | 37.4 | 35.59
2017-08-12 15:30 | 38.34 | 36.62
2017-08-12 16:00 | 39.37 | 37.72
2017-08-12 16:30 | 40.01 | 38.41
2017-08-12 17:00 | 41.49 | 39.96
2017-08-12 17:30 | 42.34 | 40.86
2017-08-12 18:00 | 44.07 | 42.64
2017-08-12 18:30 | 46.24 | 44.86
2017-08-12 19:00 | 47.07 | 45.71
2017-08-12 19:30 | 46.24 | 44.86
2017-08-12 20:00 | 44.4 | 42.98
2017-08-12 20:30 | 42.5 | 41.05
2017-08-12 21:00 | 41.46 | 39.99
2017-08-12 21:30 | 40.43 | 38.93
2017-08-12 22:00 | 39.08 | 37.57
2017-08-12 22:30 | 35.73 | 34.12
2017-08-12 23:00 | 36.03 | 34.24
2017-08-12 23:30 | 33.51 | 31.55
2017-08-13 | 32.16 | 30.12
2017-08-13 00:30 | 31.34 | 29.27
2017-08-13 01:00 | 30.17 | 28.03
2017-08-13 01:30 | 29.7 | 27.52
2017-08-13 02:00 | 29.2 | 26.99
2017-08-13 02:30 | 28.76 | 26.54
2017-08-13 03:00 | 28.46 | 26.23
2017-08-13 03:30 | 28.43 | 26.2
2017-08-13 04:00 | 28.48 | 26.25
2017-08-13 04:30 | 28.81 | 26.61
2017-08-13 05:00 | 28.89 | 26.69
2017-08-13 05:30 | 29.5 | 27.34
2017-08-13 06:00 | 30.07 | 27.94
2017-08-13 06:30 | 30.5 | 28.42
2017-08-13 07:00 | 30.99 | 28.96
2017-08-13 07:30 | 33.08 | 31.17
2017-08-13 08:00 | 34.47 | 32.61
2017-08-13 08:30 | 36.16 | 34.38
2017-08-13 09:00 | 36.16 | 34.34
2017-08-13 09:30 | 36.34 | 34.49
2017-08-13 10:00 | 36.57 | 34.69
2017-08-13 10:30 | 36.83 | 34.92
2017-08-13 11:00 | 36.24 | 34.27
2017-08-13 11:30 | 35.27 | 33.21
2017-08-13 12:00 | 33.87 | 31.71
2017-08-13 12:30 | 34.19 | 32.07
2017-08-13 13:00 | 33.74 | 31.58
2017-08-13 13:30 | 33.01 | 30.79
2017-08-13 14:00 | 33.07 | 30.85
2017-08-13 14:30 | 32.94 | 30.73
2017-08-13 15:00 | 33.99 | 31.86
2017-08-13 15:30 | 34.76 | 32.67
2017-08-13 16:00 | 36.66 | 34.71
2017-08-13 16:30 | 38.89 | 37.09
2017-08-13 17:00 | 40.09 | 38.32
2017-08-13 17:30 | 42.61 | 40.93
2017-08-13 18:00 | 45.45 | 43.88
2017-08-13 18:30 | 48.7 | 47.2
2017-08-13 19:00 | 48.92 | 47.43
2017-08-13 19:30 | 49.38 | 45.18
2017-08-13 20:00 | 48.7 | 42.17
2017-08-13 20:30 | 46.64 | 39.83
2017-08-13 21:00 | 45.14 | 38.08
2017-08-13 21:30 | 43.02 | 35.56
2017-08-13 22:00 | 41.63 | 33.86
2017-08-13 22:30 | 40.39 | 32.32
2017-08-13 23:00 | 40.44 | 32.63
2017-08-13 23:30 | 38.27 | 29.84
2017-08-14 | 36.82 | 28.02
2017-08-14 00:30 | 36.26 | 27.28
2017-08-14 01:00 | 35.3 | 26.02
2017-08-14 01:30 | 34.85 | 25.4
2017-08-14 02:00 | 34.96 | 25.56
2017-08-14 02:30 | 35.18 | 25.79
2017-08-14 03:00 | 35.19 | 25.85
2017-08-14 03:30 | 35.59 | 26.38
2017-08-14 04:00 | 35.76 | 26.6
2017-08-14 04:30 | 35.96 | 26.9
2017-08-14 05:00 | 36.71 | 27.86
2017-08-14 05:30 | 38.99 | 30.65
2017-08-14 06:00 | 41.41 | 33.61
2017-08-14 06:30 | 45.64 | 38.55
2017-08-14 07:00 | 50.23 | 43.75
2017-08-14 07:30 | 54.72 | 48.77
2017-08-14 08:00 | 55.67 | 50.13
2017-08-14 08:30 | 55.46 | 49.81
2017-08-14 09:00 | 54.46 | 48.79
2017-08-14 09:30 | 54.1 | 48.48
2017-08-14 10:00 | 53.49 | 47.74
2017-08-14 10:30 | 53.04 | 47.13
2017-08-14 11:00 | 53.57 | 47.59
2017-08-14 11:30 | 53.21 | 47.26
2017-08-14 12:00 | 54.09 | 48.23
2017-08-14 12:30 | 54.89 | 49.16
2017-08-14 13:00 | 53.75 | 47.89
2017-08-14 13:30 | 54.04 | 48.18
2017-08-14 14:00 | 54.49 | 48.66
2017-08-14 14:30 | 55.73 | 49.99
2017-08-14 15:00 | 55.62 | 49.82
2017-08-14 15:30 | 55.37 | 49.64
2017-08-14 16:00 | 55.21 | 49.54
2017-08-14 16:30 | 55.6 | 50.1
2017-08-14 17:00 | 55.3 | 49.92
2017-08-14 17:30 | 54.8 | 49.58
2017-08-14 18:00 | 55.06 | 49.96
2017-08-14 18:30 | 57.09 | 52.26
2017-08-14 19:00 | 57.21 | 52.44
2017-08-14 19:30 | 54.95 | 49.95
2017-08-14 20:00 | 52.03 | 46.76
2017-08-14 20:30 | 50 | 44.57
2017-08-14 21:00 | 48.59 | 42.29
2017-08-14 21:30 | 46.43 | 39.81
2017-08-14 22:00 | 44.64 | 37.7
2017-08-14 22:30 | 43.01 | 35.8
2017-08-14 23:00 | 42.68 | 35.55
2017-08-14 23:30 | 40.04 | 32.08
2017-08-15 | 38.78 | 30.32
2017-08-15 00:30 | 38.33 | 29.74
2017-08-15 01:00 | 37.11 | 28.25
2017-08-15 01:30 | 36.67 | 27.59
2017-08-15 02:00 | 36.46 | 27.34
2017-08-15 02:30 | 36.33 | 27.26
2017-08-15 03:00 | 36.22 | 27.13
2017-08-15 03:30 | 36.14 | 27.01
2017-08-15 04:00 | 36.21 | 27.08
2017-08-15 04:30 | 36.91 | 28
2017-08-15 05:00 | 37.3 | 28.48
2017-08-15 05:30 | 39.51 | 31.22
2017-08-15 06:00 | 41.95 | 34.16
2017-08-15 06:30 | 46.13 | 39.06
2017-08-15 07:00 | 50.04 | 43.45
2017-08-15 07:30 | 54.03 | 48.12
2017-08-15 08:00 | 54.15 | 49.51
2017-08-15 08:30 | 50.51 | 48.99
2017-08-15 09:00 | 50.52 | 48.34
2017-08-15 09:30 | 49.95 | 47.82
2017-08-15 10:00 | 49.6 | 47.64
2017-08-15 10:30 | 50.3 | 48.85
2017-08-15 11:00 | 50 | 48.78
2017-08-15 11:30 | 49.99 | 48.95
2017-08-15 12:00 | 50.56 | 49.7
2017-08-15 12:30 | 51.02 | 50.15
2017-08-15 13:00 | 50.67 | 49.75
2017-08-15 13:30 | 50.52 | 49.58
2017-08-15 14:00 | 50.19 | 49.3
2017-08-15 14:30 | 50.06 | 49.2
2017-08-15 15:00 | 50.25 | 49.27
2017-08-15 15:30 | 50.82 | 49.68
2017-08-15 16:00 | 51.44 | 50.08
2017-08-15 16:30 | 52.36 | 50.58
2017-08-15 17:00 | 53.09 | 50.91
2017-08-15 17:30 | 53.27 | 50.24
2017-08-15 18:00 | 54.58 | 51.2
2017-08-15 18:30 | 56.87 | 53.73
2017-08-15 19:00 | 56.91 | 53.72
2017-08-15 19:30 | 54.67 | 50.98
2017-08-15 20:00 | 52.19 | 47.99
2017-08-15 20:30 | 50.91 | 45.91
2017-08-15 21:00 | 50.59 | 43.48
2017-08-15 21:30 | 50.23 | 41.12
2017-08-15 22:00 | 47.87 | 38.01
2017-08-15 22:30 | 45.98 | 35.69
2017-08-15 23:00 | 41.77 | 35.84
2017-08-15 23:30 | 32.46 | 32.35
2017-08-16 | 31.13 | 31.1
2017-08-16 00:30 | 30.9 | 30.88
2017-08-16 01:00 | 29.55 | 29.52
2017-08-16 01:30 | 28.81 | 28.72
2017-08-16 02:00 | 28.49 | 28.37
2017-08-16 02:30 | 28.18 | 28.07
2017-08-16 03:00 | 27.84 | 27.74
2017-08-16 03:30 | 27.27 | 27.17
2017-08-16 04:00 | 26.87 | 26.78
2017-08-16 04:30 | 27.53 | 27.43
2017-08-16 05:00 | 28.82 | 28.7
2017-08-16 05:30 | 31.44 | 31.23
2017-08-16 06:00 | 34.49 | 34.15
2017-08-16 06:30 | 39.52 | 38.9
2017-08-16 07:00 | 45.61 | 43.55
2017-08-16 07:30 | 54.11 | 48.09
2017-08-16 08:00 | 55.12 | 49.38
2017-08-16 08:30 | 54.66 | 49.15
2017-08-16 09:00 | 54.06 | 48.39
2017-08-16 09:30 | 53.89 | 48.14
2017-08-16 10:00 | 54.93 | 49.23
2017-08-16 10:30 | 55.6 | 49.98
2017-08-16 11:00 | 55.95 | 50.3
2017-08-16 11:30 | 55.56 | 49.79
2017-08-16 12:00 | 55.87 | 50.16
2017-08-16 12:30 | 56.04 | 50.34
2017-08-16 13:00 | 56.33 | 50.62
2017-08-16 13:30 | 56.1 | 50.37
2017-08-16 14:00 | 56.36 | 50.66
2017-08-16 14:30 | 56.44 | 50.75
2017-08-16 15:00 | 57.29 | 51.72
2017-08-16 15:30 | 57.35 | 51.84
2017-08-16 16:00 | 56.64 | 51.14
2017-08-16 16:30 | 57.11 | 51.85
2017-08-16 17:00 | 56.58 | 51.37
2017-08-16 17:30 | 55.12 | 49.93
2017-08-16 18:00 | 55.96 | 50.99
2017-08-16 18:30 | 58.22 | 53.51
2017-08-16 19:00 | 58.72 | 54.09
2017-08-16 19:30 | 56.05 | 51.22
2017-08-16 20:00 | 53.8 | 48.73
2017-08-16 20:30 | 51.65 | 46.41
2017-08-16 21:00 | 49.05 | 43.52
2017-08-16 21:30 | 46.82 | 41.04
2017-08-16 22:00 | 44.84 | 38.81
2017-08-16 22:30 | 40.15 | 36.56
2017-08-16 23:00 | 37.5 | 36.68
2017-08-16 23:30 | 33.53 | 32.7
2017-08-17 | 31.09 | 31.01
2017-08-17 00:30 | 30.39 | 30.36
2017-08-17 01:00 | 28.88 | 28.84
2017-08-17 01:30 | 28.12 | 28.08
2017-08-17 02:00 | 28.06 | 28.02
2017-08-17 02:30 | 27.49 | 27.44
2017-08-17 03:00 | 27.18 | 27.12
2017-08-17 03:30 | 27 | 26.93
2017-08-17 04:00 | 27.35 | 27.28
2017-08-17 04:30 | 28.01 | 27.94
2017-08-17 05:00 | 29.22 | 29.19
2017-08-17 05:30 | 31.52 | 31.49
2017-08-17 06:00 | 34.85 | 34.8
2017-08-17 06:30 | 39.31 | 39.21
2017-08-17 07:00 | 43.33 | 43.11
2017-08-17 07:30 | 49.19 | 47.89
2017-08-17 08:00 | 50.77 | 49.38
2017-08-17 08:30 | 50.7 | 49.32
2017-08-17 09:00 | 50.19 | 48.84
2017-08-17 09:30 | 50.39 | 49.02
2017-08-17 10:00 | 50.93 | 49.54
2017-08-17 10:30 | 50.65 | 49.21
2017-08-17 11:00 | 50.23 | 48.72
2017-08-17 11:30 | 50.91 | 49.38
2017-08-17 12:00 | 51.26 | 49.72
2017-08-17 12:30 | 51.44 | 49.93
2017-08-17 13:00 | 50.98 | 49.47
2017-08-17 13:30 | 51.64 | 50.13
2017-08-17 14:00 | 52.54 | 51.04
2017-08-17 14:30 | 52.66 | 51.17
2017-08-17 15:00 | 52.52 | 51.05
2017-08-17 15:30 | 52.71 | 51.29
2017-08-17 16:00 | 53.2 | 51.81
2017-08-17 16:30 | 53.68 | 52.41
2017-08-17 17:00 | 52.86 | 51.61
2017-08-17 17:30 | 52.17 | 51
2017-08-17 18:00 | 52.57 | 51.47
2017-08-17 18:30 | 54.88 | 53.83
2017-08-17 19:00 | 55.8 | 54.78
2017-08-17 19:30 | 53.86 | 52.82
2017-08-17 20:00 | 50.76 | 49.67
2017-08-17 20:30 | 48.29 | 47.2
2017-08-17 21:00 | 46.42 | 45.29
2017-08-17 21:30 | 43.28 | 42.12
2017-08-17 22:00 | 40.84 | 39.64
2017-08-17 22:30 | 38.79 | 37.56
2017-08-17 23:00 | 38.17 | 36.93
2017-08-17 23:30 | 35.13 | 33.69
2017-08-18 | 34.82 | 33.27
2017-08-18 00:30 | 34 | 32.2
2017-08-18 01:00 | 32.5 | 30.63
2017-08-18 01:30 | 31.78 | 29.61
2017-08-18 02:00 | 31.13 | 28.9
2017-08-18 02:30 | 29.7 | 27.37
2017-08-18 03:00 | 29.59 | 27.25
2017-08-18 03:30 | 29.9 | 27.59
2017-08-18 04:00 | 31.14 | 28.94
2017-08-18 04:30 | 31.41 | 29.21
2017-08-18 05:00 | 32.02 | 29.86
2017-08-18 05:30 | 34.65 | 32.61
2017-08-18 06:00 | 37.09 | 35.11
2017-08-18 06:30 | 40.92 | 39.05
2017-08-18 07:00 | 44.66 | 42.92
2017-08-18 07:30 | 48.89 | 47.36
2017-08-18 08:00 | 50.02 | 48.61
2017-08-18 08:30 | 51.04 | 49.78
2017-08-18 09:00 | 51.06 | 49.74
2017-08-18 09:30 | 50.71 | 49.34
2017-08-18 10:00 | 50.66 | 49.26
2017-08-18 10:30 | 51.72 | 50.28
2017-08-18 11:00 | 56.06 | 51.37
2017-08-18 11:30 | 57.48 | 51.86
2017-08-18 12:00 | 57.75 | 52.12
2017-08-18 12:30 | 58.1 | 52.57
2017-08-18 13:00 | 57.83 | 52.27
2017-08-18 13:30 | 57.93 | 52.31
2017-08-18 14:00 | 58.61 | 53.03
2017-08-18 14:30 | 58.11 | 52.55
2017-08-18 15:00 | 57.93 | 52.42
2017-08-18 15:30 | 57.18 | 51.67
2017-08-18 16:00 | 57.04 | 51.55
2017-08-18 16:30 | 57.34 | 52
2017-08-18 17:00 | 56.93 | 51.69
2017-08-18 17:30 | 55.41 | 50.22
2017-08-18 18:00 | 54.83 | 49.64
2017-08-18 18:30 | 56.65 | 51.72
2017-08-18 19:00 | 56.91 | 51.99
2017-08-18 19:30 | 55.21 | 50.15
2017-08-18 20:00 | 55.39 | 50.32
2017-08-18 20:30 | 55.08 | 49.94
2017-08-18 21:00 | 54.61 | 49.46
2017-08-18 21:30 | 52.79 | 47.52
2017-08-18 22:00 | 50.68 | 45.01
2017-08-18 22:30 | 49.16 | 43.12
2017-08-18 23:00 | 49.94 | 43.71
2017-08-18 23:30 | 46.51 | 39.96
2017-08-19 | 44.2 | 37.26
2017-08-19 00:30 | 43.59 | 36.14
2017-08-19 01:00 | 42.35 | 34.64
2017-08-19 01:30 | 41.61 | 33.77
2017-08-19 02:00 | 41.17 | 33.24
2017-08-19 02:30 | 40.68 | 32.51
2017-08-19 03:00 | 40.02 | 31.64
2017-08-19 03:30 | 39.67 | 31.32
2017-08-19 04:00 | 39.41 | 31.02
2017-08-19 04:30 | 39.57 | 31.17
2017-08-19 05:00 | 40.18 | 31.9
2017-08-19 05:30 | 40.59 | 32.45
2017-08-19 06:00 | 41.31 | 33.27
2017-08-19 06:30 | 42.7 | 34.98
2017-08-19 07:00 | 44.59 | 37.21
2017-08-19 07:30 | 46.78 | 39.77
2017-08-19 08:00 | 48.85 | 42.08
2017-08-19 08:30 | 49.56 | 42.87
2017-08-19 09:00 | 48.96 | 42.1
2017-08-19 09:30 | 48.95 | 42.02
2017-08-19 10:00 | 47.93 | 40.81
2017-08-19 10:30 | 46.49 | 39.04
2017-08-19 11:00 | 46.01 | 38.44
2017-08-19 11:30 | 45.44 | 37.76
2017-08-19 12:00 | 44.24 | 36.69
2017-08-19 12:30 | 43.18 | 35.62
2017-08-19 13:00 | 41.89 | 34.07
2017-08-19 13:30 | 41.24 | 33.3
2017-08-19 14:00 | 41.34 | 33.44
2017-08-19 14:30 | 40.94 | 33.01
2017-08-19 15:00 | 41.68 | 33.91
2017-08-19 15:30 | 42.24 | 34.67
2017-08-19 16:00 | 43.19 | 35.89
2017-08-19 16:30 | 45.88 | 39.11
2017-08-19 17:00 | 46.33 | 39.65
2017-08-19 17:30 | 48.68 | 42.41
2017-08-19 18:00 | 51.91 | 46.04
2017-08-19 18:30 | 55.25 | 49.71
2017-08-19 19:00 | 55.53 | 50
2017-08-19 19:30 | 54.24 | 48.56
2017-08-19 20:00 | 52.22 | 46.32
2017-08-19 20:30 | 49.7 | 43.48
2017-08-19 21:00 | 46.19 | 42.45
2017-08-19 21:30 | 45.77 | 42.34
2017-08-19 22:00 | 44.53 | 40.92
2017-08-19 22:30 | 42.74 | 38.91
2017-08-19 23:00 | 43.78 | 40.09
2017-08-19 23:30 | 40.5 | 36.68
2017-08-20 | 38.4 | 34.3
2017-08-20 00:30 | 37.83 | 33.68
2017-08-20 01:00 | 36.91 | 32.63
2017-08-20 01:30 | 35.75 | 31.28
2017-08-20 02:00 | 35.02 | 30.42
2017-08-20 02:30 | 34.72 | 30.07
2017-08-20 03:00 | 34.55 | 29.86
2017-08-20 03:30 | 34.33 | 29.58
2017-08-20 04:00 | 34.14 | 29.34
2017-08-20 04:30 | 34.23 | 29.47
2017-08-20 05:00 | 34.47 | 29.76
2017-08-20 05:30 | 34.86 | 30.21
2017-08-20 06:00 | 35.5 | 30.96
2017-08-20 06:30 | 36.17 | 31.71
2017-08-20 07:00 | 36.57 | 32.12
2017-08-20 07:30 | 37.33 | 33
2017-08-20 08:00 | 38.14 | 33.93
2017-08-20 08:30 | 38.96 | 34.91
2017-08-20 09:00 | 39.22 | 35.26
2017-08-20 09:30 | 38.55 | 34.52
2017-08-20 10:00 | 37.69 | 33.56
2017-08-20 10:30 | 36.76 | 32.52
2017-08-20 11:00 | 36.11 | 31.7
2017-08-20 11:30 | 33.84 | 30.9
2017-08-20 12:00 | 30.78 | 30.51
2017-08-20 12:30 | 31.35 | 31.11
2017-08-20 13:00 | 29.98 | 29.7
2017-08-20 13:30 | 30.44 | 30.18
2017-08-20 14:00 | 32.24 | 30.18
2017-08-20 14:30 | 32.45 | 30.24
2017-08-20 15:00 | 32.65 | 30.46
2017-08-20 15:30 | 33.49 | 31.42
2017-08-20 16:00 | 35.15 | 33.21
2017-08-20 16:30 | 38.13 | 36.31
2017-08-20 17:00 | 39.53 | 37.77
2017-08-20 17:30 | 43.87 | 42.28
2017-08-20 18:00 | 47.06 | 45.57
2017-08-20 18:30 | 52.68 | 51.27
2017-08-20 19:00 | 54.03 | 52.64
2017-08-20 19:30 | 52.35 | 50.91
2017-08-20 20:00 | 49.18 | 47.67
2017-08-20 20:30 | 47.34 | 45.78
2017-08-20 21:00 | 45.58 | 43.98
2017-08-20 21:30 | 44.26 | 42.63
2017-08-20 22:00 | 42.17 | 40.49
2017-08-20 22:30 | 40.21 | 38.45
2017-08-20 23:00 | 39.97 | 38.22
2017-08-20 23:30 | 37.1 | 35.23
2017-08-21 | 35.08 | 33.11
2017-08-21 00:30 | 34.92 | 32.96
2017-08-21 01:00 | 33.32 | 31.29
2017-08-21 01:30 | 33.03 | 30.99
2017-08-21 02:00 | 33.87 | 31.91
2017-08-21 02:30 | 33 | 30.99
2017-08-21 03:00 | 32.67 | 30.63
2017-08-21 03:30 | 32.37 | 30.33
2017-08-21 04:00 | 33.06 | 31.04
2017-08-21 04:30 | 33.32 | 31.32
2017-08-21 05:00 | 33.55 | 31.54
2017-08-21 05:30 | 36.11 | 34.2
2017-08-21 06:00 | 39.04 | 37.22
2017-08-21 06:30 | 44.01 | 42.31
2017-08-21 07:00 | 48.53 | 46.91
2017-08-21 07:30 | 51.91 | 50.43
2017-08-21 08:00 | 52.33 | 50.9
2017-08-21 08:30 | 52.55 | 51.07
2017-08-21 09:00 | 52.52 | 50.99
2017-08-21 09:30 | 52.35 | 50.78
2017-08-21 10:00 | 51.34 | 49.75
2017-08-21 10:30 | 48.27 | 46.57
2017-08-21 11:00 | 48.32 | 46.6
2017-08-21 11:30 | 49.02 | 47.44
2017-08-21 12:00 | 49.09 | 47.51
2017-08-21 12:30 | 50.56 | 49
2017-08-21 13:00 | 49.42 | 48.02
2017-08-21 13:30 | 48.78 | 47.33
2017-08-21 14:00 | 49.46 | 48.02
2017-08-21 14:30 | 49.95 | 48.53
2017-08-21 15:00 | 49.91 | 48.52
2017-08-21 15:30 | 49.7 | 48.31
2017-08-21 16:00 | 50.79 | 49.46
2017-08-21 16:30 | 52.24 | 51.02
2017-08-21 17:00 | 51.62 | 50.44
2017-08-21 17:30 | 53.49 | 52.42
2017-08-21 18:00 | 55.13 | 54.13
2017-08-21 18:30 | 57.54 | 56.56
2017-08-21 19:00 | 58.42 | 57.46
2017-08-21 19:30 | 56.23 | 55.23
2017-08-21 20:00 | 53.5 | 52.48
2017-08-21 20:30 | 51.18 | 50.13
2017-08-21 21:00 | 48.57 | 47.49
2017-08-21 21:30 | 46.09 | 44.98
2017-08-21 22:00 | 44.29 | 43.16
2017-08-21 22:30 | 42.21 | 41.05
2017-08-21 23:00 | 42.54 | 40.83
2017-08-21 23:30 | 39.31 | 37.43
2017-08-22 | 37.73 | 35.8
2017-08-22 00:30 | 37.04 | 35.1
2017-08-22 01:00 | 35.34 | 33.33
2017-08-22 01:30 | 34.78 | 32.74
2017-08-22 02:00 | 34.32 | 32.25
2017-08-22 02:30 | 33.58 | 31.5
2017-08-22 03:00 | 33.79 | 31.73
2017-08-22 03:30 | 34.06 | 32.04
2017-08-22 04:00 | 34.42 | 32.42
2017-08-22 04:30 | 35.26 | 33.31
2017-08-22 05:00 | 35.27 | 33.31
2017-08-22 05:30 | 37.9 | 36.03
2017-08-22 06:00 | 41.04 | 39.25
2017-08-22 06:30 | 45.8 | 44.1
2017-08-22 07:00 | 50.42 | 48.81
2017-08-22 07:30 | 54.31 | 52.94
2017-08-22 08:00 | 55.11 | 53.84
2017-08-22 08:30 | 54.23 | 52.86
2017-08-22 09:00 | 52.66 | 51.28
2017-08-22 09:30 | 52.05 | 50.72
2017-08-22 10:00 | 52.03 | 50.66
2017-08-22 10:30 | 52.48 | 51.06
2017-08-22 11:00 | 52.65 | 51.25
2017-08-22 11:30 | 52.88 | 51.45
2017-08-22 12:00 | 53.32 | 51.85
2017-08-22 12:30 | 53.23 | 51.78
2017-08-22 13:00 | 52.54 | 51.08
2017-08-22 13:30 | 53.16 | 51.69
2017-08-22 14:00 | 54.47 | 53.04
2017-08-22 14:30 | 55.04 | 53.62
2017-08-22 15:00 | 55.28 | 53.91
2017-08-22 15:30 | 55.4 | 54.05
2017-08-22 16:00 | 56.35 | 55.06
2017-08-22 16:30 | 56.77 | 55.56
2017-08-22 17:00 | 55.96 | 54.79
2017-08-22 17:30 | 55.78 | 54.68
2017-08-22 18:00 | 56.79 | 55.74
2017-08-22 18:30 | 61.73 | 60.76
2017-08-22 19:00 | 62.52 | 61.56
2017-08-22 19:30 | 58.21 | 57.21
2017-08-22 20:00 | 55.25 | 54.22
2017-08-22 20:30 | 53.91 | 52.87
2017-08-22 21:00 | 50.87 | 49.8
2017-08-22 21:30 | 48.5 | 47.41
2017-08-22 22:00 | 46.42 | 45.3
2017-08-22 22:30 | 43.55 | 42.39
2017-08-22 23:00 | 44 | 42.89
2017-08-22 23:30 | 40.21 | 38.93
2017-08-23 | 36.97 | 35.51
2017-08-23 00:30 | 36.02 | 34.54
2017-08-23 01:00 | 35 | 33.14
2017-08-23 01:30 | 34.75 | 32.73
2017-08-23 02:00 | 34.15 | 32.09
2017-08-23 02:30 | 33.44 | 31.38
2017-08-23 03:00 | 32.62 | 30.52
2017-08-23 03:30 | 32.77 | 30.64
2017-08-23 04:00 | 33.09 | 30.99
2017-08-23 04:30 | 35.31 | 33.3
2017-08-23 05:00 | 36.12 | 34.13
2017-08-23 05:30 | 38.22 | 36.31
2017-08-23 06:00 | 41.55 | 39.73
2017-08-23 06:30 | 46.13 | 44.42
2017-08-23 07:00 | 50.33 | 48.72
2017-08-23 07:30 | 54.52 | 53.09
2017-08-23 08:00 | 55.47 | 54.11
2017-08-23 08:30 | 55.29 | 53.97
2017-08-23 09:00 | 54.72 | 53.42
2017-08-23 09:30 | 54.19 | 52.84
2017-08-23 10:00 | 54.89 | 53.56
2017-08-23 10:30 | 54.89 | 53.53
2017-08-23 11:00 | 53.64 | 52.2
2017-08-23 11:30 | 53.3 | 51.82
2017-08-23 12:00 | 53.08 | 51.58
2017-08-23 12:30 | 53.71 | 52.23
2017-08-23 13:00 | 53.09 | 51.6
2017-08-23 13:30 | 54.18 | 52.73
2017-08-23 14:00 | 54.14 | 52.67
2017-08-23 14:30 | 54.67 | 53.23
2017-08-23 15:00 | 54.85 | 53.45
2017-08-23 15:30 | 54.84 | 53.44
2017-08-23 16:00 | 55.29 | 53.96
2017-08-23 16:30 | 56.07 | 54.82
2017-08-23 17:00 | 55.79 | 54.59
2017-08-23 17:30 | 56.48 | 55.37
2017-08-23 18:00 | 57.84 | 56.78
2017-08-23 18:30 | 60.73 | 59.72
2017-08-23 19:00 | 61.75 | 60.76
2017-08-23 19:30 | 58.74 | 57.73
2017-08-23 20:00 | 56.09 | 55.06
2017-08-23 20:30 | 53.49 | 52.43
2017-08-23 21:00 | 51.34 | 50.26
2017-08-23 21:30 | 49.58 | 48.49
2017-08-23 22:00 | 46.55 | 45.41
2017-08-23 22:30 | 44.12 | 42.98
2017-08-23 23:00 | 44.83 | 43.73
2017-08-23 23:30 | 41.25 | 39.96
2017-08-24 | 38.98 | 37.41
2017-08-24 00:30 | 38 | 36.31
2017-08-24 01:00 | 36.8 | 34.91
2017-08-24 01:30 | 36.1 | 34.1
2017-08-24 02:00 | 35.32 | 33.3
2017-08-24 02:30 | 34.51 | 32.44
2017-08-24 03:00 | 34.17 | 32.09
2017-08-24 03:30 | 34.42 | 32.36
2017-08-24 04:00 | 34.98 | 32.96
2017-08-24 04:30 | 35.6 | 33.57
2017-08-24 05:00 | 36.88 | 34.88
2017-08-24 05:30 | 39.17 | 37.24
2017-08-24 06:00 | 41.51 | 39.63
2017-08-24 06:30 | 46.29 | 44.56
2017-08-24 07:00 | 50.25 | 48.77
2017-08-24 07:30 | 54.2 | 52.76
2017-08-24 08:00 | 55.63 | 54.28
2017-08-24 08:30 | 54.86 | 53.47
2017-08-24 09:00 | 54.03 | 52.71
2017-08-24 09:30 | 53.41 | 52.06
2017-08-24 10:00 | 53.21 | 51.82
2017-08-24 10:30 | 52.89 | 51.46
2017-08-24 11:00 | 52.99 | 51.52
2017-08-24 11:30 | 53.48 | 52
2017-08-24 12:00 | 54.13 | 52.64
2017-08-24 12:30 | 53.78 | 52.29
2017-08-24 13:00 | 52.33 | 50.79
2017-08-24 13:30 | 52.8 | 51.28
2017-08-24 14:00 | 53.59 | 52.08
2017-08-24 14:30 | 53.68 | 52.19
2017-08-24 15:00 | 54.25 | 52.78
2017-08-24 15:30 | 55.03 | 53.64
2017-08-24 16:00 | 55.31 | 53.98
2017-08-24 16:30 | 56.35 | 55.12
2017-08-24 17:00 | 56.01 | 54.83
2017-08-24 17:30 | 56.15 | 55.04
2017-08-24 18:00 | 57.75 | 56.71
2017-08-24 18:30 | 61.09 | 60.11
2017-08-24 19:00 | 61.03 | 60.06
2017-08-24 19:30 | 58.03 | 57.03
2017-08-24 20:00 | 55.71 | 54.67
2017-08-24 20:30 | 53.79 | 52.74
2017-08-24 21:00 | 53.84 | 52.81
2017-08-24 21:30 | 50.85 | 49.8
2017-08-24 22:00 | 47.22 | 46.11
2017-08-24 22:30 | 45.37 | 44.05
2017-08-24 23:00 | 45.06 | 43.76
2017-08-24 23:30 | 41.35 | 39.85
2017-08-25 | 39.09 | 37.31
2017-08-25 00:30 | 38.37 | 36.47
2017-08-25 01:00 | 37.78 | 35.85
2017-08-25 01:30 | 37.67 | 35.75
2017-08-25 02:00 | 37.42 | 35.48
2017-08-25 02:30 | 36.92 | 34.97
2017-08-25 03:00 | 36.41 | 34.44
2017-08-25 03:30 | 36.45 | 34.48
2017-08-25 04:00 | 36.26 | 34.29
2017-08-25 04:30 | 35.68 | 33.67
2017-08-25 05:00 | 35.61 | 33.57
2017-08-25 05:30 | 37.81 | 35.86
2017-08-25 06:00 | 40.69 | 38.82
2017-08-25 06:30 | 45.04 | 43.28
2017-08-25 07:00 | 50.69 | 49.08
2017-08-25 07:30 | 54.19 | 52.86
2017-08-25 08:00 | 55.6 | 54.31
2017-08-25 08:30 | 58.01 | 56.69
2017-08-25 09:00 | 56.82 | 55.47
2017-08-25 09:30 | 54.27 | 52.84
2017-08-25 10:00 | 52.58 | 51.26
2017-08-25 10:30 | 52.37 | 51.03
2017-08-25 11:00 | 50.72 | 49.32
2017-08-25 11:30 | 48.76 | 47.25
2017-08-25 12:00 | 48.35 | 46.82
2017-08-25 12:30 | 47.66 | 46.11
2017-08-25 13:00 | 46.68 | 45.14
2017-08-25 13:30 | 51.13 | 49.73
2017-08-25 14:00 | 50.12 | 48.7
2017-08-25 14:30 | 50.33 | 48.94
2017-08-25 15:00 | 50.48 | 49.1
2017-08-25 15:30 | 49.28 | 47.94
2017-08-25 16:00 | 49.87 | 48.6
2017-08-25 16:30 | 51.46 | 50.28
2017-08-25 17:00 | 51.74 | 50.59
2017-08-25 17:30 | 51.85 | 50.77
2017-08-25 18:00 | 52.95 | 51.83
2017-08-25 18:30 | 55.37 | 54.23
2017-08-25 19:00 | 56.38 | 55.26
2017-08-25 19:30 | 54.29 | 53.14
2017-08-25 20:00 | 50.91 | 49.7
2017-08-25 20:30 | 48.82 | 47.58
2017-08-25 21:00 | 46.92 | 45.64
2017-08-25 21:30 | 44.96 | 43.66
2017-08-25 22:00 | 42.78 | 41.29
2017-08-25 22:30 | 41.95 | 40.42
2017-08-25 23:00 | 42.6 | 41.11
2017-08-25 23:30 | 39.26 | 37.48
2017-08-26 | 37.4 | 35.48
2017-08-26 00:30 | 37.13 | 35.22
2017-08-26 01:00 | 35.73 | 33.77
2017-08-26 01:30 | 35.07 | 33.09
2017-08-26 02:00 | 34.45 | 32.44
2017-08-26 02:30 | 34.09 | 32.06
2017-08-26 03:00 | 33.96 | 31.95
2017-08-26 03:30 | 33.42 | 31.4
2017-08-26 04:00 | 33.26 | 31.25
2017-08-26 04:30 | 33.13 | 31.1
2017-08-26 05:00 | 33.37 | 31.34
2017-08-26 05:30 | 35.27 | 33.36
2017-08-26 06:00 | 37.59 | 35.69
2017-08-26 06:30 | 37.6 | 35.69
2017-08-26 07:00 | 38.64 | 36.78
2017-08-26 07:30 | 40.14 | 38.32
2017-08-26 08:00 | 40.82 | 39.02
2017-08-26 08:30 | 41.13 | 39.28
2017-08-26 09:00 | 41.13 | 39.25
2017-08-26 09:30 | 40.84 | 38.92
2017-08-26 10:00 | 39.67 | 37.67
2017-08-26 10:30 | 39.24 | 37.18
2017-08-26 11:00 | 38.59 | 36.45
2017-08-26 11:30 | 38.2 | 36.03
2017-08-26 12:00 | 37.61 | 35.42
2017-08-26 12:30 | 39.11 | 37.04
2017-08-26 13:00 | 37.64 | 35.49
2017-08-26 13:30 | 37.62 | 35.47
2017-08-26 14:00 | 36.83 | 34.68
2017-08-26 14:30 | 36.66 | 34.54
2017-08-26 15:00 | 37.22 | 35.16
2017-08-26 15:30 | 37.56 | 35.52
2017-08-26 16:00 | 38.54 | 36.58
2017-08-26 16:30 | 40.89 | 39.05
2017-08-26 17:00 | 42.2 | 40.44
2017-08-26 17:30 | 45.11 | 43.47
2017-08-26 18:00 | 47.48 | 45.92
2017-08-26 18:30 | 49.97 | 48.44
2017-08-26 19:00 | 51.06 | 49.53
2017-08-26 19:30 | 49.53 | 47.94
2017-08-26 20:00 | 47.63 | 45.98
2017-08-26 20:30 | 45.63 | 43.93
2017-08-26 21:00 | 44.54 | 42.82
2017-08-26 21:30 | 43.6 | 41.84
2017-08-26 22:00 | 42 | 40.21
2017-08-26 22:30 | 40.18 | 38.34
2017-08-26 23:00 | 40.41 | 38.62
2017-08-26 23:30 | 37.6 | 35.69
2017-08-27 | 36.66 | 34.72
2017-08-27 00:30 | 36.22 | 34.31
2017-08-27 01:00 | 34.57 | 32.59
2017-08-27 01:30 | 33.25 | 31.19
2017-08-27 02:00 | 33.26 | 31.21
2017-08-27 02:30 | 32.98 | 30.91
2017-08-27 03:00 | 32.93 | 30.82
2017-08-27 03:30 | 33.18 | 31.08
2017-08-27 04:00 | 32.06 | 29.96
2017-08-27 04:30 | 32.08 | 30.02
2017-08-27 05:00 | 32.43 | 30.37
2017-08-27 05:30 | 33.13 | 31.1
2017-08-27 06:00 | 33.96 | 31.99
2017-08-27 06:30 | 34.47 | 32.53
2017-08-27 07:00 | 35.24 | 33.37
2017-08-27 07:30 | 36.87 | 35.07
2017-08-27 08:00 | 37.71 | 35.95
2017-08-27 08:30 | 37.41 | 35.59
2017-08-27 09:00 | 37.28 | 35.41
2017-08-27 09:30 | 38.41 | 36.55
2017-08-27 10:00 | 39.22 | 37.35
2017-08-27 10:30 | 39.66 | 37.78
2017-08-27 11:00 | 38.86 | 36.88
2017-08-27 11:30 | 38.33 | 36.32
2017-08-27 12:00 | 37.76 | 35.69
2017-08-27 12:30 | 37.57 | 35.52
2017-08-27 13:00 | 34.82 | 32.6
2017-08-27 13:30 | 34.63 | 32.4
2017-08-27 14:00 | 34.52 | 32.29
2017-08-27 14:30 | 35.02 | 32.85
2017-08-27 15:00 | 35.13 | 32.99
2017-08-27 15:30 | 35.54 | 33.49
2017-08-27 16:00 | 37.14 | 35.2
2017-08-27 16:30 | 39.57 | 37.76
2017-08-27 17:00 | 40.47 | 38.71
2017-08-27 17:30 | 43.55 | 41.87
2017-08-27 18:00 | 47.15 | 45.59
2017-08-27 18:30 | 52.03 | 50.54
2017-08-27 19:00 | 53.57 | 52.1
2017-08-27 19:30 | 51.95 | 50.45
2017-08-27 20:00 | 48.82 | 47.23
2017-08-27 20:30 | 46.5 | 44.85
2017-08-27 21:00 | 44.62 | 42.94
2017-08-27 21:30 | 42.82 | 41.09
2017-08-27 22:00 | 41.45 | 39.67
2017-08-27 22:30 | 39.55 | 37.7
2017-08-27 23:00 | 40.23 | 38.43
2017-08-27 23:30 | 36.59 | 34.65
2017-08-28 | 35.47 | 33.46
2017-08-28 00:30 | 35.07 | 33.07
2017-08-28 01:00 | 34.03 | 32
2017-08-28 01:30 | 33.18 | 31.09
2017-08-28 02:00 | 32.92 | 30.83
2017-08-28 02:30 | 33.16 | 31.07
2017-08-28 03:00 | 33.48 | 31.42
2017-08-28 03:30 | 33.44 | 31.4
2017-08-28 04:00 | 33.54 | 31.51
2017-08-28 04:30 | 34.19 | 32.19
2017-08-28 05:00 | 35.08 | 33.11
2017-08-28 05:30 | 37.42 | 35.52
2017-08-28 06:00 | 40.62 | 38.81
2017-08-28 06:30 | 44.75 | 43.04
2017-08-28 07:00 | 49.9 | 48.28
2017-08-28 07:30 | 53.51 | 52
2017-08-28 08:00 | 54.49 | 53.03
2017-08-28 08:30 | 54.06 | 52.52
2017-08-28 09:00 | 51.62 | 50.14
2017-08-28 09:30 | 51.7 | 50.21
2017-08-28 10:00 | 52.71 | 51.21
2017-08-28 10:30 | 52.67 | 51.12
2017-08-28 11:00 | 52 | 50.39
2017-08-28 11:30 | 52.59 | 50.95
2017-08-28 12:00 | 52.93 | 51.28
2017-08-28 12:30 | 52.95 | 51.33
2017-08-28 13:00 | 52.2 | 50.56
2017-08-28 13:30 | 54.45 | 52.87
2017-08-28 14:00 | 54.36 | 52.95
2017-08-28 14:30 | 54.18 | 52.76
2017-08-28 15:00 | 54.25 | 52.84
2017-08-28 15:30 | 54.42 | 53.05
2017-08-28 16:00 | 54.51 | 53.19
2017-08-28 16:30 | 55.25 | 54.03
2017-08-28 17:00 | 55.16 | 54
2017-08-28 17:30 | 55.29 | 54.21
2017-08-28 18:00 | 56.85 | 55.82
2017-08-28 18:30 | 60.02 | 59.04
2017-08-28 19:00 | 60.22 | 59.23
2017-08-28 19:30 | 58.11 | 57.11
2017-08-28 20:00 | 56.36 | 55.34
2017-08-28 20:30 | 53.44 | 52.39
2017-08-28 21:00 | 51.39 | 50.32
2017-08-28 21:30 | 49.24 | 48.16
2017-08-28 22:00 | 46.48 | 45.35
2017-08-28 22:30 | 44.51 | 43.37
2017-08-28 23:00 | 45.24 | 44.12
2017-08-28 23:30 | 40.41 | 38.98
2017-08-29 | 38.13 | 36.46
2017-08-29 00:30 | 38.03 | 36.38
2017-08-29 01:00 | 36.69 | 34.98
2017-08-29 01:30 | 35.74 | 33.99
2017-08-29 02:00 | 35.32 | 33.57
2017-08-29 02:30 | 34.84 | 33.07
2017-08-29 03:00 | 33.95 | 31.91
2017-08-29 03:30 | 33.31 | 31.23
2017-08-29 04:00 | 33.71 | 31.63
2017-08-29 04:30 | 34.28 | 32.23
2017-08-29 05:00 | 35.46 | 33.48
2017-08-29 05:30 | 37.76 | 35.86
2017-08-29 06:00 | 40.71 | 38.91
2017-08-29 06:30 | 44.98 | 43.3
2017-08-29 07:00 | 49.51 | 47.9
2017-08-29 07:30 | 53.45 | 52.03
2017-08-29 08:00 | 55.96 | 54.51
2017-08-29 08:30 | 54.54 | 53
2017-08-29 09:00 | 54.44 | 53.01
2017-08-29 09:30 | 55.03 | 53.57
2017-08-29 10:00 | 55.16 | 53.81
2017-08-29 10:30 | 54.2 | 52.83
2017-08-29 11:00 | 53.58 | 52.14
2017-08-29 11:30 | 53.82 | 52.38
2017-08-29 12:00 | 54.47 | 53.02
2017-08-29 12:30 | 54.96 | 53.52
2017-08-29 13:00 | 54.13 | 52.7
2017-08-29 13:30 | 55.52 | 54.12
2017-08-29 14:00 | 55.22 | 53.8
2017-08-29 14:30 | 56.73 | 55.35
2017-08-29 15:00 | 56.16 | 54.78
2017-08-29 15:30 | 56.07 | 54.71
2017-08-29 16:00 | 56.22 | 54.91
2017-08-29 16:30 | 57.17 | 55.96
2017-08-29 17:00 | 57.16 | 56.01
2017-08-29 17:30 | 57.33 | 56.26
2017-08-29 18:00 | 58.14 | 57.12
2017-08-29 18:30 | 61.65 | 60.67
2017-08-29 19:00 | 62.78 | 61.8
2017-08-29 19:30 | 60.04 | 59.04
2017-08-29 20:00 | 56 | 54.96
2017-08-29 20:30 | 54.72 | 53.69
2017-08-29 21:00 | 52.18 | 51.1
2017-08-29 21:30 | 50.09 | 49
2017-08-29 22:00 | 49.01 | 47.81
2017-08-29 22:30 | 46.62 | 45.3
2017-08-29 23:00 | 46.96 | 45.69
2017-08-29 23:30 | 42.15 | 40.67
2017-08-30 | 39.83 | 38.2
2017-08-30 00:30 | 39.12 | 37.48
2017-08-30 01:00 | 37.77 | 36.05
2017-08-30 01:30 | 37.38 | 35.65
2017-08-30 02:00 | 36.03 | 34.25
2017-08-30 02:30 | 36.32 | 34.57
2017-08-30 03:00 | 36.44 | 34.69
2017-08-30 03:30 | 36.41 | 34.69
2017-08-30 04:00 | 35.13 | 33.35
2017-08-30 04:30 | 35.89 | 34.18
2017-08-30 05:00 | 37.89 | 36.27
2017-08-30 05:30 | 41.99 | 40.49
2017-08-30 06:00 | 45.18 | 43.69
2017-08-30 06:30 | 49.38 | 47.96
2017-08-30 07:00 | 54.2 | 52.83
2017-08-30 07:30 | 61.75 | 57.48
2017-08-30 08:00 | 68.64 | 57.14
2017-08-30 08:30 | 61.85 | 56.24
2017-08-30 09:00 | 55.73 | 54.82
2017-08-30 09:30 | 54.92 | 54.07
2017-08-30 10:00 | 54.85 | 54
2017-08-30 10:30 | 55.55 | 54.62
2017-08-30 11:00 | 55.45 | 54.51
2017-08-30 11:30 | 55.31 | 54.42
2017-08-30 12:00 | 55.5 | 54.63
2017-08-30 12:30 | 56.39 | 55.56
2017-08-30 13:00 | 55.77 | 54.9
2017-08-30 13:30 | 55.78 | 54.89
2017-08-30 14:00 | 55.69 | 54.8
2017-08-30 14:30 | 56.23 | 55.37
2017-08-30 15:00 | 55.98 | 55.07
2017-08-30 15:30 | 56.09 | 55.13
2017-08-30 16:00 | 57.3 | 56.29
2017-08-30 16:30 | 58.77 | 57.51
2017-08-30 17:00 | 59.68 | 58.06
2017-08-30 17:30 | 60.35 | 58.16
2017-08-30 18:00 | 61.74 | 59.26
2017-08-30 18:30 | 64.4 | 62.27
2017-08-30 19:00 | 65.66 | 63.7
2017-08-30 19:30 | 63.65 | 61.52
2017-08-30 20:00 | 60.37 | 57.8
2017-08-30 20:30 | 58.27 | 55.32
2017-08-30 21:00 | 57.26 | 54.02
2017-08-30 21:30 | 53.74 | 51.4
2017-08-30 22:00 | 48.23 | 48.22
2017-08-30 22:30 | 46.08 | 46.06
2017-08-30 23:00 | 43.75 | 43.71
2017-08-30 23:30 | 41.15 | 41.09
2017-08-31 | 39.1 | 39.05
2017-08-31 00:30 | 38.05 | 38.01
2017-08-31 01:00 | 37.27 | 37.22
2017-08-31 01:30 | 36.6 | 36.55
2017-08-31 02:00 | 36.13 | 36.09
2017-08-31 02:30 | 36.02 | 35.98
2017-08-31 03:00 | 35.2 | 35.18
2017-08-31 03:30 | 35.18 | 35.14
2017-08-31 04:00 | 35.28 | 35.24
2017-08-31 04:30 | 36.26 | 36.21
2017-08-31 05:00 | 37.38 | 37.33
2017-08-31 05:30 | 39.89 | 39.82
2017-08-31 06:00 | 43.07 | 42.93
2017-08-31 06:30 | 50.5 | 47.44
2017-08-31 07:00 | 56.85 | 51.4
2017-08-31 07:30 | 60.48 | 55.21
2017-08-31 08:00 | 60.96 | 55.63
2017-08-31 08:30 | 60.63 | 55.23
2017-08-31 09:00 | 57.9 | 52.67
2017-08-31 09:30 | 58.15 | 52.84
2017-08-31 10:00 | 57.73 | 52.29
2017-08-31 10:30 | 58.31 | 52.83
2017-08-31 11:00 | 57.74 | 52.15
2017-08-31 11:30 | 57.83 | 52.22
2017-08-31 12:00 | 58.02 | 52.43
2017-08-31 12:30 | 58.2 | 52.67
2017-08-31 13:00 | 57.72 | 52.13
2017-08-31 13:30 | 58.16 | 52.63
2017-08-31 14:00 | 58.94 | 53.48
2017-08-31 14:30 | 59.22 | 53.78
2017-08-31 15:00 | 59.4 | 54.02
2017-08-31 15:30 | 60.43 | 55.2
2017-08-31 16:00 | 61.05 | 55.94
2017-08-31 16:30 | 60.31 | 55.3
2017-08-31 17:00 | 59.56 | 54.64
2017-08-31 17:30 | 59.63 | 54.86
2017-08-31 18:00 | 61.5 | 56.93
2017-08-31 18:30 | 64.39 | 60.04
2017-08-31 19:00 | 64.33 | 60
2017-08-31 19:30 | 63.25 | 58.86
2017-08-31 20:00 | 61.04 | 56.45
2017-08-31 20:30 | 59.65 | 55.02
2017-08-31 21:00 | 57.18 | 52.43
2017-08-31 21:30 | 54.81 | 49.88
2017-08-31 22:00 | 52.13 | 46.94
2017-08-31 22:30 | 49.95 | 44.57
2017-08-31 23:00 | 50.09 | 44.43
2017-08-31 23:30 | 46.66 | 40.49
2017-09-01 | 45.39 | 38.8
2017-09-01 00:30 | 44.76 | 37.93
2017-09-01 01:00 | 42.94 | 35.8
2017-09-01 01:30 | 42.07 | 34.77
2017-09-01 02:00 | 41.69 | 34.35
2017-09-01 02:30 | 41.83 | 34
2017-09-01 03:00 | 41.6 | 33.75
2017-09-01 03:30 | 41.04 | 33.09
2017-09-01 04:00 | 41.17 | 33.28
2017-09-01 04:30 | 41.87 | 34.13
2017-09-01 05:00 | 42.76 | 35.21
2017-09-01 05:30 | 44.92 | 37.75
2017-09-01 06:00 | 48.3 | 41.59
2017-09-01 06:30 | 51.64 | 45.33
2017-09-01 07:00 | 54.94 | 48.94
2017-09-01 07:30 | 58.47 | 53.03
2017-09-01 08:00 | 59.01 | 53.8
2017-09-01 08:30 | 53.46 | 52.96
2017-09-01 09:00 | 51.73 | 51.57
2017-09-01 09:30 | 51.13 | 50.89
2017-09-01 10:00 | 51.9 | 51.47
2017-09-01 10:30 | 56.59 | 51.1
2017-09-01 11:00 | 55.76 | 50.08
2017-09-01 11:30 | 54.85 | 49.08
2017-09-01 12:00 | 54.84 | 49.11
2017-09-01 12:30 | 55.49 | 49.87
2017-09-01 13:00 | 54.89 | 49.2
2017-09-01 13:30 | 56.09 | 50.52
2017-09-01 14:00 | 55.38 | 49.65
2017-09-01 14:30 | 55.69 | 50.04
2017-09-01 15:00 | 55.21 | 49.56
2017-09-01 15:30 | 55.64 | 50.08
2017-09-01 16:00 | 56.91 | 51.6
2017-09-01 16:30 | 58.33 | 53.29
2017-09-01 17:00 | 58.84 | 53.91
2017-09-01 17:30 | 57.34 | 52.38
2017-09-01 18:00 | 59.72 | 55.03
2017-09-01 18:30 | 61.18 | 56.6
2017-09-01 19:00 | 61.05 | 56.47
2017-09-01 19:30 | 59.68 | 54.98
2017-09-01 20:00 | 59.27 | 54.56
2017-09-01 20:30 | 57.57 | 52.75
2017-09-01 21:00 | 56.17 | 51.23
2017-09-01 21:30 | 54.09 | 49.03
2017-09-01 22:00 | 52.05 | 46.82
2017-09-01 22:30 | 50.13 | 44.62
2017-09-01 23:00 | 50.31 | 44.61
2017-09-01 23:30 | 47.97 | 41.42
2017-09-02 | 45.68 | 38.56
2017-09-02 00:30 | 44.76 | 37.51
2017-09-02 01:00 | 43.42 | 35.9
2017-09-02 01:30 | 42.28 | 34.56
2017-09-02 02:00 | 41.82 | 34.04
2017-09-02 02:30 | 41.39 | 33.53
2017-09-02 03:00 | 40.93 | 32.98
2017-09-02 03:30 | 40.43 | 32.39
2017-09-02 04:00 | 39.45 | 31.17
2017-09-02 04:30 | 41.1 | 33.24
2017-09-02 05:00 | 41.02 | 33.08
2017-09-02 05:30 | 41.86 | 34.09
2017-09-02 06:00 | 42.05 | 34.33
2017-09-02 06:30 | 42.93 | 35.4
2017-09-02 07:00 | 44.5 | 37.23
2017-09-02 07:30 | 46.15 | 39.11
2017-09-02 08:00 | 47.53 | 40.64
2017-09-02 08:30 | 48.38 | 41.51
2017-09-02 09:00 | 49.75 | 43.03
2017-09-02 09:30 | 49.74 | 42.94
2017-09-02 10:00 | 49.09 | 42.09
2017-09-02 10:30 | 47.79 | 40.57
2017-09-02 11:00 | 47.26 | 40.3
2017-09-02 11:30 | 46 | 38.82
2017-09-02 12:00 | 45.75 | 38.58
2017-09-02 12:30 | 45.09 | 37.77
2017-09-02 13:00 | 44.42 | 37.06
2017-09-02 13:30 | 43.85 | 36.4
2017-09-02 14:00 | 44.56 | 37.27
2017-09-02 14:30 | 43.69 | 36.29
2017-09-02 15:00 | 44.3 | 37.02
2017-09-02 15:30 | 45.18 | 38.14
2017-09-02 16:00 | 46.14 | 39.29
2017-09-02 16:30 | 48.3 | 41.9
2017-09-02 17:00 | 49.12 | 42.84
2017-09-02 17:30 | 51.43 | 45.47
2017-09-02 18:00 | 53.5 | 47.82
2017-09-02 18:30 | 56.16 | 50.76
2017-09-02 19:00 | 57.55 | 52.23
2017-09-02 19:30 | 56.03 | 50.54
2017-09-02 20:00 | 54.13 | 48.39
2017-09-02 20:30 | 53.12 | 47.28
2017-09-02 21:00 | 50.87 | 44.8
2017-09-02 21:30 | 50.79 | 44.74
2017-09-02 22:00 | 49.63 | 43.46
2017-09-02 22:30 | 47.54 | 41.03
2017-09-02 23:00 | 48.12 | 41.78
2017-09-02 23:30 | 45.61 | 38.64
2017-09-03 | 43.72 | 36.26
2017-09-03 00:30 | 43.05 | 35.46
2017-09-03 01:00 | 41.76 | 33.88
2017-09-03 01:30 | 42.26 | 34.54
2017-09-03 02:00 | 41.72 | 33.92
2017-09-03 02:30 | 40.93 | 33.03
2017-09-03 03:00 | 40.6 | 32.55
2017-09-03 03:30 | 40.73 | 32.77
2017-09-03 04:00 | 40.79 | 32.85
2017-09-03 04:30 | 40.14 | 32.05
2017-09-03 05:00 | 40.33 | 32.29
2017-09-03 05:30 | 40.88 | 32.91
2017-09-03 06:00 | 41.47 | 33.66
2017-09-03 06:30 | 40.53 | 32.64
2017-09-03 07:00 | 41.82 | 34.25
2017-09-03 07:30 | 42.94 | 35.5
2017-09-03 08:00 | 43.66 | 36.34
2017-09-03 08:30 | 44.25 | 36.97
2017-09-03 09:00 | 44.81 | 37.57
2017-09-03 09:30 | 44.38 | 36.99
2017-09-03 10:00 | 44.77 | 37.37
2017-09-03 10:30 | 44.35 | 36.81
2017-09-03 11:00 | 44.14 | 36.54
2017-09-03 11:30 | 43.74 | 35.98
2017-09-03 12:00 | 43.17 | 35.64
2017-09-03 12:30 | 42.95 | 35.58
2017-09-03 13:00 | 42.44 | 34.97
2017-09-03 13:30 | 41.73 | 34.12
2017-09-03 14:00 | 41.59 | 33.95
2017-09-03 14:30 | 42.26 | 34.72
2017-09-03 15:00 | 42.53 | 35.18
2017-09-03 15:30 | 43.19 | 36.01
2017-09-03 16:00 | 44.38 | 37.42
2017-09-03 16:30 | 45.88 | 39.28
2017-09-03 17:00 | 47.66 | 41.33
2017-09-03 17:30 | 49.09 | 43
2017-09-03 18:00 | 52.6 | 46.92
2017-09-03 18:30 | 57.1 | 51.87
2017-09-03 19:00 | 56.85 | 51.55
2017-09-03 19:30 | 55.16 | 49.67
2017-09-03 20:00 | 53.45 | 47.71
2017-09-03 20:30 | 52.19 | 46.4
2017-09-03 21:00 | 50.8 | 44.85
2017-09-03 21:30 | 49.83 | 43.8
2017-09-03 22:00 | 47.37 | 41.01
2017-09-03 22:30 | 45.37 | 38.53
2017-09-03 23:00 | 46.95 | 40.15
2017-09-03 23:30 | 42.94 | 35.39
2017-09-04 | 41.53 | 33.68
2017-09-04 00:30 | 41.69 | 33.93
2017-09-04 01:00 | 40.37 | 32.36
2017-09-04 01:30 | 39.79 | 31.63
2017-09-04 02:00 | 39.98 | 31.85
2017-09-04 02:30 | 39.64 | 31.49
2017-09-04 03:00 | 39.68 | 31.54
2017-09-04 03:30 | 38.62 | 30.22
2017-09-04 04:00 | 39.23 | 31.01
2017-09-04 04:30 | 39.8 | 31.71
2017-09-04 05:00 | 40.55 | 32.57
2017-09-04 05:30 | 42.81 | 35.28
2017-09-04 06:00 | 45.03 | 37.87
2017-09-04 06:30 | 47.8 | 41.02
2017-09-04 07:00 | 52.01 | 45.71
2017-09-04 07:30 | 55.74 | 49.73
2017-09-04 08:00 | 56.72 | 50.97
2017-09-04 08:30 | 55.23 | 51.83
2017-09-04 09:00 | 51.15 | 50.15
2017-09-04 09:30 | 50.76 | 50.06
2017-09-04 10:00 | 49.97 | 49.34
2017-09-04 10:30 | 49.97 | 49.51
2017-09-04 11:00 | 51.53 | 50.83
2017-09-04 11:30 | 51.71 | 50.88
2017-09-04 12:00 | 52.21 | 51.46
2017-09-04 12:30 | 52.7 | 51.95
2017-09-04 13:00 | 51.69 | 51.01
2017-09-04 13:30 | 51.48 | 50.79
2017-09-04 14:00 | 52.67 | 52.02
2017-09-04 14:30 | 53.93 | 53.24
2017-09-04 15:00 | 54.3 | 53.58
2017-09-04 15:30 | 54.19 | 53.33
2017-09-04 16:00 | 56.92 | 55.96
2017-09-04 16:30 | 57.75 | 56.39
2017-09-04 17:00 | 57.58 | 55.81
2017-09-04 17:30 | 57.86 | 55.51
2017-09-04 18:00 | 59.12 | 56.5
2017-09-04 18:30 | 62.39 | 60.22
2017-09-04 19:00 | 63.83 | 61.81
2017-09-04 19:30 | 61.74 | 59.51
2017-09-04 20:00 | 59.05 | 56.37
2017-09-04 20:30 | 57.24 | 54.28
2017-09-04 21:00 | 55.95 | 52.81
2017-09-04 21:30 | 53.92 | 50.17
2017-09-04 22:00 | 51.73 | 47.39
2017-09-04 22:30 | 47.46 | 44
2017-09-04 23:00 | 43.4 | 43.25
2017-09-04 23:30 | 43.43 | 40.97
2017-09-05 | 46.37 | 39.31
2017-09-05 00:30 | 45.6 | 38.43
2017-09-05 01:00 | 44.41 | 37.03
2017-09-05 01:30 | 43.88 | 36.38
2017-09-05 02:00 | 43.6 | 36.05
2017-09-05 02:30 | 43.32 | 35.74
2017-09-05 03:00 | 42.67 | 34.96
2017-09-05 03:30 | 42.45 | 34.71
2017-09-05 04:00 | 42.8 | 35.18
2017-09-05 04:30 | 44.04 | 36.65
2017-09-05 05:00 | 44.75 | 37.46
2017-09-05 05:30 | 46.89 | 39.9
2017-09-05 06:00 | 48.7 | 42
2017-09-05 06:30 | 52.58 | 46.33
2017-09-05 07:00 | 57.26 | 51.44
2017-09-05 07:30 | 60.81 | 55.48
2017-09-05 08:00 | 61.33 | 56.01
2017-09-05 08:30 | 61.52 | 56.18
2017-09-05 09:00 | 61.05 | 55.75
2017-09-05 09:30 | 60.48 | 55.08
2017-09-05 10:00 | 60.72 | 55.27
2017-09-05 10:30 | 60.79 | 55.25
2017-09-05 11:00 | 61.37 | 55.84
2017-09-05 11:30 | 61.85 | 56.63
2017-09-05 12:00 | 62.36 | 57.12
2017-09-05 12:30 | 61.68 | 56.44
2017-09-05 13:00 | 60.99 | 55.67
2017-09-05 13:30 | 60.74 | 55.43
2017-09-05 14:00 | 61.34 | 56.09
2017-09-05 14:30 | 62.14 | 56.94
2017-09-05 15:00 | 62.88 | 57.74
2017-09-05 15:30 | 63.37 | 58.22
2017-09-05 16:00 | 63.32 | 58.24
2017-09-05 16:30 | 63.41 | 58.51
2017-09-05 17:00 | 63.14 | 58.31
2017-09-05 17:30 | 62.13 | 57.4
2017-09-05 18:00 | 62.53 | 57.94
2017-09-05 18:30 | 65.32 | 60.93
2017-09-05 19:00 | 66.72 | 62.43
2017-09-05 19:30 | 64.72 | 60.3
2017-09-05 20:00 | 61.83 | 57.17
2017-09-05 20:30 | 59.78 | 55.01
2017-09-05 21:00 | 57.92 | 53.01
2017-09-05 21:30 | 54.73 | 49.31
2017-09-05 22:00 | 52.54 | 46.47
2017-09-05 22:30 | 50.46 | 44.1
2017-09-05 23:00 | 50.19 | 44
2017-09-05 23:30 | 47.81 | 41.05
2017-09-06 | 45.32 | 38
2017-09-06 00:30 | 45.78 | 38.54
2017-09-06 01:00 | 43.86 | 36.28
2017-09-06 01:30 | 43.43 | 35.79
2017-09-06 02:00 | 42.83 | 35.1
2017-09-06 02:30 | 42.49 | 34.72
2017-09-06 03:00 | 42.52 | 34.81
2017-09-06 03:30 | 41.84 | 33.92
2017-09-06 04:00 | 41.62 | 33.67
2017-09-06 04:30 | 42.54 | 34.86
2017-09-06 05:00 | 43.43 | 35.88
2017-09-06 05:30 | 46 | 38.91
2017-09-06 06:00 | 48.24 | 41.42
2017-09-06 06:30 | 51.14 | 44.69
2017-09-06 07:00 | 54.37 | 48.26
2017-09-06 07:30 | 58.71 | 53.23
2017-09-06 08:00 | 58.52 | 52.95
2017-09-06 08:30 | 58.45 | 52.74
2017-09-06 09:00 | 54.59 | 51.89
2017-09-06 09:30 | 52.63 | 51.14
2017-09-06 10:00 | 52.04 | 50.7
2017-09-06 10:30 | 51.45 | 50.3
2017-09-06 11:00 | 52.75 | 51.9
2017-09-06 11:30 | 53 | 52.3
2017-09-06 12:00 | 52.32 | 51.59
2017-09-06 12:30 | 53.65 | 52.91
2017-09-06 13:00 | 53.16 | 52.43
2017-09-06 13:30 | 53.28 | 52.63
2017-09-06 14:00 | 54.34 | 53.81
2017-09-06 14:30 | 55.12 | 54.63
2017-09-06 15:00 | 54.75 | 54.07
2017-09-06 15:30 | 54.89 | 54.2
2017-09-06 16:00 | 56.13 | 55.26
2017-09-06 16:30 | 57.54 | 56.35
2017-09-06 17:00 | 56.8 | 55.29
2017-09-06 17:30 | 58.05 | 56.02
2017-09-06 18:00 | 59.08 | 56.77
2017-09-06 18:30 | 62.55 | 60.68
2017-09-06 19:00 | 63.81 | 61.99
2017-09-06 19:30 | 63.11 | 61.17
2017-09-06 20:00 | 58.64 | 56.33
2017-09-06 20:30 | 56.48 | 53.66
2017-09-06 21:00 | 55.78 | 52.75
2017-09-06 21:30 | 53.49 | 50.06
2017-09-06 22:00 | 50.21 | 46.94
2017-09-06 22:30 | 44.72 | 44.46
2017-09-06 23:00 | 44.8 | 44.57
2017-09-06 23:30 | 43.2 | 41.58
2017-09-07 | 40.57 | 38.65
2017-09-07 00:30 | 40.24 | 38.33
2017-09-07 01:00 | 39.14 | 37.19
2017-09-07 01:30 | 38.23 | 36.25
2017-09-07 02:00 | 37.43 | 35.43
2017-09-07 02:30 | 36.87 | 34.86
2017-09-07 03:00 | 36.33 | 34.3
2017-09-07 03:30 | 36.59 | 34.58
2017-09-07 04:00 | 37.33 | 35.38
2017-09-07 04:30 | 37.06 | 35.1
2017-09-07 05:00 | 37.6 | 35.67
2017-09-07 05:30 | 40.19 | 38.32
2017-09-07 06:00 | 42.82 | 41.02
2017-09-07 06:30 | 47.13 | 45.44
2017-09-07 07:00 | 50.89 | 49.32
2017-09-07 07:30 | 54.24 | 52.79
2017-09-07 08:00 | 53.86 | 52.32
2017-09-07 08:30 | 53.88 | 52.59
2017-09-07 09:00 | 53.32 | 52.02
2017-09-07 09:30 | 53.54 | 52.21
2017-09-07 10:00 | 52.71 | 51.32
2017-09-07 10:30 | 54.02 | 52.61
2017-09-07 11:00 | 54.3 | 52.86
2017-09-07 11:30 | 54.04 | 52.58
2017-09-07 12:00 | 54.71 | 53.25
2017-09-07 12:30 | 55.02 | 53.58
2017-09-07 13:00 | 54.48 | 53.04
2017-09-07 13:30 | 54.41 | 52.96
2017-09-07 14:00 | 54.79 | 53.35
2017-09-07 14:30 | 55.71 | 54.3
2017-09-07 15:00 | 55.64 | 54.26
2017-09-07 15:30 | 56.07 | 54.71
2017-09-07 16:00 | 55.77 | 54.45
2017-09-07 16:30 | 57.49 | 56.28
2017-09-07 17:00 | 56.33 | 55.15
2017-09-07 17:30 | 55.94 | 54.83
2017-09-07 18:00 | 57.57 | 56.53
2017-09-07 18:30 | 60.15 | 59.14
2017-09-07 19:00 | 60.74 | 59.73
2017-09-07 19:30 | 59.28 | 58.25
2017-09-07 20:00 | 57.55 | 56.51
2017-09-07 20:30 | 55.16 | 54.1
2017-09-07 21:00 | 53.5 | 52.41
2017-09-07 21:30 | 50.54 | 49.43
2017-09-07 22:00 | 47.47 | 46.34
2017-09-07 22:30 | 44.94 | 43.72
2017-09-07 23:00 | 45.49 | 43.99
2017-09-07 23:30 | 42.48 | 40.89
2017-09-08 | 39.72 | 38.05
2017-09-08 00:30 | 39.09 | 37.42
2017-09-08 01:00 | 37.59 | 35.86
2017-09-08 01:30 | 37.22 | 35.49
2017-09-08 02:00 | 36.36 | 34.59
2017-09-08 02:30 | 36.05 | 34.28
2017-09-08 03:00 | 35.6 | 33.61
2017-09-08 03:30 | 35.46 | 33.44
2017-09-08 04:00 | 35.71 | 33.71
2017-09-08 04:30 | 36.5 | 34.54
2017-09-08 05:00 | 38.03 | 36.14
2017-09-08 05:30 | 39.59 | 37.72
2017-09-08 06:00 | 42.11 | 40.32
2017-09-08 06:30 | 46.11 | 44.42
2017-09-08 07:00 | 50.11 | 48.46
2017-09-08 07:30 | 53.94 | 52.48
2017-09-08 08:00 | 54.14 | 52.65
2017-09-08 08:30 | 63.87 | 53.25
2017-09-08 09:00 | 65.16 | 53.05
2017-09-08 09:30 | 64.6 | 52.53
2017-09-08 10:00 | 64.17 | 52.13
2017-09-08 10:30 | 64.75 | 52.71
2017-09-08 11:00 | 64.27 | 52.11
2017-09-08 11:30 | 64.55 | 52.36
2017-09-08 12:00 | 64.64 | 52.48
2017-09-08 12:30 | 64.94 | 52.93
2017-09-08 13:00 | 65.51 | 53.55
2017-09-08 13:30 | 65.56 | 53.7
2017-09-08 14:00 | 64.88 | 52.91
2017-09-08 14:30 | 64.44 | 52.49
2017-09-08 15:00 | 64.7 | 52.68
2017-09-08 15:30 | 65.12 | 53.15
2017-09-08 16:00 | 65.54 | 53.76
2017-09-08 16:30 | 66.52 | 55.11
2017-09-08 17:00 | 65.85 | 54.45
2017-09-08 17:30 | 57.36 | 54.17
2017-09-08 18:00 | 55.95 | 54.77
2017-09-08 18:30 | 58.32 | 57.17
2017-09-08 19:00 | 58.94 | 57.8
2017-09-08 19:30 | 57.64 | 56.47
2017-09-08 20:00 | 55.47 | 54.27
2017-09-08 20:30 | 53.11 | 51.9
2017-09-08 21:00 | 51.62 | 50.37
2017-09-08 21:30 | 49.56 | 48.32
2017-09-08 22:00 | 47.77 | 46.52
2017-09-08 22:30 | 46.33 | 45.06
2017-09-08 23:00 | 46.29 | 45.06
2017-09-08 23:30 | 42.59 | 41.17
2017-09-09 | 40.04 | 38.46
2017-09-09 00:30 | 39.21 | 37.62
2017-09-09 01:00 | 36.84 | 35.87
2017-09-09 01:30 | 36.09 | 35.09
2017-09-09 02:00 | 35.24 | 34.3
2017-09-09 02:30 | 34.4 | 33.46
2017-09-09 03:00 | 34.11 | 33.17
2017-09-09 03:30 | 34.06 | 33.11
2017-09-09 04:00 | 34.13 | 33.18
2017-09-09 04:30 | 34.29 | 33.35
2017-09-09 05:00 | 35.49 | 34.59
2017-09-09 05:30 | 36.57 | 35.72
2017-09-09 06:00 | 36.57 | 35.72
2017-09-09 06:30 | 38.6 | 37.8
2017-09-09 07:00 | 39.13 | 38.38
2017-09-09 07:30 | 41.85 | 41.16
2017-09-09 08:00 | 41.91 | 41.23
2017-09-09 08:30 | 42.7 | 41.96
2017-09-09 09:00 | 43.46 | 42.5
2017-09-09 09:30 | 48.58 | 41.84
2017-09-09 10:00 | 49.09 | 41.5
2017-09-09 10:30 | 54.79 | 39.8
2017-09-09 11:00 | 54.12 | 38.78
2017-09-09 11:30 | 53.37 | 37.92
2017-09-09 12:00 | 54.17 | 38.92
2017-09-09 12:30 | 53.42 | 38.02
2017-09-09 13:00 | 42.51 | 35.99
2017-09-09 13:30 | 37.98 | 36.08
2017-09-09 14:00 | 37.95 | 36.04
2017-09-09 14:30 | 36.89 | 34.97
2017-09-09 15:00 | 37.6 | 35.78
2017-09-09 15:30 | 39.38 | 37.65
2017-09-09 16:00 | 40.09 | 38.41
2017-09-09 16:30 | 43.24 | 41.71
2017-09-09 17:00 | 43.02 | 41.49
2017-09-09 17:30 | 45.88 | 44.46
2017-09-09 18:00 | 48.63 | 47.26
2017-09-09 18:30 | 52.73 | 51.4
2017-09-09 19:00 | 53.79 | 52.46
2017-09-09 19:30 | 51.61 | 50.25
2017-09-09 20:00 | 50.45 | 49.05
2017-09-09 20:30 | 48.21 | 46.77
2017-09-09 21:00 | 46.51 | 45.03
2017-09-09 21:30 | 44.56 | 43.05
2017-09-09 22:00 | 43.42 | 41.89
2017-09-09 22:30 | 41.34 | 39.78
2017-09-09 23:00 | 41.87 | 40.37
2017-09-09 23:30 | 38.64 | 36.83
2017-09-10 | 36.9 | 34.99
2017-09-10 00:30 | 36.53 | 34.61
2017-09-10 01:00 | 35.44 | 33.48
2017-09-10 01:30 | 34.44 | 32.45
2017-09-10 02:00 | 34.13 | 32.13
2017-09-10 02:30 | 33.64 | 31.61
2017-09-10 03:00 | 32.74 | 30.65
2017-09-10 03:30 | 32.21 | 30.09
2017-09-10 04:00 | 31.83 | 29.71
2017-09-10 04:30 | 31.66 | 29.54
2017-09-10 05:00 | 32.23 | 30.12
2017-09-10 05:30 | 33.93 | 31.9
2017-09-10 06:00 | 34.15 | 32.14
2017-09-10 06:30 | 34.17 | 32.19
2017-09-10 07:00 | 36.62 | 34.77
2017-09-10 07:30 | 37.98 | 36.19
2017-09-10 08:00 | 37.66 | 35.85
2017-09-10 08:30 | 38.92 | 37.13
2017-09-10 09:00 | 38.83 | 37
2017-09-10 09:30 | 40.6 | 38.84
2017-09-10 10:00 | 40.34 | 38.51
2017-09-10 10:30 | 42.06 | 40.28
2017-09-10 11:00 | 41.85 | 40.04
2017-09-10 11:30 | 39.57 | 37.67
2017-09-10 12:00 | 38.89 | 36.95
2017-09-10 12:30 | 39.56 | 37.66
2017-09-10 13:00 | 36.86 | 34.79
2017-09-10 13:30 | 36.49 | 34.4
2017-09-10 14:00 | 36.66 | 34.59
2017-09-10 14:30 | 36.51 | 34.46
2017-09-10 15:00 | 37.8 | 35.81
2017-09-10 15:30 | 38.95 | 37.03
2017-09-10 16:00 | 39.68 | 37.83
2017-09-10 16:30 | 41.54 | 39.8
2017-09-10 17:00 | 41.7 | 39.96
2017-09-10 17:30 | 44.88 | 43.25
2017-09-10 18:00 | 48.67 | 47.16
2017-09-10 18:30 | 56.73 | 50.94
2017-09-10 19:00 | 66.18 | 54.25
2017-09-10 19:30 | 64.38 | 52.01
2017-09-10 20:00 | 61.65 | 48.54
2017-09-10 20:30 | 60.15 | 46.52
2017-09-10 21:00 | 58.83 | 44.88
2017-09-10 21:30 | 57.42 | 43.09
2017-09-10 22:00 | 55.94 | 41.07
2017-09-10 22:30 | 54.4 | 38.97
2017-09-10 23:00 | 54.51 | 39.4
2017-09-10 23:30 | 52.17 | 36.28
2017-09-11 | 51.06 | 34.69
2017-09-11 00:30 | 50.74 | 34.19
2017-09-11 01:00 | 49.89 | 32.95
2017-09-11 01:30 | 49.63 | 32.55
2017-09-11 02:00 | 49.36 | 32.2
2017-09-11 02:30 | 49.25 | 32.1
2017-09-11 03:00 | 49.14 | 31.99
2017-09-11 03:30 | 49.31 | 32.21
2017-09-11 04:00 | 49.41 | 32.39
2017-09-11 04:30 | 50.1 | 33.4
2017-09-11 05:00 | 51.06 | 34.8
2017-09-11 05:30 | 52.43 | 36.69
2017-09-11 06:00 | 54.55 | 39.58
2017-09-11 06:30 | 57.79 | 43.81
2017-09-11 07:00 | 60.72 | 47.44
2017-09-11 07:30 | 62.87 | 50.32
2017-09-11 08:00 | 63.83 | 51.34
2017-09-11 08:30 | 64.21 | 52.26
2017-09-11 09:00 | 64.3 | 52.51
2017-09-11 09:30 | 63.78 | 51.76
2017-09-11 10:00 | 63.65 | 51.54
2017-09-11 10:30 | 64.07 | 51.99
2017-09-11 11:00 | 64.86 | 52.86
2017-09-11 11:30 | 65.98 | 54.2
2017-09-11 12:00 | 65.15 | 53.14
2017-09-11 12:30 | 65.69 | 53.78
2017-09-11 13:00 | 65.26 | 53.27
2017-09-11 13:30 | 65.43 | 53.43
2017-09-11 14:00 | 65.69 | 53.71
2017-09-11 14:30 | 65.73 | 53.87
2017-09-11 15:00 | 65.82 | 54.03
2017-09-11 15:30 | 66.29 | 54.45
2017-09-11 16:00 | 66.17 | 54.38
2017-09-11 16:30 | 66.83 | 55.25
2017-09-11 17:00 | 66.44 | 54.91
2017-09-11 17:30 | 66.72 | 55.27
2017-09-11 18:00 | 66.9 | 55.5
2017-09-11 18:30 | 69.57 | 58.71
2017-09-11 19:00 | 70.71 | 60.18
2017-09-11 19:30 | 68 | 56.97
2017-09-11 20:00 | 66.71 | 55.41
2017-09-11 20:30 | 64.34 | 52.64
2017-09-11 21:00 | 59.31 | 49.53
2017-09-11 21:30 | 52.72 | 47.09
2017-09-11 22:00 | 50.35 | 44.46
2017-09-11 22:30 | 47.76 | 41.7
2017-09-11 23:00 | 48.02 | 42.06
2017-09-11 23:30 | 44.94 | 38.46
2017-09-12 | 43.35 | 36.25
2017-09-12 00:30 | 42.9 | 35.7
2017-09-12 01:00 | 41.46 | 34.02
2017-09-12 01:30 | 40.76 | 33.18
2017-09-12 02:00 | 40.89 | 33.07
2017-09-12 02:30 | 40.72 | 32.65
2017-09-12 03:00 | 40.42 | 32.35
2017-09-12 03:30 | 40.29 | 32.2
2017-09-12 04:00 | 40.48 | 32.43
2017-09-12 04:30 | 41.08 | 33.18
2017-09-12 05:00 | 42.18 | 34.47
2017-09-12 05:30 | 44.35 | 37
2017-09-12 06:00 | 46.87 | 39.91
2017-09-12 06:30 | 50.69 | 44.21
2017-09-12 07:00 | 54.11 | 47.95
2017-09-12 07:30 | 58.86 | 53.19
2017-09-12 08:00 | 57.49 | 51.66
2017-09-12 08:30 | 55.94 | 50.07
2017-09-12 09:00 | 57.84 | 52.22
2017-09-12 09:30 | 57.3 | 51.73
2017-09-12 10:00 | 58.72 | 53.27
2017-09-12 10:30 | 59.02 | 53.5
2017-09-12 11:00 | 55.14 | 54.25
2017-09-12 11:30 | 53.79 | 53.25
2017-09-12 12:00 | 53.63 | 53.15
2017-09-12 12:30 | 53.42 | 52.86
2017-09-12 13:00 | 52.67 | 52.12
2017-09-12 13:30 | 53.57 | 53.07
2017-09-12 14:00 | 53.28 | 52.8
2017-09-12 14:30 | 54.18 | 53.72
2017-09-12 15:00 | 54.1 | 53.59
2017-09-12 15:30 | 55.97 | 55.45
2017-09-12 16:00 | 56.85 | 56.19
2017-09-12 16:30 | 55.53 | 54.45
2017-09-12 17:00 | 54.85 | 53.29
2017-09-12 17:30 | 53.54 | 50.98
2017-09-12 18:00 | 55.78 | 52.84
2017-09-12 18:30 | 55.73 | 52.8
2017-09-12 19:00 | 57.18 | 54.3
2017-09-12 19:30 | 52.85 | 50.63
2017-09-12 20:00 | 51.19 | 48.83
2017-09-12 20:30 | 48.9 | 46.08
2017-09-12 21:00 | 47.69 | 44.61
2017-09-12 21:30 | 46.62 | 42.98
2017-09-12 22:00 | 42.27 | 39.66
2017-09-12 22:30 | 37.73 | 37.07
2017-09-12 23:00 | 39.69 | 39.63
2017-09-12 23:30 | 35.26 | 35.21
2017-09-13 | 34.02 | 33.82
2017-09-13 00:30 | 33.84 | 33.58
2017-09-13 01:00 | 32.53 | 32.28
2017-09-13 01:30 | 31.38 | 31.14
2017-09-13 02:00 | 30.49 | 30.28
2017-09-13 02:30 | 29.56 | 29.4
2017-09-13 03:00 | 28.99 | 28.86
2017-09-13 03:30 | 28.65 | 28.53
2017-09-13 04:00 | 28.97 | 28.84
2017-09-13 04:30 | 30.4 | 30.25
2017-09-13 05:00 | 31.22 | 31.03
2017-09-13 05:30 | 33.24 | 32.94
2017-09-13 06:00 | 36.29 | 35.84
2017-09-13 06:30 | 40.65 | 40
2017-09-13 07:00 | 46.35 | 44.44
2017-09-13 07:30 | 55.94 | 50.17
2017-09-13 08:00 | 57.35 | 51.78
2017-09-13 08:30 | 58.78 | 53.5
2017-09-13 09:00 | 58.42 | 53.08
2017-09-13 09:30 | 57.46 | 51.99
2017-09-13 10:00 | 57.77 | 52.28
2017-09-13 10:30 | 58.22 | 52.7
2017-09-13 11:00 | 57.71 | 52.1
2017-09-13 11:30 | 56.97 | 51.16
2017-09-13 12:00 | 57.48 | 51.76
2017-09-13 12:30 | 57.62 | 51.88
2017-09-13 13:00 | 56.88 | 51.07
2017-09-13 13:30 | 57.46 | 51.65
2017-09-13 14:00 | 57.79 | 52
2017-09-13 14:30 | 58.61 | 52.92
2017-09-13 15:00 | 58.33 | 52.67
2017-09-13 15:30 | 57.97 | 52.3
2017-09-13 16:00 | 58.12 | 52.6
2017-09-13 16:30 | 58.26 | 52.87
2017-09-13 17:00 | 57.54 | 52.24
2017-09-13 17:30 | 57.95 | 52.83
2017-09-13 18:00 | 57.2 | 51.99
2017-09-13 18:30 | 58.68 | 53.48
2017-09-13 19:00 | 59.59 | 54.49
2017-09-13 19:30 | 57.46 | 52.17
2017-09-13 20:00 | 55.6 | 50.12
2017-09-13 20:30 | 53.45 | 47.76
2017-09-13 21:00 | 51.01 | 45.16
2017-09-13 21:30 | 49.11 | 43.15
2017-09-13 22:00 | 46.48 | 40.26
2017-09-13 22:30 | 45.05 | 38.65
2017-09-13 23:00 | 44.53 | 38.12
2017-09-13 23:30 | 41.9 | 35.01
2017-09-14 | 40.1 | 32.86
2017-09-14 00:30 | 40.27 | 32.2
2017-09-14 01:00 | 39.36 | 31
2017-09-14 01:30 | 38.84 | 30.31
2017-09-14 02:00 | 38.05 | 29.39
2017-09-14 02:30 | 37.63 | 28.87
2017-09-14 03:00 | 37.33 | 28.53
2017-09-14 03:30 | 37.17 | 28.37
2017-09-14 04:00 | 37.48 | 28.72
2017-09-14 04:30 | 37.82 | 29.18
2017-09-14 05:00 | 38.42 | 29.91
2017-09-14 05:30 | 40.54 | 32.52
2017-09-14 06:00 | 43.11 | 35.57
2017-09-14 06:30 | 46.3 | 39.24
2017-09-14 07:00 | 49.95 | 43.31
2017-09-14 07:30 | 53.83 | 47.78
2017-09-14 08:00 | 55.54 | 49.62
2017-09-14 08:30 | 56.91 | 52.78
2017-09-14 09:00 | 53.61 | 52.19
2017-09-14 09:30 | 52.01 | 50.53
2017-09-14 10:00 | 52.66 | 51.15
2017-09-14 10:30 | 53.35 | 51.8
2017-09-14 11:00 | 53.46 | 51.87
2017-09-14 11:30 | 54.34 | 52.72
2017-09-14 12:00 | 56.12 | 54.54
2017-09-14 12:30 | 57.41 | 55.87
2017-09-14 13:00 | 57.13 | 55.58
2017-09-14 13:30 | 58 | 56.46
2017-09-14 14:00 | 58.45 | 56.92
2017-09-14 14:30 | 58.28 | 56.75
2017-09-14 15:00 | 58.65 | 57.15
2017-09-14 15:30 | 58.47 | 56.97
2017-09-14 16:00 | 58.46 | 57.01
2017-09-14 16:30 | 59.01 | 57.64
2017-09-14 17:00 | 58.32 | 57.01
2017-09-14 17:30 | 57 | 55.75
2017-09-14 18:00 | 57.13 | 55.89
2017-09-14 18:30 | 58.67 | 57.38
2017-09-14 19:00 | 59.38 | 58.03
2017-09-14 19:30 | 57.58 | 56.11
2017-09-14 20:00 | 55.37 | 53.87
2017-09-14 20:30 | 53.15 | 51.61
2017-09-14 21:00 | 50.92 | 49.36
2017-09-14 21:30 | 47.87 | 46.28
2017-09-14 22:00 | 45.19 | 43.54
2017-09-14 22:30 | 42.89 | 41.2
2017-09-14 23:00 | 42.68 | 41
2017-09-14 23:30 | 39.41 | 37.29
2017-09-15 | 37.77 | 35.42
2017-09-15 00:30 | 36.78 | 34.55
2017-09-15 01:00 | 35.61 | 33.4
2017-09-15 01:30 | 35.09 | 32.82
2017-09-15 02:00 | 34.31 | 31.96
2017-09-15 02:30 | 33.77 | 31.35
2017-09-15 03:00 | 33.34 | 30.86
2017-09-15 03:30 | 33.23 | 30.7
2017-09-15 04:00 | 33.35 | 30.83
2017-09-15 04:30 | 33.9 | 31.44
2017-09-15 05:00 | 34.79 | 32.42
2017-09-15 05:30 | 36.93 | 34.8
2017-09-15 06:00 | 39.34 | 37.43
2017-09-15 06:30 | 42.49 | 40.81
2017-09-15 07:00 | 46.31 | 44.86
2017-09-15 07:30 | 50.44 | 49.1
2017-09-15 08:00 | 51.48 | 50.12
2017-09-15 08:30 | 51.58 | 50.21
2017-09-15 09:00 | 50.71 | 49.14
2017-09-15 09:30 | 49.78 | 48.13
2017-09-15 10:00 | 48.48 | 46.8
2017-09-15 10:30 | 48.54 | 46.92
2017-09-15 11:00 | 47.85 | 46.23
2017-09-15 11:30 | 46.58 | 44.95
2017-09-15 12:00 | 46.61 | 44.97
2017-09-15 12:30 | 48.17 | 46.56
2017-09-15 13:00 | 48.32 | 46.71
2017-09-15 13:30 | 47.31 | 45.64
2017-09-15 14:00 | 46.84 | 45.13
2017-09-15 14:30 | 47.05 | 45.33
2017-09-15 15:00 | 46.89 | 45.15
2017-09-15 15:30 | 47.37 | 45.59
2017-09-15 16:00 | 49.54 | 47.78
2017-09-15 16:30 | 50.21 | 48.42
2017-09-15 17:00 | 49.33 | 47.43
2017-09-15 17:30 | 48.58 | 46.55
2017-09-15 18:00 | 48.59 | 46.51
2017-09-15 18:30 | 50.47 | 48.72
2017-09-15 19:00 | 51.31 | 49.63
2017-09-15 19:30 | 50.07 | 48.33
2017-09-15 20:00 | 49.18 | 47.38
2017-09-15 20:30 | 45.82 | 43.8
2017-09-15 21:00 | 43.81 | 41.63
2017-09-15 21:30 | 42.54 | 40.24
2017-09-15 22:00 | 40.26 | 37.74
2017-09-15 22:30 | 38.75 | 36.33
2017-09-15 23:00 | 39.04 | 36.68
2017-09-15 23:30 | 35.75 | 33.31
2017-09-16 | 33.43 | 30.9
2017-09-16 00:30 | 32.53 | 29.89
2017-09-16 01:00 | 31.15 | 28.34
2017-09-16 01:30 | 31.01 | 28.15
2017-09-16 02:00 | 30.69 | 27.78
2017-09-16 02:30 | 29.87 | 26.85
2017-09-16 03:00 | 29.47 | 26.39
2017-09-16 03:30 | 29.46 | 26.38
2017-09-16 04:00 | 30.26 | 27.26
2017-09-16 04:30 | 29.65 | 26.6
2017-09-16 05:00 | 29.9 | 26.91
2017-09-16 05:30 | 31.04 | 28.22
2017-09-16 06:00 | 32.42 | 29.79
2017-09-16 06:30 | 34.81 | 32.41
2017-09-16 07:00 | 35.35 | 33.04
2017-09-16 07:30 | 36.83 | 34.7
2017-09-16 08:00 | 36.87 | 34.79
2017-09-16 08:30 | 39.06 | 37.18
2017-09-16 09:00 | 38.73 | 36.9
2017-09-16 09:30 | 38.97 | 37.2
2017-09-16 10:00 | 40.44 | 38.68
2017-09-16 10:30 | 40.82 | 38.97
2017-09-16 11:00 | 39.12 | 37.18
2017-09-16 11:30 | 38.08 | 36.1
2017-09-16 12:00 | 38.06 | 36.06
2017-09-16 12:30 | 38.46 | 36.46
2017-09-16 13:00 | 37.52 | 35.43
2017-09-16 13:30 | 36.99 | 34.83
2017-09-16 14:00 | 35.93 | 33.69
2017-09-16 14:30 | 36.47 | 34.22
2017-09-16 15:00 | 37.66 | 35.46
2017-09-16 15:30 | 37.38 | 35.16
2017-09-16 16:00 | 38.68 | 36.49
2017-09-16 16:30 | 40.29 | 38.17
2017-09-16 17:00 | 41.29 | 39.21
2017-09-16 17:30 | 43.1 | 41.11
2017-09-16 18:00 | 44.68 | 42.78
2017-09-16 18:30 | 47.5 | 45.81
2017-09-16 19:00 | 48.09 | 46.43
2017-09-16 19:30 | 45.34 | 43.55
2017-09-16 20:00 | 43.61 | 41.71
2017-09-16 20:30 | 42.3 | 40.27
2017-09-16 21:00 | 41.62 | 39.55
2017-09-16 21:30 | 39.91 | 37.68
2017-09-16 22:00 | 39.08 | 36.77
2017-09-16 22:30 | 38.22 | 35.81
2017-09-16 23:00 | 38.32 | 35.88
2017-09-16 23:30 | 35.35 | 32.89
2017-09-17 | 32.82 | 30.22
2017-09-17 00:30 | 32.08 | 29.38
2017-09-17 01:00 | 31.3 | 28.51
2017-09-17 01:30 | 32.41 | 29.71
2017-09-17 02:00 | 32.12 | 29.4
2017-09-17 02:30 | 30.27 | 27.31
2017-09-17 03:00 | 30.08 | 27.11
2017-09-17 03:30 | 30.97 | 28.08
2017-09-17 04:00 | 30.29 | 27.31
2017-09-17 04:30 | 29.96 | 26.95
2017-09-17 05:00 | 30.95 | 28.05
2017-09-17 05:30 | 31.24 | 28.36
2017-09-17 06:00 | 30.61 | 27.67
2017-09-17 06:30 | 30.51 | 27.49
2017-09-17 07:00 | 31.91 | 29.07
2017-09-17 07:30 | 33.69 | 31.07
2017-09-17 08:00 | 32.63 | 29.98
2017-09-17 08:30 | 33.33 | 30.79
2017-09-17 09:00 | 35.01 | 32.7
2017-09-17 09:30 | 35.49 | 33.29
2017-09-17 10:00 | 34.61 | 32.4
2017-09-17 10:30 | 34.85 | 32.75
2017-09-17 11:00 | 34.11 | 31.98
2017-09-17 11:30 | 33.88 | 31.74
2017-09-17 12:00 | 34.51 | 32.15
2017-09-17 12:30 | 34.91 | 32.47
2017-09-17 13:00 | 34.7 | 32.24
2017-09-17 13:30 | 35.16 | 32.72
2017-09-17 14:00 | 35.17 | 32.72
2017-09-17 14:30 | 34.75 | 32.24
2017-09-17 15:00 | 35.73 | 33.29
2017-09-17 15:30 | 37.11 | 34.75
2017-09-17 16:00 | 38.97 | 36.71
2017-09-17 16:30 | 39.52 | 37.26
2017-09-17 17:00 | 40.2 | 38
2017-09-17 17:30 | 42.43 | 40.37
2017-09-17 18:00 | 45.33 | 43.43
2017-09-17 18:30 | 47.38 | 45.64
2017-09-17 19:00 | 48.04 | 46.34
2017-09-17 19:30 | 46.77 | 45
2017-09-17 20:00 | 44.55 | 42.64
2017-09-17 20:30 | 42.77 | 40.74
2017-09-17 21:00 | 41.1 | 38.95
2017-09-17 21:30 | 39.9 | 37.63
2017-09-17 22:00 | 38.67 | 36.28
2017-09-17 22:30 | 37.5 | 35
2017-09-17 23:00 | 37.6 | 35.08
2017-09-17 23:30 | 34.19 | 31.37
2017-09-18 | 32.4 | 29.65
2017-09-18 00:30 | 32.15 | 29.47
2017-09-18 01:00 | 30.79 | 27.93
2017-09-18 01:30 | 30.33 | 27.41
2017-09-18 02:00 | 30.51 | 27.61
2017-09-18 02:30 | 30.48 | 27.57
2017-09-18 03:00 | 30.32 | 27.38
2017-09-18 03:30 | 30.73 | 27.82
2017-09-18 04:00 | 30.43 | 27.5
2017-09-18 04:30 | 30.84 | 27.98
2017-09-18 05:00 | 32.08 | 29.37
2017-09-18 05:30 | 34.02 | 31.58
2017-09-18 06:00 | 36.46 | 34.3
2017-09-18 06:30 | 40.01 | 38.16
2017-09-18 07:00 | 43.24 | 41.69
2017-09-18 07:30 | 47.7 | 46.23
2017-09-18 08:00 | 50.06 | 48.7
2017-09-18 08:30 | 52.54 | 51.07
2017-09-18 09:00 | 52.65 | 51.21
2017-09-18 09:30 | 53.32 | 51.93
2017-09-18 10:00 | 51.62 | 50.21
2017-09-18 10:30 | 51.82 | 50.45
2017-09-18 11:00 | 52.98 | 51.67
2017-09-18 11:30 | 53.18 | 51.9
2017-09-18 12:00 | 53.22 | 51.98
2017-09-18 12:30 | 54.35 | 53.13
2017-09-18 13:00 | 54.85 | 53.64
2017-09-18 13:30 | 52.68 | 51.41
2017-09-18 14:00 | 52.99 | 51.74
2017-09-18 14:30 | 53.46 | 52.2
2017-09-18 15:00 | 53.75 | 52.47
2017-09-18 15:30 | 54.72 | 52.77
2017-09-18 16:00 | 54.56 | 52.23
2017-09-18 16:30 | 57.68 | 51.96
2017-09-18 17:00 | 64.52 | 50.99
2017-09-18 17:30 | 63.84 | 49.74
2017-09-18 18:00 | 64.19 | 49.91
2017-09-18 18:30 | 65.44 | 51.57
2017-09-18 19:00 | 65.99 | 52.32
2017-09-18 19:30 | 64.81 | 50.57
2017-09-18 20:00 | 63.1 | 48.19
2017-09-18 20:30 | 61.54 | 45.92
2017-09-18 21:00 | 60.26 | 44
2017-09-18 21:30 | 58.88 | 41.94
2017-09-18 22:00 | 54.62 | 38.54
2017-09-18 22:30 | 52.7 | 36.77
2017-09-18 23:00 | 52.9 | 37
2017-09-18 23:30 | 51.64 | 35.11
2017-09-19 | 50.42 | 33.3
2017-09-19 00:30 | 49.14 | 32.15
2017-09-19 01:00 | 48.27 | 30.83
2017-09-19 01:30 | 47.73 | 30.61
2017-09-19 02:00 | 47.48 | 30.58
2017-09-19 02:30 | 46.54 | 30.13
2017-09-19 03:00 | 46.1 | 29.4
2017-09-19 03:30 | 45.74 | 28.79
2017-09-19 04:00 | 45.7 | 28.69
2017-09-19 04:30 | 45.93 | 29.17
2017-09-19 05:00 | 46.96 | 30.85
2017-09-19 05:30 | 42.62 | 32.84
2017-09-19 06:00 | 37.84 | 35.86
2017-09-19 06:30 | 41.6 | 39.93
2017-09-19 07:00 | 45.38 | 43.88
2017-09-19 07:30 | 48.6 | 47.13
2017-09-19 08:00 | 51.01 | 49.47
2017-09-19 08:30 | 54.3 | 52.83
2017-09-19 09:00 | 53.78 | 52.36
2017-09-19 09:30 | 55.57 | 54.25
2017-09-19 10:00 | 57.36 | 56.11
2017-09-19 10:30 | 56.61 | 55.36
2017-09-19 11:00 | 55.29 | 54.01
2017-09-19 11:30 | 55.15 | 53.88
2017-09-19 12:00 | 52.97 | 51.57
2017-09-19 12:30 | 55.57 | 54.06
2017-09-19 13:00 | 56.6 | 54.73
2017-09-19 13:30 | 54.86 | 52.92
2017-09-19 14:00 | 56.49 | 54.43
2017-09-19 14:30 | 56.25 | 54.08
2017-09-19 15:00 | 56.57 | 54.42
2017-09-19 15:30 | 56.41 | 54.2
2017-09-19 16:00 | 56.61 | 54.33
2017-09-19 16:30 | 56.09 | 53.67
2017-09-19 17:00 | 59.95 | 52.77
2017-09-19 17:30 | 64.99 | 51.18
2017-09-19 18:00 | 65.4 | 51.59
2017-09-19 18:30 | 65.7 | 52.11
2017-09-19 19:00 | 65.44 | 51.66
2017-09-19 19:30 | 63.49 | 48.94
2017-09-19 20:00 | 62.08 | 46.87
2017-09-19 20:30 | 60.94 | 45.24
2017-09-19 21:00 | 60.34 | 44.21
2017-09-19 21:30 | 58.32 | 41.11
2017-09-19 22:00 | 56.93 | 38.79
2017-09-19 22:30 | 56.34 | 37.67
2017-09-19 23:00 | 53.96 | 37.59
2017-09-19 23:30 | 51.17 | 34.32
2017-09-20 | 49.26 | 32.05
2017-09-20 00:30 | 48.07 | 31.39
2017-09-20 01:00 | 46.95 | 29.63
2017-09-20 01:30 | 46.42 | 28.96
2017-09-20 02:00 | 46 | 29.23
2017-09-20 02:30 | 46.36 | 29.75
2017-09-20 03:00 | 46.38 | 29.75
2017-09-20 03:30 | 46.18 | 29.42
2017-09-20 04:00 | 46.71 | 30.19
2017-09-20 04:30 | 45.85 | 28.87
2017-09-20 05:00 | 46.27 | 29.66
2017-09-20 05:30 | 43.32 | 32.68
2017-09-20 06:00 | 37.84 | 35.86
2017-09-20 06:30 | 41.43 | 39.74
2017-09-20 07:00 | 44.38 | 42.86
2017-09-20 07:30 | 48.92 | 47.49
2017-09-20 08:00 | 49.94 | 48.45
2017-09-20 08:30 | 51.06 | 49.47
2017-09-20 09:00 | 52.13 | 50.66
2017-09-20 09:30 | 53.29 | 51.92
2017-09-20 10:00 | 54.45 | 53.14
2017-09-20 10:30 | 55.02 | 53.78
2017-09-20 11:00 | 55.49 | 54.3
2017-09-20 11:30 | 55.84 | 54.65
2017-09-20 12:00 | 56.4 | 55.21
2017-09-20 12:30 | 56.52 | 55.37
2017-09-20 13:00 | 55.97 | 54.81
2017-09-20 13:30 | 56.15 | 54.98
2017-09-20 14:00 | 56.35 | 55.19
2017-09-20 14:30 | 56.45 | 55.3
2017-09-20 15:00 | 56.77 | 55.62
2017-09-20 15:30 | 56.34 | 55.16
2017-09-20 16:00 | 55.18 | 53.9
2017-09-20 16:30 | 56.27 | 54.94
2017-09-20 17:00 | 56.51 | 55.15
2017-09-20 17:30 | 55.16 | 53.63
2017-09-20 18:00 | 55.15 | 53.54
2017-09-20 18:30 | 55.6 | 53.99
2017-09-20 19:00 | 57.16 | 55.6
2017-09-20 19:30 | 54.7 | 53.01
2017-09-20 20:00 | 52.39 | 50.57
2017-09-20 20:30 | 49.51 | 47.52
2017-09-20 21:00 | 47.63 | 45.5
2017-09-20 21:30 | 45.73 | 43.43
2017-09-20 22:00 | 43.49 | 40.99
2017-09-20 22:30 | 41.09 | 38.36
2017-09-20 23:00 | 41.7 | 38.98
2017-09-20 23:30 | 38.85 | 35.84
2017-09-21 | 36.07 | 33.11
2017-09-21 00:30 | 34.93 | 32.21
2017-09-21 01:00 | 34.1 | 31.29
2017-09-21 01:30 | 33.36 | 30.58
2017-09-21 02:00 | 32.59 | 29.98
2017-09-21 02:30 | 32.35 | 29.7
2017-09-21 03:00 | 32.24 | 29.56
2017-09-21 03:30 | 32.24 | 29.53
2017-09-21 04:00 | 32.13 | 29.41
2017-09-21 04:30 | 32.83 | 30.18
2017-09-21 05:00 | 33.96 | 31.46
2017-09-21 05:30 | 35.85 | 33.59
2017-09-21 06:00 | 37.98 | 35.92
2017-09-21 06:30 | 41.75 | 40.01
2017-09-21 07:00 | 44.28 | 42.76
2017-09-21 07:30 | 46.43 | 44.91
2017-09-21 08:00 | 47.84 | 46.45
2017-09-21 08:30 | 49.8 | 48.29
2017-09-21 09:00 | 51.07 | 49.56
2017-09-21 09:30 | 52.18 | 50.75
2017-09-21 10:00 | 52.39 | 51.04
2017-09-21 10:30 | 52.55 | 51.23
2017-09-21 11:00 | 53.65 | 52.42
2017-09-21 11:30 | 53.84 | 52.62
2017-09-21 12:00 | 54.57 | 53.38
2017-09-21 12:30 | 55.35 | 54.17
2017-09-21 13:00 | 54.89 | 53.69
2017-09-21 13:30 | 55.35 | 54.17
2017-09-21 14:00 | 55.26 | 54.08
2017-09-21 14:30 | 55.25 | 54.08
2017-09-21 15:00 | 55.26 | 54.08
2017-09-21 15:30 | 55.67 | 54.47
2017-09-21 16:00 | 56.21 | 54.97
2017-09-21 16:30 | 56.02 | 54.71
2017-09-21 17:00 | 55.67 | 54.28
2017-09-21 17:30 | 54.54 | 53
2017-09-21 18:00 | 55.61 | 54.04
2017-09-21 18:30 | 57.02 | 55.5
2017-09-21 19:00 | 57.09 | 55.56
2017-09-21 19:30 | 55.12 | 53.49
2017-09-21 20:00 | 53.02 | 51.29
2017-09-21 20:30 | 51 | 49.15
2017-09-21 21:00 | 49.52 | 47.56
2017-09-21 21:30 | 47.01 | 44.86
2017-09-21 22:00 | 44.45 | 42.07
2017-09-21 22:30 | 42.39 | 39.81
2017-09-21 23:00 | 42.12 | 39.5
2017-09-21 23:30 | 39.57 | 36.68
2017-09-22 | 37.77 | 34.7
2017-09-22 00:30 | 36.82 | 33.77
2017-09-22 01:00 | 34.99 | 32.32
2017-09-22 01:30 | 34.21 | 31.46
2017-09-22 02:00 | 33.18 | 30.51
2017-09-22 02:30 | 32.35 | 29.71
2017-09-22 03:00 | 32.12 | 29.45
2017-09-22 03:30 | 32.09 | 29.41
2017-09-22 04:00 | 32.07 | 29.39
2017-09-22 04:30 | 33.07 | 30.51
2017-09-22 05:00 | 33.86 | 31.4
2017-09-22 05:30 | 36.12 | 33.91
2017-09-22 06:00 | 38.42 | 36.4
2017-09-22 06:30 | 41.15 | 39.4
2017-09-22 07:00 | 44.03 | 42.5
2017-09-22 07:30 | 47.25 | 45.8
2017-09-22 08:00 | 50.83 | 49.3
2017-09-22 08:30 | 53.25 | 51.79
2017-09-22 09:00 | 56.01 | 54.72
2017-09-22 09:30 | 57.87 | 56.68
2017-09-22 10:00 | 56.82 | 55.62
2017-09-22 10:30 | 57.05 | 55.91
2017-09-22 11:00 | 56.34 | 55.16
2017-09-22 11:30 | 57.04 | 55.87
2017-09-22 12:00 | 57.79 | 56.6
2017-09-22 12:30 | 57.95 | 56.79
2017-09-22 13:00 | 57.82 | 56.68
2017-09-22 13:30 | 57.65 | 56.49
2017-09-22 14:00 | 57.24 | 56.1
2017-09-22 14:30 | 56.51 | 55.36
2017-09-22 15:00 | 56.37 | 55.2
2017-09-22 15:30 | 57.39 | 56.19
2017-09-22 16:00 | 56.98 | 55.73
2017-09-22 16:30 | 56.91 | 55.59
2017-09-22 17:00 | 56.22 | 54.82
2017-09-22 17:30 | 55.12 | 53.59
2017-09-22 18:00 | 54.18 | 52.52
2017-09-22 18:30 | 54.1 | 52.41
2017-09-22 19:00 | 54.48 | 52.82
2017-09-22 19:30 | 52.41 | 50.63
2017-09-22 20:00 | 49.93 | 48.12
2017-09-22 20:30 | 47.55 | 45.74
2017-09-22 21:00 | 46.69 | 44.8
2017-09-22 21:30 | 44.74 | 42.71
2017-09-22 22:00 | 43.02 | 40.84
2017-09-22 22:30 | 42.28 | 39.98
2017-09-22 23:00 | 41.98 | 39.63
2017-09-22 23:30 | 39.64 | 37.09
2017-09-23 | 37.91 | 35.19
2017-09-23 00:30 | 36.61 | 34.03
2017-09-23 01:00 | 35.19 | 32.52
2017-09-23 01:30 | 34.28 | 31.49
2017-09-23 02:00 | 33.06 | 30.41
2017-09-23 02:30 | 32.65 | 30.03
2017-09-23 03:00 | 32.61 | 29.96
2017-09-23 03:30 | 32.09 | 29.37
2017-09-23 04:00 | 32.08 | 29.38
2017-09-23 04:30 | 32.33 | 29.66
2017-09-23 05:00 | 33.44 | 30.91
2017-09-23 05:30 | 33.95 | 31.52
2017-09-23 06:00 | 34.73 | 32.37
2017-09-23 06:30 | 35.72 | 33.46
2017-09-23 07:00 | 36.81 | 34.67
2017-09-23 07:30 | 37.88 | 35.87
2017-09-23 08:00 | 38.92 | 37.03
2017-09-23 08:30 | 42.09 | 40.46
2017-09-23 09:00 | 44.65 | 43.04
2017-09-23 09:30 | 45.04 | 43.41
2017-09-23 10:00 | 44.54 | 42.92
2017-09-23 10:30 | 44.23 | 42.64
2017-09-23 11:00 | 43.75 | 42.17
2017-09-23 11:30 | 42.25 | 40.6
2017-09-23 12:00 | 41.55 | 39.86
2017-09-23 12:30 | 41.45 | 39.72
2017-09-23 13:00 | 40.7 | 38.91
2017-09-23 13:30 | 40.19 | 38.35
2017-09-23 14:00 | 39.94 | 38.08
2017-09-23 14:30 | 40.59 | 38.74
2017-09-23 15:00 | 40.35 | 38.46
2017-09-23 15:30 | 40.5 | 38.59
2017-09-23 16:00 | 41.98 | 40.12
2017-09-23 16:30 | 43.46 | 41.63
2017-09-23 17:00 | 43.9 | 42.06
2017-09-23 17:30 | 45.06 | 43.27
2017-09-23 18:00 | 46.66 | 44.93
2017-09-23 18:30 | 49.06 | 47.47
2017-09-23 19:00 | 49.44 | 47.88
2017-09-23 19:30 | 47.99 | 46.36
2017-09-23 20:00 | 46.36 | 44.65
2017-09-23 20:30 | 44.23 | 42.39
2017-09-23 21:00 | 43.31 | 41.41
2017-09-23 21:30 | 41.52 | 39.47
2017-09-23 22:00 | 40.8 | 38.67
2017-09-23 22:30 | 39.79 | 37.54
2017-09-23 23:00 | 39.92 | 37.66
2017-09-23 23:30 | 36.77 | 34.4
2017-09-24 | 34.55 | 32.13
2017-09-24 00:30 | 33.7 | 31.18
2017-09-24 01:00 | 33.22 | 30.64
2017-09-24 01:30 | 32.76 | 30.13
2017-09-24 02:00 | 31.7 | 28.97
2017-09-24 02:30 | 32.46 | 29.76
2017-09-24 03:00 | 31.57 | 28.77
2017-09-24 03:30 | 31.25 | 28.41
2017-09-24 04:00 | 31.01 | 28.14
2017-09-24 04:30 | 31.2 | 28.35
2017-09-24 05:00 | 31.31 | 28.48
2017-09-24 05:30 | 32.14 | 29.41
2017-09-24 06:00 | 32.01 | 29.22
2017-09-24 06:30 | 32.43 | 29.67
2017-09-24 07:00 | 32.79 | 30.09
2017-09-24 07:30 | 33 | 30.39
2017-09-24 08:00 | 34.25 | 31.8
2017-09-24 08:30 | 35.5 | 33.2
2017-09-24 09:00 | 36.98 | 34.88
2017-09-24 09:30 | 37.39 | 35.38
2017-09-24 10:00 | 37.65 | 35.63
2017-09-24 10:30 | 38.55 | 36.4
2017-09-24 11:00 | 38.42 | 36.3
2017-09-24 11:30 | 37.74 | 35.59
2017-09-24 12:00 | 37.59 | 35.44
2017-09-24 12:30 | 37.79 | 35.65
2017-09-24 13:00 | 37.18 | 34.99
2017-09-24 13:30 | 36.99 | 34.79
2017-09-24 14:00 | 37.42 | 35.24
2017-09-24 14:30 | 37.58 | 35.39
2017-09-24 15:00 | 38.5 | 36.38
2017-09-24 15:30 | 39.32 | 37.22
2017-09-24 16:00 | 40.07 | 37.99
2017-09-24 16:30 | 41.65 | 39.64
2017-09-24 17:00 | 42.41 | 40.43
2017-09-24 17:30 | 44.11 | 42.21
2017-09-24 18:00 | 46.57 | 44.79
2017-09-24 18:30 | 47.86 | 46.14
2017-09-24 19:00 | 50.14 | 48.56
2017-09-24 19:30 | 48.79 | 47.15
2017-09-24 20:00 | 47.2 | 45.45
2017-09-24 20:30 | 44.62 | 42.72
2017-09-24 21:00 | 43.55 | 41.57
2017-09-24 21:30 | 41.95 | 39.84
2017-09-24 22:00 | 40.02 | 37.75
2017-09-24 22:30 | 38.43 | 36.02
2017-09-24 23:00 | 38.66 | 36.24
2017-09-24 23:30 | 35.8 | 33.48
2017-09-25 | 34.25 | 31.77
2017-09-25 00:30 | 33.87 | 31.33
2017-09-25 01:00 | 33.17 | 30.56
2017-09-25 01:30 | 32.59 | 29.9
2017-09-25 02:00 | 32.13 | 29.41
2017-09-25 02:30 | 32.01 | 29.27
2017-09-25 03:00 | 32.08 | 29.33
2017-09-25 03:30 | 31.87 | 29.1
2017-09-25 04:00 | 32.1 | 29.35
2017-09-25 04:30 | 32.84 | 30.17
2017-09-25 05:00 | 33.92 | 31.38
2017-09-25 05:30 | 36.55 | 34.34
2017-09-25 06:00 | 38.47 | 36.43
2017-09-25 06:30 | 41.66 | 39.89
2017-09-25 07:00 | 44.97 | 43.46
2017-09-25 07:30 | 48.41 | 47
2017-09-25 08:00 | 51.17 | 49.8
2017-09-25 08:30 | 53.4 | 52.14
2017-09-25 09:00 | 55.57 | 54.35
2017-09-25 09:30 | 55.44 | 54.03
2017-09-25 10:00 | 55.56 | 53.4
2017-09-25 10:30 | 55.9 | 53.81
2017-09-25 11:00 | 55.71 | 53.67
2017-09-25 11:30 | 56.32 | 54.33
2017-09-25 12:00 | 55.98 | 54.01
2017-09-25 12:30 | 57.09 | 55.14
2017-09-25 13:00 | 56.52 | 54.55
2017-09-25 13:30 | 55.92 | 53.94
2017-09-25 14:00 | 56.61 | 54.65
2017-09-25 14:30 | 56.9 | 54.93
2017-09-25 15:00 | 56.52 | 54.51
2017-09-25 15:30 | 56.64 | 54.58
2017-09-25 16:00 | 56.31 | 54.16
2017-09-25 16:30 | 58.07 | 55.89
2017-09-25 17:00 | 57.22 | 54.9
2017-09-25 17:30 | 57.1 | 54.61
2017-09-25 18:00 | 63.87 | 53.02
2017-09-25 18:30 | 67.52 | 54.46
2017-09-25 19:00 | 67.97 | 55.05
2017-09-25 19:30 | 66.6 | 53.18
2017-09-25 20:00 | 64.5 | 50.18
2017-09-25 20:30 | 62.77 | 47.71
2017-09-25 21:00 | 61.33 | 45.6
2017-09-25 21:30 | 59.84 | 43.33
2017-09-25 22:00 | 58.15 | 40.76
2017-09-25 22:30 | 56.47 | 38.35
2017-09-25 23:00 | 56.08 | 38.37
2017-09-25 23:30 | 52.38 | 35.98
2017-09-26 | 48.94 | 33.08
2017-09-26 00:30 | 48.74 | 32.61
2017-09-26 01:00 | 37.07 | 30.85
2017-09-26 01:30 | 33.31 | 30.85
2017-09-26 02:00 | 32.54 | 29.99
2017-09-26 02:30 | 32.41 | 29.81
2017-09-26 03:00 | 32.19 | 29.56
2017-09-26 03:30 | 31.84 | 29.16
2017-09-26 04:00 | 32.57 | 29.95
2017-09-26 04:30 | 32.77 | 30.17
2017-09-26 05:00 | 33.3 | 30.77
2017-09-26 05:30 | 36.25 | 34.05
2017-09-26 06:00 | 37.45 | 35.36
2017-09-26 06:30 | 40.82 | 39.01
2017-09-26 07:00 | 43.86 | 42.3
2017-09-26 07:30 | 47.63 | 46.16
2017-09-26 08:00 | 49.24 | 47.87
2017-09-26 08:30 | 52.65 | 51.35
2017-09-26 09:00 | 53.41 | 52.09
2017-09-26 09:30 | 53.63 | 52.29
2017-09-26 10:00 | 53.27 | 51.82
2017-09-26 10:30 | 54.52 | 52.35
2017-09-26 11:00 | 55.11 | 53.02
2017-09-26 11:30 | 55.96 | 53.96
2017-09-26 12:00 | 55.76 | 53.79
2017-09-26 12:30 | 55.93 | 53.97
2017-09-26 13:00 | 55.97 | 54.02
2017-09-26 13:30 | 57.18 | 55.3
2017-09-26 14:00 | 57.97 | 56.12
2017-09-26 14:30 | 58.32 | 56.48
2017-09-26 15:00 | 59.41 | 57.61
2017-09-26 15:30 | 59.97 | 58.15
2017-09-26 16:00 | 60.33 | 58.46
2017-09-26 16:30 | 58.68 | 56.6
2017-09-26 17:00 | 59.45 | 57.31
2017-09-26 17:30 | 56.87 | 54.61
2017-09-26 18:00 | 56.23 | 53.93
2017-09-26 18:30 | 57.15 | 54.84
2017-09-26 19:00 | 58.46 | 56.22
2017-09-26 19:30 | 56.63 | 54.27
2017-09-26 20:00 | 54.41 | 51.88
2017-09-26 20:30 | 51.5 | 48.95
2017-09-26 21:00 | 49.5 | 46.88
2017-09-26 21:30 | 47.28 | 44.45
2017-09-26 22:00 | 46.09 | 42.28
2017-09-26 22:30 | 55.87 | 39.45
2017-09-26 23:00 | 56.03 | 39.51
2017-09-26 23:30 | 53.83 | 36.17
2017-09-27 | 52.85 | 34.44
2017-09-27 00:30 | 52.03 | 33.72
2017-09-27 01:00 | 50.52 | 31.77
2017-09-27 01:30 | 49.98 | 30.78
2017-09-27 02:00 | 50.06 | 30.76
2017-09-27 02:30 | 49.83 | 30.32
2017-09-27 03:00 | 50.19 | 30.89
2017-09-27 03:30 | 50.03 | 30.54
2017-09-27 04:00 | 49.89 | 30.37
2017-09-27 04:30 | 50 | 30.66
2017-09-27 05:00 | 50.67 | 31.75
2017-09-27 05:30 | 52.25 | 34.63
2017-09-27 06:00 | 53.12 | 36.12
2017-09-27 06:30 | 55.31 | 39.77
2017-09-27 07:00 | 57.94 | 43.7
2017-09-27 07:30 | 60.63 | 47.2
2017-09-27 08:00 | 63.32 | 50.58
2017-09-27 08:30 | 65.33 | 52.78
2017-09-27 09:00 | 66.74 | 54.76
2017-09-27 09:30 | 66.77 | 54.91
2017-09-27 10:00 | 67.32 | 55.67
2017-09-27 10:30 | 67.43 | 56.09
2017-09-27 11:00 | 67.97 | 56.91
2017-09-27 11:30 | 67.77 | 56.75
2017-09-27 12:00 | 67.71 | 56.69
2017-09-27 12:30 | 68.96 | 58.29
2017-09-27 13:00 | 69.27 | 58.64
2017-09-27 13:30 | 69.12 | 58.44
2017-09-27 14:00 | 70 | 59.56
2017-09-27 14:30 | 70.64 | 60.3
2017-09-27 15:00 | 70.95 | 60.64
2017-09-27 15:30 | 70.99 | 60.57
2017-09-27 16:00 | 71.2 | 60.63
2017-09-27 16:30 | 71.38 | 60.56
2017-09-27 17:00 | 70.5 | 59.28
2017-09-27 17:30 | 69.76 | 58
2017-09-27 18:00 | 69.14 | 57
2017-09-27 18:30 | 70.48 | 58.76
2017-09-27 19:00 | 71.1 | 59.47
2017-09-27 19:30 | 68.56 | 56.12
2017-09-27 20:00 | 66.35 | 53.12
2017-09-27 20:30 | 64.81 | 50.92
2017-09-27 21:00 | 63.1 | 48.5
2017-09-27 21:30 | 61.74 | 46.51
2017-09-27 22:00 | 59.05 | 44.23
2017-09-27 22:30 | 58.16 | 43.02
2017-09-27 23:00 | 57.88 | 42.55
2017-09-27 23:30 | 55.74 | 39.35
2017-09-28 | 52.12 | 36.84
2017-09-28 00:30 | 50.54 | 35.78
2017-09-28 01:00 | 49.69 | 34.36
2017-09-28 01:30 | 49.34 | 33.75
2017-09-28 02:00 | 49.05 | 33.24
2017-09-28 02:30 | 48.33 | 33
2017-09-28 03:00 | 48.2 | 32.92
2017-09-28 03:30 | 48.02 | 32.61
2017-09-28 04:00 | 48.06 | 32.55
2017-09-28 04:30 | 48.18 | 32.86
2017-09-28 05:00 | 49.35 | 34.62
2017-09-28 05:30 | 44.34 | 36.57
2017-09-28 06:00 | 40.41 | 38.63
2017-09-28 06:30 | 44.42 | 42.91
2017-09-28 07:00 | 48.42 | 47.01
2017-09-28 07:30 | 52.6 | 51.26
2017-09-28 08:00 | 55.14 | 53.77
2017-09-28 08:30 | 58.8 | 57.63
2017-09-28 09:00 | 59.41 | 58.31
2017-09-28 09:30 | 59.53 | 58.44
2017-09-28 10:00 | 60.26 | 59.14
2017-09-28 10:30 | 60.09 | 58.83
2017-09-28 11:00 | 60.62 | 59.19
2017-09-28 11:30 | 61.37 | 59.84
2017-09-28 12:00 | 61.29 | 59.68
2017-09-28 12:30 | 62.57 | 61.06
2017-09-28 13:00 | 63.01 | 61.49
2017-09-28 13:30 | 63.4 | 61.78
2017-09-28 14:00 | 63.35 | 61.73
2017-09-28 14:30 | 63.68 | 62.24
2017-09-28 15:00 | 63.23 | 61.85
2017-09-28 15:30 | 62.37 | 61.22
2017-09-28 16:00 | 61.58 | 60.71
2017-09-28 16:30 | 61.67 | 61.06
2017-09-28 17:00 | 60.07 | 59.75
2017-09-28 17:30 | 57.05 | 56.95
2017-09-28 18:00 | 57.54 | 57.49
2017-09-28 18:30 | 59.01 | 58.96
2017-09-28 19:00 | 59.12 | 59.08
2017-09-28 19:30 | 57.58 | 57.54
2017-09-28 20:00 | 54.22 | 54.2
2017-09-28 20:30 | 52.03 | 52.01
2017-09-28 21:00 | 49.88 | 49.85
2017-09-28 21:30 | 46.96 | 46.76
2017-09-28 22:00 | 44.76 | 44.57
2017-09-28 22:30 | 42.9 | 42.77
2017-09-28 23:00 | 42.57 | 42.46
2017-09-28 23:30 | 37.72 | 37.65
2017-09-29 | 37.25 | 37.18
2017-09-29 00:30 | 38.35 | 38.23
2017-09-29 01:00 | 33.39 | 33.07
2017-09-29 01:30 | 32.61 | 32.31
2017-09-29 02:00 | 32.37 | 32.09
2017-09-29 02:30 | 32.82 | 32.6
2017-09-29 03:00 | 32.08 | 31.85
2017-09-29 03:30 | 31.37 | 31.17
2017-09-29 04:00 | 31.38 | 31.19
2017-09-29 04:30 | 32.17 | 31.96
2017-09-29 05:00 | 32.63 | 32.4
2017-09-29 05:30 | 35.37 | 35.02
2017-09-29 06:00 | 37.85 | 37.37
2017-09-29 06:30 | 42.84 | 42.06
2017-09-29 07:00 | 46.09 | 45.62
2017-09-29 07:30 | 49.41 | 48.49
2017-09-29 08:00 | 52.6 | 51.8
2017-09-29 08:30 | 55.55 | 54.74
2017-09-29 09:00 | 56.84 | 56.3
2017-09-29 09:30 | 57.24 | 56.62
2017-09-29 10:00 | 57.1 | 56.34
2017-09-29 10:30 | 57 | 55.96
2017-09-29 11:00 | 57.42 | 56.28
2017-09-29 11:30 | 58.7 | 57.41
2017-09-29 12:00 | 58.55 | 57.32
2017-09-29 12:30 | 58.62 | 57.91
2017-09-29 13:00 | 59.09 | 58.82
2017-09-29 13:30 | 59.12 | 58.81
2017-09-29 14:00 | 59.13 | 58.79
2017-09-29 14:30 | 58.45 | 58.04
2017-09-29 15:00 | 59.33 | 58.85
2017-09-29 15:30 | 58.9 | 58.27
2017-09-29 16:00 | 59.18 | 58.41
2017-09-29 16:30 | 61.06 | 60.17
2017-09-29 17:00 | 61.53 | 59.9
2017-09-29 17:30 | 64.26 | 57.97
2017-09-29 18:00 | 64.17 | 57.68
2017-09-29 18:30 | 64.9 | 58.54
2017-09-29 19:00 | 63.21 | 56.57
2017-09-29 19:30 | 62.7 | 55.89
2017-09-29 20:00 | 59.65 | 52.29
2017-09-29 20:30 | 58.06 | 50.32
2017-09-29 21:00 | 56.29 | 48.17
2017-09-29 21:30 | 54.6 | 45.99
2017-09-29 22:00 | 51.87 | 43.1
2017-09-29 22:30 | 50.74 | 42.13
2017-09-29 23:00 | 49.7 | 40.93
2017-09-29 23:30 | 45.82 | 37.75
2017-09-30 | 43.65 | 35.97
2017-09-30 00:30 | 42.92 | 34.98
2017-09-30 01:00 | 41.64 | 33.36
2017-09-30 01:30 | 41.6 | 33.24
2017-09-30 02:00 | 41.34 | 32.84
2017-09-30 02:30 | 41.04 | 32.43
2017-09-30 03:00 | 40.77 | 32.16
2017-09-30 03:30 | 39.29 | 30.9
2017-09-30 04:00 | 39.08 | 30.58
2017-09-30 04:30 | 39.72 | 31.43
2017-09-30 05:00 | 40.39 | 32.31
2017-09-30 05:30 | 40.95 | 33.15
2017-09-30 06:00 | 40.87 | 33
2017-09-30 06:30 | 41.53 | 33.89
2017-09-30 07:00 | 42.68 | 35.41
2017-09-30 07:30 | 43.38 | 36.47
2017-09-30 08:00 | 44.14 | 37.57
2017-09-30 08:30 | 41.32 | 40.21
2017-09-30 09:00 | 44.05 | 43.55
2017-09-30 09:30 | 45.03 | 44.43
2017-09-30 10:00 | 44.18 | 43.51
2017-09-30 10:30 | 44.2 | 43.38
2017-09-30 11:00 | 43.96 | 43.06
2017-09-30 11:30 | 43.99 | 43.04
2017-09-30 12:00 | 43.88 | 42.96
2017-09-30 12:30 | 43.1 | 42.29
2017-09-30 13:00 | 43.05 | 42.29
2017-09-30 13:30 | 43.19 | 42.51
2017-09-30 14:00 | 41.81 | 41.16
2017-09-30 14:30 | 43.27 | 42.72
2017-09-30 15:00 | 43.75 | 43.23
2017-09-30 15:30 | 43.38 | 42.92
2017-09-30 16:00 | 45.26 | 44.85
2017-09-30 16:30 | 45.27 | 45.01
2017-09-30 17:00 | 44.76 | 44.56
2017-09-30 17:30 | 46.6 | 46.41
2017-09-30 18:00 | 47.64 | 47.45
2017-09-30 18:30 | 49.53 | 49.28
2017-09-30 19:00 | 50.89 | 50.6
2017-09-30 19:30 | 49.71 | 49.43
2017-09-30 20:00 | 47.6 | 47.34
2017-09-30 20:30 | 45.63 | 45.42
2017-09-30 21:00 | 44.23 | 44.05
2017-09-30 21:30 | 42.73 | 42.61
2017-09-30 22:00 | 41.75 | 41.67
2017-09-30 22:30 | 40.26 | 40.18
2017-09-30 23:00 | 39.6 | 39.53
2017-09-30 23:30 | 37.5 | 37.45
2017-10-01 | 35.01 | 34.97
2017-10-01 00:30 | 34.35 | 34.32
2017-10-01 01:00 | 33.19 | 33.16
2017-10-01 01:30 | 32.57 | 32.53
2017-10-01 02:00 | 32.29 | 32.26
2017-10-01 02:30 | 32.74 | 32.61
2017-10-01 03:00 | 31.46 | 31.27
2017-10-01 03:30 | 31.24 | 31.06
2017-10-01 04:00 | 31.65 | 31.5
2017-10-01 04:30 | 31.75 | 31.59
2017-10-01 05:00 | 31.27 | 31.1
2017-10-01 05:30 | 31.95 | 31.77
2017-10-01 06:00 | 31.35 | 31.2
2017-10-01 06:30 | 31.61 | 31.5
2017-10-01 07:00 | 32.41 | 32.27
2017-10-01 07:30 | 33.61 | 33.37
2017-10-01 08:00 | 37.21 | 36.89
2017-10-01 08:30 | 39.13 | 38.73
2017-10-01 09:00 | 40.41 | 39.88
2017-10-01 09:30 | 41.56 | 41.06
2017-10-01 10:00 | 39.51 | 39.33
2017-10-01 10:30 | 42.07 | 41.83
2017-10-01 11:00 | 41.44 | 41.18
2017-10-01 11:30 | 42.18 | 41.84
2017-10-01 12:00 | 43.46 | 43.14
2017-10-01 12:30 | 42.09 | 41.83
2017-10-01 13:00 | 42.42 | 42.17
2017-10-01 13:30 | 40.79 | 40.54
2017-10-01 14:00 | 43.22 | 42.98
2017-10-01 14:30 | 42.59 | 42.4
2017-10-01 15:00 | 43.04 | 42.87
2017-10-01 15:30 | 42.69 | 42.58
2017-10-01 16:00 | 42.58 | 42.5
2017-10-01 16:30 | 43.38 | 43.3
2017-10-01 17:00 | 43.89 | 43.82
2017-10-01 17:30 | 44.83 | 44.76
2017-10-01 18:00 | 44.94 | 44.87
2017-10-01 18:30 | 46.5 | 46.39
2017-10-01 19:00 | 45.87 | 45.76
2017-10-01 19:30 | 43.1 | 43.01
2017-10-01 20:00 | 42.94 | 42.86
2017-10-01 20:30 | 40.83 | 40.76
2017-10-01 21:00 | 39.5 | 39.43
2017-10-01 21:30 | 39.77 | 39.71
2017-10-01 22:00 | 38.32 | 38.27
2017-10-01 22:30 | 37.28 | 37.09
2017-10-01 23:00 | 38.01 | 37.66
2017-10-01 23:30 | 35.02 | 34.71
2017-10-02 | 34.1 | 33.82
2017-10-02 00:30 | 32.89 | 32.65
2017-10-02 01:00 | 31.78 | 31.57
2017-10-02 01:30 | 31.18 | 30.99
2017-10-02 02:00 | 31.78 | 31.6
2017-10-02 02:30 | 30.95 | 30.79
2017-10-02 03:00 | 30.14 | 29.97
2017-10-02 03:30 | 29.89 | 29.72
2017-10-02 04:00 | 30.03 | 29.87
2017-10-02 04:30 | 31.27 | 31.12
2017-10-02 05:00 | 31.37 | 31.2
2017-10-02 05:30 | 32.46 | 32.25
2017-10-02 06:00 | 32.85 | 32.64
2017-10-02 06:30 | 34.33 | 34.09
2017-10-02 07:00 | 34.92 | 34.62
2017-10-02 07:30 | 38.01 | 37.59
2017-10-02 08:00 | 39.54 | 39.02
2017-10-02 08:30 | 41.64 | 41.2
2017-10-02 09:00 | 43.62 | 43.46
2017-10-02 09:30 | 42.93 | 42.78
2017-10-02 10:00 | 42.47 | 42.29
2017-10-02 10:30 | 43.43 | 43.18
2017-10-02 11:00 | 42.85 | 42.57
2017-10-02 11:30 | 41.33 | 40.99
2017-10-02 12:00 | 43.13 | 42.83
2017-10-02 12:30 | 44.62 | 44.36
2017-10-02 13:00 | 42.03 | 41.77
2017-10-02 13:30 | 41.27 | 40.98
2017-10-02 14:00 | 42.45 | 42.16
2017-10-02 14:30 | 42.16 | 41.88
2017-10-02 15:00 | 40.48 | 40.18
2017-10-02 15:30 | 41.91 | 41.66
2017-10-02 16:00 | 42.17 | 41.98
2017-10-02 16:30 | 44.18 | 44.02
2017-10-02 17:00 | 44.12 | 43.97
2017-10-02 17:30 | 46.36 | 46.24
2017-10-02 18:00 | 47.32 | 47.21
2017-10-02 18:30 | 51.06 | 50.9
2017-10-02 19:00 | 51.56 | 51.39
2017-10-02 19:30 | 48.75 | 48.61
2017-10-02 20:00 | 46.57 | 46.46
2017-10-02 20:30 | 44.68 | 44.6
2017-10-02 21:00 | 42.96 | 42.89
2017-10-02 21:30 | 40.86 | 40.81
2017-10-02 22:00 | 38.94 | 38.89
2017-10-02 22:30 | 37.6 | 37.56
2017-10-02 23:00 | 38.04 | 38.01
2017-10-02 23:30 | 34.83 | 34.8
2017-10-03 | 34.72 | 34.69
2017-10-03 00:30 | 33.66 | 33.63
2017-10-03 01:00 | 31 | 30.97
2017-10-03 01:30 | 31.82 | 31.79
2017-10-03 02:00 | 30.71 | 30.68
2017-10-03 02:30 | 30.75 | 30.71
2017-10-03 03:00 | 30.7 | 30.66
2017-10-03 03:30 | 31.07 | 30.91
2017-10-03 04:00 | 30.91 | 30.76
2017-10-03 04:30 | 31.16 | 30.97
2017-10-03 05:00 | 32.62 | 32.41
2017-10-03 05:30 | 35.5 | 35.12
2017-10-03 06:00 | 38.74 | 38.19
2017-10-03 06:30 | 44.33 | 43.36
2017-10-03 07:00 | 49.17 | 47.69
2017-10-03 07:30 | 55.3 | 54.58
2017-10-03 08:00 | 58.68 | 57.95
2017-10-03 08:30 | 60.86 | 59.67
2017-10-03 09:00 | 63.45 | 62.08
2017-10-03 09:30 | 62.77 | 61.28
2017-10-03 10:00 | 61.68 | 60.41
2017-10-03 10:30 | 61.93 | 61.06
2017-10-03 11:00 | 62.38 | 61.38
2017-10-03 11:30 | 63.05 | 61.96
2017-10-03 12:00 | 64.14 | 62.84
2017-10-03 12:30 | 64.16 | 62.9
2017-10-03 13:00 | 63.32 | 62.01
2017-10-03 13:30 | 63.6 | 62.23
2017-10-03 14:00 | 62.7 | 61.28
2017-10-03 14:30 | 63.16 | 61.68
2017-10-03 15:00 | 63.85 | 62.51
2017-10-03 15:30 | 62.13 | 60.97
2017-10-03 16:00 | 62.17 | 61.27
2017-10-03 16:30 | 61.69 | 61.12
2017-10-03 17:00 | 59.69 | 59.37
2017-10-03 17:30 | 57.22 | 57.12
2017-10-03 18:00 | 55.82 | 55.79
2017-10-03 18:30 | 57.64 | 57.61
2017-10-03 19:00 | 57.97 | 57.94
2017-10-03 19:30 | 56 | 55.98
2017-10-03 20:00 | 52.91 | 52.89
2017-10-03 20:30 | 49.95 | 49.9
2017-10-03 21:00 | 48.22 | 48.13
2017-10-03 21:30 | 46.01 | 45.85
2017-10-03 22:00 | 44.84 | 44.58
2017-10-03 22:30 | 42.66 | 42.31
2017-10-03 23:00 | 41.81 | 41.39
2017-10-03 23:30 | 39.06 | 38.52
2017-10-04 | 36.34 | 35.84
2017-10-04 00:30 | 34.82 | 34.65
2017-10-04 01:00 | 33.91 | 33.71
2017-10-04 01:30 | 33.44 | 33.22
2017-10-04 02:00 | 33.27 | 33.02
2017-10-04 02:30 | 32.93 | 32.64
2017-10-04 03:00 | 32.92 | 32.84
2017-10-04 03:30 | 32.28 | 32.22
2017-10-04 04:00 | 31.77 | 31.53
2017-10-04 04:30 | 32.21 | 31.99
2017-10-04 05:00 | 32.8 | 32.5
2017-10-04 05:30 | 35.64 | 35.19
2017-10-04 06:00 | 38.29 | 37.72
2017-10-04 06:30 | 43.58 | 42.57
2017-10-04 07:00 | 49.02 | 47.72
2017-10-04 07:30 | 55.72 | 54.65
2017-10-04 08:00 | 64.03 | 58.03
2017-10-04 08:30 | 64.66 | 59
2017-10-04 09:00 | 66.18 | 60.94
2017-10-04 09:30 | 66.19 | 61.01
2017-10-04 10:00 | 65.09 | 59.82
2017-10-04 10:30 | 66.13 | 61.06
2017-10-04 11:00 | 67.19 | 62.26
2017-10-04 11:30 | 67.45 | 62.59
2017-10-04 12:00 | 67.69 | 62.91
2017-10-04 12:30 | 67.52 | 63
2017-10-04 13:00 | 66.5 | 65.13
2017-10-04 13:30 | 70.33 | 69.09
2017-10-04 14:00 | 71.01 | 69.79
2017-10-04 14:30 | 71.51 | 70.3
2017-10-04 15:00 | 71.32 | 70.08
2017-10-04 15:30 | 70.53 | 69.22
2017-10-04 16:00 | 71.25 | 69.91
2017-10-04 16:30 | 71.43 | 70.02
2017-10-04 17:00 | 69.84 | 68.3
2017-10-04 17:30 | 68.6 | 66.89
2017-10-04 18:00 | 68.97 | 67.18
2017-10-04 18:30 | 70.29 | 69.11
2017-10-04 19:00 | 72.22 | 71.14
2017-10-04 19:30 | 70.03 | 68.92
2017-10-04 20:00 | 67.88 | 66.75
2017-10-04 20:30 | 64.53 | 63.41
2017-10-04 21:00 | 62.3 | 61.14
2017-10-04 21:30 | 58.56 | 58.32
2017-10-04 22:00 | 56.6 | 54.89
2017-10-04 22:30 | 54.55 | 52.73
2017-10-04 23:00 | 53.86 | 52.1
2017-10-04 23:30 | 50.38 | 48.57
2017-10-05 | 48.26 | 46.31
2017-10-05 00:30 | 47.3 | 45.28
2017-10-05 01:00 | 45.67 | 43.53
2017-10-05 01:30 | 44.73 | 42.51
2017-10-05 02:00 | 44.11 | 41.85
2017-10-05 02:30 | 43.48 | 41.14
2017-10-05 03:00 | 42.71 | 40.29
2017-10-05 03:30 | 54.86 | 39.74
2017-10-05 04:00 | 54.61 | 39.41
2017-10-05 04:30 | 54.33 | 40.3
2017-10-05 05:00 | 54.9 | 41.59
2017-10-05 05:30 | 56.69 | 44.28
2017-10-05 06:00 | 58.31 | 46.54
2017-10-05 06:30 | 59.01 | 52.29
2017-10-05 07:00 | 59 | 57.46
2017-10-05 07:30 | 64.34 | 63.18
2017-10-05 08:00 | 66.52 | 65.2
2017-10-05 08:30 | 68.79 | 67.43
2017-10-05 09:00 | 70.37 | 68.9
2017-10-05 09:30 | 70.22 | 68.58
2017-10-05 10:00 | 70.72 | 68.93
2017-10-05 10:30 | 71.51 | 69.49
2017-10-05 11:00 | 71.76 | 69.55
2017-10-05 11:30 | 72.06 | 69.79
2017-10-05 12:00 | 72.8 | 70.4
2017-10-05 12:30 | 73.99 | 71.6
2017-10-05 13:00 | 73.81 | 71.39
2017-10-05 13:30 | 73.26 | 72.32
2017-10-05 14:00 | 74 | 73.07
2017-10-05 14:30 | 74.34 | 73.42
2017-10-05 15:00 | 73.41 | 72.51
2017-10-05 15:30 | 73.75 | 72.87
2017-10-05 16:00 | 74.15 | 73.32
2017-10-05 16:30 | 73.68 | 72.92
2017-10-05 17:00 | 72.03 | 70.89
2017-10-05 17:30 | 70.59 | 68.94
2017-10-05 18:00 | 71.06 | 69.34
2017-10-05 18:30 | 73.46 | 71.82
2017-10-05 19:00 | 74.77 | 73.18
2017-10-05 19:30 | 72.88 | 71.22
2017-10-05 20:00 | 69.71 | 67.9
2017-10-05 20:30 | 67.37 | 65.43
2017-10-05 21:00 | 65.61 | 63.58
2017-10-05 21:30 | 63.43 | 61.29
2017-10-05 22:00 | 60.35 | 58.01
2017-10-05 22:30 | 62.02 | 54.95
2017-10-05 23:00 | 65.74 | 54.09
2017-10-05 23:30 | 61.9 | 50.22
2017-10-06 | 60.19 | 47.94
2017-10-06 00:30 | 59.13 | 46.46
2017-10-06 01:00 | 57.19 | 44.63
2017-10-06 01:30 | 56.63 | 43.91
2017-10-06 02:00 | 56.14 | 43.22
2017-10-06 02:30 | 55.67 | 42.47
2017-10-06 03:00 | 55.21 | 41.85
2017-10-06 03:30 | 55.31 | 41.93
2017-10-06 04:00 | 49.56 | 42.76
2017-10-06 04:30 | 45.65 | 43.97
2017-10-06 05:00 | 46.86 | 45.26
2017-10-06 05:30 | 49.19 | 47.73
2017-10-06 06:00 | 50.53 | 49.12
2017-10-06 06:30 | 55.47 | 54.28
2017-10-06 07:00 | 59.4 | 58.07
2017-10-06 07:30 | 64.77 | 63.53
2017-10-06 08:00 | 67.14 | 65.85
2017-10-06 08:30 | 68.31 | 66.95
2017-10-06 09:00 | 70.46 | 68.89
2017-10-06 09:30 | 71.44 | 69.69
2017-10-06 10:00 | 71.03 | 69.25
2017-10-06 10:30 | 72.21 | 70.28
2017-10-06 11:00 | 73.1 | 71
2017-10-06 11:30 | 73.28 | 72.06
2017-10-06 12:00 | 73.5 | 72.58
2017-10-06 12:30 | 72.37 | 71.46
2017-10-06 13:00 | 70.05 | 69.11
2017-10-06 13:30 | 69.9 | 68.97
2017-10-06 14:00 | 70.26 | 69.34
2017-10-06 14:30 | 70.17 | 69.27
2017-10-06 15:00 | 69.81 | 68.95
2017-10-06 15:30 | 67.8 | 66.62
2017-10-06 16:00 | 68.48 | 66.95
2017-10-06 16:30 | 69.34 | 67.76
2017-10-06 17:00 | 69.69 | 68.06
2017-10-06 17:30 | 69.31 | 67.57
2017-10-06 18:00 | 68.12 | 66.26
2017-10-06 18:30 | 69.01 | 67.18
2017-10-06 19:00 | 70.48 | 68.7
2017-10-06 19:30 | 68.3 | 66.43
2017-10-06 20:00 | 66.07 | 64.11
2017-10-06 20:30 | 64.35 | 62.28
2017-10-06 21:00 | 62.22 | 60.02
2017-10-06 21:30 | 60.92 | 58.65
2017-10-06 22:00 | 58.27 | 55.71
2017-10-06 22:30 | 57.99 | 52.85
2017-10-06 23:00 | 58.01 | 52.79
2017-10-06 23:30 | 55.24 | 49.61
2017-10-07 | 52.88 | 46.83
2017-10-07 00:30 | 51.88 | 45.57
2017-10-07 01:00 | 49.92 | 43.28
2017-10-07 01:30 | 49.27 | 42.47
2017-10-07 02:00 | 48.06 | 40.98
2017-10-07 02:30 | 47.11 | 40.38
2017-10-07 03:00 | 44.76 | 39.92
2017-10-07 03:30 | 43.51 | 39.34
2017-10-07 04:00 | 43.23 | 39.03
2017-10-07 04:30 | 43.54 | 39.35
2017-10-07 05:00 | 44.13 | 39.99
2017-10-07 05:30 | 44.64 | 40.56
2017-10-07 06:00 | 45.08 | 41.03
2017-10-07 06:30 | 47.05 | 43.13
2017-10-07 07:00 | 48.37 | 44.52
2017-10-07 07:30 | 48.39 | 45.98
2017-10-07 08:00 | 49.23 | 47.48
2017-10-07 08:30 | 51.92 | 50.67
2017-10-07 09:00 | 54.36 | 53.03
2017-10-07 09:30 | 54.62 | 53.16
2017-10-07 10:00 | 53.69 | 52.17
2017-10-07 10:30 | 54.81 | 53.15
2017-10-07 11:00 | 54.34 | 52.52
2017-10-07 11:30 | 53.97 | 52.11
2017-10-07 12:00 | 53.06 | 51.25
2017-10-07 12:30 | 51.84 | 50.29
2017-10-07 13:00 | 51.58 | 50.2
2017-10-07 13:30 | 51.22 | 49.89
2017-10-07 14:00 | 50.92 | 49.63
2017-10-07 14:30 | 51.45 | 50.24
2017-10-07 15:00 | 51.64 | 50.55
2017-10-07 15:30 | 52.18 | 51.24
2017-10-07 16:00 | 53.04 | 52.21
2017-10-07 16:30 | 53.21 | 52.56
2017-10-07 17:00 | 53.09 | 52.56
2017-10-07 17:30 | 55.46 | 54.98
2017-10-07 18:00 | 57.63 | 57.16
2017-10-07 18:30 | 60.94 | 60.25
2017-10-07 19:00 | 61.66 | 60.87
2017-10-07 19:30 | 60.9 | 60.08
2017-10-07 20:00 | 58.29 | 57.6
2017-10-07 20:30 | 55.08 | 54.49
2017-10-07 21:00 | 53.25 | 52.76
2017-10-07 21:30 | 52.11 | 51.69
2017-10-07 22:00 | 48.59 | 48.3
2017-10-07 22:30 | 47.05 | 46.8
2017-10-07 23:00 | 46.62 | 46.41
2017-10-07 23:30 | 44.19 | 44.01
2017-10-08 | 42.43 | 42.3
2017-10-08 00:30 | 39.79 | 39.71
2017-10-08 01:00 | 38.7 | 38.62
2017-10-08 01:30 | 38.45 | 38.38
2017-10-08 02:00 | 37.97 | 37.9
2017-10-08 02:30 | 37.42 | 37.35
2017-10-08 03:00 | 36.74 | 36.69
2017-10-08 03:30 | 36.68 | 36.62
2017-10-08 04:00 | 36.79 | 36.73
2017-10-08 04:30 | 36.73 | 36.67
2017-10-08 05:00 | 35.85 | 35.8
2017-10-08 05:30 | 36.01 | 35.97
2017-10-08 06:00 | 36.27 | 36.19
2017-10-08 06:30 | 36.62 | 36.38
2017-10-08 07:00 | 38.48 | 38.2
2017-10-08 07:30 | 38.71 | 38.32
2017-10-08 08:00 | 40.08 | 39.56
2017-10-08 08:30 | 42.67 | 41.93
2017-10-08 09:00 | 44.88 | 44.34
2017-10-08 09:30 | 44.91 | 44.51
2017-10-08 10:00 | 44.45 | 44.03
2017-10-08 10:30 | 43.39 | 42.89
2017-10-08 11:00 | 44 | 43.48
2017-10-08 11:30 | 43.72 | 43.13
2017-10-08 12:00 | 43.96 | 43.34
2017-10-08 12:30 | 44.82 | 44.28
2017-10-08 13:00 | 43.94 | 43.36
2017-10-08 13:30 | 45.26 | 44.7
2017-10-08 14:00 | 44.48 | 43.94
2017-10-08 14:30 | 44.76 | 44.31
2017-10-08 15:00 | 45.74 | 45.33
2017-10-08 15:30 | 46.3 | 45.93
2017-10-08 16:00 | 47.03 | 46.7
2017-10-08 16:30 | 50.17 | 49.87
2017-10-08 17:00 | 49.55 | 49.3
2017-10-08 17:30 | 50.76 | 50.55
2017-10-08 18:00 | 53.31 | 53.08
2017-10-08 18:30 | 57.54 | 57.18
2017-10-08 19:00 | 60.72 | 60.22
2017-10-08 19:30 | 60.06 | 59.54
2017-10-08 20:00 | 58.04 | 57.56
2017-10-08 20:30 | 54.39 | 53.98
2017-10-08 21:00 | 52.32 | 51.99
2017-10-08 21:30 | 49.98 | 49.72
2017-10-08 22:00 | 47.7 | 47.51
2017-10-08 22:30 | 45.29 | 45.15
2017-10-08 23:00 | 44.73 | 44.63
2017-10-08 23:30 | 41.29 | 41.2
2017-10-09 | 39.64 | 39.56
2017-10-09 00:30 | 39.44 | 39.36
2017-10-09 01:00 | 37.12 | 37.06
2017-10-09 01:30 | 36.77 | 36.69
2017-10-09 02:00 | 36.07 | 35.7
2017-10-09 02:30 | 36.28 | 35.88
2017-10-09 03:00 | 36.01 | 35.64
2017-10-09 03:30 | 36.74 | 36.4
2017-10-09 04:00 | 37.51 | 37.16
2017-10-09 04:30 | 37.97 | 37.57
2017-10-09 05:00 | 39.42 | 38.95
2017-10-09 05:30 | 42.13 | 41.54
2017-10-09 06:00 | 44.18 | 43.48
2017-10-09 06:30 | 50.73 | 49.52
2017-10-09 07:00 | 55.8 | 54.14
2017-10-09 07:30 | 59.14 | 58.3
2017-10-09 08:00 | 61.22 | 60.75
2017-10-09 08:30 | 62.58 | 62.43
2017-10-09 09:00 | 63.19 | 62.97
2017-10-09 09:30 | 63.41 | 63.24
2017-10-09 10:00 | 62.51 | 62.37
2017-10-09 10:30 | 63.04 | 62.95
2017-10-09 11:00 | 62.85 | 62.81
2017-10-09 11:30 | 63.64 | 63.62
2017-10-09 12:00 | 64.65 | 64.63
2017-10-09 12:30 | 66.79 | 66.78
2017-10-09 13:00 | 65.93 | 65.91
2017-10-09 13:30 | 66.3 | 66.28
2017-10-09 14:00 | 66.61 | 66.6
2017-10-09 14:30 | 67.17 | 67.16
2017-10-09 15:00 | 67.35 | 67.34
2017-10-09 15:30 | 67.04 | 66.98
2017-10-09 16:00 | 68.39 | 68.27
2017-10-09 16:30 | 68.31 | 68.07
2017-10-09 17:00 | 67.69 | 67.22
2017-10-09 17:30 | 67.21 | 66.37
2017-10-09 18:00 | 70.08 | 66.23
2017-10-09 18:30 | 72.77 | 67.42
2017-10-09 19:00 | 75.54 | 70.54
2017-10-09 19:30 | 73.6 | 68.38
2017-10-09 20:00 | 71.01 | 65.44
2017-10-09 20:30 | 67.93 | 61.95
2017-10-09 21:00 | 65.55 | 59.21
2017-10-09 21:30 | 62.89 | 56.09
2017-10-09 22:00 | 60.9 | 53.69
2017-10-09 22:30 | 58.79 | 51.47
2017-10-09 23:00 | 56 | 49.94
2017-10-09 23:30 | 52.63 | 46.01
2017-10-10 | 50.45 | 43.35
2017-10-10 00:30 | 49.89 | 42.76
2017-10-10 01:00 | 48.11 | 41.14
2017-10-10 01:30 | 47.44 | 40.32
2017-10-10 02:00 | 46.13 | 39.24
2017-10-10 02:30 | 46.03 | 39.3
2017-10-10 03:00 | 45.49 | 38.94
2017-10-10 03:30 | 45.89 | 39.41
2017-10-10 04:00 | 45.9 | 39.42
2017-10-10 04:30 | 45.4 | 38.88
2017-10-10 05:00 | 46.11 | 39.74
2017-10-10 05:30 | 48.29 | 42.42
2017-10-10 06:00 | 50.55 | 45.09
2017-10-10 06:30 | 53.42 | 50.83
2017-10-10 07:00 | 55.1 | 54.51
2017-10-10 07:30 | 63.56 | 58.82
2017-10-10 08:00 | 66.27 | 60.8
2017-10-10 08:30 | 68.31 | 63.1
2017-10-10 09:00 | 69.21 | 64.29
2017-10-10 09:30 | 68.4 | 63.51
2017-10-10 10:00 | 68.56 | 63.75
2017-10-10 10:30 | 68.91 | 64.22
2017-10-10 11:00 | 69.04 | 64.42
2017-10-10 11:30 | 68.65 | 64
2017-10-10 12:00 | 68.38 | 63.73
2017-10-10 12:30 | 69.44 | 64.87
2017-10-10 13:00 | 69.41 | 64.81
2017-10-10 13:30 | 71.18 | 66.78
2017-10-10 14:00 | 72.23 | 67.92
2017-10-10 14:30 | 72.05 | 67.71
2017-10-10 15:00 | 71.96 | 67.59
2017-10-10 15:30 | 67.28 | 65.42
2017-10-10 16:00 | 65.98 | 64.46
2017-10-10 16:30 | 65.43 | 63.78
2017-10-10 17:00 | 63.91 | 62.13
2017-10-10 17:30 | 62.29 | 60.29
2017-10-10 18:00 | 60.53 | 58.31
2017-10-10 18:30 | 62.29 | 60.11
2017-10-10 19:00 | 63.76 | 61.67
2017-10-10 19:30 | 60.95 | 58.69
2017-10-10 20:00 | 58.21 | 55.73
2017-10-10 20:30 | 56.95 | 54.01
2017-10-10 21:00 | 63.46 | 50.89
2017-10-10 21:30 | 62.64 | 47.98
2017-10-10 22:00 | 60.76 | 45.17
2017-10-10 22:30 | 59.23 | 42.85
2017-10-10 23:00 | 59.01 | 42.42
2017-10-10 23:30 | 54.9 | 38.32
2017-10-11 | 52.16 | 36.19
2017-10-11 00:30 | 52.04 | 35.86
2017-10-11 01:00 | 51.05 | 34.3
2017-10-11 01:30 | 49.74 | 32.98
2017-10-11 02:00 | 49.28 | 32.6
2017-10-11 02:30 | 48.82 | 32.17
2017-10-11 03:00 | 47.41 | 31.8
2017-10-11 03:30 | 47.11 | 31.44
2017-10-11 04:00 | 47.16 | 31.55
2017-10-11 04:30 | 47.82 | 32.65
2017-10-11 05:00 | 48.76 | 34.09
2017-10-11 05:30 | 39.34 | 37.4
2017-10-11 06:00 | 40.17 | 38.41
2017-10-11 06:30 | 45.69 | 44.23
2017-10-11 07:00 | 50.12 | 48.77
2017-10-11 07:30 | 55.5 | 54.15
2017-10-11 08:00 | 57.08 | 55.85
2017-10-11 08:30 | 60.3 | 59.21
2017-10-11 09:00 | 62.39 | 60.82
2017-10-11 09:30 | 62.83 | 61.26
2017-10-11 10:00 | 62.49 | 60.93
2017-10-11 10:30 | 62.62 | 61.07
2017-10-11 11:00 | 62.91 | 61.41
2017-10-11 11:30 | 63.98 | 62.5
2017-10-11 12:00 | 65.07 | 63.65
2017-10-11 12:30 | 65.29 | 63.87
2017-10-11 13:00 | 64.93 | 63.51
2017-10-11 13:30 | 65.8 | 64.41
2017-10-11 14:00 | 64.93 | 63.51
2017-10-11 14:30 | 65.87 | 64.47
2017-10-11 15:00 | 64.92 | 63.49
2017-10-11 15:30 | 64.26 | 62.75
2017-10-11 16:00 | 64.74 | 63.16
2017-10-11 16:30 | 64.93 | 63.26
2017-10-11 17:00 | 63.32 | 61.5
2017-10-11 17:30 | 61.76 | 59.7
2017-10-11 18:00 | 61.05 | 58.81
2017-10-11 18:30 | 61.55 | 59.31
2017-10-11 19:00 | 63.22 | 61.06
2017-10-11 19:30 | 61.42 | 59.15
2017-10-11 20:00 | 58.95 | 56.47
2017-10-11 20:30 | 59.35 | 53.87
2017-10-11 21:00 | 64.49 | 50.49
2017-10-11 21:30 | 60.13 | 47.84
2017-10-11 22:00 | 58.51 | 45.65
2017-10-11 22:30 | 57.54 | 44.16
2017-10-11 23:00 | 57.17 | 43.55
2017-10-11 23:30 | 54.64 | 39.86
2017-10-12 | 53.45 | 38.02
2017-10-12 00:30 | 52.65 | 36.62
2017-10-12 01:00 | 51.22 | 34.45
2017-10-12 01:30 | 51.32 | 34.44
2017-10-12 02:00 | 51 | 33.9
2017-10-12 02:30 | 49.76 | 32.73
2017-10-12 03:00 | 48.46 | 32.12
2017-10-12 03:30 | 47.45 | 31.64
2017-10-12 04:00 | 47.34 | 31.46
2017-10-12 04:30 | 48.34 | 33.03
2017-10-12 05:00 | 45.24 | 34.34
2017-10-12 05:30 | 43.91 | 36.96
2017-10-12 06:00 | 44.76 | 38.06
2017-10-12 06:30 | 48.22 | 42.46
2017-10-12 07:00 | 52.11 | 46.78
2017-10-12 07:30 | 53.6 | 52.98
2017-10-12 08:00 | 55.88 | 55.49
2017-10-12 08:30 | 59.54 | 58.78
2017-10-12 09:00 | 61.21 | 60.14
2017-10-12 09:30 | 61.4 | 60.83
2017-10-12 10:00 | 62.07 | 61.93
2017-10-12 10:30 | 62.91 | 62.83
2017-10-12 11:00 | 61.6 | 61.55
2017-10-12 11:30 | 62.63 | 62.59
2017-10-12 12:00 | 62.65 | 62.62
2017-10-12 12:30 | 63.45 | 63.42
2017-10-12 13:00 | 62.59 | 62.56
2017-10-12 13:30 | 62.78 | 62.76
2017-10-12 14:00 | 64.88 | 64.86
2017-10-12 14:30 | 65.24 | 65.23
2017-10-12 15:00 | 65.41 | 65.39
2017-10-12 15:30 | 65.3 | 65.22
2017-10-12 16:00 | 65.7 | 65.52
2017-10-12 16:30 | 66.73 | 66.38
2017-10-12 17:00 | 59.15 | 58.33
2017-10-12 17:30 | 35.01 | 32.36
2017-10-12 18:00 | 62.77 | 57.15
2017-10-12 18:30 | 66.6 | 60.41
2017-10-12 19:00 | 67.91 | 61.85
2017-10-12 19:30 | 66.4 | 60.08
2017-10-12 20:00 | 63.24 | 56.4
2017-10-12 20:30 | 60.39 | 53.03
2017-10-12 21:00 | 58.76 | 51.01
2017-10-12 21:30 | 55.05 | 47.8
2017-10-12 22:00 | 51.46 | 44.45
2017-10-12 22:30 | 50.27 | 42.94
2017-10-12 23:00 | 50.07 | 42.65
2017-10-12 23:30 | 47.16 | 39.45
2017-10-13 | 45.11 | 37.03
2017-10-13 00:30 | 44.45 | 36.11
2017-10-13 01:00 | 43.29 | 34.59
2017-10-13 01:30 | 42.87 | 33.99
2017-10-13 02:00 | 42.28 | 33.4
2017-10-13 02:30 | 40.78 | 32.63
2017-10-13 03:00 | 40.03 | 31.76
2017-10-13 03:30 | 39.74 | 31.35
2017-10-13 04:00 | 39.71 | 31.33
2017-10-13 04:30 | 40.72 | 32.61
2017-10-13 05:00 | 41.3 | 33.45
2017-10-13 05:30 | 44.05 | 37.06
2017-10-13 06:00 | 45.56 | 38.94
2017-10-13 06:30 | 48.31 | 42.48
2017-10-13 07:00 | 53.28 | 48.09
2017-10-13 07:30 | 57.99 | 53.28
2017-10-13 08:00 | 57.88 | 56.25
2017-10-13 08:30 | 37.36 | 35.47
2017-10-13 09:00 | 60.89 | 59.77
2017-10-13 09:30 | 62.12 | 61.93
2017-10-13 10:00 | 61.53 | 61.41
2017-10-13 10:30 | 62.18 | 62.11
2017-10-13 11:00 | 62.99 | 62.95
2017-10-13 11:30 | 63.04 | 63.02
2017-10-13 12:00 | 62.64 | 62.59
2017-10-13 12:30 | 62.08 | 62.02
2017-10-13 13:00 | 60.94 | 60.86
2017-10-13 13:30 | 61.92 | 61.82
2017-10-13 14:00 | 62.15 | 62.01
2017-10-13 14:30 | 61.63 | 61.45
2017-10-13 15:00 | 61.29 | 61.09
2017-10-13 15:30 | 62.13 | 61.81
2017-10-13 16:00 | 62.33 | 61.21
2017-10-13 16:30 | 61.82 | 59.88
2017-10-13 17:00 | 61.93 | 59.91
2017-10-13 17:30 | 58.99 | 57.03
2017-10-13 18:00 | 58.12 | 56.2
2017-10-13 18:30 | 57.76 | 55.79
2017-10-13 19:00 | 58.39 | 56.45
2017-10-13 19:30 | 57.5 | 55.51
2017-10-13 20:00 | 54.74 | 52.57
2017-10-13 20:30 | 52.92 | 50.62
2017-10-13 21:00 | 51.48 | 49.03
2017-10-13 21:30 | 50.6 | 47.3
2017-10-13 22:00 | 56.53 | 44.58
2017-10-13 22:30 | 44.48 | 42.64
2017-10-13 23:00 | 44.75 | 42.9
2017-10-13 23:30 | 41.59 | 39.53
2017-10-14 | 39.6 | 37.37
2017-10-14 00:30 | 38.14 | 35.76
2017-10-14 01:00 | 36.75 | 34.25
2017-10-14 01:30 | 36.38 | 33.81
2017-10-14 02:00 | 35.7 | 33.05
2017-10-14 02:30 | 35.69 | 32.98
2017-10-14 03:00 | 34.71 | 31.9
2017-10-14 03:30 | 34.75 | 32.27
2017-10-14 04:00 | 34.2 | 31.7
2017-10-14 04:30 | 34.5 | 32.01
2017-10-14 05:00 | 34.59 | 32.15
2017-10-14 05:30 | 35.11 | 32.76
2017-10-14 06:00 | 35.86 | 33.55
2017-10-14 06:30 | 37.41 | 35.3
2017-10-14 07:00 | 38.87 | 36.93
2017-10-14 07:30 | 40.24 | 38.43
2017-10-14 08:00 | 42.64 | 41.02
2017-10-14 08:30 | 44.43 | 42.82
2017-10-14 09:00 | 42.99 | 41.24
2017-10-14 09:30 | 46.17 | 44.65
2017-10-14 10:00 | 48.01 | 46.58
2017-10-14 10:30 | 48.34 | 46.95
2017-10-14 11:00 | 45.81 | 44.35
2017-10-14 11:30 | 44.2 | 42.67
2017-10-14 12:00 | 43.28 | 41.57
2017-10-14 12:30 | 42.66 | 40.97
2017-10-14 13:00 | 42.78 | 41.09
2017-10-14 13:30 | 42.64 | 40.92
2017-10-14 14:00 | 43.27 | 41.56
2017-10-14 14:30 | 43.94 | 42.22
2017-10-14 15:00 | 43.07 | 41.3
2017-10-14 15:30 | 42.42 | 40.59
2017-10-14 16:00 | 43.3 | 41.48
2017-10-14 16:30 | 40.68 | 38.75
2017-10-14 17:00 | 44.86 | 43.03
2017-10-14 17:30 | 46.24 | 44.47
2017-10-14 18:00 | 47.16 | 45.42
2017-10-14 18:30 | 48.6 | 46.97
2017-10-14 19:00 | 48.58 | 46.98
2017-10-14 19:30 | 48.33 | 46.71
2017-10-14 20:00 | 46.72 | 45.01
2017-10-14 20:30 | 45.1 | 43.29
2017-10-14 21:00 | 44.04 | 42.14
2017-10-14 21:30 | 42.86 | 40.87
2017-10-14 22:00 | 40.68 | 38.49
2017-10-14 22:30 | 39.51 | 37.23
2017-10-14 23:00 | 40.25 | 38
2017-10-14 23:30 | 37 | 34.47
2017-10-15 | 35.91 | 33.22
2017-10-15 00:30 | 35.73 | 33
2017-10-15 01:00 | 35.06 | 32.27
2017-10-15 01:30 | 34.38 | 31.51
2017-10-15 02:00 | 33.09 | 30.1
2017-10-15 02:30 | 33.17 | 30.18
2017-10-15 03:00 | 33.57 | 30.6
2017-10-15 03:30 | 32.91 | 30.21
2017-10-15 04:00 | 31.66 | 28.87
2017-10-15 04:30 | 32.75 | 30.1
2017-10-15 05:00 | 32.67 | 30
2017-10-15 05:30 | 32.98 | 30.34
2017-10-15 06:00 | 32.91 | 30.22
2017-10-15 06:30 | 33.5 | 30.87
2017-10-15 07:00 | 34.51 | 32.03
2017-10-15 07:30 | 35.02 | 32.67
2017-10-15 08:00 | 34.46 | 32.13
2017-10-15 08:30 | 37.97 | 36.01
2017-10-15 09:00 | 38.36 | 36.15
2017-10-15 09:30 | 38.12 | 35.95
2017-10-15 10:00 | 39.75 | 37.73
2017-10-15 10:30 | 40.72 | 38.83
2017-10-15 11:00 | 40.22 | 38.32
2017-10-15 11:30 | 39.91 | 37.99
2017-10-15 12:00 | 40.4 | 38.51
2017-10-15 12:30 | 40.16 | 38.23
2017-10-15 13:00 | 39.83 | 37.91
2017-10-15 13:30 | 42.06 | 40.24
2017-10-15 14:00 | 41.03 | 39.14
2017-10-15 14:30 | 44.37 | 42.6
2017-10-15 15:00 | 44.17 | 42.36
2017-10-15 15:30 | 41.74 | 39.78
2017-10-15 16:00 | 42.35 | 40.41
2017-10-15 16:30 | 44.25 | 42.37
2017-10-15 17:00 | 44.05 | 42.14
2017-10-15 17:30 | 45.02 | 43.16
2017-10-15 18:00 | 46.75 | 44.97
2017-10-15 18:30 | 48.79 | 47.14
2017-10-15 19:00 | 49.96 | 48.38
2017-10-15 19:30 | 48.31 | 46.64
2017-10-15 20:00 | 46.09 | 44.29
2017-10-15 20:30 | 44.57 | 42.67
2017-10-15 21:00 | 43.77 | 41.8
2017-10-15 21:30 | 42.18 | 40.08
2017-10-15 22:00 | 40.01 | 37.73
2017-10-15 22:30 | 38.88 | 36.49
2017-10-15 23:00 | 39.27 | 36.9
2017-10-15 23:30 | 36.22 | 33.57
2017-10-16 | 35.51 | 32.76
2017-10-16 00:30 | 34.44 | 31.56
2017-10-16 01:00 | 33.2 | 30.47
2017-10-16 01:30 | 32.11 | 29.41
2017-10-16 02:00 | 32.12 | 29.4
2017-10-16 02:30 | 31.93 | 29.17
2017-10-16 03:00 | 31.43 | 28.63
2017-10-16 03:30 | 31.36 | 28.54
2017-10-16 04:00 | 31.28 | 28.46
2017-10-16 04:30 | 32.64 | 29.96
2017-10-16 05:00 | 33.94 | 31.43
2017-10-16 05:30 | 35.96 | 33.7
2017-10-16 06:00 | 36.98 | 34.86
2017-10-16 06:30 | 42.06 | 40.39
2017-10-16 07:00 | 46.23 | 44.78
2017-10-16 07:30 | 51.31 | 49.94
2017-10-16 08:00 | 53.48 | 52.19
2017-10-16 08:30 | 56.22 | 55.05
2017-10-16 09:00 | 58.76 | 57.56
2017-10-16 09:30 | 58.92 | 58.68
2017-10-16 10:00 | 59.07 | 57.87
2017-10-16 10:30 | 64.66 | 58.8
2017-10-16 11:00 | 65.08 | 59.36
2017-10-16 11:30 | 65.95 | 60.36
2017-10-16 12:00 | 54.92 | 50.13
2017-10-16 12:30 | 66.82 | 61.44
2017-10-16 13:00 | 66.84 | 61.38
2017-10-16 13:30 | 67.11 | 61.66
2017-10-16 14:00 | 66.76 | 61.26
2017-10-16 14:30 | 65.58 | 59.93
2017-10-16 15:00 | 63.6 | 57.71
2017-10-16 15:30 | 63.7 | 57.7
2017-10-16 16:00 | 63.15 | 56.94
2017-10-16 16:30 | 62.5 | 55.99
2017-10-16 17:00 | 61.19 | 54.92
2017-10-16 17:30 | 59.89 | 54.54
2017-10-16 18:00 | 60.04 | 54.6
2017-10-16 18:30 | 59.9 | 54.45
2017-10-16 19:00 | 59.89 | 54.39
2017-10-16 19:30 | 57.39 | 51.51
2017-10-16 20:00 | 54.95 | 48.68
2017-10-16 20:30 | 53.4 | 46.75
2017-10-16 21:00 | 51.71 | 44.65
2017-10-16 21:30 | 49.39 | 41.79
2017-10-16 22:00 | 46.98 | 38.7
2017-10-16 22:30 | 45.44 | 36.7
2017-10-16 23:00 | 45.41 | 36.6
2017-10-16 23:30 | 43 | 33.37
2017-10-17 | 42.84 | 33.11
2017-10-17 00:30 | 41.35 | 31.56
2017-10-17 01:00 | 39.39 | 29.72
2017-10-17 01:30 | 38.92 | 29.35
2017-10-17 02:00 | 38.79 | 29.16
2017-10-17 02:30 | 38.55 | 28.81
2017-10-17 03:00 | 38.01 | 28.69
2017-10-17 03:30 | 37.79 | 28.64
2017-10-17 04:00 | 38.22 | 29.25
2017-10-17 04:30 | 39.22 | 30.59
2017-10-17 05:00 | 39.59 | 31.1
2017-10-17 05:30 | 40.8 | 32.81
2017-10-17 06:00 | 42.81 | 35.41
2017-10-17 06:30 | 46.98 | 40.75
2017-10-17 07:00 | 51.54 | 45.98
2017-10-17 07:30 | 54.81 | 49.62
2017-10-17 08:00 | 58.13 | 53.33
2017-10-17 08:30 | 62.08 | 56.2
2017-10-17 09:00 | 64.16 | 58.25
2017-10-17 09:30 | 64.95 | 59.17
2017-10-17 10:00 | 66.14 | 60.4
2017-10-17 10:30 | 65.99 | 60.24
2017-10-17 11:00 | 64.39 | 58.49
2017-10-17 11:30 | 66.23 | 60.62
2017-10-17 12:00 | 65.45 | 59.8
2017-10-17 12:30 | 65.66 | 60.05
2017-10-17 13:00 | 67.67 | 62.21
2017-10-17 13:30 | 65.58 | 59.88
2017-10-17 14:00 | 64.12 | 58.45
2017-10-17 14:30 | 64.89 | 59.38
2017-10-17 15:00 | 64.82 | 59.24
2017-10-17 15:30 | 65.61 | 60.01
2017-10-17 16:00 | 66.48 | 60.84
2017-10-17 16:30 | 64.72 | 58.66
2017-10-17 17:00 | 63.3 | 56.9
2017-10-17 17:30 | 62.91 | 56.26
2017-10-17 18:00 | 62.68 | 55.78
2017-10-17 18:30 | 63.1 | 56.18
2017-10-17 19:00 | 62.87 | 55.86
2017-10-17 19:30 | 60.28 | 52.79
2017-10-17 20:00 | 58.11 | 50.15
2017-10-17 20:30 | 56.59 | 48.25
2017-10-17 21:00 | 60.48 | 43.07
2017-10-17 21:30 | 67.72 | 43.11
2017-10-17 22:00 | 66.3 | 40.43
2017-10-17 22:30 | 65.79 | 39.27
2017-10-17 23:00 | 65.93 | 39.42
2017-10-17 23:30 | 64.14 | 35.88
2017-10-18 | 62.86 | 34.47
2017-10-18 00:30 | 58.93 | 32.81
2017-10-18 01:00 | 57.67 | 31.54
2017-10-18 01:30 | 57.63 | 31.44
2017-10-18 02:00 | 57.3 | 30.73
2017-10-18 02:30 | 57.11 | 30.23
2017-10-18 03:00 | 57.03 | 30.41
2017-10-18 03:30 | 56.09 | 29.76
2017-10-18 04:00 | 56.06 | 29.72
2017-10-18 04:30 | 56.32 | 30.45
2017-10-18 05:00 | 56.74 | 31.42
2017-10-18 05:30 | 58.01 | 34.25
2017-10-18 06:00 | 56.28 | 37.87
2017-10-18 06:30 | 50.08 | 43.97
2017-10-18 07:00 | 54.77 | 49.31
2017-10-18 07:30 | 59.75 | 54.65
2017-10-18 08:00 | 61.72 | 56.96
2017-10-18 08:30 | 63.69 | 59.33
2017-10-18 09:00 | 63.72 | 61.3
2017-10-18 09:30 | 62.76 | 61.14
2017-10-18 10:00 | 61.15 | 59.54
2017-10-18 10:30 | 59.03 | 57.69
2017-10-18 11:00 | 59.95 | 58.03
2017-10-18 11:30 | 63.61 | 59.28
2017-10-18 12:00 | 67.37 | 61.71
2017-10-18 12:30 | 68.31 | 63.05
2017-10-18 13:00 | 67.11 | 61.76
2017-10-18 13:30 | 65.98 | 60.49
2017-10-18 14:00 | 63.59 | 57.63
2017-10-18 14:30 | 67.31 | 61.75
2017-10-18 15:00 | 66.76 | 61.13
2017-10-18 15:30 | 66.1 | 60.52
2017-10-18 16:00 | 68.15 | 62.84
2017-10-18 16:30 | 66.49 | 61.16
2017-10-18 17:00 | 62.39 | 59.63
2017-10-18 17:30 | 57.96 | 57.87
2017-10-18 18:00 | 57.23 | 57.19
2017-10-18 18:30 | 57.92 | 57.89
2017-10-18 19:00 | 57.61 | 57.58
2017-10-18 19:30 | 55.19 | 55.17
2017-10-18 20:00 | 53.78 | 53.76
2017-10-18 20:30 | 50.21 | 50.17
2017-10-18 21:00 | 48.64 | 48.59
2017-10-18 21:30 | 46.22 | 46.11
2017-10-18 22:00 | 43.2 | 42.94
2017-10-18 22:30 | 45.72 | 40.92
2017-10-18 23:00 | 48.46 | 40.59
2017-10-18 23:30 | 45.64 | 37.06
2017-10-19 | 44.99 | 36.15
2017-10-19 00:30 | 43.53 | 34.17
2017-10-19 01:00 | 42.57 | 32.89
2017-10-19 01:30 | 42.1 | 32.22
2017-10-19 02:00 | 41.65 | 32.16
2017-10-19 02:30 | 40.67 | 31.06
2017-10-19 03:00 | 40.14 | 30.72
2017-10-19 03:30 | 39.34 | 30.41
2017-10-19 04:00 | 39.27 | 30.79
2017-10-19 04:30 | 39.92 | 31.67
2017-10-19 05:00 | 40.85 | 32.96
2017-10-19 05:30 | 42.77 | 35.54
2017-10-19 06:00 | 45.33 | 38.78
2017-10-19 06:30 | 47.92 | 44.47
2017-10-19 07:00 | 49.65 | 49.23
2017-10-19 07:30 | 61.48 | 55.41
2017-10-19 08:00 | 64.54 | 58.56
2017-10-19 08:30 | 64.29 | 58.39
2017-10-19 09:00 | 68.17 | 62.89
2017-10-19 09:30 | 67.89 | 62.63
2017-10-19 10:00 | 67.23 | 61.95
2017-10-19 10:30 | 67.86 | 62.7
2017-10-19 11:00 | 68.29 | 63.23
2017-10-19 11:30 | 67.33 | 62.18
2017-10-19 12:00 | 67.64 | 62.63
2017-10-19 12:30 | 68.09 | 63.15
2017-10-19 13:00 | 69.74 | 64.89
2017-10-19 13:30 | 69.75 | 64.96
2017-10-19 14:00 | 70.98 | 66.27
2017-10-19 14:30 | 70.83 | 66.07
2017-10-19 15:00 | 68.46 | 63.42
2017-10-19 15:30 | 68.72 | 63.61
2017-10-19 16:00 | 67.47 | 62.1
2017-10-19 16:30 | 67.02 | 61.45
2017-10-19 17:00 | 66.12 | 60.25
2017-10-19 17:30 | 64.39 | 58.04
2017-10-19 18:00 | 64.28 | 57.72
2017-10-19 18:30 | 65.16 | 58.69
2017-10-19 19:00 | 65.77 | 59.35
2017-10-19 19:30 | 64.08 | 57.38
2017-10-19 20:00 | 62.11 | 55.1
2017-10-19 20:30 | 60.07 | 52.61
2017-10-19 21:00 | 58.84 | 51.04
2017-10-19 21:30 | 55.61 | 47.97
2017-10-19 22:00 | 51.54 | 44.55
2017-10-19 22:30 | 49.5 | 42.02
2017-10-19 23:00 | 49.44 | 41.91
2017-10-19 23:30 | 46.76 | 38.55
2017-10-20 | 45.12 | 36.37
2017-10-20 00:30 | 44.3 | 35.2
2017-10-20 01:00 | 43.02 | 33.48
2017-10-20 01:30 | 41.92 | 32.77
2017-10-20 02:00 | 41.61 | 32.3
2017-10-20 02:30 | 40.77 | 31.65
2017-10-20 03:00 | 39.88 | 31.57
2017-10-20 03:30 | 39.83 | 31.45
2017-10-20 04:00 | 39.74 | 31.28
2017-10-20 04:30 | 40.04 | 31.76
2017-10-20 05:00 | 40.73 | 32.7
2017-10-20 05:30 | 42.67 | 35.3
2017-10-20 06:00 | 44.73 | 37.99
2017-10-20 06:30 | 48.67 | 42.98
2017-10-20 07:00 | 48.24 | 47.57
2017-10-20 07:30 | 54.02 | 53.39
2017-10-20 08:00 | 56.9 | 56.2
2017-10-20 08:30 | 59.24 | 58.28
2017-10-20 09:00 | 60.2 | 58.95
2017-10-20 09:30 | 61.6 | 60.16
2017-10-20 10:00 | 59.96 | 58.31
2017-10-20 10:30 | 59.12 | 57.82
2017-10-20 11:00 | 58.91 | 58.53
2017-10-20 11:30 | 58.55 | 58.3
2017-10-20 12:00 | 60.64 | 60.39
2017-10-20 12:30 | 59.7 | 59.4
2017-10-20 13:00 | 58.11 | 57.82
2017-10-20 13:30 | 57.61 | 57.26
2017-10-20 14:00 | 58.03 | 57.65
2017-10-20 14:30 | 57.86 | 57.43
2017-10-20 15:00 | 58.54 | 57.72
2017-10-20 15:30 | 59.44 | 57.43
2017-10-20 16:00 | 59.07 | 56.98
2017-10-20 16:30 | 59.63 | 57.49
2017-10-20 17:00 | 58.44 | 56.15
2017-10-20 17:30 | 64.36 | 53.68
2017-10-20 18:00 | 65.96 | 52.27
2017-10-20 18:30 | 65.18 | 51.94
2017-10-20 19:00 | 66.05 | 53.13
2017-10-20 19:30 | 64.94 | 51.62
2017-10-20 20:00 | 63.34 | 49.36
2017-10-20 20:30 | 62.05 | 47.48
2017-10-20 21:00 | 61.05 | 45.99
2017-10-20 21:30 | 59.3 | 44.11
2017-10-20 22:00 | 55.26 | 41.56
2017-10-20 22:30 | 53.7 | 40.04
2017-10-20 23:00 | 53.65 | 39.87
2017-10-20 23:30 | 51.62 | 36.93
2017-10-21 | 50.47 | 35.16
2017-10-21 00:30 | 49.89 | 34.15
2017-10-21 01:00 | 49.15 | 32.85
2017-10-21 01:30 | 48.71 | 32.11
2017-10-21 02:00 | 48.31 | 31.49
2017-10-21 02:30 | 48.18 | 31.23
2017-10-21 03:00 | 47.99 | 30.94
2017-10-21 03:30 | 47.11 | 30.69
2017-10-21 04:00 | 47.07 | 30.58
2017-10-21 04:30 | 47.17 | 30.77
2017-10-21 05:00 | 47.39 | 31.17
2017-10-21 05:30 | 48.13 | 32.51
2017-10-21 06:00 | 48.39 | 32.87
2017-10-21 06:30 | 49.74 | 35.16
2017-10-21 07:00 | 50.71 | 36.94
2017-10-21 07:30 | 42.3 | 39.2
2017-10-21 08:00 | 42.8 | 41.17
2017-10-21 08:30 | 45.39 | 43.78
2017-10-21 09:00 | 46.43 | 44.94
2017-10-21 09:30 | 47.77 | 46.39
2017-10-21 10:00 | 48.6 | 47.25
2017-10-21 10:30 | 49.62 | 48.28
2017-10-21 11:00 | 50.21 | 48.9
2017-10-21 11:30 | 49.84 | 48.53
2017-10-21 12:00 | 48.17 | 46.79
2017-10-21 12:30 | 48.34 | 46.92
2017-10-21 13:00 | 49.71 | 48.32
2017-10-21 13:30 | 48.91 | 47.44
2017-10-21 14:00 | 48.7 | 47.19
2017-10-21 14:30 | 47.47 | 45.86
2017-10-21 15:00 | 47.02 | 45.35
2017-10-21 15:30 | 46.17 | 44.43
2017-10-21 16:00 | 45.56 | 43.77
2017-10-21 16:30 | 45.61 | 43.78
2017-10-21 17:00 | 44.94 | 43.05
2017-10-21 17:30 | 45.29 | 43.4
2017-10-21 18:00 | 46.18 | 44.33
2017-10-21 18:30 | 47.94 | 46.2
2017-10-21 19:00 | 47.64 | 45.9
2017-10-21 19:30 | 46.12 | 44.3
2017-10-21 20:00 | 44.76 | 42.85
2017-10-21 20:30 | 43.06 | 41.03
2017-10-21 21:00 | 42.29 | 40.2
2017-10-21 21:30 | 41.23 | 39.05
2017-10-21 22:00 | 40.34 | 38.08
2017-10-21 22:30 | 39.38 | 37.03
2017-10-21 23:00 | 39.75 | 37.42
2017-10-21 23:30 | 37.23 | 34.68
2017-10-22 | 35.95 | 33.25
2017-10-22 00:30 | 35.14 | 32.34
2017-10-22 01:00 | 34.26 | 31.39
2017-10-22 01:30 | 33.31 | 30.71
2017-10-22 02:00 | 32.99 | 30.36
2017-10-22 02:30 | 32.65 | 29.95
2017-10-22 03:00 | 32.4 | 29.68
2017-10-22 03:30 | 32.39 | 29.66
2017-10-22 04:00 | 32.44 | 29.72
2017-10-22 04:30 | 32.39 | 29.66
2017-10-22 05:00 | 31.41 | 28.51
2017-10-22 05:30 | 31.57 | 28.65
2017-10-22 06:00 | 31.59 | 28.61
2017-10-22 06:30 | 32.56 | 29.7
2017-10-22 07:00 | 31.71 | 28.87
2017-10-22 07:30 | 32.99 | 30.34
2017-10-22 08:00 | 34.14 | 31.66
2017-10-22 08:30 | 22.52 | 18.98
2017-10-22 09:00 | 37.12 | 35.02
2017-10-22 09:30 | 37.44 | 35.24
2017-10-22 10:00 | 37.77 | 35.51
2017-10-22 10:30 | 38.31 | 36.13
2017-10-22 11:00 | 38.34 | 36.18
2017-10-22 11:30 | 38.01 | 35.85
2017-10-22 12:00 | 31.83 | 29.33
2017-10-22 12:30 | 40.03 | 38.01
2017-10-22 13:00 | 38.76 | 36.67
2017-10-22 13:30 | 38.39 | 36.27
2017-10-22 14:00 | 38.51 | 36.4
2017-10-22 14:30 | 38.72 | 36.6
2017-10-22 15:00 | 40.5 | 38.46
2017-10-22 15:30 | 40.95 | 38.92
2017-10-22 16:00 | 41.63 | 39.6
2017-10-22 16:30 | 42.41 | 40.4
2017-10-22 17:00 | 42.86 | 40.86
2017-10-22 17:30 | 43.55 | 41.57
2017-10-22 18:00 | 45.31 | 43.43
2017-10-22 18:30 | 47.48 | 45.71
2017-10-22 19:00 | 49.33 | 47.67
2017-10-22 19:30 | 47.99 | 46.26
2017-10-22 20:00 | 46.64 | 44.83
2017-10-22 20:30 | 44.63 | 42.68
2017-10-22 21:00 | 43.52 | 41.49
2017-10-22 21:30 | 41.64 | 39.47
2017-10-22 22:00 | 39.66 | 37.33
2017-10-22 22:30 | 38.28 | 35.82
2017-10-22 23:00 | 38.42 | 35.95
2017-10-22 23:30 | 35.46 | 32.69
2017-10-23 | 34.05 | 31.12
2017-10-23 00:30 | 33.26 | 30.39
2017-10-23 01:00 | 32.18 | 29.43
2017-10-23 01:30 | 31.82 | 29.02
2017-10-23 02:00 | 31.5 | 28.66
2017-10-23 02:30 | 31.49 | 28.63
2017-10-23 03:00 | 31.43 | 28.55
2017-10-23 03:30 | 31.54 | 28.67
2017-10-23 04:00 | 31.85 | 29.04
2017-10-23 04:30 | 31.47 | 28.65
2017-10-23 05:00 | 32.18 | 29.48
2017-10-23 05:30 | 34.17 | 31.75
2017-10-23 06:00 | 36.96 | 34.83
2017-10-23 06:30 | 41.74 | 40.05
2017-10-23 07:00 | 46.18 | 44.59
2017-10-23 07:30 | 52.35 | 50.79
2017-10-23 08:00 | 54.61 | 53.23
2017-10-23 08:30 | 56.51 | 55.3
2017-10-23 09:00 | 58.61 | 57.48
2017-10-23 09:30 | 60.5 | 59.32
2017-10-23 10:00 | 58.87 | 57.69
2017-10-23 10:30 | 57 | 55.76
2017-10-23 11:00 | 57.16 | 55.89
2017-10-23 11:30 | 56.8 | 55.45
2017-10-23 12:00 | 57.58 | 56.2
2017-10-23 12:30 | 59.72 | 58.45
2017-10-23 13:00 | 57.08 | 55.81
2017-10-23 13:30 | 57.71 | 56.23
2017-10-23 14:00 | 59.15 | 57.36
2017-10-23 14:30 | 59.19 | 57.39
2017-10-23 15:00 | 59.67 | 57.86
2017-10-23 15:30 | 59.57 | 57.71
2017-10-23 16:00 | 59.81 | 57.89
2017-10-23 16:30 | 60.46 | 58.43
2017-10-23 17:00 | 58.72 | 56.59
2017-10-23 17:30 | 56.98 | 54.79
2017-10-23 18:00 | 56.5 | 54.02
2017-10-23 18:30 | 66.42 | 53.53
2017-10-23 19:00 | 67.69 | 55.22
2017-10-23 19:30 | 66.33 | 53.37
2017-10-23 20:00 | 63.87 | 50.03
2017-10-23 20:30 | 62.91 | 48.44
2017-10-23 21:00 | 60.88 | 45.57
2017-10-23 21:30 | 59.52 | 43.52
2017-10-23 22:00 | 55.72 | 39.53
2017-10-23 22:30 | 52.08 | 37.63
2017-10-23 23:00 | 51.77 | 37.15
2017-10-23 23:30 | 49.55 | 33.66
2017-10-24 | 48.42 | 32.5
2017-10-24 00:30 | 48.07 | 32.39
2017-10-24 01:00 | 47.03 | 30.62
2017-10-24 01:30 | 46.2 | 29.31
2017-10-24 02:00 | 45.99 | 28.78
2017-10-24 02:30 | 46.44 | 29.4
2017-10-24 03:00 | 46.51 | 29.46
2017-10-24 03:30 | 46.43 | 29.27
2017-10-24 04:00 | 46.14 | 28.73
2017-10-24 04:30 | 46.47 | 29.41
2017-10-24 05:00 | 46.94 | 30.37
2017-10-24 05:30 | 48.49 | 33.03
2017-10-24 06:00 | 49.72 | 35.11
2017-10-24 06:30 | 52.53 | 39.65
2017-10-24 07:00 | 46.7 | 44.54
2017-10-24 07:30 | 50.74 | 49.4
2017-10-24 08:00 | 53.59 | 52.34
2017-10-24 08:30 | 55.84 | 54.63
2017-10-24 09:00 | 57.09 | 55.95
2017-10-24 09:30 | 57.89 | 56.73
2017-10-24 10:00 | 57.1 | 55.85
2017-10-24 10:30 | 57.62 | 56.3
2017-10-24 11:00 | 58.4 | 56.84
2017-10-24 11:30 | 58.58 | 56.9
2017-10-24 12:00 | 58.47 | 56.77
2017-10-24 12:30 | 58.71 | 57.03
2017-10-24 13:00 | 58.29 | 56.61
2017-10-24 13:30 | 58.99 | 57.32
2017-10-24 14:00 | 59.8 | 58.22
2017-10-24 14:30 | 60.18 | 58.59
2017-10-24 15:00 | 60.07 | 58.49
2017-10-24 15:30 | 59.61 | 58.04
2017-10-24 16:00 | 60.86 | 59.37
2017-10-24 16:30 | 60.52 | 59.11
2017-10-24 17:00 | 58.93 | 57.57
2017-10-24 17:30 | 57.14 | 55.86
2017-10-24 18:00 | 55.29 | 53.92
2017-10-24 18:30 | 56.13 | 54.79
2017-10-24 19:00 | 58.26 | 56.97
2017-10-24 19:30 | 55.68 | 54.34
2017-10-24 20:00 | 52.99 | 51.61
2017-10-24 20:30 | 50.88 | 49.48
2017-10-24 21:00 | 47.12 | 46.83
2017-10-24 21:30 | 44.92 | 44.9
2017-10-24 22:00 | 42.02 | 42
2017-10-24 22:30 | 39.54 | 39.46
2017-10-24 23:00 | 39.12 | 38.94
2017-10-24 23:30 | 37.97 | 35.61
2017-10-25 | 36.36 | 33.83
2017-10-25 00:30 | 35.82 | 33.19
2017-10-25 01:00 | 33.68 | 31.1
2017-10-25 01:30 | 33.59 | 31.09
2017-10-25 02:00 | 33.67 | 31.13
2017-10-25 02:30 | 32.4 | 29.69
2017-10-25 03:00 | 31.77 | 28.96
2017-10-25 03:30 | 31.8 | 29.01
2017-10-25 04:00 | 32.29 | 29.55
2017-10-25 04:30 | 32.95 | 30.27
2017-10-25 05:00 | 33.64 | 31.07
2017-10-25 05:30 | 35.9 | 33.58
2017-10-25 06:00 | 38.07 | 36
2017-10-25 06:30 | 42.72 | 41.1
2017-10-25 07:00 | 46.9 | 45.39
2017-10-25 07:30 | 52.29 | 51
2017-10-25 08:00 | 52.95 | 51.69
2017-10-25 08:30 | 55.32 | 54.1
2017-10-25 09:00 | 57.38 | 55.63
2017-10-25 09:30 | 57.9 | 56.01
2017-10-25 10:00 | 57.41 | 55.74
2017-10-25 10:30 | 58.16 | 56.58
2017-10-25 11:00 | 58.21 | 56.7
2017-10-25 11:30 | 58.32 | 56.81
2017-10-25 12:00 | 58.88 | 57.4
2017-10-25 12:30 | 59.51 | 58.03
2017-10-25 13:00 | 59.1 | 57.6
2017-10-25 13:30 | 59.39 | 57.92
2017-10-25 14:00 | 59.59 | 57.96
2017-10-25 14:30 | 60.19 | 58.49
2017-10-25 15:00 | 60.25 | 58.53
2017-10-25 15:30 | 59.47 | 57.65
2017-10-25 16:00 | 59.49 | 57.59
2017-10-25 16:30 | 59.32 | 57.28
2017-10-25 17:00 | 58.98 | 56.86
2017-10-25 17:30 | 60.09 | 54.62
2017-10-25 18:00 | 59.7 | 52.91
2017-10-25 18:30 | 59.34 | 52.35
2017-10-25 19:00 | 60.46 | 53.65
2017-10-25 19:30 | 59.12 | 52.03
2017-10-25 20:00 | 57.19 | 49.65
2017-10-25 20:30 | 54.65 | 47.33
2017-10-25 21:00 | 51.25 | 44.76
2017-10-25 21:30 | 49.7 | 42.87
2017-10-25 22:00 | 47.51 | 40.12
2017-10-25 22:30 | 45.76 | 37.86
2017-10-25 23:00 | 45.39 | 37.3
2017-10-25 23:30 | 42.88 | 33.96
2017-10-26 | 41.62 | 32.17
2017-10-26 00:30 | 41.25 | 31.65
2017-10-26 01:00 | 39.66 | 30.24
2017-10-26 01:30 | 39.06 | 29.4
2017-10-26 02:00 | 38.63 | 28.77
2017-10-26 02:30 | 37.6 | 28.13
2017-10-26 03:00 | 37.59 | 28.2
2017-10-26 03:30 | 37.56 | 28.13
2017-10-26 04:00 | 37.57 | 28.1
2017-10-26 04:30 | 37.98 | 28.64
2017-10-26 05:00 | 38.87 | 29.94
2017-10-26 05:30 | 40.31 | 32.01
2017-10-26 06:00 | 42.19 | 34.58
2017-10-26 06:30 | 45.8 | 39.3
2017-10-26 07:00 | 48.83 | 42.93
2017-10-26 07:30 | 50.69 | 47.69
2017-10-26 08:00 | 54.97 | 50.05
2017-10-26 08:30 | 57.28 | 48.94
2017-10-26 09:00 | 65.75 | 53.52
2017-10-26 09:30 | 65.43 | 53.24
2017-10-26 10:00 | 65.19 | 53.06
2017-10-26 10:30 | 65.87 | 54.14
2017-10-26 11:00 | 65.82 | 54.13
2017-10-26 11:30 | 66.35 | 54.89
2017-10-26 12:00 | 66.63 | 55.26
2017-10-26 12:30 | 67.26 | 56.04
2017-10-26 13:00 | 66.69 | 55.32
2017-10-26 13:30 | 66.81 | 55.46
2017-10-26 14:00 | 67.83 | 56.8
2017-10-26 14:30 | 68.65 | 57.8
2017-10-26 15:00 | 67.94 | 56.89
2017-10-26 15:30 | 68.05 | 56.82
2017-10-26 16:00 | 68.28 | 56.94
2017-10-26 16:30 | 68.99 | 57.51
2017-10-26 17:00 | 68.59 | 56.75
2017-10-26 17:30 | 67.38 | 54.74
2017-10-26 18:00 | 67.83 | 54.88
2017-10-26 18:30 | 68.85 | 56
2017-10-26 19:00 | 69.47 | 56.88
2017-10-26 19:30 | 67.52 | 54.22
2017-10-26 20:00 | 64.82 | 51.62
2017-10-26 20:30 | 62.68 | 49.2
2017-10-26 21:00 | 61.44 | 47.44
2017-10-26 21:30 | 59.61 | 44.71
2017-10-26 22:00 | 54.85 | 41.65
2017-10-26 22:30 | 53.3 | 39.64
2017-10-26 23:00 | 52.82 | 38.81
2017-10-26 23:30 | 50.23 | 35.01
2017-10-27 | 49.65 | 33.82
2017-10-27 00:30 | 48.37 | 32.84
2017-10-27 01:00 | 47.09 | 30.93
2017-10-27 01:30 | 46.73 | 30.34
2017-10-27 02:00 | 46.32 | 29.54
2017-10-27 02:30 | 46.15 | 29.12
2017-10-27 03:00 | 45.99 | 28.78
2017-10-27 03:30 | 46.07 | 28.88
2017-10-27 04:00 | 45.98 | 28.64
2017-10-27 04:30 | 46.33 | 29.18
2017-10-27 05:00 | 46.93 | 30.24
2017-10-27 05:30 | 47.99 | 32.19
2017-10-27 06:00 | 49.29 | 34.31
2017-10-27 06:30 | 51.89 | 39.27
2017-10-27 07:00 | 45.11 | 43.56
2017-10-27 07:30 | 48.95 | 47.51
2017-10-27 08:00 | 51.66 | 50.36
2017-10-27 08:30 | 53.61 | 52.29
2017-10-27 09:00 | 54.76 | 53.57
2017-10-27 09:30 | 55.48 | 54.27
2017-10-27 10:00 | 56.21 | 54.96
2017-10-27 10:30 | 57.41 | 56.08
2017-10-27 11:00 | 57.88 | 56.49
2017-10-27 11:30 | 59.46 | 57.91
2017-10-27 12:00 | 62.01 | 60.43
2017-10-27 12:30 | 62.93 | 61.39
2017-10-27 13:00 | 62.43 | 60.86
2017-10-27 13:30 | 62.04 | 60.45
2017-10-27 14:00 | 62.31 | 60.73
2017-10-27 14:30 | 61.9 | 60.28
2017-10-27 15:00 | 62.03 | 60.38
2017-10-27 15:30 | 61.95 | 60.24
2017-10-27 16:00 | 62.2 | 60.43
2017-10-27 16:30 | 62.61 | 60.77
2017-10-27 17:00 | 61.99 | 60.01
2017-10-27 17:30 | 59.59 | 57.59
2017-10-27 18:00 | 57.72 | 55.52
2017-10-27 18:30 | 55.46 | 53.33
2017-10-27 19:00 | 57.29 | 55.27
2017-10-27 19:30 | 55.87 | 53.76
2017-10-27 20:00 | 53.13 | 50.83
2017-10-27 20:30 | 51.1 | 48.63
2017-10-27 21:00 | 49.39 | 46.75
2017-10-27 21:30 | 52.86 | 44.68
2017-10-27 22:00 | 55.63 | 42.44
2017-10-27 22:30 | 53.77 | 40.24
2017-10-27 23:00 | 53.56 | 39.89
2017-10-27 23:30 | 51.17 | 36.38
2017-10-28 | 50.03 | 34.5
2017-10-28 00:30 | 49.63 | 33.68
2017-10-28 01:00 | 48.91 | 32.48
2017-10-28 01:30 | 48.35 | 31.57
2017-10-28 02:00 | 47.82 | 30.73
2017-10-28 02:30 | 48.36 | 31.47
2017-10-28 03:00 | 47.26 | 29.75
2017-10-28 03:30 | 47.11 | 29.41
2017-10-28 04:00 | 47.52 | 30.02
2017-10-28 04:30 | 47.46 | 30.07
2017-10-28 05:00 | 47.5 | 30.19
2017-10-28 05:30 | 48.03 | 30.95
2017-10-28 06:00 | 48.48 | 31.74
2017-10-28 06:30 | 49.42 | 33.52
2017-10-28 07:00 | 50.54 | 35.51
2017-10-28 07:30 | 52.28 | 38.47
2017-10-28 08:00 | 53.4 | 40.36
2017-10-28 08:30 | 45.68 | 43.49
2017-10-28 09:00 | 46.11 | 44.67
2017-10-28 09:30 | 46.55 | 45.11
2017-10-28 10:00 | 46.89 | 45.41
2017-10-28 10:30 | 46.91 | 45.41
2017-10-28 11:00 | 47.08 | 45.55
2017-10-28 11:30 | 48.2 | 46.69
2017-10-28 12:00 | 48.31 | 46.83
2017-10-28 12:30 | 47.71 | 46.28
2017-10-28 13:00 | 47.7 | 46.32
2017-10-28 13:30 | 49.26 | 47.93
2017-10-28 14:00 | 49.56 | 48.24
2017-10-28 14:30 | 49.21 | 47.86
2017-10-28 15:00 | 49.69 | 48.35
2017-10-28 15:30 | 49.75 | 48.39
2017-10-28 16:00 | 51.3 | 49.98
2017-10-28 16:30 | 51.91 | 50.55
2017-10-28 17:00 | 50.88 | 49.44
2017-10-28 17:30 | 51.62 | 50.18
2017-10-28 18:00 | 51.9 | 50.45
2017-10-28 18:30 | 52.53 | 51.11
2017-10-28 19:00 | 54.99 | 53.67
2017-10-28 19:30 | 52.94 | 51.55
2017-10-28 20:00 | 51.21 | 49.75
2017-10-28 20:30 | 49.57 | 48.02
2017-10-28 21:00 | 47.02 | 45.33
2017-10-28 21:30 | 46.02 | 44.25
2017-10-28 22:00 | 43.69 | 41.78
2017-10-28 22:30 | 42.16 | 40.13
2017-10-28 23:00 | 42.43 | 40.38
2017-10-28 23:30 | 39.63 | 37.36
2017-10-29 | 38.47 | 36.07
2017-10-29 00:30 | 37.89 | 35.41
2017-10-29 01:00 | 37.04 | 34.48
2017-10-29 01:30 | 35.9 | 33.24
2017-10-29 02:00 | 35.86 | 33.16
2017-10-29 02:30 | 34.6 | 31.78
2017-10-29 03:00 | 34.24 | 31.37
2017-10-29 03:30 | 34.01 | 31.11
2017-10-29 04:00 | 34.1 | 31.19
2017-10-29 04:30 | 34.77 | 31.92
2017-10-29 05:00 | 34.5 | 31.62
2017-10-29 05:30 | 33.66 | 30.68
2017-10-29 06:00 | 34.41 | 31.44
2017-10-29 06:30 | 35.33 | 32.5
2017-10-29 07:00 | 36.24 | 33.58
2017-10-29 07:30 | 38.34 | 35.92
2017-10-29 08:00 | 39.69 | 37.42
2017-10-29 08:30 | 41.48 | 39.39
2017-10-29 09:00 | 44.22 | 42.36
2017-10-29 09:30 | 44.44 | 42.63
2017-10-29 10:00 | 44.22 | 42.43
2017-10-29 10:30 | 43.59 | 41.83
2017-10-29 11:00 | 43.01 | 41.26
2017-10-29 11:30 | 42.96 | 41.23
2017-10-29 12:00 | 43.32 | 41.61
2017-10-29 12:30 | 44.54 | 42.88
2017-10-29 13:00 | 44.48 | 42.83
2017-10-29 13:30 | 44.77 | 43.14
2017-10-29 14:00 | 45.06 | 43.42
2017-10-29 14:30 | 44.96 | 43.3
2017-10-29 15:00 | 46.24 | 44.62
2017-10-29 15:30 | 46.73 | 45.09
2017-10-29 16:00 | 49.22 | 47.65
2017-10-29 16:30 | 49.02 | 47.41
2017-10-29 17:00 | 47.89 | 46.21
2017-10-29 17:30 | 48.64 | 46.98
2017-10-29 18:00 | 49.41 | 47.77
2017-10-29 18:30 | 51.11 | 49.54
2017-10-29 19:00 | 53.05 | 51.6
2017-10-29 19:30 | 52.44 | 50.96
2017-10-29 20:00 | 50.14 | 48.56
2017-10-29 20:30 | 48.65 | 46.97
2017-10-29 21:00 | 46.45 | 44.64
2017-10-29 21:30 | 44.85 | 42.94
2017-10-29 22:00 | 42.83 | 40.77
2017-10-29 22:30 | 41.26 | 39.08
2017-10-29 23:00 | 42 | 39.84
2017-10-29 23:30 | 39.09 | 36.72
2017-10-30 | 37.23 | 34.69
2017-10-30 00:30 | 36.12 | 33.46
2017-10-30 01:00 | 35.57 | 32.84
2017-10-30 01:30 | 35.44 | 32.67
2017-10-30 02:00 | 34.41 | 31.52
2017-10-30 02:30 | 34.29 | 31.36
2017-10-30 03:00 | 33.88 | 30.9
2017-10-30 03:30 | 34.34 | 31.39
2017-10-30 04:00 | 33.81 | 30.82
2017-10-30 04:30 | 34.85 | 31.98
2017-10-30 05:00 | 35.15 | 32.35
2017-10-30 05:30 | 37.13 | 34.59
2017-10-30 06:00 | 40.29 | 38.07
2017-10-30 06:30 | 44.8 | 43.03
2017-10-30 07:00 | 50.34 | 48.93
2017-10-30 07:30 | 55.73 | 55.12
2017-10-30 08:00 | 61.02 | 59.88
2017-10-30 08:30 | 64.38 | 62.75
2017-10-30 09:00 | 65.9 | 64.38
2017-10-30 09:30 | 67 | 65.57
2017-10-30 10:00 | 66.16 | 64.73
2017-10-30 10:30 | 66.61 | 65.27
2017-10-30 11:00 | 67.27 | 65.97
2017-10-30 11:30 | 67.78 | 66.51
2017-10-30 12:00 | 67.66 | 66.41
2017-10-30 12:30 | 68.8 | 67.57
2017-10-30 13:00 | 69.52 | 68.29
2017-10-30 13:30 | 69.85 | 68.66
2017-10-30 14:00 | 70.95 | 69.82
2017-10-30 14:30 | 71.7 | 70.58
2017-10-30 15:00 | 71.87 | 70.72
2017-10-30 15:30 | 73.88 | 72.72
2017-10-30 16:00 | 72.79 | 71.53
2017-10-30 16:30 | 70.33 | 68.91
2017-10-30 17:00 | 67.46 | 65.84
2017-10-30 17:30 | 65 | 63.16
2017-10-30 18:00 | 63.37 | 61.32
2017-10-30 18:30 | 64.1 | 62.03
2017-10-30 19:00 | 63.75 | 61.64
2017-10-30 19:30 | 62.24 | 60.01
2017-10-30 20:00 | 60.26 | 57.75
2017-10-30 20:30 | 58.07 | 55.04
2017-10-30 21:00 | 56.52 | 53.11
2017-10-30 21:30 | 63.37 | 48.85
2017-10-30 22:00 | 62.1 | 46.95
2017-10-30 22:30 | 60.31 | 44.32
2017-10-30 23:00 | 56.68 | 42.77
2017-10-30 23:30 | 54.45 | 39.76
2017-10-31 | 53.36 | 38.07
2017-10-31 00:30 | 52.34 | 36.45
2017-10-31 01:00 | 51.96 | 35.76
2017-10-31 01:30 | 51.21 | 35.48
2017-10-31 02:00 | 50.67 | 34.8
2017-10-31 02:30 | 49.89 | 33.53
2017-10-31 03:00 | 49.49 | 32.88
2017-10-31 03:30 | 49.44 | 33.18
2017-10-31 04:00 | 49.18 | 33.52
2017-10-31 04:30 | 49.04 | 33.4
2017-10-31 05:00 | 46.75 | 34.65
2017-10-31 05:30 | 39.52 | 37.38
2017-10-31 06:00 | 42.11 | 40.18
2017-10-31 06:30 | 46.88 | 45.31
2017-10-31 07:00 | 51.82 | 50.41
2017-10-31 07:30 | 57.87 | 56.64
2017-10-31 08:00 | 61.72 | 60.11
2017-10-31 08:30 | 63.7 | 62.18
2017-10-31 09:00 | 64.92 | 63.33
2017-10-31 09:30 | 66.17 | 64.35
2017-10-31 10:00 | 67.42 | 65.45
2017-10-31 10:30 | 67.8 | 66.61
2017-10-31 11:00 | 67.75 | 67.73
2017-10-31 11:30 | 68.13 | 68.12
2017-10-31 12:00 | 68.92 | 68.9
2017-10-31 12:30 | 71.56 | 71.54
2017-10-31 13:00 | 72.8 | 72.79
2017-10-31 13:30 | 73.45 | 73.43
2017-10-31 14:00 | 71.3 | 71.28
2017-10-31 14:30 | 72.78 | 72.77
2017-10-31 15:00 | 75.61 | 75.6
2017-10-31 15:30 | 73.77 | 73.74
2017-10-31 16:00 | 72.08 | 71.95
2017-10-31 16:30 | 69.89 | 69.55
2017-10-31 17:00 | 66.66 | 66.03
2017-10-31 17:30 | 62.49 | 61.16
2017-10-31 18:00 | 62.47 | 60.72
2017-10-31 18:30 | 37.33 | 36.16
2017-10-31 19:00 | 12.44 | 12.27
2017-10-31 19:30 | 59.4 | 58.78
2017-10-31 20:00 | 52.46 | 52.03
2017-10-31 20:30 | 49.66 | 49.33
2017-10-31 21:00 | 47.78 | 47.5
2017-10-31 21:30 | 45.38 | 45.2
2017-10-31 22:00 | 42.2 | 42.12
2017-10-31 22:30 | 39.62 | 39.58
2017-10-31 23:00 | 37.41 | 37.39
2017-10-31 23:30 | 36.1 | 36.08
2017-11-01 | 34.11 | 34.09
2017-11-01 00:30 | 32.31 | 32.29
2017-11-01 01:00 | 31.4 | 31.38
2017-11-01 01:30 | 32.25 | 32.02
2017-11-01 02:00 | 31.7 | 31.47
2017-11-01 02:30 | 31.02 | 30.84
2017-11-01 03:00 | 30.36 | 30.22
2017-11-01 03:30 | 29.91 | 29.77
2017-11-01 04:00 | 30.97 | 30.83
2017-11-01 04:30 | 30.7 | 30.51
2017-11-01 05:00 | 31.66 | 31.42
2017-11-01 05:30 | 33.61 | 33.29
2017-11-01 06:00 | 36.6 | 36.17
2017-11-01 06:30 | 42.32 | 41.41
2017-11-01 07:00 | 47.32 | 46.27
2017-11-01 07:30 | 52.12 | 51.69
2017-11-01 08:00 | 56.59 | 55.72
2017-11-01 08:30 | 56.45 | 55.76
2017-11-01 09:00 | 57.72 | 56.86
2017-11-01 09:30 | 58.77 | 58.59
2017-11-01 10:00 | 58.8 | 58.79
2017-11-01 10:30 | 59.07 | 59.05
2017-11-01 11:00 | 58.75 | 58.73
2017-11-01 11:30 | 59.43 | 59.42
2017-11-01 12:00 | 62.17 | 62.14
2017-11-01 12:30 | 60.36 | 60.34
2017-11-01 13:00 | 60.44 | 60.42
2017-11-01 13:30 | 60.19 | 60.17
2017-11-01 14:00 | 61.18 | 61.15
2017-11-01 14:30 | 62.61 | 62.57
2017-11-01 15:00 | 63.24 | 63.19
2017-11-01 15:30 | 63.76 | 63.64
2017-11-01 16:00 | 65.76 | 65.59
2017-11-01 16:30 | 65.82 | 65.47
2017-11-01 17:00 | 63.8 | 63.22
2017-11-01 17:30 | 61.65 | 60.51
2017-11-01 18:00 | 60.49 | 58.74
2017-11-01 18:30 | 61.17 | 59.18
2017-11-01 19:00 | 62.7 | 60.78
2017-11-01 19:30 | 61.12 | 58.95
2017-11-01 20:00 | 58.84 | 56.41
2017-11-01 20:30 | 56.71 | 53.9
2017-11-01 21:00 | 54.33 | 50.97
2017-11-01 21:30 | 52.32 | 48.35
2017-11-01 22:00 | 47.24 | 45.89
2017-11-01 22:30 | 43.38 | 43.16
2017-11-01 23:00 | 42.84 | 42.53
2017-11-01 23:30 | 38.94 | 38.5
2017-11-02 | 37.18 | 36.6
2017-11-02 00:30 | 35.95 | 35.21
2017-11-02 01:00 | 34.46 | 33.6
2017-11-02 01:30 | 33.87 | 32.95
2017-11-02 02:00 | 33.44 | 32.37
2017-11-02 02:30 | 32.78 | 32.4
2017-11-02 03:00 | 32.15 | 32.07
2017-11-02 03:30 | 31.14 | 31.12
2017-11-02 04:00 | 31.88 | 31.87
2017-11-02 04:30 | 32.77 | 32.76
2017-11-02 05:00 | 33.23 | 33.22
2017-11-02 05:30 | 35.01 | 35
2017-11-02 06:00 | 38.29 | 38.23
2017-11-02 06:30 | 43.83 | 43.45
2017-11-02 07:00 | 48.61 | 48.32
2017-11-02 07:30 | 55.38 | 54.74
2017-11-02 08:00 | 57.89 | 57.36
2017-11-02 08:30 | 61.89 | 61.39
2017-11-02 09:00 | 62.5 | 62.34
2017-11-02 09:30 | 62.9 | 62.81
2017-11-02 10:00 | 63.76 | 63.69
2017-11-02 10:30 | 63.51 | 63.48
2017-11-02 11:00 | 61.24 | 61.21
2017-11-02 11:30 | 64.27 | 64.25
2017-11-02 12:00 | 65.41 | 65.4
2017-11-02 12:30 | 64.94 | 64.92
2017-11-02 13:00 | 64.66 | 64.64
2017-11-02 13:30 | 65.37 | 65.35
2017-11-02 14:00 | 65.74 | 65.72
2017-11-02 14:30 | 65.89 | 65.87
2017-11-02 15:00 | 65.83 | 65.79
2017-11-02 15:30 | 66.26 | 66.18
2017-11-02 16:00 | 65.93 | 65.74
2017-11-02 16:30 | 66.78 | 66.39
2017-11-02 17:00 | 63.95 | 63.36
2017-11-02 17:30 | 62.1 | 60.93
2017-11-02 18:00 | 62.65 | 61.06
2017-11-02 18:30 | 62.63 | 60.84
2017-11-02 19:00 | 62.96 | 61.28
2017-11-02 19:30 | 61.09 | 59.15
2017-11-02 20:00 | 59.65 | 57.54
2017-11-02 20:30 | 57.68 | 55.11
2017-11-02 21:00 | 56.01 | 53.13
2017-11-02 21:30 | 52.88 | 50.2
2017-11-02 22:00 | 46.59 | 46.46
2017-11-02 22:30 | 44.42 | 44.2
2017-11-02 23:00 | 44.17 | 43.91
2017-11-02 23:30 | 40.68 | 40.33
2017-11-03 | 38.14 | 37.68
2017-11-03 00:30 | 37.65 | 37.02
2017-11-03 01:00 | 35.64 | 34.92
2017-11-03 01:30 | 35.73 | 35.01
2017-11-03 02:00 | 34.94 | 34.15
2017-11-03 02:30 | 34.28 | 33.59
2017-11-03 03:00 | 33.92 | 33.67
2017-11-03 03:30 | 32.88 | 32.86
2017-11-03 04:00 | 31.86 | 31.85
2017-11-03 04:30 | 32.55 | 32.54
2017-11-03 05:00 | 33.69 | 33.68
2017-11-03 05:30 | 35.48 | 35.47
2017-11-03 06:00 | 38.42 | 38.34
2017-11-03 06:30 | 44.48 | 44.05
2017-11-03 07:00 | 48.55 | 48.27
2017-11-03 07:30 | 55.26 | 54.7
2017-11-03 08:00 | 57.46 | 57.17
2017-11-03 08:30 | 59.23 | 59.19
2017-11-03 09:00 | 60.73 | 60.59
2017-11-03 09:30 | 61.67 | 61.54
2017-11-03 10:00 | 61.52 | 61.41
2017-11-03 10:30 | 61.43 | 61.35
2017-11-03 11:00 | 61.7 | 61.66
2017-11-03 11:30 | 62.99 | 62.97
2017-11-03 12:00 | 63.31 | 63.3
2017-11-03 12:30 | 63 | 62.98
2017-11-03 13:00 | 62.69 | 62.65
2017-11-03 13:30 | 63 | 62.96
2017-11-03 14:00 | 61.72 | 61.66
2017-11-03 14:30 | 61.43 | 61.29
2017-11-03 15:00 | 61.52 | 61.34
2017-11-03 15:30 | 61.39 | 61.05
2017-11-03 16:00 | 61.39 | 60.89
2017-11-03 16:30 | 61.52 | 60.75
2017-11-03 17:00 | 60.41 | 59.39
2017-11-03 17:30 | 59.43 | 57.75
2017-11-03 18:00 | 58.17 | 55.78
2017-11-03 18:30 | 57.12 | 54.31
2017-11-03 19:00 | 57.41 | 54.57
2017-11-03 19:30 | 56.02 | 52.92
2017-11-03 20:00 | 54.57 | 51.23
2017-11-03 20:30 | 49.73 | 48.69
2017-11-03 21:00 | 46.86 | 46.73
2017-11-03 21:30 | 45.22 | 45.03
2017-11-03 22:00 | 43.12 | 42.83
2017-11-03 22:30 | 40.88 | 40.83
2017-11-03 23:00 | 40.81 | 40.73
2017-11-03 23:30 | 37.18 | 37.06
2017-11-04 | 34.98 | 34.78
2017-11-04 00:30 | 33.64 | 33.55
2017-11-04 01:00 | 32.12 | 31.95
2017-11-04 01:30 | 31.26 | 31.1
2017-11-04 02:00 | 30.46 | 30.32
2017-11-04 02:30 | 30.4 | 30.26
2017-11-04 03:00 | 29.8 | 29.68
2017-11-04 03:30 | 29.29 | 29.19
2017-11-04 04:00 | 28.85 | 28.76
2017-11-04 04:30 | 30.03 | 29.91
2017-11-04 05:00 | 30.95 | 30.82
2017-11-04 05:30 | 31.1 | 30.94
2017-11-04 06:00 | 31.95 | 31.78
2017-11-04 06:30 | 33.44 | 33.15
2017-11-04 07:00 | 35.51 | 35.06
2017-11-04 07:30 | 38.4 | 37.6
2017-11-04 08:00 | 40.86 | 40.35
2017-11-04 08:30 | 42.93 | 42.32
2017-11-04 09:00 | 44.78 | 43.96
2017-11-04 09:30 | 45.96 | 44.99
2017-11-04 10:00 | 45.67 | 44.6
2017-11-04 10:30 | 45.59 | 44.39
2017-11-04 11:00 | 46.36 | 45.03
2017-11-04 11:30 | 46.54 | 45.16
2017-11-04 12:00 | 46.09 | 44.78
2017-11-04 12:30 | 44.95 | 43.8
2017-11-04 13:00 | 44.53 | 43.51
2017-11-04 13:30 | 44.35 | 43.41
2017-11-04 14:00 | 44.78 | 43.94
2017-11-04 14:30 | 45.27 | 44.56
2017-11-04 15:00 | 44.91 | 44.22
2017-11-04 15:30 | 45.15 | 44.55
2017-11-04 16:00 | 46.44 | 45.96
2017-11-04 16:30 | 48.68 | 48.3
2017-11-04 17:00 | 47.69 | 47.42
2017-11-04 17:30 | 48.08 | 47.86
2017-11-04 18:00 | 48.19 | 48.02
2017-11-04 18:30 | 48.09 | 47.93
2017-11-04 19:00 | 49.45 | 49.22
2017-11-04 19:30 | 48.07 | 47.85
2017-11-04 20:00 | 46.28 | 46.08
2017-11-04 20:30 | 44.62 | 44.46
2017-11-04 21:00 | 43.26 | 43.13
2017-11-04 21:30 | 41.94 | 41.85
2017-11-04 22:00 | 40.68 | 40.64
2017-11-04 22:30 | 38.7 | 38.68
2017-11-04 23:00 | 38.96 | 38.95
2017-11-04 23:30 | 35.28 | 35.26
2017-11-05 | 33.09 | 33.08
2017-11-05 00:30 | 32.25 | 32.22
2017-11-05 01:00 | 30.95 | 30.9
2017-11-05 01:30 | 30.4 | 30.35
2017-11-05 02:00 | 29.78 | 29.71
2017-11-05 02:30 | 29.47 | 29.38
2017-11-05 03:00 | 29.06 | 28.97
2017-11-05 03:30 | 29.16 | 29.1
2017-11-05 04:00 | 28.92 | 28.87
2017-11-05 04:30 | 28.52 | 28.46
2017-11-05 05:00 | 28.59 | 28.52
2017-11-05 05:30 | 28.54 | 28.5
2017-11-05 06:00 | 28.36 | 28.33
2017-11-05 06:30 | 29.27 | 29.23
2017-11-05 07:00 | 29.72 | 29.64
2017-11-05 07:30 | 31.79 | 31.59
2017-11-05 08:00 | 32.99 | 32.68
2017-11-05 08:30 | 35.37 | 34.88
2017-11-05 09:00 | 36.71 | 36.49
2017-11-05 09:30 | 37.24 | 37.07
2017-11-05 10:00 | 37.38 | 37.14
2017-11-05 10:30 | 37.99 | 37.71
2017-11-05 11:00 | 37.27 | 36.96
2017-11-05 11:30 | 37.34 | 36.98
2017-11-05 12:00 | 38.45 | 38.07
2017-11-05 12:30 | 38.22 | 37.88
2017-11-05 13:00 | 39.46 | 39.08
2017-11-05 13:30 | 39.86 | 39.44
2017-11-05 14:00 | 40.78 | 40.4
2017-11-05 14:30 | 41.3 | 40.95
2017-11-05 15:00 | 42.3 | 41.97
2017-11-05 15:30 | 43.36 | 43.07
2017-11-05 16:00 | 42.52 | 42.19
2017-11-05 16:30 | 46.02 | 45.82
2017-11-05 17:00 | 45.86 | 45.67
2017-11-05 17:30 | 47.44 | 47.28
2017-11-05 18:00 | 48.25 | 48.13
2017-11-05 18:30 | 49.48 | 49.36
2017-11-05 19:00 | 51.54 | 51.35
2017-11-05 19:30 | 50.17 | 49.98
2017-11-05 20:00 | 48.42 | 48.26
2017-11-05 20:30 | 46.18 | 46.08
2017-11-05 21:00 | 44.76 | 44.66
2017-11-05 21:30 | 42.45 | 42.39
2017-11-05 22:00 | 40.59 | 40.57
2017-11-05 22:30 | 39.04 | 39.02
2017-11-05 23:00 | 39.18 | 39.17
2017-11-05 23:30 | 35.25 | 35.23
2017-11-06 | 33.61 | 33.59
2017-11-06 00:30 | 33.38 | 33.37
2017-11-06 01:00 | 32.03 | 32
2017-11-06 01:30 | 31.45 | 31.41
2017-11-06 02:00 | 31.55 | 31.5
2017-11-06 02:30 | 31.09 | 31.05
2017-11-06 03:00 | 30.74 | 30.69
2017-11-06 03:30 | 30.94 | 30.9
2017-11-06 04:00 | 31.01 | 30.98
2017-11-06 04:30 | 32.22 | 32.2
2017-11-06 05:00 | 28.55 | 28.51
2017-11-06 05:30 | 35.29 | 35.27
2017-11-06 06:00 | 38.83 | 38.79
2017-11-06 06:30 | 43.79 | 43.48
2017-11-06 07:00 | 49.6 | 49.02
2017-11-06 07:30 | 57.47 | 56.74
2017-11-06 08:00 | 60.35 | 59.73
2017-11-06 08:30 | 62.61 | 61.65
2017-11-06 09:00 | 64.69 | 63.18
2017-11-06 09:30 | 65.45 | 63.81
2017-11-06 10:00 | 65.64 | 63.94
2017-11-06 10:30 | 65.51 | 63.71
2017-11-06 11:00 | 66.23 | 64.3
2017-11-06 11:30 | 67.42 | 65.34
2017-11-06 12:00 | 66.84 | 64.78
2017-11-06 12:30 | 69.08 | 66.91
2017-11-06 13:00 | 68.26 | 66.19
2017-11-06 13:30 | 68.84 | 66.78
2017-11-06 14:00 | 69.76 | 67.68
2017-11-06 14:30 | 66.6 | 64.37
2017-11-06 15:00 | 66.04 | 63.93
2017-11-06 15:30 | 67.57 | 65.87
2017-11-06 16:00 | 67.41 | 65.99
2017-11-06 16:30 | 66.85 | 65.84
2017-11-06 17:00 | 64.78 | 64.08
2017-11-06 17:30 | 61.95 | 61.66
2017-11-06 18:00 | 59.02 | 58.96
2017-11-06 18:30 | 58.96 | 58.94
2017-11-06 19:00 | 59.87 | 59.86
2017-11-06 19:30 | 57.82 | 57.81
2017-11-06 20:00 | 55.26 | 55.23
2017-11-06 20:30 | 53.08 | 52.98
2017-11-06 21:00 | 50.58 | 50.52
2017-11-06 21:30 | 48.19 | 48.15
2017-11-06 22:00 | 45.06 | 44.84
2017-11-06 22:30 | 43.25 | 43.11
2017-11-06 23:00 | 42.62 | 42.52
2017-11-06 23:30 | 38.71 | 38.64
2017-11-07 | 36.09 | 36.06
2017-11-07 00:30 | 35.26 | 35.26
2017-11-07 01:00 | 34.49 | 34.49
2017-11-07 01:30 | 32.82 | 32.82
2017-11-07 02:00 | 32.01 | 32.01
2017-11-07 02:30 | 31.53 | 31.53
2017-11-07 03:00 | 31.31 | 31.29
2017-11-07 03:30 | 31.23 | 31.21
2017-11-07 04:00 | 31.09 | 31.07
2017-11-07 04:30 | 31.59 | 31.57
2017-11-07 05:00 | 32.64 | 32.62
2017-11-07 05:30 | 34.21 | 34.19
2017-11-07 06:00 | 36.42 | 36.39
2017-11-07 06:30 | 41.3 | 41.09
2017-11-07 07:00 | 46.54 | 46.32
2017-11-07 07:30 | 53.45 | 52.79
2017-11-07 08:00 | 58.28 | 57.55
2017-11-07 08:30 | 61.35 | 60.97
2017-11-07 09:00 | 62.5 | 62.27
2017-11-07 09:30 | 61.67 | 61.51
2017-11-07 10:00 | 62.07 | 61.97
2017-11-07 10:30 | 63.36 | 63.31
2017-11-07 11:00 | 63.52 | 63.51
2017-11-07 11:30 | 64.26 | 64.25
2017-11-07 12:00 | 64.85 | 64.84
2017-11-07 12:30 | 65.44 | 65.43
2017-11-07 13:00 | 67.04 | 67.03
2017-11-07 13:30 | 66.14 | 66.13
2017-11-07 14:00 | 67.17 | 67.16
2017-11-07 14:30 | 67.54 | 67.53
2017-11-07 15:00 | 68.27 | 68.26
2017-11-07 15:30 | 68.11 | 68.09
2017-11-07 16:00 | 68.61 | 68.52
2017-11-07 16:30 | 68.83 | 68.66
2017-11-07 17:00 | 67.24 | 66.86
2017-11-07 17:30 | 64.58 | 63.67
2017-11-07 18:00 | 60.91 | 59.99
2017-11-07 18:30 | 55.77 | 54.77
2017-11-07 19:00 | 61.7 | 60.72
2017-11-07 19:30 | 59.93 | 58.85
2017-11-07 20:00 | 57.86 | 56.52
2017-11-07 20:30 | 55.27 | 53.54
2017-11-07 21:00 | 53.36 | 51.38
2017-11-07 21:30 | 51.84 | 49.49
2017-11-07 22:00 | 46.3 | 46.23
2017-11-07 22:30 | 45.11 | 45.1
2017-11-07 23:00 | 44.02 | 44.01
2017-11-07 23:30 | 40.22 | 40.21
2017-11-08 | 38.2 | 38.18
2017-11-08 00:30 | 37.65 | 37.61
2017-11-08 01:00 | 36.88 | 36.78
2017-11-08 01:30 | 36.71 | 36.6
2017-11-08 02:00 | 35.8 | 35.66
2017-11-08 02:30 | 34.41 | 34.2
2017-11-08 03:00 | 34.17 | 33.92
2017-11-08 03:30 | 34.25 | 34.2
2017-11-08 04:00 | 34.45 | 34.44
2017-11-08 04:30 | 34.7 | 34.69
2017-11-08 05:00 | 35.94 | 35.91
2017-11-08 05:30 | 38.23 | 38.18
2017-11-08 06:00 | 40.39 | 40.25
2017-11-08 06:30 | 46.54 | 46.02
2017-11-08 07:00 | 51.3 | 50.89
2017-11-08 07:30 | 57.69 | 56.73
2017-11-08 08:00 | 62.03 | 61.41
2017-11-08 08:30 | 63.72 | 63.48
2017-11-08 09:00 | 66.04 | 65.96
2017-11-08 09:30 | 65.52 | 65.49
2017-11-08 10:00 | 64.52 | 64.51
2017-11-08 10:30 | 65.85 | 65.84
2017-11-08 11:00 | 66.34 | 66.33
2017-11-08 11:30 | 65.83 | 65.82
2017-11-08 12:00 | 66.53 | 66.52
2017-11-08 12:30 | 66.46 | 66.45
2017-11-08 13:00 | 66.57 | 66.56
2017-11-08 13:30 | 67.86 | 67.85
2017-11-08 14:00 | 67.85 | 67.85
2017-11-08 14:30 | 68.42 | 68.41
2017-11-08 15:00 | 67.95 | 67.94
2017-11-08 15:30 | 67.01 | 66.97
2017-11-08 16:00 | 67.1 | 67.01
2017-11-08 16:30 | 68.12 | 67.91
2017-11-08 17:00 | 66.56 | 66.15
2017-11-08 17:30 | 65.62 | 64.69
2017-11-08 18:00 | 61.43 | 61.04
2017-11-08 18:30 | 61.84 | 61.53
2017-11-08 19:00 | 62.79 | 62.48
2017-11-08 19:30 | 60.84 | 60.43
2017-11-08 20:00 | 58.8 | 58.29
2017-11-08 20:30 | 56.69 | 55.98
2017-11-08 21:00 | 54.62 | 53.72
2017-11-08 21:30 | 51.93 | 50.77
2017-11-08 22:00 | 49.15 | 47.63
2017-11-08 22:30 | 47.09 | 45.28
2017-11-08 23:00 | 46.52 | 44.56
2017-11-08 23:30 | 42.9 | 40.51
2017-11-09 | 41.11 | 38.32
2017-11-09 00:30 | 41.72 | 38.86
2017-11-09 01:00 | 40.69 | 37.45
2017-11-09 01:30 | 38.82 | 35.32
2017-11-09 02:00 | 38.49 | 34.79
2017-11-09 02:30 | 38.07 | 33.92
2017-11-09 03:00 | 37.75 | 33.38
2017-11-09 03:30 | 37.69 | 33.25
2017-11-09 04:00 | 37.42 | 33
2017-11-09 04:30 | 38.49 | 34.22
2017-11-09 05:00 | 39.11 | 35.11
2017-11-09 05:30 | 40.56 | 37.47
2017-11-09 06:00 | 42.3 | 39.88
2017-11-09 06:30 | 46.86 | 45.54
2017-11-09 07:00 | 51.79 | 50.5
2017-11-09 07:30 | 57.45 | 56.46
2017-11-09 08:00 | 59.76 | 58.89
2017-11-09 08:30 | 61.96 | 61.47
2017-11-09 09:00 | 60.85 | 60.46
2017-11-09 09:30 | 60.61 | 60.3
2017-11-09 10:00 | 60.32 | 60.01
2017-11-09 10:30 | 60.58 | 60.35
2017-11-09 11:00 | 61.18 | 60.96
2017-11-09 11:30 | 58.45 | 58.22
2017-11-09 12:00 | 62.66 | 62.47
2017-11-09 12:30 | 63.54 | 63.31
2017-11-09 13:00 | 59.48 | 59.19
2017-11-09 13:30 | 58.65 | 58.39
2017-11-09 14:00 | 57.62 | 57.37
2017-11-09 14:30 | 60.84 | 60.63
2017-11-09 15:00 | 59.86 | 59.54
2017-11-09 15:30 | 60.23 | 59.74
2017-11-09 16:00 | 60.72 | 60.12
2017-11-09 16:30 | 60.82 | 59.94
2017-11-09 17:00 | 59.3 | 57.9
2017-11-09 17:30 | 58.07 | 55.9
2017-11-09 18:00 | 58.57 | 55.98
2017-11-09 18:30 | 57.81 | 55.9
2017-11-09 19:00 | 58.69 | 57.18
2017-11-09 19:30 | 57.2 | 55.53
2017-11-09 20:00 | 55.34 | 53.79
2017-11-09 20:30 | 52.17 | 51.32
2017-11-09 21:00 | 49.88 | 49.51
2017-11-09 21:30 | 46.94 | 46.65
2017-11-09 22:00 | 44.21 | 44.02
2017-11-09 22:30 | 42.67 | 42.53
2017-11-09 23:00 | 42.37 | 42.26
2017-11-09 23:30 | 38.14 | 38.1
2017-11-10 | 35.89 | 35.87
2017-11-10 00:30 | 35.24 | 35.22
2017-11-10 01:00 | 33.75 | 33.73
2017-11-10 01:30 | 33.16 | 33.07
2017-11-10 02:00 | 32.79 | 32.48
2017-11-10 02:30 | 32.35 | 32.09
2017-11-10 03:00 | 32.18 | 31.93
2017-11-10 03:30 | 32.19 | 31.96
2017-11-10 04:00 | 32.44 | 32.21
2017-11-10 04:30 | 33.35 | 33.09
2017-11-10 05:00 | 34.85 | 34.5
2017-11-10 05:30 | 36.66 | 36.22
2017-11-10 06:00 | 39.64 | 39.05
2017-11-10 06:30 | 45.65 | 44.54
2017-11-10 07:00 | 50.07 | 49.59
2017-11-10 07:30 | 54.07 | 53.93
2017-11-10 08:00 | 55.58 | 55.35
2017-11-10 08:30 | 58.05 | 57.69
2017-11-10 09:00 | 59.14 | 58.72
2017-11-10 09:30 | 58.24 | 57.76
2017-11-10 10:00 | 57.37 | 56.77
2017-11-10 10:30 | 57.88 | 56.97
2017-11-10 11:00 | 57.34 | 56.3
2017-11-10 11:30 | 56.86 | 55.74
2017-11-10 12:00 | 58.14 | 56.97
2017-11-10 12:30 | 58.73 | 57.55
2017-11-10 13:00 | 59.14 | 58.05
2017-11-10 13:30 | 59.33 | 58.41
2017-11-10 14:00 | 56.43 | 55.52
2017-11-10 14:30 | 57.87 | 57.09
2017-11-10 15:00 | 56.19 | 55.47
2017-11-10 15:30 | 54.73 | 54.19
2017-11-10 16:00 | 54.86 | 54.46
2017-11-10 16:30 | 55.99 | 55.75
2017-11-10 17:00 | 54.21 | 54.12
2017-11-10 17:30 | 51.99 | 51.97
2017-11-10 18:00 | 51 | 50.97
2017-11-10 18:30 | 50.33 | 50.26
2017-11-10 19:00 | 52.38 | 52.36
2017-11-10 19:30 | 51.11 | 51.08
2017-11-10 20:00 | 49.4 | 49.36
2017-11-10 20:30 | 47.7 | 47.62
2017-11-10 21:00 | 46.28 | 46.16
2017-11-10 21:30 | 44.66 | 44.45
2017-11-10 22:00 | 42.53 | 42.19
2017-11-10 22:30 | 41.59 | 41.17
2017-11-10 23:00 | 41.74 | 41.24
2017-11-10 23:30 | 38.38 | 37.68
2017-11-11 | 35.9 | 35.4
2017-11-11 00:30 | 34.42 | 34.41
2017-11-11 01:00 | 33.47 | 33.46
2017-11-11 01:30 | 32.43 | 32.42
2017-11-11 02:00 | 31.99 | 31.97
2017-11-11 02:30 | 31.86 | 31.82
2017-11-11 03:00 | 31.82 | 31.64
2017-11-11 03:30 | 31.29 | 31.11
2017-11-11 04:00 | 31.22 | 31.07
2017-11-11 04:30 | 31.6 | 31.41
2017-11-11 05:00 | 32.64 | 32.41
2017-11-11 05:30 | 33.04 | 32.79
2017-11-11 06:00 | 33.22 | 32.98
2017-11-11 06:30 | 34.83 | 34.48
2017-11-11 07:00 | 37.65 | 37.09
2017-11-11 07:30 | 40.89 | 40.1
2017-11-11 08:00 | 42.47 | 41.51
2017-11-11 08:30 | 41.73 | 40.47
2017-11-11 09:00 | 42.92 | 42.25
2017-11-11 09:30 | 43.21 | 42.54
2017-11-11 10:00 | 42.45 | 41.68
2017-11-11 10:30 | 42.63 | 41.7
2017-11-11 11:00 | 43.27 | 42.32
2017-11-11 11:30 | 42.51 | 41.55
2017-11-11 12:00 | 42.55 | 41.66
2017-11-11 12:30 | 41.31 | 40.56
2017-11-11 13:00 | 40.35 | 39.68
2017-11-11 13:30 | 39.53 | 38.91
2017-11-11 14:00 | 38.25 | 37.64
2017-11-11 14:30 | 38.4 | 37.87
2017-11-11 15:00 | 38.86 | 38.36
2017-11-11 15:30 | 38.8 | 38.37
2017-11-11 16:00 | 40.42 | 40.11
2017-11-11 16:30 | 42.41 | 42.2
2017-11-11 17:00 | 42.08 | 41.92
2017-11-11 17:30 | 42.96 | 42.84
2017-11-11 18:00 | 43.95 | 43.86
2017-11-11 18:30 | 44.75 | 44.68
2017-11-11 19:00 | 46.6 | 46.47
2017-11-11 19:30 | 44.6 | 44.49
2017-11-11 20:00 | 42.88 | 42.77
2017-11-11 20:30 | 41.42 | 41.34
2017-11-11 21:00 | 40.43 | 40.38
2017-11-11 21:30 | 39.06 | 39.02
2017-11-11 22:00 | 37.81 | 37.79
2017-11-11 22:30 | 37.03 | 37.01
2017-11-11 23:00 | 38.8 | 38.79
2017-11-11 23:30 | 34.18 | 34.16
2017-11-12 | 31.93 | 31.9
2017-11-12 00:30 | 31.44 | 31.4
2017-11-12 01:00 | 29.87 | 29.79
2017-11-12 01:30 | 30.14 | 30.07
2017-11-12 02:00 | 29.49 | 29.42
2017-11-12 02:30 | 29.37 | 29.3
2017-11-12 03:00 | 28.72 | 28.65
2017-11-12 03:30 | 28.14 | 28.08
2017-11-12 04:00 | 28.22 | 28.17
2017-11-12 04:30 | 28.93 | 28.86
2017-11-12 05:00 | 28.85 | 28.77
2017-11-12 05:30 | 29.41 | 29.36
2017-11-12 06:00 | 28.64 | 28.62
2017-11-12 06:30 | 29.87 | 29.8
2017-11-12 07:00 | 31.12 | 31.01
2017-11-12 07:30 | 33.32 | 33.18
2017-11-12 08:00 | 35.52 | 35.32
2017-11-12 08:30 | 37.26 | 37.03
2017-11-12 09:00 | 38.9 | 38.55
2017-11-12 09:30 | 38.05 | 37.58
2017-11-12 10:00 | 36.72 | 36.11
2017-11-12 10:30 | 36.65 | 36.28
2017-11-12 11:00 | 36.7 | 36.48
2017-11-12 11:30 | 37.28 | 37.06
2017-11-12 12:00 | 38.94 | 38.76
2017-11-12 12:30 | 39.44 | 39.34
2017-11-12 13:00 | 40.08 | 40
2017-11-12 13:30 | 38 | 37.87
2017-11-12 14:00 | 37.57 | 37.45
2017-11-12 14:30 | 36.16 | 36.02
2017-11-12 15:00 | 35.71 | 35.57
2017-11-12 15:30 | 37.42 | 37.33
2017-11-12 16:00 | 36.58 | 36.52
2017-11-12 16:30 | 39.48 | 39.45
2017-11-12 17:00 | 39.99 | 39.96
2017-11-12 17:30 | 42.38 | 42.36
2017-11-12 18:00 | 42.7 | 42.68
2017-11-12 18:30 | 45.12 | 45.1
2017-11-12 19:00 | 46.17 | 46.12
2017-11-12 19:30 | 44.96 | 44.91
2017-11-12 20:00 | 43.75 | 43.72
2017-11-12 20:30 | 42.38 | 42.36
2017-11-12 21:00 | 39.86 | 39.85
2017-11-12 21:30 | 39.02 | 39.01
2017-11-12 22:00 | 37.31 | 37.3
2017-11-12 22:30 | 36.72 | 36.7
2017-11-12 23:00 | 36.83 | 36.82
2017-11-12 23:30 | 32.88 | 32.85
2017-11-13 | 30.54 | 30.47
2017-11-13 00:30 | 30.93 | 30.87
2017-11-13 01:00 | 29.49 | 29.44
2017-11-13 01:30 | 29.32 | 29.27
2017-11-13 02:00 | 29.16 | 29.11
2017-11-13 02:30 | 29.29 | 29.24
2017-11-13 03:00 | 27.95 | 27.9
2017-11-13 03:30 | 28.09 | 28.05
2017-11-13 04:00 | 28.6 | 28.54
2017-11-13 04:30 | 29.68 | 29.59
2017-11-13 05:00 | 30.62 | 30.5
2017-11-13 05:30 | 32.5 | 32.33
2017-11-13 06:00 | 35.6 | 35.28
2017-11-13 06:30 | 41.06 | 40.35
2017-11-13 07:00 | 46.31 | 45.05
2017-11-13 07:30 | 51.55 | 51.02
2017-11-13 08:00 | 55.65 | 54.89
2017-11-13 08:30 | 56.96 | 56.06
2017-11-13 09:00 | 55.81 | 55.18
2017-11-13 09:30 | 57.65 | 57.19
2017-11-13 10:00 | 57.19 | 56.79
2017-11-13 10:30 | 57.83 | 57.5
2017-11-13 11:00 | 59.79 | 59.48
2017-11-13 11:30 | 57.76 | 57.51
2017-11-13 12:00 | 53.41 | 53.24
2017-11-13 12:30 | 61.29 | 61.04
2017-11-13 13:00 | 62.79 | 62.34
2017-11-13 13:30 | 60.53 | 59.89
2017-11-13 14:00 | 59.42 | 58.84
2017-11-13 14:30 | 60.46 | 59.88
2017-11-13 15:00 | 59.87 | 59.32
2017-11-13 15:30 | 59.85 | 59.12
2017-11-13 16:00 | 58.38 | 57.31
2017-11-13 16:30 | 58.12 | 56.72
2017-11-13 17:00 | 57.69 | 55.81
2017-11-13 17:30 | 57.19 | 54.32
2017-11-13 18:00 | 57.4 | 54.16
2017-11-13 18:30 | 57.26 | 54.15
2017-11-13 19:00 | 57.32 | 54.27
2017-11-13 19:30 | 55.49 | 52.22
2017-11-13 20:00 | 50.64 | 50.53
2017-11-13 20:30 | 47.98 | 47.88
2017-11-13 21:00 | 46.62 | 46.49
2017-11-13 21:30 | 44.59 | 44.4
2017-11-13 22:00 | 41.83 | 41.46
2017-11-13 22:30 | 40.58 | 40.12
2017-11-13 23:00 | 41.04 | 40.56
2017-11-13 23:30 | 37.18 | 36.46
2017-11-14 | 34.45 | 34
2017-11-14 00:30 | 33.63 | 33.39
2017-11-14 01:00 | 32.87 | 32.63
2017-11-14 01:30 | 32.45 | 32.21
2017-11-14 02:00 | 31.87 | 31.56
2017-11-14 02:30 | 30.79 | 30.76
2017-11-14 03:00 | 30.56 | 30.41
2017-11-14 03:30 | 30.57 | 30.42
2017-11-14 04:00 | 30.78 | 30.64
2017-11-14 04:30 | 31.32 | 31.17
2017-11-14 05:00 | 32.18 | 32
2017-11-14 05:30 | 34.39 | 34.09
2017-11-14 06:00 | 36.88 | 36.44
2017-11-14 06:30 | 42.1 | 41.22
2017-11-14 07:00 | 46.6 | 45.55
2017-11-14 07:30 | 51.98 | 51.23
2017-11-14 08:00 | 53.7 | 53.31
2017-11-14 08:30 | 57.34 | 56.83
2017-11-14 09:00 | 57.6 | 56.87
2017-11-14 09:30 | 48.7 | 47.26
2017-11-14 10:00 | 57.53 | 56.73
2017-11-14 10:30 | 59.04 | 57.85
2017-11-14 11:00 | 59.42 | 57.98
2017-11-14 11:30 | 59.64 | 58.21
2017-11-14 12:00 | 59.95 | 59.66
2017-11-14 12:30 | 59.7 | 59.54
2017-11-14 13:00 | 57.99 | 57.79
2017-11-14 13:30 | 58.61 | 58.45
2017-11-14 14:00 | 58.54 | 58.4
2017-11-14 14:30 | 58.68 | 58.51
2017-11-14 15:00 | 59.57 | 59.38
2017-11-14 15:30 | 61.06 | 60.8
2017-11-14 16:00 | 60.74 | 60.26
2017-11-14 16:30 | 60.24 | 59.35
2017-11-14 17:00 | 58.29 | 57
2017-11-14 17:30 | 57.22 | 55.16
2017-11-14 18:00 | 57.31 | 54.73
2017-11-14 18:30 | 57 | 53.75
2017-11-14 19:00 | 58.76 | 55.78
2017-11-14 19:30 | 56.08 | 52.67
2017-11-14 20:00 | 53.96 | 50.04
2017-11-14 20:30 | 52.57 | 48.17
2017-11-14 21:00 | 48.1 | 46.56
2017-11-14 21:30 | 45.13 | 44.86
2017-11-14 22:00 | 39.84 | 39.5
2017-11-14 22:30 | 41.96 | 41.51
2017-11-14 23:00 | 42.07 | 41.54
2017-11-14 23:30 | 36.88 | 36.13
2017-11-15 | 34.77 | 33.83
2017-11-15 00:30 | 35.67 | 34.63
2017-11-15 01:00 | 33.43 | 32.69
2017-11-15 01:30 | 32.08 | 31.75
2017-11-15 02:00 | 32.03 | 31.67
2017-11-15 02:30 | 31.35 | 31.06
2017-11-15 03:00 | 31 | 30.87
2017-11-15 03:30 | 30.37 | 30.21
2017-11-15 04:00 | 30.45 | 30.3
2017-11-15 04:30 | 32.01 | 31.81
2017-11-15 05:00 | 33.1 | 32.84
2017-11-15 05:30 | 34.48 | 34.12
2017-11-15 06:00 | 38.21 | 37.69
2017-11-15 06:30 | 43.23 | 42.27
2017-11-15 07:00 | 47.28 | 46.59
2017-11-15 07:30 | 53.28 | 52.97
2017-11-15 08:00 | 56.01 | 55.65
2017-11-15 08:30 | 58.53 | 57.91
2017-11-15 09:00 | 58.6 | 57.88
2017-11-15 09:30 | 57.17 | 56.78
2017-11-15 10:00 | 57.09 | 56.73
2017-11-15 10:30 | 57.64 | 57.35
2017-11-15 11:00 | 58.27 | 58.06
2017-11-15 11:30 | 58.16 | 57.97
2017-11-15 12:00 | 58.68 | 58.53
2017-11-15 12:30 | 58.63 | 58.49
2017-11-15 13:00 | 57.69 | 57.56
2017-11-15 13:30 | 59.11 | 58.98
2017-11-15 14:00 | 60.5 | 60.4
2017-11-15 14:30 | 61.08 | 60.95
2017-11-15 15:00 | 59.65 | 59.49
2017-11-15 15:30 | 59.01 | 58.77
2017-11-15 16:00 | 58.92 | 58.52
2017-11-15 16:30 | 60.31 | 59.62
2017-11-15 17:00 | 58.67 | 57.67
2017-11-15 17:30 | 57.61 | 55.91
2017-11-15 18:00 | 56.94 | 54.5
2017-11-15 18:30 | 57.92 | 55.14
2017-11-15 19:00 | 59.96 | 57.57
2017-11-15 19:30 | 58.61 | 56.01
2017-11-15 20:00 | 56.44 | 53.38
2017-11-15 20:30 | 54.87 | 51.35
2017-11-15 21:00 | 53.12 | 49.1
2017-11-15 21:30 | 50.77 | 46.19
2017-11-15 22:00 | 45.35 | 43.98
2017-11-15 22:30 | 42.35 | 42.1
2017-11-15 23:00 | 42.6 | 42.3
2017-11-15 23:30 | 38.99 | 38.56
2017-11-16 | 36.47 | 35.89
2017-11-16 00:30 | 36.46 | 35.73
2017-11-16 01:00 | 35.3 | 34.49
2017-11-16 01:30 | 34.97 | 34.14
2017-11-16 02:00 | 33.79 | 32.86
2017-11-16 02:30 | 32.99 | 31.91
2017-11-16 03:00 | 31.43 | 31.3
2017-11-16 03:30 | 32.15 | 32.14
2017-11-16 04:00 | 31.6 | 31.58
2017-11-16 04:30 | 32.31 | 32.3
2017-11-16 05:00 | 33.26 | 33.25
2017-11-16 05:30 | 35.18 | 35.17
2017-11-16 06:00 | 38.9 | 38.8
2017-11-16 06:30 | 44.97 | 44.51
2017-11-16 07:00 | 49.88 | 48.85
2017-11-16 07:30 | 55.59 | 55.22
2017-11-16 08:00 | 58.32 | 57.76
2017-11-16 08:30 | 59.86 | 58.99
2017-11-16 09:00 | 60.91 | 59.72
2017-11-16 09:30 | 60.5 | 59.79
2017-11-16 10:00 | 59.93 | 59.75
2017-11-16 10:30 | 59.46 | 59.31
2017-11-16 11:00 | 59.89 | 59.8
2017-11-16 11:30 | 59.62 | 59.51
2017-11-16 12:00 | 61.07 | 60.99
2017-11-16 12:30 | 61.03 | 60.92
2017-11-16 13:00 | 60.36 | 60.26
2017-11-16 13:30 | 60.43 | 60.31
2017-11-16 14:00 | 61 | 60.89
2017-11-16 14:30 | 62.18 | 62.1
2017-11-16 15:00 | 62.71 | 62.62
2017-11-16 15:30 | 62.48 | 62.32
2017-11-16 16:00 | 62.04 | 61.69
2017-11-16 16:30 | 61.74 | 61.1
2017-11-16 17:00 | 60.38 | 59.48
2017-11-16 17:30 | 59.89 | 58.43
2017-11-16 18:00 | 58.81 | 56.61
2017-11-16 18:30 | 57.92 | 55.21
2017-11-16 19:00 | 59.37 | 56.96
2017-11-16 19:30 | 58.39 | 55.86
2017-11-16 20:00 | 57.07 | 54.24
2017-11-16 20:30 | 54.9 | 51.58
2017-11-16 21:00 | 53.87 | 50.29
2017-11-16 21:30 | 48.16 | 46.97
2017-11-16 22:00 | 44.11 | 43.88
2017-11-16 22:30 | 43.14 | 42.84
2017-11-16 23:00 | 43.04 | 42.67
2017-11-16 23:30 | 38.98 | 38.43
2017-11-17 | 36.19 | 35.46
2017-11-17 00:30 | 35.37 | 34.56
2017-11-17 01:00 | 33.92 | 32.93
2017-11-17 01:30 | 33.91 | 32.92
2017-11-17 02:00 | 34.06 | 33.05
2017-11-17 02:30 | 33.62 | 32.47
2017-11-17 03:00 | 32.43 | 32.04
2017-11-17 03:30 | 31.95 | 31.58
2017-11-17 04:00 | 31.31 | 30.94
2017-11-17 04:30 | 31.99 | 31.64
2017-11-17 05:00 | 32.97 | 32.68
2017-11-17 05:30 | 34.85 | 34.64
2017-11-17 06:00 | 37.17 | 37.08
2017-11-17 06:30 | 42.01 | 41.98
2017-11-17 07:00 | 47.31 | 47.11
2017-11-17 07:30 | 52.75 | 52.46
2017-11-17 08:00 | 56.77 | 56.33
2017-11-17 08:30 | 58.75 | 58.08
2017-11-17 09:00 | 58.28 | 57.36
2017-11-17 09:30 | 58.93 | 57.92
2017-11-17 10:00 | 57.58 | 56.49
2017-11-17 10:30 | 58.76 | 57.45
2017-11-17 11:00 | 61.13 | 59.56
2017-11-17 11:30 | 61.27 | 59.68
2017-11-17 12:00 | 61.09 | 59.49
2017-11-17 12:30 | 61.99 | 60.5
2017-11-17 13:00 | 61.04 | 59.62
2017-11-17 13:30 | 61.43 | 60.07
2017-11-17 14:00 | 60.45 | 59.07
2017-11-17 14:30 | 61.53 | 60.41
2017-11-17 15:00 | 60.6 | 59.7
2017-11-17 15:30 | 58.08 | 57.42
2017-11-17 16:00 | 58.47 | 57.93
2017-11-17 16:30 | 59.68 | 59.39
2017-11-17 17:00 | 57.7 | 57.54
2017-11-17 17:30 | 54.78 | 54.76
2017-11-17 18:00 | 51.82 | 51.8
2017-11-17 18:30 | 50.57 | 50.52
2017-11-17 19:00 | 52.06 | 52.04
2017-11-17 19:30 | 51 | 50.97
2017-11-17 20:00 | 49.47 | 49.43
2017-11-17 20:30 | 47.48 | 47.37
2017-11-17 21:00 | 46.08 | 45.94
2017-11-17 21:30 | 44.98 | 44.75
2017-11-17 22:00 | 42.71 | 42.37
2017-11-17 22:30 | 40.93 | 40.45
2017-11-17 23:00 | 41.44 | 40.91
2017-11-17 23:30 | 38.1 | 37.4
2017-11-18 | 35.61 | 34.69
2017-11-18 00:30 | 34.66 | 34.34
2017-11-18 01:00 | 32.93 | 32.6
2017-11-18 01:30 | 32.42 | 32.08
2017-11-18 02:00 | 31.98 | 31.59
2017-11-18 02:30 | 31.39 | 30.93
2017-11-18 03:00 | 31.02 | 30.66
2017-11-18 03:30 | 29.89 | 29.79
2017-11-18 04:00 | 29.64 | 29.54
2017-11-18 04:30 | 30.31 | 30.19
2017-11-18 05:00 | 30.27 | 30.14
2017-11-18 05:30 | 31.09 | 30.94
2017-11-18 06:00 | 31.37 | 31.21
2017-11-18 06:30 | 34.07 | 33.75
2017-11-18 07:00 | 35.89 | 35.4
2017-11-18 07:30 | 39.49 | 38.76
2017-11-18 08:00 | 41.18 | 40.18
2017-11-18 08:30 | 42.93 | 42.3
2017-11-18 09:00 | 44.57 | 43.87
2017-11-18 09:30 | 44.12 | 43.28
2017-11-18 10:00 | 44.36 | 43.43
2017-11-18 10:30 | 44.63 | 43.65
2017-11-18 11:00 | 44.62 | 43.63
2017-11-18 11:30 | 34.22 | 32.12
2017-11-18 12:00 | 44.29 | 43.22
2017-11-18 12:30 | 42.71 | 41.83
2017-11-18 13:00 | 43.13 | 42.27
2017-11-18 13:30 | 44.96 | 44.33
2017-11-18 14:00 | 41.29 | 40.68
2017-11-18 14:30 | 41.03 | 40.49
2017-11-18 15:00 | 41.5 | 40.97
2017-11-18 15:30 | 41.74 | 41.3
2017-11-18 16:00 | 42.94 | 42.54
2017-11-18 16:30 | 44.39 | 44.11
2017-11-18 17:00 | 44.07 | 43.87
2017-11-18 17:30 | 45.24 | 45.1
2017-11-18 18:00 | 46.02 | 45.89
2017-11-18 18:30 | 46.02 | 45.91
2017-11-18 19:00 | 47.38 | 47.19
2017-11-18 19:30 | 46.65 | 46.47
2017-11-18 20:00 | 45.31 | 45.14
2017-11-18 20:30 | 43.13 | 43.01
2017-11-18 21:00 | 41.65 | 41.57
2017-11-18 21:30 | 40.3 | 40.25
2017-11-18 22:00 | 39.22 | 39.18
2017-11-18 22:30 | 38.27 | 38.24
2017-11-18 23:00 | 38.57 | 38.55
2017-11-18 23:30 | 35.61 | 35.59
2017-11-19 | 33.55 | 33.53
2017-11-19 00:30 | 33.02 | 33
2017-11-19 01:00 | 31.84 | 31.81
2017-11-19 01:30 | 31.21 | 31.17
2017-11-19 02:00 | 30.65 | 30.61
2017-11-19 02:30 | 29.96 | 29.91
2017-11-19 03:00 | 30.7 | 30.66
2017-11-19 03:30 | 30.16 | 30.05
2017-11-19 04:00 | 29.73 | 29.63
2017-11-19 04:30 | 30.07 | 29.95
2017-11-19 05:00 | 29.79 | 29.68
2017-11-19 05:30 | 29.25 | 29.17
2017-11-19 06:00 | 29.79 | 29.72
2017-11-19 06:30 | 30.61 | 30.49
2017-11-19 07:00 | 33.11 | 32.93
2017-11-19 07:30 | 33.46 | 33.15
2017-11-19 08:00 | 35.89 | 35.46
2017-11-19 08:30 | 37.43 | 36.78
2017-11-19 09:00 | 39.54 | 39.2
2017-11-19 09:30 | 40.03 | 39.73
2017-11-19 10:00 | 39.99 | 39.62
2017-11-19 10:30 | 40.84 | 40.39
2017-11-19 11:00 | 41.7 | 41.22
2017-11-19 11:30 | 40.65 | 40.15
2017-11-19 12:00 | 40.77 | 40.24
2017-11-19 12:30 | 40.58 | 40.1
2017-11-19 13:00 | 40.4 | 39.95
2017-11-19 13:30 | 40.49 | 40.06
2017-11-19 14:00 | 41.43 | 41.01
2017-11-19 14:30 | 40.82 | 40.44
2017-11-19 15:00 | 41.22 | 40.86
2017-11-19 15:30 | 41.89 | 41.6
2017-11-19 16:00 | 43.42 | 43.17
2017-11-19 16:30 | 46.78 | 46.57
2017-11-19 17:00 | 45.06 | 44.91
2017-11-19 17:30 | 45.38 | 45.26
2017-11-19 18:00 | 46.55 | 46.44
2017-11-19 18:30 | 47.63 | 47.53
2017-11-19 19:00 | 49.84 | 49.68
2017-11-19 19:30 | 48.49 | 48.33
2017-11-19 20:00 | 46.63 | 46.51
2017-11-19 20:30 | 44.54 | 44.47
2017-11-19 21:00 | 42.92 | 42.88
2017-11-19 21:30 | 41.25 | 41.23
2017-11-19 22:00 | 38.24 | 38.22
2017-11-19 22:30 | 37 | 36.98
2017-11-19 23:00 | 38.08 | 38.06
2017-11-19 23:30 | 34.25 | 34.23
2017-11-20 | 31.83 | 31.78
2017-11-20 00:30 | 32.15 | 32.08
2017-11-20 01:00 | 31.28 | 31.22
2017-11-20 01:30 | 30.33 | 30.25
2017-11-20 02:00 | 29.85 | 29.77
2017-11-20 02:30 | 29.23 | 29.15
2017-11-20 03:00 | 29.08 | 29.02
2017-11-20 03:30 | 29.16 | 29.09
2017-11-20 04:00 | 29.15 | 29.07
2017-11-20 04:30 | 30.22 | 30.12
2017-11-20 05:00 | 30.97 | 30.84
2017-11-20 05:30 | 32.58 | 32.4
2017-11-20 06:00 | 35.46 | 35.12
2017-11-20 06:30 | 41.62 | 40.79
2017-11-20 07:00 | 46.19 | 45.46
2017-11-20 07:30 | 53.41 | 52.84
2017-11-20 08:00 | 56.3 | 55.95
2017-11-20 08:30 | 58.42 | 58.31
2017-11-20 09:00 | 61.17 | 61.15
2017-11-20 09:30 | 61.33 | 61.29
2017-11-20 10:00 | 60.17 | 60.13
2017-11-20 10:30 | 59.79 | 59.77
2017-11-20 11:00 | 61.61 | 61.6
2017-11-20 11:30 | 61.12 | 61.11
2017-11-20 12:00 | 62.12 | 62.12
2017-11-20 12:30 | 64.42 | 64.39
2017-11-20 13:00 | 60.87 | 60.76
2017-11-20 13:30 | 58.03 | 57.87
2017-11-20 14:00 | 58.07 | 57.92
2017-11-20 14:30 | 57.8 | 57.62
2017-11-20 15:00 | 56.2 | 55.98
2017-11-20 15:30 | 57.12 | 56.84
2017-11-20 16:00 | 59.32 | 58.94
2017-11-20 16:30 | 59.37 | 58.73
2017-11-20 17:00 | 56.91 | 55.92
2017-11-20 17:30 | 54.18 | 52.53
2017-11-20 18:00 | 54.06 | 51.92
2017-11-20 18:30 | 54.29 | 51.88
2017-11-20 19:00 | 54.64 | 52.38
2017-11-20 19:30 | 52.39 | 49.81
2017-11-20 20:00 | 50.88 | 48.16
2017-11-20 20:30 | 49.12 | 46.04
2017-11-20 21:00 | 47.4 | 43.79
2017-11-20 21:30 | 44.28 | 41.82
2017-11-20 22:00 | 40.12 | 40.08
2017-11-20 22:30 | 39.06 | 39
2017-11-20 23:00 | 39.39 | 39.3
2017-11-20 23:30 | 35.13 | 34.99
2017-11-21 | 33.15 | 32.96
2017-11-21 00:30 | 32.83 | 32.58
2017-11-21 01:00 | 31.8 | 31.48
2017-11-21 01:30 | 31.06 | 30.74
2017-11-21 02:00 | 30.89 | 30.54
2017-11-21 02:30 | 29.52 | 29.45
2017-11-21 03:00 | 29.55 | 29.53
2017-11-21 03:30 | 29.53 | 29.5
2017-11-21 04:00 | 29.82 | 29.8
2017-11-21 04:30 | 30.59 | 30.58
2017-11-21 05:00 | 31.87 | 31.86
2017-11-21 05:30 | 33.32 | 33.3
2017-11-21 06:00 | 37.59 | 37.54
2017-11-21 06:30 | 41.7 | 41.44
2017-11-21 07:00 | 47.77 | 47.09
2017-11-21 07:30 | 54.03 | 53.31
2017-11-21 08:00 | 57.64 | 56.53
2017-11-21 08:30 | 58.95 | 58.17
2017-11-21 09:00 | 59.32 | 59.13
2017-11-21 09:30 | 58.06 | 57.97
2017-11-21 10:00 | 57.66 | 57.58
2017-11-21 10:30 | 56.35 | 56.32
2017-11-21 11:00 | 57.44 | 57.43
2017-11-21 11:30 | 58.41 | 58.37
2017-11-21 12:00 | 60.66 | 60.53
2017-11-21 12:30 | 60.34 | 60.15
2017-11-21 13:00 | 62.26 | 62.02
2017-11-21 13:30 | 61.81 | 61.49
2017-11-21 14:00 | 61.19 | 60.87
2017-11-21 14:30 | 58.72 | 58.36
2017-11-21 15:00 | 58.86 | 58.46
2017-11-21 15:30 | 57.22 | 56.68
2017-11-21 16:00 | 57.4 | 56.61
2017-11-21 16:30 | 57.81 | 56.66
2017-11-21 17:00 | 56.91 | 55.14
2017-11-21 17:30 | 56.4 | 53.87
2017-11-21 18:00 | 55.93 | 52.83
2017-11-21 18:30 | 56.01 | 52.56
2017-11-21 19:00 | 56.73 | 53.41
2017-11-21 19:30 | 53.42 | 50.61
2017-11-21 20:00 | 50.89 | 49.58
2017-11-21 20:30 | 49.74 | 48.24
2017-11-21 21:00 | 47.34 | 45.63
2017-11-21 21:30 | 45.24 | 43.16
2017-11-21 22:00 | 43.69 | 41.14
2017-11-21 22:30 | 41.1 | 39.31
2017-11-21 23:00 | 39.31 | 39.28
2017-11-21 23:30 | 35.54 | 35.52
2017-11-22 | 32.91 | 32.9
2017-11-22 00:30 | 33.07 | 33.05
2017-11-22 01:00 | 31.26 | 31.25
2017-11-22 01:30 | 31.11 | 31.1
2017-11-22 02:00 | 30.49 | 30.47
2017-11-22 02:30 | 30.64 | 30.55
2017-11-22 03:00 | 29.97 | 29.87
2017-11-22 03:30 | 29.37 | 29.25
2017-11-22 04:00 | 29.5 | 29.38
2017-11-22 04:30 | 30.17 | 30.03
2017-11-22 05:00 | 31.12 | 30.95
2017-11-22 05:30 | 33.05 | 32.82
2017-11-22 06:00 | 36.76 | 36.41
2017-11-22 06:30 | 42.57 | 41.83
2017-11-22 07:00 | 46.82 | 46.27
2017-11-22 07:30 | 51.49 | 51.08
2017-11-22 08:00 | 53.83 | 53.69
2017-11-22 08:30 | 55.27 | 54.92
2017-11-22 09:00 | 56.29 | 55.57
2017-11-22 09:30 | 56.9 | 56.23
2017-11-22 10:00 | 59.2 | 58.52
2017-11-22 10:30 | 56.32 | 55.71
2017-11-22 11:00 | 54.98 | 54.46
2017-11-22 11:30 | 56.53 | 56.16
2017-11-22 12:00 | 56.48 | 56.14
2017-11-22 12:30 | 56.01 | 55.67
2017-11-22 13:00 | 56.76 | 56.42
2017-11-22 13:30 | 56.51 | 56.14
2017-11-22 14:00 | 54.87 | 54.5
2017-11-22 14:30 | 55.76 | 55.34
2017-11-22 15:00 | 57.98 | 57.59
2017-11-22 15:30 | 58.52 | 57.95
2017-11-22 16:00 | 57.54 | 56.72
2017-11-22 16:30 | 59.19 | 58.05
2017-11-22 17:00 | 57.72 | 56.01
2017-11-22 17:30 | 55.68 | 53.03
2017-11-22 18:00 | 55.63 | 52.41
2017-11-22 18:30 | 56.06 | 52.48
2017-11-22 19:00 | 56.51 | 53.15
2017-11-22 19:30 | 55.17 | 51.62
2017-11-22 20:00 | 53.87 | 49.99
2017-11-22 20:30 | 52.84 | 48.47
2017-11-22 21:00 | 50.68 | 45.79
2017-11-22 21:30 | 49.5 | 44.2
2017-11-22 22:00 | 43.63 | 42.49
2017-11-22 22:30 | 41.05 | 40.56
2017-11-22 23:00 | 39.88 | 39.82
2017-11-22 23:30 | 36.53 | 36.51
2017-11-23 | 34.62 | 34.61
2017-11-23 00:30 | 33.63 | 33.62
2017-11-23 01:00 | 31.56 | 31.55
2017-11-23 01:30 | 30.83 | 30.81
2017-11-23 02:00 | 30.33 | 30.31
2017-11-23 02:30 | 29.62 | 29.57
2017-11-23 03:00 | 29.74 | 29.6
2017-11-23 03:30 | 29.57 | 29.43
2017-11-23 04:00 | 30.21 | 30.07
2017-11-23 04:30 | 31.11 | 30.95
2017-11-23 05:00 | 33.23 | 33.02
2017-11-23 05:30 | 35.11 | 34.86
2017-11-23 06:00 | 38.54 | 38.12
2017-11-23 06:30 | 44.74 | 43.78
2017-11-23 07:00 | 48.99 | 48.33
2017-11-23 07:30 | 54.95 | 54.67
2017-11-23 08:00 | 56.95 | 56.76
2017-11-23 08:30 | 58.73 | 58.24
2017-11-23 09:00 | 57.58 | 56.67
2017-11-23 09:30 | 60 | 59.36
2017-11-23 10:00 | 59.02 | 58.35
2017-11-23 10:30 | 58.62 | 58.13
2017-11-23 11:00 | 58.09 | 57.72
2017-11-23 11:30 | 57.45 | 57.2
2017-11-23 12:00 | 58.28 | 58.14
2017-11-23 12:30 | 58.61 | 58.45
2017-11-23 13:00 | 58 | 57.84
2017-11-23 13:30 | 58.32 | 58.18
2017-11-23 14:00 | 58.74 | 58.61
2017-11-23 14:30 | 59.6 | 59.48
2017-11-23 15:00 | 60.16 | 60.03
2017-11-23 15:30 | 60.36 | 60.18
2017-11-23 16:00 | 61.33 | 60.89
2017-11-23 16:30 | 62.03 | 61.31
2017-11-23 17:00 | 60.74 | 59.68
2017-11-23 17:30 | 59.5 | 57.71
2017-11-23 18:00 | 59.82 | 57.44
2017-11-23 18:30 | 59.86 | 57.18
2017-11-23 19:00 | 60.65 | 58.18
2017-11-23 19:30 | 58.73 | 56.05
2017-11-23 20:00 | 56.94 | 53.93
2017-11-23 20:30 | 55.53 | 52.06
2017-11-23 21:00 | 53.96 | 49.99
2017-11-23 21:30 | 51.45 | 46.7
2017-11-23 22:00 | 49.46 | 44.1
2017-11-23 22:30 | 48.32 | 42.36
2017-11-23 23:00 | 43.45 | 42.13
2017-11-23 23:30 | 39.11 | 38.52
2017-11-24 | 36.71 | 35.94
2017-11-24 00:30 | 35.38 | 34.49
2017-11-24 01:00 | 34.15 | 33.12
2017-11-24 01:30 | 33.24 | 32.25
2017-11-24 02:00 | 31.76 | 31.35
2017-11-24 02:30 | 31.26 | 30.79
2017-11-24 03:00 | 31.17 | 30.67
2017-11-24 03:30 | 30.83 | 30.64
2017-11-24 04:00 | 30.54 | 30.5
2017-11-24 04:30 | 31.22 | 31.19
2017-11-24 05:00 | 33.56 | 33.55
2017-11-24 05:30 | 34.52 | 34.51
2017-11-24 06:00 | 37.48 | 37.45
2017-11-24 06:30 | 43.42 | 43.18
2017-11-24 07:00 | 47.97 | 47.83
2017-11-24 07:30 | 53.51 | 53.02
2017-11-24 08:00 | 55.77 | 55.08
2017-11-24 08:30 | 57.69 | 57.42
2017-11-24 09:00 | 58.05 | 57.95
2017-11-24 09:30 | 57.97 | 57.91
2017-11-24 10:00 | 57.48 | 57.44
2017-11-24 10:30 | 57.19 | 57.17
2017-11-24 11:00 | 57.64 | 57.62
2017-11-24 11:30 | 58.55 | 58.51
2017-11-24 12:00 | 59.04 | 58.89
2017-11-24 12:30 | 58.93 | 58.73
2017-11-24 13:00 | 58.52 | 58.3
2017-11-24 13:30 | 58.53 | 58.29
2017-11-24 14:00 | 59.31 | 59.06
2017-11-24 14:30 | 59.2 | 58.91
2017-11-24 15:00 | 59.49 | 59.15
2017-11-24 15:30 | 58.79 | 58.23
2017-11-24 16:00 | 59.85 | 59.09
2017-11-24 16:30 | 61.02 | 60.06
2017-11-24 17:00 | 59.93 | 58.71
2017-11-24 17:30 | 58.73 | 56.77
2017-11-24 18:00 | 56.75 | 53.98
2017-11-24 18:30 | 56.51 | 53.27
2017-11-24 19:00 | 57.54 | 54.67
2017-11-24 19:30 | 56.28 | 53.24
2017-11-24 20:00 | 55.46 | 52.15
2017-11-24 20:30 | 53.28 | 49.56
2017-11-24 21:00 | 51.62 | 47.33
2017-11-24 21:30 | 50.52 | 45.69
2017-11-24 22:00 | 49.16 | 43.64
2017-11-24 22:30 | 47.29 | 42.04
2017-11-24 23:00 | 46 | 41.79
2017-11-24 23:30 | 42.82 | 37.72
2017-11-25 | 36.64 | 35.97
2017-11-25 00:30 | 35.18 | 35.17
2017-11-25 01:00 | 33.23 | 33.22
2017-11-25 01:30 | 32.84 | 32.82
2017-11-25 02:00 | 31.84 | 31.83
2017-11-25 02:30 | 31.36 | 31.35
2017-11-25 03:00 | 31.02 | 31.01
2017-11-25 03:30 | 30.52 | 30.5
2017-11-25 04:00 | 30.36 | 30.34
2017-11-25 04:30 | 30.68 | 30.66
2017-11-25 05:00 | 30.52 | 30.49
2017-11-25 05:30 | 31.18 | 31.15
2017-11-25 06:00 | 31.93 | 31.91
2017-11-25 06:30 | 34.08 | 34.07
2017-11-25 07:00 | 35.92 | 35.89
2017-11-25 07:30 | 38.07 | 37.94
2017-11-25 08:00 | 41.36 | 41
2017-11-25 08:30 | 44.91 | 44.25
2017-11-25 09:00 | 46.54 | 45.73
2017-11-25 09:30 | 45.81 | 44.84
2017-11-25 10:00 | 45.91 | 44.9
2017-11-25 10:30 | 45.73 | 44.58
2017-11-25 11:00 | 46.05 | 44.87
2017-11-25 11:30 | 45.7 | 44.52
2017-11-25 12:00 | 45.76 | 44.58
2017-11-25 12:30 | 44.4 | 43.42
2017-11-25 13:00 | 43.62 | 42.69
2017-11-25 13:30 | 43.5 | 42.64
2017-11-25 14:00 | 44.03 | 43.26
2017-11-25 14:30 | 44.12 | 43.44
2017-11-25 15:00 | 44.22 | 43.59
2017-11-25 15:30 | 44.7 | 44.13
2017-11-25 16:00 | 45.63 | 45.2
2017-11-25 16:30 | 47.43 | 47.08
2017-11-25 17:00 | 46.7 | 46.43
2017-11-25 17:30 | 47.6 | 47.38
2017-11-25 18:00 | 48.4 | 48.21
2017-11-25 18:30 | 48.4 | 48.23
2017-11-25 19:00 | 49.07 | 48.85
2017-11-25 19:30 | 49.02 | 48.8
2017-11-25 20:00 | 47.23 | 47.04
2017-11-25 20:30 | 46.07 | 45.9
2017-11-25 21:00 | 44.23 | 44.11
2017-11-25 21:30 | 43.18 | 43.09
2017-11-25 22:00 | 41.64 | 41.59
2017-11-25 22:30 | 40.36 | 40.32
2017-11-25 23:00 | 40.39 | 40.37
2017-11-25 23:30 | 36.51 | 36.49
2017-11-26 | 34.52 | 34.5
2017-11-26 00:30 | 33.54 | 33.51
2017-11-26 01:00 | 32.4 | 32.37
2017-11-26 01:30 | 31.67 | 31.64
2017-11-26 02:00 | 31.16 | 31.1
2017-11-26 02:30 | 31.17 | 31.09
2017-11-26 03:00 | 31.42 | 31.37
2017-11-26 03:30 | 30.82 | 30.76
2017-11-26 04:00 | 31.19 | 31.13
2017-11-26 04:30 | 30.4 | 30.34
2017-11-26 05:00 | 30.25 | 30.2
2017-11-26 05:30 | 29.75 | 29.64
2017-11-26 06:00 | 30.11 | 30.01
2017-11-26 06:30 | 31.27 | 31.23
2017-11-26 07:00 | 32.05 | 32.03
2017-11-26 07:30 | 33.8 | 33.79
2017-11-26 08:00 | 35.58 | 35.54
2017-11-26 08:30 | 37.4 | 37.31
2017-11-26 09:00 | 38.77 | 38.6
2017-11-26 09:30 | 40.41 | 40.1
2017-11-26 10:00 | 39.81 | 39.44
2017-11-26 10:30 | 41.12 | 40.2
2017-11-26 11:00 | 41.88 | 40.33
2017-11-26 11:30 | 41.91 | 40.45
2017-11-26 12:00 | 42 | 40.54
2017-11-26 12:30 | 41.99 | 40.44
2017-11-26 13:00 | 41.68 | 40.03
2017-11-26 13:30 | 42.43 | 40.76
2017-11-26 14:00 | 42.13 | 40.4
2017-11-26 14:30 | 42.77 | 41.07
2017-11-26 15:00 | 43.77 | 42.1
2017-11-26 15:30 | 44.33 | 42.6
2017-11-26 16:00 | 44.97 | 43.15
2017-11-26 16:30 | 46.96 | 45.12
2017-11-26 17:00 | 47.5 | 45.61
2017-11-26 17:30 | 50.33 | 48.52
2017-11-26 18:00 | 50.22 | 48.26
2017-11-26 18:30 | 50.89 | 48.83
2017-11-26 19:00 | 52.35 | 50.61
2017-11-26 19:30 | 51.98 | 50.27
2017-11-26 20:00 | 50.28 | 48.36
2017-11-26 20:30 | 48.86 | 46.63
2017-11-26 21:00 | 47.32 | 44.87
2017-11-26 21:30 | 45.34 | 42.51
2017-11-26 22:00 | 43.81 | 40.64
2017-11-26 22:30 | 40.65 | 39.63
2017-11-26 23:00 | 38.94 | 38.93
2017-11-26 23:30 | 35.36 | 35.35
2017-11-27 | 33.66 | 33.65
2017-11-27 00:30 | 33.11 | 33.09
2017-11-27 01:00 | 31.87 | 31.85
2017-11-27 01:30 | 31.86 | 31.82
2017-11-27 02:00 | 31.27 | 31.23
2017-11-27 02:30 | 30.61 | 30.57
2017-11-27 03:00 | 30.88 | 30.84
2017-11-27 03:30 | 30.67 | 30.62
2017-11-27 04:00 | 30.94 | 30.9
2017-11-27 04:30 | 31.74 | 31.72
2017-11-27 05:00 | 32.73 | 32.71
2017-11-27 05:30 | 34.51 | 34.5
2017-11-27 06:00 | 37.9 | 37.87
2017-11-27 06:30 | 43.53 | 43.25
2017-11-27 07:00 | 49.04 | 48.76
2017-11-27 07:30 | 57.29 | 56.54
2017-11-27 08:00 | 60.56 | 59.37
2017-11-27 08:30 | 63.07 | 62.17
2017-11-27 09:00 | 65.01 | 63.86
2017-11-27 09:30 | 64.81 | 63.55
2017-11-27 10:00 | 64.68 | 63.33
2017-11-27 10:30 | 65.07 | 63.52
2017-11-27 11:00 | 65.09 | 64.28
2017-11-27 11:30 | 64.43 | 64.39
2017-11-27 12:00 | 64.02 | 63.99
2017-11-27 12:30 | 64.37 | 64.32
2017-11-27 13:00 | 64.04 | 63.98
2017-11-27 13:30 | 64.44 | 64.4
2017-11-27 14:00 | 64.79 | 64.76
2017-11-27 14:30 | 65.37 | 65.33
2017-11-27 15:00 | 65.29 | 65.23
2017-11-27 15:30 | 65.13 | 65
2017-11-27 16:00 | 65.77 | 65.53
2017-11-27 16:30 | 65.6 | 65.19
2017-11-27 17:00 | 64.19 | 63.41
2017-11-27 17:30 | 62.41 | 61
2017-11-27 18:00 | 60.35 | 58.13
2017-11-27 18:30 | 59.67 | 56.92
2017-11-27 19:00 | 60.68 | 58.21
2017-11-27 19:30 | 59.92 | 57.41
2017-11-27 20:00 | 58.07 | 55.28
2017-11-27 20:30 | 56.38 | 53.21
2017-11-27 21:00 | 54.57 | 50.84
2017-11-27 21:30 | 53.1 | 48.82
2017-11-27 22:00 | 50.84 | 45.91
2017-11-27 22:30 | 45.69 | 43.6
2017-11-27 23:00 | 43.81 | 43.44
2017-11-27 23:30 | 39.82 | 39.31
2017-11-28 | 36.73 | 36.35
2017-11-28 00:30 | 35.2 | 35
2017-11-28 01:00 | 34.1 | 33.86
2017-11-28 01:30 | 33.34 | 33.08
2017-11-28 02:00 | 33.41 | 33.17
2017-11-28 02:30 | 33.86 | 33.56
2017-11-28 03:00 | 32.64 | 32.29
2017-11-28 03:30 | 32.54 | 32.43
2017-11-28 04:00 | 32.65 | 32.63
2017-11-28 04:30 | 33.31 | 33.3
2017-11-28 05:00 | 34.67 | 34.66
2017-11-28 05:30 | 37.17 | 37.14
2017-11-28 06:00 | 40.9 | 40.77
2017-11-28 06:30 | 45.96 | 45.6
2017-11-28 07:00 | 50.42 | 50.09
2017-11-28 07:30 | 57.97 | 57.42
2017-11-28 08:00 | 63.37 | 62.92
2017-11-28 08:30 | 65.87 | 65.64
2017-11-28 09:00 | 67.33 | 67.25
2017-11-28 09:30 | 66.7 | 66.63
2017-11-28 10:00 | 66.22 | 66.18
2017-11-28 10:30 | 69.61 | 69.59
2017-11-28 11:00 | 70 | 69.99
2017-11-28 11:30 | 71.72 | 71.71
2017-11-28 12:00 | 70.16 | 70.14
2017-11-28 12:30 | 70.1 | 70.07
2017-11-28 13:00 | 70.79 | 70.73
2017-11-28 13:30 | 69.45 | 69.42
2017-11-28 14:00 | 69.24 | 69.22
2017-11-28 14:30 | 68.55 | 68.53
2017-11-28 15:00 | 67.96 | 67.92
2017-11-28 15:30 | 68.74 | 68.66
2017-11-28 16:00 | 68.92 | 68.73
2017-11-28 16:30 | 67.24 | 66.82
2017-11-28 17:00 | 65.48 | 64.76
2017-11-28 17:30 | 62.89 | 61.5
2017-11-28 18:00 | 61.05 | 59.08
2017-11-28 18:30 | 60.1 | 57.59
2017-11-28 19:00 | 61.08 | 58.74
2017-11-28 19:30 | 60.11 | 57.64
2017-11-28 20:00 | 59.04 | 56.42
2017-11-28 20:30 | 57.81 | 54.86
2017-11-28 21:00 | 56.02 | 52.66
2017-11-28 21:30 | 50.45 | 50.37
2017-11-28 22:00 | 48.74 | 48.65
2017-11-28 22:30 | 47.08 | 46.95
2017-11-28 23:00 | 46.83 | 46.65
2017-11-28 23:30 | 42.45 | 42.14
2017-11-29 | 40.23 | 39.8
2017-11-29 00:30 | 39.67 | 39.16
2017-11-29 01:00 | 38.2 | 37.6
2017-11-29 01:30 | 37.66 | 37.04
2017-11-29 02:00 | 36.77 | 36.05
2017-11-29 02:30 | 36.06 | 35.32
2017-11-29 03:00 | 35.46 | 35.22
2017-11-29 03:30 | 35.46 | 35.22
2017-11-29 04:00 | 34.75 | 34.65
2017-11-29 04:30 | 35.84 | 35.83
2017-11-29 05:00 | 37.54 | 37.51
2017-11-29 05:30 | 39.69 | 39.62
2017-11-29 06:00 | 43.05 | 42.89
2017-11-29 06:30 | 49.02 | 48.51
2017-11-29 07:00 | 53.23 | 52.91
2017-11-29 07:30 | 59.52 | 58.84
2017-11-29 08:00 | 60.6 | 60.14
2017-11-29 08:30 | 62.23 | 61.76
2017-11-29 09:00 | 63.74 | 63.55
2017-11-29 09:30 | 38.51 | 38.44
2017-11-29 10:00 | 64.22 | 64.19
2017-11-29 10:30 | 66.63 | 66.62
2017-11-29 11:00 | 67.1 | 67.09
2017-11-29 11:30 | 65.7 | 65.69
2017-11-29 12:00 | 66.57 | 66.56
2017-11-29 12:30 | 68.5 | 68.45
2017-11-29 13:00 | 69.3 | 69.25
2017-11-29 13:30 | 69.73 | 69.7
2017-11-29 14:00 | 73.2 | 73.19
2017-11-29 14:30 | 73.63 | 73.62
2017-11-29 15:00 | 67.57 | 67.55
2017-11-29 15:30 | 69.38 | 69.36
2017-11-29 16:00 | 61.2 | 61.12
2017-11-29 16:30 | 70.03 | 69.77
2017-11-29 17:00 | 67.56 | 67.01
2017-11-29 17:30 | 65.85 | 64.74
2017-11-29 18:00 | 64.27 | 62.67
2017-11-29 18:30 | 62.4 | 60.24
2017-11-29 19:00 | 63.23 | 61.16
2017-11-29 19:30 | 61.42 | 59.13
2017-11-29 20:00 | 59.11 | 56.43
2017-11-29 20:30 | 57.6 | 54.63
2017-11-29 21:00 | 55.87 | 52.58
2017-11-29 21:30 | 53.81 | 49.92
2017-11-29 22:00 | 52.26 | 47.83
2017-11-29 22:30 | 47.37 | 45.34
2017-11-29 23:00 | 45.17 | 44.92
2017-11-29 23:30 | 42.06 | 41.72
2017-11-30 | 39.39 | 38.85
2017-11-30 00:30 | 38.89 | 38.29
2017-11-30 01:00 | 36.72 | 36.01
2017-11-30 01:30 | 36.17 | 35.37
2017-11-30 02:00 | 36.1 | 35.22
2017-11-30 02:30 | 35.19 | 34.41
2017-11-30 03:00 | 33.49 | 33.36
2017-11-30 03:30 | 33.34 | 33.33
2017-11-30 04:00 | 33.31 | 33.21
2017-11-30 04:30 | 35.22 | 34.92
2017-11-30 05:00 | 36.46 | 36.09
2017-11-30 05:30 | 36.08 | 35.83
2017-11-30 06:00 | 41.19 | 40.59
2017-11-30 06:30 | 47.72 | 46.59
2017-11-30 07:00 | 51.34 | 50.54
2017-11-30 07:30 | 57.39 | 56.89
2017-11-30 08:00 | 61.18 | 60.7
2017-11-30 08:30 | 63.4 | 62.96
2017-11-30 09:00 | 64.99 | 64.73
2017-11-30 09:30 | 65.45 | 65.23
2017-11-30 10:00 | 65.04 | 64.87
2017-11-30 10:30 | 64.65 | 64.55
2017-11-30 11:00 | 64.16 | 64.12
2017-11-30 11:30 | 64.65 | 64.63
2017-11-30 12:00 | 65.46 | 65.42
2017-11-30 12:30 | 67.2 | 65.44
2017-11-30 13:00 | 67.42 | 65.65
2017-11-30 13:30 | 68 | 66.24
2017-11-30 14:00 | 69.1 | 67.38
2017-11-30 14:30 | 70.21 | 68.51
2017-11-30 15:00 | 69.76 | 68.06
2017-11-30 15:30 | 69.66 | 68
2017-11-30 16:00 | 70.37 | 68.77
2017-11-30 16:30 | 70.6 | 69.06
2017-11-30 17:00 | 68 | 66.46
2017-11-30 17:30 | 64.72 | 63.04
2017-11-30 18:00 | 62.69 | 60.73
2017-11-30 18:30 | 62.33 | 60.16
2017-11-30 19:00 | 63.61 | 61.59
2017-11-30 19:30 | 63.32 | 61.27
2017-11-30 20:00 | 61.79 | 59.5
2017-11-30 20:30 | 61.11 | 58.57
2017-11-30 21:00 | 58.47 | 55.62
2017-11-30 21:30 | 56.08 | 52.72
2017-11-30 22:00 | 52.97 | 49.39
2017-11-30 22:30 | 47.62 | 47.47
2017-11-30 23:00 | 47.67 | 47.46
2017-11-30 23:30 | 43.4 | 43.07
2017-12-01 | 39.97 | 39.7
2017-12-01 00:30 | 38.21 | 38.11
2017-12-01 01:00 | 36.9 | 36.76
2017-12-01 01:30 | 36.82 | 36.66
2017-12-01 02:00 | 35.89 | 35.68
2017-12-01 02:30 | 35.11 | 34.85
2017-12-01 03:00 | 33.8 | 33.75
2017-12-01 03:30 | 34.03 | 34.01
2017-12-01 04:00 | 34.38 | 34.35
2017-12-01 04:30 | 35.64 | 35.61
2017-12-01 05:00 | 36.62 | 36.58
2017-12-01 05:30 | 38.4 | 38.34
2017-12-01 06:00 | 41.44 | 41.33
2017-12-01 06:30 | 49.03 | 47.31
2017-12-01 07:00 | 55.51 | 53.02
2017-12-01 07:30 | 61.14 | 58.9
2017-12-01 08:00 | 62.62 | 60.43
2017-12-01 08:30 | 66.45 | 64.73
2017-12-01 09:00 | 71.61 | 70
2017-12-01 09:30 | 71.55 | 69.96
2017-12-01 10:00 | 70.44 | 68.84
2017-12-01 10:30 | 70.56 | 68.93
2017-12-01 11:00 | 68.67 | 66.99
2017-12-01 11:30 | 69.65 | 67.98
2017-12-01 12:00 | 70.4 | 68.73
2017-12-01 12:30 | 70.2 | 68.54
2017-12-01 13:00 | 66.81 | 65.06
2017-12-01 13:30 | 66.35 | 64.58
2017-12-01 14:00 | 65.86 | 64.09
2017-12-01 14:30 | 65.75 | 63.98
2017-12-01 15:00 | 66.49 | 64.75
2017-12-01 15:30 | 65.52 | 63.82
2017-12-01 16:00 | 65.23 | 63.54
2017-12-01 16:30 | 66.28 | 64.66
2017-12-01 17:00 | 63.55 | 61.92
2017-12-01 17:30 | 61.41 | 59.47
2017-12-01 18:00 | 59.82 | 57.78
2017-12-01 18:30 | 57.57 | 55.68
2017-12-01 19:00 | 57.86 | 55.97
2017-12-01 19:30 | 57.04 | 55.11
2017-12-01 20:00 | 55.84 | 53.88
2017-12-01 20:30 | 54.01 | 52
2017-12-01 21:00 | 52.04 | 49.98
2017-12-01 21:30 | 50.18 | 48.04
2017-12-01 22:00 | 48.41 | 46.11
2017-12-01 22:30 | 47.51 | 44.72
2017-12-01 23:00 | 47.44 | 44.56
2017-12-01 23:30 | 44.52 | 41.46
2017-12-02 | 42.25 | 39.02
2017-12-02 00:30 | 40.61 | 37.26
2017-12-02 01:00 | 39.25 | 35.77
2017-12-02 01:30 | 39.12 | 35.63
2017-12-02 02:00 | 38.65 | 35.11
2017-12-02 02:30 | 37.91 | 34.3
2017-12-02 03:00 | 36.95 | 33.3
2017-12-02 03:30 | 36.45 | 32.72
2017-12-02 04:00 | 36.35 | 32.62
2017-12-02 04:30 | 36.57 | 32.85
2017-12-02 05:00 | 37.41 | 33.77
2017-12-02 05:30 | 37.66 | 34.04
2017-12-02 06:00 | 38.99 | 35.51
2017-12-02 06:30 | 40.55 | 37.17
2017-12-02 07:00 | 41.48 | 38.14
2017-12-02 07:30 | 44.57 | 41.43
2017-12-02 08:00 | 47.23 | 44.25
2017-12-02 08:30 | 49.49 | 46.59
2017-12-02 09:00 | 50.3 | 47.38
2017-12-02 09:30 | 52.59 | 49.83
2017-12-02 10:00 | 54.8 | 52.14
2017-12-02 10:30 | 56.3 | 53.72
2017-12-02 11:00 | 55.78 | 53.17
2017-12-02 11:30 | 56.51 | 53.94
2017-12-02 12:00 | 55.9 | 53.33
2017-12-02 12:30 | 53.07 | 50.51
2017-12-02 13:00 | 49.96 | 47.75
2017-12-02 13:30 | 50.91 | 48.75
2017-12-02 14:00 | 50.94 | 48.8
2017-12-02 14:30 | 51.02 | 48.88
2017-12-02 15:00 | 52.54 | 50.47
2017-12-02 15:30 | 53.47 | 51.46
2017-12-02 16:00 | 54.52 | 52.59
2017-12-02 16:30 | 54.25 | 52.31
2017-12-02 17:00 | 53.15 | 51.14
2017-12-02 17:30 | 53.28 | 51.19
2017-12-02 18:00 | 53.44 | 51.32
2017-12-02 18:30 | 53.95 | 51.84
2017-12-02 19:00 | 54.39 | 52.39
2017-12-02 19:30 | 54.01 | 52.02
2017-12-02 20:00 | 52.69 | 50.61
2017-12-02 20:30 | 50.38 | 48.08
2017-12-02 21:00 | 48.94 | 46.5
2017-12-02 21:30 | 47.59 | 45
2017-12-02 22:00 | 46.12 | 43.26
2017-12-02 22:30 | 44.95 | 41.97
2017-12-02 23:00 | 44.91 | 41.96
2017-12-02 23:30 | 42.03 | 38.84
2017-12-03 | 40.73 | 37.47
2017-12-03 00:30 | 40.06 | 36.75
2017-12-03 01:00 | 38.9 | 35.48
2017-12-03 01:30 | 38.08 | 34.57
2017-12-03 02:00 | 37.62 | 34.07
2017-12-03 02:30 | 37.29 | 33.69
2017-12-03 03:00 | 37.05 | 33.43
2017-12-03 03:30 | 36.64 | 32.99
2017-12-03 04:00 | 36.52 | 32.85
2017-12-03 04:30 | 36.43 | 32.76
2017-12-03 05:00 | 36.6 | 32.93
2017-12-03 05:30 | 35.98 | 32.29
2017-12-03 06:00 | 36.53 | 32.89
2017-12-03 06:30 | 38.79 | 35.34
2017-12-03 07:00 | 40.3 | 36.97
2017-12-03 07:30 | 42.43 | 39.25
2017-12-03 08:00 | 43.52 | 40.39
2017-12-03 08:30 | 46.14 | 43.19
2017-12-03 09:00 | 47.14 | 44.25
2017-12-03 09:30 | 47.81 | 44.91
2017-12-03 10:00 | 49.55 | 46.75
2017-12-03 10:30 | 52.64 | 50.01
2017-12-03 11:00 | 50.02 | 47.22
2017-12-03 11:30 | 50.09 | 47.3
2017-12-03 12:00 | 53.25 | 50.62
2017-12-03 12:30 | 53.31 | 50.69
2017-12-03 13:00 | 54.62 | 52.09
2017-12-03 13:30 | 54.45 | 52.16
2017-12-03 14:00 | 51.57 | 49.49
2017-12-03 14:30 | 52.25 | 50.22
2017-12-03 15:00 | 51.55 | 49.49
2017-12-03 15:30 | 50.92 | 48.8
2017-12-03 16:00 | 52.94 | 50.9
2017-12-03 16:30 | 54.59 | 52.63
2017-12-03 17:00 | 54.37 | 52.41
2017-12-03 17:30 | 53.62 | 51.57
2017-12-03 18:00 | 54.9 | 52.89
2017-12-03 18:30 | 56.55 | 54.6
2017-12-03 19:00 | 57.98 | 56.16
2017-12-03 19:30 | 57.14 | 55.29
2017-12-03 20:00 | 55.58 | 53.64
2017-12-03 20:30 | 54.26 | 52.22
2017-12-03 21:00 | 51.97 | 49.94
2017-12-03 21:30 | 49.1 | 47
2017-12-03 22:00 | 46.63 | 44.09
2017-12-03 22:30 | 44.5 | 41.47
2017-12-03 23:00 | 44.74 | 41.59
2017-12-03 23:30 | 41.71 | 37.93
2017-12-04 | 40.02 | 35.9
2017-12-04 00:30 | 39.89 | 35.65
2017-12-04 01:00 | 36.04 | 34.19
2017-12-04 01:30 | 33.77 | 33.76
2017-12-04 02:00 | 33.55 | 33.54
2017-12-04 02:30 | 33.01 | 32.99
2017-12-04 03:00 | 32.51 | 32.48
2017-12-04 03:30 | 32.59 | 32.56
2017-12-04 04:00 | 32.83 | 32.81
2017-12-04 04:30 | 33.41 | 33.4
2017-12-04 05:00 | 34.52 | 34.51
2017-12-04 05:30 | 36.94 | 36.93
2017-12-04 06:00 | 40.27 | 39.92
2017-12-04 06:30 | 47.26 | 45.44
2017-12-04 07:00 | 52.42 | 50.24
2017-12-04 07:30 | 58.86 | 57.01
2017-12-04 08:00 | 61.83 | 60.17
2017-12-04 08:30 | 67.54 | 65.99
2017-12-04 09:00 | 69.8 | 68.35
2017-12-04 09:30 | 68.57 | 67.08
2017-12-04 10:00 | 67.75 | 66.25
2017-12-04 10:30 | 66.69 | 65.2
2017-12-04 11:00 | 66.53 | 65.09
2017-12-04 11:30 | 67.56 | 67
2017-12-04 12:00 | 69.05 | 69.05
2017-12-04 12:30 | 70.71 | 70.71
2017-12-04 13:00 | 69.72 | 69.72
2017-12-04 13:30 | 71.12 | 70.3
2017-12-04 14:00 | 74.82 | 70.82
2017-12-04 14:30 | 71.82 | 71.3
2017-12-04 15:00 | 71.67 | 71.29
2017-12-04 15:30 | 71.91 | 71.55
2017-12-04 16:00 | 72.67 | 72.33
2017-12-04 16:30 | 72.59 | 72.13
2017-12-04 17:00 | 70.17 | 69.28
2017-12-04 17:30 | 66.48 | 65.46
2017-12-04 18:00 | 65.54 | 64.12
2017-12-04 18:30 | 65.09 | 63.31
2017-12-04 19:00 | 65.04 | 63.89
2017-12-04 19:30 | 64.22 | 63.3
2017-12-04 20:00 | 61.2 | 60.21
2017-12-04 20:30 | 57.46 | 56.37
2017-12-04 21:00 | 54.25 | 53.04
2017-12-04 21:30 | 51.39 | 50.07
2017-12-04 22:00 | 52.14 | 47.12
2017-12-04 22:30 | 52.98 | 44.57
2017-12-04 23:00 | 52.72 | 44.2
2017-12-04 23:30 | 47.98 | 40.35
2017-12-05 | 36.11 | 29.44
2017-12-05 00:30 | 35.09 | 28.55
2017-12-05 01:00 | 34.31 | 27.56
2017-12-05 01:30 | 34 | 26.95
2017-12-05 02:00 | 41.79 | 32.88
2017-12-05 02:30 | 41.93 | 33.06
2017-12-05 03:00 | 42.11 | 33.28
2017-12-05 03:30 | 42.11 | 33.27
2017-12-05 04:00 | 42.12 | 33.28
2017-12-05 04:30 | 42.58 | 33.87
2017-12-05 05:00 | 43.33 | 34.89
2017-12-05 05:30 | 44.97 | 37.05
2017-12-05 06:00 | 46.95 | 39.57
2017-12-05 06:30 | 46.94 | 44.88
2017-12-05 07:00 | 51.56 | 50.66
2017-12-05 07:30 | 55.04 | 54.16
2017-12-05 08:00 | 58.15 | 57.33
2017-12-05 08:30 | 62.64 | 61.64
2017-12-05 09:00 | 63.48 | 62.54
2017-12-05 09:30 | 63.58 | 62.65
2017-12-05 10:00 | 64.01 | 63.1
2017-12-05 10:30 | 64.2 | 63.34
2017-12-05 11:00 | 64.66 | 63.82
2017-12-05 11:30 | 65.59 | 64.79
2017-12-05 12:00 | 66.23 | 65.44
2017-12-05 12:30 | 66.67 | 65.88
2017-12-05 13:00 | 66.42 | 65.63
2017-12-05 13:30 | 66.68 | 65.89
2017-12-05 14:00 | 66.45 | 65.65
2017-12-05 14:30 | 66.44 | 65.64
2017-12-05 15:00 | 66.84 | 66.03
2017-12-05 15:30 | 67.12 | 66.3
2017-12-05 16:00 | 67.33 | 66.47
2017-12-05 16:30 | 68.02 | 67.12
2017-12-05 17:00 | 66.81 | 65.86
2017-12-05 17:30 | 64.67 | 63.52
2017-12-05 18:00 | 62.34 | 60.55
2017-12-05 18:30 | 65.58 | 59.33
2017-12-05 19:00 | 65.79 | 59.84
2017-12-05 19:30 | 65.76 | 59.84
2017-12-05 20:00 | 64.67 | 58.57
2017-12-05 20:30 | 62.34 | 55.9
2017-12-05 21:00 | 59.25 | 53.24
2017-12-05 21:30 | 51.41 | 50.62
2017-12-05 22:00 | 49 | 48.16
2017-12-05 22:30 | 46.51 | 45.59
2017-12-05 23:00 | 46.13 | 45.18
2017-12-05 23:30 | 41.66 | 40.56
2017-12-06 | 39.19 | 38
2017-12-06 00:30 | 38.38 | 37.13
2017-12-06 01:00 | 36.85 | 35.53
2017-12-06 01:30 | 35.65 | 34.26
2017-12-06 02:00 | 34.9 | 33.49
2017-12-06 02:30 | 34.07 | 32.77
2017-12-06 03:00 | 33.9 | 32.58
2017-12-06 03:30 | 33.59 | 32.24
2017-12-06 04:00 | 33.76 | 32.42
2017-12-06 04:30 | 34.56 | 33.28
2017-12-06 05:00 | 35.22 | 33.97
2017-12-06 05:30 | 36.87 | 35.7
2017-12-06 06:00 | 39.95 | 38.93
2017-12-06 06:30 | 45.52 | 44.38
2017-12-06 07:00 | 51.2 | 49.22
2017-12-06 07:30 | 61.21 | 54.53
2017-12-06 08:00 | 64.71 | 58.74
2017-12-06 08:30 | 67.38 | 61.71
2017-12-06 09:00 | 69.38 | 63.89
2017-12-06 09:30 | 70.3 | 64.95
2017-12-06 10:00 | 71.12 | 65.91
2017-12-06 10:30 | 71.75 | 66.67
2017-12-06 11:00 | 72.4 | 67.49
2017-12-06 11:30 | 71.36 | 68.94
2017-12-06 12:00 | 70.51 | 69.83
2017-12-06 12:30 | 70.25 | 69.55
2017-12-06 13:00 | 70.46 | 69.76
2017-12-06 13:30 | 71.56 | 70.89
2017-12-06 14:00 | 72.34 | 71.67
2017-12-06 14:30 | 72.45 | 71.78
2017-12-06 15:00 | 72.16 | 71.48
2017-12-06 15:30 | 72.33 | 71.63
2017-12-06 16:00 | 72.87 | 72.16
2017-12-06 16:30 | 72.88 | 72.12
2017-12-06 17:00 | 70.8 | 69.96
2017-12-06 17:30 | 68.84 | 67.89
2017-12-06 18:00 | 66.39 | 65.18
2017-12-06 18:30 | 64.97 | 63.26
2017-12-06 19:00 | 65.51 | 63.89
2017-12-06 19:30 | 64.72 | 63.84
2017-12-06 20:00 | 62.84 | 61.91
2017-12-06 20:30 | 60.24 | 59.24
2017-12-06 21:00 | 58.21 | 57.16
2017-12-06 21:30 | 55.35 | 54.2
2017-12-06 22:00 | 52.26 | 51.14
2017-12-06 22:30 | 49.14 | 48.32
2017-12-06 23:00 | 48.75 | 47.91
2017-12-06 23:30 | 44.45 | 43.49
2017-12-07 | 41.78 | 40.72
2017-12-07 00:30 | 40.93 | 39.83
2017-12-07 01:00 | 39.57 | 38.41
2017-12-07 01:30 | 38.64 | 37.44
2017-12-07 02:00 | 37.78 | 36.53
2017-12-07 02:30 | 37.19 | 35.91
2017-12-07 03:00 | 36.71 | 35.39
2017-12-07 03:30 | 36.63 | 35.31
2017-12-07 04:00 | 36.62 | 35.29
2017-12-07 04:30 | 37.31 | 36.03
2017-12-07 05:00 | 37.96 | 36.71
2017-12-07 05:30 | 39.55 | 38.38
2017-12-07 06:00 | 42.94 | 41.92
2017-12-07 06:30 | 48.26 | 47.37
2017-12-07 07:00 | 53.67 | 52.83
2017-12-07 07:30 | 58.65 | 57.92
2017-12-07 08:00 | 62.44 | 61.58
2017-12-07 08:30 | 66.37 | 65.44
2017-12-07 09:00 | 67.55 | 66.76
2017-12-07 09:30 | 68.29 | 67.51
2017-12-07 10:00 | 68.56 | 67.8
2017-12-07 10:30 | 69.31 | 68.58
2017-12-07 11:00 | 70.12 | 69.42
2017-12-07 11:30 | 70.86 | 70.17
2017-12-07 12:00 | 71.53 | 70.86
2017-12-07 12:30 | 71.94 | 71.26
2017-12-07 13:00 | 71.7 | 71.02
2017-12-07 13:30 | 72.28 | 71.61
2017-12-07 14:00 | 72.85 | 72.18
2017-12-07 14:30 | 73.35 | 72.69
2017-12-07 15:00 | 73.05 | 72.38
2017-12-07 15:30 | 72.78 | 72.08
2017-12-07 16:00 | 72.8 | 72.07
2017-12-07 16:30 | 73.12 | 72.36
2017-12-07 17:00 | 71.64 | 70.81
2017-12-07 17:30 | 69.19 | 68.25
2017-12-07 18:00 | 67.79 | 66.75
2017-12-07 18:30 | 66.59 | 65.17
2017-12-07 19:00 | 66.18 | 65.31
2017-12-07 19:30 | 66.39 | 65.54
2017-12-07 20:00 | 64.31 | 63.41
2017-12-07 20:30 | 62.27 | 61.32
2017-12-07 21:00 | 59.88 | 58.86
2017-12-07 21:30 | 56.55 | 55.42
2017-12-07 22:00 | 53.1 | 51.84
2017-12-07 22:30 | 51.09 | 49.04
2017-12-07 23:00 | 48.77 | 47.91
2017-12-07 23:30 | 44.41 | 43.43
2017-12-08 | 41.66 | 40.57
2017-12-08 00:30 | 40.45 | 39.3
2017-12-08 01:00 | 38.9 | 37.69
2017-12-08 01:30 | 37.98 | 36.73
2017-12-08 02:00 | 37.54 | 36.26
2017-12-08 02:30 | 36.97 | 35.66
2017-12-08 03:00 | 36.59 | 35.26
2017-12-08 03:30 | 36.34 | 34.99
2017-12-08 04:00 | 36.15 | 34.78
2017-12-08 04:30 | 36.8 | 35.47
2017-12-08 05:00 | 37.85 | 36.59
2017-12-08 05:30 | 39.32 | 38.12
2017-12-08 06:00 | 42.4 | 41.35
2017-12-08 06:30 | 47.11 | 46.22
2017-12-08 07:00 | 52.29 | 51.47
2017-12-08 07:30 | 58.74 | 57.99
2017-12-08 08:00 | 62.53 | 61.7
2017-12-08 08:30 | 65.44 | 64.35
2017-12-08 09:00 | 67.71 | 66.24
2017-12-08 09:30 | 68.68 | 66.9
2017-12-08 10:00 | 68.68 | 66.86
2017-12-08 10:30 | 69.78 | 67.8
2017-12-08 11:00 | 69.62 | 68.04
2017-12-08 11:30 | 69 | 68.61
2017-12-08 12:00 | 69.92 | 69.53
2017-12-08 12:30 | 69.71 | 69.17
2017-12-08 13:00 | 70 | 69.26
2017-12-08 13:30 | 71.56 | 70.84
2017-12-08 14:00 | 71.6 | 70.87
2017-12-08 14:30 | 71.92 | 71.19
2017-12-08 15:00 | 72.19 | 71.44
2017-12-08 15:30 | 71.15 | 70.35
2017-12-08 16:00 | 69.62 | 68.74
2017-12-08 16:30 | 66.96 | 66.01
2017-12-08 17:00 | 65.65 | 64.73
2017-12-08 17:30 | 63.51 | 62.63
2017-12-08 18:00 | 60.85 | 59.86
2017-12-08 18:30 | 59.06 | 57.99
2017-12-08 19:00 | 59.45 | 58.4
2017-12-08 19:30 | 59.56 | 58.52
2017-12-08 20:00 | 58.12 | 57.03
2017-12-08 20:30 | 55.78 | 54.62
2017-12-08 21:00 | 53.85 | 52.63
2017-12-08 21:30 | 51.95 | 50.65
2017-12-08 22:00 | 52.2 | 48.05
2017-12-08 22:30 | 54.09 | 45.88
2017-12-08 23:00 | 53.87 | 45.54
2017-12-08 23:30 | 50.68 | 41.56
2017-12-09 | 48.28 | 39.13
2017-12-09 00:30 | 45.83 | 37.51
2017-12-09 01:00 | 44.66 | 36.01
2017-12-09 01:30 | 44.02 | 35.2
2017-12-09 02:00 | 43.57 | 34.61
2017-12-09 02:30 | 43.36 | 34.28
2017-12-09 03:00 | 43.27 | 34.15
2017-12-09 03:30 | 42.74 | 33.44
2017-12-09 04:00 | 42.75 | 33.46
2017-12-09 04:30 | 42.69 | 33.39
2017-12-09 05:00 | 42.83 | 33.58
2017-12-09 05:30 | 43.2 | 34.04
2017-12-09 06:00 | 43.53 | 34.41
2017-12-09 06:30 | 45.13 | 36.59
2017-12-09 07:00 | 46.72 | 38.74
2017-12-09 07:30 | 49.17 | 41.86
2017-12-09 08:00 | 50.73 | 43.88
2017-12-09 08:30 | 52.96 | 47.38
2017-12-09 09:00 | 50.81 | 49.69
2017-12-09 09:30 | 51.39 | 50.17
2017-12-09 10:00 | 51.21 | 50.02
2017-12-09 10:30 | 50.94 | 49.76
2017-12-09 11:00 | 51.06 | 49.88
2017-12-09 11:30 | 51.09 | 49.92
2017-12-09 12:00 | 51.55 | 50.38
2017-12-09 12:30 | 52.33 | 51.15
2017-12-09 13:00 | 51.29 | 50.07
2017-12-09 13:30 | 51.2 | 49.97
2017-12-09 14:00 | 51.49 | 50.27
2017-12-09 14:30 | 51.47 | 50.24
2017-12-09 15:00 | 52.05 | 50.82
2017-12-09 15:30 | 53.05 | 51.84
2017-12-09 16:00 | 54.19 | 52.99
2017-12-09 16:30 | 53.02 | 51.78
2017-12-09 17:00 | 53.95 | 52.71
2017-12-09 17:30 | 54.56 | 53.3
2017-12-09 18:00 | 57.51 | 53.25
2017-12-09 18:30 | 59.61 | 52.39
2017-12-09 19:00 | 59.82 | 52.67
2017-12-09 19:30 | 59.92 | 52.79
2017-12-09 20:00 | 58.69 | 51.31
2017-12-09 20:30 | 56.9 | 49.16
2017-12-09 21:00 | 55.6 | 47.59
2017-12-09 21:30 | 53.05 | 45.71
2017-12-09 22:00 | 51.24 | 44.13
2017-12-09 22:30 | 49.87 | 42.42
2017-12-09 23:00 | 50.07 | 42.67
2017-12-09 23:30 | 47.26 | 39.23
2017-12-10 | 45.89 | 37.45
2017-12-10 00:30 | 45.26 | 36.65
2017-12-10 01:00 | 44.25 | 35.35
2017-12-10 01:30 | 43.71 | 34.65
2017-12-10 02:00 | 43.39 | 34.22
2017-12-10 02:30 | 42.92 | 33.58
2017-12-10 03:00 | 42.36 | 32.82
2017-12-10 03:30 | 42.32 | 32.72
2017-12-10 04:00 | 42.15 | 32.46
2017-12-10 04:30 | 41.93 | 32.17
2017-12-10 05:00 | 41.95 | 32.22
2017-12-10 05:30 | 41.49 | 31.49
2017-12-10 06:00 | 41.68 | 31.75
2017-12-10 06:30 | 42.67 | 33.16
2017-12-10 07:00 | 43.83 | 34.81
2017-12-10 07:30 | 45.71 | 37.33
2017-12-10 08:00 | 46.38 | 38.25
2017-12-10 08:30 | 47.27 | 39.46
2017-12-10 09:00 | 48.09 | 40.63
2017-12-10 09:30 | 49.04 | 41.95
2017-12-10 10:00 | 49.4 | 42.44
2017-12-10 10:30 | 47.19 | 42.99
2017-12-10 11:00 | 44.26 | 43.33
2017-12-10 11:30 | 44.84 | 43.88
2017-12-10 12:00 | 45.01 | 44.07
2017-12-10 12:30 | 48.13 | 44.66
2017-12-10 13:00 | 53.14 | 45.15
2017-12-10 13:30 | 53.18 | 45.21
2017-12-10 14:00 | 53.44 | 45.56
2017-12-10 14:30 | 53.56 | 45.62
2017-12-10 15:00 | 54.34 | 46.57
2017-12-10 15:30 | 54.56 | 46.75
2017-12-10 16:00 | 55.52 | 47.86
2017-12-10 16:30 | 57.18 | 49.75
2017-12-10 17:00 | 56.97 | 49.49
2017-12-10 17:30 | 57.55 | 50.09
2017-12-10 18:00 | 58.5 | 51.17
2017-12-10 18:30 | 59.11 | 51.83
2017-12-10 19:00 | 59.76 | 52.64
2017-12-10 19:30 | 59.8 | 52.72
2017-12-10 20:00 | 58.55 | 51.25
2017-12-10 20:30 | 56.91 | 49.27
2017-12-10 21:00 | 54.38 | 47.91
2017-12-10 21:30 | 52.9 | 46.22
2017-12-10 22:00 | 51.12 | 44.1
2017-12-10 22:30 | 49.57 | 42.2
2017-12-10 23:00 | 49.66 | 42.27
2017-12-10 23:30 | 46.75 | 38.67
2017-12-11 | 45.43 | 36.98
2017-12-11 00:30 | 44.97 | 36.38
2017-12-11 01:00 | 44.02 | 35.13
2017-12-11 01:30 | 43.8 | 34.83
2017-12-11 02:00 | 43.59 | 34.54
2017-12-11 02:30 | 43.37 | 34.25
2017-12-11 03:00 | 43.02 | 33.77
2017-12-11 03:30 | 43.03 | 33.76
2017-12-11 04:00 | 42.96 | 33.65
2017-12-11 04:30 | 43.24 | 34.09
2017-12-11 05:00 | 43.76 | 34.8
2017-12-11 05:30 | 45.28 | 36.81
2017-12-11 06:00 | 47.8 | 40.08
2017-12-11 06:30 | 51.62 | 44.91
2017-12-11 07:00 | 55.5 | 49.98
2017-12-11 07:30 | 57.35 | 56.41
2017-12-11 08:00 | 62.68 | 61.68
2017-12-11 08:30 | 65.19 | 64.23
2017-12-11 09:00 | 64.95 | 64.01
2017-12-11 09:30 | 66.72 | 65.82
2017-12-11 10:00 | 64.46 | 63.54
2017-12-11 10:30 | 65.13 | 64.28
2017-12-11 11:00 | 66.03 | 65.21
2017-12-11 11:30 | 66.37 | 65.57
2017-12-11 12:00 | 67.17 | 66.39
2017-12-11 12:30 | 67.28 | 66.49
2017-12-11 13:00 | 66.88 | 66.08
2017-12-11 13:30 | 67.22 | 66.43
2017-12-11 14:00 | 67.25 | 66.46
2017-12-11 14:30 | 67.65 | 66.86
2017-12-11 15:00 | 69.2 | 68.42
2017-12-11 15:30 | 69.66 | 68.87
2017-12-11 16:00 | 67.72 | 66.88
2017-12-11 16:30 | 68.36 | 67.48
2017-12-11 17:00 | 66.14 | 65.18
2017-12-11 17:30 | 63.92 | 62.79
2017-12-11 18:00 | 64.08 | 60.99
2017-12-11 18:30 | 65.77 | 59.02
2017-12-11 19:00 | 66.28 | 59.6
2017-12-11 19:30 | 65.94 | 59.21
2017-12-11 20:00 | 64.22 | 57.2
2017-12-11 20:30 | 61.93 | 54.46
2017-12-11 21:00 | 58.28 | 50.13
2017-12-11 21:30 | 55.27 | 47.6
2017-12-11 22:00 | 52.55 | 45.07
2017-12-11 22:30 | 50.82 | 42.93
2017-12-11 23:00 | 51.43 | 43.57
2017-12-11 23:30 | 49.27 | 40.88
2017-12-12 | 47.67 | 38.83
2017-12-12 00:30 | 46.72 | 37.57
2017-12-12 01:00 | 45.67 | 36.17
2017-12-12 01:30 | 45.06 | 35.37
2017-12-12 02:00 | 44.83 | 35.06
2017-12-12 02:30 | 44.37 | 34.44
2017-12-12 03:00 | 43.64 | 33.99
2017-12-12 03:30 | 43.5 | 33.8
2017-12-12 04:00 | 43.28 | 33.48
2017-12-12 04:30 | 43.71 | 34.09
2017-12-12 05:00 | 44.42 | 35.09
2017-12-12 05:30 | 45.88 | 37.08
2017-12-12 06:00 | 48.12 | 40.02
2017-12-12 06:30 | 52.14 | 45.19
2017-12-12 07:00 | 56.65 | 50.3
2017-12-12 07:30 | 59.73 | 57.02
2017-12-12 08:00 | 60.22 | 59.42
2017-12-12 08:30 | 64.71 | 63.82
2017-12-12 09:00 | 64.68 | 63.77
2017-12-12 09:30 | 62.65 | 61.73
2017-12-12 10:00 | 63.46 | 62.57
2017-12-12 10:30 | 64.04 | 63.18
2017-12-12 11:00 | 63.75 | 62.9
2017-12-12 11:30 | 66.28 | 65.47
2017-12-12 12:00 | 65.86 | 65.05
2017-12-12 12:30 | 64.93 | 64.11
2017-12-12 13:00 | 65.2 | 64.39
2017-12-12 13:30 | 65.37 | 64.56
2017-12-12 14:00 | 65.78 | 64.98
2017-12-12 14:30 | 66.28 | 65.47
2017-12-12 15:00 | 65.83 | 65.01
2017-12-12 15:30 | 65.82 | 64.98
2017-12-12 16:00 | 65.88 | 65.01
2017-12-12 16:30 | 66.57 | 65.66
2017-12-12 17:00 | 64.97 | 64
2017-12-12 17:30 | 63.26 | 62.07
2017-12-12 18:00 | 60.98 | 59.88
2017-12-12 18:30 | 59.28 | 58.48
2017-12-12 19:00 | 60.32 | 59.54
2017-12-12 19:30 | 61.03 | 60.27
2017-12-12 20:00 | 59.66 | 58.87
2017-12-12 20:30 | 57.15 | 56.3
2017-12-12 21:00 | 54.95 | 54.04
2017-12-12 21:30 | 51.9 | 50.9
2017-12-12 22:00 | 49.62 | 48.54
2017-12-12 22:30 | 47.43 | 46.26
2017-12-12 23:00 | 47.16 | 45.96
2017-12-12 23:30 | 43.22 | 41.86
2017-12-13 | 41.4 | 39.97
2017-12-13 00:30 | 40.06 | 38.54
2017-12-13 01:00 | 38.57 | 36.97
2017-12-13 01:30 | 37.81 | 36.16
2017-12-13 02:00 | 37.91 | 35.77
2017-12-13 02:30 | 44.71 | 34.93
2017-12-13 03:00 | 44.36 | 34.44
2017-12-13 03:30 | 43.87 | 34.35
2017-12-13 04:00 | 44.02 | 34.59
2017-12-13 04:30 | 44.27 | 34.95
2017-12-13 05:00 | 45.01 | 35.94
2017-12-13 05:30 | 46.24 | 37.58
2017-12-13 06:00 | 48.71 | 40.8
2017-12-13 06:30 | 52.72 | 45.9
2017-12-13 07:00 | 56.72 | 50.79
2017-12-13 07:30 | 57.86 | 56.87
2017-12-13 08:00 | 61.49 | 60.44
2017-12-13 08:30 | 63.46 | 62.49
2017-12-13 09:00 | 62.81 | 61.87
2017-12-13 09:30 | 63.49 | 62.58
2017-12-13 10:00 | 62.72 | 61.81
2017-12-13 10:30 | 62.77 | 61.88
2017-12-13 11:00 | 63.18 | 62.31
2017-12-13 11:30 | 63.81 | 62.96
2017-12-13 12:00 | 64.24 | 63.41
2017-12-13 12:30 | 64.04 | 63.19
2017-12-13 13:00 | 63.43 | 62.57
2017-12-13 13:30 | 63.76 | 62.91
2017-12-13 14:00 | 64.59 | 63.75
2017-12-13 14:30 | 62.19 | 61.26
2017-12-13 15:00 | 63.47 | 62.56
2017-12-13 15:30 | 65.66 | 64.79
2017-12-13 16:00 | 65.96 | 65.07
2017-12-13 16:30 | 66.68 | 65.76
2017-12-13 17:00 | 65.59 | 64.61
2017-12-13 17:30 | 63.85 | 62.68
2017-12-13 18:00 | 62.85 | 61.24
2017-12-13 18:30 | 65.84 | 59.28
2017-12-13 19:00 | 67.12 | 60.54
2017-12-13 19:30 | 67.62 | 61.19
2017-12-13 20:00 | 66.22 | 59.57
2017-12-13 20:30 | 64.02 | 57.01
2017-12-13 21:00 | 62.62 | 55.34
2017-12-13 21:30 | 59.1 | 52.4
2017-12-13 22:00 | 56.21 | 49.42
2017-12-13 22:30 | 54.23 | 47.04
2017-12-13 23:00 | 54.2 | 46.98
2017-12-13 23:30 | 51 | 43.12
2017-12-14 | 49.37 | 41.09
2017-12-14 00:30 | 48.37 | 39.78
2017-12-14 01:00 | 47.22 | 38.27
2017-12-14 01:30 | 46.47 | 37.28
2017-12-14 02:00 | 46.01 | 36.67
2017-12-14 02:30 | 42.27 | 33.88
2017-12-14 03:00 | 44.97 | 35.26
2017-12-14 03:30 | 44.47 | 34.9
2017-12-14 04:00 | 44.24 | 34.88
2017-12-14 04:30 | 44.14 | 35.24
2017-12-14 05:00 | 44.72 | 36.12
2017-12-14 05:30 | 45.99 | 37.77
2017-12-14 06:00 | 48.18 | 40.62
2017-12-14 06:30 | 49.88 | 46.6
2017-12-14 07:00 | 53.71 | 50.85
2017-12-14 07:30 | 58.89 | 56.86
2017-12-14 08:00 | 61.3 | 60.69
2017-12-14 08:30 | 63.28 | 62.8
2017-12-14 09:00 | 63.32 | 62.92
2017-12-14 09:30 | 64.71 | 64.35
2017-12-14 10:00 | 65.3 | 64.94
2017-12-14 10:30 | 65.28 | 64.91
2017-12-14 11:00 | 65.36 | 64.98
2017-12-14 11:30 | 65.47 | 65.09
2017-12-14 12:00 | 65.91 | 65.53
2017-12-14 12:30 | 66.03 | 65.66
2017-12-14 13:00 | 65.79 | 65.43
2017-12-14 13:30 | 66.61 | 66.24
2017-12-14 14:00 | 67.35 | 66.99
2017-12-14 14:30 | 67.42 | 67.05
2017-12-14 15:00 | 67.41 | 67.05
2017-12-14 15:30 | 67.64 | 67.29
2017-12-14 16:00 | 67.54 | 67.21
2017-12-14 16:30 | 68.14 | 67.76
2017-12-14 17:00 | 66.93 | 66.45
2017-12-14 17:30 | 64.94 | 64.08
2017-12-14 18:00 | 64.03 | 62.75
2017-12-14 18:30 | 63.09 | 61.36
2017-12-14 19:00 | 63.38 | 61.54
2017-12-14 19:30 | 63.58 | 61.86
2017-12-14 20:00 | 61.82 | 59.83
2017-12-14 20:30 | 60.15 | 57.83
2017-12-14 21:00 | 58.91 | 56.4
2017-12-14 21:30 | 54.84 | 53.13
2017-12-14 22:00 | 51.21 | 50.22
2017-12-14 22:30 | 48.81 | 47.74
2017-12-14 23:00 | 48.51 | 47.42
2017-12-14 23:30 | 44.13 | 42.89
2017-12-15 | 41.9 | 40.55
2017-12-15 00:30 | 40.61 | 39.19
2017-12-15 01:00 | 38.82 | 37.31
2017-12-15 01:30 | 38.01 | 36.46
2017-12-15 02:00 | 37.22 | 35.63
2017-12-15 02:30 | 36.32 | 34.82
2017-12-15 03:00 | 36.03 | 34.56
2017-12-15 03:30 | 35.83 | 34.35
2017-12-15 04:00 | 35.66 | 34.21
2017-12-15 04:30 | 35.94 | 34.64
2017-12-15 05:00 | 36.72 | 35.46
2017-12-15 05:30 | 38.71 | 37.56
2017-12-15 06:00 | 41.55 | 40.53
2017-12-15 06:30 | 46.97 | 46.13
2017-12-15 07:00 | 51.62 | 50.79
2017-12-15 07:30 | 57.73 | 57.1
2017-12-15 08:00 | 61.2 | 60.58
2017-12-15 08:30 | 63.89 | 63.05
2017-12-15 09:00 | 63.86 | 63.46
2017-12-15 09:30 | 64.78 | 64.38
2017-12-15 10:00 | 64.94 | 64.52
2017-12-15 10:30 | 65.21 | 64.79
2017-12-15 11:00 | 65.74 | 65.31
2017-12-15 11:30 | 66.35 | 65.92
2017-12-15 12:00 | 66.96 | 66.52
2017-12-15 12:30 | 67.71 | 67.28
2017-12-15 13:00 | 67.56 | 67.13
2017-12-15 13:30 | 68.28 | 67.92
2017-12-15 14:00 | 67.91 | 67.56
2017-12-15 14:30 | 67.27 | 66.93
2017-12-15 15:00 | 67.1 | 66.76
2017-12-15 15:30 | 66.35 | 65.96
2017-12-15 16:00 | 66.46 | 66.02
2017-12-15 16:30 | 67.6 | 67.13
2017-12-15 17:00 | 66.38 | 65.73
2017-12-15 17:30 | 64.57 | 63.38
2017-12-15 18:00 | 63.45 | 61.7
2017-12-15 18:30 | 61.41 | 59.05
2017-12-15 19:00 | 60.79 | 58.32
2017-12-15 19:30 | 61.06 | 58.63
2017-12-15 20:00 | 59.85 | 57.17
2017-12-15 20:30 | 56.67 | 54.81
2017-12-15 21:00 | 55.05 | 52.92
2017-12-15 21:30 | 50.86 | 50.67
2017-12-15 22:00 | 48.9 | 48.87
2017-12-15 22:30 | 46.74 | 46.72
2017-12-15 23:00 | 46.2 | 46.17
2017-12-15 23:30 | 42.56 | 42.51
2017-12-16 | 40.29 | 40.22
2017-12-16 00:30 | 38.81 | 38.75
2017-12-16 01:00 | 37.13 | 37.09
2017-12-16 01:30 | 36.39 | 36.36
2017-12-16 02:00 | 35.84 | 35.81
2017-12-16 02:30 | 34.85 | 34.82
2017-12-16 03:00 | 34.5 | 34.47
2017-12-16 03:30 | 34.18 | 34.16
2017-12-16 04:00 | 33.75 | 33.72
2017-12-16 04:30 | 34.06 | 34.03
2017-12-16 05:00 | 34.1 | 34.08
2017-12-16 05:30 | 34.24 | 34.21
2017-12-16 06:00 | 35.31 | 35.28
2017-12-16 06:30 | 37.92 | 37.86
2017-12-16 07:00 | 39.22 | 39.12
2017-12-16 07:30 | 42.98 | 42.72
2017-12-16 08:00 | 46.5 | 46.02
2017-12-16 08:30 | 49.63 | 48.86
2017-12-16 09:00 | 52.29 | 51.17
2017-12-16 09:30 | 55.16 | 52.99
2017-12-16 10:00 | 55.43 | 52.52
2017-12-16 10:30 | 55.14 | 52.21
2017-12-16 11:00 | 55.19 | 52.24
2017-12-16 11:30 | 55.64 | 52.71
2017-12-16 12:00 | 55.92 | 53.03
2017-12-16 12:30 | 54.85 | 51.93
2017-12-16 13:00 | 54.05 | 51.1
2017-12-16 13:30 | 55.23 | 52.36
2017-12-16 14:00 | 54.23 | 51.33
2017-12-16 14:30 | 54.29 | 51.41
2017-12-16 15:00 | 54.94 | 52.12
2017-12-16 15:30 | 55.55 | 52.76
2017-12-16 16:00 | 56.31 | 53.59
2017-12-16 16:30 | 57.37 | 54.73
2017-12-16 17:00 | 57.66 | 55.06
2017-12-16 17:30 | 57.7 | 55.13
2017-12-16 18:00 | 58.16 | 55.61
2017-12-16 18:30 | 57.98 | 55.43
2017-12-16 19:00 | 57.8 | 55.24
2017-12-16 19:30 | 57.68 | 55.09
2017-12-16 20:00 | 56.57 | 53.94
2017-12-16 20:30 | 54.83 | 52.12
2017-12-16 21:00 | 53.54 | 50.77
2017-12-16 21:30 | 52.05 | 49.19
2017-12-16 22:00 | 50.41 | 47.47
2017-12-16 22:30 | 48.66 | 45.62
2017-12-16 23:00 | 48.5 | 45.45
2017-12-16 23:30 | 44.92 | 41.6
2017-12-17 | 43.1 | 39.66
2017-12-17 00:30 | 42.06 | 38.54
2017-12-17 01:00 | 37.45 | 36.99
2017-12-17 01:30 | 36.56 | 36.51
2017-12-17 02:00 | 35.9 | 35.85
2017-12-17 02:30 | 35.12 | 35.08
2017-12-17 03:00 | 34.8 | 34.77
2017-12-17 03:30 | 34.84 | 34.81
2017-12-17 04:00 | 34.49 | 34.46
2017-12-17 04:30 | 34.24 | 34.2
2017-12-17 05:00 | 34.17 | 34.14
2017-12-17 05:30 | 33.99 | 33.97
2017-12-17 06:00 | 34.1 | 34.08
2017-12-17 06:30 | 35.81 | 35.77
2017-12-17 07:00 | 37.27 | 37.21
2017-12-17 07:30 | 39.64 | 39.52
2017-12-17 08:00 | 41.02 | 40.83
2017-12-17 08:30 | 42.19 | 41.93
2017-12-17 09:00 | 43.13 | 42.71
2017-12-17 09:30 | 43.97 | 43.49
2017-12-17 10:00 | 43.93 | 43.33
2017-12-17 10:30 | 44.66 | 43.94
2017-12-17 11:00 | 44.47 | 43.74
2017-12-17 11:30 | 44.88 | 44.06
2017-12-17 12:00 | 45.79 | 44.94
2017-12-17 12:30 | 45.72 | 44.96
2017-12-17 13:00 | 45.03 | 44.35
2017-12-17 13:30 | 45.03 | 44.36
2017-12-17 14:00 | 45.04 | 44.42
2017-12-17 14:30 | 44.69 | 44.15
2017-12-17 15:00 | 45.77 | 45.22
2017-12-17 15:30 | 46.14 | 45.68
2017-12-17 16:00 | 47.42 | 47
2017-12-17 16:30 | 49.4 | 49.01
2017-12-17 17:00 | 49.52 | 49.17
2017-12-17 17:30 | 50.97 | 50.67
2017-12-17 18:00 | 51.68 | 51.42
2017-12-17 18:30 | 52.26 | 52.02
2017-12-17 19:00 | 52.39 | 52.14
2017-12-17 19:30 | 53.47 | 53.13
2017-12-17 20:00 | 52.59 | 52.29
2017-12-17 20:30 | 50.66 | 50.4
2017-12-17 21:00 | 49.25 | 49.03
2017-12-17 21:30 | 47.09 | 46.93
2017-12-17 22:00 | 45.2 | 45.08
2017-12-17 22:30 | 43.01 | 42.92
2017-12-17 23:00 | 42.82 | 42.75
2017-12-17 23:30 | 39.25 | 39.18
2017-12-18 | 37.57 | 37.52
2017-12-18 00:30 | 36.96 | 36.91
2017-12-18 01:00 | 35.52 | 35.48
2017-12-18 01:30 | 35.08 | 35.04
2017-12-18 02:00 | 34.78 | 34.75
2017-12-18 02:30 | 34.16 | 34.13
2017-12-18 03:00 | 33.93 | 33.9
2017-12-18 03:30 | 33.86 | 33.83
2017-12-18 04:00 | 33.99 | 33.96
2017-12-18 04:30 | 34.78 | 34.75
2017-12-18 05:00 | 35.55 | 35.51
2017-12-18 05:30 | 37.82 | 37.75
2017-12-18 06:00 | 40.66 | 40.53
2017-12-18 06:30 | 46.79 | 46.32
2017-12-18 07:00 | 52.29 | 51.81
2017-12-18 07:30 | 59.16 | 58.6
2017-12-18 08:00 | 64.61 | 63.67
2017-12-18 08:30 | 67.89 | 65.58
2017-12-18 09:00 | 69.48 | 67.2
2017-12-18 09:30 | 70.29 | 68.05
2017-12-18 10:00 | 68.66 | 66.47
2017-12-18 10:30 | 69.12 | 67.28
2017-12-18 11:00 | 69.11 | 67.23
2017-12-18 11:30 | 69.91 | 68.05
2017-12-18 12:00 | 70.21 | 68.35
2017-12-18 12:30 | 70.25 | 68.42
2017-12-18 13:00 | 69.5 | 67.66
2017-12-18 13:30 | 70.77 | 68.96
2017-12-18 14:00 | 70.9 | 69.11
2017-12-18 14:30 | 70.78 | 68.99
2017-12-18 15:00 | 71 | 69.22
2017-12-18 15:30 | 70.98 | 69.22
2017-12-18 16:00 | 70.13 | 68.36
2017-12-18 16:30 | 70.12 | 68.41
2017-12-18 17:00 | 68.15 | 66.44
2017-12-18 17:30 | 64.21 | 63.2
2017-12-18 18:00 | 52.19 | 50.99
2017-12-18 18:30 | 62.69 | 60.72
2017-12-18 19:00 | 62.59 | 60.44
2017-12-18 19:30 | 62.3 | 60.26
2017-12-18 20:00 | 60.78 | 58.54
2017-12-18 20:30 | 58.68 | 56.02
2017-12-18 21:00 | 57.13 | 54.1
2017-12-18 21:30 | 55.49 | 51.47
2017-12-18 22:00 | 53.21 | 49.03
2017-12-18 22:30 | 49.91 | 46.43
2017-12-18 23:00 | 49.4 | 45.87
2017-12-18 23:30 | 46.08 | 42.2
2017-12-19 | 44.01 | 39.88
2017-12-19 00:30 | 42.55 | 38.18
2017-12-19 01:00 | 41.03 | 36.44
2017-12-19 01:30 | 40.22 | 35.51
2017-12-19 02:00 | 39.85 | 35.03
2017-12-19 02:30 | 38.75 | 34.09
2017-12-19 03:00 | 38.37 | 33.69
2017-12-19 03:30 | 38.25 | 33.52
2017-12-19 04:00 | 38.12 | 33.37
2017-12-19 04:30 | 38.67 | 34.04
2017-12-19 05:00 | 39.34 | 34.83
2017-12-19 05:30 | 40.84 | 36.57
2017-12-19 06:00 | 43.05 | 39.14
2017-12-19 06:30 | 47.78 | 44.85
2017-12-19 07:00 | 49.48 | 49.17
2017-12-19 07:30 | 55.45 | 54.58
2017-12-19 08:00 | 61.17 | 59.27
2017-12-19 08:30 | 64.2 | 62.17
2017-12-19 09:00 | 65.78 | 63.78
2017-12-19 09:30 | 66.25 | 64.23
2017-12-19 10:00 | 66.46 | 64.41
2017-12-19 10:30 | 67.26 | 65.23
2017-12-19 11:00 | 68.79 | 66.77
2017-12-19 11:30 | 69.71 | 67.72
2017-12-19 12:00 | 69.99 | 68.01
2017-12-19 12:30 | 69.88 | 67.93
2017-12-19 13:00 | 70.35 | 68.4
2017-12-19 13:30 | 70.21 | 68.26
2017-12-19 14:00 | 70.69 | 68.76
2017-12-19 14:30 | 71.5 | 69.6
2017-12-19 15:00 | 71.29 | 69.39
2017-12-19 15:30 | 71.55 | 69.67
2017-12-19 16:00 | 71.35 | 69.62
2017-12-19 16:30 | 71.57 | 69.88
2017-12-19 17:00 | 69.69 | 68.01
2017-12-19 17:30 | 66.03 | 65.13
2017-12-19 18:00 | 64.96 | 63.73
2017-12-19 18:30 | 64.16 | 62.46
2017-12-19 19:00 | 63.78 | 61.95
2017-12-19 19:30 | 64.05 | 62.41
2017-12-19 20:00 | 62.72 | 60.88
2017-12-19 20:30 | 60.73 | 58.49
2017-12-19 21:00 | 58.26 | 56.51
2017-12-19 21:30 | 55.67 | 53.91
2017-12-19 22:00 | 53.68 | 51.49
2017-12-19 22:30 | 50.9 | 48.52
2017-12-19 23:00 | 47.15 | 46.95
2017-12-19 23:30 | 42.95 | 42.8
2017-12-20 | 40.54 | 40.42
2017-12-20 00:30 | 38.77 | 38.68
2017-12-20 01:00 | 37.08 | 37
2017-12-20 01:30 | 36.16 | 36.09
2017-12-20 02:00 | 35.31 | 35.25
2017-12-20 02:30 | 34.88 | 34.83
2017-12-20 03:00 | 34.57 | 34.52
2017-12-20 03:30 | 33.86 | 33.82
2017-12-20 04:00 | 33.79 | 33.75
2017-12-20 04:30 | 34.59 | 34.54
2017-12-20 05:00 | 35.49 | 35.44
2017-12-20 05:30 | 37 | 36.93
2017-12-20 06:00 | 39.94 | 39.82
2017-12-20 06:30 | 46.29 | 45.77
2017-12-20 07:00 | 50.58 | 50.42
2017-12-20 07:30 | 45.55 | 45.24
2017-12-20 08:00 | 44.43 | 43.72
2017-12-20 08:30 | 47.42 | 46.33
2017-12-20 09:00 | 49.81 | 48.4
2017-12-20 09:30 | 51.73 | 49.99
2017-12-20 10:00 | 52.66 | 50.84
2017-12-20 10:30 | 52.83 | 50.98
2017-12-20 11:00 | 52.57 | 50.56
2017-12-20 11:30 | 53.52 | 51.41
2017-12-20 12:00 | 53.99 | 51.87
2017-12-20 12:30 | 55.31 | 53.22
2017-12-20 13:00 | 55.3 | 53.11
2017-12-20 13:30 | 55.01 | 52.88
2017-12-20 14:00 | 55.55 | 53.45
2017-12-20 14:30 | 55.64 | 53.58
2017-12-20 15:00 | 55.86 | 53.87
2017-12-20 15:30 | 56.37 | 54.46
2017-12-20 16:00 | 58.42 | 55.94
2017-12-20 16:30 | 76.17 | 69.77
2017-12-20 17:00 | 75.54 | 68.79
2017-12-20 17:30 | 73.05 | 65.44
2017-12-20 18:00 | 68.07 | 63.61
2017-12-20 18:30 | 67.07 | 62.15
2017-12-20 19:00 | 66.76 | 61.74
2017-12-20 19:30 | 66.87 | 61.93
2017-12-20 20:00 | 65.5 | 60.29
2017-12-20 20:30 | 63.61 | 57.98
2017-12-20 21:00 | 62.07 | 56.11
2017-12-20 21:30 | 58.48 | 53.21
2017-12-20 22:00 | 55.73 | 50.46
2017-12-20 22:30 | 53.41 | 47.62
2017-12-20 23:00 | 52.29 | 45.93
2017-12-20 23:30 | 49.01 | 41.87
2017-12-21 | 47.21 | 39.81
2017-12-21 00:30 | 45.77 | 38.26
2017-12-21 01:00 | 44.19 | 36.49
2017-12-21 01:30 | 43.49 | 35.65
2017-12-21 02:00 | 42.56 | 34.58
2017-12-21 02:30 | 41.96 | 34.01
2017-12-21 03:00 | 41.42 | 33.46
2017-12-21 03:30 | 41.28 | 33.3
2017-12-21 04:00 | 41.39 | 33.38
2017-12-21 04:30 | 42.21 | 34.28
2017-12-21 05:00 | 42.74 | 34.84
2017-12-21 05:30 | 44.04 | 36.24
2017-12-21 06:00 | 46.32 | 38.74
2017-12-21 06:30 | 51.21 | 43.85
2017-12-21 07:00 | 55.11 | 48.31
2017-12-21 07:30 | 60.1 | 53.77
2017-12-21 08:00 | 62.98 | 56.87
2017-12-21 08:30 | 66.61 | 60.33
2017-12-21 09:00 | 69.51 | 62.14
2017-12-21 09:30 | 69.5 | 63.32
2017-12-21 10:00 | 70.27 | 63.34
2017-12-21 10:30 | 70.79 | 64.22
2017-12-21 11:00 | 71.1 | 64.7
2017-12-21 11:30 | 71.73 | 65.5
2017-12-21 12:00 | 72.24 | 66.08
2017-12-21 12:30 | 72.46 | 66.24
2017-12-21 13:00 | 72.38 | 66.1
2017-12-21 13:30 | 72.89 | 66.7
2017-12-21 14:00 | 73.5 | 67.45
2017-12-21 14:30 | 73.67 | 67.56
2017-12-21 15:00 | 73.44 | 67.1
2017-12-21 15:30 | 74 | 67.59
2017-12-21 16:00 | 74.14 | 67.54
2017-12-21 16:30 | 75.01 | 68.24
2017-12-21 17:00 | 74.58 | 67.51
2017-12-21 17:30 | 71.72 | 65.03
2017-12-21 18:00 | 68.45 | 64.07
2017-12-21 18:30 | 67.37 | 62.57
2017-12-21 19:00 | 67.58 | 62.8
2017-12-21 19:30 | 68.17 | 63.53
2017-12-21 20:00 | 66.94 | 62.02
2017-12-21 20:30 | 65.25 | 59.94
2017-12-21 21:00 | 63.03 | 57.77
2017-12-21 21:30 | 60.04 | 55.07
2017-12-21 22:00 | 57.13 | 52.05
2017-12-21 22:30 | 54.82 | 49.62
2017-12-21 23:00 | 53.83 | 48.7
2017-12-21 23:30 | 50.36 | 44.98
2017-12-22 | 48.25 | 42.76
2017-12-22 00:30 | 46.44 | 40.81
2017-12-22 01:00 | 45.01 | 38.46
2017-12-22 01:30 | 44.18 | 37.52
2017-12-22 02:00 | 43.58 | 36.83
2017-12-22 02:30 | 42.89 | 36.07
2017-12-22 03:00 | 42.45 | 35.61
2017-12-22 03:30 | 42.21 | 35.33
2017-12-22 04:00 | 42.26 | 35.39
2017-12-22 04:30 | 42.42 | 35.57
2017-12-22 05:00 | 43.11 | 36.28
2017-12-22 05:30 | 44.22 | 37.46
2017-12-22 06:00 | 46.17 | 39.53
2017-12-22 06:30 | 50.57 | 44.02
2017-12-22 07:00 | 54.52 | 48.43
2017-12-22 07:30 | 60.18 | 54.3
2017-12-22 08:00 | 64.19 | 58.29
2017-12-22 08:30 | 64.44 | 59.61
2017-12-22 09:00 | 66.49 | 62.81
2017-12-22 09:30 | 65.98 | 62.3
2017-12-22 10:00 | 65.35 | 61.54
2017-12-22 10:30 | 65.5 | 61.66
2017-12-22 11:00 | 66.14 | 62.29
2017-12-22 11:30 | 66.02 | 62.27
2017-12-22 12:00 | 65.75 | 61.86
2017-12-22 12:30 | 65.84 | 62.12
2017-12-22 13:00 | 66.42 | 62.75
2017-12-22 13:30 | 64 | 60.03
2017-12-22 14:00 | 63.27 | 59.14
2017-12-22 14:30 | 63 | 58.75
2017-12-22 15:00 | 62.99 | 58.66
2017-12-22 15:30 | 63.16 | 58.68
2017-12-22 16:00 | 64.2 | 59.71
2017-12-22 16:30 | 65.58 | 61.02
2017-12-22 17:00 | 64.2 | 59.41
2017-12-22 17:30 | 64.03 | 58.84
2017-12-22 18:00 | 63.16 | 57.65
2017-12-22 18:30 | 60.9 | 56.48
2017-12-22 19:00 | 60.85 | 56.41
2017-12-22 19:30 | 60.86 | 56.51
2017-12-22 20:00 | 59.86 | 55.3
2017-12-22 20:30 | 58.31 | 53.46
2017-12-22 21:00 | 56.8 | 51.68
2017-12-22 21:30 | 55.34 | 49.87
2017-12-22 22:00 | 53.6 | 47.62
2017-12-22 22:30 | 52 | 45.44
2017-12-22 23:00 | 51.27 | 44.64
2017-12-22 23:30 | 48.24 | 41.23
2017-12-23 | 45.29 | 38.08
2017-12-23 00:30 | 44.68 | 37.38
2017-12-23 01:00 | 42.87 | 35.35
2017-12-23 01:30 | 42.1 | 34.42
2017-12-23 02:00 | 41.55 | 33.8
2017-12-23 02:30 | 40.81 | 32.99
2017-12-23 03:00 | 40.18 | 32.25
2017-12-23 03:30 | 39.72 | 31.74
2017-12-23 04:00 | 39.48 | 31.48
2017-12-23 04:30 | 39.52 | 31.49
2017-12-23 05:00 | 39.78 | 31.78
2017-12-23 05:30 | 39.59 | 31.5
2017-12-23 06:00 | 40.61 | 31.73
2017-12-23 06:30 | 42.14 | 33.41
2017-12-23 07:00 | 43.59 | 34.98
2017-12-23 07:30 | 45.45 | 37.01
2017-12-23 08:00 | 46.53 | 38
2017-12-23 08:30 | 47.69 | 40.41
2017-12-23 09:00 | 48.74 | 42.2
2017-12-23 09:30 | 49.22 | 42.99
2017-12-23 10:00 | 49.66 | 43.73
2017-12-23 10:30 | 49.89 | 44.16
2017-12-23 11:00 | 50.3 | 44.75
2017-12-23 11:30 | 50.55 | 45.08
2017-12-23 12:00 | 51.58 | 46.28
2017-12-23 12:30 | 51.05 | 45.61
2017-12-23 13:00 | 50.92 | 45.46
2017-12-23 13:30 | 52.98 | 47.74
2017-12-23 14:00 | 51.05 | 45.5
2017-12-23 14:30 | 50.32 | 44.68
2017-12-23 15:00 | 51.7 | 46.3
2017-12-23 15:30 | 52.12 | 46.71
2017-12-23 16:00 | 53.09 | 47.72
2017-12-23 16:30 | 54.53 | 49.19
2017-12-23 17:00 | 54.55 | 49.1
2017-12-23 17:30 | 55.85 | 50.52
2017-12-23 18:00 | 56.94 | 51.73
2017-12-23 18:30 | 56.82 | 51.48
2017-12-23 19:00 | 56.58 | 51.2
2017-12-23 19:30 | 56.58 | 51.3
2017-12-23 20:00 | 55.81 | 50.33
2017-12-23 20:30 | 54.41 | 48.61
2017-12-23 21:00 | 53.34 | 47.27
2017-12-23 21:30 | 52.21 | 45.8
2017-12-23 22:00 | 51.04 | 44.28
2017-12-23 22:30 | 49.57 | 42.35
2017-12-23 23:00 | 49.52 | 42.14
2017-12-23 23:30 | 46.87 | 38.66
2017-12-24 | 45.45 | 36.59
2017-12-24 00:30 | 44.68 | 35.29
2017-12-24 01:00 | 42.13 | 33.32
2017-12-24 01:30 | 41.42 | 32.57
2017-12-24 02:00 | 41.03 | 32.13
2017-12-24 02:30 | 40.42 | 31.46
2017-12-24 03:00 | 40.04 | 31.02
2017-12-24 03:30 | 39.74 | 30.67
2017-12-24 04:00 | 39.67 | 30.55
2017-12-24 04:30 | 39.64 | 30.48
2017-12-24 05:00 | 37.15 | 26.94
2017-12-24 05:30 | 35.13 | 24.25
2017-12-24 06:00 | 39.22 | 30.14
2017-12-24 06:30 | 40.04 | 31.09
2017-12-24 07:00 | 41.37 | 32.57
2017-12-24 07:30 | 43.19 | 34.55
2017-12-24 08:00 | 44.89 | 36.28
2017-12-24 08:30 | 46.41 | 37.94
2017-12-24 09:00 | 47.5 | 39.22
2017-12-24 09:30 | 48.77 | 41.29
2017-12-24 10:00 | 49.1 | 41.56
2017-12-24 10:30 | 49.77 | 42.26
2017-12-24 11:00 | 50.54 | 43.05
2017-12-24 11:30 | 51.02 | 43.52
2017-12-24 12:00 | 51.62 | 44.2
2017-12-24 12:30 | 51.96 | 44.61
2017-12-24 13:00 | 51.87 | 44.5
2017-12-24 13:30 | 52.35 | 45.08
2017-12-24 14:00 | 53.01 | 45.8
2017-12-24 14:30 | 52.31 | 46.19
2017-12-24 15:00 | 52.23 | 46.9
2017-12-24 15:30 | 52.89 | 47.7
2017-12-24 16:00 | 53.17 | 48.13
2017-12-24 16:30 | 54.75 | 49.9
2017-12-24 17:00 | 55.06 | 50.27
2017-12-24 17:30 | 55.46 | 50.81
2017-12-24 18:00 | 55.47 | 50.9
2017-12-24 18:30 | 54.98 | 50.42
2017-12-24 19:00 | 54.17 | 49.59
2017-12-24 19:30 | 54.39 | 49.73
2017-12-24 20:00 | 54.08 | 49.41
2017-12-24 20:30 | 52.63 | 47.89
2017-12-24 21:00 | 51.52 | 46.66
2017-12-24 21:30 | 50.2 | 45.06
2017-12-24 22:00 | 49.11 | 43.64
2017-12-24 22:30 | 47.48 | 41.55
2017-12-24 23:00 | 47.19 | 41.07
2017-12-24 23:30 | 44.48 | 37.65
2017-12-25 | 42.96 | 35.62
2017-12-25 00:30 | 42.32 | 34.67
2017-12-25 01:00 | 40.89 | 32.77
2017-12-25 01:30 | 40.34 | 31.97
2017-12-25 02:00 | 39.81 | 31.17
2017-12-25 02:30 | 38.74 | 30.55
2017-12-25 03:00 | 37.83 | 30.05
2017-12-25 03:30 | 37.58 | 29.67
2017-12-25 04:00 | 37.48 | 29.53
2017-12-25 04:30 | 37.26 | 29.25
2017-12-25 05:00 | 37.43 | 29.55
2017-12-25 05:30 | 37.43 | 29.44
2017-12-25 06:00 | 37.81 | 29.89
2017-12-25 06:30 | 39.13 | 31.97
2017-12-25 07:00 | 40.13 | 33.41
2017-12-25 07:30 | 42.36 | 35.72
2017-12-25 08:00 | 43.72 | 37.04
2017-12-25 08:30 | 45.15 | 38.61
2017-12-25 09:00 | 45.87 | 39.8
2017-12-25 09:30 | 45.85 | 40.17
2017-12-25 10:00 | 45.55 | 39.76
2017-12-25 10:30 | 45.95 | 40.12
2017-12-25 11:00 | 46.31 | 40.46
2017-12-25 11:30 | 46.27 | 40.42
2017-12-25 12:00 | 46.05 | 40.13
2017-12-25 12:30 | 46.05 | 40.1
2017-12-25 13:00 | 45.52 | 39.43
2017-12-25 13:30 | 45.26 | 39.13
2017-12-25 14:00 | 45.52 | 39.43
2017-12-25 14:30 | 45.66 | 39.66
2017-12-25 15:00 | 46.64 | 40.76
2017-12-25 15:30 | 47.62 | 41.92
2017-12-25 16:00 | 48.33 | 42.77
2017-12-25 16:30 | 50.09 | 44.8
2017-12-25 17:00 | 50.44 | 45.24
2017-12-25 17:30 | 50.99 | 45.96
2017-12-25 18:00 | 51.19 | 46.25
2017-12-25 18:30 | 50.69 | 45.54
2017-12-25 19:00 | 50.51 | 45.24
2017-12-25 19:30 | 50.85 | 45.78
2017-12-25 20:00 | 50.68 | 45.56
2017-12-25 20:30 | 49.86 | 44.52
2017-12-25 21:00 | 49.07 | 43.52
2017-12-25 21:30 | 48.37 | 42.62
2017-12-25 22:00 | 47.2 | 41.14
2017-12-25 22:30 | 45.87 | 39.39
2017-12-25 23:00 | 45.62 | 39
2017-12-25 23:30 | 43.21 | 35.9
2017-12-26 | 42.06 | 34.36
2017-12-26 00:30 | 41.56 | 33.58
2017-12-26 01:00 | 40.7 | 32.45
2017-12-26 01:30 | 40.3 | 31.85
2017-12-26 02:00 | 39.66 | 31.02
2017-12-26 02:30 | 37.89 | 30.07
2017-12-26 03:00 | 37.77 | 29.89
2017-12-26 03:30 | 37.5 | 29.49
2017-12-26 04:00 | 37.28 | 29.18
2017-12-26 04:30 | 37.31 | 29.27
2017-12-26 05:00 | 37.39 | 29.4
2017-12-26 05:30 | 37.31 | 29.24
2017-12-26 06:00 | 37.46 | 29.41
2017-12-26 06:30 | 38.74 | 31.39
2017-12-26 07:00 | 39.54 | 32.66
2017-12-26 07:30 | 41.78 | 35.01
2017-12-26 08:00 | 44.41 | 37.75
2017-12-26 08:30 | 45.44 | 39.12
2017-12-26 09:00 | 45.77 | 39.88
2017-12-26 09:30 | 46.42 | 40.46
2017-12-26 10:00 | 46.41 | 40.37
2017-12-26 10:30 | 46.73 | 40.68
2017-12-26 11:00 | 47.22 | 41.11
2017-12-26 11:30 | 47.51 | 41.38
2017-12-26 12:00 | 47.98 | 41.9
2017-12-26 12:30 | 48.7 | 42.68
2017-12-26 13:00 | 48.8 | 42.78
2017-12-26 13:30 | 49.59 | 43.62
2017-12-26 14:00 | 50.3 | 44.4
2017-12-26 14:30 | 50.82 | 45.02
2017-12-26 15:00 | 52 | 46.32
2017-12-26 15:30 | 54.82 | 47.27
2017-12-26 16:00 | 55.84 | 48.21
2017-12-26 16:30 | 57.42 | 50.07
2017-12-26 17:00 | 58.5 | 51.37
2017-12-26 17:30 | 59.22 | 52.05
2017-12-26 18:00 | 59.94 | 52.72
2017-12-26 18:30 | 59.16 | 51.4
2017-12-26 19:00 | 58.85 | 50.93
2017-12-26 19:30 | 58.97 | 51.23
2017-12-26 20:00 | 55.61 | 47.4
2017-12-26 20:30 | 57.37 | 49.13
2017-12-26 21:00 | 55.23 | 47.47
2017-12-26 21:30 | 52.04 | 45.43
2017-12-26 22:00 | 50.36 | 43.18
2017-12-26 22:30 | 48.67 | 41.3
2017-12-26 23:00 | 48.11 | 41.21
2017-12-26 23:30 | 45.25 | 37.95
2017-12-27 | 43.66 | 36.14
2017-12-27 00:30 | 42.57 | 34.95
2017-12-27 01:00 | 41.4 | 33.55
2017-12-27 01:30 | 40.51 | 32.53
2017-12-27 02:00 | 40.68 | 32.71
2017-12-27 02:30 | 40.54 | 32.61
2017-12-27 03:00 | 40.29 | 32.26
2017-12-27 03:30 | 40.27 | 32.3
2017-12-27 04:00 | 39.86 | 31.82
2017-12-27 04:30 | 39.8 | 31.72
2017-12-27 05:00 | 41.05 | 33.1
2017-12-27 05:30 | 41.66 | 33.8
2017-12-27 06:00 | 42.45 | 34.65
2017-12-27 06:30 | 45.92 | 38.33
2017-12-27 07:00 | 48.14 | 40.5
2017-12-27 07:30 | 52.23 | 44.65
2017-12-27 08:00 | 55.56 | 47.93
2017-12-27 08:30 | 56.86 | 50.86
2017-12-27 09:00 | 58.12 | 52.27
2017-12-27 09:30 | 58.28 | 52.57
2017-12-27 10:00 | 58.13 | 52.57
2017-12-27 10:30 | 57.85 | 52.27
2017-12-27 11:00 | 58.39 | 53.06
2017-12-27 11:30 | 58.67 | 53.42
2017-12-27 12:00 | 60.14 | 54.42
2017-12-27 12:30 | 61.14 | 55.36
2017-12-27 13:00 | 61.5 | 55.76
2017-12-27 13:30 | 61.76 | 55.99
2017-12-27 14:00 | 62.57 | 56.95
2017-12-27 14:30 | 62.7 | 56.95
2017-12-27 15:00 | 63.47 | 57.74
2017-12-27 15:30 | 64.05 | 58.29
2017-12-27 16:00 | 64.64 | 58.88
2017-12-27 16:30 | 65.99 | 60.24
2017-12-27 17:00 | 65.64 | 59.68
2017-12-27 17:30 | 65.31 | 58.94
2017-12-27 18:00 | 64.53 | 57.58
2017-12-27 18:30 | 63.53 | 56.69
2017-12-27 19:00 | 63 | 56.49
2017-12-27 19:30 | 62.76 | 56.3
2017-12-27 20:00 | 62.14 | 55.52
2017-12-27 20:30 | 60.47 | 53.41
2017-12-27 21:00 | 59.24 | 51.85
2017-12-27 21:30 | 56.48 | 49.8
2017-12-27 22:00 | 51.57 | 46.57
2017-12-27 22:30 | 49.79 | 44.66
2017-12-27 23:00 | 49.4 | 44.2
2017-12-27 23:30 | 46.22 | 40.3
2017-12-28 | 44.64 | 38.28
2017-12-28 00:30 | 43.84 | 37.13
2017-12-28 01:00 | 42.7 | 35.65
2017-12-28 01:30 | 42.06 | 34.84
2017-12-28 02:00 | 41.64 | 34.27
2017-12-28 02:30 | 41.26 | 33.7
2017-12-28 03:00 | 40.86 | 33.11
2017-12-28 03:30 | 40.65 | 32.79
2017-12-28 04:00 | 40.66 | 32.79
2017-12-28 04:30 | 40.63 | 32.78
2017-12-28 05:00 | 40.73 | 32.95
2017-12-28 05:30 | 41.11 | 33.49
2017-12-28 06:00 | 41.96 | 34.71
2017-12-28 06:30 | 44.57 | 38.53
2017-12-28 07:00 | 46.39 | 40.66
2017-12-28 07:30 | 50.19 | 44.47
2017-12-28 08:00 | 53.33 | 47.54
2017-12-28 08:30 | 55.97 | 50.15
2017-12-28 09:00 | 60.78 | 54.05
2017-12-28 09:30 | 61.41 | 53.27
2017-12-28 10:00 | 58.43 | 54.15
2017-12-28 10:30 | 59.32 | 55.21
2017-12-28 11:00 | 59.4 | 55.19
2017-12-28 11:30 | 59.83 | 55.59
2017-12-28 12:00 | 60.36 | 56.18
2017-12-28 12:30 | 61.02 | 56.88
2017-12-28 13:00 | 61.15 | 57.03
2017-12-28 13:30 | 62.18 | 58.11
2017-12-28 14:00 | 61.94 | 57.85
2017-12-28 14:30 | 62.01 | 57.95
2017-12-28 15:00 | 62.56 | 58.61
2017-12-28 15:30 | 63.81 | 60.02
2017-12-28 16:00 | 64.36 | 60.62
2017-12-28 16:30 | 64.67 | 60.86
2017-12-28 17:00 | 63.99 | 59.97
2017-12-28 17:30 | 64.28 | 59.98
2017-12-28 18:00 | 64.18 | 59.66
2017-12-28 18:30 | 63.16 | 58.48
2017-12-28 19:00 | 62.4 | 58.2
2017-12-28 19:30 | 62.47 | 58.37
2017-12-28 20:00 | 61.88 | 57.67
2017-12-28 20:30 | 60.09 | 55.58
2017-12-28 21:00 | 58.79 | 54.05
2017-12-28 21:30 | 56.27 | 51.01
2017-12-28 22:00 | 53.9 | 48.03
2017-12-28 22:30 | 52.2 | 45.84
2017-12-28 23:00 | 51.66 | 45.09
2017-12-28 23:30 | 48.39 | 41.33
2017-12-29 | 46.57 | 39.33
2017-12-29 00:30 | 45.62 | 38.31
2017-12-29 01:00 | 44.2 | 36.71
2017-12-29 01:30 | 43.52 | 35.95
2017-12-29 02:00 | 43.05 | 35.42
2017-12-29 02:30 | 42.6 | 34.91
2017-12-29 03:00 | 42.23 | 34.45
2017-12-29 03:30 | 41.97 | 34.17
2017-12-29 04:00 | 41.73 | 33.87
2017-12-29 04:30 | 41.74 | 33.85
2017-12-29 05:00 | 42.04 | 34.12
2017-12-29 05:30 | 42.62 | 34.83
2017-12-29 06:00 | 44.18 | 36.51
2017-12-29 06:30 | 47.75 | 40.21
2017-12-29 07:00 | 50.84 | 43.35
2017-12-29 07:30 | 54.35 | 46.91
2017-12-29 08:00 | 56.64 | 49.93
2017-12-29 08:30 | 58.3 | 52.17
2017-12-29 09:00 | 58.23 | 53.72
2017-12-29 09:30 | 57.91 | 53.46
2017-12-29 10:00 | 58.42 | 54.14
2017-12-29 10:30 | 59.18 | 54.99
2017-12-29 11:00 | 60.13 | 55.93
2017-12-29 11:30 | 60.17 | 55.94
2017-12-29 12:00 | 60.57 | 56.43
2017-12-29 12:30 | 60.4 | 56.22
2017-12-29 13:00 | 60.25 | 56.07
2017-12-29 13:30 | 59.91 | 55.77
2017-12-29 14:00 | 59.87 | 55.77
2017-12-29 14:30 | 59.72 | 55.61
2017-12-29 15:00 | 60.38 | 56.3
2017-12-29 15:30 | 60.89 | 56.78
2017-12-29 16:00 | 61.6 | 57.48
2017-12-29 16:30 | 62.86 | 58.76
2017-12-29 17:00 | 63.16 | 59
2017-12-29 17:30 | 63.35 | 58.9
2017-12-29 18:00 | 61.76 | 57.18
2017-12-29 18:30 | 60.72 | 56.25
2017-12-29 19:00 | 60.54 | 56.03
2017-12-29 19:30 | 60.45 | 56.02
2017-12-29 20:00 | 59.65 | 55.06
2017-12-29 20:30 | 58.03 | 53.16
2017-12-29 21:00 | 56.72 | 51.54
2017-12-29 21:30 | 55.09 | 49.56
2017-12-29 22:00 | 53.32 | 47.32
2017-12-29 22:30 | 51.73 | 45.24
2017-12-29 23:00 | 51.45 | 44.82
2017-12-29 23:30 | 48.45 | 41.4
2017-12-30 | 46.54 | 39.32
2017-12-30 00:30 | 45.09 | 37.8
2017-12-30 01:00 | 43.9 | 36.37
2017-12-30 01:30 | 43.09 | 35.45
2017-12-30 02:00 | 42.58 | 34.87
2017-12-30 02:30 | 42.06 | 34.26
2017-12-30 03:00 | 41.66 | 33.82
2017-12-30 03:30 | 41.05 | 33.17
2017-12-30 04:00 | 40.71 | 32.75
2017-12-30 04:30 | 40.81 | 32.82
2017-12-30 05:00 | 41.3 | 33.43
2017-12-30 05:30 | 41.13 | 33.29
2017-12-30 06:00 | 40.89 | 33
2017-12-30 06:30 | 41.79 | 33.97
2017-12-30 07:00 | 43.46 | 35.7
2017-12-30 07:30 | 45.56 | 37.89
2017-12-30 08:00 | 47.63 | 39.99
2017-12-30 08:30 | 50.39 | 42.91
2017-12-30 09:00 | 52.04 | 45.1
2017-12-30 09:30 | 51.82 | 46.43
2017-12-30 10:00 | 52.06 | 46.89
2017-12-30 10:30 | 52.7 | 47.76
2017-12-30 11:00 | 52.85 | 48.03
2017-12-30 11:30 | 53.31 | 48.55
2017-12-30 12:00 | 53.26 | 48.52
2017-12-30 12:30 | 53.29 | 48.46
2017-12-30 13:00 | 53.47 | 48.7
2017-12-30 13:30 | 53.84 | 49.12
2017-12-30 14:00 | 54.43 | 49.76
2017-12-30 14:30 | 54.95 | 50.28
2017-12-30 15:00 | 55.87 | 51.26
2017-12-30 15:30 | 56.32 | 51.69
2017-12-30 16:00 | 57.37 | 52.83
2017-12-30 16:30 | 58.41 | 53.84
2017-12-30 17:00 | 58.89 | 54.3
2017-12-30 17:30 | 59.24 | 54.5
2017-12-30 18:00 | 60.05 | 55.32
2017-12-30 18:30 | 59.7 | 54.83
2017-12-30 19:00 | 59.43 | 54.56
2017-12-30 19:30 | 59.98 | 55.33
2017-12-30 20:00 | 59.61 | 54.88
2017-12-30 20:30 | 58.27 | 53.28
2017-12-30 21:00 | 57.07 | 51.81
2017-12-30 21:30 | 55.6 | 50.03
2017-12-30 22:00 | 54.49 | 48.66
2017-12-30 22:30 | 52.64 | 46.33
2017-12-30 23:00 | 52.39 | 45.9
2017-12-30 23:30 | 49.78 | 42.58
2017-12-31 | 48.01 | 40.67
2017-12-31 00:30 | 46.51 | 39.32
2017-12-31 01:00 | 45.59 | 38.28
2017-12-31 01:30 | 45.13 | 37.72
2017-12-31 02:00 | 44.5 | 37
2017-12-31 02:30 | 44.19 | 36.62
2017-12-31 03:00 | 43.59 | 35.97
2017-12-31 03:30 | 43.42 | 35.77
2017-12-31 04:00 | 43.3 | 35.61
2017-12-31 04:30 | 43.12 | 35.37
2017-12-31 05:00 | 43.05 | 35.31
2017-12-31 05:30 | 42.89 | 35.13
2017-12-31 06:00 | 42.34 | 34.56
2017-12-31 06:30 | 43.19 | 35.51
2017-12-31 07:00 | 44.14 | 36.51
2017-12-31 07:30 | 46.29 | 38.8
2017-12-31 08:00 | 48.2 | 40.85
2017-12-31 08:30 | 49.59 | 42.24
2017-12-31 09:00 | 50.72 | 43.39
2017-12-31 09:30 | 51.54 | 44.89
2017-12-31 10:00 | 51.45 | 45.71
2017-12-31 10:30 | 51.8 | 46.28
2017-12-31 11:00 | 52.4 | 47.08
2017-12-31 11:30 | 52.97 | 47.81
2017-12-31 12:00 | 53.53 | 48.5
2017-12-31 12:30 | 54.5 | 49.55
2017-12-31 13:00 | 55.14 | 50.3
2017-12-31 13:30 | 55.92 | 51.17
2017-12-31 14:00 | 56.73 | 52.05
2017-12-31 14:30 | 57.66 | 53.1
2017-12-31 15:00 | 58.58 | 54.13
2017-12-31 15:30 | 58.93 | 54.43
2017-12-31 16:00 | 59.91 | 55.47
2017-12-31 16:30 | 61.59 | 57.32
2017-12-31 17:00 | 61.58 | 57.23
2017-12-31 17:30 | 61.68 | 57.19
2017-12-31 18:00 | 61.84 | 57.28
2017-12-31 18:30 | 60.93 | 56.17
2017-12-31 19:00 | 60.22 | 55.42
2017-12-31 19:30 | 60.16 | 55.49
2017-12-31 20:00 | 59.22 | 54.39
2017-12-31 20:30 | 57.72 | 52.58
2017-12-31 21:00 | 56.44 | 51.04
2017-12-31 21:30 | 55.16 | 49.47
2017-12-31 22:00 | 54.7 | 48.86
2017-12-31 22:30 | 53.59 | 47.48
2017-12-31 23:00 | 53.59 | 47.39
2017-12-31 23:30 | 51.34 | 44.57
2018-01-01 | 49.93 | 42.8
2018-01-01 00:30 | 49.14 | 41.64
2018-01-01 01:00 | 48.36 | 40.65
2018-01-01 01:30 | 46.91 | 39.68
2018-01-01 02:00 | 45.99 | 38.81
2018-01-01 02:30 | 45.23 | 37.98
2018-01-01 03:00 | 44.72 | 37.38
2018-01-01 03:30 | 44.36 | 36.99
2018-01-01 04:00 | 44.11 | 36.66
2018-01-01 04:30 | 43.95 | 36.43
2018-01-01 05:00 | 44.03 | 36.48
2018-01-01 05:30 | 43.94 | 36.4
2018-01-01 06:00 | 43.89 | 36.35
2018-01-01 06:30 | 46.13 | 38.69
2018-01-01 07:00 | 47.51 | 40.08
2018-01-01 07:30 | 50.56 | 43.22
2018-01-01 08:00 | 52.71 | 45.42
2018-01-01 08:30 | 53.88 | 46.62
2018-01-01 09:00 | 55.1 | 47.86
2018-01-01 09:30 | 55.8 | 48.64
2018-01-01 10:00 | 54.67 | 49.14
2018-01-01 10:30 | 54.86 | 49.78
2018-01-01 11:00 | 55.25 | 50.68
2018-01-01 11:30 | 56.83 | 52.52
2018-01-01 12:00 | 57.81 | 53.58
2018-01-01 12:30 | 59.19 | 55.01
2018-01-01 13:00 | 60.16 | 56.04
2018-01-01 13:30 | 61.23 | 57.12
2018-01-01 14:00 | 62.95 | 58.93
2018-01-01 14:30 | 63.7 | 59.75
2018-01-01 15:00 | 64.62 | 60.69
2018-01-01 15:30 | 65.72 | 61.89
2018-01-01 16:00 | 66.46 | 62.7
2018-01-01 16:30 | 68.17 | 64.3
2018-01-01 17:00 | 68.59 | 63.57
2018-01-01 17:30 | 68.9 | 63.75
2018-01-01 18:00 | 68.55 | 63.16
2018-01-01 18:30 | 67.68 | 61.84
2018-01-01 19:00 | 67.48 | 61.49
2018-01-01 19:30 | 67.64 | 61.82
2018-01-01 20:00 | 67.14 | 61.3
2018-01-01 20:30 | 65.79 | 59.66
2018-01-01 21:00 | 63.86 | 57.28
2018-01-01 21:30 | 61.82 | 54.82
2018-01-01 22:00 | 59.77 | 52.18
2018-01-01 22:30 | 58.25 | 50.13
2018-01-01 23:00 | 57.81 | 49.47
2018-01-01 23:30 | 51.21 | 45.57
2018-01-02 | 49.47 | 43.37
2018-01-02 00:30 | 50.75 | 41.98
2018-01-02 01:00 | 49.3 | 40.3
2018-01-02 01:30 | 48.92 | 39.82
2018-01-02 02:00 | 48.43 | 39.22
2018-01-02 02:30 | 47.82 | 38.56
2018-01-02 03:00 | 47.12 | 37.71
2018-01-02 03:30 | 46.81 | 37.34
2018-01-02 04:00 | 46.21 | 36.56
2018-01-02 04:30 | 46.26 | 36.6
2018-01-02 05:00 | 46.9 | 37.3
2018-01-02 05:30 | 48.46 | 38.98
2018-01-02 06:00 | 50.21 | 40.92
2018-01-02 06:30 | 53.84 | 46.76
2018-01-02 07:00 | 57.54 | 50.94
2018-01-02 07:30 | 62.59 | 56.75
2018-01-02 08:00 | 66.57 | 60.95
2018-01-02 08:30 | 71.5 | 64.81
2018-01-02 09:00 | 73.25 | 67.14
2018-01-02 09:30 | 73.87 | 68.13
2018-01-02 10:00 | 74.03 | 68.47
2018-01-02 10:30 | 76.19 | 71
2018-01-02 11:00 | 78.41 | 73.53
2018-01-02 11:30 | 75.68 | 70.63
2018-01-02 12:00 | 77.3 | 72.55
2018-01-02 12:30 | 78.97 | 74.42
2018-01-02 13:00 | 80.6 | 76.26
2018-01-02 13:30 | 81.39 | 77.17
2018-01-02 14:00 | 82.65 | 78.6
2018-01-02 14:30 | 83.4 | 79.34
2018-01-02 15:00 | 84.97 | 81
2018-01-02 15:30 | 86.27 | 82.28
2018-01-02 16:00 | 84.87 | 80.64
2018-01-02 16:30 | 84.24 | 79.76
2018-01-02 17:00 | 84.99 | 80.32
2018-01-02 17:30 | 82.16 | 76.63
2018-01-02 18:00 | 79.96 | 73.55
2018-01-02 18:30 | 77.76 | 71.85
2018-01-02 19:00 | 76.67 | 71.64
2018-01-02 19:30 | 76.14 | 71.1
2018-01-02 20:00 | 73.2 | 67.69
2018-01-02 20:30 | 69.92 | 63.8
2018-01-02 21:00 | 67.16 | 60.48
2018-01-02 21:30 | 63.13 | 57.69
2018-01-02 22:00 | 59.29 | 54.72
2018-01-02 22:30 | 56.42 | 51.72
2018-01-02 23:00 | 57.92 | 50.45
2018-01-02 23:30 | 54.66 | 46.65
2018-01-03 | 52.64 | 44.42
2018-01-03 00:30 | 50.75 | 42.4
2018-01-03 01:00 | 49.34 | 40.77
2018-01-03 01:30 | 48.92 | 40.27
2018-01-03 02:00 | 48.67 | 39.94
2018-01-03 02:30 | 47.94 | 38.85
2018-01-03 03:00 | 48.13 | 38.36
2018-01-03 03:30 | 48.07 | 38.25
2018-01-03 04:00 | 47.97 | 38.12
2018-01-03 04:30 | 47.84 | 38.01
2018-01-03 05:00 | 48.55 | 38.72
2018-01-03 05:30 | 49.9 | 40.2
2018-01-03 06:00 | 51.43 | 41.91
2018-01-03 06:30 | 55.94 | 46.73
2018-01-03 07:00 | 59.45 | 50.99
2018-01-03 07:30 | 63.41 | 56.92
2018-01-03 08:00 | 66.88 | 61.69
2018-01-03 08:30 | 70.66 | 65.9
2018-01-03 09:00 | 73.48 | 69.01
2018-01-03 09:30 | 75.68 | 71.51
2018-01-03 10:00 | 76.45 | 72.39
2018-01-03 10:30 | 77.59 | 73.79
2018-01-03 11:00 | 78.99 | 75.43
2018-01-03 11:30 | 80.11 | 76.7
2018-01-03 12:00 | 80.97 | 77.7
2018-01-03 12:30 | 82.41 | 79.21
2018-01-03 13:00 | 82.84 | 79.68
2018-01-03 13:30 | 83.29 | 80.24
2018-01-03 14:00 | 84.77 | 81.84
2018-01-03 14:30 | 86.43 | 83.65
2018-01-03 15:00 | 86.94 | 84.16
2018-01-03 15:30 | 87.14 | 84.29
2018-01-03 16:00 | 85.31 | 82.19
2018-01-03 16:30 | 85.35 | 82.09
2018-01-03 17:00 | 84.54 | 81.02
2018-01-03 17:30 | 81.79 | 77.61
2018-01-03 18:00 | 78.42 | 73.46
2018-01-03 18:30 | 76.88 | 71.43
2018-01-03 19:00 | 76.83 | 71.33
2018-01-03 19:30 | 76.88 | 71.45
2018-01-03 20:00 | 75.47 | 69.79
2018-01-03 20:30 | 74.74 | 68.79
2018-01-03 21:00 | 75.87 | 69.97
2018-01-03 21:30 | 73.59 | 67.89
2018-01-03 22:00 | 63.96 | 60.1
2018-01-03 22:30 | 60.37 | 55.88
2018-01-03 23:00 | 59.74 | 52.98
2018-01-03 23:30 | 57.52 | 50.59
2018-01-04 | 55.57 | 48.46
2018-01-04 00:30 | 53.21 | 45.95
2018-01-04 01:00 | 51.95 | 44.54
2018-01-04 01:30 | 51.29 | 43.83
2018-01-04 02:00 | 50.64 | 43.12
2018-01-04 02:30 | 49.8 | 42.04
2018-01-04 03:00 | 49.99 | 41.48
2018-01-04 03:30 | 49.74 | 41.17
2018-01-04 04:00 | 49.46 | 40.87
2018-01-04 04:30 | 50.06 | 41.44
2018-01-04 05:00 | 50.92 | 42.34
2018-01-04 05:30 | 52.18 | 43.72
2018-01-04 06:00 | 53.78 | 45.42
2018-01-04 06:30 | 58.22 | 50.13
2018-01-04 07:00 | 62.48 | 55.16
2018-01-04 07:30 | 67.89 | 62.15
2018-01-04 08:00 | 71.4 | 66.89
2018-01-04 08:30 | 75.15 | 70.84
2018-01-04 09:00 | 77.1 | 73.13
2018-01-04 09:30 | 77.89 | 74.06
2018-01-04 10:00 | 78.05 | 74.33
2018-01-04 10:30 | 78.76 | 75.24
2018-01-04 11:00 | 79.85 | 76.5
2018-01-04 11:30 | 80.5 | 77.23
2018-01-04 12:00 | 82.12 | 79.03
2018-01-04 12:30 | 83.56 | 80.51
2018-01-04 13:00 | 83.1 | 80.02
2018-01-04 13:30 | 85.4 | 82.47
2018-01-04 14:00 | 86.4 | 83.54
2018-01-04 14:30 | 86.8 | 83.94
2018-01-04 15:00 | 86.9 | 84.01
2018-01-04 15:30 | 85.98 | 82.91
2018-01-04 16:00 | 85.42 | 82.19
2018-01-04 16:30 | 83.9 | 80.36
2018-01-04 17:00 | 82.2 | 78.3
2018-01-04 17:30 | 80.38 | 75.94
2018-01-04 18:00 | 79.91 | 75.11
2018-01-04 18:30 | 78.92 | 73.78
2018-01-04 19:00 | 78.64 | 73.4
2018-01-04 19:30 | 78.81 | 73.66
2018-01-04 20:00 | 77.86 | 72.54
2018-01-04 20:30 | 75.35 | 69.58
2018-01-04 21:00 | 73.01 | 66.75
2018-01-04 21:30 | 69.79 | 63.01
2018-01-04 22:00 | 62.4 | 58.99
2018-01-04 22:30 | 58.85 | 56.04
2018-01-04 23:00 | 57.2 | 54.11
2018-01-04 23:30 | 54.08 | 50.74
2018-01-05 | 52.16 | 48.69
2018-01-05 00:30 | 51.18 | 47.63
2018-01-05 01:00 | 46.07 | 41.99
2018-01-05 01:30 | 38.13 | 37.57
2018-01-05 02:00 | 37.17 | 37.15
2018-01-05 02:30 | 36.71 | 36.7
2018-01-05 03:00 | 36.11 | 36.1
2018-01-05 03:30 | 35.87 | 35.86
2018-01-05 04:00 | 35.95 | 35.81
2018-01-05 04:30 | 38.4 | 37.16
2018-01-05 05:00 | 44.17 | 44.14
2018-01-05 05:30 | 46.07 | 46.02
2018-01-05 06:00 | 48.08 | 48.02
2018-01-05 06:30 | 53.06 | 52.82
2018-01-05 07:00 | 59.98 | 57.83
2018-01-05 07:30 | 66.11 | 63.99
2018-01-05 08:00 | 70.16 | 68.49
2018-01-05 08:30 | 71.67 | 70.08
2018-01-05 09:00 | 72.77 | 71.19
2018-01-05 09:30 | 74.87 | 73.32
2018-01-05 10:00 | 76.16 | 74.64
2018-01-05 10:30 | 76.21 | 74.68
2018-01-05 11:00 | 76.05 | 74.5
2018-01-05 11:30 | 76.98 | 75.45
2018-01-05 12:00 | 75.78 | 74.23
2018-01-05 12:30 | 76.8 | 75.28
2018-01-05 13:00 | 75.74 | 74.19
2018-01-05 13:30 | 75.81 | 74.27
2018-01-05 14:00 | 78.03 | 76.54
2018-01-05 14:30 | 77.16 | 75.67
2018-01-05 15:00 | 75.59 | 74.09
2018-01-05 15:30 | 73.31 | 71.79
2018-01-05 16:00 | 71.28 | 69.73
2018-01-05 16:30 | 71.45 | 69.93
2018-01-05 17:00 | 69.66 | 68.14
2018-01-05 17:30 | 67 | 65.41
2018-01-05 18:00 | 64.93 | 63.1
2018-01-05 18:30 | 63.33 | 61.36
2018-01-05 19:00 | 63.95 | 62.07
2018-01-05 19:30 | 64.11 | 62.39
2018-01-05 20:00 | 62.03 | 61.34
2018-01-05 20:30 | 59.34 | 59.3
2018-01-05 21:00 | 57.45 | 57.43
2018-01-05 21:30 | 55.68 | 55.66
2018-01-05 22:00 | 53.36 | 53.34
2018-01-05 22:30 | 50.7 | 50.67
2018-01-05 23:00 | 49.45 | 49.35
2018-01-05 23:30 | 47.19 | 46.7
2018-01-06 | 46.13 | 45.48
2018-01-06 00:30 | 45.78 | 45.13
2018-01-06 01:00 | 43.13 | 42.45
2018-01-06 01:30 | 41.11 | 40.4
2018-01-06 02:00 | 40.58 | 39.86
2018-01-06 02:30 | 40.16 | 39.44
2018-01-06 03:00 | 39.77 | 39.04
2018-01-06 03:30 | 39.51 | 38.77
2018-01-06 04:00 | 39.09 | 38.35
2018-01-06 04:30 | 39.44 | 38.71
2018-01-06 05:00 | 39.75 | 39.02
2018-01-06 05:30 | 40.19 | 39.46
2018-01-06 06:00 | 40.04 | 39.31
2018-01-06 06:30 | 42.24 | 41.54
2018-01-06 07:00 | 44.27 | 43.58
2018-01-06 07:30 | 46.76 | 46.07
2018-01-06 08:00 | 48.81 | 48.1
2018-01-06 08:30 | 53.03 | 52.07
2018-01-06 09:00 | 57.15 | 55.42
2018-01-06 09:30 | 58.64 | 55.78
2018-01-06 10:00 | 57.34 | 55.29
2018-01-06 10:30 | 57.7 | 55.64
2018-01-06 11:00 | 55.94 | 53.83
2018-01-06 11:30 | 55.74 | 53.6
2018-01-06 12:00 | 58.75 | 56.74
2018-01-06 12:30 | 57.42 | 55.37
2018-01-06 13:00 | 56.03 | 53.95
2018-01-06 13:30 | 55.98 | 53.91
2018-01-06 14:00 | 56.44 | 54.4
2018-01-06 14:30 | 56.39 | 54.37
2018-01-06 15:00 | 56.66 | 54.66
2018-01-06 15:30 | 57.55 | 55.58
2018-01-06 16:00 | 58.18 | 56.24
2018-01-06 16:30 | 59.97 | 58.12
2018-01-06 17:00 | 59.85 | 58.04
2018-01-06 17:30 | 58.67 | 56.85
2018-01-06 18:00 | 59.43 | 57.63
2018-01-06 18:30 | 59.87 | 58.1
2018-01-06 19:00 | 59.45 | 57.67
2018-01-06 19:30 | 60.21 | 58.44
2018-01-06 20:00 | 59.92 | 58.13
2018-01-06 20:30 | 57.97 | 56.13
2018-01-06 21:00 | 56.31 | 54.42
2018-01-06 21:30 | 54.62 | 52.67
2018-01-06 22:00 | 52.32 | 50.55
2018-01-06 22:30 | 49.89 | 48.27
2018-01-06 23:00 | 48.7 | 47.66
2018-01-06 23:30 | 45.34 | 44.69
2018-01-07 | 43.5 | 42.83
2018-01-07 00:30 | 42.06 | 41.38
2018-01-07 01:00 | 40.67 | 39.97
2018-01-07 01:30 | 40 | 39.29
2018-01-07 02:00 | 39.68 | 38.95
2018-01-07 02:30 | 39.1 | 38.37
2018-01-07 03:00 | 38.28 | 37.54
2018-01-07 03:30 | 38.06 | 37.31
2018-01-07 04:00 | 37.97 | 37.22
2018-01-07 04:30 | 38.11 | 37.37
2018-01-07 05:00 | 38.12 | 37.37
2018-01-07 05:30 | 38 | 37.26
2018-01-07 06:00 | 37.61 | 36.87
2018-01-07 06:30 | 38.5 | 37.76
2018-01-07 07:00 | 39.13 | 38.4
2018-01-07 07:30 | 41 | 40.28
2018-01-07 08:00 | 42.44 | 41.72
2018-01-07 08:30 | 43.4 | 42.69
2018-01-07 09:00 | 43.63 | 42.91
2018-01-07 09:30 | 45.24 | 44.46
2018-01-07 10:00 | 47.07 | 45.94
2018-01-07 10:30 | 47.42 | 46.44
2018-01-07 11:00 | 47.92 | 46.98
2018-01-07 11:30 | 48.22 | 47.34
2018-01-07 12:00 | 48.94 | 48.13
2018-01-07 12:30 | 51.03 | 50.17
2018-01-07 13:00 | 49.46 | 48.63
2018-01-07 13:30 | 49.83 | 49.01
2018-01-07 14:00 | 50.56 | 49.77
2018-01-07 14:30 | 50.57 | 49.67
2018-01-07 15:00 | 50.78 | 49.86
2018-01-07 15:30 | 51.03 | 50.03
2018-01-07 16:00 | 51.79 | 50.76
2018-01-07 16:30 | 53.6 | 52.62
2018-01-07 17:00 | 54.21 | 53.19
2018-01-07 17:30 | 55.32 | 54.24
2018-01-07 18:00 | 56.7 | 55.62
2018-01-07 18:30 | 57.28 | 56.19
2018-01-07 19:00 | 57.78 | 56.76
2018-01-07 19:30 | 58.54 | 57.72
2018-01-07 20:00 | 58.38 | 57.56
2018-01-07 20:30 | 56.14 | 55.12
2018-01-07 21:00 | 54.18 | 52.97
2018-01-07 21:30 | 52.12 | 50.68
2018-01-07 22:00 | 50.37 | 48.69
2018-01-07 22:30 | 48.44 | 46.52
2018-01-07 23:00 | 48.17 | 46.06
2018-01-07 23:30 | 45.38 | 42.88
2018-01-08 | 43.97 | 41.17
2018-01-08 00:30 | 43.3 | 40.29
2018-01-08 01:00 | 42.19 | 39.05
2018-01-08 01:30 | 41.71 | 38.46
2018-01-08 02:00 | 39.09 | 37.97
2018-01-08 02:30 | 37.29 | 37.25
2018-01-08 03:00 | 37.08 | 37.04
2018-01-08 03:30 | 37.17 | 37.13
2018-01-08 04:00 | 37.4 | 37.36
2018-01-08 04:30 | 38.35 | 38.29
2018-01-08 05:00 | 39.42 | 39.35
2018-01-08 05:30 | 41.61 | 41.47
2018-01-08 06:00 | 44.26 | 44.03
2018-01-08 06:30 | 50.11 | 49.48
2018-01-08 07:00 | 54.02 | 53.4
2018-01-08 07:30 | 60.21 | 59.29
2018-01-08 08:00 | 63.87 | 62.78
2018-01-08 08:30 | 66.51 | 66.1
2018-01-08 09:00 | 66.92 | 66.6
2018-01-08 09:30 | 68.86 | 68.56
2018-01-08 10:00 | 68.9 | 68.58
2018-01-08 10:30 | 68.46 | 68.13
2018-01-08 11:00 | 69.05 | 68.72
2018-01-08 11:30 | 69.34 | 69
2018-01-08 12:00 | 69.27 | 68.93
2018-01-08 12:30 | 70.38 | 70.05
2018-01-08 13:00 | 69.97 | 69.64
2018-01-08 13:30 | 71.79 | 71.47
2018-01-08 14:00 | 73.15 | 72.82
2018-01-08 14:30 | 72.96 | 72.63
2018-01-08 15:00 | 72.79 | 72.47
2018-01-08 15:30 | 73.53 | 73.21
2018-01-08 16:00 | 73.05 | 72.75
2018-01-08 16:30 | 73.28 | 73
2018-01-08 17:00 | 71.85 | 71.54
2018-01-08 17:30 | 69.99 | 69.51
2018-01-08 18:00 | 67.76 | 66.85
2018-01-08 18:30 | 66.56 | 65.11
2018-01-08 19:00 | 66.88 | 65.45
2018-01-08 19:30 | 67.95 | 66.76
2018-01-08 20:00 | 66.84 | 65.51
2018-01-08 20:30 | 64.06 | 62.38
2018-01-08 21:00 | 61.82 | 59.85
2018-01-08 21:30 | 59.32 | 56.88
2018-01-08 22:00 | 56.7 | 53.84
2018-01-08 22:30 | 54.29 | 50.94
2018-01-08 23:00 | 50.43 | 49.72
2018-01-08 23:30 | 46.82 | 46.31
2018-01-09 | 44.65 | 44.13
2018-01-09 00:30 | 43.25 | 42.72
2018-01-09 01:00 | 41.84 | 41.26
2018-01-09 01:30 | 40.46 | 39.79
2018-01-09 02:00 | 40.16 | 39.41
2018-01-09 02:30 | 38.8 | 38.04
2018-01-09 03:00 | 38.09 | 37.34
2018-01-09 03:30 | 37.83 | 37.07
2018-01-09 04:00 | 37.48 | 36.71
2018-01-09 04:30 | 37.99 | 37.22
2018-01-09 05:00 | 38.72 | 37.95
2018-01-09 05:30 | 40.63 | 39.88
2018-01-09 06:00 | 42.8 | 42.08
2018-01-09 06:30 | 47.4 | 46.69
2018-01-09 07:00 | 52.15 | 51.53
2018-01-09 07:30 | 59.97 | 57.9
2018-01-09 08:00 | 64.13 | 62.36
2018-01-09 08:30 | 70.03 | 68.35
2018-01-09 09:00 | 72.27 | 70.6
2018-01-09 09:30 | 73.49 | 71.86
2018-01-09 10:00 | 73.29 | 71.63
2018-01-09 10:30 | 74.21 | 72.55
2018-01-09 11:00 | 75.06 | 73.4
2018-01-09 11:30 | 75.32 | 73.66
2018-01-09 12:00 | 76.43 | 74.8
2018-01-09 12:30 | 77.42 | 75.83
2018-01-09 13:00 | 76.26 | 74.65
2018-01-09 13:30 | 75.54 | 73.92
2018-01-09 14:00 | 75.32 | 73.69
2018-01-09 14:30 | 77.28 | 75.69
2018-01-09 15:00 | 76.03 | 74.44
2018-01-09 15:30 | 75.55 | 73.97
2018-01-09 16:00 | 75.38 | 73.82
2018-01-09 16:30 | 75.63 | 74.1
2018-01-09 17:00 | 74.29 | 72.79
2018-01-09 17:30 | 71.9 | 70.42
2018-01-09 18:00 | 69.61 | 68.13
2018-01-09 18:30 | 68.08 | 66.45
2018-01-09 19:00 | 67.93 | 66.26
2018-01-09 19:30 | 68.04 | 66.45
2018-01-09 20:00 | 67.45 | 65.82
2018-01-09 20:30 | 65.01 | 63.2
2018-01-09 21:00 | 62.97 | 61.02
2018-01-09 21:30 | 60.69 | 58.62
2018-01-09 22:00 | 58.13 | 55.75
2018-01-09 22:30 | 55.69 | 52.78
2018-01-09 23:00 | 53.04 | 51.38
2018-01-09 23:30 | 47.73 | 47.67
2018-01-10 | 45.57 | 45.47
2018-01-10 00:30 | 44.26 | 44.09
2018-01-10 01:00 | 42.98 | 42.77
2018-01-10 01:30 | 42.37 | 42.14
2018-01-10 02:00 | 41.1 | 41.06
2018-01-10 02:30 | 40.2 | 40.18
2018-01-10 03:00 | 39.44 | 39.37
2018-01-10 03:30 | 39.18 | 39.1
2018-01-10 04:00 | 38.95 | 38.86
2018-01-10 04:30 | 39.55 | 39.42
2018-01-10 05:00 | 40.58 | 40.41
2018-01-10 05:30 | 42.45 | 42.2
2018-01-10 06:00 | 44.59 | 44.27
2018-01-10 06:30 | 51.73 | 49.58
2018-01-10 07:00 | 56.27 | 53.73
2018-01-10 07:30 | 61.79 | 59.49
2018-01-10 08:00 | 66.7 | 65.01
2018-01-10 08:30 | 69.23 | 67.56
2018-01-10 09:00 | 71.57 | 69.92
2018-01-10 09:30 | 72.77 | 71.13
2018-01-10 10:00 | 72.83 | 71.17
2018-01-10 10:30 | 73.7 | 72.04
2018-01-10 11:00 | 74.31 | 72.65
2018-01-10 11:30 | 75.12 | 73.47
2018-01-10 12:00 | 75.71 | 74.07
2018-01-10 12:30 | 76.97 | 75.38
2018-01-10 13:00 | 75.5 | 73.89
2018-01-10 13:30 | 76.05 | 74.45
2018-01-10 14:00 | 76.75 | 75.15
2018-01-10 14:30 | 76.98 | 75.38
2018-01-10 15:00 | 77.24 | 75.67
2018-01-10 15:30 | 76.89 | 75.33
2018-01-10 16:00 | 76.46 | 74.91
2018-01-10 16:30 | 76.25 | 74.74
2018-01-10 17:00 | 74.91 | 73.42
2018-01-10 17:30 | 72.67 | 71.2
2018-01-10 18:00 | 70.69 | 69.23
2018-01-10 18:30 | 69.15 | 67.62
2018-01-10 19:00 | 68.9 | 67.34
2018-01-10 19:30 | 69.62 | 68.15
2018-01-10 20:00 | 68.72 | 67.18
2018-01-10 20:30 | 66 | 64.28
2018-01-10 21:00 | 63.37 | 61.45
2018-01-10 21:30 | 60.76 | 58.61
2018-01-10 22:00 | 58.02 | 55.57
2018-01-10 22:30 | 55.77 | 52.97
2018-01-10 23:00 | 54.88 | 51.86
2018-01-10 23:30 | 52.02 | 48.45
2018-01-11 | 46.58 | 45.93
2018-01-11 00:30 | 45.27 | 44.67
2018-01-11 01:00 | 43.68 | 43.05
2018-01-11 01:30 | 43.07 | 42.44
2018-01-11 02:00 | 42.55 | 41.92
2018-01-11 02:30 | 41.74 | 41.1
2018-01-11 03:00 | 41.16 | 40.52
2018-01-11 03:30 | 40.95 | 40.3
2018-01-11 04:00 | 40.51 | 39.85
2018-01-11 04:30 | 40.88 | 40.23
2018-01-11 05:00 | 41.5 | 40.85
2018-01-11 05:30 | 43.14 | 42.49
2018-01-11 06:00 | 44.77 | 44.15
2018-01-11 06:30 | 49.74 | 49.15
2018-01-11 07:00 | 54.11 | 53.59
2018-01-11 07:30 | 59.54 | 58.97
2018-01-11 08:00 | 65.31 | 64.72
2018-01-11 08:30 | 68.21 | 67.9
2018-01-11 09:00 | 67.53 | 67.21
2018-01-11 09:30 | 67.9 | 67.57
2018-01-11 10:00 | 67.56 | 67.22
2018-01-11 10:30 | 68.54 | 68.19
2018-01-11 11:00 | 68.98 | 68.63
2018-01-11 11:30 | 69.2 | 68.84
2018-01-11 12:00 | 70.27 | 69.96
2018-01-11 12:30 | 72.99 | 72.66
2018-01-11 13:00 | 71.94 | 71.6
2018-01-11 13:30 | 72.85 | 72.51
2018-01-11 14:00 | 73.66 | 73.32
2018-01-11 14:30 | 73.84 | 73.51
2018-01-11 15:00 | 73.66 | 73.34
2018-01-11 15:30 | 73.3 | 72.98
2018-01-11 16:00 | 73.16 | 72.85
2018-01-11 16:30 | 73.97 | 73.69
2018-01-11 17:00 | 72.74 | 72.47
2018-01-11 17:30 | 70.85 | 70.45
2018-01-11 18:00 | 70.63 | 70.09
2018-01-11 18:30 | 70.21 | 69.44
2018-01-11 19:00 | 70.31 | 69.48
2018-01-11 19:30 | 70.88 | 70.18
2018-01-11 20:00 | 70.53 | 69.83
2018-01-11 20:30 | 67.27 | 66.22
2018-01-11 21:00 | 65.38 | 64.17
2018-01-11 21:30 | 62.35 | 60.74
2018-01-11 22:00 | 59.07 | 56.99
2018-01-11 22:30 | 57.2 | 54.8
2018-01-11 23:00 | 55.42 | 53.43
2018-01-11 23:30 | 50.16 | 49.67
2018-01-12 | 47.92 | 47.41
2018-01-12 00:30 | 46.61 | 46.22
2018-01-12 01:00 | 44.25 | 44.13
2018-01-12 01:30 | 43.66 | 43.53
2018-01-12 02:00 | 43 | 42.83
2018-01-12 02:30 | 42.37 | 42.15
2018-01-12 03:00 | 42.24 | 41.99
2018-01-12 03:30 | 41.2 | 41.12
2018-01-12 04:00 | 40.89 | 40.86
2018-01-12 04:30 | 41.85 | 41.82
2018-01-12 05:00 | 43.34 | 43.29
2018-01-12 05:30 | 45.06 | 45
2018-01-12 06:00 | 47.16 | 47.08
2018-01-12 06:30 | 52.32 | 52.15
2018-01-12 07:00 | 57.36 | 57.15
2018-01-12 07:30 | 63.79 | 63.12
2018-01-12 08:00 | 69.18 | 67.31
2018-01-12 08:30 | 71.14 | 69.16
2018-01-12 09:00 | 72.49 | 70.75
2018-01-12 09:30 | 72.92 | 71.18
2018-01-12 10:00 | 72.82 | 71.07
2018-01-12 10:30 | 73.51 | 71.77
2018-01-12 11:00 | 74.13 | 72.38
2018-01-12 11:30 | 74.39 | 72.63
2018-01-12 12:00 | 74.67 | 72.91
2018-01-12 12:30 | 76.28 | 74.56
2018-01-12 13:00 | 75.15 | 73.42
2018-01-12 13:30 | 76.21 | 74.5
2018-01-12 14:00 | 76.82 | 75.12
2018-01-12 14:30 | 76.19 | 74.52
2018-01-12 15:00 | 75.52 | 73.85
2018-01-12 15:30 | 75.67 | 74.03
2018-01-12 16:00 | 75.32 | 73.7
2018-01-12 16:30 | 63.09 | 62.08
2018-01-12 17:00 | 74.07 | 72.49
2018-01-12 17:30 | 70.56 | 69.97
2018-01-12 18:00 | 68.85 | 68.03
2018-01-12 18:30 | 67.52 | 66.37
2018-01-12 19:00 | 67.26 | 66.06
2018-01-12 19:30 | 66.43 | 65.26
2018-01-12 20:00 | 65.71 | 64.46
2018-01-12 20:30 | 63.74 | 62.24
2018-01-12 21:00 | 61.57 | 59.84
2018-01-12 21:30 | 57.74 | 57.63
2018-01-12 22:00 | 55.02 | 54.99
2018-01-12 22:30 | 52.13 | 52.11
2018-01-12 23:00 | 50.91 | 50.89
2018-01-12 23:30 | 47.19 | 47.11
2018-01-13 | 44.08 | 43.96
2018-01-13 00:30 | 42.29 | 42.16
2018-01-13 01:00 | 40.34 | 40.24
2018-01-13 01:30 | 39.65 | 39.55
2018-01-13 02:00 | 38.94 | 38.85
2018-01-13 02:30 | 38.33 | 38.24
2018-01-13 03:00 | 37.46 | 37.39
2018-01-13 03:30 | 36.88 | 36.82
2018-01-13 04:00 | 36.52 | 36.46
2018-01-13 04:30 | 36.37 | 36.31
2018-01-13 05:00 | 36.56 | 36.5
2018-01-13 05:30 | 37.08 | 37.01
2018-01-13 06:00 | 37.32 | 37.26
2018-01-13 06:30 | 39.4 | 39.29
2018-01-13 07:00 | 41.37 | 41.15
2018-01-13 07:30 | 44.21 | 43.81
2018-01-13 08:00 | 46.19 | 45.59
2018-01-13 08:30 | 49.25 | 48.28
2018-01-13 09:00 | 54.72 | 51.86
2018-01-13 09:30 | 55.57 | 52.73
2018-01-13 10:00 | 55.8 | 53.02
2018-01-13 10:30 | 56.02 | 53.79
2018-01-13 11:00 | 56.38 | 54.15
2018-01-13 11:30 | 56.77 | 54.55
2018-01-13 12:00 | 57.39 | 55.2
2018-01-13 12:30 | 58.1 | 55.97
2018-01-13 13:00 | 57.12 | 54.96
2018-01-13 13:30 | 56.84 | 54.68
2018-01-13 14:00 | 57.23 | 55.1
2018-01-13 14:30 | 58.1 | 56.02
2018-01-13 15:00 | 58.29 | 56.21
2018-01-13 15:30 | 58.77 | 56.75
2018-01-13 16:00 | 59.94 | 57.97
2018-01-13 16:30 | 61.06 | 59.13
2018-01-13 17:00 | 60.81 | 58.9
2018-01-13 17:30 | 61.2 | 59.33
2018-01-13 18:00 | 62.12 | 60.3
2018-01-13 18:30 | 62.11 | 60.3
2018-01-13 19:00 | 61.63 | 59.8
2018-01-13 19:30 | 61.84 | 59.98
2018-01-13 20:00 | 61.13 | 59.28
2018-01-13 20:30 | 59.34 | 57.44
2018-01-13 21:00 | 57.48 | 55.51
2018-01-13 21:30 | 56.12 | 54.11
2018-01-13 22:00 | 53.79 | 51.72
2018-01-13 22:30 | 51.2 | 49.5
2018-01-13 23:00 | 50.09 | 48.59
2018-01-13 23:30 | 47.41 | 45.6
2018-01-14 | 45.85 | 43.81
2018-01-14 00:30 | 44.9 | 42.56
2018-01-14 01:00 | 43.51 | 40.95
2018-01-14 01:30 | 42.89 | 40.15
2018-01-14 02:00 | 42.25 | 39.37
2018-01-14 02:30 | 41.89 | 38.89
2018-01-14 03:00 | 41.51 | 38.42
2018-01-14 03:30 | 41.37 | 38.31
2018-01-14 04:00 | 41.21 | 38.03
2018-01-14 04:30 | 41.05 | 38
2018-01-14 05:00 | 40.89 | 37.79
2018-01-14 05:30 | 41.17 | 38.17
2018-01-14 06:00 | 40.72 | 37.39
2018-01-14 06:30 | 41.44 | 38.27
2018-01-14 07:00 | 42.45 | 39.68
2018-01-14 07:30 | 44.2 | 41.96
2018-01-14 08:00 | 45.46 | 43.61
2018-01-14 08:30 | 46.79 | 45.22
2018-01-14 09:00 | 47.78 | 46.47
2018-01-14 09:30 | 48.97 | 47.93
2018-01-14 10:00 | 49.2 | 48.31
2018-01-14 10:30 | 49.57 | 48.83
2018-01-14 11:00 | 49.83 | 49.17
2018-01-14 11:30 | 51.67 | 51.15
2018-01-14 12:00 | 53.2 | 52.74
2018-01-14 12:30 | 56.63 | 56.26
2018-01-14 13:00 | 58.12 | 57.78
2018-01-14 13:30 | 59.69 | 59.37
2018-01-14 14:00 | 61.76 | 61.5
2018-01-14 14:30 | 61.47 | 61.15
2018-01-14 15:00 | 59.6 | 59.27
2018-01-14 15:30 | 60.68 | 60.35
2018-01-14 16:00 | 61.83 | 61.52
2018-01-14 16:30 | 63.9 | 63.62
2018-01-14 17:00 | 65.01 | 64.73
2018-01-14 17:30 | 65.21 | 64.89
2018-01-14 18:00 | 66.77 | 66.41
2018-01-14 18:30 | 65.96 | 65.53
2018-01-14 19:00 | 65.51 | 65.1
2018-01-14 19:30 | 66.13 | 65.81
2018-01-14 20:00 | 65.77 | 65.45
2018-01-14 20:30 | 63.58 | 63.16
2018-01-14 21:00 | 61.13 | 60.61
2018-01-14 21:30 | 58.69 | 57.99
2018-01-14 22:00 | 56.01 | 55.07
2018-01-14 22:30 | 52.96 | 51.75
2018-01-14 23:00 | 52.36 | 51.03
2018-01-14 23:30 | 49.3 | 47.61
2018-01-15 | 46.91 | 44.96
2018-01-15 00:30 | 45.64 | 43.34
2018-01-15 01:00 | 44.51 | 42.11
2018-01-15 01:30 | 44.56 | 42.12
2018-01-15 02:00 | 44.33 | 41.87
2018-01-15 02:30 | 44.11 | 41.55
2018-01-15 03:00 | 43.68 | 41.02
2018-01-15 03:30 | 43.52 | 40.88
2018-01-15 04:00 | 43.64 | 41.11
2018-01-15 04:30 | 43.82 | 41.4
2018-01-15 05:00 | 44.4 | 42.23
2018-01-15 05:30 | 46.32 | 44.68
2018-01-15 06:00 | 48.56 | 47.32
2018-01-15 06:30 | 53.4 | 52.82
2018-01-15 07:00 | 59.09 | 58.57
2018-01-15 07:30 | 65.32 | 65.22
2018-01-15 08:00 | 70.01 | 69.93
2018-01-15 08:30 | 73.18 | 73.16
2018-01-15 09:00 | 75.81 | 75.27
2018-01-15 09:30 | 78.19 | 76.57
2018-01-15 10:00 | 78.49 | 76.87
2018-01-15 10:30 | 78.67 | 77.04
2018-01-15 11:00 | 81.06 | 79.47
2018-01-15 11:30 | 82.85 | 81.29
2018-01-15 12:00 | 83.47 | 81.93
2018-01-15 12:30 | 86.31 | 84.82
2018-01-15 13:00 | 84.7 | 83.17
2018-01-15 13:30 | 81.64 | 80.08
2018-01-15 14:00 | 80.83 | 79.26
2018-01-15 14:30 | 80.82 | 79.25
2018-01-15 15:00 | 79.69 | 78.11
2018-01-15 15:30 | 77.05 | 75.39
2018-01-15 16:00 | 75.11 | 73.39
2018-01-15 16:30 | 73.93 | 72.22
2018-01-15 17:00 | 71.88 | 70.15
2018-01-15 17:30 | 69.33 | 67.61
2018-01-15 18:00 | 67.03 | 65.37
2018-01-15 18:30 | 64.2 | 63.33
2018-01-15 19:00 | 64.26 | 63.38
2018-01-15 19:30 | 64.23 | 63.49
2018-01-15 20:00 | 63.71 | 62.93
2018-01-15 20:30 | 61.46 | 60.45
2018-01-15 21:00 | 59.35 | 58.14
2018-01-15 21:30 | 57.3 | 55.8
2018-01-15 22:00 | 54.81 | 52.93
2018-01-15 22:30 | 52.78 | 50.59
2018-01-15 23:00 | 49.47 | 49.31
2018-01-15 23:30 | 46.27 | 46.22
2018-01-16 | 44.33 | 44.29
2018-01-16 00:30 | 43.45 | 43.42
2018-01-16 01:00 | 41.99 | 41.97
2018-01-16 01:30 | 41.19 | 41.17
2018-01-16 02:00 | 40.49 | 40.47
2018-01-16 02:30 | 39.96 | 39.92
2018-01-16 03:00 | 39.61 | 39.57
2018-01-16 03:30 | 39.18 | 39.13
2018-01-16 04:00 | 39.39 | 39.32
2018-01-16 04:30 | 40.7 | 40.6
2018-01-16 05:00 | 41.7 | 41.56
2018-01-16 05:30 | 44.21 | 43.93
2018-01-16 06:00 | 46.07 | 45.73
2018-01-16 06:30 | 51.54 | 50.95
2018-01-16 07:00 | 55.56 | 55
2018-01-16 07:30 | 63.89 | 60.73
2018-01-16 08:00 | 65.04 | 64.16
2018-01-16 08:30 | 68.11 | 67.6
2018-01-16 09:00 | 69.62 | 69.28
2018-01-16 09:30 | 69.7 | 69.37
2018-01-16 10:00 | 69.04 | 68.7
2018-01-16 10:30 | 69.56 | 69.22
2018-01-16 11:00 | 69.84 | 69.49
2018-01-16 11:30 | 69.5 | 69.14
2018-01-16 12:00 | 70.22 | 69.87
2018-01-16 12:30 | 73.49 | 73.16
2018-01-16 13:00 | 71.47 | 71.13
2018-01-16 13:30 | 71.09 | 70.74
2018-01-16 14:00 | 70.96 | 70.6
2018-01-16 14:30 | 70.26 | 69.91
2018-01-16 15:00 | 70.5 | 70.16
2018-01-16 15:30 | 71.38 | 71.06
2018-01-16 16:00 | 70.05 | 69.73
2018-01-16 16:30 | 69.49 | 69.12
2018-01-16 17:00 | 67.03 | 66.53
2018-01-16 17:30 | 64.66 | 63.73
2018-01-16 18:00 | 64.28 | 62.93
2018-01-16 18:30 | 63.64 | 62.01
2018-01-16 19:00 | 64.08 | 62.42
2018-01-16 19:30 | 64.76 | 63.3
2018-01-16 20:00 | 64.02 | 62.47
2018-01-16 20:30 | 61.85 | 60.08
2018-01-16 21:00 | 59.63 | 57.56
2018-01-16 21:30 | 57.35 | 54.98
2018-01-16 22:00 | 55.55 | 52.77
2018-01-16 22:30 | 53.64 | 50.43
2018-01-16 23:00 | 50.97 | 49.1
2018-01-16 23:30 | 47.17 | 46.1
2018-01-17 | 45.31 | 44.17
2018-01-17 00:30 | 44.21 | 43.02
2018-01-17 01:00 | 43.06 | 41.83
2018-01-17 01:30 | 42.47 | 41.22
2018-01-17 02:00 | 41.59 | 40.29
2018-01-17 02:30 | 41.07 | 39.73
2018-01-17 03:00 | 40.92 | 39.56
2018-01-17 03:30 | 40.4 | 39.02
2018-01-17 04:00 | 40.31 | 38.99
2018-01-17 04:30 | 40.61 | 39.42
2018-01-17 05:00 | 41.63 | 40.49
2018-01-17 05:30 | 44.23 | 43.22
2018-01-17 06:00 | 46.93 | 46.01
2018-01-17 06:30 | 51.96 | 51.2
2018-01-17 07:00 | 56.51 | 55.81
2018-01-17 07:30 | 62.08 | 61.45
2018-01-17 08:00 | 65.61 | 65.11
2018-01-17 08:30 | 67.37 | 66.99
2018-01-17 09:00 | 67.81 | 67.47
2018-01-17 09:30 | 67.73 | 67.39
2018-01-17 10:00 | 67.23 | 66.88
2018-01-17 10:30 | 67.24 | 66.88
2018-01-17 11:00 | 68.46 | 68.09
2018-01-17 11:30 | 70.5 | 70.15
2018-01-17 12:00 | 67.61 | 67.24
2018-01-17 12:30 | 67.16 | 66.79
2018-01-17 13:00 | 66.72 | 66.35
2018-01-17 13:30 | 67.43 | 67.05
2018-01-17 14:00 | 68.89 | 68.52
2018-01-17 14:30 | 68.74 | 68.38
2018-01-17 15:00 | 69.9 | 69.55
2018-01-17 15:30 | 70.36 | 70.01
2018-01-17 16:00 | 68.72 | 68.39
2018-01-17 16:30 | 68.89 | 68.56
2018-01-17 17:00 | 68.55 | 68.14
2018-01-17 17:30 | 65.55 | 64.81
2018-01-17 18:00 | 64.03 | 62.81
2018-01-17 18:30 | 63.28 | 61.67
2018-01-17 19:00 | 63.55 | 61.88
2018-01-17 19:30 | 63.96 | 62.46
2018-01-17 20:00 | 63.35 | 61.76
2018-01-17 20:30 | 63.94 | 61.87
2018-01-17 21:00 | 59.63 | 58.38
2018-01-17 21:30 | 56.37 | 55.35
2018-01-17 22:00 | 54.15 | 53.05
2018-01-17 22:30 | 52.62 | 51.46
2018-01-17 23:00 | 51.66 | 50.45
2018-01-17 23:30 | 48.39 | 47.06
2018-01-18 | 46.43 | 44.96
2018-01-18 00:30 | 44.48 | 43.42
2018-01-18 01:00 | 43.19 | 42.25
2018-01-18 01:30 | 42.56 | 41.61
2018-01-18 02:00 | 42.1 | 41.13
2018-01-18 02:30 | 41.45 | 40.44
2018-01-18 03:00 | 40.68 | 39.64
2018-01-18 03:30 | 40.53 | 39.49
2018-01-18 04:00 | 40.18 | 39.13
2018-01-18 04:30 | 40.77 | 39.74
2018-01-18 05:00 | 41.98 | 41.01
2018-01-18 05:30 | 44.17 | 43.29
2018-01-18 06:00 | 45.74 | 44.9
2018-01-18 06:30 | 51.37 | 50.49
2018-01-18 07:00 | 55.49 | 54.79
2018-01-18 07:30 | 61.16 | 60.07
2018-01-18 08:00 | 63.67 | 62.83
2018-01-18 08:30 | 65.91 | 65.5
2018-01-18 09:00 | 66.47 | 66.12
2018-01-18 09:30 | 66.25 | 65.89
2018-01-18 10:00 | 66.05 | 65.7
2018-01-18 10:30 | 66.52 | 66.16
2018-01-18 11:00 | 67.41 | 67.05
2018-01-18 11:30 | 68.06 | 67.69
2018-01-18 12:00 | 69.11 | 68.74
2018-01-18 12:30 | 70.81 | 70.45
2018-01-18 13:00 | 70.17 | 69.81
2018-01-18 13:30 | 69.58 | 69.22
2018-01-18 14:00 | 70.92 | 70.56
2018-01-18 14:30 | 70.97 | 70.61
2018-01-18 15:00 | 70.96 | 70.6
2018-01-18 15:30 | 70.48 | 70.13
2018-01-18 16:00 | 60.95 | 60.76
2018-01-18 16:30 | 69.62 | 69.28
2018-01-18 17:00 | 68.7 | 68.29
2018-01-18 17:30 | 66.74 | 66.07
2018-01-18 18:00 | 66.21 | 65.13
2018-01-18 18:30 | 66.51 | 65.17
2018-01-18 19:00 | 66.48 | 65.46
2018-01-18 19:30 | 66.27 | 65.93
2018-01-18 20:00 | 65.83 | 65.49
2018-01-18 20:30 | 64.01 | 63.64
2018-01-18 21:00 | 61.79 | 61.37
2018-01-18 21:30 | 57.89 | 57.33
2018-01-18 22:00 | 54.52 | 53.85
2018-01-18 22:30 | 51.78 | 51.1
2018-01-18 23:00 | 50.71 | 50.03
2018-01-18 23:30 | 47.23 | 46.5
2018-01-19 | 45.29 | 44.55
2018-01-19 00:30 | 43.82 | 43.07
2018-01-19 01:00 | 42.19 | 41.41
2018-01-19 01:30 | 42.03 | 41.24
2018-01-19 02:00 | 41.55 | 40.76
2018-01-19 02:30 | 40.66 | 39.86
2018-01-19 03:00 | 40.19 | 39.38
2018-01-19 03:30 | 39.5 | 38.68
2018-01-19 04:00 | 39.02 | 38.21
2018-01-19 04:30 | 39.86 | 39.05
2018-01-19 05:00 | 40.91 | 40.11
2018-01-19 05:30 | 43.05 | 42.27
2018-01-19 06:00 | 44.91 | 44.15
2018-01-19 06:30 | 49.44 | 48.63
2018-01-19 07:00 | 54.04 | 53.34
2018-01-19 07:30 | 59.63 | 58.76
2018-01-19 08:00 | 63.07 | 62.59
2018-01-19 08:30 | 64.79 | 64.41
2018-01-19 09:00 | 64.56 | 64.2
2018-01-19 09:30 | 65.5 | 65.14
2018-01-19 10:00 | 64.83 | 64.46
2018-01-19 10:30 | 65.04 | 64.67
2018-01-19 11:00 | 65.99 | 65.61
2018-01-19 11:30 | 66.71 | 66.32
2018-01-19 12:00 | 66.84 | 66.46
2018-01-19 12:30 | 68.1 | 67.72
2018-01-19 13:00 | 67.14 | 66.77
2018-01-19 13:30 | 66.99 | 66.62
2018-01-19 14:00 | 67.35 | 66.99
2018-01-19 14:30 | 67.65 | 67.3
2018-01-19 15:00 | 67.7 | 67.35
2018-01-19 15:30 | 66.75 | 66.4
2018-01-19 16:00 | 66.05 | 65.65
2018-01-19 16:30 | 66.31 | 65.84
2018-01-19 17:00 | 65.62 | 64.82
2018-01-19 17:30 | 64.61 | 63.57
2018-01-19 18:00 | 63.06 | 61.52
2018-01-19 18:30 | 62.68 | 60.84
2018-01-19 19:00 | 63.1 | 61.33
2018-01-19 19:30 | 63.73 | 62.18
2018-01-19 20:00 | 62.61 | 60.93
2018-01-19 20:30 | 60.53 | 58.55
2018-01-19 21:00 | 58.56 | 56.35
2018-01-19 21:30 | 57.25 | 54.71
2018-01-19 22:00 | 54.46 | 52.17
2018-01-19 22:30 | 50.27 | 49.29
2018-01-19 23:00 | 49.31 | 48.3
2018-01-19 23:30 | 45.92 | 44.81
2018-01-20 | 43.39 | 42.18
2018-01-20 00:30 | 41.95 | 40.77
2018-01-20 01:00 | 40.35 | 39.16
2018-01-20 01:30 | 39.51 | 38.27
2018-01-20 02:00 | 38.64 | 37.41
2018-01-20 02:30 | 37.59 | 36.53
2018-01-20 03:00 | 37.26 | 36.25
2018-01-20 03:30 | 37.04 | 36.02
2018-01-20 04:00 | 36.46 | 35.4
2018-01-20 04:30 | 36.25 | 35.18
2018-01-20 05:00 | 36.45 | 35.39
2018-01-20 05:30 | 36.61 | 36.16
2018-01-20 06:00 | 36.37 | 35.98
2018-01-20 06:30 | 38.45 | 37.87
2018-01-20 07:00 | 39.81 | 39.07
2018-01-20 07:30 | 41.7 | 40.7
2018-01-20 08:00 | 44.71 | 43.32
2018-01-20 08:30 | 47.2 | 46.08
2018-01-20 09:00 | 49.06 | 48.23
2018-01-20 09:30 | 50.59 | 49.99
2018-01-20 10:00 | 50.65 | 50.1
2018-01-20 10:30 | 51.17 | 50.66
2018-01-20 11:00 | 51.19 | 50.69
2018-01-20 11:30 | 50.59 | 50.1
2018-01-20 12:00 | 51.78 | 51.29
2018-01-20 12:30 | 51.83 | 51.3
2018-01-20 13:00 | 50.67 | 50.11
2018-01-20 13:30 | 50.65 | 50.06
2018-01-20 14:00 | 51.09 | 50.51
2018-01-20 14:30 | 52.95 | 52.37
2018-01-20 15:00 | 53.3 | 52.7
2018-01-20 15:30 | 53.64 | 53
2018-01-20 16:00 | 52.88 | 52.21
2018-01-20 16:30 | 54.07 | 53.4
2018-01-20 17:00 | 55.61 | 54.9
2018-01-20 17:30 | 55.33 | 54.45
2018-01-20 18:00 | 55.72 | 54.76
2018-01-20 18:30 | 56.21 | 55.23
2018-01-20 19:00 | 56.43 | 55.51
2018-01-20 19:30 | 57.36 | 56.62
2018-01-20 20:00 | 56.76 | 55.97
2018-01-20 20:30 | 55.03 | 54.06
2018-01-20 21:00 | 53.62 | 52.55
2018-01-20 21:30 | 52.39 | 51.19
2018-01-20 22:00 | 50.85 | 49.43
2018-01-20 22:30 | 49.15 | 47.51
2018-01-20 23:00 | 48.69 | 46.88
2018-01-20 23:30 | 45.92 | 43.77
2018-01-21 | 44.28 | 41.83
2018-01-21 00:30 | 43.72 | 41.03
2018-01-21 01:00 | 39.88 | 39.77
2018-01-21 01:30 | 39.09 | 39.01
2018-01-21 02:00 | 38.45 | 38.37
2018-01-21 02:30 | 38.08 | 38
2018-01-21 03:00 | 37.42 | 37.36
2018-01-21 03:30 | 37.06 | 37
2018-01-21 04:00 | 36.83 | 36.77
2018-01-21 04:30 | 36.89 | 36.83
2018-01-21 05:00 | 37.03 | 36.96
2018-01-21 05:30 | 37.18 | 37.12
2018-01-21 06:00 | 36.74 | 36.68
2018-01-21 06:30 | 37.65 | 37.59
2018-01-21 07:00 | 37.85 | 37.79
2018-01-21 07:30 | 39.46 | 39.37
2018-01-21 08:00 | 40.53 | 40.42
2018-01-21 08:30 | 41.78 | 41.61
2018-01-21 09:00 | 43.25 | 43
2018-01-21 09:30 | 45.21 | 44.87
2018-01-21 10:00 | 45.11 | 44.69
2018-01-21 10:30 | 45.47 | 44.98
2018-01-21 11:00 | 49.1 | 48.54
2018-01-21 11:30 | 48.6 | 48
2018-01-21 12:00 | 48.21 | 47.59
2018-01-21 12:30 | 51.93 | 51.38
2018-01-21 13:00 | 49.86 | 49.29
2018-01-21 13:30 | 49.68 | 49.15
2018-01-21 14:00 | 49.21 | 48.7
2018-01-21 14:30 | 49.53 | 49.07
2018-01-21 15:00 | 49.77 | 49.32
2018-01-21 15:30 | 50.24 | 49.87
2018-01-21 16:00 | 50.04 | 49.69
2018-01-21 16:30 | 50.86 | 50.51
2018-01-21 17:00 | 51.05 | 50.73
2018-01-21 17:30 | 51.48 | 51.19
2018-01-21 18:00 | 52.78 | 52.52
2018-01-21 18:30 | 54.74 | 54.46
2018-01-21 19:00 | 55.98 | 55.63
2018-01-21 19:30 | 59.42 | 56.98
2018-01-21 20:00 | 58.91 | 56.44
2018-01-21 20:30 | 57.24 | 54.71
2018-01-21 21:00 | 55.12 | 52.5
2018-01-21 21:30 | 53.15 | 50.42
2018-01-21 22:00 | 51.45 | 48.63
2018-01-21 22:30 | 49.16 | 46.21
2018-01-21 23:00 | 48.24 | 45.24
2018-01-21 23:30 | 45.59 | 42.39
2018-01-22 | 44.06 | 40.74
2018-01-22 00:30 | 43.58 | 40.22
2018-01-22 01:00 | 42.51 | 39.08
2018-01-22 01:30 | 42.11 | 38.64
2018-01-22 02:00 | 41.96 | 38.47
2018-01-22 02:30 | 41.72 | 38.21
2018-01-22 03:00 | 41.67 | 38.16
2018-01-22 03:30 | 41.73 | 38.22
2018-01-22 04:00 | 41.72 | 38.19
2018-01-22 04:30 | 42.56 | 39.11
2018-01-22 05:00 | 43.94 | 40.56
2018-01-22 05:30 | 46.46 | 43.25
2018-01-22 06:00 | 48.83 | 45.76
2018-01-22 06:30 | 54.59 | 51.8
2018-01-22 07:00 | 59.67 | 57.18
2018-01-22 07:30 | 66.15 | 64.09
2018-01-22 08:00 | 69.43 | 67.74
2018-01-22 08:30 | 70.15 | 68.43
2018-01-22 09:00 | 70.6 | 68.86
2018-01-22 09:30 | 71.92 | 70.2
2018-01-22 10:00 | 72.22 | 70.49
2018-01-22 10:30 | 72.22 | 70.49
2018-01-22 11:00 | 71.96 | 70.2
2018-01-22 11:30 | 73.62 | 71.9
2018-01-22 12:00 | 74.22 | 72.52
2018-01-22 12:30 | 74.05 | 72.33
2018-01-22 13:00 | 72.73 | 70.98
2018-01-22 13:30 | 74.62 | 72.91
2018-01-22 14:00 | 74.34 | 72.63
2018-01-22 14:30 | 72.04 | 70.28
2018-01-22 15:00 | 71.39 | 69.61
2018-01-22 15:30 | 72.33 | 70.59
2018-01-22 16:00 | 73.66 | 71.98
2018-01-22 16:30 | 73.61 | 71.99
2018-01-22 17:00 | 71.41 | 69.78
2018-01-22 17:30 | 66.92 | 66.02
2018-01-22 18:00 | 66.09 | 64.91
2018-01-22 18:30 | 66.29 | 64.86
2018-01-22 19:00 | 66.4 | 64.95
2018-01-22 19:30 | 66.89 | 65.64
2018-01-22 20:00 | 66.07 | 64.69
2018-01-22 20:30 | 63.83 | 62.14
2018-01-22 21:00 | 61.62 | 59.69
2018-01-22 21:30 | 59.16 | 56.9
2018-01-22 22:00 | 53.86 | 53.71
2018-01-22 22:30 | 51.31 | 51.29
2018-01-22 23:00 | 49.82 | 49.79
2018-01-22 23:30 | 46.65 | 46.59
2018-01-23 | 44.83 | 44.72
2018-01-23 00:30 | 44.04 | 43.88
2018-01-23 01:00 | 42.8 | 42.61
2018-01-23 01:30 | 42.09 | 41.88
2018-01-23 02:00 | 41.52 | 41.28
2018-01-23 02:30 | 41.03 | 40.72
2018-01-23 03:00 | 40.85 | 40.52
2018-01-23 03:30 | 40.7 | 40.34
2018-01-23 04:00 | 40.89 | 40.56
2018-01-23 04:30 | 41.4 | 41.12
2018-01-23 05:00 | 42.34 | 42.12
2018-01-23 05:30 | 45.01 | 44.92
2018-01-23 06:00 | 47.28 | 47.24
2018-01-23 06:30 | 52.73 | 52.69
2018-01-23 07:00 | 58.67 | 58.46
2018-01-23 07:30 | 66.36 | 65.4
2018-01-23 08:00 | 70.44 | 68.57
2018-01-23 08:30 | 71.72 | 70
2018-01-23 09:00 | 72.67 | 70.94
2018-01-23 09:30 | 72.43 | 70.7
2018-01-23 10:00 | 72.42 | 70.65
2018-01-23 10:30 | 72.94 | 71.17
2018-01-23 11:00 | 73.8 | 72.06
2018-01-23 11:30 | 73.73 | 71.98
2018-01-23 12:00 | 73.27 | 71.49
2018-01-23 12:30 | 75.2 | 73.49
2018-01-23 13:00 | 74.34 | 72.61
2018-01-23 13:30 | 74.09 | 72.35
2018-01-23 14:00 | 74.85 | 73.11
2018-01-23 14:30 | 75.61 | 73.9
2018-01-23 15:00 | 75.22 | 73.5
2018-01-23 15:30 | 75.35 | 73.67
2018-01-23 16:00 | 77.05 | 75.42
2018-01-23 16:30 | 75.55 | 73.96
2018-01-23 17:00 | 73.76 | 72.17
2018-01-23 17:30 | 70.63 | 69.28
2018-01-23 18:00 | 67.5 | 66.46
2018-01-23 18:30 | 67.01 | 65.68
2018-01-23 19:00 | 68.35 | 67.14
2018-01-23 19:30 | 69.17 | 68.07
2018-01-23 20:00 | 68.15 | 66.95
2018-01-23 20:30 | 65.97 | 64.48
2018-01-23 21:00 | 63.89 | 62.19
2018-01-23 21:30 | 61.61 | 59.63
2018-01-23 22:00 | 57.53 | 56.16
2018-01-23 22:30 | 53.09 | 53.07
2018-01-23 23:00 | 51.71 | 51.69
2018-01-23 23:30 | 48.46 | 48.41
2018-01-24 | 46.26 | 46.17
2018-01-24 00:30 | 45.17 | 45.04
2018-01-24 01:00 | 43.93 | 43.76
2018-01-24 01:30 | 43.35 | 43.16
2018-01-24 02:00 | 42.57 | 42.34
2018-01-24 02:30 | 42.27 | 41.99
2018-01-24 03:00 | 41.88 | 41.58
2018-01-24 03:30 | 41.58 | 41.27
2018-01-24 04:00 | 41.66 | 41.35
2018-01-24 04:30 | 42.13 | 41.84
2018-01-24 05:00 | 43.22 | 43.03
2018-01-24 05:30 | 45.49 | 45.4
2018-01-24 06:00 | 47.89 | 47.86
2018-01-24 06:30 | 53.26 | 53.21
2018-01-24 07:00 | 58.34 | 58.11
2018-01-24 07:30 | 65.63 | 64.62
2018-01-24 08:00 | 69.58 | 67.63
2018-01-24 08:30 | 69.73 | 69.44
2018-01-24 09:00 | 70.12 | 70.11
2018-01-24 09:30 | 71.43 | 71.42
2018-01-24 10:00 | 71.83 | 71.82
2018-01-24 10:30 | 72.54 | 72.52
2018-01-24 11:00 | 73.38 | 73.37
2018-01-24 11:30 | 72.53 | 72.51
2018-01-24 12:00 | 73.43 | 73.37
2018-01-24 12:30 | 76 | 75.95
2018-01-24 13:00 | 74.53 | 74.5
2018-01-24 13:30 | 74.53 | 74.5
2018-01-24 14:00 | 78.11 | 78.06
2018-01-24 14:30 | 78.5 | 78.47
2018-01-24 15:00 | 75.3 | 74.69
2018-01-24 15:30 | 76.28 | 74.62
2018-01-24 16:00 | 75.11 | 73.46
2018-01-24 16:30 | 74.23 | 72.61
2018-01-24 17:00 | 71.98 | 70.34
2018-01-24 17:30 | 68.51 | 67.8
2018-01-24 18:00 | 67 | 65.96
2018-01-24 18:30 | 66.43 | 65.15
2018-01-24 19:00 | 68.03 | 66.86
2018-01-24 19:30 | 68.34 | 67.27
2018-01-24 20:00 | 66.94 | 65.73
2018-01-24 20:30 | 64.73 | 63.25
2018-01-24 21:00 | 62.34 | 60.55
2018-01-24 21:30 | 59.64 | 57.39
2018-01-24 22:00 | 57.16 | 54.46
2018-01-24 22:30 | 54.97 | 51.43
2018-01-24 23:00 | 54.7 | 50.61
2018-01-24 23:30 | 51.13 | 47.29
2018-01-25 | 48.87 | 45.37
2018-01-25 00:30 | 48.05 | 44.46
2018-01-25 01:00 | 46.99 | 43.29
2018-01-25 01:30 | 46.26 | 42.48
2018-01-25 02:00 | 45.56 | 41.68
2018-01-25 02:30 | 44.95 | 40.98
2018-01-25 03:00 | 44.54 | 40.51
2018-01-25 03:30 | 44.29 | 40.22
2018-01-25 04:00 | 44.35 | 40.29
2018-01-25 04:30 | 44.72 | 40.71
2018-01-25 05:00 | 45.8 | 41.93
2018-01-25 05:30 | 48.41 | 44.89
2018-01-25 06:00 | 50.47 | 47.16
2018-01-25 06:30 | 53.45 | 52.78
2018-01-25 07:00 | 57.18 | 57
2018-01-25 07:30 | 64.33 | 63.72
2018-01-25 08:00 | 70.08 | 68.2
2018-01-25 08:30 | 69.74 | 67.93
2018-01-25 09:00 | 69.48 | 67.66
2018-01-25 09:30 | 69.82 | 68
2018-01-25 10:00 | 70.99 | 69.19
2018-01-25 10:30 | 72.84 | 71.06
2018-01-25 11:00 | 73.33 | 71.55
2018-01-25 11:30 | 76.55 | 74.85
2018-01-25 12:00 | 74.52 | 72.79
2018-01-25 12:30 | 73.72 | 71.97
2018-01-25 13:00 | 72.84 | 71.06
2018-01-25 13:30 | 74.58 | 72.85
2018-01-25 14:00 | 73.41 | 71.65
2018-01-25 14:30 | 74.52 | 72.8
2018-01-25 15:00 | 72.67 | 70.9
2018-01-25 15:30 | 73.35 | 71.62
2018-01-25 16:00 | 74.41 | 72.76
2018-01-25 16:30 | 73.33 | 71.69
2018-01-25 17:00 | 72.36 | 70.74
2018-01-25 17:30 | 68.16 | 67.22
2018-01-25 18:00 | 66.43 | 65.33
2018-01-25 18:30 | 66.26 | 64.92
2018-01-25 19:00 | 66.36 | 64.95
2018-01-25 19:30 | 66.81 | 65.58
2018-01-25 20:00 | 65.44 | 64
2018-01-25 20:30 | 63.45 | 61.66
2018-01-25 21:00 | 61.78 | 59.79
2018-01-25 21:30 | 59.01 | 56.4
2018-01-25 22:00 | 55.71 | 52.82
2018-01-25 22:30 | 51.14 | 49.72
2018-01-25 23:00 | 49.78 | 48.88
2018-01-25 23:30 | 46.64 | 45.64
2018-01-26 | 44.68 | 43.6
2018-01-26 00:30 | 42.63 | 41.47
2018-01-26 01:00 | 40.6 | 39.5
2018-01-26 01:30 | 40.03 | 38.92
2018-01-26 02:00 | 39.6 | 38.47
2018-01-26 02:30 | 39.27 | 38.13
2018-01-26 03:00 | 38.73 | 37.57
2018-01-26 03:30 | 38.61 | 37.43
2018-01-26 04:00 | 38.41 | 37.23
2018-01-26 04:30 | 38.22 | 37.03
2018-01-26 05:00 | 38.6 | 37.44
2018-01-26 05:30 | 39.26 | 38.13
2018-01-26 06:00 | 39.28 | 38.14
2018-01-26 06:30 | 41.24 | 40.19
2018-01-26 07:00 | 42.84 | 41.85
2018-01-26 07:30 | 44.5 | 43.59
2018-01-26 08:00 | 46.15 | 45.31
2018-01-26 08:30 | 47.81 | 47.02
2018-01-26 09:00 | 48.71 | 48.01
2018-01-26 09:30 | 49.23 | 48.49
2018-01-26 10:00 | 49.87 | 49.02
2018-01-26 10:30 | 50.78 | 49.8
2018-01-26 11:00 | 50.77 | 49.75
2018-01-26 11:30 | 51.1 | 50.01
2018-01-26 12:00 | 51.96 | 50.85
2018-01-26 12:30 | 54.17 | 53.05
2018-01-26 13:00 | 52.98 | 51.85
2018-01-26 13:30 | 53.84 | 52.68
2018-01-26 14:00 | 54.99 | 53.8
2018-01-26 14:30 | 54.74 | 53.65
2018-01-26 15:00 | 55.98 | 54.95
2018-01-26 15:30 | 55.31 | 53.54
2018-01-26 16:00 | 57.66 | 54.98
2018-01-26 16:30 | 58.98 | 56.39
2018-01-26 17:00 | 58.65 | 56.06
2018-01-26 17:30 | 59.14 | 56.61
2018-01-26 18:00 | 58.68 | 56.16
2018-01-26 18:30 | 57.28 | 54.75
2018-01-26 19:00 | 57.69 | 55.18
2018-01-26 19:30 | 58.71 | 56.23
2018-01-26 20:00 | 57.78 | 55.26
2018-01-26 20:30 | 56.32 | 53.73
2018-01-26 21:00 | 54.87 | 52.22
2018-01-26 21:30 | 52.98 | 50.24
2018-01-26 22:00 | 51.52 | 48.71
2018-01-26 22:30 | 49.79 | 46.87
2018-01-26 23:00 | 49.4 | 46.47
2018-01-26 23:30 | 46.61 | 43.5
2018-01-27 | 44.82 | 41.59
2018-01-27 00:30 | 43.77 | 40.47
2018-01-27 01:00 | 42.5 | 39.09
2018-01-27 01:30 | 39.35 | 38.4
2018-01-27 02:00 | 38.8 | 38.04
2018-01-27 02:30 | 38.44 | 37.68
2018-01-27 03:00 | 38.05 | 37.28
2018-01-27 03:30 | 37.6 | 36.83
2018-01-27 04:00 | 37.53 | 36.75
2018-01-27 04:30 | 37.72 | 36.94
2018-01-27 05:00 | 37.98 | 37.2
2018-01-27 05:30 | 38.97 | 38.2
2018-01-27 06:00 | 39.35 | 38.59
2018-01-27 06:30 | 40.87 | 40.13
2018-01-27 07:00 | 43.54 | 42.81
2018-01-27 07:30 | 47.32 | 46.62
2018-01-27 08:00 | 48.86 | 48.16
2018-01-27 08:30 | 51.01 | 50.29
2018-01-27 09:00 | 53.05 | 52.16
2018-01-27 09:30 | 53.82 | 52.78
2018-01-27 10:00 | 54.28 | 53.15
2018-01-27 10:30 | 53.78 | 52.54
2018-01-27 11:00 | 54.66 | 53.39
2018-01-27 11:30 | 54.56 | 53.27
2018-01-27 12:00 | 54.36 | 53.07
2018-01-27 12:30 | 56.28 | 55.07
2018-01-27 13:00 | 55.4 | 54.22
2018-01-27 13:30 | 55.22 | 54.16
2018-01-27 14:00 | 53.46 | 52.79
2018-01-27 14:30 | 52.66 | 52.01
2018-01-27 15:00 | 53.05 | 52.42
2018-01-27 15:30 | 53.64 | 52.99
2018-01-27 16:00 | 54.39 | 53.73
2018-01-27 16:30 | 55.32 | 54.59
2018-01-27 17:00 | 56.05 | 55.24
2018-01-27 17:30 | 56.41 | 55.41
2018-01-27 18:00 | 57.1 | 56.02
2018-01-27 18:30 | 57.53 | 56.38
2018-01-27 19:00 | 57.85 | 56.76
2018-01-27 19:30 | 58 | 57.05
2018-01-27 20:00 | 57.53 | 56.56
2018-01-27 20:30 | 55.67 | 54.53
2018-01-27 21:00 | 55.28 | 54.08
2018-01-27 21:30 | 53.86 | 52.5
2018-01-27 22:00 | 52.56 | 51.01
2018-01-27 22:30 | 50.68 | 48.91
2018-01-27 23:00 | 50.46 | 48.62
2018-01-27 23:30 | 47.96 | 45.77
2018-01-28 | 47.61 | 43.41
2018-01-28 00:30 | 47.07 | 42.48
2018-01-28 01:00 | 45.69 | 40.91
2018-01-28 01:30 | 45.22 | 40.37
2018-01-28 02:00 | 44.26 | 39.26
2018-01-28 02:30 | 43.54 | 38.45
2018-01-28 03:00 | 43.25 | 38.11
2018-01-28 03:30 | 43.2 | 38.05
2018-01-28 04:00 | 43.13 | 37.96
2018-01-28 04:30 | 43.14 | 37.98
2018-01-28 05:00 | 42.92 | 37.73
2018-01-28 05:30 | 43.33 | 38.21
2018-01-28 06:00 | 42.8 | 37.57
2018-01-28 06:30 | 43.36 | 38.21
2018-01-28 07:00 | 44.2 | 39.22
2018-01-28 07:30 | 46.69 | 42.11
2018-01-28 08:00 | 47.66 | 43.24
2018-01-28 08:30 | 49.46 | 45.29
2018-01-28 09:00 | 49.31 | 45.19
2018-01-28 09:30 | 49.83 | 45.83
2018-01-28 10:00 | 50.53 | 46.67
2018-01-28 10:30 | 50.98 | 47.22
2018-01-28 11:00 | 51.34 | 47.65
2018-01-28 11:30 | 52.03 | 48.44
2018-01-28 12:00 | 52.86 | 49.34
2018-01-28 12:30 | 55.2 | 51.86
2018-01-28 13:00 | 55.17 | 51.8
2018-01-28 13:30 | 53.55 | 50.08
2018-01-28 14:00 | 54.51 | 51.14
2018-01-28 14:30 | 54.65 | 51.26
2018-01-28 15:00 | 55.83 | 52.52
2018-01-28 15:30 | 56.29 | 52.99
2018-01-28 16:00 | 57.74 | 54.52
2018-01-28 16:30 | 59.09 | 55.95
2018-01-28 17:00 | 59.51 | 56.38
2018-01-28 17:30 | 60.55 | 57.46
2018-01-28 18:00 | 61.99 | 58.95
2018-01-28 18:30 | 62.64 | 59.62
2018-01-28 19:00 | 63.26 | 60.3
2018-01-28 19:30 | 63.85 | 60.98
2018-01-28 20:00 | 61.64 | 60.82
2018-01-28 20:30 | 59.67 | 58.85
2018-01-28 21:00 | 57.22 | 56.18
2018-01-28 21:30 | 55.23 | 54
2018-01-28 22:00 | 53 | 51.52
2018-01-28 22:30 | 50.67 | 49.25
2018-01-28 23:00 | 52 | 51.78
2018-01-28 23:30 | 48.14 | 47.97
2018-01-29 | 45.76 | 45.65
2018-01-29 00:30 | 45.01 | 44.91
2018-01-29 01:00 | 43.49 | 43.41
2018-01-29 01:30 | 42.69 | 42.61
2018-01-29 02:00 | 42.35 | 42.26
2018-01-29 02:30 | 41.9 | 41.83
2018-01-29 03:00 | 40.85 | 40.78
2018-01-29 03:30 | 40.2 | 40.14
2018-01-29 04:00 | 40.23 | 40.16
2018-01-29 04:30 | 40.69 | 40.62
2018-01-29 05:00 | 41.64 | 41.55
2018-01-29 05:30 | 44.46 | 44.29
2018-01-29 06:00 | 47.76 | 47.43
2018-01-29 06:30 | 53.69 | 53.02
2018-01-29 07:00 | 58.67 | 58.18
2018-01-29 07:30 | 64.54 | 64.34
2018-01-29 08:00 | 69.63 | 69.6
2018-01-29 08:30 | 68.97 | 68.93
2018-01-29 09:00 | 70.1 | 70.08
2018-01-29 09:30 | 70.7 | 70.68
2018-01-29 10:00 | 70.54 | 70.52
2018-01-29 10:30 | 70.21 | 70.18
2018-01-29 11:00 | 70.75 | 70.71
2018-01-29 11:30 | 71.87 | 71.82
2018-01-29 12:00 | 71.32 | 71.27
2018-01-29 12:30 | 71.7 | 71.66
2018-01-29 13:00 | 71.57 | 71.52
2018-01-29 13:30 | 72.27 | 72.22
2018-01-29 14:00 | 72.95 | 72.91
2018-01-29 14:30 | 74.03 | 73.97
2018-01-29 15:00 | 73.77 | 73.72
2018-01-29 15:30 | 73.66 | 73.63
2018-01-29 16:00 | 74.85 | 74.83
2018-01-29 16:30 | 75.1 | 75.08
2018-01-29 17:00 | 74.22 | 74.14
2018-01-29 17:30 | 72.18 | 71.8
2018-01-29 18:00 | 70.61 | 69.81
2018-01-29 18:30 | 70 | 68.87
2018-01-29 19:00 | 70.65 | 69.52
2018-01-29 19:30 | 70.96 | 69.93
2018-01-29 20:00 | 69.73 | 68.58
2018-01-29 20:30 | 67.24 | 65.83
2018-01-29 21:00 | 63.12 | 62.2
2018-01-29 21:30 | 60.33 | 59.46
2018-01-29 22:00 | 58.87 | 56.32
2018-01-29 22:30 | 55.94 | 53.28
2018-01-29 23:00 | 54.65 | 51.93
2018-01-29 23:30 | 50.91 | 47.99
2018-01-30 | 48.58 | 45.54
2018-01-30 00:30 | 47.62 | 44.52
2018-01-30 01:00 | 46.15 | 42.95
2018-01-30 01:30 | 45.45 | 42.2
2018-01-30 02:00 | 44.58 | 41.28
2018-01-30 02:30 | 43.85 | 40.49
2018-01-30 03:00 | 43.21 | 39.81
2018-01-30 03:30 | 42.61 | 39.17
2018-01-30 04:00 | 42.31 | 38.84
2018-01-30 04:30 | 42.75 | 39.31
2018-01-30 05:00 | 43.42 | 40.04
2018-01-30 05:30 | 45.36 | 42.1
2018-01-30 06:00 | 47.5 | 44.37
2018-01-30 06:30 | 52.39 | 49.52
2018-01-30 07:00 | 57.68 | 55.11
2018-01-30 07:30 | 62.81 | 60.38
2018-01-30 08:00 | 66.11 | 63.72
2018-01-30 08:30 | 68.73 | 66.39
2018-01-30 09:00 | 70.69 | 68.46
2018-01-30 09:30 | 71.28 | 69.06
2018-01-30 10:00 | 73.21 | 69.82
2018-01-30 10:30 | 76.71 | 71.96
2018-01-30 11:00 | 77.21 | 72.81
2018-01-30 11:30 | 72.82 | 72.46
2018-01-30 12:00 | 71.47 | 71.1
2018-01-30 12:30 | 74.49 | 74.13
2018-01-30 13:00 | 74.08 | 73.73
2018-01-30 13:30 | 73.15 | 72.79
2018-01-30 14:00 | 74.41 | 74.05
2018-01-30 14:30 | 74.93 | 74.57
2018-01-30 15:00 | 78.54 | 78.21
2018-01-30 15:30 | 76.26 | 75.95
2018-01-30 16:00 | 68.93 | 68.39
2018-01-30 16:30 | 64.2 | 61.13
2018-01-30 17:00 | 62.44 | 59.27
2018-01-30 17:30 | 58.9 | 55.4
2018-01-30 18:00 | 59.92 | 56.38
2018-01-30 18:30 | 60.25 | 56.66
2018-01-30 19:00 | 61.17 | 57.63
2018-01-30 19:30 | 61.42 | 57.95
2018-01-30 20:00 | 60.46 | 56.92
2018-01-30 20:30 | 58.71 | 54.99
2018-01-30 21:00 | 55.58 | 52.09
2018-01-30 21:30 | 53.68 | 50.03
2018-01-30 22:00 | 49.8 | 47.73
2018-01-30 22:30 | 45.37 | 45.12
2018-01-30 23:00 | 44.35 | 44.14
2018-01-30 23:30 | 41.02 | 40.87
2018-01-31 | 38.96 | 38.86
2018-01-31 00:30 | 37.39 | 37.32
2018-01-31 01:00 | 36.11 | 36.05
2018-01-31 01:30 | 35.74 | 35.67
2018-01-31 02:00 | 34.84 | 34.79
2018-01-31 02:30 | 34.35 | 34.31
2018-01-31 03:00 | 33.89 | 33.81
2018-01-31 03:30 | 33.51 | 33.28
2018-01-31 04:00 | 33.39 | 33.15
2018-01-31 04:30 | 33.77 | 33.51
2018-01-31 05:00 | 34.96 | 34.64
2018-01-31 05:30 | 37.47 | 37
2018-01-31 06:00 | 39.61 | 39.03
2018-01-31 06:30 | 45.15 | 44.16
2018-01-31 07:00 | 49.75 | 48.98
2018-01-31 07:30 | 55.4 | 54.52
2018-01-31 08:00 | 58.47 | 57.75
2018-01-31 08:30 | 60.28 | 59.49
2018-01-31 09:00 | 63.32 | 61.84
2018-01-31 09:30 | 64.24 | 62.53
2018-01-31 10:00 | 65.46 | 63.66
2018-01-31 10:30 | 67.01 | 65.12
2018-01-31 11:00 | 68.36 | 66.48
2018-01-31 11:30 | 69.6 | 67.75
2018-01-31 12:00 | 69.11 | 68.64
2018-01-31 12:30 | 71.49 | 71.12
2018-01-31 13:00 | 70.76 | 70.4
2018-01-31 13:30 | 72.12 | 71.75
2018-01-31 14:00 | 74.01 | 73.65
2018-01-31 14:30 | 74.99 | 74.63
2018-01-31 15:00 | 75.06 | 74.71
2018-01-31 15:30 | 75.2 | 74.86
2018-01-31 16:00 | 76.45 | 76.13
2018-01-31 16:30 | 76.86 | 76.56
2018-01-31 17:00 | 76.28 | 76
2018-01-31 17:30 | 73.98 | 73.57
2018-01-31 18:00 | 71.94 | 71.19
2018-01-31 18:30 | 71.37 | 70.28
2018-01-31 19:00 | 71.14 | 69.94
2018-01-31 19:30 | 71.48 | 70.4
2018-01-31 20:00 | 70.07 | 68.86
2018-01-31 20:30 | 66.12 | 65.66
2018-01-31 21:00 | 62.72 | 62.24
2018-01-31 21:30 | 59.82 | 59.22
2018-01-31 22:00 | 56.36 | 55.74
2018-01-31 22:30 | 53.2 | 52.55
2018-01-31 23:00 | 51.65 | 51
2018-01-31 23:30 | 47.97 | 47.28
2018-02-01 | 45.83 | 45.12
2018-02-01 00:30 | 44.47 | 43.75
2018-02-01 01:00 | 42.65 | 41.9
2018-02-01 01:30 | 41.66 | 40.9
2018-02-01 02:00 | 40.51 | 39.74
2018-02-01 02:30 | 39.81 | 39.03
2018-02-01 03:00 | 39.35 | 38.57
2018-02-01 03:30 | 38.59 | 37.79
2018-02-01 04:00 | 38.25 | 37.46
2018-02-01 04:30 | 38.35 | 37.55
2018-02-01 05:00 | 39.25 | 38.45
2018-02-01 05:30 | 41.22 | 40.44
2018-02-01 06:00 | 43.05 | 42.3
2018-02-01 06:30 | 48.43 | 47.72
2018-02-01 07:00 | 53.45 | 52.83
2018-02-01 07:30 | 59.81 | 58.88
2018-02-01 08:00 | 64.39 | 63.82
2018-02-01 08:30 | 67.11 | 66.76
2018-02-01 09:00 | 69.65 | 69.3
2018-02-01 09:30 | 71.14 | 70.78
2018-02-01 10:00 | 71.97 | 71.61
2018-02-01 10:30 | 73.02 | 72.66
2018-02-01 11:00 | 73.56 | 73.19
2018-02-01 11:30 | 73.64 | 73.26
2018-02-01 12:00 | 74.37 | 74
2018-02-01 12:30 | 76.15 | 75.79
2018-02-01 13:00 | 75.62 | 75.26
2018-02-01 13:30 | 76.54 | 76.18
2018-02-01 14:00 | 77.04 | 76.69
2018-02-01 14:30 | 77.82 | 77.46
2018-02-01 15:00 | 77.72 | 77.36
2018-02-01 15:30 | 77.59 | 77.25
2018-02-01 16:00 | 78.51 | 78.19
2018-02-01 16:30 | 78.86 | 78.56
2018-02-01 17:00 | 77.77 | 77.49
2018-02-01 17:30 | 75.43 | 75.05
2018-02-01 18:00 | 75.16 | 74.67
2018-02-01 18:30 | 75.08 | 74.42
2018-02-01 19:00 | 75.1 | 74.35
2018-02-01 19:30 | 75.58 | 74.95
2018-02-01 20:00 | 74.03 | 73.28
2018-02-01 20:30 | 71.67 | 70.67
2018-02-01 21:00 | 68.6 | 67.33
2018-02-01 21:30 | 64.24 | 63
2018-02-01 22:00 | 59.28 | 58.54
2018-02-01 22:30 | 56.05 | 55.4
2018-02-01 23:00 | 54.45 | 53.82
2018-02-01 23:30 | 50.44 | 49.76
2018-02-02 | 47.87 | 47.17
2018-02-02 00:30 | 46.69 | 45.98
2018-02-02 01:00 | 45.13 | 44.41
2018-02-02 01:30 | 44.19 | 43.45
2018-02-02 02:00 | 43.35 | 42.6
2018-02-02 02:30 | 42.65 | 41.89
2018-02-02 03:00 | 41.91 | 41.16
2018-02-02 03:30 | 41.37 | 40.62
2018-02-02 04:00 | 41.34 | 40.58
2018-02-02 04:30 | 41.34 | 40.58
2018-02-02 05:00 | 42.26 | 41.49
2018-02-02 05:30 | 44.58 | 43.84
2018-02-02 06:00 | 46.25 | 45.52
2018-02-02 06:30 | 52.02 | 51.34
2018-02-02 07:00 | 57.24 | 56.58
2018-02-02 07:30 | 60.22 | 59.58
2018-02-02 08:00 | 62.61 | 62.1
2018-02-02 08:30 | 64.96 | 64.53
2018-02-02 09:00 | 65.88 | 65.54
2018-02-02 09:30 | 71.14 | 70.8
2018-02-02 10:00 | 72.97 | 72.62
2018-02-02 10:30 | 73 | 72.65
2018-02-02 11:00 | 74.07 | 73.72
2018-02-02 11:30 | 74.71 | 74.36
2018-02-02 12:00 | 75.78 | 75.44
2018-02-02 12:30 | 75.92 | 75.58
2018-02-02 13:00 | 72.91 | 72.57
2018-02-02 13:30 | 68.95 | 68.63
2018-02-02 14:00 | 69.73 | 69.41
2018-02-02 14:30 | 74.31 | 73.99
2018-02-02 15:00 | 75.16 | 74.84
2018-02-02 15:30 | 74.65 | 74.34
2018-02-02 16:00 | 75.64 | 75.35
2018-02-02 16:30 | 76.3 | 76.02
2018-02-02 17:00 | 74.72 | 74.37
2018-02-02 17:30 | 72.62 | 72.09
2018-02-02 18:00 | 69.94 | 69.51
2018-02-02 18:30 | 67.63 | 67.25
2018-02-02 19:00 | 67.76 | 67.38
2018-02-02 19:30 | 68.38 | 68.02
2018-02-02 20:00 | 67.3 | 66.92
2018-02-02 20:30 | 64.95 | 64.51
2018-02-02 21:00 | 62.49 | 62
2018-02-02 21:30 | 60.01 | 59.43
2018-02-02 22:00 | 56.65 | 55.87
2018-02-02 22:30 | 53.27 | 52.39
2018-02-02 23:00 | 51.7 | 51.07
2018-02-02 23:30 | 48.09 | 47.41
2018-02-03 | 46.06 | 45.36
2018-02-03 00:30 | 44.52 | 43.82
2018-02-03 01:00 | 43.16 | 42.43
2018-02-03 01:30 | 42.17 | 41.43
2018-02-03 02:00 | 41.69 | 40.95
2018-02-03 02:30 | 41.05 | 40.3
2018-02-03 03:00 | 40.3 | 39.53
2018-02-03 03:30 | 39.86 | 39.11
2018-02-03 04:00 | 38.98 | 38.21
2018-02-03 04:30 | 38.95 | 38.18
2018-02-03 05:00 | 38.89 | 38.12
2018-02-03 05:30 | 39.78 | 39.01
2018-02-03 06:00 | 40.34 | 39.58
2018-02-03 06:30 | 42.34 | 41.6
2018-02-03 07:00 | 44.12 | 43.39
2018-02-03 07:30 | 47.46 | 46.75
2018-02-03 08:00 | 50.91 | 50.21
2018-02-03 08:30 | 54.12 | 53.25
2018-02-03 09:00 | 56.03 | 54.93
2018-02-03 09:30 | 57.48 | 56.25
2018-02-03 10:00 | 57.8 | 56.45
2018-02-03 10:30 | 58.74 | 57.26
2018-02-03 11:00 | 58.85 | 57.33
2018-02-03 11:30 | 58.53 | 56.96
2018-02-03 12:00 | 58.99 | 57.39
2018-02-03 12:30 | 61.85 | 60.37
2018-02-03 13:00 | 62.07 | 60.59
2018-02-03 13:30 | 63.03 | 61.62
2018-02-03 14:00 | 63.52 | 62.17
2018-02-03 14:30 | 64.77 | 62.39
2018-02-03 15:00 | 63.76 | 61.33
2018-02-03 15:30 | 63.68 | 61.27
2018-02-03 16:00 | 65.08 | 62.76
2018-02-03 16:30 | 65.57 | 63.6
2018-02-03 17:00 | 63.3 | 61.46
2018-02-03 17:30 | 62.81 | 61.8
2018-02-03 18:00 | 63.09 | 62.5
2018-02-03 18:30 | 63.39 | 62.79
2018-02-03 19:00 | 63.79 | 63.29
2018-02-03 19:30 | 63.6 | 63.1
2018-02-03 20:00 | 62.27 | 61.72
2018-02-03 20:30 | 59.89 | 59.19
2018-02-03 21:00 | 55.97 | 54.99
2018-02-03 21:30 | 52.65 | 51.25
2018-02-03 22:00 | 49.8 | 47.93
2018-02-03 22:30 | 44.9 | 42.71
2018-02-03 23:00 | 46.74 | 44.21
2018-02-03 23:30 | 43.61 | 40.74
2018-02-04 | 39.48 | 38.31
2018-02-04 00:30 | 38.29 | 37.07
2018-02-04 01:00 | 36.85 | 35.56
2018-02-04 01:30 | 36.17 | 34.85
2018-02-04 02:00 | 35.71 | 34.37
2018-02-04 02:30 | 35.54 | 34.18
2018-02-04 03:00 | 35.09 | 33.71
2018-02-04 03:30 | 34.74 | 33.34
2018-02-04 04:00 | 34.68 | 33.27
2018-02-04 04:30 | 34.62 | 33.21
2018-02-04 05:00 | 34.65 | 33.26
2018-02-04 05:30 | 35.18 | 33.8
2018-02-04 06:00 | 35.19 | 33.81
2018-02-04 06:30 | 35.6 | 34.22
2018-02-04 07:00 | 36.27 | 34.94
2018-02-04 07:30 | 38.14 | 36.91
2018-02-04 08:00 | 40.52 | 39.48
2018-02-04 08:30 | 41.19 | 40.25
2018-02-04 09:00 | 41.51 | 40.6
2018-02-04 09:30 | 42.94 | 42.02
2018-02-04 10:00 | 43.92 | 43.01
2018-02-04 10:30 | 43.76 | 42.81
2018-02-04 11:00 | 44.23 | 43.26
2018-02-04 11:30 | 43.98 | 43.02
2018-02-04 12:00 | 42.66 | 41.67
2018-02-04 12:30 | 45.42 | 44.52
2018-02-04 13:00 | 43.44 | 42.53
2018-02-04 13:30 | 43.34 | 42.39
2018-02-04 14:00 | 42.74 | 41.77
2018-02-04 14:30 | 41.86 | 40.86
2018-02-04 15:00 | 41.57 | 40.54
2018-02-04 15:30 | 42.08 | 41.04
2018-02-04 16:00 | 42.03 | 40.97
2018-02-04 16:30 | 42.96 | 41.92
2018-02-04 17:00 | 43.21 | 42.17
2018-02-04 17:30 | 44.34 | 43.31
2018-02-04 18:00 | 46.06 | 45.08
2018-02-04 18:30 | 46.76 | 45.79
2018-02-04 19:00 | 46.93 | 45.98
2018-02-04 19:30 | 46.88 | 45.93
2018-02-04 20:00 | 45.43 | 44.43
2018-02-04 20:30 | 43.7 | 42.66
2018-02-04 21:00 | 42.03 | 40.92
2018-02-04 21:30 | 40.57 | 39.41
2018-02-04 22:00 | 39.14 | 37.92
2018-02-04 22:30 | 37.21 | 35.9
2018-02-04 23:00 | 36.99 | 35.65
2018-02-04 23:30 | 34.9 | 33.47
2018-02-05 | 33.96 | 32.48
2018-02-05 00:30 | 33.5 | 32
2018-02-05 01:00 | 32.24 | 30.79
2018-02-05 01:30 | 32.07 | 30.68
2018-02-05 02:00 | 31.52 | 30.11
2018-02-05 02:30 | 31.42 | 29.99
2018-02-05 03:00 | 31.33 | 29.9
2018-02-05 03:30 | 31.47 | 30.04
2018-02-05 04:00 | 31.58 | 30.17
2018-02-05 04:30 | 32.07 | 30.69
2018-02-05 05:00 | 33.09 | 31.78
2018-02-05 05:30 | 35.87 | 34.73
2018-02-05 06:00 | 38.4 | 37.38
2018-02-05 06:30 | 43.52 | 42.57
2018-02-05 07:00 | 48.24 | 47.41
2018-02-05 07:30 | 54.99 | 54.19
2018-02-05 08:00 | 57.34 | 56.49
2018-02-05 08:30 | 58.68 | 57.47
2018-02-05 09:00 | 59.39 | 58.5
2018-02-05 09:30 | 58 | 57.23
2018-02-05 10:00 | 59.28 | 58.3
2018-02-05 10:30 | 59.18 | 58.24
2018-02-05 11:00 | 62.21 | 61.33
2018-02-05 11:30 | 60.62 | 59.72
2018-02-05 12:00 | 63.88 | 63.05
2018-02-05 12:30 | 62.26 | 61.41
2018-02-05 13:00 | 62.58 | 61.73
2018-02-05 13:30 | 63.29 | 62.47
2018-02-05 14:00 | 65.7 | 64.91
2018-02-05 14:30 | 67.82 | 67.06
2018-02-05 15:00 | 66.16 | 65.34
2018-02-05 15:30 | 64.01 | 63.14
2018-02-05 16:00 | 63.35 | 62.46
2018-02-05 16:30 | 64.51 | 63.59
2018-02-05 17:00 | 62.53 | 61.51
2018-02-05 17:30 | 60.15 | 58.63
2018-02-05 18:00 | 59.09 | 56.8
2018-02-05 18:30 | 59.09 | 56.22
2018-02-05 19:00 | 59.44 | 56.51
2018-02-05 19:30 | 59.8 | 57.11
2018-02-05 20:00 | 58.57 | 55.67
2018-02-05 20:30 | 56.74 | 53.48
2018-02-05 21:00 | 54.89 | 51.21
2018-02-05 21:30 | 53.43 | 49.12
2018-02-05 22:00 | 50.6 | 46.59
2018-02-05 22:30 | 47.93 | 44.19
2018-02-05 23:00 | 47.25 | 43.41
2018-02-05 23:30 | 44.44 | 40.29
2018-02-06 | 42.91 | 38.55
2018-02-06 00:30 | 41.74 | 37.18
2018-02-06 01:00 | 40.82 | 36.11
2018-02-06 01:30 | 40.26 | 35.46
2018-02-06 02:00 | 39.77 | 34.9
2018-02-06 02:30 | 39.56 | 34.63
2018-02-06 03:00 | 39.18 | 34.17
2018-02-06 03:30 | 38.58 | 33.8
2018-02-06 04:00 | 38.64 | 33.93
2018-02-06 04:30 | 39.01 | 34.36
2018-02-06 05:00 | 40.01 | 35.55
2018-02-06 05:30 | 42.07 | 37.97
2018-02-06 06:00 | 44.45 | 40.69
2018-02-06 06:30 | 49.26 | 46.03
2018-02-06 07:00 | 53.49 | 50.51
2018-02-06 07:30 | 58.01 | 57.04
2018-02-06 08:00 | 61.01 | 60.46
2018-02-06 08:30 | 62.31 | 61.91
2018-02-06 09:00 | 63.95 | 63.77
2018-02-06 09:30 | 64.45 | 64.28
2018-02-06 10:00 | 62.74 | 62.6
2018-02-06 10:30 | 62.08 | 61.98
2018-02-06 11:00 | 62.76 | 62.7
2018-02-06 11:30 | 64.19 | 64.16
2018-02-06 12:00 | 65.72 | 65.69
2018-02-06 12:30 | 65.97 | 65.94
2018-02-06 13:00 | 64.51 | 64.47
2018-02-06 13:30 | 64.55 | 64.5
2018-02-06 14:00 | 65.77 | 65.7
2018-02-06 14:30 | 63.02 | 62.93
2018-02-06 15:00 | 62.52 | 62.44
2018-02-06 15:30 | 62.27 | 62.13
2018-02-06 16:00 | 63.11 | 62.88
2018-02-06 16:30 | 63.33 | 62.89
2018-02-06 17:00 | 62.56 | 61.82
2018-02-06 17:30 | 61.04 | 59.58
2018-02-06 18:00 | 60.44 | 58.21
2018-02-06 18:30 | 60.74 | 57.15
2018-02-06 19:00 | 61.59 | 58.07
2018-02-06 19:30 | 61.83 | 58.36
2018-02-06 20:00 | 60.7 | 57.12
2018-02-06 20:30 | 58 | 54.18
2018-02-06 21:00 | 55.17 | 51.72
2018-02-06 21:30 | 52.86 | 49.63
2018-02-06 22:00 | 50.55 | 47.1
2018-02-06 22:30 | 48.34 | 44.63
2018-02-06 23:00 | 47.49 | 43.67
2018-02-06 23:30 | 44.65 | 40.52
2018-02-07 | 42.98 | 38.61
2018-02-07 00:30 | 41.67 | 37.08
2018-02-07 01:00 | 40.52 | 35.76
2018-02-07 01:30 | 40.22 | 35.43
2018-02-07 02:00 | 40.07 | 35.25
2018-02-07 02:30 | 39.75 | 34.86
2018-02-07 03:00 | 39.34 | 34.36
2018-02-07 03:30 | 38.59 | 33.87
2018-02-07 04:00 | 38.43 | 33.67
2018-02-07 04:30 | 39.03 | 34.4
2018-02-07 05:00 | 40.13 | 35.69
2018-02-07 05:30 | 41.67 | 37.51
2018-02-07 06:00 | 43.95 | 40.11
2018-02-07 06:30 | 48.6 | 45.34
2018-02-07 07:00 | 53.67 | 50.71
2018-02-07 07:30 | 57.39 | 56.93
2018-02-07 08:00 | 60.29 | 59.81
2018-02-07 08:30 | 61.22 | 60.39
2018-02-07 09:00 | 62.63 | 61.5
2018-02-07 09:30 | 62.66 | 61.48
2018-02-07 10:00 | 63.04 | 61.75
2018-02-07 10:30 | 64.02 | 62.45
2018-02-07 11:00 | 65.85 | 63.39
2018-02-07 11:30 | 66.29 | 63.83
2018-02-07 12:00 | 65.83 | 63.36
2018-02-07 12:30 | 66.96 | 64.54
2018-02-07 13:00 | 67.08 | 64.31
2018-02-07 13:30 | 67.19 | 64.14
2018-02-07 14:00 | 67.26 | 64.28
2018-02-07 14:30 | 67.37 | 64.43
2018-02-07 15:00 | 66.99 | 64.55
2018-02-07 15:30 | 66.28 | 63.88
2018-02-07 16:00 | 67.1 | 64.77
2018-02-07 16:30 | 67.04 | 64.77
2018-02-07 17:00 | 65.33 | 63.07
2018-02-07 17:30 | 63.02 | 60.76
2018-02-07 18:00 | 60.7 | 58.45
2018-02-07 18:30 | 59.96 | 57.72
2018-02-07 19:00 | 60.26 | 58.05
2018-02-07 19:30 | 61.31 | 59.12
2018-02-07 20:00 | 60.04 | 57.82
2018-02-07 20:30 | 57.48 | 55.17
2018-02-07 21:00 | 54.69 | 52.26
2018-02-07 21:30 | 49.74 | 49.57
2018-02-07 22:00 | 47.34 | 47.17
2018-02-07 22:30 | 45.03 | 44.79
2018-02-07 23:00 | 44.29 | 43.98
2018-02-07 23:30 | 41.31 | 40.87
2018-02-08 | 39.23 | 38.67
2018-02-08 00:30 | 38.45 | 37.8
2018-02-08 01:00 | 36.98 | 36.21
2018-02-08 01:30 | 38.88 | 35.55
2018-02-08 02:00 | 40.07 | 35.2
2018-02-08 02:30 | 39.42 | 34.43
2018-02-08 03:00 | 38.98 | 33.9
2018-02-08 03:30 | 38.6 | 33.56
2018-02-08 04:00 | 38.18 | 33.33
2018-02-08 04:30 | 38.21 | 33.37
2018-02-08 05:00 | 39.15 | 34.48
2018-02-08 05:30 | 41.13 | 36.84
2018-02-08 06:00 | 43.06 | 39.04
2018-02-08 06:30 | 47.86 | 44.47
2018-02-08 07:00 | 52.6 | 49.35
2018-02-08 07:30 | 58.45 | 54.92
2018-02-08 08:00 | 61.59 | 58.42
2018-02-08 08:30 | 62.9 | 59.92
2018-02-08 09:00 | 63.97 | 61.12
2018-02-08 09:30 | 62.24 | 59.3
2018-02-08 10:00 | 64.73 | 61.93
2018-02-08 10:30 | 64.07 | 61.26
2018-02-08 11:00 | 65.07 | 62.32
2018-02-08 11:30 | 64.4 | 61.57
2018-02-08 12:00 | 62.47 | 59.54
2018-02-08 12:30 | 62.93 | 60.04
2018-02-08 13:00 | 61.53 | 58.55
2018-02-08 13:30 | 60.35 | 57.38
2018-02-08 14:00 | 61.6 | 58.77
2018-02-08 14:30 | 64.07 | 61.38
2018-02-08 15:00 | 65 | 62.3
2018-02-08 15:30 | 62.64 | 59.74
2018-02-08 16:00 | 62.25 | 59.27
2018-02-08 16:30 | 61.3 | 58.12
2018-02-08 17:00 | 59.48 | 56.11
2018-02-08 17:30 | 58.84 | 55.28
2018-02-08 18:00 | 58.08 | 55.43
2018-02-08 18:30 | 55.05 | 55.03
2018-02-08 19:00 | 55.38 | 55.36
2018-02-08 19:30 | 56.16 | 56.14
2018-02-08 20:00 | 55.02 | 55
2018-02-08 20:30 | 50.49 | 50.45
2018-02-08 21:00 | 50.54 | 50.48
2018-02-08 21:30 | 47.78 | 47.61
2018-02-08 22:00 | 45.31 | 45.03
2018-02-08 22:30 | 43.21 | 42.83
2018-02-08 23:00 | 42.64 | 42.18
2018-02-08 23:30 | 39 | 38.74
2018-02-09 | 36.55 | 36.38
2018-02-09 00:30 | 35.53 | 35.28
2018-02-09 01:00 | 34.34 | 34.02
2018-02-09 01:30 | 33.55 | 33.22
2018-02-09 02:00 | 33.16 | 32.79
2018-02-09 02:30 | 32.07 | 32.02
2018-02-09 03:00 | 31.89 | 31.86
2018-02-09 03:30 | 31.73 | 31.7
2018-02-09 04:00 | 31.88 | 31.84
2018-02-09 04:30 | 32.02 | 31.99
2018-02-09 05:00 | 32.84 | 32.82
2018-02-09 05:30 | 34.97 | 34.93
2018-02-09 06:00 | 37.63 | 37.56
2018-02-09 06:30 | 43.18 | 43
2018-02-09 07:00 | 47.8 | 47.66
2018-02-09 07:30 | 54.21 | 53.78
2018-02-09 08:00 | 57.84 | 57.02
2018-02-09 08:30 | 58.8 | 57.96
2018-02-09 09:00 | 58.54 | 57.89
2018-02-09 09:30 | 59.28 | 58.78
2018-02-09 10:00 | 62.16 | 61.66
2018-02-09 10:30 | 61.16 | 60.63
2018-02-09 11:00 | 59.48 | 59.07
2018-02-09 11:30 | 59.73 | 59.5
2018-02-09 12:00 | 59.47 | 59.31
2018-02-09 12:30 | 60.63 | 60.46
2018-02-09 13:00 | 59.59 | 59.4
2018-02-09 13:30 | 59.85 | 59.67
2018-02-09 14:00 | 59.79 | 59.54
2018-02-09 14:30 | 59.99 | 59.71
2018-02-09 15:00 | 59.91 | 59.59
2018-02-09 15:30 | 59.81 | 59.38
2018-02-09 16:00 | 60.71 | 60.15
2018-02-09 16:30 | 61.05 | 60.25
2018-02-09 17:00 | 60.65 | 59.54
2018-02-09 17:30 | 59.64 | 57.84
2018-02-09 18:00 | 59.33 | 55.67
2018-02-09 18:30 | 58.05 | 54.19
2018-02-09 19:00 | 58.53 | 54.72
2018-02-09 19:30 | 59.13 | 55.4
2018-02-09 20:00 | 57.9 | 54.05
2018-02-09 20:30 | 55.84 | 51.75
2018-02-09 21:00 | 54.03 | 49.75
2018-02-09 21:30 | 52.3 | 47.76
2018-02-09 22:00 | 49.32 | 45.37
2018-02-09 22:30 | 47.07 | 43.18
2018-02-09 23:00 | 46.28 | 42.46
2018-02-09 23:30 | 43.45 | 39.42
2018-02-10 | 41.24 | 37.07
2018-02-10 00:30 | 39.89 | 35.66
2018-02-10 01:00 | 38.57 | 34.14
2018-02-10 01:30 | 38.02 | 33.49
2018-02-10 02:00 | 37.39 | 32.76
2018-02-10 02:30 | 37.04 | 32.36
2018-02-10 03:00 | 36.55 | 31.75
2018-02-10 03:30 | 36.04 | 31.16
2018-02-10 04:00 | 35.79 | 30.84
2018-02-10 04:30 | 35.35 | 30.71
2018-02-10 05:00 | 35.53 | 30.96
2018-02-10 05:30 | 36.39 | 32
2018-02-10 06:00 | 37.01 | 32.71
2018-02-10 06:30 | 38.47 | 34.39
2018-02-10 07:00 | 39.95 | 36.16
2018-02-10 07:30 | 42.42 | 39.02
2018-02-10 08:00 | 42.63 | 41.55
2018-02-10 08:30 | 44.07 | 43.56
2018-02-10 09:00 | 46.04 | 45.32
2018-02-10 09:30 | 47.28 | 46.42
2018-02-10 10:00 | 47.56 | 46.56
2018-02-10 10:30 | 47.24 | 46.18
2018-02-10 11:00 | 47.27 | 46.13
2018-02-10 11:30 | 47.37 | 46.17
2018-02-10 12:00 | 47.15 | 46.07
2018-02-10 12:30 | 47.51 | 46.58
2018-02-10 13:00 | 45.44 | 44.59
2018-02-10 13:30 | 45.02 | 44.2
2018-02-10 14:00 | 45.48 | 44.69
2018-02-10 14:30 | 45.58 | 44.82
2018-02-10 15:00 | 45.83 | 45.19
2018-02-10 15:30 | 46.26 | 45.7
2018-02-10 16:00 | 47.28 | 46.79
2018-02-10 16:30 | 48.6 | 48.18
2018-02-10 17:00 | 49.66 | 49.29
2018-02-10 17:30 | 49.82 | 49.57
2018-02-10 18:00 | 50.66 | 50.47
2018-02-10 18:30 | 50.91 | 50.74
2018-02-10 19:00 | 50.64 | 50.48
2018-02-10 19:30 | 51.42 | 51.2
2018-02-10 20:00 | 50.57 | 50.35
2018-02-10 20:30 | 47.95 | 47.83
2018-02-10 21:00 | 45.52 | 45.43
2018-02-10 21:30 | 43.82 | 43.74
2018-02-10 22:00 | 41.98 | 41.92
2018-02-10 22:30 | 39.93 | 39.88
2018-02-10 23:00 | 39.53 | 39.49
2018-02-10 23:30 | 36.41 | 36.38
2018-02-11 | 34.59 | 34.56
2018-02-11 00:30 | 33.5 | 33.46
2018-02-11 01:00 | 32.22 | 32.16
2018-02-11 01:30 | 31.61 | 31.54
2018-02-11 02:00 | 31.16 | 31.07
2018-02-11 02:30 | 30.46 | 30.37
2018-02-11 03:00 | 30 | 29.92
2018-02-11 03:30 | 29.79 | 29.7
2018-02-11 04:00 | 29.35 | 29.27
2018-02-11 04:30 | 29.37 | 29.28
2018-02-11 05:00 | 29.91 | 29.82
2018-02-11 05:30 | 30.07 | 29.98
2018-02-11 06:00 | 29.59 | 29.51
2018-02-11 06:30 | 30.27 | 30.19
2018-02-11 07:00 | 31.26 | 31.17
2018-02-11 07:30 | 32.91 | 32.78
2018-02-11 08:00 | 34.19 | 33.98
2018-02-11 08:30 | 35.61 | 35.29
2018-02-11 09:00 | 36.68 | 36.14
2018-02-11 09:30 | 37.99 | 37.59
2018-02-11 10:00 | 38.4 | 38.21
2018-02-11 10:30 | 40.17 | 39.89
2018-02-11 11:00 | 41.2 | 40.84
2018-02-11 11:30 | 42.55 | 42.1
2018-02-11 12:00 | 44.26 | 43.76
2018-02-11 12:30 | 47.21 | 46.71
2018-02-11 13:00 | 47.61 | 47.08
2018-02-11 13:30 | 48.84 | 48.24
2018-02-11 14:00 | 49.32 | 48.74
2018-02-11 14:30 | 49 | 48.52
2018-02-11 15:00 | 50.09 | 49.61
2018-02-11 15:30 | 50.8 | 50.37
2018-02-11 16:00 | 51.83 | 51.44
2018-02-11 16:30 | 53.19 | 52.8
2018-02-11 17:00 | 53.56 | 53.21
2018-02-11 17:30 | 54.32 | 54.04
2018-02-11 18:00 | 55.74 | 55.49
2018-02-11 18:30 | 56.84 | 56.63
2018-02-11 19:00 | 57.77 | 57.53
2018-02-11 19:30 | 59.13 | 58.81
2018-02-11 20:00 | 57.78 | 57.49
2018-02-11 20:30 | 54.84 | 54.62
2018-02-11 21:00 | 52.18 | 51.99
2018-02-11 21:30 | 49.44 | 49.32
2018-02-11 22:00 | 46.1 | 46.03
2018-02-11 22:30 | 43.37 | 43.31
2018-02-11 23:00 | 42.49 | 42.44
2018-02-11 23:30 | 39.12 | 39.08
2018-02-12 | 37.13 | 37.1
2018-02-12 00:30 | 35.96 | 35.94
2018-02-12 01:00 | 34.54 | 34.51
2018-02-12 01:30 | 33.78 | 33.76
2018-02-12 02:00 | 33.49 | 33.47
2018-02-12 02:30 | 32.96 | 32.92
2018-02-12 03:00 | 32.66 | 32.62
2018-02-12 03:30 | 32.18 | 32.13
2018-02-12 04:00 | 32.07 | 32.02
2018-02-12 04:30 | 32.46 | 32.43
2018-02-12 05:00 | 33.57 | 33.54
2018-02-12 05:30 | 35.83 | 35.79
2018-02-12 06:00 | 38.45 | 38.39
2018-02-12 06:30 | 43.75 | 43.54
2018-02-12 07:00 | 49.16 | 48.98
2018-02-12 07:30 | 56.39 | 55.9
2018-02-12 08:00 | 59.75 | 59.47
2018-02-12 08:30 | 60.04 | 59.95
2018-02-12 09:00 | 63.39 | 63.37
2018-02-12 09:30 | 65.21 | 65.17
2018-02-12 10:00 | 65.95 | 65.9
2018-02-12 10:30 | 66.75 | 66.68
2018-02-12 11:00 | 68.31 | 68.29
2018-02-12 11:30 | 70.22 | 70.18
2018-02-12 12:00 | 72.48 | 72.43
2018-02-12 12:30 | 75.16 | 75.11
2018-02-12 13:00 | 74.9 | 74.86
2018-02-12 13:30 | 75.21 | 75.17
2018-02-12 14:00 | 76.13 | 76.07
2018-02-12 14:30 | 77.48 | 77.42
2018-02-12 15:00 | 78.27 | 78.22
2018-02-12 15:30 | 78.89 | 78.84
2018-02-12 16:00 | 81.05 | 81.02
2018-02-12 16:30 | 81.21 | 81.19
2018-02-12 17:00 | 80.41 | 80.36
2018-02-12 17:30 | 77.95 | 77.69
2018-02-12 18:00 | 75.84 | 75.22
2018-02-12 18:30 | 74.07 | 73.02
2018-02-12 19:00 | 73.98 | 72.95
2018-02-12 19:30 | 73.87 | 72.86
2018-02-12 20:00 | 71.94 | 70.77
2018-02-12 20:30 | 68.78 | 67.21
2018-02-12 21:00 | 65.28 | 63.22
2018-02-12 21:30 | 62.24 | 59.73
2018-02-12 22:00 | 57.02 | 55.37
2018-02-12 22:30 | 52.33 | 52.01
2018-02-12 23:00 | 50.41 | 50.17
2018-02-12 23:30 | 46.15 | 45.98
2018-02-13 | 43.51 | 43.4
2018-02-13 00:30 | 42.59 | 42.5
2018-02-13 01:00 | 40.95 | 40.87
2018-02-13 01:30 | 39.97 | 39.9
2018-02-13 02:00 | 39.44 | 39.37
2018-02-13 02:30 | 38.68 | 38.63
2018-02-13 03:00 | 38.07 | 38.02
2018-02-13 03:30 | 37.74 | 37.7
2018-02-13 04:00 | 37.34 | 37.3
2018-02-13 04:30 | 37.73 | 37.69
2018-02-13 05:00 | 39.01 | 38.95
2018-02-13 05:30 | 42.07 | 41.97
2018-02-13 06:00 | 44.84 | 44.67
2018-02-13 06:30 | 50.86 | 50.37
2018-02-13 07:00 | 56.61 | 56.19
2018-02-13 07:30 | 59.79 | 59.51
2018-02-13 08:00 | 66.33 | 66.14
2018-02-13 08:30 | 68.81 | 68.73
2018-02-13 09:00 | 70 | 69.98
2018-02-13 09:30 | 71.93 | 71.91
2018-02-13 10:00 | 72.63 | 72.6
2018-02-13 10:30 | 74.29 | 74.24
2018-02-13 11:00 | 76.43 | 76.35
2018-02-13 11:30 | 78.38 | 78.26
2018-02-13 12:00 | 81.86 | 80.67
2018-02-13 12:30 | 83.84 | 83.33
2018-02-13 13:00 | 83.47 | 83.12
2018-02-13 13:30 | 84.28 | 83.93
2018-02-13 14:00 | 85.3 | 84.95
2018-02-13 14:30 | 86.02 | 85.67
2018-02-13 15:00 | 86.02 | 85.67
2018-02-13 15:30 | 84.97 | 84.63
2018-02-13 16:00 | 86.09 | 85.77
2018-02-13 16:30 | 85.83 | 85.53
2018-02-13 17:00 | 84.65 | 84.37
2018-02-13 17:30 | 81.74 | 81.43
2018-02-13 18:00 | 79.47 | 79.03
2018-02-13 18:30 | 77.15 | 76.31
2018-02-13 19:00 | 76.79 | 75.93
2018-02-13 19:30 | 76.78 | 75.92
2018-02-13 20:00 | 74.74 | 73.84
2018-02-13 20:30 | 71.14 | 70.34
2018-02-13 21:00 | 67.67 | 66.83
2018-02-13 21:30 | 64.39 | 63.48
2018-02-13 22:00 | 60.34 | 59.32
2018-02-13 22:30 | 56.68 | 55.55
2018-02-13 23:00 | 54.99 | 53.78
2018-02-13 23:30 | 51.48 | 49.9
2018-02-14 | 47.99 | 47.12
2018-02-14 00:30 | 46.77 | 45.86
2018-02-14 01:00 | 44.96 | 44
2018-02-14 01:30 | 44.14 | 43.16
2018-02-14 02:00 | 43.05 | 42.02
2018-02-14 02:30 | 42.21 | 41.14
2018-02-14 03:00 | 41.45 | 40.35
2018-02-14 03:30 | 41.15 | 40.04
2018-02-14 04:00 | 41.06 | 39.94
2018-02-14 04:30 | 41.32 | 40.21
2018-02-14 05:00 | 42.43 | 41.37
2018-02-14 05:30 | 44.75 | 43.78
2018-02-14 06:00 | 47 | 46.11
2018-02-14 06:30 | 53.57 | 52.74
2018-02-14 07:00 | 59.77 | 58.97
2018-02-14 07:30 | 66.69 | 65.78
2018-02-14 08:00 | 71.5 | 70.25
2018-02-14 08:30 | 75.93 | 73.26
2018-02-14 09:00 | 77.34 | 75.05
2018-02-14 09:30 | 75.38 | 74.96
2018-02-14 10:00 | 75.98 | 75.58
2018-02-14 10:30 | 76.74 | 76.27
2018-02-14 11:00 | 78.75 | 78.11
2018-02-14 11:30 | 80.26 | 79.51
2018-02-14 12:00 | 80.89 | 80.11
2018-02-14 12:30 | 83.09 | 82.29
2018-02-14 13:00 | 82.24 | 81.85
2018-02-14 13:30 | 83.16 | 82.78
2018-02-14 14:00 | 84.43 | 84.05
2018-02-14 14:30 | 85.35 | 85
2018-02-14 15:00 | 85.29 | 84.94
2018-02-14 15:30 | 85.06 | 84.72
2018-02-14 16:00 | 86.33 | 86
2018-02-14 16:30 | 86.66 | 86.36
2018-02-14 17:00 | 85.89 | 85.6
2018-02-14 17:30 | 82.57 | 82.27
2018-02-14 18:00 | 79.87 | 79.21
2018-02-14 18:30 | 77.75 | 76.91
2018-02-14 19:00 | 77.83 | 76.98
2018-02-14 19:30 | 76.68 | 75.82
2018-02-14 20:00 | 74.88 | 73.99
2018-02-14 20:30 | 74.1 | 73.13
2018-02-14 21:00 | 68.96 | 67.68
2018-02-14 21:30 | 64.64 | 63.6
2018-02-14 22:00 | 60.88 | 59.87
2018-02-14 22:30 | 57.49 | 56.38
2018-02-14 23:00 | 54.54 | 53.75
2018-02-14 23:30 | 51.12 | 50.33
2018-02-15 | 48.7 | 47.85
2018-02-15 00:30 | 47.22 | 46.32
2018-02-15 01:00 | 45.4 | 44.45
2018-02-15 01:30 | 44.66 | 43.69
2018-02-15 02:00 | 43.69 | 42.67
2018-02-15 02:30 | 42.85 | 41.8
2018-02-15 03:00 | 41.93 | 40.84
2018-02-15 03:30 | 41.69 | 40.59
2018-02-15 04:00 | 41.38 | 40.26
2018-02-15 04:30 | 41.7 | 40.6
2018-02-15 05:00 | 42.35 | 41.28
2018-02-15 05:30 | 44.81 | 43.84
2018-02-15 06:00 | 47.13 | 46.24
2018-02-15 06:30 | 52.88 | 52.05
2018-02-15 07:00 | 58.82 | 58.03
2018-02-15 07:30 | 66.03 | 65.46
2018-02-15 08:00 | 71.22 | 71.15
2018-02-15 08:30 | 74.34 | 74.32
2018-02-15 09:00 | 75.74 | 75.7
2018-02-15 09:30 | 78.9 | 77.3
2018-02-15 10:00 | 78.34 | 76.69
2018-02-15 10:30 | 79.34 | 77.7
2018-02-15 11:00 | 81.07 | 79.44
2018-02-15 11:30 | 82.36 | 80.78
2018-02-15 12:00 | 84.46 | 82.93
2018-02-15 12:30 | 87.2 | 85.71
2018-02-15 13:00 | 87.06 | 85.57
2018-02-15 13:30 | 87.82 | 86.33
2018-02-15 14:00 | 89.07 | 87.6
2018-02-15 14:30 | 89.45 | 87.99
2018-02-15 15:00 | 89.44 | 88.01
2018-02-15 15:30 | 89.86 | 88.43
2018-02-15 16:00 | 90.63 | 89.24
2018-02-15 16:30 | 90.21 | 88.86
2018-02-15 17:00 | 88.74 | 87.4
2018-02-15 17:30 | 85.91 | 84.58
2018-02-15 18:00 | 82.56 | 81.22
2018-02-15 18:30 | 81.26 | 79.94
2018-02-15 19:00 | 81.01 | 79.68
2018-02-15 19:30 | 79.78 | 78.45
2018-02-15 20:00 | 76.99 | 75.61
2018-02-15 20:30 | 76.53 | 75.16
2018-02-15 21:00 | 79.32 | 78
2018-02-15 21:30 | 73.44 | 71.98
2018-02-15 22:00 | 65.06 | 63.14
2018-02-15 22:30 | 58.31 | 58.1
2018-02-15 23:00 | 54.49 | 54.47
2018-02-15 23:30 | 51.65 | 51.61
2018-02-16 | 49.6 | 49.53
2018-02-16 00:30 | 47.71 | 47.58
2018-02-16 01:00 | 46.23 | 46.11
2018-02-16 01:30 | 45.13 | 45.1
2018-02-16 02:00 | 44.75 | 44.73
2018-02-16 02:30 | 44.15 | 44.13
2018-02-16 03:00 | 43.56 | 43.54
2018-02-16 03:30 | 43.15 | 43.13
2018-02-16 04:00 | 42.96 | 42.93
2018-02-16 04:30 | 43.18 | 43.16
2018-02-16 05:00 | 44.27 | 44.25
2018-02-16 05:30 | 46.53 | 46.49
2018-02-16 06:00 | 49.42 | 49.35
2018-02-16 06:30 | 55.56 | 55.31
2018-02-16 07:00 | 61.87 | 61.16
2018-02-16 07:30 | 68.32 | 68.25
2018-02-16 08:00 | 72.5 | 72.47
2018-02-16 08:30 | 75.88 | 75.86
2018-02-16 09:00 | 77.42 | 77.36
2018-02-16 09:30 | 77.39 | 77.35
2018-02-16 10:00 | 77.49 | 77.44
2018-02-16 10:30 | 78.12 | 78.06
2018-02-16 11:00 | 79.22 | 79.12
2018-02-16 11:30 | 81.11 | 80.97
2018-02-16 12:00 | 82.32 | 82.15
2018-02-16 12:30 | 83.7 | 83.4
2018-02-16 13:00 | 84.91 | 84.58
2018-02-16 13:30 | 84.96 | 84.63
2018-02-16 14:00 | 85.74 | 85.42
2018-02-16 14:30 | 88.01 | 87.7
2018-02-16 15:00 | 83.04 | 82.72
2018-02-16 15:30 | 83.9 | 83.6
2018-02-16 16:00 | 84.93 | 84.64
2018-02-16 16:30 | 83.77 | 83.5
2018-02-16 17:00 | 83.17 | 82.91
2018-02-16 17:30 | 81.4 | 81.08
2018-02-16 18:00 | 77.21 | 76.83
2018-02-16 18:30 | 74.31 | 74.01
2018-02-16 19:00 | 74.37 | 74.06
2018-02-16 19:30 | 73.96 | 73.65
2018-02-16 20:00 | 71.87 | 71.56
2018-02-16 20:30 | 68.64 | 68.28
2018-02-16 21:00 | 65.98 | 65.57
2018-02-16 21:30 | 62.65 | 62.04
2018-02-16 22:00 | 56.47 | 55.32
2018-02-16 22:30 | 52.33 | 50.05
2018-02-16 23:00 | 52.61 | 48.6
2018-02-16 23:30 | 48.89 | 44.45
2018-02-17 | 48.65 | 41.93
2018-02-17 00:30 | 48.01 | 40.57
2018-02-17 01:00 | 46.64 | 38.89
2018-02-17 01:30 | 45.95 | 38.07
2018-02-17 02:00 | 45.3 | 37.27
2018-02-17 02:30 | 44.78 | 36.59
2018-02-17 03:00 | 44.64 | 36.42
2018-02-17 03:30 | 44.12 | 35.72
2018-02-17 04:00 | 43.76 | 35.26
2018-02-17 04:30 | 43.74 | 35.26
2018-02-17 05:00 | 43.9 | 35.5
2018-02-17 05:30 | 44.72 | 36.51
2018-02-17 06:00 | 45.2 | 37.12
2018-02-17 06:30 | 46.84 | 39.2
2018-02-17 07:00 | 48.33 | 41.12
2018-02-17 07:30 | 50.42 | 44.11
2018-02-17 08:00 | 48.63 | 47.76
2018-02-17 08:30 | 50.81 | 49.85
2018-02-17 09:00 | 52.59 | 51.47
2018-02-17 09:30 | 54.99 | 53.71
2018-02-17 10:00 | 55.67 | 54.14
2018-02-17 10:30 | 56.58 | 55.65
2018-02-17 11:00 | 58.01 | 57.12
2018-02-17 11:30 | 59.02 | 58.16
2018-02-17 12:00 | 59.34 | 58.51
2018-02-17 12:30 | 58.17 | 57.46
2018-02-17 13:00 | 59.08 | 58.45
2018-02-17 13:30 | 60.55 | 59.94
2018-02-17 14:00 | 60.45 | 59.91
2018-02-17 14:30 | 60.34 | 59.87
2018-02-17 15:00 | 62.07 | 61.61
2018-02-17 15:30 | 63.94 | 63.55
2018-02-17 16:00 | 63.26 | 62.92
2018-02-17 16:30 | 62.66 | 62.37
2018-02-17 17:00 | 61.16 | 60.91
2018-02-17 17:30 | 61.26 | 61.04
2018-02-17 18:00 | 62.64 | 62.13
2018-02-17 18:30 | 62.67 | 62.12
2018-02-17 19:00 | 62.74 | 62.13
2018-02-17 19:30 | 63.74 | 63.04
2018-02-17 20:00 | 62.08 | 61.41
2018-02-17 20:30 | 59.05 | 58.49
2018-02-17 21:00 | 57.45 | 56.94
2018-02-17 21:30 | 55.42 | 55
2018-02-17 22:00 | 53.5 | 53.14
2018-02-17 22:30 | 50.91 | 50.61
2018-02-17 23:00 | 49.86 | 49.63
2018-02-17 23:30 | 46.07 | 45.91
2018-02-18 | 43.92 | 43.81
2018-02-18 00:30 | 42.45 | 42.37
2018-02-18 01:00 | 40.76 | 40.69
2018-02-18 01:30 | 39.79 | 39.72
2018-02-18 02:00 | 39.23 | 39.17
2018-02-18 02:30 | 38.55 | 38.49
2018-02-18 03:00 | 38.02 | 37.96
2018-02-18 03:30 | 37.68 | 37.63
2018-02-18 04:00 | 37.15 | 37.1
2018-02-18 04:30 | 37.16 | 37.11
2018-02-18 05:00 | 37.25 | 37.19
2018-02-18 05:30 | 37.75 | 37.7
2018-02-18 06:00 | 37.65 | 37.6
2018-02-18 06:30 | 38.37 | 38.32
2018-02-18 07:00 | 38.94 | 38.87
2018-02-18 07:30 | 42.26 | 42.18
2018-02-18 08:00 | 43.55 | 43.4
2018-02-18 08:30 | 46.35 | 46.08
2018-02-18 09:00 | 48.31 | 47.91
2018-02-18 09:30 | 49.64 | 49.11
2018-02-18 10:00 | 50.81 | 50.16
2018-02-18 10:30 | 52.41 | 51.63
2018-02-18 11:00 | 53.48 | 52.62
2018-02-18 11:30 | 54.51 | 53.59
2018-02-18 12:00 | 55.01 | 54.06
2018-02-18 12:30 | 55.26 | 54.34
2018-02-18 13:00 | 55.55 | 54.68
2018-02-18 13:30 | 56.16 | 55.29
2018-02-18 14:00 | 56.47 | 55.61
2018-02-18 14:30 | 56 | 55.26
2018-02-18 15:00 | 56.82 | 56.07
2018-02-18 15:30 | 57.62 | 56.92
2018-02-18 16:00 | 58.65 | 57.98
2018-02-18 16:30 | 60 | 59.39
2018-02-18 17:00 | 60.07 | 59.51
2018-02-18 17:30 | 60.7 | 60.18
2018-02-18 18:00 | 62.05 | 61.57
2018-02-18 18:30 | 62.29 | 61.85
2018-02-18 19:00 | 62.88 | 62.36
2018-02-18 19:30 | 63.47 | 62.91
2018-02-18 20:00 | 60.94 | 60.44
2018-02-18 20:30 | 57.62 | 57.24
2018-02-18 21:00 | 55.33 | 54.99
2018-02-18 21:30 | 52.79 | 52.54
2018-02-18 22:00 | 49.78 | 49.61
2018-02-18 22:30 | 46.74 | 46.62
2018-02-18 23:00 | 45.85 | 45.76
2018-02-18 23:30 | 42.42 | 42.34
2018-02-19 | 40.42 | 40.36
2018-02-19 00:30 | 39.75 | 39.7
2018-02-19 01:00 | 38.04 | 37.99
2018-02-19 01:30 | 37.51 | 37.47
2018-02-19 02:00 | 37.05 | 37
2018-02-19 02:30 | 36.61 | 36.57
2018-02-19 03:00 | 36.04 | 36
2018-02-19 03:30 | 35.95 | 35.91
2018-02-19 04:00 | 35.85 | 35.81
2018-02-19 04:30 | 36.29 | 36.24
2018-02-19 05:00 | 37.29 | 37.24
2018-02-19 05:30 | 40.04 | 39.96
2018-02-19 06:00 | 42.75 | 42.62
2018-02-19 06:30 | 49.28 | 48.84
2018-02-19 07:00 | 54.96 | 54.6
2018-02-19 07:30 | 62.55 | 61.53
2018-02-19 08:00 | 67.61 | 66.38
2018-02-19 08:30 | 71.05 | 69.61
2018-02-19 09:00 | 73.78 | 71.95
2018-02-19 09:30 | 74.02 | 72.21
2018-02-19 10:00 | 73.45 | 71.58
2018-02-19 10:30 | 74.77 | 72.8
2018-02-19 11:00 | 75.37 | 73.77
2018-02-19 11:30 | 75.74 | 74.41
2018-02-19 12:00 | 71.01 | 69.51
2018-02-19 12:30 | 77.16 | 75.44
2018-02-19 13:00 | 77.67 | 75.97
2018-02-19 13:30 | 78.24 | 76.54
2018-02-19 14:00 | 78.33 | 76.63
2018-02-19 14:30 | 78.27 | 76.57
2018-02-19 15:00 | 78.69 | 76.99
2018-02-19 15:30 | 78.86 | 77.19
2018-02-19 16:00 | 79.71 | 78.08
2018-02-19 16:30 | 78.91 | 78.5
2018-02-19 17:00 | 77.65 | 77.36
2018-02-19 17:30 | 74.87 | 74.44
2018-02-19 18:00 | 72.19 | 71.42
2018-02-19 18:30 | 70.57 | 69.71
2018-02-19 19:00 | 74.81 | 74.03
2018-02-19 19:30 | 75.95 | 75.2
2018-02-19 20:00 | 73.52 | 72.72
2018-02-19 20:30 | 69.81 | 68.93
2018-02-19 21:00 | 61.62 | 60.71
2018-02-19 21:30 | 58.04 | 57.32
2018-02-19 22:00 | 54.44 | 53.64
2018-02-19 22:30 | 50.9 | 50.02
2018-02-19 23:00 | 49.57 | 48.62
2018-02-19 23:30 | 46.04 | 44.99
2018-02-20 | 44.03 | 42.91
2018-02-20 00:30 | 43.09 | 41.92
2018-02-20 01:00 | 41.46 | 40.22
2018-02-20 01:30 | 40.84 | 39.58
2018-02-20 02:00 | 40.42 | 39.14
2018-02-20 02:30 | 39.67 | 38.33
2018-02-20 03:00 | 40.3 | 37.77
2018-02-20 03:30 | 41.59 | 37.47
2018-02-20 04:00 | 41.56 | 37.49
2018-02-20 04:30 | 41.94 | 37.93
2018-02-20 05:00 | 42.89 | 39.03
2018-02-20 05:30 | 45.3 | 41.75
2018-02-20 06:00 | 47.47 | 44.19
2018-02-20 06:30 | 52.59 | 49.75
2018-02-20 07:00 | 57.57 | 55.03
2018-02-20 07:30 | 63.29 | 62.29
2018-02-20 08:00 | 65.99 | 65.05
2018-02-20 08:30 | 69.85 | 68.48
2018-02-20 09:00 | 72.65 | 70.95
2018-02-20 09:30 | 73.17 | 71.13
2018-02-20 10:00 | 74.99 | 72.79
2018-02-20 10:30 | 73.96 | 73.08
2018-02-20 11:00 | 74.69 | 74.33
2018-02-20 11:30 | 73.18 | 72.8
2018-02-20 12:00 | 74.71 | 74.34
2018-02-20 12:30 | 77.96 | 77.6
2018-02-20 13:00 | 79.04 | 78.7
2018-02-20 13:30 | 78.96 | 78.61
2018-02-20 14:00 | 76.74 | 76.37
2018-02-20 14:30 | 77.15 | 76.79
2018-02-20 15:00 | 77.25 | 76.89
2018-02-20 15:30 | 77.61 | 77.27
2018-02-20 16:00 | 78.29 | 77.97
2018-02-20 16:30 | 78.07 | 77.77
2018-02-20 17:00 | 76.9 | 76.59
2018-02-20 17:30 | 73.72 | 73.08
2018-02-20 18:00 | 71.03 | 70.08
2018-02-20 18:30 | 69.58 | 68.27
2018-02-20 19:00 | 69.66 | 68.44
2018-02-20 19:30 | 68.81 | 67.5
2018-02-20 20:00 | 66.33 | 64.74
2018-02-20 20:30 | 62.96 | 61.55
2018-02-20 21:00 | 60.14 | 59.36
2018-02-20 21:30 | 57.72 | 56.88
2018-02-20 22:00 | 50.22 | 49.15
2018-02-20 22:30 | 46.26 | 45.04
2018-02-20 23:00 | 45.81 | 44.66
2018-02-20 23:30 | 42.35 | 41.14
2018-02-21 | 40.2 | 38.88
2018-02-21 00:30 | 39.59 | 38.24
2018-02-21 01:00 | 38.17 | 36.76
2018-02-21 01:30 | 37.25 | 35.81
2018-02-21 02:00 | 36.68 | 35.2
2018-02-21 02:30 | 36.3 | 34.77
2018-02-21 03:00 | 35.76 | 34.21
2018-02-21 03:30 | 35.19 | 33.72
2018-02-21 04:00 | 35.18 | 33.77
2018-02-21 04:30 | 35.73 | 34.36
2018-02-21 05:00 | 36.67 | 35.35
2018-02-21 05:30 | 38.65 | 37.43
2018-02-21 06:00 | 41.76 | 40.69
2018-02-21 06:30 | 46.65 | 45.77
2018-02-21 07:00 | 51.37 | 50.56
2018-02-21 07:30 | 56.89 | 56.11
2018-02-21 08:00 | 60.83 | 59.86
2018-02-21 08:30 | 62.73 | 61.78
2018-02-21 09:00 | 63.73 | 62.84
2018-02-21 09:30 | 64.19 | 63.32
2018-02-21 10:00 | 64.47 | 63.62
2018-02-21 10:30 | 64.92 | 64.09
2018-02-21 11:00 | 66.09 | 65.32
2018-02-21 11:30 | 68.32 | 67.59
2018-02-21 12:00 | 69.32 | 68.6
2018-02-21 12:30 | 69.75 | 69.03
2018-02-21 13:00 | 68.99 | 68.26
2018-02-21 13:30 | 70.42 | 69.7
2018-02-21 14:00 | 72.1 | 71.41
2018-02-21 14:30 | 71.68 | 70.98
2018-02-21 15:00 | 71.19 | 70.47
2018-02-21 15:30 | 69.15 | 68.4
2018-02-21 16:00 | 69.49 | 68.71
2018-02-21 16:30 | 70.49 | 69.66
2018-02-21 17:00 | 67.11 | 66.17
2018-02-21 17:30 | 64.38 | 63.19
2018-02-21 18:00 | 63.53 | 61.8
2018-02-21 18:30 | 65.24 | 60.94
2018-02-21 19:00 | 67.88 | 61.61
2018-02-21 19:30 | 67.04 | 60.66
2018-02-21 20:00 | 65.12 | 58.47
2018-02-21 20:30 | 62.86 | 55.82
2018-02-21 21:00 | 60.96 | 53.53
2018-02-21 21:30 | 59.28 | 51.51
2018-02-21 22:00 | 57 | 49.18
2018-02-21 22:30 | 53.65 | 46.49
2018-02-21 23:00 | 52.77 | 45.44
2018-02-21 23:30 | 49.61 | 42.04
2018-02-22 | 48.09 | 40.17
2018-02-22 00:30 | 47.46 | 39.38
2018-02-22 01:00 | 46.39 | 38.02
2018-02-22 01:30 | 46.08 | 37.63
2018-02-22 02:00 | 45.57 | 36.96
2018-02-22 02:30 | 45.17 | 36.42
2018-02-22 03:00 | 44.59 | 35.62
2018-02-22 03:30 | 44.4 | 35.37
2018-02-22 04:00 | 44.32 | 35.27
2018-02-22 04:30 | 44.64 | 35.74
2018-02-22 05:00 | 45.46 | 36.83
2018-02-22 05:30 | 47.19 | 39.07
2018-02-22 06:00 | 49.7 | 42.22
2018-02-22 06:30 | 54.02 | 47.54
2018-02-22 07:00 | 57.7 | 51.98
2018-02-22 07:30 | 59.75 | 58.92
2018-02-22 08:00 | 62.83 | 61.63
2018-02-22 08:30 | 64.15 | 62.55
2018-02-22 09:00 | 66.72 | 65.82
2018-02-22 09:30 | 69.48 | 68.67
2018-02-22 10:00 | 69.69 | 68.88
2018-02-22 10:30 | 70.21 | 69.42
2018-02-22 11:00 | 69.62 | 68.84
2018-02-22 11:30 | 68.25 | 67.46
2018-02-22 12:00 | 69.1 | 68.34
2018-02-22 12:30 | 69.99 | 69.23
2018-02-22 13:00 | 67.97 | 67.18
2018-02-22 13:30 | 69.84 | 69.06
2018-02-22 14:00 | 70.35 | 69.58
2018-02-22 14:30 | 67.29 | 66.49
2018-02-22 15:00 | 67 | 66.21
2018-02-22 15:30 | 68.05 | 67.26
2018-02-22 16:00 | 68.49 | 67.68
2018-02-22 16:30 | 69.72 | 68.88
2018-02-22 17:00 | 66.92 | 65.98
2018-02-22 17:30 | 64.73 | 63.66
2018-02-22 18:00 | 65.61 | 64.31
2018-02-22 18:30 | 65.44 | 63.73
2018-02-22 19:00 | 66.41 | 64.79
2018-02-22 19:30 | 66.73 | 65.17
2018-02-22 20:00 | 64.65 | 62.84
2018-02-22 20:30 | 62.28 | 59.11
2018-02-22 21:00 | 60.5 | 56.79
2018-02-22 21:30 | 57.76 | 53.81
2018-02-22 22:00 | 54.42 | 50.15
2018-02-22 22:30 | 50.84 | 47.01
2018-02-22 23:00 | 49.3 | 45.66
2018-02-22 23:30 | 45.86 | 41.89
2018-02-23 | 43.75 | 39.8
2018-02-23 00:30 | 42.92 | 38.83
2018-02-23 01:00 | 41.56 | 37.3
2018-02-23 01:30 | 41.05 | 36.71
2018-02-23 02:00 | 40.64 | 36.22
2018-02-23 02:30 | 39.92 | 35.36
2018-02-23 03:00 | 39.44 | 34.89
2018-02-23 03:30 | 39.05 | 34.72
2018-02-23 04:00 | 39.48 | 35.2
2018-02-23 04:30 | 39.84 | 35.59
2018-02-23 05:00 | 39.18 | 34.88
2018-02-23 05:30 | 41.2 | 37.26
2018-02-23 06:00 | 44.3 | 40.78
2018-02-23 06:30 | 49.4 | 47.09
2018-02-23 07:00 | 52.59 | 52.32
2018-02-23 07:30 | 58.08 | 57.37
2018-02-23 08:00 | 62.04 | 61.45
2018-02-23 08:30 | 68 | 65.4
2018-02-23 09:00 | 69.33 | 66.64
2018-02-23 09:30 | 69.97 | 67.31
2018-02-23 10:00 | 69.77 | 67.1
2018-02-23 10:30 | 69.91 | 67.27
2018-02-23 11:00 | 69.55 | 66.89
2018-02-23 11:30 | 69.01 | 66.33
2018-02-23 12:00 | 68.77 | 66.08
2018-02-23 12:30 | 68.1 | 65.35
2018-02-23 13:00 | 66.23 | 63.37
2018-02-23 13:30 | 64.57 | 61.62
2018-02-23 14:00 | 64.24 | 61.26
2018-02-23 14:30 | 64.39 | 61.39
2018-02-23 15:00 | 60.6 | 57.36
2018-02-23 15:30 | 59.74 | 56.41
2018-02-23 16:00 | 59.42 | 56.07
2018-02-23 16:30 | 62.58 | 59.38
2018-02-23 17:00 | 61.44 | 58.08
2018-02-23 17:30 | 60.17 | 56.6
2018-02-23 18:00 | 58.72 | 54.91
2018-02-23 18:30 | 58.15 | 54.22
2018-02-23 19:00 | 58.89 | 55.06
2018-02-23 19:30 | 58.25 | 54.34
2018-02-23 20:00 | 55.33 | 52.02
2018-02-23 20:30 | 52.74 | 49.41
2018-02-23 21:00 | 51.3 | 47.84
2018-02-23 21:30 | 49.77 | 46.15
2018-02-23 22:00 | 47.98 | 44.14
2018-02-23 22:30 | 46.01 | 42.07
2018-02-23 23:00 | 45.48 | 41.6
2018-02-23 23:30 | 42.97 | 38.79
2018-02-24 | 41.27 | 36.83
2018-02-24 00:30 | 39.98 | 35.67
2018-02-24 01:00 | 38.59 | 34.18
2018-02-24 01:30 | 38.16 | 33.6
2018-02-24 02:00 | 37.84 | 33.22
2018-02-24 02:30 | 37.28 | 32.54
2018-02-24 03:00 | 37.03 | 32.26
2018-02-24 03:30 | 36.88 | 32.08
2018-02-24 04:00 | 36.8 | 31.97
2018-02-24 04:30 | 36.99 | 32.21
2018-02-24 05:00 | 37.39 | 32.69
2018-02-24 05:30 | 38.45 | 33.93
2018-02-24 06:00 | 39.53 | 35.19
2018-02-24 06:30 | 40.87 | 36.75
2018-02-24 07:00 | 42.89 | 39.04
2018-02-24 07:30 | 45.46 | 41.96
2018-02-24 08:00 | 47.96 | 44.76
2018-02-24 08:30 | 50.53 | 47.61
2018-02-24 09:00 | 52.28 | 49.54
2018-02-24 09:30 | 52.02 | 51.04
2018-02-24 10:00 | 52.12 | 51.29
2018-02-24 10:30 | 53.71 | 52.79
2018-02-24 11:00 | 55.62 | 54.78
2018-02-24 11:30 | 55.43 | 54.7
2018-02-24 12:00 | 51.72 | 51.09
2018-02-24 12:30 | 48.55 | 48.03
2018-02-24 13:00 | 44.65 | 44.13
2018-02-24 13:30 | 44.73 | 44.12
2018-02-24 14:00 | 45.09 | 44.38
2018-02-24 14:30 | 45.76 | 45.04
2018-02-24 15:00 | 48.29 | 47.62
2018-02-24 15:30 | 50.63 | 50.1
2018-02-24 16:00 | 49.7 | 49.23
2018-02-24 16:30 | 50.58 | 50.18
2018-02-24 17:00 | 50.2 | 49.88
2018-02-24 17:30 | 49.85 | 49.58
2018-02-24 18:00 | 51.01 | 50.81
2018-02-24 18:30 | 50.34 | 50.18
2018-02-24 19:00 | 50.4 | 50.19
2018-02-24 19:30 | 50.32 | 50.12
2018-02-24 20:00 | 49.07 | 48.89
2018-02-24 20:30 | 46.78 | 46.64
2018-02-24 21:00 | 45.9 | 45.77
2018-02-24 21:30 | 45.04 | 44.94
2018-02-24 22:00 | 43.51 | 43.42
2018-02-24 22:30 | 42.01 | 41.92
2018-02-24 23:00 | 41.74 | 41.67
2018-02-24 23:30 | 38.79 | 38.74
2018-02-25 | 37.04 | 37
2018-02-25 00:30 | 36.07 | 36.04
2018-02-25 01:00 | 34.98 | 34.95
2018-02-25 01:30 | 36.03 | 34.2
2018-02-25 02:00 | 37.39 | 33.79
2018-02-25 02:30 | 37.01 | 33.35
2018-02-25 03:00 | 36.71 | 33.03
2018-02-25 03:30 | 36.58 | 32.88
2018-02-25 04:00 | 35.54 | 33.11
2018-02-25 04:30 | 33.94 | 33.1
2018-02-25 05:00 | 33.72 | 32.87
2018-02-25 05:30 | 33.85 | 33.02
2018-02-25 06:00 | 34.24 | 33.42
2018-02-25 06:30 | 34.8 | 34
2018-02-25 07:00 | 35.65 | 34.85
2018-02-25 07:30 | 37.75 | 36.98
2018-02-25 08:00 | 41.01 | 39.67
2018-02-25 08:30 | 48.22 | 41.24
2018-02-25 09:00 | 48.15 | 41.26
2018-02-25 09:30 | 49.24 | 42.63
2018-02-25 10:00 | 51.04 | 44.69
2018-02-25 10:30 | 51.77 | 45.48
2018-02-25 11:00 | 51.94 | 45.64
2018-02-25 11:30 | 52.73 | 46.51
2018-02-25 12:00 | 53.27 | 47.17
2018-02-25 12:30 | 53.87 | 48.81
2018-02-25 13:00 | 51.22 | 49.24
2018-02-25 13:30 | 51.35 | 49.38
2018-02-25 14:00 | 50.53 | 48.52
2018-02-25 14:30 | 51.02 | 49.05
2018-02-25 15:00 | 54.11 | 52.27
2018-02-25 15:30 | 56.22 | 54.48
2018-02-25 16:00 | 55.83 | 54.08
2018-02-25 16:30 | 55.79 | 54.02
2018-02-25 17:00 | 53.49 | 51.56
2018-02-25 17:30 | 52.69 | 50.71
2018-02-25 18:00 | 54.19 | 52.25
2018-02-25 18:30 | 55.96 | 54.11
2018-02-25 19:00 | 56.96 | 55.24
2018-02-25 19:30 | 56.7 | 54.96
2018-02-25 20:00 | 54.94 | 53.09
2018-02-25 20:30 | 52.74 | 50.7
2018-02-25 21:00 | 51.37 | 49.22
2018-02-25 21:30 | 49.82 | 47.51
2018-02-25 22:00 | 47.95 | 45.41
2018-02-25 22:30 | 46.06 | 43.31
2018-02-25 23:00 | 45.58 | 42.67
2018-02-25 23:30 | 42.67 | 39.64
2018-02-26 | 40.82 | 37.73
2018-02-26 00:30 | 39.79 | 36.62
2018-02-26 01:00 | 38.53 | 35.25
2018-02-26 01:30 | 38.35 | 35.04
2018-02-26 02:00 | 38 | 34.65
2018-02-26 02:30 | 37.62 | 34.25
2018-02-26 03:00 | 37.32 | 33.92
2018-02-26 03:30 | 37.39 | 33.99
2018-02-26 04:00 | 37.32 | 33.92
2018-02-26 04:30 | 37.67 | 34.29
2018-02-26 05:00 | 39 | 35.71
2018-02-26 05:30 | 41.21 | 38.09
2018-02-26 06:00 | 44.19 | 41.26
2018-02-26 06:30 | 49.99 | 47.37
2018-02-26 07:00 | 55.07 | 52.73
2018-02-26 07:30 | 67.22 | 59.7
2018-02-26 08:00 | 71.05 | 63.26
2018-02-26 08:30 | 72.64 | 64.98
2018-02-26 09:00 | 74.5 | 67.09
2018-02-26 09:30 | 75.11 | 67.81
2018-02-26 10:00 | 75.91 | 68.7
2018-02-26 10:30 | 75.55 | 68.26
2018-02-26 11:00 | 76.55 | 69.35
2018-02-26 11:30 | 78.21 | 71.17
2018-02-26 12:00 | 80.86 | 73.83
2018-02-26 12:30 | 81.39 | 74.35
2018-02-26 13:00 | 80.96 | 73.89
2018-02-26 13:30 | 81.46 | 74.44
2018-02-26 14:00 | 82.37 | 75.42
2018-02-26 14:30 | 81.87 | 74.88
2018-02-26 15:00 | 81.78 | 74.81
2018-02-26 15:30 | 81.44 | 74.41
2018-02-26 16:00 | 83.13 | 76.38
2018-02-26 16:30 | 83.28 | 76.6
2018-02-26 17:00 | 78.54 | 74.72
2018-02-26 17:30 | 73.63 | 72.25
2018-02-26 18:00 | 71.12 | 69.73
2018-02-26 18:30 | 69.46 | 67.82
2018-02-26 19:00 | 70.59 | 68.84
2018-02-26 19:30 | 69.73 | 67.95
2018-02-26 20:00 | 67.04 | 65.21
2018-02-26 20:30 | 63.64 | 61.71
2018-02-26 21:00 | 60.91 | 58.9
2018-02-26 21:30 | 57.75 | 55.65
2018-02-26 22:00 | 54.68 | 52.47
2018-02-26 22:30 | 51.69 | 49.34
2018-02-26 23:00 | 50.47 | 48.15
2018-02-26 23:30 | 46.96 | 44.53
2018-02-27 | 44.99 | 42.46
2018-02-27 00:30 | 43.85 | 41.28
2018-02-27 01:00 | 42.46 | 39.79
2018-02-27 01:30 | 41.73 | 39.02
2018-02-27 02:00 | 41.12 | 38.38
2018-02-27 02:30 | 40.47 | 37.69
2018-02-27 03:00 | 39.99 | 37.18
2018-02-27 03:30 | 40.01 | 37.2
2018-02-27 04:00 | 40.25 | 37.36
2018-02-27 04:30 | 40.17 | 37.19
2018-02-27 05:00 | 41.44 | 38.53
2018-02-27 05:30 | 44.34 | 41.59
2018-02-27 06:00 | 46.92 | 44.31
2018-02-27 06:30 | 52.97 | 50.61
2018-02-27 07:00 | 58.24 | 56.09
2018-02-27 07:30 | 65.04 | 63.03
2018-02-27 08:00 | 73.85 | 66.58
2018-02-27 08:30 | 77.25 | 69.38
2018-02-27 09:00 | 78.69 | 71.23
2018-02-27 09:30 | 80.02 | 73.08
2018-02-27 10:00 | 79.6 | 72.61
2018-02-27 10:30 | 80.02 | 73.04
2018-02-27 11:00 | 76.78 | 72.95
2018-02-27 11:30 | 74.71 | 73.11
2018-02-27 12:00 | 74.46 | 72.84
2018-02-27 12:30 | 75.15 | 73.56
2018-02-27 13:00 | 76.06 | 74.5
2018-02-27 13:30 | 77.66 | 76.13
2018-02-27 14:00 | 77.83 | 76.3
2018-02-27 14:30 | 78.29 | 76.72
2018-02-27 15:00 | 78.71 | 77.17
2018-02-27 15:30 | 78.34 | 76.84
2018-02-27 16:00 | 76.82 | 75.35
2018-02-27 16:30 | 76.91 | 75.48
2018-02-27 17:00 | 74.59 | 73.16
2018-02-27 17:30 | 70.53 | 69.09
2018-02-27 18:00 | 67.54 | 65.97
2018-02-27 18:30 | 66.87 | 65.1
2018-02-27 19:00 | 68.47 | 66.82
2018-02-27 19:30 | 66.96 | 65.21
2018-02-27 20:00 | 64.51 | 62.59
2018-02-27 20:30 | 61.2 | 59.2
2018-02-27 21:00 | 58.96 | 56.89
2018-02-27 21:30 | 55.69 | 53.51
2018-02-27 22:00 | 52.61 | 50.3
2018-02-27 22:30 | 52.2 | 49.89
2018-02-27 23:00 | 49.15 | 46.72
2018-02-27 23:30 | 46.09 | 43.37
2018-02-28 | 44.15 | 41.39
2018-02-28 00:30 | 42.99 | 40.18
2018-02-28 01:00 | 42.19 | 39.31
2018-02-28 01:30 | 41.75 | 38.83
2018-02-28 02:00 | 41.33 | 38.38
2018-02-28 02:30 | 40.89 | 37.93
2018-02-28 03:00 | 40.26 | 37.26
2018-02-28 03:30 | 40.32 | 37.32
2018-02-28 04:00 | 40.15 | 37.12
2018-02-28 04:30 | 41.3 | 38.19
2018-02-28 05:00 | 42.47 | 39.43
2018-02-28 05:30 | 45.43 | 42.59
2018-02-28 06:00 | 49.1 | 46.43
2018-02-28 06:30 | 54.42 | 51.99
2018-02-28 07:00 | 60.85 | 57.13
2018-02-28 07:30 | 72.84 | 64.68
2018-02-28 08:00 | 75.1 | 67.18
2018-02-28 08:30 | 76.71 | 69.41
2018-02-28 09:00 | 79.89 | 73.05
2018-02-28 09:30 | 78.87 | 71.96
2018-02-28 10:00 | 76.49 | 69.32
2018-02-28 10:30 | 74.59 | 67.2
2018-02-28 11:00 | 74.94 | 67.56
2018-02-28 11:30 | 74.39 | 66.96
2018-02-28 12:00 | 74.86 | 67.46
2018-02-28 12:30 | 75.85 | 68.56
2018-02-28 13:00 | 75.17 | 67.81
2018-02-28 13:30 | 76.92 | 69.72
2018-02-28 14:00 | 79.09 | 72.14
2018-02-28 14:30 | 78.4 | 71.43
2018-02-28 15:00 | 77.53 | 70.42
2018-02-28 15:30 | 76.93 | 69.8
2018-02-28 16:00 | 76.83 | 69.75
2018-02-28 16:30 | 77.68 | 70.77
2018-02-28 17:00 | 77.84 | 71.05
2018-02-28 17:30 | 75.07 | 68.08
2018-02-28 18:00 | 67.89 | 65.86
2018-02-28 18:30 | 66.97 | 65.3
2018-02-28 19:00 | 68.28 | 66.7
2018-02-28 19:30 | 67.79 | 66.15
2018-02-28 20:00 | 65.56 | 63.76
2018-02-28 20:30 | 62.63 | 60.47
2018-02-28 21:00 | 60.3 | 57.78
2018-02-28 21:30 | 57.19 | 54.86
2018-02-28 22:00 | 54.06 | 51.94
2018-02-28 22:30 | 51.42 | 49.19
2018-02-28 23:00 | 50.14 | 47.87
2018-02-28 23:30 | 46.25 | 43.79
2018-03-01 | 44.25 | 41.58
2018-03-01 00:30 | 43.11 | 40.29
2018-03-01 01:00 | 41.68 | 38.78
2018-03-01 01:30 | 41.09 | 38.14
2018-03-01 02:00 | 40.74 | 37.76
2018-03-01 02:30 | 40.19 | 37.18
2018-03-01 03:00 | 39.89 | 36.86
2018-03-01 03:30 | 39.94 | 36.9
2018-03-01 04:00 | 39.7 | 36.5
2018-03-01 04:30 | 40.09 | 36.87
2018-03-01 05:00 | 41.18 | 38.02
2018-03-01 05:30 | 44 | 41.03
2018-03-01 06:00 | 46.65 | 43.83
2018-03-01 06:30 | 51.99 | 49.45
2018-03-01 07:00 | 56.99 | 54.71
2018-03-01 07:30 | 68.38 | 61.52
2018-03-01 08:00 | 73.41 | 65.83
2018-03-01 08:30 | 75.8 | 68.48
2018-03-01 09:00 | 77.69 | 70.6
2018-03-01 09:30 | 78.52 | 71.52
2018-03-01 10:00 | 79.94 | 73.06
2018-03-01 10:30 | 81.79 | 75.06
2018-03-01 11:00 | 82.51 | 75.82
2018-03-01 11:30 | 79.25 | 72.2
2018-03-01 12:00 | 75.01 | 73.68
2018-03-01 12:30 | 72.31 | 72.28
2018-03-01 13:00 | 75.3 | 75.27
2018-03-01 13:30 | 74.89 | 74.87
2018-03-01 14:00 | 73.11 | 73.08
2018-03-01 14:30 | 73.92 | 73.88
2018-03-01 15:00 | 74.3 | 74.27
2018-03-01 15:30 | 74.83 | 74.81
2018-03-01 16:00 | 75.26 | 75.24
2018-03-01 16:30 | 75.94 | 75.89
2018-03-01 17:00 | 75.02 | 74.86
2018-03-01 17:30 | 72.37 | 71.9
2018-03-01 18:00 | 71.7 | 70.92
2018-03-01 18:30 | 71.07 | 70.01
2018-03-01 19:00 | 71.39 | 70.3
2018-03-01 19:30 | 70.69 | 69.54
2018-03-01 20:00 | 68.65 | 66.76
2018-03-01 20:30 | 66.32 | 63.1
2018-03-01 21:00 | 63.19 | 59.73
2018-03-01 21:30 | 60.09 | 56.34
2018-03-01 22:00 | 56.56 | 52.43
2018-03-01 22:30 | 56.24 | 50.61
2018-03-01 23:00 | 60.62 | 48.62
2018-03-01 23:30 | 56.44 | 44.62
2018-03-02 | 54.57 | 42.08
2018-03-02 00:30 | 53.69 | 40.84
2018-03-02 01:00 | 52.7 | 39.42
2018-03-02 01:30 | 51.69 | 38.25
2018-03-02 02:00 | 50.76 | 37.32
2018-03-02 02:30 | 50.23 | 36.48
2018-03-02 03:00 | 50.15 | 36.27
2018-03-02 03:30 | 49.93 | 36.32
2018-03-02 04:00 | 49.47 | 36.11
2018-03-02 04:30 | 49.72 | 36.49
2018-03-02 05:00 | 50.49 | 37.68
2018-03-02 05:30 | 51.75 | 40.66
2018-03-02 06:00 | 47.22 | 43.89
2018-03-02 06:30 | 52.17 | 49.29
2018-03-02 07:00 | 57 | 54.4
2018-03-02 07:30 | 62.38 | 60.28
2018-03-02 08:00 | 65.04 | 64.25
2018-03-02 08:30 | 67.39 | 67.24
2018-03-02 09:00 | 69.57 | 69.53
2018-03-02 09:30 | 71.56 | 71.54
2018-03-02 10:00 | 72.51 | 72.49
2018-03-02 10:30 | 74.56 | 74.52
2018-03-02 11:00 | 74.94 | 74.89
2018-03-02 11:30 | 75.56 | 75.51
2018-03-02 12:00 | 76.41 | 76.35
2018-03-02 12:30 | 77.38 | 77.32
2018-03-02 13:00 | 77.92 | 77.86
2018-03-02 13:30 | 77.98 | 77.92
2018-03-02 14:00 | 78.1 | 78.05
2018-03-02 14:30 | 78.44 | 78.4
2018-03-02 15:00 | 77.58 | 77.56
2018-03-02 15:30 | 77.34 | 77.32
2018-03-02 16:00 | 79.11 | 79.08
2018-03-02 16:30 | 80.87 | 80.8
2018-03-02 17:00 | 78.64 | 78.43
2018-03-02 17:30 | 75.77 | 73.94
2018-03-02 18:00 | 73.06 | 70.25
2018-03-02 18:30 | 70.12 | 67.83
2018-03-02 19:00 | 70.98 | 68.8
2018-03-02 19:30 | 70.06 | 67.83
2018-03-02 20:00 | 68.04 | 65.71
2018-03-02 20:30 | 65.29 | 62.81
2018-03-02 21:00 | 63.17 | 60.56
2018-03-02 21:30 | 60.41 | 57.67
2018-03-02 22:00 | 57.62 | 54.66
2018-03-02 22:30 | 54.73 | 51.52
2018-03-02 23:00 | 53.38 | 50.05
2018-03-02 23:30 | 50.24 | 46.58
2018-03-03 | 48.05 | 44.16
2018-03-03 00:30 | 46.99 | 42.95
2018-03-03 01:00 | 45.09 | 41.02
2018-03-03 01:30 | 43.41 | 39.58
2018-03-03 02:00 | 42.73 | 38.81
2018-03-03 02:30 | 41.99 | 37.96
2018-03-03 03:00 | 41.49 | 37.38
2018-03-03 03:30 | 41.26 | 37.12
2018-03-03 04:00 | 40.91 | 36.72
2018-03-03 04:30 | 40.86 | 36.67
2018-03-03 05:00 | 40.84 | 36.66
2018-03-03 05:30 | 41.57 | 37.48
2018-03-03 06:00 | 42.28 | 38.3
2018-03-03 06:30 | 44.32 | 40.61
2018-03-03 07:00 | 45.82 | 42.32
2018-03-03 07:30 | 48.71 | 45.57
2018-03-03 08:00 | 51.82 | 48.99
2018-03-03 08:30 | 54.48 | 52.28
2018-03-03 09:00 | 55.04 | 53.96
2018-03-03 09:30 | 57.2 | 55.93
2018-03-03 10:00 | 57.69 | 56.22
2018-03-03 10:30 | 58.04 | 56.51
2018-03-03 11:00 | 58.27 | 56.55
2018-03-03 11:30 | 58.54 | 56.83
2018-03-03 12:00 | 57.69 | 56.05
2018-03-03 12:30 | 57.28 | 55.81
2018-03-03 13:00 | 56.8 | 55.4
2018-03-03 13:30 | 56.8 | 55.42
2018-03-03 14:00 | 56.66 | 55.38
2018-03-03 14:30 | 56.66 | 55.47
2018-03-03 15:00 | 57.28 | 56.15
2018-03-03 15:30 | 56.93 | 55.94
2018-03-03 16:00 | 57.41 | 56.49
2018-03-03 16:30 | 58.41 | 57.66
2018-03-03 17:00 | 58.59 | 57.89
2018-03-03 17:30 | 58.71 | 57.99
2018-03-03 18:00 | 59.4 | 58.35
2018-03-03 18:30 | 60.41 | 57.12
2018-03-03 19:00 | 60.83 | 57.6
2018-03-03 19:30 | 60.64 | 57.4
2018-03-03 20:00 | 58.74 | 55.34
2018-03-03 20:30 | 55.98 | 52.33
2018-03-03 21:00 | 54.65 | 50.86
2018-03-03 21:30 | 53.17 | 49.23
2018-03-03 22:00 | 51.6 | 47.45
2018-03-03 22:30 | 49.6 | 45.19
2018-03-03 23:00 | 47.52 | 44.11
2018-03-03 23:30 | 44.62 | 40.92
2018-03-04 | 42.84 | 38.91
2018-03-04 00:30 | 41.98 | 37.92
2018-03-04 01:00 | 40.71 | 36.49
2018-03-04 01:30 | 39.97 | 35.63
2018-03-04 02:00 | 39.53 | 35.12
2018-03-04 02:30 | 38.97 | 34.46
2018-03-04 03:00 | 38.44 | 33.85
2018-03-04 03:30 | 38.04 | 33.35
2018-03-04 04:00 | 37.9 | 33.16
2018-03-04 04:30 | 37.82 | 33.06
2018-03-04 05:00 | 37.64 | 32.86
2018-03-04 05:30 | 38.19 | 33.49
2018-03-04 06:00 | 38.22 | 33.5
2018-03-04 06:30 | 38.58 | 33.88
2018-03-04 07:00 | 39.68 | 35.19
2018-03-04 07:30 | 41.36 | 37.18
2018-03-04 08:00 | 42.36 | 38.39
2018-03-04 08:30 | 43.8 | 40.06
2018-03-04 09:00 | 44.78 | 41.22
2018-03-04 09:30 | 46.14 | 42.78
2018-03-04 10:00 | 47.82 | 44.68
2018-03-04 10:30 | 48.8 | 45.78
2018-03-04 11:00 | 49.71 | 46.81
2018-03-04 11:30 | 50.3 | 47.45
2018-03-04 12:00 | 50.63 | 47.81
2018-03-04 12:30 | 52.36 | 49.6
2018-03-04 13:00 | 51.77 | 49
2018-03-04 13:30 | 51.77 | 49.02
2018-03-04 14:00 | 52.69 | 49.99
2018-03-04 14:30 | 53.33 | 50.67
2018-03-04 15:00 | 49.74 | 48.62
2018-03-04 15:30 | 51.42 | 50.64
2018-03-04 16:00 | 54.2 | 53.47
2018-03-04 16:30 | 56.24 | 55.53
2018-03-04 17:00 | 56.89 | 56.21
2018-03-04 17:30 | 57.34 | 56.67
2018-03-04 18:00 | 59.47 | 58.83
2018-03-04 18:30 | 59.97 | 59.33
2018-03-04 19:00 | 60.88 | 60.25
2018-03-04 19:30 | 60.65 | 60.15
2018-03-04 20:00 | 58 | 57.59
2018-03-04 20:30 | 56.04 | 55.68
2018-03-04 21:00 | 53.92 | 53.63
2018-03-04 21:30 | 51.9 | 51.65
2018-03-04 22:00 | 49.94 | 49.73
2018-03-04 22:30 | 46.98 | 46.83
2018-03-04 23:00 | 45.83 | 45.73
2018-03-04 23:30 | 42.76 | 42.68
2018-03-05 | 40.99 | 40.92
2018-03-05 00:30 | 40.06 | 39.99
2018-03-05 01:00 | 39.09 | 39.02
2018-03-05 01:30 | 38.73 | 38.67
2018-03-05 02:00 | 38.71 | 38.65
2018-03-05 02:30 | 38.63 | 38.21
2018-03-05 03:00 | 38.68 | 37.43
2018-03-05 03:30 | 39.22 | 38
2018-03-05 04:00 | 38.52 | 37.26
2018-03-05 04:30 | 39.79 | 38.6
2018-03-05 05:00 | 41.15 | 40.03
2018-03-05 05:30 | 43.83 | 42.82
2018-03-05 06:00 | 46.89 | 46
2018-03-05 06:30 | 53.58 | 52.76
2018-03-05 07:00 | 59 | 58.25
2018-03-05 07:30 | 66.41 | 65.33
2018-03-05 08:00 | 71.21 | 70.38
2018-03-05 08:30 | 73 | 72.29
2018-03-05 09:00 | 75.51 | 74.87
2018-03-05 09:30 | 76.15 | 75.52
2018-03-05 10:00 | 75.55 | 74.92
2018-03-05 10:30 | 75.16 | 74.53
2018-03-05 11:00 | 76.33 | 75.72
2018-03-05 11:30 | 76.22 | 75.62
2018-03-05 12:00 | 76.4 | 75.82
2018-03-05 12:30 | 77.59 | 77.02
2018-03-05 13:00 | 77.65 | 77.07
2018-03-05 13:30 | 78.68 | 78.11
2018-03-05 14:00 | 78.64 | 78.08
2018-03-05 14:30 | 76.65 | 76.06
2018-03-05 15:00 | 76.02 | 75.43
2018-03-05 15:30 | 75.37 | 74.75
2018-03-05 16:00 | 75.42 | 74.78
2018-03-05 16:30 | 75.52 | 74.85
2018-03-05 17:00 | 74.69 | 73.97
2018-03-05 17:30 | 71.99 | 71.16
2018-03-05 18:00 | 69.13 | 68.14
2018-03-05 18:30 | 68.46 | 67.17
2018-03-05 19:00 | 69.57 | 68.36
2018-03-05 19:30 | 68.56 | 67.21
2018-03-05 20:00 | 65.86 | 64.12
2018-03-05 20:30 | 63.3 | 61.24
2018-03-05 21:00 | 60.58 | 58.53
2018-03-05 21:30 | 56.27 | 55.4
2018-03-05 22:00 | 53.29 | 52.33
2018-03-05 22:30 | 49.96 | 48.89
2018-03-05 23:00 | 49.04 | 47.94
2018-03-05 23:30 | 45.22 | 44.11
2018-03-06 | 42.87 | 41.7
2018-03-06 00:30 | 42.03 | 40.83
2018-03-06 01:00 | 41.03 | 39.79
2018-03-06 01:30 | 40.12 | 38.84
2018-03-06 02:00 | 39.49 | 38.17
2018-03-06 02:30 | 38.7 | 37.32
2018-03-06 03:00 | 37.89 | 36.52
2018-03-06 03:30 | 37.26 | 35.99
2018-03-06 04:00 | 37.18 | 35.89
2018-03-06 04:30 | 37.79 | 36.55
2018-03-06 05:00 | 39.04 | 37.86
2018-03-06 05:30 | 41.64 | 40.57
2018-03-06 06:00 | 44.92 | 43.98
2018-03-06 06:30 | 50.59 | 49.79
2018-03-06 07:00 | 56.25 | 55.53
2018-03-06 07:30 | 64.52 | 63.54
2018-03-06 08:00 | 68.19 | 67.24
2018-03-06 08:30 | 70.73 | 69.39
2018-03-06 09:00 | 73.82 | 72.12
2018-03-06 09:30 | 73.61 | 72.24
2018-03-06 10:00 | 72.19 | 71.84
2018-03-06 10:30 | 73.02 | 72.67
2018-03-06 11:00 | 71.73 | 71.36
2018-03-06 11:30 | 70.58 | 70.21
2018-03-06 12:00 | 70.87 | 70.51
2018-03-06 12:30 | 71.89 | 71.53
2018-03-06 13:00 | 72.19 | 71.83
2018-03-06 13:30 | 72.98 | 72.63
2018-03-06 14:00 | 73.14 | 72.78
2018-03-06 14:30 | 74.09 | 73.74
2018-03-06 15:00 | 73.65 | 73.3
2018-03-06 15:30 | 73.36 | 73.02
2018-03-06 16:00 | 73.33 | 73.01
2018-03-06 16:30 | 73.24 | 72.93
2018-03-06 17:00 | 72.73 | 72.36
2018-03-06 17:30 | 70.66 | 70.1
2018-03-06 18:00 | 68.87 | 67.88
2018-03-06 18:30 | 67.57 | 66.13
2018-03-06 19:00 | 68.75 | 67.39
2018-03-06 19:30 | 68.12 | 66.64
2018-03-06 20:00 | 66.09 | 64.37
2018-03-06 20:30 | 63.47 | 61.35
2018-03-06 21:00 | 59.92 | 58.75
2018-03-06 21:30 | 56.83 | 55.97
2018-03-06 22:00 | 54.12 | 53.19
2018-03-06 22:30 | 51.17 | 50.24
2018-03-06 23:00 | 50.03 | 49.09
2018-03-06 23:30 | 46.41 | 45.37
2018-03-07 | 44.55 | 43.45
2018-03-07 00:30 | 43.33 | 42.18
2018-03-07 01:00 | 42.15 | 40.94
2018-03-07 01:30 | 41.15 | 39.9
2018-03-07 02:00 | 41.02 | 39.77
2018-03-07 02:30 | 40.29 | 38.99
2018-03-07 03:00 | 39.84 | 38.52
2018-03-07 03:30 | 39.63 | 38.29
2018-03-07 04:00 | 39.44 | 38.1
2018-03-07 04:30 | 39.97 | 38.66
2018-03-07 05:00 | 41.02 | 39.76
2018-03-07 05:30 | 43.36 | 42.2
2018-03-07 06:00 | 46.25 | 45.23
2018-03-07 06:30 | 51.98 | 51.15
2018-03-07 07:00 | 57.66 | 56.96
2018-03-07 07:30 | 65.23 | 64.58
2018-03-07 08:00 | 68.28 | 67.47
2018-03-07 08:30 | 69.98 | 69.21
2018-03-07 09:00 | 71.93 | 71.23
2018-03-07 09:30 | 72.82 | 72.14
2018-03-07 10:00 | 72.41 | 71.74
2018-03-07 10:30 | 72.7 | 72.04
2018-03-07 11:00 | 72.26 | 71.61
2018-03-07 11:30 | 74.7 | 74.08
2018-03-07 12:00 | 75.22 | 74.61
2018-03-07 12:30 | 76.17 | 75.56
2018-03-07 13:00 | 71.84 | 71.18
2018-03-07 13:30 | 72.93 | 72.27
2018-03-07 14:00 | 72.72 | 72.05
2018-03-07 14:30 | 71.35 | 70.68
2018-03-07 15:00 | 74.14 | 73.49
2018-03-07 15:30 | 73.14 | 72.44
2018-03-07 16:00 | 72.06 | 71.31
2018-03-07 16:30 | 69.98 | 69.13
2018-03-07 17:00 | 67.86 | 66.94
2018-03-07 17:30 | 65.12 | 64.02
2018-03-07 18:00 | 63.81 | 62.26
2018-03-07 18:30 | 63.24 | 61.26
2018-03-07 19:00 | 64.16 | 62.29
2018-03-07 19:30 | 63.25 | 61.29
2018-03-07 20:00 | 61.94 | 59.82
2018-03-07 20:30 | 59.68 | 57.13
2018-03-07 21:00 | 56.74 | 54.93
2018-03-07 21:30 | 54.9 | 52.96
2018-03-07 22:00 | 52.72 | 50.49
2018-03-07 22:30 | 48.71 | 47.76
2018-03-07 23:00 | 47.98 | 47.01
2018-03-07 23:30 | 44.82 | 43.74
2018-03-08 | 42.88 | 41.73
2018-03-08 00:30 | 42.02 | 40.83
2018-03-08 01:00 | 40.68 | 39.42
2018-03-08 01:30 | 39.69 | 38.39
2018-03-08 02:00 | 39.26 | 37.95
2018-03-08 02:30 | 38.95 | 37.6
2018-03-08 03:00 | 38.45 | 37.07
2018-03-08 03:30 | 38.23 | 36.86
2018-03-08 04:00 | 37.96 | 36.73
2018-03-08 04:30 | 38.46 | 37.26
2018-03-08 05:00 | 32.04 | 30.65
2018-03-08 05:30 | 42.02 | 40.97
2018-03-08 06:00 | 44.97 | 44.04
2018-03-08 06:30 | 51.13 | 50.34
2018-03-08 07:00 | 56.99 | 56.29
2018-03-08 07:30 | 64.33 | 63.34
2018-03-08 08:00 | 67.12 | 65.61
2018-03-08 08:30 | 69.06 | 67.04
2018-03-08 09:00 | 71.49 | 68.85
2018-03-08 09:30 | 70.94 | 68.93
2018-03-08 10:00 | 70.78 | 68.83
2018-03-08 10:30 | 71.31 | 69.36
2018-03-08 11:00 | 73.01 | 71.1
2018-03-08 11:30 | 72.96 | 71.03
2018-03-08 12:00 | 71.94 | 69.96
2018-03-08 12:30 | 72.61 | 70.66
2018-03-08 13:00 | 75.15 | 73.29
2018-03-08 13:30 | 74.45 | 72.58
2018-03-08 14:00 | 73.36 | 71.47
2018-03-08 14:30 | 70.59 | 70.36
2018-03-08 15:00 | 69.78 | 69.69
2018-03-08 15:30 | 67.38 | 67.17
2018-03-08 16:00 | 66.42 | 66.11
2018-03-08 16:30 | 66.54 | 65.95
2018-03-08 17:00 | 63.42 | 62.32
2018-03-08 17:30 | 62.3 | 59.44
2018-03-08 18:00 | 62.58 | 59.13
2018-03-08 18:30 | 62.34 | 58.82
2018-03-08 19:00 | 62.89 | 59.61
2018-03-08 19:30 | 61.79 | 58.5
2018-03-08 20:00 | 60.81 | 57.43
2018-03-08 20:30 | 58.61 | 55.03
2018-03-08 21:00 | 56.81 | 53.06
2018-03-08 21:30 | 53.66 | 50.45
2018-03-08 22:00 | 50.52 | 47.24
2018-03-08 22:30 | 48.37 | 44.88
2018-03-08 23:00 | 47.58 | 44
2018-03-08 23:30 | 44.73 | 40.84
2018-03-09 | 43.1 | 39.02
2018-03-09 00:30 | 42.53 | 38.34
2018-03-09 01:00 | 41.36 | 37
2018-03-09 01:30 | 40.67 | 36.22
2018-03-09 02:00 | 40.55 | 36.07
2018-03-09 02:30 | 40.19 | 35.64
2018-03-09 03:00 | 39.89 | 35.28
2018-03-09 03:30 | 39.91 | 35.29
2018-03-09 04:00 | 40.05 | 35.45
2018-03-09 04:30 | 40.5 | 36.13
2018-03-09 05:00 | 41.09 | 37.02
2018-03-09 05:30 | 43.56 | 39.82
2018-03-09 06:00 | 46.78 | 43.44
2018-03-09 06:30 | 51.58 | 48.71
2018-03-09 07:00 | 56.19 | 53.54
2018-03-09 07:30 | 51.69 | 48.86
2018-03-09 08:00 | 50.41 | 47.56
2018-03-09 08:30 | 49.06 | 47.45
2018-03-09 09:00 | 50.86 | 49.71
2018-03-09 09:30 | 49.74 | 48.54
2018-03-09 10:00 | 49.61 | 48.24
2018-03-09 10:30 | 51.27 | 49.83
2018-03-09 11:00 | 51.09 | 49.83
2018-03-09 11:30 | 62.98 | 61.67
2018-03-09 12:00 | 64.13 | 62.69
2018-03-09 12:30 | 68.38 | 67.11
2018-03-09 13:00 | 65.26 | 64.11
2018-03-09 13:30 | 65.5 | 64.38
2018-03-09 14:00 | 63.53 | 62.55
2018-03-09 14:30 | 61.74 | 60.8
2018-03-09 15:00 | 63.34 | 62.53
2018-03-09 15:30 | 62.93 | 62.31
2018-03-09 16:00 | 61.55 | 61.11
2018-03-09 16:30 | 62.03 | 61.77
2018-03-09 17:00 | 60.63 | 60.49
2018-03-09 17:30 | 57.46 | 57.41
2018-03-09 18:00 | 56.24 | 56.21
2018-03-09 18:30 | 55.14 | 55.06
2018-03-09 19:00 | 56.2 | 56.1
2018-03-09 19:30 | 54.93 | 54.85
2018-03-09 20:00 | 52.94 | 52.87
2018-03-09 20:30 | 50.68 | 50.63
2018-03-09 21:00 | 48.75 | 48.71
2018-03-09 21:30 | 46.74 | 46.71
2018-03-09 22:00 | 44.89 | 44.87
2018-03-09 22:30 | 42.84 | 42.81
2018-03-09 23:00 | 42.41 | 42.34
2018-03-09 23:30 | 39.44 | 39.32
2018-03-10 | 37.75 | 37.59
2018-03-10 00:30 | 36.48 | 36.24
2018-03-10 01:00 | 35.06 | 34.76
2018-03-10 01:30 | 33.82 | 33.79
2018-03-10 02:00 | 33.53 | 33.51
2018-03-10 02:30 | 33.16 | 33.13
2018-03-10 03:00 | 32.49 | 32.46
2018-03-10 03:30 | 32.22 | 32.09
2018-03-10 04:00 | 32.4 | 32.27
2018-03-10 04:30 | 32.59 | 32.44
2018-03-10 05:00 | 32.59 | 32.43
2018-03-10 05:30 | 33.62 | 33.48
2018-03-10 06:00 | 34.8 | 34.6
2018-03-10 06:30 | 36.98 | 36.69
2018-03-10 07:00 | 38.85 | 38.5
2018-03-10 07:30 | 42.01 | 41.47
2018-03-10 08:00 | 44.14 | 43.38
2018-03-10 08:30 | 47.22 | 46.3
2018-03-10 09:00 | 48.07 | 46.07
2018-03-10 09:30 | 51.65 | 47.8
2018-03-10 10:00 | 52.05 | 48.23
2018-03-10 10:30 | 51.55 | 47.74
2018-03-10 11:00 | 49.85 | 45.92
2018-03-10 11:30 | 47.73 | 43.62
2018-03-10 12:00 | 47.66 | 43.55
2018-03-10 12:30 | 47.81 | 43.66
2018-03-10 13:00 | 47.96 | 43.82
2018-03-10 13:30 | 49.39 | 45.38
2018-03-10 14:00 | 48.17 | 44.02
2018-03-10 14:30 | 50.29 | 46.28
2018-03-10 15:00 | 49.32 | 45.19
2018-03-10 15:30 | 49.87 | 45.73
2018-03-10 16:00 | 49.85 | 45.67
2018-03-10 16:30 | 50.76 | 46.64
2018-03-10 17:00 | 50.33 | 46.14
2018-03-10 17:30 | 50.52 | 46.35
2018-03-10 18:00 | 52.18 | 48.15
2018-03-10 18:30 | 51.89 | 47.82
2018-03-10 19:00 | 52.19 | 48.18
2018-03-10 19:30 | 51.23 | 47.11
2018-03-10 20:00 | 49.95 | 45.68
2018-03-10 20:30 | 48.49 | 44.04
2018-03-10 21:00 | 47.57 | 42.98
2018-03-10 21:30 | 45.38 | 41.81
2018-03-10 22:00 | 44.46 | 40.79
2018-03-10 22:30 | 43.25 | 39.43
2018-03-10 23:00 | 43.15 | 39.28
2018-03-10 23:30 | 41.2 | 37.1
2018-03-11 | 39.9 | 35.6
2018-03-11 00:30 | 39.28 | 34.86
2018-03-11 01:00 | 37.9 | 33.27
2018-03-11 01:30 | 37.18 | 32.43
2018-03-11 02:00 | 36.88 | 32.07
2018-03-11 02:30 | 36.57 | 31.7
2018-03-11 03:00 | 36.16 | 31.21
2018-03-11 03:30 | 35.41 | 30.66
2018-03-11 04:00 | 35.1 | 30.34
2018-03-11 04:30 | 35.14 | 30.4
2018-03-11 05:00 | 35.07 | 30.31
2018-03-11 05:30 | 35.64 | 30.95
2018-03-11 06:00 | 35.84 | 31.19
2018-03-11 06:30 | 36.67 | 32.14
2018-03-11 07:00 | 36.92 | 32.43
2018-03-11 07:30 | 38.4 | 34.16
2018-03-11 08:00 | 39.32 | 35.26
2018-03-11 08:30 | 40.74 | 36.92
2018-03-11 09:00 | 41.79 | 38.16
2018-03-11 09:30 | 40.93 | 37.29
2018-03-11 10:00 | 40.31 | 36.65
2018-03-11 10:30 | 41.05 | 37.31
2018-03-11 11:00 | 40.85 | 37.01
2018-03-11 11:30 | 41.2 | 37.43
2018-03-11 12:00 | 41.53 | 37.83
2018-03-11 12:30 | 42.01 | 38.33
2018-03-11 13:00 | 41.74 | 38.04
2018-03-11 13:30 | 42.16 | 38.52
2018-03-11 14:00 | 42.67 | 39.06
2018-03-11 14:30 | 42.3 | 38.63
2018-03-11 15:00 | 43.01 | 39.4
2018-03-11 15:30 | 44.31 | 40.81
2018-03-11 16:00 | 45.04 | 41.58
2018-03-11 16:30 | 46.76 | 43.43
2018-03-11 17:00 | 47.5 | 44.22
2018-03-11 17:30 | 49.07 | 45.92
2018-03-11 18:00 | 51.41 | 48.42
2018-03-11 18:30 | 50.2 | 49.59
2018-03-11 19:00 | 51.85 | 51.71
2018-03-11 19:30 | 51.24 | 51.1
2018-03-11 20:00 | 49.28 | 49.17
2018-03-11 20:30 | 46.8 | 46.71
2018-03-11 21:00 | 45.57 | 45.5
2018-03-11 21:30 | 43.83 | 43.76
2018-03-11 22:00 | 41.78 | 41.73
2018-03-11 22:30 | 39.91 | 39.87
2018-03-11 23:00 | 39.24 | 39.21
2018-03-11 23:30 | 35.95 | 35.93
2018-03-12 | 34.3 | 34.28
2018-03-12 00:30 | 33.79 | 33.74
2018-03-12 01:00 | 32.52 | 32.4
2018-03-12 01:30 | 32.13 | 32.01
2018-03-12 02:00 | 31.64 | 31.53
2018-03-12 02:30 | 31.32 | 31.22
2018-03-12 03:00 | 31.15 | 31.03
2018-03-12 03:30 | 31.66 | 30.21
2018-03-12 04:00 | 31.99 | 30.58
2018-03-12 04:30 | 32.74 | 31.38
2018-03-12 05:00 | 34.02 | 32.73
2018-03-12 05:30 | 36.34 | 35.16
2018-03-12 06:00 | 39.21 | 38.17
2018-03-12 06:30 | 44.44 | 43.52
2018-03-12 07:00 | 49.76 | 48.92
2018-03-12 07:30 | 55.57 | 54.62
2018-03-12 08:00 | 58.61 | 57.2
2018-03-12 08:30 | 59.24 | 58.42
2018-03-12 09:00 | 59.49 | 58.92
2018-03-12 09:30 | 59.38 | 58.93
2018-03-12 10:00 | 59.28 | 58.88
2018-03-12 10:30 | 59.39 | 58.85
2018-03-12 11:00 | 59.75 | 59.11
2018-03-12 11:30 | 59.66 | 59.32
2018-03-12 12:00 | 60.88 | 59.56
2018-03-12 12:30 | 63.82 | 60.37
2018-03-12 13:00 | 62.84 | 59.2
2018-03-12 13:30 | 62.83 | 59.55
2018-03-12 14:00 | 63.12 | 59.97
2018-03-12 14:30 | 62.18 | 60.33
2018-03-12 15:00 | 60.44 | 60.11
2018-03-12 15:30 | 60.05 | 59.69
2018-03-12 16:00 | 61.08 | 60.67
2018-03-12 16:30 | 61.75 | 61.18
2018-03-12 17:00 | 61.38 | 60.46
2018-03-12 17:30 | 59.74 | 58.22
2018-03-12 18:00 | 59.07 | 56.93
2018-03-12 18:30 | 59.48 | 56.9
2018-03-12 19:00 | 60.3 | 58.78
2018-03-12 19:30 | 59.31 | 57.95
2018-03-12 20:00 | 57.9 | 56.46
2018-03-12 20:30 | 55.79 | 54.06
2018-03-12 21:00 | 53.33 | 51.22
2018-03-12 21:30 | 51.6 | 49.16
2018-03-12 22:00 | 48.27 | 46.38
2018-03-12 22:30 | 44.65 | 44.02
2018-03-12 23:00 | 43.89 | 43.26
2018-03-12 23:30 | 40.59 | 39.91
2018-03-13 | 38.76 | 38.05
2018-03-13 00:30 | 37.93 | 37.22
2018-03-13 01:00 | 36.49 | 35.76
2018-03-13 01:30 | 35.89 | 35.14
2018-03-13 02:00 | 35.29 | 34.54
2018-03-13 02:30 | 34.64 | 33.89
2018-03-13 03:00 | 34.03 | 33.25
2018-03-13 03:30 | 33.99 | 33.12
2018-03-13 04:00 | 33.89 | 33.02
2018-03-13 04:30 | 34.57 | 33.71
2018-03-13 05:00 | 35.3 | 34.45
2018-03-13 05:30 | 37.53 | 36.72
2018-03-13 06:00 | 42.97 | 40.11
2018-03-13 06:30 | 51.84 | 45.25
2018-03-13 07:00 | 56.23 | 50.3
2018-03-13 07:30 | 61.94 | 56.75
2018-03-13 08:00 | 64.4 | 59.47
2018-03-13 08:30 | 67.09 | 62.31
2018-03-13 09:00 | 67.26 | 62.45
2018-03-13 09:30 | 66.95 | 62.08
2018-03-13 10:00 | 66.89 | 62.05
2018-03-13 10:30 | 65.77 | 60.8
2018-03-13 11:00 | 65.46 | 60.43
2018-03-13 11:30 | 66.82 | 61.91
2018-03-13 12:00 | 65.49 | 61.11
2018-03-13 12:30 | 66.79 | 62.49
2018-03-13 13:00 | 66.99 | 62.74
2018-03-13 13:30 | 67.58 | 63.35
2018-03-13 14:00 | 68.23 | 64.07
2018-03-13 14:30 | 67.93 | 63.73
2018-03-13 15:00 | 67.9 | 63.72
2018-03-13 15:30 | 67.46 | 63.28
2018-03-13 16:00 | 67.99 | 63.91
2018-03-13 16:30 | 67.33 | 63.3
2018-03-13 17:00 | 66.24 | 62.23
2018-03-13 17:30 | 63.91 | 59.83
2018-03-13 18:00 | 61.75 | 58.31
2018-03-13 18:30 | 60.49 | 57.97
2018-03-13 19:00 | 61.95 | 59.7
2018-03-13 19:30 | 61.39 | 59.01
2018-03-13 20:00 | 59.42 | 56.72
2018-03-13 20:30 | 55.43 | 53.73
2018-03-13 21:00 | 52.77 | 51.66
2018-03-13 21:30 | 50.68 | 49.35
2018-03-13 22:00 | 47.95 | 46.82
2018-03-13 22:30 | 44.49 | 43.87
2018-03-13 23:00 | 43.51 | 42.89
2018-03-13 23:30 | 40.19 | 39.52
2018-03-14 | 38.52 | 37.82
2018-03-14 00:30 | 37.51 | 36.81
2018-03-14 01:00 | 36.61 | 35.89
2018-03-14 01:30 | 36.03 | 35.31
2018-03-14 02:00 | 35.15 | 34.41
2018-03-14 02:30 | 34.28 | 33.44
2018-03-14 03:00 | 34.03 | 33.16
2018-03-14 03:30 | 33.8 | 32.93
2018-03-14 04:00 | 34.01 | 33.14
2018-03-14 04:30 | 34.63 | 33.77
2018-03-14 05:00 | 35.73 | 34.9
2018-03-14 05:30 | 38.19 | 37.39
2018-03-14 06:00 | 42.49 | 40.3
2018-03-14 06:30 | 52.36 | 45.87
2018-03-14 07:00 | 56.75 | 50.92
2018-03-14 07:30 | 61.69 | 56.45
2018-03-14 08:00 | 62.98 | 59.52
2018-03-14 08:30 | 61.93 | 61.03
2018-03-14 09:00 | 62.47 | 61.32
2018-03-14 09:30 | 62.37 | 61.13
2018-03-14 10:00 | 62.29 | 60.97
2018-03-14 10:30 | 62.66 | 61.19
2018-03-14 11:00 | 62.43 | 60.63
2018-03-14 11:30 | 62.46 | 60.48
2018-03-14 12:00 | 64.41 | 62.35
2018-03-14 12:30 | 64.69 | 62.76
2018-03-14 13:00 | 64.06 | 62.24
2018-03-14 13:30 | 64.69 | 62.85
2018-03-14 14:00 | 65.08 | 63.21
2018-03-14 14:30 | 65.63 | 63.72
2018-03-14 15:00 | 65.51 | 63.7
2018-03-14 15:30 | 65.49 | 63.87
2018-03-14 16:00 | 65.64 | 64.33
2018-03-14 16:30 | 64.76 | 63.87
2018-03-14 17:00 | 63.57 | 63
2018-03-14 17:30 | 60.69 | 60.46
2018-03-14 18:00 | 58.49 | 58.43
2018-03-14 18:30 | 58.73 | 58.24
2018-03-14 19:00 | 61.33 | 60.45
2018-03-14 19:30 | 59.7 | 58.99
2018-03-14 20:00 | 57.29 | 56.66
2018-03-14 20:30 | 54.31 | 53.79
2018-03-14 21:00 | 52 | 51.6
2018-03-14 21:30 | 49.3 | 49
2018-03-14 22:00 | 48.05 | 45.94
2018-03-14 22:30 | 46.66 | 43.06
2018-03-14 23:00 | 45.81 | 42.1
2018-03-14 23:30 | 42.67 | 38.57
2018-03-15 | 41.04 | 36.71
2018-03-15 00:30 | 40.26 | 35.78
2018-03-15 01:00 | 38.92 | 34.31
2018-03-15 01:30 | 37.92 | 33.44
2018-03-15 02:00 | 37.59 | 33.04
2018-03-15 02:30 | 37.05 | 32.39
2018-03-15 03:00 | 36.73 | 32
2018-03-15 03:30 | 36.91 | 32.21
2018-03-15 04:00 | 36.89 | 32.19
2018-03-15 04:30 | 37.02 | 32.33
2018-03-15 05:00 | 38.04 | 33.51
2018-03-15 05:30 | 39.84 | 35.61
2018-03-15 06:00 | 42 | 38.1
2018-03-15 06:30 | 46.23 | 42.88
2018-03-15 07:00 | 50.47 | 47.38
2018-03-15 07:30 | 56.13 | 53.44
2018-03-15 08:00 | 58.55 | 56.02
2018-03-15 08:30 | 59.91 | 57.51
2018-03-15 09:00 | 61.42 | 59.03
2018-03-15 09:30 | 61.74 | 59.42
2018-03-15 10:00 | 61.72 | 59.42
2018-03-15 10:30 | 62.41 | 60.18
2018-03-15 11:00 | 62.01 | 60.01
2018-03-15 11:30 | 62.82 | 61.19
2018-03-15 12:00 | 63.22 | 61.58
2018-03-15 12:30 | 63.89 | 62.3
2018-03-15 13:00 | 63.84 | 62.26
2018-03-15 13:30 | 64.73 | 63.07
2018-03-15 14:00 | 65.14 | 63.52
2018-03-15 14:30 | 64.99 | 63.46
2018-03-15 15:00 | 65.21 | 63.7
2018-03-15 15:30 | 65.14 | 63.82
2018-03-15 16:00 | 65.73 | 64.62
2018-03-15 16:30 | 65.06 | 64.31
2018-03-15 17:00 | 63.97 | 63.44
2018-03-15 17:30 | 61.96 | 61.45
2018-03-15 18:00 | 61.55 | 61.06
2018-03-15 18:30 | 61.52 | 61.02
2018-03-15 19:00 | 63.37 | 62.85
2018-03-15 19:30 | 62.38 | 61.86
2018-03-15 20:00 | 60.47 | 59.94
2018-03-15 20:30 | 57.93 | 57.39
2018-03-15 21:00 | 55.53 | 54.97
2018-03-15 21:30 | 52.26 | 51.67
2018-03-15 22:00 | 49.17 | 48.48
2018-03-15 22:30 | 46.56 | 45.85
2018-03-15 23:00 | 44.97 | 44.25
2018-03-15 23:30 | 41.03 | 40.74
2018-03-16 | 38.72 | 38.64
2018-03-16 00:30 | 37.41 | 37.34
2018-03-16 01:00 | 35.85 | 35.79
2018-03-16 01:30 | 35.2 | 35.14
2018-03-16 02:00 | 35 | 34.95
2018-03-16 02:30 | 34.24 | 34.19
2018-03-16 03:00 | 33.84 | 33.61
2018-03-16 03:30 | 33.9 | 33.66
2018-03-16 04:00 | 33.95 | 33.72
2018-03-16 04:30 | 34.33 | 34.09
2018-03-16 05:00 | 35.25 | 34.95
2018-03-16 05:30 | 38.1 | 37.73
2018-03-16 06:00 | 40.88 | 40.33
2018-03-16 06:30 | 45.96 | 45.14
2018-03-16 07:00 | 50.86 | 50.17
2018-03-16 07:30 | 56.94 | 56.18
2018-03-16 08:00 | 62.04 | 58.81
2018-03-16 08:30 | 64.46 | 61.5
2018-03-16 09:00 | 65.37 | 62.58
2018-03-16 09:30 | 65.86 | 63.18
2018-03-16 10:00 | 66.15 | 63.52
2018-03-16 10:30 | 67.62 | 65.08
2018-03-16 11:00 | 67.72 | 65.23
2018-03-16 11:30 | 67.85 | 65.38
2018-03-16 12:00 | 67.92 | 65.46
2018-03-16 12:30 | 68.02 | 65.57
2018-03-16 13:00 | 67.7 | 65.23
2018-03-16 13:30 | 67.63 | 65.14
2018-03-16 14:00 | 68.06 | 65.58
2018-03-16 14:30 | 67.95 | 65.43
2018-03-16 15:00 | 67.57 | 64.99
2018-03-16 15:30 | 66.9 | 64.23
2018-03-16 16:00 | 67.48 | 64.78
2018-03-16 16:30 | 68.14 | 65.4
2018-03-16 17:00 | 67.27 | 64.41
2018-03-16 17:30 | 65.22 | 62.13
2018-03-16 18:00 | 63.19 | 59.98
2018-03-16 18:30 | 62.21 | 58.98
2018-03-16 19:00 | 63.25 | 60.12
2018-03-16 19:30 | 62.34 | 59.14
2018-03-16 20:00 | 60.4 | 57.04
2018-03-16 20:30 | 57.55 | 54.26
2018-03-16 21:00 | 52.21 | 51.75
2018-03-16 21:30 | 50.11 | 49.73
2018-03-16 22:00 | 47.76 | 47.49
2018-03-16 22:30 | 45.32 | 45.13
2018-03-16 23:00 | 44.55 | 44.43
2018-03-16 23:30 | 40.6 | 40.51
2018-03-17 | 38.35 | 38.28
2018-03-17 00:30 | 37.24 | 37.18
2018-03-17 01:00 | 35.64 | 35.6
2018-03-17 01:30 | 34.88 | 34.83
2018-03-17 02:00 | 34.14 | 34.11
2018-03-17 02:30 | 33.46 | 33.4
2018-03-17 03:00 | 32.94 | 32.78
2018-03-17 03:30 | 32.63 | 32.47
2018-03-17 04:00 | 32.21 | 32.08
2018-03-17 04:30 | 32.4 | 32.26
2018-03-17 05:00 | 32.52 | 32.38
2018-03-17 05:30 | 33.94 | 33.77
2018-03-17 06:00 | 35.08 | 34.85
2018-03-17 06:30 | 36.73 | 36.46
2018-03-17 07:00 | 38.68 | 38.27
2018-03-17 07:30 | 41.32 | 40.66
2018-03-17 08:00 | 44.36 | 43.51
2018-03-17 08:30 | 47.06 | 46.46
2018-03-17 09:00 | 48.64 | 47.79
2018-03-17 09:30 | 49.23 | 48.22
2018-03-17 10:00 | 49.46 | 48.32
2018-03-17 10:30 | 49.64 | 48.32
2018-03-17 11:00 | 49.29 | 47.93
2018-03-17 11:30 | 48.53 | 47.39
2018-03-17 12:00 | 47.58 | 47.18
2018-03-17 12:30 | 47.25 | 46.69
2018-03-17 13:00 | 43.12 | 42.53
2018-03-17 13:30 | 46.05 | 45.32
2018-03-17 14:00 | 46.3 | 45.52
2018-03-17 14:30 | 46.27 | 45.36
2018-03-17 15:00 | 47.08 | 46.15
2018-03-17 15:30 | 50.47 | 46.87
2018-03-17 16:00 | 51.6 | 47.82
2018-03-17 16:30 | 53.1 | 49.4
2018-03-17 17:00 | 53.55 | 49.86
2018-03-17 17:30 | 54.51 | 50.88
2018-03-17 18:00 | 55.18 | 51.56
2018-03-17 18:30 | 55.4 | 51.78
2018-03-17 19:00 | 56.64 | 53.17
2018-03-17 19:30 | 56.17 | 52.65
2018-03-17 20:00 | 54.94 | 51.29
2018-03-17 20:30 | 52.97 | 49.11
2018-03-17 21:00 | 51.64 | 47.63
2018-03-17 21:30 | 48.56 | 45.79
2018-03-17 22:00 | 45.09 | 44.14
2018-03-17 22:30 | 43.5 | 42.5
2018-03-17 23:00 | 42.68 | 41.63
2018-03-17 23:30 | 39.71 | 38.55
2018-03-18 | 38.25 | 37.03
2018-03-18 00:30 | 37.35 | 36.08
2018-03-18 01:00 | 36.23 | 34.9
2018-03-18 01:30 | 35.59 | 34.24
2018-03-18 02:00 | 35.06 | 33.68
2018-03-18 02:30 | 34.7 | 33.3
2018-03-18 03:00 | 34.18 | 32.74
2018-03-18 03:30 | 33.89 | 32.52
2018-03-18 04:00 | 33.34 | 32.04
2018-03-18 04:30 | 33.51 | 32.23
2018-03-18 05:00 | 33.55 | 32.27
2018-03-18 05:30 | 33.98 | 32.71
2018-03-18 06:00 | 34.17 | 32.9
2018-03-18 06:30 | 35.2 | 33.97
2018-03-18 07:00 | 36.11 | 34.92
2018-03-18 07:30 | 37.36 | 36.25
2018-03-18 08:00 | 39.33 | 38.33
2018-03-18 08:30 | 41.22 | 40.27
2018-03-18 09:00 | 42.95 | 41.95
2018-03-18 09:30 | 44.01 | 43.11
2018-03-18 10:00 | 44.86 | 44
2018-03-18 10:30 | 45.56 | 44.72
2018-03-18 11:00 | 45.94 | 45.09
2018-03-18 11:30 | 46.1 | 45.2
2018-03-18 12:00 | 46.24 | 45.34
2018-03-18 12:30 | 47.42 | 46.55
2018-03-18 13:00 | 47.22 | 46.35
2018-03-18 13:30 | 47.43 | 46.57
2018-03-18 14:00 | 48.06 | 47.2
2018-03-18 14:30 | 47.84 | 47.04
2018-03-18 15:00 | 48.96 | 48.18
2018-03-18 15:30 | 50.01 | 49.26
2018-03-18 16:00 | 51.57 | 50.42
2018-03-18 16:30 | 53.07 | 51.87
2018-03-18 17:00 | 53.78 | 52.59
2018-03-18 17:30 | 54.7 | 53.49
2018-03-18 18:00 | 56.58 | 55.41
2018-03-18 18:30 | 57.42 | 56.27
2018-03-18 19:00 | 58.99 | 57.93
2018-03-18 19:30 | 58.2 | 57.11
2018-03-18 20:00 | 56.18 | 55.04
2018-03-18 20:30 | 53.69 | 52.35
2018-03-18 21:00 | 51.84 | 50.27
2018-03-18 21:30 | 49.99 | 48.11
2018-03-18 22:00 | 47.12 | 45.46
2018-03-18 22:30 | 43.83 | 42.81
2018-03-18 23:00 | 43.33 | 42.29
2018-03-18 23:30 | 40.25 | 39.11
2018-03-19 | 38.73 | 37.53
2018-03-19 00:30 | 37.93 | 36.69
2018-03-19 01:00 | 36.87 | 35.58
2018-03-19 01:30 | 36.57 | 35.26
2018-03-19 02:00 | 36.38 | 35.07
2018-03-19 02:30 | 35.99 | 34.8
2018-03-19 03:00 | 35.64 | 34.45
2018-03-19 03:30 | 35.25 | 34.05
2018-03-19 04:00 | 35.24 | 34.04
2018-03-19 04:30 | 36.11 | 34.96
2018-03-19 05:00 | 37 | 35.9
2018-03-19 05:30 | 39.23 | 38.22
2018-03-19 06:00 | 42.54 | 41.62
2018-03-19 06:30 | 47.74 | 46.73
2018-03-19 07:00 | 52.53 | 51.66
2018-03-19 07:30 | 59.06 | 58.31
2018-03-19 08:00 | 62.74 | 62.05
2018-03-19 08:30 | 66.11 | 65.12
2018-03-19 09:00 | 68.79 | 67.52
2018-03-19 09:30 | 69.48 | 68.08
2018-03-19 10:00 | 69.02 | 67.48
2018-03-19 10:30 | 69.51 | 67.75
2018-03-19 11:00 | 70.52 | 68.51
2018-03-19 11:30 | 70.66 | 68.6
2018-03-19 12:00 | 72.43 | 70.28
2018-03-19 12:30 | 73.88 | 71.82
2018-03-19 13:00 | 71.8 | 71.35
2018-03-19 13:30 | 72.68 | 72.33
2018-03-19 14:00 | 72.38 | 72.03
2018-03-19 14:30 | 72.88 | 72.53
2018-03-19 15:00 | 72.91 | 72.56
2018-03-19 15:30 | 74.11 | 73.79
2018-03-19 16:00 | 74.59 | 74.29
2018-03-19 16:30 | 73.23 | 72.86
2018-03-19 17:00 | 70.99 | 70.46
2018-03-19 17:30 | 68.43 | 67.45
2018-03-19 18:00 | 67.17 | 65.84
2018-03-19 18:30 | 66.69 | 65.04
2018-03-19 19:00 | 67.94 | 66.44
2018-03-19 19:30 | 66.42 | 64.72
2018-03-19 20:00 | 64.58 | 62.69
2018-03-19 20:30 | 62.1 | 59.85
2018-03-19 21:00 | 59.8 | 57.19
2018-03-19 21:30 | 57.59 | 54.36
2018-03-19 22:00 | 55.51 | 51.52
2018-03-19 22:30 | 53.29 | 48.87
2018-03-19 23:00 | 52.54 | 47.95
2018-03-19 23:30 | 50.11 | 44.47
2018-03-20 | 56.59 | 42.27
2018-03-20 00:30 | 55.61 | 40.8
2018-03-20 01:00 | 55.2 | 40.03
2018-03-20 01:30 | 54.53 | 39.17
2018-03-20 02:00 | 53.4 | 38.22
2018-03-20 02:30 | 52.89 | 37.46
2018-03-20 03:00 | 50.39 | 36.69
2018-03-20 03:30 | 49.92 | 36.4
2018-03-20 04:00 | 50.01 | 36.51
2018-03-20 04:30 | 50.61 | 37.43
2018-03-20 05:00 | 51.38 | 38.55
2018-03-20 05:30 | 52.92 | 40.71
2018-03-20 06:00 | 48.11 | 44.05
2018-03-20 06:30 | 53.05 | 50.08
2018-03-20 07:00 | 58.42 | 55.96
2018-03-20 07:30 | 63.49 | 62.77
2018-03-20 08:00 | 66.2 | 65.52
2018-03-20 08:30 | 69.84 | 68.79
2018-03-20 09:00 | 70.05 | 69.61
2018-03-20 09:30 | 69.2 | 68.87
2018-03-20 10:00 | 68.38 | 68.05
2018-03-20 10:30 | 68.39 | 68.04
2018-03-20 11:00 | 69 | 68.66
2018-03-20 11:30 | 68.86 | 68.5
2018-03-20 12:00 | 68.74 | 68.38
2018-03-20 12:30 | 70.34 | 69.99
2018-03-20 13:00 | 71.5 | 71.15
2018-03-20 13:30 | 72.25 | 71.9
2018-03-20 14:00 | 72.5 | 72.14
2018-03-20 14:30 | 72.69 | 72.34
2018-03-20 15:00 | 72.45 | 72.1
2018-03-20 15:30 | 73.27 | 72.95
2018-03-20 16:00 | 73.69 | 73.39
2018-03-20 16:30 | 73.05 | 72.73
2018-03-20 17:00 | 71.04 | 70.63
2018-03-20 17:30 | 69.33 | 68.66
2018-03-20 18:00 | 67.12 | 65.83
2018-03-20 18:30 | 66.69 | 64.97
2018-03-20 19:00 | 68.47 | 66.92
2018-03-20 19:30 | 67.15 | 65.44
2018-03-20 20:00 | 65.21 | 63.35
2018-03-20 20:30 | 62.23 | 59.94
2018-03-20 21:00 | 59.33 | 57.52
2018-03-20 21:30 | 55.72 | 54.85
2018-03-20 22:00 | 53.71 | 52.8
2018-03-20 22:30 | 50.63 | 49.62
2018-03-20 23:00 | 49.57 | 48.52
2018-03-20 23:30 | 46.35 | 45.2
2018-03-21 | 43.65 | 42.39
2018-03-21 00:30 | 42.51 | 41.19
2018-03-21 01:00 | 41.05 | 39.67
2018-03-21 01:30 | 40.62 | 39.23
2018-03-21 02:00 | 39.59 | 38.25
2018-03-21 02:30 | 38.65 | 37.32
2018-03-21 03:00 | 37.94 | 36.57
2018-03-21 03:30 | 37.74 | 36.36
2018-03-21 04:00 | 37.75 | 36.37
2018-03-21 04:30 | 38.49 | 37.15
2018-03-21 05:00 | 39.74 | 38.47
2018-03-21 05:30 | 41.89 | 40.71
2018-03-21 06:00 | 45.2 | 44.17
2018-03-21 06:30 | 50.75 | 49.92
2018-03-21 07:00 | 55.71 | 55.35
2018-03-21 07:30 | 62.01 | 61.38
2018-03-21 08:00 | 65.04 | 64.48
2018-03-21 08:30 | 67.1 | 66.69
2018-03-21 09:00 | 67.32 | 66.96
2018-03-21 09:30 | 68.73 | 68.4
2018-03-21 10:00 | 68.46 | 68.14
2018-03-21 10:30 | 69.42 | 69.1
2018-03-21 11:00 | 67.5 | 67.15
2018-03-21 11:30 | 70.29 | 69.95
2018-03-21 12:00 | 70.31 | 69.98
2018-03-21 12:30 | 69.72 | 69.39
2018-03-21 13:00 | 69.36 | 69.04
2018-03-21 13:30 | 69.42 | 69.09
2018-03-21 14:00 | 66.95 | 66.59
2018-03-21 14:30 | 65.63 | 65.28
2018-03-21 15:00 | 66.29 | 65.95
2018-03-21 15:30 | 67.09 | 66.73
2018-03-21 16:00 | 66.68 | 66.26
2018-03-21 16:30 | 65.57 | 65.04
2018-03-21 17:00 | 64.66 | 63.83
2018-03-21 17:30 | 62.95 | 61.56
2018-03-21 18:00 | 61.45 | 59.44
2018-03-21 18:30 | 61.9 | 59.7
2018-03-21 19:00 | 63.45 | 61.41
2018-03-21 19:30 | 62.12 | 59.91
2018-03-21 20:00 | 60.28 | 57.8
2018-03-21 20:30 | 57.84 | 54.88
2018-03-21 21:00 | 55.51 | 51.99
2018-03-21 21:30 | 53.96 | 49.94
2018-03-21 22:00 | 52.79 | 47.56
2018-03-21 22:30 | 53.08 | 45.09
2018-03-21 23:00 | 51.64 | 44.35
2018-03-21 23:30 | 48.8 | 40.89
2018-03-22 | 47.28 | 38.98
2018-03-22 00:30 | 46.34 | 37.77
2018-03-22 01:00 | 44.96 | 36.01
2018-03-22 01:30 | 43.82 | 35.05
2018-03-22 02:00 | 43.45 | 34.51
2018-03-22 02:30 | 42.76 | 33.77
2018-03-22 03:00 | 40.42 | 33.17
2018-03-22 03:30 | 37.85 | 33.36
2018-03-22 04:00 | 37.97 | 33.5
2018-03-22 04:30 | 38.6 | 34.25
2018-03-22 05:00 | 39.69 | 35.52
2018-03-22 05:30 | 41.57 | 37.66
2018-03-22 06:00 | 44.06 | 40.49
2018-03-22 06:30 | 48.04 | 46.07
2018-03-22 07:00 | 51.29 | 50.62
2018-03-22 07:30 | 57.75 | 57.01
2018-03-22 08:00 | 60.94 | 60.38
2018-03-22 08:30 | 62.59 | 62.16
2018-03-22 09:00 | 62.8 | 62.51
2018-03-22 09:30 | 63.53 | 63.3
2018-03-22 10:00 | 63.41 | 63.24
2018-03-22 10:30 | 63.94 | 63.85
2018-03-22 11:00 | 64.04 | 63.98
2018-03-22 11:30 | 65.17 | 65.14
2018-03-22 12:00 | 66.85 | 66.83
2018-03-22 12:30 | 68.83 | 68.81
2018-03-22 13:00 | 66.04 | 66
2018-03-22 13:30 | 66.75 | 66.73
2018-03-22 14:00 | 70.52 | 70.49
2018-03-22 14:30 | 68.18 | 68.11
2018-03-22 15:00 | 67.98 | 67.91
2018-03-22 15:30 | 67.81 | 67.71
2018-03-22 16:00 | 67.82 | 67.61
2018-03-22 16:30 | 67.07 | 66.63
2018-03-22 17:00 | 65.35 | 64.56
2018-03-22 17:30 | 63.85 | 62.63
2018-03-22 18:00 | 63.67 | 61.98
2018-03-22 18:30 | 64.09 | 62.3
2018-03-22 19:00 | 64.3 | 62.42
2018-03-22 19:30 | 62.5 | 60.35
2018-03-22 20:00 | 61.17 | 58.95
2018-03-22 20:30 | 59.22 | 56.51
2018-03-22 21:00 | 57.01 | 54.17
2018-03-22 21:30 | 53.99 | 50.9
2018-03-22 22:00 | 50.65 | 47.26
2018-03-22 22:30 | 48.62 | 44.97
2018-03-22 23:00 | 47.77 | 44
2018-03-22 23:30 | 44.77 | 40.67
2018-03-23 | 43.26 | 38.96
2018-03-23 00:30 | 42.13 | 37.61
2018-03-23 01:00 | 40.94 | 36.25
2018-03-23 01:30 | 41.01 | 36.34
2018-03-23 02:00 | 40.71 | 35.97
2018-03-23 02:30 | 40.14 | 35.36
2018-03-23 03:00 | 39.55 | 34.97
2018-03-23 03:30 | 39.6 | 35.04
2018-03-23 04:00 | 39.46 | 34.84
2018-03-23 04:30 | 40.41 | 35.95
2018-03-23 05:00 | 41.34 | 37.06
2018-03-23 05:30 | 43.37 | 39.38
2018-03-23 06:00 | 46.19 | 42.6
2018-03-23 06:30 | 50.24 | 48.98
2018-03-23 07:00 | 54.86 | 54.55
2018-03-23 07:30 | 60.42 | 59.91
2018-03-23 08:00 | 63.93 | 63.4
2018-03-23 08:30 | 64.08 | 63.63
2018-03-23 09:00 | 64.05 | 63.75
2018-03-23 09:30 | 65.13 | 64.9
2018-03-23 10:00 | 64.34 | 64.14
2018-03-23 10:30 | 66.49 | 66.34
2018-03-23 11:00 | 67.4 | 67.24
2018-03-23 11:30 | 65.6 | 65.45
2018-03-23 12:00 | 66.71 | 66.53
2018-03-23 12:30 | 68.69 | 68.4
2018-03-23 13:00 | 67.17 | 66.78
2018-03-23 13:30 | 67.96 | 67.61
2018-03-23 14:00 | 66.91 | 66.45
2018-03-23 14:30 | 64.91 | 64.21
2018-03-23 15:00 | 62.92 | 62.06
2018-03-23 15:30 | 61.19 | 60.02
2018-03-23 16:00 | 61.27 | 59.91
2018-03-23 16:30 | 61.52 | 59.88
2018-03-23 17:00 | 60.08 | 57.84
2018-03-23 17:30 | 59.56 | 55.96
2018-03-23 18:00 | 58.97 | 55.25
2018-03-23 18:30 | 58.62 | 54.86
2018-03-23 19:00 | 58.24 | 54.44
2018-03-23 19:30 | 56.69 | 52.73
2018-03-23 20:00 | 54.48 | 50.29
2018-03-23 20:30 | 52.95 | 48.68
2018-03-23 21:00 | 48.92 | 47.23
2018-03-23 21:30 | 46.52 | 45.97
2018-03-23 22:00 | 44.28 | 43.71
2018-03-23 22:30 | 42.43 | 41.85
2018-03-23 23:00 | 42.57 | 41.99
2018-03-23 23:30 | 39.65 | 39.05
2018-03-24 | 37.8 | 37.18
2018-03-24 00:30 | 37.38 | 36.75
2018-03-24 01:00 | 36.06 | 35.42
2018-03-24 01:30 | 35.84 | 35.19
2018-03-24 02:00 | 35.87 | 35.21
2018-03-24 02:30 | 35.27 | 34.54
2018-03-24 03:00 | 34.97 | 34.19
2018-03-24 03:30 | 34.47 | 33.69
2018-03-24 04:00 | 34.54 | 33.75
2018-03-24 04:30 | 35.24 | 34.46
2018-03-24 05:00 | 35.8 | 35.04
2018-03-24 05:30 | 36.85 | 36.1
2018-03-24 06:00 | 38.23 | 37.5
2018-03-24 06:30 | 40.77 | 40.07
2018-03-24 07:00 | 42.6 | 41.91
2018-03-24 07:30 | 45.25 | 44.58
2018-03-24 08:00 | 47.52 | 46.85
2018-03-24 08:30 | 50.22 | 49.56
2018-03-24 09:00 | 51.02 | 50.24
2018-03-24 09:30 | 53 | 51.21
2018-03-24 10:00 | 58.05 | 52.02
2018-03-24 10:30 | 58.71 | 52.76
2018-03-24 11:00 | 59.36 | 53.49
2018-03-24 11:30 | 59.26 | 53.37
2018-03-24 12:00 | 58.63 | 52.9
2018-03-24 12:30 | 52.25 | 51.6
2018-03-24 13:00 | 52.73 | 52.02
2018-03-24 13:30 | 52.09 | 51.27
2018-03-24 14:00 | 51.57 | 50.66
2018-03-24 14:30 | 51.19 | 50.13
2018-03-24 15:00 | 51.32 | 50.2
2018-03-24 15:30 | 51.11 | 49.78
2018-03-24 16:00 | 51.35 | 49.96
2018-03-24 16:30 | 51.67 | 50.15
2018-03-24 17:00 | 51.34 | 49.66
2018-03-24 17:30 | 51.82 | 50.13
2018-03-24 18:00 | 53.05 | 51.47
2018-03-24 18:30 | 53.75 | 52.31
2018-03-24 19:00 | 53.81 | 52.38
2018-03-24 19:30 | 52.05 | 50.46
2018-03-24 20:00 | 50.74 | 49.05
2018-03-24 20:30 | 48.94 | 46.95
2018-03-24 21:00 | 46.67 | 45.35
2018-03-24 21:30 | 44.9 | 44.26
2018-03-24 22:00 | 43.57 | 42.92
2018-03-24 22:30 | 42.48 | 41.81
2018-03-24 23:00 | 42.45 | 41.79
2018-03-24 23:30 | 39.72 | 39.02
2018-03-25 | 38.17 | 37.45
2018-03-25 00:30 | 37.33 | 36.6
2018-03-25 01:00 | 36.26 | 35.5
2018-03-25 01:30 | 35.68 | 34.92
2018-03-25 02:00 | 35.46 | 34.69
2018-03-25 02:30 | 34.97 | 34.2
2018-03-25 03:00 | 34.87 | 34.1
2018-03-25 03:30 | 34.67 | 33.9
2018-03-25 04:00 | 34.58 | 33.8
2018-03-25 04:30 | 34.82 | 34.04
2018-03-25 05:00 | 34.9 | 34.12
2018-03-25 05:30 | 35.4 | 34.64
2018-03-25 06:00 | 36.08 | 35.33
2018-03-25 06:30 | 37.37 | 36.64
2018-03-25 07:00 | 38.04 | 37.33
2018-03-25 07:30 | 40.11 | 39.42
2018-03-25 08:00 | 42.69 | 42.02
2018-03-25 08:30 | 44.37 | 43.72
2018-03-25 09:00 | 45.53 | 44.89
2018-03-25 09:30 | 46.9 | 46.27
2018-03-25 10:00 | 48.15 | 47.53
2018-03-25 10:30 | 49.09 | 48.47
2018-03-25 11:00 | 48.98 | 48.35
2018-03-25 11:30 | 49.56 | 48.94
2018-03-25 12:00 | 47.79 | 47.15
2018-03-25 12:30 | 48.38 | 47.75
2018-03-25 13:00 | 48.78 | 48.17
2018-03-25 13:30 | 47.58 | 46.95
2018-03-25 14:00 | 45.72 | 45.07
2018-03-25 14:30 | 46.33 | 45.69
2018-03-25 15:00 | 46.87 | 46.24
2018-03-25 15:30 | 47.24 | 46.62
2018-03-25 16:00 | 47.46 | 46.86
2018-03-25 16:30 | 48.28 | 47.69
2018-03-25 17:00 | 48.06 | 47.48
2018-03-25 17:30 | 48.71 | 48.14
2018-03-25 18:00 | 49.88 | 49.32
2018-03-25 18:30 | 50.62 | 50.05
2018-03-25 19:00 | 51.14 | 50.58
2018-03-25 19:30 | 49.77 | 49.19
2018-03-25 20:00 | 48.43 | 47.84
2018-03-25 20:30 | 46.18 | 45.57
2018-03-25 21:00 | 44.47 | 43.84
2018-03-25 21:30 | 42.68 | 42.03
2018-03-25 22:00 | 41.17 | 40.51
2018-03-25 22:30 | 39.45 | 38.75
2018-03-25 23:00 | 39.05 | 38.35
2018-03-25 23:30 | 36.51 | 35.78
2018-03-26 | 35.14 | 34.37
2018-03-26 00:30 | 34.69 | 33.93
2018-03-26 01:00 | 33.64 | 32.85
2018-03-26 01:30 | 33.56 | 32.64
2018-03-26 02:00 | 33.37 | 32.45
2018-03-26 02:30 | 33.11 | 32.19
2018-03-26 03:00 | 32.76 | 31.83
2018-03-26 03:30 | 32.9 | 31.97
2018-03-26 04:00 | 33.28 | 32.36
2018-03-26 04:30 | 34.15 | 33.24
2018-03-26 05:00 | 35.59 | 34.71
2018-03-26 05:30 | 38.82 | 37.99
2018-03-26 06:00 | 42.37 | 41.58
2018-03-26 06:30 | 48.31 | 47.27
2018-03-26 07:00 | 53.47 | 52.66
2018-03-26 07:30 | 59.64 | 59.08
2018-03-26 08:00 | 62.91 | 62.39
2018-03-26 08:30 | 65.77 | 65.32
2018-03-26 09:00 | 67.81 | 67.42
2018-03-26 09:30 | 68.78 | 68.44
2018-03-26 10:00 | 67.57 | 67.22
2018-03-26 10:30 | 67.29 | 66.97
2018-03-26 11:00 | 66.67 | 66.36
2018-03-26 11:30 | 67.96 | 67.64
2018-03-26 12:00 | 69.97 | 69.66
2018-03-26 12:30 | 71.54 | 71.25
2018-03-26 13:00 | 69.86 | 69.56
2018-03-26 13:30 | 70.73 | 70.43
2018-03-26 14:00 | 70.99 | 70.7
2018-03-26 14:30 | 69.71 | 69.41
2018-03-26 15:00 | 69.22 | 68.92
2018-03-26 15:30 | 68.35 | 68.04
2018-03-26 16:00 | 68.74 | 68.37
2018-03-26 16:30 | 68.7 | 68.25
2018-03-26 17:00 | 66.54 | 65.74
2018-03-26 17:30 | 64.81 | 63.52
2018-03-26 18:00 | 63.56 | 61.67
2018-03-26 18:30 | 63.84 | 61.78
2018-03-26 19:00 | 62.09 | 59.68
2018-03-26 19:30 | 59.36 | 56.45
2018-03-26 20:00 | 57.07 | 53.74
2018-03-26 20:30 | 54.59 | 50.68
2018-03-26 21:00 | 49.35 | 48.28
2018-03-26 21:30 | 46.97 | 46.32
2018-03-26 22:00 | 46.21 | 45.56
2018-03-26 22:30 | 44.12 | 43.46
2018-03-26 23:00 | 43.38 | 42.71
2018-03-26 23:30 | 40.56 | 39.85
2018-03-27 | 38.84 | 38.1
2018-03-27 00:30 | 38.22 | 37.48
2018-03-27 01:00 | 37.27 | 36.51
2018-03-27 01:30 | 36.71 | 35.94
2018-03-27 02:00 | 36.18 | 35.4
2018-03-27 02:30 | 35.95 | 35.17
2018-03-27 03:00 | 35.78 | 35
2018-03-27 03:30 | 35.6 | 34.82
2018-03-27 04:00 | 35.98 | 35.21
2018-03-27 04:30 | 36.8 | 36.04
2018-03-27 05:00 | 38.12 | 37.38
2018-03-27 05:30 | 40.94 | 40.24
2018-03-27 06:00 | 44.78 | 44.11
2018-03-27 06:30 | 50.57 | 49.95
2018-03-27 07:00 | 55.79 | 55.24
2018-03-27 07:30 | 64.66 | 63.08
2018-03-27 08:00 | 68.16 | 66.52
2018-03-27 08:30 | 69.88 | 68.3
2018-03-27 09:00 | 71.5 | 69.93
2018-03-27 09:30 | 71.91 | 70.34
2018-03-27 10:00 | 71.55 | 69.97
2018-03-27 10:30 | 72.58 | 71.01
2018-03-27 11:00 | 72.52 | 70.94
2018-03-27 11:30 | 72.3 | 70.71
2018-03-27 12:00 | 70.63 | 68.99
2018-03-27 12:30 | 71.5 | 69.88
2018-03-27 13:00 | 68.3 | 66.59
2018-03-27 13:30 | 68.23 | 66.5
2018-03-27 14:00 | 70.65 | 68.98
2018-03-27 14:30 | 71.69 | 70.05
2018-03-27 15:00 | 71.59 | 69.96
2018-03-27 15:30 | 70.63 | 69.02
2018-03-27 16:00 | 70.63 | 69.05
2018-03-27 16:30 | 68.94 | 67.38
2018-03-27 17:00 | 66.94 | 65.38
2018-03-27 17:30 | 64.52 | 62.76
2018-03-27 18:00 | 63.78 | 61.97
2018-03-27 18:30 | 64.07 | 62.18
2018-03-27 19:00 | 65.2 | 63.39
2018-03-27 19:30 | 63.59 | 61.62
2018-03-27 20:00 | 61.6 | 59.32
2018-03-27 20:30 | 58.05 | 56.77
2018-03-27 21:00 | 55.52 | 54.68
2018-03-27 21:30 | 53.4 | 52.34
2018-03-27 22:00 | 50.06 | 49.38
2018-03-27 22:30 | 47.74 | 47.1
2018-03-27 23:00 | 46.53 | 45.9
2018-03-27 23:30 | 43.19 | 42.52
2018-03-28 | 41.08 | 40.38
2018-03-28 00:30 | 40 | 39.29
2018-03-28 01:00 | 38.59 | 37.85
2018-03-28 01:30 | 38.24 | 37.5
2018-03-28 02:00 | 37.67 | 36.92
2018-03-28 02:30 | 37.08 | 36.33
2018-03-28 03:00 | 36.28 | 35.52
2018-03-28 03:30 | 36.22 | 35.46
2018-03-28 04:00 | 36.52 | 35.76
2018-03-28 04:30 | 37.54 | 36.8
2018-03-28 05:00 | 38.7 | 37.96
2018-03-28 05:30 | 41.41 | 40.72
2018-03-28 06:00 | 44.77 | 44.1
2018-03-28 06:30 | 50.3 | 49.67
2018-03-28 07:00 | 55.88 | 55.33
2018-03-28 07:30 | 63.68 | 62.57
2018-03-28 08:00 | 71.3 | 66.56
2018-03-28 08:30 | 72.65 | 67.99
2018-03-28 09:00 | 73.69 | 69.06
2018-03-28 09:30 | 73.34 | 68.67
2018-03-28 10:00 | 74.42 | 69.8
2018-03-28 10:30 | 74.04 | 69.38
2018-03-28 11:00 | 72.45 | 68.18
2018-03-28 11:30 | 71.74 | 67.46
2018-03-28 12:00 | 71.57 | 67.28
2018-03-28 12:30 | 73.08 | 68.92
2018-03-28 13:00 | 72.03 | 67.8
2018-03-28 13:30 | 72.17 | 67.94
2018-03-28 14:00 | 73.93 | 69.85
2018-03-28 14:30 | 73.01 | 68.87
2018-03-28 15:00 | 71.65 | 67.43
2018-03-28 15:30 | 71.15 | 66.79
2018-03-28 16:00 | 71.08 | 66.76
2018-03-28 16:30 | 70.38 | 66.09
2018-03-28 17:00 | 69.21 | 64.94
2018-03-28 17:30 | 62.98 | 62.29
2018-03-28 18:00 | 61.41 | 60.45
2018-03-28 18:30 | 61.65 | 60.52
2018-03-28 19:00 | 63.42 | 62.41
2018-03-28 19:30 | 61.35 | 60.14
2018-03-28 20:00 | 58.9 | 57.48
2018-03-28 20:30 | 55.32 | 54.43
2018-03-28 21:00 | 53.59 | 52.48
2018-03-28 21:30 | 50.68 | 49.98
2018-03-28 22:00 | 47.73 | 47.1
2018-03-28 22:30 | 45.07 | 44.42
2018-03-28 23:00 | 44.06 | 43.4
2018-03-28 23:30 | 40.49 | 39.79
2018-03-29 | 38.29 | 37.55
2018-03-29 00:30 | 37.35 | 36.61
2018-03-29 01:00 | 36.14 | 35.37
2018-03-29 01:30 | 35.18 | 34.4
2018-03-29 02:00 | 34.5 | 33.71
2018-03-29 02:30 | 33.74 | 32.84
2018-03-29 03:00 | 33.09 | 32.16
2018-03-29 03:30 | 32.95 | 32.01
2018-03-29 04:00 | 33.13 | 32.2
2018-03-29 04:30 | 33.93 | 33.02
2018-03-29 05:00 | 34.96 | 34.06
2018-03-29 05:30 | 37.56 | 36.71
2018-03-29 06:00 | 40.85 | 40.04
2018-03-29 06:30 | 45.96 | 45.11
2018-03-29 07:00 | 50.25 | 49.57
2018-03-29 07:30 | 56.5 | 55.79
2018-03-29 08:00 | 60.06 | 59.16
2018-03-29 08:30 | 61.77 | 61.11
2018-03-29 09:00 | 62.42 | 61.58
2018-03-29 09:30 | 62.01 | 61.13
2018-03-29 10:00 | 62.52 | 61.49
2018-03-29 10:30 | 63.4 | 62.19
2018-03-29 11:00 | 64.99 | 62.73
2018-03-29 11:30 | 62.83 | 62.49
2018-03-29 12:00 | 63.6 | 63.26
2018-03-29 12:30 | 64.06 | 63.74
2018-03-29 13:00 | 64.56 | 64.24
2018-03-29 13:30 | 66.02 | 65.7
2018-03-29 14:00 | 67.5 | 67.19
2018-03-29 14:30 | 66.51 | 66.18
2018-03-29 15:00 | 67.78 | 67.44
2018-03-29 15:30 | 68.5 | 68.11
2018-03-29 16:00 | 68.04 | 67.54
2018-03-29 16:30 | 66.8 | 66.03
2018-03-29 17:00 | 64.88 | 63.74
2018-03-29 17:30 | 62.48 | 60.8
2018-03-29 18:00 | 62.21 | 60.19
2018-03-29 18:30 | 61.56 | 60.21
2018-03-29 19:00 | 62.4 | 61.24
2018-03-29 19:30 | 60.19 | 59.14
2018-03-29 20:00 | 58.14 | 57.46
2018-03-29 20:30 | 56.66 | 55.85
2018-03-29 21:00 | 54.84 | 53.81
2018-03-29 21:30 | 52.22 | 50.82
2018-03-29 22:00 | 49.43 | 47.68
2018-03-29 22:30 | 46.01 | 45.37
2018-03-29 23:00 | 45.19 | 44.56
2018-03-29 23:30 | 42.26 | 41.59
2018-03-30 | 40.47 | 39.79
2018-03-30 00:30 | 39.16 | 38.46
2018-03-30 01:00 | 37.25 | 36.53
2018-03-30 01:30 | 36.5 | 35.76
2018-03-30 02:00 | 35.65 | 34.89
2018-03-30 02:30 | 35.04 | 34.25
2018-03-30 03:00 | 34.42 | 33.52
2018-03-30 03:30 | 33.79 | 32.87
2018-03-30 04:00 | 33.44 | 32.52
2018-03-30 04:30 | 33.69 | 32.77
2018-03-30 05:00 | 33.99 | 33.08
2018-03-30 05:30 | 34.55 | 33.66
2018-03-30 06:00 | 35.2 | 34.31
2018-03-30 06:30 | 36.31 | 35.45
2018-03-30 07:00 | 37.12 | 36.27
2018-03-30 07:30 | 38.98 | 38.15
2018-03-30 08:00 | 40.07 | 39.25
2018-03-30 08:30 | 39.83 | 38.98
2018-03-30 09:00 | 40.55 | 39.69
2018-03-30 09:30 | 41.12 | 40.28
2018-03-30 10:00 | 39.56 | 38.75
2018-03-30 10:30 | 39.78 | 38.99
2018-03-30 11:00 | 40.76 | 39.99
2018-03-30 11:30 | 40.55 | 39.77
2018-03-30 12:00 | 42.09 | 41.33
2018-03-30 12:30 | 43.45 | 42.72
2018-03-30 13:00 | 43.5 | 42.77
2018-03-30 13:30 | 43.2 | 42.46
2018-03-30 14:00 | 44.31 | 43.59
2018-03-30 14:30 | 44.88 | 44.17
2018-03-30 15:00 | 45.06 | 44.35
2018-03-30 15:30 | 46.79 | 46.12
2018-03-30 16:00 | 48.01 | 47.36
2018-03-30 16:30 | 50.73 | 50.13
2018-03-30 17:00 | 50.5 | 49.9
2018-03-30 17:30 | 49.73 | 49.13
2018-03-30 18:00 | 50.3 | 49.72
2018-03-30 18:30 | 51.72 | 51.16
2018-03-30 19:00 | 52.26 | 51.7
2018-03-30 19:30 | 51.09 | 50.52
2018-03-30 20:00 | 49.6 | 49.02
2018-03-30 20:30 | 47.79 | 47.19
2018-03-30 21:00 | 47.01 | 46.4
2018-03-30 21:30 | 45.97 | 45.35
2018-03-30 22:00 | 44.42 | 43.79
2018-03-30 22:30 | 42.78 | 42.13
2018-03-30 23:00 | 42.63 | 41.98
2018-03-30 23:30 | 39.62 | 38.94
2018-03-31 | 38.16 | 37.46
2018-03-31 00:30 | 37.35 | 36.63
2018-03-31 01:00 | 36.32 | 35.59
2018-03-31 01:30 | 35.66 | 34.91
2018-03-31 02:00 | 35.14 | 34.38
2018-03-31 02:30 | 34.63 | 33.86
2018-03-31 03:00 | 34.22 | 33.44
2018-03-31 03:30 | 33.72 | 32.93
2018-03-31 04:00 | 33.51 | 32.72
2018-03-31 04:30 | 33.7 | 32.93
2018-03-31 05:00 | 33.87 | 33.1
2018-03-31 05:30 | 34.54 | 33.8
2018-03-31 06:00 | 35.08 | 34.34
2018-03-31 06:30 | 36.12 | 35.4
2018-03-31 07:00 | 37.16 | 36.45
2018-03-31 07:30 | 39.85 | 39.17
2018-03-31 08:00 | 41.7 | 41.03
2018-03-31 08:30 | 43.89 | 43.24
2018-03-31 09:00 | 45.77 | 45.11
2018-03-31 09:30 | 44.91 | 44.22
2018-03-31 10:00 | 45.05 | 44.35
2018-03-31 10:30 | 45.68 | 44.99
2018-03-31 11:00 | 43.29 | 42.55
2018-03-31 11:30 | 45.09 | 44.38
2018-03-31 12:00 | 44.23 | 43.5
2018-03-31 12:30 | 45.54 | 44.83
2018-03-31 13:00 | 46.42 | 45.73
2018-03-31 13:30 | 45.63 | 44.92
2018-03-31 14:00 | 44.44 | 43.71
2018-03-31 14:30 | 44.99 | 44.28
2018-03-31 15:00 | 46.01 | 45.32
2018-03-31 15:30 | 46.74 | 46.07
2018-03-31 16:00 | 48.51 | 47.87
2018-03-31 16:30 | 49.8 | 49.19
2018-03-31 17:00 | 49.54 | 48.93
2018-03-31 17:30 | 49.91 | 49.32
2018-03-31 18:00 | 50.44 | 49.86
2018-03-31 18:30 | 51.09 | 50.51
2018-03-31 19:00 | 51.91 | 51.34
2018-03-31 19:30 | 50.63 | 50.05
2018-03-31 20:00 | 49.11 | 48.51
2018-03-31 20:30 | 47.76 | 47.14
2018-03-31 21:00 | 46.36 | 45.73
2018-03-31 21:30 | 45.55 | 44.92
2018-03-31 22:00 | 44.2 | 43.55
2018-03-31 22:30 | 42.29 | 41.63
2018-03-31 23:00 | 42.23 | 41.57
2018-03-31 23:30 | 39.6 | 38.9
2018-04-01 | 37.99 | 37.27
2018-04-01 00:30 | 37.01 | 36.28
2018-04-01 01:00 | 35.72 | 34.97
2018-04-01 01:30 | 35.22 | 34.46
2018-04-01 02:00 | 34.6 | 33.84
2018-04-01 02:30 | 34.33 | 33.56
2018-04-01 03:00 | 34.28 | 33.5
2018-04-01 03:30 | 33.78 | 33
2018-04-01 04:00 | 33.49 | 32.7
2018-04-01 04:30 | 33.7 | 32.91
2018-04-01 05:00 | 33.61 | 32.82
2018-04-01 05:30 | 33.9 | 33.13
2018-04-01 06:00 | 34.44 | 33.67
2018-04-01 06:30 | 34.93 | 34.19
2018-04-01 07:00 | 36.13 | 35.4
2018-04-01 07:30 | 38.24 | 37.54
2018-04-01 08:00 | 40.24 | 39.56
2018-04-01 08:30 | 41.96 | 41.3
2018-04-01 09:00 | 42.64 | 41.98
2018-04-01 09:30 | 41.97 | 41.29
2018-04-01 10:00 | 42.6 | 41.92
2018-04-01 10:30 | 42.2 | 41.51
2018-04-01 11:00 | 42.39 | 41.69
2018-04-01 11:30 | 41.6 | 40.87
2018-04-01 12:00 | 42.88 | 42.17
2018-04-01 12:30 | 43.64 | 42.94
2018-04-01 13:00 | 43.35 | 42.65
2018-04-01 13:30 | 43.41 | 42.7
2018-04-01 14:00 | 45.06 | 44.39
2018-04-01 14:30 | 47.07 | 46.45
2018-04-01 15:00 | 44.64 | 43.99
2018-04-01 15:30 | 45.24 | 44.6
2018-04-01 16:00 | 45.36 | 44.73
2018-04-01 16:30 | 45.2 | 44.57
2018-04-01 17:00 | 44.62 | 43.99
2018-04-01 17:30 | 44.87 | 44.24
2018-04-01 18:00 | 46.14 | 45.53
2018-04-01 18:30 | 48.14 | 47.55
2018-04-01 19:00 | 49.13 | 48.54
2018-04-01 19:30 | 48.21 | 47.61
2018-04-01 20:00 | 46.97 | 46.35
2018-04-01 20:30 | 45.32 | 44.69
2018-04-01 21:00 | 44.23 | 43.59
2018-04-01 21:30 | 42.86 | 42.21
2018-04-01 22:00 | 41.52 | 40.86
2018-04-01 22:30 | 40.32 | 39.64
2018-04-01 23:00 | 40.45 | 39.78
2018-04-01 23:30 | 37.93 | 37.22
2018-04-02 | 36.74 | 36
2018-04-02 00:30 | 36.02 | 35.28
2018-04-02 01:00 | 34.66 | 33.9
2018-04-02 01:30 | 34.12 | 33.34
2018-04-02 02:00 | 33.98 | 33.2
2018-04-02 02:30 | 34.07 | 33.29
2018-04-02 03:00 | 33.75 | 32.87
2018-04-02 03:30 | 33.65 | 32.74
2018-04-02 04:00 | 33.44 | 32.52
2018-04-02 04:30 | 33.86 | 32.95
2018-04-02 05:00 | 33.95 | 33.04
2018-04-02 05:30 | 34.96 | 34.08
2018-04-02 06:00 | 36.09 | 35.21
2018-04-02 06:30 | 37.9 | 37.07
2018-04-02 07:00 | 39.37 | 38.56
2018-04-02 07:30 | 42.05 | 41.26
2018-04-02 08:00 | 44.5 | 43.77
2018-04-02 08:30 | 46.39 | 45.72
2018-04-02 09:00 | 48.22 | 47.58
2018-04-02 09:30 | 49.31 | 48.69
2018-04-02 10:00 | 50.69 | 50.09
2018-04-02 10:30 | 51.36 | 50.76
2018-04-02 11:00 | 51.25 | 50.64
2018-04-02 11:30 | 51.34 | 50.74
2018-04-02 12:00 | 49.87 | 49.25
2018-04-02 12:30 | 50.43 | 49.82
2018-04-02 13:00 | 50.4 | 49.79
2018-04-02 13:30 | 49.83 | 49.21
2018-04-02 14:00 | 48.04 | 47.39
2018-04-02 14:30 | 47.53 | 46.88
2018-04-02 15:00 | 48.45 | 47.82
2018-04-02 15:30 | 47.92 | 47.29
2018-04-02 16:00 | 48.12 | 47.49
2018-04-02 16:30 | 48.87 | 48.26
2018-04-02 17:00 | 48.3 | 47.69
2018-04-02 17:30 | 49.59 | 48.99
2018-04-02 18:00 | 50.04 | 49.47
2018-04-02 18:30 | 50.84 | 50.27
2018-04-02 19:00 | 51.02 | 50.46
2018-04-02 19:30 | 48.8 | 48.22
2018-04-02 20:00 | 47.07 | 46.46
2018-04-02 20:30 | 45.17 | 44.55
2018-04-02 21:00 | 43.67 | 43.03
2018-04-02 21:30 | 42.14 | 41.48
2018-04-02 22:00 | 40.73 | 40.06
2018-04-02 22:30 | 39.28 | 38.59
2018-04-02 23:00 | 39.34 | 38.66
2018-04-02 23:30 | 36.82 | 36.1
2018-04-03 | 35.32 | 34.57
2018-04-03 00:30 | 34.94 | 34.18
2018-04-03 01:00 | 33.96 | 33.1
2018-04-03 01:30 | 33.81 | 32.9
2018-04-03 02:00 | 33.47 | 32.56
2018-04-03 02:30 | 33.07 | 32.15
2018-04-03 03:00 | 33.03 | 32.11
2018-04-03 03:30 | 33.31 | 32.39
2018-04-03 04:00 | 33.35 | 32.43
2018-04-03 04:30 | 34.24 | 33.34
2018-04-03 05:00 | 35.25 | 34.37
2018-04-03 05:30 | 37.86 | 37.02
2018-04-03 06:00 | 41.15 | 40.34
2018-04-03 06:30 | 46.31 | 45.44
2018-04-03 07:00 | 51.42 | 50.64
2018-04-03 07:30 | 58.29 | 57.62
2018-04-03 08:00 | 63.02 | 62.15
2018-04-03 08:30 | 66.53 | 65.34
2018-04-03 09:00 | 67.57 | 66.75
2018-04-03 09:30 | 67.75 | 67.09
2018-04-03 10:00 | 67.05 | 66.38
2018-04-03 10:30 | 67.42 | 66.67
2018-04-03 11:00 | 67.9 | 67.13
2018-04-03 11:30 | 57.59 | 55.81
2018-04-03 12:00 | 69.07 | 66.98
2018-04-03 12:30 | 69.52 | 67.45
2018-04-03 13:00 | 67.64 | 65.51
2018-04-03 13:30 | 69.29 | 67.22
2018-04-03 14:00 | 68.79 | 66.7
2018-04-03 14:30 | 67.44 | 65.33
2018-04-03 15:00 | 67.3 | 65.19
2018-04-03 15:30 | 66.26 | 64.12
2018-04-03 16:00 | 64.85 | 62.7
2018-04-03 16:30 | 63.21 | 61.06
2018-04-03 17:00 | 60.86 | 58.69
2018-04-03 17:30 | 59.48 | 57.3
2018-04-03 18:00 | 58.71 | 56.55
2018-04-03 18:30 | 58.49 | 56.34
2018-04-03 19:00 | 57.77 | 55.62
2018-04-03 19:30 | 54.99 | 52.59
2018-04-03 20:00 | 53.2 | 50.69
2018-04-03 20:30 | 50.58 | 47.97
2018-04-03 21:00 | 48.99 | 46.29
2018-04-03 21:30 | 47.23 | 44.43
2018-04-03 22:00 | 45.07 | 42.14
2018-04-03 22:30 | 40.22 | 39.77
2018-04-03 23:00 | 40.14 | 39.99
2018-04-03 23:30 | 37.68 | 37.47
2018-04-04 | 35.64 | 35.36
2018-04-04 00:30 | 34.89 | 34.67
2018-04-04 01:00 | 33.34 | 33.2
2018-04-04 01:30 | 32.53 | 32.37
2018-04-04 02:00 | 32.72 | 32.55
2018-04-04 02:30 | 32.12 | 31.98
2018-04-04 03:00 | 31.59 | 31.47
2018-04-04 03:30 | 31.39 | 31.28
2018-04-04 04:00 | 31.53 | 31.42
2018-04-04 04:30 | 32.08 | 31.95
2018-04-04 05:00 | 32.91 | 32.76
2018-04-04 05:30 | 35.34 | 35.14
2018-04-04 06:00 | 39.03 | 38.66
2018-04-04 06:30 | 45.09 | 44.08
2018-04-04 07:00 | 51.47 | 48.7
2018-04-04 07:30 | 57.48 | 54.97
2018-04-04 08:00 | 60.89 | 58.58
2018-04-04 08:30 | 62.52 | 60.34
2018-04-04 09:00 | 64.57 | 62.45
2018-04-04 09:30 | 62.81 | 60.63
2018-04-04 10:00 | 61.97 | 60.2
2018-04-04 10:30 | 62.09 | 60.37
2018-04-04 11:00 | 60.14 | 58.32
2018-04-04 11:30 | 62.47 | 60.72
2018-04-04 12:00 | 63.25 | 61.53
2018-04-04 12:30 | 63.08 | 61.36
2018-04-04 13:00 | 64.64 | 62.98
2018-04-04 13:30 | 64.14 | 62.46
2018-04-04 14:00 | 62.59 | 60.86
2018-04-04 14:30 | 61.49 | 59.73
2018-04-04 15:00 | 60.24 | 58.45
2018-04-04 15:30 | 61.53 | 59.81
2018-04-04 16:00 | 61.86 | 60.15
2018-04-04 16:30 | 60.37 | 58.59
2018-04-04 17:00 | 58.64 | 56.56
2018-04-04 17:30 | 57.87 | 55.22
2018-04-04 18:00 | 57.09 | 53.76
2018-04-04 18:30 | 57.46 | 53.94
2018-04-04 19:00 | 58.14 | 54.63
2018-04-04 19:30 | 56.19 | 52.34
2018-04-04 20:00 | 54.19 | 49.85
2018-04-04 20:30 | 51.23 | 47.05
2018-04-04 21:00 | 48.64 | 44.93
2018-04-04 21:30 | 47.22 | 43.12
2018-04-04 22:00 | 41.04 | 40.83
2018-04-04 22:30 | 39.15 | 39.02
2018-04-04 23:00 | 39.17 | 39
2018-04-04 23:30 | 36.56 | 36.32
2018-04-05 | 34.66 | 34.48
2018-04-05 00:30 | 33.61 | 33.59
2018-04-05 01:00 | 32.36 | 32.34
2018-04-05 01:30 | 31.69 | 31.67
2018-04-05 02:00 | 31.36 | 31.34
2018-04-05 02:30 | 31.29 | 31.25
2018-04-05 03:00 | 30.57 | 30.53
2018-04-05 03:30 | 30.47 | 30.37
2018-04-05 04:00 | 30.54 | 30.44
2018-04-05 04:30 | 31.08 | 30.98
2018-04-05 05:00 | 31.86 | 31.75
2018-04-05 05:30 | 34.41 | 34.23
2018-04-05 06:00 | 37.1 | 36.78
2018-04-05 06:30 | 41.9 | 41.31
2018-04-05 07:00 | 45.55 | 45.25
2018-04-05 07:30 | 52.75 | 51
2018-04-05 08:00 | 56.67 | 54.1
2018-04-05 08:30 | 59.26 | 56.84
2018-04-05 09:00 | 60.56 | 58.17
2018-04-05 09:30 | 60.22 | 57.79
2018-04-05 10:00 | 61.09 | 58.74
2018-04-05 10:30 | 62.11 | 59.85
2018-04-05 11:00 | 61.27 | 58.95
2018-04-05 11:30 | 60.96 | 58.6
2018-04-05 12:00 | 62.5 | 60.21
2018-04-05 12:30 | 65.54 | 63.39
2018-04-05 13:00 | 64.45 | 62.27
2018-04-05 13:30 | 64.49 | 62.3
2018-04-05 14:00 | 63.03 | 60.79
2018-04-05 14:30 | 63.11 | 60.87
2018-04-05 15:00 | 64.31 | 62.13
2018-04-05 15:30 | 62.63 | 60.42
2018-04-05 16:00 | 62.01 | 59.8
2018-04-05 16:30 | 61.93 | 59.77
2018-04-05 17:00 | 59.9 | 57.72
2018-04-05 17:30 | 58.55 | 56.37
2018-04-05 18:00 | 58.57 | 56.44
2018-04-05 18:30 | 59.26 | 57.19
2018-04-05 19:00 | 59.19 | 57.12
2018-04-05 19:30 | 57.06 | 54.91
2018-04-05 20:00 | 55.07 | 52.85
2018-04-05 20:30 | 52.54 | 50.23
2018-04-05 21:00 | 50.72 | 48.32
2018-04-05 21:30 | 48.73 | 46.16
2018-04-05 22:00 | 46.1 | 43.29
2018-04-05 22:30 | 44.24 | 41.33
2018-04-05 23:00 | 43.94 | 40.96
2018-04-05 23:30 | 40.88 | 37.52
2018-04-06 | 38.96 | 35.44
2018-04-06 00:30 | 38.12 | 34.38
2018-04-06 01:00 | 36.92 | 32.98
2018-04-06 01:30 | 36.39 | 32.37
2018-04-06 02:00 | 35.87 | 31.79
2018-04-06 02:30 | 35.36 | 31.25
2018-04-06 03:00 | 35.45 | 31.35
2018-04-06 03:30 | 35.4 | 31.29
2018-04-06 04:00 | 35.28 | 31.16
2018-04-06 04:30 | 35.95 | 31.91
2018-04-06 05:00 | 36.83 | 32.89
2018-04-06 05:30 | 39.1 | 35.4
2018-04-06 06:00 | 41.79 | 38.31
2018-04-06 06:30 | 46.59 | 43.41
2018-04-06 07:00 | 50.18 | 47.35
2018-04-06 07:30 | 55.74 | 53.15
2018-04-06 08:00 | 58.59 | 56.19
2018-04-06 08:30 | 61.08 | 58.88
2018-04-06 09:00 | 61.18 | 59.43
2018-04-06 09:30 | 60.51 | 58.71
2018-04-06 10:00 | 60.85 | 59.04
2018-04-06 10:30 | 59.47 | 57.61
2018-04-06 11:00 | 60.08 | 58.21
2018-04-06 11:30 | 62.25 | 60.44
2018-04-06 12:00 | 62.6 | 60.8
2018-04-06 12:30 | 65.22 | 63.52
2018-04-06 13:00 | 64.34 | 62.62
2018-04-06 13:30 | 64.12 | 62.43
2018-04-06 14:00 | 63.04 | 61.31
2018-04-06 14:30 | 61.06 | 59.29
2018-04-06 15:00 | 61.5 | 59.75
2018-04-06 15:30 | 61.12 | 59.4
2018-04-06 16:00 | 60.51 | 58.66
2018-04-06 16:30 | 60.06 | 58.17
2018-04-06 17:00 | 59.09 | 57.02
2018-04-06 17:30 | 57.44 | 55.41
2018-04-06 18:00 | 55.94 | 54.1
2018-04-06 18:30 | 55.9 | 53.85
2018-04-06 19:00 | 55.56 | 53.37
2018-04-06 19:30 | 53.35 | 50.87
2018-04-06 20:00 | 51.58 | 48.75
2018-04-06 20:30 | 46.64 | 45.99
2018-04-06 21:00 | 44.58 | 44.55
2018-04-06 21:30 | 43 | 42.97
2018-04-06 22:00 | 41.31 | 41.24
2018-04-06 22:30 | 40.29 | 40.18
2018-04-06 23:00 | 39.86 | 39.8
2018-04-06 23:30 | 36.99 | 36.96
2018-04-07 | 34.98 | 34.95
2018-04-07 00:30 | 33.98 | 33.95
2018-04-07 01:00 | 32.91 | 32.88
2018-04-07 01:30 | 31.89 | 31.85
2018-04-07 02:00 | 31.41 | 31.3
2018-04-07 02:30 | 30.89 | 30.79
2018-04-07 03:00 | 30.56 | 30.46
2018-04-07 03:30 | 30.27 | 30.17
2018-04-07 04:00 | 30.2 | 30.11
2018-04-07 04:30 | 30.34 | 30.25
2018-04-07 05:00 | 30.87 | 30.76
2018-04-07 05:30 | 31.83 | 31.73
2018-04-07 06:00 | 33.3 | 33.15
2018-04-07 06:30 | 35.27 | 35.06
2018-04-07 07:00 | 36.63 | 36.36
2018-04-07 07:30 | 39.08 | 38.63
2018-04-07 08:00 | 43.73 | 41.27
2018-04-07 08:30 | 48.05 | 45.11
2018-04-07 09:00 | 47.17 | 44.14
2018-04-07 09:30 | 49.78 | 46.91
2018-04-07 10:00 | 51.06 | 48.27
2018-04-07 10:30 | 50.6 | 47.77
2018-04-07 11:00 | 49.28 | 46.33
2018-04-07 11:30 | 51.53 | 48.75
2018-04-07 12:00 | 50.04 | 47.18
2018-04-07 12:30 | 49.66 | 46.76
2018-04-07 13:00 | 49.89 | 46.98
2018-04-07 13:30 | 48.13 | 45.12
2018-04-07 14:00 | 47.39 | 44.34
2018-04-07 14:30 | 46.47 | 43.36
2018-04-07 15:00 | 46.53 | 43.43
2018-04-07 15:30 | 46.89 | 43.87
2018-04-07 16:00 | 47.18 | 44.19
2018-04-07 16:30 | 48.81 | 45.96
2018-04-07 17:00 | 48.73 | 45.88
2018-04-07 17:30 | 48.99 | 46.17
2018-04-07 18:00 | 49.94 | 47.18
2018-04-07 18:30 | 51.03 | 48.34
2018-04-07 19:00 | 51.06 | 48.37
2018-04-07 19:30 | 49.18 | 46.39
2018-04-07 20:00 | 47.97 | 45.09
2018-04-07 20:30 | 46.37 | 43.39
2018-04-07 21:00 | 45.2 | 42.14
2018-04-07 21:30 | 44.31 | 41.19
2018-04-07 22:00 | 43.39 | 40.2
2018-04-07 22:30 | 42.1 | 38.82
2018-04-07 23:00 | 42.31 | 39.06
2018-04-07 23:30 | 39.67 | 36.2
2018-04-08 | 38.16 | 34.56
2018-04-08 00:30 | 37.47 | 33.78
2018-04-08 01:00 | 36.56 | 32.77
2018-04-08 01:30 | 33.57 | 31.8
2018-04-08 02:00 | 31.27 | 31.21
2018-04-08 02:30 | 30.81 | 30.71
2018-04-08 03:00 | 30.58 | 30.48
2018-04-08 03:30 | 30.62 | 30.53
2018-04-08 04:00 | 30.27 | 30.18
2018-04-08 04:30 | 30.36 | 30.26
2018-04-08 05:00 | 30.41 | 30.32
2018-04-08 05:30 | 31.29 | 31.2
2018-04-08 06:00 | 31.59 | 31.5
2018-04-08 06:30 | 32.52 | 32.43
2018-04-08 07:00 | 32.96 | 32.87
2018-04-08 07:30 | 34.5 | 34.38
2018-04-08 08:00 | 35.81 | 35.6
2018-04-08 08:30 | 37.01 | 36.69
2018-04-08 09:00 | 39.01 | 38.51
2018-04-08 09:30 | 40.07 | 39.51
2018-04-08 10:00 | 39.69 | 39.5
2018-04-08 10:30 | 39.63 | 39.4
2018-04-08 11:00 | 39.53 | 39.28
2018-04-08 11:30 | 40.19 | 39.9
2018-04-08 12:00 | 39.9 | 39.6
2018-04-08 12:30 | 41.18 | 40.9
2018-04-08 13:00 | 40.73 | 40.44
2018-04-08 13:30 | 41.11 | 40.8
2018-04-08 14:00 | 42.66 | 42.34
2018-04-08 14:30 | 42.29 | 42.06
2018-04-08 15:00 | 43.74 | 43.54
2018-04-08 15:30 | 44.6 | 44.46
2018-04-08 16:00 | 45.13 | 45.01
2018-04-08 16:30 | 46.59 | 46.49
2018-04-08 17:00 | 46.08 | 46.01
2018-04-08 17:30 | 46.14 | 46.06
2018-04-08 18:00 | 47.66 | 47.58
2018-04-08 18:30 | 50.29 | 50.16
2018-04-08 19:00 | 50.41 | 50.29
2018-04-08 19:30 | 48.6 | 48.5
2018-04-08 20:00 | 47.13 | 47.05
2018-04-08 20:30 | 45.02 | 44.95
2018-04-08 21:00 | 43.32 | 43.26
2018-04-08 21:30 | 41.81 | 41.77
2018-04-08 22:00 | 40.21 | 40.17
2018-04-08 22:30 | 38.27 | 38.25
2018-04-08 23:00 | 38.17 | 38.15
2018-04-08 23:30 | 35.41 | 35.38
2018-04-09 | 33.8 | 33.77
2018-04-09 00:30 | 33.08 | 33.02
2018-04-09 01:00 | 32.39 | 32.28
2018-04-09 01:30 | 32.11 | 31.99
2018-04-09 02:00 | 31.74 | 31.63
2018-04-09 02:30 | 31.18 | 31.08
2018-04-09 03:00 | 31.27 | 31.16
2018-04-09 03:30 | 31.45 | 31.34
2018-04-09 04:00 | 31.18 | 31.08
2018-04-09 04:30 | 32.17 | 32.05
2018-04-09 05:00 | 33.38 | 33.23
2018-04-09 05:30 | 35.88 | 35.64
2018-04-09 06:00 | 39.7 | 39.27
2018-04-09 06:30 | 44.73 | 43.87
2018-04-09 07:00 | 48.52 | 48.02
2018-04-09 07:30 | 54.39 | 53.66
2018-04-09 08:00 | 57.57 | 57.04
2018-04-09 08:30 | 60.31 | 60.14
2018-04-09 09:00 | 61.4 | 61.33
2018-04-09 09:30 | 61.05 | 60.99
2018-04-09 10:00 | 60.37 | 60.32
2018-04-09 10:30 | 60.06 | 60.03
2018-04-09 11:00 | 59.87 | 59.77
2018-04-09 11:30 | 59.67 | 59.45
2018-04-09 12:00 | 60.23 | 60.05
2018-04-09 12:30 | 61.17 | 61.01
2018-04-09 13:00 | 60.55 | 60.38
2018-04-09 13:30 | 60.77 | 60.59
2018-04-09 14:00 | 60.82 | 60.61
2018-04-09 14:30 | 61.26 | 61.06
2018-04-09 15:00 | 62.04 | 61.79
2018-04-09 15:30 | 61.62 | 61.29
2018-04-09 16:00 | 61.79 | 61.32
2018-04-09 16:30 | 62.53 | 61.84
2018-04-09 17:00 | 61.53 | 60.39
2018-04-09 17:30 | 60.52 | 58.76
2018-04-09 18:00 | 59.48 | 56.99
2018-04-09 18:30 | 60.55 | 58.01
2018-04-09 19:00 | 61.13 | 58.61
2018-04-09 19:30 | 59.11 | 56.29
2018-04-09 20:00 | 55.82 | 53.69
2018-04-09 20:30 | 51.96 | 50.81
2018-04-09 21:00 | 49.92 | 48.51
2018-04-09 21:30 | 48.2 | 46.48
2018-04-09 22:00 | 45.82 | 43.78
2018-04-09 22:30 | 44.16 | 41.62
2018-04-09 23:00 | 44.15 | 41.42
2018-04-09 23:30 | 40.65 | 37.88
2018-04-10 | 35.82 | 35.78
2018-04-10 00:30 | 34.83 | 34.79
2018-04-10 01:00 | 34.25 | 33.4
2018-04-10 01:30 | 33.58 | 32.66
2018-04-10 02:00 | 33.09 | 32.16
2018-04-10 02:30 | 32.55 | 31.59
2018-04-10 03:00 | 32.19 | 31.22
2018-04-10 03:30 | 32.16 | 31.2
2018-04-10 04:00 | 32.06 | 31.1
2018-04-10 04:30 | 32.63 | 31.68
2018-04-10 05:00 | 33.86 | 32.94
2018-04-10 05:30 | 36.1 | 35.23
2018-04-10 06:00 | 39.1 | 38.26
2018-04-10 06:30 | 43.71 | 42.89
2018-04-10 07:00 | 48.19 | 47.52
2018-04-10 07:30 | 54.61 | 53.52
2018-04-10 08:00 | 59.28 | 55.79
2018-04-10 08:30 | 61.1 | 58.13
2018-04-10 09:00 | 63.81 | 59.33
2018-04-10 09:30 | 63.61 | 58.95
2018-04-10 10:00 | 63.06 | 58.43
2018-04-10 10:30 | 63.8 | 59.54
2018-04-10 11:00 | 62.98 | 58.96
2018-04-10 11:30 | 62.85 | 58.88
2018-04-10 12:00 | 62.55 | 58.64
2018-04-10 12:30 | 63.35 | 59.35
2018-04-10 13:00 | 62.9 | 58.88
2018-04-10 13:30 | 63.39 | 59.33
2018-04-10 14:00 | 63.57 | 59.64
2018-04-10 14:30 | 63.49 | 59.51
2018-04-10 15:00 | 63.93 | 59.8
2018-04-10 15:30 | 64.78 | 60.44
2018-04-10 16:00 | 65.63 | 61.04
2018-04-10 16:30 | 65.56 | 60.32
2018-04-10 17:00 | 62.42 | 59.07
2018-04-10 17:30 | 61.53 | 56.59
2018-04-10 18:00 | 61.05 | 55.55
2018-04-10 18:30 | 61.45 | 55.96
2018-04-10 19:00 | 58.98 | 56.41
2018-04-10 19:30 | 54.16 | 53.72
2018-04-10 20:00 | 51.96 | 51.5
2018-04-10 20:30 | 49.31 | 48.86
2018-04-10 21:00 | 47.85 | 47.39
2018-04-10 21:30 | 46.04 | 45.57
2018-04-10 22:00 | 43.85 | 43.38
2018-04-10 22:30 | 41.75 | 41.27
2018-04-10 23:00 | 40.07 | 39.55
2018-04-10 23:30 | 38.64 | 38.03
2018-04-11 | 38.41 | 37.76
2018-04-11 00:30 | 36.94 | 36.16
2018-04-11 01:00 | 35.17 | 34.39
2018-04-11 01:30 | 34.1 | 33.3
2018-04-11 02:00 | 33.39 | 32.49
2018-04-11 02:30 | 32.85 | 31.85
2018-04-11 03:00 | 32.46 | 31.41
2018-04-11 03:30 | 32.56 | 31.48
2018-04-11 04:00 | 32.82 | 31.78
2018-04-11 04:30 | 33.32 | 32.36
2018-04-11 05:00 | 34.48 | 33.53
2018-04-11 05:30 | 37.18 | 36.21
2018-04-11 06:00 | 40.09 | 39.1
2018-04-11 06:30 | 44.77 | 43.62
2018-04-11 07:00 | 48.63 | 47.94
2018-04-11 07:30 | 54.77 | 53.85
2018-04-11 08:00 | 57.96 | 57.51
2018-04-11 08:30 | 60.31 | 59.75
2018-04-11 09:00 | 61.12 | 60.31
2018-04-11 09:30 | 60.55 | 59.71
2018-04-11 10:00 | 60.77 | 59.89
2018-04-11 10:30 | 60.52 | 59.53
2018-04-11 11:00 | 61.04 | 59.96
2018-04-11 11:30 | 61.69 | 60.5
2018-04-11 12:00 | 61.8 | 60.5
2018-04-11 12:30 | 63.48 | 62.3
2018-04-11 13:00 | 62.8 | 61.68
2018-04-11 13:30 | 62.59 | 61.49
2018-04-11 14:00 | 62.42 | 61.19
2018-04-11 14:30 | 64.51 | 63.45
2018-04-11 15:00 | 64.63 | 63.79
2018-04-11 15:30 | 62.29 | 61.42
2018-04-11 16:00 | 61.66 | 60.92
2018-04-11 16:30 | 61.27 | 60.76
2018-04-11 17:00 | 60 | 59.51
2018-04-11 17:30 | 58.13 | 57.66
2018-04-11 18:00 | 57.34 | 56.9
2018-04-11 18:30 | 57.85 | 57.42
2018-04-11 19:00 | 58.11 | 57.69
2018-04-11 19:30 | 55.38 | 54.94
2018-04-11 20:00 | 52.69 | 52.24
2018-04-11 20:30 | 50.22 | 49.76
2018-04-11 21:00 | 47.91 | 47.42
2018-04-11 21:30 | 46.14 | 45.49
2018-04-11 22:00 | 43.66 | 42.99
2018-04-11 22:30 | 41.82 | 41.12
2018-04-11 23:00 | 41.72 | 41.03
2018-04-11 23:30 | 38.57 | 37.84
2018-04-12 | 36.56 | 35.79
2018-04-12 00:30 | 35.39 | 34.61
2018-04-12 01:00 | 34.59 | 33.8
2018-04-12 01:30 | 33.84 | 32.99
2018-04-12 02:00 | 33.25 | 32.3
2018-04-12 02:30 | 32.88 | 31.94
2018-04-12 03:00 | 32.1 | 31.14
2018-04-12 03:30 | 32.44 | 31.49
2018-04-12 04:00 | 32.29 | 31.33
2018-04-12 04:30 | 33.15 | 32.21
2018-04-12 05:00 | 34.29 | 33.38
2018-04-12 05:30 | 36.61 | 35.74
2018-04-12 06:00 | 40.28 | 39.46
2018-04-12 06:30 | 45.02 | 44.16
2018-04-12 07:00 | 49.28 | 48.57
2018-04-12 07:30 | 55.74 | 54.83
2018-04-12 08:00 | 59.56 | 58.84
2018-04-12 08:30 | 61.8 | 60.96
2018-04-12 09:00 | 62.37 | 61.46
2018-04-12 09:30 | 63.54 | 62.61
2018-04-12 10:00 | 62.74 | 61.82
2018-04-12 10:30 | 61.77 | 60.84
2018-04-12 11:00 | 60.76 | 59.72
2018-04-12 11:30 | 61.4 | 60
2018-04-12 12:00 | 65.54 | 61.41
2018-04-12 12:30 | 69.55 | 65.55
2018-04-12 13:00 | 68.01 | 63.8
2018-04-12 13:30 | 66.88 | 62.6
2018-04-12 14:00 | 67.01 | 62.72
2018-04-12 14:30 | 66.63 | 62.08
2018-04-12 15:00 | 66.32 | 61.71
2018-04-12 15:30 | 65.26 | 60.27
2018-04-12 16:00 | 64.55 | 59.27
2018-04-12 16:30 | 62.35 | 58.17
2018-04-12 17:00 | 61.08 | 56.7
2018-04-12 17:30 | 60.03 | 55.03
2018-04-12 18:00 | 60.74 | 55.61
2018-04-12 18:30 | 61.85 | 56.88
2018-04-12 19:00 | 61.41 | 56.45
2018-04-12 19:30 | 59.02 | 53.74
2018-04-12 20:00 | 57.65 | 52.23
2018-04-12 20:30 | 55.81 | 50.08
2018-04-12 21:00 | 54.3 | 48.47
2018-04-12 21:30 | 47.05 | 45.4
2018-04-12 22:00 | 43.18 | 42.55
2018-04-12 22:30 | 41.54 | 40.85
2018-04-12 23:00 | 41.2 | 40.52
2018-04-12 23:30 | 38.25 | 37.52
2018-04-13 | 36.53 | 35.79
2018-04-13 00:30 | 35.74 | 35.03
2018-04-13 01:00 | 34.28 | 33.62
2018-04-13 01:30 | 33.64 | 32.98
2018-04-13 02:00 | 32.97 | 32.28
2018-04-13 02:30 | 31.99 | 31.28
2018-04-13 03:00 | 31.84 | 31.13
2018-04-13 03:30 | 31.97 | 31.27
2018-04-13 04:00 | 31.95 | 31.25
2018-04-13 04:30 | 32.65 | 31.96
2018-04-13 05:00 | 33.87 | 33.19
2018-04-13 05:30 | 36.59 | 35.99
2018-04-13 06:00 | 39.8 | 39.23
2018-04-13 06:30 | 44.3 | 43.52
2018-04-13 07:00 | 46.97 | 46.49
2018-04-13 07:30 | 53.93 | 53.25
2018-04-13 08:00 | 64.56 | 63.72
2018-04-13 08:30 | 61.94 | 59.93
2018-04-13 09:00 | 62.58 | 59.95
2018-04-13 09:30 | 60.38 | 59.85
2018-04-13 10:00 | 59.94 | 59.44
2018-04-13 10:30 | 59.92 | 59.47
2018-04-13 11:00 | 59.68 | 59.24
2018-04-13 11:30 | 61.01 | 60.62
2018-04-13 12:00 | 60.89 | 60.5
2018-04-13 12:30 | 62.32 | 61.92
2018-04-13 13:00 | 61.46 | 61.03
2018-04-13 13:30 | 61.07 | 60.64
2018-04-13 14:00 | 61.65 | 61.22
2018-04-13 14:30 | 61.43 | 60.97
2018-04-13 15:00 | 61.66 | 61.16
2018-04-13 15:30 | 60.6 | 59.85
2018-04-13 16:00 | 60.18 | 59.28
2018-04-13 16:30 | 60.86 | 59.77
2018-04-13 17:00 | 59.11 | 58.41
2018-04-13 17:30 | 57.44 | 56.25
2018-04-13 18:00 | 56.43 | 54.73
2018-04-13 18:30 | 57.28 | 55.56
2018-04-13 19:00 | 57.33 | 55.5
2018-04-13 19:30 | 55.27 | 53.14
2018-04-13 20:00 | 53.71 | 51.31
2018-04-13 20:30 | 50.97 | 48.73
2018-04-13 21:00 | 48.75 | 46.95
2018-04-13 21:30 | 47.57 | 45.57
2018-04-13 22:00 | 43.99 | 43.03
2018-04-13 22:30 | 42.1 | 41.42
2018-04-13 23:00 | 41.69 | 41.02
2018-04-13 23:30 | 38.64 | 37.92
2018-04-14 | 36.83 | 36.08
2018-04-14 00:30 | 35.61 | 34.85
2018-04-14 01:00 | 34.03 | 33.12
2018-04-14 01:30 | 33.33 | 32.4
2018-04-14 02:00 | 32.47 | 31.52
2018-04-14 02:30 | 32.01 | 31.05
2018-04-14 03:00 | 31.58 | 30.61
2018-04-14 03:30 | 31.1 | 30.13
2018-04-14 04:00 | 30.94 | 29.95
2018-04-14 04:30 | 31.36 | 30.39
2018-04-14 05:00 | 31.74 | 30.77
2018-04-14 05:30 | 32.84 | 31.91
2018-04-14 06:00 | 34.06 | 33.14
2018-04-14 06:30 | 36.24 | 35.37
2018-04-14 07:00 | 38.06 | 37.21
2018-04-14 07:30 | 40.93 | 40.12
2018-04-14 08:00 | 43.3 | 42.5
2018-04-14 08:30 | 46.28 | 45.5
2018-04-14 09:00 | 47.12 | 46.42
2018-04-14 09:30 | 47.22 | 46.52
2018-04-14 10:00 | 46.23 | 45.51
2018-04-14 10:30 | 45.86 | 45.1
2018-04-14 11:00 | 47.39 | 46.58
2018-04-14 11:30 | 48.57 | 47.81
2018-04-14 12:00 | 49.28 | 48.58
2018-04-14 12:30 | 50.22 | 49.57
2018-04-14 13:00 | 49.42 | 48.77
2018-04-14 13:30 | 47.51 | 46.84
2018-04-14 14:00 | 46.17 | 45.5
2018-04-14 14:30 | 45.9 | 45.23
2018-04-14 15:00 | 45.11 | 44.44
2018-04-14 15:30 | 44.7 | 44.03
2018-04-14 16:00 | 44.33 | 43.66
2018-04-14 16:30 | 44.41 | 43.75
2018-04-14 17:00 | 45.11 | 44.47
2018-04-14 17:30 | 45.66 | 45.03
2018-04-14 18:00 | 46.68 | 46.07
2018-04-14 18:30 | 47.93 | 47.33
2018-04-14 19:00 | 47.81 | 47.21
2018-04-14 19:30 | 46.23 | 45.6
2018-04-14 20:00 | 44.73 | 44.09
2018-04-14 20:30 | 43.32 | 42.67
2018-04-14 21:00 | 42.66 | 41.99
2018-04-14 21:30 | 41.52 | 40.84
2018-04-14 22:00 | 39.7 | 39
2018-04-14 22:30 | 38.27 | 37.55
2018-04-14 23:00 | 38.41 | 37.7
2018-04-14 23:30 | 35.55 | 34.79
2018-04-15 | 33.97 | 33.19
2018-04-15 00:30 | 33.63 | 32.76
2018-04-15 01:00 | 32.67 | 31.74
2018-04-15 01:30 | 32.19 | 31.24
2018-04-15 02:00 | 31.71 | 30.76
2018-04-15 02:30 | 31.23 | 30.26
2018-04-15 03:00 | 30.85 | 29.88
2018-04-15 03:30 | 30.68 | 29.7
2018-04-15 04:00 | 30.56 | 29.58
2018-04-15 04:30 | 30.65 | 29.67
2018-04-15 05:00 | 30.72 | 29.74
2018-04-15 05:30 | 31.16 | 30.2
2018-04-15 06:00 | 31.39 | 30.45
2018-04-15 06:30 | 32.15 | 31.24
2018-04-15 07:00 | 32.9 | 32
2018-04-15 07:30 | 34.64 | 33.78
2018-04-15 08:00 | 35.95 | 35.09
2018-04-15 08:30 | 37.99 | 37.15
2018-04-15 09:00 | 39.53 | 38.69
2018-04-15 09:30 | 40.73 | 39.98
2018-04-15 10:00 | 41.2 | 40.47
2018-04-15 10:30 | 41.51 | 40.77
2018-04-15 11:00 | 41.08 | 40.32
2018-04-15 11:30 | 41.32 | 40.56
2018-04-15 12:00 | 40.9 | 40.13
2018-04-15 12:30 | 42.15 | 41.4
2018-04-15 13:00 | 41.94 | 41.19
2018-04-15 13:30 | 41.95 | 41.2
2018-04-15 14:00 | 42.29 | 41.55
2018-04-15 14:30 | 42.35 | 41.62
2018-04-15 15:00 | 43.22 | 42.51
2018-04-15 15:30 | 44.09 | 43.4
2018-04-15 16:00 | 45.25 | 44.59
2018-04-15 16:30 | 47.32 | 46.69
2018-04-15 17:00 | 47.76 | 47.15
2018-04-15 17:30 | 48.46 | 47.87
2018-04-15 18:00 | 50.04 | 49.47
2018-04-15 18:30 | 52.44 | 51.89
2018-04-15 19:00 | 53.21 | 52.67
2018-04-15 19:30 | 51.17 | 50.6
2018-04-15 20:00 | 49.21 | 48.62
2018-04-15 20:30 | 46.73 | 46.12
2018-04-15 21:00 | 45.01 | 44.38
2018-04-15 21:30 | 43.08 | 42.43
2018-04-15 22:00 | 41.38 | 40.72
2018-04-15 22:30 | 39.63 | 38.94
2018-04-15 23:00 | 39.24 | 38.55
2018-04-15 23:30 | 35.92 | 35.18
2018-04-16 | 34.42 | 33.65
2018-04-16 00:30 | 33.59 | 32.69
2018-04-16 01:00 | 32.52 | 31.59
2018-04-16 01:30 | 32.21 | 31.26
2018-04-16 02:00 | 32.19 | 31.25
2018-04-16 02:30 | 31.56 | 30.61
2018-04-16 03:00 | 31.17 | 30.21
2018-04-16 03:30 | 31.39 | 30.43
2018-04-16 04:00 | 31.33 | 30.37
2018-04-16 04:30 | 31.91 | 30.96
2018-04-16 05:00 | 33.29 | 32.36
2018-04-16 05:30 | 35.72 | 34.84
2018-04-16 06:00 | 38.85 | 38.02
2018-04-16 06:30 | 43.8 | 42.99
2018-04-16 07:00 | 48.72 | 47.99
2018-04-16 07:30 | 53.87 | 53.05
2018-04-16 08:00 | 57.88 | 57.23
2018-04-16 08:30 | 60.51 | 59.98
2018-04-16 09:00 | 61.35 | 60.74
2018-04-16 09:30 | 62.97 | 62.22
2018-04-16 10:00 | 64.38 | 62.8
2018-04-16 10:30 | 69.64 | 62.66
2018-04-16 11:00 | 69.89 | 63.11
2018-04-16 11:30 | 78.23 | 63.53
2018-04-16 12:00 | 81.62 | 64.39
2018-04-16 12:30 | 82.3 | 65.26
2018-04-16 13:00 | 81.98 | 64.78
2018-04-16 13:30 | 82.25 | 65.3
2018-04-16 14:00 | 82.65 | 65.75
2018-04-16 14:30 | 82.73 | 65.95
2018-04-16 15:00 | 83.2 | 66.51
2018-04-16 15:30 | 67.72 | 66.22
2018-04-16 16:00 | 65.84 | 65.52
2018-04-16 16:30 | 65.94 | 65.39
2018-04-16 17:00 | 65.27 | 64.46
2018-04-16 17:30 | 60.02 | 58.69
2018-04-16 18:00 | 62.61 | 60.55
2018-04-16 18:30 | 64.09 | 62.01
2018-04-16 19:00 | 61.87 | 61.82
2018-04-16 19:30 | 58.78 | 58.77
2018-04-16 20:00 | 56.15 | 56.15
2018-04-16 20:30 | 53.13 | 53.1
2018-04-16 21:00 | 50.55 | 50.48
2018-04-16 21:30 | 48.13 | 48
2018-04-16 22:00 | 45.45 | 45.19
2018-04-16 22:30 | 43.19 | 42.82
2018-04-16 23:00 | 42.53 | 42.04
2018-04-16 23:30 | 38.77 | 38.33
2018-04-17 | 36.4 | 36.18
2018-04-17 00:30 | 35.03 | 34.98
2018-04-17 01:00 | 33.45 | 33.44
2018-04-17 01:30 | 32.97 | 32.96
2018-04-17 02:00 | 32.41 | 32.39
2018-04-17 02:30 | 32.03 | 32.01
2018-04-17 03:00 | 31.46 | 31.41
2018-04-17 03:30 | 31.15 | 31.09
2018-04-17 04:00 | 31.21 | 31.12
2018-04-17 04:30 | 31.43 | 31.33
2018-04-17 05:00 | 32.91 | 32.79
2018-04-17 05:30 | 35.53 | 35.33
2018-04-17 06:00 | 38.96 | 38.6
2018-04-17 06:30 | 44.48 | 43.76
2018-04-17 07:00 | 49.32 | 48.76
2018-04-17 07:30 | 37.42 | 36.84
2018-04-17 08:00 | 57.55 | 56.16
2018-04-17 08:30 | 59.95 | 58.98
2018-04-17 09:00 | 60.8 | 60.23
2018-04-17 09:30 | 61.63 | 61.2
2018-04-17 10:00 | 62.7 | 62.37
2018-04-17 10:30 | 63.01 | 62.75
2018-04-17 11:00 | 63 | 62.86
2018-04-17 11:30 | 62.78 | 62.67
2018-04-17 12:00 | 63.82 | 63.74
2018-04-17 12:30 | 65.23 | 65.14
2018-04-17 13:00 | 65.16 | 65.07
2018-04-17 13:30 | 66.49 | 66.42
2018-04-17 14:00 | 66.7 | 66.63
2018-04-17 14:30 | 66.99 | 66.92
2018-04-17 15:00 | 67.07 | 67
2018-04-17 15:30 | 67.04 | 66.92
2018-04-17 16:00 | 67.32 | 67.11
2018-04-17 16:30 | 67.28 | 66.82
2018-04-17 17:00 | 65.87 | 65.08
2018-04-17 17:30 | 63.93 | 62.59
2018-04-17 18:00 | 63.3 | 61.4
2018-04-17 18:30 | 64.55 | 62.57
2018-04-17 19:00 | 64.39 | 62.28
2018-04-17 19:30 | 59.44 | 59.14
2018-04-17 20:00 | 56.63 | 56.62
2018-04-17 20:30 | 53.85 | 53.82
2018-04-17 21:00 | 51.37 | 51.3
2018-04-17 21:30 | 49.56 | 49.45
2018-04-17 22:00 | 46.88 | 46.67
2018-04-17 22:30 | 43.9 | 43.56
2018-04-17 23:00 | 42.97 | 42.5
2018-04-17 23:30 | 39.78 | 39.12
2018-04-18 | 36.98 | 36.65
2018-04-18 00:30 | 35.8 | 35.65
2018-04-18 01:00 | 34.55 | 34.54
2018-04-18 01:30 | 33.79 | 33.78
2018-04-18 02:00 | 33.34 | 33.33
2018-04-18 02:30 | 32.29 | 32.28
2018-04-18 03:00 | 32.16 | 32.14
2018-04-18 03:30 | 31.88 | 31.79
2018-04-18 04:00 | 32.04 | 31.91
2018-04-18 04:30 | 33.04 | 32.87
2018-04-18 05:00 | 34.67 | 34.44
2018-04-18 05:30 | 36.87 | 36.58
2018-04-18 06:00 | 40.07 | 39.64
2018-04-18 06:30 | 45.77 | 44.92
2018-04-18 07:00 | 51.32 | 50.59
2018-04-18 07:30 | 58.27 | 57.72
2018-04-18 08:00 | 61.53 | 61.15
2018-04-18 08:30 | 63.16 | 62.51
2018-04-18 09:00 | 65.29 | 64.4
2018-04-18 09:30 | 64.72 | 63.67
2018-04-18 10:00 | 63.54 | 62.41
2018-04-18 10:30 | 64.59 | 63.3
2018-04-18 11:00 | 64.34 | 62.94
2018-04-18 11:30 | 63.99 | 62.56
2018-04-18 12:00 | 63.77 | 62.32
2018-04-18 12:30 | 64.4 | 63.03
2018-04-18 13:00 | 64.08 | 62.74
2018-04-18 13:30 | 64.73 | 63.36
2018-04-18 14:00 | 65.16 | 63.79
2018-04-18 14:30 | 65.56 | 64.23
2018-04-18 15:00 | 65.66 | 64.42
2018-04-18 15:30 | 65.57 | 64.48
2018-04-18 16:00 | 65.53 | 64.66
2018-04-18 16:30 | 64.13 | 63.61
2018-04-18 17:00 | 63 | 62.66
2018-04-18 17:30 | 60.57 | 60.44
2018-04-18 18:00 | 59.36 | 59.35
2018-04-18 18:30 | 61 | 60.98
2018-04-18 19:00 | 60.75 | 60.74
2018-04-18 19:30 | 58.33 | 58.33
2018-04-18 20:00 | 55.42 | 55.42
2018-04-18 20:30 | 52.42 | 52.39
2018-04-18 21:00 | 44.37 | 44.31
2018-04-18 21:30 | 48.63 | 48.51
2018-04-18 22:00 | 46.2 | 45.99
2018-04-18 22:30 | 43.7 | 43.35
2018-04-18 23:00 | 43.07 | 42.63
2018-04-18 23:30 | 39.61 | 38.97
2018-04-19 | 37.61 | 36.8
2018-04-19 00:30 | 36.56 | 35.56
2018-04-19 01:00 | 34.61 | 34.05
2018-04-19 01:30 | 33.46 | 33.15
2018-04-19 02:00 | 32.75 | 32.45
2018-04-19 02:30 | 31.5 | 31.46
2018-04-19 03:00 | 31.47 | 31.42
2018-04-19 03:30 | 31.55 | 31.46
2018-04-19 04:00 | 31.53 | 31.42
2018-04-19 04:30 | 32.22 | 32.1
2018-04-19 05:00 | 34 | 33.82
2018-04-19 05:30 | 36.56 | 36.27
2018-04-19 06:00 | 40.01 | 39.48
2018-04-19 06:30 | 44.96 | 44.11
2018-04-19 07:00 | 50.11 | 49.36
2018-04-19 07:30 | 56.46 | 56.04
2018-04-19 08:00 | 60.22 | 59.84
2018-04-19 08:30 | 61.68 | 61.02
2018-04-19 09:00 | 62.62 | 61.62
2018-04-19 09:30 | 62.86 | 61.78
2018-04-19 10:00 | 63.98 | 62.84
2018-04-19 10:30 | 63.96 | 62.63
2018-04-19 11:00 | 63.14 | 61.71
2018-04-19 11:30 | 63.05 | 61.56
2018-04-19 12:00 | 63.26 | 61.67
2018-04-19 12:30 | 63.99 | 62.52
2018-04-19 13:00 | 64.13 | 62.66
2018-04-19 13:30 | 65.36 | 63.96
2018-04-19 14:00 | 66.94 | 65.66
2018-04-19 14:30 | 66.82 | 65.51
2018-04-19 15:00 | 65.26 | 63.97
2018-04-19 15:30 | 64.07 | 63.07
2018-04-19 16:00 | 63.57 | 62.79
2018-04-19 16:30 | 61.56 | 61.05
2018-04-19 17:00 | 60.69 | 60.36
2018-04-19 17:30 | 58.54 | 58.46
2018-04-19 18:00 | 58.35 | 58.34
2018-04-19 18:30 | 59.8 | 59.79
2018-04-19 19:00 | 60.06 | 60.05
2018-04-19 19:30 | 57.45 | 57.45
2018-04-19 20:00 | 55.2 | 55.19
2018-04-19 20:30 | 52.77 | 52.74
2018-04-19 21:00 | 51.22 | 51.15
2018-04-19 21:30 | 48.54 | 48.4
2018-04-19 22:00 | 45.19 | 44.9
2018-04-19 22:30 | 43.09 | 42.67
2018-04-19 23:00 | 41.65 | 41.51
2018-04-19 23:30 | 38.19 | 38.06
2018-04-20 | 36.14 | 35.93
2018-04-20 00:30 | 34.83 | 34.7
2018-04-20 01:00 | 34.02 | 33.78
2018-04-20 01:30 | 33.39 | 33.16
2018-04-20 02:00 | 32.85 | 32.65
2018-04-20 02:30 | 32.24 | 32.09
2018-04-20 03:00 | 31.72 | 31.6
2018-04-20 03:30 | 31.5 | 31.4
2018-04-20 04:00 | 31.6 | 31.49
2018-04-20 04:30 | 32.29 | 32.16
2018-04-20 05:00 | 33.13 | 32.96
2018-04-20 05:30 | 35.68 | 35.41
2018-04-20 06:00 | 38.84 | 38.39
2018-04-20 06:30 | 44.53 | 43.69
2018-04-20 07:00 | 49.77 | 49.08
2018-04-20 07:30 | 56.11 | 55.41
2018-04-20 08:00 | 57.8 | 57.54
2018-04-20 08:30 | 59.72 | 59.17
2018-04-20 09:00 | 60.87 | 60.02
2018-04-20 09:30 | 61.21 | 60.21
2018-04-20 10:00 | 61.26 | 60.16
2018-04-20 10:30 | 62.04 | 60.83
2018-04-20 11:00 | 62.27 | 60.84
2018-04-20 11:30 | 61.93 | 60.46
2018-04-20 12:00 | 61.94 | 60.46
2018-04-20 12:30 | 62.41 | 61.07
2018-04-20 13:00 | 61.29 | 59.98
2018-04-20 13:30 | 61.88 | 60.6
2018-04-20 14:00 | 61.28 | 60.08
2018-04-20 14:30 | 61.4 | 60.22
2018-04-20 15:00 | 61.02 | 60
2018-04-20 15:30 | 60.35 | 59.56
2018-04-20 16:00 | 60.49 | 59.89
2018-04-20 16:30 | 60.63 | 60.25
2018-04-20 17:00 | 59.03 | 58.85
2018-04-20 17:30 | 56.72 | 56.69
2018-04-20 18:00 | 54.97 | 54.96
2018-04-20 18:30 | 55.83 | 55.81
2018-04-20 19:00 | 55.43 | 55.41
2018-04-20 19:30 | 53.23 | 53.18
2018-04-20 20:00 | 51.4 | 51.32
2018-04-20 20:30 | 48.9 | 48.75
2018-04-20 21:00 | 47.03 | 46.82
2018-04-20 21:30 | 45.59 | 45.31
2018-04-20 22:00 | 43.58 | 43.3
2018-04-20 22:30 | 41.29 | 41.2
2018-04-20 23:00 | 41.13 | 41.02
2018-04-20 23:30 | 37.94 | 37.76
2018-04-21 | 35.57 | 35.37
2018-04-21 00:30 | 34.2 | 34.14
2018-04-21 01:00 | 32.82 | 32.69
2018-04-21 01:30 | 32.35 | 32.22
2018-04-21 02:00 | 31.98 | 31.87
2018-04-21 02:30 | 31.37 | 31.29
2018-04-21 03:00 | 30.78 | 30.7
2018-04-21 03:30 | 30.4 | 30.33
2018-04-21 04:00 | 30.15 | 30.08
2018-04-21 04:30 | 30.47 | 30.4
2018-04-21 05:00 | 30.89 | 30.81
2018-04-21 05:30 | 31.75 | 31.65
2018-04-21 06:00 | 33.17 | 33.03
2018-04-21 06:30 | 35.66 | 35.44
2018-04-21 07:00 | 37.14 | 36.87
2018-04-21 07:30 | 39.3 | 38.88
2018-04-21 08:00 | 42.46 | 41.73
2018-04-21 08:30 | 44.88 | 43.77
2018-04-21 09:00 | 46.23 | 45.57
2018-04-21 09:30 | 47.05 | 46.31
2018-04-21 10:00 | 47.17 | 46.36
2018-04-21 10:30 | 46.41 | 45.49
2018-04-21 11:00 | 46.41 | 45.41
2018-04-21 11:30 | 46.1 | 45.05
2018-04-21 12:00 | 45.31 | 44.38
2018-04-21 12:30 | 43.96 | 43.32
2018-04-21 13:00 | 42.04 | 41.44
2018-04-21 13:30 | 41.97 | 41.33
2018-04-21 14:00 | 42.28 | 41.68
2018-04-21 14:30 | 42.1 | 41.59
2018-04-21 15:00 | 42.84 | 42.37
2018-04-21 15:30 | 42.96 | 42.58
2018-04-21 16:00 | 44.05 | 43.73
2018-04-21 16:30 | 45.49 | 45.25
2018-04-21 17:00 | 45.85 | 45.66
2018-04-21 17:30 | 46.48 | 46.34
2018-04-21 18:00 | 47.66 | 47.53
2018-04-21 18:30 | 49.71 | 49.55
2018-04-21 19:00 | 49.24 | 49.09
2018-04-21 19:30 | 47.09 | 46.97
2018-04-21 20:00 | 45.13 | 45.04
2018-04-21 20:30 | 43.29 | 43.23
2018-04-21 21:00 | 42.15 | 42.11
2018-04-21 21:30 | 40.9 | 40.88
2018-04-21 22:00 | 39.11 | 39.1
2018-04-21 22:30 | 37.69 | 37.69
2018-04-21 23:00 | 37.82 | 37.81
2018-04-21 23:30 | 35.05 | 35.04
2018-04-22 | 33.56 | 33.53
2018-04-22 00:30 | 32.62 | 32.55
2018-04-22 01:00 | 31.38 | 31.31
2018-04-22 01:30 | 30.82 | 30.74
2018-04-22 02:00 | 30.54 | 30.47
2018-04-22 02:30 | 30.07 | 30.02
2018-04-22 03:00 | 29.67 | 29.63
2018-04-22 03:30 | 29.4 | 29.36
2018-04-22 04:00 | 29.33 | 29.29
2018-04-22 04:30 | 29.51 | 29.47
2018-04-22 05:00 | 29.57 | 29.53
2018-04-22 05:30 | 30.33 | 30.26
2018-04-22 06:00 | 30.86 | 30.79
2018-04-22 06:30 | 31.59 | 31.54
2018-04-22 07:00 | 32.4 | 32.34
2018-04-22 07:30 | 33.75 | 33.63
2018-04-22 08:00 | 35.55 | 35.3
2018-04-22 08:30 | 37.05 | 36.68
2018-04-22 09:00 | 38.42 | 37.83
2018-04-22 09:30 | 39.3 | 39.02
2018-04-22 10:00 | 39.36 | 39.12
2018-04-22 10:30 | 39.23 | 38.96
2018-04-22 11:00 | 39.27 | 38.96
2018-04-22 11:30 | 39 | 38.68
2018-04-22 12:00 | 38.37 | 38.04
2018-04-22 12:30 | 39.69 | 39.37
2018-04-22 13:00 | 38.68 | 38.36
2018-04-22 13:30 | 38.56 | 38.24
2018-04-22 14:00 | 38.89 | 38.59
2018-04-22 14:30 | 38.71 | 38.48
2018-04-22 15:00 | 39.02 | 38.81
2018-04-22 15:30 | 39.53 | 39.37
2018-04-22 16:00 | 40.76 | 40.64
2018-04-22 16:30 | 42.34 | 42.25
2018-04-22 17:00 | 43.23 | 43.16
2018-04-22 17:30 | 45.1 | 45.05
2018-04-22 18:00 | 47.11 | 47.05
2018-04-22 18:30 | 50.2 | 50.08
2018-04-22 19:00 | 50.09 | 49.98
2018-04-22 19:30 | 48.04 | 47.93
2018-04-22 20:00 | 45.92 | 45.85
2018-04-22 20:30 | 43.47 | 43.44
2018-04-22 21:00 | 41.88 | 41.86
2018-04-22 21:30 | 40.28 | 40.28
2018-04-22 22:00 | 38.37 | 38.37
2018-04-22 22:30 | 36.22 | 36.21
2018-04-22 23:00 | 36.12 | 36.1
2018-04-22 23:30 | 33.19 | 33.13
2018-04-23 | 31.52 | 31.45
2018-04-23 00:30 | 31 | 30.95
2018-04-23 01:00 | 29.74 | 29.7
2018-04-23 01:30 | 29.6 | 29.57
2018-04-23 02:00 | 29.27 | 29.24
2018-04-23 02:30 | 29.06 | 29.04
2018-04-23 03:00 | 28.85 | 28.83
2018-04-23 03:30 | 28.8 | 28.79
2018-04-23 04:00 | 29.04 | 29.02
2018-04-23 04:30 | 29.9 | 29.87
2018-04-23 05:00 | 31.54 | 31.46
2018-04-23 05:30 | 33.64 | 33.49
2018-04-23 06:00 | 36.89 | 36.6
2018-04-23 06:30 | 42.01 | 41.43
2018-04-23 07:00 | 46.48 | 45.91
2018-04-23 07:30 | 52 | 51.24
2018-04-23 08:00 | 54.99 | 54.05
2018-04-23 08:30 | 56.2 | 55.28
2018-04-23 09:00 | 58.2 | 57.19
2018-04-23 09:30 | 57.45 | 56.74
2018-04-23 10:00 | 57.41 | 56.59
2018-04-23 10:30 | 57.43 | 56.53
2018-04-23 11:00 | 58 | 57
2018-04-23 11:30 | 57.92 | 56.82
2018-04-23 12:00 | 58.72 | 57.49
2018-04-23 12:30 | 59.43 | 58.24
2018-04-23 13:00 | 58.5 | 57.37
2018-04-23 13:30 | 58.57 | 57.41
2018-04-23 14:00 | 58.73 | 57.57
2018-04-23 14:30 | 59.28 | 58.14
2018-04-23 15:00 | 59.01 | 58
2018-04-23 15:30 | 58.67 | 57.84
2018-04-23 16:00 | 58.92 | 58.23
2018-04-23 16:30 | 48.23 | 47.3
2018-04-23 17:00 | 58.53 | 58.31
2018-04-23 17:30 | 56.46 | 56.43
2018-04-23 18:00 | 55.74 | 55.73
2018-04-23 18:30 | 57.33 | 57.32
2018-04-23 19:00 | 56.87 | 56.86
2018-04-23 19:30 | 54.21 | 54.19
2018-04-23 20:00 | 51.7 | 51.65
2018-04-23 20:30 | 49.48 | 49.38
2018-04-23 21:00 | 47.45 | 47.31
2018-04-23 21:30 | 45.24 | 45
2018-04-23 22:00 | 42.99 | 42.6
2018-04-23 22:30 | 40.75 | 40.13
2018-04-23 23:00 | 40.31 | 39.59
2018-04-23 23:30 | 36.44 | 35.97
2018-04-24 | 34.46 | 34.14
2018-04-24 00:30 | 33.84 | 33.46
2018-04-24 01:00 | 32.26 | 31.82
2018-04-24 01:30 | 31.79 | 31.33
2018-04-24 02:00 | 31.38 | 30.92
2018-04-24 02:30 | 30.1 | 30.03
2018-04-24 03:00 | 29.4 | 29.33
2018-04-24 03:30 | 29.4 | 29.34
2018-04-24 04:00 | 29.25 | 29.2
2018-04-24 04:30 | 29.86 | 29.78
2018-04-24 05:00 | 31.12 | 30.99
2018-04-24 05:30 | 33.81 | 33.6
2018-04-24 06:00 | 37.07 | 36.7
2018-04-24 06:30 | 42.12 | 41.44
2018-04-24 07:00 | 46.65 | 46.22
2018-04-24 07:30 | 52.79 | 51.81
2018-04-24 08:00 | 55.45 | 54.26
2018-04-24 08:30 | 54.58 | 54.34
2018-04-24 09:00 | 55.92 | 55.43
2018-04-24 09:30 | 56.79 | 56.1
2018-04-24 10:00 | 57.4 | 56.54
2018-04-24 10:30 | 58.68 | 57.59
2018-04-24 11:00 | 59.16 | 58
2018-04-24 11:30 | 59.49 | 58.18
2018-04-24 12:00 | 59.64 | 58.32
2018-04-24 12:30 | 60.07 | 58.8
2018-04-24 13:00 | 59.33 | 58.05
2018-04-24 13:30 | 59.57 | 58.29
2018-04-24 14:00 | 60.35 | 59.02
2018-04-24 14:30 | 60.89 | 59.61
2018-04-24 15:00 | 60.93 | 59.66
2018-04-24 15:30 | 60.64 | 59.61
2018-04-24 16:00 | 61.11 | 60.29
2018-04-24 16:30 | 60.46 | 59.96
2018-04-24 17:00 | 58.97 | 58.71
2018-04-24 17:30 | 56.99 | 56.93
2018-04-24 18:00 | 54.98 | 54.98
2018-04-24 18:30 | 55.86 | 55.86
2018-04-24 19:00 | 55.42 | 55.41
2018-04-24 19:30 | 52.61 | 52.58
2018-04-24 20:00 | 50.7 | 50.65
2018-04-24 20:30 | 48.02 | 47.89
2018-04-24 21:00 | 46.3 | 46.12
2018-04-24 21:30 | 44.38 | 44.12
2018-04-24 22:00 | 42.53 | 42.1
2018-04-24 22:30 | 40.57 | 39.99
2018-04-24 23:00 | 40.26 | 39.54
2018-04-24 23:30 | 37.25 | 36.46
2018-04-25 | 34.16 | 33.8
2018-04-25 00:30 | 33.38 | 32.92
2018-04-25 01:00 | 32.1 | 31.57
2018-04-25 01:30 | 30.52 | 30.34
2018-04-25 02:00 | 29.63 | 29.56
2018-04-25 02:30 | 29.17 | 29.14
2018-04-25 03:00 | 28.56 | 28.54
2018-04-25 03:30 | 28.23 | 28.21
2018-04-25 04:00 | 28.26 | 28.24
2018-04-25 04:30 | 28.53 | 28.51
2018-04-25 05:00 | 28.76 | 28.73
2018-04-25 05:30 | 29.27 | 29.23
2018-04-25 06:00 | 29.97 | 29.94
2018-04-25 06:30 | 31.2 | 31.17
2018-04-25 07:00 | 32.34 | 32.31
2018-04-25 07:30 | 32.92 | 32.85
2018-04-25 08:00 | 32.7 | 32.58
2018-04-25 08:30 | 33.02 | 32.78
2018-04-25 09:00 | 33.04 | 32.68
2018-04-25 09:30 | 33.17 | 32.7
2018-04-25 10:00 | 33.87 | 33.23
2018-04-25 10:30 | 34.61 | 33.83
2018-04-25 11:00 | 34.61 | 33.73
2018-04-25 11:30 | 35.16 | 34.18
2018-04-25 12:00 | 35.31 | 34.94
2018-04-25 12:30 | 36.63 | 36.37
2018-04-25 13:00 | 35.59 | 35.34
2018-04-25 13:30 | 35.69 | 35.45
2018-04-25 14:00 | 36.14 | 35.89
2018-04-25 14:30 | 36.68 | 36.45
2018-04-25 15:00 | 37.62 | 37.4
2018-04-25 15:30 | 38.56 | 38.38
2018-04-25 16:00 | 40.19 | 40.03
2018-04-25 16:30 | 42.54 | 42.39
2018-04-25 17:00 | 43.5 | 43.38
2018-04-25 17:30 | 44.83 | 44.75
2018-04-25 18:00 | 46.88 | 46.8
2018-04-25 18:30 | 49.64 | 49.54
2018-04-25 19:00 | 49.53 | 49.44
2018-04-25 19:30 | 47.2 | 47.14
2018-04-25 20:00 | 45.2 | 45.16
2018-04-25 20:30 | 42.58 | 42.57
2018-04-25 21:00 | 40.61 | 40.61
2018-04-25 21:30 | 39.11 | 39.11
2018-04-25 22:00 | 37.22 | 37.21
2018-04-25 22:30 | 34.99 | 34.94
2018-04-25 23:00 | 35.07 | 35.01
2018-04-25 23:30 | 32.29 | 32.25
2018-04-26 | 30.84 | 30.8
2018-04-26 00:30 | 30.38 | 30.35
2018-04-26 01:00 | 29.01 | 28.99
2018-04-26 01:30 | 28.66 | 28.65
2018-04-26 02:00 | 28.55 | 28.53
2018-04-26 02:30 | 28.11 | 28.1
2018-04-26 03:00 | 28.06 | 28.05
2018-04-26 03:30 | 28 | 28
2018-04-26 04:00 | 28.59 | 28.58
2018-04-26 04:30 | 29.07 | 29.05
2018-04-26 05:00 | 30.43 | 30.4
2018-04-26 05:30 | 33.06 | 32.95
2018-04-26 06:00 | 36.29 | 36.03
2018-04-26 06:30 | 41.37 | 40.85
2018-04-26 07:00 | 46.15 | 45.55
2018-04-26 07:30 | 51.27 | 50.66
2018-04-26 08:00 | 53.87 | 52.84
2018-04-26 08:30 | 54.08 | 53.77
2018-04-26 09:00 | 53.95 | 53.63
2018-04-26 09:30 | 54.07 | 53.63
2018-04-26 10:00 | 54.52 | 53.95
2018-04-26 10:30 | 55.8 | 55.03
2018-04-26 11:00 | 56.7 | 55.74
2018-04-26 11:30 | 57.16 | 56.11
2018-04-26 12:00 | 55.83 | 54.95
2018-04-26 12:30 | 57.58 | 56.68
2018-04-26 13:00 | 58.07 | 57.09
2018-04-26 13:30 | 60.87 | 59.67
2018-04-26 14:00 | 61.21 | 61.09
2018-04-26 14:30 | 61.81 | 61.72
2018-04-26 15:00 | 61.95 | 61.84
2018-04-26 15:30 | 61.22 | 60.96
2018-04-26 16:00 | 61.6 | 61.22
2018-04-26 16:30 | 61.96 | 61.3
2018-04-26 17:00 | 60.9 | 59.83
2018-04-26 17:30 | 59.58 | 57.69
2018-04-26 18:00 | 59.36 | 57.42
2018-04-26 18:30 | 59.25 | 58.74
2018-04-26 19:00 | 58.88 | 58.28
2018-04-26 19:30 | 56.09 | 55.31
2018-04-26 20:00 | 53.92 | 52.93
2018-04-26 20:30 | 51.5 | 50.17
2018-04-26 21:00 | 49.68 | 48.02
2018-04-26 21:30 | 45.88 | 44.96
2018-04-26 22:00 | 41.52 | 41.46
2018-04-26 22:30 | 39.43 | 39.4
2018-04-26 23:00 | 38.89 | 38.87
2018-04-26 23:30 | 35.74 | 35.49
2018-04-27 | 32.53 | 32.33
2018-04-27 00:30 | 31.95 | 31.78
2018-04-27 01:00 | 30.64 | 30.49
2018-04-27 01:30 | 29.74 | 29.61
2018-04-27 02:00 | 28.81 | 28.73
2018-04-27 02:30 | 28.58 | 28.51
2018-04-27 03:00 | 28.09 | 28.04
2018-04-27 03:30 | 27.8 | 27.77
2018-04-27 04:00 | 27.81 | 27.79
2018-04-27 04:30 | 28.58 | 28.54
2018-04-27 05:00 | 31.25 | 31.17
2018-04-27 05:30 | 33.1 | 32.95
2018-04-27 06:00 | 35.87 | 35.59
2018-04-27 06:30 | 40.72 | 40.2
2018-04-27 07:00 | 45.13 | 44.82
2018-04-27 07:30 | 49.42 | 48.86
2018-04-27 08:00 | 51.64 | 50.7
2018-04-27 08:30 | 52.26 | 51.27
2018-04-27 09:00 | 52.86 | 51.32
2018-04-27 09:30 | 52.92 | 51.54
2018-04-27 10:00 | 52.94 | 51.78
2018-04-27 10:30 | 53.07 | 52.13
2018-04-27 11:00 | 53.15 | 52.37
2018-04-27 11:30 | 53.41 | 52.77
2018-04-27 12:00 | 54.28 | 53.75
2018-04-27 12:30 | 55.55 | 55.06
2018-04-27 13:00 | 55.26 | 54.91
2018-04-27 13:30 | 58.04 | 57.74
2018-04-27 14:00 | 58.2 | 57.87
2018-04-27 14:30 | 58.49 | 58.11
2018-04-27 15:00 | 58.52 | 58.07
2018-04-27 15:30 | 58.88 | 58.29
2018-04-27 16:00 | 60.13 | 59.45
2018-04-27 16:30 | 60.97 | 60.04
2018-04-27 17:00 | 60.67 | 59.31
2018-04-27 17:30 | 59.63 | 57.57
2018-04-27 18:00 | 57.74 | 55.06
2018-04-27 18:30 | 54.89 | 54.02
2018-04-27 19:00 | 54.58 | 53.63
2018-04-27 19:30 | 52.35 | 51.25
2018-04-27 20:00 | 50.64 | 49.33
2018-04-27 20:30 | 48.83 | 47.22
2018-04-27 21:00 | 47.3 | 45.38
2018-04-27 21:30 | 45.88 | 43.63
2018-04-27 22:00 | 41.3 | 41.13
2018-04-27 22:30 | 39.23 | 39.2
2018-04-27 23:00 | 39.26 | 39.25
2018-04-27 23:30 | 36.28 | 36.17
2018-04-28 | 34.74 | 34.48
2018-04-28 00:30 | 33.76 | 33.52
2018-04-28 01:00 | 31.97 | 31.78
2018-04-28 01:30 | 31.09 | 30.94
2018-04-28 02:00 | 30.16 | 30.05
2018-04-28 02:30 | 29.72 | 29.62
2018-04-28 03:00 | 29.35 | 29.27
2018-04-28 03:30 | 29.13 | 29.07
2018-04-28 04:00 | 28.75 | 28.69
2018-04-28 04:30 | 29.43 | 29.35
2018-04-28 05:00 | 35.09 | 34.98
2018-04-28 05:30 | 35.72 | 35.6
2018-04-28 06:00 | 37.33 | 37.16
2018-04-28 06:30 | 39.75 | 39.53
2018-04-28 07:00 | 41.54 | 41.27
2018-04-28 07:30 | 44.64 | 44.24
2018-04-28 08:00 | 48.08 | 47.37
2018-04-28 08:30 | 50.58 | 49.93
2018-04-28 09:00 | 50.38 | 49.93
2018-04-28 09:30 | 50.33 | 49.51
2018-04-28 10:00 | 48.35 | 47.41
2018-04-28 10:30 | 48.92 | 48.12
2018-04-28 11:00 | 48.97 | 48.19
2018-04-28 11:30 | 46.95 | 46.08
2018-04-28 12:00 | 48.44 | 47.63
2018-04-28 12:30 | 46.95 | 45.89
2018-04-28 13:00 | 42.6 | 41.29
2018-04-28 13:30 | 41.09 | 39.66
2018-04-28 14:00 | 41.28 | 39.75
2018-04-28 14:30 | 41.51 | 39.82
2018-04-28 15:00 | 42.11 | 40.36
2018-04-28 15:30 | 42.68 | 40.82
2018-04-28 16:00 | 43.86 | 41.88
2018-04-28 16:30 | 45.32 | 43.18
2018-04-28 17:00 | 46.21 | 43.97
2018-04-28 17:30 | 47.19 | 44.7
2018-04-28 18:00 | 48.44 | 46.11
2018-04-28 18:30 | 50.02 | 47.93
2018-04-28 19:00 | 48.95 | 46.7
2018-04-28 19:30 | 47.32 | 44.86
2018-04-28 20:00 | 45.99 | 43.32
2018-04-28 20:30 | 41.78 | 41.04
2018-04-28 21:00 | 39.89 | 39.88
2018-04-28 21:30 | 38.64 | 38.63
2018-04-28 22:00 | 37.57 | 37.57
2018-04-28 22:30 | 36.24 | 36.24
2018-04-28 23:00 | 36.82 | 36.82
2018-04-28 23:30 | 34.43 | 34.41
2018-04-29 | 32.91 | 32.89
2018-04-29 00:30 | 31.9 | 31.83
2018-04-29 01:00 | 30.65 | 30.58
2018-04-29 01:30 | 30.54 | 30.46
2018-04-29 02:00 | 29.99 | 29.92
2018-04-29 02:30 | 29.63 | 29.58
2018-04-29 03:00 | 29.53 | 29.48
2018-04-29 03:30 | 29.3 | 29.26
2018-04-29 04:00 | 29.3 | 29.25
2018-04-29 04:30 | 29.57 | 29.5
2018-04-29 05:00 | 29.48 | 29.42
2018-04-29 05:30 | 29.87 | 29.81
2018-04-29 06:00 | 30.54 | 30.47
2018-04-29 06:30 | 31.43 | 31.37
2018-04-29 07:00 | 32.2 | 32.13
2018-04-29 07:30 | 33.45 | 33.34
2018-04-29 08:00 | 35.03 | 34.8
2018-04-29 08:30 | 36.37 | 36.02
2018-04-29 09:00 | 37.5 | 36.97
2018-04-29 09:30 | 37.74 | 37.09
2018-04-29 10:00 | 37.94 | 37.15
2018-04-29 10:30 | 37.68 | 37.16
2018-04-29 11:00 | 36.87 | 36.59
2018-04-29 11:30 | 36.58 | 36.27
2018-04-29 12:00 | 35.79 | 35.52
2018-04-29 12:30 | 36.92 | 36.67
2018-04-29 13:00 | 35.63 | 35.41
2018-04-29 13:30 | 35.39 | 35.18
2018-04-29 14:00 | 35.85 | 35.65
2018-04-29 14:30 | 35.76 | 35.61
2018-04-29 15:00 | 36.72 | 36.58
2018-04-29 15:30 | 37.71 | 37.6
2018-04-29 16:00 | 39.03 | 38.94
2018-04-29 16:30 | 41.18 | 41.11
2018-04-29 17:00 | 42.27 | 42.21
2018-04-29 17:30 | 43.5 | 43.47
2018-04-29 18:00 | 46.14 | 46.1
2018-04-29 18:30 | 49.34 | 49.24
2018-04-29 19:00 | 49.02 | 48.94
2018-04-29 19:30 | 46.18 | 46.13
2018-04-29 20:00 | 44.51 | 44.47
2018-04-29 20:30 | 42.26 | 42.25
2018-04-29 21:00 | 40.71 | 40.7
2018-04-29 21:30 | 39.47 | 39.47
2018-04-29 22:00 | 37.47 | 37.47
2018-04-29 22:30 | 35.24 | 35.17
2018-04-29 23:00 | 35.3 | 35.17
2018-04-29 23:30 | 32.5 | 32.39
2018-04-30 | 30.97 | 30.89
2018-04-30 00:30 | 30.21 | 30.15
2018-04-30 01:00 | 29.38 | 29.33
2018-04-30 01:30 | 29.15 | 29.11
2018-04-30 02:00 | 29.16 | 29.11
2018-04-30 02:30 | 28.57 | 28.53
2018-04-30 03:00 | 28.38 | 28.35
2018-04-30 03:30 | 29.11 | 29.06
2018-04-30 04:00 | 29.23 | 29.18
2018-04-30 04:30 | 29.76 | 29.7
2018-04-30 05:00 | 30.77 | 30.67
2018-04-30 05:30 | 34.25 | 34.01
2018-04-30 06:00 | 37.74 | 37.32
2018-04-30 06:30 | 42.71 | 41.95
2018-04-30 07:00 | 47.43 | 46.86
2018-04-30 07:30 | 52.52 | 51.77
2018-04-30 08:00 | 54.48 | 53.47
2018-04-30 08:30 | 54.73 | 54.45
2018-04-30 09:00 | 55.14 | 54.72
2018-04-30 09:30 | 54.93 | 54.41
2018-04-30 10:00 | 52.39 | 51.65
2018-04-30 10:30 | 42.68 | 41.07
2018-04-30 11:00 | 55.75 | 54.85
2018-04-30 11:30 | 55.79 | 54.82
2018-04-30 12:00 | 56.09 | 55.1
2018-04-30 12:30 | 57.6 | 56.61
2018-04-30 13:00 | 56.08 | 55.14
2018-04-30 13:30 | 55.99 | 55.05
2018-04-30 14:00 | 55.87 | 54.94
2018-04-30 14:30 | 55.98 | 55.06
2018-04-30 15:00 | 56.28 | 55.43
2018-04-30 15:30 | 56.56 | 55.85
2018-04-30 16:00 | 56.95 | 56.43
2018-04-30 16:30 | 57.89 | 57.58
2018-04-30 17:00 | 57.41 | 57.25
2018-04-30 17:30 | 55.49 | 55.48
2018-04-30 18:00 | 55.46 | 55.46
2018-04-30 18:30 | 57.76 | 57.76
2018-04-30 19:00 | 56.98 | 56.97
2018-04-30 19:30 | 53.87 | 53.84
2018-04-30 20:00 | 51.05 | 50.97
2018-04-30 20:30 | 48.67 | 48.54
2018-04-30 21:00 | 46.81 | 46.63
2018-04-30 21:30 | 44.69 | 44.4
2018-04-30 22:00 | 42.29 | 41.86
2018-04-30 22:30 | 39.89 | 39.29
2018-04-30 23:00 | 39.57 | 39.18
2018-04-30 23:30 | 36.23 | 36.08
2018-05-01 | 34.32 | 34.11
2018-05-01 00:30 | 33.24 | 32.94
2018-05-01 01:00 | 32.72 | 32.42
2018-05-01 01:30 | 32.4 | 32.09
2018-05-01 02:00 | 30.82 | 30.66
2018-05-01 02:30 | 30.45 | 30.34
2018-05-01 03:00 | 30.07 | 29.97
2018-05-01 03:30 | 30.41 | 30.29
2018-05-01 04:00 | 30.43 | 30.32
2018-05-01 04:30 | 30.74 | 30.63
2018-05-01 05:00 | 31.97 | 31.83
2018-05-01 05:30 | 34.69 | 34.45
2018-05-01 06:00 | 37.81 | 37.59
2018-05-01 06:30 | 43.08 | 42.91
2018-05-01 07:00 | 48.22 | 47.8
2018-05-01 07:30 | 54.41 | 53.49
2018-05-01 08:00 | 56.41 | 56.03
2018-05-01 08:30 | 55.4 | 55.16
2018-05-01 09:00 | 55.76 | 55.36
2018-05-01 09:30 | 55.54 | 54.92
2018-05-01 10:00 | 55.62 | 54.88
2018-05-01 10:30 | 55.45 | 54.83
2018-05-01 11:00 | 54.89 | 54.34
2018-05-01 11:30 | 55.47 | 55.03
2018-05-01 12:00 | 55.07 | 54.65
2018-05-01 12:30 | 55.96 | 55.55
2018-05-01 13:00 | 55.61 | 55.16
2018-05-01 13:30 | 55.6 | 55.18
2018-05-01 14:00 | 56.29 | 55.93
2018-05-01 14:30 | 56.77 | 56.36
2018-05-01 15:00 | 56.57 | 56.12
2018-05-01 15:30 | 57.34 | 56.8
2018-05-01 16:00 | 58.11 | 57.41
2018-05-01 16:30 | 58.33 | 57.24
2018-05-01 17:00 | 58.26 | 56.63
2018-05-01 17:30 | 57.4 | 54.8
2018-05-01 18:00 | 57.9 | 54.78
2018-05-01 18:30 | 59.35 | 56.14
2018-05-01 19:00 | 58.91 | 55.63
2018-05-01 19:30 | 56.43 | 52.56
2018-05-01 20:00 | 54.61 | 50.26
2018-05-01 20:30 | 48.67 | 47.27
2018-05-01 21:00 | 45.34 | 45.03
2018-05-01 21:30 | 43.16 | 42.71
2018-05-01 22:00 | 41.38 | 40.78
2018-05-01 22:30 | 39.33 | 38.53
2018-05-01 23:00 | 37.41 | 37.12
2018-05-01 23:30 | 36.06 | 35.83
2018-05-02 | 34.31 | 34.06
2018-05-02 00:30 | 33.27 | 33.05
2018-05-02 01:00 | 32.23 | 32.02
2018-05-02 01:30 | 31.66 | 31.46
2018-05-02 02:00 | 31 | 30.83
2018-05-02 02:30 | 30.11 | 30.01
2018-05-02 03:00 | 30.12 | 30.02
2018-05-02 03:30 | 29.85 | 29.76
2018-05-02 04:00 | 29.95 | 29.87
2018-05-02 04:30 | 30.86 | 30.75
2018-05-02 05:00 | 31.83 | 31.7
2018-05-02 05:30 | 34 | 33.79
2018-05-02 06:00 | 37.5 | 37.13
2018-05-02 06:30 | 43.03 | 42.59
2018-05-02 07:00 | 47.47 | 47.45
2018-05-02 07:30 | 53.23 | 53.03
2018-05-02 08:00 | 55.82 | 55.39
2018-05-02 08:30 | 56.32 | 56.09
2018-05-02 09:00 | 55.45 | 55.07
2018-05-02 09:30 | 55.44 | 54.98
2018-05-02 10:00 | 56.46 | 55.93
2018-05-02 10:30 | 56.94 | 56.26
2018-05-02 11:00 | 58.79 | 57.97
2018-05-02 11:30 | 60.54 | 59.7
2018-05-02 12:00 | 60.45 | 59.68
2018-05-02 12:30 | 60.29 | 59.68
2018-05-02 13:00 | 58.12 | 57.61
2018-05-02 13:30 | 58.01 | 57.49
2018-05-02 14:00 | 57.64 | 57.06
2018-05-02 14:30 | 58.8 | 58.24
2018-05-02 15:00 | 57.87 | 57.32
2018-05-02 15:30 | 56.99 | 56.51
2018-05-02 16:00 | 55.99 | 55.71
2018-05-02 16:30 | 49.71 | 49.54
2018-05-02 17:00 | 54.61 | 54.57
2018-05-02 17:30 | 53.58 | 53.58
2018-05-02 18:00 | 54.83 | 54.82
2018-05-02 18:30 | 55.7 | 55.68
2018-05-02 19:00 | 54.73 | 54.7
2018-05-02 19:30 | 52.42 | 52.37
2018-05-02 20:00 | 50.56 | 50.48
2018-05-02 20:30 | 48.07 | 47.92
2018-05-02 21:00 | 45.65 | 45.41
2018-05-02 21:30 | 43.42 | 43.04
2018-05-02 22:00 | 41.52 | 41.01
2018-05-02 22:30 | 39.45 | 38.77
2018-05-02 23:00 | 39.04 | 38.84
2018-05-02 23:30 | 35.96 | 35.75
2018-05-03 | 34.42 | 34.14
2018-05-03 00:30 | 33.16 | 32.93
2018-05-03 01:00 | 31.61 | 31.4
2018-05-03 01:30 | 30.94 | 30.76
2018-05-03 02:00 | 30.36 | 30.19
2018-05-03 02:30 | 29.61 | 29.51
2018-05-03 03:00 | 29.67 | 29.56
2018-05-03 03:30 | 29.4 | 29.3
2018-05-03 04:00 | 29.54 | 29.45
2018-05-03 04:30 | 30.44 | 30.33
2018-05-03 05:00 | 31.65 | 31.51
2018-05-03 05:30 | 34.56 | 34.28
2018-05-03 06:00 | 38.12 | 37.65
2018-05-03 06:30 | 43.33 | 42.6
2018-05-03 07:00 | 48.43 | 47.91
2018-05-03 07:30 | 53.24 | 52.66
2018-05-03 08:00 | 55.91 | 55.51
2018-05-03 08:30 | 56.72 | 56.42
2018-05-03 09:00 | 56.18 | 55.71
2018-05-03 09:30 | 55.91 | 55.33
2018-05-03 10:00 | 55.89 | 55.28
2018-05-03 10:30 | 56.57 | 56.07
2018-05-03 11:00 | 57.1 | 56.73
2018-05-03 11:30 | 56.59 | 56.26
2018-05-03 12:00 | 57.28 | 56.99
2018-05-03 12:30 | 58.07 | 57.77
2018-05-03 13:00 | 56.49 | 56.08
2018-05-03 13:30 | 56.89 | 56.51
2018-05-03 14:00 | 57.79 | 57.46
2018-05-03 14:30 | 57.67 | 57.28
2018-05-03 15:00 | 58.47 | 58.05
2018-05-03 15:30 | 58.14 | 57.6
2018-05-03 16:00 | 58.71 | 58
2018-05-03 16:30 | 59.44 | 58.4
2018-05-03 17:00 | 59.05 | 57.67
2018-05-03 17:30 | 58.04 | 55.84
2018-05-03 18:00 | 58.83 | 56.25
2018-05-03 18:30 | 60.97 | 58.4
2018-05-03 19:00 | 60.38 | 57.67
2018-05-03 19:30 | 58.34 | 55.33
2018-05-03 20:00 | 56.29 | 52.83
2018-05-03 20:30 | 54.13 | 50.11
2018-05-03 21:00 | 52.22 | 47.76
2018-05-03 21:30 | 50.13 | 44.84
2018-05-03 22:00 | 48.06 | 41.91
2018-05-03 22:30 | 42.63 | 39.39
2018-05-03 23:00 | 40 | 39.39
2018-05-03 23:30 | 35.94 | 35.74
2018-05-04 | 34.8 | 33.77
2018-05-04 00:30 | 35.25 | 32.7
2018-05-04 01:00 | 33.83 | 31.14
2018-05-04 01:30 | 33.09 | 30.31
2018-05-04 02:00 | 32.52 | 29.67
2018-05-04 02:30 | 32.02 | 29.08
2018-05-04 03:00 | 31.79 | 28.83
2018-05-04 03:30 | 31.89 | 28.93
2018-05-04 04:00 | 32.01 | 29.07
2018-05-04 04:30 | 28.45 | 25.15
2018-05-04 05:00 | 33.91 | 31.2
2018-05-04 05:30 | 36.01 | 33.53
2018-05-04 06:00 | 38.91 | 36.7
2018-05-04 06:30 | 43.43 | 41.55
2018-05-04 07:00 | 47.61 | 45.84
2018-05-04 07:30 | 52.13 | 49.69
2018-05-04 08:00 | 59.04 | 52.7
2018-05-04 08:30 | 60.46 | 53.87
2018-05-04 09:00 | 60.96 | 54.61
2018-05-04 09:30 | 61.33 | 55.11
2018-05-04 10:00 | 61.71 | 55.6
2018-05-04 10:30 | 62.9 | 57
2018-05-04 11:00 | 60.1 | 56.53
2018-05-04 11:30 | 60.99 | 57.61
2018-05-04 12:00 | 60.23 | 56.81
2018-05-04 12:30 | 63 | 59.76
2018-05-04 13:00 | 62.15 | 58.81
2018-05-04 13:30 | 61.03 | 57.59
2018-05-04 14:00 | 59.98 | 56.42
2018-05-04 14:30 | 58.57 | 54.91
2018-05-04 15:00 | 59.73 | 56.12
2018-05-04 15:30 | 59.92 | 56.26
2018-05-04 16:00 | 57.5 | 55.8
2018-05-04 16:30 | 57.94 | 56.31
2018-05-04 17:00 | 56.5 | 54.78
2018-05-04 17:30 | 55.41 | 53.61
2018-05-04 18:00 | 54.99 | 53.1
2018-05-04 18:30 | 55.73 | 53.84
2018-05-04 19:00 | 54.43 | 52.49
2018-05-04 19:30 | 52.59 | 50.57
2018-05-04 20:00 | 51.19 | 49.08
2018-05-04 20:30 | 49.2 | 46.97
2018-05-04 21:00 | 47.08 | 45.28
2018-05-04 21:30 | 43.99 | 43.65
2018-05-04 22:00 | 41.76 | 41.55
2018-05-04 22:30 | 39.32 | 39.17
2018-05-04 23:00 | 39.21 | 39.01
2018-05-04 23:30 | 36.31 | 36.03
2018-05-05 | 34.05 | 33.87
2018-05-05 00:30 | 32.9 | 32.82
2018-05-05 01:00 | 31.54 | 31.43
2018-05-05 01:30 | 30.93 | 30.82
2018-05-05 02:00 | 30.22 | 30.13
2018-05-05 02:30 | 29.76 | 29.69
2018-05-05 03:00 | 29.21 | 29.16
2018-05-05 03:30 | 28.79 | 28.75
2018-05-05 04:00 | 28.69 | 28.66
2018-05-05 04:30 | 29.02 | 28.98
2018-05-05 05:00 | 29.1 | 29.06
2018-05-05 05:30 | 30.28 | 30.21
2018-05-05 06:00 | 31.79 | 31.69
2018-05-05 06:30 | 33.52 | 33.37
2018-05-05 07:00 | 35 | 34.83
2018-05-05 07:30 | 37.1 | 36.78
2018-05-05 08:00 | 38.93 | 38.43
2018-05-05 08:30 | 40.81 | 40.08
2018-05-05 09:00 | 42.12 | 41.12
2018-05-05 09:30 | 42.72 | 42.17
2018-05-05 10:00 | 42.94 | 42.39
2018-05-05 10:30 | 43.06 | 42.42
2018-05-05 11:00 | 39.73 | 38.91
2018-05-05 11:30 | 42.28 | 41.56
2018-05-05 12:00 | 41.22 | 40.55
2018-05-05 12:30 | 40.55 | 40.02
2018-05-05 13:00 | 39.31 | 38.83
2018-05-05 13:30 | 38.85 | 38.42
2018-05-05 14:00 | 38.99 | 38.61
2018-05-05 14:30 | 38.49 | 38.18
2018-05-05 15:00 | 39.08 | 38.8
2018-05-05 15:30 | 39.74 | 39.51
2018-05-05 16:00 | 40.79 | 40.6
2018-05-05 16:30 | 41.87 | 41.75
2018-05-05 17:00 | 42.74 | 42.64
2018-05-05 17:30 | 43.97 | 43.9
2018-05-05 18:00 | 45.46 | 45.38
2018-05-05 18:30 | 47.4 | 47.3
2018-05-05 19:00 | 46.38 | 46.29
2018-05-05 19:30 | 44.35 | 44.28
2018-05-05 20:00 | 42.71 | 42.67
2018-05-05 20:30 | 40.86 | 40.84
2018-05-05 21:00 | 39.73 | 39.72
2018-05-05 21:30 | 38.59 | 38.59
2018-05-05 22:00 | 37.48 | 37.48
2018-05-05 22:30 | 35.85 | 35.84
2018-05-05 23:00 | 36.17 | 36.15
2018-05-05 23:30 | 33.41 | 33.38
2018-05-06 | 32.32 | 32.26
2018-05-06 00:30 | 31.53 | 31.46
2018-05-06 01:00 | 30.34 | 30.28
2018-05-06 01:30 | 29.8 | 29.74
2018-05-06 02:00 | 29.58 | 29.52
2018-05-06 02:30 | 29.12 | 29.07
2018-05-06 03:00 | 28.77 | 28.74
2018-05-06 03:30 | 28.64 | 28.61
2018-05-06 04:00 | 28.37 | 28.35
2018-05-06 04:30 | 28.53 | 28.5
2018-05-06 05:00 | 28.45 | 28.43
2018-05-06 05:30 | 29.09 | 29.06
2018-05-06 06:00 | 29.99 | 29.94
2018-05-06 06:30 | 31.25 | 31.19
2018-05-06 07:00 | 31.87 | 31.83
2018-05-06 07:30 | 33.04 | 32.95
2018-05-06 08:00 | 34.57 | 34.43
2018-05-06 08:30 | 36.4 | 36.16
2018-05-06 09:00 | 37.47 | 37.12
2018-05-06 09:30 | 38.59 | 38.14
2018-05-06 10:00 | 36.66 | 36.08
2018-05-06 10:30 | 36.75 | 36.06
2018-05-06 11:00 | 37.33 | 37.02
2018-05-06 11:30 | 35.95 | 35.77
2018-05-06 12:00 | 35.78 | 35.59
2018-05-06 12:30 | 36.4 | 36.23
2018-05-06 13:00 | 35.77 | 35.6
2018-05-06 13:30 | 35.57 | 35.41
2018-05-06 14:00 | 35.28 | 35.15
2018-05-06 14:30 | 35.08 | 34.98
2018-05-06 15:00 | 35.42 | 35.34
2018-05-06 15:30 | 36.48 | 36.42
2018-05-06 16:00 | 37.63 | 37.58
2018-05-06 16:30 | 39.14 | 39.11
2018-05-06 17:00 | 39.64 | 39.62
2018-05-06 17:30 | 41.35 | 41.35
2018-05-06 18:00 | 43.91 | 43.89
2018-05-06 18:30 | 45.7 | 45.66
2018-05-06 19:00 | 44.89 | 44.85
2018-05-06 19:30 | 43.02 | 43
2018-05-06 20:00 | 41.3 | 41.29
2018-05-06 20:30 | 39.65 | 39.64
2018-05-06 21:00 | 38.64 | 38.64
2018-05-06 21:30 | 37.59 | 37.59
2018-05-06 22:00 | 36.5 | 36.49
2018-05-06 22:30 | 35.24 | 35.21
2018-05-06 23:00 | 35.33 | 35.3
2018-05-06 23:30 | 32.77 | 32.7
2018-05-07 | 31.3 | 31.25
2018-05-07 00:30 | 30.27 | 30.25
2018-05-07 01:00 | 29.13 | 29.11
2018-05-07 01:30 | 28.52 | 28.5
2018-05-07 02:00 | 28.07 | 28.05
2018-05-07 02:30 | 28.02 | 28.01
2018-05-07 03:00 | 27.8 | 27.8
2018-05-07 03:30 | 27.34 | 27.33
2018-05-07 04:00 | 27.43 | 27.43
2018-05-07 04:30 | 27.81 | 27.8
2018-05-07 05:00 | 28.53 | 28.51
2018-05-07 05:30 | 29.29 | 29.26
2018-05-07 06:00 | 29.82 | 29.77
2018-05-07 06:30 | 31.42 | 31.35
2018-05-07 07:00 | 32.3 | 32.23
2018-05-07 07:30 | 34 | 33.87
2018-05-07 08:00 | 35.36 | 35.2
2018-05-07 08:30 | 36.02 | 35.79
2018-05-07 09:00 | 36.95 | 36.61
2018-05-07 09:30 | 38.16 | 37.75
2018-05-07 10:00 | 36.66 | 36.18
2018-05-07 10:30 | 37.4 | 36.86
2018-05-07 11:00 | 39.82 | 39.28
2018-05-07 11:30 | 39.54 | 38.97
2018-05-07 12:00 | 39.45 | 38.87
2018-05-07 12:30 | 39.27 | 38.69
2018-05-07 13:00 | 37.16 | 36.5
2018-05-07 13:30 | 37.92 | 37.28
2018-05-07 14:00 | 36.9 | 36.24
2018-05-07 14:30 | 38.41 | 37.85
2018-05-07 15:00 | 40.04 | 39.57
2018-05-07 15:30 | 39.2 | 38.76
2018-05-07 16:00 | 40.43 | 40
2018-05-07 16:30 | 41.69 | 41.27
2018-05-07 17:00 | 42.11 | 41.76
2018-05-07 17:30 | 43.11 | 42.81
2018-05-07 18:00 | 45.91 | 45.58
2018-05-07 18:30 | 48.87 | 47.65
2018-05-07 19:00 | 48.6 | 46.73
2018-05-07 19:30 | 46.4 | 44.42
2018-05-07 20:00 | 44.08 | 41.95
2018-05-07 20:30 | 42.05 | 39.76
2018-05-07 21:00 | 40.64 | 38.24
2018-05-07 21:30 | 38.92 | 36.38
2018-05-07 22:00 | 37.48 | 34.8
2018-05-07 22:30 | 35.98 | 33.16
2018-05-07 23:00 | 36.44 | 33.63
2018-05-07 23:30 | 33.74 | 30.65
2018-05-08 | 32.59 | 29.36
2018-05-08 00:30 | 32.31 | 29.03
2018-05-08 01:00 | 27.92 | 27.79
2018-05-08 01:30 | 27.36 | 27.36
2018-05-08 02:00 | 27.37 | 27.37
2018-05-08 02:30 | 27.23 | 27.23
2018-05-08 03:00 | 27.39 | 27.38
2018-05-08 03:30 | 27.37 | 27.36
2018-05-08 04:00 | 27.87 | 27.87
2018-05-08 04:30 | 28.47 | 28.45
2018-05-08 05:00 | 29.75 | 29.72
2018-05-08 05:30 | 32.38 | 32.29
2018-05-08 06:00 | 35.61 | 35.39
2018-05-08 06:30 | 40.72 | 40.23
2018-05-08 07:00 | 46.22 | 45.48
2018-05-08 07:30 | 51.31 | 50.67
2018-05-08 08:00 | 54.8 | 53.46
2018-05-08 08:30 | 56.11 | 54.49
2018-05-08 09:00 | 56.45 | 54.84
2018-05-08 09:30 | 55.85 | 54.23
2018-05-08 10:00 | 55.73 | 54.14
2018-05-08 10:30 | 55.78 | 54.2
2018-05-08 11:00 | 56.06 | 54.51
2018-05-08 11:30 | 57.36 | 55.87
2018-05-08 12:00 | 57.59 | 56.11
2018-05-08 12:30 | 58.45 | 56.99
2018-05-08 13:00 | 56.77 | 55.27
2018-05-08 13:30 | 57.61 | 56.13
2018-05-08 14:00 | 58.73 | 57.31
2018-05-08 14:30 | 59.25 | 57.85
2018-05-08 15:00 | 59.66 | 58.27
2018-05-08 15:30 | 59.42 | 57.99
2018-05-08 16:00 | 59.84 | 58.39
2018-05-08 16:30 | 60.24 | 58.76
2018-05-08 17:00 | 59.26 | 57.7
2018-05-08 17:30 | 57.9 | 56.23
2018-05-08 18:00 | 57.85 | 56.12
2018-05-08 18:30 | 59.53 | 57.84
2018-05-08 19:00 | 59 | 57.29
2018-05-08 19:30 | 55.93 | 54.09
2018-05-08 20:00 | 53.67 | 51.72
2018-05-08 20:30 | 51.48 | 49.4
2018-05-08 21:00 | 48.03 | 46.98
2018-05-08 21:30 | 45.06 | 44.76
2018-05-08 22:00 | 42.36 | 41.88
2018-05-08 22:30 | 39.48 | 39.01
2018-05-08 23:00 | 38.86 | 38.72
2018-05-08 23:30 | 35.65 | 35.42
2018-05-09 | 33.91 | 33.58
2018-05-09 00:30 | 32.24 | 32.2
2018-05-09 01:00 | 30.96 | 30.91
2018-05-09 01:30 | 30.41 | 30.36
2018-05-09 02:00 | 30.01 | 29.96
2018-05-09 02:30 | 29.17 | 29.11
2018-05-09 03:00 | 28.76 | 28.71
2018-05-09 03:30 | 28.79 | 28.74
2018-05-09 04:00 | 28.89 | 28.84
2018-05-09 04:30 | 29.5 | 29.43
2018-05-09 05:00 | 30.97 | 30.89
2018-05-09 05:30 | 33.53 | 33.36
2018-05-09 06:00 | 36.89 | 36.59
2018-05-09 06:30 | 42.05 | 41.43
2018-05-09 07:00 | 47.16 | 46.68
2018-05-09 07:30 | 52.98 | 51.83
2018-05-09 08:00 | 56.06 | 54.48
2018-05-09 08:30 | 56.78 | 55.16
2018-05-09 09:00 | 57.11 | 55.56
2018-05-09 09:30 | 56.65 | 55.11
2018-05-09 10:00 | 56.97 | 55.45
2018-05-09 10:30 | 57.32 | 55.84
2018-05-09 11:00 | 57.77 | 56.33
2018-05-09 11:30 | 58.53 | 57.12
2018-05-09 12:00 | 58.88 | 57.51
2018-05-09 12:30 | 59.95 | 58.61
2018-05-09 13:00 | 58.46 | 57.08
2018-05-09 13:30 | 58.8 | 57.44
2018-05-09 14:00 | 59.14 | 57.79
2018-05-09 14:30 | 59.6 | 58.26
2018-05-09 15:00 | 59.29 | 57.92
2018-05-09 15:30 | 59.36 | 57.97
2018-05-09 16:00 | 60.21 | 58.81
2018-05-09 16:30 | 60.66 | 59.21
2018-05-09 17:00 | 59.55 | 58.02
2018-05-09 17:30 | 58.14 | 56.48
2018-05-09 18:00 | 58.09 | 56.39
2018-05-09 18:30 | 59.56 | 57.9
2018-05-09 19:00 | 58.21 | 56.48
2018-05-09 19:30 | 55.28 | 53.41
2018-05-09 20:00 | 53.05 | 51.06
2018-05-09 20:30 | 50.97 | 48.86
2018-05-09 21:00 | 46.6 | 46.32
2018-05-09 21:30 | 44.29 | 43.98
2018-05-09 22:00 | 42.15 | 41.69
2018-05-09 22:30 | 40.39 | 39.75
2018-05-09 23:00 | 39.81 | 39.35
2018-05-09 23:30 | 36.2 | 35.98
2018-05-10 | 34.46 | 34.17
2018-05-10 00:30 | 33.77 | 33.45
2018-05-10 01:00 | 32.39 | 32.01
2018-05-10 01:30 | 31.76 | 31.34
2018-05-10 02:00 | 31.3 | 30.81
2018-05-10 02:30 | 30.14 | 29.92
2018-05-10 03:00 | 29.77 | 29.71
2018-05-10 03:30 | 29.94 | 29.88
2018-05-10 04:00 | 30.05 | 29.99
2018-05-10 04:30 | 30.69 | 30.66
2018-05-10 05:00 | 31.82 | 31.81
2018-05-10 05:30 | 34.22 | 34.22
2018-05-10 06:00 | 37.3 | 37.27
2018-05-10 06:30 | 42.38 | 42.33
2018-05-10 07:00 | 46.38 | 46.35
2018-05-10 07:30 | 51.35 | 51.14
2018-05-10 08:00 | 54.41 | 53.9
2018-05-10 08:30 | 55.37 | 54.96
2018-05-10 09:00 | 55.72 | 55.24
2018-05-10 09:30 | 56.01 | 55.38
2018-05-10 10:00 | 56.51 | 55.73
2018-05-10 10:30 | 57.75 | 56.77
2018-05-10 11:00 | 57.22 | 55.89
2018-05-10 11:30 | 59.61 | 58.1
2018-05-10 12:00 | 60.17 | 58.7
2018-05-10 12:30 | 61.08 | 59.66
2018-05-10 13:00 | 61.17 | 59.77
2018-05-10 13:30 | 61.31 | 59.86
2018-05-10 14:00 | 62.36 | 60.89
2018-05-10 14:30 | 62.83 | 61.38
2018-05-10 15:00 | 62.32 | 61
2018-05-10 15:30 | 62.65 | 61.38
2018-05-10 16:00 | 64.16 | 62.9
2018-05-10 16:30 | 63.04 | 61.69
2018-05-10 17:00 | 61.92 | 60.48
2018-05-10 17:30 | 59.87 | 58.3
2018-05-10 18:00 | 60.53 | 58.95
2018-05-10 18:30 | 61.69 | 60.13
2018-05-10 19:00 | 60.34 | 58.72
2018-05-10 19:30 | 57.31 | 55.56
2018-05-10 20:00 | 55.62 | 53.78
2018-05-10 20:30 | 53.26 | 51.3
2018-05-10 21:00 | 51.24 | 49.16
2018-05-10 21:30 | 48.42 | 46.16
2018-05-10 22:00 | 43.6 | 43.14
2018-05-10 22:30 | 41.43 | 40.98
2018-05-10 23:00 | 41.08 | 40.55
2018-05-10 23:30 | 38.23 | 37.56
2018-05-11 | 36.4 | 35.59
2018-05-11 00:30 | 34.72 | 34.27
2018-05-11 01:00 | 32.95 | 32.67
2018-05-11 01:30 | 32.62 | 32.33
2018-05-11 02:00 | 32.01 | 31.66
2018-05-11 02:30 | 31.12 | 31
2018-05-11 03:00 | 30.62 | 30.59
2018-05-11 03:30 | 30.39 | 30.34
2018-05-11 04:00 | 30.2 | 30.16
2018-05-11 04:30 | 30.88 | 30.84
2018-05-11 05:00 | 31.96 | 31.94
2018-05-11 05:30 | 34.37 | 34.37
2018-05-11 06:00 | 37.43 | 37.41
2018-05-11 06:30 | 43.28 | 43.07
2018-05-11 07:00 | 47.19 | 47.13
2018-05-11 07:30 | 51.82 | 51.59
2018-05-11 08:00 | 54.65 | 54.23
2018-05-11 08:30 | 55.95 | 55.57
2018-05-11 09:00 | 56.92 | 56.36
2018-05-11 09:30 | 57.09 | 56.37
2018-05-11 10:00 | 57.32 | 56.54
2018-05-11 10:30 | 58.08 | 57.12
2018-05-11 11:00 | 59.35 | 58.21
2018-05-11 11:30 | 59.96 | 58.7
2018-05-11 12:00 | 60.38 | 59.2
2018-05-11 12:30 | 61.39 | 60.22
2018-05-11 13:00 | 60.98 | 59.79
2018-05-11 13:30 | 63.09 | 61.82
2018-05-11 14:00 | 63.13 | 61.87
2018-05-11 14:30 | 61.59 | 60.27
2018-05-11 15:00 | 59.89 | 58.48
2018-05-11 15:30 | 60.66 | 59.25
2018-05-11 16:00 | 61.3 | 59.87
2018-05-11 16:30 | 61.37 | 59.9
2018-05-11 17:00 | 60.33 | 58.79
2018-05-11 17:30 | 58.79 | 57.13
2018-05-11 18:00 | 57.82 | 56.09
2018-05-11 18:30 | 58.04 | 56.3
2018-05-11 19:00 | 57.02 | 55.23
2018-05-11 19:30 | 55.3 | 53.44
2018-05-11 20:00 | 52.93 | 50.93
2018-05-11 20:30 | 49.6 | 48.62
2018-05-11 21:00 | 46.66 | 46.45
2018-05-11 21:30 | 45.2 | 44.95
2018-05-11 22:00 | 43.12 | 42.71
2018-05-11 22:30 | 41.06 | 40.49
2018-05-11 23:00 | 40.9 | 40.22
2018-05-11 23:30 | 36.49 | 36.49
2018-05-12 | 34.99 | 34.99
2018-05-12 00:30 | 33.88 | 33.8
2018-05-12 01:00 | 32.44 | 32.29
2018-05-12 01:30 | 31.85 | 31.7
2018-05-12 02:00 | 31.49 | 31.36
2018-05-12 02:30 | 30.79 | 30.7
2018-05-12 03:00 | 30.27 | 30.18
2018-05-12 03:30 | 29.71 | 29.66
2018-05-12 04:00 | 29.27 | 29.22
2018-05-12 04:30 | 29.56 | 29.5
2018-05-12 05:00 | 30.13 | 30.05
2018-05-12 05:30 | 31.68 | 31.56
2018-05-12 06:00 | 32.74 | 32.58
2018-05-12 06:30 | 34.91 | 34.69
2018-05-12 07:00 | 36.57 | 36.3
2018-05-12 07:30 | 38.36 | 37.97
2018-05-12 08:00 | 39.64 | 39.1
2018-05-12 08:30 | 40.85 | 40.09
2018-05-12 09:00 | 40.85 | 39.94
2018-05-12 09:30 | 40.06 | 39.1
2018-05-12 10:00 | 39.73 | 38.65
2018-05-12 10:30 | 39.21 | 38
2018-05-12 11:00 | 36.93 | 35.89
2018-05-12 11:30 | 36.12 | 35.01
2018-05-12 12:00 | 37.04 | 35.7
2018-05-12 12:30 | 38.67 | 37.35
2018-05-12 13:00 | 37.03 | 35.72
2018-05-12 13:30 | 36.51 | 35.23
2018-05-12 14:00 | 36.88 | 35.62
2018-05-12 14:30 | 36.88 | 35.75
2018-05-12 15:00 | 37.13 | 36.14
2018-05-12 15:30 | 38.22 | 37.31
2018-05-12 16:00 | 38.79 | 38.04
2018-05-12 16:30 | 40.61 | 39.99
2018-05-12 17:00 | 41.47 | 40.89
2018-05-12 17:30 | 43.55 | 43.04
2018-05-12 18:00 | 46.91 | 45.82
2018-05-12 18:30 | 48.73 | 46.93
2018-05-12 19:00 | 47.66 | 45.8
2018-05-12 19:30 | 45.42 | 43.44
2018-05-12 20:00 | 43.68 | 41.58
2018-05-12 20:30 | 42.21 | 40
2018-05-12 21:00 | 41.01 | 38.71
2018-05-12 21:30 | 39.48 | 37.05
2018-05-12 22:00 | 38.56 | 36.05
2018-05-12 22:30 | 37.39 | 34.76
2018-05-12 23:00 | 37.94 | 35.34
2018-05-12 23:30 | 35.57 | 32.76
2018-05-13 | 34.16 | 31.18
2018-05-13 00:30 | 33.62 | 30.55
2018-05-13 01:00 | 32.44 | 29.25
2018-05-13 01:30 | 31.95 | 28.7
2018-05-13 02:00 | 31.01 | 27.88
2018-05-13 02:30 | 30.58 | 27.38
2018-05-13 03:00 | 30.39 | 27.16
2018-05-13 03:30 | 30.64 | 27.45
2018-05-13 04:00 | 30.24 | 26.97
2018-05-13 04:30 | 30.36 | 27.11
2018-05-13 05:00 | 30.76 | 27.57
2018-05-13 05:30 | 31.46 | 28.36
2018-05-13 06:00 | 32.21 | 29.21
2018-05-13 06:30 | 33.49 | 30.62
2018-05-13 07:00 | 33.73 | 30.88
2018-05-13 07:30 | 35.04 | 32.32
2018-05-13 08:00 | 36.06 | 33.47
2018-05-13 08:30 | 36.56 | 34.03
2018-05-13 09:00 | 37.23 | 34.8
2018-05-13 09:30 | 36.75 | 34.29
2018-05-13 10:00 | 35.73 | 33.22
2018-05-13 10:30 | 36.08 | 33.61
2018-05-13 11:00 | 35.49 | 33
2018-05-13 11:30 | 35.37 | 32.87
2018-05-13 12:00 | 32.97 | 30.28
2018-05-13 12:30 | 33.63 | 31.01
2018-05-13 13:00 | 33.27 | 30.63
2018-05-13 13:30 | 34.01 | 31.45
2018-05-13 14:00 | 33.95 | 31.36
2018-05-13 14:30 | 34.18 | 31.61
2018-05-13 15:00 | 34.67 | 32.14
2018-05-13 15:30 | 35.96 | 33.51
2018-05-13 16:00 | 37.95 | 35.62
2018-05-13 16:30 | 39.73 | 37.53
2018-05-13 17:00 | 40.88 | 38.75
2018-05-13 17:30 | 43.47 | 41.5
2018-05-13 18:00 | 46.97 | 45.21
2018-05-13 18:30 | 50.13 | 46.7
2018-05-13 19:00 | 52.57 | 45.04
2018-05-13 19:30 | 50.9 | 42.99
2018-05-13 20:00 | 49.99 | 41.85
2018-05-13 20:30 | 48.5 | 39.93
2018-05-13 21:00 | 47.24 | 38.31
2018-05-13 21:30 | 45.62 | 36.17
2018-05-13 22:00 | 44.3 | 34.35
2018-05-13 22:30 | 43.3 | 32.97
2018-05-13 23:00 | 43.62 | 33.34
2018-05-13 23:30 | 41.57 | 30.5
2018-05-14 | 40.44 | 28.9
2018-05-14 00:30 | 39.19 | 28.31
2018-05-14 01:00 | 30.26 | 27
2018-05-14 01:30 | 29.95 | 26.65
2018-05-14 02:00 | 29.99 | 26.69
2018-05-14 02:30 | 29.67 | 26.3
2018-05-14 03:00 | 29.71 | 26.36
2018-05-14 03:30 | 30.03 | 26.73
2018-05-14 04:00 | 30.14 | 26.85
2018-05-14 04:30 | 30.88 | 27.69
2018-05-14 05:00 | 32.4 | 29.41
2018-05-14 05:30 | 34.83 | 32.14
2018-05-14 06:00 | 37.81 | 35.42
2018-05-14 06:30 | 42.26 | 40.24
2018-05-14 07:00 | 46.4 | 44.6
2018-05-14 07:30 | 50.46 | 48.78
2018-05-14 08:00 | 51.67 | 50.03
2018-05-14 08:30 | 50.98 | 49.28
2018-05-14 09:00 | 49.36 | 47.64
2018-05-14 09:30 | 48.47 | 46.74
2018-05-14 10:00 | 47.72 | 45.98
2018-05-14 10:30 | 47.71 | 45.99
2018-05-14 11:00 | 48.24 | 46.44
2018-05-14 11:30 | 48.31 | 46.53
2018-05-14 12:00 | 48.55 | 46.8
2018-05-14 12:30 | 49.46 | 47.74
2018-05-14 13:00 | 48.47 | 46.7
2018-05-14 13:30 | 48.88 | 47.15
2018-05-14 14:00 | 49.57 | 47.86
2018-05-14 14:30 | 50.26 | 48.58
2018-05-14 15:00 | 50.45 | 48.77
2018-05-14 15:30 | 50.21 | 48.49
2018-05-14 16:00 | 51.38 | 49.68
2018-05-14 16:30 | 52.76 | 51.07
2018-05-14 17:00 | 53.04 | 51.31
2018-05-14 17:30 | 53.28 | 51.48
2018-05-14 18:00 | 54.01 | 52.21
2018-05-14 18:30 | 55.85 | 54.11
2018-05-14 19:00 | 55.07 | 53.3
2018-05-14 19:30 | 52.22 | 50.31
2018-05-14 20:00 | 50.11 | 48.07
2018-05-14 20:30 | 47.32 | 45.11
2018-05-14 21:00 | 44.8 | 42.4
2018-05-14 21:30 | 42.89 | 40.34
2018-05-14 22:00 | 39.82 | 37.48
2018-05-14 22:30 | 38.11 | 35.77
2018-05-14 23:00 | 38.44 | 36.11
2018-05-14 23:30 | 36.03 | 33.51
2018-05-15 | 34.31 | 31.64
2018-05-15 00:30 | 33.48 | 30.72
2018-05-15 01:00 | 32.08 | 29.18
2018-05-15 01:30 | 31.87 | 28.92
2018-05-15 02:00 | 31.32 | 28.27
2018-05-15 02:30 | 30.92 | 27.79
2018-05-15 03:00 | 30.83 | 27.69
2018-05-15 03:30 | 31.14 | 28.05
2018-05-15 04:00 | 31.23 | 28.15
2018-05-15 04:30 | 31.94 | 28.94
2018-05-15 05:00 | 32.77 | 29.87
2018-05-15 05:30 | 35.15 | 32.49
2018-05-15 06:00 | 38.45 | 36.11
2018-05-15 06:30 | 42.99 | 41
2018-05-15 07:00 | 47.84 | 46.14
2018-05-15 07:30 | 52.88 | 50.65
2018-05-15 08:00 | 58.37 | 51.8
2018-05-15 08:30 | 57.28 | 50.64
2018-05-15 09:00 | 53.89 | 49.56
2018-05-15 09:30 | 52.24 | 48.27
2018-05-15 10:00 | 52.15 | 48
2018-05-15 10:30 | 51.61 | 47.44
2018-05-15 11:00 | 51.85 | 47.76
2018-05-15 11:30 | 52.15 | 48.12
2018-05-15 12:00 | 52.06 | 48.06
2018-05-15 12:30 | 52.66 | 48.69
2018-05-15 13:00 | 51.55 | 47.45
2018-05-15 13:30 | 51.8 | 47.75
2018-05-15 14:00 | 52.36 | 48.36
2018-05-15 14:30 | 53.13 | 49.21
2018-05-15 15:00 | 53.59 | 49.71
2018-05-15 15:30 | 54.35 | 50.52
2018-05-15 16:00 | 55.52 | 51.72
2018-05-15 16:30 | 56.56 | 52.66
2018-05-15 17:00 | 56.27 | 52.1
2018-05-15 17:30 | 56.02 | 51.75
2018-05-15 18:00 | 56.71 | 52.75
2018-05-15 18:30 | 57.72 | 54.03
2018-05-15 19:00 | 56.83 | 53.05
2018-05-15 19:30 | 54.31 | 50.27
2018-05-15 20:00 | 52.89 | 48.69
2018-05-15 20:30 | 50.35 | 45.83
2018-05-15 21:00 | 48.16 | 43.34
2018-05-15 21:30 | 46.31 | 41.2
2018-05-15 22:00 | 44.02 | 38.73
2018-05-15 22:30 | 42.15 | 36.6
2018-05-15 23:00 | 42.47 | 36.97
2018-05-15 23:30 | 39.95 | 33.97
2018-05-16 | 38.14 | 31.75
2018-05-16 00:30 | 37.82 | 31.32
2018-05-16 01:00 | 36.82 | 30.09
2018-05-16 01:30 | 36.32 | 29.46
2018-05-16 02:00 | 35.96 | 28.99
2018-05-16 02:30 | 30.44 | 28.26
2018-05-16 03:00 | 28.62 | 27.82
2018-05-16 03:30 | 28.69 | 27.88
2018-05-16 04:00 | 28.83 | 28.03
2018-05-16 04:30 | 29.41 | 28.63
2018-05-16 05:00 | 30.61 | 29.87
2018-05-16 05:30 | 33.34 | 32.68
2018-05-16 06:00 | 36.34 | 35.76
2018-05-16 06:30 | 41.42 | 40.88
2018-05-16 07:00 | 46.23 | 45.72
2018-05-16 07:30 | 52.12 | 51.71
2018-05-16 08:00 | 53.76 | 53.39
2018-05-16 08:30 | 53.37 | 52.92
2018-05-16 09:00 | 52.91 | 52.5
2018-05-16 09:30 | 52.29 | 51.9
2018-05-16 10:00 | 51.34 | 50.94
2018-05-16 10:30 | 52.23 | 51.84
2018-05-16 11:00 | 56.32 | 55.87
2018-05-16 11:30 | 56.77 | 56.31
2018-05-16 12:00 | 55.94 | 55.38
2018-05-16 12:30 | 54.49 | 53.93
2018-05-16 13:00 | 52.03 | 51.5
2018-05-16 13:30 | 53.9 | 53.35
2018-05-16 14:00 | 54.2 | 53.63
2018-05-16 14:30 | 53.97 | 53.41
2018-05-16 15:00 | 53.71 | 53.21
2018-05-16 15:30 | 53.83 | 53.44
2018-05-16 16:00 | 53.83 | 53.46
2018-05-16 16:30 | 54.27 | 53.88
2018-05-16 17:00 | 52.96 | 52.52
2018-05-16 17:30 | 52.59 | 52.12
2018-05-16 18:00 | 54.27 | 53.82
2018-05-16 18:30 | 55.39 | 54.93
2018-05-16 19:00 | 54.97 | 54.51
2018-05-16 19:30 | 52.52 | 52.03
2018-05-16 20:00 | 50.01 | 49.48
2018-05-16 20:30 | 47.72 | 47.16
2018-05-16 21:00 | 45.25 | 44.79
2018-05-16 21:30 | 43.43 | 42.94
2018-05-16 22:00 | 40.95 | 40.41
2018-05-16 22:30 | 38.83 | 38.27
2018-05-16 23:00 | 38.91 | 38.39
2018-05-16 23:30 | 36.11 | 35.55
2018-05-17 | 34.13 | 33.52
2018-05-17 00:30 | 33.17 | 32.54
2018-05-17 01:00 | 31.59 | 30.92
2018-05-17 01:30 | 30.9 | 30.2
2018-05-17 02:00 | 30.41 | 29.69
2018-05-17 02:30 | 29.9 | 29.15
2018-05-17 03:00 | 29.85 | 29.11
2018-05-17 03:30 | 30.08 | 29.35
2018-05-17 04:00 | 30.1 | 29.36
2018-05-17 04:30 | 31.05 | 30.34
2018-05-17 05:00 | 32.04 | 31.36
2018-05-17 05:30 | 34.53 | 33.91
2018-05-17 06:00 | 37.3 | 36.75
2018-05-17 06:30 | 42.82 | 42.12
2018-05-17 07:00 | 47.44 | 46.96
2018-05-17 07:30 | 53.05 | 52.66
2018-05-17 08:00 | 55.54 | 55.17
2018-05-17 08:30 | 56.59 | 56.13
2018-05-17 09:00 | 56.35 | 55.88
2018-05-17 09:30 | 55.26 | 54.88
2018-05-17 10:00 | 53.16 | 52.78
2018-05-17 10:30 | 54.02 | 53.65
2018-05-17 11:00 | 52.96 | 52.52
2018-05-17 11:30 | 54.7 | 54.28
2018-05-17 12:00 | 55.97 | 55.56
2018-05-17 12:30 | 54.59 | 54.11
2018-05-17 13:00 | 54.57 | 54.06
2018-05-17 13:30 | 55.69 | 55.15
2018-05-17 14:00 | 54.64 | 54.11
2018-05-17 14:30 | 54.41 | 53.81
2018-05-17 15:00 | 54.74 | 54.22
2018-05-17 15:30 | 54.4 | 54.01
2018-05-17 16:00 | 54.1 | 53.72
2018-05-17 16:30 | 54.94 | 54.55
2018-05-17 17:00 | 54.38 | 53.97
2018-05-17 17:30 | 54.08 | 53.64
2018-05-17 18:00 | 55.71 | 55.28
2018-05-17 18:30 | 57.02 | 56.6
2018-05-17 19:00 | 56 | 55.56
2018-05-17 19:30 | 53.63 | 53.16
2018-05-17 20:00 | 51.59 | 51.09
2018-05-17 20:30 | 49.25 | 48.71
2018-05-17 21:00 | 46.94 | 46.36
2018-05-17 21:30 | 43.66 | 43.1
2018-05-17 22:00 | 41.17 | 40.63
2018-05-17 22:30 | 39.34 | 38.77
2018-05-17 23:00 | 39.37 | 38.79
2018-05-17 23:30 | 36.03 | 35.44
2018-05-18 | 34.14 | 33.54
2018-05-18 00:30 | 32.98 | 32.35
2018-05-18 01:00 | 31.64 | 30.97
2018-05-18 01:30 | 31.29 | 30.61
2018-05-18 02:00 | 30.8 | 30.1
2018-05-18 02:30 | 30.12 | 29.39
2018-05-18 03:00 | 29.98 | 29.24
2018-05-18 03:30 | 29.98 | 29.23
2018-05-18 04:00 | 30.04 | 29.3
2018-05-18 04:30 | 30.57 | 29.85
2018-05-18 05:00 | 31.91 | 31.23
2018-05-18 05:30 | 34.28 | 33.66
2018-05-18 06:00 | 37.05 | 36.5
2018-05-18 06:30 | 41.73 | 41.13
2018-05-18 07:00 | 46.26 | 45.82
2018-05-18 07:30 | 51.78 | 51.38
2018-05-18 08:00 | 53.41 | 53.04
2018-05-18 08:30 | 53.78 | 53.28
2018-05-18 09:00 | 53.76 | 53.37
2018-05-18 09:30 | 52.62 | 52.23
2018-05-18 10:00 | 52.16 | 51.77
2018-05-18 10:30 | 51.35 | 50.96
2018-05-18 11:00 | 52.71 | 52.31
2018-05-18 11:30 | 52.82 | 52.39
2018-05-18 12:00 | 51.99 | 51.56
2018-05-18 12:30 | 52.73 | 52.33
2018-05-18 13:00 | 51.11 | 50.68
2018-05-18 13:30 | 51.27 | 50.87
2018-05-18 14:00 | 51.78 | 51.4
2018-05-18 14:30 | 50.72 | 50.33
2018-05-18 15:00 | 50.42 | 50.02
2018-05-18 15:30 | 50.26 | 49.84
2018-05-18 16:00 | 51.42 | 51
2018-05-18 16:30 | 52.34 | 51.91
2018-05-18 17:00 | 51.88 | 51.42
2018-05-18 17:30 | 51.96 | 51.48
2018-05-18 18:00 | 52.99 | 52.52
2018-05-18 18:30 | 53.26 | 52.78
2018-05-18 19:00 | 52.13 | 51.63
2018-05-18 19:30 | 49.4 | 48.86
2018-05-18 20:00 | 47.12 | 46.67
2018-05-18 20:30 | 44.96 | 44.48
2018-05-18 21:00 | 43.24 | 42.73
2018-05-18 21:30 | 41.79 | 41.25
2018-05-18 22:00 | 39.96 | 39.38
2018-05-18 22:30 | 38.01 | 37.38
2018-05-18 23:00 | 38.63 | 38.02
2018-05-18 23:30 | 35.48 | 34.88
2018-05-19 | 33.31 | 32.66
2018-05-19 00:30 | 32.38 | 31.7
2018-05-19 01:00 | 31.2 | 30.5
2018-05-19 01:30 | 30.97 | 30.26
2018-05-19 02:00 | 30.39 | 29.66
2018-05-19 02:30 | 29.91 | 29.16
2018-05-19 03:00 | 29.67 | 28.91
2018-05-19 03:30 | 29.42 | 28.63
2018-05-19 04:00 | 29 | 28.2
2018-05-19 04:30 | 29.44 | 28.66
2018-05-19 05:00 | 29.87 | 29.11
2018-05-19 05:30 | 31.13 | 30.41
2018-05-19 06:00 | 32.16 | 31.48
2018-05-19 06:30 | 34.27 | 33.63
2018-05-19 07:00 | 35.79 | 35.19
2018-05-19 07:30 | 37.72 | 37.17
2018-05-19 08:00 | 39.36 | 38.85
2018-05-19 08:30 | 41.05 | 40.47
2018-05-19 09:00 | 41.43 | 40.7
2018-05-19 09:30 | 41.52 | 40.61
2018-05-19 10:00 | 40.74 | 40.17
2018-05-19 10:30 | 40.23 | 39.73
2018-05-19 11:00 | 40.47 | 39.98
2018-05-19 11:30 | 39.85 | 39.35
2018-05-19 12:00 | 40.45 | 39.95
2018-05-19 12:30 | 43.31 | 42.83
2018-05-19 13:00 | 40.86 | 40.34
2018-05-19 13:30 | 38.51 | 37.95
2018-05-19 14:00 | 37.82 | 37.24
2018-05-19 14:30 | 39.64 | 39.09
2018-05-19 15:00 | 38.88 | 38.31
2018-05-19 15:30 | 39.9 | 39.33
2018-05-19 16:00 | 40.3 | 39.73
2018-05-19 16:30 | 41.23 | 40.67
2018-05-19 17:00 | 41.84 | 41.28
2018-05-19 17:30 | 43.62 | 43.1
2018-05-19 18:00 | 45.89 | 45.4
2018-05-19 18:30 | 46.85 | 46.37
2018-05-19 19:00 | 45.4 | 44.91
2018-05-19 19:30 | 43.57 | 43.04
2018-05-19 20:00 | 42.04 | 41.49
2018-05-19 20:30 | 40.55 | 39.96
2018-05-19 21:00 | 39.39 | 38.79
2018-05-19 21:30 | 38.21 | 37.58
2018-05-19 22:00 | 36.98 | 36.31
2018-05-19 22:30 | 35.82 | 35.11
2018-05-19 23:00 | 37.26 | 36.58
2018-05-19 23:30 | 34.44 | 33.69
2018-05-20 | 32.19 | 31.43
2018-05-20 00:30 | 31.13 | 30.38
2018-05-20 01:00 | 30.16 | 29.38
2018-05-20 01:30 | 29.53 | 28.74
2018-05-20 02:00 | 29.39 | 28.6
2018-05-20 02:30 | 28.98 | 28.16
2018-05-20 03:00 | 28.34 | 27.5
2018-05-20 03:30 | 28.14 | 27.29
2018-05-20 04:00 | 28.18 | 27.33
2018-05-20 04:30 | 28.32 | 27.48
2018-05-20 05:00 | 28.72 | 27.89
2018-05-20 05:30 | 29.34 | 28.54
2018-05-20 06:00 | 30.28 | 29.51
2018-05-20 06:30 | 31.18 | 30.43
2018-05-20 07:00 | 31.81 | 31.07
2018-05-20 07:30 | 32.96 | 32.26
2018-05-20 08:00 | 34.21 | 33.55
2018-05-20 08:30 | 34.77 | 34.14
2018-05-20 09:00 | 35.45 | 34.85
2018-05-20 09:30 | 35.58 | 35
2018-05-20 10:00 | 35.57 | 35.01
2018-05-20 10:30 | 35.16 | 34.59
2018-05-20 11:00 | 34.84 | 34.21
2018-05-20 11:30 | 34.64 | 33.97
2018-05-20 12:00 | 34.7 | 34.03
2018-05-20 12:30 | 35.58 | 34.95
2018-05-20 13:00 | 34.32 | 33.67
2018-05-20 13:30 | 35.46 | 34.82
2018-05-20 14:00 | 34 | 33.33
2018-05-20 14:30 | 35.62 | 34.98
2018-05-20 15:00 | 35.16 | 34.49
2018-05-20 15:30 | 36.09 | 35.44
2018-05-20 16:00 | 37.61 | 36.97
2018-05-20 16:30 | 40.31 | 39.72
2018-05-20 17:00 | 40.79 | 40.2
2018-05-20 17:30 | 42.45 | 41.88
2018-05-20 18:00 | 46.03 | 45.53
2018-05-20 18:30 | 46.93 | 46.43
2018-05-20 19:00 | 46.36 | 45.86
2018-05-20 19:30 | 44.3 | 43.76
2018-05-20 20:00 | 42.98 | 42.43
2018-05-20 20:30 | 40.6 | 40
2018-05-20 21:00 | 38.63 | 37.98
2018-05-20 21:30 | 37.03 | 36.34
2018-05-20 22:00 | 35.42 | 34.69
2018-05-20 22:30 | 33.88 | 33.2
2018-05-20 23:00 | 34.39 | 33.72
2018-05-20 23:30 | 31.57 | 30.83
2018-05-21 | 30.04 | 29.25
2018-05-21 00:30 | 29.36 | 28.54
2018-05-21 01:00 | 28.22 | 27.36
2018-05-21 01:30 | 27.83 | 26.96
2018-05-21 02:00 | 27.83 | 26.96
2018-05-21 02:30 | 27.41 | 26.51
2018-05-21 03:00 | 27.2 | 26.29
2018-05-21 03:30 | 27.49 | 26.6
2018-05-21 04:00 | 27.75 | 26.86
2018-05-21 04:30 | 28.61 | 27.76
2018-05-21 05:00 | 29.81 | 29.01
2018-05-21 05:30 | 32.48 | 31.77
2018-05-21 06:00 | 35.69 | 35.08
2018-05-21 06:30 | 39.91 | 39.4
2018-05-21 07:00 | 44.14 | 43.62
2018-05-21 07:30 | 49.05 | 48.63
2018-05-21 08:00 | 50.46 | 49.93
2018-05-21 08:30 | 50.74 | 49.91
2018-05-21 09:00 | 50.73 | 49.81
2018-05-21 09:30 | 49.53 | 49.02
2018-05-21 10:00 | 49.12 | 48.55
2018-05-21 10:30 | 49.11 | 48.44
2018-05-21 11:00 | 49.58 | 49.15
2018-05-21 11:30 | 50.37 | 49.98
2018-05-21 12:00 | 50.51 | 50.11
2018-05-21 12:30 | 51.06 | 50.67
2018-05-21 13:00 | 50.78 | 50.39
2018-05-21 13:30 | 51.38 | 50.97
2018-05-21 14:00 | 51.39 | 50.93
2018-05-21 14:30 | 52.39 | 51.89
2018-05-21 15:00 | 52.3 | 51.85
2018-05-21 15:30 | 52.44 | 52.07
2018-05-21 16:00 | 53.45 | 53.07
2018-05-21 16:30 | 54.61 | 54.22
2018-05-21 17:00 | 54.88 | 54.47
2018-05-21 17:30 | 54.3 | 53.85
2018-05-21 18:00 | 55.92 | 55.47
2018-05-21 18:30 | 56.87 | 56.42
2018-05-21 19:00 | 55.56 | 55.1
2018-05-21 19:30 | 53.09 | 52.6
2018-05-21 20:00 | 50.5 | 49.96
2018-05-21 20:30 | 48.03 | 47.45
2018-05-21 21:00 | 46.08 | 45.46
2018-05-21 21:30 | 44.28 | 43.63
2018-05-21 22:00 | 41.88 | 41.17
2018-05-21 22:30 | 39.53 | 38.82
2018-05-21 23:00 | 40.2 | 39.53
2018-05-21 23:30 | 36.92 | 36.17
2018-05-22 | 34.9 | 34.09
2018-05-22 00:30 | 33.95 | 33.1
2018-05-22 01:00 | 32.76 | 31.89
2018-05-22 01:30 | 32.24 | 31.34
2018-05-22 02:00 | 31.82 | 30.9
2018-05-22 02:30 | 31.56 | 30.62
2018-05-22 03:00 | 31.49 | 30.54
2018-05-22 03:30 | 31.48 | 30.53
2018-05-22 04:00 | 31.54 | 30.59
2018-05-22 04:30 | 32.22 | 31.29
2018-05-22 05:00 | 33.57 | 32.69
2018-05-22 05:30 | 36.32 | 35.53
2018-05-22 06:00 | 39.28 | 38.58
2018-05-22 06:30 | 43.73 | 43.14
2018-05-22 07:00 | 48.29 | 47.78
2018-05-22 07:30 | 52.3 | 51.87
2018-05-22 08:00 | 53.63 | 53.24
2018-05-22 08:30 | 52.2 | 51.81
2018-05-22 09:00 | 50.37 | 49.94
2018-05-22 09:30 | 49.27 | 48.79
2018-05-22 10:00 | 48.69 | 48.1
2018-05-22 10:30 | 48.78 | 47.89
2018-05-22 11:00 | 48.32 | 47.73
2018-05-22 11:30 | 48.01 | 47.48
2018-05-22 12:00 | 48.69 | 48.21
2018-05-22 12:30 | 49.27 | 48.86
2018-05-22 13:00 | 48.97 | 48.56
2018-05-22 13:30 | 48.54 | 48.13
2018-05-22 14:00 | 49.22 | 48.81
2018-05-22 14:30 | 49.35 | 48.95
2018-05-22 15:00 | 49.77 | 49.37
2018-05-22 15:30 | 50.25 | 49.84
2018-05-22 16:00 | 51 | 50.58
2018-05-22 16:30 | 52.2 | 51.77
2018-05-22 17:00 | 52.52 | 52.07
2018-05-22 17:30 | 52.35 | 51.87
2018-05-22 18:00 | 54.96 | 54.5
2018-05-22 18:30 | 56.22 | 55.76
2018-05-22 19:00 | 55.37 | 54.9
2018-05-22 19:30 | 52.79 | 52.28
2018-05-22 20:00 | 50.32 | 49.77
2018-05-22 20:30 | 47.98 | 47.39
2018-05-22 21:00 | 45.81 | 45.17
2018-05-22 21:30 | 43.7 | 43.02
2018-05-22 22:00 | 41.23 | 40.53
2018-05-22 22:30 | 39.48 | 38.8
2018-05-22 23:00 | 39.82 | 39.13
2018-05-22 23:30 | 36.82 | 36.06
2018-05-23 | 34.7 | 33.88
2018-05-23 00:30 | 34.06 | 33.21
2018-05-23 01:00 | 32.84 | 31.96
2018-05-23 01:30 | 32.21 | 31.31
2018-05-23 02:00 | 31.56 | 30.63
2018-05-23 02:30 | 31 | 30.04
2018-05-23 03:00 | 31.03 | 30.23
2018-05-23 03:30 | 31.01 | 30.36
2018-05-23 04:00 | 31.18 | 30.51
2018-05-23 04:30 | 31.9 | 31.26
2018-05-23 05:00 | 33.29 | 32.69
2018-05-23 05:30 | 36.39 | 35.79
2018-05-23 06:00 | 39.72 | 39.07
2018-05-23 06:30 | 45.08 | 44.48
2018-05-23 07:00 | 49.9 | 49.5
2018-05-23 07:30 | 54.2 | 53.73
2018-05-23 08:00 | 54.61 | 54.24
2018-05-23 08:30 | 52.67 | 52.29
2018-05-23 09:00 | 51.42 | 50.96
2018-05-23 09:30 | 49.45 | 48.98
2018-05-23 10:00 | 47.16 | 46.72
2018-05-23 10:30 | 46.68 | 46.19
2018-05-23 11:00 | 46.98 | 46.52
2018-05-23 11:30 | 46.99 | 46.55
2018-05-23 12:00 | 47.1 | 46.66
2018-05-23 12:30 | 48.45 | 48.03
2018-05-23 13:00 | 48.28 | 47.86
2018-05-23 13:30 | 48.44 | 48.02
2018-05-23 14:00 | 49.33 | 48.92
2018-05-23 14:30 | 49.69 | 49.29
2018-05-23 15:00 | 49.56 | 49.16
2018-05-23 15:30 | 50.97 | 50.56
2018-05-23 16:00 | 50.89 | 50.46
2018-05-23 16:30 | 53.19 | 52.77
2018-05-23 17:00 | 53.66 | 53.22
2018-05-23 17:30 | 53.59 | 53.13
2018-05-23 18:00 | 55.82 | 55.38
2018-05-23 18:30 | 56.76 | 56.31
2018-05-23 19:00 | 55.53 | 55.07
2018-05-23 19:30 | 52.88 | 52.38
2018-05-23 20:00 | 50.99 | 50.46
2018-05-23 20:30 | 48.58 | 48.01
2018-05-23 21:00 | 46.17 | 45.56
2018-05-23 21:30 | 43.95 | 43.29
2018-05-23 22:00 | 41.89 | 41.18
2018-05-23 22:30 | 39.6 | 38.91
2018-05-23 23:00 | 39.95 | 39.27
2018-05-23 23:30 | 36.86 | 36.11
2018-05-24 | 35.18 | 34.39
2018-05-24 00:30 | 34.07 | 33.23
2018-05-24 01:00 | 32.86 | 31.98
2018-05-24 01:30 | 32.07 | 31.16
2018-05-24 02:00 | 31.41 | 30.5
2018-05-24 02:30 | 30.93 | 30.2
2018-05-24 03:00 | 30.76 | 30.02
2018-05-24 03:30 | 30.97 | 30.25
2018-05-24 04:00 | 30.92 | 30.18
2018-05-24 04:30 | 31.36 | 30.63
2018-05-24 05:00 | 32.54 | 31.85
2018-05-24 05:30 | 35.31 | 34.7
2018-05-24 06:00 | 38.73 | 38.2
2018-05-24 06:30 | 43.99 | 43.43
2018-05-24 07:00 | 48.33 | 47.92
2018-05-24 07:30 | 53.05 | 52.53
2018-05-24 08:00 | 53.29 | 52.87
2018-05-24 08:30 | 51.78 | 51.4
2018-05-24 09:00 | 51.76 | 51.38
2018-05-24 09:30 | 52.32 | 51.91
2018-05-24 10:00 | 52.2 | 51.79
2018-05-24 10:30 | 51.25 | 50.84
2018-05-24 11:00 | 53.37 | 52.99
2018-05-24 11:30 | 55.08 | 54.72
2018-05-24 12:00 | 55.67 | 55.22
2018-05-24 12:30 | 57.09 | 55.53
2018-05-24 13:00 | 56.08 | 54.47
2018-05-24 13:30 | 55.92 | 54.31
2018-05-24 14:00 | 56.43 | 54.84
2018-05-24 14:30 | 56.08 | 54.47
2018-05-24 15:00 | 55.34 | 53.69
2018-05-24 15:30 | 55.08 | 53.4
2018-05-24 16:00 | 55.65 | 53.96
2018-05-24 16:30 | 56.2 | 54.48
2018-05-24 17:00 | 56.08 | 54.32
2018-05-24 17:30 | 56.54 | 54.75
2018-05-24 18:00 | 59.01 | 57.31
2018-05-24 18:30 | 59.72 | 58.03
2018-05-24 19:00 | 58.26 | 56.5
2018-05-24 19:30 | 56.06 | 54.2
2018-05-24 20:00 | 54.25 | 52.3
2018-05-24 20:30 | 51.87 | 49.79
2018-05-24 21:00 | 50.2 | 48.03
2018-05-24 21:30 | 47.29 | 44.92
2018-05-24 22:00 | 42.77 | 42.05
2018-05-24 22:30 | 40.31 | 40.19
2018-05-24 23:00 | 40.24 | 40.16
2018-05-24 23:30 | 37.62 | 37.61
2018-05-25 | 35.36 | 35.36
2018-05-25 00:30 | 34.08 | 34.07
2018-05-25 01:00 | 32.65 | 32.64
2018-05-25 01:30 | 31.92 | 31.91
2018-05-25 02:00 | 31.39 | 31.37
2018-05-25 02:30 | 30.89 | 30.85
2018-05-25 03:00 | 30.71 | 30.66
2018-05-25 03:30 | 31.15 | 31.11
2018-05-25 04:00 | 30.97 | 30.93
2018-05-25 04:30 | 31.37 | 31.33
2018-05-25 05:00 | 32.92 | 32.9
2018-05-25 05:30 | 35.5 | 35.5
2018-05-25 06:00 | 38.24 | 38.23
2018-05-25 06:30 | 43.51 | 43.39
2018-05-25 07:00 | 47.47 | 47.21
2018-05-25 07:30 | 53.43 | 52.44
2018-05-25 08:00 | 55.07 | 53.51
2018-05-25 08:30 | 42.48 | 40.21
2018-05-25 09:00 | 39.89 | 37.41
2018-05-25 09:30 | 38.83 | 36.26
2018-05-25 10:00 | 37.55 | 34.9
2018-05-25 10:30 | 35.23 | 32.42
2018-05-25 11:00 | 33.6 | 30.67
2018-05-25 11:30 | 33.74 | 30.84
2018-05-25 12:00 | 34.61 | 31.8
2018-05-25 12:30 | 36.29 | 33.62
2018-05-25 13:00 | 39.29 | 36.85
2018-05-25 13:30 | 50.39 | 48.56
2018-05-25 14:00 | 51.32 | 49.51
2018-05-25 14:30 | 51.41 | 49.59
2018-05-25 15:00 | 50.99 | 49.14
2018-05-25 15:30 | 51.52 | 49.66
2018-05-25 16:00 | 52.31 | 50.45
2018-05-25 16:30 | 53.26 | 51.38
2018-05-25 17:00 | 52.75 | 50.82
2018-05-25 17:30 | 52.13 | 50.12
2018-05-25 18:00 | 53.65 | 51.7
2018-05-25 18:30 | 54.19 | 52.24
2018-05-25 19:00 | 52.91 | 50.89
2018-05-25 19:30 | 50.56 | 48.41
2018-05-25 20:00 | 48.62 | 46.35
2018-05-25 20:30 | 47.2 | 44.86
2018-05-25 21:00 | 44.98 | 42.62
2018-05-25 21:30 | 43.17 | 40.67
2018-05-25 22:00 | 41.14 | 38.47
2018-05-25 22:30 | 39.87 | 37.07
2018-05-25 23:00 | 39.97 | 37.26
2018-05-25 23:30 | 34.26 | 34.19
2018-05-26 | 32.48 | 32.41
2018-05-26 00:30 | 31.48 | 31.39
2018-05-26 01:00 | 30.17 | 30.06
2018-05-26 01:30 | 29.59 | 29.49
2018-05-26 02:00 | 28.92 | 28.85
2018-05-26 02:30 | 28.3 | 28.27
2018-05-26 03:00 | 28.02 | 28
2018-05-26 03:30 | 27.81 | 27.79
2018-05-26 04:00 | 28.08 | 28.07
2018-05-26 04:30 | 28.32 | 28.3
2018-05-26 05:00 | 28.31 | 28.3
2018-05-26 05:30 | 29.65 | 29.62
2018-05-26 06:00 | 30.81 | 30.76
2018-05-26 06:30 | 33.32 | 33.21
2018-05-26 07:00 | 35.15 | 34.99
2018-05-26 07:30 | 37.25 | 37.02
2018-05-26 08:00 | 40.36 | 40.01
2018-05-26 08:30 | 42.24 | 41.73
2018-05-26 09:00 | 43.23 | 42.54
2018-05-26 09:30 | 43.55 | 42.16
2018-05-26 10:00 | 43.89 | 41.94
2018-05-26 10:30 | 43.39 | 41.34
2018-05-26 11:00 | 42.45 | 40.3
2018-05-26 11:30 | 41.81 | 39.62
2018-05-26 12:00 | 41.12 | 38.88
2018-05-26 12:30 | 41.65 | 39.41
2018-05-26 13:00 | 41.62 | 39.36
2018-05-26 13:30 | 40.28 | 37.92
2018-05-26 14:00 | 39.93 | 37.52
2018-05-26 14:30 | 39.35 | 36.89
2018-05-26 15:00 | 40.39 | 37.98
2018-05-26 15:30 | 41.24 | 38.85
2018-05-26 16:00 | 42.16 | 39.82
2018-05-26 16:30 | 43.99 | 41.73
2018-05-26 17:00 | 43.93 | 41.66
2018-05-26 17:30 | 44.87 | 42.64
2018-05-26 18:00 | 47.17 | 45.1
2018-05-26 18:30 | 48.23 | 46.21
2018-05-26 19:00 | 46.75 | 44.64
2018-05-26 19:30 | 44.7 | 42.47
2018-05-26 20:00 | 43.19 | 40.86
2018-05-26 20:30 | 41.9 | 39.47
2018-05-26 21:00 | 40.77 | 38.26
2018-05-26 21:30 | 39.41 | 36.78
2018-05-26 22:00 | 38.49 | 35.74
2018-05-26 22:30 | 37.45 | 34.6
2018-05-26 23:00 | 37.83 | 35.12
2018-05-26 23:30 | 35.09 | 32.21
2018-05-27 | 33.88 | 30.87
2018-05-27 00:30 | 33.07 | 29.93
2018-05-27 01:00 | 32.19 | 28.94
2018-05-27 01:30 | 31.44 | 28.11
2018-05-27 02:00 | 30.89 | 27.47
2018-05-27 02:30 | 30.51 | 27.03
2018-05-27 03:00 | 30.51 | 27.01
2018-05-27 03:30 | 30.67 | 27.19
2018-05-27 04:00 | 30.4 | 26.88
2018-05-27 04:30 | 30.56 | 27.08
2018-05-27 05:00 | 30.86 | 27.42
2018-05-27 05:30 | 31.24 | 27.86
2018-05-27 06:00 | 31.96 | 28.69
2018-05-27 06:30 | 32.89 | 29.72
2018-05-27 07:00 | 33.61 | 30.51
2018-05-27 07:30 | 34.91 | 31.97
2018-05-27 08:00 | 36.47 | 33.71
2018-05-27 08:30 | 37.96 | 35.36
2018-05-27 09:00 | 38.92 | 36.42
2018-05-27 09:30 | 38.41 | 35.9
2018-05-27 10:00 | 38.72 | 36.26
2018-05-27 10:30 | 37.85 | 35.37
2018-05-27 11:00 | 37.21 | 34.71
2018-05-27 11:30 | 36.75 | 34.23
2018-05-27 12:00 | 36.72 | 34.19
2018-05-27 12:30 | 38.63 | 36.22
2018-05-27 13:00 | 36.8 | 34.26
2018-05-27 13:30 | 36.37 | 33.82
2018-05-27 14:00 | 36.8 | 34.06
2018-05-27 14:30 | 37.04 | 34.29
2018-05-27 15:00 | 37.57 | 34.86
2018-05-27 15:30 | 38.44 | 35.79
2018-05-27 16:00 | 39.96 | 37.41
2018-05-27 16:30 | 41.61 | 39.17
2018-05-27 17:00 | 43.13 | 40.78
2018-05-27 17:30 | 45.34 | 43.13
2018-05-27 18:00 | 48.47 | 46.46
2018-05-27 18:30 | 50.09 | 48.16
2018-05-27 19:00 | 48.89 | 46.89
2018-05-27 19:30 | 46.77 | 44.64
2018-05-27 20:00 | 44.61 | 42.34
2018-05-27 20:30 | 42.87 | 40.48
2018-05-27 21:00 | 41.29 | 38.78
2018-05-27 21:30 | 39.64 | 36.97
2018-05-27 22:00 | 37.85 | 35.06
2018-05-27 22:30 | 36.34 | 33.58
2018-05-27 23:00 | 36.93 | 34.22
2018-05-27 23:30 | 34.22 | 31.23
2018-05-28 | 33 | 29.88
2018-05-28 00:30 | 32.27 | 29.03
2018-05-28 01:00 | 31.37 | 28.03
2018-05-28 01:30 | 31.12 | 27.72
2018-05-28 02:00 | 31.04 | 27.63
2018-05-28 02:30 | 30.93 | 27.5
2018-05-28 03:00 | 30.63 | 27.16
2018-05-28 03:30 | 30.86 | 27.42
2018-05-28 04:00 | 30.98 | 27.56
2018-05-28 04:30 | 32 | 28.73
2018-05-28 05:00 | 32.91 | 29.77
2018-05-28 05:30 | 35.04 | 32.16
2018-05-28 06:00 | 37.89 | 35.31
2018-05-28 06:30 | 42.51 | 40.36
2018-05-28 07:00 | 47.01 | 45.06
2018-05-28 07:30 | 51.81 | 50.11
2018-05-28 08:00 | 54.42 | 52.88
2018-05-28 08:30 | 55.61 | 54.14
2018-05-28 09:00 | 55.44 | 53.95
2018-05-28 09:30 | 54.85 | 53.16
2018-05-28 10:00 | 53.95 | 52.25
2018-05-28 10:30 | 53.64 | 51.96
2018-05-28 11:00 | 54.75 | 53.14
2018-05-28 11:30 | 53.84 | 52.2
2018-05-28 12:00 | 54.39 | 52.78
2018-05-28 12:30 | 56.13 | 54.58
2018-05-28 13:00 | 54.68 | 53.07
2018-05-28 13:30 | 56.15 | 54.61
2018-05-28 14:00 | 57.5 | 55.97
2018-05-28 14:30 | 55.79 | 54.21
2018-05-28 15:00 | 57.13 | 55.58
2018-05-28 15:30 | 56.19 | 54.58
2018-05-28 16:00 | 56.04 | 54.41
2018-05-28 16:30 | 57.34 | 55.71
2018-05-28 17:00 | 56.57 | 54.87
2018-05-28 17:30 | 56.61 | 54.83
2018-05-28 18:00 | 58.35 | 56.62
2018-05-28 18:30 | 59.13 | 57.41
2018-05-28 19:00 | 58.13 | 56.36
2018-05-28 19:30 | 55.73 | 53.87
2018-05-28 20:00 | 53.55 | 51.58
2018-05-28 20:30 | 50.96 | 48.85
2018-05-28 21:00 | 48.78 | 46.55
2018-05-28 21:30 | 46.83 | 44.45
2018-05-28 22:00 | 43.06 | 41.63
2018-05-28 22:30 | 39.94 | 39.67
2018-05-28 23:00 | 40.33 | 40.23
2018-05-28 23:30 | 37.56 | 37.41
2018-05-29 | 35.57 | 35.53
2018-05-29 00:30 | 34.4 | 34.4
2018-05-29 01:00 | 33.28 | 33.28
2018-05-29 01:30 | 32.71 | 32.71
2018-05-29 02:00 | 32.12 | 32.11
2018-05-29 02:30 | 31.46 | 31.45
2018-05-29 03:00 | 31.26 | 31.24
2018-05-29 03:30 | 31.23 | 31.2
2018-05-29 04:00 | 31.58 | 31.56
2018-05-29 04:30 | 32.1 | 32.08
2018-05-29 05:00 | 33.48 | 33.47
2018-05-29 05:30 | 34.7 | 34.7
2018-05-29 06:00 | 37.66 | 37.66
2018-05-29 06:30 | 42.88 | 42.79
2018-05-29 07:00 | 48.15 | 47.89
2018-05-29 07:30 | 53.18 | 52.24
2018-05-29 08:00 | 56.12 | 54.66
2018-05-29 08:30 | 55.99 | 54.57
2018-05-29 09:00 | 55.05 | 53.4
2018-05-29 09:30 | 54.41 | 52.72
2018-05-29 10:00 | 53.12 | 51.38
2018-05-29 10:30 | 53.08 | 51.37
2018-05-29 11:00 | 53.58 | 51.92
2018-05-29 11:30 | 53.76 | 52.13
2018-05-29 12:00 | 53.85 | 52.23
2018-05-29 12:30 | 54.72 | 53.12
2018-05-29 13:00 | 53.77 | 52.13
2018-05-29 13:30 | 53.53 | 51.89
2018-05-29 14:00 | 54.11 | 52.49
2018-05-29 14:30 | 54.62 | 53.04
2018-05-29 15:00 | 54.99 | 53.4
2018-05-29 15:30 | 54.98 | 53.35
2018-05-29 16:00 | 56.92 | 55.34
2018-05-29 16:30 | 57 | 55.37
2018-05-29 17:00 | 56.14 | 54.42
2018-05-29 17:30 | 56.57 | 54.8
2018-05-29 18:00 | 56.91 | 55.13
2018-05-29 18:30 | 58.15 | 56.4
2018-05-29 19:00 | 57.25 | 55.45
2018-05-29 19:30 | 54.23 | 52.29
2018-05-29 20:00 | 51.63 | 49.54
2018-05-29 20:30 | 49.8 | 47.6
2018-05-29 21:00 | 47.41 | 45.06
2018-05-29 21:30 | 45.64 | 43.17
2018-05-29 22:00 | 44.36 | 41.79
2018-05-29 22:30 | 42.25 | 39.67
2018-05-29 23:00 | 42.42 | 39.86
2018-05-29 23:30 | 39.15 | 36.92
2018-05-30 | 33.94 | 33.67
2018-05-30 00:30 | 32.04 | 32
2018-05-30 01:00 | 31.63 | 31.59
2018-05-30 01:30 | 30.99 | 30.94
2018-05-30 02:00 | 30.73 | 30.64
2018-05-30 02:30 | 30.31 | 30.19
2018-05-30 03:00 | 30.95 | 30.81
2018-05-30 03:30 | 31.26 | 31.11
2018-05-30 04:00 | 31.35 | 31.19
2018-05-30 04:30 | 32.28 | 32.16
2018-05-30 05:00 | 33.32 | 33.23
2018-05-30 05:30 | 35.48 | 35.45
2018-05-30 06:00 | 38.14 | 38.13
2018-05-30 06:30 | 43.08 | 43.05
2018-05-30 07:00 | 47.7 | 47.54
2018-05-30 07:30 | 54.79 | 53.58
2018-05-30 08:00 | 56.14 | 54.52
2018-05-30 08:30 | 56.97 | 55.42
2018-05-30 09:00 | 55.27 | 53.64
2018-05-30 09:30 | 53.06 | 51.28
2018-05-30 10:00 | 52.62 | 50.84
2018-05-30 10:30 | 52.25 | 50.48
2018-05-30 11:00 | 52.75 | 51.03
2018-05-30 11:30 | 52.3 | 50.59
2018-05-30 12:00 | 51.94 | 50.79
2018-05-30 12:30 | 53.07 | 52.14
2018-05-30 13:00 | 52.62 | 51.69
2018-05-30 13:30 | 53.3 | 52.48
2018-05-30 14:00 | 53.4 | 52.63
2018-05-30 14:30 | 54.01 | 53.27
2018-05-30 15:00 | 54.69 | 53.82
2018-05-30 15:30 | 53.8 | 52.7
2018-05-30 16:00 | 54.06 | 52.61
2018-05-30 16:30 | 54.54 | 52.55
2018-05-30 17:00 | 55.05 | 52.63
2018-05-30 17:30 | 55.83 | 52.62
2018-05-30 18:00 | 56.91 | 53.49
2018-05-30 18:30 | 57.8 | 54.27
2018-05-30 19:00 | 57.04 | 53.29
2018-05-30 19:30 | 54.75 | 50.63
2018-05-30 20:00 | 52.97 | 48.4
2018-05-30 20:30 | 51.14 | 45.81
2018-05-30 21:00 | 49.48 | 43.53
2018-05-30 21:30 | 48.43 | 41.9
2018-05-30 22:00 | 47.02 | 39.89
2018-05-30 22:30 | 46.48 | 38.88
2018-05-30 23:00 | 45.44 | 38.29
2018-05-30 23:30 | 42.49 | 34.9
2018-05-31 | 40.72 | 32.72
2018-05-31 00:30 | 40.1 | 31.95
2018-05-31 01:00 | 39.18 | 30.77
2018-05-31 01:30 | 38.7 | 29.98
2018-05-31 02:00 | 38.5 | 29.46
2018-05-31 02:30 | 38.18 | 29.07
2018-05-31 03:00 | 38.03 | 28.89
2018-05-31 03:30 | 37.91 | 28.72
2018-05-31 04:00 | 38.05 | 28.9
2018-05-31 04:30 | 38.58 | 29.63
2018-05-31 05:00 | 39.27 | 30.55
2018-05-31 05:30 | 41.15 | 32.93
2018-05-31 06:00 | 43.61 | 35.96
2018-05-31 06:30 | 47.74 | 40.85
2018-05-31 07:00 | 51.41 | 45.2
2018-05-31 07:30 | 54.76 | 49.81
2018-05-31 08:00 | 54.62 | 51.46
2018-05-31 08:30 | 53.96 | 50.73
2018-05-31 09:00 | 52.76 | 49.41
2018-05-31 09:30 | 51.5 | 48.15
2018-05-31 10:00 | 50.3 | 46.83
2018-05-31 10:30 | 50.05 | 46.56
2018-05-31 11:00 | 47.97 | 45.91
2018-05-31 11:30 | 47.6 | 46.03
2018-05-31 12:00 | 47.51 | 45.99
2018-05-31 12:30 | 48.93 | 47.53
2018-05-31 13:00 | 48.16 | 46.72
2018-05-31 13:30 | 48.03 | 46.6
2018-05-31 14:00 | 48.38 | 47.02
2018-05-31 14:30 | 48.88 | 47.48
2018-05-31 15:00 | 49.04 | 47.68
2018-05-31 15:30 | 49.19 | 47.51
2018-05-31 16:00 | 50.38 | 48.48
2018-05-31 16:30 | 51.59 | 49.23
2018-05-31 17:00 | 52.4 | 49.48
2018-05-31 17:30 | 53.84 | 50.2
2018-05-31 18:00 | 56.51 | 52.89
2018-05-31 18:30 | 58.16 | 54.65
2018-05-31 19:00 | 57.36 | 53.62
2018-05-31 19:30 | 55.16 | 50.9
2018-05-31 20:00 | 50.34 | 48.77
2018-05-31 20:30 | 47.04 | 46.48
2018-05-31 21:00 | 45.28 | 44.69
2018-05-31 21:30 | 42.61 | 41.92
2018-05-31 22:00 | 40.84 | 40.12
2018-05-31 22:30 | 39.22 | 38.58
2018-05-31 23:00 | 39.35 | 38.7
2018-05-31 23:30 | 35.44 | 34.7
2018-06-01 | 33.14 | 32.33
2018-06-01 00:30 | 32.56 | 31.72
2018-06-01 01:00 | 31.49 | 30.62
2018-06-01 01:30 | 30.41 | 29.5
2018-06-01 02:00 | 30.27 | 29.36
2018-06-01 02:30 | 29.54 | 28.79
2018-06-01 03:00 | 28.98 | 28.25
2018-06-01 03:30 | 29.02 | 28.28
2018-06-01 04:00 | 29.35 | 28.61
2018-06-01 04:30 | 29.22 | 28.49
2018-06-01 05:00 | 31.24 | 30.56
2018-06-01 05:30 | 34.22 | 33.62
2018-06-01 06:00 | 37.64 | 37.12
2018-06-01 06:30 | 45.24 | 42.45
2018-06-01 07:00 | 50.81 | 46.69
2018-06-01 07:30 | 54.53 | 50.79
2018-06-01 08:00 | 54.23 | 50.55
2018-06-01 08:30 | 50.67 | 46.74
2018-06-01 09:00 | 51.86 | 47.86
2018-06-01 09:30 | 50.69 | 46.56
2018-06-01 10:00 | 49.06 | 44.76
2018-06-01 10:30 | 48.02 | 43.63
2018-06-01 11:00 | 46.75 | 42.29
2018-06-01 11:30 | 47.04 | 42.66
2018-06-01 12:00 | 47.13 | 42.77
2018-06-01 12:30 | 47.18 | 42.64
2018-06-01 13:00 | 47.24 | 42.59
2018-06-01 13:30 | 46.82 | 42.09
2018-06-01 14:00 | 46.42 | 41.66
2018-06-01 14:30 | 43.7 | 38.61
2018-06-01 15:00 | 47.88 | 43.26
2018-06-01 15:30 | 47.5 | 42.77
2018-06-01 16:00 | 48.43 | 43.73
2018-06-01 16:30 | 50.55 | 46
2018-06-01 17:00 | 51.55 | 47.07
2018-06-01 17:30 | 51.53 | 46.97
2018-06-01 18:00 | 53.99 | 49.69
2018-06-01 18:30 | 55.28 | 51.09
2018-06-01 19:00 | 54.01 | 49.66
2018-06-01 19:30 | 52.33 | 47.77
2018-06-01 20:00 | 50.77 | 46.01
2018-06-01 20:30 | 49.37 | 44.42
2018-06-01 21:00 | 47.95 | 42.76
2018-06-01 21:30 | 46.24 | 40.78
2018-06-01 22:00 | 43.86 | 38.2
2018-06-01 22:30 | 42.12 | 36.24
2018-06-01 23:00 | 43.17 | 37.43
2018-06-01 23:30 | 40.19 | 33.85
2018-06-02 | 38.77 | 32.32
2018-06-02 00:30 | 37.42 | 30.78
2018-06-02 01:00 | 36.43 | 29.53
2018-06-02 01:30 | 35 | 28.04
2018-06-02 02:00 | 34.83 | 27.9
2018-06-02 02:30 | 34.79 | 27.83
2018-06-02 03:00 | 34.62 | 27.59
2018-06-02 03:30 | 33.92 | 26.68
2018-06-02 04:00 | 33.88 | 26.62
2018-06-02 04:30 | 33.98 | 26.77
2018-06-02 05:00 | 34.72 | 27.7
2018-06-02 05:30 | 35.89 | 29.22
2018-06-02 06:00 | 36.59 | 30.1
2018-06-02 06:30 | 38.9 | 32.96
2018-06-02 07:00 | 40.59 | 34.99
2018-06-02 07:30 | 42.64 | 37.42
2018-06-02 08:00 | 43.94 | 38.99
2018-06-02 08:30 | 44.51 | 39.68
2018-06-02 09:00 | 43.99 | 39.15
2018-06-02 09:30 | 42.97 | 38.01
2018-06-02 10:00 | 41.94 | 36.85
2018-06-02 10:30 | 40.38 | 35.07
2018-06-02 11:00 | 39.53 | 34.12
2018-06-02 11:30 | 38.6 | 33.05
2018-06-02 12:00 | 38.35 | 32.74
2018-06-02 12:30 | 38.63 | 33.02
2018-06-02 13:00 | 36.82 | 30.84
2018-06-02 13:30 | 36.51 | 30.47
2018-06-02 14:00 | 36.93 | 30.96
2018-06-02 14:30 | 37.3 | 31.37
2018-06-02 15:00 | 37.34 | 31.42
2018-06-02 15:30 | 38.42 | 32.67
2018-06-02 16:00 | 39.99 | 34.52
2018-06-02 16:30 | 41.99 | 36.8
2018-06-02 17:00 | 43.78 | 38.86
2018-06-02 17:30 | 45.6 | 40.92
2018-06-02 18:00 | 48.36 | 44.06
2018-06-02 18:30 | 49.56 | 45.41
2018-06-02 19:00 | 48.2 | 43.88
2018-06-02 19:30 | 46.42 | 41.86
2018-06-02 20:00 | 45.32 | 40.6
2018-06-02 20:30 | 43.85 | 38.9
2018-06-02 21:00 | 42.59 | 37.44
2018-06-02 21:30 | 41.69 | 36.37
2018-06-02 22:00 | 40.72 | 35.21
2018-06-02 22:30 | 39.87 | 34.18
2018-06-02 23:00 | 40.73 | 35.15
2018-06-02 23:30 | 38.09 | 32.01
2018-06-03 | 35.98 | 29.36
2018-06-03 00:30 | 36.16 | 29.53
2018-06-03 01:00 | 35.74 | 29.05
2018-06-03 01:30 | 34.99 | 28.07
2018-06-03 02:00 | 34.01 | 26.78
2018-06-03 02:30 | 33.67 | 26.32
2018-06-03 03:00 | 33.76 | 26.45
2018-06-03 03:30 | 34.57 | 27.47
2018-06-03 04:00 | 34.5 | 27.37
2018-06-03 04:30 | 34.63 | 27.56
2018-06-03 05:00 | 35.03 | 28.08
2018-06-03 05:30 | 35.13 | 28.23
2018-06-03 06:00 | 35.17 | 28.27
2018-06-03 06:30 | 36.58 | 30.02
2018-06-03 07:00 | 37.64 | 31.29
2018-06-03 07:30 | 38.59 | 32.47
2018-06-03 08:00 | 40.11 | 34.31
2018-06-03 08:30 | 39.37 | 33.46
2018-06-03 09:00 | 38.76 | 32.78
2018-06-03 09:30 | 38.59 | 32.63
2018-06-03 10:00 | 37.64 | 31.51
2018-06-03 10:30 | 37 | 30.77
2018-06-03 11:00 | 36.21 | 29.84
2018-06-03 11:30 | 35.3 | 28.73
2018-06-03 12:00 | 34.89 | 28.23
2018-06-03 12:30 | 36 | 29.63
2018-06-03 13:00 | 35.82 | 29.42
2018-06-03 13:30 | 35.22 | 28.7
2018-06-03 14:00 | 35.22 | 28.69
2018-06-03 14:30 | 35.65 | 29.22
2018-06-03 15:00 | 36.65 | 30.44
2018-06-03 15:30 | 37.1 | 30.99
2018-06-03 16:00 | 38.44 | 32.58
2018-06-03 16:30 | 40.88 | 35.45
2018-06-03 17:00 | 42.65 | 37.51
2018-06-03 17:30 | 45.43 | 40.69
2018-06-03 18:00 | 49.7 | 45.52
2018-06-03 18:30 | 51.75 | 47.8
2018-06-03 19:00 | 50.65 | 46.58
2018-06-03 19:30 | 48.65 | 44.34
2018-06-03 20:00 | 46.67 | 42.1
2018-06-03 20:30 | 45.17 | 40.37
2018-06-03 21:00 | 43.32 | 38.22
2018-06-03 21:30 | 41.7 | 36.3
2018-06-03 22:00 | 40.5 | 34.88
2018-06-03 22:30 | 39.1 | 33.18
2018-06-03 23:00 | 39.74 | 33.95
2018-06-03 23:30 | 37.09 | 30.72
2018-06-04 | 35.37 | 28.52
2018-06-04 00:30 | 35.23 | 28.32
2018-06-04 01:00 | 34.4 | 27.25
2018-06-04 01:30 | 33.86 | 26.56
2018-06-04 02:00 | 33.34 | 25.89
2018-06-04 02:30 | 33.55 | 26.11
2018-06-04 03:00 | 33.44 | 25.96
2018-06-04 03:30 | 33.69 | 26.3
2018-06-04 04:00 | 33.89 | 26.56
2018-06-04 04:30 | 34.54 | 27.42
2018-06-04 05:00 | 35.61 | 28.81
2018-06-04 05:30 | 38.21 | 32.07
2018-06-04 06:00 | 41.24 | 35.76
2018-06-04 06:30 | 45.59 | 40.87
2018-06-04 07:00 | 50.67 | 46.48
2018-06-04 07:30 | 56.12 | 52.44
2018-06-04 08:00 | 57.02 | 53.49
2018-06-04 08:30 | 54.67 | 50.99
2018-06-04 09:00 | 51.87 | 47.97
2018-06-04 09:30 | 50.05 | 46.02
2018-06-04 10:00 | 48.3 | 44.13
2018-06-04 10:30 | 47.2 | 42.93
2018-06-04 11:00 | 47.44 | 42.99
2018-06-04 11:30 | 48.8 | 44.42
2018-06-04 12:00 | 49.07 | 44.62
2018-06-04 12:30 | 49.07 | 44.61
2018-06-04 13:00 | 47.75 | 43.16
2018-06-04 13:30 | 48.17 | 43.66
2018-06-04 14:00 | 49.02 | 44.61
2018-06-04 14:30 | 49.05 | 44.62
2018-06-04 15:00 | 49.52 | 45.14
2018-06-04 15:30 | 49.89 | 45.5
2018-06-04 16:00 | 51.24 | 46.93
2018-06-04 16:30 | 53.11 | 48.91
2018-06-04 17:00 | 53.37 | 49.11
2018-06-04 17:30 | 53.41 | 49.08
2018-06-04 18:00 | 57.04 | 53.04
2018-06-04 18:30 | 58.48 | 54.59
2018-06-04 19:00 | 58.07 | 54.15
2018-06-04 19:30 | 55.18 | 50.98
2018-06-04 20:00 | 53.18 | 48.73
2018-06-04 20:30 | 50.84 | 46.11
2018-06-04 21:00 | 48.26 | 43.19
2018-06-04 21:30 | 46.34 | 40.94
2018-06-04 22:00 | 44.32 | 38.81
2018-06-04 22:30 | 42.48 | 36.72
2018-06-04 23:00 | 42.45 | 36.65
2018-06-04 23:30 | 40.26 | 34.05
2018-06-05 | 38.68 | 32.09
2018-06-05 00:30 | 37.89 | 31.09
2018-06-05 01:00 | 36.74 | 29.7
2018-06-05 01:30 | 36.81 | 29.74
2018-06-05 02:00 | 36.25 | 29
2018-06-05 02:30 | 35.57 | 28.07
2018-06-05 03:00 | 33.63 | 28.44
2018-06-05 03:30 | 28.79 | 27.78
2018-06-05 04:00 | 29.18 | 28.33
2018-06-05 04:30 | 29.85 | 29.03
2018-06-05 05:00 | 31 | 30.21
2018-06-05 05:30 | 33.52 | 32.81
2018-06-05 06:00 | 36.72 | 36.1
2018-06-05 06:30 | 42.18 | 41.68
2018-06-05 07:00 | 47.45 | 47
2018-06-05 07:30 | 52 | 51.6
2018-06-05 08:00 | 52.6 | 52.22
2018-06-05 08:30 | 51.25 | 50.36
2018-06-05 09:00 | 50.12 | 48.41
2018-06-05 09:30 | 48.25 | 46.48
2018-06-05 10:00 | 46.99 | 45.19
2018-06-05 10:30 | 46.66 | 44.88
2018-06-05 11:00 | 46.78 | 44.91
2018-06-05 11:30 | 46.77 | 44.88
2018-06-05 12:00 | 46.45 | 44.56
2018-06-05 12:30 | 45.41 | 43.49
2018-06-05 13:00 | 46.15 | 44.24
2018-06-05 13:30 | 46.29 | 44.4
2018-06-05 14:00 | 46.72 | 44.86
2018-06-05 14:30 | 47.52 | 45.69
2018-06-05 15:00 | 47.86 | 46.03
2018-06-05 15:30 | 48.94 | 47.12
2018-06-05 16:00 | 50.61 | 48.83
2018-06-05 16:30 | 51.52 | 49.73
2018-06-05 17:00 | 51.04 | 49.19
2018-06-05 17:30 | 51.73 | 49.84
2018-06-05 18:00 | 53.67 | 51.87
2018-06-05 18:30 | 55.12 | 53.36
2018-06-05 19:00 | 54.36 | 52.56
2018-06-05 19:30 | 52.13 | 50.23
2018-06-05 20:00 | 48.93 | 46.87
2018-06-05 20:30 | 48.19 | 46.05
2018-06-05 21:00 | 45.91 | 43.64
2018-06-05 21:30 | 43.31 | 40.85
2018-06-05 22:00 | 41.3 | 38.83
2018-06-05 22:30 | 39.56 | 36.97
2018-06-05 23:00 | 39.3 | 36.68
2018-06-05 23:30 | 37.21 | 34.4
2018-06-06 | 34.96 | 31.91
2018-06-06 00:30 | 34.25 | 31.1
2018-06-06 01:00 | 32.93 | 29.61
2018-06-06 01:30 | 32.32 | 28.92
2018-06-06 02:00 | 32.84 | 29.49
2018-06-06 02:30 | 32.11 | 28.65
2018-06-06 03:00 | 31.78 | 28.27
2018-06-06 03:30 | 30.48 | 27.05
2018-06-06 04:00 | 30.42 | 26.97
2018-06-06 04:30 | 31.81 | 28.56
2018-06-06 05:00 | 32.57 | 29.43
2018-06-06 05:30 | 34.51 | 31.61
2018-06-06 06:00 | 37.57 | 34.98
2018-06-06 06:30 | 42.61 | 40.46
2018-06-06 07:00 | 47.83 | 45.88
2018-06-06 07:30 | 52.39 | 50.67
2018-06-06 08:00 | 53.93 | 52.31
2018-06-06 08:30 | 53.37 | 51.77
2018-06-06 09:00 | 51.23 | 49.6
2018-06-06 09:30 | 49.54 | 47.85
2018-06-06 10:00 | 49.16 | 47.48
2018-06-06 10:30 | 48.54 | 46.81
2018-06-06 11:00 | 48 | 46.17
2018-06-06 11:30 | 47.98 | 46.16
2018-06-06 12:00 | 47.61 | 45.79
2018-06-06 12:30 | 48.21 | 46.4
2018-06-06 13:00 | 47.99 | 46.16
2018-06-06 13:30 | 49.1 | 47.33
2018-06-06 14:00 | 48.93 | 47.15
2018-06-06 14:30 | 49.12 | 47.36
2018-06-06 15:00 | 49.3 | 47.52
2018-06-06 15:30 | 49.93 | 48.16
2018-06-06 16:00 | 50.13 | 48.32
2018-06-06 16:30 | 51.82 | 50.03
2018-06-06 17:00 | 51.28 | 49.43
2018-06-06 17:30 | 51.73 | 49.84
2018-06-06 18:00 | 53.67 | 51.85
2018-06-06 18:30 | 55.47 | 53.72
2018-06-06 19:00 | 54.74 | 52.93
2018-06-06 19:30 | 52.78 | 50.87
2018-06-06 20:00 | 50.21 | 48.17
2018-06-06 20:30 | 47.33 | 45.11
2018-06-06 21:00 | 43.61 | 41.14
2018-06-06 21:30 | 42.57 | 40.01
2018-06-06 22:00 | 40.68 | 37.97
2018-06-06 22:30 | 40.24 | 37.47
2018-06-06 23:00 | 40.31 | 37.72
2018-06-06 23:30 | 36.84 | 33.97
2018-06-07 | 35.16 | 32.11
2018-06-07 00:30 | 34.66 | 31.54
2018-06-07 01:00 | 33.83 | 30.62
2018-06-07 01:30 | 33.48 | 30.2
2018-06-07 02:00 | 31.86 | 28.39
2018-06-07 02:30 | 31.04 | 27.47
2018-06-07 03:00 | 30.7 | 27.28
2018-06-07 03:30 | 30.45 | 27.01
2018-06-07 04:00 | 30.21 | 26.99
2018-06-07 04:30 | 31.18 | 28.09
2018-06-07 05:00 | 32.38 | 29.44
2018-06-07 05:30 | 34.75 | 32.08
2018-06-07 06:00 | 38.1 | 35.72
2018-06-07 06:30 | 42.83 | 40.85
2018-06-07 07:00 | 46.44 | 44.62
2018-06-07 07:30 | 50.37 | 48.74
2018-06-07 08:00 | 52.72 | 51.06
2018-06-07 08:30 | 51.47 | 49.79
2018-06-07 09:00 | 49.67 | 47.94
2018-06-07 09:30 | 48.37 | 46.61
2018-06-07 10:00 | 47.65 | 45.88
2018-06-07 10:30 | 42.75 | 40.76
2018-06-07 11:00 | 47.87 | 46.03
2018-06-07 11:30 | 48.17 | 46.35
2018-06-07 12:00 | 46.75 | 44.89
2018-06-07 12:30 | 47.65 | 45.82
2018-06-07 13:00 | 46.1 | 44.19
2018-06-07 13:30 | 46.93 | 45.06
2018-06-07 14:00 | 47.53 | 45.69
2018-06-07 14:30 | 47.78 | 45.96
2018-06-07 15:00 | 47.76 | 45.91
2018-06-07 15:30 | 48.17 | 46.31
2018-06-07 16:00 | 49.76 | 47.94
2018-06-07 16:30 | 52.01 | 50.24
2018-06-07 17:00 | 52.1 | 50.29
2018-06-07 17:30 | 52.33 | 50.48
2018-06-07 18:00 | 55.41 | 53.68
2018-06-07 18:30 | 56.89 | 55.19
2018-06-07 19:00 | 55.06 | 53.35
2018-06-07 19:30 | 51.6 | 49.78
2018-06-07 20:00 | 49.74 | 47.82
2018-06-07 20:30 | 48.03 | 46.02
2018-06-07 21:00 | 45.58 | 43.42
2018-06-07 21:30 | 42.56 | 40.18
2018-06-07 22:00 | 39.92 | 37.32
2018-06-07 22:30 | 38.57 | 36.04
2018-06-07 23:00 | 38.71 | 36.21
2018-06-07 23:30 | 35.86 | 33.1
2018-06-08 | 34.09 | 31.15
2018-06-08 00:30 | 34.04 | 31.07
2018-06-08 01:00 | 32.7 | 29.57
2018-06-08 01:30 | 31.73 | 28.48
2018-06-08 02:00 | 30.74 | 27.36
2018-06-08 02:30 | 30.04 | 26.74
2018-06-08 03:00 | 29.51 | 26.2
2018-06-08 03:30 | 29.67 | 26.39
2018-06-08 04:00 | 29.72 | 26.44
2018-06-08 04:30 | 30.51 | 27.34
2018-06-08 05:00 | 32.33 | 29.38
2018-06-08 05:30 | 34.34 | 31.63
2018-06-08 06:00 | 36.43 | 33.95
2018-06-08 06:30 | 41.17 | 39.1
2018-06-08 07:00 | 49.54 | 43.35
2018-06-08 07:30 | 59.18 | 48.16
2018-06-08 08:00 | 61.3 | 50.98
2018-06-08 08:30 | 60.47 | 50.12
2018-06-08 09:00 | 60.16 | 49.77
2018-06-08 09:30 | 59.4 | 48.88
2018-06-08 10:00 | 58.59 | 47.43
2018-06-08 10:30 | 59.64 | 48.79
2018-06-08 11:00 | 59.73 | 48.92
2018-06-08 11:30 | 58.49 | 47.22
2018-06-08 12:00 | 57.95 | 46.56
2018-06-08 12:30 | 59.94 | 49.04
2018-06-08 13:00 | 57.6 | 46.05
2018-06-08 13:30 | 57.3 | 45.66
2018-06-08 14:00 | 57.81 | 46.26
2018-06-08 14:30 | 58.75 | 47.32
2018-06-08 15:00 | 58 | 46.27
2018-06-08 15:30 | 58.49 | 46.78
2018-06-08 16:00 | 61.09 | 49.96
2018-06-08 16:30 | 61.67 | 50.54
2018-06-08 17:00 | 61.5 | 50.26
2018-06-08 17:30 | 61.21 | 49.8
2018-06-08 18:00 | 62.85 | 51.87
2018-06-08 18:30 | 62.47 | 51.31
2018-06-08 19:00 | 61.09 | 49.58
2018-06-08 19:30 | 59.47 | 47.55
2018-06-08 20:00 | 57.12 | 44.9
2018-06-08 20:30 | 55.36 | 42.5
2018-06-08 21:00 | 54 | 40.62
2018-06-08 21:30 | 52.97 | 39.12
2018-06-08 22:00 | 48.73 | 38.22
2018-06-08 22:30 | 41.68 | 36.27
2018-06-08 23:00 | 41.8 | 36.52
2018-06-08 23:30 | 39.57 | 33.89
2018-06-09 | 37.19 | 31.03
2018-06-09 00:30 | 36.36 | 29.98
2018-06-09 01:00 | 35.08 | 28.33
2018-06-09 01:30 | 35.12 | 28.38
2018-06-09 02:00 | 34.55 | 27.67
2018-06-09 02:30 | 33.93 | 26.9
2018-06-09 03:00 | 33.99 | 26.89
2018-06-09 03:30 | 33.66 | 26.46
2018-06-09 04:00 | 34.44 | 27.46
2018-06-09 04:30 | 34.68 | 27.8
2018-06-09 05:00 | 34.97 | 28.18
2018-06-09 05:30 | 35.8 | 29.23
2018-06-09 06:00 | 36.38 | 29.98
2018-06-09 06:30 | 37.68 | 31.64
2018-06-09 07:00 | 39.15 | 33.43
2018-06-09 07:30 | 41.04 | 35.7
2018-06-09 08:00 | 42.26 | 37.17
2018-06-09 08:30 | 43.67 | 38.85
2018-06-09 09:00 | 44.95 | 40.38
2018-06-09 09:30 | 44.67 | 40.11
2018-06-09 10:00 | 44.25 | 39.65
2018-06-09 10:30 | 43.85 | 39.26
2018-06-09 11:00 | 43.1 | 38.46
2018-06-09 11:30 | 42.02 | 37.22
2018-06-09 12:00 | 40.99 | 36.01
2018-06-09 12:30 | 41.24 | 36.28
2018-06-09 13:00 | 39.89 | 34.66
2018-06-09 13:30 | 39.61 | 34.23
2018-06-09 14:00 | 39.65 | 34.02
2018-06-09 14:30 | 39.54 | 33.81
2018-06-09 15:00 | 40.69 | 35.13
2018-06-09 15:30 | 41.65 | 36.23
2018-06-09 16:00 | 42.36 | 37.02
2018-06-09 16:30 | 43.8 | 38.64
2018-06-09 17:00 | 44.81 | 39.76
2018-06-09 17:30 | 47 | 42.23
2018-06-09 18:00 | 48.77 | 44.27
2018-06-09 18:30 | 49.67 | 45.25
2018-06-09 19:00 | 48.83 | 44.31
2018-06-09 19:30 | 46.06 | 41.17
2018-06-09 20:00 | 44.42 | 39.26
2018-06-09 20:30 | 43.99 | 38.72
2018-06-09 21:00 | 43 | 37.58
2018-06-09 21:30 | 42.21 | 36.63
2018-06-09 22:00 | 40.69 | 34.8
2018-06-09 22:30 | 38.76 | 32.73
2018-06-09 23:00 | 39.32 | 33.49
2018-06-09 23:30 | 36.84 | 30.49
2018-06-10 | 35.8 | 29.17
2018-06-10 00:30 | 35.64 | 28.92
2018-06-10 01:00 | 34.13 | 27
2018-06-10 01:30 | 33.74 | 26.51
2018-06-10 02:00 | 33.26 | 25.86
2018-06-10 02:30 | 33.48 | 26.13
2018-06-10 03:00 | 33.58 | 26.25
2018-06-10 03:30 | 33.46 | 26.09
2018-06-10 04:00 | 33.19 | 25.74
2018-06-10 04:30 | 33.39 | 26.05
2018-06-10 05:00 | 33.94 | 26.73
2018-06-10 05:30 | 33.89 | 26.67
2018-06-10 06:00 | 34.02 | 26.84
2018-06-10 06:30 | 35.17 | 28.34
2018-06-10 07:00 | 35.57 | 28.8
2018-06-10 07:30 | 37.49 | 31.18
2018-06-10 08:00 | 39.67 | 33.81
2018-06-10 08:30 | 40.63 | 35
2018-06-10 09:00 | 40.54 | 34.98
2018-06-10 09:30 | 40.22 | 34.67
2018-06-10 10:00 | 40 | 34.49
2018-06-10 10:30 | 39.54 | 34.01
2018-06-10 11:00 | 39.14 | 33.6
2018-06-10 11:30 | 38.8 | 33.22
2018-06-10 12:00 | 38.51 | 32.91
2018-06-10 12:30 | 40.31 | 35.01
2018-06-10 13:00 | 39.4 | 33.96
2018-06-10 13:30 | 39.15 | 33.67
2018-06-10 14:00 | 39.05 | 33.54
2018-06-10 14:30 | 39.12 | 33.58
2018-06-10 15:00 | 40.04 | 34.67
2018-06-10 15:30 | 39.43 | 33.91
2018-06-10 16:00 | 40.01 | 34.58
2018-06-10 16:30 | 42.26 | 37.16
2018-06-10 17:00 | 43.28 | 38.33
2018-06-10 17:30 | 45.97 | 41.34
2018-06-10 18:00 | 49.11 | 44.9
2018-06-10 18:30 | 50.71 | 46.66
2018-06-10 19:00 | 50.65 | 46.59
2018-06-10 19:30 | 48.76 | 44.48
2018-06-10 20:00 | 45.96 | 41.32
2018-06-10 20:30 | 43.88 | 38.93
2018-06-10 21:00 | 43.12 | 38.04
2018-06-10 21:30 | 40.97 | 35.55
2018-06-10 22:00 | 39.62 | 33.94
2018-06-10 22:30 | 38.17 | 32.2
2018-06-10 23:00 | 38.87 | 33.02
2018-06-10 23:30 | 37.06 | 30.83
2018-06-11 | 36.07 | 29.58
2018-06-11 00:30 | 35.61 | 28.94
2018-06-11 01:00 | 34.62 | 27.74
2018-06-11 01:30 | 34 | 26.83
2018-06-11 02:00 | 34.32 | 27.24
2018-06-11 02:30 | 33.76 | 26.47
2018-06-11 03:00 | 33.39 | 26.02
2018-06-11 03:30 | 33.36 | 26
2018-06-11 04:00 | 33.52 | 26.21
2018-06-11 04:30 | 34.37 | 27.34
2018-06-11 05:00 | 36.04 | 29.48
2018-06-11 05:30 | 37.99 | 31.93
2018-06-11 06:00 | 40.31 | 34.78
2018-06-11 06:30 | 44.61 | 39.86
2018-06-11 07:00 | 47.8 | 43.55
2018-06-11 07:30 | 52.8 | 48.86
2018-06-11 08:00 | 54.04 | 50.07
2018-06-11 08:30 | 53.17 | 49.17
2018-06-11 09:00 | 51.94 | 47.88
2018-06-11 09:30 | 51 | 46.91
2018-06-11 10:00 | 50.69 | 46.41
2018-06-11 10:30 | 51.16 | 46.91
2018-06-11 11:00 | 51.21 | 47.04
2018-06-11 11:30 | 51.79 | 47.73
2018-06-11 12:00 | 51.63 | 47.59
2018-06-11 12:30 | 52.57 | 48.62
2018-06-11 13:00 | 52.16 | 48.17
2018-06-11 13:30 | 51.87 | 47.85
2018-06-11 14:00 | 52.42 | 48.46
2018-06-11 14:30 | 53.33 | 49.43
2018-06-11 15:00 | 53.12 | 49.18
2018-06-11 15:30 | 54.27 | 50.37
2018-06-11 16:00 | 54.81 | 50.91
2018-06-11 16:30 | 55.45 | 51.51
2018-06-11 17:00 | 55.61 | 51.63
2018-06-11 17:30 | 55.13 | 51.02
2018-06-11 18:00 | 56.48 | 52.45
2018-06-11 18:30 | 57.99 | 54.07
2018-06-11 19:00 | 57.72 | 53.76
2018-06-11 19:30 | 55.09 | 50.85
2018-06-11 20:00 | 52.82 | 48.34
2018-06-11 20:30 | 50.08 | 45.21
2018-06-11 21:00 | 47.66 | 42.47
2018-06-11 21:30 | 46.55 | 41.17
2018-06-11 22:00 | 44.73 | 39.01
2018-06-11 22:30 | 38.06 | 36.07
2018-06-11 23:00 | 37.01 | 36.31
2018-06-11 23:30 | 34.14 | 33.37
2018-06-12 | 31.62 | 30.97
2018-06-12 00:30 | 30.51 | 29.84
2018-06-12 01:00 | 29.64 | 28.95
2018-06-12 01:30 | 29.22 | 28.52
2018-06-12 02:00 | 29.42 | 28.71
2018-06-12 02:30 | 28.49 | 27.76
2018-06-12 03:00 | 28.28 | 27.53
2018-06-12 03:30 | 27.86 | 27.1
2018-06-12 04:00 | 27.84 | 27.07
2018-06-12 04:30 | 28.57 | 27.82
2018-06-12 05:00 | 29.72 | 29.01
2018-06-12 05:30 | 32.58 | 31.96
2018-06-12 06:00 | 35.38 | 34.82
2018-06-12 06:30 | 41.02 | 40.57
2018-06-12 07:00 | 48.32 | 44.84
2018-06-12 07:30 | 53.7 | 49.86
2018-06-12 08:00 | 54.04 | 50.31
2018-06-12 08:30 | 53.47 | 49.69
2018-06-12 09:00 | 52.73 | 48.79
2018-06-12 09:30 | 51.75 | 47.76
2018-06-12 10:00 | 51.1 | 46.92
2018-06-12 10:30 | 51.48 | 47.32
2018-06-12 11:00 | 51.61 | 47.52
2018-06-12 11:30 | 51.73 | 47.71
2018-06-12 12:00 | 51.99 | 48.02
2018-06-12 12:30 | 53.03 | 49.16
2018-06-12 13:00 | 52.57 | 48.65
2018-06-12 13:30 | 53.33 | 49.5
2018-06-12 14:00 | 53.82 | 50.05
2018-06-12 14:30 | 54 | 50.23
2018-06-12 15:00 | 54.76 | 51.03
2018-06-12 15:30 | 55.45 | 51.73
2018-06-12 16:00 | 57.14 | 53.5
2018-06-12 16:30 | 58.15 | 54.49
2018-06-12 17:00 | 57.1 | 53.29
2018-06-12 17:30 | 57.01 | 53.11
2018-06-12 18:00 | 59.59 | 55.88
2018-06-12 18:30 | 59.35 | 55.6
2018-06-12 19:00 | 58.86 | 55.05
2018-06-12 19:30 | 56.22 | 52.19
2018-06-12 20:00 | 53.34 | 49.01
2018-06-12 20:30 | 51.77 | 47.21
2018-06-12 21:00 | 49.93 | 45.13
2018-06-12 21:30 | 48.67 | 43.67
2018-06-12 22:00 | 45.18 | 39.87
2018-06-12 22:30 | 43.03 | 37.75
2018-06-12 23:00 | 43.31 | 38.05
2018-06-12 23:30 | 40.91 | 35.21
2018-06-13 | 38.96 | 32.85
2018-06-13 00:30 | 38.13 | 31.8
2018-06-13 01:00 | 37.78 | 31.42
2018-06-13 01:30 | 37.06 | 30.47
2018-06-13 02:00 | 35.96 | 29.09
2018-06-13 02:30 | 35.47 | 28.41
2018-06-13 03:00 | 35.56 | 28.48
2018-06-13 03:30 | 35.36 | 28.21
2018-06-13 04:00 | 35.52 | 28.41
2018-06-13 04:30 | 36.24 | 29.37
2018-06-13 05:00 | 37.32 | 30.73
2018-06-13 05:30 | 39.12 | 32.98
2018-06-13 06:00 | 42.21 | 36.7
2018-06-13 06:30 | 46.77 | 42.07
2018-06-13 07:00 | 51.18 | 47.06
2018-06-13 07:30 | 56.52 | 52.99
2018-06-13 08:00 | 58.3 | 55
2018-06-13 08:30 | 57.56 | 54.26
2018-06-13 09:00 | 55.7 | 52.3
2018-06-13 09:30 | 53.93 | 50.4
2018-06-13 10:00 | 53.77 | 49.86
2018-06-13 10:30 | 53.88 | 49.98
2018-06-13 11:00 | 54.79 | 51.03
2018-06-13 11:30 | 52.57 | 48.7
2018-06-13 12:00 | 55.24 | 51.6
2018-06-13 12:30 | 55.81 | 52.21
2018-06-13 13:00 | 54.4 | 50.68
2018-06-13 13:30 | 55.14 | 51.5
2018-06-13 14:00 | 55.31 | 51.68
2018-06-13 14:30 | 56.85 | 53.34
2018-06-13 15:00 | 56.78 | 53.24
2018-06-13 15:30 | 57.05 | 53.5
2018-06-13 16:00 | 57.37 | 53.8
2018-06-13 16:30 | 58.22 | 54.62
2018-06-13 17:00 | 58.79 | 55.16
2018-06-13 17:30 | 57.5 | 53.65
2018-06-13 18:00 | 58.74 | 54.95
2018-06-13 18:30 | 59.65 | 55.9
2018-06-13 19:00 | 58.41 | 54.55
2018-06-13 19:30 | 56.62 | 52.59
2018-06-13 20:00 | 54.62 | 50.38
2018-06-13 20:30 | 52.19 | 47.66
2018-06-13 21:00 | 50.04 | 45.24
2018-06-13 21:30 | 48.73 | 43.93
2018-06-13 22:00 | 45.88 | 40.77
2018-06-13 22:30 | 44.29 | 38.94
2018-06-13 23:00 | 44.28 | 39.06
2018-06-13 23:30 | 41.15 | 35.54
2018-06-14 | 39.74 | 33.86
2018-06-14 00:30 | 38.64 | 32.51
2018-06-14 01:00 | 37.26 | 30.78
2018-06-14 01:30 | 36.52 | 29.84
2018-06-14 02:00 | 35.99 | 29.18
2018-06-14 02:30 | 35.44 | 28.4
2018-06-14 03:00 | 35.02 | 27.83
2018-06-14 03:30 | 34.41 | 27.43
2018-06-14 04:00 | 34.5 | 27.56
2018-06-14 04:30 | 35.18 | 28.43
2018-06-14 05:00 | 36.29 | 29.85
2018-06-14 05:30 | 38.38 | 32.49
2018-06-14 06:00 | 40.65 | 35.2
2018-06-14 06:30 | 44.84 | 40.15
2018-06-14 07:00 | 49.35 | 45.07
2018-06-14 07:30 | 53.4 | 49.58
2018-06-14 08:00 | 55.05 | 51.25
2018-06-14 08:30 | 54.68 | 50.88
2018-06-14 09:00 | 53.3 | 49.41
2018-06-14 09:30 | 52.92 | 48.91
2018-06-14 10:00 | 53.31 | 49.25
2018-06-14 10:30 | 54.04 | 50.12
2018-06-14 11:00 | 54.47 | 50.65
2018-06-14 11:30 | 54.77 | 51.04
2018-06-14 12:00 | 55.21 | 51.55
2018-06-14 12:30 | 56.24 | 52.66
2018-06-14 13:00 | 55.75 | 52.12
2018-06-14 13:30 | 56.24 | 52.69
2018-06-14 14:00 | 56.57 | 53.06
2018-06-14 14:30 | 57.48 | 54.05
2018-06-14 15:00 | 57.15 | 53.64
2018-06-14 15:30 | 57.92 | 54.45
2018-06-14 16:00 | 59.16 | 55.72
2018-06-14 16:30 | 59.27 | 55.74
2018-06-14 17:00 | 57.96 | 54.24
2018-06-14 17:30 | 58.52 | 54.75
2018-06-14 18:00 | 60.47 | 56.84
2018-06-14 18:30 | 62.57 | 59.07
2018-06-14 19:00 | 61.42 | 57.83
2018-06-14 19:30 | 58.64 | 54.79
2018-06-14 20:00 | 56.06 | 51.95
2018-06-14 20:30 | 53.21 | 48.78
2018-06-14 21:00 | 51.26 | 46.6
2018-06-14 21:30 | 48.97 | 43.97
2018-06-14 22:00 | 46.21 | 40.8
2018-06-14 22:30 | 45.32 | 40.07
2018-06-14 23:00 | 44.94 | 39.88
2018-06-14 23:30 | 42.82 | 37.44
2018-06-15 | 40.98 | 35.3
2018-06-15 00:30 | 39.26 | 33.21
2018-06-15 01:00 | 38.61 | 32.41
2018-06-15 01:30 | 37.57 | 31.11
2018-06-15 02:00 | 36.66 | 30.03
2018-06-15 02:30 | 36.17 | 29.33
2018-06-15 03:00 | 36.32 | 29.81
2018-06-15 03:30 | 36.05 | 29.59
2018-06-15 04:00 | 35.84 | 29.28
2018-06-15 04:30 | 36.87 | 30.56
2018-06-15 05:00 | 38.54 | 32.6
2018-06-15 05:30 | 39.85 | 34.21
2018-06-15 06:00 | 42.55 | 37.45
2018-06-15 06:30 | 46.63 | 42.14
2018-06-15 07:00 | 51.01 | 46.91
2018-06-15 07:30 | 57.33 | 52.55
2018-06-15 08:00 | 59.15 | 52.76
2018-06-15 08:30 | 58.13 | 51.58
2018-06-15 09:00 | 57.8 | 51.32
2018-06-15 09:30 | 57.23 | 50.72
2018-06-15 10:00 | 56.99 | 50.1
2018-06-15 10:30 | 58.77 | 52.08
2018-06-15 11:00 | 59.06 | 52.47
2018-06-15 11:30 | 57.7 | 50.97
2018-06-15 12:00 | 58.53 | 51.94
2018-06-15 12:30 | 56.77 | 49.99
2018-06-15 13:00 | 58.3 | 51.65
2018-06-15 13:30 | 58.01 | 51.27
2018-06-15 14:00 | 58.36 | 51.65
2018-06-15 14:30 | 57.82 | 50.98
2018-06-15 15:00 | 58.03 | 51.19
2018-06-15 15:30 | 56.29 | 49.05
2018-06-15 16:00 | 57.13 | 49.89
2018-06-15 16:30 | 58.71 | 51.6
2018-06-15 17:00 | 58.33 | 51.12
2018-06-15 17:30 | 58.23 | 50.89
2018-06-15 18:00 | 58.29 | 50.92
2018-06-15 18:30 | 58.97 | 51.89
2018-06-15 19:00 | 57.1 | 50.02
2018-06-15 19:30 | 55.58 | 48.37
2018-06-15 20:00 | 53.3 | 45.61
2018-06-15 20:30 | 52.21 | 44.25
2018-06-15 21:00 | 50.77 | 42.48
2018-06-15 21:30 | 49.64 | 41.05
2018-06-15 22:00 | 47.14 | 37.87
2018-06-15 22:30 | 45.68 | 36.34
2018-06-15 23:00 | 46.48 | 37.34
2018-06-15 23:30 | 44.05 | 34.12
2018-06-16 | 42.5 | 31.97
2018-06-16 00:30 | 41.88 | 31.1
2018-06-16 01:00 | 40.86 | 29.62
2018-06-16 01:30 | 40.65 | 29.3
2018-06-16 02:00 | 40.25 | 28.7
2018-06-16 02:30 | 39.94 | 28.21
2018-06-16 03:00 | 39.71 | 27.84
2018-06-16 03:30 | 39.95 | 28.22
2018-06-16 04:00 | 39.69 | 27.79
2018-06-16 04:30 | 40.3 | 28.72
2018-06-16 05:00 | 38.78 | 26.68
2018-06-16 05:30 | 41.02 | 29.8
2018-06-16 06:00 | 41.41 | 30.36
2018-06-16 06:30 | 43.02 | 32.65
2018-06-16 07:00 | 44.02 | 34.02
2018-06-16 07:30 | 46.1 | 36.83
2018-06-16 08:00 | 48.13 | 39.43
2018-06-16 08:30 | 48.85 | 40.44
2018-06-16 09:00 | 49.18 | 40.91
2018-06-16 09:30 | 49.48 | 41.35
2018-06-16 10:00 | 48.81 | 40.57
2018-06-16 10:30 | 48.82 | 40.64
2018-06-16 11:00 | 48.58 | 40.42
2018-06-16 11:30 | 46.92 | 38.3
2018-06-16 12:00 | 46.17 | 37.02
2018-06-16 12:30 | 46.47 | 37.28
2018-06-16 13:00 | 44.58 | 34.8
2018-06-16 13:30 | 44.95 | 35.34
2018-06-16 14:00 | 46.7 | 37.52
2018-06-16 14:30 | 46.95 | 37.74
2018-06-16 15:00 | 46.06 | 36.53
2018-06-16 15:30 | 46.91 | 37.56
2018-06-16 16:00 | 48.13 | 39.06
2018-06-16 16:30 | 48.19 | 39.11
2018-06-16 17:00 | 48.27 | 39.19
2018-06-16 17:30 | 49.9 | 41.2
2018-06-16 18:00 | 52.79 | 44.83
2018-06-16 18:30 | 53.67 | 45.85
2018-06-16 19:00 | 52.49 | 44.4
2018-06-16 19:30 | 50.67 | 42.15
2018-06-16 20:00 | 49.6 | 40.8
2018-06-16 20:30 | 47.6 | 38.25
2018-06-16 21:00 | 46.28 | 36.55
2018-06-16 21:30 | 45.5 | 35.49
2018-06-16 22:00 | 41.43 | 33.86
2018-06-16 22:30 | 35.12 | 32.44
2018-06-16 23:00 | 36.34 | 33.75
2018-06-16 23:30 | 34.29 | 31.49
2018-06-17 | 32.87 | 29.92
2018-06-17 00:30 | 31.91 | 28.83
2018-06-17 01:00 | 31.07 | 27.93
2018-06-17 01:30 | 30.69 | 27.47
2018-06-17 02:00 | 29.18 | 25.74
2018-06-17 02:30 | 28.84 | 25.35
2018-06-17 03:00 | 28.85 | 25.36
2018-06-17 03:30 | 28.92 | 25.43
2018-06-17 04:00 | 29.47 | 26.05
2018-06-17 04:30 | 29.83 | 26.46
2018-06-17 05:00 | 30.01 | 26.68
2018-06-17 05:30 | 30.08 | 26.77
2018-06-17 06:00 | 30.79 | 27.59
2018-06-17 06:30 | 32 | 28.94
2018-06-17 07:00 | 32.25 | 29.21
2018-06-17 07:30 | 33.04 | 30.08
2018-06-17 08:00 | 34.44 | 31.64
2018-06-17 08:30 | 35.37 | 32.66
2018-06-17 09:00 | 37.19 | 34.67
2018-06-17 09:30 | 38.77 | 36.39
2018-06-17 10:00 | 38.5 | 36.11
2018-06-17 10:30 | 37.9 | 35.49
2018-06-17 11:00 | 36.71 | 34.23
2018-06-17 11:30 | 34.55 | 31.9
2018-06-17 12:00 | 34.16 | 31.48
2018-06-17 12:30 | 36.52 | 34.03
2018-06-17 13:00 | 35.21 | 32.62
2018-06-17 13:30 | 34.64 | 32.01
2018-06-17 14:00 | 34.65 | 32.02
2018-06-17 14:30 | 35.76 | 33.21
2018-06-17 15:00 | 36.65 | 34.16
2018-06-17 15:30 | 36.38 | 33.85
2018-06-17 16:00 | 36.82 | 34.32
2018-06-17 16:30 | 39.28 | 36.96
2018-06-17 17:00 | 39.46 | 37.15
2018-06-17 17:30 | 42.95 | 40.87
2018-06-17 18:00 | 47.5 | 44.5
2018-06-17 18:30 | 49.72 | 45.47
2018-06-17 19:00 | 48.23 | 43.8
2018-06-17 19:30 | 46.97 | 42.36
2018-06-17 20:00 | 45.52 | 40.71
2018-06-17 20:30 | 43.8 | 38.72
2018-06-17 21:00 | 41.62 | 36.19
2018-06-17 21:30 | 41.07 | 35.5
2018-06-17 22:00 | 39.26 | 33.33
2018-06-17 22:30 | 38.12 | 31.95
2018-06-17 23:00 | 38.02 | 31.81
2018-06-17 23:30 | 35.6 | 28.78
2018-06-18 | 34.11 | 26.86
2018-06-18 00:30 | 33.99 | 26.67
2018-06-18 01:00 | 33.25 | 25.72
2018-06-18 01:30 | 33.31 | 25.78
2018-06-18 02:00 | 33.19 | 25.63
2018-06-18 02:30 | 32.85 | 25.15
2018-06-18 03:00 | 32.59 | 24.79
2018-06-18 03:30 | 33.35 | 25.79
2018-06-18 04:00 | 32.81 | 25.08
2018-06-18 04:30 | 33.51 | 26.05
2018-06-18 05:00 | 34.64 | 27.55
2018-06-18 05:30 | 37.48 | 31.14
2018-06-18 06:00 | 40.67 | 35.04
2018-06-18 06:30 | 45.18 | 40.4
2018-06-18 07:00 | 49.52 | 45.26
2018-06-18 07:30 | 54.4 | 50.53
2018-06-18 08:00 | 56.15 | 52.53
2018-06-18 08:30 | 56.97 | 53.47
2018-06-18 09:00 | 55.02 | 51.4
2018-06-18 09:30 | 53.3 | 49.55
2018-06-18 10:00 | 51.05 | 47.12
2018-06-18 10:30 | 48.22 | 44.05
2018-06-18 11:00 | 47.82 | 43.42
2018-06-18 11:30 | 48.29 | 43.93
2018-06-18 12:00 | 48 | 43.6
2018-06-18 12:30 | 48.78 | 44.47
2018-06-18 13:00 | 48.83 | 44.29
2018-06-18 13:30 | 48.72 | 44.17
2018-06-18 14:00 | 49.11 | 44.61
2018-06-18 14:30 | 49.4 | 44.94
2018-06-18 15:00 | 49.8 | 45.36
2018-06-18 15:30 | 49.92 | 45.48
2018-06-18 16:00 | 50.77 | 46.36
2018-06-18 16:30 | 52.7 | 48.39
2018-06-18 17:00 | 53.25 | 48.93
2018-06-18 17:30 | 54.42 | 50.11
2018-06-18 18:00 | 57.63 | 53.6
2018-06-18 18:30 | 59.66 | 55.76
2018-06-18 19:00 | 58.71 | 54.72
2018-06-18 19:30 | 56.16 | 51.92
2018-06-18 20:00 | 54.17 | 49.7
2018-06-18 20:30 | 51.71 | 46.94
2018-06-18 21:00 | 49.19 | 44.08
2018-06-18 21:30 | 47.4 | 42.22
2018-06-18 22:00 | 45.25 | 39.82
2018-06-18 22:30 | 43.53 | 37.82
2018-06-18 23:00 | 43.71 | 38.02
2018-06-18 23:30 | 41.66 | 35.59
2018-06-19 | 37.89 | 33.73
2018-06-19 00:30 | 33.5 | 32.67
2018-06-19 01:00 | 31.89 | 31.01
2018-06-19 01:30 | 30.92 | 30.02
2018-06-19 02:00 | 29.84 | 28.83
2018-06-19 02:30 | 29.61 | 28.5
2018-06-19 03:00 | 29.2 | 28.05
2018-06-19 03:30 | 28.89 | 28.03
2018-06-19 04:00 | 29.04 | 28.28
2018-06-19 04:30 | 31.16 | 30.45
2018-06-19 05:00 | 32.57 | 31.9
2018-06-19 05:30 | 35.92 | 35.34
2018-06-19 06:00 | 39.19 | 38.68
2018-06-19 06:30 | 45.73 | 45.29
2018-06-19 07:00 | 51.34 | 50.96
2018-06-19 07:30 | 59.27 | 57.14
2018-06-19 08:00 | 60.71 | 57.26
2018-06-19 08:30 | 58.4 | 54.8
2018-06-19 09:00 | 54.81 | 50.96
2018-06-19 09:30 | 53.41 | 49.48
2018-06-19 10:00 | 51.71 | 47.64
2018-06-19 10:30 | 50.73 | 46.6
2018-06-19 11:00 | 49.03 | 44.74
2018-06-19 11:30 | 47.74 | 43.32
2018-06-19 12:00 | 47.48 | 43.03
2018-06-19 12:30 | 47.85 | 43.43
2018-06-19 13:00 | 46.92 | 42.39
2018-06-19 13:30 | 47.22 | 42.56
2018-06-19 14:00 | 48.45 | 43.89
2018-06-19 14:30 | 49.26 | 44.79
2018-06-19 15:00 | 48.67 | 44.13
2018-06-19 15:30 | 49.83 | 45.37
2018-06-19 16:00 | 51.16 | 46.82
2018-06-19 16:30 | 53.19 | 48.98
2018-06-19 17:00 | 54.13 | 49.92
2018-06-19 17:30 | 54.73 | 50.46
2018-06-19 18:00 | 58.23 | 54.26
2018-06-19 18:30 | 59.71 | 55.83
2018-06-19 19:00 | 59.4 | 55.47
2018-06-19 19:30 | 57.67 | 53.58
2018-06-19 20:00 | 55.55 | 51.25
2018-06-19 20:30 | 53.46 | 48.9
2018-06-19 21:00 | 51.01 | 46.14
2018-06-19 21:30 | 48.95 | 43.79
2018-06-19 22:00 | 46.73 | 41.49
2018-06-19 22:30 | 44.9 | 39.39
2018-06-19 23:00 | 45.72 | 40.3
2018-06-19 23:30 | 39.07 | 36.27
2018-06-20 | 34.29 | 33.49
2018-06-20 00:30 | 34.21 | 33.39
2018-06-20 01:00 | 31.85 | 30.98
2018-06-20 01:30 | 31.06 | 30.27
2018-06-20 02:00 | 30.1 | 29.26
2018-06-20 02:30 | 29.55 | 28.68
2018-06-20 03:00 | 29.85 | 28.99
2018-06-20 03:30 | 31 | 30.17
2018-06-20 04:00 | 31.1 | 30.27
2018-06-20 04:30 | 31.55 | 30.74
2018-06-20 05:00 | 32.55 | 31.77
2018-06-20 05:30 | 35.84 | 35.16
2018-06-20 06:00 | 38.91 | 38.3
2018-06-20 06:30 | 45.21 | 44.73
2018-06-20 07:00 | 51.25 | 50.87
2018-06-20 07:30 | 59.26 | 56.97
2018-06-20 08:00 | 61.87 | 58.54
2018-06-20 08:30 | 59.38 | 55.85
2018-06-20 09:00 | 55.65 | 51.86
2018-06-20 09:30 | 52.88 | 48.88
2018-06-20 10:00 | 50.7 | 46.5
2018-06-20 10:30 | 49.45 | 45.15
2018-06-20 11:00 | 48.64 | 44.28
2018-06-20 11:30 | 48.11 | 43.72
2018-06-20 12:00 | 47.59 | 43.15
2018-06-20 12:30 | 49.06 | 44.77
2018-06-20 13:00 | 47.87 | 43.42
2018-06-20 13:30 | 47.87 | 43.26
2018-06-20 14:00 | 48.6 | 44.01
2018-06-20 14:30 | 49.42 | 44.94
2018-06-20 15:00 | 50.09 | 45.7
2018-06-20 15:30 | 50.6 | 46.2
2018-06-20 16:00 | 52.08 | 47.78
2018-06-20 16:30 | 53.97 | 49.76
2018-06-20 17:00 | 55.49 | 51.35
2018-06-20 17:30 | 56.39 | 52.23
2018-06-20 18:00 | 58.78 | 54.82
2018-06-20 18:30 | 60.2 | 56.33
2018-06-20 19:00 | 59.02 | 55.04
2018-06-20 19:30 | 56.19 | 51.96
2018-06-20 20:00 | 54.42 | 50.01
2018-06-20 20:30 | 52.52 | 47.85
2018-06-20 21:00 | 50.89 | 46.02
2018-06-20 21:30 | 49.36 | 44.27
2018-06-20 22:00 | 45.41 | 43.55
2018-06-20 22:30 | 42.21 | 41.6
2018-06-20 23:00 | 41.73 | 41.11
2018-06-20 23:30 | 38.9 | 38.22
2018-06-21 | 36.84 | 36.11
2018-06-21 00:30 | 35.15 | 34.37
2018-06-21 01:00 | 33.5 | 32.66
2018-06-21 01:30 | 32.19 | 31.34
2018-06-21 02:00 | 31.16 | 30.36
2018-06-21 02:30 | 30.69 | 29.91
2018-06-21 03:00 | 31.43 | 30.73
2018-06-21 03:30 | 31.71 | 31.02
2018-06-21 04:00 | 30.49 | 29.76
2018-06-21 04:30 | 30.95 | 30.24
2018-06-21 05:00 | 31.68 | 30.99
2018-06-21 05:30 | 33.74 | 33.11
2018-06-21 06:00 | 35.66 | 35.08
2018-06-21 06:30 | 38.23 | 37.71
2018-06-21 07:00 | 40.08 | 39.59
2018-06-21 07:30 | 43.21 | 42.78
2018-06-21 08:00 | 44.06 | 43.64
2018-06-21 08:30 | 43.3 | 42.77
2018-06-21 09:00 | 44.54 | 42.64
2018-06-21 09:30 | 43.69 | 41.76
2018-06-21 10:00 | 42.22 | 40.23
2018-06-21 10:30 | 41.44 | 39.44
2018-06-21 11:00 | 40.21 | 38.15
2018-06-21 11:30 | 39.63 | 37.56
2018-06-21 12:00 | 39.35 | 37.27
2018-06-21 12:30 | 40.16 | 38.13
2018-06-21 13:00 | 39.8 | 37.75
2018-06-21 13:30 | 39.73 | 37.67
2018-06-21 14:00 | 40.31 | 38.28
2018-06-21 14:30 | 40.39 | 38.35
2018-06-21 15:00 | 39.96 | 37.9
2018-06-21 15:30 | 40.56 | 38.52
2018-06-21 16:00 | 42.45 | 40.5
2018-06-21 16:30 | 44.47 | 42.6
2018-06-21 17:00 | 45.36 | 43.52
2018-06-21 17:30 | 47.8 | 46.07
2018-06-21 18:00 | 52.57 | 51.05
2018-06-21 18:30 | 53.52 | 52.02
2018-06-21 19:00 | 51.83 | 50.26
2018-06-21 19:30 | 49.96 | 48.31
2018-06-21 20:00 | 47.89 | 46.14
2018-06-21 20:30 | 45.77 | 43.91
2018-06-21 21:00 | 43.62 | 41.64
2018-06-21 21:30 | 41.93 | 39.84
2018-06-21 22:00 | 41.11 | 38.94
2018-06-21 22:30 | 39.39 | 37.09
2018-06-21 23:00 | 38.89 | 36.55
2018-06-21 23:30 | 36.32 | 33.76
2018-06-22 | 34.67 | 31.96
2018-06-22 00:30 | 33.86 | 31.06
2018-06-22 01:00 | 32.49 | 29.57
2018-06-22 01:30 | 32.08 | 29.1
2018-06-22 02:00 | 31.63 | 28.6
2018-06-22 02:30 | 31.87 | 28.83
2018-06-22 03:00 | 31.85 | 28.81
2018-06-22 03:30 | 31.85 | 28.79
2018-06-22 04:00 | 31.42 | 28.33
2018-06-22 04:30 | 32.45 | 29.49
2018-06-22 05:00 | 33.35 | 30.51
2018-06-22 05:30 | 34.5 | 31.8
2018-06-22 06:00 | 36.3 | 33.78
2018-06-22 06:30 | 40.46 | 38.31
2018-06-22 07:00 | 44.42 | 42.44
2018-06-22 07:30 | 49.4 | 47.65
2018-06-22 08:00 | 53.75 | 51.01
2018-06-22 08:30 | 55.12 | 51.48
2018-06-22 09:00 | 54.92 | 51.31
2018-06-22 09:30 | 56.41 | 52.92
2018-06-22 10:00 | 53.6 | 49.9
2018-06-22 10:30 | 50.24 | 48.06
2018-06-22 11:00 | 49.4 | 47.55
2018-06-22 11:30 | 53.14 | 51.4
2018-06-22 12:00 | 50.73 | 48.91
2018-06-22 12:30 | 48.13 | 46.23
2018-06-22 13:00 | 50.82 | 49.01
2018-06-22 13:30 | 47.87 | 45.93
2018-06-22 14:00 | 47.88 | 45.95
2018-06-22 14:30 | 47.72 | 45.77
2018-06-22 15:00 | 47.2 | 45.19
2018-06-22 15:30 | 47.55 | 45.52
2018-06-22 16:00 | 48.69 | 46.69
2018-06-22 16:30 | 51.66 | 49.74
2018-06-22 17:00 | 52.28 | 50.35
2018-06-22 17:30 | 52.02 | 50.05
2018-06-22 18:00 | 53.91 | 52.03
2018-06-22 18:30 | 53.51 | 51.59
2018-06-22 19:00 | 51.54 | 49.52
2018-06-22 19:30 | 49.46 | 47.32
2018-06-22 20:00 | 47.91 | 45.69
2018-06-22 20:30 | 46.13 | 43.85
2018-06-22 21:00 | 42.68 | 42.53
2018-06-22 21:30 | 40.81 | 40.6
2018-06-22 22:00 | 39.22 | 39.01
2018-06-22 22:30 | 37.63 | 37.61
2018-06-22 23:00 | 37.81 | 37.77
2018-06-22 23:30 | 34.52 | 34.44
2018-06-23 | 31.97 | 31.85
2018-06-23 00:30 | 31.31 | 31.17
2018-06-23 01:00 | 29.67 | 29.49
2018-06-23 01:30 | 29.04 | 28.84
2018-06-23 02:00 | 28.18 | 28.15
2018-06-23 02:30 | 27.84 | 27.84
2018-06-23 03:00 | 28.56 | 28.56
2018-06-23 03:30 | 27.83 | 27.82
2018-06-23 04:00 | 27.13 | 27.13
2018-06-23 04:30 | 27.7 | 27.7
2018-06-23 05:00 | 27.96 | 27.96
2018-06-23 05:30 | 28.85 | 28.83
2018-06-23 06:00 | 30.36 | 30.33
2018-06-23 06:30 | 32.94 | 32.83
2018-06-23 07:00 | 34.59 | 34.48
2018-06-23 07:30 | 36.7 | 36.55
2018-06-23 08:00 | 37.98 | 37.76
2018-06-23 08:30 | 39.43 | 39.06
2018-06-23 09:00 | 40.41 | 39.9
2018-06-23 09:30 | 41.47 | 40.85
2018-06-23 10:00 | 40.15 | 39.47
2018-06-23 10:30 | 39.76 | 39.05
2018-06-23 11:00 | 37.5 | 36.7
2018-06-23 11:30 | 37.36 | 36.56
2018-06-23 12:00 | 35.62 | 34.81
2018-06-23 12:30 | 36.54 | 35.83
2018-06-23 13:00 | 34.12 | 33.43
2018-06-23 13:30 | 33.71 | 33.05
2018-06-23 14:00 | 34.66 | 34.1
2018-06-23 14:30 | 33.85 | 33.33
2018-06-23 15:00 | 33.97 | 33.54
2018-06-23 15:30 | 34.65 | 34.3
2018-06-23 16:00 | 35.87 | 35.59
2018-06-23 16:30 | 37.56 | 37.33
2018-06-23 17:00 | 39.13 | 38.94
2018-06-23 17:30 | 41.37 | 41.18
2018-06-23 18:00 | 44.04 | 43.79
2018-06-23 18:30 | 45.02 | 44.76
2018-06-23 19:00 | 44.38 | 44.13
2018-06-23 19:30 | 41.41 | 41.2
2018-06-23 20:00 | 39.81 | 39.63
2018-06-23 20:30 | 37.89 | 37.75
2018-06-23 21:00 | 36.42 | 36.31
2018-06-23 21:30 | 35.82 | 35.74
2018-06-23 22:00 | 35.37 | 35.3
2018-06-23 22:30 | 33.72 | 33.67
2018-06-23 23:00 | 33.49 | 33.47
2018-06-23 23:30 | 31.11 | 31.1
2018-06-24 | 29.33 | 29.32
2018-06-24 00:30 | 28.14 | 28.14
2018-06-24 01:00 | 26.96 | 26.96
2018-06-24 01:30 | 26.68 | 26.67
2018-06-24 02:00 | 27 | 27
2018-06-24 02:30 | 25.32 | 25.31
2018-06-24 03:00 | 25.29 | 25.28
2018-06-24 03:30 | 25.16 | 25.15
2018-06-24 04:00 | 25.09 | 25.08
2018-06-24 04:30 | 25.2 | 25.19
2018-06-24 05:00 | 25.36 | 25.36
2018-06-24 05:30 | 25.95 | 25.95
2018-06-24 06:00 | 27.5 | 27.5
2018-06-24 06:30 | 28.56 | 28.56
2018-06-24 07:00 | 28.3 | 28.29
2018-06-24 07:30 | 30.07 | 30.07
2018-06-24 08:00 | 30.78 | 30.78
2018-06-24 08:30 | 31.64 | 31.64
2018-06-24 09:00 | 32.09 | 32.07
2018-06-24 09:30 | 32.68 | 32.6
2018-06-24 10:00 | 32.52 | 32.41
2018-06-24 10:30 | 32.86 | 32.7
2018-06-24 11:00 | 32.09 | 31.89
2018-06-24 11:30 | 30.76 | 30.51
2018-06-24 12:00 | 30.85 | 30.58
2018-06-24 12:30 | 31.14 | 30.91
2018-06-24 13:00 | 30.31 | 30.1
2018-06-24 13:30 | 29.55 | 29.34
2018-06-24 14:00 | 29.62 | 29.41
2018-06-24 14:30 | 30.37 | 30.18
2018-06-24 15:00 | 30.62 | 30.45
2018-06-24 15:30 | 31.85 | 31.7
2018-06-24 16:00 | 33.87 | 33.75
2018-06-24 16:30 | 36.67 | 36.56
2018-06-24 17:00 | 37.83 | 37.74
2018-06-24 17:30 | 41.21 | 41.11
2018-06-24 18:00 | 45.17 | 45
2018-06-24 18:30 | 47.18 | 46.98
2018-06-24 19:00 | 45.93 | 45.74
2018-06-24 19:30 | 43.64 | 43.48
2018-06-24 20:00 | 40.71 | 40.59
2018-06-24 20:30 | 37.49 | 37.41
2018-06-24 21:00 | 36.89 | 36.82
2018-06-24 21:30 | 36.04 | 36
2018-06-24 22:00 | 34.13 | 34.11
2018-06-24 22:30 | 33.35 | 33.33
2018-06-24 23:00 | 34.46 | 34.44
2018-06-24 23:30 | 30.34 | 30.34
2018-06-25 | 28.19 | 28.19
2018-06-25 00:30 | 27.51 | 27.51
2018-06-25 01:00 | 26.93 | 26.93
2018-06-25 01:30 | 26.12 | 26.1
2018-06-25 02:00 | 26.07 | 26.05
2018-06-25 02:30 | 25.49 | 25.47
2018-06-25 03:00 | 26.11 | 26.09
2018-06-25 03:30 | 25.81 | 25.79
2018-06-25 04:00 | 25.64 | 25.62
2018-06-25 04:30 | 26.71 | 26.7
2018-06-25 05:00 | 28.01 | 28.01
2018-06-25 05:30 | 31.24 | 31.24
2018-06-25 06:00 | 34.76 | 34.69
2018-06-25 06:30 | 40.56 | 40.27
2018-06-25 07:00 | 45.18 | 44.8
2018-06-25 07:30 | 49.76 | 49.54
2018-06-25 08:00 | 51.3 | 50.92
2018-06-25 08:30 | 50.02 | 49.48
2018-06-25 09:00 | 48.17 | 47.48
2018-06-25 09:30 | 47.4 | 46.58
2018-06-25 10:00 | 46.71 | 45.79
2018-06-25 10:30 | 47.09 | 46.04
2018-06-25 11:00 | 47.33 | 46.88
2018-06-25 11:30 | 47.28 | 47.21
2018-06-25 12:00 | 45.7 | 45.6
2018-06-25 12:30 | 46.34 | 46.27
2018-06-25 13:00 | 44.56 | 44.49
2018-06-25 13:30 | 45.54 | 45.46
2018-06-25 14:00 | 47.76 | 47.69
2018-06-25 14:30 | 48.04 | 47.97
2018-06-25 15:00 | 48.13 | 48.09
2018-06-25 15:30 | 47.55 | 47.52
2018-06-25 16:00 | 48.38 | 48.38
2018-06-25 16:30 | 50.15 | 50.14
2018-06-25 17:00 | 49.9 | 49.86
2018-06-25 17:30 | 51.23 | 51.09
2018-06-25 18:00 | 53.34 | 53.22
2018-06-25 18:30 | 54.9 | 54.75
2018-06-25 19:00 | 53.82 | 53.62
2018-06-25 19:30 | 51.39 | 51.15
2018-06-25 20:00 | 49.21 | 48.92
2018-06-25 20:30 | 46.77 | 46.35
2018-06-25 21:00 | 44.36 | 43.83
2018-06-25 21:30 | 42.75 | 42.13
2018-06-25 22:00 | 40.4 | 39.61
2018-06-25 22:30 | 37.74 | 37.46
2018-06-25 23:00 | 37.98 | 37.69
2018-06-25 23:30 | 34.33 | 33.95
2018-06-26 | 32.21 | 31.69
2018-06-26 00:30 | 32.33 | 31.75
2018-06-26 01:00 | 30.76 | 30.25
2018-06-26 01:30 | 29.97 | 29.88
2018-06-26 02:00 | 29.77 | 29.68
2018-06-26 02:30 | 28.7 | 28.61
2018-06-26 03:00 | 28.06 | 28.05
2018-06-26 03:30 | 27.92 | 27.9
2018-06-26 04:00 | 27.5 | 27.48
2018-06-26 04:30 | 27.83 | 27.8
2018-06-26 05:00 | 29.21 | 29.15
2018-06-26 05:30 | 31.98 | 31.86
2018-06-26 06:00 | 35.02 | 34.83
2018-06-26 06:30 | 41.12 | 40.63
2018-06-26 07:00 | 45.49 | 45.21
2018-06-26 07:30 | 50.55 | 50.34
2018-06-26 08:00 | 53.78 | 53.63
2018-06-26 08:30 | 53.41 | 53.21
2018-06-26 09:00 | 54.16 | 53.86
2018-06-26 09:30 | 52.7 | 52.39
2018-06-26 10:00 | 52.07 | 51.73
2018-06-26 10:30 | 52.19 | 51.8
2018-06-26 11:00 | 52.11 | 51.65
2018-06-26 11:30 | 51.87 | 51.34
2018-06-26 12:00 | 53.95 | 53.41
2018-06-26 12:30 | 54.54 | 54.08
2018-06-26 13:00 | 51.66 | 51.21
2018-06-26 13:30 | 51.64 | 51.44
2018-06-26 14:00 | 52.51 | 52.43
2018-06-26 14:30 | 52.41 | 52.36
2018-06-26 15:00 | 51.41 | 51.37
2018-06-26 15:30 | 51.07 | 51.05
2018-06-26 16:00 | 51.41 | 51.41
2018-06-26 16:30 | 52.82 | 52.82
2018-06-26 17:00 | 52.83 | 52.82
2018-06-26 17:30 | 53.24 | 53.19
2018-06-26 18:00 | 55.1 | 55.04
2018-06-26 18:30 | 54.86 | 54.75
2018-06-26 19:00 | 54.14 | 54.01
2018-06-26 19:30 | 51.18 | 50.97
2018-06-26 20:00 | 48.48 | 48.2
2018-06-26 20:30 | 47.58 | 47.2
2018-06-26 21:00 | 46.22 | 45.66
2018-06-26 21:30 | 44.41 | 43.75
2018-06-26 22:00 | 41.59 | 41.14
2018-06-26 22:30 | 39.88 | 39.65
2018-06-26 23:00 | 39.97 | 39.71
2018-06-26 23:30 | 36.75 | 36.35
2018-06-27 | 34.59 | 34.09
2018-06-27 00:30 | 33.65 | 33.05
2018-06-27 01:00 | 31.49 | 30.83
2018-06-27 01:30 | 30.74 | 29.99
2018-06-27 02:00 | 31.6 | 28.88
2018-06-27 02:30 | 31.31 | 28.37
2018-06-27 03:00 | 30.75 | 27.67
2018-06-27 03:30 | 30.97 | 27.86
2018-06-27 04:00 | 30.92 | 27.8
2018-06-27 04:30 | 31.99 | 28.98
2018-06-27 05:00 | 32.48 | 29.51
2018-06-27 05:30 | 34.64 | 31.85
2018-06-27 06:00 | 37.47 | 34.89
2018-06-27 06:30 | 41.47 | 40.29
2018-06-27 07:00 | 45.11 | 44.68
2018-06-27 07:30 | 50.29 | 49.88
2018-06-27 08:00 | 52.25 | 52.07
2018-06-27 08:30 | 53.5 | 53.26
2018-06-27 09:00 | 53.1 | 52.75
2018-06-27 09:30 | 53.68 | 53.29
2018-06-27 10:00 | 54.28 | 53.89
2018-06-27 10:30 | 53.45 | 53.13
2018-06-27 11:00 | 53.43 | 53.28
2018-06-27 11:30 | 53.31 | 53.13
2018-06-27 12:00 | 52.62 | 52.45
2018-06-27 12:30 | 53.26 | 53.09
2018-06-27 13:00 | 53.01 | 52.87
2018-06-27 13:30 | 52.87 | 52.73
2018-06-27 14:00 | 51.58 | 51.44
2018-06-27 14:30 | 52.11 | 51.97
2018-06-27 15:00 | 52.04 | 51.92
2018-06-27 15:30 | 52.04 | 51.99
2018-06-27 16:00 | 53.63 | 53.6
2018-06-27 16:30 | 53.38 | 53.38
2018-06-27 17:00 | 52.62 | 52.62
2018-06-27 17:30 | 52.59 | 52.55
2018-06-27 18:00 | 54.26 | 54.21
2018-06-27 18:30 | 55.34 | 55.27
2018-06-27 19:00 | 54.09 | 53.99
2018-06-27 19:30 | 50.87 | 50.69
2018-06-27 20:00 | 49.46 | 49.22
2018-06-27 20:30 | 47.29 | 46.93
2018-06-27 21:00 | 44.47 | 44.01
2018-06-27 21:30 | 41.99 | 41.33
2018-06-27 22:00 | 39.21 | 38.69
2018-06-27 22:30 | 36.97 | 36.81
2018-06-27 23:00 | 36.91 | 36.9
2018-06-27 23:30 | 34.12 | 34.11
2018-06-28 | 32.51 | 32.48
2018-06-28 00:30 | 33.32 | 33.26
2018-06-28 01:00 | 32.07 | 31.99
2018-06-28 01:30 | 31.15 | 31.06
2018-06-28 02:00 | 28.42 | 28.28
2018-06-28 02:30 | 27.14 | 27.13
2018-06-28 03:00 | 27.68 | 27.67
2018-06-28 03:30 | 27.31 | 27.3
2018-06-28 04:00 | 27.73 | 27.72
2018-06-28 04:30 | 29.32 | 29.28
2018-06-28 05:00 | 30.63 | 30.58
2018-06-28 05:30 | 32.67 | 32.57
2018-06-28 06:00 | 35.17 | 34.97
2018-06-28 06:30 | 40.53 | 40.05
2018-06-28 07:00 | 44.56 | 44.37
2018-06-28 07:30 | 50 | 49.6
2018-06-28 08:00 | 53.04 | 52.6
2018-06-28 08:30 | 54.55 | 54.18
2018-06-28 09:00 | 53.44 | 53.06
2018-06-28 09:30 | 53.26 | 52.88
2018-06-28 10:00 | 51.58 | 51.18
2018-06-28 10:30 | 53.07 | 52.64
2018-06-28 11:00 | 51.15 | 50.72
2018-06-28 11:30 | 50.5 | 50.08
2018-06-28 12:00 | 50.26 | 49.83
2018-06-28 12:30 | 50.68 | 50.25
2018-06-28 13:00 | 49.83 | 49.4
2018-06-28 13:30 | 49 | 48.55
2018-06-28 14:00 | 49.48 | 49.04
2018-06-28 14:30 | 50.45 | 50.02
2018-06-28 15:00 | 52.77 | 52.35
2018-06-28 15:30 | 52.5 | 52.06
2018-06-28 16:00 | 52.86 | 52.42
2018-06-28 16:30 | 53.32 | 52.87
2018-06-28 17:00 | 52.52 | 52.04
2018-06-28 17:30 | 52.3 | 51.8
2018-06-28 18:00 | 54.87 | 54.39
2018-06-28 18:30 | 55.37 | 54.88
2018-06-28 19:00 | 54.25 | 53.75
2018-06-28 19:30 | 51.72 | 51.19
2018-06-28 20:00 | 49.61 | 49.04
2018-06-28 20:30 | 47.86 | 47.26
2018-06-28 21:00 | 45.33 | 44.74
2018-06-28 21:30 | 42.4 | 41.85
2018-06-28 22:00 | 40.2 | 39.6
2018-06-28 22:30 | 38.18 | 37.6
2018-06-28 23:00 | 38.34 | 37.78
2018-06-28 23:30 | 35.95 | 35.35
2018-06-29 | 34.41 | 33.78
2018-06-29 00:30 | 33.05 | 32.37
2018-06-29 01:00 | 31.01 | 30.28
2018-06-29 01:30 | 30.42 | 29.67
2018-06-29 02:00 | 29.39 | 28.6
2018-06-29 02:30 | 28.88 | 28.06
2018-06-29 03:00 | 28.05 | 27.2
2018-06-29 03:30 | 27.64 | 26.76
2018-06-29 04:00 | 28.24 | 27.4
2018-06-29 04:30 | 29.8 | 29.01
2018-06-29 05:00 | 30.94 | 30.18
2018-06-29 05:30 | 33.18 | 32.5
2018-06-29 06:00 | 36.32 | 35.73
2018-06-29 06:30 | 41.12 | 40.59
2018-06-29 07:00 | 45.39 | 44.91
2018-06-29 07:30 | 48.37 | 47.92
2018-06-29 08:00 | 50.67 | 50.1
2018-06-29 08:30 | 52.51 | 51.72
2018-06-29 09:00 | 52.6 | 52.12
2018-06-29 09:30 | 52.22 | 51.83
2018-06-29 10:00 | 51.96 | 51.54
2018-06-29 10:30 | 51.61 | 51.19
2018-06-29 11:00 | 50.49 | 50.06
2018-06-29 11:30 | 51.02 | 50.6
2018-06-29 12:00 | 51.33 | 50.92
2018-06-29 12:30 | 51.55 | 51.13
2018-06-29 13:00 | 48.68 | 48.23
2018-06-29 13:30 | 47.56 | 47.11
2018-06-29 14:00 | 47.83 | 47.37
2018-06-29 14:30 | 47.57 | 47.11
2018-06-29 15:00 | 47.28 | 46.81
2018-06-29 15:30 | 47.62 | 47.14
2018-06-29 16:00 | 48.84 | 48.36
2018-06-29 16:30 | 50.65 | 50.17
2018-06-29 17:00 | 50.33 | 49.82
2018-06-29 17:30 | 49.98 | 49.44
2018-06-29 18:00 | 51.59 | 51.06
2018-06-29 18:30 | 51.92 | 51.4
2018-06-29 19:00 | 50.85 | 50.42
2018-06-29 19:30 | 48.78 | 48.33
2018-06-29 20:00 | 46.13 | 45.64
2018-06-29 20:30 | 44.31 | 43.79
2018-06-29 21:00 | 42.32 | 41.76
2018-06-29 21:30 | 41.24 | 40.65
2018-06-29 22:00 | 39.13 | 38.49
2018-06-29 22:30 | 37.51 | 36.83
2018-06-29 23:00 | 37.64 | 37.02
2018-06-29 23:30 | 35.23 | 34.58
2018-06-30 | 33.7 | 33.01
2018-06-30 00:30 | 31.58 | 30.82
2018-06-30 01:00 | 29.93 | 29.12
2018-06-30 01:30 | 29.1 | 28.27
2018-06-30 02:00 | 28.56 | 27.7
2018-06-30 02:30 | 27.82 | 26.95
2018-06-30 03:00 | 27.76 | 26.87
2018-06-30 03:30 | 27.6 | 26.7
2018-06-30 04:00 | 27.82 | 26.94
2018-06-30 04:30 | 28.1 | 27.21
2018-06-30 05:00 | 28.51 | 27.64
2018-06-30 05:30 | 29.09 | 28.23
2018-06-30 06:00 | 30.34 | 29.5
2018-06-30 06:30 | 32.74 | 31.95
2018-06-30 07:00 | 33.43 | 32.66
2018-06-30 07:30 | 35.84 | 35.11
2018-06-30 08:00 | 37.5 | 36.79
2018-06-30 08:30 | 40.46 | 39.79
2018-06-30 09:00 | 42.52 | 41.87
2018-06-30 09:30 | 42.45 | 41.78
2018-06-30 10:00 | 40.66 | 39.91
2018-06-30 10:30 | 40.16 | 39.27
2018-06-30 11:00 | 38.9 | 37.96
2018-06-30 11:30 | 37.97 | 37.22
2018-06-30 12:00 | 37.3 | 36.6
2018-06-30 12:30 | 37.13 | 36.43
2018-06-30 13:00 | 35.94 | 35.22
2018-06-30 13:30 | 34.63 | 33.89
2018-06-30 14:00 | 35.22 | 34.5
2018-06-30 14:30 | 35.73 | 35.02
2018-06-30 15:00 | 35.63 | 34.94
2018-06-30 15:30 | 36.51 | 35.85
2018-06-30 16:00 | 36.11 | 35.44
2018-06-30 16:30 | 39.24 | 38.63
2018-06-30 17:00 | 40.98 | 40.4
2018-06-30 17:30 | 41.89 | 41.33
2018-06-30 18:00 | 43.96 | 43.43
2018-06-30 18:30 | 45.17 | 44.65
2018-06-30 19:00 | 43.72 | 43.19
2018-06-30 19:30 | 41.9 | 41.34
2018-06-30 20:00 | 40.23 | 39.65
2018-06-30 20:30 | 38.84 | 38.24
2018-06-30 21:00 | 37.54 | 36.93
2018-06-30 21:30 | 36.62 | 36
2018-06-30 22:00 | 35.77 | 35.14
2018-06-30 22:30 | 33.85 | 33.19
2018-06-30 23:00 | 34.99 | 34.36
2018-06-30 23:30 | 31.99 | 31.23
2018-07-01 | 30.74 | 29.93
2018-07-01 00:30 | 30.2 | 29.38
2018-07-01 01:00 | 28.85 | 28
2018-07-01 01:30 | 28.21 | 27.33
2018-07-01 02:00 | 27.96 | 27.08
2018-07-01 02:30 | 28.08 | 27.2
2018-07-01 03:00 | 27.66 | 26.77
2018-07-01 03:30 | 27.95 | 27.07
2018-07-01 04:00 | 27.26 | 26.36
2018-07-01 04:30 | 27.14 | 26.24
2018-07-01 05:00 | 27.15 | 26.24
2018-07-01 05:30 | 27.9 | 27.01
2018-07-01 06:00 | 28.66 | 27.8
2018-07-01 06:30 | 29.91 | 29.08
2018-07-01 07:00 | 30.69 | 29.88
2018-07-01 07:30 | 32.14 | 31.36
2018-07-01 08:00 | 33.93 | 33.2
2018-07-01 08:30 | 36.3 | 35.61
2018-07-01 09:00 | 38.79 | 38.13
2018-07-01 09:30 | 39.8 | 39.15
2018-07-01 10:00 | 38.8 | 38.12
2018-07-01 10:30 | 40.7 | 40.05
2018-07-01 11:00 | 41.01 | 40.36
2018-07-01 11:30 | 39.93 | 39.26
2018-07-01 12:00 | 36.49 | 35.75
2018-07-01 12:30 | 38.41 | 37.7
2018-07-01 13:00 | 37.47 | 36.75
2018-07-01 13:30 | 38.7 | 38
2018-07-01 14:00 | 39.94 | 39.28
2018-07-01 14:30 | 39.24 | 38.57
2018-07-01 15:00 | 38.31 | 37.62
2018-07-01 15:30 | 38.95 | 38.28
2018-07-01 16:00 | 38.77 | 38.1
2018-07-01 16:30 | 38.37 | 37.7
2018-07-01 17:00 | 37.9 | 37.22
2018-07-01 17:30 | 40.63 | 40
2018-07-01 18:00 | 43.7 | 43.12
2018-07-01 18:30 | 46.08 | 45.53
2018-07-01 19:00 | 45.37 | 44.81
2018-07-01 19:30 | 43.47 | 42.89
2018-07-01 20:00 | 41.78 | 41.17
2018-07-01 20:30 | 40.54 | 39.91
2018-07-01 21:00 | 38.8 | 38.14
2018-07-01 21:30 | 37.03 | 36.35
2018-07-01 22:00 | 35 | 34.28
2018-07-01 22:30 | 33.22 | 32.48
2018-07-01 23:00 | 33.69 | 32.96
2018-07-01 23:30 | 31.18 | 30.39
2018-07-02 | 29.27 | 28.43
2018-07-02 00:30 | 28.61 | 27.76
2018-07-02 01:00 | 28.41 | 27.54
2018-07-02 01:30 | 27.76 | 26.87
2018-07-02 02:00 | 27.62 | 26.73
2018-07-02 02:30 | 26.68 | 25.76
2018-07-02 03:00 | 26.55 | 25.63
2018-07-02 03:30 | 26.76 | 25.84
2018-07-02 04:00 | 27.19 | 26.28
2018-07-02 04:30 | 27.88 | 26.99
2018-07-02 05:00 | 29.04 | 28.18
2018-07-02 05:30 | 31.99 | 31.19
2018-07-02 06:00 | 35.77 | 35.04
2018-07-02 06:30 | 40 | 39.31
2018-07-02 07:00 | 42.93 | 42.27
2018-07-02 07:30 | 47.07 | 46.51
2018-07-02 08:00 | 50.13 | 49.49
2018-07-02 08:30 | 54.09 | 53.2
2018-07-02 09:00 | 55.27 | 54.86
2018-07-02 09:30 | 54.91 | 54.63
2018-07-02 10:00 | 55.63 | 55.54
2018-07-02 10:30 | 56.61 | 56.49
2018-07-02 11:00 | 55.32 | 55.19
2018-07-02 11:30 | 54.95 | 54.79
2018-07-02 12:00 | 54.15 | 53.98
2018-07-02 12:30 | 53.46 | 53.3
2018-07-02 13:00 | 54.15 | 54
2018-07-02 13:30 | 53.58 | 53.41
2018-07-02 14:00 | 52.51 | 52.35
2018-07-02 14:30 | 52.41 | 52.24
2018-07-02 15:00 | 51.11 | 50.99
2018-07-02 15:30 | 50.81 | 50.71
2018-07-02 16:00 | 50.27 | 50.21
2018-07-02 16:30 | 50.99 | 50.97
2018-07-02 17:00 | 51.13 | 51.13
2018-07-02 17:30 | 50.58 | 50.5
2018-07-02 18:00 | 51.97 | 51.9
2018-07-02 18:30 | 53.01 | 53.01
2018-07-02 19:00 | 52.51 | 52.51
2018-07-02 19:30 | 51.04 | 51.04
2018-07-02 20:00 | 48.11 | 48.09
2018-07-02 20:30 | 44.97 | 44.91
2018-07-02 21:00 | 42.66 | 42.57
2018-07-02 21:30 | 40.3 | 40.17
2018-07-02 22:00 | 39.38 | 39.19
2018-07-02 22:30 | 36.65 | 36.6
2018-07-02 23:00 | 36.62 | 36.61
2018-07-02 23:30 | 33.38 | 33.36
2018-07-03 | 32.42 | 32.37
2018-07-03 00:30 | 31.61 | 31.56
2018-07-03 01:00 | 30.11 | 30.02
2018-07-03 01:30 | 28.93 | 28.84
2018-07-03 02:00 | 28.46 | 28.35
2018-07-03 02:30 | 27.59 | 27.43
2018-07-03 03:00 | 26.84 | 26.82
2018-07-03 03:30 | 26.94 | 26.93
2018-07-03 04:00 | 26.59 | 26.58
2018-07-03 04:30 | 28.51 | 28.48
2018-07-03 05:00 | 30.06 | 30.01
2018-07-03 05:30 | 31.82 | 31.7
2018-07-03 06:00 | 34.85 | 34.65
2018-07-03 06:30 | 40.05 | 39.51
2018-07-03 07:00 | 43.27 | 43.06
2018-07-03 07:30 | 47.8 | 47.37
2018-07-03 08:00 | 51.69 | 51.04
2018-07-03 08:30 | 54.53 | 54.16
2018-07-03 09:00 | 55.59 | 55.14
2018-07-03 09:30 | 54.12 | 53.66
2018-07-03 10:00 | 52.38 | 51.96
2018-07-03 10:30 | 51.98 | 51.57
2018-07-03 11:00 | 50.55 | 50.14
2018-07-03 11:30 | 48.38 | 47.96
2018-07-03 12:00 | 47.85 | 47.43
2018-07-03 12:30 | 48.52 | 48.11
2018-07-03 13:00 | 49.1 | 48.69
2018-07-03 13:30 | 49.53 | 49.13
2018-07-03 14:00 | 51.88 | 51.48
2018-07-03 14:30 | 51.61 | 51.21
2018-07-03 15:00 | 50.71 | 50.31
2018-07-03 15:30 | 52.82 | 52.42
2018-07-03 16:00 | 52.69 | 52.28
2018-07-03 16:30 | 52.12 | 51.68
2018-07-03 17:00 | 51.68 | 51.21
2018-07-03 17:30 | 51.44 | 50.94
2018-07-03 18:00 | 53.06 | 52.56
2018-07-03 18:30 | 53.58 | 53.08
2018-07-03 19:00 | 51.92 | 51.39
2018-07-03 19:30 | 49.33 | 48.77
2018-07-03 20:00 | 47.77 | 47.18
2018-07-03 20:30 | 45.14 | 44.49
2018-07-03 21:00 | 42.88 | 42.18
2018-07-03 21:30 | 41.37 | 40.64
2018-07-03 22:00 | 40.45 | 39.74
2018-07-03 22:30 | 39.55 | 38.85
2018-07-03 23:00 | 37.46 | 36.7
2018-07-03 23:30 | 35.05 | 34.23
2018-07-04 | 33.5 | 32.64
2018-07-04 00:30 | 33.06 | 32.39
2018-07-04 01:00 | 31.64 | 31
2018-07-04 01:30 | 30.77 | 30.1
2018-07-04 02:00 | 29.42 | 28.66
2018-07-04 02:30 | 35.34 | 34.73
2018-07-04 03:00 | 38.43 | 37.87
2018-07-04 03:30 | 35.17 | 34.55
2018-07-04 04:00 | 33.08 | 32.43
2018-07-04 04:30 | 32 | 31.31
2018-07-04 05:00 | 32.42 | 31.73
2018-07-04 05:30 | 34.33 | 33.67
2018-07-04 06:00 | 36.93 | 36.31
2018-07-04 06:30 | 41.74 | 41.17
2018-07-04 07:00 | 44.45 | 43.9
2018-07-04 07:30 | 48.24 | 47.71
2018-07-04 08:00 | 50.43 | 49.83
2018-07-04 08:30 | 45.28 | 44.6
2018-07-04 09:00 | 36.5 | 35.94
2018-07-04 09:30 | 36.29 | 35.68
2018-07-04 10:00 | 36.71 | 36
2018-07-04 10:30 | 34.72 | 34.08
2018-07-04 11:00 | 34.03 | 33.38
2018-07-04 11:30 | 33.6 | 32.95
2018-07-04 12:00 | 33.15 | 32.49
2018-07-04 12:30 | 32.96 | 32.3
2018-07-04 13:00 | 32.95 | 32.28
2018-07-04 13:30 | 32.45 | 31.77
2018-07-04 14:00 | 33.63 | 32.97
2018-07-04 14:30 | 36.4 | 35.8
2018-07-04 15:00 | 47.54 | 47.07
2018-07-04 15:30 | 48.4 | 47.93
2018-07-04 16:00 | 48.49 | 48.01
2018-07-04 16:30 | 49.34 | 48.85
2018-07-04 17:00 | 50.46 | 49.96
2018-07-04 17:30 | 50.3 | 49.76
2018-07-04 18:00 | 51.31 | 50.77
2018-07-04 18:30 | 52.3 | 51.76
2018-07-04 19:00 | 52.41 | 51.87
2018-07-04 19:30 | 49.04 | 48.44
2018-07-04 20:00 | 47.74 | 47.12
2018-07-04 20:30 | 45.71 | 45.05
2018-07-04 21:00 | 43.3 | 42.6
2018-07-04 21:30 | 41.72 | 40.98
2018-07-04 22:00 | 38.81 | 38.28
2018-07-04 22:30 | 38.13 | 37.6
2018-07-04 23:00 | 38.51 | 37.98
2018-07-04 23:30 | 34.73 | 34.15
2018-07-05 | 32.06 | 31.39
2018-07-05 00:30 | 30.87 | 30.15
2018-07-05 01:00 | 30.77 | 30.04
2018-07-05 01:30 | 30.06 | 29.32
2018-07-05 02:00 | 29.17 | 28.41
2018-07-05 02:30 | 27.5 | 26.68
2018-07-05 03:00 | 26.94 | 26.04
2018-07-05 03:30 | 27.33 | 26.44
2018-07-05 04:00 | 27.68 | 26.81
2018-07-05 04:30 | 28.4 | 27.54
2018-07-05 05:00 | 29.37 | 28.53
2018-07-05 05:30 | 31.9 | 31.11
2018-07-05 06:00 | 35.52 | 34.81
2018-07-05 06:30 | 39.77 | 39.1
2018-07-05 07:00 | 43.37 | 42.79
2018-07-05 07:30 | 47.33 | 46.79
2018-07-05 08:00 | 48.53 | 47.97
2018-07-05 08:30 | 49.65 | 48.96
2018-07-05 09:00 | 51.14 | 50.32
2018-07-05 09:30 | 50.62 | 50.11
2018-07-05 10:00 | 50.75 | 50.21
2018-07-05 10:30 | 51.03 | 50.61
2018-07-05 11:00 | 50.84 | 50.42
2018-07-05 11:30 | 49.99 | 49.57
2018-07-05 12:00 | 50.12 | 49.71
2018-07-05 12:30 | 50.31 | 49.9
2018-07-05 13:00 | 50.34 | 49.93
2018-07-05 13:30 | 48.79 | 48.37
2018-07-05 14:00 | 49.44 | 49.03
2018-07-05 14:30 | 49.51 | 49.09
2018-07-05 15:00 | 51.03 | 50.63
2018-07-05 15:30 | 50.64 | 50.22
2018-07-05 16:00 | 50.65 | 50.2
2018-07-05 16:30 | 51.04 | 50.58
2018-07-05 17:00 | 51.48 | 51.01
2018-07-05 17:30 | 51.8 | 51.3
2018-07-05 18:00 | 52.91 | 52.41
2018-07-05 18:30 | 53.17 | 52.67
2018-07-05 19:00 | 52.37 | 51.85
2018-07-05 19:30 | 50.26 | 49.71
2018-07-05 20:00 | 48.34 | 47.75
2018-07-05 20:30 | 46.48 | 45.85
2018-07-05 21:00 | 44.85 | 44.19
2018-07-05 21:30 | 43.3 | 42.59
2018-07-05 22:00 | 40.45 | 39.55
2018-07-05 22:30 | 38.49 | 37.84
2018-07-05 23:00 | 39.61 | 39.1
2018-07-05 23:30 | 35.83 | 35.27
2018-07-06 | 32.81 | 32.19
2018-07-06 00:30 | 32.25 | 31.61
2018-07-06 01:00 | 31.29 | 30.58
2018-07-06 01:30 | 30.34 | 29.6
2018-07-06 02:00 | 29.22 | 28.45
2018-07-06 02:30 | 28.05 | 27.26
2018-07-06 03:00 | 28.14 | 27.26
2018-07-06 03:30 | 27.75 | 26.86
2018-07-06 04:00 | 27.84 | 26.96
2018-07-06 04:30 | 28.64 | 27.78
2018-07-06 05:00 | 30.25 | 29.42
2018-07-06 05:30 | 32.71 | 31.93
2018-07-06 06:00 | 35.12 | 34.39
2018-07-06 06:30 | 39.75 | 39.08
2018-07-06 07:00 | 42.82 | 42.24
2018-07-06 07:30 | 46.5 | 45.95
2018-07-06 08:00 | 49.23 | 48.68
2018-07-06 08:30 | 51.82 | 51.1
2018-07-06 09:00 | 51.44 | 50.61
2018-07-06 09:30 | 50.35 | 49.35
2018-07-06 10:00 | 51.33 | 50.25
2018-07-06 10:30 | 49.99 | 49.32
2018-07-06 11:00 | 49.58 | 49.16
2018-07-06 11:30 | 49.64 | 49.23
2018-07-06 12:00 | 49.26 | 48.85
2018-07-06 12:30 | 48.72 | 48.31
2018-07-06 13:00 | 49.2 | 48.79
2018-07-06 13:30 | 49.13 | 48.71
2018-07-06 14:00 | 49.17 | 48.75
2018-07-06 14:30 | 48.81 | 48.37
2018-07-06 15:00 | 50.02 | 49.58
2018-07-06 15:30 | 51.38 | 50.93
2018-07-06 16:00 | 50.72 | 50.24
2018-07-06 16:30 | 50.19 | 49.68
2018-07-06 17:00 | 50.3 | 49.78
2018-07-06 17:30 | 50.43 | 49.88
2018-07-06 18:00 | 51.17 | 50.64
2018-07-06 18:30 | 50.06 | 49.56
2018-07-06 19:00 | 48.74 | 48.21
2018-07-06 19:30 | 47.03 | 46.48
2018-07-06 20:00 | 44.66 | 44.07
2018-07-06 20:30 | 43.03 | 42.41
2018-07-06 21:00 | 41.64 | 40.99
2018-07-06 21:30 | 41.01 | 40.34
2018-07-06 22:00 | 39.21 | 38.55
2018-07-06 22:30 | 37.89 | 37.22
2018-07-06 23:00 | 38.71 | 38.05
2018-07-06 23:30 | 35.5 | 34.78
2018-07-07 | 33.01 | 32.3
2018-07-07 00:30 | 32.23 | 31.49
2018-07-07 01:00 | 29.91 | 29.11
2018-07-07 01:30 | 28.86 | 28.03
2018-07-07 02:00 | 29.18 | 28.36
2018-07-07 02:30 | 28.83 | 27.98
2018-07-07 03:00 | 28.2 | 27.34
2018-07-07 03:30 | 27.56 | 26.68
2018-07-07 04:00 | 27.58 | 26.7
2018-07-07 04:30 | 28.9 | 28.06
2018-07-07 05:00 | 28.46 | 27.61
2018-07-07 05:30 | 29.46 | 28.65
2018-07-07 06:00 | 30.74 | 29.98
2018-07-07 06:30 | 33.98 | 33.31
2018-07-07 07:00 | 34.67 | 34.02
2018-07-07 07:30 | 36.37 | 35.76
2018-07-07 08:00 | 37.76 | 37.2
2018-07-07 08:30 | 39.92 | 39.41
2018-07-07 09:00 | 41.59 | 41.02
2018-07-07 09:30 | 42.8 | 42.09
2018-07-07 10:00 | 43.75 | 42.97
2018-07-07 10:30 | 44.12 | 43.21
2018-07-07 11:00 | 43.6 | 43.03
2018-07-07 11:30 | 42.21 | 41.71
2018-07-07 12:00 | 41.38 | 40.87
2018-07-07 12:30 | 39.47 | 38.92
2018-07-07 13:00 | 37.79 | 37.2
2018-07-07 13:30 | 38.24 | 37.66
2018-07-07 14:00 | 38.4 | 37.81
2018-07-07 14:30 | 38.75 | 38.15
2018-07-07 15:00 | 38.68 | 38.08
2018-07-07 15:30 | 38.03 | 37.41
2018-07-07 16:00 | 39.38 | 38.77
2018-07-07 16:30 | 40.34 | 39.74
2018-07-07 17:00 | 41.44 | 40.86
2018-07-07 17:30 | 43.19 | 42.64
2018-07-07 18:00 | 45.32 | 44.8
2018-07-07 18:30 | 45.2 | 44.68
2018-07-07 19:00 | 44.22 | 43.69
2018-07-07 19:30 | 41.82 | 41.25
2018-07-07 20:00 | 40.44 | 39.83
2018-07-07 20:30 | 38.81 | 38.16
2018-07-07 21:00 | 37.66 | 36.99
2018-07-07 21:30 | 36.78 | 36.08
2018-07-07 22:00 | 35.5 | 34.77
2018-07-07 22:30 | 35.76 | 35.02
2018-07-07 23:00 | 36.64 | 35.92
2018-07-07 23:30 | 32.93 | 32.15
2018-07-08 | 31.73 | 30.96
2018-07-08 00:30 | 30.8 | 30.01
2018-07-08 01:00 | 29.1 | 28.26
2018-07-08 01:30 | 28.68 | 27.83
2018-07-08 02:00 | 28.13 | 27.26
2018-07-08 02:30 | 28.1 | 27.23
2018-07-08 03:00 | 27.19 | 26.29
2018-07-08 03:30 | 27.76 | 26.89
2018-07-08 04:00 | 27.1 | 26.21
2018-07-08 04:30 | 27.51 | 26.63
2018-07-08 05:00 | 26.94 | 26.04
2018-07-08 05:30 | 27.27 | 26.38
2018-07-08 06:00 | 27.97 | 27.11
2018-07-08 06:30 | 29.76 | 28.96
2018-07-08 07:00 | 29.64 | 28.83
2018-07-08 07:30 | 30.73 | 29.96
2018-07-08 08:00 | 31.18 | 30.41
2018-07-08 08:30 | 31.98 | 31.22
2018-07-08 09:00 | 32.34 | 31.58
2018-07-08 09:30 | 32.53 | 31.76
2018-07-08 10:00 | 31.4 | 30.59
2018-07-08 10:30 | 31.09 | 30.27
2018-07-08 11:00 | 30.6 | 29.77
2018-07-08 11:30 | 29.42 | 28.54
2018-07-08 12:00 | 29.13 | 28.25
2018-07-08 12:30 | 28.77 | 27.89
2018-07-08 13:00 | 28.37 | 27.47
2018-07-08 13:30 | 27.64 | 26.72
2018-07-08 14:00 | 28.09 | 27.2
2018-07-08 14:30 | 28.85 | 27.99
2018-07-08 15:00 | 30.17 | 29.35
2018-07-08 15:30 | 31.32 | 30.53
2018-07-08 16:00 | 32.09 | 31.33
2018-07-08 16:30 | 34.78 | 34.09
2018-07-08 17:00 | 35.68 | 35.01
2018-07-08 17:30 | 39.11 | 38.51
2018-07-08 18:00 | 42.63 | 42.05
2018-07-08 18:30 | 44.67 | 44.12
2018-07-08 19:00 | 44.62 | 44.07
2018-07-08 19:30 | 41.89 | 41.3
2018-07-08 20:00 | 40.04 | 39.43
2018-07-08 20:30 | 39.95 | 39.34
2018-07-08 21:00 | 37.46 | 36.81
2018-07-08 21:30 | 36.34 | 35.67
2018-07-08 22:00 | 34.94 | 34.25
2018-07-08 22:30 | 34.26 | 33.56
2018-07-08 23:00 | 34.67 | 34
2018-07-08 23:30 | 31.72 | 31
2018-07-09 | 29.27 | 28.48
2018-07-09 00:30 | 29.43 | 28.65
2018-07-09 01:00 | 27.72 | 26.89
2018-07-09 01:30 | 27.94 | 27.12
2018-07-09 02:00 | 27.29 | 26.45
2018-07-09 02:30 | 27.33 | 26.49
2018-07-09 03:00 | 26.98 | 26.13
2018-07-09 03:30 | 26.88 | 26.02
2018-07-09 04:00 | 26.99 | 26.14
2018-07-09 04:30 | 28.59 | 27.78
2018-07-09 05:00 | 29.55 | 28.77
2018-07-09 05:30 | 32.26 | 31.54
2018-07-09 06:00 | 36.13 | 35.48
2018-07-09 06:30 | 42.41 | 41.86
2018-07-09 07:00 | 46.27 | 45.81
2018-07-09 07:30 | 49.4 | 48.98
2018-07-09 08:00 | 50.61 | 50.22
2018-07-09 08:30 | 50.68 | 50.22
2018-07-09 09:00 | 50.31 | 49.69
2018-07-09 09:30 | 48.44 | 47.99
2018-07-09 10:00 | 48.14 | 47.71
2018-07-09 10:30 | 47.83 | 47.39
2018-07-09 11:00 | 45.5 | 45.05
2018-07-09 11:30 | 44.74 | 44.28
2018-07-09 12:00 | 43.97 | 43.5
2018-07-09 12:30 | 43.93 | 43.46
2018-07-09 13:00 | 43.42 | 42.94
2018-07-09 13:30 | 43.91 | 43.45
2018-07-09 14:00 | 44.62 | 44.16
2018-07-09 14:30 | 45.42 | 44.97
2018-07-09 15:00 | 47.7 | 47.28
2018-07-09 15:30 | 48.02 | 47.58
2018-07-09 16:00 | 49.05 | 48.61
2018-07-09 16:30 | 48.68 | 48.21
2018-07-09 17:00 | 49.74 | 49.27
2018-07-09 17:30 | 51.32 | 50.83
2018-07-09 18:00 | 53.34 | 52.87
2018-07-09 18:30 | 54.77 | 54.31
2018-07-09 19:00 | 53.55 | 53.07
2018-07-09 19:30 | 51.11 | 50.63
2018-07-09 20:00 | 49.46 | 48.99
2018-07-09 20:30 | 47.02 | 46.52
2018-07-09 21:00 | 45.51 | 44.98
2018-07-09 21:30 | 43.3 | 42.73
2018-07-09 22:00 | 42.06 | 41.46
2018-07-09 22:30 | 40.01 | 39.37
2018-07-09 23:00 | 41.06 | 40.42
2018-07-09 23:30 | 37.56 | 36.85
2018-07-10 | 34.73 | 34.07
2018-07-10 00:30 | 33.86 | 33.21
2018-07-10 01:00 | 32.17 | 31.5
2018-07-10 01:30 | 31.44 | 30.74
2018-07-10 02:00 | 31.39 | 30.68
2018-07-10 02:30 | 30.85 | 30.14
2018-07-10 03:00 | 30.17 | 29.45
2018-07-10 03:30 | 30.33 | 29.62
2018-07-10 04:00 | 30.27 | 29.56
2018-07-10 04:30 | 32.32 | 31.66
2018-07-10 05:00 | 34.73 | 34.11
2018-07-10 05:30 | 37.69 | 37.1
2018-07-10 06:00 | 40.44 | 39.89
2018-07-10 06:30 | 44.01 | 43.47
2018-07-10 07:00 | 49 | 48.5
2018-07-10 07:30 | 55.12 | 54.65
2018-07-10 08:00 | 55.6 | 55.06
2018-07-10 08:30 | 55.39 | 54.71
2018-07-10 09:00 | 53.1 | 52.25
2018-07-10 09:30 | 50.42 | 50.09
2018-07-10 10:00 | 48.44 | 48.16
2018-07-10 10:30 | 47.91 | 47.57
2018-07-10 11:00 | 46.52 | 46.09
2018-07-10 11:30 | 45.86 | 45.36
2018-07-10 12:00 | 45.66 | 45.09
2018-07-10 12:30 | 45.39 | 44.95
2018-07-10 13:00 | 44.27 | 44.23
2018-07-10 13:30 | 44.34 | 44.29
2018-07-10 14:00 | 45.9 | 45.84
2018-07-10 14:30 | 45.54 | 45.47
2018-07-10 15:00 | 46.52 | 46.46
2018-07-10 15:30 | 47.68 | 47.65
2018-07-10 16:00 | 48.51 | 48.5
2018-07-10 16:30 | 48.92 | 48.91
2018-07-10 17:00 | 49.71 | 49.65
2018-07-10 17:30 | 50.9 | 50.74
2018-07-10 18:00 | 53.86 | 53.71
2018-07-10 18:30 | 54 | 53.88
2018-07-10 19:00 | 53.23 | 53.23
2018-07-10 19:30 | 51.18 | 51.16
2018-07-10 20:00 | 48.37 | 48.32
2018-07-10 20:30 | 46.6 | 46.52
2018-07-10 21:00 | 45.14 | 45.03
2018-07-10 21:30 | 42.79 | 42.62
2018-07-10 22:00 | 40.69 | 40.62
2018-07-10 22:30 | 39.49 | 39.48
2018-07-10 23:00 | 39.65 | 39.63
2018-07-10 23:30 | 36.23 | 36.18
2018-07-11 | 33.34 | 33.29
2018-07-11 00:30 | 32.15 | 32.11
2018-07-11 01:00 | 31.11 | 31.06
2018-07-11 01:30 | 30.27 | 30.23
2018-07-11 02:00 | 29.48 | 29.46
2018-07-11 02:30 | 29.18 | 29.17
2018-07-11 03:00 | 28.6 | 28.59
2018-07-11 03:30 | 28.89 | 28.88
2018-07-11 04:00 | 29.13 | 29.12
2018-07-11 04:30 | 29.87 | 29.85
2018-07-11 05:00 | 30.88 | 30.85
2018-07-11 05:30 | 33.94 | 33.85
2018-07-11 06:00 | 36.42 | 36.24
2018-07-11 06:30 | 42.39 | 42.02
2018-07-11 07:00 | 45.3 | 45.2
2018-07-11 07:30 | 50.01 | 49.74
2018-07-11 08:00 | 54.42 | 53.83
2018-07-11 08:30 | 54.06 | 53.26
2018-07-11 09:00 | 54.51 | 53.48
2018-07-11 09:30 | 52.48 | 51.89
2018-07-11 10:00 | 51.6 | 51.15
2018-07-11 10:30 | 53.54 | 52.96
2018-07-11 11:00 | 53.98 | 53.39
2018-07-11 11:30 | 50.53 | 49.88
2018-07-11 12:00 | 49.87 | 49.7
2018-07-11 12:30 | 50.6 | 50.46
2018-07-11 13:00 | 49.17 | 49.08
2018-07-11 13:30 | 47.22 | 47.11
2018-07-11 14:00 | 47.54 | 47.39
2018-07-11 14:30 | 47.09 | 46.95
2018-07-11 15:00 | 48.53 | 48.43
2018-07-11 15:30 | 48.96 | 48.91
2018-07-11 16:00 | 50.29 | 50.27
2018-07-11 16:30 | 50.67 | 50.67
2018-07-11 17:00 | 49.73 | 49.69
2018-07-11 17:30 | 50.33 | 50.19
2018-07-11 18:00 | 51.36 | 51.18
2018-07-11 18:30 | 51.92 | 51.71
2018-07-11 19:00 | 52.38 | 52.16
2018-07-11 19:30 | 50.96 | 50.67
2018-07-11 20:00 | 49.03 | 48.69
2018-07-11 20:30 | 46.65 | 46.18
2018-07-11 21:00 | 45 | 43.58
2018-07-11 21:30 | 44.08 | 42.07
2018-07-11 22:00 | 42.03 | 39.87
2018-07-11 22:30 | 41.05 | 38.8
2018-07-11 23:00 | 43.03 | 40.9
2018-07-11 23:30 | 39.33 | 36.98
2018-07-12 | 36.89 | 34.36
2018-07-12 00:30 | 35.48 | 32.84
2018-07-12 01:00 | 33.82 | 31.07
2018-07-12 01:30 | 33.33 | 30.51
2018-07-12 02:00 | 32.73 | 29.84
2018-07-12 02:30 | 31.92 | 28.96
2018-07-12 03:00 | 31.43 | 28.34
2018-07-12 03:30 | 31.58 | 28.46
2018-07-12 04:00 | 32.16 | 29.11
2018-07-12 04:30 | 32.32 | 29.28
2018-07-12 05:00 | 33.6 | 30.68
2018-07-12 05:30 | 35.99 | 33.25
2018-07-12 06:00 | 38.48 | 35.92
2018-07-12 06:30 | 43.12 | 40.83
2018-07-12 07:00 | 47.72 | 45.72
2018-07-12 07:30 | 50.88 | 50.34
2018-07-12 08:00 | 51.85 | 51.46
2018-07-12 08:30 | 51.11 | 51
2018-07-12 09:00 | 49.21 | 49.02
2018-07-12 09:30 | 47.54 | 47.3
2018-07-12 10:00 | 46.96 | 46.66
2018-07-12 10:30 | 45.95 | 45.61
2018-07-12 11:00 | 46.25 | 46.12
2018-07-12 11:30 | 46.92 | 46.78
2018-07-12 12:00 | 47.68 | 47.52
2018-07-12 12:30 | 46.84 | 46.74
2018-07-12 13:00 | 46.61 | 46.52
2018-07-12 13:30 | 47.07 | 46.94
2018-07-12 14:00 | 47.05 | 46.93
2018-07-12 14:30 | 47.97 | 47.84
2018-07-12 15:00 | 47.6 | 47.5
2018-07-12 15:30 | 48.32 | 48.27
2018-07-12 16:00 | 49.19 | 49.17
2018-07-12 16:30 | 50.3 | 50.29
2018-07-12 17:00 | 51.04 | 51
2018-07-12 17:30 | 51.74 | 51.6
2018-07-12 18:00 | 54.02 | 53.85
2018-07-12 18:30 | 55.51 | 55.37
2018-07-12 19:00 | 54.52 | 54.35
2018-07-12 19:30 | 52.34 | 52.12
2018-07-12 20:00 | 50.19 | 50.09
2018-07-12 20:30 | 48.24 | 48.18
2018-07-12 21:00 | 45.99 | 45.96
2018-07-12 21:30 | 42.77 | 42.76
2018-07-12 22:00 | 39.97 | 39.97
2018-07-12 22:30 | 37.99 | 37.86
2018-07-12 23:00 | 40.33 | 40.18
2018-07-12 23:30 | 37.04 | 36.92
2018-07-13 | 33.98 | 33.9
2018-07-13 00:30 | 32.41 | 32.36
2018-07-13 01:00 | 30.51 | 30.49
2018-07-13 01:30 | 29.18 | 29.16
2018-07-13 02:00 | 28.2 | 28.2
2018-07-13 02:30 | 27.42 | 27.42
2018-07-13 03:00 | 27.38 | 27.38
2018-07-13 03:30 | 27.64 | 27.64
2018-07-13 04:00 | 28.27 | 28.27
2018-07-13 04:30 | 29.31 | 29.31
2018-07-13 05:00 | 30.03 | 30.03
2018-07-13 05:30 | 31.5 | 31.48
2018-07-13 06:00 | 34.36 | 34.27
2018-07-13 06:30 | 40.16 | 39.89
2018-07-13 07:00 | 43.22 | 43.11
2018-07-13 07:30 | 46.47 | 46.3
2018-07-13 08:00 | 47.9 | 47.56
2018-07-13 08:30 | 48.44 | 47.97
2018-07-13 09:00 | 47.81 | 47.25
2018-07-13 09:30 | 46.43 | 45.81
2018-07-13 10:00 | 45.41 | 44.68
2018-07-13 10:30 | 44.49 | 43.64
2018-07-13 11:00 | 44.64 | 43.54
2018-07-13 11:30 | 45.56 | 44.45
2018-07-13 12:00 | 44.95 | 44.45
2018-07-13 12:30 | 43.26 | 42.78
2018-07-13 13:00 | 42.45 | 41.96
2018-07-13 13:30 | 42.49 | 42
2018-07-13 14:00 | 43.49 | 43
2018-07-13 14:30 | 44.05 | 43.56
2018-07-13 15:00 | 44.78 | 44.3
2018-07-13 15:30 | 43.09 | 42.9
2018-07-13 16:00 | 43.65 | 43.6
2018-07-13 16:30 | 45.84 | 45.83
2018-07-13 17:00 | 45.79 | 45.79
2018-07-13 17:30 | 45.72 | 45.71
2018-07-13 18:00 | 47.44 | 47.41
2018-07-13 18:30 | 48.14 | 48.11
2018-07-13 19:00 | 43.96 | 43.9
2018-07-13 19:30 | 44.96 | 44.94
2018-07-13 20:00 | 44.37 | 44.36
2018-07-13 20:30 | 43.65 | 43.65
2018-07-13 21:00 | 40.68 | 40.68
2018-07-13 21:30 | 39.41 | 39.4
2018-07-13 22:00 | 37.48 | 37.44
2018-07-13 22:30 | 36.45 | 36.38
2018-07-13 23:00 | 38.13 | 38.08
2018-07-13 23:30 | 34.59 | 34.56
2018-07-14 | 31.51 | 31.49
2018-07-14 00:30 | 30.26 | 30.26
2018-07-14 01:00 | 29.74 | 29.74
2018-07-14 01:30 | 29.08 | 29.08
2018-07-14 02:00 | 27.29 | 27.29
2018-07-14 02:30 | 28.01 | 28.01
2018-07-14 03:00 | 27.26 | 27.26
2018-07-14 03:30 | 27.27 | 27.27
2018-07-14 04:00 | 26.94 | 26.94
2018-07-14 04:30 | 27.15 | 27.15
2018-07-14 05:00 | 28.28 | 28.28
2018-07-14 05:30 | 29.34 | 29.33
2018-07-14 06:00 | 30.62 | 30.61
2018-07-14 06:30 | 33.36 | 33.32
2018-07-14 07:00 | 35.99 | 35.95
2018-07-14 07:30 | 36.89 | 36.83
2018-07-14 08:00 | 37.4 | 37.27
2018-07-14 08:30 | 38.6 | 38.43
2018-07-14 09:00 | 37.85 | 37.6
2018-07-14 09:30 | 37.82 | 37.49
2018-07-14 10:00 | 36.18 | 35.82
2018-07-14 10:30 | 35.25 | 34.86
2018-07-14 11:00 | 34.72 | 34.26
2018-07-14 11:30 | 32.93 | 32.45
2018-07-14 12:00 | 32.2 | 31.69
2018-07-14 12:30 | 30.84 | 30.44
2018-07-14 13:00 | 30.36 | 29.98
2018-07-14 13:30 | 29.78 | 29.45
2018-07-14 14:00 | 29.08 | 28.8
2018-07-14 14:30 | 29.14 | 28.89
2018-07-14 15:00 | 29.7 | 29.49
2018-07-14 15:30 | 30.13 | 29.98
2018-07-14 16:00 | 31.94 | 31.81
2018-07-14 16:30 | 33.9 | 33.79
2018-07-14 17:00 | 36.25 | 36.16
2018-07-14 17:30 | 39.94 | 39.82
2018-07-14 18:00 | 42.18 | 42.01
2018-07-14 18:30 | 43.78 | 43.58
2018-07-14 19:00 | 42.92 | 42.76
2018-07-14 19:30 | 40.94 | 40.8
2018-07-14 20:00 | 39.62 | 39.49
2018-07-14 20:30 | 38.05 | 37.96
2018-07-14 21:00 | 37.5 | 37.43
2018-07-14 21:30 | 35.66 | 35.61
2018-07-14 22:00 | 34.58 | 34.56
2018-07-14 22:30 | 32.87 | 32.85
2018-07-14 23:00 | 34.63 | 34.63
2018-07-14 23:30 | 31.86 | 31.86
2018-07-15 | 30.47 | 30.47
2018-07-15 00:30 | 31.45 | 31.45
2018-07-15 01:00 | 29.09 | 29.08
2018-07-15 01:30 | 27.58 | 27.57
2018-07-15 02:00 | 26.96 | 26.94
2018-07-15 02:30 | 26.88 | 26.86
2018-07-15 03:00 | 26.17 | 26.15
2018-07-15 03:30 | 25.93 | 25.89
2018-07-15 04:00 | 25.7 | 25.67
2018-07-15 04:30 | 26.61 | 26.58
2018-07-15 05:00 | 26.44 | 26.42
2018-07-15 05:30 | 27.49 | 27.48
2018-07-15 06:00 | 28.66 | 28.65
2018-07-15 06:30 | 30.12 | 30.12
2018-07-15 07:00 | 30.81 | 30.8
2018-07-15 07:30 | 31.67 | 31.67
2018-07-15 08:00 | 33.03 | 33.03
2018-07-15 08:30 | 34.07 | 34.07
2018-07-15 09:00 | 33.21 | 33.19
2018-07-15 09:30 | 33.19 | 33.15
2018-07-15 10:00 | 31.36 | 31.31
2018-07-15 10:30 | 31.1 | 31.03
2018-07-15 11:00 | 30.41 | 30.32
2018-07-15 11:30 | 29.11 | 28.99
2018-07-15 12:00 | 29.47 | 29.34
2018-07-15 12:30 | 28.31 | 28.2
2018-07-15 13:00 | 27.38 | 27.27
2018-07-15 13:30 | 27.04 | 26.92
2018-07-15 14:00 | 27.55 | 27.45
2018-07-15 14:30 | 27.72 | 27.63
2018-07-15 15:00 | 28.9 | 28.83
2018-07-15 15:30 | 30.75 | 30.7
2018-07-15 16:00 | 31.59 | 31.55
2018-07-15 16:30 | 34.61 | 34.57
2018-07-15 17:00 | 37.42 | 37.38
2018-07-15 17:30 | 39.85 | 39.79
2018-07-15 18:00 | 43.61 | 43.52
2018-07-15 18:30 | 46.05 | 45.9
2018-07-15 19:00 | 45.73 | 45.6
2018-07-15 19:30 | 43.22 | 43.13
2018-07-15 20:00 | 41.66 | 41.57
2018-07-15 20:30 | 39.31 | 39.26
2018-07-15 21:00 | 38.82 | 38.78
2018-07-15 21:30 | 36.46 | 36.44
2018-07-15 22:00 | 34.83 | 34.83
2018-07-15 22:30 | 33.63 | 33.63
2018-07-15 23:00 | 34.66 | 34.66
2018-07-15 23:30 | 31.21 | 31.21
2018-07-16 | 29.23 | 29.22
2018-07-16 00:30 | 29.25 | 29.24
2018-07-16 01:00 | 27.71 | 27.69
2018-07-16 01:30 | 26.86 | 26.83
2018-07-16 02:00 | 26.28 | 26.25
2018-07-16 02:30 | 26.31 | 26.28
2018-07-16 03:00 | 26.67 | 26.65
2018-07-16 03:30 | 26.65 | 26.63
2018-07-16 04:00 | 27.23 | 27.21
2018-07-16 04:30 | 28.05 | 28.04
2018-07-16 05:00 | 30.12 | 30.12
2018-07-16 05:30 | 32.9 | 32.89
2018-07-16 06:00 | 36.28 | 36.22
2018-07-16 06:30 | 42.26 | 42.01
2018-07-16 07:00 | 47.65 | 47.41
2018-07-16 07:30 | 52.71 | 52.54
2018-07-16 08:00 | 53.58 | 53.26
2018-07-16 08:30 | 51.33 | 50.93
2018-07-16 09:00 | 49.01 | 48.49
2018-07-16 09:30 | 46.49 | 45.89
2018-07-16 10:00 | 45.12 | 44.48
2018-07-16 10:30 | 44.62 | 43.87
2018-07-16 11:00 | 44.76 | 43.74
2018-07-16 11:30 | 44.4 | 43.39
2018-07-16 12:00 | 44.14 | 43.72
2018-07-16 12:30 | 44.6 | 44.16
2018-07-16 13:00 | 43.7 | 43.24
2018-07-16 13:30 | 43.5 | 43
2018-07-16 14:00 | 44.83 | 44.33
2018-07-16 14:30 | 44.92 | 44.43
2018-07-16 15:00 | 45.38 | 44.95
2018-07-16 15:30 | 45.87 | 45.5
2018-07-16 16:00 | 46.94 | 46.71
2018-07-16 16:30 | 48.97 | 48.84
2018-07-16 17:00 | 49.01 | 48.96
2018-07-16 17:30 | 48.96 | 48.96
2018-07-16 18:00 | 51.43 | 51.43
2018-07-16 18:30 | 52.75 | 52.75
2018-07-16 19:00 | 51.58 | 51.57
2018-07-16 19:30 | 49.64 | 49.64
2018-07-16 20:00 | 47.18 | 47.16
2018-07-16 20:30 | 45.59 | 45.53
2018-07-16 21:00 | 43.49 | 43.38
2018-07-16 21:30 | 41.38 | 41.19
2018-07-16 22:00 | 38.59 | 38.57
2018-07-16 22:30 | 37.28 | 37.28
2018-07-16 23:00 | 38.25 | 38.24
2018-07-16 23:30 | 34.85 | 34.82
2018-07-17 | 33.51 | 33.45
2018-07-17 00:30 | 31.7 | 31.6
2018-07-17 01:00 | 29.98 | 29.85
2018-07-17 01:30 | 29.18 | 29.12
2018-07-17 02:00 | 28.41 | 28.39
2018-07-17 02:30 | 27.48 | 27.47
2018-07-17 03:00 | 27.52 | 27.52
2018-07-17 03:30 | 27.16 | 27.16
2018-07-17 04:00 | 27.58 | 27.58
2018-07-17 04:30 | 30.5 | 30.49
2018-07-17 05:00 | 31.86 | 31.84
2018-07-17 05:30 | 34.79 | 34.73
2018-07-17 06:00 | 38.31 | 38.16
2018-07-17 06:30 | 42.85 | 42.46
2018-07-17 07:00 | 47.66 | 47.41
2018-07-17 07:30 | 53.05 | 52.82
2018-07-17 08:00 | 53.95 | 53.53
2018-07-17 08:30 | 51.75 | 51.23
2018-07-17 09:00 | 50.43 | 49.73
2018-07-17 09:30 | 48.17 | 47.41
2018-07-17 10:00 | 45.39 | 45.1
2018-07-17 10:30 | 42.82 | 42.5
2018-07-17 11:00 | 43.34 | 42.91
2018-07-17 11:30 | 42.6 | 42.29
2018-07-17 12:00 | 42.72 | 42.62
2018-07-17 12:30 | 41.73 | 41.66
2018-07-17 13:00 | 41.48 | 41.43
2018-07-17 13:30 | 42.88 | 42.82
2018-07-17 14:00 | 48.43 | 48.34
2018-07-17 14:30 | 49.46 | 49.36
2018-07-17 15:00 | 46.23 | 46.16
2018-07-17 15:30 | 47.34 | 47.31
2018-07-17 16:00 | 47.64 | 47.63
2018-07-17 16:30 | 48.73 | 48.73
2018-07-17 17:00 | 48.8 | 48.77
2018-07-17 17:30 | 50.38 | 50.27
2018-07-17 18:00 | 51.05 | 50.86
2018-07-17 18:30 | 52.64 | 52.47
2018-07-17 19:00 | 52.23 | 52.05
2018-07-17 19:30 | 49.95 | 49.64
2018-07-17 20:00 | 48.09 | 47.66
2018-07-17 20:30 | 46.4 | 45.96
2018-07-17 21:00 | 44.46 | 43.91
2018-07-17 21:30 | 43.64 | 42.45
2018-07-17 22:00 | 43.86 | 39.17
2018-07-17 22:30 | 42.42 | 37.51
2018-07-17 23:00 | 43.38 | 38.62
2018-07-17 23:30 | 40.21 | 35
2018-07-18 | 38.3 | 32.8
2018-07-18 00:30 | 37.15 | 31.43
2018-07-18 01:00 | 35.47 | 29.42
2018-07-18 01:30 | 35.07 | 29.07
2018-07-18 02:00 | 33.97 | 27.58
2018-07-18 02:30 | 33.77 | 27.19
2018-07-18 03:00 | 33.7 | 26.97
2018-07-18 03:30 | 34.75 | 28.3
2018-07-18 04:00 | 35.08 | 28.7
2018-07-18 04:30 | 34.66 | 28.27
2018-07-18 05:00 | 36.07 | 29.96
2018-07-18 05:30 | 38.46 | 32.8
2018-07-18 06:00 | 41.15 | 35.87
2018-07-18 06:30 | 44.48 | 41.23
2018-07-18 07:00 | 46.75 | 46.13
2018-07-18 07:30 | 51.72 | 51.22
2018-07-18 08:00 | 52.44 | 51.97
2018-07-18 08:30 | 50.49 | 49.99
2018-07-18 09:00 | 49.04 | 48.49
2018-07-18 09:30 | 47.38 | 46.81
2018-07-18 10:00 | 46.1 | 45.5
2018-07-18 10:30 | 46.91 | 46.31
2018-07-18 11:00 | 46.92 | 46.36
2018-07-18 11:30 | 45.95 | 45.38
2018-07-18 12:00 | 45.69 | 45.12
2018-07-18 12:30 | 45.88 | 45.31
2018-07-18 13:00 | 44.85 | 44.27
2018-07-18 13:30 | 45.46 | 44.89
2018-07-18 14:00 | 45.88 | 45.32
2018-07-18 14:30 | 45.56 | 44.99
2018-07-18 15:00 | 46.42 | 45.87
2018-07-18 15:30 | 46.83 | 46.3
2018-07-18 16:00 | 49.69 | 49.21
2018-07-18 16:30 | 49.85 | 49.39
2018-07-18 17:00 | 50.61 | 50.17
2018-07-18 17:30 | 50.17 | 49.75
2018-07-18 18:00 | 51.55 | 51.16
2018-07-18 18:30 | 52.49 | 52.11
2018-07-18 19:00 | 52.03 | 51.64
2018-07-18 19:30 | 50.14 | 49.74
2018-07-18 20:00 | 48.6 | 48.2
2018-07-18 20:30 | 45.15 | 44.67
2018-07-18 21:00 | 43.79 | 43.23
2018-07-18 21:30 | 41.71 | 40.98
2018-07-18 22:00 | 39.62 | 38.98
2018-07-18 22:30 | 38.09 | 37.54
2018-07-18 23:00 | 39.4 | 38.87
2018-07-18 23:30 | 37.41 | 36.85
2018-07-19 | 32.79 | 32.12
2018-07-19 00:30 | 31.96 | 31.24
2018-07-19 01:00 | 30.41 | 29.66
2018-07-19 01:30 | 29.82 | 29.05
2018-07-19 02:00 | 28.78 | 27.94
2018-07-19 02:30 | 28.18 | 27.28
2018-07-19 03:00 | 27.57 | 26.66
2018-07-19 03:30 | 28.65 | 27.78
2018-07-19 04:00 | 28.14 | 27.25
2018-07-19 04:30 | 30.6 | 29.78
2018-07-19 05:00 | 32.03 | 31.24
2018-07-19 05:30 | 34.63 | 33.89
2018-07-19 06:00 | 37.95 | 37.27
2018-07-19 06:30 | 39.98 | 39.23
2018-07-19 07:00 | 47.56 | 46.99
2018-07-19 07:30 | 52.45 | 51.95
2018-07-19 08:00 | 54.09 | 53.61
2018-07-19 08:30 | 52.46 | 51.95
2018-07-19 09:00 | 50.9 | 50.35
2018-07-19 09:30 | 49.75 | 49.13
2018-07-19 10:00 | 48.66 | 47.89
2018-07-19 10:30 | 48.57 | 47.95
2018-07-19 11:00 | 48.66 | 48.1
2018-07-19 11:30 | 48.45 | 47.88
2018-07-19 12:00 | 48.97 | 48.41
2018-07-19 12:30 | 48.17 | 47.59
2018-07-19 13:00 | 48.01 | 47.44
2018-07-19 13:30 | 48.25 | 47.69
2018-07-19 14:00 | 48.93 | 48.4
2018-07-19 14:30 | 49.49 | 48.97
2018-07-19 15:00 | 49.66 | 49.15
2018-07-19 15:30 | 50.59 | 50.1
2018-07-19 16:00 | 51.37 | 50.89
2018-07-19 16:30 | 52.13 | 51.68
2018-07-19 17:00 | 52.08 | 51.65
2018-07-19 17:30 | 52.09 | 51.69
2018-07-19 18:00 | 54.13 | 53.75
2018-07-19 18:30 | 55.48 | 55.11
2018-07-19 19:00 | 54.91 | 54.55
2018-07-19 19:30 | 52.59 | 52.21
2018-07-19 20:00 | 50.3 | 49.91
2018-07-19 20:30 | 48.37 | 47.96
2018-07-19 21:00 | 46.46 | 46.02
2018-07-19 21:30 | 43.46 | 42.85
2018-07-19 22:00 | 41.97 | 41.36
2018-07-19 22:30 | 40.86 | 40.34
2018-07-19 23:00 | 41.73 | 41.22
2018-07-19 23:30 | 37.97 | 37.42
2018-07-20 | 35.31 | 34.73
2018-07-20 00:30 | 34.35 | 33.74
2018-07-20 01:00 | 33.08 | 32.42
2018-07-20 01:30 | 31.29 | 30.56
2018-07-20 02:00 | 30.21 | 29.43
2018-07-20 02:30 | 28.53 | 27.74
2018-07-20 03:00 | 29.05 | 28.27
2018-07-20 03:30 | 30.14 | 29.39
2018-07-20 04:00 | 28.84 | 28.05
2018-07-20 04:30 | 30.31 | 29.57
2018-07-20 05:00 | 32.13 | 31.42
2018-07-20 05:30 | 34.58 | 33.91
2018-07-20 06:00 | 38.03 | 37.4
2018-07-20 06:30 | 43.27 | 42.7
2018-07-20 07:00 | 46.63 | 46.11
2018-07-20 07:30 | 49.91 | 49.44
2018-07-20 08:00 | 50.59 | 50.11
2018-07-20 08:30 | 50.84 | 50.34
2018-07-20 09:00 | 51.56 | 51.05
2018-07-20 09:30 | 48.98 | 48.43
2018-07-20 10:00 | 47.91 | 47.34
2018-07-20 10:30 | 49.42 | 48.9
2018-07-20 11:00 | 49.76 | 49.24
2018-07-20 11:30 | 49.64 | 49.11
2018-07-20 12:00 | 49.26 | 48.72
2018-07-20 12:30 | 48.04 | 47.49
2018-07-20 13:00 | 48.23 | 47.68
2018-07-20 13:30 | 48.96 | 48.43
2018-07-20 14:00 | 48.13 | 47.58
2018-07-20 14:30 | 48.47 | 47.94
2018-07-20 15:00 | 48.53 | 48
2018-07-20 15:30 | 49.8 | 49.31
2018-07-20 16:00 | 50.52 | 50.04
2018-07-20 16:30 | 50.77 | 50.31
2018-07-20 17:00 | 50.36 | 49.92
2018-07-20 17:30 | 50.6 | 50.18
2018-07-20 18:00 | 51.38 | 50.97
2018-07-20 18:30 | 51.33 | 50.93
2018-07-20 19:00 | 50.55 | 50.15
2018-07-20 19:30 | 48.12 | 47.7
2018-07-20 20:00 | 46.48 | 46.05
2018-07-20 20:30 | 44.28 | 43.82
2018-07-20 21:00 | 42.59 | 42.07
2018-07-20 21:30 | 41.78 | 41.23
2018-07-20 22:00 | 39.69 | 39.09
2018-07-20 22:30 | 38.84 | 38.23
2018-07-20 23:00 | 39.83 | 39.24
2018-07-20 23:30 | 36.33 | 35.62
2018-07-21 | 33.72 | 32.96
2018-07-21 00:30 | 31.7 | 30.9
2018-07-21 01:00 | 30.14 | 29.29
2018-07-21 01:30 | 29.31 | 28.44
2018-07-21 02:00 | 28.55 | 27.66
2018-07-21 02:30 | 29.41 | 28.56
2018-07-21 03:00 | 29.5 | 28.65
2018-07-21 03:30 | 29 | 28.13
2018-07-21 04:00 | 28.86 | 27.99
2018-07-21 04:30 | 28.54 | 27.66
2018-07-21 05:00 | 29.35 | 28.48
2018-07-21 05:30 | 30.82 | 29.99
2018-07-21 06:00 | 30.98 | 30.16
2018-07-21 06:30 | 33.75 | 32.99
2018-07-21 07:00 | 34.17 | 33.41
2018-07-21 07:30 | 36.28 | 35.56
2018-07-21 08:00 | 37.43 | 36.72
2018-07-21 08:30 | 39.37 | 38.69
2018-07-21 09:00 | 37.32 | 36.57
2018-07-21 09:30 | 40.25 | 39.56
2018-07-21 10:00 | 39.73 | 39.02
2018-07-21 10:30 | 40.13 | 39.41
2018-07-21 11:00 | 38.54 | 37.79
2018-07-21 11:30 | 37.27 | 36.45
2018-07-21 12:00 | 35.32 | 34.5
2018-07-21 12:30 | 34.3 | 33.48
2018-07-21 13:00 | 33.52 | 32.67
2018-07-21 13:30 | 31.83 | 30.94
2018-07-21 14:00 | 31.87 | 30.99
2018-07-21 14:30 | 31.78 | 30.9
2018-07-21 15:00 | 32.15 | 31.3
2018-07-21 15:30 | 33.11 | 32.29
2018-07-21 16:00 | 35.02 | 34.25
2018-07-21 16:30 | 36.56 | 35.84
2018-07-21 17:00 | 37.93 | 37.25
2018-07-21 17:30 | 40.5 | 39.86
2018-07-21 18:00 | 43.2 | 42.6
2018-07-21 18:30 | 44.53 | 43.95
2018-07-21 19:00 | 43.36 | 42.76
2018-07-21 19:30 | 42.37 | 41.75
2018-07-21 20:00 | 40.92 | 40.28
2018-07-21 20:30 | 38.39 | 37.72
2018-07-21 21:00 | 37.33 | 36.65
2018-07-21 21:30 | 36.78 | 36.09
2018-07-21 22:00 | 36.53 | 35.84
2018-07-21 22:30 | 35.24 | 34.53
2018-07-21 23:00 | 35.87 | 35.17
2018-07-21 23:30 | 33.19 | 32.43
2018-07-22 | 31.33 | 30.54
2018-07-22 00:30 | 30.29 | 29.48
2018-07-22 01:00 | 29.31 | 28.47
2018-07-22 01:30 | 28.48 | 27.61
2018-07-22 02:00 | 27.8 | 26.91
2018-07-22 02:30 | 27.94 | 27.06
2018-07-22 03:00 | 27.45 | 26.56
2018-07-22 03:30 | 27.11 | 26.21
2018-07-22 04:00 | 27.59 | 26.7
2018-07-22 04:30 | 27.75 | 26.87
2018-07-22 05:00 | 28.15 | 27.28
2018-07-22 05:30 | 28.93 | 28.08
2018-07-22 06:00 | 29.1 | 28.25
2018-07-22 06:30 | 29.98 | 29.15
2018-07-22 07:00 | 30.3 | 29.49
2018-07-22 07:30 | 32.13 | 31.36
2018-07-22 08:00 | 32.84 | 32.09
2018-07-22 08:30 | 33.6 | 32.85
2018-07-22 09:00 | 33.67 | 32.91
2018-07-22 09:30 | 34.01 | 33.25
2018-07-22 10:00 | 33.19 | 32.4
2018-07-22 10:30 | 33.29 | 32.5
2018-07-22 11:00 | 32.24 | 31.41
2018-07-22 11:30 | 32.21 | 31.36
2018-07-22 12:00 | 32.26 | 31.42
2018-07-22 12:30 | 31.32 | 30.44
2018-07-22 13:00 | 30.29 | 29.38
2018-07-22 13:30 | 30.54 | 29.64
2018-07-22 14:00 | 30.37 | 29.47
2018-07-22 14:30 | 31.25 | 30.38
2018-07-22 15:00 | 31.75 | 30.9
2018-07-22 15:30 | 32.82 | 32.01
2018-07-22 16:00 | 34.14 | 33.36
2018-07-22 16:30 | 36.73 | 36.02
2018-07-22 17:00 | 38.07 | 37.39
2018-07-22 17:30 | 41.07 | 40.45
2018-07-22 18:00 | 44.8 | 44.23
2018-07-22 18:30 | 46.79 | 46.24
2018-07-22 19:00 | 46.77 | 46.22
2018-07-22 19:30 | 43.57 | 42.98
2018-07-22 20:00 | 42.6 | 42
2018-07-22 20:30 | 40.71 | 40.09
2018-07-22 21:00 | 38.74 | 38.08
2018-07-22 21:30 | 37.08 | 36.39
2018-07-22 22:00 | 36.39 | 35.69
2018-07-22 22:30 | 34.73 | 34
2018-07-22 23:00 | 35.4 | 34.7
2018-07-22 23:30 | 32.06 | 31.28
2018-07-23 | 30.97 | 30.17
2018-07-23 00:30 | 30.34 | 29.52
2018-07-23 01:00 | 28.82 | 27.96
2018-07-23 01:30 | 28.26 | 27.38
2018-07-23 02:00 | 27.9 | 27.01
2018-07-23 02:30 | 27.23 | 26.33
2018-07-23 03:00 | 27.32 | 26.41
2018-07-23 03:30 | 27.01 | 26.09
2018-07-23 04:00 | 27.89 | 27
2018-07-23 04:30 | 29.2 | 28.35
2018-07-23 05:00 | 30.78 | 29.97
2018-07-23 05:30 | 33.53 | 32.77
2018-07-23 06:00 | 36.84 | 36.13
2018-07-23 06:30 | 41.81 | 41.16
2018-07-23 07:00 | 45.5 | 44.88
2018-07-23 07:30 | 49.92 | 49.42
2018-07-23 08:00 | 51.1 | 50.62
2018-07-23 08:30 | 50.5 | 50
2018-07-23 09:00 | 49.02 | 48.48
2018-07-23 09:30 | 47.59 | 47.03
2018-07-23 10:00 | 46.32 | 45.74
2018-07-23 10:30 | 46.84 | 46.29
2018-07-23 11:00 | 46.84 | 46.3
2018-07-23 11:30 | 46.49 | 45.94
2018-07-23 12:00 | 46.05 | 45.49
2018-07-23 12:30 | 45.74 | 45.19
2018-07-23 13:00 | 45.65 | 45.09
2018-07-23 13:30 | 45.92 | 45.36
2018-07-23 14:00 | 46.43 | 45.88
2018-07-23 14:30 | 46.73 | 46.18
2018-07-23 15:00 | 47.47 | 46.93
2018-07-23 15:30 | 47.51 | 46.98
2018-07-23 16:00 | 48.67 | 48.16
2018-07-23 16:30 | 49.96 | 49.49
2018-07-23 17:00 | 50.07 | 49.62
2018-07-23 17:30 | 50.6 | 50.18
2018-07-23 18:00 | 52.04 | 51.64
2018-07-23 18:30 | 53.14 | 52.76
2018-07-23 19:00 | 52.08 | 51.69
2018-07-23 19:30 | 50.75 | 50.36
2018-07-23 20:00 | 48.61 | 48.2
2018-07-23 20:30 | 46.17 | 45.69
2018-07-23 21:00 | 43.54 | 42.97
2018-07-23 21:30 | 42.35 | 41.68
2018-07-23 22:00 | 39.48 | 38.94
2018-07-23 22:30 | 38.18 | 37.63
2018-07-23 23:00 | 39.33 | 38.8
2018-07-23 23:30 | 36.21 | 35.64
2018-07-24 | 33.91 | 33.29
2018-07-24 00:30 | 33.87 | 32.04
2018-07-24 01:00 | 32.65 | 29.94
2018-07-24 01:30 | 32.26 | 29.5
2018-07-24 02:00 | 31.6 | 28.78
2018-07-24 02:30 | 31.14 | 28.26
2018-07-24 03:00 | 30.82 | 27.78
2018-07-24 03:30 | 30.97 | 27.95
2018-07-24 04:00 | 31.07 | 28.03
2018-07-24 04:30 | 32.16 | 29.1
2018-07-24 05:00 | 33.34 | 30.4
2018-07-24 05:30 | 35.37 | 32.59
2018-07-24 06:00 | 38.37 | 35.8
2018-07-24 06:30 | 43.21 | 40.9
2018-07-24 07:00 | 48.14 | 46.14
2018-07-24 07:30 | 54.06 | 52.27
2018-07-24 08:00 | 54.89 | 53.19
2018-07-24 08:30 | 53.56 | 51.78
2018-07-24 09:00 | 51.44 | 49.56
2018-07-24 09:30 | 49.69 | 47.73
2018-07-24 10:00 | 48.08 | 46.03
2018-07-24 10:30 | 47.96 | 45.89
2018-07-24 11:00 | 48.83 | 46.86
2018-07-24 11:30 | 47.51 | 45.49
2018-07-24 12:00 | 47.67 | 45.65
2018-07-24 12:30 | 47.93 | 45.93
2018-07-24 13:00 | 47.07 | 45.03
2018-07-24 13:30 | 47.62 | 45.61
2018-07-24 14:00 | 48.09 | 46.11
2018-07-24 14:30 | 48.16 | 46.17
2018-07-24 15:00 | 48.4 | 46.44
2018-07-24 15:30 | 49.32 | 47.42
2018-07-24 16:00 | 49.66 | 47.8
2018-07-24 16:30 | 51.04 | 49.27
2018-07-24 17:00 | 51.62 | 49.91
2018-07-24 17:30 | 52.21 | 50.56
2018-07-24 18:00 | 53.4 | 51.81
2018-07-24 18:30 | 54.44 | 52.89
2018-07-24 19:00 | 54.14 | 52.59
2018-07-24 19:30 | 52.28 | 50.68
2018-07-24 20:00 | 50.2 | 48.53
2018-07-24 20:30 | 48.14 | 46.4
2018-07-24 21:00 | 45.09 | 43.23
2018-07-24 21:30 | 44.34 | 42.45
2018-07-24 22:00 | 43.3 | 41.29
2018-07-24 22:30 | 41.66 | 39.55
2018-07-24 23:00 | 42.49 | 40.43
2018-07-24 23:30 | 38.35 | 36.05
2018-07-25 | 35.27 | 32.75
2018-07-25 00:30 | 35.08 | 32.55
2018-07-25 01:00 | 34.03 | 31.42
2018-07-25 01:30 | 33.24 | 30.55
2018-07-25 02:00 | 32.22 | 29.44
2018-07-25 02:30 | 31.53 | 28.48
2018-07-25 03:00 | 31.71 | 28.61
2018-07-25 03:30 | 31.37 | 28.25
2018-07-25 04:00 | 30.35 | 27.1
2018-07-25 04:30 | 32.12 | 29.07
2018-07-25 05:00 | 33.42 | 30.49
2018-07-25 05:30 | 34.82 | 32
2018-07-25 06:00 | 38.49 | 35.95
2018-07-25 06:30 | 44.14 | 41.9
2018-07-25 07:00 | 47.79 | 45.77
2018-07-25 07:30 | 51.67 | 49.99
2018-07-25 08:00 | 52.66 | 52.32
2018-07-25 08:30 | 49.97 | 49.83
2018-07-25 09:00 | 48.39 | 48.16
2018-07-25 09:30 | 46.71 | 46.44
2018-07-25 10:00 | 46.38 | 46.05
2018-07-25 10:30 | 45.85 | 45.54
2018-07-25 11:00 | 45.26 | 45.14
2018-07-25 11:30 | 45.36 | 45.2
2018-07-25 12:00 | 45.71 | 45.53
2018-07-25 12:30 | 46.86 | 46.71
2018-07-25 13:00 | 45.48 | 45.35
2018-07-25 13:30 | 45.73 | 45.57
2018-07-25 14:00 | 45.94 | 45.79
2018-07-25 14:30 | 47.25 | 47.08
2018-07-25 15:00 | 47.15 | 46.99
2018-07-25 15:30 | 47.43 | 47.3
2018-07-25 16:00 | 48.44 | 48.39
2018-07-25 16:30 | 50.47 | 50.46
2018-07-25 17:00 | 49.61 | 49.61
2018-07-25 17:30 | 50.17 | 50.11
2018-07-25 18:00 | 52.15 | 52.05
2018-07-25 18:30 | 53.44 | 53.35
2018-07-25 19:00 | 52.91 | 52.79
2018-07-25 19:30 | 50.66 | 50.49
2018-07-25 20:00 | 48.41 | 48.16
2018-07-25 20:30 | 46.4 | 46.01
2018-07-25 21:00 | 44.05 | 43.58
2018-07-25 21:30 | 41.99 | 41.38
2018-07-25 22:00 | 40.47 | 38.9
2018-07-25 22:30 | 40.54 | 38.36
2018-07-25 23:00 | 41.77 | 39.66
2018-07-25 23:30 | 38.03 | 35.69
2018-07-26 | 35.78 | 33.29
2018-07-26 00:30 | 34.82 | 32.27
2018-07-26 01:00 | 33.49 | 30.82
2018-07-26 01:30 | 32.08 | 29.28
2018-07-26 02:00 | 31.09 | 28.14
2018-07-26 02:30 | 30.69 | 27.46
2018-07-26 03:00 | 30.17 | 26.88
2018-07-26 03:30 | 30.12 | 26.83
2018-07-26 04:00 | 30.3 | 27.02
2018-07-26 04:30 | 31.27 | 28.11
2018-07-26 05:00 | 32.31 | 29.25
2018-07-26 05:30 | 36.14 | 33.42
2018-07-26 06:00 | 38.47 | 35.9
2018-07-26 06:30 | 44.04 | 41.78
2018-07-26 07:00 | 48.02 | 46.02
2018-07-26 07:30 | 51.9 | 50.04
2018-07-26 08:00 | 53.59 | 51.76
2018-07-26 08:30 | 51.88 | 51.05
2018-07-26 09:00 | 51.16 | 50.22
2018-07-26 09:30 | 49.58 | 48.41
2018-07-26 10:00 | 48.93 | 47.73
2018-07-26 10:30 | 48.86 | 48.64
2018-07-26 11:00 | 47.61 | 47.39
2018-07-26 11:30 | 47.32 | 47.03
2018-07-26 12:00 | 46.33 | 46.04
2018-07-26 12:30 | 46.82 | 46.57
2018-07-26 13:00 | 47.18 | 46.94
2018-07-26 13:30 | 47.13 | 46.89
2018-07-26 14:00 | 46.64 | 46.37
2018-07-26 14:30 | 46.57 | 46.32
2018-07-26 15:00 | 47.92 | 47.7
2018-07-26 15:30 | 49.01 | 48.86
2018-07-26 16:00 | 49.76 | 49.68
2018-07-26 16:30 | 51.06 | 51.04
2018-07-26 17:00 | 51.41 | 51.4
2018-07-26 17:30 | 50.89 | 50.84
2018-07-26 18:00 | 53.34 | 53.26
2018-07-26 18:30 | 54.87 | 54.8
2018-07-26 19:00 | 53.54 | 53.43
2018-07-26 19:30 | 51.66 | 51.51
2018-07-26 20:00 | 48.96 | 48.73
2018-07-26 20:30 | 47.42 | 47.11
2018-07-26 21:00 | 45.61 | 45.22
2018-07-26 21:30 | 43.52 | 42.94
2018-07-26 22:00 | 41.89 | 40.99
2018-07-26 22:30 | 41.37 | 39.26
2018-07-26 23:00 | 41.51 | 39.4
2018-07-26 23:30 | 38.51 | 36.22
2018-07-27 | 35.6 | 33.12
2018-07-27 00:30 | 35.14 | 32.61
2018-07-27 01:00 | 33.99 | 31.39
2018-07-27 01:30 | 33.08 | 30.39
2018-07-27 02:00 | 31.85 | 28.97
2018-07-27 02:30 | 31.23 | 28.08
2018-07-27 03:00 | 30.97 | 27.79
2018-07-27 03:30 | 31.24 | 28.1
2018-07-27 04:00 | 31.15 | 27.99
2018-07-27 04:30 | 32.06 | 29.01
2018-07-27 05:00 | 33.4 | 30.48
2018-07-27 05:30 | 35.21 | 32.42
2018-07-27 06:00 | 38.78 | 36.25
2018-07-27 06:30 | 43.6 | 41.33
2018-07-27 07:00 | 47.45 | 45.45
2018-07-27 07:30 | 51.21 | 49.33
2018-07-27 08:00 | 51.93 | 51.25
2018-07-27 08:30 | 53.13 | 52.68
2018-07-27 09:00 | 52.03 | 51.6
2018-07-27 09:30 | 50.46 | 49.95
2018-07-27 10:00 | 49.46 | 49.16
2018-07-27 10:30 | 50.05 | 49.85
2018-07-27 11:00 | 49 | 48.72
2018-07-27 11:30 | 49.13 | 48.81
2018-07-27 12:00 | 49.01 | 48.64
2018-07-27 12:30 | 49.08 | 48.71
2018-07-27 13:00 | 48.67 | 48.36
2018-07-27 13:30 | 49.1 | 48.8
2018-07-27 14:00 | 49.29 | 49.02
2018-07-27 14:30 | 48.3 | 48.09
2018-07-27 15:00 | 46.22 | 46.09
2018-07-27 15:30 | 45.98 | 45.93
2018-07-27 16:00 | 46.8 | 46.79
2018-07-27 16:30 | 47.03 | 47.03
2018-07-27 17:00 | 48.32 | 48.31
2018-07-27 17:30 | 48.59 | 48.49
2018-07-27 18:00 | 50.45 | 50.34
2018-07-27 18:30 | 51.58 | 51.48
2018-07-27 19:00 | 50.5 | 50.34
2018-07-27 19:30 | 47.72 | 47.5
2018-07-27 20:00 | 45.65 | 45.39
2018-07-27 20:30 | 44.11 | 43.69
2018-07-27 21:00 | 42.45 | 41.95
2018-07-27 21:30 | 41.8 | 41.19
2018-07-27 22:00 | 40.41 | 39.65
2018-07-27 22:30 | 39.1 | 38.49
2018-07-27 23:00 | 39.79 | 39.27
2018-07-27 23:30 | 35.85 | 35.26
2018-07-28 | 33.73 | 33.05
2018-07-28 00:30 | 32.62 | 31.84
2018-07-28 01:00 | 31.31 | 30.49
2018-07-28 01:30 | 30.44 | 29.6
2018-07-28 02:00 | 29.49 | 28.63
2018-07-28 02:30 | 29.14 | 28.27
2018-07-28 03:00 | 28.7 | 27.82
2018-07-28 03:30 | 28.82 | 27.95
2018-07-28 04:00 | 28.87 | 28
2018-07-28 04:30 | 28.91 | 28.04
2018-07-28 05:00 | 28.84 | 27.97
2018-07-28 05:30 | 30.63 | 29.81
2018-07-28 06:00 | 31.53 | 30.74
2018-07-28 06:30 | 33.51 | 32.75
2018-07-28 07:00 | 34.68 | 33.95
2018-07-28 07:30 | 36.57 | 35.87
2018-07-28 08:00 | 37.41 | 36.71
2018-07-28 08:30 | 37.62 | 36.92
2018-07-28 09:00 | 37.92 | 37.22
2018-07-28 09:30 | 38.01 | 37.29
2018-07-28 10:00 | 38.5 | 37.77
2018-07-28 10:30 | 38.07 | 37.32
2018-07-28 11:00 | 37.6 | 36.79
2018-07-28 11:30 | 36.49 | 35.68
2018-07-28 12:00 | 35.84 | 35.01
2018-07-28 12:30 | 33.72 | 32.87
2018-07-28 13:00 | 33.23 | 32.38
2018-07-28 13:30 | 33.05 | 32.2
2018-07-28 14:00 | 33.61 | 32.77
2018-07-28 14:30 | 33.77 | 32.94
2018-07-28 15:00 | 35.43 | 34.64
2018-07-28 15:30 | 35.46 | 34.68
2018-07-28 16:00 | 36.45 | 35.7
2018-07-28 16:30 | 38.57 | 37.87
2018-07-28 17:00 | 39.78 | 39.12
2018-07-28 17:30 | 42.06 | 41.44
2018-07-28 18:00 | 44.51 | 43.91
2018-07-28 18:30 | 44.99 | 44.38
2018-07-28 19:00 | 44.85 | 44.25
2018-07-28 19:30 | 42.57 | 41.93
2018-07-28 20:00 | 41.53 | 40.88
2018-07-28 20:30 | 39.62 | 38.94
2018-07-28 21:00 | 39.46 | 38.77
2018-07-28 21:30 | 37.84 | 37.14
2018-07-28 22:00 | 37.51 | 36.81
2018-07-28 22:30 | 35.93 | 35.21
2018-07-28 23:00 | 37.41 | 36.72
2018-07-28 23:30 | 33.91 | 33.15
2018-07-29 | 31.02 | 30.19
2018-07-29 00:30 | 30.69 | 29.86
2018-07-29 01:00 | 29.31 | 28.44
2018-07-29 01:30 | 29.07 | 28.2
2018-07-29 02:00 | 28.88 | 28
2018-07-29 02:30 | 28.35 | 27.46
2018-07-29 03:00 | 28.12 | 27.23
2018-07-29 03:30 | 26.98 | 26.04
2018-07-29 04:00 | 27.46 | 26.54
2018-07-29 04:30 | 27.76 | 26.85
2018-07-29 05:00 | 28.14 | 27.24
2018-07-29 05:30 | 29.19 | 28.32
2018-07-29 06:00 | 29.75 | 28.9
2018-07-29 06:30 | 30.95 | 30.13
2018-07-29 07:00 | 31.78 | 30.99
2018-07-29 07:30 | 32.9 | 32.13
2018-07-29 08:00 | 33.4 | 32.63
2018-07-29 08:30 | 33.51 | 32.73
2018-07-29 09:00 | 34.37 | 33.6
2018-07-29 09:30 | 34.82 | 34.05
2018-07-29 10:00 | 34.69 | 33.91
2018-07-29 10:30 | 34.83 | 34.04
2018-07-29 11:00 | 33.43 | 32.59
2018-07-29 11:30 | 33.53 | 32.7
2018-07-29 12:00 | 32.16 | 31.29
2018-07-29 12:30 | 31.51 | 30.62
2018-07-29 13:00 | 31.33 | 30.44
2018-07-29 13:30 | 31.12 | 30.21
2018-07-29 14:00 | 31.67 | 30.78
2018-07-29 14:30 | 32.34 | 31.48
2018-07-29 15:00 | 32.91 | 32.07
2018-07-29 15:30 | 34.77 | 33.99
2018-07-29 16:00 | 35.99 | 35.24
2018-07-29 16:30 | 37.93 | 37.22
2018-07-29 17:00 | 39.13 | 38.46
2018-07-29 17:30 | 41.84 | 41.22
2018-07-29 18:00 | 44.88 | 44.3
2018-07-29 18:30 | 46.62 | 46.06
2018-07-29 19:00 | 46.18 | 45.62
2018-07-29 19:30 | 44.36 | 43.77
2018-07-29 20:00 | 42.76 | 42.15
2018-07-29 20:30 | 40.37 | 39.74
2018-07-29 21:00 | 39.32 | 38.66
2018-07-29 21:30 | 37.29 | 36.61
2018-07-29 22:00 | 35.92 | 35.21
2018-07-29 22:30 | 34.4 | 33.68
2018-07-29 23:00 | 36 | 35.31
2018-07-29 23:30 | 32.46 | 31.69
2018-07-30 | 30.44 | 29.63
2018-07-30 00:30 | 29.3 | 28.46
2018-07-30 01:00 | 28.26 | 27.39
2018-07-30 01:30 | 27.49 | 26.59
2018-07-30 02:00 | 27.92 | 27.04
2018-07-30 02:30 | 28.59 | 27.73
2018-07-30 03:00 | 28.51 | 27.65
2018-07-30 03:30 | 28.61 | 27.76
2018-07-30 04:00 | 29.12 | 28.27
2018-07-30 04:30 | 29.52 | 28.68
2018-07-30 05:00 | 29.99 | 29.16
2018-07-30 05:30 | 32.55 | 31.77
2018-07-30 06:00 | 35.27 | 34.54
2018-07-30 06:30 | 39.8 | 39.13
2018-07-30 07:00 | 45.09 | 44.49
2018-07-30 07:30 | 49.56 | 49.04
2018-07-30 08:00 | 50.27 | 49.73
2018-07-30 08:30 | 49.58 | 49.01
2018-07-30 09:00 | 49.31 | 48.76
2018-07-30 09:30 | 48.22 | 47.64
2018-07-30 10:00 | 47.23 | 46.68
2018-07-30 10:30 | 46.85 | 46.3
2018-07-30 11:00 | 47.53 | 46.98
2018-07-30 11:30 | 47.65 | 47.1
2018-07-30 12:00 | 47.14 | 46.58
2018-07-30 12:30 | 46.78 | 46.22
2018-07-30 13:00 | 45.92 | 45.35
2018-07-30 13:30 | 45.93 | 45.35
2018-07-30 14:00 | 46.05 | 45.48
2018-07-30 14:30 | 47.18 | 46.63
2018-07-30 15:00 | 48.16 | 47.62
2018-07-30 15:30 | 48.06 | 47.54
2018-07-30 16:00 | 49.33 | 48.83
2018-07-30 16:30 | 50.62 | 50.15
2018-07-30 17:00 | 50.37 | 49.92
2018-07-30 17:30 | 50.61 | 50.19
2018-07-30 18:00 | 51.11 | 50.71
2018-07-30 18:30 | 53.2 | 52.82
2018-07-30 19:00 | 53.1 | 52.73
2018-07-30 19:30 | 50.7 | 50.31
2018-07-30 20:00 | 47.58 | 47.16
2018-07-30 20:30 | 45.78 | 45.26
2018-07-30 21:00 | 43.22 | 42.71
2018-07-30 21:30 | 41.43 | 40.85
2018-07-30 22:00 | 39.64 | 38.99
2018-07-30 22:30 | 38.26 | 37.58
2018-07-30 23:00 | 39.05 | 38.38
2018-07-30 23:30 | 35.61 | 34.88
2018-07-31 | 33.72 | 32.95
2018-07-31 00:30 | 32.43 | 31.63
2018-07-31 01:00 | 30.77 | 29.94
2018-07-31 01:30 | 30.64 | 29.8
2018-07-31 02:00 | 30.06 | 29.21
2018-07-31 02:30 | 28.2 | 27.31
2018-07-31 03:00 | 27.58 | 26.67
2018-07-31 03:30 | 28.02 | 27.12
2018-07-31 04:00 | 28.61 | 27.74
2018-07-31 04:30 | 29.38 | 28.53
2018-07-31 05:00 | 30.19 | 29.36
2018-07-31 05:30 | 33.75 | 32.99
2018-07-31 06:00 | 36.76 | 36.05
2018-07-31 06:30 | 40.76 | 40.1
2018-07-31 07:00 | 45.6 | 45.04
2018-07-31 07:30 | 50.56 | 50.03
2018-07-31 08:00 | 51.08 | 50.54
2018-07-31 08:30 | 50.91 | 50.38
2018-07-31 09:00 | 49.54 | 49.01
2018-07-31 09:30 | 48.19 | 47.63
2018-07-31 10:00 | 46.67 | 46.09
2018-07-31 10:30 | 46.19 | 45.59
2018-07-31 11:00 | 45.12 | 44.52
2018-07-31 11:30 | 44.42 | 43.84
2018-07-31 12:00 | 43.75 | 43.15
2018-07-31 12:30 | 43.53 | 42.94
2018-07-31 13:00 | 43.21 | 42.61
2018-07-31 13:30 | 44.34 | 43.76
2018-07-31 14:00 | 46.14 | 45.57
2018-07-31 14:30 | 47.13 | 46.58
2018-07-31 15:00 | 47.3 | 46.76
2018-07-31 15:30 | 47.84 | 47.31
2018-07-31 16:00 | 49.1 | 48.6
2018-07-31 16:30 | 51.53 | 51.06
2018-07-31 17:00 | 51.87 | 51.43
2018-07-31 17:30 | 51.21 | 50.79
2018-07-31 18:00 | 52.59 | 52.2
2018-07-31 18:30 | 55.43 | 55.06
2018-07-31 19:00 | 54.88 | 54.51
2018-07-31 19:30 | 51.35 | 50.97
2018-07-31 20:00 | 48.89 | 48.49
2018-07-31 20:30 | 47.64 | 47.22
2018-07-31 21:00 | 46.02 | 45.52
2018-07-31 21:30 | 44.03 | 43.38
2018-07-31 22:00 | 41.73 | 41.16
2018-07-31 22:30 | 39.97 | 39.39
2018-07-31 23:00 | 41.13 | 40.5
2018-07-31 23:30 | 37.14 | 36.44
2018-08-01 | 34.69 | 33.95
2018-08-01 00:30 | 34.3 | 33.55
2018-08-01 01:00 | 33.3 | 32.52
2018-08-01 01:30 | 32.3 | 31.5
2018-08-01 02:00 | 30.78 | 29.94
2018-08-01 02:30 | 30.6 | 29.77
2018-08-01 03:00 | 29.8 | 28.95
2018-08-01 03:30 | 29.84 | 28.99
2018-08-01 04:00 | 30.48 | 29.64
2018-08-01 04:30 | 30.86 | 30.04
2018-08-01 05:00 | 32.85 | 32.07
2018-08-01 05:30 | 34.64 | 33.9
2018-08-01 06:00 | 38.41 | 37.72
2018-08-01 06:30 | 43.68 | 43.05
2018-08-01 07:00 | 48.94 | 48.42
2018-08-01 07:30 | 52.35 | 51.84
2018-08-01 08:00 | 54.23 | 53.69
2018-08-01 08:30 | 53.65 | 52.95
2018-08-01 09:00 | 52.08 | 51.57
2018-08-01 09:30 | 49.61 | 49.07
2018-08-01 10:00 | 47.9 | 47.33
2018-08-01 10:30 | 48.73 | 48.15
2018-08-01 11:00 | 48.62 | 47.93
2018-08-01 11:30 | 48.11 | 47.57
2018-08-01 12:00 | 47.89 | 47.34
2018-08-01 12:30 | 48.44 | 47.89
2018-08-01 13:00 | 48.12 | 47.57
2018-08-01 13:30 | 48.37 | 47.82
2018-08-01 14:00 | 48.71 | 48.17
2018-08-01 14:30 | 49.4 | 48.86
2018-08-01 15:00 | 48.06 | 47.52
2018-08-01 15:30 | 48.5 | 47.97
2018-08-01 16:00 | 50.17 | 49.67
2018-08-01 16:30 | 51.42 | 50.96
2018-08-01 17:00 | 50.99 | 50.55
2018-08-01 17:30 | 51.18 | 50.76
2018-08-01 18:00 | 52.12 | 51.72
2018-08-01 18:30 | 54.69 | 54.31
2018-08-01 19:00 | 55.11 | 54.73
2018-08-01 19:30 | 52.66 | 52.27
2018-08-01 20:00 | 50.92 | 50.53
2018-08-01 20:30 | 48.27 | 47.86
2018-08-01 21:00 | 46.28 | 45.85
2018-08-01 21:30 | 43.2 | 42.67
2018-08-01 22:00 | 41.81 | 41.27
2018-08-01 22:30 | 39.72 | 39.18
2018-08-01 23:00 | 40.81 | 40.3
2018-08-01 23:30 | 38.13 | 37.58
2018-08-02 | 35.06 | 34.43
2018-08-02 00:30 | 34.05 | 33.38
2018-08-02 01:00 | 32.16 | 31.44
2018-08-02 01:30 | 31.49 | 30.76
2018-08-02 02:00 | 30.29 | 29.53
2018-08-02 02:30 | 30.25 | 29.5
2018-08-02 03:00 | 30.48 | 29.74
2018-08-02 03:30 | 30.04 | 29.28
2018-08-02 04:00 | 30.64 | 29.9
2018-08-02 04:30 | 31.57 | 30.86
2018-08-02 05:00 | 32.1 | 31.39
2018-08-02 05:30 | 34.81 | 34.14
2018-08-02 06:00 | 39.04 | 38.43
2018-08-02 06:30 | 44.05 | 43.5
2018-08-02 07:00 | 47.78 | 47.25
2018-08-02 07:30 | 52.41 | 51.9
2018-08-02 08:00 | 53.16 | 52.61
2018-08-02 08:30 | 51.4 | 50.73
2018-08-02 09:00 | 49.06 | 48.52
2018-08-02 09:30 | 33.64 | 32.85
2018-08-02 10:00 | 27.71 | 26.73
2018-08-02 10:30 | 27.5 | 26.36
2018-08-02 11:00 | 27.17 | 26.55
2018-08-02 11:30 | 27.33 | 26.37
2018-08-02 12:00 | 42.7 | 42.08
2018-08-02 12:30 | 45.24 | 44.66
2018-08-02 13:00 | 45.07 | 44.49
2018-08-02 13:30 | 45.76 | 45.18
2018-08-02 14:00 | 45.93 | 45.34
2018-08-02 14:30 | 47.57 | 47.01
2018-08-02 15:00 | 48.69 | 48.15
2018-08-02 15:30 | 48.43 | 47.9
2018-08-02 16:00 | 49.47 | 48.96
2018-08-02 16:30 | 51.94 | 51.49
2018-08-02 17:00 | 51.45 | 51.01
2018-08-02 17:30 | 52.38 | 51.97
2018-08-02 18:00 | 53.31 | 52.92
2018-08-02 18:30 | 49.1 | 48.68
2018-08-02 19:00 | 48.79 | 48.38
2018-08-02 19:30 | 46.99 | 46.57
2018-08-02 20:00 | 49.02 | 48.61
2018-08-02 20:30 | 51.24 | 50.84
2018-08-02 21:00 | 49.19 | 48.78
2018-08-02 21:30 | 46.5 | 46.06
2018-08-02 22:00 | 44.08 | 43.59
2018-08-02 22:30 | 42.46 | 41.95
2018-08-02 23:00 | 42.77 | 42.26
2018-08-02 23:30 | 40.19 | 39.65
2018-08-03 | 37.49 | 36.91
2018-08-03 00:30 | 36.16 | 35.57
2018-08-03 01:00 | 34.32 | 33.69
2018-08-03 01:30 | 33.78 | 33.16
2018-08-03 02:00 | 33.4 | 32.73
2018-08-03 02:30 | 32.11 | 31.39
2018-08-03 03:00 | 32.18 | 31.46
2018-08-03 03:30 | 31.73 | 31
2018-08-03 04:00 | 31.76 | 31.04
2018-08-03 04:30 | 31.94 | 31.15
2018-08-03 05:00 | 34.08 | 33.32
2018-08-03 05:30 | 36.25 | 35.52
2018-08-03 06:00 | 38.72 | 38.03
2018-08-03 06:30 | 44.52 | 43.9
2018-08-03 07:00 | 48.44 | 47.9
2018-08-03 07:30 | 52.54 | 52.02
2018-08-03 08:00 | 52.97 | 52.47
2018-08-03 08:30 | 52.5 | 52
2018-08-03 09:00 | 51.01 | 50.48
2018-08-03 09:30 | 50.99 | 50.45
2018-08-03 10:00 | 49.56 | 49.02
2018-08-03 10:30 | 50.23 | 49.71
2018-08-03 11:00 | 50.04 | 49.51
2018-08-03 11:30 | 49.9 | 49.36
2018-08-03 12:00 | 48.69 | 48.13
2018-08-03 12:30 | 49.46 | 48.92
2018-08-03 13:00 | 48.27 | 47.71
2018-08-03 13:30 | 49.2 | 48.65
2018-08-03 14:00 | 51.07 | 50.56
2018-08-03 14:30 | 47.47 | 46.93
2018-08-03 15:00 | 46.68 | 46.14
2018-08-03 15:30 | 47.15 | 46.63
2018-08-03 16:00 | 47.85 | 47.36
2018-08-03 16:30 | 49.69 | 49.23
2018-08-03 17:00 | 49.63 | 49.19
2018-08-03 17:30 | 49.03 | 48.61
2018-08-03 18:00 | 50.19 | 49.79
2018-08-03 18:30 | 51.92 | 51.54
2018-08-03 19:00 | 50.25 | 49.86
2018-08-03 19:30 | 47.39 | 46.98
2018-08-03 20:00 | 46.02 | 45.58
2018-08-03 20:30 | 44.11 | 43.57
2018-08-03 21:00 | 42.42 | 41.85
2018-08-03 21:30 | 41.03 | 40.51
2018-08-03 22:00 | 38.98 | 38.41
2018-08-03 22:30 | 37.94 | 37.27
2018-08-03 23:00 | 38.66 | 37.99
2018-08-03 23:30 | 34.8 | 34.06
2018-08-04 | 32.33 | 31.55
2018-08-04 00:30 | 32.43 | 31.65
2018-08-04 01:00 | 30.28 | 29.45
2018-08-04 01:30 | 29.76 | 28.91
2018-08-04 02:00 | 28.53 | 27.66
2018-08-04 02:30 | 28.84 | 27.98
2018-08-04 03:00 | 28.63 | 27.77
2018-08-04 03:30 | 28.24 | 27.36
2018-08-04 04:00 | 27.54 | 26.64
2018-08-04 04:30 | 28.17 | 27.29
2018-08-04 05:00 | 28.44 | 27.56
2018-08-04 05:30 | 29.17 | 28.31
2018-08-04 06:00 | 30.36 | 29.53
2018-08-04 06:30 | 33.66 | 32.9
2018-08-04 07:00 | 35 | 34.26
2018-08-04 07:30 | 37.35 | 36.65
2018-08-04 08:00 | 38.62 | 37.93
2018-08-04 08:30 | 40.15 | 39.48
2018-08-04 09:00 | 41.33 | 40.66
2018-08-04 09:30 | 41.69 | 41.02
2018-08-04 10:00 | 39.8 | 39.08
2018-08-04 10:30 | 39.85 | 39.04
2018-08-04 11:00 | 39.47 | 38.54
2018-08-04 11:30 | 37.89 | 36.9
2018-08-04 12:00 | 36.5 | 35.49
2018-08-04 12:30 | 34.9 | 33.99
2018-08-04 13:00 | 34.03 | 33.19
2018-08-04 13:30 | 34 | 33.23
2018-08-04 14:00 | 34.07 | 33.31
2018-08-04 14:30 | 34.45 | 33.71
2018-08-04 15:00 | 34.81 | 34.08
2018-08-04 15:30 | 35.72 | 35.03
2018-08-04 16:00 | 37.61 | 36.95
2018-08-04 16:30 | 39.25 | 38.63
2018-08-04 17:00 | 40.5 | 39.91
2018-08-04 17:30 | 41.8 | 41.23
2018-08-04 18:00 | 44.1 | 43.57
2018-08-04 18:30 | 46.79 | 46.28
2018-08-04 19:00 | 46.08 | 45.57
2018-08-04 19:30 | 43.86 | 43.32
2018-08-04 20:00 | 42.14 | 41.59
2018-08-04 20:30 | 40.07 | 39.48
2018-08-04 21:00 | 39.21 | 38.62
2018-08-04 21:30 | 37.14 | 36.51
2018-08-04 22:00 | 36.52 | 35.84
2018-08-04 22:30 | 35.9 | 35.19
2018-08-04 23:00 | 37.73 | 37.05
2018-08-04 23:30 | 34.12 | 33.38
2018-08-05 | 32.08 | 31.3
2018-08-05 00:30 | 31.27 | 30.47
2018-08-05 01:00 | 29.13 | 28.27
2018-08-05 01:30 | 28.95 | 28.09
2018-08-05 02:00 | 29.78 | 28.95
2018-08-05 02:30 | 28.56 | 27.69
2018-08-05 03:00 | 28.3 | 27.44
2018-08-05 03:30 | 28.38 | 27.52
2018-08-05 04:00 | 28.13 | 27.26
2018-08-05 04:30 | 28.5 | 27.64
2018-08-05 05:00 | 28.46 | 27.59
2018-08-05 05:30 | 28.79 | 27.94
2018-08-05 06:00 | 29.95 | 29.12
2018-08-05 06:30 | 31.42 | 30.63
2018-08-05 07:00 | 30.58 | 29.77
2018-08-05 07:30 | 31.71 | 30.94
2018-08-05 08:00 | 33.23 | 32.49
2018-08-05 08:30 | 33.92 | 33.18
2018-08-05 09:00 | 33.77 | 33.02
2018-08-05 09:30 | 34.23 | 33.47
2018-08-05 10:00 | 34.2 | 33.42
2018-08-05 10:30 | 35.15 | 34.38
2018-08-05 11:00 | 34.11 | 33.31
2018-08-05 11:30 | 33.77 | 32.94
2018-08-05 12:00 | 33.24 | 32.4
2018-08-05 12:30 | 32.77 | 31.92
2018-08-05 13:00 | 32.89 | 32.04
2018-08-05 13:30 | 31.87 | 30.99
2018-08-05 14:00 | 33.32 | 32.48
2018-08-05 14:30 | 33.07 | 32.23
2018-08-05 15:00 | 33.43 | 32.6
2018-08-05 15:30 | 34.88 | 34.1
2018-08-05 16:00 | 36.58 | 35.84
2018-08-05 16:30 | 39.81 | 39.14
2018-08-05 17:00 | 40.69 | 40.03
2018-08-05 17:30 | 42.7 | 42.09
2018-08-05 18:00 | 46.18 | 45.62
2018-08-05 18:30 | 49.25 | 48.72
2018-08-05 19:00 | 48.92 | 48.38
2018-08-05 19:30 | 46.84 | 46.28
2018-08-05 20:00 | 44.45 | 43.86
2018-08-05 20:30 | 42.44 | 41.82
2018-08-05 21:00 | 41.16 | 40.53
2018-08-05 21:30 | 38.31 | 37.63
2018-08-05 22:00 | 37.59 | 36.91
2018-08-05 22:30 | 36.81 | 36.12
2018-08-05 23:00 | 36.72 | 36.03
2018-08-05 23:30 | 34 | 33.26
2018-08-06 | 31.28 | 30.47
2018-08-06 00:30 | 31.13 | 30.33
2018-08-06 01:00 | 30.36 | 29.53
2018-08-06 01:30 | 29.32 | 28.48
2018-08-06 02:00 | 28.7 | 27.83
2018-08-06 02:30 | 28.89 | 28.02
2018-08-06 03:00 | 29.17 | 28.31
2018-08-06 03:30 | 28.96 | 28.1
2018-08-06 04:00 | 28.42 | 27.55
2018-08-06 04:30 | 29.24 | 28.38
2018-08-06 05:00 | 31.76 | 30.96
2018-08-06 05:30 | 33.76 | 33
2018-08-06 06:00 | 35.88 | 35.14
2018-08-06 06:30 | 41.45 | 40.79
2018-08-06 07:00 | 45.45 | 44.79
2018-08-06 07:30 | 49.7 | 49.16
2018-08-06 08:00 | 51.19 | 50.61
2018-08-06 08:30 | 51.91 | 51.14
2018-08-06 09:00 | 51.81 | 50.78
2018-08-06 09:30 | 50.58 | 49.48
2018-08-06 10:00 | 50.21 | 49.7
2018-08-06 10:30 | 51.25 | 50.75
2018-08-06 11:00 | 50.68 | 50.16
2018-08-06 11:30 | 51.06 | 50.53
2018-08-06 12:00 | 51.46 | 50.94
2018-08-06 12:30 | 50.86 | 50.32
2018-08-06 13:00 | 49.84 | 49.3
2018-08-06 13:30 | 49.81 | 49.27
2018-08-06 14:00 | 50.15 | 49.61
2018-08-06 14:30 | 51.04 | 50.51
2018-08-06 15:00 | 51.6 | 51.09
2018-08-06 15:30 | 51.55 | 51.05
2018-08-06 16:00 | 51.95 | 51.47
2018-08-06 16:30 | 53.76 | 53.31
2018-08-06 17:00 | 53.24 | 52.8
2018-08-06 17:30 | 53.08 | 52.67
2018-08-06 18:00 | 54.06 | 53.67
2018-08-06 18:30 | 56.18 | 55.81
2018-08-06 19:00 | 55.29 | 54.92
2018-08-06 19:30 | 52.52 | 52.13
2018-08-06 20:00 | 50.43 | 50.03
2018-08-06 20:30 | 47.29 | 46.87
2018-08-06 21:00 | 47.29 | 46.87
2018-08-06 21:30 | 45.04 | 44.59
2018-08-06 22:00 | 43.25 | 42.68
2018-08-06 22:30 | 42.48 | 41.87
2018-08-06 23:00 | 42.02 | 41.44
2018-08-06 23:30 | 36.89 | 36.32
2018-08-07 | 33.99 | 33.37
2018-08-07 00:30 | 33.83 | 33.2
2018-08-07 01:00 | 32.43 | 31.78
2018-08-07 01:30 | 32.49 | 31.84
2018-08-07 02:00 | 31.11 | 30.42
2018-08-07 02:30 | 31.75 | 31.03
2018-08-07 03:00 | 30.08 | 29.23
2018-08-07 03:30 | 29.59 | 28.73
2018-08-07 04:00 | 29.82 | 28.97
2018-08-07 04:30 | 30.98 | 30.16
2018-08-07 05:00 | 32.48 | 31.68
2018-08-07 05:30 | 35.15 | 34.4
2018-08-07 06:00 | 37.99 | 37.28
2018-08-07 06:30 | 43.54 | 42.8
2018-08-07 07:00 | 47.71 | 47.14
2018-08-07 07:30 | 53.14 | 52.47
2018-08-07 08:00 | 55.65 | 55.1
2018-08-07 08:30 | 57.31 | 56.25
2018-08-07 09:00 | 56.58 | 55.83
2018-08-07 09:30 | 56.76 | 56.12
2018-08-07 10:00 | 56.63 | 56.02
2018-08-07 10:30 | 56.12 | 55.49
2018-08-07 11:00 | 56.16 | 55.44
2018-08-07 11:30 | 55.51 | 54.74
2018-08-07 12:00 | 54.62 | 53.93
2018-08-07 12:30 | 54.07 | 53.42
2018-08-07 13:00 | 54.57 | 53.97
2018-08-07 13:30 | 56.56 | 55.99
2018-08-07 14:00 | 56.16 | 55.6
2018-08-07 14:30 | 54.82 | 54.3
2018-08-07 15:00 | 53.64 | 53.17
2018-08-07 15:30 | 51.91 | 51.51
2018-08-07 16:00 | 51.53 | 51.12
2018-08-07 16:30 | 52.06 | 51.64
2018-08-07 17:00 | 50.8 | 50.35
2018-08-07 17:30 | 51.68 | 51.21
2018-08-07 18:00 | 53.26 | 52.8
2018-08-07 18:30 | 54.72 | 54.28
2018-08-07 19:00 | 54.34 | 53.89
2018-08-07 19:30 | 51.72 | 51.24
2018-08-07 20:00 | 48.35 | 47.82
2018-08-07 20:30 | 46.71 | 46.15
2018-08-07 21:00 | 44.08 | 43.47
2018-08-07 21:30 | 41.64 | 41.13
2018-08-07 22:00 | 39.69 | 39.1
2018-08-07 22:30 | 37.69 | 37.06
2018-08-07 23:00 | 39.15 | 38.56
2018-08-07 23:30 | 8.3 | 3.84
2018-08-08 | 30.75 | 30
2018-08-08 00:30 | 31.76 | 31.04
2018-08-08 01:00 | 30.11 | 29.36
2018-08-08 01:30 | 30.27 | 29.53
2018-08-08 02:00 | 29.5 | 28.71
2018-08-08 02:30 | 28.28 | 27.4
2018-08-08 03:00 | 28.46 | 27.58
2018-08-08 03:30 | 28.22 | 27.33
2018-08-08 04:00 | 28.4 | 27.52
2018-08-08 04:30 | 29.51 | 28.66
2018-08-08 05:00 | 30.63 | 29.81
2018-08-08 05:30 | 33.53 | 32.78
2018-08-08 06:00 | 36.88 | 36.18
2018-08-08 06:30 | 43.35 | 42.73
2018-08-08 07:00 | 48.53 | 47.97
2018-08-08 07:30 | 53.11 | 52.62
2018-08-08 08:00 | 52.88 | 52.38
2018-08-08 08:30 | 51.03 | 50.49
2018-08-08 09:00 | 47.61 | 46.93
2018-08-08 09:30 | 45.93 | 45.2
2018-08-08 10:00 | 45.67 | 44.8
2018-08-08 10:30 | 44.17 | 43.16
2018-08-08 11:00 | 43.48 | 42.27
2018-08-08 11:30 | 44.45 | 43.12
2018-08-08 12:00 | 43.66 | 42.21
2018-08-08 12:30 | 43.1 | 41.72
2018-08-08 13:00 | 42.38 | 41.12
2018-08-08 13:30 | 42.88 | 41.57
2018-08-08 14:00 | 43.87 | 42.51
2018-08-08 14:30 | 43.79 | 42.49
2018-08-08 15:00 | 44.76 | 43.55
2018-08-08 15:30 | 44.23 | 43.14
2018-08-08 16:00 | 45.25 | 44.38
2018-08-08 16:30 | 47.32 | 46.7
2018-08-08 17:00 | 47.84 | 47.45
2018-08-08 17:30 | 49.18 | 48.97
2018-08-08 18:00 | 49.75 | 49.62
2018-08-08 18:30 | 52.39 | 52.23
2018-08-08 19:00 | 52.88 | 52.73
2018-08-08 19:30 | 50.56 | 50.43
2018-08-08 20:00 | 48.95 | 48.86
2018-08-08 20:30 | 46.45 | 46.39
2018-08-08 21:00 | 44.51 | 44.47
2018-08-08 21:30 | 42.22 | 42.21
2018-08-08 22:00 | 39.52 | 39.51
2018-08-08 22:30 | 38.1 | 38.09
2018-08-08 23:00 | 38.56 | 38.55
2018-08-08 23:30 | 34.97 | 34.94
2018-08-09 | 32.83 | 32.77
2018-08-09 00:30 | 32.21 | 32.11
2018-08-09 01:00 | 31.59 | 31.46
2018-08-09 01:30 | 29.85 | 29.47
2018-08-09 02:00 | 31.28 | 28.27
2018-08-09 02:30 | 30.71 | 27.65
2018-08-09 03:00 | 30.34 | 27.24
2018-08-09 03:30 | 30.68 | 27.62
2018-08-09 04:00 | 31.26 | 28.26
2018-08-09 04:30 | 32.86 | 30.03
2018-08-09 05:00 | 34.96 | 32.32
2018-08-09 05:30 | 38.06 | 35.64
2018-08-09 06:00 | 40.78 | 38.51
2018-08-09 06:30 | 45.61 | 43.57
2018-08-09 07:00 | 49.86 | 47.97
2018-08-09 07:30 | 53.01 | 51.21
2018-08-09 08:00 | 52.91 | 51.08
2018-08-09 08:30 | 51.17 | 49.23
2018-08-09 09:00 | 49.35 | 47.3
2018-08-09 09:30 | 48.42 | 46.31
2018-08-09 10:00 | 46.52 | 44.31
2018-08-09 10:30 | 45.84 | 43.57
2018-08-09 11:00 | 45.7 | 43.4
2018-08-09 11:30 | 46.27 | 44.01
2018-08-09 12:00 | 46.49 | 44.32
2018-08-09 12:30 | 45.95 | 43.76
2018-08-09 13:00 | 45.52 | 43.31
2018-08-09 13:30 | 45.7 | 43.5
2018-08-09 14:00 | 45.95 | 43.76
2018-08-09 14:30 | 46.34 | 44.17
2018-08-09 15:00 | 47.38 | 45.27
2018-08-09 15:30 | 47.54 | 45.44
2018-08-09 16:00 | 48.34 | 46.3
2018-08-09 16:30 | 50.41 | 48.49
2018-08-09 17:00 | 50.48 | 48.61
2018-08-09 17:30 | 50.6 | 48.81
2018-08-09 18:00 | 52.96 | 51.29
2018-08-09 18:30 | 54.37 | 52.75
2018-08-09 19:00 | 52.47 | 50.8
2018-08-09 19:30 | 50.41 | 48.67
2018-08-09 20:00 | 50.08 | 48.31
2018-08-09 20:30 | 49.97 | 48.2
2018-08-09 21:00 | 48.19 | 46.35
2018-08-09 21:30 | 45.56 | 43.55
2018-08-09 22:00 | 43.45 | 41.32
2018-08-09 22:30 | 42.24 | 40.06
2018-08-09 23:00 | 42.26 | 39.98
2018-08-09 23:30 | 37.78 | 35.2
2018-08-10 | 34.61 | 31.78
2018-08-10 00:30 | 33.98 | 31.09
2018-08-10 01:00 | 32.67 | 29.67
2018-08-10 01:30 | 32.36 | 29.3
2018-08-10 02:00 | 32.57 | 29.56
2018-08-10 02:30 | 32.45 | 29.44
2018-08-10 03:00 | 31.39 | 28.27
2018-08-10 03:30 | 31.17 | 28.03
2018-08-10 04:00 | 31.47 | 28.36
2018-08-10 04:30 | 32.04 | 28.99
2018-08-10 05:00 | 32.59 | 29.59
2018-08-10 05:30 | 34.45 | 31.61
2018-08-10 06:00 | 37.38 | 34.77
2018-08-10 06:30 | 42.89 | 40.59
2018-08-10 07:00 | 48.37 | 46.63
2018-08-10 07:30 | 51.34 | 51.1
2018-08-10 08:00 | 50.94 | 50.63
2018-08-10 08:30 | 50.34 | 49.91
2018-08-10 09:00 | 47.94 | 47.42
2018-08-10 09:30 | 45.22 | 44.61
2018-08-10 10:00 | 43.52 | 42.81
2018-08-10 10:30 | 41.27 | 40.29
2018-08-10 11:00 | 42.53 | 41.62
2018-08-10 11:30 | 41.78 | 40.97
2018-08-10 12:00 | 41.15 | 40.96
2018-08-10 12:30 | 40.94 | 40.92
2018-08-10 13:00 | 41.04 | 41.03
2018-08-10 13:30 | 40.95 | 40.94
2018-08-10 14:00 | 40.03 | 40.03
2018-08-10 14:30 | 40.13 | 40.13
2018-08-10 15:00 | 41.43 | 41.43
2018-08-10 15:30 | 41.37 | 41.34
2018-08-10 16:00 | 42.92 | 42.88
2018-08-10 16:30 | 44.93 | 44.83
2018-08-10 17:00 | 44.32 | 44.1
2018-08-10 17:30 | 44.43 | 44.37
2018-08-10 18:00 | 46.29 | 46.25
2018-08-10 18:30 | 48.41 | 48.39
2018-08-10 19:00 | 48.77 | 48.75
2018-08-10 19:30 | 46.09 | 46.04
2018-08-10 20:00 | 44.25 | 44.16
2018-08-10 20:30 | 42.41 | 42.27
2018-08-10 21:00 | 41.36 | 41.2
2018-08-10 21:30 | 41.18 | 41.01
2018-08-10 22:00 | 39.52 | 39.52
2018-08-10 22:30 | 37.26 | 37.2
2018-08-10 23:00 | 37.24 | 37.15
2018-08-10 23:30 | 35.35 | 35.29
2018-08-11 | 33.81 | 33.77
2018-08-11 00:30 | 32.98 | 32.96
2018-08-11 01:00 | 31.56 | 31.54
2018-08-11 01:30 | 28.81 | 28.8
2018-08-11 02:00 | 27.38 | 27.37
2018-08-11 02:30 | 27.11 | 27.1
2018-08-11 03:00 | 27.54 | 27.54
2018-08-11 03:30 | 26.58 | 26.58
2018-08-11 04:00 | 26.99 | 26.99
2018-08-11 04:30 | 27.85 | 27.85
2018-08-11 05:00 | 27.59 | 27.59
2018-08-11 05:30 | 28.88 | 28.87
2018-08-11 06:00 | 30.02 | 30
2018-08-11 06:30 | 32.14 | 32.1
2018-08-11 07:00 | 33.3 | 33.24
2018-08-11 07:30 | 35.49 | 35.4
2018-08-11 08:00 | 37.17 | 37.02
2018-08-11 08:30 | 36.6 | 36.38
2018-08-11 09:00 | 37.78 | 37.48
2018-08-11 09:30 | 37.2 | 36.75
2018-08-11 10:00 | 37.07 | 36.51
2018-08-11 10:30 | 36.51 | 35.86
2018-08-11 11:00 | 34.99 | 34.21
2018-08-11 11:30 | 34.06 | 33.24
2018-08-11 12:00 | 33.76 | 32.94
2018-08-11 12:30 | 32.29 | 31.49
2018-08-11 13:00 | 31.4 | 30.66
2018-08-11 13:30 | 31.53 | 30.82
2018-08-11 14:00 | 31.83 | 31.19
2018-08-11 14:30 | 31.55 | 31.02
2018-08-11 15:00 | 31.25 | 30.79
2018-08-11 15:30 | 31.93 | 31.53
2018-08-11 16:00 | 34.47 | 34.13
2018-08-11 16:30 | 36.53 | 36.28
2018-08-11 17:00 | 37.94 | 37.72
2018-08-11 17:30 | 40.52 | 40.33
2018-08-11 18:00 | 42.85 | 42.66
2018-08-11 18:30 | 45.53 | 45.21
2018-08-11 19:00 | 44.04 | 43.74
2018-08-11 19:30 | 42.71 | 42.43
2018-08-11 20:00 | 40.6 | 40.34
2018-08-11 20:30 | 38.88 | 38.67
2018-08-11 21:00 | 38.34 | 38.16
2018-08-11 21:30 | 37.99 | 37.86
2018-08-11 22:00 | 36.04 | 35.96
2018-08-11 22:30 | 35.26 | 35.2
2018-08-11 23:00 | 36.15 | 36.11
2018-08-11 23:30 | 32.33 | 32.3
2018-08-12 | 30.15 | 30.14
2018-08-12 00:30 | 29.21 | 29.21
2018-08-12 01:00 | 29.63 | 29.63
2018-08-12 01:30 | 28.38 | 28.38
2018-08-12 02:00 | 26.98 | 26.98
2018-08-12 02:30 | 26.48 | 26.47
2018-08-12 03:00 | 26.45 | 26.45
2018-08-12 03:30 | 26.02 | 26.01
2018-08-12 04:00 | 26.5 | 26.49
2018-08-12 04:30 | 26.95 | 26.95
2018-08-12 05:00 | 27.41 | 27.41
2018-08-12 05:30 | 27.22 | 27.22
2018-08-12 06:00 | 28 | 28
2018-08-12 06:30 | 29.41 | 29.41
2018-08-12 07:00 | 30.69 | 30.69
2018-08-12 07:30 | 31.04 | 31.04
2018-08-12 08:00 | 31.62 | 31.62
2018-08-12 08:30 | 31.48 | 31.47
2018-08-12 09:00 | 32.46 | 32.43
2018-08-12 09:30 | 32.02 | 31.94
2018-08-12 10:00 | 32.32 | 32.21
2018-08-12 10:30 | 32.71 | 32.51
2018-08-12 11:00 | 31.73 | 31.44
2018-08-12 11:30 | 31.53 | 31.18
2018-08-12 12:00 | 30.77 | 30.38
2018-08-12 12:30 | 31.17 | 30.8
2018-08-12 13:00 | 30.86 | 30.46
2018-08-12 13:30 | 29.95 | 29.56
2018-08-12 14:00 | 30.56 | 30.23
2018-08-12 14:30 | 31.67 | 31.34
2018-08-12 15:00 | 31.16 | 30.86
2018-08-12 15:30 | 33.13 | 32.9
2018-08-12 16:00 | 35.91 | 35.7
2018-08-12 16:30 | 38.21 | 38.04
2018-08-12 17:00 | 38.22 | 38.05
2018-08-12 17:30 | 40.44 | 40.29
2018-08-12 18:00 | 43.9 | 43.71
2018-08-12 18:30 | 47.35 | 47.05
2018-08-12 19:00 | 47.25 | 46.95
2018-08-12 19:30 | 44.37 | 44.11
2018-08-12 20:00 | 42 | 41.79
2018-08-12 20:30 | 40.31 | 40.13
2018-08-12 21:00 | 38.31 | 38.16
2018-08-12 21:30 | 37.58 | 37.48
2018-08-12 22:00 | 35.54 | 35.47
2018-08-12 22:30 | 33.83 | 33.79
2018-08-12 23:00 | 35.35 | 35.31
2018-08-12 23:30 | 31.93 | 31.91
2018-08-13 | 29.25 | 29.24
2018-08-13 00:30 | 28.56 | 28.56
2018-08-13 01:00 | 27.89 | 27.88
2018-08-13 01:30 | 27.53 | 27.53
2018-08-13 02:00 | 26.63 | 26.63
2018-08-13 02:30 | 26.48 | 26.48
2018-08-13 03:00 | 25.9 | 25.9
2018-08-13 03:30 | 25.91 | 25.91
2018-08-13 04:00 | 25.98 | 25.98
2018-08-13 04:30 | 27.24 | 27.23
2018-08-13 05:00 | 28.33 | 28.33
2018-08-13 05:30 | 30.69 | 30.67
2018-08-13 06:00 | 33.82 | 33.76
2018-08-13 06:30 | 38.76 | 38.53
2018-08-13 07:00 | 44.34 | 43.87
2018-08-13 07:30 | 48.64 | 48.38
2018-08-13 08:00 | 49.13 | 48.74
2018-08-13 08:30 | 49.32 | 48.78
2018-08-13 09:00 | 47.17 | 46.51
2018-08-13 09:30 | 45.04 | 44.33
2018-08-13 10:00 | 43.55 | 42.75
2018-08-13 10:30 | 42.68 | 41.84
2018-08-13 11:00 | 42.04 | 40.93
2018-08-13 11:30 | 41.91 | 41.12
2018-08-13 12:00 | 41.88 | 41.83
2018-08-13 12:30 | 41.87 | 41.84
2018-08-13 13:00 | 40.06 | 40.03
2018-08-13 13:30 | 41.66 | 41.61
2018-08-13 14:00 | 42.67 | 42.6
2018-08-13 14:30 | 42.71 | 42.63
2018-08-13 15:00 | 43.59 | 43.55
2018-08-13 15:30 | 43.6 | 43.59
2018-08-13 16:00 | 45.79 | 45.79
2018-08-13 16:30 | 47.59 | 47.58
2018-08-13 17:00 | 48.81 | 48.74
2018-08-13 17:30 | 49.86 | 49.65
2018-08-13 18:00 | 53.35 | 53.14
2018-08-13 18:30 | 57.58 | 57.35
2018-08-13 19:00 | 58.93 | 58.66
2018-08-13 19:30 | 55.91 | 55.7
2018-08-13 20:00 | 53.54 | 53.35
2018-08-13 20:30 | 51.32 | 51.19
2018-08-13 21:00 | 44.87 | 44.72
2018-08-13 21:30 | 46.6 | 46.54
2018-08-13 22:00 | 44.68 | 44.44
2018-08-13 22:30 | 43.64 | 43.32
2018-08-13 23:00 | 44.19 | 43.89
2018-08-13 23:30 | 40.23 | 39.96
2018-08-14 | 37.64 | 37.4
2018-08-14 00:30 | 36.18 | 35.97
2018-08-14 01:00 | 34.1 | 33.94
2018-08-14 01:30 | 34.15 | 34
2018-08-14 02:00 | 34.24 | 34.09
2018-08-14 02:30 | 32.8 | 32.72
2018-08-14 03:00 | 32.61 | 32.54
2018-08-14 03:30 | 32.96 | 32.89
2018-08-14 04:00 | 32.2 | 32.14
2018-08-14 04:30 | 33.02 | 32.97
2018-08-14 05:00 | 35.21 | 35.15
2018-08-14 05:30 | 37.85 | 37.74
2018-08-14 06:00 | 40.77 | 40.57
2018-08-14 06:30 | 47.23 | 46.76
2018-08-14 07:00 | 53.22 | 52.94
2018-08-14 07:30 | 56.16 | 55.74
2018-08-14 08:00 | 55.65 | 55.47
2018-08-14 08:30 | 53.51 | 53.31
2018-08-14 09:00 | 49.29 | 48.98
2018-08-14 09:30 | 43.18 | 42.71
2018-08-14 10:00 | 42.74 | 42.29
2018-08-14 10:30 | 45.09 | 44.72
2018-08-14 11:00 | 43.74 | 43.3
2018-08-14 11:30 | 42.43 | 41.94
2018-08-14 12:00 | 42.24 | 41.65
2018-08-14 12:30 | 42.43 | 42.12
2018-08-14 13:00 | 42.07 | 42.02
2018-08-14 13:30 | 42.47 | 42.42
2018-08-14 14:00 | 42.54 | 42.49
2018-08-14 14:30 | 42.56 | 42.51
2018-08-14 15:00 | 40.28 | 40.2
2018-08-14 15:30 | 38 | 37.97
2018-08-14 16:00 | 42.05 | 42.05
2018-08-14 16:30 | 49.87 | 49.87
2018-08-14 17:00 | 50.29 | 50.26
2018-08-14 17:30 | 51.86 | 51.76
2018-08-14 18:00 | 54.65 | 54.54
2018-08-14 18:30 | 58.16 | 58.13
2018-08-14 19:00 | 59.38 | 59.35
2018-08-14 19:30 | 57.04 | 56.76
2018-08-14 20:00 | 54.18 | 53.96
2018-08-14 20:30 | 51.01 | 50.85
2018-08-14 21:00 | 49.64 | 49.52
2018-08-14 21:30 | 48.04 | 47.95
2018-08-14 22:00 | 45.36 | 45.06
2018-08-14 22:30 | 43.92 | 43.5
2018-08-14 23:00 | 45.51 | 45.12
2018-08-14 23:30 | 41.73 | 41.4
2018-08-15 | 38.87 | 38.57
2018-08-15 00:30 | 37.57 | 37.34
2018-08-15 01:00 | 35.67 | 35.46
2018-08-15 01:30 | 34.93 | 34.75
2018-08-15 02:00 | 33.42 | 33.28
2018-08-15 02:30 | 32.54 | 32.41
2018-08-15 03:00 | 32.22 | 32.12
2018-08-15 03:30 | 31.9 | 31.82
2018-08-15 04:00 | 31.74 | 31.66
2018-08-15 04:30 | 33.63 | 33.56
2018-08-15 05:00 | 34.12 | 34.03
2018-08-15 05:30 | 37.05 | 36.89
2018-08-15 06:00 | 40.78 | 40.46
2018-08-15 06:30 | 46.05 | 45.52
2018-08-15 07:00 | 50.64 | 50.22
2018-08-15 07:30 | 54.22 | 53.88
2018-08-15 08:00 | 53.21 | 52.7
2018-08-15 08:30 | 51.95 | 51.27
2018-08-15 09:00 | 50.53 | 49.69
2018-08-15 09:30 | 48.38 | 47.38
2018-08-15 10:00 | 46 | 45.37
2018-08-15 10:30 | 45.3 | 44.84
2018-08-15 11:00 | 45.01 | 44.89
2018-08-15 11:30 | 44.85 | 44.72
2018-08-15 12:00 | 44.63 | 44.49
2018-08-15 12:30 | 43.92 | 43.79
2018-08-15 13:00 | 43.61 | 43.47
2018-08-15 13:30 | 43.77 | 43.63
2018-08-15 14:00 | 44.31 | 44.18
2018-08-15 14:30 | 43.96 | 43.85
2018-08-15 15:00 | 45.56 | 45.48
2018-08-15 15:30 | 46.12 | 46.07
2018-08-15 16:00 | 47.61 | 47.59
2018-08-15 16:30 | 50.41 | 50.41
2018-08-15 17:00 | 50.52 | 50.51
2018-08-15 17:30 | 51.64 | 51.56
2018-08-15 18:00 | 54.57 | 54.44
2018-08-15 18:30 | 58.71 | 58.32
2018-08-15 19:00 | 59.76 | 59.34
2018-08-15 19:30 | 56.91 | 56.53
2018-08-15 20:00 | 54.07 | 53.75
2018-08-15 20:30 | 51.87 | 51.61
2018-08-15 21:00 | 50.06 | 49.84
2018-08-15 21:30 | 48.28 | 48.11
2018-08-15 22:00 | 45.44 | 45.08
2018-08-15 22:30 | 44.69 | 44.26
2018-08-15 23:00 | 45.52 | 45.1
2018-08-15 23:30 | 42.21 | 41.82
2018-08-16 | 39.28 | 38.95
2018-08-16 00:30 | 36.77 | 36.52
2018-08-16 01:00 | 35.74 | 35.49
2018-08-16 01:30 | 34.98 | 34.75
2018-08-16 02:00 | 34.24 | 34.06
2018-08-16 02:30 | 33.1 | 32.99
2018-08-16 03:00 | 32.74 | 32.63
2018-08-16 03:30 | 33.14 | 33.04
2018-08-16 04:00 | 33.21 | 33.13
2018-08-16 04:30 | 33.53 | 33.44
2018-08-16 05:00 | 34.84 | 34.72
2018-08-16 05:30 | 37.16 | 36.97
2018-08-16 06:00 | 40.26 | 39.99
2018-08-16 06:30 | 45.82 | 45.27
2018-08-16 07:00 | 49.88 | 49.28
2018-08-16 07:30 | 54.43 | 53.99
2018-08-16 08:00 | 54.11 | 53.51
2018-08-16 08:30 | 52.85 | 52.06
2018-08-16 09:00 | 51.82 | 50.86
2018-08-16 09:30 | 48.79 | 47.92
2018-08-16 10:00 | 47.8 | 46.86
2018-08-16 10:30 | 47.38 | 46.51
2018-08-16 11:00 | 48.23 | 47.69
2018-08-16 11:30 | 47.69 | 47.13
2018-08-16 12:00 | 48.31 | 48.2
2018-08-16 12:30 | 45.01 | 44.91
2018-08-16 13:00 | 44.54 | 44.42
2018-08-16 13:30 | 45.33 | 45.21
2018-08-16 14:00 | 45.25 | 45.05
2018-08-16 14:30 | 45.92 | 45.72
2018-08-16 15:00 | 45.02 | 44.86
2018-08-16 15:30 | 45.52 | 45.43
2018-08-16 16:00 | 47.48 | 47.43
2018-08-16 16:30 | 49.8 | 49.79
2018-08-16 17:00 | 48.61 | 48.6
2018-08-16 17:30 | 48.97 | 48.89
2018-08-16 18:00 | 51.15 | 51.02
2018-08-16 18:30 | 54.52 | 54.42
2018-08-16 19:00 | 53.6 | 53.5
2018-08-16 19:30 | 50.96 | 50.83
2018-08-16 20:00 | 49.74 | 49.62
2018-08-16 20:30 | 46.8 | 46.71
2018-08-16 21:00 | 44.92 | 44.86
2018-08-16 21:30 | 42.05 | 42.03
2018-08-16 22:00 | 39.91 | 39.91
2018-08-16 22:30 | 38.52 | 38.42
2018-08-16 23:00 | 39.6 | 39.42
2018-08-16 23:30 | 36.14 | 35.99
2018-08-17 | 33.31 | 33.22
2018-08-17 00:30 | 31.87 | 31.78
2018-08-17 01:00 | 30.84 | 30.77
2018-08-17 01:30 | 29.6 | 29.54
2018-08-17 02:00 | 29.04 | 29.01
2018-08-17 02:30 | 27.03 | 27.02
2018-08-17 03:00 | 27.48 | 27.47
2018-08-17 03:30 | 29.48 | 29.48
2018-08-17 04:00 | 27.85 | 27.84
2018-08-17 04:30 | 29.62 | 29.61
2018-08-17 05:00 | 31.02 | 30.99
2018-08-17 05:30 | 33.3 | 33.22
2018-08-17 06:00 | 36.39 | 36.25
2018-08-17 06:30 | 41.12 | 40.77
2018-08-17 07:00 | 45.02 | 44.87
2018-08-17 07:30 | 48.33 | 48.05
2018-08-17 08:00 | 49.66 | 49.18
2018-08-17 08:30 | 48.37 | 47.71
2018-08-17 09:00 | 47.63 | 46.76
2018-08-17 09:30 | 47.08 | 46.07
2018-08-17 10:00 | 45.3 | 44.61
2018-08-17 10:30 | 45.48 | 44.86
2018-08-17 11:00 | 46.27 | 45.47
2018-08-17 11:30 | 45.65 | 44.73
2018-08-17 12:00 | 46.47 | 45.53
2018-08-17 12:30 | 45.64 | 44.74
2018-08-17 13:00 | 45.5 | 44.62
2018-08-17 13:30 | 45.95 | 45.16
2018-08-17 14:00 | 46.97 | 46.29
2018-08-17 14:30 | 46.87 | 46.28
2018-08-17 15:00 | 46.3 | 45.78
2018-08-17 15:30 | 45.77 | 45.36
2018-08-17 16:00 | 47.31 | 47.09
2018-08-17 16:30 | 48.81 | 48.7
2018-08-17 17:00 | 49.16 | 49.1
2018-08-17 17:30 | 49.11 | 49.1
2018-08-17 18:00 | 50.24 | 50.24
2018-08-17 18:30 | 51.9 | 51.9
2018-08-17 19:00 | 52.87 | 52.87
2018-08-17 19:30 | 50.6 | 50.59
2018-08-17 20:00 | 48.01 | 47.99
2018-08-17 20:30 | 44.69 | 44.64
2018-08-17 21:00 | 43.65 | 43.62
2018-08-17 21:30 | 42.06 | 42.05
2018-08-17 22:00 | 40.78 | 40.78
2018-08-17 22:30 | 39.17 | 39.06
2018-08-17 23:00 | 39.82 | 39.65
2018-08-17 23:30 | 35.83 | 35.7
2018-08-18 | 33.56 | 33.46
2018-08-18 00:30 | 32.85 | 32.78
2018-08-18 01:00 | 31.72 | 31.67
2018-08-18 01:30 | 31.26 | 31.23
2018-08-18 02:00 | 29.75 | 29.72
2018-08-18 02:30 | 30.01 | 29.99
2018-08-18 03:00 | 29.58 | 29.56
2018-08-18 03:30 | 28.82 | 28.81
2018-08-18 04:00 | 28.86 | 28.84
2018-08-18 04:30 | 29.24 | 29.23
2018-08-18 05:00 | 29.63 | 29.61
2018-08-18 05:30 | 30.99 | 30.95
2018-08-18 06:00 | 31.97 | 31.92
2018-08-18 06:30 | 33.76 | 33.68
2018-08-18 07:00 | 35.34 | 35.26
2018-08-18 07:30 | 37.14 | 37
2018-08-18 08:00 | 38.07 | 37.86
2018-08-18 08:30 | 38.27 | 37.99
2018-08-18 09:00 | 38.95 | 38.56
2018-08-18 09:30 | 38.3 | 37.75
2018-08-18 10:00 | 38.29 | 37.64
2018-08-18 10:30 | 37.9 | 37.03
2018-08-18 11:00 | 37.73 | 36.73
2018-08-18 11:30 | 37.17 | 36.22
2018-08-18 12:00 | 35.88 | 35.63
2018-08-18 12:30 | 35.16 | 34.96
2018-08-18 13:00 | 34.25 | 34.08
2018-08-18 13:30 | 34.06 | 33.92
2018-08-18 14:00 | 34.36 | 34.24
2018-08-18 14:30 | 33.74 | 33.66
2018-08-18 15:00 | 34.26 | 34.2
2018-08-18 15:30 | 34.56 | 34.52
2018-08-18 16:00 | 36.7 | 36.67
2018-08-18 16:30 | 39.72 | 39.71
2018-08-18 17:00 | 40.3 | 40.29
2018-08-18 17:30 | 42.42 | 42.41
2018-08-18 18:00 | 44.13 | 44.12
2018-08-18 18:30 | 47.19 | 47.16
2018-08-18 19:00 | 47.44 | 47.39
2018-08-18 19:30 | 44.5 | 44.48
2018-08-18 20:00 | 43.03 | 43.02
2018-08-18 20:30 | 42.08 | 42.08
2018-08-18 21:00 | 41.12 | 41.12
2018-08-18 21:30 | 39.62 | 39.62
2018-08-18 22:00 | 37.98 | 37.98
2018-08-18 22:30 | 37.65 | 37.64
2018-08-18 23:00 | 37.75 | 37.69
2018-08-18 23:30 | 34.51 | 34.41
2018-08-19 | 32.45 | 32.39
2018-08-19 00:30 | 31.99 | 31.95
2018-08-19 01:00 | 31.41 | 31.38
2018-08-19 01:30 | 29.85 | 29.83
2018-08-19 02:00 | 29.63 | 29.61
2018-08-19 02:30 | 29.8 | 29.79
2018-08-19 03:00 | 29.6 | 29.59
2018-08-19 03:30 | 29.2 | 29.2
2018-08-19 04:00 | 28.54 | 28.54
2018-08-19 04:30 | 28.67 | 28.67
2018-08-19 05:00 | 29.66 | 29.66
2018-08-19 05:30 | 29.84 | 29.84
2018-08-19 06:00 | 29.43 | 29.42
2018-08-19 06:30 | 30.98 | 30.98
2018-08-19 07:00 | 30.87 | 30.87
2018-08-19 07:30 | 31.74 | 31.74
2018-08-19 08:00 | 32.29 | 32.27
2018-08-19 08:30 | 32.6 | 32.56
2018-08-19 09:00 | 33.83 | 33.75
2018-08-19 09:30 | 32.48 | 32.37
2018-08-19 10:00 | 32.17 | 32.01
2018-08-19 10:30 | 31.79 | 31.56
2018-08-19 11:00 | 31.56 | 31.28
2018-08-19 11:30 | 31.87 | 31.53
2018-08-19 12:00 | 30.47 | 30.09
2018-08-19 12:30 | 30.09 | 29.73
2018-08-19 13:00 | 29.76 | 29.39
2018-08-19 13:30 | 29.86 | 29.49
2018-08-19 14:00 | 30.29 | 29.91
2018-08-19 14:30 | 30.44 | 30.05
2018-08-19 15:00 | 32.21 | 31.88
2018-08-19 15:30 | 33.63 | 33.37
2018-08-19 16:00 | 34.17 | 33.93
2018-08-19 16:30 | 37.69 | 37.47
2018-08-19 17:00 | 38.53 | 38.31
2018-08-19 17:30 | 41.7 | 41.51
2018-08-19 18:00 | 44.41 | 44.18
2018-08-19 18:30 | 48.07 | 47.74
2018-08-19 19:00 | 48.36 | 48.04
2018-08-19 19:30 | 46.01 | 45.74
2018-08-19 20:00 | 44.59 | 44.35
2018-08-19 20:30 | 41.97 | 41.77
2018-08-19 21:00 | 40.21 | 40.04
2018-08-19 21:30 | 38.84 | 38.72
2018-08-19 22:00 | 37.17 | 37.08
2018-08-19 22:30 | 35.46 | 35.4
2018-08-19 23:00 | 36.2 | 36.15
2018-08-19 23:30 | 33.06 | 33.03
2018-08-20 | 32.16 | 32.15
2018-08-20 00:30 | 31.3 | 31.29
2018-08-20 01:00 | 29.82 | 29.82
2018-08-20 01:30 | 28.34 | 28.33
2018-08-20 02:00 | 28.13 | 28.13
2018-08-20 02:30 | 28.36 | 28.36
2018-08-20 03:00 | 27.37 | 27.37
2018-08-20 03:30 | 27.82 | 27.81
2018-08-20 04:00 | 29.54 | 29.54
2018-08-20 04:30 | 28.82 | 28.82
2018-08-20 05:00 | 28.65 | 28.65
2018-08-20 05:30 | 32.42 | 32.4
2018-08-20 06:00 | 34.32 | 34.26
2018-08-20 06:30 | 40.5 | 40.29
2018-08-20 07:00 | 45.04 | 44.66
2018-08-20 07:30 | 47.92 | 47.75
2018-08-20 08:00 | 48.11 | 47.77
2018-08-20 08:30 | 46.29 | 45.86
2018-08-20 09:00 | 44.99 | 44.43
2018-08-20 09:30 | 43.56 | 42.94
2018-08-20 10:00 | 41.72 | 41.04
2018-08-20 10:30 | 40.78 | 39.98
2018-08-20 11:00 | 41.64 | 40.66
2018-08-20 11:30 | 41.49 | 40.36
2018-08-20 12:00 | 41.58 | 40.35
2018-08-20 12:30 | 41.5 | 40.32
2018-08-20 13:00 | 41.38 | 40.22
2018-08-20 13:30 | 41.83 | 40.64
2018-08-20 14:00 | 42.15 | 40.81
2018-08-20 14:30 | 42.6 | 41.93
2018-08-20 15:00 | 42.62 | 42.29
2018-08-20 15:30 | 43.03 | 42.76
2018-08-20 16:00 | 44.29 | 44.13
2018-08-20 16:30 | 46.67 | 46.62
2018-08-20 17:00 | 46.9 | 46.89
2018-08-20 17:30 | 48.22 | 48.21
2018-08-20 18:00 | 51.97 | 51.96
2018-08-20 18:30 | 53.83 | 53.83
2018-08-20 19:00 | 53.87 | 53.87
2018-08-20 19:30 | 51.48 | 51.47
2018-08-20 20:00 | 49.84 | 49.82
2018-08-20 20:30 | 47.51 | 47.45
2018-08-20 21:00 | 45.72 | 45.63
2018-08-20 21:30 | 43.88 | 43.82
2018-08-20 22:00 | 41.29 | 41.29
2018-08-20 22:30 | 39.38 | 39.37
2018-08-20 23:00 | 40.34 | 40.33
2018-08-20 23:30 | 37.13 | 37.11
2018-08-21 | 34.41 | 34.35
2018-08-21 00:30 | 34.31 | 34.24
2018-08-21 01:00 | 33.27 | 33.19
2018-08-21 01:30 | 32.26 | 32.17
2018-08-21 02:00 | 32.33 | 32.21
2018-08-21 02:30 | 32.68 | 31.72
2018-08-21 03:00 | 34.07 | 31.33
2018-08-21 03:30 | 34.18 | 31.46
2018-08-21 04:00 | 33.81 | 31.06
2018-08-21 04:30 | 34.32 | 31.57
2018-08-21 05:00 | 34.54 | 31.71
2018-08-21 05:30 | 38.06 | 35.5
2018-08-21 06:00 | 41.79 | 39.45
2018-08-21 06:30 | 47.03 | 44.93
2018-08-21 07:00 | 51.99 | 50.17
2018-08-21 07:30 | 56.33 | 54.62
2018-08-21 08:00 | 56.94 | 55.21
2018-08-21 08:30 | 53.91 | 52.05
2018-08-21 09:00 | 50.84 | 48.85
2018-08-21 09:30 | 48.37 | 46.26
2018-08-21 10:00 | 46.59 | 44.39
2018-08-21 10:30 | 46.01 | 43.76
2018-08-21 11:00 | 46.34 | 44.09
2018-08-21 11:30 | 45.67 | 43.39
2018-08-21 12:00 | 45.75 | 43.46
2018-08-21 12:30 | 44.83 | 42.48
2018-08-21 13:00 | 42.97 | 40.52
2018-08-21 13:30 | 43.35 | 40.92
2018-08-21 14:00 | 43.07 | 41.34
2018-08-21 14:30 | 43.61 | 42.3
2018-08-21 15:00 | 46.08 | 44.89
2018-08-21 15:30 | 47.53 | 46.55
2018-08-21 16:00 | 49 | 48.46
2018-08-21 16:30 | 49.59 | 49.08
2018-08-21 17:00 | 49.28 | 48.79
2018-08-21 17:30 | 49.85 | 49.39
2018-08-21 18:00 | 52.44 | 52.02
2018-08-21 18:30 | 55.76 | 55.36
2018-08-21 19:00 | 55.8 | 55.41
2018-08-21 19:30 | 54.16 | 53.75
2018-08-21 20:00 | 52.25 | 51.83
2018-08-21 20:30 | 50.94 | 50.51
2018-08-21 21:00 | 49.02 | 48.58
2018-08-21 21:30 | 46.2 | 45.74
2018-08-21 22:00 | 43.32 | 42.8
2018-08-21 22:30 | 41.57 | 41.01
2018-08-21 23:00 | 41.33 | 40.77
2018-08-21 23:30 | 39.5 | 38.91
2018-08-22 | 35.84 | 35.19
2018-08-22 00:30 | 34.42 | 33.75
2018-08-22 01:00 | 33.57 | 32.89
2018-08-22 01:30 | 33.63 | 32.95
2018-08-22 02:00 | 32.05 | 31.35
2018-08-22 02:30 | 31.67 | 30.95
2018-08-22 03:00 | 31.3 | 30.57
2018-08-22 03:30 | 31.05 | 30.32
2018-08-22 04:00 | 31.23 | 30.51
2018-08-22 04:30 | 32.3 | 31.6
2018-08-22 05:00 | 34.22 | 33.56
2018-08-22 05:30 | 38.6 | 38.01
2018-08-22 06:00 | 40.1 | 39.52
2018-08-22 06:30 | 45.93 | 45.4
2018-08-22 07:00 | 51.07 | 50.58
2018-08-22 07:30 | 53.43 | 52.95
2018-08-22 08:00 | 50.23 | 49.69
2018-08-22 08:30 | 54.32 | 53.12
2018-08-22 09:00 | 53.25 | 51.72
2018-08-22 09:30 | 50.16 | 49.15
2018-08-22 10:00 | 48.53 | 47.51
2018-08-22 10:30 | 47.63 | 46.41
2018-08-22 11:00 | 45.59 | 44.2
2018-08-22 11:30 | 44.98 | 43.98
2018-08-22 12:00 | 44.33 | 43.81
2018-08-22 12:30 | 45.19 | 44.69
2018-08-22 13:00 | 42.91 | 42.37
2018-08-22 13:30 | 44.29 | 43.77
2018-08-22 14:00 | 43.28 | 42.75
2018-08-22 14:30 | 43.72 | 43.2
2018-08-22 15:00 | 44.64 | 44.12
2018-08-22 15:30 | 46.69 | 46.19
2018-08-22 16:00 | 47.55 | 47.04
2018-08-22 16:30 | 49.35 | 48.84
2018-08-22 17:00 | 48.86 | 48.38
2018-08-22 17:30 | 49.44 | 49.01
2018-08-22 18:00 | 50.93 | 50.53
2018-08-22 18:30 | 53.37 | 52.95
2018-08-22 19:00 | 53.88 | 53.46
2018-08-22 19:30 | 51.61 | 51.17
2018-08-22 20:00 | 49.7 | 49.25
2018-08-22 20:30 | 48 | 47.54
2018-08-22 21:00 | 45.68 | 45.2
2018-08-22 21:30 | 44.14 | 43.65
2018-08-22 22:00 | 42.32 | 41.77
2018-08-22 22:30 | 39.69 | 39.1
2018-08-22 23:00 | 40 | 39.41
2018-08-22 23:30 | 37.2 | 36.57
2018-08-23 | 34.79 | 34.12
2018-08-23 00:30 | 35.46 | 34.81
2018-08-23 01:00 | 34.06 | 33.38
2018-08-23 01:30 | 32.4 | 31.68
2018-08-23 02:00 | 30.69 | 29.94
2018-08-23 02:30 | 31.13 | 30.39
2018-08-23 03:00 | 30.71 | 29.97
2018-08-23 03:30 | 30.68 | 29.94
2018-08-23 04:00 | 31.34 | 30.61
2018-08-23 04:30 | 32.61 | 31.91
2018-08-23 05:00 | 33.35 | 32.66
2018-08-23 05:30 | 36.37 | 35.73
2018-08-23 06:00 | 39.39 | 38.78
2018-08-23 06:30 | 43.77 | 43.21
2018-08-23 07:00 | 49.12 | 48.6
2018-08-23 07:30 | 52.45 | 51.93
2018-08-23 08:00 | 53.07 | 52.49
2018-08-23 08:30 | 50.68 | 49.99
2018-08-23 09:00 | 48.09 | 47.2
2018-08-23 09:30 | 47.23 | 46.18
2018-08-23 10:00 | 46.3 | 45.17
2018-08-23 10:30 | 45.91 | 44.57
2018-08-23 11:00 | 45.67 | 44.97
2018-08-23 11:30 | 44.16 | 43.57
2018-08-23 12:00 | 44.5 | 43.91
2018-08-23 12:30 | 44.38 | 43.79
2018-08-23 13:00 | 44.29 | 43.7
2018-08-23 13:30 | 45.05 | 44.47
2018-08-23 14:00 | 46.08 | 45.51
2018-08-23 14:30 | 47.49 | 46.93
2018-08-23 15:00 | 48.01 | 47.43
2018-08-23 15:30 | 49.15 | 48.62
2018-08-23 16:00 | 50.43 | 49.94
2018-08-23 16:30 | 52.25 | 51.79
2018-08-23 17:00 | 51.77 | 51.34
2018-08-23 17:30 | 51.34 | 50.92
2018-08-23 18:00 | 53.52 | 53.14
2018-08-23 18:30 | 56.6 | 56.24
2018-08-23 19:00 | 56.78 | 56.42
2018-08-23 19:30 | 53.26 | 52.88
2018-08-23 20:00 | 50.75 | 50.36
2018-08-23 20:30 | 49.12 | 48.72
2018-08-23 21:00 | 47.32 | 46.9
2018-08-23 21:30 | 45.37 | 44.84
2018-08-23 22:00 | 42.31 | 41.59
2018-08-23 22:30 | 41.32 | 40.81
2018-08-23 23:00 | 42.4 | 41.9
2018-08-23 23:30 | 38.49 | 37.91
2018-08-24 | 37.11 | 36.48
2018-08-24 00:30 | 35.34 | 34.69
2018-08-24 01:00 | 33.65 | 32.96
2018-08-24 01:30 | 32.09 | 31.37
2018-08-24 02:00 | 30.99 | 30.25
2018-08-24 02:30 | 30.43 | 29.68
2018-08-24 03:00 | 30.09 | 29.33
2018-08-24 03:30 | 30.17 | 29.41
2018-08-24 04:00 | 30.84 | 30.1
2018-08-24 04:30 | 32.3 | 31.6
2018-08-24 05:00 | 33.57 | 32.89
2018-08-24 05:30 | 36.05 | 35.41
2018-08-24 06:00 | 38.58 | 37.97
2018-08-24 06:30 | 43.02 | 42.45
2018-08-24 07:00 | 46.86 | 46.33
2018-08-24 07:30 | 50.7 | 50.18
2018-08-24 08:00 | 51.16 | 50.63
2018-08-24 08:30 | 49.41 | 48.84
2018-08-24 09:00 | 47.35 | 46.62
2018-08-24 09:30 | 47.4 | 46.55
2018-08-24 10:00 | 46.58 | 45.57
2018-08-24 10:30 | 46.37 | 45.36
2018-08-24 11:00 | 45.42 | 44.81
2018-08-24 11:30 | 45.91 | 45.27
2018-08-24 12:00 | 45.21 | 44.56
2018-08-24 12:30 | 44.88 | 44.25
2018-08-24 13:00 | 45.2 | 44.58
2018-08-24 13:30 | 44.96 | 44.34
2018-08-24 14:00 | 44.62 | 43.99
2018-08-24 14:30 | 44.47 | 43.85
2018-08-24 15:00 | 44.31 | 43.7
2018-08-24 15:30 | 45.34 | 44.76
2018-08-24 16:00 | 46.45 | 45.89
2018-08-24 16:30 | 48.62 | 48.11
2018-08-24 17:00 | 48.94 | 48.45
2018-08-24 17:30 | 49.17 | 48.7
2018-08-24 18:00 | 49.61 | 49.16
2018-08-24 18:30 | 50.87 | 50.43
2018-08-24 19:00 | 50.49 | 50.05
2018-08-24 19:30 | 48.79 | 48.34
2018-08-24 20:00 | 46.7 | 46.23
2018-08-24 20:30 | 45.1 | 44.61
2018-08-24 21:00 | 43.44 | 42.94
2018-08-24 21:30 | 41.46 | 40.95
2018-08-24 22:00 | 39.77 | 39.24
2018-08-24 22:30 | 39.1 | 38.57
2018-08-24 23:00 | 39.6 | 39.02
2018-08-24 23:30 | 37.24 | 36.55
2018-08-25 | 34.95 | 34.22
2018-08-25 00:30 | 34.24 | 33.49
2018-08-25 01:00 | 32.84 | 32.06
2018-08-25 01:30 | 32.1 | 31.31
2018-08-25 02:00 | 31.51 | 30.7
2018-08-25 02:30 | 30.36 | 29.53
2018-08-25 03:00 | 30.01 | 29.16
2018-08-25 03:30 | 30.63 | 29.81
2018-08-25 04:00 | 30.11 | 29.27
2018-08-25 04:30 | 30.52 | 29.68
2018-08-25 05:00 | 30.54 | 29.71
2018-08-25 05:30 | 31.71 | 30.9
2018-08-25 06:00 | 32.71 | 31.92
2018-08-25 06:30 | 34.36 | 33.61
2018-08-25 07:00 | 35.52 | 34.79
2018-08-25 07:30 | 37.66 | 36.97
2018-08-25 08:00 | 38.49 | 37.8
2018-08-25 08:30 | 38.9 | 38.2
2018-08-25 09:00 | 40 | 39.31
2018-08-25 09:30 | 42.26 | 41.6
2018-08-25 10:00 | 42.46 | 41.8
2018-08-25 10:30 | 42.41 | 41.73
2018-08-25 11:00 | 40.31 | 39.56
2018-08-25 11:30 | 39.12 | 38.33
2018-08-25 12:00 | 36.66 | 35.81
2018-08-25 12:30 | 36.76 | 35.98
2018-08-25 13:00 | 35.94 | 35.14
2018-08-25 13:30 | 38.04 | 37.3
2018-08-25 14:00 | 30 | 28.98
2018-08-25 14:30 | 26 | 24.58
2018-08-25 15:00 | 38.03 | 37.31
2018-08-25 15:30 | 37.5 | 36.78
2018-08-25 16:00 | 37.17 | 36.44
2018-08-25 16:30 | 38.5 | 37.81
2018-08-25 17:00 | 39.19 | 38.51
2018-08-25 17:30 | 41.66 | 41.03
2018-08-25 18:00 | 44.46 | 43.87
2018-08-25 18:30 | 46.17 | 45.59
2018-08-25 19:00 | 46.35 | 45.78
2018-08-25 19:30 | 44.82 | 44.22
2018-08-25 20:00 | 43.36 | 42.75
2018-08-25 20:30 | 41.27 | 40.63
2018-08-25 21:00 | 41.61 | 40.98
2018-08-25 21:30 | 39.89 | 39.23
2018-08-25 22:00 | 38.59 | 37.92
2018-08-25 22:30 | 38.29 | 37.61
2018-08-25 23:00 | 38.73 | 38.07
2018-08-25 23:30 | 36.1 | 35.39
2018-08-26 | 33.33 | 32.56
2018-08-26 00:30 | 32.62 | 31.84
2018-08-26 01:00 | 31.41 | 30.6
2018-08-26 01:30 | 31 | 30.18
2018-08-26 02:00 | 30.09 | 29.24
2018-08-26 02:30 | 29.52 | 28.66
2018-08-26 03:00 | 29.92 | 29.08
2018-08-26 03:30 | 30.4 | 29.58
2018-08-26 04:00 | 30.22 | 29.39
2018-08-26 04:30 | 30.72 | 29.9
2018-08-26 05:00 | 30.43 | 29.61
2018-08-26 05:30 | 30.9 | 30.08
2018-08-26 06:00 | 31.21 | 30.4
2018-08-26 06:30 | 31.77 | 30.98
2018-08-26 07:00 | 32.3 | 31.53
2018-08-26 07:30 | 37.38 | 36.72
2018-08-26 08:00 | 39.06 | 38.42
2018-08-26 08:30 | 39.68 | 39.03
2018-08-26 09:00 | 41.62 | 40.99
2018-08-26 09:30 | 43.47 | 42.87
2018-08-26 10:00 | 42.36 | 41.74
2018-08-26 10:30 | 42.65 | 42.02
2018-08-26 11:00 | 40.75 | 40.08
2018-08-26 11:30 | 39.73 | 39.03
2018-08-26 12:00 | 38.6 | 37.88
2018-08-26 12:30 | 38.39 | 37.66
2018-08-26 13:00 | 35.84 | 35.05
2018-08-26 13:30 | 34.08 | 33.25
2018-08-26 14:00 | 34.45 | 33.63
2018-08-26 14:30 | 34.41 | 33.6
2018-08-26 15:00 | 35.25 | 34.46
2018-08-26 15:30 | 38.62 | 37.92
2018-08-26 16:00 | 39.86 | 39.18
2018-08-26 16:30 | 39.86 | 39.18
2018-08-26 17:00 | 41.18 | 40.54
2018-08-26 17:30 | 42.88 | 42.27
2018-08-26 18:00 | 46.45 | 45.89
2018-08-26 18:30 | 49.62 | 49.08
2018-08-26 19:00 | 48.84 | 48.29
2018-08-26 19:30 | 48.25 | 47.7
2018-08-26 20:00 | 45.71 | 45.13
2018-08-26 20:30 | 43.79 | 43.19
2018-08-26 21:00 | 42.6 | 41.98
2018-08-26 21:30 | 40.52 | 39.88
2018-08-26 22:00 | 37.67 | 36.98
2018-08-26 22:30 | 36.83 | 36.13
2018-08-26 23:00 | 37.47 | 36.79
2018-08-26 23:30 | 34.23 | 33.49
2018-08-27 | 33.85 | 33.11
2018-08-27 00:30 | 32.83 | 32.07
2018-08-27 01:00 | 30.97 | 30.16
2018-08-27 01:30 | 29.74 | 28.89
2018-08-27 02:00 | 30.02 | 29.18
2018-08-27 02:30 | 30.27 | 29.45
2018-08-27 03:00 | 28.96 | 28.11
2018-08-27 03:30 | 28.99 | 28.13
2018-08-27 04:00 | 29.13 | 28.28
2018-08-27 04:30 | 30.77 | 29.96
2018-08-27 05:00 | 31.57 | 30.78
2018-08-27 05:30 | 33.68 | 32.93
2018-08-27 06:00 | 36.57 | 35.86
2018-08-27 06:30 | 41.78 | 41.14
2018-08-27 07:00 | 45.18 | 44.57
2018-08-27 07:30 | 49.82 | 49.3
2018-08-27 08:00 | 50.21 | 49.54
2018-08-27 08:30 | 50 | 49.34
2018-08-27 09:00 | 48.19 | 47.31
2018-08-27 09:30 | 46.88 | 45.86
2018-08-27 10:00 | 45.63 | 44.5
2018-08-27 10:30 | 44.98 | 44.11
2018-08-27 11:00 | 44.95 | 44.34
2018-08-27 11:30 | 44.69 | 43.9
2018-08-27 12:00 | 45.13 | 44.36
2018-08-27 12:30 | 45.7 | 44.95
2018-08-27 13:00 | 43.89 | 43.17
2018-08-27 13:30 | 43.96 | 43.23
2018-08-27 14:00 | 44.2 | 43.46
2018-08-27 14:30 | 45.34 | 44.68
2018-08-27 15:00 | 45.57 | 44.97
2018-08-27 15:30 | 45.61 | 45.11
2018-08-27 16:00 | 47.31 | 46.95
2018-08-27 16:30 | 50.39 | 50.17
2018-08-27 17:00 | 50.36 | 50.25
2018-08-27 17:30 | 49.95 | 49.81
2018-08-27 18:00 | 51.99 | 51.78
2018-08-27 18:30 | 55.51 | 55.24
2018-08-27 19:00 | 55.22 | 54.95
2018-08-27 19:30 | 52.73 | 52.53
2018-08-27 20:00 | 51.22 | 51.08
2018-08-27 20:30 | 48.35 | 48.27
2018-08-27 21:00 | 46.17 | 46.12
2018-08-27 21:30 | 42.94 | 42.92
2018-08-27 22:00 | 41.68 | 41.58
2018-08-27 22:30 | 39.19 | 38.96
2018-08-27 23:00 | 41.88 | 41.67
2018-08-27 23:30 | 39 | 38.82
2018-08-28 | 36.26 | 36.1
2018-08-28 00:30 | 34.08 | 33.95
2018-08-28 01:00 | 32.95 | 32.84
2018-08-28 01:30 | 32.57 | 32.47
2018-08-28 02:00 | 31.01 | 30.93
2018-08-28 02:30 | 30.29 | 30.24
2018-08-28 03:00 | 30.29 | 30.26
2018-08-28 03:30 | 30.02 | 29.99
2018-08-28 04:00 | 30.46 | 30.43
2018-08-28 04:30 | 33 | 32.97
2018-08-28 05:00 | 33.68 | 33.64
2018-08-28 05:30 | 34.46 | 34.38
2018-08-28 06:00 | 38.27 | 38.13
2018-08-28 06:30 | 42.66 | 42.39
2018-08-28 07:00 | 47.13 | 46.62
2018-08-28 07:30 | 51.15 | 50.24
2018-08-28 08:00 | 51.81 | 50.55
2018-08-28 08:30 | 52.12 | 50.54
2018-08-28 09:00 | 49.76 | 47.89
2018-08-28 09:30 | 48.45 | 46.37
2018-08-28 10:00 | 47.95 | 45.65
2018-08-28 10:30 | 47.85 | 45.22
2018-08-28 11:00 | 47.9 | 46.13
2018-08-28 11:30 | 46.98 | 45.19
2018-08-28 12:00 | 46.78 | 44.94
2018-08-28 12:30 | 46.86 | 45.01
2018-08-28 13:00 | 46.52 | 44.63
2018-08-28 13:30 | 47.3 | 45.34
2018-08-28 14:00 | 47.81 | 45.88
2018-08-28 14:30 | 48.57 | 46.69
2018-08-28 15:00 | 49.09 | 47.33
2018-08-28 15:30 | 49.08 | 47.42
2018-08-28 16:00 | 49.66 | 48.38
2018-08-28 16:30 | 51.43 | 50.52
2018-08-28 17:00 | 51.08 | 50.47
2018-08-28 17:30 | 50.72 | 50.36
2018-08-28 18:00 | 53.59 | 53.28
2018-08-28 18:30 | 57.32 | 56.97
2018-08-28 19:00 | 57.58 | 57.21
2018-08-28 19:30 | 54.01 | 53.71
2018-08-28 20:00 | 51.96 | 51.73
2018-08-28 20:30 | 50.02 | 49.83
2018-08-28 21:00 | 47.5 | 47.38
2018-08-28 21:30 | 45.73 | 45.64
2018-08-28 22:00 | 43.1 | 42.83
2018-08-28 22:30 | 43.02 | 42.66
2018-08-28 23:00 | 43.76 | 43.44
2018-08-28 23:30 | 39.88 | 39.55
2018-08-29 | 37.43 | 37.16
2018-08-29 00:30 | 35.78 | 35.55
2018-08-29 01:00 | 34.12 | 33.94
2018-08-29 01:30 | 32.96 | 32.8
2018-08-29 02:00 | 32.91 | 32.78
2018-08-29 02:30 | 32.49 | 32.37
2018-08-29 03:00 | 31.72 | 31.62
2018-08-29 03:30 | 30.99 | 30.91
2018-08-29 04:00 | 31.58 | 31.47
2018-08-29 04:30 | 32.03 | 31.92
2018-08-29 05:00 | 33.7 | 33.58
2018-08-29 05:30 | 36.26 | 36.08
2018-08-29 06:00 | 39.47 | 39.2
2018-08-29 06:30 | 44.75 | 44.31
2018-08-29 07:00 | 49.77 | 49.04
2018-08-29 07:30 | 53.43 | 52.36
2018-08-29 08:00 | 53.07 | 51.68
2018-08-29 08:30 | 50.92 | 49.21
2018-08-29 09:00 | 49.69 | 47.68
2018-08-29 09:30 | 48.9 | 46.68
2018-08-29 10:00 | 47.67 | 45.27
2018-08-29 10:30 | 47.29 | 44.79
2018-08-29 11:00 | 46.59 | 44.81
2018-08-29 11:30 | 46.64 | 44.73
2018-08-29 12:00 | 46.69 | 44.74
2018-08-29 12:30 | 46.56 | 44.64
2018-08-29 13:00 | 45.3 | 44.48
2018-08-29 13:30 | 45.64 | 45.45
2018-08-29 14:00 | 45.58 | 45.38
2018-08-29 14:30 | 46.34 | 46.17
2018-08-29 15:00 | 46.91 | 46.79
2018-08-29 15:30 | 47.19 | 47.13
2018-08-29 16:00 | 47.84 | 47.8
2018-08-29 16:30 | 51.55 | 51.53
2018-08-29 17:00 | 50.97 | 50.96
2018-08-29 17:30 | 51.46 | 51.4
2018-08-29 18:00 | 53.4 | 53.28
2018-08-29 18:30 | 56.38 | 56.32
2018-08-29 19:00 | 57.2 | 57.15
2018-08-29 19:30 | 54.64 | 54.58
2018-08-29 20:00 | 52.63 | 52.53
2018-08-29 20:30 | 49.85 | 49.82
2018-08-29 21:00 | 47.25 | 47.24
2018-08-29 21:30 | 46.32 | 46.31
2018-08-29 22:00 | 43.17 | 42.92
2018-08-29 22:30 | 41.67 | 41.27
2018-08-29 23:00 | 42.99 | 42.67
2018-08-29 23:30 | 38.43 | 38.15
2018-08-30 | 36.99 | 36.75
2018-08-30 00:30 | 35.64 | 35.39
2018-08-30 01:00 | 35.21 | 35
2018-08-30 01:30 | 33.44 | 33.24
2018-08-30 02:00 | 31.92 | 31.76
2018-08-30 02:30 | 31.27 | 31.15
2018-08-30 03:00 | 31.03 | 30.93
2018-08-30 03:30 | 31.4 | 31.31
2018-08-30 04:00 | 31.03 | 30.95
2018-08-30 04:30 | 31.54 | 31.47
2018-08-30 05:00 | 33.08 | 32.97
2018-08-30 05:30 | 36.07 | 35.9
2018-08-30 06:00 | 38.4 | 38.16
2018-08-30 06:30 | 43.15 | 42.74
2018-08-30 07:00 | 47.61 | 47.26
2018-08-30 07:30 | 50.39 | 50.1
2018-08-30 08:00 | 50.48 | 50
2018-08-30 08:30 | 49.2 | 48.49
2018-08-30 09:00 | 48.92 | 47.99
2018-08-30 09:30 | 47.93 | 46.78
2018-08-30 10:00 | 46.48 | 45.24
2018-08-30 10:30 | 46.43 | 45.76
2018-08-30 11:00 | 44.65 | 44.34
2018-08-30 11:30 | 44.22 | 43.95
2018-08-30 12:00 | 43.98 | 43.71
2018-08-30 12:30 | 44.38 | 44.13
2018-08-30 13:00 | 44.17 | 43.96
2018-08-30 13:30 | 44.13 | 43.9
2018-08-30 14:00 | 44.61 | 44.33
2018-08-30 14:30 | 45.1 | 44.83
2018-08-30 15:00 | 45.77 | 45.52
2018-08-30 15:30 | 45.87 | 45.72
2018-08-30 16:00 | 47.04 | 46.96
2018-08-30 16:30 | 49.71 | 49.68
2018-08-30 17:00 | 50.18 | 50.17
2018-08-30 17:30 | 49.58 | 49.54
2018-08-30 18:00 | 50.89 | 50.78
2018-08-30 18:30 | 53.69 | 53.52
2018-08-30 19:00 | 53.88 | 53.62
2018-08-30 19:30 | 52.21 | 51.99
2018-08-30 20:00 | 48.64 | 48.49
2018-08-30 20:30 | 47.42 | 47.31
2018-08-30 21:00 | 45.17 | 45.1
2018-08-30 21:30 | 42.07 | 42.04
2018-08-30 22:00 | 40.09 | 40.09
2018-08-30 22:30 | 37.39 | 37.33
2018-08-30 23:00 | 38.37 | 38.21
2018-08-30 23:30 | 34.65 | 34.53
2018-08-31 | 32.53 | 32.42
2018-08-31 00:30 | 31.73 | 31.67
2018-08-31 01:00 | 30.21 | 30.15
2018-08-31 01:30 | 29.24 | 29.19
2018-08-31 02:00 | 28.23 | 28.19
2018-08-31 02:30 | 27.36 | 27.35
2018-08-31 03:00 | 27.26 | 27.25
2018-08-31 03:30 | 28.13 | 28.12
2018-08-31 04:00 | 28.81 | 28.8
2018-08-31 04:30 | 29.13 | 29.12
2018-08-31 05:00 | 30.7 | 30.68
2018-08-31 05:30 | 32.2 | 32.15
2018-08-31 06:00 | 34.72 | 34.58
2018-08-31 06:30 | 35.86 | 35.42
2018-08-31 07:00 | 43.89 | 43.66
2018-08-31 07:30 | 46.23 | 46.01
2018-08-31 08:00 | 47.5 | 47.12
2018-08-31 08:30 | 46.73 | 46.19
2018-08-31 09:00 | 45.84 | 45.04
2018-08-31 09:30 | 45.76 | 44.81
2018-08-31 10:00 | 46.08 | 45.71
2018-08-31 10:30 | 48 | 47.51
2018-08-31 11:00 | 46.04 | 45.41
2018-08-31 11:30 | 45.79 | 45.04
2018-08-31 12:00 | 45.46 | 44.54
2018-08-31 12:30 | 46.19 | 45.3
2018-08-31 13:00 | 46.65 | 45.74
2018-08-31 13:30 | 46.42 | 45.53
2018-08-31 14:00 | 45.34 | 44.49
2018-08-31 14:30 | 44.89 | 44.15
2018-08-31 15:00 | 45.12 | 44.45
2018-08-31 15:30 | 45.48 | 44.94
2018-08-31 16:00 | 48.13 | 47.76
2018-08-31 16:30 | 49.02 | 48.81
2018-08-31 17:00 | 47.67 | 47.57
2018-08-31 17:30 | 47.93 | 47.91
2018-08-31 18:00 | 47.87 | 47.87
2018-08-31 18:30 | 50.42 | 50.42
2018-08-31 19:00 | 50.3 | 50.3
2018-08-31 19:30 | 48.14 | 48.01
2018-08-31 20:00 | 46.59 | 46.46
2018-08-31 20:30 | 44.61 | 44.51
2018-08-31 21:00 | 42.06 | 42
2018-08-31 21:30 | 40.34 | 40.32
2018-08-31 22:00 | 38.34 | 38.34
2018-08-31 22:30 | 37.96 | 37.96
2018-08-31 23:00 | 37.92 | 37.85
2018-08-31 23:30 | 34.49 | 34.35
2018-09-01 | 33.29 | 33.18
2018-09-01 00:30 | 31.75 | 31.69
2018-09-01 01:00 | 30.16 | 30.09
2018-09-01 01:30 | 29.71 | 29.67
2018-09-01 02:00 | 28.97 | 28.94
2018-09-01 02:30 | 28.06 | 28.04
2018-09-01 03:00 | 27.95 | 27.93
2018-09-01 03:30 | 27.94 | 27.92
2018-09-01 04:00 | 27.37 | 27.36
2018-09-01 04:30 | 28.47 | 28.46
2018-09-01 05:00 | 29.01 | 28.99
2018-09-01 05:30 | 30.03 | 29.99
2018-09-01 06:00 | 31.45 | 31.4
2018-09-01 06:30 | 32.81 | 32.74
2018-09-01 07:00 | 33.85 | 33.75
2018-09-01 07:30 | 35.42 | 35.23
2018-09-01 08:00 | 37.92 | 37.6
2018-09-01 08:30 | 39.06 | 38.58
2018-09-01 09:00 | 38.81 | 38.18
2018-09-01 09:30 | 39.95 | 39.11
2018-09-01 10:00 | 38.34 | 37.34
2018-09-01 10:30 | 38 | 37.22
2018-09-01 11:00 | 37.69 | 37.24
2018-09-01 11:30 | 37.74 | 37.25
2018-09-01 12:00 | 38.27 | 37.75
2018-09-01 12:30 | 36.7 | 36.26
2018-09-01 13:00 | 36.24 | 35.8
2018-09-01 13:30 | 36.21 | 35.79
2018-09-01 14:00 | 36.54 | 36.19
2018-09-01 14:30 | 36.97 | 36.7
2018-09-01 15:00 | 36.7 | 36.5
2018-09-01 15:30 | 37.46 | 37.31
2018-09-01 16:00 | 38.56 | 38.45
2018-09-01 16:30 | 41.32 | 41.24
2018-09-01 17:00 | 41.85 | 41.78
2018-09-01 17:30 | 43.38 | 43.33
2018-09-01 18:00 | 45.88 | 45.83
2018-09-01 18:30 | 47.37 | 47.29
2018-09-01 19:00 | 47.05 | 46.97
2018-09-01 19:30 | 45.1 | 45.06
2018-09-01 20:00 | 43.24 | 43.21
2018-09-01 20:30 | 41.86 | 41.84
2018-09-01 21:00 | 40.82 | 40.81
2018-09-01 21:30 | 39.15 | 39.15
2018-09-01 22:00 | 37.82 | 37.81
2018-09-01 22:30 | 36.56 | 36.54
2018-09-01 23:00 | 37.08 | 37.05
2018-09-01 23:30 | 33.77 | 33.71
2018-09-02 | 32.11 | 32.07
2018-09-02 00:30 | 31.62 | 31.59
2018-09-02 01:00 | 30.28 | 30.25
2018-09-02 01:30 | 29.37 | 29.31
2018-09-02 02:00 | 31.72 | 28.58
2018-09-02 02:30 | 31.47 | 28.3
2018-09-02 03:00 | 31.1 | 27.87
2018-09-02 03:30 | 30.56 | 27.27
2018-09-02 04:00 | 31.01 | 27.78
2018-09-02 04:30 | 32.16 | 29.07
2018-09-02 05:00 | 31.42 | 28.23
2018-09-02 05:30 | 32.68 | 29.63
2018-09-02 06:00 | 32.81 | 29.79
2018-09-02 06:30 | 33.9 | 30.99
2018-09-02 07:00 | 33.91 | 31
2018-09-02 07:30 | 34.24 | 31.35
2018-09-02 08:00 | 34.93 | 32.09
2018-09-02 08:30 | 35.29 | 32.46
2018-09-02 09:00 | 35.36 | 32.52
2018-09-02 09:30 | 35.02 | 32.12
2018-09-02 10:00 | 34.63 | 31.66
2018-09-02 10:30 | 35.06 | 32.1
2018-09-02 11:00 | 34.71 | 31.71
2018-09-02 11:30 | 34.71 | 31.68
2018-09-02 12:00 | 34.42 | 31.36
2018-09-02 12:30 | 34.81 | 31.78
2018-09-02 13:00 | 34.99 | 32.07
2018-09-02 13:30 | 34.59 | 31.68
2018-09-02 14:00 | 35.09 | 32.22
2018-09-02 14:30 | 34.8 | 31.93
2018-09-02 15:00 | 35.57 | 32.78
2018-09-02 15:30 | 36.56 | 33.87
2018-09-02 16:00 | 38.35 | 35.82
2018-09-02 16:30 | 41.2 | 38.88
2018-09-02 17:00 | 41.41 | 39.12
2018-09-02 17:30 | 43.12 | 40.94
2018-09-02 18:00 | 45.77 | 43.73
2018-09-02 18:30 | 48.12 | 46.19
2018-09-02 19:00 | 48.59 | 46.69
2018-09-02 19:30 | 46.84 | 44.84
2018-09-02 20:00 | 45.7 | 43.66
2018-09-02 20:30 | 44.02 | 41.9
2018-09-02 21:00 | 42.36 | 40.15
2018-09-02 21:30 | 39.93 | 37.58
2018-09-02 22:00 | 38.55 | 36.08
2018-09-02 22:30 | 37.06 | 34.41
2018-09-02 23:00 | 37.93 | 35.34
2018-09-02 23:30 | 34.82 | 31.97
2018-09-03 | 33.71 | 30.77
2018-09-03 00:30 | 33.28 | 30.33
2018-09-03 01:00 | 32.04 | 28.92
2018-09-03 01:30 | 30.72 | 27.46
2018-09-03 02:00 | 31.18 | 27.97
2018-09-03 02:30 | 31.06 | 27.85
2018-09-03 03:00 | 30.53 | 27.25
2018-09-03 03:30 | 30.48 | 27.19
2018-09-03 04:00 | 31.29 | 28.1
2018-09-03 04:30 | 31.85 | 28.73
2018-09-03 05:00 | 32.25 | 29.16
2018-09-03 05:30 | 34.37 | 31.47
2018-09-03 06:00 | 38.28 | 35.67
2018-09-03 06:30 | 41.11 | 38.66
2018-09-03 07:00 | 44.56 | 42.27
2018-09-03 07:30 | 48.22 | 46.15
2018-09-03 08:00 | 49.07 | 47.02
2018-09-03 08:30 | 48.98 | 46.91
2018-09-03 09:00 | 47.84 | 45.67
2018-09-03 09:30 | 47.38 | 45.23
2018-09-03 10:00 | 47.37 | 45.24
2018-09-03 10:30 | 47.68 | 45.65
2018-09-03 11:00 | 47.79 | 45.76
2018-09-03 11:30 | 48.16 | 46.09
2018-09-03 12:00 | 48.31 | 46.26
2018-09-03 12:30 | 48.73 | 46.7
2018-09-03 13:00 | 48.07 | 46.01
2018-09-03 13:30 | 49.05 | 47.04
2018-09-03 14:00 | 49.67 | 47.67
2018-09-03 14:30 | 50.2 | 48.23
2018-09-03 15:00 | 50.99 | 49.07
2018-09-03 15:30 | 52.41 | 50.59
2018-09-03 16:00 | 52.98 | 51.21
2018-09-03 16:30 | 54.67 | 52.97
2018-09-03 17:00 | 54.23 | 52.53
2018-09-03 17:30 | 54.76 | 53.13
2018-09-03 18:00 | 54.14 | 52.51
2018-09-03 18:30 | 55.92 | 54.37
2018-09-03 19:00 | 56.33 | 54.79
2018-09-03 19:30 | 53.77 | 52.15
2018-09-03 20:00 | 51.5 | 49.81
2018-09-03 20:30 | 50.3 | 48.56
2018-09-03 21:00 | 48.38 | 46.57
2018-09-03 21:30 | 46.14 | 44.25
2018-09-03 22:00 | 43.73 | 41.73
2018-09-03 22:30 | 41.72 | 39.42
2018-09-03 23:00 | 47.68 | 40.02
2018-09-03 23:30 | 44.55 | 36.12
2018-09-04 | 42.75 | 33.87
2018-09-04 00:30 | 42.28 | 33.26
2018-09-04 01:00 | 41.36 | 32.05
2018-09-04 01:30 | 40.85 | 31.34
2018-09-04 02:00 | 40.5 | 30.76
2018-09-04 02:30 | 40.16 | 30.25
2018-09-04 03:00 | 39.6 | 29.52
2018-09-04 03:30 | 39.53 | 29.42
2018-09-04 04:00 | 39.46 | 29.32
2018-09-04 04:30 | 39.98 | 30
2018-09-04 05:00 | 40.57 | 30.8
2018-09-04 05:30 | 42.41 | 33.24
2018-09-04 06:00 | 44.67 | 36.11
2018-09-04 06:30 | 48.47 | 40.72
2018-09-04 07:00 | 46.05 | 43.84
2018-09-04 07:30 | 49.4 | 47.48
2018-09-04 08:00 | 50.71 | 48.8
2018-09-04 08:30 | 51.21 | 49.28
2018-09-04 09:00 | 51.16 | 49.28
2018-09-04 09:30 | 51.28 | 49.4
2018-09-04 10:00 | 51.05 | 49.15
2018-09-04 10:30 | 52.44 | 50.57
2018-09-04 11:00 | 52.47 | 50.58
2018-09-04 11:30 | 52.18 | 51.17
2018-09-04 12:00 | 53.83 | 53.16
2018-09-04 12:30 | 53.13 | 52.54
2018-09-04 13:00 | 50.42 | 49.81
2018-09-04 13:30 | 51.05 | 50.4
2018-09-04 14:00 | 53.33 | 52.72
2018-09-04 14:30 | 53.33 | 52.77
2018-09-04 15:00 | 52.54 | 52.01
2018-09-04 15:30 | 55.73 | 55.25
2018-09-04 16:00 | 55.37 | 54.9
2018-09-04 16:30 | 55.63 | 55.19
2018-09-04 17:00 | 54.44 | 54.01
2018-09-04 17:30 | 54.17 | 52.67
2018-09-04 18:00 | 57.42 | 53.88
2018-09-04 18:30 | 58.57 | 55.13
2018-09-04 19:00 | 57.36 | 53.86
2018-09-04 19:30 | 53.91 | 50.32
2018-09-04 20:00 | 51.47 | 47.68
2018-09-04 20:30 | 48.81 | 44.76
2018-09-04 21:00 | 47.56 | 43.38
2018-09-04 21:30 | 46.62 | 42.33
2018-09-04 22:00 | 44.64 | 40.16
2018-09-04 22:30 | 43.27 | 38.55
2018-09-04 23:00 | 43.66 | 38.97
2018-09-04 23:30 | 39.83 | 34.56
2018-09-05 | 38.12 | 32.57
2018-09-05 00:30 | 38.25 | 32.69
2018-09-05 01:00 | 37.36 | 31.64
2018-09-05 01:30 | 36.44 | 30.53
2018-09-05 02:00 | 35.43 | 29.28
2018-09-05 02:30 | 34.73 | 28.31
2018-09-05 03:00 | 34.68 | 28.26
2018-09-05 03:30 | 34.98 | 28.63
2018-09-05 04:00 | 35.11 | 28.78
2018-09-05 04:30 | 35.66 | 29.46
2018-09-05 05:00 | 36.27 | 30.2
2018-09-05 05:30 | 38.82 | 33.19
2018-09-05 06:00 | 41.89 | 36.72
2018-09-05 06:30 | 45.23 | 40.48
2018-09-05 07:00 | 48.97 | 44.73
2018-09-05 07:30 | 53.8 | 49.95
2018-09-05 08:00 | 55.74 | 52.01
2018-09-05 08:30 | 55.11 | 52.79
2018-09-05 09:00 | 55.05 | 53.28
2018-09-05 09:30 | 54.93 | 53.21
2018-09-05 10:00 | 54.43 | 52.7
2018-09-05 10:30 | 53.8 | 52.05
2018-09-05 11:00 | 55.41 | 53.7
2018-09-05 11:30 | 54.84 | 53.1
2018-09-05 12:00 | 53.85 | 52.06
2018-09-05 12:30 | 51.55 | 49.67
2018-09-05 13:00 | 50.46 | 48.55
2018-09-05 13:30 | 49.81 | 47.86
2018-09-05 14:00 | 50.85 | 48.94
2018-09-05 14:30 | 51.2 | 49.3
2018-09-05 15:00 | 52.1 | 50.25
2018-09-05 15:30 | 51.82 | 49.96
2018-09-05 16:00 | 52.33 | 50.52
2018-09-05 16:30 | 53.36 | 51.62
2018-09-05 17:00 | 53.39 | 51.69
2018-09-05 17:30 | 52.02 | 50.32
2018-09-05 18:00 | 52.92 | 51.27
2018-09-05 18:30 | 54.39 | 52.81
2018-09-05 19:00 | 54.43 | 52.86
2018-09-05 19:30 | 51.99 | 50.33
2018-09-05 20:00 | 49.73 | 47.99
2018-09-05 20:30 | 46.71 | 44.85
2018-09-05 21:00 | 44.97 | 43.04
2018-09-05 21:30 | 43.08 | 40.99
2018-09-05 22:00 | 41.33 | 39.02
2018-09-05 22:30 | 40.26 | 37.89
2018-09-05 23:00 | 40.86 | 38.43
2018-09-05 23:30 | 37.39 | 34.69
2018-09-06 | 34.92 | 32.01
2018-09-06 00:30 | 33.9 | 30.91
2018-09-06 01:00 | 32.91 | 29.82
2018-09-06 01:30 | 32.3 | 29.13
2018-09-06 02:00 | 31.8 | 28.58
2018-09-06 02:30 | 23.02 | 18.12
2018-09-06 03:00 | 31.04 | 27.72
2018-09-06 03:30 | 30.68 | 27.31
2018-09-06 04:00 | 30.57 | 27.21
2018-09-06 04:30 | 31.58 | 28.37
2018-09-06 05:00 | 32.47 | 29.32
2018-09-06 05:30 | 34.8 | 31.88
2018-09-06 06:00 | 37.95 | 35.25
2018-09-06 06:30 | 41.87 | 39.43
2018-09-06 07:00 | 46.35 | 44.17
2018-09-06 07:30 | 51.59 | 49.69
2018-09-06 08:00 | 54.32 | 52.53
2018-09-06 08:30 | 54.87 | 53.08
2018-09-06 09:00 | 55.25 | 53.53
2018-09-06 09:30 | 53.8 | 52.02
2018-09-06 10:00 | 52.77 | 50.93
2018-09-06 10:30 | 52.6 | 50.73
2018-09-06 11:00 | 52.59 | 50.71
2018-09-06 11:30 | 51.2 | 49.25
2018-09-06 12:00 | 51.04 | 49.08
2018-09-06 12:30 | 51.13 | 49.18
2018-09-06 13:00 | 47.79 | 45.68
2018-09-06 13:30 | 51.57 | 49.63
2018-09-06 14:00 | 52.41 | 50.52
2018-09-06 14:30 | 53.41 | 51.55
2018-09-06 15:00 | 54.38 | 52.56
2018-09-06 15:30 | 54.57 | 52.78
2018-09-06 16:00 | 55.61 | 53.88
2018-09-06 16:30 | 57.28 | 55.64
2018-09-06 17:00 | 56.8 | 55.17
2018-09-06 17:30 | 55.46 | 53.84
2018-09-06 18:00 | 56.09 | 54.53
2018-09-06 18:30 | 57.82 | 56.32
2018-09-06 19:00 | 57.62 | 56.1
2018-09-06 19:30 | 56.55 | 54.96
2018-09-06 20:00 | 53.78 | 52.11
2018-09-06 20:30 | 51.86 | 50.14
2018-09-06 21:00 | 50.04 | 48.29
2018-09-06 21:30 | 47.69 | 45.87
2018-09-06 22:00 | 45.67 | 43.77
2018-09-06 22:30 | 42.09 | 39.96
2018-09-06 23:00 | 42.4 | 40.26
2018-09-06 23:30 | 38.66 | 36.29
2018-09-07 | 36.81 | 34.29
2018-09-07 00:30 | 36.69 | 34.18
2018-09-07 01:00 | 35.96 | 33.4
2018-09-07 01:30 | 31.55 | 30.96
2018-09-07 02:00 | 31.01 | 30.28
2018-09-07 02:30 | 30.59 | 29.72
2018-09-07 03:00 | 30.34 | 29.47
2018-09-07 03:30 | 29.74 | 28.85
2018-09-07 04:00 | 30.03 | 29.12
2018-09-07 04:30 | 30.22 | 29.39
2018-09-07 05:00 | 31.37 | 30.62
2018-09-07 05:30 | 34.1 | 33.62
2018-09-07 06:00 | 36.27 | 35.96
2018-09-07 06:30 | 40.37 | 40.27
2018-09-07 07:00 | 46.69 | 46.68
2018-09-07 07:30 | 51.43 | 50.42
2018-09-07 08:00 | 51.77 | 50.17
2018-09-07 08:30 | 51.42 | 49.86
2018-09-07 09:00 | 53.16 | 51.64
2018-09-07 09:30 | 52.06 | 50.47
2018-09-07 10:00 | 50.74 | 49.13
2018-09-07 10:30 | 50.4 | 48.81
2018-09-07 11:00 | 51.17 | 49.64
2018-09-07 11:30 | 53.08 | 51.62
2018-09-07 12:00 | 53.27 | 51.82
2018-09-07 12:30 | 52.57 | 51.1
2018-09-07 13:00 | 51.47 | 49.96
2018-09-07 13:30 | 50.81 | 49.27
2018-09-07 14:00 | 51.51 | 49.99
2018-09-07 14:30 | 50.7 | 49.14
2018-09-07 15:00 | 51.48 | 49.94
2018-09-07 15:30 | 51.87 | 50.29
2018-09-07 16:00 | 52.68 | 51.1
2018-09-07 16:30 | 55.11 | 53.58
2018-09-07 17:00 | 54.19 | 52.58
2018-09-07 17:30 | 52.49 | 50.75
2018-09-07 18:00 | 52.4 | 50.6
2018-09-07 18:30 | 53.05 | 51.28
2018-09-07 19:00 | 53.36 | 51.6
2018-09-07 19:30 | 51.6 | 49.75
2018-09-07 20:00 | 50.25 | 48.34
2018-09-07 20:30 | 47.99 | 45.93
2018-09-07 21:00 | 46.75 | 44.61
2018-09-07 21:30 | 45.05 | 42.79
2018-09-07 22:00 | 43.53 | 41.13
2018-09-07 22:30 | 42.41 | 39.92
2018-09-07 23:00 | 43.29 | 41.01
2018-09-07 23:30 | 39.03 | 36.44
2018-09-08 | 36.83 | 34.02
2018-09-08 00:30 | 36.17 | 33.26
2018-09-08 01:00 | 32.34 | 30.78
2018-09-08 01:30 | 30.58 | 29.97
2018-09-08 02:00 | 29.62 | 29.49
2018-09-08 02:30 | 28.94 | 28.85
2018-09-08 03:00 | 29.37 | 29.34
2018-09-08 03:30 | 28.72 | 28.71
2018-09-08 04:00 | 28.58 | 28.56
2018-09-08 04:30 | 29.3 | 29.27
2018-09-08 05:00 | 29.34 | 29.29
2018-09-08 05:30 | 31.42 | 31.33
2018-09-08 06:00 | 32.1 | 32
2018-09-08 06:30 | 34.19 | 34.06
2018-09-08 07:00 | 35.63 | 35.44
2018-09-08 07:30 | 37.58 | 37.04
2018-09-08 08:00 | 40.23 | 38.19
2018-09-08 08:30 | 41.47 | 39.55
2018-09-08 09:00 | 43.72 | 41.96
2018-09-08 09:30 | 44.65 | 42.03
2018-09-08 10:00 | 49.23 | 41.67
2018-09-08 10:30 | 49.15 | 41.44
2018-09-08 11:00 | 49.49 | 41.59
2018-09-08 11:30 | 47.8 | 39.56
2018-09-08 12:00 | 46.91 | 38.41
2018-09-08 12:30 | 46.58 | 37.97
2018-09-08 13:00 | 45.06 | 36.02
2018-09-08 13:30 | 44.53 | 35.31
2018-09-08 14:00 | 45.26 | 36.2
2018-09-08 14:30 | 45.23 | 36.07
2018-09-08 15:00 | 45.67 | 36.59
2018-09-08 15:30 | 46.39 | 37.46
2018-09-08 16:00 | 47.46 | 38.78
2018-09-08 16:30 | 49.13 | 40.81
2018-09-08 17:00 | 49.59 | 41.34
2018-09-08 17:30 | 51.2 | 43.29
2018-09-08 18:00 | 52.81 | 45.26
2018-09-08 18:30 | 53.59 | 46.26
2018-09-08 19:00 | 54.08 | 46.84
2018-09-08 19:30 | 52.73 | 45.18
2018-09-08 20:00 | 51.8 | 44.01
2018-09-08 20:30 | 50.8 | 42.75
2018-09-08 21:00 | 49.66 | 41.32
2018-09-08 21:30 | 48.69 | 40.1
2018-09-08 22:00 | 47.61 | 38.67
2018-09-08 22:30 | 47.37 | 38.32
2018-09-08 23:00 | 47.45 | 38.55
2018-09-08 23:30 | 44.41 | 34.93
2018-09-09 | 43.22 | 33.36
2018-09-09 00:30 | 42.87 | 32.93
2018-09-09 01:00 | 42.07 | 31.61
2018-09-09 01:30 | 41.54 | 30.96
2018-09-09 02:00 | 41.04 | 30.33
2018-09-09 02:30 | 40.89 | 30.06
2018-09-09 03:00 | 41.09 | 30.37
2018-09-09 03:30 | 40.59 | 29.68
2018-09-09 04:00 | 40.45 | 29.42
2018-09-09 04:30 | 40.76 | 29.91
2018-09-09 05:00 | 40.65 | 29.73
2018-09-09 05:30 | 41.33 | 30.71
2018-09-09 06:00 | 41.57 | 31.01
2018-09-09 06:30 | 42.36 | 32.04
2018-09-09 07:00 | 43.26 | 33.31
2018-09-09 07:30 | 43.44 | 33.65
2018-09-09 08:00 | 43.32 | 33.52
2018-09-09 08:30 | 44.21 | 34.83
2018-09-09 09:00 | 44.25 | 35.03
2018-09-09 09:30 | 44.75 | 35.78
2018-09-09 10:00 | 45.46 | 36.78
2018-09-09 10:30 | 46.14 | 37.67
2018-09-09 11:00 | 45.5 | 36.92
2018-09-09 11:30 | 44.75 | 35.97
2018-09-09 12:00 | 45.03 | 35.86
2018-09-09 12:30 | 44.75 | 35.49
2018-09-09 13:00 | 43.7 | 34.13
2018-09-09 13:30 | 43.61 | 34.02
2018-09-09 14:00 | 44.02 | 34.54
2018-09-09 14:30 | 38.31 | 26.93
2018-09-09 15:00 | 45.6 | 36.43
2018-09-09 15:30 | 46.6 | 37.62
2018-09-09 16:00 | 47.37 | 38.53
2018-09-09 16:30 | 48.99 | 40.54
2018-09-09 17:00 | 49.69 | 41.42
2018-09-09 17:30 | 51.37 | 43.5
2018-09-09 18:00 | 53.07 | 45.56
2018-09-09 18:30 | 49.37 | 47.7
2018-09-09 19:00 | 48.92 | 48.5
2018-09-09 19:30 | 47.12 | 46.68
2018-09-09 20:00 | 44.41 | 43.93
2018-09-09 20:30 | 41.55 | 41.02
2018-09-09 21:00 | 39.98 | 39.42
2018-09-09 21:30 | 38.76 | 38.17
2018-09-09 22:00 | 36.63 | 35.96
2018-09-09 22:30 | 35.56 | 34.83
2018-09-09 23:00 | 36.1 | 35.38
2018-09-09 23:30 | 33.21 | 32.43
2018-09-10 | 30.68 | 29.85
2018-09-10 00:30 | 31.14 | 30.33
2018-09-10 01:00 | 30.54 | 29.7
2018-09-10 01:30 | 28.56 | 27.67
2018-09-10 02:00 | 28.61 | 27.71
2018-09-10 02:30 | 28.35 | 27.44
2018-09-10 03:00 | 28.08 | 27.18
2018-09-10 03:30 | 28.42 | 27.52
2018-09-10 04:00 | 28.12 | 27.22
2018-09-10 04:30 | 29.4 | 28.53
2018-09-10 05:00 | 30.38 | 29.53
2018-09-10 05:30 | 33.25 | 32.46
2018-09-10 06:00 | 36.45 | 35.72
2018-09-10 06:30 | 41.32 | 40.65
2018-09-10 07:00 | 44.47 | 43.79
2018-09-10 07:30 | 47.76 | 47.18
2018-09-10 08:00 | 48.1 | 47.51
2018-09-10 08:30 | 46.28 | 45.67
2018-09-10 09:00 | 44.23 | 43.53
2018-09-10 09:30 | 46.6 | 45.68
2018-09-10 10:00 | 46.16 | 44.3
2018-09-10 10:30 | 46.58 | 44.79
2018-09-10 11:00 | 47.13 | 45.39
2018-09-10 11:30 | 46.6 | 44.85
2018-09-10 12:00 | 45.93 | 44.16
2018-09-10 12:30 | 46 | 44.22
2018-09-10 13:00 | 45.58 | 43.77
2018-09-10 13:30 | 46.52 | 44.75
2018-09-10 14:00 | 46.76 | 45.01
2018-09-10 14:30 | 46.39 | 44.61
2018-09-10 15:00 | 46.72 | 44.95
2018-09-10 15:30 | 49.79 | 48.11
2018-09-10 16:00 | 49.91 | 48.21
2018-09-10 16:30 | 51.7 | 50.02
2018-09-10 17:00 | 51.45 | 49.72
2018-09-10 17:30 | 50.87 | 49.03
2018-09-10 18:00 | 51.69 | 49.85
2018-09-10 18:30 | 53.15 | 51.36
2018-09-10 19:00 | 53.65 | 51.87
2018-09-10 19:30 | 51.2 | 49.3
2018-09-10 20:00 | 48.44 | 46.39
2018-09-10 20:30 | 47.24 | 45.09
2018-09-10 21:00 | 44.63 | 42.32
2018-09-10 21:30 | 42.95 | 40.58
2018-09-10 22:00 | 40.48 | 38.03
2018-09-10 22:30 | 38.38 | 35.93
2018-09-10 23:00 | 39.13 | 36.73
2018-09-10 23:30 | 36.42 | 33.8
2018-09-11 | 34.02 | 31.16
2018-09-11 00:30 | 33.39 | 30.43
2018-09-11 01:00 | 32.54 | 29.51
2018-09-11 01:30 | 31.43 | 28.23
2018-09-11 02:00 | 30.98 | 27.7
2018-09-11 02:30 | 30.06 | 26.86
2018-09-11 03:00 | 29.69 | 26.46
2018-09-11 03:30 | 29.63 | 26.39
2018-09-11 04:00 | 30.21 | 27.04
2018-09-11 04:30 | 30.94 | 27.88
2018-09-11 05:00 | 32.37 | 29.48
2018-09-11 05:30 | 34.41 | 31.78
2018-09-11 06:00 | 37.15 | 34.79
2018-09-11 06:30 | 40.85 | 38.79
2018-09-11 07:00 | 44.13 | 42.31
2018-09-11 07:30 | 48.73 | 46.96
2018-09-11 08:00 | 49.99 | 48.29
2018-09-11 08:30 | 51.01 | 49.41
2018-09-11 09:00 | 51.04 | 49.49
2018-09-11 09:30 | 50.81 | 49.14
2018-09-11 10:00 | 48.97 | 47.24
2018-09-11 10:30 | 49.17 | 47.47
2018-09-11 11:00 | 49.66 | 48.02
2018-09-11 11:30 | 50.81 | 49.22
2018-09-11 12:00 | 55.63 | 54.17
2018-09-11 12:30 | 54.54 | 53.05
2018-09-11 13:00 | 55.05 | 53.56
2018-09-11 13:30 | 55.51 | 54.03
2018-09-11 14:00 | 51.98 | 50.4
2018-09-11 14:30 | 50.32 | 48.68
2018-09-11 15:00 | 51.73 | 50.13
2018-09-11 15:30 | 50.67 | 49
2018-09-11 16:00 | 51.68 | 50.02
2018-09-11 16:30 | 52.75 | 51.09
2018-09-11 17:00 | 51.8 | 50.05
2018-09-11 17:30 | 51.46 | 49.63
2018-09-11 18:00 | 52.06 | 50.22
2018-09-11 18:30 | 54.67 | 52.94
2018-09-11 19:00 | 53.53 | 51.75
2018-09-11 19:30 | 51.71 | 49.83
2018-09-11 20:00 | 49.66 | 47.69
2018-09-11 20:30 | 47.31 | 45.19
2018-09-11 21:00 | 45.8 | 43.57
2018-09-11 21:30 | 43.65 | 41.34
2018-09-11 22:00 | 41.82 | 39.49
2018-09-11 22:30 | 39.79 | 37.31
2018-09-11 23:00 | 39.44 | 37.1
2018-09-11 23:30 | 36.76 | 34.19
2018-09-12 | 34.98 | 32.24
2018-09-12 00:30 | 35.49 | 32.78
2018-09-12 01:00 | 33.57 | 30.64
2018-09-12 01:30 | 31.81 | 28.68
2018-09-12 02:00 | 31.04 | 27.79
2018-09-12 02:30 | 32.61 | 29.51
2018-09-12 03:00 | 31.35 | 28.31
2018-09-12 03:30 | 31.05 | 28.01
2018-09-12 04:00 | 30.94 | 27.9
2018-09-12 04:30 | 31.69 | 28.76
2018-09-12 05:00 | 32.9 | 30.11
2018-09-12 05:30 | 35.38 | 32.86
2018-09-12 06:00 | 38.16 | 35.9
2018-09-12 06:30 | 41.9 | 39.93
2018-09-12 07:00 | 46.01 | 44.29
2018-09-12 07:30 | 50.67 | 49.07
2018-09-12 08:00 | 51.23 | 49.64
2018-09-12 08:30 | 50.94 | 49.4
2018-09-12 09:00 | 51.97 | 50.43
2018-09-12 09:30 | 52.43 | 50.88
2018-09-12 10:00 | 53.83 | 52.32
2018-09-12 10:30 | 52.2 | 50.65
2018-09-12 11:00 | 50.22 | 48.63
2018-09-12 11:30 | 50.23 | 48.67
2018-09-12 12:00 | 49.19 | 47.58
2018-09-12 12:30 | 48.45 | 46.8
2018-09-12 13:00 | 47.89 | 46.22
2018-09-12 13:30 | 48.64 | 46.99
2018-09-12 14:00 | 49.74 | 48.11
2018-09-12 14:30 | 50.36 | 48.76
2018-09-12 15:00 | 51.39 | 49.8
2018-09-12 15:30 | 51.61 | 50
2018-09-12 16:00 | 51.35 | 49.69
2018-09-12 16:30 | 52.39 | 50.72
2018-09-12 17:00 | 51.34 | 49.57
2018-09-12 17:30 | 50.77 | 48.89
2018-09-12 18:00 | 51.21 | 49.3
2018-09-12 18:30 | 53.46 | 51.64
2018-09-12 19:00 | 54.8 | 53.03
2018-09-12 19:30 | 51.73 | 49.83
2018-09-12 20:00 | 49.61 | 47.59
2018-09-12 20:30 | 47.72 | 45.58
2018-09-12 21:00 | 45.38 | 43.09
2018-09-12 21:30 | 43.58 | 41.15
2018-09-12 22:00 | 40.96 | 38.98
2018-09-12 22:30 | 38.62 | 37.65
2018-09-12 23:00 | 38.99 | 38.58
2018-09-12 23:30 | 35.79 | 35.31
2018-09-13 | 32.95 | 32.35
2018-09-13 00:30 | 32.08 | 31.4
2018-09-13 01:00 | 30.35 | 30.05
2018-09-13 01:30 | 28.96 | 28.8
2018-09-13 02:00 | 28.28 | 28.09
2018-09-13 02:30 | 27.76 | 27.54
2018-09-13 03:00 | 27.33 | 27.3
2018-09-13 03:30 | 26.71 | 26.7
2018-09-13 04:00 | 27.33 | 27.33
2018-09-13 04:30 | 28.05 | 28.04
2018-09-13 05:00 | 29.5 | 29.48
2018-09-13 05:30 | 33.01 | 32.94
2018-09-13 06:00 | 34.88 | 34.75
2018-09-13 06:30 | 39.08 | 38.8
2018-09-13 07:00 | 43.04 | 42.81
2018-09-13 07:30 | 46.98 | 46.63
2018-09-13 08:00 | 48.18 | 47.52
2018-09-13 08:30 | 48.68 | 48.24
2018-09-13 09:00 | 49.74 | 49.26
2018-09-13 09:30 | 49.18 | 48.8
2018-09-13 10:00 | 47.98 | 47.6
2018-09-13 10:30 | 46.73 | 46.34
2018-09-13 11:00 | 47.25 | 46.85
2018-09-13 11:30 | 48.66 | 47.59
2018-09-13 12:00 | 48.74 | 47.14
2018-09-13 12:30 | 48.95 | 47.33
2018-09-13 13:00 | 49.2 | 47.58
2018-09-13 13:30 | 49.67 | 48.08
2018-09-13 14:00 | 49.56 | 47.96
2018-09-13 14:30 | 49.72 | 48.11
2018-09-13 15:00 | 49.89 | 48.26
2018-09-13 15:30 | 50.79 | 49.14
2018-09-13 16:00 | 52.92 | 51.31
2018-09-13 16:30 | 52.59 | 50.93
2018-09-13 17:00 | 51.98 | 50.24
2018-09-13 17:30 | 52.1 | 50.27
2018-09-13 18:00 | 53.26 | 51.43
2018-09-13 18:30 | 54.42 | 52.64
2018-09-13 19:00 | 54.13 | 52.33
2018-09-13 19:30 | 52.64 | 50.75
2018-09-13 20:00 | 50.92 | 48.94
2018-09-13 20:30 | 48.8 | 46.7
2018-09-13 21:00 | 47.09 | 44.87
2018-09-13 21:30 | 44.17 | 41.73
2018-09-13 22:00 | 40.18 | 38.78
2018-09-13 22:30 | 37.35 | 37.03
2018-09-13 23:00 | 39.35 | 37.48
2018-09-13 23:30 | 36.51 | 33.79
2018-09-14 | 34.59 | 31.67
2018-09-14 00:30 | 33.99 | 30.99
2018-09-14 01:00 | 33.34 | 30.23
2018-09-14 01:30 | 32.51 | 29.37
2018-09-14 02:00 | 31.07 | 27.94
2018-09-14 02:30 | 30.16 | 27.06
2018-09-14 03:00 | 29.61 | 26.54
2018-09-14 03:30 | 30.01 | 26.98
2018-09-14 04:00 | 29.88 | 26.85
2018-09-14 04:30 | 30.44 | 27.46
2018-09-14 05:00 | 31.48 | 28.64
2018-09-14 05:30 | 33.76 | 31.19
2018-09-14 06:00 | 36.68 | 34.38
2018-09-14 06:30 | 45.94 | 38.14
2018-09-14 07:00 | 49.74 | 42.04
2018-09-14 07:30 | 52.85 | 45.08
2018-09-14 08:00 | 56.76 | 45.95
2018-09-14 08:30 | 55.66 | 44.78
2018-09-14 09:00 | 56.53 | 45.6
2018-09-14 09:30 | 56.79 | 45.47
2018-09-14 10:00 | 56.24 | 44.79
2018-09-14 10:30 | 56.11 | 44.71
2018-09-14 11:00 | 56.18 | 44.89
2018-09-14 11:30 | 55.96 | 44.68
2018-09-14 12:00 | 56.12 | 44.84
2018-09-14 12:30 | 56.1 | 44.78
2018-09-14 13:00 | 55.71 | 44.26
2018-09-14 13:30 | 55.83 | 44.4
2018-09-14 14:00 | 56.16 | 44.78
2018-09-14 14:30 | 55.93 | 44.38
2018-09-14 15:00 | 56.27 | 44.73
2018-09-14 15:30 | 56.73 | 45.2
2018-09-14 16:00 | 57.76 | 46.43
2018-09-14 16:30 | 58.98 | 47.81
2018-09-14 17:00 | 58.74 | 47.28
2018-09-14 17:30 | 58.43 | 46.68
2018-09-14 18:00 | 58.05 | 46.08
2018-09-14 18:30 | 58.53 | 46.69
2018-09-14 19:00 | 58.79 | 47.09
2018-09-14 19:30 | 57.63 | 45.49
2018-09-14 20:00 | 56.22 | 43.55
2018-09-14 20:30 | 51.07 | 41.43
2018-09-14 21:00 | 45.13 | 39.88
2018-09-14 21:30 | 44.01 | 38.55
2018-09-14 22:00 | 42.37 | 36.83
2018-09-14 22:30 | 41.39 | 35.83
2018-09-14 23:00 | 41.25 | 36.06
2018-09-14 23:30 | 38.12 | 32.58
2018-09-15 | 36.69 | 30.84
2018-09-15 00:30 | 35.94 | 29.96
2018-09-15 01:00 | 34.74 | 28.4
2018-09-15 01:30 | 34.32 | 27.85
2018-09-15 02:00 | 33.89 | 27.26
2018-09-15 02:30 | 33.66 | 26.93
2018-09-15 03:00 | 33.4 | 26.58
2018-09-15 03:30 | 33.45 | 26.62
2018-09-15 04:00 | 33.45 | 26.62
2018-09-15 04:30 | 33.67 | 26.91
2018-09-15 05:00 | 33.93 | 27.26
2018-09-15 05:30 | 34.92 | 28.55
2018-09-15 06:00 | 35.59 | 29.38
2018-09-15 06:30 | 36.64 | 30.68
2018-09-15 07:00 | 37.67 | 31.97
2018-09-15 07:30 | 38.71 | 33.32
2018-09-15 08:00 | 39.18 | 33.93
2018-09-15 08:30 | 40.13 | 35.12
2018-09-15 09:00 | 41.08 | 36.33
2018-09-15 09:30 | 45.1 | 37.52
2018-09-15 10:00 | 44.89 | 36.59
2018-09-15 10:30 | 44.53 | 36.07
2018-09-15 11:00 | 44.37 | 35.52
2018-09-15 11:30 | 43.91 | 34.92
2018-09-15 12:00 | 43.36 | 34.19
2018-09-15 12:30 | 42.73 | 33.31
2018-09-15 13:00 | 42.1 | 32.42
2018-09-15 13:30 | 41.91 | 32.09
2018-09-15 14:00 | 41.92 | 32.08
2018-09-15 14:30 | 42.22 | 32.44
2018-09-15 15:00 | 42.56 | 32.85
2018-09-15 15:30 | 43.2 | 33.69
2018-09-15 16:00 | 44.31 | 35.05
2018-09-15 16:30 | 46.06 | 37.25
2018-09-15 17:00 | 46.32 | 37.56
2018-09-15 17:30 | 47.68 | 39.26
2018-09-15 18:00 | 48.97 | 40.91
2018-09-15 18:30 | 50.38 | 42.69
2018-09-15 19:00 | 50.51 | 42.87
2018-09-15 19:30 | 49.36 | 41.43
2018-09-15 20:00 | 48.18 | 39.9
2018-09-15 20:30 | 46.76 | 38.05
2018-09-15 21:00 | 45.84 | 36.85
2018-09-15 21:30 | 44.93 | 35.64
2018-09-15 22:00 | 44.24 | 34.67
2018-09-15 22:30 | 42.96 | 33.45
2018-09-15 23:00 | 43.3 | 33.92
2018-09-15 23:30 | 41.3 | 31.2
2018-09-16 | 40.17 | 29.59
2018-09-16 00:30 | 39.65 | 28.79
2018-09-16 01:00 | 38.9 | 27.68
2018-09-16 01:30 | 38.59 | 27.17
2018-09-16 02:00 | 38.33 | 26.69
2018-09-16 02:30 | 37.92 | 26.13
2018-09-16 03:00 | 37.95 | 26.08
2018-09-16 03:30 | 37.85 | 25.91
2018-09-16 04:00 | 37.91 | 25.98
2018-09-16 04:30 | 38.07 | 26.21
2018-09-16 05:00 | 38.08 | 26.2
2018-09-16 05:30 | 38.39 | 26.66
2018-09-16 06:00 | 38.68 | 27.04
2018-09-16 06:30 | 39.04 | 27.52
2018-09-16 07:00 | 39.24 | 27.87
2018-09-16 07:30 | 39.66 | 28.56
2018-09-16 08:00 | 39.83 | 28.92
2018-09-16 08:30 | 39.73 | 28.88
2018-09-16 09:00 | 40.36 | 29.94
2018-09-16 09:30 | 40.7 | 30.54
2018-09-16 10:00 | 40.79 | 30.77
2018-09-16 10:30 | 40.47 | 30.38
2018-09-16 11:00 | 40.44 | 30.44
2018-09-16 11:30 | 40.49 | 30.58
2018-09-16 12:00 | 40.6 | 30.77
2018-09-16 12:30 | 40.83 | 31.08
2018-09-16 13:00 | 40.74 | 30.99
2018-09-16 13:30 | 40.69 | 30.9
2018-09-16 14:00 | 40.81 | 31.05
2018-09-16 14:30 | 40.67 | 30.81
2018-09-16 15:00 | 41.31 | 31.67
2018-09-16 15:30 | 42.03 | 32.54
2018-09-16 16:00 | 43.37 | 34.28
2018-09-16 16:30 | 45.41 | 36.86
2018-09-16 17:00 | 45.88 | 37.48
2018-09-16 17:30 | 47.32 | 39.29
2018-09-16 18:00 | 49.48 | 41.97
2018-09-16 18:30 | 56.01 | 44.66
2018-09-16 19:00 | 60.42 | 44.85
2018-09-16 19:30 | 59.16 | 42.88
2018-09-16 20:00 | 57.91 | 40.92
2018-09-16 20:30 | 56.91 | 39.24
2018-09-16 21:00 | 55.96 | 37.75
2018-09-16 21:30 | 55.13 | 36.28
2018-09-16 22:00 | 54.45 | 34.78
2018-09-16 22:30 | 53.74 | 33.45
2018-09-16 23:00 | 54.17 | 34.1
2018-09-16 23:30 | 52.38 | 30.83
2018-09-17 | 45.7 | 28.92
2018-09-17 00:30 | 39.38 | 28.38
2018-09-17 01:00 | 38.87 | 27.48
2018-09-17 01:30 | 38.81 | 27.32
2018-09-17 02:00 | 38.73 | 27.21
2018-09-17 02:30 | 38.51 | 26.85
2018-09-17 03:00 | 38.56 | 26.94
2018-09-17 03:30 | 38.63 | 27.04
2018-09-17 04:00 | 38.81 | 27.28
2018-09-17 04:30 | 39.02 | 27.65
2018-09-17 05:00 | 39.75 | 28.79
2018-09-17 05:30 | 41.28 | 31.08
2018-09-17 06:00 | 42.87 | 33.31
2018-09-17 06:30 | 45.4 | 36.76
2018-09-17 07:00 | 48.87 | 41.27
2018-09-17 07:30 | 52.61 | 45.39
2018-09-17 08:00 | 53.76 | 46.6
2018-09-17 08:30 | 53.67 | 46.69
2018-09-17 09:00 | 53.67 | 46.65
2018-09-17 09:30 | 53.05 | 45.76
2018-09-17 10:00 | 52.97 | 45.66
2018-09-17 10:30 | 53.19 | 45.98
2018-09-17 11:00 | 52.77 | 45.57
2018-09-17 11:30 | 52.86 | 45.75
2018-09-17 12:00 | 53.08 | 46.05
2018-09-17 12:30 | 53.49 | 46.51
2018-09-17 13:00 | 53.06 | 45.97
2018-09-17 13:30 | 53.17 | 46.1
2018-09-17 14:00 | 53.58 | 46.6
2018-09-17 14:30 | 54.35 | 47.49
2018-09-17 15:00 | 55.02 | 48.26
2018-09-17 15:30 | 55.82 | 49.12
2018-09-17 16:00 | 57.12 | 50.54
2018-09-17 16:30 | 58.58 | 52.12
2018-09-17 17:00 | 58.26 | 51.66
2018-09-17 17:30 | 57.25 | 50.33
2018-09-17 18:00 | 57.9 | 51.02
2018-09-17 18:30 | 59.2 | 52.55
2018-09-17 19:00 | 59.16 | 52.47
2018-09-17 19:30 | 57.14 | 50.04
2018-09-17 20:00 | 55.12 | 47.62
2018-09-17 20:30 | 53.4 | 45.51
2018-09-17 21:00 | 51.75 | 43.53
2018-09-17 21:30 | 50.23 | 41.59
2018-09-17 22:00 | 48.95 | 39.92
2018-09-17 22:30 | 47.09 | 38.14
2018-09-17 23:00 | 40.77 | 38.24
2018-09-17 23:30 | 37.69 | 35.03
2018-09-18 | 35.61 | 32.82
2018-09-18 00:30 | 35.25 | 32.43
2018-09-18 01:00 | 34.4 | 31.49
2018-09-18 01:30 | 33.51 | 30.48
2018-09-18 02:00 | 32.72 | 29.58
2018-09-18 02:30 | 31.96 | 28.85
2018-09-18 03:00 | 31.41 | 28.61
2018-09-18 03:30 | 31.32 | 28.51
2018-09-18 04:00 | 31.4 | 28.58
2018-09-18 04:30 | 32.14 | 29.42
2018-09-18 05:00 | 33.21 | 30.6
2018-09-18 05:30 | 35.31 | 32.94
2018-09-18 06:00 | 38.21 | 36.1
2018-09-18 06:30 | 45.72 | 40.66
2018-09-18 07:00 | 51.95 | 44.83
2018-09-18 07:30 | 55.28 | 48.54
2018-09-18 08:00 | 57.02 | 50.61
2018-09-18 08:30 | 58.65 | 52.3
2018-09-18 09:00 | 58.45 | 52.2
2018-09-18 09:30 | 57.96 | 51.66
2018-09-18 10:00 | 57.29 | 50.93
2018-09-18 10:30 | 56.87 | 50.5
2018-09-18 11:00 | 56.56 | 50.2
2018-09-18 11:30 | 56.41 | 50.09
2018-09-18 12:00 | 56.39 | 50.14
2018-09-18 12:30 | 56.82 | 50.62
2018-09-18 13:00 | 56.72 | 50.49
2018-09-18 13:30 | 57.4 | 51.29
2018-09-18 14:00 | 56.92 | 50.74
2018-09-18 14:30 | 57.31 | 51.16
2018-09-18 15:00 | 57.89 | 51.79
2018-09-18 15:30 | 58.36 | 52.24
2018-09-18 16:00 | 59.35 | 53.32
2018-09-18 16:30 | 59.87 | 53.71
2018-09-18 17:00 | 58.97 | 52.55
2018-09-18 17:30 | 58.07 | 51.38
2018-09-18 18:00 | 57.12 | 50.31
2018-09-18 18:30 | 57.86 | 51.26
2018-09-18 19:00 | 58.35 | 51.83
2018-09-18 19:30 | 56.69 | 49.86
2018-09-18 20:00 | 54.8 | 47.6
2018-09-18 20:30 | 52.62 | 44.88
2018-09-18 21:00 | 50.98 | 42.83
2018-09-18 21:30 | 50.04 | 41.67
2018-09-18 22:00 | 48.82 | 40.06
2018-09-18 22:30 | 47.64 | 38.41
2018-09-18 23:00 | 46.94 | 37.91
2018-09-18 23:30 | 44.56 | 34.83
2018-09-19 | 42.9 | 32.55
2018-09-19 00:30 | 42.51 | 32.12
2018-09-19 01:00 | 41.96 | 31.24
2018-09-19 01:30 | 41.48 | 30.54
2018-09-19 02:00 | 40.86 | 29.56
2018-09-19 02:30 | 40.07 | 28.48
2018-09-19 03:00 | 39.66 | 28.37
2018-09-19 03:30 | 39.76 | 28.52
2018-09-19 04:00 | 39.31 | 28.23
2018-09-19 04:30 | 40.01 | 29.58
2018-09-19 05:00 | 41.21 | 31.3
2018-09-19 05:30 | 42.24 | 32.78
2018-09-19 06:00 | 44.41 | 35.68
2018-09-19 06:30 | 47.55 | 39.82
2018-09-19 07:00 | 50.74 | 43.51
2018-09-19 07:30 | 54.3 | 47.73
2018-09-19 08:00 | 55 | 48.38
2018-09-19 08:30 | 56.36 | 50.04
2018-09-19 09:00 | 56.7 | 50.33
2018-09-19 09:30 | 56.64 | 50.32
2018-09-19 10:00 | 55.6 | 49.12
2018-09-19 10:30 | 55.56 | 49.13
2018-09-19 11:00 | 55.77 | 49.46
2018-09-19 11:30 | 58.08 | 49.71
2018-09-19 12:00 | 59.77 | 49.89
2018-09-19 12:30 | 59.87 | 49.94
2018-09-19 13:00 | 59.61 | 49.57
2018-09-19 13:30 | 60.1 | 50.18
2018-09-19 14:00 | 60.41 | 50.59
2018-09-19 14:30 | 61.19 | 51.62
2018-09-19 15:00 | 61.65 | 52.15
2018-09-19 15:30 | 61.99 | 52.41
2018-09-19 16:00 | 62.63 | 53.05
2018-09-19 16:30 | 64.12 | 54.7
2018-09-19 17:00 | 63.46 | 53.72
2018-09-19 17:30 | 62.84 | 52.71
2018-09-19 18:00 | 62.01 | 51.44
2018-09-19 18:30 | 63.13 | 52.85
2018-09-19 19:00 | 63.23 | 52.97
2018-09-19 19:30 | 61.66 | 50.98
2018-09-19 20:00 | 60.18 | 48.99
2018-09-19 20:30 | 58.11 | 46.2
2018-09-19 21:00 | 56.91 | 44.54
2018-09-19 21:30 | 53.63 | 42.64
2018-09-19 22:00 | 49.71 | 40.84
2018-09-19 22:30 | 48.18 | 39.17
2018-09-19 23:00 | 48.28 | 39.44
2018-09-19 23:30 | 45.56 | 35.89
2018-09-20 | 44.09 | 33.89
2018-09-20 00:30 | 43.41 | 32.89
2018-09-20 01:00 | 42.55 | 31.7
2018-09-20 01:30 | 34.2 | 30.88
2018-09-20 02:00 | 33.13 | 30.02
2018-09-20 02:30 | 32.5 | 29.29
2018-09-20 03:00 | 32.66 | 29.48
2018-09-20 03:30 | 32.64 | 29.45
2018-09-20 04:00 | 32.58 | 29.37
2018-09-20 04:30 | 33.3 | 30.18
2018-09-20 05:00 | 34.38 | 31.39
2018-09-20 05:30 | 36.69 | 33.97
2018-09-20 06:00 | 38.45 | 35.91
2018-09-20 06:30 | 42.25 | 40.04
2018-09-20 07:00 | 45.59 | 43.65
2018-09-20 07:30 | 49.26 | 47
2018-09-20 08:00 | 55.24 | 48.51
2018-09-20 08:30 | 55.62 | 49.11
2018-09-20 09:00 | 55.52 | 48.95
2018-09-20 09:30 | 55.98 | 49.42
2018-09-20 10:00 | 55.84 | 49.34
2018-09-20 10:30 | 55.83 | 49.38
2018-09-20 11:00 | 59.49 | 50.06
2018-09-20 11:30 | 60.09 | 50.16
2018-09-20 12:00 | 60.53 | 50.75
2018-09-20 12:30 | 64.99 | 51.74
2018-09-20 13:00 | 64.93 | 50.78
2018-09-20 13:30 | 65.08 | 50.97
2018-09-20 14:00 | 65.68 | 51.75
2018-09-20 14:30 | 66.08 | 52.28
2018-09-20 15:00 | 66.38 | 52.65
2018-09-20 15:30 | 66.73 | 53.03
2018-09-20 16:00 | 67.44 | 53.9
2018-09-20 16:30 | 68.46 | 54.99
2018-09-20 17:00 | 67.9 | 53.99
2018-09-20 17:30 | 67.37 | 52.96
2018-09-20 18:00 | 67.75 | 53.23
2018-09-20 18:30 | 68.51 | 54.31
2018-09-20 19:00 | 68.54 | 54.46
2018-09-20 19:30 | 67.42 | 52.9
2018-09-20 20:00 | 65.68 | 50.44
2018-09-20 20:30 | 64.37 | 48.47
2018-09-20 21:00 | 63.41 | 46.95
2018-09-20 21:30 | 55.93 | 43.79
2018-09-20 22:00 | 50.01 | 41.39
2018-09-20 22:30 | 48.86 | 39.96
2018-09-20 23:00 | 48.96 | 40.48
2018-09-20 23:30 | 46.33 | 37.12
2018-09-21 | 44.83 | 35.13
2018-09-21 00:30 | 44.08 | 34.15
2018-09-21 01:00 | 43.58 | 33.28
2018-09-21 01:30 | 42.85 | 32.24
2018-09-21 02:00 | 42.41 | 31.59
2018-09-21 02:30 | 42.04 | 31.03
2018-09-21 03:00 | 41.89 | 30.77
2018-09-21 03:30 | 41.86 | 30.73
2018-09-21 04:00 | 41.97 | 30.86
2018-09-21 04:30 | 42.25 | 31.3
2018-09-21 05:00 | 42.7 | 31.93
2018-09-21 05:30 | 44.21 | 34.08
2018-09-21 06:00 | 45.43 | 35.76
2018-09-21 06:30 | 47.34 | 38.36
2018-09-21 07:00 | 49.4 | 41.11
2018-09-21 07:30 | 51.84 | 44.23
2018-09-21 08:00 | 53.47 | 46.37
2018-09-21 08:30 | 53.43 | 46.48
2018-09-21 09:00 | 52.78 | 45.77
2018-09-21 09:30 | 52.85 | 45.56
2018-09-21 10:00 | 51.73 | 44.24
2018-09-21 10:30 | 51.64 | 44.22
2018-09-21 11:00 | 51.44 | 44.03
2018-09-21 11:30 | 51.05 | 43.61
2018-09-21 12:00 | 50.93 | 43.5
2018-09-21 12:30 | 50.97 | 43.51
2018-09-21 13:00 | 50.67 | 43.12
2018-09-21 13:30 | 50.61 | 43.01
2018-09-21 14:00 | 50.46 | 42.79
2018-09-21 14:30 | 50.7 | 43.02
2018-09-21 15:00 | 50.98 | 43.3
2018-09-21 15:30 | 51.54 | 43.86
2018-09-21 16:00 | 52.7 | 45.17
2018-09-21 16:30 | 54.2 | 46.88
2018-09-21 17:00 | 54.17 | 46.76
2018-09-21 17:30 | 54.22 | 46.66
2018-09-21 18:00 | 54.56 | 46.99
2018-09-21 18:30 | 55.66 | 48.35
2018-09-21 19:00 | 55.95 | 48.75
2018-09-21 19:30 | 54.79 | 47.35
2018-09-21 20:00 | 53.22 | 45.44
2018-09-21 20:30 | 51.64 | 43.47
2018-09-21 21:00 | 50.57 | 42.11
2018-09-21 21:30 | 49.12 | 40.21
2018-09-21 22:00 | 47.86 | 38.51
2018-09-21 22:30 | 47.01 | 37.47
2018-09-21 23:00 | 47 | 37.77
2018-09-21 23:30 | 44.68 | 34.71
2018-09-22 | 43.03 | 32.76
2018-09-22 00:30 | 42.28 | 31.92
2018-09-22 01:00 | 41.3 | 30.51
2018-09-22 01:30 | 40.96 | 30.03
2018-09-22 02:00 | 40.3 | 29.33
2018-09-22 02:30 | 39.67 | 28.81
2018-09-22 03:00 | 39.77 | 28.98
2018-09-22 03:30 | 39.71 | 28.93
2018-09-22 04:00 | 39.68 | 28.85
2018-09-22 04:30 | 39.56 | 28.74
2018-09-22 05:00 | 40.34 | 29.84
2018-09-22 05:30 | 40.74 | 30.44
2018-09-22 06:00 | 41.22 | 31.15
2018-09-22 06:30 | 41.27 | 31.28
2018-09-22 07:00 | 41.96 | 32.29
2018-09-22 07:30 | 43.38 | 34.24
2018-09-22 08:00 | 45.31 | 36.78
2018-09-22 08:30 | 48.52 | 40.81
2018-09-22 09:00 | 49.14 | 41.62
2018-09-22 09:30 | 48.28 | 40.67
2018-09-22 10:00 | 46.59 | 38.33
2018-09-22 10:30 | 48.96 | 35.98
2018-09-22 11:00 | 48.6 | 35.5
2018-09-22 11:30 | 48.03 | 34.68
2018-09-22 12:00 | 48.05 | 34.1
2018-09-22 12:30 | 48.06 | 33.83
2018-09-22 13:00 | 47.88 | 33.46
2018-09-22 13:30 | 47.57 | 32.89
2018-09-22 14:00 | 45.11 | 33.46
2018-09-22 14:30 | 39 | 33.42
2018-09-22 15:00 | 39.75 | 34.29
2018-09-22 15:30 | 40.57 | 35.22
2018-09-22 16:00 | 41.97 | 36.8
2018-09-22 16:30 | 44.61 | 39.81
2018-09-22 17:00 | 44.8 | 40.01
2018-09-22 17:30 | 46.67 | 42.13
2018-09-22 18:00 | 48.98 | 44.78
2018-09-22 18:30 | 54.08 | 46.83
2018-09-22 19:00 | 58.51 | 48.01
2018-09-22 19:30 | 57.23 | 46.31
2018-09-22 20:00 | 56.15 | 44.86
2018-09-22 20:30 | 55.11 | 43.51
2018-09-22 21:00 | 55 | 43.41
2018-09-22 21:30 | 54.1 | 42.17
2018-09-22 22:00 | 53.13 | 40.68
2018-09-22 22:30 | 52.66 | 40.02
2018-09-22 23:00 | 52.89 | 40.64
2018-09-22 23:30 | 50.3 | 37.34
2018-09-23 | 49.15 | 35.63
2018-09-23 00:30 | 48.58 | 34.9
2018-09-23 01:00 | 47.79 | 33.5
2018-09-23 01:30 | 47.34 | 32.77
2018-09-23 02:00 | 47.21 | 32.59
2018-09-23 02:30 | 46.84 | 32
2018-09-23 03:00 | 46.46 | 31.31
2018-09-23 03:30 | 46.29 | 31.04
2018-09-23 04:00 | 46.48 | 31.31
2018-09-23 04:30 | 46.55 | 31.42
2018-09-23 05:00 | 46.74 | 31.77
2018-09-23 05:30 | 46.97 | 32.2
2018-09-23 06:00 | 47.12 | 32.4
2018-09-23 06:30 | 47.76 | 33.28
2018-09-23 07:00 | 48.26 | 34.06
2018-09-23 07:30 | 48.29 | 34.12
2018-09-23 08:00 | 48.37 | 34.38
2018-09-23 08:30 | 48.62 | 34.22
2018-09-23 09:00 | 48.48 | 34.04
2018-09-23 09:30 | 48.44 | 34.02
2018-09-23 10:00 | 48.21 | 33.78
2018-09-23 10:30 | 47.81 | 33.29
2018-09-23 11:00 | 47.84 | 33.37
2018-09-23 11:30 | 47.51 | 32.91
2018-09-23 12:00 | 47.53 | 33
2018-09-23 12:30 | 47.94 | 33.56
2018-09-23 13:00 | 47.32 | 32.66
2018-09-23 13:30 | 47.33 | 32.62
2018-09-23 14:00 | 47.2 | 32.44
2018-09-23 14:30 | 47.05 | 32.15
2018-09-23 15:00 | 47.98 | 33.54
2018-09-23 15:30 | 48.95 | 34.93
2018-09-23 16:00 | 50.31 | 36.89
2018-09-23 16:30 | 51.76 | 38.87
2018-09-23 17:00 | 52.38 | 39.68
2018-09-23 17:30 | 54.3 | 42.33
2018-09-23 18:00 | 56.6 | 45.43
2018-09-23 18:30 | 58.89 | 48.6
2018-09-23 19:00 | 59.79 | 49.85
2018-09-23 19:30 | 58.98 | 48.77
2018-09-23 20:00 | 57.46 | 46.71
2018-09-23 20:30 | 56.15 | 44.92
2018-09-23 21:00 | 55.18 | 43.64
2018-09-23 21:30 | 54.3 | 42.48
2018-09-23 22:00 | 53.4 | 41.21
2018-09-23 22:30 | 52.82 | 40.27
2018-09-23 23:00 | 53.23 | 40.73
2018-09-23 23:30 | 50.78 | 37.09
2018-09-24 | 49.7 | 35.5
2018-09-24 00:30 | 49.3 | 34.83
2018-09-24 01:00 | 41.02 | 33.38
2018-09-24 01:30 | 38.38 | 32.68
2018-09-24 02:00 | 38.01 | 32.21
2018-09-24 02:30 | 37.67 | 31.8
2018-09-24 03:00 | 37.53 | 31.61
2018-09-24 03:30 | 37.58 | 31.67
2018-09-24 04:00 | 37.56 | 31.63
2018-09-24 04:30 | 38.21 | 32.48
2018-09-24 05:00 | 39.24 | 33.73
2018-09-24 05:30 | 41.71 | 36.69
2018-09-24 06:00 | 43.38 | 38.64
2018-09-24 06:30 | 46.94 | 42.69
2018-09-24 07:00 | 49.69 | 45.64
2018-09-24 07:30 | 51.44 | 47.7
2018-09-24 08:00 | 53.1 | 49.51
2018-09-24 08:30 | 54.49 | 51
2018-09-24 09:00 | 55.53 | 52.03
2018-09-24 09:30 | 55.44 | 51.91
2018-09-24 10:00 | 53.68 | 50.03
2018-09-24 10:30 | 53.51 | 49.9
2018-09-24 11:00 | 53.48 | 49.93
2018-09-24 11:30 | 53.75 | 50.23
2018-09-24 12:00 | 56.04 | 50.41
2018-09-24 12:30 | 57.27 | 50.96
2018-09-24 13:00 | 56.58 | 50.16
2018-09-24 13:30 | 55.6 | 48.96
2018-09-24 14:00 | 56.12 | 49.54
2018-09-24 14:30 | 56.18 | 49.61
2018-09-24 15:00 | 56.41 | 49.85
2018-09-24 15:30 | 56.69 | 50.1
2018-09-24 16:00 | 57.23 | 50.62
2018-09-24 16:30 | 58.52 | 51.95
2018-09-24 17:00 | 57.76 | 50.94
2018-09-24 17:30 | 57.32 | 50.24
2018-09-24 18:00 | 57.4 | 50.21
2018-09-24 18:30 | 58.39 | 51.39
2018-09-24 19:00 | 58.64 | 51.73
2018-09-24 19:30 | 57.22 | 50.04
2018-09-24 20:00 | 54.93 | 47.27
2018-09-24 20:30 | 53.05 | 44.93
2018-09-24 21:00 | 51.85 | 43.41
2018-09-24 21:30 | 47.65 | 42.07
2018-09-24 22:00 | 42.26 | 39.88
2018-09-24 22:30 | 40.53 | 38.51
2018-09-24 23:00 | 40.58 | 38.58
2018-09-24 23:30 | 37.93 | 35.76
2018-09-25 | 36.24 | 33.93
2018-09-25 00:30 | 35.65 | 33.3
2018-09-25 01:00 | 34.68 | 32.23
2018-09-25 01:30 | 34 | 31.48
2018-09-25 02:00 | 33.29 | 30.69
2018-09-25 02:30 | 32.87 | 30.21
2018-09-25 03:00 | 32.55 | 29.85
2018-09-25 03:30 | 32.7 | 30
2018-09-25 04:00 | 32.75 | 30.06
2018-09-25 04:30 | 33.34 | 30.73
2018-09-25 05:00 | 34.29 | 31.77
2018-09-25 05:30 | 36.3 | 33.98
2018-09-25 06:00 | 38.31 | 36.14
2018-09-25 06:30 | 41.9 | 40.03
2018-09-25 07:00 | 45.13 | 43.35
2018-09-25 07:30 | 49.59 | 46.83
2018-09-25 08:00 | 56.35 | 49.7
2018-09-25 08:30 | 57.03 | 50.52
2018-09-25 09:00 | 57.82 | 51.27
2018-09-25 09:30 | 57.11 | 50.5
2018-09-25 10:00 | 56.44 | 49.76
2018-09-25 10:30 | 57.32 | 50.83
2018-09-25 11:00 | 56.46 | 49.94
2018-09-25 11:30 | 57.19 | 50.81
2018-09-25 12:00 | 57.16 | 50.79
2018-09-25 12:30 | 56.93 | 50.51
2018-09-25 13:00 | 56.32 | 49.79
2018-09-25 13:30 | 56.29 | 49.74
2018-09-25 14:00 | 57.06 | 50.65
2018-09-25 14:30 | 57.52 | 51.18
2018-09-25 15:00 | 58.16 | 51.86
2018-09-25 15:30 | 58.28 | 51.94
2018-09-25 16:00 | 59.11 | 52.81
2018-09-25 16:30 | 60.25 | 54.01
2018-09-25 17:00 | 59.4 | 52.87
2018-09-25 17:30 | 58.41 | 51.53
2018-09-25 18:00 | 58.05 | 51
2018-09-25 18:30 | 59.06 | 52.18
2018-09-25 19:00 | 59.11 | 52.28
2018-09-25 19:30 | 57.59 | 50.46
2018-09-25 20:00 | 55.67 | 48.13
2018-09-25 20:30 | 53.73 | 45.91
2018-09-25 21:00 | 51.7 | 44.16
2018-09-25 21:30 | 50.25 | 42.35
2018-09-25 22:00 | 49.07 | 40.86
2018-09-25 22:30 | 47.42 | 39.18
2018-09-25 23:00 | 47.66 | 39.42
2018-09-25 23:30 | 45.01 | 36.04
2018-09-26 | 43.91 | 34.59
2018-09-26 00:30 | 43.17 | 33.55
2018-09-26 01:00 | 41.63 | 31.44
2018-09-26 01:30 | 40.93 | 30.44
2018-09-26 02:00 | 40.6 | 29.99
2018-09-26 02:30 | 40.25 | 29.44
2018-09-26 03:00 | 40.1 | 29.17
2018-09-26 03:30 | 40.27 | 29.41
2018-09-26 04:00 | 40.04 | 29.1
2018-09-26 04:30 | 40.65 | 29.95
2018-09-26 05:00 | 41.47 | 31.1
2018-09-26 05:30 | 43.01 | 33.27
2018-09-26 06:00 | 44.57 | 35.36
2018-09-26 06:30 | 47.58 | 39.36
2018-09-26 07:00 | 49.95 | 42.13
2018-09-26 07:30 | 52.98 | 45.8
2018-09-26 08:00 | 54.71 | 47.66
2018-09-26 08:30 | 55.1 | 48.19
2018-09-26 09:00 | 55.91 | 48.98
2018-09-26 09:30 | 55.63 | 48.69
2018-09-26 10:00 | 55.86 | 49.02
2018-09-26 10:30 | 55.54 | 48.74
2018-09-26 11:00 | 55.26 | 48.48
2018-09-26 11:30 | 55.69 | 49.03
2018-09-26 12:00 | 55.96 | 49.36
2018-09-26 12:30 | 55.88 | 49.26
2018-09-26 13:00 | 56.08 | 49.45
2018-09-26 13:30 | 56.37 | 49.78
2018-09-26 14:00 | 56.13 | 49.5
2018-09-26 14:30 | 56.58 | 50.01
2018-09-26 15:00 | 57.21 | 50.71
2018-09-26 15:30 | 57.37 | 50.84
2018-09-26 16:00 | 58.43 | 52.01
2018-09-26 16:30 | 59.76 | 53.39
2018-09-26 17:00 | 58.49 | 51.73
2018-09-26 17:30 | 57.44 | 50.32
2018-09-26 18:00 | 57.21 | 49.94
2018-09-26 18:30 | 57.9 | 50.76
2018-09-26 19:00 | 58.13 | 51.06
2018-09-26 19:30 | 56.34 | 48.89
2018-09-26 20:00 | 54 | 46.58
2018-09-26 20:30 | 51.87 | 44.27
2018-09-26 21:00 | 50.7 | 42.83
2018-09-26 21:30 | 48.94 | 40.62
2018-09-26 22:00 | 47.93 | 39.27
2018-09-26 22:30 | 46.7 | 37.81
2018-09-26 23:00 | 46.45 | 37.82
2018-09-26 23:30 | 43.9 | 34.48
2018-09-27 | 42.59 | 32.69
2018-09-27 00:30 | 41.98 | 31.88
2018-09-27 01:00 | 41.27 | 30.8
2018-09-27 01:30 | 40.61 | 29.91
2018-09-27 02:00 | 40.23 | 29.34
2018-09-27 02:30 | 39.79 | 28.65
2018-09-27 03:00 | 39.74 | 28.58
2018-09-27 03:30 | 39.75 | 28.53
2018-09-27 04:00 | 39.63 | 28.33
2018-09-27 04:30 | 40.36 | 29.39
2018-09-27 05:00 | 41.21 | 30.6
2018-09-27 05:30 | 42.83 | 32.95
2018-09-27 06:00 | 44.2 | 34.8
2018-09-27 06:30 | 46.81 | 38.33
2018-09-27 07:00 | 49.33 | 41.23
2018-09-27 07:30 | 51.75 | 44.29
2018-09-27 08:00 | 53.33 | 46.05
2018-09-27 08:30 | 54.07 | 47.05
2018-09-27 09:00 | 54.97 | 47.99
2018-09-27 09:30 | 55.73 | 48.85
2018-09-27 10:00 | 55.16 | 48.26
2018-09-27 10:30 | 55.2 | 48.41
2018-09-27 11:00 | 54.91 | 48.12
2018-09-27 11:30 | 55.07 | 48.36
2018-09-27 12:00 | 54.96 | 48.27
2018-09-27 12:30 | 55.74 | 49.16
2018-09-27 13:00 | 55.23 | 48.55
2018-09-27 13:30 | 55.72 | 49.12
2018-09-27 14:00 | 56.38 | 49.87
2018-09-27 14:30 | 56.73 | 50.24
2018-09-27 15:00 | 57.16 | 50.71
2018-09-27 15:30 | 57.4 | 50.91
2018-09-27 16:00 | 57.94 | 51.45
2018-09-27 16:30 | 59.07 | 52.61
2018-09-27 17:00 | 58.85 | 52.24
2018-09-27 17:30 | 58.32 | 51.47
2018-09-27 18:00 | 58.47 | 51.55
2018-09-27 18:30 | 59.18 | 52.38
2018-09-27 19:00 | 59.67 | 52.93
2018-09-27 19:30 | 57.84 | 50.78
2018-09-27 20:00 | 55.99 | 48.59
2018-09-27 20:30 | 54.46 | 46.7
2018-09-27 21:00 | 53.25 | 45.2
2018-09-27 21:30 | 50.97 | 42.35
2018-09-27 22:00 | 49.22 | 40.1
2018-09-27 22:30 | 47.45 | 38
2018-09-27 23:00 | 47.47 | 38.43
2018-09-27 23:30 | 44.48 | 34.85
2018-09-28 | 43.15 | 33.04
2018-09-28 00:30 | 42.47 | 32.08
2018-09-28 01:00 | 41.39 | 30.57
2018-09-28 01:30 | 40.84 | 29.77
2018-09-28 02:00 | 40.53 | 29.36
2018-09-28 02:30 | 39.95 | 28.78
2018-09-28 03:00 | 39.47 | 28.36
2018-09-28 03:30 | 39.47 | 28.33
2018-09-28 04:00 | 39.34 | 28.15
2018-09-28 04:30 | 39.66 | 28.6
2018-09-28 05:00 | 40.41 | 29.64
2018-09-28 05:30 | 41.76 | 31.59
2018-09-28 06:00 | 43.13 | 33.46
2018-09-28 06:30 | 45.81 | 37.1
2018-09-28 07:00 | 48.34 | 40.02
2018-09-28 07:30 | 50.29 | 42.56
2018-09-28 08:00 | 51.99 | 44.78
2018-09-28 08:30 | 53.29 | 46.48
2018-09-28 09:00 | 53.59 | 46.68
2018-09-28 09:30 | 53.61 | 46.68
2018-09-28 10:00 | 52.95 | 45.93
2018-09-28 10:30 | 54.03 | 47.26
2018-09-28 11:00 | 54.8 | 47.9
2018-09-28 11:30 | 54.44 | 47.52
2018-09-28 12:00 | 54.46 | 47.56
2018-09-28 12:30 | 55 | 48.14
2018-09-28 13:00 | 54.03 | 47.01
2018-09-28 13:30 | 53.95 | 46.9
2018-09-28 14:00 | 54.29 | 47.3
2018-09-28 14:30 | 53.78 | 46.61
2018-09-28 15:00 | 54.03 | 46.84
2018-09-28 15:30 | 54.07 | 46.81
2018-09-28 16:00 | 54.55 | 47.31
2018-09-28 16:30 | 55.94 | 48.83
2018-09-28 17:00 | 55.28 | 47.93
2018-09-28 17:30 | 55.06 | 47.55
2018-09-28 18:00 | 55 | 47.41
2018-09-28 18:30 | 55.33 | 47.81
2018-09-28 19:00 | 55.74 | 48.29
2018-09-28 19:30 | 54.57 | 46.87
2018-09-28 20:00 | 52.82 | 44.71
2018-09-28 20:30 | 51.28 | 42.79
2018-09-28 21:00 | 50.23 | 41.5
2018-09-28 21:30 | 48.93 | 40.26
2018-09-28 22:00 | 47.64 | 38.56
2018-09-28 22:30 | 46.33 | 36.86
2018-09-28 23:00 | 46.32 | 37.21
2018-09-28 23:30 | 43.94 | 34.06
2018-09-29 | 42.27 | 32.26
2018-09-29 00:30 | 41.6 | 31.49
2018-09-29 01:00 | 40.9 | 30.43
2018-09-29 01:30 | 40.4 | 29.72
2018-09-29 02:00 | 40.09 | 29.29
2018-09-29 02:30 | 39.69 | 28.65
2018-09-29 03:00 | 39.61 | 28.54
2018-09-29 03:30 | 39.49 | 28.35
2018-09-29 04:00 | 39.5 | 28.37
2018-09-29 04:30 | 39.53 | 28.4
2018-09-29 05:00 | 39.57 | 28.45
2018-09-29 05:30 | 39.98 | 29.05
2018-09-29 06:00 | 40.33 | 29.52
2018-09-29 06:30 | 41.69 | 31.44
2018-09-29 07:00 | 42 | 31.9
2018-09-29 07:30 | 42.43 | 32.58
2018-09-29 08:00 | 43.23 | 33.74
2018-09-29 08:30 | 43.9 | 34.77
2018-09-29 09:00 | 44.93 | 36.21
2018-09-29 09:30 | 45.12 | 36.51
2018-09-29 10:00 | 44.92 | 36.13
2018-09-29 10:30 | 44.8 | 35.79
2018-09-29 11:00 | 44.47 | 35.39
2018-09-29 11:30 | 44.36 | 35.24
2018-09-29 12:00 | 43.81 | 34.52
2018-09-29 12:30 | 43.13 | 33.58
2018-09-29 13:00 | 42.48 | 32.71
2018-09-29 13:30 | 42.23 | 32.35
2018-09-29 14:00 | 42.64 | 32.85
2018-09-29 14:30 | 42.51 | 32.63
2018-09-29 15:00 | 42.63 | 32.75
2018-09-29 15:30 | 43.51 | 33.88
2018-09-29 16:00 | 44.69 | 35.36
2018-09-29 16:30 | 46.35 | 37.44
2018-09-29 17:00 | 46.59 | 37.7
2018-09-29 17:30 | 47.81 | 39.2
2018-09-29 18:00 | 49.33 | 41.08
2018-09-29 18:30 | 50.67 | 42.79
2018-09-29 19:00 | 50.98 | 43.18
2018-09-29 19:30 | 49.81 | 41.73
2018-09-29 20:00 | 48.77 | 40.41
2018-09-29 20:30 | 47.7 | 39.09
2018-09-29 21:00 | 46.76 | 37.85
2018-09-29 21:30 | 45.84 | 36.64
2018-09-29 22:00 | 45.18 | 35.72
2018-09-29 22:30 | 44.19 | 34.79
2018-09-29 23:00 | 44.5 | 35.27
2018-09-29 23:30 | 42.44 | 32.58
2018-09-30 | 41.32 | 31.03
2018-09-30 00:30 | 40.78 | 30.18
2018-09-30 01:00 | 39.94 | 29.01
2018-09-30 01:30 | 39.57 | 28.49
2018-09-30 02:00 | 39.29 | 28.05
2018-09-30 02:30 | 38.94 | 27.53
2018-09-30 03:00 | 38.88 | 27.4
2018-09-30 03:30 | 38.76 | 27.21
2018-09-30 04:00 | 38.75 | 27.18
2018-09-30 04:30 | 39.01 | 27.59
2018-09-30 05:00 | 39.12 | 27.69
2018-09-30 05:30 | 39.34 | 28.02
2018-09-30 06:00 | 39.08 | 27.6
2018-09-30 06:30 | 39.56 | 28.28
2018-09-30 07:00 | 39.75 | 28.59
2018-09-30 07:30 | 39.79 | 28.76
2018-09-30 08:00 | 39.8 | 28.88
2018-09-30 08:30 | 41.08 | 30.77
2018-09-30 09:00 | 41.22 | 31.07
2018-09-30 09:30 | 41.49 | 31.47
2018-09-30 10:00 | 41.46 | 31.47
2018-09-30 10:30 | 41.03 | 30.99
2018-09-30 11:00 | 41.03 | 31.05
2018-09-30 11:30 | 40.62 | 30.52
2018-09-30 12:00 | 40.5 | 30.37
2018-09-30 12:30 | 40.66 | 30.64
2018-09-30 13:00 | 40.36 | 30.22
2018-09-30 13:30 | 40.42 | 30.27
2018-09-30 14:00 | 41.25 | 31.06
2018-09-30 14:30 | 41.63 | 31.3
2018-09-30 15:00 | 42.18 | 32.01
2018-09-30 15:30 | 42.88 | 32.94
2018-09-30 16:00 | 44.32 | 34.76
2018-09-30 16:30 | 46.2 | 37.16
2018-09-30 17:00 | 46.51 | 37.52
2018-09-30 17:30 | 47.37 | 38.56
2018-09-30 18:00 | 48.94 | 40.54
2018-09-30 18:30 | 50.43 | 42.44
2018-09-30 19:00 | 50.56 | 42.61
2018-09-30 19:30 | 49.33 | 41.09
2018-09-30 20:00 | 48.07 | 39.48
2018-09-30 20:30 | 46.94 | 38.02
2018-09-30 21:00 | 46.42 | 37.37
2018-09-30 21:30 | 45.54 | 36.18
2018-09-30 22:00 | 44.93 | 35.32
2018-09-30 22:30 | 44.52 | 34.82
2018-09-30 23:00 | 44.55 | 35.27
2018-09-30 23:30 | 42.33 | 32.33
2018-10-01 | 41.18 | 30.74
2018-10-01 00:30 | 40.48 | 29.83
2018-10-01 01:00 | 39.73 | 28.66
2018-10-01 01:30 | 39.4 | 28.17
2018-10-01 02:00 | 39.24 | 27.91
2018-10-01 02:30 | 39.08 | 27.7
2018-10-01 03:00 | 38.98 | 27.52
2018-10-01 03:30 | 38.77 | 27.18
2018-10-01 04:00 | 38.85 | 27.3
2018-10-01 04:30 | 38.84 | 27.3
2018-10-01 05:00 | 39.17 | 27.81
2018-10-01 05:30 | 39.94 | 28.96
2018-10-01 06:00 | 39.94 | 28.9
2018-10-01 06:30 | 40.86 | 30.23
2018-10-01 07:00 | 41.5 | 31.16
2018-10-01 07:30 | 42.3 | 32.38
2018-10-01 08:00 | 42.71 | 33.04
2018-10-01 08:30 | 42.64 | 33.07
2018-10-01 09:00 | 42.58 | 33.09
2018-10-01 09:30 | 42.27 | 32.74
2018-10-01 10:00 | 42.54 | 33.13
2018-10-01 10:30 | 43.22 | 34.06
2018-10-01 11:00 | 44.67 | 35.74
2018-10-01 11:30 | 45.25 | 36.23
2018-10-01 12:00 | 43.47 | 33.99
2018-10-01 12:30 | 42.92 | 33.28
2018-10-01 13:00 | 42.46 | 32.66
2018-10-01 13:30 | 42.54 | 32.78
2018-10-01 14:00 | 43.31 | 33.76
2018-10-01 14:30 | 43.61 | 34.11
2018-10-01 15:00 | 44.19 | 34.85
2018-10-01 15:30 | 44.3 | 34.96
2018-10-01 16:00 | 45.53 | 36.5
2018-10-01 16:30 | 47.48 | 38.89
2018-10-01 17:00 | 48.34 | 39.91
2018-10-01 17:30 | 49.82 | 41.69
2018-10-01 18:00 | 51.98 | 44.29
2018-10-01 18:30 | 53.06 | 45.59
2018-10-01 19:00 | 52.94 | 45.47
2018-10-01 19:30 | 51.55 | 43.82
2018-10-01 20:00 | 50.2 | 42.12
2018-10-01 20:30 | 48.56 | 40.07
2018-10-01 21:00 | 47.5 | 38.68
2018-10-01 21:30 | 45.67 | 36.31
2018-10-01 22:00 | 44.74 | 35.08
2018-10-01 22:30 | 43.89 | 33.94
2018-10-01 23:00 | 43.86 | 34.24
2018-10-01 23:30 | 41.65 | 31.36
2018-10-02 | 40.48 | 29.74
2018-10-02 00:30 | 40.26 | 29.39
2018-10-02 01:00 | 39.6 | 28.44
2018-10-02 01:30 | 39.58 | 28.46
2018-10-02 02:00 | 39.41 | 28.2
2018-10-02 02:30 | 39.12 | 27.73
2018-10-02 03:00 | 39.12 | 27.71
2018-10-02 03:30 | 39.23 | 27.87
2018-10-02 04:00 | 39.17 | 27.78
2018-10-02 04:30 | 39.71 | 28.62
2018-10-02 05:00 | 40.46 | 29.73
2018-10-02 05:30 | 41.85 | 31.71
2018-10-02 06:00 | 43.53 | 34.02
2018-10-02 06:30 | 46.37 | 37.86
2018-10-02 07:00 | 49.42 | 41.56
2018-10-02 07:30 | 52.25 | 45.04
2018-10-02 08:00 | 55 | 48.4
2018-10-02 08:30 | 55.76 | 49.33
2018-10-02 09:00 | 55.5 | 48.85
2018-10-02 09:30 | 55.01 | 48.35
2018-10-02 10:00 | 54.77 | 48.11
2018-10-02 10:30 | 54.31 | 47.63
2018-10-02 11:00 | 54.23 | 47.61
2018-10-02 11:30 | 53.94 | 47.09
2018-10-02 12:00 | 54.48 | 47.66
2018-10-02 12:30 | 55.01 | 48.24
2018-10-02 13:00 | 55.15 | 48.37
2018-10-02 13:30 | 56.79 | 50.26
2018-10-02 14:00 | 56.11 | 49.53
2018-10-02 14:30 | 55.83 | 49.2
2018-10-02 15:00 | 57 | 50.49
2018-10-02 15:30 | 57.41 | 50.89
2018-10-02 16:00 | 58.23 | 51.74
2018-10-02 16:30 | 59.78 | 53.4
2018-10-02 17:00 | 57.27 | 50.35
2018-10-02 17:30 | 57.04 | 49.92
2018-10-02 18:00 | 57.47 | 50.32
2018-10-02 18:30 | 58.47 | 51.48
2018-10-02 19:00 | 58.63 | 51.67
2018-10-02 19:30 | 56.67 | 49.35
2018-10-02 20:00 | 54.8 | 47.07
2018-10-02 20:30 | 52.74 | 44.53
2018-10-02 21:00 | 51.21 | 42.62
2018-10-02 21:30 | 49.61 | 40.64
2018-10-02 22:00 | 47.03 | 38.9
2018-10-02 22:30 | 39.67 | 37.18
2018-10-02 23:00 | 39.47 | 37.17
2018-10-02 23:30 | 36.5 | 33.99
2018-10-03 | 35.24 | 32.63
2018-10-03 00:30 | 34.48 | 31.81
2018-10-03 01:00 | 33.59 | 30.8
2018-10-03 01:30 | 32.88 | 30.01
2018-10-03 02:00 | 32.39 | 29.46
2018-10-03 02:30 | 31.87 | 28.86
2018-10-03 03:00 | 31.58 | 28.53
2018-10-03 03:30 | 31.52 | 28.46
2018-10-03 04:00 | 31.74 | 28.7
2018-10-03 04:30 | 32.35 | 29.45
2018-10-03 05:00 | 33.18 | 30.54
2018-10-03 05:30 | 35.27 | 32.86
2018-10-03 06:00 | 37.11 | 34.87
2018-10-03 06:30 | 40.87 | 38.94
2018-10-03 07:00 | 44.08 | 42.24
2018-10-03 07:30 | 47.62 | 45.33
2018-10-03 08:00 | 54.96 | 48.01
2018-10-03 08:30 | 55.89 | 48.99
2018-10-03 09:00 | 55.7 | 48.84
2018-10-03 09:30 | 55.12 | 48.2
2018-10-03 10:00 | 54.83 | 47.9
2018-10-03 10:30 | 55.76 | 49.04
2018-10-03 11:00 | 55.65 | 48.96
2018-10-03 11:30 | 55.24 | 48.5
2018-10-03 12:00 | 55.23 | 48.53
2018-10-03 12:30 | 55.34 | 48.66
2018-10-03 13:00 | 54.65 | 47.81
2018-10-03 13:30 | 55.32 | 48.57
2018-10-03 14:00 | 55.24 | 48.48
2018-10-03 14:30 | 55.6 | 48.89
2018-10-03 15:00 | 55.72 | 48.98
2018-10-03 15:30 | 55.73 | 48.94
2018-10-03 16:00 | 56.39 | 49.61
2018-10-03 16:30 | 57.82 | 51.14
2018-10-03 17:00 | 57.38 | 50.49
2018-10-03 17:30 | 56.8 | 49.61
2018-10-03 18:00 | 56.68 | 49.36
2018-10-03 18:30 | 57.78 | 50.62
2018-10-03 19:00 | 58.03 | 50.92
2018-10-03 19:30 | 56.15 | 48.69
2018-10-03 20:00 | 54.21 | 46.33
2018-10-03 20:30 | 52.54 | 44.26
2018-10-03 21:00 | 50.72 | 42.29
2018-10-03 21:30 | 49.49 | 40.89
2018-10-03 22:00 | 48 | 38.96
2018-10-03 22:30 | 46.49 | 37.32
2018-10-03 23:00 | 46.92 | 37.93
2018-10-03 23:30 | 44.56 | 34.87
2018-10-04 | 42.73 | 32.42
2018-10-04 00:30 | 42.42 | 31.98
2018-10-04 01:00 | 41.62 | 30.87
2018-10-04 01:30 | 41.06 | 30.08
2018-10-04 02:00 | 40.39 | 29.31
2018-10-04 02:30 | 39.61 | 28.56
2018-10-04 03:00 | 39.26 | 28.01
2018-10-04 03:30 | 39.28 | 28.03
2018-10-04 04:00 | 39.35 | 28.1
2018-10-04 04:30 | 39.85 | 28.83
2018-10-04 05:00 | 40.38 | 29.59
2018-10-04 05:30 | 42.05 | 31.98
2018-10-04 06:00 | 43.38 | 33.74
2018-10-04 06:30 | 46.15 | 37.51
2018-10-04 07:00 | 48.53 | 40.26
2018-10-04 07:30 | 50.57 | 42.91
2018-10-04 08:00 | 51.47 | 44.13
2018-10-04 08:30 | 52.45 | 45.48
2018-10-04 09:00 | 53.4 | 46.67
2018-10-04 09:30 | 54.32 | 47.26
2018-10-04 10:00 | 53.91 | 46.76
2018-10-04 10:30 | 54.43 | 47.45
2018-10-04 11:00 | 54.45 | 47.54
2018-10-04 11:30 | 54.8 | 48.01
2018-10-04 12:00 | 55.13 | 48.43
2018-10-04 12:30 | 55.73 | 49.14
2018-10-04 13:00 | 55.18 | 48.48
2018-10-04 13:30 | 55.41 | 48.75
2018-10-04 14:00 | 56.2 | 49.69
2018-10-04 14:30 | 56.74 | 50.3
2018-10-04 15:00 | 57.16 | 50.74
2018-10-04 15:30 | 57.69 | 51.3
2018-10-04 16:00 | 58.6 | 52.26
2018-10-04 16:30 | 58.98 | 52.52
2018-10-04 17:00 | 58.63 | 52.01
2018-10-04 17:30 | 57.68 | 50.73
2018-10-04 18:00 | 58.85 | 52
2018-10-04 18:30 | 59.92 | 53.21
2018-10-04 19:00 | 60.45 | 53.84
2018-10-04 19:30 | 58.47 | 51.5
2018-10-04 20:00 | 56.44 | 49.07
2018-10-04 20:30 | 54.67 | 46.91
2018-10-04 21:00 | 52.71 | 45.16
2018-10-04 21:30 | 50.29 | 42.4
2018-10-04 22:00 | 48.92 | 40.68
2018-10-04 22:30 | 47.27 | 38.74
2018-10-04 23:00 | 47.29 | 39.03
2018-10-04 23:30 | 44.64 | 35.65
2018-10-05 | 43.04 | 33.53
2018-10-05 00:30 | 42.39 | 32.73
2018-10-05 01:00 | 41.73 | 31.73
2018-10-05 01:30 | 41.01 | 30.71
2018-10-05 02:00 | 40.45 | 29.9
2018-10-05 02:30 | 40.03 | 29.25
2018-10-05 03:00 | 39.77 | 28.86
2018-10-05 03:30 | 39.82 | 28.93
2018-10-05 04:00 | 39.75 | 28.8
2018-10-05 04:30 | 40.05 | 29.2
2018-10-05 05:00 | 40.96 | 30.55
2018-10-05 05:30 | 42.53 | 32.78
2018-10-05 06:00 | 43.63 | 34.23
2018-10-05 06:30 | 46.72 | 38.36
2018-10-05 07:00 | 49.31 | 41.34
2018-10-05 07:30 | 52.02 | 44.8
2018-10-05 08:00 | 53.45 | 46.32
2018-10-05 08:30 | 54.51 | 47.54
2018-10-05 09:00 | 56.11 | 49.3
2018-10-05 09:30 | 56.22 | 49.45
2018-10-05 10:00 | 56.06 | 49.35
2018-10-05 10:30 | 55.84 | 49.16
2018-10-05 11:00 | 55.67 | 49.05
2018-10-05 11:30 | 55.82 | 49.27
2018-10-05 12:00 | 55.58 | 48.98
2018-10-05 12:30 | 55.71 | 49.13
2018-10-05 13:00 | 55.47 | 48.83
2018-10-05 13:30 | 55.38 | 48.7
2018-10-05 14:00 | 55.7 | 49.06
2018-10-05 14:30 | 56.06 | 49.44
2018-10-05 15:00 | 56.2 | 49.55
2018-10-05 15:30 | 56.27 | 49.54
2018-10-05 16:00 | 56.77 | 50.04
2018-10-05 16:30 | 57.89 | 51.24
2018-10-05 17:00 | 58.06 | 51.33
2018-10-05 17:30 | 56.6 | 49.48
2018-10-05 18:00 | 56.76 | 49.57
2018-10-05 18:30 | 57.03 | 49.89
2018-10-05 19:00 | 57.16 | 50.03
2018-10-05 19:30 | 55.6 | 48.17
2018-10-05 20:00 | 53.96 | 46.49
2018-10-05 20:30 | 52.67 | 45.04
2018-10-05 21:00 | 51.53 | 43.64
2018-10-05 21:30 | 50.15 | 41.91
2018-10-05 22:00 | 48.97 | 40.38
2018-10-05 22:30 | 47.78 | 38.79
2018-10-05 23:00 | 48.03 | 39.07
2018-10-05 23:30 | 45.1 | 35.45
2018-10-06 | 43.6 | 33.76
2018-10-06 00:30 | 43.11 | 33.07
2018-10-06 01:00 | 42.35 | 32.01
2018-10-06 01:30 | 41.88 | 31.34
2018-10-06 02:00 | 41.65 | 31.05
2018-10-06 02:30 | 41.28 | 30.52
2018-10-06 03:00 | 40.94 | 30.02
2018-10-06 03:30 | 40.61 | 29.73
2018-10-06 04:00 | 40.31 | 29.67
2018-10-06 04:30 | 40.44 | 29.88
2018-10-06 05:00 | 41.02 | 30.73
2018-10-06 05:30 | 41.8 | 31.83
2018-10-06 06:00 | 42.09 | 32.17
2018-10-06 06:30 | 43.37 | 33.95
2018-10-06 07:00 | 43.87 | 34.66
2018-10-06 07:30 | 44.74 | 35.9
2018-10-06 08:00 | 45.87 | 37.44
2018-10-06 08:30 | 47.55 | 39.72
2018-10-06 09:00 | 48.14 | 40.51
2018-10-06 09:30 | 49.54 | 41.92
2018-10-06 10:00 | 50.05 | 42.54
2018-10-06 10:30 | 49.56 | 41.99
2018-10-06 11:00 | 48.7 | 40.98
2018-10-06 11:30 | 46.2 | 37.93
2018-10-06 12:00 | 45.99 | 37.64
2018-10-06 12:30 | 46.02 | 37.62
2018-10-06 13:00 | 45.13 | 36.47
2018-10-06 13:30 | 44.8 | 36.03
2018-10-06 14:00 | 44.79 | 35.97
2018-10-06 14:30 | 45.05 | 36.23
2018-10-06 15:00 | 45.7 | 37
2018-10-06 15:30 | 46.37 | 37.81
2018-10-06 16:00 | 47.09 | 38.65
2018-10-06 16:30 | 49.5 | 41.52
2018-10-06 17:00 | 48.44 | 40.17
2018-10-06 17:30 | 49.59 | 41.56
2018-10-06 18:00 | 50.9 | 43.16
2018-10-06 18:30 | 52.5 | 45.1
2018-10-06 19:00 | 53.21 | 45.98
2018-10-06 19:30 | 51.94 | 44.47
2018-10-06 20:00 | 50.78 | 43.06
2018-10-06 20:30 | 49.73 | 41.77
2018-10-06 21:00 | 49.03 | 40.88
2018-10-06 21:30 | 47.96 | 39.54
2018-10-06 22:00 | 47.33 | 38.7
2018-10-06 22:30 | 46.51 | 37.61
2018-10-06 23:00 | 46.89 | 38.03
2018-10-06 23:30 | 44.55 | 34.95
2018-10-07 | 43.07 | 33.14
2018-10-07 00:30 | 42.3 | 32.5
2018-10-07 01:00 | 41.68 | 31.59
2018-10-07 01:30 | 41.06 | 30.72
2018-10-07 02:00 | 40.66 | 30.17
2018-10-07 02:30 | 40.21 | 29.52
2018-10-07 03:00 | 40.12 | 29.33
2018-10-07 03:30 | 39.98 | 29.12
2018-10-07 04:00 | 39.93 | 29.03
2018-10-07 04:30 | 40.12 | 29.34
2018-10-07 05:00 | 40.32 | 29.62
2018-10-07 05:30 | 40.73 | 30.23
2018-10-07 06:00 | 40.54 | 29.9
2018-10-07 06:30 | 40.7 | 30.38
2018-10-07 07:00 | 41.22 | 31.11
2018-10-07 07:30 | 41.28 | 31.29
2018-10-07 08:00 | 41.28 | 31.34
2018-10-07 08:30 | 42.29 | 32.8
2018-10-07 09:00 | 43.06 | 33.98
2018-10-07 09:30 | 43.65 | 34.8
2018-10-07 10:00 | 43.42 | 34.61
2018-10-07 10:30 | 43.91 | 34.96
2018-10-07 11:00 | 43.83 | 34.77
2018-10-07 11:30 | 43.71 | 34.64
2018-10-07 12:00 | 44.26 | 35.4
2018-10-07 12:30 | 44.36 | 35.54
2018-10-07 13:00 | 43.65 | 34.61
2018-10-07 13:30 | 43.8 | 34.81
2018-10-07 14:00 | 43.99 | 34.99
2018-10-07 14:30 | 44.08 | 35.07
2018-10-07 15:00 | 44.78 | 35.94
2018-10-07 15:30 | 45.69 | 37.07
2018-10-07 16:00 | 46.82 | 38.45
2018-10-07 16:30 | 48.63 | 40.62
2018-10-07 17:00 | 48.73 | 40.67
2018-10-07 17:30 | 50.44 | 42.73
2018-10-07 18:00 | 52.67 | 45.41
2018-10-07 18:30 | 53.98 | 47.02
2018-10-07 19:00 | 54.14 | 47.25
2018-10-07 19:30 | 52.56 | 45.39
2018-10-07 20:00 | 51.16 | 43.71
2018-10-07 20:30 | 49.78 | 42
2018-10-07 21:00 | 48.81 | 40.81
2018-10-07 21:30 | 47.44 | 39.04
2018-10-07 22:00 | 45.97 | 37.11
2018-10-07 22:30 | 45.13 | 35.98
2018-10-07 23:00 | 45.25 | 36.12
2018-10-07 23:30 | 42.7 | 33.12
2018-10-08 | 41.53 | 31.68
2018-10-08 00:30 | 41.25 | 31.25
2018-10-08 01:00 | 40.25 | 29.89
2018-10-08 01:30 | 39.95 | 29.44
2018-10-08 02:00 | 39.79 | 29.21
2018-10-08 02:30 | 39.58 | 28.85
2018-10-08 03:00 | 39.43 | 28.6
2018-10-08 03:30 | 39.74 | 29.07
2018-10-08 04:00 | 39.82 | 29.2
2018-10-08 04:30 | 40.43 | 30.1
2018-10-08 05:00 | 41.44 | 31.53
2018-10-08 05:30 | 43.42 | 34.24
2018-10-08 06:00 | 45.26 | 36.67
2018-10-08 06:30 | 48.96 | 41.43
2018-10-08 07:00 | 52.06 | 45.01
2018-10-08 07:30 | 55.84 | 49.41
2018-10-08 08:00 | 59.02 | 51.97
2018-10-08 08:30 | 62.57 | 52.94
2018-10-08 09:00 | 63.98 | 54.75
2018-10-08 09:30 | 63.84 | 54.61
2018-10-08 10:00 | 64.15 | 55.02
2018-10-08 10:30 | 65.16 | 56.25
2018-10-08 11:00 | 65.37 | 56.52
2018-10-08 11:30 | 64.53 | 55.58
2018-10-08 12:00 | 64.28 | 55.32
2018-10-08 12:30 | 62.99 | 53.81
2018-10-08 13:00 | 63.1 | 53.96
2018-10-08 13:30 | 63.86 | 54.87
2018-10-08 14:00 | 63.97 | 55.01
2018-10-08 14:30 | 64.8 | 55.97
2018-10-08 15:00 | 64.71 | 55.84
2018-10-08 15:30 | 64.43 | 55.42
2018-10-08 16:00 | 64.4 | 55.24
2018-10-08 16:30 | 65.39 | 56.24
2018-10-08 17:00 | 65.19 | 55.79
2018-10-08 17:30 | 64.6 | 54.87
2018-10-08 18:00 | 63.3 | 53.16
2018-10-08 18:30 | 64.09 | 54.09
2018-10-08 19:00 | 64.64 | 54.78
2018-10-08 19:30 | 62.82 | 52.52
2018-10-08 20:00 | 60.79 | 49.9
2018-10-08 20:30 | 59.03 | 47.64
2018-10-08 21:00 | 57.71 | 45.85
2018-10-08 21:30 | 55.99 | 43.55
2018-10-08 22:00 | 54.52 | 41.45
2018-10-08 22:30 | 53.08 | 39.91
2018-10-08 23:00 | 53.32 | 40.3
2018-10-08 23:30 | 50.5 | 36.68
2018-10-09 | 49.07 | 34.81
2018-10-09 00:30 | 48.35 | 33.81
2018-10-09 01:00 | 47.84 | 32.89
2018-10-09 01:30 | 47.28 | 32
2018-10-09 02:00 | 46.9 | 31.37
2018-10-09 02:30 | 46.58 | 30.79
2018-10-09 03:00 | 46.53 | 30.69
2018-10-09 03:30 | 46.54 | 30.68
2018-10-09 04:00 | 46.46 | 30.51
2018-10-09 04:30 | 46.67 | 31.14
2018-10-09 05:00 | 47.05 | 32.22
2018-10-09 05:30 | 48.28 | 34.17
2018-10-09 06:00 | 49.51 | 35.95
2018-10-09 06:30 | 52.31 | 40.12
2018-10-09 07:00 | 55.51 | 44.34
2018-10-09 07:30 | 59.07 | 48.82
2018-10-09 08:00 | 61.1 | 51.04
2018-10-09 08:30 | 60.07 | 49.86
2018-10-09 09:00 | 63.1 | 53.63
2018-10-09 09:30 | 62.95 | 53.53
2018-10-09 10:00 | 62.33 | 52.85
2018-10-09 10:30 | 62.32 | 52.82
2018-10-09 11:00 | 62.75 | 53.25
2018-10-09 11:30 | 63.08 | 53.71
2018-10-09 12:00 | 63.17 | 53.86
2018-10-09 12:30 | 64.16 | 55.03
2018-10-09 13:00 | 63.86 | 54.66
2018-10-09 13:30 | 63.79 | 54.59
2018-10-09 14:00 | 64.55 | 55.5
2018-10-09 14:30 | 65.13 | 56.18
2018-10-09 15:00 | 65.26 | 56.27
2018-10-09 15:30 | 65.08 | 55.95
2018-10-09 16:00 | 65.86 | 56.7
2018-10-09 16:30 | 66.57 | 57.41
2018-10-09 17:00 | 65.98 | 56.58
2018-10-09 17:30 | 64.54 | 54.57
2018-10-09 18:00 | 63.86 | 53.74
2018-10-09 18:30 | 64.5 | 54.53
2018-10-09 19:00 | 65.03 | 55.21
2018-10-09 19:30 | 62.4 | 51.93
2018-10-09 20:00 | 60.59 | 49.64
2018-10-09 20:30 | 59.19 | 47.78
2018-10-09 21:00 | 57.93 | 46.13
2018-10-09 21:30 | 56.78 | 44.57
2018-10-09 22:00 | 53.05 | 42.77
2018-10-09 22:30 | 49.75 | 41.1
2018-10-09 23:00 | 49.87 | 41.24
2018-10-09 23:30 | 46.84 | 37.63
2018-10-10 | 45.08 | 35.56
2018-10-10 00:30 | 44.53 | 34.82
2018-10-10 01:00 | 43.64 | 33.59
2018-10-10 01:30 | 43.05 | 32.75
2018-10-10 02:00 | 42.59 | 32.09
2018-10-10 02:30 | 42.09 | 31.38
2018-10-10 03:00 | 41.96 | 31.16
2018-10-10 03:30 | 41.87 | 31.02
2018-10-10 04:00 | 41.56 | 30.9
2018-10-10 04:30 | 41.58 | 31.54
2018-10-10 05:00 | 42.04 | 32.34
2018-10-10 05:30 | 43.49 | 34.32
2018-10-10 06:00 | 44.71 | 35.97
2018-10-10 06:30 | 47.98 | 40.2
2018-10-10 07:00 | 51.89 | 44.76
2018-10-10 07:30 | 55.96 | 49.67
2018-10-10 08:00 | 59.17 | 52.9
2018-10-10 08:30 | 59.2 | 53.04
2018-10-10 09:00 | 59.61 | 53.62
2018-10-10 09:30 | 60.37 | 54.53
2018-10-10 10:00 | 59.86 | 54.01
2018-10-10 10:30 | 67.17 | 54.81
2018-10-10 11:00 | 67.68 | 54.41
2018-10-10 11:30 | 67.67 | 54.56
2018-10-10 12:00 | 67.38 | 54.21
2018-10-10 12:30 | 67.65 | 54.51
2018-10-10 13:00 | 67.24 | 53.91
2018-10-10 13:30 | 67.75 | 54.57
2018-10-10 14:00 | 68.22 | 55.16
2018-10-10 14:30 | 69.03 | 56.14
2018-10-10 15:00 | 69.42 | 56.6
2018-10-10 15:30 | 69.73 | 56.87
2018-10-10 16:00 | 70.57 | 57.84
2018-10-10 16:30 | 71.34 | 58.58
2018-10-10 17:00 | 70.28 | 56.97
2018-10-10 17:30 | 69.18 | 55.28
2018-10-10 18:00 | 68.62 | 54.27
2018-10-10 18:30 | 69.08 | 54.84
2018-10-10 19:00 | 69.4 | 55.29
2018-10-10 19:30 | 67.86 | 53.24
2018-10-10 20:00 | 66.07 | 50.73
2018-10-10 20:30 | 64.61 | 48.64
2018-10-10 21:00 | 63.13 | 46.53
2018-10-10 21:30 | 61.32 | 44.14
2018-10-10 22:00 | 59.89 | 42.23
2018-10-10 22:30 | 59.1 | 40.97
2018-10-10 23:00 | 59.36 | 41.31
2018-10-10 23:30 | 57.05 | 37.69
2018-10-11 | 46.97 | 35.27
2018-10-11 00:30 | 43.83 | 34.29
2018-10-11 01:00 | 42.87 | 33.08
2018-10-11 01:30 | 42.44 | 32.5
2018-10-11 02:00 | 42.04 | 31.92
2018-10-11 02:30 | 41.56 | 31.2
2018-10-11 03:00 | 41.51 | 31.13
2018-10-11 03:30 | 41.74 | 31.42
2018-10-11 04:00 | 41.68 | 31.31
2018-10-11 04:30 | 41.97 | 31.71
2018-10-11 05:00 | 42.72 | 32.76
2018-10-11 05:30 | 44.27 | 34.9
2018-10-11 06:00 | 45.63 | 36.65
2018-10-11 06:30 | 49.02 | 41.07
2018-10-11 07:00 | 52.34 | 45.27
2018-10-11 07:30 | 56.21 | 49.99
2018-10-11 08:00 | 60.11 | 54.04
2018-10-11 08:30 | 60.16 | 54.15
2018-10-11 09:00 | 60.11 | 54.2
2018-10-11 09:30 | 60.48 | 54.68
2018-10-11 10:00 | 59.61 | 53.74
2018-10-11 10:30 | 59.98 | 54.2
2018-10-11 11:00 | 60.42 | 54.75
2018-10-11 11:30 | 67.09 | 55.23
2018-10-11 12:00 | 68.58 | 55.7
2018-10-11 12:30 | 68.58 | 55.7
2018-10-11 13:00 | 68.25 | 55.23
2018-10-11 13:30 | 68.94 | 56.13
2018-10-11 14:00 | 69.41 | 56.74
2018-10-11 14:30 | 69.82 | 57.24
2018-10-11 15:00 | 70.03 | 57.44
2018-10-11 15:30 | 70.11 | 57.45
2018-10-11 16:00 | 70.86 | 58.21
2018-10-11 16:30 | 71.7 | 59.09
2018-10-11 17:00 | 70.91 | 57.87
2018-10-11 17:30 | 69.59 | 55.88
2018-10-11 18:00 | 68.97 | 54.8
2018-10-11 18:30 | 69.63 | 55.64
2018-10-11 19:00 | 70.18 | 56.43
2018-10-11 19:30 | 68.56 | 54.19
2018-10-11 20:00 | 66.82 | 51.81
2018-10-11 20:30 | 65.53 | 49.94
2018-10-11 21:00 | 64.22 | 48.06
2018-10-11 21:30 | 62.71 | 45.83
2018-10-11 22:00 | 61.32 | 43.73
2018-10-11 22:30 | 49.97 | 41.28
2018-10-11 23:00 | 49.85 | 41.37
2018-10-11 23:30 | 47 | 38.01
2018-10-12 | 45.54 | 36.12
2018-10-12 00:30 | 44.48 | 35.09
2018-10-12 01:00 | 43.24 | 33.57
2018-10-12 01:30 | 42.64 | 32.73
2018-10-12 02:00 | 42.07 | 31.94
2018-10-12 02:30 | 41.78 | 31.5
2018-10-12 03:00 | 41.47 | 31.03
2018-10-12 03:30 | 41.47 | 31.05
2018-10-12 04:00 | 41.51 | 31.03
2018-10-12 04:30 | 41.82 | 31.48
2018-10-12 05:00 | 42.57 | 32.51
2018-10-12 05:30 | 44.34 | 34.98
2018-10-12 06:00 | 45.65 | 36.7
2018-10-12 06:30 | 49.91 | 42.21
2018-10-12 07:00 | 53.35 | 46.52
2018-10-12 07:30 | 58.08 | 51.67
2018-10-12 08:00 | 69.27 | 56.19
2018-10-12 08:30 | 69.24 | 56.17
2018-10-12 09:00 | 68.99 | 55.57
2018-10-12 09:30 | 69.39 | 56.18
2018-10-12 10:00 | 70.65 | 57.79
2018-10-12 10:30 | 71.9 | 59.41
2018-10-12 11:00 | 67.69 | 54.2
2018-10-12 11:30 | 68.67 | 55.52
2018-10-12 12:00 | 68.51 | 55.36
2018-10-12 12:30 | 68.32 | 55.06
2018-10-12 13:00 | 68.66 | 55.45
2018-10-12 13:30 | 71.09 | 58.4
2018-10-12 14:00 | 70.67 | 57.78
2018-10-12 14:30 | 67.92 | 54.31
2018-10-12 15:00 | 69.78 | 56.54
2018-10-12 15:30 | 68.89 | 55.15
2018-10-12 16:00 | 69.37 | 55.66
2018-10-12 16:30 | 69.11 | 55.16
2018-10-12 17:00 | 67.77 | 53.25
2018-10-12 17:30 | 66.4 | 51.25
2018-10-12 18:00 | 66.22 | 50.8
2018-10-12 18:30 | 66.38 | 51.08
2018-10-12 19:00 | 65.78 | 50.48
2018-10-12 19:30 | 64.34 | 48.84
2018-10-12 20:00 | 64.48 | 48.98
2018-10-12 20:30 | 63.38 | 47.34
2018-10-12 21:00 | 59.8 | 45.8
2018-10-12 21:30 | 55.75 | 43.57
2018-10-12 22:00 | 54.27 | 41.52
2018-10-12 22:30 | 54.12 | 41.26
2018-10-12 23:00 | 54.93 | 42.28
2018-10-12 23:30 | 52.79 | 39.34
2018-10-13 | 51.36 | 37.27
2018-10-13 00:30 | 50.15 | 36.12
2018-10-13 01:00 | 48.89 | 34.2
2018-10-13 01:30 | 48.27 | 33.24
2018-10-13 02:00 | 47.97 | 32.77
2018-10-13 02:30 | 47.48 | 32.5
2018-10-13 03:00 | 46.97 | 31.9
2018-10-13 03:30 | 46.84 | 31.68
2018-10-13 04:00 | 46.85 | 31.71
2018-10-13 04:30 | 47.05 | 32.05
2018-10-13 05:00 | 47.4 | 32.6
2018-10-13 05:30 | 48.06 | 33.65
2018-10-13 06:00 | 48.39 | 34.13
2018-10-13 06:30 | 49.77 | 36.25
2018-10-13 07:00 | 51.67 | 39
2018-10-13 07:30 | 54.03 | 42.3
2018-10-13 08:00 | 55.36 | 44.16
2018-10-13 08:30 | 56.7 | 46
2018-10-13 09:00 | 57.7 | 47.28
2018-10-13 09:30 | 56.58 | 45.98
2018-10-13 10:00 | 56.88 | 46.23
2018-10-13 10:30 | 58.16 | 47.59
2018-10-13 11:00 | 57.94 | 47.33
2018-10-13 11:30 | 57.56 | 46.83
2018-10-13 12:00 | 53.84 | 42.08
2018-10-13 12:30 | 53.62 | 41.71
2018-10-13 13:00 | 53.54 | 41.49
2018-10-13 13:30 | 52.33 | 39.89
2018-10-13 14:00 | 51.99 | 39.41
2018-10-13 14:30 | 53.73 | 41.65
2018-10-13 15:00 | 52.98 | 40.6
2018-10-13 15:30 | 53.94 | 41.81
2018-10-13 16:00 | 54.13 | 42.03
2018-10-13 16:30 | 52.49 | 39.81
2018-10-13 17:00 | 53.34 | 40.84
2018-10-13 17:30 | 54.15 | 41.86
2018-10-13 18:00 | 55.47 | 43.63
2018-10-13 18:30 | 56.07 | 44.5
2018-10-13 19:00 | 56.01 | 44.43
2018-10-13 19:30 | 54.96 | 43.05
2018-10-13 20:00 | 54.11 | 41.89
2018-10-13 20:30 | 53.01 | 40.38
2018-10-13 21:00 | 52.5 | 39.64
2018-10-13 21:30 | 51.81 | 38.63
2018-10-13 22:00 | 50.94 | 37.29
2018-10-13 22:30 | 49.88 | 35.64
2018-10-13 23:00 | 48.7 | 34.08
2018-10-13 23:30 | 46.59 | 31.07
2018-10-14 | 45.77 | 29.77
2018-10-14 00:30 | 45.7 | 29.6
2018-10-14 01:00 | 44.78 | 28.06
2018-10-14 01:30 | 44.28 | 27.18
2018-10-14 02:00 | 43.93 | 26.56
2018-10-14 02:30 | 43.69 | 26.08
2018-10-14 03:00 | 43.55 | 25.73
2018-10-14 03:30 | 43.58 | 25.74
2018-10-14 04:00 | 40.71 | 25.61
2018-10-14 04:30 | 37.81 | 25.86
2018-10-14 05:00 | 37.91 | 26
2018-10-14 05:30 | 38.13 | 26.3
2018-10-14 06:00 | 37.86 | 25.82
2018-10-14 06:30 | 38.59 | 26.97
2018-10-14 07:00 | 38.64 | 27.12
2018-10-14 07:30 | 38.79 | 27.46
2018-10-14 08:00 | 39.09 | 28.04
2018-10-14 08:30 | 39.82 | 29.23
2018-10-14 09:00 | 40.28 | 29.98
2018-10-14 09:30 | 40.63 | 30.56
2018-10-14 10:00 | 40.37 | 30.29
2018-10-14 10:30 | 40.47 | 30.49
2018-10-14 11:00 | 40.5 | 30.63
2018-10-14 11:30 | 40.03 | 30.03
2018-10-14 12:00 | 40.32 | 30.43
2018-10-14 12:30 | 40.98 | 31.06
2018-10-14 13:00 | 41.32 | 31.31
2018-10-14 13:30 | 41.54 | 31.59
2018-10-14 14:00 | 41.81 | 31.92
2018-10-14 14:30 | 41.95 | 32.09
2018-10-14 15:00 | 42.32 | 32.51
2018-10-14 15:30 | 43.18 | 33.56
2018-10-14 16:00 | 44.02 | 34.6
2018-10-14 16:30 | 46.13 | 37.26
2018-10-14 17:00 | 46.57 | 37.79
2018-10-14 17:30 | 48.42 | 40.11
2018-10-14 18:00 | 49.79 | 41.75
2018-10-14 18:30 | 51.6 | 44.01
2018-10-14 19:00 | 52.33 | 44.91
2018-10-14 19:30 | 51.04 | 43.36
2018-10-14 20:00 | 49.72 | 41.7
2018-10-14 20:30 | 48.2 | 39.79
2018-10-14 21:00 | 46.86 | 38.07
2018-10-14 21:30 | 45.69 | 36.55
2018-10-14 22:00 | 44.46 | 34.92
2018-10-14 22:30 | 43.25 | 33.47
2018-10-14 23:00 | 43.47 | 34.04
2018-10-14 23:30 | 41.28 | 31.07
2018-10-15 | 40.19 | 29.49
2018-10-15 00:30 | 39.75 | 28.92
2018-10-15 01:00 | 39.03 | 27.74
2018-10-15 01:30 | 38.53 | 27.01
2018-10-15 02:00 | 38.55 | 27.05
2018-10-15 02:30 | 38.5 | 26.96
2018-10-15 03:00 | 38.38 | 26.76
2018-10-15 03:30 | 38.37 | 26.75
2018-10-15 04:00 | 38.42 | 26.83
2018-10-15 04:30 | 38.85 | 27.52
2018-10-15 05:00 | 39.74 | 28.83
2018-10-15 05:30 | 41 | 30.64
2018-10-15 06:00 | 42.62 | 32.92
2018-10-15 06:30 | 45.87 | 37.37
2018-10-15 07:00 | 48.95 | 41.24
2018-10-15 07:30 | 52.76 | 45.82
2018-10-15 08:00 | 54.4 | 47.93
2018-10-15 08:30 | 56.33 | 49.87
2018-10-15 09:00 | 57.35 | 50.93
2018-10-15 09:30 | 57.44 | 51.12
2018-10-15 10:00 | 56.45 | 50
2018-10-15 10:30 | 56.6 | 50.24
2018-10-15 11:00 | 57.01 | 50.81
2018-10-15 11:30 | 57.4 | 51.28
2018-10-15 12:00 | 58.18 | 52.19
2018-10-15 12:30 | 58.87 | 52.99
2018-10-15 13:00 | 58.2 | 52.2
2018-10-15 13:30 | 59.1 | 53.24
2018-10-15 14:00 | 59.47 | 53.65
2018-10-15 14:30 | 60.12 | 54.37
2018-10-15 15:00 | 60.27 | 54.5
2018-10-15 15:30 | 60.16 | 54.29
2018-10-15 16:00 | 61.34 | 55.58
2018-10-15 16:30 | 62.39 | 56.65
2018-10-15 17:00 | 61.34 | 55.34
2018-10-15 17:30 | 60.01 | 53.66
2018-10-15 18:00 | 59.39 | 52.79
2018-10-15 18:30 | 59.53 | 52.95
2018-10-15 19:00 | 60.14 | 53.66
2018-10-15 19:30 | 58.32 | 51.51
2018-10-15 20:00 | 56.26 | 49.06
2018-10-15 20:30 | 54.77 | 47.24
2018-10-15 21:00 | 52.92 | 44.99
2018-10-15 21:30 | 51.43 | 43.15
2018-10-15 22:00 | 49.71 | 40.96
2018-10-15 22:30 | 48.18 | 39.01
2018-10-15 23:00 | 48.48 | 39.3
2018-10-15 23:30 | 45.55 | 35.68
2018-10-16 | 43.89 | 33.71
2018-10-16 00:30 | 43.24 | 32.81
2018-10-16 01:00 | 42.34 | 31.55
2018-10-16 01:30 | 41.52 | 30.8
2018-10-16 02:00 | 40.89 | 30.09
2018-10-16 02:30 | 40.34 | 29.27
2018-10-16 03:00 | 40.15 | 28.99
2018-10-16 03:30 | 40.28 | 29.15
2018-10-16 04:00 | 40.22 | 29.15
2018-10-16 04:30 | 40.27 | 29.75
2018-10-16 05:00 | 40.9 | 30.65
2018-10-16 05:30 | 42.36 | 32.7
2018-10-16 06:00 | 44.15 | 35.08
2018-10-16 06:30 | 47.28 | 39.23
2018-10-16 07:00 | 50.01 | 42.53
2018-10-16 07:30 | 55.16 | 48.72
2018-10-16 08:00 | 56.26 | 49.68
2018-10-16 08:30 | 58.52 | 52.26
2018-10-16 09:00 | 59.75 | 53.75
2018-10-16 09:30 | 60.86 | 55.06
2018-10-16 10:00 | 62.01 | 56.37
2018-10-16 10:30 | 67.66 | 57.11
2018-10-16 11:00 | 67.49 | 54.09
2018-10-16 11:30 | 66.85 | 53.4
2018-10-16 12:00 | 67.25 | 53.99
2018-10-16 12:30 | 68.84 | 56
2018-10-16 13:00 | 68.49 | 55.56
2018-10-16 13:30 | 68.59 | 55.69
2018-10-16 14:00 | 70.46 | 58
2018-10-16 14:30 | 71.98 | 59.85
2018-10-16 15:00 | 69.56 | 56.87
2018-10-16 15:30 | 70.88 | 58.31
2018-10-16 16:00 | 71.91 | 59.18
2018-10-16 16:30 | 72.08 | 59.15
2018-10-16 17:00 | 70.65 | 57.09
2018-10-16 17:30 | 69.36 | 55.04
2018-10-16 18:00 | 62.01 | 53.61
2018-10-16 18:30 | 60.75 | 54.22
2018-10-16 19:00 | 60.95 | 54.43
2018-10-16 19:30 | 59.31 | 52.52
2018-10-16 20:00 | 57.01 | 49.78
2018-10-16 20:30 | 55.38 | 47.85
2018-10-16 21:00 | 53.75 | 46
2018-10-16 21:30 | 51.82 | 43.68
2018-10-16 22:00 | 50.43 | 41.95
2018-10-16 22:30 | 48.9 | 39.99
2018-10-16 23:00 | 49.04 | 40.12
2018-10-16 23:30 | 46.42 | 36.71
2018-10-17 | 45.13 | 35.13
2018-10-17 00:30 | 44.05 | 34.11
2018-10-17 01:00 | 43.16 | 32.79
2018-10-17 01:30 | 42.59 | 32.06
2018-10-17 02:00 | 41.54 | 31.08
2018-10-17 02:30 | 41.2 | 30.6
2018-10-17 03:00 | 41.04 | 30.35
2018-10-17 03:30 | 41.12 | 30.43
2018-10-17 04:00 | 41.21 | 30.55
2018-10-17 04:30 | 41.68 | 31.19
2018-10-17 05:00 | 42.44 | 32.31
2018-10-17 05:30 | 43.92 | 34.34
2018-10-17 06:00 | 45.34 | 36.24
2018-10-17 06:30 | 49.95 | 42.23
2018-10-17 07:00 | 54.08 | 47.35
2018-10-17 07:30 | 58.91 | 53.09
2018-10-17 08:00 | 61.41 | 55.47
2018-10-17 08:30 | 62.44 | 56.71
2018-10-17 09:00 | 58.95 | 54.54
2018-10-17 09:30 | 57.59 | 56.1
2018-10-17 10:00 | 57.53 | 56.05
2018-10-17 10:30 | 56.9 | 55.42
2018-10-17 11:00 | 58 | 56.59
2018-10-17 11:30 | 57.98 | 56.58
2018-10-17 12:00 | 59.09 | 57.72
2018-10-17 12:30 | 59 | 57.63
2018-10-17 13:00 | 58.67 | 57.29
2018-10-17 13:30 | 59.73 | 58.36
2018-10-17 14:00 | 63.66 | 62.34
2018-10-17 14:30 | 64.98 | 63.67
2018-10-17 15:00 | 64.56 | 63.22
2018-10-17 15:30 | 62.19 | 60.75
2018-10-17 16:00 | 60.62 | 59.08
2018-10-17 16:30 | 60.28 | 58.68
2018-10-17 17:00 | 58.09 | 56.37
2018-10-17 17:30 | 54.02 | 53.91
2018-10-17 18:00 | 53.05 | 53.02
2018-10-17 18:30 | 52.96 | 52.91
2018-10-17 19:00 | 52.53 | 52.46
2018-10-17 19:30 | 50.46 | 50.36
2018-10-17 20:00 | 48.69 | 48.53
2018-10-17 20:30 | 46.56 | 46.32
2018-10-17 21:00 | 45 | 44.75
2018-10-17 21:30 | 43.45 | 43.11
2018-10-17 22:00 | 41.79 | 41.34
2018-10-17 22:30 | 40.3 | 39.68
2018-10-17 23:00 | 40.28 | 39.61
2018-10-17 23:30 | 37.38 | 36.12
2018-10-18 | 35.19 | 32.76
2018-10-18 00:30 | 35.95 | 33.47
2018-10-18 01:00 | 34.69 | 32.04
2018-10-18 01:30 | 34.16 | 31.47
2018-10-18 02:00 | 33.53 | 30.79
2018-10-18 02:30 | 33.22 | 30.45
2018-10-18 03:00 | 32.93 | 30.13
2018-10-18 03:30 | 32.95 | 30.16
2018-10-18 04:00 | 32.98 | 30.19
2018-10-18 04:30 | 33.59 | 30.82
2018-10-18 05:00 | 34.35 | 31.54
2018-10-18 05:30 | 36.21 | 33.53
2018-10-18 06:00 | 38.52 | 36
2018-10-18 06:30 | 40.26 | 39.56
2018-10-18 07:00 | 42.87 | 42.74
2018-10-18 07:30 | 50.96 | 50.1
2018-10-18 08:00 | 54.14 | 52.58
2018-10-18 08:30 | 56.41 | 54.93
2018-10-18 09:00 | 55.84 | 54.61
2018-10-18 09:30 | 55.23 | 54.53
2018-10-18 10:00 | 55.6 | 54.99
2018-10-18 10:30 | 55.17 | 54.71
2018-10-18 11:00 | 55.52 | 55.17
2018-10-18 11:30 | 55.84 | 55.55
2018-10-18 12:00 | 55.79 | 55.54
2018-10-18 12:30 | 56.43 | 56.16
2018-10-18 13:00 | 56.01 | 55.71
2018-10-18 13:30 | 56.37 | 56.08
2018-10-18 14:00 | 56.61 | 56.31
2018-10-18 14:30 | 57.24 | 56.92
2018-10-18 15:00 | 56.96 | 56.57
2018-10-18 15:30 | 57.25 | 56.71
2018-10-18 16:00 | 58.61 | 57.97
2018-10-18 16:30 | 60.49 | 59.52
2018-10-18 17:00 | 58.2 | 56.66
2018-10-18 17:30 | 56.74 | 54.33
2018-10-18 18:00 | 56.81 | 53.84
2018-10-18 18:30 | 57.58 | 54.52
2018-10-18 19:00 | 58.39 | 55.36
2018-10-18 19:30 | 57.1 | 53.78
2018-10-18 20:00 | 55.33 | 51.66
2018-10-18 20:30 | 53.49 | 49.53
2018-10-18 21:00 | 49.25 | 47.58
2018-10-18 21:30 | 46.94 | 45.19
2018-10-18 22:00 | 44.86 | 43.03
2018-10-18 22:30 | 43.41 | 41.51
2018-10-18 23:00 | 43.26 | 41.37
2018-10-18 23:30 | 39.9 | 37.84
2018-10-19 | 37.91 | 35.73
2018-10-19 00:30 | 36.73 | 34.48
2018-10-19 01:00 | 35.7 | 33.18
2018-10-19 01:30 | 34.8 | 32.15
2018-10-19 02:00 | 34.16 | 31.47
2018-10-19 02:30 | 33.44 | 30.7
2018-10-19 03:00 | 32.95 | 30.17
2018-10-19 03:30 | 33 | 30.22
2018-10-19 04:00 | 33.11 | 30.34
2018-10-19 04:30 | 33.47 | 30.74
2018-10-19 05:00 | 34.35 | 31.69
2018-10-19 05:30 | 36.06 | 33.51
2018-10-19 06:00 | 37.81 | 35.38
2018-10-19 06:30 | 41.64 | 40.59
2018-10-19 07:00 | 45.46 | 44.89
2018-10-19 07:30 | 50.14 | 49.3
2018-10-19 08:00 | 54.09 | 53.26
2018-10-19 08:30 | 54.39 | 53.95
2018-10-19 09:00 | 53.04 | 52.44
2018-10-19 09:30 | 53.81 | 53.09
2018-10-19 10:00 | 54.22 | 53.38
2018-10-19 10:30 | 54.54 | 53.56
2018-10-19 11:00 | 55.29 | 54.19
2018-10-19 11:30 | 55.27 | 54.1
2018-10-19 12:00 | 55.62 | 54.45
2018-10-19 12:30 | 56.11 | 55.05
2018-10-19 13:00 | 55.56 | 54.55
2018-10-19 13:30 | 55.78 | 54.83
2018-10-19 14:00 | 55.86 | 55.03
2018-10-19 14:30 | 54.46 | 53.67
2018-10-19 15:00 | 53.95 | 53.31
2018-10-19 15:30 | 54.87 | 54.43
2018-10-19 16:00 | 55.39 | 55.02
2018-10-19 16:30 | 55.69 | 55.29
2018-10-19 17:00 | 54.57 | 54.14
2018-10-19 17:30 | 52.78 | 52.31
2018-10-19 18:00 | 51.56 | 51.04
2018-10-19 18:30 | 51.58 | 51.05
2018-10-19 19:00 | 52.21 | 51.69
2018-10-19 19:30 | 50.58 | 50.03
2018-10-19 20:00 | 48.91 | 48.34
2018-10-19 20:30 | 47.14 | 46.53
2018-10-19 21:00 | 45.23 | 44.71
2018-10-19 21:30 | 43.75 | 43.24
2018-10-19 22:00 | 42.34 | 41.82
2018-10-19 22:30 | 40.41 | 39.87
2018-10-19 23:00 | 40.17 | 39.64
2018-10-19 23:30 | 37.02 | 36.44
2018-10-20 | 35.35 | 34.75
2018-10-20 00:30 | 34.37 | 33.75
2018-10-20 01:00 | 32.76 | 31.99
2018-10-20 01:30 | 32.42 | 31.6
2018-10-20 02:00 | 31.98 | 31.18
2018-10-20 02:30 | 31.38 | 30.57
2018-10-20 03:00 | 30.75 | 29.93
2018-10-20 03:30 | 30.68 | 29.87
2018-10-20 04:00 | 30.65 | 29.83
2018-10-20 04:30 | 30.78 | 29.96
2018-10-20 05:00 | 30.81 | 29.99
2018-10-20 05:30 | 31.61 | 30.81
2018-10-20 06:00 | 31.91 | 31.12
2018-10-20 06:30 | 33.7 | 32.93
2018-10-20 07:00 | 34.68 | 33.92
2018-10-20 07:30 | 36.74 | 36
2018-10-20 08:00 | 37.53 | 36.82
2018-10-20 08:30 | 40.11 | 39.04
2018-10-20 09:00 | 40.78 | 40.27
2018-10-20 09:30 | 38.59 | 37.92
2018-10-20 10:00 | 40.7 | 40.01
2018-10-20 10:30 | 40.35 | 39.55
2018-10-20 11:00 | 39.95 | 39.16
2018-10-20 11:30 | 39.64 | 38.86
2018-10-20 12:00 | 39.15 | 38.38
2018-10-20 12:30 | 38.26 | 37.66
2018-10-20 13:00 | 37.41 | 36.87
2018-10-20 13:30 | 37.09 | 36.64
2018-10-20 14:00 | 37.52 | 37.11
2018-10-20 14:30 | 37.35 | 37.03
2018-10-20 15:00 | 37.9 | 37.63
2018-10-20 15:30 | 38.77 | 38.54
2018-10-20 16:00 | 40.2 | 40.02
2018-10-20 16:30 | 42.07 | 41.93
2018-10-20 17:00 | 42.29 | 42.19
2018-10-20 17:30 | 43.49 | 43.43
2018-10-20 18:00 | 44.69 | 44.64
2018-10-20 18:30 | 45.54 | 45.5
2018-10-20 19:00 | 46.3 | 46.24
2018-10-20 19:30 | 44.89 | 44.84
2018-10-20 20:00 | 43.29 | 43.25
2018-10-20 20:30 | 41.99 | 41.97
2018-10-20 21:00 | 40.76 | 40.75
2018-10-20 21:30 | 39.21 | 39.21
2018-10-20 22:00 | 38.22 | 38.22
2018-10-20 22:30 | 37.31 | 37.31
2018-10-20 23:00 | 37.4 | 37.39
2018-10-20 23:30 | 34.37 | 34.35
2018-10-21 | 32.76 | 32.7
2018-10-21 00:30 | 31.69 | 31.63
2018-10-21 01:00 | 30.36 | 30.32
2018-10-21 01:30 | 29.49 | 29.46
2018-10-21 02:00 | 29 | 28.99
2018-10-21 02:30 | 28.82 | 28.81
2018-10-21 03:00 | 28.35 | 28.34
2018-10-21 03:30 | 28.24 | 28.24
2018-10-21 04:00 | 28.06 | 28.05
2018-10-21 04:30 | 28.4 | 28.39
2018-10-21 05:00 | 28.66 | 28.64
2018-10-21 05:30 | 28.76 | 28.74
2018-10-21 06:00 | 28.73 | 28.73
2018-10-21 06:30 | 29.3 | 29.29
2018-10-21 07:00 | 29.52 | 29.49
2018-10-21 07:30 | 30.59 | 30.51
2018-10-21 08:00 | 32.98 | 32.82
2018-10-21 08:30 | 34.26 | 34.01
2018-10-21 09:00 | 34.78 | 34.41
2018-10-21 09:30 | 36.19 | 35.72
2018-10-21 10:00 | 36.83 | 36.21
2018-10-21 10:30 | 37.53 | 37.13
2018-10-21 11:00 | 36.82 | 36.6
2018-10-21 11:30 | 35.75 | 35.51
2018-10-21 12:00 | 35.95 | 35.68
2018-10-21 12:30 | 36.35 | 36.08
2018-10-21 13:00 | 35.72 | 35.46
2018-10-21 13:30 | 35.92 | 35.65
2018-10-21 14:00 | 36.09 | 35.88
2018-10-21 14:30 | 36.42 | 36.24
2018-10-21 15:00 | 37.32 | 37.16
2018-10-21 15:30 | 38.26 | 38.14
2018-10-21 16:00 | 39.59 | 39.5
2018-10-21 16:30 | 42.04 | 41.95
2018-10-21 17:00 | 42.72 | 42.65
2018-10-21 17:30 | 44.45 | 44.4
2018-10-21 18:00 | 46.25 | 46.19
2018-10-21 18:30 | 47.46 | 47.4
2018-10-21 19:00 | 48.69 | 48.6
2018-10-21 19:30 | 47.33 | 47.25
2018-10-21 20:00 | 45.27 | 45.22
2018-10-21 20:30 | 43.81 | 43.78
2018-10-21 21:00 | 42.3 | 42.28
2018-10-21 21:30 | 40.63 | 40.62
2018-10-21 22:00 | 39.33 | 39.32
2018-10-21 22:30 | 37.98 | 37.98
2018-10-21 23:00 | 37.93 | 37.93
2018-10-21 23:30 | 34.75 | 34.72
2018-10-22 | 32.9 | 32.8
2018-10-22 00:30 | 32.69 | 32.6
2018-10-22 01:00 | 31.46 | 31.38
2018-10-22 01:30 | 30.82 | 30.75
2018-10-22 02:00 | 30.7 | 30.62
2018-10-22 02:30 | 30.18 | 30.13
2018-10-22 03:00 | 29.95 | 29.9
2018-10-22 03:30 | 30.15 | 30.1
2018-10-22 04:00 | 29.92 | 29.88
2018-10-22 04:30 | 30.81 | 30.73
2018-10-22 05:00 | 32.29 | 32.16
2018-10-22 05:30 | 34.5 | 34.3
2018-10-22 06:00 | 36.95 | 36.68
2018-10-22 06:30 | 42.78 | 42.06
2018-10-22 07:00 | 45.84 | 45.3
2018-10-22 07:30 | 51.68 | 50.67
2018-10-22 08:00 | 55.82 | 55.13
2018-10-22 08:30 | 57.59 | 57.2
2018-10-22 09:00 | 59.08 | 58.63
2018-10-22 09:30 | 58.77 | 58.24
2018-10-22 10:00 | 56.44 | 55.81
2018-10-22 10:30 | 56.74 | 55.99
2018-10-22 11:00 | 57.08 | 56.12
2018-10-22 11:30 | 57.75 | 56.71
2018-10-22 12:00 | 58.77 | 57.62
2018-10-22 12:30 | 59.5 | 58.3
2018-10-22 13:00 | 59.38 | 58.19
2018-10-22 13:30 | 60.01 | 58.8
2018-10-22 14:00 | 60.96 | 59.69
2018-10-22 14:30 | 61.48 | 60.22
2018-10-22 15:00 | 62.11 | 60.94
2018-10-22 15:30 | 62.18 | 61.16
2018-10-22 16:00 | 62.21 | 61.42
2018-10-22 16:30 | 62.13 | 61.66
2018-10-22 17:00 | 62.08 | 61.74
2018-10-22 17:30 | 59.43 | 59.04
2018-10-22 18:00 | 57.16 | 56.73
2018-10-22 18:30 | 57.13 | 56.69
2018-10-22 19:00 | 57.65 | 57.21
2018-10-22 19:30 | 55.76 | 55.3
2018-10-22 20:00 | 53.54 | 53.04
2018-10-22 20:30 | 51.13 | 50.61
2018-10-22 21:00 | 48.6 | 48.1
2018-10-22 21:30 | 46.39 | 45.86
2018-10-22 22:00 | 44.65 | 44.08
2018-10-22 22:30 | 42.83 | 42.23
2018-10-22 23:00 | 38.56 | 37.9
2018-10-22 23:30 | 39.57 | 38.89
2018-10-23 | 37.95 | 37.24
2018-10-23 00:30 | 36.93 | 36.21
2018-10-23 01:00 | 35.35 | 34.65
2018-10-23 01:30 | 34.85 | 34.15
2018-10-23 02:00 | 34.47 | 33.75
2018-10-23 02:30 | 33.81 | 33.07
2018-10-23 03:00 | 33.43 | 32.68
2018-10-23 03:30 | 33.46 | 32.71
2018-10-23 04:00 | 33.11 | 32.34
2018-10-23 04:30 | 33.65 | 32.89
2018-10-23 05:00 | 35.16 | 34.45
2018-10-23 05:30 | 36.81 | 36.16
2018-10-23 06:00 | 39.11 | 38.51
2018-10-23 06:30 | 43.79 | 43.31
2018-10-23 07:00 | 42.04 | 41.31
2018-10-23 07:30 | 38.9 | 37.53
2018-10-23 08:00 | 45.41 | 44.79
2018-10-23 08:30 | 58.39 | 57.68
2018-10-23 09:00 | 59.25 | 58.33
2018-10-23 09:30 | 59.7 | 58.61
2018-10-23 10:00 | 59.1 | 57.98
2018-10-23 10:30 | 59.74 | 58.44
2018-10-23 11:00 | 59.86 | 58.5
2018-10-23 11:30 | 60.3 | 58.8
2018-10-23 12:00 | 61.02 | 59.37
2018-10-23 12:30 | 61.34 | 59.77
2018-10-23 13:00 | 60.47 | 59
2018-10-23 13:30 | 60.61 | 59.17
2018-10-23 14:00 | 61.82 | 60.25
2018-10-23 14:30 | 63.11 | 61.55
2018-10-23 15:00 | 62.49 | 61.16
2018-10-23 15:30 | 62.05 | 60.95
2018-10-23 16:00 | 62.44 | 61.68
2018-10-23 16:30 | 62.37 | 61.85
2018-10-23 17:00 | 60.97 | 60.61
2018-10-23 17:30 | 58.66 | 58.28
2018-10-23 18:00 | 57.35 | 56.93
2018-10-23 18:30 | 57.33 | 56.89
2018-10-23 19:00 | 58.52 | 58.09
2018-10-23 19:30 | 56.37 | 55.92
2018-10-23 20:00 | 54.09 | 53.61
2018-10-23 20:30 | 51.63 | 51.11
2018-10-23 21:00 | 49.13 | 48.6
2018-10-23 21:30 | 47.34 | 46.82
2018-10-23 22:00 | 45.27 | 44.71
2018-10-23 22:30 | 43.13 | 42.53
2018-10-23 23:00 | 42.81 | 42.2
2018-10-23 23:30 | 39.47 | 38.79
2018-10-24 | 37.18 | 36.54
2018-10-24 00:30 | 35.95 | 35.31
2018-10-24 01:00 | 34.41 | 33.73
2018-10-24 01:30 | 33.38 | 32.68
2018-10-24 02:00 | 32.76 | 32.06
2018-10-24 02:30 | 32.16 | 31.44
2018-10-24 03:00 | 32.01 | 31.23
2018-10-24 03:30 | 31.87 | 31.07
2018-10-24 04:00 | 31.62 | 30.82
2018-10-24 04:30 | 31.92 | 31.12
2018-10-24 05:00 | 33.02 | 32.24
2018-10-24 05:30 | 34.58 | 33.84
2018-10-24 06:00 | 36.54 | 35.82
2018-10-24 06:30 | 41.79 | 41.06
2018-10-24 07:00 | 45.88 | 45.25
2018-10-24 07:30 | 50.75 | 49.76
2018-10-24 08:00 | 53.72 | 52.88
2018-10-24 08:30 | 55.26 | 54.12
2018-10-24 09:00 | 55.67 | 54.95
2018-10-24 09:30 | 56.16 | 55.31
2018-10-24 10:00 | 56.18 | 55.22
2018-10-24 10:30 | 56.62 | 55.53
2018-10-24 11:00 | 57 | 55.76
2018-10-24 11:30 | 57.53 | 56.23
2018-10-24 12:00 | 58.09 | 56.78
2018-10-24 12:30 | 58.49 | 57.21
2018-10-24 13:00 | 58.9 | 57.64
2018-10-24 13:30 | 59.37 | 58.06
2018-10-24 14:00 | 59.72 | 58.44
2018-10-24 14:30 | 60.22 | 58.97
2018-10-24 15:00 | 60.7 | 59.53
2018-10-24 15:30 | 60.44 | 59.46
2018-10-24 16:00 | 61.7 | 60.9
2018-10-24 16:30 | 61.52 | 60.98
2018-10-24 17:00 | 60.38 | 60.01
2018-10-24 17:30 | 58.65 | 58.28
2018-10-24 18:00 | 56.68 | 56.25
2018-10-24 18:30 | 56.48 | 56.04
2018-10-24 19:00 | 58.45 | 58.03
2018-10-24 19:30 | 56.49 | 56.05
2018-10-24 20:00 | 54.26 | 53.79
2018-10-24 20:30 | 51.96 | 51.46
2018-10-24 21:00 | 49.96 | 49.43
2018-10-24 21:30 | 47.35 | 46.81
2018-10-24 22:00 | 45.2 | 44.65
2018-10-24 22:30 | 43.46 | 42.87
2018-10-24 23:00 | 43.13 | 42.53
2018-10-24 23:30 | 39.65 | 38.98
2018-10-25 | 33.13 | 32.34
2018-10-25 00:30 | 36.62 | 35.92
2018-10-25 01:00 | 35 | 34.33
2018-10-25 01:30 | 34.41 | 33.73
2018-10-25 02:00 | 33.73 | 33.04
2018-10-25 02:30 | 33 | 32.29
2018-10-25 03:00 | 32.63 | 31.9
2018-10-25 03:30 | 32.55 | 31.76
2018-10-25 04:00 | 32.12 | 31.33
2018-10-25 04:30 | 32.91 | 32.13
2018-10-25 05:00 | 33.78 | 33.02
2018-10-25 05:30 | 35.42 | 34.68
2018-10-25 06:00 | 37.47 | 36.76
2018-10-25 06:30 | 42.45 | 41.69
2018-10-25 07:00 | 45.72 | 45.05
2018-10-25 07:30 | 49.01 | 48.35
2018-10-25 08:00 | 53.11 | 52.63
2018-10-25 08:30 | 55.59 | 55.06
2018-10-25 09:00 | 56.45 | 55.61
2018-10-25 09:30 | 57.18 | 56.13
2018-10-25 10:00 | 57.22 | 56.15
2018-10-25 10:30 | 56.97 | 55.79
2018-10-25 11:00 | 57.23 | 55.96
2018-10-25 11:30 | 57.53 | 56.19
2018-10-25 12:00 | 57.76 | 56.39
2018-10-25 12:30 | 58.89 | 57.43
2018-10-25 13:00 | 57.86 | 56.48
2018-10-25 13:30 | 58.74 | 57.31
2018-10-25 14:00 | 59.36 | 57.96
2018-10-25 14:30 | 59.92 | 58.6
2018-10-25 15:00 | 59.77 | 58.57
2018-10-25 15:30 | 60.23 | 59.21
2018-10-25 16:00 | 61.06 | 60.2
2018-10-25 16:30 | 61.4 | 60.84
2018-10-25 17:00 | 60.24 | 59.86
2018-10-25 17:30 | 57.8 | 57.41
2018-10-25 18:00 | 57.43 | 57.01
2018-10-25 18:30 | 57.29 | 56.86
2018-10-25 19:00 | 58.18 | 57.77
2018-10-25 19:30 | 56.38 | 55.94
2018-10-25 20:00 | 54.17 | 53.7
2018-10-25 20:30 | 52.02 | 51.52
2018-10-25 21:00 | 50.65 | 50.13
2018-10-25 21:30 | 48.12 | 47.55
2018-10-25 22:00 | 45.69 | 45.12
2018-10-25 22:30 | 43.71 | 43.14
2018-10-25 23:00 | 43.42 | 42.83
2018-10-25 23:30 | 39.67 | 39
2018-10-26 | 37.65 | 36.99
2018-10-26 00:30 | 36.47 | 35.88
2018-10-26 01:00 | 35.07 | 34.47
2018-10-26 01:30 | 34.43 | 33.81
2018-10-26 02:00 | 33.47 | 32.84
2018-10-26 02:30 | 32.59 | 31.92
2018-10-26 03:00 | 32.18 | 31.5
2018-10-26 03:30 | 31.87 | 31.18
2018-10-26 04:00 | 31.73 | 31.03
2018-10-26 04:30 | 32.25 | 31.56
2018-10-26 05:00 | 33.16 | 32.5
2018-10-26 05:30 | 34.63 | 34.01
2018-10-26 06:00 | 36.67 | 36.09
2018-10-26 06:30 | 41.29 | 40.56
2018-10-26 07:00 | 45.59 | 44.27
2018-10-26 07:30 | 49.26 | 48.23
2018-10-26 08:00 | 51.06 | 50.62
2018-10-26 08:30 | 52.92 | 52.53
2018-10-26 09:00 | 53.77 | 53.4
2018-10-26 09:30 | 54.01 | 53.63
2018-10-26 10:00 | 54.52 | 54.14
2018-10-26 10:30 | 54.92 | 54.54
2018-10-26 11:00 | 55.16 | 54.77
2018-10-26 11:30 | 56.28 | 55.89
2018-10-26 12:00 | 56.16 | 55.77
2018-10-26 12:30 | 56.74 | 56.36
2018-10-26 13:00 | 57 | 56.62
2018-10-26 13:30 | 57.4 | 57.02
2018-10-26 14:00 | 57.74 | 57.38
2018-10-26 14:30 | 58.15 | 57.8
2018-10-26 15:00 | 58.53 | 58.18
2018-10-26 15:30 | 58.67 | 58.34
2018-10-26 16:00 | 59.21 | 58.89
2018-10-26 16:30 | 59.91 | 59.58
2018-10-26 17:00 | 58.91 | 58.35
2018-10-26 17:30 | 57.8 | 56.77
2018-10-26 18:00 | 56.56 | 55.06
2018-10-26 18:30 | 56.35 | 54.63
2018-10-26 19:00 | 56.67 | 54.94
2018-10-26 19:30 | 55.58 | 53.72
2018-10-26 20:00 | 52.25 | 50.88
2018-10-26 20:30 | 50.67 | 49.26
2018-10-26 21:00 | 49.13 | 47.56
2018-10-26 21:30 | 47.6 | 45.72
2018-10-26 22:00 | 46.37 | 44.22
2018-10-26 22:30 | 44.92 | 42.33
2018-10-26 23:00 | 44.68 | 41.57
2018-10-26 23:30 | 42.47 | 38.26
2018-10-27 | 40.71 | 36.3
2018-10-27 00:30 | 39.87 | 35.27
2018-10-27 01:00 | 39.09 | 34.32
2018-10-27 01:30 | 38.45 | 33.56
2018-10-27 02:00 | 37.67 | 32.68
2018-10-27 02:30 | 37.48 | 32.46
2018-10-27 03:00 | 36.89 | 31.8
2018-10-27 03:30 | 36.78 | 31.66
2018-10-27 04:00 | 36.5 | 31.34
2018-10-27 04:30 | 37.09 | 31.99
2018-10-27 05:00 | 37.25 | 32.17
2018-10-27 05:30 | 37.36 | 32.31
2018-10-27 06:00 | 37.66 | 32.66
2018-10-27 06:30 | 39.5 | 34.73
2018-10-27 07:00 | 40.33 | 35.62
2018-10-27 07:30 | 40.55 | 35.86
2018-10-27 08:00 | 35.96 | 30.6
2018-10-27 08:30 | 31.08 | 28.44
2018-10-27 09:00 | 30.9 | 30.32
2018-10-27 09:30 | 31.79 | 31.11
2018-10-27 10:00 | 32.55 | 31.72
2018-10-27 10:30 | 32.99 | 32.06
2018-10-27 11:00 | 33.19 | 32.22
2018-10-27 11:30 | 36.34 | 34.7
2018-10-27 12:00 | 46.21 | 44.45
2018-10-27 12:30 | 48.66 | 46.99
2018-10-27 13:00 | 48.07 | 46.4
2018-10-27 13:30 | 48.64 | 46.98
2018-10-27 14:00 | 49.21 | 47.59
2018-10-27 14:30 | 49.67 | 48.06
2018-10-27 15:00 | 50.71 | 49.15
2018-10-27 15:30 | 51.2 | 49.68
2018-10-27 16:00 | 52.55 | 51.09
2018-10-27 16:30 | 54.22 | 52.82
2018-10-27 17:00 | 54.61 | 53.23
2018-10-27 17:30 | 55.54 | 54.2
2018-10-27 18:00 | 56.14 | 54.83
2018-10-27 18:30 | 56.77 | 55.47
2018-10-27 19:00 | 57.5 | 56.21
2018-10-27 19:30 | 56.47 | 55.16
2018-10-27 20:00 | 54.72 | 53.36
2018-10-27 20:30 | 52.96 | 51.54
2018-10-27 21:00 | 51.82 | 50.26
2018-10-27 21:30 | 50.31 | 48.54
2018-10-27 22:00 | 47.7 | 47.48
2018-10-27 22:30 | 46.35 | 46.25
2018-10-27 23:00 | 45.87 | 45.8
2018-10-27 23:30 | 42.09 | 42.06
2018-10-28 | 40.13 | 40.12
2018-10-28 00:30 | 38.95 | 38.94
2018-10-28 01:00 | 37.45 | 37.45
2018-10-28 01:30 | 36.47 | 36.46
2018-10-28 02:00 | 35.77 | 35.76
2018-10-28 02:30 | 35.25 | 35.21
2018-10-28 03:00 | 34.79 | 34.66
2018-10-28 03:30 | 34.53 | 34.4
2018-10-28 04:00 | 34.02 | 33.89
2018-10-28 04:30 | 34.3 | 34.15
2018-10-28 05:00 | 34.48 | 34.34
2018-10-28 05:30 | 34.15 | 34.02
2018-10-28 06:00 | 33.66 | 33.56
2018-10-28 06:30 | 34.82 | 34.67
2018-10-28 07:00 | 35.14 | 34.94
2018-10-28 07:30 | 36.66 | 36.31
2018-10-28 08:00 | 38.25 | 37.69
2018-10-28 08:30 | 39.86 | 39.12
2018-10-28 09:00 | 40.69 | 39.7
2018-10-28 09:30 | 41.03 | 40.48
2018-10-28 10:00 | 41.81 | 41.37
2018-10-28 10:30 | 43.07 | 42.46
2018-10-28 11:00 | 43.56 | 42.88
2018-10-28 11:30 | 43.46 | 42.85
2018-10-28 12:00 | 43.87 | 43.24
2018-10-28 12:30 | 44.68 | 44.06
2018-10-28 13:00 | 45.14 | 44.5
2018-10-28 13:30 | 45.56 | 44.92
2018-10-28 14:00 | 46.45 | 45.84
2018-10-28 14:30 | 47.17 | 46.62
2018-10-28 15:00 | 47.99 | 47.49
2018-10-28 15:30 | 49.06 | 48.61
2018-10-28 16:00 | 50.53 | 50.11
2018-10-28 16:30 | 52.83 | 52.43
2018-10-28 17:00 | 53.17 | 52.84
2018-10-28 17:30 | 54.38 | 54.11
2018-10-28 18:00 | 54.9 | 54.69
2018-10-28 18:30 | 56 | 55.79
2018-10-28 19:00 | 56.7 | 56.44
2018-10-28 19:30 | 54.86 | 54.64
2018-10-28 20:00 | 53.27 | 53.08
2018-10-28 20:30 | 51.95 | 51.8
2018-10-28 21:00 | 48.16 | 48.06
2018-10-28 21:30 | 45.81 | 45.74
2018-10-28 22:00 | 43.42 | 43.39
2018-10-28 22:30 | 42.81 | 42.8
2018-10-28 23:00 | 42.22 | 42.21
2018-10-28 23:30 | 38.21 | 38.21
2018-10-29 | 37.11 | 37.11
2018-10-29 00:30 | 36.8 | 36.8
2018-10-29 01:00 | 34.95 | 34.86
2018-10-29 01:30 | 35.48 | 35.33
2018-10-29 02:00 | 33.76 | 33.61
2018-10-29 02:30 | 33.89 | 33.77
2018-10-29 03:00 | 33.53 | 33.43
2018-10-29 03:30 | 33.48 | 33.37
2018-10-29 04:00 | 33.72 | 33.6
2018-10-29 04:30 | 34.47 | 34.33
2018-10-29 05:00 | 35.88 | 35.69
2018-10-29 05:30 | 37.93 | 37.65
2018-10-29 06:00 | 40.93 | 40.48
2018-10-29 06:30 | 46.81 | 45.81
2018-10-29 07:00 | 51.45 | 50.58
2018-10-29 07:30 | 56.44 | 55.84
2018-10-29 08:00 | 61.6 | 61.13
2018-10-29 08:30 | 63.53 | 62.77
2018-10-29 09:00 | 64.86 | 63.62
2018-10-29 09:30 | 65.04 | 63.77
2018-10-29 10:00 | 65.35 | 64.04
2018-10-29 10:30 | 64.78 | 63.36
2018-10-29 11:00 | 65.95 | 64.35
2018-10-29 11:30 | 66.94 | 65.27
2018-10-29 12:00 | 66.94 | 65.22
2018-10-29 12:30 | 68.16 | 66.46
2018-10-29 13:00 | 67.33 | 65.61
2018-10-29 13:30 | 68.36 | 66.65
2018-10-29 14:00 | 68.64 | 66.92
2018-10-29 14:30 | 69.68 | 67.98
2018-10-29 15:00 | 70.08 | 68.51
2018-10-29 15:30 | 69.63 | 68.27
2018-10-29 16:00 | 69.67 | 68.51
2018-10-29 16:30 | 69.23 | 68.05
2018-10-29 17:00 | 69.36 | 68.14
2018-10-29 17:30 | 65.97 | 64.59
2018-10-29 18:00 | 63.72 | 62.21
2018-10-29 18:30 | 63.34 | 61.79
2018-10-29 19:00 | 64.05 | 62.53
2018-10-29 19:30 | 62.91 | 61.33
2018-10-29 20:00 | 60.09 | 58.41
2018-10-29 20:30 | 58.21 | 56.45
2018-10-29 21:00 | 55.94 | 54.08
2018-10-29 21:30 | 53.42 | 51.43
2018-10-29 22:00 | 51.3 | 49.37
2018-10-29 22:30 | 46.54 | 46.28
2018-10-29 23:00 | 46.43 | 46.13
2018-10-29 23:30 | 43.25 | 42.98
2018-10-30 | 41.8 | 41.73
2018-10-30 00:30 | 39.99 | 39.94
2018-10-30 01:00 | 37.97 | 37.96
2018-10-30 01:30 | 37.02 | 37.01
2018-10-30 02:00 | 36.66 | 36.66
2018-10-30 02:30 | 35.53 | 35.47
2018-10-30 03:00 | 35.6 | 35.36
2018-10-30 03:30 | 35.38 | 35.15
2018-10-30 04:00 | 34.94 | 34.72
2018-10-30 04:30 | 36.13 | 35.91
2018-10-30 05:00 | 38.21 | 37.94
2018-10-30 05:30 | 39.88 | 39.44
2018-10-30 06:00 | 41.96 | 41.39
2018-10-30 06:30 | 48.02 | 46.95
2018-10-30 07:00 | 52.13 | 51.3
2018-10-30 07:30 | 59.4 | 57.95
2018-10-30 08:00 | 62.17 | 60.8
2018-10-30 08:30 | 63.55 | 62.26
2018-10-30 09:00 | 64.86 | 63.62
2018-10-30 09:30 | 65.93 | 64.58
2018-10-30 10:00 | 64.13 | 62.67
2018-10-30 10:30 | 64.01 | 62.38
2018-10-30 11:00 | 67.24 | 64.88
2018-10-30 11:30 | 67.78 | 64.98
2018-10-30 12:00 | 67.6 | 64.79
2018-10-30 12:30 | 68.05 | 65.24
2018-10-30 13:00 | 67.19 | 64.33
2018-10-30 13:30 | 67.61 | 64.78
2018-10-30 14:00 | 68.6 | 65.82
2018-10-30 14:30 | 69.1 | 66.35
2018-10-30 15:00 | 70.04 | 67.3
2018-10-30 15:30 | 70.04 | 67.26
2018-10-30 16:00 | 69.54 | 66.66
2018-10-30 16:30 | 70.29 | 67.32
2018-10-30 17:00 | 68.76 | 65.65
2018-10-30 17:30 | 67.15 | 63.83
2018-10-30 18:00 | 65.94 | 62.46
2018-10-30 18:30 | 62.62 | 62.24
2018-10-30 19:00 | 63.75 | 63.38
2018-10-30 19:30 | 61.88 | 61.49
2018-10-30 20:00 | 59.17 | 58.75
2018-10-30 20:30 | 57.49 | 57.04
2018-10-30 21:00 | 54.5 | 54.02
2018-10-30 21:30 | 51.75 | 51.24
2018-10-30 22:00 | 49.49 | 48.94
2018-10-30 22:30 | 46.87 | 46.26
2018-10-30 23:00 | 47.8 | 47.21
2018-10-30 23:30 | 43.21 | 42.62
2018-10-31 | 41.83 | 41.21
2018-10-31 00:30 | 39.44 | 38.76
2018-10-31 01:00 | 39.17 | 38.49
2018-10-31 01:30 | 38.55 | 37.85
2018-10-31 02:00 | 37.44 | 36.71
2018-10-31 02:30 | 36.08 | 35.33
2018-10-31 03:00 | 36.21 | 35.61
2018-10-31 03:30 | 36.23 | 35.65
2018-10-31 04:00 | 35.26 | 34.65
2018-10-31 04:30 | 35.47 | 34.87
2018-10-31 05:00 | 38.2 | 37.66
2018-10-31 05:30 | 40.75 | 40.19
2018-10-31 06:00 | 42.99 | 42.33
2018-10-31 06:30 | 49.28 | 48.14
2018-10-31 07:00 | 52.76 | 52.3
2018-10-31 07:30 | 57.65 | 57.25
2018-10-31 08:00 | 59.65 | 59.23
2018-10-31 08:30 | 60.89 | 60.09
2018-10-31 09:00 | 65.84 | 64.92
2018-10-31 09:30 | 63.5 | 62.48
2018-10-31 10:00 | 61.38 | 60.2
2018-10-31 10:30 | 64.57 | 63.22
2018-10-31 11:00 | 63.78 | 61.42
2018-10-31 11:30 | 64.02 | 60.91
2018-10-31 12:00 | 65.89 | 62.89
2018-10-31 12:30 | 68.11 | 65.22
2018-10-31 13:00 | 66.64 | 63.65
2018-10-31 13:30 | 64.88 | 61.78
2018-10-31 14:00 | 64.47 | 61.38
2018-10-31 14:30 | 65.08 | 62.03
2018-10-31 15:00 | 65.71 | 62.65
2018-10-31 15:30 | 66.21 | 63.14
2018-10-31 16:00 | 67.95 | 64.92
2018-10-31 16:30 | 69.52 | 66.51
2018-10-31 17:00 | 66.92 | 63.66
2018-10-31 17:30 | 65.5 | 62.03
2018-10-31 18:00 | 60.5 | 59.9
2018-10-31 18:30 | 60.3 | 59.91
2018-10-31 19:00 | 61.41 | 61.03
2018-10-31 19:30 | 60.69 | 60.29
2018-10-31 20:00 | 58.59 | 58.17
2018-10-31 20:30 | 55.85 | 55.4
2018-10-31 21:00 | 55.12 | 54.66
2018-10-31 21:30 | 52.65 | 52.14
2018-10-31 22:00 | 49.22 | 48.67
2018-10-31 22:30 | 47.55 | 46.97
2018-10-31 23:00 | 47.92 | 47.35
2018-10-31 23:30 | 44.81 | 44.23
2018-11-01 | 42.77 | 42.18
2018-11-01 00:30 | 41.04 | 40.49
2018-11-01 01:00 | 38.98 | 38.38
2018-11-01 01:30 | 37.9 | 37.29
2018-11-01 02:00 | 37.13 | 36.5
2018-11-01 02:30 | 37.42 | 36.78
2018-11-01 03:00 | 36.97 | 36.32
2018-11-01 03:30 | 36.52 | 35.86
2018-11-01 04:00 | 37.01 | 36.35
2018-11-01 04:30 | 37.79 | 37.15
2018-11-01 05:00 | 38.4 | 37.79
2018-11-01 05:30 | 40.58 | 40.01
2018-11-01 06:00 | 42.13 | 41.6
2018-11-01 06:30 | 47.67 | 47.21
2018-11-01 07:00 | 52.73 | 52.31
2018-11-01 07:30 | 58.05 | 57.65
2018-11-01 08:00 | 61.57 | 60.96
2018-11-01 08:30 | 63.08 | 62.22
2018-11-01 09:00 | 62.83 | 61.74
2018-11-01 09:30 | 63.7 | 62.45
2018-11-01 10:00 | 63.39 | 62.05
2018-11-01 10:30 | 65.06 | 63.58
2018-11-01 11:00 | 61.77 | 60.02
2018-11-01 11:30 | 65.31 | 63.27
2018-11-01 12:00 | 66.49 | 63.61
2018-11-01 12:30 | 69.04 | 66.27
2018-11-01 13:00 | 66.05 | 63.1
2018-11-01 13:30 | 67.53 | 64.66
2018-11-01 14:00 | 69.93 | 67.18
2018-11-01 14:30 | 67.95 | 65.09
2018-11-01 15:00 | 69.07 | 66.23
2018-11-01 15:30 | 68.36 | 65.43
2018-11-01 16:00 | 68.54 | 65.55
2018-11-01 16:30 | 68.2 | 65.14
2018-11-01 17:00 | 66.99 | 63.77
2018-11-01 17:30 | 63.94 | 60.39
2018-11-01 18:00 | 63.55 | 59.9
2018-11-01 18:30 | 63.55 | 59.86
2018-11-01 19:00 | 63.99 | 60.33
2018-11-01 19:30 | 62.47 | 58.68
2018-11-01 20:00 | 60.07 | 56.68
2018-11-01 20:30 | 54.87 | 54.4
2018-11-01 21:00 | 53.43 | 52.94
2018-11-01 21:30 | 50.38 | 49.85
2018-11-01 22:00 | 47.36 | 46.77
2018-11-01 22:30 | 45.8 | 45.18
2018-11-01 23:00 | 44.65 | 44
2018-11-01 23:30 | 41.21 | 40.54
2018-11-02 | 40.06 | 39.39
2018-11-02 00:30 | 38.95 | 38.26
2018-11-02 01:00 | 37.23 | 36.58
2018-11-02 01:30 | 36.72 | 36.06
2018-11-02 02:00 | 34.97 | 34.27
2018-11-02 02:30 | 34.67 | 34.03
2018-11-02 03:00 | 34.08 | 33.45
2018-11-02 03:30 | 33.81 | 33.17
2018-11-02 04:00 | 34.06 | 33.42
2018-11-02 04:30 | 35.5 | 34.89
2018-11-02 05:00 | 35.5 | 34.9
2018-11-02 05:30 | 37.5 | 36.95
2018-11-02 06:00 | 39.88 | 39.34
2018-11-02 06:30 | 45.36 | 44.51
2018-11-02 07:00 | 49.66 | 48.9
2018-11-02 07:30 | 52.98 | 52.15
2018-11-02 08:00 | 53.69 | 53.31
2018-11-02 08:30 | 55.6 | 55.05
2018-11-02 09:00 | 56.05 | 55.33
2018-11-02 09:30 | 55.78 | 54.94
2018-11-02 10:00 | 55.8 | 54.86
2018-11-02 10:30 | 56.92 | 55.84
2018-11-02 11:00 | 58.84 | 57.65
2018-11-02 11:30 | 59.29 | 58
2018-11-02 12:00 | 60.59 | 59.35
2018-11-02 12:30 | 59.01 | 57.84
2018-11-02 13:00 | 59.71 | 58.67
2018-11-02 13:30 | 58.04 | 57
2018-11-02 14:00 | 55.49 | 54.35
2018-11-02 14:30 | 59.19 | 58.39
2018-11-02 15:00 | 58.41 | 57.72
2018-11-02 15:30 | 58.55 | 58.04
2018-11-02 16:00 | 58.41 | 58.04
2018-11-02 16:30 | 58.28 | 57.93
2018-11-02 17:00 | 56.95 | 56.56
2018-11-02 17:30 | 55.51 | 55.08
2018-11-02 18:00 | 55.04 | 54.59
2018-11-02 18:30 | 53.97 | 53.49
2018-11-02 19:00 | 55.78 | 55.33
2018-11-02 19:30 | 54.19 | 53.71
2018-11-02 20:00 | 51.79 | 51.29
2018-11-02 20:30 | 50.15 | 49.62
2018-11-02 21:00 | 47.97 | 47.39
2018-11-02 21:30 | 46.37 | 45.77
2018-11-02 22:00 | 45.28 | 44.65
2018-11-02 22:30 | 43.67 | 43.01
2018-11-02 23:00 | 43.33 | 42.68
2018-11-02 23:30 | 40.2 | 39.51
2018-11-03 | 38.11 | 37.36
2018-11-03 00:30 | 36.03 | 35.46
2018-11-03 01:00 | 34.96 | 34.37
2018-11-03 01:30 | 33.99 | 33.28
2018-11-03 02:00 | 33.32 | 32.55
2018-11-03 02:30 | 33.2 | 32.43
2018-11-03 03:00 | 32.36 | 31.58
2018-11-03 03:30 | 32.23 | 31.44
2018-11-03 04:00 | 32.96 | 32.2
2018-11-03 04:30 | 32.47 | 31.69
2018-11-03 05:00 | 32.55 | 31.77
2018-11-03 05:30 | 33.23 | 32.47
2018-11-03 06:00 | 34.2 | 33.46
2018-11-03 06:30 | 36.19 | 35.47
2018-11-03 07:00 | 36.77 | 36.05
2018-11-03 07:30 | 38.1 | 37.38
2018-11-03 08:00 | 40.81 | 40.01
2018-11-03 08:30 | 43.59 | 42.48
2018-11-03 09:00 | 42.7 | 41.99
2018-11-03 09:30 | 41.36 | 40.69
2018-11-03 10:00 | 41.77 | 41.04
2018-11-03 10:30 | 41.51 | 40.69
2018-11-03 11:00 | 42.64 | 41.69
2018-11-03 11:30 | 41.49 | 40.5
2018-11-03 12:00 | 41.77 | 40.86
2018-11-03 12:30 | 40.7 | 39.96
2018-11-03 13:00 | 39.97 | 39.24
2018-11-03 13:30 | 39.44 | 38.73
2018-11-03 14:00 | 39.94 | 39.25
2018-11-03 14:30 | 41.17 | 40.52
2018-11-03 15:00 | 42.31 | 41.68
2018-11-03 15:30 | 43.53 | 42.93
2018-11-03 16:00 | 44.12 | 43.53
2018-11-03 16:30 | 47.27 | 46.73
2018-11-03 17:00 | 47.8 | 47.28
2018-11-03 17:30 | 48.82 | 48.31
2018-11-03 18:00 | 49.71 | 49.22
2018-11-03 18:30 | 49.67 | 49.18
2018-11-03 19:00 | 50.29 | 49.8
2018-11-03 19:30 | 49.12 | 48.63
2018-11-03 20:00 | 47.33 | 46.82
2018-11-03 20:30 | 45.66 | 45.13
2018-11-03 21:00 | 44.79 | 44.26
2018-11-03 21:30 | 44.12 | 43.59
2018-11-03 22:00 | 42.78 | 42.23
2018-11-03 22:30 | 41.97 | 41.41
2018-11-03 23:00 | 41.29 | 40.73
2018-11-03 23:30 | 38.47 | 37.88
2018-11-04 | 36.2 | 35.57
2018-11-04 00:30 | 35.22 | 34.53
2018-11-04 01:00 | 33.91 | 33.16
2018-11-04 01:30 | 33.48 | 32.73
2018-11-04 02:00 | 33.04 | 32.28
2018-11-04 02:30 | 32.59 | 31.82
2018-11-04 03:00 | 32.44 | 31.67
2018-11-04 03:30 | 31.09 | 30.27
2018-11-04 04:00 | 30.34 | 29.5
2018-11-04 04:30 | 32 | 31.21
2018-11-04 05:00 | 31.86 | 31.07
2018-11-04 05:30 | 30.87 | 30.08
2018-11-04 06:00 | 30.91 | 30.12
2018-11-04 06:30 | 31.91 | 31.14
2018-11-04 07:00 | 32.77 | 32.01
2018-11-04 07:30 | 33.03 | 32.25
2018-11-04 08:00 | 33.92 | 33.14
2018-11-04 08:30 | 35.43 | 34.67
2018-11-04 09:00 | 37.08 | 36.34
2018-11-04 09:30 | 36.94 | 36.13
2018-11-04 10:00 | 37.62 | 36.73
2018-11-04 10:30 | 37.37 | 36.67
2018-11-04 11:00 | 38.01 | 37.32
2018-11-04 11:30 | 38.79 | 38.11
2018-11-04 12:00 | 37.97 | 37.27
2018-11-04 12:30 | 39.04 | 38.36
2018-11-04 13:00 | 40.39 | 39.74
2018-11-04 13:30 | 40.59 | 39.94
2018-11-04 14:00 | 42.56 | 41.94
2018-11-04 14:30 | 42.7 | 42.09
2018-11-04 15:00 | 43.96 | 43.37
2018-11-04 15:30 | 44.11 | 43.54
2018-11-04 16:00 | 46.3 | 45.76
2018-11-04 16:30 | 49.34 | 48.84
2018-11-04 17:00 | 50.25 | 49.76
2018-11-04 17:30 | 52.17 | 51.7
2018-11-04 18:00 | 54.06 | 53.61
2018-11-04 18:30 | 55.08 | 54.67
2018-11-04 19:00 | 56.07 | 55.71
2018-11-04 19:30 | 54.73 | 54.35
2018-11-04 20:00 | 52.53 | 52.12
2018-11-04 20:30 | 50.07 | 49.63
2018-11-04 21:00 | 48.23 | 47.77
2018-11-04 21:30 | 46.12 | 45.63
2018-11-04 22:00 | 44.14 | 43.6
2018-11-04 22:30 | 42.72 | 42.16
2018-11-04 23:00 | 42.59 | 42.01
2018-11-04 23:30 | 39.09 | 38.49
2018-11-05 | 37.36 | 36.76
2018-11-05 00:30 | 36.8 | 36.19
2018-11-05 01:00 | 34.02 | 33.35
2018-11-05 01:30 | 33.24 | 32.55
2018-11-05 02:00 | 33.19 | 32.49
2018-11-05 02:30 | 33.64 | 32.95
2018-11-05 03:00 | 33.15 | 32.45
2018-11-05 03:30 | 33.13 | 32.43
2018-11-05 04:00 | 33.1 | 32.41
2018-11-05 04:30 | 33.26 | 32.57
2018-11-05 05:00 | 34.33 | 33.68
2018-11-05 05:30 | 37.08 | 36.5
2018-11-05 06:00 | 38.65 | 38.1
2018-11-05 06:30 | 43.85 | 43.09
2018-11-05 07:00 | 47.69 | 46.93
2018-11-05 07:30 | 53.52 | 52.6
2018-11-05 08:00 | 56.31 | 55.95
2018-11-05 08:30 | 58.93 | 58.38
2018-11-05 09:00 | 59.22 | 58.39
2018-11-05 09:30 | 60.87 | 59.97
2018-11-05 10:00 | 60.63 | 59.69
2018-11-05 10:30 | 60.4 | 59.33
2018-11-05 11:00 | 60.73 | 59.43
2018-11-05 11:30 | 61.75 | 60.3
2018-11-05 12:00 | 61.26 | 59.72
2018-11-05 12:30 | 62.26 | 60.85
2018-11-05 13:00 | 62.04 | 60.67
2018-11-05 13:30 | 62.97 | 61.6
2018-11-05 14:00 | 63.68 | 62.19
2018-11-05 14:30 | 64.41 | 62.97
2018-11-05 15:00 | 63.96 | 62.61
2018-11-05 15:30 | 64.16 | 62.87
2018-11-05 16:00 | 64.9 | 63.62
2018-11-05 16:30 | 66.42 | 65.12
2018-11-05 17:00 | 66.22 | 64.86
2018-11-05 17:30 | 64.48 | 63.01
2018-11-05 18:00 | 62.69 | 61.11
2018-11-05 18:30 | 62.15 | 60.51
2018-11-05 19:00 | 63.47 | 61.89
2018-11-05 19:30 | 61.16 | 59.49
2018-11-05 20:00 | 58.68 | 56.91
2018-11-05 20:30 | 55.18 | 54.21
2018-11-05 21:00 | 53.76 | 53.27
2018-11-05 21:30 | 51.42 | 50.89
2018-11-05 22:00 | 49.43 | 48.87
2018-11-05 22:30 | 46.75 | 46.14
2018-11-05 23:00 | 46.18 | 45.55
2018-11-05 23:30 | 42.52 | 41.82
2018-11-06 | 39.32 | 38.58
2018-11-06 00:30 | 37.6 | 36.97
2018-11-06 01:00 | 36.32 | 35.75
2018-11-06 01:30 | 35.53 | 34.95
2018-11-06 02:00 | 34.62 | 34.02
2018-11-06 02:30 | 33.86 | 33.18
2018-11-06 03:00 | 33.73 | 33.05
2018-11-06 03:30 | 33.91 | 33.23
2018-11-06 04:00 | 34.01 | 33.27
2018-11-06 04:30 | 35.84 | 35.12
2018-11-06 05:00 | 36.02 | 35.31
2018-11-06 05:30 | 37.65 | 36.96
2018-11-06 06:00 | 39.16 | 38.49
2018-11-06 06:30 | 44.2 | 43.31
2018-11-06 07:00 | 48.1 | 47.44
2018-11-06 07:30 | 54.87 | 53.76
2018-11-06 08:00 | 58.13 | 56.61
2018-11-06 08:30 | 59.39 | 57.92
2018-11-06 09:00 | 60.49 | 59.1
2018-11-06 09:30 | 61.13 | 59.78
2018-11-06 10:00 | 61.3 | 59.98
2018-11-06 10:30 | 60.18 | 58.76
2018-11-06 11:00 | 63.14 | 61.79
2018-11-06 11:30 | 63.09 | 61.66
2018-11-06 12:00 | 62.39 | 60.87
2018-11-06 12:30 | 61.76 | 60.25
2018-11-06 13:00 | 61.22 | 59.83
2018-11-06 13:30 | 61.1 | 59.7
2018-11-06 14:00 | 61.3 | 59.95
2018-11-06 14:30 | 61.49 | 60.16
2018-11-06 15:00 | 63.31 | 62.05
2018-11-06 15:30 | 64.56 | 63.3
2018-11-06 16:00 | 64.38 | 63.09
2018-11-06 16:30 | 64.97 | 63.64
2018-11-06 17:00 | 64 | 62.6
2018-11-06 17:30 | 62.2 | 60.68
2018-11-06 18:00 | 61.18 | 59.58
2018-11-06 18:30 | 48.05 | 46
2018-11-06 19:00 | 59.8 | 58.14
2018-11-06 19:30 | 61.12 | 59.48
2018-11-06 20:00 | 58.53 | 56.78
2018-11-06 20:30 | 56.82 | 55
2018-11-06 21:00 | 47.58 | 45.37
2018-11-06 21:30 | 49.06 | 48.73
2018-11-06 22:00 | 47.55 | 47.35
2018-11-06 22:30 | 44.69 | 44.36
2018-11-06 23:00 | 44.19 | 43.81
2018-11-06 23:30 | 40.48 | 39.89
2018-11-07 | 38.84 | 38.12
2018-11-07 00:30 | 37.3 | 36.71
2018-11-07 01:00 | 35.88 | 35.64
2018-11-07 01:30 | 36.01 | 35.75
2018-11-07 02:00 | 34.94 | 34.65
2018-11-07 02:30 | 34.17 | 33.91
2018-11-07 03:00 | 33.92 | 33.92
2018-11-07 03:30 | 33.62 | 33.61
2018-11-07 04:00 | 33.29 | 33.25
2018-11-07 04:30 | 33.83 | 33.66
2018-11-07 05:00 | 34.71 | 34.51
2018-11-07 05:30 | 36.76 | 36.52
2018-11-07 06:00 | 39.83 | 39.43
2018-11-07 06:30 | 46.17 | 45.15
2018-11-07 07:00 | 50.39 | 49.68
2018-11-07 07:30 | 54.77 | 54.35
2018-11-07 08:00 | 56.61 | 56.27
2018-11-07 08:30 | 58.16 | 57.61
2018-11-07 09:00 | 59.87 | 59.52
2018-11-07 09:30 | 60.7 | 60.42
2018-11-07 10:00 | 60.13 | 59.92
2018-11-07 10:30 | 60.21 | 60.05
2018-11-07 11:00 | 60.12 | 60.03
2018-11-07 11:30 | 60.39 | 60.28
2018-11-07 12:00 | 61.06 | 61
2018-11-07 12:30 | 62.05 | 61.98
2018-11-07 13:00 | 62.37 | 62.3
2018-11-07 13:30 | 62.93 | 62.87
2018-11-07 14:00 | 58.47 | 58.42
2018-11-07 14:30 | 64.11 | 64.05
2018-11-07 15:00 | 65.08 | 65.02
2018-11-07 15:30 | 65.74 | 65.64
2018-11-07 16:00 | 67.06 | 66.88
2018-11-07 16:30 | 68.26 | 67.96
2018-11-07 17:00 | 66.85 | 66.24
2018-11-07 17:30 | 64.74 | 63.54
2018-11-07 18:00 | 63.27 | 61.41
2018-11-07 18:30 | 62.42 | 61.08
2018-11-07 19:00 | 62.54 | 62.16
2018-11-07 19:30 | 61.24 | 60.79
2018-11-07 20:00 | 59.39 | 58.85
2018-11-07 20:30 | 56.95 | 56.23
2018-11-07 21:00 | 54.64 | 53.7
2018-11-07 21:30 | 52.49 | 51.28
2018-11-07 22:00 | 50.57 | 49.07
2018-11-07 22:30 | 48.41 | 47
2018-11-07 23:00 | 46.61 | 46.46
2018-11-07 23:30 | 42.38 | 42.28
2018-11-08 | 40.39 | 40.32
2018-11-08 00:30 | 39.47 | 39.41
2018-11-08 01:00 | 37.9 | 37.87
2018-11-08 01:30 | 38.01 | 37.99
2018-11-08 02:00 | 37.71 | 37.69
2018-11-08 02:30 | 36.58 | 36.57
2018-11-08 03:00 | 36.4 | 36.14
2018-11-08 03:30 | 36.4 | 36.14
2018-11-08 04:00 | 36.06 | 35.81
2018-11-08 04:30 | 36.45 | 36.19
2018-11-08 05:00 | 37.69 | 37.39
2018-11-08 05:30 | 38.98 | 38.62
2018-11-08 06:00 | 41.31 | 40.82
2018-11-08 06:30 | 47.26 | 46.25
2018-11-08 07:00 | 51.45 | 50.91
2018-11-08 07:30 | 56.09 | 55.83
2018-11-08 08:00 | 58.73 | 58.29
2018-11-08 08:30 | 60.62 | 59.88
2018-11-08 09:00 | 62.78 | 61.65
2018-11-08 09:30 | 64.61 | 63.24
2018-11-08 10:00 | 65.03 | 63.59
2018-11-08 10:30 | 64.66 | 63.11
2018-11-08 11:00 | 65.85 | 64.13
2018-11-08 11:30 | 68.73 | 66.86
2018-11-08 12:00 | 69.33 | 67.26
2018-11-08 12:30 | 69.16 | 66.46
2018-11-08 13:00 | 69.03 | 66.31
2018-11-08 13:30 | 69.79 | 67.11
2018-11-08 14:00 | 70.4 | 67.76
2018-11-08 14:30 | 71.23 | 68.58
2018-11-08 15:00 | 72.03 | 69.4
2018-11-08 15:30 | 72.21 | 69.54
2018-11-08 16:00 | 73.22 | 70.52
2018-11-08 16:30 | 73.98 | 71.23
2018-11-08 17:00 | 72.34 | 69.43
2018-11-08 17:30 | 69.52 | 66.37
2018-11-08 18:00 | 68.95 | 65.7
2018-11-08 18:30 | 68.62 | 65.29
2018-11-08 19:00 | 70.1 | 66.87
2018-11-08 19:30 | 69 | 65.69
2018-11-08 20:00 | 67.11 | 63.66
2018-11-08 20:30 | 65.05 | 61.52
2018-11-08 21:00 | 59.8 | 59.4
2018-11-08 21:30 | 57.03 | 56.59
2018-11-08 22:00 | 54.16 | 53.69
2018-11-08 22:30 | 51.79 | 51.28
2018-11-08 23:00 | 51.76 | 51.24
2018-11-08 23:30 | 48.36 | 47.79
2018-11-09 | 45.54 | 44.93
2018-11-09 00:30 | 43.79 | 43.13
2018-11-09 01:00 | 40.63 | 40.12
2018-11-09 01:30 | 38.89 | 38.2
2018-11-09 02:00 | 36.72 | 35.89
2018-11-09 02:30 | 35.9 | 35.33
2018-11-09 03:00 | 35.55 | 34.97
2018-11-09 03:30 | 34.97 | 34.39
2018-11-09 04:00 | 34.96 | 34.31
2018-11-09 04:30 | 34.82 | 34.08
2018-11-09 05:00 | 35.91 | 35.18
2018-11-09 05:30 | 37.61 | 36.91
2018-11-09 06:00 | 39.65 | 38.97
2018-11-09 06:30 | 45.71 | 44.82
2018-11-09 07:00 | 50.46 | 49.72
2018-11-09 07:30 | 54.62 | 53.93
2018-11-09 08:00 | 56.81 | 56.39
2018-11-09 08:30 | 57.86 | 57.42
2018-11-09 09:00 | 59.81 | 59.21
2018-11-09 09:30 | 59.79 | 59.01
2018-11-09 10:00 | 61.89 | 61.17
2018-11-09 10:30 | 61.87 | 61.05
2018-11-09 11:00 | 59.94 | 58.97
2018-11-09 11:30 | 59.02 | 57.92
2018-11-09 12:00 | 58.63 | 57.42
2018-11-09 12:30 | 57.92 | 56.67
2018-11-09 13:00 | 57 | 55.8
2018-11-09 13:30 | 56.84 | 55.71
2018-11-09 14:00 | 56.21 | 55.22
2018-11-09 14:30 | 56.89 | 55.95
2018-11-09 15:00 | 57.64 | 56.77
2018-11-09 15:30 | 57.08 | 56.46
2018-11-09 16:00 | 58.18 | 57.72
2018-11-09 16:30 | 59.51 | 59.16
2018-11-09 17:00 | 58.25 | 57.87
2018-11-09 17:30 | 57.3 | 56.88
2018-11-09 18:00 | 56.73 | 56.28
2018-11-09 18:30 | 57.04 | 56.58
2018-11-09 19:00 | 57.93 | 57.49
2018-11-09 19:30 | 56.71 | 56.26
2018-11-09 20:00 | 55.04 | 54.57
2018-11-09 20:30 | 53.1 | 52.61
2018-11-09 21:00 | 51.02 | 50.5
2018-11-09 21:30 | 49.48 | 48.94
2018-11-09 22:00 | 47.86 | 47.28
2018-11-09 22:30 | 46.55 | 45.94
2018-11-09 23:00 | 46.27 | 45.64
2018-11-09 23:30 | 42.71 | 42.03
2018-11-10 | 40.6 | 39.94
2018-11-10 00:30 | 39.73 | 39.05
2018-11-10 01:00 | 38.48 | 37.76
2018-11-10 01:30 | 37.51 | 36.82
2018-11-10 02:00 | 36.75 | 36.17
2018-11-10 02:30 | 36.28 | 35.69
2018-11-10 03:00 | 36.01 | 35.42
2018-11-10 03:30 | 35.74 | 35.14
2018-11-10 04:00 | 35.53 | 34.92
2018-11-10 04:30 | 35.82 | 35.22
2018-11-10 05:00 | 35.98 | 35.38
2018-11-10 05:30 | 36.41 | 35.82
2018-11-10 06:00 | 37.27 | 36.7
2018-11-10 06:30 | 39.6 | 39.08
2018-11-10 07:00 | 41.06 | 40.47
2018-11-10 07:30 | 44.09 | 43.28
2018-11-10 08:00 | 46.03 | 44.89
2018-11-10 08:30 | 50.28 | 49.57
2018-11-10 09:00 | 52.04 | 51.34
2018-11-10 09:30 | 53.19 | 52.51
2018-11-10 10:00 | 53.32 | 52.61
2018-11-10 10:30 | 51.82 | 51.04
2018-11-10 11:00 | 50.76 | 49.82
2018-11-10 11:30 | 50.29 | 49.37
2018-11-10 12:00 | 47.41 | 46.46
2018-11-10 12:30 | 45.19 | 44.39
2018-11-10 13:00 | 45.03 | 44.33
2018-11-10 13:30 | 42.75 | 42.06
2018-11-10 14:00 | 43.16 | 42.55
2018-11-10 14:30 | 42.99 | 42.39
2018-11-10 15:00 | 43.09 | 42.53
2018-11-10 15:30 | 44.03 | 43.54
2018-11-10 16:00 | 45.86 | 45.4
2018-11-10 16:30 | 45.99 | 45.52
2018-11-10 17:00 | 46.49 | 46.02
2018-11-10 17:30 | 47.68 | 47.21
2018-11-10 18:00 | 48.53 | 48.07
2018-11-10 18:30 | 49.33 | 48.87
2018-11-10 19:00 | 50.55 | 50.12
2018-11-10 19:30 | 49.28 | 48.83
2018-11-10 20:00 | 48.16 | 47.69
2018-11-10 20:30 | 46.76 | 46.27
2018-11-10 21:00 | 45.59 | 45.08
2018-11-10 21:30 | 44.37 | 43.84
2018-11-10 22:00 | 43.12 | 42.54
2018-11-10 22:30 | 42.2 | 41.61
2018-11-10 23:00 | 42.7 | 42.12
2018-11-10 23:30 | 39.38 | 38.75
2018-11-11 | 37.57 | 36.93
2018-11-11 00:30 | 37.04 | 36.32
2018-11-11 01:00 | 35.83 | 35.09
2018-11-11 01:30 | 35.16 | 34.41
2018-11-11 02:00 | 34.73 | 33.97
2018-11-11 02:30 | 34.42 | 33.66
2018-11-11 03:00 | 34.24 | 33.47
2018-11-11 03:30 | 34.13 | 33.36
2018-11-11 04:00 | 34.03 | 33.26
2018-11-11 04:30 | 34.34 | 33.57
2018-11-11 05:00 | 34.33 | 33.57
2018-11-11 05:30 | 33.85 | 33.08
2018-11-11 06:00 | 33.72 | 32.95
2018-11-11 06:30 | 35.11 | 34.36
2018-11-11 07:00 | 35.22 | 34.46
2018-11-11 07:30 | 35.73 | 34.98
2018-11-11 08:00 | 36.24 | 35.48
2018-11-11 08:30 | 37.15 | 36.39
2018-11-11 09:00 | 37.54 | 36.76
2018-11-11 09:30 | 37.86 | 36.95
2018-11-11 10:00 | 38.32 | 37.6
2018-11-11 10:30 | 39.21 | 38.51
2018-11-11 11:00 | 40.17 | 39.49
2018-11-11 11:30 | 40.54 | 39.86
2018-11-11 12:00 | 40.45 | 39.77
2018-11-11 12:30 | 40.41 | 39.74
2018-11-11 13:00 | 39.34 | 38.65
2018-11-11 13:30 | 39.37 | 38.68
2018-11-11 14:00 | 38.91 | 38.22
2018-11-11 14:30 | 39.26 | 38.58
2018-11-11 15:00 | 40.27 | 39.61
2018-11-11 15:30 | 41.84 | 41.19
2018-11-11 16:00 | 42.97 | 42.34
2018-11-11 16:30 | 45.77 | 45.19
2018-11-11 17:00 | 46.89 | 46.33
2018-11-11 17:30 | 48.95 | 48.42
2018-11-11 18:00 | 50.35 | 49.84
2018-11-11 18:30 | 51.99 | 51.5
2018-11-11 19:00 | 53.98 | 53.5
2018-11-11 19:30 | 53.19 | 52.7
2018-11-11 20:00 | 51.6 | 51.1
2018-11-11 20:30 | 49.66 | 49.14
2018-11-11 21:00 | 47.96 | 47.42
2018-11-11 21:30 | 46.12 | 45.57
2018-11-11 22:00 | 44.48 | 43.91
2018-11-11 22:30 | 43.03 | 42.45
2018-11-11 23:00 | 43.32 | 42.74
2018-11-11 23:30 | 39.6 | 38.98
2018-11-12 | 37.95 | 37.32
2018-11-12 00:30 | 37.33 | 36.68
2018-11-12 01:00 | 36.47 | 35.75
2018-11-12 01:30 | 36.34 | 35.6
2018-11-12 02:00 | 36.1 | 35.36
2018-11-12 02:30 | 35.5 | 34.75
2018-11-12 03:00 | 35.47 | 34.73
2018-11-12 03:30 | 35.5 | 34.75
2018-11-12 04:00 | 35.4 | 34.65
2018-11-12 04:30 | 36.06 | 35.32
2018-11-12 05:00 | 37.39 | 36.67
2018-11-12 05:30 | 38.93 | 38.23
2018-11-12 06:00 | 42.03 | 41.35
2018-11-12 06:30 | 47.84 | 46.65
2018-11-12 07:00 | 51.38 | 50.39
2018-11-12 07:30 | 56.52 | 56.01
2018-11-12 08:00 | 58.53 | 58.03
2018-11-12 08:30 | 59.87 | 59.09
2018-11-12 09:00 | 60.71 | 59.62
2018-11-12 09:30 | 61.76 | 60.36
2018-11-12 10:00 | 61.74 | 60.32
2018-11-12 10:30 | 62.12 | 60.62
2018-11-12 11:00 | 62.91 | 61.38
2018-11-12 11:30 | 62.24 | 60.67
2018-11-12 12:00 | 63.53 | 61.94
2018-11-12 12:30 | 62.51 | 60.99
2018-11-12 13:00 | 63.85 | 62.39
2018-11-12 13:30 | 62.83 | 61.25
2018-11-12 14:00 | 61.79 | 60.22
2018-11-12 14:30 | 62.62 | 61.08
2018-11-12 15:00 | 62.56 | 61.22
2018-11-12 15:30 | 62.45 | 61.32
2018-11-12 16:00 | 62.26 | 61.45
2018-11-12 16:30 | 63.98 | 63.36
2018-11-12 17:00 | 62.84 | 62.45
2018-11-12 17:30 | 61.05 | 60.69
2018-11-12 18:00 | 60.02 | 59.63
2018-11-12 18:30 | 60.11 | 59.7
2018-11-12 19:00 | 61.19 | 60.8
2018-11-12 19:30 | 59.99 | 59.59
2018-11-12 20:00 | 57.94 | 57.51
2018-11-12 20:30 | 55.7 | 55.24
2018-11-12 21:00 | 52.99 | 52.49
2018-11-12 21:30 | 50.14 | 49.59
2018-11-12 22:00 | 47.59 | 47.09
2018-11-12 22:30 | 45.84 | 45.4
2018-11-12 23:00 | 46.18 | 45.74
2018-11-12 23:30 | 42.55 | 42.08
2018-11-13 | 40.27 | 39.73
2018-11-13 00:30 | 38.77 | 38.13
2018-11-13 01:00 | 37.53 | 36.95
2018-11-13 01:30 | 36.54 | 35.93
2018-11-13 02:00 | 35.79 | 35.11
2018-11-13 02:30 | 35.56 | 34.88
2018-11-13 03:00 | 35.12 | 34.43
2018-11-13 03:30 | 34.77 | 34.09
2018-11-13 04:00 | 34.56 | 33.81
2018-11-13 04:30 | 35.22 | 34.46
2018-11-13 05:00 | 36.61 | 35.88
2018-11-13 05:30 | 38.45 | 37.75
2018-11-13 06:00 | 40.38 | 39.69
2018-11-13 06:30 | 45.62 | 44.62
2018-11-13 07:00 | 50.06 | 49.19
2018-11-13 07:30 | 55.63 | 54.48
2018-11-13 08:00 | 57.39 | 56.88
2018-11-13 08:30 | 58.68 | 57.99
2018-11-13 09:00 | 59.01 | 58.07
2018-11-13 09:30 | 58.84 | 57.78
2018-11-13 10:00 | 57.76 | 56.69
2018-11-13 10:30 | 57.94 | 56.75
2018-11-13 11:00 | 59.85 | 58.34
2018-11-13 11:30 | 60.39 | 58.86
2018-11-13 12:00 | 61.28 | 59.74
2018-11-13 12:30 | 61.97 | 60.48
2018-11-13 13:00 | 62.38 | 60.95
2018-11-13 13:30 | 62.28 | 60.79
2018-11-13 14:00 | 64.18 | 62.72
2018-11-13 14:30 | 65.5 | 64.11
2018-11-13 15:00 | 65.71 | 64.47
2018-11-13 15:30 | 62.93 | 61.86
2018-11-13 16:00 | 63.99 | 63.1
2018-11-13 16:30 | 65.25 | 64.58
2018-11-13 17:00 | 64.33 | 63.92
2018-11-13 17:30 | 61.76 | 61.41
2018-11-13 18:00 | 60.77 | 60.38
2018-11-13 18:30 | 60.14 | 59.72
2018-11-13 19:00 | 61.53 | 61.13
2018-11-13 19:30 | 60.37 | 59.95
2018-11-13 20:00 | 58.45 | 58.01
2018-11-13 20:30 | 55.83 | 55.43
2018-11-13 21:00 | 53.79 | 53.39
2018-11-13 21:30 | 51.66 | 51.25
2018-11-13 22:00 | 49.28 | 48.85
2018-11-13 22:30 | 47.49 | 47.05
2018-11-13 23:00 | 47.41 | 46.98
2018-11-13 23:30 | 43.7 | 43.24
2018-11-14 | 41.5 | 41.01
2018-11-14 00:30 | 40.34 | 39.81
2018-11-14 01:00 | 39.31 | 38.75
2018-11-14 01:30 | 38.67 | 38.1
2018-11-14 02:00 | 38.03 | 37.45
2018-11-14 02:30 | 37.19 | 36.61
2018-11-14 03:00 | 37.08 | 36.49
2018-11-14 03:30 | 36.92 | 36.33
2018-11-14 04:00 | 36.73 | 36.11
2018-11-14 04:30 | 37.96 | 37.32
2018-11-14 05:00 | 38.81 | 38.18
2018-11-14 05:30 | 40.44 | 39.83
2018-11-14 06:00 | 43.03 | 42.45
2018-11-14 06:30 | 48.78 | 48.17
2018-11-14 07:00 | 53.75 | 52.74
2018-11-14 07:30 | 58.32 | 57.53
2018-11-14 08:00 | 60.77 | 60.07
2018-11-14 08:30 | 63.43 | 62.4
2018-11-14 09:00 | 64.87 | 63.47
2018-11-14 09:30 | 63.93 | 63.79
2018-11-14 10:00 | 63.12 | 63.06
2018-11-14 10:30 | 63.39 | 63.36
2018-11-14 11:00 | 63.47 | 63.44
2018-11-14 11:30 | 61.29 | 61.25
2018-11-14 12:00 | 62.8 | 62.78
2018-11-14 12:30 | 64.29 | 64.28
2018-11-14 13:00 | 63.68 | 63.65
2018-11-14 13:30 | 64.05 | 64.03
2018-11-14 14:00 | 64.86 | 64.84
2018-11-14 14:30 | 66.24 | 66.23
2018-11-14 15:00 | 66.19 | 66.15
2018-11-14 15:30 | 65.91 | 65.81
2018-11-14 16:00 | 67.29 | 67.14
2018-11-14 16:30 | 68.42 | 68.14
2018-11-14 17:00 | 67.61 | 67.09
2018-11-14 17:30 | 65.77 | 64.68
2018-11-14 18:00 | 66.05 | 64.65
2018-11-14 18:30 | 67.36 | 65.8
2018-11-14 19:00 | 69.83 | 68.63
2018-11-14 19:30 | 68.9 | 67.68
2018-11-14 20:00 | 67.21 | 65.96
2018-11-14 20:30 | 65.37 | 63.94
2018-11-14 21:00 | 63.72 | 62.11
2018-11-14 21:30 | 62.78 | 59.81
2018-11-14 22:00 | 59.86 | 57.41
2018-11-14 22:30 | 55.44 | 55.03
2018-11-14 23:00 | 55.19 | 54.78
2018-11-14 23:30 | 51.2 | 50.77
2018-11-15 | 48.95 | 48.5
2018-11-15 00:30 | 47.77 | 47.32
2018-11-15 01:00 | 46.11 | 45.57
2018-11-15 01:30 | 44.98 | 44.39
2018-11-15 02:00 | 44.1 | 43.5
2018-11-15 02:30 | 43.57 | 42.97
2018-11-15 03:00 | 42.89 | 42.28
2018-11-15 03:30 | 42.29 | 41.68
2018-11-15 04:00 | 41.85 | 41.23
2018-11-15 04:30 | 42.33 | 41.71
2018-11-15 05:00 | 43.77 | 43.17
2018-11-15 05:30 | 45.5 | 44.91
2018-11-15 06:00 | 48.04 | 47.47
2018-11-15 06:30 | 52.94 | 52.19
2018-11-15 07:00 | 56.96 | 55.74
2018-11-15 07:30 | 54.26 | 53.02
2018-11-15 08:00 | 47.57 | 46.78
2018-11-15 08:30 | 48.9 | 47.78
2018-11-15 09:00 | 49.9 | 48.4
2018-11-15 09:30 | 50.58 | 48.94
2018-11-15 10:00 | 49.81 | 48.05
2018-11-15 10:30 | 49.97 | 48.17
2018-11-15 11:00 | 49.69 | 47.78
2018-11-15 11:30 | 54.31 | 52.31
2018-11-15 12:00 | 67.1 | 65.05
2018-11-15 12:30 | 67.12 | 65.2
2018-11-15 13:00 | 66.64 | 64.72
2018-11-15 13:30 | 66.81 | 64.91
2018-11-15 14:00 | 67.82 | 65.9
2018-11-15 14:30 | 68.54 | 66.64
2018-11-15 15:00 | 67.53 | 65.83
2018-11-15 15:30 | 66.79 | 65.41
2018-11-15 16:00 | 67.62 | 66.53
2018-11-15 16:30 | 68.76 | 67.9
2018-11-15 17:00 | 66.79 | 66.23
2018-11-15 17:30 | 63.64 | 63.31
2018-11-15 18:00 | 63.13 | 62.78
2018-11-15 18:30 | 62.99 | 62.63
2018-11-15 19:00 | 64.62 | 64.27
2018-11-15 19:30 | 63.42 | 63.06
2018-11-15 20:00 | 61.72 | 61.34
2018-11-15 20:30 | 59.27 | 58.86
2018-11-15 21:00 | 57.16 | 56.73
2018-11-15 21:30 | 54.65 | 54.18
2018-11-15 22:00 | 51.96 | 51.45
2018-11-15 22:30 | 49.96 | 49.45
2018-11-15 23:00 | 49.49 | 49.07
2018-11-15 23:30 | 45 | 44.54
2018-11-16 | 42.61 | 42.13
2018-11-16 00:30 | 41.4 | 40.91
2018-11-16 01:00 | 39.98 | 39.46
2018-11-16 01:30 | 39.1 | 38.56
2018-11-16 02:00 | 38.25 | 37.61
2018-11-16 02:30 | 37.54 | 36.94
2018-11-16 03:00 | 36.69 | 36.1
2018-11-16 03:30 | 36.28 | 35.62
2018-11-16 04:00 | 36.15 | 35.48
2018-11-16 04:30 | 36.97 | 36.25
2018-11-16 05:00 | 38.11 | 37.39
2018-11-16 05:30 | 39.53 | 38.83
2018-11-16 06:00 | 41.82 | 41.15
2018-11-16 06:30 | 47.11 | 46.1
2018-11-16 07:00 | 50.95 | 50.19
2018-11-16 07:30 | 55.33 | 54.37
2018-11-16 08:00 | 57.34 | 56.35
2018-11-16 08:30 | 59.39 | 58.3
2018-11-16 09:00 | 59.77 | 58.79
2018-11-16 09:30 | 59.83 | 58.81
2018-11-16 10:00 | 60.01 | 58.89
2018-11-16 10:30 | 60.57 | 59.35
2018-11-16 11:00 | 61.08 | 59.72
2018-11-16 11:30 | 61.41 | 59.93
2018-11-16 12:00 | 61.48 | 59.95
2018-11-16 12:30 | 62.03 | 60.61
2018-11-16 13:00 | 62.18 | 60.78
2018-11-16 13:30 | 62.18 | 60.84
2018-11-16 14:00 | 62.04 | 60.76
2018-11-16 14:30 | 61.88 | 60.75
2018-11-16 15:00 | 61.32 | 60.35
2018-11-16 15:30 | 61.2 | 60.46
2018-11-16 16:00 | 61.96 | 61.39
2018-11-16 16:30 | 63.25 | 62.84
2018-11-16 17:00 | 62.98 | 62.65
2018-11-16 17:30 | 61.31 | 60.94
2018-11-16 18:00 | 59.62 | 59.21
2018-11-16 18:30 | 59.44 | 59.02
2018-11-16 19:00 | 60.12 | 59.72
2018-11-16 19:30 | 59.36 | 58.95
2018-11-16 20:00 | 57.19 | 56.74
2018-11-16 20:30 | 54.49 | 54.07
2018-11-16 21:00 | 52.76 | 52.34
2018-11-16 21:30 | 51.28 | 50.86
2018-11-16 22:00 | 49.42 | 48.99
2018-11-16 22:30 | 47.9 | 47.45
2018-11-16 23:00 | 47.77 | 47.33
2018-11-16 23:30 | 43.77 | 43.3
2018-11-17 | 41.45 | 40.94
2018-11-17 00:30 | 40.08 | 39.53
2018-11-17 01:00 | 38.4 | 37.79
2018-11-17 01:30 | 37.82 | 37.18
2018-11-17 02:00 | 37.28 | 36.63
2018-11-17 02:30 | 36.78 | 36.12
2018-11-17 03:00 | 36.16 | 35.48
2018-11-17 03:30 | 35.83 | 35.1
2018-11-17 04:00 | 35.62 | 34.88
2018-11-17 04:30 | 35.75 | 35.01
2018-11-17 05:00 | 36.3 | 35.57
2018-11-17 05:30 | 36.06 | 35.33
2018-11-17 06:00 | 36.68 | 35.95
2018-11-17 06:30 | 38.29 | 37.57
2018-11-17 07:00 | 39.44 | 38.73
2018-11-17 07:30 | 41.09 | 40.23
2018-11-17 08:00 | 42.69 | 41.5
2018-11-17 08:30 | 45.93 | 44.43
2018-11-17 09:00 | 46.4 | 45.46
2018-11-17 09:30 | 46.05 | 45.17
2018-11-17 10:00 | 46.36 | 45.31
2018-11-17 10:30 | 46.19 | 45.01
2018-11-17 11:00 | 46.16 | 44.93
2018-11-17 11:30 | 46.12 | 44.88
2018-11-17 12:00 | 46.34 | 45.14
2018-11-17 12:30 | 45.36 | 44.34
2018-11-17 13:00 | 44.51 | 43.58
2018-11-17 13:30 | 44.59 | 43.71
2018-11-17 14:00 | 44.99 | 44.15
2018-11-17 14:30 | 44.82 | 44.11
2018-11-17 15:00 | 45.77 | 45.09
2018-11-17 15:30 | 46.73 | 46.13
2018-11-17 16:00 | 48.3 | 47.72
2018-11-17 16:30 | 50.57 | 50.03
2018-11-17 17:00 | 51.36 | 50.83
2018-11-17 17:30 | 52.81 | 52.31
2018-11-17 18:00 | 53.86 | 53.37
2018-11-17 18:30 | 54.57 | 54.08
2018-11-17 19:00 | 55.08 | 54.59
2018-11-17 19:30 | 54.44 | 53.95
2018-11-17 20:00 | 52.94 | 52.43
2018-11-17 20:30 | 51.58 | 51.06
2018-11-17 21:00 | 50.11 | 49.58
2018-11-17 21:30 | 48.69 | 48.15
2018-11-17 22:00 | 46.87 | 46.32
2018-11-17 22:30 | 45.61 | 45.04
2018-11-17 23:00 | 45.67 | 45.11
2018-11-17 23:30 | 42.07 | 41.47
2018-11-18 | 40.16 | 39.54
2018-11-18 00:30 | 39.06 | 38.44
2018-11-18 01:00 | 37.87 | 37.24
2018-11-18 01:30 | 37.02 | 36.38
2018-11-18 02:00 | 36.25 | 35.57
2018-11-18 02:30 | 35.98 | 35.25
2018-11-18 03:00 | 35.45 | 34.71
2018-11-18 03:30 | 35.26 | 34.52
2018-11-18 04:00 | 35.02 | 34.28
2018-11-18 04:30 | 35.25 | 34.51
2018-11-18 05:00 | 35.6 | 34.86
2018-11-18 05:30 | 35.1 | 34.36
2018-11-18 06:00 | 34.74 | 33.99
2018-11-18 06:30 | 35.85 | 35.11
2018-11-18 07:00 | 36.28 | 35.55
2018-11-18 07:30 | 37.27 | 36.54
2018-11-18 08:00 | 38.75 | 38.04
2018-11-18 08:30 | 40.97 | 40.24
2018-11-18 09:00 | 40.97 | 40.03
2018-11-18 09:30 | 41.06 | 40.31
2018-11-18 10:00 | 40.92 | 40.26
2018-11-18 10:30 | 42.15 | 41.48
2018-11-18 11:00 | 42.62 | 41.94
2018-11-18 11:30 | 42.67 | 42.01
2018-11-18 12:00 | 43.17 | 42.51
2018-11-18 12:30 | 43.17 | 42.53
2018-11-18 13:00 | 33.69 | 32.63
2018-11-18 13:30 | 38.8 | 37.98
2018-11-18 14:00 | 45.02 | 44.41
2018-11-18 14:30 | 45.4 | 44.8
2018-11-18 15:00 | 46.47 | 45.88
2018-11-18 15:30 | 47.84 | 47.28
2018-11-18 16:00 | 48.87 | 48.32
2018-11-18 16:30 | 51.24 | 50.71
2018-11-18 17:00 | 52.01 | 51.49
2018-11-18 17:30 | 53.76 | 53.27
2018-11-18 18:00 | 55.38 | 54.9
2018-11-18 18:30 | 56.23 | 55.77
2018-11-18 19:00 | 57.46 | 57
2018-11-18 19:30 | 57.05 | 56.59
2018-11-18 20:00 | 55.49 | 55.01
2018-11-18 20:30 | 53.26 | 52.77
2018-11-18 21:00 | 51.47 | 50.97
2018-11-18 21:30 | 49.11 | 48.59
2018-11-18 22:00 | 47.06 | 46.53
2018-11-18 22:30 | 45.58 | 45.04
2018-11-18 23:00 | 45.72 | 45.19
2018-11-18 23:30 | 41.87 | 41.29
2018-11-19 | 40.26 | 39.66
2018-11-19 00:30 | 39.88 | 39.28
2018-11-19 01:00 | 38.65 | 38.04
2018-11-19 01:30 | 38.31 | 37.69
2018-11-19 02:00 | 38.36 | 37.73
2018-11-19 02:30 | 38.05 | 37.35
2018-11-19 03:00 | 37.65 | 36.94
2018-11-19 03:30 | 37.86 | 37.16
2018-11-19 04:00 | 37.82 | 37.12
2018-11-19 04:30 | 38.69 | 37.99
2018-11-19 05:00 | 39.47 | 38.79
2018-11-19 05:30 | 41.6 | 40.93
2018-11-19 06:00 | 44.98 | 44.22
2018-11-19 06:30 | 50.9 | 49.54
2018-11-19 07:00 | 55.03 | 53.84
2018-11-19 07:30 | 59.15 | 58.64
2018-11-19 08:00 | 62.67 | 62.13
2018-11-19 08:30 | 63.06 | 62.24
2018-11-19 09:00 | 64.69 | 63.59
2018-11-19 09:30 | 66.04 | 64.78
2018-11-19 10:00 | 65.05 | 63.77
2018-11-19 10:30 | 66.42 | 64.98
2018-11-19 11:00 | 65.92 | 64.26
2018-11-19 11:30 | 66.32 | 64.5
2018-11-19 12:00 | 66.1 | 64.25
2018-11-19 12:30 | 66.55 | 64.77
2018-11-19 13:00 | 66.82 | 65.05
2018-11-19 13:30 | 67.4 | 65.57
2018-11-19 14:00 | 67.79 | 65.94
2018-11-19 14:30 | 67.74 | 66.02
2018-11-19 15:00 | 67.65 | 66.14
2018-11-19 15:30 | 67.05 | 65.71
2018-11-19 16:00 | 67.4 | 66.32
2018-11-19 16:30 | 69.58 | 68.7
2018-11-19 17:00 | 68.27 | 67.68
2018-11-19 17:30 | 65.3 | 64.96
2018-11-19 18:00 | 64.22 | 63.87
2018-11-19 18:30 | 63.28 | 62.91
2018-11-19 19:00 | 64.58 | 64.22
2018-11-19 19:30 | 63.71 | 63.34
2018-11-19 20:00 | 61.94 | 61.55
2018-11-19 20:30 | 59.47 | 59.06
2018-11-19 21:00 | 56.76 | 56.31
2018-11-19 21:30 | 53.91 | 53.42
2018-11-19 22:00 | 51.08 | 50.65
2018-11-19 22:30 | 49.35 | 48.93
2018-11-19 23:00 | 49.39 | 48.98
2018-11-19 23:30 | 45.66 | 45.21
2018-11-20 | 43.6 | 43.14
2018-11-20 00:30 | 42.78 | 42.31
2018-11-20 01:00 | 41.4 | 40.91
2018-11-20 01:30 | 40.82 | 40.33
2018-11-20 02:00 | 40.06 | 39.55
2018-11-20 02:30 | 39.33 | 38.8
2018-11-20 03:00 | 38.96 | 38.35
2018-11-20 03:30 | 35.05 | 34.37
2018-11-20 04:00 | 38.89 | 38.32
2018-11-20 04:30 | 39.62 | 39.07
2018-11-20 05:00 | 40.7 | 40.16
2018-11-20 05:30 | 42.79 | 42.26
2018-11-20 06:00 | 45.06 | 44.54
2018-11-20 06:30 | 50.08 | 49.58
2018-11-20 07:00 | 54.54 | 54.1
2018-11-20 07:30 | 60.12 | 59.63
2018-11-20 08:00 | 63.37 | 62.64
2018-11-20 08:30 | 63.88 | 62.89
2018-11-20 09:00 | 65.17 | 63.89
2018-11-20 09:30 | 64.68 | 63.31
2018-11-20 10:00 | 63.86 | 62.47
2018-11-20 10:30 | 64.33 | 62.8
2018-11-20 11:00 | 66.16 | 64.39
2018-11-20 11:30 | 66.73 | 64.87
2018-11-20 12:00 | 67.92 | 66.1
2018-11-20 12:30 | 69.64 | 67.84
2018-11-20 13:00 | 67.18 | 65.44
2018-11-20 13:30 | 67.72 | 65.98
2018-11-20 14:00 | 67.83 | 66.2
2018-11-20 14:30 | 66.49 | 64.88
2018-11-20 15:00 | 67.46 | 65.91
2018-11-20 15:30 | 67.58 | 66.22
2018-11-20 16:00 | 69.12 | 67.98
2018-11-20 16:30 | 69.34 | 68.51
2018-11-20 17:00 | 66.05 | 65.56
2018-11-20 17:30 | 62.99 | 62.65
2018-11-20 18:00 | 62.54 | 62.17
2018-11-20 18:30 | 62.36 | 61.99
2018-11-20 19:00 | 63.82 | 63.47
2018-11-20 19:30 | 63.18 | 62.81
2018-11-20 20:00 | 61.05 | 60.67
2018-11-20 20:30 | 59.02 | 58.61
2018-11-20 21:00 | 56.63 | 56.19
2018-11-20 21:30 | 54.25 | 53.78
2018-11-20 22:00 | 51.81 | 51.3
2018-11-20 22:30 | 49.68 | 49.13
2018-11-20 23:00 | 49.19 | 48.67
2018-11-20 23:30 | 45.07 | 44.61
2018-11-21 | 43.54 | 43.07
2018-11-21 00:30 | 42.19 | 41.71
2018-11-21 01:00 | 40.72 | 40.23
2018-11-21 01:30 | 40.2 | 39.7
2018-11-21 02:00 | 39.61 | 39.11
2018-11-21 02:30 | 39.35 | 38.83
2018-11-21 03:00 | 38.73 | 38.16
2018-11-21 03:30 | 38.58 | 37.97
2018-11-21 04:00 | 38.65 | 38
2018-11-21 04:30 | 39.52 | 38.89
2018-11-21 05:00 | 41.11 | 40.5
2018-11-21 05:30 | 42.98 | 42.39
2018-11-21 06:00 | 46.16 | 45.59
2018-11-21 06:30 | 51.45 | 50.83
2018-11-21 07:00 | 56.28 | 55.74
2018-11-21 07:30 | 61.39 | 60.89
2018-11-21 08:00 | 63.45 | 62.72
2018-11-21 08:30 | 64.55 | 63.5
2018-11-21 09:00 | 65.4 | 64
2018-11-21 09:30 | 65.05 | 63.54
2018-11-21 10:00 | 64.52 | 63.01
2018-11-21 10:30 | 64.65 | 62.98
2018-11-21 11:00 | 66.4 | 64.34
2018-11-21 11:30 | 66.57 | 64.41
2018-11-21 12:00 | 67.41 | 65.2
2018-11-21 12:30 | 68.08 | 65.89
2018-11-21 13:00 | 68.27 | 66.12
2018-11-21 13:30 | 68.42 | 66.36
2018-11-21 14:00 | 69.62 | 67.54
2018-11-21 14:30 | 69.92 | 67.96
2018-11-21 15:00 | 70.51 | 68.59
2018-11-21 15:30 | 70.75 | 69.11
2018-11-21 16:00 | 71.11 | 69.74
2018-11-21 16:30 | 71.96 | 70.83
2018-11-21 17:00 | 70.76 | 69.57
2018-11-21 17:30 | 68.14 | 66.81
2018-11-21 18:00 | 67.04 | 65.63
2018-11-21 18:30 | 66.25 | 64.76
2018-11-21 19:00 | 67.91 | 66.48
2018-11-21 19:30 | 66.6 | 65.12
2018-11-21 20:00 | 64.95 | 63.42
2018-11-21 20:30 | 61.4 | 60.97
2018-11-21 21:00 | 58.21 | 58.21
2018-11-21 21:30 | 54.99 | 54.98
2018-11-21 22:00 | 52.43 | 52.39
2018-11-21 22:30 | 50.26 | 50.18
2018-11-21 23:00 | 50.41 | 50.32
2018-11-21 23:30 | 46.24 | 45.9
2018-11-22 | 45.47 | 43.53
2018-11-22 00:30 | 44.07 | 42.09
2018-11-22 01:00 | 42.81 | 40.75
2018-11-22 01:30 | 42.2 | 40.11
2018-11-22 02:00 | 41.57 | 39.48
2018-11-22 02:30 | 40.84 | 38.74
2018-11-22 03:00 | 40.3 | 38.09
2018-11-22 03:30 | 40.08 | 37.83
2018-11-22 04:00 | 40.47 | 38.24
2018-11-22 04:30 | 41.54 | 39.36
2018-11-22 05:00 | 42.5 | 40.38
2018-11-22 05:30 | 44.49 | 42.47
2018-11-22 06:00 | 47.71 | 45.82
2018-11-22 06:30 | 53.38 | 51.76
2018-11-22 07:00 | 56.4 | 56.22
2018-11-22 07:30 | 61.84 | 61.46
2018-11-22 08:00 | 65.64 | 64.74
2018-11-22 08:30 | 66.29 | 65.08
2018-11-22 09:00 | 66.87 | 65.42
2018-11-22 09:30 | 67.66 | 65.44
2018-11-22 10:00 | 69.98 | 67.32
2018-11-22 10:30 | 70.66 | 68.04
2018-11-22 11:00 | 70.66 | 68.06
2018-11-22 11:30 | 71.44 | 68.89
2018-11-22 12:00 | 71.88 | 69.37
2018-11-22 12:30 | 72.79 | 70.32
2018-11-22 13:00 | 73.1 | 70.65
2018-11-22 13:30 | 77.92 | 73.01
2018-11-22 14:00 | 80.66 | 73.46
2018-11-22 14:30 | 81.22 | 74.12
2018-11-22 15:00 | 82.61 | 75.57
2018-11-22 15:30 | 83.72 | 76.57
2018-11-22 16:00 | 83.86 | 76.56
2018-11-22 16:30 | 84.22 | 76.79
2018-11-22 17:00 | 82.29 | 74.52
2018-11-22 17:30 | 75.06 | 71.91
2018-11-22 18:00 | 74.12 | 71.2
2018-11-22 18:30 | 73.69 | 70.7
2018-11-22 19:00 | 73.22 | 70.17
2018-11-22 19:30 | 67.38 | 66.4
2018-11-22 20:00 | 64.36 | 64
2018-11-22 20:30 | 62.37 | 61.99
2018-11-22 21:00 | 60.33 | 59.92
2018-11-22 21:30 | 57.23 | 56.78
2018-11-22 22:00 | 54.37 | 53.89
2018-11-22 22:30 | 51.92 | 51.5
2018-11-22 23:00 | 51.18 | 50.77
2018-11-22 23:30 | 47.12 | 46.68
2018-11-23 | 44.99 | 44.53
2018-11-23 00:30 | 43.86 | 43.4
2018-11-23 01:00 | 42.25 | 41.78
2018-11-23 01:30 | 41.71 | 41.22
2018-11-23 02:00 | 41.8 | 40.49
2018-11-23 02:30 | 44.12 | 39.61
2018-11-23 03:00 | 43.94 | 39.41
2018-11-23 03:30 | 43.6 | 39.02
2018-11-23 04:00 | 43.25 | 38.62
2018-11-23 04:30 | 43.88 | 39.33
2018-11-23 05:00 | 44.98 | 40.54
2018-11-23 05:30 | 46.62 | 42.34
2018-11-23 06:00 | 47.67 | 43.49
2018-11-23 06:30 | 52.9 | 49.1
2018-11-23 07:00 | 57.31 | 53.77
2018-11-23 07:30 | 62.21 | 60.68
2018-11-23 08:00 | 64.81 | 63.97
2018-11-23 08:30 | 65.09 | 63.83
2018-11-23 09:00 | 67.28 | 66.04
2018-11-23 09:30 | 68.81 | 67.6
2018-11-23 10:00 | 69.18 | 67.96
2018-11-23 10:30 | 71 | 69.8
2018-11-23 11:00 | 71.84 | 70.78
2018-11-23 11:30 | 73.2 | 72.89
2018-11-23 12:00 | 73.99 | 73.68
2018-11-23 12:30 | 73.6 | 73.3
2018-11-23 13:00 | 73.39 | 73.09
2018-11-23 13:30 | 73.98 | 73.69
2018-11-23 14:00 | 75.42 | 75.14
2018-11-23 14:30 | 75.67 | 75.39
2018-11-23 15:00 | 75.24 | 74.96
2018-11-23 15:30 | 75.28 | 75.02
2018-11-23 16:00 | 75.47 | 75.22
2018-11-23 16:30 | 76.55 | 76.31
2018-11-23 17:00 | 75.65 | 75.38
2018-11-23 17:30 | 73.84 | 73.27
2018-11-23 18:00 | 72.77 | 71.91
2018-11-23 18:30 | 71.4 | 70.25
2018-11-23 19:00 | 72.03 | 71.02
2018-11-23 19:30 | 71.11 | 70
2018-11-23 20:00 | 69.49 | 68.2
2018-11-23 20:30 | 67.26 | 65.68
2018-11-23 21:00 | 65.16 | 63.3
2018-11-23 21:30 | 63.36 | 60.65
2018-11-23 22:00 | 60.79 | 57.97
2018-11-23 22:30 | 58.39 | 55.35
2018-11-23 23:00 | 56.39 | 53.08
2018-11-23 23:30 | 52.26 | 48.71
2018-11-24 | 50.01 | 46.29
2018-11-24 00:30 | 48.37 | 44.36
2018-11-24 01:00 | 46.99 | 42.5
2018-11-24 01:30 | 46.08 | 41.47
2018-11-24 02:00 | 45.04 | 40.31
2018-11-24 02:30 | 44.42 | 39.62
2018-11-24 03:00 | 43.75 | 38.87
2018-11-24 03:30 | 40.31 | 38.07
2018-11-24 04:00 | 38.38 | 37.67
2018-11-24 04:30 | 38.28 | 37.57
2018-11-24 05:00 | 38.13 | 37.42
2018-11-24 05:30 | 37.37 | 36.65
2018-11-24 06:00 | 38 | 37.29
2018-11-24 06:30 | 40.47 | 39.77
2018-11-24 07:00 | 41.83 | 41.04
2018-11-24 07:30 | 43.07 | 42.02
2018-11-24 08:00 | 44.32 | 42.98
2018-11-24 08:30 | 46.41 | 45.38
2018-11-24 09:00 | 48.19 | 47.22
2018-11-24 09:30 | 49.01 | 47.88
2018-11-24 10:00 | 49.54 | 48.24
2018-11-24 10:30 | 50.61 | 49.16
2018-11-24 11:00 | 51.83 | 50.29
2018-11-24 11:30 | 52.93 | 51.37
2018-11-24 12:00 | 53.54 | 51.98
2018-11-24 12:30 | 53.08 | 51.74
2018-11-24 13:00 | 53.06 | 51.81
2018-11-24 13:30 | 53.67 | 52.47
2018-11-24 14:00 | 54.2 | 53.07
2018-11-24 14:30 | 54.68 | 53.65
2018-11-24 15:00 | 55.17 | 54.18
2018-11-24 15:30 | 55.81 | 54.96
2018-11-24 16:00 | 58.16 | 57.29
2018-11-24 16:30 | 60.83 | 60.02
2018-11-24 17:00 | 61.63 | 60.9
2018-11-24 17:30 | 62.03 | 61.39
2018-11-24 18:00 | 62.77 | 62.15
2018-11-24 18:30 | 63.03 | 62.44
2018-11-24 19:00 | 63.77 | 63.11
2018-11-24 19:30 | 64.01 | 63.33
2018-11-24 20:00 | 62.71 | 62.03
2018-11-24 20:30 | 60.58 | 60
2018-11-24 21:00 | 58.73 | 58.19
2018-11-24 21:30 | 56.49 | 56.03
2018-11-24 22:00 | 54.83 | 54.44
2018-11-24 22:30 | 52.62 | 52.22
2018-11-24 23:00 | 51.82 | 51.41
2018-11-24 23:30 | 47.98 | 47.52
2018-11-25 | 46.17 | 45.7
2018-11-25 00:30 | 45.17 | 44.67
2018-11-25 01:00 | 43.47 | 42.94
2018-11-25 01:30 | 42.2 | 41.65
2018-11-25 02:00 | 41.45 | 40.88
2018-11-25 02:30 | 40.67 | 40.09
2018-11-25 03:00 | 39.9 | 39.3
2018-11-25 03:30 | 39.11 | 38.49
2018-11-25 04:00 | 38.4 | 37.85
2018-11-25 04:30 | 38.37 | 37.83
2018-11-25 05:00 | 38.23 | 37.68
2018-11-25 05:30 | 37.39 | 36.82
2018-11-25 06:00 | 37.17 | 36.59
2018-11-25 06:30 | 38.81 | 38.27
2018-11-25 07:00 | 39.33 | 38.81
2018-11-25 07:30 | 41.31 | 40.66
2018-11-25 08:00 | 42.88 | 42.01
2018-11-25 08:30 | 45.23 | 44.18
2018-11-25 09:00 | 47.26 | 46.62
2018-11-25 09:30 | 49.18 | 48.49
2018-11-25 10:00 | 51.63 | 50.76
2018-11-25 10:30 | 54.4 | 53.36
2018-11-25 11:00 | 55.92 | 54.8
2018-11-25 11:30 | 58.06 | 56.84
2018-11-25 12:00 | 60.42 | 59.11
2018-11-25 12:30 | 62.48 | 61.17
2018-11-25 13:00 | 63.08 | 61.8
2018-11-25 13:30 | 64.45 | 63.19
2018-11-25 14:00 | 65.57 | 64.39
2018-11-25 14:30 | 65.33 | 64.22
2018-11-25 15:00 | 67.01 | 66.05
2018-11-25 15:30 | 67.78 | 66.85
2018-11-25 16:00 | 68.16 | 67.27
2018-11-25 16:30 | 69.29 | 68.41
2018-11-25 17:00 | 68.45 | 67.62
2018-11-25 17:30 | 69.3 | 68.55
2018-11-25 18:00 | 70.79 | 69.99
2018-11-25 18:30 | 70.73 | 70.02
2018-11-25 19:00 | 70.03 | 69.27
2018-11-25 19:30 | 67.87 | 67.18
2018-11-25 20:00 | 68.17 | 67.52
2018-11-25 20:30 | 67.88 | 67.3
2018-11-25 21:00 | 63.89 | 63.38
2018-11-25 21:30 | 59.59 | 59.21
2018-11-25 22:00 | 55.88 | 55.51
2018-11-25 22:30 | 52.66 | 52.26
2018-11-25 23:00 | 50.6 | 50.17
2018-11-25 23:30 | 48.47 | 48.01
2018-11-26 | 46.67 | 46.18
2018-11-26 00:30 | 45.43 | 44.92
2018-11-26 01:00 | 44.34 | 43.81
2018-11-26 01:30 | 43.47 | 42.93
2018-11-26 02:00 | 43.13 | 42.58
2018-11-26 02:30 | 42.08 | 42.03
2018-11-26 03:00 | 41.83 | 41.8
2018-11-26 03:30 | 41.36 | 41.34
2018-11-26 04:00 | 40.98 | 40.95
2018-11-26 04:30 | 41.69 | 41.65
2018-11-26 05:00 | 42.64 | 42.57
2018-11-26 05:30 | 44.2 | 44.07
2018-11-26 06:00 | 47.43 | 47.16
2018-11-26 06:30 | 55.16 | 54.48
2018-11-26 07:00 | 61.33 | 60.58
2018-11-26 07:30 | 67.19 | 66.49
2018-11-26 08:00 | 71.86 | 70.65
2018-11-26 08:30 | 76.08 | 74.35
2018-11-26 09:00 | 77.86 | 76.56
2018-11-26 09:30 | 78.55 | 77.27
2018-11-26 10:00 | 78.75 | 77.48
2018-11-26 10:30 | 80.4 | 79.18
2018-11-26 11:00 | 81.69 | 80.51
2018-11-26 11:30 | 83.31 | 82.19
2018-11-26 12:00 | 85.42 | 84.34
2018-11-26 12:30 | 86.75 | 85.69
2018-11-26 13:00 | 87 | 85.94
2018-11-26 13:30 | 88.06 | 87.01
2018-11-26 14:00 | 88.8 | 87.76
2018-11-26 14:30 | 88.93 | 87.9
2018-11-26 15:00 | 89.48 | 88.45
2018-11-26 15:30 | 89.61 | 88.56
2018-11-26 16:00 | 89.68 | 88.61
2018-11-26 16:30 | 88.9 | 87.78
2018-11-26 17:00 | 87.67 | 86.5
2018-11-26 17:30 | 85.01 | 83.73
2018-11-26 18:00 | 83.6 | 82.25
2018-11-26 18:30 | 81.86 | 80.44
2018-11-26 19:00 | 80.31 | 79.76
2018-11-26 19:30 | 79.34 | 78.77
2018-11-26 20:00 | 76.7 | 75.98
2018-11-26 20:30 | 74.48 | 73.55
2018-11-26 21:00 | 75.71 | 74.7
2018-11-26 21:30 | 74.36 | 73.09
2018-11-26 22:00 | 65.04 | 62.97
2018-11-26 22:30 | 59.36 | 56.9
2018-11-26 23:00 | 54.75 | 53.15
2018-11-26 23:30 | 51.88 | 50.18
2018-11-27 | 49.7 | 47.94
2018-11-27 00:30 | 47.9 | 46.08
2018-11-27 01:00 | 46.85 | 44.98
2018-11-27 01:30 | 46.11 | 44.22
2018-11-27 02:00 | 46.15 | 44.27
2018-11-27 02:30 | 45.27 | 43.35
2018-11-27 03:00 | 44.68 | 42.73
2018-11-27 03:30 | 44.11 | 42.14
2018-11-27 04:00 | 43.9 | 41.92
2018-11-27 04:30 | 44.46 | 42.51
2018-11-27 05:00 | 45.13 | 43.2
2018-11-27 05:30 | 46.12 | 44.22
2018-11-27 06:00 | 48.5 | 46.69
2018-11-27 06:30 | 54.43 | 52.75
2018-11-27 07:00 | 59.75 | 58.18
2018-11-27 07:30 | 64.62 | 63.32
2018-11-27 08:00 | 66.12 | 65.18
2018-11-27 08:30 | 69.17 | 67.73
2018-11-27 09:00 | 73.25 | 71.34
2018-11-27 09:30 | 76.42 | 74.27
2018-11-27 10:00 | 78.55 | 76.29
2018-11-27 10:30 | 80.5 | 79.01
2018-11-27 11:00 | 82.44 | 81.29
2018-11-27 11:30 | 84.31 | 83.21
2018-11-27 12:00 | 86.28 | 85.14
2018-11-27 12:30 | 87.66 | 87.37
2018-11-27 13:00 | 87.94 | 87.68
2018-11-27 13:30 | 88.52 | 88.22
2018-11-27 14:00 | 89.62 | 89.33
2018-11-27 14:30 | 89.97 | 89.68
2018-11-27 15:00 | 89.89 | 89.59
2018-11-27 15:30 | 89.77 | 89.46
2018-11-27 16:00 | 90.1 | 89.78
2018-11-27 16:30 | 88.66 | 88.42
2018-11-27 17:00 | 86.65 | 86.42
2018-11-27 17:30 | 83.7 | 83.17
2018-11-27 18:00 | 81.64 | 81.31
2018-11-27 18:30 | 80.17 | 79.65
2018-11-27 19:00 | 80.64 | 80.17
2018-11-27 19:30 | 79.2 | 78.6
2018-11-27 20:00 | 77.6 | 75.46
2018-11-27 20:30 | 73.5 | 72.96
2018-11-27 21:00 | 70.48 | 70.13
2018-11-27 21:30 | 69.83 | 69.48
2018-11-27 22:00 | 71.84 | 71.5
2018-11-27 22:30 | 64.96 | 64.59
2018-11-27 23:00 | 60.07 | 59.68
2018-11-27 23:30 | 55.19 | 54.77
2018-11-28 | 54.07 | 51.46
2018-11-28 00:30 | 53.13 | 49.21
2018-11-28 01:00 | 52.33 | 48.31
2018-11-28 01:30 | 51.75 | 47.67
2018-11-28 02:00 | 51.13 | 46.98
2018-11-28 02:30 | 50.45 | 46.24
2018-11-28 03:00 | 49.66 | 45.36
2018-11-28 03:30 | 49.23 | 44.9
2018-11-28 04:00 | 48.64 | 44.28
2018-11-28 04:30 | 49.37 | 45.09
2018-11-28 05:00 | 50.15 | 45.93
2018-11-28 05:30 | 51.95 | 47.87
2018-11-28 06:00 | 54.26 | 50.35
2018-11-28 06:30 | 61 | 57.5
2018-11-28 07:00 | 66.41 | 63.17
2018-11-28 07:30 | 73.9 | 71.73
2018-11-28 08:00 | 76.16 | 75.79
2018-11-28 08:30 | 78.47 | 78.18
2018-11-28 09:00 | 81.66 | 81.37
2018-11-28 09:30 | 83.56 | 83.27
2018-11-28 10:00 | 85.11 | 84.82
2018-11-28 10:30 | 86.9 | 86.64
2018-11-28 11:00 | 88.7 | 88.45
2018-11-28 11:30 | 89.31 | 89.04
2018-11-28 12:00 | 91.33 | 90.91
2018-11-28 12:30 | 93.79 | 93.5
2018-11-28 13:00 | 94.17 | 93.93
2018-11-28 13:30 | 95.95 | 95.71
2018-11-28 14:00 | 94.71 | 94.46
2018-11-28 14:30 | 97.38 | 97.15
2018-11-28 15:00 | 96.39 | 96.33
2018-11-28 15:30 | 93.73 | 93.72
2018-11-28 16:00 | 97.57 | 97.56
2018-11-28 16:30 | 93.84 | 93.83
2018-11-28 17:00 | 90.64 | 90.53
2018-11-28 17:30 | 87.7 | 87.32
2018-11-28 18:00 | 86.25 | 85.38
2018-11-28 18:30 | 79.74 | 78.74
2018-11-28 19:00 | 85.67 | 84.75
2018-11-28 19:30 | 85.8 | 84.89
2018-11-28 20:00 | 82.66 | 81.73
2018-11-28 20:30 | 78.34 | 77.36
2018-11-28 21:00 | 74.52 | 73.48
2018-11-28 21:30 | 73.72 | 72.56
2018-11-28 22:00 | 76.55 | 75.4
2018-11-28 22:30 | 69.75 | 65.06
2018-11-28 23:00 | 66.53 | 60.8
2018-11-28 23:30 | 63.36 | 55.03
2018-11-29 | 58.4 | 52.13
2018-11-29 00:30 | 56.92 | 50.42
2018-11-29 01:00 | 55.42 | 48.69
2018-11-29 01:30 | 54.25 | 47.35
2018-11-29 02:00 | 53.33 | 46.29
2018-11-29 02:30 | 52.16 | 44.96
2018-11-29 03:00 | 51.18 | 43.8
2018-11-29 03:30 | 50.38 | 42.9
2018-11-29 04:00 | 49.8 | 42.11
2018-11-29 04:30 | 50.21 | 42.51
2018-11-29 05:00 | 50.81 | 43.2
2018-11-29 05:30 | 51.89 | 44.47
2018-11-29 06:00 | 54.05 | 46.93
2018-11-29 06:30 | 59.3 | 52.9
2018-11-29 07:00 | 64.05 | 58.21
2018-11-29 07:30 | 67.56 | 64.28
2018-11-29 08:00 | 71.44 | 66.56
2018-11-29 08:30 | 73.05 | 68.25
2018-11-29 09:00 | 74.69 | 69.99
2018-11-29 09:30 | 75.85 | 71.21
2018-11-29 10:00 | 75.53 | 70.87
2018-11-29 10:30 | 75.8 | 71.16
2018-11-29 11:00 | 76.65 | 72.05
2018-11-29 11:30 | 77.73 | 73.2
2018-11-29 12:00 | 78.07 | 73.55
2018-11-29 12:30 | 79.06 | 74.6
2018-11-29 13:00 | 78.76 | 74.29
2018-11-29 13:30 | 76.51 | 76.1
2018-11-29 14:00 | 77.55 | 77.29
2018-11-29 14:30 | 78.78 | 78.52
2018-11-29 15:00 | 78.99 | 78.72
2018-11-29 15:30 | 78.75 | 78.47
2018-11-29 16:00 | 78.94 | 78.65
2018-11-29 16:30 | 78.23 | 77.92
2018-11-29 17:00 | 77.84 | 77.51
2018-11-29 17:30 | 75.99 | 75.6
2018-11-29 18:00 | 75.19 | 74.64
2018-11-29 18:30 | 74.97 | 74.26
2018-11-29 19:00 | 75.01 | 74.3
2018-11-29 19:30 | 73.61 | 72.8
2018-11-29 20:00 | 71.41 | 70.42
2018-11-29 20:30 | 71 | 69.86
2018-11-29 21:00 | 66.68 | 65.06
2018-11-29 21:30 | 61.03 | 60.18
2018-11-29 22:00 | 56.4 | 55.99
2018-11-29 22:30 | 52.6 | 52.14
2018-11-29 23:00 | 50.55 | 50.06
2018-11-29 23:30 | 47.85 | 47.37
2018-11-30 | 45.45 | 44.95
2018-11-30 00:30 | 43.95 | 43.42
2018-11-30 01:00 | 42.38 | 41.83
2018-11-30 01:30 | 41.76 | 41.2
2018-11-30 02:00 | 40.99 | 40.41
2018-11-30 02:30 | 40.16 | 39.56
2018-11-30 03:00 | 39.51 | 38.97
2018-11-30 03:30 | 38.89 | 38.34
2018-11-30 04:00 | 38.84 | 38.29
2018-11-30 04:30 | 39.12 | 38.58
2018-11-30 05:00 | 39.64 | 39.11
2018-11-30 05:30 | 40.89 | 40.38
2018-11-30 06:00 | 43.51 | 43.05
2018-11-30 06:30 | 48.75 | 48.16
2018-11-30 07:00 | 54.86 | 52.37
2018-11-30 07:30 | 60.35 | 57.2
2018-11-30 08:00 | 60.14 | 57.07
2018-11-30 08:30 | 67.12 | 63.46
2018-11-30 09:00 | 74.46 | 66.97
2018-11-30 09:30 | 75.06 | 67.72
2018-11-30 10:00 | 76.11 | 69
2018-11-30 10:30 | 78.31 | 70.28
2018-11-30 11:00 | 77.54 | 71.96
2018-11-30 11:30 | 77.91 | 72.97
2018-11-30 12:00 | 79.4 | 74.59
2018-11-30 12:30 | 81.32 | 76.67
2018-11-30 13:00 | 81.6 | 76.96
2018-11-30 13:30 | 82.11 | 77.48
2018-11-30 14:00 | 82.52 | 77.88
2018-11-30 14:30 | 82.39 | 77.71
2018-11-30 15:00 | 82.51 | 77.82
2018-11-30 15:30 | 82.77 | 78.04
2018-11-30 16:00 | 83.43 | 78.7
2018-11-30 16:30 | 83.24 | 78.43
2018-11-30 17:00 | 82.92 | 78.02
2018-11-30 17:30 | 80.91 | 75.72
2018-11-30 18:00 | 78.92 | 74.45
2018-11-30 18:30 | 73.73 | 72.29
2018-11-30 19:00 | 74.08 | 72.67
2018-11-30 19:30 | 70.24 | 68.69
2018-11-30 20:00 | 67.47 | 65.82
2018-11-30 20:30 | 65.33 | 63.6
2018-11-30 21:00 | 62.64 | 61.28
2018-11-30 21:30 | 59.89 | 58.55
2018-11-30 22:00 | 57.61 | 55.99
2018-11-30 22:30 | 55.03 | 52.99
2018-11-30 23:00 | 55.03 | 53.26
2018-11-30 23:30 | 50.87 | 50.62
2018-12-01 | 48.64 | 48.19
2018-12-01 00:30 | 46.91 | 46.42
2018-12-01 01:00 | 45.36 | 44.86
2018-12-01 01:30 | 44.28 | 43.76
2018-12-01 02:00 | 43.36 | 42.82
2018-12-01 02:30 | 42.43 | 41.86
2018-12-01 03:00 | 41.95 | 41.38
2018-12-01 03:30 | 41.61 | 41.02
2018-12-01 04:00 | 41.26 | 40.67
2018-12-01 04:30 | 41.42 | 40.84
2018-12-01 05:00 | 41.77 | 41.19
2018-12-01 05:30 | 41.2 | 40.61
2018-12-01 06:00 | 41.53 | 40.95
2018-12-01 06:30 | 42.06 | 41.51
2018-12-01 07:00 | 43.63 | 43.12
2018-12-01 07:30 | 46.64 | 46.21
2018-12-01 08:00 | 49.53 | 49.15
2018-12-01 08:30 | 52.54 | 52.17
2018-12-01 09:00 | 55.67 | 55.17
2018-12-01 09:30 | 57.06 | 56.1
2018-12-01 10:00 | 60.36 | 57.13
2018-12-01 10:30 | 60.19 | 56.99
2018-12-01 11:00 | 60.76 | 57.61
2018-12-01 11:30 | 62.33 | 59.25
2018-12-01 12:00 | 64.98 | 62.04
2018-12-01 12:30 | 65.73 | 62.8
2018-12-01 13:00 | 65.88 | 62.95
2018-12-01 13:30 | 66.01 | 63.08
2018-12-01 14:00 | 66.67 | 63.78
2018-12-01 14:30 | 67.4 | 64.52
2018-12-01 15:00 | 68.37 | 65.54
2018-12-01 15:30 | 69.44 | 66.65
2018-12-01 16:00 | 70.56 | 67.81
2018-12-01 16:30 | 71.77 | 69.06
2018-12-01 17:00 | 72.56 | 69.89
2018-12-01 17:30 | 72.21 | 69.5
2018-12-01 18:00 | 72.48 | 69.76
2018-12-01 18:30 | 72 | 69.23
2018-12-01 19:00 | 72.56 | 69.85
2018-12-01 19:30 | 71.06 | 68.27
2018-12-01 20:00 | 69.5 | 66.63
2018-12-01 20:30 | 69.84 | 66.97
2018-12-01 21:00 | 66.61 | 63.53
2018-12-01 21:30 | 64.47 | 61.22
2018-12-01 22:00 | 62.24 | 58.82
2018-12-01 22:30 | 60.11 | 56.52
2018-12-01 23:00 | 58.53 | 54.8
2018-12-01 23:30 | 56.35 | 52.42
2018-12-02 | 54.39 | 50.24
2018-12-02 00:30 | 52.83 | 48.52
2018-12-02 01:00 | 51.82 | 47.33
2018-12-02 01:30 | 49.91 | 46.26
2018-12-02 02:00 | 46.1 | 45.59
2018-12-02 02:30 | 45.28 | 44.8
2018-12-02 03:00 | 44.88 | 44.42
2018-12-02 03:30 | 44.53 | 44.07
2018-12-02 04:00 | 43.97 | 43.5
2018-12-02 04:30 | 43.85 | 43.38
2018-12-02 05:00 | 43.7 | 43.23
2018-12-02 05:30 | 43.28 | 42.81
2018-12-02 06:00 | 43.37 | 42.89
2018-12-02 06:30 | 45.36 | 44.92
2018-12-02 07:00 | 46.21 | 45.79
2018-12-02 07:30 | 48.36 | 47.97
2018-12-02 08:00 | 50.14 | 49.72
2018-12-02 08:30 | 52.21 | 51.68
2018-12-02 09:00 | 53.91 | 52.52
2018-12-02 09:30 | 57.44 | 54.05
2018-12-02 10:00 | 58.01 | 54.7
2018-12-02 10:30 | 58.9 | 55.7
2018-12-02 11:00 | 59.27 | 56.11
2018-12-02 11:30 | 59.92 | 56.8
2018-12-02 12:00 | 61.25 | 58.17
2018-12-02 12:30 | 63.16 | 60.18
2018-12-02 13:00 | 63.51 | 60.57
2018-12-02 13:30 | 64.28 | 61.38
2018-12-02 14:00 | 65.21 | 62.36
2018-12-02 14:30 | 65.92 | 63.1
2018-12-02 15:00 | 67.09 | 64.32
2018-12-02 15:30 | 68.45 | 65.74
2018-12-02 16:00 | 69.14 | 66.44
2018-12-02 16:30 | 70.52 | 67.89
2018-12-02 17:00 | 71.09 | 68.47
2018-12-02 17:30 | 71.73 | 69.14
2018-12-02 18:00 | 72.01 | 69.43
2018-12-02 18:30 | 70.53 | 67.87
2018-12-02 19:00 | 72.33 | 68.03
2018-12-02 19:30 | 75.88 | 67.98
2018-12-02 20:00 | 74.55 | 66.38
2018-12-02 20:30 | 75.12 | 66.94
2018-12-02 21:00 | 77.1 | 69.16
2018-12-02 21:30 | 71.38 | 62.5
2018-12-02 22:00 | 67.31 | 57.63
2018-12-02 22:30 | 63.9 | 53.52
2018-12-02 23:00 | 62.07 | 51.13
2018-12-02 23:30 | 56.97 | 49.01
2018-12-03 | 49.7 | 47.21
2018-12-03 00:30 | 48.12 | 46.06
2018-12-03 01:00 | 45.36 | 44.82
2018-12-03 01:30 | 44.22 | 44.14
2018-12-03 02:00 | 44.04 | 43.97
2018-12-03 02:30 | 43.42 | 43.36
2018-12-03 03:00 | 42.9 | 42.85
2018-12-03 03:30 | 42.75 | 42.7
2018-12-03 04:00 | 42.3 | 42.25
2018-12-03 04:30 | 42.88 | 42.82
2018-12-03 05:00 | 43.7 | 43.6
2018-12-03 05:30 | 45.78 | 45.64
2018-12-03 06:00 | 49.26 | 48.92
2018-12-03 06:30 | 56.89 | 55.93
2018-12-03 07:00 | 62.69 | 61.17
2018-12-03 07:30 | 69.78 | 68.1
2018-12-03 08:00 | 73.76 | 71.56
2018-12-03 08:30 | 76.09 | 74.57
2018-12-03 09:00 | 77.34 | 76.14
2018-12-03 09:30 | 78.4 | 77.24
2018-12-03 10:00 | 79.05 | 77.91
2018-12-03 10:30 | 80.36 | 79.27
2018-12-03 11:00 | 81.54 | 79.92
2018-12-03 11:30 | 85.16 | 80.94
2018-12-03 12:00 | 86.53 | 82.17
2018-12-03 12:30 | 87.94 | 83.68
2018-12-03 13:00 | 89.73 | 83.97
2018-12-03 13:30 | 93.74 | 84.73
2018-12-03 14:00 | 93.16 | 85.74
2018-12-03 14:30 | 89.34 | 86.9
2018-12-03 15:00 | 89.62 | 87.16
2018-12-03 15:30 | 91.1 | 88.67
2018-12-03 16:00 | 90.02 | 87.49
2018-12-03 16:30 | 89.35 | 86.74
2018-12-03 17:00 | 88.41 | 85.79
2018-12-03 17:30 | 81.72 | 81.38
2018-12-03 18:00 | 79.63 | 79.29
2018-12-03 18:30 | 78.37 | 78
2018-12-03 19:00 | 78.1 | 77.73
2018-12-03 19:30 | 76.69 | 76.3
2018-12-03 20:00 | 74.66 | 74.25
2018-12-03 20:30 | 73.02 | 72.51
2018-12-03 21:00 | 72.6 | 72
2018-12-03 21:30 | 69.3 | 68.36
2018-12-03 22:00 | 61.5 | 59.63
2018-12-03 22:30 | 55.48 | 52.25
2018-12-03 23:00 | 53.02 | 49.69
2018-12-03 23:30 | 50.08 | 46.58
2018-12-04 | 48.3 | 44.65
2018-12-04 00:30 | 47.14 | 43.16
2018-12-04 01:00 | 46.25 | 41.99
2018-12-04 01:30 | 45.7 | 41.32
2018-12-04 02:00 | 45.32 | 40.86
2018-12-04 02:30 | 44.76 | 40.26
2018-12-04 03:00 | 44.21 | 39.66
2018-12-04 03:30 | 43.35 | 38.71
2018-12-04 04:00 | 42.96 | 38.64
2018-12-04 04:30 | 41.3 | 39.27
2018-12-04 05:00 | 41.78 | 39.77
2018-12-04 05:30 | 43.35 | 41.4
2018-12-04 06:00 | 45.1 | 45.07
2018-12-04 06:30 | 51.92 | 51.85
2018-12-04 07:00 | 57.73 | 57.5
2018-12-04 07:30 | 64.74 | 63.91
2018-12-04 08:00 | 68.46 | 67.57
2018-12-04 08:30 | 70.26 | 70.22
2018-12-04 09:00 | 72.73 | 72.73
2018-12-04 09:30 | 73.07 | 73.07
2018-12-04 10:00 | 73.69 | 73.68
2018-12-04 10:30 | 74.64 | 74.61
2018-12-04 11:00 | 75.48 | 75.43
2018-12-04 11:30 | 77.07 | 76.98
2018-12-04 12:00 | 78.3 | 78.18
2018-12-04 12:30 | 79.43 | 79.32
2018-12-04 13:00 | 79.31 | 79.22
2018-12-04 13:30 | 80.34 | 80.24
2018-12-04 14:00 | 81.13 | 81.04
2018-12-04 14:30 | 82.02 | 81.92
2018-12-04 15:00 | 82.83 | 82.73
2018-12-04 15:30 | 83.72 | 83.65
2018-12-04 16:00 | 84.84 | 84.81
2018-12-04 16:30 | 87.18 | 87.18
2018-12-04 17:00 | 84.24 | 84.21
2018-12-04 17:30 | 80.98 | 80.76
2018-12-04 18:00 | 79.16 | 78.71
2018-12-04 18:30 | 76.14 | 75.34
2018-12-04 19:00 | 74.41 | 73.45
2018-12-04 19:30 | 73.63 | 72.61
2018-12-04 20:00 | 75.75 | 74.72
2018-12-04 20:30 | 72.46 | 71.15
2018-12-04 21:00 | 67.62 | 65.82
2018-12-04 21:30 | 64.2 | 62
2018-12-04 22:00 | 59.46 | 57.98
2018-12-04 22:30 | 55.11 | 53.51
2018-12-04 23:00 | 51.88 | 50.2
2018-12-04 23:30 | 48.53 | 46.72
2018-12-05 | 46.46 | 44.58
2018-12-05 00:30 | 44.05 | 42.12
2018-12-05 01:00 | 43.42 | 41.47
2018-12-05 01:30 | 42.89 | 40.9
2018-12-05 02:00 | 41.85 | 39.81
2018-12-05 02:30 | 41.28 | 39.23
2018-12-05 03:00 | 40.66 | 38.45
2018-12-05 03:30 | 40.44 | 38.13
2018-12-05 04:00 | 40.45 | 38.14
2018-12-05 04:30 | 40.99 | 38.71
2018-12-05 05:00 | 42.01 | 39.77
2018-12-05 05:30 | 44.22 | 42.09
2018-12-05 06:00 | 47.13 | 45.12
2018-12-05 06:30 | 52.14 | 50.6
2018-12-05 07:00 | 55.4 | 55.33
2018-12-05 07:30 | 62.59 | 62.2
2018-12-05 08:00 | 67.49 | 66.74
2018-12-05 08:30 | 67.67 | 66.56
2018-12-05 09:00 | 73.35 | 71.9
2018-12-05 09:30 | 75.21 | 73.75
2018-12-05 10:00 | 73.29 | 71.96
2018-12-05 10:30 | 73.47 | 72
2018-12-05 11:00 | 73.21 | 71.55
2018-12-05 11:30 | 74.36 | 72.65
2018-12-05 12:00 | 72.56 | 70.78
2018-12-05 12:30 | 71.84 | 69.95
2018-12-05 13:00 | 71.62 | 69.7
2018-12-05 13:30 | 74.91 | 72.94
2018-12-05 14:00 | 75.25 | 73.32
2018-12-05 14:30 | 74.58 | 72.77
2018-12-05 15:00 | 72.7 | 71.07
2018-12-05 15:30 | 73.77 | 72.44
2018-12-05 16:00 | 71.53 | 70.37
2018-12-05 16:30 | 70.86 | 69.65
2018-12-05 17:00 | 69.73 | 68.45
2018-12-05 17:30 | 67.17 | 65.79
2018-12-05 18:00 | 66.59 | 65.2
2018-12-05 18:30 | 65.24 | 63.77
2018-12-05 19:00 | 65.94 | 64.5
2018-12-05 19:30 | 64.74 | 63.25
2018-12-05 20:00 | 62.95 | 61.4
2018-12-05 20:30 | 61.45 | 59.83
2018-12-05 21:00 | 60 | 58.32
2018-12-05 21:30 | 57.08 | 55.28
2018-12-05 22:00 | 54.32 | 52.49
2018-12-05 22:30 | 50.44 | 49.9
2018-12-05 23:00 | 49.46 | 48.9
2018-12-05 23:30 | 47.12 | 46.52
2018-12-06 | 45.19 | 44.55
2018-12-06 00:30 | 43.25 | 42.58
2018-12-06 01:00 | 41.64 | 40.93
2018-12-06 01:30 | 40.63 | 39.9
2018-12-06 02:00 | 40.13 | 39.39
2018-12-06 02:30 | 39.21 | 38.42
2018-12-06 03:00 | 38.49 | 37.61
2018-12-06 03:30 | 38.39 | 37.51
2018-12-06 04:00 | 38.48 | 37.59
2018-12-06 04:30 | 39.26 | 38.46
2018-12-06 05:00 | 40.13 | 39.38
2018-12-06 05:30 | 42.14 | 41.43
2018-12-06 06:00 | 45.04 | 44.41
2018-12-06 06:30 | 50.88 | 50.38
2018-12-06 07:00 | 54.86 | 54.45
2018-12-06 07:30 | 60.33 | 60
2018-12-06 08:00 | 65.62 | 63.83
2018-12-06 08:30 | 70.26 | 67.45
2018-12-06 09:00 | 68.86 | 66.03
2018-12-06 09:30 | 70.66 | 67.91
2018-12-06 10:00 | 71.36 | 68.63
2018-12-06 10:30 | 68.8 | 65.97
2018-12-06 11:00 | 71.55 | 68.87
2018-12-06 11:30 | 71.6 | 68.91
2018-12-06 12:00 | 70.79 | 68.07
2018-12-06 12:30 | 70.67 | 67.9
2018-12-06 13:00 | 68.58 | 65.67
2018-12-06 13:30 | 69.17 | 66.29
2018-12-06 14:00 | 69.11 | 66.22
2018-12-06 14:30 | 68.22 | 65.28
2018-12-06 15:00 | 66.42 | 63.37
2018-12-06 15:30 | 66.48 | 63.38
2018-12-06 16:00 | 66.1 | 62.91
2018-12-06 16:30 | 64.17 | 60.76
2018-12-06 17:00 | 62.87 | 59.29
2018-12-06 17:30 | 60.69 | 56.9
2018-12-06 18:00 | 59.89 | 55.97
2018-12-06 18:30 | 59.26 | 55.25
2018-12-06 19:00 | 60.06 | 56.12
2018-12-06 19:30 | 58.1 | 53.97
2018-12-06 20:00 | 56.52 | 52.21
2018-12-06 20:30 | 53.92 | 49.78
2018-12-06 21:00 | 52.47 | 48.19
2018-12-06 21:30 | 50.33 | 45.78
2018-12-06 22:00 | 48.48 | 43.69
2018-12-06 22:30 | 46.51 | 41.44
2018-12-06 23:00 | 45.86 | 40.67
2018-12-06 23:30 | 44.12 | 38.66
2018-12-07 | 42.87 | 37.19
2018-12-07 00:30 | 41.86 | 36.01
2018-12-07 01:00 | 41.02 | 35.3
2018-12-07 01:30 | 40.53 | 34.71
2018-12-07 02:00 | 40.07 | 34.15
2018-12-07 02:30 | 39.54 | 33.49
2018-12-07 03:00 | 38.93 | 32.75
2018-12-07 03:30 | 38.95 | 32.75
2018-12-07 04:00 | 39.01 | 32.81
2018-12-07 04:30 | 39.72 | 33.69
2018-12-07 05:00 | 40.77 | 35
2018-12-07 05:30 | 42.7 | 37.29
2018-12-07 06:00 | 44.98 | 39.97
2018-12-07 06:30 | 50.32 | 46.11
2018-12-07 07:00 | 54.94 | 51.09
2018-12-07 07:30 | 58.81 | 55.34
2018-12-07 08:00 | 59.81 | 56.33
2018-12-07 08:30 | 59.88 | 56.21
2018-12-07 09:00 | 60.74 | 57.18
2018-12-07 09:30 | 63.47 | 60.11
2018-12-07 10:00 | 63.43 | 60.11
2018-12-07 10:30 | 63.36 | 60.08
2018-12-07 11:00 | 64.96 | 61.83
2018-12-07 11:30 | 64.63 | 61.51
2018-12-07 12:00 | 63.86 | 60.72
2018-12-07 12:30 | 65.36 | 62.3
2018-12-07 13:00 | 64.1 | 60.96
2018-12-07 13:30 | 64.74 | 61.61
2018-12-07 14:00 | 66.77 | 63.71
2018-12-07 14:30 | 65.54 | 62.36
2018-12-07 15:00 | 63.12 | 59.75
2018-12-07 15:30 | 62.12 | 58.62
2018-12-07 16:00 | 62.51 | 58.99
2018-12-07 16:30 | 61.83 | 58.19
2018-12-07 17:00 | 60.95 | 57.11
2018-12-07 17:30 | 55.74 | 54.76
2018-12-07 18:00 | 54.21 | 53.84
2018-12-07 18:30 | 53.41 | 53.04
2018-12-07 19:00 | 52.91 | 52.53
2018-12-07 19:30 | 52.04 | 51.65
2018-12-07 20:00 | 50.39 | 49.98
2018-12-07 20:30 | 48.12 | 47.67
2018-12-07 21:00 | 46.6 | 46.13
2018-12-07 21:30 | 44.96 | 44.47
2018-12-07 22:00 | 43.24 | 42.71
2018-12-07 22:30 | 41.23 | 40.66
2018-12-07 23:00 | 40.07 | 39.47
2018-12-07 23:30 | 38.54 | 37.91
2018-12-08 | 37.14 | 36.48
2018-12-08 00:30 | 35.83 | 35.23
2018-12-08 01:00 | 34.72 | 34.08
2018-12-08 01:30 | 34.21 | 33.57
2018-12-08 02:00 | 34 | 33.36
2018-12-08 02:30 | 33.56 | 32.91
2018-12-08 03:00 | 32.7 | 32.02
2018-12-08 03:30 | 32.67 | 31.99
2018-12-08 04:00 | 32.22 | 31.52
2018-12-08 04:30 | 32.53 | 31.85
2018-12-08 05:00 | 32.73 | 32.05
2018-12-08 05:30 | 33.68 | 33.01
2018-12-08 06:00 | 34.69 | 34.05
2018-12-08 06:30 | 37.03 | 36.46
2018-12-08 07:00 | 38.23 | 37.69
2018-12-08 07:30 | 40.02 | 39.53
2018-12-08 08:00 | 42.39 | 41.91
2018-12-08 08:30 | 44.92 | 44.24
2018-12-08 09:00 | 46.62 | 45.75
2018-12-08 09:30 | 47.77 | 46.86
2018-12-08 10:00 | 47.34 | 46.67
2018-12-08 10:30 | 48.15 | 47.73
2018-12-08 11:00 | 47.94 | 47.47
2018-12-08 11:30 | 46.63 | 46.18
2018-12-08 12:00 | 47.12 | 46.69
2018-12-08 12:30 | 48.88 | 48.48
2018-12-08 13:00 | 46.29 | 45.85
2018-12-08 13:30 | 45.9 | 45.46
2018-12-08 14:00 | 46.82 | 46.38
2018-12-08 14:30 | 46.01 | 45.55
2018-12-08 15:00 | 45.98 | 45.51
2018-12-08 15:30 | 46.15 | 45.69
2018-12-08 16:00 | 46.59 | 46.13
2018-12-08 16:30 | 46.78 | 46.3
2018-12-08 17:00 | 46.87 | 46.39
2018-12-08 17:30 | 47.3 | 46.83
2018-12-08 18:00 | 48.43 | 47.97
2018-12-08 18:30 | 47.72 | 47.25
2018-12-08 19:00 | 48.08 | 47.62
2018-12-08 19:30 | 47.21 | 46.74
2018-12-08 20:00 | 46.51 | 46.03
2018-12-08 20:30 | 44.54 | 44.03
2018-12-08 21:00 | 43.55 | 43.02
2018-12-08 21:30 | 42.43 | 41.87
2018-12-08 22:00 | 41.38 | 40.8
2018-12-08 22:30 | 39.33 | 38.71
2018-12-08 23:00 | 39.27 | 38.65
2018-12-08 23:30 | 37.27 | 36.61
2018-12-09 | 36.28 | 35.6
2018-12-09 00:30 | 35.35 | 34.71
2018-12-09 01:00 | 34.07 | 33.43
2018-12-09 01:30 | 33.48 | 32.82
2018-12-09 02:00 | 33.45 | 32.79
2018-12-09 02:30 | 32.71 | 32.03
2018-12-09 03:00 | 32.28 | 31.58
2018-12-09 03:30 | 32.25 | 31.55
2018-12-09 04:00 | 32.19 | 31.49
2018-12-09 04:30 | 32.51 | 31.83
2018-12-09 05:00 | 32.33 | 31.64
2018-12-09 05:30 | 32.81 | 32.13
2018-12-09 06:00 | 33.41 | 32.74
2018-12-09 06:30 | 35.06 | 34.42
2018-12-09 07:00 | 36.25 | 35.64
2018-12-09 07:30 | 38.43 | 37.88
2018-12-09 08:00 | 40.12 | 39.61
2018-12-09 08:30 | 42.01 | 41.54
2018-12-09 09:00 | 45.18 | 44.74
2018-12-09 09:30 | 46.49 | 46.01
2018-12-09 10:00 | 47.04 | 46.44
2018-12-09 10:30 | 47.27 | 46.63
2018-12-09 11:00 | 47.22 | 46.56
2018-12-09 11:30 | 44.75 | 44.12
2018-12-09 12:00 | 43.82 | 43.34
2018-12-09 12:30 | 48.82 | 48.39
2018-12-09 13:00 | 47.81 | 47.36
2018-12-09 13:30 | 45.69 | 45.21
2018-12-09 14:00 | 45.71 | 45.23
2018-12-09 14:30 | 44.7 | 44.21
2018-12-09 15:00 | 42.59 | 42.07
2018-12-09 15:30 | 44.1 | 43.6
2018-12-09 16:00 | 44.99 | 44.49
2018-12-09 16:30 | 44.11 | 43.61
2018-12-09 17:00 | 46.1 | 45.61
2018-12-09 17:30 | 48.18 | 47.72
2018-12-09 18:00 | 50.43 | 49.99
2018-12-09 18:30 | 50.8 | 50.37
2018-12-09 19:00 | 51.16 | 50.74
2018-12-09 19:30 | 49.65 | 49.21
2018-12-09 20:00 | 48.51 | 48.04
2018-12-09 20:30 | 46.59 | 46.1
2018-12-09 21:00 | 44.88 | 44.37
2018-12-09 21:30 | 43.29 | 42.74
2018-12-09 22:00 | 41.7 | 41.13
2018-12-09 22:30 | 39.42 | 38.8
2018-12-09 23:00 | 38.9 | 38.26
2018-12-09 23:30 | 36.76 | 36.08
2018-12-10 | 35.54 | 34.84
2018-12-10 00:30 | 34.76 | 34.11
2018-12-10 01:00 | 34.04 | 33.4
2018-12-10 01:30 | 33.88 | 33.24
2018-12-10 02:00 | 33.69 | 33.04
2018-12-10 02:30 | 33.42 | 32.76
2018-12-10 03:00 | 33.28 | 32.61
2018-12-10 03:30 | 33.37 | 32.7
2018-12-10 04:00 | 33.38 | 32.72
2018-12-10 04:30 | 34.21 | 33.57
2018-12-10 05:00 | 35.22 | 34.61
2018-12-10 05:30 | 36.84 | 36.27
2018-12-10 06:00 | 39.59 | 39.08
2018-12-10 06:30 | 45.86 | 45.1
2018-12-10 07:00 | 50.81 | 50.26
2018-12-10 07:30 | 56.22 | 55.45
2018-12-10 08:00 | 59.15 | 58.81
2018-12-10 08:30 | 63.98 | 62.8
2018-12-10 09:00 | 65.14 | 62.01
2018-12-10 09:30 | 65.78 | 62.72
2018-12-10 10:00 | 66.75 | 63.75
2018-12-10 10:30 | 68.18 | 65.27
2018-12-10 11:00 | 67.99 | 65.08
2018-12-10 11:30 | 65.91 | 62.93
2018-12-10 12:00 | 65.54 | 62.57
2018-12-10 12:30 | 67.46 | 64.59
2018-12-10 13:00 | 65.52 | 62.57
2018-12-10 13:30 | 66.27 | 63.38
2018-12-10 14:00 | 67.66 | 64.83
2018-12-10 14:30 | 69.86 | 67.14
2018-12-10 15:00 | 71.85 | 69.18
2018-12-10 15:30 | 68.77 | 65.91
2018-12-10 16:00 | 68.46 | 65.54
2018-12-10 16:30 | 69.09 | 66.15
2018-12-10 17:00 | 67.47 | 64.35
2018-12-10 17:30 | 65.09 | 61.74
2018-12-10 18:00 | 64.29 | 60.81
2018-12-10 18:30 | 62.96 | 59.24
2018-12-10 19:00 | 63.28 | 59.57
2018-12-10 19:30 | 63.15 | 59.43
2018-12-10 20:00 | 61.64 | 57.8
2018-12-10 20:30 | 59.67 | 55.62
2018-12-10 21:00 | 55.65 | 53.77
2018-12-10 21:30 | 51.96 | 51.44
2018-12-10 22:00 | 49.27 | 48.71
2018-12-10 22:30 | 46.15 | 45.53
2018-12-10 23:00 | 45.15 | 44.5
2018-12-10 23:30 | 42.26 | 41.57
2018-12-11 | 40.08 | 39.49
2018-12-11 00:30 | 39.17 | 38.56
2018-12-11 01:00 | 38.27 | 37.65
2018-12-11 01:30 | 37.4 | 36.78
2018-12-11 02:00 | 37.06 | 36.44
2018-12-11 02:30 | 36.45 | 35.82
2018-12-11 03:00 | 36.08 | 35.46
2018-12-11 03:30 | 36.09 | 35.47
2018-12-11 04:00 | 35.97 | 35.34
2018-12-11 04:30 | 36.77 | 36.15
2018-12-11 05:00 | 37.99 | 37.39
2018-12-11 05:30 | 39.78 | 39.21
2018-12-11 06:00 | 42.74 | 42.19
2018-12-11 06:30 | 48.79 | 48.34
2018-12-11 07:00 | 52.97 | 52.59
2018-12-11 07:30 | 58.7 | 58.36
2018-12-11 08:00 | 62.69 | 61.52
2018-12-11 08:30 | 67.23 | 64.29
2018-12-11 09:00 | 66.75 | 63.83
2018-12-11 09:30 | 65.73 | 62.8
2018-12-11 10:00 | 66.36 | 63.49
2018-12-11 10:30 | 66.39 | 63.55
2018-12-11 11:00 | 67.49 | 64.73
2018-12-11 11:30 | 68.39 | 65.66
2018-12-11 12:00 | 68.72 | 66.03
2018-12-11 12:30 | 70.98 | 68.37
2018-12-11 13:00 | 69.41 | 66.73
2018-12-11 13:30 | 72.35 | 68.91
2018-12-11 14:00 | 76.63 | 68.87
2018-12-11 14:30 | 75.23 | 67.25
2018-12-11 15:00 | 76.34 | 68.5
2018-12-11 15:30 | 76.16 | 68.19
2018-12-11 16:00 | 77.35 | 69.41
2018-12-11 16:30 | 78.21 | 70.23
2018-12-11 17:00 | 76.57 | 68.18
2018-12-11 17:30 | 74.79 | 65.89
2018-12-11 18:00 | 73.39 | 64.09
2018-12-11 18:30 | 72.45 | 62.84
2018-12-11 19:00 | 73.52 | 64.14
2018-12-11 19:30 | 73.73 | 64.39
2018-12-11 20:00 | 72.1 | 62.42
2018-12-11 20:30 | 65.77 | 60.13
2018-12-11 21:00 | 61.89 | 58.13
2018-12-11 21:30 | 59.44 | 55.47
2018-12-11 22:00 | 56.72 | 52.45
2018-12-11 22:30 | 54 | 49.4
2018-12-11 23:00 | 50.43 | 47.87
2018-12-11 23:30 | 45.03 | 44.54
2018-12-12 | 42.76 | 42.24
2018-12-12 00:30 | 41.57 | 41.03
2018-12-12 01:00 | 40.57 | 40.01
2018-12-12 01:30 | 39.91 | 39.33
2018-12-12 02:00 | 39.63 | 39.05
2018-12-12 02:30 | 38.93 | 38.32
2018-12-12 03:00 | 38.35 | 37.81
2018-12-12 03:30 | 38.27 | 37.73
2018-12-12 04:00 | 38.39 | 37.85
2018-12-12 04:30 | 39.37 | 38.85
2018-12-12 05:00 | 40.57 | 40.07
2018-12-12 05:30 | 42.24 | 41.77
2018-12-12 06:00 | 45.47 | 44.9
2018-12-12 06:30 | 52.73 | 51.36
2018-12-12 07:00 | 57.03 | 55.57
2018-12-12 07:30 | 63.51 | 62.16
2018-12-12 08:00 | 66.55 | 65.29
2018-12-12 08:30 | 66.21 | 64.98
2018-12-12 09:00 | 67.02 | 64.97
2018-12-12 09:30 | 71.93 | 66.81
2018-12-12 10:00 | 73.39 | 68.39
2018-12-12 10:30 | 74.53 | 69.62
2018-12-12 11:00 | 69.98 | 64.71
2018-12-12 11:30 | 70.38 | 69.36
2018-12-12 12:00 | 71.29 | 70.93
2018-12-12 12:30 | 67.92 | 67.54
2018-12-12 13:00 | 69.42 | 69.04
2018-12-12 13:30 | 71.07 | 70.7
2018-12-12 14:00 | 69.49 | 69.1
2018-12-12 14:30 | 67.92 | 67.51
2018-12-12 15:00 | 69.28 | 68.89
2018-12-12 15:30 | 69.76 | 69.36
2018-12-12 16:00 | 68.29 | 67.86
2018-12-12 16:30 | 68.36 | 67.76
2018-12-12 17:00 | 65.99 | 65.04
2018-12-12 17:30 | 64.09 | 62.59
2018-12-12 18:00 | 63.17 | 61.19
2018-12-12 18:30 | 63 | 60.67
2018-12-12 19:00 | 63.8 | 61.55
2018-12-12 19:30 | 63.43 | 61.05
2018-12-12 20:00 | 62.23 | 59.67
2018-12-12 20:30 | 60.23 | 57.21
2018-12-12 21:00 | 58.58 | 55.25
2018-12-12 21:30 | 56.72 | 52.95
2018-12-12 22:00 | 54.69 | 50.39
2018-12-12 22:30 | 52.2 | 47.2
2018-12-12 23:00 | 46.21 | 45.72
2018-12-12 23:30 | 43.69 | 43.23
2018-12-13 | 42.35 | 41.83
2018-12-13 00:30 | 41.11 | 40.51
2018-12-13 01:00 | 40.1 | 39.43
2018-12-13 01:30 | 39.63 | 38.93
2018-12-13 02:00 | 38.83 | 38.05
2018-12-13 02:30 | 37.66 | 37.07
2018-12-13 03:00 | 37.35 | 36.82
2018-12-13 03:30 | 37.53 | 37
2018-12-13 04:00 | 37.47 | 36.93
2018-12-13 04:30 | 38.39 | 37.86
2018-12-13 05:00 | 39.66 | 39.15
2018-12-13 05:30 | 41.77 | 41.28
2018-12-13 06:00 | 44.63 | 44.16
2018-12-13 06:30 | 50.62 | 50.18
2018-12-13 07:00 | 55.77 | 55.39
2018-12-13 07:30 | 61.43 | 61.08
2018-12-13 08:00 | 64.09 | 63.52
2018-12-13 08:30 | 68.66 | 65.81
2018-12-13 09:00 | 66.69 | 63.84
2018-12-13 09:30 | 71.51 | 68.86
2018-12-13 10:00 | 71.74 | 68.67
2018-12-13 10:30 | 72.2 | 68.9
2018-12-13 11:00 | 72.39 | 69.16
2018-12-13 11:30 | 73.45 | 70.31
2018-12-13 12:00 | 74.08 | 70.97
2018-12-13 12:30 | 77.94 | 75.01
2018-12-13 13:00 | 77.41 | 74.44
2018-12-13 13:30 | 79.75 | 76.88
2018-12-13 14:00 | 82.08 | 79.28
2018-12-13 14:30 | 81.22 | 78.37
2018-12-13 15:00 | 75.95 | 72.72
2018-12-13 15:30 | 71.37 | 68.74
2018-12-13 16:00 | 66.55 | 65.73
2018-12-13 16:30 | 63.33 | 62.24
2018-12-13 17:00 | 63.16 | 61.73
2018-12-13 17:30 | 61.89 | 59.93
2018-12-13 18:00 | 61.99 | 59.68
2018-12-13 18:30 | 61.96 | 59.27
2018-12-13 19:00 | 62.98 | 60.51
2018-12-13 19:30 | 62.39 | 59.76
2018-12-13 20:00 | 60.72 | 57.83
2018-12-13 20:30 | 57.52 | 55.36
2018-12-13 21:00 | 54.1 | 53.74
2018-12-13 21:30 | 52.15 | 51.78
2018-12-13 22:00 | 49.09 | 48.71
2018-12-13 22:30 | 46.46 | 46.06
2018-12-13 23:00 | 45.36 | 44.94
2018-12-13 23:30 | 42.07 | 41.48
2018-12-14 | 40.18 | 39.58
2018-12-14 00:30 | 38.78 | 38.27
2018-12-14 01:00 | 37.73 | 37.19
2018-12-14 01:30 | 36.8 | 36.26
2018-12-14 02:00 | 36.23 | 35.68
2018-12-14 02:30 | 35.47 | 34.92
2018-12-14 03:00 | 35 | 34.4
2018-12-14 03:30 | 34.86 | 34.21
2018-12-14 04:00 | 34.9 | 34.2
2018-12-14 04:30 | 35.65 | 34.97
2018-12-14 05:00 | 36.93 | 36.29
2018-12-14 05:30 | 38.6 | 38.06
2018-12-14 06:00 | 41.34 | 40.85
2018-12-14 06:30 | 48.04 | 47.38
2018-12-14 07:00 | 52.25 | 51.63
2018-12-14 07:30 | 58.55 | 56.47
2018-12-14 08:00 | 60.32 | 59.23
2018-12-14 08:30 | 62.18 | 61.58
2018-12-14 09:00 | 64.86 | 64.41
2018-12-14 09:30 | 67.16 | 66.73
2018-12-14 10:00 | 65.61 | 65.18
2018-12-14 10:30 | 65.94 | 65.52
2018-12-14 11:00 | 64.83 | 64.41
2018-12-14 11:30 | 68.62 | 68.23
2018-12-14 12:00 | 67.41 | 67.04
2018-12-14 12:30 | 71.54 | 71.18
2018-12-14 13:00 | 71.66 | 71.3
2018-12-14 13:30 | 70.12 | 69.75
2018-12-14 14:00 | 72.75 | 72.38
2018-12-14 14:30 | 71.3 | 70.92
2018-12-14 15:00 | 72.6 | 72.22
2018-12-14 15:30 | 74.23 | 73.85
2018-12-14 16:00 | 75.23 | 74.85
2018-12-14 16:30 | 75.59 | 75.2
2018-12-14 17:00 | 74.13 | 73.57
2018-12-14 17:30 | 70.87 | 69.91
2018-12-14 18:00 | 69.22 | 67.83
2018-12-14 18:30 | 67.64 | 65.82
2018-12-14 19:00 | 67.44 | 65.65
2018-12-14 19:30 | 67.53 | 65.77
2018-12-14 20:00 | 66.15 | 64.2
2018-12-14 20:30 | 63.65 | 61.28
2018-12-14 21:00 | 61.95 | 59.34
2018-12-14 21:30 | 60.16 | 57.14
2018-12-14 22:00 | 58.43 | 54.87
2018-12-14 22:30 | 55.67 | 51.54
2018-12-14 23:00 | 54.73 | 50.27
2018-12-14 23:30 | 52.1 | 46.89
2018-12-15 | 50.61 | 44.82
2018-12-15 00:30 | 47.18 | 42.86
2018-12-15 01:00 | 42.76 | 41.36
2018-12-15 01:30 | 41.12 | 40.55
2018-12-15 02:00 | 40.55 | 39.98
2018-12-15 02:30 | 39.83 | 39.24
2018-12-15 03:00 | 39.29 | 38.7
2018-12-15 03:30 | 38.78 | 38.18
2018-12-15 04:00 | 38.75 | 38.16
2018-12-15 04:30 | 38.91 | 38.32
2018-12-15 05:00 | 39.2 | 38.61
2018-12-15 05:30 | 39.95 | 39.37
2018-12-15 06:00 | 40.41 | 39.83
2018-12-15 06:30 | 42.82 | 42.27
2018-12-15 07:00 | 45.03 | 44.49
2018-12-15 07:30 | 47.97 | 47.44
2018-12-15 08:00 | 51.95 | 51.45
2018-12-15 08:30 | 55.12 | 54.56
2018-12-15 09:00 | 55.27 | 54.59
2018-12-15 09:30 | 56.04 | 55.23
2018-12-15 10:00 | 56.77 | 55.93
2018-12-15 10:30 | 55.84 | 54.93
2018-12-15 11:00 | 56 | 54.97
2018-12-15 11:30 | 56.35 | 55.31
2018-12-15 12:00 | 57.65 | 56.73
2018-12-15 12:30 | 58.42 | 57.67
2018-12-15 13:00 | 56.81 | 56.17
2018-12-15 13:30 | 54.38 | 53.83
2018-12-15 14:00 | 55.35 | 54.84
2018-12-15 14:30 | 53.46 | 52.96
2018-12-15 15:00 | 53.53 | 53.06
2018-12-15 15:30 | 53.13 | 52.6
2018-12-15 16:00 | 55.06 | 54.58
2018-12-15 16:30 | 55.8 | 55.39
2018-12-15 17:00 | 56.61 | 56.24
2018-12-15 17:30 | 56.43 | 56.07
2018-12-15 18:00 | 56.63 | 56.28
2018-12-15 18:30 | 56.55 | 56.2
2018-12-15 19:00 | 57.13 | 56.78
2018-12-15 19:30 | 57.3 | 56.95
2018-12-15 20:00 | 56.26 | 55.91
2018-12-15 20:30 | 54.78 | 54.41
2018-12-15 21:00 | 53.3 | 52.92
2018-12-15 21:30 | 51.14 | 50.73
2018-12-15 22:00 | 49.29 | 48.85
2018-12-15 22:30 | 46.91 | 46.43
2018-12-15 23:00 | 46.51 | 46.02
2018-12-15 23:30 | 44.17 | 43.65
2018-12-16 | 42.26 | 41.7
2018-12-16 00:30 | 40.66 | 40.06
2018-12-16 01:00 | 39.47 | 38.85
2018-12-16 01:30 | 39.28 | 38.66
2018-12-16 02:00 | 38.34 | 37.7
2018-12-16 02:30 | 37.87 | 37.22
2018-12-16 03:00 | 37.33 | 36.66
2018-12-16 03:30 | 37.1 | 36.42
2018-12-16 04:00 | 37.06 | 36.39
2018-12-16 04:30 | 37.18 | 36.5
2018-12-16 05:00 | 37.42 | 36.76
2018-12-16 05:30 | 37.59 | 36.92
2018-12-16 06:00 | 37.79 | 37.12
2018-12-16 06:30 | 39.58 | 38.95
2018-12-16 07:00 | 40.94 | 40.34
2018-12-16 07:30 | 43.5 | 42.96
2018-12-16 08:00 | 45.26 | 44.76
2018-12-16 08:30 | 47.69 | 47.23
2018-12-16 09:00 | 51.21 | 50.79
2018-12-16 09:30 | 51.97 | 51.56
2018-12-16 10:00 | 50.55 | 50.13
2018-12-16 10:30 | 48.45 | 48.02
2018-12-16 11:00 | 46.43 | 45.97
2018-12-16 11:30 | 46.78 | 46.34
2018-12-16 12:00 | 47.92 | 47.5
2018-12-16 12:30 | 53.15 | 52.77
2018-12-16 13:00 | 50.47 | 50.07
2018-12-16 13:30 | 48.24 | 47.82
2018-12-16 14:00 | 50.85 | 50.46
2018-12-16 14:30 | 50.87 | 50.47
2018-12-16 15:00 | 51.44 | 51.04
2018-12-16 15:30 | 51.72 | 51.32
2018-12-16 16:00 | 50.76 | 50.34
2018-12-16 16:30 | 53.03 | 52.63
2018-12-16 17:00 | 54.39 | 54
2018-12-16 17:30 | 54.7 | 54.32
2018-12-16 18:00 | 54.71 | 54.32
2018-12-16 18:30 | 54.24 | 53.84
2018-12-16 19:00 | 54.61 | 54.22
2018-12-16 19:30 | 54.8 | 54.41
2018-12-16 20:00 | 53.84 | 53.45
2018-12-16 20:30 | 51.74 | 51.32
2018-12-16 21:00 | 49.7 | 49.24
2018-12-16 21:30 | 47.42 | 46.93
2018-12-16 22:00 | 45.34 | 44.81
2018-12-16 22:30 | 42.69 | 42.12
2018-12-16 23:00 | 42.32 | 41.74
2018-12-16 23:30 | 39.82 | 39.19
2018-12-17 | 37.89 | 37.22
2018-12-17 00:30 | 36.65 | 36.03
2018-12-17 01:00 | 35.49 | 34.85
2018-12-17 01:30 | 34.91 | 34.26
2018-12-17 02:00 | 34.49 | 33.82
2018-12-17 02:30 | 34.32 | 33.66
2018-12-17 03:00 | 33.99 | 33.31
2018-12-17 03:30 | 33.99 | 33.32
2018-12-17 04:00 | 34.08 | 33.41
2018-12-17 04:30 | 35.32 | 34.68
2018-12-17 05:00 | 36.23 | 35.61
2018-12-17 05:30 | 38.35 | 37.78
2018-12-17 06:00 | 41.21 | 40.71
2018-12-17 06:30 | 47.53 | 46.73
2018-12-17 07:00 | 52.22 | 51.53
2018-12-17 07:30 | 58.49 | 57.87
2018-12-17 08:00 | 61.66 | 60.95
2018-12-17 08:30 | 63.32 | 62.26
2018-12-17 09:00 | 67.96 | 65.9
2018-12-17 09:30 | 69.34 | 66.34
2018-12-17 10:00 | 68.74 | 65.71
2018-12-17 10:30 | 69.26 | 66.28
2018-12-17 11:00 | 68.1 | 65.1
2018-12-17 11:30 | 71.69 | 68.88
2018-12-17 12:00 | 71.03 | 68.21
2018-12-17 12:30 | 69.5 | 66.61
2018-12-17 13:00 | 70.43 | 67.59
2018-12-17 13:30 | 69.83 | 66.99
2018-12-17 14:00 | 71.83 | 69.08
2018-12-17 14:30 | 73.78 | 71.11
2018-12-17 15:00 | 74.44 | 71.79
2018-12-17 15:30 | 75.05 | 72.39
2018-12-17 16:00 | 73.25 | 70.48
2018-12-17 16:30 | 70.51 | 67.57
2018-12-17 17:00 | 70.61 | 67.59
2018-12-17 17:30 | 70.02 | 66.87
2018-12-17 18:00 | 70.12 | 66.89
2018-12-17 18:30 | 68.72 | 65.67
2018-12-17 19:00 | 68.74 | 65.71
2018-12-17 19:30 | 68.69 | 65.66
2018-12-17 20:00 | 67.07 | 63.92
2018-12-17 20:30 | 64.12 | 60.74
2018-12-17 21:00 | 62.15 | 58.6
2018-12-17 21:30 | 59.26 | 55.48
2018-12-17 22:00 | 56.4 | 52.4
2018-12-17 22:30 | 53.4 | 49.08
2018-12-17 23:00 | 52.22 | 47.74
2018-12-17 23:30 | 48.01 | 44.09
2018-12-18 | 42.44 | 41.88
2018-12-18 00:30 | 40.95 | 40.37
2018-12-18 01:00 | 39.61 | 38.99
2018-12-18 01:30 | 38.24 | 37.6
2018-12-18 02:00 | 37.46 | 36.8
2018-12-18 02:30 | 36.42 | 35.73
2018-12-18 03:00 | 35.6 | 34.91
2018-12-18 03:30 | 35.4 | 34.77
2018-12-18 04:00 | 35.16 | 34.52
2018-12-18 04:30 | 35.65 | 35.02
2018-12-18 05:00 | 36.97 | 36.38
2018-12-18 05:30 | 38.68 | 38.12
2018-12-18 06:00 | 41.32 | 40.83
2018-12-18 06:30 | 47.8 | 46.99
2018-12-18 07:00 | 52.07 | 51.41
2018-12-18 07:30 | 57.18 | 56.32
2018-12-18 08:00 | 59.8 | 59.3
2018-12-18 08:30 | 62.06 | 61.74
2018-12-18 09:00 | 64.84 | 64.53
2018-12-18 09:30 | 65.33 | 65.02
2018-12-18 10:00 | 64.58 | 64.27
2018-12-18 10:30 | 64.91 | 64.6
2018-12-18 11:00 | 62.71 | 62.38
2018-12-18 11:30 | 62.37 | 62.03
2018-12-18 12:00 | 62.21 | 61.88
2018-12-18 12:30 | 63.01 | 62.71
2018-12-18 13:00 | 62.11 | 61.81
2018-12-18 13:30 | 63.63 | 63.33
2018-12-18 14:00 | 64.56 | 64.27
2018-12-18 14:30 | 62.95 | 62.6
2018-12-18 15:00 | 65.84 | 65.56
2018-12-18 15:30 | 63.21 | 62.9
2018-12-18 16:00 | 69.2 | 68.94
2018-12-18 16:30 | 70.64 | 70.38
2018-12-18 17:00 | 70.84 | 70.4
2018-12-18 17:30 | 68.67 | 68.31
2018-12-18 18:00 | 68.51 | 68.05
2018-12-18 18:30 | 67.09 | 66.3
2018-12-18 19:00 | 66.7 | 65.8
2018-12-18 19:30 | 66.83 | 65.96
2018-12-18 20:00 | 65.53 | 64.49
2018-12-18 20:30 | 63.06 | 61.76
2018-12-18 21:00 | 61.54 | 60.12
2018-12-18 21:30 | 58.56 | 56.74
2018-12-18 22:00 | 56.01 | 53.79
2018-12-18 22:30 | 52.5 | 50.18
2018-12-18 23:00 | 49.88 | 47.99
2018-12-18 23:30 | 46.9 | 44.62
2018-12-19 | 44.88 | 42.25
2018-12-19 00:30 | 43.34 | 40.33
2018-12-19 01:00 | 40.92 | 38.79
2018-12-19 01:30 | 39.82 | 37.85
2018-12-19 02:00 | 38.32 | 37.62
2018-12-19 02:30 | 37.71 | 37.4
2018-12-19 03:00 | 37.1 | 36.84
2018-12-19 03:30 | 36.98 | 36.72
2018-12-19 04:00 | 36.71 | 36.45
2018-12-19 04:30 | 37.24 | 36.95
2018-12-19 05:00 | 38.39 | 38.06
2018-12-19 05:30 | 40.03 | 39.67
2018-12-19 06:00 | 42.91 | 42.36
2018-12-19 06:30 | 49.92 | 49
2018-12-19 07:00 | 53.78 | 52.93
2018-12-19 07:30 | 60.91 | 59.6
2018-12-19 08:00 | 63.24 | 61.9
2018-12-19 08:30 | 66.99 | 65.24
2018-12-19 09:00 | 69.08 | 66.97
2018-12-19 09:30 | 72.47 | 68.11
2018-12-19 10:00 | 73.37 | 68.57
2018-12-19 10:30 | 73.21 | 68.46
2018-12-19 11:00 | 73.56 | 68.89
2018-12-19 11:30 | 73.65 | 69.01
2018-12-19 12:00 | 74.56 | 69.89
2018-12-19 12:30 | 73.23 | 68.35
2018-12-19 13:00 | 73.68 | 68.76
2018-12-19 13:30 | 72.49 | 69.88
2018-12-19 14:00 | 72.33 | 70.94
2018-12-19 14:30 | 72.74 | 71.35
2018-12-19 15:00 | 73.77 | 72.4
2018-12-19 15:30 | 74.25 | 72.86
2018-12-19 16:00 | 75.1 | 73.7
2018-12-19 16:30 | 75.36 | 73.94
2018-12-19 17:00 | 74.62 | 73.13
2018-12-19 17:30 | 72.8 | 71.26
2018-12-19 18:00 | 71.35 | 69.79
2018-12-19 18:30 | 70.25 | 68.6
2018-12-19 19:00 | 70.11 | 68.44
2018-12-19 19:30 | 70.48 | 68.82
2018-12-19 20:00 | 68.74 | 67.02
2018-12-19 20:30 | 65.25 | 63.94
2018-12-19 21:00 | 63.3 | 62.03
2018-12-19 21:30 | 59.51 | 58.65
2018-12-19 22:00 | 55.77 | 55.73
2018-12-19 22:30 | 52.17 | 52.16
2018-12-19 23:00 | 50.56 | 50.56
2018-12-19 23:30 | 46.89 | 46.89
2018-12-20 | 44.82 | 44.81
2018-12-20 00:30 | 43 | 42.97
2018-12-20 01:00 | 41.36 | 41.29
2018-12-20 01:30 | 40.2 | 40.12
2018-12-20 02:00 | 39.69 | 39.6
2018-12-20 02:30 | 38.76 | 38.75
2018-12-20 03:00 | 38.08 | 38.08
2018-12-20 03:30 | 37.72 | 37.72
2018-12-20 04:00 | 37.75 | 37.75
2018-12-20 04:30 | 38.33 | 38.32
2018-12-20 05:00 | 39.78 | 39.75
2018-12-20 05:30 | 41.38 | 41.34
2018-12-20 06:00 | 44.21 | 44.09
2018-12-20 06:30 | 49.99 | 49.54
2018-12-20 07:00 | 55.25 | 54.29
2018-12-20 07:30 | 61.06 | 60.05
2018-12-20 08:00 | 65.16 | 63.86
2018-12-20 08:30 | 68.55 | 67.02
2018-12-20 09:00 | 68.67 | 67.17
2018-12-20 09:30 | 70.07 | 68.61
2018-12-20 10:00 | 69.56 | 68.11
2018-12-20 10:30 | 69.01 | 67.57
2018-12-20 11:00 | 68.57 | 67.14
2018-12-20 11:30 | 69.51 | 68.11
2018-12-20 12:00 | 69.69 | 68.28
2018-12-20 12:30 | 70.6 | 69.2
2018-12-20 13:00 | 69.16 | 67.73
2018-12-20 13:30 | 69.8 | 68.37
2018-12-20 14:00 | 70.61 | 69.2
2018-12-20 14:30 | 71.04 | 69.63
2018-12-20 15:00 | 72.03 | 70.64
2018-12-20 15:30 | 72.76 | 71.36
2018-12-20 16:00 | 73.38 | 71.96
2018-12-20 16:30 | 73.69 | 72.24
2018-12-20 17:00 | 72.88 | 71.36
2018-12-20 17:30 | 69.17 | 68.61
2018-12-20 18:00 | 69.04 | 68.32
2018-12-20 18:30 | 68.11 | 67.12
2018-12-20 19:00 | 67.91 | 66.86
2018-12-20 19:30 | 68.77 | 67.84
2018-12-20 20:00 | 67.71 | 66.59
2018-12-20 20:30 | 65.77 | 64.41
2018-12-20 21:00 | 64.14 | 62.68
2018-12-20 21:30 | 61.4 | 59.6
2018-12-20 22:00 | 58.64 | 56.46
2018-12-20 22:30 | 54.59 | 52.84
2018-12-20 23:00 | 53.04 | 51.38
2018-12-20 23:30 | 49.35 | 47.57
2018-12-21 | 46.89 | 45.02
2018-12-21 00:30 | 45.31 | 43.38
2018-12-21 01:00 | 43.66 | 41.65
2018-12-21 01:30 | 42.82 | 40.76
2018-12-21 02:00 | 41.98 | 39.88
2018-12-21 02:30 | 40.73 | 38.48
2018-12-21 03:00 | 40.42 | 38.02
2018-12-21 03:30 | 39.96 | 37.54
2018-12-21 04:00 | 40.11 | 37.68
2018-12-21 04:30 | 40.46 | 38.05
2018-12-21 05:00 | 41.03 | 38.66
2018-12-21 05:30 | 42.15 | 39.84
2018-12-21 06:00 | 44.59 | 42.39
2018-12-21 06:30 | 50.24 | 48.69
2018-12-21 07:00 | 53.86 | 53.2
2018-12-21 07:30 | 59.06 | 58.4
2018-12-21 08:00 | 63.33 | 62.48
2018-12-21 08:30 | 65.93 | 64.75
2018-12-21 09:00 | 69.33 | 67.68
2018-12-21 09:30 | 70.21 | 68.52
2018-12-21 10:00 | 70.1 | 68.37
2018-12-21 10:30 | 70.21 | 68.34
2018-12-21 11:00 | 70.55 | 68.61
2018-12-21 11:30 | 70.68 | 68.77
2018-12-21 12:00 | 70.04 | 68.21
2018-12-21 12:30 | 71.1 | 69.38
2018-12-21 13:00 | 70.06 | 68.43
2018-12-21 13:30 | 70.38 | 68.82
2018-12-21 14:00 | 70.5 | 69.01
2018-12-21 14:30 | 70.08 | 68.72
2018-12-21 15:00 | 70.22 | 68.98
2018-12-21 15:30 | 70.97 | 69.83
2018-12-21 16:00 | 72.27 | 71.16
2018-12-21 16:30 | 72.61 | 71.48
2018-12-21 17:00 | 72.92 | 71.78
2018-12-21 17:30 | 71.67 | 70.48
2018-12-21 18:00 | 70.68 | 69.43
2018-12-21 18:30 | 69.47 | 68.17
2018-12-21 19:00 | 68.3 | 66.97
2018-12-21 19:30 | 68.93 | 67.62
2018-12-21 20:00 | 67.7 | 66.35
2018-12-21 20:30 | 65.48 | 64.01
2018-12-21 21:00 | 63.12 | 61.67
2018-12-21 21:30 | 60.76 | 59.24
2018-12-21 22:00 | 57.87 | 56.23
2018-12-21 22:30 | 54.64 | 52.88
2018-12-21 23:00 | 53.66 | 51.85
2018-12-21 23:30 | 50.07 | 48.09
2018-12-22 | 47.14 | 45.41
2018-12-22 00:30 | 43.05 | 43.05
2018-12-22 01:00 | 41.52 | 41.52
2018-12-22 01:30 | 41.01 | 41.01
2018-12-22 02:00 | 40.16 | 40.16
2018-12-22 02:30 | 30.71 | 30.68
2018-12-22 03:00 | 27 | 26.75
2018-12-22 03:30 | 38.96 | 38.81
2018-12-22 04:00 | 38.54 | 38.4
2018-12-22 04:30 | 38.77 | 38.62
2018-12-22 05:00 | 38.81 | 38.65
2018-12-22 05:30 | 38.65 | 38.55
2018-12-22 06:00 | 39.1 | 38.99
2018-12-22 06:30 | 41.36 | 41.13
2018-12-22 07:00 | 43.51 | 43.16
2018-12-22 07:30 | 47.22 | 46.76
2018-12-22 08:00 | 48.44 | 48.21
2018-12-22 08:30 | 51.88 | 51.53
2018-12-22 09:00 | 55.26 | 54.76
2018-12-22 09:30 | 54.73 | 54.13
2018-12-22 10:00 | 53.76 | 53.05
2018-12-22 10:30 | 55.58 | 54.77
2018-12-22 11:00 | 56.28 | 55.41
2018-12-22 11:30 | 57.47 | 56.64
2018-12-22 12:00 | 54.97 | 54.13
2018-12-22 12:30 | 56.92 | 56.12
2018-12-22 13:00 | 56.61 | 55.87
2018-12-22 13:30 | 55.03 | 54.3
2018-12-22 14:00 | 56.46 | 55.75
2018-12-22 14:30 | 58.16 | 57.49
2018-12-22 15:00 | 56.7 | 56.08
2018-12-22 15:30 | 57.4 | 56.83
2018-12-22 16:00 | 59.07 | 58.52
2018-12-22 16:30 | 59.9 | 59.46
2018-12-22 17:00 | 61.12 | 60.73
2018-12-22 17:30 | 61.88 | 61.51
2018-12-22 18:00 | 62.28 | 61.94
2018-12-22 18:30 | 62.13 | 61.84
2018-12-22 19:00 | 61.58 | 61.28
2018-12-22 19:30 | 62.41 | 62.05
2018-12-22 20:00 | 61.17 | 60.84
2018-12-22 20:30 | 58.93 | 58.67
2018-12-22 21:00 | 56.65 | 56.43
2018-12-22 21:30 | 54.43 | 54.25
2018-12-22 22:00 | 52.48 | 52.37
2018-12-22 22:30 | 50.41 | 50.32
2018-12-22 23:00 | 49.38 | 49.33
2018-12-22 23:30 | 46.14 | 46.11
2018-12-23 | 43.86 | 43.85
2018-12-23 00:30 | 41.75 | 41.75
2018-12-23 01:00 | 40.52 | 40.52
2018-12-23 01:30 | 39.47 | 39.47
2018-12-23 02:00 | 38.72 | 38.71
2018-12-23 02:30 | 37.92 | 37.91
2018-12-23 03:00 | 37.26 | 37.16
2018-12-23 03:30 | 37 | 36.89
2018-12-23 04:00 | 36.76 | 36.66
2018-12-23 04:30 | 36.8 | 36.69
2018-12-23 05:00 | 36.74 | 36.63
2018-12-23 05:30 | 36.08 | 36.02
2018-12-23 06:00 | 36.09 | 36.04
2018-12-23 06:30 | 38.08 | 37.98
2018-12-23 07:00 | 38.95 | 38.82
2018-12-23 07:30 | 40.99 | 40.78
2018-12-23 08:00 | 41.95 | 41.64
2018-12-23 08:30 | 43.5 | 43.08
2018-12-23 09:00 | 44.8 | 44.5
2018-12-23 09:30 | 41.84 | 41.54
2018-12-23 10:00 | 47.83 | 47.52
2018-12-23 10:30 | 53.22 | 52.89
2018-12-23 11:00 | 56.37 | 56.1
2018-12-23 11:30 | 54.82 | 54.59
2018-12-23 12:00 | 53.28 | 53.09
2018-12-23 12:30 | 54.75 | 54.57
2018-12-23 13:00 | 51.89 | 51.74
2018-12-23 13:30 | 50.69 | 50.55
2018-12-23 14:00 | 49.22 | 49.09
2018-12-23 14:30 | 47.81 | 47.7
2018-12-23 15:00 | 47.67 | 47.59
2018-12-23 15:30 | 47.3 | 47.18
2018-12-23 16:00 | 47.56 | 47.16
2018-12-23 16:30 | 48.11 | 47.71
2018-12-23 17:00 | 48.11 | 47.73
2018-12-23 17:30 | 48.16 | 47.74
2018-12-23 18:00 | 48.84 | 48.42
2018-12-23 18:30 | 49.72 | 49.32
2018-12-23 19:00 | 50.21 | 49.79
2018-12-23 19:30 | 50.63 | 50.18
2018-12-23 20:00 | 49.63 | 49.2
2018-12-23 20:30 | 48.46 | 48.06
2018-12-23 21:00 | 47.39 | 47.02
2018-12-23 21:30 | 45.64 | 45.32
2018-12-23 22:00 | 44.52 | 44.23
2018-12-23 22:30 | 42.56 | 42.3
2018-12-23 23:00 | 42.78 | 42.56
2018-12-23 23:30 | 39.94 | 39.76
2018-12-24 | 38.32 | 38.17
2018-12-24 00:30 | 37.22 | 37.11
2018-12-24 01:00 | 35.8 | 35.71
2018-12-24 01:30 | 34.87 | 34.79
2018-12-24 02:00 | 34.28 | 34.21
2018-12-24 02:30 | 33.95 | 33.88
2018-12-24 03:00 | 33.73 | 33.67
2018-12-24 03:30 | 33.68 | 33.63
2018-12-24 04:00 | 33.68 | 33.62
2018-12-24 04:30 | 33.91 | 33.83
2018-12-24 05:00 | 34.39 | 34.31
2018-12-24 05:30 | 34.82 | 34.75
2018-12-24 06:00 | 35.98 | 35.9
2018-12-24 06:30 | 39.58 | 39.32
2018-12-24 07:00 | 41.96 | 41.53
2018-12-24 07:30 | 45.65 | 45.13
2018-12-24 08:00 | 46.47 | 46.15
2018-12-24 08:30 | 47.49 | 47.07
2018-12-24 09:00 | 47.17 | 46.65
2018-12-24 09:30 | 47.69 | 47.09
2018-12-24 10:00 | 46.67 | 46
2018-12-24 10:30 | 46.26 | 45.47
2018-12-24 11:00 | 46.17 | 45.32
2018-12-24 11:30 | 47.64 | 46.79
2018-12-24 12:00 | 46.68 | 45.79
2018-12-24 12:30 | 47.54 | 46.7
2018-12-24 13:00 | 46.62 | 45.85
2018-12-24 13:30 | 46.23 | 45.56
2018-12-24 14:00 | 44.95 | 44.3
2018-12-24 14:30 | 45.65 | 45.03
2018-12-24 15:00 | 45.22 | 44.65
2018-12-24 15:30 | 44.82 | 44.36
2018-12-24 16:00 | 46.36 | 45.96
2018-12-24 16:30 | 48.32 | 48
2018-12-24 17:00 | 49.14 | 48.87
2018-12-24 17:30 | 49.7 | 49.51
2018-12-24 18:00 | 49.49 | 49.38
2018-12-24 18:30 | 48.29 | 48.26
2018-12-24 19:00 | 48.71 | 48.69
2018-12-24 19:30 | 49.3 | 49.26
2018-12-24 20:00 | 49.08 | 49.05
2018-12-24 20:30 | 47.56 | 47.54
2018-12-24 21:00 | 46.24 | 46.23
2018-12-24 21:30 | 44.55 | 44.55
2018-12-24 22:00 | 42.85 | 42.85
2018-12-24 22:30 | 41.33 | 41.33
2018-12-24 23:00 | 41.21 | 41.19
2018-12-24 23:30 | 38.19 | 38.13
2018-12-25 | 36.65 | 36.59
2018-12-25 00:30 | 35.48 | 35.44
2018-12-25 01:00 | 33.94 | 33.91
2018-12-25 01:30 | 33.11 | 33.09
2018-12-25 02:00 | 32.48 | 32.47
2018-12-25 02:30 | 31.85 | 31.84
2018-12-25 03:00 | 31.64 | 31.63
2018-12-25 03:30 | 31.63 | 31.61
2018-12-25 04:00 | 31.56 | 31.55
2018-12-25 04:30 | 31.67 | 31.66
2018-12-25 05:00 | 31.91 | 31.89
2018-12-25 05:30 | 32.15 | 32.14
2018-12-25 06:00 | 32.84 | 32.83
2018-12-25 06:30 | 34.41 | 34.38
2018-12-25 07:00 | 35.4 | 35.34
2018-12-25 07:30 | 38.78 | 38.66
2018-12-25 08:00 | 40.11 | 39.94
2018-12-25 08:30 | 39.28 | 39.08
2018-12-25 09:00 | 39.9 | 39.68
2018-12-25 09:30 | 40.4 | 40.17
2018-12-25 10:00 | 39.06 | 38.81
2018-12-25 10:30 | 39.58 | 39.3
2018-12-25 11:00 | 38.11 | 37.84
2018-12-25 11:30 | 37.74 | 37.46
2018-12-25 12:00 | 36.23 | 35.91
2018-12-25 12:30 | 37.36 | 37.04
2018-12-25 13:00 | 36.16 | 35.88
2018-12-25 13:30 | 36.14 | 35.84
2018-12-25 14:00 | 37.43 | 37.16
2018-12-25 14:30 | 35.48 | 35.23
2018-12-25 15:00 | 33.61 | 33.32
2018-12-25 15:30 | 33.29 | 32.98
2018-12-25 16:00 | 30.03 | 29.56
2018-12-25 16:30 | 37.05 | 36.76
2018-12-25 17:00 | 38.46 | 38.25
2018-12-25 17:30 | 38.77 | 38.58
2018-12-25 18:00 | 39.36 | 39.2
2018-12-25 18:30 | 39.18 | 39.1
2018-12-25 19:00 | 39.94 | 39.85
2018-12-25 19:30 | 41.7 | 41.56
2018-12-25 20:00 | 41.81 | 41.68
2018-12-25 20:30 | 41.52 | 41.4
2018-12-25 21:00 | 41.22 | 41.1
2018-12-25 21:30 | 40.85 | 40.74
2018-12-25 22:00 | 39.93 | 39.84
2018-12-25 22:30 | 38.49 | 38.42
2018-12-25 23:00 | 38.85 | 38.78
2018-12-25 23:30 | 36.65 | 36.6
2018-12-26 | 35.31 | 35.27
2018-12-26 00:30 | 34.66 | 34.63
2018-12-26 01:00 | 33.34 | 33.32
2018-12-26 01:30 | 32.72 | 32.7
2018-12-26 02:00 | 32.45 | 32.43
2018-12-26 02:30 | 32.24 | 32.23
2018-12-26 03:00 | 31.65 | 31.64
2018-12-26 03:30 | 31.21 | 31.2
2018-12-26 04:00 | 31.03 | 31.02
2018-12-26 04:30 | 30.83 | 30.82
2018-12-26 05:00 | 31.13 | 31.12
2018-12-26 05:30 | 30.87 | 30.87
2018-12-26 06:00 | 30.84 | 30.83
2018-12-26 06:30 | 33.42 | 33.41
2018-12-26 07:00 | 33.23 | 33.19
2018-12-26 07:30 | 35.94 | 35.8
2018-12-26 08:00 | 38.09 | 37.9
2018-12-26 08:30 | 40.23 | 39.97
2018-12-26 09:00 | 40.93 | 40.62
2018-12-26 09:30 | 41.95 | 41.61
2018-12-26 10:00 | 40.7 | 40.28
2018-12-26 10:30 | 40.09 | 39.95
2018-12-26 11:00 | 38.63 | 38.51
2018-12-26 11:30 | 38.55 | 38.4
2018-12-26 12:00 | 41.04 | 40.9
2018-12-26 12:30 | 43.05 | 42.91
2018-12-26 13:00 | 41.07 | 40.94
2018-12-26 13:30 | 39.63 | 39.49
2018-12-26 14:00 | 40.28 | 40.13
2018-12-26 14:30 | 40.4 | 40.26
2018-12-26 15:00 | 41.7 | 41.58
2018-12-26 15:30 | 41.08 | 40.98
2018-12-26 16:00 | 41.35 | 41.25
2018-12-26 16:30 | 42.86 | 42.79
2018-12-26 17:00 | 43.89 | 43.85
2018-12-26 17:30 | 45.18 | 45.13
2018-12-26 18:00 | 46.62 | 46.59
2018-12-26 18:30 | 46.55 | 46.54
2018-12-26 19:00 | 46.92 | 46.91
2018-12-26 19:30 | 47.67 | 47.65
2018-12-26 20:00 | 47.4 | 47.39
2018-12-26 20:30 | 46.16 | 46.16
2018-12-26 21:00 | 44.99 | 44.99
2018-12-26 21:30 | 43.6 | 43.6
2018-12-26 22:00 | 42.19 | 42.19
2018-12-26 22:30 | 40.27 | 40.25
2018-12-26 23:00 | 40.84 | 40.82
2018-12-26 23:30 | 37.83 | 37.78
2018-12-27 | 36.14 | 36.08
2018-12-27 00:30 | 35.51 | 35.47
2018-12-27 01:00 | 34.16 | 34.13
2018-12-27 01:30 | 33.82 | 33.79
2018-12-27 02:00 | 33.46 | 33.43
2018-12-27 02:30 | 32.8 | 32.78
2018-12-27 03:00 | 32.37 | 32.35
2018-12-27 03:30 | 32.5 | 32.48
2018-12-27 04:00 | 32.47 | 32.45
2018-12-27 04:30 | 32.66 | 32.63
2018-12-27 05:00 | 32.8 | 32.77
2018-12-27 05:30 | 33.27 | 33.25
2018-12-27 06:00 | 34.41 | 34.36
2018-12-27 06:30 | 37.98 | 37.81
2018-12-27 07:00 | 39.73 | 39.41
2018-12-27 07:30 | 42.84 | 42.15
2018-12-27 08:00 | 44.3 | 43.79
2018-12-27 08:30 | 46.93 | 46.43
2018-12-27 09:00 | 48.53 | 47.9
2018-12-27 09:30 | 47.48 | 46.67
2018-12-27 10:00 | 47.51 | 46.6
2018-12-27 10:30 | 47.76 | 46.68
2018-12-27 11:00 | 49.29 | 48.11
2018-12-27 11:30 | 48.36 | 47.14
2018-12-27 12:00 | 48.52 | 47.27
2018-12-27 12:30 | 49.43 | 48.22
2018-12-27 13:00 | 49.01 | 47.73
2018-12-27 13:30 | 49.56 | 48.32
2018-12-27 14:00 | 50.47 | 49.2
2018-12-27 14:30 | 51.71 | 50.54
2018-12-27 15:00 | 52.49 | 51.41
2018-12-27 15:30 | 53.56 | 52.6
2018-12-27 16:00 | 54.63 | 53.83
2018-12-27 16:30 | 53.4 | 52.71
2018-12-27 17:00 | 53.88 | 53.34
2018-12-27 17:30 | 54.09 | 53.68
2018-12-27 18:00 | 54.37 | 54.11
2018-12-27 18:30 | 53.6 | 53.46
2018-12-27 19:00 | 53.74 | 53.62
2018-12-27 19:30 | 54.49 | 54.34
2018-12-27 20:00 | 53.63 | 53.5
2018-12-27 20:30 | 51.84 | 51.76
2018-12-27 21:00 | 50.22 | 50.16
2018-12-27 21:30 | 47.92 | 47.9
2018-12-27 22:00 | 45.57 | 45.56
2018-12-27 22:30 | 43.06 | 43.06
2018-12-27 23:00 | 42.44 | 42.44
2018-12-27 23:30 | 39.41 | 39.39
2018-12-28 | 37.29 | 37.25
2018-12-28 00:30 | 35.57 | 35.52
2018-12-28 01:00 | 34.41 | 34.37
2018-12-28 01:30 | 33.56 | 33.53
2018-12-28 02:00 | 33.4 | 33.36
2018-12-28 02:30 | 33 | 32.96
2018-12-28 03:00 | 32.93 | 32.9
2018-12-28 03:30 | 32.77 | 32.74
2018-12-28 04:00 | 32.73 | 32.7
2018-12-28 04:30 | 32.93 | 32.89
2018-12-28 05:00 | 33.5 | 33.45
2018-12-28 05:30 | 33.77 | 33.74
2018-12-28 06:00 | 35.43 | 35.37
2018-12-28 06:30 | 39.1 | 38.85
2018-12-28 07:00 | 40.89 | 40.46
2018-12-28 07:30 | 45.63 | 44.9
2018-12-28 08:00 | 46.57 | 46.19
2018-12-28 08:30 | 48.17 | 47.64
2018-12-28 09:00 | 49.02 | 48.26
2018-12-28 09:30 | 49.23 | 48.33
2018-12-28 10:00 | 51.22 | 50.29
2018-12-28 10:30 | 50.92 | 49.92
2018-12-28 11:00 | 48.59 | 47.45
2018-12-28 11:30 | 49.08 | 47.92
2018-12-28 12:00 | 49.79 | 48.57
2018-12-28 12:30 | 51.44 | 50.28
2018-12-28 13:00 | 49.36 | 48.12
2018-12-28 13:30 | 49.14 | 47.96
2018-12-28 14:00 | 50.23 | 49.07
2018-12-28 14:30 | 51.2 | 50.12
2018-12-28 15:00 | 50.92 | 49.93
2018-12-28 15:30 | 51.48 | 50.58
2018-12-28 16:00 | 51.82 | 51.04
2018-12-28 16:30 | 53.45 | 52.76
2018-12-28 17:00 | 54.72 | 54.16
2018-12-28 17:30 | 54.1 | 53.68
2018-12-28 18:00 | 53.54 | 53.29
2018-12-28 18:30 | 52.15 | 52.03
2018-12-28 19:00 | 52.17 | 52.07
2018-12-28 19:30 | 52.95 | 52.82
2018-12-28 20:00 | 52.8 | 52.68
2018-12-28 20:30 | 50.76 | 50.69
2018-12-28 21:00 | 49.47 | 49.41
2018-12-28 21:30 | 47.78 | 47.74
2018-12-28 22:00 | 45.72 | 45.71
2018-12-28 22:30 | 43.17 | 43.17
2018-12-28 23:00 | 43.24 | 43.24
2018-12-28 23:30 | 40.45 | 40.44
2018-12-29 | 38.57 | 38.56
2018-12-29 00:30 | 37.31 | 37.27
2018-12-29 01:00 | 36.16 | 36.1
2018-12-29 01:30 | 35.61 | 35.56
2018-12-29 02:00 | 34.95 | 34.89
2018-12-29 02:30 | 34.29 | 34.24
2018-12-29 03:00 | 33.86 | 33.82
2018-12-29 03:30 | 33.94 | 33.9
2018-12-29 04:00 | 34 | 33.95
2018-12-29 04:30 | 34.18 | 34.14
2018-12-29 05:00 | 34.55 | 34.5
2018-12-29 05:30 | 34.9 | 34.86
2018-12-29 06:00 | 34.68 | 34.65
2018-12-29 06:30 | 36.11 | 36.04
2018-12-29 07:00 | 36.84 | 36.72
2018-12-29 07:30 | 39.49 | 39.27
2018-12-29 08:00 | 40.26 | 39.93
2018-12-29 08:30 | 39.94 | 39.76
2018-12-29 09:00 | 42.57 | 42.42
2018-12-29 09:30 | 42.88 | 42.66
2018-12-29 10:00 | 43.05 | 42.79
2018-12-29 10:30 | 45.52 | 45.25
2018-12-29 11:00 | 46.03 | 45.74
2018-12-29 11:30 | 41.93 | 41.62
2018-12-29 12:00 | 43.22 | 42.9
2018-12-29 12:30 | 41.96 | 41.69
2018-12-29 13:00 | 38.36 | 38.06
2018-12-29 13:30 | 41.2 | 40.94
2018-12-29 14:00 | 42.72 | 42.51
2018-12-29 14:30 | 39.94 | 39.69
2018-12-29 15:00 | 45.2 | 45.02
2018-12-29 15:30 | 46.05 | 45.92
2018-12-29 16:00 | 47.41 | 47.32
2018-12-29 16:30 | 45.79 | 45.73
2018-12-29 17:00 | 45.58 | 45.56
2018-12-29 17:30 | 45.9 | 45.86
2018-12-29 18:00 | 48.23 | 48.21
2018-12-29 18:30 | 48.66 | 48.64
2018-12-29 19:00 | 48.24 | 48.23
2018-12-29 19:30 | 48.9 | 48.87
2018-12-29 20:00 | 48.38 | 48.36
2018-12-29 20:30 | 47.24 | 47.23
2018-12-29 21:00 | 45.95 | 45.94
2018-12-29 21:30 | 44.61 | 44.61
2018-12-29 22:00 | 43.59 | 43.59
2018-12-29 22:30 | 41.92 | 41.92
2018-12-29 23:00 | 42.11 | 42.11
2018-12-29 23:30 | 39.33 | 39.32
2018-12-30 | 37.82 | 37.79
2018-12-30 00:30 | 36.75 | 36.7
2018-12-30 01:00 | 35.59 | 35.54
2018-12-30 01:30 | 35.07 | 35
2018-12-30 02:00 | 34.64 | 34.58
2018-12-30 02:30 | 34.31 | 34.24
2018-12-30 03:00 | 33.61 | 33.54
2018-12-30 03:30 | 33.6 | 33.56
2018-12-30 04:00 | 33.55 | 33.5
2018-12-30 04:30 | 33.48 | 33.43
2018-12-30 05:00 | 33.42 | 33.38
2018-12-30 05:30 | 33.38 | 33.36
2018-12-30 06:00 | 32.98 | 32.97
2018-12-30 06:30 | 34.24 | 34.19
2018-12-30 07:00 | 34.83 | 34.76
2018-12-30 07:30 | 36.09 | 35.91
2018-12-30 08:00 | 37.22 | 36.91
2018-12-30 08:30 | 38.82 | 38.41
2018-12-30 09:00 | 39.36 | 39.29
2018-12-30 09:30 | 38.98 | 38.87
2018-12-30 10:00 | 39.82 | 39.69
2018-12-30 10:30 | 39.85 | 39.69
2018-12-30 11:00 | 38.7 | 38.53
2018-12-30 11:30 | 39.79 | 39.62
2018-12-30 12:00 | 41.64 | 41.51
2018-12-30 12:30 | 41.7 | 41.58
2018-12-30 13:00 | 38.36 | 38.22
2018-12-30 13:30 | 40 | 39.83
2018-12-30 14:00 | 39.27 | 39.08
2018-12-30 14:30 | 39.7 | 39.53
2018-12-30 15:00 | 41.32 | 41.15
2018-12-30 15:30 | 44.04 | 43.9
2018-12-30 16:00 | 43.56 | 43.46
2018-12-30 16:30 | 44.19 | 44.11
2018-12-30 17:00 | 45.1 | 45.04
2018-12-30 17:30 | 46.98 | 46.93
2018-12-30 18:00 | 48.55 | 48.51
2018-12-30 18:30 | 49.85 | 49.83
2018-12-30 19:00 | 49.94 | 49.91
2018-12-30 19:30 | 50.56 | 50.51
2018-12-30 20:00 | 50.3 | 50.26
2018-12-30 20:30 | 48.77 | 48.75
2018-12-30 21:00 | 47.16 | 47.15
2018-12-30 21:30 | 45.4 | 45.39
2018-12-30 22:00 | 43.82 | 43.82
2018-12-30 22:30 | 41.62 | 41.62
2018-12-30 23:00 | 41.84 | 41.83
2018-12-30 23:30 | 38.5 | 38.47
2018-12-31 | 36.99 | 36.95
2018-12-31 00:30 | 35.68 | 35.63
2018-12-31 01:00 | 34.1 | 34.06
2018-12-31 01:30 | 33.38 | 33.34
2018-12-31 02:00 | 32.73 | 32.7
2018-12-31 02:30 | 32.55 | 32.52
2018-12-31 03:00 | 32.21 | 32.18
2018-12-31 03:30 | 32.27 | 32.24
2018-12-31 04:00 | 32.11 | 32.08
2018-12-31 04:30 | 32.32 | 32.29
2018-12-31 05:00 | 33.08 | 33.03
2018-12-31 05:30 | 33.61 | 33.57
2018-12-31 06:00 | 34.75 | 34.69
2018-12-31 06:30 | 38.43 | 38.21
2018-12-31 07:00 | 40.44 | 40.1
2018-12-31 07:30 | 42.73 | 42.23
2018-12-31 08:00 | 43.96 | 43.68
2018-12-31 08:30 | 45.16 | 44.72
2018-12-31 09:00 | 45.94 | 45.3
2018-12-31 09:30 | 46.76 | 45.94
2018-12-31 10:00 | 47.09 | 46.2
2018-12-31 10:30 | 47.74 | 46.76
2018-12-31 11:00 | 49.22 | 48.19
2018-12-31 11:30 | 50.82 | 49.77
2018-12-31 12:00 | 48.82 | 47.7
2018-12-31 12:30 | 50.03 | 48.92
2018-12-31 13:00 | 50.21 | 49.12
2018-12-31 13:30 | 49.58 | 48.53
2018-12-31 14:00 | 49.19 | 48.23
2018-12-31 14:30 | 49.6 | 48.72
2018-12-31 15:00 | 49.86 | 49.07
2018-12-31 15:30 | 49.47 | 48.75
2018-12-31 16:00 | 50.3 | 49.69
2018-12-31 16:30 | 52.46 | 51.95
2018-12-31 17:00 | 53.03 | 52.65
2018-12-31 17:30 | 51.17 | 50.9
2018-12-31 18:00 | 50.8 | 50.63
2018-12-31 18:30 | 49.89 | 49.82
2018-12-31 19:00 | 49.61 | 49.56
2018-12-31 19:30 | 49.6 | 49.53
2018-12-31 20:00 | 48.55 | 48.5
2018-12-31 20:30 | 46.68 | 46.65
2018-12-31 21:00 | 45.12 | 45.1
2018-12-31 21:30 | 43.28 | 43.27
2018-12-31 22:00 | 42.38 | 42.38
2018-12-31 22:30 | 41.42 | 41.41
2018-12-31 23:00 | 41.83 | 41.82
2018-12-31 23:30 | 38.83 | 38.81
2019-01-01 | 37.68 | 37.64
2019-01-01 00:30 | 36.62 | 36.57
2019-01-01 01:00 | 35.72 | 35.65
2019-01-01 01:30 | 35.16 | 35.09
2019-01-01 02:00 | 34.7 | 34.61
2019-01-01 02:30 | 34.05 | 33.98
2019-01-01 03:00 | 33.19 | 33.16
2019-01-01 03:30 | 32.96 | 32.94
2019-01-01 04:00 | 32.72 | 32.69
2019-01-01 04:30 | 32.5 | 32.47
2019-01-01 05:00 | 32.73 | 32.7
2019-01-01 05:30 | 32.16 | 32.15
2019-01-01 06:00 | 32.29 | 32.28
2019-01-01 06:30 | 34.28 | 34.23
2019-01-01 07:00 | 35.01 | 34.92
2019-01-01 07:30 | 36.11 | 35.9
2019-01-01 08:00 | 36.51 | 36.19
2019-01-01 08:30 | 36.76 | 36.33
2019-01-01 09:00 | 36.55 | 36.39
2019-01-01 09:30 | 36.49 | 36.38
2019-01-01 10:00 | 36.76 | 36.62
2019-01-01 10:30 | 37.17 | 36.99
2019-01-01 11:00 | 36.41 | 36.21
2019-01-01 11:30 | 36.8 | 36.57
2019-01-01 12:00 | 37.26 | 37.02
2019-01-01 12:30 | 38.71 | 38.46
2019-01-01 13:00 | 38.14 | 37.88
2019-01-01 13:30 | 39.19 | 38.89
2019-01-01 14:00 | 40.45 | 40.19
2019-01-01 14:30 | 41.78 | 41.53
2019-01-01 15:00 | 42.16 | 41.9
2019-01-01 15:30 | 43.91 | 43.68
2019-01-01 16:00 | 45.43 | 45.2
2019-01-01 16:30 | 47.27 | 47.06
2019-01-01 17:00 | 48.51 | 48.33
2019-01-01 17:30 | 49.61 | 49.47
2019-01-01 18:00 | 50.18 | 50.08
2019-01-01 18:30 | 50.37 | 50.33
2019-01-01 19:00 | 50.7 | 50.68
2019-01-01 19:30 | 51.71 | 51.66
2019-01-01 20:00 | 51.07 | 51.02
2019-01-01 20:30 | 49.15 | 49.13
2019-01-01 21:00 | 47.53 | 47.52
2019-01-01 21:30 | 45.41 | 45.41
2019-01-01 22:00 | 43.64 | 43.64
2019-01-01 22:30 | 41.9 | 41.9
2019-01-01 23:00 | 42.02 | 42.01
2019-01-01 23:30 | 38.88 | 38.86
2019-01-02 | 37.06 | 37.01
2019-01-02 00:30 | 36.19 | 36.12
2019-01-02 01:00 | 34.64 | 34.59
2019-01-02 01:30 | 33.83 | 33.79
2019-01-02 02:00 | 33.45 | 33.41
2019-01-02 02:30 | 32.77 | 32.74
2019-01-02 03:00 | 32.52 | 32.5
2019-01-02 03:30 | 32.73 | 32.7
2019-01-02 04:00 | 32.36 | 32.34
2019-01-02 04:30 | 32.85 | 32.82
2019-01-02 05:00 | 33.39 | 33.35
2019-01-02 05:30 | 33.67 | 33.64
2019-01-02 06:00 | 35.64 | 35.57
2019-01-02 06:30 | 40.42 | 40.1
2019-01-02 07:00 | 43.82 | 43.18
2019-01-02 07:30 | 48.15 | 47.29
2019-01-02 08:00 | 50.59 | 50.26
2019-01-02 08:30 | 52.61 | 52.23
2019-01-02 09:00 | 54.28 | 53.69
2019-01-02 09:30 | 54.4 | 53.71
2019-01-02 10:00 | 54.24 | 53.46
2019-01-02 10:30 | 54.41 | 53.53
2019-01-02 11:00 | 54.93 | 53.89
2019-01-02 11:30 | 57.47 | 56.35
2019-01-02 12:00 | 56.59 | 55.38
2019-01-02 12:30 | 57.47 | 56.29
2019-01-02 13:00 | 56.98 | 55.79
2019-01-02 13:30 | 57.26 | 56.09
2019-01-02 14:00 | 58.51 | 57.28
2019-01-02 14:30 | 58.79 | 57.64
2019-01-02 15:00 | 60.48 | 59.4
2019-01-02 15:30 | 61.08 | 60.14
2019-01-02 16:00 | 60.84 | 60.04
2019-01-02 16:30 | 60.78 | 60.16
2019-01-02 17:00 | 60.2 | 59.79
2019-01-02 17:30 | 58.4 | 58.2
2019-01-02 18:00 | 57.02 | 56.97
2019-01-02 18:30 | 56.02 | 56.01
2019-01-02 19:00 | 55.86 | 55.86
2019-01-02 19:30 | 55.96 | 55.95
2019-01-02 20:00 | 54.74 | 54.74
2019-01-02 20:30 | 52.71 | 52.71
2019-01-02 21:00 | 50.48 | 50.47
2019-01-02 21:30 | 48.4 | 48.36
2019-01-02 22:00 | 46.07 | 46.03
2019-01-02 22:30 | 44.09 | 44.08
2019-01-02 23:00 | 44.11 | 44.1
2019-01-02 23:30 | 40.59 | 40.59
2019-01-03 | 38.64 | 38.64
2019-01-03 00:30 | 37.68 | 37.66
2019-01-03 01:00 | 36.24 | 36.21
2019-01-03 01:30 | 35.43 | 35.33
2019-01-03 02:00 | 34.72 | 34.63
2019-01-03 02:30 | 34.54 | 34.46
2019-01-03 03:00 | 33.82 | 33.76
2019-01-03 03:30 | 34.65 | 34.57
2019-01-03 04:00 | 34.45 | 34.38
2019-01-03 04:30 | 35.19 | 35.11
2019-01-03 05:00 | 35.69 | 35.59
2019-01-03 05:30 | 35.88 | 35.8
2019-01-03 06:00 | 37.08 | 36.97
2019-01-03 06:30 | 41.76 | 41.38
2019-01-03 07:00 | 45.29 | 44.55
2019-01-03 07:30 | 48.31 | 47.46
2019-01-03 08:00 | 50.42 | 50.14
2019-01-03 08:30 | 53.08 | 52.58
2019-01-03 09:00 | 55.05 | 54.32
2019-01-03 09:30 | 55.67 | 54.86
2019-01-03 10:00 | 55.85 | 54.96
2019-01-03 10:30 | 57 | 55.91
2019-01-03 11:00 | 56.82 | 55.62
2019-01-03 11:30 | 57.68 | 56.34
2019-01-03 12:00 | 57.87 | 56.5
2019-01-03 12:30 | 59.07 | 57.78
2019-01-03 13:00 | 58.82 | 57.49
2019-01-03 13:30 | 59.53 | 58.21
2019-01-03 14:00 | 60.25 | 58.97
2019-01-03 14:30 | 61.54 | 60.16
2019-01-03 15:00 | 62.17 | 60.82
2019-01-03 15:30 | 62.48 | 61.18
2019-01-03 16:00 | 63.2 | 61.89
2019-01-03 16:30 | 63.92 | 62.6
2019-01-03 17:00 | 64.24 | 62.86
2019-01-03 17:30 | 63.41 | 61.96
2019-01-03 18:00 | 63.53 | 62.05
2019-01-03 18:30 | 62.59 | 61.03
2019-01-03 19:00 | 61.57 | 60.07
2019-01-03 19:30 | 61.88 | 60.41
2019-01-03 20:00 | 60.88 | 59.37
2019-01-03 20:30 | 58.22 | 56.6
2019-01-03 21:00 | 56.72 | 55.04
2019-01-03 21:30 | 53.85 | 52.02
2019-01-03 22:00 | 49.39 | 49.01
2019-01-03 22:30 | 46.79 | 46.76
2019-01-03 23:00 | 46.68 | 46.66
2019-01-03 23:30 | 43.16 | 43.15
2019-01-04 | 40.67 | 40.67
2019-01-04 00:30 | 39.59 | 39.59
2019-01-04 01:00 | 38.62 | 38.61
2019-01-04 01:30 | 37.73 | 37.72
2019-01-04 02:00 | 37.03 | 37.02
2019-01-04 02:30 | 36.31 | 36.29
2019-01-04 03:00 | 35.91 | 35.82
2019-01-04 03:30 | 35.78 | 35.7
2019-01-04 04:00 | 35.74 | 35.65
2019-01-04 04:30 | 36.23 | 36.11
2019-01-04 05:00 | 36.79 | 36.65
2019-01-04 05:30 | 37.48 | 37.35
2019-01-04 06:00 | 39.07 | 38.89
2019-01-04 06:30 | 44.86 | 44.32
2019-01-04 07:00 | 48.06 | 47.11
2019-01-04 07:30 | 51.54 | 51.12
2019-01-04 08:00 | 53.71 | 53.31
2019-01-04 08:30 | 55.63 | 55.03
2019-01-04 09:00 | 56.82 | 56.02
2019-01-04 09:30 | 58.62 | 57.7
2019-01-04 10:00 | 57.4 | 56.41
2019-01-04 10:30 | 57.57 | 56.42
2019-01-04 11:00 | 58.1 | 56.83
2019-01-04 11:30 | 58.6 | 57.19
2019-01-04 12:00 | 58.33 | 56.9
2019-01-04 12:30 | 58.56 | 58
2019-01-04 13:00 | 58.49 | 58.16
2019-01-04 13:30 | 57.96 | 57.63
2019-01-04 14:00 | 57.9 | 57.57
2019-01-04 14:30 | 58.7 | 58.37
2019-01-04 15:00 | 59.08 | 58.76
2019-01-04 15:30 | 59.42 | 59.05
2019-01-04 16:00 | 60.49 | 60.04
2019-01-04 16:30 | 61.37 | 60.8
2019-01-04 17:00 | 61.02 | 60.23
2019-01-04 17:30 | 59.24 | 58.43
2019-01-04 18:00 | 57.36 | 56.94
2019-01-04 18:30 | 57.12 | 56.72
2019-01-04 19:00 | 57.01 | 56.61
2019-01-04 19:30 | 57.55 | 57.15
2019-01-04 20:00 | 56.03 | 55.62
2019-01-04 20:30 | 54.54 | 54.09
2019-01-04 21:00 | 53.03 | 52.56
2019-01-04 21:30 | 51.05 | 50.56
2019-01-04 22:00 | 49.4 | 48.89
2019-01-04 22:30 | 46.95 | 46.43
2019-01-04 23:00 | 47.01 | 46.5
2019-01-04 23:30 | 43.2 | 42.65
2019-01-05 | 41.07 | 40.49
2019-01-05 00:30 | 39.83 | 39.25
2019-01-05 01:00 | 38.8 | 38.2
2019-01-05 01:30 | 37.91 | 37.29
2019-01-05 02:00 | 37.08 | 36.44
2019-01-05 02:30 | 36.44 | 35.8
2019-01-05 03:00 | 36.76 | 36.07
2019-01-05 03:30 | 35.65 | 34.93
2019-01-05 04:00 | 35.76 | 35.04
2019-01-05 04:30 | 35.72 | 35
2019-01-05 05:00 | 36.05 | 35.32
2019-01-05 05:30 | 36.12 | 35.41
2019-01-05 06:00 | 36.42 | 35.71
2019-01-05 06:30 | 38.56 | 37.88
2019-01-05 07:00 | 39.25 | 38.56
2019-01-05 07:30 | 41.54 | 40.86
2019-01-05 08:00 | 43.94 | 43.23
2019-01-05 08:30 | 45.96 | 45.37
2019-01-05 09:00 | 47.92 | 47.33
2019-01-05 09:30 | 48.39 | 47.75
2019-01-05 10:00 | 48.19 | 47.48
2019-01-05 10:30 | 48.03 | 47.24
2019-01-05 11:00 | 48.29 | 47.47
2019-01-05 11:30 | 47.31 | 46.45
2019-01-05 12:00 | 47.65 | 46.82
2019-01-05 12:30 | 48.09 | 47.36
2019-01-05 13:00 | 47.13 | 46.43
2019-01-05 13:30 | 46.77 | 46.11
2019-01-05 14:00 | 47.11 | 46.5
2019-01-05 14:30 | 47.13 | 46.54
2019-01-05 15:00 | 47.66 | 47.07
2019-01-05 15:30 | 48.75 | 48.19
2019-01-05 16:00 | 50.21 | 49.67
2019-01-05 16:30 | 50.77 | 50.25
2019-01-05 17:00 | 51.97 | 51.47
2019-01-05 17:30 | 53.42 | 52.93
2019-01-05 18:00 | 54.52 | 54.06
2019-01-05 18:30 | 54.73 | 54.27
2019-01-05 19:00 | 54.41 | 53.95
2019-01-05 19:30 | 54.53 | 54.07
2019-01-05 20:00 | 53.98 | 53.52
2019-01-05 20:30 | 52.47 | 52
2019-01-05 21:00 | 51.25 | 50.77
2019-01-05 21:30 | 49.44 | 48.93
2019-01-05 22:00 | 48.13 | 47.62
2019-01-05 22:30 | 45.66 | 45.13
2019-01-05 23:00 | 46.13 | 45.61
2019-01-05 23:30 | 42.61 | 42.05
2019-01-06 | 40.75 | 40.17
2019-01-06 00:30 | 39.41 | 38.81
2019-01-06 01:00 | 37.89 | 37.28
2019-01-06 01:30 | 36.68 | 36.05
2019-01-06 02:00 | 36.26 | 35.62
2019-01-06 02:30 | 35.86 | 35.22
2019-01-06 03:00 | 35.03 | 34.32
2019-01-06 03:30 | 34.64 | 33.91
2019-01-06 04:00 | 34.24 | 33.5
2019-01-06 04:30 | 34.07 | 33.32
2019-01-06 05:00 | 34.05 | 33.3
2019-01-06 05:30 | 33.65 | 32.91
2019-01-06 06:00 | 33.41 | 32.66
2019-01-06 06:30 | 35 | 34.28
2019-01-06 07:00 | 36.07 | 35.36
2019-01-06 07:30 | 36.88 | 36.16
2019-01-06 08:00 | 37.61 | 36.89
2019-01-06 08:30 | 38.94 | 38.22
2019-01-06 09:00 | 40.16 | 39.47
2019-01-06 09:30 | 41.72 | 41.09
2019-01-06 10:00 | 42.47 | 41.84
2019-01-06 10:30 | 42.38 | 41.75
2019-01-06 11:00 | 42.38 | 41.74
2019-01-06 11:30 | 42.72 | 42.08
2019-01-06 12:00 | 43.36 | 42.73
2019-01-06 12:30 | 44.51 | 43.9
2019-01-06 13:00 | 44.35 | 43.74
2019-01-06 13:30 | 44.4 | 43.78
2019-01-06 14:00 | 45.31 | 44.71
2019-01-06 14:30 | 45.71 | 45.12
2019-01-06 15:00 | 46.83 | 46.26
2019-01-06 15:30 | 47.97 | 47.42
2019-01-06 16:00 | 49.28 | 48.75
2019-01-06 16:30 | 51.01 | 50.5
2019-01-06 17:00 | 51.87 | 51.38
2019-01-06 17:30 | 53.47 | 53
2019-01-06 18:00 | 54.51 | 54.04
2019-01-06 18:30 | 55.16 | 54.71
2019-01-06 19:00 | 55.69 | 55.24
2019-01-06 19:30 | 56.61 | 56.16
2019-01-06 20:00 | 56.47 | 56.01
2019-01-06 20:30 | 54.8 | 54.33
2019-01-06 21:00 | 53 | 52.52
2019-01-06 21:30 | 50.44 | 49.94
2019-01-06 22:00 | 48.14 | 47.63
2019-01-06 22:30 | 45.58 | 45.05
2019-01-06 23:00 | 45.74 | 45.22
2019-01-06 23:30 | 42.21 | 41.65
2019-01-07 | 40.1 | 39.52
2019-01-07 00:30 | 39.68 | 39.1
2019-01-07 01:00 | 38.95 | 38.35
2019-01-07 01:30 | 38.08 | 37.47
2019-01-07 02:00 | 38.08 | 37.46
2019-01-07 02:30 | 37.43 | 36.73
2019-01-07 03:00 | 37.24 | 36.54
2019-01-07 03:30 | 36.64 | 35.94
2019-01-07 04:00 | 36.64 | 35.93
2019-01-07 04:30 | 37 | 36.3
2019-01-07 05:00 | 38.25 | 37.56
2019-01-07 05:30 | 40.53 | 39.87
2019-01-07 06:00 | 42.76 | 42.12
2019-01-07 06:30 | 48.93 | 47.97
2019-01-07 07:00 | 53.56 | 52.7
2019-01-07 07:30 | 59.12 | 58.43
2019-01-07 08:00 | 61.47 | 60.52
2019-01-07 08:30 | 64.05 | 62.97
2019-01-07 09:00 | 68.04 | 67.17
2019-01-07 09:30 | 68.68 | 67.77
2019-01-07 10:00 | 66.75 | 65.77
2019-01-07 10:30 | 68.35 | 67.3
2019-01-07 11:00 | 70.89 | 69.85
2019-01-07 11:30 | 70.73 | 69.69
2019-01-07 12:00 | 68.76 | 67.69
2019-01-07 12:30 | 66.54 | 65.38
2019-01-07 13:00 | 65.3 | 63.97
2019-01-07 13:30 | 65.61 | 64.24
2019-01-07 14:00 | 67.1 | 65.71
2019-01-07 14:30 | 67.27 | 65.97
2019-01-07 15:00 | 67.76 | 66.51
2019-01-07 15:30 | 68.95 | 67.85
2019-01-07 16:00 | 68.62 | 67.74
2019-01-07 16:30 | 67.97 | 67.31
2019-01-07 17:00 | 68.04 | 67.59
2019-01-07 17:30 | 64.23 | 63.89
2019-01-07 18:00 | 63.72 | 63.35
2019-01-07 18:30 | 62.92 | 62.52
2019-01-07 19:00 | 62.8 | 62.39
2019-01-07 19:30 | 63.3 | 62.9
2019-01-07 20:00 | 62.12 | 61.71
2019-01-07 20:30 | 59.28 | 59.06
2019-01-07 21:00 | 56.92 | 56.88
2019-01-07 21:30 | 54.06 | 53.97
2019-01-07 22:00 | 50.63 | 50.41
2019-01-07 22:30 | 48.5 | 47.64
2019-01-07 23:00 | 49.2 | 47.47
2019-01-07 23:30 | 45.59 | 43.71
2019-01-08 | 43.74 | 41.8
2019-01-08 00:30 | 42.14 | 40.14
2019-01-08 01:00 | 40.57 | 38.36
2019-01-08 01:30 | 40.41 | 38.08
2019-01-08 02:00 | 39.96 | 37.6
2019-01-08 02:30 | 40.2 | 37.84
2019-01-08 03:00 | 39.13 | 36.62
2019-01-08 03:30 | 38.66 | 36.11
2019-01-08 04:00 | 38.43 | 35.87
2019-01-08 04:30 | 38.83 | 36.29
2019-01-08 05:00 | 39.34 | 36.83
2019-01-08 05:30 | 41.24 | 38.85
2019-01-08 06:00 | 43.67 | 41.4
2019-01-08 06:30 | 49.28 | 47.22
2019-01-08 07:00 | 52.34 | 51.56
2019-01-08 07:30 | 57.2 | 56.45
2019-01-08 08:00 | 60.2 | 59.58
2019-01-08 08:30 | 62.53 | 62.04
2019-01-08 09:00 | 63.96 | 63.55
2019-01-08 09:30 | 63.83 | 63.41
2019-01-08 10:00 | 63.67 | 63.26
2019-01-08 10:30 | 64.45 | 64.04
2019-01-08 11:00 | 64.28 | 63.86
2019-01-08 11:30 | 63.12 | 62.7
2019-01-08 12:00 | 62.75 | 62.33
2019-01-08 12:30 | 63.12 | 62.7
2019-01-08 13:00 | 61.73 | 61.31
2019-01-08 13:30 | 61.59 | 61.16
2019-01-08 14:00 | 61.01 | 60.58
2019-01-08 14:30 | 60.82 | 60.39
2019-01-08 15:00 | 59.83 | 59.39
2019-01-08 15:30 | 59.79 | 59.37
2019-01-08 16:00 | 59.05 | 58.63
2019-01-08 16:30 | 57.66 | 57.25
2019-01-08 17:00 | 55.96 | 55.54
2019-01-08 17:30 | 53.95 | 53.55
2019-01-08 18:00 | 53.34 | 52.95
2019-01-08 18:30 | 52.89 | 52.51
2019-01-08 19:00 | 52.59 | 52.21
2019-01-08 19:30 | 52.78 | 52.4
2019-01-08 20:00 | 51.5 | 51.11
2019-01-08 20:30 | 49.96 | 49.56
2019-01-08 21:00 | 48.47 | 47.96
2019-01-08 21:30 | 46.65 | 46.12
2019-01-08 22:00 | 44.53 | 43.98
2019-01-08 22:30 | 42.41 | 41.84
2019-01-08 23:00 | 43.09 | 42.53
2019-01-08 23:30 | 40.04 | 39.44
2019-01-09 | 38.24 | 37.62
2019-01-09 00:30 | 36.74 | 36.05
2019-01-09 01:00 | 35.68 | 34.95
2019-01-09 01:30 | 35.14 | 34.39
2019-01-09 02:00 | 34.81 | 34.06
2019-01-09 02:30 | 34.88 | 34.13
2019-01-09 03:00 | 35.07 | 34.33
2019-01-09 03:30 | 35.61 | 34.88
2019-01-09 04:00 | 36.13 | 35.41
2019-01-09 04:30 | 37.05 | 36.34
2019-01-09 05:00 | 38.15 | 37.46
2019-01-09 05:30 | 39.86 | 39.19
2019-01-09 06:00 | 42.25 | 41.6
2019-01-09 06:30 | 48.75 | 47.84
2019-01-09 07:00 | 53.44 | 52.74
2019-01-09 07:30 | 58.39 | 57.48
2019-01-09 08:00 | 60.79 | 60.43
2019-01-09 08:30 | 65.11 | 64.58
2019-01-09 09:00 | 67.11 | 66.45
2019-01-09 09:30 | 67.9 | 67.26
2019-01-09 10:00 | 64.2 | 63.51
2019-01-09 10:30 | 64.61 | 63.64
2019-01-09 11:00 | 68.76 | 67.64
2019-01-09 11:30 | 70.24 | 69.06
2019-01-09 12:00 | 65.86 | 64.61
2019-01-09 12:30 | 68.2 | 66.9
2019-01-09 13:00 | 67.59 | 67.18
2019-01-09 13:30 | 68.26 | 68.17
2019-01-09 14:00 | 69.46 | 69.38
2019-01-09 14:30 | 69.52 | 69.43
2019-01-09 15:00 | 69.64 | 69.53
2019-01-09 15:30 | 72.11 | 71.95
2019-01-09 16:00 | 70.99 | 70.68
2019-01-09 16:30 | 69.73 | 69.25
2019-01-09 17:00 | 68.76 | 68
2019-01-09 17:30 | 67.63 | 66.38
2019-01-09 18:00 | 65.74 | 64.11
2019-01-09 18:30 | 64.38 | 63.21
2019-01-09 19:00 | 64.29 | 63.06
2019-01-09 19:30 | 63.78 | 62.47
2019-01-09 20:00 | 62.13 | 60.62
2019-01-09 20:30 | 60.14 | 58.41
2019-01-09 21:00 | 58.16 | 56.13
2019-01-09 21:30 | 56.48 | 54.13
2019-01-09 22:00 | 54.33 | 51.59
2019-01-09 22:30 | 53.18 | 48.27
2019-01-09 23:00 | 50.07 | 48.07
2019-01-09 23:30 | 46.41 | 44.5
2019-01-10 | 44.99 | 43.02
2019-01-10 00:30 | 44.09 | 42.08
2019-01-10 01:00 | 43.32 | 41.27
2019-01-10 01:30 | 42.06 | 39.95
2019-01-10 02:00 | 41.38 | 39.22
2019-01-10 02:30 | 40.41 | 38.1
2019-01-10 03:00 | 40.26 | 37.85
2019-01-10 03:30 | 39.97 | 37.53
2019-01-10 04:00 | 39.97 | 37.53
2019-01-10 04:30 | 40.53 | 38.11
2019-01-10 05:00 | 41.41 | 39.05
2019-01-10 05:30 | 43.52 | 41.27
2019-01-10 06:00 | 45.82 | 43.67
2019-01-10 06:30 | 50.56 | 48.79
2019-01-10 07:00 | 53.9 | 52.92
2019-01-10 07:30 | 59.26 | 58.71
2019-01-10 08:00 | 61.95 | 61
2019-01-10 08:30 | 66.06 | 64.74
2019-01-10 09:00 | 68.36 | 67.13
2019-01-10 09:30 | 68.94 | 67.71
2019-01-10 10:00 | 68.69 | 67.45
2019-01-10 10:30 | 67.57 | 66.33
2019-01-10 11:00 | 69.05 | 67.85
2019-01-10 11:30 | 67.77 | 66.57
2019-01-10 12:00 | 71.15 | 70.01
2019-01-10 12:30 | 70.82 | 69.66
2019-01-10 13:00 | 70.61 | 69.44
2019-01-10 13:30 | 71.71 | 70.56
2019-01-10 14:00 | 68.55 | 67.35
2019-01-10 14:30 | 68.05 | 66.85
2019-01-10 15:00 | 67.64 | 66.43
2019-01-10 15:30 | 69.83 | 68.63
2019-01-10 16:00 | 69.79 | 68.56
2019-01-10 16:30 | 67.83 | 66.51
2019-01-10 17:00 | 66.32 | 64.91
2019-01-10 17:30 | 63.55 | 62
2019-01-10 18:00 | 63.33 | 61.72
2019-01-10 18:30 | 62.39 | 60.72
2019-01-10 19:00 | 61.39 | 59.68
2019-01-10 19:30 | 60.63 | 58.88
2019-01-10 20:00 | 59.47 | 57.69
2019-01-10 20:30 | 57.08 | 55.34
2019-01-10 21:00 | 55.34 | 53.64
2019-01-10 21:30 | 52.75 | 50.92
2019-01-10 22:00 | 50.01 | 48.05
2019-01-10 22:30 | 46.82 | 45.12
2019-01-10 23:00 | 45.48 | 45.44
2019-01-10 23:30 | 41.97 | 41.96
2019-01-11 | 40.11 | 40.11
2019-01-11 00:30 | 38.48 | 38.37
2019-01-11 01:00 | 37.05 | 36.85
2019-01-11 01:30 | 36.6 | 36.4
2019-01-11 02:00 | 35.9 | 35.72
2019-01-11 02:30 | 35.36 | 35.2
2019-01-11 03:00 | 35.39 | 35.23
2019-01-11 03:30 | 34.79 | 34.66
2019-01-11 04:00 | 35.27 | 35.15
2019-01-11 04:30 | 35.33 | 35.19
2019-01-11 05:00 | 36.31 | 36.14
2019-01-11 05:30 | 38.27 | 38.05
2019-01-11 06:00 | 41.54 | 41.19
2019-01-11 06:30 | 47.03 | 46.23
2019-01-11 07:00 | 51.95 | 51.28
2019-01-11 07:30 | 57.85 | 56.95
2019-01-11 08:00 | 60.55 | 59.89
2019-01-11 08:30 | 62.46 | 61.99
2019-01-11 09:00 | 64.64 | 64
2019-01-11 09:30 | 64.75 | 64
2019-01-11 10:00 | 62.35 | 61.57
2019-01-11 10:30 | 61.9 | 60.96
2019-01-11 11:00 | 62.18 | 61.09
2019-01-11 11:30 | 62.23 | 61.05
2019-01-11 12:00 | 63.08 | 61.84
2019-01-11 12:30 | 65.47 | 64.28
2019-01-11 13:00 | 64.92 | 63.84
2019-01-11 13:30 | 63.46 | 62.5
2019-01-11 14:00 | 63.67 | 62.72
2019-01-11 14:30 | 62.57 | 61.74
2019-01-11 15:00 | 59.36 | 58.48
2019-01-11 15:30 | 62.66 | 62.05
2019-01-11 16:00 | 63.03 | 62.53
2019-01-11 16:30 | 63.61 | 63.28
2019-01-11 17:00 | 63.61 | 63.44
2019-01-11 17:30 | 60.54 | 60.51
2019-01-11 18:00 | 58.61 | 58.61
2019-01-11 18:30 | 57.29 | 57.25
2019-01-11 19:00 | 56.9 | 56.85
2019-01-11 19:30 | 56.88 | 56.83
2019-01-11 20:00 | 55.81 | 55.74
2019-01-11 20:30 | 53.67 | 53.53
2019-01-11 21:00 | 51.99 | 51.94
2019-01-11 21:30 | 50.11 | 50.1
2019-01-11 22:00 | 48.33 | 48.29
2019-01-11 22:30 | 45.79 | 45.74
2019-01-11 23:00 | 46.05 | 46.02
2019-01-11 23:30 | 42.26 | 42.26
2019-01-12 | 39.82 | 39.82
2019-01-12 00:30 | 38.46 | 38.42
2019-01-12 01:00 | 37.04 | 36.9
2019-01-12 01:30 | 36.62 | 36.48
2019-01-12 02:00 | 35.6 | 35.48
2019-01-12 02:30 | 29.57 | 29.39
2019-01-12 03:00 | 34.3 | 34.22
2019-01-12 03:30 | 33.83 | 33.77
2019-01-12 04:00 | 33.48 | 33.44
2019-01-12 04:30 | 33.82 | 33.77
2019-01-12 05:00 | 33.89 | 33.83
2019-01-12 05:30 | 34.4 | 34.36
2019-01-12 06:00 | 34.75 | 34.7
2019-01-12 06:30 | 36.54 | 36.41
2019-01-12 07:00 | 37.45 | 37.22
2019-01-12 07:30 | 40.33 | 39.9
2019-01-12 08:00 | 43.45 | 42.76
2019-01-12 08:30 | 46.31 | 45.86
2019-01-12 09:00 | 47.67 | 47.25
2019-01-12 09:30 | 49.33 | 48.84
2019-01-12 10:00 | 47.21 | 46.61
2019-01-12 10:30 | 46.84 | 46.17
2019-01-12 11:00 | 46.28 | 45.53
2019-01-12 11:30 | 44.95 | 44.15
2019-01-12 12:00 | 44.54 | 43.79
2019-01-12 12:30 | 44.86 | 44.21
2019-01-12 13:00 | 43.43 | 42.86
2019-01-12 13:30 | 43.38 | 42.86
2019-01-12 14:00 | 43.66 | 43.18
2019-01-12 14:30 | 43.89 | 43.45
2019-01-12 15:00 | 44.6 | 44.2
2019-01-12 15:30 | 45.16 | 44.82
2019-01-12 16:00 | 46.52 | 46.22
2019-01-12 16:30 | 47.16 | 46.95
2019-01-12 17:00 | 48.7 | 48.56
2019-01-12 17:30 | 49.66 | 49.54
2019-01-12 18:00 | 51.27 | 51.17
2019-01-12 18:30 | 51.51 | 51.45
2019-01-12 19:00 | 51.41 | 51.36
2019-01-12 19:30 | 52.13 | 52.05
2019-01-12 20:00 | 51.62 | 51.55
2019-01-12 20:30 | 49.72 | 49.68
2019-01-12 21:00 | 48.18 | 48.14
2019-01-12 21:30 | 46.69 | 46.67
2019-01-12 22:00 | 44.91 | 44.91
2019-01-12 22:30 | 43.09 | 43.09
2019-01-12 23:00 | 43.99 | 43.99
2019-01-12 23:30 | 40.62 | 40.62
2019-01-13 | 38.61 | 38.59
2019-01-13 00:30 | 37.62 | 37.58
2019-01-13 01:00 | 36.33 | 36.29
2019-01-13 01:30 | 35.27 | 35.22
2019-01-13 02:00 | 34.84 | 34.78
2019-01-13 02:30 | 34.31 | 34.26
2019-01-13 03:00 | 33.73 | 33.69
2019-01-13 03:30 | 33.42 | 33.39
2019-01-13 04:00 | 33.26 | 33.23
2019-01-13 04:30 | 33.31 | 33.27
2019-01-13 05:00 | 33.41 | 33.37
2019-01-13 05:30 | 33.71 | 33.69
2019-01-13 06:00 | 33.49 | 33.48
2019-01-13 06:30 | 34.72 | 34.69
2019-01-13 07:00 | 34.8 | 34.76
2019-01-13 07:30 | 35.65 | 35.55
2019-01-13 08:00 | 37.77 | 37.59
2019-01-13 08:30 | 39.49 | 39.2
2019-01-13 09:00 | 40.95 | 40.49
2019-01-13 09:30 | 44.33 | 44.12
2019-01-13 10:00 | 42.51 | 42.38
2019-01-13 10:30 | 41.5 | 41.32
2019-01-13 11:00 | 42.64 | 42.43
2019-01-13 11:30 | 39.64 | 39.4
2019-01-13 12:00 | 41.01 | 40.77
2019-01-13 12:30 | 42.28 | 42.04
2019-01-13 13:00 | 42.62 | 42.36
2019-01-13 13:30 | 43.42 | 43.15
2019-01-13 14:00 | 43.51 | 43.27
2019-01-13 14:30 | 43.32 | 43.1
2019-01-13 15:00 | 43.95 | 43.74
2019-01-13 15:30 | 46.46 | 46.28
2019-01-13 16:00 | 48.98 | 48.85
2019-01-13 16:30 | 49.19 | 49.07
2019-01-13 17:00 | 49.32 | 49.21
2019-01-13 17:30 | 50.64 | 50.55
2019-01-13 18:00 | 52.02 | 51.95
2019-01-13 18:30 | 52.63 | 52.58
2019-01-13 19:00 | 53.44 | 53.4
2019-01-13 19:30 | 54.42 | 54.35
2019-01-13 20:00 | 52.59 | 52.54
2019-01-13 20:30 | 50.81 | 50.77
2019-01-13 21:00 | 49.07 | 49.05
2019-01-13 21:30 | 47.55 | 47.53
2019-01-13 22:00 | 45.78 | 45.78
2019-01-13 22:30 | 43.44 | 43.44
2019-01-13 23:00 | 44.1 | 44.09
2019-01-13 23:30 | 40.38 | 40.37
2019-01-14 | 38.52 | 38.49
2019-01-14 00:30 | 37.59 | 37.55
2019-01-14 01:00 | 36.14 | 36.09
2019-01-14 01:30 | 35.65 | 35.59
2019-01-14 02:00 | 35.21 | 35.15
2019-01-14 02:30 | 34.77 | 34.71
2019-01-14 03:00 | 34.62 | 34.57
2019-01-14 03:30 | 34.31 | 34.27
2019-01-14 04:00 | 34.48 | 34.42
2019-01-14 04:30 | 34.9 | 34.83
2019-01-14 05:00 | 35.67 | 35.59
2019-01-14 05:30 | 38.05 | 37.91
2019-01-14 06:00 | 40.75 | 40.49
2019-01-14 06:30 | 46.49 | 45.82
2019-01-14 07:00 | 50.63 | 50.05
2019-01-14 07:30 | 56.66 | 56.44
2019-01-14 08:00 | 60.96 | 60.72
2019-01-14 08:30 | 63.19 | 62.76
2019-01-14 09:00 | 64.19 | 63.54
2019-01-14 09:30 | 65.51 | 64.74
2019-01-14 10:00 | 65.56 | 64.86
2019-01-14 10:30 | 65.12 | 64.35
2019-01-14 11:00 | 64.17 | 63.22
2019-01-14 11:30 | 66.07 | 64.95
2019-01-14 12:00 | 65.46 | 64.19
2019-01-14 12:30 | 66.39 | 65.13
2019-01-14 13:00 | 66.78 | 65.58
2019-01-14 13:30 | 65.68 | 64.34
2019-01-14 14:00 | 65.45 | 64.12
2019-01-14 14:30 | 65.43 | 64.17
2019-01-14 15:00 | 65.73 | 64.54
2019-01-14 15:30 | 66.42 | 65.36
2019-01-14 16:00 | 66.72 | 65.84
2019-01-14 16:30 | 66.78 | 66.13
2019-01-14 17:00 | 66.15 | 65.76
2019-01-14 17:30 | 64.18 | 64.03
2019-01-14 18:00 | 62.49 | 62.45
2019-01-14 18:30 | 61.95 | 61.95
2019-01-14 19:00 | 62.58 | 62.58
2019-01-14 19:30 | 63.08 | 63.08
2019-01-14 20:00 | 61.54 | 61.45
2019-01-14 20:30 | 59.03 | 58.99
2019-01-14 21:00 | 56.98 | 56.96
2019-01-14 21:30 | 54.39 | 54.38
2019-01-14 22:00 | 51.39 | 51.39
2019-01-14 22:30 | 48.46 | 48.45
2019-01-14 23:00 | 48.74 | 48.72
2019-01-14 23:30 | 44.98 | 44.92
2019-01-15 | 42.38 | 42.28
2019-01-15 00:30 | 40.62 | 40.6
2019-01-15 01:00 | 39.52 | 39.38
2019-01-15 01:30 | 39.58 | 39.3
2019-01-15 02:00 | 38.6 | 38.35
2019-01-15 02:30 | 37.92 | 37.68
2019-01-15 03:00 | 37.5 | 37.3
2019-01-15 03:30 | 37.29 | 37.1
2019-01-15 04:00 | 37.16 | 36.99
2019-01-15 04:30 | 37.79 | 37.59
2019-01-15 05:00 | 38.72 | 38.49
2019-01-15 05:30 | 40.91 | 40.61
2019-01-15 06:00 | 43.26 | 42.85
2019-01-15 06:30 | 49.31 | 48.38
2019-01-15 07:00 | 53.72 | 52.97
2019-01-15 07:30 | 60.17 | 59.31
2019-01-15 08:00 | 62.06 | 61.09
2019-01-15 08:30 | 62.94 | 62.28
2019-01-15 09:00 | 66.2 | 65.29
2019-01-15 09:30 | 63.61 | 62.61
2019-01-15 10:00 | 63.66 | 62.61
2019-01-15 10:30 | 64.5 | 63.29
2019-01-15 11:00 | 63.8 | 62.45
2019-01-15 11:30 | 64.17 | 62.78
2019-01-15 12:00 | 66.72 | 65.28
2019-01-15 12:30 | 66.89 | 65.48
2019-01-15 13:00 | 65.43 | 64.03
2019-01-15 13:30 | 65.34 | 63.94
2019-01-15 14:00 | 65.82 | 64.44
2019-01-15 14:30 | 66.87 | 65.52
2019-01-15 15:00 | 70.76 | 69.56
2019-01-15 15:30 | 68.26 | 67.18
2019-01-15 16:00 | 66.6 | 65.63
2019-01-15 16:30 | 66.64 | 65.98
2019-01-15 17:00 | 66.72 | 66.3
2019-01-15 17:30 | 64.34 | 64.18
2019-01-15 18:00 | 63.31 | 63.27
2019-01-15 18:30 | 62.43 | 62.43
2019-01-15 19:00 | 62.47 | 62.47
2019-01-15 19:30 | 62.84 | 62.84
2019-01-15 20:00 | 61.58 | 61.58
2019-01-15 20:30 | 58.95 | 58.93
2019-01-15 21:00 | 57 | 56.96
2019-01-15 21:30 | 54.13 | 54.05
2019-01-15 22:00 | 51.18 | 51.02
2019-01-15 22:30 | 48.2 | 47.92
2019-01-15 23:00 | 48.46 | 48.03
2019-01-15 23:30 | 46.03 | 44.1
2019-01-16 | 43.82 | 41.66
2019-01-16 00:30 | 42.62 | 40.42
2019-01-16 01:00 | 41.45 | 39.17
2019-01-16 01:30 | 40.8 | 38.48
2019-01-16 02:00 | 40.08 | 37.71
2019-01-16 02:30 | 39.04 | 36.52
2019-01-16 03:00 | 38.46 | 35.87
2019-01-16 03:30 | 38.16 | 35.56
2019-01-16 04:00 | 38.05 | 35.44
2019-01-16 04:30 | 38.24 | 35.65
2019-01-16 05:00 | 39.09 | 36.54
2019-01-16 05:30 | 40.97 | 38.54
2019-01-16 06:00 | 42.69 | 40.35
2019-01-16 06:30 | 47.65 | 45.51
2019-01-16 07:00 | 52.03 | 50.11
2019-01-16 07:30 | 58.11 | 56.96
2019-01-16 08:00 | 60.55 | 59.45
2019-01-16 08:30 | 63.55 | 62.45
2019-01-16 09:00 | 64 | 63.52
2019-01-16 09:30 | 63.57 | 63.4
2019-01-16 10:00 | 63.43 | 63.27
2019-01-16 10:30 | 63.39 | 63.23
2019-01-16 11:00 | 65.36 | 65.24
2019-01-16 11:30 | 64.96 | 64.87
2019-01-16 12:00 | 65.14 | 65.08
2019-01-16 12:30 | 66.8 | 66.74
2019-01-16 13:00 | 65.92 | 65.85
2019-01-16 13:30 | 66.25 | 66.18
2019-01-16 14:00 | 66.89 | 66.83
2019-01-16 14:30 | 67.18 | 67.11
2019-01-16 15:00 | 67.55 | 67.45
2019-01-16 15:30 | 68.36 | 68.23
2019-01-16 16:00 | 68.96 | 68.77
2019-01-16 16:30 | 70.19 | 69.85
2019-01-16 17:00 | 69.34 | 68.73
2019-01-16 17:30 | 67.75 | 66.69
2019-01-16 18:00 | 66.95 | 65.34
2019-01-16 18:30 | 66.1 | 64
2019-01-16 19:00 | 65.79 | 63.45
2019-01-16 19:30 | 65.36 | 63.03
2019-01-16 20:00 | 63.93 | 61.35
2019-01-16 20:30 | 61.86 | 58.85
2019-01-16 21:00 | 60.04 | 56.79
2019-01-16 21:30 | 58.34 | 54.51
2019-01-16 22:00 | 56.83 | 51.43
2019-01-16 22:30 | 54.11 | 48.39
2019-01-16 23:00 | 54.36 | 48.68
2019-01-16 23:30 | 48.05 | 44.56
2019-01-17 | 44.22 | 42.11
2019-01-17 00:30 | 42.66 | 40.5
2019-01-17 01:00 | 41.3 | 38.96
2019-01-17 01:30 | 40.55 | 38.13
2019-01-17 02:00 | 39.69 | 37.22
2019-01-17 02:30 | 38.65 | 36.13
2019-01-17 03:00 | 37.97 | 35.4
2019-01-17 03:30 | 37.88 | 35.3
2019-01-17 04:00 | 37.87 | 35.3
2019-01-17 04:30 | 38.44 | 35.9
2019-01-17 05:00 | 39.46 | 36.98
2019-01-17 05:30 | 41.17 | 38.8
2019-01-17 06:00 | 43.02 | 40.74
2019-01-17 06:30 | 47.29 | 46
2019-01-17 07:00 | 51.13 | 50.48
2019-01-17 07:30 | 57.58 | 56.47
2019-01-17 08:00 | 59.86 | 59.52
2019-01-17 08:30 | 63.01 | 62.33
2019-01-17 09:00 | 64.17 | 63.32
2019-01-17 09:30 | 64.39 | 63.38
2019-01-17 10:00 | 66.13 | 65.02
2019-01-17 10:30 | 66.67 | 65.29
2019-01-17 11:00 | 67.26 | 65.68
2019-01-17 11:30 | 68.27 | 66.66
2019-01-17 12:00 | 69.11 | 67.42
2019-01-17 12:30 | 70.27 | 68.63
2019-01-17 13:00 | 69.37 | 67.76
2019-01-17 13:30 | 69.67 | 68.07
2019-01-17 14:00 | 69.75 | 68.16
2019-01-17 14:30 | 70.73 | 69.13
2019-01-17 15:00 | 70.81 | 69.32
2019-01-17 15:30 | 71.31 | 69.91
2019-01-17 16:00 | 71.7 | 70.51
2019-01-17 16:30 | 71.84 | 70.68
2019-01-17 17:00 | 69.81 | 68.56
2019-01-17 17:30 | 68.55 | 67.22
2019-01-17 18:00 | 67.71 | 66.32
2019-01-17 18:30 | 67.09 | 65.63
2019-01-17 19:00 | 66.98 | 65.49
2019-01-17 19:30 | 67.18 | 65.7
2019-01-17 20:00 | 66.08 | 64.56
2019-01-17 20:30 | 62.87 | 61.93
2019-01-17 21:00 | 59.76 | 59.5
2019-01-17 21:30 | 57.11 | 56.72
2019-01-17 22:00 | 54.19 | 53.89
2019-01-17 22:30 | 50.74 | 50.54
2019-01-17 23:00 | 50.56 | 50.41
2019-01-17 23:30 | 46.37 | 46.27
2019-01-18 | 43.77 | 43.72
2019-01-18 00:30 | 41.95 | 41.93
2019-01-18 01:00 | 40.57 | 40.55
2019-01-18 01:30 | 39.98 | 39.97
2019-01-18 02:00 | 39.16 | 39.14
2019-01-18 02:30 | 38.83 | 38.56
2019-01-18 03:00 | 38.19 | 37.96
2019-01-18 03:30 | 37.62 | 37.4
2019-01-18 04:00 | 37.62 | 37.42
2019-01-18 04:30 | 38.09 | 37.87
2019-01-18 05:00 | 39.28 | 38.99
2019-01-18 05:30 | 41.44 | 41.07
2019-01-18 06:00 | 43.86 | 43.35
2019-01-18 06:30 | 49.12 | 48.4
2019-01-18 07:00 | 53.4 | 52.65
2019-01-18 07:30 | 60.05 | 59.51
2019-01-18 08:00 | 64.38 | 63.88
2019-01-18 08:30 | 64.82 | 64.04
2019-01-18 09:00 | 66.45 | 65.33
2019-01-18 09:30 | 67.52 | 66.33
2019-01-18 10:00 | 66.9 | 65.68
2019-01-18 10:30 | 66.48 | 65.23
2019-01-18 11:00 | 67.4 | 65.98
2019-01-18 11:30 | 68.07 | 66.51
2019-01-18 12:00 | 68.15 | 66.51
2019-01-18 12:30 | 69.75 | 68.15
2019-01-18 13:00 | 70.53 | 69.09
2019-01-18 13:30 | 69.85 | 68.45
2019-01-18 14:00 | 70.16 | 68.76
2019-01-18 14:30 | 69.98 | 68.75
2019-01-18 15:00 | 69.74 | 68.69
2019-01-18 15:30 | 69.21 | 68.34
2019-01-18 16:00 | 68.34 | 67.65
2019-01-18 16:30 | 67.8 | 67.27
2019-01-18 17:00 | 66.66 | 66.32
2019-01-18 17:30 | 64.54 | 64.41
2019-01-18 18:00 | 62.77 | 62.75
2019-01-18 18:30 | 60.39 | 60.39
2019-01-18 19:00 | 60.65 | 60.64
2019-01-18 19:30 | 60.65 | 60.65
2019-01-18 20:00 | 59.36 | 59.35
2019-01-18 20:30 | 57.18 | 57.15
2019-01-18 21:00 | 54.7 | 54.62
2019-01-18 21:30 | 53.13 | 53
2019-01-18 22:00 | 50.73 | 50.5
2019-01-18 22:30 | 49.32 | 47.74
2019-01-18 23:00 | 49.61 | 47.78
2019-01-18 23:30 | 45.71 | 43.64
2019-01-19 | 43.45 | 41.28
2019-01-19 00:30 | 42.26 | 40.05
2019-01-19 01:00 | 41.34 | 39.05
2019-01-19 01:30 | 40.62 | 38.27
2019-01-19 02:00 | 39.83 | 37.43
2019-01-19 02:30 | 39.17 | 36.63
2019-01-19 03:00 | 38.64 | 36.05
2019-01-19 03:30 | 38.37 | 35.76
2019-01-19 04:00 | 38.08 | 35.45
2019-01-19 04:30 | 38.11 | 35.48
2019-01-19 05:00 | 38.19 | 35.56
2019-01-19 05:30 | 39 | 36.44
2019-01-19 06:00 | 38.73 | 36.2
2019-01-19 06:30 | 40.36 | 37.93
2019-01-19 07:00 | 41.69 | 39.33
2019-01-19 07:30 | 44.6 | 42.38
2019-01-19 08:00 | 45.58 | 43.38
2019-01-19 08:30 | 46.75 | 45.89
2019-01-19 09:00 | 49.09 | 48.48
2019-01-19 09:30 | 49.79 | 49.03
2019-01-19 10:00 | 49.91 | 49.06
2019-01-19 10:30 | 49.92 | 49.02
2019-01-19 11:00 | 49.19 | 48.19
2019-01-19 11:30 | 50.23 | 49.12
2019-01-19 12:00 | 49.34 | 48.28
2019-01-19 12:30 | 51.91 | 51.07
2019-01-19 13:00 | 52.88 | 52.22
2019-01-19 13:30 | 49.66 | 48.99
2019-01-19 14:00 | 47.93 | 47.21
2019-01-19 14:30 | 47.57 | 46.92
2019-01-19 15:00 | 48.37 | 47.77
2019-01-19 15:30 | 49.91 | 49.37
2019-01-19 16:00 | 50.75 | 50.27
2019-01-19 16:30 | 51.49 | 51.14
2019-01-19 17:00 | 52.78 | 52.48
2019-01-19 17:30 | 53.06 | 52.83
2019-01-19 18:00 | 54.23 | 54.04
2019-01-19 18:30 | 54.49 | 54.35
2019-01-19 19:00 | 54.7 | 54.56
2019-01-19 19:30 | 55.76 | 55.56
2019-01-19 20:00 | 55.02 | 54.85
2019-01-19 20:30 | 52.88 | 52.75
2019-01-19 21:00 | 51.66 | 51.54
2019-01-19 21:30 | 50.17 | 50.06
2019-01-19 22:00 | 48.33 | 48.27
2019-01-19 22:30 | 45.9 | 45.86
2019-01-19 23:00 | 46.52 | 46.5
2019-01-19 23:30 | 42.97 | 42.96
2019-01-20 | 40.69 | 40.69
2019-01-20 00:30 | 39.57 | 39.56
2019-01-20 01:00 | 38.41 | 38.35
2019-01-20 01:30 | 37.59 | 37.45
2019-01-20 02:00 | 36.97 | 36.84
2019-01-20 02:30 | 36.57 | 36.45
2019-01-20 03:00 | 35.79 | 35.7
2019-01-20 03:30 | 35.37 | 35.29
2019-01-20 04:00 | 35.17 | 35.1
2019-01-20 04:30 | 35.21 | 35.13
2019-01-20 05:00 | 35.12 | 35.04
2019-01-20 05:30 | 35.38 | 35.32
2019-01-20 06:00 | 34.69 | 34.66
2019-01-20 06:30 | 35.84 | 35.79
2019-01-20 07:00 | 36.59 | 36.5
2019-01-20 07:30 | 37.76 | 37.59
2019-01-20 08:00 | 38.54 | 38.21
2019-01-20 08:30 | 40.16 | 39.67
2019-01-20 09:00 | 41.08 | 40.69
2019-01-20 09:30 | 42.04 | 41.83
2019-01-20 10:00 | 43.75 | 43.51
2019-01-20 10:30 | 42.03 | 41.75
2019-01-20 11:00 | 42.79 | 42.48
2019-01-20 11:30 | 43.26 | 42.9
2019-01-20 12:00 | 42.75 | 42.4
2019-01-20 12:30 | 45.56 | 45.2
2019-01-20 13:00 | 45.64 | 45.29
2019-01-20 13:30 | 45.08 | 44.67
2019-01-20 14:00 | 45.43 | 45.02
2019-01-20 14:30 | 45.33 | 44.99
2019-01-20 15:00 | 46.38 | 46.06
2019-01-20 15:30 | 47.25 | 46.99
2019-01-20 16:00 | 48.7 | 48.46
2019-01-20 16:30 | 49.24 | 49.04
2019-01-20 17:00 | 50.69 | 50.53
2019-01-20 17:30 | 52.23 | 52.09
2019-01-20 18:00 | 53.38 | 53.27
2019-01-20 18:30 | 54.05 | 53.97
2019-01-20 19:00 | 54.42 | 54.35
2019-01-20 19:30 | 55.71 | 55.57
2019-01-20 20:00 | 55.37 | 55.24
2019-01-20 20:30 | 53.58 | 53.48
2019-01-20 21:00 | 51.55 | 51.48
2019-01-20 21:30 | 49.35 | 49.31
2019-01-20 22:00 | 47.05 | 47.03
2019-01-20 22:30 | 44.71 | 44.7
2019-01-20 23:00 | 45.55 | 45.55
2019-01-20 23:30 | 41.65 | 41.65
2019-01-21 | 39.23 | 39.22
2019-01-21 00:30 | 38.13 | 38.1
2019-01-21 01:00 | 38.23 | 37.06
2019-01-21 01:30 | 39.08 | 36.56
2019-01-21 02:00 | 38.81 | 36.26
2019-01-21 02:30 | 38.3 | 35.71
2019-01-21 03:00 | 37.83 | 35.22
2019-01-21 03:30 | 37.87 | 35.25
2019-01-21 04:00 | 37.89 | 35.27
2019-01-21 04:30 | 38.9 | 36.34
2019-01-21 05:00 | 40.12 | 37.63
2019-01-21 05:30 | 42.1 | 39.73
2019-01-21 06:00 | 44.71 | 42.47
2019-01-21 06:30 | 50.41 | 48.38
2019-01-21 07:00 | 54.97 | 53.2
2019-01-21 07:30 | 59.74 | 59
2019-01-21 08:00 | 62.55 | 61.42
2019-01-21 08:30 | 64.47 | 62.98
2019-01-21 09:00 | 65.82 | 63.97
2019-01-21 09:30 | 66.08 | 64
2019-01-21 10:00 | 66.2 | 63.95
2019-01-21 10:30 | 66.42 | 63.93
2019-01-21 11:00 | 66.66 | 64.08
2019-01-21 11:30 | 67.61 | 64.82
2019-01-21 12:00 | 68.4 | 65.59
2019-01-21 12:30 | 68.91 | 66.08
2019-01-21 13:00 | 69.17 | 66.32
2019-01-21 13:30 | 69.52 | 66.73
2019-01-21 14:00 | 70.17 | 67.39
2019-01-21 14:30 | 70.34 | 67.63
2019-01-21 15:00 | 70.51 | 68.4
2019-01-21 15:30 | 70.77 | 69.47
2019-01-21 16:00 | 70.63 | 69.45
2019-01-21 16:30 | 70.1 | 68.87
2019-01-21 17:00 | 69.17 | 67.88
2019-01-21 17:30 | 67.31 | 65.91
2019-01-21 18:00 | 65.91 | 64.4
2019-01-21 18:30 | 63.4 | 63.36
2019-01-21 19:00 | 63.07 | 62.96
2019-01-21 19:30 | 64 | 63.84
2019-01-21 20:00 | 62.23 | 62.12
2019-01-21 20:30 | 59.45 | 59.4
2019-01-21 21:00 | 57.14 | 57.1
2019-01-21 21:30 | 54.45 | 54.43
2019-01-21 22:00 | 51.61 | 51.61
2019-01-21 22:30 | 48.3 | 48.29
2019-01-21 23:00 | 48.81 | 48.79
2019-01-21 23:30 | 45.08 | 45.03
2019-01-22 | 42.54 | 42.28
2019-01-22 00:30 | 43.1 | 41.01
2019-01-22 01:00 | 42.07 | 39.86
2019-01-22 01:30 | 41.7 | 39.41
2019-01-22 02:00 | 41.23 | 38.91
2019-01-22 02:30 | 40.65 | 38.29
2019-01-22 03:00 | 39.84 | 37.49
2019-01-22 03:30 | 39.58 | 37.22
2019-01-22 04:00 | 39.49 | 37.05
2019-01-22 04:30 | 40.25 | 37.81
2019-01-22 05:00 | 41.35 | 38.97
2019-01-22 05:30 | 43.48 | 41.21
2019-01-22 06:00 | 45.35 | 43.16
2019-01-22 06:30 | 49.71 | 48.36
2019-01-22 07:00 | 54.6 | 53.72
2019-01-22 07:30 | 55.27 | 54.5
2019-01-22 08:00 | 48.72 | 48.19
2019-01-22 08:30 | 48.67 | 47.93
2019-01-22 09:00 | 51.27 | 50.2
2019-01-22 09:30 | 50.76 | 49.47
2019-01-22 10:00 | 49.82 | 48.44
2019-01-22 10:30 | 52.5 | 51.1
2019-01-22 11:00 | 52.46 | 51.04
2019-01-22 11:30 | 52.31 | 50.84
2019-01-22 12:00 | 51.02 | 49.44
2019-01-22 12:30 | 51.84 | 50.28
2019-01-22 13:00 | 68.47 | 66.73
2019-01-22 13:30 | 68.53 | 66.78
2019-01-22 14:00 | 69.11 | 67.34
2019-01-22 14:30 | 69.68 | 67.93
2019-01-22 15:00 | 70.23 | 68.62
2019-01-22 15:30 | 70.48 | 69.02
2019-01-22 16:00 | 70.57 | 69.42
2019-01-22 16:30 | 69.82 | 69.06
2019-01-22 17:00 | 68.29 | 67.83
2019-01-22 17:30 | 66.5 | 66.19
2019-01-22 18:00 | 65.03 | 64.67
2019-01-22 18:30 | 62.98 | 62.59
2019-01-22 19:00 | 63.01 | 62.61
2019-01-22 19:30 | 63.65 | 63.25
2019-01-22 20:00 | 62 | 61.59
2019-01-22 20:30 | 59.61 | 59.42
2019-01-22 21:00 | 57.56 | 57.53
2019-01-22 21:30 | 55.13 | 55.07
2019-01-22 22:00 | 51.81 | 51.67
2019-01-22 22:30 | 49.38 | 48.58
2019-01-22 23:00 | 50.27 | 48.57
2019-01-22 23:30 | 46.48 | 44.67
2019-01-23 | 43.96 | 42.05
2019-01-23 00:30 | 42.88 | 40.93
2019-01-23 01:00 | 41.78 | 39.68
2019-01-23 01:30 | 41.27 | 39.02
2019-01-23 02:00 | 40.61 | 38.33
2019-01-23 02:30 | 40.12 | 37.81
2019-01-23 03:00 | 39.69 | 37.35
2019-01-23 03:30 | 39.75 | 37.43
2019-01-23 04:00 | 39.59 | 37.15
2019-01-23 04:30 | 40.53 | 38.11
2019-01-23 05:00 | 41.41 | 39
2019-01-23 05:30 | 43.43 | 41.12
2019-01-23 06:00 | 45.72 | 43.52
2019-01-23 06:30 | 49.96 | 47.92
2019-01-23 07:00 | 54.88 | 53.06
2019-01-23 07:30 | 60.89 | 60.04
2019-01-23 08:00 | 64.8 | 64.31
2019-01-23 08:30 | 67.99 | 67.23
2019-01-23 09:00 | 70.23 | 69.54
2019-01-23 09:30 | 70.55 | 70.35
2019-01-23 10:00 | 69.14 | 68.93
2019-01-23 10:30 | 68.91 | 68.76
2019-01-23 11:00 | 68.96 | 68.85
2019-01-23 11:30 | 68.45 | 68.38
2019-01-23 12:00 | 67.87 | 67.82
2019-01-23 12:30 | 68.63 | 68.57
2019-01-23 13:00 | 68.61 | 68.55
2019-01-23 13:30 | 69.11 | 69.07
2019-01-23 14:00 | 70.06 | 70.02
2019-01-23 14:30 | 69.26 | 69.23
2019-01-23 15:00 | 68.58 | 68.54
2019-01-23 15:30 | 69.39 | 69.32
2019-01-23 16:00 | 70.06 | 69.94
2019-01-23 16:30 | 69.99 | 69.73
2019-01-23 17:00 | 70.09 | 69.6
2019-01-23 17:30 | 68.04 | 67.1
2019-01-23 18:00 | 67.41 | 65.97
2019-01-23 18:30 | 66.02 | 64.01
2019-01-23 19:00 | 65.96 | 63.82
2019-01-23 19:30 | 66.73 | 64.73
2019-01-23 20:00 | 65.51 | 63.22
2019-01-23 20:30 | 63.33 | 60.64
2019-01-23 21:00 | 61.28 | 58.25
2019-01-23 21:30 | 58.66 | 55.11
2019-01-23 22:00 | 56.72 | 51.79
2019-01-23 22:30 | 54.21 | 48.5
2019-01-23 23:00 | 54.54 | 48.89
2019-01-23 23:30 | 50.75 | 44.51
2019-01-24 | 48.75 | 41.97
2019-01-24 00:30 | 48.07 | 40.22
2019-01-24 01:00 | 43.44 | 38.82
2019-01-24 01:30 | 42.82 | 38.11
2019-01-24 02:00 | 41.9 | 37.08
2019-01-24 02:30 | 40.75 | 35.64
2019-01-24 03:00 | 40.32 | 35.08
2019-01-24 03:30 | 40.08 | 34.7
2019-01-24 04:00 | 39.97 | 34.58
2019-01-24 04:30 | 40.51 | 35.2
2019-01-24 05:00 | 41.33 | 36.13
2019-01-24 05:30 | 43.4 | 38.48
2019-01-24 06:00 | 45.08 | 40.34
2019-01-24 06:30 | 46.28 | 45.43
2019-01-24 07:00 | 50.36 | 49.69
2019-01-24 07:30 | 56.28 | 55.44
2019-01-24 08:00 | 59.27 | 58.8
2019-01-24 08:30 | 61.28 | 60.65
2019-01-24 09:00 | 63.21 | 62.33
2019-01-24 09:30 | 64.19 | 63.12
2019-01-24 10:00 | 64.92 | 63.71
2019-01-24 10:30 | 65.81 | 64.47
2019-01-24 11:00 | 67.62 | 65.96
2019-01-24 11:30 | 68 | 66.23
2019-01-24 12:00 | 68.89 | 66.99
2019-01-24 12:30 | 70.87 | 69.07
2019-01-24 13:00 | 70.64 | 68.88
2019-01-24 13:30 | 71.62 | 69.8
2019-01-24 14:00 | 72.28 | 70.46
2019-01-24 14:30 | 74 | 72.2
2019-01-24 15:00 | 74.87 | 73.11
2019-01-24 15:30 | 75.32 | 73.76
2019-01-24 16:00 | 74.25 | 72.9
2019-01-24 16:30 | 72.68 | 71.78
2019-01-24 17:00 | 72.99 | 72.57
2019-01-24 17:30 | 69.86 | 68.97
2019-01-24 18:00 | 68.07 | 66.64
2019-01-24 18:30 | 67.07 | 65.15
2019-01-24 19:00 | 67.17 | 65.2
2019-01-24 19:30 | 67.74 | 65.93
2019-01-24 20:00 | 67 | 65.05
2019-01-24 20:30 | 64.89 | 62.51
2019-01-24 21:00 | 62.99 | 60.33
2019-01-24 21:30 | 60.31 | 57.39
2019-01-24 22:00 | 55.39 | 53.87
2019-01-24 22:30 | 51.98 | 50.37
2019-01-24 23:00 | 52.45 | 50.86
2019-01-24 23:30 | 48.63 | 46.9
2019-01-25 | 45.88 | 44.05
2019-01-25 00:30 | 44.21 | 42.34
2019-01-25 01:00 | 43.16 | 41.22
2019-01-25 01:30 | 42.62 | 40.65
2019-01-25 02:00 | 41.85 | 39.82
2019-01-25 02:30 | 40.78 | 38.52
2019-01-25 03:00 | 40.31 | 38.01
2019-01-25 03:30 | 39.82 | 37.48
2019-01-25 04:00 | 40.2 | 37.77
2019-01-25 04:30 | 40.95 | 38.58
2019-01-25 05:00 | 42.04 | 39.73
2019-01-25 05:30 | 44.49 | 42.3
2019-01-25 06:00 | 45.59 | 44.36
2019-01-25 06:30 | 50.33 | 49.44
2019-01-25 07:00 | 54.76 | 53.95
2019-01-25 07:30 | 60.64 | 59.97
2019-01-25 08:00 | 63.89 | 63.31
2019-01-25 08:30 | 66.52 | 65.6
2019-01-25 09:00 | 68.44 | 67.26
2019-01-25 09:30 | 69.06 | 67.81
2019-01-25 10:00 | 68.14 | 66.8
2019-01-25 10:30 | 68.27 | 66.77
2019-01-25 11:00 | 69.2 | 67.49
2019-01-25 11:30 | 69.51 | 67.71
2019-01-25 12:00 | 69.21 | 67.46
2019-01-25 12:30 | 69.18 | 67.63
2019-01-25 13:00 | 68.51 | 66.95
2019-01-25 13:30 | 69.24 | 67.69
2019-01-25 14:00 | 69.09 | 67.67
2019-01-25 14:30 | 69.05 | 67.69
2019-01-25 15:00 | 69.2 | 67.98
2019-01-25 15:30 | 69.5 | 68.51
2019-01-25 16:00 | 68.34 | 67.59
2019-01-25 16:30 | 67.78 | 67.26
2019-01-25 17:00 | 67.73 | 67.35
2019-01-25 17:30 | 66.7 | 66.38
2019-01-25 18:00 | 63.71 | 63.35
2019-01-25 18:30 | 62.45 | 62.05
2019-01-25 19:00 | 62.58 | 62.18
2019-01-25 19:30 | 63.08 | 62.68
2019-01-25 20:00 | 61.72 | 61.31
2019-01-25 20:30 | 60.05 | 59.62
2019-01-25 21:00 | 58.22 | 57.76
2019-01-25 21:30 | 55.76 | 55.33
2019-01-25 22:00 | 52.89 | 52.5
2019-01-25 22:30 | 50.8 | 50.39
2019-01-25 23:00 | 50.78 | 50.34
2019-01-25 23:30 | 47.08 | 46.61
2019-01-26 | 44.42 | 43.88
2019-01-26 00:30 | 42.9 | 42.34
2019-01-26 01:00 | 41.61 | 41.04
2019-01-26 01:30 | 40.6 | 40.02
2019-01-26 02:00 | 39.73 | 39.15
2019-01-26 02:30 | 39.13 | 38.54
2019-01-26 03:00 | 38.71 | 38.11
2019-01-26 03:30 | 38.51 | 37.84
2019-01-26 04:00 | 38.27 | 37.6
2019-01-26 04:30 | 38.65 | 37.99
2019-01-26 05:00 | 39.02 | 38.36
2019-01-26 05:30 | 39.95 | 39.3
2019-01-26 06:00 | 39.88 | 39.23
2019-01-26 06:30 | 41.32 | 40.68
2019-01-26 07:00 | 42.54 | 41.91
2019-01-26 07:30 | 45.3 | 44.67
2019-01-26 08:00 | 47.97 | 47.34
2019-01-26 08:30 | 49.28 | 48.74
2019-01-26 09:00 | 50.09 | 49.53
2019-01-26 09:30 | 51.15 | 50.5
2019-01-26 10:00 | 50.9 | 50.16
2019-01-26 10:30 | 49.76 | 48.95
2019-01-26 11:00 | 49.46 | 48.46
2019-01-26 11:30 | 51.37 | 50.43
2019-01-26 12:00 | 52.38 | 51.57
2019-01-26 12:30 | 53.98 | 53.32
2019-01-26 13:00 | 52.01 | 51.42
2019-01-26 13:30 | 50.53 | 49.96
2019-01-26 14:00 | 47.62 | 47.03
2019-01-26 14:30 | 48.27 | 47.7
2019-01-26 15:00 | 48.26 | 47.69
2019-01-26 15:30 | 50.24 | 49.71
2019-01-26 16:00 | 49.03 | 48.49
2019-01-26 16:30 | 49.7 | 49.17
2019-01-26 17:00 | 49.99 | 49.47
2019-01-26 17:30 | 50.29 | 49.78
2019-01-26 18:00 | 51.74 | 51.26
2019-01-26 18:30 | 51.73 | 51.25
2019-01-26 19:00 | 52.23 | 51.75
2019-01-26 19:30 | 53.09 | 52.62
2019-01-26 20:00 | 52.75 | 52.27
2019-01-26 20:30 | 51.77 | 51.28
2019-01-26 21:00 | 50.76 | 50.26
2019-01-26 21:30 | 49.19 | 48.69
2019-01-26 22:00 | 47.98 | 47.47
2019-01-26 22:30 | 46.28 | 45.75
2019-01-26 23:00 | 47.06 | 46.54
2019-01-26 23:30 | 43.93 | 43.38
2019-01-27 | 41.96 | 41.39
2019-01-27 00:30 | 41.01 | 40.43
2019-01-27 01:00 | 40.06 | 39.47
2019-01-27 01:30 | 39.4 | 38.79
2019-01-27 02:00 | 38.91 | 38.3
2019-01-27 02:30 | 38.48 | 37.86
2019-01-27 03:00 | 37.8 | 37.13
2019-01-27 03:30 | 37.74 | 37.04
2019-01-27 04:00 | 37.73 | 37.03
2019-01-27 04:30 | 37.95 | 37.25
2019-01-27 05:00 | 32.52 | 31.67
2019-01-27 05:30 | 37.61 | 36.9
2019-01-27 06:00 | 38.28 | 37.6
2019-01-27 06:30 | 39.11 | 38.44
2019-01-27 07:00 | 40.02 | 39.36
2019-01-27 07:30 | 41.55 | 40.91
2019-01-27 08:00 | 42.68 | 42.04
2019-01-27 08:30 | 46.2 | 45.6
2019-01-27 09:00 | 47.68 | 47.08
2019-01-27 09:30 | 48.35 | 47.77
2019-01-27 10:00 | 50.01 | 49.5
2019-01-27 10:30 | 50.97 | 50.46
2019-01-27 11:00 | 50.31 | 49.79
2019-01-27 11:30 | 48.88 | 48.34
2019-01-27 12:00 | 47.63 | 47.07
2019-01-27 12:30 | 49.1 | 48.56
2019-01-27 13:00 | 48.15 | 47.6
2019-01-27 13:30 | 47.93 | 47.38
2019-01-27 14:00 | 46.54 | 45.97
2019-01-27 14:30 | 47.52 | 46.97
2019-01-27 15:00 | 46.9 | 46.34
2019-01-27 15:30 | 46.81 | 46.27
2019-01-27 16:00 | 46.65 | 46.11
2019-01-27 16:30 | 47.24 | 46.72
2019-01-27 17:00 | 47.92 | 47.41
2019-01-27 17:30 | 48.19 | 47.68
2019-01-27 18:00 | 49.09 | 48.6
2019-01-27 18:30 | 49.72 | 49.23
2019-01-27 19:00 | 49.64 | 49.16
2019-01-27 19:30 | 49.84 | 49.36
2019-01-27 20:00 | 49.37 | 48.88
2019-01-27 20:30 | 47.88 | 47.37
2019-01-27 21:00 | 45.89 | 45.36
2019-01-27 21:30 | 44.96 | 44.42
2019-01-27 22:00 | 44.31 | 43.77
2019-01-27 22:30 | 42.59 | 42.03
2019-01-27 23:00 | 43.23 | 42.68
2019-01-27 23:30 | 39.25 | 39.13
2019-01-28 | 37.42 | 37.39
2019-01-28 00:30 | 37.11 | 37.05
2019-01-28 01:00 | 36.45 | 36.35
2019-01-28 01:30 | 35.38 | 35.29
2019-01-28 02:00 | 34.59 | 34.51
2019-01-28 02:30 | 34.59 | 34.5
2019-01-28 03:00 | 34.36 | 34.28
2019-01-28 03:30 | 34.72 | 34.64
2019-01-28 04:00 | 34.28 | 34.21
2019-01-28 04:30 | 34.5 | 34.41
2019-01-28 05:00 | 35.19 | 35.09
2019-01-28 05:30 | 36.58 | 36.48
2019-01-28 06:00 | 37.43 | 37.3
2019-01-28 06:30 | 39.49 | 39.29
2019-01-28 07:00 | 42.55 | 40.82
2019-01-28 07:30 | 44.99 | 43.2
2019-01-28 08:00 | 47.39 | 45.74
2019-01-28 08:30 | 48.64 | 47.04
2019-01-28 09:00 | 49.38 | 47.74
2019-01-28 09:30 | 50.25 | 48.6
2019-01-28 10:00 | 50.89 | 49.27
2019-01-28 10:30 | 51.4 | 49.8
2019-01-28 11:00 | 52.5 | 50.94
2019-01-28 11:30 | 51.87 | 50.3
2019-01-28 12:00 | 51.21 | 49.61
2019-01-28 12:30 | 51.33 | 49.75
2019-01-28 13:00 | 50.93 | 49.31
2019-01-28 13:30 | 48.84 | 47.16
2019-01-28 14:00 | 48.64 | 46.95
2019-01-28 14:30 | 47.64 | 45.9
2019-01-28 15:00 | 47.16 | 45.41
2019-01-28 15:30 | 48.66 | 46.97
2019-01-28 16:00 | 50.59 | 48.96
2019-01-28 16:30 | 51.87 | 50.28
2019-01-28 17:00 | 52.09 | 50.49
2019-01-28 17:30 | 53.12 | 51.55
2019-01-28 18:00 | 54.55 | 53.03
2019-01-28 18:30 | 54.02 | 52.46
2019-01-28 19:00 | 54 | 52.44
2019-01-28 19:30 | 53.86 | 52.29
2019-01-28 20:00 | 52.68 | 51.08
2019-01-28 20:30 | 50.91 | 49.21
2019-01-28 21:00 | 49.24 | 47.47
2019-01-28 21:30 | 47.22 | 45.34
2019-01-28 22:00 | 45.59 | 43.62
2019-01-28 22:30 | 43.92 | 41.84
2019-01-28 23:00 | 45.47 | 43.47
2019-01-28 23:30 | 41.24 | 38.98
2019-01-29 | 39.41 | 37.12
2019-01-29 00:30 | 38.19 | 35.9
2019-01-29 01:00 | 37.33 | 34.96
2019-01-29 01:30 | 37.16 | 34.77
2019-01-29 02:00 | 37.03 | 34.63
2019-01-29 02:30 | 36.92 | 34.52
2019-01-29 03:00 | 36.93 | 34.51
2019-01-29 03:30 | 36.85 | 34.43
2019-01-29 04:00 | 37.21 | 34.84
2019-01-29 04:30 | 38.44 | 36.18
2019-01-29 05:00 | 39.57 | 37.39
2019-01-29 05:30 | 41.99 | 39.98
2019-01-29 06:00 | 44.26 | 42.41
2019-01-29 06:30 | 50.46 | 48.96
2019-01-29 07:00 | 60.33 | 55.43
2019-01-29 07:30 | 68.01 | 62.79
2019-01-29 08:00 | 70.75 | 65.86
2019-01-29 08:30 | 72.78 | 68.18
2019-01-29 09:00 | 74.28 | 69.43
2019-01-29 09:30 | 76.24 | 71.05
2019-01-29 10:00 | 76.62 | 71.44
2019-01-29 10:30 | 76.57 | 71.39
2019-01-29 11:00 | 76.96 | 71.81
2019-01-29 11:30 | 76.19 | 70.91
2019-01-29 12:00 | 72.46 | 68.98
2019-01-29 12:30 | 70.58 | 69.16
2019-01-29 13:00 | 70.38 | 68.94
2019-01-29 13:30 | 69.57 | 68.13
2019-01-29 14:00 | 70.2 | 68.77
2019-01-29 14:30 | 70.19 | 68.74
2019-01-29 15:00 | 68.8 | 67.31
2019-01-29 15:30 | 67.89 | 66.35
2019-01-29 16:00 | 68.15 | 66.59
2019-01-29 16:30 | 67.53 | 65.92
2019-01-29 17:00 | 66.17 | 64.47
2019-01-29 17:30 | 64.1 | 62.22
2019-01-29 18:00 | 63.28 | 60.92
2019-01-29 18:30 | 62.26 | 59.38
2019-01-29 19:00 | 54.28 | 51.45
2019-01-29 19:30 | 62.09 | 59.08
2019-01-29 20:00 | 60.76 | 57.49
2019-01-29 20:30 | 58.67 | 54.83
2019-01-29 21:00 | 57.08 | 53.04
2019-01-29 21:30 | 55.18 | 50.7
2019-01-29 22:00 | 52.92 | 48.23
2019-01-29 22:30 | 46.25 | 45.71
2019-01-29 23:00 | 46.13 | 46.08
2019-01-29 23:30 | 42.29 | 42.2
2019-01-30 | 39.9 | 39.84
2019-01-30 00:30 | 38.74 | 38.74
2019-01-30 01:00 | 38.07 | 38.07
2019-01-30 01:30 | 37.15 | 37.15
2019-01-30 02:00 | 36.39 | 36.39
2019-01-30 02:30 | 36.11 | 36.11
2019-01-30 03:00 | 35.35 | 35.2
2019-01-30 03:30 | 35.14 | 35.02
2019-01-30 04:00 | 35.32 | 35.2
2019-01-30 04:30 | 35.9 | 35.76
2019-01-30 05:00 | 37.1 | 36.91
2019-01-30 05:30 | 39.94 | 39.67
2019-01-30 06:00 | 43.46 | 43.02
2019-01-30 06:30 | 51.28 | 49.85
2019-01-30 07:00 | 56.69 | 55.36
2019-01-30 07:30 | 67.3 | 62.62
2019-01-30 08:00 | 70.01 | 65
2019-01-30 08:30 | 71.33 | 66.55
2019-01-30 09:00 | 72.89 | 68.3
2019-01-30 09:30 | 73.41 | 68.89
2019-01-30 10:00 | 73.06 | 68.5
2019-01-30 10:30 | 73.55 | 69.08
2019-01-30 11:00 | 72.16 | 67.59
2019-01-30 11:30 | 73.56 | 69.12
2019-01-30 12:00 | 73.56 | 69.12
2019-01-30 12:30 | 74.74 | 70.37
2019-01-30 13:00 | 73.5 | 69.02
2019-01-30 13:30 | 72.69 | 68.15
2019-01-30 14:00 | 71.93 | 67.29
2019-01-30 14:30 | 72 | 67.18
2019-01-30 15:00 | 71.49 | 66.6
2019-01-30 15:30 | 71.25 | 66.3
2019-01-30 16:00 | 70.78 | 65.68
2019-01-30 16:30 | 70.33 | 65.11
2019-01-30 17:00 | 70.33 | 65.12
2019-01-30 17:30 | 68.44 | 62.95
2019-01-30 18:00 | 67.46 | 61.77
2019-01-30 18:30 | 66.27 | 60.33
2019-01-30 19:00 | 66.63 | 60.77
2019-01-30 19:30 | 66.64 | 60.75
2019-01-30 20:00 | 64.83 | 58.68
2019-01-30 20:30 | 62.04 | 55.91
2019-01-30 21:00 | 60.2 | 54
2019-01-30 21:30 | 58.53 | 52.06
2019-01-30 22:00 | 56.43 | 49.58
2019-01-30 22:30 | 53.97 | 46.67
2019-01-30 23:00 | 54.69 | 47.48
2019-01-30 23:30 | 51.46 | 43.56
2019-01-31 | 49.51 | 41.17
2019-01-31 00:30 | 48.11 | 39.81
2019-01-31 01:00 | 47.34 | 38.86
2019-01-31 01:30 | 46.67 | 38
2019-01-31 02:00 | 46.31 | 37.52
2019-01-31 02:30 | 45.85 | 36.92
2019-01-31 03:00 | 45.39 | 36.29
2019-01-31 03:30 | 45.53 | 36.49
2019-01-31 04:00 | 45.71 | 36.71
2019-01-31 04:30 | 46.38 | 37.58
2019-01-31 05:00 | 47.35 | 38.84
2019-01-31 05:30 | 49.36 | 41.37
2019-01-31 06:00 | 51.44 | 43.97
2019-01-31 06:30 | 56.66 | 50.28
2019-01-31 07:00 | 61.41 | 55.62
2019-01-31 07:30 | 67.39 | 62.34
2019-01-31 08:00 | 72.05 | 66.69
2019-01-31 08:30 | 79.39 | 68.8
2019-01-31 09:00 | 74.82 | 68.72
2019-01-31 09:30 | 68.13 | 67.59
2019-01-31 10:00 | 68.02 | 66.82
2019-01-31 10:30 | 68.72 | 67.52
2019-01-31 11:00 | 67.85 | 66.62
2019-01-31 11:30 | 68.62 | 67.4
2019-01-31 12:00 | 69.65 | 68.47
2019-01-31 12:30 | 67.98 | 66.76
2019-01-31 13:00 | 66.72 | 65.48
2019-01-31 13:30 | 66.11 | 64.86
2019-01-31 14:00 | 67.69 | 66.48
2019-01-31 14:30 | 67.21 | 65.99
2019-01-31 15:00 | 67.53 | 66.31
2019-01-31 15:30 | 65.65 | 64.31
2019-01-31 16:00 | 66.97 | 65.52
2019-01-31 16:30 | 66.13 | 65.26
2019-01-31 17:00 | 63.39 | 63.15
2019-01-31 17:30 | 61.35 | 61.27
2019-01-31 18:00 | 61.1 | 61.09
2019-01-31 18:30 | 61.21 | 61.21
2019-01-31 19:00 | 61.93 | 61.93
2019-01-31 19:30 | 61.67 | 61.67
2019-01-31 20:00 | 61.84 | 60.39
2019-01-31 20:30 | 59.86 | 58.29
2019-01-31 21:00 | 57.96 | 56.22
2019-01-31 21:30 | 55.22 | 53.4
2019-01-31 22:00 | 53.04 | 51.14
2019-01-31 22:30 | 49.89 | 47.87
2019-01-31 23:00 | 50 | 48.04
2019-01-31 23:30 | 45.63 | 43.6
2019-02-01 | 43.61 | 41.47
2019-02-01 00:30 | 42.54 | 40.27
2019-02-01 01:00 | 41.44 | 39.07
2019-02-01 01:30 | 40.98 | 38.58
2019-02-01 02:00 | 40.17 | 37.72
2019-02-01 02:30 | 39.61 | 37.13
2019-02-01 03:00 | 39.46 | 36.98
2019-02-01 03:30 | 39.09 | 36.59
2019-02-01 04:00 | 39.13 | 36.62
2019-02-01 04:30 | 39.83 | 37.36
2019-02-01 05:00 | 41.1 | 38.71
2019-02-01 05:30 | 43.41 | 41.15
2019-02-01 06:00 | 45.58 | 43.41
2019-02-01 06:30 | 51.25 | 49.64
2019-02-01 07:00 | 55.92 | 55.18
2019-02-01 07:30 | 63.18 | 62.29
2019-02-01 08:00 | 65.15 | 64.27
2019-02-01 08:30 | 66.02 | 65.3
2019-02-01 09:00 | 67.24 | 66.29
2019-02-01 09:30 | 66.86 | 65.75
2019-02-01 10:00 | 64.91 | 63.79
2019-02-01 10:30 | 66.94 | 65.71
2019-02-01 11:00 | 67.12 | 65.84
2019-02-01 11:30 | 66.82 | 65.39
2019-02-01 12:00 | 65.56 | 64.06
2019-02-01 12:30 | 68.59 | 67.22
2019-02-01 13:00 | 68.94 | 67.69
2019-02-01 13:30 | 67.03 | 65.77
2019-02-01 14:00 | 67.84 | 66.62
2019-02-01 14:30 | 66.93 | 65.84
2019-02-01 15:00 | 65.12 | 64.1
2019-02-01 15:30 | 65.47 | 64.69
2019-02-01 16:00 | 66.72 | 66.16
2019-02-01 16:30 | 64.79 | 64.42
2019-02-01 17:00 | 63.45 | 63.06
2019-02-01 17:30 | 62.21 | 61.82
2019-02-01 18:00 | 61.24 | 61.03
2019-02-01 18:30 | 59.84 | 59.75
2019-02-01 19:00 | 59.5 | 59.42
2019-02-01 19:30 | 59.75 | 59.67
2019-02-01 20:00 | 58.76 | 58.71
2019-02-01 20:30 | 56.81 | 56.78
2019-02-01 21:00 | 54.88 | 54.69
2019-02-01 21:30 | 53.08 | 52.88
2019-02-01 22:00 | 51.25 | 51.1
2019-02-01 22:30 | 48.38 | 48.29
2019-02-01 23:00 | 48.68 | 48.62
2019-02-01 23:30 | 44.66 | 44.64
2019-02-02 | 42.55 | 42.54
2019-02-02 00:30 | 41.18 | 41.18
2019-02-02 01:00 | 40.33 | 40.15
2019-02-02 01:30 | 39.68 | 39.44
2019-02-02 02:00 | 38.9 | 38.68
2019-02-02 02:30 | 38.2 | 38
2019-02-02 03:00 | 37.58 | 37.4
2019-02-02 03:30 | 37.25 | 37.08
2019-02-02 04:00 | 37.28 | 37.1
2019-02-02 04:30 | 37.34 | 37.17
2019-02-02 05:00 | 37.73 | 37.53
2019-02-02 05:30 | 38.78 | 38.59
2019-02-02 06:00 | 39.49 | 39.28
2019-02-02 06:30 | 41.58 | 41.27
2019-02-02 07:00 | 42.44 | 42.03
2019-02-02 07:30 | 45.1 | 44.46
2019-02-02 08:00 | 48.76 | 47.83
2019-02-02 08:30 | 52.82 | 52.35
2019-02-02 09:00 | 52.65 | 52
2019-02-02 09:30 | 52.34 | 51.57
2019-02-02 10:00 | 52.38 | 51.48
2019-02-02 10:30 | 51.75 | 50.77
2019-02-02 11:00 | 52.64 | 51.61
2019-02-02 11:30 | 54.22 | 53.3
2019-02-02 12:00 | 53.37 | 52.49
2019-02-02 12:30 | 51.95 | 51.14
2019-02-02 13:00 | 48.99 | 48.21
2019-02-02 13:30 | 49.46 | 48.64
2019-02-02 14:00 | 51.14 | 50.42
2019-02-02 14:30 | 50.5 | 49.9
2019-02-02 15:00 | 48.8 | 48.24
2019-02-02 15:30 | 51.1 | 50.66
2019-02-02 16:00 | 51.58 | 51.23
2019-02-02 16:30 | 51.04 | 50.8
2019-02-02 17:00 | 51.98 | 51.78
2019-02-02 17:30 | 51.96 | 51.81
2019-02-02 18:00 | 52.98 | 52.85
2019-02-02 18:30 | 53.45 | 53.34
2019-02-02 19:00 | 53.99 | 53.87
2019-02-02 19:30 | 54.6 | 54.46
2019-02-02 20:00 | 53.62 | 53.49
2019-02-02 20:30 | 52.09 | 51.99
2019-02-02 21:00 | 50.97 | 50.88
2019-02-02 21:30 | 49.46 | 49.39
2019-02-02 22:00 | 48.01 | 47.96
2019-02-02 22:30 | 46.39 | 46.36
2019-02-02 23:00 | 47.23 | 47.22
2019-02-02 23:30 | 42.92 | 42.92
2019-02-03 | 41.19 | 41.19
2019-02-03 00:30 | 40.21 | 40.21
2019-02-03 01:00 | 39.2 | 39.19
2019-02-03 01:30 | 38.57 | 38.41
2019-02-03 02:00 | 37.96 | 37.81
2019-02-03 02:30 | 36.96 | 36.84
2019-02-03 03:00 | 36.21 | 36.13
2019-02-03 03:30 | 35.93 | 35.86
2019-02-03 04:00 | 35.73 | 35.66
2019-02-03 04:30 | 35.94 | 35.86
2019-02-03 05:00 | 36.14 | 36.04
2019-02-03 05:30 | 36.42 | 36.35
2019-02-03 06:00 | 36.21 | 36.15
2019-02-03 06:30 | 37.6 | 37.54
2019-02-03 07:00 | 38.58 | 38.48
2019-02-03 07:30 | 40.4 | 40.23
2019-02-03 08:00 | 42.14 | 41.83
2019-02-03 08:30 | 45.54 | 45.14
2019-02-03 09:00 | 48.04 | 47.59
2019-02-03 09:30 | 49.78 | 49.48
2019-02-03 10:00 | 49.8 | 49.66
2019-02-03 10:30 | 51.49 | 51.33
2019-02-03 11:00 | 48.91 | 48.76
2019-02-03 11:30 | 50.13 | 49.98
2019-02-03 12:00 | 48.88 | 48.73
2019-02-03 12:30 | 47.85 | 47.69
2019-02-03 13:00 | 48.98 | 48.83
2019-02-03 13:30 | 48.34 | 48.2
2019-02-03 14:00 | 49.71 | 49.59
2019-02-03 14:30 | 48.97 | 48.92
2019-02-03 15:00 | 46.91 | 46.88
2019-02-03 15:30 | 47.68 | 47.66
2019-02-03 16:00 | 47 | 46.99
2019-02-03 16:30 | 47.56 | 47.55
2019-02-03 17:00 | 48.02 | 48.01
2019-02-03 17:30 | 48.5 | 48.49
2019-02-03 18:00 | 49.81 | 49.8
2019-02-03 18:30 | 50.25 | 50.24
2019-02-03 19:00 | 51.02 | 51
2019-02-03 19:30 | 52.34 | 50.59
2019-02-03 20:00 | 47.7 | 45.63
2019-02-03 20:30 | 49.74 | 47.8
2019-02-03 21:00 | 48.19 | 46.17
2019-02-03 21:30 | 46.99 | 44.91
2019-02-03 22:00 | 45.41 | 43.32
2019-02-03 22:30 | 43.75 | 41.57
2019-02-03 23:00 | 44.31 | 42.15
2019-02-03 23:30 | 41.01 | 38.61
2019-02-04 | 39.4 | 36.98
2019-02-04 00:30 | 38.58 | 36.12
2019-02-04 01:00 | 37.82 | 35.29
2019-02-04 01:30 | 37.41 | 34.85
2019-02-04 02:00 | 36.89 | 34.29
2019-02-04 02:30 | 36.44 | 33.79
2019-02-04 03:00 | 36.36 | 33.71
2019-02-04 03:30 | 36.79 | 34.17
2019-02-04 04:00 | 36.64 | 34.02
2019-02-04 04:30 | 37.61 | 35.04
2019-02-04 05:00 | 38.85 | 36.36
2019-02-04 05:30 | 41.47 | 39.13
2019-02-04 06:00 | 44.57 | 42.38
2019-02-04 06:30 | 49.24 | 47.34
2019-02-04 07:00 | 53.31 | 52.69
2019-02-04 07:30 | 61.34 | 60.66
2019-02-04 08:00 | 65.8 | 65.01
2019-02-04 08:30 | 67.69 | 66.6
2019-02-04 09:00 | 67.84 | 66.44
2019-02-04 09:30 | 69.78 | 68.24
2019-02-04 10:00 | 69.92 | 68.5
2019-02-04 10:30 | 67.57 | 65.96
2019-02-04 11:00 | 68.91 | 67.06
2019-02-04 11:30 | 71.47 | 69.69
2019-02-04 12:00 | 70.75 | 69.1
2019-02-04 12:30 | 68.81 | 67.39
2019-02-04 13:00 | 65.87 | 64.41
2019-02-04 13:30 | 68.94 | 67.39
2019-02-04 14:00 | 70.25 | 68.67
2019-02-04 14:30 | 68.62 | 67.06
2019-02-04 15:00 | 68.09 | 66.76
2019-02-04 15:30 | 63.83 | 62.55
2019-02-04 16:00 | 65.91 | 64.82
2019-02-04 16:30 | 66.45 | 65.67
2019-02-04 17:00 | 64.75 | 64.22
2019-02-04 17:30 | 62.4 | 62.06
2019-02-04 18:00 | 61.31 | 60.95
2019-02-04 18:30 | 59.4 | 59.01
2019-02-04 19:00 | 58.89 | 58.49
2019-02-04 19:30 | 59.1 | 58.71
2019-02-04 20:00 | 57.3 | 56.88
2019-02-04 20:30 | 55.32 | 54.88
2019-02-04 21:00 | 53.55 | 53.09
2019-02-04 21:30 | 51.18 | 50.73
2019-02-04 22:00 | 49.26 | 48.8
2019-02-04 22:30 | 46.36 | 45.88
2019-02-04 23:00 | 46.52 | 46.05
2019-02-04 23:30 | 42.83 | 42.32
2019-02-05 | 40.61 | 40.04
2019-02-05 00:30 | 39.6 | 39
2019-02-05 01:00 | 38.17 | 37.54
2019-02-05 01:30 | 37.62 | 36.98
2019-02-05 02:00 | 37.13 | 36.48
2019-02-05 02:30 | 36.83 | 36.18
2019-02-05 03:00 | 36.25 | 35.6
2019-02-05 03:30 | 36.13 | 35.48
2019-02-05 04:00 | 36.09 | 35.43
2019-02-05 04:30 | 36.94 | 36.3
2019-02-05 05:00 | 38 | 37.37
2019-02-05 05:30 | 40.74 | 40.14
2019-02-05 06:00 | 43.46 | 42.88
2019-02-05 06:30 | 49.21 | 48.67
2019-02-05 07:00 | 54.91 | 54.29
2019-02-05 07:30 | 63.35 | 62.53
2019-02-05 08:00 | 67.13 | 66.29
2019-02-05 08:30 | 69.08 | 67.95
2019-02-05 09:00 | 69.73 | 68.47
2019-02-05 09:30 | 70.2 | 68.88
2019-02-05 10:00 | 70.17 | 68.78
2019-02-05 10:30 | 69.71 | 68.3
2019-02-05 11:00 | 69.31 | 67.89
2019-02-05 11:30 | 67.91 | 66.5
2019-02-05 12:00 | 66.91 | 65.39
2019-02-05 12:30 | 66.08 | 64.56
2019-02-05 13:00 | 64.78 | 63.33
2019-02-05 13:30 | 67.17 | 65.81
2019-02-05 14:00 | 67.48 | 66.24
2019-02-05 14:30 | 66.5 | 65.31
2019-02-05 15:00 | 65.32 | 64.16
2019-02-05 15:30 | 64.33 | 63.39
2019-02-05 16:00 | 63.57 | 62.79
2019-02-05 16:30 | 62.86 | 62.28
2019-02-05 17:00 | 62.12 | 61.7
2019-02-05 17:30 | 59.8 | 59.44
2019-02-05 18:00 | 59.51 | 59.13
2019-02-05 18:30 | 58.65 | 58.24
2019-02-05 19:00 | 59.2 | 58.8
2019-02-05 19:30 | 58.92 | 58.52
2019-02-05 20:00 | 56.86 | 56.43
2019-02-05 20:30 | 54.46 | 54.04
2019-02-05 21:00 | 52.12 | 51.68
2019-02-05 21:30 | 50.08 | 49.62
2019-02-05 22:00 | 48.39 | 47.92
2019-02-05 22:30 | 46.38 | 45.89
2019-02-05 23:00 | 43.03 | 42.49
2019-02-05 23:30 | 43.2 | 42.63
2019-02-06 | 40.79 | 40.19
2019-02-06 00:30 | 39.03 | 38.42
2019-02-06 01:00 | 38.44 | 37.8
2019-02-06 01:30 | 38.05 | 37.41
2019-02-06 02:00 | 38.03 | 37.39
2019-02-06 02:30 | 37.59 | 36.95
2019-02-06 03:00 | 37.17 | 36.49
2019-02-06 03:30 | 37.19 | 36.47
2019-02-06 04:00 | 36.77 | 36.05
2019-02-06 04:30 | 37.93 | 37.23
2019-02-06 05:00 | 39.38 | 38.69
2019-02-06 05:30 | 42.09 | 41.44
2019-02-06 06:00 | 45.43 | 44.8
2019-02-06 06:30 | 51.43 | 50.47
2019-02-06 07:00 | 56.75 | 56
2019-02-06 07:30 | 63.4 | 62.5
2019-02-06 08:00 | 66.27 | 65.48
2019-02-06 08:30 | 68.11 | 67.16
2019-02-06 09:00 | 69.69 | 68.43
2019-02-06 09:30 | 70.07 | 68.67
2019-02-06 10:00 | 71.32 | 69.58
2019-02-06 10:30 | 72.15 | 70.38
2019-02-06 11:00 | 72.56 | 70.68
2019-02-06 11:30 | 72.89 | 71.07
2019-02-06 12:00 | 72.1 | 70.42
2019-02-06 12:30 | 73.08 | 71.58
2019-02-06 13:00 | 70.71 | 69.22
2019-02-06 13:30 | 70.87 | 69.38
2019-02-06 14:00 | 70.03 | 68.58
2019-02-06 14:30 | 69.96 | 68.46
2019-02-06 15:00 | 70.2 | 68.84
2019-02-06 15:30 | 68.67 | 67.5
2019-02-06 16:00 | 68.22 | 67.28
2019-02-06 16:30 | 66.8 | 66.13
2019-02-06 17:00 | 65.58 | 65.11
2019-02-06 17:30 | 63.08 | 62.75
2019-02-06 18:00 | 62.51 | 62.15
2019-02-06 18:30 | 60.61 | 60.22
2019-02-06 19:00 | 59.85 | 59.45
2019-02-06 19:30 | 58.15 | 57.73
2019-02-06 20:00 | 56.59 | 56.15
2019-02-06 20:30 | 53.47 | 53.04
2019-02-06 21:00 | 50.67 | 50.22
2019-02-06 21:30 | 48.65 | 48.18
2019-02-06 22:00 | 46.87 | 46.39
2019-02-06 22:30 | 43.83 | 43.31
2019-02-06 23:00 | 44.58 | 44.03
2019-02-06 23:30 | 41.18 | 40.59
2019-02-07 | 39.72 | 39.11
2019-02-07 00:30 | 39.21 | 38.6
2019-02-07 01:00 | 38.39 | 37.76
2019-02-07 01:30 | 37.75 | 37.12
2019-02-07 02:00 | 37.27 | 36.62
2019-02-07 02:30 | 36.41 | 35.7
2019-02-07 03:00 | 35.47 | 34.74
2019-02-07 03:30 | 35.36 | 34.62
2019-02-07 04:00 | 35.73 | 35
2019-02-07 04:30 | 36.36 | 35.64
2019-02-07 05:00 | 37.78 | 37.08
2019-02-07 05:30 | 41 | 40.33
2019-02-07 06:00 | 44.58 | 43.95
2019-02-07 06:30 | 49.76 | 48.99
2019-02-07 07:00 | 55.23 | 54.46
2019-02-07 07:30 | 62.54 | 61.64
2019-02-07 08:00 | 66.03 | 65.29
2019-02-07 08:30 | 68.55 | 67.56
2019-02-07 09:00 | 69.88 | 68.64
2019-02-07 09:30 | 70.42 | 69.14
2019-02-07 10:00 | 70.24 | 68.96
2019-02-07 10:30 | 70.75 | 69.4
2019-02-07 11:00 | 70.78 | 69.38
2019-02-07 11:30 | 70.85 | 69.34
2019-02-07 12:00 | 69.28 | 67.89
2019-02-07 12:30 | 70.1 | 68.8
2019-02-07 13:00 | 68.51 | 67.19
2019-02-07 13:30 | 68.61 | 67.26
2019-02-07 14:00 | 67.23 | 65.91
2019-02-07 14:30 | 65.98 | 64.66
2019-02-07 15:00 | 66.72 | 65.52
2019-02-07 15:30 | 64.81 | 63.81
2019-02-07 16:00 | 64.8 | 63.99
2019-02-07 16:30 | 63.75 | 63.13
2019-02-07 17:00 | 62.46 | 62.03
2019-02-07 17:30 | 60.27 | 59.91
2019-02-07 18:00 | 60.48 | 60.1
2019-02-07 18:30 | 59.81 | 59.42
2019-02-07 19:00 | 59.18 | 58.78
2019-02-07 19:30 | 58.48 | 58.07
2019-02-07 20:00 | 56.62 | 56.2
2019-02-07 20:30 | 54.35 | 53.93
2019-02-07 21:00 | 52.33 | 51.89
2019-02-07 21:30 | 50 | 49.55
2019-02-07 22:00 | 47.93 | 47.46
2019-02-07 22:30 | 44.91 | 44.42
2019-02-07 23:00 | 45.36 | 44.84
2019-02-07 23:30 | 42.25 | 41.67
2019-02-08 | 40.09 | 39.48
2019-02-08 00:30 | 38.55 | 37.95
2019-02-08 01:00 | 38.25 | 37.63
2019-02-08 01:30 | 38.05 | 37.43
2019-02-08 02:00 | 37.56 | 36.93
2019-02-08 02:30 | 36.68 | 35.98
2019-02-08 03:00 | 36.65 | 35.94
2019-02-08 03:30 | 36.01 | 35.29
2019-02-08 04:00 | 35.77 | 35.05
2019-02-08 04:30 | 36.33 | 35.63
2019-02-08 05:00 | 37.52 | 36.83
2019-02-08 05:30 | 39.7 | 39.04
2019-02-08 06:00 | 43.12 | 42.49
2019-02-08 06:30 | 49.24 | 48.48
2019-02-08 07:00 | 54.92 | 54.29
2019-02-08 07:30 | 60.72 | 60.03
2019-02-08 08:00 | 63.94 | 63.2
2019-02-08 08:30 | 66.46 | 65.36
2019-02-08 09:00 | 67.18 | 65.85
2019-02-08 09:30 | 64.26 | 62.76
2019-02-08 10:00 | 66.81 | 65.28
2019-02-08 10:30 | 67.82 | 65.97
2019-02-08 11:00 | 68.11 | 66.08
2019-02-08 11:30 | 67.84 | 65.7
2019-02-08 12:00 | 66.95 | 64.77
2019-02-08 12:30 | 66.87 | 64.74
2019-02-08 13:00 | 67.38 | 65.17
2019-02-08 13:30 | 69.33 | 67.26
2019-02-08 14:00 | 68.85 | 66.93
2019-02-08 14:30 | 69.19 | 67.36
2019-02-08 15:00 | 68.34 | 66.85
2019-02-08 15:30 | 66.81 | 65.68
2019-02-08 16:00 | 66.15 | 65.2
2019-02-08 16:30 | 62.43 | 61.68
2019-02-08 17:00 | 62.47 | 61.82
2019-02-08 17:30 | 61.81 | 61.52
2019-02-08 18:00 | 59.19 | 59.11
2019-02-08 18:30 | 57.28 | 57.27
2019-02-08 19:00 | 57.4 | 57.39
2019-02-08 19:30 | 56.55 | 56.54
2019-02-08 20:00 | 54.85 | 54.85
2019-02-08 20:30 | 52.41 | 52.41
2019-02-08 21:00 | 51.21 | 51.21
2019-02-08 21:30 | 48.93 | 48.89
2019-02-08 22:00 | 47.23 | 47.19
2019-02-08 22:30 | 45.73 | 45.71
2019-02-08 23:00 | 47.03 | 47.01
2019-02-08 23:30 | 43.15 | 43.15
2019-02-09 | 40.89 | 40.86
2019-02-09 00:30 | 39.86 | 39.69
2019-02-09 01:00 | 38.5 | 38.36
2019-02-09 01:30 | 38 | 37.84
2019-02-09 02:00 | 37.14 | 37.01
2019-02-09 02:30 | 36.34 | 36.22
2019-02-09 03:00 | 35.78 | 35.69
2019-02-09 03:30 | 35.75 | 35.67
2019-02-09 04:00 | 35.31 | 35.26
2019-02-09 04:30 | 35.76 | 35.68
2019-02-09 05:00 | 36.19 | 36.07
2019-02-09 05:30 | 37.23 | 37.13
2019-02-09 06:00 | 37.99 | 37.87
2019-02-09 06:30 | 40.13 | 39.91
2019-02-09 07:00 | 42.79 | 42.4
2019-02-09 07:30 | 45.81 | 45.2
2019-02-09 08:00 | 47.75 | 46.83
2019-02-09 08:30 | 50.37 | 49.85
2019-02-09 09:00 | 52.06 | 51.39
2019-02-09 09:30 | 54.51 | 53.72
2019-02-09 10:00 | 55.04 | 54.22
2019-02-09 10:30 | 55.77 | 54.88
2019-02-09 11:00 | 53.6 | 52.64
2019-02-09 11:30 | 51.95 | 50.95
2019-02-09 12:00 | 50.95 | 49.97
2019-02-09 12:30 | 50.6 | 49.77
2019-02-09 13:00 | 49.69 | 48.87
2019-02-09 13:30 | 49.43 | 48.66
2019-02-09 14:00 | 48.99 | 48.27
2019-02-09 14:30 | 49.28 | 48.62
2019-02-09 15:00 | 49.84 | 49.23
2019-02-09 15:30 | 50.72 | 50.2
2019-02-09 16:00 | 51.68 | 51.23
2019-02-09 16:30 | 52.77 | 52.43
2019-02-09 17:00 | 54.05 | 53.76
2019-02-09 17:30 | 55.14 | 55.02
2019-02-09 18:00 | 55.97 | 55.78
2019-02-09 18:30 | 56.18 | 56.05
2019-02-09 19:00 | 56.53 | 56.4
2019-02-09 19:30 | 57.01 | 56.85
2019-02-09 20:00 | 55.81 | 55.66
2019-02-09 20:30 | 53.58 | 53.47
2019-02-09 21:00 | 51.55 | 51.48
2019-02-09 21:30 | 49.88 | 49.83
2019-02-09 22:00 | 48.16 | 48.12
2019-02-09 22:30 | 45.74 | 45.73
2019-02-09 23:00 | 46.16 | 46.15
2019-02-09 23:30 | 41.74 | 41.73
2019-02-10 | 39.63 | 39.59
2019-02-10 00:30 | 38.24 | 38.15
2019-02-10 01:00 | 37.14 | 37.06
2019-02-10 01:30 | 36.14 | 36.08
2019-02-10 02:00 | 35.48 | 35.42
2019-02-10 02:30 | 34.78 | 34.72
2019-02-10 03:00 | 34.2 | 34.16
2019-02-10 03:30 | 34.15 | 34.11
2019-02-10 04:00 | 33.83 | 33.79
2019-02-10 04:30 | 33.88 | 33.84
2019-02-10 05:00 | 34.1 | 34.06
2019-02-10 05:30 | 34.43 | 34.4
2019-02-10 06:00 | 34.24 | 34.21
2019-02-10 06:30 | 34.93 | 34.89
2019-02-10 07:00 | 35.86 | 35.8
2019-02-10 07:30 | 38.54 | 38.39
2019-02-10 08:00 | 40.34 | 40.01
2019-02-10 08:30 | 42.86 | 42.34
2019-02-10 09:00 | 43.22 | 42.58
2019-02-10 09:30 | 44.8 | 44.28
2019-02-10 10:00 | 46.55 | 46.25
2019-02-10 10:30 | 46.88 | 46.52
2019-02-10 11:00 | 47.34 | 46.91
2019-02-10 11:30 | 48.36 | 47.9
2019-02-10 12:00 | 48.55 | 48.11
2019-02-10 12:30 | 49.66 | 49.22
2019-02-10 13:00 | 49.22 | 48.77
2019-02-10 13:30 | 49.54 | 49.08
2019-02-10 14:00 | 50.5 | 50.06
2019-02-10 14:30 | 51.22 | 50.78
2019-02-10 15:00 | 51.91 | 51.48
2019-02-10 15:30 | 52.85 | 52.49
2019-02-10 16:00 | 53.76 | 53.46
2019-02-10 16:30 | 55.51 | 55.26
2019-02-10 17:00 | 56.92 | 56.69
2019-02-10 17:30 | 58.82 | 58.61
2019-02-10 18:00 | 64.38 | 64.17
2019-02-10 18:30 | 72.78 | 72.53
2019-02-10 19:00 | 73.78 | 73.49
2019-02-10 19:30 | 73.46 | 73.15
2019-02-10 20:00 | 70.99 | 70.72
2019-02-10 20:30 | 68.04 | 67.84
2019-02-10 21:00 | 64.79 | 64.62
2019-02-10 21:30 | 61.74 | 61.63
2019-02-10 22:00 | 58.12 | 58.06
2019-02-10 22:30 | 54.32 | 54.29
2019-02-10 23:00 | 54.26 | 54.24
2019-02-10 23:30 | 49.02 | 49.02
2019-02-11 | 46.36 | 46.3
2019-02-11 00:30 | 44.93 | 44.81
2019-02-11 01:00 | 43.52 | 43.42
2019-02-11 01:30 | 42.7 | 42.61
2019-02-11 02:00 | 42.09 | 42
2019-02-11 02:30 | 41.35 | 41.26
2019-02-11 03:00 | 40.67 | 40.61
2019-02-11 03:30 | 40.61 | 40.54
2019-02-11 04:00 | 40.64 | 40.56
2019-02-11 04:30 | 41.35 | 41.27
2019-02-11 05:00 | 43.05 | 42.92
2019-02-11 05:30 | 46.18 | 45.96
2019-02-11 06:00 | 49.94 | 49.54
2019-02-11 06:30 | 57.27 | 56.41
2019-02-11 07:00 | 63.49 | 62.63
2019-02-11 07:30 | 69.63 | 68.91
2019-02-11 08:00 | 72.33 | 71.25
2019-02-11 08:30 | 74.99 | 73.23
2019-02-11 09:00 | 75.68 | 73.68
2019-02-11 09:30 | 78.69 | 76.59
2019-02-11 10:00 | 78.39 | 76.19
2019-02-11 10:30 | 77.09 | 74.75
2019-02-11 11:00 | 77.97 | 75.43
2019-02-11 11:30 | 79.64 | 75.29
2019-02-11 12:00 | 80.78 | 76.49
2019-02-11 12:30 | 81.53 | 77.29
2019-02-11 13:00 | 80.9 | 76.62
2019-02-11 13:30 | 82.57 | 78.36
2019-02-11 14:00 | 83.95 | 80.28
2019-02-11 14:30 | 81.77 | 80.62
2019-02-11 15:00 | 80.07 | 78.76
2019-02-11 15:30 | 80.72 | 79.17
2019-02-11 16:00 | 83.75 | 82.14
2019-02-11 16:30 | 85.77 | 83.92
2019-02-11 17:00 | 86.98 | 84.67
2019-02-11 17:30 | 86.82 | 83.76
2019-02-11 18:00 | 86.71 | 83.03
2019-02-11 18:30 | 86.08 | 82.19
2019-02-11 19:00 | 85.8 | 82.83
2019-02-11 19:30 | 85.21 | 82.23
2019-02-11 20:00 | 83.19 | 79.75
2019-02-11 20:30 | 79.72 | 75.61
2019-02-11 21:00 | 75.88 | 70.3
2019-02-11 21:30 | 73.34 | 67.13
2019-02-11 22:00 | 69.8 | 63.14
2019-02-11 22:30 | 66.78 | 59.17
2019-02-11 23:00 | 66.96 | 59
2019-02-11 23:30 | 63.5 | 54.5
2019-02-12 | 60.82 | 51.32
2019-02-12 00:30 | 58.83 | 48.65
2019-02-12 01:00 | 50.69 | 46.86
2019-02-12 01:30 | 47.27 | 45.85
2019-02-12 02:00 | 46.44 | 44.9
2019-02-12 02:30 | 45.49 | 43.83
2019-02-12 03:00 | 44.85 | 42.95
2019-02-12 03:30 | 44.42 | 42.37
2019-02-12 04:00 | 44.08 | 42
2019-02-12 04:30 | 44.66 | 42.7
2019-02-12 05:00 | 45.94 | 44.25
2019-02-12 05:30 | 48.07 | 46.69
2019-02-12 06:00 | 50.21 | 49.18
2019-02-12 06:30 | 55.82 | 55.34
2019-02-12 07:00 | 62.43 | 62.06
2019-02-12 07:30 | 69.01 | 68.13
2019-02-12 08:00 | 73.05 | 70.3
2019-02-12 08:30 | 74.62 | 71.99
2019-02-12 09:00 | 75.9 | 73.3
2019-02-12 09:30 | 64.59 | 61.58
2019-02-12 10:00 | 76.76 | 74.25
2019-02-12 10:30 | 77.25 | 74.8
2019-02-12 11:00 | 77.66 | 75.25
2019-02-12 11:30 | 80.28 | 76.23
2019-02-12 12:00 | 84.53 | 77.7
2019-02-12 12:30 | 86.43 | 79.81
2019-02-12 13:00 | 86.59 | 79.99
2019-02-12 13:30 | 87.58 | 81.05
2019-02-12 14:00 | 88.6 | 82.18
2019-02-12 14:30 | 89.74 | 83.42
2019-02-12 15:00 | 90.52 | 84.24
2019-02-12 15:30 | 91.76 | 85.55
2019-02-12 16:00 | 94.26 | 88.2
2019-02-12 16:30 | 95.74 | 89.93
2019-02-12 17:00 | 90.96 | 90.53
2019-02-12 17:30 | 89.65 | 89.39
2019-02-12 18:00 | 89.43 | 89.14
2019-02-12 18:30 | 88.7 | 88.4
2019-02-12 19:00 | 88.84 | 88.53
2019-02-12 19:30 | 89.24 | 88.94
2019-02-12 20:00 | 86.35 | 86
2019-02-12 20:30 | 82.61 | 82.11
2019-02-12 21:00 | 78.32 | 77.59
2019-02-12 21:30 | 73.01 | 72.51
2019-02-12 22:00 | 68.4 | 68.31
2019-02-12 22:30 | 63.26 | 63.23
2019-02-12 23:00 | 61.83 | 61.81
2019-02-12 23:30 | 55.99 | 55.98
2019-02-13 | 52.69 | 52.68
2019-02-13 00:30 | 50.93 | 50.69
2019-02-13 01:00 | 48.73 | 48.34
2019-02-13 01:30 | 47.26 | 46.94
2019-02-13 02:00 | 46.18 | 45.9
2019-02-13 02:30 | 45.32 | 45.05
2019-02-13 03:00 | 44.12 | 43.92
2019-02-13 03:30 | 43.51 | 43.32
2019-02-13 04:00 | 43.4 | 43.22
2019-02-13 04:30 | 44.19 | 43.98
2019-02-13 05:00 | 45.59 | 45.34
2019-02-13 05:30 | 48.05 | 47.72
2019-02-13 06:00 | 50.62 | 50.17
2019-02-13 06:30 | 57.68 | 56.76
2019-02-13 07:00 | 63.22 | 62.47
2019-02-13 07:30 | 68.57 | 67.89
2019-02-13 08:00 | 71.09 | 69.95
2019-02-13 08:30 | 73.22 | 70.85
2019-02-13 09:00 | 74.47 | 71.83
2019-02-13 09:30 | 73.49 | 72.54
2019-02-13 10:00 | 73.83 | 73.47
2019-02-13 10:30 | 74.5 | 74.15
2019-02-13 11:00 | 74.74 | 74.4
2019-02-13 11:30 | 73.73 | 73.39
2019-02-13 12:00 | 74.45 | 74.11
2019-02-13 12:30 | 76.13 | 75.8
2019-02-13 13:00 | 76.4 | 76.07
2019-02-13 13:30 | 77.22 | 76.89
2019-02-13 14:00 | 79.1 | 78.79
2019-02-13 14:30 | 81.45 | 81.15
2019-02-13 15:00 | 82.7 | 82.4
2019-02-13 15:30 | 83.67 | 83.37
2019-02-13 16:00 | 86.73 | 86.43
2019-02-13 16:30 | 88.11 | 87.8
2019-02-13 17:00 | 89.73 | 89.4
2019-02-13 17:30 | 88.94 | 88.58
2019-02-13 18:00 | 89.37 | 88.91
2019-02-13 18:30 | 88.16 | 87.43
2019-02-13 19:00 | 87.99 | 87.24
2019-02-13 19:30 | 88 | 87.3
2019-02-13 20:00 | 85.31 | 84.39
2019-02-13 20:30 | 80.6 | 79.33
2019-02-13 21:00 | 70.53 | 70.02
2019-02-13 21:30 | 71.84 | 71.54
2019-02-13 22:00 | 66.39 | 66.07
2019-02-13 22:30 | 61.8 | 61.47
2019-02-13 23:00 | 57.86 | 57.5
2019-02-13 23:30 | 53.84 | 53.43
2019-02-14 | 50.79 | 50.36
2019-02-14 00:30 | 49.27 | 48.83
2019-02-14 01:00 | 47.1 | 46.63
2019-02-14 01:30 | 46.12 | 45.6
2019-02-14 02:00 | 44.85 | 44.32
2019-02-14 02:30 | 44.12 | 43.59
2019-02-14 03:00 | 42.04 | 41.5
2019-02-14 03:30 | 40.75 | 40.18
2019-02-14 04:00 | 41.44 | 40.83
2019-02-14 04:30 | 43.02 | 42.43
2019-02-14 05:00 | 43.92 | 43.34
2019-02-14 05:30 | 46.79 | 46.24
2019-02-14 06:00 | 49.61 | 49.08
2019-02-14 06:30 | 56.35 | 55.53
2019-02-14 07:00 | 62.01 | 61.35
2019-02-14 07:30 | 68.03 | 67.39
2019-02-14 08:00 | 71.22 | 70.65
2019-02-14 08:30 | 73.43 | 72.11
2019-02-14 09:00 | 76.56 | 74.05
2019-02-14 09:30 | 77.45 | 75.01
2019-02-14 10:00 | 77.84 | 75.44
2019-02-14 10:30 | 78.48 | 76.14
2019-02-14 11:00 | 78.81 | 76.45
2019-02-14 11:30 | 78.9 | 76.55
2019-02-14 12:00 | 79.71 | 77.4
2019-02-14 12:30 | 81.56 | 79.31
2019-02-14 13:00 | 81.18 | 78.92
2019-02-14 13:30 | 81.91 | 79.69
2019-02-14 14:00 | 83.05 | 80.87
2019-02-14 14:30 | 84.38 | 82.24
2019-02-14 15:00 | 85.27 | 83.15
2019-02-14 15:30 | 85.76 | 83.62
2019-02-14 16:00 | 88.54 | 86.45
2019-02-14 16:30 | 90.27 | 88.19
2019-02-14 17:00 | 90.99 | 88.88
2019-02-14 17:30 | 89.91 | 87.7
2019-02-14 18:00 | 89.79 | 87.58
2019-02-14 18:30 | 89.24 | 86.89
2019-02-14 19:00 | 89.32 | 86.96
2019-02-14 19:30 | 89.45 | 87.1
2019-02-14 20:00 | 86.81 | 84.34
2019-02-14 20:30 | 83.38 | 80.79
2019-02-14 21:00 | 80.89 | 78.18
2019-02-14 21:30 | 76.47 | 73.52
2019-02-14 22:00 | 68.84 | 68.3
2019-02-14 22:30 | 63.84 | 63.46
2019-02-14 23:00 | 62.25 | 61.87
2019-02-14 23:30 | 57.56 | 57.16
2019-02-15 | 54.77 | 54.35
2019-02-15 00:30 | 52.72 | 52.29
2019-02-15 01:00 | 50.26 | 49.81
2019-02-15 01:30 | 49.26 | 48.8
2019-02-15 02:00 | 48.14 | 47.68
2019-02-15 02:30 | 47.27 | 46.8
2019-02-15 03:00 | 46.24 | 45.76
2019-02-15 03:30 | 45.56 | 45.03
2019-02-15 04:00 | 45.46 | 44.93
2019-02-15 04:30 | 45.98 | 45.45
2019-02-15 05:00 | 46.6 | 46.07
2019-02-15 05:30 | 49.28 | 48.76
2019-02-15 06:00 | 52.08 | 51.59
2019-02-15 06:30 | 58.07 | 57.59
2019-02-15 07:00 | 63.74 | 63.07
2019-02-15 07:30 | 70.49 | 69.77
2019-02-15 08:00 | 73.73 | 72.5
2019-02-15 08:30 | 76.02 | 74.97
2019-02-15 09:00 | 76.35 | 75.15
2019-02-15 09:30 | 75.34 | 73.91
2019-02-15 10:00 | 77.18 | 74.74
2019-02-15 10:30 | 77.2 | 74.78
2019-02-15 11:00 | 77.64 | 75.26
2019-02-15 11:30 | 77.45 | 75.08
2019-02-15 12:00 | 78.1 | 75.75
2019-02-15 12:30 | 78.85 | 76.51
2019-02-15 13:00 | 77.95 | 75.57
2019-02-15 13:30 | 78.02 | 75.63
2019-02-15 14:00 | 79.54 | 77.16
2019-02-15 14:30 | 80.3 | 77.92
2019-02-15 15:00 | 80.5 | 78.12
2019-02-15 15:30 | 80.58 | 78.14
2019-02-15 16:00 | 81.74 | 79.3
2019-02-15 16:30 | 82.81 | 80.34
2019-02-15 17:00 | 83.32 | 80.83
2019-02-15 17:30 | 82.98 | 80.43
2019-02-15 18:00 | 79.93 | 79.48
2019-02-15 18:30 | 78.22 | 77.92
2019-02-15 19:00 | 79.01 | 78.72
2019-02-15 19:30 | 78.65 | 78.35
2019-02-15 20:00 | 76.47 | 76.16
2019-02-15 20:30 | 73.44 | 73.11
2019-02-15 21:00 | 70.22 | 69.88
2019-02-15 21:30 | 67.6 | 67.24
2019-02-15 22:00 | 64.58 | 64.21
2019-02-15 22:30 | 61.13 | 60.75
2019-02-15 23:00 | 59.94 | 59.56
2019-02-15 23:30 | 55.49 | 55.09
2019-02-16 | 52.64 | 52.23
2019-02-16 00:30 | 50.54 | 50.08
2019-02-16 01:00 | 48.98 | 48.5
2019-02-16 01:30 | 48.31 | 47.83
2019-02-16 02:00 | 47.23 | 46.74
2019-02-16 02:30 | 46.41 | 45.91
2019-02-16 03:00 | 45.33 | 44.81
2019-02-16 03:30 | 44.81 | 44.24
2019-02-16 04:00 | 44.6 | 44.03
2019-02-16 04:30 | 44.71 | 44.12
2019-02-16 05:00 | 44.78 | 44.2
2019-02-16 05:30 | 45.41 | 44.84
2019-02-16 06:00 | 45.94 | 45.37
2019-02-16 06:30 | 48.13 | 47.58
2019-02-16 07:00 | 49.64 | 49.12
2019-02-16 07:30 | 52.3 | 51.76
2019-02-16 08:00 | 55.89 | 55.22
2019-02-16 08:30 | 58.73 | 58.3
2019-02-16 09:00 | 59.48 | 58.87
2019-02-16 09:30 | 59.75 | 59.03
2019-02-16 10:00 | 59.81 | 58.94
2019-02-16 10:30 | 60.28 | 59.35
2019-02-16 11:00 | 57.31 | 56.33
2019-02-16 11:30 | 56.48 | 55.46
2019-02-16 12:00 | 56.4 | 55.37
2019-02-16 12:30 | 57.43 | 56.55
2019-02-16 13:00 | 56.46 | 55.6
2019-02-16 13:30 | 56.91 | 56.04
2019-02-16 14:00 | 56.84 | 56.1
2019-02-16 14:30 | 57.43 | 56.76
2019-02-16 15:00 | 58.39 | 57.79
2019-02-16 15:30 | 59.49 | 58.96
2019-02-16 16:00 | 60.72 | 60.27
2019-02-16 16:30 | 62.62 | 62.24
2019-02-16 17:00 | 64.22 | 63.87
2019-02-16 17:30 | 64.64 | 64.31
2019-02-16 18:00 | 66.07 | 65.76
2019-02-16 18:30 | 66.3 | 65.98
2019-02-16 19:00 | 67.07 | 66.76
2019-02-16 19:30 | 67.93 | 67.63
2019-02-16 20:00 | 66.31 | 66
2019-02-16 20:30 | 63.72 | 63.39
2019-02-16 21:00 | 62.36 | 62.02
2019-02-16 21:30 | 60.56 | 60.21
2019-02-16 22:00 | 58.76 | 58.39
2019-02-16 22:30 | 56.06 | 55.66
2019-02-16 23:00 | 55.92 | 55.5
2019-02-16 23:30 | 51.65 | 51.18
2019-02-17 | 49.65 | 49.16
2019-02-17 00:30 | 47.92 | 47.42
2019-02-17 01:00 | 46.61 | 46.11
2019-02-17 01:30 | 45.45 | 44.94
2019-02-17 02:00 | 44.24 | 43.68
2019-02-17 02:30 | 43.44 | 42.85
2019-02-17 03:00 | 42.84 | 42.24
2019-02-17 03:30 | 42.52 | 41.93
2019-02-17 04:00 | 42.1 | 41.5
2019-02-17 04:30 | 41.81 | 41.2
2019-02-17 05:00 | 41.74 | 41.13
2019-02-17 05:30 | 42.02 | 41.42
2019-02-17 06:00 | 41.98 | 41.38
2019-02-17 06:30 | 43.61 | 43.04
2019-02-17 07:00 | 44.54 | 43.97
2019-02-17 07:30 | 45.48 | 44.91
2019-02-17 08:00 | 46.55 | 45.98
2019-02-17 08:30 | 47.1 | 46.51
2019-02-17 09:00 | 47.59 | 46.97
2019-02-17 09:30 | 48.01 | 47.48
2019-02-17 10:00 | 47.79 | 47.24
2019-02-17 10:30 | 48.45 | 47.91
2019-02-17 11:00 | 48.53 | 47.98
2019-02-17 11:30 | 48.71 | 48.16
2019-02-17 12:00 | 49.11 | 48.56
2019-02-17 12:30 | 51.29 | 50.77
2019-02-17 13:00 | 51.08 | 50.55
2019-02-17 13:30 | 51.32 | 50.8
2019-02-17 14:00 | 51.72 | 51.21
2019-02-17 14:30 | 52.65 | 52.15
2019-02-17 15:00 | 53.8 | 53.32
2019-02-17 15:30 | 54.96 | 54.49
2019-02-17 16:00 | 56.88 | 56.43
2019-02-17 16:30 | 59.28 | 58.86
2019-02-17 17:00 | 61.62 | 61.22
2019-02-17 17:30 | 64.24 | 63.92
2019-02-17 18:00 | 67.1 | 66.79
2019-02-17 18:30 | 68.32 | 68.02
2019-02-17 19:00 | 69.24 | 68.94
2019-02-17 19:30 | 70.3 | 70.01
2019-02-17 20:00 | 68.53 | 68.23
2019-02-17 20:30 | 65.35 | 65.03
2019-02-17 21:00 | 62.4 | 62.05
2019-02-17 21:30 | 59.55 | 59.17
2019-02-17 22:00 | 56.1 | 55.68
2019-02-17 22:30 | 52.92 | 52.46
2019-02-17 23:00 | 52.27 | 51.8
2019-02-17 23:30 | 48.05 | 47.55
2019-02-18 | 45.69 | 45.19
2019-02-18 00:30 | 44.1 | 43.53
2019-02-18 01:00 | 42.6 | 42
2019-02-18 01:30 | 41.86 | 41.25
2019-02-18 02:00 | 41.22 | 40.61
2019-02-18 02:30 | 40.63 | 40.01
2019-02-18 03:00 | 40.21 | 39.58
2019-02-18 03:30 | 39.8 | 39.17
2019-02-18 04:00 | 39.82 | 39.19
2019-02-18 04:30 | 40.58 | 39.95
2019-02-18 05:00 | 41.71 | 41.1
2019-02-18 05:30 | 44.21 | 43.62
2019-02-18 06:00 | 46.73 | 46.15
2019-02-18 06:30 | 53.15 | 52.49
2019-02-18 07:00 | 58.22 | 57.71
2019-02-18 07:30 | 64.63 | 63.91
2019-02-18 08:00 | 67.28 | 66.32
2019-02-18 08:30 | 68.93 | 67.42
2019-02-18 09:00 | 69.95 | 68.17
2019-02-18 09:30 | 71.07 | 69.19
2019-02-18 10:00 | 70.05 | 69
2019-02-18 10:30 | 70.07 | 69.67
2019-02-18 11:00 | 70.22 | 69.83
2019-02-18 11:30 | 70.82 | 70.44
2019-02-18 12:00 | 70.32 | 69.94
2019-02-18 12:30 | 71.63 | 71.26
2019-02-18 13:00 | 70.58 | 70.2
2019-02-18 13:30 | 70.76 | 70.38
2019-02-18 14:00 | 71.43 | 71.06
2019-02-18 14:30 | 72.04 | 71.66
2019-02-18 15:00 | 72.58 | 72.21
2019-02-18 15:30 | 73.58 | 73.2
2019-02-18 16:00 | 75.52 | 75.14
2019-02-18 16:30 | 76.96 | 76.57
2019-02-18 17:00 | 77.87 | 77.46
2019-02-18 17:30 | 77.01 | 76.18
2019-02-18 18:00 | 78.01 | 76.88
2019-02-18 18:30 | 77.66 | 76.2
2019-02-18 19:00 | 77.94 | 76.4
2019-02-18 19:30 | 77.86 | 76.31
2019-02-18 20:00 | 75.19 | 73.35
2019-02-18 20:30 | 72.29 | 70.15
2019-02-18 21:00 | 69.48 | 67.01
2019-02-18 21:30 | 65.71 | 62.58
2019-02-18 22:00 | 62.77 | 59.18
2019-02-18 22:30 | 59.44 | 55.54
2019-02-18 23:00 | 58.3 | 55.13
2019-02-18 23:30 | 53.42 | 49.91
2019-02-19 | 50.69 | 46.98
2019-02-19 00:30 | 49.06 | 45.2
2019-02-19 01:00 | 47.91 | 43.89
2019-02-19 01:30 | 47.27 | 43.14
2019-02-19 02:00 | 46.25 | 42.02
2019-02-19 02:30 | 45.47 | 41.1
2019-02-19 03:00 | 44.79 | 40.3
2019-02-19 03:30 | 44.54 | 40.02
2019-02-19 04:00 | 44.5 | 39.97
2019-02-19 04:30 | 44.74 | 40.24
2019-02-19 05:00 | 45.77 | 41.37
2019-02-19 05:30 | 47.94 | 43.95
2019-02-19 06:00 | 47.57 | 47.07
2019-02-19 06:30 | 52.57 | 52.1
2019-02-19 07:00 | 57.56 | 57.08
2019-02-19 07:30 | 63.75 | 63.04
2019-02-19 08:00 | 64.85 | 64.05
2019-02-19 08:30 | 66.96 | 65.74
2019-02-19 09:00 | 68.03 | 67.4
2019-02-19 09:30 | 67.83 | 67.45
2019-02-19 10:00 | 67.61 | 67.24
2019-02-19 10:30 | 68.79 | 68.4
2019-02-19 11:00 | 69.43 | 69.04
2019-02-19 11:30 | 70.04 | 69.67
2019-02-19 12:00 | 70.87 | 70.5
2019-02-19 12:30 | 73.59 | 73.24
2019-02-19 13:00 | 73.36 | 73.01
2019-02-19 13:30 | 73.69 | 73.35
2019-02-19 14:00 | 73.26 | 72.92
2019-02-19 14:30 | 77.74 | 77.41
2019-02-19 15:00 | 79.21 | 78.89
2019-02-19 15:30 | 80.93 | 80.62
2019-02-19 16:00 | 59.64 | 59.26
2019-02-19 16:30 | 85.76 | 85.45
2019-02-19 17:00 | 86.23 | 85.9
2019-02-19 17:30 | 85.59 | 85.23
2019-02-19 18:00 | 84.88 | 84.25
2019-02-19 18:30 | 84.1 | 83.17
2019-02-19 19:00 | 83.82 | 82.81
2019-02-19 19:30 | 82.99 | 81.96
2019-02-19 20:00 | 80.69 | 79.45
2019-02-19 20:30 | 76.83 | 75.23
2019-02-19 21:00 | 73.22 | 71.26
2019-02-19 21:30 | 70.01 | 67.61
2019-02-19 22:00 | 69.93 | 66.46
2019-02-19 22:30 | 73.88 | 69.79
2019-02-19 23:00 | 65.88 | 60.82
2019-02-19 23:30 | 60.68 | 55.11
2019-02-20 | 57.76 | 51.87
2019-02-20 00:30 | 56.32 | 50.24
2019-02-20 01:00 | 54.7 | 48.32
2019-02-20 01:30 | 53.83 | 47.33
2019-02-20 02:00 | 53.34 | 46.74
2019-02-20 02:30 | 52.9 | 46.21
2019-02-20 03:00 | 52.42 | 45.55
2019-02-20 03:30 | 52.32 | 45.42
2019-02-20 04:00 | 52.41 | 45.5
2019-02-20 04:30 | 52.8 | 45.96
2019-02-20 05:00 | 53.92 | 47.23
2019-02-20 05:30 | 52.64 | 50.42
2019-02-20 06:00 | 55.1 | 53.37
2019-02-20 06:30 | 61.45 | 60.01
2019-02-20 07:00 | 66.31 | 65.72
2019-02-20 07:30 | 72.49 | 71.65
2019-02-20 08:00 | 76.47 | 75.15
2019-02-20 08:30 | 78.45 | 76.62
2019-02-20 09:00 | 80.03 | 77.79
2019-02-20 09:30 | 81.69 | 79.18
2019-02-20 10:00 | 81.39 | 79.24
2019-02-20 10:30 | 80.79 | 79.21
2019-02-20 11:00 | 81.44 | 80.23
2019-02-20 11:30 | 81.89 | 80.69
2019-02-20 12:00 | 82.71 | 81.53
2019-02-20 12:30 | 84.31 | 83.16
2019-02-20 13:00 | 84.39 | 83.23
2019-02-20 13:30 | 86.32 | 85.2
2019-02-20 14:00 | 87.19 | 86.09
2019-02-20 14:30 | 88.65 | 87.57
2019-02-20 15:00 | 89.41 | 88.34
2019-02-20 15:30 | 89.96 | 88.88
2019-02-20 16:00 | 92.21 | 91.13
2019-02-20 16:30 | 93.35 | 92.25
2019-02-20 17:00 | 94.54 | 93.43
2019-02-20 17:30 | 93.22 | 92.04
2019-02-20 18:00 | 93.09 | 91.86
2019-02-20 18:30 | 91.25 | 89.96
2019-02-20 19:00 | 91.21 | 89.91
2019-02-20 19:30 | 90.33 | 89.25
2019-02-20 20:00 | 86.99 | 86.21
2019-02-20 20:30 | 82.79 | 81.71
2019-02-20 21:00 | 79.65 | 78.36
2019-02-20 21:30 | 75.33 | 73.58
2019-02-20 22:00 | 70.83 | 68.77
2019-02-20 22:30 | 65.35 | 64.05
2019-02-20 23:00 | 63.28 | 61.94
2019-02-20 23:30 | 59.09 | 57.66
2019-02-21 | 56.51 | 55.02
2019-02-21 00:30 | 54.81 | 53.27
2019-02-21 01:00 | 53.32 | 51.73
2019-02-21 01:30 | 52.65 | 51.04
2019-02-21 02:00 | 51.63 | 49.99
2019-02-21 02:30 | 50.49 | 48.82
2019-02-21 03:00 | 49.21 | 47.42
2019-02-21 03:30 | 48.17 | 46.25
2019-02-21 04:00 | 47.63 | 45.69
2019-02-21 04:30 | 47.63 | 45.69
2019-02-21 05:00 | 48.37 | 46.45
2019-02-21 05:30 | 51.1 | 49.27
2019-02-21 06:00 | 54 | 52.26
2019-02-21 06:30 | 60.06 | 58.75
2019-02-21 07:00 | 65.34 | 64.72
2019-02-21 07:30 | 71.44 | 70.64
2019-02-21 08:00 | 75.48 | 74.23
2019-02-21 08:30 | 76.59 | 75.45
2019-02-21 09:00 | 77.19 | 75.68
2019-02-21 09:30 | 78.19 | 76.58
2019-02-21 10:00 | 77.91 | 76.17
2019-02-21 10:30 | 78.54 | 76.59
2019-02-21 11:00 | 78.99 | 76.93
2019-02-21 11:30 | 79.34 | 77.09
2019-02-21 12:00 | 79.79 | 77.49
2019-02-21 12:30 | 82.22 | 80
2019-02-21 13:00 | 82.51 | 80.28
2019-02-21 13:30 | 83.6 | 81.42
2019-02-21 14:00 | 84.88 | 82.72
2019-02-21 14:30 | 86.54 | 84.47
2019-02-21 15:00 | 85.39 | 85.38
2019-02-21 15:30 | 86.2 | 85.48
2019-02-21 16:00 | 88.64 | 87.65
2019-02-21 16:30 | 89.51 | 88.56
2019-02-21 17:00 | 90.4 | 89.48
2019-02-21 17:30 | 89.74 | 88.83
2019-02-21 18:00 | 90.33 | 89.46
2019-02-21 18:30 | 89.9 | 89.04
2019-02-21 19:00 | 90.38 | 89.53
2019-02-21 19:30 | 90.13 | 89.29
2019-02-21 20:00 | 87.23 | 86.37
2019-02-21 20:30 | 83.35 | 82.25
2019-02-21 21:00 | 81.24 | 78.46
2019-02-21 21:30 | 77.64 | 73.5
2019-02-21 22:00 | 73.46 | 69.02
2019-02-21 22:30 | 72.35 | 63.27
2019-02-21 23:00 | 71.11 | 60.45
2019-02-21 23:30 | 67.99 | 56.69
2019-02-22 | 65.86 | 53.9
2019-02-22 00:30 | 64.23 | 51.68
2019-02-22 01:00 | 63.1 | 50.17
2019-02-22 01:30 | 62.31 | 49.12
2019-02-22 02:00 | 61.61 | 48.19
2019-02-22 02:30 | 60.89 | 47.27
2019-02-22 03:00 | 60.48 | 46.6
2019-02-22 03:30 | 60.23 | 46.26
2019-02-22 04:00 | 60.24 | 46.25
2019-02-22 04:30 | 60.33 | 46.39
2019-02-22 05:00 | 60.87 | 47.11
2019-02-22 05:30 | 63.15 | 50.01
2019-02-22 06:00 | 65.37 | 52.86
2019-02-22 06:30 | 66 | 58.47
2019-02-22 07:00 | 69.03 | 63.67
2019-02-22 07:30 | 71.57 | 69.7
2019-02-22 08:00 | 74.18 | 72.83
2019-02-22 08:30 | 77.17 | 75.86
2019-02-22 09:00 | 77.56 | 76.47
2019-02-22 09:30 | 77.74 | 76.64
2019-02-22 10:00 | 77.06 | 75.85
2019-02-22 10:30 | 75.51 | 74.11
2019-02-22 11:00 | 73.42 | 71.81
2019-02-22 11:30 | 75.2 | 73.53
2019-02-22 12:00 | 78.39 | 76.75
2019-02-22 12:30 | 79.39 | 77.77
2019-02-22 13:00 | 78.23 | 76.6
2019-02-22 13:30 | 80.04 | 78.5
2019-02-22 14:00 | 79.1 | 78.14
2019-02-22 14:30 | 78.94 | 78.93
2019-02-22 15:00 | 80.03 | 80.01
2019-02-22 15:30 | 80.65 | 80.54
2019-02-22 16:00 | 82.58 | 81.57
2019-02-22 16:30 | 83.33 | 82.35
2019-02-22 17:00 | 84.39 | 83.44
2019-02-22 17:30 | 84.2 | 83.28
2019-02-22 18:00 | 82.19 | 81.24
2019-02-22 18:30 | 80.4 | 79.16
2019-02-22 19:00 | 80.31 | 79.1
2019-02-22 19:30 | 79.83 | 78.54
2019-02-22 20:00 | 78.52 | 75.99
2019-02-22 20:30 | 77.12 | 72.97
2019-02-22 21:00 | 74.23 | 69.88
2019-02-22 21:30 | 71.25 | 66.69
2019-02-22 22:00 | 71.77 | 63.15
2019-02-22 22:30 | 70.06 | 58.92
2019-02-22 23:00 | 68.56 | 57.01
2019-02-22 23:30 | 63.13 | 53.83
2019-02-23 | 57.08 | 50.42
2019-02-23 00:30 | 55.51 | 48.64
2019-02-23 01:00 | 53.96 | 46.86
2019-02-23 01:30 | 52.93 | 45.66
2019-02-23 02:00 | 51.96 | 44.54
2019-02-23 02:30 | 51.39 | 43.85
2019-02-23 03:00 | 51 | 43.25
2019-02-23 03:30 | 50.86 | 43.09
2019-02-23 04:00 | 50.78 | 42.98
2019-02-23 04:30 | 50.97 | 43.21
2019-02-23 05:00 | 51.02 | 43.27
2019-02-23 05:30 | 52.03 | 44.48
2019-02-23 06:00 | 52.84 | 45.39
2019-02-23 06:30 | 54.98 | 47.89
2019-02-23 07:00 | 56.93 | 50.13
2019-02-23 07:30 | 60.29 | 53.9
2019-02-23 08:00 | 61.88 | 55.63
2019-02-23 08:30 | 63.74 | 57.8
2019-02-23 09:00 | 66.56 | 62.57
2019-02-23 09:30 | 63.98 | 62.44
2019-02-23 10:00 | 62.78 | 61.21
2019-02-23 10:30 | 60.95 | 59.32
2019-02-23 11:00 | 60.41 | 58.76
2019-02-23 11:30 | 56.72 | 54.94
2019-02-23 12:00 | 57.05 | 55.27
2019-02-23 12:30 | 63.02 | 61.44
2019-02-23 13:00 | 64.29 | 62.77
2019-02-23 13:30 | 62.86 | 61.32
2019-02-23 14:00 | 62.91 | 61.38
2019-02-23 14:30 | 60.88 | 59.29
2019-02-23 15:00 | 58.94 | 57.29
2019-02-23 15:30 | 61.34 | 59.77
2019-02-23 16:00 | 61.75 | 60.18
2019-02-23 16:30 | 63.12 | 61.54
2019-02-23 17:00 | 61.6 | 60
2019-02-23 17:30 | 62.38 | 60.82
2019-02-23 18:00 | 63.87 | 62.35
2019-02-23 18:30 | 65 | 63.52
2019-02-23 19:00 | 65.81 | 64.33
2019-02-23 19:30 | 65.31 | 63.83
2019-02-23 20:00 | 63.66 | 62.14
2019-02-23 20:30 | 61.74 | 60.16
2019-02-23 21:00 | 60.19 | 58.57
2019-02-23 21:30 | 58.58 | 56.91
2019-02-23 22:00 | 56.85 | 55.14
2019-02-23 22:30 | 54.4 | 52.61
2019-02-23 23:00 | 53.41 | 51.6
2019-02-23 23:30 | 50.91 | 49.01
2019-02-24 | 49 | 47.02
2019-02-24 00:30 | 47.59 | 45.58
2019-02-24 01:00 | 46.26 | 44.16
2019-02-24 01:30 | 45.33 | 43.19
2019-02-24 02:00 | 44.75 | 42.59
2019-02-24 02:30 | 44.33 | 42.08
2019-02-24 03:00 | 43.98 | 41.67
2019-02-24 03:30 | 43.54 | 41.21
2019-02-24 04:00 | 43.43 | 41.09
2019-02-24 04:30 | 43.76 | 41.43
2019-02-24 05:00 | 44.13 | 41.82
2019-02-24 05:30 | 44.62 | 42.35
2019-02-24 06:00 | 44.77 | 42.5
2019-02-24 06:30 | 45.67 | 43.45
2019-02-24 07:00 | 47.01 | 44.85
2019-02-24 07:30 | 49.27 | 47.21
2019-02-24 08:00 | 49.55 | 47.47
2019-02-24 08:30 | 51.1 | 49.07
2019-02-24 09:00 | 51.28 | 49.24
2019-02-24 09:30 | 54.4 | 52.5
2019-02-24 10:00 | 56.68 | 54.93
2019-02-24 10:30 | 56.8 | 55.04
2019-02-24 11:00 | 53.7 | 51.84
2019-02-24 11:30 | 54.65 | 52.81
2019-02-24 12:00 | 53.23 | 51.35
2019-02-24 12:30 | 53.02 | 51.12
2019-02-24 13:00 | 49.64 | 47.59
2019-02-24 13:30 | 48.23 | 46.11
2019-02-24 14:00 | 48.65 | 46.54
2019-02-24 14:30 | 49.35 | 47.28
2019-02-24 15:00 | 50.9 | 48.91
2019-02-24 15:30 | 52.29 | 50.36
2019-02-24 16:00 | 54.08 | 52.23
2019-02-24 16:30 | 56.5 | 54.75
2019-02-24 17:00 | 59.11 | 57.45
2019-02-24 17:30 | 61.35 | 59.77
2019-02-24 18:00 | 64.07 | 62.57
2019-02-24 18:30 | 65.42 | 63.97
2019-02-24 19:00 | 66.32 | 64.89
2019-02-24 19:30 | 66.97 | 65.55
2019-02-24 20:00 | 64.89 | 63.42
2019-02-24 20:30 | 62.56 | 61.03
2019-02-24 21:00 | 60.59 | 59
2019-02-24 21:30 | 57.96 | 56.3
2019-02-24 22:00 | 55.11 | 53.36
2019-02-24 22:30 | 52.43 | 50.6
2019-02-24 23:00 | 51.04 | 49.15
2019-02-24 23:30 | 48.15 | 46.14
2019-02-25 | 46.48 | 44.31
2019-02-25 00:30 | 45.5 | 43.29
2019-02-25 01:00 | 44.55 | 42.28
2019-02-25 01:30 | 44.01 | 41.69
2019-02-25 02:00 | 43.51 | 41.18
2019-02-25 02:30 | 42.96 | 40.59
2019-02-25 03:00 | 42.69 | 40.31
2019-02-25 03:30 | 42.69 | 40.31
2019-02-25 04:00 | 42.69 | 40.31
2019-02-25 04:30 | 43.21 | 40.86
2019-02-25 05:00 | 44.31 | 42.01
2019-02-25 05:30 | 47.12 | 44.95
2019-02-25 06:00 | 50.2 | 48.15
2019-02-25 06:30 | 56.48 | 54.65
2019-02-25 07:00 | 61.78 | 60.13
2019-02-25 07:30 | 66.48 | 64.95
2019-02-25 08:00 | 67.24 | 65.69
2019-02-25 08:30 | 64.7 | 63.05
2019-02-25 09:00 | 70.34 | 68.8
2019-02-25 09:30 | 71.52 | 69.95
2019-02-25 10:00 | 67.24 | 65.52
2019-02-25 10:30 | 68.37 | 66.48
2019-02-25 11:00 | 65.83 | 63.66
2019-02-25 11:30 | 65.33 | 62.95
2019-02-25 12:00 | 67.63 | 65.22
2019-02-25 12:30 | 69.2 | 66.73
2019-02-25 13:00 | 70.94 | 68.8
2019-02-25 13:30 | 71.75 | 69.56
2019-02-25 14:00 | 70.02 | 67.72
2019-02-25 14:30 | 72.01 | 69.79
2019-02-25 15:00 | 70.73 | 68.6
2019-02-25 15:30 | 70.51 | 68.66
2019-02-25 16:00 | 72.53 | 70.88
2019-02-25 16:30 | 72.69 | 71.46
2019-02-25 17:00 | 73.16 | 72.23
2019-02-25 17:30 | 72.78 | 72.22
2019-02-25 18:00 | 72.87 | 72.57
2019-02-25 18:30 | 71.33 | 71.19
2019-02-25 19:00 | 72.59 | 72.45
2019-02-25 19:30 | 73.22 | 72.21
2019-02-25 20:00 | 71 | 69.6
2019-02-25 20:30 | 67.99 | 66.53
2019-02-25 21:00 | 65.46 | 63.95
2019-02-25 21:30 | 62.71 | 61.13
2019-02-25 22:00 | 63.71 | 58.3
2019-02-25 22:30 | 60.76 | 54.36
2019-02-25 23:00 | 59.21 | 52.59
2019-02-25 23:30 | 56.64 | 49.64
2019-02-26 | 54.37 | 47.31
2019-02-26 00:30 | 53.25 | 46.1
2019-02-26 01:00 | 52.27 | 44.83
2019-02-26 01:30 | 51.4 | 43.81
2019-02-26 02:00 | 50.7 | 42.99
2019-02-26 02:30 | 49.88 | 42.02
2019-02-26 03:00 | 49.49 | 41.56
2019-02-26 03:30 | 49.31 | 41.34
2019-02-26 04:00 | 49.26 | 41.27
2019-02-26 04:30 | 49.33 | 41.38
2019-02-26 05:00 | 50.51 | 42.76
2019-02-26 05:30 | 52.95 | 45.61
2019-02-26 06:00 | 55.33 | 48.36
2019-02-26 06:30 | 60.04 | 53.67
2019-02-26 07:00 | 64.46 | 58.57
2019-02-26 07:30 | 67.41 | 64.33
2019-02-26 08:00 | 66.86 | 65.32
2019-02-26 08:30 | 68.63 | 67.11
2019-02-26 09:00 | 67.72 | 66.18
2019-02-26 09:30 | 70.3 | 68.81
2019-02-26 10:00 | 64.55 | 62.91
2019-02-26 10:30 | 67.75 | 66.25
2019-02-26 11:00 | 64.48 | 62.87
2019-02-26 11:30 | 65.55 | 63.98
2019-02-26 12:00 | 62.73 | 61.07
2019-02-26 12:30 | 64.28 | 62.65
2019-02-26 13:00 | 62.81 | 61.14
2019-02-26 13:30 | 61.69 | 59.98
2019-02-26 14:00 | 62.12 | 60.42
2019-02-26 14:30 | 63.78 | 62.13
2019-02-26 15:00 | 65.02 | 63.41
2019-02-26 15:30 | 68.32 | 66.82
2019-02-26 16:00 | 67.36 | 65.85
2019-02-26 16:30 | 66.65 | 65.15
2019-02-26 17:00 | 68.57 | 67.16
2019-02-26 17:30 | 68.4 | 67.02
2019-02-26 18:00 | 68.19 | 66.85
2019-02-26 18:30 | 67.51 | 66.19
2019-02-26 19:00 | 68.83 | 67.53
2019-02-26 19:30 | 69.04 | 67.74
2019-02-26 20:00 | 66.88 | 65.54
2019-02-26 20:30 | 64.17 | 62.78
2019-02-26 21:00 | 62.05 | 60.6
2019-02-26 21:30 | 60.1 | 58.61
2019-02-26 22:00 | 57.42 | 55.87
2019-02-26 22:30 | 54.15 | 52.47
2019-02-26 23:00 | 52.96 | 51.12
2019-02-26 23:30 | 49.72 | 47.75
2019-02-27 | 47.28 | 45.14
2019-02-27 00:30 | 46.21 | 43.99
2019-02-27 01:00 | 45.28 | 43
2019-02-27 01:30 | 44.74 | 42.43
2019-02-27 02:00 | 44.07 | 41.73
2019-02-27 02:30 | 43.37 | 40.99
2019-02-27 03:00 | 42.94 | 40.56
2019-02-27 03:30 | 42.78 | 40.39
2019-02-27 04:00 | 42.58 | 40.18
2019-02-27 04:30 | 43.2 | 40.83
2019-02-27 05:00 | 44.26 | 41.94
2019-02-27 05:30 | 46.98 | 44.78
2019-02-27 06:00 | 50.11 | 48.04
2019-02-27 06:30 | 55.9 | 54.01
2019-02-27 07:00 | 60.53 | 58.83
2019-02-27 07:30 | 65.77 | 64.2
2019-02-27 08:00 | 68.38 | 66.87
2019-02-27 08:30 | 68.22 | 66.71
2019-02-27 09:00 | 69.46 | 67.99
2019-02-27 09:30 | 67.5 | 65.98
2019-02-27 10:00 | 66.31 | 64.75
2019-02-27 10:30 | 64.11 | 62.47
2019-02-27 11:00 | 66.08 | 64.49
2019-02-27 11:30 | 65.44 | 63.81
2019-02-27 12:00 | 65.72 | 64.11
2019-02-27 12:30 | 71.37 | 69.9
2019-02-27 13:00 | 66.94 | 65.38
2019-02-27 13:30 | 66.17 | 65.15
2019-02-27 14:00 | 67.39 | 66.71
2019-02-27 14:30 | 66.06 | 65.42
2019-02-27 15:00 | 64.91 | 64.21
2019-02-27 15:30 | 65.67 | 65.01
2019-02-27 16:00 | 66.18 | 65.63
2019-02-27 16:30 | 66.38 | 66
2019-02-27 17:00 | 66.33 | 66.12
2019-02-27 17:30 | 66.76 | 66.7
2019-02-27 18:00 | 68.17 | 68.16
2019-02-27 18:30 | 66.45 | 66.43
2019-02-27 19:00 | 68.41 | 68.41
2019-02-27 19:30 | 67.28 | 67.27
2019-02-27 20:00 | 64.91 | 64.88
2019-02-27 20:30 | 62.43 | 62.38
2019-02-27 21:00 | 60.25 | 60.17
2019-02-27 21:30 | 57.65 | 57.49
2019-02-27 22:00 | 55.17 | 54.7
2019-02-27 22:30 | 52.6 | 51
2019-02-27 23:00 | 52.03 | 50.42
2019-02-27 23:30 | 48.86 | 47.11
2019-02-28 | 46.74 | 44.83
2019-02-28 00:30 | 45.87 | 43.93
2019-02-28 01:00 | 45.13 | 43.15
2019-02-28 01:30 | 44.37 | 42.37
2019-02-28 02:00 | 43.48 | 41.41
2019-02-28 02:30 | 42.49 | 40.3
2019-02-28 03:00 | 42.34 | 40.14
2019-02-28 03:30 | 42.12 | 39.92
2019-02-28 04:00 | 41.85 | 39.64
2019-02-28 04:30 | 42.57 | 40.39
2019-02-28 05:00 | 42.54 | 40.35
2019-02-28 05:30 | 45.2 | 43.14
2019-02-28 06:00 | 48.95 | 47.03
2019-02-28 06:30 | 54.91 | 53.16
2019-02-28 07:00 | 60.4 | 58.78
2019-02-28 07:30 | 65.81 | 64.93
2019-02-28 08:00 | 68.34 | 67.4
2019-02-28 08:30 | 67.12 | 65.91
2019-02-28 09:00 | 68 | 66.84
2019-02-28 09:30 | 71.49 | 70.39
2019-02-28 10:00 | 69.4 | 68.27
2019-02-28 10:30 | 63.45 | 62.18
2019-02-28 11:00 | 70.34 | 69.2
2019-02-28 11:30 | 65.58 | 64.36
2019-02-28 12:00 | 64.73 | 63.49
2019-02-28 12:30 | 63.75 | 62.48
2019-02-28 13:00 | 64.7 | 63.45
2019-02-28 13:30 | 64.21 | 62.93
2019-02-28 14:00 | 65.55 | 64.3
2019-02-28 14:30 | 66.35 | 65.12
2019-02-28 15:00 | 65.98 | 64.74
2019-02-28 15:30 | 66.18 | 64.96
2019-02-28 16:00 | 66.26 | 65.07
2019-02-28 16:30 | 67.92 | 66.79
2019-02-28 17:00 | 69.47 | 68.37
2019-02-28 17:30 | 68.25 | 66.79
2019-02-28 18:00 | 69.62 | 67.8
2019-02-28 18:30 | 70.79 | 68.61
2019-02-28 19:00 | 72.62 | 70.61
2019-02-28 19:30 | 72.34 | 70.22
2019-02-28 20:00 | 70.15 | 67.72
2019-02-28 20:30 | 67.64 | 65
2019-02-28 21:00 | 63.93 | 62.61
2019-02-28 21:30 | 61.29 | 59.92
2019-02-28 22:00 | 58.15 | 56.7
2019-02-28 22:30 | 54.51 | 52.97
2019-02-28 23:00 | 53.06 | 51.5
2019-02-28 23:30 | 49.6 | 47.87
2019-03-01 | 47.34 | 45.49
2019-03-01 00:30 | 46.21 | 44.3
2019-03-01 01:00 | 44.75 | 42.78
2019-03-01 01:30 | 44.3 | 42.27
2019-03-01 02:00 | 43.8 | 41.69
2019-03-01 02:30 | 43.31 | 41.17
2019-03-01 03:00 | 42.5 | 40.34
2019-03-01 03:30 | 42.06 | 39.88
2019-03-01 04:00 | 41.87 | 39.69
2019-03-01 04:30 | 41.72 | 39.53
2019-03-01 05:00 | 43.13 | 41
2019-03-01 05:30 | 46.33 | 44.34
2019-03-01 06:00 | 49.17 | 47.29
2019-03-01 06:30 | 54.76 | 53.04
2019-03-01 07:00 | 59.31 | 58.25
2019-03-01 07:30 | 65.45 | 64.5
2019-03-01 08:00 | 67.95 | 66.85
2019-03-01 08:30 | 68.75 | 67.82
2019-03-01 09:00 | 70.14 | 68.93
2019-03-01 09:30 | 68.89 | 67.66
2019-03-01 10:00 | 67.89 | 66.58
2019-03-01 10:30 | 70.56 | 69.28
2019-03-01 11:00 | 70.25 | 68.83
2019-03-01 11:30 | 70.35 | 68.92
2019-03-01 12:00 | 67.47 | 65.93
2019-03-01 12:30 | 72.22 | 70.71
2019-03-01 13:00 | 66.63 | 64.31
2019-03-01 13:30 | 61.36 | 59.63
2019-03-01 14:00 | 64.72 | 63.06
2019-03-01 14:30 | 63.77 | 62.15
2019-03-01 15:00 | 63.6 | 62.16
2019-03-01 15:30 | 63.33 | 62.16
2019-03-01 16:00 | 64.48 | 63.57
2019-03-01 16:30 | 66.48 | 65.83
2019-03-01 17:00 | 65.56 | 65.15
2019-03-01 17:30 | 64.82 | 64.51
2019-03-01 18:00 | 64.92 | 64.59
2019-03-01 18:30 | 64.82 | 64.47
2019-03-01 19:00 | 66.35 | 66.01
2019-03-01 19:30 | 66.63 | 66.28
2019-03-01 20:00 | 64.52 | 64.15
2019-03-01 20:30 | 62.32 | 61.93
2019-03-01 21:00 | 60.61 | 60.2
2019-03-01 21:30 | 58.99 | 58.56
2019-03-01 22:00 | 56.62 | 56.21
2019-03-01 22:30 | 53.54 | 53.14
2019-03-01 23:00 | 52.2 | 51.79
2019-03-01 23:30 | 48.78 | 48.34
2019-03-02 | 46.53 | 46.08
2019-03-02 00:30 | 44.89 | 44.4
2019-03-02 01:00 | 43.42 | 42.88
2019-03-02 01:30 | 41.95 | 41.4
2019-03-02 02:00 | 41.46 | 40.91
2019-03-02 02:30 | 41.05 | 40.49
2019-03-02 03:00 | 40.29 | 39.73
2019-03-02 03:30 | 39.83 | 39.27
2019-03-02 04:00 | 39.73 | 39.16
2019-03-02 04:30 | 39.98 | 39.41
2019-03-02 05:00 | 40.38 | 39.81
2019-03-02 05:30 | 41.54 | 40.99
2019-03-02 06:00 | 41.72 | 41.18
2019-03-02 06:30 | 44.03 | 43.5
2019-03-02 07:00 | 45.79 | 45.28
2019-03-02 07:30 | 47.82 | 47.31
2019-03-02 08:00 | 49.46 | 48.94
2019-03-02 08:30 | 51.38 | 50.87
2019-03-02 09:00 | 52.64 | 52.17
2019-03-02 09:30 | 55.09 | 54.64
2019-03-02 10:00 | 53.25 | 52.78
2019-03-02 10:30 | 54.23 | 53.76
2019-03-02 11:00 | 49.41 | 48.88
2019-03-02 11:30 | 51.86 | 51.36
2019-03-02 12:00 | 53.75 | 53.28
2019-03-02 12:30 | 50.79 | 50.3
2019-03-02 13:00 | 49.99 | 49.49
2019-03-02 13:30 | 53.82 | 53.37
2019-03-02 14:00 | 50.98 | 50.5
2019-03-02 14:30 | 47.09 | 46.57
2019-03-02 15:00 | 47.57 | 47.06
2019-03-02 15:30 | 48.65 | 48.16
2019-03-02 16:00 | 50.95 | 50.49
2019-03-02 16:30 | 52.8 | 52.36
2019-03-02 17:00 | 55.15 | 54.74
2019-03-02 17:30 | 56.41 | 56.01
2019-03-02 18:00 | 58.51 | 58.14
2019-03-02 18:30 | 59.94 | 59.58
2019-03-02 19:00 | 61.59 | 61.23
2019-03-02 19:30 | 61.7 | 61.34
2019-03-02 20:00 | 60.02 | 59.66
2019-03-02 20:30 | 57.99 | 57.61
2019-03-02 21:00 | 56.61 | 56.23
2019-03-02 21:30 | 55.63 | 55.24
2019-03-02 22:00 | 54.06 | 53.66
2019-03-02 22:30 | 50.94 | 50.52
2019-03-02 23:00 | 50.27 | 49.84
2019-03-02 23:30 | 47.24 | 46.74
2019-03-03 | 44.98 | 44.47
2019-03-03 00:30 | 43.62 | 43.04
2019-03-03 01:00 | 42.11 | 41.51
2019-03-03 01:30 | 41.42 | 40.8
2019-03-03 02:00 | 41 | 40.38
2019-03-03 02:30 | 40.07 | 39.44
2019-03-03 03:00 | 38.69 | 38.04
2019-03-03 03:30 | 38.74 | 38.09
2019-03-03 04:00 | 39.37 | 38.74
2019-03-03 04:30 | 38.77 | 38.13
2019-03-03 05:00 | 39.17 | 38.53
2019-03-03 05:30 | 39.12 | 38.48
2019-03-03 06:00 | 39.26 | 38.63
2019-03-03 06:30 | 40.84 | 40.24
2019-03-03 07:00 | 41.69 | 41.09
2019-03-03 07:30 | 43.96 | 43.38
2019-03-03 08:00 | 45.79 | 45.23
2019-03-03 08:30 | 46.37 | 45.8
2019-03-03 09:00 | 46.05 | 45.46
2019-03-03 09:30 | 45.23 | 44.62
2019-03-03 10:00 | 44.64 | 44.06
2019-03-03 10:30 | 44.03 | 43.44
2019-03-03 11:00 | 46.16 | 45.6
2019-03-03 11:30 | 52.65 | 52.18
2019-03-03 12:00 | 47.44 | 46.91
2019-03-03 12:30 | 44.57 | 44
2019-03-03 13:00 | 43.02 | 42.42
2019-03-03 13:30 | 44.71 | 44.13
2019-03-03 14:00 | 44.63 | 44.05
2019-03-03 14:30 | 44.96 | 44.38
2019-03-03 15:00 | 46.1 | 45.54
2019-03-03 15:30 | 48.97 | 48.46
2019-03-03 16:00 | 51.16 | 50.67
2019-03-03 16:30 | 52.47 | 52
2019-03-03 17:00 | 55.19 | 54.75
2019-03-03 17:30 | 57.54 | 57.12
2019-03-03 18:00 | 60.38 | 59.97
2019-03-03 18:30 | 62.69 | 62.3
2019-03-03 19:00 | 64.61 | 64.21
2019-03-03 19:30 | 64.23 | 63.82
2019-03-03 20:00 | 61.88 | 61.47
2019-03-03 20:30 | 59.6 | 59.18
2019-03-03 21:00 | 57.83 | 57.4
2019-03-03 21:30 | 55.75 | 55.3
2019-03-03 22:00 | 52.72 | 52.25
2019-03-03 22:30 | 49.77 | 49.28
2019-03-03 23:00 | 48.98 | 48.49
2019-03-03 23:30 | 45.76 | 45.2
2019-03-04 | 43.62 | 43.02
2019-03-04 00:30 | 42.08 | 41.46
2019-03-04 01:00 | 41.22 | 40.58
2019-03-04 01:30 | 40.57 | 39.92
2019-03-04 02:00 | 39.55 | 38.88
2019-03-04 02:30 | 38.94 | 38.26
2019-03-04 03:00 | 38.36 | 37.68
2019-03-04 03:30 | 38.9 | 38.23
2019-03-04 04:00 | 38.47 | 37.78
2019-03-04 04:30 | 38.98 | 38.3
2019-03-04 05:00 | 40.1 | 39.45
2019-03-04 05:30 | 42.74 | 42.12
2019-03-04 06:00 | 45.83 | 45.23
2019-03-04 06:30 | 52.34 | 51.74
2019-03-04 07:00 | 57.84 | 57.33
2019-03-04 07:30 | 64.55 | 63.98
2019-03-04 08:00 | 66.45 | 65.96
2019-03-04 08:30 | 68.15 | 67.39
2019-03-04 09:00 | 69.08 | 68.23
2019-03-04 09:30 | 70.59 | 69.69
2019-03-04 10:00 | 66.75 | 65.77
2019-03-04 10:30 | 66.35 | 65.26
2019-03-04 11:00 | 68.85 | 67.68
2019-03-04 11:30 | 68.51 | 67.12
2019-03-04 12:00 | 66.68 | 65.03
2019-03-04 12:30 | 64.94 | 63.61
2019-03-04 13:00 | 68.43 | 67.5
2019-03-04 13:30 | 68.33 | 67.47
2019-03-04 14:00 | 65.07 | 64.1
2019-03-04 14:30 | 65.49 | 64.4
2019-03-04 15:00 | 66.85 | 65.79
2019-03-04 15:30 | 66.8 | 65.85
2019-03-04 16:00 | 68.81 | 68.08
2019-03-04 16:30 | 68.4 | 67.98
2019-03-04 17:00 | 69.22 | 68.91
2019-03-04 17:30 | 68.51 | 68.17
2019-03-04 18:00 | 68.59 | 68.23
2019-03-04 18:30 | 68.21 | 67.83
2019-03-04 19:00 | 70.16 | 69.8
2019-03-04 19:30 | 69.75 | 69.38
2019-03-04 20:00 | 67.62 | 67.23
2019-03-04 20:30 | 65.19 | 64.77
2019-03-04 21:00 | 62.19 | 61.84
2019-03-04 21:30 | 59.4 | 59.06
2019-03-04 22:00 | 56.46 | 56.11
2019-03-04 22:30 | 53.12 | 52.75
2019-03-04 23:00 | 52.54 | 52.14
2019-03-04 23:30 | 49.3 | 48.77
2019-03-05 | 46.23 | 45.69
2019-03-05 00:30 | 44.75 | 44.23
2019-03-05 01:00 | 43.3 | 42.76
2019-03-05 01:30 | 42.44 | 41.9
2019-03-05 02:00 | 41.89 | 41.34
2019-03-05 02:30 | 41.38 | 40.83
2019-03-05 03:00 | 40.76 | 40.2
2019-03-05 03:30 | 40.79 | 40.23
2019-03-05 04:00 | 40.19 | 39.62
2019-03-05 04:30 | 40.88 | 40.32
2019-03-05 05:00 | 42.2 | 41.65
2019-03-05 05:30 | 44.84 | 44.32
2019-03-05 06:00 | 48.13 | 47.63
2019-03-05 06:30 | 54.06 | 53.59
2019-03-05 07:00 | 59.43 | 58.93
2019-03-05 07:30 | 66.12 | 65.27
2019-03-05 08:00 | 68.53 | 67.99
2019-03-05 08:30 | 68.76 | 68.39
2019-03-05 09:00 | 70.22 | 69.71
2019-03-05 09:30 | 69.28 | 68.75
2019-03-05 10:00 | 66.2 | 65.52
2019-03-05 10:30 | 70.63 | 69.85
2019-03-05 11:00 | 72.74 | 72
2019-03-05 11:30 | 69.95 | 69.17
2019-03-05 12:00 | 69.05 | 68.16
2019-03-05 12:30 | 71.01 | 70.07
2019-03-05 13:00 | 66.45 | 65.42
2019-03-05 13:30 | 71.5 | 70.48
2019-03-05 14:00 | 70.84 | 69.77
2019-03-05 14:30 | 74.15 | 73.13
2019-03-05 15:00 | 75.47 | 74.58
2019-03-05 15:30 | 74.07 | 73.38
2019-03-05 16:00 | 72.44 | 71.92
2019-03-05 16:30 | 71.04 | 70.74
2019-03-05 17:00 | 69.68 | 69.37
2019-03-05 17:30 | 69.94 | 69.62
2019-03-05 18:00 | 70.59 | 70.25
2019-03-05 18:30 | 71.03 | 70.67
2019-03-05 19:00 | 72.73 | 72.4
2019-03-05 19:30 | 71.1 | 70.74
2019-03-05 20:00 | 69.02 | 68.65
2019-03-05 20:30 | 66.41 | 66.02
2019-03-05 21:00 | 64.12 | 63.69
2019-03-05 21:30 | 61.7 | 61.26
2019-03-05 22:00 | 58.66 | 58.25
2019-03-05 22:30 | 55.05 | 54.7
2019-03-05 23:00 | 54.44 | 54.08
2019-03-05 23:30 | 50.87 | 50.43
2019-03-06 | 48.32 | 47.79
2019-03-06 00:30 | 46.08 | 45.53
2019-03-06 01:00 | 45.05 | 44.47
2019-03-06 01:30 | 44.57 | 43.98
2019-03-06 02:00 | 44.27 | 43.67
2019-03-06 02:30 | 43.91 | 43.31
2019-03-06 03:00 | 43.02 | 42.41
2019-03-06 03:30 | 42.63 | 42.02
2019-03-06 04:00 | 42.6 | 41.98
2019-03-06 04:30 | 43.91 | 43.31
2019-03-06 05:00 | 45.29 | 44.7
2019-03-06 05:30 | 48.23 | 47.67
2019-03-06 06:00 | 51.63 | 51.02
2019-03-06 06:30 | 58.88 | 58.05
2019-03-06 07:00 | 64.68 | 63.95
2019-03-06 07:30 | 71.76 | 71.21
2019-03-06 08:00 | 76.33 | 75.85
2019-03-06 08:30 | 78.28 | 77.67
2019-03-06 09:00 | 80.36 | 79.56
2019-03-06 09:30 | 79.76 | 78.98
2019-03-06 10:00 | 79.39 | 78.64
2019-03-06 10:30 | 79.15 | 78.42
2019-03-06 11:00 | 77.78 | 77.06
2019-03-06 11:30 | 70.76 | 69.86
2019-03-06 12:00 | 74.89 | 74.31
2019-03-06 12:30 | 75.48 | 74.89
2019-03-06 13:00 | 72.27 | 71.7
2019-03-06 13:30 | 67.71 | 67.03
2019-03-06 14:00 | 64.02 | 63.12
2019-03-06 14:30 | 67.33 | 66.33
2019-03-06 15:00 | 68.93 | 68.01
2019-03-06 15:30 | 70.98 | 70.2
2019-03-06 16:00 | 68.99 | 68.5
2019-03-06 16:30 | 66.42 | 66.16
2019-03-06 17:00 | 68.42 | 68.28
2019-03-06 17:30 | 71.33 | 71.26
2019-03-06 18:00 | 71.04 | 71.03
2019-03-06 18:30 | 69.56 | 69.56
2019-03-06 19:00 | 69.75 | 69.69
2019-03-06 19:30 | 67.54 | 67.48
2019-03-06 20:00 | 65.46 | 65.42
2019-03-06 20:30 | 62.52 | 62.51
2019-03-06 21:00 | 59.81 | 59.81
2019-03-06 21:30 | 61.52 | 61.52
2019-03-06 22:00 | 56.76 | 56.75
2019-03-06 22:30 | 53.2 | 53.16
2019-03-06 23:00 | 50.7 | 50.63
2019-03-06 23:30 | 47.98 | 47.74
2019-03-07 | 47.59 | 45.74
2019-03-07 00:30 | 46.54 | 44.65
2019-03-07 01:00 | 45.03 | 43.01
2019-03-07 01:30 | 44.13 | 42.02
2019-03-07 02:00 | 43.47 | 41.34
2019-03-07 02:30 | 43.02 | 40.86
2019-03-07 03:00 | 42.56 | 40.38
2019-03-07 03:30 | 42.16 | 39.96
2019-03-07 04:00 | 42.38 | 40.2
2019-03-07 04:30 | 43.2 | 41.05
2019-03-07 05:00 | 45.08 | 43.02
2019-03-07 05:30 | 48.79 | 46.86
2019-03-07 06:00 | 51.73 | 49.93
2019-03-07 06:30 | 57.23 | 55.95
2019-03-07 07:00 | 62.05 | 61.46
2019-03-07 07:30 | 69.53 | 68.35
2019-03-07 08:00 | 73.32 | 72.21
2019-03-07 08:30 | 75.09 | 73.91
2019-03-07 09:00 | 74.89 | 73.64
2019-03-07 09:30 | 73.72 | 72.59
2019-03-07 10:00 | 74.86 | 73.77
2019-03-07 10:30 | 75.88 | 74.82
2019-03-07 11:00 | 76.17 | 75.12
2019-03-07 11:30 | 75.25 | 74.15
2019-03-07 12:00 | 72.41 | 71.13
2019-03-07 12:30 | 72.98 | 71.57
2019-03-07 13:00 | 74.51 | 73.02
2019-03-07 13:30 | 75.94 | 74.5
2019-03-07 14:00 | 74.46 | 72.83
2019-03-07 14:30 | 79.05 | 77.44
2019-03-07 15:00 | 78.16 | 76.7
2019-03-07 15:30 | 76.71 | 75.45
2019-03-07 16:00 | 80.56 | 79.49
2019-03-07 16:30 | 79.73 | 78.69
2019-03-07 17:00 | 78.89 | 77.81
2019-03-07 17:30 | 77.44 | 76.28
2019-03-07 18:00 | 77.27 | 76.06
2019-03-07 18:30 | 78.64 | 77.44
2019-03-07 19:00 | 79.23 | 78.03
2019-03-07 19:30 | 78.96 | 77.76
2019-03-07 20:00 | 76.34 | 75.07
2019-03-07 20:30 | 73.88 | 72.54
2019-03-07 21:00 | 71.61 | 70.21
2019-03-07 21:30 | 68.27 | 66.76
2019-03-07 22:00 | 64.33 | 62.97
2019-03-07 22:30 | 58.65 | 58.55
2019-03-07 23:00 | 57.61 | 57.44
2019-03-07 23:30 | 53.63 | 53.36
2019-03-08 | 51.29 | 50.98
2019-03-08 00:30 | 49.39 | 49.01
2019-03-08 01:00 | 48.63 | 47.5
2019-03-08 01:30 | 47.65 | 45.89
2019-03-08 02:00 | 46.64 | 44.84
2019-03-08 02:30 | 46.9 | 45.11
2019-03-08 03:00 | 45.78 | 43.85
2019-03-08 03:30 | 45.56 | 43.63
2019-03-08 04:00 | 45.61 | 43.65
2019-03-08 04:30 | 45.82 | 43.8
2019-03-08 05:00 | 47.12 | 45.15
2019-03-08 05:30 | 49.88 | 48.01
2019-03-08 06:00 | 52.92 | 51.14
2019-03-08 06:30 | 59.99 | 58.65
2019-03-08 07:00 | 66.35 | 65.48
2019-03-08 07:30 | 72.37 | 71.6
2019-03-08 08:00 | 75.36 | 74.3
2019-03-08 08:30 | 75.76 | 74.63
2019-03-08 09:00 | 75.47 | 74.36
2019-03-08 09:30 | 76.78 | 75.71
2019-03-08 10:00 | 74.36 | 73.24
2019-03-08 10:30 | 76.47 | 75.28
2019-03-08 11:00 | 77.52 | 76.35
2019-03-08 11:30 | 78.66 | 77.5
2019-03-08 12:00 | 78.97 | 77.81
2019-03-08 12:30 | 79.18 | 78.06
2019-03-08 13:00 | 76.14 | 75.05
2019-03-08 13:30 | 72.03 | 70.88
2019-03-08 14:00 | 74.89 | 73.79
2019-03-08 14:30 | 75.73 | 74.62
2019-03-08 15:00 | 72.16 | 70.95
2019-03-08 15:30 | 70.41 | 69.14
2019-03-08 16:00 | 72.64 | 71.39
2019-03-08 16:30 | 72.91 | 71.65
2019-03-08 17:00 | 73.09 | 71.8
2019-03-08 17:30 | 72.05 | 70.69
2019-03-08 18:00 | 70.67 | 69.24
2019-03-08 18:30 | 68.09 | 66.69
2019-03-08 19:00 | 68.47 | 67.17
2019-03-08 19:30 | 66.98 | 65.64
2019-03-08 20:00 | 65.39 | 64
2019-03-08 20:30 | 63.46 | 62.01
2019-03-08 21:00 | 61.76 | 60.25
2019-03-08 21:30 | 59.69 | 58.1
2019-03-08 22:00 | 57.45 | 55.77
2019-03-08 22:30 | 54.89 | 53.09
2019-03-08 23:00 | 54.86 | 53.04
2019-03-08 23:30 | 49.85 | 48.22
2019-03-09 | 45.94 | 45.94
2019-03-09 00:30 | 44.46 | 44.45
2019-03-09 01:00 | 43.06 | 43.05
2019-03-09 01:30 | 42.02 | 42.01
2019-03-09 02:00 | 41.18 | 41.17
2019-03-09 02:30 | 40.58 | 40.56
2019-03-09 03:00 | 40.02 | 39.96
2019-03-09 03:30 | 39.55 | 39.47
2019-03-09 04:00 | 39.5 | 39.41
2019-03-09 04:30 | 39.67 | 39.57
2019-03-09 05:00 | 39.82 | 39.75
2019-03-09 05:30 | 40.71 | 40.65
2019-03-09 06:00 | 41.74 | 41.66
2019-03-09 06:30 | 44.53 | 44.39
2019-03-09 07:00 | 46.26 | 46.07
2019-03-09 07:30 | 49.35 | 49
2019-03-09 08:00 | 52.09 | 51.62
2019-03-09 08:30 | 54.5 | 54.26
2019-03-09 09:00 | 57.27 | 56.91
2019-03-09 09:30 | 55.81 | 55.37
2019-03-09 10:00 | 55.42 | 54.83
2019-03-09 10:30 | 54.15 | 53.4
2019-03-09 11:00 | 57.7 | 56.99
2019-03-09 11:30 | 59.16 | 58.51
2019-03-09 12:00 | 55.03 | 54.46
2019-03-09 12:30 | 54.73 | 54.2
2019-03-09 13:00 | 55.06 | 54.57
2019-03-09 13:30 | 53.66 | 53.18
2019-03-09 14:00 | 53.59 | 53.12
2019-03-09 14:30 | 55.9 | 55.49
2019-03-09 15:00 | 56.89 | 56.54
2019-03-09 15:30 | 59.2 | 58.92
2019-03-09 16:00 | 58.18 | 57.95
2019-03-09 16:30 | 57.51 | 57.32
2019-03-09 17:00 | 59.49 | 59.34
2019-03-09 17:30 | 60.34 | 60.23
2019-03-09 18:00 | 61.21 | 61.12
2019-03-09 18:30 | 61.97 | 61.86
2019-03-09 19:00 | 62.37 | 62.23
2019-03-09 19:30 | 60.92 | 60.8
2019-03-09 20:00 | 59.1 | 59.01
2019-03-09 20:30 | 56.99 | 56.92
2019-03-09 21:00 | 55.12 | 55.07
2019-03-09 21:30 | 53.48 | 53.44
2019-03-09 22:00 | 51.02 | 51.01
2019-03-09 22:30 | 49.23 | 49.23
2019-03-09 23:00 | 49.31 | 49.31
2019-03-09 23:30 | 45.99 | 45.98
2019-03-10 | 43.93 | 43.91
2019-03-10 00:30 | 42.59 | 42.56
2019-03-10 01:00 | 41.23 | 41.18
2019-03-10 01:30 | 40.22 | 40.16
2019-03-10 02:00 | 39.47 | 39.39
2019-03-10 02:30 | 38.75 | 38.67
2019-03-10 03:00 | 37.9 | 37.88
2019-03-10 03:30 | 37.41 | 37.39
2019-03-10 04:00 | 37.2 | 37.19
2019-03-10 04:30 | 37.4 | 37.38
2019-03-10 05:00 | 37.48 | 37.46
2019-03-10 05:30 | 38.13 | 38.12
2019-03-10 06:00 | 38.31 | 38.3
2019-03-10 06:30 | 39.43 | 39.42
2019-03-10 07:00 | 40.26 | 40.24
2019-03-10 07:30 | 42.56 | 42.51
2019-03-10 08:00 | 43.33 | 43.19
2019-03-10 08:30 | 45.31 | 45.03
2019-03-10 09:00 | 45.47 | 45.14
2019-03-10 09:30 | 46.69 | 46.61
2019-03-10 10:00 | 47.05 | 46.91
2019-03-10 10:30 | 48.09 | 47.91
2019-03-10 11:00 | 46.47 | 46.26
2019-03-10 11:30 | 45.16 | 44.9
2019-03-10 12:00 | 45.19 | 44.88
2019-03-10 12:30 | 46.6 | 46.31
2019-03-10 13:00 | 46.47 | 46.18
2019-03-10 13:30 | 47.6 | 47.29
2019-03-10 14:00 | 48.29 | 47.98
2019-03-10 14:30 | 48.43 | 48.14
2019-03-10 15:00 | 49.68 | 49.42
2019-03-10 15:30 | 51.19 | 50.98
2019-03-10 16:00 | 52.12 | 51.89
2019-03-10 16:30 | 53 | 52.79
2019-03-10 17:00 | 58.15 | 58.02
2019-03-10 17:30 | 60.06 | 59.94
2019-03-10 18:00 | 62.87 | 62.77
2019-03-10 18:30 | 64.78 | 64.68
2019-03-10 19:00 | 66.01 | 65.88
2019-03-10 19:30 | 65.62 | 65.5
2019-03-10 20:00 | 62.63 | 62.54
2019-03-10 20:30 | 60.18 | 60.12
2019-03-10 21:00 | 57.43 | 57.4
2019-03-10 21:30 | 55.01 | 54.99
2019-03-10 22:00 | 51.84 | 51.84
2019-03-10 22:30 | 48.29 | 48.29
2019-03-10 23:00 | 47.83 | 47.82
2019-03-10 23:30 | 43.89 | 43.85
2019-03-11 | 41.13 | 41.06
2019-03-11 00:30 | 39.78 | 39.74
2019-03-11 01:00 | 38.68 | 38.66
2019-03-11 01:30 | 37.76 | 37.74
2019-03-11 02:00 | 37.22 | 37.21
2019-03-11 02:30 | 36.86 | 36.85
2019-03-11 03:00 | 36.53 | 36.52
2019-03-11 03:30 | 36.52 | 36.51
2019-03-11 04:00 | 36.5 | 36.49
2019-03-11 04:30 | 37.33 | 37.32
2019-03-11 05:00 | 38.66 | 38.63
2019-03-11 05:30 | 41.55 | 41.47
2019-03-11 06:00 | 44.55 | 44.38
2019-03-11 06:30 | 51.4 | 50.89
2019-03-11 07:00 | 57 | 56.39
2019-03-11 07:30 | 62.84 | 62.3
2019-03-11 08:00 | 65.38 | 64.69
2019-03-11 08:30 | 67.23 | 66.08
2019-03-11 09:00 | 68.5 | 66.92
2019-03-11 09:30 | 70.76 | 69.01
2019-03-11 10:00 | 70.65 | 68.81
2019-03-11 10:30 | 69.96 | 67.86
2019-03-11 11:00 | 70.73 | 68.42
2019-03-11 11:30 | 71.04 | 68.64
2019-03-11 12:00 | 71.84 | 69.33
2019-03-11 12:30 | 73.64 | 71.18
2019-03-11 13:00 | 73.32 | 70.83
2019-03-11 13:30 | 73.67 | 71.13
2019-03-11 14:00 | 76.2 | 72.78
2019-03-11 14:30 | 78.63 | 74.15
2019-03-11 15:00 | 79.69 | 75.27
2019-03-11 15:30 | 80.89 | 76.4
2019-03-11 16:00 | 83.34 | 78.86
2019-03-11 16:30 | 83.72 | 79.15
2019-03-11 17:00 | 84.8 | 80.2
2019-03-11 17:30 | 83.94 | 79.15
2019-03-11 18:00 | 83.56 | 78.61
2019-03-11 18:30 | 82.2 | 77.17
2019-03-11 19:00 | 83.61 | 78.81
2019-03-11 19:30 | 82.16 | 77.23
2019-03-11 20:00 | 79.04 | 73.8
2019-03-11 20:30 | 75.19 | 69.74
2019-03-11 21:00 | 71.54 | 65.73
2019-03-11 21:30 | 65.47 | 61.98
2019-03-11 22:00 | 59.68 | 58.08
2019-03-11 22:30 | 55.57 | 53.8
2019-03-11 23:00 | 54.91 | 53.1
2019-03-11 23:30 | 49.05 | 48.59
2019-03-12 | 45.93 | 45.92
2019-03-12 00:30 | 44.3 | 44.3
2019-03-12 01:00 | 43.16 | 43.16
2019-03-12 01:30 | 42.04 | 42.02
2019-03-12 02:00 | 41.16 | 40.99
2019-03-12 02:30 | 40.18 | 40.03
2019-03-12 03:00 | 39.1 | 39
2019-03-12 03:30 | 38.91 | 38.82
2019-03-12 04:00 | 38.65 | 38.56
2019-03-12 04:30 | 39.42 | 39.33
2019-03-12 05:00 | 40.91 | 40.77
2019-03-12 05:30 | 43.63 | 43.43
2019-03-12 06:00 | 46.37 | 46.07
2019-03-12 06:30 | 52.81 | 52.15
2019-03-12 07:00 | 58.18 | 57.71
2019-03-12 07:30 | 64.71 | 64.05
2019-03-12 08:00 | 67.13 | 66.24
2019-03-12 08:30 | 67.29 | 66.01
2019-03-12 09:00 | 70.07 | 68.32
2019-03-12 09:30 | 69.55 | 67.63
2019-03-12 10:00 | 69.6 | 67.49
2019-03-12 10:30 | 70.86 | 68.6
2019-03-12 11:00 | 70.53 | 69.92
2019-03-12 11:30 | 70.71 | 70.41
2019-03-12 12:00 | 71.67 | 71.37
2019-03-12 12:30 | 72.91 | 72.62
2019-03-12 13:00 | 73.88 | 73.59
2019-03-12 13:30 | 74.54 | 74.25
2019-03-12 14:00 | 74.87 | 74.58
2019-03-12 14:30 | 76.1 | 75.82
2019-03-12 15:00 | 77.17 | 76.9
2019-03-12 15:30 | 78.4 | 78.13
2019-03-12 16:00 | 80.5 | 80.26
2019-03-12 16:30 | 81.51 | 81.28
2019-03-12 17:00 | 81.6 | 81.32
2019-03-12 17:30 | 79.85 | 79.58
2019-03-12 18:00 | 73.36 | 72.96
2019-03-12 18:30 | 78.64 | 77.94
2019-03-12 19:00 | 80.92 | 80.33
2019-03-12 19:30 | 79.46 | 78.78
2019-03-12 20:00 | 76.38 | 75.45
2019-03-12 20:30 | 72.95 | 71.69
2019-03-12 21:00 | 71.02 | 68.56
2019-03-12 21:30 | 67.73 | 65.14
2019-03-12 22:00 | 64.04 | 61.26
2019-03-12 22:30 | 60.18 | 57.15
2019-03-12 23:00 | 57.84 | 54.66
2019-03-12 23:30 | 54.03 | 50.28
2019-03-13 | 52.09 | 48.05
2019-03-13 00:30 | 50.86 | 46.72
2019-03-13 01:00 | 49.25 | 44.96
2019-03-13 01:30 | 48.22 | 43.84
2019-03-13 02:00 | 47.86 | 43.44
2019-03-13 02:30 | 46.99 | 42.47
2019-03-13 03:00 | 46.39 | 41.8
2019-03-13 03:30 | 46.25 | 41.64
2019-03-13 04:00 | 46.11 | 41.49
2019-03-13 04:30 | 47.03 | 42.52
2019-03-13 05:00 | 47.81 | 43.38
2019-03-13 05:30 | 50.08 | 45.86
2019-03-13 06:00 | 52.78 | 48.78
2019-03-13 06:30 | 57.61 | 54.56
2019-03-13 07:00 | 59.83 | 59.41
2019-03-13 07:30 | 65.8 | 65.23
2019-03-13 08:00 | 70.27 | 69.14
2019-03-13 08:30 | 71.59 | 70.03
2019-03-13 09:00 | 73.44 | 71.41
2019-03-13 09:30 | 73.21 | 72.82
2019-03-13 10:00 | 73.25 | 72.88
2019-03-13 10:30 | 72.83 | 72.47
2019-03-13 11:00 | 73.4 | 73.05
2019-03-13 11:30 | 69.25 | 68.89
2019-03-13 12:00 | 74.9 | 74.56
2019-03-13 12:30 | 76.46 | 76.13
2019-03-13 13:00 | 76.16 | 75.83
2019-03-13 13:30 | 76.81 | 76.49
2019-03-13 14:00 | 77.66 | 77.34
2019-03-13 14:30 | 78.59 | 78.28
2019-03-13 15:00 | 79.92 | 79.6
2019-03-13 15:30 | 81.35 | 81.04
2019-03-13 16:00 | 86.24 | 85.94
2019-03-13 16:30 | 86.62 | 86.3
2019-03-13 17:00 | 84.41 | 84.06
2019-03-13 17:30 | 80.84 | 80.49
2019-03-13 18:00 | 80.97 | 80.56
2019-03-13 18:30 | 80.33 | 79.74
2019-03-13 19:00 | 82.16 | 81.68
2019-03-13 19:30 | 81.03 | 80.47
2019-03-13 20:00 | 77.79 | 77.07
2019-03-13 20:30 | 73.82 | 72.86
2019-03-13 21:00 | 70.43 | 69.22
2019-03-13 21:30 | 66.9 | 65.37
2019-03-13 22:00 | 62.46 | 61.15
2019-03-13 22:30 | 58.53 | 57.08
2019-03-13 23:00 | 57.75 | 56.07
2019-03-13 23:30 | 53.96 | 51.22
2019-03-14 | 52.04 | 48.58
2019-03-14 00:30 | 50.23 | 46.66
2019-03-14 01:00 | 49.14 | 45.46
2019-03-14 01:30 | 47.82 | 44.05
2019-03-14 02:00 | 46.98 | 43.13
2019-03-14 02:30 | 46.2 | 42.29
2019-03-14 03:00 | 47.99 | 41.5
2019-03-14 03:30 | 51.58 | 41.09
2019-03-14 04:00 | 51.45 | 40.92
2019-03-14 04:30 | 52.03 | 41.64
2019-03-14 05:00 | 48.53 | 42.57
2019-03-14 05:30 | 47.47 | 45.41
2019-03-14 06:00 | 50.19 | 48.22
2019-03-14 06:30 | 55.5 | 54.22
2019-03-14 07:00 | 59.97 | 59.25
2019-03-14 07:30 | 66.05 | 65.32
2019-03-14 08:00 | 68.48 | 67.56
2019-03-14 08:30 | 70.18 | 69.37
2019-03-14 09:00 | 73.28 | 72.15
2019-03-14 09:30 | 75.85 | 74.46
2019-03-14 10:00 | 75.22 | 73.8
2019-03-14 10:30 | 75.61 | 74.08
2019-03-14 11:00 | 77.06 | 75.41
2019-03-14 11:30 | 76.94 | 75.14
2019-03-14 12:00 | 77.39 | 75.26
2019-03-14 12:30 | 79.18 | 76.84
2019-03-14 13:00 | 79.26 | 76.92
2019-03-14 13:30 | 80.53 | 78.25
2019-03-14 14:00 | 81.21 | 78.95
2019-03-14 14:30 | 82.35 | 80.13
2019-03-14 15:00 | 83.4 | 81.21
2019-03-14 15:30 | 83.77 | 81.56
2019-03-14 16:00 | 86.31 | 84.13
2019-03-14 16:30 | 87.08 | 84.86
2019-03-14 17:00 | 87.6 | 85.35
2019-03-14 17:30 | 86.44 | 84.07
2019-03-14 18:00 | 86.11 | 83.64
2019-03-14 18:30 | 85.71 | 83.18
2019-03-14 19:00 | 86.71 | 84.23
2019-03-14 19:30 | 85.79 | 83.27
2019-03-14 20:00 | 82.3 | 79.6
2019-03-14 20:30 | 78.7 | 75.8
2019-03-14 21:00 | 74.62 | 71.73
2019-03-14 21:30 | 70.36 | 67.28
2019-03-14 22:00 | 66.23 | 62.85
2019-03-14 22:30 | 58.57 | 57.56
2019-03-14 23:00 | 58.09 | 57.71
2019-03-14 23:30 | 53.63 | 53.2
2019-03-15 | 50.87 | 50.42
2019-03-15 00:30 | 49.01 | 48.52
2019-03-15 01:00 | 47.18 | 46.67
2019-03-15 01:30 | 46.25 | 45.73
2019-03-15 02:00 | 45.07 | 44.53
2019-03-15 02:30 | 44.17 | 43.63
2019-03-15 03:00 | 43.36 | 42.78
2019-03-15 03:30 | 42.94 | 42.32
2019-03-15 04:00 | 43.01 | 42.39
2019-03-15 04:30 | 43.63 | 43.02
2019-03-15 05:00 | 44.62 | 44.01
2019-03-15 05:30 | 47.12 | 46.54
2019-03-15 06:00 | 50.34 | 49.77
2019-03-15 06:30 | 56.71 | 55.79
2019-03-15 07:00 | 61.46 | 60.76
2019-03-15 07:30 | 67 | 66.41
2019-03-15 08:00 | 68.76 | 68.31
2019-03-15 08:30 | 72.45 | 71.61
2019-03-15 09:00 | 73.81 | 72.8
2019-03-15 09:30 | 74.75 | 73.53
2019-03-15 10:00 | 74.93 | 73.62
2019-03-15 10:30 | 76.23 | 74.45
2019-03-15 11:00 | 78.18 | 75.79
2019-03-15 11:30 | 79.33 | 76.98
2019-03-15 12:00 | 80.14 | 77.8
2019-03-15 12:30 | 79.54 | 77.13
2019-03-15 13:00 | 80.19 | 77.83
2019-03-15 13:30 | 78.76 | 76.37
2019-03-15 14:00 | 79.44 | 77.04
2019-03-15 14:30 | 77.82 | 75.34
2019-03-15 15:00 | 75.39 | 72.78
2019-03-15 15:30 | 75.02 | 72.35
2019-03-15 16:00 | 75.86 | 73.2
2019-03-15 16:30 | 76.43 | 73.75
2019-03-15 17:00 | 76.32 | 73.58
2019-03-15 17:30 | 74.78 | 71.9
2019-03-15 18:00 | 72.65 | 69.91
2019-03-15 18:30 | 68.21 | 67.85
2019-03-15 19:00 | 69.09 | 68.75
2019-03-15 19:30 | 68.3 | 67.95
2019-03-15 20:00 | 66.08 | 65.7
2019-03-15 20:30 | 63.35 | 62.95
2019-03-15 21:00 | 60.96 | 60.54
2019-03-15 21:30 | 58.6 | 58.15
2019-03-15 22:00 | 55.74 | 55.25
2019-03-15 22:30 | 52.78 | 52.25
2019-03-15 23:00 | 52.57 | 52.03
2019-03-15 23:30 | 48.44 | 47.93
2019-03-16 | 46.11 | 45.6
2019-03-16 00:30 | 44.07 | 43.54
2019-03-16 01:00 | 42.78 | 42.22
2019-03-16 01:30 | 42.09 | 41.52
2019-03-16 02:00 | 40.6 | 40.55
2019-03-16 02:30 | 39.96 | 39.96
2019-03-16 03:00 | 39.26 | 39.26
2019-03-16 03:30 | 39 | 39
2019-03-16 04:00 | 38.66 | 38.66
2019-03-16 04:30 | 39 | 39
2019-03-16 05:00 | 38.68 | 38.68
2019-03-16 05:30 | 39.65 | 39.64
2019-03-16 06:00 | 40.26 | 40.26
2019-03-16 06:30 | 42.15 | 42.14
2019-03-16 07:00 | 44.07 | 44.03
2019-03-16 07:30 | 45.5 | 45.37
2019-03-16 08:00 | 47.58 | 47.3
2019-03-16 08:30 | 50.8 | 50.32
2019-03-16 09:00 | 53.36 | 52.72
2019-03-16 09:30 | 53.8 | 52.97
2019-03-16 10:00 | 54.42 | 53.45
2019-03-16 10:30 | 53.58 | 52.5
2019-03-16 11:00 | 54.63 | 53.51
2019-03-16 11:30 | 54.8 | 53.63
2019-03-16 12:00 | 54.02 | 52.87
2019-03-16 12:30 | 54.73 | 53.71
2019-03-16 13:00 | 56.17 | 55.24
2019-03-16 13:30 | 54.92 | 54.07
2019-03-16 14:00 | 54.5 | 53.69
2019-03-16 14:30 | 55.84 | 55.08
2019-03-16 15:00 | 57.74 | 57.06
2019-03-16 15:30 | 56.05 | 55.46
2019-03-16 16:00 | 54.86 | 54.36
2019-03-16 16:30 | 55.48 | 55.06
2019-03-16 17:00 | 56.72 | 56.37
2019-03-16 17:30 | 58.05 | 57.77
2019-03-16 18:00 | 58.07 | 57.85
2019-03-16 18:30 | 57.75 | 57.56
2019-03-16 19:00 | 59.05 | 58.8
2019-03-16 19:30 | 58.19 | 57.94
2019-03-16 20:00 | 56.89 | 56.67
2019-03-16 20:30 | 54.79 | 54.61
2019-03-16 21:00 | 52.85 | 52.7
2019-03-16 21:30 | 51.21 | 51.1
2019-03-16 22:00 | 49.16 | 49.09
2019-03-16 22:30 | 47.28 | 47.23
2019-03-16 23:00 | 47.39 | 47.36
2019-03-16 23:30 | 43.79 | 43.79
2019-03-17 | 41.83 | 41.83
2019-03-17 00:30 | 40.37 | 40.37
2019-03-17 01:00 | 39.03 | 39.02
2019-03-17 01:30 | 38.33 | 38.32
2019-03-17 02:00 | 37.85 | 37.83
2019-03-17 02:30 | 37.23 | 37.21
2019-03-17 03:00 | 36.34 | 36.3
2019-03-17 03:30 | 36.1 | 36
2019-03-17 04:00 | 35.86 | 35.77
2019-03-17 04:30 | 35.63 | 35.53
2019-03-17 05:00 | 35.64 | 35.54
2019-03-17 05:30 | 36.13 | 36.04
2019-03-17 06:00 | 36.41 | 36.32
2019-03-17 06:30 | 37.85 | 37.75
2019-03-17 07:00 | 39.47 | 39.34
2019-03-17 07:30 | 41.84 | 41.63
2019-03-17 08:00 | 42.31 | 42
2019-03-17 08:30 | 43.2 | 42.76
2019-03-17 09:00 | 44.02 | 43.52
2019-03-17 09:30 | 46.93 | 46.71
2019-03-17 10:00 | 48.29 | 48.02
2019-03-17 10:30 | 48.97 | 48.61
2019-03-17 11:00 | 48.52 | 48.11
2019-03-17 11:30 | 48.47 | 48.03
2019-03-17 12:00 | 49.6 | 49.13
2019-03-17 12:30 | 50.4 | 49.92
2019-03-17 13:00 | 49.68 | 49.18
2019-03-17 13:30 | 49.98 | 49.48
2019-03-17 14:00 | 51.88 | 51.41
2019-03-17 14:30 | 51.04 | 50.63
2019-03-17 15:00 | 51.57 | 51.14
2019-03-17 15:30 | 52.36 | 52.01
2019-03-17 16:00 | 54.18 | 53.84
2019-03-17 16:30 | 55.93 | 55.64
2019-03-17 17:00 | 57.06 | 56.82
2019-03-17 17:30 | 57.97 | 57.76
2019-03-17 18:00 | 59.43 | 59.24
2019-03-17 18:30 | 60.66 | 60.47
2019-03-17 19:00 | 62.4 | 62.16
2019-03-17 19:30 | 61.58 | 61.37
2019-03-17 20:00 | 59.01 | 58.83
2019-03-17 20:30 | 56.2 | 56.07
2019-03-17 21:00 | 53.76 | 53.67
2019-03-17 21:30 | 51.31 | 51.25
2019-03-17 22:00 | 48.57 | 48.54
2019-03-17 22:30 | 46.05 | 46.04
2019-03-17 23:00 | 46.13 | 46.13
2019-03-17 23:30 | 42.3 | 42.3
2019-03-18 | 40.27 | 40.26
2019-03-18 00:30 | 38.92 | 38.9
2019-03-18 01:00 | 38.02 | 38
2019-03-18 01:30 | 37.52 | 37.49
2019-03-18 02:00 | 37.06 | 37.03
2019-03-18 02:30 | 36.44 | 36.29
2019-03-18 03:00 | 36.3 | 35.61
2019-03-18 03:30 | 36.4 | 35.69
2019-03-18 04:00 | 36.73 | 36.02
2019-03-18 04:30 | 37.86 | 37.17
2019-03-18 05:00 | 39.08 | 38.41
2019-03-18 05:30 | 41.82 | 41.18
2019-03-18 06:00 | 44.9 | 44.28
2019-03-18 06:30 | 50.86 | 49.99
2019-03-18 07:00 | 55.68 | 55.08
2019-03-18 07:30 | 62.13 | 61.32
2019-03-18 08:00 | 65.02 | 63.97
2019-03-18 08:30 | 66.38 | 65.43
2019-03-18 09:00 | 67.93 | 66.88
2019-03-18 09:30 | 69.38 | 68.15
2019-03-18 10:00 | 69.25 | 67.93
2019-03-18 10:30 | 70.21 | 68.8
2019-03-18 11:00 | 70.89 | 69.25
2019-03-18 11:30 | 72.55 | 70.77
2019-03-18 12:00 | 74.19 | 72.43
2019-03-18 12:30 | 77.99 | 75.85
2019-03-18 13:00 | 74.55 | 71.96
2019-03-18 13:30 | 75.06 | 72.5
2019-03-18 14:00 | 75.57 | 73.04
2019-03-18 14:30 | 75.94 | 73.41
2019-03-18 15:00 | 79.02 | 76.6
2019-03-18 15:30 | 78.01 | 75.52
2019-03-18 16:00 | 77.42 | 74.87
2019-03-18 16:30 | 75.79 | 73.09
2019-03-18 17:00 | 76 | 73.25
2019-03-18 17:30 | 74.71 | 71.85
2019-03-18 18:00 | 72.79 | 69.87
2019-03-18 18:30 | 72.18 | 69.22
2019-03-18 19:00 | 73.25 | 70.48
2019-03-18 19:30 | 72.18 | 69.33
2019-03-18 20:00 | 69.63 | 66.61
2019-03-18 20:30 | 66.56 | 63.32
2019-03-18 21:00 | 63.7 | 60.24
2019-03-18 21:30 | 61.24 | 57.57
2019-03-18 22:00 | 56.71 | 54.2
2019-03-18 22:30 | 51.47 | 51.04
2019-03-18 23:00 | 51.17 | 50.73
2019-03-18 23:30 | 46.76 | 46.26
2019-03-19 | 44.34 | 43.8
2019-03-19 00:30 | 42.84 | 42.28
2019-03-19 01:00 | 41.52 | 40.93
2019-03-19 01:30 | 40.74 | 40.14
2019-03-19 02:00 | 39.91 | 39.29
2019-03-19 02:30 | 39.13 | 38.46
2019-03-19 03:00 | 38.4 | 37.71
2019-03-19 03:30 | 38.15 | 37.45
2019-03-19 04:00 | 38.31 | 37.62
2019-03-19 04:30 | 39.27 | 38.6
2019-03-19 05:00 | 40.53 | 39.87
2019-03-19 05:30 | 43.28 | 42.65
2019-03-19 06:00 | 45.77 | 45.16
2019-03-19 06:30 | 51.15 | 50.47
2019-03-19 07:00 | 55.59 | 54.96
2019-03-19 07:30 | 62.27 | 61.46
2019-03-19 08:00 | 64.65 | 63.66
2019-03-19 08:30 | 66.8 | 65.34
2019-03-19 09:00 | 69.66 | 67.84
2019-03-19 09:30 | 70.66 | 68.92
2019-03-19 10:00 | 71.35 | 69.91
2019-03-19 10:30 | 70.97 | 69.39
2019-03-19 11:00 | 71.34 | 69.65
2019-03-19 11:30 | 72.5 | 70.73
2019-03-19 12:00 | 73.42 | 71.64
2019-03-19 12:30 | 75.2 | 73.45
2019-03-19 13:00 | 74.08 | 72.36
2019-03-19 13:30 | 74.47 | 72.71
2019-03-19 14:00 | 75.41 | 73.61
2019-03-19 14:30 | 65.27 | 62.65
2019-03-19 15:00 | 77.21 | 75.51
2019-03-19 15:30 | 79.11 | 77.59
2019-03-19 16:00 | 80.47 | 79.22
2019-03-19 16:30 | 79.34 | 78.32
2019-03-19 17:00 | 77.79 | 76.71
2019-03-19 17:30 | 74.36 | 73.17
2019-03-19 18:00 | 73.81 | 72.62
2019-03-19 18:30 | 73.35 | 72.25
2019-03-19 19:00 | 74.45 | 73.38
2019-03-19 19:30 | 73.07 | 71.96
2019-03-19 20:00 | 70.35 | 69.17
2019-03-19 20:30 | 66.94 | 65.66
2019-03-19 21:00 | 64.04 | 62.65
2019-03-19 21:30 | 61.05 | 59.54
2019-03-19 22:00 | 57.73 | 56.1
2019-03-19 22:30 | 54.48 | 52.7
2019-03-19 23:00 | 53.83 | 52
2019-03-19 23:30 | 47.94 | 47.11
2019-03-20 | 44.39 | 44.37
2019-03-20 00:30 | 42.97 | 42.96
2019-03-20 01:00 | 41.35 | 41.34
2019-03-20 01:30 | 40.31 | 40.31
2019-03-20 02:00 | 39.86 | 39.86
2019-03-20 02:30 | 39.02 | 39.02
2019-03-20 03:00 | 38.58 | 38.58
2019-03-20 03:30 | 38.27 | 38.14
2019-03-20 04:00 | 38.41 | 38.24
2019-03-20 04:30 | 39.2 | 39
2019-03-20 05:00 | 40.25 | 40.02
2019-03-20 05:30 | 43.09 | 42.77
2019-03-20 06:00 | 45.99 | 45.51
2019-03-20 06:30 | 51.63 | 51
2019-03-20 07:00 | 56.15 | 55.57
2019-03-20 07:30 | 62.28 | 61.7
2019-03-20 08:00 | 66.49 | 65.42
2019-03-20 08:30 | 68.67 | 66.98
2019-03-20 09:00 | 71.38 | 69.32
2019-03-20 09:30 | 72.39 | 70.2
2019-03-20 10:00 | 71.87 | 69.6
2019-03-20 10:30 | 72.32 | 69.83
2019-03-20 11:00 | 74.26 | 71.47
2019-03-20 11:30 | 75.79 | 71.96
2019-03-20 12:00 | 77.08 | 72.54
2019-03-20 12:30 | 78.26 | 73.82
2019-03-20 13:00 | 78.42 | 73.98
2019-03-20 13:30 | 79.36 | 75.01
2019-03-20 14:00 | 79.92 | 75.6
2019-03-20 14:30 | 81.29 | 77.05
2019-03-20 15:00 | 81.81 | 77.59
2019-03-20 15:30 | 82.1 | 77.86
2019-03-20 16:00 | 83.16 | 78.93
2019-03-20 16:30 | 83.03 | 78.7
2019-03-20 17:00 | 82.57 | 78.12
2019-03-20 17:30 | 80.6 | 75.87
2019-03-20 18:00 | 79.26 | 74.29
2019-03-20 18:30 | 77.67 | 72.46
2019-03-20 19:00 | 78.35 | 73.4
2019-03-20 19:30 | 76.74 | 71.67
2019-03-20 20:00 | 74.07 | 68.71
2019-03-20 20:30 | 71 | 65.26
2019-03-20 21:00 | 66.5 | 62.19
2019-03-20 21:30 | 60.73 | 59.2
2019-03-20 22:00 | 57.27 | 55.6
2019-03-20 22:30 | 53.93 | 52.12
2019-03-20 23:00 | 53.88 | 52.05
2019-03-20 23:30 | 49.63 | 47.59
2019-03-21 | 45.48 | 44.8
2019-03-21 00:30 | 43.29 | 43.28
2019-03-21 01:00 | 41.73 | 41.73
2019-03-21 01:30 | 40.96 | 40.96
2019-03-21 02:00 | 40 | 40
2019-03-21 02:30 | 39.3 | 39.29
2019-03-21 03:00 | 38.42 | 38.41
2019-03-21 03:30 | 37.98 | 37.86
2019-03-21 04:00 | 38.11 | 37.97
2019-03-21 04:30 | 39.1 | 38.94
2019-03-21 05:00 | 40.16 | 39.96
2019-03-21 05:30 | 42.95 | 42.65
2019-03-21 06:00 | 45.72 | 45.27
2019-03-21 06:30 | 51.17 | 50.43
2019-03-21 07:00 | 55.83 | 55.23
2019-03-21 07:30 | 62.8 | 61.99
2019-03-21 08:00 | 66.88 | 65.63
2019-03-21 08:30 | 72.13 | 70.4
2019-03-21 09:00 | 73.54 | 71.59
2019-03-21 09:30 | 74.74 | 72.6
2019-03-21 10:00 | 74.45 | 72.28
2019-03-21 10:30 | 74.36 | 72.15
2019-03-21 11:00 | 75.36 | 72.81
2019-03-21 11:30 | 73.95 | 71.31
2019-03-21 12:00 | 75.59 | 72.85
2019-03-21 12:30 | 78.17 | 75.63
2019-03-21 13:00 | 75.42 | 72.88
2019-03-21 13:30 | 77.19 | 74.58
2019-03-21 14:00 | 77.91 | 75.42
2019-03-21 14:30 | 76.88 | 74.33
2019-03-21 15:00 | 79.85 | 77.5
2019-03-21 15:30 | 78.35 | 75.99
2019-03-21 16:00 | 78.38 | 75.99
2019-03-21 16:30 | 77.32 | 74.82
2019-03-21 17:00 | 75 | 72.32
2019-03-21 17:30 | 72.63 | 69.76
2019-03-21 18:00 | 71.72 | 68.73
2019-03-21 18:30 | 71.82 | 68.84
2019-03-21 19:00 | 72.74 | 69.95
2019-03-21 19:30 | 71.5 | 68.63
2019-03-21 20:00 | 69.91 | 66.93
2019-03-21 20:30 | 67.39 | 64.22
2019-03-21 21:00 | 64.57 | 61.19
2019-03-21 21:30 | 61.65 | 58.02
2019-03-21 22:00 | 58.84 | 54.95
2019-03-21 22:30 | 51.82 | 50.83
2019-03-21 23:00 | 50.93 | 50.48
2019-03-21 23:30 | 46.79 | 46.29
2019-03-22 | 45.07 | 44.54
2019-03-22 00:30 | 43.55 | 42.99
2019-03-22 01:00 | 42.63 | 42.05
2019-03-22 01:30 | 41.67 | 41.08
2019-03-22 02:00 | 41.22 | 40.61
2019-03-22 02:30 | 40.23 | 39.65
2019-03-22 03:00 | 39.6 | 39
2019-03-22 03:30 | 39.22 | 38.59
2019-03-22 04:00 | 39.45 | 38.79
2019-03-22 04:30 | 40.19 | 39.54
2019-03-22 05:00 | 41.42 | 40.78
2019-03-22 05:30 | 44.22 | 43.61
2019-03-22 06:00 | 47.36 | 46.73
2019-03-22 06:30 | 52.85 | 52.08
2019-03-22 07:00 | 57.67 | 56.93
2019-03-22 07:30 | 63.91 | 63.1
2019-03-22 08:00 | 67.52 | 66.47
2019-03-22 08:30 | 69.44 | 67.97
2019-03-22 09:00 | 71.77 | 69.37
2019-03-22 09:30 | 75.5 | 73
2019-03-22 10:00 | 74.59 | 72.02
2019-03-22 10:30 | 73.05 | 70.45
2019-03-22 11:00 | 73.26 | 70.69
2019-03-22 11:30 | 72.54 | 69.97
2019-03-22 12:00 | 72.68 | 70.14
2019-03-22 12:30 | 72.59 | 70.02
2019-03-22 13:00 | 72.97 | 70.4
2019-03-22 13:30 | 73.88 | 71.33
2019-03-22 14:00 | 72.5 | 69.89
2019-03-22 14:30 | 72.32 | 69.68
2019-03-22 15:00 | 71.41 | 68.69
2019-03-22 15:30 | 70.59 | 67.77
2019-03-22 16:00 | 71.77 | 68.97
2019-03-22 16:30 | 71.58 | 68.69
2019-03-22 17:00 | 69.34 | 66.28
2019-03-22 17:30 | 67.61 | 64.39
2019-03-22 18:00 | 67.04 | 63.71
2019-03-22 18:30 | 66.66 | 63.42
2019-03-22 19:00 | 67.12 | 63.96
2019-03-22 19:30 | 65.59 | 62.31
2019-03-22 20:00 | 63.54 | 60.11
2019-03-22 20:30 | 62.12 | 58.56
2019-03-22 21:00 | 60.44 | 56.73
2019-03-22 21:30 | 58.59 | 54.69
2019-03-22 22:00 | 54.34 | 52.2
2019-03-22 22:30 | 50.26 | 49.81
2019-03-22 23:00 | 50.7 | 50.25
2019-03-22 23:30 | 46.5 | 45.99
2019-03-23 | 44.39 | 43.84
2019-03-23 00:30 | 43.12 | 42.54
2019-03-23 01:00 | 41.87 | 41.27
2019-03-23 01:30 | 41.08 | 40.47
2019-03-23 02:00 | 40.61 | 39.98
2019-03-23 02:30 | 40.23 | 39.61
2019-03-23 03:00 | 38.99 | 38.4
2019-03-23 03:30 | 38.94 | 38.28
2019-03-23 04:00 | 38.65 | 37.98
2019-03-23 04:30 | 39.01 | 38.35
2019-03-23 05:00 | 39.12 | 38.46
2019-03-23 05:30 | 40.55 | 39.92
2019-03-23 06:00 | 41.51 | 40.88
2019-03-23 06:30 | 43.37 | 42.76
2019-03-23 07:00 | 44.23 | 43.62
2019-03-23 07:30 | 46.8 | 46.2
2019-03-23 08:00 | 49.39 | 48.84
2019-03-23 08:30 | 52.17 | 51.65
2019-03-23 09:00 | 55.99 | 55.39
2019-03-23 09:30 | 54.77 | 53.99
2019-03-23 10:00 | 55.74 | 54.88
2019-03-23 10:30 | 56.36 | 55.43
2019-03-23 11:00 | 55.32 | 54.31
2019-03-23 11:30 | 55.01 | 54.2
2019-03-23 12:00 | 57.49 | 56.48
2019-03-23 12:30 | 56.2 | 55.35
2019-03-23 13:00 | 54.74 | 53.9
2019-03-23 13:30 | 54.9 | 54.26
2019-03-23 14:00 | 53.17 | 52.45
2019-03-23 14:30 | 54.07 | 53.41
2019-03-23 15:00 | 54.49 | 53.89
2019-03-23 15:30 | 57.25 | 56.73
2019-03-23 16:00 | 58.6 | 58.12
2019-03-23 16:30 | 59.29 | 58.9
2019-03-23 17:00 | 60.88 | 60.54
2019-03-23 17:30 | 59.38 | 59.03
2019-03-23 18:00 | 59.8 | 59.45
2019-03-23 18:30 | 60.34 | 59.99
2019-03-23 19:00 | 60.87 | 60.52
2019-03-23 19:30 | 59.63 | 59.28
2019-03-23 20:00 | 57.94 | 57.57
2019-03-23 20:30 | 56.15 | 55.76
2019-03-23 21:00 | 54.9 | 54.49
2019-03-23 21:30 | 52.85 | 52.41
2019-03-23 22:00 | 50.95 | 50.49
2019-03-23 22:30 | 48.82 | 48.33
2019-03-23 23:00 | 49.27 | 48.78
2019-03-23 23:30 | 45.27 | 44.72
2019-03-24 | 43.41 | 42.83
2019-03-24 00:30 | 41.88 | 41.28
2019-03-24 01:00 | 40.58 | 40.01
2019-03-24 01:30 | 40.06 | 39.48
2019-03-24 02:00 | 39.22 | 38.63
2019-03-24 02:30 | 36.28 | 36.05
2019-03-24 03:00 | 35.44 | 35.38
2019-03-24 03:30 | 35.44 | 35.4
2019-03-24 04:00 | 35.48 | 35.31
2019-03-24 04:30 | 36.11 | 35.4
2019-03-24 05:00 | 35.98 | 35.27
2019-03-24 05:30 | 36.24 | 35.54
2019-03-24 06:00 | 36.63 | 35.94
2019-03-24 06:30 | 37.37 | 36.69
2019-03-24 07:00 | 38.05 | 37.38
2019-03-24 07:30 | 40.39 | 39.75
2019-03-24 08:00 | 42.94 | 42.32
2019-03-24 08:30 | 43.86 | 43.23
2019-03-24 09:00 | 45.18 | 44.6
2019-03-24 09:30 | 46.59 | 46.03
2019-03-24 10:00 | 47.31 | 46.75
2019-03-24 10:30 | 48.1 | 47.55
2019-03-24 11:00 | 47.85 | 47.29
2019-03-24 11:30 | 47.86 | 47.3
2019-03-24 12:00 | 48.52 | 47.97
2019-03-24 12:30 | 49.94 | 49.4
2019-03-24 13:00 | 50.24 | 49.71
2019-03-24 13:30 | 50.76 | 50.23
2019-03-24 14:00 | 53.25 | 52.75
2019-03-24 14:30 | 56.28 | 55.82
2019-03-24 15:00 | 55.78 | 55.31
2019-03-24 15:30 | 56.47 | 56.02
2019-03-24 16:00 | 56.54 | 56.09
2019-03-24 16:30 | 56.92 | 56.48
2019-03-24 17:00 | 58.26 | 57.82
2019-03-24 17:30 | 58.67 | 58.25
2019-03-24 18:00 | 60.5 | 60.09
2019-03-24 18:30 | 62.63 | 62.25
2019-03-24 19:00 | 62.92 | 62.6
2019-03-24 19:30 | 59.95 | 59.6
2019-03-24 20:00 | 57.35 | 56.97
2019-03-24 20:30 | 54.99 | 54.59
2019-03-24 21:00 | 52.67 | 52.24
2019-03-24 21:30 | 50.43 | 49.96
2019-03-24 22:00 | 47.65 | 47.14
2019-03-24 22:30 | 44.95 | 44.39
2019-03-24 23:00 | 45.53 | 44.97
2019-03-24 23:30 | 41.69 | 41.11
2019-03-25 | 39.79 | 39.21
2019-03-25 00:30 | 38.75 | 38.16
2019-03-25 01:00 | 37.49 | 36.88
2019-03-25 01:30 | 36.92 | 36.29
2019-03-25 02:00 | 36.41 | 35.78
2019-03-25 02:30 | 35.72 | 35.01
2019-03-25 03:00 | 35.24 | 34.52
2019-03-25 03:30 | 35.13 | 34.41
2019-03-25 04:00 | 35.3 | 34.58
2019-03-25 04:30 | 36.29 | 35.59
2019-03-25 05:00 | 37.28 | 36.59
2019-03-25 05:30 | 39.93 | 39.27
2019-03-25 06:00 | 42.87 | 42.24
2019-03-25 06:30 | 48.64 | 47.91
2019-03-25 07:00 | 53.91 | 53.31
2019-03-25 07:30 | 59.31 | 58.69
2019-03-25 08:00 | 63.33 | 62.36
2019-03-25 08:30 | 64.03 | 62.72
2019-03-25 09:00 | 65.41 | 63.78
2019-03-25 09:30 | 67.46 | 65.59
2019-03-25 10:00 | 67 | 65.01
2019-03-25 10:30 | 68.47 | 66.26
2019-03-25 11:00 | 70.53 | 67.82
2019-03-25 11:30 | 70.91 | 68.14
2019-03-25 12:00 | 71.46 | 68.76
2019-03-25 12:30 | 72.78 | 70.14
2019-03-25 13:00 | 73.1 | 70.47
2019-03-25 13:30 | 74.16 | 71.59
2019-03-25 14:00 | 75 | 72.47
2019-03-25 14:30 | 74.76 | 72.22
2019-03-25 15:00 | 75.56 | 73.04
2019-03-25 15:30 | 76.48 | 73.95
2019-03-25 16:00 | 77.43 | 74.92
2019-03-25 16:30 | 77.62 | 75.05
2019-03-25 17:00 | 76.79 | 74.13
2019-03-25 17:30 | 74.27 | 71.37
2019-03-25 18:00 | 72.83 | 69.79
2019-03-25 18:30 | 71.05 | 67.85
2019-03-25 19:00 | 72.18 | 69.04
2019-03-25 19:30 | 70.65 | 67.38
2019-03-25 20:00 | 68.32 | 64.87
2019-03-25 20:30 | 62.46 | 61.47
2019-03-25 21:00 | 59.24 | 58.79
2019-03-25 21:30 | 55.89 | 55.4
2019-03-25 22:00 | 52.94 | 52.42
2019-03-25 22:30 | 49.48 | 49.07
2019-03-25 23:00 | 49.28 | 48.87
2019-03-25 23:30 | 45.21 | 44.72
2019-03-26 | 42.98 | 42.47
2019-03-26 00:30 | 41.36 | 40.84
2019-03-26 01:00 | 40.28 | 39.74
2019-03-26 01:30 | 39.66 | 39.11
2019-03-26 02:00 | 39.01 | 38.46
2019-03-26 02:30 | 37.65 | 37.08
2019-03-26 03:00 | 36.93 | 36.36
2019-03-26 03:30 | 37.11 | 36.5
2019-03-26 04:00 | 37.07 | 36.44
2019-03-26 04:30 | 37.59 | 36.95
2019-03-26 05:00 | 38.53 | 37.91
2019-03-26 05:30 | 40.79 | 40.18
2019-03-26 06:00 | 43.13 | 42.55
2019-03-26 06:30 | 48.48 | 47.93
2019-03-26 07:00 | 53.44 | 52.8
2019-03-26 07:30 | 59.95 | 59.3
2019-03-26 08:00 | 63.72 | 62.62
2019-03-26 08:30 | 66 | 64.41
2019-03-26 09:00 | 67.89 | 66
2019-03-26 09:30 | 68.86 | 66.75
2019-03-26 10:00 | 68.65 | 66.48
2019-03-26 10:30 | 70.79 | 68.16
2019-03-26 11:00 | 71.78 | 69.07
2019-03-26 11:30 | 72.09 | 69.41
2019-03-26 12:00 | 72.81 | 70.17
2019-03-26 12:30 | 73.28 | 70.67
2019-03-26 13:00 | 73.18 | 70.55
2019-03-26 13:30 | 73.94 | 71.37
2019-03-26 14:00 | 74.53 | 71.98
2019-03-26 14:30 | 75.13 | 72.6
2019-03-26 15:00 | 75.82 | 73.32
2019-03-26 15:30 | 76.15 | 73.63
2019-03-26 16:00 | 77.46 | 74.97
2019-03-26 16:30 | 77.54 | 74.98
2019-03-26 17:00 | 77.23 | 74.59
2019-03-26 17:30 | 74.95 | 72.12
2019-03-26 18:00 | 73.48 | 70.5
2019-03-26 18:30 | 72.86 | 69.79
2019-03-26 19:00 | 73.77 | 70.75
2019-03-26 19:30 | 72.2 | 69.06
2019-03-26 20:00 | 69.65 | 66.32
2019-03-26 20:30 | 66.68 | 63.11
2019-03-26 21:00 | 63.76 | 60.33
2019-03-26 21:30 | 58.27 | 57.82
2019-03-26 22:00 | 55.31 | 54.82
2019-03-26 22:30 | 52.42 | 51.89
2019-03-26 23:00 | 52.13 | 51.62
2019-03-26 23:30 | 47.92 | 47.5
2019-03-27 | 45.74 | 45.3
2019-03-27 00:30 | 44.1 | 43.58
2019-03-27 01:00 | 43.16 | 42.61
2019-03-27 01:30 | 42.45 | 41.82
2019-03-27 02:00 | 41.54 | 40.96
2019-03-27 02:30 | 40.52 | 40
2019-03-27 03:00 | 40.06 | 39.53
2019-03-27 03:30 | 40.15 | 39.62
2019-03-27 04:00 | 40.04 | 39.51
2019-03-27 04:30 | 40.85 | 40.32
2019-03-27 05:00 | 41.74 | 41.22
2019-03-27 05:30 | 44.61 | 44.11
2019-03-27 06:00 | 47.1 | 46.62
2019-03-27 06:30 | 52.36 | 51.89
2019-03-27 07:00 | 56.73 | 56.28
2019-03-27 07:30 | 63.43 | 62.66
2019-03-27 08:00 | 67.46 | 66.11
2019-03-27 08:30 | 72.96 | 70.43
2019-03-27 09:00 | 73.93 | 71.42
2019-03-27 09:30 | 73.52 | 71.02
2019-03-27 10:00 | 75.67 | 73.26
2019-03-27 10:30 | 73.73 | 71.23
2019-03-27 11:00 | 75.1 | 72.57
2019-03-27 11:30 | 74.89 | 72.38
2019-03-27 12:00 | 75.05 | 72.54
2019-03-27 12:30 | 77.88 | 75.47
2019-03-27 13:00 | 77.1 | 74.67
2019-03-27 13:30 | 78.78 | 76.41
2019-03-27 14:00 | 79.68 | 77.32
2019-03-27 14:30 | 77.99 | 75.54
2019-03-27 15:00 | 76.91 | 74.41
2019-03-27 15:30 | 75.96 | 73.36
2019-03-27 16:00 | 74.85 | 72.16
2019-03-27 16:30 | 73.49 | 70.67
2019-03-27 17:00 | 72.42 | 69.48
2019-03-27 17:30 | 70.31 | 67.17
2019-03-27 18:00 | 69.02 | 65.73
2019-03-27 18:30 | 68.26 | 64.88
2019-03-27 19:00 | 68.82 | 65.47
2019-03-27 19:30 | 67.06 | 63.57
2019-03-27 20:00 | 65.1 | 61.45
2019-03-27 20:30 | 59.09 | 58.02
2019-03-27 21:00 | 55.9 | 55.42
2019-03-27 21:30 | 53.43 | 52.91
2019-03-27 22:00 | 51.22 | 50.67
2019-03-27 22:30 | 48.53 | 48.02
2019-03-27 23:00 | 48.21 | 47.78
2019-03-27 23:30 | 44.77 | 44.29
2019-03-28 | 42.66 | 42.16
2019-03-28 00:30 | 41.31 | 40.8
2019-03-28 01:00 | 40.22 | 39.69
2019-03-28 01:30 | 39.4 | 38.87
2019-03-28 02:00 | 38.85 | 38.31
2019-03-28 02:30 | 38.06 | 37.51
2019-03-28 03:00 | 37.3 | 36.75
2019-03-28 03:30 | 37.11 | 36.56
2019-03-28 04:00 | 37.46 | 36.91
2019-03-28 04:30 | 37.8 | 37.25
2019-03-28 05:00 | 38.4 | 37.85
2019-03-28 05:30 | 40.8 | 40.27
2019-03-28 06:00 | 43.08 | 42.57
2019-03-28 06:30 | 47.86 | 47.38
2019-03-28 07:00 | 52.66 | 52.19
2019-03-28 07:30 | 58.95 | 58.48
2019-03-28 08:00 | 61.41 | 60.49
2019-03-28 08:30 | 63.45 | 62.31
2019-03-28 09:00 | 65.84 | 64.55
2019-03-28 09:30 | 64.89 | 63.53
2019-03-28 10:00 | 65.49 | 64.16
2019-03-28 10:30 | 65.32 | 64.21
2019-03-28 11:00 | 65 | 64.58
2019-03-28 11:30 | 63.42 | 63
2019-03-28 12:00 | 62.17 | 61.75
2019-03-28 12:30 | 64.07 | 63.66
2019-03-28 13:00 | 63.71 | 63.29
2019-03-28 13:30 | 63.71 | 63.3
2019-03-28 14:00 | 63.72 | 63.3
2019-03-28 14:30 | 65.48 | 65.08
2019-03-28 15:00 | 63.86 | 63.44
2019-03-28 15:30 | 65.29 | 64.88
2019-03-28 16:00 | 65.83 | 65.41
2019-03-28 16:30 | 65.02 | 64.56
2019-03-28 17:00 | 63.25 | 62.7
2019-03-28 17:30 | 61.7 | 60.76
2019-03-28 18:00 | 61.41 | 60.08
2019-03-28 18:30 | 62 | 60.54
2019-03-28 19:00 | 62.14 | 60.57
2019-03-28 19:30 | 60.76 | 59.05
2019-03-28 20:00 | 59.58 | 57.77
2019-03-28 20:30 | 57.88 | 55.74
2019-03-28 21:00 | 56.09 | 53.67
2019-03-28 21:30 | 53.52 | 50.5
2019-03-28 22:00 | 51.29 | 47.85
2019-03-28 22:30 | 49.09 | 45.05
2019-03-28 23:00 | 49.08 | 45.06
2019-03-28 23:30 | 45.62 | 41.25
2019-03-29 | 43.99 | 39.44
2019-03-29 00:30 | 42.7 | 38.01
2019-03-29 01:00 | 41.21 | 36.3
2019-03-29 01:30 | 40.24 | 35.18
2019-03-29 02:00 | 39.84 | 34.74
2019-03-29 02:30 | 39.28 | 34.11
2019-03-29 03:00 | 39.09 | 33.83
2019-03-29 03:30 | 38.93 | 33.53
2019-03-29 04:00 | 39.06 | 33.67
2019-03-29 04:30 | 39.55 | 34.23
2019-03-29 05:00 | 40.32 | 35.1
2019-03-29 05:30 | 42.19 | 37.21
2019-03-29 06:00 | 44.65 | 39.99
2019-03-29 06:30 | 46.43 | 45.41
2019-03-29 07:00 | 50.76 | 50.19
2019-03-29 07:30 | 56.93 | 56.38
2019-03-29 08:00 | 60.5 | 59.65
2019-03-29 08:30 | 62.29 | 61.22
2019-03-29 09:00 | 63.53 | 62.13
2019-03-29 09:30 | 64.36 | 62.96
2019-03-29 10:00 | 63.06 | 61.58
2019-03-29 10:30 | 64.39 | 62.87
2019-03-29 11:00 | 62.47 | 60.87
2019-03-29 11:30 | 61.9 | 60.35
2019-03-29 12:00 | 64.83 | 63.27
2019-03-29 12:30 | 63.21 | 61.79
2019-03-29 13:00 | 61.81 | 60.31
2019-03-29 13:30 | 63.2 | 61.74
2019-03-29 14:00 | 62.21 | 60.7
2019-03-29 14:30 | 63.82 | 62.32
2019-03-29 15:00 | 66.6 | 65.28
2019-03-29 15:30 | 62.68 | 61.35
2019-03-29 16:00 | 61.53 | 60.16
2019-03-29 16:30 | 62 | 60.61
2019-03-29 17:00 | 62.47 | 61.06
2019-03-29 17:30 | 61.36 | 59.86
2019-03-29 18:00 | 59.17 | 57.55
2019-03-29 18:30 | 57.61 | 55.9
2019-03-29 19:00 | 57.72 | 56.01
2019-03-29 19:30 | 56.12 | 54.34
2019-03-29 20:00 | 54.04 | 52.16
2019-03-29 20:30 | 51.93 | 49.99
2019-03-29 21:00 | 49.87 | 47.91
2019-03-29 21:30 | 48.21 | 46.15
2019-03-29 22:00 | 46.64 | 44.47
2019-03-29 22:30 | 44.76 | 42.46
2019-03-29 23:00 | 42.62 | 42.62
2019-03-29 23:30 | 39.58 | 39.58
2019-03-30 | 37.69 | 37.68
2019-03-30 00:30 | 36.04 | 36.01
2019-03-30 01:00 | 35.13 | 35.08
2019-03-30 01:30 | 34.27 | 34.21
2019-03-30 02:00 | 33.58 | 33.51
2019-03-30 02:30 | 33.11 | 33.02
2019-03-30 03:00 | 32.4 | 32.36
2019-03-30 03:30 | 32.03 | 32
2019-03-30 04:00 | 32.01 | 31.98
2019-03-30 04:30 | 32.24 | 32.2
2019-03-30 05:00 | 32.41 | 32.36
2019-03-30 05:30 | 33.44 | 33.36
2019-03-30 06:00 | 33.89 | 33.79
2019-03-30 06:30 | 35.41 | 35.28
2019-03-30 07:00 | 37.69 | 37.46
2019-03-30 07:30 | 41.29 | 40.84
2019-03-30 08:00 | 45.52 | 45.33
2019-03-30 08:30 | 47.39 | 47.14
2019-03-30 09:00 | 47.66 | 47.28
2019-03-30 09:30 | 47.28 | 46.81
2019-03-30 10:00 | 47.71 | 47.08
2019-03-30 10:30 | 49.77 | 49.03
2019-03-30 11:00 | 49.52 | 48.76
2019-03-30 11:30 | 49.17 | 48.35
2019-03-30 12:00 | 49.79 | 48.99
2019-03-30 12:30 | 49.01 | 48.33
2019-03-30 13:00 | 48.86 | 48.2
2019-03-30 13:30 | 49.07 | 48.4
2019-03-30 14:00 | 49.82 | 49.19
2019-03-30 14:30 | 49.92 | 49.33
2019-03-30 15:00 | 51.37 | 50.85
2019-03-30 15:30 | 50.88 | 50.4
2019-03-30 16:00 | 54.69 | 54.29
2019-03-30 16:30 | 54.92 | 54.64
2019-03-30 17:00 | 54.81 | 54.55
2019-03-30 17:30 | 54.06 | 53.89
2019-03-30 18:00 | 54.74 | 54.58
2019-03-30 18:30 | 55.18 | 55.03
2019-03-30 19:00 | 53.01 | 52.91
2019-03-30 19:30 | 50.33 | 50.26
2019-03-30 20:00 | 48.25 | 48.2
2019-03-30 20:30 | 46.43 | 46.4
2019-03-30 21:00 | 45.06 | 45.05
2019-03-30 21:30 | 43.71 | 43.7
2019-03-30 22:00 | 42.33 | 42.33
2019-03-30 22:30 | 40.71 | 40.7
2019-03-30 23:00 | 41.35 | 41.34
2019-03-30 23:30 | 37.7 | 37.67
2019-03-31 | 35.91 | 35.85
2019-03-31 00:30 | 35.11 | 35.04
2019-03-31 01:00 | 33.97 | 33.87
2019-03-31 01:30 | 33.31 | 33.21
2019-03-31 02:00 | 33.16 | 33.05
2019-03-31 02:30 | 32.75 | 32.63
2019-03-31 03:00 | 32.47 | 32.34
2019-03-31 03:30 | 32.03 | 31.99
2019-03-31 04:00 | 31.87 | 31.84
2019-03-31 04:30 | 31.96 | 31.92
2019-03-31 05:00 | 32.27 | 32.23
2019-03-31 05:30 | 32.32 | 32.27
2019-03-31 06:00 | 32.74 | 32.7
2019-03-31 06:30 | 33.56 | 33.52
2019-03-31 07:00 | 34.22 | 34.16
2019-03-31 07:30 | 36.65 | 36.52
2019-03-31 08:00 | 37.63 | 37.39
2019-03-31 08:30 | 38.45 | 38.08
2019-03-31 09:00 | 40.09 | 39.92
2019-03-31 09:30 | 46.04 | 45.9
2019-03-31 10:00 | 42.99 | 42.81
2019-03-31 10:30 | 43.2 | 42.93
2019-03-31 11:00 | 42.75 | 42.45
2019-03-31 11:30 | 41.85 | 41.54
2019-03-31 12:00 | 43.06 | 42.73
2019-03-31 12:30 | 42.73 | 42.4
2019-03-31 13:00 | 41.94 | 41.63
2019-03-31 13:30 | 42.63 | 42.31
2019-03-31 14:00 | 44.32 | 43.99
2019-03-31 14:30 | 45 | 44.75
2019-03-31 15:00 | 46.42 | 46.21
2019-03-31 15:30 | 48.85 | 48.66
2019-03-31 16:00 | 47.56 | 47.42
2019-03-31 16:30 | 48.4 | 48.29
2019-03-31 17:00 | 49.46 | 49.37
2019-03-31 17:30 | 50.05 | 50.01
2019-03-31 18:00 | 51.2 | 51.17
2019-03-31 18:30 | 52.35 | 52.31
2019-03-31 19:00 | 53.54 | 53.48
2019-03-31 19:30 | 52.02 | 51.98
2019-03-31 20:00 | 50.15 | 50.12
2019-03-31 20:30 | 48.23 | 48.22
2019-03-31 21:00 | 46.35 | 46.34
2019-03-31 21:30 | 44.29 | 44.29
2019-03-31 22:00 | 41.93 | 41.93
2019-03-31 22:30 | 39.52 | 39.5
2019-03-31 23:00 | 40.2 | 40.16
2019-03-31 23:30 | 36.85 | 36.78
2019-04-01 | 34.64 | 34.57
2019-04-01 00:30 | 33.47 | 33.45
2019-04-01 01:00 | 32.17 | 32.15
2019-04-01 01:30 | 31.31 | 31.3
2019-04-01 02:00 | 31.33 | 31.32
2019-04-01 02:30 | 31.11 | 31.1
2019-04-01 03:00 | 30.53 | 30.53
2019-04-01 03:30 | 30.29 | 30.29
2019-04-01 04:00 | 30.54 | 30.54
2019-04-01 04:30 | 31.25 | 31.24
2019-04-01 05:00 | 32.4 | 32.37
2019-04-01 05:30 | 34.77 | 34.69
2019-04-01 06:00 | 37.76 | 37.58
2019-04-01 06:30 | 42.59 | 42.14
2019-04-01 07:00 | 47.14 | 46.73
2019-04-01 07:30 | 53.22 | 52.72
2019-04-01 08:00 | 54.96 | 54.53
2019-04-01 08:30 | 56.27 | 55.5
2019-04-01 09:00 | 57.29 | 56.21
2019-04-01 09:30 | 59.68 | 58.5
2019-04-01 10:00 | 60.63 | 59.42
2019-04-01 10:30 | 60.18 | 58.84
2019-04-01 11:00 | 61.44 | 60.11
2019-04-01 11:30 | 60.92 | 59.42
2019-04-01 12:00 | 60.01 | 58.44
2019-04-01 12:30 | 61.8 | 60.25
2019-04-01 13:00 | 61.17 | 59.69
2019-04-01 13:30 | 62.66 | 61.14
2019-04-01 14:00 | 60.6 | 59.14
2019-04-01 14:30 | 60.75 | 59.16
2019-04-01 15:00 | 62.1 | 60.64
2019-04-01 15:30 | 63.74 | 62.45
2019-04-01 16:00 | 63.01 | 61.91
2019-04-01 16:30 | 62.33 | 61.6
2019-04-01 17:00 | 61.48 | 60.98
2019-04-01 17:30 | 58.91 | 58.55
2019-04-01 18:00 | 58.01 | 57.62
2019-04-01 18:30 | 57.37 | 56.96
2019-04-01 19:00 | 57.71 | 57.3
2019-04-01 19:30 | 55.49 | 55.06
2019-04-01 20:00 | 52.83 | 52.36
2019-04-01 20:30 | 50.37 | 49.86
2019-04-01 21:00 | 48.77 | 48.24
2019-04-01 21:30 | 47.21 | 46.65
2019-04-01 22:00 | 44.72 | 44.18
2019-04-01 22:30 | 42.63 | 42.05
2019-04-01 23:00 | 42.93 | 42.37
2019-04-01 23:30 | 39.57 | 38.98
2019-04-02 | 37.61 | 36.99
2019-04-02 00:30 | 36.64 | 36
2019-04-02 01:00 | 35.68 | 35.03
2019-04-02 01:30 | 34.82 | 34.15
2019-04-02 02:00 | 33.91 | 33.17
2019-04-02 02:30 | 33.57 | 32.8
2019-04-02 03:00 | 33.23 | 32.46
2019-04-02 03:30 | 33.37 | 32.6
2019-04-02 04:00 | 33.66 | 32.89
2019-04-02 04:30 | 34.14 | 33.38
2019-04-02 05:00 | 35.11 | 34.37
2019-04-02 05:30 | 37.35 | 36.64
2019-04-02 06:00 | 39.97 | 39.29
2019-04-02 06:30 | 44.6 | 43.89
2019-04-02 07:00 | 48.57 | 47.98
2019-04-02 07:30 | 53.9 | 53.26
2019-04-02 08:00 | 56.11 | 55.5
2019-04-02 08:30 | 57.18 | 56.25
2019-04-02 09:00 | 57.54 | 56.16
2019-04-02 09:30 | 57.93 | 56.33
2019-04-02 10:00 | 58.27 | 56.56
2019-04-02 10:30 | 58.76 | 56.99
2019-04-02 11:00 | 58.88 | 56.85
2019-04-02 11:30 | 58.55 | 56.46
2019-04-02 12:00 | 59.44 | 57.31
2019-04-02 12:30 | 59.88 | 57.74
2019-04-02 13:00 | 60.23 | 58.17
2019-04-02 13:30 | 59.88 | 57.75
2019-04-02 14:00 | 62.07 | 59.94
2019-04-02 14:30 | 63.9 | 61.88
2019-04-02 15:00 | 62.21 | 60.24
2019-04-02 15:30 | 63.44 | 61.73
2019-04-02 16:00 | 63.8 | 62.4
2019-04-02 16:30 | 63.01 | 61.9
2019-04-02 17:00 | 61.88 | 60.99
2019-04-02 17:30 | 60.36 | 59.89
2019-04-02 18:00 | 60.05 | 59.71
2019-04-02 18:30 | 59.34 | 58.97
2019-04-02 19:00 | 59.47 | 59.1
2019-04-02 19:30 | 57.94 | 57.55
2019-04-02 20:00 | 55.7 | 55.28
2019-04-02 20:30 | 53.38 | 52.93
2019-04-02 21:00 | 51.07 | 50.59
2019-04-02 21:30 | 49.48 | 48.98
2019-04-02 22:00 | 47.4 | 46.86
2019-04-02 22:30 | 44.8 | 44.25
2019-04-02 23:00 | 45.46 | 44.98
2019-04-02 23:30 | 42.4 | 41.88
2019-04-03 | 39.81 | 39.27
2019-04-03 00:30 | 38.23 | 37.68
2019-04-03 01:00 | 37.54 | 36.97
2019-04-03 01:30 | 36.79 | 36.21
2019-04-03 02:00 | 35.94 | 35.35
2019-04-03 02:30 | 35.3 | 34.71
2019-04-03 03:00 | 34.91 | 34.24
2019-04-03 03:30 | 34.91 | 34.24
2019-04-03 04:00 | 35.17 | 34.5
2019-04-03 04:30 | 36.06 | 35.4
2019-04-03 05:00 | 36.88 | 36.23
2019-04-03 05:30 | 38.95 | 38.33
2019-04-03 06:00 | 41.45 | 40.85
2019-04-03 06:30 | 46.09 | 45.52
2019-04-03 07:00 | 50.06 | 49.51
2019-04-03 07:30 | 55.46 | 54.74
2019-04-03 08:00 | 57.79 | 57.05
2019-04-03 08:30 | 58.7 | 57.58
2019-04-03 09:00 | 59 | 57.59
2019-04-03 09:30 | 58.89 | 57.31
2019-04-03 10:00 | 59.04 | 57.29
2019-04-03 10:30 | 59.48 | 57.55
2019-04-03 11:00 | 59.66 | 57.58
2019-04-03 11:30 | 61.17 | 58.9
2019-04-03 12:00 | 62.43 | 60.15
2019-04-03 12:30 | 63.46 | 61.24
2019-04-03 13:00 | 63.39 | 61.2
2019-04-03 13:30 | 63.65 | 61.48
2019-04-03 14:00 | 63.79 | 61.52
2019-04-03 14:30 | 65.83 | 63.69
2019-04-03 15:00 | 67.94 | 66.25
2019-04-03 15:30 | 64.41 | 62.76
2019-04-03 16:00 | 63.87 | 62.4
2019-04-03 16:30 | 64.3 | 63.21
2019-04-03 17:00 | 63.31 | 62.46
2019-04-03 17:30 | 60.84 | 60.41
2019-04-03 18:00 | 59.43 | 59.07
2019-04-03 18:30 | 59.3 | 58.92
2019-04-03 19:00 | 60.77 | 60.41
2019-04-03 19:30 | 58.79 | 58.4
2019-04-03 20:00 | 56.27 | 55.86
2019-04-03 20:30 | 53.6 | 53.14
2019-04-03 21:00 | 51.33 | 50.84
2019-04-03 21:30 | 49.31 | 48.79
2019-04-03 22:00 | 46.97 | 46.41
2019-04-03 22:30 | 44.34 | 43.84
2019-04-03 23:00 | 44.55 | 44.01
2019-04-03 23:30 | 40.87 | 40.28
2019-04-04 | 38.79 | 38.18
2019-04-04 00:30 | 37.8 | 37.17
2019-04-04 01:00 | 36.84 | 36.2
2019-04-04 01:30 | 36.27 | 35.62
2019-04-04 02:00 | 35.19 | 34.52
2019-04-04 02:30 | 34.58 | 33.83
2019-04-04 03:00 | 34.25 | 33.49
2019-04-04 03:30 | 34.22 | 33.46
2019-04-04 04:00 | 34.26 | 33.51
2019-04-04 04:30 | 35.07 | 34.33
2019-04-04 05:00 | 35.85 | 35.12
2019-04-04 05:30 | 38.34 | 37.64
2019-04-04 06:00 | 41.54 | 40.91
2019-04-04 06:30 | 45.88 | 45.31
2019-04-04 07:00 | 50.04 | 49.45
2019-04-04 07:30 | 55.69 | 54.88
2019-04-04 08:00 | 57.09 | 56.34
2019-04-04 08:30 | 59.67 | 58.6
2019-04-04 09:00 | 59.82 | 58.65
2019-04-04 09:30 | 59.15 | 57.66
2019-04-04 10:00 | 57.59 | 55.88
2019-04-04 10:30 | 57.93 | 56.02
2019-04-04 11:00 | 60.1 | 58.06
2019-04-04 11:30 | 60.41 | 58.35
2019-04-04 12:00 | 60.69 | 58.56
2019-04-04 12:30 | 61.39 | 59.33
2019-04-04 13:00 | 62.67 | 60.7
2019-04-04 13:30 | 65.11 | 63.17
2019-04-04 14:00 | 64.63 | 62.6
2019-04-04 14:30 | 61.8 | 59.74
2019-04-04 15:00 | 62.28 | 60.33
2019-04-04 15:30 | 63.13 | 61.41
2019-04-04 16:00 | 62.78 | 61.36
2019-04-04 16:30 | 63.24 | 62.17
2019-04-04 17:00 | 62.75 | 62.01
2019-04-04 17:30 | 60.22 | 59.82
2019-04-04 18:00 | 59.96 | 59.61
2019-04-04 18:30 | 60.56 | 60.2
2019-04-04 19:00 | 61.09 | 60.73
2019-04-04 19:30 | 58.11 | 57.72
2019-04-04 20:00 | 55.51 | 55.08
2019-04-04 20:30 | 52.53 | 52.07
2019-04-04 21:00 | 50.81 | 50.32
2019-04-04 21:30 | 48.51 | 47.98
2019-04-04 22:00 | 46.34 | 45.76
2019-04-04 22:30 | 43.62 | 43.11
2019-04-04 23:00 | 43.95 | 43.46
2019-04-04 23:30 | 40.65 | 40.12
2019-04-05 | 38.31 | 37.75
2019-04-05 00:30 | 36.97 | 36.4
2019-04-05 01:00 | 36.22 | 35.63
2019-04-05 01:30 | 35.6 | 34.99
2019-04-05 02:00 | 34.66 | 33.98
2019-04-05 02:30 | 34.36 | 33.68
2019-04-05 03:00 | 33.79 | 33.09
2019-04-05 03:30 | 33.63 | 32.93
2019-04-05 04:00 | 33.99 | 33.31
2019-04-05 04:30 | 34.97 | 34.29
2019-04-05 05:00 | 35.72 | 35.05
2019-04-05 05:30 | 38.06 | 37.42
2019-04-05 06:00 | 41.06 | 40.46
2019-04-05 06:30 | 45.46 | 44.89
2019-04-05 07:00 | 48.91 | 48.34
2019-04-05 07:30 | 54.08 | 53.44
2019-04-05 08:00 | 56.97 | 56.27
2019-04-05 08:30 | 57.92 | 56.94
2019-04-05 09:00 | 58.1 | 56.85
2019-04-05 09:30 | 58.94 | 57.5
2019-04-05 10:00 | 60.01 | 58.47
2019-04-05 10:30 | 59.4 | 57.61
2019-04-05 11:00 | 59.03 | 56.92
2019-04-05 11:30 | 59.22 | 57.16
2019-04-05 12:00 | 58.66 | 56.7
2019-04-05 12:30 | 59.04 | 57.18
2019-04-05 13:00 | 59.12 | 57.36
2019-04-05 13:30 | 60.89 | 59.19
2019-04-05 14:00 | 60.46 | 58.83
2019-04-05 14:30 | 61.7 | 60.34
2019-04-05 15:00 | 60.71 | 59.77
2019-04-05 15:30 | 59.16 | 58.39
2019-04-05 16:00 | 56.66 | 56.03
2019-04-05 16:30 | 56.22 | 55.75
2019-04-05 17:00 | 56.15 | 55.78
2019-04-05 17:30 | 55.14 | 54.74
2019-04-05 18:00 | 54.41 | 53.98
2019-04-05 18:30 | 54.38 | 53.94
2019-04-05 19:00 | 54.28 | 53.83
2019-04-05 19:30 | 52.45 | 51.99
2019-04-05 20:00 | 50.3 | 49.86
2019-04-05 20:30 | 48.14 | 47.66
2019-04-05 21:00 | 46.68 | 46.18
2019-04-05 21:30 | 45.04 | 44.51
2019-04-05 22:00 | 43.41 | 42.85
2019-04-05 22:30 | 41.63 | 41.02
2019-04-05 23:00 | 41.87 | 41.29
2019-04-05 23:30 | 37.79 | 37.18
2019-04-06 | 35.59 | 34.95
2019-04-06 00:30 | 34.55 | 33.84
2019-04-06 01:00 | 33.59 | 32.84
2019-04-06 01:30 | 32.83 | 32.06
2019-04-06 02:00 | 32.43 | 31.65
2019-04-06 02:30 | 32.24 | 31.46
2019-04-06 03:00 | 31.61 | 30.81
2019-04-06 03:30 | 31.5 | 30.7
2019-04-06 04:00 | 31.64 | 30.85
2019-04-06 04:30 | 32.17 | 31.39
2019-04-06 05:00 | 32.49 | 31.7
2019-04-06 05:30 | 33.3 | 32.53
2019-04-06 06:00 | 34.45 | 33.71
2019-04-06 06:30 | 36.15 | 35.43
2019-04-06 07:00 | 37.22 | 36.52
2019-04-06 07:30 | 39.49 | 38.82
2019-04-06 08:00 | 41.21 | 40.55
2019-04-06 08:30 | 44.39 | 43.79
2019-04-06 09:00 | 46.31 | 45.76
2019-04-06 09:30 | 47.16 | 46.61
2019-04-06 10:00 | 42.36 | 41.73
2019-04-06 10:30 | 41.71 | 41.05
2019-04-06 11:00 | 42.68 | 42.04
2019-04-06 11:30 | 43.54 | 42.91
2019-04-06 12:00 | 43.26 | 42.63
2019-04-06 12:30 | 41.05 | 40.39
2019-04-06 13:00 | 38.73 | 38.03
2019-04-06 13:30 | 39.25 | 38.57
2019-04-06 14:00 | 39.05 | 38.36
2019-04-06 14:30 | 39.45 | 38.77
2019-04-06 15:00 | 39.88 | 39.22
2019-04-06 15:30 | 41.76 | 41.14
2019-04-06 16:00 | 43.96 | 43.38
2019-04-06 16:30 | 44.86 | 44.31
2019-04-06 17:00 | 45 | 44.45
2019-04-06 17:30 | 44.55 | 44.01
2019-04-06 18:00 | 45.94 | 45.43
2019-04-06 18:30 | 47.16 | 46.67
2019-04-06 19:00 | 46.88 | 46.38
2019-04-06 19:30 | 44.95 | 44.43
2019-04-06 20:00 | 43.51 | 42.97
2019-04-06 20:30 | 41.93 | 41.38
2019-04-06 21:00 | 41.77 | 41.21
2019-04-06 21:30 | 40.34 | 39.76
2019-04-06 22:00 | 39.32 | 38.74
2019-04-06 22:30 | 37.88 | 37.28
2019-04-06 23:00 | 38.56 | 37.98
2019-04-06 23:30 | 35.76 | 35.13
2019-04-07 | 34.11 | 33.45
2019-04-07 00:30 | 33.37 | 32.68
2019-04-07 01:00 | 32.43 | 31.66
2019-04-07 01:30 | 31.67 | 30.89
2019-04-07 02:00 | 31.5 | 30.71
2019-04-07 02:30 | 31.08 | 30.27
2019-04-07 03:00 | 30.43 | 29.61
2019-04-07 03:30 | 30.27 | 29.46
2019-04-07 04:00 | 29.98 | 29.16
2019-04-07 04:30 | 30.2 | 29.39
2019-04-07 05:00 | 30.51 | 29.7
2019-04-07 05:30 | 30.54 | 29.73
2019-04-07 06:00 | 31.24 | 30.44
2019-04-07 06:30 | 31.83 | 31.05
2019-04-07 07:00 | 32.21 | 31.44
2019-04-07 07:30 | 34.42 | 33.7
2019-04-07 08:00 | 35.57 | 34.85
2019-04-07 08:30 | 37.32 | 36.65
2019-04-07 09:00 | 35.42 | 34.66
2019-04-07 09:30 | 35.91 | 35.14
2019-04-07 10:00 | 40.49 | 39.87
2019-04-07 10:30 | 41.18 | 40.57
2019-04-07 11:00 | 39.3 | 38.65
2019-04-07 11:30 | 37.6 | 36.92
2019-04-07 12:00 | 38.9 | 38.25
2019-04-07 12:30 | 42.95 | 42.38
2019-04-07 13:00 | 38.14 | 37.49
2019-04-07 13:30 | 35.8 | 35.09
2019-04-07 14:00 | 35.83 | 35.11
2019-04-07 14:30 | 36.24 | 35.54
2019-04-07 15:00 | 37.22 | 36.54
2019-04-07 15:30 | 38.6 | 37.95
2019-04-07 16:00 | 39.88 | 39.27
2019-04-07 16:30 | 41.33 | 40.74
2019-04-07 17:00 | 42.73 | 42.17
2019-04-07 17:30 | 43.68 | 43.15
2019-04-07 18:00 | 45.35 | 44.84
2019-04-07 18:30 | 47.87 | 47.39
2019-04-07 19:00 | 48.39 | 47.91
2019-04-07 19:30 | 46.29 | 45.8
2019-04-07 20:00 | 44.19 | 43.68
2019-04-07 20:30 | 42.44 | 41.91
2019-04-07 21:00 | 41.38 | 40.83
2019-04-07 21:30 | 40.26 | 39.69
2019-04-07 22:00 | 38.37 | 37.78
2019-04-07 22:30 | 37.05 | 36.45
2019-04-07 23:00 | 37.97 | 37.38
2019-04-07 23:30 | 34.67 | 34.03
2019-04-08 | 32.78 | 32.1
2019-04-08 00:30 | 32.17 | 31.42
2019-04-08 01:00 | 31.24 | 30.45
2019-04-08 01:30 | 30.52 | 29.71
2019-04-08 02:00 | 30.2 | 29.38
2019-04-08 02:30 | 29.61 | 28.78
2019-04-08 03:00 | 29.4 | 28.56
2019-04-08 03:30 | 29.17 | 28.33
2019-04-08 04:00 | 29.52 | 28.69
2019-04-08 04:30 | 30.08 | 29.26
2019-04-08 05:00 | 30.92 | 30.12
2019-04-08 05:30 | 33.36 | 32.61
2019-04-08 06:00 | 35.96 | 35.25
2019-04-08 06:30 | 40.19 | 39.52
2019-04-08 07:00 | 43.86 | 43.19
2019-04-08 07:30 | 48.01 | 47.37
2019-04-08 08:00 | 50.6 | 50.04
2019-04-08 08:30 | 52.98 | 52.38
2019-04-08 09:00 | 54.57 | 53.71
2019-04-08 09:30 | 54.89 | 53.88
2019-04-08 10:00 | 54.55 | 53.44
2019-04-08 10:30 | 55.59 | 54.23
2019-04-08 11:00 | 56.67 | 55.02
2019-04-08 11:30 | 57.93 | 56.2
2019-04-08 12:00 | 58.51 | 56.79
2019-04-08 12:30 | 57.11 | 56.03
2019-04-08 13:00 | 55.77 | 55
2019-04-08 13:30 | 56.28 | 55.5
2019-04-08 14:00 | 56.92 | 56.15
2019-04-08 14:30 | 57.72 | 56.96
2019-04-08 15:00 | 58.05 | 57.38
2019-04-08 15:30 | 59 | 58.38
2019-04-08 16:00 | 59.38 | 58.92
2019-04-08 16:30 | 59.32 | 58.97
2019-04-08 17:00 | 59.56 | 59.19
2019-04-08 17:30 | 57.98 | 57.56
2019-04-08 18:00 | 57.22 | 56.82
2019-04-08 18:30 | 56.95 | 56.58
2019-04-08 19:00 | 57.03 | 56.67
2019-04-08 19:30 | 54.34 | 53.95
2019-04-08 20:00 | 52.23 | 51.81
2019-04-08 20:30 | 49.74 | 49.29
2019-04-08 21:00 | 48.12 | 47.65
2019-04-08 21:30 | 45.83 | 45.32
2019-04-08 22:00 | 44.89 | 44.36
2019-04-08 22:30 | 42.71 | 42.14
2019-04-08 23:00 | 42.99 | 42.42
2019-04-08 23:30 | 39.65 | 39.02
2019-04-09 | 37.14 | 36.51
2019-04-09 00:30 | 36.07 | 35.39
2019-04-09 01:00 | 35.25 | 34.5
2019-04-09 01:30 | 34.52 | 33.76
2019-04-09 02:00 | 34.36 | 33.59
2019-04-09 02:30 | 33.61 | 32.84
2019-04-09 03:00 | 32.57 | 31.78
2019-04-09 03:30 | 32.24 | 31.44
2019-04-09 04:00 | 32.08 | 31.28
2019-04-09 04:30 | 32.88 | 32.09
2019-04-09 05:00 | 33.93 | 33.17
2019-04-09 05:30 | 35.56 | 34.83
2019-04-09 06:00 | 38.22 | 37.52
2019-04-09 06:30 | 42.49 | 41.82
2019-04-09 07:00 | 46.48 | 45.81
2019-04-09 07:30 | 51.4 | 50.75
2019-04-09 08:00 | 54.41 | 53.71
2019-04-09 08:30 | 55.82 | 55.22
2019-04-09 09:00 | 55.44 | 54.52
2019-04-09 09:30 | 56.04 | 54.89
2019-04-09 10:00 | 56.27 | 54.96
2019-04-09 10:30 | 57.41 | 56.09
2019-04-09 11:00 | 57.86 | 56.87
2019-04-09 11:30 | 57.02 | 55.98
2019-04-09 12:00 | 57.01 | 55.91
2019-04-09 12:30 | 57.42 | 56.42
2019-04-09 13:00 | 56.83 | 55.83
2019-04-09 13:30 | 57.12 | 56.16
2019-04-09 14:00 | 57.74 | 56.82
2019-04-09 14:30 | 58.4 | 57.51
2019-04-09 15:00 | 59.43 | 58.57
2019-04-09 15:30 | 59.11 | 58.42
2019-04-09 16:00 | 59.44 | 58.98
2019-04-09 16:30 | 59.55 | 59.2
2019-04-09 17:00 | 59.76 | 59.4
2019-04-09 17:30 | 57.93 | 57.52
2019-04-09 18:00 | 56.73 | 56.31
2019-04-09 18:30 | 56.83 | 56.42
2019-04-09 19:00 | 56.9 | 56.48
2019-04-09 19:30 | 54.18 | 53.74
2019-04-09 20:00 | 51.78 | 51.3
2019-04-09 20:30 | 49.52 | 49
2019-04-09 21:00 | 47.29 | 46.78
2019-04-09 21:30 | 45.42 | 44.9
2019-04-09 22:00 | 43.63 | 43.08
2019-04-09 22:30 | 41.36 | 40.76
2019-04-09 23:00 | 41.61 | 41
2019-04-09 23:30 | 37.85 | 37.25
2019-04-10 | 35.7 | 35.06
2019-04-10 00:30 | 34.84 | 34.18
2019-04-10 01:00 | 33.94 | 33.26
2019-04-10 01:30 | 32.94 | 32.23
2019-04-10 02:00 | 31.99 | 31.24
2019-04-10 02:30 | 31.26 | 30.45
2019-04-10 03:00 | 30.66 | 29.84
2019-04-10 03:30 | 30.87 | 30.04
2019-04-10 04:00 | 31.08 | 30.26
2019-04-10 04:30 | 31.64 | 30.84
2019-04-10 05:00 | 32.68 | 31.9
2019-04-10 05:30 | 34.8 | 34.07
2019-04-10 06:00 | 37.19 | 36.48
2019-04-10 06:30 | 41.27 | 40.61
2019-04-10 07:00 | 44.61 | 43.98
2019-04-10 07:30 | 47.93 | 47.34
2019-04-10 08:00 | 51.45 | 50.75
2019-04-10 08:30 | 52.55 | 51.97
2019-04-10 09:00 | 53.92 | 53.44
2019-04-10 09:30 | 53.49 | 53
2019-04-10 10:00 | 53.56 | 53.06
2019-04-10 10:30 | 54.87 | 54.23
2019-04-10 11:00 | 54.68 | 53.93
2019-04-10 11:30 | 55.62 | 54.69
2019-04-10 12:00 | 56.54 | 55.54
2019-04-10 12:30 | 56.55 | 55.65
2019-04-10 13:00 | 56.02 | 55.18
2019-04-10 13:30 | 56.59 | 55.67
2019-04-10 14:00 | 57.96 | 57
2019-04-10 14:30 | 58.59 | 57.71
2019-04-10 15:00 | 59.35 | 58.51
2019-04-10 15:30 | 59.84 | 59.16
2019-04-10 16:00 | 60.57 | 60.07
2019-04-10 16:30 | 60.02 | 59.72
2019-04-10 17:00 | 59.53 | 59.3
2019-04-10 17:30 | 57.68 | 57.44
2019-04-10 18:00 | 56.4 | 56.31
2019-04-10 18:30 | 56.53 | 56.49
2019-04-10 19:00 | 56.65 | 56.62
2019-04-10 19:30 | 53.74 | 53.73
2019-04-10 20:00 | 51.23 | 51.23
2019-04-10 20:30 | 48.99 | 48.99
2019-04-10 21:00 | 46.81 | 46.79
2019-04-10 21:30 | 44.57 | 44.51
2019-04-10 22:00 | 42.4 | 42.28
2019-04-10 22:30 | 40.29 | 40.08
2019-04-10 23:00 | 41.13 | 40.9
2019-04-10 23:30 | 37.75 | 37.43
2019-04-11 | 35.41 | 35.08
2019-04-11 00:30 | 33.87 | 33.83
2019-04-11 01:00 | 32.69 | 32.62
2019-04-11 01:30 | 32.11 | 32.03
2019-04-11 02:00 | 31.57 | 31.46
2019-04-11 02:30 | 31.04 | 30.9
2019-04-11 03:00 | 30.6 | 30.44
2019-04-11 03:30 | 30.68 | 30.53
2019-04-11 04:00 | 31.13 | 31
2019-04-11 04:30 | 31.81 | 31.7
2019-04-11 05:00 | 32.76 | 32.68
2019-04-11 05:30 | 34.64 | 34.61
2019-04-11 06:00 | 37 | 37
2019-04-11 06:30 | 41.11 | 41.06
2019-04-11 07:00 | 44.64 | 44.49
2019-04-11 07:30 | 49.32 | 48.88
2019-04-11 08:00 | 53.64 | 53.09
2019-04-11 08:30 | 57.94 | 57.46
2019-04-11 09:00 | 57.72 | 56.99
2019-04-11 09:30 | 56.27 | 55.36
2019-04-11 10:00 | 56.33 | 55.32
2019-04-11 10:30 | 57.82 | 56.62
2019-04-11 11:00 | 56.4 | 55.36
2019-04-11 11:30 | 56.37 | 55.55
2019-04-11 12:00 | 55.75 | 54.89
2019-04-11 12:30 | 61.02 | 60.3
2019-04-11 13:00 | 55.33 | 54.59
2019-04-11 13:30 | 57.38 | 56.61
2019-04-11 14:00 | 57.28 | 56.45
2019-04-11 14:30 | 58.39 | 57.62
2019-04-11 15:00 | 59.29 | 58.52
2019-04-11 15:30 | 61.72 | 61.09
2019-04-11 16:00 | 61.17 | 60.77
2019-04-11 16:30 | 58.86 | 58.65
2019-04-11 17:00 | 58.11 | 57.85
2019-04-11 17:30 | 56.65 | 56.43
2019-04-11 18:00 | 56.73 | 56.64
2019-04-11 18:30 | 57.1 | 57.03
2019-04-11 19:00 | 56.21 | 56.18
2019-04-11 19:30 | 53.45 | 53.44
2019-04-11 20:00 | 51.64 | 51.63
2019-04-11 20:30 | 49.8 | 49.8
2019-04-11 21:00 | 48.16 | 48.16
2019-04-11 21:30 | 45.54 | 45.52
2019-04-11 22:00 | 43.48 | 43.42
2019-04-11 22:30 | 41.33 | 41.2
2019-04-11 23:00 | 42.08 | 41.93
2019-04-11 23:30 | 39.04 | 38.84
2019-04-12 | 37.05 | 36.78
2019-04-12 00:30 | 36.32 | 35.95
2019-04-12 01:00 | 36.98 | 34.48
2019-04-12 01:30 | 36.18 | 33.58
2019-04-12 02:00 | 35.68 | 33.06
2019-04-12 02:30 | 35.14 | 32.47
2019-04-12 03:00 | 35.15 | 32.47
2019-04-12 03:30 | 34.81 | 32.11
2019-04-12 04:00 | 34.88 | 32.19
2019-04-12 04:30 | 35.33 | 32.68
2019-04-12 05:00 | 36.25 | 33.66
2019-04-12 05:30 | 38.64 | 36.2
2019-04-12 06:00 | 41.26 | 38.96
2019-04-12 06:30 | 44.99 | 42.85
2019-04-12 07:00 | 48.04 | 46.01
2019-04-12 07:30 | 52.81 | 51.55
2019-04-12 08:00 | 54.3 | 53.69
2019-04-12 08:30 | 56.32 | 55.5
2019-04-12 09:00 | 55.6 | 54.63
2019-04-12 09:30 | 55.05 | 53.93
2019-04-12 10:00 | 54.68 | 53.47
2019-04-12 10:30 | 54.41 | 53.03
2019-04-12 11:00 | 54.76 | 53.21
2019-04-12 11:30 | 54.49 | 52.94
2019-04-12 12:00 | 53.87 | 52.22
2019-04-12 12:30 | 53.5 | 52.05
2019-04-12 13:00 | 53.06 | 51.67
2019-04-12 13:30 | 52.97 | 51.6
2019-04-12 14:00 | 53.3 | 52
2019-04-12 14:30 | 53.49 | 52.3
2019-04-12 15:00 | 53.24 | 52.82
2019-04-12 15:30 | 53.62 | 53.41
2019-04-12 16:00 | 53.56 | 53.45
2019-04-12 16:30 | 54.19 | 54.1
2019-04-12 17:00 | 54.06 | 53.83
2019-04-12 17:30 | 52.33 | 52.27
2019-04-12 18:00 | 51.94 | 51.93
2019-04-12 18:30 | 51.97 | 51.94
2019-04-12 19:00 | 51.47 | 51.31
2019-04-12 19:30 | 49.68 | 49.56
2019-04-12 20:00 | 48.1 | 48
2019-04-12 20:30 | 46.15 | 46.08
2019-04-12 21:00 | 44.94 | 44.89
2019-04-12 21:30 | 43.52 | 43.5
2019-04-12 22:00 | 41.41 | 41.41
2019-04-12 22:30 | 40.4 | 40.4
2019-04-12 23:00 | 40.76 | 40.76
2019-04-12 23:30 | 37.09 | 37.06
2019-04-13 | 34.69 | 34.62
2019-04-13 00:30 | 33.7 | 33.65
2019-04-13 01:00 | 32.48 | 32.44
2019-04-13 01:30 | 31.92 | 31.89
2019-04-13 02:00 | 31 | 30.98
2019-04-13 02:30 | 30.38 | 30.36
2019-04-13 03:00 | 30.16 | 30.15
2019-04-13 03:30 | 29.77 | 29.77
2019-04-13 04:00 | 29.86 | 29.86
2019-04-13 04:30 | 30.24 | 30.22
2019-04-13 05:00 | 31.12 | 31.08
2019-04-13 05:30 | 31.82 | 31.78
2019-04-13 06:00 | 32.78 | 32.72
2019-04-13 06:30 | 34.41 | 34.31
2019-04-13 07:00 | 35.23 | 35.08
2019-04-13 07:30 | 38.06 | 37.76
2019-04-13 08:00 | 39.38 | 38.91
2019-04-13 08:30 | 40.9 | 40.23
2019-04-13 09:00 | 41.1 | 40.67
2019-04-13 09:30 | 40.41 | 40.15
2019-04-13 10:00 | 40.99 | 40.64
2019-04-13 10:30 | 39.82 | 39.39
2019-04-13 11:00 | 38.73 | 38.27
2019-04-13 11:30 | 38.17 | 37.7
2019-04-13 12:00 | 37.75 | 37.3
2019-04-13 12:30 | 38.76 | 38.42
2019-04-13 13:00 | 38.62 | 38.33
2019-04-13 13:30 | 36.5 | 36.21
2019-04-13 14:00 | 37.58 | 37.32
2019-04-13 14:30 | 36.95 | 36.72
2019-04-13 15:00 | 37.99 | 37.8
2019-04-13 15:30 | 39.45 | 39.34
2019-04-13 16:00 | 41.37 | 41.28
2019-04-13 16:30 | 41.29 | 41.24
2019-04-13 17:00 | 42.31 | 42.29
2019-04-13 17:30 | 43.07 | 43.06
2019-04-13 18:00 | 44.95 | 44.94
2019-04-13 18:30 | 46.32 | 46.31
2019-04-13 19:00 | 46.09 | 46.08
2019-04-13 19:30 | 44.19 | 44.19
2019-04-13 20:00 | 42.78 | 42.78
2019-04-13 20:30 | 41.58 | 41.58
2019-04-13 21:00 | 40.21 | 40.2
2019-04-13 21:30 | 38.77 | 38.75
2019-04-13 22:00 | 37.62 | 37.59
2019-04-13 22:30 | 36.36 | 36.3
2019-04-13 23:00 | 37.25 | 37.16
2019-04-13 23:30 | 33.95 | 33.88
2019-04-14 | 32.18 | 32.17
2019-04-14 00:30 | 31.53 | 31.52
2019-04-14 01:00 | 30.82 | 30.81
2019-04-14 01:30 | 30.4 | 30.4
2019-04-14 02:00 | 30.07 | 30.07
2019-04-14 02:30 | 29.76 | 29.75
2019-04-14 03:00 | 29.31 | 29.31
2019-04-14 03:30 | 29.2 | 29.2
2019-04-14 04:00 | 29.67 | 29.67
2019-04-14 04:30 | 29.78 | 29.78
2019-04-14 05:00 | 29.94 | 29.94
2019-04-14 05:30 | 30.37 | 30.36
2019-04-14 06:00 | 31.24 | 31.23
2019-04-14 06:30 | 31.43 | 31.43
2019-04-14 07:00 | 32.07 | 32.06
2019-04-14 07:30 | 33.23 | 33.19
2019-04-14 08:00 | 34.38 | 34.28
2019-04-14 08:30 | 35.33 | 35.19
2019-04-14 09:00 | 36.04 | 35.81
2019-04-14 09:30 | 36.31 | 36.03
2019-04-14 10:00 | 36.35 | 35.94
2019-04-14 10:30 | 34.91 | 34.51
2019-04-14 11:00 | 33.17 | 33.1
2019-04-14 11:30 | 32.69 | 32.58
2019-04-14 12:00 | 32.25 | 32.15
2019-04-14 12:30 | 32.96 | 32.88
2019-04-14 13:00 | 32.55 | 32.47
2019-04-14 13:30 | 33.22 | 33.14
2019-04-14 14:00 | 33.94 | 33.88
2019-04-14 14:30 | 33.9 | 33.87
2019-04-14 15:00 | 34.44 | 34.41
2019-04-14 15:30 | 35.78 | 35.76
2019-04-14 16:00 | 37.46 | 37.45
2019-04-14 16:30 | 39.74 | 39.73
2019-04-14 17:00 | 41.24 | 41.24
2019-04-14 17:30 | 42.28 | 42.28
2019-04-14 18:00 | 43.97 | 43.97
2019-04-14 18:30 | 46.26 | 46.26
2019-04-14 19:00 | 46.29 | 46.29
2019-04-14 19:30 | 44.69 | 44.69
2019-04-14 20:00 | 43.03 | 43.03
2019-04-14 20:30 | 41.39 | 41.38
2019-04-14 21:00 | 40 | 39.98
2019-04-14 21:30 | 38.63 | 38.59
2019-04-14 22:00 | 36.9 | 36.84
2019-04-14 22:30 | 35.38 | 35.29
2019-04-14 23:00 | 36.57 | 36.46
2019-04-14 23:30 | 33.71 | 33.55
2019-04-15 | 31.88 | 31.78
2019-04-15 00:30 | 30.96 | 30.96
2019-04-15 01:00 | 30.32 | 30.32
2019-04-15 01:30 | 29.78 | 29.77
2019-04-15 02:00 | 29.41 | 29.41
2019-04-15 02:30 | 29.28 | 29.28
2019-04-15 03:00 | 28.61 | 28.61
2019-04-15 03:30 | 28.61 | 28.61
2019-04-15 04:00 | 28.93 | 28.93
2019-04-15 04:30 | 29.83 | 29.83
2019-04-15 05:00 | 30.86 | 30.85
2019-04-15 05:30 | 32.99 | 32.95
2019-04-15 06:00 | 35.83 | 35.71
2019-04-15 06:30 | 41.21 | 40.81
2019-04-15 07:00 | 45.28 | 44.72
2019-04-15 07:30 | 49.83 | 49.3
2019-04-15 08:00 | 51.56 | 51.21
2019-04-15 08:30 | 55.47 | 55.01
2019-04-15 09:00 | 55.69 | 55.09
2019-04-15 09:30 | 53.05 | 52.24
2019-04-15 10:00 | 52.44 | 51.44
2019-04-15 10:30 | 53.67 | 52.46
2019-04-15 11:00 | 53.77 | 52.46
2019-04-15 11:30 | 54.25 | 52.8
2019-04-15 12:00 | 54.17 | 52.68
2019-04-15 12:30 | 55.32 | 53.9
2019-04-15 13:00 | 53.95 | 52.49
2019-04-15 13:30 | 54.39 | 53.35
2019-04-15 14:00 | 55.23 | 54.52
2019-04-15 14:30 | 56.65 | 55.96
2019-04-15 15:00 | 56.55 | 55.95
2019-04-15 15:30 | 56.32 | 55.81
2019-04-15 16:00 | 55.95 | 55.61
2019-04-15 16:30 | 56.95 | 56.76
2019-04-15 17:00 | 56.67 | 56.59
2019-04-15 17:30 | 55.8 | 55.79
2019-04-15 18:00 | 54.96 | 54.94
2019-04-15 18:30 | 54.83 | 54.82
2019-04-15 19:00 | 54.8 | 54.79
2019-04-15 19:30 | 51.86 | 51.86
2019-04-15 20:00 | 49.75 | 49.75
2019-04-15 20:30 | 47.52 | 47.5
2019-04-15 21:00 | 45.43 | 45.37
2019-04-15 21:30 | 43.58 | 43.49
2019-04-15 22:00 | 42.05 | 41.91
2019-04-15 22:30 | 40.41 | 40.21
2019-04-15 23:00 | 41.34 | 41.11
2019-04-15 23:30 | 37.84 | 37.59
2019-04-16 | 35.33 | 35.3
2019-04-16 00:30 | 33.63 | 33.56
2019-04-16 01:00 | 32.84 | 32.77
2019-04-16 01:30 | 32.24 | 32.18
2019-04-16 02:00 | 31.46 | 31.41
2019-04-16 02:30 | 31.19 | 31.15
2019-04-16 03:00 | 30.51 | 30.49
2019-04-16 03:30 | 30.33 | 30.31
2019-04-16 04:00 | 30.29 | 30.28
2019-04-16 04:30 | 31.34 | 31.32
2019-04-16 05:00 | 32.9 | 32.85
2019-04-16 05:30 | 35.06 | 34.96
2019-04-16 06:00 | 37.83 | 37.62
2019-04-16 06:30 | 42.53 | 42.02
2019-04-16 07:00 | 45.78 | 45.31
2019-04-16 07:30 | 50.27 | 49.66
2019-04-16 08:00 | 53.11 | 52.64
2019-04-16 08:30 | 54.85 | 54.18
2019-04-16 09:00 | 55.7 | 54.85
2019-04-16 09:30 | 55.85 | 54.87
2019-04-16 10:00 | 54.53 | 53.45
2019-04-16 10:30 | 54.91 | 53.69
2019-04-16 11:00 | 55.38 | 53.98
2019-04-16 11:30 | 55.42 | 53.87
2019-04-16 12:00 | 54.62 | 53
2019-04-16 12:30 | 54.45 | 52.9
2019-04-16 13:00 | 53.32 | 51.84
2019-04-16 13:30 | 53.92 | 52.97
2019-04-16 14:00 | 53 | 52.39
2019-04-16 14:30 | 54.38 | 53.83
2019-04-16 15:00 | 54.88 | 54.36
2019-04-16 15:30 | 55.47 | 54.99
2019-04-16 16:00 | 57.44 | 57.04
2019-04-16 16:30 | 57.89 | 57.69
2019-04-16 17:00 | 57.34 | 57.27
2019-04-16 17:30 | 55.34 | 55.34
2019-04-16 18:00 | 54.96 | 54.94
2019-04-16 18:30 | 55.35 | 55.29
2019-04-16 19:00 | 55.17 | 55.09
2019-04-16 19:30 | 52.32 | 52.25
2019-04-16 20:00 | 50.28 | 50.28
2019-04-16 20:30 | 47.75 | 47.73
2019-04-16 21:00 | 46.11 | 46.07
2019-04-16 21:30 | 44.11 | 44.04
2019-04-16 22:00 | 42.22 | 42.08
2019-04-16 22:30 | 40.36 | 40.16
2019-04-16 23:00 | 40.84 | 40.65
2019-04-16 23:30 | 37.06 | 37.04
2019-04-17 | 35.08 | 35.02
2019-04-17 00:30 | 34.02 | 33.95
2019-04-17 01:00 | 32.66 | 32.6
2019-04-17 01:30 | 32.17 | 32.12
2019-04-17 02:00 | 31.69 | 31.64
2019-04-17 02:30 | 31.14 | 31.11
2019-04-17 03:00 | 30.55 | 30.54
2019-04-17 03:30 | 30.25 | 30.23
2019-04-17 04:00 | 30.52 | 30.5
2019-04-17 04:30 | 31.36 | 31.33
2019-04-17 05:00 | 32.11 | 32.08
2019-04-17 05:30 | 34.63 | 34.52
2019-04-17 06:00 | 37.21 | 37.03
2019-04-17 06:30 | 41.25 | 40.87
2019-04-17 07:00 | 45.33 | 44.88
2019-04-17 07:30 | 49.54 | 49.03
2019-04-17 08:00 | 51.57 | 51.24
2019-04-17 08:30 | 53.7 | 53.13
2019-04-17 09:00 | 54.36 | 53.55
2019-04-17 09:30 | 54.31 | 53.41
2019-04-17 10:00 | 54.13 | 53.2
2019-04-17 10:30 | 54.21 | 53.1
2019-04-17 11:00 | 53.76 | 52.62
2019-04-17 11:30 | 54.44 | 53.27
2019-04-17 12:00 | 54.05 | 53.27
2019-04-17 12:30 | 54.06 | 53.36
2019-04-17 13:00 | 53.67 | 53
2019-04-17 13:30 | 53.95 | 53.28
2019-04-17 14:00 | 54.12 | 53.5
2019-04-17 14:30 | 54.54 | 53.93
2019-04-17 15:00 | 55.43 | 54.85
2019-04-17 15:30 | 56.19 | 55.73
2019-04-17 16:00 | 56.36 | 56.04
2019-04-17 16:30 | 56.62 | 56.47
2019-04-17 17:00 | 56.41 | 56.36
2019-04-17 17:30 | 55.28 | 55.28
2019-04-17 18:00 | 54.45 | 54.42
2019-04-17 18:30 | 54.04 | 54.01
2019-04-17 19:00 | 53.65 | 53.65
2019-04-17 19:30 | 51.1 | 51.09
2019-04-17 20:00 | 49.34 | 49.33
2019-04-17 20:30 | 47.42 | 47.39
2019-04-17 21:00 | 45.38 | 45.33
2019-04-17 21:30 | 44.06 | 43.97
2019-04-17 22:00 | 42.37 | 42.23
2019-04-17 22:30 | 40.47 | 40.25
2019-04-17 23:00 | 40.77 | 40.51
2019-04-17 23:30 | 37.48 | 37.3
2019-04-18 | 34.77 | 34.69
2019-04-18 00:30 | 33.74 | 33.69
2019-04-18 01:00 | 32.67 | 32.63
2019-04-18 01:30 | 31.61 | 31.58
2019-04-18 02:00 | 31.13 | 31.11
2019-04-18 02:30 | 30.49 | 30.49
2019-04-18 03:00 | 29.89 | 29.89
2019-04-18 03:30 | 29.74 | 29.74
2019-04-18 04:00 | 29.65 | 29.65
2019-04-18 04:30 | 30.33 | 30.33
2019-04-18 05:00 | 31.48 | 31.47
2019-04-18 05:30 | 33.95 | 33.89
2019-04-18 06:00 | 36.84 | 36.7
2019-04-18 06:30 | 40.87 | 40.55
2019-04-18 07:00 | 45.25 | 44.79
2019-04-18 07:30 | 49.42 | 48.98
2019-04-18 08:00 | 51.08 | 50.71
2019-04-18 08:30 | 52.78 | 52.33
2019-04-18 09:00 | 53.09 | 52.45
2019-04-18 09:30 | 52.5 | 51.72
2019-04-18 10:00 | 52.4 | 51.58
2019-04-18 10:30 | 52.62 | 51.59
2019-04-18 11:00 | 52.82 | 51.65
2019-04-18 11:30 | 52.88 | 51.63
2019-04-18 12:00 | 52.75 | 51.48
2019-04-18 12:30 | 52.75 | 51.49
2019-04-18 13:00 | 52.27 | 51.06
2019-04-18 13:30 | 52.77 | 51.6
2019-04-18 14:00 | 53.04 | 51.92
2019-04-18 14:30 | 53.63 | 52.55
2019-04-18 15:00 | 53.96 | 53.04
2019-04-18 15:30 | 54.25 | 53.5
2019-04-18 16:00 | 54.72 | 54.13
2019-04-18 16:30 | 55.62 | 55.21
2019-04-18 17:00 | 54.78 | 54.59
2019-04-18 17:30 | 52.07 | 52.03
2019-04-18 18:00 | 51.86 | 51.86
2019-04-18 18:30 | 52.55 | 52.54
2019-04-18 19:00 | 52.31 | 52.31
2019-04-18 19:30 | 49.63 | 49.61
2019-04-18 20:00 | 48.29 | 48.26
2019-04-18 20:30 | 46.54 | 46.48
2019-04-18 21:00 | 45.11 | 45.02
2019-04-18 21:30 | 43.09 | 42.93
2019-04-18 22:00 | 41.24 | 41.02
2019-04-18 22:30 | 39.29 | 38.94
2019-04-18 23:00 | 39.6 | 39.17
2019-04-18 23:30 | 36.04 | 35.76
2019-04-19 | 33.45 | 33.43
2019-04-19 00:30 | 32.16 | 32.16
2019-04-19 01:00 | 31.11 | 31.11
2019-04-19 01:30 | 30.28 | 30.28
2019-04-19 02:00 | 29.85 | 29.85
2019-04-19 02:30 | 29.39 | 29.39
2019-04-19 03:00 | 29.11 | 29.11
2019-04-19 03:30 | 28.96 | 28.96
2019-04-19 04:00 | 28.47 | 28.47
2019-04-19 04:30 | 28.57 | 28.57
2019-04-19 05:00 | 28.69 | 28.69
2019-04-19 05:30 | 29.27 | 29.27
2019-04-19 06:00 | 30.1 | 30.1
2019-04-19 06:30 | 30.77 | 30.76
2019-04-19 07:00 | 31.7 | 31.69
2019-04-19 07:30 | 32.83 | 32.79
2019-04-19 08:00 | 33.27 | 33.17
2019-04-19 08:30 | 33.01 | 32.84
2019-04-19 09:00 | 32.66 | 32.42
2019-04-19 09:30 | 32.17 | 31.84
2019-04-19 10:00 | 32.23 | 31.83
2019-04-19 10:30 | 32.01 | 31.57
2019-04-19 11:00 | 30.91 | 30.45
2019-04-19 11:30 | 30.64 | 30.12
2019-04-19 12:00 | 30.5 | 29.94
2019-04-19 12:30 | 31.31 | 30.79
2019-04-19 13:00 | 30.5 | 29.95
2019-04-19 13:30 | 30.31 | 29.75
2019-04-19 14:00 | 30.78 | 30.25
2019-04-19 14:30 | 31.79 | 31.27
2019-04-19 15:00 | 32.35 | 31.88
2019-04-19 15:30 | 33.67 | 33.25
2019-04-19 16:00 | 35.56 | 35.19
2019-04-19 16:30 | 37.58 | 37.25
2019-04-19 17:00 | 38.77 | 38.49
2019-04-19 17:30 | 39.82 | 39.63
2019-04-19 18:00 | 41.27 | 41.1
2019-04-19 18:30 | 43.35 | 43.16
2019-04-19 19:00 | 43.11 | 42.94
2019-04-19 19:30 | 41.36 | 41.21
2019-04-19 20:00 | 39.79 | 39.66
2019-04-19 20:30 | 38.12 | 38.04
2019-04-19 21:00 | 36.63 | 36.57
2019-04-19 21:30 | 35.72 | 35.67
2019-04-19 22:00 | 35.13 | 35.09
2019-04-19 22:30 | 34.14 | 34.12
2019-04-19 23:00 | 35.46 | 35.44
2019-04-19 23:30 | 32.6 | 32.59
2019-04-20 | 31.05 | 31.04
2019-04-20 00:30 | 30.31 | 30.31
2019-04-20 01:00 | 29.27 | 29.27
2019-04-20 01:30 | 28.92 | 28.92
2019-04-20 02:00 | 28.51 | 28.51
2019-04-20 02:30 | 28.3 | 28.3
2019-04-20 03:00 | 27.64 | 27.64
2019-04-20 03:30 | 28.1 | 28.1
2019-04-20 04:00 | 27.74 | 27.73
2019-04-20 04:30 | 28.08 | 28.08
2019-04-20 05:00 | 28.61 | 28.61
2019-04-20 05:30 | 29.27 | 29.27
2019-04-20 06:00 | 29.62 | 29.62
2019-04-20 06:30 | 30.33 | 30.33
2019-04-20 07:00 | 30.91 | 30.9
2019-04-20 07:30 | 32.54 | 32.51
2019-04-20 08:00 | 33.54 | 33.45
2019-04-20 08:30 | 34.73 | 34.53
2019-04-20 09:00 | 34.53 | 34.23
2019-04-20 09:30 | 34.96 | 34.6
2019-04-20 10:00 | 33.66 | 33.62
2019-04-20 10:30 | 33.11 | 33.06
2019-04-20 11:00 | 32.35 | 32.28
2019-04-20 11:30 | 32.33 | 32.23
2019-04-20 12:00 | 32.73 | 32.62
2019-04-20 12:30 | 33.31 | 33.21
2019-04-20 13:00 | 32.58 | 32.47
2019-04-20 13:30 | 33 | 32.9
2019-04-20 14:00 | 34.32 | 34.24
2019-04-20 14:30 | 35.01 | 34.94
2019-04-20 15:00 | 35.28 | 35.22
2019-04-20 15:30 | 37.19 | 37.16
2019-04-20 16:00 | 37.57 | 37.55
2019-04-20 16:30 | 39.71 | 39.7
2019-04-20 17:00 | 41.48 | 41.47
2019-04-20 17:30 | 41.93 | 41.93
2019-04-20 18:00 | 43.15 | 43.15
2019-04-20 18:30 | 44.48 | 44.48
2019-04-20 19:00 | 43.69 | 43.69
2019-04-20 19:30 | 42.21 | 42.21
2019-04-20 20:00 | 41.22 | 41.22
2019-04-20 20:30 | 40.05 | 40.04
2019-04-20 21:00 | 38.96 | 38.94
2019-04-20 21:30 | 37.86 | 37.82
2019-04-20 22:00 | 37.32 | 37.28
2019-04-20 22:30 | 36.35 | 36.3
2019-04-20 23:00 | 37.55 | 37.5
2019-04-20 23:30 | 34.89 | 34.79
2019-04-21 | 32.93 | 32.77
2019-04-21 00:30 | 32.42 | 32.25
2019-04-21 01:00 | 30.99 | 30.75
2019-04-21 01:30 | 30.55 | 30.52
2019-04-21 02:00 | 30.18 | 30.18
2019-04-21 02:30 | 29.54 | 29.54
2019-04-21 03:00 | 29.31 | 29.31
2019-04-21 03:30 | 28.71 | 28.71
2019-04-21 04:00 | 28.41 | 28.41
2019-04-21 04:30 | 28.74 | 28.73
2019-04-21 05:00 | 28.72 | 28.72
2019-04-21 05:30 | 29.09 | 29.09
2019-04-21 06:00 | 29.72 | 29.72
2019-04-21 06:30 | 30.11 | 30.11
2019-04-21 07:00 | 30.65 | 30.65
2019-04-21 07:30 | 32.13 | 32.12
2019-04-21 08:00 | 34.33 | 34.27
2019-04-21 08:30 | 34.99 | 34.91
2019-04-21 09:00 | 36.17 | 36.03
2019-04-21 09:30 | 37.19 | 37.02
2019-04-21 10:00 | 37.91 | 37.7
2019-04-21 10:30 | 37.56 | 37.31
2019-04-21 11:00 | 36.89 | 36.64
2019-04-21 11:30 | 35.23 | 34.94
2019-04-21 12:00 | 33.02 | 32.7
2019-04-21 12:30 | 32.45 | 32.44
2019-04-21 13:00 | 34.88 | 34.87
2019-04-21 13:30 | 37.84 | 37.84
2019-04-21 14:00 | 38.36 | 38.36
2019-04-21 14:30 | 35.87 | 35.87
2019-04-21 15:00 | 36.11 | 36.11
2019-04-21 15:30 | 34.75 | 34.75
2019-04-21 16:00 | 37.45 | 37.45
2019-04-21 16:30 | 38.91 | 38.91
2019-04-21 17:00 | 39.24 | 39.24
2019-04-21 17:30 | 40.35 | 40.34
2019-04-21 18:00 | 41.48 | 41.47
2019-04-21 18:30 | 43.6 | 43.6
2019-04-21 19:00 | 43.42 | 43.42
2019-04-21 19:30 | 41.97 | 41.96
2019-04-21 20:00 | 40.52 | 40.51
2019-04-21 20:30 | 39.41 | 39.38
2019-04-21 21:00 | 38.3 | 38.26
2019-04-21 21:30 | 37.08 | 37.01
2019-04-21 22:00 | 36.02 | 35.91
2019-04-21 22:30 | 35.06 | 34.93
2019-04-21 23:00 | 36.49 | 36.37
2019-04-21 23:30 | 34.03 | 33.87
2019-04-22 | 32.36 | 32.16
2019-04-22 00:30 | 31.11 | 31.08
2019-04-22 01:00 | 30.43 | 30.43
2019-04-22 01:30 | 29.82 | 29.82
2019-04-22 02:00 | 29.36 | 29.36
2019-04-22 02:30 | 29.12 | 29.12
2019-04-22 03:00 | 28.78 | 28.78
2019-04-22 03:30 | 28.83 | 28.83
2019-04-22 04:00 | 28.97 | 28.97
2019-04-22 04:30 | 29.47 | 29.47
2019-04-22 05:00 | 29.47 | 29.47
2019-04-22 05:30 | 30.3 | 30.29
2019-04-22 06:00 | 31.43 | 31.41
2019-04-22 06:30 | 33.28 | 33.23
2019-04-22 07:00 | 34.25 | 34.2
2019-04-22 07:30 | 35.78 | 35.66
2019-04-22 08:00 | 38.67 | 38.46
2019-04-22 08:30 | 38.77 | 38.5
2019-04-22 09:00 | 39.75 | 39.4
2019-04-22 09:30 | 40.7 | 40.39
2019-04-22 10:00 | 37.31 | 36.99
2019-04-22 10:30 | 41.07 | 41.01
2019-04-22 11:00 | 41.68 | 41.62
2019-04-22 11:30 | 43.33 | 43.27
2019-04-22 12:00 | 42.98 | 42.93
2019-04-22 12:30 | 42.97 | 42.91
2019-04-22 13:00 | 43.87 | 43.81
2019-04-22 13:30 | 42.82 | 42.79
2019-04-22 14:00 | 42.29 | 42.28
2019-04-22 14:30 | 39.93 | 39.91
2019-04-22 15:00 | 42.24 | 42.23
2019-04-22 15:30 | 41.6 | 41.6
2019-04-22 16:00 | 42.1 | 42.09
2019-04-22 16:30 | 43.26 | 43.25
2019-04-22 17:00 | 43.51 | 43.51
2019-04-22 17:30 | 44.93 | 44.93
2019-04-22 18:00 | 47.56 | 47.55
2019-04-22 18:30 | 47.23 | 47.23
2019-04-22 19:00 | 45.74 | 45.74
2019-04-22 19:30 | 43.11 | 43.09
2019-04-22 20:00 | 41.6 | 41.58
2019-04-22 20:30 | 40.08 | 40.03
2019-04-22 21:00 | 38.93 | 38.87
2019-04-22 21:30 | 37.26 | 37.18
2019-04-22 22:00 | 35.66 | 35.53
2019-04-22 22:30 | 34.12 | 34.05
2019-04-22 23:00 | 35.15 | 35.15
2019-04-22 23:30 | 32.85 | 32.85
2019-04-23 | 31.24 | 31.24
2019-04-23 00:30 | 30.48 | 30.48
2019-04-23 01:00 | 29.64 | 29.64
2019-04-23 01:30 | 29.21 | 29.21
2019-04-23 02:00 | 28.66 | 28.66
2019-04-23 02:30 | 28.42 | 28.42
2019-04-23 03:00 | 28.54 | 28.54
2019-04-23 03:30 | 28.63 | 28.63
2019-04-23 04:00 | 28.67 | 28.67
2019-04-23 04:30 | 29.67 | 29.67
2019-04-23 05:00 | 30.9 | 30.89
2019-04-23 05:30 | 33.43 | 33.38
2019-04-23 06:00 | 35.93 | 35.81
2019-04-23 06:30 | 41.52 | 41.15
2019-04-23 07:00 | 47.06 | 46.35
2019-04-23 07:30 | 52.94 | 52.3
2019-04-23 08:00 | 55.02 | 54.72
2019-04-23 08:30 | 55.96 | 55.64
2019-04-23 09:00 | 56.45 | 55.97
2019-04-23 09:30 | 57.74 | 57.19
2019-04-23 10:00 | 55.74 | 55.15
2019-04-23 10:30 | 55.45 | 54.64
2019-04-23 11:00 | 56.73 | 55.78
2019-04-23 11:30 | 61.13 | 60.21
2019-04-23 12:00 | 61.57 | 60.78
2019-04-23 12:30 | 61.33 | 60.63
2019-04-23 13:00 | 59.69 | 58.97
2019-04-23 13:30 | 58.37 | 57.56
2019-04-23 14:00 | 59.86 | 59.01
2019-04-23 14:30 | 60.22 | 59.41
2019-04-23 15:00 | 58.33 | 57.57
2019-04-23 15:30 | 58.23 | 57.54
2019-04-23 16:00 | 58.44 | 57.89
2019-04-23 16:30 | 57.87 | 57.51
2019-04-23 17:00 | 55.88 | 55.68
2019-04-23 17:30 | 54.66 | 54.6
2019-04-23 18:00 | 54.82 | 54.81
2019-04-23 18:30 | 54.92 | 54.92
2019-04-23 19:00 | 53.65 | 53.64
2019-04-23 19:30 | 51.21 | 51.21
2019-04-23 20:00 | 49.14 | 49.12
2019-04-23 20:30 | 47.06 | 47.03
2019-04-23 21:00 | 45.17 | 45.16
2019-04-23 21:30 | 43.09 | 43.09
2019-04-23 22:00 | 41.2 | 41.2
2019-04-23 22:30 | 38.88 | 38.87
2019-04-23 23:00 | 39.81 | 39.79
2019-04-23 23:30 | 36.8 | 36.75
2019-04-24 | 35.04 | 34.97
2019-04-24 00:30 | 33.72 | 33.68
2019-04-24 01:00 | 32.62 | 32.59
2019-04-24 01:30 | 31.85 | 31.82
2019-04-24 02:00 | 31.16 | 31.14
2019-04-24 02:30 | 31.03 | 31.02
2019-04-24 03:00 | 30.62 | 30.61
2019-04-24 03:30 | 30.92 | 30.91
2019-04-24 04:00 | 31.02 | 31
2019-04-24 04:30 | 31.68 | 31.67
2019-04-24 05:00 | 32.47 | 32.45
2019-04-24 05:30 | 34.78 | 34.71
2019-04-24 06:00 | 37.57 | 37.42
2019-04-24 06:30 | 42.78 | 42.4
2019-04-24 07:00 | 47.63 | 46.92
2019-04-24 07:30 | 54.33 | 53.75
2019-04-24 08:00 | 57.25 | 56.94
2019-04-24 08:30 | 59.63 | 59.17
2019-04-24 09:00 | 60.11 | 59.5
2019-04-24 09:30 | 59.46 | 58.76
2019-04-24 10:00 | 62.47 | 61.79
2019-04-24 10:30 | 62.67 | 62.01
2019-04-24 11:00 | 62.45 | 61.7
2019-04-24 11:30 | 61.56 | 60.71
2019-04-24 12:00 | 59.69 | 58.74
2019-04-24 12:30 | 60.66 | 59.68
2019-04-24 13:00 | 60.98 | 60.07
2019-04-24 13:30 | 62.93 | 62.12
2019-04-24 14:00 | 61.74 | 60.98
2019-04-24 14:30 | 60.53 | 59.76
2019-04-24 15:00 | 60.55 | 59.83
2019-04-24 15:30 | 59.2 | 58.6
2019-04-24 16:00 | 57.88 | 57.44
2019-04-24 16:30 | 58.01 | 57.71
2019-04-24 17:00 | 57.23 | 57.03
2019-04-24 17:30 | 55.19 | 55.14
2019-04-24 18:00 | 55.05 | 55.03
2019-04-24 18:30 | 54.23 | 54.23
2019-04-24 19:00 | 53.18 | 53.18
2019-04-24 19:30 | 50.31 | 50.29
2019-04-24 20:00 | 49.14 | 49.12
2019-04-24 20:30 | 47.41 | 47.36
2019-04-24 21:00 | 45.7 | 45.66
2019-04-24 21:30 | 43.32 | 43.31
2019-04-24 22:00 | 41.39 | 41.39
2019-04-24 22:30 | 39.66 | 39.65
2019-04-24 23:00 | 40.78 | 40.77
2019-04-24 23:30 | 37.8 | 37.77
2019-04-25 | 35.54 | 35.48
2019-04-25 00:30 | 34.14 | 34.06
2019-04-25 01:00 | 32.71 | 32.69
2019-04-25 01:30 | 32.06 | 32.04
2019-04-25 02:00 | 32.06 | 32.03
2019-04-25 02:30 | 31.82 | 31.8
2019-04-25 03:00 | 30.89 | 30.88
2019-04-25 03:30 | 30.38 | 30.38
2019-04-25 04:00 | 30.36 | 30.36
2019-04-25 04:30 | 30.6 | 30.59
2019-04-25 05:00 | 30.69 | 30.68
2019-04-25 05:30 | 31.15 | 31.14
2019-04-25 06:00 | 32.18 | 32.16
2019-04-25 06:30 | 33.66 | 33.62
2019-04-25 07:00 | 34.73 | 34.67
2019-04-25 07:30 | 36.4 | 36.28
2019-04-25 08:00 | 36.71 | 36.54
2019-04-25 08:30 | 37.14 | 36.93
2019-04-25 09:00 | 37.24 | 36.98
2019-04-25 09:30 | 37.96 | 37.67
2019-04-25 10:00 | 37.83 | 37.44
2019-04-25 10:30 | 40.28 | 39.85
2019-04-25 11:00 | 38.53 | 38.07
2019-04-25 11:30 | 37.13 | 36.55
2019-04-25 12:00 | 36.33 | 35.66
2019-04-25 12:30 | 36.69 | 36.25
2019-04-25 13:00 | 35.66 | 35.54
2019-04-25 13:30 | 36.2 | 36.06
2019-04-25 14:00 | 35.93 | 35.8
2019-04-25 14:30 | 36.8 | 36.67
2019-04-25 15:00 | 37.84 | 37.72
2019-04-25 15:30 | 39.33 | 39.24
2019-04-25 16:00 | 40.88 | 40.8
2019-04-25 16:30 | 42.84 | 42.78
2019-04-25 17:00 | 44.02 | 43.98
2019-04-25 17:30 | 45.46 | 45.44
2019-04-25 18:00 | 47.42 | 47.4
2019-04-25 18:30 | 49.71 | 49.69
2019-04-25 19:00 | 49.51 | 49.49
2019-04-25 19:30 | 47.58 | 47.57
2019-04-25 20:00 | 45.42 | 45.42
2019-04-25 20:30 | 43.3 | 43.3
2019-04-25 21:00 | 41.94 | 41.94
2019-04-25 21:30 | 40.36 | 40.33
2019-04-25 22:00 | 38.37 | 38.31
2019-04-25 22:30 | 36.64 | 36.54
2019-04-25 23:00 | 37.1 | 36.98
2019-04-25 23:30 | 34.25 | 34.08
2019-04-26 | 32.87 | 32.67
2019-04-26 00:30 | 31.68 | 31.65
2019-04-26 01:00 | 30.86 | 30.86
2019-04-26 01:30 | 30.36 | 30.36
2019-04-26 02:00 | 29.83 | 29.83
2019-04-26 02:30 | 29.4 | 29.4
2019-04-26 03:00 | 29.08 | 29.08
2019-04-26 03:30 | 29.06 | 29.06
2019-04-26 04:00 | 29.63 | 29.63
2019-04-26 04:30 | 30.72 | 30.71
2019-04-26 05:00 | 32.08 | 32.06
2019-04-26 05:30 | 34.43 | 34.36
2019-04-26 06:00 | 36.94 | 36.79
2019-04-26 06:30 | 40.98 | 40.65
2019-04-26 07:00 | 45.16 | 44.58
2019-04-26 07:30 | 50.91 | 50.32
2019-04-26 08:00 | 53.23 | 53.02
2019-04-26 08:30 | 54.59 | 54.2
2019-04-26 09:00 | 55.76 | 55.21
2019-04-26 09:30 | 56.47 | 55.82
2019-04-26 10:00 | 55.64 | 54.89
2019-04-26 10:30 | 55.81 | 54.88
2019-04-26 11:00 | 57.26 | 56.18
2019-04-26 11:30 | 57.18 | 56.04
2019-04-26 12:00 | 56.68 | 55.48
2019-04-26 12:30 | 56.93 | 55.82
2019-04-26 13:00 | 55.34 | 54.2
2019-04-26 13:30 | 55.94 | 54.85
2019-04-26 14:00 | 54.98 | 53.93
2019-04-26 14:30 | 55.48 | 54.52
2019-04-26 15:00 | 55.35 | 54.51
2019-04-26 15:30 | 56.44 | 55.75
2019-04-26 16:00 | 57.79 | 57.26
2019-04-26 16:30 | 58.26 | 57.9
2019-04-26 17:00 | 58.43 | 58.19
2019-04-26 17:30 | 57.97 | 57.86
2019-04-26 18:00 | 56.94 | 56.91
2019-04-26 18:30 | 56.7 | 56.68
2019-04-26 19:00 | 55.28 | 55.28
2019-04-26 19:30 | 53.08 | 53.08
2019-04-26 20:00 | 50.74 | 50.72
2019-04-26 20:30 | 49.06 | 49.03
2019-04-26 21:00 | 47.49 | 47.45
2019-04-26 21:30 | 45.84 | 45.81
2019-04-26 22:00 | 43.69 | 43.69
2019-04-26 22:30 | 41.71 | 41.71
2019-04-26 23:00 | 42.56 | 42.55
2019-04-26 23:30 | 38.97 | 38.94
2019-04-27 | 36.95 | 36.9
2019-04-27 00:30 | 35.89 | 35.81
2019-04-27 01:00 | 34.17 | 34.11
2019-04-27 01:30 | 33.2 | 33.17
2019-04-27 02:00 | 32.66 | 32.64
2019-04-27 02:30 | 32.07 | 32.05
2019-04-27 03:00 | 31.41 | 31.4
2019-04-27 03:30 | 31.19 | 31.18
2019-04-27 04:00 | 31.34 | 31.33
2019-04-27 04:30 | 31.53 | 31.52
2019-04-27 05:00 | 31.93 | 31.92
2019-04-27 05:30 | 32.77 | 32.75
2019-04-27 06:00 | 33.85 | 33.82
2019-04-27 06:30 | 35.91 | 35.84
2019-04-27 07:00 | 37.09 | 37
2019-04-27 07:30 | 39.56 | 39.38
2019-04-27 08:00 | 42.61 | 42.29
2019-04-27 08:30 | 44.79 | 44.32
2019-04-27 09:00 | 46.07 | 45.58
2019-04-27 09:30 | 46.53 | 46.37
2019-04-27 10:00 | 47.16 | 47.01
2019-04-27 10:30 | 47.2 | 47.03
2019-04-27 11:00 | 45.85 | 45.64
2019-04-27 11:30 | 47.21 | 47.02
2019-04-27 12:00 | 47.56 | 47.39
2019-04-27 12:30 | 47.54 | 47.43
2019-04-27 13:00 | 46.04 | 45.96
2019-04-27 13:30 | 45.42 | 45.36
2019-04-27 14:00 | 44.97 | 44.92
2019-04-27 14:30 | 44 | 43.96
2019-04-27 15:00 | 42.39 | 42.35
2019-04-27 15:30 | 42.56 | 42.55
2019-04-27 16:00 | 43.28 | 43.27
2019-04-27 16:30 | 44.18 | 44.17
2019-04-27 17:00 | 44.6 | 44.6
2019-04-27 17:30 | 45.43 | 45.43
2019-04-27 18:00 | 47.16 | 47.15
2019-04-27 18:30 | 48.55 | 48.54
2019-04-27 19:00 | 47.37 | 47.37
2019-04-27 19:30 | 45.94 | 45.94
2019-04-27 20:00 | 44.51 | 44.51
2019-04-27 20:30 | 43.03 | 43.03
2019-04-27 21:00 | 41.73 | 41.73
2019-04-27 21:30 | 40.82 | 40.82
2019-04-27 22:00 | 39.69 | 39.68
2019-04-27 22:30 | 38.04 | 38
2019-04-27 23:00 | 39.5 | 39.46
2019-04-27 23:30 | 36 | 35.91
2019-04-28 | 34.49 | 34.37
2019-04-28 00:30 | 33.29 | 33.23
2019-04-28 01:00 | 31.99 | 31.98
2019-04-28 01:30 | 31.47 | 31.46
2019-04-28 02:00 | 30.9 | 30.9
2019-04-28 02:30 | 30.49 | 30.49
2019-04-28 03:00 | 30.28 | 30.28
2019-04-28 03:30 | 29.92 | 29.92
2019-04-28 04:00 | 29.66 | 29.66
2019-04-28 04:30 | 29.99 | 29.99
2019-04-28 05:00 | 30.42 | 30.42
2019-04-28 05:30 | 30.7 | 30.7
2019-04-28 06:00 | 31.38 | 31.38
2019-04-28 06:30 | 32.21 | 32.2
2019-04-28 07:00 | 33.15 | 33.15
2019-04-28 07:30 | 34.79 | 34.78
2019-04-28 08:00 | 36.49 | 36.46
2019-04-28 08:30 | 38.12 | 38.05
2019-04-28 09:00 | 39.08 | 38.95
2019-04-28 09:30 | 40.91 | 40.7
2019-04-28 10:00 | 42.24 | 41.98
2019-04-28 10:30 | 41.9 | 41.66
2019-04-28 11:00 | 41.26 | 41.24
2019-04-28 11:30 | 35.07 | 35.03
2019-04-28 12:00 | 36.35 | 36.29
2019-04-28 12:30 | 39.2 | 39.17
2019-04-28 13:00 | 39.08 | 39.05
2019-04-28 13:30 | 40.16 | 40.14
2019-04-28 14:00 | 37.98 | 37.96
2019-04-28 14:30 | 38.26 | 38.24
2019-04-28 15:00 | 37.44 | 37.42
2019-04-28 15:30 | 38.44 | 38.42
2019-04-28 16:00 | 40.38 | 40.37
2019-04-28 16:30 | 42.34 | 42.34
2019-04-28 17:00 | 44.02 | 44.02
2019-04-28 17:30 | 45.7 | 45.7
2019-04-28 18:00 | 47.83 | 47.83
2019-04-28 18:30 | 50.87 | 50.86
2019-04-28 19:00 | 49.82 | 49.81
2019-04-28 19:30 | 47.84 | 47.84
2019-04-28 20:00 | 45.97 | 45.97
2019-04-28 20:30 | 44.24 | 44.24
2019-04-28 21:00 | 42.28 | 42.26
2019-04-28 21:30 | 40.59 | 40.55
2019-04-28 22:00 | 39.02 | 38.95
2019-04-28 22:30 | 37.05 | 36.95
2019-04-28 23:00 | 38.37 | 38.31
2019-04-28 23:30 | 34.69 | 34.68
2019-04-29 | 32.7 | 32.7
2019-04-29 00:30 | 31.82 | 31.82
2019-04-29 01:00 | 30.54 | 30.54
2019-04-29 01:30 | 30.1 | 30.1
2019-04-29 02:00 | 29.78 | 29.78
2019-04-29 02:30 | 29.61 | 29.61
2019-04-29 03:00 | 29.34 | 29.34
2019-04-29 03:30 | 29 | 29
2019-04-29 04:00 | 29.14 | 29.14
2019-04-29 04:30 | 29.88 | 29.87
2019-04-29 05:00 | 31.31 | 31.31
2019-04-29 05:30 | 33.97 | 33.95
2019-04-29 06:00 | 36.81 | 36.73
2019-04-29 06:30 | 41.23 | 40.98
2019-04-29 07:00 | 46.35 | 45.84
2019-04-29 07:30 | 51.72 | 51.19
2019-04-29 08:00 | 54.1 | 53.7
2019-04-29 08:30 | 54.08 | 53.7
2019-04-29 09:00 | 54.41 | 53.84
2019-04-29 09:30 | 54.02 | 53.35
2019-04-29 10:00 | 53.78 | 53
2019-04-29 10:30 | 52.62 | 51.67
2019-04-29 11:00 | 53.22 | 52.08
2019-04-29 11:30 | 53.68 | 52.5
2019-04-29 12:00 | 54.04 | 52.81
2019-04-29 12:30 | 55.21 | 54.03
2019-04-29 13:00 | 53.67 | 52.52
2019-04-29 13:30 | 53.76 | 52.54
2019-04-29 14:00 | 55.08 | 53.79
2019-04-29 14:30 | 54.81 | 53.55
2019-04-29 15:00 | 56.69 | 55.59
2019-04-29 15:30 | 56.36 | 55.45
2019-04-29 16:00 | 56.93 | 56.21
2019-04-29 16:30 | 56.53 | 56.09
2019-04-29 17:00 | 54.59 | 54.32
2019-04-29 17:30 | 53.16 | 53.1
2019-04-29 18:00 | 53.39 | 53.38
2019-04-29 18:30 | 54.17 | 54.17
2019-04-29 19:00 | 52.74 | 52.74
2019-04-29 19:30 | 50.08 | 50.06
2019-04-29 20:00 | 48.09 | 48.05
2019-04-29 20:30 | 45.73 | 45.66
2019-04-29 21:00 | 43.68 | 43.55
2019-04-29 21:30 | 41.93 | 41.73
2019-04-29 22:00 | 40.14 | 39.88
2019-04-29 22:30 | 38.41 | 38.09
2019-04-29 23:00 | 38.88 | 38.74
2019-04-29 23:30 | 36 | 35.98
2019-04-30 | 34.17 | 34.14
2019-04-30 00:30 | 33.26 | 33.19
2019-04-30 01:00 | 32.11 | 32.03
2019-04-30 01:30 | 31.39 | 31.31
2019-04-30 02:00 | 30.68 | 30.57
2019-04-30 02:30 | 30.44 | 30.3
2019-04-30 03:00 | 30.36 | 30.34
2019-04-30 03:30 | 30.08 | 30.06
2019-04-30 04:00 | 29.85 | 29.84
2019-04-30 04:30 | 31.19 | 31.15
2019-04-30 05:00 | 33.36 | 33.26
2019-04-30 05:30 | 36.25 | 36.06
2019-04-30 06:00 | 38.96 | 38.66
2019-04-30 06:30 | 44.25 | 43.8
2019-04-30 07:00 | 48.7 | 48.37
2019-04-30 07:30 | 54.92 | 54.18
2019-04-30 08:00 | 58.36 | 57.75
2019-04-30 08:30 | 59.83 | 59.08
2019-04-30 09:00 | 61.37 | 60.56
2019-04-30 09:30 | 60.6 | 59.74
2019-04-30 10:00 | 59.71 | 58.78
2019-04-30 10:30 | 58.36 | 57.33
2019-04-30 11:00 | 59.2 | 58.06
2019-04-30 11:30 | 58.65 | 57.46
2019-04-30 12:00 | 59.29 | 58.11
2019-04-30 12:30 | 60.45 | 59.35
2019-04-30 13:00 | 60.36 | 59.43
2019-04-30 13:30 | 58.93 | 57.99
2019-04-30 14:00 | 59.08 | 58.02
2019-04-30 14:30 | 59.18 | 58.17
2019-04-30 15:00 | 59.08 | 58.14
2019-04-30 15:30 | 58.63 | 57.82
2019-04-30 16:00 | 57.44 | 56.86
2019-04-30 16:30 | 54.82 | 54.39
2019-04-30 17:00 | 55.05 | 54.67
2019-04-30 17:30 | 54.24 | 53.82
2019-04-30 18:00 | 55.13 | 54.7
2019-04-30 18:30 | 55.65 | 55.21
2019-04-30 19:00 | 54.58 | 54.13
2019-04-30 19:30 | 52.02 | 51.53
2019-04-30 20:00 | 49.91 | 49.39
2019-04-30 20:30 | 47.9 | 47.34
2019-04-30 21:00 | 45.73 | 45.13
2019-04-30 21:30 | 44.09 | 43.46
2019-04-30 22:00 | 42.08 | 41.45
2019-04-30 22:30 | 40.02 | 39.39
2019-04-30 23:00 | 41.1 | 40.48
2019-04-30 23:30 | 37.74 | 37.12
2019-05-01 | 35.4 | 34.75
2019-05-01 00:30 | 34.54 | 33.86
2019-05-01 01:00 | 33.78 | 33.09
2019-05-01 01:30 | 33.22 | 32.52
2019-05-01 02:00 | 32.81 | 32.09
2019-05-01 02:30 | 32.52 | 31.8
2019-05-01 03:00 | 32.09 | 31.35
2019-05-01 03:30 | 31.65 | 30.89
2019-05-01 04:00 | 32.01 | 31.26
2019-05-01 04:30 | 33.1 | 32.38
2019-05-01 05:00 | 34.13 | 33.44
2019-05-01 05:30 | 36.07 | 35.44
2019-05-01 06:00 | 38.55 | 37.98
2019-05-01 06:30 | 43.1 | 42.61
2019-05-01 07:00 | 47.53 | 47.08
2019-05-01 07:30 | 51.79 | 51.22
2019-05-01 08:00 | 54.35 | 53.8
2019-05-01 08:30 | 57.42 | 56.83
2019-05-01 09:00 | 59.06 | 58.29
2019-05-01 09:30 | 56.87 | 55.97
2019-05-01 10:00 | 58.29 | 57.31
2019-05-01 10:30 | 57.76 | 56.59
2019-05-01 11:00 | 57.03 | 55.65
2019-05-01 11:30 | 57.24 | 55.65
2019-05-01 12:00 | 57.07 | 55.44
2019-05-01 12:30 | 57.75 | 56.16
2019-05-01 13:00 | 57.72 | 56.18
2019-05-01 13:30 | 58.54 | 56.99
2019-05-01 14:00 | 59.18 | 57.58
2019-05-01 14:30 | 60.1 | 58.53
2019-05-01 15:00 | 60.19 | 58.66
2019-05-01 15:30 | 60.91 | 59.6
2019-05-01 16:00 | 60.94 | 59.91
2019-05-01 16:30 | 60.84 | 60.1
2019-05-01 17:00 | 60.23 | 59.74
2019-05-01 17:30 | 58.27 | 58.03
2019-05-01 18:00 | 58.09 | 57.99
2019-05-01 18:30 | 58.45 | 58.15
2019-05-01 19:00 | 57.66 | 57.36
2019-05-01 19:30 | 55.24 | 54.98
2019-05-01 20:00 | 53.12 | 52.91
2019-05-01 20:30 | 51.02 | 50.87
2019-05-01 21:00 | 49.16 | 49.04
2019-05-01 21:30 | 46.89 | 46.81
2019-05-01 22:00 | 44.61 | 44.58
2019-05-01 22:30 | 42.53 | 42.52
2019-05-01 23:00 | 43 | 42.98
2019-05-01 23:30 | 39.48 | 39.48
2019-05-02 | 37.65 | 37.65
2019-05-02 00:30 | 36.8 | 36.73
2019-05-02 01:00 | 35.92 | 35.72
2019-05-02 01:30 | 34.98 | 34.8
2019-05-02 02:00 | 34.02 | 33.87
2019-05-02 02:30 | 33.77 | 33.64
2019-05-02 03:00 | 33.48 | 33.36
2019-05-02 03:30 | 33.33 | 33.22
2019-05-02 04:00 | 33.06 | 32.98
2019-05-02 04:30 | 34.16 | 34.04
2019-05-02 05:00 | 35.49 | 35.34
2019-05-02 05:30 | 37.93 | 37.68
2019-05-02 06:00 | 40.51 | 40.12
2019-05-02 06:30 | 45.27 | 44.72
2019-05-02 07:00 | 50.1 | 49.73
2019-05-02 07:30 | 56.61 | 55.83
2019-05-02 08:00 | 59.18 | 58.6
2019-05-02 08:30 | 60.7 | 59.87
2019-05-02 09:00 | 61.6 | 60.57
2019-05-02 09:30 | 62.88 | 61.58
2019-05-02 10:00 | 61.81 | 60.46
2019-05-02 10:30 | 62.88 | 61.57
2019-05-02 11:00 | 63.45 | 62.15
2019-05-02 11:30 | 61.31 | 59.98
2019-05-02 12:00 | 63.6 | 62.19
2019-05-02 12:30 | 62.6 | 61.26
2019-05-02 13:00 | 60.01 | 58.62
2019-05-02 13:30 | 60.48 | 58.95
2019-05-02 14:00 | 60.7 | 59.17
2019-05-02 14:30 | 60.32 | 58.78
2019-05-02 15:00 | 60.62 | 59.18
2019-05-02 15:30 | 62.5 | 61.19
2019-05-02 16:00 | 62.81 | 61.48
2019-05-02 16:30 | 62.25 | 60.86
2019-05-02 17:00 | 60.94 | 59.46
2019-05-02 17:30 | 59.46 | 57.89
2019-05-02 18:00 | 59.44 | 57.94
2019-05-02 18:30 | 60.6 | 59.14
2019-05-02 19:00 | 59.68 | 58.17
2019-05-02 19:30 | 57.31 | 55.7
2019-05-02 20:00 | 55.18 | 53.47
2019-05-02 20:30 | 53.17 | 51.37
2019-05-02 21:00 | 51.62 | 49.74
2019-05-02 21:30 | 49.24 | 47.23
2019-05-02 22:00 | 46.9 | 44.75
2019-05-02 22:30 | 42.62 | 42.03
2019-05-02 23:00 | 42.65 | 42.65
2019-05-02 23:30 | 39.34 | 39.34
2019-05-03 | 37.61 | 37.61
2019-05-03 00:30 | 36.25 | 36.17
2019-05-03 01:00 | 35.27 | 35.12
2019-05-03 01:30 | 34.53 | 34.39
2019-05-03 02:00 | 33.86 | 33.73
2019-05-03 02:30 | 33.38 | 33.28
2019-05-03 03:00 | 32.99 | 32.89
2019-05-03 03:30 | 32.68 | 32.59
2019-05-03 04:00 | 33.08 | 32.98
2019-05-03 04:30 | 34.01 | 33.89
2019-05-03 05:00 | 35.68 | 35.5
2019-05-03 05:30 | 37.97 | 37.7
2019-05-03 06:00 | 40.66 | 40.24
2019-05-03 06:30 | 44.97 | 44.34
2019-05-03 07:00 | 49.23 | 48.89
2019-05-03 07:30 | 54.96 | 54.18
2019-05-03 08:00 | 57 | 56.41
2019-05-03 08:30 | 58.07 | 57.25
2019-05-03 09:00 | 61.24 | 60.27
2019-05-03 09:30 | 61.13 | 60.21
2019-05-03 10:00 | 61.02 | 60.16
2019-05-03 10:30 | 61.02 | 60.01
2019-05-03 11:00 | 56.92 | 55.76
2019-05-03 11:30 | 58.38 | 57.11
2019-05-03 12:00 | 56.71 | 55.81
2019-05-03 12:30 | 56.9 | 56.16
2019-05-03 13:00 | 55.78 | 55.1
2019-05-03 13:30 | 55.18 | 54.55
2019-05-03 14:00 | 55.27 | 54.67
2019-05-03 14:30 | 55.67 | 55.14
2019-05-03 15:00 | 55.56 | 55.1
2019-05-03 15:30 | 55.89 | 55.58
2019-05-03 16:00 | 56.27 | 56.1
2019-05-03 16:30 | 56.85 | 56.75
2019-05-03 17:00 | 56.6 | 56.57
2019-05-03 17:30 | 55.67 | 55.67
2019-05-03 18:00 | 55.89 | 55.87
2019-05-03 18:30 | 55.52 | 55.46
2019-05-03 19:00 | 54.21 | 54.19
2019-05-03 19:30 | 51.67 | 51.67
2019-05-03 20:00 | 49.45 | 49.44
2019-05-03 20:30 | 47.4 | 47.38
2019-05-03 21:00 | 46.07 | 46.03
2019-05-03 21:30 | 44.3 | 44.21
2019-05-03 22:00 | 42.36 | 42.19
2019-05-03 22:30 | 41 | 40.78
2019-05-03 23:00 | 41.9 | 41.66
2019-05-03 23:30 | 38.48 | 38.12
2019-05-04 | 36.7 | 36.27
2019-05-04 00:30 | 34.89 | 34.78
2019-05-04 01:00 | 34.26 | 34.21
2019-05-04 01:30 | 33.3 | 33.23
2019-05-04 02:00 | 32.27 | 32.2
2019-05-04 02:30 | 31.67 | 31.65
2019-05-04 03:00 | 31.17 | 31.16
2019-05-04 03:30 | 30.75 | 30.74
2019-05-04 04:00 | 30.68 | 30.67
2019-05-04 04:30 | 30.93 | 30.93
2019-05-04 05:00 | 31.34 | 31.32
2019-05-04 05:30 | 32.31 | 32.28
2019-05-04 06:00 | 33.08 | 33.05
2019-05-04 06:30 | 34.14 | 34.09
2019-05-04 07:00 | 34.99 | 34.92
2019-05-04 07:30 | 37.61 | 37.42
2019-05-04 08:00 | 40.97 | 40.65
2019-05-04 08:30 | 41.59 | 41.05
2019-05-04 09:00 | 42.41 | 41.75
2019-05-04 09:30 | 42.62 | 42.36
2019-05-04 10:00 | 42.23 | 41.9
2019-05-04 10:30 | 43.5 | 43.14
2019-05-04 11:00 | 44.03 | 43.67
2019-05-04 11:30 | 42.43 | 42.05
2019-05-04 12:00 | 40.28 | 39.87
2019-05-04 12:30 | 40.6 | 40.27
2019-05-04 13:00 | 43.26 | 42.99
2019-05-04 13:30 | 39.72 | 39.46
2019-05-04 14:00 | 41.03 | 40.81
2019-05-04 14:30 | 43.62 | 43.44
2019-05-04 15:00 | 43.14 | 42.98
2019-05-04 15:30 | 43.47 | 43.36
2019-05-04 16:00 | 43.65 | 43.57
2019-05-04 16:30 | 45.65 | 45.59
2019-05-04 17:00 | 45.54 | 45.51
2019-05-04 17:30 | 46.37 | 46.36
2019-05-04 18:00 | 48.13 | 48.11
2019-05-04 18:30 | 48.07 | 48.06
2019-05-04 19:00 | 46.81 | 46.8
2019-05-04 19:30 | 44.89 | 44.89
2019-05-04 20:00 | 43.47 | 43.47
2019-05-04 20:30 | 41.93 | 41.92
2019-05-04 21:00 | 41.23 | 41.23
2019-05-04 21:30 | 39.97 | 39.96
2019-05-04 22:00 | 38.84 | 38.82
2019-05-04 22:30 | 37.59 | 37.55
2019-05-04 23:00 | 38.52 | 38.47
2019-05-04 23:30 | 35.46 | 35.39
2019-05-05 | 33.29 | 33.26
2019-05-05 00:30 | 32.61 | 32.59
2019-05-05 01:00 | 32 | 31.98
2019-05-05 01:30 | 31.61 | 31.59
2019-05-05 02:00 | 30.89 | 30.88
2019-05-05 02:30 | 30.41 | 30.4
2019-05-05 03:00 | 29.65 | 29.65
2019-05-05 03:30 | 29.15 | 29.15
2019-05-05 04:00 | 29.23 | 29.23
2019-05-05 04:30 | 29.47 | 29.47
2019-05-05 05:00 | 29.89 | 29.89
2019-05-05 05:30 | 30.61 | 30.61
2019-05-05 06:00 | 31.09 | 31.08
2019-05-05 06:30 | 31.5 | 31.5
2019-05-05 07:00 | 31.29 | 31.29
2019-05-05 07:30 | 32.77 | 32.77
2019-05-05 08:00 | 33.09 | 33.08
2019-05-05 08:30 | 32.96 | 32.9
2019-05-05 09:00 | 32.9 | 32.76
2019-05-05 09:30 | 32.83 | 32.64
2019-05-05 10:00 | 31.37 | 31.15
2019-05-05 10:30 | 30.77 | 30.5
2019-05-05 11:00 | 29.85 | 29.55
2019-05-05 11:30 | 29.76 | 29.42
2019-05-05 12:00 | 29.37 | 29
2019-05-05 12:30 | 30.48 | 30.11
2019-05-05 13:00 | 30.13 | 29.72
2019-05-05 13:30 | 30.52 | 30.11
2019-05-05 14:00 | 30.88 | 30.5
2019-05-05 14:30 | 31.46 | 31.12
2019-05-05 15:00 | 32.52 | 32.2
2019-05-05 15:30 | 33.62 | 33.34
2019-05-05 16:00 | 35.32 | 35.08
2019-05-05 16:30 | 37.38 | 37.19
2019-05-05 17:00 | 38.57 | 38.42
2019-05-05 17:30 | 39.81 | 39.71
2019-05-05 18:00 | 41.69 | 41.57
2019-05-05 18:30 | 43.5 | 43.38
2019-05-05 19:00 | 42.41 | 42.31
2019-05-05 19:30 | 40.94 | 40.85
2019-05-05 20:00 | 39.08 | 39.02
2019-05-05 20:30 | 37.15 | 37.13
2019-05-05 21:00 | 36.13 | 36.1
2019-05-05 21:30 | 34.86 | 34.85
2019-05-05 22:00 | 33.88 | 33.88
2019-05-05 22:30 | 33 | 33
2019-05-05 23:00 | 34.35 | 34.35
2019-05-05 23:30 | 31.1 | 31.1
2019-05-06 | 29.44 | 29.43
2019-05-06 00:30 | 28.69 | 28.67
2019-05-06 01:00 | 27.98 | 27.96
2019-05-06 01:30 | 27.29 | 27.26
2019-05-06 02:00 | 26.75 | 26.71
2019-05-06 02:30 | 26.49 | 26.44
2019-05-06 03:00 | 26.27 | 26.22
2019-05-06 03:30 | 26.54 | 26.5
2019-05-06 04:00 | 26.42 | 26.37
2019-05-06 04:30 | 26.76 | 26.72
2019-05-06 05:00 | 27.41 | 27.39
2019-05-06 05:30 | 27.59 | 27.56
2019-05-06 06:00 | 28.38 | 28.36
2019-05-06 06:30 | 28.99 | 28.97
2019-05-06 07:00 | 29.62 | 29.61
2019-05-06 07:30 | 30.17 | 30.17
2019-05-06 08:00 | 30.51 | 30.51
2019-05-06 08:30 | 30.26 | 30.23
2019-05-06 09:00 | 29.8 | 29.75
2019-05-06 09:30 | 29.33 | 29.24
2019-05-06 10:00 | 28.55 | 28.42
2019-05-06 10:30 | 28.24 | 28.06
2019-05-06 11:00 | 27.8 | 27.56
2019-05-06 11:30 | 27.64 | 27.33
2019-05-06 12:00 | 27.7 | 27.35
2019-05-06 12:30 | 28.65 | 28.29
2019-05-06 13:00 | 28.43 | 28.03
2019-05-06 13:30 | 28.62 | 28.24
2019-05-06 14:00 | 29.07 | 28.69
2019-05-06 14:30 | 29.76 | 29.4
2019-05-06 15:00 | 30.69 | 30.39
2019-05-06 15:30 | 31.68 | 31.46
2019-05-06 16:00 | 33.75 | 33.55
2019-05-06 16:30 | 36.53 | 36.36
2019-05-06 17:00 | 37.61 | 37.48
2019-05-06 17:30 | 39.55 | 39.46
2019-05-06 18:00 | 42.47 | 42.38
2019-05-06 18:30 | 44.7 | 44.6
2019-05-06 19:00 | 43.47 | 43.37
2019-05-06 19:30 | 41.24 | 41.17
2019-05-06 20:00 | 39.6 | 39.55
2019-05-06 20:30 | 37.81 | 37.78
2019-05-06 21:00 | 36.32 | 36.3
2019-05-06 21:30 | 34.76 | 34.75
2019-05-06 22:00 | 33.08 | 33.08
2019-05-06 22:30 | 31.29 | 31.29
2019-05-06 23:00 | 32.42 | 32.41
2019-05-06 23:30 | 29.32 | 29.3
2019-05-07 | 27.8 | 27.78
2019-05-07 00:30 | 27.37 | 27.34
2019-05-07 01:00 | 26.48 | 26.45
2019-05-07 01:30 | 26.09 | 26.05
2019-05-07 02:00 | 25.69 | 25.64
2019-05-07 02:30 | 25.48 | 25.42
2019-05-07 03:00 | 25.06 | 24.99
2019-05-07 03:30 | 25.72 | 25.67
2019-05-07 04:00 | 25.87 | 25.82
2019-05-07 04:30 | 26.98 | 26.95
2019-05-07 05:00 | 28.12 | 28.1
2019-05-07 05:30 | 30.09 | 30.08
2019-05-07 06:00 | 32.82 | 32.81
2019-05-07 06:30 | 37.08 | 36.99
2019-05-07 07:00 | 41.17 | 40.93
2019-05-07 07:30 | 45.7 | 45.29
2019-05-07 08:00 | 46.78 | 46.49
2019-05-07 08:30 | 46.21 | 45.7
2019-05-07 09:00 | 45.34 | 44.64
2019-05-07 09:30 | 44.68 | 44.03
2019-05-07 10:00 | 43.87 | 43.55
2019-05-07 10:30 | 43.86 | 43.42
2019-05-07 11:00 | 43.95 | 43.37
2019-05-07 11:30 | 44.21 | 43.49
2019-05-07 12:00 | 44.87 | 44.05
2019-05-07 12:30 | 45.7 | 44.91
2019-05-07 13:00 | 45.6 | 44.81
2019-05-07 13:30 | 46.24 | 45.43
2019-05-07 14:00 | 47.79 | 46.89
2019-05-07 14:30 | 48.18 | 47.35
2019-05-07 15:00 | 49.29 | 48.5
2019-05-07 15:30 | 49.89 | 49.23
2019-05-07 16:00 | 50.54 | 50.09
2019-05-07 16:30 | 51.58 | 51.29
2019-05-07 17:00 | 51.71 | 51.55
2019-05-07 17:30 | 50.58 | 50.56
2019-05-07 18:00 | 51.1 | 51.1
2019-05-07 18:30 | 51.85 | 51.84
2019-05-07 19:00 | 50.9 | 50.89
2019-05-07 19:30 | 48.27 | 48.23
2019-05-07 20:00 | 46.07 | 45.98
2019-05-07 20:30 | 43.84 | 43.71
2019-05-07 21:00 | 42.05 | 42.05
2019-05-07 21:30 | 39.86 | 39.86
2019-05-07 22:00 | 37.54 | 37.45
2019-05-07 22:30 | 35.72 | 35.64
2019-05-07 23:00 | 36.63 | 36.56
2019-05-07 23:30 | 33.51 | 33.46
2019-05-08 | 31.57 | 31.54
2019-05-08 00:30 | 30.75 | 30.73
2019-05-08 01:00 | 29.78 | 29.77
2019-05-08 01:30 | 29.29 | 29.27
2019-05-08 02:00 | 28.34 | 28.34
2019-05-08 02:30 | 27.46 | 27.46
2019-05-08 03:00 | 27.19 | 27.19
2019-05-08 03:30 | 27.14 | 27.14
2019-05-08 04:00 | 27.37 | 27.36
2019-05-08 04:30 | 28.51 | 28.51
2019-05-08 05:00 | 29.77 | 29.77
2019-05-08 05:30 | 32.1 | 32.08
2019-05-08 06:00 | 34.61 | 34.53
2019-05-08 06:30 | 38.9 | 38.68
2019-05-08 07:00 | 42.81 | 42.43
2019-05-08 07:30 | 47.01 | 46.75
2019-05-08 08:00 | 48.17 | 47.81
2019-05-08 08:30 | 49.18 | 48.51
2019-05-08 09:00 | 49.34 | 48.41
2019-05-08 09:30 | 49.03 | 48.51
2019-05-08 10:00 | 48.38 | 47.8
2019-05-08 10:30 | 49.47 | 48.74
2019-05-08 11:00 | 49.55 | 48.6
2019-05-08 11:30 | 48.56 | 47.53
2019-05-08 12:00 | 49.3 | 48.84
2019-05-08 12:30 | 49.47 | 49.04
2019-05-08 13:00 | 49.53 | 49.1
2019-05-08 13:30 | 49.48 | 49.09
2019-05-08 14:00 | 49.96 | 49.58
2019-05-08 14:30 | 50.36 | 49.98
2019-05-08 15:00 | 52.53 | 52.2
2019-05-08 15:30 | 53.52 | 53.33
2019-05-08 16:00 | 54.8 | 54.66
2019-05-08 16:30 | 53.35 | 53.32
2019-05-08 17:00 | 53.21 | 53.21
2019-05-08 17:30 | 51.65 | 51.6
2019-05-08 18:00 | 52.28 | 52.16
2019-05-08 18:30 | 53.44 | 53.29
2019-05-08 19:00 | 52.36 | 52.15
2019-05-08 19:30 | 50.34 | 50.1
2019-05-08 20:00 | 47.9 | 47.55
2019-05-08 20:30 | 45.09 | 45
2019-05-08 21:00 | 43.23 | 43.11
2019-05-08 21:30 | 41.51 | 41.33
2019-05-08 22:00 | 39.6 | 39.32
2019-05-08 22:30 | 37.09 | 36.93
2019-05-08 23:00 | 37.26 | 37.2
2019-05-08 23:30 | 34.41 | 34.33
2019-05-09 | 32.71 | 32.64
2019-05-09 00:30 | 31.6 | 31.56
2019-05-09 01:00 | 30.52 | 30.49
2019-05-09 01:30 | 29.55 | 29.52
2019-05-09 02:00 | 29.15 | 29.14
2019-05-09 02:30 | 28.3 | 28.3
2019-05-09 03:00 | 27.73 | 27.72
2019-05-09 03:30 | 27.77 | 27.77
2019-05-09 04:00 | 28.2 | 28.2
2019-05-09 04:30 | 29.34 | 29.34
2019-05-09 05:00 | 30.24 | 30.23
2019-05-09 05:30 | 32.64 | 32.61
2019-05-09 06:00 | 35.52 | 35.44
2019-05-09 06:30 | 39.41 | 39.18
2019-05-09 07:00 | 44.11 | 43.63
2019-05-09 07:30 | 48.39 | 47.98
2019-05-09 08:00 | 50.45 | 49.83
2019-05-09 08:30 | 51.84 | 50.95
2019-05-09 09:00 | 51.63 | 51.05
2019-05-09 09:30 | 51.67 | 50.95
2019-05-09 10:00 | 51.89 | 51.08
2019-05-09 10:30 | 52.76 | 51.71
2019-05-09 11:00 | 53.2 | 52
2019-05-09 11:30 | 53.13 | 51.8
2019-05-09 12:00 | 52.51 | 51.22
2019-05-09 12:30 | 52.85 | 51.59
2019-05-09 13:00 | 53.16 | 51.99
2019-05-09 13:30 | 56.64 | 55.31
2019-05-09 14:00 | 58.48 | 57.1
2019-05-09 14:30 | 58.66 | 57.26
2019-05-09 15:00 | 57.12 | 55.66
2019-05-09 15:30 | 57.03 | 55.55
2019-05-09 16:00 | 57.29 | 55.78
2019-05-09 16:30 | 58.14 | 56.6
2019-05-09 17:00 | 57.39 | 55.79
2019-05-09 17:30 | 56.2 | 54.5
2019-05-09 18:00 | 57.62 | 55.95
2019-05-09 18:30 | 58.49 | 56.84
2019-05-09 19:00 | 57.03 | 55.31
2019-05-09 19:30 | 54.41 | 52.56
2019-05-09 20:00 | 52.39 | 50.44
2019-05-09 20:30 | 50.53 | 48.47
2019-05-09 21:00 | 49.02 | 46.91
2019-05-09 21:30 | 46.37 | 44.2
2019-05-09 22:00 | 44.13 | 41.81
2019-05-09 22:30 | 41.76 | 39.26
2019-05-09 23:00 | 42.12 | 39.64
2019-05-09 23:30 | 36.44 | 36.27
2019-05-10 | 34.37 | 34.32
2019-05-10 00:30 | 33.46 | 33.37
2019-05-10 01:00 | 32.54 | 32.46
2019-05-10 01:30 | 31.62 | 31.54
2019-05-10 02:00 | 30.75 | 30.7
2019-05-10 02:30 | 30.3 | 30.26
2019-05-10 03:00 | 29.8 | 29.78
2019-05-10 03:30 | 29.71 | 29.69
2019-05-10 04:00 | 30.02 | 29.99
2019-05-10 04:30 | 30.82 | 30.78
2019-05-10 05:00 | 32.54 | 32.47
2019-05-10 05:30 | 35.12 | 34.98
2019-05-10 06:00 | 38.06 | 37.82
2019-05-10 06:30 | 42.64 | 42.13
2019-05-10 07:00 | 46.9 | 46.56
2019-05-10 07:30 | 52.64 | 52.03
2019-05-10 08:00 | 55.48 | 54.94
2019-05-10 08:30 | 57.77 | 57.12
2019-05-10 09:00 | 60.26 | 59.18
2019-05-10 09:30 | 60.78 | 59.39
2019-05-10 10:00 | 59.17 | 57.75
2019-05-10 10:30 | 57.89 | 56.46
2019-05-10 11:00 | 56.35 | 54.91
2019-05-10 11:30 | 56.74 | 55.26
2019-05-10 12:00 | 56.33 | 54.87
2019-05-10 12:30 | 57.16 | 55.75
2019-05-10 13:00 | 55.57 | 54.1
2019-05-10 13:30 | 55 | 53.52
2019-05-10 14:00 | 55.78 | 54.3
2019-05-10 14:30 | 55.31 | 53.8
2019-05-10 15:00 | 55.84 | 54.32
2019-05-10 15:30 | 56.14 | 54.61
2019-05-10 16:00 | 57.06 | 55.54
2019-05-10 16:30 | 58.12 | 56.58
2019-05-10 17:00 | 57.87 | 56.28
2019-05-10 17:30 | 56.62 | 54.94
2019-05-10 18:00 | 56.81 | 55.11
2019-05-10 18:30 | 55.91 | 54.14
2019-05-10 19:00 | 54.58 | 52.74
2019-05-10 19:30 | 52.67 | 50.74
2019-05-10 20:00 | 50.94 | 48.92
2019-05-10 20:30 | 48.89 | 46.74
2019-05-10 21:00 | 47.63 | 45.4
2019-05-10 21:30 | 45.65 | 43.74
2019-05-10 22:00 | 42 | 41.85
2019-05-10 22:30 | 40.14 | 40.1
2019-05-10 23:00 | 40.42 | 40.41
2019-05-10 23:30 | 37.22 | 37.15
2019-05-11 | 35.76 | 35.66
2019-05-11 00:30 | 34.62 | 34.55
2019-05-11 01:00 | 33.24 | 33.19
2019-05-11 01:30 | 32.06 | 32.02
2019-05-11 02:00 | 31.02 | 31
2019-05-11 02:30 | 29.7 | 29.7
2019-05-11 03:00 | 28.72 | 28.72
2019-05-11 03:30 | 28.08 | 28.07
2019-05-11 04:00 | 27.96 | 27.96
2019-05-11 04:30 | 28.46 | 28.46
2019-05-11 05:00 | 28.8 | 28.8
2019-05-11 05:30 | 29.97 | 29.96
2019-05-11 06:00 | 30.66 | 30.65
2019-05-11 06:30 | 32.22 | 32.2
2019-05-11 07:00 | 33.13 | 33.11
2019-05-11 07:30 | 35.01 | 34.95
2019-05-11 08:00 | 35.41 | 35.29
2019-05-11 08:30 | 36.05 | 35.83
2019-05-11 09:00 | 36.22 | 35.9
2019-05-11 09:30 | 35.43 | 35.01
2019-05-11 10:00 | 34.44 | 33.97
2019-05-11 10:30 | 33.49 | 32.94
2019-05-11 11:00 | 33.23 | 32.55
2019-05-11 11:30 | 32.02 | 31.37
2019-05-11 12:00 | 31.51 | 30.82
2019-05-11 12:30 | 31.63 | 31.04
2019-05-11 13:00 | 30.61 | 30.02
2019-05-11 13:30 | 31.38 | 30.8
2019-05-11 14:00 | 32.09 | 31.56
2019-05-11 14:30 | 32.72 | 32.23
2019-05-11 15:00 | 32.96 | 32.6
2019-05-11 15:30 | 33.82 | 33.57
2019-05-11 16:00 | 35.64 | 35.44
2019-05-11 16:30 | 38.11 | 37.95
2019-05-11 17:00 | 40.07 | 39.93
2019-05-11 17:30 | 41.51 | 41.4
2019-05-11 18:00 | 43.81 | 43.69
2019-05-11 18:30 | 44.7 | 44.58
2019-05-11 19:00 | 43.53 | 43.44
2019-05-11 19:30 | 41.85 | 41.77
2019-05-11 20:00 | 40.22 | 40.15
2019-05-11 20:30 | 38.41 | 38.38
2019-05-11 21:00 | 37.2 | 37.18
2019-05-11 21:30 | 35.97 | 35.96
2019-05-11 22:00 | 35.28 | 35.27
2019-05-11 22:30 | 33.89 | 33.88
2019-05-11 23:00 | 35.02 | 35.02
2019-05-11 23:30 | 32.06 | 32.06
2019-05-12 | 30.44 | 30.43
2019-05-12 00:30 | 29.69 | 29.67
2019-05-12 01:00 | 28.51 | 28.48
2019-05-12 01:30 | 28.01 | 27.99
2019-05-12 02:00 | 27.43 | 27.4
2019-05-12 02:30 | 26.79 | 26.75
2019-05-12 03:00 | 26.38 | 26.32
2019-05-12 03:30 | 26.75 | 26.11
2019-05-12 04:00 | 29.32 | 26.08
2019-05-12 04:30 | 29.85 | 26.66
2019-05-12 05:00 | 29.97 | 26.8
2019-05-12 05:30 | 30.83 | 27.78
2019-05-12 06:00 | 31.55 | 28.56
2019-05-12 06:30 | 32.46 | 29.56
2019-05-12 07:00 | 33.48 | 30.71
2019-05-12 07:30 | 34.57 | 31.9
2019-05-12 08:00 | 34.24 | 31.52
2019-05-12 08:30 | 34.04 | 31.29
2019-05-12 09:00 | 33.44 | 30.61
2019-05-12 09:30 | 33.19 | 30.32
2019-05-12 10:00 | 32.09 | 29.1
2019-05-12 10:30 | 31.62 | 28.54
2019-05-12 11:00 | 30.93 | 27.75
2019-05-12 11:30 | 30.27 | 27
2019-05-12 12:00 | 30.08 | 26.79
2019-05-12 12:30 | 30.8 | 27.59
2019-05-12 13:00 | 30.36 | 27.13
2019-05-12 13:30 | 31.09 | 27.91
2019-05-12 14:00 | 31.2 | 28.04
2019-05-12 14:30 | 31.86 | 28.78
2019-05-12 15:00 | 32.85 | 29.89
2019-05-12 15:30 | 34.51 | 31.71
2019-05-12 16:00 | 36.66 | 34.07
2019-05-12 16:30 | 39.24 | 36.87
2019-05-12 17:00 | 41.19 | 38.92
2019-05-12 17:30 | 43.39 | 41.25
2019-05-12 18:00 | 45.21 | 44.18
2019-05-12 18:30 | 46.38 | 46.24
2019-05-12 19:00 | 45.12 | 45
2019-05-12 19:30 | 43.34 | 43.23
2019-05-12 20:00 | 42.02 | 41.92
2019-05-12 20:30 | 40.16 | 40.09
2019-05-12 21:00 | 38.53 | 38.48
2019-05-12 21:30 | 37.17 | 37.13
2019-05-12 22:00 | 35.62 | 35.61
2019-05-12 22:30 | 33.9 | 33.9
2019-05-12 23:00 | 34.66 | 34.66
2019-05-12 23:30 | 31.86 | 31.86
2019-05-13 | 30.35 | 30.35
2019-05-13 00:30 | 30.16 | 30.16
2019-05-13 01:00 | 29.45 | 29.45
2019-05-13 01:30 | 28.81 | 28.81
2019-05-13 02:00 | 28 | 27.99
2019-05-13 02:30 | 27.71 | 27.7
2019-05-13 03:00 | 27.33 | 27.31
2019-05-13 03:30 | 27.82 | 27.81
2019-05-13 04:00 | 28.18 | 28.18
2019-05-13 04:30 | 29.26 | 29.26
2019-05-13 05:00 | 30.59 | 30.59
2019-05-13 05:30 | 32.75 | 32.75
2019-05-13 06:00 | 35.29 | 35.26
2019-05-13 06:30 | 40.93 | 40.71
2019-05-13 07:00 | 45.16 | 44.74
2019-05-13 07:30 | 50.6 | 50.28
2019-05-13 08:00 | 52.4 | 51.99
2019-05-13 08:30 | 54.81 | 54.15
2019-05-13 09:00 | 55.83 | 54.37
2019-05-13 09:30 | 53.99 | 52.34
2019-05-13 10:00 | 53.8 | 52.12
2019-05-13 10:30 | 52.38 | 50.68
2019-05-13 11:00 | 50.76 | 49.04
2019-05-13 11:30 | 50.01 | 48.28
2019-05-13 12:00 | 50.89 | 49.22
2019-05-13 12:30 | 52.56 | 50.96
2019-05-13 13:00 | 52.64 | 51.02
2019-05-13 13:30 | 52.69 | 51.08
2019-05-13 14:00 | 53.8 | 52.22
2019-05-13 14:30 | 56.12 | 54.57
2019-05-13 15:00 | 58.53 | 57.04
2019-05-13 15:30 | 60.1 | 58.63
2019-05-13 16:00 | 59.55 | 58.04
2019-05-13 16:30 | 57.8 | 56.17
2019-05-13 17:00 | 58.07 | 56.41
2019-05-13 17:30 | 58.45 | 56.76
2019-05-13 18:00 | 59.09 | 57.39
2019-05-13 18:30 | 58.63 | 56.89
2019-05-13 19:00 | 56.76 | 54.93
2019-05-13 19:30 | 54.2 | 52.25
2019-05-13 20:00 | 50.73 | 49.6
2019-05-13 20:30 | 47.48 | 47.41
2019-05-13 21:00 | 45.69 | 45.58
2019-05-13 21:30 | 43.95 | 43.79
2019-05-13 22:00 | 41.65 | 41.41
2019-05-13 22:30 | 38.98 | 38.66
2019-05-13 23:00 | 36.63 | 36.6
2019-05-13 23:30 | 35.22 | 35.17
2019-05-14 | 34.19 | 34.14
2019-05-14 00:30 | 33.02 | 32.94
2019-05-14 01:00 | 32.34 | 32.25
2019-05-14 01:30 | 31.76 | 31.64
2019-05-14 02:00 | 31.16 | 31.02
2019-05-14 02:30 | 30.65 | 30.5
2019-05-14 03:00 | 30.08 | 29.89
2019-05-14 03:30 | 30.18 | 30
2019-05-14 04:00 | 30.77 | 30.6
2019-05-14 04:30 | 32.29 | 31.51
2019-05-14 05:00 | 34.91 | 32.33
2019-05-14 05:30 | 37.27 | 34.86
2019-05-14 06:00 | 40.04 | 37.79
2019-05-14 06:30 | 44.69 | 42.66
2019-05-14 07:00 | 47.92 | 47.12
2019-05-14 07:30 | 53.24 | 52.88
2019-05-14 08:00 | 55.79 | 55.2
2019-05-14 08:30 | 57.68 | 56.78
2019-05-14 09:00 | 57.32 | 56.79
2019-05-14 09:30 | 57.33 | 56.86
2019-05-14 10:00 | 57.72 | 57.22
2019-05-14 10:30 | 59.48 | 58.77
2019-05-14 11:00 | 59.79 | 59.01
2019-05-14 11:30 | 60.04 | 59.24
2019-05-14 12:00 | 60.24 | 59.46
2019-05-14 12:30 | 59.32 | 58.55
2019-05-14 13:00 | 59.31 | 58.57
2019-05-14 13:30 | 59.58 | 58.85
2019-05-14 14:00 | 59.94 | 59.23
2019-05-14 14:30 | 59.28 | 58.56
2019-05-14 15:00 | 58.03 | 57.38
2019-05-14 15:30 | 58.62 | 58.05
2019-05-14 16:00 | 58.72 | 58.26
2019-05-14 16:30 | 57.62 | 57.39
2019-05-14 17:00 | 57.26 | 57.13
2019-05-14 17:30 | 56.76 | 56.71
2019-05-14 18:00 | 57.68 | 57.66
2019-05-14 18:30 | 57.43 | 57.43
2019-05-14 19:00 | 55.44 | 55.43
2019-05-14 19:30 | 52.53 | 52.52
2019-05-14 20:00 | 50.24 | 50.21
2019-05-14 20:30 | 48.15 | 48.1
2019-05-14 21:00 | 46.02 | 45.94
2019-05-14 21:30 | 43.82 | 43.67
2019-05-14 22:00 | 41.61 | 41.39
2019-05-14 22:30 | 39.34 | 38.99
2019-05-14 23:00 | 37.66 | 36.98
2019-05-14 23:30 | 36.14 | 35.42
2019-05-15 | 34.53 | 33.78
2019-05-15 00:30 | 33.53 | 32.76
2019-05-15 01:00 | 32.79 | 32.01
2019-05-15 01:30 | 32.1 | 31.3
2019-05-15 02:00 | 31.6 | 30.8
2019-05-15 02:30 | 31.09 | 30.28
2019-05-15 03:00 | 31.05 | 30.24
2019-05-15 03:30 | 30.85 | 30.03
2019-05-15 04:00 | 30.97 | 30.16
2019-05-15 04:30 | 31.89 | 31.1
2019-05-15 05:00 | 33.34 | 32.57
2019-05-15 05:30 | 36.28 | 35.58
2019-05-15 06:00 | 39.27 | 38.6
2019-05-15 06:30 | 44.29 | 43.69
2019-05-15 07:00 | 48.54 | 47.94
2019-05-15 07:30 | 54.11 | 53.59
2019-05-15 08:00 | 57.18 | 56.44
2019-05-15 08:30 | 58.01 | 57
2019-05-15 09:00 | 57.08 | 56.46
2019-05-15 09:30 | 54.99 | 54.41
2019-05-15 10:00 | 52.7 | 52.01
2019-05-15 10:30 | 53.67 | 52.7
2019-05-15 11:00 | 54.29 | 53.14
2019-05-15 11:30 | 55.05 | 53.89
2019-05-15 12:00 | 54.9 | 54.12
2019-05-15 12:30 | 55.13 | 54.63
2019-05-15 13:00 | 56.04 | 55.65
2019-05-15 13:30 | 58.11 | 57.75
2019-05-15 14:00 | 57.16 | 56.78
2019-05-15 14:30 | 56.04 | 55.65
2019-05-15 15:00 | 55.11 | 54.73
2019-05-15 15:30 | 57.82 | 57.46
2019-05-15 16:00 | 47.73 | 47.19
2019-05-15 16:30 | 56.17 | 55.75
2019-05-15 17:00 | 56.19 | 55.75
2019-05-15 17:30 | 56.01 | 55.54
2019-05-15 18:00 | 58.26 | 57.81
2019-05-15 18:30 | 58.81 | 58.35
2019-05-15 19:00 | 57.5 | 57.02
2019-05-15 19:30 | 54.53 | 54.01
2019-05-15 20:00 | 52.6 | 52.05
2019-05-15 20:30 | 49.36 | 48.93
2019-05-15 21:00 | 47.59 | 47.15
2019-05-15 21:30 | 45.86 | 45.31
2019-05-15 22:00 | 43.63 | 43.11
2019-05-15 22:30 | 40.74 | 40.19
2019-05-15 23:00 | 39.03 | 38.43
2019-05-15 23:30 | 36.75 | 36.12
2019-05-16 | 35.02 | 34.36
2019-05-16 00:30 | 33.86 | 33.18
2019-05-16 01:00 | 33.26 | 32.57
2019-05-16 01:30 | 33.27 | 32.58
2019-05-16 02:00 | 32.71 | 32.02
2019-05-16 02:30 | 32.22 | 31.52
2019-05-16 03:00 | 31.67 | 30.96
2019-05-16 03:30 | 31.29 | 30.57
2019-05-16 04:00 | 31.51 | 30.81
2019-05-16 04:30 | 32.43 | 31.73
2019-05-16 05:00 | 33.52 | 32.85
2019-05-16 05:30 | 36.43 | 35.81
2019-05-16 06:00 | 39.23 | 38.64
2019-05-16 06:30 | 43.98 | 43.43
2019-05-16 07:00 | 48.58 | 48.07
2019-05-16 07:30 | 54.22 | 53.71
2019-05-16 08:00 | 55.94 | 55.27
2019-05-16 08:30 | 57.23 | 56.56
2019-05-16 09:00 | 57.27 | 56.76
2019-05-16 09:30 | 56.99 | 56.43
2019-05-16 10:00 | 55.35 | 54.74
2019-05-16 10:30 | 55.84 | 55.13
2019-05-16 11:00 | 52.79 | 51.9
2019-05-16 11:30 | 51.96 | 50.88
2019-05-16 12:00 | 51.87 | 50.72
2019-05-16 12:30 | 51.26 | 50.71
2019-05-16 13:00 | 51.72 | 51.26
2019-05-16 13:30 | 53.67 | 53.25
2019-05-16 14:00 | 53.72 | 53.29
2019-05-16 14:30 | 54.19 | 53.74
2019-05-16 15:00 | 56.09 | 55.72
2019-05-16 15:30 | 56 | 55.62
2019-05-16 16:00 | 56.59 | 56.2
2019-05-16 16:30 | 55.7 | 55.27
2019-05-16 17:00 | 56.14 | 55.69
2019-05-16 17:30 | 55.86 | 55.4
2019-05-16 18:00 | 57.47 | 57.01
2019-05-16 18:30 | 58.47 | 58.01
2019-05-16 19:00 | 57.51 | 57.03
2019-05-16 19:30 | 54.64 | 54.14
2019-05-16 20:00 | 52.57 | 52.2
2019-05-16 20:30 | 49.89 | 49.5
2019-05-16 21:00 | 48.52 | 48.1
2019-05-16 21:30 | 46.23 | 45.67
2019-05-16 22:00 | 43.73 | 43.01
2019-05-16 22:30 | 40.88 | 40.05
2019-05-16 23:00 | 38.17 | 37.63
2019-05-16 23:30 | 36.63 | 36.06
2019-05-17 | 35.31 | 34.73
2019-05-17 00:30 | 34.16 | 33.55
2019-05-17 01:00 | 33.26 | 32.64
2019-05-17 01:30 | 32.34 | 31.63
2019-05-17 02:00 | 31.4 | 30.68
2019-05-17 02:30 | 31.13 | 30.41
2019-05-17 03:00 | 30.45 | 29.64
2019-05-17 03:30 | 30.65 | 29.84
2019-05-17 04:00 | 31 | 30.2
2019-05-17 04:30 | 31.88 | 31.09
2019-05-17 05:00 | 32.76 | 31.99
2019-05-17 05:30 | 35.42 | 34.71
2019-05-17 06:00 | 38.34 | 37.66
2019-05-17 06:30 | 43.18 | 42.56
2019-05-17 07:00 | 47.25 | 46.68
2019-05-17 07:30 | 52.59 | 52.09
2019-05-17 08:00 | 54.49 | 53.92
2019-05-17 08:30 | 54.81 | 53.98
2019-05-17 09:00 | 54.83 | 54.28
2019-05-17 09:30 | 52.66 | 52.14
2019-05-17 10:00 | 51.85 | 51.32
2019-05-17 10:30 | 54.08 | 53.52
2019-05-17 11:00 | 51.05 | 50.23
2019-05-17 11:30 | 51.24 | 50.35
2019-05-17 12:00 | 51.06 | 50.13
2019-05-17 12:30 | 50.8 | 49.92
2019-05-17 13:00 | 50.38 | 49.49
2019-05-17 13:30 | 50.19 | 49.39
2019-05-17 14:00 | 50.35 | 49.56
2019-05-17 14:30 | 51.25 | 50.56
2019-05-17 15:00 | 52.47 | 51.9
2019-05-17 15:30 | 52.36 | 51.85
2019-05-17 16:00 | 53.5 | 53
2019-05-17 16:30 | 52.88 | 52.39
2019-05-17 17:00 | 53.07 | 52.61
2019-05-17 17:30 | 53.82 | 53.38
2019-05-17 18:00 | 55.24 | 54.8
2019-05-17 18:30 | 55.24 | 54.78
2019-05-17 19:00 | 53.7 | 53.23
2019-05-17 19:30 | 50.8 | 50.31
2019-05-17 20:00 | 48.83 | 48.33
2019-05-17 20:30 | 47.55 | 47.04
2019-05-17 21:00 | 46.16 | 45.63
2019-05-17 21:30 | 44.32 | 43.78
2019-05-17 22:00 | 41.81 | 41.25
2019-05-17 22:30 | 39.77 | 39.15
2019-05-17 23:00 | 38.13 | 37.46
2019-05-17 23:30 | 36.97 | 36.28
2019-05-18 | 35.41 | 34.69
2019-05-18 00:30 | 33.8 | 33.05
2019-05-18 01:00 | 32.83 | 32.06
2019-05-18 01:30 | 31.97 | 31.18
2019-05-18 02:00 | 31.19 | 30.39
2019-05-18 02:30 | 30.98 | 30.17
2019-05-18 03:00 | 30.48 | 29.66
2019-05-18 03:30 | 30.37 | 29.55
2019-05-18 04:00 | 30.3 | 29.48
2019-05-18 04:30 | 30.59 | 29.78
2019-05-18 05:00 | 30.84 | 30.03
2019-05-18 05:30 | 31.86 | 31.09
2019-05-18 06:00 | 33.41 | 32.67
2019-05-18 06:30 | 35.34 | 34.63
2019-05-18 07:00 | 36.61 | 35.92
2019-05-18 07:30 | 38.92 | 38.25
2019-05-18 08:00 | 40.27 | 39.61
2019-05-18 08:30 | 41.45 | 40.79
2019-05-18 09:00 | 41.27 | 40.59
2019-05-18 09:30 | 40.81 | 40.11
2019-05-18 10:00 | 39.54 | 38.8
2019-05-18 10:30 | 39.28 | 38.47
2019-05-18 11:00 | 39.17 | 38.49
2019-05-18 11:30 | 38.62 | 37.93
2019-05-18 12:00 | 37.83 | 37.13
2019-05-18 12:30 | 36.88 | 36.17
2019-05-18 13:00 | 35.67 | 34.94
2019-05-18 13:30 | 36.58 | 35.87
2019-05-18 14:00 | 37.22 | 36.54
2019-05-18 14:30 | 36.9 | 36.22
2019-05-18 15:00 | 37.7 | 37.04
2019-05-18 15:30 | 38.7 | 38.07
2019-05-18 16:00 | 40.61 | 40.02
2019-05-18 16:30 | 41.6 | 41.03
2019-05-18 17:00 | 42.85 | 42.31
2019-05-18 17:30 | 44.41 | 43.89
2019-05-18 18:00 | 46.47 | 45.97
2019-05-18 18:30 | 47.33 | 46.84
2019-05-18 19:00 | 46.5 | 46
2019-05-18 19:30 | 44.58 | 44.07
2019-05-18 20:00 | 43.08 | 42.55
2019-05-18 20:30 | 41.62 | 41.08
2019-05-18 21:00 | 40.55 | 39.99
2019-05-18 21:30 | 39.26 | 38.69
2019-05-18 22:00 | 38.49 | 37.9
2019-05-18 22:30 | 37.02 | 36.36
2019-05-18 23:00 | 35.63 | 34.94
2019-05-18 23:30 | 34.41 | 33.69
2019-05-19 | 33.09 | 32.35
2019-05-19 00:30 | 32.04 | 31.27
2019-05-19 01:00 | 31.33 | 30.55
2019-05-19 01:30 | 30.7 | 29.9
2019-05-19 02:00 | 30.08 | 29.27
2019-05-19 02:30 | 29.96 | 29.15
2019-05-19 03:00 | 29.56 | 28.73
2019-05-19 03:30 | 29.13 | 28.29
2019-05-19 04:00 | 29.03 | 28.19
2019-05-19 04:30 | 28.98 | 28.14
2019-05-19 05:00 | 29.08 | 28.24
2019-05-19 05:30 | 29.68 | 28.87
2019-05-19 06:00 | 30.32 | 29.53
2019-05-19 06:30 | 31.21 | 30.44
2019-05-19 07:00 | 31.62 | 30.86
2019-05-19 07:30 | 33.4 | 32.68
2019-05-19 08:00 | 34.08 | 33.36
2019-05-19 08:30 | 34.78 | 34.06
2019-05-19 09:00 | 34.64 | 33.91
2019-05-19 09:30 | 36.04 | 35.33
2019-05-19 10:00 | 36.4 | 35.68
2019-05-19 10:30 | 34.83 | 34.07
2019-05-19 11:00 | 33.58 | 32.78
2019-05-19 11:30 | 32.66 | 31.83
2019-05-19 12:00 | 33.25 | 32.43
2019-05-19 12:30 | 33.15 | 32.32
2019-05-19 13:00 | 32.9 | 32.07
2019-05-19 13:30 | 33.12 | 32.3
2019-05-19 14:00 | 33.72 | 32.91
2019-05-19 14:30 | 34.78 | 34
2019-05-19 15:00 | 36.67 | 35.93
2019-05-19 15:30 | 37.44 | 36.73
2019-05-19 16:00 | 39.4 | 38.74
2019-05-19 16:30 | 41.64 | 41.03
2019-05-19 17:00 | 43.65 | 43.06
2019-05-19 17:30 | 45.44 | 44.88
2019-05-19 18:00 | 48.31 | 47.78
2019-05-19 18:30 | 49.87 | 49.36
2019-05-19 19:00 | 48.38 | 47.85
2019-05-19 19:30 | 46.27 | 45.72
2019-05-19 20:00 | 44.29 | 43.72
2019-05-19 20:30 | 42.43 | 41.84
2019-05-19 21:00 | 41.26 | 40.65
2019-05-19 21:30 | 39.43 | 38.8
2019-05-19 22:00 | 37.57 | 36.91
2019-05-19 22:30 | 35.28 | 34.58
2019-05-19 23:00 | 33.71 | 32.99
2019-05-19 23:30 | 32.48 | 31.72
2019-05-20 | 31.2 | 30.42
2019-05-20 00:30 | 30.38 | 29.58
2019-05-20 01:00 | 29.75 | 28.93
2019-05-20 01:30 | 29.23 | 28.39
2019-05-20 02:00 | 28.93 | 28.09
2019-05-20 02:30 | 28.86 | 28.02
2019-05-20 03:00 | 28.33 | 27.47
2019-05-20 03:30 | 28.73 | 27.89
2019-05-20 04:00 | 28.84 | 28
2019-05-20 04:30 | 30.06 | 29.24
2019-05-20 05:00 | 31.26 | 30.47
2019-05-20 05:30 | 33.72 | 32.99
2019-05-20 06:00 | 36.54 | 35.85
2019-05-20 06:30 | 41.4 | 40.76
2019-05-20 07:00 | 45.63 | 45.03
2019-05-20 07:30 | 50.53 | 49.96
2019-05-20 08:00 | 51.6 | 51.06
2019-05-20 08:30 | 51.6 | 50.89
2019-05-20 09:00 | 51.66 | 50.94
2019-05-20 09:30 | 52.03 | 51.5
2019-05-20 10:00 | 49.58 | 49.02
2019-05-20 10:30 | 48.56 | 47.94
2019-05-20 11:00 | 50.82 | 50.01
2019-05-20 11:30 | 50.7 | 49.8
2019-05-20 12:00 | 50.48 | 49.57
2019-05-20 12:30 | 51.3 | 50.41
2019-05-20 13:00 | 51.16 | 50.25
2019-05-20 13:30 | 51.34 | 50.44
2019-05-20 14:00 | 53.67 | 52.67
2019-05-20 14:30 | 56.66 | 55.71
2019-05-20 15:00 | 59.26 | 58.49
2019-05-20 15:30 | 59.05 | 58.42
2019-05-20 16:00 | 57.39 | 56.9
2019-05-20 16:30 | 56.15 | 55.68
2019-05-20 17:00 | 56.41 | 55.97
2019-05-20 17:30 | 53.6 | 53.16
2019-05-20 18:00 | 55.74 | 55.33
2019-05-20 18:30 | 56.34 | 55.94
2019-05-20 19:00 | 54.93 | 54.53
2019-05-20 19:30 | 52.33 | 51.91
2019-05-20 20:00 | 49.36 | 48.92
2019-05-20 20:30 | 46.93 | 46.48
2019-05-20 21:00 | 44.69 | 44.21
2019-05-20 21:30 | 42.86 | 42.37
2019-05-20 22:00 | 41.03 | 40.52
2019-05-20 22:30 | 38.72 | 38.08
2019-05-20 23:00 | 36.94 | 36.24
2019-05-20 23:30 | 35.46 | 34.73
2019-05-21 | 34.09 | 33.33
2019-05-21 00:30 | 32.83 | 32.05
2019-05-21 01:00 | 32.01 | 31.21
2019-05-21 01:30 | 31.58 | 30.77
2019-05-21 02:00 | 30.9 | 30.09
2019-05-21 02:30 | 30.65 | 29.83
2019-05-21 03:00 | 30.43 | 29.61
2019-05-21 03:30 | 30.45 | 29.62
2019-05-21 04:00 | 30.26 | 29.43
2019-05-21 04:30 | 31.37 | 30.57
2019-05-21 05:00 | 32.63 | 31.85
2019-05-21 05:30 | 35.22 | 34.49
2019-05-21 06:00 | 37.7 | 37.01
2019-05-21 06:30 | 42.41 | 41.77
2019-05-21 07:00 | 46.66 | 46
2019-05-21 07:30 | 52.3 | 51.73
2019-05-21 08:00 | 54.07 | 53.47
2019-05-21 08:30 | 54.49 | 53.61
2019-05-21 09:00 | 51.74 | 51.06
2019-05-21 09:30 | 51.34 | 50.78
2019-05-21 10:00 | 50.99 | 50.35
2019-05-21 10:30 | 53.06 | 52.32
2019-05-21 11:00 | 56.94 | 56.17
2019-05-21 11:30 | 53.83 | 52.99
2019-05-21 12:00 | 52.64 | 51.67
2019-05-21 12:30 | 51.12 | 50.6
2019-05-21 13:00 | 50.3 | 49.77
2019-05-21 13:30 | 51.12 | 50.59
2019-05-21 14:00 | 51.24 | 50.71
2019-05-21 14:30 | 52.06 | 51.55
2019-05-21 15:00 | 53.77 | 53.27
2019-05-21 15:30 | 55.5 | 55.03
2019-05-21 16:00 | 55.6 | 55.15
2019-05-21 16:30 | 55.13 | 54.7
2019-05-21 17:00 | 56.03 | 55.62
2019-05-21 17:30 | 55.64 | 55.26
2019-05-21 18:00 | 56.82 | 56.46
2019-05-21 18:30 | 57.03 | 56.68
2019-05-21 19:00 | 56.32 | 55.97
2019-05-21 19:30 | 53.53 | 53.16
2019-05-21 20:00 | 50.68 | 50.26
2019-05-21 20:30 | 47.98 | 47.53
2019-05-21 21:00 | 46.03 | 45.56
2019-05-21 21:30 | 44.08 | 43.6
2019-05-21 22:00 | 41.93 | 41.43
2019-05-21 22:30 | 39.64 | 39.06
2019-05-21 23:00 | 37.69 | 37.07
2019-05-21 23:30 | 35.83 | 35.12
2019-05-22 | 34.39 | 33.65
2019-05-22 00:30 | 33.26 | 32.49
2019-05-22 01:00 | 32.54 | 31.75
2019-05-22 01:30 | 31.45 | 30.65
2019-05-22 02:00 | 18.41 | 16.89
2019-05-22 02:30 | 30.61 | 29.79
2019-05-22 03:00 | 30.51 | 29.69
2019-05-22 03:30 | 30.66 | 29.84
2019-05-22 04:00 | 29.99 | 29.17
2019-05-22 04:30 | 30.68 | 29.88
2019-05-22 05:00 | 32.02 | 31.24
2019-05-22 05:30 | 35.06 | 34.34
2019-05-22 06:00 | 38.01 | 37.34
2019-05-22 06:30 | 42.45 | 41.82
2019-05-22 07:00 | 47.06 | 46.46
2019-05-22 07:30 | 52.53 | 51.99
2019-05-22 08:00 | 54.54 | 54.03
2019-05-22 08:30 | 53.47 | 52.8
2019-05-22 09:00 | 52.68 | 51.96
2019-05-22 09:30 | 54.43 | 53.93
2019-05-22 10:00 | 55.45 | 54.96
2019-05-22 10:30 | 56.46 | 55.97
2019-05-22 11:00 | 54.65 | 54.13
2019-05-22 11:30 | 55.46 | 54.88
2019-05-22 12:00 | 55.56 | 54.94
2019-05-22 12:30 | 57.27 | 56.77
2019-05-22 13:00 | 54.66 | 54.16
2019-05-22 13:30 | 56.22 | 55.74
2019-05-22 14:00 | 56.37 | 55.88
2019-05-22 14:30 | 56.56 | 56.07
2019-05-22 15:00 | 56.31 | 55.82
2019-05-22 15:30 | 55.53 | 55.04
2019-05-22 16:00 | 54.79 | 54.32
2019-05-22 16:30 | 54.58 | 54.13
2019-05-22 17:00 | 54.87 | 54.43
2019-05-22 17:30 | 54.52 | 54.1
2019-05-22 18:00 | 56.91 | 56.52
2019-05-22 18:30 | 57.77 | 57.39
2019-05-22 19:00 | 56.32 | 55.93
2019-05-22 19:30 | 53.49 | 53.09
2019-05-22 20:00 | 51.18 | 50.75
2019-05-22 20:30 | 49.04 | 48.6
2019-05-22 21:00 | 46.73 | 46.28
2019-05-22 21:30 | 43.96 | 43.5
2019-05-22 22:00 | 42.08 | 41.59
2019-05-22 22:30 | 40.01 | 39.46
2019-05-22 23:00 | 37.78 | 37.18
2019-05-22 23:30 | 35.42 | 34.78
2019-05-23 | 33.96 | 33.3
2019-05-23 00:30 | 32.47 | 31.78
2019-05-23 01:00 | 31.66 | 30.88
2019-05-23 01:30 | 31.19 | 30.41
2019-05-23 02:00 | 30.48 | 29.68
2019-05-23 02:30 | 30.59 | 29.79
2019-05-23 03:00 | 30.57 | 29.77
2019-05-23 03:30 | 30.66 | 29.86
2019-05-23 04:00 | 30.49 | 29.69
2019-05-23 04:30 | 31.35 | 30.57
2019-05-23 05:00 | 32.89 | 32.14
2019-05-23 05:30 | 35 | 34.29
2019-05-23 06:00 | 37.91 | 37.25
2019-05-23 06:30 | 42.27 | 41.65
2019-05-23 07:00 | 46.78 | 46.21
2019-05-23 07:30 | 52.11 | 51.62
2019-05-23 08:00 | 53.25 | 52.63
2019-05-23 08:30 | 53.01 | 51.8
2019-05-23 09:00 | 51.65 | 50.87
2019-05-23 09:30 | 50.48 | 49.75
2019-05-23 10:00 | 49.37 | 48.56
2019-05-23 10:30 | 49.02 | 48.39
2019-05-23 11:00 | 49.37 | 48.67
2019-05-23 11:30 | 49.35 | 48.58
2019-05-23 12:00 | 48.98 | 48.16
2019-05-23 12:30 | 50.16 | 49.35
2019-05-23 13:00 | 49.53 | 48.76
2019-05-23 13:30 | 49.62 | 48.83
2019-05-23 14:00 | 50.15 | 49.37
2019-05-23 14:30 | 50.97 | 50.21
2019-05-23 15:00 | 51.88 | 51.16
2019-05-23 15:30 | 53.18 | 52.56
2019-05-23 16:00 | 54.25 | 53.79
2019-05-23 16:30 | 54.63 | 54.25
2019-05-23 17:00 | 55.08 | 54.69
2019-05-23 17:30 | 54.25 | 53.81
2019-05-23 18:00 | 56 | 55.57
2019-05-23 18:30 | 57.63 | 57.21
2019-05-23 19:00 | 56.59 | 56.15
2019-05-23 19:30 | 55.57 | 55.11
2019-05-23 20:00 | 53.53 | 53.04
2019-05-23 20:30 | 50.15 | 49.62
2019-05-23 21:00 | 47.7 | 47.13
2019-05-23 21:30 | 44.92 | 44.36
2019-05-23 22:00 | 42.03 | 41.55
2019-05-23 22:30 | 39.17 | 38.62
2019-05-23 23:00 | 37.45 | 36.85
2019-05-23 23:30 | 35.37 | 34.74
2019-05-24 | 33.45 | 32.78
2019-05-24 00:30 | 32.06 | 31.34
2019-05-24 01:00 | 31.26 | 30.48
2019-05-24 01:30 | 31 | 30.21
2019-05-24 02:00 | 30.7 | 29.9
2019-05-24 02:30 | 30.4 | 29.6
2019-05-24 03:00 | 30.22 | 29.41
2019-05-24 03:30 | 30.19 | 29.39
2019-05-24 04:00 | 30.09 | 29.27
2019-05-24 04:30 | 30.61 | 29.82
2019-05-24 05:00 | 32.02 | 31.25
2019-05-24 05:30 | 34.86 | 34.15
2019-05-24 06:00 | 37.87 | 37.2
2019-05-24 06:30 | 42.07 | 41.45
2019-05-24 07:00 | 46.81 | 46.23
2019-05-24 07:30 | 52.77 | 52.27
2019-05-24 08:00 | 54.63 | 54.1
2019-05-24 08:30 | 54.02 | 53.27
2019-05-24 09:00 | 55.93 | 55.38
2019-05-24 09:30 | 54.23 | 53.75
2019-05-24 10:00 | 52.74 | 52.24
2019-05-24 10:30 | 51.98 | 51.45
2019-05-24 11:00 | 52.88 | 52.21
2019-05-24 11:30 | 53.26 | 52.61
2019-05-24 12:00 | 50.44 | 49.7
2019-05-24 12:30 | 51.59 | 50.92
2019-05-24 13:00 | 52.64 | 52.02
2019-05-24 13:30 | 49.62 | 48.94
2019-05-24 14:00 | 50.99 | 50.35
2019-05-24 14:30 | 51.86 | 51.33
2019-05-24 15:00 | 52.81 | 52.31
2019-05-24 15:30 | 52.88 | 52.4
2019-05-24 16:00 | 52.56 | 52.08
2019-05-24 16:30 | 50.95 | 50.48
2019-05-24 17:00 | 52.16 | 51.71
2019-05-24 17:30 | 52.19 | 51.76
2019-05-24 18:00 | 53.47 | 53.05
2019-05-24 18:30 | 53.03 | 52.62
2019-05-24 19:00 | 51.42 | 51
2019-05-24 19:30 | 49.14 | 48.71
2019-05-24 20:00 | 47.39 | 46.94
2019-05-24 20:30 | 45.71 | 45.25
2019-05-24 21:00 | 44.01 | 43.54
2019-05-24 21:30 | 42.05 | 41.56
2019-05-24 22:00 | 40.38 | 39.84
2019-05-24 22:30 | 38.69 | 38.12
2019-05-24 23:00 | 36.99 | 36.35
2019-05-24 23:30 | 35.27 | 34.57
2019-05-25 | 33.73 | 33.01
2019-05-25 00:30 | 32.52 | 31.77
2019-05-25 01:00 | 31.85 | 31.09
2019-05-25 01:30 | 31.09 | 30.31
2019-05-25 02:00 | 30.28 | 29.49
2019-05-25 02:30 | 29.75 | 28.94
2019-05-25 03:00 | 29.48 | 28.67
2019-05-25 03:30 | 29.35 | 28.53
2019-05-25 04:00 | 29.45 | 28.63
2019-05-25 04:30 | 29.58 | 28.77
2019-05-25 05:00 | 30.01 | 29.21
2019-05-25 05:30 | 31.36 | 30.6
2019-05-25 06:00 | 32.75 | 32.02
2019-05-25 06:30 | 35.04 | 34.34
2019-05-25 07:00 | 36.39 | 35.72
2019-05-25 07:30 | 39.05 | 38.4
2019-05-25 08:00 | 40.62 | 39.99
2019-05-25 08:30 | 42.53 | 41.91
2019-05-25 09:00 | 42.9 | 42.27
2019-05-25 09:30 | 41.33 | 40.67
2019-05-25 10:00 | 40.71 | 40.03
2019-05-25 10:30 | 40.09 | 39.35
2019-05-25 11:00 | 40.02 | 39.34
2019-05-25 11:30 | 39 | 38.32
2019-05-25 12:00 | 38.09 | 37.4
2019-05-25 12:30 | 37.64 | 36.95
2019-05-25 13:00 | 39 | 38.36
2019-05-25 13:30 | 38.88 | 38.25
2019-05-25 14:00 | 37.79 | 37.14
2019-05-25 14:30 | 37.88 | 37.24
2019-05-25 15:00 | 39.6 | 38.99
2019-05-25 15:30 | 39.79 | 39.18
2019-05-25 16:00 | 41.21 | 40.63
2019-05-25 16:30 | 41.71 | 41.16
2019-05-25 17:00 | 42.64 | 42.1
2019-05-25 17:30 | 44.88 | 44.37
2019-05-25 18:00 | 47.01 | 46.52
2019-05-25 18:30 | 47.31 | 46.82
2019-05-25 19:00 | 46.44 | 45.94
2019-05-25 19:30 | 44.67 | 44.15
2019-05-25 20:00 | 43.36 | 42.83
2019-05-25 20:30 | 41.57 | 41.02
2019-05-25 21:00 | 40.54 | 39.97
2019-05-25 21:30 | 39.37 | 38.79
2019-05-25 22:00 | 38.36 | 37.77
2019-05-25 22:30 | 36.71 | 36.08
2019-05-25 23:00 | 35.47 | 34.77
2019-05-25 23:30 | 34.34 | 33.62
2019-05-26 | 32.97 | 32.22
2019-05-26 00:30 | 31.67 | 30.89
2019-05-26 01:00 | 30.93 | 30.14
2019-05-26 01:30 | 30.42 | 29.62
2019-05-26 02:00 | 30.4 | 29.59
2019-05-26 02:30 | 29.84 | 29.02
2019-05-26 03:00 | 29.29 | 28.46
2019-05-26 03:30 | 29.08 | 28.24
2019-05-26 04:00 | 29.02 | 28.18
2019-05-26 04:30 | 29.68 | 28.86
2019-05-26 05:00 | 29.71 | 28.89
2019-05-26 05:30 | 30.36 | 29.56
2019-05-26 06:00 | 30.79 | 30
2019-05-26 06:30 | 32.09 | 31.33
2019-05-26 07:00 | 32.25 | 31.5
2019-05-26 07:30 | 34.17 | 33.46
2019-05-26 08:00 | 35.38 | 34.69
2019-05-26 08:30 | 36.89 | 36.21
2019-05-26 09:00 | 36.65 | 35.95
2019-05-26 09:30 | 36.55 | 35.84
2019-05-26 10:00 | 36.99 | 36.27
2019-05-26 10:30 | 36.78 | 36.04
2019-05-26 11:00 | 36.25 | 35.49
2019-05-26 11:30 | 35.29 | 34.51
2019-05-26 12:00 | 34.89 | 34.09
2019-05-26 12:30 | 34.66 | 33.86
2019-05-26 13:00 | 33.91 | 33.09
2019-05-26 13:30 | 35.46 | 34.76
2019-05-26 14:00 | 35.43 | 34.73
2019-05-26 14:30 | 35.68 | 34.99
2019-05-26 15:00 | 37.17 | 36.51
2019-05-26 15:30 | 38.39 | 37.77
2019-05-26 16:00 | 40.37 | 39.79
2019-05-26 16:30 | 42.31 | 41.76
2019-05-26 17:00 | 44.98 | 44.47
2019-05-26 17:30 | 46.88 | 46.4
2019-05-26 18:00 | 51.05 | 50.59
2019-05-26 18:30 | 52.42 | 51.97
2019-05-26 19:00 | 50.79 | 50.33
2019-05-26 19:30 | 48.39 | 47.92
2019-05-26 20:00 | 46.55 | 46.06
2019-05-26 20:30 | 44.79 | 44.28
2019-05-26 21:00 | 43.22 | 42.69
2019-05-26 21:30 | 41.47 | 40.92
2019-05-26 22:00 | 38.89 | 38.25
2019-05-26 22:30 | 37.13 | 36.46
2019-05-26 23:00 | 35.43 | 34.74
2019-05-26 23:30 | 34.25 | 33.53
2019-05-27 | 33.2 | 32.45
2019-05-27 00:30 | 32.35 | 31.59
2019-05-27 01:00 | 31.79 | 31.01
2019-05-27 01:30 | 31.2 | 30.41
2019-05-27 02:00 | 30.99 | 30.2
2019-05-27 02:30 | 30.9 | 30.1
2019-05-27 03:00 | 30.71 | 29.91
2019-05-27 03:30 | 31.18 | 30.39
2019-05-27 04:00 | 31.51 | 30.72
2019-05-27 04:30 | 32.94 | 32.18
2019-05-27 05:00 | 34.02 | 33.29
2019-05-27 05:30 | 36.46 | 35.77
2019-05-27 06:00 | 39.26 | 38.6
2019-05-27 06:30 | 44.1 | 43.48
2019-05-27 07:00 | 48.54 | 47.99
2019-05-27 07:30 | 53.92 | 53.41
2019-05-27 08:00 | 55.91 | 55.29
2019-05-27 08:30 | 56.91 | 56.01
2019-05-27 09:00 | 57.9 | 57.39
2019-05-27 09:30 | 57.01 | 56.47
2019-05-27 10:00 | 58.38 | 57.75
2019-05-27 10:30 | 59.65 | 58.93
2019-05-27 11:00 | 57.78 | 56.96
2019-05-27 11:30 | 58.28 | 57.35
2019-05-27 12:00 | 59.11 | 58.05
2019-05-27 12:30 | 58.77 | 57.82
2019-05-27 13:00 | 57.57 | 56.84
2019-05-27 13:30 | 59.77 | 59.06
2019-05-27 14:00 | 59.46 | 58.72
2019-05-27 14:30 | 60.48 | 59.74
2019-05-27 15:00 | 58.09 | 57.46
2019-05-27 15:30 | 57.85 | 57.29
2019-05-27 16:00 | 58.26 | 57.85
2019-05-27 16:30 | 57.76 | 57.54
2019-05-27 17:00 | 57 | 56.89
2019-05-27 17:30 | 56.86 | 56.83
2019-05-27 18:00 | 58.62 | 58.6
2019-05-27 18:30 | 58.23 | 58.23
2019-05-27 19:00 | 56.76 | 56.76
2019-05-27 19:30 | 54.32 | 54.31
2019-05-27 20:00 | 51.82 | 51.8
2019-05-27 20:30 | 48.71 | 48.64
2019-05-27 21:00 | 46.9 | 46.81
2019-05-27 21:30 | 44.75 | 44.58
2019-05-27 22:00 | 42.59 | 42.35
2019-05-27 22:30 | 41.43 | 39.56
2019-05-27 23:00 | 39.69 | 37.24
2019-05-27 23:30 | 38.45 | 35.92
2019-05-28 | 37.13 | 34.5
2019-05-28 00:30 | 35.78 | 33.04
2019-05-28 01:00 | 35.13 | 32.34
2019-05-28 01:30 | 34.85 | 32.02
2019-05-28 02:00 | 34.47 | 31.62
2019-05-28 02:30 | 34.11 | 31.24
2019-05-28 03:00 | 34.21 | 31.34
2019-05-28 03:30 | 34.04 | 31.15
2019-05-28 04:00 | 34.05 | 31.16
2019-05-28 04:30 | 35.23 | 32.43
2019-05-28 05:00 | 36.67 | 33.98
2019-05-28 05:30 | 39.45 | 36.95
2019-05-28 06:00 | 41.6 | 39.24
2019-05-28 06:30 | 45.81 | 43.65
2019-05-28 07:00 | 49.94 | 48.02
2019-05-28 07:30 | 54.89 | 53.14
2019-05-28 08:00 | 55.64 | 53.87
2019-05-28 08:30 | 54.67 | 53.69
2019-05-28 09:00 | 53.5 | 52.72
2019-05-28 09:30 | 53.61 | 53.07
2019-05-28 10:00 | 52.39 | 51.8
2019-05-28 10:30 | 50.79 | 50.08
2019-05-28 11:00 | 50.57 | 49.77
2019-05-28 11:30 | 50.71 | 49.85
2019-05-28 12:00 | 50.22 | 49.33
2019-05-28 12:30 | 49.61 | 48.8
2019-05-28 13:00 | 49.84 | 49.05
2019-05-28 13:30 | 50.01 | 49.2
2019-05-28 14:00 | 51 | 50.21
2019-05-28 14:30 | 51.67 | 50.94
2019-05-28 15:00 | 51.8 | 51.18
2019-05-28 15:30 | 52.69 | 52.16
2019-05-28 16:00 | 53.94 | 53.58
2019-05-28 16:30 | 53.64 | 53.46
2019-05-28 17:00 | 54.46 | 54.38
2019-05-28 17:30 | 54.09 | 54.08
2019-05-28 18:00 | 56.34 | 56.34
2019-05-28 18:30 | 56.97 | 56.97
2019-05-28 19:00 | 55.99 | 55.99
2019-05-28 19:30 | 53.55 | 53.55
2019-05-28 20:00 | 51.43 | 51.41
2019-05-28 20:30 | 48.68 | 48.61
2019-05-28 21:00 | 46.55 | 46.43
2019-05-28 21:30 | 44.56 | 44.38
2019-05-28 22:00 | 41.8 | 41.72
2019-05-28 22:30 | 39.05 | 39.03
2019-05-28 23:00 | 36.89 | 36.84
2019-05-28 23:30 | 35.12 | 35.05
2019-05-29 | 34.46 | 33.19
2019-05-29 00:30 | 34.71 | 32.02
2019-05-29 01:00 | 34.37 | 31.62
2019-05-29 01:30 | 34.27 | 31.38
2019-05-29 02:00 | 33.68 | 30.77
2019-05-29 02:30 | 32.92 | 29.93
2019-05-29 03:00 | 32.85 | 29.85
2019-05-29 03:30 | 32.92 | 29.92
2019-05-29 04:00 | 32.91 | 29.92
2019-05-29 04:30 | 33.92 | 31.03
2019-05-29 05:00 | 35.2 | 32.41
2019-05-29 05:30 | 37.63 | 35.03
2019-05-29 06:00 | 40.43 | 38.01
2019-05-29 06:30 | 44.65 | 42.44
2019-05-29 07:00 | 48.76 | 46.78
2019-05-29 07:30 | 54.08 | 52.31
2019-05-29 08:00 | 55.38 | 53.62
2019-05-29 08:30 | 55.59 | 53.8
2019-05-29 09:00 | 53.59 | 51.69
2019-05-29 09:30 | 53.6 | 51.73
2019-05-29 10:00 | 54.66 | 52.86
2019-05-29 10:30 | 52.48 | 50.56
2019-05-29 11:00 | 30.1 | 26.32
2019-05-29 11:30 | 52.56 | 51.5
2019-05-29 12:00 | 53.47 | 52.36
2019-05-29 12:30 | 52.95 | 51.86
2019-05-29 13:00 | 52.42 | 51.39
2019-05-29 13:30 | 52.78 | 51.77
2019-05-29 14:00 | 53.3 | 52.34
2019-05-29 14:30 | 54.13 | 53.19
2019-05-29 15:00 | 55.01 | 54.14
2019-05-29 15:30 | 56.07 | 55.35
2019-05-29 16:00 | 58.09 | 57.58
2019-05-29 16:30 | 56.67 | 56.21
2019-05-29 17:00 | 56.3 | 55.85
2019-05-29 17:30 | 55.74 | 55.31
2019-05-29 18:00 | 57.48 | 57.07
2019-05-29 18:30 | 58.09 | 57.7
2019-05-29 19:00 | 56.42 | 56.03
2019-05-29 19:30 | 53.69 | 53.27
2019-05-29 20:00 | 51.69 | 51.26
2019-05-29 20:30 | 49.21 | 48.77
2019-05-29 21:00 | 47.42 | 46.96
2019-05-29 21:30 | 45.09 | 44.62
2019-05-29 22:00 | 42.31 | 41.79
2019-05-29 22:30 | 39.87 | 39.28
2019-05-29 23:00 | 37.83 | 37.21
2019-05-29 23:30 | 36.3 | 35.66
2019-05-30 | 34.68 | 34.02
2019-05-30 00:30 | 33.17 | 32.48
2019-05-30 01:00 | 32.73 | 32.03
2019-05-30 01:30 | 32.45 | 31.75
2019-05-30 02:00 | 32.01 | 31.3
2019-05-30 02:30 | 31.29 | 30.57
2019-05-30 03:00 | 30.88 | 30.15
2019-05-30 03:30 | 31.17 | 30.46
2019-05-30 04:00 | 31.28 | 30.52
2019-05-30 04:30 | 31.83 | 31.07
2019-05-30 05:00 | 33.53 | 32.8
2019-05-30 05:30 | 36.1 | 35.42
2019-05-30 06:00 | 38.49 | 37.83
2019-05-30 06:30 | 42.81 | 42.2
2019-05-30 07:00 | 47.19 | 46.65
2019-05-30 07:30 | 51.27 | 50.78
2019-05-30 08:00 | 52.88 | 52.38
2019-05-30 08:30 | 52.75 | 52.09
2019-05-30 09:00 | 53.75 | 52.89
2019-05-30 09:30 | 54.2 | 53.71
2019-05-30 10:00 | 53.15 | 52.65
2019-05-30 10:30 | 52.82 | 52.16
2019-05-30 11:00 | 54.62 | 53.8
2019-05-30 11:30 | 56.44 | 55.57
2019-05-30 12:00 | 56.22 | 55.33
2019-05-30 12:30 | 54.27 | 53.38
2019-05-30 13:00 | 57.9 | 57.1
2019-05-30 13:30 | 59.16 | 58.4
2019-05-30 14:00 | 57.56 | 56.76
2019-05-30 14:30 | 55.6 | 54.74
2019-05-30 15:00 | 56.23 | 55.46
2019-05-30 15:30 | 58.09 | 57.46
2019-05-30 16:00 | 58.04 | 57.56
2019-05-30 16:30 | 57.03 | 56.66
2019-05-30 17:00 | 57.17 | 56.78
2019-05-30 17:30 | 57.01 | 56.6
2019-05-30 18:00 | 59.52 | 59.13
2019-05-30 18:30 | 59.71 | 59.31
2019-05-30 19:00 | 56.91 | 56.48
2019-05-30 19:30 | 54.28 | 53.81
2019-05-30 20:00 | 51.84 | 51.33
2019-05-30 20:30 | 49.36 | 48.83
2019-05-30 21:00 | 48.2 | 47.65
2019-05-30 21:30 | 45.89 | 45.29
2019-05-30 22:00 | 43.12 | 42.51
2019-05-30 22:30 | 39.84 | 39.33
2019-05-30 23:00 | 38.07 | 37.53
2019-05-30 23:30 | 36.14 | 35.44
2019-05-31 | 34.34 | 33.61
2019-05-31 00:30 | 32.65 | 31.89
2019-05-31 01:00 | 32.2 | 31.43
2019-05-31 01:30 | 31.72 | 30.94
2019-05-31 02:00 | 31.03 | 30.24
2019-05-31 02:30 | 30.49 | 29.69
2019-05-31 03:00 | 30.15 | 29.35
2019-05-31 03:30 | 30.41 | 29.61
2019-05-31 04:00 | 30.9 | 30.11
2019-05-31 04:30 | 31.13 | 30.34
2019-05-31 05:00 | 32.02 | 31.25
2019-05-31 05:30 | 34.34 | 33.63
2019-05-31 06:00 | 37.02 | 36.34
2019-05-31 06:30 | 41.66 | 41.03
2019-05-31 07:00 | 45.82 | 45.25
2019-05-31 07:30 | 51.65 | 51.14
2019-05-31 08:00 | 54.41 | 53.91
2019-05-31 08:30 | 55.79 | 55.27
2019-05-31 09:00 | 56 | 55.35
2019-05-31 09:30 | 55.37 | 54.76
2019-05-31 10:00 | 53.65 | 53.08
2019-05-31 10:30 | 54.79 | 54.18
2019-05-31 11:00 | 55.05 | 54.39
2019-05-31 11:30 | 53.24 | 52.56
2019-05-31 12:00 | 53.71 | 53.05
2019-05-31 12:30 | 52.92 | 52.36
2019-05-31 13:00 | 52.55 | 52
2019-05-31 13:30 | 51.52 | 50.96
2019-05-31 14:00 | 50.99 | 50.43
2019-05-31 14:30 | 50.57 | 50.02
2019-05-31 15:00 | 50.4 | 49.86
2019-05-31 15:30 | 49.89 | 49.34
2019-05-31 16:00 | 50.05 | 49.52
2019-05-31 16:30 | 50.54 | 50.03
2019-05-31 17:00 | 50.92 | 50.42
2019-05-31 17:30 | 51.56 | 51.08
2019-05-31 18:00 | 53.34 | 52.87
2019-05-31 18:30 | 51.75 | 51.29
2019-05-31 19:00 | 50.43 | 49.96
2019-05-31 19:30 | 48.59 | 48.09
2019-05-31 20:00 | 46.26 | 45.7
2019-05-31 20:30 | 44 | 43.41
2019-05-31 21:00 | 42.52 | 41.91
2019-05-31 21:30 | 41.23 | 40.61
2019-05-31 22:00 | 38.96 | 38.3
2019-05-31 22:30 | 36.82 | 36.14
2019-05-31 23:00 | 34.96 | 34.24
2019-05-31 23:30 | 33.63 | 32.88
2019-06-01 | 31.65 | 31.11
2019-06-01 00:30 | 29.42 | 29.39
2019-06-01 01:00 | 28.85 | 28.82
2019-06-01 01:30 | 28.2 | 28.17
2019-06-01 02:00 | 27.95 | 27.92
2019-06-01 02:30 | 27.38 | 27.34
2019-06-01 03:00 | 27.06 | 27.01
2019-06-01 03:30 | 27.15 | 27.09
2019-06-01 04:00 | 27.09 | 27.03
2019-06-01 04:30 | 27.66 | 27.62
2019-06-01 05:00 | 27.98 | 27.94
2019-06-01 05:30 | 29.66 | 29.63
2019-06-01 06:00 | 30.61 | 30.6
2019-06-01 06:30 | 33.05 | 33.05
2019-06-01 07:00 | 35.01 | 35
2019-06-01 07:30 | 37.81 | 37.79
2019-06-01 08:00 | 39.15 | 39.11
2019-06-01 08:30 | 40.66 | 40.58
2019-06-01 09:00 | 41.64 | 41.53
2019-06-01 09:30 | 40.3 | 40.16
2019-06-01 10:00 | 40.38 | 40.22
2019-06-01 10:30 | 39.87 | 39.68
2019-06-01 11:00 | 39.74 | 39.55
2019-06-01 11:30 | 40.13 | 39.94
2019-06-01 12:00 | 38.84 | 38.66
2019-06-01 12:30 | 36.48 | 36.35
2019-06-01 13:00 | 33.15 | 33.05
2019-06-01 13:30 | 32.07 | 31.96
2019-06-01 14:00 | 31.3 | 31.17
2019-06-01 14:30 | 32.81 | 32.72
2019-06-01 15:00 | 35.35 | 35.3
2019-06-01 15:30 | 35.36 | 35.33
2019-06-01 16:00 | 38.65 | 38.61
2019-06-01 16:30 | 40 | 39.98
2019-06-01 17:00 | 41.23 | 41.21
2019-06-01 17:30 | 43.55 | 43.5
2019-06-01 18:00 | 46.76 | 46.67
2019-06-01 18:30 | 46.58 | 46.51
2019-06-01 19:00 | 44.76 | 44.71
2019-06-01 19:30 | 43.46 | 43.4
2019-06-01 20:00 | 41.61 | 41.58
2019-06-01 20:30 | 39.97 | 39.95
2019-06-01 21:00 | 38.79 | 38.78
2019-06-01 21:30 | 37.42 | 37.41
2019-06-01 22:00 | 36.08 | 36.08
2019-06-01 22:30 | 34.41 | 34.41
2019-06-01 23:00 | 32.73 | 32.72
2019-06-01 23:30 | 31.65 | 31.64
2019-06-02 | 30.13 | 30.11
2019-06-02 00:30 | 28.67 | 28.62
2019-06-02 01:00 | 27.97 | 27.93
2019-06-02 01:30 | 27.78 | 27.74
2019-06-02 02:00 | 26.89 | 26.84
2019-06-02 02:30 | 26.72 | 26.67
2019-06-02 03:00 | 26.45 | 26.38
2019-06-02 03:30 | 26.53 | 26.47
2019-06-02 04:00 | 26.45 | 26.39
2019-06-02 04:30 | 26.91 | 26.86
2019-06-02 05:00 | 27.23 | 27.19
2019-06-02 05:30 | 28.01 | 27.94
2019-06-02 06:00 | 28.75 | 28.7
2019-06-02 06:30 | 29.98 | 29.94
2019-06-02 07:00 | 30.62 | 30.58
2019-06-02 07:30 | 32.7 | 32.68
2019-06-02 08:00 | 33.27 | 33.25
2019-06-02 08:30 | 34.75 | 34.75
2019-06-02 09:00 | 35.93 | 35.93
2019-06-02 09:30 | 36.83 | 36.82
2019-06-02 10:00 | 35.9 | 35.9
2019-06-02 10:30 | 37.29 | 37.26
2019-06-02 11:00 | 38.79 | 38.75
2019-06-02 11:30 | 37.56 | 37.51
2019-06-02 12:00 | 36.45 | 36.4
2019-06-02 12:30 | 37 | 36.95
2019-06-02 13:00 | 38.07 | 38.02
2019-06-02 13:30 | 34.57 | 34.51
2019-06-02 14:00 | 34.6 | 34.54
2019-06-02 14:30 | 36.17 | 36.13
2019-06-02 15:00 | 36.46 | 36.42
2019-06-02 15:30 | 36.37 | 36.34
2019-06-02 16:00 | 37.51 | 37.48
2019-06-02 16:30 | 37.92 | 37.9
2019-06-02 17:00 | 39.32 | 39.31
2019-06-02 17:30 | 41.82 | 41.79
2019-06-02 18:00 | 46.62 | 46.33
2019-06-02 18:30 | 50.05 | 48.26
2019-06-02 19:00 | 48.58 | 46.73
2019-06-02 19:30 | 46.61 | 44.65
2019-06-02 20:00 | 44.53 | 42.44
2019-06-02 20:30 | 42.55 | 40.33
2019-06-02 21:00 | 40.97 | 38.64
2019-06-02 21:30 | 39.95 | 37.54
2019-06-02 22:00 | 38.18 | 35.62
2019-06-02 22:30 | 35.95 | 33.18
2019-06-02 23:00 | 34.35 | 31.42
2019-06-02 23:30 | 33.01 | 29.92
2019-06-03 | 31.98 | 28.77
2019-06-03 00:30 | 31.1 | 27.77
2019-06-03 01:00 | 30.54 | 27.13
2019-06-03 01:30 | 30.46 | 27.03
2019-06-03 02:00 | 30.05 | 26.56
2019-06-03 02:30 | 29.85 | 26.34
2019-06-03 03:00 | 29.92 | 26.41
2019-06-03 03:30 | 30.03 | 26.53
2019-06-03 04:00 | 30.11 | 26.63
2019-06-03 04:30 | 31.24 | 27.93
2019-06-03 05:00 | 32.75 | 29.65
2019-06-03 05:30 | 35.14 | 32.3
2019-06-03 06:00 | 37.54 | 34.96
2019-06-03 06:30 | 41.92 | 39.72
2019-06-03 07:00 | 45.58 | 43.64
2019-06-03 07:30 | 51.16 | 49.47
2019-06-03 08:00 | 52.02 | 50.34
2019-06-03 08:30 | 52.02 | 50.39
2019-06-03 09:00 | 50.43 | 48.77
2019-06-03 09:30 | 49.14 | 47.46
2019-06-03 10:00 | 47.88 | 46.14
2019-06-03 10:30 | 48.44 | 46.76
2019-06-03 11:00 | 48.36 | 46.66
2019-06-03 11:30 | 49.76 | 48.05
2019-06-03 12:00 | 48.43 | 46.68
2019-06-03 12:30 | 46.98 | 45.19
2019-06-03 13:00 | 48.07 | 46.32
2019-06-03 13:30 | 47.92 | 46.17
2019-06-03 14:00 | 48.24 | 46.51
2019-06-03 14:30 | 49.22 | 47.52
2019-06-03 15:00 | 49.82 | 48.13
2019-06-03 15:30 | 50.6 | 48.91
2019-06-03 16:00 | 51.83 | 50.15
2019-06-03 16:30 | 52.64 | 50.94
2019-06-03 17:00 | 53.56 | 51.85
2019-06-03 17:30 | 54.29 | 52.56
2019-06-03 18:00 | 56.7 | 55.05
2019-06-03 18:30 | 57.29 | 55.64
2019-06-03 19:00 | 56.1 | 54.4
2019-06-03 19:30 | 53.51 | 51.69
2019-06-03 20:00 | 51.17 | 49.22
2019-06-03 20:30 | 48.8 | 46.73
2019-06-03 21:00 | 46.72 | 44.53
2019-06-03 21:30 | 44.71 | 42.53
2019-06-03 22:00 | 42.58 | 40.27
2019-06-03 22:30 | 40.16 | 37.67
2019-06-03 23:00 | 37.98 | 35.3
2019-06-03 23:30 | 36.55 | 33.75
2019-06-04 | 35.26 | 32.32
2019-06-04 00:30 | 34.22 | 31.15
2019-06-04 01:00 | 33.88 | 30.77
2019-06-04 01:30 | 33.46 | 30.3
2019-06-04 02:00 | 33.1 | 29.88
2019-06-04 02:30 | 32.79 | 29.54
2019-06-04 03:00 | 32.27 | 29.15
2019-06-04 03:30 | 31.91 | 28.76
2019-06-04 04:00 | 31.48 | 28.24
2019-06-04 04:30 | 32.18 | 29.03
2019-06-04 05:00 | 33.53 | 30.55
2019-06-04 05:30 | 36.02 | 33.32
2019-06-04 06:00 | 38.57 | 36.1
2019-06-04 06:30 | 43.26 | 41.17
2019-06-04 07:00 | 47.97 | 46.11
2019-06-04 07:30 | 52.09 | 50.38
2019-06-04 08:00 | 53.05 | 51.42
2019-06-04 08:30 | 51.53 | 49.88
2019-06-04 09:00 | 48.34 | 46.57
2019-06-04 09:30 | 46.37 | 44.54
2019-06-04 10:00 | 45.05 | 43.16
2019-06-04 10:30 | 43.58 | 41.65
2019-06-04 11:00 | 42.57 | 40.6
2019-06-04 11:30 | 42.81 | 40.88
2019-06-04 12:00 | 42.04 | 40.08
2019-06-04 12:30 | 41.66 | 39.67
2019-06-04 13:00 | 40.97 | 38.92
2019-06-04 13:30 | 42.21 | 40.23
2019-06-04 14:00 | 43.42 | 41.52
2019-06-04 14:30 | 44.79 | 42.95
2019-06-04 15:00 | 47.12 | 45.36
2019-06-04 15:30 | 47.28 | 45.48
2019-06-04 16:00 | 48.93 | 47.16
2019-06-04 16:30 | 49.4 | 47.59
2019-06-04 17:00 | 51.83 | 50.08
2019-06-04 17:30 | 53.02 | 51.27
2019-06-04 18:00 | 57.21 | 55.62
2019-06-04 18:30 | 57.63 | 56.03
2019-06-04 19:00 | 56.41 | 54.83
2019-06-04 19:30 | 53.56 | 51.92
2019-06-04 20:00 | 51.78 | 50.07
2019-06-04 20:30 | 49.43 | 47.6
2019-06-04 21:00 | 47.39 | 45.45
2019-06-04 21:30 | 46.21 | 44.2
2019-06-04 22:00 | 43.5 | 41.33
2019-06-04 22:30 | 40.84 | 38.48
2019-06-04 23:00 | 38.78 | 36.26
2019-06-04 23:30 | 37.47 | 34.84
2019-06-05 | 35.88 | 33.1
2019-06-05 00:30 | 34.82 | 31.91
2019-06-05 01:00 | 34.41 | 31.46
2019-06-05 01:30 | 33.93 | 30.92
2019-06-05 02:00 | 33.3 | 30.23
2019-06-05 02:30 | 33.06 | 29.94
2019-06-05 03:00 | 32.93 | 29.78
2019-06-05 03:30 | 33.1 | 29.97
2019-06-05 04:00 | 32.99 | 29.84
2019-06-05 04:30 | 34.17 | 31.16
2019-06-05 05:00 | 35.61 | 32.76
2019-06-05 05:30 | 38.48 | 35.92
2019-06-05 06:00 | 41.53 | 39.22
2019-06-05 06:30 | 46.4 | 44.44
2019-06-05 07:00 | 50.94 | 49.2
2019-06-05 07:30 | 54.68 | 53.02
2019-06-05 08:00 | 48.13 | 46.23
2019-06-05 08:30 | 40.53 | 38.21
2019-06-05 09:00 | 38.07 | 35.6
2019-06-05 09:30 | 36.3 | 33.71
2019-06-05 10:00 | 36.67 | 34.1
2019-06-05 10:30 | 35.2 | 32.53
2019-06-05 11:00 | 35.75 | 33.13
2019-06-05 11:30 | 35.13 | 32.47
2019-06-05 12:00 | 35.39 | 32.8
2019-06-05 12:30 | 35.12 | 32.52
2019-06-05 13:00 | 35.47 | 32.91
2019-06-05 13:30 | 34.41 | 31.75
2019-06-05 14:00 | 35.45 | 32.9
2019-06-05 14:30 | 34.78 | 32.2
2019-06-05 15:00 | 33.49 | 30.82
2019-06-05 15:30 | 46.05 | 44.18
2019-06-05 16:00 | 51.02 | 49.35
2019-06-05 16:30 | 48.92 | 47.11
2019-06-05 17:00 | 50.31 | 48.52
2019-06-05 17:30 | 53.93 | 52.36
2019-06-05 18:00 | 57.95 | 56.55
2019-06-05 18:30 | 58.55 | 57.16
2019-06-05 19:00 | 56.97 | 55.49
2019-06-05 19:30 | 54.31 | 52.73
2019-06-05 20:00 | 52.23 | 50.56
2019-06-05 20:30 | 49.34 | 47.51
2019-06-05 21:00 | 46.45 | 44.47
2019-06-05 21:30 | 45.01 | 42.93
2019-06-05 22:00 | 43.08 | 40.88
2019-06-05 22:30 | 40.75 | 38.39
2019-06-05 23:00 | 39.46 | 36.99
2019-06-05 23:30 | 37.74 | 35.13
2019-06-06 | 35.5 | 32.68
2019-06-06 00:30 | 33.91 | 30.92
2019-06-06 01:00 | 33.21 | 30.12
2019-06-06 01:30 | 32.68 | 29.59
2019-06-06 02:00 | 32.17 | 29.03
2019-06-06 02:30 | 31.85 | 28.65
2019-06-06 03:00 | 31.68 | 28.45
2019-06-06 03:30 | 31.58 | 28.33
2019-06-06 04:00 | 31.48 | 28.23
2019-06-06 04:30 | 32.6 | 29.49
2019-06-06 05:00 | 33.76 | 30.81
2019-06-06 05:30 | 36.41 | 33.73
2019-06-06 06:00 | 39.13 | 36.66
2019-06-06 06:30 | 43.57 | 41.44
2019-06-06 07:00 | 48.27 | 46.44
2019-06-06 07:30 | 53.88 | 52.27
2019-06-06 08:00 | 55.76 | 54.2
2019-06-06 08:30 | 53.99 | 52.39
2019-06-06 09:00 | 52.22 | 50.58
2019-06-06 09:30 | 51.45 | 49.77
2019-06-06 10:00 | 50 | 48.27
2019-06-06 10:30 | 46.37 | 44.53
2019-06-06 11:00 | 46.05 | 44.22
2019-06-06 11:30 | 45.54 | 43.69
2019-06-06 12:00 | 47.25 | 45.48
2019-06-06 12:30 | 46.24 | 44.41
2019-06-06 13:00 | 43.96 | 42.03
2019-06-06 13:30 | 42.54 | 40.52
2019-06-06 14:00 | 42.67 | 40.68
2019-06-06 14:30 | 43.52 | 41.59
2019-06-06 15:00 | 46.53 | 44.73
2019-06-06 15:30 | 48.81 | 47.07
2019-06-06 16:00 | 49.31 | 47.56
2019-06-06 16:30 | 50.17 | 48.39
2019-06-06 17:00 | 51.91 | 50.16
2019-06-06 17:30 | 53.95 | 52.26
2019-06-06 18:00 | 57.56 | 56.02
2019-06-06 18:30 | 57.56 | 55.99
2019-06-06 19:00 | 55.03 | 53.37
2019-06-06 19:30 | 53.2 | 51.46
2019-06-06 20:00 | 51.28 | 49.45
2019-06-06 20:30 | 48.77 | 46.81
2019-06-06 21:00 | 47.23 | 45.17
2019-06-06 21:30 | 45.04 | 42.84
2019-06-06 22:00 | 42.57 | 40.2
2019-06-06 22:30 | 40.37 | 37.86
2019-06-06 23:00 | 37.61 | 34.89
2019-06-06 23:30 | 36.64 | 33.83
2019-06-07 | 34.95 | 31.95
2019-06-07 00:30 | 33.73 | 30.57
2019-06-07 01:00 | 33.2 | 29.98
2019-06-07 01:30 | 32.18 | 28.97
2019-06-07 02:00 | 31.47 | 28.32
2019-06-07 02:30 | 30.96 | 27.7
2019-06-07 03:00 | 30.45 | 27.11
2019-06-07 03:30 | 30.55 | 27.22
2019-06-07 04:00 | 31.37 | 28.13
2019-06-07 04:30 | 31.76 | 28.59
2019-06-07 05:00 | 32.95 | 29.94
2019-06-07 05:30 | 35.04 | 32.27
2019-06-07 06:00 | 38.82 | 36.39
2019-06-07 06:30 | 43.18 | 41.1
2019-06-07 07:00 | 47.02 | 45.19
2019-06-07 07:30 | 51.89 | 50.27
2019-06-07 08:00 | 54.35 | 52.78
2019-06-07 08:30 | 53.82 | 52.26
2019-06-07 09:00 | 52.76 | 51.17
2019-06-07 09:30 | 54.06 | 52.52
2019-06-07 10:00 | 54.96 | 53.46
2019-06-07 10:30 | 52.64 | 51.07
2019-06-07 11:00 | 53.68 | 52.16
2019-06-07 11:30 | 53.32 | 51.8
2019-06-07 12:00 | 51.15 | 49.56
2019-06-07 12:30 | 49.66 | 48.01
2019-06-07 13:00 | 49.29 | 47.61
2019-06-07 13:30 | 52.1 | 50.51
2019-06-07 14:00 | 49.93 | 48.27
2019-06-07 14:30 | 49.99 | 48.31
2019-06-07 15:00 | 51.07 | 49.41
2019-06-07 15:30 | 49.8 | 48.06
2019-06-07 16:00 | 49.47 | 47.71
2019-06-07 16:30 | 50.64 | 48.88
2019-06-07 17:00 | 51.03 | 49.27
2019-06-07 17:30 | 52.37 | 50.63
2019-06-07 18:00 | 54.7 | 53.06
2019-06-07 18:30 | 53.9 | 52.21
2019-06-07 19:00 | 53.59 | 51.87
2019-06-07 19:30 | 51.78 | 49.98
2019-06-07 20:00 | 49.46 | 47.55
2019-06-07 20:30 | 46.94 | 45.03
2019-06-07 21:00 | 44.57 | 42.53
2019-06-07 21:30 | 42.1 | 39.9
2019-06-07 22:00 | 40.23 | 37.88
2019-06-07 22:30 | 38.51 | 36.02
2019-06-07 23:00 | 37.33 | 34.74
2019-06-07 23:30 | 36.04 | 33.3
2019-06-08 | 34.63 | 31.75
2019-06-08 00:30 | 32.65 | 29.54
2019-06-08 01:00 | 31.59 | 28.35
2019-06-08 01:30 | 31.23 | 27.94
2019-06-08 02:00 | 30.61 | 27.24
2019-06-08 02:30 | 30.43 | 27.03
2019-06-08 03:00 | 30.05 | 26.59
2019-06-08 03:30 | 30.32 | 26.89
2019-06-08 04:00 | 29.68 | 26.16
2019-06-08 04:30 | 30.5 | 27.09
2019-06-08 05:00 | 30.52 | 27.13
2019-06-08 05:30 | 31.76 | 28.55
2019-06-08 06:00 | 32.96 | 29.91
2019-06-08 06:30 | 35.31 | 32.53
2019-06-08 07:00 | 37.11 | 34.51
2019-06-08 07:30 | 37.85 | 35.32
2019-06-08 08:00 | 39.4 | 37.02
2019-06-08 08:30 | 41.81 | 39.63
2019-06-08 09:00 | 41.71 | 39.56
2019-06-08 09:30 | 41.61 | 39.47
2019-06-08 10:00 | 37.81 | 35.45
2019-06-08 10:30 | 37.5 | 35.15
2019-06-08 11:00 | 37.42 | 35.09
2019-06-08 11:30 | 38.34 | 36.06
2019-06-08 12:00 | 37.62 | 35.26
2019-06-08 12:30 | 41.52 | 39.35
2019-06-08 13:00 | 39.05 | 36.71
2019-06-08 13:30 | 38.89 | 36.53
2019-06-08 14:00 | 38.16 | 35.74
2019-06-08 14:30 | 37.44 | 34.96
2019-06-08 15:00 | 40.23 | 37.92
2019-06-08 15:30 | 41.21 | 38.94
2019-06-08 16:00 | 41.7 | 39.46
2019-06-08 16:30 | 41.19 | 38.93
2019-06-08 17:00 | 43.37 | 41.24
2019-06-08 17:30 | 45.95 | 43.96
2019-06-08 18:00 | 48.81 | 46.98
2019-06-08 18:30 | 48.58 | 46.75
2019-06-08 19:00 | 46.31 | 44.37
2019-06-08 19:30 | 44.47 | 42.43
2019-06-08 20:00 | 43.15 | 41.03
2019-06-08 20:30 | 41.83 | 39.62
2019-06-08 21:00 | 40.58 | 38.29
2019-06-08 21:30 | 40.58 | 38.27
2019-06-08 22:00 | 38.98 | 36.54
2019-06-08 22:30 | 37.99 | 35.45
2019-06-08 23:00 | 36.49 | 33.81
2019-06-08 23:30 | 34.57 | 31.69
2019-06-09 | 33.41 | 30.4
2019-06-09 00:30 | 32.09 | 28.92
2019-06-09 01:00 | 31.16 | 27.87
2019-06-09 01:30 | 30.64 | 27.28
2019-06-09 02:00 | 30.12 | 26.72
2019-06-09 02:30 | 29.89 | 26.41
2019-06-09 03:00 | 29.36 | 25.79
2019-06-09 03:30 | 29.42 | 25.87
2019-06-09 04:00 | 29.75 | 26.24
2019-06-09 04:30 | 29.55 | 26.02
2019-06-09 05:00 | 30.23 | 26.8
2019-06-09 05:30 | 31.05 | 27.73
2019-06-09 06:00 | 31.33 | 28.06
2019-06-09 06:30 | 32.38 | 29.23
2019-06-09 07:00 | 32.79 | 29.68
2019-06-09 07:30 | 34.15 | 31.19
2019-06-09 08:00 | 35.25 | 32.43
2019-06-09 08:30 | 36.6 | 33.92
2019-06-09 09:00 | 36.62 | 33.96
2019-06-09 09:30 | 37.28 | 34.71
2019-06-09 10:00 | 36.89 | 34.31
2019-06-09 10:30 | 35.05 | 32.37
2019-06-09 11:00 | 33.84 | 31.05
2019-06-09 11:30 | 33.14 | 30.3
2019-06-09 12:00 | 33.15 | 30.33
2019-06-09 12:30 | 35.84 | 33.24
2019-06-09 13:00 | 35.88 | 33.27
2019-06-09 13:30 | 36.68 | 34.14
2019-06-09 14:00 | 37.26 | 34.75
2019-06-09 14:30 | 36.41 | 33.84
2019-06-09 15:00 | 35.31 | 32.64
2019-06-09 15:30 | 37 | 34.46
2019-06-09 16:00 | 38.5 | 36.06
2019-06-09 16:30 | 40.04 | 37.7
2019-06-09 17:00 | 42.41 | 40.21
2019-06-09 17:30 | 44.59 | 42.52
2019-06-09 18:00 | 47.62 | 45.74
2019-06-09 18:30 | 49.74 | 47.96
2019-06-09 19:00 | 48.96 | 47.13
2019-06-09 19:30 | 47.03 | 45.11
2019-06-09 20:00 | 44.58 | 42.52
2019-06-09 20:30 | 42.28 | 40.07
2019-06-09 21:00 | 40.58 | 38.25
2019-06-09 21:30 | 39.38 | 36.95
2019-06-09 22:00 | 37.6 | 35.02
2019-06-09 22:30 | 35.71 | 32.94
2019-06-09 23:00 | 34.9 | 32.05
2019-06-09 23:30 | 33.58 | 30.58
2019-06-10 | 32.44 | 29.3
2019-06-10 00:30 | 31.53 | 28.27
2019-06-10 01:00 | 30.96 | 27.62
2019-06-10 01:30 | 29.9 | 26.41
2019-06-10 02:00 | 29.23 | 25.65
2019-06-10 02:30 | 29.35 | 25.77
2019-06-10 03:00 | 29.87 | 26.35
2019-06-10 03:30 | 28.8 | 25.13
2019-06-10 04:00 | 29.09 | 25.48
2019-06-10 04:30 | 30.05 | 26.59
2019-06-10 05:00 | 30.99 | 27.68
2019-06-10 05:30 | 33.52 | 30.53
2019-06-10 06:00 | 37.29 | 34.71
2019-06-10 06:30 | 41.92 | 39.74
2019-06-10 07:00 | 46.29 | 44.42
2019-06-10 07:30 | 50.22 | 48.54
2019-06-10 08:00 | 52.53 | 50.9
2019-06-10 08:30 | 52.02 | 50.42
2019-06-10 09:00 | 51.74 | 50.16
2019-06-10 09:30 | 49.3 | 47.65
2019-06-10 10:00 | 47.57 | 45.8
2019-06-10 10:30 | 47.45 | 45.63
2019-06-10 11:00 | 48.13 | 46.35
2019-06-10 11:30 | 51.38 | 49.7
2019-06-10 12:00 | 51.17 | 49.48
2019-06-10 12:30 | 50.07 | 48.33
2019-06-10 13:00 | 48.23 | 46.43
2019-06-10 13:30 | 48.15 | 46.36
2019-06-10 14:00 | 47.73 | 45.92
2019-06-10 14:30 | 48.52 | 46.75
2019-06-10 15:00 | 49.97 | 48.23
2019-06-10 15:30 | 50.34 | 48.6
2019-06-10 16:00 | 51.64 | 49.91
2019-06-10 16:30 | 51.68 | 49.89
2019-06-10 17:00 | 52.88 | 51.09
2019-06-10 17:30 | 53.44 | 51.61
2019-06-10 18:00 | 55.54 | 53.79
2019-06-10 18:30 | 56.43 | 54.68
2019-06-10 19:00 | 55.4 | 53.6
2019-06-10 19:30 | 53.17 | 51.26
2019-06-10 20:00 | 50.79 | 48.76
2019-06-10 20:30 | 47.99 | 45.81
2019-06-10 21:00 | 43.53 | 42.85
2019-06-10 21:30 | 41.71 | 41.38
2019-06-10 22:00 | 39.74 | 39.71
2019-06-10 22:30 | 36.58 | 36.52
2019-06-10 23:00 | 34.39 | 34.31
2019-06-10 23:30 | 32.28 | 32.16
2019-06-11 | 31.3 | 31.14
2019-06-11 00:30 | 30.56 | 30.38
2019-06-11 01:00 | 29.78 | 29.6
2019-06-11 01:30 | 29.51 | 29.29
2019-06-11 02:00 | 29.02 | 28.77
2019-06-11 02:30 | 27.49 | 27.48
2019-06-11 03:00 | 27.28 | 27.27
2019-06-11 03:30 | 28.08 | 28.07
2019-06-11 04:00 | 27.83 | 27.82
2019-06-11 04:30 | 28.21 | 28.21
2019-06-11 05:00 | 30.27 | 30.27
2019-06-11 05:30 | 31.92 | 31.9
2019-06-11 06:00 | 34.7 | 34.62
2019-06-11 06:30 | 39.68 | 39.46
2019-06-11 07:00 | 44.49 | 44.16
2019-06-11 07:30 | 48.99 | 48.78
2019-06-11 08:00 | 52.45 | 51.29
2019-06-11 08:30 | 52.64 | 51.1
2019-06-11 09:00 | 53.59 | 52.12
2019-06-11 09:30 | 53.79 | 52.33
2019-06-11 10:00 | 51.54 | 49.98
2019-06-11 10:30 | 52.09 | 50.48
2019-06-11 11:00 | 52.49 | 50.92
2019-06-11 11:30 | 51.78 | 50.19
2019-06-11 12:00 | 51.92 | 50.31
2019-06-11 12:30 | 50.61 | 48.94
2019-06-11 13:00 | 48.72 | 46.97
2019-06-11 13:30 | 51.12 | 49.47
2019-06-11 14:00 | 50.26 | 48.58
2019-06-11 14:30 | 52.03 | 50.42
2019-06-11 15:00 | 51.2 | 49.54
2019-06-11 15:30 | 51.85 | 50.19
2019-06-11 16:00 | 52.68 | 51.03
2019-06-11 16:30 | 52.43 | 50.71
2019-06-11 17:00 | 53.17 | 51.44
2019-06-11 17:30 | 53.96 | 52.21
2019-06-11 18:00 | 55.58 | 53.89
2019-06-11 18:30 | 57.12 | 55.46
2019-06-11 19:00 | 55.32 | 53.58
2019-06-11 19:30 | 52.72 | 50.85
2019-06-11 20:00 | 50.59 | 48.62
2019-06-11 20:30 | 48.32 | 46.21
2019-06-11 21:00 | 46.44 | 44.21
2019-06-11 21:30 | 45.05 | 42.75
2019-06-11 22:00 | 43.05 | 40.75
2019-06-11 22:30 | 39.98 | 37.44
2019-06-11 23:00 | 38.69 | 36.05
2019-06-11 23:30 | 36.35 | 33.49
2019-06-12 | 35.14 | 32.14
2019-06-12 00:30 | 33.52 | 30.34
2019-06-12 01:00 | 30.66 | 28.86
2019-06-12 01:30 | 28.42 | 28.07
2019-06-12 02:00 | 28.09 | 27.73
2019-06-12 02:30 | 27.11 | 27.04
2019-06-12 03:00 | 26.67 | 26.66
2019-06-12 03:30 | 26.54 | 26.52
2019-06-12 04:00 | 26.95 | 26.94
2019-06-12 04:30 | 28.2 | 28.19
2019-06-12 05:00 | 29.34 | 29.33
2019-06-12 05:30 | 31.92 | 31.91
2019-06-12 06:00 | 34.77 | 34.72
2019-06-12 06:30 | 39.96 | 39.76
2019-06-12 07:00 | 44.95 | 44.52
2019-06-12 07:30 | 50.24 | 50.02
2019-06-12 08:00 | 54.08 | 53.68
2019-06-12 08:30 | 53.24 | 51.68
2019-06-12 09:00 | 50.93 | 49.33
2019-06-12 09:30 | 49.56 | 47.92
2019-06-12 10:00 | 51.54 | 49.97
2019-06-12 10:30 | 51 | 49.43
2019-06-12 11:00 | 47.96 | 46.28
2019-06-12 11:30 | 47.48 | 45.69
2019-06-12 12:00 | 47.55 | 45.79
2019-06-12 12:30 | 47.05 | 45.27
2019-06-12 13:00 | 46.73 | 44.91
2019-06-12 13:30 | 47.05 | 45.28
2019-06-12 14:00 | 47.87 | 46.13
2019-06-12 14:30 | 48.47 | 46.74
2019-06-12 15:00 | 49.79 | 48.12
2019-06-12 15:30 | 50.73 | 49.06
2019-06-12 16:00 | 52.7 | 51.07
2019-06-12 16:30 | 53.31 | 51.65
2019-06-12 17:00 | 53.17 | 51.45
2019-06-12 17:30 | 53.97 | 52.21
2019-06-12 18:00 | 56.88 | 55.22
2019-06-12 18:30 | 57.61 | 55.95
2019-06-12 19:00 | 56.56 | 54.86
2019-06-12 19:30 | 54.21 | 52.42
2019-06-12 20:00 | 52.56 | 50.68
2019-06-12 20:30 | 50.34 | 48.34
2019-06-12 21:00 | 48.31 | 46.19
2019-06-12 21:30 | 44.64 | 42.37
2019-06-12 22:00 | 42.33 | 40.01
2019-06-12 22:30 | 39.88 | 37.37
2019-06-12 23:00 | 38.12 | 35.47
2019-06-12 23:30 | 36.52 | 33.73
2019-06-13 | 35.33 | 32.39
2019-06-13 00:30 | 34.03 | 30.95
2019-06-13 01:00 | 34.59 | 31.54
2019-06-13 01:30 | 33.48 | 30.32
2019-06-13 02:00 | 34.06 | 31.01
2019-06-13 02:30 | 33.14 | 30.14
2019-06-13 03:00 | 31.09 | 27.85
2019-06-13 03:30 | 30.87 | 27.61
2019-06-13 04:00 | 31.42 | 28.24
2019-06-13 04:30 | 32.65 | 29.6
2019-06-13 05:00 | 34.01 | 31.12
2019-06-13 05:30 | 36.29 | 33.65
2019-06-13 06:00 | 37.8 | 35.31
2019-06-13 06:30 | 41.8 | 39.66
2019-06-13 07:00 | 46.19 | 44.35
2019-06-13 07:30 | 51.99 | 50.34
2019-06-13 08:00 | 53.78 | 52.22
2019-06-13 08:30 | 53.81 | 52.29
2019-06-13 09:00 | 53.28 | 51.76
2019-06-13 09:30 | 52.68 | 51.15
2019-06-13 10:00 | 51.24 | 49.66
2019-06-13 10:30 | 53.22 | 51.61
2019-06-13 11:00 | 54.58 | 53.02
2019-06-13 11:30 | 50.8 | 49.13
2019-06-13 12:00 | 51.21 | 49.57
2019-06-13 12:30 | 50.81 | 49.15
2019-06-13 13:00 | 51.28 | 49.62
2019-06-13 13:30 | 51.37 | 49.73
2019-06-13 14:00 | 52.2 | 50.59
2019-06-13 14:30 | 51.55 | 49.91
2019-06-13 15:00 | 52.3 | 50.68
2019-06-13 15:30 | 52.41 | 50.78
2019-06-13 16:00 | 52.97 | 51.32
2019-06-13 16:30 | 53.53 | 51.84
2019-06-13 17:00 | 54.34 | 52.63
2019-06-13 17:30 | 53.61 | 51.83
2019-06-13 18:00 | 56.27 | 54.58
2019-06-13 18:30 | 57.31 | 55.63
2019-06-13 19:00 | 56.42 | 54.7
2019-06-13 19:30 | 54.44 | 52.63
2019-06-13 20:00 | 52.18 | 50.26
2019-06-13 20:30 | 50.29 | 48.27
2019-06-13 21:00 | 48.73 | 46.7
2019-06-13 21:30 | 45.95 | 43.82
2019-06-13 22:00 | 43.09 | 40.83
2019-06-13 22:30 | 40.14 | 37.79
2019-06-13 23:00 | 38.39 | 35.9
2019-06-13 23:30 | 36.16 | 33.48
2019-06-14 | 34.85 | 32.04
2019-06-14 00:30 | 34.22 | 31.32
2019-06-14 01:00 | 33.18 | 30.16
2019-06-14 01:30 | 32.13 | 28.99
2019-06-14 02:00 | 32.01 | 28.86
2019-06-14 02:30 | 31.34 | 28.09
2019-06-14 03:00 | 31.67 | 28.44
2019-06-14 03:30 | 30.84 | 27.52
2019-06-14 04:00 | 30.95 | 27.63
2019-06-14 04:30 | 32.09 | 28.92
2019-06-14 05:00 | 33.83 | 30.87
2019-06-14 05:30 | 35.33 | 32.56
2019-06-14 06:00 | 37.4 | 34.85
2019-06-14 06:30 | 41.82 | 39.63
2019-06-14 07:00 | 45.74 | 43.8
2019-06-14 07:30 | 51.7 | 49.97
2019-06-14 08:00 | 53.01 | 51.37
2019-06-14 08:30 | 52.42 | 50.81
2019-06-14 09:00 | 51.39 | 49.78
2019-06-14 09:30 | 48.98 | 47.3
2019-06-14 10:00 | 48.72 | 47
2019-06-14 10:30 | 50.22 | 48.44
2019-06-14 11:00 | 49.54 | 47.68
2019-06-14 11:30 | 48.86 | 46.98
2019-06-14 12:00 | 48.34 | 46.44
2019-06-14 12:30 | 47.55 | 45.61
2019-06-14 13:00 | 47.37 | 45.42
2019-06-14 13:30 | 47.1 | 45.14
2019-06-14 14:00 | 47.46 | 45.51
2019-06-14 14:30 | 47.27 | 45.29
2019-06-14 15:00 | 47.85 | 45.88
2019-06-14 15:30 | 48.41 | 46.42
2019-06-14 16:00 | 51.39 | 49.5
2019-06-14 16:30 | 51.96 | 50.04
2019-06-14 17:00 | 51.65 | 49.69
2019-06-14 17:30 | 52.18 | 50.18
2019-06-14 18:00 | 53.4 | 51.44
2019-06-14 18:30 | 53.77 | 51.81
2019-06-14 19:00 | 52.41 | 50.38
2019-06-14 19:30 | 49.16 | 48.17
2019-06-14 20:00 | 45.93 | 45.88
2019-06-14 20:30 | 44.4 | 44.4
2019-06-14 21:00 | 42.23 | 42.23
2019-06-14 21:30 | 40.25 | 40.24
2019-06-14 22:00 | 37.76 | 37.71
2019-06-14 22:30 | 35.21 | 35.16
2019-06-14 23:00 | 35.73 | 35.7
2019-06-14 23:30 | 34.61 | 34.59
2019-06-15 | 32.94 | 32.93
2019-06-15 00:30 | 32.2 | 32.19
2019-06-15 01:00 | 29.75 | 29.74
2019-06-15 01:30 | 28.41 | 28.41
2019-06-15 02:00 | 27.55 | 27.55
2019-06-15 02:30 | 27.63 | 27.63
2019-06-15 03:00 | 27.28 | 27.28
2019-06-15 03:30 | 26.6 | 26.59
2019-06-15 04:00 | 27.02 | 27.01
2019-06-15 04:30 | 27.35 | 27.35
2019-06-15 05:00 | 27.88 | 27.88
2019-06-15 05:30 | 29.31 | 29.3
2019-06-15 06:00 | 30.71 | 30.7
2019-06-15 06:30 | 32.55 | 32.52
2019-06-15 07:00 | 34.53 | 34.51
2019-06-15 07:30 | 35.64 | 35.56
2019-06-15 08:00 | 36.87 | 36.74
2019-06-15 08:30 | 38.39 | 38.17
2019-06-15 09:00 | 38.13 | 37.82
2019-06-15 09:30 | 37.18 | 36.73
2019-06-15 10:00 | 36.66 | 36.1
2019-06-15 10:30 | 35.68 | 35.01
2019-06-15 11:00 | 35.41 | 34.64
2019-06-15 11:30 | 35.33 | 34.48
2019-06-15 12:00 | 35.21 | 34.39
2019-06-15 12:30 | 33.34 | 32.61
2019-06-15 13:00 | 33.08 | 32.44
2019-06-15 13:30 | 32.9 | 32.25
2019-06-15 14:00 | 33.42 | 32.83
2019-06-15 14:30 | 33.68 | 33.19
2019-06-15 15:00 | 33.77 | 33.36
2019-06-15 15:30 | 34.8 | 34.46
2019-06-15 16:00 | 36.93 | 36.62
2019-06-15 16:30 | 38.37 | 38.14
2019-06-15 17:00 | 40.71 | 40.5
2019-06-15 17:30 | 42.55 | 42.36
2019-06-15 18:00 | 46.68 | 46.44
2019-06-15 18:30 | 47.66 | 47.4
2019-06-15 19:00 | 46.35 | 46.12
2019-06-15 19:30 | 43.64 | 43.44
2019-06-15 20:00 | 42.45 | 42.29
2019-06-15 20:30 | 39.84 | 39.73
2019-06-15 21:00 | 38.63 | 38.54
2019-06-15 21:30 | 36.89 | 36.83
2019-06-15 22:00 | 35.69 | 35.65
2019-06-15 22:30 | 33.86 | 33.85
2019-06-15 23:00 | 32.71 | 32.71
2019-06-15 23:30 | 31.4 | 31.4
2019-06-16 | 30.45 | 30.45
2019-06-16 00:30 | 29.57 | 29.57
2019-06-16 01:00 | 28.76 | 28.76
2019-06-16 01:30 | 28.6 | 28.6
2019-06-16 02:00 | 27.38 | 27.38
2019-06-16 02:30 | 26.68 | 26.68
2019-06-16 03:00 | 26.38 | 26.38
2019-06-16 03:30 | 26.53 | 26.53
2019-06-16 04:00 | 26.08 | 26.07
2019-06-16 04:30 | 26.38 | 26.37
2019-06-16 05:00 | 26.83 | 26.83
2019-06-16 05:30 | 28.34 | 28.34
2019-06-16 06:00 | 28.65 | 28.65
2019-06-16 06:30 | 30.08 | 30.08
2019-06-16 07:00 | 30.52 | 30.52
2019-06-16 07:30 | 32.13 | 32.13
2019-06-16 08:00 | 32.53 | 32.53
2019-06-16 08:30 | 33.57 | 33.56
2019-06-16 09:00 | 33.87 | 33.82
2019-06-16 09:30 | 36.34 | 36.23
2019-06-16 10:00 | 37.87 | 37.72
2019-06-16 10:30 | 36.44 | 36.26
2019-06-16 11:00 | 35 | 34.78
2019-06-16 11:30 | 31.95 | 31.65
2019-06-16 12:00 | 32.21 | 31.87
2019-06-16 12:30 | 32.9 | 32.62
2019-06-16 13:00 | 33.07 | 32.83
2019-06-16 13:30 | 35.61 | 35.39
2019-06-16 14:00 | 37.26 | 37.1
2019-06-16 14:30 | 38.65 | 38.53
2019-06-16 15:00 | 37.88 | 37.77
2019-06-16 15:30 | 36.15 | 36.03
2019-06-16 16:00 | 36.42 | 36.32
2019-06-16 16:30 | 38.22 | 38.13
2019-06-16 17:00 | 39.99 | 39.91
2019-06-16 17:30 | 41.98 | 41.9
2019-06-16 18:00 | 46.35 | 46.21
2019-06-16 18:30 | 49.16 | 49
2019-06-16 19:00 | 47.06 | 46.92
2019-06-16 19:30 | 44.9 | 44.79
2019-06-16 20:00 | 43.09 | 43
2019-06-16 20:30 | 40.98 | 40.93
2019-06-16 21:00 | 39.27 | 39.23
2019-06-16 21:30 | 37.55 | 37.53
2019-06-16 22:00 | 36.14 | 36.13
2019-06-16 22:30 | 33.24 | 33.23
2019-06-16 23:00 | 31.43 | 31.43
2019-06-16 23:30 | 30.05 | 30.05
2019-06-17 | 29.3 | 29.3
2019-06-17 00:30 | 27.82 | 27.8
2019-06-17 01:00 | 27.19 | 27.17
2019-06-17 01:30 | 27.03 | 27.01
2019-06-17 02:00 | 26.96 | 26.94
2019-06-17 02:30 | 26.63 | 26.61
2019-06-17 03:00 | 25.92 | 25.88
2019-06-17 03:30 | 26.57 | 26.53
2019-06-17 04:00 | 27.1 | 27.07
2019-06-17 04:30 | 28.02 | 28
2019-06-17 05:00 | 29.88 | 29.87
2019-06-17 05:30 | 31.56 | 31.56
2019-06-17 06:00 | 34.02 | 33.99
2019-06-17 06:30 | 39.25 | 39.09
2019-06-17 07:00 | 43.1 | 42.79
2019-06-17 07:30 | 48.64 | 48.39
2019-06-17 08:00 | 49.69 | 49.36
2019-06-17 08:30 | 49.48 | 48.91
2019-06-17 09:00 | 48.42 | 47.65
2019-06-17 09:30 | 49.48 | 48.16
2019-06-17 10:00 | 49.99 | 48.26
2019-06-17 10:30 | 50.88 | 49.21
2019-06-17 11:00 | 50.54 | 48.9
2019-06-17 11:30 | 48.8 | 47.12
2019-06-17 12:00 | 48.8 | 47.12
2019-06-17 12:30 | 48.44 | 46.74
2019-06-17 13:00 | 48.34 | 46.63
2019-06-17 13:30 | 49.17 | 47.49
2019-06-17 14:00 | 48.57 | 46.87
2019-06-17 14:30 | 50.24 | 48.58
2019-06-17 15:00 | 50.57 | 48.92
2019-06-17 15:30 | 51.35 | 49.71
2019-06-17 16:00 | 52.19 | 50.55
2019-06-17 16:30 | 53.03 | 51.35
2019-06-17 17:00 | 54.14 | 52.44
2019-06-17 17:30 | 53.51 | 51.72
2019-06-17 18:00 | 55.53 | 53.81
2019-06-17 18:30 | 56.02 | 54.3
2019-06-17 19:00 | 54.52 | 52.73
2019-06-17 19:30 | 51.86 | 49.93
2019-06-17 20:00 | 50.09 | 48.06
2019-06-17 20:30 | 48.17 | 46.02
2019-06-17 21:00 | 45.46 | 43.25
2019-06-17 21:30 | 42.9 | 40.63
2019-06-17 22:00 | 40.52 | 38.21
2019-06-17 22:30 | 38.49 | 36.01
2019-06-17 23:00 | 36.67 | 34.02
2019-06-17 23:30 | 34.96 | 32.15
2019-06-18 | 33.72 | 30.83
2019-06-18 00:30 | 32.73 | 29.74
2019-06-18 01:00 | 31.77 | 28.68
2019-06-18 01:30 | 31.22 | 28.07
2019-06-18 02:00 | 31.33 | 28.17
2019-06-18 02:30 | 28.19 | 24.57
2019-06-18 03:00 | 24.97 | 20.68
2019-06-18 03:30 | 24.99 | 20.7
2019-06-18 04:00 | 24.99 | 20.7
2019-06-18 04:30 | 25.42 | 21.24
2019-06-18 05:00 | 26.44 | 22.46
2019-06-18 05:30 | 27.7 | 23.97
2019-06-18 06:00 | 29.43 | 25.99
2019-06-18 06:30 | 32.51 | 29.5
2019-06-18 07:00 | 35.45 | 32.75
2019-06-18 07:30 | 39.21 | 36.87
2019-06-18 08:00 | 40.25 | 38.02
2019-06-18 08:30 | 39.52 | 37.28
2019-06-18 09:00 | 37.83 | 35.5
2019-06-18 09:30 | 36.33 | 33.92
2019-06-18 10:00 | 34.75 | 32.24
2019-06-18 10:30 | 33.96 | 31.41
2019-06-18 11:00 | 33.55 | 30.98
2019-06-18 11:30 | 33.18 | 30.59
2019-06-18 12:00 | 33 | 30.4
2019-06-18 12:30 | 33 | 30.41
2019-06-18 13:00 | 33.11 | 30.52
2019-06-18 13:30 | 33.53 | 30.97
2019-06-18 14:00 | 34.3 | 31.82
2019-06-18 14:30 | 41.46 | 39.47
2019-06-18 15:00 | 48.07 | 46.31
2019-06-18 15:30 | 49.33 | 47.6
2019-06-18 16:00 | 51.01 | 49.32
2019-06-18 16:30 | 51.8 | 50.09
2019-06-18 17:00 | 52.81 | 51.09
2019-06-18 17:30 | 52.88 | 51.13
2019-06-18 18:00 | 55.63 | 53.96
2019-06-18 18:30 | 56.43 | 54.85
2019-06-18 19:00 | 55.72 | 54.14
2019-06-18 19:30 | 53.72 | 52.06
2019-06-18 20:00 | 51.22 | 49.45
2019-06-18 20:30 | 49.1 | 47.22
2019-06-18 21:00 | 47.84 | 45.96
2019-06-18 21:30 | 44.82 | 42.84
2019-06-18 22:00 | 42.12 | 39.98
2019-06-18 22:30 | 38.91 | 36.53
2019-06-18 23:00 | 37.73 | 35.24
2019-06-18 23:30 | 35.73 | 33.07
2019-06-19 | 33.83 | 30.97
2019-06-19 00:30 | 33.58 | 30.68
2019-06-19 01:00 | 32.62 | 29.61
2019-06-19 01:30 | 31.95 | 28.86
2019-06-19 02:00 | 31.16 | 27.99
2019-06-19 02:30 | 30.94 | 27.68
2019-06-19 03:00 | 30.73 | 27.43
2019-06-19 03:30 | 30.69 | 27.38
2019-06-19 04:00 | 31.32 | 28.1
2019-06-19 04:30 | 32.78 | 29.74
2019-06-19 05:00 | 34.4 | 31.55
2019-06-19 05:30 | 37.36 | 34.82
2019-06-19 06:00 | 40.14 | 37.83
2019-06-19 06:30 | 44.84 | 42.88
2019-06-19 07:00 | 50.72 | 49.01
2019-06-19 07:30 | 55.21 | 53.66
2019-06-19 08:00 | 56.04 | 54.54
2019-06-19 08:30 | 53.32 | 51.76
2019-06-19 09:00 | 50.31 | 48.67
2019-06-19 09:30 | 48.24 | 46.54
2019-06-19 10:00 | 45.74 | 43.95
2019-06-19 10:30 | 44.63 | 42.81
2019-06-19 11:00 | 46.46 | 42.63
2019-06-19 11:30 | 46.58 | 42.06
2019-06-19 12:00 | 46.72 | 42.26
2019-06-19 12:30 | 46.08 | 41.51
2019-06-19 13:00 | 46.5 | 41.96
2019-06-19 13:30 | 46.83 | 42.34
2019-06-19 14:00 | 46.91 | 42.46
2019-06-19 14:30 | 47.7 | 43.33
2019-06-19 15:00 | 48.62 | 44.32
2019-06-19 15:30 | 50 | 45.8
2019-06-19 16:00 | 51.51 | 47.41
2019-06-19 16:30 | 52.96 | 48.89
2019-06-19 17:00 | 54.61 | 50.62
2019-06-19 17:30 | 55.18 | 51.16
2019-06-19 18:00 | 56.92 | 53.28
2019-06-19 18:30 | 58.77 | 55.42
2019-06-19 19:00 | 56.89 | 53.4
2019-06-19 19:30 | 54.56 | 50.86
2019-06-19 20:00 | 52.69 | 48.8
2019-06-19 20:30 | 51.5 | 47.49
2019-06-19 21:00 | 49.32 | 45.06
2019-06-19 21:30 | 47.57 | 43.08
2019-06-19 22:00 | 46.19 | 41.51
2019-06-19 22:30 | 43.85 | 38.81
2019-06-19 23:00 | 43.21 | 38.05
2019-06-19 23:30 | 41.07 | 35.53
2019-06-20 | 39.74 | 33.95
2019-06-20 00:30 | 38.91 | 32.91
2019-06-20 01:00 | 38.07 | 31.9
2019-06-20 01:30 | 37.36 | 31.01
2019-06-20 02:00 | 36.89 | 30.43
2019-06-20 02:30 | 36.5 | 29.93
2019-06-20 03:00 | 36.36 | 29.73
2019-06-20 03:30 | 36.32 | 29.68
2019-06-20 04:00 | 36.34 | 29.69
2019-06-20 04:30 | 36.85 | 30.32
2019-06-20 05:00 | 37.31 | 30.9
2019-06-20 05:30 | 38.47 | 32.33
2019-06-20 06:00 | 39.75 | 33.89
2019-06-20 06:30 | 42.18 | 36.78
2019-06-20 07:00 | 43.56 | 38.41
2019-06-20 07:30 | 45.94 | 41.16
2019-06-20 08:00 | 46.51 | 41.84
2019-06-20 08:30 | 47.06 | 42.5
2019-06-20 09:00 | 45.25 | 40.51
2019-06-20 09:30 | 44.43 | 39.6
2019-06-20 10:00 | 43.73 | 38.83
2019-06-20 10:30 | 42.64 | 37.62
2019-06-20 11:00 | 40.52 | 35.23
2019-06-20 11:30 | 39.85 | 34.49
2019-06-20 12:00 | 39.28 | 33.84
2019-06-20 12:30 | 39.12 | 33.66
2019-06-20 13:00 | 38.62 | 33.08
2019-06-20 13:30 | 39.14 | 33.66
2019-06-20 14:00 | 38.78 | 33.21
2019-06-20 14:30 | 39.41 | 33.89
2019-06-20 15:00 | 40.26 | 34.78
2019-06-20 15:30 | 41.55 | 36.26
2019-06-20 16:00 | 43.85 | 38.86
2019-06-20 16:30 | 45.47 | 40.63
2019-06-20 17:00 | 48.23 | 43.7
2019-06-20 17:30 | 50.28 | 45.95
2019-06-20 18:00 | 52.81 | 48.76
2019-06-20 18:30 | 54.86 | 50.99
2019-06-20 19:00 | 54.63 | 50.72
2019-06-20 19:30 | 52.36 | 48.23
2019-06-20 20:00 | 50.94 | 46.65
2019-06-20 20:30 | 49.6 | 45.14
2019-06-20 21:00 | 47.75 | 43.04
2019-06-20 21:30 | 45.87 | 40.89
2019-06-20 22:00 | 44.09 | 38.82
2019-06-20 22:30 | 41.91 | 36.26
2019-06-20 23:00 | 41.21 | 35.43
2019-06-20 23:30 | 39.69 | 33.61
2019-06-21 | 33.73 | 31.59
2019-06-21 00:30 | 31.86 | 31.12
2019-06-21 01:00 | 30.77 | 30.01
2019-06-21 01:30 | 30.1 | 29.32
2019-06-21 02:00 | 29.39 | 28.59
2019-06-21 02:30 | 29.5 | 28.69
2019-06-21 03:00 | 29.13 | 28.31
2019-06-21 03:30 | 29.56 | 28.75
2019-06-21 04:00 | 29.6 | 28.8
2019-06-21 04:30 | 30.67 | 29.9
2019-06-21 05:00 | 32.12 | 31.4
2019-06-21 05:30 | 34.54 | 33.89
2019-06-21 06:00 | 37.04 | 36.45
2019-06-21 06:30 | 41.61 | 41.11
2019-06-21 07:00 | 45.25 | 44.81
2019-06-21 07:30 | 49.68 | 49.29
2019-06-21 08:00 | 50.45 | 50.04
2019-06-21 08:30 | 48.71 | 48.3
2019-06-21 09:00 | 45.97 | 45.54
2019-06-21 09:30 | 40.56 | 40.09
2019-06-21 10:00 | 37.15 | 36.64
2019-06-21 10:30 | 26.49 | 25.44
2019-06-21 11:00 | 40.67 | 40.11
2019-06-21 11:30 | 39.68 | 39.04
2019-06-21 12:00 | 39.62 | 38.98
2019-06-21 12:30 | 39.86 | 39.23
2019-06-21 13:00 | 39.6 | 38.95
2019-06-21 13:30 | 39.19 | 38.64
2019-06-21 14:00 | 39.67 | 39.19
2019-06-21 14:30 | 40.44 | 39.98
2019-06-21 15:00 | 34.11 | 33.45
2019-06-21 15:30 | 41.55 | 41.1
2019-06-21 16:00 | 43.57 | 43.13
2019-06-21 16:30 | 45.69 | 45.25
2019-06-21 17:00 | 47.15 | 46.71
2019-06-21 17:30 | 47.38 | 46.93
2019-06-21 18:00 | 50.13 | 49.7
2019-06-21 18:30 | 51.27 | 50.84
2019-06-21 19:00 | 50.65 | 50.22
2019-06-21 19:30 | 48.53 | 48.07
2019-06-21 20:00 | 46.69 | 46.2
2019-06-21 20:30 | 45.31 | 44.8
2019-06-21 21:00 | 44.12 | 43.59
2019-06-21 21:30 | 42.3 | 41.75
2019-06-21 22:00 | 39.91 | 39.37
2019-06-21 22:30 | 37.67 | 37.09
2019-06-21 23:00 | 36.65 | 36.04
2019-06-21 23:30 | 34.3 | 33.64
2019-06-22 | 32.79 | 32.09
2019-06-22 00:30 | 32.43 | 31.72
2019-06-22 01:00 | 31.48 | 30.74
2019-06-22 01:30 | 31.13 | 30.38
2019-06-22 02:00 | 29.59 | 28.79
2019-06-22 02:30 | 29.46 | 28.65
2019-06-22 03:00 | 29.27 | 28.45
2019-06-22 03:30 | 28.9 | 28.07
2019-06-22 04:00 | 29.14 | 28.32
2019-06-22 04:30 | 29.58 | 28.78
2019-06-22 05:00 | 30.46 | 29.68
2019-06-22 05:30 | 32 | 31.26
2019-06-22 06:00 | 33.24 | 32.54
2019-06-22 06:30 | 36.15 | 35.53
2019-06-22 07:00 | 38.12 | 37.53
2019-06-22 07:30 | 40.41 | 39.87
2019-06-22 08:00 | 40.66 | 40.13
2019-06-22 08:30 | 40.35 | 39.83
2019-06-22 09:00 | 39.62 | 39.1
2019-06-22 09:30 | 37.99 | 37.45
2019-06-22 10:00 | 35.97 | 35.4
2019-06-22 10:30 | 34.6 | 34.01
2019-06-22 11:00 | 33.27 | 32.67
2019-06-22 11:30 | 31.71 | 31.08
2019-06-22 12:00 | 30.71 | 30.05
2019-06-22 12:30 | 29.71 | 29.02
2019-06-22 13:00 | 28.91 | 28.19
2019-06-22 13:30 | 28.21 | 27.47
2019-06-22 14:00 | 28.72 | 27.99
2019-06-22 14:30 | 29.69 | 28.98
2019-06-22 15:00 | 30.84 | 30.16
2019-06-22 15:30 | 32.88 | 32.23
2019-06-22 16:00 | 34.43 | 33.81
2019-06-22 16:30 | 37.69 | 37.12
2019-06-22 17:00 | 39.45 | 38.9
2019-06-22 17:30 | 43.3 | 42.82
2019-06-22 18:00 | 47.38 | 46.95
2019-06-22 18:30 | 49.42 | 49.02
2019-06-22 19:00 | 48.13 | 47.71
2019-06-22 19:30 | 46.1 | 45.65
2019-06-22 20:00 | 44.51 | 44.04
2019-06-22 20:30 | 43.11 | 42.61
2019-06-22 21:00 | 41.62 | 41.1
2019-06-22 21:30 | 40.31 | 39.77
2019-06-22 22:00 | 39.13 | 38.56
2019-06-22 22:30 | 38.77 | 38.18
2019-06-22 23:00 | 36.5 | 35.87
2019-06-22 23:30 | 33.95 | 33.26
2019-06-23 | 34.71 | 34.03
2019-06-23 00:30 | 32.76 | 32.02
2019-06-23 01:00 | 31.86 | 31.11
2019-06-23 01:30 | 30.21 | 29.41
2019-06-23 02:00 | 29.93 | 29.13
2019-06-23 02:30 | 29.59 | 28.77
2019-06-23 03:00 | 29.54 | 28.71
2019-06-23 03:30 | 30.37 | 29.57
2019-06-23 04:00 | 29.6 | 28.78
2019-06-23 04:30 | 29.6 | 28.77
2019-06-23 05:00 | 29.48 | 28.65
2019-06-23 05:30 | 30.3 | 29.5
2019-06-23 06:00 | 31.86 | 31.1
2019-06-23 06:30 | 32.86 | 32.13
2019-06-23 07:00 | 33.93 | 33.23
2019-06-23 07:30 | 35.76 | 35.11
2019-06-23 08:00 | 36.19 | 35.55
2019-06-23 08:30 | 37.2 | 36.58
2019-06-23 09:00 | 34.93 | 34.28
2019-06-23 09:30 | 34.66 | 34.02
2019-06-23 10:00 | 33.5 | 32.84
2019-06-23 10:30 | 32.29 | 31.62
2019-06-23 11:00 | 31.14 | 30.45
2019-06-23 11:30 | 33.67 | 33.04
2019-06-23 12:00 | 33.08 | 32.44
2019-06-23 12:30 | 34.9 | 34.29
2019-06-23 13:00 | 32.1 | 31.44
2019-06-23 13:30 | 31.22 | 30.55
2019-06-23 14:00 | 31.69 | 31.03
2019-06-23 14:30 | 32.71 | 32.06
2019-06-23 15:00 | 32.55 | 31.9
2019-06-23 15:30 | 33.98 | 33.34
2019-06-23 16:00 | 35.08 | 34.47
2019-06-23 16:30 | 38.35 | 37.79
2019-06-23 17:00 | 40.6 | 40.07
2019-06-23 17:30 | 43.79 | 43.31
2019-06-23 18:00 | 48.75 | 48.33
2019-06-23 18:30 | 49.76 | 49.36
2019-06-23 19:00 | 48.6 | 48.18
2019-06-23 19:30 | 46 | 45.55
2019-06-23 20:00 | 45.45 | 45
2019-06-23 20:30 | 43.26 | 42.77
2019-06-23 21:00 | 40.73 | 40.2
2019-06-23 21:30 | 39.1 | 38.53
2019-06-23 22:00 | 36.75 | 36.13
2019-06-23 22:30 | 35.42 | 34.77
2019-06-23 23:00 | 34.09 | 33.41
2019-06-23 23:30 | 31.71 | 30.98
2019-06-24 | 30.19 | 29.41
2019-06-24 00:30 | 30.09 | 29.29
2019-06-24 01:00 | 29.09 | 28.27
2019-06-24 01:30 | 29.03 | 28.21
2019-06-24 02:00 | 28.57 | 27.73
2019-06-24 02:30 | 27.83 | 26.97
2019-06-24 03:00 | 27.85 | 26.98
2019-06-24 03:30 | 27.66 | 26.79
2019-06-24 04:00 | 28.4 | 27.55
2019-06-24 04:30 | 30.13 | 29.33
2019-06-24 05:00 | 31.41 | 30.66
2019-06-24 05:30 | 34.33 | 33.67
2019-06-24 06:00 | 36.83 | 36.23
2019-06-24 06:30 | 40.47 | 39.97
2019-06-24 07:00 | 45.91 | 45.49
2019-06-24 07:30 | 50.36 | 49.95
2019-06-24 08:00 | 51.11 | 50.73
2019-06-24 08:30 | 49.07 | 48.69
2019-06-24 09:00 | 46.17 | 45.77
2019-06-24 09:30 | 44.56 | 44.12
2019-06-24 10:00 | 43.42 | 42.93
2019-06-24 10:30 | 42.84 | 42.22
2019-06-24 11:00 | 42.72 | 41.95
2019-06-24 11:30 | 43.27 | 42.43
2019-06-24 12:00 | 43.58 | 42.73
2019-06-24 12:30 | 43 | 42.21
2019-06-24 13:00 | 42.43 | 41.62
2019-06-24 13:30 | 42.42 | 41.54
2019-06-24 14:00 | 42.73 | 41.8
2019-06-24 14:30 | 42.83 | 41.97
2019-06-24 15:00 | 43.92 | 43.13
2019-06-24 15:30 | 44.58 | 43.92
2019-06-24 16:00 | 46.32 | 45.84
2019-06-24 16:30 | 47.87 | 47.48
2019-06-24 17:00 | 49.44 | 49.05
2019-06-24 17:30 | 51.82 | 51.43
2019-06-24 18:00 | 54.02 | 53.65
2019-06-24 18:30 | 54.94 | 54.57
2019-06-24 19:00 | 53.93 | 53.55
2019-06-24 19:30 | 50.92 | 50.56
2019-06-24 20:00 | 48.85 | 48.47
2019-06-24 20:30 | 47.64 | 47.25
2019-06-24 21:00 | 45.47 | 45.05
2019-06-24 21:30 | 42.96 | 42.5
2019-06-24 22:00 | 40.04 | 39.53
2019-06-24 22:30 | 36.15 | 35.56
2019-06-24 23:00 | 35.11 | 34.5
2019-06-24 23:30 | 34.37 | 33.74
2019-06-25 | 32.72 | 32.04
2019-06-25 00:30 | 32.29 | 31.6
2019-06-25 01:00 | 30.82 | 30.08
2019-06-25 01:30 | 30.31 | 29.56
2019-06-25 02:00 | 28.78 | 27.98
2019-06-25 02:30 | 28.48 | 27.66
2019-06-25 03:00 | 27.42 | 26.56
2019-06-25 03:30 | 27.89 | 27.05
2019-06-25 04:00 | 28.43 | 27.6
2019-06-25 04:30 | 29.73 | 28.95
2019-06-25 05:00 | 30.89 | 30.15
2019-06-25 05:30 | 34.35 | 33.71
2019-06-25 06:00 | 36.83 | 36.25
2019-06-25 06:30 | 41.46 | 40.97
2019-06-25 07:00 | 45.82 | 45.4
2019-06-25 07:30 | 51.2 | 50.82
2019-06-25 08:00 | 52.05 | 51.68
2019-06-25 08:30 | 50.75 | 50.38
2019-06-25 09:00 | 47.71 | 47.25
2019-06-25 09:30 | 45.56 | 45.09
2019-06-25 10:00 | 44.21 | 43.67
2019-06-25 10:30 | 44.3 | 43.66
2019-06-25 11:00 | 44.06 | 43.21
2019-06-25 11:30 | 42.4 | 41.49
2019-06-25 12:00 | 41.99 | 41.09
2019-06-25 12:30 | 41.97 | 41.1
2019-06-25 13:00 | 41.15 | 40.35
2019-06-25 13:30 | 42.43 | 41.64
2019-06-25 14:00 | 41.22 | 40.4
2019-06-25 14:30 | 42.28 | 41.47
2019-06-25 15:00 | 42.92 | 42.19
2019-06-25 15:30 | 43.98 | 43.43
2019-06-25 16:00 | 45.08 | 44.66
2019-06-25 16:30 | 46.19 | 45.78
2019-06-25 17:00 | 48 | 47.59
2019-06-25 17:30 | 50.28 | 49.87
2019-06-25 18:00 | 52.63 | 52.23
2019-06-25 18:30 | 53.77 | 53.21
2019-06-25 19:00 | 56.43 | 52.79
2019-06-25 19:30 | 54.18 | 50.33
2019-06-25 20:00 | 52.47 | 48.44
2019-06-25 20:30 | 50.32 | 46.05
2019-06-25 21:00 | 48.62 | 44.12
2019-06-25 21:30 | 46.6 | 41.82
2019-06-25 22:00 | 44.39 | 39.25
2019-06-25 22:30 | 42.18 | 36.66
2019-06-25 23:00 | 41.04 | 35.3
2019-06-25 23:30 | 38.7 | 32.48
2019-06-26 | 37.24 | 30.67
2019-06-26 00:30 | 37 | 30.35
2019-06-26 01:00 | 36.18 | 29.34
2019-06-26 01:30 | 33.02 | 28.26
2019-06-26 02:00 | 28.42 | 27.59
2019-06-26 02:30 | 28.1 | 27.26
2019-06-26 03:00 | 27.54 | 26.67
2019-06-26 03:30 | 27.84 | 26.98
2019-06-26 04:00 | 28.06 | 27.21
2019-06-26 04:30 | 29.23 | 28.42
2019-06-26 05:00 | 30.91 | 30.16
2019-06-26 05:30 | 34.14 | 33.48
2019-06-26 06:00 | 37.53 | 36.95
2019-06-26 06:30 | 42.11 | 41.62
2019-06-26 07:00 | 46.23 | 45.82
2019-06-26 07:30 | 50.84 | 50.44
2019-06-26 08:00 | 50.85 | 50.46
2019-06-26 08:30 | 49.06 | 48.68
2019-06-26 09:00 | 46.54 | 46.13
2019-06-26 09:30 | 44.7 | 44.26
2019-06-26 10:00 | 43.36 | 42.82
2019-06-26 10:30 | 42.36 | 41.66
2019-06-26 11:00 | 42.49 | 41.61
2019-06-26 11:30 | 42.53 | 41.59
2019-06-26 12:00 | 42.65 | 41.65
2019-06-26 12:30 | 42.8 | 41.86
2019-06-26 13:00 | 42.45 | 41.56
2019-06-26 13:30 | 42.1 | 41.2
2019-06-26 14:00 | 42.96 | 42.05
2019-06-26 14:30 | 43.92 | 43.05
2019-06-26 15:00 | 44.37 | 43.58
2019-06-26 15:30 | 45.29 | 44.6
2019-06-26 16:00 | 46.11 | 45.58
2019-06-26 16:30 | 47.43 | 47.04
2019-06-26 17:00 | 49.81 | 49.42
2019-06-26 17:30 | 51 | 50.6
2019-06-26 18:00 | 53.86 | 53.48
2019-06-26 18:30 | 54.48 | 54.1
2019-06-26 19:00 | 53.42 | 53.03
2019-06-26 19:30 | 51.37 | 50.95
2019-06-26 20:00 | 49.22 | 48.77
2019-06-26 20:30 | 46.93 | 46.45
2019-06-26 21:00 | 44.77 | 44.25
2019-06-26 21:30 | 43.07 | 42.52
2019-06-26 22:00 | 40.36 | 39.83
2019-06-26 22:30 | 37.74 | 37.16
2019-06-26 23:00 | 36.75 | 36.15
2019-06-26 23:30 | 35 | 34.35
2019-06-27 | 32.06 | 31.34
2019-06-27 00:30 | 32.21 | 31.49
2019-06-27 01:00 | 30.19 | 29.42
2019-06-27 01:30 | 29.48 | 28.67
2019-06-27 02:00 | 29.61 | 28.81
2019-06-27 02:30 | 29.66 | 28.86
2019-06-27 03:00 | 28.54 | 27.7
2019-06-27 03:30 | 28.6 | 27.77
2019-06-27 04:00 | 28.51 | 27.68
2019-06-27 04:30 | 30.32 | 29.54
2019-06-27 05:00 | 31.06 | 30.29
2019-06-27 05:30 | 33.75 | 33.04
2019-06-27 06:00 | 36.16 | 35.48
2019-06-27 06:30 | 40.7 | 40.08
2019-06-27 07:00 | 44.91 | 44.39
2019-06-27 07:30 | 49.24 | 48.83
2019-06-27 08:00 | 52.37 | 52.01
2019-06-27 08:30 | 53.22 | 52.79
2019-06-27 09:00 | 52.95 | 52.48
2019-06-27 09:30 | 51.12 | 50.59
2019-06-27 10:00 | 49.17 | 48.59
2019-06-27 10:30 | 49.43 | 48.79
2019-06-27 11:00 | 48.18 | 47.41
2019-06-27 11:30 | 52.35 | 51.28
2019-06-27 12:00 | 54.47 | 50.76
2019-06-27 12:30 | 51.65 | 47.56
2019-06-27 13:00 | 50.13 | 45.76
2019-06-27 13:30 | 53.38 | 49.34
2019-06-27 14:00 | 53.64 | 49.62
2019-06-27 14:30 | 53.07 | 48.95
2019-06-27 15:00 | 53.31 | 49.19
2019-06-27 15:30 | 54.33 | 50.25
2019-06-27 16:00 | 55.48 | 51.45
2019-06-27 16:30 | 55.83 | 51.76
2019-06-27 17:00 | 56.11 | 52.03
2019-06-27 17:30 | 56.73 | 52.63
2019-06-27 18:00 | 59.25 | 55.38
2019-06-27 18:30 | 59.72 | 55.85
2019-06-27 19:00 | 59.14 | 55.28
2019-06-27 19:30 | 56.51 | 52.57
2019-06-27 20:00 | 54.77 | 50.65
2019-06-27 20:30 | 52.89 | 48.54
2019-06-27 21:00 | 48.79 | 46.65
2019-06-27 21:30 | 44.72 | 44.18
2019-06-27 22:00 | 42.02 | 41.45
2019-06-27 22:30 | 38.42 | 37.86
2019-06-27 23:00 | 36.49 | 35.89
2019-06-27 23:30 | 33.97 | 33.31
2019-06-28 | 33.27 | 32.58
2019-06-28 00:30 | 32.77 | 32.08
2019-06-28 01:00 | 30.97 | 30.23
2019-06-28 01:30 | 30.92 | 30.17
2019-06-28 02:00 | 29.8 | 29.02
2019-06-28 02:30 | 29.03 | 28.22
2019-06-28 03:00 | 28.43 | 27.59
2019-06-28 03:30 | 29.29 | 28.48
2019-06-28 04:00 | 30.45 | 29.68
2019-06-28 04:30 | 31.55 | 30.8
2019-06-28 05:00 | 31.15 | 30.4
2019-06-28 05:30 | 33.84 | 33.17
2019-06-28 06:00 | 36.95 | 36.37
2019-06-28 06:30 | 41.73 | 41.25
2019-06-28 07:00 | 45.1 | 44.66
2019-06-28 07:30 | 49.94 | 49.55
2019-06-28 08:00 | 51.1 | 50.73
2019-06-28 08:30 | 51.52 | 51.07
2019-06-28 09:00 | 53.03 | 52.42
2019-06-28 09:30 | 52.76 | 52.04
2019-06-28 10:00 | 47.24 | 46.33
2019-06-28 10:30 | 46.34 | 45.71
2019-06-28 11:00 | 46.05 | 45.63
2019-06-28 11:30 | 45.64 | 45.22
2019-06-28 12:00 | 45.22 | 44.79
2019-06-28 12:30 | 44.37 | 43.93
2019-06-28 13:00 | 44.75 | 44.32
2019-06-28 13:30 | 45.19 | 44.77
2019-06-28 14:00 | 46.28 | 45.86
2019-06-28 14:30 | 47.65 | 47.23
2019-06-28 15:00 | 47.13 | 46.7
2019-06-28 15:30 | 49.09 | 48.66
2019-06-28 16:00 | 47.35 | 46.9
2019-06-28 16:30 | 47.82 | 47.36
2019-06-28 17:00 | 49.66 | 49.23
2019-06-28 17:30 | 49.85 | 49.44
2019-06-28 18:00 | 51.79 | 51.39
2019-06-28 18:30 | 53.21 | 52.81
2019-06-28 19:00 | 52.27 | 51.86
2019-06-28 19:30 | 50.14 | 49.71
2019-06-28 20:00 | 47.59 | 47.13
2019-06-28 20:30 | 45.66 | 45.17
2019-06-28 21:00 | 43.43 | 42.91
2019-06-28 21:30 | 42.06 | 41.5
2019-06-28 22:00 | 39.73 | 39.13
2019-06-28 22:30 | 38.26 | 37.7
2019-06-28 23:00 | 37.29 | 36.71
2019-06-28 23:30 | 35.71 | 35.1
2019-06-29 | 33.79 | 33.13
2019-06-29 00:30 | 32.38 | 31.68
2019-06-29 01:00 | 30.25 | 29.49
2019-06-29 01:30 | 28.66 | 27.83
2019-06-29 02:00 | 28.42 | 27.59
2019-06-29 02:30 | 27.89 | 27.03
2019-06-29 03:00 | 27.87 | 27.02
2019-06-29 03:30 | 28.13 | 27.29
2019-06-29 04:00 | 28.59 | 27.76
2019-06-29 04:30 | 28.56 | 27.74
2019-06-29 05:00 | 28.56 | 27.75
2019-06-29 05:30 | 30.4 | 29.64
2019-06-29 06:00 | 31.07 | 30.33
2019-06-29 06:30 | 32.9 | 32.21
2019-06-29 07:00 | 35.28 | 34.65
2019-06-29 07:30 | 38.17 | 37.61
2019-06-29 08:00 | 38.65 | 38.11
2019-06-29 08:30 | 38.07 | 37.54
2019-06-29 09:00 | 39.77 | 39.28
2019-06-29 09:30 | 39.72 | 39.25
2019-06-29 10:00 | 38.24 | 37.75
2019-06-29 10:30 | 36.72 | 36.21
2019-06-29 11:00 | 35.97 | 35.43
2019-06-29 11:30 | 32.89 | 32.3
2019-06-29 12:00 | 32.53 | 31.96
2019-06-29 12:30 | 31.66 | 31.06
2019-06-29 13:00 | 30.84 | 30.22
2019-06-29 13:30 | 30.65 | 30.02
2019-06-29 14:00 | 30.87 | 30.25
2019-06-29 14:30 | 32.03 | 31.42
2019-06-29 15:00 | 31.84 | 31.22
2019-06-29 15:30 | 32.54 | 31.92
2019-06-29 16:00 | 33.87 | 33.26
2019-06-29 16:30 | 35.93 | 35.35
2019-06-29 17:00 | 39.04 | 38.51
2019-06-29 17:30 | 41.72 | 41.22
2019-06-29 18:00 | 43.58 | 43.11
2019-06-29 18:30 | 45.92 | 45.48
2019-06-29 19:00 | 43.84 | 43.37
2019-06-29 19:30 | 41.67 | 41.16
2019-06-29 20:00 | 40.79 | 40.27
2019-06-29 20:30 | 39.49 | 38.95
2019-06-29 21:00 | 39.67 | 39.13
2019-06-29 21:30 | 37.73 | 37.15
2019-06-29 22:00 | 36.04 | 35.41
2019-06-29 22:30 | 35.45 | 34.81
2019-06-29 23:00 | 33.82 | 33.14
2019-06-29 23:30 | 31.89 | 31.16
2019-06-30 | 31.2 | 30.44
2019-06-30 00:30 | 29.73 | 28.92
2019-06-30 01:00 | 29.38 | 28.55
2019-06-30 01:30 | 29.04 | 28.21
2019-06-30 02:00 | 28.8 | 27.96
2019-06-30 02:30 | 28.3 | 27.44
2019-06-30 03:00 | 27.16 | 26.26
2019-06-30 03:30 | 27.13 | 26.23
2019-06-30 04:00 | 27.38 | 26.48
2019-06-30 04:30 | 26.85 | 25.94
2019-06-30 05:00 | 26.7 | 25.78
2019-06-30 05:30 | 27.32 | 26.42
2019-06-30 06:00 | 27.97 | 27.1
2019-06-30 06:30 | 29.54 | 28.73
2019-06-30 07:00 | 30.32 | 29.52
2019-06-30 07:30 | 31.65 | 30.89
2019-06-30 08:00 | 31.64 | 30.88
2019-06-30 08:30 | 31.53 | 30.79
2019-06-30 09:00 | 31.57 | 30.84
2019-06-30 09:30 | 32.44 | 31.75
2019-06-30 10:00 | 31.02 | 30.31
2019-06-30 10:30 | 30.26 | 29.55
2019-06-30 11:00 | 29.29 | 28.57
2019-06-30 11:30 | 28.97 | 28.25
2019-06-30 12:00 | 29.96 | 29.26
2019-06-30 12:30 | 25.69 | 24.89
2019-06-30 13:00 | 29 | 28.29
2019-06-30 13:30 | 28.73 | 28.02
2019-06-30 14:00 | 28.15 | 27.41
2019-06-30 14:30 | 28.31 | 27.57
2019-06-30 15:00 | 29.99 | 29.29
2019-06-30 15:30 | 32.14 | 31.48
2019-06-30 16:00 | 33.55 | 32.91
2019-06-30 16:30 | 35.86 | 35.27
2019-06-30 17:00 | 38.05 | 37.49
2019-06-30 17:30 | 40.34 | 39.81
2019-06-30 18:00 | 44.91 | 44.45
2019-06-30 18:30 | 47.46 | 47.03
2019-06-30 19:00 | 46.19 | 45.75
2019-06-30 19:30 | 44.05 | 43.58
2019-06-30 20:00 | 42.33 | 41.84
2019-06-30 20:30 | 40.14 | 39.61
2019-06-30 21:00 | 38.41 | 37.84
2019-06-30 21:30 | 37.09 | 36.5
2019-06-30 22:00 | 35.26 | 34.62
2019-06-30 22:30 | 33.43 | 32.74
2019-06-30 23:00 | 31.86 | 31.13
2019-06-30 23:30 | 30.1 | 29.31
2019-07-01 | 28.72 | 27.88
2019-07-01 00:30 | 27.99 | 27.12
2019-07-01 01:00 | 27.5 | 26.61
2019-07-01 01:30 | 27.18 | 26.28
2019-07-01 02:00 | 26.74 | 25.83
2019-07-01 02:30 | 26.17 | 25.23
2019-07-01 03:00 | 25.83 | 24.87
2019-07-01 03:30 | 26.37 | 25.44
2019-07-01 04:00 | 27.05 | 26.14
2019-07-01 04:30 | 27.35 | 26.46
2019-07-01 05:00 | 28.49 | 27.65
2019-07-01 05:30 | 31.33 | 30.59
2019-07-01 06:00 | 33.9 | 33.24
2019-07-01 06:30 | 38.3 | 37.75
2019-07-01 07:00 | 41.2 | 40.72
2019-07-01 07:30 | 45.57 | 45.11
2019-07-01 08:00 | 46.82 | 46.29
2019-07-01 08:30 | 46.48 | 46.08
2019-07-01 09:00 | 45.95 | 45.49
2019-07-01 09:30 | 45.68 | 45.13
2019-07-01 10:00 | 40.67 | 40.16
2019-07-01 10:30 | 44.32 | 42.91
2019-07-01 11:00 | 45.27 | 43.32
2019-07-01 11:30 | 44.6 | 42.65
2019-07-01 12:00 | 44.51 | 42.57
2019-07-01 12:30 | 44.18 | 42.21
2019-07-01 13:00 | 44.4 | 42.43
2019-07-01 13:30 | 44.23 | 42.26
2019-07-01 14:00 | 44.87 | 42.93
2019-07-01 14:30 | 45.18 | 43.25
2019-07-01 15:00 | 46.28 | 44.38
2019-07-01 15:30 | 47.5 | 45.63
2019-07-01 16:00 | 47.89 | 45.99
2019-07-01 16:30 | 48.74 | 46.82
2019-07-01 17:00 | 50.12 | 48.23
2019-07-01 17:30 | 50.15 | 48.2
2019-07-01 18:00 | 49.67 | 47.76
2019-07-01 18:30 | 54.6 | 52.78
2019-07-01 19:00 | 53.9 | 52.05
2019-07-01 19:30 | 50.99 | 48.99
2019-07-01 20:00 | 48.61 | 46.58
2019-07-01 20:30 | 46.71 | 44.61
2019-07-01 21:00 | 44.84 | 42.63
2019-07-01 21:30 | 42.53 | 40.15
2019-07-01 22:00 | 40.39 | 38
2019-07-01 22:30 | 37.98 | 35.43
2019-07-01 23:00 | 36.16 | 33.47
2019-07-01 23:30 | 34.57 | 31.71
2019-07-02 | 32.89 | 29.85
2019-07-02 00:30 | 32.82 | 29.75
2019-07-02 01:00 | 31.6 | 28.37
2019-07-02 01:30 | 31.18 | 27.9
2019-07-02 02:00 | 30.6 | 27.24
2019-07-02 02:30 | 30.02 | 26.58
2019-07-02 03:00 | 29.93 | 26.46
2019-07-02 03:30 | 30 | 26.53
2019-07-02 04:00 | 30.23 | 26.81
2019-07-02 04:30 | 31.93 | 28.73
2019-07-02 05:00 | 32.1 | 28.95
2019-07-02 05:30 | 34.18 | 31.28
2019-07-02 06:00 | 36.49 | 33.84
2019-07-02 06:30 | 40.42 | 38.12
2019-07-02 07:00 | 44.11 | 42.08
2019-07-02 07:30 | 48.03 | 46.18
2019-07-02 08:00 | 49.23 | 47.42
2019-07-02 08:30 | 49 | 47.21
2019-07-02 09:00 | 47.65 | 45.84
2019-07-02 09:30 | 47.91 | 46.14
2019-07-02 10:00 | 45.95 | 44.13
2019-07-02 10:30 | 45.95 | 44.11
2019-07-02 11:00 | 45.45 | 43.51
2019-07-02 11:30 | 45.42 | 43.49
2019-07-02 12:00 | 44.56 | 42.62
2019-07-02 12:30 | 44.28 | 42.33
2019-07-02 13:00 | 44.52 | 42.57
2019-07-02 13:30 | 45.32 | 43.39
2019-07-02 14:00 | 45.25 | 43.32
2019-07-02 14:30 | 46.06 | 44.16
2019-07-02 15:00 | 46.65 | 44.77
2019-07-02 15:30 | 47.98 | 46.14
2019-07-02 16:00 | 48.87 | 47.04
2019-07-02 16:30 | 50.33 | 48.5
2019-07-02 17:00 | 51.49 | 49.66
2019-07-02 17:30 | 51.75 | 49.87
2019-07-02 18:00 | 53.23 | 51.39
2019-07-02 18:30 | 54.69 | 52.87
2019-07-02 19:00 | 53.47 | 51.61
2019-07-02 19:30 | 51 | 49
2019-07-02 20:00 | 48.87 | 46.75
2019-07-02 20:30 | 47.05 | 44.83
2019-07-02 21:00 | 44.63 | 42.25
2019-07-02 21:30 | 42.85 | 40.37
2019-07-02 22:00 | 41.65 | 39.2
2019-07-02 22:30 | 38.76 | 36.09
2019-07-02 23:00 | 37.46 | 34.68
2019-07-02 23:30 | 35.2 | 32.19
2019-07-03 | 33.24 | 30
2019-07-03 00:30 | 30.21 | 29.38
2019-07-03 01:00 | 28.79 | 28.41
2019-07-03 01:30 | 28.11 | 27.81
2019-07-03 02:00 | 27.36 | 27.36
2019-07-03 02:30 | 27.15 | 27.13
2019-07-03 03:00 | 27.56 | 27.54
2019-07-03 03:30 | 27.14 | 27.11
2019-07-03 04:00 | 26.91 | 26.89
2019-07-03 04:30 | 28.11 | 28.1
2019-07-03 05:00 | 29.25 | 29.25
2019-07-03 05:30 | 31.92 | 31.91
2019-07-03 06:00 | 34.81 | 34.77
2019-07-03 06:30 | 39.09 | 38.95
2019-07-03 07:00 | 42.89 | 42.58
2019-07-03 07:30 | 46.86 | 46.67
2019-07-03 08:00 | 49.65 | 49.43
2019-07-03 08:30 | 49.72 | 49.31
2019-07-03 09:00 | 48.58 | 48.12
2019-07-03 09:30 | 47.81 | 47.23
2019-07-03 10:00 | 47.68 | 47.05
2019-07-03 10:30 | 47.79 | 46.98
2019-07-03 11:00 | 46.23 | 45.19
2019-07-03 11:30 | 46.84 | 45.33
2019-07-03 12:00 | 46.33 | 44.52
2019-07-03 12:30 | 47.2 | 45.42
2019-07-03 13:00 | 46.35 | 44.52
2019-07-03 13:30 | 48 | 46.24
2019-07-03 14:00 | 49.47 | 47.77
2019-07-03 14:30 | 48.67 | 46.92
2019-07-03 15:00 | 49.35 | 47.63
2019-07-03 15:30 | 50 | 48.27
2019-07-03 16:00 | 50.66 | 48.91
2019-07-03 16:30 | 51.39 | 49.63
2019-07-03 17:00 | 52.47 | 50.73
2019-07-03 17:30 | 52.45 | 50.64
2019-07-03 18:00 | 54.38 | 52.64
2019-07-03 18:30 | 55.43 | 53.71
2019-07-03 19:00 | 54.19 | 52.41
2019-07-03 19:30 | 51.63 | 49.73
2019-07-03 20:00 | 49.81 | 47.81
2019-07-03 20:30 | 48.38 | 46.3
2019-07-03 21:00 | 46.62 | 44.43
2019-07-03 21:30 | 44.9 | 42.58
2019-07-03 22:00 | 42.83 | 40.4
2019-07-03 22:30 | 39.74 | 37.22
2019-07-03 23:00 | 38.11 | 35.46
2019-07-03 23:30 | 36 | 33.16
2019-07-04 | 34.62 | 31.64
2019-07-04 00:30 | 34.22 | 31.17
2019-07-04 01:00 | 33.08 | 29.91
2019-07-04 01:30 | 32.88 | 29.68
2019-07-04 02:00 | 32.13 | 28.98
2019-07-04 02:30 | 31.7 | 28.58
2019-07-04 03:00 | 30.62 | 27.36
2019-07-04 03:30 | 31.29 | 28.09
2019-07-04 04:00 | 30.89 | 27.63
2019-07-04 04:30 | 31.98 | 28.86
2019-07-04 05:00 | 33.29 | 30.31
2019-07-04 05:30 | 34.89 | 32.1
2019-07-04 06:00 | 37.31 | 34.8
2019-07-04 06:30 | 40.71 | 38.49
2019-07-04 07:00 | 43.69 | 41.7
2019-07-04 07:30 | 48.57 | 46.8
2019-07-04 08:00 | 50.7 | 49.03
2019-07-04 08:30 | 51.93 | 50.34
2019-07-04 09:00 | 52.06 | 50.5
2019-07-04 09:30 | 50.47 | 48.87
2019-07-04 10:00 | 49.25 | 47.63
2019-07-04 10:30 | 49.62 | 48.04
2019-07-04 11:00 | 51.03 | 49.42
2019-07-04 11:30 | 52.58 | 50.98
2019-07-04 12:00 | 55.12 | 53.59
2019-07-04 12:30 | 56.46 | 54.96
2019-07-04 13:00 | 56.55 | 55.04
2019-07-04 13:30 | 55.51 | 53.96
2019-07-04 14:00 | 54.7 | 53.14
2019-07-04 14:30 | 55.04 | 53.47
2019-07-04 15:00 | 55.01 | 53.44
2019-07-04 15:30 | 55.31 | 53.73
2019-07-04 16:00 | 55.1 | 53.46
2019-07-04 16:30 | 55.04 | 53.37
2019-07-04 17:00 | 54.57 | 52.85
2019-07-04 17:30 | 55.2 | 53.46
2019-07-04 18:00 | 57.07 | 55.39
2019-07-04 18:30 | 56.42 | 54.71
2019-07-04 19:00 | 55.37 | 53.62
2019-07-04 19:30 | 53.05 | 51.19
2019-07-04 20:00 | 51.38 | 49.43
2019-07-04 20:30 | 50.04 | 48
2019-07-04 21:00 | 48.25 | 46.12
2019-07-04 21:30 | 44.91 | 42.58
2019-07-04 22:00 | 42.82 | 40.33
2019-07-04 22:30 | 40.18 | 37.63
2019-07-04 23:00 | 38.45 | 35.81
2019-07-04 23:30 | 36.54 | 33.73
2019-07-05 | 34.84 | 31.85
2019-07-05 00:30 | 32.57 | 30.89
2019-07-05 01:00 | 29.98 | 29.73
2019-07-05 01:30 | 29.08 | 28.81
2019-07-05 02:00 | 29.25 | 29.11
2019-07-05 02:30 | 27.77 | 27.76
2019-07-05 03:00 | 27.39 | 27.38
2019-07-05 03:30 | 26.6 | 26.58
2019-07-05 04:00 | 26.76 | 26.73
2019-07-05 04:30 | 27.24 | 27.22
2019-07-05 05:00 | 29.34 | 29.34
2019-07-05 05:30 | 33.27 | 33.26
2019-07-05 06:00 | 35.64 | 35.6
2019-07-05 06:30 | 39.74 | 39.58
2019-07-05 07:00 | 43.64 | 43.25
2019-07-05 07:30 | 48.63 | 48.44
2019-07-05 08:00 | 52.18 | 51.84
2019-07-05 08:30 | 55.11 | 54.61
2019-07-05 09:00 | 55.69 | 55.21
2019-07-05 09:30 | 55.95 | 55.46
2019-07-05 10:00 | 55.86 | 55.36
2019-07-05 10:30 | 55.29 | 54.77
2019-07-05 11:00 | 56.03 | 55.42
2019-07-05 11:30 | 51.37 | 50.77
2019-07-05 12:00 | 51.31 | 50.74
2019-07-05 12:30 | 47.43 | 46.94
2019-07-05 13:00 | 45.75 | 45.28
2019-07-05 13:30 | 45.67 | 45.21
2019-07-05 14:00 | 48.72 | 48.31
2019-07-05 14:30 | 47.5 | 47.1
2019-07-05 15:00 | 48.21 | 47.82
2019-07-05 15:30 | 48.66 | 48.26
2019-07-05 16:00 | 46.51 | 46.08
2019-07-05 16:30 | 47.15 | 46.71
2019-07-05 17:00 | 49.55 | 49.13
2019-07-05 17:30 | 51.27 | 50.85
2019-07-05 18:00 | 52.41 | 52
2019-07-05 18:30 | 52.51 | 52.09
2019-07-05 19:00 | 51.41 | 50.98
2019-07-05 19:30 | 49.64 | 49.19
2019-07-05 20:00 | 47.46 | 46.98
2019-07-05 20:30 | 46.18 | 45.68
2019-07-05 21:00 | 44.24 | 43.71
2019-07-05 21:30 | 42.9 | 42.34
2019-07-05 22:00 | 41.8 | 41.22
2019-07-05 22:30 | 39.94 | 39.32
2019-07-05 23:00 | 39.23 | 38.58
2019-07-05 23:30 | 37.19 | 36.49
2019-07-06 | 35.51 | 34.77
2019-07-06 00:30 | 34.39 | 33.61
2019-07-06 01:00 | 33.46 | 32.66
2019-07-06 01:30 | 32.63 | 31.81
2019-07-06 02:00 | 32.04 | 31.2
2019-07-06 02:30 | 31.38 | 30.59
2019-07-06 03:00 | 31.18 | 30.41
2019-07-06 03:30 | 30.73 | 29.94
2019-07-06 04:00 | 30.78 | 30
2019-07-06 04:30 | 31.69 | 30.94
2019-07-06 05:00 | 31.86 | 31.12
2019-07-06 05:30 | 32.91 | 32.2
2019-07-06 06:00 | 34.05 | 33.37
2019-07-06 06:30 | 35.98 | 35.35
2019-07-06 07:00 | 37.38 | 36.79
2019-07-06 07:30 | 39.98 | 39.44
2019-07-06 08:00 | 42.75 | 42.26
2019-07-06 08:30 | 45.62 | 45.18
2019-07-06 09:00 | 47.61 | 47.2
2019-07-06 09:30 | 48.52 | 48.12
2019-07-06 10:00 | 48.51 | 48.11
2019-07-06 10:30 | 48.31 | 47.91
2019-07-06 11:00 | 46.9 | 46.49
2019-07-06 11:30 | 48.38 | 48
2019-07-06 12:00 | 43.8 | 43.37
2019-07-06 12:30 | 43.92 | 43.48
2019-07-06 13:00 | 41.58 | 41.11
2019-07-06 13:30 | 42.17 | 41.71
2019-07-06 14:00 | 42.98 | 42.51
2019-07-06 14:30 | 41.95 | 41.47
2019-07-06 15:00 | 42.94 | 42.47
2019-07-06 15:30 | 43.32 | 42.85
2019-07-06 16:00 | 44.14 | 43.67
2019-07-06 16:30 | 45.81 | 45.36
2019-07-06 17:00 | 46.35 | 45.9
2019-07-06 17:30 | 47.28 | 46.84
2019-07-06 18:00 | 50.15 | 49.75
2019-07-06 18:30 | 50.54 | 50.15
2019-07-06 19:00 | 49.43 | 49.02
2019-07-06 19:30 | 47.83 | 47.4
2019-07-06 20:00 | 46.21 | 45.77
2019-07-06 20:30 | 44.49 | 44.02
2019-07-06 21:00 | 42.9 | 42.4
2019-07-06 21:30 | 41.2 | 40.68
2019-07-06 22:00 | 40.52 | 39.99
2019-07-06 22:30 | 39.05 | 38.48
2019-07-06 23:00 | 37.63 | 37.02
2019-07-06 23:30 | 36.25 | 35.62
2019-07-07 | 35.37 | 34.71
2019-07-07 00:30 | 34.22 | 33.54
2019-07-07 01:00 | 33.17 | 32.46
2019-07-07 01:30 | 32.53 | 31.81
2019-07-07 02:00 | 31.92 | 31.18
2019-07-07 02:30 | 31.98 | 31.25
2019-07-07 03:00 | 31.25 | 30.48
2019-07-07 03:30 | 30.91 | 30.13
2019-07-07 04:00 | 30.75 | 29.97
2019-07-07 04:30 | 31.71 | 30.97
2019-07-07 05:00 | 31.99 | 31.25
2019-07-07 05:30 | 32.37 | 31.64
2019-07-07 06:00 | 33.07 | 32.36
2019-07-07 06:30 | 33.82 | 33.13
2019-07-07 07:00 | 33.96 | 33.25
2019-07-07 07:30 | 35.7 | 35.04
2019-07-07 08:00 | 37.32 | 36.69
2019-07-07 08:30 | 38.24 | 37.65
2019-07-07 09:00 | 39.88 | 39.32
2019-07-07 09:30 | 41.56 | 41.04
2019-07-07 10:00 | 42.14 | 41.64
2019-07-07 10:30 | 43.89 | 43.41
2019-07-07 11:00 | 42.62 | 42.13
2019-07-07 11:30 | 43.64 | 43.16
2019-07-07 12:00 | 44.23 | 43.76
2019-07-07 12:30 | 42.76 | 42.27
2019-07-07 13:00 | 43.1 | 42.61
2019-07-07 13:30 | 43.15 | 42.67
2019-07-07 14:00 | 41.57 | 41.07
2019-07-07 14:30 | 41.5 | 41
2019-07-07 15:00 | 42.38 | 41.89
2019-07-07 15:30 | 42.8 | 42.31
2019-07-07 16:00 | 43.21 | 42.72
2019-07-07 16:30 | 44.11 | 43.63
2019-07-07 17:00 | 45.46 | 45
2019-07-07 17:30 | 47.19 | 46.75
2019-07-07 18:00 | 50.68 | 50.28
2019-07-07 18:30 | 52.3 | 51.92
2019-07-07 19:00 | 51.31 | 50.92
2019-07-07 19:30 | 49.04 | 48.62
2019-07-07 20:00 | 46.66 | 46.21
2019-07-07 20:30 | 45.28 | 44.82
2019-07-07 21:00 | 43.66 | 43.18
2019-07-07 21:30 | 41.81 | 41.29
2019-07-07 22:00 | 40.55 | 40.01
2019-07-07 22:30 | 38.35 | 37.77
2019-07-07 23:00 | 36.9 | 36.29
2019-07-07 23:30 | 34.78 | 34.13
2019-07-08 | 33.23 | 32.52
2019-07-08 00:30 | 31.9 | 31.15
2019-07-08 01:00 | 31.56 | 30.8
2019-07-08 01:30 | 31.18 | 30.42
2019-07-08 02:00 | 31.26 | 30.5
2019-07-08 02:30 | 30.92 | 30.15
2019-07-08 03:00 | 30.65 | 29.88
2019-07-08 03:30 | 30.41 | 29.62
2019-07-08 04:00 | 30.87 | 30.09
2019-07-08 04:30 | 31.9 | 31.16
2019-07-08 05:00 | 33 | 32.3
2019-07-08 05:30 | 35.49 | 34.86
2019-07-08 06:00 | 38.38 | 37.82
2019-07-08 06:30 | 29.05 | 28.18
2019-07-08 07:00 | 43.19 | 42.73
2019-07-08 07:30 | 50.93 | 50.53
2019-07-08 08:00 | 51.89 | 51.53
2019-07-08 08:30 | 53.89 | 53.47
2019-07-08 09:00 | 54.49 | 54
2019-07-08 09:30 | 53.88 | 53.25
2019-07-08 10:00 | 51.84 | 51.09
2019-07-08 10:30 | 49.57 | 49.19
2019-07-08 11:00 | 49.89 | 49.51
2019-07-08 11:30 | 50.35 | 49.88
2019-07-08 12:00 | 51.83 | 51.38
2019-07-08 12:30 | 52.37 | 51.99
2019-07-08 13:00 | 51.76 | 51.4
2019-07-08 13:30 | 50.08 | 49.7
2019-07-08 14:00 | 49.85 | 49.44
2019-07-08 14:30 | 52.67 | 52.32
2019-07-08 15:00 | 54.9 | 54.56
2019-07-08 15:30 | 54.12 | 53.76
2019-07-08 16:00 | 52.97 | 52.59
2019-07-08 16:30 | 53.28 | 52.88
2019-07-08 17:00 | 54.27 | 53.86
2019-07-08 17:30 | 54.61 | 54.18
2019-07-08 18:00 | 56.33 | 55.9
2019-07-08 18:30 | 57 | 56.58
2019-07-08 19:00 | 55.41 | 54.97
2019-07-08 19:30 | 52.71 | 52.23
2019-07-08 20:00 | 50.58 | 50.07
2019-07-08 20:30 | 48.91 | 48.38
2019-07-08 21:00 | 46.88 | 46.31
2019-07-08 21:30 | 44.55 | 43.93
2019-07-08 22:00 | 42.68 | 42.08
2019-07-08 22:30 | 39.77 | 39.15
2019-07-08 23:00 | 38.44 | 37.79
2019-07-08 23:30 | 36.39 | 35.69
2019-07-09 | 34.27 | 33.5
2019-07-09 00:30 | 33.54 | 32.75
2019-07-09 01:00 | 32.94 | 32.13
2019-07-09 01:30 | 32.22 | 31.39
2019-07-09 02:00 | 31.38 | 30.52
2019-07-09 02:30 | 31.32 | 30.45
2019-07-09 03:00 | 31.23 | 30.36
2019-07-09 03:30 | 31.18 | 30.3
2019-07-09 04:00 | 31.38 | 30.51
2019-07-09 04:30 | 32.24 | 31.39
2019-07-09 05:00 | 33.43 | 32.63
2019-07-09 05:30 | 35.72 | 34.99
2019-07-09 06:00 | 37.88 | 37.21
2019-07-09 06:30 | 42.52 | 41.96
2019-07-09 07:00 | 45.61 | 45.13
2019-07-09 07:30 | 49.94 | 49.53
2019-07-09 08:00 | 52.16 | 51.79
2019-07-09 08:30 | 53.44 | 53.07
2019-07-09 09:00 | 53.72 | 53.22
2019-07-09 09:30 | 52.05 | 51.46
2019-07-09 10:00 | 51.28 | 50.58
2019-07-09 10:30 | 50.03 | 49.13
2019-07-09 11:00 | 48.91 | 48.22
2019-07-09 11:30 | 48.11 | 47.66
2019-07-09 12:00 | 48.36 | 47.86
2019-07-09 12:30 | 48.09 | 47.64
2019-07-09 13:00 | 49.24 | 48.86
2019-07-09 13:30 | 48.53 | 48.13
2019-07-09 14:00 | 50.06 | 49.67
2019-07-09 14:30 | 50.7 | 50.33
2019-07-09 15:00 | 51.84 | 51.49
2019-07-09 15:30 | 51.38 | 51.02
2019-07-09 16:00 | 53.52 | 53.16
2019-07-09 16:30 | 53.95 | 53.57
2019-07-09 17:00 | 53.95 | 53.54
2019-07-09 17:30 | 54.67 | 54.24
2019-07-09 18:00 | 57.04 | 56.63
2019-07-09 18:30 | 58.07 | 57.66
2019-07-09 19:00 | 56.79 | 56.36
2019-07-09 19:30 | 53.96 | 53.49
2019-07-09 20:00 | 51.88 | 51.39
2019-07-09 20:30 | 49.49 | 48.96
2019-07-09 21:00 | 47.88 | 47.33
2019-07-09 21:30 | 45.96 | 45.37
2019-07-09 22:00 | 43.68 | 43.12
2019-07-09 22:30 | 40.95 | 40.34
2019-07-09 23:00 | 38.92 | 38.28
2019-07-09 23:30 | 36.96 | 36.27
2019-07-10 | 35.22 | 34.54
2019-07-10 00:30 | 33.54 | 32.91
2019-07-10 01:00 | 32.63 | 31.98
2019-07-10 01:30 | 32.24 | 31.59
2019-07-10 02:00 | 31.76 | 31.1
2019-07-10 02:30 | 31.19 | 30.52
2019-07-10 03:00 | 31.01 | 30.34
2019-07-10 03:30 | 31.03 | 30.36
2019-07-10 04:00 | 31.69 | 31.04
2019-07-10 04:30 | 32.26 | 31.61
2019-07-10 05:00 | 33.33 | 32.71
2019-07-10 05:30 | 35.75 | 35.15
2019-07-10 06:00 | 38.53 | 37.96
2019-07-10 06:30 | 43.23 | 42.71
2019-07-10 07:00 | 46.55 | 46.05
2019-07-10 07:30 | 50.86 | 50.37
2019-07-10 08:00 | 53.73 | 53.28
2019-07-10 08:30 | 54.56 | 54.11
2019-07-10 09:00 | 54.03 | 53.51
2019-07-10 09:30 | 54.74 | 54.06
2019-07-10 10:00 | 53.54 | 52.73
2019-07-10 10:30 | 53.12 | 52.57
2019-07-10 11:00 | 52.38 | 52
2019-07-10 11:30 | 50.28 | 49.83
2019-07-10 12:00 | 50.02 | 49.47
2019-07-10 12:30 | 49.27 | 48.77
2019-07-10 13:00 | 49.51 | 49
2019-07-10 13:30 | 49.56 | 49
2019-07-10 14:00 | 50.51 | 49.95
2019-07-10 14:30 | 51.27 | 50.67
2019-07-10 15:00 | 51.79 | 51.28
2019-07-10 15:30 | 53.1 | 52.66
2019-07-10 16:00 | 54.95 | 54.58
2019-07-10 16:30 | 55.9 | 55.52
2019-07-10 17:00 | 55.46 | 55.06
2019-07-10 17:30 | 55.36 | 54.94
2019-07-10 18:00 | 56.59 | 56.17
2019-07-10 18:30 | 57.66 | 57.25
2019-07-10 19:00 | 57.08 | 56.66
2019-07-10 19:30 | 54.71 | 54.27
2019-07-10 20:00 | 52.38 | 51.9
2019-07-10 20:30 | 49.77 | 49.25
2019-07-10 21:00 | 47.73 | 47.18
2019-07-10 21:30 | 46.18 | 45.61
2019-07-10 22:00 | 43.47 | 42.84
2019-07-10 22:30 | 41.75 | 41.17
2019-07-10 23:00 | 41.31 | 40.73
2019-07-10 23:30 | 38.8 | 38.16
2019-07-11 | 36.11 | 35.42
2019-07-11 00:30 | 34.47 | 33.85
2019-07-11 01:00 | 34.37 | 33.74
2019-07-11 01:30 | 33.58 | 32.93
2019-07-11 02:00 | 32.77 | 32.12
2019-07-11 02:30 | 32.48 | 31.82
2019-07-11 03:00 | 32.16 | 31.5
2019-07-11 03:30 | 32.19 | 31.52
2019-07-11 04:00 | 31.98 | 31.31
2019-07-11 04:30 | 32.67 | 32.02
2019-07-11 05:00 | 34.15 | 33.52
2019-07-11 05:30 | 36.47 | 35.87
2019-07-11 06:00 | 38.83 | 38.26
2019-07-11 06:30 | 43.02 | 42.49
2019-07-11 07:00 | 46.62 | 46.11
2019-07-11 07:30 | 50.95 | 50.45
2019-07-11 08:00 | 53.36 | 52.88
2019-07-11 08:30 | 54.81 | 54.23
2019-07-11 09:00 | 52.42 | 51.62
2019-07-11 09:30 | 52.71 | 51.76
2019-07-11 10:00 | 52.11 | 51.33
2019-07-11 10:30 | 52.73 | 52.29
2019-07-11 11:00 | 51.43 | 50.94
2019-07-11 11:30 | 52.65 | 52.07
2019-07-11 12:00 | 55.85 | 55.32
2019-07-11 12:30 | 51.58 | 51.06
2019-07-11 13:00 | 52.27 | 51.79
2019-07-11 13:30 | 52.24 | 51.73
2019-07-11 14:00 | 52.81 | 52.3
2019-07-11 14:30 | 55.41 | 54.96
2019-07-11 15:00 | 54.1 | 53.67
2019-07-11 15:30 | 51.96 | 51.57
2019-07-11 16:00 | 52.89 | 52.53
2019-07-11 16:30 | 53.52 | 53.14
2019-07-11 17:00 | 54.82 | 54.43
2019-07-11 17:30 | 54.95 | 54.54
2019-07-11 18:00 | 56.69 | 56.28
2019-07-11 18:30 | 58.9 | 58.51
2019-07-11 19:00 | 58.01 | 57.61
2019-07-11 19:30 | 56.05 | 55.62
2019-07-11 20:00 | 53.48 | 53.01
2019-07-11 20:30 | 51.46 | 50.96
2019-07-11 21:00 | 49.94 | 49.42
2019-07-11 21:30 | 47.57 | 47.01
2019-07-11 22:00 | 44.7 | 44.13
2019-07-11 22:30 | 41.7 | 41.12
2019-07-11 23:00 | 40.58 | 39.97
2019-07-11 23:30 | 38.23 | 37.58
2019-07-12 | 35.99 | 35.37
2019-07-12 00:30 | 35.15 | 34.5
2019-07-12 01:00 | 34.01 | 33.33
2019-07-12 01:30 | 33.46 | 32.77
2019-07-12 02:00 | 33.1 | 32.39
2019-07-12 02:30 | 32.43 | 31.7
2019-07-12 03:00 | 31.95 | 31.2
2019-07-12 03:30 | 31.8 | 31.05
2019-07-12 04:00 | 31.82 | 31.08
2019-07-12 04:30 | 32.76 | 32.04
2019-07-12 05:00 | 34.05 | 33.35
2019-07-12 05:30 | 36.56 | 35.9
2019-07-12 06:00 | 39.1 | 38.48
2019-07-12 06:30 | 42.97 | 42.38
2019-07-12 07:00 | 46.61 | 46.08
2019-07-12 07:30 | 50.16 | 49.66
2019-07-12 08:00 | 51.87 | 51.37
2019-07-12 08:30 | 51.3 | 50.77
2019-07-12 09:00 | 45.2 | 44.47
2019-07-12 09:30 | 35.26 | 34.52
2019-07-12 10:00 | 33.58 | 32.78
2019-07-12 10:30 | 32.97 | 32.15
2019-07-12 11:00 | 32.75 | 31.98
2019-07-12 11:30 | 44.8 | 44.19
2019-07-12 12:00 | 45.93 | 45.34
2019-07-12 12:30 | 34.08 | 33.32
2019-07-12 13:00 | 32.04 | 31.25
2019-07-12 13:30 | 32.25 | 31.46
2019-07-12 14:00 | 32.06 | 31.27
2019-07-12 14:30 | 31.73 | 30.93
2019-07-12 15:00 | 45.48 | 44.91
2019-07-12 15:30 | 46.4 | 45.86
2019-07-12 16:00 | 46.48 | 45.96
2019-07-12 16:30 | 47.94 | 47.44
2019-07-12 17:00 | 47.62 | 47.13
2019-07-12 17:30 | 47.96 | 47.5
2019-07-12 18:00 | 50.77 | 50.34
2019-07-12 18:30 | 52.06 | 51.65
2019-07-12 19:00 | 50.62 | 50.2
2019-07-12 19:30 | 48.91 | 48.49
2019-07-12 20:00 | 46.51 | 46.07
2019-07-12 20:30 | 44.97 | 44.52
2019-07-12 21:00 | 43.01 | 42.54
2019-07-12 21:30 | 41.69 | 41.21
2019-07-12 22:00 | 39.67 | 39.11
2019-07-12 22:30 | 36.9 | 36.24
2019-07-12 23:00 | 35.63 | 34.96
2019-07-12 23:30 | 33.26 | 32.53
2019-07-13 | 31.35 | 30.59
2019-07-13 00:30 | 30.59 | 29.83
2019-07-13 01:00 | 29.55 | 28.77
2019-07-13 01:30 | 28.67 | 27.86
2019-07-13 02:00 | 27.9 | 27.08
2019-07-13 02:30 | 27.35 | 26.51
2019-07-13 03:00 | 27.43 | 26.6
2019-07-13 03:30 | 27.34 | 26.5
2019-07-13 04:00 | 27.21 | 26.35
2019-07-13 04:30 | 27.56 | 26.71
2019-07-13 05:00 | 28.12 | 27.28
2019-07-13 05:30 | 29.63 | 28.83
2019-07-13 06:00 | 31.34 | 30.58
2019-07-13 06:30 | 33.07 | 32.36
2019-07-13 07:00 | 34.12 | 33.44
2019-07-13 07:30 | 36.29 | 35.64
2019-07-13 08:00 | 37.24 | 36.61
2019-07-13 08:30 | 37.27 | 36.62
2019-07-13 09:00 | 37.29 | 36.62
2019-07-13 09:30 | 35.71 | 34.99
2019-07-13 10:00 | 33.93 | 33.17
2019-07-13 10:30 | 32.54 | 31.74
2019-07-13 11:00 | 31.96 | 31.14
2019-07-13 11:30 | 31.3 | 30.44
2019-07-13 12:00 | 31.31 | 30.46
2019-07-13 12:30 | 29.98 | 29.1
2019-07-13 13:00 | 28.74 | 27.81
2019-07-13 13:30 | 28.85 | 27.93
2019-07-13 14:00 | 30.24 | 29.37
2019-07-13 14:30 | 29.89 | 29.01
2019-07-13 15:00 | 31 | 30.17
2019-07-13 15:30 | 31.96 | 31.15
2019-07-13 16:00 | 33.36 | 32.6
2019-07-13 16:30 | 35.1 | 34.39
2019-07-13 17:00 | 37.64 | 36.98
2019-07-13 17:30 | 40.22 | 39.61
2019-07-13 18:00 | 43.37 | 42.78
2019-07-13 18:30 | 45.59 | 45.03
2019-07-13 19:00 | 44.1 | 43.54
2019-07-13 19:30 | 42.35 | 41.77
2019-07-13 20:00 | 41.63 | 41.03
2019-07-13 20:30 | 39.81 | 39.2
2019-07-13 21:00 | 38.86 | 38.26
2019-07-13 21:30 | 37.5 | 36.88
2019-07-13 22:00 | 36.14 | 35.5
2019-07-13 22:30 | 34.22 | 33.56
2019-07-13 23:00 | 33.09 | 32.4
2019-07-13 23:30 | 31.51 | 30.79
2019-07-14 | 29.83 | 29.07
2019-07-14 00:30 | 29.15 | 28.39
2019-07-14 01:00 | 28.42 | 27.63
2019-07-14 01:30 | 28.08 | 27.28
2019-07-14 02:00 | 27.14 | 26.32
2019-07-14 02:30 | 27.08 | 26.25
2019-07-14 03:00 | 26.56 | 25.71
2019-07-14 03:30 | 26.29 | 25.43
2019-07-14 04:00 | 26.2 | 25.35
2019-07-14 04:30 | 26.8 | 25.96
2019-07-14 05:00 | 27 | 26.17
2019-07-14 05:30 | 27.29 | 26.47
2019-07-14 06:00 | 28.95 | 28.17
2019-07-14 06:30 | 29.88 | 29.13
2019-07-14 07:00 | 30.51 | 29.78
2019-07-14 07:30 | 31.34 | 30.63
2019-07-14 08:00 | 32.27 | 31.55
2019-07-14 08:30 | 31.87 | 31.14
2019-07-14 09:00 | 31.37 | 30.62
2019-07-14 09:30 | 31.14 | 30.38
2019-07-14 10:00 | 29.69 | 28.88
2019-07-14 10:30 | 28.7 | 27.85
2019-07-14 11:00 | 28.68 | 27.82
2019-07-14 11:30 | 26.98 | 26.06
2019-07-14 12:00 | 25.83 | 24.86
2019-07-14 12:30 | 26.63 | 25.69
2019-07-14 13:00 | 25.54 | 24.56
2019-07-14 13:30 | 26.27 | 25.31
2019-07-14 14:00 | 26.22 | 25.26
2019-07-14 14:30 | 26.44 | 25.5
2019-07-14 15:00 | 27.54 | 26.64
2019-07-14 15:30 | 29.32 | 28.49
2019-07-14 16:00 | 31.74 | 30.97
2019-07-14 16:30 | 34.47 | 33.76
2019-07-14 17:00 | 37.7 | 37.07
2019-07-14 17:30 | 40.51 | 39.93
2019-07-14 18:00 | 44.91 | 44.38
2019-07-14 18:30 | 48.27 | 47.78
2019-07-14 19:00 | 48.05 | 47.56
2019-07-14 19:30 | 45.91 | 45.4
2019-07-14 20:00 | 43.76 | 43.22
2019-07-14 20:30 | 42.54 | 41.99
2019-07-14 21:00 | 41.27 | 40.71
2019-07-14 21:30 | 39.3 | 38.71
2019-07-14 22:00 | 36.81 | 36.18
2019-07-14 22:30 | 34.41 | 33.75
2019-07-14 23:00 | 32.54 | 31.85
2019-07-14 23:30 | 31.35 | 30.63
2019-07-15 | 29.55 | 28.79
2019-07-15 00:30 | 29 | 28.24
2019-07-15 01:00 | 28.38 | 27.59
2019-07-15 01:30 | 27.97 | 27.17
2019-07-15 02:00 | 27.65 | 26.85
2019-07-15 02:30 | 27.53 | 26.72
2019-07-15 03:00 | 27.44 | 26.63
2019-07-15 03:30 | 27.39 | 26.58
2019-07-15 04:00 | 27.68 | 26.88
2019-07-15 04:30 | 29.04 | 28.28
2019-07-15 05:00 | 30.71 | 29.98
2019-07-15 05:30 | 33.72 | 33.05
2019-07-15 06:00 | 36.96 | 36.33
2019-07-15 06:30 | 43.44 | 42.88
2019-07-15 07:00 | 49.14 | 48.62
2019-07-15 07:30 | 54.5 | 54.01
2019-07-15 08:00 | 49.8 | 49.3
2019-07-15 08:30 | 38.08 | 37.43
2019-07-15 09:00 | 39.55 | 38.91
2019-07-15 09:30 | 44.7 | 44.12
2019-07-15 10:00 | 42.26 | 41.63
2019-07-15 10:30 | 40.68 | 40.02
2019-07-15 11:00 | 40.98 | 40.32
2019-07-15 11:30 | 40.81 | 40.12
2019-07-15 12:00 | 38.72 | 38
2019-07-15 12:30 | 38.71 | 38
2019-07-15 13:00 | 37.88 | 37.15
2019-07-15 13:30 | 38.24 | 37.5
2019-07-15 14:00 | 39.11 | 38.4
2019-07-15 14:30 | 40.53 | 39.84
2019-07-15 15:00 | 41.49 | 40.83
2019-07-15 15:30 | 42.28 | 41.72
2019-07-15 16:00 | 44.58 | 44.16
2019-07-15 16:30 | 45.22 | 44.79
2019-07-15 17:00 | 46.94 | 46.52
2019-07-15 17:30 | 49.46 | 49.04
2019-07-15 18:00 | 52.59 | 52.19
2019-07-15 18:30 | 55.17 | 54.79
2019-07-15 19:00 | 55.12 | 54.74
2019-07-15 19:30 | 53.36 | 52.96
2019-07-15 20:00 | 52 | 51.58
2019-07-15 20:30 | 49.36 | 48.9
2019-07-15 21:00 | 46.97 | 46.47
2019-07-15 21:30 | 44.71 | 44.18
2019-07-15 22:00 | 42 | 41.42
2019-07-15 22:30 | 38.45 | 37.81
2019-07-15 23:00 | 37.11 | 36.43
2019-07-15 23:30 | 34.93 | 34.2
2019-07-16 | 33.09 | 32.34
2019-07-16 00:30 | 31.96 | 31.23
2019-07-16 01:00 | 31.11 | 30.36
2019-07-16 01:30 | 30.6 | 29.84
2019-07-16 02:00 | 30.26 | 29.49
2019-07-16 02:30 | 29.43 | 28.62
2019-07-16 03:00 | 29.24 | 28.43
2019-07-16 03:30 | 29.43 | 28.64
2019-07-16 04:00 | 29.61 | 28.82
2019-07-16 04:30 | 30.94 | 30.2
2019-07-16 05:00 | 32.54 | 31.84
2019-07-16 05:30 | 35.03 | 34.4
2019-07-16 06:00 | 37.88 | 37.32
2019-07-16 06:30 | 43.11 | 42.65
2019-07-16 07:00 | 48.62 | 48.23
2019-07-16 07:30 | 53.71 | 53.35
2019-07-16 08:00 | 53.88 | 53.54
2019-07-16 08:30 | 51.64 | 51.28
2019-07-16 09:00 | 49.15 | 48.66
2019-07-16 09:30 | 46.4 | 45.9
2019-07-16 10:00 | 44.48 | 43.92
2019-07-16 10:30 | 42.52 | 41.91
2019-07-16 11:00 | 41.42 | 40.72
2019-07-16 11:30 | 40.9 | 40.11
2019-07-16 12:00 | 40.4 | 39.6
2019-07-16 12:30 | 39.72 | 38.98
2019-07-16 13:00 | 39.48 | 38.77
2019-07-16 13:30 | 39.5 | 38.8
2019-07-16 14:00 | 40 | 39.29
2019-07-16 14:30 | 40.7 | 39.97
2019-07-16 15:00 | 40.93 | 40.26
2019-07-16 15:30 | 42.38 | 41.76
2019-07-16 16:00 | 43.58 | 43.1
2019-07-16 16:30 | 45.66 | 45.23
2019-07-16 17:00 | 47.52 | 47.09
2019-07-16 17:30 | 49.67 | 49.24
2019-07-16 18:00 | 53.16 | 52.76
2019-07-16 18:30 | 55.92 | 55.54
2019-07-16 19:00 | 56.03 | 55.65
2019-07-16 19:30 | 54.28 | 53.89
2019-07-16 20:00 | 52.29 | 51.87
2019-07-16 20:30 | 50.32 | 49.87
2019-07-16 21:00 | 47.57 | 47.08
2019-07-16 21:30 | 45.51 | 45
2019-07-16 22:00 | 42.97 | 42.41
2019-07-16 22:30 | 39.39 | 38.77
2019-07-16 23:00 | 37.72 | 37.05
2019-07-16 23:30 | 35.36 | 34.65
2019-07-17 | 33.43 | 32.67
2019-07-17 00:30 | 32.83 | 32.04
2019-07-17 01:00 | 31.72 | 30.9
2019-07-17 01:30 | 31.23 | 30.4
2019-07-17 02:00 | 30.91 | 30.06
2019-07-17 02:30 | 30.13 | 29.29
2019-07-17 03:00 | 29.9 | 29.12
2019-07-17 03:30 | 29.78 | 29
2019-07-17 04:00 | 30.37 | 29.61
2019-07-17 04:30 | 31.65 | 30.93
2019-07-17 05:00 | 33.09 | 32.41
2019-07-17 05:30 | 36.18 | 35.58
2019-07-17 06:00 | 39.87 | 39.35
2019-07-17 06:30 | 45.58 | 45.16
2019-07-17 07:00 | 51.13 | 50.44
2019-07-17 07:30 | 59.82 | 56.36
2019-07-17 08:00 | 59.82 | 56.42
2019-07-17 08:30 | 56.79 | 53.21
2019-07-17 09:00 | 53.87 | 50
2019-07-17 09:30 | 50.88 | 46.69
2019-07-17 10:00 | 48.17 | 43.74
2019-07-17 10:30 | 47.14 | 42.64
2019-07-17 11:00 | 46.15 | 41.57
2019-07-17 11:30 | 45.44 | 40.78
2019-07-17 12:00 | 45.44 | 40.79
2019-07-17 12:30 | 44.05 | 39.22
2019-07-17 13:00 | 43.81 | 38.95
2019-07-17 13:30 | 44.12 | 39.3
2019-07-17 14:00 | 44.63 | 39.88
2019-07-17 14:30 | 44.88 | 40.14
2019-07-17 15:00 | 46.05 | 41.43
2019-07-17 15:30 | 47.42 | 42.93
2019-07-17 16:00 | 48.69 | 44.27
2019-07-17 16:30 | 50.1 | 45.75
2019-07-17 17:00 | 51.64 | 47.36
2019-07-17 17:30 | 53.22 | 49.02
2019-07-17 18:00 | 55.95 | 51.99
2019-07-17 18:30 | 58.01 | 54.24
2019-07-17 19:00 | 58.05 | 54.28
2019-07-17 19:30 | 56.27 | 52.33
2019-07-17 20:00 | 54.51 | 50.38
2019-07-17 20:30 | 52.91 | 48.58
2019-07-17 21:00 | 51.73 | 47.27
2019-07-17 21:30 | 48.08 | 44.91
2019-07-17 22:00 | 41.81 | 41.22
2019-07-17 22:30 | 38.57 | 37.93
2019-07-17 23:00 | 37.18 | 36.5
2019-07-17 23:30 | 34.59 | 33.85
2019-07-18 | 32.87 | 32.08
2019-07-18 00:30 | 32.27 | 31.52
2019-07-18 01:00 | 30.85 | 30.09
2019-07-18 01:30 | 30.22 | 29.45
2019-07-18 02:00 | 29.84 | 29.07
2019-07-18 02:30 | 29.41 | 28.6
2019-07-18 03:00 | 28.86 | 28.04
2019-07-18 03:30 | 28.97 | 28.15
2019-07-18 04:00 | 29.05 | 28.23
2019-07-18 04:30 | 31.15 | 30.39
2019-07-18 05:00 | 32.47 | 31.75
2019-07-18 05:30 | 35.44 | 34.81
2019-07-18 06:00 | 38.68 | 38.12
2019-07-18 06:30 | 43.89 | 43.43
2019-07-18 07:00 | 49.94 | 49.55
2019-07-18 07:30 | 55.18 | 54.82
2019-07-18 08:00 | 55.15 | 54.81
2019-07-18 08:30 | 52.23 | 51.86
2019-07-18 09:00 | 48.79 | 48.34
2019-07-18 09:30 | 45.57 | 45.14
2019-07-18 10:00 | 42.91 | 42.42
2019-07-18 10:30 | 41.59 | 41.02
2019-07-18 11:00 | 40.69 | 40
2019-07-18 11:30 | 39.9 | 39.11
2019-07-18 12:00 | 39.43 | 38.61
2019-07-18 12:30 | 38.49 | 37.72
2019-07-18 13:00 | 38.07 | 37.3
2019-07-18 13:30 | 39.06 | 38.24
2019-07-18 14:00 | 40.24 | 39.45
2019-07-18 14:30 | 41.01 | 40.17
2019-07-18 15:00 | 40.71 | 39.98
2019-07-18 15:30 | 41.64 | 41.04
2019-07-18 16:00 | 43.8 | 43.33
2019-07-18 16:30 | 45.37 | 44.95
2019-07-18 17:00 | 47.07 | 46.66
2019-07-18 17:30 | 48.9 | 48.49
2019-07-18 18:00 | 52.33 | 51.94
2019-07-18 18:30 | 55.47 | 55.11
2019-07-18 19:00 | 55.87 | 55.51
2019-07-18 19:30 | 54.33 | 53.96
2019-07-18 20:00 | 52.58 | 52.19
2019-07-18 20:30 | 50.21 | 49.79
2019-07-18 21:00 | 48.62 | 48.17
2019-07-18 21:30 | 46.38 | 45.89
2019-07-18 22:00 | 43.29 | 42.76
2019-07-18 22:30 | 39.48 | 38.87
2019-07-18 23:00 | 38.13 | 37.49
2019-07-18 23:30 | 35.99 | 35.3
2019-07-19 | 34.06 | 33.32
2019-07-19 00:30 | 33.22 | 32.45
2019-07-19 01:00 | 31.99 | 31.2
2019-07-19 01:30 | 30.93 | 30.2
2019-07-19 02:00 | 30.5 | 29.75
2019-07-19 02:30 | 30.06 | 29.29
2019-07-19 03:00 | 29.79 | 29.01
2019-07-19 03:30 | 29.72 | 28.94
2019-07-19 04:00 | 29.96 | 29.18
2019-07-19 04:30 | 31.17 | 30.42
2019-07-19 05:00 | 33.13 | 32.45
2019-07-19 05:30 | 35.87 | 35.25
2019-07-19 06:00 | 39.44 | 38.9
2019-07-19 06:30 | 44.46 | 44.02
2019-07-19 07:00 | 50.1 | 49.71
2019-07-19 07:30 | 55.36 | 55.01
2019-07-19 08:00 | 55.36 | 55.02
2019-07-19 08:30 | 52.31 | 51.96
2019-07-19 09:00 | 48.36 | 47.98
2019-07-19 09:30 | 45.55 | 45.14
2019-07-19 10:00 | 42.91 | 42.48
2019-07-19 10:30 | 40.84 | 40.39
2019-07-19 11:00 | 39.56 | 39.04
2019-07-19 11:30 | 38.42 | 37.85
2019-07-19 12:00 | 37.64 | 37.04
2019-07-19 12:30 | 37.04 | 36.5
2019-07-19 13:00 | 37.72 | 37.21
2019-07-19 13:30 | 37.02 | 36.5
2019-07-19 14:00 | 36.89 | 36.39
2019-07-19 14:30 | 37.37 | 36.88
2019-07-19 15:00 | 38.54 | 38.05
2019-07-19 15:30 | 38.84 | 38.34
2019-07-19 16:00 | 40.9 | 40.42
2019-07-19 16:30 | 42.74 | 42.26
2019-07-19 17:00 | 44.64 | 44.18
2019-07-19 17:30 | 47.03 | 46.57
2019-07-19 18:00 | 50.16 | 49.74
2019-07-19 18:30 | 53.38 | 52.99
2019-07-19 19:00 | 52.63 | 52.23
2019-07-19 19:30 | 50.07 | 49.64
2019-07-19 20:00 | 47.69 | 47.23
2019-07-19 20:30 | 46.12 | 45.63
2019-07-19 21:00 | 44.97 | 44.47
2019-07-19 21:30 | 43.01 | 42.47
2019-07-19 22:00 | 40.85 | 40.32
2019-07-19 22:30 | 37.56 | 36.99
2019-07-19 23:00 | 37.18 | 36.59
2019-07-19 23:30 | 34.78 | 34.14
2019-07-20 | 32.72 | 32.03
2019-07-20 00:30 | 32.06 | 31.35
2019-07-20 01:00 | 30.97 | 30.23
2019-07-20 01:30 | 30.14 | 29.36
2019-07-20 02:00 | 29.42 | 28.61
2019-07-20 02:30 | 28.78 | 27.95
2019-07-20 03:00 | 28.53 | 27.69
2019-07-20 03:30 | 28.57 | 27.72
2019-07-20 04:00 | 28.9 | 28.07
2019-07-20 04:30 | 29.42 | 28.61
2019-07-20 05:00 | 29.88 | 29.09
2019-07-20 05:30 | 31.44 | 30.7
2019-07-20 06:00 | 33.02 | 32.32
2019-07-20 06:30 | 35.09 | 34.45
2019-07-20 07:00 | 36.79 | 36.18
2019-07-20 07:30 | 39.01 | 38.46
2019-07-20 08:00 | 39.93 | 39.4
2019-07-20 08:30 | 39.7 | 39.18
2019-07-20 09:00 | 38.84 | 38.31
2019-07-20 09:30 | 36.54 | 35.99
2019-07-20 10:00 | 34.45 | 33.86
2019-07-20 10:30 | 34.1 | 33.51
2019-07-20 11:00 | 31.73 | 31.11
2019-07-20 11:30 | 30.88 | 30.24
2019-07-20 12:00 | 29.64 | 28.96
2019-07-20 12:30 | 28.9 | 28.2
2019-07-20 13:00 | 30.25 | 29.58
2019-07-20 13:30 | 29.61 | 28.93
2019-07-20 14:00 | 29.19 | 28.48
2019-07-20 14:30 | 28.9 | 28.19
2019-07-20 15:00 | 30.21 | 29.53
2019-07-20 15:30 | 33.75 | 33.13
2019-07-20 16:00 | 33.46 | 32.83
2019-07-20 16:30 | 34.59 | 33.97
2019-07-20 17:00 | 37.98 | 37.41
2019-07-20 17:30 | 40.79 | 40.27
2019-07-20 18:00 | 43.52 | 43.04
2019-07-20 18:30 | 45.03 | 44.58
2019-07-20 19:00 | 45.06 | 44.6
2019-07-20 19:30 | 43.06 | 42.57
2019-07-20 20:00 | 42.17 | 41.67
2019-07-20 20:30 | 39.8 | 39.26
2019-07-20 21:00 | 38.52 | 37.95
2019-07-20 21:30 | 37.74 | 37.16
2019-07-20 22:00 | 36.28 | 35.67
2019-07-20 22:30 | 35.12 | 34.48
2019-07-20 23:00 | 33.02 | 32.32
2019-07-20 23:30 | 31.68 | 30.94
2019-07-21 | 30.35 | 29.57
2019-07-21 00:30 | 29.52 | 28.72
2019-07-21 01:00 | 28.73 | 27.9
2019-07-21 01:30 | 28 | 27.14
2019-07-21 02:00 | 27.38 | 26.51
2019-07-21 02:30 | 27.13 | 26.24
2019-07-21 03:00 | 27.08 | 26.18
2019-07-21 03:30 | 26.54 | 25.61
2019-07-21 04:00 | 26.55 | 25.62
2019-07-21 04:30 | 26.97 | 26.07
2019-07-21 05:00 | 27.27 | 26.37
2019-07-21 05:30 | 27.66 | 26.78
2019-07-21 06:00 | 28.72 | 27.88
2019-07-21 06:30 | 29.66 | 28.85
2019-07-21 07:00 | 30.09 | 29.29
2019-07-21 07:30 | 31.24 | 30.48
2019-07-21 08:00 | 32.54 | 31.82
2019-07-21 08:30 | 33 | 32.31
2019-07-21 09:00 | 33.02 | 32.34
2019-07-21 09:30 | 34.42 | 33.77
2019-07-21 10:00 | 32.28 | 31.6
2019-07-21 10:30 | 30.81 | 30.11
2019-07-21 11:00 | 30.53 | 29.83
2019-07-21 11:30 | 29.23 | 28.51
2019-07-21 12:00 | 28.85 | 28.13
2019-07-21 12:30 | 28.69 | 27.95
2019-07-21 13:00 | 27.96 | 27.21
2019-07-21 13:30 | 28.01 | 27.25
2019-07-21 14:00 | 28.65 | 27.92
2019-07-21 14:30 | 29.17 | 28.44
2019-07-21 15:00 | 31.23 | 30.54
2019-07-21 15:30 | 33.85 | 33.21
2019-07-21 16:00 | 33.69 | 33.05
2019-07-21 16:30 | 36.06 | 35.46
2019-07-21 17:00 | 38.62 | 38.06
2019-07-21 17:30 | 42.25 | 41.75
2019-07-21 18:00 | 45.9 | 45.45
2019-07-21 18:30 | 47.55 | 47.12
2019-07-21 19:00 | 46.26 | 45.82
2019-07-21 19:30 | 44.67 | 44.21
2019-07-21 20:00 | 42.78 | 42.28
2019-07-21 20:30 | 41.1 | 40.58
2019-07-21 21:00 | 39.35 | 38.8
2019-07-21 21:30 | 38.14 | 37.56
2019-07-21 22:00 | 36.05 | 35.42
2019-07-21 22:30 | 33.69 | 33.01
2019-07-21 23:00 | 31.84 | 31.11
2019-07-21 23:30 | 30.08 | 29.29
2019-07-22 | 28.53 | 27.68
2019-07-22 00:30 | 27.67 | 26.79
2019-07-22 01:00 | 26.91 | 26
2019-07-22 01:30 | 26.79 | 25.88
2019-07-22 02:00 | 26.43 | 25.51
2019-07-22 02:30 | 26.68 | 25.76
2019-07-22 03:00 | 26.11 | 25.17
2019-07-22 03:30 | 26.01 | 25.07
2019-07-22 04:00 | 26.33 | 25.4
2019-07-22 04:30 | 27.19 | 26.3
2019-07-22 05:00 | 28.56 | 27.73
2019-07-22 05:30 | 30.71 | 29.95
2019-07-22 06:00 | 34.2 | 33.55
2019-07-22 06:30 | 38.46 | 37.92
2019-07-22 07:00 | 42.94 | 42.49
2019-07-22 07:30 | 48.1 | 47.68
2019-07-22 08:00 | 49.87 | 49.49
2019-07-22 08:30 | 48.04 | 47.64
2019-07-22 09:00 | 47.98 | 47.51
2019-07-22 09:30 | 46.75 | 46.25
2019-07-22 10:00 | 48.29 | 47.73
2019-07-22 10:30 | 48.7 | 48.05
2019-07-22 11:00 | 48.09 | 47.23
2019-07-22 11:30 | 45.66 | 44.67
2019-07-22 12:00 | 45.67 | 45.22
2019-07-22 12:30 | 45.79 | 45.38
2019-07-22 13:00 | 47.29 | 46.89
2019-07-22 13:30 | 46.02 | 45.61
2019-07-22 14:00 | 45.84 | 45.43
2019-07-22 14:30 | 47.2 | 46.8
2019-07-22 15:00 | 46.32 | 45.9
2019-07-22 15:30 | 46.41 | 45.99
2019-07-22 16:00 | 48.04 | 47.6
2019-07-22 16:30 | 48.61 | 48.16
2019-07-22 17:00 | 50.12 | 49.67
2019-07-22 17:30 | 50.83 | 50.36
2019-07-22 18:00 | 53.13 | 52.67
2019-07-22 18:30 | 53.46 | 53.01
2019-07-22 19:00 | 52.78 | 52.31
2019-07-22 19:30 | 50.43 | 49.94
2019-07-22 20:00 | 48.42 | 47.89
2019-07-22 20:30 | 45.62 | 45.04
2019-07-22 21:00 | 43.21 | 42.64
2019-07-22 21:30 | 41.22 | 40.71
2019-07-22 22:00 | 39.06 | 38.51
2019-07-22 22:30 | 35.94 | 35.33
2019-07-22 23:00 | 34.11 | 33.46
2019-07-22 23:30 | 31.96 | 31.26
2019-07-23 | 30.62 | 29.88
2019-07-23 00:30 | 29.97 | 29.19
2019-07-23 01:00 | 29.01 | 28.21
2019-07-23 01:30 | 28.28 | 27.45
2019-07-23 02:00 | 27.68 | 26.84
2019-07-23 02:30 | 27.78 | 26.93
2019-07-23 03:00 | 27.6 | 26.74
2019-07-23 03:30 | 27.6 | 26.73
2019-07-23 04:00 | 27.36 | 26.48
2019-07-23 04:30 | 28.75 | 27.93
2019-07-23 05:00 | 30.32 | 29.54
2019-07-23 05:30 | 33.18 | 32.49
2019-07-23 06:00 | 35.25 | 34.62
2019-07-23 06:30 | 40.28 | 39.77
2019-07-23 07:00 | 43.94 | 43.5
2019-07-23 07:30 | 49.43 | 49.01
2019-07-23 08:00 | 49.89 | 49.51
2019-07-23 08:30 | 49.21 | 48.81
2019-07-23 09:00 | 48.81 | 48.36
2019-07-23 09:30 | 47.75 | 47.24
2019-07-23 10:00 | 44.17 | 43.52
2019-07-23 10:30 | 42.7 | 41.88
2019-07-23 11:00 | 42.79 | 41.76
2019-07-23 11:30 | 42.63 | 41.53
2019-07-23 12:00 | 42.5 | 41.31
2019-07-23 12:30 | 41.32 | 40.7
2019-07-23 13:00 | 40.77 | 40.3
2019-07-23 13:30 | 42.19 | 41.74
2019-07-23 14:00 | 42.25 | 41.8
2019-07-23 14:30 | 43.53 | 43.11
2019-07-23 15:00 | 44.46 | 44.04
2019-07-23 15:30 | 45.77 | 45.36
2019-07-23 16:00 | 46.74 | 46.32
2019-07-23 16:30 | 47.97 | 47.54
2019-07-23 17:00 | 49.28 | 48.84
2019-07-23 17:30 | 50.19 | 49.73
2019-07-23 18:00 | 52.21 | 51.77
2019-07-23 18:30 | 54.11 | 53.68
2019-07-23 19:00 | 53.27 | 52.82
2019-07-23 19:30 | 51.01 | 50.53
2019-07-23 20:00 | 49.03 | 48.52
2019-07-23 20:30 | 46.5 | 45.94
2019-07-23 21:00 | 43.89 | 43.37
2019-07-23 21:30 | 41.63 | 41.14
2019-07-23 22:00 | 40.51 | 40
2019-07-23 22:30 | 37.46 | 36.89
2019-07-23 23:00 | 35.87 | 35.26
2019-07-23 23:30 | 33.09 | 32.42
2019-07-24 | 31.48 | 30.77
2019-07-24 00:30 | 30.92 | 30.18
2019-07-24 01:00 | 29.53 | 28.75
2019-07-24 01:30 | 29.17 | 28.37
2019-07-24 02:00 | 28.84 | 28.04
2019-07-24 02:30 | 28.3 | 27.48
2019-07-24 03:00 | 28.34 | 27.5
2019-07-24 03:30 | 27.24 | 26.37
2019-07-24 04:00 | 28.71 | 27.89
2019-07-24 04:30 | 29.16 | 28.36
2019-07-24 05:00 | 30.84 | 30.1
2019-07-24 05:30 | 33.25 | 32.58
2019-07-24 06:00 | 36.06 | 35.46
2019-07-24 06:30 | 41.03 | 40.55
2019-07-24 07:00 | 45.22 | 44.8
2019-07-24 07:30 | 50.85 | 50.44
2019-07-24 08:00 | 54.92 | 54.45
2019-07-24 08:30 | 52.22 | 51.74
2019-07-24 09:00 | 48.52 | 48.06
2019-07-24 09:30 | 45.05 | 44.54
2019-07-24 10:00 | 43.67 | 43.12
2019-07-24 10:30 | 43.11 | 42.37
2019-07-24 11:00 | 43.08 | 42.14
2019-07-24 11:30 | 43.01 | 41.88
2019-07-24 12:00 | 42.39 | 41.23
2019-07-24 12:30 | 41.85 | 40.95
2019-07-24 13:00 | 41.03 | 40.56
2019-07-24 13:30 | 41.94 | 41.49
2019-07-24 14:00 | 42.81 | 42.37
2019-07-24 14:30 | 42.66 | 42.21
2019-07-24 15:00 | 44.33 | 43.9
2019-07-24 15:30 | 45.39 | 44.96
2019-07-24 16:00 | 47.47 | 47.04
2019-07-24 16:30 | 47.84 | 47.38
2019-07-24 17:00 | 48.2 | 47.73
2019-07-24 17:30 | 52.17 | 51.67
2019-07-24 18:00 | 52.31 | 51.83
2019-07-24 18:30 | 53.49 | 53.04
2019-07-24 19:00 | 53.1 | 52.65
2019-07-24 19:30 | 50.6 | 50.1
2019-07-24 20:00 | 48.26 | 47.76
2019-07-24 20:30 | 46.07 | 45.58
2019-07-24 21:00 | 43.95 | 43.44
2019-07-24 21:30 | 41.76 | 41.26
2019-07-24 22:00 | 40 | 39.47
2019-07-24 22:30 | 36.52 | 35.91
2019-07-24 23:00 | 35.32 | 34.69
2019-07-24 23:30 | 33.12 | 32.44
2019-07-25 | 31.56 | 30.84
2019-07-25 00:30 | 30.69 | 29.94
2019-07-25 01:00 | 29.33 | 28.53
2019-07-25 01:30 | 28.87 | 28.07
2019-07-25 02:00 | 29.01 | 28.21
2019-07-25 02:30 | 27.78 | 26.93
2019-07-25 03:00 | 28.22 | 27.38
2019-07-25 03:30 | 28.28 | 27.44
2019-07-25 04:00 | 28.73 | 27.9
2019-07-25 04:30 | 29.25 | 28.43
2019-07-25 05:00 | 30.88 | 30.12
2019-07-25 05:30 | 34.28 | 33.61
2019-07-25 06:00 | 37.09 | 36.5
2019-07-25 06:30 | 42.72 | 42.24
2019-07-25 07:00 | 46.46 | 46.05
2019-07-25 07:30 | 51.54 | 51.15
2019-07-25 08:00 | 51.39 | 51.02
2019-07-25 08:30 | 48.99 | 48.61
2019-07-25 09:00 | 46.63 | 46.19
2019-07-25 09:30 | 44.12 | 43.61
2019-07-25 10:00 | 42.43 | 41.81
2019-07-25 10:30 | 42.15 | 41.38
2019-07-25 11:00 | 41.91 | 40.98
2019-07-25 11:30 | 41.65 | 40.57
2019-07-25 12:00 | 41.38 | 40.21
2019-07-25 12:30 | 40.77 | 39.93
2019-07-25 13:00 | 40.14 | 39.66
2019-07-25 13:30 | 40.64 | 40.18
2019-07-25 14:00 | 41.73 | 41.28
2019-07-25 14:30 | 42.81 | 42.37
2019-07-25 15:00 | 43.18 | 42.74
2019-07-25 15:30 | 44.46 | 44.03
2019-07-25 16:00 | 46.07 | 45.64
2019-07-25 16:30 | 46.92 | 46.47
2019-07-25 17:00 | 48 | 47.54
2019-07-25 17:30 | 49.1 | 48.63
2019-07-25 18:00 | 51.85 | 51.39
2019-07-25 18:30 | 53.47 | 53.03
2019-07-25 19:00 | 52.91 | 52.5
2019-07-25 19:30 | 50.97 | 50.55
2019-07-25 20:00 | 49.61 | 49.17
2019-07-25 20:30 | 47.3 | 46.83
2019-07-25 21:00 | 45.87 | 45.37
2019-07-25 21:30 | 43.46 | 42.92
2019-07-25 22:00 | 40.41 | 39.88
2019-07-25 22:30 | 37.27 | 36.69
2019-07-25 23:00 | 36.23 | 35.62
2019-07-25 23:30 | 33.96 | 33.31
2019-07-26 | 31.73 | 31.01
2019-07-26 00:30 | 31.56 | 30.84
2019-07-26 01:00 | 30.22 | 29.45
2019-07-26 01:30 | 29.6 | 28.82
2019-07-26 02:00 | 28.68 | 27.87
2019-07-26 02:30 | 28.59 | 27.76
2019-07-26 03:00 | 27.94 | 27.08
2019-07-26 03:30 | 28.07 | 27.22
2019-07-26 04:00 | 28.48 | 27.64
2019-07-26 04:30 | 29.03 | 28.2
2019-07-26 05:00 | 30.18 | 29.4
2019-07-26 05:30 | 33.45 | 32.78
2019-07-26 06:00 | 36.42 | 35.82
2019-07-26 06:30 | 41.53 | 41.04
2019-07-26 07:00 | 45.77 | 45.36
2019-07-26 07:30 | 50.71 | 50.31
2019-07-26 08:00 | 50.52 | 50.14
2019-07-26 08:30 | 48.84 | 48.45
2019-07-26 09:00 | 46.13 | 45.68
2019-07-26 09:30 | 44.16 | 43.67
2019-07-26 10:00 | 42.68 | 42.11
2019-07-26 10:30 | 42.04 | 41.43
2019-07-26 11:00 | 42.32 | 41.54
2019-07-26 11:30 | 41.72 | 40.82
2019-07-26 12:00 | 40.99 | 39.97
2019-07-26 12:30 | 41.05 | 40.12
2019-07-26 13:00 | 41.18 | 40.27
2019-07-26 13:30 | 38.68 | 37.75
2019-07-26 14:00 | 29.67 | 28.21
2019-07-26 14:30 | 40.6 | 39.85
2019-07-26 15:00 | 40.39 | 39.74
2019-07-26 15:30 | 41.12 | 40.62
2019-07-26 16:00 | 42.61 | 42.17
2019-07-26 16:30 | 44.3 | 43.86
2019-07-26 17:00 | 45.86 | 45.42
2019-07-26 17:30 | 47.02 | 46.57
2019-07-26 18:00 | 48.79 | 48.36
2019-07-26 18:30 | 50.09 | 49.66
2019-07-26 19:00 | 49.4 | 48.97
2019-07-26 19:30 | 47.24 | 46.77
2019-07-26 20:00 | 45.57 | 45.08
2019-07-26 20:30 | 43.31 | 42.78
2019-07-26 21:00 | 42.21 | 41.65
2019-07-26 21:30 | 41.32 | 40.74
2019-07-26 22:00 | 38.99 | 38.36
2019-07-26 22:30 | 36.42 | 35.73
2019-07-26 23:00 | 36.81 | 36.12
2019-07-26 23:30 | 33.57 | 32.8
2019-07-27 | 31.28 | 30.53
2019-07-27 00:30 | 30.7 | 29.93
2019-07-27 01:00 | 29.29 | 28.48
2019-07-27 01:30 | 28.83 | 28
2019-07-27 02:00 | 28.57 | 27.74
2019-07-27 02:30 | 28 | 27.14
2019-07-27 03:00 | 27.69 | 26.81
2019-07-27 03:30 | 27.07 | 26.18
2019-07-27 04:00 | 27.4 | 26.52
2019-07-27 04:30 | 27.95 | 27.09
2019-07-27 05:00 | 28.38 | 27.54
2019-07-27 05:30 | 30.19 | 29.42
2019-07-27 06:00 | 31.36 | 30.61
2019-07-27 06:30 | 33.59 | 32.92
2019-07-27 07:00 | 35.15 | 34.51
2019-07-27 07:30 | 37.51 | 36.93
2019-07-27 08:00 | 37.73 | 37.16
2019-07-27 08:30 | 37.76 | 37.21
2019-07-27 09:00 | 37.12 | 36.57
2019-07-27 09:30 | 35.99 | 35.43
2019-07-27 10:00 | 35.08 | 34.52
2019-07-27 10:30 | 33.83 | 33.26
2019-07-27 11:00 | 32.64 | 32.05
2019-07-27 11:30 | 31.51 | 30.9
2019-07-27 12:00 | 30.45 | 29.82
2019-07-27 12:30 | 29.79 | 29.13
2019-07-27 13:00 | 29.14 | 28.48
2019-07-27 13:30 | 28.44 | 27.75
2019-07-27 14:00 | 28.92 | 28.23
2019-07-27 14:30 | 29.75 | 29.08
2019-07-27 15:00 | 31.11 | 30.47
2019-07-27 15:30 | 31.77 | 31.14
2019-07-27 16:00 | 33.43 | 32.81
2019-07-27 16:30 | 35.75 | 35.16
2019-07-27 17:00 | 38.45 | 37.91
2019-07-27 17:30 | 41.03 | 40.53
2019-07-27 18:00 | 43.94 | 43.48
2019-07-27 18:30 | 45.14 | 44.7
2019-07-27 19:00 | 44.56 | 44.11
2019-07-27 19:30 | 42.9 | 42.42
2019-07-27 20:00 | 41.88 | 41.39
2019-07-27 20:30 | 39.92 | 39.4
2019-07-27 21:00 | 38.46 | 37.9
2019-07-27 21:30 | 37.28 | 36.7
2019-07-27 22:00 | 36.12 | 35.51
2019-07-27 22:30 | 35.47 | 34.84
2019-07-27 23:00 | 33.54 | 32.86
2019-07-27 23:30 | 31.86 | 31.14
2019-07-28 | 30.66 | 29.9
2019-07-28 00:30 | 29.53 | 28.73
2019-07-28 01:00 | 28.5 | 27.66
2019-07-28 01:30 | 28.08 | 27.23
2019-07-28 02:00 | 28.47 | 27.63
2019-07-28 02:30 | 27.28 | 26.4
2019-07-28 03:00 | 26.71 | 25.8
2019-07-28 03:30 | 26.91 | 26.01
2019-07-28 04:00 | 27.24 | 26.35
2019-07-28 04:30 | 26.82 | 25.91
2019-07-28 05:00 | 27.42 | 26.54
2019-07-28 05:30 | 28.51 | 27.67
2019-07-28 06:00 | 29.16 | 28.34
2019-07-28 06:30 | 30.33 | 29.55
2019-07-28 07:00 | 30.91 | 30.14
2019-07-28 07:30 | 31.89 | 31.16
2019-07-28 08:00 | 32.61 | 31.9
2019-07-28 08:30 | 33.16 | 32.48
2019-07-28 09:00 | 33.51 | 32.82
2019-07-28 09:30 | 32.53 | 31.85
2019-07-28 10:00 | 32.54 | 31.88
2019-07-28 10:30 | 31.92 | 31.26
2019-07-28 11:00 | 30.88 | 30.21
2019-07-28 11:30 | 29.75 | 29.05
2019-07-28 12:00 | 28.96 | 28.25
2019-07-28 12:30 | 28.77 | 28.06
2019-07-28 13:00 | 28.24 | 27.52
2019-07-28 13:30 | 28.64 | 27.93
2019-07-28 14:00 | 28 | 27.28
2019-07-28 14:30 | 28.47 | 27.74
2019-07-28 15:00 | 29.12 | 28.41
2019-07-28 15:30 | 32.09 | 31.44
2019-07-28 16:00 | 34.23 | 33.6
2019-07-28 16:30 | 37.22 | 36.62
2019-07-28 17:00 | 37.74 | 37.17
2019-07-28 17:30 | 41.71 | 41.21
2019-07-28 18:00 | 44.25 | 43.79
2019-07-28 18:30 | 47.06 | 46.63
2019-07-28 19:00 | 46.93 | 46.5
2019-07-28 19:30 | 45.34 | 44.89
2019-07-28 20:00 | 43.57 | 43.09
2019-07-28 20:30 | 41.61 | 41.09
2019-07-28 21:00 | 39.75 | 39.2
2019-07-28 21:30 | 37.64 | 37.04
2019-07-28 22:00 | 36.21 | 35.58
2019-07-28 22:30 | 33.86 | 33.18
2019-07-28 23:00 | 32.8 | 32.09
2019-07-28 23:30 | 30.5 | 29.73
2019-07-29 | 29.22 | 28.4
2019-07-29 00:30 | 28.41 | 27.56
2019-07-29 01:00 | 28.2 | 27.34
2019-07-29 01:30 | 28.25 | 27.39
2019-07-29 02:00 | 27.94 | 27.08
2019-07-29 02:30 | 27.52 | 26.63
2019-07-29 03:00 | 26.96 | 26.05
2019-07-29 03:30 | 27.33 | 26.43
2019-07-29 04:00 | 27.42 | 26.53
2019-07-29 04:30 | 28.43 | 27.57
2019-07-29 05:00 | 29.62 | 28.8
2019-07-29 05:30 | 32.58 | 31.87
2019-07-29 06:00 | 35.49 | 34.86
2019-07-29 06:30 | 40.49 | 39.97
2019-07-29 07:00 | 44.03 | 43.58
2019-07-29 07:30 | 51.05 | 50.64
2019-07-29 08:00 | 50.39 | 50.01
2019-07-29 08:30 | 48.34 | 47.95
2019-07-29 09:00 | 46.41 | 45.95
2019-07-29 09:30 | 44.32 | 43.82
2019-07-29 10:00 | 43.03 | 42.42
2019-07-29 10:30 | 42.77 | 41.99
2019-07-29 11:00 | 42.99 | 41.93
2019-07-29 11:30 | 43.24 | 42.05
2019-07-29 12:00 | 42.74 | 41.48
2019-07-29 12:30 | 42.34 | 41.1
2019-07-29 13:00 | 42.33 | 41.1
2019-07-29 13:30 | 43.64 | 42.43
2019-07-29 14:00 | 43.47 | 42.76
2019-07-29 14:30 | 44.22 | 43.8
2019-07-29 15:00 | 44.72 | 44.3
2019-07-29 15:30 | 45.27 | 44.85
2019-07-29 16:00 | 47.04 | 46.62
2019-07-29 16:30 | 47.51 | 47.06
2019-07-29 17:00 | 49.09 | 48.63
2019-07-29 17:30 | 50.66 | 50.2
2019-07-29 18:00 | 53.26 | 52.8
2019-07-29 18:30 | 55.76 | 55.33
2019-07-29 19:00 | 54.25 | 53.81
2019-07-29 19:30 | 51.94 | 51.47
2019-07-29 20:00 | 49.96 | 49.46
2019-07-29 20:30 | 47.21 | 46.66
2019-07-29 21:00 | 44.69 | 44.16
2019-07-29 21:30 | 43.23 | 42.68
2019-07-29 22:00 | 40.98 | 40.39
2019-07-29 22:30 | 38.32 | 37.66
2019-07-29 23:00 | 36.23 | 35.52
2019-07-29 23:30 | 34.53 | 33.78
2019-07-30 | 33.16 | 32.38
2019-07-30 00:30 | 32.12 | 31.3
2019-07-30 01:00 | 31.2 | 30.36
2019-07-30 01:30 | 31.22 | 30.38
2019-07-30 02:00 | 30.12 | 29.23
2019-07-30 02:30 | 29.93 | 29.02
2019-07-30 03:00 | 28.59 | 28
2019-07-30 03:30 | 29.15 | 28.66
2019-07-30 04:00 | 28.66 | 28.13
2019-07-30 04:30 | 30.1 | 29.67
2019-07-30 05:00 | 31.2 | 30.83
2019-07-30 05:30 | 33.8 | 33.59
2019-07-30 06:00 | 37.44 | 37.34
2019-07-30 06:30 | 42.43 | 42.42
2019-07-30 07:00 | 46.39 | 46.37
2019-07-30 07:30 | 51.26 | 51.13
2019-07-30 08:00 | 51.95 | 51.7
2019-07-30 08:30 | 50.46 | 50.07
2019-07-30 09:00 | 48.06 | 47.53
2019-07-30 09:30 | 46.25 | 45.61
2019-07-30 10:00 | 44.24 | 43.6
2019-07-30 10:30 | 44.52 | 43.73
2019-07-30 11:00 | 45.09 | 44.01
2019-07-30 11:30 | 44.79 | 43.59
2019-07-30 12:00 | 44.76 | 43.07
2019-07-30 12:30 | 44.99 | 43.06
2019-07-30 13:00 | 44.76 | 42.8
2019-07-30 13:30 | 44.44 | 42.46
2019-07-30 14:00 | 44.76 | 42.81
2019-07-30 14:30 | 45.26 | 43.34
2019-07-30 15:00 | 46.17 | 44.27
2019-07-30 15:30 | 47.67 | 45.82
2019-07-30 16:00 | 50.78 | 49.02
2019-07-30 16:30 | 50.93 | 49.12
2019-07-30 17:00 | 51.72 | 49.89
2019-07-30 17:30 | 52.68 | 50.83
2019-07-30 18:00 | 54.68 | 52.89
2019-07-30 18:30 | 56.55 | 54.83
2019-07-30 19:00 | 56.88 | 55.16
2019-07-30 19:30 | 54.65 | 52.83
2019-07-30 20:00 | 52.45 | 50.51
2019-07-30 20:30 | 50.67 | 48.64
2019-07-30 21:00 | 47.43 | 45.38
2019-07-30 21:30 | 45.25 | 43.06
2019-07-30 22:00 | 42.95 | 40.6
2019-07-30 22:30 | 40.54 | 38.01
2019-07-30 23:00 | 36.83 | 36.29
2019-07-30 23:30 | 33.8 | 33.67
2019-07-31 | 32.78 | 32.58
2019-07-31 00:30 | 32.09 | 31.87
2019-07-31 01:00 | 31.55 | 31.3
2019-07-31 01:30 | 30.39 | 30.1
2019-07-31 02:00 | 29.36 | 29.01
2019-07-31 02:30 | 28.91 | 28.52
2019-07-31 03:00 | 29.46 | 29.05
2019-07-31 03:30 | 29.49 | 29.1
2019-07-31 04:00 | 29.78 | 29.36
2019-07-31 04:30 | 30.81 | 30.46
2019-07-31 05:00 | 32.32 | 32.05
2019-07-31 05:30 | 34.38 | 34.21
2019-07-31 06:00 | 37.94 | 37.87
2019-07-31 06:30 | 41.76 | 41.75
2019-07-31 07:00 | 46.31 | 46.28
2019-07-31 07:30 | 51.89 | 51.73
2019-07-31 08:00 | 53.17 | 52.89
2019-07-31 08:30 | 51.22 | 50.76
2019-07-31 09:00 | 48.55 | 47.99
2019-07-31 09:30 | 47.92 | 47.29
2019-07-31 10:00 | 47.18 | 46.5
2019-07-31 10:30 | 46.85 | 45.96
2019-07-31 11:00 | 46.17 | 44.8
2019-07-31 11:30 | 46.66 | 44.81
2019-07-31 12:00 | 46.44 | 44.61
2019-07-31 12:30 | 45.42 | 43.52
2019-07-31 13:00 | 45.12 | 43.18
2019-07-31 13:30 | 45.28 | 43.35
2019-07-31 14:00 | 45.49 | 43.58
2019-07-31 14:30 | 46.3 | 44.43
2019-07-31 15:00 | 47.46 | 45.63
2019-07-31 15:30 | 47.84 | 45.99
2019-07-31 16:00 | 49.4 | 47.58
2019-07-31 16:30 | 49.88 | 48.01
2019-07-31 17:00 | 51.26 | 49.4
2019-07-31 17:30 | 52.24 | 50.35
2019-07-31 18:00 | 54.73 | 52.92
2019-07-31 18:30 | 56.82 | 55.09
2019-07-31 19:00 | 55.89 | 54.13
2019-07-31 19:30 | 53.87 | 52.01
2019-07-31 20:00 | 52.16 | 50.21
2019-07-31 20:30 | 49.86 | 47.79
2019-07-31 21:00 | 47.67 | 45.5
2019-07-31 21:30 | 45.91 | 43.76
2019-07-31 22:00 | 43.28 | 40.94
2019-07-31 22:30 | 40.55 | 38.01
2019-07-31 23:00 | 39.23 | 36.59
2019-07-31 23:30 | 37.15 | 34.32
2019-08-01 | 35.87 | 32.9
2019-08-01 00:30 | 35.28 | 32.26
2019-08-01 01:00 | 33.29 | 31.15
2019-08-01 01:30 | 30.9 | 30.64
2019-08-01 02:00 | 30.62 | 30.32
2019-08-01 02:30 | 29.65 | 29.32
2019-08-01 03:00 | 29.73 | 29.33
2019-08-01 03:30 | 29.62 | 29.22
2019-08-01 04:00 | 29.01 | 28.61
2019-08-01 04:30 | 30.28 | 29.95
2019-08-01 05:00 | 31.97 | 31.69
2019-08-01 05:30 | 33.55 | 33.37
2019-08-01 06:00 | 36.2 | 36.12
2019-08-01 06:30 | 41.24 | 41.23
2019-08-01 07:00 | 45.52 | 45.5
2019-08-01 07:30 | 50.9 | 50.74
2019-08-01 08:00 | 52.13 | 51.84
2019-08-01 08:30 | 51.56 | 51.11
2019-08-01 09:00 | 51.18 | 50.6
2019-08-01 09:30 | 46.99 | 46.32
2019-08-01 10:00 | 45.48 | 44.74
2019-08-01 10:30 | 46.39 | 45.49
2019-08-01 11:00 | 46.64 | 45.59
2019-08-01 11:30 | 46.13 | 45.43
2019-08-01 12:00 | 45.55 | 45.07
2019-08-01 12:30 | 45.07 | 44.6
2019-08-01 13:00 | 43.3 | 42.89
2019-08-01 13:30 | 44.77 | 44.4
2019-08-01 14:00 | 44.88 | 44.51
2019-08-01 14:30 | 45.88 | 45.51
2019-08-01 15:00 | 46.52 | 46.2
2019-08-01 15:30 | 47.54 | 47.29
2019-08-01 16:00 | 48.91 | 48.77
2019-08-01 16:30 | 50.06 | 50.02
2019-08-01 17:00 | 51.12 | 51.11
2019-08-01 17:30 | 50.52 | 50.51
2019-08-01 18:00 | 54.68 | 54.67
2019-08-01 18:30 | 56.83 | 56.82
2019-08-01 19:00 | 57.1 | 57.09
2019-08-01 19:30 | 54.51 | 54.48
2019-08-01 20:00 | 51.82 | 51.75
2019-08-01 20:30 | 49.04 | 48.91
2019-08-01 21:00 | 47.18 | 46.98
2019-08-01 21:30 | 44 | 43.84
2019-08-01 22:00 | 39.99 | 39.95
2019-08-01 22:30 | 37.48 | 37.4
2019-08-01 23:00 | 36.24 | 36.13
2019-08-01 23:30 | 33.93 | 33.78
2019-08-02 | 32.41 | 32.22
2019-08-02 00:30 | 31.71 | 31.48
2019-08-02 01:00 | 30.96 | 30.69
2019-08-02 01:30 | 29.94 | 29.61
2019-08-02 02:00 | 29.77 | 29.4
2019-08-02 02:30 | 29.04 | 28.62
2019-08-02 03:00 | 28.74 | 28.29
2019-08-02 03:30 | 28.51 | 28.04
2019-08-02 04:00 | 28.74 | 28.29
2019-08-02 04:30 | 29.7 | 29.29
2019-08-02 05:00 | 31.24 | 30.93
2019-08-02 05:30 | 33.5 | 33.3
2019-08-02 06:00 | 36.32 | 36.23
2019-08-02 06:30 | 41 | 41
2019-08-02 07:00 | 45.72 | 45.69
2019-08-02 07:30 | 50.63 | 50.49
2019-08-02 08:00 | 51.4 | 51.11
2019-08-02 08:30 | 50.79 | 50.37
2019-08-02 09:00 | 48.49 | 47.95
2019-08-02 09:30 | 47.04 | 46.44
2019-08-02 10:00 | 46.94 | 46.27
2019-08-02 10:30 | 44.57 | 43.78
2019-08-02 11:00 | 44.86 | 43.71
2019-08-02 11:30 | 46.25 | 44.53
2019-08-02 12:00 | 44.59 | 42.8
2019-08-02 12:30 | 43.59 | 41.73
2019-08-02 13:00 | 42.71 | 40.78
2019-08-02 13:30 | 42.82 | 40.9
2019-08-02 14:00 | 43.44 | 41.41
2019-08-02 14:30 | 44.18 | 42.13
2019-08-02 15:00 | 45.38 | 43.37
2019-08-02 15:30 | 46.92 | 44.94
2019-08-02 16:00 | 46.19 | 44.13
2019-08-02 16:30 | 48.31 | 46.31
2019-08-02 17:00 | 49.81 | 47.85
2019-08-02 17:30 | 50.98 | 49.03
2019-08-02 18:00 | 51.97 | 50.03
2019-08-02 18:30 | 53.39 | 51.51
2019-08-02 19:00 | 53.01 | 51.12
2019-08-02 19:30 | 51.22 | 49.24
2019-08-02 20:00 | 49.81 | 47.75
2019-08-02 20:30 | 47.99 | 45.82
2019-08-02 21:00 | 45.87 | 43.55
2019-08-02 21:30 | 44.13 | 42.02
2019-08-02 22:00 | 40.64 | 40.05
2019-08-02 22:30 | 38.71 | 38.07
2019-08-02 23:00 | 37.49 | 36.83
2019-08-02 23:30 | 35.64 | 34.93
2019-08-03 | 34.23 | 33.48
2019-08-03 00:30 | 33.41 | 32.63
2019-08-03 01:00 | 31.84 | 31.02
2019-08-03 01:30 | 30.97 | 30.14
2019-08-03 02:00 | 30.61 | 29.85
2019-08-03 02:30 | 30.77 | 30.01
2019-08-03 03:00 | 30.28 | 29.51
2019-08-03 03:30 | 29.64 | 28.85
2019-08-03 04:00 | 29.35 | 28.55
2019-08-03 04:30 | 29.57 | 28.78
2019-08-03 05:00 | 29.77 | 28.98
2019-08-03 05:30 | 31.09 | 30.35
2019-08-03 06:00 | 32.36 | 31.65
2019-08-03 06:30 | 35.04 | 34.4
2019-08-03 07:00 | 35.63 | 35
2019-08-03 07:30 | 37.82 | 37.24
2019-08-03 08:00 | 39.88 | 39.35
2019-08-03 08:30 | 41.1 | 40.6
2019-08-03 09:00 | 39.81 | 39.31
2019-08-03 09:30 | 41.72 | 41.25
2019-08-03 10:00 | 38.4 | 37.88
2019-08-03 10:30 | 37.07 | 36.55
2019-08-03 11:00 | 36.1 | 35.58
2019-08-03 11:30 | 36.03 | 35.5
2019-08-03 12:00 | 34.04 | 33.49
2019-08-03 12:30 | 33.57 | 33
2019-08-03 13:00 | 32.81 | 32.22
2019-08-03 13:30 | 31.4 | 30.77
2019-08-03 14:00 | 32.05 | 31.43
2019-08-03 14:30 | 31.89 | 31.26
2019-08-03 15:00 | 31.24 | 30.59
2019-08-03 15:30 | 32.71 | 32.08
2019-08-03 16:00 | 34.82 | 34.23
2019-08-03 16:30 | 37.07 | 36.5
2019-08-03 17:00 | 39.61 | 39.08
2019-08-03 17:30 | 42.24 | 41.74
2019-08-03 18:00 | 45.22 | 44.77
2019-08-03 18:30 | 47.1 | 46.67
2019-08-03 19:00 | 46.11 | 45.68
2019-08-03 19:30 | 43.81 | 43.34
2019-08-03 20:00 | 42.87 | 42.38
2019-08-03 20:30 | 41.64 | 41.13
2019-08-03 21:00 | 40.7 | 40.18
2019-08-03 21:30 | 39.29 | 38.75
2019-08-03 22:00 | 38.17 | 37.59
2019-08-03 22:30 | 36.54 | 35.93
2019-08-03 23:00 | 35.23 | 34.59
2019-08-03 23:30 | 33.5 | 32.81
2019-08-04 | 31.84 | 31.1
2019-08-04 00:30 | 30.76 | 30
2019-08-04 01:00 | 31.1 | 30.35
2019-08-04 01:30 | 29.49 | 28.68
2019-08-04 02:00 | 29.17 | 28.36
2019-08-04 02:30 | 29.19 | 28.37
2019-08-04 03:00 | 28.55 | 27.71
2019-08-04 03:30 | 28.21 | 27.35
2019-08-04 04:00 | 28.2 | 27.34
2019-08-04 04:30 | 29.12 | 28.29
2019-08-04 05:00 | 28.34 | 27.49
2019-08-04 05:30 | 29.2 | 28.38
2019-08-04 06:00 | 29.99 | 29.19
2019-08-04 06:30 | 31.2 | 30.44
2019-08-04 07:00 | 32.05 | 31.31
2019-08-04 07:30 | 33.44 | 32.74
2019-08-04 08:00 | 34.47 | 33.8
2019-08-04 08:30 | 33.6 | 32.92
2019-08-04 09:00 | 34.56 | 33.91
2019-08-04 09:30 | 34.58 | 33.95
2019-08-04 10:00 | 32.29 | 31.62
2019-08-04 10:30 | 31.22 | 30.54
2019-08-04 11:00 | 31.48 | 30.82
2019-08-04 11:30 | 30.62 | 29.95
2019-08-04 12:00 | 29.92 | 29.24
2019-08-04 12:30 | 29.17 | 28.46
2019-08-04 13:00 | 28.93 | 28.21
2019-08-04 13:30 | 28.91 | 28.19
2019-08-04 14:00 | 28.7 | 27.97
2019-08-04 14:30 | 28.35 | 27.61
2019-08-04 15:00 | 30.07 | 29.37
2019-08-04 15:30 | 31.55 | 30.87
2019-08-04 16:00 | 33.97 | 33.34
2019-08-04 16:30 | 36.17 | 35.58
2019-08-04 17:00 | 38.72 | 38.17
2019-08-04 17:30 | 42.06 | 41.55
2019-08-04 18:00 | 45.34 | 44.88
2019-08-04 18:30 | 48.51 | 48.09
2019-08-04 19:00 | 48.42 | 48
2019-08-04 19:30 | 46.05 | 45.6
2019-08-04 20:00 | 44.57 | 44.1
2019-08-04 20:30 | 43.44 | 42.95
2019-08-04 21:00 | 41.42 | 40.9
2019-08-04 21:30 | 38.84 | 38.27
2019-08-04 22:00 | 36.8 | 36.19
2019-08-04 22:30 | 35.45 | 34.81
2019-08-04 23:00 | 33.34 | 32.65
2019-08-04 23:30 | 31.73 | 30.99
2019-08-05 | 30.66 | 29.89
2019-08-05 00:30 | 30.25 | 29.47
2019-08-05 01:00 | 29.61 | 28.8
2019-08-05 01:30 | 28.7 | 27.86
2019-08-05 02:00 | 28.18 | 27.33
2019-08-05 02:30 | 28.72 | 27.88
2019-08-05 03:00 | 28.1 | 27.24
2019-08-05 03:30 | 27.61 | 26.73
2019-08-05 04:00 | 27.97 | 27.11
2019-08-05 04:30 | 29.42 | 28.61
2019-08-05 05:00 | 30.23 | 29.45
2019-08-05 05:30 | 32.65 | 31.96
2019-08-05 06:00 | 35.72 | 35.1
2019-08-05 06:30 | 40.08 | 39.57
2019-08-05 07:00 | 44.34 | 43.91
2019-08-05 07:30 | 49.36 | 48.95
2019-08-05 08:00 | 49.34 | 48.95
2019-08-05 08:30 | 48.47 | 48.05
2019-08-05 09:00 | 47.17 | 46.6
2019-08-05 09:30 | 48.95 | 48.31
2019-08-05 10:00 | 49.98 | 49.32
2019-08-05 10:30 | 49.82 | 49.09
2019-08-05 11:00 | 50.66 | 49.88
2019-08-05 11:30 | 49.61 | 48.73
2019-08-05 12:00 | 45.47 | 44.78
2019-08-05 12:30 | 47.46 | 47.07
2019-08-05 13:00 | 48.67 | 48.29
2019-08-05 13:30 | 47.6 | 47.21
2019-08-05 14:00 | 45.76 | 45.35
2019-08-05 14:30 | 45.07 | 44.65
2019-08-05 15:00 | 47.43 | 47.03
2019-08-05 15:30 | 49.53 | 49.15
2019-08-05 16:00 | 49.7 | 49.3
2019-08-05 16:30 | 50.56 | 50.14
2019-08-05 17:00 | 51.46 | 51.03
2019-08-05 17:30 | 52.26 | 51.82
2019-08-05 18:00 | 53.61 | 53.17
2019-08-05 18:30 | 55.57 | 55.14
2019-08-05 19:00 | 55.35 | 54.92
2019-08-05 19:30 | 52.74 | 52.27
2019-08-05 20:00 | 50.62 | 50.13
2019-08-05 20:30 | 48.26 | 47.73
2019-08-05 21:00 | 46.33 | 45.79
2019-08-05 21:30 | 43.87 | 43.34
2019-08-05 22:00 | 41.17 | 40.59
2019-08-05 22:30 | 38.32 | 37.69
2019-08-05 23:00 | 37 | 36.33
2019-08-05 23:30 | 34.72 | 33.99
2019-08-06 | 33.07 | 32.29
2019-08-06 00:30 | 32.27 | 31.47
2019-08-06 01:00 | 31.07 | 30.23
2019-08-06 01:30 | 30.44 | 29.67
2019-08-06 02:00 | 29.85 | 29.08
2019-08-06 02:30 | 29.52 | 28.73
2019-08-06 03:00 | 28.78 | 27.96
2019-08-06 03:30 | 28.89 | 28.08
2019-08-06 04:00 | 29.26 | 28.46
2019-08-06 04:30 | 30.25 | 29.48
2019-08-06 05:00 | 31.92 | 31.2
2019-08-06 05:30 | 34.48 | 33.83
2019-08-06 06:00 | 37.26 | 36.69
2019-08-06 06:30 | 41.67 | 41.19
2019-08-06 07:00 | 45.57 | 45.13
2019-08-06 07:30 | 50.67 | 50.28
2019-08-06 08:00 | 42.34 | 41.87
2019-08-06 08:30 | 36.7 | 36.14
2019-08-06 09:00 | 34.59 | 34
2019-08-06 09:30 | 31.86 | 31.25
2019-08-06 10:00 | 32.55 | 31.96
2019-08-06 10:30 | 31.55 | 30.95
2019-08-06 11:00 | 32.14 | 31.57
2019-08-06 11:30 | 31.86 | 31.27
2019-08-06 12:00 | 30.2 | 29.58
2019-08-06 12:30 | 29.4 | 28.76
2019-08-06 13:00 | 29.49 | 28.86
2019-08-06 13:30 | 29.23 | 28.54
2019-08-06 14:00 | 29.82 | 29.11
2019-08-06 14:30 | 30.52 | 29.83
2019-08-06 15:00 | 31.33 | 30.66
2019-08-06 15:30 | 33.3 | 32.66
2019-08-06 16:00 | 34.22 | 33.59
2019-08-06 16:30 | 36.36 | 35.75
2019-08-06 17:00 | 37.63 | 37.03
2019-08-06 17:30 | 38.85 | 38.24
2019-08-06 18:00 | 44.03 | 43.49
2019-08-06 18:30 | 55.42 | 54.99
2019-08-06 19:00 | 55.5 | 55.07
2019-08-06 19:30 | 52.8 | 52.34
2019-08-06 20:00 | 50.72 | 50.23
2019-08-06 20:30 | 49.51 | 49
2019-08-06 21:00 | 46.56 | 46
2019-08-06 21:30 | 44.23 | 43.7
2019-08-06 22:00 | 41.1 | 40.52
2019-08-06 22:30 | 38.01 | 37.37
2019-08-06 23:00 | 37 | 36.35
2019-08-06 23:30 | 34.48 | 33.85
2019-08-07 | 32.54 | 31.86
2019-08-07 00:30 | 31.96 | 31.26
2019-08-07 01:00 | 31.38 | 30.66
2019-08-07 01:30 | 30.98 | 30.24
2019-08-07 02:00 | 29.65 | 28.88
2019-08-07 02:30 | 29.09 | 28.29
2019-08-07 03:00 | 28.7 | 27.89
2019-08-07 03:30 | 28.73 | 27.92
2019-08-07 04:00 | 29.83 | 29.06
2019-08-07 04:30 | 31.83 | 31.11
2019-08-07 05:00 | 33.03 | 32.35
2019-08-07 05:30 | 34.91 | 34.28
2019-08-07 06:00 | 37.91 | 37.36
2019-08-07 06:30 | 41.51 | 41.04
2019-08-07 07:00 | 46.22 | 45.79
2019-08-07 07:30 | 50.82 | 50.44
2019-08-07 08:00 | 51.28 | 50.86
2019-08-07 08:30 | 50.65 | 49.96
2019-08-07 09:00 | 49 | 47.34
2019-08-07 09:30 | 47.98 | 46.33
2019-08-07 10:00 | 46.87 | 45.19
2019-08-07 10:30 | 47.1 | 45.4
2019-08-07 11:00 | 47.69 | 45.97
2019-08-07 11:30 | 46.65 | 44.89
2019-08-07 12:00 | 46.28 | 44.51
2019-08-07 12:30 | 46.39 | 44.62
2019-08-07 13:00 | 47.09 | 45.31
2019-08-07 13:30 | 45.71 | 43.91
2019-08-07 14:00 | 46.47 | 44.72
2019-08-07 14:30 | 48.45 | 46.77
2019-08-07 15:00 | 49.48 | 47.83
2019-08-07 15:30 | 50.56 | 48.92
2019-08-07 16:00 | 52.53 | 50.91
2019-08-07 16:30 | 52.63 | 50.95
2019-08-07 17:00 | 52.44 | 50.7
2019-08-07 17:30 | 53.77 | 52.03
2019-08-07 18:00 | 54.72 | 52.99
2019-08-07 18:30 | 57.47 | 55.85
2019-08-07 19:00 | 57.33 | 55.7
2019-08-07 19:30 | 54.08 | 52.31
2019-08-07 20:00 | 52.12 | 50.27
2019-08-07 20:30 | 50.26 | 48.3
2019-08-07 21:00 | 48.45 | 46.37
2019-08-07 21:30 | 45.95 | 43.72
2019-08-07 22:00 | 43.89 | 41.66
2019-08-07 22:30 | 40.39 | 37.95
2019-08-07 23:00 | 39.49 | 36.96
2019-08-07 23:30 | 37.52 | 34.81
2019-08-08 | 35.79 | 33.02
2019-08-08 00:30 | 35.57 | 32.87
2019-08-08 01:00 | 34.49 | 31.67
2019-08-08 01:30 | 33.68 | 30.77
2019-08-08 02:00 | 32.7 | 29.72
2019-08-08 02:30 | 32.51 | 29.48
2019-08-08 03:00 | 32.14 | 29.05
2019-08-08 03:30 | 32.03 | 28.92
2019-08-08 04:00 | 32.05 | 28.94
2019-08-08 04:30 | 32.72 | 29.7
2019-08-08 05:00 | 34.07 | 31.19
2019-08-08 05:30 | 36.65 | 34.05
2019-08-08 06:00 | 39.25 | 36.89
2019-08-08 06:30 | 43.38 | 41.36
2019-08-08 07:00 | 48.45 | 46.67
2019-08-08 07:30 | 52.44 | 50.8
2019-08-08 08:00 | 55.38 | 53.88
2019-08-08 08:30 | 55.25 | 53.72
2019-08-08 09:00 | 54.28 | 52.81
2019-08-08 09:30 | 53.04 | 51.54
2019-08-08 10:00 | 49.16 | 47.53
2019-08-08 10:30 | 46.99 | 45.21
2019-08-08 11:00 | 47.46 | 45.7
2019-08-08 11:30 | 48.03 | 46.33
2019-08-08 12:00 | 48.66 | 47
2019-08-08 12:30 | 48.83 | 47.18
2019-08-08 13:00 | 48.39 | 46.7
2019-08-08 13:30 | 48.02 | 46.33
2019-08-08 14:00 | 49.12 | 47.48
2019-08-08 14:30 | 50.03 | 48.42
2019-08-08 15:00 | 52.47 | 50.94
2019-08-08 15:30 | 54.19 | 52.69
2019-08-08 16:00 | 55.45 | 53.97
2019-08-08 16:30 | 54.63 | 53.07
2019-08-08 17:00 | 55.05 | 53.46
2019-08-08 17:30 | 54.86 | 53.21
2019-08-08 18:00 | 56.09 | 54.44
2019-08-08 18:30 | 58.42 | 56.85
2019-08-08 19:00 | 57.55 | 55.94
2019-08-08 19:30 | 56.22 | 54.53
2019-08-08 20:00 | 53.23 | 51.42
2019-08-08 20:30 | 50.96 | 49.04
2019-08-08 21:00 | 49.59 | 47.58
2019-08-08 21:30 | 47.02 | 44.84
2019-08-08 22:00 | 44.23 | 41.94
2019-08-08 22:30 | 41.34 | 38.93
2019-08-08 23:00 | 40.31 | 37.83
2019-08-08 23:30 | 38.39 | 35.89
2019-08-09 | 35.82 | 33.15
2019-08-09 00:30 | 35.32 | 32.57
2019-08-09 01:00 | 34.36 | 31.51
2019-08-09 01:30 | 33.57 | 30.64
2019-08-09 02:00 | 33.04 | 30.02
2019-08-09 02:30 | 32.23 | 29.09
2019-08-09 03:00 | 32.01 | 28.85
2019-08-09 03:30 | 32.13 | 28.97
2019-08-09 04:00 | 32.22 | 29.08
2019-08-09 04:30 | 33 | 29.98
2019-08-09 05:00 | 33.9 | 30.99
2019-08-09 05:30 | 35.9 | 33.21
2019-08-09 06:00 | 38.33 | 35.87
2019-08-09 06:30 | 42.86 | 40.78
2019-08-09 07:00 | 46.84 | 44.92
2019-08-09 07:30 | 51.12 | 49.4
2019-08-09 08:00 | 52.05 | 50.41
2019-08-09 08:30 | 50.06 | 48.37
2019-08-09 09:00 | 47.91 | 46.19
2019-08-09 09:30 | 47.03 | 45.29
2019-08-09 10:00 | 45.91 | 44.14
2019-08-09 10:30 | 45.6 | 43.86
2019-08-09 11:00 | 46.29 | 44.51
2019-08-09 11:30 | 44.72 | 42.81
2019-08-09 12:00 | 44.3 | 42.38
2019-08-09 12:30 | 44.2 | 42.28
2019-08-09 13:00 | 45.33 | 43.46
2019-08-09 13:30 | 46.16 | 44.34
2019-08-09 14:00 | 46.51 | 44.68
2019-08-09 14:30 | 45.86 | 44
2019-08-09 15:00 | 46.04 | 44.16
2019-08-09 15:30 | 46.57 | 44.66
2019-08-09 16:00 | 48.34 | 46.49
2019-08-09 16:30 | 49.56 | 47.7
2019-08-09 17:00 | 50.43 | 48.57
2019-08-09 17:30 | 51.17 | 49.27
2019-08-09 18:00 | 52.94 | 51.11
2019-08-09 18:30 | 53.56 | 51.74
2019-08-09 19:00 | 53.02 | 51.17
2019-08-09 19:30 | 50.62 | 48.63
2019-08-09 20:00 | 47.81 | 45.68
2019-08-09 20:30 | 46.66 | 44.46
2019-08-09 21:00 | 45.75 | 43.46
2019-08-09 21:30 | 43.82 | 41.51
2019-08-09 22:00 | 41.76 | 39.54
2019-08-09 22:30 | 39.44 | 37.04
2019-08-09 23:00 | 38.37 | 35.87
2019-08-09 23:30 | 36.35 | 33.67
2019-08-10 | 35.04 | 32.23
2019-08-10 00:30 | 34.37 | 31.49
2019-08-10 01:00 | 33.65 | 30.68
2019-08-10 01:30 | 33.07 | 30.01
2019-08-10 02:00 | 32.05 | 28.91
2019-08-10 02:30 | 31.37 | 28.1
2019-08-10 03:00 | 31.05 | 27.74
2019-08-10 03:30 | 30.81 | 27.47
2019-08-10 04:00 | 28.36 | 28.33
2019-08-10 04:30 | 28.85 | 28.85
2019-08-10 05:00 | 28.91 | 28.9
2019-08-10 05:30 | 29.95 | 29.95
2019-08-10 06:00 | 31.21 | 31.21
2019-08-10 06:30 | 33.18 | 33.17
2019-08-10 07:00 | 34.15 | 34.14
2019-08-10 07:30 | 36.01 | 35.98
2019-08-10 08:00 | 37.17 | 37.11
2019-08-10 08:30 | 38.8 | 38.65
2019-08-10 09:00 | 38.33 | 38.09
2019-08-10 09:30 | 37.3 | 37.01
2019-08-10 10:00 | 34.85 | 34.52
2019-08-10 10:30 | 33.92 | 33.49
2019-08-10 11:00 | 33.24 | 32.72
2019-08-10 11:30 | 31.89 | 31.32
2019-08-10 12:00 | 30.98 | 30.35
2019-08-10 12:30 | 29.92 | 29.41
2019-08-10 13:00 | 29.33 | 28.79
2019-08-10 13:30 | 29.6 | 29.11
2019-08-10 14:00 | 29.79 | 29.34
2019-08-10 14:30 | 30.72 | 30.32
2019-08-10 15:00 | 32.44 | 32.06
2019-08-10 15:30 | 33.67 | 33.36
2019-08-10 16:00 | 35.64 | 35.38
2019-08-10 16:30 | 36.92 | 36.71
2019-08-10 17:00 | 38.45 | 38.28
2019-08-10 17:30 | 40.74 | 40.62
2019-08-10 18:00 | 43.81 | 43.68
2019-08-10 18:30 | 45.92 | 45.64
2019-08-10 19:00 | 47.7 | 45.83
2019-08-10 19:30 | 45.45 | 43.46
2019-08-10 20:00 | 43.87 | 41.78
2019-08-10 20:30 | 42.41 | 40.22
2019-08-10 21:00 | 41.72 | 39.49
2019-08-10 21:30 | 40.09 | 37.73
2019-08-10 22:00 | 38.74 | 36.24
2019-08-10 22:30 | 37.6 | 35.01
2019-08-10 23:00 | 36.07 | 33.36
2019-08-10 23:30 | 34.63 | 31.78
2019-08-11 | 33.63 | 30.68
2019-08-11 00:30 | 32.75 | 29.69
2019-08-11 01:00 | 32.03 | 28.89
2019-08-11 01:30 | 31.44 | 28.21
2019-08-11 02:00 | 31.71 | 28.43
2019-08-11 02:30 | 28.99 | 27.81
2019-08-11 03:00 | 26.91 | 26.89
2019-08-11 03:30 | 26.88 | 26.84
2019-08-11 04:00 | 27.09 | 27.06
2019-08-11 04:30 | 27.46 | 27.43
2019-08-11 05:00 | 27.5 | 27.47
2019-08-11 05:30 | 28.16 | 28.13
2019-08-11 06:00 | 29.09 | 29.07
2019-08-11 06:30 | 30.66 | 30.65
2019-08-11 07:00 | 31.22 | 31.21
2019-08-11 07:30 | 32.18 | 32.17
2019-08-11 08:00 | 32.01 | 32.01
2019-08-11 08:30 | 31.82 | 31.82
2019-08-11 09:00 | 31.03 | 31.02
2019-08-11 09:30 | 30.44 | 30.42
2019-08-11 10:00 | 29.34 | 29.32
2019-08-11 10:30 | 29.03 | 28.99
2019-08-11 11:00 | 27.6 | 27.54
2019-08-11 11:30 | 26.8 | 26.72
2019-08-11 12:00 | 25.56 | 25.46
2019-08-11 12:30 | 25.49 | 25.36
2019-08-11 13:00 | 25.29 | 25.14
2019-08-11 13:30 | 24.93 | 24.81
2019-08-11 14:00 | 25.28 | 25.17
2019-08-11 14:30 | 26.15 | 26.06
2019-08-11 15:00 | 27.79 | 27.71
2019-08-11 15:30 | 29.61 | 29.56
2019-08-11 16:00 | 32 | 31.95
2019-08-11 16:30 | 34.24 | 34.2
2019-08-11 17:00 | 36.81 | 36.78
2019-08-11 17:30 | 40.45 | 40.42
2019-08-11 18:00 | 44.29 | 44.27
2019-08-11 18:30 | 47.87 | 47.8
2019-08-11 19:00 | 48.27 | 48.2
2019-08-11 19:30 | 46.29 | 46.24
2019-08-11 20:00 | 44.54 | 44.5
2019-08-11 20:30 | 43.23 | 43.21
2019-08-11 21:00 | 41 | 40.99
2019-08-11 21:30 | 39.06 | 39.06
2019-08-11 22:00 | 37.07 | 37.07
2019-08-11 22:30 | 34.58 | 34.58
2019-08-11 23:00 | 32.97 | 32.97
2019-08-11 23:30 | 31.58 | 31.56
2019-08-12 | 30.07 | 30.04
2019-08-12 00:30 | 29.52 | 29.47
2019-08-12 01:00 | 28.38 | 28.32
2019-08-12 01:30 | 28.1 | 28.05
2019-08-12 02:00 | 27.83 | 27.75
2019-08-12 02:30 | 29.02 | 28.95
2019-08-12 03:00 | 27.8 | 27.73
2019-08-12 03:30 | 28.08 | 28.02
2019-08-12 04:00 | 28.58 | 28.52
2019-08-12 04:30 | 29.83 | 29.79
2019-08-12 05:00 | 31.6 | 31.58
2019-08-12 05:30 | 34.7 | 34.69
2019-08-12 06:00 | 38.36 | 38.35
2019-08-12 06:30 | 43.55 | 43.46
2019-08-12 07:00 | 49.48 | 49.31
2019-08-12 07:30 | 53.32 | 53.23
2019-08-12 08:00 | 52.72 | 52.53
2019-08-12 08:30 | 50.03 | 49.75
2019-08-12 09:00 | 46.21 | 45.87
2019-08-12 09:30 | 44.3 | 43.9
2019-08-12 10:00 | 42.52 | 42.12
2019-08-12 10:30 | 40.94 | 40.42
2019-08-12 11:00 | 39.74 | 39.08
2019-08-12 11:30 | 39.61 | 38.89
2019-08-12 12:00 | 40.85 | 40.06
2019-08-12 12:30 | 39.95 | 39.09
2019-08-12 13:00 | 39.42 | 38.56
2019-08-12 13:30 | 39.26 | 38.39
2019-08-12 14:00 | 39.24 | 38.36
2019-08-12 14:30 | 40.52 | 39.65
2019-08-12 15:00 | 41.42 | 40.59
2019-08-12 15:30 | 41.79 | 41.12
2019-08-12 16:00 | 44.7 | 44.21
2019-08-12 16:30 | 46.1 | 45.76
2019-08-12 17:00 | 48.16 | 47.95
2019-08-12 17:30 | 49.6 | 49.5
2019-08-12 18:00 | 51.76 | 51.71
2019-08-12 18:30 | 55.34 | 55.28
2019-08-12 19:00 | 55.57 | 55.52
2019-08-12 19:30 | 53.24 | 53.21
2019-08-12 20:00 | 51.12 | 51.11
2019-08-12 20:30 | 52.49 | 52.45
2019-08-12 21:00 | 49.43 | 49.41
2019-08-12 21:30 | 45.4 | 45.4
2019-08-12 22:00 | 41.35 | 41.32
2019-08-12 22:30 | 38.49 | 38.43
2019-08-12 23:00 | 37.65 | 37.59
2019-08-12 23:30 | 35.76 | 35.67
2019-08-13 | 33.97 | 33.85
2019-08-13 00:30 | 33.33 | 33.2
2019-08-13 01:00 | 32.12 | 31.96
2019-08-13 01:30 | 31.4 | 31.21
2019-08-13 02:00 | 31.16 | 30.96
2019-08-13 02:30 | 31.9 | 31.66
2019-08-13 03:00 | 30.85 | 30.58
2019-08-13 03:30 | 31.02 | 30.74
2019-08-13 04:00 | 30.9 | 30.6
2019-08-13 04:30 | 32.91 | 32.68
2019-08-13 05:00 | 33.78 | 33.59
2019-08-13 05:30 | 33.07 | 32.84
2019-08-13 06:00 | 34.99 | 34.83
2019-08-13 06:30 | 40.23 | 40.19
2019-08-13 07:00 | 44.45 | 44.45
2019-08-13 07:30 | 48.33 | 48.28
2019-08-13 08:00 | 48.41 | 48.29
2019-08-13 08:30 | 45.09 | 44.96
2019-08-13 09:00 | 42.44 | 42.24
2019-08-13 09:30 | 39.79 | 39.58
2019-08-13 10:00 | 38.18 | 37.92
2019-08-13 10:30 | 41.51 | 40.87
2019-08-13 11:00 | 43.39 | 42.38
2019-08-13 11:30 | 44.54 | 42.71
2019-08-13 12:00 | 44.28 | 42.36
2019-08-13 12:30 | 43.64 | 41.68
2019-08-13 13:00 | 42.76 | 40.73
2019-08-13 13:30 | 43.41 | 41.43
2019-08-13 14:00 | 43.72 | 41.75
2019-08-13 14:30 | 44.11 | 42.16
2019-08-13 15:00 | 44.4 | 42.44
2019-08-13 15:30 | 45.92 | 44.02
2019-08-13 16:00 | 47.56 | 45.68
2019-08-13 16:30 | 48.83 | 46.95
2019-08-13 17:00 | 50.05 | 48.18
2019-08-13 17:30 | 51.78 | 49.92
2019-08-13 18:00 | 53.72 | 51.91
2019-08-13 18:30 | 55.93 | 54.2
2019-08-13 19:00 | 56.52 | 54.82
2019-08-13 19:30 | 54.46 | 52.68
2019-08-13 20:00 | 52.66 | 50.78
2019-08-13 20:30 | 50.58 | 48.58
2019-08-13 21:00 | 48.39 | 46.27
2019-08-13 21:30 | 46.59 | 44.36
2019-08-13 22:00 | 43.92 | 41.51
2019-08-13 22:30 | 40.66 | 37.99
2019-08-13 23:00 | 39.6 | 36.85
2019-08-13 23:30 | 37.54 | 34.59
2019-08-14 | 32.94 | 32.26
2019-08-14 00:30 | 32.34 | 32.12
2019-08-14 01:00 | 30.93 | 30.69
2019-08-14 01:30 | 30.34 | 30.07
2019-08-14 02:00 | 29.7 | 29.4
2019-08-14 02:30 | 29.97 | 29.63
2019-08-14 03:00 | 29.05 | 28.64
2019-08-14 03:30 | 29.41 | 29.03
2019-08-14 04:00 | 29.31 | 28.86
2019-08-14 04:30 | 31.01 | 30.62
2019-08-14 05:00 | 31.83 | 31.49
2019-08-14 05:30 | 35.16 | 34.96
2019-08-14 06:00 | 38.01 | 37.92
2019-08-14 06:30 | 43.53 | 43.52
2019-08-14 07:00 | 47.92 | 47.89
2019-08-14 07:30 | 52.68 | 52.55
2019-08-14 08:00 | 51.57 | 51.32
2019-08-14 08:30 | 49.15 | 48.79
2019-08-14 09:00 | 46.1 | 45.64
2019-08-14 09:30 | 44.64 | 44.1
2019-08-14 10:00 | 42.85 | 42.27
2019-08-14 10:30 | 42.05 | 41.29
2019-08-14 11:00 | 41.64 | 40.74
2019-08-14 11:30 | 42.7 | 41.37
2019-08-14 12:00 | 42.94 | 41.07
2019-08-14 12:30 | 42.54 | 40.65
2019-08-14 13:00 | 42.8 | 40.92
2019-08-14 13:30 | 41.78 | 39.84
2019-08-14 14:00 | 42.54 | 40.65
2019-08-14 14:30 | 43.43 | 41.59
2019-08-14 15:00 | 44.29 | 42.47
2019-08-14 15:30 | 45.61 | 43.82
2019-08-14 16:00 | 47.4 | 45.66
2019-08-14 16:30 | 49.92 | 48.23
2019-08-14 17:00 | 50.47 | 48.75
2019-08-14 17:30 | 50.72 | 48.94
2019-08-14 18:00 | 53.08 | 51.36
2019-08-14 18:30 | 55.9 | 54.27
2019-08-14 19:00 | 56.15 | 54.53
2019-08-14 19:30 | 54.69 | 52.99
2019-08-14 20:00 | 52.53 | 50.74
2019-08-14 20:30 | 49.95 | 48.04
2019-08-14 21:00 | 48.49 | 46.49
2019-08-14 21:30 | 46.15 | 44.01
2019-08-14 22:00 | 43.22 | 40.89
2019-08-14 22:30 | 40.08 | 37.56
2019-08-14 23:00 | 39.3 | 36.7
2019-08-14 23:30 | 37.3 | 34.53
2019-08-15 | 36.58 | 33.73
2019-08-15 00:30 | 35.67 | 32.79
2019-08-15 01:00 | 33.92 | 31.01
2019-08-15 01:30 | 33.14 | 30.15
2019-08-15 02:00 | 32.57 | 29.5
2019-08-15 02:30 | 32.23 | 29.1
2019-08-15 03:00 | 31.96 | 28.81
2019-08-15 03:30 | 32.12 | 28.99
2019-08-15 04:00 | 32.2 | 29.08
2019-08-15 04:30 | 32.83 | 29.78
2019-08-15 05:00 | 34 | 31.11
2019-08-15 05:30 | 36.41 | 33.77
2019-08-15 06:00 | 39.19 | 36.79
2019-08-15 06:30 | 43.73 | 41.67
2019-08-15 07:00 | 47.79 | 45.89
2019-08-15 07:30 | 52.71 | 51.05
2019-08-15 08:00 | 53.74 | 52.17
2019-08-15 08:30 | 53.35 | 51.8
2019-08-15 09:00 | 51.66 | 50.09
2019-08-15 09:30 | 51.97 | 50.43
2019-08-15 10:00 | 52.54 | 51.03
2019-08-15 10:30 | 52.05 | 50.54
2019-08-15 11:00 | 52.25 | 50.76
2019-08-15 11:30 | 50.94 | 49.33
2019-08-15 12:00 | 48.45 | 46.75
2019-08-15 12:30 | 47.12 | 45.35
2019-08-15 13:00 | 47.67 | 45.93
2019-08-15 13:30 | 47.79 | 46.03
2019-08-15 14:00 | 48.95 | 47.26
2019-08-15 14:30 | 48.24 | 46.5
2019-08-15 15:00 | 48.96 | 47.24
2019-08-15 15:30 | 50.39 | 48.71
2019-08-15 16:00 | 52.26 | 50.61
2019-08-15 16:30 | 52.66 | 50.97
2019-08-15 17:00 | 52.63 | 50.87
2019-08-15 17:30 | 54.18 | 52.43
2019-08-15 18:00 | 55.04 | 53.3
2019-08-15 18:30 | 58.94 | 57.35
2019-08-15 19:00 | 58.52 | 56.91
2019-08-15 19:30 | 56.15 | 54.44
2019-08-15 20:00 | 53.79 | 51.98
2019-08-15 20:30 | 51.79 | 49.87
2019-08-15 21:00 | 50.94 | 48.96
2019-08-15 21:30 | 46.69 | 44.46
2019-08-15 22:00 | 43.63 | 41.35
2019-08-15 22:30 | 41.19 | 38.75
2019-08-15 23:00 | 40.04 | 37.5
2019-08-15 23:30 | 38.26 | 35.58
2019-08-16 | 36.17 | 33.29
2019-08-16 00:30 | 35.49 | 32.53
2019-08-16 01:00 | 34.49 | 31.42
2019-08-16 01:30 | 30.78 | 30.39
2019-08-16 02:00 | 30.12 | 30.07
2019-08-16 02:30 | 29.92 | 29.91
2019-08-16 03:00 | 29.42 | 29.41
2019-08-16 03:30 | 28.48 | 28.47
2019-08-16 04:00 | 29.72 | 29.71
2019-08-16 04:30 | 29.73 | 29.72
2019-08-16 05:00 | 31.76 | 31.76
2019-08-16 05:30 | 33.58 | 33.56
2019-08-16 06:00 | 35.83 | 35.78
2019-08-16 06:30 | 40.32 | 40.16
2019-08-16 07:00 | 45.49 | 45.36
2019-08-16 07:30 | 49.4 | 49.24
2019-08-16 08:00 | 50.07 | 49.78
2019-08-16 08:30 | 48.02 | 47.56
2019-08-16 09:00 | 46.43 | 45.83
2019-08-16 09:30 | 46.28 | 45.54
2019-08-16 10:00 | 45.05 | 44.23
2019-08-16 10:30 | 44.84 | 43.44
2019-08-16 11:00 | 44.4 | 42.45
2019-08-16 11:30 | 44.01 | 42.06
2019-08-16 12:00 | 43.27 | 41.27
2019-08-16 12:30 | 43.8 | 41.82
2019-08-16 13:00 | 43.05 | 41.02
2019-08-16 13:30 | 42.6 | 40.54
2019-08-16 14:00 | 42.88 | 40.82
2019-08-16 14:30 | 43.23 | 41.18
2019-08-16 15:00 | 43.37 | 41.3
2019-08-16 15:30 | 44.38 | 42.34
2019-08-16 16:00 | 46.3 | 44.31
2019-08-16 16:30 | 47.66 | 45.68
2019-08-16 17:00 | 48.54 | 46.55
2019-08-16 17:30 | 49.17 | 47.14
2019-08-16 18:00 | 50.18 | 48.17
2019-08-16 18:30 | 51.62 | 49.68
2019-08-16 19:00 | 51.97 | 50.01
2019-08-16 19:30 | 50.18 | 48.14
2019-08-16 20:00 | 48.54 | 46.42
2019-08-16 20:30 | 46.6 | 44.36
2019-08-16 21:00 | 44.68 | 42.48
2019-08-16 21:30 | 43 | 40.69
2019-08-16 22:00 | 41.46 | 39.02
2019-08-16 22:30 | 39.17 | 36.54
2019-08-16 23:00 | 37.83 | 35.07
2019-08-16 23:30 | 36.25 | 33.54
2019-08-17 | 35.49 | 32.7
2019-08-17 00:30 | 34.26 | 31.36
2019-08-17 01:00 | 33.05 | 30.02
2019-08-17 01:30 | 32.39 | 29.26
2019-08-17 02:00 | 32.12 | 28.95
2019-08-17 02:30 | 31.62 | 28.38
2019-08-17 03:00 | 31.09 | 27.78
2019-08-17 03:30 | 30.86 | 27.52
2019-08-17 04:00 | 31.7 | 28.46
2019-08-17 04:30 | 31.42 | 28.14
2019-08-17 05:00 | 31.8 | 28.59
2019-08-17 05:30 | 33.03 | 29.98
2019-08-17 06:00 | 33.97 | 31.03
2019-08-17 06:30 | 35.89 | 33.15
2019-08-17 07:00 | 37.11 | 34.49
2019-08-17 07:30 | 38.38 | 35.89
2019-08-17 08:00 | 38.74 | 36.31
2019-08-17 08:30 | 39.22 | 36.87
2019-08-17 09:00 | 39.11 | 36.79
2019-08-17 09:30 | 37.77 | 35.39
2019-08-17 10:00 | 36.79 | 34.37
2019-08-17 10:30 | 36.14 | 33.71
2019-08-17 11:00 | 35.42 | 32.95
2019-08-17 11:30 | 34.8 | 32.3
2019-08-17 12:00 | 33.59 | 30.98
2019-08-17 12:30 | 32.53 | 29.79
2019-08-17 13:00 | 32.33 | 29.57
2019-08-17 13:30 | 32.42 | 29.66
2019-08-17 14:00 | 33.53 | 30.84
2019-08-17 14:30 | 33.58 | 30.84
2019-08-17 15:00 | 33.44 | 30.68
2019-08-17 15:30 | 35.06 | 32.42
2019-08-17 16:00 | 36.57 | 34.05
2019-08-17 16:30 | 38.16 | 35.74
2019-08-17 17:00 | 40.85 | 38.59
2019-08-17 17:30 | 43.58 | 41.47
2019-08-17 18:00 | 45.1 | 43.08
2019-08-17 18:30 | 47.24 | 45.34
2019-08-17 19:00 | 47.04 | 45.13
2019-08-17 19:30 | 45.25 | 43.24
2019-08-17 20:00 | 44.27 | 42.2
2019-08-17 20:30 | 42.34 | 40.14
2019-08-17 21:00 | 41.16 | 38.88
2019-08-17 21:30 | 39.89 | 37.5
2019-08-17 22:00 | 39.03 | 36.56
2019-08-17 22:30 | 36.97 | 34.32
2019-08-17 23:00 | 36.61 | 33.91
2019-08-17 23:30 | 35.72 | 32.94
2019-08-18 | 34.08 | 31.13
2019-08-18 00:30 | 33.11 | 30.03
2019-08-18 01:00 | 32.67 | 29.54
2019-08-18 01:30 | 31.82 | 28.59
2019-08-18 02:00 | 31.54 | 28.28
2019-08-18 02:30 | 30.78 | 27.37
2019-08-18 03:00 | 30.58 | 27.16
2019-08-18 03:30 | 30.96 | 27.58
2019-08-18 04:00 | 30.62 | 27.22
2019-08-18 04:30 | 31.66 | 28.37
2019-08-18 05:00 | 31.02 | 27.65
2019-08-18 05:30 | 32.17 | 28.96
2019-08-18 06:00 | 32.74 | 29.6
2019-08-18 06:30 | 33.01 | 29.89
2019-08-18 07:00 | 33.34 | 30.24
2019-08-18 07:30 | 34.02 | 31.02
2019-08-18 08:00 | 33.67 | 30.66
2019-08-18 08:30 | 33.95 | 31
2019-08-18 09:00 | 33.84 | 30.91
2019-08-18 09:30 | 33.1 | 30.13
2019-08-18 10:00 | 32.36 | 29.37
2019-08-18 10:30 | 32.72 | 29.8
2019-08-18 11:00 | 31.6 | 28.6
2019-08-18 11:30 | 30.45 | 27.35
2019-08-18 12:00 | 30.41 | 27.32
2019-08-18 12:30 | 30.16 | 27.05
2019-08-18 13:00 | 29.97 | 26.84
2019-08-18 13:30 | 30.05 | 26.94
2019-08-18 14:00 | 31.73 | 28.81
2019-08-18 14:30 | 31.52 | 28.57
2019-08-18 15:00 | 32.53 | 29.66
2019-08-18 15:30 | 33.81 | 31.05
2019-08-18 16:00 | 35.32 | 32.68
2019-08-18 16:30 | 37.03 | 34.49
2019-08-18 17:00 | 39.6 | 37.25
2019-08-18 17:30 | 42.4 | 40.23
2019-08-18 18:00 | 45.87 | 43.89
2019-08-18 18:30 | 49.44 | 47.65
2019-08-18 19:00 | 49.07 | 47.27
2019-08-18 19:30 | 47.82 | 45.95
2019-08-18 20:00 | 45.52 | 43.52
2019-08-18 20:30 | 43.84 | 41.75
2019-08-18 21:00 | 42.31 | 40.11
2019-08-18 21:30 | 40.65 | 38.33
2019-08-18 22:00 | 40.16 | 37.78
2019-08-18 22:30 | 36.72 | 34.04
2019-08-18 23:00 | 35.42 | 32.61
2019-08-18 23:30 | 33.55 | 30.54
2019-08-19 | 32.63 | 29.51
2019-08-19 00:30 | 31.45 | 28.18
2019-08-19 01:00 | 32.14 | 28.95
2019-08-19 01:30 | 31.24 | 27.94
2019-08-19 02:00 | 30.93 | 27.59
2019-08-19 02:30 | 30.36 | 26.93
2019-08-19 03:00 | 30.12 | 26.65
2019-08-19 03:30 | 30.28 | 26.83
2019-08-19 04:00 | 30.56 | 27.17
2019-08-19 04:30 | 32.04 | 28.84
2019-08-19 05:00 | 32.72 | 29.62
2019-08-19 05:30 | 35.06 | 32.23
2019-08-19 06:00 | 37.35 | 34.75
2019-08-19 06:30 | 41.56 | 39.33
2019-08-19 07:00 | 45.88 | 43.96
2019-08-19 07:30 | 50.24 | 48.44
2019-08-19 08:00 | 50.2 | 48.46
2019-08-19 08:30 | 48.68 | 46.92
2019-08-19 09:00 | 46.96 | 45.16
2019-08-19 09:30 | 45.87 | 44.04
2019-08-19 10:00 | 44.45 | 42.6
2019-08-19 10:30 | 44 | 42.15
2019-08-19 11:00 | 43.79 | 41.98
2019-08-19 11:30 | 43.4 | 41.58
2019-08-19 12:00 | 43.69 | 41.75
2019-08-19 12:30 | 43.15 | 41.17
2019-08-19 13:00 | 43.14 | 41.16
2019-08-19 13:30 | 44.78 | 42.88
2019-08-19 14:00 | 45.73 | 43.88
2019-08-19 14:30 | 45.54 | 43.66
2019-08-19 15:00 | 45.38 | 43.48
2019-08-19 15:30 | 46.32 | 44.43
2019-08-19 16:00 | 48.43 | 46.61
2019-08-19 16:30 | 48.96 | 47.1
2019-08-19 17:00 | 51.25 | 49.44
2019-08-19 17:30 | 52.72 | 50.9
2019-08-19 18:00 | 54.2 | 52.4
2019-08-19 18:30 | 55.91 | 54.16
2019-08-19 19:00 | 55.85 | 54.08
2019-08-19 19:30 | 52.49 | 50.56
2019-08-19 20:00 | 50.76 | 48.74
2019-08-19 20:30 | 47.71 | 46.16
2019-08-19 21:00 | 44.85 | 44.32
2019-08-19 21:30 | 42.96 | 42.42
2019-08-19 22:00 | 40.12 | 39.52
2019-08-19 22:30 | 37.27 | 36.62
2019-08-19 23:00 | 36.36 | 35.69
2019-08-19 23:30 | 34.64 | 33.92
2019-08-20 | 33.1 | 32.35
2019-08-20 00:30 | 32.48 | 31.7
2019-08-20 01:00 | 31.87 | 31.07
2019-08-20 01:30 | 31.1 | 30.27
2019-08-20 02:00 | 30.02 | 29.16
2019-08-20 02:30 | 29.58 | 28.7
2019-08-20 03:00 | 29.47 | 28.58
2019-08-20 03:30 | 29.33 | 28.43
2019-08-20 04:00 | 29.74 | 28.85
2019-08-20 04:30 | 30.11 | 29.24
2019-08-20 05:00 | 31.62 | 30.81
2019-08-20 05:30 | 34.25 | 33.51
2019-08-20 06:00 | 36.83 | 36.16
2019-08-20 06:30 | 41.17 | 40.62
2019-08-20 07:00 | 46.14 | 45.67
2019-08-20 07:30 | 50.52 | 50.14
2019-08-20 08:00 | 50.01 | 49.64
2019-08-20 08:30 | 48.57 | 48.17
2019-08-20 09:00 | 46.28 | 45.76
2019-08-20 09:30 | 43.14 | 42.59
2019-08-20 10:00 | 41.71 | 41.13
2019-08-20 10:30 | 42.36 | 41.57
2019-08-20 11:00 | 42.58 | 40.98
2019-08-20 11:30 | 42.59 | 40.72
2019-08-20 12:00 | 41.15 | 39.19
2019-08-20 12:30 | 41.23 | 39.25
2019-08-20 13:00 | 40.24 | 38.19
2019-08-20 13:30 | 40.54 | 38.52
2019-08-20 14:00 | 41.21 | 39.25
2019-08-20 14:30 | 42.35 | 40.44
2019-08-20 15:00 | 42.8 | 40.89
2019-08-20 15:30 | 43.73 | 41.83
2019-08-20 16:00 | 45.33 | 43.47
2019-08-20 16:30 | 47.24 | 45.4
2019-08-20 17:00 | 48.75 | 46.94
2019-08-20 17:30 | 50.23 | 48.42
2019-08-20 18:00 | 52.41 | 50.67
2019-08-20 18:30 | 55.01 | 53.37
2019-08-20 19:00 | 55.14 | 53.52
2019-08-20 19:30 | 53.16 | 51.44
2019-08-20 20:00 | 51.2 | 49.39
2019-08-20 20:30 | 48.91 | 46.98
2019-08-20 21:00 | 46.93 | 44.89
2019-08-20 21:30 | 44.79 | 42.6
2019-08-20 22:00 | 42.58 | 40.24
2019-08-20 22:30 | 39.87 | 37.32
2019-08-20 23:00 | 38.56 | 35.9
2019-08-20 23:30 | 36.01 | 33.1
2019-08-21 | 34.5 | 31.42
2019-08-21 00:30 | 34.26 | 31.13
2019-08-21 01:00 | 33.55 | 30.35
2019-08-21 01:30 | 33.45 | 30.23
2019-08-21 02:00 | 32.52 | 29.19
2019-08-21 02:30 | 32.04 | 28.64
2019-08-21 03:00 | 32.06 | 28.62
2019-08-21 03:30 | 29.45 | 28.23
2019-08-21 04:00 | 29.54 | 29.14
2019-08-21 04:30 | 31.27 | 30.96
2019-08-21 05:00 | 32.01 | 31.74
2019-08-21 05:30 | 34.21 | 34.03
2019-08-21 06:00 | 37.23 | 37.16
2019-08-21 06:30 | 42.19 | 42.19
2019-08-21 07:00 | 46.62 | 46.59
2019-08-21 07:30 | 51.22 | 51.07
2019-08-21 08:00 | 50.58 | 50.31
2019-08-21 08:30 | 49.07 | 48.62
2019-08-21 09:00 | 47.65 | 45.95
2019-08-21 09:30 | 45.45 | 43.59
2019-08-21 10:00 | 43.59 | 41.65
2019-08-21 10:30 | 42.85 | 40.89
2019-08-21 11:00 | 43.38 | 41.47
2019-08-21 11:30 | 42.4 | 40.46
2019-08-21 12:00 | 41.64 | 39.67
2019-08-21 12:30 | 41.21 | 39.21
2019-08-21 13:00 | 40.9 | 38.87
2019-08-21 13:30 | 40.96 | 38.94
2019-08-21 14:00 | 41.39 | 39.4
2019-08-21 14:30 | 42.22 | 40.26
2019-08-21 15:00 | 43.86 | 42
2019-08-21 15:30 | 44.92 | 43.07
2019-08-21 16:00 | 45.91 | 44.07
2019-08-21 16:30 | 47.09 | 45.23
2019-08-21 17:00 | 48.89 | 47.06
2019-08-21 17:30 | 50.65 | 48.85
2019-08-21 18:00 | 52.35 | 50.6
2019-08-21 18:30 | 54.61 | 52.94
2019-08-21 19:00 | 54.95 | 53.28
2019-08-21 19:30 | 53.34 | 51.6
2019-08-21 20:00 | 51.95 | 50.15
2019-08-21 20:30 | 50.15 | 48.26
2019-08-21 21:00 | 47.71 | 45.66
2019-08-21 21:30 | 45.87 | 43.71
2019-08-21 22:00 | 43.55 | 41.23
2019-08-21 22:30 | 41.31 | 38.82
2019-08-21 23:00 | 39.64 | 37.01
2019-08-21 23:30 | 36.76 | 33.98
2019-08-22 | 32.48 | 32.25
2019-08-22 00:30 | 32.1 | 31.79
2019-08-22 01:00 | 30.69 | 30.33
2019-08-22 01:30 | 30.28 | 29.9
2019-08-22 02:00 | 29.75 | 29.36
2019-08-22 02:30 | 29.46 | 29.2
2019-08-22 03:00 | 28.89 | 28.86
2019-08-22 03:30 | 29.76 | 29.74
2019-08-22 04:00 | 28.91 | 28.88
2019-08-22 04:30 | 30.18 | 30.16
2019-08-22 05:00 | 31.82 | 31.81
2019-08-22 05:30 | 34.9 | 34.9
2019-08-22 06:00 | 39.89 | 39.85
2019-08-22 06:30 | 44.76 | 44.62
2019-08-22 07:00 | 49.55 | 49.49
2019-08-22 07:30 | 53.7 | 53.56
2019-08-22 08:00 | 53.26 | 52.9
2019-08-22 08:30 | 48.74 | 48.33
2019-08-22 09:00 | 45.07 | 44.58
2019-08-22 09:30 | 42.91 | 42.4
2019-08-22 10:00 | 41.02 | 40.4
2019-08-22 10:30 | 40.18 | 39.34
2019-08-22 11:00 | 40.78 | 39.67
2019-08-22 11:30 | 39.93 | 38.84
2019-08-22 12:00 | 39.53 | 38.37
2019-08-22 12:30 | 38.87 | 37.73
2019-08-22 13:00 | 38.93 | 37.82
2019-08-22 13:30 | 39.19 | 38.71
2019-08-22 14:00 | 39.63 | 39.12
2019-08-22 14:30 | 40.35 | 39.8
2019-08-22 15:00 | 41.2 | 40.71
2019-08-22 15:30 | 42.31 | 41.84
2019-08-22 16:00 | 43.8 | 43.33
2019-08-22 16:30 | 45.19 | 44.71
2019-08-22 17:00 | 46.23 | 45.73
2019-08-22 17:30 | 47.45 | 46.93
2019-08-22 18:00 | 49.74 | 49.25
2019-08-22 18:30 | 52.84 | 52.38
2019-08-22 19:00 | 53.38 | 52.92
2019-08-22 19:30 | 51.64 | 51.16
2019-08-22 20:00 | 49.33 | 48.82
2019-08-22 20:30 | 47.78 | 47.26
2019-08-22 21:00 | 45.09 | 44.57
2019-08-22 21:30 | 42.95 | 42.39
2019-08-22 22:00 | 40.79 | 40.19
2019-08-22 22:30 | 38.45 | 37.8
2019-08-22 23:00 | 36.45 | 35.76
2019-08-22 23:30 | 34.26 | 33.51
2019-08-23 | 32.85 | 32.06
2019-08-23 00:30 | 31.95 | 31.13
2019-08-23 01:00 | 30.23 | 29.34
2019-08-23 01:30 | 30.09 | 29.22
2019-08-23 02:00 | 28.69 | 27.87
2019-08-23 02:30 | 29.41 | 28.61
2019-08-23 03:00 | 28.51 | 27.67
2019-08-23 03:30 | 28.38 | 27.53
2019-08-23 04:00 | 28.38 | 27.53
2019-08-23 04:30 | 29.84 | 29.04
2019-08-23 05:00 | 30.39 | 29.61
2019-08-23 05:30 | 33.66 | 32.97
2019-08-23 06:00 | 37.25 | 36.66
2019-08-23 06:30 | 42.41 | 41.89
2019-08-23 07:00 | 46.45 | 45.97
2019-08-23 07:30 | 49.41 | 49
2019-08-23 08:00 | 49.21 | 48.81
2019-08-23 08:30 | 46.3 | 45.9
2019-08-23 09:00 | 43.3 | 42.84
2019-08-23 09:30 | 41.27 | 40.74
2019-08-23 10:00 | 39.63 | 39.07
2019-08-23 10:30 | 38.2 | 37.49
2019-08-23 11:00 | 37.48 | 36.67
2019-08-23 11:30 | 36.73 | 35.89
2019-08-23 12:00 | 37.16 | 36.29
2019-08-23 12:30 | 37.26 | 36.43
2019-08-23 13:00 | 36.36 | 35.56
2019-08-23 13:30 | 36.86 | 36.12
2019-08-23 14:00 | 36.59 | 35.87
2019-08-23 14:30 | 37.05 | 36.42
2019-08-23 15:00 | 37.86 | 37.28
2019-08-23 15:30 | 39.52 | 39.03
2019-08-23 16:00 | 41.35 | 40.88
2019-08-23 16:30 | 43.05 | 42.58
2019-08-23 17:00 | 44.96 | 44.5
2019-08-23 17:30 | 46.61 | 46.14
2019-08-23 18:00 | 47.78 | 47.32
2019-08-23 18:30 | 49.93 | 49.49
2019-08-23 19:00 | 50.18 | 49.74
2019-08-23 19:30 | 47.81 | 47.33
2019-08-23 20:00 | 45.81 | 45.31
2019-08-23 20:30 | 44.21 | 43.67
2019-08-23 21:00 | 42.48 | 41.94
2019-08-23 21:30 | 40.63 | 40.1
2019-08-23 22:00 | 38.98 | 38.42
2019-08-23 22:30 | 36.94 | 36.34
2019-08-23 23:00 | 37 | 36.39
2019-08-23 23:30 | 35.02 | 34.37
2019-08-24 | 32.4 | 31.68
2019-08-24 00:30 | 31.24 | 30.48
2019-08-24 01:00 | 30.07 | 29.27
2019-08-24 01:30 | 29.5 | 28.68
2019-08-24 02:00 | 28.98 | 28.14
2019-08-24 02:30 | 27.7 | 26.83
2019-08-24 03:00 | 27.44 | 26.55
2019-08-24 03:30 | 27.08 | 26.18
2019-08-24 04:00 | 26.59 | 25.66
2019-08-24 04:30 | 27.66 | 26.78
2019-08-24 05:00 | 27.27 | 26.37
2019-08-24 05:30 | 28.99 | 28.16
2019-08-24 06:00 | 29.94 | 29.14
2019-08-24 06:30 | 31.68 | 30.94
2019-08-24 07:00 | 33.54 | 32.86
2019-08-24 07:30 | 36.35 | 35.74
2019-08-24 08:00 | 36.15 | 35.55
2019-08-24 08:30 | 36.58 | 36.01
2019-08-24 09:00 | 37.83 | 37.29
2019-08-24 09:30 | 40.46 | 39.95
2019-08-24 10:00 | 38.82 | 38.3
2019-08-24 10:30 | 37.45 | 36.92
2019-08-24 11:00 | 34.44 | 33.87
2019-08-24 11:30 | 21.78 | 20.56
2019-08-24 12:00 | 36.48 | 35.93
2019-08-24 12:30 | 33.22 | 32.6
2019-08-24 13:00 | 29.77 | 29.09
2019-08-24 13:30 | 29.43 | 28.74
2019-08-24 14:00 | 34.27 | 33.67
2019-08-24 14:30 | 33.99 | 33.37
2019-08-24 15:00 | 31.21 | 30.53
2019-08-24 15:30 | 32.14 | 31.48
2019-08-24 16:00 | 34.58 | 33.95
2019-08-24 16:30 | 35.44 | 34.82
2019-08-24 17:00 | 37.85 | 37.27
2019-08-24 17:30 | 39.44 | 38.88
2019-08-24 18:00 | 41.41 | 40.88
2019-08-24 18:30 | 43.99 | 43.51
2019-08-24 19:00 | 43.36 | 42.87
2019-08-24 19:30 | 41.94 | 41.42
2019-08-24 20:00 | 40.73 | 40.19
2019-08-24 20:30 | 39.36 | 38.79
2019-08-24 21:00 | 37.91 | 37.31
2019-08-24 21:30 | 36.86 | 36.25
2019-08-24 22:00 | 35.27 | 34.62
2019-08-24 22:30 | 34.1 | 33.41
2019-08-24 23:00 | 32.61 | 31.89
2019-08-24 23:30 | 31.09 | 30.32
2019-08-25 | 29.92 | 29.12
2019-08-25 00:30 | 28.78 | 27.94
2019-08-25 01:00 | 28.11 | 27.24
2019-08-25 01:30 | 27.86 | 26.98
2019-08-25 02:00 | 27.51 | 26.61
2019-08-25 02:30 | 27.1 | 26.17
2019-08-25 03:00 | 27.38 | 26.46
2019-08-25 03:30 | 26.55 | 25.61
2019-08-25 04:00 | 26.01 | 25.04
2019-08-25 04:30 | 26.31 | 25.36
2019-08-25 05:00 | 26.31 | 25.42
2019-08-25 05:30 | 26.71 | 25.86
2019-08-25 06:00 | 27.46 | 26.64
2019-08-25 06:30 | 28.27 | 27.48
2019-08-25 07:00 | 29.25 | 28.49
2019-08-25 07:30 | 31.12 | 30.41
2019-08-25 08:00 | 30.93 | 30.2
2019-08-25 08:30 | 30.3 | 29.52
2019-08-25 09:00 | 31.17 | 30.4
2019-08-25 09:30 | 29.85 | 29.03
2019-08-25 10:00 | 29.64 | 28.8
2019-08-25 10:30 | 28.45 | 27.56
2019-08-25 11:00 | 28.75 | 27.86
2019-08-25 11:30 | 27.63 | 26.7
2019-08-25 12:00 | 27.17 | 26.22
2019-08-25 12:30 | 26.81 | 25.84
2019-08-25 13:00 | 26.56 | 25.58
2019-08-25 13:30 | 26.58 | 25.6
2019-08-25 14:00 | 27.28 | 26.33
2019-08-25 14:30 | 27.26 | 26.33
2019-08-25 15:00 | 28.7 | 27.81
2019-08-25 15:30 | 30.07 | 29.23
2019-08-25 16:00 | 32.21 | 31.44
2019-08-25 16:30 | 33.85 | 33.12
2019-08-25 17:00 | 37.16 | 36.51
2019-08-25 17:30 | 40.35 | 39.75
2019-08-25 18:00 | 42.5 | 41.94
2019-08-25 18:30 | 46.1 | 45.58
2019-08-25 19:00 | 47.5 | 46.99
2019-08-25 19:30 | 44.79 | 44.25
2019-08-25 20:00 | 42.53 | 41.96
2019-08-25 20:30 | 40.28 | 39.69
2019-08-25 21:00 | 39.84 | 39.24
2019-08-25 21:30 | 37.53 | 36.9
2019-08-25 22:00 | 36.42 | 35.78
2019-08-25 22:30 | 33.75 | 33.05
2019-08-25 23:00 | 31.96 | 31.23
2019-08-25 23:30 | 29.96 | 29.19
2019-08-26 | 28.39 | 27.57
2019-08-26 00:30 | 27.9 | 27.07
2019-08-26 01:00 | 27.52 | 26.68
2019-08-26 01:30 | 26.53 | 25.66
2019-08-26 02:00 | 26.79 | 25.93
2019-08-26 02:30 | 26.7 | 25.85
2019-08-26 03:00 | 26.39 | 25.53
2019-08-26 03:30 | 26.09 | 25.22
2019-08-26 04:00 | 26.59 | 25.73
2019-08-26 04:30 | 27.15 | 26.29
2019-08-26 05:00 | 28.76 | 27.95
2019-08-26 05:30 | 31.59 | 30.84
2019-08-26 06:00 | 34.7 | 34.01
2019-08-26 06:30 | 38.5 | 37.86
2019-08-26 07:00 | 42.84 | 42.25
2019-08-26 07:30 | 46.13 | 45.58
2019-08-26 08:00 | 46.01 | 45.46
2019-08-26 08:30 | 44.45 | 43.87
2019-08-26 09:00 | 42.93 | 42.31
2019-08-26 09:30 | 42.39 | 41.74
2019-08-26 10:00 | 43.1 | 42.38
2019-08-26 10:30 | 41.94 | 41
2019-08-26 11:00 | 40.85 | 40.2
2019-08-26 11:30 | 40.37 | 39.72
2019-08-26 12:00 | 41 | 40.34
2019-08-26 12:30 | 40.79 | 40.13
2019-08-26 13:00 | 41.3 | 40.65
2019-08-26 13:30 | 41.92 | 41.28
2019-08-26 14:00 | 43.41 | 42.8
2019-08-26 14:30 | 44.36 | 43.77
2019-08-26 15:00 | 45.46 | 44.89
2019-08-26 15:30 | 46.48 | 45.9
2019-08-26 16:00 | 48.37 | 47.83
2019-08-26 16:30 | 49.67 | 49.17
2019-08-26 17:00 | 50.98 | 50.52
2019-08-26 17:30 | 51.56 | 51.13
2019-08-26 18:00 | 52.58 | 52.18
2019-08-26 18:30 | 55.19 | 54.81
2019-08-26 19:00 | 54.95 | 54.57
2019-08-26 19:30 | 50.97 | 50.57
2019-08-26 20:00 | 48.15 | 47.73
2019-08-26 20:30 | 45.8 | 45.36
2019-08-26 21:00 | 43.66 | 43.2
2019-08-26 21:30 | 42.43 | 41.92
2019-08-26 22:00 | 41.27 | 40.73
2019-08-26 22:30 | 36.94 | 36.35
2019-08-26 23:00 | 35.76 | 35.16
2019-08-26 23:30 | 33.76 | 33.12
2019-08-27 | 31.47 | 30.78
2019-08-27 00:30 | 31.34 | 30.64
2019-08-27 01:00 | 30.02 | 29.3
2019-08-27 01:30 | 29.34 | 28.61
2019-08-27 02:00 | 28.72 | 27.94
2019-08-27 02:30 | 28.14 | 27.3
2019-08-27 03:00 | 27.79 | 26.93
2019-08-27 03:30 | 27.91 | 27.06
2019-08-27 04:00 | 27.85 | 27.01
2019-08-27 04:30 | 28.74 | 27.93
2019-08-27 05:00 | 29.84 | 29.05
2019-08-27 05:30 | 32.51 | 31.78
2019-08-27 06:00 | 34.98 | 34.28
2019-08-27 06:30 | 38.95 | 38.31
2019-08-27 07:00 | 43.73 | 43.14
2019-08-27 07:30 | 47.24 | 46.7
2019-08-27 08:00 | 47.54 | 47
2019-08-27 08:30 | 45.25 | 44.67
2019-08-27 09:00 | 39.76 | 38.99
2019-08-27 09:30 | 39.56 | 38.87
2019-08-27 10:00 | 41.35 | 40.64
2019-08-27 10:30 | 41.42 | 40.73
2019-08-27 11:00 | 41.44 | 40.8
2019-08-27 11:30 | 41.21 | 40.55
2019-08-27 12:00 | 41.63 | 40.98
2019-08-27 12:30 | 41.26 | 40.59
2019-08-27 13:00 | 41.38 | 40.72
2019-08-27 13:30 | 42.5 | 41.85
2019-08-27 14:00 | 43.84 | 43.19
2019-08-27 14:30 | 43.45 | 42.8
2019-08-27 15:00 | 43.72 | 43.09
2019-08-27 15:30 | 46.6 | 46.03
2019-08-27 16:00 | 47.4 | 46.84
2019-08-27 16:30 | 48.31 | 47.78
2019-08-27 17:00 | 49.45 | 48.96
2019-08-27 17:30 | 50.62 | 50.17
2019-08-27 18:00 | 51.57 | 51.15
2019-08-27 18:30 | 53.88 | 53.48
2019-08-27 19:00 | 54.26 | 53.86
2019-08-27 19:30 | 51.74 | 51.33
2019-08-27 20:00 | 49.12 | 48.69
2019-08-27 20:30 | 47.25 | 46.81
2019-08-27 21:00 | 44.42 | 43.96
2019-08-27 21:30 | 42.56 | 42.06
2019-08-27 22:00 | 41.01 | 40.45
2019-08-27 22:30 | 37.79 | 37.19
2019-08-27 23:00 | 35.98 | 35.36
2019-08-27 23:30 | 33.22 | 32.56
2019-08-28 | 32.03 | 31.36
2019-08-28 00:30 | 30.93 | 30.24
2019-08-28 01:00 | 30 | 29.29
2019-08-28 01:30 | 29.54 | 28.82
2019-08-28 02:00 | 28.71 | 27.98
2019-08-28 02:30 | 29.02 | 28.29
2019-08-28 03:00 | 28.9 | 28.12
2019-08-28 03:30 | 28.16 | 27.33
2019-08-28 04:00 | 27.82 | 26.98
2019-08-28 04:30 | 28.88 | 28.07
2019-08-28 05:00 | 30.27 | 29.49
2019-08-28 05:30 | 32.81 | 32.09
2019-08-28 06:00 | 34.97 | 34.28
2019-08-28 06:30 | 39.61 | 38.97
2019-08-28 07:00 | 43.48 | 42.88
2019-08-28 07:30 | 48.62 | 48.08
2019-08-28 08:00 | 49.81 | 49.29
2019-08-28 08:30 | 47.99 | 47.46
2019-08-28 09:00 | 45.95 | 45.25
2019-08-28 09:30 | 45.66 | 44.79
2019-08-28 10:00 | 44.43 | 43.43
2019-08-28 10:30 | 43.93 | 43.39
2019-08-28 11:00 | 45.09 | 44.56
2019-08-28 11:30 | 46 | 45.38
2019-08-28 12:00 | 45.79 | 45.08
2019-08-28 12:30 | 44.1 | 43.41
2019-08-28 13:00 | 43.75 | 43.13
2019-08-28 13:30 | 43.39 | 42.7
2019-08-28 14:00 | 45.24 | 44.54
2019-08-28 14:30 | 45.77 | 45.06
2019-08-28 15:00 | 45.66 | 45.05
2019-08-28 15:30 | 46.5 | 46.02
2019-08-28 16:00 | 47.43 | 47.03
2019-08-28 16:30 | 49.09 | 48.68
2019-08-28 17:00 | 49.13 | 48.69
2019-08-28 17:30 | 50.39 | 49.94
2019-08-28 18:00 | 52.29 | 51.84
2019-08-28 18:30 | 54.69 | 54.26
2019-08-28 19:00 | 53.83 | 53.4
2019-08-28 19:30 | 51.6 | 51.13
2019-08-28 20:00 | 48.98 | 48.48
2019-08-28 20:30 | 46.33 | 45.78
2019-08-28 21:00 | 44.88 | 44.3
2019-08-28 21:30 | 44.56 | 43.97
2019-08-28 22:00 | 40.64 | 40.06
2019-08-28 22:30 | 37.25 | 36.6
2019-08-28 23:00 | 35.61 | 34.91
2019-08-28 23:30 | 33.83 | 33.1
2019-08-29 | 32.3 | 31.52
2019-08-29 00:30 | 31.99 | 31.2
2019-08-29 01:00 | 30.74 | 29.9
2019-08-29 01:30 | 30.67 | 29.83
2019-08-29 02:00 | 29.1 | 28.2
2019-08-29 02:30 | 28.94 | 28.13
2019-08-29 03:00 | 28.44 | 27.62
2019-08-29 03:30 | 28.01 | 27.18
2019-08-29 04:00 | 28.44 | 27.62
2019-08-29 04:30 | 29.07 | 28.28
2019-08-29 05:00 | 30.85 | 30.1
2019-08-29 05:30 | 33.19 | 32.52
2019-08-29 06:00 | 35.43 | 34.82
2019-08-29 06:30 | 39.35 | 38.83
2019-08-29 07:00 | 43.88 | 43.43
2019-08-29 07:30 | 47.34 | 46.89
2019-08-29 08:00 | 48.01 | 47.57
2019-08-29 08:30 | 48.73 | 48.08
2019-08-29 09:00 | 48.36 | 47.49
2019-08-29 09:30 | 46.69 | 46.28
2019-08-29 10:00 | 46.33 | 45.92
2019-08-29 10:30 | 45.48 | 45.03
2019-08-29 11:00 | 44.29 | 43.76
2019-08-29 11:30 | 43.55 | 42.94
2019-08-29 12:00 | 43.43 | 42.73
2019-08-29 12:30 | 42.9 | 42.23
2019-08-29 13:00 | 41.32 | 40.69
2019-08-29 13:30 | 41.85 | 41.24
2019-08-29 14:00 | 42.04 | 41.45
2019-08-29 14:30 | 39.41 | 38.69
2019-08-29 15:00 | 20.61 | 18.3
2019-08-29 15:30 | 45.16 | 44.73
2019-08-29 16:00 | 46.38 | 45.97
2019-08-29 16:30 | 48.8 | 48.38
2019-08-29 17:00 | 50.25 | 49.82
2019-08-29 17:30 | 50.6 | 50.15
2019-08-29 18:00 | 52.59 | 52.15
2019-08-29 18:30 | 53.73 | 53.3
2019-08-29 19:00 | 53.81 | 53.37
2019-08-29 19:30 | 51.96 | 51.49
2019-08-29 20:00 | 50.3 | 49.81
2019-08-29 20:30 | 47.5 | 46.97
2019-08-29 21:00 | 46.42 | 45.87
2019-08-29 21:30 | 43.2 | 42.59
2019-08-29 22:00 | 40.26 | 39.61
2019-08-29 22:30 | 37.17 | 36.52
2019-08-29 23:00 | 36.23 | 35.55
2019-08-29 23:30 | 33.18 | 32.42
2019-08-30 | 32.81 | 32.04
2019-08-30 00:30 | 31.24 | 30.42
2019-08-30 01:00 | 29.78 | 28.9
2019-08-30 01:30 | 29.34 | 28.45
2019-08-30 02:00 | 28.72 | 27.81
2019-08-30 02:30 | 28.18 | 27.23
2019-08-30 03:00 | 27.37 | 26.49
2019-08-30 03:30 | 27.33 | 26.45
2019-08-30 04:00 | 27.5 | 26.63
2019-08-30 04:30 | 28.81 | 27.98
2019-08-30 05:00 | 29.1 | 28.29
2019-08-30 05:30 | 31.63 | 30.91
2019-08-30 06:00 | 34.97 | 34.34
2019-08-30 06:30 | 39.51 | 38.99
2019-08-30 07:00 | 43.33 | 42.88
2019-08-30 07:30 | 47.05 | 46.62
2019-08-30 08:00 | 49.08 | 48.68
2019-08-30 08:30 | 48.95 | 48.39
2019-08-30 09:00 | 49.41 | 48.65
2019-08-30 09:30 | 48.46 | 47.58
2019-08-30 10:00 | 46.92 | 46.1
2019-08-30 10:30 | 45.39 | 44.94
2019-08-30 11:00 | 45.57 | 44.99
2019-08-30 11:30 | 44.9 | 44.22
2019-08-30 12:00 | 44.28 | 43.6
2019-08-30 12:30 | 43.49 | 42.91
2019-08-30 13:00 | 43.12 | 42.59
2019-08-30 13:30 | 43.41 | 42.92
2019-08-30 14:00 | 43.69 | 43.25
2019-08-30 14:30 | 43.97 | 43.54
2019-08-30 15:00 | 45.53 | 45.11
2019-08-30 15:30 | 45.55 | 45.12
2019-08-30 16:00 | 48.24 | 47.83
2019-08-30 16:30 | 48.3 | 47.87
2019-08-30 17:00 | 50.12 | 49.68
2019-08-30 17:30 | 50.82 | 50.37
2019-08-30 18:00 | 49.7 | 49.22
2019-08-30 18:30 | 51.64 | 51.18
2019-08-30 19:00 | 52.19 | 51.74
2019-08-30 19:30 | 49.71 | 49.22
2019-08-30 20:00 | 47.49 | 46.96
2019-08-30 20:30 | 45.54 | 44.98
2019-08-30 21:00 | 44.37 | 43.78
2019-08-30 21:30 | 42.74 | 42.12
2019-08-30 22:00 | 40.34 | 39.72
2019-08-30 22:30 | 37.99 | 37.36
2019-08-30 23:00 | 36.9 | 36.31
2019-08-30 23:30 | 35.03 | 34.41
2019-08-31 | 33.53 | 32.87
2019-08-31 00:30 | 32.82 | 32.14
2019-08-31 01:00 | 31.83 | 31.12
2019-08-31 01:30 | 31.51 | 30.8
2019-08-31 02:00 | 30.88 | 30.14
2019-08-31 02:30 | 30.46 | 29.7
2019-08-31 03:00 | 29.73 | 28.95
2019-08-31 03:30 | 28.65 | 27.82
2019-08-31 04:00 | 28.58 | 27.75
2019-08-31 04:30 | 27.96 | 27.1
2019-08-31 05:00 | 28.01 | 27.16
2019-08-31 05:30 | 29.39 | 28.59
2019-08-31 06:00 | 31.85 | 31.12
2019-08-31 06:30 | 32.89 | 32.2
2019-08-31 07:00 | 33.48 | 32.8
2019-08-31 07:30 | 35.07 | 34.44
2019-08-31 08:00 | 34.97 | 34.36
2019-08-31 08:30 | 35.84 | 35.26
2019-08-31 09:00 | 35.41 | 34.84
2019-08-31 09:30 | 37.64 | 37.13
2019-08-31 10:00 | 34.95 | 34.4
2019-08-31 10:30 | 33.66 | 33.09
2019-08-31 11:00 | 32.83 | 32.18
2019-08-31 11:30 | 31.46 | 30.77
2019-08-31 12:00 | 31.2 | 30.51
2019-08-31 12:30 | 30.2 | 29.47
2019-08-31 13:00 | 30.41 | 29.68
2019-08-31 13:30 | 30.37 | 29.64
2019-08-31 14:00 | 30.36 | 29.62
2019-08-31 14:30 | 30.31 | 29.56
2019-08-31 15:00 | 30.76 | 30.02
2019-08-31 15:30 | 31.76 | 31.03
2019-08-31 16:00 | 33.84 | 33.15
2019-08-31 16:30 | 35.66 | 34.99
2019-08-31 17:00 | 38.15 | 37.52
2019-08-31 17:30 | 40.57 | 39.98
2019-08-31 18:00 | 43 | 42.43
2019-08-31 18:30 | 47.02 | 46.52
2019-08-31 19:00 | 46.64 | 46.14
2019-08-31 19:30 | 44.34 | 43.81
2019-08-31 20:00 | 43.01 | 42.45
2019-08-31 20:30 | 41.11 | 40.51
2019-08-31 21:00 | 39.02 | 38.39
2019-08-31 21:30 | 37.03 | 36.35
2019-08-31 22:00 | 36.05 | 35.36
2019-08-31 22:30 | 34.57 | 33.91
2019-08-31 23:00 | 32.66 | 31.95
2019-08-31 23:30 | 30.64 | 29.91
2019-09-01 | 29.25 | 28.51
2019-09-01 00:30 | 29.89 | 29.16
2019-09-01 01:00 | 28.89 | 28.13
2019-09-01 01:30 | 28.12 | 27.33
2019-09-01 02:00 | 27.18 | 26.38
2019-09-01 02:30 | 26.99 | 26.16
2019-09-01 03:00 | 26.87 | 26.02
2019-09-01 03:30 | 25.94 | 25.06
2019-09-01 04:00 | 26.26 | 25.4
2019-09-01 04:30 | 26.15 | 25.28
2019-09-01 05:00 | 26.39 | 25.53
2019-09-01 05:30 | 27.2 | 26.37
2019-09-01 06:00 | 27.82 | 27.02
2019-09-01 06:30 | 29.16 | 28.39
2019-09-01 07:00 | 29.98 | 29.24
2019-09-01 07:30 | 29.63 | 28.89
2019-09-01 08:00 | 29.72 | 29
2019-09-01 08:30 | 29.97 | 29.28
2019-09-01 09:00 | 29.85 | 29.17
2019-09-01 09:30 | 30.41 | 29.76
2019-09-01 10:00 | 29.39 | 28.72
2019-09-01 10:30 | 28.54 | 27.87
2019-09-01 11:00 | 26.94 | 26.23
2019-09-01 11:30 | 26.59 | 25.88
2019-09-01 12:00 | 26.66 | 25.95
2019-09-01 12:30 | 27.23 | 26.53
2019-09-01 13:00 | 25.72 | 24.99
2019-09-01 13:30 | 25.58 | 24.84
2019-09-01 14:00 | 25.75 | 25.01
2019-09-01 14:30 | 26.35 | 25.63
2019-09-01 15:00 | 28.26 | 27.58
2019-09-01 15:30 | 30.03 | 29.38
2019-09-01 16:00 | 33.3 | 32.71
2019-09-01 16:30 | 35.77 | 35.22
2019-09-01 17:00 | 37.34 | 36.81
2019-09-01 17:30 | 38.81 | 38.3
2019-09-01 18:00 | 43.18 | 42.73
2019-09-01 18:30 | 45.5 | 45.08
2019-09-01 19:00 | 46.91 | 46.51
2019-09-01 19:30 | 43.9 | 43.46
2019-09-01 20:00 | 42.43 | 41.98
2019-09-01 20:30 | 40.93 | 40.45
2019-09-01 21:00 | 39.83 | 39.32
2019-09-01 21:30 | 37.13 | 36.58
2019-09-01 22:00 | 35.44 | 34.85
2019-09-01 22:30 | 33.51 | 32.87
2019-09-01 23:00 | 31.18 | 30.48
2019-09-01 23:30 | 30.1 | 29.37
2019-09-02 | 28.64 | 27.87
2019-09-02 00:30 | 28.02 | 27.22
2019-09-02 01:00 | 27.36 | 26.54
2019-09-02 01:30 | 27.29 | 26.46
2019-09-02 02:00 | 26.44 | 25.58
2019-09-02 02:30 | 26.91 | 26.06
2019-09-02 03:00 | 26.16 | 25.29
2019-09-02 03:30 | 26.01 | 25.14
2019-09-02 04:00 | 26.37 | 25.51
2019-09-02 04:30 | 27.35 | 26.53
2019-09-02 05:00 | 28.3 | 27.51
2019-09-02 05:30 | 31.29 | 30.59
2019-09-02 06:00 | 34.64 | 34.04
2019-09-02 06:30 | 38.41 | 37.9
2019-09-02 07:00 | 41.58 | 41.08
2019-09-02 07:30 | 45.77 | 45.2
2019-09-02 08:00 | 45.5 | 44.99
2019-09-02 08:30 | 44.99 | 44.23
2019-09-02 09:00 | 43.8 | 42.7
2019-09-02 09:30 | 43.18 | 41.83
2019-09-02 10:00 | 42.51 | 41.25
2019-09-02 10:30 | 42.4 | 41.6
2019-09-02 11:00 | 42.88 | 41.9
2019-09-02 11:30 | 41.97 | 40.9
2019-09-02 12:00 | 42.21 | 41.05
2019-09-02 12:30 | 41.61 | 40.53
2019-09-02 13:00 | 41.19 | 40.17
2019-09-02 13:30 | 40.94 | 39.87
2019-09-02 14:00 | 42.46 | 41.29
2019-09-02 14:30 | 42.92 | 41.82
2019-09-02 15:00 | 43.82 | 42.84
2019-09-02 15:30 | 44.25 | 43.44
2019-09-02 16:00 | 46 | 45.39
2019-09-02 16:30 | 47.69 | 47.29
2019-09-02 17:00 | 48.55 | 48.14
2019-09-02 17:30 | 49.4 | 48.97
2019-09-02 18:00 | 50.5 | 50.06
2019-09-02 18:30 | 52.9 | 52.49
2019-09-02 19:00 | 53.67 | 53.26
2019-09-02 19:30 | 52.96 | 52.53
2019-09-02 20:00 | 48.81 | 48.33
2019-09-02 20:30 | 46.52 | 46.01
2019-09-02 21:00 | 44.16 | 43.63
2019-09-02 21:30 | 41.75 | 41.24
2019-09-02 22:00 | 40.64 | 40.09
2019-09-02 22:30 | 39.21 | 38.63
2019-09-02 23:00 | 36.76 | 36.13
2019-09-02 23:30 | 34.82 | 34.15
2019-09-03 | 32.61 | 31.89
2019-09-03 00:30 | 30.6 | 29.82
2019-09-03 01:00 | 31.24 | 30.47
2019-09-03 01:30 | 30.98 | 30.2
2019-09-03 02:00 | 28.93 | 28.13
2019-09-03 02:30 | 28.42 | 27.67
2019-09-03 03:00 | 27.97 | 27.2
2019-09-03 03:30 | 28.52 | 27.77
2019-09-03 04:00 | 28.58 | 27.82
2019-09-03 04:30 | 30.04 | 29.31
2019-09-03 05:00 | 30.49 | 29.78
2019-09-03 05:30 | 33.41 | 32.78
2019-09-03 06:00 | 35.84 | 35.27
2019-09-03 06:30 | 39.65 | 39.16
2019-09-03 07:00 | 43.43 | 42.88
2019-09-03 07:30 | 47 | 46.59
2019-09-03 08:00 | 46.51 | 46
2019-09-03 08:30 | 46.08 | 45.29
2019-09-03 09:00 | 43.67 | 42.64
2019-09-03 09:30 | 42.77 | 41.53
2019-09-03 10:00 | 40.47 | 38.96
2019-09-03 10:30 | 42.59 | 41.34
2019-09-03 11:00 | 44.11 | 43.14
2019-09-03 11:30 | 41.95 | 40.81
2019-09-03 12:00 | 41.96 | 41.1
2019-09-03 12:30 | 41.07 | 40.4
2019-09-03 13:00 | 41.16 | 40.46
2019-09-03 13:30 | 41.38 | 40.71
2019-09-03 14:00 | 41.86 | 41.2
2019-09-03 14:30 | 42.61 | 41.93
2019-09-03 15:00 | 44.77 | 44.12
2019-09-03 15:30 | 45.38 | 44.86
2019-09-03 16:00 | 46.94 | 46.52
2019-09-03 16:30 | 49.32 | 48.92
2019-09-03 17:00 | 50.82 | 50.4
2019-09-03 17:30 | 50.62 | 50.17
2019-09-03 18:00 | 51.17 | 50.77
2019-09-03 18:30 | 54.65 | 54.28
2019-09-03 19:00 | 54.47 | 54.09
2019-09-03 19:30 | 51.47 | 51.06
2019-09-03 20:00 | 49.73 | 49.29
2019-09-03 20:30 | 48.12 | 47.66
2019-09-03 21:00 | 44.6 | 44.09
2019-09-03 21:30 | 42.85 | 42.34
2019-09-03 22:00 | 40.74 | 40.23
2019-09-03 22:30 | 36.97 | 36.39
2019-09-03 23:00 | 35.7 | 35.09
2019-09-03 23:30 | 33.8 | 33.15
2019-09-04 | 31.99 | 31.29
2019-09-04 00:30 | 31.93 | 31.22
2019-09-04 01:00 | 30.53 | 29.79
2019-09-04 01:30 | 29.86 | 29.09
2019-09-04 02:00 | 29.51 | 28.73
2019-09-04 02:30 | 29.1 | 28.3
2019-09-04 03:00 | 28.65 | 27.83
2019-09-04 03:30 | 28.75 | 27.94
2019-09-04 04:00 | 28.82 | 28
2019-09-04 04:30 | 30.04 | 29.26
2019-09-04 05:00 | 31.22 | 30.47
2019-09-04 05:30 | 33.92 | 33.25
2019-09-04 06:00 | 36.64 | 36.04
2019-09-04 06:30 | 40.98 | 40.48
2019-09-04 07:00 | 44.65 | 44.22
2019-09-04 07:30 | 48 | 47.54
2019-09-04 08:00 | 46.96 | 46.54
2019-09-04 08:30 | 45.01 | 44.56
2019-09-04 09:00 | 42.6 | 42.07
2019-09-04 09:30 | 42.24 | 41.49
2019-09-04 10:00 | 41.27 | 40.35
2019-09-04 10:30 | 41.61 | 40.52
2019-09-04 11:00 | 41.72 | 41.12
2019-09-04 11:30 | 42.09 | 41.35
2019-09-04 12:00 | 42.56 | 41.9
2019-09-04 12:30 | 42.36 | 41.88
2019-09-04 13:00 | 42.61 | 42.13
2019-09-04 13:30 | 42.56 | 42.09
2019-09-04 14:00 | 44.11 | 43.66
2019-09-04 14:30 | 45.03 | 44.59
2019-09-04 15:00 | 46.51 | 46.08
2019-09-04 15:30 | 47.44 | 47.01
2019-09-04 16:00 | 48.91 | 48.48
2019-09-04 16:30 | 49.85 | 49.34
2019-09-04 17:00 | 50.71 | 50.14
2019-09-04 17:30 | 51.57 | 51.2
2019-09-04 18:00 | 52.21 | 51.82
2019-09-04 18:30 | 53.93 | 53.56
2019-09-04 19:00 | 54.93 | 54.56
2019-09-04 19:30 | 52.35 | 51.96
2019-09-04 20:00 | 49.51 | 49.08
2019-09-04 20:30 | 48.85 | 48.4
2019-09-04 21:00 | 45.98 | 45.49
2019-09-04 21:30 | 43.16 | 42.65
2019-09-04 22:00 | 40.6 | 40.09
2019-09-04 22:30 | 37.05 | 36.47
2019-09-04 23:00 | 36.12 | 35.52
2019-09-04 23:30 | 33.85 | 33.21
2019-09-05 | 32.39 | 31.7
2019-09-05 00:30 | 31.81 | 31.1
2019-09-05 01:00 | 30.44 | 29.69
2019-09-05 01:30 | 29.8 | 29.02
2019-09-05 02:00 | 29.39 | 28.6
2019-09-05 02:30 | 29.36 | 28.56
2019-09-05 03:00 | 28.59 | 27.76
2019-09-05 03:30 | 29.08 | 28.27
2019-09-05 04:00 | 29.54 | 28.75
2019-09-05 04:30 | 30.54 | 29.77
2019-09-05 05:00 | 31.88 | 31.16
2019-09-05 05:30 | 34.23 | 33.57
2019-09-05 06:00 | 36.49 | 35.89
2019-09-05 06:30 | 40.25 | 39.73
2019-09-05 07:00 | 44.34 | 43.91
2019-09-05 07:30 | 47.01 | 46.45
2019-09-05 08:00 | 46.34 | 45.92
2019-09-05 08:30 | 44.62 | 44.18
2019-09-05 09:00 | 42.11 | 41.44
2019-09-05 09:30 | 40.69 | 39.72
2019-09-05 10:00 | 41.41 | 40.72
2019-09-05 10:30 | 41.45 | 40.93
2019-09-05 11:00 | 42.55 | 41.89
2019-09-05 11:30 | 43.63 | 42.79
2019-09-05 12:00 | 44.09 | 43.16
2019-09-05 12:30 | 45.2 | 44.16
2019-09-05 13:00 | 45.43 | 44.44
2019-09-05 13:30 | 45.45 | 44.85
2019-09-05 14:00 | 46.09 | 45.67
2019-09-05 14:30 | 47.62 | 47.22
2019-09-05 15:00 | 48.73 | 48.34
2019-09-05 15:30 | 49.82 | 49.42
2019-09-05 16:00 | 51.08 | 50.69
2019-09-05 16:30 | 50.54 | 50.1
2019-09-05 17:00 | 52.62 | 51.93
2019-09-05 17:30 | 52.12 | 51.71
2019-09-05 18:00 | 53.77 | 53.41
2019-09-05 18:30 | 54.5 | 54.15
2019-09-05 19:00 | 54.28 | 53.92
2019-09-05 19:30 | 52.72 | 52.34
2019-09-05 20:00 | 50.05 | 49.63
2019-09-05 20:30 | 47.8 | 47.35
2019-09-05 21:00 | 46.02 | 45.54
2019-09-05 21:30 | 43.75 | 43.24
2019-09-05 22:00 | 40.83 | 40.28
2019-09-05 22:30 | 37.69 | 37.13
2019-09-05 23:00 | 38.87 | 38.33
2019-09-05 23:30 | 35.48 | 34.87
2019-09-06 | 33.16 | 32.49
2019-09-06 00:30 | 33.11 | 32.44
2019-09-06 01:00 | 31.18 | 30.44
2019-09-06 01:30 | 29.55 | 28.77
2019-09-06 02:00 | 28.83 | 28.02
2019-09-06 02:30 | 28.4 | 27.58
2019-09-06 03:00 | 27.84 | 26.99
2019-09-06 03:30 | 27.78 | 26.92
2019-09-06 04:00 | 27.38 | 27.34
2019-09-06 04:30 | 27.82 | 27.81
2019-09-06 05:00 | 29.5 | 29.5
2019-09-06 05:30 | 31.68 | 31.68
2019-09-06 06:00 | 34.97 | 34.95
2019-09-06 06:30 | 39.47 | 39.37
2019-09-06 07:00 | 43.16 | 42.89
2019-09-06 07:30 | 45.81 | 45.71
2019-09-06 08:00 | 46.53 | 46.31
2019-09-06 08:30 | 44.52 | 44.11
2019-09-06 09:00 | 44.05 | 43.44
2019-09-06 09:30 | 43.98 | 43.2
2019-09-06 10:00 | 43.52 | 43.04
2019-09-06 10:30 | 43.35 | 42.89
2019-09-06 11:00 | 42.91 | 42.32
2019-09-06 11:30 | 42.84 | 42.16
2019-09-06 12:00 | 42.95 | 42.21
2019-09-06 12:30 | 43.35 | 42.58
2019-09-06 13:00 | 44.08 | 43.37
2019-09-06 13:30 | 45.08 | 44.37
2019-09-06 14:00 | 44.81 | 44.12
2019-09-06 14:30 | 45.42 | 44.84
2019-09-06 15:00 | 45.41 | 44.87
2019-09-06 15:30 | 46.59 | 46.16
2019-09-06 16:00 | 47.9 | 47.6
2019-09-06 16:30 | 48.74 | 48.61
2019-09-06 17:00 | 49.17 | 49.13
2019-09-06 17:30 | 50.49 | 50.49
2019-09-06 18:00 | 50.51 | 50.48
2019-09-06 18:30 | 51.78 | 51.67
2019-09-06 19:00 | 52.08 | 51.99
2019-09-06 19:30 | 49.64 | 49.58
2019-09-06 20:00 | 47.64 | 47.6
2019-09-06 20:30 | 45.48 | 45.47
2019-09-06 21:00 | 44.07 | 44.07
2019-09-06 21:30 | 42.27 | 42.27
2019-09-06 22:00 | 40.68 | 40.67
2019-09-06 22:30 | 37.9 | 37.83
2019-09-06 23:00 | 36.88 | 36.82
2019-09-06 23:30 | 34.65 | 34.62
2019-09-07 | 32.95 | 32.94
2019-09-07 00:30 | 32.21 | 32.2
2019-09-07 01:00 | 30.77 | 30.77
2019-09-07 01:30 | 30.01 | 30.01
2019-09-07 02:00 | 29.92 | 29.92
2019-09-07 02:30 | 29.22 | 29.22
2019-09-07 03:00 | 28.91 | 28.91
2019-09-07 03:30 | 28.63 | 28.63
2019-09-07 04:00 | 28.72 | 28.72
2019-09-07 04:30 | 28.86 | 28.86
2019-09-07 05:00 | 29.34 | 29.34
2019-09-07 05:30 | 30.28 | 30.28
2019-09-07 06:00 | 32.06 | 32.06
2019-09-07 06:30 | 32.5 | 32.5
2019-09-07 07:00 | 34.22 | 34.21
2019-09-07 07:30 | 35.27 | 35.23
2019-09-07 08:00 | 35.54 | 35.45
2019-09-07 08:30 | 35.8 | 35.63
2019-09-07 09:00 | 35.28 | 34.97
2019-09-07 09:30 | 35.11 | 34.67
2019-09-07 10:00 | 34.58 | 33.98
2019-09-07 10:30 | 34.62 | 33.9
2019-09-07 11:00 | 34.09 | 33.2
2019-09-07 11:30 | 33.48 | 32.8
2019-09-07 12:00 | 32.54 | 32.34
2019-09-07 12:30 | 32 | 31.84
2019-09-07 13:00 | 29.65 | 29.5
2019-09-07 13:30 | 29.61 | 29.46
2019-09-07 14:00 | 30.46 | 30.32
2019-09-07 14:30 | 30.41 | 30.34
2019-09-07 15:00 | 30.84 | 30.79
2019-09-07 15:30 | 32.47 | 32.44
2019-09-07 16:00 | 34.68 | 34.66
2019-09-07 16:30 | 36.07 | 36.07
2019-09-07 17:00 | 39.72 | 39.72
2019-09-07 17:30 | 43.25 | 43.24
2019-09-07 18:00 | 45.93 | 45.93
2019-09-07 18:30 | 47.79 | 47.78
2019-09-07 19:00 | 47.62 | 47.61
2019-09-07 19:30 | 45.94 | 45.94
2019-09-07 20:00 | 44.38 | 44.38
2019-09-07 20:30 | 42.98 | 42.98
2019-09-07 21:00 | 40.86 | 40.84
2019-09-07 21:30 | 39.71 | 39.69
2019-09-07 22:00 | 38.84 | 38.74
2019-09-07 22:30 | 37.18 | 37.12
2019-09-07 23:00 | 35.52 | 35.48
2019-09-07 23:30 | 33.87 | 33.84
2019-09-08 | 32.81 | 32.79
2019-09-08 00:30 | 31.37 | 31.37
2019-09-08 01:00 | 30.4 | 30.4
2019-09-08 01:30 | 30.48 | 30.48
2019-09-08 02:00 | 29.41 | 29.4
2019-09-08 02:30 | 28.76 | 28.76
2019-09-08 03:00 | 28.79 | 28.78
2019-09-08 03:30 | 28.45 | 28.44
2019-09-08 04:00 | 28.09 | 28.08
2019-09-08 04:30 | 28.32 | 28.31
2019-09-08 05:00 | 28.53 | 28.52
2019-09-08 05:30 | 29.75 | 29.74
2019-09-08 06:00 | 30.94 | 30.93
2019-09-08 06:30 | 31.08 | 31.06
2019-09-08 07:00 | 31.03 | 31.01
2019-09-08 07:30 | 31.5 | 31.49
2019-09-08 08:00 | 31.19 | 31.19
2019-09-08 08:30 | 30.05 | 30.05
2019-09-08 09:00 | 29.58 | 29.57
2019-09-08 09:30 | 28.81 | 28.79
2019-09-08 10:00 | 28.57 | 28.5
2019-09-08 10:30 | 27.63 | 27.51
2019-09-08 11:00 | 27.47 | 27.32
2019-09-08 11:30 | 26.5 | 26.32
2019-09-08 12:00 | 26.72 | 26.48
2019-09-08 12:30 | 26.11 | 25.89
2019-09-08 13:00 | 25.96 | 25.76
2019-09-08 13:30 | 26.7 | 26.48
2019-09-08 14:00 | 26.69 | 26.46
2019-09-08 14:30 | 28.21 | 28.05
2019-09-08 15:00 | 28.84 | 28.69
2019-09-08 15:30 | 31.18 | 31.07
2019-09-08 16:00 | 33.48 | 33.37
2019-09-08 16:30 | 34.63 | 34.55
2019-09-08 17:00 | 36.84 | 36.78
2019-09-08 17:30 | 41.07 | 41
2019-09-08 18:00 | 44.28 | 44.19
2019-09-08 18:30 | 46.97 | 46.85
2019-09-08 19:00 | 47.03 | 46.93
2019-09-08 19:30 | 45.38 | 45.29
2019-09-08 20:00 | 44.08 | 43.99
2019-09-08 20:30 | 41.56 | 41.51
2019-09-08 21:00 | 40.09 | 40.06
2019-09-08 21:30 | 38.62 | 38.6
2019-09-08 22:00 | 37.04 | 37.02
2019-09-08 22:30 | 34.36 | 34.36
2019-09-08 23:00 | 32.71 | 32.71
2019-09-08 23:30 | 30.91 | 30.91
2019-09-09 | 29.78 | 29.77
2019-09-09 00:30 | 29.18 | 29.17
2019-09-09 01:00 | 28.68 | 28.66
2019-09-09 01:30 | 28.06 | 28.04
2019-09-09 02:00 | 27.77 | 27.74
2019-09-09 02:30 | 27.7 | 27.67
2019-09-09 03:00 | 27.64 | 27.61
2019-09-09 03:30 | 27.71 | 27.69
2019-09-09 04:00 | 28.14 | 28.12
2019-09-09 04:30 | 29.22 | 29.2
2019-09-09 05:00 | 30.78 | 30.78
2019-09-09 05:30 | 32.99 | 32.99
2019-09-09 06:00 | 35.46 | 35.45
2019-09-09 06:30 | 39.54 | 39.46
2019-09-09 07:00 | 43.75 | 43.47
2019-09-09 07:30 | 46.79 | 46.68
2019-09-09 08:00 | 46.04 | 45.85
2019-09-09 08:30 | 42.51 | 42.23
2019-09-09 09:00 | 41.06 | 40.67
2019-09-09 09:30 | 39.2 | 38.71
2019-09-09 10:00 | 38.38 | 37.74
2019-09-09 10:30 | 38.03 | 37.23
2019-09-09 11:00 | 37.99 | 37.06
2019-09-09 11:30 | 37.71 | 37.22
2019-09-09 12:00 | 38.4 | 37.96
2019-09-09 12:30 | 39.04 | 38.57
2019-09-09 13:00 | 38.7 | 38.24
2019-09-09 13:30 | 39.09 | 38.65
2019-09-09 14:00 | 39.69 | 39.25
2019-09-09 14:30 | 40.1 | 39.71
2019-09-09 15:00 | 41.38 | 41.02
2019-09-09 15:30 | 42.71 | 42.4
2019-09-09 16:00 | 44.73 | 44.52
2019-09-09 16:30 | 45.33 | 45.26
2019-09-09 17:00 | 46.72 | 46.71
2019-09-09 17:30 | 47.65 | 47.64
2019-09-09 18:00 | 49.27 | 49.24
2019-09-09 18:30 | 52 | 51.96
2019-09-09 19:00 | 52.72 | 52.68
2019-09-09 19:30 | 49.98 | 49.9
2019-09-09 20:00 | 47.65 | 47.52
2019-09-09 20:30 | 45.79 | 45.75
2019-09-09 21:00 | 43.21 | 43.21
2019-09-09 21:30 | 41.49 | 41.48
2019-09-09 22:00 | 39.05 | 39.03
2019-09-09 22:30 | 36.62 | 36.53
2019-09-09 23:00 | 34.97 | 34.92
2019-09-09 23:30 | 32.62 | 32.59
2019-09-10 | 31.11 | 31.08
2019-09-10 00:30 | 30.68 | 30.66
2019-09-10 01:00 | 29.74 | 29.74
2019-09-10 01:30 | 29.07 | 29.06
2019-09-10 02:00 | 28.29 | 28.29
2019-09-10 02:30 | 28.37 | 28.37
2019-09-10 03:00 | 27.68 | 27.68
2019-09-10 03:30 | 27.32 | 27.32
2019-09-10 04:00 | 27.24 | 27.23
2019-09-10 04:30 | 28.36 | 28.35
2019-09-10 05:00 | 29.49 | 29.48
2019-09-10 05:30 | 32.98 | 32.97
2019-09-10 06:00 | 35.53 | 35.49
2019-09-10 06:30 | 39.02 | 38.9
2019-09-10 07:00 | 42.91 | 42.62
2019-09-10 07:30 | 45.62 | 45.5
2019-09-10 08:00 | 45.31 | 45.1
2019-09-10 08:30 | 43.17 | 42.83
2019-09-10 09:00 | 40.89 | 40.47
2019-09-10 09:30 | 38.78 | 38.3
2019-09-10 10:00 | 37.56 | 36.98
2019-09-10 10:30 | 37.34 | 36.56
2019-09-10 11:00 | 37.12 | 36.18
2019-09-10 11:30 | 38.05 | 36.31
2019-09-10 12:00 | 38.52 | 36.41
2019-09-10 12:30 | 38.1 | 35.96
2019-09-10 13:00 | 37.84 | 35.67
2019-09-10 13:30 | 38.47 | 36.34
2019-09-10 14:00 | 39.39 | 37.24
2019-09-10 14:30 | 40.48 | 38.3
2019-09-10 15:00 | 41.72 | 39.59
2019-09-10 15:30 | 43.06 | 40.98
2019-09-10 16:00 | 45.47 | 43.48
2019-09-10 16:30 | 46.89 | 44.91
2019-09-10 17:00 | 48.43 | 46.49
2019-09-10 17:30 | 48.89 | 46.9
2019-09-10 18:00 | 50.58 | 48.63
2019-09-10 18:30 | 53.15 | 51.32
2019-09-10 19:00 | 54.08 | 52.29
2019-09-10 19:30 | 52.07 | 50.19
2019-09-10 20:00 | 50 | 48
2019-09-10 20:30 | 47.83 | 45.87
2019-09-10 21:00 | 46 | 43.95
2019-09-10 21:30 | 44.15 | 41.97
2019-09-10 22:00 | 41.71 | 39.35
2019-09-10 22:30 | 39.45 | 36.91
2019-09-10 23:00 | 38.08 | 35.43
2019-09-10 23:30 | 36.11 | 33.29
2019-09-11 | 34.65 | 31.67
2019-09-11 00:30 | 34.33 | 31.29
2019-09-11 01:00 | 33.01 | 29.82
2019-09-11 01:30 | 32.57 | 29.34
2019-09-11 02:00 | 32.02 | 28.7
2019-09-11 02:30 | 31.37 | 28.02
2019-09-11 03:00 | 32.08 | 28.97
2019-09-11 03:30 | 31.17 | 27.95
2019-09-11 04:00 | 30.7 | 27.45
2019-09-11 04:30 | 32.4 | 29.31
2019-09-11 05:00 | 32.66 | 29.62
2019-09-11 05:30 | 35.26 | 32.52
2019-09-11 06:00 | 39.49 | 37.11
2019-09-11 06:30 | 42.33 | 40.18
2019-09-11 07:00 | 46.05 | 44.16
2019-09-11 07:30 | 48.33 | 46.46
2019-09-11 08:00 | 49.56 | 47.8
2019-09-11 08:30 | 46.73 | 44.88
2019-09-11 09:00 | 42.72 | 40.71
2019-09-11 09:30 | 42.39 | 40.39
2019-09-11 10:00 | 40.62 | 38.54
2019-09-11 10:30 | 40.55 | 38.51
2019-09-11 11:00 | 40.68 | 38.69
2019-09-11 11:30 | 42.74 | 40.86
2019-09-11 12:00 | 45.2 | 43.29
2019-09-11 12:30 | 46.39 | 44.52
2019-09-11 13:00 | 44.75 | 42.81
2019-09-11 13:30 | 45.24 | 43.32
2019-09-11 14:00 | 43.25 | 41.24
2019-09-11 14:30 | 41.77 | 39.72
2019-09-11 15:00 | 43.38 | 41.37
2019-09-11 15:30 | 44.76 | 42.79
2019-09-11 16:00 | 46.13 | 44.21
2019-09-11 16:30 | 47.47 | 45.55
2019-09-11 17:00 | 48.3 | 46.4
2019-09-11 17:30 | 49.27 | 47.47
2019-09-11 18:00 | 50.98 | 49.21
2019-09-11 18:30 | 53.71 | 52.05
2019-09-11 19:00 | 54.21 | 52.58
2019-09-11 19:30 | 52.13 | 50.4
2019-09-11 20:00 | 50.38 | 48.56
2019-09-11 20:30 | 48.6 | 46.76
2019-09-11 21:00 | 46.64 | 44.79
2019-09-11 21:30 | 44.79 | 42.85
2019-09-11 22:00 | 41.87 | 39.74
2019-09-11 22:30 | 39.87 | 37.58
2019-09-11 23:00 | 38.71 | 36.34
2019-09-11 23:30 | 36.13 | 33.54
2019-09-12 | 34.68 | 31.95
2019-09-12 00:30 | 34 | 31.18
2019-09-12 01:00 | 33.11 | 30.2
2019-09-12 01:30 | 32.52 | 29.55
2019-09-12 02:00 | 31.97 | 28.92
2019-09-12 02:30 | 32.44 | 29.43
2019-09-12 03:00 | 31.75 | 28.64
2019-09-12 03:30 | 32.25 | 29.19
2019-09-12 04:00 | 33.08 | 30.11
2019-09-12 04:30 | 32.44 | 29.41
2019-09-12 05:00 | 33.94 | 31.08
2019-09-12 05:30 | 35.42 | 32.72
2019-09-12 06:00 | 38.43 | 36
2019-09-12 06:30 | 42.96 | 40.87
2019-09-12 07:00 | 45.39 | 43.51
2019-09-12 07:30 | 48.27 | 46.6
2019-09-12 08:00 | 49.56 | 47.99
2019-09-12 08:30 | 46.67 | 44.96
2019-09-12 09:00 | 46.48 | 44.42
2019-09-12 09:30 | 49.78 | 47.11
2019-09-12 10:00 | 50.4 | 46.67
2019-09-12 10:30 | 46.14 | 42.01
2019-09-12 11:00 | 45.12 | 40.75
2019-09-12 11:30 | 47.21 | 43.1
2019-09-12 12:00 | 46.96 | 42.83
2019-09-12 12:30 | 47.82 | 43.75
2019-09-12 13:00 | 45.09 | 40.74
2019-09-12 13:30 | 44.88 | 40.49
2019-09-12 14:00 | 46.56 | 42.36
2019-09-12 14:30 | 47.73 | 43.65
2019-09-12 15:00 | 47.66 | 43.55
2019-09-12 15:30 | 48.55 | 44.47
2019-09-12 16:00 | 50.24 | 46.27
2019-09-12 16:30 | 50.63 | 46.61
2019-09-12 17:00 | 51.62 | 47.58
2019-09-12 17:30 | 52.31 | 48.23
2019-09-12 18:00 | 54.73 | 50.82
2019-09-12 18:30 | 57.97 | 54.34
2019-09-12 19:00 | 59.1 | 55.56
2019-09-12 19:30 | 56.4 | 52.64
2019-09-12 20:00 | 54.54 | 50.59
2019-09-12 20:30 | 52.29 | 48.08
2019-09-12 21:00 | 50.84 | 46.44
2019-09-12 21:30 | 49.07 | 44.45
2019-09-12 22:00 | 46.04 | 41.1
2019-09-12 22:30 | 43.12 | 37.92
2019-09-12 23:00 | 42.42 | 37.12
2019-09-12 23:30 | 40.34 | 34.68
2019-09-13 | 39.12 | 33.18
2019-09-13 00:30 | 38.38 | 32.24
2019-09-13 01:00 | 36.91 | 30.42
2019-09-13 01:30 | 36.51 | 29.91
2019-09-13 02:00 | 36.79 | 30.26
2019-09-13 02:30 | 35.51 | 28.59
2019-09-13 03:00 | 35.36 | 28.4
2019-09-13 03:30 | 35.08 | 28.06
2019-09-13 04:00 | 35.34 | 28.37
2019-09-13 04:30 | 35.53 | 28.6
2019-09-13 05:00 | 36.76 | 30.15
2019-09-13 05:30 | 38.58 | 32.42
2019-09-13 06:00 | 40.68 | 35
2019-09-13 06:30 | 44.56 | 39.55
2019-09-13 07:00 | 48.49 | 44.11
2019-09-13 07:30 | 51.02 | 46.96
2019-09-13 08:00 | 49.7 | 45.56
2019-09-13 08:30 | 48.94 | 44.78
2019-09-13 09:00 | 47.7 | 43.48
2019-09-13 09:30 | 46.76 | 42.5
2019-09-13 10:00 | 46.14 | 41.76
2019-09-13 10:30 | 45.36 | 40.78
2019-09-13 11:00 | 45.07 | 40.5
2019-09-13 11:30 | 44.63 | 40.05
2019-09-13 12:00 | 44.88 | 40.33
2019-09-13 12:30 | 45.73 | 41.27
2019-09-13 13:00 | 45.42 | 40.91
2019-09-13 13:30 | 45.51 | 41.02
2019-09-13 14:00 | 45.89 | 41.46
2019-09-13 14:30 | 45.93 | 41.48
2019-09-13 15:00 | 46.71 | 42.3
2019-09-13 15:30 | 46.89 | 42.42
2019-09-13 16:00 | 48.48 | 44.11
2019-09-13 16:30 | 49.76 | 45.43
2019-09-13 17:00 | 51.39 | 47.18
2019-09-13 17:30 | 52.13 | 47.89
2019-09-13 18:00 | 49 | 44.46
2019-09-13 18:30 | 54.42 | 50.32
2019-09-13 19:00 | 54.97 | 50.93
2019-09-13 19:30 | 53.48 | 49.3
2019-09-13 20:00 | 51.8 | 47.46
2019-09-13 20:30 | 49.86 | 45.28
2019-09-13 21:00 | 48.45 | 43.84
2019-09-13 21:30 | 46.83 | 41.98
2019-09-13 22:00 | 44.94 | 39.8
2019-09-13 22:30 | 41.58 | 37.89
2019-09-13 23:00 | 37.9 | 37.34
2019-09-13 23:30 | 35.72 | 35.11
2019-09-14 | 34.73 | 34.1
2019-09-14 00:30 | 34.03 | 33.37
2019-09-14 01:00 | 32.85 | 32.16
2019-09-14 01:30 | 32.04 | 31.34
2019-09-14 02:00 | 31.37 | 30.65
2019-09-14 02:30 | 31.19 | 30.46
2019-09-14 03:00 | 30.87 | 30.13
2019-09-14 03:30 | 30.75 | 30.01
2019-09-14 04:00 | 30.31 | 29.54
2019-09-14 04:30 | 30.47 | 29.71
2019-09-14 05:00 | 31.59 | 30.86
2019-09-14 05:30 | 32.85 | 32.15
2019-09-14 06:00 | 34.07 | 33.4
2019-09-14 06:30 | 34.95 | 34.3
2019-09-14 07:00 | 36.04 | 35.42
2019-09-14 07:30 | 36.16 | 35.56
2019-09-14 08:00 | 35.66 | 35.07
2019-09-14 08:30 | 35.3 | 34.71
2019-09-14 09:00 | 35.16 | 34.6
2019-09-14 09:30 | 34.98 | 34.43
2019-09-14 10:00 | 34.25 | 33.66
2019-09-14 10:30 | 33.51 | 32.83
2019-09-14 11:00 | 33.72 | 32.93
2019-09-14 11:30 | 32.53 | 31.62
2019-09-14 12:00 | 31.62 | 30.79
2019-09-14 12:30 | 31.18 | 30.47
2019-09-14 13:00 | 30.63 | 29.97
2019-09-14 13:30 | 30.31 | 29.68
2019-09-14 14:00 | 30.23 | 29.6
2019-09-14 14:30 | 30.51 | 29.87
2019-09-14 15:00 | 32.07 | 31.46
2019-09-14 15:30 | 32.89 | 32.27
2019-09-14 16:00 | 34.67 | 34.08
2019-09-14 16:30 | 36.67 | 36.11
2019-09-14 17:00 | 38.82 | 38.29
2019-09-14 17:30 | 42.26 | 41.77
2019-09-14 18:00 | 44.13 | 43.66
2019-09-14 18:30 | 46.36 | 45.92
2019-09-14 19:00 | 46.78 | 46.34
2019-09-14 19:30 | 44.9 | 44.44
2019-09-14 20:00 | 43.62 | 43.14
2019-09-14 20:30 | 41.83 | 41.32
2019-09-14 21:00 | 40.57 | 40.04
2019-09-14 21:30 | 39.35 | 38.8
2019-09-14 22:00 | 38.02 | 37.45
2019-09-14 22:30 | 36.59 | 35.98
2019-09-14 23:00 | 35.89 | 35.26
2019-09-14 23:30 | 34.79 | 34.15
2019-09-15 | 33.19 | 32.5
2019-09-15 00:30 | 32.28 | 31.56
2019-09-15 01:00 | 30.85 | 30.1
2019-09-15 01:30 | 30.41 | 29.65
2019-09-15 02:00 | 30.21 | 29.44
2019-09-15 02:30 | 30.44 | 29.67
2019-09-15 03:00 | 29.9 | 29.11
2019-09-15 03:30 | 29.32 | 28.51
2019-09-15 04:00 | 29.24 | 28.42
2019-09-15 04:30 | 29.43 | 28.62
2019-09-15 05:00 | 30.13 | 29.35
2019-09-15 05:30 | 30.49 | 29.71
2019-09-15 06:00 | 31.34 | 30.58
2019-09-15 06:30 | 31.69 | 30.93
2019-09-15 07:00 | 31.29 | 30.52
2019-09-15 07:30 | 31.45 | 30.69
2019-09-15 08:00 | 30.39 | 29.62
2019-09-15 08:30 | 30.48 | 29.72
2019-09-15 09:00 | 29.82 | 29.06
2019-09-15 09:30 | 31.01 | 30.3
2019-09-15 10:00 | 31.06 | 30.38
2019-09-15 10:30 | 29.25 | 28.54
2019-09-15 11:00 | 29.22 | 28.52
2019-09-15 11:30 | 29.03 | 28.33
2019-09-15 12:00 | 28.63 | 27.92
2019-09-15 12:30 | 28.64 | 27.93
2019-09-15 13:00 | 29.14 | 28.46
2019-09-15 13:30 | 28.93 | 28.23
2019-09-15 14:00 | 30.04 | 29.37
2019-09-15 14:30 | 29.9 | 29.22
2019-09-15 15:00 | 31.57 | 30.93
2019-09-15 15:30 | 32.74 | 32.11
2019-09-15 16:00 | 34.82 | 34.22
2019-09-15 16:30 | 36.81 | 36.24
2019-09-15 17:00 | 38.58 | 38.03
2019-09-15 17:30 | 41.21 | 40.7
2019-09-15 18:00 | 44.45 | 43.98
2019-09-15 18:30 | 47.99 | 47.57
2019-09-15 19:00 | 49.21 | 48.8
2019-09-15 19:30 | 46.84 | 46.41
2019-09-15 20:00 | 45.72 | 45.27
2019-09-15 20:30 | 43.64 | 43.16
2019-09-15 21:00 | 41.25 | 40.73
2019-09-15 21:30 | 38.9 | 38.35
2019-09-15 22:00 | 37.45 | 36.87
2019-09-15 22:30 | 36.85 | 36.25
2019-09-15 23:00 | 34.36 | 33.71
2019-09-15 23:30 | 32.52 | 31.82
2019-09-16 | 31.29 | 30.56
2019-09-16 00:30 | 30.44 | 29.68
2019-09-16 01:00 | 30.38 | 29.62
2019-09-16 01:30 | 28.95 | 28.14
2019-09-16 02:00 | 28.64 | 27.82
2019-09-16 02:30 | 28.75 | 27.93
2019-09-16 03:00 | 28.54 | 27.72
2019-09-16 03:30 | 28.82 | 28
2019-09-16 04:00 | 29.03 | 28.22
2019-09-16 04:30 | 30.01 | 29.23
2019-09-16 05:00 | 31.15 | 30.41
2019-09-16 05:30 | 33.13 | 32.45
2019-09-16 06:00 | 35.41 | 34.79
2019-09-16 06:30 | 39.2 | 38.67
2019-09-16 07:00 | 42.28 | 41.82
2019-09-16 07:30 | 44.97 | 44.44
2019-09-16 08:00 | 44.93 | 44.16
2019-09-16 08:30 | 45.07 | 43.93
2019-09-16 09:00 | 44.56 | 42.96
2019-09-16 09:30 | 45.26 | 42.51
2019-09-16 10:00 | 46.2 | 41.85
2019-09-16 10:30 | 46.34 | 42
2019-09-16 11:00 | 45.47 | 41.08
2019-09-16 11:30 | 45.61 | 41.26
2019-09-16 12:00 | 45.71 | 41.41
2019-09-16 12:30 | 45.3 | 40.93
2019-09-16 13:00 | 45.34 | 40.95
2019-09-16 13:30 | 45.87 | 41.57
2019-09-16 14:00 | 44.83 | 40.45
2019-09-16 14:30 | 47.51 | 43.39
2019-09-16 15:00 | 48.13 | 44.04
2019-09-16 15:30 | 49.38 | 45.37
2019-09-16 16:00 | 51.02 | 47.1
2019-09-16 16:30 | 52.18 | 48.27
2019-09-16 17:00 | 52.39 | 48.4
2019-09-16 17:30 | 53.9 | 49.97
2019-09-16 18:00 | 55.32 | 51.45
2019-09-16 18:30 | 56.89 | 53.16
2019-09-16 19:00 | 57.96 | 54.31
2019-09-16 19:30 | 55.56 | 51.69
2019-09-16 20:00 | 52.86 | 48.7
2019-09-16 20:30 | 50.61 | 46.18
2019-09-16 21:00 | 48.72 | 44.07
2019-09-16 21:30 | 46.71 | 42.03
2019-09-16 22:00 | 44.72 | 39.75
2019-09-16 22:30 | 41.89 | 36.46
2019-09-16 23:00 | 40.76 | 35.09
2019-09-16 23:30 | 39.32 | 33.36
2019-09-17 | 37.99 | 31.73
2019-09-17 00:30 | 37.32 | 30.88
2019-09-17 01:00 | 37.14 | 30.69
2019-09-17 01:30 | 36.91 | 30.4
2019-09-17 02:00 | 35.81 | 29
2019-09-17 02:30 | 35.6 | 28.72
2019-09-17 03:00 | 34.9 | 27.85
2019-09-17 03:30 | 35.07 | 27.99
2019-09-17 04:00 | 35.55 | 28.62
2019-09-17 04:30 | 35.95 | 29.11
2019-09-17 05:00 | 37.14 | 30.62
2019-09-17 05:30 | 39.03 | 32.99
2019-09-17 06:00 | 41.76 | 36.27
2019-09-17 06:30 | 45 | 40.09
2019-09-17 07:00 | 47.51 | 43.03
2019-09-17 07:30 | 49.7 | 45.57
2019-09-17 08:00 | 49.45 | 45.42
2019-09-17 08:30 | 49.26 | 45.32
2019-09-17 09:00 | 47.82 | 43.84
2019-09-17 09:30 | 46.83 | 42.79
2019-09-17 10:00 | 45.03 | 40.81
2019-09-17 10:30 | 45.65 | 41.38
2019-09-17 11:00 | 46.74 | 42.58
2019-09-17 11:30 | 46.99 | 42.85
2019-09-17 12:00 | 46.8 | 42.66
2019-09-17 12:30 | 45.99 | 41.72
2019-09-17 13:00 | 46.76 | 42.58
2019-09-17 13:30 | 47.45 | 43.38
2019-09-17 14:00 | 47.41 | 43.33
2019-09-17 14:30 | 49.22 | 45.31
2019-09-17 15:00 | 50.14 | 46.31
2019-09-17 15:30 | 50.69 | 46.86
2019-09-17 16:00 | 53.06 | 49.37
2019-09-17 16:30 | 53.79 | 50.04
2019-09-17 17:00 | 54.15 | 50.33
2019-09-17 17:30 | 54.41 | 50.51
2019-09-17 18:00 | 55.46 | 51.59
2019-09-17 18:30 | 56.43 | 52.64
2019-09-17 19:00 | 57.54 | 53.83
2019-09-17 19:30 | 55.62 | 51.72
2019-09-17 20:00 | 53.99 | 49.92
2019-09-17 20:30 | 51.72 | 47.4
2019-09-17 21:00 | 49.79 | 45.22
2019-09-17 21:30 | 47.54 | 42.87
2019-09-17 22:00 | 45.39 | 40.49
2019-09-17 22:30 | 42.8 | 37.47
2019-09-17 23:00 | 42.22 | 36.76
2019-09-17 23:30 | 40.41 | 34.64
2019-09-18 | 39.54 | 33.59
2019-09-18 00:30 | 38.68 | 32.54
2019-09-18 01:00 | 36.55 | 31.22
2019-09-18 01:30 | 31.64 | 30.96
2019-09-18 02:00 | 30.83 | 30.13
2019-09-18 02:30 | 31.62 | 30.94
2019-09-18 03:00 | 30.74 | 30.02
2019-09-18 03:30 | 30.11 | 29.38
2019-09-18 04:00 | 30.5 | 29.77
2019-09-18 04:30 | 30.67 | 29.94
2019-09-18 05:00 | 31.72 | 31.03
2019-09-18 05:30 | 33.7 | 33.06
2019-09-18 06:00 | 35.99 | 35.41
2019-09-18 06:30 | 39.83 | 39.33
2019-09-18 07:00 | 43.36 | 42.87
2019-09-18 07:30 | 47.32 | 46.44
2019-09-18 08:00 | 48.06 | 46.72
2019-09-18 08:30 | 46.81 | 45.18
2019-09-18 09:00 | 46.11 | 44.1
2019-09-18 09:30 | 47.14 | 43.74
2019-09-18 10:00 | 47.04 | 42.93
2019-09-18 10:30 | 46.57 | 42.33
2019-09-18 11:00 | 47.45 | 43.35
2019-09-18 11:30 | 47.06 | 42.95
2019-09-18 12:00 | 48.24 | 44.28
2019-09-18 12:30 | 47.76 | 43.76
2019-09-18 13:00 | 47.69 | 43.66
2019-09-18 13:30 | 47.9 | 43.89
2019-09-18 14:00 | 49.33 | 45.47
2019-09-18 14:30 | 50.18 | 46.39
2019-09-18 15:00 | 51.38 | 47.68
2019-09-18 15:30 | 52.63 | 48.99
2019-09-18 16:00 | 53.57 | 49.93
2019-09-18 16:30 | 53.8 | 50.06
2019-09-18 17:00 | 55.6 | 51.95
2019-09-18 17:30 | 55.43 | 51.67
2019-09-18 18:00 | 56.72 | 53.01
2019-09-18 18:30 | 58.59 | 55.04
2019-09-18 19:00 | 58.73 | 55.17
2019-09-18 19:30 | 56.86 | 53.13
2019-09-18 20:00 | 54.95 | 51.02
2019-09-18 20:30 | 53.94 | 49.9
2019-09-18 21:00 | 51.94 | 47.66
2019-09-18 21:30 | 49.88 | 45.34
2019-09-18 22:00 | 47.07 | 42.25
2019-09-18 22:30 | 44.63 | 39.64
2019-09-18 23:00 | 43.48 | 38.3
2019-09-18 23:30 | 41.56 | 36.06
2019-09-19 | 40.01 | 34.21
2019-09-19 00:30 | 39.74 | 33.87
2019-09-19 01:00 | 38.17 | 31.97
2019-09-19 01:30 | 38.17 | 31.96
2019-09-19 02:00 | 37.25 | 30.8
2019-09-19 02:30 | 35.12 | 29.94
2019-09-19 03:00 | 30.3 | 29.58
2019-09-19 03:30 | 30.55 | 29.83
2019-09-19 04:00 | 30.81 | 30.09
2019-09-19 04:30 | 31.76 | 31.07
2019-09-19 05:00 | 32.54 | 31.87
2019-09-19 05:30 | 35.56 | 34.97
2019-09-19 06:00 | 37.44 | 36.88
2019-09-19 06:30 | 41.27 | 40.78
2019-09-19 07:00 | 43.88 | 43.35
2019-09-19 07:30 | 47.29 | 46.35
2019-09-19 08:00 | 47.82 | 46.49
2019-09-19 08:30 | 47.36 | 45.35
2019-09-19 09:00 | 48.71 | 46.52
2019-09-19 09:30 | 48.05 | 46.59
2019-09-19 10:00 | 48.09 | 46.57
2019-09-19 10:30 | 47.48 | 45.75
2019-09-19 11:00 | 46.17 | 44.17
2019-09-19 11:30 | 46.36 | 44.3
2019-09-19 12:00 | 48.41 | 46.32
2019-09-19 12:30 | 50.4 | 48.36
2019-09-19 13:00 | 49.6 | 47.61
2019-09-19 13:30 | 49.79 | 47.73
2019-09-19 14:00 | 51.36 | 49.32
2019-09-19 14:30 | 50.31 | 48.31
2019-09-19 15:00 | 49.62 | 47.58
2019-09-19 15:30 | 51.42 | 49.74
2019-09-19 16:00 | 52.79 | 51.45
2019-09-19 16:30 | 52.93 | 52.02
2019-09-19 17:00 | 53.14 | 52.45
2019-09-19 17:30 | 52 | 51.59
2019-09-19 18:00 | 53.85 | 53.5
2019-09-19 18:30 | 56.8 | 56.45
2019-09-19 19:00 | 56.96 | 56.62
2019-09-19 19:30 | 54.88 | 54.53
2019-09-19 20:00 | 52.91 | 52.53
2019-09-19 20:30 | 50.75 | 50.35
2019-09-19 21:00 | 48.94 | 48.52
2019-09-19 21:30 | 46.04 | 45.57
2019-09-19 22:00 | 43.44 | 42.93
2019-09-19 22:30 | 40.97 | 40.47
2019-09-19 23:00 | 38.64 | 38.12
2019-09-19 23:30 | 36.83 | 36.27
2019-09-20 | 35.5 | 34.92
2019-09-20 00:30 | 35.5 | 34.92
2019-09-20 01:00 | 33.54 | 32.9
2019-09-20 01:30 | 32.4 | 31.73
2019-09-20 02:00 | 31.86 | 31.18
2019-09-20 02:30 | 31.35 | 30.64
2019-09-20 03:00 | 30.59 | 29.86
2019-09-20 03:30 | 30.24 | 29.5
2019-09-20 04:00 | 30.55 | 29.81
2019-09-20 04:30 | 31.36 | 30.64
2019-09-20 05:00 | 32.74 | 32.07
2019-09-20 05:30 | 34.53 | 33.91
2019-09-20 06:00 | 37.04 | 36.47
2019-09-20 06:30 | 40.54 | 40.06
2019-09-20 07:00 | 44.29 | 43.63
2019-09-20 07:30 | 49.23 | 48.07
2019-09-20 08:00 | 50.22 | 48.68
2019-09-20 08:30 | 50.74 | 48.74
2019-09-20 09:00 | 49.41 | 47.64
2019-09-20 09:30 | 50.68 | 49.46
2019-09-20 10:00 | 49.94 | 48.52
2019-09-20 10:30 | 49.28 | 47.64
2019-09-20 11:00 | 49.24 | 47.38
2019-09-20 11:30 | 48.77 | 46.75
2019-09-20 12:00 | 47.23 | 45.19
2019-09-20 12:30 | 46.4 | 44.36
2019-09-20 13:00 | 46.2 | 44.23
2019-09-20 13:30 | 45.85 | 44.06
2019-09-20 14:00 | 46.22 | 44.58
2019-09-20 14:30 | 46.1 | 44.56
2019-09-20 15:00 | 45.54 | 44.09
2019-09-20 15:30 | 46.41 | 45.34
2019-09-20 16:00 | 48.48 | 47.59
2019-09-20 16:30 | 48.74 | 48.09
2019-09-20 17:00 | 49.49 | 49.05
2019-09-20 17:30 | 49.63 | 49.23
2019-09-20 18:00 | 50.47 | 50.06
2019-09-20 18:30 | 52.53 | 52.13
2019-09-20 19:00 | 53.93 | 53.55
2019-09-20 19:30 | 52.47 | 52.08
2019-09-20 20:00 | 49.5 | 49.08
2019-09-20 20:30 | 46.82 | 46.36
2019-09-20 21:00 | 45.49 | 45.01
2019-09-20 21:30 | 44.58 | 44.07
2019-09-20 22:00 | 42.25 | 41.71
2019-09-20 22:30 | 39.91 | 39.36
2019-09-20 23:00 | 39.39 | 38.87
2019-09-20 23:30 | 36.51 | 35.93
2019-09-21 | 35.21 | 34.6
2019-09-21 00:30 | 34.4 | 33.77
2019-09-21 01:00 | 33.21 | 32.56
2019-09-21 01:30 | 32.83 | 32.17
2019-09-21 02:00 | 32.17 | 31.49
2019-09-21 02:30 | 31.58 | 30.88
2019-09-21 03:00 | 32.24 | 31.54
2019-09-21 03:30 | 30.62 | 29.89
2019-09-21 04:00 | 30.71 | 29.98
2019-09-21 04:30 | 31.23 | 30.52
2019-09-21 05:00 | 31.67 | 30.97
2019-09-21 05:30 | 33.04 | 32.39
2019-09-21 06:00 | 33.43 | 32.77
2019-09-21 06:30 | 35.46 | 34.84
2019-09-21 07:00 | 35.68 | 35.09
2019-09-21 07:30 | 36.61 | 36.06
2019-09-21 08:00 | 37.44 | 36.92
2019-09-21 08:30 | 38.7 | 38.21
2019-09-21 09:00 | 38.7 | 38.13
2019-09-21 09:30 | 37.73 | 36.97
2019-09-21 10:00 | 37.49 | 36.56
2019-09-21 10:30 | 36.17 | 35.12
2019-09-21 11:00 | 35.45 | 34.73
2019-09-21 11:30 | 36.33 | 35.78
2019-09-21 12:00 | 35.34 | 34.77
2019-09-21 12:30 | 33.09 | 32.46
2019-09-21 13:00 | 32.78 | 32.13
2019-09-21 13:30 | 32.18 | 31.52
2019-09-21 14:00 | 32.63 | 31.96
2019-09-21 14:30 | 35.49 | 34.87
2019-09-21 15:00 | 34.05 | 33.4
2019-09-21 15:30 | 35.76 | 35.14
2019-09-21 16:00 | 38.14 | 37.55
2019-09-21 16:30 | 38.94 | 38.36
2019-09-21 17:00 | 41.51 | 40.96
2019-09-21 17:30 | 43.13 | 42.6
2019-09-21 18:00 | 45.7 | 45.19
2019-09-21 18:30 | 47.23 | 46.75
2019-09-21 19:00 | 47.23 | 46.75
2019-09-21 19:30 | 45.85 | 45.35
2019-09-21 20:00 | 44.54 | 44.02
2019-09-21 20:30 | 43.35 | 42.81
2019-09-21 21:00 | 41.84 | 41.27
2019-09-21 21:30 | 39.61 | 39
2019-09-21 22:00 | 37.92 | 37.27
2019-09-21 22:30 | 36.86 | 36.25
2019-09-21 23:00 | 34.78 | 34.16
2019-09-21 23:30 | 33.61 | 32.97
2019-09-22 | 32.29 | 31.61
2019-09-22 00:30 | 31.37 | 30.66
2019-09-22 01:00 | 30.67 | 29.93
2019-09-22 01:30 | 29.88 | 29.12
2019-09-22 02:00 | 29.4 | 28.63
2019-09-22 02:30 | 29 | 28.21
2019-09-22 03:00 | 28.52 | 27.71
2019-09-22 03:30 | 28.49 | 27.67
2019-09-22 04:00 | 28.5 | 27.67
2019-09-22 04:30 | 28.71 | 27.88
2019-09-22 05:00 | 28.57 | 27.71
2019-09-22 05:30 | 29.09 | 28.27
2019-09-22 06:00 | 29.32 | 28.51
2019-09-22 06:30 | 30.34 | 29.56
2019-09-22 07:00 | 30.51 | 29.73
2019-09-22 07:30 | 32.09 | 31.34
2019-09-22 08:00 | 32.9 | 32.17
2019-09-22 08:30 | 34.44 | 33.73
2019-09-22 09:00 | 34.74 | 34.03
2019-09-22 09:30 | 35.62 | 34.93
2019-09-22 10:00 | 32.8 | 32.02
2019-09-22 10:30 | 31.29 | 30.46
2019-09-22 11:00 | 31.29 | 30.46
2019-09-22 11:30 | 31.59 | 30.74
2019-09-22 12:00 | 31.37 | 30.51
2019-09-22 12:30 | 31.49 | 30.63
2019-09-22 13:00 | 29.79 | 28.87
2019-09-22 13:30 | 31.46 | 30.61
2019-09-22 14:00 | 30.71 | 29.83
2019-09-22 14:30 | 31.95 | 31.11
2019-09-22 15:00 | 31.89 | 31.06
2019-09-22 15:30 | 33.26 | 32.47
2019-09-22 16:00 | 35.24 | 34.49
2019-09-22 16:30 | 38.24 | 37.57
2019-09-22 17:00 | 38.57 | 37.91
2019-09-22 17:30 | 41.77 | 41.18
2019-09-22 18:00 | 44.78 | 44.22
2019-09-22 18:30 | 47.41 | 46.97
2019-09-22 19:00 | 47.39 | 46.98
2019-09-22 19:30 | 45.79 | 45.36
2019-09-22 20:00 | 44.73 | 44.29
2019-09-22 20:30 | 42.97 | 42.5
2019-09-22 21:00 | 41.21 | 40.72
2019-09-22 21:30 | 39.82 | 39.29
2019-09-22 22:00 | 38.8 | 38.25
2019-09-22 22:30 | 36.19 | 35.58
2019-09-22 23:00 | 34.23 | 33.57
2019-09-22 23:30 | 32.54 | 31.84
2019-09-23 | 31.31 | 30.58
2019-09-23 00:30 | 30.78 | 30.04
2019-09-23 01:00 | 29.69 | 28.92
2019-09-23 01:30 | 29.11 | 28.33
2019-09-23 02:00 | 28.9 | 28.11
2019-09-23 02:30 | 29.28 | 28.49
2019-09-23 03:00 | 29.06 | 28.26
2019-09-23 03:30 | 28.85 | 28.05
2019-09-23 04:00 | 28.7 | 27.9
2019-09-23 04:30 | 29.74 | 28.98
2019-09-23 05:00 | 30.66 | 29.93
2019-09-23 05:30 | 32.55 | 31.87
2019-09-23 06:00 | 34.14 | 33.5
2019-09-23 06:30 | 38.3 | 37.76
2019-09-23 07:00 | 40.33 | 39.84
2019-09-23 07:30 | 44.29 | 43.47
2019-09-23 08:00 | 45.53 | 44.3
2019-09-23 08:30 | 46.91 | 45.2
2019-09-23 09:00 | 47.55 | 45.54
2019-09-23 09:30 | 47.7 | 46.43
2019-09-23 10:00 | 46.9 | 45.54
2019-09-23 10:30 | 47.44 | 45.81
2019-09-23 11:00 | 48.63 | 46.79
2019-09-23 11:30 | 50.16 | 48.14
2019-09-23 12:00 | 49.21 | 47.07
2019-09-23 12:30 | 48.24 | 46.01
2019-09-23 13:00 | 47.67 | 45.52
2019-09-23 13:30 | 47.6 | 45.49
2019-09-23 14:00 | 48.16 | 46.1
2019-09-23 14:30 | 48.8 | 46.76
2019-09-23 15:00 | 49.52 | 47.66
2019-09-23 15:30 | 50.76 | 49.11
2019-09-23 16:00 | 51.39 | 50.01
2019-09-23 16:30 | 52.34 | 51.36
2019-09-23 17:00 | 52.33 | 51.68
2019-09-23 17:30 | 51.5 | 51.12
2019-09-23 18:00 | 51.94 | 51.56
2019-09-23 18:30 | 53.76 | 53.39
2019-09-23 19:00 | 54.16 | 53.79
2019-09-23 19:30 | 51.86 | 51.46
2019-09-23 20:00 | 49.76 | 49.34
2019-09-23 20:30 | 47.01 | 46.55
2019-09-23 21:00 | 45.5 | 45.01
2019-09-23 21:30 | 43.47 | 42.95
2019-09-23 22:00 | 41.79 | 41.24
2019-09-23 22:30 | 38.46 | 37.91
2019-09-23 23:00 | 37.57 | 37.01
2019-09-23 23:30 | 35.41 | 34.81
2019-09-24 | 34.25 | 33.62
2019-09-24 00:30 | 34 | 33.36
2019-09-24 01:00 | 32.15 | 31.46
2019-09-24 01:30 | 31.8 | 31.09
2019-09-24 02:00 | 31.19 | 30.47
2019-09-24 02:30 | 30.58 | 29.84
2019-09-24 03:00 | 30.62 | 29.88
2019-09-24 03:30 | 29.98 | 29.21
2019-09-24 04:00 | 30.02 | 29.26
2019-09-24 04:30 | 31.04 | 30.31
2019-09-24 05:00 | 32.31 | 31.61
2019-09-24 05:30 | 33.69 | 33.38
2019-09-24 06:00 | 34.99 | 34.9
2019-09-24 06:30 | 38.08 | 37.86
2019-09-24 07:00 | 40.88 | 40.41
2019-09-24 07:30 | 45.34 | 44.33
2019-09-24 08:00 | 46.85 | 45.3
2019-09-24 08:30 | 47.84 | 45.73
2019-09-24 09:00 | 48.62 | 46.86
2019-09-24 09:30 | 47.44 | 45.79
2019-09-24 10:00 | 46.48 | 44.71
2019-09-24 10:30 | 46.19 | 44.22
2019-09-24 11:00 | 46.87 | 44.65
2019-09-24 11:30 | 46.75 | 44.44
2019-09-24 12:00 | 47.03 | 44.73
2019-09-24 12:30 | 47.51 | 45.18
2019-09-24 13:00 | 47.02 | 44.67
2019-09-24 13:30 | 47.67 | 45.38
2019-09-24 14:00 | 49.07 | 46.88
2019-09-24 14:30 | 49.04 | 46.75
2019-09-24 15:00 | 50.71 | 48.53
2019-09-24 15:30 | 51.21 | 49.22
2019-09-24 16:00 | 55.33 | 53.84
2019-09-24 16:30 | 54.02 | 52.5
2019-09-24 17:00 | 52.78 | 51.16
2019-09-24 17:30 | 52.78 | 51.1
2019-09-24 18:00 | 54.29 | 52.64
2019-09-24 18:30 | 56.61 | 55.04
2019-09-24 19:00 | 57.17 | 55.63
2019-09-24 19:30 | 54.22 | 52.56
2019-09-24 20:00 | 51.72 | 49.95
2019-09-24 20:30 | 49.48 | 47.59
2019-09-24 21:00 | 47.44 | 45.43
2019-09-24 21:30 | 46.16 | 44.08
2019-09-24 22:00 | 44.79 | 42.61
2019-09-24 22:30 | 41.94 | 39.67
2019-09-24 23:00 | 40.48 | 38.19
2019-09-24 23:30 | 38.44 | 35.99
2019-09-25 | 36.6 | 33.98
2019-09-25 00:30 | 35.88 | 33.18
2019-09-25 01:00 | 35.01 | 32.22
2019-09-25 01:30 | 34.91 | 32.09
2019-09-25 02:00 | 31.49 | 30.25
2019-09-25 02:30 | 29.55 | 29.54
2019-09-25 03:00 | 29.64 | 29.63
2019-09-25 03:30 | 29.73 | 29.72
2019-09-25 04:00 | 29.66 | 29.66
2019-09-25 04:30 | 30.51 | 30.5
2019-09-25 05:00 | 30.8 | 30.79
2019-09-25 05:30 | 34.12 | 34.06
2019-09-25 06:00 | 36.41 | 36.32
2019-09-25 06:30 | 39.21 | 38.94
2019-09-25 07:00 | 42.93 | 42.34
2019-09-25 07:30 | 47.9 | 46.82
2019-09-25 08:00 | 48.82 | 47.33
2019-09-25 08:30 | 51.59 | 49.58
2019-09-25 09:00 | 51.63 | 50.19
2019-09-25 09:30 | 51.74 | 50.22
2019-09-25 10:00 | 50.65 | 48.94
2019-09-25 10:30 | 50.75 | 48.87
2019-09-25 11:00 | 50.15 | 47.95
2019-09-25 11:30 | 49.8 | 47.42
2019-09-25 12:00 | 48.66 | 46.37
2019-09-25 12:30 | 47.62 | 45.43
2019-09-25 13:00 | 47.91 | 45.91
2019-09-25 13:30 | 48.49 | 46.47
2019-09-25 14:00 | 48.73 | 46.64
2019-09-25 14:30 | 51.24 | 49.27
2019-09-25 15:00 | 51.11 | 49.15
2019-09-25 15:30 | 52.64 | 50.9
2019-09-25 16:00 | 52.67 | 51.25
2019-09-25 16:30 | 54.21 | 53.22
2019-09-25 17:00 | 52.84 | 52.08
2019-09-25 17:30 | 52.02 | 51.6
2019-09-25 18:00 | 52.15 | 51.77
2019-09-25 18:30 | 54.49 | 54.13
2019-09-25 19:00 | 56.32 | 55.97
2019-09-25 19:30 | 53.04 | 52.67
2019-09-25 20:00 | 50.81 | 50.41
2019-09-25 20:30 | 49 | 48.58
2019-09-25 21:00 | 48.11 | 47.67
2019-09-25 21:30 | 45.99 | 45.52
2019-09-25 22:00 | 43.28 | 42.77
2019-09-25 22:30 | 40.25 | 39.72
2019-09-25 23:00 | 38.89 | 38.37
2019-09-25 23:30 | 37.23 | 36.68
2019-09-26 | 35.29 | 34.7
2019-09-26 00:30 | 34.21 | 33.59
2019-09-26 01:00 | 33.69 | 33.05
2019-09-26 01:30 | 32.65 | 31.99
2019-09-26 02:00 | 32.72 | 32.06
2019-09-26 02:30 | 31.85 | 31.16
2019-09-26 03:00 | 31.56 | 30.86
2019-09-26 03:30 | 31.99 | 31.29
2019-09-26 04:00 | 31.2 | 30.48
2019-09-26 04:30 | 31.78 | 31.08
2019-09-26 05:00 | 32.98 | 32.32
2019-09-26 05:30 | 34.82 | 34.2
2019-09-26 06:00 | 36.8 | 36.23
2019-09-26 06:30 | 41.03 | 40.55
2019-09-26 07:00 | 43.82 | 43.14
2019-09-26 07:30 | 48.94 | 47.61
2019-09-26 08:00 | 51.98 | 50.12
2019-09-26 08:30 | 52.71 | 50.39
2019-09-26 09:00 | 52.5 | 50.91
2019-09-26 09:30 | 51.48 | 49.73
2019-09-26 10:00 | 51.6 | 49.76
2019-09-26 10:30 | 51.11 | 49.05
2019-09-26 11:00 | 51.49 | 49.01
2019-09-26 11:30 | 54.24 | 51.65
2019-09-26 12:00 | 53.8 | 51.11
2019-09-26 12:30 | 53.07 | 50.49
2019-09-26 13:00 | 51.73 | 49.3
2019-09-26 13:30 | 51.02 | 48.67
2019-09-26 14:00 | 51.26 | 48.95
2019-09-26 14:30 | 53.62 | 51.26
2019-09-26 15:00 | 55.14 | 52.87
2019-09-26 15:30 | 55.61 | 53.63
2019-09-26 16:00 | 54.96 | 53.3
2019-09-26 16:30 | 54.94 | 53.68
2019-09-26 17:00 | 53.76 | 52.94
2019-09-26 17:30 | 53.3 | 52.8
2019-09-26 18:00 | 55.18 | 54.82
2019-09-26 18:30 | 56.75 | 56.41
2019-09-26 19:00 | 56.73 | 56.4
2019-09-26 19:30 | 55.1 | 54.75
2019-09-26 20:00 | 52.49 | 52.11
2019-09-26 20:30 | 50.97 | 50.57
2019-09-26 21:00 | 49.24 | 48.82
2019-09-26 21:30 | 46.98 | 46.53
2019-09-26 22:00 | 44.48 | 43.99
2019-09-26 22:30 | 41.8 | 41.31
2019-09-26 23:00 | 40.29 | 39.8
2019-09-26 23:30 | 38.98 | 38.47
2019-09-27 | 36.81 | 36.26
2019-09-27 00:30 | 35.4 | 34.82
2019-09-27 01:00 | 34.79 | 34.2
2019-09-27 01:30 | 34.24 | 33.63
2019-09-27 02:00 | 33.64 | 33.01
2019-09-27 02:30 | 32.84 | 32.2
2019-09-27 03:00 | 32.6 | 31.94
2019-09-27 03:30 | 32.49 | 31.83
2019-09-27 04:00 | 32.62 | 31.96
2019-09-27 04:30 | 33.11 | 32.46
2019-09-27 05:00 | 34.11 | 33.48
2019-09-27 05:30 | 36.2 | 35.63
2019-09-27 06:00 | 39.48 | 38.97
2019-09-27 06:30 | 42.31 | 41.78
2019-09-27 07:00 | 45.79 | 44.96
2019-09-27 07:30 | 49.09 | 47.79
2019-09-27 08:00 | 52.45 | 50.63
2019-09-27 08:30 | 56.23 | 54.16
2019-09-27 09:00 | 55.57 | 53.59
2019-09-27 09:30 | 54.01 | 52.5
2019-09-27 10:00 | 53.51 | 51.9
2019-09-27 10:30 | 47.83 | 45.57
2019-09-27 11:00 | 50.86 | 48.69
2019-09-27 11:30 | 51.72 | 49.25
2019-09-27 12:00 | 50.34 | 47.85
2019-09-27 12:30 | 49.59 | 47.13
2019-09-27 13:00 | 49 | 46.79
2019-09-27 13:30 | 48.83 | 46.64
2019-09-27 14:00 | 49.86 | 47.88
2019-09-27 14:30 | 49.76 | 47.95
2019-09-27 15:00 | 49.74 | 48.07
2019-09-27 15:30 | 49.85 | 48.43
2019-09-27 16:00 | 49.81 | 48.76
2019-09-27 16:30 | 50.46 | 49.73
2019-09-27 17:00 | 51.3 | 50.81
2019-09-27 17:30 | 51.46 | 51.09
2019-09-27 18:00 | 51.57 | 51.18
2019-09-27 18:30 | 52.85 | 52.47
2019-09-27 19:00 | 54.12 | 53.76
2019-09-27 19:30 | 52.38 | 51.99
2019-09-27 20:00 | 50.23 | 49.82
2019-09-27 20:30 | 47.76 | 47.31
2019-09-27 21:00 | 46.45 | 45.98
2019-09-27 21:30 | 44.61 | 44.11
2019-09-27 22:00 | 42.91 | 42.38
2019-09-27 22:30 | 41.06 | 40.54
2019-09-27 23:00 | 39.49 | 38.97
2019-09-27 23:30 | 37.39 | 36.83
2019-09-28 | 35.51 | 34.9
2019-09-28 00:30 | 34.56 | 33.93
2019-09-28 01:00 | 33.96 | 33.31
2019-09-28 01:30 | 32.9 | 32.23
2019-09-28 02:00 | 32.72 | 32.04
2019-09-28 02:30 | 32.19 | 31.5
2019-09-28 03:00 | 31.79 | 31.08
2019-09-28 03:30 | 31.4 | 30.66
2019-09-28 04:00 | 31.42 | 30.68
2019-09-28 04:30 | 31.56 | 30.82
2019-09-28 05:00 | 32.44 | 31.73
2019-09-28 05:30 | 33.25 | 32.57
2019-09-28 06:00 | 33.45 | 32.76
2019-09-28 06:30 | 34.77 | 34.12
2019-09-28 07:00 | 35.01 | 34.38
2019-09-28 07:30 | 35.53 | 34.93
2019-09-28 08:00 | 35.32 | 34.73
2019-09-28 08:30 | 35.81 | 35.25
2019-09-28 09:00 | 38.1 | 37.55
2019-09-28 09:30 | 39.05 | 38.46
2019-09-28 10:00 | 37.26 | 36.57
2019-09-28 10:30 | 35.92 | 35.06
2019-09-28 11:00 | 35.02 | 34.07
2019-09-28 11:30 | 34 | 33.4
2019-09-28 12:00 | 33.28 | 32.67
2019-09-28 12:30 | 23.51 | 22.44
2019-09-28 13:00 | 32 | 31.34
2019-09-28 13:30 | 32.26 | 31.61
2019-09-28 14:00 | 32.62 | 31.96
2019-09-28 14:30 | 32.59 | 31.91
2019-09-28 15:00 | 33.81 | 33.16
2019-09-28 15:30 | 35.13 | 34.49
2019-09-28 16:00 | 35.55 | 34.9
2019-09-28 16:30 | 36.63 | 35.98
2019-09-28 17:00 | 39.19 | 38.58
2019-09-28 17:30 | 41.67 | 41.1
2019-09-28 18:00 | 43.93 | 43.39
2019-09-28 18:30 | 46.04 | 45.53
2019-09-28 19:00 | 46.69 | 46.2
2019-09-28 19:30 | 44.86 | 44.34
2019-09-28 20:00 | 43.45 | 42.91
2019-09-28 20:30 | 41.63 | 41.05
2019-09-28 21:00 | 40.53 | 39.93
2019-09-28 21:30 | 39.35 | 38.72
2019-09-28 22:00 | 38.39 | 37.74
2019-09-28 22:30 | 35.97 | 35.32
2019-09-28 23:00 | 34.62 | 33.98
2019-09-28 23:30 | 33.62 | 32.95
2019-09-29 | 32.52 | 31.81
2019-09-29 00:30 | 31.94 | 31.22
2019-09-29 01:00 | 30.75 | 29.98
2019-09-29 01:30 | 30.37 | 29.59
2019-09-29 02:00 | 29.14 | 28.35
2019-09-29 02:30 | 28.84 | 28.03
2019-09-29 03:00 | 29.22 | 28.43
2019-09-29 03:30 | 28.48 | 27.64
2019-09-29 04:00 | 28.34 | 27.49
2019-09-29 04:30 | 28.54 | 27.7
2019-09-29 05:00 | 28.56 | 27.72
2019-09-29 05:30 | 30.46 | 29.68
2019-09-29 06:00 | 29.21 | 28.4
2019-09-29 06:30 | 29.64 | 28.84
2019-09-29 07:00 | 29.33 | 28.52
2019-09-29 07:30 | 29.64 | 28.82
2019-09-29 08:00 | 29.71 | 28.87
2019-09-29 08:30 | 30.32 | 29.49
2019-09-29 09:00 | 30.9 | 30.06
2019-09-29 09:30 | 31.73 | 30.9
2019-09-29 10:00 | 31.15 | 30.29
2019-09-29 10:30 | 30.47 | 29.57
2019-09-29 11:00 | 29.63 | 28.69
2019-09-29 11:30 | 29.36 | 28.41
2019-09-29 12:00 | 29.27 | 28.4
2019-09-29 12:30 | 29.3 | 28.43
2019-09-29 13:00 | 29.34 | 28.49
2019-09-29 13:30 | 30.01 | 29.17
2019-09-29 14:00 | 30.54 | 29.72
2019-09-29 14:30 | 30.97 | 30.17
2019-09-29 15:00 | 32.33 | 31.58
2019-09-29 15:30 | 33.87 | 33.16
2019-09-29 16:00 | 36.6 | 35.95
2019-09-29 16:30 | 37.86 | 37.24
2019-09-29 17:00 | 39.6 | 39.02
2019-09-29 17:30 | 41.84 | 41.3
2019-09-29 18:00 | 44.66 | 44.16
2019-09-29 18:30 | 47.19 | 46.71
2019-09-29 19:00 | 48.38 | 47.91
2019-09-29 19:30 | 46.98 | 46.5
2019-09-29 20:00 | 45.06 | 44.56
2019-09-29 20:30 | 43.09 | 42.56
2019-09-29 21:00 | 41.27 | 40.72
2019-09-29 21:30 | 39.72 | 39.16
2019-09-29 22:00 | 38.2 | 37.58
2019-09-29 22:30 | 36.2 | 35.52
2019-09-29 23:00 | 34.42 | 33.7
2019-09-29 23:30 | 32.64 | 31.89
2019-09-30 | 31.42 | 30.64
2019-09-30 00:30 | 31.39 | 30.61
2019-09-30 01:00 | 29.82 | 29
2019-09-30 01:30 | 29.49 | 28.67
2019-09-30 02:00 | 29.07 | 28.24
2019-09-30 02:30 | 29.25 | 28.42
2019-09-30 03:00 | 28.15 | 27.32
2019-09-30 03:30 | 28.08 | 27.25
2019-09-30 04:00 | 28.79 | 27.98
2019-09-30 04:30 | 29.75 | 28.97
2019-09-30 05:00 | 31.3 | 30.55
2019-09-30 05:30 | 33.04 | 32.33
2019-09-30 06:00 | 34.51 | 33.8
2019-09-30 06:30 | 39.73 | 39.08
2019-09-30 07:00 | 41.64 | 40.99
2019-09-30 07:30 | 45.26 | 44.29
2019-09-30 08:00 | 47.18 | 45.69
2019-09-30 08:30 | 50.25 | 48.49
2019-09-30 09:00 | 51.57 | 50.26
2019-09-30 09:30 | 51.94 | 50.51
2019-09-30 10:00 | 49.76 | 48.12
2019-09-30 10:30 | 49.28 | 47.27
2019-09-30 11:00 | 50.82 | 48.41
2019-09-30 11:30 | 51.05 | 48.52
2019-09-30 12:00 | 51.13 | 48.57
2019-09-30 12:30 | 50.71 | 48.19
2019-09-30 13:00 | 51.2 | 48.7
2019-09-30 13:30 | 51.62 | 49.12
2019-09-30 14:00 | 52.44 | 49.94
2019-09-30 14:30 | 53.2 | 50.77
2019-09-30 15:00 | 54.07 | 51.78
2019-09-30 15:30 | 54.39 | 52.39
2019-09-30 16:00 | 55.43 | 53.74
2019-09-30 16:30 | 55.87 | 54.59
2019-09-30 17:00 | 55.74 | 54.84
2019-09-30 17:30 | 54.21 | 53.73
2019-09-30 18:00 | 54.33 | 53.98
2019-09-30 18:30 | 56.18 | 55.84
2019-09-30 19:00 | 57.16 | 56.82
2019-09-30 19:30 | 54.73 | 54.37
2019-09-30 20:00 | 51.83 | 51.44
2019-09-30 20:30 | 50.14 | 49.73
2019-09-30 21:00 | 47.39 | 46.94
2019-09-30 21:30 | 45.07 | 44.59
2019-09-30 22:00 | 42.99 | 42.47
2019-09-30 22:30 | 40.55 | 40.02
2019-09-30 23:00 | 38.66 | 38.14
2019-09-30 23:30 | 36.99 | 36.44
2019-10-01 | 35.83 | 35.26
2019-10-01 00:30 | 34.66 | 34.06
2019-10-01 01:00 | 34.51 | 33.91
2019-10-01 01:30 | 33.69 | 33.07
2019-10-01 02:00 | 32.82 | 32.17
2019-10-01 02:30 | 32.39 | 31.73
2019-10-01 03:00 | 31.82 | 31.14
2019-10-01 03:30 | 31.76 | 31.07
2019-10-01 04:00 | 31.79 | 31.1
2019-10-01 04:30 | 32.28 | 31.61
2019-10-01 05:00 | 33.29 | 32.64
2019-10-01 05:30 | 36.27 | 35.7
2019-10-01 06:00 | 37.09 | 36.54
2019-10-01 06:30 | 41.44 | 40.91
2019-10-01 07:00 | 44.29 | 43.43
2019-10-01 07:30 | 50.11 | 48.58
2019-10-01 08:00 | 54.33 | 52.2
2019-10-01 08:30 | 55.22 | 52.89
2019-10-01 09:00 | 55.28 | 53.46
2019-10-01 09:30 | 54.68 | 52.71
2019-10-01 10:00 | 53.76 | 51.58
2019-10-01 10:30 | 53.97 | 51.38
2019-10-01 11:00 | 55.1 | 51.77
2019-10-01 11:30 | 55.61 | 52.3
2019-10-01 12:00 | 54.6 | 51.21
2019-10-01 12:30 | 54.59 | 51.18
2019-10-01 13:00 | 53.85 | 50.36
2019-10-01 13:30 | 52.97 | 49.37
2019-10-01 14:00 | 55.95 | 52.62
2019-10-01 14:30 | 55.97 | 52.63
2019-10-01 15:00 | 57.12 | 53.84
2019-10-01 15:30 | 58.19 | 54.93
2019-10-01 16:00 | 59.07 | 55.82
2019-10-01 16:30 | 60.16 | 56.87
2019-10-01 17:00 | 59.74 | 56.3
2019-10-01 17:30 | 58.81 | 55.2
2019-10-01 18:00 | 58.83 | 55.16
2019-10-01 18:30 | 59.88 | 56.28
2019-10-01 19:00 | 60.02 | 56.42
2019-10-01 19:30 | 57.97 | 54.21
2019-10-01 20:00 | 56.02 | 52.07
2019-10-01 20:30 | 54.36 | 50.23
2019-10-01 21:00 | 49.93 | 47.89
2019-10-01 21:30 | 46.15 | 45.68
2019-10-01 22:00 | 44.35 | 43.85
2019-10-01 22:30 | 41.89 | 41.35
2019-10-01 23:00 | 40.13 | 39.58
2019-10-01 23:30 | 37.89 | 37.36
2019-10-02 | 36.34 | 35.78
2019-10-02 00:30 | 35.02 | 34.42
2019-10-02 01:00 | 34.24 | 33.62
2019-10-02 01:30 | 33.5 | 32.87
2019-10-02 02:00 | 32.86 | 32.2
2019-10-02 02:30 | 32.37 | 31.7
2019-10-02 03:00 | 32.8 | 32.14
2019-10-02 03:30 | 32.27 | 31.59
2019-10-02 04:00 | 32.18 | 31.5
2019-10-02 04:30 | 32.95 | 32.28
2019-10-02 05:00 | 33.69 | 33.04
2019-10-02 05:30 | 35.8 | 35.21
2019-10-02 06:00 | 38.52 | 37.99
2019-10-02 06:30 | 43.08 | 42.59
2019-10-02 07:00 | 45.25 | 44.5
2019-10-02 07:30 | 50.1 | 48.74
2019-10-02 08:00 | 53.19 | 51.32
2019-10-02 08:30 | 53.08 | 51.65
2019-10-02 09:00 | 53.1 | 51.33
2019-10-02 09:30 | 52.15 | 50.24
2019-10-02 10:00 | 50.72 | 48.73
2019-10-02 10:30 | 50.1 | 47.97
2019-10-02 11:00 | 48.87 | 46.53
2019-10-02 11:30 | 49.53 | 47.02
2019-10-02 12:00 | 49.85 | 47.16
2019-10-02 12:30 | 48.88 | 46.24
2019-10-02 13:00 | 49.23 | 46.8
2019-10-02 13:30 | 50.06 | 47.54
2019-10-02 14:00 | 50.64 | 48.18
2019-10-02 14:30 | 51.64 | 49.35
2019-10-02 15:00 | 51.92 | 49.58
2019-10-02 15:30 | 53.22 | 51.22
2019-10-02 16:00 | 54.26 | 52.6
2019-10-02 16:30 | 55.45 | 54.25
2019-10-02 17:00 | 54.65 | 53.8
2019-10-02 17:30 | 53.19 | 52.73
2019-10-02 18:00 | 53.3 | 52.93
2019-10-02 18:30 | 54.46 | 54.1
2019-10-02 19:00 | 54.78 | 54.42
2019-10-02 19:30 | 52.51 | 52.13
2019-10-02 20:00 | 50.81 | 50.41
2019-10-02 20:30 | 49.18 | 48.76
2019-10-02 21:00 | 47.21 | 46.76
2019-10-02 21:30 | 44.47 | 43.97
2019-10-02 22:00 | 42.83 | 42.3
2019-10-02 22:30 | 39.81 | 39.24
2019-10-02 23:00 | 37.78 | 37.25
2019-10-02 23:30 | 36.09 | 35.52
2019-10-03 | 34.79 | 34.2
2019-10-03 00:30 | 33.83 | 33.21
2019-10-03 01:00 | 32.8 | 32.15
2019-10-03 01:30 | 32.4 | 31.74
2019-10-03 02:00 | 31.63 | 30.95
2019-10-03 02:30 | 30.98 | 30.27
2019-10-03 03:00 | 30.45 | 29.73
2019-10-03 03:30 | 30.4 | 29.68
2019-10-03 04:00 | 31.02 | 30.31
2019-10-03 04:30 | 32.08 | 31.4
2019-10-03 05:00 | 32.61 | 31.94
2019-10-03 05:30 | 35.24 | 34.64
2019-10-03 06:00 | 37.38 | 36.82
2019-10-03 06:30 | 40.62 | 40.14
2019-10-03 07:00 | 43.35 | 42.72
2019-10-03 07:30 | 47.96 | 46.77
2019-10-03 08:00 | 51.43 | 49.72
2019-10-03 08:30 | 54.51 | 52.67
2019-10-03 09:00 | 53.38 | 51.87
2019-10-03 09:30 | 52.42 | 50.8
2019-10-03 10:00 | 52.24 | 50.59
2019-10-03 10:30 | 50.62 | 48.8
2019-10-03 11:00 | 51.81 | 49.85
2019-10-03 11:30 | 54.22 | 52.26
2019-10-03 12:00 | 54.58 | 52.68
2019-10-03 12:30 | 53.41 | 51.55
2019-10-03 13:00 | 51.83 | 50.01
2019-10-03 13:30 | 51.76 | 49.96
2019-10-03 14:00 | 55.42 | 53.55
2019-10-03 14:30 | 55.04 | 53.4
2019-10-03 15:00 | 51.88 | 49.82
2019-10-03 15:30 | 53.39 | 51.68
2019-10-03 16:00 | 53.94 | 52.49
2019-10-03 16:30 | 53.5 | 52.49
2019-10-03 17:00 | 53.08 | 52.44
2019-10-03 17:30 | 52.33 | 51.94
2019-10-03 18:00 | 53.13 | 52.76
2019-10-03 18:30 | 54.75 | 54.39
2019-10-03 19:00 | 55.67 | 55.32
2019-10-03 19:30 | 53.72 | 53.35
2019-10-03 20:00 | 51.69 | 51.3
2019-10-03 20:30 | 49.79 | 49.37
2019-10-03 21:00 | 47.84 | 47.39
2019-10-03 21:30 | 45.56 | 45.07
2019-10-03 22:00 | 43.29 | 42.79
2019-10-03 22:30 | 40.85 | 40.37
2019-10-03 23:00 | 38.91 | 38.41
2019-10-03 23:30 | 37.07 | 36.53
2019-10-04 | 35.51 | 34.94
2019-10-04 00:30 | 34.14 | 33.53
2019-10-04 01:00 | 33.13 | 32.49
2019-10-04 01:30 | 32.76 | 32.11
2019-10-04 02:00 | 32.2 | 31.54
2019-10-04 02:30 | 31.38 | 30.69
2019-10-04 03:00 | 30.7 | 30
2019-10-04 03:30 | 30.79 | 30.08
2019-10-04 04:00 | 30.94 | 30.23
2019-10-04 04:30 | 31.5 | 30.8
2019-10-04 05:00 | 32.47 | 31.81
2019-10-04 05:30 | 34.69 | 34.08
2019-10-04 06:00 | 35.84 | 35.26
2019-10-04 06:30 | 38.37 | 37.84
2019-10-04 07:00 | 41.52 | 41.02
2019-10-04 07:30 | 45.07 | 44.18
2019-10-04 08:00 | 45.99 | 44.55
2019-10-04 08:30 | 47.68 | 45.76
2019-10-04 09:00 | 46.98 | 45.01
2019-10-04 09:30 | 47.74 | 46.43
2019-10-04 10:00 | 46.2 | 44.74
2019-10-04 10:30 | 45.52 | 43.84
2019-10-04 11:00 | 45.19 | 43.43
2019-10-04 11:30 | 45.17 | 43.32
2019-10-04 12:00 | 44.68 | 42.73
2019-10-04 12:30 | 44.91 | 43.1
2019-10-04 13:00 | 44.08 | 42.28
2019-10-04 13:30 | 43.44 | 41.63
2019-10-04 14:00 | 43.31 | 41.68
2019-10-04 14:30 | 43.6 | 42.18
2019-10-04 15:00 | 44.34 | 43.11
2019-10-04 15:30 | 44.64 | 43.58
2019-10-04 16:00 | 45.26 | 44.5
2019-10-04 16:30 | 46.13 | 45.63
2019-10-04 17:00 | 46.84 | 46.42
2019-10-04 17:30 | 48.06 | 47.63
2019-10-04 18:00 | 49.83 | 49.41
2019-10-04 18:30 | 50.28 | 49.85
2019-10-04 19:00 | 50.8 | 50.38
2019-10-04 19:30 | 48.87 | 48.43
2019-10-04 20:00 | 46.62 | 46.15
2019-10-04 20:30 | 44.75 | 44.25
2019-10-04 21:00 | 43.97 | 43.45
2019-10-04 21:30 | 42.43 | 41.89
2019-10-04 22:00 | 39.89 | 39.31
2019-10-04 22:30 | 37.47 | 36.9
2019-10-04 23:00 | 35.81 | 35.2
2019-10-04 23:30 | 34.33 | 33.69
2019-10-05 | 32.59 | 31.9
2019-10-05 00:30 | 32.68 | 31.98
2019-10-05 01:00 | 30.39 | 29.63
2019-10-05 01:30 | 29.89 | 29.07
2019-10-05 02:00 | 29.62 | 28.79
2019-10-05 02:30 | 29.25 | 28.42
2019-10-05 03:00 | 28.47 | 27.62
2019-10-05 03:30 | 28.33 | 27.47
2019-10-05 04:00 | 28.76 | 27.91
2019-10-05 04:30 | 29 | 28.16
2019-10-05 05:00 | 29.06 | 28.23
2019-10-05 05:30 | 29.78 | 28.96
2019-10-05 06:00 | 30.41 | 29.62
2019-10-05 06:30 | 30.87 | 30.08
2019-10-05 07:00 | 31.25 | 30.46
2019-10-05 07:30 | 32.1 | 31.31
2019-10-05 08:00 | 32.39 | 31.59
2019-10-05 08:30 | 32.58 | 31.78
2019-10-05 09:00 | 32.3 | 31.47
2019-10-05 09:30 | 32.08 | 31.24
2019-10-05 10:00 | 30.8 | 29.91
2019-10-05 10:30 | 30.3 | 29.37
2019-10-05 11:00 | 30.46 | 29.53
2019-10-05 11:30 | 29.92 | 28.97
2019-10-05 12:00 | 28.87 | 27.87
2019-10-05 12:30 | 28.76 | 27.78
2019-10-05 13:00 | 26.89 | 25.84
2019-10-05 13:30 | 26.11 | 25.03
2019-10-05 14:00 | 26.56 | 25.5
2019-10-05 14:30 | 27.32 | 26.3
2019-10-05 15:00 | 28.26 | 27.29
2019-10-05 15:30 | 29.57 | 28.65
2019-10-05 16:00 | 31.35 | 30.5
2019-10-05 16:30 | 32.77 | 31.98
2019-10-05 17:00 | 35.76 | 35.04
2019-10-05 17:30 | 39.78 | 39.14
2019-10-05 18:00 | 42.19 | 41.59
2019-10-05 18:30 | 43.75 | 43.17
2019-10-05 19:00 | 45.48 | 44.92
2019-10-05 19:30 | 43.88 | 43.29
2019-10-05 20:00 | 42.62 | 42.02
2019-10-05 20:30 | 40.53 | 39.9
2019-10-05 21:00 | 39.17 | 38.52
2019-10-05 21:30 | 37.91 | 37.24
2019-10-05 22:00 | 36.78 | 36.1
2019-10-05 22:30 | 35.18 | 34.48
2019-10-05 23:00 | 33.44 | 32.71
2019-10-05 23:30 | 32.26 | 31.5
2019-10-06 | 31.11 | 30.33
2019-10-06 00:30 | 30.05 | 29.25
2019-10-06 01:00 | 29.31 | 28.49
2019-10-06 01:30 | 28.63 | 27.79
2019-10-06 02:00 | 28.38 | 27.54
2019-10-06 02:30 | 28.15 | 27.3
2019-10-06 03:00 | 27.47 | 26.6
2019-10-06 03:30 | 27.39 | 26.53
2019-10-06 04:00 | 27.45 | 26.59
2019-10-06 04:30 | 28.61 | 27.78
2019-10-06 05:00 | 29.31 | 28.5
2019-10-06 05:30 | 29.55 | 28.75
2019-10-06 06:00 | 29.34 | 28.53
2019-10-06 06:30 | 29.09 | 28.28
2019-10-06 07:00 | 28.09 | 27.24
2019-10-06 07:30 | 28.31 | 27.46
2019-10-06 08:00 | 28.21 | 27.34
2019-10-06 08:30 | 27.92 | 27.02
2019-10-06 09:00 | 27.44 | 26.51
2019-10-06 09:30 | 27.71 | 26.77
2019-10-06 10:00 | 26.92 | 25.94
2019-10-06 10:30 | 27.15 | 26.16
2019-10-06 11:00 | 26.9 | 25.89
2019-10-06 11:30 | 27.46 | 26.47
2019-10-06 12:00 | 27.35 | 26.35
2019-10-06 12:30 | 26.89 | 25.88
2019-10-06 13:00 | 27.07 | 26.05
2019-10-06 13:30 | 26.82 | 25.8
2019-10-06 14:00 | 27.78 | 26.81
2019-10-06 14:30 | 28.49 | 27.54
2019-10-06 15:00 | 29.54 | 28.64
2019-10-06 15:30 | 31.31 | 30.47
2019-10-06 16:00 | 33.36 | 32.58
2019-10-06 16:30 | 34.83 | 34.1
2019-10-06 17:00 | 36.78 | 36.09
2019-10-06 17:30 | 39.46 | 38.83
2019-10-06 18:00 | 42.34 | 41.75
2019-10-06 18:30 | 44.47 | 43.9
2019-10-06 19:00 | 44.88 | 44.31
2019-10-06 19:30 | 43.26 | 42.68
2019-10-06 20:00 | 42.66 | 42.07
2019-10-06 20:30 | 41.1 | 40.49
2019-10-06 21:00 | 40.32 | 39.69
2019-10-06 21:30 | 39.01 | 38.38
2019-10-06 22:00 | 36.73 | 36.06
2019-10-06 22:30 | 35.33 | 34.64
2019-10-06 23:00 | 34.17 | 33.47
2019-10-06 23:30 | 31.62 | 30.86
2019-10-07 | 30.21 | 29.43
2019-10-07 00:30 | 29.63 | 28.83
2019-10-07 01:00 | 29.34 | 28.53
2019-10-07 01:30 | 28.77 | 27.95
2019-10-07 02:00 | 28.54 | 27.71
2019-10-07 02:30 | 27.96 | 27.12
2019-10-07 03:00 | 27.54 | 26.68
2019-10-07 03:30 | 27.34 | 26.48
2019-10-07 04:00 | 27.21 | 26.35
2019-10-07 04:30 | 27.68 | 26.83
2019-10-07 05:00 | 28.35 | 27.51
2019-10-07 05:30 | 28.68 | 27.86
2019-10-07 06:00 | 28.61 | 27.8
2019-10-07 06:30 | 29.48 | 28.69
2019-10-07 07:00 | 28.93 | 28.11
2019-10-07 07:30 | 30.05 | 29.24
2019-10-07 08:00 | 30.23 | 29.4
2019-10-07 08:30 | 30.72 | 29.89
2019-10-07 09:00 | 31 | 30.16
2019-10-07 09:30 | 30.76 | 29.89
2019-10-07 10:00 | 30.2 | 29.3
2019-10-07 10:30 | 30.62 | 29.72
2019-10-07 11:00 | 30.9 | 30
2019-10-07 11:30 | 31.14 | 30.23
2019-10-07 12:00 | 32.04 | 31.2
2019-10-07 12:30 | 32.32 | 31.5
2019-10-07 13:00 | 32.51 | 31.7
2019-10-07 13:30 | 32.41 | 31.61
2019-10-07 14:00 | 32.86 | 32.07
2019-10-07 14:30 | 33.98 | 33.22
2019-10-07 15:00 | 35.31 | 34.59
2019-10-07 15:30 | 37.42 | 36.75
2019-10-07 16:00 | 39.53 | 38.9
2019-10-07 16:30 | 42.07 | 41.51
2019-10-07 17:00 | 43.21 | 42.67
2019-10-07 17:30 | 45.69 | 45.18
2019-10-07 18:00 | 47.35 | 46.87
2019-10-07 18:30 | 49.42 | 48.97
2019-10-07 19:00 | 51.08 | 50.63
2019-10-07 19:30 | 49.03 | 48.57
2019-10-07 20:00 | 47.68 | 47.21
2019-10-07 20:30 | 44.82 | 44.33
2019-10-07 21:00 | 42.68 | 42.16
2019-10-07 21:30 | 40.86 | 40.32
2019-10-07 22:00 | 38.85 | 38.25
2019-10-07 22:30 | 36.97 | 36.32
2019-10-07 23:00 | 36.31 | 35.65
2019-10-07 23:30 | 33.34 | 32.61
2019-10-08 | 32.16 | 31.42
2019-10-08 00:30 | 31.52 | 30.76
2019-10-08 01:00 | 31.18 | 30.41
2019-10-08 01:30 | 30.04 | 29.24
2019-10-08 02:00 | 29.45 | 28.65
2019-10-08 02:30 | 29.71 | 28.91
2019-10-08 03:00 | 28.84 | 28.01
2019-10-08 03:30 | 28.68 | 27.85
2019-10-08 04:00 | 28.88 | 28.06
2019-10-08 04:30 | 30.63 | 29.86
2019-10-08 05:00 | 32.81 | 32.08
2019-10-08 05:30 | 35.15 | 34.45
2019-10-08 06:00 | 36.63 | 35.95
2019-10-08 06:30 | 40.29 | 39.65
2019-10-08 07:00 | 43.8 | 43.19
2019-10-08 07:30 | 46.47 | 45.44
2019-10-08 08:00 | 49.56 | 47.96
2019-10-08 08:30 | 50.21 | 48.03
2019-10-08 09:00 | 49.62 | 48
2019-10-08 09:30 | 50.95 | 48.99
2019-10-08 10:00 | 52.11 | 49.89
2019-10-08 10:30 | 53.73 | 51.22
2019-10-08 11:00 | 54.52 | 51.82
2019-10-08 11:30 | 55.53 | 52.29
2019-10-08 12:00 | 56.13 | 52.94
2019-10-08 12:30 | 56.41 | 53.2
2019-10-08 13:00 | 56 | 52.71
2019-10-08 13:30 | 55.86 | 52.56
2019-10-08 14:00 | 56.86 | 53.62
2019-10-08 14:30 | 57.73 | 54.56
2019-10-08 15:00 | 58.34 | 55.19
2019-10-08 15:30 | 59.35 | 56.22
2019-10-08 16:00 | 61.11 | 58.05
2019-10-08 16:30 | 61.31 | 58.16
2019-10-08 17:00 | 61.35 | 58.1
2019-10-08 17:30 | 59.78 | 56.3
2019-10-08 18:00 | 59.09 | 55.47
2019-10-08 18:30 | 60.48 | 56.95
2019-10-08 19:00 | 61.84 | 58.41
2019-10-08 19:30 | 59.92 | 56.33
2019-10-08 20:00 | 57.56 | 53.77
2019-10-08 20:30 | 55.17 | 51.14
2019-10-08 21:00 | 49.54 | 48.55
2019-10-08 21:30 | 47.8 | 47.34
2019-10-08 22:00 | 44.94 | 44.44
2019-10-08 22:30 | 41.81 | 41.3
2019-10-08 23:00 | 39.59 | 39.08
2019-10-08 23:30 | 37.44 | 36.89
2019-10-09 | 35.92 | 35.34
2019-10-09 00:30 | 34.71 | 34.09
2019-10-09 01:00 | 33.69 | 33.05
2019-10-09 01:30 | 33.3 | 32.64
2019-10-09 02:00 | 32.44 | 31.76
2019-10-09 02:30 | 31.98 | 31.28
2019-10-09 03:00 | 31.29 | 30.58
2019-10-09 03:30 | 31.18 | 30.46
2019-10-09 04:00 | 31.49 | 30.78
2019-10-09 04:30 | 32.07 | 31.38
2019-10-09 05:00 | 33.05 | 32.38
2019-10-09 05:30 | 34.87 | 34.25
2019-10-09 06:00 | 37.62 | 37.05
2019-10-09 06:30 | 40.33 | 39.84
2019-10-09 07:00 | 43.88 | 43.15
2019-10-09 07:30 | 47.89 | 47.11
2019-10-09 08:00 | 50.18 | 49.17
2019-10-09 08:30 | 47.91 | 47.03
2019-10-09 09:00 | 49.86 | 48.78
2019-10-09 09:30 | 50.83 | 49.54
2019-10-09 10:00 | 52.39 | 51.06
2019-10-09 10:30 | 51.88 | 50.33
2019-10-09 11:00 | 51.94 | 50.22
2019-10-09 11:30 | 52.39 | 50.58
2019-10-09 12:00 | 52.96 | 51.11
2019-10-09 12:30 | 53.11 | 51.28
2019-10-09 13:00 | 53.82 | 52.07
2019-10-09 13:30 | 54.48 | 52.75
2019-10-09 14:00 | 56.53 | 54.87
2019-10-09 14:30 | 55.43 | 53.75
2019-10-09 15:00 | 54.56 | 53.03
2019-10-09 15:30 | 57.39 | 55.98
2019-10-09 16:00 | 58.39 | 57.22
2019-10-09 16:30 | 58.88 | 58.11
2019-10-09 17:00 | 58.48 | 57.99
2019-10-09 17:30 | 57.46 | 57.11
2019-10-09 18:00 | 57.65 | 57.29
2019-10-09 18:30 | 58.57 | 58.21
2019-10-09 19:00 | 59.66 | 59.31
2019-10-09 19:30 | 57.9 | 57.53
2019-10-09 20:00 | 55.45 | 55.05
2019-10-09 20:30 | 53.07 | 52.64
2019-10-09 21:00 | 51.28 | 50.83
2019-10-09 21:30 | 48.47 | 47.98
2019-10-09 22:00 | 45.62 | 45.07
2019-10-09 22:30 | 43.33 | 42.74
2019-10-09 23:00 | 40.69 | 40.11
2019-10-09 23:30 | 38.99 | 38.37
2019-10-10 | 37.68 | 37.04
2019-10-10 00:30 | 36.36 | 35.71
2019-10-10 01:00 | 35.28 | 34.61
2019-10-10 01:30 | 34.57 | 33.89
2019-10-10 02:00 | 33.97 | 33.28
2019-10-10 02:30 | 33.5 | 32.8
2019-10-10 03:00 | 33.68 | 32.99
2019-10-10 03:30 | 33.18 | 32.43
2019-10-10 04:00 | 33.56 | 32.79
2019-10-10 04:30 | 33.95 | 33.19
2019-10-10 05:00 | 34.59 | 33.85
2019-10-10 05:30 | 37.15 | 36.45
2019-10-10 06:00 | 38.48 | 37.8
2019-10-10 06:30 | 43.78 | 43.15
2019-10-10 07:00 | 48.89 | 48
2019-10-10 07:30 | 56.14 | 54.41
2019-10-10 08:00 | 58.59 | 56.72
2019-10-10 08:30 | 58.48 | 56.74
2019-10-10 09:00 | 60.35 | 58.41
2019-10-10 09:30 | 59.86 | 57.7
2019-10-10 10:00 | 58.92 | 56.37
2019-10-10 10:30 | 59.02 | 56.34
2019-10-10 11:00 | 57.66 | 54.71
2019-10-10 11:30 | 58.27 | 55.17
2019-10-10 12:00 | 60.53 | 57.55
2019-10-10 12:30 | 57.84 | 54.9
2019-10-10 13:00 | 56.82 | 53.95
2019-10-10 13:30 | 57.18 | 54.35
2019-10-10 14:00 | 58.15 | 55.38
2019-10-10 14:30 | 59.39 | 56.76
2019-10-10 15:00 | 60.09 | 57.63
2019-10-10 15:30 | 61.64 | 59.53
2019-10-10 16:00 | 60.95 | 59.39
2019-10-10 16:30 | 60.81 | 59.5
2019-10-10 17:00 | 60.05 | 58.69
2019-10-10 17:30 | 58.55 | 57.1
2019-10-10 18:00 | 58.28 | 56.79
2019-10-10 18:30 | 59.33 | 57.86
2019-10-10 19:00 | 59.65 | 58.19
2019-10-10 19:30 | 57.95 | 56.42
2019-10-10 20:00 | 56.38 | 54.8
2019-10-10 20:30 | 54.36 | 52.69
2019-10-10 21:00 | 52.65 | 50.88
2019-10-10 21:30 | 50.01 | 48.12
2019-10-10 22:00 | 47.4 | 45.35
2019-10-10 22:30 | 42.72 | 42.68
2019-10-10 23:00 | 40.95 | 40.9
2019-10-10 23:30 | 39.02 | 38.78
2019-10-11 | 37.63 | 37.44
2019-10-11 00:30 | 36.64 | 36.5
2019-10-11 01:00 | 35.9 | 35.74
2019-10-11 01:30 | 34.79 | 34.65
2019-10-11 02:00 | 34.18 | 34.05
2019-10-11 02:30 | 33.67 | 33.56
2019-10-11 03:00 | 33.56 | 33.48
2019-10-11 03:30 | 32.95 | 32.86
2019-10-11 04:00 | 32.91 | 32.84
2019-10-11 04:30 | 33.99 | 33.92
2019-10-11 05:00 | 35.43 | 35.32
2019-10-11 05:30 | 37.56 | 37.37
2019-10-11 06:00 | 39.69 | 39.47
2019-10-11 06:30 | 44.52 | 44.05
2019-10-11 07:00 | 48.78 | 47.94
2019-10-11 07:30 | 53.61 | 52.17
2019-10-11 08:00 | 54.39 | 52.42
2019-10-11 08:30 | 55.49 | 54.01
2019-10-11 09:00 | 58.24 | 56.57
2019-10-11 09:30 | 57.62 | 55.93
2019-10-11 10:00 | 57.46 | 55.72
2019-10-11 10:30 | 55.14 | 53.28
2019-10-11 11:00 | 57.03 | 55.17
2019-10-11 11:30 | 50.86 | 48.63
2019-10-11 12:00 | 50.57 | 48.26
2019-10-11 12:30 | 48.98 | 46.57
2019-10-11 13:00 | 49.36 | 47.11
2019-10-11 13:30 | 55.13 | 53.27
2019-10-11 14:00 | 56.92 | 55.3
2019-10-11 14:30 | 51.09 | 49.38
2019-10-11 15:00 | 55.3 | 53.95
2019-10-11 15:30 | 57.07 | 56.11
2019-10-11 16:00 | 52.4 | 51.7
2019-10-11 16:30 | 49.07 | 48.58
2019-10-11 17:00 | 50.26 | 49.87
2019-10-11 17:30 | 50.57 | 50.19
2019-10-11 18:00 | 50.58 | 50.18
2019-10-11 18:30 | 51.33 | 50.93
2019-10-11 19:00 | 51.22 | 50.81
2019-10-11 19:30 | 50.21 | 49.79
2019-10-11 20:00 | 48.03 | 47.58
2019-10-11 20:30 | 45.24 | 44.75
2019-10-11 21:00 | 43.49 | 42.97
2019-10-11 21:30 | 42.15 | 41.59
2019-10-11 22:00 | 40.67 | 40.1
2019-10-11 22:30 | 38.97 | 38.43
2019-10-11 23:00 | 36.33 | 35.74
2019-10-11 23:30 | 34.92 | 34.3
2019-10-12 | 33.46 | 32.81
2019-10-12 00:30 | 32.3 | 31.61
2019-10-12 01:00 | 31.28 | 30.56
2019-10-12 01:30 | 31.5 | 30.78
2019-10-12 02:00 | 30.51 | 29.78
2019-10-12 02:30 | 30.47 | 29.72
2019-10-12 03:00 | 29.8 | 29.03
2019-10-12 03:30 | 29.95 | 29.19
2019-10-12 04:00 | 29.83 | 29.07
2019-10-12 04:30 | 30.08 | 29.32
2019-10-12 05:00 | 30.87 | 30.14
2019-10-12 05:30 | 31.82 | 31.1
2019-10-12 06:00 | 31.99 | 31.27
2019-10-12 06:30 | 33.35 | 32.68
2019-10-12 07:00 | 33.14 | 32.48
2019-10-12 07:30 | 34.18 | 33.58
2019-10-12 08:00 | 34.95 | 34.39
2019-10-12 08:30 | 36.46 | 35.91
2019-10-12 09:00 | 36.73 | 36.02
2019-10-12 09:30 | 37.34 | 36.61
2019-10-12 10:00 | 37.35 | 36.83
2019-10-12 10:30 | 38.66 | 38.16
2019-10-12 11:00 | 39.76 | 39.28
2019-10-12 11:30 | 39.74 | 39.26
2019-10-12 12:00 | 39.03 | 38.55
2019-10-12 12:30 | 40.05 | 39.57
2019-10-12 13:00 | 38.72 | 38.21
2019-10-12 13:30 | 38.3 | 37.78
2019-10-12 14:00 | 36.29 | 35.74
2019-10-12 14:30 | 36.62 | 36.08
2019-10-12 15:00 | 37.21 | 36.66
2019-10-12 15:30 | 38.73 | 38.2
2019-10-12 16:00 | 40.47 | 39.96
2019-10-12 16:30 | 41.49 | 40.97
2019-10-12 17:00 | 43.48 | 42.98
2019-10-12 17:30 | 45.73 | 45.26
2019-10-12 18:00 | 47.77 | 47.3
2019-10-12 18:30 | 48.29 | 47.83
2019-10-12 19:00 | 49.19 | 48.74
2019-10-12 19:30 | 48.04 | 47.58
2019-10-12 20:00 | 45.99 | 45.49
2019-10-12 20:30 | 44.43 | 43.91
2019-10-12 21:00 | 43.45 | 42.91
2019-10-12 21:30 | 41.67 | 41.1
2019-10-12 22:00 | 40.42 | 39.82
2019-10-12 22:30 | 38.48 | 37.85
2019-10-12 23:00 | 36.59 | 36
2019-10-12 23:30 | 34.9 | 34.28
2019-10-13 | 33.54 | 32.88
2019-10-13 00:30 | 32.4 | 31.71
2019-10-13 01:00 | 31.69 | 30.98
2019-10-13 01:30 | 31.23 | 30.49
2019-10-13 02:00 | 30.64 | 29.89
2019-10-13 02:30 | 30.16 | 29.39
2019-10-13 03:00 | 29.52 | 28.73
2019-10-13 03:30 | 29.51 | 28.72
2019-10-13 04:00 | 29.51 | 28.72
2019-10-13 04:30 | 30.44 | 29.68
2019-10-13 05:00 | 30.3 | 29.54
2019-10-13 05:30 | 30.51 | 29.75
2019-10-13 06:00 | 30.13 | 29.35
2019-10-13 06:30 | 30.51 | 29.75
2019-10-13 07:00 | 30.64 | 29.88
2019-10-13 07:30 | 30.91 | 30.18
2019-10-13 08:00 | 32.66 | 31.99
2019-10-13 08:30 | 34.5 | 33.89
2019-10-13 09:00 | 33.45 | 32.84
2019-10-13 09:30 | 34.29 | 33.72
2019-10-13 10:00 | 34.21 | 33.65
2019-10-13 10:30 | 33.49 | 32.91
2019-10-13 11:00 | 33.12 | 32.48
2019-10-13 11:30 | 33.56 | 32.93
2019-10-13 12:00 | 33.46 | 32.83
2019-10-13 12:30 | 33.36 | 32.72
2019-10-13 13:00 | 33.59 | 32.95
2019-10-13 13:30 | 34.16 | 33.54
2019-10-13 14:00 | 35.53 | 34.92
2019-10-13 14:30 | 35.73 | 35.12
2019-10-13 15:00 | 36.67 | 36.08
2019-10-13 15:30 | 38.4 | 37.83
2019-10-13 16:00 | 40.58 | 40.04
2019-10-13 16:30 | 41.38 | 40.84
2019-10-13 17:00 | 43.87 | 43.36
2019-10-13 17:30 | 46.19 | 45.7
2019-10-13 18:00 | 49.28 | 48.82
2019-10-13 18:30 | 51.48 | 51.05
2019-10-13 19:00 | 52.25 | 51.83
2019-10-13 19:30 | 50.1 | 49.66
2019-10-13 20:00 | 48.31 | 47.85
2019-10-13 20:30 | 46.39 | 45.89
2019-10-13 21:00 | 44.28 | 43.75
2019-10-13 21:30 | 42.69 | 42.13
2019-10-13 22:00 | 40.91 | 40.31
2019-10-13 22:30 | 38.04 | 37.47
2019-10-13 23:00 | 36.25 | 35.64
2019-10-13 23:30 | 35.32 | 34.7
2019-10-14 | 33.64 | 32.97
2019-10-14 00:30 | 32.69 | 31.99
2019-10-14 01:00 | 31.91 | 31.2
2019-10-14 01:30 | 31.36 | 30.64
2019-10-14 02:00 | 31.29 | 30.57
2019-10-14 02:30 | 30.9 | 30.16
2019-10-14 03:00 | 30.2 | 29.43
2019-10-14 03:30 | 30.51 | 29.75
2019-10-14 04:00 | 30.85 | 30.1
2019-10-14 04:30 | 31.3 | 30.57
2019-10-14 05:00 | 32.62 | 31.93
2019-10-14 05:30 | 34.88 | 34.26
2019-10-14 06:00 | 37.17 | 36.6
2019-10-14 06:30 | 41.62 | 41.15
2019-10-14 07:00 | 45.82 | 45.12
2019-10-14 07:30 | 52.93 | 51.4
2019-10-14 08:00 | 53.88 | 52.67
2019-10-14 08:30 | 54.73 | 53.24
2019-10-14 09:00 | 54.08 | 52.24
2019-10-14 09:30 | 53.55 | 51.53
2019-10-14 10:00 | 53.8 | 51.57
2019-10-14 10:30 | 54.75 | 51.94
2019-10-14 11:00 | 56.16 | 52.99
2019-10-14 11:30 | 57.02 | 53.92
2019-10-14 12:00 | 55.81 | 52.64
2019-10-14 12:30 | 55.59 | 52.4
2019-10-14 13:00 | 54.68 | 51.41
2019-10-14 13:30 | 55.34 | 52.12
2019-10-14 14:00 | 55.31 | 52.09
2019-10-14 14:30 | 57.86 | 54.79
2019-10-14 15:00 | 57.22 | 54.09
2019-10-14 15:30 | 57.66 | 54.48
2019-10-14 16:00 | 59.13 | 55.94
2019-10-14 16:30 | 61.21 | 58.01
2019-10-14 17:00 | 60.66 | 57.36
2019-10-14 17:30 | 59.1 | 55.55
2019-10-14 18:00 | 58.43 | 54.74
2019-10-14 18:30 | 58.04 | 54.28
2019-10-14 19:00 | 59.08 | 55.39
2019-10-14 19:30 | 57.15 | 53.28
2019-10-14 20:00 | 53.6 | 51.67
2019-10-14 20:30 | 49.72 | 49.29
2019-10-14 21:00 | 47.31 | 46.84
2019-10-14 21:30 | 44.95 | 44.45
2019-10-14 22:00 | 43.2 | 42.68
2019-10-14 22:30 | 40.49 | 39.97
2019-10-14 23:00 | 38.64 | 38.12
2019-10-14 23:30 | 36.76 | 36.2
2019-10-15 | 35.27 | 34.68
2019-10-15 00:30 | 33.96 | 33.34
2019-10-15 01:00 | 33.5 | 32.88
2019-10-15 01:30 | 32.9 | 32.26
2019-10-15 02:00 | 32.58 | 31.92
2019-10-15 02:30 | 32.63 | 31.96
2019-10-15 03:00 | 31.43 | 30.73
2019-10-15 03:30 | 31.61 | 30.91
2019-10-15 04:00 | 31.5 | 30.8
2019-10-15 04:30 | 32.24 | 31.55
2019-10-15 05:00 | 33.69 | 33.05
2019-10-15 05:30 | 35.53 | 34.94
2019-10-15 06:00 | 37.61 | 37.06
2019-10-15 06:30 | 41.75 | 41.26
2019-10-15 07:00 | 45.84 | 44.93
2019-10-15 07:30 | 51.31 | 49.61
2019-10-15 08:00 | 54.11 | 52.76
2019-10-15 08:30 | 54.76 | 53.03
2019-10-15 09:00 | 55.32 | 53.24
2019-10-15 09:30 | 53.56 | 51.28
2019-10-15 10:00 | 53.4 | 50.89
2019-10-15 10:30 | 54.53 | 51.81
2019-10-15 11:00 | 54.7 | 51.63
2019-10-15 11:30 | 55.28 | 52.16
2019-10-15 12:00 | 55.44 | 52.2
2019-10-15 12:30 | 56.48 | 53.32
2019-10-15 13:00 | 56.43 | 53.28
2019-10-15 13:30 | 57.14 | 53.94
2019-10-15 14:00 | 58.15 | 55.11
2019-10-15 14:30 | 59.06 | 56.04
2019-10-15 15:00 | 59.05 | 56.16
2019-10-15 15:30 | 59.43 | 56.85
2019-10-15 16:00 | 61.99 | 59.2
2019-10-15 16:30 | 62.5 | 59.44
2019-10-15 17:00 | 62.78 | 59.65
2019-10-15 17:30 | 61.76 | 58.43
2019-10-15 18:00 | 59.81 | 56.26
2019-10-15 18:30 | 60.97 | 57.46
2019-10-15 19:00 | 61.25 | 57.76
2019-10-15 19:30 | 59.26 | 55.59
2019-10-15 20:00 | 57.34 | 53.51
2019-10-15 20:30 | 55.44 | 51.44
2019-10-15 21:00 | 53.63 | 49.5
2019-10-15 21:30 | 51.24 | 46.85
2019-10-15 22:00 | 43.24 | 37.94
2019-10-15 22:30 | 43.48 | 42.31
2019-10-15 23:00 | 40.23 | 39.66
2019-10-15 23:30 | 38.19 | 37.66
2019-10-16 | 37.01 | 36.46
2019-10-16 00:30 | 36.48 | 35.92
2019-10-16 01:00 | 35.08 | 34.48
2019-10-16 01:30 | 33.99 | 33.37
2019-10-16 02:00 | 33.31 | 32.68
2019-10-16 02:30 | 32.84 | 32.19
2019-10-16 03:00 | 32.3 | 31.63
2019-10-16 03:30 | 32.38 | 31.71
2019-10-16 04:00 | 31.98 | 31.29
2019-10-16 04:30 | 33.06 | 32.4
2019-10-16 05:00 | 34.33 | 33.71
2019-10-16 05:30 | 35.91 | 35.33
2019-10-16 06:00 | 38.09 | 37.56
2019-10-16 06:30 | 42.26 | 41.73
2019-10-16 07:00 | 46.84 | 45.82
2019-10-16 07:30 | 52.96 | 51.12
2019-10-16 08:00 | 56.88 | 53.52
2019-10-16 08:30 | 57.68 | 54.4
2019-10-16 09:00 | 58.3 | 55.12
2019-10-16 09:30 | 58.57 | 55.42
2019-10-16 10:00 | 58.02 | 54.88
2019-10-16 10:30 | 57.17 | 53.99
2019-10-16 11:00 | 58.85 | 55.82
2019-10-16 11:30 | 59.62 | 56.61
2019-10-16 12:00 | 58.3 | 55.23
2019-10-16 12:30 | 58.63 | 55.58
2019-10-16 13:00 | 60.39 | 57.46
2019-10-16 13:30 | 60.1 | 57.14
2019-10-16 14:00 | 58.2 | 55.13
2019-10-16 14:30 | 58.57 | 55.51
2019-10-16 15:00 | 58.02 | 54.88
2019-10-16 15:30 | 59.05 | 55.9
2019-10-16 16:00 | 59.91 | 56.71
2019-10-16 16:30 | 61.04 | 57.84
2019-10-16 17:00 | 60.73 | 57.49
2019-10-16 17:30 | 59.73 | 56.32
2019-10-16 18:00 | 59.57 | 56.07
2019-10-16 18:30 | 60.14 | 56.65
2019-10-16 19:00 | 61.52 | 58.14
2019-10-16 19:30 | 59.31 | 55.75
2019-10-16 20:00 | 57.08 | 53.33
2019-10-16 20:30 | 55.61 | 51.72
2019-10-16 21:00 | 54.05 | 49.98
2019-10-16 21:30 | 51.46 | 47.1
2019-10-16 22:00 | 49.71 | 45.13
2019-10-16 22:30 | 45.62 | 42.46
2019-10-16 23:00 | 40.34 | 39.78
2019-10-16 23:30 | 37.89 | 37.35
2019-10-17 | 36.65 | 36.09
2019-10-17 00:30 | 35.48 | 34.9
2019-10-17 01:00 | 34.67 | 34.07
2019-10-17 01:30 | 34.08 | 33.47
2019-10-17 02:00 | 33 | 32.35
2019-10-17 02:30 | 33.2 | 32.56
2019-10-17 03:00 | 33.29 | 32.65
2019-10-17 03:30 | 33.11 | 32.47
2019-10-17 04:00 | 32.71 | 32.05
2019-10-17 04:30 | 33.96 | 33.33
2019-10-17 05:00 | 36.01 | 35.44
2019-10-17 05:30 | 37.26 | 36.72
2019-10-17 06:00 | 39.29 | 38.79
2019-10-17 06:30 | 44.64 | 44.13
2019-10-17 07:00 | 48.39 | 47.46
2019-10-17 07:30 | 54.58 | 52.75
2019-10-17 08:00 | 59.01 | 55.71
2019-10-17 08:30 | 58.87 | 55.67
2019-10-17 09:00 | 59.1 | 55.95
2019-10-17 09:30 | 59.73 | 56.64
2019-10-17 10:00 | 59.7 | 56.62
2019-10-17 10:30 | 59.4 | 56.32
2019-10-17 11:00 | 58.74 | 55.68
2019-10-17 11:30 | 58.31 | 55.25
2019-10-17 12:00 | 59.82 | 56.86
2019-10-17 12:30 | 59.1 | 56.12
2019-10-17 13:00 | 57.51 | 54.38
2019-10-17 13:30 | 55.83 | 52.57
2019-10-17 14:00 | 56.97 | 53.78
2019-10-17 14:30 | 56.5 | 53.27
2019-10-17 15:00 | 56.9 | 53.71
2019-10-17 15:30 | 59.42 | 56.33
2019-10-17 16:00 | 61.1 | 58.07
2019-10-17 16:30 | 61.62 | 58.55
2019-10-17 17:00 | 63.19 | 60.15
2019-10-17 17:30 | 62.28 | 59.09
2019-10-17 18:00 | 61.87 | 58.58
2019-10-17 18:30 | 61.49 | 58.15
2019-10-17 19:00 | 63.08 | 59.85
2019-10-17 19:30 | 61.21 | 57.85
2019-10-17 20:00 | 58.07 | 54.43
2019-10-17 20:30 | 56.93 | 53.08
2019-10-17 21:00 | 54.84 | 50.89
2019-10-17 21:30 | 52.57 | 48.31
2019-10-17 22:00 | 46.26 | 45.25
2019-10-17 22:30 | 43.11 | 42.67
2019-10-17 23:00 | 40.62 | 40.14
2019-10-17 23:30 | 39.36 | 38.86
2019-10-18 | 37.16 | 36.62
2019-10-18 00:30 | 35.94 | 35.37
2019-10-18 01:00 | 34.63 | 34.04
2019-10-18 01:30 | 33.77 | 33.15
2019-10-18 02:00 | 32.8 | 32.16
2019-10-18 02:30 | 33.33 | 32.69
2019-10-18 03:00 | 33.29 | 32.65
2019-10-18 03:30 | 33.06 | 32.41
2019-10-18 04:00 | 33.14 | 32.49
2019-10-18 04:30 | 33.93 | 33.31
2019-10-18 05:00 | 34.28 | 33.67
2019-10-18 05:30 | 36.44 | 35.89
2019-10-18 06:00 | 38.71 | 38.2
2019-10-18 06:30 | 43.2 | 42.69
2019-10-18 07:00 | 47.48 | 46.5
2019-10-18 07:30 | 53.2 | 51.51
2019-10-18 08:00 | 56.26 | 54.76
2019-10-18 08:30 | 57.41 | 55.61
2019-10-18 09:00 | 57.4 | 55.12
2019-10-18 09:30 | 56.77 | 54.34
2019-10-18 10:00 | 57.7 | 54.92
2019-10-18 10:30 | 58.57 | 55.48
2019-10-18 11:00 | 59.39 | 56.15
2019-10-18 11:30 | 60.94 | 56.65
2019-10-18 12:00 | 63.46 | 58.11
2019-10-18 12:30 | 63.16 | 57.75
2019-10-18 13:00 | 62.41 | 56.89
2019-10-18 13:30 | 62.7 | 57.18
2019-10-18 14:00 | 62.54 | 56.97
2019-10-18 14:30 | 63.07 | 57.52
2019-10-18 15:00 | 63.22 | 57.63
2019-10-18 15:30 | 63.01 | 57.29
2019-10-18 16:00 | 64.24 | 58.55
2019-10-18 16:30 | 64.74 | 59.02
2019-10-18 17:00 | 64.72 | 58.84
2019-10-18 17:30 | 63.55 | 57.38
2019-10-18 18:00 | 62.97 | 56.6
2019-10-18 18:30 | 63.22 | 56.82
2019-10-18 19:00 | 63.18 | 56.78
2019-10-18 19:30 | 61.85 | 55.24
2019-10-18 20:00 | 59.97 | 53.05
2019-10-18 20:30 | 54.45 | 51.28
2019-10-18 21:00 | 50.68 | 48.85
2019-10-18 21:30 | 49.06 | 47.14
2019-10-18 22:00 | 46.99 | 44.95
2019-10-18 22:30 | 43.62 | 41.39
2019-10-18 23:00 | 43.29 | 41.01
2019-10-18 23:30 | 42.01 | 39.76
2019-10-19 | 39.52 | 37.16
2019-10-19 00:30 | 39.27 | 36.87
2019-10-19 01:00 | 38.42 | 35.96
2019-10-19 01:30 | 37.69 | 35.16
2019-10-19 02:00 | 36.95 | 34.39
2019-10-19 02:30 | 37.14 | 34.54
2019-10-19 03:00 | 36.76 | 34.13
2019-10-19 03:30 | 36.4 | 33.74
2019-10-19 04:00 | 35.89 | 33.18
2019-10-19 04:30 | 36.24 | 33.56
2019-10-19 05:00 | 36.64 | 34.01
2019-10-19 05:30 | 37.24 | 34.66
2019-10-19 06:00 | 37.62 | 35.06
2019-10-19 06:30 | 39.3 | 36.89
2019-10-19 07:00 | 40.28 | 37.99
2019-10-19 07:30 | 41.68 | 39.53
2019-10-19 08:00 | 43.38 | 41.4
2019-10-19 08:30 | 44.72 | 42.86
2019-10-19 09:00 | 44.94 | 42.98
2019-10-19 09:30 | 45.85 | 43.96
2019-10-19 10:00 | 44.98 | 43.07
2019-10-19 10:30 | 43.53 | 41.55
2019-10-19 11:00 | 44 | 42.07
2019-10-19 11:30 | 43.04 | 41.07
2019-10-19 12:00 | 43.55 | 41.59
2019-10-19 12:30 | 42.66 | 40.63
2019-10-19 13:00 | 41.99 | 39.91
2019-10-19 13:30 | 42.27 | 40.2
2019-10-19 14:00 | 42.79 | 40.75
2019-10-19 14:30 | 43.27 | 41.23
2019-10-19 15:00 | 44.84 | 42.85
2019-10-19 15:30 | 45.32 | 43.33
2019-10-19 16:00 | 47.21 | 45.29
2019-10-19 16:30 | 47.56 | 45.62
2019-10-19 17:00 | 48.94 | 47.03
2019-10-19 17:30 | 50.01 | 48.14
2019-10-19 18:00 | 50.94 | 49.1
2019-10-19 18:30 | 51.5 | 49.69
2019-10-19 19:00 | 53.88 | 52.18
2019-10-19 19:30 | 52.1 | 50.31
2019-10-19 20:00 | 50.18 | 48.31
2019-10-19 20:30 | 48.49 | 46.53
2019-10-19 21:00 | 47.17 | 45.14
2019-10-19 21:30 | 46.09 | 44
2019-10-19 22:00 | 44.99 | 42.82
2019-10-19 22:30 | 43.81 | 41.57
2019-10-19 23:00 | 42.38 | 40.07
2019-10-19 23:30 | 40.73 | 38.47
2019-10-20 | 40.12 | 37.8
2019-10-20 00:30 | 38.84 | 36.42
2019-10-20 01:00 | 37.35 | 34.81
2019-10-20 01:30 | 37.02 | 34.45
2019-10-20 02:00 | 36.54 | 33.97
2019-10-20 02:30 | 33.3 | 33.28
2019-10-20 03:00 | 32.69 | 32.67
2019-10-20 03:30 | 32.31 | 32.29
2019-10-20 04:00 | 32.28 | 32.26
2019-10-20 04:30 | 32.97 | 32.96
2019-10-20 05:00 | 32.58 | 32.57
2019-10-20 05:30 | 31.9 | 31.9
2019-10-20 06:00 | 31.59 | 31.58
2019-10-20 06:30 | 32.87 | 32.86
2019-10-20 07:00 | 33.84 | 33.82
2019-10-20 07:30 | 36.42 | 36.37
2019-10-20 08:00 | 38.07 | 37.98
2019-10-20 08:30 | 38.56 | 38.4
2019-10-20 09:00 | 41.46 | 41.25
2019-10-20 09:30 | 39.84 | 39.58
2019-10-20 10:00 | 40.77 | 40.41
2019-10-20 10:30 | 43.9 | 43.54
2019-10-20 11:00 | 42.62 | 42.23
2019-10-20 11:30 | 40.24 | 39.76
2019-10-20 12:00 | 40.24 | 39.75
2019-10-20 12:30 | 36.84 | 36.32
2019-10-20 13:00 | 36.72 | 36.63
2019-10-20 13:30 | 36.21 | 36.08
2019-10-20 14:00 | 36.52 | 36.39
2019-10-20 14:30 | 37.17 | 37.07
2019-10-20 15:00 | 38.51 | 38.42
2019-10-20 15:30 | 39.54 | 39.47
2019-10-20 16:00 | 42.36 | 42.3
2019-10-20 16:30 | 45.34 | 45.3
2019-10-20 17:00 | 47.5 | 47.48
2019-10-20 17:30 | 48.9 | 48.88
2019-10-20 18:00 | 50.72 | 50.7
2019-10-20 18:30 | 51.69 | 51.66
2019-10-20 19:00 | 52.35 | 52.32
2019-10-20 19:30 | 50.77 | 50.75
2019-10-20 20:00 | 49.43 | 49.41
2019-10-20 20:30 | 47.79 | 47.78
2019-10-20 21:00 | 45.53 | 45.53
2019-10-20 21:30 | 43.25 | 43.24
2019-10-20 22:00 | 41.4 | 41.39
2019-10-20 22:30 | 39.18 | 39.13
2019-10-20 23:00 | 37.28 | 37.23
2019-10-20 23:30 | 35.04 | 35.02
2019-10-21 | 33.64 | 33.62
2019-10-21 00:30 | 33.54 | 33.53
2019-10-21 01:00 | 33.07 | 33.06
2019-10-21 01:30 | 31.4 | 31.39
2019-10-21 02:00 | 31.02 | 31.01
2019-10-21 02:30 | 31 | 31
2019-10-21 03:00 | 30.21 | 30.21
2019-10-21 03:30 | 31.27 | 31.27
2019-10-21 04:00 | 31.61 | 31.61
2019-10-21 04:30 | 33.04 | 33.04
2019-10-21 05:00 | 34.58 | 34.56
2019-10-21 05:30 | 36.88 | 36.83
2019-10-21 06:00 | 38.07 | 37.97
2019-10-21 06:30 | 42.43 | 42.07
2019-10-21 07:00 | 45.83 | 45.03
2019-10-21 07:30 | 51.47 | 49.95
2019-10-21 08:00 | 55.99 | 53.9
2019-10-21 08:30 | 55.17 | 53.52
2019-10-21 09:00 | 56.47 | 54.65
2019-10-21 09:30 | 56.39 | 54.27
2019-10-21 10:00 | 55.28 | 53.03
2019-10-21 10:30 | 55.48 | 53.08
2019-10-21 11:00 | 55.89 | 53.35
2019-10-21 11:30 | 55.76 | 53.15
2019-10-21 12:00 | 55.45 | 52.83
2019-10-21 12:30 | 54.72 | 52.08
2019-10-21 13:00 | 52.8 | 50.23
2019-10-21 13:30 | 54.38 | 51.82
2019-10-21 14:00 | 55.19 | 52.66
2019-10-21 14:30 | 55.2 | 52.86
2019-10-21 15:00 | 56.32 | 54.04
2019-10-21 15:30 | 56.44 | 54.31
2019-10-21 16:00 | 57.59 | 55.86
2019-10-21 16:30 | 57.47 | 56.1
2019-10-21 17:00 | 58.3 | 56.93
2019-10-21 17:30 | 56.53 | 55.05
2019-10-21 18:00 | 56.15 | 54.6
2019-10-21 18:30 | 55.56 | 53.96
2019-10-21 19:00 | 56.66 | 55.1
2019-10-21 19:30 | 55.51 | 53.91
2019-10-21 20:00 | 53.25 | 51.55
2019-10-21 20:30 | 50.69 | 48.88
2019-10-21 21:00 | 48.74 | 46.82
2019-10-21 21:30 | 47.56 | 45.56
2019-10-21 22:00 | 44.54 | 42.35
2019-10-21 22:30 | 42.21 | 39.88
2019-10-21 23:00 | 40.78 | 38.51
2019-10-21 23:30 | 38.52 | 36.09
2019-10-22 | 37.2 | 34.66
2019-10-22 00:30 | 36.18 | 33.55
2019-10-22 01:00 | 35.62 | 32.92
2019-10-22 01:30 | 34.82 | 32.31
2019-10-22 02:00 | 32.51 | 31.84
2019-10-22 02:30 | 32.64 | 31.97
2019-10-22 03:00 | 31.75 | 31.06
2019-10-22 03:30 | 31.28 | 30.57
2019-10-22 04:00 | 31.48 | 30.77
2019-10-22 04:30 | 32.22 | 31.53
2019-10-22 05:00 | 33.17 | 32.51
2019-10-22 05:30 | 35.21 | 34.61
2019-10-22 06:00 | 37.21 | 36.65
2019-10-22 06:30 | 41.36 | 40.89
2019-10-22 07:00 | 45.16 | 44.4
2019-10-22 07:30 | 49.63 | 48.55
2019-10-22 08:00 | 50.17 | 49.52
2019-10-22 08:30 | 47.58 | 47.08
2019-10-22 09:00 | 49.81 | 49.06
2019-10-22 09:30 | 49.32 | 48.44
2019-10-22 10:00 | 48.49 | 47.48
2019-10-22 10:30 | 48.93 | 47.83
2019-10-22 11:00 | 48.49 | 47.17
2019-10-22 11:30 | 48.78 | 47.38
2019-10-22 12:00 | 49.41 | 47.99
2019-10-22 12:30 | 49.25 | 47.9
2019-10-22 13:00 | 48.08 | 46.79
2019-10-22 13:30 | 48.68 | 47.4
2019-10-22 14:00 | 49.75 | 48.4
2019-10-22 14:30 | 50.47 | 49.16
2019-10-22 15:00 | 51.23 | 50.04
2019-10-22 15:30 | 52.78 | 51.83
2019-10-22 16:00 | 54.23 | 53.48
2019-10-22 16:30 | 54.12 | 53.68
2019-10-22 17:00 | 53.98 | 53.62
2019-10-22 17:30 | 53.21 | 52.81
2019-10-22 18:00 | 52.69 | 52.26
2019-10-22 18:30 | 53.17 | 52.74
2019-10-22 19:00 | 54.91 | 54.5
2019-10-22 19:30 | 53.08 | 52.65
2019-10-22 20:00 | 49.67 | 49.2
2019-10-22 20:30 | 49.65 | 49.16
2019-10-22 21:00 | 47.15 | 46.63
2019-10-22 21:30 | 45.98 | 45.44
2019-10-22 22:00 | 46.62 | 46.1
2019-10-22 22:30 | 43.46 | 42.95
2019-10-22 23:00 | 41.38 | 40.83
2019-10-22 23:30 | 38.84 | 38.24
2019-10-23 | 37.99 | 37.38
2019-10-23 00:30 | 36.55 | 35.9
2019-10-23 01:00 | 36.56 | 35.91
2019-10-23 01:30 | 35.48 | 34.8
2019-10-23 02:00 | 34.66 | 33.96
2019-10-23 02:30 | 34.44 | 33.73
2019-10-23 03:00 | 33.89 | 33.16
2019-10-23 03:30 | 34.14 | 33.43
2019-10-23 04:00 | 34.3 | 33.58
2019-10-23 04:30 | 34.75 | 34.04
2019-10-23 05:00 | 36.07 | 35.4
2019-10-23 05:30 | 38.38 | 37.78
2019-10-23 06:00 | 40.07 | 39.5
2019-10-23 06:30 | 44.39 | 43.92
2019-10-23 07:00 | 47.84 | 47.41
2019-10-23 07:30 | 51.39 | 50.64
2019-10-23 08:00 | 50.59 | 49.4
2019-10-23 08:30 | 51.25 | 50.49
2019-10-23 09:00 | 51.01 | 50.14
2019-10-23 09:30 | 50.8 | 49.83
2019-10-23 10:00 | 49.53 | 48.51
2019-10-23 10:30 | 49.98 | 48.88
2019-10-23 11:00 | 50.24 | 48.89
2019-10-23 11:30 | 49.79 | 48.35
2019-10-23 12:00 | 50.12 | 48.59
2019-10-23 12:30 | 51.77 | 50.33
2019-10-23 13:00 | 52.14 | 50.84
2019-10-23 13:30 | 51.58 | 50.25
2019-10-23 14:00 | 53.54 | 52.28
2019-10-23 14:30 | 53.32 | 52.1
2019-10-23 15:00 | 52.76 | 51.61
2019-10-23 15:30 | 53.09 | 52.12
2019-10-23 16:00 | 53.39 | 52.67
2019-10-23 16:30 | 53.61 | 53.17
2019-10-23 17:00 | 53.93 | 53.57
2019-10-23 17:30 | 52.61 | 52.21
2019-10-23 18:00 | 52.18 | 51.75
2019-10-23 18:30 | 52.9 | 52.46
2019-10-23 19:00 | 54.86 | 54.45
2019-10-23 19:30 | 53.16 | 52.73
2019-10-23 20:00 | 51.42 | 50.96
2019-10-23 20:30 | 49.83 | 49.36
2019-10-23 21:00 | 47.95 | 47.44
2019-10-23 21:30 | 45.22 | 44.67
2019-10-23 22:00 | 42.54 | 41.97
2019-10-23 22:30 | 40.72 | 40.16
2019-10-23 23:00 | 38.76 | 38.16
2019-10-23 23:30 | 36.8 | 36.16
2019-10-24 | 34.89 | 34.19
2019-10-24 00:30 | 33.89 | 33.16
2019-10-24 01:00 | 34.01 | 33.29
2019-10-24 01:30 | 32.55 | 31.79
2019-10-24 02:00 | 32.25 | 31.47
2019-10-24 02:30 | 31.92 | 31.13
2019-10-24 03:00 | 31.25 | 30.43
2019-10-24 03:30 | 30.8 | 29.95
2019-10-24 04:00 | 30.76 | 29.91
2019-10-24 04:30 | 31.72 | 30.91
2019-10-24 05:00 | 33.3 | 32.55
2019-10-24 05:30 | 35.21 | 34.51
2019-10-24 06:00 | 36.59 | 35.93
2019-10-24 06:30 | 41.12 | 40.59
2019-10-24 07:00 | 44.11 | 43.65
2019-10-24 07:30 | 50.11 | 49.59
2019-10-24 08:00 | 51.5 | 50.62
2019-10-24 08:30 | 51.66 | 50.38
2019-10-24 09:00 | 52.81 | 51.93
2019-10-24 09:30 | 52.57 | 51.05
2019-10-24 10:00 | 53.42 | 51.95
2019-10-24 10:30 | 53.31 | 51.85
2019-10-24 11:00 | 53.32 | 51.88
2019-10-24 11:30 | 51.85 | 50.36
2019-10-24 12:00 | 51.69 | 50.2
2019-10-24 12:30 | 50.59 | 49.06
2019-10-24 13:00 | 49.5 | 47.94
2019-10-24 13:30 | 50.35 | 48.81
2019-10-24 14:00 | 51.17 | 49.65
2019-10-24 14:30 | 51.7 | 50.21
2019-10-24 15:00 | 54.31 | 52.88
2019-10-24 15:30 | 54.17 | 52.72
2019-10-24 16:00 | 54.71 | 53.23
2019-10-24 16:30 | 55.73 | 54.21
2019-10-24 17:00 | 55.68 | 54.13
2019-10-24 17:30 | 54.39 | 52.73
2019-10-24 18:00 | 54.59 | 52.85
2019-10-24 18:30 | 55.35 | 53.63
2019-10-24 19:00 | 57.64 | 56.01
2019-10-24 19:30 | 57.03 | 55.37
2019-10-24 20:00 | 54.26 | 52.49
2019-10-24 20:30 | 51.39 | 49.47
2019-10-24 21:00 | 49.84 | 47.96
2019-10-24 21:30 | 47.89 | 45.92
2019-10-24 22:00 | 45.08 | 42.94
2019-10-24 22:30 | 42.97 | 40.83
2019-10-24 23:00 | 41.37 | 39.16
2019-10-24 23:30 | 38.88 | 36.49
2019-10-25 | 37.23 | 34.69
2019-10-25 00:30 | 36.73 | 34.16
2019-10-25 01:00 | 35.72 | 33.04
2019-10-25 01:30 | 35.03 | 32.29
2019-10-25 02:00 | 34.43 | 31.62
2019-10-25 02:30 | 33.4 | 30.44
2019-10-25 03:00 | 33.18 | 30.19
2019-10-25 03:30 | 33 | 29.97
2019-10-25 04:00 | 32.89 | 29.85
2019-10-25 04:30 | 33.44 | 30.46
2019-10-25 05:00 | 34.44 | 31.59
2019-10-25 05:30 | 36.22 | 33.54
2019-10-25 06:00 | 38.67 | 36.2
2019-10-25 06:30 | 42.09 | 39.94
2019-10-25 07:00 | 44.86 | 42.96
2019-10-25 07:30 | 48.54 | 46.9
2019-10-25 08:00 | 52.26 | 50.4
2019-10-25 08:30 | 52.59 | 50.53
2019-10-25 09:00 | 52.96 | 51.23
2019-10-25 09:30 | 52.1 | 50.17
2019-10-25 10:00 | 52.87 | 50.72
2019-10-25 10:30 | 53.53 | 51.08
2019-10-25 11:00 | 52.6 | 49.97
2019-10-25 11:30 | 52.13 | 49.48
2019-10-25 12:00 | 52.35 | 49.62
2019-10-25 12:30 | 52.56 | 49.95
2019-10-25 13:00 | 53.31 | 50.81
2019-10-25 13:30 | 52.99 | 50.61
2019-10-25 14:00 | 53.91 | 51.57
2019-10-25 14:30 | 55.66 | 53.61
2019-10-25 15:00 | 54.08 | 52.23
2019-10-25 15:30 | 54.23 | 52.77
2019-10-25 16:00 | 54.5 | 53.07
2019-10-25 16:30 | 54.91 | 53.44
2019-10-25 17:00 | 55.89 | 54.4
2019-10-25 17:30 | 54.35 | 52.74
2019-10-25 18:00 | 53.29 | 51.61
2019-10-25 18:30 | 54.49 | 52.85
2019-10-25 19:00 | 56.23 | 54.67
2019-10-25 19:30 | 54.33 | 52.69
2019-10-25 20:00 | 52.64 | 50.92
2019-10-25 20:30 | 50.73 | 48.91
2019-10-25 21:00 | 48.96 | 47.05
2019-10-25 21:30 | 47.38 | 45.37
2019-10-25 22:00 | 45.86 | 43.75
2019-10-25 22:30 | 44.54 | 42.36
2019-10-25 23:00 | 41.92 | 39.72
2019-10-25 23:30 | 40.18 | 37.84
2019-10-26 | 38.45 | 35.97
2019-10-26 00:30 | 38.29 | 35.79
2019-10-26 01:00 | 37.32 | 34.77
2019-10-26 01:30 | 36.81 | 34.2
2019-10-26 02:00 | 35.86 | 33.16
2019-10-26 02:30 | 36.17 | 33.49
2019-10-26 03:00 | 35.21 | 32.43
2019-10-26 03:30 | 34.77 | 31.95
2019-10-26 04:00 | 34.5 | 31.63
2019-10-26 04:30 | 35.4 | 32.61
2019-10-26 05:00 | 34.88 | 32.05
2019-10-26 05:30 | 35.28 | 32.46
2019-10-26 06:00 | 36.04 | 33.28
2019-10-26 06:30 | 36.67 | 34.01
2019-10-26 07:00 | 37.25 | 34.69
2019-10-26 07:30 | 38.66 | 36.27
2019-10-26 08:00 | 39.58 | 37.32
2019-10-26 08:30 | 40.47 | 38.33
2019-10-26 09:00 | 40.85 | 38.77
2019-10-26 09:30 | 40.79 | 38.75
2019-10-26 10:00 | 40.53 | 38.49
2019-10-26 10:30 | 37.82 | 35.52
2019-10-26 11:00 | 40.82 | 38.67
2019-10-26 11:30 | 40.93 | 38.78
2019-10-26 12:00 | 40.25 | 38.06
2019-10-26 12:30 | 39.42 | 37.15
2019-10-26 13:00 | 39 | 36.69
2019-10-26 13:30 | 39.31 | 37.02
2019-10-26 14:00 | 38.94 | 36.61
2019-10-26 14:30 | 39.72 | 37.42
2019-10-26 15:00 | 40.69 | 38.43
2019-10-26 15:30 | 41.69 | 39.47
2019-10-26 16:00 | 43.8 | 41.68
2019-10-26 16:30 | 44.89 | 42.78
2019-10-26 17:00 | 46.92 | 44.9
2019-10-26 17:30 | 47.4 | 45.4
2019-10-26 18:00 | 48.72 | 46.77
2019-10-26 18:30 | 50.12 | 48.23
2019-10-26 19:00 | 50.85 | 49.03
2019-10-26 19:30 | 50.31 | 48.45
2019-10-26 20:00 | 48.44 | 46.48
2019-10-26 20:30 | 47.21 | 45.17
2019-10-26 21:00 | 45.92 | 43.8
2019-10-26 21:30 | 44.8 | 42.61
2019-10-26 22:00 | 43.57 | 41.29
2019-10-26 22:30 | 42.09 | 39.81
2019-10-26 23:00 | 40.3 | 37.97
2019-10-26 23:30 | 38.81 | 36.35
2019-10-27 | 37.28 | 34.68
2019-10-27 00:30 | 36.83 | 34.18
2019-10-27 01:00 | 35.81 | 33.07
2019-10-27 01:30 | 35.22 | 32.42
2019-10-27 02:00 | 34.95 | 32.13
2019-10-27 02:30 | 34.49 | 31.6
2019-10-27 03:00 | 33.29 | 30.27
2019-10-27 03:30 | 33.09 | 30.03
2019-10-27 04:00 | 33.19 | 30.14
2019-10-27 04:30 | 31.76 | 30.47
2019-10-27 05:00 | 29.98 | 29.98
2019-10-27 05:30 | 30.66 | 30.66
2019-10-27 06:00 | 30.4 | 30.39
2019-10-27 06:30 | 31 | 31
2019-10-27 07:00 | 28.63 | 28.63
2019-10-27 07:30 | 27.72 | 27.69
2019-10-27 08:00 | 31.57 | 31.45
2019-10-27 08:30 | 32.24 | 32.04
2019-10-27 09:00 | 33.06 | 32.75
2019-10-27 09:30 | 34.41 | 34.01
2019-10-27 10:00 | 33.27 | 32.77
2019-10-27 10:30 | 33.54 | 32.86
2019-10-27 11:00 | 30.04 | 29.56
2019-10-27 11:30 | 33.07 | 32.4
2019-10-27 12:00 | 32.93 | 32.79
2019-10-27 12:30 | 32.67 | 32.53
2019-10-27 13:00 | 33.5 | 33.35
2019-10-27 13:30 | 34.33 | 34.16
2019-10-27 14:00 | 34.63 | 34.51
2019-10-27 14:30 | 35.14 | 35.04
2019-10-27 15:00 | 36.63 | 36.55
2019-10-27 15:30 | 38.14 | 38.08
2019-10-27 16:00 | 40.16 | 40.12
2019-10-27 16:30 | 42.19 | 42.16
2019-10-27 17:00 | 43.71 | 43.7
2019-10-27 17:30 | 45.67 | 45.66
2019-10-27 18:00 | 48.16 | 48.16
2019-10-27 18:30 | 49.53 | 49.53
2019-10-27 19:00 | 51.81 | 51.79
2019-10-27 19:30 | 50.14 | 50.13
2019-10-27 20:00 | 47.83 | 47.83
2019-10-27 20:30 | 46.14 | 46.14
2019-10-27 21:00 | 43.99 | 43.99
2019-10-27 21:30 | 41.98 | 41.91
2019-10-27 22:00 | 40.7 | 40.59
2019-10-27 22:30 | 38.69 | 38.62
2019-10-27 23:00 | 36.6 | 36.54
2019-10-27 23:30 | 34.45 | 34.42
2019-10-28 | 33.46 | 33.44
2019-10-28 00:30 | 33.41 | 33.4
2019-10-28 01:00 | 32.16 | 32.15
2019-10-28 01:30 | 31.6 | 31.59
2019-10-28 02:00 | 31.21 | 31.21
2019-10-28 02:30 | 30.87 | 30.87
2019-10-28 03:00 | 29.79 | 29.79
2019-10-28 03:30 | 29.81 | 29.81
2019-10-28 04:00 | 29.99 | 29.99
2019-10-28 04:30 | 30.93 | 30.93
2019-10-28 05:00 | 33.23 | 33.23
2019-10-28 05:30 | 34.24 | 34.22
2019-10-28 06:00 | 36.28 | 36.23
2019-10-28 06:30 | 40.26 | 40.01
2019-10-28 07:00 | 44.32 | 43.63
2019-10-28 07:30 | 50.78 | 48.9
2019-10-28 08:00 | 54.42 | 51.48
2019-10-28 08:30 | 56.28 | 53.68
2019-10-28 09:00 | 55.64 | 52.94
2019-10-28 09:30 | 55.62 | 52.72
2019-10-28 10:00 | 56.91 | 53.71
2019-10-28 10:30 | 56.62 | 53.13
2019-10-28 11:00 | 58.88 | 55.05
2019-10-28 11:30 | 57.99 | 54.01
2019-10-28 12:00 | 59.85 | 55.96
2019-10-28 12:30 | 59.25 | 55.38
2019-10-28 13:00 | 57.71 | 53.84
2019-10-28 13:30 | 60.58 | 55.69
2019-10-28 14:00 | 62.12 | 56.64
2019-10-28 14:30 | 62.97 | 57.58
2019-10-28 15:00 | 62.75 | 57.31
2019-10-28 15:30 | 63.68 | 58.27
2019-10-28 16:00 | 66.01 | 60.73
2019-10-28 16:30 | 65.88 | 60.48
2019-10-28 17:00 | 65.38 | 59.79
2019-10-28 17:30 | 63.88 | 57.94
2019-10-28 18:00 | 63.77 | 57.67
2019-10-28 18:30 | 63.66 | 57.52
2019-10-28 19:00 | 64.4 | 58.38
2019-10-28 19:30 | 63.81 | 57.71
2019-10-28 20:00 | 61.43 | 54.98
2019-10-28 20:30 | 59.32 | 52.52
2019-10-28 21:00 | 57.76 | 50.67
2019-10-28 21:30 | 50.38 | 47.57
2019-10-28 22:00 | 47.46 | 45.57
2019-10-28 22:30 | 45.04 | 43.11
2019-10-28 23:00 | 42.76 | 40.73
2019-10-28 23:30 | 40.86 | 38.7
2019-10-29 | 39.53 | 37.28
2019-10-29 00:30 | 40.29 | 38.08
2019-10-29 01:00 | 39 | 36.7
2019-10-29 01:30 | 37.94 | 35.57
2019-10-29 02:00 | 37.14 | 34.72
2019-10-29 02:30 | 37.17 | 34.74
2019-10-29 03:00 | 36.6 | 34.11
2019-10-29 03:30 | 37.66 | 35.24
2019-10-29 04:00 | 36.4 | 33.89
2019-10-29 04:30 | 37.27 | 34.83
2019-10-29 05:00 | 38.54 | 36.2
2019-10-29 05:30 | 40.01 | 37.8
2019-10-29 06:00 | 42.28 | 40.22
2019-10-29 06:30 | 46.45 | 44.68
2019-10-29 07:00 | 46.14 | 44.34
2019-10-29 07:30 | 41.91 | 39.93
2019-10-29 08:00 | 43.9 | 41.97
2019-10-29 08:30 | 46.91 | 45.1
2019-10-29 09:00 | 43.99 | 42.06
2019-10-29 09:30 | 41.92 | 40.22
2019-10-29 10:00 | 41.37 | 40.14
2019-10-29 10:30 | 40.68 | 39.35
2019-10-29 11:00 | 39.28 | 37.73
2019-10-29 11:30 | 39.13 | 37.58
2019-10-29 12:00 | 40.17 | 38.66
2019-10-29 12:30 | 39.95 | 38.4
2019-10-29 13:00 | 39.48 | 37.93
2019-10-29 13:30 | 39.93 | 38.42
2019-10-29 14:00 | 44.22 | 42.93
2019-10-29 14:30 | 45.67 | 44.46
2019-10-29 15:00 | 46.48 | 45.4
2019-10-29 15:30 | 44.68 | 43.68
2019-10-29 16:00 | 44.67 | 43.76
2019-10-29 16:30 | 45.1 | 44.38
2019-10-29 17:00 | 43.91 | 43.4
2019-10-29 17:30 | 43.05 | 42.79
2019-10-29 18:00 | 43.09 | 42.95
2019-10-29 18:30 | 44.05 | 43.91
2019-10-29 19:00 | 44.82 | 44.7
2019-10-29 19:30 | 44.1 | 44
2019-10-29 20:00 | 41.73 | 41.66
2019-10-29 20:30 | 39.17 | 39.13
2019-10-29 21:00 | 37.31 | 37.29
2019-10-29 21:30 | 35.76 | 35.75
2019-10-29 22:00 | 33.99 | 33.99
2019-10-29 22:30 | 31.91 | 31.9
2019-10-29 23:00 | 30.42 | 30.25
2019-10-29 23:30 | 29.72 | 29.56
2019-10-30 | 28.52 | 28.37
2019-10-30 00:30 | 31.02 | 30.88
2019-10-30 01:00 | 27.47 | 27.36
2019-10-30 01:30 | 26.13 | 26.03
2019-10-30 02:00 | 25.47 | 25.38
2019-10-30 02:30 | 25.11 | 25.02
2019-10-30 03:00 | 24.67 | 24.6
2019-10-30 03:30 | 24.32 | 24.25
2019-10-30 04:00 | 24.88 | 24.79
2019-10-30 04:30 | 26.45 | 26.34
2019-10-30 05:00 | 26.89 | 26.75
2019-10-30 05:30 | 27.84 | 27.7
2019-10-30 06:00 | 29.35 | 29.18
2019-10-30 06:30 | 33.33 | 32.98
2019-10-30 07:00 | 34.92 | 34.41
2019-10-30 07:30 | 38.99 | 38.11
2019-10-30 08:00 | 39.24 | 38.69
2019-10-30 08:30 | 41.8 | 41.05
2019-10-30 09:00 | 41.22 | 40.14
2019-10-30 09:30 | 40.82 | 39.57
2019-10-30 10:00 | 41.48 | 40.19
2019-10-30 10:30 | 41.61 | 40.24
2019-10-30 11:00 | 43.53 | 42.21
2019-10-30 11:30 | 43.07 | 41.61
2019-10-30 12:00 | 42.76 | 41.29
2019-10-30 12:30 | 44.76 | 43.5
2019-10-30 13:00 | 44.19 | 43
2019-10-30 13:30 | 45.08 | 43.94
2019-10-30 14:00 | 44.16 | 43.13
2019-10-30 14:30 | 42.57 | 41.52
2019-10-30 15:00 | 40.92 | 39.84
2019-10-30 15:30 | 40.78 | 39.78
2019-10-30 16:00 | 41.52 | 40.6
2019-10-30 16:30 | 44.06 | 43.31
2019-10-30 17:00 | 43.57 | 43.05
2019-10-30 17:30 | 43.44 | 43.12
2019-10-30 18:00 | 44.33 | 44.14
2019-10-30 18:30 | 44.64 | 44.5
2019-10-30 19:00 | 45.52 | 45.37
2019-10-30 19:30 | 44.04 | 43.9
2019-10-30 20:00 | 41.99 | 41.9
2019-10-30 20:30 | 41.57 | 41.5
2019-10-30 21:00 | 39.03 | 38.99
2019-10-30 21:30 | 37.2 | 37.17
2019-10-30 22:00 | 34.96 | 34.95
2019-10-30 22:30 | 33.81 | 33.75
2019-10-30 23:00 | 31.62 | 31.38
2019-10-30 23:30 | 30.16 | 29.95
2019-10-31 | 30.26 | 30.08
2019-10-31 00:30 | 29.41 | 29.26
2019-10-31 01:00 | 27.95 | 27.8
2019-10-31 01:30 | 28.14 | 28
2019-10-31 02:00 | 27.27 | 27.15
2019-10-31 02:30 | 26.42 | 26.32
2019-10-31 03:00 | 25.53 | 25.46
2019-10-31 03:30 | 26.61 | 26.54
2019-10-31 04:00 | 26.21 | 26.13
2019-10-31 04:30 | 25.97 | 25.88
2019-10-31 05:00 | 26.6 | 26.5
2019-10-31 05:30 | 25.65 | 25.56
2019-10-31 06:00 | 25.6 | 25.49
2019-10-31 06:30 | 28.73 | 28.5
2019-10-31 07:00 | 34.86 | 34.41
2019-10-31 07:30 | 37.44 | 36.65
2019-10-31 08:00 | 39.87 | 39.13
2019-10-31 08:30 | 38.43 | 37.89
2019-10-31 09:00 | 36.96 | 36.15
2019-10-31 09:30 | 39.81 | 38.69
2019-10-31 10:00 | 40.96 | 39.77
2019-10-31 10:30 | 39.58 | 38.34
2019-10-31 11:00 | 40.6 | 39.31
2019-10-31 11:30 | 40.49 | 39.12
2019-10-31 12:00 | 39.85 | 38.41
2019-10-31 12:30 | 39.21 | 37.79
2019-10-31 13:00 | 39.02 | 37.59
2019-10-31 13:30 | 40.35 | 38.84
2019-10-31 14:00 | 42.37 | 40.97
2019-10-31 14:30 | 45.06 | 43.72
2019-10-31 15:00 | 46.74 | 45.55
2019-10-31 15:30 | 47.82 | 46.86
2019-10-31 16:00 | 46.82 | 46.02
2019-10-31 16:30 | 46.53 | 45.88
2019-10-31 17:00 | 44.4 | 43.95
2019-10-31 17:30 | 41.79 | 41.52
2019-10-31 18:00 | 43.02 | 42.84
2019-10-31 18:30 | 43.35 | 43.21
2019-10-31 19:00 | 44.03 | 43.9
2019-10-31 19:30 | 42.71 | 42.59
2019-10-31 20:00 | 41.6 | 41.52
2019-10-31 20:30 | 40.27 | 40.22
2019-10-31 21:00 | 39.59 | 39.55
2019-10-31 21:30 | 36.03 | 36.01
2019-10-31 22:00 | 34.72 | 34.71
2019-10-31 22:30 | 32.13 | 32.12
2019-10-31 23:00 | 30.63 | 30.42
2019-10-31 23:30 | 29.66 | 29.48
2019-11-01 | 27.75 | 27.59
2019-11-01 00:30 | 29.44 | 29.3
2019-11-01 01:00 | 27.34 | 27.22
2019-11-01 01:30 | 25.79 | 25.69
2019-11-01 02:00 | 25.16 | 25.08
2019-11-01 02:30 | 24.55 | 24.47
2019-11-01 03:00 | 23.98 | 23.93
2019-11-01 03:30 | 24.49 | 24.44
2019-11-01 04:00 | 24.21 | 24.15
2019-11-01 04:30 | 26.25 | 26.19
2019-11-01 05:00 | 26.97 | 26.88
2019-11-01 05:30 | 26.99 | 26.87
2019-11-01 06:00 | 29.4 | 29.28
2019-11-01 06:30 | 32.89 | 32.64
2019-11-01 07:00 | 34.63 | 34.23
2019-11-01 07:30 | 33.99 | 32.93
2019-11-01 08:00 | 34.68 | 33.76
2019-11-01 08:30 | 38.83 | 38.13
2019-11-01 09:00 | 38.92 | 38
2019-11-01 09:30 | 38.75 | 37.69
2019-11-01 10:00 | 38.36 | 37.27
2019-11-01 10:30 | 38.46 | 37.23
2019-11-01 11:00 | 41.78 | 40.58
2019-11-01 11:30 | 42.31 | 40.96
2019-11-01 12:00 | 39.8 | 38.33
2019-11-01 12:30 | 39.46 | 37.9
2019-11-01 13:00 | 41.68 | 40.26
2019-11-01 13:30 | 42.3 | 41.02
2019-11-01 14:00 | 41.87 | 40.5
2019-11-01 14:30 | 42.04 | 40.67
2019-11-01 15:00 | 42.32 | 41.1
2019-11-01 15:30 | 42.31 | 41.35
2019-11-01 16:00 | 42.72 | 41.93
2019-11-01 16:30 | 44.6 | 43.94
2019-11-01 17:00 | 45.62 | 45.1
2019-11-01 17:30 | 45.15 | 44.84
2019-11-01 18:00 | 44.58 | 44.41
2019-11-01 18:30 | 45.19 | 45.04
2019-11-01 19:00 | 46.27 | 46.1
2019-11-01 19:30 | 45.14 | 45.01
2019-11-01 20:00 | 43.48 | 43.37
2019-11-01 20:30 | 41.41 | 41.33
2019-11-01 21:00 | 40.29 | 40.24
2019-11-01 21:30 | 38.33 | 38.29
2019-11-01 22:00 | 36.97 | 36.96
2019-11-01 22:30 | 35.98 | 35.98
2019-11-01 23:00 | 34.46 | 34.46
2019-11-01 23:30 | 33.1 | 33.02
2019-11-02 | 31.71 | 31.52
2019-11-02 00:30 | 33.16 | 32.99
2019-11-02 01:00 | 31.37 | 31.21
2019-11-02 01:30 | 29.71 | 29.56
2019-11-02 02:00 | 28.38 | 28.26
2019-11-02 02:30 | 27.84 | 27.73
2019-11-02 03:00 | 27.74 | 27.63
2019-11-02 03:30 | 27.36 | 27.26
2019-11-02 04:00 | 26.98 | 26.88
2019-11-02 04:30 | 27.28 | 27.19
2019-11-02 05:00 | 27.36 | 27.25
2019-11-02 05:30 | 27.39 | 27.32
2019-11-02 06:00 | 27.91 | 27.85
2019-11-02 06:30 | 29.62 | 29.51
2019-11-02 07:00 | 29.87 | 29.71
2019-11-02 07:30 | 31.56 | 31.28
2019-11-02 08:00 | 32.28 | 31.82
2019-11-02 08:30 | 36.87 | 36.26
2019-11-02 09:00 | 35.51 | 34.71
2019-11-02 09:30 | 34.15 | 33.4
2019-11-02 10:00 | 34.99 | 34.69
2019-11-02 10:30 | 32.55 | 32.15
2019-11-02 11:00 | 31.73 | 31.31
2019-11-02 11:30 | 32.07 | 31.63
2019-11-02 12:00 | 31.56 | 31.12
2019-11-02 12:30 | 31.48 | 31.08
2019-11-02 13:00 | 31.43 | 31.04
2019-11-02 13:30 | 29.18 | 28.82
2019-11-02 14:00 | 29.39 | 29.03
2019-11-02 14:30 | 29.49 | 29.2
2019-11-02 15:00 | 30.76 | 30.54
2019-11-02 15:30 | 31.78 | 31.6
2019-11-02 16:00 | 33.43 | 33.27
2019-11-02 16:30 | 34.45 | 34.36
2019-11-02 17:00 | 37.26 | 37.2
2019-11-02 17:30 | 39.66 | 39.59
2019-11-02 18:00 | 41.66 | 41.58
2019-11-02 18:30 | 42.61 | 42.53
2019-11-02 19:00 | 43.38 | 43.26
2019-11-02 19:30 | 42.67 | 42.57
2019-11-02 20:00 | 41.32 | 41.23
2019-11-02 20:30 | 40.54 | 40.47
2019-11-02 21:00 | 38.9 | 38.85
2019-11-02 21:30 | 37.39 | 37.36
2019-11-02 22:00 | 36.13 | 36.11
2019-11-02 22:30 | 34.92 | 34.92
2019-11-02 23:00 | 33.67 | 33.67
2019-11-02 23:30 | 32.06 | 32.06
2019-11-03 | 31.08 | 31.03
2019-11-03 00:30 | 30.83 | 30.65
2019-11-03 01:00 | 29.69 | 29.53
2019-11-03 01:30 | 28.67 | 28.51
2019-11-03 02:00 | 28.05 | 27.91
2019-11-03 02:30 | 27.79 | 27.66
2019-11-03 03:00 | 26.99 | 26.88
2019-11-03 03:30 | 26.93 | 26.83
2019-11-03 04:00 | 26.66 | 26.56
2019-11-03 04:30 | 27.29 | 27.19
2019-11-03 05:00 | 26.97 | 26.88
2019-11-03 05:30 | 26.6 | 26.53
2019-11-03 06:00 | 26.98 | 26.91
2019-11-03 06:30 | 27.74 | 27.64
2019-11-03 07:00 | 27.22 | 27.08
2019-11-03 07:30 | 28.11 | 27.88
2019-11-03 08:00 | 29.08 | 28.69
2019-11-03 08:30 | 29.29 | 28.8
2019-11-03 09:00 | 28.75 | 28.23
2019-11-03 09:30 | 29.08 | 28.44
2019-11-03 10:00 | 30 | 29.88
2019-11-03 10:30 | 29.42 | 29.24
2019-11-03 11:00 | 29.46 | 29.25
2019-11-03 11:30 | 29.81 | 29.58
2019-11-03 12:00 | 30.14 | 29.87
2019-11-03 12:30 | 30.38 | 30.12
2019-11-03 13:00 | 30.84 | 30.56
2019-11-03 13:30 | 31.38 | 31.13
2019-11-03 14:00 | 31.99 | 31.79
2019-11-03 14:30 | 31.81 | 31.62
2019-11-03 15:00 | 32.4 | 32.26
2019-11-03 15:30 | 33.78 | 33.66
2019-11-03 16:00 | 35.6 | 35.49
2019-11-03 16:30 | 37.01 | 36.92
2019-11-03 17:00 | 37.29 | 37.23
2019-11-03 17:30 | 38.29 | 38.24
2019-11-03 18:00 | 40.51 | 40.45
2019-11-03 18:30 | 41.38 | 41.33
2019-11-03 19:00 | 42.6 | 42.51
2019-11-03 19:30 | 42.51 | 42.43
2019-11-03 20:00 | 40.51 | 40.45
2019-11-03 20:30 | 38.74 | 38.7
2019-11-03 21:00 | 37.4 | 37.37
2019-11-03 21:30 | 35.56 | 35.55
2019-11-03 22:00 | 33.8 | 33.79
2019-11-03 22:30 | 31.8 | 31.75
2019-11-03 23:00 | 30.39 | 30.17
2019-11-03 23:30 | 29.27 | 29.06
2019-11-04 | 28.36 | 28.19
2019-11-04 00:30 | 28.36 | 28.21
2019-11-04 01:00 | 27.28 | 27.14
2019-11-04 01:30 | 26.49 | 26.36
2019-11-04 02:00 | 26.07 | 25.94
2019-11-04 02:30 | 25.64 | 25.53
2019-11-04 03:00 | 25.24 | 25.14
2019-11-04 03:30 | 25.04 | 24.93
2019-11-04 04:00 | 25.18 | 25.06
2019-11-04 04:30 | 25.71 | 25.59
2019-11-04 05:00 | 26.49 | 26.33
2019-11-04 05:30 | 27.31 | 27.17
2019-11-04 06:00 | 28.51 | 28.33
2019-11-04 06:30 | 31.85 | 31.46
2019-11-04 07:00 | 34.4 | 33.76
2019-11-04 07:30 | 38.21 | 37.05
2019-11-04 08:00 | 40.32 | 39.43
2019-11-04 08:30 | 41.41 | 40.46
2019-11-04 09:00 | 41.92 | 40.73
2019-11-04 09:30 | 42.13 | 40.73
2019-11-04 10:00 | 41.84 | 40.37
2019-11-04 10:30 | 41.62 | 40.09
2019-11-04 11:00 | 42.03 | 40.32
2019-11-04 11:30 | 42.28 | 40.52
2019-11-04 12:00 | 42.41 | 40.57
2019-11-04 12:30 | 42.39 | 40.6
2019-11-04 13:00 | 42.11 | 40.34
2019-11-04 13:30 | 42.03 | 40.32
2019-11-04 14:00 | 42.8 | 41.1
2019-11-04 14:30 | 43.57 | 41.89
2019-11-04 15:00 | 44.06 | 42.45
2019-11-04 15:30 | 44.8 | 43.41
2019-11-04 16:00 | 45.86 | 44.6
2019-11-04 16:30 | 47.01 | 45.96
2019-11-04 17:00 | 47.49 | 46.66
2019-11-04 17:30 | 46.78 | 46.3
2019-11-04 18:00 | 47.33 | 47.03
2019-11-04 18:30 | 47.69 | 47.45
2019-11-04 19:00 | 49.8 | 49.62
2019-11-04 19:30 | 48.93 | 48.79
2019-11-04 20:00 | 46.59 | 46.5
2019-11-04 20:30 | 45.11 | 45.02
2019-11-04 21:00 | 42.33 | 42.27
2019-11-04 21:30 | 39.24 | 39.2
2019-11-04 22:00 | 35.68 | 35.67
2019-11-04 22:30 | 34.04 | 34.04
2019-11-04 23:00 | 31.23 | 31.12
2019-11-04 23:30 | 29.51 | 29.34
2019-11-05 | 28.06 | 27.9
2019-11-05 00:30 | 27.71 | 27.58
2019-11-05 01:00 | 31.17 | 30.96
2019-11-05 01:30 | 33.24 | 32.96
2019-11-05 02:00 | 26.8 | 26.68
2019-11-05 02:30 | 25.8 | 25.69
2019-11-05 03:00 | 26 | 25.91
2019-11-05 03:30 | 25.86 | 25.77
2019-11-05 04:00 | 25.34 | 25.25
2019-11-05 04:30 | 26.83 | 26.72
2019-11-05 05:00 | 27.03 | 26.9
2019-11-05 05:30 | 27.38 | 27.25
2019-11-05 06:00 | 28.72 | 28.56
2019-11-05 06:30 | 31.69 | 31.36
2019-11-05 07:00 | 34.17 | 33.57
2019-11-05 07:30 | 37.72 | 36.72
2019-11-05 08:00 | 39.57 | 39
2019-11-05 08:30 | 40.78 | 39.91
2019-11-05 09:00 | 41.48 | 40.34
2019-11-05 09:30 | 43.26 | 41.81
2019-11-05 10:00 | 43.22 | 41.69
2019-11-05 10:30 | 41.1 | 39.16
2019-11-05 11:00 | 43.8 | 41.95
2019-11-05 11:30 | 43.2 | 41.38
2019-11-05 12:00 | 43.23 | 41.32
2019-11-05 12:30 | 43.25 | 41.31
2019-11-05 13:00 | 44.04 | 42.14
2019-11-05 13:30 | 44.1 | 42.28
2019-11-05 14:00 | 43.85 | 42.06
2019-11-05 14:30 | 44.1 | 42.38
2019-11-05 15:00 | 58.2 | 54.87
2019-11-05 15:30 | 63.08 | 59.67
2019-11-05 16:00 | 64.38 | 61.53
2019-11-05 16:30 | 64.85 | 62.5
2019-11-05 17:00 | 64.35 | 62.47
2019-11-05 17:30 | 61.74 | 60.52
2019-11-05 18:00 | 59.52 | 58.7
2019-11-05 18:30 | 58.33 | 57.67
2019-11-05 19:00 | 60.02 | 59.28
2019-11-05 19:30 | 58.69 | 58.04
2019-11-05 20:00 | 56.31 | 55.74
2019-11-05 20:30 | 53.84 | 53.4
2019-11-05 21:00 | 51.62 | 51.23
2019-11-05 21:30 | 48.74 | 48.45
2019-11-05 22:00 | 45.96 | 45.75
2019-11-05 22:30 | 43.66 | 43.51
2019-11-05 23:00 | 41.49 | 41.09
2019-11-05 23:30 | 39.95 | 39.38
2019-11-06 | 39.01 | 38.5
2019-11-06 00:30 | 39.02 | 38.56
2019-11-06 01:00 | 36.43 | 36.03
2019-11-06 01:30 | 34.71 | 34.34
2019-11-06 02:00 | 34.33 | 33.99
2019-11-06 02:30 | 33.19 | 32.88
2019-11-06 03:00 | 32.7 | 32.41
2019-11-06 03:30 | 33.35 | 33.05
2019-11-06 04:00 | 32.48 | 32.21
2019-11-06 04:30 | 32.95 | 32.72
2019-11-06 05:00 | 33.43 | 33.18
2019-11-06 05:30 | 34.41 | 34.16
2019-11-06 06:00 | 36.61 | 36.26
2019-11-06 06:30 | 40.98 | 40.26
2019-11-06 07:00 | 43.95 | 42.69
2019-11-06 07:30 | 48.11 | 46.01
2019-11-06 08:00 | 49.58 | 47.32
2019-11-06 08:30 | 49.47 | 47.46
2019-11-06 09:00 | 49.78 | 47.34
2019-11-06 09:30 | 49.85 | 46.95
2019-11-06 10:00 | 49.63 | 46.42
2019-11-06 10:30 | 49.52 | 46.22
2019-11-06 11:00 | 49.52 | 45.97
2019-11-06 11:30 | 50 | 46.39
2019-11-06 12:00 | 50.32 | 46.53
2019-11-06 12:30 | 50.21 | 46.42
2019-11-06 13:00 | 49.87 | 46.28
2019-11-06 13:30 | 50.65 | 47.03
2019-11-06 14:00 | 51.36 | 47.82
2019-11-06 14:30 | 52.62 | 49.38
2019-11-06 15:00 | 53.06 | 49.95
2019-11-06 15:30 | 53.41 | 50.65
2019-11-06 16:00 | 55.25 | 52.94
2019-11-06 16:30 | 54.87 | 53.08
2019-11-06 17:00 | 55.55 | 54.11
2019-11-06 17:30 | 54.36 | 53.46
2019-11-06 18:00 | 53.36 | 52.79
2019-11-06 18:30 | 53.42 | 53.02
2019-11-06 19:00 | 55.38 | 54.88
2019-11-06 19:30 | 54.59 | 54.17
2019-11-06 20:00 | 51.36 | 51
2019-11-06 20:30 | 49.97 | 49.62
2019-11-06 21:00 | 48.21 | 47.93
2019-11-06 21:30 | 45 | 44.83
2019-11-06 22:00 | 42.69 | 42.57
2019-11-06 22:30 | 40.65 | 40.09
2019-11-06 23:00 | 38.1 | 37.6
2019-11-06 23:30 | 36.6 | 36.15
2019-11-07 | 36.12 | 35.71
2019-11-07 00:30 | 37.51 | 37.15
2019-11-07 01:00 | 34.24 | 33.93
2019-11-07 01:30 | 32.68 | 32.39
2019-11-07 02:00 | 31.95 | 31.68
2019-11-07 02:30 | 31.3 | 31.04
2019-11-07 03:00 | 30.63 | 30.42
2019-11-07 03:30 | 30.33 | 30.13
2019-11-07 04:00 | 30.33 | 30.12
2019-11-07 04:30 | 31.16 | 30.97
2019-11-07 05:00 | 32.34 | 32.1
2019-11-07 05:30 | 34.05 | 33.8
2019-11-07 06:00 | 37.32 | 36.98
2019-11-07 06:30 | 40.2 | 39.52
2019-11-07 07:00 | 44.17 | 43
2019-11-07 07:30 | 49.62 | 47.5
2019-11-07 08:00 | 51.17 | 48.55
2019-11-07 08:30 | 51.71 | 49.47
2019-11-07 09:00 | 53.39 | 50.53
2019-11-07 09:30 | 54.63 | 51.57
2019-11-07 10:00 | 54.58 | 51.29
2019-11-07 10:30 | 54.83 | 51.16
2019-11-07 11:00 | 55.85 | 51.8
2019-11-07 11:30 | 56.72 | 52.51
2019-11-07 12:00 | 57.45 | 53.05
2019-11-07 12:30 | 57.46 | 53.21
2019-11-07 13:00 | 58.3 | 54.19
2019-11-07 13:30 | 59.06 | 54.95
2019-11-07 14:00 | 59.96 | 55.93
2019-11-07 14:30 | 60.83 | 56.92
2019-11-07 15:00 | 61.04 | 57.27
2019-11-07 15:30 | 61.59 | 58.15
2019-11-07 16:00 | 61.87 | 58.94
2019-11-07 16:30 | 61.34 | 59.05
2019-11-07 17:00 | 61.34 | 59.6
2019-11-07 17:30 | 58.6 | 57.43
2019-11-07 18:00 | 58.66 | 57.79
2019-11-07 18:30 | 58.87 | 58.17
2019-11-07 19:00 | 60.58 | 59.8
2019-11-07 19:30 | 58.93 | 58.25
2019-11-07 20:00 | 55.79 | 55.25
2019-11-07 20:30 | 54.38 | 53.91
2019-11-07 21:00 | 52.71 | 52.29
2019-11-07 21:30 | 49.32 | 49
2019-11-07 22:00 | 47.52 | 47.28
2019-11-07 22:30 | 44.63 | 44.07
2019-11-07 23:00 | 42.47 | 41.74
2019-11-07 23:30 | 40.84 | 40.14
2019-11-08 | 40.24 | 39.61
2019-11-08 00:30 | 39.52 | 38.99
2019-11-08 01:00 | 38.03 | 37.54
2019-11-08 01:30 | 35.48 | 35.02
2019-11-08 02:00 | 33.99 | 33.56
2019-11-08 02:30 | 34.52 | 34.12
2019-11-08 03:00 | 34.28 | 33.92
2019-11-08 03:30 | 32.82 | 32.47
2019-11-08 04:00 | 32.71 | 32.38
2019-11-08 04:30 | 33.92 | 33.59
2019-11-08 05:00 | 34.77 | 34.42
2019-11-08 05:30 | 36.53 | 36.17
2019-11-08 06:00 | 37.97 | 37.5
2019-11-08 06:30 | 42.45 | 41.62
2019-11-08 07:00 | 46.07 | 44.7
2019-11-08 07:30 | 50.93 | 48.66
2019-11-08 08:00 | 53.42 | 50.35
2019-11-08 08:30 | 53.55 | 50.96
2019-11-08 09:00 | 53.69 | 50.74
2019-11-08 09:30 | 54.09 | 50.95
2019-11-08 10:00 | 55.19 | 51.86
2019-11-08 10:30 | 57.52 | 52.31
2019-11-08 11:00 | 61 | 52.61
2019-11-08 11:30 | 61.86 | 53.59
2019-11-08 12:00 | 62.44 | 54.29
2019-11-08 12:30 | 62.62 | 54.51
2019-11-08 13:00 | 62.9 | 54.81
2019-11-08 13:30 | 63.28 | 55.27
2019-11-08 14:00 | 64.73 | 56.23
2019-11-08 14:30 | 67.22 | 56.74
2019-11-08 15:00 | 66.9 | 56.33
2019-11-08 15:30 | 67.77 | 57.32
2019-11-08 16:00 | 70.3 | 58.19
2019-11-08 16:30 | 73.07 | 61.74
2019-11-08 17:00 | 61.42 | 60.92
2019-11-08 17:30 | 59.61 | 58.99
2019-11-08 18:00 | 58.68 | 58.25
2019-11-08 18:30 | 57.83 | 57.48
2019-11-08 19:00 | 58.14 | 57.78
2019-11-08 19:30 | 56.8 | 56.44
2019-11-08 20:00 | 55.47 | 55.1
2019-11-08 20:30 | 53.83 | 53.43
2019-11-08 21:00 | 52.89 | 52.48
2019-11-08 21:30 | 50.1 | 49.67
2019-11-08 22:00 | 47.72 | 47.27
2019-11-08 22:30 | 45.38 | 44.4
2019-11-08 23:00 | 44.39 | 42.66
2019-11-08 23:30 | 42.23 | 40.39
2019-11-09 | 40.97 | 39.06
2019-11-09 00:30 | 39.96 | 38
2019-11-09 01:00 | 38.16 | 36.1
2019-11-09 01:30 | 37.24 | 35.12
2019-11-09 02:00 | 37.23 | 35.11
2019-11-09 02:30 | 37.75 | 35.65
2019-11-09 03:00 | 36.01 | 33.8
2019-11-09 03:30 | 35.27 | 33.01
2019-11-09 04:00 | 35.47 | 33.22
2019-11-09 04:30 | 34.89 | 32.6
2019-11-09 05:00 | 36.06 | 33.85
2019-11-09 05:30 | 35.6 | 33.36
2019-11-09 06:00 | 36.6 | 34.44
2019-11-09 06:30 | 37.7 | 35.59
2019-11-09 07:00 | 38.63 | 36.58
2019-11-09 07:30 | 40.43 | 38.47
2019-11-09 08:00 | 41.19 | 39.27
2019-11-09 08:30 | 42.35 | 40.49
2019-11-09 09:00 | 43.85 | 42.06
2019-11-09 09:30 | 44.69 | 42.94
2019-11-09 10:00 | 44.93 | 43.19
2019-11-09 10:30 | 45.52 | 43.81
2019-11-09 11:00 | 46.91 | 45.25
2019-11-09 11:30 | 47.05 | 45.4
2019-11-09 12:00 | 47.11 | 45.47
2019-11-09 12:30 | 46.15 | 44.48
2019-11-09 13:00 | 46.24 | 44.56
2019-11-09 13:30 | 46.72 | 45.07
2019-11-09 14:00 | 46.06 | 44.38
2019-11-09 14:30 | 46.51 | 44.85
2019-11-09 15:00 | 48.77 | 47.19
2019-11-09 15:30 | 49.91 | 48.38
2019-11-09 16:00 | 51.59 | 50.12
2019-11-09 16:30 | 51.53 | 50.06
2019-11-09 17:00 | 54.08 | 52.7
2019-11-09 17:30 | 54.36 | 53
2019-11-09 18:00 | 54.61 | 54.06
2019-11-09 18:30 | 54.9 | 54.55
2019-11-09 19:00 | 56.57 | 56.24
2019-11-09 19:30 | 55.02 | 54.68
2019-11-09 20:00 | 53.05 | 52.69
2019-11-09 20:30 | 50.78 | 50.4
2019-11-09 21:00 | 49 | 48.6
2019-11-09 21:30 | 46.44 | 46.02
2019-11-09 22:00 | 44.51 | 44.07
2019-11-09 22:30 | 42.85 | 42.38
2019-11-09 23:00 | 41.44 | 40.95
2019-11-09 23:30 | 40.05 | 39.55
2019-11-10 | 37.83 | 37.29
2019-11-10 00:30 | 36.15 | 35.59
2019-11-10 01:00 | 35.59 | 35.01
2019-11-10 01:30 | 34.66 | 34.07
2019-11-10 02:00 | 34.21 | 33.62
2019-11-10 02:30 | 33.53 | 32.93
2019-11-10 03:00 | 32.61 | 32
2019-11-10 03:30 | 33.32 | 32.72
2019-11-10 04:00 | 33.7 | 33.11
2019-11-10 04:30 | 33.14 | 32.54
2019-11-10 05:00 | 32.77 | 32.16
2019-11-10 05:30 | 31.77 | 31.14
2019-11-10 06:00 | 31.26 | 30.62
2019-11-10 06:30 | 31.33 | 30.69
2019-11-10 07:00 | 31.56 | 30.92
2019-11-10 07:30 | 31.78 | 31.14
2019-11-10 08:00 | 31.93 | 31.29
2019-11-10 08:30 | 32.94 | 32.32
2019-11-10 09:00 | 33.42 | 32.81
2019-11-10 09:30 | 33.36 | 32.74
2019-11-10 10:00 | 32.37 | 31.74
2019-11-10 10:30 | 32 | 31.37
2019-11-10 11:00 | 32.32 | 31.65
2019-11-10 11:30 | 32.28 | 31.56
2019-11-10 12:00 | 32.9 | 32.25
2019-11-10 12:30 | 33.67 | 33.07
2019-11-10 13:00 | 33.24 | 32.63
2019-11-10 13:30 | 33.71 | 33.12
2019-11-10 14:00 | 34.74 | 34.16
2019-11-10 14:30 | 35.64 | 35.08
2019-11-10 15:00 | 36.27 | 35.72
2019-11-10 15:30 | 37.53 | 37.01
2019-11-10 16:00 | 40.14 | 39.65
2019-11-10 16:30 | 42.19 | 41.72
2019-11-10 17:00 | 45.29 | 44.85
2019-11-10 17:30 | 46.23 | 45.8
2019-11-10 18:00 | 48.47 | 48.07
2019-11-10 18:30 | 50.43 | 50.05
2019-11-10 19:00 | 52.7 | 52.33
2019-11-10 19:30 | 51.38 | 51.01
2019-11-10 20:00 | 49.18 | 48.78
2019-11-10 20:30 | 47.73 | 47.32
2019-11-10 21:00 | 46.44 | 46.02
2019-11-10 21:30 | 43.9 | 43.45
2019-11-10 22:00 | 41.77 | 41.29
2019-11-10 22:30 | 38.91 | 38.39
2019-11-10 23:00 | 38.14 | 37.61
2019-11-10 23:30 | 35.82 | 35.25
2019-11-11 | 34.83 | 34.24
2019-11-11 00:30 | 33.38 | 32.76
2019-11-11 01:00 | 32.42 | 31.78
2019-11-11 01:30 | 32.17 | 31.54
2019-11-11 02:00 | 32.87 | 32.25
2019-11-11 02:30 | 31.25 | 30.59
2019-11-11 03:00 | 30.88 | 30.21
2019-11-11 03:30 | 31.38 | 30.72
2019-11-11 04:00 | 31.96 | 31.32
2019-11-11 04:30 | 31.87 | 31.23
2019-11-11 05:00 | 33.53 | 32.92
2019-11-11 05:30 | 34.68 | 34.1
2019-11-11 06:00 | 36.86 | 36.3
2019-11-11 06:30 | 40.4 | 39.89
2019-11-11 07:00 | 43.12 | 42.51
2019-11-11 07:30 | 47.15 | 45.91
2019-11-11 08:00 | 49.27 | 47.4
2019-11-11 08:30 | 50.7 | 48.69
2019-11-11 09:00 | 50.49 | 49.58
2019-11-11 09:30 | 51.36 | 50.26
2019-11-11 10:00 | 51.96 | 50.7
2019-11-11 10:30 | 54.25 | 52.77
2019-11-11 11:00 | 55.2 | 53.43
2019-11-11 11:30 | 55.3 | 53.52
2019-11-11 12:00 | 54.48 | 52.56
2019-11-11 12:30 | 54.81 | 52.93
2019-11-11 13:00 | 55.34 | 53.52
2019-11-11 13:30 | 54.96 | 53.17
2019-11-11 14:00 | 56.11 | 54.22
2019-11-11 14:30 | 56.81 | 55.01
2019-11-11 15:00 | 57.55 | 55.9
2019-11-11 15:30 | 59.43 | 57.99
2019-11-11 16:00 | 60.94 | 59.7
2019-11-11 16:30 | 60.39 | 59.54
2019-11-11 17:00 | 60.78 | 60.22
2019-11-11 17:30 | 59.62 | 59.34
2019-11-11 18:00 | 58.67 | 58.53
2019-11-11 18:30 | 58.51 | 58.19
2019-11-11 19:00 | 60.89 | 60.02
2019-11-11 19:30 | 59.73 | 58.7
2019-11-11 20:00 | 57.8 | 56.72
2019-11-11 20:30 | 55.1 | 53.96
2019-11-11 21:00 | 52.29 | 51.07
2019-11-11 21:30 | 49.6 | 48.3
2019-11-11 22:00 | 47.45 | 46.07
2019-11-11 22:30 | 44.23 | 42.76
2019-11-11 23:00 | 41.95 | 40.4
2019-11-11 23:30 | 40.09 | 38.45
2019-11-12 | 38.6 | 36.9
2019-11-12 00:30 | 37.93 | 36.19
2019-11-12 01:00 | 37.82 | 36.07
2019-11-12 01:30 | 36.82 | 35.01
2019-11-12 02:00 | 35.88 | 34.02
2019-11-12 02:30 | 36.15 | 34.3
2019-11-12 03:00 | 35.51 | 33.62
2019-11-12 03:30 | 34.17 | 32.77
2019-11-12 04:00 | 33.56 | 33.14
2019-11-12 04:30 | 33.84 | 33.43
2019-11-12 05:00 | 35.61 | 35.22
2019-11-12 05:30 | 35.98 | 35.6
2019-11-12 06:00 | 37.77 | 37.41
2019-11-12 06:30 | 42.45 | 41.96
2019-11-12 07:00 | 46.93 | 45.93
2019-11-12 07:30 | 51.22 | 50.34
2019-11-12 08:00 | 53.26 | 51.98
2019-11-12 08:30 | 53.92 | 52.95
2019-11-12 09:00 | 53.85 | 52.66
2019-11-12 09:30 | 54.23 | 52.92
2019-11-12 10:00 | 53.34 | 51.84
2019-11-12 10:30 | 53.98 | 52.28
2019-11-12 11:00 | 55.23 | 53.32
2019-11-12 11:30 | 56.36 | 54.34
2019-11-12 12:00 | 56.62 | 54.56
2019-11-12 12:30 | 56.14 | 54.17
2019-11-12 13:00 | 56.83 | 54.95
2019-11-12 13:30 | 57.1 | 55.15
2019-11-12 14:00 | 58.78 | 56.8
2019-11-12 14:30 | 59.48 | 57.51
2019-11-12 15:00 | 60.09 | 58.29
2019-11-12 15:30 | 61.06 | 59.57
2019-11-12 16:00 | 62.15 | 60.91
2019-11-12 16:30 | 62.51 | 61.61
2019-11-12 17:00 | 61.6 | 60.99
2019-11-12 17:30 | 60.19 | 59.37
2019-11-12 18:00 | 59.36 | 58.81
2019-11-12 18:30 | 58.7 | 58.33
2019-11-12 19:00 | 60.91 | 60.48
2019-11-12 19:30 | 58.31 | 57.96
2019-11-12 20:00 | 56.27 | 55.96
2019-11-12 20:30 | 53.75 | 53.51
2019-11-12 21:00 | 51.59 | 51.33
2019-11-12 21:30 | 49.66 | 49.39
2019-11-12 22:00 | 46.57 | 46.28
2019-11-12 22:30 | 44.13 | 43.79
2019-11-12 23:00 | 42.13 | 41.69
2019-11-12 23:30 | 40.3 | 39.93
2019-11-13 | 38.63 | 38.28
2019-11-13 00:30 | 37.92 | 37.57
2019-11-13 01:00 | 35.76 | 35.38
2019-11-13 01:30 | 35.87 | 35.49
2019-11-13 02:00 | 34.67 | 34.28
2019-11-13 02:30 | 34.2 | 33.8
2019-11-13 03:00 | 35.41 | 35.02
2019-11-13 03:30 | 34.76 | 34.36
2019-11-13 04:00 | 33.59 | 33.17
2019-11-13 04:30 | 34.08 | 33.67
2019-11-13 05:00 | 35.29 | 34.9
2019-11-13 05:30 | 36.2 | 35.82
2019-11-13 06:00 | 38.51 | 38.15
2019-11-13 06:30 | 42.28 | 41.78
2019-11-13 07:00 | 46.33 | 45.32
2019-11-13 07:30 | 53.32 | 51.45
2019-11-13 08:00 | 55.11 | 53.18
2019-11-13 08:30 | 56.34 | 54.44
2019-11-13 09:00 | 57.16 | 54.84
2019-11-13 09:30 | 56.95 | 54.37
2019-11-13 10:00 | 56.36 | 53.71
2019-11-13 10:30 | 56.91 | 53.98
2019-11-13 11:00 | 58.03 | 54.84
2019-11-13 11:30 | 59.14 | 55.94
2019-11-13 12:00 | 59.58 | 56.19
2019-11-13 12:30 | 60.16 | 56.79
2019-11-13 13:00 | 60.52 | 57.18
2019-11-13 13:30 | 62.75 | 59.41
2019-11-13 14:00 | 63.18 | 59.86
2019-11-13 14:30 | 64.5 | 61.17
2019-11-13 15:00 | 65.12 | 61.92
2019-11-13 15:30 | 65.98 | 63.15
2019-11-13 16:00 | 66.82 | 64.44
2019-11-13 16:30 | 66.02 | 64.12
2019-11-13 17:00 | 65.02 | 63.59
2019-11-13 17:30 | 62.59 | 61.6
2019-11-13 18:00 | 61.26 | 60.26
2019-11-13 18:30 | 62 | 61.01
2019-11-13 19:00 | 62.81 | 61.84
2019-11-13 19:30 | 61.64 | 60.65
2019-11-13 20:00 | 60.55 | 59.53
2019-11-13 20:30 | 57.22 | 56.13
2019-11-13 21:00 | 55.12 | 53.98
2019-11-13 21:30 | 52.44 | 51.22
2019-11-13 22:00 | 49.98 | 48.69
2019-11-13 22:30 | 47.58 | 46.2
2019-11-13 23:00 | 45.49 | 44.04
2019-11-13 23:30 | 43.18 | 41.64
2019-11-14 | 41.56 | 40
2019-11-14 00:30 | 40.09 | 38.46
2019-11-14 01:00 | 38.6 | 36.89
2019-11-14 01:30 | 37.72 | 35.97
2019-11-14 02:00 | 37.15 | 35.36
2019-11-14 02:30 | 35.46 | 34.78
2019-11-14 03:00 | 34.79 | 34.39
2019-11-14 03:30 | 34.41 | 34
2019-11-14 04:00 | 34.89 | 34.49
2019-11-14 04:30 | 35.65 | 35.26
2019-11-14 05:00 | 36.72 | 36.35
2019-11-14 05:30 | 38.01 | 37.66
2019-11-14 06:00 | 40.15 | 39.81
2019-11-14 06:30 | 45.53 | 44.83
2019-11-14 07:00 | 49.32 | 48.04
2019-11-14 07:30 | 56.13 | 53.86
2019-11-14 08:00 | 58.44 | 56.32
2019-11-14 08:30 | 60.72 | 58.44
2019-11-14 09:00 | 62.04 | 59.29
2019-11-14 09:30 | 62.77 | 59.71
2019-11-14 10:00 | 63.13 | 59.86
2019-11-14 10:30 | 63.7 | 60.28
2019-11-14 11:00 | 64.68 | 61.06
2019-11-14 11:30 | 65.21 | 61.45
2019-11-14 12:00 | 65.4 | 61.35
2019-11-14 12:30 | 64.91 | 61.07
2019-11-14 13:00 | 66.19 | 62.43
2019-11-14 13:30 | 67.56 | 63.74
2019-11-14 14:00 | 68.96 | 65.11
2019-11-14 14:30 | 69.57 | 65.86
2019-11-14 15:00 | 70.04 | 66.51
2019-11-14 15:30 | 69.51 | 66.29
2019-11-14 16:00 | 69.03 | 66.52
2019-11-14 16:30 | 70.06 | 67.99
2019-11-14 17:00 | 70.02 | 67.95
2019-11-14 17:30 | 66.95 | 64.75
2019-11-14 18:00 | 66.26 | 64.01
2019-11-14 18:30 | 65.63 | 63.36
2019-11-14 19:00 | 67.12 | 64.91
2019-11-14 19:30 | 65.63 | 63.33
2019-11-14 20:00 | 64.54 | 62.2
2019-11-14 20:30 | 61.55 | 59.06
2019-11-14 21:00 | 60.03 | 57.46
2019-11-14 21:30 | 57.15 | 54.43
2019-11-14 22:00 | 54.41 | 51.5
2019-11-14 22:30 | 51.09 | 48.5
2019-11-14 23:00 | 47.18 | 45.8
2019-11-14 23:30 | 44.37 | 42.9
2019-11-15 | 42.77 | 41.28
2019-11-15 00:30 | 42.04 | 40.5
2019-11-15 01:00 | 40.28 | 38.67
2019-11-15 01:30 | 40.44 | 38.83
2019-11-15 02:00 | 39.11 | 37.44
2019-11-15 02:30 | 39.04 | 37.36
2019-11-15 03:00 | 38.19 | 36.46
2019-11-15 03:30 | 37.68 | 35.92
2019-11-15 04:00 | 37.04 | 35.24
2019-11-15 04:30 | 37.92 | 36.17
2019-11-15 05:00 | 39.84 | 38.19
2019-11-15 05:30 | 40.09 | 38.45
2019-11-15 06:00 | 42.1 | 40.57
2019-11-15 06:30 | 47.07 | 45.74
2019-11-15 07:00 | 51.03 | 49.48
2019-11-15 07:30 | 57.41 | 55
2019-11-15 08:00 | 61 | 58.97
2019-11-15 08:30 | 64.47 | 62.26
2019-11-15 09:00 | 64.78 | 62.32
2019-11-15 09:30 | 64.91 | 62.41
2019-11-15 10:00 | 62.13 | 59.42
2019-11-15 10:30 | 61.58 | 58.51
2019-11-15 11:00 | 61.22 | 57.93
2019-11-15 11:30 | 64.39 | 61.17
2019-11-15 12:00 | 61.12 | 57.73
2019-11-15 12:30 | 64.06 | 60.91
2019-11-15 13:00 | 62.63 | 59.47
2019-11-15 13:30 | 61.68 | 58.44
2019-11-15 14:00 | 62.14 | 59.05
2019-11-15 14:30 | 62.2 | 59.37
2019-11-15 15:00 | 61.56 | 59.36
2019-11-15 15:30 | 60.69 | 59.53
2019-11-15 16:00 | 62.22 | 61.24
2019-11-15 16:30 | 62.48 | 61.5
2019-11-15 17:00 | 62.78 | 61.8
2019-11-15 17:30 | 61.84 | 60.83
2019-11-15 18:00 | 60.93 | 59.89
2019-11-15 18:30 | 59.94 | 58.87
2019-11-15 19:00 | 61.11 | 60.09
2019-11-15 19:30 | 60.57 | 59.54
2019-11-15 20:00 | 57.77 | 56.69
2019-11-15 20:30 | 55.79 | 54.66
2019-11-15 21:00 | 53.91 | 52.73
2019-11-15 21:30 | 52.13 | 50.91
2019-11-15 22:00 | 50.35 | 49.07
2019-11-15 22:30 | 47.67 | 46.29
2019-11-15 23:00 | 45.82 | 44.37
2019-11-15 23:30 | 43.28 | 42.51
2019-11-16 | 40.87 | 40.52
2019-11-16 00:30 | 39.4 | 39.06
2019-11-16 01:00 | 38.53 | 38.18
2019-11-16 01:30 | 37.99 | 37.63
2019-11-16 02:00 | 37.05 | 36.68
2019-11-16 02:30 | 36.69 | 36.32
2019-11-16 03:00 | 35.78 | 35.4
2019-11-16 03:30 | 35.5 | 35.11
2019-11-16 04:00 | 35.57 | 35.18
2019-11-16 04:30 | 35.55 | 35.17
2019-11-16 05:00 | 36.93 | 36.56
2019-11-16 05:30 | 37.19 | 36.82
2019-11-16 06:00 | 37.16 | 36.79
2019-11-16 06:30 | 37.01 | 36.65
2019-11-16 07:00 | 38.03 | 37.67
2019-11-16 07:30 | 39.53 | 39.04
2019-11-16 08:00 | 42.69 | 41.92
2019-11-16 08:30 | 45.06 | 44.05
2019-11-16 09:00 | 47.33 | 46.23
2019-11-16 09:30 | 47.34 | 46.85
2019-11-16 10:00 | 45.53 | 44.93
2019-11-16 10:30 | 44.61 | 43.9
2019-11-16 11:00 | 44.68 | 43.94
2019-11-16 11:30 | 44.35 | 43.62
2019-11-16 12:00 | 44.21 | 43.51
2019-11-16 12:30 | 43.67 | 43.09
2019-11-16 13:00 | 43.31 | 42.76
2019-11-16 13:30 | 43.61 | 43.07
2019-11-16 14:00 | 43.87 | 43.37
2019-11-16 14:30 | 44.19 | 43.79
2019-11-16 15:00 | 45.39 | 45.04
2019-11-16 15:30 | 46.89 | 46.57
2019-11-16 16:00 | 48.99 | 48.71
2019-11-16 16:30 | 50.18 | 49.92
2019-11-16 17:00 | 50.75 | 50.49
2019-11-16 17:30 | 52.33 | 52.07
2019-11-16 18:00 | 54.09 | 53.85
2019-11-16 18:30 | 54.19 | 53.94
2019-11-16 19:00 | 56.03 | 55.8
2019-11-16 19:30 | 55.24 | 55
2019-11-16 20:00 | 53.38 | 53.13
2019-11-16 20:30 | 53.22 | 52.97
2019-11-16 21:00 | 52.34 | 52.08
2019-11-16 21:30 | 49.37 | 49.09
2019-11-16 22:00 | 47.28 | 46.99
2019-11-16 22:30 | 45.52 | 45.22
2019-11-16 23:00 | 43.79 | 43.47
2019-11-16 23:30 | 41.93 | 41.59
2019-11-17 | 40.51 | 40.16
2019-11-17 00:30 | 39.78 | 39.44
2019-11-17 01:00 | 38.93 | 38.58
2019-11-17 01:30 | 38.76 | 38.4
2019-11-17 02:00 | 37.49 | 37.12
2019-11-17 02:30 | 37.21 | 36.84
2019-11-17 03:00 | 36.33 | 35.95
2019-11-17 03:30 | 36.07 | 35.69
2019-11-17 04:00 | 35.87 | 35.48
2019-11-17 04:30 | 35.49 | 35.1
2019-11-17 05:00 | 36.31 | 35.93
2019-11-17 05:30 | 35.07 | 34.67
2019-11-17 06:00 | 35.29 | 34.89
2019-11-17 06:30 | 35.32 | 34.92
2019-11-17 07:00 | 35.71 | 35.32
2019-11-17 07:30 | 36.5 | 36.12
2019-11-17 08:00 | 38.29 | 37.93
2019-11-17 08:30 | 40.94 | 40.51
2019-11-17 09:00 | 41.35 | 40.82
2019-11-17 09:30 | 40.89 | 40.35
2019-11-17 10:00 | 39.62 | 39.27
2019-11-17 10:30 | 40.59 | 40.26
2019-11-17 11:00 | 40.64 | 40.29
2019-11-17 11:30 | 40.24 | 39.89
2019-11-17 12:00 | 40.65 | 40.31
2019-11-17 12:30 | 41.62 | 41.27
2019-11-17 13:00 | 42.53 | 42.16
2019-11-17 13:30 | 43.86 | 43.54
2019-11-17 14:00 | 44.36 | 44.06
2019-11-17 14:30 | 45.9 | 45.6
2019-11-17 15:00 | 47.33 | 47.05
2019-11-17 15:30 | 49.59 | 49.32
2019-11-17 16:00 | 51.06 | 50.8
2019-11-17 16:30 | 52.82 | 52.57
2019-11-17 17:00 | 53.87 | 53.63
2019-11-17 17:30 | 54.06 | 53.81
2019-11-17 18:00 | 55.95 | 55.72
2019-11-17 18:30 | 58.11 | 57.89
2019-11-17 19:00 | 59.08 | 58.86
2019-11-17 19:30 | 58.65 | 58.43
2019-11-17 20:00 | 57.19 | 56.96
2019-11-17 20:30 | 55.53 | 55.29
2019-11-17 21:00 | 52.89 | 52.64
2019-11-17 21:30 | 51.39 | 51.13
2019-11-17 22:00 | 48.76 | 48.48
2019-11-17 22:30 | 45.86 | 45.56
2019-11-17 23:00 | 43.67 | 43.35
2019-11-17 23:30 | 41.7 | 41.37
2019-11-18 | 40.01 | 39.68
2019-11-18 00:30 | 39.19 | 38.85
2019-11-18 01:00 | 38.56 | 38.21
2019-11-18 01:30 | 38.33 | 37.97
2019-11-18 02:00 | 37.34 | 36.98
2019-11-18 02:30 | 36.85 | 36.48
2019-11-18 03:00 | 36.41 | 36.03
2019-11-18 03:30 | 36.15 | 35.77
2019-11-18 04:00 | 36.25 | 35.87
2019-11-18 04:30 | 36.67 | 36.29
2019-11-18 05:00 | 38.15 | 37.79
2019-11-18 05:30 | 39.52 | 39.17
2019-11-18 06:00 | 41.11 | 40.78
2019-11-18 06:30 | 46.11 | 45.38
2019-11-18 07:00 | 51.57 | 50.23
2019-11-18 07:30 | 57.13 | 55.09
2019-11-18 08:00 | 60.02 | 58.18
2019-11-18 08:30 | 63.1 | 60.57
2019-11-18 09:00 | 63.94 | 60.97
2019-11-18 09:30 | 63.78 | 60.68
2019-11-18 10:00 | 64 | 60.82
2019-11-18 10:30 | 64.63 | 61.22
2019-11-18 11:00 | 65.37 | 61.67
2019-11-18 11:30 | 66.7 | 62.86
2019-11-18 12:00 | 68.19 | 64.22
2019-11-18 12:30 | 68.37 | 64.46
2019-11-18 13:00 | 68.5 | 64.81
2019-11-18 13:30 | 69.25 | 65.54
2019-11-18 14:00 | 70.21 | 66.52
2019-11-18 14:30 | 71.41 | 67.74
2019-11-18 15:00 | 72.1 | 68.57
2019-11-18 15:30 | 72.77 | 69.48
2019-11-18 16:00 | 73.82 | 70.9
2019-11-18 16:30 | 73.84 | 71.44
2019-11-18 17:00 | 72.98 | 70.94
2019-11-18 17:30 | 70.37 | 68.32
2019-11-18 18:00 | 69.92 | 67.84
2019-11-18 18:30 | 69.52 | 67.42
2019-11-18 19:00 | 71.02 | 68.98
2019-11-18 19:30 | 68.23 | 66.07
2019-11-18 20:00 | 65.59 | 63.33
2019-11-18 20:30 | 64.21 | 61.86
2019-11-18 21:00 | 61.81 | 59.35
2019-11-18 21:30 | 58.49 | 55.85
2019-11-18 22:00 | 56.08 | 53.3
2019-11-18 22:30 | 52.86 | 49.85
2019-11-18 23:00 | 49.72 | 46.74
2019-11-18 23:30 | 45.3 | 43.84
2019-11-19 | 44.03 | 42.55
2019-11-19 00:30 | 42.2 | 40.66
2019-11-19 01:00 | 42.49 | 40.96
2019-11-19 01:30 | 41.36 | 39.79
2019-11-19 02:00 | 41.36 | 39.78
2019-11-19 02:30 | 40.69 | 39.07
2019-11-19 03:00 | 39.38 | 37.71
2019-11-19 03:30 | 39.21 | 37.52
2019-11-19 04:00 | 38.77 | 37.06
2019-11-19 04:30 | 40.02 | 38.38
2019-11-19 05:00 | 41.36 | 39.79
2019-11-19 05:30 | 42.65 | 41.13
2019-11-19 06:00 | 44.7 | 43.26
2019-11-19 06:30 | 48.93 | 47.66
2019-11-19 07:00 | 53.09 | 51.58
2019-11-19 07:30 | 59.63 | 57.69
2019-11-19 08:00 | 61.9 | 59.87
2019-11-19 08:30 | 63.38 | 60.8
2019-11-19 09:00 | 64.43 | 61.38
2019-11-19 09:30 | 64.38 | 61.14
2019-11-19 10:00 | 64.59 | 61.28
2019-11-19 10:30 | 64.96 | 61.37
2019-11-19 11:00 | 65.57 | 61.62
2019-11-19 11:30 | 65.13 | 61.16
2019-11-19 12:00 | 66.71 | 62.75
2019-11-19 12:30 | 66.31 | 62.32
2019-11-19 13:00 | 66 | 62.24
2019-11-19 13:30 | 66.99 | 63.2
2019-11-19 14:00 | 68.75 | 65
2019-11-19 14:30 | 69.08 | 65.51
2019-11-19 15:00 | 69.53 | 65.95
2019-11-19 15:30 | 69.76 | 66.5
2019-11-19 16:00 | 69.94 | 67.17
2019-11-19 16:30 | 69.29 | 67.08
2019-11-19 17:00 | 68.66 | 66.57
2019-11-19 17:30 | 67.03 | 64.84
2019-11-19 18:00 | 66.23 | 64
2019-11-19 18:30 | 66.58 | 64.35
2019-11-19 19:00 | 66.96 | 64.75
2019-11-19 19:30 | 66.6 | 64.38
2019-11-19 20:00 | 64.04 | 61.68
2019-11-19 20:30 | 61.3 | 58.82
2019-11-19 21:00 | 59.18 | 56.59
2019-11-19 21:30 | 56.85 | 54.11
2019-11-19 22:00 | 54.21 | 51.29
2019-11-19 22:30 | 50.29 | 48.26
2019-11-19 23:00 | 46.51 | 45.1
2019-11-19 23:30 | 45.41 | 43.95
2019-11-20 | 42.86 | 41.35
2019-11-20 00:30 | 41.82 | 40.27
2019-11-20 01:00 | 40.73 | 39.13
2019-11-20 01:30 | 39.83 | 38.18
2019-11-20 02:00 | 39.8 | 38.16
2019-11-20 02:30 | 38.85 | 37.15
2019-11-20 03:00 | 38.3 | 36.57
2019-11-20 03:30 | 37.86 | 36.1
2019-11-20 04:00 | 37.58 | 35.81
2019-11-20 04:30 | 38.13 | 36.38
2019-11-20 05:00 | 38.63 | 36.91
2019-11-20 05:30 | 40.29 | 38.65
2019-11-20 06:00 | 42.68 | 41.16
2019-11-20 06:30 | 46.69 | 45.34
2019-11-20 07:00 | 49.66 | 48.28
2019-11-20 07:30 | 55.66 | 53.54
2019-11-20 08:00 | 59.46 | 57.45
2019-11-20 08:30 | 61.34 | 60.26
2019-11-20 09:00 | 61.02 | 59.94
2019-11-20 09:30 | 61.1 | 60.04
2019-11-20 10:00 | 60.27 | 59.19
2019-11-20 10:30 | 61.18 | 60.12
2019-11-20 11:00 | 61.35 | 60.31
2019-11-20 11:30 | 63.07 | 62.06
2019-11-20 12:00 | 63.23 | 62.22
2019-11-20 12:30 | 64.31 | 63.32
2019-11-20 13:00 | 64.3 | 63.32
2019-11-20 13:30 | 65.3 | 64.34
2019-11-20 14:00 | 66.91 | 65.97
2019-11-20 14:30 | 67.15 | 66.22
2019-11-20 15:00 | 68.01 | 67.08
2019-11-20 15:30 | 68.02 | 67.09
2019-11-20 16:00 | 70.02 | 69.11
2019-11-20 16:30 | 70.25 | 69.33
2019-11-20 17:00 | 70.12 | 69.19
2019-11-20 17:30 | 67.72 | 66.73
2019-11-20 18:00 | 65.81 | 65.22
2019-11-20 18:30 | 65.96 | 65.47
2019-11-20 19:00 | 67.01 | 66.63
2019-11-20 19:30 | 65.63 | 65.13
2019-11-20 20:00 | 63.06 | 62.43
2019-11-20 20:30 | 60.61 | 59.81
2019-11-20 21:00 | 58.94 | 57.95
2019-11-20 21:30 | 55.76 | 54.53
2019-11-20 22:00 | 52.99 | 51.56
2019-11-20 22:30 | 50.39 | 48.6
2019-11-20 23:00 | 48.5 | 46.43
2019-11-20 23:30 | 46.16 | 43.67
2019-11-21 | 44.57 | 41.83
2019-11-21 00:30 | 42.71 | 41.08
2019-11-21 01:00 | 41.96 | 40.31
2019-11-21 01:30 | 41.12 | 39.38
2019-11-21 02:00 | 40.49 | 38.62
2019-11-21 02:30 | 39.94 | 37.95
2019-11-21 03:00 | 39.4 | 37.24
2019-11-21 03:30 | 39.98 | 37.73
2019-11-21 04:00 | 40.19 | 37.98
2019-11-21 04:30 | 40.76 | 38.63
2019-11-21 05:00 | 41.26 | 39.29
2019-11-21 05:30 | 41.64 | 39.82
2019-11-21 06:00 | 43.37 | 41.75
2019-11-21 06:30 | 47.46 | 46.03
2019-11-21 07:00 | 50.9 | 49.57
2019-11-21 07:30 | 55.55 | 54.35
2019-11-21 08:00 | 58.39 | 57.25
2019-11-21 08:30 | 60.62 | 59.54
2019-11-21 09:00 | 61.07 | 59.99
2019-11-21 09:30 | 60.63 | 59.54
2019-11-21 10:00 | 59.83 | 58.73
2019-11-21 10:30 | 60.09 | 58.99
2019-11-21 11:00 | 61.05 | 59.97
2019-11-21 11:30 | 60.8 | 59.71
2019-11-21 12:00 | 64.36 | 63.34
2019-11-21 12:30 | 63.51 | 62.47
2019-11-21 13:00 | 63.39 | 62.35
2019-11-21 13:30 | 64.44 | 63.42
2019-11-21 14:00 | 64.21 | 63.2
2019-11-21 14:30 | 63.84 | 62.82
2019-11-21 15:00 | 62.77 | 61.73
2019-11-21 15:30 | 62.97 | 61.93
2019-11-21 16:00 | 63.44 | 62.42
2019-11-21 16:30 | 63.75 | 62.73
2019-11-21 17:00 | 64.83 | 63.58
2019-11-21 17:30 | 63.33 | 61.42
2019-11-21 18:00 | 62.98 | 61.66
2019-11-21 18:30 | 61.6 | 60.55
2019-11-21 19:00 | 62.91 | 61.89
2019-11-21 19:30 | 62.46 | 61.44
2019-11-21 20:00 | 59.88 | 58.81
2019-11-21 20:30 | 58.98 | 57.88
2019-11-21 21:00 | 56.43 | 55.21
2019-11-21 21:30 | 54.26 | 52.81
2019-11-21 22:00 | 51.35 | 49.47
2019-11-21 22:30 | 48.49 | 46.11
2019-11-21 23:00 | 43.95 | 42.18
2019-11-21 23:30 | 43.92 | 42.33
2019-11-22 | 42.36 | 40.69
2019-11-22 00:30 | 40.9 | 39.16
2019-11-22 01:00 | 40.7 | 38.95
2019-11-22 01:30 | 40.85 | 39.1
2019-11-22 02:00 | 38.99 | 37.15
2019-11-22 02:30 | 38.12 | 36.23
2019-11-22 03:00 | 36.71 | 34.75
2019-11-22 03:30 | 36.21 | 34.22
2019-11-22 04:00 | 37.07 | 35.13
2019-11-22 04:30 | 37.73 | 35.82
2019-11-22 05:00 | 38.96 | 37.12
2019-11-22 05:30 | 39.88 | 38.09
2019-11-22 06:00 | 41.89 | 40.19
2019-11-22 06:30 | 46.16 | 44.9
2019-11-22 07:00 | 49.54 | 48.25
2019-11-22 07:30 | 54.81 | 52.75
2019-11-22 08:00 | 56.59 | 55.33
2019-11-22 08:30 | 55.69 | 54.56
2019-11-22 09:00 | 55.63 | 54.74
2019-11-22 09:30 | 56.55 | 55.81
2019-11-22 10:00 | 56.75 | 56.08
2019-11-22 10:30 | 57.06 | 56.47
2019-11-22 11:00 | 57.49 | 56.98
2019-11-22 11:30 | 58.65 | 58.22
2019-11-22 12:00 | 56.3 | 55.89
2019-11-22 12:30 | 55.87 | 55.45
2019-11-22 13:00 | 55.87 | 55.38
2019-11-22 13:30 | 56.21 | 55.73
2019-11-22 14:00 | 56.53 | 55.96
2019-11-22 14:30 | 56.85 | 56.22
2019-11-22 15:00 | 57.23 | 56.4
2019-11-22 15:30 | 56.61 | 55.45
2019-11-22 16:00 | 57.83 | 56.43
2019-11-22 16:30 | 59.01 | 57.34
2019-11-22 17:00 | 59.95 | 57.97
2019-11-22 17:30 | 60.2 | 57.72
2019-11-22 18:00 | 59.82 | 56.79
2019-11-22 18:30 | 59.05 | 55.91
2019-11-22 19:00 | 58.15 | 57.02
2019-11-22 19:30 | 58.16 | 57.01
2019-11-22 20:00 | 55.94 | 54.59
2019-11-22 20:30 | 53.86 | 52.33
2019-11-22 21:00 | 53.7 | 52.03
2019-11-22 21:30 | 52.07 | 50.2
2019-11-22 22:00 | 49.93 | 47.8
2019-11-22 22:30 | 48.44 | 46.4
2019-11-22 23:00 | 40.03 | 38.88
2019-11-22 23:30 | 37.63 | 37.18
2019-11-23 | 36.41 | 36.01
2019-11-23 00:30 | 35.39 | 35.02
2019-11-23 01:00 | 34.49 | 34.16
2019-11-23 01:30 | 33.17 | 32.77
2019-11-23 02:00 | 33.03 | 32.41
2019-11-23 02:30 | 32.79 | 32.15
2019-11-23 03:00 | 33.11 | 32.48
2019-11-23 03:30 | 32.4 | 31.76
2019-11-23 04:00 | 31.32 | 30.65
2019-11-23 04:30 | 32.29 | 31.65
2019-11-23 05:00 | 32.51 | 31.87
2019-11-23 05:30 | 32.21 | 31.56
2019-11-23 06:00 | 33.92 | 33.31
2019-11-23 06:30 | 35.12 | 34.53
2019-11-23 07:00 | 35.66 | 35.07
2019-11-23 07:30 | 37.7 | 37.16
2019-11-23 08:00 | 38.16 | 37.55
2019-11-23 08:30 | 40.88 | 39.87
2019-11-23 09:00 | 41.87 | 40.68
2019-11-23 09:30 | 41.64 | 41.05
2019-11-23 10:00 | 41.26 | 40.62
2019-11-23 10:30 | 41.72 | 40.98
2019-11-23 11:00 | 41.98 | 41.23
2019-11-23 11:30 | 41.49 | 40.76
2019-11-23 12:00 | 40.76 | 40.04
2019-11-23 12:30 | 39.89 | 39.29
2019-11-23 13:00 | 41.88 | 41.32
2019-11-23 13:30 | 41.11 | 40.58
2019-11-23 14:00 | 41.08 | 40.56
2019-11-23 14:30 | 41.22 | 40.74
2019-11-23 15:00 | 42.12 | 41.65
2019-11-23 15:30 | 43.76 | 43.3
2019-11-23 16:00 | 45.57 | 45.12
2019-11-23 16:30 | 46.08 | 45.63
2019-11-23 17:00 | 48.82 | 48.41
2019-11-23 17:30 | 51.03 | 50.64
2019-11-23 18:00 | 53.34 | 52.97
2019-11-23 18:30 | 52.57 | 52.19
2019-11-23 19:00 | 53.54 | 53.17
2019-11-23 19:30 | 52.98 | 52.6
2019-11-23 20:00 | 51.36 | 50.97
2019-11-23 20:30 | 49.84 | 49.45
2019-11-23 21:00 | 48.35 | 47.94
2019-11-23 21:30 | 47.1 | 46.67
2019-11-23 22:00 | 45.43 | 44.99
2019-11-23 22:30 | 43.93 | 43.48
2019-11-23 23:00 | 41.71 | 41.22
2019-11-23 23:30 | 39.69 | 39.17
2019-11-24 | 38.23 | 37.69
2019-11-24 00:30 | 36.9 | 36.34
2019-11-24 01:00 | 35.52 | 34.94
2019-11-24 01:30 | 34.9 | 34.3
2019-11-24 02:00 | 34.4 | 33.8
2019-11-24 02:30 | 34.09 | 33.48
2019-11-24 03:00 | 32.99 | 32.36
2019-11-24 03:30 | 32.89 | 32.26
2019-11-24 04:00 | 32.68 | 32.04
2019-11-24 04:30 | 32.66 | 32.02
2019-11-24 05:00 | 32.18 | 31.54
2019-11-24 05:30 | 31.96 | 31.31
2019-11-24 06:00 | 32.19 | 31.55
2019-11-24 06:30 | 32.33 | 31.69
2019-11-24 07:00 | 32.21 | 31.56
2019-11-24 07:30 | 33.61 | 32.98
2019-11-24 08:00 | 33.4 | 32.77
2019-11-24 08:30 | 35.11 | 34.51
2019-11-24 09:00 | 35.7 | 35.13
2019-11-24 09:30 | 36.17 | 35.53
2019-11-24 10:00 | 36.5 | 35.77
2019-11-24 10:30 | 37.09 | 36.53
2019-11-24 11:00 | 37.03 | 36.47
2019-11-24 11:30 | 37.39 | 36.83
2019-11-24 12:00 | 38.14 | 37.6
2019-11-24 12:30 | 38.4 | 37.86
2019-11-24 13:00 | 38.87 | 38.33
2019-11-24 13:30 | 39.64 | 39.11
2019-11-24 14:00 | 40.3 | 39.79
2019-11-24 14:30 | 41.34 | 40.85
2019-11-24 15:00 | 44.34 | 43.89
2019-11-24 15:30 | 45.36 | 44.92
2019-11-24 16:00 | 45.83 | 45.39
2019-11-24 16:30 | 46.74 | 46.31
2019-11-24 17:00 | 48.38 | 47.97
2019-11-24 17:30 | 50.33 | 49.93
2019-11-24 18:00 | 52.42 | 52.05
2019-11-24 18:30 | 53.3 | 52.93
2019-11-24 19:00 | 54.92 | 54.57
2019-11-24 19:30 | 55.51 | 55.16
2019-11-24 20:00 | 53.25 | 52.89
2019-11-24 20:30 | 51.01 | 50.63
2019-11-24 21:00 | 49.89 | 49.49
2019-11-24 21:30 | 47.7 | 47.29
2019-11-24 22:00 | 45.17 | 44.73
2019-11-24 22:30 | 42.58 | 42.1
2019-11-24 23:00 | 41.73 | 41.23
2019-11-24 23:30 | 39.3 | 38.78
2019-11-25 | 37.18 | 36.62
2019-11-25 00:30 | 36.53 | 35.97
2019-11-25 01:00 | 35.75 | 35.17
2019-11-25 01:30 | 35.2 | 34.62
2019-11-25 02:00 | 35.51 | 34.93
2019-11-25 02:30 | 34.61 | 34.01
2019-11-25 03:00 | 34.17 | 33.56
2019-11-25 03:30 | 34.26 | 33.65
2019-11-25 04:00 | 34.47 | 33.87
2019-11-25 04:30 | 35.18 | 34.59
2019-11-25 05:00 | 35.31 | 34.72
2019-11-25 05:30 | 36.73 | 36.17
2019-11-25 06:00 | 39.61 | 39.09
2019-11-25 06:30 | 43.54 | 42.97
2019-11-25 07:00 | 48.3 | 47.18
2019-11-25 07:30 | 57.04 | 55
2019-11-25 08:00 | 58.01 | 56
2019-11-25 08:30 | 61.75 | 59.73
2019-11-25 09:00 | 61.37 | 58.86
2019-11-25 09:30 | 60.99 | 58.26
2019-11-25 10:00 | 60.92 | 58.04
2019-11-25 10:30 | 59.61 | 56.57
2019-11-25 11:00 | 59.8 | 56.58
2019-11-25 11:30 | 60.56 | 57.23
2019-11-25 12:00 | 62.11 | 58.57
2019-11-25 12:30 | 62.94 | 59.55
2019-11-25 13:00 | 61.9 | 58.63
2019-11-25 13:30 | 62.85 | 59.58
2019-11-25 14:00 | 63.3 | 61.31
2019-11-25 14:30 | 62.04 | 60.99
2019-11-25 15:00 | 62.67 | 61.62
2019-11-25 15:30 | 64.03 | 63
2019-11-25 16:00 | 64.77 | 63.74
2019-11-25 16:30 | 64.37 | 63.34
2019-11-25 17:00 | 62.59 | 62.34
2019-11-25 17:30 | 61.53 | 61.15
2019-11-25 18:00 | 61.41 | 60.71
2019-11-25 18:30 | 61.19 | 60.25
2019-11-25 19:00 | 62.92 | 62.12
2019-11-25 19:30 | 61.68 | 60.8
2019-11-25 20:00 | 59.58 | 58.5
2019-11-25 20:30 | 58.06 | 56.85
2019-11-25 21:00 | 55.68 | 54.29
2019-11-25 21:30 | 53.1 | 51.37
2019-11-25 22:00 | 50.62 | 48.62
2019-11-25 22:30 | 48.1 | 45.61
2019-11-25 23:00 | 45.18 | 43.44
2019-11-25 23:30 | 43.51 | 41.86
2019-11-26 | 41.95 | 40.23
2019-11-26 00:30 | 40.02 | 38.22
2019-11-26 01:00 | 39.4 | 37.56
2019-11-26 01:30 | 38.7 | 36.81
2019-11-26 02:00 | 37.84 | 35.91
2019-11-26 02:30 | 37.75 | 35.81
2019-11-26 03:00 | 37.3 | 35.33
2019-11-26 03:30 | 37.2 | 35.23
2019-11-26 04:00 | 36.89 | 34.9
2019-11-26 04:30 | 37.61 | 35.67
2019-11-26 05:00 | 37.68 | 35.74
2019-11-26 05:30 | 38.9 | 37.02
2019-11-26 06:00 | 41.69 | 39.95
2019-11-26 06:30 | 46.67 | 45.12
2019-11-26 07:00 | 48.58 | 47.07
2019-11-26 07:30 | 54.61 | 52.51
2019-11-26 08:00 | 57.05 | 54.98
2019-11-26 08:30 | 60 | 57.66
2019-11-26 09:00 | 62.59 | 60.05
2019-11-26 09:30 | 60.37 | 59.45
2019-11-26 10:00 | 57.91 | 57.67
2019-11-26 10:30 | 58.69 | 58.45
2019-11-26 11:00 | 59.04 | 58.81
2019-11-26 11:30 | 57.48 | 57.24
2019-11-26 12:00 | 59.03 | 58.8
2019-11-26 12:30 | 59.4 | 59.17
2019-11-26 13:00 | 58.49 | 58.26
2019-11-26 13:30 | 59.85 | 59.63
2019-11-26 14:00 | 60.43 | 60.21
2019-11-26 14:30 | 61.78 | 61.57
2019-11-26 15:00 | 62.48 | 62.27
2019-11-26 15:30 | 63.25 | 63.04
2019-11-26 16:00 | 64.75 | 64.54
2019-11-26 16:30 | 66.07 | 65.86
2019-11-26 17:00 | 66.58 | 66.37
2019-11-26 17:30 | 65 | 64.76
2019-11-26 18:00 | 63.7 | 63.25
2019-11-26 18:30 | 62.96 | 62.33
2019-11-26 19:00 | 64.23 | 63.7
2019-11-26 19:30 | 63.5 | 62.91
2019-11-26 20:00 | 61.14 | 60.38
2019-11-26 20:30 | 59.24 | 58.29
2019-11-26 21:00 | 56.92 | 55.8
2019-11-26 21:30 | 55.2 | 53.89
2019-11-26 22:00 | 51.92 | 50.24
2019-11-26 22:30 | 49.81 | 47.83
2019-11-26 23:00 | 47.85 | 46.14
2019-11-26 23:30 | 44.36 | 43.73
2019-11-27 | 41.94 | 41.47
2019-11-27 00:30 | 40.35 | 39.87
2019-11-27 01:00 | 39.21 | 38.69
2019-11-27 01:30 | 39 | 38.47
2019-11-27 02:00 | 37.68 | 37.13
2019-11-27 02:30 | 37.04 | 36.47
2019-11-27 03:00 | 36.44 | 35.88
2019-11-27 03:30 | 36.47 | 35.91
2019-11-27 04:00 | 36.3 | 35.73
2019-11-27 04:30 | 37.14 | 36.59
2019-11-27 05:00 | 38.71 | 38.17
2019-11-27 05:30 | 39.12 | 38.6
2019-11-27 06:00 | 41.15 | 40.65
2019-11-27 06:30 | 45.6 | 44.86
2019-11-27 07:00 | 50.07 | 48.71
2019-11-27 07:30 | 55.75 | 53.52
2019-11-27 08:00 | 61.04 | 59.22
2019-11-27 08:30 | 61.55 | 59.34
2019-11-27 09:00 | 62.91 | 60.26
2019-11-27 09:30 | 64.32 | 61.5
2019-11-27 10:00 | 61.6 | 58.58
2019-11-27 10:30 | 64.6 | 61.31
2019-11-27 11:00 | 65.19 | 61.55
2019-11-27 11:30 | 67.33 | 63.61
2019-11-27 12:00 | 64.07 | 60.08
2019-11-27 12:30 | 65.88 | 62.11
2019-11-27 13:00 | 65.28 | 61.56
2019-11-27 13:30 | 66.16 | 62.39
2019-11-27 14:00 | 67.25 | 63.64
2019-11-27 14:30 | 67.77 | 64.34
2019-11-27 15:00 | 67.29 | 63.95
2019-11-27 15:30 | 68.03 | 65.05
2019-11-27 16:00 | 69.57 | 67
2019-11-27 16:30 | 69.66 | 67.56
2019-11-27 17:00 | 69.5 | 67.43
2019-11-27 17:30 | 67.79 | 65.63
2019-11-27 18:00 | 68.2 | 66.04
2019-11-27 18:30 | 67.78 | 65.61
2019-11-27 19:00 | 67.63 | 65.47
2019-11-27 19:30 | 66.54 | 64.32
2019-11-27 20:00 | 63.79 | 61.45
2019-11-27 20:30 | 60.89 | 59.01
2019-11-27 21:00 | 57.98 | 56.86
2019-11-27 21:30 | 55.45 | 54.27
2019-11-27 22:00 | 52.83 | 51.61
2019-11-27 22:30 | 50.61 | 49.35
2019-11-27 23:00 | 48.34 | 47.01
2019-11-27 23:30 | 46.34 | 44.95
2019-11-28 | 43.47 | 42.01
2019-11-28 00:30 | 42.03 | 40.51
2019-11-28 01:00 | 41 | 39.43
2019-11-28 01:30 | 40.41 | 38.82
2019-11-28 02:00 | 40.05 | 38.44
2019-11-28 02:30 | 39.21 | 37.55
2019-11-28 03:00 | 39 | 37.32
2019-11-28 03:30 | 39.35 | 37.69
2019-11-28 04:00 | 38.39 | 36.68
2019-11-28 04:30 | 39.13 | 37.46
2019-11-28 05:00 | 40.36 | 38.75
2019-11-28 05:30 | 41.66 | 40.11
2019-11-28 06:00 | 43.71 | 42.26
2019-11-28 06:30 | 47.8 | 46.5
2019-11-28 07:00 | 52.63 | 51.07
2019-11-28 07:30 | 58.2 | 55.84
2019-11-28 08:00 | 61.03 | 58.99
2019-11-28 08:30 | 62.69 | 60.18
2019-11-28 09:00 | 63.81 | 60.83
2019-11-28 09:30 | 63.39 | 60.1
2019-11-28 10:00 | 63.65 | 60.31
2019-11-28 10:30 | 64.35 | 60.78
2019-11-28 11:00 | 63.64 | 59.87
2019-11-28 11:30 | 63.46 | 59.66
2019-11-28 12:00 | 63.5 | 59.49
2019-11-28 12:30 | 65.18 | 61.39
2019-11-28 13:00 | 64.86 | 61.13
2019-11-28 13:30 | 65.73 | 61.89
2019-11-28 14:00 | 66.84 | 63.11
2019-11-28 14:30 | 67.63 | 64
2019-11-28 15:00 | 66.88 | 63.42
2019-11-28 15:30 | 67.05 | 63.9
2019-11-28 16:00 | 68.48 | 65.69
2019-11-28 16:30 | 68.23 | 66.02
2019-11-28 17:00 | 67.93 | 65.78
2019-11-28 17:30 | 67.3 | 65.09
2019-11-28 18:00 | 66.7 | 64.47
2019-11-28 18:30 | 67.19 | 64.99
2019-11-28 19:00 | 67.64 | 65.44
2019-11-28 19:30 | 66.42 | 64.14
2019-11-28 20:00 | 64.32 | 61.97
2019-11-28 20:30 | 62.15 | 59.68
2019-11-28 21:00 | 60.18 | 57.61
2019-11-28 21:30 | 58.35 | 55.64
2019-11-28 22:00 | 54.83 | 51.96
2019-11-28 22:30 | 52.47 | 49.41
2019-11-28 23:00 | 48.23 | 46.47
2019-11-28 23:30 | 45.64 | 44.19
2019-11-29 | 43.7 | 42.76
2019-11-29 00:30 | 41.85 | 41.42
2019-11-29 01:00 | 40.29 | 39.89
2019-11-29 01:30 | 39.37 | 39
2019-11-29 02:00 | 38.33 | 37.98
2019-11-29 02:30 | 38.06 | 37.71
2019-11-29 03:00 | 37.7 | 37.34
2019-11-29 03:30 | 37 | 36.62
2019-11-29 04:00 | 36.65 | 36.28
2019-11-29 04:30 | 37.4 | 37.03
2019-11-29 05:00 | 38.17 | 37.81
2019-11-29 05:30 | 39.16 | 38.81
2019-11-29 06:00 | 41.46 | 41.08
2019-11-29 06:30 | 45.85 | 45.04
2019-11-29 07:00 | 51.15 | 49.76
2019-11-29 07:30 | 57.32 | 55.15
2019-11-29 08:00 | 59.69 | 57.75
2019-11-29 08:30 | 60.01 | 57.82
2019-11-29 09:00 | 61.53 | 59.04
2019-11-29 09:30 | 62.41 | 59.72
2019-11-29 10:00 | 61.58 | 58.77
2019-11-29 10:30 | 61.58 | 58.64
2019-11-29 11:00 | 60.4 | 57.29
2019-11-29 11:30 | 62.92 | 59.65
2019-11-29 12:00 | 61.93 | 58.63
2019-11-29 12:30 | 61.01 | 57.83
2019-11-29 13:00 | 60.94 | 57.83
2019-11-29 13:30 | 60.67 | 57.71
2019-11-29 14:00 | 60.52 | 57.7
2019-11-29 14:30 | 61.51 | 58.91
2019-11-29 15:00 | 61.59 | 59.17
2019-11-29 15:30 | 61.2 | 59.13
2019-11-29 16:00 | 61.97 | 60.2
2019-11-29 16:30 | 62.65 | 61.27
2019-11-29 17:00 | 62.48 | 61.33
2019-11-29 17:30 | 61.63 | 60.64
2019-11-29 18:00 | 61.88 | 60.88
2019-11-29 18:30 | 60.86 | 59.85
2019-11-29 19:00 | 61.01 | 60
2019-11-29 19:30 | 60.98 | 59.98
2019-11-29 20:00 | 59.25 | 58.21
2019-11-29 20:30 | 57 | 55.91
2019-11-29 21:00 | 55.41 | 54.28
2019-11-29 21:30 | 53.94 | 52.76
2019-11-29 22:00 | 51.42 | 50.17
2019-11-29 22:30 | 49.43 | 48.11
2019-11-29 23:00 | 47.22 | 45.81
2019-11-29 23:30 | 44.73 | 43.52
2019-11-30 | 41.68 | 41.36
2019-11-30 00:30 | 40.21 | 39.88
2019-11-30 01:00 | 39.01 | 38.66
2019-11-30 01:30 | 38.29 | 37.93
2019-11-30 02:00 | 37.3 | 36.93
2019-11-30 02:30 | 36.81 | 36.43
2019-11-30 03:00 | 36.1 | 35.71
2019-11-30 03:30 | 35.7 | 35.31
2019-11-30 04:00 | 35.43 | 35.03
2019-11-30 04:30 | 35.33 | 34.93
2019-11-30 05:00 | 34.75 | 34.34
2019-11-30 05:30 | 34.52 | 34.32
2019-11-30 06:00 | 35.19 | 35.09
2019-11-30 06:30 | 36.97 | 36.8
2019-11-30 07:00 | 37.03 | 36.78
2019-11-30 07:30 | 39.57 | 39.08
2019-11-30 08:00 | 40.4 | 39.65
2019-11-30 08:30 | 42.58 | 41.53
2019-11-30 09:00 | 42.66 | 41.73
2019-11-30 09:30 | 42.73 | 42.14
2019-11-30 10:00 | 42.22 | 41.54
2019-11-30 10:30 | 42.78 | 42.06
2019-11-30 11:00 | 42.68 | 41.89
2019-11-30 11:30 | 42.76 | 41.92
2019-11-30 12:00 | 42.03 | 41.23
2019-11-30 12:30 | 41.37 | 40.7
2019-11-30 13:00 | 42.26 | 41.68
2019-11-30 13:30 | 41.71 | 41.18
2019-11-30 14:00 | 42.24 | 41.78
2019-11-30 14:30 | 43.47 | 43.07
2019-11-30 15:00 | 44.16 | 43.79
2019-11-30 15:30 | 45.94 | 45.61
2019-11-30 16:00 | 47.64 | 47.37
2019-11-30 16:30 | 48.6 | 48.43
2019-11-30 17:00 | 50.05 | 49.91
2019-11-30 17:30 | 52.63 | 52.5
2019-11-30 18:00 | 54.16 | 54.03
2019-11-30 18:30 | 54.62 | 54.51
2019-11-30 19:00 | 54.89 | 54.74
2019-11-30 19:30 | 55.01 | 54.83
2019-11-30 20:00 | 53.05 | 52.91
2019-11-30 20:30 | 51.17 | 51.07
2019-11-30 21:00 | 49.82 | 49.75
2019-11-30 21:30 | 48.32 | 48.27
2019-11-30 22:00 | 45.31 | 45.29
2019-11-30 22:30 | 43.66 | 43.63
2019-11-30 23:00 | 42.24 | 41.74
2019-11-30 23:30 | 40.47 | 39.94
2019-12-01 | 38.67 | 38.11
2019-12-01 00:30 | 37.16 | 36.61
2019-12-01 01:00 | 36.47 | 35.89
2019-12-01 01:30 | 35.77 | 35.18
2019-12-01 02:00 | 35.12 | 34.52
2019-12-01 02:30 | 35.16 | 34.55
2019-12-01 03:00 | 34.46 | 33.85
2019-12-01 03:30 | 33.77 | 33.14
2019-12-01 04:00 | 33.24 | 32.61
2019-12-01 04:30 | 33.25 | 32.62
2019-12-01 05:00 | 32.94 | 32.3
2019-12-01 05:30 | 32.42 | 31.76
2019-12-01 06:00 | 32.33 | 31.68
2019-12-01 06:30 | 32.89 | 32.24
2019-12-01 07:00 | 34.44 | 33.82
2019-12-01 07:30 | 34.66 | 34.05
2019-12-01 08:00 | 37.63 | 37.06
2019-12-01 08:30 | 38.2 | 37.64
2019-12-01 09:00 | 38.64 | 38.11
2019-12-01 09:30 | 39.07 | 38.49
2019-12-01 10:00 | 39.6 | 39.02
2019-12-01 10:30 | 41.22 | 40.71
2019-12-01 11:00 | 40.71 | 40.2
2019-12-01 11:30 | 40.46 | 39.95
2019-12-01 12:00 | 39.86 | 39.33
2019-12-01 12:30 | 41.89 | 41.4
2019-12-01 13:00 | 42.92 | 42.45
2019-12-01 13:30 | 41.72 | 41.24
2019-12-01 14:00 | 44.57 | 44.12
2019-12-01 14:30 | 43.36 | 42.89
2019-12-01 15:00 | 47.28 | 46.84
2019-12-01 15:30 | 50.04 | 49.63
2019-12-01 16:00 | 50.6 | 50.2
2019-12-01 16:30 | 50.66 | 50.27
2019-12-01 17:00 | 51.1 | 50.71
2019-12-01 17:30 | 53.4 | 53.04
2019-12-01 18:00 | 55.82 | 55.47
2019-12-01 18:30 | 56.59 | 56.25
2019-12-01 19:00 | 58.76 | 58.44
2019-12-01 19:30 | 58.23 | 57.91
2019-12-01 20:00 | 56.49 | 56.15
2019-12-01 20:30 | 55.59 | 55.23
2019-12-01 21:00 | 52.65 | 52.28
2019-12-01 21:30 | 50.51 | 50.12
2019-12-01 22:00 | 48.46 | 48.05
2019-12-01 22:30 | 46.14 | 45.71
2019-12-01 23:00 | 44.25 | 43.8
2019-12-01 23:30 | 42.27 | 41.79
2019-12-02 | 40.24 | 39.72
2019-12-02 00:30 | 40.02 | 39.5
2019-12-02 01:00 | 38.34 | 37.8
2019-12-02 01:30 | 37.73 | 37.17
2019-12-02 02:00 | 37.76 | 37.21
2019-12-02 02:30 | 37.51 | 36.95
2019-12-02 03:00 | 36.73 | 36.16
2019-12-02 03:30 | 36.31 | 35.73
2019-12-02 04:00 | 37.04 | 36.47
2019-12-02 04:30 | 37.72 | 37.16
2019-12-02 05:00 | 38.02 | 37.47
2019-12-02 05:30 | 39.89 | 39.36
2019-12-02 06:00 | 42.87 | 42.39
2019-12-02 06:30 | 48.93 | 48.09
2019-12-02 07:00 | 53.69 | 52.15
2019-12-02 07:30 | 60.39 | 58.53
2019-12-02 08:00 | 63.48 | 61.27
2019-12-02 08:30 | 66.38 | 63.55
2019-12-02 09:00 | 68.56 | 65.34
2019-12-02 09:30 | 70.24 | 66.75
2019-12-02 10:00 | 70.38 | 66.76
2019-12-02 10:30 | 72.07 | 68.13
2019-12-02 11:00 | 74.28 | 70.1
2019-12-02 11:30 | 75.84 | 71.5
2019-12-02 12:00 | 76.89 | 72.4
2019-12-02 12:30 | 77 | 72.62
2019-12-02 13:00 | 77.49 | 73.12
2019-12-02 13:30 | 78.5 | 74.23
2019-12-02 14:00 | 79.77 | 75.98
2019-12-02 14:30 | 80.57 | 77
2019-12-02 15:00 | 81.66 | 78.16
2019-12-02 15:30 | 83.34 | 79.92
2019-12-02 16:00 | 83.93 | 80.51
2019-12-02 16:30 | 83.6 | 80.13
2019-12-02 17:00 | 83.86 | 80.38
2019-12-02 17:30 | 80.71 | 77.82
2019-12-02 18:00 | 77.08 | 75
2019-12-02 18:30 | 73.49 | 72.45
2019-12-02 19:00 | 72.23 | 71.3
2019-12-02 19:30 | 70.83 | 69.94
2019-12-02 20:00 | 70.49 | 70.16
2019-12-02 20:30 | 70.22 | 69.83
2019-12-02 21:00 | 67.46 | 66.92
2019-12-02 21:30 | 61.9 | 61.06
2019-12-02 22:00 | 58.22 | 57.12
2019-12-02 22:30 | 55.08 | 53.62
2019-12-02 23:00 | 51.94 | 50.14
2019-12-02 23:30 | 49.57 | 47.44
2019-12-03 | 47.81 | 45.45
2019-12-03 00:30 | 45.08 | 43.54
2019-12-03 01:00 | 43.93 | 42.36
2019-12-03 01:30 | 42.82 | 41.14
2019-12-03 02:00 | 41.97 | 40.14
2019-12-03 02:30 | 41.19 | 39.14
2019-12-03 03:00 | 41.79 | 38.15
2019-12-03 03:30 | 41.45 | 37.78
2019-12-03 04:00 | 41.12 | 37.48
2019-12-03 04:30 | 41.94 | 38.4
2019-12-03 05:00 | 43.24 | 39.82
2019-12-03 05:30 | 44.41 | 41.1
2019-12-03 06:00 | 46.6 | 43.47
2019-12-03 06:30 | 51 | 48.17
2019-12-03 07:00 | 54.51 | 51.89
2019-12-03 07:30 | 58.52 | 57.13
2019-12-03 08:00 | 61.53 | 60.45
2019-12-03 08:30 | 63.36 | 62.38
2019-12-03 09:00 | 64.39 | 64.1
2019-12-03 09:30 | 65.58 | 65.3
2019-12-03 10:00 | 66.81 | 66.54
2019-12-03 10:30 | 68.24 | 67.9
2019-12-03 11:00 | 69.31 | 68.85
2019-12-03 11:30 | 70.87 | 70.32
2019-12-03 12:00 | 72.27 | 71.73
2019-12-03 12:30 | 73.17 | 72.67
2019-12-03 13:00 | 72.19 | 71.67
2019-12-03 13:30 | 73.09 | 72.54
2019-12-03 14:00 | 74.52 | 74.48
2019-12-03 14:30 | 74.88 | 74.88
2019-12-03 15:00 | 76.65 | 76.59
2019-12-03 15:30 | 78.41 | 78.26
2019-12-03 16:00 | 81.42 | 81.21
2019-12-03 16:30 | 80.49 | 80.13
2019-12-03 17:00 | 79.38 | 79.17
2019-12-03 17:30 | 77.38 | 76.85
2019-12-03 18:00 | 75.04 | 74.11
2019-12-03 18:30 | 73.9 | 72.65
2019-12-03 19:00 | 72.7 | 71.38
2019-12-03 19:30 | 72.01 | 70.63
2019-12-03 20:00 | 70.03 | 68.46
2019-12-03 20:30 | 68.73 | 66.89
2019-12-03 21:00 | 70.83 | 69.07
2019-12-03 21:30 | 66.22 | 64.95
2019-12-03 22:00 | 60.05 | 58.26
2019-12-03 22:30 | 56.21 | 53.98
2019-12-03 23:00 | 53.55 | 50.9
2019-12-03 23:30 | 51.46 | 48.47
2019-12-04 | 50.06 | 46.76
2019-12-04 00:30 | 49.39 | 44.3
2019-12-04 01:00 | 48.12 | 42.74
2019-12-04 01:30 | 47.35 | 41.85
2019-12-04 02:00 | 45.56 | 41.83
2019-12-04 02:30 | 45.83 | 42.5
2019-12-04 03:00 | 44.38 | 40.91
2019-12-04 03:30 | 43.45 | 39.91
2019-12-04 04:00 | 42.6 | 38.97
2019-12-04 04:30 | 43.3 | 39.74
2019-12-04 05:00 | 45.65 | 42.29
2019-12-04 05:30 | 45.34 | 41.95
2019-12-04 06:00 | 47.32 | 44.13
2019-12-04 06:30 | 51.77 | 50.36
2019-12-04 07:00 | 55.81 | 53.98
2019-12-04 07:30 | 62.22 | 59.85
2019-12-04 08:00 | 64.58 | 64.34
2019-12-04 08:30 | 67.43 | 67.22
2019-12-04 09:00 | 69.34 | 69.06
2019-12-04 09:30 | 70.96 | 70.59
2019-12-04 10:00 | 71.83 | 71.58
2019-12-04 10:30 | 72.4 | 72.2
2019-12-04 11:00 | 74.14 | 73.95
2019-12-04 11:30 | 74.54 | 74.35
2019-12-04 12:00 | 75.43 | 75.25
2019-12-04 12:30 | 76.08 | 75.89
2019-12-04 13:00 | 76.63 | 76.45
2019-12-04 13:30 | 77.82 | 77.64
2019-12-04 14:00 | 79.76 | 79.58
2019-12-04 14:30 | 80.87 | 80.7
2019-12-04 15:00 | 81.37 | 81.2
2019-12-04 15:30 | 82.13 | 81.97
2019-12-04 16:00 | 84.78 | 84.61
2019-12-04 16:30 | 85.54 | 85.38
2019-12-04 17:00 | 85.02 | 84.85
2019-12-04 17:30 | 81.74 | 81.41
2019-12-04 18:00 | 79.72 | 79.06
2019-12-04 18:30 | 78.48 | 77.6
2019-12-04 19:00 | 80.01 | 79.3
2019-12-04 19:30 | 79.6 | 78.81
2019-12-04 20:00 | 77.86 | 76.91
2019-12-04 20:30 | 75.39 | 74.23
2019-12-04 21:00 | 73.9 | 72.71
2019-12-04 21:30 | 71.69 | 70.98
2019-12-04 22:00 | 74.14 | 73.39
2019-12-04 22:30 | 68.42 | 67.29
2019-12-04 23:00 | 62.65 | 61.07
2019-12-04 23:30 | 58.39 | 56.72
2019-12-05 | 55.66 | 54.41
2019-12-05 00:30 | 53.77 | 52.47
2019-12-05 01:00 | 52.6 | 51.27
2019-12-05 01:30 | 51.62 | 50.26
2019-12-05 02:00 | 50.74 | 49.36
2019-12-05 02:30 | 50.16 | 48.76
2019-12-05 03:00 | 49 | 47.55
2019-12-05 03:30 | 48.54 | 47.08
2019-12-05 04:00 | 48.14 | 46.65
2019-12-05 04:30 | 48.57 | 47.1
2019-12-05 05:00 | 49.73 | 48.3
2019-12-05 05:30 | 51.38 | 49.99
2019-12-05 06:00 | 53.9 | 52.58
2019-12-05 06:30 | 59.97 | 58.91
2019-12-05 07:00 | 65.11 | 63.53
2019-12-05 07:30 | 71.88 | 70.13
2019-12-05 08:00 | 74.3 | 73.81
2019-12-05 08:30 | 75.92 | 75.73
2019-12-05 09:00 | 76.82 | 76.64
2019-12-05 09:30 | 76.49 | 76.3
2019-12-05 10:00 | 76.09 | 75.89
2019-12-05 10:30 | 72.59 | 72.38
2019-12-05 11:00 | 77.54 | 77.35
2019-12-05 11:30 | 77.66 | 77.47
2019-12-05 12:00 | 79.24 | 79.05
2019-12-05 12:30 | 80.01 | 79.83
2019-12-05 13:00 | 80.33 | 80.15
2019-12-05 13:30 | 81.61 | 81.44
2019-12-05 14:00 | 83.13 | 82.96
2019-12-05 14:30 | 85.1 | 84.93
2019-12-05 15:00 | 86.27 | 86.1
2019-12-05 15:30 | 73.53 | 73.33
2019-12-05 16:00 | 88.15 | 87.97
2019-12-05 16:30 | 83.5 | 83.26
2019-12-05 17:00 | 82.12 | 81.93
2019-12-05 17:30 | 80.34 | 79.99
2019-12-05 18:00 | 79.81 | 79.19
2019-12-05 18:30 | 74.96 | 74.12
2019-12-05 19:00 | 77.72 | 76.76
2019-12-05 19:30 | 77.43 | 76.4
2019-12-05 20:00 | 76.06 | 74.92
2019-12-05 20:30 | 73.95 | 72.64
2019-12-05 21:00 | 73.47 | 72.07
2019-12-05 21:30 | 72.83 | 71.25
2019-12-05 22:00 | 72.42 | 70.67
2019-12-05 22:30 | 63.65 | 60.55
2019-12-05 23:00 | 58.61 | 55.91
2019-12-05 23:30 | 55.71 | 53.09
2019-12-06 | 53.53 | 50.79
2019-12-06 00:30 | 52.04 | 49.22
2019-12-06 01:00 | 50.83 | 47.9
2019-12-06 01:30 | 50.56 | 47.61
2019-12-06 02:00 | 50.23 | 47.27
2019-12-06 02:30 | 49.64 | 46.64
2019-12-06 03:00 | 48.99 | 45.93
2019-12-06 03:30 | 48.54 | 45.45
2019-12-06 04:00 | 48.09 | 44.96
2019-12-06 04:30 | 48.59 | 45.49
2019-12-06 05:00 | 50.02 | 47.02
2019-12-06 05:30 | 51.67 | 48.78
2019-12-06 06:00 | 53.37 | 51.26
2019-12-06 06:30 | 58.15 | 57.12
2019-12-06 07:00 | 62.65 | 61.41
2019-12-06 07:30 | 69.51 | 68.01
2019-12-06 08:00 | 72.64 | 70.96
2019-12-06 08:30 | 75.77 | 73.46
2019-12-06 09:00 | 77.58 | 74.91
2019-12-06 09:30 | 77.45 | 74.75
2019-12-06 10:00 | 76.82 | 74.09
2019-12-06 10:30 | 77.64 | 74.01
2019-12-06 11:00 | 80.19 | 74.53
2019-12-06 11:30 | 80.56 | 75.09
2019-12-06 12:00 | 81.19 | 75.67
2019-12-06 12:30 | 81.34 | 75.81
2019-12-06 13:00 | 81.55 | 76.03
2019-12-06 13:30 | 82.08 | 76.58
2019-12-06 14:00 | 82.79 | 77.33
2019-12-06 14:30 | 83.71 | 78.31
2019-12-06 15:00 | 83.94 | 78.57
2019-12-06 15:30 | 84.57 | 79.21
2019-12-06 16:00 | 86.76 | 81.54
2019-12-06 16:30 | 85.68 | 80.33
2019-12-06 17:00 | 84.65 | 79.19
2019-12-06 17:30 | 83.12 | 77.48
2019-12-06 18:00 | 80.99 | 75.12
2019-12-06 18:30 | 79.43 | 73.39
2019-12-06 19:00 | 78.98 | 72.92
2019-12-06 19:30 | 77.78 | 71.59
2019-12-06 20:00 | 73.05 | 69.03
2019-12-06 20:30 | 71.94 | 67.88
2019-12-06 21:00 | 72.85 | 68.83
2019-12-06 21:30 | 69.79 | 65.53
2019-12-06 22:00 | 63.92 | 61.2
2019-12-06 22:30 | 60.51 | 58.1
2019-12-06 23:00 | 56.86 | 55.71
2019-12-06 23:30 | 54.43 | 53.21
2019-12-07 | 51.79 | 50.97
2019-12-07 00:30 | 49.52 | 49.23
2019-12-07 01:00 | 47.77 | 47.47
2019-12-07 01:30 | 46.57 | 46.28
2019-12-07 02:00 | 46.05 | 45.75
2019-12-07 02:30 | 44.96 | 44.65
2019-12-07 03:00 | 44.29 | 43.97
2019-12-07 03:30 | 43.48 | 43.15
2019-12-07 04:00 | 42.84 | 42.51
2019-12-07 04:30 | 42.76 | 42.45
2019-12-07 05:00 | 43.49 | 43.17
2019-12-07 05:30 | 43.7 | 43.39
2019-12-07 06:00 | 44.19 | 43.86
2019-12-07 06:30 | 47.43 | 46.88
2019-12-07 07:00 | 49.55 | 48.76
2019-12-07 07:30 | 52.55 | 51.43
2019-12-07 08:00 | 54.57 | 53.25
2019-12-07 08:30 | 53.88 | 53.12
2019-12-07 09:00 | 53.53 | 52.61
2019-12-07 09:30 | 56.36 | 55.25
2019-12-07 10:00 | 56.37 | 55.16
2019-12-07 10:30 | 57.23 | 55.83
2019-12-07 11:00 | 57.5 | 56.08
2019-12-07 11:30 | 57.33 | 55.91
2019-12-07 12:00 | 57.37 | 55.99
2019-12-07 12:30 | 56.84 | 55.64
2019-12-07 13:00 | 55.46 | 54.31
2019-12-07 13:30 | 54.55 | 53.45
2019-12-07 14:00 | 55.07 | 54.02
2019-12-07 14:30 | 56.94 | 56
2019-12-07 15:00 | 57.08 | 56.22
2019-12-07 15:30 | 57.91 | 57.01
2019-12-07 16:00 | 60.99 | 60.23
2019-12-07 16:30 | 61.41 | 60.8
2019-12-07 17:00 | 63.65 | 63.1
2019-12-07 17:30 | 65.33 | 64.85
2019-12-07 18:00 | 65.86 | 65.44
2019-12-07 18:30 | 64.89 | 64.56
2019-12-07 19:00 | 65.15 | 64.78
2019-12-07 19:30 | 65.5 | 65.08
2019-12-07 20:00 | 63.72 | 63.33
2019-12-07 20:30 | 61.33 | 60.98
2019-12-07 21:00 | 59.63 | 59.32
2019-12-07 21:30 | 57.7 | 57.44
2019-12-07 22:00 | 55.89 | 55.66
2019-12-07 22:30 | 54.41 | 54.17
2019-12-07 23:00 | 52.07 | 51.81
2019-12-07 23:30 | 49.57 | 49.3
2019-12-08 | 47.61 | 47.32
2019-12-08 00:30 | 46.18 | 45.87
2019-12-08 01:00 | 44.81 | 44.49
2019-12-08 01:30 | 43.73 | 43.42
2019-12-08 02:00 | 43.11 | 42.8
2019-12-08 02:30 | 42.4 | 42.08
2019-12-08 03:00 | 41.64 | 41.32
2019-12-08 03:30 | 41.17 | 40.84
2019-12-08 04:00 | 40.23 | 39.89
2019-12-08 04:30 | 40.49 | 40.15
2019-12-08 05:00 | 40.43 | 40.09
2019-12-08 05:30 | 39.53 | 39.18
2019-12-08 06:00 | 39.62 | 39.28
2019-12-08 06:30 | 42.87 | 42.54
2019-12-08 07:00 | 44.72 | 44.25
2019-12-08 07:30 | 46.73 | 46.06
2019-12-08 08:00 | 42.98 | 42.32
2019-12-08 08:30 | 42.91 | 42.17
2019-12-08 09:00 | 44.02 | 43.17
2019-12-08 09:30 | 44.9 | 44.48
2019-12-08 10:00 | 45.58 | 45.18
2019-12-08 10:30 | 46.28 | 45.79
2019-12-08 11:00 | 47.08 | 46.55
2019-12-08 11:30 | 47.17 | 46.63
2019-12-08 12:00 | 47.93 | 47.39
2019-12-08 12:30 | 49.69 | 49.12
2019-12-08 13:00 | 49.83 | 49.27
2019-12-08 13:30 | 50.63 | 50.07
2019-12-08 14:00 | 51.41 | 50.89
2019-12-08 14:30 | 51.79 | 51.32
2019-12-08 15:00 | 52.42 | 52.02
2019-12-08 15:30 | 54.19 | 53.81
2019-12-08 16:00 | 55.65 | 55.31
2019-12-08 16:30 | 57.4 | 57.07
2019-12-08 17:00 | 57.01 | 56.74
2019-12-08 17:30 | 57.78 | 57.55
2019-12-08 18:00 | 60.81 | 60.57
2019-12-08 18:30 | 61.87 | 61.63
2019-12-08 19:00 | 62.39 | 62.12
2019-12-08 19:30 | 62.71 | 62.41
2019-12-08 20:00 | 60.89 | 60.63
2019-12-08 20:30 | 58.59 | 58.36
2019-12-08 21:00 | 56.39 | 56.16
2019-12-08 21:30 | 53.83 | 53.58
2019-12-08 22:00 | 51.09 | 50.83
2019-12-08 22:30 | 48.54 | 48.25
2019-12-08 23:00 | 46.16 | 45.86
2019-12-08 23:30 | 43.92 | 43.61
2019-12-09 | 42.37 | 42.05
2019-12-09 00:30 | 40.93 | 40.6
2019-12-09 01:00 | 40.05 | 39.71
2019-12-09 01:30 | 39.41 | 39.06
2019-12-09 02:00 | 39 | 38.65
2019-12-09 02:30 | 38.7 | 38.34
2019-12-09 03:00 | 38.28 | 37.92
2019-12-09 03:30 | 38.34 | 37.98
2019-12-09 04:00 | 38.2 | 37.84
2019-12-09 04:30 | 38.84 | 38.49
2019-12-09 05:00 | 40.42 | 40.08
2019-12-09 05:30 | 41.84 | 41.51
2019-12-09 06:00 | 44.68 | 44.3
2019-12-09 06:30 | 50.15 | 49.32
2019-12-09 07:00 | 55.23 | 53.82
2019-12-09 07:30 | 61.84 | 59.53
2019-12-09 08:00 | 64.8 | 62.89
2019-12-09 08:30 | 67.11 | 64.7
2019-12-09 09:00 | 67.12 | 64.29
2019-12-09 09:30 | 68.31 | 65.34
2019-12-09 10:00 | 68.43 | 65.31
2019-12-09 10:30 | 66.93 | 63.55
2019-12-09 11:00 | 68.55 | 65
2019-12-09 11:30 | 68.11 | 67.1
2019-12-09 12:00 | 67.27 | 66.33
2019-12-09 12:30 | 66.6 | 65.65
2019-12-09 13:00 | 66.79 | 65.84
2019-12-09 13:30 | 66.9 | 65.95
2019-12-09 14:00 | 68.01 | 67.07
2019-12-09 14:30 | 68.77 | 67.85
2019-12-09 15:00 | 69.64 | 68.73
2019-12-09 15:30 | 70.53 | 69.62
2019-12-09 16:00 | 71.58 | 70.69
2019-12-09 16:30 | 71.83 | 70.9
2019-12-09 17:00 | 71.39 | 70.49
2019-12-09 17:30 | 69.04 | 68.49
2019-12-09 18:00 | 67.87 | 66.99
2019-12-09 18:30 | 67.85 | 66.74
2019-12-09 19:00 | 68.88 | 67.84
2019-12-09 19:30 | 68.57 | 67.54
2019-12-09 20:00 | 67.05 | 65.89
2019-12-09 20:30 | 64.92 | 63.59
2019-12-09 21:00 | 62.78 | 61.22
2019-12-09 21:30 | 59.87 | 58.91
2019-12-09 22:00 | 56.1 | 55.75
2019-12-09 22:30 | 53.49 | 53.13
2019-12-09 23:00 | 51.1 | 50.72
2019-12-09 23:30 | 48.98 | 48.57
2019-12-10 | 47.42 | 47
2019-12-10 00:30 | 45.8 | 45.36
2019-12-10 01:00 | 44.64 | 44.19
2019-12-10 01:30 | 43.93 | 43.47
2019-12-10 02:00 | 43.25 | 42.78
2019-12-10 02:30 | 42.69 | 42.21
2019-12-10 03:00 | 42.02 | 41.53
2019-12-10 03:30 | 41.56 | 41.07
2019-12-10 04:00 | 41.37 | 40.88
2019-12-10 04:30 | 41.71 | 41.22
2019-12-10 05:00 | 42.91 | 42.43
2019-12-10 05:30 | 44.49 | 44.03
2019-12-10 06:00 | 46.42 | 45.98
2019-12-10 06:30 | 51.53 | 51.04
2019-12-10 07:00 | 56.15 | 55.22
2019-12-10 07:30 | 62.29 | 60.88
2019-12-10 08:00 | 64.2 | 63.54
2019-12-10 08:30 | 65.92 | 65.02
2019-12-10 09:00 | 66.79 | 65.66
2019-12-10 09:30 | 66.61 | 65.39
2019-12-10 10:00 | 65.34 | 64.01
2019-12-10 10:30 | 65.23 | 63.81
2019-12-10 11:00 | 65.97 | 64.47
2019-12-10 11:30 | 65.97 | 64.35
2019-12-10 12:00 | 67.02 | 65.32
2019-12-10 12:30 | 68.84 | 67.18
2019-12-10 13:00 | 69.43 | 67.78
2019-12-10 13:30 | 70.75 | 69.1
2019-12-10 14:00 | 71.36 | 69.64
2019-12-10 14:30 | 71.7 | 70.11
2019-12-10 15:00 | 72.55 | 70.98
2019-12-10 15:30 | 73.79 | 72.45
2019-12-10 16:00 | 74.09 | 73.04
2019-12-10 16:30 | 73.82 | 73.02
2019-12-10 17:00 | 73.49 | 72.96
2019-12-10 17:30 | 71.41 | 71.15
2019-12-10 18:00 | 68.92 | 68.73
2019-12-10 18:30 | 68.8 | 68.6
2019-12-10 19:00 | 69.52 | 69.33
2019-12-10 19:30 | 69.53 | 69.34
2019-12-10 20:00 | 67.27 | 67.07
2019-12-10 20:30 | 65.19 | 64.98
2019-12-10 21:00 | 63.08 | 62.86
2019-12-10 21:30 | 60.46 | 60.22
2019-12-10 22:00 | 57.79 | 57.54
2019-12-10 22:30 | 54.63 | 54.36
2019-12-10 23:00 | 52.05 | 51.76
2019-12-10 23:30 | 49.65 | 49.35
2019-12-11 | 47.12 | 47.09
2019-12-11 00:30 | 45.36 | 45.34
2019-12-11 01:00 | 44.06 | 44.04
2019-12-11 01:30 | 41.82 | 41.78
2019-12-11 02:00 | 36.69 | 36.57
2019-12-11 02:30 | 40.19 | 40.15
2019-12-11 03:00 | 40.68 | 40.67
2019-12-11 03:30 | 40.59 | 40.52
2019-12-11 04:00 | 40.16 | 39.92
2019-12-11 04:30 | 40.9 | 40.65
2019-12-11 05:00 | 42.14 | 41.81
2019-12-11 05:30 | 43.94 | 43.56
2019-12-11 06:00 | 46.1 | 45.57
2019-12-11 06:30 | 51.12 | 50.15
2019-12-11 07:00 | 55.5 | 53.96
2019-12-11 07:30 | 61.47 | 58.98
2019-12-11 08:00 | 65.25 | 62.77
2019-12-11 08:30 | 68.89 | 65.85
2019-12-11 09:00 | 69.78 | 66.35
2019-12-11 09:30 | 70.37 | 66.74
2019-12-11 10:00 | 69.9 | 66.18
2019-12-11 10:30 | 70.11 | 66.25
2019-12-11 11:00 | 71.71 | 67.52
2019-12-11 11:30 | 71.88 | 67.65
2019-12-11 12:00 | 70.76 | 68.55
2019-12-11 12:30 | 70.65 | 68.46
2019-12-11 13:00 | 71.22 | 69.05
2019-12-11 13:30 | 71.76 | 69.59
2019-12-11 14:00 | 72.58 | 70.45
2019-12-11 14:30 | 73.7 | 71.6
2019-12-11 15:00 | 74.69 | 72.63
2019-12-11 15:30 | 75.74 | 73.7
2019-12-11 16:00 | 77.32 | 75.32
2019-12-11 16:30 | 77.49 | 75.48
2019-12-11 17:00 | 76.02 | 74.92
2019-12-11 17:30 | 73.68 | 73.27
2019-12-11 18:00 | 73.24 | 72.75
2019-12-11 18:30 | 72.64 | 71.96
2019-12-11 19:00 | 71.28 | 70.53
2019-12-11 19:30 | 70.52 | 69.72
2019-12-11 20:00 | 69.08 | 68.13
2019-12-11 20:30 | 66.78 | 65.65
2019-12-11 21:00 | 67.38 | 66.19
2019-12-11 21:30 | 67.27 | 65.96
2019-12-11 22:00 | 62.69 | 61
2019-12-11 22:30 | 57.7 | 55.39
2019-12-11 23:00 | 53.87 | 52.21
2019-12-11 23:30 | 50.03 | 49.65
2019-12-12 | 48.16 | 47.76
2019-12-12 00:30 | 46.06 | 45.63
2019-12-12 01:00 | 44.67 | 44.22
2019-12-12 01:30 | 43.85 | 43.39
2019-12-12 02:00 | 42.81 | 42.34
2019-12-12 02:30 | 42.41 | 41.93
2019-12-12 03:00 | 41.67 | 41.19
2019-12-12 03:30 | 41.05 | 40.56
2019-12-12 04:00 | 40.86 | 40.37
2019-12-12 04:30 | 42.25 | 41.79
2019-12-12 05:00 | 43.44 | 42.96
2019-12-12 05:30 | 45.74 | 45.22
2019-12-12 06:00 | 48 | 47.33
2019-12-12 06:30 | 52.5 | 51.39
2019-12-12 07:00 | 56.92 | 55.5
2019-12-12 07:30 | 61.54 | 60.79
2019-12-12 08:00 | 64.65 | 64.4
2019-12-12 08:30 | 65.61 | 65.39
2019-12-12 09:00 | 69.11 | 68.91
2019-12-12 09:30 | 69.31 | 69.1
2019-12-12 10:00 | 69.52 | 69.32
2019-12-12 10:30 | 68.7 | 68.49
2019-12-12 11:00 | 69.04 | 68.84
2019-12-12 11:30 | 69.37 | 69.17
2019-12-12 12:00 | 69.6 | 69.4
2019-12-12 12:30 | 70.86 | 70.67
2019-12-12 13:00 | 70.73 | 70.54
2019-12-12 13:30 | 72.12 | 71.93
2019-12-12 14:00 | 73.34 | 73.16
2019-12-12 14:30 | 74.57 | 74.39
2019-12-12 15:00 | 75.34 | 75.16
2019-12-12 15:30 | 76.77 | 76.6
2019-12-12 16:00 | 77.72 | 77.54
2019-12-12 16:30 | 77.67 | 77.49
2019-12-12 17:00 | 76.17 | 75.98
2019-12-12 17:30 | 74.96 | 74.73
2019-12-12 18:00 | 74.37 | 73.97
2019-12-12 18:30 | 73.64 | 73.04
2019-12-12 19:00 | 73.11 | 72.47
2019-12-12 19:30 | 72.65 | 72
2019-12-12 20:00 | 70.64 | 69.8
2019-12-12 20:30 | 69.66 | 68.68
2019-12-12 21:00 | 69.7 | 68.7
2019-12-12 21:30 | 65.22 | 63.87
2019-12-12 22:00 | 61.9 | 60.17
2019-12-12 22:30 | 56.38 | 55.91
2019-12-12 23:00 | 53.18 | 53.17
2019-12-12 23:30 | 50.85 | 50.85
2019-12-13 | 48.62 | 48.59
2019-12-13 00:30 | 47.23 | 47.11
2019-12-13 01:00 | 46.11 | 46
2019-12-13 01:30 | 45.2 | 45.1
2019-12-13 02:00 | 44.12 | 44.05
2019-12-13 02:30 | 43.29 | 43.25
2019-12-13 03:00 | 42.39 | 42.36
2019-12-13 03:30 | 41.96 | 41.95
2019-12-13 04:00 | 41.86 | 41.84
2019-12-13 04:30 | 42.25 | 42.23
2019-12-13 05:00 | 43.74 | 43.7
2019-12-13 05:30 | 45.42 | 45.36
2019-12-13 06:00 | 47.94 | 47.79
2019-12-13 06:30 | 52.74 | 52.28
2019-12-13 07:00 | 57.71 | 56.74
2019-12-13 07:30 | 59.44 | 58.08
2019-12-13 08:00 | 47.86 | 47.18
2019-12-13 08:30 | 41.55 | 40.96
2019-12-13 09:00 | 43.62 | 42.71
2019-12-13 09:30 | 43.64 | 42.63
2019-12-13 10:00 | 43.57 | 42.5
2019-12-13 10:30 | 44.46 | 43.22
2019-12-13 11:00 | 44.88 | 43.59
2019-12-13 11:30 | 45.7 | 44.34
2019-12-13 12:00 | 45.99 | 44.59
2019-12-13 12:30 | 46.77 | 45.33
2019-12-13 13:00 | 47.96 | 46.44
2019-12-13 13:30 | 48.66 | 47.19
2019-12-13 14:00 | 49.02 | 47.64
2019-12-13 14:30 | 49.4 | 48.07
2019-12-13 15:00 | 50.05 | 48.91
2019-12-13 15:30 | 50.78 | 49.77
2019-12-13 16:00 | 51.81 | 50.89
2019-12-13 16:30 | 53.06 | 52.24
2019-12-13 17:00 | 53.28 | 52.61
2019-12-13 17:30 | 50.92 | 50.47
2019-12-13 18:00 | 48.52 | 48.22
2019-12-13 18:30 | 48.09 | 47.82
2019-12-13 19:00 | 47.25 | 46.98
2019-12-13 19:30 | 46.66 | 46.38
2019-12-13 20:00 | 45.6 | 45.31
2019-12-13 20:30 | 44.69 | 44.4
2019-12-13 21:00 | 43.24 | 42.94
2019-12-13 21:30 | 41.92 | 41.6
2019-12-13 22:00 | 39.52 | 39.18
2019-12-13 22:30 | 37.43 | 37.07
2019-12-13 23:00 | 35.82 | 35.43
2019-12-13 23:30 | 34.14 | 33.73
2019-12-14 | 32.76 | 32.33
2019-12-14 00:30 | 31.51 | 31.07
2019-12-14 01:00 | 30.79 | 30.35
2019-12-14 01:30 | 30.19 | 29.74
2019-12-14 02:00 | 29.44 | 28.98
2019-12-14 02:30 | 28.92 | 28.45
2019-12-14 03:00 | 28.32 | 27.84
2019-12-14 03:30 | 28.31 | 27.82
2019-12-14 04:00 | 28.01 | 27.52
2019-12-14 04:30 | 28.1 | 27.61
2019-12-14 05:00 | 28.22 | 27.73
2019-12-14 05:30 | 28.16 | 27.67
2019-12-14 06:00 | 28.37 | 27.88
2019-12-14 06:30 | 29.82 | 29.36
2019-12-14 07:00 | 30.96 | 30.52
2019-12-14 07:30 | 32.45 | 32.04
2019-12-14 08:00 | 34.64 | 34.16
2019-12-14 08:30 | 36.66 | 36.27
2019-12-14 09:00 | 38.64 | 38.3
2019-12-14 09:30 | 40.07 | 39.75
2019-12-14 10:00 | 40.16 | 39.83
2019-12-14 10:30 | 40.11 | 39.72
2019-12-14 11:00 | 42.52 | 42.01
2019-12-14 11:30 | 42.15 | 41.61
2019-12-14 12:00 | 42.83 | 42.29
2019-12-14 12:30 | 41.24 | 40.76
2019-12-14 13:00 | 41.3 | 40.81
2019-12-14 13:30 | 41.57 | 41.13
2019-12-14 14:00 | 42.03 | 41.61
2019-12-14 14:30 | 42.05 | 41.71
2019-12-14 15:00 | 42.79 | 42.49
2019-12-14 15:30 | 43.61 | 43.32
2019-12-14 16:00 | 44.93 | 44.65
2019-12-14 16:30 | 44.36 | 44.07
2019-12-14 17:00 | 44.52 | 44.24
2019-12-14 17:30 | 44.6 | 44.31
2019-12-14 18:00 | 44.44 | 44.15
2019-12-14 18:30 | 43.88 | 43.58
2019-12-14 19:00 | 43.81 | 43.52
2019-12-14 19:30 | 43.33 | 43.03
2019-12-14 20:00 | 42.38 | 42.07
2019-12-14 20:30 | 40.9 | 40.58
2019-12-14 21:00 | 35.43 | 35.04
2019-12-14 21:30 | 32.79 | 32.36
2019-12-14 22:00 | 31.51 | 31.06
2019-12-14 22:30 | 29.87 | 29.39
2019-12-14 23:00 | 28.41 | 27.91
2019-12-14 23:30 | 27.02 | 26.48
2019-12-15 | 26.05 | 25.49
2019-12-15 00:30 | 25.39 | 24.86
2019-12-15 01:00 | 24.49 | 23.93
2019-12-15 01:30 | 24.09 | 23.53
2019-12-15 02:00 | 23.89 | 23.32
2019-12-15 02:30 | 23.41 | 22.82
2019-12-15 03:00 | 23.06 | 22.46
2019-12-15 03:30 | 22.87 | 22.27
2019-12-15 04:00 | 22.6 | 21.99
2019-12-15 04:30 | 22.84 | 22.24
2019-12-15 05:00 | 22.95 | 22.35
2019-12-15 05:30 | 22.65 | 22.04
2019-12-15 06:00 | 22.65 | 22.04
2019-12-15 06:30 | 23.43 | 22.84
2019-12-15 07:00 | 23.89 | 23.32
2019-12-15 07:30 | 24.98 | 24.44
2019-12-15 08:00 | 25.72 | 25.2
2019-12-15 08:30 | 26.53 | 26.03
2019-12-15 09:00 | 27.66 | 27.19
2019-12-15 09:30 | 29.73 | 29.28
2019-12-15 10:00 | 30.78 | 30.34
2019-12-15 10:30 | 31.54 | 31.12
2019-12-15 11:00 | 32.01 | 31.6
2019-12-15 11:30 | 33.03 | 32.64
2019-12-15 12:00 | 33.05 | 32.65
2019-12-15 12:30 | 33.78 | 33.4
2019-12-15 13:00 | 35.12 | 34.75
2019-12-15 13:30 | 36.56 | 36.21
2019-12-15 14:00 | 36.98 | 36.63
2019-12-15 14:30 | 37.55 | 37.21
2019-12-15 15:00 | 38.36 | 38.03
2019-12-15 15:30 | 38.69 | 38.36
2019-12-15 16:00 | 39.95 | 39.63
2019-12-15 16:30 | 40.75 | 40.44
2019-12-15 17:00 | 41.46 | 41.16
2019-12-15 17:30 | 42.08 | 41.77
2019-12-15 18:00 | 43 | 42.7
2019-12-15 18:30 | 43.01 | 42.71
2019-12-15 19:00 | 42.96 | 42.67
2019-12-15 19:30 | 43.22 | 42.93
2019-12-15 20:00 | 42.19 | 41.89
2019-12-15 20:30 | 41.02 | 40.7
2019-12-15 21:00 | 39.45 | 39.11
2019-12-15 21:30 | 37.39 | 37.03
2019-12-15 22:00 | 35.81 | 35.44
2019-12-15 22:30 | 33.5 | 33.09
2019-12-15 23:00 | 31.88 | 31.45
2019-12-15 23:30 | 30.55 | 30.1
2019-12-16 | 29.29 | 28.82
2019-12-16 00:30 | 28.39 | 27.9
2019-12-16 01:00 | 27.47 | 26.97
2019-12-16 01:30 | 26.75 | 26.25
2019-12-16 02:00 | 26.35 | 25.84
2019-12-16 02:30 | 26.15 | 25.63
2019-12-16 03:00 | 25.75 | 25.23
2019-12-16 03:30 | 25.46 | 24.93
2019-12-16 04:00 | 25.44 | 24.92
2019-12-16 04:30 | 25.9 | 25.38
2019-12-16 05:00 | 26.21 | 25.7
2019-12-16 05:30 | 26.63 | 26.13
2019-12-16 06:00 | 27.84 | 27.36
2019-12-16 06:30 | 30.84 | 30.42
2019-12-16 07:00 | 33.16 | 32.76
2019-12-16 07:30 | 36.59 | 36.15
2019-12-16 08:00 | 39.54 | 39.17
2019-12-16 08:30 | 42.23 | 41.54
2019-12-16 09:00 | 43.67 | 42.77
2019-12-16 09:30 | 43.66 | 42.7
2019-12-16 10:00 | 44.24 | 43.17
2019-12-16 10:30 | 44.64 | 43.51
2019-12-16 11:00 | 45.32 | 44.08
2019-12-16 11:30 | 46.55 | 45.21
2019-12-16 12:00 | 47.5 | 46.1
2019-12-16 12:30 | 47.73 | 46.46
2019-12-16 13:00 | 47.98 | 46.75
2019-12-16 13:30 | 50.14 | 48.78
2019-12-16 14:00 | 51.04 | 49.63
2019-12-16 14:30 | 51.73 | 50.29
2019-12-16 15:00 | 50.95 | 50.49
2019-12-16 15:30 | 52.19 | 51.84
2019-12-16 16:00 | 52.7 | 52.31
2019-12-16 16:30 | 53.63 | 53.21
2019-12-16 17:00 | 54.15 | 53.6
2019-12-16 17:30 | 53.43 | 52.57
2019-12-16 18:00 | 51.47 | 50.08
2019-12-16 18:30 | 50.86 | 49.15
2019-12-16 19:00 | 50.69 | 48.9
2019-12-16 19:30 | 49.84 | 48
2019-12-16 20:00 | 48.74 | 46.69
2019-12-16 20:30 | 47.1 | 44.73
2019-12-16 21:00 | 46.12 | 43.54
2019-12-16 21:30 | 45.62 | 42.86
2019-12-16 22:00 | 42.09 | 38.84
2019-12-16 22:30 | 37.59 | 35.73
2019-12-16 23:00 | 35.83 | 33.86
2019-12-16 23:30 | 34.56 | 32.5
2019-12-17 | 33.15 | 31
2019-12-17 00:30 | 31.93 | 29.68
2019-12-17 01:00 | 31.59 | 29.32
2019-12-17 01:30 | 30.82 | 28.48
2019-12-17 02:00 | 30.18 | 27.78
2019-12-17 02:30 | 29.91 | 27.45
2019-12-17 03:00 | 29.44 | 26.94
2019-12-17 03:30 | 29.17 | 26.65
2019-12-17 04:00 | 29.22 | 26.7
2019-12-17 04:30 | 29.24 | 26.73
2019-12-17 05:00 | 29.56 | 27.07
2019-12-17 05:30 | 30.01 | 27.56
2019-12-17 06:00 | 30.7 | 28.31
2019-12-17 06:30 | 33.91 | 31.77
2019-12-17 07:00 | 36.06 | 34.06
2019-12-17 07:30 | 39.1 | 38.47
2019-12-17 08:00 | 41.97 | 41.48
2019-12-17 08:30 | 44.7 | 44.1
2019-12-17 09:00 | 44.99 | 44.11
2019-12-17 09:30 | 45.81 | 44.8
2019-12-17 10:00 | 46.05 | 44.99
2019-12-17 10:30 | 45.67 | 44.57
2019-12-17 11:00 | 46.85 | 45.65
2019-12-17 11:30 | 47.22 | 45.95
2019-12-17 12:00 | 47.8 | 46.43
2019-12-17 12:30 | 48.26 | 46.93
2019-12-17 13:00 | 48.35 | 47.08
2019-12-17 13:30 | 48.87 | 47.57
2019-12-17 14:00 | 49.31 | 48.01
2019-12-17 14:30 | 50.85 | 49.52
2019-12-17 15:00 | 51.49 | 50.13
2019-12-17 15:30 | 52.03 | 50.79
2019-12-17 16:00 | 60.21 | 58.81
2019-12-17 16:30 | 61.54 | 60.16
2019-12-17 17:00 | 61.82 | 60.65
2019-12-17 17:30 | 60.1 | 59.12
2019-12-17 18:00 | 58.5 | 57.47
2019-12-17 18:30 | 57.42 | 56.38
2019-12-17 19:00 | 56.72 | 55.65
2019-12-17 19:30 | 55.65 | 54.56
2019-12-17 20:00 | 54.2 | 53.07
2019-12-17 20:30 | 53.64 | 52.48
2019-12-17 21:00 | 52.73 | 51.55
2019-12-17 21:30 | 52.55 | 51.37
2019-12-17 22:00 | 49.31 | 48.03
2019-12-17 22:30 | 45.42 | 44
2019-12-17 23:00 | 43.17 | 41.65
2019-12-17 23:30 | 41.24 | 39.62
2019-12-18 | 39.38 | 37.68
2019-12-18 00:30 | 39.27 | 37.54
2019-12-18 01:00 | 36.92 | 36.4
2019-12-18 01:30 | 36.12 | 35.72
2019-12-18 02:00 | 35.51 | 35.11
2019-12-18 02:30 | 34.64 | 34.25
2019-12-18 03:00 | 34.31 | 33.91
2019-12-18 03:30 | 34.26 | 33.87
2019-12-18 04:00 | 34.11 | 33.71
2019-12-18 04:30 | 34.3 | 33.9
2019-12-18 05:00 | 34.79 | 34.4
2019-12-18 05:30 | 35.44 | 35.06
2019-12-18 06:00 | 36.57 | 36.2
2019-12-18 06:30 | 39.38 | 38.98
2019-12-18 07:00 | 42.52 | 41.92
2019-12-18 07:30 | 45.69 | 45.1
2019-12-18 08:00 | 46.89 | 46.27
2019-12-18 08:30 | 47.91 | 47.15
2019-12-18 09:00 | 43.56 | 42.81
2019-12-18 09:30 | 43.47 | 42.74
2019-12-18 10:00 | 41.52 | 40.68
2019-12-18 10:30 | 40.53 | 39.7
2019-12-18 11:00 | 42.06 | 41.17
2019-12-18 11:30 | 44.54 | 43.62
2019-12-18 12:00 | 44.6 | 43.74
2019-12-18 12:30 | 43.67 | 42.93
2019-12-18 13:00 | 41.91 | 41.05
2019-12-18 13:30 | 41.51 | 40.6
2019-12-18 14:00 | 43.95 | 42.9
2019-12-18 14:30 | 48.86 | 47.53
2019-12-18 15:00 | 49.79 | 48.5
2019-12-18 15:30 | 51.35 | 50.07
2019-12-18 16:00 | 51.52 | 50.42
2019-12-18 16:30 | 52.82 | 51.83
2019-12-18 17:00 | 54.12 | 53.24
2019-12-18 17:30 | 52.26 | 51.75
2019-12-18 18:00 | 50.56 | 50.27
2019-12-18 18:30 | 49.49 | 49.23
2019-12-18 19:00 | 49.73 | 49.46
2019-12-18 19:30 | 49.5 | 49.23
2019-12-18 20:00 | 48.02 | 47.74
2019-12-18 20:30 | 45.95 | 45.66
2019-12-18 21:00 | 44.53 | 44.22
2019-12-18 21:30 | 42.61 | 42.29
2019-12-18 22:00 | 40.56 | 40.23
2019-12-18 22:30 | 37.89 | 37.53
2019-12-18 23:00 | 36.08 | 35.69
2019-12-18 23:30 | 34.87 | 34.47
2019-12-19 | 33.67 | 33.25
2019-12-19 00:30 | 32.59 | 32.16
2019-12-19 01:00 | 31.2 | 31.13
2019-12-19 01:30 | 30.92 | 30.87
2019-12-19 02:00 | 30.74 | 30.69
2019-12-19 02:30 | 30.45 | 30.39
2019-12-19 03:00 | 29.89 | 29.85
2019-12-19 03:30 | 29.69 | 29.66
2019-12-19 04:00 | 29.75 | 29.72
2019-12-19 04:30 | 30.01 | 29.96
2019-12-19 05:00 | 30.54 | 30.48
2019-12-19 05:30 | 31.05 | 31
2019-12-19 06:00 | 32.54 | 32.44
2019-12-19 06:30 | 35.94 | 35.69
2019-12-19 07:00 | 38.51 | 38.08
2019-12-19 07:30 | 42.98 | 42.26
2019-12-19 08:00 | 44.99 | 44.45
2019-12-19 08:30 | 46.9 | 46.31
2019-12-19 09:00 | 45.65 | 44.81
2019-12-19 09:30 | 44.33 | 43.3
2019-12-19 10:00 | 43.76 | 42.86
2019-12-19 10:30 | 44.63 | 44.09
2019-12-19 11:00 | 47.92 | 47.5
2019-12-19 11:30 | 46.47 | 46.05
2019-12-19 12:00 | 46.65 | 46.27
2019-12-19 12:30 | 47 | 46.57
2019-12-19 13:00 | 48.44 | 48.02
2019-12-19 13:30 | 46.8 | 46.58
2019-12-19 14:00 | 49.66 | 49.36
2019-12-19 14:30 | 49.06 | 48.67
2019-12-19 15:00 | 48.84 | 48.4
2019-12-19 15:30 | 50.16 | 49.72
2019-12-19 16:00 | 51.34 | 50.84
2019-12-19 16:30 | 53.71 | 53.22
2019-12-19 17:00 | 55.09 | 54.49
2019-12-19 17:30 | 55.29 | 54.45
2019-12-19 18:00 | 55.36 | 54.27
2019-12-19 18:30 | 55.28 | 53.9
2019-12-19 19:00 | 55.48 | 54.12
2019-12-19 19:30 | 55.52 | 54.14
2019-12-19 20:00 | 54.74 | 53.26
2019-12-19 20:30 | 53.03 | 51.28
2019-12-19 21:00 | 51.47 | 49.43
2019-12-19 21:30 | 48.08 | 46.85
2019-12-19 22:00 | 44.56 | 44.13
2019-12-19 22:30 | 42.16 | 41.71
2019-12-19 23:00 | 39.58 | 39.09
2019-12-19 23:30 | 37.28 | 36.76
2019-12-20 | 35.82 | 35.28
2019-12-20 00:30 | 33.85 | 33.27
2019-12-20 01:00 | 32.81 | 32.2
2019-12-20 01:30 | 32.44 | 31.82
2019-12-20 02:00 | 31.76 | 31.13
2019-12-20 02:30 | 31.35 | 30.7
2019-12-20 03:00 | 31.03 | 30.37
2019-12-20 03:30 | 31.03 | 30.38
2019-12-20 04:00 | 31.04 | 30.38
2019-12-20 04:30 | 31.29 | 30.65
2019-12-20 05:00 | 31.71 | 31.07
2019-12-20 05:30 | 32.64 | 32.02
2019-12-20 06:00 | 33.88 | 33.28
2019-12-20 06:30 | 36.5 | 35.95
2019-12-20 07:00 | 38.63 | 38.12
2019-12-20 07:30 | 41.92 | 41.35
2019-12-20 08:00 | 43.95 | 43.51
2019-12-20 08:30 | 46.32 | 45.64
2019-12-20 09:00 | 47.88 | 47.01
2019-12-20 09:30 | 47.69 | 46.68
2019-12-20 10:00 | 47.06 | 45.88
2019-12-20 10:30 | 46.87 | 45.61
2019-12-20 11:00 | 46.81 | 45.5
2019-12-20 11:30 | 47.23 | 45.9
2019-12-20 12:00 | 47.53 | 46.19
2019-12-20 12:30 | 47.64 | 46.32
2019-12-20 13:00 | 47.23 | 45.97
2019-12-20 13:30 | 47.06 | 45.9
2019-12-20 14:00 | 47.79 | 46.65
2019-12-20 14:30 | 48.84 | 47.74
2019-12-20 15:00 | 49.44 | 48.43
2019-12-20 15:30 | 50 | 49.11
2019-12-20 16:00 | 51.46 | 50.65
2019-12-20 16:30 | 52.66 | 51.97
2019-12-20 17:00 | 53.88 | 53.26
2019-12-20 17:30 | 53.62 | 53.19
2019-12-20 18:00 | 53.12 | 52.82
2019-12-20 18:30 | 52.68 | 52.44
2019-12-20 19:00 | 52.33 | 52.09
2019-12-20 19:30 | 52.1 | 51.86
2019-12-20 20:00 | 50.68 | 50.43
2019-12-20 20:30 | 48.93 | 48.67
2019-12-20 21:00 | 47.33 | 47.06
2019-12-20 21:30 | 45.94 | 45.65
2019-12-20 22:00 | 44.39 | 44.09
2019-12-20 22:30 | 42.81 | 42.5
2019-12-20 23:00 | 41.27 | 40.94
2019-12-20 23:30 | 39.32 | 38.97
2019-12-21 | 37.38 | 37
2019-12-21 00:30 | 35.49 | 35.09
2019-12-21 01:00 | 34.34 | 33.93
2019-12-21 01:30 | 33.53 | 33.13
2019-12-21 02:00 | 32.82 | 32.41
2019-12-21 02:30 | 32.36 | 31.95
2019-12-21 03:00 | 32.25 | 31.83
2019-12-21 03:30 | 31.99 | 31.57
2019-12-21 04:00 | 31.96 | 31.54
2019-12-21 04:30 | 32.05 | 31.63
2019-12-21 05:00 | 32.11 | 31.69
2019-12-21 05:30 | 32.18 | 31.76
2019-12-21 06:00 | 32.46 | 32.05
2019-12-21 06:30 | 33.65 | 33.25
2019-12-21 07:00 | 34.38 | 33.99
2019-12-21 07:30 | 36.29 | 35.93
2019-12-21 08:00 | 37.41 | 37
2019-12-21 08:30 | 38.43 | 38.08
2019-12-21 09:00 | 39.06 | 38.72
2019-12-21 09:30 | 38.66 | 38.32
2019-12-21 10:00 | 38.82 | 38.49
2019-12-21 10:30 | 38.61 | 38.27
2019-12-21 11:00 | 39.1 | 38.72
2019-12-21 11:30 | 38.89 | 38.48
2019-12-21 12:00 | 38.84 | 38.43
2019-12-21 12:30 | 38.62 | 38.25
2019-12-21 13:00 | 38.55 | 38.21
2019-12-21 13:30 | 38.97 | 38.63
2019-12-21 14:00 | 39.72 | 39.39
2019-12-21 14:30 | 40.16 | 39.84
2019-12-21 15:00 | 40.91 | 40.59
2019-12-21 15:30 | 41.72 | 41.41
2019-12-21 16:00 | 43.34 | 43.04
2019-12-21 16:30 | 44.83 | 44.54
2019-12-21 17:00 | 47.37 | 47.09
2019-12-21 17:30 | 48.27 | 48
2019-12-21 18:00 | 49.14 | 48.87
2019-12-21 18:30 | 49.06 | 48.78
2019-12-21 19:00 | 48.79 | 48.51
2019-12-21 19:30 | 49.02 | 48.74
2019-12-21 20:00 | 48.14 | 47.86
2019-12-21 20:30 | 47.15 | 46.86
2019-12-21 21:00 | 45.9 | 45.61
2019-12-21 21:30 | 44.56 | 44.25
2019-12-21 22:00 | 43.41 | 43.09
2019-12-21 22:30 | 41.72 | 41.38
2019-12-21 23:00 | 40.15 | 39.79
2019-12-21 23:30 | 38 | 37.62
2019-12-22 | 27.02 | 26.51
2019-12-22 00:30 | 19.36 | 19.18
2019-12-22 01:00 | 18.69 | 18.69
2019-12-22 01:30 | 30.9 | 30.42
2019-12-22 02:00 | 34.99 | 34.42
2019-12-22 02:30 | 30.85 | 30.2
2019-12-22 03:00 | 30.16 | 29.49
2019-12-22 03:30 | 29.73 | 29.06
2019-12-22 04:00 | 29.49 | 28.81
2019-12-22 04:30 | 29.5 | 28.82
2019-12-22 05:00 | 29.54 | 28.86
2019-12-22 05:30 | 29.2 | 28.52
2019-12-22 06:00 | 29.6 | 28.93
2019-12-22 06:30 | 30.15 | 29.49
2019-12-22 07:00 | 31.09 | 30.44
2019-12-22 07:30 | 32.61 | 31.99
2019-12-22 08:00 | 33.99 | 33.39
2019-12-22 08:30 | 35.77 | 35.2
2019-12-22 09:00 | 35.25 | 34.69
2019-12-22 09:30 | 34.95 | 34.37
2019-12-22 10:00 | 37.96 | 37.43
2019-12-22 10:30 | 35.93 | 35.37
2019-12-22 11:00 | 34.98 | 34.4
2019-12-22 11:30 | 34.82 | 34.24
2019-12-22 12:00 | 35.05 | 34.48
2019-12-22 12:30 | 35.4 | 34.83
2019-12-22 13:00 | 35.44 | 34.87
2019-12-22 13:30 | 36.16 | 35.61
2019-12-22 14:00 | 37.55 | 37.02
2019-12-22 14:30 | 38.44 | 37.92
2019-12-22 15:00 | 39.65 | 39.15
2019-12-22 15:30 | 40.77 | 40.28
2019-12-22 16:00 | 42.17 | 41.7
2019-12-22 16:30 | 43.76 | 43.32
2019-12-22 17:00 | 45.57 | 45.14
2019-12-22 17:30 | 47.41 | 47
2019-12-22 18:00 | 48.21 | 48.08
2019-12-22 18:30 | 48.35 | 48.3
2019-12-22 19:00 | 48.44 | 48.4
2019-12-22 19:30 | 49.05 | 48.98
2019-12-22 20:00 | 48.06 | 48
2019-12-22 20:30 | 46.84 | 46.8
2019-12-22 21:00 | 45.6 | 45.56
2019-12-22 21:30 | 43.58 | 43.57
2019-12-22 22:00 | 42.08 | 42.07
2019-12-22 22:30 | 40 | 39.99
2019-12-22 23:00 | 37.8 | 37.79
2019-12-22 23:30 | 35.9 | 35.88
2019-12-23 | 34.2 | 34.16
2019-12-23 00:30 | 33 | 32.92
2019-12-23 01:00 | 32.33 | 32.26
2019-12-23 01:30 | 31.43 | 31.37
2019-12-23 02:00 | 31.06 | 31
2019-12-23 02:30 | 30.8 | 30.74
2019-12-23 03:00 | 30.05 | 30.01
2019-12-23 03:30 | 29.8 | 29.76
2019-12-23 04:00 | 29.52 | 29.49
2019-12-23 04:30 | 29.48 | 29.46
2019-12-23 05:00 | 29.83 | 29.8
2019-12-23 05:30 | 29.85 | 29.83
2019-12-23 06:00 | 30.8 | 30.77
2019-12-23 06:30 | 33.37 | 33.25
2019-12-23 07:00 | 35.08 | 34.84
2019-12-23 07:30 | 38.48 | 37.95
2019-12-23 08:00 | 40.81 | 40.46
2019-12-23 08:30 | 42.79 | 42.34
2019-12-23 09:00 | 42.92 | 42.36
2019-12-23 09:30 | 42.96 | 42.29
2019-12-23 10:00 | 42.62 | 41.9
2019-12-23 10:30 | 43.59 | 42.78
2019-12-23 11:00 | 44.98 | 44.12
2019-12-23 11:30 | 44.76 | 43.81
2019-12-23 12:00 | 44.88 | 43.89
2019-12-23 12:30 | 45.38 | 44.38
2019-12-23 13:00 | 45.93 | 44.91
2019-12-23 13:30 | 46.78 | 45.81
2019-12-23 14:00 | 49.53 | 48.48
2019-12-23 14:30 | 48.96 | 47.77
2019-12-23 15:00 | 49.27 | 48.08
2019-12-23 15:30 | 49.93 | 48.76
2019-12-23 16:00 | 51.03 | 49.88
2019-12-23 16:30 | 52.55 | 51.41
2019-12-23 17:00 | 53.39 | 52.26
2019-12-23 17:30 | 53.22 | 52.08
2019-12-23 18:00 | 53.18 | 52.03
2019-12-23 18:30 | 53.12 | 51.97
2019-12-23 19:00 | 52.94 | 51.78
2019-12-23 19:30 | 52.82 | 51.65
2019-12-23 20:00 | 51.33 | 50.13
2019-12-23 20:30 | 49.78 | 48.53
2019-12-23 21:00 | 48.37 | 47.07
2019-12-23 21:30 | 46.89 | 45.54
2019-12-23 22:00 | 44.68 | 43.25
2019-12-23 22:30 | 42.2 | 40.65
2019-12-23 23:00 | 40.29 | 38.66
2019-12-23 23:30 | 38.64 | 36.92
2019-12-24 | 36.86 | 35.06
2019-12-24 00:30 | 35.55 | 33.71
2019-12-24 01:00 | 34.43 | 32.56
2019-12-24 01:30 | 33.64 | 31.72
2019-12-24 02:00 | 33.05 | 31.09
2019-12-24 02:30 | 32.91 | 30.93
2019-12-24 03:00 | 32.21 | 30.18
2019-12-24 03:30 | 31.76 | 29.7
2019-12-24 04:00 | 31.82 | 29.76
2019-12-24 04:30 | 31.99 | 29.94
2019-12-24 05:00 | 32.01 | 29.96
2019-12-24 05:30 | 32.34 | 30.31
2019-12-24 06:00 | 33.31 | 31.35
2019-12-24 06:30 | 34.93 | 33.09
2019-12-24 07:00 | 35.84 | 34.06
2019-12-24 07:30 | 38.64 | 37.02
2019-12-24 08:00 | 40.47 | 38.91
2019-12-24 08:30 | 41.97 | 40.47
2019-12-24 09:00 | 43.48 | 42.05
2019-12-24 09:30 | 43.66 | 42.25
2019-12-24 10:00 | 43.25 | 41.83
2019-12-24 10:30 | 44.1 | 42.72
2019-12-24 11:00 | 44.24 | 42.85
2019-12-24 11:30 | 44.43 | 43.06
2019-12-24 12:00 | 44.43 | 43.05
2019-12-24 12:30 | 44.82 | 43.46
2019-12-24 13:00 | 45.32 | 43.97
2019-12-24 13:30 | 45.72 | 44.39
2019-12-24 14:00 | 46.46 | 45.15
2019-12-24 14:30 | 47.04 | 45.75
2019-12-24 15:00 | 48.23 | 46.97
2019-12-24 15:30 | 49.48 | 48.26
2019-12-24 16:00 | 50.82 | 49.63
2019-12-24 16:30 | 51.99 | 50.83
2019-12-24 17:00 | 53.09 | 51.96
2019-12-24 17:30 | 53.62 | 52.49
2019-12-24 18:00 | 52.53 | 51.36
2019-12-24 18:30 | 51.2 | 50
2019-12-24 19:00 | 50.1 | 48.86
2019-12-24 19:30 | 49.87 | 48.62
2019-12-24 20:00 | 49.12 | 47.84
2019-12-24 20:30 | 48.1 | 46.76
2019-12-24 21:00 | 45.98 | 45.29
2019-12-24 21:30 | 44.08 | 43.76
2019-12-24 22:00 | 42.71 | 42.38
2019-12-24 22:30 | 40.77 | 40.42
2019-12-24 23:00 | 38.82 | 38.45
2019-12-24 23:30 | 36.97 | 36.58
2019-12-25 | 35.4 | 34.99
2019-12-25 00:30 | 33.95 | 33.55
2019-12-25 01:00 | 32.87 | 32.44
2019-12-25 01:30 | 32.27 | 31.84
2019-12-25 02:00 | 31.59 | 31.15
2019-12-25 02:30 | 30.97 | 30.51
2019-12-25 03:00 | 30.41 | 29.95
2019-12-25 03:30 | 30.54 | 30.08
2019-12-25 04:00 | 30.41 | 29.95
2019-12-25 04:30 | 30.46 | 29.99
2019-12-25 05:00 | 30.67 | 30.21
2019-12-25 05:30 | 30.67 | 30.21
2019-12-25 06:00 | 31.34 | 30.89
2019-12-25 06:30 | 33.5 | 33.09
2019-12-25 07:00 | 34.76 | 34.36
2019-12-25 07:30 | 35.83 | 35.46
2019-12-25 08:00 | 37.76 | 37.43
2019-12-25 08:30 | 37.62 | 37.27
2019-12-25 09:00 | 35.16 | 34.73
2019-12-25 09:30 | 34.43 | 33.93
2019-12-25 10:00 | 34.8 | 34.26
2019-12-25 10:30 | 35.08 | 34.5
2019-12-25 11:00 | 35.32 | 34.71
2019-12-25 11:30 | 35.35 | 34.97
2019-12-25 12:00 | 35.11 | 34.75
2019-12-25 12:30 | 34.85 | 34.48
2019-12-25 13:00 | 34.98 | 34.61
2019-12-25 13:30 | 35.03 | 34.65
2019-12-25 14:00 | 35.62 | 35.25
2019-12-25 14:30 | 36.21 | 35.85
2019-12-25 15:00 | 37.31 | 36.95
2019-12-25 15:30 | 38.65 | 38.31
2019-12-25 16:00 | 40.67 | 40.35
2019-12-25 16:30 | 42.3 | 41.99
2019-12-25 17:00 | 43.64 | 43.34
2019-12-25 17:30 | 44.14 | 43.83
2019-12-25 18:00 | 44.66 | 44.36
2019-12-25 18:30 | 43.71 | 43.39
2019-12-25 19:00 | 40.39 | 40.23
2019-12-25 19:30 | 40.6 | 40.6
2019-12-25 20:00 | 40.82 | 40.82
2019-12-25 20:30 | 40.86 | 40.85
2019-12-25 21:00 | 44.71 | 44.71
2019-12-25 21:30 | 43.25 | 43.24
2019-12-25 22:00 | 42.41 | 42.38
2019-12-25 22:30 | 39.96 | 39.9
2019-12-25 23:00 | 37.96 | 37.92
2019-12-25 23:30 | 36.39 | 36.37
2019-12-26 | 33.75 | 33.74
2019-12-26 00:30 | 34.66 | 34.64
2019-12-26 01:00 | 34.06 | 34.05
2019-12-26 01:30 | 33.21 | 33.2
2019-12-26 02:00 | 32.54 | 32.52
2019-12-26 02:30 | 32.71 | 32.7
2019-12-26 03:00 | 32.61 | 32.6
2019-12-26 03:30 | 32.36 | 32.36
2019-12-26 04:00 | 31.92 | 31.91
2019-12-26 04:30 | 32.51 | 32.5
2019-12-26 05:00 | 32.97 | 32.95
2019-12-26 05:30 | 32 | 31.99
2019-12-26 06:00 | 31.38 | 31.38
2019-12-26 06:30 | 32.48 | 32.46
2019-12-26 07:00 | 33.14 | 33.09
2019-12-26 07:30 | 34.06 | 33.91
2019-12-26 08:00 | 35.8 | 35.52
2019-12-26 08:30 | 36.92 | 36.66
2019-12-26 09:00 | 40.88 | 40.78
2019-12-26 09:30 | 42.23 | 42.08
2019-12-26 10:00 | 40.7 | 40.49
2019-12-26 10:30 | 41.02 | 40.74
2019-12-26 11:00 | 40.57 | 40.23
2019-12-26 11:30 | 40.95 | 40.57
2019-12-26 12:00 | 41.28 | 40.87
2019-12-26 12:30 | 42.05 | 41.63
2019-12-26 13:00 | 42.5 | 42.06
2019-12-26 13:30 | 43.46 | 42.99
2019-12-26 14:00 | 44.31 | 43.84
2019-12-26 14:30 | 44.63 | 44.24
2019-12-26 15:00 | 45.12 | 44.77
2019-12-26 15:30 | 45.63 | 45.31
2019-12-26 16:00 | 46.64 | 46.36
2019-12-26 16:30 | 48.33 | 48.08
2019-12-26 17:00 | 49.72 | 49.52
2019-12-26 17:30 | 50.01 | 49.88
2019-12-26 18:00 | 50.36 | 50.28
2019-12-26 18:30 | 49.18 | 49.16
2019-12-26 19:00 | 49.17 | 49.16
2019-12-26 19:30 | 49.76 | 49.74
2019-12-26 20:00 | 49.08 | 49.07
2019-12-26 20:30 | 48.2 | 48.19
2019-12-26 21:00 | 46.66 | 46.65
2019-12-26 21:30 | 44.68 | 44.68
2019-12-26 22:00 | 42.63 | 42.62
2019-12-26 22:30 | 40.52 | 40.49
2019-12-26 23:00 | 38.83 | 38.78
2019-12-26 23:30 | 36.77 | 36.67
2019-12-27 | 34.78 | 34.72
2019-12-27 00:30 | 34.07 | 34.06
2019-12-27 01:00 | 33.28 | 33.27
2019-12-27 01:30 | 32.85 | 32.84
2019-12-27 02:00 | 32.21 | 32.2
2019-12-27 02:30 | 31.54 | 31.53
2019-12-27 03:00 | 31.4 | 31.39
2019-12-27 03:30 | 31.03 | 31.02
2019-12-27 04:00 | 30.91 | 30.91
2019-12-27 04:30 | 31.1 | 31.09
2019-12-27 05:00 | 31.59 | 31.58
2019-12-27 05:30 | 32.6 | 32.59
2019-12-27 06:00 | 32.88 | 32.87
2019-12-27 06:30 | 34.46 | 34.38
2019-12-27 07:00 | 37.3 | 37.13
2019-12-27 07:30 | 39.74 | 39.32
2019-12-27 08:00 | 41.77 | 41.23
2019-12-27 08:30 | 42.61 | 42.44
2019-12-27 09:00 | 46.07 | 45.9
2019-12-27 09:30 | 44.11 | 43.89
2019-12-27 10:00 | 44.04 | 43.81
2019-12-27 10:30 | 43.22 | 42.89
2019-12-27 11:00 | 43.57 | 43.2
2019-12-27 11:30 | 41.52 | 41.19
2019-12-27 12:00 | 41.64 | 41.3
2019-12-27 12:30 | 40.16 | 39.75
2019-12-27 13:00 | 39.53 | 39.09
2019-12-27 13:30 | 42.06 | 41.65
2019-12-27 14:00 | 39.97 | 39.47
2019-12-27 14:30 | 41.71 | 41.23
2019-12-27 15:00 | 43.03 | 42.59
2019-12-27 15:30 | 44.28 | 43.92
2019-12-27 16:00 | 44.89 | 44.63
2019-12-27 16:30 | 46.57 | 46.35
2019-12-27 17:00 | 45.89 | 45.74
2019-12-27 17:30 | 45.74 | 45.66
2019-12-27 18:00 | 44.21 | 44.19
2019-12-27 18:30 | 43.72 | 43.72
2019-12-27 19:00 | 44.73 | 44.73
2019-12-27 19:30 | 45.62 | 45.61
2019-12-27 20:00 | 44.43 | 44.43
2019-12-27 20:30 | 42.98 | 42.97
2019-12-27 21:00 | 41.99 | 41.98
2019-12-27 21:30 | 40.62 | 40.6
2019-12-27 22:00 | 38.97 | 38.92
2019-12-27 22:30 | 36.17 | 36.02
2019-12-27 23:00 | 37.37 | 37.27
2019-12-27 23:30 | 35.68 | 35.56
2019-12-28 | 34.85 | 34.84
2019-12-28 00:30 | 33.76 | 33.75
2019-12-28 01:00 | 32.89 | 32.88
2019-12-28 01:30 | 32.27 | 32.26
2019-12-28 02:00 | 31.79 | 31.78
2019-12-28 02:30 | 31.04 | 31.04
2019-12-28 03:00 | 30.89 | 30.89
2019-12-28 03:30 | 30.85 | 30.84
2019-12-28 04:00 | 30.53 | 30.52
2019-12-28 04:30 | 30.43 | 30.43
2019-12-28 05:00 | 30.69 | 30.68
2019-12-28 05:30 | 31.23 | 31.23
2019-12-28 06:00 | 31.83 | 31.83
2019-12-28 06:30 | 33.57 | 33.56
2019-12-28 07:00 | 34.67 | 34.65
2019-12-28 07:30 | 37.01 | 36.95
2019-12-28 08:00 | 39.41 | 39.31
2019-12-28 08:30 | 41.61 | 41.44
2019-12-28 09:00 | 42.83 | 42.64
2019-12-28 09:30 | 42.46 | 42.24
2019-12-28 10:00 | 43.41 | 43.17
2019-12-28 10:30 | 42.59 | 42.3
2019-12-28 11:00 | 42.14 | 41.8
2019-12-28 11:30 | 41 | 40.68
2019-12-28 12:00 | 40.26 | 40.19
2019-12-28 12:30 | 39.4 | 39.33
2019-12-28 13:00 | 42.9 | 42.85
2019-12-28 13:30 | 42.7 | 42.67
2019-12-28 14:00 | 43.81 | 43.78
2019-12-28 14:30 | 43.74 | 43.73
2019-12-28 15:00 | 42.82 | 42.82
2019-12-28 15:30 | 42.23 | 42.22
2019-12-28 16:00 | 40.94 | 40.94
2019-12-28 16:30 | 41.81 | 41.81
2019-12-28 17:00 | 42.44 | 42.43
2019-12-28 17:30 | 43.06 | 43.05
2019-12-28 18:00 | 43.84 | 43.81
2019-12-28 18:30 | 44.13 | 44.1
2019-12-28 19:00 | 44.35 | 44.34
2019-12-28 19:30 | 43.76 | 43.75
2019-12-28 20:00 | 42.72 | 42.7
2019-12-28 20:30 | 41.43 | 41.4
2019-12-28 21:00 | 40.28 | 40.24
2019-12-28 21:30 | 39.44 | 39.39
2019-12-28 22:00 | 38.57 | 38.49
2019-12-28 22:30 | 37.46 | 37.36
2019-12-28 23:00 | 35.67 | 35.59
2019-12-28 23:30 | 34 | 33.99
2019-12-29 | 33.35 | 33.35
2019-12-29 00:30 | 32.56 | 32.55
2019-12-29 01:00 | 31.52 | 31.51
2019-12-29 01:30 | 31.2 | 31.19
2019-12-29 02:00 | 30.51 | 30.51
2019-12-29 02:30 | 30.13 | 30.13
2019-12-29 03:00 | 29.65 | 29.65
2019-12-29 03:30 | 29.65 | 29.64
2019-12-29 04:00 | 29.71 | 29.7
2019-12-29 04:30 | 29.66 | 29.66
2019-12-29 05:00 | 29.77 | 29.76
2019-12-29 05:30 | 29.98 | 29.98
2019-12-29 06:00 | 30.21 | 30.2
2019-12-29 06:30 | 32.18 | 32.18
2019-12-29 07:00 | 32.51 | 32.5
2019-12-29 07:30 | 34.47 | 34.44
2019-12-29 08:00 | 36.43 | 36.36
2019-12-29 08:30 | 36.72 | 36.62
2019-12-29 09:00 | 37.19 | 37.05
2019-12-29 09:30 | 40.45 | 40.29
2019-12-29 10:00 | 40.51 | 40.29
2019-12-29 10:30 | 40.25 | 39.97
2019-12-29 11:00 | 39.27 | 38.96
2019-12-29 11:30 | 34.43 | 34.09
2019-12-29 12:00 | 31.97 | 31.94
2019-12-29 12:30 | 32.31 | 32.25
2019-12-29 13:00 | 32.24 | 32.19
2019-12-29 13:30 | 32.17 | 32.08
2019-12-29 14:00 | 31.74 | 31.66
2019-12-29 14:30 | 32.57 | 32.51
2019-12-29 15:00 | 36.88 | 36.84
2019-12-29 15:30 | 35.45 | 35.42
2019-12-29 16:00 | 35.61 | 35.6
2019-12-29 16:30 | 37.56 | 37.55
2019-12-29 17:00 | 39.56 | 39.56
2019-12-29 17:30 | 41.51 | 41.51
2019-12-29 18:00 | 43.9 | 43.9
2019-12-29 18:30 | 44.68 | 44.68
2019-12-29 19:00 | 45.33 | 45.32
2019-12-29 19:30 | 46.71 | 46.71
2019-12-29 20:00 | 45.78 | 45.78
2019-12-29 20:30 | 44.9 | 44.89
2019-12-29 21:00 | 43.74 | 43.74
2019-12-29 21:30 | 42.44 | 42.42
2019-12-29 22:00 | 41.16 | 41.13
2019-12-29 22:30 | 39.28 | 39.23
2019-12-29 23:00 | 36.8 | 36.75
2019-12-29 23:30 | 35.22 | 35.2
2019-12-30 | 34.41 | 34.39
2019-12-30 00:30 | 32.93 | 32.93
2019-12-30 01:00 | 32.31 | 32.31
2019-12-30 01:30 | 31.66 | 31.66
2019-12-30 02:00 | 30.84 | 30.84
2019-12-30 02:30 | 30.85 | 30.85
2019-12-30 03:00 | 30.58 | 30.57
2019-12-30 03:30 | 30.86 | 30.85
2019-12-30 04:00 | 30.57 | 30.57
2019-12-30 04:30 | 30.97 | 30.97
2019-12-30 05:00 | 31.15 | 31.14
2019-12-30 05:30 | 31.95 | 31.95
2019-12-30 06:00 | 33.4 | 33.39
2019-12-30 06:30 | 35.81 | 35.72
2019-12-30 07:00 | 38.87 | 38.63
2019-12-30 07:30 | 42.6 | 42.06
2019-12-30 08:00 | 45.74 | 44.99
2019-12-30 08:30 | 47.66 | 47.33
2019-12-30 09:00 | 48.58 | 48.14
2019-12-30 09:30 | 47.88 | 47.4
2019-12-30 10:00 | 46.6 | 45.98
2019-12-30 10:30 | 46.66 | 45.77
2019-12-30 11:00 | 47.89 | 46.99
2019-12-30 11:30 | 49.49 | 48.61
2019-12-30 12:00 | 48.4 | 47.45
2019-12-30 12:30 | 47.73 | 46.85
2019-12-30 13:00 | 49.93 | 49.12
2019-12-30 13:30 | 49.3 | 48.54
2019-12-30 14:00 | 48.44 | 47.68
2019-12-30 14:30 | 49.63 | 48.97
2019-12-30 15:00 | 49.53 | 48.93
2019-12-30 15:30 | 47.4 | 46.82
2019-12-30 16:00 | 47.37 | 46.75
2019-12-30 16:30 | 47.75 | 47.24
2019-12-30 17:00 | 49.55 | 49.18
2019-12-30 17:30 | 49.12 | 48.92
2019-12-30 18:00 | 48.63 | 48.56
2019-12-30 18:30 | 48.28 | 48.27
2019-12-30 19:00 | 48.99 | 48.98
2019-12-30 19:30 | 49.71 | 49.68
2019-12-30 20:00 | 49.35 | 49.33
2019-12-30 20:30 | 47.91 | 47.89
2019-12-30 21:00 | 46.84 | 46.84
2019-12-30 21:30 | 44.92 | 44.92
2019-12-30 22:00 | 42.62 | 42.62
2019-12-30 22:30 | 40.82 | 40.8
2019-12-30 23:00 | 38.73 | 38.69
2019-12-30 23:30 | 36.78 | 36.73
2019-12-31 | 35.26 | 35.22
2019-12-31 00:30 | 33.82 | 33.8
2019-12-31 01:00 | 32.83 | 32.82
2019-12-31 01:30 | 31.93 | 31.92
2019-12-31 02:00 | 31.1 | 31.09
2019-12-31 02:30 | 30.9 | 30.89
2019-12-31 03:00 | 30.28 | 30.28
2019-12-31 03:30 | 30.71 | 30.7
2019-12-31 04:00 | 30.07 | 30.07
2019-12-31 04:30 | 30.19 | 30.19
2019-12-31 05:00 | 30.89 | 30.88
2019-12-31 05:30 | 31.28 | 31.27
2019-12-31 06:00 | 31.04 | 31.04
2019-12-31 06:30 | 34.43 | 34.33
2019-12-31 07:00 | 37.36 | 37.03
2019-12-31 07:30 | 40.83 | 40.11
2019-12-31 08:00 | 42.69 | 41.81
2019-12-31 08:30 | 43.39 | 42.88
2019-12-31 09:00 | 44.92 | 44.21
2019-12-31 09:30 | 46.33 | 45.43
2019-12-31 10:00 | 47.82 | 46.74
2019-12-31 10:30 | 47.66 | 46.44
2019-12-31 11:00 | 47.47 | 46.07
2019-12-31 11:30 | 46.78 | 45.42
2019-12-31 12:00 | 46.49 | 45.14
2019-12-31 12:30 | 47.71 | 46.27
2019-12-31 13:00 | 47.45 | 46.06
2019-12-31 13:30 | 47.78 | 46.37
2019-12-31 14:00 | 48.13 | 46.77
2019-12-31 14:30 | 48.34 | 47.11
2019-12-31 15:00 | 48.78 | 47.56
2019-12-31 15:30 | 50.03 | 48.85
2019-12-31 16:00 | 51.29 | 50.14
2019-12-31 16:30 | 52.13 | 50.98
2019-12-31 17:00 | 53.9 | 52.79
2019-12-31 17:30 | 54.69 | 53.6
2019-12-31 18:00 | 53.72 | 52.59
2019-12-31 18:30 | 52.35 | 51.17
2019-12-31 19:00 | 51.62 | 50.41
2019-12-31 19:30 | 51.32 | 50.11
2019-12-31 20:00 | 49.9 | 48.64
2019-12-31 20:30 | 48.28 | 46.97
2019-12-31 21:00 | 46.68 | 45.31
2019-12-31 21:30 | 45.05 | 43.62
2019-12-31 22:00 | 44.12 | 42.65
2019-12-31 22:30 | 42.94 | 41.41
2019-12-31 23:00 | 41.58 | 39.99
2019-12-31 23:30 | 40.07 | 38.41
2020-01-01 | 38.76 | 37.04
2020-01-01 00:30 | 37.79 | 36.01
2020-01-01 01:00 | 37.3 | 35.53
2020-01-01 01:30 | 36.21 | 34.4
2020-01-01 02:00 | 35.43 | 33.58
2020-01-01 02:30 | 34.97 | 33.08
2020-01-01 03:00 | 34.3 | 32.36
2020-01-01 03:30 | 34.17 | 32.23
2020-01-01 04:00 | 33.81 | 31.84
2020-01-01 04:30 | 33.72 | 31.74
2020-01-01 05:00 | 33.55 | 31.56
2020-01-01 05:30 | 33.07 | 31.04
2020-01-01 06:00 | 32.71 | 30.65
2020-01-01 06:30 | 33.57 | 31.59
2020-01-01 07:00 | 33.87 | 31.93
2020-01-01 07:30 | 35.2 | 33.37
2020-01-01 08:00 | 36.15 | 34.4
2020-01-01 08:30 | 37.03 | 35.28
2020-01-01 09:00 | 37.5 | 35.79
2020-01-01 09:30 | 38.35 | 36.7
2020-01-01 10:00 | 39.17 | 37.56
2020-01-01 10:30 | 39.27 | 37.66
2020-01-01 11:00 | 39.61 | 38.02
2020-01-01 11:30 | 39.83 | 38.25
2020-01-01 12:00 | 39.52 | 37.94
2020-01-01 12:30 | 40.04 | 38.48
2020-01-01 13:00 | 40.65 | 39.11
2020-01-01 13:30 | 41.52 | 40.02
2020-01-01 14:00 | 42.18 | 40.71
2020-01-01 14:30 | 43.53 | 42.11
2020-01-01 15:00 | 44.77 | 43.39
2020-01-01 15:30 | 46.09 | 44.76
2020-01-01 16:00 | 48.1 | 46.83
2020-01-01 16:30 | 50.12 | 48.91
2020-01-01 17:00 | 52.07 | 50.91
2020-01-01 17:30 | 53.34 | 52.2
2020-01-01 18:00 | 53.86 | 52.73
2020-01-01 18:30 | 53.78 | 52.64
2020-01-01 19:00 | 53.36 | 52.19
2020-01-01 19:30 | 53.67 | 52.52
2020-01-01 20:00 | 53.17 | 52.01
2020-01-01 20:30 | 51.67 | 50.47
2020-01-01 21:00 | 49.94 | 48.68
2020-01-01 21:30 | 48.41 | 47.1
2020-01-01 22:00 | 46.47 | 45.09
2020-01-01 22:30 | 44 | 42.52
2020-01-01 23:00 | 42.03 | 40.46
2020-01-01 23:30 | 40.47 | 38.82
2020-01-02 | 38.99 | 37.27
2020-01-02 00:30 | 37.72 | 35.97
2020-01-02 01:00 | 36.73 | 34.95
2020-01-02 01:30 | 35.89 | 34.06
2020-01-02 02:00 | 35.21 | 33.33
2020-01-02 02:30 | 35.06 | 33.17
2020-01-02 03:00 | 34.8 | 32.89
2020-01-02 03:30 | 34.61 | 32.68
2020-01-02 04:00 | 34.37 | 32.43
2020-01-02 04:30 | 34.77 | 32.85
2020-01-02 05:00 | 35.3 | 33.43
2020-01-02 05:30 | 35.74 | 33.9
2020-01-02 06:00 | 36.93 | 35.16
2020-01-02 06:30 | 40.42 | 38.85
2020-01-02 07:00 | 43.37 | 41.94
2020-01-02 07:30 | 47.97 | 46.72
2020-01-02 08:00 | 51.29 | 50.08
2020-01-02 08:30 | 53.45 | 52.33
2020-01-02 09:00 | 55.56 | 54.24
2020-01-02 09:30 | 55.78 | 54.32
2020-01-02 10:00 | 55.93 | 54.41
2020-01-02 10:30 | 56.36 | 55.33
2020-01-02 11:00 | 57.31 | 56.27
2020-01-02 11:30 | 56.9 | 55.83
2020-01-02 12:00 | 57.6 | 56.48
2020-01-02 12:30 | 58.84 | 57.73
2020-01-02 13:00 | 58.14 | 57.03
2020-01-02 13:30 | 58.76 | 57.65
2020-01-02 14:00 | 59.33 | 58.26
2020-01-02 14:30 | 61.91 | 60.91
2020-01-02 15:00 | 60.61 | 59.63
2020-01-02 15:30 | 61.28 | 60.34
2020-01-02 16:00 | 62.62 | 61.69
2020-01-02 16:30 | 63.32 | 62.39
2020-01-02 17:00 | 64.07 | 63.15
2020-01-02 17:30 | 63.54 | 62.6
2020-01-02 18:00 | 63.61 | 62.66
2020-01-02 18:30 | 63.33 | 62.38
2020-01-02 19:00 | 63.12 | 62.16
2020-01-02 19:30 | 63.53 | 62.57
2020-01-02 20:00 | 62.09 | 61.08
2020-01-02 20:30 | 59.84 | 58.78
2020-01-02 21:00 | 58.3 | 57.2
2020-01-02 21:30 | 55.11 | 53.93
2020-01-02 22:00 | 51.71 | 50.48
2020-01-02 22:30 | 48.88 | 47.57
2020-01-02 23:00 | 46.96 | 45.59
2020-01-02 23:30 | 44.84 | 43.39
2020-01-03 | 42.77 | 41.23
2020-01-03 00:30 | 41.46 | 39.87
2020-01-03 01:00 | 40.39 | 38.75
2020-01-03 01:30 | 39.47 | 37.84
2020-01-03 02:00 | 38.77 | 37.1
2020-01-03 02:30 | 38.64 | 36.97
2020-01-03 03:00 | 38.42 | 36.74
2020-01-03 03:30 | 38.49 | 36.82
2020-01-03 04:00 | 38.01 | 36.32
2020-01-03 04:30 | 38.22 | 36.54
2020-01-03 05:00 | 38.88 | 37.24
2020-01-03 05:30 | 39.41 | 37.79
2020-01-03 06:00 | 40.36 | 38.78
2020-01-03 06:30 | 43.54 | 42.11
2020-01-03 07:00 | 46.61 | 45.3
2020-01-03 07:30 | 51.87 | 50.6
2020-01-03 08:00 | 54.42 | 53.33
2020-01-03 08:30 | 57.66 | 56.48
2020-01-03 09:00 | 59.08 | 57.79
2020-01-03 09:30 | 56.21 | 54.72
2020-01-03 10:00 | 57.15 | 55.5
2020-01-03 10:30 | 58.49 | 56.66
2020-01-03 11:00 | 58.16 | 56.17
2020-01-03 11:30 | 59.06 | 57.08
2020-01-03 12:00 | 59.73 | 57.7
2020-01-03 12:30 | 59.43 | 57.36
2020-01-03 13:00 | 60.08 | 57.73
2020-01-03 13:30 | 60.87 | 58.55
2020-01-03 14:00 | 60.44 | 58.09
2020-01-03 14:30 | 60.69 | 58.35
2020-01-03 15:00 | 61.7 | 59.4
2020-01-03 15:30 | 62.87 | 60.61
2020-01-03 16:00 | 64.75 | 62.55
2020-01-03 16:30 | 64.07 | 61.83
2020-01-03 17:00 | 63.79 | 61.53
2020-01-03 17:30 | 62.52 | 60.17
2020-01-03 18:00 | 60.89 | 58.45
2020-01-03 18:30 | 59.41 | 56.89
2020-01-03 19:00 | 59.23 | 56.62
2020-01-03 19:30 | 59.14 | 56.54
2020-01-03 20:00 | 57.77 | 55.1
2020-01-03 20:30 | 56.23 | 53.49
2020-01-03 21:00 | 54.46 | 51.61
2020-01-03 21:30 | 52.56 | 49.58
2020-01-03 22:00 | 49.46 | 47.41
2020-01-03 22:30 | 46.59 | 45.19
2020-01-03 23:00 | 43.32 | 42.74
2020-01-03 23:30 | 41.27 | 40.93
2020-01-04 | 39.62 | 39.29
2020-01-04 00:30 | 37.96 | 37.9
2020-01-04 01:00 | 36.79 | 36.74
2020-01-04 01:30 | 36.01 | 35.96
2020-01-04 02:00 | 35.23 | 35.19
2020-01-04 02:30 | 35.03 | 35
2020-01-04 03:00 | 34.55 | 34.52
2020-01-04 03:30 | 34.31 | 34.29
2020-01-04 04:00 | 34.02 | 34
2020-01-04 04:30 | 34.37 | 34.34
2020-01-04 05:00 | 34.28 | 34.25
2020-01-04 05:30 | 34.11 | 34.09
2020-01-04 06:00 | 34 | 33.99
2020-01-04 06:30 | 35.33 | 35.27
2020-01-04 07:00 | 36.3 | 36.15
2020-01-04 07:30 | 38.41 | 38.09
2020-01-04 08:00 | 39.3 | 38.79
2020-01-04 08:30 | 41.38 | 40.69
2020-01-04 09:00 | 41.8 | 41.49
2020-01-04 09:30 | 43.24 | 42.86
2020-01-04 10:00 | 43.02 | 42.59
2020-01-04 10:30 | 42.67 | 42.17
2020-01-04 11:00 | 40.89 | 40.39
2020-01-04 11:30 | 40.97 | 40.51
2020-01-04 12:00 | 40.07 | 39.54
2020-01-04 12:30 | 39.83 | 39.33
2020-01-04 13:00 | 39 | 38.57
2020-01-04 13:30 | 37.68 | 37.27
2020-01-04 14:00 | 38.28 | 37.93
2020-01-04 14:30 | 37.88 | 37.58
2020-01-04 15:00 | 39.57 | 39.32
2020-01-04 15:30 | 42.26 | 42.05
2020-01-04 16:00 | 43.01 | 42.85
2020-01-04 16:30 | 43.36 | 43.25
2020-01-04 17:00 | 45.3 | 45.2
2020-01-04 17:30 | 48.9 | 48.84
2020-01-04 18:00 | 50.26 | 50.23
2020-01-04 18:30 | 49.73 | 49.72
2020-01-04 19:00 | 49.72 | 49.71
2020-01-04 19:30 | 50.21 | 50.19
2020-01-04 20:00 | 49.96 | 49.94
2020-01-04 20:30 | 48.67 | 48.66
2020-01-04 21:00 | 47.37 | 47.37
2020-01-04 21:30 | 45.73 | 45.72
2020-01-04 22:00 | 44.77 | 44.76
2020-01-04 22:30 | 43.13 | 43.13
2020-01-04 23:00 | 41.08 | 41.06
2020-01-04 23:30 | 39.46 | 39.42
2020-01-05 | 38.07 | 38.02
2020-01-05 00:30 | 36.91 | 36.85
2020-01-05 01:00 | 35.67 | 35.63
2020-01-05 01:30 | 34.91 | 34.88
2020-01-05 02:00 | 34.28 | 34.25
2020-01-05 02:30 | 34.12 | 34.1
2020-01-05 03:00 | 33.34 | 33.33
2020-01-05 03:30 | 33.34 | 33.33
2020-01-05 04:00 | 33.31 | 33.29
2020-01-05 04:30 | 33.24 | 33.23
2020-01-05 05:00 | 33.34 | 33.32
2020-01-05 05:30 | 33.19 | 33.18
2020-01-05 06:00 | 32.62 | 32.61
2020-01-05 06:30 | 33.84 | 33.82
2020-01-05 07:00 | 34.01 | 33.97
2020-01-05 07:30 | 34.43 | 34.34
2020-01-05 08:00 | 34.87 | 34.69
2020-01-05 08:30 | 36.96 | 36.61
2020-01-05 09:00 | 37.67 | 37.29
2020-01-05 09:30 | 39.02 | 38.95
2020-01-05 10:00 | 38.44 | 38.32
2020-01-05 10:30 | 37.84 | 37.65
2020-01-05 11:00 | 38.12 | 37.89
2020-01-05 11:30 | 38.17 | 37.91
2020-01-05 12:00 | 39.76 | 39.5
2020-01-05 12:30 | 40.65 | 40.42
2020-01-05 13:00 | 41.24 | 41.06
2020-01-05 13:30 | 41.73 | 41.54
2020-01-05 14:00 | 41.02 | 40.83
2020-01-05 14:30 | 40.19 | 40.02
2020-01-05 15:00 | 41.12 | 40.99
2020-01-05 15:30 | 42.62 | 42.5
2020-01-05 16:00 | 44.18 | 44.08
2020-01-05 16:30 | 45.86 | 45.77
2020-01-05 17:00 | 48.02 | 47.97
2020-01-05 17:30 | 48.74 | 48.72
2020-01-05 18:00 | 50.07 | 50.05
2020-01-05 18:30 | 50.71 | 50.7
2020-01-05 19:00 | 51.38 | 51.37
2020-01-05 19:30 | 52.64 | 52.6
2020-01-05 20:00 | 51.96 | 51.92
2020-01-05 20:30 | 50.82 | 50.78
2020-01-05 21:00 | 48.95 | 48.93
2020-01-05 21:30 | 47.13 | 47.13
2020-01-05 22:00 | 45.4 | 45.4
2020-01-05 22:30 | 43.54 | 43.54
2020-01-05 23:00 | 41.81 | 41.81
2020-01-05 23:30 | 40.08 | 40.07
2020-01-06 | 38.33 | 38.31
2020-01-06 00:30 | 37.04 | 36.97
2020-01-06 01:00 | 35.53 | 35.49
2020-01-06 01:30 | 35.4 | 35.34
2020-01-06 02:00 | 35.09 | 35.03
2020-01-06 02:30 | 34.55 | 34.51
2020-01-06 03:00 | 33.97 | 33.94
2020-01-06 03:30 | 34.14 | 34.1
2020-01-06 04:00 | 33.67 | 33.64
2020-01-06 04:30 | 34.21 | 34.19
2020-01-06 05:00 | 34.39 | 34.35
2020-01-06 05:30 | 36.26 | 36.19
2020-01-06 06:00 | 38.85 | 38.72
2020-01-06 06:30 | 44.63 | 44.16
2020-01-06 07:00 | 50.22 | 49.31
2020-01-06 07:30 | 57.59 | 56
2020-01-06 08:00 | 60.98 | 60.35
2020-01-06 08:30 | 64.47 | 63.6
2020-01-06 09:00 | 65.4 | 64.33
2020-01-06 09:30 | 64.49 | 63.39
2020-01-06 10:00 | 64.27 | 63.05
2020-01-06 10:30 | 60.91 | 59.54
2020-01-06 11:00 | 62.96 | 61.46
2020-01-06 11:30 | 61.58 | 59.97
2020-01-06 12:00 | 61.05 | 59.89
2020-01-06 12:30 | 64.26 | 63.26
2020-01-06 13:00 | 64.82 | 63.91
2020-01-06 13:30 | 65.38 | 64.42
2020-01-06 14:00 | 68.57 | 67.65
2020-01-06 14:30 | 66.27 | 65.46
2020-01-06 15:00 | 63.4 | 62.63
2020-01-06 15:30 | 66.12 | 65.38
2020-01-06 16:00 | 67.6 | 67.07
2020-01-06 16:30 | 66.25 | 65.94
2020-01-06 17:00 | 64.36 | 64.16
2020-01-06 17:30 | 61.22 | 60.68
2020-01-06 18:00 | 58.08 | 57.6
2020-01-06 18:30 | 56.71 | 56.42
2020-01-06 19:00 | 56.82 | 56.59
2020-01-06 19:30 | 57.08 | 56.84
2020-01-06 20:00 | 55.86 | 55.63
2020-01-06 20:30 | 54.16 | 53.92
2020-01-06 21:00 | 52.13 | 51.89
2020-01-06 21:30 | 50.19 | 49.93
2020-01-06 22:00 | 47.94 | 47.66
2020-01-06 22:30 | 45.69 | 45.39
2020-01-06 23:00 | 43.3 | 42.98
2020-01-06 23:30 | 41.83 | 41.5
2020-01-07 | 40.21 | 39.86
2020-01-07 00:30 | 38.68 | 38.34
2020-01-07 01:00 | 38.04 | 37.69
2020-01-07 01:30 | 37.3 | 36.94
2020-01-07 02:00 | 36.89 | 36.53
2020-01-07 02:30 | 36.49 | 36.13
2020-01-07 03:00 | 35.81 | 35.43
2020-01-07 03:30 | 35.32 | 34.94
2020-01-07 04:00 | 35.17 | 34.79
2020-01-07 04:30 | 35.55 | 35.17
2020-01-07 05:00 | 36.19 | 35.82
2020-01-07 05:30 | 38.01 | 37.66
2020-01-07 06:00 | 39.73 | 39.38
2020-01-07 06:30 | 44.56 | 43.88
2020-01-07 07:00 | 49.15 | 48.02
2020-01-07 07:30 | 53.92 | 53.01
2020-01-07 08:00 | 58.45 | 57.62
2020-01-07 08:30 | 61.34 | 60.55
2020-01-07 09:00 | 62.85 | 62.14
2020-01-07 09:30 | 62.99 | 62.21
2020-01-07 10:00 | 59.76 | 58.93
2020-01-07 10:30 | 63.48 | 62.53
2020-01-07 11:00 | 64.81 | 63.7
2020-01-07 11:30 | 64.17 | 62.95
2020-01-07 12:00 | 64.42 | 63.13
2020-01-07 12:30 | 66.63 | 65.44
2020-01-07 13:00 | 67.44 | 66.4
2020-01-07 13:30 | 69.07 | 68.08
2020-01-07 14:00 | 65.62 | 64.56
2020-01-07 14:30 | 68.68 | 67.65
2020-01-07 15:00 | 66.59 | 65.65
2020-01-07 15:30 | 66.83 | 65.97
2020-01-07 16:00 | 67.19 | 66.53
2020-01-07 16:30 | 66.69 | 66.29
2020-01-07 17:00 | 64.79 | 64.57
2020-01-07 17:30 | 62.84 | 62.63
2020-01-07 18:00 | 59.43 | 59.2
2020-01-07 18:30 | 58.59 | 58.3
2020-01-07 19:00 | 59.75 | 59.44
2020-01-07 19:30 | 60.18 | 59.85
2020-01-07 20:00 | 58.76 | 58.47
2020-01-07 20:30 | 56.31 | 56.07
2020-01-07 21:00 | 54.29 | 54.05
2020-01-07 21:30 | 51.65 | 51.4
2020-01-07 22:00 | 49.19 | 48.92
2020-01-07 22:30 | 46.61 | 46.32
2020-01-07 23:00 | 44.17 | 43.86
2020-01-07 23:30 | 42.13 | 41.8
2020-01-08 | 40.24 | 39.9
2020-01-08 00:30 | 38.57 | 38.23
2020-01-08 01:00 | 37.34 | 36.98
2020-01-08 01:30 | 36.63 | 36.26
2020-01-08 02:00 | 36.03 | 35.65
2020-01-08 02:30 | 35.82 | 35.44
2020-01-08 03:00 | 35.08 | 34.69
2020-01-08 03:30 | 34.85 | 34.46
2020-01-08 04:00 | 34.68 | 34.29
2020-01-08 04:30 | 35.1 | 34.71
2020-01-08 05:00 | 35.57 | 35.19
2020-01-08 05:30 | 37.09 | 36.73
2020-01-08 06:00 | 38.58 | 38.24
2020-01-08 06:30 | 43.33 | 42.77
2020-01-08 07:00 | 48.15 | 47.28
2020-01-08 07:30 | 53.62 | 52.76
2020-01-08 08:00 | 56.24 | 55.4
2020-01-08 08:30 | 58.27 | 57.18
2020-01-08 09:00 | 60.99 | 59.52
2020-01-08 09:30 | 61.77 | 60.11
2020-01-08 10:00 | 61.55 | 59.83
2020-01-08 10:30 | 62.39 | 60.56
2020-01-08 11:00 | 63.18 | 61.05
2020-01-08 11:30 | 63 | 60.83
2020-01-08 12:00 | 63.76 | 61.57
2020-01-08 12:30 | 65.11 | 63.02
2020-01-08 13:00 | 63.66 | 61.78
2020-01-08 13:30 | 65.31 | 63.37
2020-01-08 14:00 | 65.84 | 63.87
2020-01-08 14:30 | 66.67 | 64.65
2020-01-08 15:00 | 67.74 | 65.74
2020-01-08 15:30 | 68.13 | 66.27
2020-01-08 16:00 | 68.17 | 66.61
2020-01-08 16:30 | 69.21 | 67.64
2020-01-08 17:00 | 67.05 | 66.26
2020-01-08 17:30 | 64.33 | 63.9
2020-01-08 18:00 | 62.61 | 62.42
2020-01-08 18:30 | 61.96 | 61.7
2020-01-08 19:00 | 61.61 | 61.27
2020-01-08 19:30 | 61.47 | 61.12
2020-01-08 20:00 | 60.56 | 60.22
2020-01-08 20:30 | 58.66 | 58.31
2020-01-08 21:00 | 56.73 | 56.37
2020-01-08 21:30 | 53.89 | 53.49
2020-01-08 22:00 | 51.15 | 50.73
2020-01-08 22:30 | 49.44 | 48
2020-01-08 23:00 | 47.25 | 45.65
2020-01-08 23:30 | 45.55 | 43.22
2020-01-09 | 44.83 | 41.27
2020-01-09 00:30 | 43.47 | 39.79
2020-01-09 01:00 | 41.88 | 38.02
2020-01-09 01:30 | 41.08 | 37.14
2020-01-09 02:00 | 40.4 | 36.37
2020-01-09 02:30 | 40.02 | 35.95
2020-01-09 03:00 | 39.52 | 35.38
2020-01-09 03:30 | 39.12 | 34.94
2020-01-09 04:00 | 38.96 | 34.76
2020-01-09 04:30 | 39.1 | 34.91
2020-01-09 05:00 | 39.79 | 35.67
2020-01-09 05:30 | 41.05 | 37.07
2020-01-09 06:00 | 42.62 | 38.83
2020-01-09 06:30 | 46.69 | 43.28
2020-01-09 07:00 | 50.08 | 46.93
2020-01-09 07:30 | 55.9 | 53.13
2020-01-09 08:00 | 58.79 | 56.19
2020-01-09 08:30 | 62.36 | 59.94
2020-01-09 09:00 | 63.46 | 61.14
2020-01-09 09:30 | 63.1 | 61.49
2020-01-09 10:00 | 62.8 | 61.08
2020-01-09 10:30 | 64.6 | 62.67
2020-01-09 11:00 | 66.16 | 63.84
2020-01-09 11:30 | 65.45 | 63.1
2020-01-09 12:00 | 66.16 | 63.75
2020-01-09 12:30 | 65.85 | 63.54
2020-01-09 13:00 | 65.7 | 63.42
2020-01-09 13:30 | 65.25 | 62.95
2020-01-09 14:00 | 56.68 | 55.3
2020-01-09 14:30 | 47.13 | 46.02
2020-01-09 15:00 | 47.47 | 46.4
2020-01-09 15:30 | 47.97 | 46.97
2020-01-09 16:00 | 48.42 | 47.51
2020-01-09 16:30 | 48.81 | 48.04
2020-01-09 17:00 | 49.06 | 48.43
2020-01-09 17:30 | 47.79 | 47.34
2020-01-09 18:00 | 47.69 | 47.23
2020-01-09 18:30 | 46.77 | 46.3
2020-01-09 19:00 | 46.62 | 46.15
2020-01-09 19:30 | 46.35 | 45.88
2020-01-09 20:00 | 45.59 | 45.12
2020-01-09 20:30 | 44.04 | 43.55
2020-01-09 21:00 | 42.33 | 41.81
2020-01-09 21:30 | 40.37 | 38.81
2020-01-09 22:00 | 39.17 | 36.07
2020-01-09 22:30 | 38.41 | 34.11
2020-01-09 23:00 | 36.92 | 32.42
2020-01-09 23:30 | 37.44 | 30.73
2020-01-10 | 37.43 | 29.54
2020-01-10 00:30 | 36.5 | 28.5
2020-01-10 01:00 | 35.98 | 27.83
2020-01-10 01:30 | 35.36 | 26.99
2020-01-10 02:00 | 34.99 | 26.5
2020-01-10 02:30 | 34.8 | 26.26
2020-01-10 03:00 | 34.54 | 25.91
2020-01-10 03:30 | 34.42 | 25.72
2020-01-10 04:00 | 34.17 | 25.4
2020-01-10 04:30 | 34.16 | 25.39
2020-01-10 05:00 | 34.71 | 26.15
2020-01-10 05:30 | 35.05 | 26.59
2020-01-10 06:00 | 35.94 | 27.79
2020-01-10 06:30 | 38.23 | 30.77
2020-01-10 07:00 | 40.05 | 33
2020-01-10 07:30 | 43.6 | 37.29
2020-01-10 08:00 | 46.11 | 40.25
2020-01-10 08:30 | 48.3 | 42.77
2020-01-10 09:00 | 48.47 | 42.96
2020-01-10 09:30 | 48.27 | 42.74
2020-01-10 10:00 | 48.77 | 43.32
2020-01-10 10:30 | 48 | 43.28
2020-01-10 11:00 | 46.77 | 43.43
2020-01-10 11:30 | 46.62 | 43.26
2020-01-10 12:00 | 47.41 | 44.12
2020-01-10 12:30 | 47.95 | 44.7
2020-01-10 13:00 | 48.78 | 45.61
2020-01-10 13:30 | 61.31 | 59.55
2020-01-10 14:00 | 65.97 | 64.85
2020-01-10 14:30 | 66.64 | 65.57
2020-01-10 15:00 | 66.74 | 65.67
2020-01-10 15:30 | 66.95 | 65.89
2020-01-10 16:00 | 67.57 | 66.5
2020-01-10 16:30 | 67.77 | 66.71
2020-01-10 17:00 | 67.33 | 66.25
2020-01-10 17:30 | 66.08 | 64.98
2020-01-10 18:00 | 64.37 | 63.25
2020-01-10 18:30 | 63.08 | 61.94
2020-01-10 19:00 | 62.97 | 61.83
2020-01-10 19:30 | 62.94 | 61.8
2020-01-10 20:00 | 62.15 | 60.99
2020-01-10 20:30 | 60.36 | 59.16
2020-01-10 21:00 | 58.73 | 57.49
2020-01-10 21:30 | 57.2 | 55.92
2020-01-10 22:00 | 54.96 | 53.63
2020-01-10 22:30 | 52.53 | 51.11
2020-01-10 23:00 | 50.2 | 48.71
2020-01-10 23:30 | 47.9 | 46.33
2020-01-11 | 46.64 | 44.23
2020-01-11 00:30 | 46.15 | 42.73
2020-01-11 01:00 | 45.22 | 41.73
2020-01-11 01:30 | 44.33 | 40.75
2020-01-11 02:00 | 43.94 | 40.22
2020-01-11 02:30 | 43.48 | 39.71
2020-01-11 03:00 | 42.97 | 39.14
2020-01-11 03:30 | 42.59 | 38.72
2020-01-11 04:00 | 42.07 | 38.15
2020-01-11 04:30 | 42.16 | 38.25
2020-01-11 05:00 | 42.31 | 38.4
2020-01-11 05:30 | 42.77 | 38.93
2020-01-11 06:00 | 42.43 | 38.55
2020-01-11 06:30 | 44.34 | 40.65
2020-01-11 07:00 | 45.08 | 41.53
2020-01-11 07:30 | 47.77 | 44.46
2020-01-11 08:00 | 48.67 | 45.44
2020-01-11 08:30 | 53.3 | 50.38
2020-01-11 09:00 | 54.49 | 51.65
2020-01-11 09:30 | 53.46 | 50.57
2020-01-11 10:00 | 51.46 | 48.44
2020-01-11 10:30 | 52.36 | 49.41
2020-01-11 11:00 | 52.59 | 49.66
2020-01-11 11:30 | 52.68 | 49.75
2020-01-11 12:00 | 52.44 | 49.5
2020-01-11 12:30 | 51.64 | 48.64
2020-01-11 13:00 | 51.4 | 48.41
2020-01-11 13:30 | 51.28 | 48.27
2020-01-11 14:00 | 51.73 | 48.76
2020-01-11 14:30 | 52.24 | 49.29
2020-01-11 15:00 | 53.04 | 50.14
2020-01-11 15:30 | 54.04 | 51.21
2020-01-11 16:00 | 55.45 | 52.7
2020-01-11 16:30 | 56.6 | 53.92
2020-01-11 17:00 | 57.27 | 54.63
2020-01-11 17:30 | 58.01 | 55.43
2020-01-11 18:00 | 59.29 | 56.78
2020-01-11 18:30 | 59.21 | 56.69
2020-01-11 19:00 | 59.15 | 56.64
2020-01-11 19:30 | 60.34 | 57.88
2020-01-11 20:00 | 59.73 | 57.24
2020-01-11 20:30 | 58.2 | 55.62
2020-01-11 21:00 | 56.37 | 53.68
2020-01-11 21:30 | 54.6 | 51.82
2020-01-11 22:00 | 53.11 | 50.23
2020-01-11 22:30 | 51.18 | 48.17
2020-01-11 23:00 | 49.19 | 46.02
2020-01-11 23:30 | 47.04 | 43.69
2020-01-12 | 45.54 | 42.06
2020-01-12 00:30 | 44.04 | 40.43
2020-01-12 01:00 | 42.97 | 39.25
2020-01-12 01:30 | 42.32 | 38.53
2020-01-12 02:00 | 41.53 | 37.64
2020-01-12 02:30 | 41.06 | 37.13
2020-01-12 03:00 | 40.56 | 36.56
2020-01-12 03:30 | 40.08 | 36.03
2020-01-12 04:00 | 39.78 | 35.68
2020-01-12 04:30 | 39.69 | 35.57
2020-01-12 05:00 | 39.72 | 35.62
2020-01-12 05:30 | 39.63 | 35.52
2020-01-12 06:00 | 38.81 | 34.57
2020-01-12 06:30 | 39.65 | 35.51
2020-01-12 07:00 | 39.84 | 35.73
2020-01-12 07:30 | 41.16 | 37.21
2020-01-12 08:00 | 43.15 | 39.42
2020-01-12 08:30 | 44.91 | 41.35
2020-01-12 09:00 | 44.3 | 40.69
2020-01-12 09:30 | 46.24 | 42.81
2020-01-12 10:00 | 47.31 | 43.97
2020-01-12 10:30 | 47.96 | 44.67
2020-01-12 11:00 | 50.15 | 47.04
2020-01-12 11:30 | 48.89 | 45.69
2020-01-12 12:00 | 48.68 | 45.47
2020-01-12 12:30 | 49.43 | 46.28
2020-01-12 13:00 | 48.43 | 45.2
2020-01-12 13:30 | 49.57 | 46.43
2020-01-12 14:00 | 50.42 | 47.34
2020-01-12 14:30 | 51.27 | 48.26
2020-01-12 15:00 | 52.54 | 49.61
2020-01-12 15:30 | 53.54 | 50.68
2020-01-12 16:00 | 55.2 | 52.45
2020-01-12 16:30 | 57.02 | 54.38
2020-01-12 17:00 | 58.67 | 56.13
2020-01-12 17:30 | 59.15 | 56.63
2020-01-12 18:00 | 60.41 | 57.95
2020-01-12 18:30 | 60.85 | 58.42
2020-01-12 19:00 | 61.48 | 59.07
2020-01-12 19:30 | 62.12 | 59.74
2020-01-12 20:00 | 60.95 | 58.5
2020-01-12 20:30 | 58.97 | 56.42
2020-01-12 21:00 | 56.91 | 54.24
2020-01-12 21:30 | 55.2 | 52.42
2020-01-12 22:00 | 53.11 | 50.21
2020-01-12 22:30 | 50.99 | 47.93
2020-01-12 23:00 | 48.99 | 45.77
2020-01-12 23:30 | 47.11 | 43.76
2020-01-13 | 45.95 | 42.49
2020-01-13 00:30 | 44.55 | 40.95
2020-01-13 01:00 | 43.7 | 40.01
2020-01-13 01:30 | 43.32 | 39.61
2020-01-13 02:00 | 43 | 39.24
2020-01-13 02:30 | 42.71 | 38.92
2020-01-13 03:00 | 42.38 | 38.55
2020-01-13 03:30 | 42.29 | 38.45
2020-01-13 04:00 | 42.41 | 38.58
2020-01-13 04:30 | 42.71 | 38.91
2020-01-13 05:00 | 43.8 | 40.11
2020-01-13 05:30 | 45.77 | 42.27
2020-01-13 06:00 | 47.85 | 44.52
2020-01-13 06:30 | 53.02 | 50.07
2020-01-13 07:00 | 57.6 | 54.91
2020-01-13 07:30 | 63.38 | 61.39
2020-01-13 08:00 | 67.95 | 65.83
2020-01-13 08:30 | 71.28 | 68.52
2020-01-13 09:00 | 71.08 | 67.53
2020-01-13 09:30 | 69.57 | 68.93
2020-01-13 10:00 | 68.25 | 68.03
2020-01-13 10:30 | 67.68 | 67.38
2020-01-13 11:00 | 69.79 | 69.44
2020-01-13 11:30 | 69.59 | 69.23
2020-01-13 12:00 | 70.5 | 70.1
2020-01-13 12:30 | 72.42 | 72
2020-01-13 13:00 | 72.14 | 71.72
2020-01-13 13:30 | 72.97 | 72.5
2020-01-13 14:00 | 73.82 | 73.3
2020-01-13 14:30 | 75 | 74.52
2020-01-13 15:00 | 76.07 | 75.63
2020-01-13 15:30 | 76.15 | 75.82
2020-01-13 16:00 | 75.85 | 75.62
2020-01-13 16:30 | 73.02 | 72.94
2020-01-13 17:00 | 70.96 | 70.96
2020-01-13 17:30 | 71.16 | 71.1
2020-01-13 18:00 | 70.64 | 70.38
2020-01-13 18:30 | 69.67 | 69.28
2020-01-13 19:00 | 70.15 | 69.22
2020-01-13 19:30 | 69.81 | 68.85
2020-01-13 20:00 | 68.19 | 67.21
2020-01-13 20:30 | 65.58 | 64.55
2020-01-13 21:00 | 62.76 | 61.67
2020-01-13 21:30 | 60.72 | 58.46
2020-01-13 22:00 | 58.48 | 55.64
2020-01-13 22:30 | 57.21 | 52.73
2020-01-13 23:00 | 56.26 | 50.22
2020-01-13 23:30 | 55.13 | 47.89
2020-01-14 | 53.76 | 46.25
2020-01-14 00:30 | 52.34 | 44.53
2020-01-14 01:00 | 51.48 | 43.49
2020-01-14 01:30 | 50.87 | 42.77
2020-01-14 02:00 | 50.38 | 42.15
2020-01-14 02:30 | 49.94 | 41.61
2020-01-14 03:00 | 49.44 | 40.98
2020-01-14 03:30 | 48.98 | 40.44
2020-01-14 04:00 | 48.8 | 40.24
2020-01-14 04:30 | 49.28 | 40.83
2020-01-14 05:00 | 50.15 | 41.91
2020-01-14 05:30 | 52.08 | 44.23
2020-01-14 06:00 | 53.64 | 46.06
2020-01-14 06:30 | 57.78 | 50.89
2020-01-14 07:00 | 61.81 | 55.5
2020-01-14 07:30 | 65.95 | 62.6
2020-01-14 08:00 | 66.98 | 66.88
2020-01-14 08:30 | 69.17 | 69.16
2020-01-14 09:00 | 70.14 | 70.14
2020-01-14 09:30 | 69.94 | 69.94
2020-01-14 10:00 | 70.13 | 70.13
2020-01-14 10:30 | 70.17 | 70.13
2020-01-14 11:00 | 69.7 | 69.63
2020-01-14 11:30 | 71.42 | 71.33
2020-01-14 12:00 | 72.1 | 72.09
2020-01-14 12:30 | 71.82 | 71.82
2020-01-14 13:00 | 73.12 | 73.11
2020-01-14 13:30 | 74.07 | 74.07
2020-01-14 14:00 | 72.24 | 72.24
2020-01-14 14:30 | 73.05 | 73.05
2020-01-14 15:00 | 73.32 | 73.32
2020-01-14 15:30 | 74.33 | 74.32
2020-01-14 16:00 | 75.42 | 75.36
2020-01-14 16:30 | 74.95 | 74.78
2020-01-14 17:00 | 74.68 | 74.29
2020-01-14 17:30 | 73.51 | 72.73
2020-01-14 18:00 | 71.9 | 70.55
2020-01-14 18:30 | 70.96 | 69.18
2020-01-14 19:00 | 71.12 | 69.18
2020-01-14 19:30 | 70.81 | 68.92
2020-01-14 20:00 | 69.85 | 67.79
2020-01-14 20:30 | 67.56 | 65.18
2020-01-14 21:00 | 65.36 | 62.72
2020-01-14 21:30 | 62.65 | 59.73
2020-01-14 22:00 | 56.66 | 56.35
2020-01-14 22:30 | 53.85 | 53.51
2020-01-14 23:00 | 51.33 | 50.98
2020-01-14 23:30 | 48.82 | 48.45
2020-01-15 | 46.51 | 46.12
2020-01-15 00:30 | 45 | 44.56
2020-01-15 01:00 | 43.68 | 43.15
2020-01-15 01:30 | 42.85 | 42.25
2020-01-15 02:00 | 42.05 | 41.4
2020-01-15 02:30 | 41.28 | 40.81
2020-01-15 03:00 | 40.57 | 40.1
2020-01-15 03:30 | 40.27 | 39.79
2020-01-15 04:00 | 39.82 | 39.34
2020-01-15 04:30 | 40.47 | 39.99
2020-01-15 05:00 | 41.63 | 41.17
2020-01-15 05:30 | 43.57 | 43.13
2020-01-15 06:00 | 45.19 | 44.77
2020-01-15 06:30 | 50.07 | 49.68
2020-01-15 07:00 | 54.58 | 54.23
2020-01-15 07:30 | 59.92 | 59.5
2020-01-15 08:00 | 63.36 | 62.81
2020-01-15 08:30 | 68.51 | 67.52
2020-01-15 09:00 | 69.1 | 67.89
2020-01-15 09:30 | 70 | 68.65
2020-01-15 10:00 | 69.69 | 68.24
2020-01-15 10:30 | 71.63 | 69.83
2020-01-15 11:00 | 72.3 | 70.39
2020-01-15 11:30 | 72.23 | 70.32
2020-01-15 12:00 | 72.94 | 71
2020-01-15 12:30 | 72.66 | 70.74
2020-01-15 13:00 | 74.87 | 71.56
2020-01-15 13:30 | 75.89 | 72.43
2020-01-15 14:00 | 76.77 | 73.36
2020-01-15 14:30 | 77.59 | 74.22
2020-01-15 15:00 | 78.15 | 74.81
2020-01-15 15:30 | 78.77 | 75.44
2020-01-15 16:00 | 79.7 | 76.4
2020-01-15 16:30 | 80.57 | 77.28
2020-01-15 17:00 | 80.24 | 76.91
2020-01-15 17:30 | 78.16 | 74.65
2020-01-15 18:00 | 77.03 | 73.39
2020-01-15 18:30 | 75.49 | 71.68
2020-01-15 19:00 | 74.9 | 71.06
2020-01-15 19:30 | 74.74 | 70.9
2020-01-15 20:00 | 73.78 | 69.89
2020-01-15 20:30 | 71.05 | 67.1
2020-01-15 21:00 | 68.63 | 64.49
2020-01-15 21:30 | 65.56 | 61.14
2020-01-15 22:00 | 62.49 | 57.77
2020-01-15 22:30 | 59.49 | 54.54
2020-01-15 23:00 | 57.13 | 51.95
2020-01-15 23:30 | 55.01 | 49.57
2020-01-16 | 53 | 47.29
2020-01-16 00:30 | 49.23 | 45.3
2020-01-16 01:00 | 47.06 | 43.66
2020-01-16 01:30 | 46.61 | 43.15
2020-01-16 02:00 | 46.05 | 42.52
2020-01-16 02:30 | 43.01 | 41.31
2020-01-16 03:00 | 42.27 | 40.77
2020-01-16 03:30 | 41.99 | 40.47
2020-01-16 04:00 | 41.7 | 40.18
2020-01-16 04:30 | 42.14 | 40.64
2020-01-16 05:00 | 43.19 | 41.74
2020-01-16 05:30 | 45.3 | 43.93
2020-01-16 06:00 | 46.71 | 45.4
2020-01-16 06:30 | 51.65 | 50.48
2020-01-16 07:00 | 56.22 | 54.62
2020-01-16 07:30 | 62.86 | 60.62
2020-01-16 08:00 | 66.87 | 64.75
2020-01-16 08:30 | 71.66 | 69.73
2020-01-16 09:00 | 72.47 | 70.53
2020-01-16 09:30 | 73.79 | 71.17
2020-01-16 10:00 | 77.18 | 73.79
2020-01-16 10:30 | 78.26 | 74.92
2020-01-16 11:00 | 72.75 | 69.12
2020-01-16 11:30 | 72.84 | 69.23
2020-01-16 12:00 | 72.69 | 69.08
2020-01-16 12:30 | 73.82 | 70.25
2020-01-16 13:00 | 74.68 | 71.12
2020-01-16 13:30 | 76.45 | 72.98
2020-01-16 14:00 | 81.97 | 78.79
2020-01-16 14:30 | 84.25 | 81.14
2020-01-16 15:00 | 80.44 | 77.16
2020-01-16 15:30 | 78.12 | 74.68
2020-01-16 16:00 | 75.85 | 72.28
2020-01-16 16:30 | 74.85 | 71.17
2020-01-16 17:00 | 75.7 | 72.01
2020-01-16 17:30 | 75.1 | 71.38
2020-01-16 18:00 | 73.75 | 69.92
2020-01-16 18:30 | 72.8 | 68.88
2020-01-16 19:00 | 72.64 | 68.76
2020-01-16 19:30 | 72.95 | 69.15
2020-01-16 20:00 | 71.55 | 67.64
2020-01-16 20:30 | 69.3 | 65.21
2020-01-16 21:00 | 67.3 | 63.04
2020-01-16 21:30 | 64.31 | 59.78
2020-01-16 22:00 | 60.36 | 55.42
2020-01-16 22:30 | 55.36 | 52.11
2020-01-16 23:00 | 52.63 | 49.66
2020-01-16 23:30 | 50.6 | 47.48
2020-01-17 | 48.66 | 45.4
2020-01-17 00:30 | 47.45 | 44.08
2020-01-17 01:00 | 46.2 | 42.76
2020-01-17 01:30 | 45.43 | 41.97
2020-01-17 02:00 | 44.86 | 41.33
2020-01-17 02:30 | 44.41 | 40.83
2020-01-17 03:00 | 43.84 | 40.19
2020-01-17 03:30 | 43.49 | 39.82
2020-01-17 04:00 | 43.33 | 39.64
2020-01-17 04:30 | 43.38 | 39.7
2020-01-17 05:00 | 44.81 | 41.28
2020-01-17 05:30 | 47.51 | 44.24
2020-01-17 06:00 | 48.89 | 45.75
2020-01-17 06:30 | 53.76 | 51.01
2020-01-17 07:00 | 58.05 | 55.56
2020-01-17 07:30 | 64.28 | 62.04
2020-01-17 08:00 | 70.23 | 68.21
2020-01-17 08:30 | 70.34 | 68.38
2020-01-17 09:00 | 70.74 | 68.75
2020-01-17 09:30 | 71.77 | 69.82
2020-01-17 10:00 | 71.25 | 69.31
2020-01-17 10:30 | 71.36 | 69.43
2020-01-17 11:00 | 79.04 | 76.78
2020-01-17 11:30 | 78.8 | 75.47
2020-01-17 12:00 | 68.04 | 63.99
2020-01-17 12:30 | 63.36 | 58.96
2020-01-17 13:00 | 70.47 | 66.54
2020-01-17 13:30 | 69.39 | 65.38
2020-01-17 14:00 | 70.26 | 66.29
2020-01-17 14:30 | 68.82 | 64.73
2020-01-17 15:00 | 68.8 | 64.68
2020-01-17 15:30 | 68.29 | 64.1
2020-01-17 16:00 | 63.02 | 58.4
2020-01-17 16:30 | 61.27 | 56.44
2020-01-17 17:00 | 64.04 | 59.45
2020-01-17 17:30 | 63.42 | 58.73
2020-01-17 18:00 | 59.43 | 56.62
2020-01-17 18:30 | 56.63 | 53.82
2020-01-17 19:00 | 57.04 | 54.25
2020-01-17 19:30 | 56.19 | 55.18
2020-01-17 20:00 | 54.78 | 54.5
2020-01-17 20:30 | 52.71 | 52.44
2020-01-17 21:00 | 50.61 | 50.27
2020-01-17 21:30 | 48.86 | 48.59
2020-01-17 22:00 | 46.04 | 45.9
2020-01-17 22:30 | 43.81 | 43.6
2020-01-17 23:00 | 42.22 | 41.79
2020-01-17 23:30 | 40.76 | 40.28
2020-01-18 | 39.05 | 38.54
2020-01-18 00:30 | 37.8 | 37.26
2020-01-18 01:00 | 36.54 | 36
2020-01-18 01:30 | 34.4 | 33.83
2020-01-18 02:00 | 33.73 | 33.14
2020-01-18 02:30 | 33.56 | 32.97
2020-01-18 03:00 | 33.57 | 32.98
2020-01-18 03:30 | 33.93 | 33.34
2020-01-18 04:00 | 33.92 | 33.34
2020-01-18 04:30 | 34.16 | 33.58
2020-01-18 05:00 | 34.5 | 33.92
2020-01-18 05:30 | 35.29 | 34.73
2020-01-18 06:00 | 35.07 | 34.51
2020-01-18 06:30 | 37.09 | 36.55
2020-01-18 07:00 | 38.56 | 38.04
2020-01-18 07:30 | 40.09 | 39.61
2020-01-18 08:00 | 40.91 | 40.33
2020-01-18 08:30 | 43.74 | 42.8
2020-01-18 09:00 | 44.93 | 44.33
2020-01-18 09:30 | 45.53 | 44.99
2020-01-18 10:00 | 46.39 | 45.67
2020-01-18 10:30 | 47.71 | 46.87
2020-01-18 11:00 | 49.08 | 48.11
2020-01-18 11:30 | 49.31 | 48.34
2020-01-18 12:00 | 50.3 | 49.34
2020-01-18 12:30 | 49.67 | 48.8
2020-01-18 13:00 | 49.93 | 49.1
2020-01-18 13:30 | 50.51 | 49.69
2020-01-18 14:00 | 51.37 | 50.58
2020-01-18 14:30 | 52.02 | 51.34
2020-01-18 15:00 | 53.38 | 52.71
2020-01-18 15:30 | 55.38 | 54.77
2020-01-18 16:00 | 57.56 | 57.01
2020-01-18 16:30 | 58.79 | 58.32
2020-01-18 17:00 | 59.64 | 59.26
2020-01-18 17:30 | 61.02 | 60.72
2020-01-18 18:00 | 62.32 | 62.05
2020-01-18 18:30 | 61.88 | 61.68
2020-01-18 19:00 | 61.47 | 61.27
2020-01-18 19:30 | 62.53 | 62.3
2020-01-18 20:00 | 61.8 | 61.58
2020-01-18 20:30 | 59.39 | 59.18
2020-01-18 21:00 | 57.37 | 57.15
2020-01-18 21:30 | 55.21 | 54.97
2020-01-18 22:00 | 53.12 | 52.87
2020-01-18 22:30 | 51.07 | 50.81
2020-01-18 23:00 | 48.48 | 48.21
2020-01-18 23:30 | 45.8 | 45.5
2020-01-19 | 43.93 | 43.62
2020-01-19 00:30 | 42.28 | 41.95
2020-01-19 01:00 | 40.92 | 40.58
2020-01-19 01:30 | 39.91 | 39.57
2020-01-19 02:00 | 39.28 | 38.94
2020-01-19 02:30 | 38.66 | 38.32
2020-01-19 03:00 | 37.95 | 37.6
2020-01-19 03:30 | 37.55 | 37.19
2020-01-19 04:00 | 37.53 | 37.17
2020-01-19 04:30 | 37.11 | 36.75
2020-01-19 05:00 | 36.89 | 36.53
2020-01-19 05:30 | 36.87 | 36.51
2020-01-19 06:00 | 36.51 | 36.13
2020-01-19 06:30 | 37.7 | 37.34
2020-01-19 07:00 | 38.29 | 37.94
2020-01-19 07:30 | 38.76 | 38.42
2020-01-19 08:00 | 40.74 | 40.42
2020-01-19 08:30 | 42.81 | 42.35
2020-01-19 09:00 | 43.94 | 43.34
2020-01-19 09:30 | 45.14 | 44.65
2020-01-19 10:00 | 45.68 | 45.37
2020-01-19 10:30 | 47.82 | 47.4
2020-01-19 11:00 | 48.8 | 48.37
2020-01-19 11:30 | 49.75 | 49.27
2020-01-19 12:00 | 51.82 | 51.26
2020-01-19 12:30 | 53.31 | 52.72
2020-01-19 13:00 | 54.61 | 53.95
2020-01-19 13:30 | 55.26 | 54.63
2020-01-19 14:00 | 55.62 | 55.03
2020-01-19 14:30 | 56.14 | 55.61
2020-01-19 15:00 | 57.43 | 56.93
2020-01-19 15:30 | 59.95 | 59.48
2020-01-19 16:00 | 64 | 63.35
2020-01-19 16:30 | 64.93 | 64.05
2020-01-19 17:00 | 65.45 | 64.58
2020-01-19 17:30 | 66.54 | 65.68
2020-01-19 18:00 | 68.22 | 67.38
2020-01-19 18:30 | 69.05 | 68.22
2020-01-19 19:00 | 68.55 | 67.7
2020-01-19 19:30 | 68.96 | 68.11
2020-01-19 20:00 | 67.74 | 66.84
2020-01-19 20:30 | 65.22 | 64.27
2020-01-19 21:00 | 62.51 | 61.51
2020-01-19 21:30 | 59.53 | 58.46
2020-01-19 22:00 | 56.29 | 55.14
2020-01-19 22:30 | 52.92 | 51.7
2020-01-19 23:00 | 50.35 | 49.1
2020-01-19 23:30 | 48.34 | 47.01
2020-01-20 | 46.81 | 45.44
2020-01-20 00:30 | 45.61 | 44.19
2020-01-20 01:00 | 44.4 | 42.94
2020-01-20 01:30 | 43.75 | 42.26
2020-01-20 02:00 | 43.26 | 41.75
2020-01-20 02:30 | 42.78 | 41.25
2020-01-20 03:00 | 42.39 | 40.88
2020-01-20 03:30 | 42.21 | 40.72
2020-01-20 04:00 | 42.27 | 40.78
2020-01-20 04:30 | 42.49 | 41
2020-01-20 05:00 | 43.91 | 42.49
2020-01-20 05:30 | 46.36 | 45.03
2020-01-20 06:00 | 48.79 | 47.55
2020-01-20 06:30 | 54.47 | 53.34
2020-01-20 07:00 | 61.04 | 59.58
2020-01-20 07:30 | 67.63 | 66.64
2020-01-20 08:00 | 72.86 | 71.31
2020-01-20 08:30 | 77.63 | 75.4
2020-01-20 09:00 | 80.28 | 77.08
2020-01-20 09:30 | 80.94 | 77.79
2020-01-20 10:00 | 80.25 | 77.07
2020-01-20 10:30 | 79.91 | 76.73
2020-01-20 11:00 | 82.64 | 77.88
2020-01-20 11:30 | 84.09 | 79.09
2020-01-20 12:00 | 85.12 | 80.23
2020-01-20 12:30 | 85.48 | 80.62
2020-01-20 13:00 | 87.37 | 81.44
2020-01-20 13:30 | 90.14 | 83.11
2020-01-20 14:00 | 90.72 | 83.87
2020-01-20 14:30 | 91.85 | 85.02
2020-01-20 15:00 | 86.29 | 78.79
2020-01-20 15:30 | 85.54 | 77.95
2020-01-20 16:00 | 89.7 | 82.51
2020-01-20 16:30 | 89.23 | 81.95
2020-01-20 17:00 | 86.27 | 78.54
2020-01-20 17:30 | 82.31 | 73.92
2020-01-20 18:00 | 80.1 | 71.37
2020-01-20 18:30 | 79.01 | 70.11
2020-01-20 19:00 | 79.43 | 70.61
2020-01-20 19:30 | 77.68 | 68.53
2020-01-20 20:00 | 74.22 | 65.62
2020-01-20 20:30 | 59.96 | 57.51
2020-01-20 21:00 | 56.03 | 54.92
2020-01-20 21:30 | 52.24 | 51.02
2020-01-20 22:00 | 49.04 | 47.72
2020-01-20 22:30 | 46.27 | 44.85
2020-01-20 23:00 | 44.48 | 42.98
2020-01-20 23:30 | 42.01 | 40.95
2020-01-21 | 39.5 | 39.12
2020-01-21 00:30 | 38.12 | 37.76
2020-01-21 01:00 | 37.37 | 36.99
2020-01-21 01:30 | 36.56 | 36.17
2020-01-21 02:00 | 35.9 | 35.5
2020-01-21 02:30 | 35.39 | 34.99
2020-01-21 03:00 | 34.93 | 34.52
2020-01-21 03:30 | 34.61 | 34.21
2020-01-21 04:00 | 34.61 | 34.21
2020-01-21 04:30 | 35.1 | 34.72
2020-01-21 05:00 | 36.15 | 35.79
2020-01-21 05:30 | 38.19 | 37.85
2020-01-21 06:00 | 39.81 | 39.49
2020-01-21 06:30 | 44.96 | 44.41
2020-01-21 07:00 | 49.52 | 49.03
2020-01-21 07:30 | 54.81 | 54.17
2020-01-21 08:00 | 58.27 | 57.48
2020-01-21 08:30 | 61.47 | 59.97
2020-01-21 09:00 | 66.22 | 63.67
2020-01-21 09:30 | 70.38 | 66.7
2020-01-21 10:00 | 72.13 | 68.53
2020-01-21 10:30 | 71.88 | 68.27
2020-01-21 11:00 | 72.12 | 68.56
2020-01-21 11:30 | 71.77 | 68.21
2020-01-21 12:00 | 72.21 | 68.68
2020-01-21 12:30 | 75.02 | 69.65
2020-01-21 13:00 | 76.05 | 70.42
2020-01-21 13:30 | 76.33 | 70.66
2020-01-21 14:00 | 78.07 | 72.57
2020-01-21 14:30 | 79.37 | 73.97
2020-01-21 15:00 | 80.94 | 75.63
2020-01-21 15:30 | 81.52 | 76.26
2020-01-21 16:00 | 83.02 | 77.86
2020-01-21 16:30 | 84.27 | 79.17
2020-01-21 17:00 | 82.15 | 76.8
2020-01-21 17:30 | 78.66 | 72.93
2020-01-21 18:00 | 75.66 | 69.56
2020-01-21 18:30 | 73.8 | 67.51
2020-01-21 19:00 | 73.57 | 67.23
2020-01-21 19:30 | 73.27 | 66.91
2020-01-21 20:00 | 71.44 | 64.84
2020-01-21 20:30 | 69.29 | 62.39
2020-01-21 21:00 | 66.93 | 59.68
2020-01-21 21:30 | 61.44 | 56.55
2020-01-21 22:00 | 58.98 | 53.95
2020-01-21 22:30 | 54.68 | 50.84
2020-01-21 23:00 | 51.47 | 48.39
2020-01-21 23:30 | 49.21 | 46.02
2020-01-22 | 47.5 | 44.17
2020-01-22 00:30 | 46.36 | 42.92
2020-01-22 01:00 | 45.36 | 41.88
2020-01-22 01:30 | 44.63 | 41.11
2020-01-22 02:00 | 43.97 | 40.39
2020-01-22 02:30 | 43.41 | 39.78
2020-01-22 03:00 | 43.03 | 39.36
2020-01-22 03:30 | 42.93 | 39.24
2020-01-22 04:00 | 42.78 | 39.07
2020-01-22 04:30 | 42.89 | 39.22
2020-01-22 05:00 | 43.76 | 40.17
2020-01-22 05:30 | 45.4 | 41.99
2020-01-22 06:00 | 47.03 | 43.75
2020-01-22 06:30 | 51.49 | 48.62
2020-01-22 07:00 | 55.97 | 53.37
2020-01-22 07:30 | 62.03 | 59.66
2020-01-22 08:00 | 66.03 | 63.87
2020-01-22 08:30 | 69.94 | 67.86
2020-01-22 09:00 | 70.6 | 68.4
2020-01-22 09:30 | 71.87 | 69.71
2020-01-22 10:00 | 71.11 | 68.93
2020-01-22 10:30 | 71.25 | 69.09
2020-01-22 11:00 | 70.54 | 68.35
2020-01-22 11:30 | 71.47 | 69.32
2020-01-22 12:00 | 72.78 | 70.68
2020-01-22 12:30 | 73.49 | 71.41
2020-01-22 13:00 | 73.42 | 71.34
2020-01-22 13:30 | 74.51 | 72.48
2020-01-22 14:00 | 74.96 | 72.94
2020-01-22 14:30 | 76.03 | 74.06
2020-01-22 15:00 | 77.1 | 75.15
2020-01-22 15:30 | 77.88 | 75.95
2020-01-22 16:00 | 78.52 | 76.6
2020-01-22 16:30 | 78.99 | 77.06
2020-01-22 17:00 | 79.98 | 78.07
2020-01-22 17:30 | 77.84 | 75.83
2020-01-22 18:00 | 76.69 | 74.64
2020-01-22 18:30 | 74.69 | 72.56
2020-01-22 19:00 | 73.82 | 71.66
2020-01-22 19:30 | 73.25 | 71.39
2020-01-22 20:00 | 69.97 | 68.99
2020-01-22 20:30 | 66.91 | 65.91
2020-01-22 21:00 | 64.42 | 63.37
2020-01-22 21:30 | 61.12 | 59.97
2020-01-22 22:00 | 57.81 | 56.37
2020-01-22 22:30 | 54.49 | 52.67
2020-01-22 23:00 | 52.08 | 49.93
2020-01-22 23:30 | 50.11 | 47.64
2020-01-23 | 48.05 | 45.19
2020-01-23 00:30 | 44.02 | 43.25
2020-01-23 01:00 | 42.7 | 42.25
2020-01-23 01:30 | 42 | 41.55
2020-01-23 02:00 | 41.32 | 40.86
2020-01-23 02:30 | 40.64 | 40.15
2020-01-23 03:00 | 40.33 | 39.84
2020-01-23 03:30 | 40.11 | 39.62
2020-01-23 04:00 | 39.6 | 39.1
2020-01-23 04:30 | 39.66 | 39.17
2020-01-23 05:00 | 40.57 | 40.09
2020-01-23 05:30 | 42.42 | 41.96
2020-01-23 06:00 | 44.34 | 43.89
2020-01-23 06:30 | 49.34 | 48.56
2020-01-23 07:00 | 53.43 | 52.71
2020-01-23 07:30 | 60.22 | 59.79
2020-01-23 08:00 | 65.04 | 64.15
2020-01-23 08:30 | 69.32 | 68.39
2020-01-23 09:00 | 69.37 | 68.45
2020-01-23 09:30 | 70.6 | 69.7
2020-01-23 10:00 | 71.88 | 71.01
2020-01-23 10:30 | 73.28 | 72.42
2020-01-23 11:00 | 71.23 | 70.35
2020-01-23 11:30 | 71.03 | 70.15
2020-01-23 12:00 | 72.9 | 72.05
2020-01-23 12:30 | 72.11 | 71.28
2020-01-23 13:00 | 73.33 | 72.5
2020-01-23 13:30 | 73.53 | 72.7
2020-01-23 14:00 | 75.52 | 74.71
2020-01-23 14:30 | 80.26 | 79.52
2020-01-23 15:00 | 81.06 | 80.32
2020-01-23 15:30 | 80.26 | 79.5
2020-01-23 16:00 | 78.08 | 77.28
2020-01-23 16:30 | 76.87 | 76.05
2020-01-23 17:00 | 75.81 | 74.97
2020-01-23 17:30 | 72.91 | 72.01
2020-01-23 18:00 | 72.18 | 71.26
2020-01-23 18:30 | 71.94 | 71
2020-01-23 19:00 | 72.01 | 71.03
2020-01-23 19:30 | 72.14 | 71.18
2020-01-23 20:00 | 70.57 | 69.51
2020-01-23 20:30 | 68.28 | 66.97
2020-01-23 21:00 | 66.04 | 64.44
2020-01-23 21:30 | 61.97 | 60.6
2020-01-23 22:00 | 57.42 | 55.9
2020-01-23 22:30 | 54.4 | 52.57
2020-01-23 23:00 | 49.84 | 49.79
2020-01-23 23:30 | 47.47 | 47.43
2020-01-24 | 45.41 | 45.39
2020-01-24 00:30 | 43.7 | 43.69
2020-01-24 01:00 | 42.53 | 42.52
2020-01-24 01:30 | 41.42 | 41.42
2020-01-24 02:00 | 40.76 | 40.76
2020-01-24 02:30 | 40.27 | 40.26
2020-01-24 03:00 | 39.4 | 39.32
2020-01-24 03:30 | 38.83 | 38.65
2020-01-24 04:00 | 38.73 | 38.56
2020-01-24 04:30 | 39.04 | 38.85
2020-01-24 05:00 | 40.03 | 39.79
2020-01-24 05:30 | 42.49 | 42.16
2020-01-24 06:00 | 44.62 | 44.19
2020-01-24 06:30 | 49.47 | 48.69
2020-01-24 07:00 | 53.54 | 52.88
2020-01-24 07:30 | 59.77 | 59.2
2020-01-24 08:00 | 64.38 | 63.5
2020-01-24 08:30 | 71.16 | 69.8
2020-01-24 09:00 | 74.31 | 72.47
2020-01-24 09:30 | 73.2 | 71.33
2020-01-24 10:00 | 72.44 | 70.54
2020-01-24 10:30 | 70.78 | 68.84
2020-01-24 11:00 | 70.97 | 69.01
2020-01-24 11:30 | 72.01 | 69.91
2020-01-24 12:00 | 75.04 | 71.58
2020-01-24 12:30 | 74.58 | 71.1
2020-01-24 13:00 | 75.19 | 71.74
2020-01-24 13:30 | 74.88 | 71.41
2020-01-24 14:00 | 74.94 | 71.46
2020-01-24 14:30 | 75.08 | 71.61
2020-01-24 15:00 | 75.69 | 72.24
2020-01-24 15:30 | 76.43 | 73.02
2020-01-24 16:00 | 77.99 | 74.67
2020-01-24 16:30 | 79.78 | 76.53
2020-01-24 17:00 | 79.14 | 75.84
2020-01-24 17:30 | 75.93 | 72.41
2020-01-24 18:00 | 72.74 | 68.98
2020-01-24 18:30 | 71.84 | 68.02
2020-01-24 19:00 | 71.82 | 68
2020-01-24 19:30 | 71.39 | 67.47
2020-01-24 20:00 | 69.5 | 65.54
2020-01-24 20:30 | 65.37 | 62.99
2020-01-24 21:00 | 63.47 | 61
2020-01-24 21:30 | 60.39 | 58.46
2020-01-24 22:00 | 55.88 | 54.91
2020-01-24 22:30 | 51.33 | 51.05
2020-01-24 23:00 | 48.78 | 48.49
2020-01-24 23:30 | 46.21 | 45.91
2020-01-25 | 44.52 | 44.21
2020-01-25 00:30 | 42.81 | 42.48
2020-01-25 01:00 | 41.58 | 41.24
2020-01-25 01:30 | 40.71 | 40.37
2020-01-25 02:00 | 39.9 | 39.54
2020-01-25 02:30 | 39.21 | 38.84
2020-01-25 03:00 | 38.58 | 38.23
2020-01-25 03:30 | 38.12 | 37.76
2020-01-25 04:00 | 37.73 | 37.37
2020-01-25 04:30 | 37.95 | 37.59
2020-01-25 05:00 | 38.27 | 37.92
2020-01-25 05:30 | 38.05 | 37.71
2020-01-25 06:00 | 37.74 | 37.4
2020-01-25 06:30 | 39.3 | 38.98
2020-01-25 07:00 | 40.4 | 40.08
2020-01-25 07:30 | 43 | 42.58
2020-01-25 08:00 | 44.14 | 43.68
2020-01-25 08:30 | 47.23 | 46.94
2020-01-25 09:00 | 48.3 | 47.91
2020-01-25 09:30 | 50.97 | 50.47
2020-01-25 10:00 | 50.95 | 50.43
2020-01-25 10:30 | 49.94 | 49.32
2020-01-25 11:00 | 48.96 | 48.25
2020-01-25 11:30 | 47.99 | 47.24
2020-01-25 12:00 | 47.57 | 46.84
2020-01-25 12:30 | 46.59 | 45.92
2020-01-25 13:00 | 49.36 | 48.75
2020-01-25 13:30 | 49.46 | 48.88
2020-01-25 14:00 | 51.7 | 51.17
2020-01-25 14:30 | 55.51 | 55.07
2020-01-25 15:00 | 56.15 | 55.75
2020-01-25 15:30 | 57.43 | 57.06
2020-01-25 16:00 | 57.34 | 57.04
2020-01-25 16:30 | 55.67 | 55.44
2020-01-25 17:00 | 54.55 | 54.31
2020-01-25 17:30 | 53.81 | 53.57
2020-01-25 18:00 | 52.47 | 52.22
2020-01-25 18:30 | 51.59 | 51.34
2020-01-25 19:00 | 51.87 | 51.62
2020-01-25 19:30 | 50.82 | 50.56
2020-01-25 20:00 | 49.59 | 49.32
2020-01-25 20:30 | 48.36 | 48.09
2020-01-25 21:00 | 46.89 | 46.61
2020-01-25 21:30 | 45.51 | 45.21
2020-01-25 22:00 | 44.01 | 43.7
2020-01-25 22:30 | 42.16 | 41.84
2020-01-25 23:00 | 40.46 | 40.12
2020-01-25 23:30 | 38.79 | 38.43
2020-01-26 | 37.32 | 36.94
2020-01-26 00:30 | 36.07 | 35.7
2020-01-26 01:00 | 35.28 | 34.9
2020-01-26 01:30 | 34.9 | 34.51
2020-01-26 02:00 | 34.45 | 34.06
2020-01-26 02:30 | 34.13 | 33.74
2020-01-26 03:00 | 33.82 | 33.42
2020-01-26 03:30 | 33.92 | 33.52
2020-01-26 04:00 | 33.54 | 33.14
2020-01-26 04:30 | 33.32 | 32.91
2020-01-26 05:00 | 33.16 | 32.75
2020-01-26 05:30 | 33.74 | 33.34
2020-01-26 06:00 | 33.87 | 33.46
2020-01-26 06:30 | 34.75 | 34.36
2020-01-26 07:00 | 35.68 | 35.3
2020-01-26 07:30 | 38.06 | 37.71
2020-01-26 08:00 | 40.44 | 40.12
2020-01-26 08:30 | 42.52 | 42.22
2020-01-26 09:00 | 42.88 | 42.58
2020-01-26 09:30 | 42.83 | 42.53
2020-01-26 10:00 | 43.88 | 43.55
2020-01-26 10:30 | 45.01 | 44.68
2020-01-26 11:00 | 41.87 | 41.55
2020-01-26 11:30 | 40.58 | 40.25
2020-01-26 12:00 | 39.51 | 39.17
2020-01-26 12:30 | 41.72 | 41.4
2020-01-26 13:00 | 45.81 | 45.52
2020-01-26 13:30 | 45.95 | 45.65
2020-01-26 14:00 | 43.41 | 43.09
2020-01-26 14:30 | 42.78 | 42.47
2020-01-26 15:00 | 42.18 | 41.86
2020-01-26 15:30 | 42.51 | 42.19
2020-01-26 16:00 | 43.1 | 42.78
2020-01-26 16:30 | 42.84 | 42.52
2020-01-26 17:00 | 42.5 | 42.18
2020-01-26 17:30 | 42.27 | 41.95
2020-01-26 18:00 | 43.23 | 42.91
2020-01-26 18:30 | 43.9 | 43.58
2020-01-26 19:00 | 44.6 | 44.3
2020-01-26 19:30 | 45.79 | 45.5
2020-01-26 20:00 | 45.37 | 45.07
2020-01-26 20:30 | 44.43 | 44.12
2020-01-26 21:00 | 43.45 | 43.14
2020-01-26 21:30 | 42.23 | 41.9
2020-01-26 22:00 | 41.11 | 40.77
2020-01-26 22:30 | 39.32 | 38.96
2020-01-26 23:00 | 37.81 | 37.44
2020-01-26 23:30 | 36.34 | 35.95
2020-01-27 | 35.07 | 34.69
2020-01-27 00:30 | 34.41 | 34.01
2020-01-27 01:00 | 33.38 | 32.97
2020-01-27 01:30 | 32.52 | 32.1
2020-01-27 02:00 | 31.98 | 31.56
2020-01-27 02:30 | 31.92 | 31.49
2020-01-27 03:00 | 31.95 | 31.52
2020-01-27 03:30 | 31.77 | 31.34
2020-01-27 04:00 | 31.35 | 30.91
2020-01-27 04:30 | 31.45 | 31.02
2020-01-27 05:00 | 31.87 | 31.45
2020-01-27 05:30 | 32.66 | 32.25
2020-01-27 06:00 | 32.69 | 32.27
2020-01-27 06:30 | 34.83 | 34.45
2020-01-27 07:00 | 35.11 | 34.73
2020-01-27 07:30 | 37.93 | 37.58
2020-01-27 08:00 | 40.99 | 40.57
2020-01-27 08:30 | 44.34 | 44.05
2020-01-27 09:00 | 44.85 | 44.57
2020-01-27 09:30 | 45.95 | 45.66
2020-01-27 10:00 | 45.24 | 44.95
2020-01-27 10:30 | 46.36 | 46.09
2020-01-27 11:00 | 44.83 | 44.55
2020-01-27 11:30 | 46.06 | 45.78
2020-01-27 12:00 | 45.43 | 45.15
2020-01-27 12:30 | 46.47 | 46.19
2020-01-27 13:00 | 49.03 | 48.77
2020-01-27 13:30 | 48.06 | 47.79
2020-01-27 14:00 | 48.39 | 48.12
2020-01-27 14:30 | 47.04 | 46.76
2020-01-27 15:00 | 46.59 | 46.31
2020-01-27 15:30 | 47.4 | 47.13
2020-01-27 16:00 | 47.91 | 47.64
2020-01-27 16:30 | 48.03 | 47.76
2020-01-27 17:00 | 49.11 | 48.85
2020-01-27 17:30 | 50.44 | 50.18
2020-01-27 18:00 | 50.79 | 50.53
2020-01-27 18:30 | 50.32 | 50.05
2020-01-27 19:00 | 50.31 | 50.05
2020-01-27 19:30 | 49.7 | 49.43
2020-01-27 20:00 | 48.23 | 47.96
2020-01-27 20:30 | 46.24 | 45.95
2020-01-27 21:00 | 44.68 | 44.37
2020-01-27 21:30 | 42.98 | 42.66
2020-01-27 22:00 | 40.84 | 40.5
2020-01-27 22:30 | 38.6 | 38.23
2020-01-27 23:00 | 36.86 | 36.49
2020-01-27 23:30 | 35.21 | 34.83
2020-01-28 | 33.97 | 33.58
2020-01-28 00:30 | 33.42 | 33.01
2020-01-28 01:00 | 32.59 | 32.17
2020-01-28 01:30 | 32.32 | 31.9
2020-01-28 02:00 | 31.87 | 31.44
2020-01-28 02:30 | 31.6 | 31.16
2020-01-28 03:00 | 31.38 | 30.94
2020-01-28 03:30 | 31.46 | 31.03
2020-01-28 04:00 | 31.99 | 31.56
2020-01-28 04:30 | 32.27 | 31.85
2020-01-28 05:00 | 33.55 | 33.15
2020-01-28 05:30 | 35.8 | 35.43
2020-01-28 06:00 | 38.24 | 37.91
2020-01-28 06:30 | 42.79 | 42.41
2020-01-28 07:00 | 47.93 | 47.23
2020-01-28 07:30 | 54.59 | 53.83
2020-01-28 08:00 | 57.96 | 57.66
2020-01-28 08:30 | 59.62 | 59.12
2020-01-28 09:00 | 61.54 | 60.94
2020-01-28 09:30 | 61.06 | 60.39
2020-01-28 10:00 | 62.23 | 61.44
2020-01-28 10:30 | 62.63 | 61.75
2020-01-28 11:00 | 61.61 | 60.63
2020-01-28 11:30 | 62.37 | 61.28
2020-01-28 12:00 | 61.47 | 60.27
2020-01-28 12:30 | 62.07 | 60.84
2020-01-28 13:00 | 63.97 | 62.8
2020-01-28 13:30 | 63.69 | 62.65
2020-01-28 14:00 | 59.61 | 58.54
2020-01-28 14:30 | 61.51 | 60.44
2020-01-28 15:00 | 63.11 | 62.13
2020-01-28 15:30 | 62.94 | 62.01
2020-01-28 16:00 | 62.44 | 61.51
2020-01-28 16:30 | 63.42 | 62.5
2020-01-28 17:00 | 62.38 | 61.43
2020-01-28 17:30 | 60.48 | 59.48
2020-01-28 18:00 | 59.39 | 58.36
2020-01-28 18:30 | 59.6 | 58.57
2020-01-28 19:00 | 59.9 | 58.91
2020-01-28 19:30 | 59.31 | 58.29
2020-01-28 20:00 | 57.59 | 56.55
2020-01-28 20:30 | 55.59 | 54.5
2020-01-28 21:00 | 53.53 | 52.38
2020-01-28 21:30 | 51.08 | 49.87
2020-01-28 22:00 | 48.18 | 46.87
2020-01-28 22:30 | 46.7 | 45.33
2020-01-28 23:00 | 44.8 | 43.36
2020-01-28 23:30 | 42.93 | 41.41
2020-01-29 | 40.3 | 38.68
2020-01-29 00:30 | 38.64 | 37.02
2020-01-29 01:00 | 37.74 | 36.05
2020-01-29 01:30 | 37.26 | 35.54
2020-01-29 02:00 | 36.69 | 34.94
2020-01-29 02:30 | 36.39 | 34.62
2020-01-29 03:00 | 35.92 | 34.12
2020-01-29 03:30 | 35.75 | 33.94
2020-01-29 04:00 | 35.73 | 33.92
2020-01-29 04:30 | 36.21 | 34.43
2020-01-29 05:00 | 37.25 | 35.54
2020-01-29 05:30 | 39.4 | 37.8
2020-01-29 06:00 | 41.16 | 39.64
2020-01-29 06:30 | 45.68 | 44.37
2020-01-29 07:00 | 49.99 | 48.8
2020-01-29 07:30 | 54.68 | 53.61
2020-01-29 08:00 | 58.88 | 57.92
2020-01-29 08:30 | 58.97 | 57.99
2020-01-29 09:00 | 60.3 | 59.29
2020-01-29 09:30 | 61.59 | 60.44
2020-01-29 10:00 | 64.86 | 63.25
2020-01-29 10:30 | 65.27 | 63.15
2020-01-29 11:00 | 66.11 | 64.03
2020-01-29 11:30 | 66.09 | 64.01
2020-01-29 12:00 | 66.41 | 64.35
2020-01-29 12:30 | 67.04 | 65
2020-01-29 13:00 | 68.57 | 66.59
2020-01-29 13:30 | 70.12 | 67.9
2020-01-29 14:00 | 71.45 | 67.78
2020-01-29 14:30 | 70.79 | 67.09
2020-01-29 15:00 | 71.66 | 68
2020-01-29 15:30 | 71.61 | 67.93
2020-01-29 16:00 | 73.78 | 70.22
2020-01-29 16:30 | 74.94 | 71.42
2020-01-29 17:00 | 74.78 | 71.21
2020-01-29 17:30 | 72.37 | 68.59
2020-01-29 18:00 | 71.06 | 67.16
2020-01-29 18:30 | 71.12 | 67.23
2020-01-29 19:00 | 71.78 | 67.94
2020-01-29 19:30 | 71.85 | 68.01
2020-01-29 20:00 | 69.63 | 65.68
2020-01-29 20:30 | 67.06 | 62.93
2020-01-29 21:00 | 64.55 | 60.19
2020-01-29 21:30 | 61.16 | 56.46
2020-01-29 22:00 | 57.94 | 52.87
2020-01-29 22:30 | 54.86 | 49.37
2020-01-29 23:00 | 50.55 | 46.69
2020-01-29 23:30 | 45.51 | 44.09
2020-01-30 | 43.65 | 42.16
2020-01-30 00:30 | 42.14 | 40.59
2020-01-30 01:00 | 41.1 | 39.54
2020-01-30 01:30 | 40.19 | 38.61
2020-01-30 02:00 | 39.78 | 38.17
2020-01-30 02:30 | 39.07 | 37.43
2020-01-30 03:00 | 38.76 | 37.11
2020-01-30 03:30 | 38.74 | 37.09
2020-01-30 04:00 | 38.77 | 37.12
2020-01-30 04:30 | 39.19 | 37.56
2020-01-30 05:00 | 40.24 | 38.67
2020-01-30 05:30 | 42.15 | 40.67
2020-01-30 06:00 | 44.32 | 42.93
2020-01-30 06:30 | 49.01 | 47.8
2020-01-30 07:00 | 53.19 | 52.07
2020-01-30 07:30 | 60.81 | 59.84
2020-01-30 08:00 | 62.82 | 61.87
2020-01-30 08:30 | 62.75 | 61.69
2020-01-30 09:00 | 70.79 | 67.54
2020-01-30 09:30 | 70.5 | 66.7
2020-01-30 10:00 | 68.75 | 64.76
2020-01-30 10:30 | 68.79 | 64.81
2020-01-30 11:00 | 71.08 | 67.3
2020-01-30 11:30 | 72.87 | 69.18
2020-01-30 12:00 | 69.97 | 66.1
2020-01-30 12:30 | 70.35 | 66.53
2020-01-30 13:00 | 69.44 | 65.57
2020-01-30 13:30 | 69.31 | 65.44
2020-01-30 14:00 | 69.42 | 65.58
2020-01-30 14:30 | 71.32 | 67.59
2020-01-30 15:00 | 71.88 | 68.17
2020-01-30 15:30 | 72.04 | 68.32
2020-01-30 16:00 | 74.45 | 70.87
2020-01-30 16:30 | 74.81 | 71.15
2020-01-30 17:00 | 74.29 | 70.59
2020-01-30 17:30 | 71.01 | 67.07
2020-01-30 18:00 | 70.7 | 66.72
2020-01-30 18:30 | 70.12 | 66.08
2020-01-30 19:00 | 70.09 | 66.12
2020-01-30 19:30 | 69.86 | 65.92
2020-01-30 20:00 | 67.94 | 63.85
2020-01-30 20:30 | 66.01 | 61.72
2020-01-30 21:00 | 63.64 | 59.13
2020-01-30 21:30 | 60.17 | 55.29
2020-01-30 22:00 | 56.8 | 51.47
2020-01-30 22:30 | 53.07 | 48.27
2020-01-30 23:00 | 49.02 | 45.73
2020-01-30 23:30 | 47.34 | 43.9
2020-01-31 | 45.6 | 41.99
2020-01-31 00:30 | 44.22 | 40.46
2020-01-31 01:00 | 42.27 | 39.55
2020-01-31 01:30 | 40.36 | 38.69
2020-01-31 02:00 | 39.54 | 37.83
2020-01-31 02:30 | 39.17 | 37.45
2020-01-31 03:00 | 38.58 | 36.89
2020-01-31 03:30 | 38.65 | 36.96
2020-01-31 04:00 | 38.4 | 36.69
2020-01-31 04:30 | 38.68 | 36.99
2020-01-31 05:00 | 39.65 | 38.01
2020-01-31 05:30 | 41.65 | 40.1
2020-01-31 06:00 | 43.55 | 42.1
2020-01-31 06:30 | 48.78 | 47.54
2020-01-31 07:00 | 53.84 | 52.7
2020-01-31 07:30 | 60.24 | 59.22
2020-01-31 08:00 | 61.84 | 60.89
2020-01-31 08:30 | 64.01 | 62.86
2020-01-31 09:00 | 65.65 | 63.57
2020-01-31 09:30 | 65.04 | 62.82
2020-01-31 10:00 | 65.48 | 63.28
2020-01-31 10:30 | 64.43 | 62.19
2020-01-31 11:00 | 65.04 | 62.84
2020-01-31 11:30 | 64.86 | 62.66
2020-01-31 12:00 | 64.93 | 62.72
2020-01-31 12:30 | 64.62 | 62.4
2020-01-31 13:00 | 64.99 | 62.79
2020-01-31 13:30 | 65.55 | 63.37
2020-01-31 14:00 | 65.77 | 63.57
2020-01-31 14:30 | 65.93 | 63.75
2020-01-31 15:00 | 65.91 | 63.72
2020-01-31 15:30 | 65.89 | 63.7
2020-01-31 16:00 | 66.88 | 64.7
2020-01-31 16:30 | 68.02 | 65.86
2020-01-31 17:00 | 68.52 | 66.36
2020-01-31 17:30 | 67.62 | 65.4
2020-01-31 18:00 | 65.07 | 62.79
2020-01-31 18:30 | 63.31 | 60.94
2020-01-31 19:00 | 63.33 | 60.97
2020-01-31 19:30 | 63.24 | 60.86
2020-01-31 20:00 | 61.81 | 59.36
2020-01-31 20:30 | 59.98 | 57.43
2020-01-31 21:00 | 58.91 | 56.29
2020-01-31 21:30 | 56.49 | 53.74
2020-01-31 22:00 | 58.07 | 55.41
2020-01-31 22:30 | 59.36 | 56.76
2020-01-31 23:00 | 52.16 | 49.13
2020-01-31 23:30 | 48.2 | 44.84
2020-02-01 | 46.14 | 42.59
2020-02-01 00:30 | 44.79 | 41.1
2020-02-01 01:00 | 43.69 | 39.89
2020-02-01 01:30 | 40.77 | 38.76
2020-02-01 02:00 | 39.76 | 38.06
2020-02-01 02:30 | 39.5 | 37.79
2020-02-01 03:00 | 38.99 | 37.25
2020-02-01 03:30 | 38.2 | 36.51
2020-02-01 04:00 | 37.9 | 36.16
2020-02-01 04:30 | 38.03 | 36.29
2020-02-01 05:00 | 38.24 | 36.52
2020-02-01 05:30 | 38.9 | 37.22
2020-02-01 06:00 | 38.64 | 36.94
2020-02-01 06:30 | 40.31 | 38.71
2020-02-01 07:00 | 41.71 | 40.19
2020-02-01 07:30 | 46.99 | 45.69
2020-02-01 08:00 | 52.43 | 51.27
2020-02-01 08:30 | 55.87 | 54.76
2020-02-01 09:00 | 54.3 | 53.19
2020-02-01 09:30 | 54.03 | 52.92
2020-02-01 10:00 | 52.71 | 51.58
2020-02-01 10:30 | 53.42 | 52.27
2020-02-01 11:00 | 49.99 | 48.77
2020-02-01 11:30 | 49.44 | 48.22
2020-02-01 12:00 | 49.99 | 48.77
2020-02-01 12:30 | 49.31 | 48.07
2020-02-01 13:00 | 46.53 | 45.21
2020-02-01 13:30 | 46.5 | 45.18
2020-02-01 14:00 | 47.06 | 45.75
2020-02-01 14:30 | 47.07 | 45.76
2020-02-01 15:00 | 47.79 | 46.5
2020-02-01 15:30 | 49.62 | 48.38
2020-02-01 16:00 | 51.52 | 50.34
2020-02-01 16:30 | 52.71 | 51.54
2020-02-01 17:00 | 55.17 | 54.06
2020-02-01 17:30 | 57.83 | 56.77
2020-02-01 18:00 | 58.44 | 57.39
2020-02-01 18:30 | 58.05 | 56.99
2020-02-01 19:00 | 58.25 | 57.19
2020-02-01 19:30 | 59.05 | 58.02
2020-02-01 20:00 | 58.15 | 57.1
2020-02-01 20:30 | 56.22 | 55.12
2020-02-01 21:00 | 54.46 | 53.31
2020-02-01 21:30 | 52.75 | 51.55
2020-02-01 22:00 | 50.86 | 49.61
2020-02-01 22:30 | 48.68 | 47.36
2020-02-01 23:00 | 46.77 | 45.38
2020-02-01 23:30 | 44.73 | 43.27
2020-02-02 | 42.82 | 41.28
2020-02-02 00:30 | 41.3 | 39.7
2020-02-02 01:00 | 40.2 | 38.55
2020-02-02 01:30 | 39.6 | 37.91
2020-02-02 02:00 | 38.96 | 37.23
2020-02-02 02:30 | 38.31 | 36.55
2020-02-02 03:00 | 37.38 | 35.63
2020-02-02 03:30 | 37.03 | 35.26
2020-02-02 04:00 | 36.69 | 34.9
2020-02-02 04:30 | 36.87 | 35.09
2020-02-02 05:00 | 36.84 | 35.06
2020-02-02 05:30 | 37.24 | 35.48
2020-02-02 06:00 | 36.65 | 34.85
2020-02-02 06:30 | 37.36 | 35.61
2020-02-02 07:00 | 37.73 | 36
2020-02-02 07:30 | 39.15 | 37.5
2020-02-02 08:00 | 39.64 | 38.04
2020-02-02 08:30 | 41.23 | 39.66
2020-02-02 09:00 | 42.57 | 41.07
2020-02-02 09:30 | 43.74 | 42.29
2020-02-02 10:00 | 44.64 | 43.24
2020-02-02 10:30 | 45.18 | 43.8
2020-02-02 11:00 | 45.33 | 43.96
2020-02-02 11:30 | 45.43 | 44.07
2020-02-02 12:00 | 45.8 | 44.45
2020-02-02 12:30 | 46.18 | 44.84
2020-02-02 13:00 | 46.5 | 45.17
2020-02-02 13:30 | 46.99 | 45.67
2020-02-02 14:00 | 48.07 | 46.79
2020-02-02 14:30 | 49.01 | 47.74
2020-02-02 15:00 | 50.28 | 49.07
2020-02-02 15:30 | 52 | 50.82
2020-02-02 16:00 | 53.63 | 52.49
2020-02-02 16:30 | 55.43 | 54.33
2020-02-02 17:00 | 56.58 | 55.51
2020-02-02 17:30 | 58.03 | 56.98
2020-02-02 18:00 | 60.01 | 59.01
2020-02-02 18:30 | 60.45 | 59.46
2020-02-02 19:00 | 60.89 | 59.85
2020-02-02 19:30 | 61.63 | 60.61
2020-02-02 20:00 | 60.04 | 58.99
2020-02-02 20:30 | 57.46 | 56.34
2020-02-02 21:00 | 54.91 | 53.72
2020-02-02 21:30 | 52.07 | 50.8
2020-02-02 22:00 | 49.78 | 48.43
2020-02-02 22:30 | 46.41 | 45.57
2020-02-02 23:00 | 43.41 | 43.07
2020-02-02 23:30 | 40.93 | 40.58
2020-02-03 | 39.18 | 38.82
2020-02-03 00:30 | 37.99 | 37.62
2020-02-03 01:00 | 36.63 | 36.26
2020-02-03 01:30 | 35.68 | 35.3
2020-02-03 02:00 | 35.16 | 34.77
2020-02-03 02:30 | 34.58 | 34.19
2020-02-03 03:00 | 34.18 | 33.78
2020-02-03 03:30 | 34.24 | 33.84
2020-02-03 04:00 | 33.79 | 33.39
2020-02-03 04:30 | 34.08 | 33.68
2020-02-03 05:00 | 35.11 | 34.73
2020-02-03 05:30 | 38.33 | 37.99
2020-02-03 06:00 | 40.28 | 39.95
2020-02-03 06:30 | 45.1 | 44.58
2020-02-03 07:00 | 49.7 | 48.93
2020-02-03 07:30 | 55.25 | 54.83
2020-02-03 08:00 | 58.53 | 57.89
2020-02-03 08:30 | 59.67 | 58.66
2020-02-03 09:00 | 60.96 | 59.68
2020-02-03 09:30 | 62.95 | 61.6
2020-02-03 10:00 | 62.13 | 60.7
2020-02-03 10:30 | 62.37 | 60.77
2020-02-03 11:00 | 63.4 | 61.36
2020-02-03 11:30 | 63.77 | 61.56
2020-02-03 12:00 | 63.97 | 61.78
2020-02-03 12:30 | 65.75 | 63.25
2020-02-03 13:00 | 66.23 | 63.85
2020-02-03 13:30 | 66.75 | 64.4
2020-02-03 14:00 | 67.75 | 65.43
2020-02-03 14:30 | 68.04 | 65.73
2020-02-03 15:00 | 68.72 | 66.44
2020-02-03 15:30 | 69.59 | 67.33
2020-02-03 16:00 | 71.38 | 69.18
2020-02-03 16:30 | 72.41 | 70.23
2020-02-03 17:00 | 72.63 | 70.43
2020-02-03 17:30 | 70.94 | 68.79
2020-02-03 18:00 | 68.12 | 67.03
2020-02-03 18:30 | 65.32 | 64.26
2020-02-03 19:00 | 64.56 | 63.64
2020-02-03 19:30 | 64.26 | 63.43
2020-02-03 20:00 | 62.57 | 61.58
2020-02-03 20:30 | 60.35 | 59.13
2020-02-03 21:00 | 57.99 | 56.49
2020-02-03 21:30 | 57.85 | 56.21
2020-02-03 22:00 | 55.31 | 53.36
2020-02-03 22:30 | 55.78 | 53.61
2020-02-03 23:00 | 49.41 | 46.54
2020-02-03 23:30 | 44.72 | 42.35
2020-02-04 | 40.23 | 39.75
2020-02-04 00:30 | 38.71 | 38.18
2020-02-04 01:00 | 37.48 | 36.94
2020-02-04 01:30 | 36.65 | 36.1
2020-02-04 02:00 | 35.99 | 35.43
2020-02-04 02:30 | 35.43 | 34.86
2020-02-04 03:00 | 34.72 | 34.14
2020-02-04 03:30 | 34.31 | 33.72
2020-02-04 04:00 | 33.98 | 33.38
2020-02-04 04:30 | 34.34 | 33.75
2020-02-04 05:00 | 35.34 | 34.76
2020-02-04 05:30 | 37.68 | 37.14
2020-02-04 06:00 | 39.22 | 38.7
2020-02-04 06:30 | 43.56 | 43.06
2020-02-04 07:00 | 48.48 | 47.52
2020-02-04 07:30 | 53.89 | 53.21
2020-02-04 08:00 | 56.73 | 56.17
2020-02-04 08:30 | 59.33 | 58.38
2020-02-04 09:00 | 62.21 | 60.9
2020-02-04 09:30 | 63.9 | 61.99
2020-02-04 10:00 | 65.11 | 62.91
2020-02-04 10:30 | 65.47 | 63.3
2020-02-04 11:00 | 65.42 | 63.25
2020-02-04 11:30 | 65.25 | 63.09
2020-02-04 12:00 | 65.9 | 63.77
2020-02-04 12:30 | 66.89 | 64.79
2020-02-04 13:00 | 65.84 | 63.7
2020-02-04 13:30 | 68.37 | 66.28
2020-02-04 14:00 | 69.69 | 67.56
2020-02-04 14:30 | 72.09 | 70.05
2020-02-04 15:00 | 70.65 | 68.77
2020-02-04 15:30 | 71.23 | 69.54
2020-02-04 16:00 | 72.5 | 71.38
2020-02-04 16:30 | 72.78 | 71.88
2020-02-04 17:00 | 73.24 | 72.22
2020-02-04 17:30 | 71.7 | 70.66
2020-02-04 18:00 | 70.75 | 69.14
2020-02-04 18:30 | 70.32 | 68.05
2020-02-04 19:00 | 70.45 | 68.19
2020-02-04 19:30 | 70.31 | 68.05
2020-02-04 20:00 | 68.47 | 66.14
2020-02-04 20:30 | 65.92 | 63.28
2020-02-04 21:00 | 64.27 | 59.94
2020-02-04 21:30 | 61.44 | 56.58
2020-02-04 22:00 | 60.24 | 53
2020-02-04 22:30 | 59.67 | 49.45
2020-02-04 23:00 | 57.83 | 46.88
2020-02-04 23:30 | 56.29 | 44.91
2020-02-05 | 54.95 | 43.13
2020-02-05 00:30 | 53.75 | 41.6
2020-02-05 01:00 | 52.89 | 40.45
2020-02-05 01:30 | 52.12 | 39.4
2020-02-05 02:00 | 51.72 | 38.83
2020-02-05 02:30 | 51.25 | 38.15
2020-02-05 03:00 | 50.45 | 37.18
2020-02-05 03:30 | 50.13 | 36.66
2020-02-05 04:00 | 49.79 | 36.18
2020-02-05 04:30 | 49.93 | 36.39
2020-02-05 05:00 | 50.23 | 36.77
2020-02-05 05:30 | 52.38 | 39.78
2020-02-05 06:00 | 54.14 | 42.14
2020-02-05 06:30 | 57.82 | 46.87
2020-02-05 07:00 | 60.63 | 50.48
2020-02-05 07:30 | 65.42 | 56.18
2020-02-05 08:00 | 70.14 | 61.64
2020-02-05 08:30 | 71.19 | 62.92
2020-02-05 09:00 | 73.1 | 65.11
2020-02-05 09:30 | 72.31 | 64.27
2020-02-05 10:00 | 72.84 | 64.88
2020-02-05 10:30 | 73.23 | 65.35
2020-02-05 11:00 | 73.87 | 66.08
2020-02-05 11:30 | 74.11 | 66.35
2020-02-05 12:00 | 74.45 | 66.76
2020-02-05 12:30 | 72.42 | 64.52
2020-02-05 13:00 | 74.75 | 67.12
2020-02-05 13:30 | 76.56 | 69.16
2020-02-05 14:00 | 76.89 | 69.6
2020-02-05 14:30 | 78.75 | 71.66
2020-02-05 15:00 | 77.58 | 70.38
2020-02-05 15:30 | 71.41 | 63.37
2020-02-05 16:00 | 81.38 | 74.63
2020-02-05 16:30 | 79.59 | 72.62
2020-02-05 17:00 | 75.63 | 68.15
2020-02-05 17:30 | 71.7 | 63.67
2020-02-05 18:00 | 71.24 | 63.07
2020-02-05 18:30 | 70.77 | 62.63
2020-02-05 19:00 | 71.04 | 62.92
2020-02-05 19:30 | 71.47 | 63.4
2020-02-05 20:00 | 69.97 | 61.68
2020-02-05 20:30 | 67.82 | 59.14
2020-02-05 21:00 | 65.64 | 56.54
2020-02-05 21:30 | 62.81 | 53.14
2020-02-05 22:00 | 60.27 | 50.04
2020-02-05 22:30 | 57.69 | 46.72
2020-02-05 23:00 | 55.81 | 44.28
2020-02-05 23:30 | 54.05 | 41.98
2020-02-06 | 52.47 | 39.94
2020-02-06 00:30 | 51.73 | 38.8
2020-02-06 01:00 | 50.57 | 37.31
2020-02-06 01:30 | 50.15 | 36.72
2020-02-06 02:00 | 49.84 | 36.33
2020-02-06 02:30 | 49.26 | 35.44
2020-02-06 03:00 | 49.05 | 35.16
2020-02-06 03:30 | 48.77 | 34.71
2020-02-06 04:00 | 48.63 | 34.52
2020-02-06 04:30 | 48.77 | 34.73
2020-02-06 05:00 | 49.44 | 35.7
2020-02-06 05:30 | 51 | 37.89
2020-02-06 06:00 | 52.36 | 39.76
2020-02-06 06:30 | 56.16 | 44.73
2020-02-06 07:00 | 59.82 | 49.42
2020-02-06 07:30 | 64.66 | 55.33
2020-02-06 08:00 | 66.91 | 57.88
2020-02-06 08:30 | 68.79 | 60.09
2020-02-06 09:00 | 69.66 | 61.14
2020-02-06 09:30 | 70.53 | 62.16
2020-02-06 10:00 | 71.68 | 63.48
2020-02-06 10:30 | 73.13 | 65.15
2020-02-06 11:00 | 71.09 | 62.83
2020-02-06 11:30 | 73.65 | 65.78
2020-02-06 12:00 | 76.2 | 68.68
2020-02-06 12:30 | 72.99 | 65.03
2020-02-06 13:00 | 70.86 | 62.59
2020-02-06 13:30 | 65.87 | 63.29
2020-02-06 14:00 | 65.3 | 65.29
2020-02-06 14:30 | 66.6 | 66.59
2020-02-06 15:00 | 66.27 | 66.26
2020-02-06 15:30 | 67.78 | 67.74
2020-02-06 16:00 | 71.19 | 71.13
2020-02-06 16:30 | 69.3 | 69.16
2020-02-06 17:00 | 69.72 | 69.44
2020-02-06 17:30 | 69.41 | 68.86
2020-02-06 18:00 | 68.31 | 67.87
2020-02-06 18:30 | 68.17 | 67.67
2020-02-06 19:00 | 68.27 | 67.72
2020-02-06 19:30 | 68.18 | 67.67
2020-02-06 20:00 | 66.35 | 65.69
2020-02-06 20:30 | 64.11 | 63.26
2020-02-06 21:00 | 62.08 | 61.09
2020-02-06 21:30 | 58.28 | 56.95
2020-02-06 22:00 | 53.91 | 52.08
2020-02-06 22:30 | 51.17 | 48.84
2020-02-06 23:00 | 48.22 | 46.13
2020-02-06 23:30 | 45.53 | 44.04
2020-02-07 | 43.34 | 41.75
2020-02-07 00:30 | 42.04 | 40.4
2020-02-07 01:00 | 40.74 | 39.05
2020-02-07 01:30 | 39.51 | 37.7
2020-02-07 02:00 | 39.3 | 37.52
2020-02-07 02:30 | 38.75 | 36.95
2020-02-07 03:00 | 38 | 36.14
2020-02-07 03:30 | 37.78 | 35.93
2020-02-07 04:00 | 37.07 | 35.17
2020-02-07 04:30 | 37.3 | 35.4
2020-02-07 05:00 | 38.47 | 36.64
2020-02-07 05:30 | 47.34 | 46.22
2020-02-07 06:00 | 50.5 | 49.76
2020-02-07 06:30 | 55.94 | 54.7
2020-02-07 07:00 | 58.63 | 56.86
2020-02-07 07:30 | 66.54 | 65.63
2020-02-07 08:00 | 63.11 | 62.18
2020-02-07 08:30 | 65.81 | 64.85
2020-02-07 09:00 | 68.1 | 66.96
2020-02-07 09:30 | 71.5 | 69.6
2020-02-07 10:00 | 72.96 | 71.06
2020-02-07 10:30 | 72.72 | 70.82
2020-02-07 11:00 | 73.25 | 71.34
2020-02-07 11:30 | 75.76 | 72.41
2020-02-07 12:00 | 74.78 | 71.22
2020-02-07 12:30 | 77.05 | 73.64
2020-02-07 13:00 | 78.35 | 74.98
2020-02-07 13:30 | 76.39 | 72.91
2020-02-07 14:00 | 76.78 | 73.31
2020-02-07 14:30 | 72.13 | 68.41
2020-02-07 15:00 | 71.37 | 67.6
2020-02-07 15:30 | 72.33 | 68.58
2020-02-07 16:00 | 73.83 | 70.16
2020-02-07 16:30 | 74.75 | 71.13
2020-02-07 17:00 | 75.39 | 71.79
2020-02-07 17:30 | 74 | 70.32
2020-02-07 18:00 | 71.73 | 67.91
2020-02-07 18:30 | 70.63 | 66.73
2020-02-07 19:00 | 69.72 | 65.73
2020-02-07 19:30 | 69.51 | 65.51
2020-02-07 20:00 | 68.59 | 64.52
2020-02-07 20:30 | 66.63 | 62.41
2020-02-07 21:00 | 64.29 | 59.82
2020-02-07 21:30 | 62.24 | 57.58
2020-02-07 22:00 | 59.62 | 54.67
2020-02-07 22:30 | 56.78 | 51.5
2020-02-07 23:00 | 54.7 | 49.15
2020-02-07 23:30 | 50.1 | 46.55
2020-02-08 | 47.7 | 44.3
2020-02-08 00:30 | 46.12 | 42.58
2020-02-08 01:00 | 44.63 | 40.93
2020-02-08 01:30 | 43.27 | 40.08
2020-02-08 02:00 | 40.43 | 38.77
2020-02-08 02:30 | 40.1 | 38.43
2020-02-08 03:00 | 39.37 | 37.74
2020-02-08 03:30 | 38.82 | 37.13
2020-02-08 04:00 | 37.69 | 35.94
2020-02-08 04:30 | 37.59 | 35.85
2020-02-08 05:00 | 38.3 | 36.59
2020-02-08 05:30 | 39.23 | 37.58
2020-02-08 06:00 | 39.29 | 37.62
2020-02-08 06:30 | 40.73 | 39.16
2020-02-08 07:00 | 42.3 | 40.82
2020-02-08 07:30 | 45.47 | 44.12
2020-02-08 08:00 | 45.22 | 43.83
2020-02-08 08:30 | 50.08 | 48.87
2020-02-08 09:00 | 52 | 50.83
2020-02-08 09:30 | 52.17 | 51.01
2020-02-08 10:00 | 52.93 | 51.8
2020-02-08 10:30 | 52.78 | 51.66
2020-02-08 11:00 | 56.78 | 55.74
2020-02-08 11:30 | 55.4 | 54.34
2020-02-08 12:00 | 52.04 | 50.9
2020-02-08 12:30 | 53.89 | 52.8
2020-02-08 13:00 | 53.24 | 52.12
2020-02-08 13:30 | 53.18 | 52.06
2020-02-08 14:00 | 53.03 | 51.9
2020-02-08 14:30 | 54.06 | 52.95
2020-02-08 15:00 | 54.41 | 53.31
2020-02-08 15:30 | 58.93 | 57.93
2020-02-08 16:00 | 60.59 | 59.62
2020-02-08 16:30 | 64.21 | 63.29
2020-02-08 17:00 | 61.27 | 60.29
2020-02-08 17:30 | 60.83 | 59.85
2020-02-08 18:00 | 61.1 | 60.12
2020-02-08 18:30 | 61.55 | 60.57
2020-02-08 19:00 | 61.08 | 60.1
2020-02-08 19:30 | 61.07 | 60.09
2020-02-08 20:00 | 59.86 | 58.85
2020-02-08 20:30 | 57.92 | 56.86
2020-02-08 21:00 | 55.58 | 54.47
2020-02-08 21:30 | 53.65 | 52.49
2020-02-08 22:00 | 51.51 | 50.28
2020-02-08 22:30 | 49.05 | 47.75
2020-02-08 23:00 | 47.21 | 45.84
2020-02-08 23:30 | 45.49 | 44.06
2020-02-09 | 43.85 | 42.35
2020-02-09 00:30 | 42.35 | 40.78
2020-02-09 01:00 | 39.29 | 37.64
2020-02-09 01:30 | 37.21 | 35.45
2020-02-09 02:00 | 36.01 | 34.18
2020-02-09 02:30 | 35.64 | 33.79
2020-02-09 03:00 | 34.76 | 32.84
2020-02-09 03:30 | 34.3 | 32.35
2020-02-09 04:00 | 34.19 | 32.23
2020-02-09 04:30 | 34.14 | 32.18
2020-02-09 05:00 | 34.09 | 32.14
2020-02-09 05:30 | 34.16 | 32.21
2020-02-09 06:00 | 33.75 | 31.75
2020-02-09 06:30 | 34.84 | 32.93
2020-02-09 07:00 | 35.29 | 33.41
2020-02-09 07:30 | 36.05 | 34.23
2020-02-09 08:00 | 36.79 | 35.05
2020-02-09 08:30 | 39.75 | 38.07
2020-02-09 09:00 | 41.4 | 39.84
2020-02-09 09:30 | 42.29 | 40.78
2020-02-09 10:00 | 43.43 | 41.98
2020-02-09 10:30 | 45.62 | 44.26
2020-02-09 11:00 | 46.74 | 45.42
2020-02-09 11:30 | 47.43 | 46.13
2020-02-09 12:00 | 48.47 | 47.2
2020-02-09 12:30 | 50.54 | 49.34
2020-02-09 13:00 | 53.17 | 52.04
2020-02-09 13:30 | 55.4 | 54.33
2020-02-09 14:00 | 55.57 | 54.49
2020-02-09 14:30 | 56.7 | 55.65
2020-02-09 15:00 | 59.53 | 58.55
2020-02-09 15:30 | 59.21 | 58.21
2020-02-09 16:00 | 61.03 | 60.06
2020-02-09 16:30 | 59.38 | 58.38
2020-02-09 17:00 | 61.46 | 60.5
2020-02-09 17:30 | 63.74 | 62.81
2020-02-09 18:00 | 65.5 | 64.6
2020-02-09 18:30 | 65.55 | 64.65
2020-02-09 19:00 | 65.3 | 64.4
2020-02-09 19:30 | 65.47 | 64.57
2020-02-09 20:00 | 63.83 | 62.89
2020-02-09 20:30 | 61.1 | 60.1
2020-02-09 21:00 | 58.08 | 57.02
2020-02-09 21:30 | 54.67 | 53.52
2020-02-09 22:00 | 51.58 | 50.34
2020-02-09 22:30 | 48.38 | 47.04
2020-02-09 23:00 | 45.81 | 44.38
2020-02-09 23:30 | 43.72 | 42.21
2020-02-10 | 42.19 | 40.62
2020-02-10 00:30 | 41.02 | 39.39
2020-02-10 01:00 | 39.93 | 38.25
2020-02-10 01:30 | 39.14 | 37.42
2020-02-10 02:00 | 38.68 | 36.94
2020-02-10 02:30 | 38.35 | 36.58
2020-02-10 03:00 | 37.73 | 36
2020-02-10 03:30 | 37.19 | 35.43
2020-02-10 04:00 | 37.32 | 35.56
2020-02-10 04:30 | 37.66 | 35.92
2020-02-10 05:00 | 38.64 | 36.97
2020-02-10 05:30 | 41.11 | 39.57
2020-02-10 06:00 | 43.86 | 42.44
2020-02-10 06:30 | 48.85 | 47.63
2020-02-10 07:00 | 53.73 | 52.52
2020-02-10 07:30 | 60.81 | 59.73
2020-02-10 08:00 | 60.16 | 59.18
2020-02-10 08:30 | 53.95 | 52.66
2020-02-10 09:00 | 52.76 | 51.34
2020-02-10 09:30 | 53.62 | 52.04
2020-02-10 10:00 | 53.45 | 51.8
2020-02-10 10:30 | 56.08 | 54.37
2020-02-10 11:00 | 56.9 | 55.19
2020-02-10 11:30 | 58.46 | 56.79
2020-02-10 12:00 | 57.18 | 55.45
2020-02-10 12:30 | 56.42 | 54.61
2020-02-10 13:00 | 56.76 | 54.89
2020-02-10 13:30 | 57.29 | 55.41
2020-02-10 14:00 | 59.82 | 57.81
2020-02-10 14:30 | 63.37 | 61.45
2020-02-10 15:00 | 62.58 | 60.76
2020-02-10 15:30 | 59.47 | 57.8
2020-02-10 16:00 | 63.35 | 61.81
2020-02-10 16:30 | 63.09 | 61.67
2020-02-10 17:00 | 61.26 | 60.03
2020-02-10 17:30 | 58.7 | 56.83
2020-02-10 18:00 | 64.93 | 61.99
2020-02-10 18:30 | 69.92 | 67.23
2020-02-10 19:00 | 69.98 | 67.31
2020-02-10 19:30 | 69.54 | 66.85
2020-02-10 20:00 | 67.28 | 64.48
2020-02-10 20:30 | 64.36 | 61.4
2020-02-10 21:00 | 61.68 | 58.52
2020-02-10 21:30 | 58.69 | 55.33
2020-02-10 22:00 | 55.15 | 51.49
2020-02-10 22:30 | 52.1 | 48.18
2020-02-10 23:00 | 45.18 | 44.88
2020-02-10 23:30 | 42.81 | 42.81
2020-02-11 | 40.7 | 40.7
2020-02-11 00:30 | 39.56 | 39.55
2020-02-11 01:00 | 39.04 | 39.03
2020-02-11 01:30 | 38.29 | 38.27
2020-02-11 02:00 | 37.9 | 37.88
2020-02-11 02:30 | 37.69 | 37.66
2020-02-11 03:00 | 36.66 | 36.62
2020-02-11 03:30 | 36.63 | 36.6
2020-02-11 04:00 | 35.95 | 35.91
2020-02-11 04:30 | 35.56 | 35.51
2020-02-11 05:00 | 37 | 36.98
2020-02-11 05:30 | 39.19 | 39.19
2020-02-11 06:00 | 40.25 | 40.25
2020-02-11 06:30 | 43.54 | 43.52
2020-02-11 07:00 | 46.97 | 46.85
2020-02-11 07:30 | 51.25 | 50.86
2020-02-11 08:00 | 56.08 | 55.25
2020-02-11 08:30 | 59.78 | 58.53
2020-02-11 09:00 | 59.1 | 57.54
2020-02-11 09:30 | 59.83 | 58.03
2020-02-11 10:00 | 59.63 | 57.64
2020-02-11 10:30 | 60.62 | 58.63
2020-02-11 11:00 | 60.88 | 58.76
2020-02-11 11:30 | 62.16 | 59.99
2020-02-11 12:00 | 63.13 | 60.88
2020-02-11 12:30 | 63.33 | 60.95
2020-02-11 13:00 | 63.24 | 60.91
2020-02-11 13:30 | 63.54 | 61.19
2020-02-11 14:00 | 63.96 | 61.65
2020-02-11 14:30 | 64.8 | 62.53
2020-02-11 15:00 | 65.91 | 63.76
2020-02-11 15:30 | 66.91 | 64.9
2020-02-11 16:00 | 71.8 | 70
2020-02-11 16:30 | 73.83 | 71.95
2020-02-11 17:00 | 71.55 | 69.57
2020-02-11 17:30 | 71.35 | 69.34
2020-02-11 18:00 | 70.56 | 68.52
2020-02-11 18:30 | 69.99 | 67.95
2020-02-11 19:00 | 69.68 | 67.63
2020-02-11 19:30 | 69.15 | 67.07
2020-02-11 20:00 | 66.85 | 64.66
2020-02-11 20:30 | 63.96 | 61.62
2020-02-11 21:00 | 60.94 | 58.44
2020-02-11 21:30 | 57.3 | 54.59
2020-02-11 22:00 | 53.59 | 50.63
2020-02-11 22:30 | 48.53 | 47.07
2020-02-11 23:00 | 45.78 | 44.34
2020-02-11 23:30 | 43.05 | 42
2020-02-12 | 40.45 | 40.09
2020-02-12 00:30 | 39.36 | 39
2020-02-12 01:00 | 38.32 | 37.95
2020-02-12 01:30 | 37.56 | 37.18
2020-02-12 02:00 | 36.8 | 36.46
2020-02-12 02:30 | 36.07 | 36.01
2020-02-12 03:00 | 35.74 | 35.67
2020-02-12 03:30 | 35.47 | 35.4
2020-02-12 04:00 | 35.39 | 35.32
2020-02-12 04:30 | 35.56 | 35.49
2020-02-12 05:00 | 36.51 | 36.47
2020-02-12 05:30 | 38.86 | 38.85
2020-02-12 06:00 | 40.55 | 40.55
2020-02-12 06:30 | 44.46 | 44.42
2020-02-12 07:00 | 47.31 | 47.19
2020-02-12 07:30 | 51.68 | 51.24
2020-02-12 08:00 | 56.04 | 55.25
2020-02-12 08:30 | 57.56 | 56.49
2020-02-12 09:00 | 57.21 | 55.84
2020-02-12 09:30 | 59.43 | 57.87
2020-02-12 10:00 | 59.28 | 57.52
2020-02-12 10:30 | 57.5 | 55.57
2020-02-12 11:00 | 58.88 | 56.77
2020-02-12 11:30 | 60.92 | 58.71
2020-02-12 12:00 | 62.29 | 60.04
2020-02-12 12:30 | 64.15 | 61.72
2020-02-12 13:00 | 65.32 | 62.95
2020-02-12 13:30 | 66.3 | 63.88
2020-02-12 14:00 | 67.55 | 65.11
2020-02-12 14:30 | 68.79 | 66.4
2020-02-12 15:00 | 74.08 | 71.9
2020-02-12 15:30 | 71.69 | 69.7
2020-02-12 16:00 | 71.29 | 69.06
2020-02-12 16:30 | 75.83 | 73.79
2020-02-12 17:00 | 71.88 | 69.84
2020-02-12 17:30 | 63.98 | 62.91
2020-02-12 18:00 | 62.03 | 61.19
2020-02-12 18:30 | 61.19 | 60.11
2020-02-12 19:00 | 59.14 | 57.86
2020-02-12 19:30 | 57.04 | 55.43
2020-02-12 20:00 | 55.53 | 53.78
2020-02-12 20:30 | 53.71 | 51.69
2020-02-12 21:00 | 51.59 | 49.34
2020-02-12 21:30 | 48.63 | 45.77
2020-02-12 22:00 | 46.1 | 42.74
2020-02-12 22:30 | 43.68 | 39.64
2020-02-12 23:00 | 42.5 | 37.36
2020-02-12 23:30 | 38.28 | 31.51
2020-02-13 | 40.45 | 33.75
2020-02-13 00:30 | 39.69 | 33.19
2020-02-13 01:00 | 37.29 | 31.99
2020-02-13 01:30 | 35.62 | 31.38
2020-02-13 02:00 | 35.21 | 30.91
2020-02-13 02:30 | 34.85 | 30.51
2020-02-13 03:00 | 34.64 | 30.25
2020-02-13 03:30 | 34.5 | 30.08
2020-02-13 04:00 | 34.35 | 29.9
2020-02-13 04:30 | 34.56 | 30.14
2020-02-13 05:00 | 35.31 | 30.99
2020-02-13 05:30 | 36.89 | 32.79
2020-02-13 06:00 | 38.23 | 34.29
2020-02-13 06:30 | 40.14 | 37.73
2020-02-13 07:00 | 42.33 | 40.74
2020-02-13 07:30 | 46.4 | 45.85
2020-02-13 08:00 | 49.12 | 48.5
2020-02-13 08:30 | 51.88 | 50.96
2020-02-13 09:00 | 53.87 | 52.55
2020-02-13 09:30 | 55.77 | 54.17
2020-02-13 10:00 | 56.13 | 54.42
2020-02-13 10:30 | 56.22 | 54.51
2020-02-13 11:00 | 56.99 | 55.01
2020-02-13 11:30 | 58.83 | 56.73
2020-02-13 12:00 | 60.04 | 57.99
2020-02-13 12:30 | 62.11 | 60.01
2020-02-13 13:00 | 62.09 | 59.94
2020-02-13 13:30 | 62.55 | 60.43
2020-02-13 14:00 | 64.33 | 62.15
2020-02-13 14:30 | 64.33 | 62.15
2020-02-13 15:00 | 66.34 | 64.3
2020-02-13 15:30 | 69.56 | 67.66
2020-02-13 16:00 | 73.94 | 72.22
2020-02-13 16:30 | 73.52 | 71.63
2020-02-13 17:00 | 71.46 | 69.47
2020-02-13 17:30 | 68.91 | 66.82
2020-02-13 18:00 | 67.63 | 65.48
2020-02-13 18:30 | 68.65 | 66.55
2020-02-13 19:00 | 68.55 | 66.44
2020-02-13 19:30 | 67.5 | 65.34
2020-02-13 20:00 | 65.22 | 62.97
2020-02-13 20:30 | 62.19 | 59.78
2020-02-13 21:00 | 59.17 | 56.58
2020-02-13 21:30 | 54.83 | 51.97
2020-02-13 22:00 | 49.25 | 47.56
2020-02-13 22:30 | 45.75 | 44.3
2020-02-13 23:00 | 42.48 | 41.73
2020-02-13 23:30 | 39.69 | 39.33
2020-02-14 | 38.03 | 37.65
2020-02-14 00:30 | 36.95 | 36.56
2020-02-14 01:00 | 35.69 | 35.6
2020-02-14 01:30 | 35.57 | 35.5
2020-02-14 02:00 | 35.09 | 35.02
2020-02-14 02:30 | 34.49 | 34.4
2020-02-14 03:00 | 34.12 | 34.02
2020-02-14 03:30 | 33.73 | 33.63
2020-02-14 04:00 | 33.57 | 33.46
2020-02-14 04:30 | 33.65 | 33.56
2020-02-14 05:00 | 34.19 | 34.12
2020-02-14 05:30 | 35.95 | 35.92
2020-02-14 06:00 | 37.04 | 37.02
2020-02-14 06:30 | 41.14 | 41.12
2020-02-14 07:00 | 44.02 | 43.94
2020-02-14 07:30 | 49.49 | 49.11
2020-02-14 08:00 | 53.05 | 52.29
2020-02-14 08:30 | 55.52 | 54.36
2020-02-14 09:00 | 57.79 | 56.35
2020-02-14 09:30 | 60.36 | 58.63
2020-02-14 10:00 | 61.18 | 59.41
2020-02-14 10:30 | 62.31 | 60.47
2020-02-14 11:00 | 63.65 | 61.65
2020-02-14 11:30 | 63.09 | 61.07
2020-02-14 12:00 | 64.23 | 62.12
2020-02-14 12:30 | 64.85 | 62.74
2020-02-14 13:00 | 66.28 | 64.14
2020-02-14 13:30 | 67.65 | 65.44
2020-02-14 14:00 | 68.27 | 67.33
2020-02-14 14:30 | 71.95 | 71.07
2020-02-14 15:00 | 69 | 68.07
2020-02-14 15:30 | 70.4 | 69.49
2020-02-14 16:00 | 73.92 | 73.06
2020-02-14 16:30 | 74.79 | 73.93
2020-02-14 17:00 | 72.5 | 71.6
2020-02-14 17:30 | 71.15 | 70.21
2020-02-14 18:00 | 68.78 | 67.79
2020-02-14 18:30 | 65.4 | 64.47
2020-02-14 19:00 | 63.5 | 62.48
2020-02-14 19:30 | 62.37 | 61.28
2020-02-14 20:00 | 60.64 | 59.38
2020-02-14 20:30 | 57.94 | 56.35
2020-02-14 21:00 | 55.89 | 54.07
2020-02-14 21:30 | 52.45 | 49.68
2020-02-14 22:00 | 51.33 | 47.05
2020-02-14 22:30 | 49.5 | 44.27
2020-02-14 23:00 | 47.07 | 41.35
2020-02-14 23:30 | 45.06 | 39.43
2020-02-15 | 43.67 | 37.81
2020-02-15 00:30 | 42.74 | 36.68
2020-02-15 01:00 | 41.83 | 35.61
2020-02-15 01:30 | 40.78 | 34.35
2020-02-15 02:00 | 40.24 | 33.71
2020-02-15 02:30 | 39.97 | 33.36
2020-02-15 03:00 | 39.46 | 32.61
2020-02-15 03:30 | 39.17 | 32.39
2020-02-15 04:00 | 39.06 | 32.23
2020-02-15 04:30 | 39.14 | 32.34
2020-02-15 05:00 | 39.26 | 32.51
2020-02-15 05:30 | 39.81 | 33.18
2020-02-15 06:00 | 39.8 | 33.19
2020-02-15 06:30 | 40.92 | 34.53
2020-02-15 07:00 | 40.05 | 36.08
2020-02-15 07:30 | 42.71 | 39.16
2020-02-15 08:00 | 44.87 | 41.57
2020-02-15 08:30 | 47.38 | 44.24
2020-02-15 09:00 | 49.2 | 46.4
2020-02-15 09:30 | 51.16 | 49.79
2020-02-15 10:00 | 51.84 | 50.5
2020-02-15 10:30 | 52.3 | 51.35
2020-02-15 11:00 | 53.76 | 53.04
2020-02-15 11:30 | 53.62 | 52.86
2020-02-15 12:00 | 54.79 | 54.04
2020-02-15 12:30 | 55.6 | 54.92
2020-02-15 13:00 | 55.34 | 54.73
2020-02-15 13:30 | 54.92 | 54.33
2020-02-15 14:00 | 55.95 | 55.36
2020-02-15 14:30 | 58.68 | 58.09
2020-02-15 15:00 | 58.99 | 58.41
2020-02-15 15:30 | 64.93 | 64.46
2020-02-15 16:00 | 64.3 | 63.89
2020-02-15 16:30 | 58.19 | 57.88
2020-02-15 17:00 | 52.85 | 52.61
2020-02-15 17:30 | 51.01 | 50.75
2020-02-15 18:00 | 50.56 | 50.3
2020-02-15 18:30 | 49.38 | 49.12
2020-02-15 19:00 | 49.81 | 49.55
2020-02-15 19:30 | 49.62 | 49.36
2020-02-15 20:00 | 48.45 | 48.18
2020-02-15 20:30 | 47.08 | 46.8
2020-02-15 21:00 | 45.75 | 45.46
2020-02-15 21:30 | 43.95 | 43.64
2020-02-15 22:00 | 42.48 | 42.16
2020-02-15 22:30 | 40.44 | 40.1
2020-02-15 23:00 | 38.72 | 38.36
2020-02-15 23:30 | 37.28 | 36.9
2020-02-16 | 35.51 | 35.1
2020-02-16 00:30 | 34.21 | 33.79
2020-02-16 01:00 | 33.26 | 32.82
2020-02-16 01:30 | 32.47 | 32.02
2020-02-16 02:00 | 31.87 | 31.41
2020-02-16 02:30 | 31.63 | 31.17
2020-02-16 03:00 | 30.65 | 30.6
2020-02-16 03:30 | 30.62 | 30.61
2020-02-16 04:00 | 30.26 | 30.25
2020-02-16 04:30 | 30.28 | 30.27
2020-02-16 05:00 | 30.37 | 30.37
2020-02-16 05:30 | 30.59 | 30.58
2020-02-16 06:00 | 30.23 | 30.22
2020-02-16 06:30 | 31.11 | 31.11
2020-02-16 07:00 | 31.65 | 31.64
2020-02-16 07:30 | 33.76 | 33.69
2020-02-16 08:00 | 35.41 | 35.24
2020-02-16 08:30 | 37.47 | 37.14
2020-02-16 09:00 | 40.14 | 40.07
2020-02-16 09:30 | 41.57 | 41.47
2020-02-16 10:00 | 43.13 | 42.96
2020-02-16 10:30 | 45.64 | 45.38
2020-02-16 11:00 | 46.42 | 46.11
2020-02-16 11:30 | 47.04 | 46.67
2020-02-16 12:00 | 47.99 | 47.61
2020-02-16 12:30 | 49.38 | 49.01
2020-02-16 13:00 | 50.01 | 49.6
2020-02-16 13:30 | 50.78 | 50.38
2020-02-16 14:00 | 51.63 | 51.22
2020-02-16 14:30 | 53.69 | 53.29
2020-02-16 15:00 | 54.09 | 53.69
2020-02-16 15:30 | 55.29 | 54.94
2020-02-16 16:00 | 57.25 | 56.91
2020-02-16 16:30 | 59.34 | 59.02
2020-02-16 17:00 | 60.79 | 60.49
2020-02-16 17:30 | 62.3 | 62.07
2020-02-16 18:00 | 63.37 | 63.14
2020-02-16 18:30 | 62.64 | 62.44
2020-02-16 19:00 | 62.29 | 62.1
2020-02-16 19:30 | 62.23 | 62.03
2020-02-16 20:00 | 60.6 | 60.43
2020-02-16 20:30 | 58.1 | 57.97
2020-02-16 21:00 | 55.1 | 55.02
2020-02-16 21:30 | 52.27 | 52.22
2020-02-16 22:00 | 49.48 | 49.46
2020-02-16 22:30 | 46.47 | 46.47
2020-02-16 23:00 | 43.6 | 43.6
2020-02-16 23:30 | 40.99 | 40.98
2020-02-17 | 39.23 | 39.21
2020-02-17 00:30 | 38.23 | 38.2
2020-02-17 01:00 | 37.25 | 37.21
2020-02-17 01:30 | 36.35 | 36.29
2020-02-17 02:00 | 35.71 | 35.65
2020-02-17 02:30 | 35.45 | 35.37
2020-02-17 03:00 | 34.98 | 34.89
2020-02-17 03:30 | 34.87 | 34.79
2020-02-17 04:00 | 34.57 | 34.47
2020-02-17 04:30 | 34.79 | 34.71
2020-02-17 05:00 | 35.42 | 35.37
2020-02-17 05:30 | 37.39 | 37.37
2020-02-17 06:00 | 39.05 | 39.05
2020-02-17 06:30 | 42.6 | 42.58
2020-02-17 07:00 | 46.21 | 46.09
2020-02-17 07:30 | 52.75 | 52.28
2020-02-17 08:00 | 56.91 | 56
2020-02-17 08:30 | 59.62 | 58.26
2020-02-17 09:00 | 61.66 | 59.95
2020-02-17 09:30 | 63.61 | 61.49
2020-02-17 10:00 | 62.91 | 60.27
2020-02-17 10:30 | 62.46 | 59.99
2020-02-17 11:00 | 62.83 | 60.39
2020-02-17 11:30 | 63.23 | 60.81
2020-02-17 12:00 | 63.93 | 61.55
2020-02-17 12:30 | 64.19 | 61.82
2020-02-17 13:00 | 65.07 | 62.73
2020-02-17 13:30 | 66.09 | 63.8
2020-02-17 14:00 | 70.7 | 68.59
2020-02-17 14:30 | 70.58 | 68.44
2020-02-17 15:00 | 67.78 | 65.55
2020-02-17 15:30 | 67.1 | 64.84
2020-02-17 16:00 | 68.48 | 66.26
2020-02-17 16:30 | 70.9 | 68.78
2020-02-17 17:00 | 72.28 | 70.18
2020-02-17 17:30 | 71.94 | 69.81
2020-02-17 18:00 | 69.73 | 67.5
2020-02-17 18:30 | 68.38 | 66.88
2020-02-17 19:00 | 67.57 | 66.6
2020-02-17 19:30 | 67.28 | 66.29
2020-02-17 20:00 | 65.4 | 64.36
2020-02-17 20:30 | 62.14 | 61.01
2020-02-17 21:00 | 59.22 | 57.87
2020-02-17 21:30 | 53.82 | 53.74
2020-02-17 22:00 | 49.97 | 49.94
2020-02-17 22:30 | 46.65 | 46.64
2020-02-17 23:00 | 44.16 | 44.16
2020-02-17 23:30 | 41.8 | 41.8
2020-02-18 | 39.74 | 39.73
2020-02-18 00:30 | 38.5 | 38.47
2020-02-18 01:00 | 37.58 | 37.55
2020-02-18 01:30 | 36.84 | 36.8
2020-02-18 02:00 | 36.02 | 35.97
2020-02-18 02:30 | 35.41 | 35.35
2020-02-18 03:00 | 34.52 | 34.46
2020-02-18 03:30 | 34.45 | 34.4
2020-02-18 04:00 | 34.41 | 34.35
2020-02-18 04:30 | 34.38 | 34.32
2020-02-18 05:00 | 35.36 | 35.26
2020-02-18 05:30 | 37.62 | 37.46
2020-02-18 06:00 | 39.66 | 39.44
2020-02-18 06:30 | 42.86 | 42.46
2020-02-18 07:00 | 46.32 | 45.69
2020-02-18 07:30 | 51.91 | 51.26
2020-02-18 08:00 | 55.66 | 54.85
2020-02-18 08:30 | 57.34 | 56.21
2020-02-18 09:00 | 61.31 | 59.91
2020-02-18 09:30 | 60.73 | 59.28
2020-02-18 10:00 | 56.66 | 55.17
2020-02-18 10:30 | 56.03 | 54.44
2020-02-18 11:00 | 58.5 | 56.77
2020-02-18 11:30 | 55.72 | 53.81
2020-02-18 12:00 | 57.8 | 55.69
2020-02-18 12:30 | 59.33 | 57.27
2020-02-18 13:00 | 59.87 | 57.92
2020-02-18 13:30 | 61.19 | 59.16
2020-02-18 14:00 | 62.08 | 59.97
2020-02-18 14:30 | 63.27 | 61.19
2020-02-18 15:00 | 64.71 | 62.59
2020-02-18 15:30 | 65.78 | 63.9
2020-02-18 16:00 | 67.07 | 65.36
2020-02-18 16:30 | 68.66 | 67.1
2020-02-18 17:00 | 70.48 | 69.14
2020-02-18 17:30 | 68.83 | 67.88
2020-02-18 18:00 | 66.91 | 66.04
2020-02-18 18:30 | 65.02 | 64.12
2020-02-18 19:00 | 65.06 | 64.17
2020-02-18 19:30 | 64.27 | 63.36
2020-02-18 20:00 | 62 | 61.04
2020-02-18 20:30 | 59.19 | 58.17
2020-02-18 21:00 | 56.46 | 55.37
2020-02-18 21:30 | 52.82 | 51.63
2020-02-18 22:00 | 54.34 | 53.2
2020-02-18 22:30 | 55.06 | 53.91
2020-02-18 23:00 | 47.03 | 45.65
2020-02-18 23:30 | 42.98 | 41.44
2020-02-19 | 39.39 | 38.94
2020-02-19 00:30 | 37.89 | 37.51
2020-02-19 01:00 | 37.13 | 36.74
2020-02-19 01:30 | 36.49 | 36.1
2020-02-19 02:00 | 36.02 | 35.62
2020-02-19 02:30 | 35.8 | 35.39
2020-02-19 03:00 | 35.28 | 34.91
2020-02-19 03:30 | 35.02 | 34.63
2020-02-19 04:00 | 34.98 | 34.59
2020-02-19 04:30 | 35.07 | 34.69
2020-02-19 05:00 | 35.98 | 35.62
2020-02-19 05:30 | 38.11 | 37.77
2020-02-19 06:00 | 39.46 | 39.13
2020-02-19 06:30 | 42.93 | 42.56
2020-02-19 07:00 | 42.34 | 41.37
2020-02-19 07:30 | 44.78 | 43.35
2020-02-19 08:00 | 45.2 | 44.13
2020-02-19 08:30 | 46.63 | 46.03
2020-02-19 09:00 | 49.01 | 48.64
2020-02-19 09:30 | 49.88 | 49.59
2020-02-19 10:00 | 49.85 | 49.56
2020-02-19 10:30 | 50.01 | 49.75
2020-02-19 11:00 | 50.31 | 50.08
2020-02-19 11:30 | 50.7 | 50.52
2020-02-19 12:00 | 50.54 | 50.36
2020-02-19 12:30 | 49.17 | 48.98
2020-02-19 13:00 | 50.72 | 50.58
2020-02-19 13:30 | 50.11 | 49.96
2020-02-19 14:00 | 50.97 | 50.86
2020-02-19 14:30 | 54.2 | 54.14
2020-02-19 15:00 | 56.72 | 56.67
2020-02-19 15:30 | 56.14 | 56.07
2020-02-19 16:00 | 57.3 | 57.22
2020-02-19 16:30 | 58.22 | 58.12
2020-02-19 17:00 | 59.39 | 59.26
2020-02-19 17:30 | 58.49 | 58.15
2020-02-19 18:00 | 57.44 | 56.77
2020-02-19 18:30 | 56.78 | 55.79
2020-02-19 19:00 | 55.42 | 54.37
2020-02-19 19:30 | 79.33 | 78.17
2020-02-19 20:00 | 77.81 | 77.36
2020-02-19 20:30 | 75.9 | 75.71
2020-02-19 21:00 | 71.71 | 71.37
2020-02-19 21:30 | 67.77 | 67.26
2020-02-19 22:00 | 63.47 | 62.68
2020-02-19 22:30 | 59.61 | 58.54
2020-02-19 23:00 | 55.55 | 55.3
2020-02-19 23:30 | 52.91 | 52.73
2020-02-20 | 50.64 | 50.5
2020-02-20 00:30 | 48.95 | 48.86
2020-02-20 01:00 | 47.96 | 47.88
2020-02-20 01:30 | 46.99 | 46.92
2020-02-20 02:00 | 46.15 | 46.1
2020-02-20 02:30 | 45.13 | 45.08
2020-02-20 03:00 | 44.55 | 44.52
2020-02-20 03:30 | 44.03 | 44.01
2020-02-20 04:00 | 43.86 | 43.84
2020-02-20 04:30 | 44.24 | 44.22
2020-02-20 05:00 | 45.72 | 45.67
2020-02-20 05:30 | 48.35 | 48.25
2020-02-20 06:00 | 51.03 | 50.86
2020-02-20 06:30 | 56.92 | 56.45
2020-02-20 07:00 | 62.37 | 61.61
2020-02-20 07:30 | 69.29 | 68.33
2020-02-20 08:00 | 73.91 | 72.31
2020-02-20 08:30 | 75.53 | 75.37
2020-02-20 09:00 | 76.4 | 76.33
2020-02-20 09:30 | 78.8 | 78.68
2020-02-20 10:00 | 80.1 | 79.9
2020-02-20 10:30 | 80.38 | 80.15
2020-02-20 11:00 | 81.41 | 81.11
2020-02-20 11:30 | 82.66 | 82.23
2020-02-20 12:00 | 83.02 | 82.86
2020-02-20 12:30 | 83.06 | 82.97
2020-02-20 13:00 | 83.68 | 83.6
2020-02-20 13:30 | 84.31 | 84.21
2020-02-20 14:00 | 86.12 | 86
2020-02-20 14:30 | 87.1 | 86.97
2020-02-20 15:00 | 86.85 | 86.74
2020-02-20 15:30 | 87 | 86.94
2020-02-20 16:00 | 89.49 | 89.47
2020-02-20 16:30 | 88.29 | 88.29
2020-02-20 17:00 | 89.15 | 89.12
2020-02-20 17:30 | 86.04 | 85.79
2020-02-20 18:00 | 85.61 | 85.19
2020-02-20 18:30 | 84.78 | 84.18
2020-02-20 19:00 | 79.82 | 79.27
2020-02-20 19:30 | 84.26 | 83.59
2020-02-20 20:00 | 81.45 | 80.6
2020-02-20 20:30 | 77.76 | 76.96
2020-02-20 21:00 | 73.91 | 73.65
2020-02-20 21:30 | 69.15 | 68.71
2020-02-20 22:00 | 64.13 | 63.38
2020-02-20 22:30 | 60.08 | 59.41
2020-02-20 23:00 | 56.84 | 56.61
2020-02-20 23:30 | 54.04 | 53.87
2020-02-21 | 51.52 | 51.4
2020-02-21 00:30 | 49.76 | 49.66
2020-02-21 01:00 | 48.28 | 48.2
2020-02-21 01:30 | 47.44 | 47.37
2020-02-21 02:00 | 46.28 | 46.24
2020-02-21 02:30 | 45.71 | 45.67
2020-02-21 03:00 | 45.2 | 45.18
2020-02-21 03:30 | 44.83 | 44.81
2020-02-21 04:00 | 44.69 | 44.67
2020-02-21 04:30 | 45.18 | 45.15
2020-02-21 05:00 | 46.73 | 46.67
2020-02-21 05:30 | 49.89 | 49.73
2020-02-21 06:00 | 52.53 | 52.28
2020-02-21 06:30 | 57.89 | 57.31
2020-02-21 07:00 | 63.75 | 63.2
2020-02-21 07:30 | 70.64 | 69.61
2020-02-21 08:00 | 74.82 | 73.57
2020-02-21 08:30 | 78.29 | 76.89
2020-02-21 09:00 | 78.03 | 77.45
2020-02-21 09:30 | 80.23 | 80.22
2020-02-21 10:00 | 78.77 | 78.77
2020-02-21 10:30 | 81.24 | 81.23
2020-02-21 11:00 | 82.9 | 82.88
2020-02-21 11:30 | 78.96 | 78.95
2020-02-21 12:00 | 84.66 | 84.61
2020-02-21 12:30 | 83.22 | 83.2
2020-02-21 13:00 | 80.16 | 80.16
2020-02-21 13:30 | 81.07 | 81.06
2020-02-21 14:00 | 81.23 | 81.22
2020-02-21 14:30 | 78.88 | 78.87
2020-02-21 15:00 | 80.82 | 80.81
2020-02-21 15:30 | 81.42 | 81.41
2020-02-21 16:00 | 82.64 | 82.6
2020-02-21 16:30 | 83.1 | 83.01
2020-02-21 17:00 | 83.82 | 83.63
2020-02-21 17:30 | 82.12 | 81.7
2020-02-21 18:00 | 79.17 | 79.04
2020-02-21 18:30 | 77.89 | 77.74
2020-02-21 19:00 | 77.69 | 77.54
2020-02-21 19:30 | 77.5 | 77.34
2020-02-21 20:00 | 75.15 | 74.92
2020-02-21 20:30 | 72.54 | 72.21
2020-02-21 21:00 | 70.57 | 70.15
2020-02-21 21:30 | 67.62 | 67.03
2020-02-21 22:00 | 64.89 | 64.07
2020-02-21 22:30 | 62.24 | 61.16
2020-02-21 23:00 | 59.58 | 58.21
2020-02-21 23:30 | 57.18 | 55.53
2020-02-22 | 54.53 | 53.22
2020-02-22 00:30 | 51.71 | 51.63
2020-02-22 01:00 | 50.51 | 50.44
2020-02-22 01:30 | 49.71 | 49.65
2020-02-22 02:00 | 48.65 | 48.59
2020-02-22 02:30 | 47.32 | 47.29
2020-02-22 03:00 | 46.32 | 46.3
2020-02-22 03:30 | 46.13 | 46.11
2020-02-22 04:00 | 45.43 | 45.42
2020-02-22 04:30 | 45.96 | 45.96
2020-02-22 05:00 | 46.03 | 46.03
2020-02-22 05:30 | 46.88 | 46.87
2020-02-22 06:00 | 47.4 | 47.38
2020-02-22 06:30 | 49.29 | 49.21
2020-02-22 07:00 | 51.26 | 51.1
2020-02-22 07:30 | 55.01 | 54.71
2020-02-22 08:00 | 58.14 | 57.66
2020-02-22 08:30 | 60.88 | 60.16
2020-02-22 09:00 | 60.91 | 59.97
2020-02-22 09:30 | 61.2 | 60.11
2020-02-22 10:00 | 59.17 | 57.99
2020-02-22 10:30 | 60.72 | 59.4
2020-02-22 11:00 | 62.93 | 61.48
2020-02-22 11:30 | 66.67 | 65.29
2020-02-22 12:00 | 64.74 | 63.37
2020-02-22 12:30 | 65.77 | 64.63
2020-02-22 13:00 | 66.03 | 65.02
2020-02-22 13:30 | 61.37 | 60.38
2020-02-22 14:00 | 60.87 | 59.89
2020-02-22 14:30 | 66.62 | 65.77
2020-02-22 15:00 | 65.87 | 65.08
2020-02-22 15:30 | 67.09 | 66.37
2020-02-22 16:00 | 66.9 | 66.29
2020-02-22 16:30 | 65.63 | 65.19
2020-02-22 17:00 | 62.22 | 61.9
2020-02-22 17:30 | 60.98 | 60.77
2020-02-22 18:00 | 61.09 | 60.92
2020-02-22 18:30 | 60.36 | 60.22
2020-02-22 19:00 | 60.13 | 59.96
2020-02-22 19:30 | 59.06 | 58.9
2020-02-22 20:00 | 57.73 | 57.59
2020-02-22 20:30 | 55.22 | 55.13
2020-02-22 21:00 | 53.31 | 53.24
2020-02-22 21:30 | 51.47 | 51.43
2020-02-22 22:00 | 50.1 | 50.07
2020-02-22 22:30 | 48.49 | 48.48
2020-02-22 23:00 | 47.11 | 47.11
2020-02-22 23:30 | 45.37 | 45.37
2020-02-23 | 44.33 | 44.33
2020-02-23 00:30 | 43.15 | 43.15
2020-02-23 01:00 | 42.18 | 42.17
2020-02-23 01:30 | 41.35 | 41.34
2020-02-23 02:00 | 40.56 | 40.54
2020-02-23 02:30 | 40.1 | 40.07
2020-02-23 03:00 | 39.4 | 39.34
2020-02-23 03:30 | 38.96 | 38.89
2020-02-23 04:00 | 38.67 | 38.6
2020-02-23 04:30 | 39.02 | 38.95
2020-02-23 05:00 | 39.21 | 39.12
2020-02-23 05:30 | 39.86 | 39.75
2020-02-23 06:00 | 40.17 | 40.05
2020-02-23 06:30 | 41.19 | 41.06
2020-02-23 07:00 | 41.62 | 41.48
2020-02-23 07:30 | 42.04 | 41.85
2020-02-23 08:00 | 46.32 | 45.98
2020-02-23 08:30 | 47.36 | 47.15
2020-02-23 09:00 | 48.61 | 48.49
2020-02-23 09:30 | 47.98 | 47.8
2020-02-23 10:00 | 52.21 | 52.01
2020-02-23 10:30 | 53.88 | 53.63
2020-02-23 11:00 | 54.13 | 53.83
2020-02-23 11:30 | 54.4 | 54.11
2020-02-23 12:00 | 54.54 | 54.26
2020-02-23 12:30 | 55.93 | 55.67
2020-02-23 13:00 | 55.67 | 55.45
2020-02-23 13:30 | 53.74 | 53.53
2020-02-23 14:00 | 54.43 | 54.24
2020-02-23 14:30 | 55.79 | 55.64
2020-02-23 15:00 | 53.93 | 53.82
2020-02-23 15:30 | 51.02 | 50.92
2020-02-23 16:00 | 54.78 | 54.67
2020-02-23 16:30 | 56.57 | 56.47
2020-02-23 17:00 | 57.34 | 57.25
2020-02-23 17:30 | 56.72 | 56.66
2020-02-23 18:00 | 56.83 | 56.79
2020-02-23 18:30 | 56.44 | 56.4
2020-02-23 19:00 | 56.62 | 56.56
2020-02-23 19:30 | 55.78 | 55.74
2020-02-23 20:00 | 53.99 | 53.96
2020-02-23 20:30 | 52.24 | 52.22
2020-02-23 21:00 | 50.79 | 50.78
2020-02-23 21:30 | 48.58 | 48.57
2020-02-23 22:00 | 46.9 | 46.9
2020-02-23 22:30 | 45.05 | 45.05
2020-02-23 23:00 | 43.08 | 43.07
2020-02-23 23:30 | 41.19 | 41.13
2020-02-24 | 39.98 | 39.91
2020-02-24 00:30 | 39.32 | 39.25
2020-02-24 01:00 | 38.77 | 38.7
2020-02-24 01:30 | 38.27 | 38.21
2020-02-24 02:00 | 37.8 | 37.75
2020-02-24 02:30 | 37.56 | 37.52
2020-02-24 03:00 | 37.73 | 37.69
2020-02-24 03:30 | 38.17 | 38.12
2020-02-24 04:00 | 38.17 | 38.11
2020-02-24 04:30 | 39.22 | 39.15
2020-02-24 05:00 | 40.75 | 40.63
2020-02-24 05:30 | 43.5 | 43.27
2020-02-24 06:00 | 46.98 | 46.57
2020-02-24 06:30 | 52.44 | 51.71
2020-02-24 07:00 | 58.66 | 57.43
2020-02-24 07:30 | 65.79 | 64.85
2020-02-24 08:00 | 69.46 | 68.59
2020-02-24 08:30 | 70.36 | 69.2
2020-02-24 09:00 | 71.8 | 70.42
2020-02-24 09:30 | 73.71 | 72.19
2020-02-24 10:00 | 73.11 | 71.54
2020-02-24 10:30 | 70.51 | 68.76
2020-02-24 11:00 | 71.99 | 70.03
2020-02-24 11:30 | 71.42 | 71.08
2020-02-24 12:00 | 72.99 | 72.98
2020-02-24 12:30 | 72.93 | 72.92
2020-02-24 13:00 | 69.01 | 69
2020-02-24 13:30 | 68.98 | 68.98
2020-02-24 14:00 | 71.4 | 71.4
2020-02-24 14:30 | 71.26 | 71.26
2020-02-24 15:00 | 71.09 | 71.09
2020-02-24 15:30 | 71.74 | 71.74
2020-02-24 16:00 | 70.31 | 70.24
2020-02-24 16:30 | 70.01 | 69.83
2020-02-24 17:00 | 69.99 | 69.64
2020-02-24 17:30 | 68.99 | 68.31
2020-02-24 18:00 | 68.37 | 67.7
2020-02-24 18:30 | 67.51 | 66.9
2020-02-24 19:00 | 68.81 | 68.29
2020-02-24 19:30 | 67.59 | 67
2020-02-24 20:00 | 65.16 | 64.39
2020-02-24 20:30 | 62.69 | 61.74
2020-02-24 21:00 | 60.37 | 59.3
2020-02-24 21:30 | 58 | 56.65
2020-02-24 22:00 | 54.68 | 52.99
2020-02-24 22:30 | 51.92 | 49.63
2020-02-24 23:00 | 50.07 | 47.06
2020-02-24 23:30 | 48.4 | 45.38
2020-02-25 | 46.32 | 43.16
2020-02-25 00:30 | 44.99 | 41.62
2020-02-25 01:00 | 44.11 | 40.72
2020-02-25 01:30 | 43.31 | 39.84
2020-02-25 02:00 | 42.53 | 39
2020-02-25 02:30 | 42.34 | 38.79
2020-02-25 03:00 | 41.61 | 37.99
2020-02-25 03:30 | 41.43 | 37.78
2020-02-25 04:00 | 41.64 | 38.02
2020-02-25 04:30 | 42.32 | 38.76
2020-02-25 05:00 | 43.51 | 40.03
2020-02-25 05:30 | 46.22 | 43
2020-02-25 06:00 | 49.03 | 46
2020-02-25 06:30 | 52.77 | 51.2
2020-02-25 07:00 | 58.6 | 57.13
2020-02-25 07:30 | 64.18 | 63.03
2020-02-25 08:00 | 66.68 | 65.66
2020-02-25 08:30 | 69.97 | 68.54
2020-02-25 09:00 | 70.66 | 68.99
2020-02-25 09:30 | 71.82 | 70.07
2020-02-25 10:00 | 69.91 | 68.08
2020-02-25 10:30 | 69.57 | 67.47
2020-02-25 11:00 | 74.43 | 72.23
2020-02-25 11:30 | 76.59 | 74.3
2020-02-25 12:00 | 74.63 | 72.3
2020-02-25 12:30 | 76.18 | 73.94
2020-02-25 13:00 | 77.81 | 75.67
2020-02-25 13:30 | 74.51 | 72.55
2020-02-25 14:00 | 51.93 | 50.53
2020-02-25 14:30 | 55.21 | 54.09
2020-02-25 15:00 | 75.93 | 73.64
2020-02-25 15:30 | 77.8 | 75.76
2020-02-25 16:00 | 78.84 | 77.18
2020-02-25 16:30 | 75.9 | 74.62
2020-02-25 17:00 | 74.64 | 73.75
2020-02-25 17:30 | 72.13 | 71.3
2020-02-25 18:00 | 70.76 | 69.9
2020-02-25 18:30 | 70.22 | 69.38
2020-02-25 19:00 | 71.28 | 70.47
2020-02-25 19:30 | 69.7 | 68.85
2020-02-25 20:00 | 67.38 | 66.5
2020-02-25 20:30 | 64.56 | 63.63
2020-02-25 21:00 | 62.23 | 61.24
2020-02-25 21:30 | 59.16 | 58.11
2020-02-25 22:00 | 56.12 | 54.99
2020-02-25 22:30 | 52.5 | 51.26
2020-02-25 23:00 | 48.97 | 48.46
2020-02-25 23:30 | 46.61 | 46.32
2020-02-26 | 44.26 | 43.94
2020-02-26 00:30 | 43.22 | 42.9
2020-02-26 01:00 | 41.87 | 41.83
2020-02-26 01:30 | 41.34 | 41.1
2020-02-26 02:00 | 41.19 | 40.95
2020-02-26 02:30 | 40.3 | 40.11
2020-02-26 03:00 | 39.59 | 39.42
2020-02-26 03:30 | 39.65 | 39.49
2020-02-26 04:00 | 39.05 | 38.9
2020-02-26 04:30 | 39.36 | 39.21
2020-02-26 05:00 | 40.68 | 40.48
2020-02-26 05:30 | 43.5 | 43.18
2020-02-26 06:00 | 47.1 | 46.59
2020-02-26 06:30 | 52.58 | 51.69
2020-02-26 07:00 | 58.54 | 57.1
2020-02-26 07:30 | 65.47 | 64.23
2020-02-26 08:00 | 66.5 | 65.41
2020-02-26 08:30 | 66.92 | 65.39
2020-02-26 09:00 | 68.68 | 66.7
2020-02-26 09:30 | 69.81 | 67.71
2020-02-26 10:00 | 70.18 | 67.94
2020-02-26 10:30 | 72.54 | 70.14
2020-02-26 11:00 | 76.11 | 73.44
2020-02-26 11:30 | 74.25 | 72.74
2020-02-26 12:00 | 71.65 | 71.52
2020-02-26 12:30 | 72.46 | 72.42
2020-02-26 13:00 | 74.72 | 74.67
2020-02-26 13:30 | 75.71 | 75.66
2020-02-26 14:00 | 76.44 | 76.36
2020-02-26 14:30 | 78.17 | 78.08
2020-02-26 15:00 | 78.71 | 78.65
2020-02-26 15:30 | 82.32 | 82.3
2020-02-26 16:00 | 80.6 | 80.59
2020-02-26 16:30 | 80.2 | 80.19
2020-02-26 17:00 | 76.99 | 76.89
2020-02-26 17:30 | 74.46 | 74.1
2020-02-26 18:00 | 74.91 | 74.3
2020-02-26 18:30 | 74.42 | 73.54
2020-02-26 19:00 | 75.05 | 74.15
2020-02-26 19:30 | 73.42 | 72.46
2020-02-26 20:00 | 71.2 | 70.07
2020-02-26 20:30 | 68.66 | 67.02
2020-02-26 21:00 | 66.68 | 64.47
2020-02-26 21:30 | 64.77 | 61
2020-02-26 22:00 | 61.69 | 57.16
2020-02-26 22:30 | 60.47 | 53.84
2020-02-26 23:00 | 58.22 | 51.27
2020-02-26 23:30 | 56.16 | 48.84
2020-02-27 | 54.22 | 46.59
2020-02-27 00:30 | 52.94 | 45.01
2020-02-27 01:00 | 52.46 | 43.87
2020-02-27 01:30 | 50.93 | 42.65
2020-02-27 02:00 | 50.44 | 42.02
2020-02-27 02:30 | 50.19 | 41.72
2020-02-27 03:00 | 49.56 | 40.68
2020-02-27 03:30 | 49.08 | 40.43
2020-02-27 04:00 | 49.15 | 40.5
2020-02-27 04:30 | 49.49 | 40.91
2020-02-27 05:00 | 50.56 | 42.18
2020-02-27 05:30 | 52.61 | 44.66
2020-02-27 06:00 | 54.99 | 47.49
2020-02-27 06:30 | 57.75 | 52.92
2020-02-27 07:00 | 60.76 | 58.47
2020-02-27 07:30 | 66.28 | 65.34
2020-02-27 08:00 | 67.91 | 67.6
2020-02-27 08:30 | 69.17 | 68.85
2020-02-27 09:00 | 69.46 | 69.16
2020-02-27 09:30 | 70.98 | 70.69
2020-02-27 10:00 | 72.11 | 71.8
2020-02-27 10:30 | 75 | 74.62
2020-02-27 11:00 | 76.1 | 75.62
2020-02-27 11:30 | 72.97 | 72.46
2020-02-27 12:00 | 73.99 | 73.43
2020-02-27 12:30 | 75.58 | 75.04
2020-02-27 13:00 | 76.49 | 75.94
2020-02-27 13:30 | 79.9 | 79.3
2020-02-27 14:00 | 86.67 | 86.09
2020-02-27 14:30 | 75.07 | 74.8
2020-02-27 15:00 | 73.06 | 72.79
2020-02-27 15:30 | 66.3 | 65.98
2020-02-27 16:00 | 67.96 | 67.68
2020-02-27 16:30 | 70.53 | 70.26
2020-02-27 17:00 | 72.13 | 71.86
2020-02-27 17:30 | 73.03 | 72.56
2020-02-27 18:00 | 74.88 | 74.28
2020-02-27 18:30 | 74.7 | 73.92
2020-02-27 19:00 | 74.69 | 73.89
2020-02-27 19:30 | 73.58 | 72.75
2020-02-27 20:00 | 71.51 | 70.45
2020-02-27 20:30 | 68.89 | 67.75
2020-02-27 21:00 | 66.03 | 64.96
2020-02-27 21:30 | 61.15 | 59.98
2020-02-27 22:00 | 56.71 | 55.31
2020-02-27 22:30 | 53.67 | 52.41
2020-02-27 23:00 | 50.69 | 49.35
2020-02-27 23:30 | 48.39 | 46.97
2020-02-28 | 45.95 | 44.46
2020-02-28 00:30 | 44.3 | 42.74
2020-02-28 01:00 | 43.35 | 41.73
2020-02-28 01:30 | 41.08 | 40.62
2020-02-28 02:00 | 40.56 | 40.11
2020-02-28 02:30 | 40.11 | 39.65
2020-02-28 03:00 | 39.38 | 38.91
2020-02-28 03:30 | 39.23 | 38.77
2020-02-28 04:00 | 39.53 | 39.06
2020-02-28 04:30 | 40.52 | 40.06
2020-02-28 05:00 | 41.45 | 41
2020-02-28 05:30 | 43.78 | 43.36
2020-02-28 06:00 | 46.12 | 45.67
2020-02-28 06:30 | 51.82 | 51.03
2020-02-28 07:00 | 57.3 | 55.99
2020-02-28 07:30 | 64.83 | 62.61
2020-02-28 08:00 | 68.77 | 66.65
2020-02-28 08:30 | 71.28 | 69.17
2020-02-28 09:00 | 72.9 | 70.9
2020-02-28 09:30 | 73.52 | 71.53
2020-02-28 10:00 | 73.78 | 71.81
2020-02-28 10:30 | 75.47 | 73.59
2020-02-28 11:00 | 75.83 | 73.95
2020-02-28 11:30 | 76.18 | 74.33
2020-02-28 12:00 | 76.42 | 74.58
2020-02-28 12:30 | 77.69 | 75.87
2020-02-28 13:00 | 78.45 | 76.66
2020-02-28 13:30 | 79.02 | 77.24
2020-02-28 14:00 | 80.2 | 78.44
2020-02-28 14:30 | 81.6 | 79.89
2020-02-28 15:00 | 82.19 | 80.47
2020-02-28 15:30 | 82.51 | 80.78
2020-02-28 16:00 | 84.11 | 82.43
2020-02-28 16:30 | 85.08 | 83.39
2020-02-28 17:00 | 85.59 | 83.9
2020-02-28 17:30 | 83.57 | 81.81
2020-02-28 18:00 | 80.33 | 78.51
2020-02-28 18:30 | 78.74 | 76.9
2020-02-28 19:00 | 78.31 | 76.47
2020-02-28 19:30 | 77.33 | 75.44
2020-02-28 20:00 | 74.63 | 72.65
2020-02-28 20:30 | 71.8 | 69.71
2020-02-28 21:00 | 68.99 | 66.77
2020-02-28 21:30 | 65.55 | 63.74
2020-02-28 22:00 | 61.14 | 59.94
2020-02-28 22:30 | 58.08 | 56.61
2020-02-28 23:00 | 55.92 | 54.13
2020-02-28 23:30 | 52.06 | 51.56
2020-02-29 | 49.02 | 48.75
2020-02-29 00:30 | 47.23 | 46.95
2020-02-29 01:00 | 45.65 | 45.36
2020-02-29 01:30 | 42.01 | 41.69
2020-02-29 02:00 | 41.07 | 40.74
2020-02-29 02:30 | 40.27 | 39.93
2020-02-29 03:00 | 39.23 | 38.92
2020-02-29 03:30 | 38.7 | 38.37
2020-02-29 04:00 | 38.15 | 37.81
2020-02-29 04:30 | 38.23 | 37.89
2020-02-29 05:00 | 38.72 | 38.39
2020-02-29 05:30 | 40.16 | 39.85
2020-02-29 06:00 | 40.86 | 40.55
2020-02-29 06:30 | 43.25 | 42.97
2020-02-29 07:00 | 45.59 | 45.2
2020-02-29 07:30 | 47.92 | 47.3
2020-02-29 08:00 | 50.57 | 49.84
2020-02-29 08:30 | 53.51 | 52.97
2020-02-29 09:00 | 55.13 | 54.41
2020-02-29 09:30 | 55.92 | 55.07
2020-02-29 10:00 | 56.14 | 55.15
2020-02-29 10:30 | 56.87 | 55.82
2020-02-29 11:00 | 58.19 | 57.03
2020-02-29 11:30 | 57.62 | 56.45
2020-02-29 12:00 | 56.82 | 55.67
2020-02-29 12:30 | 58.97 | 58.02
2020-02-29 13:00 | 60.51 | 59.6
2020-02-29 13:30 | 58.98 | 58.05
2020-02-29 14:00 | 58.37 | 57.43
2020-02-29 14:30 | 58.69 | 57.75
2020-02-29 15:00 | 59.7 | 58.78
2020-02-29 15:30 | 61.05 | 60.14
2020-02-29 16:00 | 61.88 | 60.98
2020-02-29 16:30 | 63 | 62.11
2020-02-29 17:00 | 65.08 | 64.23
2020-02-29 17:30 | 65.9 | 65.06
2020-02-29 18:00 | 67.09 | 66.26
2020-02-29 18:30 | 66.54 | 65.7
2020-02-29 19:00 | 66.77 | 65.95
2020-02-29 19:30 | 66.3 | 65.46
2020-02-29 20:00 | 64.51 | 63.64
2020-02-29 20:30 | 62.21 | 61.29
2020-02-29 21:00 | 60.23 | 59.27
2020-02-29 21:30 | 58.2 | 57.2
2020-02-29 22:00 | 56.14 | 55.08
2020-02-29 22:30 | 53.61 | 52.49
2020-02-29 23:00 | 51.61 | 50.44
2020-02-29 23:30 | 49.68 | 48.45
2020-03-01 | 47.8 | 46.51
Formulas:
Date/Time = [Date/Time, row above]+30/24/60

## 24. Historic ratings
PQ Rating (MVA) |  | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer | 2019 Winter | 2019/20 Summer
|  | 303 | 303 | 303 | 303 | 303 | 303
Transformers | T038T01 | 92 | 92 | 92 | 92 | 92 | 92
| T038T02 | 124 | 124 | 124 | 124 | 124 | 124
| T038T03 | 87 | 87 | 87 | 87 | 87 | 87

## 26. Unplanned outages
Unplanned Outage Date/Time | Element Affected | Element Type | Outage Cause | Outage Duration (mins) | Customer Outage Duration (mins) | MW Lost (Instantaneous) | MW Minutes
2017-05-05 15:33 | T038 132KV 2 TRANSFORMER | TRANSFORMER | HV Equipment malfunction or failure | 44.85
2017-05-24 03:40 | T038 132KV 2 TRANSFORMER | TRANSFORMER | Secondary system malfunction or failure | 4.0333
2017-06-08 07:52 | T038 132KV 2 TRANSFORMER | TRANSFORMER | Secondary system malfunction or failure | 122.3333
2017-10-31 18:18 | 7451 - T038 Mackay to T141 Pioneer Valley | FEEDER | Human Error | 29.9167 | 29.92 | 62 | 1896.95
2017-10-31 18:18 | T038 132KV 3 TRANSFORMER | TRANSFORMER | Human Error | 29.9167
2019-03-24 02:09 | 7238 - T141 Pioneer Valley to T038 Mackay | FEEDER | Natural Hazard | 101.9333
2019-03-24 02:09 | T038 132KV 2 TRANSFORMER | TRANSFORMER | Natural Hazard | 101.9333
2019-05-01 16:49 | 7451 - T038 Mackay to T141 Pioneer Valley | FEEDER | Secondary system malfunction or failure | 70.9833
2019-05-01 16:49 | T038 132KV 3 TRANSFORMER | TRANSFORMER | Secondary system malfunction or failure | 70.9833