## Cover Page
AER Rule | Field Name | Value(s)
1 | Constrained connection point ID | Mudgeeraba
2 | Constraint primary driver | Asset condition
3 | Constraint investment type | Asset renewal
4 | Constrained connection point latitude (decimal degrees) | -28.095
| Constrained connection point longitude (decimal degrees) | 153.397
5 | Affect on residential customers
| Annual Energy | Not available
| Maximum Demand | Not available
6,7 | Effect on industrial and commercial customers
| Annual Energy | Not available
| Maximum Demand | Not available
8 | Load profile (maximum day, MVA)
50% PoE
Load profile (minimum day, MVA)
Minimum demand data (MVA)
| Max. demand, maximum demand day (MVA) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| 10% PoE | 436.7254 | 467.9552 | 218.1997 | 219.0441 | 480.3775 | 219.2355 | 218.5488 | 218.5551 | 472.6263 | 285.3031 | 285.4987
| 50% PoE | 415.304 | 445.002 | 207.497 | 208.3 | 456.815 | 208.482 | 207.829 | 207.835 | 449.444 | 271.309 | 271.495
9 | Max. demand, minimum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Maximum demand data | 170.371 | 182.506 | 261.258 | 193.364 | 456.815 | 225.517 | 200.92 | 194.567 | 226.932 | 202.394 | 202.826
10 | Load profile (maximum day, MW)
Load profile 50%
| Max. demand, maximum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| 10% PoE | 287.0477 | 328.4947 | 385.0602 | 413.3782 | 415.8873 | 416.0587 | 391.5747 | 401.7109 | 392.1594 | 388.9258 | 421.5521
| 50% PoE | 272.968 | 312.382 | 366.173 | 393.102 | 395.488 | 395.651 | 372.368 | 382.007 | 372.924 | 369.849 | 400.875
11 | Load profile (minimum day, MW)
Minimum demand data (MW)
| Min. demand, minimum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Mininum demand data | 70.474 | 71.866 | 93.999 | 71.979 | 116.108 | 91.048 | 89.833 | 66.547 | 88.761 | 87.034 | 85.186
12 | Voltage Level (kV) | 275/110
13 | Maximum load at risk per year | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Load at risk (MW, peak) | 0 | 0 | 0 | 0 | 0 | 298.9 | 300.8 | 302.7 | 304.6 | 306.7 | 306.7
| Load at risk (MVA, peak) | 0 | 0 | 0 | 0 | 0 | 332.1 | 334.2 | 336.3 | 338.4 | 340.7 | 340.7
14 | Load duration curve
15 | Preferred investment | Mudgeeraba 275kV and 110kV primary plant replacement_2026
16 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Capital cost ($m, nominal) | [5 empty] | 20
17 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Operating cost ($m, nominal) | [5 empty] | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
18 | Preferred investment cost accuracy | 0.3
19 | Preferred investment proposed timing | 2025-12-31
20 | Demand reduction to defer the investment by 1 year
21 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Annual deferral value ($m, nominal)
22 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Load transfer capacity (MVA) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
23 | Historic load trace
24 | Historic ratings
25 | Limitation asset | Primary plant
26 | Unplanned outages
27 | Maximum fault level (kA) | 22.9 (110kV)
28 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Economic cost ($m) | 0 | 0 | 0 | 0 | 0 | 15.7638 | 16.008 | 16.2522 | 16.4964 | 16.9807 | 16.9247
29 | VCR ($m/MWh) | 0.04003
30 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Annual unserved energy (MWh) | 0 | 0 | 0 | 0 | 0 | 393.8 | 399.9 | 406 | 412.1 | 424.2 | 422.8

## 8. Load profile max (50% PoE)
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:30 | 117.009 | 126.297 | 170.915 | 171.438 | 130.441 | 171.599 | 171.665 | 171.396 | 154.359 | 131.905 | 132.054
1:00 | 111.812 | 122.154 | 159.263 | 159.768 | 122.878 | 159.811 | 159.898 | 159.778 | 149.95 | 123.815 | 123.949
1:30 | 107.362 | 120.177 | 161.869 | 161.997 | 121.553 | 162.05 | 162.111 | 162.148 | 141.999 | 119.849 | 118.643
2:00 | 104.659 | 136.595 | 156.792 | 157.28 | 119.025 | 157.232 | 157.279 | 157.456 | 140.465 | 114.584 | 115.826
2:30 | 99.844 | 114.615 | 159.95 | 160.402 | 117.249 | 160.384 | 160.377 | 160.555 | 136.53 | 112.269 | 112.395
3:00 | 99.743 | 113.976 | 158.619 | 159.021 | 116.108 | 159.051 | 158.96 | 159.117 | 132.982 | 112.669 | 112.791
3:30 | 100.324 | 115.022 | 157.763 | 157.896 | 116.508 | 157.841 | 157.828 | 157.827 | 132.938 | 113.525 | 113.601
4:00 | 100.641 | 119.143 | 159.581 | 159.715 | 117.209 | 159.652 | 159.752 | 159.802 | 129.987 | 113.465 | 113.533
4:30 | 100.642 | 117.095 | 164.001 | 163.023 | 118.323 | 164.276 | 164.32 | 164.311 | 130.338 | 115.727 | 115.788
5:00 | 100.388 | 118.731 | 130.747 | 131.087 | 118.085 | 131.209 | 131.286 | 131.371 | 130.349 | 120.523 | 121.876
5:30 | 101.664 | 124.597 | 139.187 | 138.974 | 124.639 | 140.573 | 140.644 | 140.687 | 134.006 | 130.848 | 131.043
6:00 | 103.531 | 132.185 | 149.905 | 150.381 | 132.556 | 150.491 | 150.578 | 150.626 | 135.825 | 141.173 | 139.67
6:30 | 106.032 | 146.996 | 166.875 | 168.316 | 151.913 | 170.139 | 168.427 | 170.057 | 139.568 | 158.659 | 158.684
7:00 | 111.198 | 158.298 | 167.704 | 168.652 | 194.748 | 168.685 | 168.72 | 168.756 | 143.853 | 174.804 | 174.965
7:30 | 114.51 | 162.944 | 175.379 | 175.953 | 203.48 | 175.372 | 175.866 | 175.438 | 152.379 | 181.314 | 181.271
8:00 | 131.982 | 170.428 | 175.516 | 177.268 | 207.978 | 176.406 | 175.547 | 175.68 | 170.323 | 173.649 | 172.497
8:30 | 127.847 | 169.565 | 163.204 | 164.758 | 208.838 | 163.361 | 162.736 | 162.325 | 172.878 | 162.148 | 161.096
9:00 | 129.91 | 174.467 | 164.445 | 161.016 | 209.187 | 160.179 | 179.485 | 191.488 | 181.609 | 157.556 | 165.346
9:30 | 139.723 | 193.745 | 152.9615 | 150.139 | 215.649 | 147.342 | 146.027 | 144.829 | 219.549 | 168.497 | 169.482
10:00 | 153.826 | 188.034 | 141.478 | 139.402 | 217.503 | 171.504 | 171.234 | 169.949 | 295.945 | 175.428 | 173.618
10:30 | 163.532 | 184.23 | 167.793 | 166.444 | 205.614 | 127.059 | 126.002 | 148.765 | 289.032 | 167.662 | 146.186
11:00 | 167.634 | 183.78 | 164.047 | 162.093 | 214.755 | 130.469 | 129.207 | 127.581 | 286.853 | 155.4685 | 144.4515
11:30 | 197.429 | 183.101 | 162.102 | 160.818 | 216.732 | 130.132 | 130.279 | 128.143 | 255.537 | 143.275 | 142.717
12:00 | 280.621 | 182.952 | 168.621 | 167.655 | 220.356 | 135.838 | 130.9405 | 131.638 | 262.778 | 153.469
12:30 | 269.07 | 209.889 | 171.154 | 170.764 | 217.431 | 131.879 | 131.602 | 135.847 | 303.632 | 163.663 | 147.608
13:00 | 236.227 | 182.172 | 172.76 | 171.325 | 218.161 | 168.743 | 150.143 | 152.8875 | 313.951 | 166.033 | 155.1175
13:30 | 275.508 | 197.227 | 174.5 | 171.929 | 215.53 | 169.737 | 168.684 | 169.928 | 320.004 | 164.308 | 162.627
14:00 | 270.379 | 228.313 | 142.286 | 175.131 | 212.111 | 172.922 | 172.136 | 171.027 | 449.444 | 147.539 | 146.178
14:30 | 415.304 | 245.291 | 144.629 | 143.198 | 217.311 | 141.428 | 159.145 | 175.497 | 259.812 | 148.009 | 146.714
15:00 | 216.737 | 264.277 | 153.5187 | 148.916 | 235.769 | 147.022 | 146.154 | 145.311 | 426.838 | 169.255 | 168.242
15:30 | 292.787 | 313.186 | 162.4083 | 158.918 | 287.248 | 183.726 | 182.656 | 194.07 | 251.014 | 182.057 | 182.577
16:00 | 292.843 | 445.002 | 171.298 | 172.822 | 313.379 | 171.672 | 179.5705 | 168.954 | 273.089 | 212.707 | 212.186
16:30 | 237.941 | 378.416 | 176.972 | 175.888 | 456.815 | 175.194 | 176.485 | 176.264 | 273.116 | 167.076 | 168.202
17:00 | 214.775 | 283.026 | 207.497 | 208.3 | 280.807 | 208.482 | 207.829 | 207.835 | 349.054 | 271.309 | 271.495
17:30 | 215.3607 | 414.631 | 272.375 | 272.207 | 425.065 | 272.568 | 272.739 | 272.951 | 332.6565 | 268.384 | 268.466
18:00 | 215.9463 | 415.553 | 341.581 | 342.298 | 438.738 | 342.857 | 343.121 | 343.359 | 316.259 | 328.376 | 329.019
18:30 | 216.532 | 417.178 | 381.438 | 382.532 | 424.197 | 382.928 | 383.187 | 383.496 | 325.454 | 454.991 | 455.892
19:00 | 216.116 | 417.521 | 460.74 | 461.577 | 422.768 | 461.724 | 461.916 | 462.168 | 312.063 | 306.085 | 302.129
19:30 | 210.484 | 264.359 | 360.956 | 362.016 | 412.396 | 362.289 | 371.92 | 372.121 | 312.504 | 305.827 | 306.317
20:00 | 204.852 | 389.392 | 333.487 | 334.572 | 439.579 | 334.851 | 335.016 | 335.144 | 306.762 | 310.153 | 310.559
20:30 | 199.213 | 276.621 | 328.779 | 329.828 | 431.605 | 329.993 | 330.124 | 330.241 | 290.939 | 314.88 | 315.237
21:00 | 244.901 | 255.257 | 305.083 | 304.465 | 337.482 | 306.306 | 306.43 | 306.53 | 312.656 | 287.093 | 287.874
21:30 | 286.586 | 174.416 | 247.027 | 205.79 | 256.322 | 216.476 | 216.572 | 206.678 | 339.987 | 204.166 | 225.556
22:00 | 341.043 | 170.72 | 181.236 | 182.469 | 220.432 | 182.613 | 182.739 | 182.866 | 405.665 | 172.472 | 172.77
22:30 | 333.575 | 168.477 | 217.77 | 177.275 | 170.151 | 177.441 | 177.572 | 177.616 | 439.415 | 172.188 | 172.56
23:00 | 350.224 | 180.351 | 213.412 | 214.209 | 167.787 | 214.371 | 214.474 | 214.558 | 419.99 | 183.687 | 184.034
23:30 | 186.914 | 151.753 | 203.931 | 205.55 | 157.132 | 205.711 | 205.776 | 205.825 | 266.677 | 159.895 | 160.077
0:00 | 120.939 | 134.482 | 191.558 | 192.789 | 140.749 | 192.901 | 192.964 | 192.994 | 168.17 | 145.286 | 144.187

## 8. Load profile min
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:30 | 98.982 | 96.379 | 119.35 | 130.49 | 119.479 | 120.861 | 121.168 | 130.584 | 119.699 | 119.832 | 119.843
1:00 | 92.903 | 89.518 | 115.761 | 124.663 | 115.827 | 115.931 | 115.982 | 124.775 | 114.51 | 114.751 | 116.176
1:30 | 88.398 | 84.333 | 112.56 | 120.282 | 112.496 | 112.713 | 112.646 | 120.424 | 112.819 | 112.951 | 112.957
2:00 | 84.103 | 86.511 | 109.5 | 116.672 | 109.602 | 109.682 | 109.729 | 116.83 | 109.824 | 109.982 | 109.984
2:30 | 81.134 | 78.296 | 102.176 | 113.653 | 102.185 | 102.214 | 102.239 | 113.953 | 102.307 | 102.39 | 102.56
3:00 | 78.209 | 78.697 | 102.46 | 113.153 | 102.622 | 102.759 | 102.787 | 113.298 | 102.857 | 102.911 | 102.917
3:30 | 77.307 | 77.007 | 103.876 | 112.94 | 104.056 | 104.128 | 104.162 | 113.133 | 104.221 | 104.316 | 104.322
4:00 | 75.992 | 76.912 | 104.603 | 113.339 | 105.234 | 104.846 | 104.872 | 113.417 | 104.84 | 104.923 | 104.927
4:30 | 76.912 | 77.572 | 105.38 | 113.038 | 105.429 | 105.498 | 105.523 | 113.081 | 105.587 | 105.677 | 105.684
5:00 | 78.513 | 81.963 | 106.009 | 112.433 | 104.065 | 104.176 | 106.162 | 112.642 | 106.116 | 106.212 | 106.247
5:30 | 81.276 | 81.463 | 113.86 | 113.514 | 113.79 | 108.611 | 108.758 | 113.527 | 108.72 | 108.806 | 108.83
6:00 | 84.626 | 84.216 | 110.271 | 116.323 | 110.292 | 110.324 | 112.578 | 116.446 | 112.802 | 112.873 | 110.517
6:30 | 90.191 | 88.82 | 115.926 | 120.131 | 115.617 | 115.307 | 115.273 | 120.294 | 115.037 | 115.163 | 114.94
7:00 | 94.012 | 92.79 | 119.348 | 123.587 | 118.853 | 118.547 | 118.138 | 123.544 | 118.215 | 117.359 | 117.227
7:30 | 101.433 | 99.609 | 127.039 | 127.043 | 126.472 | 127.739 | 131.55 | 126.608 | 130.89 | 130.372 | 130.192
8:00 | 113.446 | 100.132 | 137.63 | 127.407 | 136.643 | 136.252 | 138.898 | 126.104 | 147.264 | 142.958 | 185.512
8:30 | 115.085 | 126.658 | 175.642 | 128.444 | 174.643 | 173.822 | 173.062 | 125.195 | 170.847 | 169.408 | 169.198
9:00 | 115.315 | 114.433 | 172.662 | 122.893 | 170.761 | 169.307 | 168.431 | 121.9532 | 166.6395 | 164.121 | 163.3
9:30 | 117.874 | 102.208 | 170.394 | 117.923 | 167.479 | 166.647 | 165.094 | 118.7115 | 162.432 | 161.11 | 160.217
10:00 | 114.007 | 111.4015 | 165.243 | 122.716 | 162.334 | 160.791 | 159.489 | 115.4698 | 171.605 | 169.522 | 168.549
10:30 | 184.949 | 120.595 | 164.785 | 118.3046 | 161.669 | 161.161 | 159.093 | 112.228 | 169.663 | 167.924 | 154.106
11:00 | 189.089 | 122.225 | 166.526 | 113.8932 | 163.404 | 162.111 | 161.556 | 108.9863 | 158.737 | 167.006 | 165.918
11:30 | 213.495 | 103.8435 | 169.136 | 109.4818 | 166.503 | 166.018 | 164.276 | 105.7445 | 162.299 | 160.742 | 159.604
12:00 | 102.802 | 85.462 | 169.186 | 105.0704 | 166.509 | 165.448 | 164.408 | 102.5027 | 162.427 | 160.837 | 159.725
12:30 | 108.196 | 209.254 | 173.717 | 100.659 | 171.45 | 169.749 | 169.179 | 99.261 | 166.323 | 166.044 | 164.95
13:00 | 106.781 | 162.778 | 179.945 | 98.7693 | 177.893 | 176.491 | 175.234 | 186.051 | 172.386 | 170.83 | 169.937
13:30 | 109.539 | 127.4685 | 187.916 | 96.8797 | 184.224 | 183.087 | 182.018 | 171.9937 | 179.379 | 178.426 | 178.869
14:00 | 119.867 | 92.159 | 195.767 | 94.99 | 191.969 | 190.766 | 191.103 | 157.9365 | 188.272 | 186.843 | 184.903
14:30 | 204.899 | 110.5355 | 212.023 | 93.704 | 157.532 | 163.47 | 208.268 | 143.8793 | 184.421 | 205.141 | 204.189
15:00 | 170.365 | 128.912 | 150.965 | 132.597 | 149.372 | 148.52 | 147.739 | 129.822 | 146.8 | 145.638 | 144.874
15:30 | 273.185 | 124.816 | 210.916 | 139.797 | 209.399 | 208.751 | 207.777 | 137.127 | 207.735 | 206.452 | 205.876
16:00 | 257.302 | 120.72 | 230.281 | 140.43 | 231.25 | 230.66 | 231.104 | 140.571 | 227.584 | 229.786 | 229.634
16:30 | 198.835 | 132.651 | 239.297 | 149.115 | 238.72 | 238.41 | 238.089 | 147.861 | 237.619 | 237.519 | 237.264
17:00 | 317.02 | 149.617 | 314.887 | 165.617 | 313.101 | 312.956 | 312.993 | 164.525 | 312.943 | 283.1395 | 313.069
17:30 | 224.415 | 134.119 | 266.328 | 172.715 | 266.405 | 266.435 | 266.54 | 173.842 | 266.702 | 328.76 | 328.837
18:00 | 215.963 | 141.141 | 268.497 | 182.697 | 267.502 | 270.136 | 270.339 | 183.675 | 271.168 | 271.904 | 272.058
18:30 | 227.501 | 206.795 | 272.282 | 254.203 | 272.627 | 272.786 | 273.003 | 255.213 | 273.635 | 274.204 | 274.329
19:00 | 224.836 | 211.052 | 288.631 | 271.08 | 288.956 | 289.142 | 289.324 | 271.887 | 289.94 | 290.514 | 290.613
19:30 | 234.364 | 206.794 | 276.753 | 265.024 | 277.041 | 277.194 | 277.344 | 265.527 | 277.8 | 278.536 | 278.605
20:00 | 262.841 | 188.502 | 273.383 | 220.231 | 273.951 | 274.059 | 274.22 | 225.371 | 274.693 | 275.129 | 275.178
20:30 | 276.606 | 136.065 | 259.496 | 175.851 | 259.451 | 259.981 | 259.469 | 179.723 | 259.537 | 261.219 | 259.748
21:00 | 333.256 | 128.98 | 189.643 | 161.827 | 189.854 | 189.906 | 190.418 | 162.405 | 190.425 | 190.95 | 190.98
21:30 | 274.348 | 125.539 | 162.136 | 157.875 | 162.291 | 162.422 | 162.528 | 158.413 | 162.885 | 163.317 | 163.348
22:00 | 221.426 | 119.973 | 161.02 | 153.219 | 160.263 | 160.032 | 160.122 | 152.553 | 160.467 | 160.878 | 160.91
22:30 | 176.001 | 118.608 | 160.11 | 146.788 | 160.308 | 160.347 | 160.407 | 146.693 | 160.644 | 160.19 | 160.22
23:00 | 176.072 | 123.821 | 153.112 | 146.453 | 153.267 | 153.268 | 153.339 | 141.034 | 153.54 | 153.844 | 153.873
23:30 | 253.534 | 116.987 | 144.887 | 135.127 | 145.008 | 144.993 | 145.042 | 135.375 | 145.184 | 145.449 | 145.469
0:00 | 106.859 | 104.794 | 132.686 | 142.609 | 132.64 | 134.856 | 134.902 | 140.858 | 135.038 | 133.105 | 132.812

## 10. Load profile (50% PoE)
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:30 | 104.173 | 104.061 | 153.486 | 168.787 | 156.267 | 137.326 | 160.755 | 136.81 | 156.956 | 169.117 | 169.218
1:00 | 100.87 | 100.947 | 145.858 | 162.014 | 148.058 | 132.562 | 155.371 | 132.476 | 152.716 | 162.688 | 162.556
1:30 | 98.701 | 98.641 | 141.977 | 157.114 | 143.279 | 129.658 | 148.074 | 129.713 | 148.425 | 157.422 | 157.454
2:00 | 92.564 | 92.71 | 140.308 | 151.356 | 138.127 | 121.543 | 142.922 | 121.591 | 146.042 | 151.639 | 151.646
2:30 | 95.656 | 95.86 | 139.164 | 148.578 | 136.074 | 125.789 | 142.051 | 125.803 | 144.57 | 148.3545 | 148.375
3:00 | 95.107 | 95.353 | 138.436 | 145.494 | 134.871 | 124.971 | 141.847 | 124.899 | 143.137 | 145.07 | 145.075
3:30 | 93.309 | 93.675 | 137.085 | 143.82 | 134.954 | 122.862 | 143.349 | 122.747 | 143.82 | 143.374 | 143.38
4:00 | 95.46 | 95.754 | 137.02 | 141.793 | 134.57 | 125.545 | 141.711 | 125.444 | 142.897 | 141.685 | 141.691
4:30 | 97.578 | 98.169 | 137.607 | 141.966 | 135.945 | 128.593 | 139.791 | 128.569 | 142.733 | 141.452 | 142.052
5:00 | 99.778 | 100.042 | 139.46 | 143.276 | 136.905 | 131.159 | 136.371 | 131.243 | 145.868 | 143.646 | 143.698
5:30 | 105.093 | 105.112 | 143.792 | 150.316 | 142.73 | 137.878 | 137.636 | 138.08 | 149.118 | 150.524 | 150.557
6:00 | 109.873 | 109.864 | 152.737 | 160.614 | 150.16 | 144.135 | 139.482 | 144.175 | 157.26 | 160.762 | 160.806
6:30 | 121.048 | 120.922 | 162.44 | 178.678 | 158.336 | 160.086 | 145.238 | 160.124 | 167.914 | 178.871 | 179.384
7:00 | 137.117 | 134.765 | 173.703 | 200.36 | 173.521 | 182.176 | 149.74 | 182.032 | 180.297 | 200.024 | 200.038
7:30 | 148.264 | 147.893 | 198.713 | 221.15 | 195.19 | 197.207 | 154.834 | 196.874 | 209.001 | 220.291 | 219.366
8:00 | 155.274 | 159.283 | 212.168 | 231.809 | 205.527 | 210.689 | 180.324 | 210.018 | 224.575 | 230.294 | 230.193
8:30 | 164.265 | 154.463 | 217.627 | 243.0715 | 206.466 | 220.692 | 215.502 | 203.812 | 232.02 | 290.408 | 246.956
9:00 | 180.5565 | 205.725 | 223.086 | 254.334 | 227.862 | 242.923 | 185.896 | 259.401 | 257.572 | 271.145 | 271.347
9:30 | 196.848 | 209.4 | 224.369 | 249.828 | 248.191 | 265.154 | 187.461 | 263.176 | 237.168 | 296.099 | 295.738
10:00 | 213.718 | 211.568 | 245.218 | 262.16 | 240.0905 | 270.245 | 197.295 | 271.068 | 233.555 | 302.2215 | 301.503
10:30 | 218.919 | 217.039 | 254.2285 | 248.34 | 231.99 | 243.021 | 213.744 | 273.983 | 290.787 | 308.344 | 307.268
11:00 | 206.365 | 220.586 | 263.239 | 255.587 | 281.185 | 241.321 | 220.512 | 280.758 | 287.286 | 256.196 | 279.4495
11:30 | 186.96 | 227.18 | 265.777 | 275.897 | 290.573 | 243.897 | 229.473 | 291.615 | 283.785 | 252.504 | 251.631
12:00 | 181.199 | 178.541 | 269.422 | 296.207 | 291.211 | 246.473 | 239.288 | 256.406 | 259.406 | 260.468 | 257.8905
12:30 | 195.434 | 192.9365 | 271.2 | 296.711 | 299.196 | 258.62 | 250.092 | 236.03 | 262.5955 | 265.311 | 264.15
13:00 | 209.669 | 207.332 | 277.974 | 297.215 | 308.439 | 270.767 | 258.362 | 244.142 | 265.785 | 282.4315 | 281.314
13:30 | 214.8595 | 219.9192 | 284.748 | 321.1867 | 305.277 | 281.224 | 288.584 | 265.8218 | 297.694 | 299.552 | 298.478
14:00 | 220.05 | 232.5065 | 295.825 | 345.1585 | 311.655 | 297.9092 | 281.927 | 287.5015 | 277.977 | 305.4101 | 306.889
14:30 | 272.968 | 245.0938 | 307.344 | 369.1302 | 324.379 | 314.5943 | 303.506 | 309.1812 | 271.705 | 311.2682 | 338.2177
15:00 | 270.9797 | 257.681 | 335.893 | 393.102 | 348.082 | 331.2795 | 321.042 | 330.861 | 282.854 | 317.1263 | 369.5463
15:30 | 268.9913 | 265.8585 | 330.621 | 388.0753 | 371.785 | 347.9647 | 340.085 | 347.9097 | 293.97 | 322.9843 | 400.875
16:00 | 267.003 | 274.036 | 339.216 | 383.0485 | 395.488 | 364.6498 | 356.2265 | 364.9583 | 313.653 | 328.8424 | 391.7425
16:30 | 264.252 | 291.467 | 347.811 | 378.0218 | 382.018 | 381.335 | 372.368 | 382.007 | 328.756 | 334.7005 | 382.6099
17:00 | 261.501 | 301.9245 | 356.406 | 372.9951 | 368.548 | 395.651 | 327.468 | 373.0916 | 339.056 | 340.5586 | 373.4774
17:30 | 258.75 | 312.382 | 366.173 | 367.9684 | 355.078 | 383.827 | 321.348 | 364.1761 | 372.924 | 346.4167 | 364.3448
18:00 | 255.999 | 300.72 | 340.175 | 362.9416 | 323.4815 | 372.003 | 315.228 | 355.2607 |  | 352.2748 | 355.2123
18:30 | 253.248 | 289.058 | 314.177 | 357.9149 | 291.885 | 360.179 | 318.654 | 346.3452 | 321.146 | 358.1328 | 346.0798
19:00 | 250.497 | 277.396 | 293.276 | 352.8882 | 274.191 | 348.355 | 318.942 | 337.4298 | 359.727 | 363.9909 | 336.9472
19:30 | 247.746 | 265.734 | 289.496 | 347.8615 | 251.92 | 336.531 | 301.593 | 328.5143 | 357.957 | 369.849 | 327.8147
20:00 | 244.995 | 254.072 | 284.761 | 342.8347 | 248.251 | 324.707 | 284.244 | 319.5989 | 355.546 | 357.584 | 318.6822
20:30 | 242.244 | 242.41 | 276.83 | 337.808 | 238.091 | 312.883 | 271.173 | 310.6834 | 318.523 | 345.319 | 309.5496
21:00 | 227.742 | 229.548 | 260.167 | 326.517 | 231.472 | 301.059 | 252.399 | 301.768 | 312.801 | 333.054 | 300.4171
21:30 | 213.24 | 212.371 | 242.237 | 303.6435 | 222.184 | 279.676 | 233.785 | 280.471 | 286.187 | 307.59 | 291.2845
22:00 | 195.527 | 195.194 | 226.717 | 280.77 | 213.724 | 258.672 | 213.819 | 259.2 | 265.96 | 282.126 | 282.152
22:30 | 173.689 | 182.489 | 215.465 | 249.032 | 197.52 | 228.912 | 203.793 | 229.347 | 232.448 | 250.175 | 249.72
23:00 | 171.733 | 171.674 | 207.139 | 237.056 | 199.084 | 227.79 | 196.326 | 228.196 | 222.58 | 237.811 | 237.637
23:30 | 152.253 | 152.289 | 187.072 | 216.135 | 175.954 | 205.933 | 175.745 | 206.559 | 201.149 | 213.081 | 212.526
0:00 | 112.22 | 112.165 | 166.657 | 188.173 | 177.181 | 147.43 | 172.51 | 147.512 | 170.011 | 188.751 | 188.765

## 11. Load profile min
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:30 | 86.132 | 86.468 | 112.896 | 124.96 | 130.441 | 123.365 | 125.207 | 125.062 | 133.123 | 125.18 | 125.378
1:00 | 82.344 | 83.002 | 108.719 | 118.565 | 122.878 | 117.679 | 116.451 | 118.676 | 121.474 | 116.601 | 116.739
1:30 | 79.704 | 80.594 | 105.806 | 113.554 | 121.553 | 113.395 | 110.922 | 113.711 | 119.522 | 111.043 | 111.171
2:00 | 77.448 | 78.872 | 103.251 | 110.128 | 119.025 | 110.725 | 106.919 | 110.292 | 109.431 | 107.017 | 107.135
2:30 | 70.474 | 71.866 | 93.999 | 107.548 | 117.249 | 109.313 | 104.774 | 107.664 | 106.845 | 104.888 | 105.006
3:00 | 70.82 | 72.151 | 94.334 | 107.1 | 116.108 | 108.343 | 105.417 | 107.224 | 104.421 | 105.521 | 105.68
3:30 | 71.785 | 73.15 | 95.68 | 106.99 | 116.508 | 107.267 | 103.959 | 107.137 | 103.315 | 104.069 | 104.17
4:00 | 72.403 | 73.674 | 96.411 | 107.397 | 117.209 | 106.915 | 102.424 | 107.501 | 102.165 | 102.5 | 102.6
4:30 | 72.948 | 74.193 | 97.06 | 106.998 | 118.323 | 109.932 | 102.679 | 107.085 | 102.22 | 102.797 | 102.896
5:00 | 73.415 | 74.615 | 97.589 | 106.366 | 118.085 | 114.853 | 102.857 | 106.558 | 103.062 | 103.067 | 103.263
5:30 | 75.344 | 76.357 | 100.191 | 107.282 | 124.639 | 138.743 | 105.048 | 107.461 | 105 | 105.184 | 105.308
6:00 | 78.409 | 79.142 | 103.473 | 109.931 | 132.556 | 127.593 | 108.655 | 110.086 | 108.716 | 108.817 | 108.978
6:30 | 82.649 | 83.45 | 109.054 | 113.759 | 151.913 | 142.55 | 115.174 | 113.933 | 116.515 | 115.365 | 115.465
7:00 | 85.529 | 86.04 | 112.27 | 117.3075 | 194.748 | 202.956 | 119.229 | 117.202 | 122.325 | 119.329 | 119.409
7:30 | 92.113 | 92.211 | 120.122 | 120.856 | 203.48 | 173.84 | 123.286 | 120.273 | 125.066 | 123.023 | 122.849
8:00 | 101.673 | 100.829 | 131.042 | 120.711 | 207.978 | 172.578 | 121.916 | 119.483 | 122.869 | 120.916 | 120.416
8:30 | 140.496 | 139.778 | 170.88 | 117.641 | 208.838 | 173.173 | 148.878 | 114.454 | 115.706 | 146.557 | 145.411
9:00 | 130.443 | 129.368 | 167.669 | 111.886 | 209.187 | 225.517 | 165.766 | 109.0614 | 130.714 | 128.317 | 126.866
9:30 | 129.084 | 127.744 | 165.307 | 106.596 | 215.649 | 181.524 | 118.846 | 103.6688 | 114.331 | 115.3 | 153.903
10:00 | 124.997 | 123.585 | 159.862 | 112.84 | 217.503 | 91.048 | 150.438 | 98.2761 | 106.372 | 146.376 | 105.234
10:30 | 125.016 | 123.617 | 159.765 | 105.4236 | 205.614 | 198.171 | 143.902 | 92.8835 | 101.609 | 101.818 | 99.776
11:00 | 126.635 | 125.151 | 161.681 | 98.0072 | 214.755 | 150.481 | 137.118 | 87.4909 | 99.0394 | 94.742 | 94.2515
11:30 | 128.693 | 127.099 | 164.355 | 90.5908 | 216.732 | 139.698 | 94.339 | 82.0983 | 96.4698 | 90.511 | 88.727
12:00 | 128.871 | 127.262 | 164.474 | 83.1744 | 220.356 | 127.506 | 92.211 | 76.7056 | 93.9002 | 88.565 | 87.416
12:30 | 132.444 | 130.882 | 169.192 | 75.758 | 217.431 | 129.704 | 91.369 | 71.313 | 91.3306 | 87.168 | 85.249
13:00 | 136.475 | 135.069 | 174.674 | 74.4983 | 218.161 | 135.932 | 89.833 | 66.547 | 88.761 | 87.034 | 85.186
13:30 | 142.234 | 140.782 | 182.272 | 73.2387 | 215.53 | 141.061 | 105.464 | 80.9485 | 91.706 | 88.234 | 86.713
14:00 | 151.914 | 150.361 | 190.296 | 71.979 | 212.111 | 154.738 | 121.095 | 95.35 | 96.333 | 90.92 | 89.171
14:30 | 110.518 | 108.977 | 207.831 | 78.473 | 217.311 | 163.285 | 136.726 | 109.7515 | 140.642 | 98.213 | 97.21
15:00 | 127.885 | 126.361 | 144.032 | 127.142 | 235.769 | 178.395 | 152.357 | 124.153 | 136.7465 | 149.807 | 105.655
15:30 | 170.371 | 167.405 | 205.896 | 133.033 | 287.248 | 156.695 | 125.178 | 130.57 | 132.851 | 123.084 | 119.836
16:00 | 141.412 | 174.069 | 227.502 | 133.347 | 313.379 | 198.996 | 178.315 | 131.471 | 152.593 | 134.483 | 134.017
16:30 | 131.371 | 182.506 | 239.268 | 142.539 | 456.815 | 210.302 | 148.037 | 141.477 | 135.324 | 147.347 | 147.516
17:00 | 150.843 | 151.587 | 261.258 | 156.336 | 280.807 | 221.608 | 163.467 | 155.984 | 193.546 | 163.436 | 163.66
17:30 | 142.595 | 152.68 | 188.954 | 166.033 | 425.065 | 195.858 | 178.917 | 166.83 | 202.22 | 179.954 | 180.774
18:00 | 141.844 | 142.492 | 192.503 | 174.08 | 438.738 | 205.501 | 188.24 | 175.195 | 191.181 | 189.426 | 190.232
18:30 | 144.634 | 144.776 | 195.996 | 190.075 | 424.197 | 211.613 | 197.752 | 191.378 | 204.68 | 198.85 | 199.751
19:00 | 150.632 | 150.689 | 202.366 | 193.364 | 422.768 | 208.895 | 200.92 | 194.567 | 206.491 | 202.394 | 202.826
19:30 | 145.71 | 145.847 | 197.806 | 188.307 | 412.396 | 202.789 | 193.686 | 188.573 | 200.551 | 194.727 | 195.828
20:00 | 142.571 | 142.66 | 193.595 | 174.246 | 439.579 | 197.893 | 191.933 | 178.372 | 200.536 | 192.27 | 193.377
20:30 | 139.142 | 139.191 | 187.784 | 166.988 | 431.605 | 190.542 | 193.17 | 170.913 | 226.932 | 193.778 | 194.49
21:00 | 128.059 | 128.567 | 170.717 | 158.634 | 337.482 | 176.837 | 189.833 | 159.166 | 188.406 | 190.36 | 190.879
21:30 | 122.722 | 122.815 | 162.003 | 151.77 | 256.322 | 167.5055 | 177.797 | 152.261 | 177.173 | 178.291 | 178.748
22:00 | 117.52 | 117.132 | 154.398 | 142.342 | 220.432 | 158.174 | 166.663 | 146.0745 | 161.425 | 166.711 | 167.053
22:30 | 115.997 | 116.057 | 152.245 | 139.654 | 170.151 | 155.553 | 157.786 | 139.888 | 152.592 | 158.054 | 158.356
23:00 | 110.26 | 110.339 | 144.87 | 139.372 | 167.787 | 154.614 | 155.963 | 134.3835 | 152.014 | 156.236 | 156.422
23:30 | 105.369 | 105.51 | 138.455 | 128.653 | 157.132 | 145.229 | 143.061 | 128.879 | 141.863 | 143.218 | 143.162
0:00 | 95.888 | 95.828 | 125.811 | 134.9 | 140.749 | 133.969 | 139.927 | 135.894 | 148.199 | 140.289 | 140.535

## 23. Historic load trace
Date/Time | Load (MVA) | Load (MW)
2017-03-01 00:30 | 28.44 | 28.09
2017-03-01 01:00 | 6.34 | 3.74
2017-03-01 01:30 | 12.55 | -11.18
2017-03-01 02:00 | 14.94 | -13.83
2017-03-01 02:30 | 25.48 | -24.87
2017-03-01 03:00 | 18.81 | -17.11
2017-03-01 03:30 | 22.29 | -19.64
2017-03-01 04:00 | 34.62 | -32.65
2017-03-01 04:30 | 26.05 | -23.72
2017-03-01 05:00 | 14.28 | -9.12
2017-03-01 05:30 | 11.54 | 4.64
2017-03-01 06:00 | 15.79 | 14.44
2017-03-01 06:30 | 31.31 | 28.89
2017-03-01 07:00 | 61.54 | 57.69
2017-03-01 07:30 | 94.39 | 90.04
2017-03-01 08:00 | 95.43 | 82.6
2017-03-01 08:30 | 111.73 | 97.14
2017-03-01 09:00 | 108.29 | 89.41
2017-03-01 09:30 | 112.74 | 90.84
2017-03-01 10:00 | 109.39 | 84.89
2017-03-01 10:30 | 109.42 | 87.64
2017-03-01 11:00 | 112.21 | 90.29
2017-03-01 11:30 | 112.62 | 90.52
2017-03-01 12:00 | 106.79 | 93.4
2017-03-01 12:30 | 107.55 | 94.47
2017-03-01 13:00 | 123.68 | 112.21
2017-03-01 13:30 | 125.07 | 113.21
2017-03-01 14:00 | 133.37 | 122.37
2017-03-01 14:30 | 143.99 | 137.6
2017-03-01 15:00 | 158.92 | 154.53
2017-03-01 15:30 | 184.63 | 180.95
2017-03-01 16:00 | 198.3 | 195.92
2017-03-01 16:30 | 188.99 | 188.74
2017-03-01 17:00 | 204.7 | 204.44
2017-03-01 17:30 | 218.38 | 218.06
2017-03-01 18:00 | 196.54 | 196.11
2017-03-01 18:30 | 204.86 | 204.28
2017-03-01 19:00 | 230.56 | 229.46
2017-03-01 19:30 | 240.99 | 240.11
2017-03-01 20:00 | 213.79 | 213.61
2017-03-01 20:30 | 202.68 | 202.65
2017-03-01 21:00 | 176.16 | 176.15
2017-03-01 21:30 | 156.98 | 156.86
2017-03-01 22:00 | 128.15 | 127.87
2017-03-01 22:30 | 143.69 | 143.56
2017-03-01 23:00 | 157.72 | 157.52
2017-03-01 23:30 | 125.63 | 125.6
2017-03-02 | 60.9 | 60.67
2017-03-02 00:30 | 30.32 | 30.15
2017-03-02 01:00 | 30.7 | 30.67
2017-03-02 01:30 | 23.98 | 23.91
2017-03-02 02:00 | 11.66 | 11.53
2017-03-02 02:30 | 5.64 | 5.14
2017-03-02 03:00 | 3.16 | 0.49
2017-03-02 03:30 | 7.27 | -6.51
2017-03-02 04:00 | 15.14 | 14.97
2017-03-02 04:30 | 3.94 | 0.21
2017-03-02 05:00 | 6.36 | -3.2
2017-03-02 05:30 | 12.98 | 9.16
2017-03-02 06:00 | 25.35 | 23.88
2017-03-02 06:30 | 45.01 | 42.98
2017-03-02 07:00 | 67.21 | 63.39
2017-03-02 07:30 | 105.81 | 90.73
2017-03-02 08:00 | 98.83 | 79.93
2017-03-02 08:30 | 98.67 | 74.79
2017-03-02 09:00 | 119.87 | 97.47
2017-03-02 09:30 | 120.55 | 90.36
2017-03-02 10:00 | 107.82 | 95.44
2017-03-02 10:30 | 111.78 | 102.78
2017-03-02 11:00 | 112.33 | 102.59
2017-03-02 11:30 | 122 | 112.14
2017-03-02 12:00 | 132.12 | 123.5
2017-03-02 12:30 | 125.17 | 117.79
2017-03-02 13:00 | 145.03 | 138.59
2017-03-02 13:30 | 152.69 | 146.44
2017-03-02 14:00 | 153.46 | 146.89
2017-03-02 14:30 | 177.01 | 171.19
2017-03-02 15:00 | 163.7 | 157.94
2017-03-02 15:30 | 157.98 | 152.76
2017-03-02 16:00 | 174.12 | 169.51
2017-03-02 16:30 | 197.98 | 194.22
2017-03-02 17:00 | 215.66 | 212.67
2017-03-02 17:30 | 205.93 | 205.08
2017-03-02 18:00 | 203.29 | 202.89
2017-03-02 18:30 | 222.69 | 222.27
2017-03-02 19:00 | 247.64 | 246.82
2017-03-02 19:30 | 240.28 | 239.54
2017-03-02 20:00 | 244.09 | 242.71
2017-03-02 20:30 | 235.91 | 234.95
2017-03-02 21:00 | 200.13 | 199.85
2017-03-02 21:30 | 175.5 | 175.5
2017-03-02 22:00 | 147.64 | 147.53
2017-03-02 22:30 | 156.8 | 156.8
2017-03-02 23:00 | 172.78 | 172.6
2017-03-02 23:30 | 137.44 | 137.29
2017-03-03 | 72.82 | 72.38
2017-03-03 00:30 | 60.42 | 60.09
2017-03-03 01:00 | 50.64 | 50.38
2017-03-03 01:30 | 28.32 | 27.88
2017-03-03 02:00 | 16.66 | 16.14
2017-03-03 02:30 | 21.25 | 21.01
2017-03-03 03:00 | 21.67 | 21.56
2017-03-03 03:30 | 24.17 | 24.1
2017-03-03 04:00 | 15.19 | 15.03
2017-03-03 04:30 | 3.87 | 1.46
2017-03-03 05:00 | 6.71 | 4.22
2017-03-03 05:30 | 31.74 | 30.87
2017-03-03 06:00 | 50.99 | 50.42
2017-03-03 06:30 | 80.16 | 79.25
2017-03-03 07:00 | 84.61 | 82.71
2017-03-03 07:30 | 110.48 | 102.32
2017-03-03 08:00 | 116.37 | 106.59
2017-03-03 08:30 | 107.39 | 93.32
2017-03-03 09:00 | 126.42 | 113.08
2017-03-03 09:30 | 136.9 | 128.95
2017-03-03 10:00 | 146.61 | 139.68
2017-03-03 10:30 | 154.44 | 148.24
2017-03-03 11:00 | 145.36 | 138.4
2017-03-03 11:30 | 150.59 | 143.31
2017-03-03 12:00 | 141.47 | 133.36
2017-03-03 12:30 | 142.95 | 138.44
2017-03-03 13:00 | 131.65 | 127.11
2017-03-03 13:30 | 130.44 | 125.71
2017-03-03 14:00 | 133.9 | 128.89
2017-03-03 14:30 | 143.59 | 138.79
2017-03-03 15:00 | 180.35 | 177.16
2017-03-03 15:30 | 194.23 | 192.94
2017-03-03 16:00 | 217.64 | 216.82
2017-03-03 16:30 | 236.2 | 235.39
2017-03-03 17:00 | 253.17 | 252.49
2017-03-03 17:30 | 254.89 | 254.1
2017-03-03 18:00 | 248.59 | 244
2017-03-03 18:30 | 249.67 | 246.28
2017-03-03 19:00 | 256.33 | 252.55
2017-03-03 19:30 | 251.2 | 247.56
2017-03-03 20:00 | 248.84 | 246.11
2017-03-03 20:30 | 235.69 | 233.26
2017-03-03 21:00 | 203.3 | 202.86
2017-03-03 21:30 | 181.86 | 181.74
2017-03-03 22:00 | 148.16 | 148.11
2017-03-03 22:30 | 163.3 | 163.12
2017-03-03 23:00 | 182.06 | 181.94
2017-03-03 23:30 | 151.51 | 151.51
2017-03-04 | 92.5 | 91.63
2017-03-04 00:30 | 70.21 | 68.53
2017-03-04 01:00 | 58.96 | 56.34
2017-03-04 01:30 | 39.5 | 35.1
2017-03-04 02:00 | 28.97 | 22.34
2017-03-04 02:30 | 27.12 | 19.59
2017-03-04 03:00 | 44.46 | 39.07
2017-03-04 03:30 | 47.61 | 41.98
2017-03-04 04:00 | 42.06 | 35
2017-03-04 04:30 | 35.25 | 27.74
2017-03-04 05:00 | 22.68 | 10.85
2017-03-04 05:30 | 24.54 | 16.33
2017-03-04 06:00 | 28.32 | 20.26
2017-03-04 06:30 | 41.87 | 37.39
2017-03-04 07:00 | 49.65 | 47.18
2017-03-04 07:30 | 44.53 | 43.26
2017-03-04 08:00 | 28.21 | 28.1
2017-03-04 08:30 | 39.54 | 38.47
2017-03-04 09:00 | 71.43 | 71.1
2017-03-04 09:30 | 88.97 | 88.56
2017-03-04 10:00 | 89.13 | 88.38
2017-03-04 10:30 | 95.13 | 94.08
2017-03-04 11:00 | 82.98 | 81.42
2017-03-04 11:30 | 82.5 | 80.69
2017-03-04 12:00 | 78.98 | 76.69
2017-03-04 12:30 | 83.93 | 80.93
2017-03-04 13:00 | 74.35 | 71.67
2017-03-04 13:30 | 73.43 | 71.69
2017-03-04 14:00 | 96.2 | 95.05
2017-03-04 14:30 | 113.55 | 112.33
2017-03-04 15:00 | 118.79 | 117.75
2017-03-04 15:30 | 135.22 | 134.17
2017-03-04 16:00 | 152.84 | 151.8
2017-03-04 16:30 | 160.19 | 159.31
2017-03-04 17:00 | 167.44 | 166.64
2017-03-04 17:30 | 163.91 | 163.13
2017-03-04 18:00 | 158.34 | 155.39
2017-03-04 18:30 | 184.29 | 178.29
2017-03-04 19:00 | 215.04 | 209.1
2017-03-04 19:30 | 201.13 | 195.55
2017-03-04 20:00 | 201.95 | 197.07
2017-03-04 20:30 | 200.28 | 196.12
2017-03-04 21:00 | 183.74 | 180.16
2017-03-04 21:30 | 170.02 | 168.63
2017-03-04 22:00 | 153.2 | 152.99
2017-03-04 22:30 | 172.49 | 172.32
2017-03-04 23:00 | 179.46 | 179.4
2017-03-04 23:30 | 166.09 | 166.08
2017-03-05 | 113.72 | 113.59
2017-03-05 00:30 | 77 | 76.46
2017-03-05 01:00 | 55.26 | 53.75
2017-03-05 01:30 | 31.66 | 31.4
2017-03-05 02:00 | 12.25 | 11.4
2017-03-05 02:30 | 9.22 | 8.33
2017-03-05 03:00 | 9.88 | 8.96
2017-03-05 03:30 | 7.46 | 6.3
2017-03-05 04:00 | 3.6 | -0.24
2017-03-05 04:30 | 3.45 | -2.16
2017-03-05 05:00 | 2.35 | 0.04
2017-03-05 05:30 | 0.72 | 0.31
2017-03-05 06:00 | 14.07 | 13.83
2017-03-05 06:30 | 10.71 | 10.57
2017-03-05 07:00 | 26.27 | 26.19
2017-03-05 07:30 | 33.29 | 33.29
2017-03-05 08:00 | 51.37 | 50.01
2017-03-05 08:30 | 80.71 | 80.16
2017-03-05 09:00 | 110.92 | 110.89
2017-03-05 09:30 | 116.95 | 116.9
2017-03-05 10:00 | 113.48 | 113.37
2017-03-05 10:30 | 113.86 | 113.6
2017-03-05 11:00 | 127.62 | 126.03
2017-03-05 11:30 | 129.43 | 127.85
2017-03-05 12:00 | 141.78 | 139.97
2017-03-05 12:30 | 145.46 | 143.75
2017-03-05 13:00 | 167.67 | 166.21
2017-03-05 13:30 | 180.22 | 178.79
2017-03-05 14:00 | 186.51 | 185.19
2017-03-05 14:30 | 207.29 | 205.15
2017-03-05 15:00 | 210.9 | 207.45
2017-03-05 15:30 | 230.76 | 227.24
2017-03-05 16:00 | 226.83 | 221.67
2017-03-05 16:30 | 240.71 | 235.65
2017-03-05 17:00 | 249.16 | 243.93
2017-03-05 17:30 | 251.52 | 246.19
2017-03-05 18:00 | 250.86 | 244.97
2017-03-05 18:30 | 247.83 | 241.33
2017-03-05 19:00 | 254.89 | 248.16
2017-03-05 19:30 | 247.07 | 241.22
2017-03-05 20:00 | 234.04 | 229.03
2017-03-05 20:30 | 227.3 | 223.12
2017-03-05 21:00 | 212.12 | 209.56
2017-03-05 21:30 | 191.22 | 190.85
2017-03-05 22:00 | 167.04 | 166.82
2017-03-05 22:30 | 167.87 | 165.81
2017-03-05 23:00 | 166.53 | 165.23
2017-03-05 23:30 | 136.02 | 135.91
2017-03-06 | 85.58 | 85.48
2017-03-06 00:30 | 68.39 | 68.33
2017-03-06 01:00 | 55.94 | 55.93
2017-03-06 01:30 | 46.79 | 46.78
2017-03-06 02:00 | 34.08 | 33.62
2017-03-06 02:30 | 24.96 | 24.56
2017-03-06 03:00 | 27.38 | 26.59
2017-03-06 03:30 | 26.86 | 26.14
2017-03-06 04:00 | 21.98 | 21.45
2017-03-06 04:30 | 3.79 | -3.79
2017-03-06 05:00 | 7.01 | 7
2017-03-06 05:30 | 19.77 | 19.69
2017-03-06 06:00 | 44.31 | 44.31
2017-03-06 06:30 | 91.5 | 91.04
2017-03-06 07:00 | 94.81 | 94.48
2017-03-06 07:30 | 138.68 | 138.33
2017-03-06 08:00 | 157.55 | 154.19
2017-03-06 08:30 | 168.49 | 164.07
2017-03-06 09:00 | 169.07 | 162.63
2017-03-06 09:30 | 180.95 | 174.65
2017-03-06 10:00 | 183.93 | 181.1
2017-03-06 10:30 | 192.57 | 191.02
2017-03-06 11:00 | 185.69 | 183.9
2017-03-06 11:30 | 200.17 | 198.5
2017-03-06 12:00 | 209.25 | 207.55
2017-03-06 12:30 | 214.47 | 212.71
2017-03-06 13:00 | 214.3 | 212.06
2017-03-06 13:30 | 220.72 | 217.51
2017-03-06 14:00 | 229.77 | 226.98
2017-03-06 14:30 | 231.94 | 229.54
2017-03-06 15:00 | 221.21 | 219.16
2017-03-06 15:30 | 222.15 | 220.37
2017-03-06 16:00 | 241.89 | 240.11
2017-03-06 16:30 | 245.33 | 243.46
2017-03-06 17:00 | 250.02 | 248.11
2017-03-06 17:30 | 245.91 | 243.65
2017-03-06 18:00 | 247.64 | 243.88
2017-03-06 18:30 | 247.74 | 245.96
2017-03-06 19:00 | 245.37 | 244.21
2017-03-06 19:30 | 240.1 | 239.55
2017-03-06 20:00 | 238.26 | 238.11
2017-03-06 20:30 | 217.36 | 217.34
2017-03-06 21:00 | 197.37 | 197.37
2017-03-06 21:30 | 180.99 | 180.98
2017-03-06 22:00 | 151.2 | 151
2017-03-06 22:30 | 148.59 | 148.24
2017-03-06 23:00 | 167.59 | 167.16
2017-03-06 23:30 | 131.59 | 131.17
2017-03-07 | 79.32 | 78.62
2017-03-07 00:30 | 59.81 | 58.66
2017-03-07 01:00 | 49.46 | 47.33
2017-03-07 01:30 | 51.79 | 48.75
2017-03-07 02:00 | 23.12 | 9.65
2017-03-07 02:30 | 36.67 | 28.13
2017-03-07 03:00 | 34.09 | 24.46
2017-03-07 03:30 | 43.62 | 36.85
2017-03-07 04:00 | 57.25 | 52.32
2017-03-07 04:30 | 19.49 | -2.46
2017-03-07 05:00 | 20.34 | 8.08
2017-03-07 05:30 | 38.28 | 34.68
2017-03-07 06:00 | 66.95 | 64.84
2017-03-07 06:30 | 86.99 | 85.71
2017-03-07 07:00 | 91.74 | 91.24
2017-03-07 07:30 | 120.17 | 120.08
2017-03-07 08:00 | 121.57 | 121.35
2017-03-07 08:30 | 103.96 | 103.55
2017-03-07 09:00 | 100.02 | 99.6
2017-03-07 09:30 | 113.07 | 112.73
2017-03-07 10:00 | 103.84 | 103.36
2017-03-07 10:30 | 110.25 | 109.6
2017-03-07 11:00 | 108.09 | 107.19
2017-03-07 11:30 | 107.28 | 106.61
2017-03-07 12:00 | 115.21 | 114.83
2017-03-07 12:30 | 135.28 | 134.94
2017-03-07 13:00 | 143.32 | 142.93
2017-03-07 13:30 | 151.71 | 150.82
2017-03-07 14:00 | 145.17 | 144.69
2017-03-07 14:30 | 158.9 | 158.29
2017-03-07 15:00 | 185.38 | 184.81
2017-03-07 15:30 | 192.07 | 191.61
2017-03-07 16:00 | 193.91 | 193.51
2017-03-07 16:30 | 200.31 | 200.05
2017-03-07 17:00 | 215.95 | 215.8
2017-03-07 17:30 | 223.77 | 223.72
2017-03-07 18:00 | 207.62 | 207.16
2017-03-07 18:30 | 198.09 | 197.34
2017-03-07 19:00 | 218.18 | 216.95
2017-03-07 19:30 | 205.53 | 204.47
2017-03-07 20:00 | 199.22 | 198.48
2017-03-07 20:30 | 188.99 | 188.85
2017-03-07 21:00 | 177.04 | 176.95
2017-03-07 21:30 | 170.62 | 170.53
2017-03-07 22:00 | 150.94 | 150.64
2017-03-07 22:30 | 144.95 | 144.64
2017-03-07 23:00 | 147.79 | 147.49
2017-03-07 23:30 | 109.94 | 109.41
2017-03-08 | 73.74 | 72.64
2017-03-08 00:30 | 51.37 | 50.93
2017-03-08 01:00 | 44.91 | 44.71
2017-03-08 01:30 | 46 | 45.82
2017-03-08 02:00 | 41.14 | 40.92
2017-03-08 02:30 | 26.41 | 26.4
2017-03-08 03:00 | 7.27 | 6.22
2017-03-08 03:30 | 4.85 | 3.49
2017-03-08 04:00 | 8.18 | 7.15
2017-03-08 04:30 | 13.17 | 12.58
2017-03-08 05:00 | 16.09 | 15.8
2017-03-08 05:30 | 26.86 | 26.82
2017-03-08 06:00 | 18.38 | 18.37
2017-03-08 06:30 | 33.2 | 30.18
2017-03-08 07:00 | 42.26 | 40.85
2017-03-08 07:30 | 66.42 | 66.06
2017-03-08 08:00 | 90 | 89.79
2017-03-08 08:30 | 89.07 | 88.89
2017-03-08 09:00 | 83.07 | 83.05
2017-03-08 09:30 | 92.64 | 92.34
2017-03-08 10:00 | 94.03 | 93.64
2017-03-08 10:30 | 83.45 | 82.91
2017-03-08 11:00 | 88.06 | 87.28
2017-03-08 11:30 | 78.24 | 77.05
2017-03-08 12:00 | 78.76 | 77.35
2017-03-08 12:30 | 65.74 | 64.32
2017-03-08 13:00 | 62.12 | 60.42
2017-03-08 13:30 | 76.29 | 74.68
2017-03-08 14:00 | 92.31 | 89.61
2017-03-08 14:30 | 95.4 | 93.29
2017-03-08 15:00 | 102.34 | 101.14
2017-03-08 15:30 | 114.31 | 113.38
2017-03-08 16:00 | 112.95 | 112.08
2017-03-08 16:30 | 116.24 | 115.63
2017-03-08 17:00 | 121.01 | 120.45
2017-03-08 17:30 | 113.06 | 110.86
2017-03-08 18:00 | 106.23 | 102.65
2017-03-08 18:30 | 127.22 | 124.07
2017-03-08 19:00 | 156.51 | 153.45
2017-03-08 19:30 | 145.14 | 142.38
2017-03-08 20:00 | 135.65 | 133.44
2017-03-08 20:30 | 122.47 | 120.8
2017-03-08 21:00 | 108.52 | 107.36
2017-03-08 21:30 | 83.58 | 77.71
2017-03-08 22:00 | 53.26 | 43.65
2017-03-08 22:30 | 50.47 | 48.47
2017-03-08 23:00 | 73.64 | 72.46
2017-03-08 23:30 | 55.84 | 55.81
2017-03-09 | 8.88 | 7.92
2017-03-09 00:30 | 7.8 | 4.08
2017-03-09 01:00 | 9.54 | 2.9
2017-03-09 01:30 | 10.65 | -5.5
2017-03-09 02:00 | 11.62 | -8.73
2017-03-09 02:30 | 14.26 | -11.79
2017-03-09 03:00 | 17.5 | -16.18
2017-03-09 03:30 | 14.68 | -12.09
2017-03-09 04:00 | 11.65 | -3.75
2017-03-09 04:30 | 10.19 | -1.85
2017-03-09 05:00 | 13.79 | -12.52
2017-03-09 05:30 | 5.04 | -3.58
2017-03-09 06:00 | 11.13 | 7.83
2017-03-09 06:30 | 13.47 | -13.47
2017-03-09 07:00 | 25.62 | -24.5
2017-03-09 07:30 | 26.24 | -9.3
2017-03-09 08:00 | 34.42 | -27
2017-03-09 08:30 | 39.84 | -29.14
2017-03-09 09:00 | 40.84 | -32.46
2017-03-09 09:30 | 39.25 | -30
2017-03-09 10:00 | 47.83 | -36.01
2017-03-09 10:30 | 50.01 | -29.89
2017-03-09 11:00 | 61.47 | -40.63
2017-03-09 11:30 | 62.12 | -43.49
2017-03-09 12:00 | 62.3 | -43.56
2017-03-09 12:30 | 57.74 | -42.96
2017-03-09 13:00 | 47.44 | -34.33
2017-03-09 13:30 | 45.14 | -31.81
2017-03-09 14:00 | 37.79 | -22.23
2017-03-09 14:30 | 20.95 | 1.47
2017-03-09 15:00 | 77.54 | 76.77
2017-03-09 15:30 | 92.1 | 91.59
2017-03-09 16:00 | 120.52 | 120.15
2017-03-09 16:30 | 150.58 | 150.31
2017-03-09 17:00 | 153.49 | 153.31
2017-03-09 17:30 | 148.11 | 148
2017-03-09 18:00 | 150.89 | 148.73
2017-03-09 18:30 | 157.08 | 154.26
2017-03-09 19:00 | 170.14 | 166.61
2017-03-09 19:30 | 175.33 | 172.19
2017-03-09 20:00 | 161.5 | 159.66
2017-03-09 20:30 | 134.74 | 134.53
2017-03-09 21:00 | 123.26 | 123.21
2017-03-09 21:30 | 88.58 | 88.54
2017-03-09 22:00 | 74.97 | 74.97
2017-03-09 22:30 | 65.74 | 65.72
2017-03-09 23:00 | 87.85 | 87.74
2017-03-09 23:30 | 65.77 | 65.23
2017-03-10 | 19.69 | 15.5
2017-03-10 00:30 | 18.72 | -2.52
2017-03-10 01:00 | 23.36 | -15.01
2017-03-10 01:30 | 30.95 | -25.28
2017-03-10 02:00 | 27.81 | -19.56
2017-03-10 02:30 | 31.94 | -25.62
2017-03-10 03:00 | 39.34 | -35.5
2017-03-10 03:30 | 41.84 | -38.35
2017-03-10 04:00 | 42.3 | -38.14
2017-03-10 04:30 | 36.53 | -30.94
2017-03-10 05:00 | 29.95 | -22.65
2017-03-10 05:30 | 23.33 | -15.83
2017-03-10 06:00 | 19.65 | 4.83
2017-03-10 06:30 | 31.24 | 26.14
2017-03-10 07:00 | 39.36 | 37.14
2017-03-10 07:30 | 33.86 | 33.35
2017-03-10 08:00 | 36.48 | 35.96
2017-03-10 08:30 | 29.7 | 29.69
2017-03-10 09:00 | 36.21 | 35.92
2017-03-10 09:30 | 39.67 | 38.65
2017-03-10 10:00 | 40.65 | 38.91
2017-03-10 10:30 | 42.69 | 40.51
2017-03-10 11:00 | 44.71 | 41.98
2017-03-10 11:30 | 36.71 | 32.38
2017-03-10 12:00 | 41.3 | 37.45
2017-03-10 12:30 | 50.68 | 46.47
2017-03-10 13:00 | 55.66 | 51.98
2017-03-10 13:30 | 64.13 | 61.35
2017-03-10 14:00 | 75.33 | 73.16
2017-03-10 14:30 | 97.06 | 95.46
2017-03-10 15:00 | 88.41 | 86.6
2017-03-10 15:30 | 104.31 | 103.17
2017-03-10 16:00 | 129.16 | 128.47
2017-03-10 16:30 | 156.44 | 155.98
2017-03-10 17:00 | 167.5 | 167.09
2017-03-10 17:30 | 168.31 | 167.51
2017-03-10 18:00 | 147.83 | 144.8
2017-03-10 18:30 | 138.43 | 135.58
2017-03-10 19:00 | 163.93 | 160.65
2017-03-10 19:30 | 148.99 | 146
2017-03-10 20:00 | 134.08 | 132.56
2017-03-10 20:30 | 117.05 | 116.76
2017-03-10 21:00 | 82.89 | 82.7
2017-03-10 21:30 | 61.37 | 61.18
2017-03-10 22:00 | 57.31 | 57.26
2017-03-10 22:30 | 87.97 | 87.96
2017-03-10 23:00 | 109.32 | 108.31
2017-03-10 23:30 | 74.99 | 73.15
2017-03-11 | 25.23 | 18.49
2017-03-11 00:30 | 23.46 | 12.81
2017-03-11 01:00 | 23.17 | 10.23
2017-03-11 01:30 | 22.18 | 8.79
2017-03-11 02:00 | 21.07 | -9.99
2017-03-11 02:30 | 27.39 | -21.04
2017-03-11 03:00 | 36.55 | -32.9
2017-03-11 03:30 | 40.07 | -37.43
2017-03-11 04:00 | 42.63 | -40.07
2017-03-11 04:30 | 39.95 | -36.24
2017-03-11 05:00 | 39.8 | -35.73
2017-03-11 05:30 | 29.63 | -21.87
2017-03-11 06:00 | 26.2 | -17.44
2017-03-11 06:30 | 20.54 | -2.93
2017-03-11 07:00 | 19.26 | 1.58
2017-03-11 07:30 | 24.74 | 17.1
2017-03-11 08:00 | 25.76 | 21.56
2017-03-11 08:30 | 21.36 | 19.66
2017-03-11 09:00 | 33.62 | 33.08
2017-03-11 09:30 | 36.1 | 35.94
2017-03-11 10:00 | 23.17 | 23.08
2017-03-11 10:30 | 30.31 | 30.29
2017-03-11 11:00 | 32.46 | 32.45
2017-03-11 11:30 | 43.83 | 43.81
2017-03-11 12:00 | 46.02 | 46.01
2017-03-11 12:30 | 51.76 | 51.75
2017-03-11 13:00 | 52.5 | 52.49
2017-03-11 13:30 | 57.97 | 57.97
2017-03-11 14:00 | 94.52 | 94.52
2017-03-11 14:30 | 102.41 | 102.41
2017-03-11 15:00 | 123.09 | 123.09
2017-03-11 15:30 | 142.14 | 142.14
2017-03-11 16:00 | 160.96 | 160.96
2017-03-11 16:30 | 156.49 | 156.49
2017-03-11 17:00 | 173.64 | 173.64
2017-03-11 17:30 | 182.07 | 182.05
2017-03-11 18:00 | 183.27 | 183.21
2017-03-11 18:30 | 190.71 | 190.69
2017-03-11 19:00 | 209.54 | 209.54
2017-03-11 19:30 | 204.16 | 204.16
2017-03-11 20:00 | 202.9 | 202.86
2017-03-11 20:30 | 191.56 | 191.46
2017-03-11 21:00 | 171.34 | 171.19
2017-03-11 21:30 | 163.92 | 163.83
2017-03-11 22:00 | 139.18 | 139.16
2017-03-11 22:30 | 139.88 | 139.88
2017-03-11 23:00 | 155.31 | 155.3
2017-03-11 23:30 | 133.32 | 133.22
2017-03-12 | 89.7 | 89.24
2017-03-12 00:30 | 86.54 | 82.77
2017-03-12 01:00 | 79.3 | 74.39
2017-03-12 01:30 | 60.38 | 53.77
2017-03-12 02:00 | 54.93 | 47.68
2017-03-12 02:30 | 48.79 | 40.8
2017-03-12 03:00 | 40.33 | 30.57
2017-03-12 03:30 | 38.57 | 28.3
2017-03-12 04:00 | 33.71 | 21.7
2017-03-12 04:30 | 34.36 | 23.31
2017-03-12 05:00 | 28.16 | 13.86
2017-03-12 05:30 | 32.11 | 20.09
2017-03-12 06:00 | 31.77 | 20.76
2017-03-12 06:30 | 38.12 | 29.81
2017-03-12 07:00 | 40.63 | 32.45
2017-03-12 07:30 | 51.89 | 46.65
2017-03-12 08:00 | 46.37 | 42.12
2017-03-12 08:30 | 50.21 | 47.53
2017-03-12 09:00 | 66.11 | 64.84
2017-03-12 09:30 | 99.25 | 99.22
2017-03-12 10:00 | 112.05 | 111.43
2017-03-12 10:30 | 123.51 | 123.5
2017-03-12 11:00 | 114.47 | 114.47
2017-03-12 11:30 | 113.78 | 113.77
2017-03-12 12:00 | 117.53 | 117.48
2017-03-12 12:30 | 136.26 | 136.21
2017-03-12 13:00 | 146.7 | 146.69
2017-03-12 13:30 | 151.08 | 151.08
2017-03-12 14:00 | 160 | 159.98
2017-03-12 14:30 | 179.16 | 179.11
2017-03-12 15:00 | 194.19 | 194.14
2017-03-12 15:30 | 190.71 | 190.63
2017-03-12 16:00 | 189.85 | 189.72
2017-03-12 16:30 | 199.18 | 199.07
2017-03-12 17:00 | 220.35 | 220.08
2017-03-12 17:30 | 232.37 | 232.2
2017-03-12 18:00 | 234.59 | 234.42
2017-03-12 18:30 | 237.36 | 237.03
2017-03-12 19:00 | 243.44 | 242.87
2017-03-12 19:30 | 237.78 | 237.44
2017-03-12 20:00 | 233.51 | 233.32
2017-03-12 20:30 | 222.33 | 220.18
2017-03-12 21:00 | 211.95 | 211.46
2017-03-12 21:30 | 202.59 | 202.48
2017-03-12 22:00 | 187.54 | 187.5
2017-03-12 22:30 | 186.86 | 186.83
2017-03-12 23:00 | 186.51 | 186.49
2017-03-12 23:30 | 163.89 | 163.44
2017-03-13 | 121.65 | 120.23
2017-03-13 00:30 | 103.42 | 101.24
2017-03-13 01:00 | 106.9 | 104.51
2017-03-13 01:30 | 97.92 | 94.99
2017-03-13 02:00 | 87.34 | 84.06
2017-03-13 02:30 | 75.46 | 71.9
2017-03-13 03:00 | 68.74 | 64.61
2017-03-13 03:30 | 67.07 | 62.92
2017-03-13 04:00 | 61.98 | 57.63
2017-03-13 04:30 | 60.49 | 56.59
2017-03-13 05:00 | 68.04 | 64.98
2017-03-13 05:30 | 82.71 | 81.48
2017-03-13 06:00 | 106.45 | 105.64
2017-03-13 06:30 | 127.09 | 126.72
2017-03-13 07:00 | 162 | 162
2017-03-13 07:30 | 194.74 | 194.69
2017-03-13 08:00 | 208.81 | 208.56
2017-03-13 08:30 | 209.67 | 209.08
2017-03-13 09:00 | 198.45 | 197.1
2017-03-13 09:30 | 209.02 | 206.46
2017-03-13 10:00 | 213.54 | 211.31
2017-03-13 10:30 | 178.12 | 176.33
2017-03-13 11:00 | 161.62 | 159.47
2017-03-13 11:30 | 157.74 | 155.68
2017-03-13 12:00 | 149.59 | 147.95
2017-03-13 12:30 | 144.48 | 143.1
2017-03-13 13:00 | 146.52 | 145.27
2017-03-13 13:30 | 159.57 | 158
2017-03-13 14:00 | 174.8 | 173.43
2017-03-13 14:30 | 176.88 | 175.47
2017-03-13 15:00 | 180.29 | 179
2017-03-13 15:30 | 185.41 | 184.19
2017-03-13 16:00 | 200.57 | 199.61
2017-03-13 16:30 | 199.88 | 199.13
2017-03-13 17:00 | 214.76 | 213.95
2017-03-13 17:30 | 216.26 | 215.46
2017-03-13 18:00 | 212.76 | 211.73
2017-03-13 18:30 | 227.88 | 226.49
2017-03-13 19:00 | 245.36 | 243.69
2017-03-13 19:30 | 234.41 | 233.08
2017-03-13 20:00 | 230.54 | 229.62
2017-03-13 20:30 | 224.78 | 223.28
2017-03-13 21:00 | 210.36 | 208.16
2017-03-13 21:30 | 199.4 | 197.62
2017-03-13 22:00 | 179.19 | 177.64
2017-03-13 22:30 | 169.84 | 168.22
2017-03-13 23:00 | 177.16 | 175.74
2017-03-13 23:30 | 143.31 | 143.21
2017-03-14 | 84.16 | 82.19
2017-03-14 00:30 | 67.13 | 63.8
2017-03-14 01:00 | 61.16 | 56.73
2017-03-14 01:30 | 47.97 | 41.6
2017-03-14 02:00 | 43.02 | 35.32
2017-03-14 02:30 | 30.74 | 19.48
2017-03-14 03:00 | 26.59 | 12.38
2017-03-14 03:30 | 26.53 | 13.17
2017-03-14 04:00 | 34.02 | 24.98
2017-03-14 04:30 | 38.12 | 31.34
2017-03-14 05:00 | 41.77 | 36.32
2017-03-14 05:30 | 62.47 | 60.43
2017-03-14 06:00 | 57.39 | 55.88
2017-03-14 06:30 | 82.93 | 82.24
2017-03-14 07:00 | 124.11 | 124.05
2017-03-14 07:30 | 136.36 | 135.95
2017-03-14 08:00 | 138.61 | 138.14
2017-03-14 08:30 | 134.54 | 134.27
2017-03-14 09:00 | 149.88 | 148.91
2017-03-14 09:30 | 166.49 | 165.39
2017-03-14 10:00 | 155.49 | 154.56
2017-03-14 10:30 | 145.57 | 144.94
2017-03-14 11:00 | 128.46 | 127.58
2017-03-14 11:30 | 130.36 | 129.81
2017-03-14 12:00 | 136.28 | 135.85
2017-03-14 12:30 | 119.38 | 118.72
2017-03-14 13:00 | 89.16 | 87.31
2017-03-14 13:30 | 84.14 | 79.38
2017-03-14 14:00 | 99.46 | 95.16
2017-03-14 14:30 | 124.78 | 121.36
2017-03-14 15:00 | 134.15 | 131.38
2017-03-14 15:30 | 131.19 | 128.84
2017-03-14 16:00 | 153.49 | 151.13
2017-03-14 16:30 | 160.28 | 158.41
2017-03-14 17:00 | 184.84 | 182.98
2017-03-14 17:30 | 191.27 | 189.06
2017-03-14 18:00 | 203.34 | 200.71
2017-03-14 18:30 | 216.63 | 213.81
2017-03-14 19:00 | 203.86 | 200.81
2017-03-14 19:30 | 187.01 | 184.15
2017-03-14 20:00 | 183.41 | 181.06
2017-03-14 20:30 | 179.72 | 178.17
2017-03-14 21:00 | 175.72 | 174.46
2017-03-14 21:30 | 166.97 | 166.84
2017-03-14 22:00 | 165.43 | 164.87
2017-03-14 22:30 | 163.32 | 162.95
2017-03-14 23:00 | 181.98 | 181.72
2017-03-14 23:30 | 151.37 | 151.37
2017-03-15 | 100.38 | 99.23
2017-03-15 00:30 | 104.19 | 104.12
2017-03-15 01:00 | 103.91 | 103.65
2017-03-15 01:30 | 95.84 | 95.45
2017-03-15 02:00 | 73.86 | 73.29
2017-03-15 02:30 | 70.67 | 70.11
2017-03-15 03:00 | 67.56 | 66.99
2017-03-15 03:30 | 68.19 | 67.68
2017-03-15 04:00 | 73.53 | 73.21
2017-03-15 04:30 | 72.35 | 72.21
2017-03-15 05:00 | 70 | 69.96
2017-03-15 05:30 | 88.48 | 88.44
2017-03-15 06:00 | 112.52 | 112.31
2017-03-15 06:30 | 163.32 | 163.14
2017-03-15 07:00 | 155.49 | 155.49
2017-03-15 07:30 | 164.26 | 164.24
2017-03-15 08:00 | 157.03 | 156.05
2017-03-15 08:30 | 152.8 | 148.99
2017-03-15 09:00 | 155.78 | 151.2
2017-03-15 09:30 | 151.93 | 145.9
2017-03-15 10:00 | 177.85 | 172.13
2017-03-15 10:30 | 178.87 | 173.38
2017-03-15 11:00 | 94.05 | 81.16
2017-03-15 11:30 | 100.04 | 95.5
2017-03-15 12:00 | 156.25 | 154.25
2017-03-15 12:30 | 135.26 | 133.11
2017-03-15 13:00 | 140.17 | 138.37
2017-03-15 13:30 | 145.53 | 143.92
2017-03-15 14:00 | 154.51 | 152.62
2017-03-15 14:30 | 165.37 | 163.84
2017-03-15 15:00 | 156.91 | 155.52
2017-03-15 15:30 | 158.56 | 157.27
2017-03-15 16:00 | 153.58 | 152.17
2017-03-15 16:30 | 167.9 | 165.98
2017-03-15 17:00 | 186.54 | 182.36
2017-03-15 17:30 | 199.71 | 193.09
2017-03-15 18:00 | 197.76 | 192.02
2017-03-15 18:30 | 213.23 | 207.78
2017-03-15 19:00 | 204.59 | 198.87
2017-03-15 19:30 | 187.16 | 181.9
2017-03-15 20:00 | 178.69 | 173.91
2017-03-15 20:30 | 155.06 | 150.77
2017-03-15 21:00 | 161.49 | 160.14
2017-03-15 21:30 | 139.37 | 139.37
2017-03-15 22:00 | 105.15 | 104.71
2017-03-15 22:30 | 98.99 | 98.55
2017-03-15 23:00 | 115.84 | 115.26
2017-03-15 23:30 | 93.37 | 92.21
2017-03-16 | 51.66 | 48.82
2017-03-16 00:30 | 53.68 | 50.05
2017-03-16 01:00 | 53.48 | 48.78
2017-03-16 01:30 | 39.67 | 32.55
2017-03-16 02:00 | 36.25 | 26.8
2017-03-16 02:30 | 39.66 | 31.01
2017-03-16 03:00 | 35.82 | 26.06
2017-03-16 03:30 | 27.52 | 14.14
2017-03-16 04:00 | 22.77 | 5.52
2017-03-16 04:30 | 24.29 | 12.42
2017-03-16 05:00 | 26.29 | 17.05
2017-03-16 05:30 | 41.17 | 38
2017-03-16 06:00 | 49.04 | 46.79
2017-03-16 06:30 | 53.05 | 52.04
2017-03-16 07:00 | 67.29 | 67.28
2017-03-16 07:30 | 80.42 | 79.96
2017-03-16 08:00 | 94.19 | 92.32
2017-03-16 08:30 | 85.04 | 79.41
2017-03-16 09:00 | 84.06 | 80.26
2017-03-16 09:30 | 94.64 | 92.48
2017-03-16 10:00 | 118.23 | 114.22
2017-03-16 10:30 | 118.32 | 114.72
2017-03-16 11:00 | 121.32 | 117.68
2017-03-16 11:30 | 123.04 | 119.14
2017-03-16 12:00 | 125.71 | 122.02
2017-03-16 12:30 | 138.18 | 136.02
2017-03-16 13:00 | 138.25 | 135.57
2017-03-16 13:30 | 139.74 | 137.09
2017-03-16 14:00 | 155.22 | 152.72
2017-03-16 14:30 | 150.18 | 147.87
2017-03-16 15:00 | 143.28 | 141.58
2017-03-16 15:30 | 151.54 | 146.55
2017-03-16 16:00 | 158.89 | 150.61
2017-03-16 16:30 | 155 | 146.64
2017-03-16 17:00 | 156.31 | 147.58
2017-03-16 17:30 | 157.97 | 148.4
2017-03-16 18:00 | 155.29 | 145.68
2017-03-16 18:30 | 153.59 | 149.82
2017-03-16 19:00 | 217.26 | 214.95
2017-03-16 19:30 | 209.37 | 207.02
2017-03-16 20:00 | 199.2 | 194.44
2017-03-16 20:30 | 202.06 | 198.42
2017-03-16 21:00 | 198.31 | 197.09
2017-03-16 21:30 | 180.73 | 180.14
2017-03-16 22:00 | 145.93 | 145.89
2017-03-16 22:30 | 152.81 | 152.61
2017-03-16 23:00 | 163.67 | 163.58
2017-03-16 23:30 | 122.83 | 122.81
2017-03-17 | 73.69 | 73.69
2017-03-17 00:30 | 61.27 | 61.14
2017-03-17 01:00 | 61.63 | 59.39
2017-03-17 01:30 | 56.58 | 54.7
2017-03-17 02:00 | 51.66 | 49.35
2017-03-17 02:30 | 37.2 | 33.97
2017-03-17 03:00 | 25.04 | 20.13
2017-03-17 03:30 | 23.81 | 18.64
2017-03-17 04:00 | 17.35 | 9.41
2017-03-17 04:30 | 17.7 | 11.22
2017-03-17 05:00 | 22.97 | 19.21
2017-03-17 05:30 | 47.76 | 46.52
2017-03-17 06:00 | 45.31 | 43.8
2017-03-17 06:30 | 20.79 | 20.76
2017-03-17 07:00 | 64.72 | 62.53
2017-03-17 07:30 | 92.72 | 82.82
2017-03-17 08:00 | 107.69 | 92.19
2017-03-17 08:30 | 130.83 | 114.41
2017-03-17 09:00 | 152.4 | 139.55
2017-03-17 09:30 | 169.77 | 159.49
2017-03-17 10:00 | 175.81 | 164.7
2017-03-17 10:30 | 179.75 | 168.85
2017-03-17 11:00 | 187.34 | 178.78
2017-03-17 11:30 | 195.59 | 186.98
2017-03-17 12:00 | 206.15 | 197.16
2017-03-17 12:30 | 229.95 | 221.17
2017-03-17 13:00 | 243.51 | 235.48
2017-03-17 13:30 | 244.5 | 237.04
2017-03-17 14:00 | 235.2 | 228.18
2017-03-17 14:30 | 230.25 | 223.22
2017-03-17 15:00 | 231.81 | 224.94
2017-03-17 15:30 | 255.74 | 249.69
2017-03-17 16:00 | 254.63 | 248.92
2017-03-17 16:30 | 245.87 | 241.09
2017-03-17 17:00 | 239.8 | 237.95
2017-03-17 17:30 | 232.19 | 231.45
2017-03-17 18:00 | 217.43 | 217.16
2017-03-17 18:30 | 221.45 | 221.26
2017-03-17 19:00 | 232.91 | 232.58
2017-03-17 19:30 | 224.03 | 223.83
2017-03-17 20:00 | 206.22 | 206.1
2017-03-17 20:30 | 195.16 | 195.13
2017-03-17 21:00 | 158.65 | 157.99
2017-03-17 21:30 | 146.09 | 145.35
2017-03-17 22:00 | 134.72 | 134.29
2017-03-17 22:30 | 145.06 | 144.78
2017-03-17 23:00 | 139.61 | 139.44
2017-03-17 23:30 | 109.88 | 109.47
2017-03-18 | 75.62 | 75.37
2017-03-18 00:30 | 78.56 | 78.51
2017-03-18 01:00 | 68.21 | 68.2
2017-03-18 01:30 | 56.49 | 56.49
2017-03-18 02:00 | 41.95 | 41.94
2017-03-18 02:30 | 33.12 | 33.09
2017-03-18 03:00 | 18.62 | 18.58
2017-03-18 03:30 | 20.31 | 17.42
2017-03-18 04:00 | 17.92 | 6.2
2017-03-18 04:30 | 18.59 | 10.62
2017-03-18 05:00 | 26.72 | 22.36
2017-03-18 05:30 | 35.5 | 33.18
2017-03-18 06:00 | 28.95 | 26.07
2017-03-18 06:30 | 30.91 | 28.9
2017-03-18 07:00 | 41.37 | 40.85
2017-03-18 07:30 | 66.29 | 66.28
2017-03-18 08:00 | 88.61 | 79.17
2017-03-18 08:30 | 92.77 | 75.57
2017-03-18 09:00 | 103.95 | 86.5
2017-03-18 09:30 | 98.11 | 77.32
2017-03-18 10:00 | 110.67 | 90.46
2017-03-18 10:30 | 111.74 | 90.65
2017-03-18 11:00 | 114.56 | 93.62
2017-03-18 11:30 | 127.6 | 108.88
2017-03-18 12:00 | 132.01 | 113.68
2017-03-18 12:30 | 142.74 | 125.43
2017-03-18 13:00 | 155.21 | 141.04
2017-03-18 13:30 | 166.19 | 155.14
2017-03-18 14:00 | 173.49 | 165.13
2017-03-18 14:30 | 174.63 | 165.73
2017-03-18 15:00 | 181.93 | 172.78
2017-03-18 15:30 | 192.35 | 183.32
2017-03-18 16:00 | 190.79 | 182.21
2017-03-18 16:30 | 186.93 | 178.66
2017-03-18 17:00 | 197.43 | 189.64
2017-03-18 17:30 | 193.41 | 186.27
2017-03-18 18:00 | 168.91 | 160.93
2017-03-18 18:30 | 180.21 | 172.51
2017-03-18 19:00 | 201.03 | 193.99
2017-03-18 19:30 | 191.3 | 184.03
2017-03-18 20:00 | 191.48 | 184.61
2017-03-18 20:30 | 214.97 | 209.58
2017-03-18 21:00 | 214.56 | 209.86
2017-03-18 21:30 | 208.67 | 201.19
2017-03-18 22:00 | 190.11 | 183.02
2017-03-18 22:30 | 190.81 | 184.58
2017-03-18 23:00 | 207.16 | 202.12
2017-03-18 23:30 | 179.64 | 178.05
2017-03-19 | 132.71 | 132.35
2017-03-19 00:30 | 117.58 | 117.41
2017-03-19 01:00 | 95.34 | 95.3
2017-03-19 01:30 | 72.3 | 72.3
2017-03-19 02:00 | 55.16 | 55.16
2017-03-19 02:30 | 45.98 | 45.96
2017-03-19 03:00 | 30.81 | 30.78
2017-03-19 03:30 | 29.68 | 29.61
2017-03-19 04:00 | 16.68 | 16.6
2017-03-19 04:30 | 18.97 | 18.76
2017-03-19 05:00 | 21.36 | 21.13
2017-03-19 05:30 | 21.52 | 21.4
2017-03-19 06:00 | 23.78 | 23.69
2017-03-19 06:30 | 27.7 | 27.61
2017-03-19 07:00 | 28.18 | 28.15
2017-03-19 07:30 | 49.7 | 49.66
2017-03-19 08:00 | 64.58 | 64.37
2017-03-19 08:30 | 65.23 | 64.53
2017-03-19 09:00 | 58.46 | 57.27
2017-03-19 09:30 | 65.85 | 64.03
2017-03-19 10:00 | 79.23 | 74.63
2017-03-19 10:30 | 101.65 | 89.66
2017-03-19 11:00 | 107.06 | 80.53
2017-03-19 11:30 | 92.36 | 59.01
2017-03-19 12:00 | 97.01 | 63.65
2017-03-19 12:30 | 107.64 | 78.45
2017-03-19 13:00 | 114.89 | 91.99
2017-03-19 13:30 | 104.69 | 96.84
2017-03-19 14:00 | 93.31 | 86.01
2017-03-19 14:30 | 95.05 | 88.04
2017-03-19 15:00 | 85.1 | 77.53
2017-03-19 15:30 | 79.93 | 72.12
2017-03-19 16:00 | 75.83 | 68.31
2017-03-19 16:30 | 73.91 | 66.59
2017-03-19 17:00 | 76.34 | 69.48
2017-03-19 17:30 | 90.75 | 85.37
2017-03-19 18:00 | 108.5 | 103.78
2017-03-19 18:30 | 129.33 | 124.39
2017-03-19 19:00 | 152.97 | 148.43
2017-03-19 19:30 | 135.91 | 131.49
2017-03-19 20:00 | 142.18 | 134.12
2017-03-19 20:30 | 154.93 | 149.23
2017-03-19 21:00 | 122.96 | 122.28
2017-03-19 21:30 | 123.5 | 123.12
2017-03-19 22:00 | 106.4 | 106.1
2017-03-19 22:30 | 115.42 | 115.23
2017-03-19 23:00 | 127.4 | 127.32
2017-03-19 23:30 | 112.4 | 112.37
2017-03-20 | 67.5 | 67.46
2017-03-20 00:30 | 45.4 | 44.97
2017-03-20 01:00 | 35.5 | 35.12
2017-03-20 01:30 | 17.65 | 17.06
2017-03-20 02:00 | 11.38 | 10.39
2017-03-20 02:30 | 6.19 | -3.75
2017-03-20 03:00 | 14.99 | -13.64
2017-03-20 03:30 | 18.36 | -16.91
2017-03-20 04:00 | 18.8 | -17.01
2017-03-20 04:30 | 11.88 | -7.95
2017-03-20 05:00 | 13.64 | 9.61
2017-03-20 05:30 | 11.88 | 3.38
2017-03-20 06:00 | 13.03 | 12.9
2017-03-20 06:30 | 32.17 | 31.51
2017-03-20 07:00 | 56.6 | 55.77
2017-03-20 07:30 | 70.25 | 63.67
2017-03-20 08:00 | 61.21 | 50.38
2017-03-20 08:30 | 65.03 | 48.31
2017-03-20 09:00 | 84.41 | 68.91
2017-03-20 09:30 | 99.55 | 85.24
2017-03-20 10:00 | 84.68 | 76.25
2017-03-20 10:30 | 85.97 | 77.95
2017-03-20 11:00 | 82.67 | 74.36
2017-03-20 11:30 | 81.71 | 73.39
2017-03-20 12:00 | 71.04 | 61.87
2017-03-20 12:30 | 70.88 | 61.71
2017-03-20 13:00 | 89.92 | 83.93
2017-03-20 13:30 | 91.89 | 86.47
2017-03-20 14:00 | 97.4 | 92.82
2017-03-20 14:30 | 94.26 | 89.7
2017-03-20 15:00 | 87.59 | 83.07
2017-03-20 15:30 | 75.52 | 69.71
2017-03-20 16:00 | 83.7 | 73.72
2017-03-20 16:30 | 83.54 | 74.4
2017-03-20 17:00 | 102.22 | 95.32
2017-03-20 17:30 | 117.41 | 112.35
2017-03-20 18:00 | 122.09 | 117.66
2017-03-20 18:30 | 132.23 | 127.41
2017-03-20 19:00 | 134.68 | 129.93
2017-03-20 19:30 | 103.88 | 98.47
2017-03-20 20:00 | 105.23 | 100.76
2017-03-20 20:30 | 130.28 | 129.77
2017-03-20 21:00 | 125.91 | 125.9
2017-03-20 21:30 | 102.1 | 101.78
2017-03-20 22:00 | 93.26 | 93.21
2017-03-20 22:30 | 92.94 | 92.94
2017-03-20 23:00 | 108.91 | 108.9
2017-03-20 23:30 | 86.67 | 86.61
2017-03-21 | 43.28 | 42.7
2017-03-21 00:30 | 50.67 | 49.97
2017-03-21 01:00 | 38.4 | 37.43
2017-03-21 01:30 | 17.93 | 15.59
2017-03-21 02:00 | 11.31 | 6.84
2017-03-21 02:30 | 18.69 | 16.06
2017-03-21 03:00 | 12.33 | 7.9
2017-03-21 03:30 | 16.35 | 13.23
2017-03-21 04:00 | 22.8 | 20.74
2017-03-21 04:30 | 18.62 | 16.72
2017-03-21 05:00 | 17.69 | -16.99
2017-03-21 05:30 | 37.69 | 37.57
2017-03-21 06:00 | 48.37 | 48.37
2017-03-21 06:30 | 61.84 | 61.69
2017-03-21 07:00 | 83.58 | 83.2
2017-03-21 07:30 | 110.47 | 110.4
2017-03-21 08:00 | 103.13 | 102.9
2017-03-21 08:30 | 113.81 | 110.2
2017-03-21 09:00 | 113.94 | 108.94
2017-03-21 09:30 | 113.22 | 107.68
2017-03-21 10:00 | 119.63 | 115.29
2017-03-21 10:30 | 119.61 | 115.82
2017-03-21 11:00 | 135 | 132.01
2017-03-21 11:30 | 117.12 | 114.8
2017-03-21 12:00 | 187.86 | 185.98
2017-03-21 12:30 | 128.05 | 125.17
2017-03-21 13:00 | 121.45 | 117.82
2017-03-21 13:30 | 122.4 | 118.76
2017-03-21 14:00 | 119.62 | 115.85
2017-03-21 14:30 | 119.84 | 116.11
2017-03-21 15:00 | 116.96 | 113.46
2017-03-21 15:30 | 118.46 | 115.35
2017-03-21 16:00 | 121.93 | 119.2
2017-03-21 16:30 | 125.8 | 123.44
2017-03-21 17:00 | 133.34 | 131.47
2017-03-21 17:30 | 140.77 | 139.59
2017-03-21 18:00 | 146.25 | 143.25
2017-03-21 18:30 | 164.79 | 161.73
2017-03-21 19:00 | 174.39 | 171.54
2017-03-21 19:30 | 148.42 | 145.32
2017-03-21 20:00 | 148.13 | 145.72
2017-03-21 20:30 | 136.91 | 135.15
2017-03-21 21:00 | 113.63 | 112.29
2017-03-21 21:30 | 117.66 | 116.13
2017-03-21 22:00 | 98.73 | 98.67
2017-03-21 22:30 | 91.39 | 91.32
2017-03-21 23:00 | 91.84 | 91.79
2017-03-21 23:30 | 71.1 | 71.09
2017-03-22 | 40.64 | 40.57
2017-03-22 00:30 | 28.68 | 28.46
2017-03-22 01:00 | 24.26 | 23.86
2017-03-22 01:30 | 19.52 | 18.57
2017-03-22 02:00 | 15.05 | 13.45
2017-03-22 02:30 | 13.92 | 12.11
2017-03-22 03:00 | 12.33 | 10.36
2017-03-22 03:30 | 10.42 | 8.28
2017-03-22 04:00 | 6.89 | 3.33
2017-03-22 04:30 | 7.42 | 5.59
2017-03-22 05:00 | 10.89 | 10.07
2017-03-22 05:30 | 46.9 | 46.87
2017-03-22 06:00 | 51.15 | 51.13
2017-03-22 06:30 | 62.27 | 62.2
2017-03-22 07:00 | 80.83 | 80.46
2017-03-22 07:30 | 98.9 | 98.69
2017-03-22 08:00 | 100.36 | 100.06
2017-03-22 08:30 | 112.07 | 109.21
2017-03-22 09:00 | 119.46 | 116.37
2017-03-22 09:30 | 121.66 | 117.64
2017-03-22 10:00 | 124.92 | 120.01
2017-03-22 10:30 | 132.98 | 124.72
2017-03-22 11:00 | 125.37 | 121.25
2017-03-22 11:30 | 123.07 | 119.14
2017-03-22 12:00 | 118.25 | 114.39
2017-03-22 12:30 | 120.51 | 116.67
2017-03-22 13:00 | 121.61 | 117.61
2017-03-22 13:30 | 126.61 | 122.54
2017-03-22 14:00 | 127.28 | 123.26
2017-03-22 14:30 | 125.79 | 122.04
2017-03-22 15:00 | 125.05 | 121.82
2017-03-22 15:30 | 120.75 | 117.95
2017-03-22 16:00 | 127.83 | 125.81
2017-03-22 16:30 | 138.16 | 136.67
2017-03-22 17:00 | 134.6 | 133.42
2017-03-22 17:30 | 128.9 | 127.08
2017-03-22 18:00 | 126.19 | 123.47
2017-03-22 18:30 | 153.41 | 147.08
2017-03-22 19:00 | 166.71 | 159.43
2017-03-22 19:30 | 149.24 | 142.18
2017-03-22 20:00 | 142.55 | 136.17
2017-03-22 20:30 | 132.91 | 126.61
2017-03-22 21:00 | 102.05 | 93.91
2017-03-22 21:30 | 84.16 | 80.12
2017-03-22 22:00 | 69.41 | 66.4
2017-03-22 22:30 | 64.4 | 61.53
2017-03-22 23:00 | 92.37 | 92.36
2017-03-22 23:30 | 78.97 | 78.91
2017-03-23 | 30 | 29.51
2017-03-23 00:30 | 16.11 | 14.59
2017-03-23 01:00 | 13.02 | 9.82
2017-03-23 01:30 | 10.07 | 4.59
2017-03-23 02:00 | 9.51 | 0.9
2017-03-23 02:30 | 9.77 | -0.65
2017-03-23 03:00 | 9.98 | -1.58
2017-03-23 03:30 | 7.9 | -1.17
2017-03-23 04:00 | 7.33 | -0.87
2017-03-23 04:30 | 6.69 | 2.38
2017-03-23 05:00 | 7.83 | 6.32
2017-03-23 05:30 | 33.83 | 33.8
2017-03-23 06:00 | 45.94 | 45.9
2017-03-23 06:30 | 62.91 | 62.51
2017-03-23 07:00 | 86.29 | 86.28
2017-03-23 07:30 | 103.76 | 103.76
2017-03-23 08:00 | 108.12 | 107.79
2017-03-23 08:30 | 130.97 | 127.1
2017-03-23 09:00 | 130.74 | 126.13
2017-03-23 09:30 | 137.41 | 121.98
2017-03-23 10:00 | 115.82 | 105.81
2017-03-23 10:30 | 128.23 | 118.81
2017-03-23 11:00 | 122.55 | 113.19
2017-03-23 11:30 | 114.55 | 104.13
2017-03-23 12:00 | 123.79 | 114
2017-03-23 12:30 | 125.67 | 115.41
2017-03-23 13:00 | 131.25 | 120.93
2017-03-23 13:30 | 138.71 | 128.33
2017-03-23 14:00 | 159.92 | 150.44
2017-03-23 14:30 | 160.64 | 156.21
2017-03-23 15:00 | 144.7 | 140.37
2017-03-23 15:30 | 141.29 | 137.79
2017-03-23 16:00 | 145.71 | 142.71
2017-03-23 16:30 | 150.65 | 148.27
2017-03-23 17:00 | 154.53 | 152.59
2017-03-23 17:30 | 153.94 | 152.39
2017-03-23 18:00 | 157.51 | 155.91
2017-03-23 18:30 | 173.6 | 171.72
2017-03-23 19:00 | 202.67 | 201.17
2017-03-23 19:30 | 168.23 | 166.91
2017-03-23 20:00 | 162.99 | 162.01
2017-03-23 20:30 | 175.44 | 175.28
2017-03-23 21:00 | 148.4 | 148.4
2017-03-23 21:30 | 105.87 | 105.87
2017-03-23 22:00 | 76.53 | 76.53
2017-03-23 22:30 | 80.83 | 80.77
2017-03-23 23:00 | 113.27 | 113.21
2017-03-23 23:30 | 78.5 | 78.44
2017-03-24 | 32.92 | 29.92
2017-03-24 00:30 | 26.19 | 16.06
2017-03-24 01:00 | 24.9 | 11.89
2017-03-24 01:30 | 22.31 | 6.75
2017-03-24 02:00 | 27.92 | 2.75
2017-03-24 02:30 | 28 | 1.18
2017-03-24 03:00 | 28 | 0.06
2017-03-24 03:30 | 27.8 | -0.51
2017-03-24 04:00 | 27.73 | -1.18
2017-03-24 04:30 | 27.94 | 1.03
2017-03-24 05:00 | 29.55 | 7.75
2017-03-24 05:30 | 36.14 | 20.27
2017-03-24 06:00 | 40.11 | 30.95
2017-03-24 06:30 | 55.3 | 49.55
2017-03-24 07:00 | 69.96 | 68.18
2017-03-24 07:30 | 90.96 | 90.19
2017-03-24 08:00 | 95.2 | 94.98
2017-03-24 08:30 | 111.04 | 105.23
2017-03-24 09:00 | 132.28 | 116.17
2017-03-24 09:30 | 131.43 | 114.88
2017-03-24 10:00 | 124.92 | 106.73
2017-03-24 10:30 | 133.06 | 114.45
2017-03-24 11:00 | 132.86 | 113.12
2017-03-24 11:30 | 143.92 | 124.76
2017-03-24 12:00 | 153.82 | 135.01
2017-03-24 12:30 | 135.77 | 130.99
2017-03-24 13:00 | 130.91 | 127.32
2017-03-24 13:30 | 126.71 | 122.4
2017-03-24 14:00 | 126.27 | 120.91
2017-03-24 14:30 | 130.24 | 125.39
2017-03-24 15:00 | 122.34 | 117.54
2017-03-24 15:30 | 119.87 | 116.42
2017-03-24 16:00 | 119.12 | 115.81
2017-03-24 16:30 | 99.86 | 96.42
2017-03-24 17:00 | 109.39 | 106.47
2017-03-24 17:30 | 111.92 | 108.98
2017-03-24 18:00 | 101.6 | 98.64
2017-03-24 18:30 | 98.71 | 96.45
2017-03-24 19:00 | 83.01 | 80.22
2017-03-24 19:30 | 39.34 | 16.74
2017-03-24 20:00 | 62.37 | 55.23
2017-03-24 20:30 | 73.38 | 70.94
2017-03-24 21:00 | 42.15 | 42.1
2017-03-24 21:30 | 35.52 | 35.51
2017-03-24 22:00 | 12.46 | 12.45
2017-03-24 22:30 | 46.76 | 46.7
2017-03-24 23:00 | 70.01 | 69.86
2017-03-24 23:30 | 49.68 | 49.38
2017-03-25 | 5.27 | 3.03
2017-03-25 00:30 | 23.55 | -22.85
2017-03-25 01:00 | 33.85 | -33.09
2017-03-25 01:30 | 31.47 | -30.54
2017-03-25 02:00 | 32.99 | -31.86
2017-03-25 02:30 | 45.72 | -45.02
2017-03-25 03:00 | 55.78 | -55.49
2017-03-25 03:30 | 51.98 | -51.58
2017-03-25 04:00 | 52.81 | -52.44
2017-03-25 04:30 | 46.48 | -45.76
2017-03-25 05:00 | 47.38 | -46.76
2017-03-25 05:30 | 49.3 | -48.94
2017-03-25 06:00 | 50.66 | -50.42
2017-03-25 06:30 | 35.46 | -35.16
2017-03-25 07:00 | 30.28 | -30.21
2017-03-25 07:30 | 23.87 | -23.86
2017-03-25 08:00 | 22.94 | -22.88
2017-03-25 08:30 | 41.66 | -39.82
2017-03-25 09:00 | 12.07 | 6.46
2017-03-25 09:30 | 25.41 | 24.04
2017-03-25 10:00 | 22.86 | 21.58
2017-03-25 10:30 | 22.77 | 21.43
2017-03-25 11:00 | 22.44 | 21.09
2017-03-25 11:30 | 12.66 | -8.25
2017-03-25 12:00 | 32.59 | -30.19
2017-03-25 12:30 | 28.79 | -26.01
2017-03-25 13:00 | 35.12 | -32.84
2017-03-25 13:30 | 11.26 | -6.43
2017-03-25 14:00 | 13.92 | 11.55
2017-03-25 14:30 | 26.68 | 25.87
2017-03-25 15:00 | 43.14 | 42.84
2017-03-25 15:30 | 71.78 | 71.76
2017-03-25 16:00 | 89.29 | 89.29
2017-03-25 16:30 | 109.82 | 109.71
2017-03-25 17:00 | 129.27 | 129.19
2017-03-25 17:30 | 115.7 | 115.66
2017-03-25 18:00 | 101.09 | 101.08
2017-03-25 18:30 | 119.74 | 119.74
2017-03-25 19:00 | 136.86 | 136.86
2017-03-25 19:30 | 125.88 | 125.88
2017-03-25 20:00 | 105.15 | 105.13
2017-03-25 20:30 | 94.37 | 94.36
2017-03-25 21:00 | 68.29 | 68.27
2017-03-25 21:30 | 65.49 | 65.49
2017-03-25 22:00 | 56.96 | 56.91
2017-03-25 22:30 | 67.39 | 67.29
2017-03-25 23:00 | 106.16 | 105.99
2017-03-25 23:30 | 79.08 | 78.57
2017-03-26 | 37.31 | 35.36
2017-03-26 00:30 | 21.41 | 17.4
2017-03-26 01:00 | 15.66 | 10.16
2017-03-26 01:30 | 20.16 | -11.2
2017-03-26 02:00 | 36.98 | -34.25
2017-03-26 02:30 | 37.62 | -35.11
2017-03-26 03:00 | 44.66 | -43.19
2017-03-26 03:30 | 43.78 | -42.42
2017-03-26 04:00 | 43.87 | -42.62
2017-03-26 04:30 | 41.72 | -40.28
2017-03-26 05:00 | 44.05 | -42.86
2017-03-26 05:30 | 38.23 | -36.19
2017-03-26 06:00 | 37.98 | -36.06
2017-03-26 06:30 | 36.89 | -35.2
2017-03-26 07:00 | 34.36 | -32.8
2017-03-26 07:30 | 36.71 | -35.78
2017-03-26 08:00 | 27.43 | -26.84
2017-03-26 08:30 | 11.7 | -11.12
2017-03-26 09:00 | 17.98 | -14.47
2017-03-26 09:30 | 32.18 | 29.58
2017-03-26 10:00 | 57.07 | 55.06
2017-03-26 10:30 | 69.29 | 61.53
2017-03-26 11:00 | 64.62 | 53.54
2017-03-26 11:30 | 59.25 | 46.89
2017-03-26 12:00 | 73.24 | 59.43
2017-03-26 12:30 | 93.73 | 68.32
2017-03-26 13:00 | 88.18 | 60.48
2017-03-26 13:30 | 88.61 | 61.11
2017-03-26 14:00 | 100.3 | 91.06
2017-03-26 14:30 | 108.09 | 103.32
2017-03-26 15:00 | 105.42 | 100.36
2017-03-26 15:30 | 104.02 | 98.89
2017-03-26 16:00 | 113.88 | 109.16
2017-03-26 16:30 | 133.01 | 129.03
2017-03-26 17:00 | 146.18 | 142.83
2017-03-26 17:30 | 132.61 | 129.41
2017-03-26 18:00 | 136.01 | 132.81
2017-03-26 18:30 | 156.62 | 152.76
2017-03-26 19:00 | 170.4 | 166.76
2017-03-26 19:30 | 146.1 | 143.99
2017-03-26 20:00 | 130.51 | 129.29
2017-03-26 20:30 | 152.45 | 152.19
2017-03-26 21:00 | 116.01 | 115.86
2017-03-26 21:30 | 102.96 | 102.94
2017-03-26 22:00 | 81.96 | 81.56
2017-03-26 22:30 | 87.92 | 86.98
2017-03-26 23:00 | 115.84 | 115.33
2017-03-26 23:30 | 93.55 | 93.15
2017-03-27 | 50.23 | 49.55
2017-03-27 00:30 | 21.44 | 20.43
2017-03-27 01:00 | 6.75 | 4.48
2017-03-27 01:30 | 11.57 | 10.84
2017-03-27 02:00 | 8.42 | 7.66
2017-03-27 02:30 | 5.67 | -4.43
2017-03-27 03:00 | 12.3 | -11.67
2017-03-27 03:30 | 19.53 | -19.09
2017-03-27 04:00 | 24.24 | -23.83
2017-03-27 04:30 | 11 | -9.77
2017-03-27 05:00 | 5.87 | 1.57
2017-03-27 05:30 | 9.76 | -1.16
2017-03-27 06:00 | 14.38 | -3.46
2017-03-27 06:30 | 34.42 | 29.86
2017-03-27 07:00 | 66.16 | 58.95
2017-03-27 07:30 | 86.3 | 68.56
2017-03-27 08:00 | 85.6 | 65.08
2017-03-27 08:30 | 93.66 | 70.04
2017-03-27 09:00 | 123.67 | 92.33
2017-03-27 09:30 | 131.18 | 100.39
2017-03-27 10:00 | 132.89 | 101.64
2017-03-27 10:30 | 140.76 | 109.2
2017-03-27 11:00 | 126.37 | 89.91
2017-03-27 11:30 | 115.28 | 73.82
2017-03-27 12:00 | 134.07 | 84.24
2017-03-27 12:30 | 133.19 | 86.1
2017-03-27 13:00 | 127.88 | 80.16
2017-03-27 13:30 | 132.85 | 87.94
2017-03-27 14:00 | 139.89 | 99.53
2017-03-27 14:30 | 137.58 | 95.51
2017-03-27 15:00 | 137.5 | 95.63
2017-03-27 15:30 | 149.73 | 112.8
2017-03-27 16:00 | 159.98 | 126.78
2017-03-27 16:30 | 140.94 | 103.75
2017-03-27 17:00 | 149.2 | 116.11
2017-03-27 17:30 | 158.92 | 130.61
2017-03-27 18:00 | 156.61 | 128.87
2017-03-27 18:30 | 158.98 | 130.68
2017-03-27 19:00 | 154.51 | 125.77
2017-03-27 19:30 | 137.16 | 104.9
2017-03-27 20:00 | 122.94 | 86.75
2017-03-27 20:30 | 110.93 | 78.53
2017-03-27 21:00 | 84.95 | 50.75
2017-03-27 21:30 | 76.97 | 40.34
2017-03-27 22:00 | 64.98 | 30.43
2017-03-27 22:30 | 51.29 | 41.67
2017-03-27 23:00 | 55.08 | 54.42
2017-03-27 23:30 | 38.42 | 37.89
2017-03-28 | 19.67 | 19.19
2017-03-28 00:30 | 7.8 | 6.44
2017-03-28 01:00 | 7.56 | 6.54
2017-03-28 01:30 | 9.01 | 4.03
2017-03-28 02:00 | 8.78 | 4.51
2017-03-28 02:30 | 9.72 | 7.04
2017-03-28 03:00 | 6.87 | -2.16
2017-03-28 03:30 | 12.98 | -10.31
2017-03-28 04:00 | 9.52 | -4.81
2017-03-28 04:30 | 11.13 | -5.86
2017-03-28 05:00 | 15.62 | -11.31
2017-03-28 05:30 | 14.17 | -2.52
2017-03-28 06:00 | 17.41 | 11.32
2017-03-28 06:30 | 31.28 | 27.1
2017-03-28 07:00 | 47.96 | 36.75
2017-03-28 07:30 | 85.94 | 50.14
2017-03-28 08:00 | 93.25 | 54.25
2017-03-28 08:30 | 100.23 | 57.83
2017-03-28 09:00 | 105.36 | 60.82
2017-03-28 09:30 | 120.59 | 62.94
2017-03-28 10:00 | 122.77 | 64.22
2017-03-28 10:30 | 121.5 | 59.44
2017-03-28 11:00 | 118.07 | 51.65
2017-03-28 11:30 | 117.8 | 52.09
2017-03-28 12:00 | 118.1 | 52.55
2017-03-28 12:30 | 121.37 | 57.29
2017-03-28 13:00 | 125.97 | 65.64
2017-03-28 13:30 | 138.58 | 72.83
2017-03-28 14:00 | 147.29 | 78.51
2017-03-28 14:30 | 150.03 | 82.9
2017-03-28 15:00 | 150.52 | 86.71
2017-03-28 15:30 | 152.11 | 90.25
2017-03-28 16:00 | 153.99 | 96.84
2017-03-28 16:30 | 149.79 | 102.6
2017-03-28 17:00 | 157.28 | 122.66
2017-03-28 17:30 | 142.6 | 114.18
2017-03-28 18:00 | 140.07 | 111.38
2017-03-28 18:30 | 158.33 | 131.5
2017-03-28 19:00 | 165.85 | 140.77
2017-03-28 19:30 | 138.71 | 109.95
2017-03-28 20:00 | 130.24 | 101.18
2017-03-28 20:30 | 113.24 | 94.7
2017-03-28 21:00 | 109.14 | 94.59
2017-03-28 21:30 | 96.1 | 82.07
2017-03-28 22:00 | 77.74 | 58.56
2017-03-28 22:30 | 76.04 | 57.58
2017-03-28 23:00 | 79.61 | 64.02
2017-03-28 23:30 | 50.64 | 37.48
2017-03-29 | 21.8 | 18.89
2017-03-29 00:30 | 14.09 | 10.62
2017-03-29 01:00 | 11.36 | 7.61
2017-03-29 01:30 | 10.29 | 5.42
2017-03-29 02:00 | 9.93 | 5.15
2017-03-29 02:30 | 9.69 | 5.27
2017-03-29 03:00 | 9.09 | 4.32
2017-03-29 03:30 | 9.09 | 4.77
2017-03-29 04:00 | 10.66 | 6.88
2017-03-29 04:30 | 13.13 | 9.49
2017-03-29 05:00 | 12.62 | 8.38
2017-03-29 05:30 | 20.19 | 15.8
2017-03-29 06:00 | 24.43 | 20.54
2017-03-29 06:30 | 34.36 | 30.86
2017-03-29 07:00 | 72.98 | 66.25
2017-03-29 07:30 | 94.74 | 86.9
2017-03-29 08:00 | 78.93 | 72.48
2017-03-29 08:30 | 93.85 | 86.09
2017-03-29 09:00 | 167.16 | 160.66
2017-03-29 09:30 | 145.84 | 135.55
2017-03-29 10:00 | 124.45 | 112.37
2017-03-29 10:30 | 124.9 | 112.64
2017-03-29 11:00 | 128.13 | 116.16
2017-03-29 11:30 | 136.54 | 126.05
2017-03-29 12:00 | 138.33 | 127.6
2017-03-29 12:30 | 140.04 | 128.97
2017-03-29 13:00 | 135.05 | 123.45
2017-03-29 13:30 | 143.87 | 133.56
2017-03-29 14:00 | 122.07 | 109.71
2017-03-29 14:30 | 135.07 | 123.61
2017-03-29 15:00 | 136.28 | 125.67
2017-03-29 15:30 | 127.23 | 117.06
2017-03-29 16:00 | 122.26 | 112.4
2017-03-29 16:30 | 113.42 | 108.42
2017-03-29 17:00 | 121.09 | 117.58
2017-03-29 17:30 | 117.8 | 114.63
2017-03-29 18:00 | 138.1 | 135.21
2017-03-29 18:30 | 155.11 | 152.41
2017-03-29 19:00 | 178.16 | 175.96
2017-03-29 19:30 | 161.96 | 160.39
2017-03-29 20:00 | 141.45 | 138.73
2017-03-29 20:30 | 140.96 | 138.04
2017-03-29 21:00 | 101.11 | 97.82
2017-03-29 21:30 | 81.55 | 77.01
2017-03-29 22:00 | 76.11 | 72.5
2017-03-29 22:30 | 112.14 | 109.36
2017-03-29 23:00 | 127.18 | 126.73
2017-03-29 23:30 | 88.64 | 88.63
2017-03-30 | 45.16 | 45.12
2017-03-30 00:30 | 34.03 | 33.92
2017-03-30 01:00 | 32.4 | 32.01
2017-03-30 01:30 | 20.05 | 19.21
2017-03-30 02:00 | 21.35 | 20.61
2017-03-30 02:30 | 13.4 | 12.26
2017-03-30 03:00 | 9.4 | 7.99
2017-03-30 03:30 | 10.31 | 8.83
2017-03-30 04:00 | 12.25 | 11.64
2017-03-30 04:30 | 14.65 | 14.63
2017-03-30 05:00 | 14.75 | 14.75
2017-03-30 05:30 | 23.33 | 21.89
2017-03-30 06:00 | 34.38 | 28.02
2017-03-30 06:30 | 63.15 | 59.4
2017-03-30 07:00 | 80.37 | 76.01
2017-03-30 07:30 | 115.78 | 107.62
2017-03-30 08:00 | 131.47 | 123.27
2017-03-30 08:30 | 106.38 | 90.05
2017-03-30 09:00 | 108.18 | 90.52
2017-03-30 09:30 | 105.85 | 88.02
2017-03-30 10:00 | 105.91 | 87.88
2017-03-30 10:30 | 105.63 | 88.51
2017-03-30 11:00 | 105.62 | 89.18
2017-03-30 11:30 | 102.74 | 89.98
2017-03-30 12:00 | 110.34 | 104.59
2017-03-30 12:30 | 100.9 | 95.51
2017-03-30 13:00 | 112.36 | 108.15
2017-03-30 13:30 | 116.13 | 115.22
2017-03-30 14:00 | 113.19 | 112.54
2017-03-30 14:30 | 107.02 | 104.69
2017-03-30 15:00 | 121.36 | 117.49
2017-03-30 15:30 | 111.36 | 107.82
2017-03-30 16:00 | 110.4 | 106.62
2017-03-30 16:30 | 124.92 | 121.5
2017-03-30 17:00 | 128.09 | 124.37
2017-03-30 17:30 | 135.9 | 131.72
2017-03-30 18:00 | 122.01 | 118.35
2017-03-30 18:30 | 118.57 | 116.3
2017-03-30 19:00 | 55.82 | 46.1
2017-03-30 19:30 | 55.51 | 49.27
2017-03-30 20:00 | 51.45 | 46.15
2017-03-30 20:30 | 45.31 | 43.11
2017-03-30 21:00 | 45.44 | 41.89
2017-03-30 21:30 | 88.28 | 87.32
2017-03-30 22:00 | 66.13 | 65.4
2017-03-30 22:30 | 72.61 | 72.01
2017-03-30 23:00 | 94.89 | 94.49
2017-03-30 23:30 | 58.49 | 57.43
2017-03-31 | 25.79 | 23.58
2017-03-31 00:30 | 11.37 | 10.95
2017-03-31 01:00 | 6.89 | 3.56
2017-03-31 01:30 | 48.61 | 48.28
2017-03-31 02:00 | 51.44 | 51.37
2017-03-31 02:30 | 57.04 | 56.92
2017-03-31 03:00 | 59.06 | 58.84
2017-03-31 03:30 | 60.9 | 60.67
2017-03-31 04:00 | 61.63 | 61.4
2017-03-31 04:30 | 62.25 | 62.02
2017-03-31 05:00 | 62.7 | 62.45
2017-03-31 05:30 | 60.8 | 60.77
2017-03-31 06:00 | 65.64 | 65.64
2017-03-31 06:30 | 70.95 | 70.93
2017-03-31 07:00 | 76.83 | 76.76
2017-03-31 07:30 | 87.04 | 86.58
2017-03-31 08:00 | 93.14 | 91.69
2017-03-31 08:30 | 95.85 | 91.37
2017-03-31 09:00 | 94.53 | 90.08
2017-03-31 09:30 | 94.81 | 90.45
2017-03-31 10:00 | 95.33 | 90.62
2017-03-31 10:30 | 95.17 | 90.45
2017-03-31 11:00 | 96.25 | 91.76
2017-03-31 11:30 | 96.61 | 92.09
2017-03-31 12:00 | 107.2 | 102.33
2017-03-31 12:30 | 104.28 | 98.96
2017-03-31 13:00 | 109.39 | 105.82
2017-03-31 13:30 | 111.17 | 109.07
2017-03-31 14:00 | 114.75 | 109.77
2017-03-31 14:30 | 107.69 | 102.89
2017-03-31 15:00 | 110.05 | 105.51
2017-03-31 15:30 | 114.05 | 109.6
2017-03-31 16:00 | 121.5 | 117.37
2017-03-31 16:30 | 127.14 | 123.33
2017-03-31 17:00 | 129.88 | 125.99
2017-03-31 17:30 | 144.32 | 136.86
2017-03-31 18:00 | 158.66 | 149.58
2017-03-31 18:30 | 164.83 | 155.02
2017-03-31 19:00 | 174.79 | 165.75
2017-03-31 19:30 | 156.04 | 147.27
2017-03-31 20:00 | 125.33 | 120.86
2017-03-31 20:30 | 111 | 110.85
2017-03-31 21:00 | 82.83 | 82.82
2017-03-31 21:30 | 86.93 | 86.84
2017-03-31 22:00 | 69.11 | 68.79
2017-03-31 22:30 | 86.68 | 86.4
2017-03-31 23:00 | 98.77 | 98.47
2017-03-31 23:30 | 77.9 | 77.68
2017-04-01 | 61.43 | 61.35
2017-04-01 00:30 | 53.75 | 51.16
2017-04-01 01:00 | 57.06 | 55.25
2017-04-01 01:30 | 59.96 | 58.49
2017-04-01 02:00 | 60.59 | 59.23
2017-04-01 02:30 | 60.35 | 59.05
2017-04-01 03:00 | 60 | 58.92
2017-04-01 03:30 | 59.07 | 57.85
2017-04-01 04:00 | 61.27 | 56.76
2017-04-01 04:30 | 62.97 | 56.43
2017-04-01 05:00 | 62.86 | 56.04
2017-04-01 05:30 | 64.71 | 57.53
2017-04-01 06:00 | 65.15 | 57.54
2017-04-01 06:30 | 66.77 | 58.31
2017-04-01 07:00 | 67.43 | 58.91
2017-04-01 07:30 | 69 | 64.65
2017-04-01 08:00 | 71.15 | 68.33
2017-04-01 08:30 | 78.34 | 75.25
2017-04-01 09:00 | 81.91 | 81.28
2017-04-01 09:30 | 87.36 | 86.34
2017-04-01 10:00 | 87.86 | 85.72
2017-04-01 10:30 | 84.42 | 82.1
2017-04-01 11:00 | 84.97 | 82.94
2017-04-01 11:30 | 81.73 | 79.74
2017-04-01 12:00 | 81.55 | 79.68
2017-04-01 12:30 | 83.49 | 81.68
2017-04-01 13:00 | 85.77 | 84.19
2017-04-01 13:30 | 89.64 | 88.2
2017-04-01 14:00 | 91.4 | 90.06
2017-04-01 14:30 | 93.32 | 92.03
2017-04-01 15:00 | 94.95 | 93.7
2017-04-01 15:30 | 95.89 | 94.53
2017-04-01 16:00 | 99.52 | 98.14
2017-04-01 16:30 | 100.45 | 98.97
2017-04-01 17:00 | 101.28 | 98.25
2017-04-01 17:30 | 100.78 | 93.06
2017-04-01 18:00 | 101.06 | 91.33
2017-04-01 18:30 | 104.91 | 93.9
2017-04-01 19:00 | 107.8 | 97.51
2017-04-01 19:30 | 105.21 | 95.83
2017-04-01 20:00 | 112.21 | 95.27
2017-04-01 20:30 | 107.71 | 90.87
2017-04-01 21:00 | 93.54 | 82.35
2017-04-01 21:30 | 90.56 | 81.96
2017-04-01 22:00 | 86.89 | 83.83
2017-04-01 22:30 | 83.65 | 80.99
2017-04-01 23:00 | 85.92 | 83.37
2017-04-01 23:30 | 77.87 | 75.51
2017-04-02 | 65.31 | 63.14
2017-04-02 00:30 | 56.19 | 54.06
2017-04-02 01:00 | 57.53 | 56.05
2017-04-02 01:30 | 57.82 | 56.51
2017-04-02 02:00 | 56.8 | 55.47
2017-04-02 02:30 | 55.82 | 54.52
2017-04-02 03:00 | 55.49 | 54.25
2017-04-02 03:30 | 55.39 | 54.12
2017-04-02 04:00 | 55.24 | 53.99
2017-04-02 04:30 | 55.41 | 54.11
2017-04-02 05:00 | 57.02 | 55.76
2017-04-02 05:30 | 58.26 | 56.93
2017-04-02 06:00 | 57.78 | 56.27
2017-04-02 06:30 | 57.1 | 55.47
2017-04-02 07:00 | 57.43 | 55.55
2017-04-02 07:30 | 59.49 | 57.22
2017-04-02 08:00 | 62.64 | 59.73
2017-04-02 08:30 | 66.4 | 63.42
2017-04-02 09:00 | 68.23 | 65.4
2017-04-02 09:30 | 76.09 | 70.43
2017-04-02 10:00 | 80.69 | 72.2
2017-04-02 10:30 | 77.81 | 69.13
2017-04-02 11:00 | 77.26 | 68.42
2017-04-02 11:30 | 74.57 | 65.81
2017-04-02 12:00 | 72.88 | 63.1
2017-04-02 12:30 | 69.37 | 58.63
2017-04-02 13:00 | 70.58 | 60.1
2017-04-02 13:30 | 80.73 | 71.98
2017-04-02 14:00 | 77.15 | 67.75
2017-04-02 14:30 | 77.73 | 67.98
2017-04-02 15:00 | 79.44 | 69.51
2017-04-02 15:30 | 88.8 | 80.43
2017-04-02 16:00 | 85.79 | 77.11
2017-04-02 16:30 | 89.9 | 81.58
2017-04-02 17:00 | 97.24 | 89.26
2017-04-02 17:30 | 96.18 | 85.9
2017-04-02 18:00 | 96.1 | 85.91
2017-04-02 18:30 | 103.79 | 91.43
2017-04-02 19:00 | 106.41 | 95
2017-04-02 19:30 | 107.85 | 93.01
2017-04-02 20:00 | 110.55 | 93.79
2017-04-02 20:30 | 109.72 | 94.35
2017-04-02 21:00 | 97.41 | 88.68
2017-04-02 21:30 | 83.4 | 82.08
2017-04-02 22:00 | 74.48 | 74.44
2017-04-02 22:30 | 78.65 | 78.64
2017-04-02 23:00 | 88.4 | 88.4
2017-04-02 23:30 | 72.14 | 72.12
2017-04-03 | 57.03 | 56.86
2017-04-03 00:30 | 49.63 | 49.24
2017-04-03 01:00 | 44.52 | 43.98
2017-04-03 01:30 | 41.33 | 40.82
2017-04-03 02:00 | 44.54 | 44.46
2017-04-03 02:30 | 48.09 | 48.09
2017-04-03 03:00 | 49.83 | 49.83
2017-04-03 03:30 | 50.38 | 50.38
2017-04-03 04:00 | 51.97 | 51.97
2017-04-03 04:30 | 54.39 | 54.38
2017-04-03 05:00 | 56.45 | 56.44
2017-04-03 05:30 | 58.49 | 58.49
2017-04-03 06:00 | 60.01 | 60.01
2017-04-03 06:30 | 64.74 | 63.48
2017-04-03 07:00 | 79.28 | 76.18
2017-04-03 07:30 | 86.6 | 83.07
2017-04-03 08:00 | 85.59 | 83.09
2017-04-03 08:30 | 86.37 | 85.33
2017-04-03 09:00 | 85.04 | 84.09
2017-04-03 09:30 | 86.11 | 84.95
2017-04-03 10:00 | 89.05 | 87.45
2017-04-03 10:30 | 81.35 | 78.57
2017-04-03 11:00 | 77.41 | 74.32
2017-04-03 11:30 | 77.56 | 74.59
2017-04-03 12:00 | 88.79 | 86.25
2017-04-03 12:30 | 82.32 | 79.61
2017-04-03 13:00 | 81.18 | 78.26
2017-04-03 13:30 | 88.44 | 85.71
2017-04-03 14:00 | 90.69 | 88.16
2017-04-03 14:30 | 89.04 | 86.59
2017-04-03 15:00 | 88.89 | 86.4
2017-04-03 15:30 | 88.91 | 86.44
2017-04-03 16:00 | 93.63 | 91.52
2017-04-03 16:30 | 96.76 | 95.04
2017-04-03 17:00 | 99.31 | 97.89
2017-04-03 17:30 | 98.36 | 96.97
2017-04-03 18:00 | 97.01 | 95.95
2017-04-03 18:30 | 98.62 | 96.87
2017-04-03 19:00 | 102.39 | 101.12
2017-04-03 19:30 | 102.25 | 101.06
2017-04-03 20:00 | 102.93 | 101.62
2017-04-03 20:30 | 101.49 | 100.72
2017-04-03 21:00 | 93.99 | 93.53
2017-04-03 21:30 | 87.53 | 87.25
2017-04-03 22:00 | 79.79 | 79.66
2017-04-03 22:30 | 81.98 | 81.91
2017-04-03 23:00 | 91.2 | 91.19
2017-04-03 23:30 | 70.39 | 70.38
2017-04-04 | 50.33 | 50.28
2017-04-04 00:30 | 38.52 | 38.26
2017-04-04 01:00 | 31.75 | 31.25
2017-04-04 01:30 | 28.95 | 28.27
2017-04-04 02:00 | 35.07 | 35.06
2017-04-04 02:30 | 42.96 | 42.96
2017-04-04 03:00 | 47.19 | 47.18
2017-04-04 03:30 | 48.27 | 48.27
2017-04-04 04:00 | 50.63 | 50.62
2017-04-04 04:30 | 54.13 | 54.12
2017-04-04 05:00 | 56.31 | 56.31
2017-04-04 05:30 | 59.18 | 59.14
2017-04-04 06:00 | 63.42 | 63.4
2017-04-04 06:30 | 66.43 | 66.41
2017-04-04 07:00 | 76.31 | 76.26
2017-04-04 07:30 | 90.89 | 88.94
2017-04-04 08:00 | 90.71 | 88.2
2017-04-04 08:30 | 93.42 | 90.37
2017-04-04 09:00 | 89.53 | 84.24
2017-04-04 09:30 | 101.16 | 89.36
2017-04-04 10:00 | 101.28 | 89.34
2017-04-04 10:30 | 84.01 | 68.19
2017-04-04 11:00 | 101.34 | 89.81
2017-04-04 11:30 | 46.23 | -1.78
2017-04-04 12:00 | 48.07 | -9.8
2017-04-04 12:30 | 47.59 | -4.64
2017-04-04 13:00 | 48.31 | -2.33
2017-04-04 13:30 | 48.17 | 2.27
2017-04-04 14:00 | 47.7 | -2.11
2017-04-04 14:30 | 47.21 | 1.86
2017-04-04 15:00 | 47.35 | -3.05
2017-04-04 15:30 | 47.49 | 7.45
2017-04-04 16:00 | 45.88 | 4.41
2017-04-04 16:30 | 45.17 | 9.65
2017-04-04 17:00 | 50.71 | 27.42
2017-04-04 17:30 | 54.26 | 37.16
2017-04-04 18:00 | 58.36 | 42.38
2017-04-04 18:30 | 80.32 | 67.15
2017-04-04 19:00 | 81.84 | 69.77
2017-04-04 19:30 | 63.73 | 49.46
2017-04-04 20:00 | 54.18 | 38
2017-04-04 20:30 | 49.09 | 33.12
2017-04-04 21:00 | 42.44 | 24.63
2017-04-04 21:30 | 32.4 | 21.2
2017-04-04 22:00 | 17.96 | 17.96
2017-04-04 22:30 | 25.63 | 25.62
2017-04-04 23:00 | 34.29 | 34.16
2017-04-04 23:30 | 22.64 | 22.39
2017-04-05 | 7.88 | 6.33
2017-04-05 00:30 | 6.57 | -1.92
2017-04-05 01:00 | 9.66 | -7.46
2017-04-05 01:30 | 10.89 | -8.86
2017-04-05 02:00 | 10.23 | -7.29
2017-04-05 02:30 | 8.12 | -4.82
2017-04-05 03:00 | 5.28 | -2.56
2017-04-05 03:30 | 5.2 | -1.99
2017-04-05 04:00 | 5.23 | 0.85
2017-04-05 04:30 | 6.41 | 3.99
2017-04-05 05:00 | 5.35 | 1.94
2017-04-05 05:30 | 6.15 | 5.82
2017-04-05 06:00 | 8.13 | 7.59
2017-04-05 06:30 | 9.8 | 9.5
2017-04-05 07:00 | 23.43 | 17.24
2017-04-05 07:30 | 32.92 | 18.82
2017-04-05 08:00 | 38.12 | 9.83
2017-04-05 08:30 | 43.3 | 16.71
2017-04-05 09:00 | 44.5 | 10.31
2017-04-05 09:30 | 45.48 | 0.74
2017-04-05 10:00 | 47.58 | -1.95
2017-04-05 10:30 | 49.12 | -6.3
2017-04-05 11:00 | 49.71 | -4.44
2017-04-05 11:30 | 50.33 | -2.4
2017-04-05 12:00 | 50.09 | -4.5
2017-04-05 12:30 | 50.46 | -7.51
2017-04-05 13:00 | 50.2 | -9.05
2017-04-05 13:30 | 49.79 | 3.29
2017-04-05 14:00 | 50.63 | 2.17
2017-04-05 14:30 | 39.01 | 15.91
2017-04-05 15:00 | 34.57 | 8.57
2017-04-05 15:30 | 30.27 | 6.19
2017-04-05 16:00 | 34.46 | 32.79
2017-04-05 16:30 | 51.23 | 50.32
2017-04-05 17:00 | 63.17 | 62.69
2017-04-05 17:30 | 83.12 | 82.85
2017-04-05 18:00 | 83.84 | 83.39
2017-04-05 18:30 | 74.37 | 73.41
2017-04-05 19:00 | 70.7 | 69.89
2017-04-05 19:30 | 49.05 | 48.13
2017-04-05 20:00 | 38.2 | 37.19
2017-04-05 20:30 | 27.45 | 26.37
2017-04-05 21:00 | 22.89 | 22.01
2017-04-05 21:30 | 18.69 | 18.49
2017-04-05 22:00 | 13.12 | 13.12
2017-04-05 22:30 | 18.73 | 18.69
2017-04-05 23:00 | 25.41 | 25.2
2017-04-05 23:30 | 18.14 | 17.54
2017-04-06 | 6.21 | 2.35
2017-04-06 00:30 | 9.31 | -6.04
2017-04-06 01:00 | 10.01 | -9.84
2017-04-06 01:30 | 12.62 | -12.53
2017-04-06 02:00 | 10.95 | -10.93
2017-04-06 02:30 | 8.05 | -7.46
2017-04-06 03:00 | 7.31 | -5.86
2017-04-06 03:30 | 6.78 | -3.6
2017-04-06 04:00 | 6.29 | -1.6
2017-04-06 04:30 | 5.94 | 0.55
2017-04-06 05:00 | 6.52 | -1.27
2017-04-06 05:30 | 5.32 | 3.32
2017-04-06 06:00 | 7.54 | 7.52
2017-04-06 06:30 | 7.58 | 7.39
2017-04-06 07:00 | 10.83 | 10.83
2017-04-06 07:30 | 21.79 | 14.81
2017-04-06 08:00 | 8.79 | 7.11
2017-04-06 08:30 | 12.79 | 9.24
2017-04-06 09:00 | 15.13 | 9.86
2017-04-06 09:30 | 12.5 | -0.75
2017-04-06 10:00 | 15.35 | -2.68
2017-04-06 10:30 | 17.98 | 3.35
2017-04-06 11:00 | 20.31 | 12.34
2017-04-06 11:30 | 18.43 | 10.59
2017-04-06 12:00 | 16.12 | -0.99
2017-04-06 12:30 | 16.73 | 2.3
2017-04-06 13:00 | 17.32 | -1.17
2017-04-06 13:30 | 18 | -4.2
2017-04-06 14:00 | 45.06 | 3.08
2017-04-06 14:30 | 49.92 | 6.38
2017-04-06 15:00 | 48.79 | 1.76
2017-04-06 15:30 | 47.11 | 3.97
2017-04-06 16:00 | 42.1 | 8.65
2017-04-06 16:30 | 30.95 | 10.84
2017-04-06 17:00 | 35.34 | 20.17
2017-04-06 17:30 | 42.85 | 32.4
2017-04-06 18:00 | 60.91 | 49.19
2017-04-06 18:30 | 72.38 | 64.03
2017-04-06 19:00 | 75.01 | 68.57
2017-04-06 19:30 | 67.49 | 52.26
2017-04-06 20:00 | 46.54 | 41.78
2017-04-06 20:30 | 36.55 | 35.06
2017-04-06 21:00 | 28.4 | 27.52
2017-04-06 21:30 | 29.64 | 29.22
2017-04-06 22:00 | 26.43 | 26.33
2017-04-06 22:30 | 32.77 | 32.73
2017-04-06 23:00 | 38.28 | 38.27
2017-04-06 23:30 | 30.8 | 30.79
2017-04-07 | 16.65 | 16.51
2017-04-07 00:30 | 8.03 | 6.94
2017-04-07 01:00 | 11.51 | -11.1
2017-04-07 01:30 | 15.75 | -15.49
2017-04-07 02:00 | 10.48 | -9.16
2017-04-07 02:30 | 8.77 | -5.19
2017-04-07 03:00 | 8.36 | -1.2
2017-04-07 03:30 | 10.92 | 6.03
2017-04-07 04:00 | 11.46 | 6.87
2017-04-07 04:30 | 11.92 | 9.41
2017-04-07 05:00 | 12.8 | 10.65
2017-04-07 05:30 | 13.43 | 12.06
2017-04-07 06:00 | 18.63 | 17.72
2017-04-07 06:30 | 22.59 | 22.24
2017-04-07 07:00 | 20.66 | 18.05
2017-04-07 07:30 | 20.45 | 13.02
2017-04-07 08:00 | 22.52 | 10.21
2017-04-07 08:30 | 27.43 | 13.35
2017-04-07 09:00 | 25.07 | 7.75
2017-04-07 09:30 | 10.94 | -0.41
2017-04-07 10:00 | 11.82 | -2.08
2017-04-07 10:30 | 15.44 | -10.2
2017-04-07 11:00 | 15.74 | -8.81
2017-04-07 11:30 | 15.97 | -8.31
2017-04-07 12:00 | 15.69 | -7.89
2017-04-07 12:30 | 13.56 | -1.79
2017-04-07 13:00 | 14.6 | -5.77
2017-04-07 13:30 | 16.44 | -8.93
2017-04-07 14:00 | 14.52 | -2.02
2017-04-07 14:30 | 13.78 | 0.85
2017-04-07 15:00 | 12.54 | -2.71
2017-04-07 15:30 | 13.1 | -2.57
2017-04-07 16:00 | 10.83 | 3.25
2017-04-07 16:30 | 13.08 | 9.28
2017-04-07 17:00 | 17.42 | 14.51
2017-04-07 17:30 | 25.75 | 24.54
2017-04-07 18:00 | 33.3 | 30.55
2017-04-07 18:30 | 43.41 | 40.87
2017-04-07 19:00 | 47.77 | 43.25
2017-04-07 19:30 | 40.11 | 38.05
2017-04-07 20:00 | 39.11 | 37.34
2017-04-07 20:30 | 38.97 | 35.14
2017-04-07 21:00 | 35.23 | 31.16
2017-04-07 21:30 | 30.54 | 29.49
2017-04-07 22:00 | 25.63 | 24.94
2017-04-07 22:30 | 30.56 | 30.24
2017-04-07 23:00 | 37.04 | 36.93
2017-04-07 23:30 | 27.71 | 27.68
2017-04-08 | 13.64 | 13.64
2017-04-08 00:30 | 6.06 | 5.39
2017-04-08 01:00 | 3.79 | 1
2017-04-08 01:30 | 3.82 | -1.75
2017-04-08 02:00 | 5.17 | -0.14
2017-04-08 02:30 | 7.35 | 2.53
2017-04-08 03:00 | 7.51 | 3.32
2017-04-08 03:30 | 7.88 | 4.35
2017-04-08 04:00 | 7.93 | 4.66
2017-04-08 04:30 | 9.21 | 5.85
2017-04-08 05:00 | 10.12 | 6.22
2017-04-08 05:30 | 12.45 | 8.74
2017-04-08 06:00 | 14.42 | 11.28
2017-04-08 06:30 | 15.5 | 12.89
2017-04-08 07:00 | 17.83 | 15.09
2017-04-08 07:30 | 15.15 | 13.63
2017-04-08 08:00 | 15.1 | 14.12
2017-04-08 08:30 | 14.93 | 14.5
2017-04-08 09:00 | 24.73 | 24.51
2017-04-08 09:30 | 26.02 | 23.24
2017-04-08 10:00 | 25.19 | 16.44
2017-04-08 10:30 | 18.62 | 12.98
2017-04-08 11:00 | 15.14 | 14.72
2017-04-08 11:30 | 26.17 | 20.63
2017-04-08 12:00 | 21.13 | 14.96
2017-04-08 12:30 | 17.62 | 10.87
2017-04-08 13:00 | 14.06 | 7.33
2017-04-08 13:30 | 13.93 | 6.23
2017-04-08 14:00 | 18.93 | 15.55
2017-04-08 14:30 | 18.62 | 13.73
2017-04-08 15:00 | 19.29 | 13.54
2017-04-08 15:30 | 17.82 | 10.89
2017-04-08 16:00 | 25.21 | 18.32
2017-04-08 16:30 | 21.47 | 15.63
2017-04-08 17:00 | 27.02 | 22.96
2017-04-08 17:30 | 32.51 | 29.32
2017-04-08 18:00 | 39.15 | 35.54
2017-04-08 18:30 | 47.91 | 44.77
2017-04-08 19:00 | 52.54 | 50.2
2017-04-08 19:30 | 38.15 | 35.47
2017-04-08 20:00 | 36.05 | 33.78
2017-04-08 20:30 | 33.53 | 31.63
2017-04-08 21:00 | 31.34 | 27
2017-04-08 21:30 | 25.21 | 24.97
2017-04-08 22:00 | 22.59 | 22.04
2017-04-08 22:30 | 32.3 | 32.15
2017-04-08 23:00 | 53.27 | 53.26
2017-04-08 23:30 | 40.17 | 40.16
2017-04-09 | 18.8 | 18.7
2017-04-09 00:30 | 8.59 | 7.82
2017-04-09 01:00 | 5.45 | 3.83
2017-04-09 01:30 | 4.65 | 1.47
2017-04-09 02:00 | 6.95 | 4.34
2017-04-09 02:30 | 8.44 | 5.63
2017-04-09 03:00 | 8.84 | 5.94
2017-04-09 03:30 | 9.49 | 6.95
2017-04-09 04:00 | 10.56 | 7.88
2017-04-09 04:30 | 10.28 | 7.28
2017-04-09 05:00 | 10.62 | 7.49
2017-04-09 05:30 | 12.36 | 8.99
2017-04-09 06:00 | 12.39 | 8.74
2017-04-09 06:30 | 13.21 | 10.5
2017-04-09 07:00 | 14.52 | 11.07
2017-04-09 07:30 | 14.85 | 11.24
2017-04-09 08:00 | 15.81 | 12.48
2017-04-09 08:30 | 19.14 | 18.05
2017-04-09 09:00 | 23.32 | 19.23
2017-04-09 09:30 | 21.37 | 17.08
2017-04-09 10:00 | 17.52 | 12.53
2017-04-09 10:30 | 16.67 | 12.34
2017-04-09 11:00 | 12.44 | 5.07
2017-04-09 11:30 | 12.13 | 1.22
2017-04-09 12:00 | 12.25 | 4.35
2017-04-09 12:30 | 17.56 | 13.39
2017-04-09 13:00 | 15.08 | 10.29
2017-04-09 13:30 | 13.61 | 7.93
2017-04-09 14:00 | 15.71 | 10.23
2017-04-09 14:30 | 20.64 | 17.52
2017-04-09 15:00 | 18.82 | 15.89
2017-04-09 15:30 | 100.6 | 98.87
2017-04-09 16:00 | 107.22 | 105.65
2017-04-09 16:30 | 92.45 | 91.72
2017-04-09 17:00 | 61.29 | 59.87
2017-04-09 17:30 | 95.7 | 94.86
2017-04-09 18:00 | 123.53 | 122.74
2017-04-09 18:30 | 135.23 | 134.45
2017-04-09 19:00 | 144.15 | 143.48
2017-04-09 19:30 | 122.11 | 121.76
2017-04-09 20:00 | 120.52 | 119.73
2017-04-09 20:30 | 108.3 | 107.45
2017-04-09 21:00 | 77.4 | 77.39
2017-04-09 21:30 | 51.56 | 50.86
2017-04-09 22:00 | 33.04 | 31.86
2017-04-09 22:30 | 52.98 | 52.03
2017-04-09 23:00 | 82.68 | 82.02
2017-04-09 23:30 | 56.21 | 55.32
2017-04-10 | 27.6 | 25.98
2017-04-10 00:30 | 20.78 | 18.83
2017-04-10 01:00 | 23.07 | 20.32
2017-04-10 01:30 | 18.82 | 15.64
2017-04-10 02:00 | 17.22 | 14.61
2017-04-10 02:30 | 16.16 | 13.97
2017-04-10 03:00 | 30.75 | 27.6
2017-04-10 03:30 | 36.43 | 33.23
2017-04-10 04:00 | 43.94 | 41.19
2017-04-10 04:30 | 47.59 | 45.01
2017-04-10 05:00 | 47.84 | 45.16
2017-04-10 05:30 | 56.54 | 53.96
2017-04-10 06:00 | 53.37 | 51.4
2017-04-10 06:30 | 56.09 | 56.01
2017-04-10 07:00 | 74.76 | 72.91
2017-04-10 07:30 | 84.76 | 81.97
2017-04-10 08:00 | 76.26 | 72.26
2017-04-10 08:30 | 61.9 | 50.42
2017-04-10 09:00 | 69.36 | 44.92
2017-04-10 09:30 | 71.62 | 46.94
2017-04-10 10:00 | 72.4 | 47.67
2017-04-10 10:30 | 77.12 | 53.5
2017-04-10 11:00 | 77.76 | 53.19
2017-04-10 11:30 | 77.04 | 51.09
2017-04-10 12:00 | 77.79 | 52.25
2017-04-10 12:30 | 67.61 | 49.56
2017-04-10 13:00 | 59.03 | 38.89
2017-04-10 13:30 | 58.24 | 36.79
2017-04-10 14:00 | 60.75 | 40.1
2017-04-10 14:30 | 61.45 | 41.63
2017-04-10 15:00 | 61.11 | 41.61
2017-04-10 15:30 | 86.04 | 74.3
2017-04-10 16:00 | 115.78 | 108.09
2017-04-10 16:30 | 127.16 | 120.98
2017-04-10 17:00 | 136.66 | 131.21
2017-04-10 17:30 | 135.06 | 130.69
2017-04-10 18:00 | 133.87 | 129.79
2017-04-10 18:30 | 137.4 | 136.07
2017-04-10 19:00 | 135.72 | 130.95
2017-04-10 19:30 | 110.87 | 105.79
2017-04-10 20:00 | 90.52 | 84.9
2017-04-10 20:30 | 57.44 | 50.55
2017-04-10 21:00 | 31.48 | 31.08
2017-04-10 21:30 | 24.87 | 24.83
2017-04-10 22:00 | 17.54 | 17.51
2017-04-10 22:30 | 25.37 | 25.37
2017-04-10 23:00 | 37.3 | 37.21
2017-04-10 23:30 | 23.28 | 23.07
2017-04-11 | 4.91 | 4.03
2017-04-11 00:30 | 4.27 | -3.83
2017-04-11 01:00 | 8.63 | -8.57
2017-04-11 01:30 | 9.15 | -9.08
2017-04-11 02:00 | 7.13 | -7.02
2017-04-11 02:30 | 5.37 | -4.66
2017-04-11 03:00 | 5.3 | -3.93
2017-04-11 03:30 | 4.62 | -2.26
2017-04-11 04:00 | 4.69 | -0.32
2017-04-11 04:30 | 5.92 | 1.81
2017-04-11 05:00 | 6 | 1.93
2017-04-11 05:30 | 8.81 | 6.31
2017-04-11 06:00 | 9.18 | 7.77
2017-04-11 06:30 | 9.63 | 9.39
2017-04-11 07:00 | 15.18 | 15.15
2017-04-11 07:30 | 21.68 | 21.05
2017-04-11 08:00 | 24.29 | 22.77
2017-04-11 08:30 | 34.42 | 22.56
2017-04-11 09:00 | 41.87 | 25.66
2017-04-11 09:30 | 41.84 | 23.77
2017-04-11 10:00 | 42.47 | 22.56
2017-04-11 10:30 | 41.19 | 16.37
2017-04-11 11:00 | 42.03 | 16.26
2017-04-11 11:30 | 40.76 | 13.49
2017-04-11 12:00 | 42.28 | 15.35
2017-04-11 12:30 | 42.12 | 15.92
2017-04-11 13:00 | 41.71 | 16.43
2017-04-11 13:30 | 41.99 | 16.36
2017-04-11 14:00 | 51.62 | 17.65
2017-04-11 14:30 | 57.55 | 22.31
2017-04-11 15:00 | 59.08 | 27.25
2017-04-11 15:30 | 74.55 | 54.29
2017-04-11 16:00 | 97.17 | 73.02
2017-04-11 16:30 | 112.42 | 92.63
2017-04-11 17:00 | 133 | 117.72
2017-04-11 17:30 | 138.29 | 126.04
2017-04-11 18:00 | 141.98 | 134.72
2017-04-11 18:30 | 132.57 | 124.3
2017-04-11 19:00 | 132.16 | 124.17
2017-04-11 19:30 | 117.56 | 109.26
2017-04-11 20:00 | 92.93 | 83.67
2017-04-11 20:30 | 78.33 | 68.07
2017-04-11 21:00 | 41.9 | 36.89
2017-04-11 21:30 | 26.42 | 25.83
2017-04-11 22:00 | 19.11 | 18.86
2017-04-11 22:30 | 57.23 | 57.23
2017-04-11 23:00 | 76.83 | 76.8
2017-04-11 23:30 | 38.4 | 38.31
2017-04-12 | 8.66 | 8.33
2017-04-12 00:30 | 3.21 | -2.66
2017-04-12 01:00 | 5.85 | -5.68
2017-04-12 01:30 | 9.13 | -9.05
2017-04-12 02:00 | 8.22 | -8.11
2017-04-12 02:30 | 6.23 | -5.43
2017-04-12 03:00 | 5.3 | -3.83
2017-04-12 03:30 | 5.06 | -2.83
2017-04-12 04:00 | 4.55 | -0.62
2017-04-12 04:30 | 5.9 | 1.14
2017-04-12 05:00 | 5.28 | 0.53
2017-04-12 05:30 | 6.22 | 4.55
2017-04-12 06:00 | 10.41 | 10.09
2017-04-12 06:30 | 33.32 | 33.23
2017-04-12 07:00 | 34.38 | 34.37
2017-04-12 07:30 | 40.23 | 39.88
2017-04-12 08:00 | 42.01 | 41.19
2017-04-12 08:30 | 49.71 | 42.32
2017-04-12 09:00 | 55.44 | 44.32
2017-04-12 09:30 | 56.95 | 27.61
2017-04-12 10:00 | 90.66 | 27.25
2017-04-12 10:30 | 89.71 | 21.21
2017-04-12 11:00 | 92.28 | 28
2017-04-12 11:30 | 92.56 | 29.91
2017-04-12 12:00 | 75.49 | 23.87
2017-04-12 12:30 | 78.46 | 33.39
2017-04-12 13:00 | 77.74 | 30.57
2017-04-12 13:30 | 73 | 24.74
2017-04-12 14:00 | 72.83 | 26.02
2017-04-12 14:30 | 73.9 | 29.59
2017-04-12 15:00 | 85.51 | 51.77
2017-04-12 15:30 | 93.76 | 65.74
2017-04-12 16:00 | 97.9 | 74.29
2017-04-12 16:30 | 103.63 | 83.49
2017-04-12 17:00 | 113.98 | 96.7
2017-04-12 17:30 | 113.55 | 96.7
2017-04-12 18:00 | 117.9 | 101.32
2017-04-12 18:30 | 124.39 | 107.83
2017-04-12 19:00 | 117.12 | 102.21
2017-04-12 19:30 | 81.51 | 70.91
2017-04-12 20:00 | 70.3 | 58.25
2017-04-12 20:30 | 64.25 | 52.88
2017-04-12 21:00 | 35.39 | 18.17
2017-04-12 21:30 | 15.62 | 15.4
2017-04-12 22:00 | 17.7 | 17.7
2017-04-12 22:30 | 63.49 | 63.37
2017-04-12 23:00 | 85.3 | 85.04
2017-04-12 23:30 | 44.79 | 43.95
2017-04-13 | 10.03 | 6.29
2017-04-13 00:30 | 9.22 | -5.19
2017-04-13 01:00 | 11.55 | -9.41
2017-04-13 01:30 | 12.53 | -10.41
2017-04-13 02:00 | 14.32 | -12.59
2017-04-13 02:30 | 16.29 | -14.85
2017-04-13 03:00 | 17.62 | -16.5
2017-04-13 03:30 | 17.96 | -16.64
2017-04-13 04:00 | 14.16 | -11.9
2017-04-13 04:30 | 10.91 | -5.1
2017-04-13 05:00 | 10.5 | -3.7
2017-04-13 05:30 | 8.95 | 1.49
2017-04-13 06:00 | 23.76 | 22.6
2017-04-13 06:30 | 39.36 | 38.96
2017-04-13 07:00 | 56.12 | 55.89
2017-04-13 07:30 | 60.51 | 60.51
2017-04-13 08:00 | 37.62 | 36.48
2017-04-13 08:30 | 28.64 | 27.86
2017-04-13 09:00 | 26.5 | 24.83
2017-04-13 09:30 | 26.03 | 23.52
2017-04-13 10:00 | 22.7 | 18.86
2017-04-13 10:30 | 19.5 | 13.41
2017-04-13 11:00 | 19.86 | 12.74
2017-04-13 11:30 | 22.64 | 15.71
2017-04-13 12:00 | 19.85 | 8.09
2017-04-13 12:30 | 19.9 | -2.84
2017-04-13 13:00 | 20.92 | 7.53
2017-04-13 13:30 | 26.1 | 17.24
2017-04-13 14:00 | 25.11 | 17.05
2017-04-13 14:30 | 26.94 | 19.56
2017-04-13 15:00 | 29.4 | 23.36
2017-04-13 15:30 | 34.84 | 30.82
2017-04-13 16:00 | 48.14 | 45.87
2017-04-13 16:30 | 67.37 | 66.03
2017-04-13 17:00 | 70.34 | 69.27
2017-04-13 17:30 | 62.68 | 61.74
2017-04-13 18:00 | 76.55 | 75.4
2017-04-13 18:30 | 92.35 | 91.2
2017-04-13 19:00 | 84.83 | 83.77
2017-04-13 19:30 | 79.71 | 78.96
2017-04-13 20:00 | 74.11 | 73.45
2017-04-13 20:30 | 71.68 | 71.24
2017-04-13 21:00 | 46.72 | 44.95
2017-04-13 21:30 | 22.35 | 20.89
2017-04-13 22:00 | 8.92 | 8.89
2017-04-13 22:30 | 31.94 | 31.9
2017-04-13 23:00 | 46.78 | 46.64
2017-04-13 23:30 | 24.21 | 23.87
2017-04-14 | 4.17 | 0.86
2017-04-14 00:30 | 8.36 | -7.04
2017-04-14 01:00 | 9.04 | -6.18
2017-04-14 01:30 | 13.08 | -10.89
2017-04-14 02:00 | 15.45 | -12.93
2017-04-14 02:30 | 26.3 | -19.11
2017-04-14 03:00 | 28.9 | -24.2
2017-04-14 03:30 | 27.49 | -22.33
2017-04-14 04:00 | 24.98 | -19.02
2017-04-14 04:30 | 23.09 | -15.32
2017-04-14 05:00 | 23.15 | -14.51
2017-04-14 05:30 | 22.32 | -11.4
2017-04-14 06:00 | 23.34 | -13.49
2017-04-14 06:30 | 23.61 | -17.7
2017-04-14 07:00 | 23.32 | -18.24
2017-04-14 07:30 | 19.63 | -13.82
2017-04-14 08:00 | 15.2 | -10.56
2017-04-14 08:30 | 7.35 | -4.37
2017-04-14 09:00 | 1.7 | 0.22
2017-04-14 09:30 | 22.84 | -0.33
2017-04-14 10:00 | 32.55 | -3.68
2017-04-14 10:30 | 34.31 | -10.68
2017-04-14 11:00 | 19.89 | -18.89
2017-04-14 11:30 | 26.51 | -26.48
2017-04-14 12:00 | 29.57 | -29.57
2017-04-14 12:30 | 28.87 | -28.86
2017-04-14 13:00 | 20.32 | -20.31
2017-04-14 13:30 | 23.08 | -23.06
2017-04-14 14:00 | 10.47 | -10.45
2017-04-14 14:30 | 14.73 | -14.68
2017-04-14 15:00 | 9.14 | -9.08
2017-04-14 15:30 | 8 | 1.65
2017-04-14 16:00 | 10.89 | -0.5
2017-04-14 16:30 | 11.63 | -0.23
2017-04-14 17:00 | 14.88 | 9.67
2017-04-14 17:30 | 19.61 | 17.2
2017-04-14 18:00 | 25.37 | 24.25
2017-04-14 18:30 | 37.4 | 36.7
2017-04-14 19:00 | 33.93 | 32.97
2017-04-14 19:30 | 23.18 | 21.72
2017-04-14 20:00 | 19.59 | 17.42
2017-04-14 20:30 | 16.81 | 14.33
2017-04-14 21:00 | 12.12 | 7.26
2017-04-14 21:30 | 10.57 | 3.01
2017-04-14 22:00 | 10.49 | -6.24
2017-04-14 22:30 | 11.24 | 10.45
2017-04-14 23:00 | 23.28 | 22.62
2017-04-14 23:30 | 16.5 | 15.13
2017-04-15 | 6.52 | 1.12
2017-04-15 00:30 | 12.05 | -10.9
2017-04-15 01:00 | 19.66 | -19.31
2017-04-15 01:30 | 22.35 | -22.13
2017-04-15 02:00 | 24.11 | -23.94
2017-04-15 02:30 | 28.46 | -28.4
2017-04-15 03:00 | 34.31 | -34.31
2017-04-15 03:30 | 32.05 | -32.03
2017-04-15 04:00 | 34.11 | -34.1
2017-04-15 04:30 | 31.4 | -31.35
2017-04-15 05:00 | 26.93 | -26.75
2017-04-15 05:30 | 19.99 | -19.3
2017-04-15 06:00 | 15.12 | -14.01
2017-04-15 06:30 | 14.25 | -12.4
2017-04-15 07:00 | 18.94 | -6.12
2017-04-15 07:30 | 21.98 | -4.64
2017-04-15 08:00 | 18.75 | -8.16
2017-04-15 08:30 | 6.53 | -6.48
2017-04-15 09:00 | 6.39 | -5.4
2017-04-15 09:30 | 8.61 | -6.67
2017-04-15 10:00 | 11.58 | -8.96
2017-04-15 10:30 | 28.6 | -16.24
2017-04-15 11:00 | 30.75 | -16.83
2017-04-15 11:30 | 30.7 | -16.43
2017-04-15 12:00 | 28.35 | -12.04
2017-04-15 12:30 | 25.65 | -5.1
2017-04-15 13:00 | 25.04 | -4.44
2017-04-15 13:30 | 26.3 | -7.56
2017-04-15 14:00 | 37.88 | 3.53
2017-04-15 14:30 | 50.2 | 3.14
2017-04-15 15:00 | 39.81 | -10.19
2017-04-15 15:30 | 38.54 | 5.23
2017-04-15 16:00 | 46.56 | 27.45
2017-04-15 16:30 | 59.75 | 46.84
2017-04-15 17:00 | 76.5 | 67.58
2017-04-15 17:30 | 71.94 | 62.34
2017-04-15 18:00 | 80.19 | 71.43
2017-04-15 18:30 | 93.47 | 93.07
2017-04-15 19:00 | 84.16 | 83.99
2017-04-15 19:30 | 43.04 | 42.88
2017-04-15 20:00 | 39.06 | 36.46
2017-04-15 20:30 | 29.3 | 24.82
2017-04-15 21:00 | 24.39 | 19.86
2017-04-15 21:30 | 14.03 | 13.82
2017-04-15 22:00 | 3.71 | 3.52
2017-04-15 22:30 | 19.6 | 19.43
2017-04-15 23:00 | 32.09 | 31.83
2017-04-15 23:30 | 19.43 | 18.63
2017-04-16 | 5.56 | -0.04
2017-04-16 00:30 | 12.98 | -12.2
2017-04-16 01:00 | 20.78 | -20.4
2017-04-16 01:30 | 24.6 | -24.32
2017-04-16 02:00 | 26.2 | -25.97
2017-04-16 02:30 | 29.32 | -29.26
2017-04-16 03:00 | 31.31 | -31.29
2017-04-16 03:30 | 29.24 | -27.53
2017-04-16 04:00 | 29.93 | -28.02
2017-04-16 04:30 | 33.18 | -32.18
2017-04-16 05:00 | 28.96 | -27.02
2017-04-16 05:30 | 26.62 | -23.66
2017-04-16 06:00 | 24.76 | -21.06
2017-04-16 06:30 | 21.08 | -16.55
2017-04-16 07:00 | 19.58 | -12.77
2017-04-16 07:30 | 22.2 | -14.88
2017-04-16 08:00 | 24.06 | -16.93
2017-04-16 08:30 | 23.67 | -17.7
2017-04-16 09:00 | 23.85 | -23.38
2017-04-16 09:30 | 13.19 | -11.43
2017-04-16 10:00 | 20.55 | -18.72
2017-04-16 10:30 | 30.32 | -13.67
2017-04-16 11:00 | 39.04 | -25.92
2017-04-16 11:30 | 41.16 | -34.21
2017-04-16 12:00 | 43.83 | -37.18
2017-04-16 12:30 | 44.74 | -38.3
2017-04-16 13:00 | 45.31 | -38.53
2017-04-16 13:30 | 38.65 | -30.21
2017-04-16 14:00 | 40.77 | -32.69
2017-04-16 14:30 | 41.48 | -34.12
2017-04-16 15:00 | 31.36 | -21.87
2017-04-16 15:30 | 25.34 | -13.24
2017-04-16 16:00 | 23.55 | -9.04
2017-04-16 16:30 | 21.85 | 6.55
2017-04-16 17:00 | 43.96 | 39.58
2017-04-16 17:30 | 43.71 | 39.34
2017-04-16 18:00 | 57.54 | 53.52
2017-04-16 18:30 | 82.01 | 79.1
2017-04-16 19:00 | 80.63 | 77.86
2017-04-16 19:30 | 68.4 | 66.84
2017-04-16 20:00 | 50.69 | 50.66
2017-04-16 20:30 | 38.62 | 38.61
2017-04-16 21:00 | 21.28 | 21.28
2017-04-16 21:30 | 12.68 | 12.58
2017-04-16 22:00 | 5.31 | 4.23
2017-04-16 22:30 | 16.9 | 16.24
2017-04-16 23:00 | 27.04 | 26.34
2017-04-16 23:30 | 16.27 | 14.71
2017-04-17 | 6.62 | -2.62
2017-04-17 00:30 | 13.99 | -13.29
2017-04-17 01:00 | 20.97 | -20.72
2017-04-17 01:30 | 26.37 | -26.24
2017-04-17 02:00 | 26.75 | -26.01
2017-04-17 02:30 | 29.47 | -27.56
2017-04-17 03:00 | 29.25 | -27.38
2017-04-17 03:30 | 28.31 | -26.44
2017-04-17 04:00 | 28.24 | -26.3
2017-04-17 04:30 | 26.39 | -23.84
2017-04-17 05:00 | 25.55 | -22.71
2017-04-17 05:30 | 24.48 | -20.48
2017-04-17 06:00 | 22.02 | -16.54
2017-04-17 06:30 | 19.56 | -13.27
2017-04-17 07:00 | 21.56 | -16.49
2017-04-17 07:30 | 22.63 | -14.7
2017-04-17 08:00 | 21.06 | -10.33
2017-04-17 08:30 | 14.97 | -7.99
2017-04-17 09:00 | 1.93 | -0.21
2017-04-17 09:30 | 4.7 | 0.68
2017-04-17 10:00 | 7.39 | -2.71
2017-04-17 10:30 | 13.04 | -10.46
2017-04-17 11:00 | 20.08 | -18.2
2017-04-17 11:30 | 23.87 | -22.19
2017-04-17 12:00 | 22.95 | -21.26
2017-04-17 12:30 | 23.69 | -22.28
2017-04-17 13:00 | 25.84 | -24.49
2017-04-17 13:30 | 26.76 | -25.55
2017-04-17 14:00 | 23.42 | -22.36
2017-04-17 14:30 | 17.47 | -15.94
2017-04-17 15:00 | 12.52 | -10.59
2017-04-17 15:30 | 12.22 | 10.8
2017-04-17 16:00 | 17.6 | 16.69
2017-04-17 16:30 | 31.1 | 29.04
2017-04-17 17:00 | 52.14 | 51.81
2017-04-17 17:30 | 65.02 | 64.91
2017-04-17 18:00 | 77.83 | 77.64
2017-04-17 18:30 | 84.9 | 84.55
2017-04-17 19:00 | 74.35 | 73.5
2017-04-17 19:30 | 52.07 | 49.07
2017-04-17 20:00 | 44.33 | 41.27
2017-04-17 20:30 | 28.46 | 27.86
2017-04-17 21:00 | 18.6 | 18.54
2017-04-17 21:30 | 16.47 | 16.22
2017-04-17 22:00 | 7.73 | 6.49
2017-04-17 22:30 | 16.78 | 15.7
2017-04-17 23:00 | 26.14 | 25.11
2017-04-17 23:30 | 18.74 | 16.87
2017-04-18 | 7.31 | -2.14
2017-04-18 00:30 | 14.47 | -13.34
2017-04-18 01:00 | 20.93 | -20.44
2017-04-18 01:30 | 23.58 | -22.93
2017-04-18 02:00 | 28.07 | -24.38
2017-04-18 02:30 | 27.96 | -24.29
2017-04-18 03:00 | 28.23 | -24.81
2017-04-18 03:30 | 26.69 | -23
2017-04-18 04:00 | 24.83 | -20.15
2017-04-18 04:30 | 23.46 | -17.11
2017-04-18 05:00 | 22.7 | -14.93
2017-04-18 05:30 | 22.56 | -12.08
2017-04-18 06:00 | 19.75 | -9.25
2017-04-18 06:30 | 13.72 | 2.2
2017-04-18 07:00 | 26.28 | 23.78
2017-04-18 07:30 | 42.89 | 32.29
2017-04-18 08:00 | 51.1 | 17.84
2017-04-18 08:30 | 52.76 | 9.47
2017-04-18 09:00 | 55.19 | 3.33
2017-04-18 09:30 | 58.32 | -6.81
2017-04-18 10:00 | 60.58 | -4.14
2017-04-18 10:30 | 62.02 | -3.23
2017-04-18 11:00 | 61.78 | -1.13
2017-04-18 11:30 | 62.63 | -7.44
2017-04-18 12:00 | 63.06 | -5.65
2017-04-18 12:30 | 62.8 | -3.61
2017-04-18 13:00 | 62.74 | 2.89
2017-04-18 13:30 | 62.57 | 5.6
2017-04-18 14:00 | 64.08 | 14.4
2017-04-18 14:30 | 68.67 | 25.07
2017-04-18 15:00 | 69.95 | 28.46
2017-04-18 15:30 | 70.06 | 31.05
2017-04-18 16:00 | 70.26 | 34.43
2017-04-18 16:30 | 68.7 | 32.97
2017-04-18 17:00 | 74.39 | 45.53
2017-04-18 17:30 | 82.88 | 60.59
2017-04-18 18:00 | 95.35 | 76.86
2017-04-18 18:30 | 107.97 | 91.59
2017-04-18 19:00 | 104.54 | 88.27
2017-04-18 19:30 | 82.16 | 61.62
2017-04-18 20:00 | 67.38 | 41.56
2017-04-18 20:30 | 60.85 | 33.04
2017-04-18 21:00 | 41.98 | 20.3
2017-04-18 21:30 | 35.07 | 17.74
2017-04-18 22:00 | 30.22 | 9.34
2017-04-18 22:30 | 37.4 | 25.93
2017-04-18 23:00 | 56.67 | 50.9
2017-04-18 23:30 | 33.42 | 24.43
2017-04-19 | 22.09 | 2.12
2017-04-19 00:30 | 25.27 | -11.12
2017-04-19 01:00 | 30.78 | -18.75
2017-04-19 01:30 | 33.05 | -22.08
2017-04-19 02:00 | 37.15 | -27.02
2017-04-19 02:30 | 35.99 | -25.68
2017-04-19 03:00 | 27.26 | -23.14
2017-04-19 03:30 | 23.52 | -22.57
2017-04-19 04:00 | 20.85 | -20.06
2017-04-19 04:30 | 17.28 | -16.77
2017-04-19 05:00 | 16.96 | -16.41
2017-04-19 05:30 | 9.04 | -7.44
2017-04-19 06:00 | 6.95 | 3.07
2017-04-19 06:30 | 15.39 | 13.52
2017-04-19 07:00 | 53.86 | 53.22
2017-04-19 07:30 | 53.71 | 47.6
2017-04-19 08:00 | 72.63 | 31.58
2017-04-19 08:30 | 70.19 | 16.13
2017-04-19 09:00 | 48.5 | 2.94
2017-04-19 09:30 | 41.88 | -6.08
2017-04-19 10:00 | 40.28 | 6.15
2017-04-19 10:30 | 33.75 | 15.94
2017-04-19 11:00 | 29.52 | 1.47
2017-04-19 11:30 | 20.01 | 3.5
2017-04-19 12:00 | 13.03 | -2.68
2017-04-19 12:30 | 12.91 | -5.7
2017-04-19 13:00 | 14.98 | -9.32
2017-04-19 13:30 | 12.52 | -4.62
2017-04-19 14:00 | 13.32 | -5.32
2017-04-19 14:30 | 14.98 | -8.76
2017-04-19 15:00 | 13.52 | -3.35
2017-04-19 15:30 | 15.61 | 9.34
2017-04-19 16:00 | 36.85 | 35.12
2017-04-19 16:30 | 54.82 | 53.99
2017-04-19 17:00 | 66.95 | 66.35
2017-04-19 17:30 | 63.22 | 62.68
2017-04-19 18:00 | 72.72 | 71.72
2017-04-19 18:30 | 90.36 | 89.22
2017-04-19 19:00 | 85.96 | 85.19
2017-04-19 19:30 | 78.51 | 78.01
2017-04-19 20:00 | 70.2 | 70.1
2017-04-19 20:30 | 64.9 | 64.82
2017-04-19 21:00 | 34.58 | 34.46
2017-04-19 21:30 | 34.26 | 34.25
2017-04-19 22:00 | 23.75 | 23.7
2017-04-19 22:30 | 53.31 | 53.21
2017-04-19 23:00 | 66.26 | 66.06
2017-04-19 23:30 | 32.27 | 31.38
2017-04-20 | 8.92 | 4.21
2017-04-20 00:30 | 8.67 | -4.69
2017-04-20 01:00 | 15.05 | -13.72
2017-04-20 01:30 | 18.45 | -17.47
2017-04-20 02:00 | 20.43 | -19.89
2017-04-20 02:30 | 22.41 | -19.29
2017-04-20 03:00 | 25.11 | -20.06
2017-04-20 03:30 | 24.96 | -19.79
2017-04-20 04:00 | 22.99 | -16.16
2017-04-20 04:30 | 22.01 | -12.85
2017-04-20 05:00 | 22.62 | -14.39
2017-04-20 05:30 | 18.39 | -3.89
2017-04-20 06:00 | 19.61 | 6.95
2017-04-20 06:30 | 20.87 | 18.82
2017-04-20 07:00 | 52.76 | 51.1
2017-04-20 07:30 | 61.7 | 59.15
2017-04-20 08:00 | 48.5 | 43.87
2017-04-20 08:30 | 42.8 | 35.1
2017-04-20 09:00 | 39.03 | 28.37
2017-04-20 09:30 | 41.42 | 30.4
2017-04-20 10:00 | 32.89 | 12.53
2017-04-20 10:30 | 31.35 | 0.29
2017-04-20 11:00 | 32.53 | -5.1
2017-04-20 11:30 | 34.94 | -13.37
2017-04-20 12:00 | 34.56 | -10.55
2017-04-20 12:30 | 32.6 | -5.65
2017-04-20 13:00 | 34.84 | -12.49
2017-04-20 13:30 | 39.79 | -22.24
2017-04-20 14:00 | 34.37 | -11.96
2017-04-20 14:30 | 32.02 | -3.79
2017-04-20 15:00 | 31.14 | -3
2017-04-20 15:30 | 28.86 | -1.72
2017-04-20 16:00 | 28.94 | 5.72
2017-04-20 16:30 | 35.98 | 23.68
2017-04-20 17:00 | 53.79 | 47.1
2017-04-20 17:30 | 61.1 | 55.11
2017-04-20 18:00 | 82.12 | 76.76
2017-04-20 18:30 | 92.71 | 90.89
2017-04-20 19:00 | 97.27 | 96.12
2017-04-20 19:30 | 71.8 | 70.82
2017-04-20 20:00 | 54.85 | 53.88
2017-04-20 20:30 | 58.2 | 57.79
2017-04-20 21:00 | 29.06 | 28.51
2017-04-20 21:30 | 17.59 | 17.37
2017-04-20 22:00 | 10.57 | 10.52
2017-04-20 22:30 | 28.38 | 28.32
2017-04-20 23:00 | 49.72 | 49.51
2017-04-20 23:30 | 26.05 | 25.19
2017-04-21 | 7.01 | 1.27
2017-04-21 00:30 | 11.94 | -10.83
2017-04-21 01:00 | 18.11 | -17.71
2017-04-21 01:30 | 24.2 | -23.97
2017-04-21 02:00 | 27.6 | -27.44
2017-04-21 02:30 | 29.28 | -29.17
2017-04-21 03:00 | 32.77 | -32.74
2017-04-21 03:30 | 32.85 | -32.82
2017-04-21 04:00 | 31.48 | -31.43
2017-04-21 04:30 | 31.69 | -31.63
2017-04-21 05:00 | 23.31 | -23
2017-04-21 05:30 | 9.14 | -4.26
2017-04-21 06:00 | 10.66 | 7.62
2017-04-21 06:30 | 35.41 | 34.99
2017-04-21 07:00 | 78.54 | 78.38
2017-04-21 07:30 | 84.54 | 84.51
2017-04-21 08:00 | 64.33 | 64.32
2017-04-21 08:30 | 34.54 | 34.36
2017-04-21 09:00 | 29.84 | 27.43
2017-04-21 09:30 | 36.89 | 23.22
2017-04-21 10:00 | 26.05 | 20.11
2017-04-21 10:30 | 28.71 | 24.28
2017-04-21 11:00 | 33.54 | 30.31
2017-04-21 11:30 | 30.25 | 26.87
2017-04-21 12:00 | 41.27 | 38.61
2017-04-21 12:30 | 33.72 | 30.98
2017-04-21 13:00 | 28.48 | 25.42
2017-04-21 13:30 | 16.12 | 9.36
2017-04-21 14:00 | 17.59 | 12.46
2017-04-21 14:30 | 23.75 | 20.56
2017-04-21 15:00 | 23.73 | 21.06
2017-04-21 15:30 | 14.45 | 10.53
2017-04-21 16:00 | 14.43 | 11.54
2017-04-21 16:30 | 42.51 | 41.85
2017-04-21 17:00 | 46.08 | 45.76
2017-04-21 17:30 | 51.7 | 51.43
2017-04-21 18:00 | 63.84 | 62.04
2017-04-21 18:30 | 71.71 | 71.18
2017-04-21 19:00 | 69.61 | 69.21
2017-04-21 19:30 | 52.07 | 52.04
2017-04-21 20:00 | 48.72 | 48.69
2017-04-21 20:30 | 44.68 | 44.62
2017-04-21 21:00 | 38.26 | 38.06
2017-04-21 21:30 | 32.29 | 32.27
2017-04-21 22:00 | 22.59 | 22.54
2017-04-21 22:30 | 70.95 | 70.86
2017-04-21 23:00 | 78.52 | 78.24
2017-04-21 23:30 | 44.58 | 43.93
2017-04-22 | 10.11 | 5.78
2017-04-22 00:30 | 13.73 | -7.51
2017-04-22 01:00 | 25.15 | -15.44
2017-04-22 01:30 | 24.9 | -17.71
2017-04-22 02:00 | 27.43 | -22.67
2017-04-22 02:30 | 27.66 | -23.11
2017-04-22 03:00 | 28.41 | -24.59
2017-04-22 03:30 | 27.78 | -23.89
2017-04-22 04:00 | 27.52 | -23.95
2017-04-22 04:30 | 27.31 | -23.38
2017-04-22 05:00 | 27.05 | -22.85
2017-04-22 05:30 | 27.64 | -23.08
2017-04-22 06:00 | 25.36 | -18.33
2017-04-22 06:30 | 22.7 | -15.35
2017-04-22 07:00 | 20.36 | -10.38
2017-04-22 07:30 | 19.49 | -0.84
2017-04-22 08:00 | 18.87 | 7.27
2017-04-22 08:30 | 15.65 | 7.94
2017-04-22 09:00 | 8.69 | 8.21
2017-04-22 09:30 | 7.94 | 6.08
2017-04-22 10:00 | 7.7 | 4.4
2017-04-22 10:30 | 7.37 | 1.94
2017-04-22 11:00 | 8.15 | -3.83
2017-04-22 11:30 | 9.7 | -6.8
2017-04-22 12:00 | 6.44 | -2.03
2017-04-22 12:30 | 12.98 | -11.52
2017-04-22 13:00 | 9.6 | -7.78
2017-04-22 13:30 | 9.68 | -6.05
2017-04-22 14:00 | 10.03 | -1.54
2017-04-22 14:30 | 10.11 | -0.57
2017-04-22 15:00 | 10 | 1.02
2017-04-22 15:30 | 10.57 | 4.72
2017-04-22 16:00 | 14.7 | 11.41
2017-04-22 16:30 | 13.94 | 10
2017-04-22 17:00 | 24.19 | 21.01
2017-04-22 17:30 | 32.47 | 30.18
2017-04-22 18:00 | 45.02 | 35.95
2017-04-22 18:30 | 49.01 | 44
2017-04-22 19:00 | 48.47 | 47.14
2017-04-22 19:30 | 30.48 | 28.79
2017-04-22 20:00 | 26.85 | 22.3
2017-04-22 20:30 | 24.05 | 21.56
2017-04-22 21:00 | 18.6 | 17.85
2017-04-22 21:30 | 15.15 | 14.44
2017-04-22 22:00 | 11.82 | 11.44
2017-04-22 22:30 | 20.54 | 20.45
2017-04-22 23:00 | 28.31 | 28.31
2017-04-22 23:30 | 20.42 | 20.39
2017-04-23 | 8.75 | 8.5
2017-04-23 00:30 | 2.02 | 0.73
2017-04-23 01:00 | 3.01 | -2.58
2017-04-23 01:30 | 6.21 | -5.89
2017-04-23 02:00 | 9.42 | -5.52
2017-04-23 02:30 | 10.32 | -4.73
2017-04-23 03:00 | 10.3 | -4.91
2017-04-23 03:30 | 10.05 | -4.36
2017-04-23 04:00 | 9.64 | -4.08
2017-04-23 04:30 | 10 | -4.02
2017-04-23 05:00 | 10.61 | -3.91
2017-04-23 05:30 | 10.98 | -1.3
2017-04-23 06:00 | 10.92 | -1.44
2017-04-23 06:30 | 8.01 | -0.44
2017-04-23 07:00 | 9.07 | 1.36
2017-04-23 07:30 | 12.09 | 1.7
2017-04-23 08:00 | 13.8 | 3.1
2017-04-23 08:30 | 11.54 | 2.33
2017-04-23 09:00 | 8.46 | 1.13
2017-04-23 09:30 | 0.93 | 0.37
2017-04-23 10:00 | 9.72 | -3.87
2017-04-23 10:30 | 12.65 | -7.93
2017-04-23 11:00 | 11.45 | -3.82
2017-04-23 11:30 | 10.79 | 1.37
2017-04-23 12:00 | 11.77 | -4.92
2017-04-23 12:30 | 11.16 | -2.65
2017-04-23 13:00 | 10.87 | 1.83
2017-04-23 13:30 | 13.15 | -6.61
2017-04-23 14:00 | 10.95 | -0.13
2017-04-23 14:30 | 10.93 | -2.15
2017-04-23 15:00 | 10.91 | -2.32
2017-04-23 15:30 | 11.11 | 2.08
2017-04-23 16:00 | 12.33 | 6.3
2017-04-23 16:30 | 11.72 | 11.71
2017-04-23 17:00 | 21.75 | 21.75
2017-04-23 17:30 | 33.62 | 33.55
2017-04-23 18:00 | 57.49 | 57.27
2017-04-23 18:30 | 80.85 | 80.7
2017-04-23 19:00 | 96.44 | 96.42
2017-04-23 19:30 | 86.66 | 86.66
2017-04-23 20:00 | 72.37 | 72.34
2017-04-23 20:30 | 55.15 | 55.04
2017-04-23 21:00 | 27.48 | 27.21
2017-04-23 21:30 | 15.96 | 15.93
2017-04-23 22:00 | 11.96 | 11.92
2017-04-23 22:30 | 17.86 | 17.84
2017-04-23 23:00 | 25.44 | 25.43
2017-04-23 23:30 | 19.9 | 19.81
2017-04-24 | 9.5 | 9.34
2017-04-24 00:30 | 2.37 | 2.12
2017-04-24 01:00 | 3.76 | -3.33
2017-04-24 01:30 | 6.57 | -6.11
2017-04-24 02:00 | 11.93 | -5.84
2017-04-24 02:30 | 11.79 | -4.7
2017-04-24 03:00 | 11.7 | -4.62
2017-04-24 03:30 | 11.57 | -3.88
2017-04-24 04:00 | 11.54 | -3.89
2017-04-24 04:30 | 11.53 | -3.1
2017-04-24 05:00 | 10.94 | -1.45
2017-04-24 05:30 | 13.32 | 0.66
2017-04-24 06:00 | 13.95 | 3.26
2017-04-24 06:30 | 15.8 | 11.27
2017-04-24 07:00 | 21.79 | 19.19
2017-04-24 07:30 | 26.39 | 26.39
2017-04-24 08:00 | 27.15 | 27.14
2017-04-24 08:30 | 25.49 | 25.35
2017-04-24 09:00 | 23.14 | 22.74
2017-04-24 09:30 | 18.09 | 16.46
2017-04-24 10:00 | 19.73 | 17.41
2017-04-24 10:30 | 14.36 | 10.57
2017-04-24 11:00 | 19.27 | 16.97
2017-04-24 11:30 | 19.5 | 17.05
2017-04-24 12:00 | 20.17 | 17.64
2017-04-24 12:30 | 18.67 | 15.97
2017-04-24 13:00 | 18.86 | 16.63
2017-04-24 13:30 | 18.06 | 15.45
2017-04-24 14:00 | 16.65 | 13.6
2017-04-24 14:30 | 23.92 | 22.08
2017-04-24 15:00 | 23.16 | 23.03
2017-04-24 15:30 | 12.49 | 12.46
2017-04-24 16:00 | 12.42 | 12.38
2017-04-24 16:30 | 25.43 | 25.3
2017-04-24 17:00 | 46.24 | 46.01
2017-04-24 17:30 | 50.61 | 50.46
2017-04-24 18:00 | 44.59 | 44.57
2017-04-24 18:30 | 49.15 | 49.12
2017-04-24 19:00 | 57.94 | 57.85
2017-04-24 19:30 | 39.24 | 38.94
2017-04-24 20:00 | 30.78 | 30.15
2017-04-24 20:30 | 29.88 | 29.83
2017-04-24 21:00 | 18.08 | 17.84
2017-04-24 21:30 | 14.86 | 14.74
2017-04-24 22:00 | 3.54 | 3.46
2017-04-24 22:30 | 23.91 | 23.84
2017-04-24 23:00 | 31.61 | 31.4
2017-04-24 23:30 | 18.84 | 18.2
2017-04-25 | 4.17 | -1.49
2017-04-25 00:30 | 13.45 | -13.16
2017-04-25 01:00 | 23.19 | -23.14
2017-04-25 01:30 | 32.66 | -32.66
2017-04-25 02:00 | 27.55 | -27.54
2017-04-25 02:30 | 27.04 | -26.98
2017-04-25 03:00 | 32.07 | -32.06
2017-04-25 03:30 | 30.54 | -30.52
2017-04-25 04:00 | 26.33 | -26.27
2017-04-25 04:30 | 19.05 | -18.53
2017-04-25 05:00 | 22.56 | -21.98
2017-04-25 05:30 | 19.44 | -18.49
2017-04-25 06:00 | 18.31 | -17.33
2017-04-25 06:30 | 14.89 | -13.95
2017-04-25 07:00 | 12.23 | -10.13
2017-04-25 07:30 | 10.22 | -6.34
2017-04-25 08:00 | 14.24 | -11.41
2017-04-25 08:30 | 9.44 | -6.3
2017-04-25 09:00 | 10.4 | -9.33
2017-04-25 09:30 | 13.08 | -13.01
2017-04-25 10:00 | 1.43 | -1.21
2017-04-25 10:30 | 1.32 | -0.66
2017-04-25 11:00 | 8.61 | -8.38
2017-04-25 11:30 | 5.09 | -4.67
2017-04-25 12:00 | 28.63 | -28.53
2017-04-25 12:30 | 32.27 | -32.19
2017-04-25 13:00 | 30.02 | -29.93
2017-04-25 13:30 | 32.52 | -32.44
2017-04-25 14:00 | 22.92 | -22.85
2017-04-25 14:30 | 19.22 | -19.14
2017-04-25 15:00 | 15.87 | -15.81
2017-04-25 15:30 | 7.72 | -7.68
2017-04-25 16:00 | 2.79 | 2.79
2017-04-25 16:30 | 19.29 | 19.29
2017-04-25 17:00 | 29.52 | 29.52
2017-04-25 17:30 | 52.92 | 52.92
2017-04-25 18:00 | 95.17 | 90.72
2017-04-25 18:30 | 94.35 | 87.69
2017-04-25 19:00 | 96.42 | 90.11
2017-04-25 19:30 | 85.77 | 79.24
2017-04-25 20:00 | 79.98 | 78.48
2017-04-25 20:30 | 57.99 | 57.84
2017-04-25 21:00 | 43.2 | 43.07
2017-04-25 21:30 | 36.87 | 36.52
2017-04-25 22:00 | 17.2 | 16.24
2017-04-25 22:30 | 32.94 | 32.28
2017-04-25 23:00 | 58.92 | 58.35
2017-04-25 23:30 | 37.06 | 35.95
2017-04-26 | 15.98 | 13.36
2017-04-26 00:30 | 7.57 | 0.41
2017-04-26 01:00 | 12.2 | -10.5
2017-04-26 01:30 | 13.88 | -12.3
2017-04-26 02:00 | 19.3 | -9.89
2017-04-26 02:30 | 21.95 | -13.65
2017-04-26 03:00 | 24.76 | -19.45
2017-04-26 03:30 | 22.96 | -16.19
2017-04-26 04:00 | 21.68 | -13.34
2017-04-26 04:30 | 21.11 | -10.49
2017-04-26 05:00 | 21.22 | -7.67
2017-04-26 05:30 | 22.28 | 0.83
2017-04-26 06:00 | 25.88 | 12.77
2017-04-26 06:30 | 34.08 | 27.06
2017-04-26 07:00 | 51.42 | 51.35
2017-04-26 07:30 | 43.75 | 41.73
2017-04-26 08:00 | 49.1 | 32.94
2017-04-26 08:30 | 46.45 | 23.84
2017-04-26 09:00 | 49.73 | 23.11
2017-04-26 09:30 | 60.51 | 39.53
2017-04-26 10:00 | 70.51 | 53.5
2017-04-26 10:30 | 63.91 | 44.45
2017-04-26 11:00 | 57.75 | 33.25
2017-04-26 11:30 | 62.98 | 40.97
2017-04-26 12:00 | 75.64 | 59.36
2017-04-26 12:30 | 74.51 | 58.78
2017-04-26 13:00 | 71.64 | 55.74
2017-04-26 13:30 | 59.59 | 39.67
2017-04-26 14:00 | 59.56 | 39.26
2017-04-26 14:30 | 67.42 | 50.41
2017-04-26 15:00 | 77.93 | 65.06
2017-04-26 15:30 | 83.23 | 71.59
2017-04-26 16:00 | 93.2 | 83.25
2017-04-26 16:30 | 93.96 | 85.18
2017-04-26 17:00 | 91.34 | 82.36
2017-04-26 17:30 | 91.01 | 80.8
2017-04-26 18:00 | 100.95 | 91.4
2017-04-26 18:30 | 101.52 | 91.89
2017-04-26 19:00 | 97.15 | 88.18
2017-04-26 19:30 | 84.74 | 75.38
2017-04-26 20:00 | 62.69 | 57.56
2017-04-26 20:30 | 53.33 | 48.99
2017-04-26 21:00 | 40.12 | 35.23
2017-04-26 21:30 | 32.87 | 28.61
2017-04-26 22:00 | 22.84 | 18.02
2017-04-26 22:30 | 45.97 | 44.68
2017-04-26 23:00 | 67.76 | 67.36
2017-04-26 23:30 | 32.48 | 32.35
2017-04-27 | 10.84 | 5.6
2017-04-27 00:30 | 11.41 | -9.13
2017-04-27 01:00 | 18.38 | -17.48
2017-04-27 01:30 | 21.98 | -21.31
2017-04-27 02:00 | 22.79 | -22.13
2017-04-27 02:30 | 28.45 | -28.1
2017-04-27 03:00 | 31.56 | -31.45
2017-04-27 03:30 | 27.46 | -27.23
2017-04-27 04:00 | 24.22 | -23.78
2017-04-27 04:30 | 21.73 | -20.93
2017-04-27 05:00 | 20.97 | -20.02
2017-04-27 05:30 | 16.66 | -15.28
2017-04-27 06:00 | 7.48 | -3.17
2017-04-27 06:30 | 17.86 | 17.13
2017-04-27 07:00 | 41.83 | 41.63
2017-04-27 07:30 | 39.24 | 39.24
2017-04-27 08:00 | 28.98 | 28.98
2017-04-27 08:30 | 13.31 | 12.58
2017-04-27 09:00 | 7.43 | -4.3
2017-04-27 09:30 | 11.24 | -9.05
2017-04-27 10:00 | 19.66 | -17.68
2017-04-27 10:30 | 28.93 | -26.45
2017-04-27 11:00 | 38.46 | -36
2017-04-27 11:30 | 42.02 | -39.78
2017-04-27 12:00 | 42.72 | -40.62
2017-04-27 12:30 | 41.88 | -39.88
2017-04-27 13:00 | 37.49 | -35.37
2017-04-27 13:30 | 31 | -28.88
2017-04-27 14:00 | 24.22 | -21.42
2017-04-27 14:30 | 20.05 | -16.49
2017-04-27 15:00 | 13.49 | -8.88
2017-04-27 15:30 | 9.17 | 3.06
2017-04-27 16:00 | 29.73 | 29.01
2017-04-27 16:30 | 32.57 | 32.18
2017-04-27 17:00 | 37.34 | 37.3
2017-04-27 17:30 | 47.77 | 47.69
2017-04-27 18:00 | 58.65 | 58.65
2017-04-27 18:30 | 53 | 52.99
2017-04-27 19:00 | 74.93 | 74.93
2017-04-27 19:30 | 66.03 | 66.02
2017-04-27 20:00 | 52.33 | 52.31
2017-04-27 20:30 | 46.42 | 46.4
2017-04-27 21:00 | 34.2 | 34.14
2017-04-27 21:30 | 23.73 | 23.73
2017-04-27 22:00 | 14.8 | 14.47
2017-04-27 22:30 | 33.13 | 32.36
2017-04-27 23:00 | 43.2 | 42.3
2017-04-27 23:30 | 27.01 | 21.16
2017-04-28 | 17.73 | 2.32
2017-04-28 00:30 | 16.42 | -0.39
2017-04-28 01:00 | 15.98 | -4.7
2017-04-28 01:30 | 19.53 | -13.45
2017-04-28 02:00 | 23.41 | -19.67
2017-04-28 02:30 | 27 | -24.78
2017-04-28 03:00 | 30.95 | -29.84
2017-04-28 03:30 | 30.6 | -29.85
2017-04-28 04:00 | 28.44 | -27.43
2017-04-28 04:30 | 26.32 | -24.89
2017-04-28 05:00 | 25.43 | -22.74
2017-04-28 05:30 | 20.61 | -12.54
2017-04-28 06:00 | 18.88 | 1.76
2017-04-28 06:30 | 34.79 | 29.07
2017-04-28 07:00 | 74.3 | 72.24
2017-04-28 07:30 | 56.89 | 55.11
2017-04-28 08:00 | 32.56 | 30.31
2017-04-28 08:30 | 13.44 | 13.04
2017-04-28 09:00 | 6.5 | 1.5
2017-04-28 09:30 | 14.31 | -10.83
2017-04-28 10:00 | 21.87 | -19.25
2017-04-28 10:30 | 31.31 | -28.29
2017-04-28 11:00 | 33.08 | -29.62
2017-04-28 11:30 | 31.18 | -27.77
2017-04-28 12:00 | 29.46 | -26.23
2017-04-28 12:30 | 28.65 | -25.33
2017-04-28 13:00 | 17.74 | -12.77
2017-04-28 13:30 | 14.11 | -7.63
2017-04-28 14:00 | 18.1 | 14.8
2017-04-28 14:30 | 14.9 | 11.54
2017-04-28 15:00 | 10.52 | 7.03
2017-04-28 15:30 | 13.83 | 12.3
2017-04-28 16:00 | 15.04 | 13.31
2017-04-28 16:30 | 19.44 | 19.25
2017-04-28 17:00 | 40.71 | 40.59
2017-04-28 17:30 | 52.49 | 52.38
2017-04-28 18:00 | 60.32 | 60.31
2017-04-28 18:30 | 60.03 | 60.03
2017-04-28 19:00 | 71.7 | 71.54
2017-04-28 19:30 | 70.72 | 70.17
2017-04-28 20:00 | 65.71 | 65.66
2017-04-28 20:30 | 56.23 | 56.21
2017-04-28 21:00 | 25.79 | 25.77
2017-04-28 21:30 | 25.19 | 25.13
2017-04-28 22:00 | 13.26 | 12.97
2017-04-28 22:30 | 26.65 | 26.36
2017-04-28 23:00 | 51.23 | 51.04
2017-04-28 23:30 | 31.48 | 30.82
2017-04-29 | 8.55 | 5.19
2017-04-29 00:30 | 16.93 | -7.49
2017-04-29 01:00 | 24.27 | -19.11
2017-04-29 01:30 | 27.44 | -23.59
2017-04-29 02:00 | 28.45 | -25.3
2017-04-29 02:30 | 31.44 | -29.4
2017-04-29 03:00 | 29.13 | -27.32
2017-04-29 03:30 | 26.9 | -23.79
2017-04-29 04:00 | 28.79 | -26.43
2017-04-29 04:30 | 26.91 | -23.87
2017-04-29 05:00 | 24.3 | -20.14
2017-04-29 05:30 | 22.26 | -15.8
2017-04-29 06:00 | 21.45 | -12.58
2017-04-29 06:30 | 20.12 | -10.89
2017-04-29 07:00 | 19.98 | -4.35
2017-04-29 07:30 | 19.76 | -1.28
2017-04-29 08:00 | 18.69 | 0.1
2017-04-29 08:30 | 15.68 | -4.34
2017-04-29 09:00 | 12.85 | -6.19
2017-04-29 09:30 | 15.57 | -11.67
2017-04-29 10:00 | 20.21 | -19.39
2017-04-29 10:30 | 27.55 | -27.3
2017-04-29 11:00 | 31.13 | -30.94
2017-04-29 11:30 | 36.57 | -36.35
2017-04-29 12:00 | 39.68 | -39.49
2017-04-29 12:30 | 40.07 | -39.83
2017-04-29 13:00 | 38.61 | -38.22
2017-04-29 13:30 | 32.39 | -31.68
2017-04-29 14:00 | 26.96 | -26.05
2017-04-29 14:30 | 23.75 | -22.63
2017-04-29 15:00 | 19.3 | -17.79
2017-04-29 15:30 | 11.06 | -7.44
2017-04-29 16:00 | 18.94 | 16.39
2017-04-29 16:30 | 37.82 | 36.4
2017-04-29 17:00 | 56.96 | 56.95
2017-04-29 17:30 | 59.44 | 59.07
2017-04-29 18:00 | 65.25 | 65.16
2017-04-29 18:30 | 68.31 | 67.99
2017-04-29 19:00 | 66.22 | 65.44
2017-04-29 19:30 | 45.76 | 44.64
2017-04-29 20:00 | 31.13 | 31.1
2017-04-29 20:30 | 28.28 | 28.28
2017-04-29 21:00 | 20.78 | 20.77
2017-04-29 21:30 | 20.65 | 20.48
2017-04-29 22:00 | 16.48 | 15.83
2017-04-29 22:30 | 33.46 | 32.98
2017-04-29 23:00 | 53.8 | 53.36
2017-04-29 23:30 | 30.74 | 27.89
2017-04-30 | 22.66 | 8.18
2017-04-30 00:30 | 19.24 | -0.21
2017-04-30 01:00 | 20.53 | -10.38
2017-04-30 01:30 | 23.22 | -16.39
2017-04-30 02:00 | 24.16 | -18.37
2017-04-30 02:30 | 18.56 | -17.77
2017-04-30 03:00 | 16.76 | -16.61
2017-04-30 03:30 | 16.04 | -15.94
2017-04-30 04:00 | 15.6 | -15.49
2017-04-30 04:30 | 16.06 | -15.89
2017-04-30 05:00 | 15.68 | -15.41
2017-04-30 05:30 | 12.46 | -11.8
2017-04-30 06:00 | 12.66 | -11.45
2017-04-30 06:30 | 13.33 | -12.86
2017-04-30 07:00 | 7.39 | -7.02
2017-04-30 07:30 | 7.04 | -4.83
2017-04-30 08:00 | 8.75 | -4.16
2017-04-30 08:30 | 8.63 | 1.06
2017-04-30 09:00 | 9.54 | 6.04
2017-04-30 09:30 | 7.79 | -3.26
2017-04-30 10:00 | 12.85 | -9.18
2017-04-30 10:30 | 11.99 | -7.91
2017-04-30 11:00 | 16.86 | -14.33
2017-04-30 11:30 | 24.18 | -23.85
2017-04-30 12:00 | 30.07 | -29.33
2017-04-30 12:30 | 28.87 | -28.01
2017-04-30 13:00 | 31.02 | -30.19
2017-04-30 13:30 | 26.59 | -25.36
2017-04-30 14:00 | 21.56 | -19.86
2017-04-30 14:30 | 15.12 | -12.6
2017-04-30 15:00 | 10.34 | 2.15
2017-04-30 15:30 | 23.45 | 20.21
2017-04-30 16:00 | 27.89 | 24.79
2017-04-30 16:30 | 31.74 | 29.59
2017-04-30 17:00 | 44.15 | 43.15
2017-04-30 17:30 | 51.78 | 51.43
2017-04-30 18:00 | 80.12 | 80.12
2017-04-30 18:30 | 87.8 | 87.75
2017-04-30 19:00 | 91.49 | 91.49
2017-04-30 19:30 | 70.84 | 70.84
2017-04-30 20:00 | 49 | 48.99
2017-04-30 20:30 | 46.23 | 45.99
2017-04-30 21:00 | 40.38 | 35.91
2017-04-30 21:30 | 30.57 | 23.63
2017-04-30 22:00 | 29.3 | 19.78
2017-04-30 22:30 | 37.08 | 29.3
2017-04-30 23:00 | 54.75 | 50.35
2017-04-30 23:30 | 39.96 | 33.87
2017-05-01 | 22.22 | 10.19
2017-05-01 00:30 | 10.9 | 1.94
2017-05-01 01:00 | 5.14 | -1.98
2017-05-01 01:30 | 6.59 | -5.51
2017-05-01 02:00 | 8.5 | -8.07
2017-05-01 02:30 | 9.81 | -9.57
2017-05-01 03:00 | 9.83 | -9.72
2017-05-01 03:30 | 8.57 | -8.4
2017-05-01 04:00 | 7.71 | -7.5
2017-05-01 04:30 | 3.3 | 1.3
2017-05-01 05:00 | 3.42 | -1.92
2017-05-01 05:30 | 3.7 | 0.51
2017-05-01 06:00 | 5.81 | 3.59
2017-05-01 06:30 | 2.48 | -1.14
2017-05-01 07:00 | 2.19 | 1.73
2017-05-01 07:30 | 6.67 | 5.6
2017-05-01 08:00 | 6.9 | 5.76
2017-05-01 08:30 | 8.32 | 8.16
2017-05-01 09:00 | 12.99 | 12.81
2017-05-01 09:30 | 10.61 | 9.33
2017-05-01 10:00 | 6.95 | 5.44
2017-05-01 10:30 | 5.39 | 2.61
2017-05-01 11:00 | 5.57 | -2.49
2017-05-01 11:30 | 6.87 | -3.23
2017-05-01 12:00 | 10.09 | -6.29
2017-05-01 12:30 | 8.46 | -5.02
2017-05-01 13:00 | 15.21 | -12.87
2017-05-01 13:30 | 11.47 | -8.04
2017-05-01 14:00 | 11.29 | -7.91
2017-05-01 14:30 | 9.47 | -3.65
2017-05-01 15:00 | 10.58 | 5.51
2017-05-01 15:30 | 17.18 | 14.23
2017-05-01 16:00 | 20.54 | 18.13
2017-05-01 16:30 | 29.81 | 28.06
2017-05-01 17:00 | 56.22 | 56.22
2017-05-01 17:30 | 87.66 | 87.39
2017-05-01 18:00 | 119.33 | 119.23
2017-05-01 18:30 | 114.87 | 114.71
2017-05-01 19:00 | 97.21 | 97.18
2017-05-01 19:30 | 79.55 | 77.85
2017-05-01 20:00 | 75.53 | 73.72
2017-05-01 20:30 | 74 | 72.2
2017-05-01 21:00 | 78.38 | 78.35
2017-05-01 21:30 | 67.56 | 67.04
2017-05-01 22:00 | 42.31 | 41.68
2017-05-01 22:30 | 50.1 | 49.62
2017-05-01 23:00 | 66.96 | 66.55
2017-05-01 23:30 | 36 | 35.39
2017-05-02 | 11.59 | 11.19
2017-05-02 00:30 | 4.59 | 4.55
2017-05-02 01:00 | 3.61 | -3.61
2017-05-02 01:30 | 6.27 | -6.25
2017-05-02 02:00 | 8.05 | -7.98
2017-05-02 02:30 | 6.92 | -6.7
2017-05-02 03:00 | 8.24 | -7.86
2017-05-02 03:30 | 8.97 | -8.52
2017-05-02 04:00 | 4.26 | -4.2
2017-05-02 04:30 | 4.17 | -4.04
2017-05-02 05:00 | 2.47 | -1.14
2017-05-02 05:30 | 6.25 | 3.23
2017-05-02 06:00 | 21.57 | 19.63
2017-05-02 06:30 | 38.36 | 38.14
2017-05-02 07:00 | 59.77 | 59.53
2017-05-02 07:30 | 68.28 | 68.19
2017-05-02 08:00 | 66.5 | 66.49
2017-05-02 08:30 | 57.44 | 57.42
2017-05-02 09:00 | 60.29 | 60.29
2017-05-02 09:30 | 54.79 | 54.44
2017-05-02 10:00 | 53.5 | 53.26
2017-05-02 10:30 | 51.36 | 51.08
2017-05-02 11:00 | 50.66 | 50.47
2017-05-02 11:30 | 42.81 | 42.64
2017-05-02 12:00 | 48.74 | 48.64
2017-05-02 12:30 | 40.22 | 40.11
2017-05-02 13:00 | 35.91 | 35.85
2017-05-02 13:30 | 42.53 | 42.52
2017-05-02 14:00 | 52.81 | 52.81
2017-05-02 14:30 | 62.33 | 62.33
2017-05-02 15:00 | 65.14 | 65.14
2017-05-02 15:30 | 81.36 | 81.35
2017-05-02 16:00 | 89.17 | 89.16
2017-05-02 16:30 | 86.07 | 86.01
2017-05-02 17:00 | 102.85 | 102.77
2017-05-02 17:30 | 117.81 | 117.81
2017-05-02 18:00 | 134.45 | 131.78
2017-05-02 18:30 | 134.79 | 132.19
2017-05-02 19:00 | 131.28 | 131
2017-05-02 19:30 | 127.58 | 127.53
2017-05-02 20:00 | 110.43 | 110.41
2017-05-02 20:30 | 93.25 | 93.2
2017-05-02 21:00 | 85.31 | 84.63
2017-05-02 21:30 | 67.31 | 67.24
2017-05-02 22:00 | 29.96 | 28.3
2017-05-02 22:30 | 53.73 | 51.82
2017-05-02 23:00 | 47.38 | 47.26
2017-05-02 23:30 | 20.61 | 20.27
2017-05-03 | 5.94 | 4.08
2017-05-03 00:30 | 4.89 | -3.06
2017-05-03 01:00 | 11.87 | -11.68
2017-05-03 01:30 | 14.84 | -14.72
2017-05-03 02:00 | 14.93 | -14.84
2017-05-03 02:30 | 13.94 | -13.82
2017-05-03 03:00 | 16.78 | -16.76
2017-05-03 03:30 | 16.56 | -16.53
2017-05-03 04:00 | 15.59 | -15.55
2017-05-03 04:30 | 9.74 | -9.53
2017-05-03 05:00 | 5.29 | -4.58
2017-05-03 05:30 | 11.17 | 10.24
2017-05-03 06:00 | 28.49 | 28.24
2017-05-03 06:30 | 57.56 | 57.55
2017-05-03 07:00 | 67.9 | 67.9
2017-05-03 07:30 | 72.47 | 72.36
2017-05-03 08:00 | 72.57 | 72.43
2017-05-03 08:30 | 68.35 | 68.15
2017-05-03 09:00 | 65.98 | 65.86
2017-05-03 09:30 | 70.56 | 70.51
2017-05-03 10:00 | 67.32 | 67.31
2017-05-03 10:30 | 69.21 | 69.2
2017-05-03 11:00 | 47.25 | 47.24
2017-05-03 11:30 | 45.89 | 45.86
2017-05-03 12:00 | 55.15 | 49.42
2017-05-03 12:30 | 52.68 | 47.87
2017-05-03 13:00 | 58.09 | 54.98
2017-05-03 13:30 | 64.14 | 62.16
2017-05-03 14:00 | 76.32 | 74.59
2017-05-03 14:30 | 82.74 | 81.19
2017-05-03 15:00 | 77.35 | 76.02
2017-05-03 15:30 | 80.07 | 79.03
2017-05-03 16:00 | 85.64 | 84.78
2017-05-03 16:30 | 87.71 | 87.02
2017-05-03 17:00 | 100.68 | 100.23
2017-05-03 17:30 | 127.1 | 126.61
2017-05-03 18:00 | 99.88 | 98.73
2017-05-03 18:30 | 91.01 | 89.95
2017-05-03 19:00 | 88.9 | 88.07
2017-05-03 19:30 | 90.47 | 89.98
2017-05-03 20:00 | 83.63 | 82.4
2017-05-03 20:30 | 81.84 | 79.1
2017-05-03 21:00 | 55.2 | 54.41
2017-05-03 21:30 | 57.72 | 57.66
2017-05-03 22:00 | 40.68 | 40.67
2017-05-03 22:30 | 45.02 | 45.01
2017-05-03 23:00 | 45.18 | 45.15
2017-05-03 23:30 | 27.89 | 27.72
2017-05-04 | 6.59 | 5.27
2017-05-04 00:30 | 6.79 | -5.92
2017-05-04 01:00 | 12.28 | -11.84
2017-05-04 01:30 | 18.87 | -18.77
2017-05-04 02:00 | 25.8 | -25.79
2017-05-04 02:30 | 23.34 | -23.31
2017-05-04 03:00 | 18.7 | -18.51
2017-05-04 03:30 | 20.51 | -20.43
2017-05-04 04:00 | 21.75 | -21.71
2017-05-04 04:30 | 15.63 | -15.25
2017-05-04 05:00 | 10.83 | -8.98
2017-05-04 05:30 | 6.5 | 0.66
2017-05-04 06:00 | 19.31 | 18.62
2017-05-04 06:30 | 39.46 | 39.42
2017-05-04 07:00 | 58.02 | 58.01
2017-05-04 07:30 | 72.12 | 72.11
2017-05-04 08:00 | 74.88 | 74.51
2017-05-04 08:30 | 62.73 | 62.33
2017-05-04 09:00 | 58.83 | 58.49
2017-05-04 09:30 | 59.68 | 59.47
2017-05-04 10:00 | 56.18 | 56.01
2017-05-04 10:30 | 50.69 | 50.54
2017-05-04 11:00 | 60.02 | 59.93
2017-05-04 11:30 | 62.93 | 62.87
2017-05-04 12:00 | 63.92 | 63.85
2017-05-04 12:30 | 63.06 | 62.99
2017-05-04 13:00 | 64.29 | 64.2
2017-05-04 13:30 | 64.78 | 64.66
2017-05-04 14:00 | 60.03 | 59.9
2017-05-04 14:30 | 67.55 | 67.43
2017-05-04 15:00 | 65.08 | 64.92
2017-05-04 15:30 | 64.3 | 64.06
2017-05-04 16:00 | 70.48 | 70.18
2017-05-04 16:30 | 83.89 | 83.56
2017-05-04 17:00 | 89.15 | 88.79
2017-05-04 17:30 | 94.16 | 93.98
2017-05-04 18:00 | 103.35 | 103
2017-05-04 18:30 | 85.79 | 84.11
2017-05-04 19:00 | 99 | 97.78
2017-05-04 19:30 | 99.78 | 98.52
2017-05-04 20:00 | 92.79 | 92.19
2017-05-04 20:30 | 73.43 | 73.43
2017-05-04 21:00 | 44.7 | 44.58
2017-05-04 21:30 | 41.63 | 41.63
2017-05-04 22:00 | 22.19 | 22.1
2017-05-04 22:30 | 29.2 | 29.09
2017-05-04 23:00 | 46.67 | 46.47
2017-05-04 23:30 | 29.59 | 29.05
2017-05-05 | 8.43 | 6.21
2017-05-05 00:30 | 5.63 | -1.3
2017-05-05 01:00 | 14.85 | -4.06
2017-05-05 01:30 | 20.44 | -4.27
2017-05-05 02:00 | 21.18 | -8.89
2017-05-05 02:30 | 21.64 | -8.04
2017-05-05 03:00 | 22.92 | -12.48
2017-05-05 03:30 | 21.98 | -10.77
2017-05-05 04:00 | 21.82 | -10.32
2017-05-05 04:30 | 21.59 | -8.48
2017-05-05 05:00 | 21.53 | -1.65
2017-05-05 05:30 | 25.56 | 7.83
2017-05-05 06:00 | 37.39 | 28.17
2017-05-05 06:30 | 46.25 | 45.56
2017-05-05 07:00 | 74.19 | 73.98
2017-05-05 07:30 | 79.51 | 79.33
2017-05-05 08:00 | 71.29 | 70.54
2017-05-05 08:30 | 67.66 | 65.56
2017-05-05 09:00 | 64.02 | 61.52
2017-05-05 09:30 | 59.84 | 56.5
2017-05-05 10:00 | 58.42 | 55
2017-05-05 10:30 | 55.86 | 51.96
2017-05-05 11:00 | 54.86 | 51.06
2017-05-05 11:30 | 53.96 | 50.41
2017-05-05 12:00 | 56.21 | 53.13
2017-05-05 12:30 | 56.08 | 53.21
2017-05-05 13:00 | 56.67 | 53.86
2017-05-05 13:30 | 50.25 | 47.16
2017-05-05 14:00 | 66.57 | 64.26
2017-05-05 14:30 | 67.86 | 65.95
2017-05-05 15:00 | 64.35 | 62.56
2017-05-05 15:30 | 62.72 | 61.15
2017-05-05 16:00 | 66.66 | 65.9
2017-05-05 16:30 | 72.8 | 72.23
2017-05-05 17:00 | 81.06 | 80.23
2017-05-05 17:30 | 80.76 | 79.8
2017-05-05 18:00 | 81.18 | 80.98
2017-05-05 18:30 | 76.56 | 76.37
2017-05-05 19:00 | 86.83 | 86.73
2017-05-05 19:30 | 86.95 | 86.91
2017-05-05 20:00 | 77.09 | 77.06
2017-05-05 20:30 | 68.04 | 68.02
2017-05-05 21:00 | 53.58 | 53.5
2017-05-05 21:30 | 42.59 | 42.38
2017-05-05 22:00 | 21.79 | 21.6
2017-05-05 22:30 | 52.32 | 52.26
2017-05-05 23:00 | 81.11 | 81.05
2017-05-05 23:30 | 48.59 | 48.41
2017-05-06 | 21.75 | 21.34
2017-05-06 00:30 | 7.33 | 6.79
2017-05-06 01:00 | 5.56 | -5.39
2017-05-06 01:30 | 9.74 | -9.64
2017-05-06 02:00 | 10.59 | -9.99
2017-05-06 02:30 | 12.48 | -8.22
2017-05-06 03:00 | 10.59 | -8.44
2017-05-06 03:30 | 8.61 | -4.91
2017-05-06 04:00 | 9.14 | -5.3
2017-05-06 04:30 | 10.01 | -3.75
2017-05-06 05:00 | 10.37 | -1.5
2017-05-06 05:30 | 10.07 | -1.63
2017-05-06 06:00 | 11.54 | 3.21
2017-05-06 06:30 | 12.71 | 4.96
2017-05-06 07:00 | 26.08 | 21.73
2017-05-06 07:30 | 30.08 | 25.77
2017-05-06 08:00 | 26.17 | 22.19
2017-05-06 08:30 | 35.57 | 35.13
2017-05-06 09:00 | 60.38 | 60.2
2017-05-06 09:30 | 56.75 | 56.44
2017-05-06 10:00 | 40.69 | 39.99
2017-05-06 10:30 | 34.96 | 34.06
2017-05-06 11:00 | 34.28 | 33.17
2017-05-06 11:30 | 32.62 | 31.41
2017-05-06 12:00 | 29.5 | 28.28
2017-05-06 12:30 | 26.51 | 25.34
2017-05-06 13:00 | 24.12 | 22.91
2017-05-06 13:30 | 25.16 | 23.99
2017-05-06 14:00 | 30.39 | 29.52
2017-05-06 14:30 | 34.41 | 33.59
2017-05-06 15:00 | 37.62 | 36.99
2017-05-06 15:30 | 40.74 | 40.22
2017-05-06 16:00 | 57.79 | 57.43
2017-05-06 16:30 | 58.24 | 58.23
2017-05-06 17:00 | 67.95 | 67.87
2017-05-06 17:30 | 62.27 | 62.26
2017-05-06 18:00 | 46.02 | 45.86
2017-05-06 18:30 | 84.44 | 84.42
2017-05-06 19:00 | 123.36 | 123.36
2017-05-06 19:30 | 108.39 | 108.27
2017-05-06 20:00 | 97.01 | 96.79
2017-05-06 20:30 | 93.86 | 93.37
2017-05-06 21:00 | 85.66 | 84.81
2017-05-06 21:30 | 46.57 | 46.52
2017-05-06 22:00 | 54.99 | 54.92
2017-05-06 22:30 | 63.22 | 63.1
2017-05-06 23:00 | 88.83 | 88.68
2017-05-06 23:30 | 62.48 | 62.1
2017-05-07 | 34.25 | 33.5
2017-05-07 00:30 | 17.17 | 15.02
2017-05-07 01:00 | 9.19 | -2.11
2017-05-07 01:30 | 9.67 | -5.68
2017-05-07 02:00 | 8.96 | -4.73
2017-05-07 02:30 | 9.82 | -7.68
2017-05-07 03:00 | 10.3 | -8.19
2017-05-07 03:30 | 9.62 | -7.26
2017-05-07 04:00 | 9.31 | -6.61
2017-05-07 04:30 | 9.64 | -6.09
2017-05-07 05:00 | 9.82 | -6.15
2017-05-07 05:30 | 9.68 | -4.73
2017-05-07 06:00 | 10.6 | -4.85
2017-05-07 06:30 | 9.96 | -3.23
2017-05-07 07:00 | 9.72 | -1.28
2017-05-07 07:30 | 13 | 4.11
2017-05-07 08:00 | 33.51 | 30.47
2017-05-07 08:30 | 33.93 | 31.97
2017-05-07 09:00 | 32.04 | 31.96
2017-05-07 09:30 | 32.4 | 32.23
2017-05-07 10:00 | 31.24 | 30.82
2017-05-07 10:30 | 28.38 | 27.72
2017-05-07 11:00 | 26.54 | 25.77
2017-05-07 11:30 | 22 | 20.96
2017-05-07 12:00 | 20.24 | 19.09
2017-05-07 12:30 | 19.46 | 18.36
2017-05-07 13:00 | 21.27 | 20.3
2017-05-07 13:30 | 22.51 | 21.58
2017-05-07 14:00 | 27.47 | 26.68
2017-05-07 14:30 | 35.16 | 34.61
2017-05-07 15:00 | 45.96 | 45.67
2017-05-07 15:30 | 54.4 | 54.19
2017-05-07 16:00 | 65.87 | 65.72
2017-05-07 16:30 | 67.75 | 67.67
2017-05-07 17:00 | 80.55 | 80.55
2017-05-07 17:30 | 132.54 | 132.53
2017-05-07 18:00 | 146.07 | 146.04
2017-05-07 18:30 | 133.65 | 133.62
2017-05-07 19:00 | 132.6 | 132.6
2017-05-07 19:30 | 115.89 | 115.89
2017-05-07 20:00 | 107.11 | 107.05
2017-05-07 20:30 | 85.3 | 85.27
2017-05-07 21:00 | 78.29 | 78.28
2017-05-07 21:30 | 65.07 | 65.07
2017-05-07 22:00 | 33.59 | 33.53
2017-05-07 22:30 | 59.41 | 59.29
2017-05-07 23:00 | 86.97 | 86.79
2017-05-07 23:30 | 60.01 | 59.58
2017-05-08 | 27.18 | 26.51
2017-05-08 00:30 | 17.88 | 12.86
2017-05-08 01:00 | 14.73 | 0.35
2017-05-08 01:30 | 14.19 | -6.05
2017-05-08 02:00 | 14.49 | -6.25
2017-05-08 02:30 | 11.84 | -5.24
2017-05-08 03:00 | 10.09 | -5.71
2017-05-08 03:30 | 9.99 | -5.27
2017-05-08 04:00 | 9.76 | -4.14
2017-05-08 04:30 | 10.53 | -3.11
2017-05-08 05:00 | 11.93 | -1.92
2017-05-08 05:30 | 18.05 | 9.84
2017-05-08 06:00 | 27.09 | 22.52
2017-05-08 06:30 | 37.46 | 36.12
2017-05-08 07:00 | 52.06 | 52.06
2017-05-08 07:30 | 66.85 | 66.32
2017-05-08 08:00 | 86.91 | 86.08
2017-05-08 08:30 | 68.72 | 67.38
2017-05-08 09:00 | 73.63 | 72.17
2017-05-08 09:30 | 62.04 | 61.81
2017-05-08 10:00 | 62.34 | 62.21
2017-05-08 10:30 | 52.7 | 52.44
2017-05-08 11:00 | 54.82 | 54.2
2017-05-08 11:30 | 66.21 | 65.7
2017-05-08 12:00 | 56.42 | 55.96
2017-05-08 12:30 | 57.07 | 56.67
2017-05-08 13:00 | 60.02 | 59.75
2017-05-08 13:30 | 55.69 | 55.68
2017-05-08 14:00 | 53.47 | 53.36
2017-05-08 14:30 | 59.03 | 58.91
2017-05-08 15:00 | 85.38 | 85.25
2017-05-08 15:30 | 91.4 | 91.24
2017-05-08 16:00 | 103.08 | 102.93
2017-05-08 16:30 | 114.81 | 114.68
2017-05-08 17:00 | 138.59 | 138.55
2017-05-08 17:30 | 142.82 | 141.85
2017-05-08 18:00 | 152.6 | 150.26
2017-05-08 18:30 | 139.85 | 139.71
2017-05-08 19:00 | 138.85 | 138.78
2017-05-08 19:30 | 123.56 | 123.26
2017-05-08 20:00 | 109.5 | 109.48
2017-05-08 20:30 | 91.66 | 91.52
2017-05-08 21:00 | 69.11 | 68.64
2017-05-08 21:30 | 44.07 | 43.93
2017-05-08 22:00 | 45.03 | 44.61
2017-05-08 22:30 | 74.75 | 74.38
2017-05-08 23:00 | 91.02 | 90.6
2017-05-08 23:30 | 68.29 | 67.59
2017-05-09 | 25.22 | 23.17
2017-05-09 00:30 | 10.18 | 6.35
2017-05-09 01:00 | 7.65 | -3.7
2017-05-09 01:30 | 15.79 | -8.77
2017-05-09 02:00 | 20.5 | -7.28
2017-05-09 02:30 | 21.64 | -10.55
2017-05-09 03:00 | 22.19 | -11.94
2017-05-09 03:30 | 21.85 | -11.3
2017-05-09 04:00 | 21.39 | -7.88
2017-05-09 04:30 | 21.87 | -2.4
2017-05-09 05:00 | 22.59 | -0.2
2017-05-09 05:30 | 25.5 | 6.66
2017-05-09 06:00 | 33.8 | 23.99
2017-05-09 06:30 | 54.31 | 51.31
2017-05-09 07:00 | 68.88 | 68.49
2017-05-09 07:30 | 91.43 | 91.35
2017-05-09 08:00 | 59.23 | 59.23
2017-05-09 08:30 | 47.8 | 47.78
2017-05-09 09:00 | 48.59 | 48.4
2017-05-09 09:30 | 56.25 | 56.15
2017-05-09 10:00 | 46.25 | 46.15
2017-05-09 10:30 | 34.51 | 33.67
2017-05-09 11:00 | 31.21 | 30.31
2017-05-09 11:30 | 19.63 | 18.79
2017-05-09 12:00 | 19.74 | 18.93
2017-05-09 12:30 | 35.58 | 35.17
2017-05-09 13:00 | 39.43 | 39.17
2017-05-09 13:30 | 33.97 | 33.62
2017-05-09 14:00 | 29.51 | 29.12
2017-05-09 14:30 | 33.06 | 32.8
2017-05-09 15:00 | 34.26 | 33.99
2017-05-09 15:30 | 61.42 | 61.35
2017-05-09 16:00 | 92.3 | 92.28
2017-05-09 16:30 | 117.42 | 117.42
2017-05-09 17:00 | 140.44 | 140.42
2017-05-09 17:30 | 140.92 | 140.81
2017-05-09 18:00 | 138.1 | 137.27
2017-05-09 18:30 | 144.69 | 144.06
2017-05-09 19:00 | 148.82 | 147.68
2017-05-09 19:30 | 139.69 | 138.12
2017-05-09 20:00 | 127.98 | 126.69
2017-05-09 20:30 | 117.48 | 117.42
2017-05-09 21:00 | 103.96 | 103.71
2017-05-09 21:30 | 101.07 | 100.7
2017-05-09 22:00 | 75.21 | 74.39
2017-05-09 22:30 | 86 | 85.36
2017-05-09 23:00 | 101.93 | 101.22
2017-05-09 23:30 | 84.49 | 83.76
2017-05-10 | 48.08 | 46.96
2017-05-10 00:30 | 28.25 | 27.05
2017-05-10 01:00 | 7.35 | 1.13
2017-05-10 01:30 | 7.06 | -4.58
2017-05-10 02:00 | 8.37 | -7.24
2017-05-10 02:30 | 8.7 | -8.01
2017-05-10 03:00 | 8.18 | -7.61
2017-05-10 03:30 | 6.22 | -5.56
2017-05-10 04:00 | 4.58 | -2.24
2017-05-10 04:30 | 5.44 | 0.61
2017-05-10 05:00 | 7.42 | 2.14
2017-05-10 05:30 | 16.09 | 11.48
2017-05-10 06:00 | 27.57 | 24.66
2017-05-10 06:30 | 41.83 | 40.94
2017-05-10 07:00 | 70.22 | 70.08
2017-05-10 07:30 | 111.46 | 111.46
2017-05-10 08:00 | 115.91 | 115.72
2017-05-10 08:30 | 110.16 | 109.88
2017-05-10 09:00 | 123.17 | 122.65
2017-05-10 09:30 | 134.82 | 128.19
2017-05-10 10:00 | 146.46 | 138.16
2017-05-10 10:30 | 148.64 | 136.51
2017-05-10 11:00 | 148.76 | 136.44
2017-05-10 11:30 | 141.32 | 128.57
2017-05-10 12:00 | 137.36 | 124.44
2017-05-10 12:30 | 136.88 | 125.09
2017-05-10 13:00 | 131.47 | 118.94
2017-05-10 13:30 | 129.58 | 116.22
2017-05-10 14:00 | 129.31 | 115.91
2017-05-10 14:30 | 119.38 | 104.87
2017-05-10 15:00 | 126.58 | 113.55
2017-05-10 15:30 | 115.89 | 101.9
2017-05-10 16:00 | 118.57 | 105.04
2017-05-10 16:30 | 129.51 | 117.32
2017-05-10 17:00 | 151.03 | 140.27
2017-05-10 17:30 | 152.86 | 144.39
2017-05-10 18:00 | 150.56 | 143.27
2017-05-10 18:30 | 145.07 | 137.35
2017-05-10 19:00 | 147.28 | 140.04
2017-05-10 19:30 | 132.47 | 126.86
2017-05-10 20:00 | 122.56 | 118.44
2017-05-10 20:30 | 121.65 | 116.52
2017-05-10 21:00 | 99.06 | 93.46
2017-05-10 21:30 | 85.98 | 80.46
2017-05-10 22:00 | 60.33 | 53.62
2017-05-10 22:30 | 69.11 | 63.4
2017-05-10 23:00 | 96.88 | 93.44
2017-05-10 23:30 | 67.93 | 63.87
2017-05-11 | 38.56 | 30.83
2017-05-11 00:30 | 26.93 | 10.04
2017-05-11 01:00 | 5.38 | -2.93
2017-05-11 01:30 | 10.55 | -10.26
2017-05-11 02:00 | 11.4 | -11.1
2017-05-11 02:30 | 9.21 | -8.73
2017-05-11 03:00 | 8.21 | -7.58
2017-05-11 03:30 | 6.2 | -5.22
2017-05-11 04:00 | 5.04 | -2.3
2017-05-11 04:30 | 6.13 | 0.26
2017-05-11 05:00 | 6.32 | 1.74
2017-05-11 05:30 | 10.64 | 8.65
2017-05-11 06:00 | 25.61 | 25.1
2017-05-11 06:30 | 55.41 | 55.35
2017-05-11 07:00 | 89.68 | 85.01
2017-05-11 07:30 | 110.52 | 105.74
2017-05-11 08:00 | 81.6 | 74.15
2017-05-11 08:30 | 62.97 | 51.52
2017-05-11 09:00 | 68.89 | 57.43
2017-05-11 09:30 | 52.65 | 34.99
2017-05-11 10:00 | 51.28 | 31.63
2017-05-11 10:30 | 53.22 | 36.85
2017-05-11 11:00 | 55.97 | 41.08
2017-05-11 11:30 | 42.51 | 18.14
2017-05-11 12:00 | 38.43 | 5.36
2017-05-11 12:30 | 38.61 | 6.53
2017-05-11 13:00 | 42 | 18.08
2017-05-11 13:30 | 49.23 | 31.41
2017-05-11 14:00 | 42.03 | 16.7
2017-05-11 14:30 | 43.85 | 15.04
2017-05-11 15:00 | 43.96 | 17.13
2017-05-11 15:30 | 45.63 | 22.98
2017-05-11 16:00 | 51.03 | 33.87
2017-05-11 16:30 | 54.54 | 39.74
2017-05-11 17:00 | 89.77 | 82.26
2017-05-11 17:30 | 90.36 | 83
2017-05-11 18:00 | 94.33 | 90.57
2017-05-11 18:30 | 102.69 | 99.04
2017-05-11 19:00 | 106.14 | 102.9
2017-05-11 19:30 | 94.96 | 92
2017-05-11 20:00 | 95.64 | 89.36
2017-05-11 20:30 | 86.25 | 79.18
2017-05-11 21:00 | 62 | 59.46
2017-05-11 21:30 | 32.74 | 29.38
2017-05-11 22:00 | 23.32 | 19.78
2017-05-11 22:30 | 40.76 | 39.53
2017-05-11 23:00 | 65.64 | 65.14
2017-05-11 23:30 | 40.23 | 39.44
2017-05-12 | 23.56 | 21.09
2017-05-12 00:30 | 13.87 | 5.85
2017-05-12 01:00 | 14.25 | -3.7
2017-05-12 01:30 | 17.65 | -9.99
2017-05-12 02:00 | 19.61 | -12.18
2017-05-12 02:30 | 18.39 | -10.46
2017-05-12 03:00 | 16.78 | -7.79
2017-05-12 03:30 | 13.54 | -4.34
2017-05-12 04:00 | 12.46 | -2.74
2017-05-12 04:30 | 12.4 | -2.2
2017-05-12 05:00 | 12.58 | -2.65
2017-05-12 05:30 | 11.35 | 1.81
2017-05-12 06:00 | 25.93 | 23.53
2017-05-12 06:30 | 67.42 | 62.01
2017-05-12 07:00 | 106.83 | 102.84
2017-05-12 07:30 | 127.55 | 123.45
2017-05-12 08:00 | 110.71 | 105.53
2017-05-12 08:30 | 107.17 | 101.1
2017-05-12 09:00 | 102.41 | 95.24
2017-05-12 09:30 | 87.04 | 78.01
2017-05-12 10:00 | 70.87 | 59.04
2017-05-12 10:30 | 48.39 | 37.08
2017-05-12 11:00 | 49.54 | 42.69
2017-05-12 11:30 | 61.74 | 56.14
2017-05-12 12:00 | 72.28 | 67.57
2017-05-12 12:30 | 70.34 | 66.07
2017-05-12 13:00 | 59.42 | 54.3
2017-05-12 13:30 | 54.67 | 48.67
2017-05-12 14:00 | 54.62 | 48.59
2017-05-12 14:30 | 58.19 | 52.75
2017-05-12 15:00 | 67.5 | 63.46
2017-05-12 15:30 | 76.48 | 73.01
2017-05-12 16:00 | 77.05 | 73.44
2017-05-12 16:30 | 82.18 | 79
2017-05-12 17:00 | 107.41 | 104.96
2017-05-12 17:30 | 118.49 | 96.45
2017-05-12 18:00 | 124.88 | 100.43
2017-05-12 18:30 | 125.63 | 109.96
2017-05-12 19:00 | 129.12 | 116.24
2017-05-12 19:30 | 123.52 | 110.69
2017-05-12 20:00 | 124.22 | 112.01
2017-05-12 20:30 | 120.56 | 108.79
2017-05-12 21:00 | 100.13 | 93.89
2017-05-12 21:30 | 70.79 | 69.65
2017-05-12 22:00 | 58.31 | 56.74
2017-05-12 22:30 | 70.44 | 69.24
2017-05-12 23:00 | 95.46 | 94.76
2017-05-12 23:30 | 75.42 | 74.69
2017-05-13 | 45.2 | 43.74
2017-05-13 00:30 | 24.87 | 21
2017-05-13 01:00 | 18.64 | 14.44
2017-05-13 01:30 | 4.99 | -1.58
2017-05-13 02:00 | 9.51 | -8.58
2017-05-13 02:30 | 12.43 | -11.88
2017-05-13 03:00 | 11.52 | -10.98
2017-05-13 03:30 | 9.68 | -8.76
2017-05-13 04:00 | 8.93 | -7.83
2017-05-13 04:30 | 8.02 | -6.3
2017-05-13 05:00 | 6.03 | -2.79
2017-05-13 05:30 | 6.2 | -2.59
2017-05-13 06:00 | 5.52 | 0.61
2017-05-13 06:30 | 7.31 | 5.43
2017-05-13 07:00 | 12.66 | 11.78
2017-05-13 07:30 | 33.25 | 32.89
2017-05-13 08:00 | 31.98 | 31.84
2017-05-13 08:30 | 53.69 | 50.8
2017-05-13 09:00 | 52.3 | 48.63
2017-05-13 09:30 | 38.7 | 32.48
2017-05-13 10:00 | 37.17 | 29.18
2017-05-13 10:30 | 38.31 | 30.09
2017-05-13 11:00 | 41.24 | 34.71
2017-05-13 11:30 | 53.33 | 48.54
2017-05-13 12:00 | 57.71 | 53.64
2017-05-13 12:30 | 53.87 | 49.64
2017-05-13 13:00 | 51.08 | 46.8
2017-05-13 13:30 | 59.92 | 56.33
2017-05-13 14:00 | 64.57 | 61.52
2017-05-13 14:30 | 56.62 | 53.12
2017-05-13 15:00 | 37.01 | 35.1
2017-05-13 15:30 | 39.88 | 39.83
2017-05-13 16:00 | 52.08 | 52.06
2017-05-13 16:30 | 61.11 | 61.1
2017-05-13 17:00 | 67.68 | 67.62
2017-05-13 17:30 | 93.34 | 93.28
2017-05-13 18:00 | 106.94 | 106.83
2017-05-13 18:30 | 119.41 | 119.33
2017-05-13 19:00 | 123.7 | 123.67
2017-05-13 19:30 | 108.51 | 108.51
2017-05-13 20:00 | 103.46 | 103.42
2017-05-13 20:30 | 107.47 | 107.45
2017-05-13 21:00 | 81.01 | 81
2017-05-13 21:30 | 65.16 | 65.14
2017-05-13 22:00 | 44.86 | 44.78
2017-05-13 22:30 | 70 | 69.9
2017-05-13 23:00 | 73.3 | 73.09
2017-05-13 23:30 | 47.34 | 46.54
2017-05-14 | 25.19 | 23.12
2017-05-14 00:30 | 7.17 | 5.32
2017-05-14 01:00 | 4.48 | -3.52
2017-05-14 01:30 | 7.85 | -7.59
2017-05-14 02:00 | 8.9 | -8.14
2017-05-14 02:30 | 7.83 | -7.18
2017-05-14 03:00 | 8.07 | -7.58
2017-05-14 03:30 | 7.99 | -7.56
2017-05-14 04:00 | 6.54 | -5.81
2017-05-14 04:30 | 4.79 | -3.39
2017-05-14 05:00 | 6.95 | -3.3
2017-05-14 05:30 | 7.37 | -2.05
2017-05-14 06:00 | 8.25 | -1.05
2017-05-14 06:30 | 8.71 | -0.92
2017-05-14 07:00 | 8.75 | 1.65
2017-05-14 07:30 | 13.13 | 6.78
2017-05-14 08:00 | 18.8 | 13.38
2017-05-14 08:30 | 28.99 | 25.49
2017-05-14 09:00 | 38.12 | 36.3
2017-05-14 09:30 | 44.46 | 43.14
2017-05-14 10:00 | 38.4 | 38.22
2017-05-14 10:30 | 45.6 | 45.24
2017-05-14 11:00 | 47.61 | 47.5
2017-05-14 11:30 | 39.37 | 39.31
2017-05-14 12:00 | 41.76 | 41.72
2017-05-14 12:30 | 37.18 | 37.13
2017-05-14 13:00 | 30.57 | 30.42
2017-05-14 13:30 | 31.97 | 31.87
2017-05-14 14:00 | 32.22 | 32.07
2017-05-14 14:30 | 20.03 | 19.56
2017-05-14 15:00 | 31.63 | 31.45
2017-05-14 15:30 | 53 | 52.96
2017-05-14 16:00 | 68.44 | 68.43
2017-05-14 16:30 | 85.7 | 85.66
2017-05-14 17:00 | 109.74 | 109.61
2017-05-14 17:30 | 118.26 | 117.91
2017-05-14 18:00 | 119.31 | 118.74
2017-05-14 18:30 | 130.3 | 129.5
2017-05-14 19:00 | 135.43 | 134.68
2017-05-14 19:30 | 122.21 | 121.57
2017-05-14 20:00 | 125.11 | 124.72
2017-05-14 20:30 | 114.96 | 114.56
2017-05-14 21:00 | 90.81 | 90.1
2017-05-14 21:30 | 86.93 | 86.02
2017-05-14 22:00 | 62.3 | 60.76
2017-05-14 22:30 | 80.68 | 79.68
2017-05-14 23:00 | 82.3 | 81.12
2017-05-14 23:30 | 62.63 | 61.33
2017-05-15 | 35.49 | 33.4
2017-05-15 00:30 | 14.32 | 10.53
2017-05-15 01:00 | 7.36 | -0.26
2017-05-15 01:30 | 7.06 | -4.4
2017-05-15 02:00 | 7.22 | -4.97
2017-05-15 02:30 | 6.79 | -4.42
2017-05-15 03:00 | 6.36 | -3.83
2017-05-15 03:30 | 6.26 | -3.27
2017-05-15 04:00 | 6.18 | -0.5
2017-05-15 04:30 | 7.16 | 0.58
2017-05-15 05:00 | 8.58 | 1.39
2017-05-15 05:30 | 11.52 | 3.49
2017-05-15 06:00 | 30.09 | 26.89
2017-05-15 06:30 | 50.14 | 48.64
2017-05-15 07:00 | 76.26 | 75.51
2017-05-15 07:30 | 118.26 | 118.13
2017-05-15 08:00 | 95.49 | 95.42
2017-05-15 08:30 | 81.7 | 81.62
2017-05-15 09:00 | 83.27 | 83.27
2017-05-15 09:30 | 78.07 | 78.07
2017-05-15 10:00 | 62.71 | 62.7
2017-05-15 10:30 | 54.07 | 54.01
2017-05-15 11:00 | 42.13 | 41.91
2017-05-15 11:30 | 39.32 | 37.44
2017-05-15 12:00 | 36.77 | 34.51
2017-05-15 12:30 | 40.27 | 38.44
2017-05-15 13:00 | 42.45 | 40.77
2017-05-15 13:30 | 51.08 | 49.91
2017-05-15 14:00 | 62.8 | 61.86
2017-05-15 14:30 | 69.95 | 69.11
2017-05-15 15:00 | 70.39 | 69.64
2017-05-15 15:30 | 90.88 | 90.38
2017-05-15 16:00 | 99.45 | 99.07
2017-05-15 16:30 | 106.14 | 106.09
2017-05-15 17:00 | 111.24 | 111.08
2017-05-15 17:30 | 133.03 | 132.63
2017-05-15 18:00 | 136.16 | 135.42
2017-05-15 18:30 | 134.99 | 134.41
2017-05-15 19:00 | 142.33 | 141.95
2017-05-15 19:30 | 146.21 | 145.94
2017-05-15 20:00 | 136.2 | 136.17
2017-05-15 20:30 | 106.48 | 106.48
2017-05-15 21:00 | 98.1 | 98.07
2017-05-15 21:30 | 87.04 | 87.03
2017-05-15 22:00 | 76.26 | 76.24
2017-05-15 22:30 | 72.54 | 72.52
2017-05-15 23:00 | 96.98 | 96.93
2017-05-15 23:30 | 77.76 | 77.62
2017-05-16 | 55.59 | 53.84
2017-05-16 00:30 | 28.97 | 24.21
2017-05-16 01:00 | 14.02 | 2.11
2017-05-16 01:30 | 13.28 | -5.87
2017-05-16 02:00 | 11.32 | -9.18
2017-05-16 02:30 | 10.55 | -8.01
2017-05-16 03:00 | 10.09 | -7.84
2017-05-16 03:30 | 9.01 | -6.27
2017-05-16 04:00 | 7.86 | -3.29
2017-05-16 04:30 | 8.93 | -2.04
2017-05-16 05:00 | 10.22 | -1.42
2017-05-16 05:30 | 15.59 | 7.95
2017-05-16 06:00 | 48.57 | 46.01
2017-05-16 06:30 | 70.1 | 69.07
2017-05-16 07:00 | 81.39 | 80.96
2017-05-16 07:30 | 93.22 | 93.06
2017-05-16 08:00 | 72.46 | 72.46
2017-05-16 08:30 | 71.02 | 71.01
2017-05-16 09:00 | 56.53 | 56.53
2017-05-16 09:30 | 21.37 | 20.79
2017-05-16 10:00 | 23.67 | 19.9
2017-05-16 10:30 | 25.23 | 22.23
2017-05-16 11:00 | 13.6 | 6.08
2017-05-16 11:30 | 19.15 | 14.76
2017-05-16 12:00 | 24.09 | 20.7
2017-05-16 12:30 | 17.28 | 11.28
2017-05-16 13:00 | 21.44 | 17.11
2017-05-16 13:30 | 32.89 | 30.27
2017-05-16 14:00 | 41.77 | 39.93
2017-05-16 14:30 | 41.89 | 40.19
2017-05-16 15:00 | 61.08 | 60.04
2017-05-16 15:30 | 71.59 | 70.83
2017-05-16 16:00 | 85.27 | 84.68
2017-05-16 16:30 | 87.17 | 86.76
2017-05-16 17:00 | 109.96 | 109.78
2017-05-16 17:30 | 113.24 | 112.99
2017-05-16 18:00 | 123.21 | 122.64
2017-05-16 18:30 | 126.57 | 126.08
2017-05-16 19:00 | 123.39 | 123.1
2017-05-16 19:30 | 113.56 | 113.31
2017-05-16 20:00 | 111.61 | 111.55
2017-05-16 20:30 | 95.73 | 95.7
2017-05-16 21:00 | 97.88 | 97.87
2017-05-16 21:30 | 101.32 | 101.31
2017-05-16 22:00 | 92.95 | 92.83
2017-05-16 22:30 | 91.32 | 91.2
2017-05-16 23:00 | 107.2 | 107.02
2017-05-16 23:30 | 84.05 | 83.69
2017-05-17 | 62.95 | 62.57
2017-05-17 00:30 | 34 | 31.63
2017-05-17 01:00 | 16.17 | 7.75
2017-05-17 01:30 | 12.38 | -0.37
2017-05-17 02:00 | 8.61 | -2.9
2017-05-17 02:30 | 9.85 | -5.03
2017-05-17 03:00 | 9.8 | -6.4
2017-05-17 03:30 | 8.7 | -4.43
2017-05-17 04:00 | 8.45 | -0.96
2017-05-17 04:30 | 10.4 | 1.25
2017-05-17 05:00 | 11.65 | 1.82
2017-05-17 05:30 | 15.01 | 5.24
2017-05-17 06:00 | 21.56 | 20.39
2017-05-17 06:30 | 48.91 | 47.14
2017-05-17 07:00 | 98.43 | 97.54
2017-05-17 07:30 | 132.08 | 130.97
2017-05-17 08:00 | 115.44 | 114.04
2017-05-17 08:30 | 79.58 | 76.7
2017-05-17 09:00 | 79.06 | 68.18
2017-05-17 09:30 | 69.4 | 56.44
2017-05-17 10:00 | 54.57 | 35.21
2017-05-17 10:30 | 54.82 | 35.78
2017-05-17 11:00 | 70.61 | 58.29
2017-05-17 11:30 | 68.31 | 55.42
2017-05-17 12:00 | 65.4 | 52.03
2017-05-17 12:30 | 69.53 | 54.9
2017-05-17 13:00 | 77.88 | 64.99
2017-05-17 13:30 | 79.36 | 66.88
2017-05-17 14:00 | 70.69 | 55.94
2017-05-17 14:30 | 72.64 | 58.58
2017-05-17 15:00 | 75.14 | 61.89
2017-05-17 15:30 | 92.06 | 81.76
2017-05-17 16:00 | 100.21 | 91.52
2017-05-17 16:30 | 119.08 | 112.32
2017-05-17 17:00 | 130.27 | 126.82
2017-05-17 17:30 | 143.03 | 140.25
2017-05-17 18:00 | 131.45 | 128.54
2017-05-17 18:30 | 131.23 | 128.53
2017-05-17 19:00 | 127.93 | 127.51
2017-05-17 19:30 | 116 | 115.78
2017-05-17 20:00 | 111.98 | 111.78
2017-05-17 20:30 | 98.13 | 97.18
2017-05-17 21:00 | 99.96 | 95.11
2017-05-17 21:30 | 101.82 | 98.01
2017-05-17 22:00 | 73.56 | 69
2017-05-17 22:30 | 78.87 | 74.42
2017-05-17 23:00 | 107.77 | 104.89
2017-05-17 23:30 | 82.67 | 79.33
2017-05-18 | 55.54 | 52.87
2017-05-18 00:30 | 23.27 | 22.05
2017-05-18 01:00 | 9.52 | 3.56
2017-05-18 01:30 | 10.96 | -3.62
2017-05-18 02:00 | 15.65 | -10.46
2017-05-18 02:30 | 15.4 | -9.63
2017-05-18 03:00 | 14.46 | -8.42
2017-05-18 03:30 | 13.07 | -6.71
2017-05-18 04:00 | 11.01 | -3.93
2017-05-18 04:30 | 8.36 | -0.34
2017-05-18 05:00 | 8.03 | 0.56
2017-05-18 05:30 | 9.69 | 5.75
2017-05-18 06:00 | 19.86 | 17.87
2017-05-18 06:30 | 45.3 | 43.82
2017-05-18 07:00 | 49.93 | 47.92
2017-05-18 07:30 | 70.2 | 64.32
2017-05-18 08:00 | 98.24 | 95.76
2017-05-18 08:30 | 105.78 | 103.13
2017-05-18 09:00 | 92.24 | 88.8
2017-05-18 09:30 | 74.45 | 70.03
2017-05-18 10:00 | 73.47 | 68.78
2017-05-18 10:30 | 70.64 | 65.2
2017-05-18 11:00 | 71.74 | 66.22
2017-05-18 11:30 | 68.74 | 62.95
2017-05-18 12:00 | 69.2 | 63.5
2017-05-18 12:30 | 64.19 | 61.06
2017-05-18 13:00 | 60.74 | 60.59
2017-05-18 13:30 | 63.93 | 63.92
2017-05-18 14:00 | 65.3 | 65.23
2017-05-18 14:30 | 67.78 | 67.57
2017-05-18 15:00 | 66.81 | 66.75
2017-05-18 15:30 | 68.12 | 68.08
2017-05-18 16:00 | 70.48 | 70.45
2017-05-18 16:30 | 72.12 | 72.09
2017-05-18 17:00 | 75.55 | 75.48
2017-05-18 17:30 | 106.24 | 105.93
2017-05-18 18:00 | 144.15 | 143.82
2017-05-18 18:30 | 135.2 | 134.98
2017-05-18 19:00 | 143.31 | 143.11
2017-05-18 19:30 | 133.63 | 133.45
2017-05-18 20:00 | 119.32 | 119.25
2017-05-18 20:30 | 119.97 | 119.95
2017-05-18 21:00 | 119.46 | 119.44
2017-05-18 21:30 | 118.91 | 118.86
2017-05-18 22:00 | 91.67 | 91.52
2017-05-18 22:30 | 103.15 | 103.03
2017-05-18 23:00 | 110.38 | 110.19
2017-05-18 23:30 | 75.11 | 74.68
2017-05-19 | 49.21 | 48.52
2017-05-19 00:30 | 33.26 | 32.63
2017-05-19 01:00 | 8.13 | 6.72
2017-05-19 01:30 | 4.33 | -1.35
2017-05-19 02:00 | 6.7 | -5.48
2017-05-19 02:30 | 8.98 | -6.62
2017-05-19 03:00 | 9.6 | -7.88
2017-05-19 03:30 | 8.17 | -4.54
2017-05-19 04:00 | 7.79 | -2.51
2017-05-19 04:30 | 8.07 | -0.61
2017-05-19 05:00 | 8.17 | 1.34
2017-05-19 05:30 | 17.61 | 15.38
2017-05-19 06:00 | 35.56 | 35.05
2017-05-19 06:30 | 52.55 | 52.54
2017-05-19 07:00 | 52.42 | 52.42
2017-05-19 07:30 | 74.52 | 67.86
2017-05-19 08:00 | 89.97 | 82.23
2017-05-19 08:30 | 91.09 | 82.03
2017-05-19 09:00 | 92.46 | 82.43
2017-05-19 09:30 | 83.01 | 71.5
2017-05-19 10:00 | 81.89 | 69.87
2017-05-19 10:30 | 81.81 | 69.18
2017-05-19 11:00 | 81.75 | 69.37
2017-05-19 11:30 | 81.04 | 68.59
2017-05-19 12:00 | 80.29 | 67.89
2017-05-19 12:30 | 81.5 | 69.5
2017-05-19 13:00 | 82 | 70.63
2017-05-19 13:30 | 82.18 | 71.1
2017-05-19 14:00 | 82.69 | 73.21
2017-05-19 14:30 | 81.6 | 72.71
2017-05-19 15:00 | 78.12 | 69.35
2017-05-19 15:30 | 78.44 | 70.33
2017-05-19 16:00 | 82.29 | 74.88
2017-05-19 16:30 | 85.73 | 78.31
2017-05-19 17:00 | 89.71 | 81.45
2017-05-19 17:30 | 160.03 | 154.79
2017-05-19 18:00 | 162.97 | 158.17
2017-05-19 18:30 | 145.55 | 140.27
2017-05-19 19:00 | 154.21 | 149.34
2017-05-19 19:30 | 149.14 | 144.97
2017-05-19 20:00 | 147.63 | 143.58
2017-05-19 20:30 | 140.65 | 138.63
2017-05-19 21:00 | 111.56 | 111.54
2017-05-19 21:30 | 107.26 | 107.14
2017-05-19 22:00 | 87.12 | 86.81
2017-05-19 22:30 | 114.83 | 114.53
2017-05-19 23:00 | 139.38 | 139.07
2017-05-19 23:30 | 100.92 | 100.44
2017-05-20 | 49.25 | 48.14
2017-05-20 00:30 | 32.13 | 30.84
2017-05-20 01:00 | 26.35 | 25.13
2017-05-20 01:30 | 15.1 | 12.87
2017-05-20 02:00 | 13.55 | 10.9
2017-05-20 02:30 | 15.75 | 13.63
2017-05-20 03:00 | 18.28 | 15.4
2017-05-20 03:30 | 33.03 | 31.39
2017-05-20 04:00 | 20.16 | 17.61
2017-05-20 04:30 | 10.23 | -1.5
2017-05-20 05:00 | 10.32 | -0.35
2017-05-20 05:30 | 12.95 | 7.19
2017-05-20 06:00 | 24.19 | 21.42
2017-05-20 06:30 | 28.67 | 26.62
2017-05-20 07:00 | 39.43 | 38.21
2017-05-20 07:30 | 44.88 | 44.1
2017-05-20 08:00 | 46.94 | 46.64
2017-05-20 08:30 | 61.95 | 61.94
2017-05-20 09:00 | 70.59 | 70.59
2017-05-20 09:30 | 57.41 | 57.39
2017-05-20 10:00 | 55.67 | 55.6
2017-05-20 10:30 | 65.75 | 65.63
2017-05-20 11:00 | 65.62 | 65.47
2017-05-20 11:30 | 70.45 | 70.32
2017-05-20 12:00 | 67.17 | 67.07
2017-05-20 12:30 | 62.56 | 62.49
2017-05-20 13:00 | 62.36 | 62.31
2017-05-20 13:30 | 56.04 | 55.99
2017-05-20 14:00 | 52.3 | 52.23
2017-05-20 14:30 | 56.84 | 56.77
2017-05-20 15:00 | 68.18 | 68.13
2017-05-20 15:30 | 82.28 | 82.25
2017-05-20 16:00 | 103.8 | 103.77
2017-05-20 16:30 | 112.59 | 112.56
2017-05-20 17:00 | 122.58 | 122.52
2017-05-20 17:30 | 121.23 | 121.03
2017-05-20 18:00 | 126.49 | 126.32
2017-05-20 18:30 | 129.7 | 129.45
2017-05-20 19:00 | 132.06 | 131.73
2017-05-20 19:30 | 128.8 | 128.27
2017-05-20 20:00 | 122.59 | 122.42
2017-05-20 20:30 | 108.45 | 108.45
2017-05-20 21:00 | 87.85 | 87.82
2017-05-20 21:30 | 83.04 | 82.94
2017-05-20 22:00 | 76.24 | 75.97
2017-05-20 22:30 | 97.06 | 96.74
2017-05-20 23:00 | 118.5 | 118.11
2017-05-20 23:30 | 87.86 | 87.15
2017-05-21 | 61.14 | 59.96
2017-05-21 00:30 | 50.57 | 49.1
2017-05-21 01:00 | 32.17 | 30.12
2017-05-21 01:30 | 23.37 | 20.62
2017-05-21 02:00 | 10 | -1.89
2017-05-21 02:30 | 11.66 | -7.55
2017-05-21 03:00 | 12.55 | -9.4
2017-05-21 03:30 | 12.38 | -8.95
2017-05-21 04:00 | 13.19 | -10.2
2017-05-21 04:30 | 19.01 | -17.63
2017-05-21 05:00 | 21.14 | -20.1
2017-05-21 05:30 | 20.76 | -19.66
2017-05-21 06:00 | 21.17 | -20.37
2017-05-21 06:30 | 14.94 | -13.65
2017-05-21 07:00 | 11.15 | -9.37
2017-05-21 07:30 | 8.1 | -5.25
2017-05-21 08:00 | 9.85 | -8.4
2017-05-21 08:30 | 6.62 | -5.58
2017-05-21 09:00 | 3.21 | -2.91
2017-05-21 09:30 | 6.51 | -6.44
2017-05-21 10:00 | 11.74 | -11.39
2017-05-21 10:30 | 14.55 | -14.08
2017-05-21 11:00 | 13.76 | -13.26
2017-05-21 11:30 | 11.97 | -11.56
2017-05-21 12:00 | 7.21 | 6.87
2017-05-21 12:30 | 9.08 | 8.95
2017-05-21 13:00 | 6.95 | 6.68
2017-05-21 13:30 | 4.68 | -4.05
2017-05-21 14:00 | 2.87 | 1.63
2017-05-21 14:30 | 6.07 | -5.21
2017-05-21 15:00 | 5.03 | 3.96
2017-05-21 15:30 | 31.21 | 31.12
2017-05-21 16:00 | 55.7 | 55.66
2017-05-21 16:30 | 58.26 | 58.23
2017-05-21 17:00 | 72.49 | 71.88
2017-05-21 17:30 | 97.31 | 97.03
2017-05-21 18:00 | 112.98 | 112.81
2017-05-21 18:30 | 109.54 | 109.25
2017-05-21 19:00 | 106.38 | 105.81
2017-05-21 19:30 | 99.68 | 99.4
2017-05-21 20:00 | 91.31 | 91.31
2017-05-21 20:30 | 84.93 | 84.91
2017-05-21 21:00 | 57.03 | 56.89
2017-05-21 21:30 | 45.37 | 44.94
2017-05-21 22:00 | 26.02 | 24.66
2017-05-21 22:30 | 51.52 | 50.46
2017-05-21 23:00 | 52.5 | 51.09
2017-05-21 23:30 | 34.02 | 31.54
2017-05-22 | 18.3 | 14.4
2017-05-22 00:30 | 12.36 | 6.45
2017-05-22 01:00 | 9.71 | -3.1
2017-05-22 01:30 | 14.1 | -11.38
2017-05-22 02:00 | 20.69 | -19.34
2017-05-22 02:30 | 20.51 | -19.07
2017-05-22 03:00 | 22.09 | -20.97
2017-05-22 03:30 | 20.87 | -19.62
2017-05-22 04:00 | 16.25 | -14.01
2017-05-22 04:30 | 12.42 | -7.16
2017-05-22 05:00 | 11.32 | -3.16
2017-05-22 05:30 | 10.6 | 2.5
2017-05-22 06:00 | 20.16 | 17.89
2017-05-22 06:30 | 48.33 | 46.99
2017-05-22 07:00 | 74.16 | 67.89
2017-05-22 07:30 | 76.28 | 69.87
2017-05-22 08:00 | 66.47 | 58.32
2017-05-22 08:30 | 62.49 | 52.56
2017-05-22 09:00 | 56.67 | 43.96
2017-05-22 09:30 | 56.57 | 41.37
2017-05-22 10:00 | 56.66 | 42.12
2017-05-22 10:30 | 62.31 | 49.37
2017-05-22 11:00 | 62.74 | 49.42
2017-05-22 11:30 | 61.87 | 48.62
2017-05-22 12:00 | 60.38 | 46.12
2017-05-22 12:30 | 61.29 | 47.57
2017-05-22 13:00 | 76.98 | 66.38
2017-05-22 13:30 | 81.48 | 71.75
2017-05-22 14:00 | 81.28 | 71.38
2017-05-22 14:30 | 81.04 | 71.48
2017-05-22 15:00 | 84.57 | 75.92
2017-05-22 15:30 | 106.57 | 100.16
2017-05-22 16:00 | 121.66 | 116.37
2017-05-22 16:30 | 129.32 | 124.79
2017-05-22 17:00 | 140.07 | 135.99
2017-05-22 17:30 | 144.19 | 139.58
2017-05-22 18:00 | 157.65 | 152.97
2017-05-22 18:30 | 156.86 | 152.05
2017-05-22 19:00 | 144.26 | 139.41
2017-05-22 19:30 | 127.25 | 123.75
2017-05-22 20:00 | 109.48 | 108.13
2017-05-22 20:30 | 105.85 | 104.76
2017-05-22 21:00 | 74.77 | 73.46
2017-05-22 21:30 | 61.93 | 60.96
2017-05-22 22:00 | 43.92 | 43.06
2017-05-22 22:30 | 61.56 | 61.53
2017-05-22 23:00 | 79.46 | 78.72
2017-05-22 23:30 | 54.39 | 53
2017-05-23 | 18.93 | 15.94
2017-05-23 00:30 | 7.78 | 0.34
2017-05-23 01:00 | 13.24 | -8.07
2017-05-23 01:30 | 16.52 | -11.45
2017-05-23 02:00 | 19.1 | -14.55
2017-05-23 02:30 | 14.33 | -11.73
2017-05-23 03:00 | 16.16 | -16.02
2017-05-23 03:30 | 15 | -14.89
2017-05-23 04:00 | 14.3 | -14.2
2017-05-23 04:30 | 10.37 | -10.31
2017-05-23 05:00 | 8.71 | -8.06
2017-05-23 05:30 | 5.91 | -0.3
2017-05-23 06:00 | 21.52 | 16.09
2017-05-23 06:30 | 19.41 | 17.32
2017-05-23 07:00 | 30.64 | 30.45
2017-05-23 07:30 | 62.02 | 61.3
2017-05-23 08:00 | 55.07 | 52.16
2017-05-23 08:30 | 52.16 | 48.16
2017-05-23 09:00 | 51.98 | 47.16
2017-05-23 09:30 | 48.14 | 42.01
2017-05-23 10:00 | 29.66 | 15.64
2017-05-23 10:30 | 30.85 | 16.68
2017-05-23 11:00 | 33.5 | 19.67
2017-05-23 11:30 | 31.24 | 14.73
2017-05-23 12:00 | 33.35 | 20.4
2017-05-23 12:30 | 39.36 | 19.47
2017-05-23 13:00 | 40.88 | 22.69
2017-05-23 13:30 | 38.26 | 19.75
2017-05-23 14:00 | 36.8 | 29.04
2017-05-23 14:30 | 47 | 41.66
2017-05-23 15:00 | 46.04 | 42.09
2017-05-23 15:30 | 91.64 | 91.63
2017-05-23 16:00 | 110.53 | 110.45
2017-05-23 16:30 | 115.04 | 114.93
2017-05-23 17:00 | 117.21 | 117.14
2017-05-23 17:30 | 119.31 | 119.3
2017-05-23 18:00 | 142.01 | 141.58
2017-05-23 18:30 | 137.99 | 135.99
2017-05-23 19:00 | 135.28 | 131.21
2017-05-23 19:30 | 133.37 | 125.73
2017-05-23 20:00 | 117.99 | 117.73
2017-05-23 20:30 | 114.4 | 114.33
2017-05-23 21:00 | 85.33 | 84.9
2017-05-23 21:30 | 68.65 | 67.18
2017-05-23 22:00 | 42.13 | 39.2
2017-05-23 22:30 | 78.63 | 77.12
2017-05-23 23:00 | 93.75 | 92.47
2017-05-23 23:30 | 67.51 | 65.8
2017-05-24 | 29.41 | 25.32
2017-05-24 00:30 | 17.57 | 11.8
2017-05-24 01:00 | 13.87 | -7.06
2017-05-24 01:30 | 28.99 | -27.31
2017-05-24 02:00 | 35.34 | -34.2
2017-05-24 02:30 | 37 | -36.13
2017-05-24 03:00 | 37.54 | -36.79
2017-05-24 03:30 | 38.29 | -37.69
2017-05-24 04:00 | 36.02 | -35.21
2017-05-24 04:30 | 35.24 | -34.1
2017-05-24 05:00 | 30.43 | -28.2
2017-05-24 05:30 | 16.83 | 1.5
2017-05-24 06:00 | 43.85 | 39.79
2017-05-24 06:30 | 92.82 | 91.45
2017-05-24 07:00 | 127.42 | 126.52
2017-05-24 07:30 | 142.43 | 142.43
2017-05-24 08:00 | 115.37 | 114.96
2017-05-24 08:30 | 105.94 | 105.46
2017-05-24 09:00 | 108.29 | 107.38
2017-05-24 09:30 | 103.72 | 102.96
2017-05-24 10:00 | 90.41 | 89.82
2017-05-24 10:30 | 68.87 | 67.7
2017-05-24 11:00 | 62.81 | 61.27
2017-05-24 11:30 | 57.02 | 55.35
2017-05-24 12:00 | 55.43 | 53.88
2017-05-24 12:30 | 56.98 | 55.26
2017-05-24 13:00 | 44.5 | 42.65
2017-05-24 13:30 | 58.94 | 57.91
2017-05-24 14:00 | 54.67 | 54.29
2017-05-24 14:30 | 68.44 | 68.37
2017-05-24 15:00 | 94.89 | 94.88
2017-05-24 15:30 | 127.01 | 127
2017-05-24 16:00 | 156.79 | 156.78
2017-05-24 16:30 | 184.43 | 184.42
2017-05-24 17:00 | 200.15 | 200.15
2017-05-24 17:30 | 207.6 | 207.59
2017-05-24 18:00 | 198.54 | 198.47
2017-05-24 18:30 | 192.72 | 192.68
2017-05-24 19:00 | 182.99 | 182.97
2017-05-24 19:30 | 163.22 | 163.22
2017-05-24 20:00 | 152.42 | 152.39
2017-05-24 20:30 | 135.86 | 135.74
2017-05-24 21:00 | 107.61 | 107.59
2017-05-24 21:30 | 94.91 | 94.78
2017-05-24 22:00 | 62.43 | 61.81
2017-05-24 22:30 | 65.29 | 64.13
2017-05-24 23:00 | 56.5 | 55.18
2017-05-24 23:30 | 47.58 | 45.1
2017-05-25 | 46.21 | 42.37
2017-05-25 00:30 | 35.3 | 30.72
2017-05-25 01:00 | 14.21 | 4.06
2017-05-25 01:30 | 24.8 | -22.3
2017-05-25 02:00 | 30.28 | -28.58
2017-05-25 02:30 | 26 | -24.01
2017-05-25 03:00 | 29.69 | -28.29
2017-05-25 03:30 | 35.93 | -35.15
2017-05-25 04:00 | 33.42 | -32.49
2017-05-25 04:30 | 22.96 | -20
2017-05-25 05:00 | 22.25 | -18.1
2017-05-25 05:30 | 20.31 | 10.73
2017-05-25 06:00 | 44.68 | 40.63
2017-05-25 06:30 | 67.49 | 65.26
2017-05-25 07:00 | 86.19 | 84.68
2017-05-25 07:30 | 118.25 | 117.39
2017-05-25 08:00 | 85.71 | 85.71
2017-05-25 08:30 | 63.09 | 62.69
2017-05-25 09:00 | 56.83 | 56.11
2017-05-25 09:30 | 55.15 | 54.12
2017-05-25 10:00 | 50 | 48.82
2017-05-25 10:30 | 50.81 | 49.26
2017-05-25 11:00 | 39.97 | 37.61
2017-05-25 11:30 | 31.63 | 28.63
2017-05-25 12:00 | 36.19 | 33.3
2017-05-25 12:30 | 39.15 | 36.41
2017-05-25 13:00 | 48.63 | 46.81
2017-05-25 13:30 | 55.53 | 54.11
2017-05-25 14:00 | 61.67 | 60.46
2017-05-25 14:30 | 62.29 | 61.04
2017-05-25 15:00 | 75.03 | 74.21
2017-05-25 15:30 | 90.96 | 90.47
2017-05-25 16:00 | 105.59 | 105.3
2017-05-25 16:30 | 128.59 | 128.47
2017-05-25 17:00 | 145.16 | 145.07
2017-05-25 17:30 | 147.02 | 146.79
2017-05-25 18:00 | 154.17 | 153.84
2017-05-25 18:30 | 147.99 | 147.8
2017-05-25 19:00 | 146.71 | 146.63
2017-05-25 19:30 | 132.84 | 132.8
2017-05-25 20:00 | 123.4 | 123.4
2017-05-25 20:30 | 129.28 | 129.28
2017-05-25 21:00 | 106.29 | 106.29
2017-05-25 21:30 | 94.77 | 94.72
2017-05-25 22:00 | 70.12 | 69.79
2017-05-25 22:30 | 92.9 | 92.25
2017-05-25 23:00 | 116.89 | 116.15
2017-05-25 23:30 | 89.62 | 88.26
2017-05-26 | 41.55 | 38.41
2017-05-26 00:30 | 18.86 | 14.73
2017-05-26 01:00 | 11.73 | -5.13
2017-05-26 01:30 | 19.33 | -16.62
2017-05-26 02:00 | 19.66 | -17.23
2017-05-26 02:30 | 18.45 | -16.39
2017-05-26 03:00 | 18.52 | -16.62
2017-05-26 03:30 | 21.22 | -19.3
2017-05-26 04:00 | 24.21 | -22.04
2017-05-26 04:30 | 20.53 | -16.99
2017-05-26 05:00 | 14.14 | -3.48
2017-05-26 05:30 | 26.19 | 19.24
2017-05-26 06:00 | 50.81 | 47.01
2017-05-26 06:30 | 77.46 | 75.56
2017-05-26 07:00 | 96.97 | 95.62
2017-05-26 07:30 | 107.74 | 106.99
2017-05-26 08:00 | 92.19 | 92.08
2017-05-26 08:30 | 82.74 | 82.52
2017-05-26 09:00 | 78.94 | 78.57
2017-05-26 09:30 | 60.56 | 59.88
2017-05-26 10:00 | 55.28 | 54.56
2017-05-26 10:30 | 48.2 | 47.29
2017-05-26 11:00 | 53.78 | 52.8
2017-05-26 11:30 | 50.11 | 48.86
2017-05-26 12:00 | 52.34 | 51.24
2017-05-26 12:30 | 49.38 | 48.65
2017-05-26 13:00 | 63.8 | 63.24
2017-05-26 13:30 | 70.38 | 69.92
2017-05-26 14:00 | 68.64 | 68.19
2017-05-26 14:30 | 75.19 | 74.83
2017-05-26 15:00 | 77.46 | 77.21
2017-05-26 15:30 | 95.57 | 95.44
2017-05-26 16:00 | 120.74 | 120.67
2017-05-26 16:30 | 144.93 | 144.9
2017-05-26 17:00 | 151.97 | 151.95
2017-05-26 17:30 | 149.87 | 149.84
2017-05-26 18:00 | 144.35 | 144.34
2017-05-26 18:30 | 132.17 | 132.13
2017-05-26 19:00 | 136.79 | 136.73
2017-05-26 19:30 | 132.8 | 132.7
2017-05-26 20:00 | 125.64 | 125.62
2017-05-26 20:30 | 120.3 | 120.27
2017-05-26 21:00 | 110.09 | 110.04
2017-05-26 21:30 | 102.03 | 101.88
2017-05-26 22:00 | 81.2 | 80.79
2017-05-26 22:30 | 108.25 | 107.82
2017-05-26 23:00 | 135.99 | 135.35
2017-05-26 23:30 | 110.28 | 108.75
2017-05-27 | 74.88 | 71.64
2017-05-27 00:30 | 40.32 | 35.18
2017-05-27 01:00 | 17.01 | 7.28
2017-05-27 01:30 | 14.01 | -1.09
2017-05-27 02:00 | 14.6 | -2.98
2017-05-27 02:30 | 20.56 | -13.94
2017-05-27 03:00 | 18.56 | -18.18
2017-05-27 03:30 | 16.11 | -15.94
2017-05-27 04:00 | 15.27 | -15.1
2017-05-27 04:30 | 31.87 | -31.68
2017-05-27 05:00 | 29.8 | -29.69
2017-05-27 05:30 | 22.19 | -22.16
2017-05-27 06:00 | 2.94 | 2.76
2017-05-27 06:30 | 24.72 | 24.51
2017-05-27 07:00 | 31.02 | 30.75
2017-05-27 07:30 | 47.42 | 46.83
2017-05-27 08:00 | 36.88 | 36.46
2017-05-27 08:30 | 38.89 | 36.42
2017-05-27 09:00 | 34.46 | 30.97
2017-05-27 09:30 | 35.74 | 32.72
2017-05-27 10:00 | 47.64 | 45.53
2017-05-27 10:30 | 49.52 | 47.57
2017-05-27 11:00 | 43.93 | 42.06
2017-05-27 11:30 | 34.48 | 31.87
2017-05-27 12:00 | 32.45 | 29.47
2017-05-27 12:30 | 37.64 | 34.84
2017-05-27 13:00 | 37.65 | 34.81
2017-05-27 13:30 | 42.5 | 39.89
2017-05-27 14:00 | 40.2 | 37.34
2017-05-27 14:30 | 45.97 | 43.5
2017-05-27 15:00 | 47.31 | 44.81
2017-05-27 15:30 | 58.16 | 56.03
2017-05-27 16:00 | 82.72 | 81.22
2017-05-27 16:30 | 98.91 | 97.63
2017-05-27 17:00 | 132.59 | 131.83
2017-05-27 17:30 | 159.12 | 158.97
2017-05-27 18:00 | 168.91 | 168.57
2017-05-27 18:30 | 158.58 | 158.24
2017-05-27 19:00 | 158.96 | 158.67
2017-05-27 19:30 | 126.4 | 126.27
2017-05-27 20:00 | 130.7 | 130.67
2017-05-27 20:30 | 126.02 | 126.02
2017-05-27 21:00 | 100.55 | 98.96
2017-05-27 21:30 | 93.94 | 92.13
2017-05-27 22:00 | 79.49 | 76.93
2017-05-27 22:30 | 80.6 | 77.57
2017-05-27 23:00 | 92.83 | 89.71
2017-05-27 23:30 | 72.98 | 68.78
2017-05-28 | 36.96 | 28.95
2017-05-28 00:30 | 27.98 | 17.24
2017-05-28 01:00 | 20.69 | 1.79
2017-05-28 01:30 | 28.48 | -21.29
2017-05-28 02:00 | 38.17 | -33.83
2017-05-28 02:30 | 37.51 | -34.67
2017-05-28 03:00 | 35.65 | -35.5
2017-05-28 03:30 | 37.54 | -37.31
2017-05-28 04:00 | 36.28 | -36.03
2017-05-28 04:30 | 37.37 | -37.05
2017-05-28 05:00 | 37.67 | -37.33
2017-05-28 05:30 | 37.34 | -37.03
2017-05-28 06:00 | 32.44 | -32.34
2017-05-28 06:30 | 13.84 | -13.84
2017-05-28 07:00 | 5.54 | 5.54
2017-05-28 07:30 | 7.11 | 7.06
2017-05-28 08:00 | 9.79 | 9.62
2017-05-28 08:30 | 3.07 | 2.39
2017-05-28 09:00 | 18.85 | -4.12
2017-05-28 09:30 | 19.68 | 6.66
2017-05-28 10:00 | 20.4 | 9.39
2017-05-28 10:30 | 25.7 | 17.81
2017-05-28 11:00 | 17.58 | 2.52
2017-05-28 11:30 | 18.86 | 6.69
2017-05-28 12:00 | 19.27 | 9.45
2017-05-28 12:30 | 23.84 | 15.78
2017-05-28 13:00 | 25.61 | 18.6
2017-05-28 13:30 | 35.21 | 30.01
2017-05-28 14:00 | 30.1 | 24.37
2017-05-28 14:30 | 33.77 | 29.1
2017-05-28 15:00 | 30.56 | 25.78
2017-05-28 15:30 | 34.94 | 30.56
2017-05-28 16:00 | 58.5 | 55.76
2017-05-28 16:30 | 81.73 | 79.72
2017-05-28 17:00 | 113.28 | 112.13
2017-05-28 17:30 | 153.11 | 153.08
2017-05-28 18:00 | 164.17 | 164.12
2017-05-28 18:30 | 164.98 | 164.86
2017-05-28 19:00 | 161.37 | 161.23
2017-05-28 19:30 | 135.3 | 135.26
2017-05-28 20:00 | 117.79 | 116.77
2017-05-28 20:30 | 108.81 | 107.44
2017-05-28 21:00 | 95.71 | 93.57
2017-05-28 21:30 | 81.07 | 78.14
2017-05-28 22:00 | 76.32 | 72.67
2017-05-28 22:30 | 82.43 | 78.91
2017-05-28 23:00 | 89.04 | 85.26
2017-05-28 23:30 | 59.34 | 54.03
2017-05-29 | 36.64 | 28.49
2017-05-29 00:30 | 24.44 | 11.59
2017-05-29 01:00 | 25.72 | -17.37
2017-05-29 01:30 | 35.1 | -30.32
2017-05-29 02:00 | 37.21 | -32.77
2017-05-29 02:30 | 37.76 | -33.38
2017-05-29 03:00 | 39.71 | -36.13
2017-05-29 03:30 | 40.15 | -36.84
2017-05-29 04:00 | 43.09 | -40.9
2017-05-29 04:30 | 37.5 | -33.52
2017-05-29 05:00 | 34.69 | -29.72
2017-05-29 05:30 | 21.79 | -2.71
2017-05-29 06:00 | 48.76 | 42.74
2017-05-29 06:30 | 72.06 | 69.64
2017-05-29 07:00 | 109.06 | 107.76
2017-05-29 07:30 | 127.58 | 126.85
2017-05-29 08:00 | 109.23 | 109.14
2017-05-29 08:30 | 97.15 | 96.27
2017-05-29 09:00 | 80.56 | 79.34
2017-05-29 09:30 | 66.56 | 64.77
2017-05-29 10:00 | 64.08 | 62.58
2017-05-29 10:30 | 60.29 | 58.28
2017-05-29 11:00 | 58.5 | 55.9
2017-05-29 11:30 | 54.05 | 51.57
2017-05-29 12:00 | 53.6 | 51.02
2017-05-29 12:30 | 44.24 | 41.22
2017-05-29 13:00 | 41.77 | 38.14
2017-05-29 13:30 | 46.49 | 43.49
2017-05-29 14:00 | 62.45 | 60.83
2017-05-29 14:30 | 66.82 | 65.37
2017-05-29 15:00 | 80.09 | 78.97
2017-05-29 15:30 | 97.18 | 96.45
2017-05-29 16:00 | 104.06 | 103.58
2017-05-29 16:30 | 109.02 | 108.5
2017-05-29 17:00 | 117.1 | 116.36
2017-05-29 17:30 | 137.26 | 135.74
2017-05-29 18:00 | 149.66 | 147.75
2017-05-29 18:30 | 136.6 | 134.84
2017-05-29 19:00 | 140.2 | 138.5
2017-05-29 19:30 | 129.68 | 128.23
2017-05-29 20:00 | 121.48 | 120.07
2017-05-29 20:30 | 119.23 | 118.96
2017-05-29 21:00 | 104.99 | 104.39
2017-05-29 21:30 | 89.25 | 88.23
2017-05-29 22:00 | 64.34 | 62.08
2017-05-29 22:30 | 87.03 | 85.3
2017-05-29 23:00 | 92.46 | 90.68
2017-05-29 23:30 | 70 | 67.38
2017-05-30 | 37.14 | 33.37
2017-05-30 00:30 | 12.97 | -5.84
2017-05-30 01:00 | 24.57 | -22.84
2017-05-30 01:30 | 32.96 | -32.19
2017-05-30 02:00 | 32.18 | -31.36
2017-05-30 02:30 | 34.55 | -32.19
2017-05-30 03:00 | 34.95 | -34.26
2017-05-30 03:30 | 33.58 | -33.28
2017-05-30 04:00 | 35.63 | -35.15
2017-05-30 04:30 | 28.73 | -28.59
2017-05-30 05:00 | 28.51 | -28.46
2017-05-30 05:30 | 14.54 | -14.54
2017-05-30 06:00 | 3.55 | 3.07
2017-05-30 06:30 | 45.03 | 44.45
2017-05-30 07:00 | 90.21 | 88.59
2017-05-30 07:30 | 114.99 | 114.96
2017-05-30 08:00 | 85.65 | 83.85
2017-05-30 08:30 | 56.72 | 51.76
2017-05-30 09:00 | 36.71 | 25.76
2017-05-30 09:30 | 29.52 | -8.03
2017-05-30 10:00 | 31.16 | -6.7
2017-05-30 10:30 | 28.21 | 5.93
2017-05-30 11:00 | 21.82 | 1.48
2017-05-30 11:30 | 23.29 | -6.55
2017-05-30 12:00 | 23.94 | -8.45
2017-05-30 12:30 | 22.57 | -1.25
2017-05-30 13:00 | 24.17 | 7.89
2017-05-30 13:30 | 45.59 | 40.93
2017-05-30 14:00 | 56.76 | 53.52
2017-05-30 14:30 | 54.89 | 51.31
2017-05-30 15:00 | 61.43 | 58.37
2017-05-30 15:30 | 78.22 | 76.17
2017-05-30 16:00 | 98.74 | 97.26
2017-05-30 16:30 | 118.79 | 117.76
2017-05-30 17:00 | 100.84 | 99.4
2017-05-30 17:30 | 110.84 | 110.37
2017-05-30 18:00 | 115.65 | 115.31
2017-05-30 18:30 | 114.14 | 113.87
2017-05-30 19:00 | 117.74 | 117.59
2017-05-30 19:30 | 105.04 | 105
2017-05-30 20:00 | 95.26 | 94.09
2017-05-30 20:30 | 82.15 | 80.99
2017-05-30 21:00 | 74.43 | 73.83
2017-05-30 21:30 | 80.9 | 80.65
2017-05-30 22:00 | 58.79 | 58.76
2017-05-30 22:30 | 56.29 | 56.29
2017-05-30 23:00 | 79.28 | 79.28
2017-05-30 23:30 | 56.64 | 56.6
2017-05-31 | 26.54 | 26.42
2017-05-31 00:30 | 12.78 | 12.73
2017-05-31 01:00 | 11.54 | -11.51
2017-05-31 01:30 | 34.97 | -34.89
2017-05-31 02:00 | 42.08 | -42
2017-05-31 02:30 | 50.24 | -50.07
2017-05-31 03:00 | 53.41 | -53.24
2017-05-31 03:30 | 54.75 | -54.58
2017-05-31 04:00 | 51.53 | -51.42
2017-05-31 04:30 | 50.09 | -50.03
2017-05-31 05:00 | 43.84 | -43.75
2017-05-31 05:30 | 21.85 | -21.85
2017-05-31 06:00 | 16.46 | 16.36
2017-05-31 06:30 | 58.24 | 58.09
2017-05-31 07:00 | 102.51 | 102.36
2017-05-31 07:30 | 134.78 | 134.27
2017-05-31 08:00 | 111.35 | 110.61
2017-05-31 08:30 | 88.06 | 86.98
2017-05-31 09:00 | 72.84 | 71.47
2017-05-31 09:30 | 63.81 | 62.22
2017-05-31 10:00 | 49.61 | 47.58
2017-05-31 10:30 | 42.62 | 39.79
2017-05-31 11:00 | 19.72 | 10.13
2017-05-31 11:30 | 17.7 | 3.71
2017-05-31 12:00 | 17.1 | 4.17
2017-05-31 12:30 | 20.4 | 12.48
2017-05-31 13:00 | 30.13 | 25.82
2017-05-31 13:30 | 39.92 | 36.4
2017-05-31 14:00 | 43.29 | 40
2017-05-31 14:30 | 36.01 | 31.71
2017-05-31 15:00 | 25.77 | 19.7
2017-05-31 15:30 | 51.12 | 48.54
2017-05-31 16:00 | 65.97 | 64.25
2017-05-31 16:30 | 73.46 | 72.05
2017-05-31 17:00 | 84.4 | 83.13
2017-05-31 17:30 | 108.25 | 102.68
2017-05-31 18:00 | 142.49 | 126.29
2017-05-31 18:30 | 138.96 | 129.18
2017-05-31 19:00 | 145.47 | 136.42
2017-05-31 19:30 | 137.24 | 128.67
2017-05-31 20:00 | 121.59 | 120.48
2017-05-31 20:30 | 99.97 | 99.04
2017-05-31 21:00 | 65.73 | 64.88
2017-05-31 21:30 | 47.9 | 47.22
2017-05-31 22:00 | 39.38 | 39.18
2017-05-31 22:30 | 51.23 | 51.17
2017-05-31 23:00 | 81.13 | 81.12
2017-05-31 23:30 | 50.6 | 50.5
2017-06-01 | 4.13 | 3.22
2017-06-01 00:30 | 26.63 | -20.56
2017-06-01 01:00 | 40.99 | -36.41
2017-06-01 01:30 | 52.97 | -49.89
2017-06-01 02:00 | 55.06 | -52.26
2017-06-01 02:30 | 55.84 | -53.23
2017-06-01 03:00 | 57.29 | -54.92
2017-06-01 03:30 | 57.04 | -54.59
2017-06-01 04:00 | 53.68 | -50.78
2017-06-01 04:30 | 50.39 | -46.68
2017-06-01 05:00 | 44.72 | -40.23
2017-06-01 05:30 | 23.14 | -11.71
2017-06-01 06:00 | 32.85 | 26.46
2017-06-01 06:30 | 52.49 | 52.07
2017-06-01 07:00 | 62.88 | 61.52
2017-06-01 07:30 | 81.72 | 79.88
2017-06-01 08:00 | 50.89 | 46.61
2017-06-01 08:30 | 29.38 | 19.95
2017-06-01 09:00 | 28.47 | 18.23
2017-06-01 09:30 | 26.9 | -13.74
2017-06-01 10:00 | 36.26 | -27.73
2017-06-01 10:30 | 48.11 | -40.88
2017-06-01 11:00 | 51.44 | -44.29
2017-06-01 11:30 | 41.91 | -33.77
2017-06-01 12:00 | 38.29 | -28.69
2017-06-01 12:30 | 36.01 | -25.64
2017-06-01 13:00 | 39.79 | -30.33
2017-06-01 13:30 | 32.87 | -20.96
2017-06-01 14:00 | 29.41 | -15.14
2017-06-01 14:30 | 27.41 | -10.47
2017-06-01 15:00 | 28.01 | -0.56
2017-06-01 15:30 | 30.01 | 13.06
2017-06-01 16:00 | 37.87 | 27.05
2017-06-01 16:30 | 44.29 | 35.25
2017-06-01 17:00 | 56.81 | 49.48
2017-06-01 17:30 | 97.86 | 88.44
2017-06-01 18:00 | 123.63 | 115.78
2017-06-01 18:30 | 120.42 | 113.66
2017-06-01 19:00 | 123.5 | 117.31
2017-06-01 19:30 | 113.13 | 107.07
2017-06-01 20:00 | 106.08 | 105.76
2017-06-01 20:30 | 92.7 | 92.69
2017-06-01 21:00 | 47.54 | 47.29
2017-06-01 21:30 | 28.71 | 27.82
2017-06-01 22:00 | 9.86 | 6.23
2017-06-01 22:30 | 17.35 | 14.49
2017-06-01 23:00 | 35.14 | 33.02
2017-06-01 23:30 | 20.61 | 16.32
2017-06-02 | 22.82 | -18.08
2017-06-02 00:30 | 39.02 | -37.72
2017-06-02 01:00 | 43.57 | -41.51
2017-06-02 01:30 | 48.29 | -47.2
2017-06-02 02:00 | 52.9 | -52.22
2017-06-02 02:30 | 54.31 | -53.7
2017-06-02 03:00 | 57.81 | -57.52
2017-06-02 03:30 | 62.28 | -62.16
2017-06-02 04:00 | 64.9 | -64.77
2017-06-02 04:30 | 62.19 | -61.9
2017-06-02 05:00 | 54.47 | -53.52
2017-06-02 05:30 | 38.31 | -35.45
2017-06-02 06:00 | 18.19 | -1.56
2017-06-02 06:30 | 57.13 | 54.01
2017-06-02 07:00 | 96.64 | 95.83
2017-06-02 07:30 | 122.14 | 121.47
2017-06-02 08:00 | 82.67 | 82.02
2017-06-02 08:30 | 52.26 | 51.72
2017-06-02 09:00 | 34.78 | 34.42
2017-06-02 09:30 | 15.49 | 14.87
2017-06-02 10:00 | 7.42 | 4.25
2017-06-02 10:30 | 11.75 | -10.4
2017-06-02 11:00 | 20.54 | -19.81
2017-06-02 11:30 | 12.02 | -10.24
2017-06-02 12:00 | 2.81 | -2.56
2017-06-02 12:30 | 5.37 | -5.36
2017-06-02 13:00 | 3.56 | 3.51
2017-06-02 13:30 | 4.31 | 4.25
2017-06-02 14:00 | 7.7 | 7.46
2017-06-02 14:30 | 10.33 | 9.99
2017-06-02 15:00 | 26.65 | 26.35
2017-06-02 15:30 | 42.29 | 42
2017-06-02 16:00 | 44.4 | 44.12
2017-06-02 16:30 | 45.87 | 45.64
2017-06-02 17:00 | 46.85 | 46.76
2017-06-02 17:30 | 81.92 | 81.92
2017-06-02 18:00 | 114.34 | 114.28
2017-06-02 18:30 | 112.61 | 112.59
2017-06-02 19:00 | 109.31 | 109.3
2017-06-02 19:30 | 95.49 | 95.48
2017-06-02 20:00 | 83.36 | 83.35
2017-06-02 20:30 | 70.33 | 70.29
2017-06-02 21:00 | 49.61 | 49.5
2017-06-02 21:30 | 44.42 | 44.07
2017-06-02 22:00 | 22.25 | 19.69
2017-06-02 22:30 | 18.44 | 15.97
2017-06-02 23:00 | 39.25 | 37.78
2017-06-02 23:30 | 16.83 | 10.89
2017-06-03 | 26.45 | -22.13
2017-06-03 00:30 | 34.2 | -31.79
2017-06-03 01:00 | 37.49 | -36.29
2017-06-03 01:30 | 41.32 | -40.77
2017-06-03 02:00 | 48.69 | -47.8
2017-06-03 02:30 | 50.12 | -49.01
2017-06-03 03:00 | 61.45 | -61.35
2017-06-03 03:30 | 66.1 | -66.1
2017-06-03 04:00 | 65.66 | -65.66
2017-06-03 04:30 | 64.54 | -64.52
2017-06-03 05:00 | 63.68 | -63.64
2017-06-03 05:30 | 62.48 | -62.41
2017-06-03 06:00 | 51.52 | -50.14
2017-06-03 06:30 | 44 | -40.78
2017-06-03 07:00 | 28.68 | -19.05
2017-06-03 07:30 | 31.63 | 19.75
2017-06-03 08:00 | 33.37 | 24.42
2017-06-03 08:30 | 17.32 | 1.66
2017-06-03 09:00 | 17.42 | 5.58
2017-06-03 09:30 | 37.63 | -37.51
2017-06-03 10:00 | 60.4 | -60.35
2017-06-03 10:30 | 65.9 | -65.85
2017-06-03 11:00 | 69.47 | -69.41
2017-06-03 11:30 | 71.99 | -71.91
2017-06-03 12:00 | 74.7 | -74.63
2017-06-03 12:30 | 74.1 | -74.08
2017-06-03 13:00 | 76.17 | -76.15
2017-06-03 13:30 | 74.47 | -74.44
2017-06-03 14:00 | 72.81 | -72.79
2017-06-03 14:30 | 68.19 | -68.17
2017-06-03 15:00 | 65.48 | -65.45
2017-06-03 15:30 | 57.49 | -57.48
2017-06-03 16:00 | 7.71 | -5.49
2017-06-03 16:30 | 14.51 | 13.61
2017-06-03 17:00 | 28.9 | 28.85
2017-06-03 17:30 | 44.13 | 43.97
2017-06-03 18:00 | 42.85 | 42.83
2017-06-03 18:30 | 23.01 | 23.01
2017-06-03 19:00 | 40.9 | 40.57
2017-06-03 19:30 | 29.94 | 29.16
2017-06-03 20:00 | 30.3 | 28.71
2017-06-03 20:30 | 34.03 | -33.65
2017-06-03 21:00 | 45.49 | -45.44
2017-06-03 21:30 | 7.72 | -4.74
2017-06-03 22:00 | 22.39 | -21.3
2017-06-03 22:30 | 32.69 | -31.97
2017-06-03 23:00 | 14.13 | 7.2
2017-06-03 23:30 | 19.23 | -12.75
2017-06-04 | 37.91 | -35.53
2017-06-04 00:30 | 35.95 | -32.54
2017-06-04 01:00 | 42.78 | -40.53
2017-06-04 01:30 | 65 | -64.98
2017-06-04 02:00 | 63.56 | -63.55
2017-06-04 02:30 | 64.23 | -64.23
2017-06-04 03:00 | 65.17 | -65.17
2017-06-04 03:30 | 64.01 | -64.01
2017-06-04 04:00 | 63.46 | -63.46
2017-06-04 04:30 | 63.09 | -63.09
2017-06-04 05:00 | 61.3 | -61.26
2017-06-04 05:30 | 63.23 | -63.22
2017-06-04 06:00 | 62.61 | -62.58
2017-06-04 06:30 | 60.52 | -60.48
2017-06-04 07:00 | 54.74 | -54.48
2017-06-04 07:30 | 34.9 | -30.3
2017-06-04 08:00 | 33.41 | -28.09
2017-06-04 08:30 | 35.87 | -32.46
2017-06-04 09:00 | 45.39 | -44.66
2017-06-04 09:30 | 52.89 | -52.82
2017-06-04 10:00 | 58 | -57.97
2017-06-04 10:30 | 52.46 | -52.28
2017-06-04 11:00 | 68.47 | -68.46
2017-06-04 11:30 | 69.93 | -69.92
2017-06-04 12:00 | 62.56 | -62.49
2017-06-04 12:30 | 53.64 | -53.32
2017-06-04 13:00 | 49.92 | -49.48
2017-06-04 13:30 | 47.78 | -47.26
2017-06-04 14:00 | 44.91 | -44.47
2017-06-04 14:30 | 43.67 | -43.38
2017-06-04 15:00 | 33.7 | -32.97
2017-06-04 15:30 | 12.5 | -9.34
2017-06-04 16:00 | 12.89 | 9.71
2017-06-04 16:30 | 46.77 | 45.91
2017-06-04 17:00 | 69.45 | 68.93
2017-06-04 17:30 | 103.05 | 102.85
2017-06-04 18:00 | 116.15 | 115.88
2017-06-04 18:30 | 122.03 | 122.01
2017-06-04 19:00 | 120.29 | 120.21
2017-06-04 19:30 | 101.89 | 101.54
2017-06-04 20:00 | 91.67 | 91.06
2017-06-04 20:30 | 65.29 | 65.29
2017-06-04 21:00 | 40.34 | 40.33
2017-06-04 21:30 | 29.88 | 29.75
2017-06-04 22:00 | 19.96 | 8.64
2017-06-04 22:30 | 21.9 | 8.2
2017-06-04 23:00 | 43.91 | 36.36
2017-06-04 23:30 | 33.22 | 22.5
2017-06-05 | 22.8 | -6.28
2017-06-05 00:30 | 25.87 | -15.92
2017-06-05 01:00 | 34.57 | -30.13
2017-06-05 01:30 | 41.56 | -39.31
2017-06-05 02:00 | 51.14 | -50.58
2017-06-05 02:30 | 49.11 | -48.15
2017-06-05 03:00 | 61.6 | -61.6
2017-06-05 03:30 | 60.92 | -60.92
2017-06-05 04:00 | 58.56 | -58.52
2017-06-05 04:30 | 52.36 | -51.96
2017-06-05 05:00 | 52.04 | -51.5
2017-06-05 05:30 | 42.29 | -38.97
2017-06-05 06:00 | 22.57 | -3.85
2017-06-05 06:30 | 32.72 | 26.15
2017-06-05 07:00 | 53.38 | 52.72
2017-06-05 07:30 | 87.54 | 87.41
2017-06-05 08:00 | 65.68 | 63.32
2017-06-05 08:30 | 40.18 | 34.61
2017-06-05 09:00 | 25.49 | 13.87
2017-06-05 09:30 | 25.23 | -10.63
2017-06-05 10:00 | 29.95 | -18.66
2017-06-05 10:30 | 25.4 | -17.67
2017-06-05 11:00 | 52.08 | -45.72
2017-06-05 11:30 | 57.06 | -50.72
2017-06-05 12:00 | 52.15 | -47.34
2017-06-05 12:30 | 54.32 | -53.33
2017-06-05 13:00 | 41.49 | -41.47
2017-06-05 13:30 | 27.27 | -27.27
2017-06-05 14:00 | 26.14 | -26.03
2017-06-05 14:30 | 9.51 | -9.4
2017-06-05 15:00 | 18.67 | 17.92
2017-06-05 15:30 | 47.57 | 46.96
2017-06-05 16:00 | 72.62 | 72.17
2017-06-05 16:30 | 87.78 | 87.43
2017-06-05 17:00 | 106.69 | 106.6
2017-06-05 17:30 | 116.01 | 115.53
2017-06-05 18:00 | 123.01 | 121.78
2017-06-05 18:30 | 127 | 126.28
2017-06-05 19:00 | 127.29 | 126.85
2017-06-05 19:30 | 119.78 | 119.61
2017-06-05 20:00 | 107.51 | 107.48
2017-06-05 20:30 | 94.89 | 94.89
2017-06-05 21:00 | 93.93 | 93.83
2017-06-05 21:30 | 99.19 | 99.03
2017-06-05 22:00 | 74.31 | 73.63
2017-06-05 22:30 | 77.1 | 76.07
2017-06-05 23:00 | 92.5 | 91.27
2017-06-05 23:30 | 71.2 | 68.77
2017-06-06 | 23.77 | 15.76
2017-06-06 00:30 | 17.79 | -7.72
2017-06-06 01:00 | 22.13 | -16.18
2017-06-06 01:30 | 25.8 | -22.6
2017-06-06 02:00 | 30.09 | -27.96
2017-06-06 02:30 | 32.56 | -30.75
2017-06-06 03:00 | 33.16 | -31.16
2017-06-06 03:30 | 32.74 | -30.45
2017-06-06 04:00 | 32.81 | -31.03
2017-06-06 04:30 | 31.39 | -29.29
2017-06-06 05:00 | 31.1 | -28.6
2017-06-06 05:30 | 20.54 | -9.1
2017-06-06 06:00 | 22.34 | 10.62
2017-06-06 06:30 | 63.16 | 60.51
2017-06-06 07:00 | 89.36 | 88.96
2017-06-06 07:30 | 128.98 | 128.97
2017-06-06 08:00 | 105.25 | 105.25
2017-06-06 08:30 | 74.65 | 74.6
2017-06-06 09:00 | 58.13 | 58.05
2017-06-06 09:30 | 30.4 | 30.15
2017-06-06 10:00 | 22 | 21.55
2017-06-06 10:30 | 14.82 | 14.42
2017-06-06 11:00 | 9.37 | 8.67
2017-06-06 11:30 | 5.9 | 3.05
2017-06-06 12:00 | 5.42 | 1.47
2017-06-06 12:30 | 4.83 | -2.34
2017-06-06 13:00 | 6.02 | -4.65
2017-06-06 13:30 | 4.62 | -1.05
2017-06-06 14:00 | 6.17 | 2.81
2017-06-06 14:30 | 10.45 | 8.66
2017-06-06 15:00 | 14.15 | 13.01
2017-06-06 15:30 | 19.81 | 19.06
2017-06-06 16:00 | 26.74 | 26.29
2017-06-06 16:30 | 45.86 | 44.86
2017-06-06 17:00 | 62.83 | 53.62
2017-06-06 17:30 | 95.11 | 87.69
2017-06-06 18:00 | 119.4 | 114.77
2017-06-06 18:30 | 121.99 | 117.82
2017-06-06 19:00 | 126.16 | 122.52
2017-06-06 19:30 | 115.73 | 113.66
2017-06-06 20:00 | 109.38 | 108.72
2017-06-06 20:30 | 107.31 | 106.8
2017-06-06 21:00 | 96.53 | 96.23
2017-06-06 21:30 | 89.33 | 89.24
2017-06-06 22:00 | 77.98 | 77.94
2017-06-06 22:30 | 99.1 | 98.69
2017-06-06 23:00 | 100.83 | 100.29
2017-06-06 23:30 | 68.39 | 66.94
2017-06-07 | 40.25 | 37.6
2017-06-07 00:30 | 28.78 | 25.38
2017-06-07 01:00 | 18.83 | 14.04
2017-06-07 01:30 | 10.24 | 6.48
2017-06-07 02:00 | 8.6 | 3.75
2017-06-07 02:30 | 7.73 | 1.97
2017-06-07 03:00 | 7.28 | 0.15
2017-06-07 03:30 | 7.6 | 0.18
2017-06-07 04:00 | 8.41 | 2.16
2017-06-07 04:30 | 11.62 | 6.61
2017-06-07 05:00 | 17.84 | 13.68
2017-06-07 05:30 | 30.09 | 26.16
2017-06-07 06:00 | 68.64 | 66.5
2017-06-07 06:30 | 96.54 | 96.53
2017-06-07 07:00 | 130.13 | 130.13
2017-06-07 07:30 | 159.19 | 158.82
2017-06-07 08:00 | 140.04 | 138.77
2017-06-07 08:30 | 96.38 | 95.72
2017-06-07 09:00 | 76.16 | 76.11
2017-06-07 09:30 | 66.68 | 66.64
2017-06-07 10:00 | 58.33 | 56.02
2017-06-07 10:30 | 47.69 | 47.31
2017-06-07 11:00 | 42.9 | 42.72
2017-06-07 11:30 | 36.61 | 36.36
2017-06-07 12:00 | 32.21 | 31.82
2017-06-07 12:30 | 11.96 | 11.33
2017-06-07 13:00 | 41.49 | -41.01
2017-06-07 13:30 | 40.57 | -40.14
2017-06-07 14:00 | 25.7 | -25.27
2017-06-07 14:30 | 20.15 | -19.7
2017-06-07 15:00 | 13.17 | -12.65
2017-06-07 15:30 | 10.62 | 10.37
2017-06-07 16:00 | 29.46 | 29.4
2017-06-07 16:30 | 56.22 | 55.93
2017-06-07 17:00 | 90.94 | 88.11
2017-06-07 17:30 | 145.02 | 132.69
2017-06-07 18:00 | 160.13 | 147.35
2017-06-07 18:30 | 171.95 | 159.67
2017-06-07 19:00 | 186.1 | 175.08
2017-06-07 19:30 | 184.75 | 177.15
2017-06-07 20:00 | 174.08 | 170.06
2017-06-07 20:30 | 155.16 | 151.24
2017-06-07 21:00 | 125.94 | 122.41
2017-06-07 21:30 | 122.83 | 120.43
2017-06-07 22:00 | 103.23 | 103.03
2017-06-07 22:30 | 94.74 | 94.54
2017-06-07 23:00 | 94.39 | 93.12
2017-06-07 23:30 | 58.39 | 56.07
2017-06-08 | 20.98 | 13.43
2017-06-08 00:30 | 17.3 | 4.9
2017-06-08 01:00 | 17.19 | -9.62
2017-06-08 01:30 | 23.16 | -20.5
2017-06-08 02:00 | 27.81 | -25.97
2017-06-08 02:30 | 28.75 | -27.23
2017-06-08 03:00 | 31.48 | -30.56
2017-06-08 03:30 | 33.95 | -33.39
2017-06-08 04:00 | 34.08 | -33.67
2017-06-08 04:30 | 28.44 | -26.87
2017-06-08 05:00 | 26.64 | -23.66
2017-06-08 05:30 | 19.08 | -5.67
2017-06-08 06:00 | 35.84 | 29.25
2017-06-08 06:30 | 94.83 | 94.16
2017-06-08 07:00 | 145.54 | 145.45
2017-06-08 07:30 | 190.72 | 190.68
2017-06-08 08:00 | 160.86 | 160.79
2017-06-08 08:30 | 112.09 | 112.08
2017-06-08 09:00 | 53.82 | 53.82
2017-06-08 09:30 | 24.99 | 24.94
2017-06-08 10:00 | 9.84 | 9.77
2017-06-08 10:30 | 2.16 | -2.08
2017-06-08 11:00 | 3.57 | -2.88
2017-06-08 11:30 | 3.72 | -2.66
2017-06-08 12:00 | 15.29 | -14.66
2017-06-08 12:30 | 24.75 | -24.29
2017-06-08 13:00 | 9.89 | -7.83
2017-06-08 13:30 | 13.88 | 1.21
2017-06-08 14:00 | 22.56 | 18.1
2017-06-08 14:30 | 27.73 | 25.16
2017-06-08 15:00 | 32.45 | 29.26
2017-06-08 15:30 | 54.59 | 52.48
2017-06-08 16:00 | 88.4 | 87.15
2017-06-08 16:30 | 88.86 | 87.7
2017-06-08 17:00 | 103.1 | 102.38
2017-06-08 17:30 | 140.16 | 140.09
2017-06-08 18:00 | 173.5 | 173.5
2017-06-08 18:30 | 185.59 | 185.13
2017-06-08 19:00 | 197.62 | 197.62
2017-06-08 19:30 | 197.92 | 197.92
2017-06-08 20:00 | 178.29 | 178.2
2017-06-08 20:30 | 165.61 | 165.59
2017-06-08 21:00 | 132.77 | 132.77
2017-06-08 21:30 | 115.34 | 115.34
2017-06-08 22:00 | 91.91 | 91.8
2017-06-08 22:30 | 87.05 | 86.1
2017-06-08 23:00 | 102.45 | 99.25
2017-06-08 23:30 | 77.7 | 73.17
2017-06-09 | 43.89 | 35.42
2017-06-09 00:30 | 27.05 | 13.05
2017-06-09 01:00 | 22.84 | -9.47
2017-06-09 01:30 | 26.65 | -18.88
2017-06-09 02:00 | 30.89 | -25.43
2017-06-09 02:30 | 34.35 | -30.41
2017-06-09 03:00 | 37.22 | -33.98
2017-06-09 03:30 | 35.87 | -32.31
2017-06-09 04:00 | 64.31 | -64.14
2017-06-09 04:30 | 37.07 | -35.99
2017-06-09 05:00 | 29.86 | -25.42
2017-06-09 05:30 | 24.33 | -10.61
2017-06-09 06:00 | 45.16 | 38
2017-06-09 06:30 | 90.15 | 87.64
2017-06-09 07:00 | 133.27 | 132.02
2017-06-09 07:30 | 158.38 | 157.82
2017-06-09 08:00 | 173.33 | 172.97
2017-06-09 08:30 | 132.81 | 132.25
2017-06-09 09:00 | 141.37 | 141.3
2017-06-09 09:30 | 135.12 | 135.09
2017-06-09 10:00 | 68.01 | 66.15
2017-06-09 10:30 | 27.14 | 27.09
2017-06-09 11:00 | 14 | 13.9
2017-06-09 11:30 | 5.5 | 5.26
2017-06-09 12:00 | 6.91 | 5.76
2017-06-09 12:30 | 13.46 | 11.44
2017-06-09 13:00 | 13.82 | 11.8
2017-06-09 13:30 | 20.06 | 19.46
2017-06-09 14:00 | 18.7 | 18.61
2017-06-09 14:30 | 26.48 | 26.44
2017-06-09 15:00 | 46.57 | 46.56
2017-06-09 15:30 | 46.01 | 46.01
2017-06-09 16:00 | 37.94 | 37.94
2017-06-09 16:30 | 43.07 | 43.07
2017-06-09 17:00 | 72.11 | 72.1
2017-06-09 17:30 | 117.71 | 113.37
2017-06-09 18:00 | 129.66 | 125.47
2017-06-09 18:30 | 127.98 | 123.22
2017-06-09 19:00 | 131.54 | 127.28
2017-06-09 19:30 | 129.66 | 127.49
2017-06-09 20:00 | 118.5 | 118.22
2017-06-09 20:30 | 107.43 | 107.43
2017-06-09 21:00 | 89.5 | 89.4
2017-06-09 21:30 | 70.97 | 70.64
2017-06-09 22:00 | 42.09 | 40.99
2017-06-09 22:30 | 48.92 | 47.43
2017-06-09 23:00 | 60.54 | 59.03
2017-06-09 23:30 | 37.19 | 33.77
2017-06-10 | 20 | 12.53
2017-06-10 00:30 | 18.57 | -11.64
2017-06-10 01:00 | 26.65 | -16.3
2017-06-10 01:30 | 40.16 | -32.15
2017-06-10 02:00 | 50.67 | -45.22
2017-06-10 02:30 | 52.19 | -47.14
2017-06-10 03:00 | 56.4 | -52.25
2017-06-10 03:30 | 63.62 | -60.64
2017-06-10 04:00 | 67.49 | -65.22
2017-06-10 04:30 | 81.53 | -81.46
2017-06-10 05:00 | 74.13 | -73.96
2017-06-10 05:30 | 57.79 | -54.46
2017-06-10 06:00 | 38.9 | -29.26
2017-06-10 06:30 | 35.55 | -21.86
2017-06-10 07:00 | 29.23 | -3.05
2017-06-10 07:30 | 39.36 | 25.13
2017-06-10 08:00 | 42.56 | 31.93
2017-06-10 08:30 | 38.9 | 28.55
2017-06-10 09:00 | 27.96 | 22.82
2017-06-10 09:30 | 15.74 | 15.49
2017-06-10 10:00 | 13.55 | 13.32
2017-06-10 10:30 | 4.82 | 4.31
2017-06-10 11:00 | 14.08 | -13.94
2017-06-10 11:30 | 11.71 | -11.37
2017-06-10 12:00 | 15.13 | -14.9
2017-06-10 12:30 | 12.18 | -11.62
2017-06-10 13:00 | 6.63 | 5.41
2017-06-10 13:30 | 8.81 | 7.7
2017-06-10 14:00 | 6.04 | 4.33
2017-06-10 14:30 | 8.75 | 7.42
2017-06-10 15:00 | 7.45 | 6.13
2017-06-10 15:30 | 15.29 | 14.67
2017-06-10 16:00 | 36.19 | 35.92
2017-06-10 16:30 | 38.68 | 38.5
2017-06-10 17:00 | 55.65 | 55.61
2017-06-10 17:30 | 109.87 | 109.09
2017-06-10 18:00 | 110.85 | 110.11
2017-06-10 18:30 | 101 | 99.99
2017-06-10 19:00 | 102.05 | 100.79
2017-06-10 19:30 | 75.53 | 73.41
2017-06-10 20:00 | 75.45 | 72.97
2017-06-10 20:30 | 66.69 | 63.36
2017-06-10 21:00 | 47.74 | 42.44
2017-06-10 21:30 | 34.42 | 32.54
2017-06-10 22:00 | 36.65 | 35.2
2017-06-10 22:30 | 63.66 | 62.39
2017-06-10 23:00 | 63.38 | 61.61
2017-06-10 23:30 | 49.73 | 46.89
2017-06-11 | 23.49 | 16.98
2017-06-11 00:30 | 19.51 | -13.17
2017-06-11 01:00 | 32.25 | -29.11
2017-06-11 01:30 | 44.56 | -38.59
2017-06-11 02:00 | 50.42 | -44.77
2017-06-11 02:30 | 46.75 | -40.32
2017-06-11 03:00 | 51.25 | -45.95
2017-06-11 03:30 | 51.22 | -46.09
2017-06-11 04:00 | 55.52 | -51.14
2017-06-11 04:30 | 52.57 | -47.71
2017-06-11 05:00 | 51.54 | -46.35
2017-06-11 05:30 | 45.11 | -37.81
2017-06-11 06:00 | 36.8 | -25.34
2017-06-11 06:30 | 33.46 | -17.55
2017-06-11 07:00 | 28.48 | -3.68
2017-06-11 07:30 | 35.69 | 18.07
2017-06-11 08:00 | 46.47 | 33.76
2017-06-11 08:30 | 66.99 | 60.16
2017-06-11 09:00 | 69.03 | 63.56
2017-06-11 09:30 | 54.5 | 49.4
2017-06-11 10:00 | 43.86 | 43.72
2017-06-11 10:30 | 46.72 | 46.64
2017-06-11 11:00 | 51.74 | 51.64
2017-06-11 11:30 | 59.76 | 59.69
2017-06-11 12:00 | 88.24 | 88.17
2017-06-11 12:30 | 80.29 | 80.1
2017-06-11 13:00 | 72.02 | 71.76
2017-06-11 13:30 | 68.23 | 68.01
2017-06-11 14:00 | 72.36 | 72.14
2017-06-11 14:30 | 86.88 | 86.73
2017-06-11 15:00 | 81.77 | 81.61
2017-06-11 15:30 | 95.11 | 94.95
2017-06-11 16:00 | 109.52 | 109.4
2017-06-11 16:30 | 124.96 | 124.93
2017-06-11 17:00 | 163.03 | 163.03
2017-06-11 17:30 | 201.68 | 201.29
2017-06-11 18:00 | 205.57 | 204.96
2017-06-11 18:30 | 206.93 | 206.48
2017-06-11 19:00 | 199.66 | 199.34
2017-06-11 19:30 | 175.72 | 175.29
2017-06-11 20:00 | 167.34 | 165.85
2017-06-11 20:30 | 152.28 | 151.56
2017-06-11 21:00 | 138.14 | 137.96
2017-06-11 21:30 | 135.84 | 135.77
2017-06-11 22:00 | 113.64 | 113.63
2017-06-11 22:30 | 122.38 | 122.38
2017-06-11 23:00 | 118.55 | 118.55
2017-06-11 23:30 | 91.31 | 91.29
2017-06-12 | 59.09 | 59.05
2017-06-12 00:30 | 26.55 | 26.51
2017-06-12 01:00 | 0.76 | -0.08
2017-06-12 01:30 | 28.69 | -28.69
2017-06-12 02:00 | 46.96 | -46.95
2017-06-12 02:30 | 53.01 | -53
2017-06-12 03:00 | 74.76 | -74.44
2017-06-12 03:30 | 85.26 | -84.69
2017-06-12 04:00 | 77.45 | -77.13
2017-06-12 04:30 | 54.29 | -54.29
2017-06-12 05:00 | 48.71 | -48.71
2017-06-12 05:30 | 20.73 | -20.7
2017-06-12 06:00 | 20.54 | 20.51
2017-06-12 06:30 | 65.84 | 65.69
2017-06-12 07:00 | 111.82 | 111.78
2017-06-12 07:30 | 135.3 | 135.15
2017-06-12 08:00 | 136.13 | 135.88
2017-06-12 08:30 | 110.8 | 109.93
2017-06-12 09:00 | 58.96 | 50.86
2017-06-12 09:30 | 40.42 | 26.57
2017-06-12 10:00 | 34.79 | 17.32
2017-06-12 10:30 | 39.84 | 25.69
2017-06-12 11:00 | 41.55 | 29.08
2017-06-12 11:30 | 33.87 | 17.39
2017-06-12 12:00 | 27.99 | 1.17
2017-06-12 12:30 | 27.44 | -3.34
2017-06-12 13:00 | 27.9 | 4.11
2017-06-12 13:30 | 33.06 | 18.06
2017-06-12 14:00 | 35.82 | 22.81
2017-06-12 14:30 | 34.09 | 18.72
2017-06-12 15:00 | 39.16 | 26.84
2017-06-12 15:30 | 56.77 | 49.6
2017-06-12 16:00 | 73.17 | 68.15
2017-06-12 16:30 | 75.19 | 70.18
2017-06-12 17:00 | 89.26 | 80.73
2017-06-12 17:30 | 117.63 | 114.62
2017-06-12 18:00 | 126.35 | 124.97
2017-06-12 18:30 | 126.51 | 126.29
2017-06-12 19:00 | 128.17 | 128.14
2017-06-12 19:30 | 123.3 | 123.1
2017-06-12 20:00 | 104.22 | 103.05
2017-06-12 20:30 | 99.95 | 98.48
2017-06-12 21:00 | 84.79 | 84.57
2017-06-12 21:30 | 55.25 | 54.67
2017-06-12 22:00 | 13.61 | 8.66
2017-06-12 22:30 | 16.26 | 11.24
2017-06-12 23:00 | 14.39 | 8.55
2017-06-12 23:30 | 12.56 | 1.95
2017-06-13 | 13.62 | -3.98
2017-06-13 00:30 | 18.04 | -10.28
2017-06-13 01:00 | 34.67 | -22.85
2017-06-13 01:30 | 40.26 | -31.05
2017-06-13 02:00 | 43.49 | -35.51
2017-06-13 02:30 | 43.51 | -35.24
2017-06-13 03:00 | 44 | -36.05
2017-06-13 03:30 | 47.59 | -40.76
2017-06-13 04:00 | 60.01 | -58
2017-06-13 04:30 | 51.95 | -49.51
2017-06-13 05:00 | 59.91 | -58.38
2017-06-13 05:30 | 39.98 | -32.08
2017-06-13 06:00 | 27.95 | -14.16
2017-06-13 06:30 | 16.7 | 3.83
2017-06-13 07:00 | 39.72 | 39.6
2017-06-13 07:30 | 67.66 | 67.65
2017-06-13 08:00 | 55.77 | 55.73
2017-06-13 08:30 | 36.81 | 33.32
2017-06-13 09:00 | 33.23 | 25.69
2017-06-13 09:30 | 33.1 | 24.55
2017-06-13 10:00 | 45.63 | 39.48
2017-06-13 10:30 | 55.44 | 50.15
2017-06-13 11:00 | 55.89 | 50.44
2017-06-13 11:30 | 54.76 | 49.33
2017-06-13 12:00 | 71.84 | 67.43
2017-06-13 12:30 | 78.74 | 74.97
2017-06-13 13:00 | 76.16 | 72.31
2017-06-13 13:30 | 73.38 | 69.39
2017-06-13 14:00 | 61.56 | 57.12
2017-06-13 14:30 | 60.29 | 55.7
2017-06-13 15:00 | 62.69 | 58.42
2017-06-13 15:30 | 58.22 | 54.04
2017-06-13 16:00 | 56.94 | 52.75
2017-06-13 16:30 | 77.56 | 74.56
2017-06-13 17:00 | 116.16 | 114.07
2017-06-13 17:30 | 128.62 | 123.71
2017-06-13 18:00 | 105.74 | 100.63
2017-06-13 18:30 | 96.49 | 91
2017-06-13 19:00 | 91.23 | 87.26
2017-06-13 19:30 | 80.62 | 80.34
2017-06-13 20:00 | 69.59 | 69.4
2017-06-13 20:30 | 39.15 | 38.99
2017-06-13 21:00 | 35.01 | 34.08
2017-06-13 21:30 | 28.9 | 21.56
2017-06-13 22:00 | 21.79 | -5.96
2017-06-13 22:30 | 21.21 | -0.39
2017-06-13 23:00 | 3.3 | -0.53
2017-06-13 23:30 | 19.88 | -3.64
2017-06-14 | 28.71 | -12.53
2017-06-14 00:30 | 35.86 | -26.85
2017-06-14 01:00 | 39.57 | -32.6
2017-06-14 01:30 | 57.34 | -55.05
2017-06-14 02:00 | 70.03 | -69.6
2017-06-14 02:30 | 72.88 | -72.87
2017-06-14 03:00 | 74.27 | -74.23
2017-06-14 03:30 | 73.39 | -73.35
2017-06-14 04:00 | 63.84 | -63.66
2017-06-14 04:30 | 41.87 | -34.6
2017-06-14 05:00 | 65.66 | -65.07
2017-06-14 05:30 | 42.27 | -35.16
2017-06-14 06:00 | 33.28 | -23.11
2017-06-14 06:30 | 17.58 | -15.89
2017-06-14 07:00 | 5.53 | 1.66
2017-06-14 07:30 | 48.98 | 48.97
2017-06-14 08:00 | 57.57 | 57.54
2017-06-14 08:30 | 49.67 | 49.57
2017-06-14 09:00 | 25.16 | 24.72
2017-06-14 09:30 | 29.23 | 28.71
2017-06-14 10:00 | 29.9 | 29.15
2017-06-14 10:30 | 31.44 | 30.33
2017-06-14 11:00 | 26.93 | 25.53
2017-06-14 11:30 | 15.98 | 13.32
2017-06-14 12:00 | 10.22 | -4.55
2017-06-14 12:30 | 22.55 | -21.26
2017-06-14 13:00 | 14.24 | -12.44
2017-06-14 13:30 | 14.58 | -12.93
2017-06-14 14:00 | 17.51 | -16.14
2017-06-14 14:30 | 10.1 | -7.35
2017-06-14 15:00 | 13.49 | -11.99
2017-06-14 15:30 | 12.34 | -11.18
2017-06-14 16:00 | 5.85 | 3.03
2017-06-14 16:30 | 20 | 19.29
2017-06-14 17:00 | 69.33 | 68.83
2017-06-14 17:30 | 81.05 | 76
2017-06-14 18:00 | 72.88 | 67.03
2017-06-14 18:30 | 70.75 | 65.81
2017-06-14 19:00 | 78.03 | 75.83
2017-06-14 19:30 | 87.13 | 86.95
2017-06-14 20:00 | 83.11 | 81.79
2017-06-14 20:30 | 53.99 | 52.87
2017-06-14 21:00 | 32.65 | 30.18
2017-06-14 21:30 | 23.92 | 18.9
2017-06-14 22:00 | 15.39 | 5.05
2017-06-14 22:30 | 18.07 | 12.46
2017-06-14 23:00 | 27.14 | 21.73
2017-06-14 23:30 | 12.97 | -0.88
2017-06-15 | 28.7 | -17.66
2017-06-15 00:30 | 33.09 | -22.74
2017-06-15 01:00 | 35.61 | -27.7
2017-06-15 01:30 | 39.14 | -33.09
2017-06-15 02:00 | 42.93 | -37.88
2017-06-15 02:30 | 46.15 | -41.89
2017-06-15 03:00 | 46.58 | -42.51
2017-06-15 03:30 | 48.22 | -44.73
2017-06-15 04:00 | 54.85 | -52.64
2017-06-15 04:30 | 54.26 | -51.91
2017-06-15 05:00 | 44.42 | -38.26
2017-06-15 05:30 | 37.71 | -27.78
2017-06-15 06:00 | 28.86 | -14.69
2017-06-15 06:30 | 20.34 | -1.04
2017-06-15 07:00 | 44.77 | 40.07
2017-06-15 07:30 | 73.47 | 73.16
2017-06-15 08:00 | 58.47 | 56.9
2017-06-15 08:30 | 60.02 | 58.53
2017-06-15 09:00 | 46.47 | 44.81
2017-06-15 09:30 | 28.03 | 25.31
2017-06-15 10:00 | 22.51 | 19.11
2017-06-15 10:30 | 20.93 | 17.87
2017-06-15 11:00 | 21.79 | 19.1
2017-06-15 11:30 | 16.65 | 14.68
2017-06-15 12:00 | 17.74 | 16.83
2017-06-15 12:30 | 11.49 | 9.83
2017-06-15 13:00 | 7.3 | -2.81
2017-06-15 13:30 | 18.97 | 17.47
2017-06-15 14:00 | 25.86 | 24.68
2017-06-15 14:30 | 32.65 | 31.65
2017-06-15 15:00 | 30.42 | 29.34
2017-06-15 15:30 | 23.46 | 21.59
2017-06-15 16:00 | 22.8 | 20.92
2017-06-15 16:30 | 49.28 | 48.82
2017-06-15 17:00 | 80.25 | 80.04
2017-06-15 17:30 | 117.3 | 117.27
2017-06-15 18:00 | 132.23 | 132.13
2017-06-15 18:30 | 124.52 | 124.29
2017-06-15 19:00 | 117.28 | 117.09
2017-06-15 19:30 | 104.14 | 103.84
2017-06-15 20:00 | 90.46 | 89.28
2017-06-15 20:30 | 81.84 | 80.67
2017-06-15 21:00 | 57.85 | 56.39
2017-06-15 21:30 | 44.85 | 44.78
2017-06-15 22:00 | 34.63 | 33.86
2017-06-15 22:30 | 42.78 | 42.36
2017-06-15 23:00 | 47.65 | 46.73
2017-06-15 23:30 | 18.44 | 15.69
2017-06-16 | 21.24 | -8.44
2017-06-16 00:30 | 22.23 | -13.93
2017-06-16 01:00 | 30.42 | -27.08
2017-06-16 01:30 | 36.51 | -34.43
2017-06-16 02:00 | 43.51 | -42.48
2017-06-16 02:30 | 43.85 | -42.86
2017-06-16 03:00 | 46.14 | -45.53
2017-06-16 03:30 | 48.21 | -47.78
2017-06-16 04:00 | 44.04 | -43.35
2017-06-16 04:30 | 31.67 | -28.37
2017-06-16 05:00 | 29.76 | -24.77
2017-06-16 05:30 | 23.76 | -12.67
2017-06-16 06:00 | 21.9 | 6.01
2017-06-16 06:30 | 23.7 | 15.77
2017-06-16 07:00 | 26.66 | 26.45
2017-06-16 07:30 | 45.44 | 45.08
2017-06-16 08:00 | 20.63 | 15.58
2017-06-16 08:30 | 9.84 | -1.49
2017-06-16 09:00 | 8.86 | 0.99
2017-06-16 09:30 | 5.64 | -3.64
2017-06-16 10:00 | 7.17 | -6.93
2017-06-16 10:30 | 5.14 | -4.43
2017-06-16 11:00 | 8.5 | -8.09
2017-06-16 11:30 | 3.41 | -0.89
2017-06-16 12:00 | 11.03 | 9.83
2017-06-16 12:30 | 11.5 | 9.91
2017-06-16 13:00 | 6.56 | 0.28
2017-06-16 13:30 | 8.94 | 6.87
2017-06-16 14:00 | 6.21 | 2.15
2017-06-16 14:30 | 7.45 | 4.76
2017-06-16 15:00 | 22.58 | 21.46
2017-06-16 15:30 | 21.29 | 19.52
2017-06-16 16:00 | 34.7 | 33.7
2017-06-16 16:30 | 31.6 | 30.59
2017-06-16 17:00 | 40.36 | 39.92
2017-06-16 17:30 | 73.71 | 73.71
2017-06-16 18:00 | 88.5 | 88.38
2017-06-16 18:30 | 84.12 | 83.99
2017-06-16 19:00 | 81.72 | 81.59
2017-06-16 19:30 | 76.18 | 76.04
2017-06-16 20:00 | 71.26 | 71.22
2017-06-16 20:30 | 63.77 | 63.25
2017-06-16 21:00 | 60 | 59.48
2017-06-16 21:30 | 50.29 | 49.31
2017-06-16 22:00 | 43.26 | 41.83
2017-06-16 22:30 | 40.68 | 40.63
2017-06-16 23:00 | 43.93 | 43.79
2017-06-16 23:30 | 28.77 | 28.41
2017-06-17 | 22.15 | 20.79
2017-06-17 00:30 | 20.13 | 18.51
2017-06-17 01:00 | 22.63 | 21.53
2017-06-17 01:30 | 9.44 | 7.97
2017-06-17 02:00 | 5.38 | 1.57
2017-06-17 02:30 | 6.39 | -3.99
2017-06-17 03:00 | 8.31 | -6.94
2017-06-17 03:30 | 24.8 | -24.8
2017-06-17 04:00 | 34.26 | -34.2
2017-06-17 04:30 | 21.51 | -21.38
2017-06-17 05:00 | 18.32 | -17.96
2017-06-17 05:30 | 14.68 | -14.12
2017-06-17 06:00 | 6.34 | -2.92
2017-06-17 06:30 | 11.17 | 8.66
2017-06-17 07:00 | 19.75 | 17.98
2017-06-17 07:30 | 30.25 | 29.41
2017-06-17 08:00 | 41.55 | 41.42
2017-06-17 08:30 | 56.17 | 56.17
2017-06-17 09:00 | 63.15 | 63.07
2017-06-17 09:30 | 66.73 | 66.58
2017-06-17 10:00 | 24.23 | 23.72
2017-06-17 10:30 | 7.96 | 5.91
2017-06-17 11:00 | 8.12 | 6.09
2017-06-17 11:30 | 6.04 | 1.03
2017-06-17 12:00 | 8.23 | -6.09
2017-06-17 12:30 | 14.08 | -13.47
2017-06-17 13:00 | 23.12 | -22.71
2017-06-17 13:30 | 2.34 | -0.81
2017-06-17 14:00 | 4.01 | 3.47
2017-06-17 14:30 | 3.5 | 2
2017-06-17 15:00 | 5.45 | 4.99
2017-06-17 15:30 | 5.33 | 4.96
2017-06-17 16:00 | 5.21 | 4.96
2017-06-17 16:30 | 9.7 | 9.24
2017-06-17 17:00 | 20.4 | 19.51
2017-06-17 17:30 | 26.84 | 24.29
2017-06-17 18:00 | 33.38 | 18.35
2017-06-17 18:30 | 26.09 | 18.77
2017-06-17 19:00 | 25.49 | 24.32
2017-06-17 19:30 | 28.38 | 28.15
2017-06-17 20:00 | 29.46 | 29.21
2017-06-17 20:30 | 30.94 | 29.78
2017-06-17 21:00 | 30.59 | 29.67
2017-06-17 21:30 | 33.99 | 33.94
2017-06-17 22:00 | 22.58 | 22.27
2017-06-17 22:30 | 28.35 | 28.05
2017-06-17 23:00 | 34.31 | 33.68
2017-06-17 23:30 | 19.71 | 18.04
2017-06-18 | 10.25 | 4.42
2017-06-18 00:30 | 14.76 | -5.87
2017-06-18 01:00 | 27.97 | -18.85
2017-06-18 01:30 | 31.85 | -25.42
2017-06-18 02:00 | 38.17 | -34.28
2017-06-18 02:30 | 38.4 | -34.57
2017-06-18 03:00 | 39.91 | -37.93
2017-06-18 03:30 | 36.71 | -33.37
2017-06-18 04:00 | 36.68 | -33.3
2017-06-18 04:30 | 40.79 | -39.08
2017-06-18 05:00 | 41.14 | -39.4
2017-06-18 05:30 | 37.41 | -34.32
2017-06-18 06:00 | 35.74 | -31.99
2017-06-18 06:30 | 32.27 | -26.49
2017-06-18 07:00 | 28.9 | -21.72
2017-06-18 07:30 | 28.42 | -21.5
2017-06-18 08:00 | 26.3 | -17.66
2017-06-18 08:30 | 24.26 | -14.08
2017-06-18 09:00 | 21.26 | -10.61
2017-06-18 09:30 | 21.88 | -14.48
2017-06-18 10:00 | 24.79 | -19.69
2017-06-18 10:30 | 28.74 | -24.75
2017-06-18 11:00 | 34.51 | -31.34
2017-06-18 11:30 | 41.01 | -38.61
2017-06-18 12:00 | 43.31 | -41.02
2017-06-18 12:30 | 46.38 | -44.35
2017-06-18 13:00 | 46.07 | -44.09
2017-06-18 13:30 | 42.11 | -39.89
2017-06-18 14:00 | 37.52 | -36.84
2017-06-18 14:30 | 34.76 | -34.74
2017-06-18 15:00 | 29.38 | -29.38
2017-06-18 15:30 | 18.48 | -18.47
2017-06-18 16:00 | 2.32 | -1.83
2017-06-18 16:30 | 28.78 | 28.76
2017-06-18 17:00 | 36.99 | 33.34
2017-06-18 17:30 | 63.82 | 63.27
2017-06-18 18:00 | 78.14 | 77.68
2017-06-18 18:30 | 69.71 | 69.29
2017-06-18 19:00 | 81.06 | 80.88
2017-06-18 19:30 | 60.4 | 60.3
2017-06-18 20:00 | 60.94 | 60.33
2017-06-18 20:30 | 59.98 | 58.92
2017-06-18 21:00 | 54.45 | 52.48
2017-06-18 21:30 | 44.59 | 39.68
2017-06-18 22:00 | 32.95 | 24.5
2017-06-18 22:30 | 35.54 | 26.95
2017-06-18 23:00 | 34.13 | 23.75
2017-06-18 23:30 | 25.91 | 6
2017-06-19 | 24.3 | -5.93
2017-06-19 00:30 | 26.55 | -15.26
2017-06-19 01:00 | 30.99 | -24.39
2017-06-19 01:30 | 35.9 | -31.72
2017-06-19 02:00 | 39.82 | -36.7
2017-06-19 02:30 | 41.74 | -39.29
2017-06-19 03:00 | 42.33 | -40.24
2017-06-19 03:30 | 45.75 | -44.64
2017-06-19 04:00 | 47.4 | -46.76
2017-06-19 04:30 | 46.59 | -45.91
2017-06-19 05:00 | 42.86 | -41.52
2017-06-19 05:30 | 35.25 | -29.47
2017-06-19 06:00 | 27.11 | -15.72
2017-06-19 06:30 | 15.41 | 0.65
2017-06-19 07:00 | 26.47 | 23.1
2017-06-19 07:30 | 59.5 | 57.45
2017-06-19 08:00 | 49.41 | 45.35
2017-06-19 08:30 | 28.22 | 17.11
2017-06-19 09:00 | 30.07 | 19.02
2017-06-19 09:30 | 25.34 | 3.15
2017-06-19 10:00 | 25.27 | -3.02
2017-06-19 10:30 | 25.09 | -1.17
2017-06-19 11:00 | 26.89 | -5.91
2017-06-19 11:30 | 27.44 | 0.32
2017-06-19 12:00 | 28.37 | 9.02
2017-06-19 12:30 | 27.05 | 10.26
2017-06-19 13:00 | 37.02 | 28.39
2017-06-19 13:30 | 27.99 | 14.29
2017-06-19 14:00 | 24.69 | -3.81
2017-06-19 14:30 | 24.32 | -3.62
2017-06-19 15:00 | 26.71 | 12.65
2017-06-19 15:30 | 35.43 | 27.04
2017-06-19 16:00 | 40.65 | 33.72
2017-06-19 16:30 | 50.08 | 44.89
2017-06-19 17:00 | 73.93 | 73.33
2017-06-19 17:30 | 111.25 | 110.28
2017-06-19 18:00 | 126.4 | 125.32
2017-06-19 18:30 | 114.23 | 113.3
2017-06-19 19:00 | 118.8 | 118.22
2017-06-19 19:30 | 96.4 | 96.07
2017-06-19 20:00 | 85.87 | 85.75
2017-06-19 20:30 | 82.46 | 82.12
2017-06-19 21:00 | 63.45 | 62.46
2017-06-19 21:30 | 54.87 | 53.18
2017-06-19 22:00 | 47.38 | 43.29
2017-06-19 22:30 | 39.85 | 33.4
2017-06-19 23:00 | 44.04 | 37.1
2017-06-19 23:30 | 30.73 | 19.42
2017-06-20 | 22.75 | -4.06
2017-06-20 00:30 | 25.91 | -16.5
2017-06-20 01:00 | 31.18 | -26.15
2017-06-20 01:30 | 36.7 | -33.7
2017-06-20 02:00 | 42.57 | -40.61
2017-06-20 02:30 | 44.52 | -42.91
2017-06-20 03:00 | 42.13 | -39.81
2017-06-20 03:30 | 43.14 | -40.85
2017-06-20 04:00 | 43.99 | -42.38
2017-06-20 04:30 | 39.3 | -35.85
2017-06-20 05:00 | 36.43 | -30.93
2017-06-20 05:30 | 30.99 | -21.08
2017-06-20 06:00 | 17.1 | -6.43
2017-06-20 06:30 | 26.18 | 25.54
2017-06-20 07:00 | 64.44 | 64.18
2017-06-20 07:30 | 79.83 | 79.82
2017-06-20 08:00 | 79.67 | 79.64
2017-06-20 08:30 | 65.85 | 65.3
2017-06-20 09:00 | 53.87 | 48.56
2017-06-20 09:30 | 42.8 | 36.32
2017-06-20 10:00 | 48.11 | 42.66
2017-06-20 10:30 | 26.25 | 12.92
2017-06-20 11:00 | 24.8 | 8.61
2017-06-20 11:30 | 29.28 | 18.9
2017-06-20 12:00 | 26.72 | 15.95
2017-06-20 12:30 | 27.32 | 16.43
2017-06-20 13:00 | 28.51 | 17.85
2017-06-20 13:30 | 34.42 | 26.26
2017-06-20 14:00 | 32.88 | 27.04
2017-06-20 14:30 | 29.37 | 22.46
2017-06-20 15:00 | 30.45 | 24.21
2017-06-20 15:30 | 37.32 | 33.11
2017-06-20 16:00 | 46.38 | 43.15
2017-06-20 16:30 | 60.34 | 57.64
2017-06-20 17:00 | 77.83 | 75.73
2017-06-20 17:30 | 97.53 | 96.22
2017-06-20 18:00 | 107.31 | 106.83
2017-06-20 18:30 | 98.06 | 97.72
2017-06-20 19:00 | 98.29 | 98.13
2017-06-20 19:30 | 73.58 | 73.23
2017-06-20 20:00 | 60.29 | 58.99
2017-06-20 20:30 | 62.42 | 60.62
2017-06-20 21:00 | 63.05 | 59.93
2017-06-20 21:30 | 73.67 | 69.77
2017-06-20 22:00 | 43.56 | 35.82
2017-06-20 22:30 | 40.34 | 30.16
2017-06-20 23:00 | 53.47 | 45.31
2017-06-20 23:30 | 40.32 | 27.63
2017-06-21 | 28.13 | -4.5
2017-06-21 00:30 | 30.77 | -15.1
2017-06-21 01:00 | 37.87 | -28.51
2017-06-21 01:30 | 42.85 | -35.65
2017-06-21 02:00 | 52.57 | -49.05
2017-06-21 02:30 | 68.86 | -68.64
2017-06-21 03:00 | 67.61 | -67.27
2017-06-21 03:30 | 73.05 | -73.03
2017-06-21 04:00 | 70.37 | -70.34
2017-06-21 04:30 | 67.54 | -67.46
2017-06-21 05:00 | 51.86 | -48
2017-06-21 05:30 | 35.4 | -20.38
2017-06-21 06:00 | 28.98 | -2.68
2017-06-21 06:30 | 29.13 | 15.03
2017-06-21 07:00 | 39 | 35.88
2017-06-21 07:30 | 69.83 | 68.77
2017-06-21 08:00 | 56.47 | 54.58
2017-06-21 08:30 | 40.42 | 36.98
2017-06-21 09:00 | 25.2 | 17.81
2017-06-21 09:30 | 22.11 | 12.27
2017-06-21 10:00 | 20.09 | 4.8
2017-06-21 10:30 | 22.22 | -9.04
2017-06-21 11:00 | 26.38 | -16.4
2017-06-21 11:30 | 30.22 | -22.75
2017-06-21 12:00 | 29 | -21.57
2017-06-21 12:30 | 25.14 | -16.75
2017-06-21 13:00 | 16.81 | 1.05
2017-06-21 13:30 | 18.21 | -5.99
2017-06-21 14:00 | 20.52 | -12.96
2017-06-21 14:30 | 19.88 | -11.36
2017-06-21 15:00 | 20.14 | -6.59
2017-06-21 15:30 | 19.72 | -6.99
2017-06-21 16:00 | 23.58 | 16.57
2017-06-21 16:30 | 41.38 | 38.17
2017-06-21 17:00 | 72.41 | 70.36
2017-06-21 17:30 | 109.15 | 108.01
2017-06-21 18:00 | 126.36 | 126.02
2017-06-21 18:30 | 124.44 | 124.28
2017-06-21 19:00 | 111.26 | 111.25
2017-06-21 19:30 | 93.94 | 93.72
2017-06-21 20:00 | 81.55 | 81.02
2017-06-21 20:30 | 72.47 | 71.55
2017-06-21 21:00 | 59.93 | 59.29
2017-06-21 21:30 | 56.74 | 56.46
2017-06-21 22:00 | 47.92 | 46.48
2017-06-21 22:30 | 44.81 | 43.13
2017-06-21 23:00 | 61.21 | 59.25
2017-06-21 23:30 | 39.88 | 31.33
2017-06-22 | 22.28 | -4.76
2017-06-22 00:30 | 26.73 | -19.65
2017-06-22 01:00 | 42.73 | -42.03
2017-06-22 01:30 | 59.14 | -59.06
2017-06-22 02:00 | 57.75 | -57.75
2017-06-22 02:30 | 55.71 | -55.63
2017-06-22 03:00 | 54.08 | -53.88
2017-06-22 03:30 | 52.78 | -52.5
2017-06-22 04:00 | 49.73 | -49.33
2017-06-22 04:30 | 39.65 | -36.75
2017-06-22 05:00 | 36.91 | -31.85
2017-06-22 05:30 | 32.13 | -22.3
2017-06-22 06:00 | 24.97 | 4.09
2017-06-22 06:30 | 34.13 | 28.16
2017-06-22 07:00 | 49.83 | 46
2017-06-22 07:30 | 79.88 | 79.55
2017-06-22 08:00 | 66.05 | 64.66
2017-06-22 08:30 | 53.54 | 52.28
2017-06-22 09:00 | 47.27 | 46.08
2017-06-22 09:30 | 32.04 | 31.01
2017-06-22 10:00 | 14.98 | 12.6
2017-06-22 10:30 | 12.34 | 8.41
2017-06-22 11:00 | 10.78 | -2.53
2017-06-22 11:30 | 10.09 | -5.19
2017-06-22 12:00 | 5.42 | -1.92
2017-06-22 12:30 | 5.71 | 5.12
2017-06-22 13:00 | 9.87 | 9.64
2017-06-22 13:30 | 17.96 | 17.84
2017-06-22 14:00 | 20.35 | 20.22
2017-06-22 14:30 | 22.91 | 22.84
2017-06-22 15:00 | 17.31 | 17.21
2017-06-22 15:30 | 22.77 | 22.68
2017-06-22 16:00 | 44.56 | 44.55
2017-06-22 16:30 | 65.25 | 65.25
2017-06-22 17:00 | 87.11 | 87.11
2017-06-22 17:30 | 105.24 | 104.93
2017-06-22 18:00 | 104.52 | 104.22
2017-06-22 18:30 | 95.41 | 94.93
2017-06-22 19:00 | 98 | 97.37
2017-06-22 19:30 | 94.37 | 93.48
2017-06-22 20:00 | 89.71 | 88.53
2017-06-22 20:30 | 88.84 | 87.2
2017-06-22 21:00 | 58.28 | 54.83
2017-06-22 21:30 | 49.87 | 44.68
2017-06-22 22:00 | 43.04 | 35.16
2017-06-22 22:30 | 43.36 | 35.93
2017-06-22 23:00 | 59.83 | 51.99
2017-06-22 23:30 | 46.1 | 35.39
2017-06-23 | 29.85 | 10.36
2017-06-23 00:30 | 29.06 | -15.69
2017-06-23 01:00 | 34.12 | -25.58
2017-06-23 01:30 | 38.09 | -30.5
2017-06-23 02:00 | 39.3 | -31.48
2017-06-23 02:30 | 40.43 | -32.79
2017-06-23 03:00 | 40.43 | -32.54
2017-06-23 03:30 | 40.69 | -32.8
2017-06-23 04:00 | 37.18 | -26.55
2017-06-23 04:30 | 35.55 | -28.55
2017-06-23 05:00 | 31.17 | -25.83
2017-06-23 05:30 | 24.59 | -12.17
2017-06-23 06:00 | 22.61 | 6.46
2017-06-23 06:30 | 36.25 | 33.69
2017-06-23 07:00 | 66.78 | 65.41
2017-06-23 07:30 | 93.57 | 93.04
2017-06-23 08:00 | 73.96 | 73.52
2017-06-23 08:30 | 102.86 | 102.63
2017-06-23 09:00 | 83.44 | 83.29
2017-06-23 09:30 | 60.2 | 59.73
2017-06-23 10:00 | 52.62 | 51.82
2017-06-23 10:30 | 40.64 | 39.92
2017-06-23 11:00 | 32.45 | 31.9
2017-06-23 11:30 | 28.43 | 27.61
2017-06-23 12:00 | 26.51 | 24.62
2017-06-23 12:30 | 27.62 | 24.29
2017-06-23 13:00 | 37.87 | 34.81
2017-06-23 13:30 | 42.66 | 39.93
2017-06-23 14:00 | 44.89 | 42.29
2017-06-23 14:30 | 48.28 | 45.72
2017-06-23 15:00 | 24.16 | 15.25
2017-06-23 15:30 | 31.41 | 22.92
2017-06-23 16:00 | 51.75 | 46.15
2017-06-23 16:30 | 70.35 | 66.37
2017-06-23 17:00 | 81.61 | 78.86
2017-06-23 17:30 | 109.09 | 108.28
2017-06-23 18:00 | 128.19 | 128.1
2017-06-23 18:30 | 123.12 | 123.09
2017-06-23 19:00 | 123.45 | 123.45
2017-06-23 19:30 | 115.42 | 114.65
2017-06-23 20:00 | 104.32 | 103.37
2017-06-23 20:30 | 104.84 | 104.09
2017-06-23 21:00 | 102.02 | 101.43
2017-06-23 21:30 | 85.6 | 85.16
2017-06-23 22:00 | 74.86 | 74.55
2017-06-23 22:30 | 73.26 | 73.11
2017-06-23 23:00 | 79.82 | 79.78
2017-06-23 23:30 | 52.2 | 52.16
2017-06-24 | 21.16 | 20.95
2017-06-24 00:30 | 7.36 | 4.85
2017-06-24 01:00 | 21.15 | -18.31
2017-06-24 01:30 | 24.92 | -22.88
2017-06-24 02:00 | 27.47 | -25.9
2017-06-24 02:30 | 28.8 | -27.21
2017-06-24 03:00 | 31.17 | -29.81
2017-06-24 03:30 | 32.96 | -31.68
2017-06-24 04:00 | 31.57 | -30.22
2017-06-24 04:30 | 34.7 | -33.51
2017-06-24 05:00 | 33.24 | -31.89
2017-06-24 05:30 | 27.68 | -25.55
2017-06-24 06:00 | 23.27 | -20.27
2017-06-24 06:30 | 16.61 | -12.2
2017-06-24 07:00 | 13.25 | 6.57
2017-06-24 07:30 | 27.59 | 25.66
2017-06-24 08:00 | 22.18 | 21.03
2017-06-24 08:30 | 20.81 | 20.29
2017-06-24 09:00 | 13.2 | 13.06
2017-06-24 09:30 | 1.38 | 0.97
2017-06-24 10:00 | 11.49 | -11.48
2017-06-24 10:30 | 18.74 | -18.74
2017-06-24 11:00 | 15.83 | -15.79
2017-06-24 11:30 | 24.07 | -24.04
2017-06-24 12:00 | 26.82 | -26.78
2017-06-24 12:30 | 26.48 | -26.42
2017-06-24 13:00 | 28.49 | -28.42
2017-06-24 13:30 | 24.28 | -24.2
2017-06-24 14:00 | 25.22 | -25.09
2017-06-24 14:30 | 17.96 | -17.81
2017-06-24 15:00 | 5.79 | -5.24
2017-06-24 15:30 | 12.7 | 12.35
2017-06-24 16:00 | 27.87 | 27.67
2017-06-24 16:30 | 42.2 | 42.06
2017-06-24 17:00 | 68.22 | 67.82
2017-06-24 17:30 | 89.63 | 86.5
2017-06-24 18:00 | 98.9 | 92.68
2017-06-24 18:30 | 100.27 | 92.79
2017-06-24 19:00 | 103.68 | 90.97
2017-06-24 19:30 | 98.07 | 85.32
2017-06-24 20:00 | 101.51 | 90
2017-06-24 20:30 | 87.89 | 86.02
2017-06-24 21:00 | 70.5 | 70.28
2017-06-24 21:30 | 58.99 | 58.54
2017-06-24 22:00 | 36.45 | 35.53
2017-06-24 22:30 | 39.5 | 38.29
2017-06-24 23:00 | 48.81 | 47.43
2017-06-24 23:30 | 28.85 | 25.77
2017-06-25 | 12.89 | 3.52
2017-06-25 00:30 | 15.39 | -10.45
2017-06-25 01:00 | 18.11 | -14.78
2017-06-25 01:30 | 20.56 | -17.42
2017-06-25 02:00 | 21.63 | -18.67
2017-06-25 02:30 | 23 | -18.37
2017-06-25 03:00 | 32.66 | -18.06
2017-06-25 03:30 | 32.68 | -18.67
2017-06-25 04:00 | 31.85 | -18.22
2017-06-25 04:30 | 31.54 | -16.87
2017-06-25 05:00 | 31.45 | -16.34
2017-06-25 05:30 | 31.24 | -15.46
2017-06-25 06:00 | 30.57 | -13.91
2017-06-25 06:30 | 29.72 | -12.63
2017-06-25 07:00 | 28.02 | -11.45
2017-06-25 07:30 | 26.99 | -7.83
2017-06-25 08:00 | 26.98 | -4.54
2017-06-25 08:30 | 24.94 | -1.55
2017-06-25 09:00 | 12.15 | 0.81
2017-06-25 09:30 | 7.29 | 2.35
2017-06-25 10:00 | 6.33 | 2.55
2017-06-25 10:30 | 5.64 | 2.14
2017-06-25 11:00 | 5.37 | -0.34
2017-06-25 11:30 | 6.33 | -2.99
2017-06-25 12:00 | 6.16 | -3.85
2017-06-25 12:30 | 7.2 | -4.99
2017-06-25 13:00 | 6.96 | -4.56
2017-06-25 13:30 | 7.05 | -4.76
2017-06-25 14:00 | 6.41 | -3.51
2017-06-25 14:30 | 5.63 | -1.94
2017-06-25 15:00 | 4.88 | -2.03
2017-06-25 15:30 | 6.61 | 3.38
2017-06-25 16:00 | 12.17 | 10.96
2017-06-25 16:30 | 28.5 | 25.83
2017-06-25 17:00 | 48.42 | 38.2
2017-06-25 17:30 | 53.66 | 41.49
2017-06-25 18:00 | 58.12 | 42.97
2017-06-25 18:30 | 57.51 | 43.09
2017-06-25 19:00 | 58.62 | 45.62
2017-06-25 19:30 | 56.87 | 45.47
2017-06-25 20:00 | 56.36 | 46.46
2017-06-25 20:30 | 56.16 | 47.42
2017-06-25 21:00 | 50.82 | 42.34
2017-06-25 21:30 | 44.82 | 36.14
2017-06-25 22:00 | 38.39 | 29.78
2017-06-25 22:30 | 36.18 | 33.59
2017-06-25 23:00 | 43.27 | 40.45
2017-06-25 23:30 | 33.04 | 28.92
2017-06-26 | 21.35 | 16.21
2017-06-26 00:30 | 15.19 | 8.66
2017-06-26 01:00 | 12.31 | 1.98
2017-06-26 01:30 | 11.79 | -2.38
2017-06-26 02:00 | 10.88 | -0.61
2017-06-26 02:30 | 27.48 | 2.12
2017-06-26 03:00 | 27.94 | 3.38
2017-06-26 03:30 | 28.49 | 4.1
2017-06-26 04:00 | 29.5 | 6.18
2017-06-26 04:30 | 30.58 | 6.22
2017-06-26 05:00 | 31.32 | 8.47
2017-06-26 05:30 | 30.51 | 9.94
2017-06-26 06:00 | 33.29 | 15.89
2017-06-26 06:30 | 26.48 | 22.71
2017-06-26 07:00 | 32.2 | 31.71
2017-06-26 07:30 | 41.82 | 41.31
2017-06-26 08:00 | 44.26 | 44.12
2017-06-26 08:30 | 45.98 | 45.71
2017-06-26 09:00 | 48.63 | 48.13
2017-06-26 09:30 | 44.12 | 43.41
2017-06-26 10:00 | 43.26 | 42.41
2017-06-26 10:30 | 38.7 | 37.56
2017-06-26 11:00 | 35.76 | 34.71
2017-06-26 11:30 | 32.81 | 31.58
2017-06-26 12:00 | 32.02 | 30.88
2017-06-26 12:30 | 31.22 | 30.11
2017-06-26 13:00 | 32.19 | 31.21
2017-06-26 13:30 | 31.8 | 31.07
2017-06-26 14:00 | 32.94 | 32.37
2017-06-26 14:30 | 35.31 | 34.88
2017-06-26 15:00 | 36.64 | 36.38
2017-06-26 15:30 | 39.33 | 39.18
2017-06-26 16:00 | 60.32 | 60.26
2017-06-26 16:30 | 92.56 | 92.54
2017-06-26 17:00 | 100.37 | 100.35
2017-06-26 17:30 | 135.6 | 132.15
2017-06-26 18:00 | 142.29 | 136.44
2017-06-26 18:30 | 137.3 | 131.7
2017-06-26 19:00 | 137.91 | 134.97
2017-06-26 19:30 | 124.31 | 120.88
2017-06-26 20:00 | 123.83 | 119.8
2017-06-26 20:30 | 102.71 | 98.46
2017-06-26 21:00 | 80.03 | 75.11
2017-06-26 21:30 | 65.43 | 65.31
2017-06-26 22:00 | 56.33 | 55.22
2017-06-26 22:30 | 50.61 | 49
2017-06-26 23:00 | 52.63 | 50.67
2017-06-26 23:30 | 32.1 | 28.29
2017-06-27 | 12.04 | 0.79
2017-06-27 00:30 | 17.72 | -14.88
2017-06-27 01:00 | 26.82 | -25.4
2017-06-27 01:30 | 31.54 | -30.58
2017-06-27 02:00 | 32.98 | -32.07
2017-06-27 02:30 | 33.48 | -32.62
2017-06-27 03:00 | 32.73 | -31.8
2017-06-27 03:30 | 32.69 | -31.61
2017-06-27 04:00 | 32.58 | -31.36
2017-06-27 04:30 | 28.04 | -25.94
2017-06-27 05:00 | 26.65 | -24.29
2017-06-27 05:30 | 19.96 | -15.93
2017-06-27 06:00 | 12.3 | 0.5
2017-06-27 06:30 | 19.34 | 10.9
2017-06-27 07:00 | 34.94 | 20.52
2017-06-27 07:30 | 97.62 | 92.71
2017-06-27 08:00 | 124.02 | 117.25
2017-06-27 08:30 | 128.47 | 119.04
2017-06-27 09:00 | 126.4 | 116.1
2017-06-27 09:30 | 123.24 | 112.78
2017-06-27 10:00 | 122.79 | 111.67
2017-06-27 10:30 | 117.88 | 105.95
2017-06-27 11:00 | 118.44 | 105.86
2017-06-27 11:30 | 116.57 | 103.49
2017-06-27 12:00 | 114.69 | 101.33
2017-06-27 12:30 | 116.11 | 103.39
2017-06-27 13:00 | 119.51 | 107.17
2017-06-27 13:30 | 114.52 | 102.38
2017-06-27 14:00 | 122.07 | 110.65
2017-06-27 14:30 | 114.76 | 102.6
2017-06-27 15:00 | 115.31 | 103.67
2017-06-27 15:30 | 113.7 | 102.33
2017-06-27 16:00 | 119.38 | 108.7
2017-06-27 16:30 | 118.69 | 108.84
2017-06-27 17:00 | 107 | 99.84
2017-06-27 17:30 | 111.87 | 103.95
2017-06-27 18:00 | 118.67 | 112.37
2017-06-27 18:30 | 116.18 | 111.02
2017-06-27 19:00 | 115.27 | 110.85
2017-06-27 19:30 | 95.82 | 95.49
2017-06-27 20:00 | 97.21 | 94.71
2017-06-27 20:30 | 103.09 | 100.67
2017-06-27 21:00 | 98.48 | 95.57
2017-06-27 21:30 | 76.61 | 71.9
2017-06-27 22:00 | 57.95 | 50.25
2017-06-27 22:30 | 58.66 | 50.39
2017-06-27 23:00 | 55.59 | 46.31
2017-06-27 23:30 | 46.73 | 36.57
2017-06-28 | 30.43 | 13.27
2017-06-28 00:30 | 27.18 | -10.17
2017-06-28 01:00 | 31.22 | -21.02
2017-06-28 01:30 | 36.8 | -29.91
2017-06-28 02:00 | 39.42 | -33.92
2017-06-28 02:30 | 39.79 | -34.52
2017-06-28 03:00 | 37.65 | -31.85
2017-06-28 03:30 | 39.09 | -33.58
2017-06-28 04:00 | 38.14 | -32.24
2017-06-28 04:30 | 35.64 | -28.06
2017-06-28 05:00 | 34.58 | -25.36
2017-06-28 05:30 | 31.71 | -18.5
2017-06-28 06:00 | 26.85 | -3.01
2017-06-28 06:30 | 22.26 | -0.01
2017-06-28 07:00 | 8.07 | 2.32
2017-06-28 07:30 | 35.97 | 35.97
2017-06-28 08:00 | 41.95 | 41.94
2017-06-28 08:30 | 41.43 | 41.2
2017-06-28 09:00 | 39.82 | 39.33
2017-06-28 09:30 | 32.8 | 32.09
2017-06-28 10:00 | 33.61 | 32.67
2017-06-28 10:30 | 28.68 | 27.88
2017-06-28 11:00 | 28.77 | 28.02
2017-06-28 11:30 | 24.7 | 23.55
2017-06-28 12:00 | 34.74 | 25.83
2017-06-28 12:30 | 44.42 | 36.57
2017-06-28 13:00 | 43.01 | 35.05
2017-06-28 13:30 | 39.98 | 31.08
2017-06-28 14:00 | 41.41 | 33
2017-06-28 14:30 | 42.61 | 34.37
2017-06-28 15:00 | 38.07 | 30.4
2017-06-28 15:30 | 29.07 | 18.98
2017-06-28 16:00 | 46.8 | 32.61
2017-06-28 16:30 | 51.24 | 36.02
2017-06-28 17:00 | 53.95 | 39.48
2017-06-28 17:30 | 52.32 | 43.93
2017-06-28 18:00 | 52.87 | 45.22
2017-06-28 18:30 | 76.76 | 75.28
2017-06-28 19:00 | 107.88 | 107.77
2017-06-28 19:30 | 91.07 | 91.03
2017-06-28 20:00 | 81.97 | 81.96
2017-06-28 20:30 | 93.88 | 92.68
2017-06-28 21:00 | 75.8 | 73.55
2017-06-28 21:30 | 69 | 66.34
2017-06-28 22:00 | 59.99 | 56.96
2017-06-28 22:30 | 54.38 | 47.87
2017-06-28 23:00 | 53.39 | 45.7
2017-06-28 23:30 | 33.29 | 19.47
2017-06-29 | 27.15 | -2.48
2017-06-29 00:30 | 28.46 | -14.8
2017-06-29 01:00 | 31.54 | -21.12
2017-06-29 01:30 | 34.27 | -26.34
2017-06-29 02:00 | 35.03 | -27.48
2017-06-29 02:30 | 37.77 | -31.54
2017-06-29 03:00 | 35.72 | -28.51
2017-06-29 03:30 | 36.41 | -29.33
2017-06-29 04:00 | 35.02 | -26.65
2017-06-29 04:30 | 35.49 | -26.81
2017-06-29 05:00 | 35.44 | -25.55
2017-06-29 05:30 | 34.83 | -23.54
2017-06-29 06:00 | 28.99 | -13.15
2017-06-29 06:30 | 22.87 | -0.75
2017-06-29 07:00 | 34.15 | 25.96
2017-06-29 07:30 | 54.67 | 51.39
2017-06-29 08:00 | 45.31 | 41.52
2017-06-29 08:30 | 36.54 | 32.28
2017-06-29 09:00 | 33.36 | 30.05
2017-06-29 09:30 | 28.32 | 24.09
2017-06-29 10:00 | 26.33 | 23.32
2017-06-29 10:30 | 11.79 | 4.94
2017-06-29 11:00 | 4.93 | 4.51
2017-06-29 11:30 | 7.39 | 5.67
2017-06-29 12:00 | 7.68 | -0.89
2017-06-29 12:30 | 12.04 | 5.69
2017-06-29 13:00 | 16.39 | 13.06
2017-06-29 13:30 | 23.74 | 22.19
2017-06-29 14:00 | 34.69 | 34.15
2017-06-29 14:30 | 38.82 | 38.27
2017-06-29 15:00 | 41.8 | 41.35
2017-06-29 15:30 | 56.47 | 56.28
2017-06-29 16:00 | 73.26 | 73.2
2017-06-29 16:30 | 97.38 | 97.36
2017-06-29 17:00 | 105.65 | 105.65
2017-06-29 17:30 | 123.59 | 123.44
2017-06-29 18:00 | 126.05 | 125.83
2017-06-29 18:30 | 119.14 | 118.69
2017-06-29 19:00 | 138.02 | 137.33
2017-06-29 19:30 | 122.58 | 122.52
2017-06-29 20:00 | 124.28 | 124.16
2017-06-29 20:30 | 131.4 | 131.22
2017-06-29 21:00 | 101.57 | 101.08
2017-06-29 21:30 | 81.93 | 81.03
2017-06-29 22:00 | 55.61 | 53.59
2017-06-29 22:30 | 55.62 | 53.1
2017-06-29 23:00 | 64.05 | 61.07
2017-06-29 23:30 | 45 | 39.95
2017-06-30 | 24.26 | 9.37
2017-06-30 00:30 | 27.33 | -14.11
2017-06-30 01:00 | 29.57 | -21.37
2017-06-30 01:30 | 27.33 | -26.19
2017-06-30 02:00 | 29.15 | -27.91
2017-06-30 02:30 | 30.06 | -29.22
2017-06-30 03:00 | 28.13 | -27.19
2017-06-30 03:30 | 33.33 | -27.57
2017-06-30 04:00 | 37.81 | -30.51
2017-06-30 04:30 | 36.94 | -28.67
2017-06-30 05:00 | 35.99 | -26.3
2017-06-30 05:30 | 32.79 | -19.7
2017-06-30 06:00 | 29.54 | -13.52
2017-06-30 06:30 | 25.05 | -7.69
2017-06-30 07:00 | 25.9 | 14.5
2017-06-30 07:30 | 46.01 | 42.63
2017-06-30 08:00 | 41 | 36.63
2017-06-30 08:30 | 28.72 | 24.77
2017-06-30 09:00 | 28.9 | 25.69
2017-06-30 09:30 | 22.17 | 18.29
2017-06-30 10:00 | 27.73 | 25.03
2017-06-30 10:30 | 22.16 | 18.86
2017-06-30 11:00 | 15.45 | 10.56
2017-06-30 11:30 | 6.8 | 4.24
2017-06-30 12:00 | 6.8 | -6.19
2017-06-30 12:30 | 5.85 | -5.57
2017-06-30 13:00 | 1.92 | -1.06
2017-06-30 13:30 | 1.37 | -0.74
2017-06-30 14:00 | 1.46 | 1.02
2017-06-30 14:30 | 3.93 | 3.82
2017-06-30 15:00 | 3.83 | 3.77
2017-06-30 15:30 | 14.6 | 14.6
2017-06-30 16:00 | 30.27 | 30.26
2017-06-30 16:30 | 52.67 | 52.66
2017-06-30 17:00 | 51.31 | 51.3
2017-06-30 17:30 | 63.17 | 62.8
2017-06-30 18:00 | 57.17 | 54.16
2017-06-30 18:30 | 47.06 | 46.07
2017-06-30 19:00 | 54.52 | 53.5
2017-06-30 19:30 | 54.63 | 52.86
2017-06-30 20:00 | 65.08 | 63.14
2017-06-30 20:30 | 45.58 | 42.55
2017-06-30 21:00 | 48.39 | 45.17
2017-06-30 21:30 | 40.1 | 37.8
2017-06-30 22:00 | 29.03 | 28.42
2017-06-30 22:30 | 27.79 | 26.96
2017-06-30 23:00 | 34.83 | 33.77
2017-06-30 23:30 | 21.02 | 13.57
2017-07-01 | 22.02 | -12.43
2017-07-01 00:30 | 21.25 | -15.27
2017-07-01 01:00 | 24.99 | -21.39
2017-07-01 01:30 | 30.06 | -28.28
2017-07-01 02:00 | 34.34 | -33.29
2017-07-01 02:30 | 32.55 | -31.46
2017-07-01 03:00 | 36.05 | -33.84
2017-07-01 03:30 | 40.5 | -36.85
2017-07-01 04:00 | 43.75 | -42.21
2017-07-01 04:30 | 36.34 | -34.73
2017-07-01 05:00 | 33.33 | -30.93
2017-07-01 05:30 | 28.05 | -22.75
2017-07-01 06:00 | 27.47 | -19.33
2017-07-01 06:30 | 29.62 | -19.37
2017-07-01 07:00 | 27.76 | -15.96
2017-07-01 07:30 | 24.42 | -7.66
2017-07-01 08:00 | 21.11 | -6.15
2017-07-01 08:30 | 7.76 | -7.27
2017-07-01 09:00 | 18.17 | -10.15
2017-07-01 09:30 | 19.98 | -13
2017-07-01 10:00 | 21.1 | -14.86
2017-07-01 10:30 | 25.29 | -22.47
2017-07-01 11:00 | 36.22 | -30.19
2017-07-01 11:30 | 40.7 | -35.72
2017-07-01 12:00 | 54.1 | -52.69
2017-07-01 12:30 | 62.89 | -62.32
2017-07-01 13:00 | 68.51 | -68.17
2017-07-01 13:30 | 65.29 | -64.87
2017-07-01 14:00 | 64.67 | -64.51
2017-07-01 14:30 | 61.88 | -61.87
2017-07-01 15:00 | 44.43 | -44.26
2017-07-01 15:30 | 21.93 | -21.88
2017-07-01 16:00 | 5.47 | -5.13
2017-07-01 16:30 | 14.09 | 14.05
2017-07-01 17:00 | 19.72 | 19.53
2017-07-01 17:30 | 38.08 | 37.14
2017-07-01 18:00 | 50.52 | 49.29
2017-07-01 18:30 | 55.56 | 54.53
2017-07-01 19:00 | 65.9 | 65.24
2017-07-01 19:30 | 71.98 | 71.98
2017-07-01 20:00 | 65.35 | 63.92
2017-07-01 20:30 | 44.32 | 42.21
2017-07-01 21:00 | 36.08 | 32.57
2017-07-01 21:30 | 34.97 | 30.19
2017-07-01 22:00 | 36.5 | 30.97
2017-07-01 22:30 | 50.31 | 46.28
2017-07-01 23:00 | 68.28 | 63.09
2017-07-01 23:30 | 52.11 | 45.36
2017-07-02 | 25.82 | 23.43
2017-07-02 00:30 | 20.72 | 3.36
2017-07-02 01:00 | 25.34 | -6.93
2017-07-02 01:30 | 24.65 | -10.36
2017-07-02 02:00 | 26.74 | -16.84
2017-07-02 02:30 | 30.45 | -23.48
2017-07-02 03:00 | 31.27 | -26.21
2017-07-02 03:30 | 34.72 | -31.01
2017-07-02 04:00 | 38.46 | -35.66
2017-07-02 04:30 | 37.32 | -34.04
2017-07-02 05:00 | 39.5 | -37
2017-07-02 05:30 | 32.65 | -30.19
2017-07-02 06:00 | 26.79 | -21.13
2017-07-02 06:30 | 30.01 | -24.55
2017-07-02 07:00 | 27.21 | -20.7
2017-07-02 07:30 | 24.67 | -14.08
2017-07-02 08:00 | 22.84 | -11.2
2017-07-02 08:30 | 32.82 | -32.56
2017-07-02 09:00 | 19.22 | -19.21
2017-07-02 09:30 | 15.11 | -15.07
2017-07-02 10:00 | 22.11 | -21.94
2017-07-02 10:30 | 24.27 | -24.18
2017-07-02 11:00 | 33.69 | -33.67
2017-07-02 11:30 | 34.92 | -34.89
2017-07-02 12:00 | 29.77 | -29.68
2017-07-02 12:30 | 29.28 | -29.19
2017-07-02 13:00 | 34.96 | -34.9
2017-07-02 13:30 | 38.94 | -38.91
2017-07-02 14:00 | 48.48 | -48.48
2017-07-02 14:30 | 54.76 | -54.67
2017-07-02 15:00 | 37.27 | -37.27
2017-07-02 15:30 | 26.04 | -25.99
2017-07-02 16:00 | 17.73 | -17.69
2017-07-02 16:30 | 1.72 | -0.81
2017-07-02 17:00 | 39.24 | 39.24
2017-07-02 17:30 | 72.05 | 72.02
2017-07-02 18:00 | 97.79 | 97.58
2017-07-02 18:30 | 95.15 | 94.81
2017-07-02 19:00 | 98.77 | 98.38
2017-07-02 19:30 | 101.13 | 100.54
2017-07-02 20:00 | 100.34 | 99.64
2017-07-02 20:30 | 77.23 | 76.05
2017-07-02 21:00 | 43.78 | 40.93
2017-07-02 21:30 | 44.47 | 40.01
2017-07-02 22:00 | 36 | 29.83
2017-07-02 22:30 | 47.26 | 40.3
2017-07-02 23:00 | 60.6 | 53.95
2017-07-02 23:30 | 45.65 | 35.51
2017-07-03 | 29.27 | 13.04
2017-07-03 00:30 | 24.71 | -4.76
2017-07-03 01:00 | 28.76 | -17.61
2017-07-03 01:30 | 32.08 | -23.46
2017-07-03 02:00 | 33.25 | -25.25
2017-07-03 02:30 | 49.06 | -48.44
2017-07-03 03:00 | 62.14 | -62.13
2017-07-03 03:30 | 64.65 | -64.64
2017-07-03 04:00 | 63.28 | -63.28
2017-07-03 04:30 | 62.55 | -62.55
2017-07-03 05:00 | 61.97 | -61.88
2017-07-03 05:30 | 36.99 | -32.4
2017-07-03 06:00 | 24.09 | -2.08
2017-07-03 06:30 | 24.22 | 13.91
2017-07-03 07:00 | 24.53 | 21.19
2017-07-03 07:30 | 33.81 | 33.64
2017-07-03 08:00 | 45.96 | 20.84
2017-07-03 08:30 | 43.18 | -1.38
2017-07-03 09:00 | 56.62 | -28.14
2017-07-03 09:30 | 66.29 | -44.12
2017-07-03 10:00 | 76.08 | -56.43
2017-07-03 10:30 | 78.75 | -59.72
2017-07-03 11:00 | 77.75 | -60.06
2017-07-03 11:30 | 83.22 | -66.05
2017-07-03 12:00 | 87.06 | -69.81
2017-07-03 12:30 | 86.87 | -69.82
2017-07-03 13:00 | 80.99 | -63.34
2017-07-03 13:30 | 82.2 | -63.81
2017-07-03 14:00 | 75.7 | -62.09
2017-07-03 14:30 | 60.02 | -52.27
2017-07-03 15:00 | 35.36 | -34.97
2017-07-03 15:30 | 23.97 | -23.95
2017-07-03 16:00 | 11.37 | -8.71
2017-07-03 16:30 | 9.73 | 2.31
2017-07-03 17:00 | 15.8 | 13.38
2017-07-03 17:30 | 62.6 | 62.12
2017-07-03 18:00 | 76.7 | 76.68
2017-07-03 18:30 | 77.9 | 77.9
2017-07-03 19:00 | 77.94 | 77.88
2017-07-03 19:30 | 71.98 | 71.77
2017-07-03 20:00 | 53.06 | 52.78
2017-07-03 20:30 | 29.65 | 28.78
2017-07-03 21:00 | 15.9 | 15.79
2017-07-03 21:30 | 16.79 | 16.64
2017-07-03 22:00 | 16.72 | 3.64
2017-07-03 22:30 | 27.08 | 21.02
2017-07-03 23:00 | 55.04 | 49.56
2017-07-03 23:30 | 59.09 | 51.94
2017-07-04 | 35.06 | 23.29
2017-07-04 00:30 | 24.72 | 0.65
2017-07-04 01:00 | 24.62 | -7
2017-07-04 01:30 | 25.72 | -12.67
2017-07-04 02:00 | 27.36 | -15.61
2017-07-04 02:30 | 23.72 | -16.54
2017-07-04 03:00 | 26.88 | -21.93
2017-07-04 03:30 | 30.35 | -27.46
2017-07-04 04:00 | 24.64 | -20.42
2017-07-04 04:30 | 27.26 | -23.51
2017-07-04 05:00 | 31.15 | -27.5
2017-07-04 05:30 | 25.02 | -15.82
2017-07-04 06:00 | 24.78 | 4.43
2017-07-04 06:30 | 30.74 | 15.82
2017-07-04 07:00 | 36.34 | 36.34
2017-07-04 07:30 | 58.46 | 56.03
2017-07-04 08:00 | 53.46 | 49.9
2017-07-04 08:30 | 50.68 | 45.54
2017-07-04 09:00 | 44.97 | 38.37
2017-07-04 09:30 | 36.92 | 28.56
2017-07-04 10:00 | 36.78 | 27.41
2017-07-04 10:30 | 37.42 | 30.68
2017-07-04 11:00 | 18.71 | 17.46
2017-07-04 11:30 | 19.05 | 11.61
2017-07-04 12:00 | 29.08 | 12.82
2017-07-04 12:30 | 29.72 | 15.21
2017-07-04 13:00 | 30.18 | 16.05
2017-07-04 13:30 | 31.35 | 17.81
2017-07-04 14:00 | 32.47 | 19.8
2017-07-04 14:30 | 33.1 | 20.24
2017-07-04 15:00 | 36.57 | 26.59
2017-07-04 15:30 | 41.85 | 33.5
2017-07-04 16:00 | 50.31 | 44.84
2017-07-04 16:30 | 57.16 | 52.82
2017-07-04 17:00 | 85.02 | 69.79
2017-07-04 17:30 | 89.51 | 66.76
2017-07-04 18:00 | 81.67 | 56.07
2017-07-04 18:30 | 75.26 | 48.31
2017-07-04 19:00 | 83.76 | 62.48
2017-07-04 19:30 | 75.82 | 52.39
2017-07-04 20:00 | 75 | 53.7
2017-07-04 20:30 | 81.86 | 72.97
2017-07-04 21:00 | 63.68 | 55.62
2017-07-04 21:30 | 52.57 | 44.15
2017-07-04 22:00 | 30.32 | 29.39
2017-07-04 22:30 | 31.96 | 30.12
2017-07-04 23:00 | 42.24 | 40.46
2017-07-04 23:30 | 27.79 | 25.07
2017-07-05 | 11.07 | -1.92
2017-07-05 00:30 | 18.53 | -16.76
2017-07-05 01:00 | 27.57 | -26.74
2017-07-05 01:30 | 29.55 | -28.81
2017-07-05 02:00 | 31.01 | -30.25
2017-07-05 02:30 | 32.87 | -32.27
2017-07-05 03:00 | 51.18 | -51.16
2017-07-05 03:30 | 37.07 | -36.49
2017-07-05 04:00 | 32.72 | -31.74
2017-07-05 04:30 | 31.84 | -30.73
2017-07-05 05:00 | 30.2 | -28.9
2017-07-05 05:30 | 21.01 | -18.52
2017-07-05 06:00 | 10.1 | 0.14
2017-07-05 06:30 | 21.9 | 18.09
2017-07-05 07:00 | 41.02 | 35.89
2017-07-05 07:30 | 64.19 | 62.27
2017-07-05 08:00 | 55.08 | 53.34
2017-07-05 08:30 | 44.32 | 42.61
2017-07-05 09:00 | 52.66 | 51.65
2017-07-05 09:30 | 31.48 | 29.82
2017-07-05 10:00 | 16.75 | 14.06
2017-07-05 10:30 | 12.01 | 8.4
2017-07-05 11:00 | 7.84 | 0.8
2017-07-05 11:30 | 8.93 | -5.54
2017-07-05 12:00 | 17.36 | -16.27
2017-07-05 12:30 | 20.09 | -19.15
2017-07-05 13:00 | 24.67 | -23.88
2017-07-05 13:30 | 23.07 | -22.11
2017-07-05 14:00 | 22.57 | -21.38
2017-07-05 14:30 | 19.39 | -18.14
2017-07-05 15:00 | 12.96 | -10.55
2017-07-05 15:30 | 8.43 | 2.47
2017-07-05 16:00 | 26.64 | 24.91
2017-07-05 16:30 | 35.47 | 33.94
2017-07-05 17:00 | 54.6 | 53.88
2017-07-05 17:30 | 47.86 | 45.19
2017-07-05 18:00 | 74.68 | 53.57
2017-07-05 18:30 | 62.75 | 52.27
2017-07-05 19:00 | 52.14 | 45.9
2017-07-05 19:30 | 50.26 | 44.95
2017-07-05 20:00 | 54.62 | 43.31
2017-07-05 20:30 | 55.04 | 43.71
2017-07-05 21:00 | 47.68 | 35.41
2017-07-05 21:30 | 47.29 | 37.16
2017-07-05 22:00 | 33.29 | 22.05
2017-07-05 22:30 | 24.58 | 21.12
2017-07-05 23:00 | 29.44 | 24.48
2017-07-05 23:30 | 10.27 | 3.21
2017-07-06 | 18.77 | -16.71
2017-07-06 00:30 | 28.86 | -28.16
2017-07-06 01:00 | 31.93 | -31.43
2017-07-06 01:30 | 38.57 | -38.2
2017-07-06 02:00 | 49.57 | -49.52
2017-07-06 02:30 | 64.74 | -64.61
2017-07-06 03:00 | 65.15 | -65.03
2017-07-06 03:30 | 65.94 | -65.86
2017-07-06 04:00 | 60.49 | -60.49
2017-07-06 04:30 | 60.52 | -60.52
2017-07-06 05:00 | 38.2 | -37.79
2017-07-06 05:30 | 28.84 | -27.87
2017-07-06 06:00 | 20.1 | -18.46
2017-07-06 06:30 | 9.1 | 4.3
2017-07-06 07:00 | 25.91 | 23.54
2017-07-06 07:30 | 48.46 | 46.42
2017-07-06 08:00 | 48.38 | 46.62
2017-07-06 08:30 | 39.21 | 35.66
2017-07-06 09:00 | 30.34 | 24.61
2017-07-06 09:30 | 21.03 | 11.21
2017-07-06 10:00 | 19.17 | 5.35
2017-07-06 10:30 | 18.41 | -0.51
2017-07-06 11:00 | 24.51 | -15.38
2017-07-06 11:30 | 30.78 | -23.51
2017-07-06 12:00 | 33.76 | -26.89
2017-07-06 12:30 | 33.11 | -26.3
2017-07-06 13:00 | 30.25 | -22.81
2017-07-06 13:30 | 32.51 | -25.81
2017-07-06 14:00 | 31.56 | -24.66
2017-07-06 14:30 | 34.12 | -27.54
2017-07-06 15:00 | 26.29 | -17.99
2017-07-06 15:30 | 21.02 | -9.93
2017-07-06 16:00 | 19.98 | 10.29
2017-07-06 16:30 | 31.4 | 27.09
2017-07-06 17:00 | 51.04 | 48.4
2017-07-06 17:30 | 66.03 | 59.4
2017-07-06 18:00 | 90.23 | 82.1
2017-07-06 18:30 | 90.02 | 82.24
2017-07-06 19:00 | 91.54 | 83.87
2017-07-06 19:30 | 88.7 | 81.88
2017-07-06 20:00 | 87.84 | 81.26
2017-07-06 20:30 | 82.54 | 76.18
2017-07-06 21:00 | 59.22 | 51.3
2017-07-06 21:30 | 41.5 | 32.1
2017-07-06 22:00 | 35.67 | 21.53
2017-07-06 22:30 | 42.84 | 32.66
2017-07-06 23:00 | 46.76 | 46.6
2017-07-06 23:30 | 28.28 | 26.12
2017-07-07 | 12.98 | 7.65
2017-07-07 00:30 | 13.55 | -10.53
2017-07-07 01:00 | 22.92 | -21.8
2017-07-07 01:30 | 32.12 | -31.58
2017-07-07 02:00 | 43.07 | -42.9
2017-07-07 02:30 | 37.81 | -37.6
2017-07-07 03:00 | 61.12 | -61.06
2017-07-07 03:30 | 63.11 | -63.02
2017-07-07 04:00 | 60 | -59.96
2017-07-07 04:30 | 54.46 | -54.46
2017-07-07 05:00 | 48.54 | -48.52
2017-07-07 05:30 | 27.65 | -27.01
2017-07-07 06:00 | 13.16 | -10.89
2017-07-07 06:30 | 14.4 | 13.18
2017-07-07 07:00 | 36.76 | 35.04
2017-07-07 07:30 | 55.18 | 53.8
2017-07-07 08:00 | 39.74 | 39.12
2017-07-07 08:30 | 46.92 | 46.25
2017-07-07 09:00 | 52.15 | 51.08
2017-07-07 09:30 | 49.17 | 47.81
2017-07-07 10:00 | 73.45 | 72.41
2017-07-07 10:30 | 82.42 | 81.57
2017-07-07 11:00 | 73.16 | 72.5
2017-07-07 11:30 | 70.54 | 69.84
2017-07-07 12:00 | 75.83 | 75.18
2017-07-07 12:30 | 76.99 | 76.5
2017-07-07 13:00 | 73.68 | 73.26
2017-07-07 13:30 | 60.01 | 59.51
2017-07-07 14:00 | 60.17 | 59.89
2017-07-07 14:30 | 54.63 | 54.62
2017-07-07 15:00 | 60.4 | 60.4
2017-07-07 15:30 | 60.61 | 60.61
2017-07-07 16:00 | 66.4 | 66.4
2017-07-07 16:30 | 71.17 | 71.13
2017-07-07 17:00 | 76.81 | 76.79
2017-07-07 17:30 | 79.63 | 79.6
2017-07-07 18:00 | 88.26 | 88.11
2017-07-07 18:30 | 92.65 | 92.55
2017-07-07 19:00 | 96.63 | 96.57
2017-07-07 19:30 | 76.99 | 76.96
2017-07-07 20:00 | 67.39 | 67.39
2017-07-07 20:30 | 50.13 | 50.11
2017-07-07 21:00 | 24.59 | 24.45
2017-07-07 21:30 | 24.45 | 23.74
2017-07-07 22:00 | 23.19 | 21.28
2017-07-07 22:30 | 36.93 | 33.16
2017-07-07 23:00 | 44.42 | 43.5
2017-07-07 23:30 | 21.47 | 19.53
2017-07-08 | 11.26 | -7.36
2017-07-08 00:30 | 18.86 | -17.47
2017-07-08 01:00 | 20.86 | -19.86
2017-07-08 01:30 | 22.31 | -21.31
2017-07-08 02:00 | 26.83 | -26.24
2017-07-08 02:30 | 28.27 | -27.46
2017-07-08 03:00 | 30 | -29.31
2017-07-08 03:30 | 29.55 | -28.78
2017-07-08 04:00 | 28.25 | -27.5
2017-07-08 04:30 | 24.94 | -23.13
2017-07-08 05:00 | 25.19 | -22.99
2017-07-08 05:30 | 20.92 | -17.69
2017-07-08 06:00 | 12.68 | -2.23
2017-07-08 06:30 | 14.06 | 6.09
2017-07-08 07:00 | 16.71 | 11.76
2017-07-08 07:30 | 14.68 | 11.36
2017-07-08 08:00 | 13.21 | 12.2
2017-07-08 08:30 | 1.61 | 1.33
2017-07-08 09:00 | 19.59 | -6.1
2017-07-08 09:30 | 24.08 | -14.81
2017-07-08 10:00 | 21.13 | -12
2017-07-08 10:30 | 41.58 | -36.53
2017-07-08 11:00 | 38.03 | -33.14
2017-07-08 11:30 | 27.97 | -23.37
2017-07-08 12:00 | 28.83 | -25.52
2017-07-08 12:30 | 38.05 | -35.47
2017-07-08 13:00 | 35.19 | -32.5
2017-07-08 13:30 | 38.1 | -35.53
2017-07-08 14:00 | 36.76 | -34.2
2017-07-08 14:30 | 34.1 | -31.24
2017-07-08 15:00 | 27.63 | -24.44
2017-07-08 15:30 | 19.32 | -14.44
2017-07-08 16:00 | 15.05 | 8.25
2017-07-08 16:30 | 20.96 | 16.24
2017-07-08 17:00 | 36.62 | 31.54
2017-07-08 17:30 | 64.09 | 39.96
2017-07-08 18:00 | 72.96 | 59.71
2017-07-08 18:30 | 76.91 | 68.21
2017-07-08 19:00 | 73.79 | 70.24
2017-07-08 19:30 | 66.56 | 62.96
2017-07-08 20:00 | 64.96 | 61.28
2017-07-08 20:30 | 75.3 | 67.88
2017-07-08 21:00 | 62.66 | 53.77
2017-07-08 21:30 | 55.93 | 51.92
2017-07-08 22:00 | 46.32 | 45.84
2017-07-08 22:30 | 59.75 | 59.19
2017-07-08 23:00 | 73.82 | 73.21
2017-07-08 23:30 | 58.97 | 58.05
2017-07-09 | 24.68 | 22.44
2017-07-09 00:30 | 11.72 | 7.5
2017-07-09 01:00 | 13.96 | -11.56
2017-07-09 01:30 | 22.29 | -21.11
2017-07-09 02:00 | 26.22 | -25.36
2017-07-09 02:30 | 29.95 | -29.34
2017-07-09 03:00 | 31.45 | -30.94
2017-07-09 03:30 | 30.73 | -30.03
2017-07-09 04:00 | 29.47 | -28.7
2017-07-09 04:30 | 29.57 | -28.78
2017-07-09 05:00 | 31.24 | -30.49
2017-07-09 05:30 | 29.61 | -28.64
2017-07-09 06:00 | 27.69 | -26.53
2017-07-09 06:30 | 26.18 | -24.91
2017-07-09 07:00 | 19.97 | -18.35
2017-07-09 07:30 | 10.79 | -5.32
2017-07-09 08:00 | 14.25 | 10.54
2017-07-09 08:30 | 19.65 | 17.88
2017-07-09 09:00 | 19.07 | 17.83
2017-07-09 09:30 | 12.41 | 10.83
2017-07-09 10:00 | 5.48 | 1.84
2017-07-09 10:30 | 12.55 | -11.76
2017-07-09 11:00 | 23.03 | -22.53
2017-07-09 11:30 | 29.76 | -29.3
2017-07-09 12:00 | 37.31 | -37.02
2017-07-09 12:30 | 40.53 | -40.29
2017-07-09 13:00 | 38.35 | -38.08
2017-07-09 13:30 | 36.91 | -36.65
2017-07-09 14:00 | 34.92 | -34.55
2017-07-09 14:30 | 30.96 | -30.49
2017-07-09 15:00 | 26.34 | -25.65
2017-07-09 15:30 | 19.4 | -18.17
2017-07-09 16:00 | 12.06 | 9.21
2017-07-09 16:30 | 44.01 | 43.42
2017-07-09 17:00 | 72.92 | 72.91
2017-07-09 17:30 | 103.61 | 103.51
2017-07-09 18:00 | 124.5 | 117.3
2017-07-09 18:30 | 111.31 | 103.32
2017-07-09 19:00 | 109.68 | 102.68
2017-07-09 19:30 | 93.18 | 90.9
2017-07-09 20:00 | 87.93 | 85.88
2017-07-09 20:30 | 71.4 | 69.26
2017-07-09 21:00 | 54.2 | 54.18
2017-07-09 21:30 | 51.55 | 46.19
2017-07-09 22:00 | 34.54 | 25.87
2017-07-09 22:30 | 29.4 | 26.98
2017-07-09 23:00 | 28.77 | 26.13
2017-07-09 23:30 | 12.34 | 2.54
2017-07-10 | 16.3 | -13.15
2017-07-10 00:30 | 23.87 | -22.42
2017-07-10 01:00 | 37.28 | -36.92
2017-07-10 01:30 | 60.9 | -60.88
2017-07-10 02:00 | 49.5 | -49.49
2017-07-10 02:30 | 36.68 | -35.91
2017-07-10 03:00 | 41.68 | -41.19
2017-07-10 03:30 | 38.06 | -37.29
2017-07-10 04:00 | 34.51 | -33.38
2017-07-10 04:30 | 45.85 | -45.39
2017-07-10 05:00 | 43.31 | -42.75
2017-07-10 05:30 | 26.54 | -24.56
2017-07-10 06:00 | 14.75 | -9.79
2017-07-10 06:30 | 14.85 | 13.28
2017-07-10 07:00 | 52.05 | 48.96
2017-07-10 07:30 | 73 | 72.39
2017-07-10 08:00 | 75.01 | 72.31
2017-07-10 08:30 | 56.89 | 52.7
2017-07-10 09:00 | 32.01 | 22.31
2017-07-10 09:30 | 26.58 | 9.98
2017-07-10 10:00 | 25.8 | 8.7
2017-07-10 10:30 | 29.22 | 12.05
2017-07-10 11:00 | 41.22 | 13.45
2017-07-10 11:30 | 39.04 | -4.04
2017-07-10 12:00 | 39.01 | -3.15
2017-07-10 12:30 | 39.1 | -7.82
2017-07-10 13:00 | 38.48 | -1.1
2017-07-10 13:30 | 37.63 | -2.08
2017-07-10 14:00 | 40.83 | -11.92
2017-07-10 14:30 | 38.45 | 4.1
2017-07-10 15:00 | 38.4 | 4.72
2017-07-10 15:30 | 38.99 | 13.11
2017-07-10 16:00 | 45.31 | 27.06
2017-07-10 16:30 | 58.19 | 46.88
2017-07-10 17:00 | 72.06 | 68.04
2017-07-10 17:30 | 95.18 | 92.5
2017-07-10 18:00 | 98.42 | 94.71
2017-07-10 18:30 | 96.77 | 92.15
2017-07-10 19:00 | 101.42 | 97.54
2017-07-10 19:30 | 93.39 | 89.79
2017-07-10 20:00 | 78.94 | 75.55
2017-07-10 20:30 | 69.43 | 66.6
2017-07-10 21:00 | 58.01 | 51.49
2017-07-10 21:30 | 49.21 | 38.52
2017-07-10 22:00 | 30.65 | 12.59
2017-07-10 22:30 | 27.38 | 21.07
2017-07-10 23:00 | 46.72 | 45.1
2017-07-10 23:30 | 27.02 | 24.58
2017-07-11 | 11.44 | -7.43
2017-07-11 00:30 | 24.42 | -23.51
2017-07-11 01:00 | 57.23 | -57.2
2017-07-11 01:30 | 65.45 | -65.33
2017-07-11 02:00 | 66.99 | -66.85
2017-07-11 02:30 | 64.64 | -64.53
2017-07-11 03:00 | 62.99 | -62.9
2017-07-11 03:30 | 60.41 | -60.37
2017-07-11 04:00 | 56.11 | -56.11
2017-07-11 04:30 | 47.53 | -47.49
2017-07-11 05:00 | 47.17 | -47.04
2017-07-11 05:30 | 29.35 | -28.46
2017-07-11 06:00 | 19.8 | -18.44
2017-07-11 06:30 | 4.15 | 4.13
2017-07-11 07:00 | 39.59 | 37.1
2017-07-11 07:30 | 62.94 | 61.07
2017-07-11 08:00 | 46.5 | 38.49
2017-07-11 08:30 | 36.5 | 19.84
2017-07-11 09:00 | 32 | -2.45
2017-07-11 09:30 | 40.49 | -21.58
2017-07-11 10:00 | 41.99 | -24.35
2017-07-11 10:30 | 56.47 | -43.32
2017-07-11 11:00 | 77.25 | -58.41
2017-07-11 11:30 | 85.97 | -65.92
2017-07-11 12:00 | 91.34 | -72.14
2017-07-11 12:30 | 92.09 | -73.74
2017-07-11 13:00 | 91.03 | -73.29
2017-07-11 13:30 | 90.23 | -72.6
2017-07-11 14:00 | 91.82 | -73.92
2017-07-11 14:30 | 75.45 | -55.91
2017-07-11 15:00 | 86.83 | -68.17
2017-07-11 15:30 | 58.74 | -35.28
2017-07-11 16:00 | 48.65 | -12.36
2017-07-11 16:30 | 45.81 | 5.27
2017-07-11 17:00 | 50.47 | 17.33
2017-07-11 17:30 | 48.41 | 24.81
2017-07-11 18:00 | 60.77 | 42.97
2017-07-11 18:30 | 63.92 | 48.17
2017-07-11 19:00 | 77.99 | 67.87
2017-07-11 19:30 | 82.42 | 79.72
2017-07-11 20:00 | 78.72 | 76.22
2017-07-11 20:30 | 69.52 | 69.03
2017-07-11 21:00 | 51.19 | 48.62
2017-07-11 21:30 | 35.94 | 30.65
2017-07-11 22:00 | 27.14 | 15.9
2017-07-11 22:30 | 35.71 | 27.16
2017-07-11 23:00 | 44.52 | 43.14
2017-07-11 23:30 | 19.91 | 15.66
2017-07-12 | 15.3 | -9.93
2017-07-12 00:30 | 31.4 | -30.29
2017-07-12 01:00 | 57.83 | -57.82
2017-07-12 01:30 | 61.74 | -61.71
2017-07-12 02:00 | 69.65 | -69.55
2017-07-12 02:30 | 67.86 | -67.77
2017-07-12 03:00 | 67.38 | -67.28
2017-07-12 03:30 | 64.36 | -64.32
2017-07-12 04:00 | 57.38 | -57.37
2017-07-12 04:30 | 59.01 | -58.98
2017-07-12 05:00 | 60.33 | -60.31
2017-07-12 05:30 | 34.78 | -33.88
2017-07-12 06:00 | 15.72 | -13.02
2017-07-12 06:30 | 23.76 | 15.61
2017-07-12 07:00 | 33.08 | 28.01
2017-07-12 07:30 | 50.4 | 48.76
2017-07-12 08:00 | 32.67 | 32.47
2017-07-12 08:30 | 7.14 | 2.88
2017-07-12 09:00 | 25.76 | -23.91
2017-07-12 09:30 | 51.76 | -49.07
2017-07-12 10:00 | 60.42 | -55.55
2017-07-12 10:30 | 67.21 | -61.08
2017-07-12 11:00 | 69.51 | -63.84
2017-07-12 11:30 | 75.32 | -70.28
2017-07-12 12:00 | 73.7 | -68.61
2017-07-12 12:30 | 76.64 | -72.07
2017-07-12 13:00 | 75.52 | -71.26
2017-07-12 13:30 | 74.6 | -70.8
2017-07-12 14:00 | 75.05 | -71.25
2017-07-12 14:30 | 65.68 | -61.5
2017-07-12 15:00 | 73.75 | -60.97
2017-07-12 15:30 | 77.76 | -65.09
2017-07-12 16:00 | 73.57 | -60.47
2017-07-12 16:30 | 55 | -40.7
2017-07-12 17:00 | 21.67 | -4.22
2017-07-12 17:30 | 31.68 | 20.54
2017-07-12 18:00 | 58.03 | 51.45
2017-07-12 18:30 | 61.48 | 55.43
2017-07-12 19:00 | 66.63 | 61.4
2017-07-12 19:30 | 55.87 | 50.24
2017-07-12 20:00 | 55.06 | 49.97
2017-07-12 20:30 | 50 | 44.94
2017-07-12 21:00 | 34.3 | 28.86
2017-07-12 21:30 | 27.54 | 23.65
2017-07-12 22:00 | 12.78 | 7.06
2017-07-12 22:30 | 20.53 | 18.77
2017-07-12 23:00 | 24.04 | 23.32
2017-07-12 23:30 | 8.41 | 6.99
2017-07-13 | 20.02 | -19.09
2017-07-13 00:30 | 45.32 | -43.79
2017-07-13 01:00 | 47.54 | -46.12
2017-07-13 01:30 | 67.31 | -65.19
2017-07-13 02:00 | 72.4 | -69.99
2017-07-13 02:30 | 72.11 | -69.67
2017-07-13 03:00 | 66.92 | -64.64
2017-07-13 03:30 | 62.5 | -60.75
2017-07-13 04:00 | 66.62 | -64.81
2017-07-13 04:30 | 58.69 | -57.12
2017-07-13 05:00 | 55.03 | -53.55
2017-07-13 05:30 | 40.8 | -40.4
2017-07-13 06:00 | 29.84 | -17.52
2017-07-13 06:30 | 20.32 | 0.19
2017-07-13 07:00 | 44.55 | 43.69
2017-07-13 07:30 | 79.24 | 78.12
2017-07-13 08:00 | 64.09 | 61.62
2017-07-13 08:30 | 37.67 | 32.81
2017-07-13 09:00 | 21.35 | 10.27
2017-07-13 09:30 | 38.06 | 2.88
2017-07-13 10:00 | 47.65 | 2.87
2017-07-13 10:30 | 47.14 | -3.61
2017-07-13 11:00 | 47.14 | -8.3
2017-07-13 11:30 | 49.57 | -12.82
2017-07-13 12:00 | 49.3 | -13.39
2017-07-13 12:30 | 48.84 | -9.29
2017-07-13 13:00 | 64.98 | -39.5
2017-07-13 13:30 | 85.46 | -64.33
2017-07-13 14:00 | 89.82 | -69.94
2017-07-13 14:30 | 82.09 | -59.71
2017-07-13 15:00 | 60.37 | -33.05
2017-07-13 15:30 | 77.55 | -53.83
2017-07-13 16:00 | 56.88 | -19.38
2017-07-13 16:30 | 57.99 | -24.08
2017-07-13 17:00 | 48.61 | 26.87
2017-07-13 17:30 | 65.37 | 51.68
2017-07-13 18:00 | 85.94 | 74.85
2017-07-13 18:30 | 107.3 | 98.58
2017-07-13 19:00 | 114.23 | 106.65
2017-07-13 19:30 | 100.75 | 92.7
2017-07-13 20:00 | 91.6 | 83.38
2017-07-13 20:30 | 83.76 | 79.64
2017-07-13 21:00 | 51.4 | 51.4
2017-07-13 21:30 | 40.91 | 40.85
2017-07-13 22:00 | 21.91 | 21.9
2017-07-13 22:30 | 25.46 | 24.63
2017-07-13 23:00 | 23.78 | 23.25
2017-07-13 23:30 | 6.98 | 6.05
2017-07-14 | 10.79 | -9.74
2017-07-14 00:30 | 13.52 | -12.24
2017-07-14 01:00 | 19.12 | -18.16
2017-07-14 01:30 | 26.6 | -25.78
2017-07-14 02:00 | 38.99 | -38.16
2017-07-14 02:30 | 34.07 | -33.2
2017-07-14 03:00 | 33.22 | -32.38
2017-07-14 03:30 | 32.97 | -32.15
2017-07-14 04:00 | 31.53 | -30.88
2017-07-14 04:30 | 30.92 | -30.42
2017-07-14 05:00 | 25.33 | -24.96
2017-07-14 05:30 | 22.09 | -21.76
2017-07-14 06:00 | 4.61 | -2.93
2017-07-14 06:30 | 37.62 | 37.05
2017-07-14 07:00 | 81.97 | 81.85
2017-07-14 07:30 | 107.51 | 107.51
2017-07-14 08:00 | 106.99 | 106.99
2017-07-14 08:30 | 63.65 | 63.65
2017-07-14 09:00 | 27.21 | 27.2
2017-07-14 09:30 | 2.88 | 1.38
2017-07-14 10:00 | 18.11 | -17.62
2017-07-14 10:30 | 34.51 | -33.67
2017-07-14 11:00 | 55.21 | -49.63
2017-07-14 11:30 | 52.91 | -47.52
2017-07-14 12:00 | 41.15 | -35.33
2017-07-14 12:30 | 38.3 | -34.22
2017-07-14 13:00 | 63.18 | -58.73
2017-07-14 13:30 | 74.1 | -70.04
2017-07-14 14:00 | 48.34 | -44.32
2017-07-14 14:30 | 24.77 | -20.31
2017-07-14 15:00 | 27.65 | -24.48
2017-07-14 15:30 | 23.35 | -19.75
2017-07-14 16:00 | 12.66 | -6.22
2017-07-14 16:30 | 18.2 | 14.74
2017-07-14 17:00 | 39.38 | 36.52
2017-07-14 17:30 | 65.35 | 63.16
2017-07-14 18:00 | 100.3 | 94.49
2017-07-14 18:30 | 106.06 | 102.8
2017-07-14 19:00 | 105.61 | 104.05
2017-07-14 19:30 | 93.7 | 92.13
2017-07-14 20:00 | 89.03 | 88.07
2017-07-14 20:30 | 112.45 | 110.94
2017-07-14 21:00 | 94.62 | 92.75
2017-07-14 21:30 | 77.84 | 74.92
2017-07-14 22:00 | 52.71 | 46.92
2017-07-14 22:30 | 84.89 | 82.81
2017-07-14 23:00 | 87.56 | 86.36
2017-07-14 23:30 | 46.69 | 44.1
2017-07-15 | 18.48 | 11.94
2017-07-15 00:30 | 12.02 | 2.82
2017-07-15 01:00 | 17.82 | -13.9
2017-07-15 01:30 | 30.2 | -28.65
2017-07-15 02:00 | 35.43 | -34.43
2017-07-15 02:30 | 36.03 | -35.08
2017-07-15 03:00 | 35.39 | -34.41
2017-07-15 03:30 | 36.49 | -35.53
2017-07-15 04:00 | 38.05 | -37.28
2017-07-15 04:30 | 38.7 | -38.05
2017-07-15 05:00 | 38.46 | -37.7
2017-07-15 05:30 | 33.79 | -32.39
2017-07-15 06:00 | 29.68 | -27.76
2017-07-15 06:30 | 26.33 | -23.57
2017-07-15 07:00 | 15.49 | -10.16
2017-07-15 07:30 | 15.97 | 11.28
2017-07-15 08:00 | 16.8 | 13.92
2017-07-15 08:30 | 17.09 | 17.08
2017-07-15 09:00 | 13.12 | 11.55
2017-07-15 09:30 | 7.64 | 3.4
2017-07-15 10:00 | 15.02 | -12.81
2017-07-15 10:30 | 31.82 | -30.47
2017-07-15 11:00 | 25.64 | -23.93
2017-07-15 11:30 | 30.53 | -29.28
2017-07-15 12:00 | 36.13 | -35
2017-07-15 12:30 | 40.65 | -39.65
2017-07-15 13:00 | 40.31 | -39.38
2017-07-15 13:30 | 34.79 | -33.81
2017-07-15 14:00 | 32.29 | -31.32
2017-07-15 14:30 | 22.71 | -20.95
2017-07-15 15:00 | 13.73 | -5.29
2017-07-15 15:30 | 12.29 | 1.34
2017-07-15 16:00 | 17.33 | 12.55
2017-07-15 16:30 | 25.73 | 22.52
2017-07-15 17:00 | 48.1 | 45.01
2017-07-15 17:30 | 74.79 | 64.86
2017-07-15 18:00 | 86.58 | 77.58
2017-07-15 18:30 | 81.2 | 75.56
2017-07-15 19:00 | 76.65 | 74.07
2017-07-15 19:30 | 57.1 | 53.97
2017-07-15 20:00 | 52.6 | 49.41
2017-07-15 20:30 | 40.57 | 37.12
2017-07-15 21:00 | 17.61 | 17.61
2017-07-15 21:30 | 24.66 | 17.32
2017-07-15 22:00 | 22.23 | 10.36
2017-07-15 22:30 | 33.54 | 25.63
2017-07-15 23:00 | 45.3 | 38.75
2017-07-15 23:30 | 36.43 | 26.69
2017-07-16 | 23.56 | -2.7
2017-07-16 00:30 | 29.04 | -19.72
2017-07-16 01:00 | 33.99 | -27.56
2017-07-16 01:30 | 37.83 | -32.87
2017-07-16 02:00 | 40.05 | -35.77
2017-07-16 02:30 | 45.56 | -42.2
2017-07-16 03:00 | 42.09 | -39.07
2017-07-16 03:30 | 40.22 | -36.76
2017-07-16 04:00 | 40.91 | -37.41
2017-07-16 04:30 | 49.69 | -49.05
2017-07-16 05:00 | 38.1 | -36.74
2017-07-16 05:30 | 36.15 | -33.96
2017-07-16 06:00 | 33.88 | -30.59
2017-07-16 06:30 | 30.39 | -24.6
2017-07-16 07:00 | 26.76 | -18.7
2017-07-16 07:30 | 24.1 | -10.93
2017-07-16 08:00 | 26.86 | 1.31
2017-07-16 08:30 | 18.29 | 3.6
2017-07-16 09:00 | 5.43 | 5.41
2017-07-16 09:30 | 15.57 | 15.57
2017-07-16 10:00 | 17.23 | 17.21
2017-07-16 10:30 | 16.19 | 16.19
2017-07-16 11:00 | 5.93 | -5.89
2017-07-16 11:30 | 27.29 | -27.28
2017-07-16 12:00 | 32.22 | -32.15
2017-07-16 12:30 | 26.88 | -26.58
2017-07-16 13:00 | 35.55 | -35.25
2017-07-16 13:30 | 37.51 | -37.19
2017-07-16 14:00 | 28.51 | -28.18
2017-07-16 14:30 | 23.37 | -23.02
2017-07-16 15:00 | 12.74 | -12.24
2017-07-16 15:30 | 2.96 | -0.15
2017-07-16 16:00 | 11.76 | 11.49
2017-07-16 16:30 | 21.67 | 21.66
2017-07-16 17:00 | 33.68 | 33.29
2017-07-16 17:30 | 51.37 | 44.45
2017-07-16 18:00 | 85.51 | 81.19
2017-07-16 18:30 | 116.14 | 113.76
2017-07-16 19:00 | 113.68 | 113.5
2017-07-16 19:30 | 86.92 | 85.94
2017-07-16 20:00 | 67.44 | 66
2017-07-16 20:30 | 58.19 | 56.89
2017-07-16 21:00 | 38.39 | 37.05
2017-07-16 21:30 | 32.86 | 30.05
2017-07-16 22:00 | 32.32 | 18.68
2017-07-16 22:30 | 39.22 | 27.96
2017-07-16 23:00 | 33.17 | 32.64
2017-07-16 23:30 | 16.96 | 16.95
2017-07-17 | 4.11 | -2.72
2017-07-17 00:30 | 10.53 | -10.44
2017-07-17 01:00 | 18.27 | -14.44
2017-07-17 01:30 | 22.38 | -19.71
2017-07-17 02:00 | 27.54 | -25.6
2017-07-17 02:30 | 29.56 | -27.82
2017-07-17 03:00 | 30.53 | -29.01
2017-07-17 03:30 | 29.98 | -28.42
2017-07-17 04:00 | 26.02 | 2.52
2017-07-17 04:30 | 72.27 | 67.14
2017-07-17 05:00 | 71.92 | 65.5
2017-07-17 05:30 | 46.6 | 36.37
2017-07-17 06:00 | 15.59 | 2.99
2017-07-17 06:30 | 45.2 | 44.81
2017-07-17 07:00 | 83.05 | 82.75
2017-07-17 07:30 | 135.6 | 134.38
2017-07-17 08:00 | 116.89 | 115.97
2017-07-17 08:30 | 81.01 | 79.22
2017-07-17 09:00 | 43.36 | 39.43
2017-07-17 09:30 | 28.4 | 19.79
2017-07-17 10:00 | 20.88 | 2.55
2017-07-17 10:30 | 23.65 | -11.67
2017-07-17 11:00 | 25.36 | -13.4
2017-07-17 11:30 | 26.82 | -15.65
2017-07-17 12:00 | 26.65 | -15.56
2017-07-17 12:30 | 26.95 | -15.97
2017-07-17 13:00 | 23.7 | -10.2
2017-07-17 13:30 | 23.42 | -11.15
2017-07-17 14:00 | 22.21 | -8.21
2017-07-17 14:30 | 20.6 | -2.84
2017-07-17 15:00 | 21.49 | 9.46
2017-07-17 15:30 | 22.02 | 11.5
2017-07-17 16:00 | 24.67 | 16.96
2017-07-17 16:30 | 37.23 | 29.21
2017-07-17 17:00 | 58.94 | 39.91
2017-07-17 17:30 | 89.13 | 60.61
2017-07-17 18:00 | 113.75 | 91.27
2017-07-17 18:30 | 112.64 | 93.69
2017-07-17 19:00 | 96 | 89.48
2017-07-17 19:30 | 77.39 | 69.82
2017-07-17 20:00 | 66.83 | 59.43
2017-07-17 20:30 | 61.91 | 54.8
2017-07-17 21:00 | 47.54 | 38.83
2017-07-17 21:30 | 35.42 | 34.71
2017-07-17 22:00 | 22.02 | 21.3
2017-07-17 22:30 | 12.27 | 11.38
2017-07-17 23:00 | 24.49 | 24.37
2017-07-17 23:30 | 4.01 | 4.01
2017-07-18 | 15.92 | -8.81
2017-07-18 00:30 | 24.83 | -22.77
2017-07-18 01:00 | 48.87 | -48.75
2017-07-18 01:30 | 62.58 | -62.53
2017-07-18 02:00 | 43.18 | -43.02
2017-07-18 02:30 | 35.49 | -34.74
2017-07-18 03:00 | 50.78 | -49.17
2017-07-18 03:30 | 42.07 | -38.13
2017-07-18 04:00 | 39.47 | -34.86
2017-07-18 04:30 | 43.7 | -39.83
2017-07-18 05:00 | 55.05 | -52.99
2017-07-18 05:30 | 41.19 | -38.68
2017-07-18 06:00 | 21.12 | -19.67
2017-07-18 06:30 | 6.67 | 0.85
2017-07-18 07:00 | 35.57 | 24.27
2017-07-18 07:30 | 69.91 | 63.43
2017-07-18 08:00 | 72.76 | 65.44
2017-07-18 08:30 | 51.01 | 38.38
2017-07-18 09:00 | 42.31 | 23.34
2017-07-18 09:30 | 36.59 | -3.05
2017-07-18 10:00 | 36.76 | -6.65
2017-07-18 10:30 | 39.51 | -13.61
2017-07-18 11:00 | 43.23 | -21.91
2017-07-18 11:30 | 46.79 | -26.68
2017-07-18 12:00 | 51.54 | -33.87
2017-07-18 12:30 | 47 | -26.27
2017-07-18 13:00 | 43.94 | -20.97
2017-07-18 13:30 | 40.5 | -13.65
2017-07-18 14:00 | 39.96 | 10.11
2017-07-18 14:30 | 40.57 | 14.46
2017-07-18 15:00 | 44.6 | 24.47
2017-07-18 15:30 | 48.45 | 32.11
2017-07-18 16:00 | 57.9 | 46.14
2017-07-18 16:30 | 78.62 | 71.07
2017-07-18 17:00 | 89.96 | 83.74
2017-07-18 17:30 | 106.93 | 101.04
2017-07-18 18:00 | 143.85 | 136.42
2017-07-18 18:30 | 156.43 | 147.02
2017-07-18 19:00 | 158.31 | 150.33
2017-07-18 19:30 | 135.28 | 131.09
2017-07-18 20:00 | 121.37 | 117.2
2017-07-18 20:30 | 109.71 | 105.61
2017-07-18 21:00 | 85.56 | 84.92
2017-07-18 21:30 | 50.43 | 49.76
2017-07-18 22:00 | 37.67 | 36.4
2017-07-18 22:30 | 33.37 | 31.75
2017-07-18 23:00 | 33.97 | 31.74
2017-07-18 23:30 | 12.63 | 1.24
2017-07-19 | 16.13 | -15.93
2017-07-19 00:30 | 53.39 | -46.02
2017-07-19 01:00 | 68.88 | -56.62
2017-07-19 01:30 | 71.49 | -64.82
2017-07-19 02:00 | 62.56 | -57.32
2017-07-19 02:30 | 57.79 | -57.78
2017-07-19 03:00 | 43.07 | -42.75
2017-07-19 03:30 | 33.39 | -32.43
2017-07-19 04:00 | 29.15 | -27.68
2017-07-19 04:30 | 24.24 | -21.73
2017-07-19 05:00 | 22.39 | -19.3
2017-07-19 05:30 | 26.67 | -26.02
2017-07-19 06:00 | 15.7 | -14.91
2017-07-19 06:30 | 28.26 | 4.41
2017-07-19 07:00 | 34.8 | 26.31
2017-07-19 07:30 | 75.38 | 71.31
2017-07-19 08:00 | 59.41 | 52.74
2017-07-19 08:30 | 39.24 | 25.3
2017-07-19 09:00 | 33.4 | 10.62
2017-07-19 09:30 | 33.04 | -3.8
2017-07-19 10:00 | 35.99 | -12.36
2017-07-19 10:30 | 62.68 | -39.69
2017-07-19 11:00 | 65.76 | -39.02
2017-07-19 11:30 | 82.17 | -60.27
2017-07-19 12:00 | 74.88 | -51.31
2017-07-19 12:30 | 78.87 | -56.39
2017-07-19 13:00 | 85.23 | -64.37
2017-07-19 13:30 | 84.38 | -63.83
2017-07-19 14:00 | 64.87 | -40.14
2017-07-19 14:30 | 41.86 | -25.76
2017-07-19 15:00 | 33.26 | -9.69
2017-07-19 15:30 | 30.85 | 2.8
2017-07-19 16:00 | 31.73 | 10.42
2017-07-19 16:30 | 38.42 | 25.34
2017-07-19 17:00 | 45.87 | 35.66
2017-07-19 17:30 | 75.23 | 59.78
2017-07-19 18:00 | 114.93 | 106.64
2017-07-19 18:30 | 117.53 | 110.31
2017-07-19 19:00 | 114.84 | 107.83
2017-07-19 19:30 | 103.89 | 96.93
2017-07-19 20:00 | 90.73 | 83.46
2017-07-19 20:30 | 98.77 | 93.29
2017-07-19 21:00 | 86.85 | 85.96
2017-07-19 21:30 | 80.45 | 77.58
2017-07-19 22:00 | 61.17 | 58.07
2017-07-19 22:30 | 60.85 | 58.05
2017-07-19 23:00 | 72.03 | 70.44
2017-07-19 23:30 | 38.69 | 35.62
2017-07-20 | 16.16 | 3.02
2017-07-20 00:30 | 26.83 | -19.05
2017-07-20 01:00 | 35.95 | -29.45
2017-07-20 01:30 | 31.23 | -28.6
2017-07-20 02:00 | 33.21 | -32.62
2017-07-20 02:30 | 35.27 | -34.62
2017-07-20 03:00 | 42.55 | -41.75
2017-07-20 03:30 | 55.31 | -53.93
2017-07-20 04:00 | 48.47 | -47.38
2017-07-20 04:30 | 28.1 | -27.72
2017-07-20 05:00 | 24.44 | -24.24
2017-07-20 05:30 | 17.26 | -17.16
2017-07-20 06:00 | 13.17 | 11.76
2017-07-20 06:30 | 57.93 | 46.01
2017-07-20 07:00 | 82.25 | 78.49
2017-07-20 07:30 | 130.09 | 126.75
2017-07-20 08:00 | 109.44 | 105.12
2017-07-20 08:30 | 67.8 | 60.57
2017-07-20 09:00 | 41.2 | 26.15
2017-07-20 09:30 | 32.25 | 2.87
2017-07-20 10:00 | 33.43 | -11.67
2017-07-20 10:30 | 53.15 | -40.63
2017-07-20 11:00 | 63.06 | -52.08
2017-07-20 11:30 | 73.64 | -61.91
2017-07-20 12:00 | 78.73 | -66.98
2017-07-20 12:30 | 81.97 | -70.49
2017-07-20 13:00 | 66.69 | -54.71
2017-07-20 13:30 | 53.04 | -40.21
2017-07-20 14:00 | 49.08 | -34.67
2017-07-20 14:30 | 42.88 | -25.99
2017-07-20 15:00 | 42.52 | -26.2
2017-07-20 15:30 | 38.38 | -19.65
2017-07-20 16:00 | 35.95 | -17.02
2017-07-20 16:30 | 33.16 | 16.78
2017-07-20 17:00 | 40.67 | 28.84
2017-07-20 17:30 | 58.65 | 45.45
2017-07-20 18:00 | 96.54 | 76.48
2017-07-20 18:30 | 116.3 | 95.24
2017-07-20 19:00 | 122.84 | 103.64
2017-07-20 19:30 | 111.34 | 91.19
2017-07-20 20:00 | 95.55 | 72.23
2017-07-20 20:30 | 96.39 | 75.52
2017-07-20 21:00 | 84.52 | 64.44
2017-07-20 21:30 | 81.68 | 70.86
2017-07-20 22:00 | 56.58 | 55.04
2017-07-20 22:30 | 52.96 | 52.74
2017-07-20 23:00 | 55.57 | 55.55
2017-07-20 23:30 | 28.46 | 28.46
2017-07-21 | 8.84 | -8.48
2017-07-21 00:30 | 21.32 | -20.96
2017-07-21 01:00 | 51.78 | -50.64
2017-07-21 01:30 | 32.42 | -31.98
2017-07-21 02:00 | 31.42 | -31.13
2017-07-21 02:30 | 33.54 | -33.25
2017-07-21 03:00 | 34.12 | -33.86
2017-07-21 03:30 | 44.02 | -43.56
2017-07-21 04:00 | 48.43 | -47.86
2017-07-21 04:30 | 23.56 | -23.54
2017-07-21 05:00 | 17.52 | -17.52
2017-07-21 05:30 | 2.39 | -2.22
2017-07-21 06:00 | 11.23 | 11.16
2017-07-21 06:30 | 25.87 | 24.78
2017-07-21 07:00 | 62.44 | 54.43
2017-07-21 07:30 | 114.23 | 98.08
2017-07-21 08:00 | 103.45 | 83.54
2017-07-21 08:30 | 76.03 | 43.95
2017-07-21 09:00 | 70.55 | 35.28
2017-07-21 09:30 | 66.01 | 24.98
2017-07-21 10:00 | 59.67 | 15.38
2017-07-21 10:30 | 49.31 | 7.43
2017-07-21 11:00 | 48.41 | -6.96
2017-07-21 11:30 | 49.68 | -13.79
2017-07-21 12:00 | 50.09 | -16.54
2017-07-21 12:30 | 54.3 | -4.76
2017-07-21 13:00 | 54.21 | -5.42
2017-07-21 13:30 | 54.11 | -6.88
2017-07-21 14:00 | 59.67 | -25.07
2017-07-21 14:30 | 57.72 | -20.28
2017-07-21 15:00 | 52.36 | -2.91
2017-07-21 15:30 | 55.76 | 23.71
2017-07-21 16:00 | 68.78 | 47.13
2017-07-21 16:30 | 99.38 | 85.64
2017-07-21 17:00 | 125.78 | 115.06
2017-07-21 17:30 | 127.62 | 114.8
2017-07-21 18:00 | 155.05 | 141.21
2017-07-21 18:30 | 154.99 | 141.1
2017-07-21 19:00 | 164.03 | 157.33
2017-07-21 19:30 | 151.9 | 150.62
2017-07-21 20:00 | 136.84 | 136.83
2017-07-21 20:30 | 139.45 | 139.45
2017-07-21 21:00 | 123.95 | 123.93
2017-07-21 21:30 | 104.84 | 103.95
2017-07-21 22:00 | 84.16 | 82.37
2017-07-21 22:30 | 86.06 | 84.2
2017-07-21 23:00 | 80.03 | 78.9
2017-07-21 23:30 | 55.18 | 53.26
2017-07-22 | 19.9 | 9.16
2017-07-22 00:30 | 15.91 | -2.98
2017-07-22 01:00 | 20.31 | -14.8
2017-07-22 01:30 | 25.57 | -22.89
2017-07-22 02:00 | 32.44 | -31.12
2017-07-22 02:30 | 39.37 | -38.77
2017-07-22 03:00 | 51.47 | -51.41
2017-07-22 03:30 | 28.09 | -27.87
2017-07-22 04:00 | 28.78 | -27.57
2017-07-22 04:30 | 27.18 | 23.74
2017-07-22 05:00 | 51.5 | 47.49
2017-07-22 05:30 | 57.46 | 53.38
2017-07-22 06:00 | 15.68 | -0.7
2017-07-22 06:30 | 18.82 | 9.61
2017-07-22 07:00 | 25.78 | 19.39
2017-07-22 07:30 | 47.84 | 47.77
2017-07-22 08:00 | 40.31 | 40.09
2017-07-22 08:30 | 45.81 | 45.55
2017-07-22 09:00 | 38.05 | 37.87
2017-07-22 09:30 | 18.76 | 18.04
2017-07-22 10:00 | 7.7 | 0.95
2017-07-22 10:30 | 21.97 | -18.87
2017-07-22 11:00 | 46.76 | -44.39
2017-07-22 11:30 | 47.91 | -45.22
2017-07-22 12:00 | 46.51 | -46.34
2017-07-22 12:30 | 49.88 | -49.31
2017-07-22 13:00 | 48.44 | -47.8
2017-07-22 13:30 | 48.67 | -48.1
2017-07-22 14:00 | 30.69 | -28.02
2017-07-22 14:30 | 23.77 | 16.61
2017-07-22 15:00 | 16.89 | 2.67
2017-07-22 15:30 | 26.53 | -21.69
2017-07-22 16:00 | 15.55 | -9.04
2017-07-22 16:30 | 33.97 | 30.41
2017-07-22 17:00 | 52.88 | 52.24
2017-07-22 17:30 | 94.73 | 94.69
2017-07-22 18:00 | 117.05 | 116.99
2017-07-22 18:30 | 128.52 | 128.45
2017-07-22 19:00 | 118.85 | 118.78
2017-07-22 19:30 | 112.53 | 112.49
2017-07-22 20:00 | 126.38 | 126.37
2017-07-22 20:30 | 118.01 | 118.01
2017-07-22 21:00 | 100.02 | 100.01
2017-07-22 21:30 | 94.47 | 94.46
2017-07-22 22:00 | 79.4 | 79.4
2017-07-22 22:30 | 69 | 69
2017-07-22 23:00 | 68.45 | 68.4
2017-07-22 23:30 | 53.06 | 52.21
2017-07-23 | 21.01 | 6.37
2017-07-23 00:30 | 20 | -11.6
2017-07-23 01:00 | 45.04 | -43.96
2017-07-23 01:30 | 51.98 | -51.57
2017-07-23 02:00 | 57 | -56.85
2017-07-23 02:30 | 59.4 | -59.35
2017-07-23 03:00 | 55.66 | -55.53
2017-07-23 03:30 | 53.18 | -53
2017-07-23 04:00 | 55.66 | -55.54
2017-07-23 04:30 | 48.18 | -47.89
2017-07-23 05:00 | 46.47 | -46.03
2017-07-23 05:30 | 51.22 | -50.8
2017-07-23 06:00 | 35.45 | -33.89
2017-07-23 06:30 | 42.03 | -40.68
2017-07-23 07:00 | 40.26 | -38.94
2017-07-23 07:30 | 18.53 | -6.77
2017-07-23 08:00 | 19.83 | 5.81
2017-07-23 08:30 | 19.19 | 9.19
2017-07-23 09:00 | 11.58 | 1.08
2017-07-23 09:30 | 11.92 | -7.08
2017-07-23 10:00 | 25.57 | -24.45
2017-07-23 10:30 | 44.79 | -44.49
2017-07-23 11:00 | 46.44 | -46.14
2017-07-23 11:30 | 48.65 | -48.29
2017-07-23 12:00 | 50.54 | -49.89
2017-07-23 12:30 | 53.14 | -52.62
2017-07-23 13:00 | 53.07 | -52.55
2017-07-23 13:30 | 52.35 | -51.87
2017-07-23 14:00 | 42.39 | -41.59
2017-07-23 14:30 | 41.79 | -40.93
2017-07-23 15:00 | 46.82 | -46.17
2017-07-23 15:30 | 25.05 | -21.86
2017-07-23 16:00 | 14.25 | 0.54
2017-07-23 16:30 | 32.49 | 28.43
2017-07-23 17:00 | 80.71 | 79.57
2017-07-23 17:30 | 116.88 | 116.86
2017-07-23 18:00 | 181.3 | 181.23
2017-07-23 18:30 | 199.51 | 199.37
2017-07-23 19:00 | 190.42 | 190.34
2017-07-23 19:30 | 172.07 | 172.01
2017-07-23 20:00 | 165.07 | 165.05
2017-07-23 20:30 | 154.25 | 154.24
2017-07-23 21:00 | 132.93 | 132.92
2017-07-23 21:30 | 114.97 | 114.96
2017-07-23 22:00 | 88.65 | 88.65
2017-07-23 22:30 | 93.09 | 92.87
2017-07-23 23:00 | 91.76 | 91.08
2017-07-23 23:30 | 54.92 | 53.72
2017-07-24 | 19.85 | 19.28
2017-07-24 00:30 | 5.66 | 5.65
2017-07-24 01:00 | 3.07 | -2.18
2017-07-24 01:30 | 16.27 | -15.72
2017-07-24 02:00 | 40.05 | -39.3
2017-07-24 02:30 | 44.61 | -43.63
2017-07-24 03:00 | 42.27 | -41.1
2017-07-24 03:30 | 50.33 | -49.04
2017-07-24 04:00 | 46.12 | -45.11
2017-07-24 04:30 | 31.73 | -31.17
2017-07-24 05:00 | 22.87 | -22.75
2017-07-24 05:30 | 6 | 2.82
2017-07-24 06:00 | 55.79 | 54.8
2017-07-24 06:30 | 103 | 102.92
2017-07-24 07:00 | 158.45 | 157.68
2017-07-24 07:30 | 221.81 | 220.52
2017-07-24 08:00 | 199.04 | 198.89
2017-07-24 08:30 | 135.84 | 135.59
2017-07-24 09:00 | 89.71 | 89.36
2017-07-24 09:30 | 64 | 63.24
2017-07-24 10:00 | 54.03 | 53.17
2017-07-24 10:30 | 35.82 | 34.4
2017-07-24 11:00 | 20.57 | 18.16
2017-07-24 11:30 | 10.45 | 7.43
2017-07-24 12:00 | 11.7 | -11.68
2017-07-24 12:30 | 15.69 | -15.17
2017-07-24 13:00 | 23.91 | -23.45
2017-07-24 13:30 | 15.62 | -14.46
2017-07-24 14:00 | 13.31 | -11.89
2017-07-24 14:30 | 6.88 | 0.3
2017-07-24 15:00 | 15.19 | 12.99
2017-07-24 15:30 | 28.23 | 26.72
2017-07-24 16:00 | 54.18 | 52.64
2017-07-24 16:30 | 87.71 | 86.57
2017-07-24 17:00 | 120.98 | 120.18
2017-07-24 17:30 | 154.28 | 154.04
2017-07-24 18:00 | 172.35 | 172.2
2017-07-24 18:30 | 196.72 | 196.51
2017-07-24 19:00 | 185.14 | 184.98
2017-07-24 19:30 | 163.71 | 163.64
2017-07-24 20:00 | 150 | 149.7
2017-07-24 20:30 | 151.54 | 151.18
2017-07-24 21:00 | 132.62 | 132.52
2017-07-24 21:30 | 134.28 | 134.26
2017-07-24 22:00 | 114.01 | 113.17
2017-07-24 22:30 | 121.39 | 119.19
2017-07-24 23:00 | 121.55 | 119.21
2017-07-24 23:30 | 81.59 | 78.26
2017-07-25 | 23.43 | 20.07
2017-07-25 00:30 | 12.11 | -2.16
2017-07-25 01:00 | 30.3 | -27.83
2017-07-25 01:30 | 25.48 | -22.01
2017-07-25 02:00 | 17.01 | -10.67
2017-07-25 02:30 | 15.81 | 0.43
2017-07-25 03:00 | 25.39 | -5.85
2017-07-25 03:30 | 27.2 | 8.84
2017-07-25 04:00 | 62.84 | 54.99
2017-07-25 04:30 | 56.72 | 50.1
2017-07-25 05:00 | 86.27 | 82.56
2017-07-25 05:30 | 61.77 | 54.84
2017-07-25 06:00 | 77.81 | 73.09
2017-07-25 06:30 | 111.35 | 110.6
2017-07-25 07:00 | 157.19 | 156.8
2017-07-25 07:30 | 202.76 | 202.46
2017-07-25 08:00 | 173.69 | 173.53
2017-07-25 08:30 | 122.81 | 122.37
2017-07-25 09:00 | 77.52 | 76.53
2017-07-25 09:30 | 47.74 | 45.53
2017-07-25 10:00 | 31.03 | 26.72
2017-07-25 10:30 | 22.56 | 14.6
2017-07-25 11:00 | 15.22 | 12.43
2017-07-25 11:30 | 8.79 | 8.23
2017-07-25 12:00 | 5.48 | 4.97
2017-07-25 12:30 | 3.97 | -3.16
2017-07-25 13:00 | 16.32 | -11.94
2017-07-25 13:30 | 23.48 | -13.67
2017-07-25 14:00 | 22 | -10.46
2017-07-25 14:30 | 17.98 | 0.54
2017-07-25 15:00 | 22.66 | 14.56
2017-07-25 15:30 | 30.63 | 25.88
2017-07-25 16:00 | 49.07 | 46.53
2017-07-25 16:30 | 65.78 | 63.12
2017-07-25 17:00 | 88.77 | 60.57
2017-07-25 17:30 | 92.87 | 66.13
2017-07-25 18:00 | 119.52 | 101.45
2017-07-25 18:30 | 121.14 | 103.56
2017-07-25 19:00 | 131.45 | 115.65
2017-07-25 19:30 | 110.55 | 92.74
2017-07-25 20:00 | 94.31 | 73.66
2017-07-25 20:30 | 84.47 | 68.03
2017-07-25 21:00 | 76.75 | 67.23
2017-07-25 21:30 | 76.93 | 67.15
2017-07-25 22:00 | 70.94 | 56.91
2017-07-25 22:30 | 71.7 | 59.81
2017-07-25 23:00 | 65.19 | 65.08
2017-07-25 23:30 | 37.77 | 37.74
2017-07-26 | 1.12 | -1.07
2017-07-26 00:30 | 20.45 | -20.35
2017-07-26 01:00 | 28.77 | -28.43
2017-07-26 01:30 | 29.24 | -28.9
2017-07-26 02:00 | 29.96 | -29.63
2017-07-26 02:30 | 31.13 | -30.51
2017-07-26 03:00 | 31.74 | -30.39
2017-07-26 03:30 | 25.17 | -23.85
2017-07-26 04:00 | 20.73 | -19.65
2017-07-26 04:30 | 14.8 | -13.48
2017-07-26 05:00 | 13.51 | -11.74
2017-07-26 05:30 | 7.69 | 0.31
2017-07-26 06:00 | 9.11 | 8.17
2017-07-26 06:30 | 40.68 | 38.91
2017-07-26 07:00 | 74.61 | 71.49
2017-07-26 07:30 | 138.1 | 135.26
2017-07-26 08:00 | 112.2 | 108.2
2017-07-26 08:30 | 71.43 | 65.38
2017-07-26 09:00 | 39.91 | 29.13
2017-07-26 09:30 | 30.26 | 14.26
2017-07-26 10:00 | 33.21 | 7.65
2017-07-26 10:30 | 41.38 | -14.53
2017-07-26 11:00 | 43.46 | -19.45
2017-07-26 11:30 | 50.34 | -30.93
2017-07-26 12:00 | 47.19 | -26.11
2017-07-26 12:30 | 48.98 | -28.96
2017-07-26 13:00 | 47.35 | -27.14
2017-07-26 13:30 | 46.05 | -25.11
2017-07-26 14:00 | 43.26 | -20.13
2017-07-26 14:30 | 39.85 | -7.79
2017-07-26 15:00 | 38.15 | -1.15
2017-07-26 15:30 | 40.6 | 15.95
2017-07-26 16:00 | 48.22 | 32.48
2017-07-26 16:30 | 58.3 | 46.53
2017-07-26 17:00 | 76.44 | 40.54
2017-07-26 17:30 | 62.46 | 13.15
2017-07-26 18:00 | 55.92 | 11.7
2017-07-26 18:30 | 63.65 | 47.25
2017-07-26 19:00 | 51.39 | 36.33
2017-07-26 19:30 | 37.78 | 7.35
2017-07-26 20:00 | 36.91 | 10.58
2017-07-26 20:30 | 34.22 | -3.68
2017-07-26 21:00 | 43.97 | 34.57
2017-07-26 21:30 | 53.03 | 46.39
2017-07-26 22:00 | 44.21 | 38.42
2017-07-26 22:30 | 42.23 | 37.48
2017-07-26 23:00 | 45.53 | 42.04
2017-07-26 23:30 | 26.67 | 26.32
2017-07-27 | 17.51 | 9.73
2017-07-27 00:30 | 10.77 | -2.86
2017-07-27 01:00 | 14.38 | -12.29
2017-07-27 01:30 | 18.58 | -17
2017-07-27 02:00 | 16.69 | -15.04
2017-07-27 02:30 | 11.98 | -9.54
2017-07-27 03:00 | 8.93 | -4.79
2017-07-27 03:30 | 7.08 | -2.69
2017-07-27 04:00 | 8.22 | 1.35
2017-07-27 04:30 | 13.44 | 5.59
2017-07-27 05:00 | 16.59 | 8.5
2017-07-27 05:30 | 18.72 | 11.9
2017-07-27 06:00 | 22.16 | 21.39
2017-07-27 06:30 | 31.99 | 30.89
2017-07-27 07:00 | 50.8 | 45.71
2017-07-27 07:30 | 66.69 | 60.24
2017-07-27 08:00 | 65.08 | 57.6
2017-07-27 08:30 | 59.48 | 51.64
2017-07-27 09:00 | 55.9 | 47.89
2017-07-27 09:30 | 48.2 | 39.42
2017-07-27 10:00 | 50.73 | 33.16
2017-07-27 10:30 | 49.67 | 27.73
2017-07-27 11:00 | 49.76 | 26.23
2017-07-27 11:30 | 49.21 | 24.45
2017-07-27 12:00 | 47.97 | 22.67
2017-07-27 12:30 | 45.93 | 23.06
2017-07-27 13:00 | 45.58 | 24.26
2017-07-27 13:30 | 45.32 | 24.08
2017-07-27 14:00 | 44.58 | 24.34
2017-07-27 14:30 | 47.28 | 27.74
2017-07-27 15:00 | 45.62 | 25.83
2017-07-27 15:30 | 48.09 | 29.45
2017-07-27 16:00 | 66.13 | 33.98
2017-07-27 16:30 | 97.13 | 38.34
2017-07-27 17:00 | 98.23 | 42.08
2017-07-27 17:30 | 88.33 | 48.59
2017-07-27 18:00 | 91.08 | 77.9
2017-07-27 18:30 | 94.95 | 84.02
2017-07-27 19:00 | 100.37 | 90.41
2017-07-27 19:30 | 86.52 | 75.69
2017-07-27 20:00 | 75.34 | 63.26
2017-07-27 20:30 | 78.41 | 61.25
2017-07-27 21:00 | 73.4 | 56.51
2017-07-27 21:30 | 64.55 | 48.89
2017-07-27 22:00 | 65.68 | 41.65
2017-07-27 22:30 | 52.51 | 45.27
2017-07-27 23:00 | 56.56 | 55.23
2017-07-27 23:30 | 27.49 | 25.49
2017-07-28 | 13.83 | 10.86
2017-07-28 00:30 | 11.31 | -4.01
2017-07-28 01:00 | 17.66 | -12.71
2017-07-28 01:30 | 22.53 | -16.63
2017-07-28 02:00 | 22.06 | -15.64
2017-07-28 02:30 | 19.19 | -10.83
2017-07-28 03:00 | 17.86 | -7.68
2017-07-28 03:30 | 15.63 | -3.33
2017-07-28 04:00 | 13.95 | 0.27
2017-07-28 04:30 | 11.72 | 1.13
2017-07-28 05:00 | 16.38 | -10.89
2017-07-28 05:30 | 15.8 | -9.26
2017-07-28 06:00 | 16.17 | 11.36
2017-07-28 06:30 | 34.87 | 26.74
2017-07-28 07:00 | 50.75 | 45
2017-07-28 07:30 | 90.09 | 79.24
2017-07-28 08:00 | 79.67 | 66.38
2017-07-28 08:30 | 66.94 | 50.03
2017-07-28 09:00 | 65.35 | 48.25
2017-07-28 09:30 | 62.75 | 44.6
2017-07-28 10:00 | 59.71 | 40.12
2017-07-28 10:30 | 67.23 | 36.47
2017-07-28 11:00 | 66.75 | 33.71
2017-07-28 11:30 | 67.92 | 34.54
2017-07-28 12:00 | 65.7 | 31.46
2017-07-28 12:30 | 62.75 | 27.24
2017-07-28 13:00 | 61.33 | 25.85
2017-07-28 13:30 | 69.76 | 42.35
2017-07-28 14:00 | 71.01 | 44.28
2017-07-28 14:30 | 72.7 | 46.45
2017-07-28 15:00 | 72.56 | 46.98
2017-07-28 15:30 | 73.66 | 49.04
2017-07-28 16:00 | 77.43 | 54.91
2017-07-28 16:30 | 99.39 | 83.97
2017-07-28 17:00 | 115.34 | 102.46
2017-07-28 17:30 | 136.07 | 121.55
2017-07-28 18:00 | 148.82 | 132.89
2017-07-28 18:30 | 142.43 | 129.08
2017-07-28 19:00 | 142.94 | 130.12
2017-07-28 19:30 | 131.41 | 118.45
2017-07-28 20:00 | 121.48 | 108.06
2017-07-28 20:30 | 116.95 | 95.62
2017-07-28 21:00 | 113.46 | 92.17
2017-07-28 21:30 | 107.57 | 86.96
2017-07-28 22:00 | 90.13 | 67
2017-07-28 22:30 | 100.1 | 96.47
2017-07-28 23:00 | 118.68 | 115.78
2017-07-28 23:30 | 90.2 | 86.68
2017-07-29 | 46.5 | 39.57
2017-07-29 00:30 | 45.15 | 37.39
2017-07-29 01:00 | 27.71 | 2.41
2017-07-29 01:30 | 30.31 | -10.23
2017-07-29 02:00 | 29.78 | -7.42
2017-07-29 02:30 | 28.51 | -1.8
2017-07-29 03:00 | 28.63 | 1.62
2017-07-29 03:30 | 28.31 | 5.63
2017-07-29 04:00 | 28.41 | 6.45
2017-07-29 04:30 | 28.33 | 9.46
2017-07-29 05:00 | 29.02 | 11.89
2017-07-29 05:30 | 29.79 | 15.71
2017-07-29 06:00 | 32.61 | 19.99
2017-07-29 06:30 | 35.03 | 24.31
2017-07-29 07:00 | 38.8 | 29.54
2017-07-29 07:30 | 45.47 | 35.75
2017-07-29 08:00 | 50.68 | 38.8
2017-07-29 08:30 | 53.26 | 40.47
2017-07-29 09:00 | 53.6 | 39.64
2017-07-29 09:30 | 53.32 | 39.29
2017-07-29 10:00 | 51.27 | 36.43
2017-07-29 10:30 | 50.3 | 34.84
2017-07-29 11:00 | 48.45 | 32.11
2017-07-29 11:30 | 46.56 | 30.36
2017-07-29 12:00 | 44.34 | 27.39
2017-07-29 12:30 | 43.08 | 26.09
2017-07-29 13:00 | 30.79 | 25.56
2017-07-29 13:30 | 29.21 | 25.37
2017-07-29 14:00 | 31.24 | 27.14
2017-07-29 14:30 | 33.38 | 29.5
2017-07-29 15:00 | 33.08 | 29.26
2017-07-29 15:30 | 34.44 | 30.99
2017-07-29 16:00 | 37.95 | 34.94
2017-07-29 16:30 | 45.83 | 40.11
2017-07-29 17:00 | 70.24 | 52.09
2017-07-29 17:30 | 92.11 | 57.51
2017-07-29 18:00 | 105.38 | 71.91
2017-07-29 18:30 | 123.33 | 97.23
2017-07-29 19:00 | 130.75 | 107.25
2017-07-29 19:30 | 110.86 | 83.11
2017-07-29 20:00 | 104.66 | 76.8
2017-07-29 20:30 | 102.93 | 75.97
2017-07-29 21:00 | 96.6 | 69.56
2017-07-29 21:30 | 87.7 | 81.11
2017-07-29 22:00 | 66.22 | 64.64
2017-07-29 22:30 | 72.53 | 71.32
2017-07-29 23:00 | 76.92 | 75.89
2017-07-29 23:30 | 48.67 | 47.54
2017-07-30 | 32.09 | 30.97
2017-07-30 00:30 | 21.26 | 19.39
2017-07-30 01:00 | 13.29 | 9.59
2017-07-30 01:30 | 6.15 | 3.49
2017-07-30 02:00 | 8.68 | 3.75
2017-07-30 02:30 | 9.36 | 5.43
2017-07-30 03:00 | 9.79 | 6.74
2017-07-30 03:30 | 10.89 | 8.2
2017-07-30 04:00 | 13.04 | 8.6
2017-07-30 04:30 | 14.13 | 9.59
2017-07-30 05:00 | 15.52 | 11
2017-07-30 05:30 | 16.44 | 12.3
2017-07-30 06:00 | 18.46 | 15.15
2017-07-30 06:30 | 19.98 | 17.25
2017-07-30 07:00 | 21.79 | 19.45
2017-07-30 07:30 | 27.13 | 24.58
2017-07-30 08:00 | 30.1 | 28.24
2017-07-30 08:30 | 33.4 | 32.6
2017-07-30 09:00 | 35.34 | 35.01
2017-07-30 09:30 | 35.06 | 34.77
2017-07-30 10:00 | 34.49 | 34.27
2017-07-30 10:30 | 31.26 | 30.96
2017-07-30 11:00 | 29.91 | 29.58
2017-07-30 11:30 | 27.18 | 26.82
2017-07-30 12:00 | 26.22 | 25.72
2017-07-30 12:30 | 22.63 | 22.22
2017-07-30 13:00 | 20.82 | 20.39
2017-07-30 13:30 | 21.28 | 20.88
2017-07-30 14:00 | 23.33 | 22.92
2017-07-30 14:30 | 25.24 | 24.93
2017-07-30 15:00 | 26.15 | 25.87
2017-07-30 15:30 | 28.47 | 28.25
2017-07-30 16:00 | 32.26 | 32.1
2017-07-30 16:30 | 36.83 | 36.66
2017-07-30 17:00 | 59.01 | 54.42
2017-07-30 17:30 | 111.66 | 100.68
2017-07-30 18:00 | 158.14 | 148.07
2017-07-30 18:30 | 186.11 | 177.27
2017-07-30 19:00 | 182.71 | 174.17
2017-07-30 19:30 | 155.21 | 146.11
2017-07-30 20:00 | 144.65 | 135.7
2017-07-30 20:30 | 129.1 | 126.22
2017-07-30 21:00 | 94.24 | 93.16
2017-07-30 21:30 | 82.38 | 81.59
2017-07-30 22:00 | 69.27 | 68.79
2017-07-30 22:30 | 65.42 | 65.13
2017-07-30 23:00 | 63.42 | 63.15
2017-07-30 23:30 | 44.84 | 44.62
2017-07-31 | 23.16 | 22.71
2017-07-31 00:30 | 12.85 | 11.39
2017-07-31 01:00 | 6.08 | 3.43
2017-07-31 01:30 | 9.39 | -1.15
2017-07-31 02:00 | 8.65 | -0.06
2017-07-31 02:30 | 9.32 | 2.98
2017-07-31 03:00 | 8.75 | 3.39
2017-07-31 03:30 | 9.56 | 3.91
2017-07-31 04:00 | 11 | 6.2
2017-07-31 04:30 | 14.48 | 10.02
2017-07-31 05:00 | 17.56 | 13.23
2017-07-31 05:30 | 23.45 | 20.14
2017-07-31 06:00 | 34.1 | 32.08
2017-07-31 06:30 | 73.45 | 73.16
2017-07-31 07:00 | 99.8 | 99.77
2017-07-31 07:30 | 154.87 | 149.14
2017-07-31 08:00 | 116.08 | 102.38
2017-07-31 08:30 | 86.39 | 66.11
2017-07-31 09:00 | 73.63 | 47.71
2017-07-31 09:30 | 67.53 | 37.32
2017-07-31 10:00 | 65.37 | 33.29
2017-07-31 10:30 | 61.68 | 26.28
2017-07-31 11:00 | 61.65 | 25.87
2017-07-31 11:30 | 60.68 | 22.61
2017-07-31 12:00 | 57.97 | 14.97
2017-07-31 12:30 | 58.28 | 15.31
2017-07-31 13:00 | 59.08 | 17.52
2017-07-31 13:30 | 59.98 | 19.45
2017-07-31 14:00 | 60.56 | 19.94
2017-07-31 14:30 | 61.59 | 22.24
2017-07-31 15:00 | 60.96 | 22.19
2017-07-31 15:30 | 60.2 | 21.58
2017-07-31 16:00 | 60.56 | 25.17
2017-07-31 16:30 | 60.93 | 27.71
2017-07-31 17:00 | 62.95 | 32.31
2017-07-31 17:30 | 69.77 | 36.04
2017-07-31 18:00 | 94.25 | 51.89
2017-07-31 18:30 | 96.7 | 56.48
2017-07-31 19:00 | 97.34 | 59.78
2017-07-31 19:30 | 89.22 | 48.8
2017-07-31 20:00 | 86.7 | 48.63
2017-07-31 20:30 | 85.71 | 50.43
2017-07-31 21:00 | 79.81 | 44.6
2017-07-31 21:30 | 73.63 | 37.78
2017-07-31 22:00 | 60.54 | 29.23
2017-07-31 22:30 | 51.33 | 29.1
2017-07-31 23:00 | 52.74 | 34.84
2017-07-31 23:30 | 21.47 | 21.02
2017-08-01 | 14.42 | 9.34
2017-08-01 00:30 | 8.71 | 0.24
2017-08-01 01:00 | 9.34 | -6.13
2017-08-01 01:30 | 10.95 | -8.84
2017-08-01 02:00 | 10.93 | -9.28
2017-08-01 02:30 | 9.03 | -6.54
2017-08-01 03:00 | 8.83 | -6.48
2017-08-01 03:30 | 7.76 | -4.38
2017-08-01 04:00 | 7.62 | -0.17
2017-08-01 04:30 | 8.84 | 2.75
2017-08-01 05:00 | 10.14 | 3.82
2017-08-01 05:30 | 11.84 | 6.95
2017-08-01 06:00 | 15.04 | 13.83
2017-08-01 06:30 | 26.82 | 26.81
2017-08-01 07:00 | 103.35 | 103.31
2017-08-01 07:30 | 130.12 | 130.09
2017-08-01 08:00 | 131.19 | 130.95
2017-08-01 08:30 | 125.67 | 125.43
2017-08-01 09:00 | 121.8 | 121.54
2017-08-01 09:30 | 113.54 | 113.28
2017-08-01 10:00 | 110.82 | 110.6
2017-08-01 10:30 | 103.27 | 103.02
2017-08-01 11:00 | 104.96 | 104.72
2017-08-01 11:30 | 103.46 | 103.24
2017-08-01 12:00 | 101.56 | 101.33
2017-08-01 12:30 | 101.95 | 101.18
2017-08-01 13:00 | 105.77 | 103.79
2017-08-01 13:30 | 104.99 | 102.96
2017-08-01 14:00 | 106.32 | 104.35
2017-08-01 14:30 | 107.81 | 105.94
2017-08-01 15:00 | 107.58 | 105.83
2017-08-01 15:30 | 108.32 | 106.74
2017-08-01 16:00 | 111.56 | 110.08
2017-08-01 16:30 | 114.21 | 112.47
2017-08-01 17:00 | 133.76 | 117.13
2017-08-01 17:30 | 142.07 | 121.07
2017-08-01 18:00 | 146.56 | 123.91
2017-08-01 18:30 | 141.41 | 123.61
2017-08-01 19:00 | 145.27 | 128.78
2017-08-01 19:30 | 141.52 | 125.99
2017-08-01 20:00 | 140.56 | 126.2
2017-08-01 20:30 | 143.44 | 131.47
2017-08-01 21:00 | 136.67 | 127.72
2017-08-01 21:30 | 130.53 | 120.25
2017-08-01 22:00 | 124.13 | 111.72
2017-08-01 22:30 | 126.16 | 111.66
2017-08-01 23:00 | 131.53 | 118.23
2017-08-01 23:30 | 115.81 | 101.54
2017-08-02 | 94.04 | 82.49
2017-08-02 00:30 | 67.6 | 67.41
2017-08-02 01:00 | 58.19 | 57.82
2017-08-02 01:30 | 52.75 | 52.28
2017-08-02 02:00 | 57.58 | 57.09
2017-08-02 02:30 | 65.36 | 64.95
2017-08-02 03:00 | 71.21 | 70.8
2017-08-02 03:30 | 74.68 | 74.32
2017-08-02 04:00 | 77.89 | 77.62
2017-08-02 04:30 | 81.82 | 81.62
2017-08-02 05:00 | 85.34 | 85.19
2017-08-02 05:30 | 90.02 | 89.83
2017-08-02 06:00 | 99.41 | 97.13
2017-08-02 06:30 | 118.58 | 104.86
2017-08-02 07:00 | 145.31 | 122.28
2017-08-02 07:30 | 157.79 | 134.98
2017-08-02 08:00 | 157.6 | 135.52
2017-08-02 08:30 | 151.3 | 128.47
2017-08-02 09:00 | 148.37 | 124.88
2017-08-02 09:30 | 140.69 | 116.89
2017-08-02 10:00 | 119.03 | 113.93
2017-08-02 10:30 | 109.77 | 106.34
2017-08-02 11:00 | 108.85 | 105.48
2017-08-02 11:30 | 105.42 | 101.9
2017-08-02 12:00 | 105.46 | 101.96
2017-08-02 12:30 | 99.17 | 95.59
2017-08-02 13:00 | 67.11 | 61.42
2017-08-02 13:30 | 70.5 | 65.14
2017-08-02 14:00 | 71.67 | 66.41
2017-08-02 14:30 | 72.51 | 67.39
2017-08-02 15:00 | 70.38 | 65.07
2017-08-02 15:30 | 76.4 | 64.94
2017-08-02 16:00 | 79.16 | 68.37
2017-08-02 16:30 | 83.85 | 73.86
2017-08-02 17:00 | 101.11 | 80.81
2017-08-02 17:30 | 106.75 | 83.67
2017-08-02 18:00 | 115.82 | 88.67
2017-08-02 18:30 | 116.88 | 90.61
2017-08-02 19:00 | 118.52 | 93.55
2017-08-02 19:30 | 117.97 | 94.18
2017-08-02 20:00 | 116.7 | 94.48
2017-08-02 20:30 | 116.17 | 95.32
2017-08-02 21:00 | 108.76 | 88.77
2017-08-02 21:30 | 93.94 | 82.23
2017-08-02 22:00 | 82.86 | 72.33
2017-08-02 22:30 | 73.29 | 69.43
2017-08-02 23:00 | 74.61 | 74.59
2017-08-02 23:30 | 71.34 | 70.92
2017-08-03 | 63.28 | 62.92
2017-08-03 00:30 | 54.82 | 54.24
2017-08-03 01:00 | 46.5 | 45.7
2017-08-03 01:30 | 45.3 | 45.07
2017-08-03 02:00 | 52.5 | 52.4
2017-08-03 02:30 | 59.98 | 59.89
2017-08-03 03:00 | 65.53 | 65.45
2017-08-03 03:30 | 70.46 | 70.36
2017-08-03 04:00 | 74.91 | 74.76
2017-08-03 04:30 | 76.88 | 76.61
2017-08-03 05:00 | 80.5 | 80.17
2017-08-03 05:30 | 88.63 | 88.1
2017-08-03 06:00 | 94.78 | 94.46
2017-08-03 06:30 | 105.97 | 104.83
2017-08-03 07:00 | 126.33 | 121.64
2017-08-03 07:30 | 138.06 | 132.26
2017-08-03 08:00 | 138.2 | 132.24
2017-08-03 08:30 | 133.72 | 127.56
2017-08-03 09:00 | 126.79 | 120.34
2017-08-03 09:30 | 119.13 | 112.31
2017-08-03 10:00 | 122.12 | 114.97
2017-08-03 10:30 | 115.44 | 107.75
2017-08-03 11:00 | 111.71 | 103.99
2017-08-03 11:30 | 109.26 | 101.45
2017-08-03 12:00 | 108.2 | 100.39
2017-08-03 12:30 | 116.67 | 109.35
2017-08-03 13:00 | 116.19 | 109.06
2017-08-03 13:30 | 113.64 | 106.31
2017-08-03 14:00 | 110.65 | 103.1
2017-08-03 14:30 | 115 | 107.68
2017-08-03 15:00 | 113.89 | 106.76
2017-08-03 15:30 | 112.27 | 105.26
2017-08-03 16:00 | 116.6 | 110.05
2017-08-03 16:30 | 118.21 | 112.15
2017-08-03 17:00 | 122.09 | 116.7
2017-08-03 17:30 | 63.91 | 45.03
2017-08-03 18:00 | 88.4 | 46.49
2017-08-03 18:30 | 80.15 | 46.19
2017-08-03 19:00 | 95.65 | 71.59
2017-08-03 19:30 | 89.33 | 65
2017-08-03 20:00 | 81.92 | 55.26
2017-08-03 20:30 | 79.56 | 55.02
2017-08-03 21:00 | 63.1 | 48.05
2017-08-03 21:30 | 61.68 | 40
2017-08-03 22:00 | 44.94 | 30.5
2017-08-03 22:30 | 30.03 | 28.56
2017-08-03 23:00 | 34.79 | 33.85
2017-08-03 23:30 | 21.67 | 20.95
2017-08-04 | 9.35 | 7.63
2017-08-04 00:30 | 7.47 | -0.54
2017-08-04 01:00 | 11.93 | -7.31
2017-08-04 01:30 | 14.44 | -10.74
2017-08-04 02:00 | 14.45 | -10.99
2017-08-04 02:30 | 11.92 | -9.39
2017-08-04 03:00 | 10.68 | -7.39
2017-08-04 03:30 | 10.46 | -6.74
2017-08-04 04:00 | 9.58 | -3.28
2017-08-04 04:30 | 10.64 | 1.08
2017-08-04 05:00 | 11.04 | 1.95
2017-08-04 05:30 | 9.98 | 2.82
2017-08-04 06:00 | 13.46 | 8.93
2017-08-04 06:30 | 17.19 | 17.16
2017-08-04 07:00 | 39.89 | 33.24
2017-08-04 07:30 | 82.01 | 46.57
2017-08-04 08:00 | 81.89 | 44.12
2017-08-04 08:30 | 81.19 | 41.45
2017-08-04 09:00 | 75.4 | 38.87
2017-08-04 09:30 | 63.73 | 30.85
2017-08-04 10:00 | 63.02 | 29.58
2017-08-04 10:30 | 60.36 | 22.82
2017-08-04 11:00 | 60.93 | 21.72
2017-08-04 11:30 | 38.4 | 19.35
2017-08-04 12:00 | 32.52 | 19.39
2017-08-04 12:30 | 32.03 | 19.34
2017-08-04 13:00 | 31.9 | 19.44
2017-08-04 13:30 | 30.17 | 18.98
2017-08-04 14:00 | 31.9 | 21.98
2017-08-04 14:30 | 31.62 | 22.93
2017-08-04 15:00 | 26.43 | 15.38
2017-08-04 15:30 | 38.24 | -30.36
2017-08-04 16:00 | 69.27 | -34.36
2017-08-04 16:30 | 78.26 | -25.71
2017-08-04 17:00 | 75.63 | -17.26
2017-08-04 17:30 | 72.73 | -7.23
2017-08-04 18:00 | 74.77 | 12.3
2017-08-04 18:30 | 80.31 | 34.48
2017-08-04 19:00 | 74.96 | 37.97
2017-08-04 19:30 | 64.67 | 24.57
2017-08-04 20:00 | 62.09 | 20.02
2017-08-04 20:30 | 51.16 | 22.42
2017-08-04 21:00 | 43.1 | 15.41
2017-08-04 21:30 | 52.03 | 32.84
2017-08-04 22:00 | 36.45 | 24.55
2017-08-04 22:30 | 27.53 | 24.19
2017-08-04 23:00 | 32.08 | 30.29
2017-08-04 23:30 | 22.63 | 20.98
2017-08-05 | 12.1 | 9.55
2017-08-05 00:30 | 6.43 | -2.4
2017-08-05 01:00 | 8.13 | -7.78
2017-08-05 01:30 | 11.43 | -11.29
2017-08-05 02:00 | 11.53 | -11.41
2017-08-05 02:30 | 9.79 | -9.71
2017-08-05 03:00 | 9.61 | -9.58
2017-08-05 03:30 | 8.47 | -8.35
2017-08-05 04:00 | 7.82 | -7.74
2017-08-05 04:30 | 6.07 | -5.87
2017-08-05 05:00 | 5.86 | -5.48
2017-08-05 05:30 | 4.45 | -3.02
2017-08-05 06:00 | 5.23 | 2.83
2017-08-05 06:30 | 9.31 | 7.93
2017-08-05 07:00 | 15.23 | 14.18
2017-08-05 07:30 | 17.12 | 17
2017-08-05 08:00 | 22.96 | 19.68
2017-08-05 08:30 | 29.15 | 23.04
2017-08-05 09:00 | 30.68 | 23.98
2017-08-05 09:30 | 30.05 | 22.83
2017-08-05 10:00 | 28.65 | 20.98
2017-08-05 10:30 | 27.7 | 19.38
2017-08-05 11:00 | 26.61 | 18.07
2017-08-05 11:30 | 23.64 | 13.92
2017-08-05 12:00 | 22.92 | 13.1
2017-08-05 12:30 | 21.25 | 12.04
2017-08-05 13:00 | 21.13 | 11.36
2017-08-05 13:30 | 21.54 | 12.1
2017-08-05 14:00 | 22.29 | 13.74
2017-08-05 14:30 | 29.26 | 21.79
2017-08-05 15:00 | 55 | 52.12
2017-08-05 15:30 | 44.13 | 40.48
2017-08-05 16:00 | 50.93 | 47.02
2017-08-05 16:30 | 53.83 | 50.09
2017-08-05 17:00 | 60.6 | 56.66
2017-08-05 17:30 | 85.94 | 66.99
2017-08-05 18:00 | 90.92 | 76.95
2017-08-05 18:30 | 98.5 | 88.26
2017-08-05 19:00 | 103.25 | 93.92
2017-08-05 19:30 | 103.73 | 99.11
2017-08-05 20:00 | 94.02 | 92.25
2017-08-05 20:30 | 90.9 | 89.24
2017-08-05 21:00 | 70.56 | 70.4
2017-08-05 21:30 | 65.83 | 62.91
2017-08-05 22:00 | 63.01 | 59.92
2017-08-05 22:30 | 76.03 | 74.15
2017-08-05 23:00 | 76.39 | 74.99
2017-08-05 23:30 | 58.22 | 56.7
2017-08-06 | 44.63 | 42.91
2017-08-06 00:30 | 33.49 | 31.31
2017-08-06 01:00 | 18.7 | 18.54
2017-08-06 01:30 | 9.85 | 7.6
2017-08-06 02:00 | 8.83 | 7.19
2017-08-06 02:30 | 9.28 | 7.99
2017-08-06 03:00 | 14.99 | 14.19
2017-08-06 03:30 | 25.74 | 25.15
2017-08-06 04:00 | 20.78 | 20.2
2017-08-06 04:30 | 24.66 | 24.1
2017-08-06 05:00 | 22.66 | 22.05
2017-08-06 05:30 | 11.89 | 10.65
2017-08-06 06:00 | 15.52 | 14.6
2017-08-06 06:30 | 19.36 | 18.85
2017-08-06 07:00 | 28.31 | 27.84
2017-08-06 07:30 | 35.92 | 35.51
2017-08-06 08:00 | 43.7 | 43.59
2017-08-06 08:30 | 59.35 | 59.34
2017-08-06 09:00 | 61.81 | 61.79
2017-08-06 09:30 | 52 | 51.96
2017-08-06 10:00 | 47.18 | 47.12
2017-08-06 10:30 | 41.26 | 41.21
2017-08-06 11:00 | 31.93 | 31.86
2017-08-06 11:30 | 29.64 | 29.57
2017-08-06 12:00 | 32.67 | 32.58
2017-08-06 12:30 | 31.14 | 31.04
2017-08-06 13:00 | 24.5 | 24.49
2017-08-06 13:30 | 27.79 | 27.7
2017-08-06 14:00 | 30.72 | 30.62
2017-08-06 14:30 | 36.1 | 36.05
2017-08-06 15:00 | 42.97 | 42.95
2017-08-06 15:30 | 50.18 | 50.17
2017-08-06 16:00 | 58.59 | 58.58
2017-08-06 16:30 | 80.48 | 80.48
2017-08-06 17:00 | 99.73 | 98.96
2017-08-06 17:30 | 126.02 | 113.12
2017-08-06 18:00 | 128.49 | 113.44
2017-08-06 18:30 | 127.68 | 112.54
2017-08-06 19:00 | 119.72 | 104.01
2017-08-06 19:30 | 108.27 | 91.59
2017-08-06 20:00 | 101.32 | 83.62
2017-08-06 20:30 | 96.07 | 78.77
2017-08-06 21:00 | 84.64 | 66.34
2017-08-06 21:30 | 76.53 | 57.96
2017-08-06 22:00 | 63.16 | 49.88
2017-08-06 22:30 | 56.08 | 55.91
2017-08-06 23:00 | 63.01 | 62.73
2017-08-06 23:30 | 39.47 | 38.95
2017-08-07 | 23.31 | 22.54
2017-08-07 00:30 | 14.07 | 13.03
2017-08-07 01:00 | 5.94 | 3.32
2017-08-07 01:30 | 4.26 | -1.16
2017-08-07 02:00 | 4.64 | 0.74
2017-08-07 02:30 | 6.07 | 3.01
2017-08-07 03:00 | 6.42 | 3.53
2017-08-07 03:30 | 7.18 | 4.28
2017-08-07 04:00 | 8.47 | 5.32
2017-08-07 04:30 | 11 | 8.25
2017-08-07 05:00 | 12.84 | 10.81
2017-08-07 05:30 | 18.11 | 16.81
2017-08-07 06:00 | 29.39 | 28.85
2017-08-07 06:30 | 42.09 | 39.81
2017-08-07 07:00 | 60.23 | 55.32
2017-08-07 07:30 | 95.3 | 90.95
2017-08-07 08:00 | 92.71 | 75.1
2017-08-07 08:30 | 92.89 | 69.5
2017-08-07 09:00 | 90.56 | 64.92
2017-08-07 09:30 | 86.88 | 58.88
2017-08-07 10:00 | 86.44 | 55.9
2017-08-07 10:30 | 83.23 | 50.74
2017-08-07 11:00 | 84.74 | 53.02
2017-08-07 11:30 | 80.11 | 43.8
2017-08-07 12:00 | 78.23 | 42.18
2017-08-07 12:30 | 81.47 | 49.15
2017-08-07 13:00 | 81.56 | 49.31
2017-08-07 13:30 | 80.82 | 48.7
2017-08-07 14:00 | 80.74 | 49.43
2017-08-07 14:30 | 82.08 | 51.33
2017-08-07 15:00 | 81.18 | 50.87
2017-08-07 15:30 | 82.37 | 53.55
2017-08-07 16:00 | 83.33 | 56.52
2017-08-07 16:30 | 86.56 | 62.01
2017-08-07 17:00 | 88.01 | 63.78
2017-08-07 17:30 | 91.26 | 68.12
2017-08-07 18:00 | 94.65 | 72.08
2017-08-07 18:30 | 84.64 | 75.48
2017-08-07 19:00 | 83.71 | 79.88
2017-08-07 19:30 | 79.05 | 74.49
2017-08-07 20:00 | 81.4 | 71.54
2017-08-07 20:30 | 82.12 | 73.52
2017-08-07 21:00 | 77.63 | 69.55
2017-08-07 21:30 | 63.62 | 60.28
2017-08-07 22:00 | 51.16 | 51.12
2017-08-07 22:30 | 50.27 | 50.22
2017-08-07 23:00 | 54.24 | 54.09
2017-08-07 23:30 | 37.11 | 36.69
2017-08-08 | 18.43 | 17.97
2017-08-08 00:30 | 5.51 | 5.14
2017-08-08 01:00 | 6.21 | -6.04
2017-08-08 01:30 | 12.4 | -12.14
2017-08-08 02:00 | 10.5 | -9.62
2017-08-08 02:30 | 6.03 | -4.5
2017-08-08 03:00 | 4.93 | -1.42
2017-08-08 03:30 | 5.18 | 2.51
2017-08-08 04:00 | 6.98 | 6.04
2017-08-08 04:30 | 10.4 | 10.3
2017-08-08 05:00 | 14.66 | 14.61
2017-08-08 05:30 | 20.62 | 19.93
2017-08-08 06:00 | 30.72 | 29.86
2017-08-08 06:30 | 42.45 | 40.89
2017-08-08 07:00 | 72.4 | 63.61
2017-08-08 07:30 | 84.75 | 75.33
2017-08-08 08:00 | 84.76 | 74.74
2017-08-08 08:30 | 81.24 | 69.86
2017-08-08 09:00 | 75.8 | 63.16
2017-08-08 09:30 | 69.36 | 55.42
2017-08-08 10:00 | 64.25 | 48.87
2017-08-08 10:30 | 58.36 | 41.24
2017-08-08 11:00 | 57.64 | 40.35
2017-08-08 11:30 | 58.03 | 38.99
2017-08-08 12:00 | 58.05 | 39.11
2017-08-08 12:30 | 57.18 | 38.04
2017-08-08 13:00 | 58.76 | 40.44
2017-08-08 13:30 | 59.85 | 41.68
2017-08-08 14:00 | 61.93 | 44.24
2017-08-08 14:30 | 61.95 | 44.76
2017-08-08 15:00 | 62.99 | 46.57
2017-08-08 15:30 | 63.83 | 48.47
2017-08-08 16:00 | 65.87 | 52.02
2017-08-08 16:30 | 69.5 | 57.12
2017-08-08 17:00 | 80.41 | 69.91
2017-08-08 17:30 | 83.17 | 72.67
2017-08-08 18:00 | 104.86 | 94.31
2017-08-08 18:30 | 113.55 | 103
2017-08-08 19:00 | 125.95 | 117.12
2017-08-08 19:30 | 109.49 | 99.7
2017-08-08 20:00 | 94.39 | 83.05
2017-08-08 20:30 | 90.92 | 80.45
2017-08-08 21:00 | 85.75 | 76.16
2017-08-08 21:30 | 77.08 | 68.35
2017-08-08 22:00 | 67.6 | 60.07
2017-08-08 22:30 | 60.54 | 53.68
2017-08-08 23:00 | 59.32 | 59.23
2017-08-08 23:30 | 41.17 | 40.87
2017-08-09 | 22.15 | 21.39
2017-08-09 00:30 | 9 | 7.56
2017-08-09 01:00 | 3.66 | -2.13
2017-08-09 01:30 | 9.64 | -9.32
2017-08-09 02:00 | 7.86 | -7.7
2017-08-09 02:30 | 2.63 | -2.12
2017-08-09 03:00 | 3.07 | 1.91
2017-08-09 03:30 | 7.62 | 5.92
2017-08-09 04:00 | 12.86 | 10.47
2017-08-09 04:30 | 16.66 | 14.46
2017-08-09 05:00 | 20.68 | 18.92
2017-08-09 05:30 | 25.69 | 24.56
2017-08-09 06:00 | 35.92 | 35.72
2017-08-09 06:30 | 54.32 | 54.27
2017-08-09 07:00 | 99.82 | 99.82
2017-08-09 07:30 | 126.39 | 126.37
2017-08-09 08:00 | 96.08 | 95.83
2017-08-09 08:30 | 75.84 | 75.5
2017-08-09 09:00 | 66.76 | 66.43
2017-08-09 09:30 | 57.36 | 57.03
2017-08-09 10:00 | 48.95 | 48.58
2017-08-09 10:30 | 40.78 | 40.53
2017-08-09 11:00 | 38.2 | 38.02
2017-08-09 11:30 | 36.57 | 36.4
2017-08-09 12:00 | 36.54 | 36.27
2017-08-09 12:30 | 37.2 | 36.43
2017-08-09 13:00 | 39.06 | 37.37
2017-08-09 13:30 | 40.15 | 38.35
2017-08-09 14:00 | 41.75 | 39.86
2017-08-09 14:30 | 44.23 | 42.54
2017-08-09 15:00 | 44.2 | 42.84
2017-08-09 15:30 | 20.33 | 16.76
2017-08-09 16:00 | 29.69 | 27.33
2017-08-09 16:30 | 60.54 | 59.99
2017-08-09 17:00 | 88.96 | 88.96
2017-08-09 17:30 | 106.27 | 106.24
2017-08-09 18:00 | 145.46 | 144.19
2017-08-09 18:30 | 176.66 | 173.69
2017-08-09 19:00 | 183.55 | 180.54
2017-08-09 19:30 | 163.18 | 160.56
2017-08-09 20:00 | 154.33 | 152.75
2017-08-09 20:30 | 143.65 | 142.11
2017-08-09 21:00 | 105.35 | 103.21
2017-08-09 21:30 | 78.85 | 78.85
2017-08-09 22:00 | 58.78 | 58.74
2017-08-09 22:30 | 74.55 | 74.46
2017-08-09 23:00 | 83.6 | 83.43
2017-08-09 23:30 | 43.36 | 42.89
2017-08-10 | 23.62 | 22.62
2017-08-10 00:30 | 9.11 | 7.61
2017-08-10 01:00 | 4.64 | -3.56
2017-08-10 01:30 | 10.5 | -10.22
2017-08-10 02:00 | 9.26 | -9.04
2017-08-10 02:30 | 4.81 | -4.2
2017-08-10 03:00 | 2.41 | -0.14
2017-08-10 03:30 | 5.02 | 4.27
2017-08-10 04:00 | 8.73 | 7.85
2017-08-10 04:30 | 13.12 | 12.28
2017-08-10 05:00 | 17.98 | 17.08
2017-08-10 05:30 | 24.36 | 23.75
2017-08-10 06:00 | 49.8 | 49.69
2017-08-10 06:30 | 69.84 | 69.83
2017-08-10 07:00 | 107.32 | 107.29
2017-08-10 07:30 | 133.45 | 133.45
2017-08-10 08:00 | 99.03 | 98.97
2017-08-10 08:30 | 71.2 | 70.96
2017-08-10 09:00 | 64.33 | 64.14
2017-08-10 09:30 | 56.48 | 56.33
2017-08-10 10:00 | 44.39 | 44.32
2017-08-10 10:30 | 41.19 | 41.08
2017-08-10 11:00 | 43.21 | 41.61
2017-08-10 11:30 | 40 | 38.36
2017-08-10 12:00 | 38.46 | 36.67
2017-08-10 12:30 | 39.68 | 37.96
2017-08-10 13:00 | 41.21 | 39.55
2017-08-10 13:30 | 42.78 | 41.28
2017-08-10 14:00 | 24.3 | 21.4
2017-08-10 14:30 | 14.07 | 3.43
2017-08-10 15:00 | 18.88 | 13.24
2017-08-10 15:30 | 34.78 | 32.37
2017-08-10 16:00 | 46.42 | 44.74
2017-08-10 16:30 | 58.02 | 56.75
2017-08-10 17:00 | 80.23 | 79.95
2017-08-10 17:30 | 91.08 | 90.86
2017-08-10 18:00 | 135.75 | 135.26
2017-08-10 18:30 | 168.05 | 167.68
2017-08-10 19:00 | 174.41 | 174.18
2017-08-10 19:30 | 156.56 | 156.37
2017-08-10 20:00 | 136.86 | 136.7
2017-08-10 20:30 | 125.92 | 125.9
2017-08-10 21:00 | 114.41 | 114.34
2017-08-10 21:30 | 93.78 | 93.59
2017-08-10 22:00 | 56.37 | 56.23
2017-08-10 22:30 | 81.51 | 81.44
2017-08-10 23:00 | 79.64 | 79.54
2017-08-10 23:30 | 52.91 | 52.71
2017-08-11 | 22.93 | 22.48
2017-08-11 00:30 | 8.08 | 7.36
2017-08-11 01:00 | 4.64 | -4.3
2017-08-11 01:30 | 9.65 | -9.65
2017-08-11 02:00 | 9.1 | -9.1
2017-08-11 02:30 | 4.43 | -4.37
2017-08-11 03:00 | 1.48 | -0.55
2017-08-11 03:30 | 5.29 | 4.41
2017-08-11 04:00 | 9.88 | 8.49
2017-08-11 04:30 | 14.27 | 12.78
2017-08-11 05:00 | 16.69 | 15.36
2017-08-11 05:30 | 22.16 | 21.34
2017-08-11 06:00 | 30.2 | 29.79
2017-08-11 06:30 | 43.61 | 43.59
2017-08-11 07:00 | 83.44 | 83.41
2017-08-11 07:30 | 106.77 | 106.6
2017-08-11 08:00 | 78.77 | 78.26
2017-08-11 08:30 | 64.96 | 64.24
2017-08-11 09:00 | 61.02 | 59.87
2017-08-11 09:30 | 54.43 | 53.01
2017-08-11 10:00 | 47.81 | 45.91
2017-08-11 10:30 | 43.05 | 40.77
2017-08-11 11:00 | 41.81 | 39.29
2017-08-11 11:30 | 41.85 | 38.92
2017-08-11 12:00 | 41.7 | 38.75
2017-08-11 12:30 | 40.64 | 37.75
2017-08-11 13:00 | 41.11 | 38.28
2017-08-11 13:30 | 42.63 | 39.99
2017-08-11 14:00 | 44.58 | 42.08
2017-08-11 14:30 | 47.42 | 44.97
2017-08-11 15:00 | 48.76 | 46.54
2017-08-11 15:30 | 48.39 | 46.44
2017-08-11 16:00 | 44.81 | 43.13
2017-08-11 16:30 | 59.65 | 58.95
2017-08-11 17:00 | 79.72 | 79.61
2017-08-11 17:30 | 87.31 | 87.28
2017-08-11 18:00 | 111.66 | 111.55
2017-08-11 18:30 | 121.37 | 121.16
2017-08-11 19:00 | 124.6 | 124.47
2017-08-11 19:30 | 108.04 | 107.99
2017-08-11 20:00 | 95.61 | 95.54
2017-08-11 20:30 | 81.4 | 81.29
2017-08-11 21:00 | 63.41 | 63.26
2017-08-11 21:30 | 55.61 | 55.57
2017-08-11 22:00 | 49.03 | 49.02
2017-08-11 22:30 | 57.64 | 57.63
2017-08-11 23:00 | 73.29 | 73.22
2017-08-11 23:30 | 55.33 | 55.17
2017-08-12 | 20.31 | 20.06
2017-08-12 00:30 | 5.51 | 5.1
2017-08-12 01:00 | 6.03 | -6
2017-08-12 01:30 | 12.82 | -12.79
2017-08-12 02:00 | 9.92 | -9.92
2017-08-12 02:30 | 5.3 | -3.81
2017-08-12 03:00 | 4.08 | -0.69
2017-08-12 03:30 | 5.35 | 3.14
2017-08-12 04:00 | 7.52 | 6.17
2017-08-12 04:30 | 8.75 | 7.11
2017-08-12 05:00 | 11.62 | 10.29
2017-08-12 05:30 | 14.21 | 12.78
2017-08-12 06:00 | 17.36 | 16.05
2017-08-12 06:30 | 19.92 | 18.73
2017-08-12 07:00 | 24.58 | 23.8
2017-08-12 07:30 | 30.01 | 29.51
2017-08-12 08:00 | 30.67 | 30.55
2017-08-12 08:30 | 32.21 | 32.21
2017-08-12 09:00 | 33.4 | 33.34
2017-08-12 09:30 | 34.19 | 34.06
2017-08-12 10:00 | 30.72 | 30.48
2017-08-12 10:30 | 30.08 | 29.58
2017-08-12 11:00 | 42.29 | 41.23
2017-08-12 11:30 | 38.28 | 37.18
2017-08-12 12:00 | 28.25 | 27.07
2017-08-12 12:30 | 33.38 | 32.36
2017-08-12 13:00 | 27.73 | 26.73
2017-08-12 13:30 | 32.54 | 31.7
2017-08-12 14:00 | 30.11 | 29.41
2017-08-12 14:30 | 34 | 33.42
2017-08-12 15:00 | 29.12 | 28.48
2017-08-12 15:30 | 31 | 30.41
2017-08-12 16:00 | 35.05 | 34.52
2017-08-12 16:30 | 39.87 | 39.42
2017-08-12 17:00 | 49.29 | 47.86
2017-08-12 17:30 | 55.7 | 51.7
2017-08-12 18:00 | 63.82 | 59.05
2017-08-12 18:30 | 78.89 | 75.34
2017-08-12 19:00 | 80.57 | 77.47
2017-08-12 19:30 | 62.93 | 59.69
2017-08-12 20:00 | 52.87 | 52.87
2017-08-12 20:30 | 54.57 | 54.49
2017-08-12 21:00 | 51.68 | 51.59
2017-08-12 21:30 | 46.22 | 46.21
2017-08-12 22:00 | 40.21 | 40.17
2017-08-12 22:30 | 43.4 | 43.31
2017-08-12 23:00 | 51.59 | 51.38
2017-08-12 23:30 | 39.55 | 39.02
2017-08-13 | 25.79 | 25.09
2017-08-13 00:30 | 15.19 | 14.14
2017-08-13 01:00 | 7.16 | 5.37
2017-08-13 01:30 | 5.54 | 0.6
2017-08-13 02:00 | 4.74 | 0.95
2017-08-13 02:30 | 5.64 | 3.24
2017-08-13 03:00 | 6.36 | 4.5
2017-08-13 03:30 | 7.1 | 5.56
2017-08-13 04:00 | 6.06 | 4.38
2017-08-13 04:30 | 6.29 | 4.53
2017-08-13 05:00 | 7.6 | 5.9
2017-08-13 05:30 | 9.08 | 7.45
2017-08-13 06:00 | 10.72 | 9.17
2017-08-13 06:30 | 12.29 | 10.91
2017-08-13 07:00 | 15.93 | 15.01
2017-08-13 07:30 | 29.02 | 28.32
2017-08-13 08:00 | 28.42 | 27.8
2017-08-13 08:30 | 26.57 | 26.18
2017-08-13 09:00 | 28.44 | 28.32
2017-08-13 09:30 | 30.98 | 30.97
2017-08-13 10:00 | 33.59 | 33.59
2017-08-13 10:30 | 38.96 | 38.92
2017-08-13 11:00 | 62.05 | 62.02
2017-08-13 11:30 | 29.6 | 29.49
2017-08-13 12:00 | 28.76 | 28.65
2017-08-13 12:30 | 24.29 | 24.14
2017-08-13 13:00 | 22.67 | 22.46
2017-08-13 13:30 | 22.47 | 22.28
2017-08-13 14:00 | 26.1 | 25.94
2017-08-13 14:30 | 27.99 | 27.82
2017-08-13 15:00 | 27.26 | 27.06
2017-08-13 15:30 | 28.52 | 28.3
2017-08-13 16:00 | 32.35 | 31.99
2017-08-13 16:30 | 36.05 | 35.54
2017-08-13 17:00 | 48.5 | 48.44
2017-08-13 17:30 | 58 | 57.88
2017-08-13 18:00 | 84.73 | 84.68
2017-08-13 18:30 | 117.33 | 117.25
2017-08-13 19:00 | 115.63 | 115.6
2017-08-13 19:30 | 96.46 | 96.39
2017-08-13 20:00 | 81.28 | 81.26
2017-08-13 20:30 | 68.89 | 68.8
2017-08-13 21:00 | 53.11 | 53.06
2017-08-13 21:30 | 49.84 | 49.84
2017-08-13 22:00 | 42.66 | 42.59
2017-08-13 22:30 | 43.88 | 43.65
2017-08-13 23:00 | 51.91 | 51.61
2017-08-13 23:30 | 36.93 | 36.37
2017-08-14 | 23 | 22.39
2017-08-14 00:30 | 12.32 | 11.72
2017-08-14 01:00 | 5.2 | 3.16
2017-08-14 01:30 | 4.95 | 0.04
2017-08-14 02:00 | 4.44 | 0.59
2017-08-14 02:30 | 5.58 | 2.96
2017-08-14 03:00 | 6.46 | 4.44
2017-08-14 03:30 | 7.05 | 5.11
2017-08-14 04:00 | 9.13 | 7.14
2017-08-14 04:30 | 11.3 | 9.22
2017-08-14 05:00 | 13.21 | 10.95
2017-08-14 05:30 | 17.86 | 16.53
2017-08-14 06:00 | 24.04 | 23.32
2017-08-14 06:30 | 34.38 | 34.33
2017-08-14 07:00 | 51.34 | 51.34
2017-08-14 07:30 | 64.72 | 64.55
2017-08-14 08:00 | 65 | 64.5
2017-08-14 08:30 | 65.28 | 64.66
2017-08-14 09:00 | 58.68 | 58.14
2017-08-14 09:30 | 52.32 | 51.72
2017-08-14 10:00 | 49.07 | 48.36
2017-08-14 10:30 | 46.09 | 45.64
2017-08-14 11:00 | 44.67 | 44.43
2017-08-14 11:30 | 45.14 | 44.96
2017-08-14 12:00 | 42.31 | 42.18
2017-08-14 12:30 | 40.02 | 39.91
2017-08-14 13:00 | 48.82 | 48.75
2017-08-14 13:30 | 49.02 | 48.95
2017-08-14 14:00 | 46.13 | 46.03
2017-08-14 14:30 | 50.33 | 50.25
2017-08-14 15:00 | 50.68 | 50.61
2017-08-14 15:30 | 48.33 | 48.31
2017-08-14 16:00 | 51.79 | 51.78
2017-08-14 16:30 | 55.01 | 54.85
2017-08-14 17:00 | 61.08 | 60.57
2017-08-14 17:30 | 66.61 | 65.85
2017-08-14 18:00 | 88.41 | 85.24
2017-08-14 18:30 | 113.07 | 109.3
2017-08-14 19:00 | 115.95 | 113.19
2017-08-14 19:30 | 91.58 | 88.74
2017-08-14 20:00 | 71.23 | 70.05
2017-08-14 20:30 | 71.56 | 69.47
2017-08-14 21:00 | 65.49 | 63.83
2017-08-14 21:30 | 58.72 | 57.26
2017-08-14 22:00 | 48.99 | 48.19
2017-08-14 22:30 | 47.85 | 47.23
2017-08-14 23:00 | 52.07 | 52.06
2017-08-14 23:30 | 35.06 | 34.97
2017-08-15 | 16.47 | 15.97
2017-08-15 00:30 | 7.24 | 4.26
2017-08-15 01:00 | 8.53 | -7.04
2017-08-15 01:30 | 12.71 | -12.12
2017-08-15 02:00 | 11.22 | -10.73
2017-08-15 02:30 | 7.74 | -5.38
2017-08-15 03:00 | 7.34 | -1.37
2017-08-15 03:30 | 7.81 | 2.26
2017-08-15 04:00 | 10.3 | 5.64
2017-08-15 04:30 | 13.96 | 10.08
2017-08-15 05:00 | 16.47 | 13.13
2017-08-15 05:30 | 20.65 | 18.91
2017-08-15 06:00 | 27.12 | 26.87
2017-08-15 06:30 | 51.07 | 40.63
2017-08-15 07:00 | 72.17 | 63.24
2017-08-15 07:30 | 99.03 | 90.99
2017-08-15 08:00 | 84.91 | 73.43
2017-08-15 08:30 | 77.04 | 63.39
2017-08-15 09:00 | 73.46 | 58.23
2017-08-15 09:30 | 69.29 | 52.03
2017-08-15 10:00 | 63.75 | 44.81
2017-08-15 10:30 | 59.26 | 39.97
2017-08-15 11:00 | 60.17 | 40.28
2017-08-15 11:30 | 58.74 | 37.96
2017-08-15 12:00 | 58.33 | 38.76
2017-08-15 12:30 | 59.17 | 40.38
2017-08-15 13:00 | 59.89 | 40.75
2017-08-15 13:30 | 62.34 | 43.44
2017-08-15 14:00 | 65.64 | 47.49
2017-08-15 14:30 | 67.08 | 48.67
2017-08-15 15:00 | 68.19 | 50.7
2017-08-15 15:30 | 66.95 | 49.98
2017-08-15 16:00 | 70.78 | 55.3
2017-08-15 16:30 | 74.27 | 59.99
2017-08-15 17:00 | 77.94 | 65.01
2017-08-15 17:30 | 75.24 | 69.61
2017-08-15 18:00 | 95.19 | 89.92
2017-08-15 18:30 | 111.93 | 107.78
2017-08-15 19:00 | 116.06 | 112.69
2017-08-15 19:30 | 93.9 | 90.47
2017-08-15 20:00 | 74.43 | 70.77
2017-08-15 20:30 | 68.49 | 67.05
2017-08-15 21:00 | 67.77 | 67.45
2017-08-15 21:30 | 78.53 | 78.48
2017-08-15 22:00 | 50.46 | 50.46
2017-08-15 22:30 | 61.22 | 61.21
2017-08-15 23:00 | 68.74 | 68.67
2017-08-15 23:30 | 35.16 | 35.02
2017-08-16 | 17.51 | 17.01
2017-08-16 00:30 | 6.05 | 3.97
2017-08-16 01:00 | 8.65 | -7.64
2017-08-16 01:30 | 12.89 | -12.41
2017-08-16 02:00 | 9.66 | -8.83
2017-08-16 02:30 | 6.21 | -4.17
2017-08-16 03:00 | 9.15 | 6.8
2017-08-16 03:30 | 21.48 | 19.55
2017-08-16 04:00 | 20.6 | 18.22
2017-08-16 04:30 | 37.21 | 35.65
2017-08-16 05:00 | 43.85 | 42.52
2017-08-16 05:30 | 39.79 | 38.7
2017-08-16 06:00 | 53.21 | 52.92
2017-08-16 06:30 | 60.4 | 60.4
2017-08-16 07:00 | 74.87 | 74.73
2017-08-16 07:30 | 98.27 | 97.84
2017-08-16 08:00 | 90.65 | 90.24
2017-08-16 08:30 | 66.67 | 65.93
2017-08-16 09:00 | 58.34 | 57.53
2017-08-16 09:30 | 54.17 | 53.06
2017-08-16 10:00 | 48.95 | 48.16
2017-08-16 10:30 | 44.14 | 43.7
2017-08-16 11:00 | 45.53 | 45.04
2017-08-16 11:30 | 43.24 | 42.75
2017-08-16 12:00 | 44.05 | 43.38
2017-08-16 12:30 | 46.87 | 46.15
2017-08-16 13:00 | 47.51 | 46.87
2017-08-16 13:30 | 49.16 | 48.54
2017-08-16 14:00 | 50.41 | 49.92
2017-08-16 14:30 | 96.71 | 96.42
2017-08-16 15:00 | 82.55 | 82.42
2017-08-16 15:30 | 89.7 | 89.62
2017-08-16 16:00 | 105.5 | 105.44
2017-08-16 16:30 | 108.09 | 108.05
2017-08-16 17:00 | 127.72 | 127.67
2017-08-16 17:30 | 144.01 | 143.95
2017-08-16 18:00 | 181.04 | 180.76
2017-08-16 18:30 | 201.52 | 201.05
2017-08-16 19:00 | 199.57 | 199.2
2017-08-16 19:30 | 170.93 | 170.7
2017-08-16 20:00 | 151.12 | 151.03
2017-08-16 20:30 | 133.73 | 133.69
2017-08-16 21:00 | 114.82 | 114.68
2017-08-16 21:30 | 124.08 | 124.08
2017-08-16 22:00 | 113.49 | 113.45
2017-08-16 22:30 | 114.72 | 114.66
2017-08-16 23:00 | 125.21 | 125.15
2017-08-16 23:30 | 90.93 | 90.78
2017-08-17 | 31.35 | 30.74
2017-08-17 00:30 | 10.59 | 7.71
2017-08-17 01:00 | 9.96 | -7.82
2017-08-17 01:30 | 13.59 | -12.55
2017-08-17 02:00 | 10.73 | -9.84
2017-08-17 02:30 | 6.47 | -4.23
2017-08-17 03:00 | 5.37 | -1.78
2017-08-17 03:30 | 7.26 | 4.02
2017-08-17 04:00 | 9.08 | 6
2017-08-17 04:30 | 20.48 | 18.92
2017-08-17 05:00 | 22.1 | 20.98
2017-08-17 05:30 | 30.33 | 29.73
2017-08-17 06:00 | 26.66 | 26.51
2017-08-17 06:30 | 48.15 | 48.1
2017-08-17 07:00 | 81.71 | 81.71
2017-08-17 07:30 | 116.41 | 116.24
2017-08-17 08:00 | 103.82 | 103.68
2017-08-17 08:30 | 74.15 | 73.47
2017-08-17 09:00 | 56.62 | 55.88
2017-08-17 09:30 | 52.42 | 52.17
2017-08-17 10:00 | 45.96 | 45.6
2017-08-17 10:30 | 44.18 | 43.11
2017-08-17 11:00 | 43.71 | 42.64
2017-08-17 11:30 | 45.37 | 44.39
2017-08-17 12:00 | 45.66 | 44.83
2017-08-17 12:30 | 48.1 | 47.43
2017-08-17 13:00 | 50.05 | 49.46
2017-08-17 13:30 | 53.56 | 53.02
2017-08-17 14:00 | 71.31 | 70.97
2017-08-17 14:30 | 92.38 | 92.16
2017-08-17 15:00 | 109.43 | 109.28
2017-08-17 15:30 | 112.4 | 112.28
2017-08-17 16:00 | 102.95 | 102.84
2017-08-17 16:30 | 116.19 | 116.11
2017-08-17 17:00 | 121.16 | 121.07
2017-08-17 17:30 | 122.82 | 122.64
2017-08-17 18:00 | 135.88 | 131.56
2017-08-17 18:30 | 150.71 | 147.15
2017-08-17 19:00 | 145.38 | 141.91
2017-08-17 19:30 | 116.76 | 113.04
2017-08-17 20:00 | 99.31 | 95.43
2017-08-17 20:30 | 76.65 | 74.25
2017-08-17 21:00 | 67.77 | 66.92
2017-08-17 21:30 | 60.79 | 59.58
2017-08-17 22:00 | 50.31 | 50.02
2017-08-17 22:30 | 50.08 | 50.06
2017-08-17 23:00 | 54.22 | 54.21
2017-08-17 23:30 | 35.72 | 35.71
2017-08-18 | 16.66 | 16.52
2017-08-18 00:30 | 6.16 | 4.04
2017-08-18 01:00 | 7.24 | -5.66
2017-08-18 01:30 | 10.92 | -9.66
2017-08-18 02:00 | 8.86 | -7.51
2017-08-18 02:30 | 6 | -2.75
2017-08-18 03:00 | 5.39 | 0.1
2017-08-18 03:30 | 8.93 | 4.24
2017-08-18 04:00 | 10.71 | 6.05
2017-08-18 04:30 | 13.15 | 9.37
2017-08-18 05:00 | 14.06 | 10.81
2017-08-18 05:30 | 17.76 | 15.88
2017-08-18 06:00 | 23.9 | 23.41
2017-08-18 06:30 | 32.86 | 32.85
2017-08-18 07:00 | 58.14 | 51.47
2017-08-18 07:30 | 74.97 | 64.83
2017-08-18 08:00 | 76.38 | 65.7
2017-08-18 08:30 | 74.8 | 62.29
2017-08-18 09:00 | 72.33 | 57.96
2017-08-18 09:30 | 66.87 | 52.17
2017-08-18 10:00 | 61.76 | 45.62
2017-08-18 10:30 | 61.43 | 43.23
2017-08-18 11:00 | 61 | 42.23
2017-08-18 11:30 | 59.02 | 39.31
2017-08-18 12:00 | 59.32 | 37.98
2017-08-18 12:30 | 59.42 | 37.62
2017-08-18 13:00 | 59.88 | 37.89
2017-08-18 13:30 | 60.25 | 38.95
2017-08-18 14:00 | 62.18 | 42.04
2017-08-18 14:30 | 64.12 | 45.3
2017-08-18 15:00 | 64.2 | 46.58
2017-08-18 15:30 | 63.37 | 47.05
2017-08-18 16:00 | 67.05 | 52.58
2017-08-18 16:30 | 69.28 | 56.3
2017-08-18 17:00 | 72.57 | 60.91
2017-08-18 17:30 | 72.11 | 61.11
2017-08-18 18:00 | 74.5 | 61.6
2017-08-18 18:30 | 76.16 | 63.85
2017-08-18 19:00 | 78.2 | 66.83
2017-08-18 19:30 | 74.2 | 63.74
2017-08-18 20:00 | 73.9 | 62.41
2017-08-18 20:30 | 74.81 | 63.83
2017-08-18 21:00 | 70.17 | 59.89
2017-08-18 21:30 | 57.56 | 54.1
2017-08-18 22:00 | 46.26 | 46.26
2017-08-18 22:30 | 44.62 | 44.61
2017-08-18 23:00 | 49.95 | 49.92
2017-08-18 23:30 | 33.55 | 33.45
2017-08-19 | 17.21 | 16.62
2017-08-19 00:30 | 6.44 | 2.78
2017-08-19 01:00 | 9.27 | -7.7
2017-08-19 01:30 | 14.3 | -13.87
2017-08-19 02:00 | 11.42 | -10.91
2017-08-19 02:30 | 7.88 | -6.7
2017-08-19 03:00 | 5.26 | -2.27
2017-08-19 03:30 | 6.06 | 0.54
2017-08-19 04:00 | 1.28 | 0.99
2017-08-19 04:30 | 2.95 | 2.8
2017-08-19 05:00 | 5.75 | 5.37
2017-08-19 05:30 | 9.76 | 8.8
2017-08-19 06:00 | 13.28 | 12.37
2017-08-19 06:30 | 15.78 | 15.22
2017-08-19 07:00 | 21.37 | 21.08
2017-08-19 07:30 | 26.73 | 26.71
2017-08-19 08:00 | 28.3 | 28.3
2017-08-19 08:30 | 29.95 | 29.89
2017-08-19 09:00 | 32.54 | 31.77
2017-08-19 09:30 | 32.73 | 31.8
2017-08-19 10:00 | 32.71 | 31.8
2017-08-19 10:30 | 30.39 | 29.65
2017-08-19 11:00 | 29.26 | 28.61
2017-08-19 11:30 | 25.49 | 25.01
2017-08-19 12:00 | 23.19 | 22.78
2017-08-19 12:30 | 22.26 | 21.98
2017-08-19 13:00 | 21.61 | 21.4
2017-08-19 13:30 | 21.97 | 21.85
2017-08-19 14:00 | 23.09 | 22.95
2017-08-19 14:30 | 24.59 | 24.43
2017-08-19 15:00 | 25.2 | 25.05
2017-08-19 15:30 | 26.89 | 26.75
2017-08-19 16:00 | 31.71 | 31.56
2017-08-19 16:30 | 35.04 | 34.74
2017-08-19 17:00 | 44.61 | 44.24
2017-08-19 17:30 | 48.9 | 48.46
2017-08-19 18:00 | 52.57 | 51.06
2017-08-19 18:30 | 57.46 | 54.45
2017-08-19 19:00 | 62.02 | 57.59
2017-08-19 19:30 | 61.02 | 57.73
2017-08-19 20:00 | 58.69 | 55.67
2017-08-19 20:30 | 59.71 | 57.21
2017-08-19 21:00 | 55.15 | 53.14
2017-08-19 21:30 | 50.16 | 49.74
2017-08-19 22:00 | 45.54 | 45.41
2017-08-19 22:30 | 48.07 | 48.01
2017-08-19 23:00 | 56.01 | 56
2017-08-19 23:30 | 42.34 | 42.34
2017-08-20 | 27.57 | 27.41
2017-08-20 00:30 | 18.65 | 17.07
2017-08-20 01:00 | 10.11 | 6.28
2017-08-20 01:30 | 7.14 | -0.1
2017-08-20 02:00 | 6.29 | 0.38
2017-08-20 02:30 | 6.32 | 2.4
2017-08-20 03:00 | 6.41 | 3.17
2017-08-20 03:30 | 8.4 | 5.71
2017-08-20 04:00 | 7.82 | 5.26
2017-08-20 04:30 | 8.58 | 6.14
2017-08-20 05:00 | 9.37 | 7
2017-08-20 05:30 | 11.79 | 9.4
2017-08-20 06:00 | 14.21 | 11.78
2017-08-20 06:30 | 15.08 | 12.65
2017-08-20 07:00 | 19.12 | 16.88
2017-08-20 07:30 | 21.85 | 20.69
2017-08-20 08:00 | 23.54 | 23.19
2017-08-20 08:30 | 26.7 | 26.66
2017-08-20 09:00 | 29.63 | 29.61
2017-08-20 09:30 | 30.37 | 30.3
2017-08-20 10:00 | 28.41 | 28.31
2017-08-20 10:30 | 27.43 | 27.36
2017-08-20 11:00 | 24.27 | 24.22
2017-08-20 11:30 | 21.86 | 21.84
2017-08-20 12:00 | 21.06 | 21.05
2017-08-20 12:30 | 19.8 | 19.8
2017-08-20 13:00 | 19.13 | 19.13
2017-08-20 13:30 | 19.2 | 19.2
2017-08-20 14:00 | 21.74 | 21.73
2017-08-20 14:30 | 21.52 | 21.51
2017-08-20 15:00 | 19.72 | 19.71
2017-08-20 15:30 | 21.65 | 21.64
2017-08-20 16:00 | 26.38 | 26.34
2017-08-20 16:30 | 30.79 | 30.71
2017-08-20 17:00 | 42.25 | 42.03
2017-08-20 17:30 | 48.77 | 48.26
2017-08-20 18:00 | 60.18 | 56.03
2017-08-20 18:30 | 97.45 | 79.47
2017-08-20 19:00 | 102.29 | 90.72
2017-08-20 19:30 | 88.57 | 76.18
2017-08-20 20:00 | 75.61 | 62.39
2017-08-20 20:30 | 78.31 | 63.17
2017-08-20 21:00 | 79.97 | 58.48
2017-08-20 21:30 | 74.44 | 53.02
2017-08-20 22:00 | 59.54 | 44.7
2017-08-20 22:30 | 42.23 | 42.23
2017-08-20 23:00 | 48.76 | 48.66
2017-08-20 23:30 | 37.67 | 37.43
2017-08-21 | 23.39 | 22.78
2017-08-21 00:30 | 14.87 | 13.38
2017-08-21 01:00 | 7.92 | 4.88
2017-08-21 01:30 | 6.57 | 2.05
2017-08-21 02:00 | 6.23 | 2.34
2017-08-21 02:30 | 7.51 | 4.2
2017-08-21 03:00 | 8.41 | 5.79
2017-08-21 03:30 | 12.11 | 7.63
2017-08-21 04:00 | 13.66 | 8.94
2017-08-21 04:30 | 16.15 | 11.98
2017-08-21 05:00 | 18.48 | 15.15
2017-08-21 05:30 | 23.14 | 21.75
2017-08-21 06:00 | 31.28 | 31.09
2017-08-21 06:30 | 42.83 | 42.75
2017-08-21 07:00 | 67.82 | 67.53
2017-08-21 07:30 | 106.07 | 105.92
2017-08-21 08:00 | 63.61 | 63.3
2017-08-21 08:30 | 41.34 | 40.73
2017-08-21 09:00 | 37.93 | 36.93
2017-08-21 09:30 | 36.92 | 35.71
2017-08-21 10:00 | 31.85 | 30.66
2017-08-21 10:30 | 27.56 | 26.22
2017-08-21 11:00 | 18.1 | 18.07
2017-08-21 11:30 | 24.99 | 24.92
2017-08-21 12:00 | 19.33 | 18.87
2017-08-21 12:30 | 16.65 | 13.31
2017-08-21 13:00 | 15.83 | -8.53
2017-08-21 13:30 | 30.33 | -14.63
2017-08-21 14:00 | 20.19 | 5.03
2017-08-21 14:30 | 21.6 | 11.31
2017-08-21 15:00 | 25.6 | 17.73
2017-08-21 15:30 | 29.55 | 23.35
2017-08-21 16:00 | 36.11 | 30.97
2017-08-21 16:30 | 43.12 | 39.48
2017-08-21 17:00 | 61.67 | 59.27
2017-08-21 17:30 | 88.45 | 75.08
2017-08-21 18:00 | 102.41 | 73.84
2017-08-21 18:30 | 108.92 | 82.73
2017-08-21 19:00 | 106.34 | 80.54
2017-08-21 19:30 | 94.86 | 65.95
2017-08-21 20:00 | 84.5 | 51.37
2017-08-21 20:30 | 83.04 | 46.38
2017-08-21 21:00 | 83.24 | 42.2
2017-08-21 21:30 | 74.58 | 35.77
2017-08-21 22:00 | 58.56 | 27.65
2017-08-21 22:30 | 43.6 | 27.53
2017-08-21 23:00 | 47.04 | 33.7
2017-08-21 23:30 | 26.63 | 15.53
2017-08-22 | 7.63 | 5.12
2017-08-22 00:30 | 6.2 | -0.94
2017-08-22 01:00 | 9.41 | -7.13
2017-08-22 01:30 | 11.93 | -10.82
2017-08-22 02:00 | 11.58 | -10.66
2017-08-22 02:30 | 8.63 | -6.88
2017-08-22 03:00 | 8.43 | -6.71
2017-08-22 03:30 | 8.53 | -4.13
2017-08-22 04:00 | 8.2 | -0.22
2017-08-22 04:30 | 8.66 | 1.76
2017-08-22 05:00 | 9.55 | 2.7
2017-08-22 05:30 | 11.31 | 2.91
2017-08-22 06:00 | 13.64 | 10.83
2017-08-22 06:30 | 24.19 | 20.35
2017-08-22 07:00 | 42.4 | 38.44
2017-08-22 07:30 | 51.67 | 49.37
2017-08-22 08:00 | 44.17 | 43
2017-08-22 08:30 | 42.65 | 41.41
2017-08-22 09:00 | 43.4 | 41.88
2017-08-22 09:30 | 35.1 | 33.23
2017-08-22 10:00 | 28.99 | 28.58
2017-08-22 10:30 | 22.88 | 22.85
2017-08-22 11:00 | 24.06 | 24.01
2017-08-22 11:30 | 21.84 | 21.76
2017-08-22 12:00 | 23.24 | 23.01
2017-08-22 12:30 | 23.98 | 23.8
2017-08-22 13:00 | 25.35 | 25.17
2017-08-22 13:30 | 24.96 | 24.82
2017-08-22 14:00 | 10.36 | 10.29
2017-08-22 14:30 | 9.15 | 9.15
2017-08-22 15:00 | 16.11 | 16.03
2017-08-22 15:30 | 28.77 | 28.64
2017-08-22 16:00 | 30.71 | 30.63
2017-08-22 16:30 | 33.32 | 33.25
2017-08-22 17:00 | 36.92 | 36.72
2017-08-22 17:30 | 54.55 | 53.56
2017-08-22 18:00 | 76.2 | 74.84
2017-08-22 18:30 | 94.19 | 93.51
2017-08-22 19:00 | 88.59 | 88.06
2017-08-22 19:30 | 73.74 | 73.3
2017-08-22 20:00 | 52.37 | 52.03
2017-08-22 20:30 | 41.48 | 40.4
2017-08-22 21:00 | 34.63 | 33.37
2017-08-22 21:30 | 29.93 | 27.95
2017-08-22 22:00 | 25.4 | 24.16
2017-08-22 22:30 | 26.11 | 25.22
2017-08-22 23:00 | 29.4 | 28.45
2017-08-22 23:30 | 20.29 | 17.23
2017-08-23 | 10.27 | 3.94
2017-08-23 00:30 | 10.18 | -3.28
2017-08-23 01:00 | 7.16 | -7.16
2017-08-23 01:30 | 11.99 | -10.63
2017-08-23 02:00 | 11.2 | -9.96
2017-08-23 02:30 | 9.83 | -7.25
2017-08-23 03:00 | 10.2 | -6.03
2017-08-23 03:30 | 10.54 | -3.12
2017-08-23 04:00 | 10.82 | 0.26
2017-08-23 04:30 | 9.17 | 2.25
2017-08-23 05:00 | 9.4 | 3.11
2017-08-23 05:30 | 11.16 | 3.78
2017-08-23 06:00 | 10.34 | 10.25
2017-08-23 06:30 | 18.52 | 18.43
2017-08-23 07:00 | 42.41 | 42.29
2017-08-23 07:30 | 73.87 | 67.21
2017-08-23 08:00 | 81.46 | 57.38
2017-08-23 08:30 | 70.92 | 39.25
2017-08-23 09:00 | 71.28 | 37.36
2017-08-23 09:30 | 68.48 | 33.41
2017-08-23 10:00 | 67.6 | 30.5
2017-08-23 10:30 | 66.56 | 24.97
2017-08-23 11:00 | 66.52 | 23.86
2017-08-23 11:30 | 65.08 | 20.78
2017-08-23 12:00 | 65.58 | 19.87
2017-08-23 12:30 | 59.84 | 19.69
2017-08-23 13:00 | 50.71 | 20.24
2017-08-23 13:30 | 50.66 | 20.76
2017-08-23 14:00 | 52.14 | 23.12
2017-08-23 14:30 | 53.02 | 25.12
2017-08-23 15:00 | 52.53 | 25.43
2017-08-23 15:30 | 52.43 | 26.74
2017-08-23 16:00 | 52.56 | 30.1
2017-08-23 16:30 | 63.07 | 47.47
2017-08-23 17:00 | 75.32 | 63.44
2017-08-23 17:30 | 78.93 | 67.96
2017-08-23 18:00 | 97.36 | 83.82
2017-08-23 18:30 | 115.56 | 98.82
2017-08-23 19:00 | 113.72 | 97.72
2017-08-23 19:30 | 102.6 | 85.01
2017-08-23 20:00 | 85.08 | 63.37
2017-08-23 20:30 | 77.37 | 52.77
2017-08-23 21:00 | 72.75 | 46.57
2017-08-23 21:30 | 73.03 | 51.71
2017-08-23 22:00 | 43.4 | 33.68
2017-08-23 22:30 | 48.85 | 48.66
2017-08-23 23:00 | 61.84 | 61.74
2017-08-23 23:30 | 28.25 | 27.95
2017-08-24 | 6.63 | 4.31
2017-08-24 00:30 | 7.45 | -4.09
2017-08-24 01:00 | 10.89 | -8.76
2017-08-24 01:30 | 12.37 | -10.83
2017-08-24 02:00 | 11.83 | -10.35
2017-08-24 02:30 | 10.4 | -8.72
2017-08-24 03:00 | 9.13 | -6.77
2017-08-24 03:30 | 8.5 | -5.17
2017-08-24 04:00 | 8.46 | -1.45
2017-08-24 04:30 | 8.08 | 0.89
2017-08-24 05:00 | 7.24 | 0.76
2017-08-24 05:30 | 6.03 | 2.88
2017-08-24 06:00 | 9.43 | 9.05
2017-08-24 06:30 | 17.67 | 17.56
2017-08-24 07:00 | 40.65 | 36.93
2017-08-24 07:30 | 62.75 | 57.19
2017-08-24 08:00 | 77.46 | 66.86
2017-08-24 08:30 | 69.52 | 62.95
2017-08-24 09:00 | 62.78 | 54.59
2017-08-24 09:30 | 50.65 | 39.59
2017-08-24 10:00 | 39.59 | 26.91
2017-08-24 10:30 | 51.98 | 42.42
2017-08-24 11:00 | 65.08 | 57.12
2017-08-24 11:30 | 48.1 | 36.84
2017-08-24 12:00 | 35.82 | 27.74
2017-08-24 12:30 | 18.4 | 16.4
2017-08-24 13:00 | 22.03 | 19.83
2017-08-24 13:30 | 21.02 | 19.22
2017-08-24 14:00 | 21.05 | 18.77
2017-08-24 14:30 | 30.1 | 29
2017-08-24 15:00 | 41.78 | 41.18
2017-08-24 15:30 | 50.43 | 49.96
2017-08-24 16:00 | 68.68 | 68.33
2017-08-24 16:30 | 80.99 | 80.79
2017-08-24 17:00 | 79.25 | 78.99
2017-08-24 17:30 | 48.08 | 47.71
2017-08-24 18:00 | 51.04 | 47.72
2017-08-24 18:30 | 84.47 | 59.31
2017-08-24 19:00 | 97.19 | 76.92
2017-08-24 19:30 | 72.57 | 58.25
2017-08-24 20:00 | 71.54 | 46.4
2017-08-24 20:30 | 71.31 | 46.59
2017-08-24 21:00 | 68.51 | 41.65
2017-08-24 21:30 | 63.59 | 35.36
2017-08-24 22:00 | 33.72 | 26.46
2017-08-24 22:30 | 30.08 | 27.39
2017-08-24 23:00 | 36.64 | 35
2017-08-24 23:30 | 20.4 | 17.04
2017-08-25 | 11.11 | 4.58
2017-08-25 00:30 | 9.85 | -3.75
2017-08-25 01:00 | 12.86 | -9.07
2017-08-25 01:30 | 15.89 | -12.06
2017-08-25 02:00 | 12.39 | -11.23
2017-08-25 02:30 | 10.38 | -9.12
2017-08-25 03:00 | 9.08 | -7.78
2017-08-25 03:30 | 8.24 | -6.31
2017-08-25 04:00 | 6.98 | -1.7
2017-08-25 04:30 | 6.99 | 0.56
2017-08-25 05:00 | 6.9 | 1.26
2017-08-25 05:30 | 5.81 | 1.92
2017-08-25 06:00 | 8.79 | 8.37
2017-08-25 06:30 | 17.45 | 17.31
2017-08-25 07:00 | 37.29 | 33.17
2017-08-25 07:30 | 71.59 | 51.39
2017-08-25 08:00 | 66.14 | 43.39
2017-08-25 08:30 | 57.71 | 39.2
2017-08-25 09:00 | 59.23 | 39.47
2017-08-25 09:30 | 56.57 | 34.29
2017-08-25 10:00 | 54.14 | 28.71
2017-08-25 10:30 | 51.42 | 21.97
2017-08-25 11:00 | 50.67 | 22.22
2017-08-25 11:30 | 28.68 | 17.48
2017-08-25 12:00 | 16.61 | 13.82
2017-08-25 12:30 | 19.52 | 17.06
2017-08-25 13:00 | 20.11 | 17.95
2017-08-25 13:30 | 20.91 | 19.08
2017-08-25 14:00 | 21.18 | 19.56
2017-08-25 14:30 | 23.54 | 22.5
2017-08-25 15:00 | 21.86 | 20.77
2017-08-25 15:30 | 22.13 | 21.21
2017-08-25 16:00 | 26.04 | 25.39
2017-08-25 16:30 | 33.42 | 32.99
2017-08-25 17:00 | 43.04 | 38.4
2017-08-25 17:30 | 42.37 | 33.62
2017-08-25 18:00 | 63.97 | 39.07
2017-08-25 18:30 | 77.32 | 58.78
2017-08-25 19:00 | 81.69 | 67.66
2017-08-25 19:30 | 73.38 | 59.16
2017-08-25 20:00 | 48.07 | 46.56
2017-08-25 20:30 | 44.36 | 43.24
2017-08-25 21:00 | 35.75 | 35.06
2017-08-25 21:30 | 34.17 | 30.8
2017-08-25 22:00 | 28.53 | 24.23
2017-08-25 22:30 | 28.52 | 24.82
2017-08-25 23:00 | 32.93 | 30.57
2017-08-25 23:30 | 21.04 | 17.7
2017-08-26 | 11.7 | 6.54
2017-08-26 00:30 | 9.08 | -2.48
2017-08-26 01:00 | 6.71 | -6.37
2017-08-26 01:30 | 12.9 | -12.31
2017-08-26 02:00 | 12.32 | -11.87
2017-08-26 02:30 | 11.04 | -10.27
2017-08-26 03:00 | 9.09 | -9.04
2017-08-26 03:30 | 8.64 | -8.63
2017-08-26 04:00 | 7.4 | -7.39
2017-08-26 04:30 | 5.86 | -5.78
2017-08-26 05:00 | 4.49 | -4.29
2017-08-26 05:30 | 3.22 | -1.85
2017-08-26 06:00 | 3.18 | 0.87
2017-08-26 06:30 | 5.68 | 3.98
2017-08-26 07:00 | 8.2 | 6.92
2017-08-26 07:30 | 11.36 | 10.52
2017-08-26 08:00 | 13.9 | 13.21
2017-08-26 08:30 | 15.03 | 14.73
2017-08-26 09:00 | 16.86 | 16.86
2017-08-26 09:30 | 17.43 | 17.42
2017-08-26 10:00 | 16.62 | 16.61
2017-08-26 10:30 | 15.21 | 15.14
2017-08-26 11:00 | 14.57 | 14.49
2017-08-26 11:30 | 12.35 | 12.23
2017-08-26 12:00 | 9.65 | 9.53
2017-08-26 12:30 | 14.16 | 14.15
2017-08-26 13:00 | 18.21 | 18.17
2017-08-26 13:30 | 18.58 | 18.43
2017-08-26 14:00 | 21.52 | 21.29
2017-08-26 14:30 | 20.73 | 20.49
2017-08-26 15:00 | 22.73 | 22.44
2017-08-26 15:30 | 22.11 | 21.85
2017-08-26 16:00 | 25.6 | 25.32
2017-08-26 16:30 | 28.33 | 28.18
2017-08-26 17:00 | 38.21 | 38.17
2017-08-26 17:30 | 50.53 | 50.3
2017-08-26 18:00 | 95.04 | 89.5
2017-08-26 18:30 | 132.8 | 118.62
2017-08-26 19:00 | 138.37 | 125.39
2017-08-26 19:30 | 120.19 | 107.56
2017-08-26 20:00 | 89.31 | 81.56
2017-08-26 20:30 | 78.7 | 70.53
2017-08-26 21:00 | 51.62 | 51.16
2017-08-26 21:30 | 46.63 | 46.6
2017-08-26 22:00 | 41.9 | 41.9
2017-08-26 22:30 | 53.81 | 53.78
2017-08-26 23:00 | 84.99 | 84.85
2017-08-26 23:30 | 56.23 | 56.05
2017-08-27 | 26.17 | 25.67
2017-08-27 00:30 | 16.6 | 14.93
2017-08-27 01:00 | 8.86 | 5.38
2017-08-27 01:30 | 6.03 | -0.33
2017-08-27 02:00 | 3.69 | 1.02
2017-08-27 02:30 | 6.22 | 3.99
2017-08-27 03:00 | 6.84 | 5.22
2017-08-27 03:30 | 6.54 | 5.96
2017-08-27 04:00 | 6.68 | 6.13
2017-08-27 04:30 | 7.12 | 6.51
2017-08-27 05:00 | 7.98 | 7.54
2017-08-27 05:30 | 8.6 | 8.29
2017-08-27 06:00 | 10.95 | 10.73
2017-08-27 06:30 | 12.79 | 12.31
2017-08-27 07:00 | 14.86 | 14.48
2017-08-27 07:30 | 16.83 | 16.82
2017-08-27 08:00 | 23.15 | 23.14
2017-08-27 08:30 | 24.26 | 24.25
2017-08-27 09:00 | 26.1 | 26.1
2017-08-27 09:30 | 24.83 | 24.81
2017-08-27 10:00 | 24.26 | 24.19
2017-08-27 10:30 | 23.83 | 23.72
2017-08-27 11:00 | 28.24 | 28.17
2017-08-27 11:30 | 34.99 | 34.91
2017-08-27 12:00 | 27.11 | 26.99
2017-08-27 12:30 | 26.47 | 26.31
2017-08-27 13:00 | 24.1 | 23.94
2017-08-27 13:30 | 28.72 | 28.49
2017-08-27 14:00 | 2.75 | 1.54
2017-08-27 14:30 | 8.42 | 8.15
2017-08-27 15:00 | 12.65 | 12.05
2017-08-27 15:30 | 16.65 | 15.91
2017-08-27 16:00 | 19.76 | 19.34
2017-08-27 16:30 | 31.65 | 31.57
2017-08-27 17:00 | 49.47 | 49.47
2017-08-27 17:30 | 76.12 | 75.97
2017-08-27 18:00 | 107.68 | 101.7
2017-08-27 18:30 | 147.57 | 134.97
2017-08-27 19:00 | 153.2 | 141.79
2017-08-27 19:30 | 130.15 | 124.69
2017-08-27 20:00 | 114.04 | 108.86
2017-08-27 20:30 | 86.74 | 80.27
2017-08-27 21:00 | 55.49 | 55.42
2017-08-27 21:30 | 48.96 | 48.95
2017-08-27 22:00 | 41.12 | 41.11
2017-08-27 22:30 | 50.24 | 50.15
2017-08-27 23:00 | 66.84 | 66.63
2017-08-27 23:30 | 42.82 | 42.52
2017-08-28 | 22.64 | 21.79
2017-08-28 00:30 | 15.17 | 13.23
2017-08-28 01:00 | 7.77 | 4.29
2017-08-28 01:30 | 2.41 | 0.21
2017-08-28 02:00 | 5.17 | 0.94
2017-08-28 02:30 | 4.58 | 4.15
2017-08-28 03:00 | 5.36 | 5.15
2017-08-28 03:30 | 7.11 | 6.57
2017-08-28 04:00 | 8.77 | 8.76
2017-08-28 04:30 | 12.49 | 12.34
2017-08-28 05:00 | 16.32 | 16.12
2017-08-28 05:30 | 23.07 | 22.6
2017-08-28 06:00 | 30.8 | 30.61
2017-08-28 06:30 | 42.62 | 42.31
2017-08-28 07:00 | 64.98 | 60.62
2017-08-28 07:30 | 91.32 | 88.26
2017-08-28 08:00 | 50.29 | 45.15
2017-08-28 08:30 | 45.66 | 39.98
2017-08-28 09:00 | 41.12 | 35.83
2017-08-28 09:30 | 34.22 | 28.1
2017-08-28 10:00 | 31.87 | 25.93
2017-08-28 10:30 | 24.6 | 19.39
2017-08-28 11:00 | 23.12 | 17.4
2017-08-28 11:30 | 15.29 | 11.92
2017-08-28 12:00 | 14.63 | 13.04
2017-08-28 12:30 | 16.11 | 14.75
2017-08-28 13:00 | 17.07 | 16.07
2017-08-28 13:30 | 16.75 | 16.01
2017-08-28 14:00 | 18.21 | 17.6
2017-08-28 14:30 | 20.43 | 19.93
2017-08-28 15:00 | 20.83 | 20.33
2017-08-28 15:30 | 19.92 | 19.53
2017-08-28 16:00 | 24.59 | 24.16
2017-08-28 16:30 | 28.4 | 28
2017-08-28 17:00 | 34.16 | 32.93
2017-08-28 17:30 | 39.14 | 37.81
2017-08-28 18:00 | 57.73 | 43.58
2017-08-28 18:30 | 71.43 | 47.82
2017-08-28 19:00 | 73.14 | 51.19
2017-08-28 19:30 | 55.8 | 49.18
2017-08-28 20:00 | 49.66 | 47.21
2017-08-28 20:30 | 50.28 | 48.16
2017-08-28 21:00 | 43.07 | 41.63
2017-08-28 21:30 | 36.08 | 35.7
2017-08-28 22:00 | 28.96 | 28.93
2017-08-28 22:30 | 28.05 | 28.05
2017-08-28 23:00 | 31.42 | 31.39
2017-08-28 23:30 | 22.66 | 22.5
2017-08-29 | 11.09 | 10.49
2017-08-29 00:30 | 4.18 | 0.71
2017-08-29 01:00 | 6.09 | -5.82
2017-08-29 01:30 | 9.08 | -9.08
2017-08-29 02:00 | 8.83 | -8.82
2017-08-29 02:30 | 7.35 | -7.27
2017-08-29 03:00 | 6.73 | -6.31
2017-08-29 03:30 | 5.35 | -4.38
2017-08-29 04:00 | 3.95 | -0.58
2017-08-29 04:30 | 5.72 | 2.68
2017-08-29 05:00 | 6.75 | 3.56
2017-08-29 05:30 | 6.99 | 5.97
2017-08-29 06:00 | 13.97 | 13.93
2017-08-29 06:30 | 22.27 | 21.95
2017-08-29 07:00 | 35.01 | 34.1
2017-08-29 07:30 | 50.3 | 49.28
2017-08-29 08:00 | 47.69 | 44.62
2017-08-29 08:30 | 41.67 | 38.4
2017-08-29 09:00 | 41.4 | 35.25
2017-08-29 09:30 | 37.98 | 29.86
2017-08-29 10:00 | 25.33 | 23.51
2017-08-29 10:30 | 18.08 | 17.83
2017-08-29 11:00 | 36.86 | 36.86
2017-08-29 11:30 | 107.85 | 107.8
2017-08-29 12:00 | 105.75 | 105.72
2017-08-29 12:30 | 101.14 | 101.02
2017-08-29 13:00 | 99.67 | 99.47
2017-08-29 13:30 | 100.44 | 100.38
2017-08-29 14:00 | 69.9 | 69.83
2017-08-29 14:30 | 20.7 | 20.33
2017-08-29 15:00 | 20.74 | 20.42
2017-08-29 15:30 | 21.39 | 20.97
2017-08-29 16:00 | 24.85 | 24.52
2017-08-29 16:30 | 28.26 | 27.98
2017-08-29 17:00 | 34.22 | 34.22
2017-08-29 17:30 | 38.09 | 35.16
2017-08-29 18:00 | 51.47 | 44.87
2017-08-29 18:30 | 52.77 | 43.25
2017-08-29 19:00 | 54.5 | 45.91
2017-08-29 19:30 | 57.45 | 46.8
2017-08-29 20:00 | 47.17 | 43.74
2017-08-29 20:30 | 48.26 | 44.81
2017-08-29 21:00 | 40.41 | 39.04
2017-08-29 21:30 | 34.23 | 33.92
2017-08-29 22:00 | 27.27 | 27.22
2017-08-29 22:30 | 23.91 | 23.91
2017-08-29 23:00 | 28.99 | 28.93
2017-08-29 23:30 | 20.89 | 20.8
2017-08-30 | 10.11 | 9.66
2017-08-30 00:30 | 6.37 | 0.82
2017-08-30 01:00 | 8.91 | -5.06
2017-08-30 01:30 | 10.76 | -8.98
2017-08-30 02:00 | 10.18 | -9.07
2017-08-30 02:30 | 8.86 | -7.55
2017-08-30 03:00 | 8.13 | -6.4
2017-08-30 03:30 | 6.55 | -3.39
2017-08-30 04:00 | 6.79 | 0.22
2017-08-30 04:30 | 8 | 1.58
2017-08-30 05:00 | 8.78 | 2.36
2017-08-30 05:30 | 10.56 | 4.84
2017-08-30 06:00 | 14.35 | 12.46
2017-08-30 06:30 | 19.77 | 19.7
2017-08-30 07:00 | 32.86 | 32.83
2017-08-30 07:30 | 66.93 | 66.47
2017-08-30 08:00 | 70.62 | 69.62
2017-08-30 08:30 | 114.98 | 114.47
2017-08-30 09:00 | 42.11 | 39.07
2017-08-30 09:30 | 37.12 | 34.23
2017-08-30 10:00 | 31.63 | 30.46
2017-08-30 10:30 | 27.19 | 26.56
2017-08-30 11:00 | 25.28 | 24.62
2017-08-30 11:30 | 22.23 | 21.42
2017-08-30 12:00 | 20.99 | 20.08
2017-08-30 12:30 | 21.21 | 20.45
2017-08-30 13:00 | 21.51 | 20.08
2017-08-30 13:30 | 22.15 | 19.63
2017-08-30 14:00 | 22.26 | 19.79
2017-08-30 14:30 | 24.85 | 22.49
2017-08-30 15:00 | 23.8 | 21.51
2017-08-30 15:30 | 25.7 | 23.94
2017-08-30 16:00 | 28.69 | 27.06
2017-08-30 16:30 | 34.34 | 32.34
2017-08-30 17:00 | 45.43 | 44.79
2017-08-30 17:30 | 40.48 | 39.78
2017-08-30 18:00 | 66.91 | 66.23
2017-08-30 18:30 | 84 | 78.1
2017-08-30 19:00 | 83.55 | 78.63
2017-08-30 19:30 | 73.35 | 68.36
2017-08-30 20:00 | 60.32 | 57.1
2017-08-30 20:30 | 44.76 | 44.12
2017-08-30 21:00 | 40.68 | 39.62
2017-08-30 21:30 | 40.67 | 40.18
2017-08-30 22:00 | 29.66 | 29.61
2017-08-30 22:30 | 46.87 | 46.71
2017-08-30 23:00 | 52.89 | 52.62
2017-08-30 23:30 | 20.66 | 20.15
2017-08-31 | 7.23 | 5.54
2017-08-31 00:30 | 7.03 | -2.94
2017-08-31 01:00 | 9.59 | -7.68
2017-08-31 01:30 | 10.2 | -9.73
2017-08-31 02:00 | 9.29 | -9.28
2017-08-31 02:30 | 7.84 | -7.81
2017-08-31 03:00 | 6.48 | -6.48
2017-08-31 03:30 | 4.67 | -4.59
2017-08-31 04:00 | 2.42 | -0.92
2017-08-31 04:30 | 4.14 | 1.83
2017-08-31 05:00 | 5.55 | 1.91
2017-08-31 05:30 | 7.76 | 3.55
2017-08-31 06:00 | 12.89 | 10.76
2017-08-31 06:30 | 17.56 | 17.41
2017-08-31 07:00 | 34.21 | 33.73
2017-08-31 07:30 | 54.59 | 54.1
2017-08-31 08:00 | 40.17 | 39.34
2017-08-31 08:30 | 33.85 | 32.54
2017-08-31 09:00 | 31.59 | 30.6
2017-08-31 09:30 | 25.92 | 24.62
2017-08-31 10:00 | 24.41 | 23.22
2017-08-31 10:30 | 18.4 | 16.86
2017-08-31 11:00 | 6.94 | 6.67
2017-08-31 11:30 | 35.43 | 35.02
2017-08-31 12:00 | 39.28 | 38.3
2017-08-31 12:30 | 38.92 | 38
2017-08-31 13:00 | 23.4 | 21.41
2017-08-31 13:30 | 23.32 | 21.4
2017-08-31 14:00 | 26.95 | 25.29
2017-08-31 14:30 | 31.19 | 29.8
2017-08-31 15:00 | 27.92 | 26.82
2017-08-31 15:30 | 24.44 | 23.46
2017-08-31 16:00 | 26.56 | 25.75
2017-08-31 16:30 | 27.67 | 27.02
2017-08-31 17:00 | 31.47 | 28.91
2017-08-31 17:30 | 35.33 | 33.11
2017-08-31 18:00 | 50.79 | 48.85
2017-08-31 18:30 | 84.18 | 69.09
2017-08-31 19:00 | 91.49 | 80.31
2017-08-31 19:30 | 73.22 | 67.42
2017-08-31 20:00 | 68.61 | 62.67
2017-08-31 20:30 | 50.57 | 44.09
2017-08-31 21:00 | 37.63 | 37.15
2017-08-31 21:30 | 33.01 | 32.8
2017-08-31 22:00 | 24.43 | 24.33
2017-08-31 22:30 | 29.95 | 29.95
2017-08-31 23:00 | 33.49 | 33.34
2017-08-31 23:30 | 18.94 | 18.43
2017-09-01 | 8.31 | 6.21
2017-09-01 00:30 | 6.97 | -3.41
2017-09-01 01:00 | 10.26 | -9.17
2017-09-01 01:30 | 13.12 | -12.61
2017-09-01 02:00 | 12.44 | -12.43
2017-09-01 02:30 | 11.12 | -11.11
2017-09-01 03:00 | 9.9 | -9.89
2017-09-01 03:30 | 8.17 | -8.16
2017-09-01 04:00 | 6.34 | -6.28
2017-09-01 04:30 | 5.31 | -4.75
2017-09-01 05:00 | 4.56 | -3.42
2017-09-01 05:30 | 6.83 | -2.81
2017-09-01 06:00 | 5.71 | -1.4
2017-09-01 06:30 | 6.46 | -1.38
2017-09-01 07:00 | 9.4 | 6.28
2017-09-01 07:30 | 14.42 | 14.06
2017-09-01 08:00 | 15.93 | 15.93
2017-09-01 08:30 | 20.23 | 20.04
2017-09-01 09:00 | 23.36 | 22.83
2017-09-01 09:30 | 20.99 | 20.69
2017-09-01 10:00 | 19.26 | 19.1
2017-09-01 10:30 | 12.42 | 12.37
2017-09-01 11:00 | 14.09 | 14.06
2017-09-01 11:30 | 29.18 | 28.9
2017-09-01 12:00 | 28.69 | 28.36
2017-09-01 12:30 | 25.81 | 25.62
2017-09-01 13:00 | 20.76 | 20.73
2017-09-01 13:30 | 21.68 | 21.64
2017-09-01 14:00 | 24.1 | 24.06
2017-09-01 14:30 | 28.81 | 28.78
2017-09-01 15:00 | 27.2 | 27.17
2017-09-01 15:30 | 29.51 | 29.5
2017-09-01 16:00 | 35.37 | 35.37
2017-09-01 16:30 | 39.32 | 39.11
2017-09-01 17:00 | 49.54 | 49.47
2017-09-01 17:30 | 57.35 | 57.35
2017-09-01 18:00 | 61.84 | 61.55
2017-09-01 18:30 | 80.16 | 79.22
2017-09-01 19:00 | 105.05 | 104.8
2017-09-01 19:30 | 96.29 | 96.15
2017-09-01 20:00 | 82.51 | 82.4
2017-09-01 20:30 | 68.15 | 68.14
2017-09-01 21:00 | 54.24 | 54.23
2017-09-01 21:30 | 53.11 | 53.09
2017-09-01 22:00 | 42.45 | 42.33
2017-09-01 22:30 | 45.18 | 45.02
2017-09-01 23:00 | 61.21 | 61.02
2017-09-01 23:30 | 38 | 37.58
2017-09-02 | 16.76 | 16.27
2017-09-02 00:30 | 5.94 | 3.58
2017-09-02 01:00 | 9.82 | -6.71
2017-09-02 01:30 | 16.5 | -13.74
2017-09-02 02:00 | 13.09 | -8.86
2017-09-02 02:30 | 10.51 | -4.67
2017-09-02 03:00 | 9.25 | -1.86
2017-09-02 03:30 | 25.92 | 0.24
2017-09-02 04:00 | 25.35 | 1.38
2017-09-02 04:30 | 23.46 | -0.98
2017-09-02 05:00 | 21.27 | 0.78
2017-09-02 05:30 | 19.45 | 2.35
2017-09-02 06:00 | 18.72 | 4.93
2017-09-02 06:30 | 19.04 | 7.35
2017-09-02 07:00 | 18.68 | 11.52
2017-09-02 07:30 | 19.93 | 15.04
2017-09-02 08:00 | 19.94 | 16.8
2017-09-02 08:30 | 22.99 | 18.77
2017-09-02 09:00 | 21.4 | 21.25
2017-09-02 09:30 | 22.62 | 22.41
2017-09-02 10:00 | 20.74 | 20.6
2017-09-02 10:30 | 21 | 20.91
2017-09-02 11:00 | 22.93 | 22.8
2017-09-02 11:30 | 25.86 | 25.69
2017-09-02 12:00 | 23.2 | 23.04
2017-09-02 12:30 | 20.21 | 20.05
2017-09-02 13:00 | 16.92 | 16.73
2017-09-02 13:30 | 15.57 | 15.41
2017-09-02 14:00 | 19.05 | 18.94
2017-09-02 14:30 | 22.62 | 22.53
2017-09-02 15:00 | 21.25 | 21.17
2017-09-02 15:30 | 22.52 | 22.47
2017-09-02 16:00 | 28.09 | 28.05
2017-09-02 16:30 | 34.96 | 33.49
2017-09-02 17:00 | 48.84 | 44.03
2017-09-02 17:30 | 52.28 | 47.46
2017-09-02 18:00 | 82 | 72.55
2017-09-02 18:30 | 125.68 | 112.56
2017-09-02 19:00 | 116.69 | 102.79
2017-09-02 19:30 | 120.28 | 107.82
2017-09-02 20:00 | 104.35 | 90.66
2017-09-02 20:30 | 92.36 | 88.75
2017-09-02 21:00 | 82.7 | 81.14
2017-09-02 21:30 | 68.33 | 66.83
2017-09-02 22:00 | 50.82 | 49.18
2017-09-02 22:30 | 80.51 | 79.71
2017-09-02 23:00 | 95.17 | 94.64
2017-09-02 23:30 | 66.02 | 65.44
2017-09-03 | 27.36 | 25.38
2017-09-03 00:30 | 12.38 | -1.1
2017-09-03 01:00 | 17.15 | -11.37
2017-09-03 01:30 | 19.6 | -18.32
2017-09-03 02:00 | 16.01 | -14.96
2017-09-03 02:30 | 14.69 | -13.64
2017-09-03 03:00 | 17.95 | -17.15
2017-09-03 03:30 | 13.35 | -12.22
2017-09-03 04:00 | 11.92 | -10.82
2017-09-03 04:30 | 17.73 | -16.79
2017-09-03 05:00 | 18.24 | -17.25
2017-09-03 05:30 | 12.21 | -10.6
2017-09-03 06:00 | 11.22 | -9.72
2017-09-03 06:30 | 10.12 | -8.72
2017-09-03 07:00 | 5.98 | -3.55
2017-09-03 07:30 | 5.66 | 2.67
2017-09-03 08:00 | 8.03 | 5.97
2017-09-03 08:30 | 8.09 | 6.81
2017-09-03 09:00 | 8.9 | 8.5
2017-09-03 09:30 | 13.26 | 13.18
2017-09-03 10:00 | 13.52 | 13.51
2017-09-03 10:30 | 14.9 | 14.84
2017-09-03 11:00 | 7.94 | 7.8
2017-09-03 11:30 | 7.92 | 7.73
2017-09-03 12:00 | 8.48 | 8.32
2017-09-03 12:30 | 4.18 | 4.05
2017-09-03 13:00 | 2.57 | 2.22
2017-09-03 13:30 | 4.31 | 4
2017-09-03 14:00 | 6.22 | 5.99
2017-09-03 14:30 | 14.67 | 14.49
2017-09-03 15:00 | 12.4 | 12.26
2017-09-03 15:30 | 13.56 | 13.47
2017-09-03 16:00 | 25.49 | 25.47
2017-09-03 16:30 | 52.05 | 51.91
2017-09-03 17:00 | 85.73 | 83.71
2017-09-03 17:30 | 117.21 | 115.69
2017-09-03 18:00 | 128.81 | 125.28
2017-09-03 18:30 | 164.72 | 154.85
2017-09-03 19:00 | 162.77 | 153.31
2017-09-03 19:30 | 136.47 | 125.84
2017-09-03 20:00 | 121.2 | 109.7
2017-09-03 20:30 | 109.09 | 97.2
2017-09-03 21:00 | 88.69 | 74.67
2017-09-03 21:30 | 51.69 | 47.42
2017-09-03 22:00 | 26.04 | 22.33
2017-09-03 22:30 | 56.97 | 55.87
2017-09-03 23:00 | 71.29 | 70.54
2017-09-03 23:30 | 41.54 | 40.46
2017-09-04 | 12.33 | 4.62
2017-09-04 00:30 | 13.83 | -5.86
2017-09-04 01:00 | 16.86 | -10.33
2017-09-04 01:30 | 22.12 | -17.28
2017-09-04 02:00 | 10.66 | -10.41
2017-09-04 02:30 | 8.03 | -6.97
2017-09-04 03:00 | 8.44 | -7.86
2017-09-04 03:30 | 8.34 | -7.08
2017-09-04 04:00 | 7.19 | -4.15
2017-09-04 04:30 | 6.56 | -1.08
2017-09-04 05:00 | 7.37 | -1.78
2017-09-04 05:30 | 18.06 | 16.6
2017-09-04 06:00 | 66.87 | 66.4
2017-09-04 06:30 | 86.35 | 86.09
2017-09-04 07:00 | 103.22 | 103.18
2017-09-04 07:30 | 102.74 | 102.74
2017-09-04 08:00 | 77.35 | 75.35
2017-09-04 08:30 | 61.58 | 55.94
2017-09-04 09:00 | 50.02 | 39.81
2017-09-04 09:30 | 49.28 | 36.35
2017-09-04 10:00 | 48.19 | 33.68
2017-09-04 10:30 | 44.31 | 26.95
2017-09-04 11:00 | 42.85 | 23.71
2017-09-04 11:30 | 44.32 | 24.44
2017-09-04 12:00 | 48.5 | 26.99
2017-09-04 12:30 | 49.87 | 28.44
2017-09-04 13:00 | 52.29 | 32.35
2017-09-04 13:30 | 77.61 | 39.63
2017-09-04 14:00 | 104.38 | 54.87
2017-09-04 14:30 | 107.8 | 64.61
2017-09-04 15:00 | 115.95 | 78.14
2017-09-04 15:30 | 126.61 | 95.72
2017-09-04 16:00 | 142.1 | 116.34
2017-09-04 16:30 | 148.09 | 124.45
2017-09-04 17:00 | 150.58 | 128.32
2017-09-04 17:30 | 156.57 | 136.25
2017-09-04 18:00 | 186.99 | 169.22
2017-09-04 18:30 | 210.3 | 194.06
2017-09-04 19:00 | 216.05 | 201.33
2017-09-04 19:30 | 189.69 | 175.22
2017-09-04 20:00 | 174.09 | 158.03
2017-09-04 20:30 | 158.93 | 142.71
2017-09-04 21:00 | 115.37 | 102.31
2017-09-04 21:30 | 89.26 | 75.95
2017-09-04 22:00 | 60.74 | 41.74
2017-09-04 22:30 | 68.25 | 67.26
2017-09-04 23:00 | 83.46 | 82.78
2017-09-04 23:30 | 51.84 | 50.89
2017-09-05 | 16.22 | 12.58
2017-09-05 00:30 | 11.52 | 1.81
2017-09-05 01:00 | 19.44 | -15.09
2017-09-05 01:30 | 24.09 | -20.5
2017-09-05 02:00 | 22.3 | -18.59
2017-09-05 02:30 | 19.02 | -16.78
2017-09-05 03:00 | 15.99 | -13.69
2017-09-05 03:30 | 11.57 | -7.94
2017-09-05 04:00 | 11.9 | -7.83
2017-09-05 04:30 | 10.92 | -2.81
2017-09-05 05:00 | 11.2 | 2.63
2017-09-05 05:30 | 10.16 | 2.87
2017-09-05 06:00 | 11.11 | 8.33
2017-09-05 06:30 | 21.63 | 20.71
2017-09-05 07:00 | 42 | 41.73
2017-09-05 07:30 | 64.89 | 63.65
2017-09-05 08:00 | 55.45 | 53.11
2017-09-05 08:30 | 45.59 | 44.82
2017-09-05 09:00 | 38.81 | 37.57
2017-09-05 09:30 | 34.47 | 32.46
2017-09-05 10:00 | 30.49 | 27.26
2017-09-05 10:30 | 29.1 | 25.01
2017-09-05 11:00 | 27.01 | 22.89
2017-09-05 11:30 | 25.54 | 21.2
2017-09-05 12:00 | 23.75 | 18.9
2017-09-05 12:30 | 33.16 | 20.63
2017-09-05 13:00 | 38.16 | 21.36
2017-09-05 13:30 | 40.86 | 25.33
2017-09-05 14:00 | 44.27 | 29.57
2017-09-05 14:30 | 48.76 | 35.65
2017-09-05 15:00 | 48.43 | 35.43
2017-09-05 15:30 | 54.04 | 43.11
2017-09-05 16:00 | 65.07 | 52.17
2017-09-05 16:30 | 87.61 | 81.4
2017-09-05 17:00 | 110.78 | 106.42
2017-09-05 17:30 | 132.72 | 129.57
2017-09-05 18:00 | 138.83 | 135.06
2017-09-05 18:30 | 149.22 | 138.64
2017-09-05 19:00 | 149.38 | 143.2
2017-09-05 19:30 | 130.27 | 122.53
2017-09-05 20:00 | 111.25 | 97.01
2017-09-05 20:30 | 106.36 | 92.38
2017-09-05 21:00 | 72.65 | 65.1
2017-09-05 21:30 | 65.97 | 63.82
2017-09-05 22:00 | 45.71 | 43.42
2017-09-05 22:30 | 68.93 | 67.71
2017-09-05 23:00 | 79.76 | 78.78
2017-09-05 23:30 | 39.48 | 37.67
2017-09-06 | 18.21 | 12.56
2017-09-06 00:30 | 14 | -0.16
2017-09-06 01:00 | 16.49 | -9.05
2017-09-06 01:30 | 19.04 | -12.82
2017-09-06 02:00 | 16.59 | -9.12
2017-09-06 02:30 | 4.82 | -3.39
2017-09-06 03:00 | 4.21 | -0.03
2017-09-06 03:30 | 5.47 | 2.27
2017-09-06 04:00 | 9.01 | 6.66
2017-09-06 04:30 | 12.73 | 10.59
2017-09-06 05:00 | 14.84 | 12.48
2017-09-06 05:30 | 19.64 | 17.71
2017-09-06 06:00 | 29.91 | 28.54
2017-09-06 06:30 | 55.68 | 55.12
2017-09-06 07:00 | 88.78 | 88.6
2017-09-06 07:30 | 117.28 | 115.61
2017-09-06 08:00 | 90.17 | 85.17
2017-09-06 08:30 | 66.58 | 58.19
2017-09-06 09:00 | 62.05 | 52.16
2017-09-06 09:30 | 56.1 | 44.5
2017-09-06 10:00 | 53.85 | 41.04
2017-09-06 10:30 | 51.32 | 36.3
2017-09-06 11:00 | 51.41 | 36.05
2017-09-06 11:30 | 50.56 | 34.14
2017-09-06 12:00 | 50.89 | 34.04
2017-09-06 12:30 | 52.35 | 36.02
2017-09-06 13:00 | 52.73 | 36.21
2017-09-06 13:30 | 54.93 | 39.09
2017-09-06 14:00 | 56.77 | 41.45
2017-09-06 14:30 | 58.13 | 43.68
2017-09-06 15:00 | 59.12 | 45.54
2017-09-06 15:30 | 60.58 | 47.68
2017-09-06 16:00 | 64.17 | 52.59
2017-09-06 16:30 | 76.34 | 67.48
2017-09-06 17:00 | 98.67 | 92.87
2017-09-06 17:30 | 111.69 | 107.17
2017-09-06 18:00 | 110.87 | 106.1
2017-09-06 18:30 | 126.95 | 125.4
2017-09-06 19:00 | 133.47 | 132.22
2017-09-06 19:30 | 111.25 | 110.2
2017-09-06 20:00 | 87.84 | 86.71
2017-09-06 20:30 | 79.33 | 77.88
2017-09-06 21:00 | 63.55 | 61
2017-09-06 21:30 | 58.75 | 56.54
2017-09-06 22:00 | 45.85 | 44.05
2017-09-06 22:30 | 56.28 | 55.37
2017-09-06 23:00 | 65.12 | 64.56
2017-09-06 23:30 | 40.13 | 39.12
2017-09-07 | 17.33 | 14.13
2017-09-07 00:30 | 11.01 | 0.07
2017-09-07 01:00 | 15 | -9.34
2017-09-07 01:30 | 19.71 | -15.45
2017-09-07 02:00 | 15.45 | -9.52
2017-09-07 02:30 | 11.74 | -3.65
2017-09-07 03:00 | 9.86 | -0.32
2017-09-07 03:30 | 9.86 | 3.51
2017-09-07 04:00 | 10.38 | 6.54
2017-09-07 04:30 | 12.13 | 9.89
2017-09-07 05:00 | 15.37 | 13.65
2017-09-07 05:30 | 20.08 | 18.72
2017-09-07 06:00 | 49.08 | 48.82
2017-09-07 06:30 | 75.24 | 74.75
2017-09-07 07:00 | 97.61 | 97.56
2017-09-07 07:30 | 93.94 | 93.94
2017-09-07 08:00 | 78.16 | 78.08
2017-09-07 08:30 | 72.86 | 72.7
2017-09-07 09:00 | 71.39 | 71.03
2017-09-07 09:30 | 63.01 | 62.51
2017-09-07 10:00 | 46.29 | 45.37
2017-09-07 10:30 | 36.66 | 35.11
2017-09-07 11:00 | 35.83 | 33.65
2017-09-07 11:30 | 34.64 | 32.29
2017-09-07 12:00 | 34.69 | 32.32
2017-09-07 12:30 | 35.85 | 33.64
2017-09-07 13:00 | 42.87 | 35.57
2017-09-07 13:30 | 46.57 | 36.57
2017-09-07 14:00 | 48.74 | 39.39
2017-09-07 14:30 | 51.3 | 42.55
2017-09-07 15:00 | 50.63 | 42.32
2017-09-07 15:30 | 52.23 | 43.26
2017-09-07 16:00 | 66.77 | 49.22
2017-09-07 16:30 | 79.9 | 57.56
2017-09-07 17:00 | 101.22 | 71.93
2017-09-07 17:30 | 105.24 | 78.13
2017-09-07 18:00 | 117.03 | 91.72
2017-09-07 18:30 | 143.76 | 123.1
2017-09-07 19:00 | 152.75 | 133.77
2017-09-07 19:30 | 134.32 | 113.78
2017-09-07 20:00 | 119.71 | 97.29
2017-09-07 20:30 | 112.54 | 89.05
2017-09-07 21:00 | 101.32 | 75.52
2017-09-07 21:30 | 89.06 | 67.06
2017-09-07 22:00 | 59.89 | 52.63
2017-09-07 22:30 | 54.98 | 53.23
2017-09-07 23:00 | 65.66 | 64.61
2017-09-07 23:30 | 39.77 | 38.23
2017-09-08 | 24.43 | 21.38
2017-09-08 00:30 | 16.72 | 11.5
2017-09-08 01:00 | 12.86 | 1.32
2017-09-08 01:30 | 13.77 | -3.76
2017-09-08 02:00 | 14.75 | -5.72
2017-09-08 02:30 | 14.5 | -4.13
2017-09-08 03:00 | 12.83 | 1.6
2017-09-08 03:30 | 12.42 | 3.48
2017-09-08 04:00 | 12.71 | 6.18
2017-09-08 04:30 | 13.84 | 8.43
2017-09-08 05:00 | 16.62 | 12.54
2017-09-08 05:30 | 21.23 | 18.25
2017-09-08 06:00 | 38.68 | 37.21
2017-09-08 06:30 | 50.43 | 49.27
2017-09-08 07:00 | 74.91 | 73.54
2017-09-08 07:30 | 78.95 | 76.15
2017-09-08 08:00 | 68.74 | 63.76
2017-09-08 08:30 | 64.19 | 57.63
2017-09-08 09:00 | 60.99 | 53.32
2017-09-08 09:30 | 54.04 | 44.65
2017-09-08 10:00 | 51.62 | 41.34
2017-09-08 10:30 | 47.46 | 35.34
2017-09-08 11:00 | 47.55 | 34.98
2017-09-08 11:30 | 47.25 | 34.14
2017-09-08 12:00 | 46.66 | 32.83
2017-09-08 12:30 | 47.78 | 34.09
2017-09-08 13:00 | 49.88 | 36.94
2017-09-08 13:30 | 50.65 | 38.61
2017-09-08 14:00 | 51.1 | 40.54
2017-09-08 14:30 | 51.32 | 41.36
2017-09-08 15:00 | 51.43 | 41.82
2017-09-08 15:30 | 50.57 | 42.15
2017-09-08 16:00 | 64.39 | 47.74
2017-09-08 16:30 | 91.17 | 55.92
2017-09-08 17:00 | 97.79 | 67.32
2017-09-08 17:30 | 105.26 | 78.13
2017-09-08 18:00 | 112.56 | 84.77
2017-09-08 18:30 | 101.85 | 99.58
2017-09-08 19:00 | 104.95 | 102.88
2017-09-08 19:30 | 88.02 | 85.87
2017-09-08 20:00 | 79.9 | 79.69
2017-09-08 20:30 | 79.43 | 79.14
2017-09-08 21:00 | 70.04 | 69.74
2017-09-08 21:30 | 65.13 | 64.28
2017-09-08 22:00 | 55.7 | 53.18
2017-09-08 22:30 | 58.26 | 56.27
2017-09-08 23:00 | 62.32 | 60.78
2017-09-08 23:30 | 44.44 | 42.32
2017-09-09 | 30.69 | 27.08
2017-09-09 00:30 | 21.89 | 15.93
2017-09-09 01:00 | 15.99 | 4.23
2017-09-09 01:30 | 15.84 | -0.87
2017-09-09 02:00 | 5.45 | -3.41
2017-09-09 02:30 | 4.45 | -4.38
2017-09-09 03:00 | 0.72 | -0.67
2017-09-09 03:30 | 0.83 | 0.7
2017-09-09 04:00 | 3.26 | 3.24
2017-09-09 04:30 | 5.52 | 5.48
2017-09-09 05:00 | 7.51 | 7.4
2017-09-09 05:30 | 9.77 | 9.56
2017-09-09 06:00 | 13.01 | 12.79
2017-09-09 06:30 | 16.48 | 16.18
2017-09-09 07:00 | 20.4 | 19.91
2017-09-09 07:30 | 26.12 | 25.6
2017-09-09 08:00 | 29.23 | 29.07
2017-09-09 08:30 | 32.21 | 32.18
2017-09-09 09:00 | 30.22 | 30.14
2017-09-09 09:30 | 29.7 | 29.52
2017-09-09 10:00 | 28.9 | 28.68
2017-09-09 10:30 | 28.65 | 28.37
2017-09-09 11:00 | 26.75 | 26.3
2017-09-09 11:30 | 25.83 | 25.42
2017-09-09 12:00 | 23.61 | 23.34
2017-09-09 12:30 | 21.97 | 21.79
2017-09-09 13:00 | 20.68 | 20.53
2017-09-09 13:30 | 21.66 | 21.53
2017-09-09 14:00 | 24.72 | 24.61
2017-09-09 14:30 | 26.32 | 26.23
2017-09-09 15:00 | 28.52 | 28.45
2017-09-09 15:30 | 29.23 | 29.17
2017-09-09 16:00 | 34.41 | 34.37
2017-09-09 16:30 | 43.05 | 42.49
2017-09-09 17:00 | 58.56 | 54.74
2017-09-09 17:30 | 66.08 | 62.79
2017-09-09 18:00 | 82.83 | 74.9
2017-09-09 18:30 | 96.71 | 86.92
2017-09-09 19:00 | 106.95 | 98.85
2017-09-09 19:30 | 91.32 | 82.1
2017-09-09 20:00 | 86.13 | 76.62
2017-09-09 20:30 | 75.48 | 71.55
2017-09-09 21:00 | 62.09 | 60.08
2017-09-09 21:30 | 53.46 | 53.45
2017-09-09 22:00 | 46.9 | 46.77
2017-09-09 22:30 | 88.97 | 88.8
2017-09-09 23:00 | 103.33 | 102.94
2017-09-09 23:30 | 74.75 | 74.26
2017-09-10 | 26.47 | 26.28
2017-09-10 00:30 | 13.93 | 13.91
2017-09-10 01:00 | 6.2 | 5.81
2017-09-10 01:30 | 3.61 | 0.16
2017-09-10 02:00 | 4.26 | 0.7
2017-09-10 02:30 | 4.91 | 2.95
2017-09-10 03:00 | 8.53 | 3.55
2017-09-10 03:30 | 20.64 | 4.54
2017-09-10 04:00 | 20.48 | 3.89
2017-09-10 04:30 | 20.67 | 4.15
2017-09-10 05:00 | 20.65 | 4.34
2017-09-10 05:30 | 19.75 | 6.17
2017-09-10 06:00 | 22.24 | 8.49
2017-09-10 06:30 | 22.93 | 9.34
2017-09-10 07:00 | 23.36 | 10.25
2017-09-10 07:30 | 22.91 | 14.43
2017-09-10 08:00 | 22.43 | 16.44
2017-09-10 08:30 | 22.75 | 18.09
2017-09-10 09:00 | 26.23 | 20.92
2017-09-10 09:30 | 27.54 | 23.28
2017-09-10 10:00 | 26.83 | 23.3
2017-09-10 10:30 | 25.12 | 21.63
2017-09-10 11:00 | 25.74 | 22.86
2017-09-10 11:30 | 24.46 | 21.04
2017-09-10 12:00 | 23.83 | 20.36
2017-09-10 12:30 | 22.46 | 18.48
2017-09-10 13:00 | 22.35 | 18.06
2017-09-10 13:30 | 23.61 | 19.82
2017-09-10 14:00 | 24.89 | 21.42
2017-09-10 14:30 | 26.04 | 23.02
2017-09-10 15:00 | 26.73 | 23.96
2017-09-10 15:30 | 28.49 | 26.39
2017-09-10 16:00 | 31.7 | 31.7
2017-09-10 16:30 | 41.41 | 41.3
2017-09-10 17:00 | 51.2 | 51.09
2017-09-10 17:30 | 61.91 | 60.53
2017-09-10 18:00 | 77.89 | 74.75
2017-09-10 18:30 | 108.52 | 106.16
2017-09-10 19:00 | 120.32 | 118.12
2017-09-10 19:30 | 111.29 | 108.88
2017-09-10 20:00 | 95.32 | 94.74
2017-09-10 20:30 | 77.7 | 77.5
2017-09-10 21:00 | 59.75 | 59.61
2017-09-10 21:30 | 53.55 | 53.5
2017-09-10 22:00 | 40.87 | 40.87
2017-09-10 22:30 | 50.78 | 50.75
2017-09-10 23:00 | 59.92 | 59.85
2017-09-10 23:30 | 37.57 | 37.46
2017-09-11 | 19.81 | 19.8
2017-09-11 00:30 | 11.48 | 9.61
2017-09-11 01:00 | 7.72 | 3.36
2017-09-11 01:30 | 7.26 | -0.68
2017-09-11 02:00 | 6.62 | 1.9
2017-09-11 02:30 | 7.22 | 3.85
2017-09-11 03:00 | 20.07 | 5.47
2017-09-11 03:30 | 23.09 | 7.54
2017-09-11 04:00 | 23 | 6.03
2017-09-11 04:30 | 21.95 | 7.11
2017-09-11 05:00 | 21.91 | 10.6
2017-09-11 05:30 | 21.89 | 16.07
2017-09-11 06:00 | 43.69 | 42.07
2017-09-11 06:30 | 70.6 | 70.16
2017-09-11 07:00 | 85.07 | 85.06
2017-09-11 07:30 | 104.09 | 104.05
2017-09-11 08:00 | 87.04 | 87.04
2017-09-11 08:30 | 58.37 | 57.58
2017-09-11 09:00 | 51.36 | 50.8
2017-09-11 09:30 | 43.98 | 42.89
2017-09-11 10:00 | 42.12 | 41.15
2017-09-11 10:30 | 34.29 | 33.59
2017-09-11 11:00 | 38 | 37.82
2017-09-11 11:30 | 35.48 | 35.3
2017-09-11 12:00 | 36.92 | 36.78
2017-09-11 12:30 | 36.82 | 36.79
2017-09-11 13:00 | 32.52 | 32.44
2017-09-11 13:30 | 33.31 | 33.25
2017-09-11 14:00 | 38.39 | 38.39
2017-09-11 14:30 | 42.83 | 42.81
2017-09-11 15:00 | 46.38 | 45.82
2017-09-11 15:30 | 49.61 | 47.65
2017-09-11 16:00 | 54.7 | 52.87
2017-09-11 16:30 | 80.13 | 79.06
2017-09-11 17:00 | 124.12 | 123.7
2017-09-11 17:30 | 129.26 | 128.67
2017-09-11 18:00 | 130.18 | 128.99
2017-09-11 18:30 | 164.27 | 163.94
2017-09-11 19:00 | 174.65 | 174.31
2017-09-11 19:30 | 154.86 | 154.74
2017-09-11 20:00 | 146.33 | 146.33
2017-09-11 20:30 | 128.92 | 128.9
2017-09-11 21:00 | 105.67 | 105.61
2017-09-11 21:30 | 109.57 | 109.53
2017-09-11 22:00 | 88.88 | 88.87
2017-09-11 22:30 | 107.78 | 107.74
2017-09-11 23:00 | 115.87 | 115.79
2017-09-11 23:30 | 80.49 | 80.31
2017-09-12 | 39.23 | 39.11
2017-09-12 00:30 | 19.37 | 19.11
2017-09-12 01:00 | 6.54 | -6.52
2017-09-12 01:30 | 14.43 | -14.25
2017-09-12 02:00 | 9.95 | -9.61
2017-09-12 02:30 | 5.77 | -5.09
2017-09-12 03:00 | 3.39 | -1.16
2017-09-12 03:30 | 3.57 | 1.91
2017-09-12 04:00 | 5.16 | 4.63
2017-09-12 04:30 | 6.83 | 6.8
2017-09-12 05:00 | 8.83 | 8.8
2017-09-12 05:30 | 18.4 | 17.62
2017-09-12 06:00 | 37.08 | 36.33
2017-09-12 06:30 | 41.88 | 40.41
2017-09-12 07:00 | 78.48 | 77.82
2017-09-12 07:30 | 92.93 | 92.8
2017-09-12 08:00 | 81.28 | 80.15
2017-09-12 08:30 | 54.79 | 52.98
2017-09-12 09:00 | 50.67 | 49.7
2017-09-12 09:30 | 43.48 | 43.43
2017-09-12 10:00 | 42.59 | 42.57
2017-09-12 10:30 | 38.49 | 38.47
2017-09-12 11:00 | 38.87 | 38.85
2017-09-12 11:30 | 37.35 | 37.25
2017-09-12 12:00 | 40.19 | 40.05
2017-09-12 12:30 | 41.13 | 40.89
2017-09-12 13:00 | 45.42 | 45.07
2017-09-12 13:30 | 46.62 | 46.36
2017-09-12 14:00 | 49.98 | 49.73
2017-09-12 14:30 | 53.1 | 52.94
2017-09-12 15:00 | 56.42 | 56.41
2017-09-12 15:30 | 57.85 | 57.85
2017-09-12 16:00 | 86.28 | 86.23
2017-09-12 16:30 | 112.21 | 112.16
2017-09-12 17:00 | 117.9 | 117.83
2017-09-12 17:30 | 131.33 | 131.33
2017-09-12 18:00 | 146.06 | 146.04
2017-09-12 18:30 | 180.02 | 179.97
2017-09-12 19:00 | 190.7 | 190.06
2017-09-12 19:30 | 157.17 | 156.59
2017-09-12 20:00 | 135.41 | 135.01
2017-09-12 20:30 | 123.05 | 122.86
2017-09-12 21:00 | 99.68 | 97.78
2017-09-12 21:30 | 97.61 | 95.95
2017-09-12 22:00 | 79.12 | 77.68
2017-09-12 22:30 | 94.73 | 93.78
2017-09-12 23:00 | 100.38 | 99.7
2017-09-12 23:30 | 70.62 | 69.85
2017-09-13 | 26 | 22.38
2017-09-13 00:30 | 15 | 0.68
2017-09-13 01:00 | 17.49 | -7.57
2017-09-13 01:30 | 19.6 | -11.23
2017-09-13 02:00 | 17.4 | -6.49
2017-09-13 02:30 | 12.08 | -0.74
2017-09-13 03:00 | 2.6 | 1.88
2017-09-13 03:30 | 4.71 | 4.35
2017-09-13 04:00 | 7.45 | 6.77
2017-09-13 04:30 | 10.49 | 9.29
2017-09-13 05:00 | 12.87 | 11.76
2017-09-13 05:30 | 19.74 | 18.28
2017-09-13 06:00 | 45.56 | 44.43
2017-09-13 06:30 | 68.89 | 68.16
2017-09-13 07:00 | 101.16 | 100.96
2017-09-13 07:30 | 139.66 | 138.72
2017-09-13 08:00 | 124.08 | 121.95
2017-09-13 08:30 | 98.91 | 95.59
2017-09-13 09:00 | 75.22 | 68.94
2017-09-13 09:30 | 61.75 | 52.26
2017-09-13 10:00 | 61.07 | 47.86
2017-09-13 10:30 | 75.8 | 44.82
2017-09-13 11:00 | 97.13 | 45.87
2017-09-13 11:30 | 98.34 | 47.15
2017-09-13 12:00 | 80 | 46.62
2017-09-13 12:30 | 81.09 | 50.58
2017-09-13 13:00 | 84.07 | 56.17
2017-09-13 13:30 | 82.52 | 52.73
2017-09-13 14:00 | 88.9 | 61.56
2017-09-13 14:30 | 94.5 | 69.36
2017-09-13 15:00 | 99.35 | 76.21
2017-09-13 15:30 | 110.56 | 91.03
2017-09-13 16:00 | 139.8 | 125.76
2017-09-13 16:30 | 159.89 | 148.51
2017-09-13 17:00 | 163.75 | 153.26
2017-09-13 17:30 | 175.49 | 166.34
2017-09-13 18:00 | 172.52 | 162.86
2017-09-13 18:30 | 195.53 | 186.75
2017-09-13 19:00 | 205.54 | 197.57
2017-09-13 19:30 | 178.64 | 170.39
2017-09-13 20:00 | 167.33 | 158.94
2017-09-13 20:30 | 165.98 | 158.43
2017-09-13 21:00 | 148.99 | 146.99
2017-09-13 21:30 | 133.94 | 133.25
2017-09-13 22:00 | 95.35 | 94.94
2017-09-13 22:30 | 136.48 | 136.32
2017-09-13 23:00 | 153.66 | 153.59
2017-09-13 23:30 | 128.87 | 128.86
2017-09-14 | 76.79 | 76.72
2017-09-14 00:30 | 48.56 | 46.5
2017-09-14 01:00 | 6.85 | 6.85
2017-09-14 01:30 | 11.76 | -11.72
2017-09-14 02:00 | 7.54 | -7.54
2017-09-14 02:30 | 3.75 | -2.72
2017-09-14 03:00 | 2.72 | 0.64
2017-09-14 03:30 | 3.73 | 2.34
2017-09-14 04:00 | 5.47 | 4.38
2017-09-14 04:30 | 9.6 | 8.21
2017-09-14 05:00 | 11.68 | 10.26
2017-09-14 05:30 | 18.53 | 17.59
2017-09-14 06:00 | 39.33 | 38.72
2017-09-14 06:30 | 52 | 51.72
2017-09-14 07:00 | 76.84 | 76.74
2017-09-14 07:30 | 98.32 | 98.28
2017-09-14 08:00 | 107.94 | 107.94
2017-09-14 08:30 | 112.56 | 112.43
2017-09-14 09:00 | 98.58 | 98.36
2017-09-14 09:30 | 62.4 | 61.63
2017-09-14 10:00 | 52.11 | 50.95
2017-09-14 10:30 | 39.97 | 38.84
2017-09-14 11:00 | 34.75 | 34.75
2017-09-14 11:30 | 37.72 | 37.65
2017-09-14 12:00 | 7.88 | -7.87
2017-09-14 12:30 | 21.85 | -21.84
2017-09-14 13:00 | 40.18 | -40.17
2017-09-14 13:30 | 40.44 | -40.43
2017-09-14 14:00 | 16.6 | -16.28
2017-09-14 14:30 | 18.71 | 17.24
2017-09-14 15:00 | 41.89 | 41.31
2017-09-14 15:30 | 46.76 | 45.44
2017-09-14 16:00 | 59.92 | 58.8
2017-09-14 16:30 | 108.89 | 108.09
2017-09-14 17:00 | 131.85 | 131.21
2017-09-14 17:30 | 159.6 | 159.1
2017-09-14 18:00 | 171.2 | 170.95
2017-09-14 18:30 | 195.59 | 195.54
2017-09-14 19:00 | 196.1 | 196.07
2017-09-14 19:30 | 169.9 | 169.8
2017-09-14 20:00 | 143.85 | 143.61
2017-09-14 20:30 | 121.62 | 121.54
2017-09-14 21:00 | 98.64 | 98.62
2017-09-14 21:30 | 92.65 | 92.57
2017-09-14 22:00 | 69.44 | 69.12
2017-09-14 22:30 | 84.47 | 83.75
2017-09-14 23:00 | 83.84 | 82.86
2017-09-14 23:30 | 46.39 | 44.23
2017-09-15 | 11.75 | 3
2017-09-15 00:30 | 12.3 | -7.9
2017-09-15 01:00 | 26.26 | -24.98
2017-09-15 01:30 | 41.91 | -41.31
2017-09-15 02:00 | 47.42 | -47.06
2017-09-15 02:30 | 31.63 | -31.02
2017-09-15 03:00 | 19.17 | -17.43
2017-09-15 03:30 | 9.88 | -4.21
2017-09-15 04:00 | 11.26 | 4.12
2017-09-15 04:30 | 16.63 | 11.87
2017-09-15 05:00 | 13.21 | 6.93
2017-09-15 05:30 | 44.24 | 42.08
2017-09-15 06:00 | 87.87 | 86.59
2017-09-15 06:30 | 126.25 | 125.75
2017-09-15 07:00 | 156.87 | 156.7
2017-09-15 07:30 | 156.05 | 156.01
2017-09-15 08:00 | 121.62 | 121.62
2017-09-15 08:30 | 93.13 | 93.13
2017-09-15 09:00 | 59.48 | 59.41
2017-09-15 09:30 | 29.31 | 28.85
2017-09-15 10:00 | 13.65 | 12.09
2017-09-15 10:30 | 10.24 | -6.85
2017-09-15 11:00 | 20.01 | -18.03
2017-09-15 11:30 | 33.05 | -30.56
2017-09-15 12:00 | 35.02 | -32.51
2017-09-15 12:30 | 28.84 | -26.5
2017-09-15 13:00 | 23.64 | -21.18
2017-09-15 13:30 | 23.46 | -20.88
2017-09-15 14:00 | 16.43 | -13.07
2017-09-15 14:30 | 18.7 | -15.78
2017-09-15 15:00 | 10.6 | -6.83
2017-09-15 15:30 | 20.57 | 19.85
2017-09-15 16:00 | 44.2 | 44.03
2017-09-15 16:30 | 75.78 | 75.75
2017-09-15 17:00 | 117.06 | 117.06
2017-09-15 17:30 | 137.99 | 137.97
2017-09-15 18:00 | 141.66 | 141.66
2017-09-15 18:30 | 169.15 | 169.14
2017-09-15 19:00 | 185.06 | 185
2017-09-15 19:30 | 169.95 | 169.82
2017-09-15 20:00 | 153.8 | 153.56
2017-09-15 20:30 | 132.59 | 132.42
2017-09-15 21:00 | 116.09 | 115.99
2017-09-15 21:30 | 95.72 | 95.53
2017-09-15 22:00 | 64.72 | 64.18
2017-09-15 22:30 | 118.79 | 118.33
2017-09-15 23:00 | 143.04 | 142.44
2017-09-15 23:30 | 112.51 | 111.37
2017-09-16 | 57.39 | 55.72
2017-09-16 00:30 | 20.57 | 17.27
2017-09-16 01:00 | 10.13 | -0.35
2017-09-16 01:30 | 15.89 | -13.24
2017-09-16 02:00 | 27.52 | -26.53
2017-09-16 02:30 | 36.16 | -35.58
2017-09-16 03:00 | 40.52 | -40.09
2017-09-16 03:30 | 41.69 | -41.32
2017-09-16 04:00 | 36.63 | -36.11
2017-09-16 04:30 | 36.65 | -36.01
2017-09-16 05:00 | 19.68 | -17.55
2017-09-16 05:30 | 10.39 | -4.01
2017-09-16 06:00 | 18.71 | 16.14
2017-09-16 06:30 | 16.6 | 13.14
2017-09-16 07:00 | 22.03 | 18.78
2017-09-16 07:30 | 14.18 | 9.48
2017-09-16 08:00 | 9.36 | -7.38
2017-09-16 08:30 | 15 | -14.48
2017-09-16 09:00 | 30 | -23.02
2017-09-16 09:30 | 36.7 | -30.71
2017-09-16 10:00 | 46.05 | -40.89
2017-09-16 10:30 | 50.76 | -45.31
2017-09-16 11:00 | 52.61 | -47.48
2017-09-16 11:30 | 54.53 | -49.58
2017-09-16 12:00 | 57.44 | -52.84
2017-09-16 12:30 | 57.57 | -53.02
2017-09-16 13:00 | 57.96 | -53.45
2017-09-16 13:30 | 57.16 | -52.55
2017-09-16 14:00 | 55.22 | -50.46
2017-09-16 14:30 | 51.92 | -46.6
2017-09-16 15:00 | 44.73 | -39.14
2017-09-16 15:30 | 29.53 | -21.3
2017-09-16 16:00 | 19.69 | -1.61
2017-09-16 16:30 | 35.03 | 29.82
2017-09-16 17:00 | 76.81 | 74.82
2017-09-16 17:30 | 98.91 | 97.54
2017-09-16 18:00 | 102.75 | 96.33
2017-09-16 18:30 | 138.01 | 128.14
2017-09-16 19:00 | 138.96 | 129.37
2017-09-16 19:30 | 120.08 | 109.65
2017-09-16 20:00 | 107.97 | 100.78
2017-09-16 20:30 | 80.1 | 78.96
2017-09-16 21:00 | 52.58 | 51.09
2017-09-16 21:30 | 47.75 | 46.61
2017-09-16 22:00 | 34.45 | 33.4
2017-09-16 22:30 | 78.32 | 78.02
2017-09-16 23:00 | 104.53 | 104.37
2017-09-16 23:30 | 84.92 | 84.81
2017-09-17 | 38.3 | 37.88
2017-09-17 00:30 | 8.02 | 1.15
2017-09-17 01:00 | 32.3 | -30.69
2017-09-17 01:30 | 43.58 | -42.06
2017-09-17 02:00 | 41.25 | -39.34
2017-09-17 02:30 | 41.18 | -39.13
2017-09-17 03:00 | 43.16 | -41.12
2017-09-17 03:30 | 45.7 | -43.79
2017-09-17 04:00 | 54.1 | -52.34
2017-09-17 04:30 | 51.08 | -49.32
2017-09-17 05:00 | 51.41 | -49.65
2017-09-17 05:30 | 43.66 | -41.92
2017-09-17 06:00 | 29.59 | -29.59
2017-09-17 06:30 | 55.25 | -54.8
2017-09-17 07:00 | 51.18 | -50.64
2017-09-17 07:30 | 54.33 | -53.99
2017-09-17 08:00 | 53.33 | -53.07
2017-09-17 08:30 | 47.87 | -47.74
2017-09-17 09:00 | 45.95 | -45.87
2017-09-17 09:30 | 43.41 | -43.36
2017-09-17 10:00 | 43.86 | -43.86
2017-09-17 10:30 | 34.34 | -34.33
2017-09-17 11:00 | 27.19 | -27.18
2017-09-17 11:30 | 35.51 | -35.5
2017-09-17 12:00 | 51.62 | -51.61
2017-09-17 12:30 | 46.93 | -46.92
2017-09-17 13:00 | 28.03 | -28.03
2017-09-17 13:30 | 30.06 | -30.06
2017-09-17 14:00 | 39.9 | -39.9
2017-09-17 14:30 | 38.7 | -38.7
2017-09-17 15:00 | 23.76 | -23.71
2017-09-17 15:30 | 15.56 | -15.4
2017-09-17 16:00 | 2.89 | -1.57
2017-09-17 16:30 | 47.3 | 45.94
2017-09-17 17:00 | 102.45 | 101.39
2017-09-17 17:30 | 130.73 | 129.72
2017-09-17 18:00 | 134.21 | 131.61
2017-09-17 18:30 | 149.9 | 131.97
2017-09-17 19:00 | 151.99 | 134.57
2017-09-17 19:30 | 127.64 | 106.9
2017-09-17 20:00 | 120 | 99.45
2017-09-17 20:30 | 96.8 | 84.44
2017-09-17 21:00 | 84.3 | 72.96
2017-09-17 21:30 | 56.63 | 55.15
2017-09-17 22:00 | 36.17 | 34.01
2017-09-17 22:30 | 58.14 | 57.02
2017-09-17 23:00 | 71.46 | 70.56
2017-09-17 23:30 | 46.66 | 45.35
2017-09-18 | 22.59 | 18.64
2017-09-18 00:30 | 15.78 | 7.18
2017-09-18 01:00 | 15.43 | 0.81
2017-09-18 01:30 | 16.56 | -2.73
2017-09-18 02:00 | 16.51 | -0.7
2017-09-18 02:30 | 16.25 | 2.19
2017-09-18 03:00 | 16.64 | 3.95
2017-09-18 03:30 | 16.2 | 5.53
2017-09-18 04:00 | 15.76 | 7.06
2017-09-18 04:30 | 16.48 | 8.99
2017-09-18 05:00 | 17.57 | 11.78
2017-09-18 05:30 | 20.96 | 17.52
2017-09-18 06:00 | 27.39 | 25.33
2017-09-18 06:30 | 54.22 | 53.05
2017-09-18 07:00 | 71.36 | 69.64
2017-09-18 07:30 | 70.29 | 67.41
2017-09-18 08:00 | 61.8 | 56.06
2017-09-18 08:30 | 73.1 | 59.05
2017-09-18 09:00 | 75 | 57.82
2017-09-18 09:30 | 73.17 | 54.93
2017-09-18 10:00 | 69.8 | 54.73
2017-09-18 10:30 | 62.79 | 47.32
2017-09-18 11:00 | 63.49 | 47.93
2017-09-18 11:30 | 52.71 | 44.8
2017-09-18 12:00 | 47.24 | 41.5
2017-09-18 12:30 | 47.66 | 42.22
2017-09-18 13:00 | 48.18 | 43.31
2017-09-18 13:30 | 49.53 | 44.84
2017-09-18 14:00 | 49.96 | 45.1
2017-09-18 14:30 | 53.05 | 48.61
2017-09-18 15:00 | 53.41 | 49.12
2017-09-18 15:30 | 54.74 | 50.98
2017-09-18 16:00 | 85.75 | 83.79
2017-09-18 16:30 | 105.76 | 104.56
2017-09-18 17:00 | 131.71 | 130.8
2017-09-18 17:30 | 160.3 | 159.71
2017-09-18 18:00 | 168.39 | 167.66
2017-09-18 18:30 | 184.76 | 183.85
2017-09-18 19:00 | 190.55 | 189.79
2017-09-18 19:30 | 162.66 | 162.01
2017-09-18 20:00 | 135.5 | 134.92
2017-09-18 20:30 | 131.29 | 130.82
2017-09-18 21:00 | 99.17 | 98.7
2017-09-18 21:30 | 70.5 | 70.49
2017-09-18 22:00 | 43.42 | 43.28
2017-09-18 22:30 | 61.82 | 61.63
2017-09-18 23:00 | 79.86 | 79.61
2017-09-18 23:30 | 56.81 | 56.77
2017-09-19 | 17 | 16.35
2017-09-19 00:30 | 8.94 | -0.6
2017-09-19 01:00 | 14.92 | -10.59
2017-09-19 01:30 | 18.81 | -13.82
2017-09-19 02:00 | 15.04 | -8.55
2017-09-19 02:30 | 8.94 | -3.14
2017-09-19 03:00 | 1.53 | -0.91
2017-09-19 03:30 | 2.99 | 2.86
2017-09-19 04:00 | 5.37 | 5.36
2017-09-19 04:30 | 8.68 | 8.5
2017-09-19 05:00 | 11.59 | 10.88
2017-09-19 05:30 | 17 | 15.7
2017-09-19 06:00 | 22.82 | 21.81
2017-09-19 06:30 | 31.88 | 29.78
2017-09-19 07:00 | 48.64 | 47.57
2017-09-19 07:30 | 56.68 | 53.94
2017-09-19 08:00 | 55.02 | 49.66
2017-09-19 08:30 | 56.8 | 49.88
2017-09-19 09:00 | 68.74 | 50.63
2017-09-19 09:30 | 66.95 | 46
2017-09-19 10:00 | 65.66 | 42.71
2017-09-19 10:30 | 62.41 | 38.01
2017-09-19 11:00 | 63.52 | 39.06
2017-09-19 11:30 | 62.34 | 36.91
2017-09-19 12:00 | 64.7 | 39.47
2017-09-19 12:30 | 56.8 | 41.2
2017-09-19 13:00 | 54.29 | 42.2
2017-09-19 13:30 | 57.03 | 44.72
2017-09-19 14:00 | 58.64 | 46.09
2017-09-19 14:30 | 61.9 | 49.86
2017-09-19 15:00 | 68.57 | 58.39
2017-09-19 15:30 | 88.19 | 81.14
2017-09-19 16:00 | 98.03 | 92.22
2017-09-19 16:30 | 103.68 | 98.48
2017-09-19 17:00 | 119.45 | 115.47
2017-09-19 17:30 | 132.19 | 129.07
2017-09-19 18:00 | 148.49 | 145.36
2017-09-19 18:30 | 170.41 | 168.57
2017-09-19 19:00 | 178.61 | 178.02
2017-09-19 19:30 | 150.06 | 149.72
2017-09-19 20:00 | 133.5 | 133.26
2017-09-19 20:30 | 129.52 | 129.35
2017-09-19 21:00 | 91.63 | 88.81
2017-09-19 21:30 | 72.41 | 69.24
2017-09-19 22:00 | 54.45 | 51.1
2017-09-19 22:30 | 67.29 | 65.16
2017-09-19 23:00 | 68.29 | 66.47
2017-09-19 23:30 | 46.6 | 44.54
2017-09-20 | 15.82 | 15.82
2017-09-20 00:30 | 0.57 | 0.54
2017-09-20 01:00 | 7.84 | -7.78
2017-09-20 01:30 | 10.5 | -10.44
2017-09-20 02:00 | 9.06 | -6.74
2017-09-20 02:30 | 6.24 | -1.75
2017-09-20 03:00 | 6.3 | 0.68
2017-09-20 03:30 | 7.07 | 3.14
2017-09-20 04:00 | 8.32 | 6.56
2017-09-20 04:30 | 9.1 | 8.3
2017-09-20 05:00 | 10.73 | 10.46
2017-09-20 05:30 | 15.21 | 15.18
2017-09-20 06:00 | 21.02 | 20.96
2017-09-20 06:30 | 26.74 | 26.36
2017-09-20 07:00 | 39.28 | 39.21
2017-09-20 07:30 | 52.23 | 50.12
2017-09-20 08:00 | 48.9 | 41.61
2017-09-20 08:30 | 42.85 | 33.66
2017-09-20 09:00 | 46.28 | 35.57
2017-09-20 09:30 | 43.67 | 30.81
2017-09-20 10:00 | 42.49 | 28.28
2017-09-20 10:30 | 52.7 | 23.79
2017-09-20 11:00 | 53.78 | 24.06
2017-09-20 11:30 | 52.16 | 20.53
2017-09-20 12:00 | 51.41 | 20.71
2017-09-20 12:30 | 50.75 | 21.69
2017-09-20 13:00 | 50.37 | 22.19
2017-09-20 13:30 | 50.68 | 22.03
2017-09-20 14:00 | 51.77 | 23.51
2017-09-20 14:30 | 53.18 | 26.89
2017-09-20 15:00 | 53.98 | 29.13
2017-09-20 15:30 | 52.66 | 28.19
2017-09-20 16:00 | 48.1 | 30.91
2017-09-20 16:30 | 45.59 | 36.13
2017-09-20 17:00 | 63.89 | 58.17
2017-09-20 17:30 | 83.2 | 79.54
2017-09-20 18:00 | 93.69 | 90.06
2017-09-20 18:30 | 107.85 | 104.26
2017-09-20 19:00 | 129.07 | 126.45
2017-09-20 19:30 | 107.68 | 104.99
2017-09-20 20:00 | 101.53 | 99.38
2017-09-20 20:30 | 84.58 | 82.41
2017-09-20 21:00 | 66.32 | 57.54
2017-09-20 21:30 | 62.34 | 54.31
2017-09-20 22:00 | 48.22 | 38.5
2017-09-20 22:30 | 70.47 | 65.27
2017-09-20 23:00 | 70.6 | 66.08
2017-09-20 23:30 | 35.71 | 24.22
2017-09-21 | 26.55 | 1.76
2017-09-21 00:30 | 18.82 | -9.08
2017-09-21 01:00 | 22.88 | -15.65
2017-09-21 01:30 | 25.14 | -18.14
2017-09-21 02:00 | 15.92 | -15.67
2017-09-21 02:30 | 8.84 | -8.84
2017-09-21 03:00 | 6.7 | -6.69
2017-09-21 03:30 | 5.27 | -5.27
2017-09-21 04:00 | 2.61 | -2.18
2017-09-21 04:30 | 3.05 | 1.02
2017-09-21 05:00 | 3.2 | 1.76
2017-09-21 05:30 | 5.37 | 4.58
2017-09-21 06:00 | 9.43 | 8.59
2017-09-21 06:30 | 12.65 | 12.09
2017-09-21 07:00 | 23.74 | 23.68
2017-09-21 07:30 | 31.76 | 31.62
2017-09-21 08:00 | 31.78 | 31.16
2017-09-21 08:30 | 43.45 | 34.46
2017-09-21 09:00 | 51.67 | 38.79
2017-09-21 09:30 | 75.5 | 37.74
2017-09-21 10:00 | 90.31 | 37.11
2017-09-21 10:30 | 89.86 | 33.06
2017-09-21 11:00 | 88.76 | 32.13
2017-09-21 11:30 | 67.98 | 28.09
2017-09-21 12:00 | 67.35 | 27.03
2017-09-21 12:30 | 66.26 | 24.5
2017-09-21 13:00 | 67.34 | 26.89
2017-09-21 13:30 | 67.4 | 27.31
2017-09-21 14:00 | 67.88 | 29.18
2017-09-21 14:30 | 68.57 | 30.81
2017-09-21 15:00 | 68.03 | 31.21
2017-09-21 15:30 | 78.74 | 52.59
2017-09-21 16:00 | 81.79 | 58.03
2017-09-21 16:30 | 82.57 | 60.5
2017-09-21 17:00 | 89.97 | 71.09
2017-09-21 17:30 | 101.87 | 86.43
2017-09-21 18:00 | 121.24 | 108.07
2017-09-21 18:30 | 146.91 | 135.16
2017-09-21 19:00 | 150.08 | 138.66
2017-09-21 19:30 | 132.55 | 120.36
2017-09-21 20:00 | 124.32 | 111.64
2017-09-21 20:30 | 104.15 | 95.75
2017-09-21 21:00 | 67.6 | 64.77
2017-09-21 21:30 | 58.61 | 56.39
2017-09-21 22:00 | 47.53 | 45.92
2017-09-21 22:30 | 62.84 | 61.96
2017-09-21 23:00 | 67.15 | 66.59
2017-09-21 23:30 | 37.03 | 34.39
2017-09-22 | 21.23 | 15.45
2017-09-22 00:30 | 14.58 | 2.57
2017-09-22 01:00 | 6.96 | -5.86
2017-09-22 01:30 | 10.84 | -10.06
2017-09-22 02:00 | 6.76 | -5.5
2017-09-22 02:30 | 4.2 | 0.43
2017-09-22 03:00 | 5.41 | 3.25
2017-09-22 03:30 | 7.81 | 5.33
2017-09-22 04:00 | 7.71 | 4.6
2017-09-22 04:30 | 5.8 | 1.66
2017-09-22 05:00 | 7.32 | 3.74
2017-09-22 05:30 | 13.3 | 10.05
2017-09-22 06:00 | 17.08 | 14.76
2017-09-22 06:30 | 22.81 | 22.39
2017-09-22 07:00 | 39.68 | 39.67
2017-09-22 07:30 | 48.33 | 48.33
2017-09-22 08:00 | 53.82 | 53.67
2017-09-22 08:30 | 62.58 | 56.36
2017-09-22 09:00 | 66.74 | 59.38
2017-09-22 09:30 | 79.41 | 57.39
2017-09-22 10:00 | 86.1 | 56.47
2017-09-22 10:30 | 84.21 | 52.26
2017-09-22 11:00 | 85.96 | 54.27
2017-09-22 11:30 | 85.19 | 53.11
2017-09-22 12:00 | 83.78 | 51.93
2017-09-22 12:30 | 84.27 | 53.54
2017-09-22 13:00 | 86.01 | 55.79
2017-09-22 13:30 | 87.25 | 57.51
2017-09-22 14:00 | 102.94 | 80.55
2017-09-22 14:30 | 113.8 | 94.15
2017-09-22 15:00 | 126.4 | 109.91
2017-09-22 15:30 | 144.21 | 131.2
2017-09-22 16:00 | 153.91 | 141.94
2017-09-22 16:30 | 167.05 | 156.53
2017-09-22 17:00 | 181.5 | 171.86
2017-09-22 17:30 | 187.08 | 178.45
2017-09-22 18:00 | 170.89 | 161.14
2017-09-22 18:30 | 172.41 | 162.67
2017-09-22 19:00 | 171.37 | 162.27
2017-09-22 19:30 | 164.09 | 155.42
2017-09-22 20:00 | 152.47 | 145.56
2017-09-22 20:30 | 105.06 | 104.12
2017-09-22 21:00 | 94.3 | 93.34
2017-09-22 21:30 | 85.96 | 85.29
2017-09-22 22:00 | 51.91 | 51.17
2017-09-22 22:30 | 76.08 | 75.77
2017-09-22 23:00 | 105.31 | 105.22
2017-09-22 23:30 | 66.28 | 66.22
2017-09-23 | 20.06 | 19.29
2017-09-23 00:30 | 15.35 | 1.01
2017-09-23 01:00 | 17.76 | -6.4
2017-09-23 01:30 | 19.42 | -9.07
2017-09-23 02:00 | 11.16 | -4.57
2017-09-23 02:30 | 2.18 | 0
2017-09-23 03:00 | 3.39 | 2.26
2017-09-23 03:30 | 5.68 | 5.05
2017-09-23 04:00 | 4.64 | 3.73
2017-09-23 04:30 | 7.29 | 6.33
2017-09-23 05:00 | 7.3 | 6.37
2017-09-23 05:30 | 10.39 | 9.22
2017-09-23 06:00 | 10.31 | 9.58
2017-09-23 06:30 | 12.87 | 12.15
2017-09-23 07:00 | 16.14 | 15.57
2017-09-23 07:30 | 21.04 | 20.69
2017-09-23 08:00 | 25.82 | 25.81
2017-09-23 08:30 | 30.01 | 29.87
2017-09-23 09:00 | 34.16 | 32.7
2017-09-23 09:30 | 40.57 | 34.08
2017-09-23 10:00 | 46.3 | 34.02
2017-09-23 10:30 | 47.05 | 34.89
2017-09-23 11:00 | 46.82 | 33.8
2017-09-23 11:30 | 44.2 | 29.83
2017-09-23 12:00 | 46.25 | 32.69
2017-09-23 12:30 | 45.77 | 32.14
2017-09-23 13:00 | 47 | 33.75
2017-09-23 13:30 | 48.26 | 35.48
2017-09-23 14:00 | 50.42 | 38.15
2017-09-23 14:30 | 52.99 | 41.42
2017-09-23 15:00 | 71.9 | 43.99
2017-09-23 15:30 | 78.38 | 44.8
2017-09-23 16:00 | 80.89 | 48.84
2017-09-23 16:30 | 109.88 | 89.85
2017-09-23 17:00 | 134.46 | 119.32
2017-09-23 17:30 | 155.44 | 143.38
2017-09-23 18:00 | 143.47 | 130.36
2017-09-23 18:30 | 160.34 | 147.53
2017-09-23 19:00 | 169.79 | 158.28
2017-09-23 19:30 | 166.99 | 155.84
2017-09-23 20:00 | 170.27 | 159.84
2017-09-23 20:30 | 156.01 | 150.22
2017-09-23 21:00 | 135.06 | 132.97
2017-09-23 21:30 | 113.04 | 111.28
2017-09-23 22:00 | 83.46 | 81.5
2017-09-23 22:30 | 98.8 | 97.35
2017-09-23 23:00 | 107.85 | 106.78
2017-09-23 23:30 | 72.17 | 70.95
2017-09-24 | 27.76 | 22.94
2017-09-24 00:30 | 21.22 | 12.92
2017-09-24 01:00 | 19.01 | 6.82
2017-09-24 01:30 | 18.22 | 1.67
2017-09-24 02:00 | 13.89 | 3.69
2017-09-24 02:30 | 5.48 | 5.32
2017-09-24 03:00 | 5.61 | 5.52
2017-09-24 03:30 | 7.95 | 7.91
2017-09-24 04:00 | 12.89 | 12.87
2017-09-24 04:30 | 12.33 | 12.29
2017-09-24 05:00 | 12.38 | 12.31
2017-09-24 05:30 | 7.33 | 7.22
2017-09-24 06:00 | 7.59 | 7.59
2017-09-24 06:30 | 9.24 | 9.24
2017-09-24 07:00 | 11.11 | 11.11
2017-09-24 07:30 | 15.23 | 15.21
2017-09-24 08:00 | 18.96 | 18.94
2017-09-24 08:30 | 17.85 | 17.84
2017-09-24 09:00 | 20.63 | 20.4
2017-09-24 09:30 | 23.89 | 22.15
2017-09-24 10:00 | 21.67 | 18.59
2017-09-24 10:30 | 24.41 | 20.83
2017-09-24 11:00 | 27.1 | 23.47
2017-09-24 11:30 | 27.1 | 23.19
2017-09-24 12:00 | 22.15 | 16.98
2017-09-24 12:30 | 22.24 | 17.02
2017-09-24 13:00 | 23.05 | 17.81
2017-09-24 13:30 | 32 | 28.33
2017-09-24 14:00 | 131.84 | 131.16
2017-09-24 14:30 | 130.9 | 130.17
2017-09-24 15:00 | 103.88 | 102.03
2017-09-24 15:30 | 87.45 | 74.87
2017-09-24 16:00 | 167.49 | 155.6
2017-09-24 16:30 | 177.56 | 167.27
2017-09-24 17:00 | 175.47 | 166.78
2017-09-24 17:30 | 196.51 | 188.65
2017-09-24 18:00 | 203.33 | 195.07
2017-09-24 18:30 | 212.26 | 206.13
2017-09-24 19:00 | 210.83 | 206.51
2017-09-24 19:30 | 196.49 | 195.28
2017-09-24 20:00 | 180.6 | 177.15
2017-09-24 20:30 | 159.61 | 157.83
2017-09-24 21:00 | 133.2 | 131.3
2017-09-24 21:30 | 124.04 | 122.49
2017-09-24 22:00 | 101.09 | 99.68
2017-09-24 22:30 | 106.66 | 105.58
2017-09-24 23:00 | 125.06 | 124.35
2017-09-24 23:30 | 83.9 | 83.1
2017-09-25 | 38.34 | 35.82
2017-09-25 00:30 | 15.25 | 14.74
2017-09-25 01:00 | 4.78 | 4.11
2017-09-25 01:30 | 2.15 | 1.14
2017-09-25 02:00 | 9.97 | 9.75
2017-09-25 02:30 | 32.75 | 32.35
2017-09-25 03:00 | 39.78 | 39.38
2017-09-25 03:30 | 43.72 | 43.15
2017-09-25 04:00 | 40.03 | 39.25
2017-09-25 04:30 | 28.29 | 27.1
2017-09-25 05:00 | 20.88 | 19.06
2017-09-25 05:30 | 24.89 | 23.64
2017-09-25 06:00 | 40.51 | 39.89
2017-09-25 06:30 | 73.81 | 73.69
2017-09-25 07:00 | 114.22 | 114.22
2017-09-25 07:30 | 135.89 | 135.74
2017-09-25 08:00 | 130.1 | 128.99
2017-09-25 08:30 | 137.14 | 132.63
2017-09-25 09:00 | 141.87 | 138.59
2017-09-25 09:30 | 149.12 | 145.32
2017-09-25 10:00 | 141.15 | 136.77
2017-09-25 10:30 | 135.43 | 130.56
2017-09-25 11:00 | 117.65 | 111.48
2017-09-25 11:30 | 117.53 | 110.99
2017-09-25 12:00 | 125 | 118.83
2017-09-25 12:30 | 133.49 | 127.45
2017-09-25 13:00 | 144.89 | 139
2017-09-25 13:30 | 179.86 | 168.54
2017-09-25 14:00 | 196.41 | 183.16
2017-09-25 14:30 | 205.23 | 192.51
2017-09-25 15:00 | 197.04 | 184.24
2017-09-25 15:30 | 208.76 | 197.08
2017-09-25 16:00 | 216.17 | 205.4
2017-09-25 16:30 | 220.47 | 209.85
2017-09-25 17:00 | 222.8 | 212.76
2017-09-25 17:30 | 226.06 | 217.24
2017-09-25 18:00 | 227.89 | 219.26
2017-09-25 18:30 | 237.99 | 229.29
2017-09-25 19:00 | 236.92 | 228.56
2017-09-25 19:30 | 226.54 | 218.66
2017-09-25 20:00 | 211.54 | 204.25
2017-09-25 20:30 | 186.02 | 178.57
2017-09-25 21:00 | 152.78 | 143.67
2017-09-25 21:30 | 157.48 | 155.95
2017-09-25 22:00 | 138.82 | 137.45
2017-09-25 22:30 | 142.98 | 141.93
2017-09-25 23:00 | 136.79 | 135.91
2017-09-25 23:30 | 111.91 | 111.05
2017-09-26 | 61.15 | 59.41
2017-09-26 00:30 | 35.41 | 31.5
2017-09-26 01:00 | 20.03 | 17.97
2017-09-26 01:30 | 3.34 | 2.79
2017-09-26 02:00 | 4.89 | 4.55
2017-09-26 02:30 | 15.85 | 15.67
2017-09-26 03:00 | 10.11 | 9.74
2017-09-26 03:30 | 37.07 | 36.56
2017-09-26 04:00 | 42.86 | 42.18
2017-09-26 04:30 | 37.83 | 36.9
2017-09-26 05:00 | 56.53 | 55.91
2017-09-26 05:30 | 53.1 | 52.66
2017-09-26 06:00 | 71.13 | 70.78
2017-09-26 06:30 | 109.67 | 109.53
2017-09-26 07:00 | 117.71 | 117.69
2017-09-26 07:30 | 133.29 | 133.28
2017-09-26 08:00 | 151.18 | 151.04
2017-09-26 08:30 | 166.53 | 166.53
2017-09-26 09:00 | 139.66 | 139.64
2017-09-26 09:30 | 137.62 | 137.52
2017-09-26 10:00 | 149.69 | 149.53
2017-09-26 10:30 | 152.72 | 152.52
2017-09-26 11:00 | 144.21 | 143.98
2017-09-26 11:30 | 114.73 | 114.5
2017-09-26 12:00 | 129.65 | 129.37
2017-09-26 12:30 | 135.86 | 135.54
2017-09-26 13:00 | 105.23 | 105.16
2017-09-26 13:30 | 98.44 | 98.43
2017-09-26 14:00 | 94.21 | 94.2
2017-09-26 14:30 | 107.09 | 107.07
2017-09-26 15:00 | 151.23 | 151.15
2017-09-26 15:30 | 157.36 | 157.23
2017-09-26 16:00 | 161.01 | 160.88
2017-09-26 16:30 | 167.65 | 167.54
2017-09-26 17:00 | 175.03 | 174.9
2017-09-26 17:30 | 179.4 | 179.28
2017-09-26 18:00 | 182.81 | 182.45
2017-09-26 18:30 | 184.09 | 183.11
2017-09-26 19:00 | 188.61 | 187.78
2017-09-26 19:30 | 185.9 | 185.3
2017-09-26 20:00 | 181.14 | 180.73
2017-09-26 20:30 | 174.47 | 174.18
2017-09-26 21:00 | 152.09 | 152.09
2017-09-26 21:30 | 151.74 | 151.72
2017-09-26 22:00 | 141.48 | 141.33
2017-09-26 22:30 | 142.57 | 142.49
2017-09-26 23:00 | 142.91 | 142.57
2017-09-26 23:30 | 133.27 | 132.81
2017-09-27 | 118.82 | 118.55
2017-09-27 00:30 | 105.61 | 105.39
2017-09-27 01:00 | 91.59 | 91.33
2017-09-27 01:30 | 86.46 | 86.24
2017-09-27 02:00 | 88.95 | 88.63
2017-09-27 02:30 | 94.09 | 93.68
2017-09-27 03:00 | 92.32 | 91.9
2017-09-27 03:30 | 94.99 | 94.57
2017-09-27 04:00 | 84.86 | 84.23
2017-09-27 04:30 | 84.02 | 83.21
2017-09-27 05:00 | 91.93 | 91.03
2017-09-27 05:30 | 111.05 | 110.06
2017-09-27 06:00 | 112.57 | 111.73
2017-09-27 06:30 | 130.62 | 130.09
2017-09-27 07:00 | 140.9 | 140.61
2017-09-27 07:30 | 155.28 | 155.23
2017-09-27 08:00 | 160.87 | 160.81
2017-09-27 08:30 | 155.64 | 155.21
2017-09-27 09:00 | 153.56 | 153.2
2017-09-27 09:30 | 157.94 | 157.56
2017-09-27 10:00 | 159.86 | 159.66
2017-09-27 10:30 | 164.76 | 164.63
2017-09-27 11:00 | 159.72 | 159.56
2017-09-27 11:30 | 157.26 | 157.09
2017-09-27 12:00 | 157.49 | 157.35
2017-09-27 12:30 | 155.88 | 155.72
2017-09-27 13:00 | 152.13 | 151.78
2017-09-27 13:30 | 155.78 | 155.32
2017-09-27 14:00 | 157.28 | 156.69
2017-09-27 14:30 | 157.93 | 157.59
2017-09-27 15:00 | 163.92 | 163.61
2017-09-27 15:30 | 151.68 | 151.41
2017-09-27 16:00 | 163.28 | 163.03
2017-09-27 16:30 | 171.3 | 171.22
2017-09-27 17:00 | 177.18 | 177.09
2017-09-27 17:30 | 179.55 | 179.38
2017-09-27 18:00 | 182.68 | 182.47
2017-09-27 18:30 | 187.2 | 186.88
2017-09-27 19:00 | 187.35 | 187.04
2017-09-27 19:30 | 177.67 | 177.5
2017-09-27 20:00 | 174.36 | 174.26
2017-09-27 20:30 | 172.56 | 172.33
2017-09-27 21:00 | 160.63 | 160.56
2017-09-27 21:30 | 155.7 | 155.55
2017-09-27 22:00 | 147.16 | 146.83
2017-09-27 22:30 | 146.81 | 146.49
2017-09-27 23:00 | 145.3 | 144.9
2017-09-27 23:30 | 116.9 | 116.23
2017-09-28 | 61.38 | 60.34
2017-09-28 00:30 | 64.67 | 64.38
2017-09-28 01:00 | 46.75 | 46.54
2017-09-28 01:30 | 26.91 | 26.41
2017-09-28 02:00 | 27.96 | 27.64
2017-09-28 02:30 | 71.8 | 71.24
2017-09-28 03:00 | 68.01 | 67.6
2017-09-28 03:30 | 53.61 | 53.38
2017-09-28 04:00 | 65.7 | 65.58
2017-09-28 04:30 | 62.63 | 62.57
2017-09-28 05:00 | 51.05 | 51.02
2017-09-28 05:30 | 69.95 | 69.94
2017-09-28 06:00 | 111.24 | 111.22
2017-09-28 06:30 | 125.2 | 125.16
2017-09-28 07:00 | 129.02 | 128.4
2017-09-28 07:30 | 144.25 | 144.24
2017-09-28 08:00 | 151.61 | 151.6
2017-09-28 08:30 | 149.51 | 149.51
2017-09-28 09:00 | 135.44 | 135.37
2017-09-28 09:30 | 129.01 | 128.27
2017-09-28 10:00 | 129.2 | 126.69
2017-09-28 10:30 | 132.39 | 129.8
2017-09-28 11:00 | 144.2 | 133.6
2017-09-28 11:30 | 158.3 | 145.59
2017-09-28 12:00 | 169.57 | 157.35
2017-09-28 12:30 | 171.9 | 159.52
2017-09-28 13:00 | 172.51 | 159.8
2017-09-28 13:30 | 172.39 | 159.65
2017-09-28 14:00 | 175.59 | 163.13
2017-09-28 14:30 | 178.8 | 166.14
2017-09-28 15:00 | 184.75 | 172.57
2017-09-28 15:30 | 189.5 | 177.8
2017-09-28 16:00 | 194.31 | 183.12
2017-09-28 16:30 | 200.64 | 190.01
2017-09-28 17:00 | 204.4 | 194.6
2017-09-28 17:30 | 203.34 | 194.26
2017-09-28 18:00 | 205.81 | 197.26
2017-09-28 18:30 | 213.94 | 205.14
2017-09-28 19:00 | 214.47 | 206.07
2017-09-28 19:30 | 204.95 | 197.52
2017-09-28 20:00 | 192.55 | 192.1
2017-09-28 20:30 | 189.15 | 189.14
2017-09-28 21:00 | 176.38 | 176.37
2017-09-28 21:30 | 152.93 | 152.83
2017-09-28 22:00 | 97.54 | 97.12
2017-09-28 22:30 | 85.53 | 84.92
2017-09-28 23:00 | 99.5 | 98.9
2017-09-28 23:30 | 116.98 | 116.51
2017-09-29 | 85.11 | 84.54
2017-09-29 00:30 | 55.72 | 55.68
2017-09-29 01:00 | 48.73 | 48.72
2017-09-29 01:30 | 47.69 | 47.68
2017-09-29 02:00 | 29.76 | 29.76
2017-09-29 02:30 | 33.47 | 33.44
2017-09-29 03:00 | 32.07 | 31.97
2017-09-29 03:30 | 32.01 | 31.73
2017-09-29 04:00 | 25.1 | 24.8
2017-09-29 04:30 | 18.63 | 18.16
2017-09-29 05:00 | 27.42 | 27
2017-09-29 05:30 | 34.37 | 34.01
2017-09-29 06:00 | 56.91 | 56.71
2017-09-29 06:30 | 95.51 | 95.47
2017-09-29 07:00 | 129.84 | 129.83
2017-09-29 07:30 | 142.4 | 142.1
2017-09-29 08:00 | 157.62 | 154.58
2017-09-29 08:30 | 159.8 | 156.08
2017-09-29 09:00 | 157.05 | 152.43
2017-09-29 09:30 | 147.91 | 142.14
2017-09-29 10:00 | 138.32 | 131.8
2017-09-29 10:30 | 144.06 | 136.94
2017-09-29 11:00 | 157.59 | 150.37
2017-09-29 11:30 | 174.99 | 169.75
2017-09-29 12:00 | 169.9 | 166.68
2017-09-29 12:30 | 168.9 | 165.47
2017-09-29 13:00 | 171.06 | 167.38
2017-09-29 13:30 | 170 | 166.41
2017-09-29 14:00 | 173.56 | 170.08
2017-09-29 14:30 | 176.22 | 173.76
2017-09-29 15:00 | 174.7 | 173.3
2017-09-29 15:30 | 181.06 | 179.93
2017-09-29 16:00 | 210.48 | 210.05
2017-09-29 16:30 | 210.34 | 210.03
2017-09-29 17:00 | 212.37 | 210.88
2017-09-29 17:30 | 211.31 | 208.15
2017-09-29 18:00 | 213.84 | 210.42
2017-09-29 18:30 | 220.06 | 215.62
2017-09-29 19:00 | 217.72 | 212.48
2017-09-29 19:30 | 214.2 | 209.25
2017-09-29 20:00 | 209.16 | 206.79
2017-09-29 20:30 | 201.26 | 199.61
2017-09-29 21:00 | 191.65 | 190.23
2017-09-29 21:30 | 180.75 | 179.3
2017-09-29 22:00 | 168.96 | 168.26
2017-09-29 22:30 | 171.94 | 171.92
2017-09-29 23:00 | 169.53 | 169.51
2017-09-29 23:30 | 148.85 | 148.83
2017-09-30 | 97.34 | 96.6
2017-09-30 00:30 | 63.79 | 63.06
2017-09-30 01:00 | 35.3 | 34.46
2017-09-30 01:30 | 17.21 | 16.44
2017-09-30 02:00 | 19.04 | 19.02
2017-09-30 02:30 | 41.91 | 41.86
2017-09-30 03:00 | 47.16 | 47.1
2017-09-30 03:30 | 45.26 | 45.24
2017-09-30 04:00 | 43.81 | 43.81
2017-09-30 04:30 | 52.88 | 52.87
2017-09-30 05:00 | 55.31 | 55.28
2017-09-30 05:30 | 50.11 | 50.07
2017-09-30 06:00 | 53.1 | 53.1
2017-09-30 06:30 | 59.57 | 59.52
2017-09-30 07:00 | 59.72 | 59.47
2017-09-30 07:30 | 55.22 | 54.64
2017-09-30 08:00 | 54.25 | 54.22
2017-09-30 08:30 | 64.88 | 64.47
2017-09-30 09:00 | 84.84 | 79.21
2017-09-30 09:30 | 96.12 | 90.08
2017-09-30 10:00 | 80.45 | 72.48
2017-09-30 10:30 | 82.1 | 73.49
2017-09-30 11:00 | 80 | 71.01
2017-09-30 11:30 | 78.03 | 68.44
2017-09-30 12:00 | 97.92 | 90.46
2017-09-30 12:30 | 103.75 | 91.9
2017-09-30 13:00 | 126.26 | 116.39
2017-09-30 13:30 | 139.87 | 130.93
2017-09-30 14:00 | 161.29 | 153.69
2017-09-30 14:30 | 162.01 | 154.7
2017-09-30 15:00 | 172.67 | 165.97
2017-09-30 15:30 | 176.44 | 175
2017-09-30 16:00 | 177.3 | 177.13
2017-09-30 16:30 | 179.03 | 178.88
2017-09-30 17:00 | 182.89 | 182.83
2017-09-30 17:30 | 181.39 | 180.87
2017-09-30 18:00 | 182.08 | 179.67
2017-09-30 18:30 | 186.65 | 185.42
2017-09-30 19:00 | 188.9 | 187.96
2017-09-30 19:30 | 183.82 | 183.06
2017-09-30 20:00 | 180.65 | 180.07
2017-09-30 20:30 | 177.81 | 177.52
2017-09-30 21:00 | 170.32 | 170.1
2017-09-30 21:30 | 156.89 | 156.7
2017-09-30 22:00 | 130.7 | 130.63
2017-09-30 22:30 | 150.43 | 150.34
2017-09-30 23:00 | 160.72 | 160.55
2017-09-30 23:30 | 133.44 | 133.04
2017-10-01 | 77.15 | 76.32
2017-10-01 00:30 | 48.37 | 47.06
2017-10-01 01:00 | 17.06 | 13.68
2017-10-01 01:30 | 9.18 | 2.33
2017-10-01 02:00 | 9.09 | 4.11
2017-10-01 02:30 | 18.61 | 16.53
2017-10-01 03:00 | 16.6 | 14.43
2017-10-01 03:30 | 27.33 | 25.91
2017-10-01 04:00 | 22.71 | 21.25
2017-10-01 04:30 | 19.95 | 18.48
2017-10-01 05:00 | 18.06 | 16.21
2017-10-01 05:30 | 14.51 | 11.94
2017-10-01 06:00 | 22.95 | 21.63
2017-10-01 06:30 | 19.57 | 17.65
2017-10-01 07:00 | 31.78 | 30.38
2017-10-01 07:30 | 37.98 | 36.65
2017-10-01 08:00 | 44.77 | 43.58
2017-10-01 08:30 | 70.93 | 70.48
2017-10-01 09:00 | 81.45 | 81.21
2017-10-01 09:30 | 98.52 | 98.44
2017-10-01 10:00 | 95.04 | 95.02
2017-10-01 10:30 | 93.17 | 92.89
2017-10-01 11:00 | 106.84 | 105.1
2017-10-01 11:30 | 109.56 | 107.94
2017-10-01 12:00 | 116.21 | 114.66
2017-10-01 12:30 | 122.6 | 121.25
2017-10-01 13:00 | 121.54 | 120.27
2017-10-01 13:30 | 126.53 | 125.33
2017-10-01 14:00 | 127.69 | 126.57
2017-10-01 14:30 | 118.63 | 117.5
2017-10-01 15:00 | 121.05 | 120.01
2017-10-01 15:30 | 137.47 | 136.56
2017-10-01 16:00 | 139.22 | 138.35
2017-10-01 16:30 | 132.95 | 132.09
2017-10-01 17:00 | 151.83 | 150.94
2017-10-01 17:30 | 168.95 | 167.95
2017-10-01 18:00 | 183.58 | 182.32
2017-10-01 18:30 | 188.82 | 187.57
2017-10-01 19:00 | 168.5 | 167.37
2017-10-01 19:30 | 155 | 154.05
2017-10-01 20:00 | 152.22 | 151.4
2017-10-01 20:30 | 148.26 | 147.64
2017-10-01 21:00 | 119.4 | 118.83
2017-10-01 21:30 | 123.64 | 123.23
2017-10-01 22:00 | 97.45 | 97.1
2017-10-01 22:30 | 121.54 | 121.29
2017-10-01 23:00 | 154.89 | 154.71
2017-10-01 23:30 | 139.71 | 139.63
2017-10-02 | 95.32 | 95.29
2017-10-02 00:30 | 59.76 | 58.21
2017-10-02 01:00 | 37.12 | 34.74
2017-10-02 01:30 | 15.43 | 11.03
2017-10-02 02:00 | 14.99 | 11.33
2017-10-02 02:30 | 13.84 | 9.9
2017-10-02 03:00 | 15.44 | 12.64
2017-10-02 03:30 | 14.08 | 10.45
2017-10-02 04:00 | 16.27 | 13.24
2017-10-02 04:30 | 12.07 | 7.73
2017-10-02 05:00 | 13.4 | 9.18
2017-10-02 05:30 | 15.16 | 10.42
2017-10-02 06:00 | 16.63 | 13.41
2017-10-02 06:30 | 21.58 | 18.65
2017-10-02 07:00 | 23.65 | 21.4
2017-10-02 07:30 | 31.13 | 30.3
2017-10-02 08:00 | 51.34 | 51.01
2017-10-02 08:30 | 91.26 | 91.2
2017-10-02 09:00 | 130.41 | 129.84
2017-10-02 09:30 | 139.31 | 138.04
2017-10-02 10:00 | 160.64 | 159.61
2017-10-02 10:30 | 168.24 | 167.12
2017-10-02 11:00 | 158.35 | 157.1
2017-10-02 11:30 | 131.42 | 130.02
2017-10-02 12:00 | 138 | 136.72
2017-10-02 12:30 | 135.73 | 134.53
2017-10-02 13:00 | 118.5 | 117.31
2017-10-02 13:30 | 133.15 | 132.09
2017-10-02 14:00 | 135.94 | 134.86
2017-10-02 14:30 | 141.87 | 140.8
2017-10-02 15:00 | 143.13 | 142.09
2017-10-02 15:30 | 158.64 | 157.7
2017-10-02 16:00 | 168.47 | 167.59
2017-10-02 16:30 | 181.21 | 180.19
2017-10-02 17:00 | 189.1 | 187.94
2017-10-02 17:30 | 195.07 | 193.77
2017-10-02 18:00 | 199.58 | 197.05
2017-10-02 18:30 | 207.57 | 199.89
2017-10-02 19:00 | 203.62 | 197.45
2017-10-02 19:30 | 198.48 | 192.84
2017-10-02 20:00 | 193.03 | 188.43
2017-10-02 20:30 | 180.96 | 180.66
2017-10-02 21:00 | 170.15 | 169.97
2017-10-02 21:30 | 165.82 | 165.57
2017-10-02 22:00 | 138.73 | 138.22
2017-10-02 22:30 | 150.68 | 150.17
2017-10-02 23:00 | 153.87 | 153.35
2017-10-02 23:30 | 142.07 | 141.52
2017-10-03 | 112.92 | 112.3
2017-10-03 00:30 | 99.3 | 98.82
2017-10-03 01:00 | 77.07 | 76.45
2017-10-03 01:30 | 53.21 | 52.49
2017-10-03 02:00 | 66.17 | 65.51
2017-10-03 02:30 | 63.76 | 63.17
2017-10-03 03:00 | 85.57 | 85.05
2017-10-03 03:30 | 87.93 | 87.28
2017-10-03 04:00 | 83.51 | 82.68
2017-10-03 04:30 | 79.62 | 78.62
2017-10-03 05:00 | 61.57 | 60.09
2017-10-03 05:30 | 69.79 | 68.74
2017-10-03 06:00 | 100.44 | 99.78
2017-10-03 06:30 | 147.87 | 147.63
2017-10-03 07:00 | 162.38 | 162.32
2017-10-03 07:30 | 178.92 | 178.7
2017-10-03 08:00 | 184.03 | 182.49
2017-10-03 08:30 | 183.56 | 181.65
2017-10-03 09:00 | 181.72 | 180.9
2017-10-03 09:30 | 176.74 | 176.28
2017-10-03 10:00 | 171.09 | 170.58
2017-10-03 10:30 | 174.14 | 173.54
2017-10-03 11:00 | 169.3 | 168.54
2017-10-03 11:30 | 165.59 | 164.91
2017-10-03 12:00 | 158.26 | 157.51
2017-10-03 12:30 | 152.73 | 151.95
2017-10-03 13:00 | 144.35 | 143.59
2017-10-03 13:30 | 160.45 | 159.66
2017-10-03 14:00 | 171.19 | 170.46
2017-10-03 14:30 | 167.39 | 166.66
2017-10-03 15:00 | 164.39 | 163.69
2017-10-03 15:30 | 168.34 | 167.85
2017-10-03 16:00 | 175.4 | 175
2017-10-03 16:30 | 182.11 | 181.78
2017-10-03 17:00 | 189.47 | 189.19
2017-10-03 17:30 | 196.65 | 196.4
2017-10-03 18:00 | 205.59 | 205.32
2017-10-03 18:30 | 211.4 | 211.06
2017-10-03 19:00 | 208.47 | 208.14
2017-10-03 19:30 | 203.36 | 203.15
2017-10-03 20:00 | 202.73 | 202.6
2017-10-03 20:30 | 189.75 | 189.65
2017-10-03 21:00 | 181.59 | 181.58
2017-10-03 21:30 | 175 | 175
2017-10-03 22:00 | 160.37 | 160.32
2017-10-03 22:30 | 162.96 | 162.59
2017-10-03 23:00 | 160.12 | 159.74
2017-10-03 23:30 | 147.19 | 146.87
2017-10-04 | 136.26 | 135.99
2017-10-04 00:30 | 99.39 | 99.09
2017-10-04 01:00 | 79.93 | 79.11
2017-10-04 01:30 | 71.21 | 70.32
2017-10-04 02:00 | 91.61 | 91.02
2017-10-04 02:30 | 103.14 | 102.66
2017-10-04 03:00 | 100.62 | 100.14
2017-10-04 03:30 | 87.28 | 86.71
2017-10-04 04:00 | 77.97 | 77.08
2017-10-04 04:30 | 85.46 | 84.5
2017-10-04 05:00 | 95.6 | 94.72
2017-10-04 05:30 | 117.95 | 117.33
2017-10-04 06:00 | 131.08 | 130.58
2017-10-04 06:30 | 140.28 | 140.11
2017-10-04 07:00 | 150.58 | 150.54
2017-10-04 07:30 | 163.88 | 163.88
2017-10-04 08:00 | 172.53 | 171.42
2017-10-04 08:30 | 170.9 | 168.35
2017-10-04 09:00 | 169.82 | 166.85
2017-10-04 09:30 | 175.33 | 170.63
2017-10-04 10:00 | 186.25 | 174.99
2017-10-04 10:30 | 185.87 | 176.85
2017-10-04 11:00 | 172.46 | 162.79
2017-10-04 11:30 | 164.98 | 155.28
2017-10-04 12:00 | 165.92 | 156.39
2017-10-04 12:30 | 162.85 | 153.14
2017-10-04 13:00 | 164.95 | 155.47
2017-10-04 13:30 | 163.79 | 154.04
2017-10-04 14:00 | 168.2 | 158.67
2017-10-04 14:30 | 174.24 | 164.66
2017-10-04 15:00 | 183.55 | 174.89
2017-10-04 15:30 | 189.97 | 181.89
2017-10-04 16:00 | 191.73 | 183.9
2017-10-04 16:30 | 194.8 | 187.63
2017-10-04 17:00 | 201.92 | 195.36
2017-10-04 17:30 | 206.93 | 201.09
2017-10-04 18:00 | 215.51 | 210.04
2017-10-04 18:30 | 222.16 | 216.03
2017-10-04 19:00 | 221.14 | 214.78
2017-10-04 19:30 | 215.45 | 209.99
2017-10-04 20:00 | 205.63 | 203.76
2017-10-04 20:30 | 197.12 | 195.77
2017-10-04 21:00 | 186.49 | 186.47
2017-10-04 21:30 | 181.98 | 181.89
2017-10-04 22:00 | 169.59 | 169.33
2017-10-04 22:30 | 166.21 | 166.1
2017-10-04 23:00 | 163.55 | 163.48
2017-10-04 23:30 | 154.64 | 154.46
2017-10-05 | 133.37 | 133.01
2017-10-05 00:30 | 110.05 | 109.41
2017-10-05 01:00 | 94.06 | 93.12
2017-10-05 01:30 | 79.18 | 77.98
2017-10-05 02:00 | 79.96 | 78.81
2017-10-05 02:30 | 98.78 | 97.87
2017-10-05 03:00 | 100.97 | 100.12
2017-10-05 03:30 | 90.64 | 89.73
2017-10-05 04:00 | 81.31 | 80.2
2017-10-05 04:30 | 88.13 | 87.17
2017-10-05 05:00 | 100.27 | 99.49
2017-10-05 05:30 | 72.55 | 71.52
2017-10-05 06:00 | 102.57 | 101.95
2017-10-05 06:30 | 147.17 | 147.03
2017-10-05 07:00 | 159.35 | 159.35
2017-10-05 07:30 | 167.91 | 164.9
2017-10-05 08:00 | 185.88 | 176.38
2017-10-05 08:30 | 185.4 | 176.77
2017-10-05 09:00 | 185.3 | 175.87
2017-10-05 09:30 | 150.98 | 140.01
2017-10-05 10:00 | 140.7 | 129.71
2017-10-05 10:30 | 144.04 | 132.98
2017-10-05 11:00 | 153.42 | 142.73
2017-10-05 11:30 | 149.65 | 138.66
2017-10-05 12:00 | 149.87 | 138.99
2017-10-05 12:30 | 172.64 | 163.05
2017-10-05 13:00 | 175.06 | 165.45
2017-10-05 13:30 | 182.14 | 172.93
2017-10-05 14:00 | 184.28 | 174.99
2017-10-05 14:30 | 187.21 | 178.13
2017-10-05 15:00 | 193.84 | 185.03
2017-10-05 15:30 | 196.77 | 187.41
2017-10-05 16:00 | 203.4 | 194.89
2017-10-05 16:30 | 206.49 | 198.72
2017-10-05 17:00 | 213.82 | 206.6
2017-10-05 17:30 | 215.86 | 209.01
2017-10-05 18:00 | 222.78 | 215.95
2017-10-05 18:30 | 226 | 220.78
2017-10-05 19:00 | 228.36 | 224.59
2017-10-05 19:30 | 216.74 | 215.81
2017-10-05 20:00 | 214.78 | 214.04
2017-10-05 20:30 | 214.21 | 213.7
2017-10-05 21:00 | 196 | 195.93
2017-10-05 21:30 | 184.87 | 184.84
2017-10-05 22:00 | 155.56 | 155.56
2017-10-05 22:30 | 160.5 | 160.48
2017-10-05 23:00 | 171.06 | 171.03
2017-10-05 23:30 | 135.25 | 135.24
2017-10-06 | 115.52 | 115.52
2017-10-06 00:30 | 88.15 | 88.12
2017-10-06 01:00 | 61.46 | 60.97
2017-10-06 01:30 | 41.06 | 40.53
2017-10-06 02:00 | 38.02 | 37.62
2017-10-06 02:30 | 41.28 | 41
2017-10-06 03:00 | 50.77 | 50.53
2017-10-06 03:30 | 60.65 | 60.55
2017-10-06 04:00 | 36.96 | 36.74
2017-10-06 04:30 | 48.88 | 48.63
2017-10-06 05:00 | 49.1 | 48.82
2017-10-06 05:30 | 77.3 | 77.05
2017-10-06 06:00 | 97.97 | 97.72
2017-10-06 06:30 | 138.64 | 138.43
2017-10-06 07:00 | 116.74 | 116.55
2017-10-06 07:30 | 148.23 | 147.01
2017-10-06 08:00 | 152.35 | 148.02
2017-10-06 08:30 | 156.76 | 150.33
2017-10-06 09:00 | 168.59 | 160.96
2017-10-06 09:30 | 174.71 | 167.86
2017-10-06 10:00 | 187.58 | 182.06
2017-10-06 10:30 | 202.41 | 196.31
2017-10-06 11:00 | 192.88 | 185.65
2017-10-06 11:30 | 186.01 | 179.48
2017-10-06 12:00 | 187.81 | 181.89
2017-10-06 12:30 | 184.72 | 180.59
2017-10-06 13:00 | 187.9 | 183.62
2017-10-06 13:30 | 199.74 | 196.64
2017-10-06 14:00 | 209.9 | 207.03
2017-10-06 14:30 | 221.58 | 220.72
2017-10-06 15:00 | 219.93 | 218.95
2017-10-06 15:30 | 212.29 | 210.57
2017-10-06 16:00 | 213.6 | 207.01
2017-10-06 16:30 | 220.33 | 214.59
2017-10-06 17:00 | 213.51 | 213.19
2017-10-06 17:30 | 212.77 | 212.4
2017-10-06 18:00 | 212.49 | 211.87
2017-10-06 18:30 | 216.44 | 215.59
2017-10-06 19:00 | 221.05 | 220.31
2017-10-06 19:30 | 212.66 | 212.17
2017-10-06 20:00 | 211 | 210.58
2017-10-06 20:30 | 206.67 | 206.33
2017-10-06 21:00 | 193.95 | 193.61
2017-10-06 21:30 | 182.79 | 182.39
2017-10-06 22:00 | 171.83 | 171.72
2017-10-06 22:30 | 176.64 | 176.14
2017-10-06 23:00 | 174.79 | 174.34
2017-10-06 23:30 | 158.68 | 158.45
2017-10-07 | 144.58 | 143.68
2017-10-07 00:30 | 125.22 | 123.78
2017-10-07 01:00 | 128.75 | 127.17
2017-10-07 01:30 | 114.49 | 112.52
2017-10-07 02:00 | 108.4 | 106.68
2017-10-07 02:30 | 99.13 | 98.76
2017-10-07 03:00 | 73.55 | 73.47
2017-10-07 03:30 | 61.61 | 61.54
2017-10-07 04:00 | 50.43 | 50.34
2017-10-07 04:30 | 46.63 | 46.53
2017-10-07 05:00 | 50 | 49.9
2017-10-07 05:30 | 60.89 | 60.85
2017-10-07 06:00 | 69.31 | 69.3
2017-10-07 06:30 | 85.76 | 85.73
2017-10-07 07:00 | 104.99 | 104.73
2017-10-07 07:30 | 116.94 | 115.26
2017-10-07 08:00 | 107.14 | 105.47
2017-10-07 08:30 | 167.38 | 167.32
2017-10-07 09:00 | 169.57 | 169.51
2017-10-07 09:30 | 171.67 | 171.57
2017-10-07 10:00 | 170.58 | 170.47
2017-10-07 10:30 | 169.99 | 169.97
2017-10-07 11:00 | 155.35 | 155.23
2017-10-07 11:30 | 159.63 | 159.21
2017-10-07 12:00 | 169.99 | 169.48
2017-10-07 12:30 | 150.6 | 150.09
2017-10-07 13:00 | 122.87 | 121.93
2017-10-07 13:30 | 139.37 | 138.65
2017-10-07 14:00 | 168.8 | 168.67
2017-10-07 14:30 | 169.42 | 169.41
2017-10-07 15:00 | 166.46 | 166.45
2017-10-07 15:30 | 172.69 | 172.65
2017-10-07 16:00 | 170.31 | 170.3
2017-10-07 16:30 | 175.94 | 175.88
2017-10-07 17:00 | 181.69 | 181.63
2017-10-07 17:30 | 182 | 182
2017-10-07 18:00 | 184.17 | 184.17
2017-10-07 18:30 | 189.36 | 189.36
2017-10-07 19:00 | 192.57 | 192.53
2017-10-07 19:30 | 187.66 | 187.65
2017-10-07 20:00 | 183.83 | 183.64
2017-10-07 20:30 | 181.23 | 180.41
2017-10-07 21:00 | 161.42 | 160.32
2017-10-07 21:30 | 151.48 | 150.09
2017-10-07 22:00 | 133.7 | 131.78
2017-10-07 22:30 | 157.97 | 156.52
2017-10-07 23:00 | 163.87 | 162.6
2017-10-07 23:30 | 152 | 150.3
2017-10-08 | 108.19 | 105.51
2017-10-08 00:30 | 79.88 | 76.76
2017-10-08 01:00 | 63.41 | 59.95
2017-10-08 01:30 | 56.1 | 51.97
2017-10-08 02:00 | 51.31 | 50.31
2017-10-08 02:30 | 52.24 | 52.19
2017-10-08 03:00 | 45.74 | 45.7
2017-10-08 03:30 | 43.58 | 43.55
2017-10-08 04:00 | 40.11 | 40.08
2017-10-08 04:30 | 64.65 | 64.63
2017-10-08 05:00 | 76.02 | 76
2017-10-08 05:30 | 70.14 | 70.13
2017-10-08 06:00 | 54.06 | 54.06
2017-10-08 06:30 | 31.96 | 31.94
2017-10-08 07:00 | 25.4 | 25.2
2017-10-08 07:30 | 29.27 | 25.17
2017-10-08 08:00 | 30.17 | 22.9
2017-10-08 08:30 | 51.69 | 47.57
2017-10-08 09:00 | 52.2 | 48.19
2017-10-08 09:30 | 58.07 | 55.04
2017-10-08 10:00 | 94.66 | 93.9
2017-10-08 10:30 | 110.71 | 110.63
2017-10-08 11:00 | 105.16 | 105.06
2017-10-08 11:30 | 89.77 | 89.66
2017-10-08 12:00 | 76.01 | 75.83
2017-10-08 12:30 | 99.44 | 99.37
2017-10-08 13:00 | 100.38 | 100.32
2017-10-08 13:30 | 97.1 | 97.03
2017-10-08 14:00 | 106.47 | 106.4
2017-10-08 14:30 | 104.69 | 104.59
2017-10-08 15:00 | 104.29 | 104.2
2017-10-08 15:30 | 112.51 | 112.44
2017-10-08 16:00 | 121.31 | 121.26
2017-10-08 16:30 | 137.02 | 137
2017-10-08 17:00 | 164.46 | 164.43
2017-10-08 17:30 | 176.7 | 176.67
2017-10-08 18:00 | 188.84 | 188.78
2017-10-08 18:30 | 202.5 | 201.91
2017-10-08 19:00 | 201.56 | 200.52
2017-10-08 19:30 | 194.39 | 193.6
2017-10-08 20:00 | 192.72 | 191.67
2017-10-08 20:30 | 189.59 | 188.73
2017-10-08 21:00 | 181.51 | 180.87
2017-10-08 21:30 | 172.83 | 172.28
2017-10-08 22:00 | 145.43 | 144.98
2017-10-08 22:30 | 153.7 | 153.36
2017-10-08 23:00 | 160.45 | 160.18
2017-10-08 23:30 | 128.55 | 128.35
2017-10-09 | 75.86 | 75.67
2017-10-09 00:30 | 52.91 | 52.76
2017-10-09 01:00 | 46.37 | 46.26
2017-10-09 01:30 | 43.64 | 43.52
2017-10-09 02:00 | 51.21 | 49.32
2017-10-09 02:30 | 49.36 | 46.38
2017-10-09 03:00 | 72.79 | 70.78
2017-10-09 03:30 | 67.99 | 65.84
2017-10-09 04:00 | 63.9 | 61.74
2017-10-09 04:30 | 42.36 | 39.3
2017-10-09 05:00 | 45.64 | 43.06
2017-10-09 05:30 | 50.84 | 49.13
2017-10-09 06:00 | 61.22 | 60.24
2017-10-09 06:30 | 122.04 | 121.86
2017-10-09 07:00 | 104.02 | 100.6
2017-10-09 07:30 | 118.1 | 105.35
2017-10-09 08:00 | 128.04 | 114.31
2017-10-09 08:30 | 126.35 | 112.14
2017-10-09 09:00 | 127.27 | 113.23
2017-10-09 09:30 | 144.72 | 131.54
2017-10-09 10:00 | 122.31 | 105.54
2017-10-09 10:30 | 145.47 | 130.15
2017-10-09 11:00 | 166.53 | 152.26
2017-10-09 11:30 | 178.81 | 164.97
2017-10-09 12:00 | 186.26 | 172.26
2017-10-09 12:30 | 194.16 | 181
2017-10-09 13:00 | 193.32 | 180.12
2017-10-09 13:30 | 185.19 | 173.61
2017-10-09 14:00 | 149.13 | 134.58
2017-10-09 14:30 | 140.28 | 124
2017-10-09 15:00 | 140.68 | 124.16
2017-10-09 15:30 | 143.76 | 128.1
2017-10-09 16:00 | 147.54 | 132.47
2017-10-09 16:30 | 146.92 | 132
2017-10-09 17:00 | 148.6 | 134.75
2017-10-09 17:30 | 148.79 | 135.46
2017-10-09 18:00 | 149.06 | 135.07
2017-10-09 18:30 | 157.78 | 142.66
2017-10-09 19:00 | 164.23 | 150.22
2017-10-09 19:30 | 160.94 | 148.42
2017-10-09 20:00 | 157.08 | 146.04
2017-10-09 20:30 | 148.57 | 138.85
2017-10-09 21:00 | 136.53 | 127.41
2017-10-09 21:30 | 131.72 | 123.69
2017-10-09 22:00 | 181.22 | 179.13
2017-10-09 22:30 | 175.85 | 175.63
2017-10-09 23:00 | 174.36 | 174.23
2017-10-09 23:30 | 147.16 | 146.47
2017-10-10 | 108.94 | 108.28
2017-10-10 00:30 | 95.08 | 94.64
2017-10-10 01:00 | 91.29 | 91.04
2017-10-10 01:30 | 82.42 | 82.25
2017-10-10 02:00 | 79.66 | 79.51
2017-10-10 02:30 | 73.55 | 73.41
2017-10-10 03:00 | 79.2 | 79.08
2017-10-10 03:30 | 88.81 | 88.72
2017-10-10 04:00 | 83.66 | 83.61
2017-10-10 04:30 | 96.38 | 96.31
2017-10-10 05:00 | 90.44 | 90.34
2017-10-10 05:30 | 107.52 | 107.39
2017-10-10 06:00 | 97.46 | 97.13
2017-10-10 06:30 | 130.7 | 129.79
2017-10-10 07:00 | 168.77 | 167.31
2017-10-10 07:30 | 189.64 | 181.81
2017-10-10 08:00 | 192.39 | 182.27
2017-10-10 08:30 | 194.97 | 184.73
2017-10-10 09:00 | 196.05 | 183.31
2017-10-10 09:30 | 216.02 | 203.72
2017-10-10 10:00 | 154.21 | 134.91
2017-10-10 10:30 | 168.66 | 156.86
2017-10-10 11:00 | 192.37 | 184.76
2017-10-10 11:30 | 170.1 | 165.77
2017-10-10 12:00 | 199.6 | 195.65
2017-10-10 12:30 | 171.57 | 167.02
2017-10-10 13:00 | 176.2 | 171.59
2017-10-10 13:30 | 212.39 | 208.8
2017-10-10 14:00 | 185.46 | 181.67
2017-10-10 14:30 | 145.72 | 141.01
2017-10-10 15:00 | 139.17 | 134.82
2017-10-10 15:30 | 140.75 | 136.68
2017-10-10 16:00 | 142.98 | 139.28
2017-10-10 16:30 | 148.08 | 144.9
2017-10-10 17:00 | 149.15 | 146.69
2017-10-10 17:30 | 143.2 | 141.56
2017-10-10 18:00 | 140.26 | 138.96
2017-10-10 18:30 | 144.29 | 142.62
2017-10-10 19:00 | 147.96 | 146.17
2017-10-10 19:30 | 144.97 | 143.48
2017-10-10 20:00 | 143.31 | 142.66
2017-10-10 20:30 | 149.64 | 149.57
2017-10-10 21:00 | 127.44 | 127.18
2017-10-10 21:30 | 121.52 | 121.16
2017-10-10 22:00 | 184.64 | 184.49
2017-10-10 22:30 | 179.75 | 179.54
2017-10-10 23:00 | 177.88 | 177.64
2017-10-10 23:30 | 166.24 | 165.84
2017-10-11 | 112.63 | 112.37
2017-10-11 00:30 | 91.75 | 91.23
2017-10-11 01:00 | 121.81 | 121.3
2017-10-11 01:30 | 114.22 | 113.44
2017-10-11 02:00 | 123.11 | 122.24
2017-10-11 02:30 | 121.64 | 120.68
2017-10-11 03:00 | 114.72 | 113.22
2017-10-11 03:30 | 113.87 | 111.48
2017-10-11 04:00 | 116.95 | 114.56
2017-10-11 04:30 | 122.63 | 120.08
2017-10-11 05:00 | 125.37 | 123.24
2017-10-11 05:30 | 123.14 | 120.68
2017-10-11 06:00 | 103.01 | 100.76
2017-10-11 06:30 | 112.88 | 112.82
2017-10-11 07:00 | 120.63 | 120.55
2017-10-11 07:30 | 126.41 | 117.82
2017-10-11 08:00 | 129.31 | 120.13
2017-10-11 08:30 | 127.45 | 116.43
2017-10-11 09:00 | 130.44 | 118.95
2017-10-11 09:30 | 131.85 | 120.25
2017-10-11 10:00 | 138.05 | 126.78
2017-10-11 10:30 | 134.23 | 123.16
2017-10-11 11:00 | 131.48 | 119.98
2017-10-11 11:30 | 133.43 | 121.91
2017-10-11 12:00 | 133.93 | 121.93
2017-10-11 12:30 | 139.25 | 127.31
2017-10-11 13:00 | 136.51 | 123.94
2017-10-11 13:30 | 138 | 125.15
2017-10-11 14:00 | 138.13 | 127.55
2017-10-11 14:30 | 135.48 | 124.66
2017-10-11 15:00 | 134.83 | 124.31
2017-10-11 15:30 | 136.63 | 126.19
2017-10-11 16:00 | 136 | 126.78
2017-10-11 16:30 | 135.11 | 126.97
2017-10-11 17:00 | 135.41 | 127.97
2017-10-11 17:30 | 130.52 | 126.19
2017-10-11 18:00 | 126.35 | 124.57
2017-10-11 18:30 | 130.64 | 128.52
2017-10-11 19:00 | 135.65 | 133.82
2017-10-11 19:30 | 133.56 | 132.25
2017-10-11 20:00 | 128.75 | 128.72
2017-10-11 20:30 | 122.59 | 122.51
2017-10-11 21:00 | 113.53 | 113.4
2017-10-11 21:30 | 107.08 | 106.95
2017-10-11 22:00 | 103.09 | 102.8
2017-10-11 22:30 | 114.41 | 114.25
2017-10-11 23:00 | 113.36 | 113.32
2017-10-11 23:30 | 73.81 | 73.65
2017-10-12 | 57.49 | 57
2017-10-12 00:30 | 48.85 | 48.02
2017-10-12 01:00 | 51.41 | 50.56
2017-10-12 01:30 | 106.75 | 106.22
2017-10-12 02:00 | 112.87 | 112.32
2017-10-12 02:30 | 89.32 | 88.52
2017-10-12 03:00 | 86.98 | 86.18
2017-10-12 03:30 | 107.23 | 106.58
2017-10-12 04:00 | 107.13 | 106.39
2017-10-12 04:30 | 109.23 | 108.54
2017-10-12 05:00 | 113.69 | 113.15
2017-10-12 05:30 | 106.93 | 106.49
2017-10-12 06:00 | 66.29 | 65.88
2017-10-12 06:30 | 78.21 | 78.21
2017-10-12 07:00 | 87.87 | 87.47
2017-10-12 07:30 | 118.82 | 103
2017-10-12 08:00 | 128.75 | 112.01
2017-10-12 08:30 | 128 | 109.4
2017-10-12 09:00 | 135.59 | 112.35
2017-10-12 09:30 | 141.19 | 111.48
2017-10-12 10:00 | 134 | 103.35
2017-10-12 10:30 | 135.72 | 108.33
2017-10-12 11:00 | 142.2 | 116.49
2017-10-12 11:30 | 137.95 | 112.1
2017-10-12 12:00 | 140.87 | 116.1
2017-10-12 12:30 | 142.95 | 119.27
2017-10-12 13:00 | 136.41 | 111.89
2017-10-12 13:30 | 138.96 | 115.07
2017-10-12 14:00 | 137.86 | 113.57
2017-10-12 14:30 | 140.52 | 116.52
2017-10-12 15:00 | 139.8 | 114.97
2017-10-12 15:30 | 137.57 | 114.9
2017-10-12 16:00 | 137.94 | 115.78
2017-10-12 16:30 | 138.51 | 117
2017-10-12 17:00 | 137.89 | 117.15
2017-10-12 17:30 | 137.44 | 117.43
2017-10-12 18:00 | 139.28 | 119.01
2017-10-12 18:30 | 146.21 | 125.6
2017-10-12 19:00 | 151.57 | 131.88
2017-10-12 19:30 | 146.13 | 129.04
2017-10-12 20:00 | 135.85 | 125.81
2017-10-12 20:30 | 132.17 | 122.84
2017-10-12 21:00 | 111.81 | 110.7
2017-10-12 21:30 | 105.91 | 104.73
2017-10-12 22:00 | 102.37 | 101.36
2017-10-12 22:30 | 114.44 | 113.75
2017-10-12 23:00 | 107 | 106.46
2017-10-12 23:30 | 71.6 | 71.06
2017-10-13 | 54.96 | 54.39
2017-10-13 00:30 | 43.12 | 42.53
2017-10-13 01:00 | 48.56 | 48.08
2017-10-13 01:30 | 80.09 | 79.97
2017-10-13 02:00 | 100.27 | 99.38
2017-10-13 02:30 | 97.62 | 96.65
2017-10-13 03:00 | 97.5 | 96.65
2017-10-13 03:30 | 110.89 | 110.11
2017-10-13 04:00 | 112.95 | 112.02
2017-10-13 04:30 | 111.79 | 110.82
2017-10-13 05:00 | 118.24 | 117.28
2017-10-13 05:30 | 81.04 | 80.08
2017-10-13 06:00 | 31.34 | 29.09
2017-10-13 06:30 | 40.57 | 40.02
2017-10-13 07:00 | 52.84 | 52.15
2017-10-13 07:30 | 75.4 | 66.1
2017-10-13 08:00 | 79.41 | 69.73
2017-10-13 08:30 | 80.97 | 62.47
2017-10-13 09:00 | 91.9 | 62.12
2017-10-13 09:30 | 94.81 | 65.24
2017-10-13 10:00 | 98.52 | 71.17
2017-10-13 10:30 | 97.72 | 74.01
2017-10-13 11:00 | 98.67 | 76.27
2017-10-13 11:30 | 105.57 | 80.34
2017-10-13 12:00 | 118.07 | 84.03
2017-10-13 12:30 | 119.63 | 85.72
2017-10-13 13:00 | 136.55 | 108.28
2017-10-13 13:30 | 133.7 | 104.29
2017-10-13 14:00 | 144.51 | 117.77
2017-10-13 14:30 | 211.83 | 194.18
2017-10-13 15:00 | 172.08 | 150.78
2017-10-13 15:30 | 123.01 | 94.07
2017-10-13 16:00 | 122.91 | 94.71
2017-10-13 16:30 | 113.71 | 95.42
2017-10-13 17:00 | 110.68 | 96
2017-10-13 17:30 | 98.48 | 89.19
2017-10-13 18:00 | 90.59 | 84.71
2017-10-13 18:30 | 93.18 | 86.21
2017-10-13 19:00 | 96.04 | 89.16
2017-10-13 19:30 | 91.58 | 86.62
2017-10-13 20:00 | 88.17 | 86.46
2017-10-13 20:30 | 92.96 | 92.96
2017-10-13 21:00 | 96.63 | 96.46
2017-10-13 21:30 | 105.92 | 104.44
2017-10-13 22:00 | 108.73 | 108.51
2017-10-13 22:30 | 120.08 | 118.97
2017-10-13 23:00 | 115.47 | 114.27
2017-10-13 23:30 | 83.58 | 81.89
2017-10-14 | 69.37 | 65.16
2017-10-14 00:30 | 60.05 | 55.83
2017-10-14 01:00 | 61.86 | 58.15
2017-10-14 01:30 | 79.21 | 76.34
2017-10-14 02:00 | 78.14 | 75.36
2017-10-14 02:30 | 79.45 | 76.54
2017-10-14 03:00 | 84.28 | 80.46
2017-10-14 03:30 | 86.79 | 83.29
2017-10-14 04:00 | 85.99 | 82.73
2017-10-14 04:30 | 75.55 | 71.65
2017-10-14 05:00 | 69.97 | 65.44
2017-10-14 05:30 | 63.63 | 60.13
2017-10-14 06:00 | 16.28 | -12.51
2017-10-14 06:30 | 52.62 | -52.59
2017-10-14 07:00 | 38.9 | 35.11
2017-10-14 07:30 | 65.23 | 62.09
2017-10-14 08:00 | 73.18 | 72.55
2017-10-14 08:30 | 62.56 | 62.47
2017-10-14 09:00 | 42.93 | 42.38
2017-10-14 09:30 | 37.67 | 37.38
2017-10-14 10:00 | 21.62 | 21.38
2017-10-14 10:30 | 13.55 | 13.23
2017-10-14 11:00 | 8.73 | 7.76
2017-10-14 11:30 | 13.97 | -13.63
2017-10-14 12:00 | 7.62 | -6.68
2017-10-14 12:30 | 26.8 | 25.7
2017-10-14 13:00 | 76.73 | 75.95
2017-10-14 13:30 | 91.31 | 90.45
2017-10-14 14:00 | 83.8 | 82.67
2017-10-14 14:30 | 80.99 | 79.71
2017-10-14 15:00 | 81.09 | 79.72
2017-10-14 15:30 | 73.27 | 71.83
2017-10-14 16:00 | 80.19 | 78.88
2017-10-14 16:30 | 100.43 | 99.46
2017-10-14 17:00 | 106.62 | 105.89
2017-10-14 17:30 | 103.65 | 102.95
2017-10-14 18:00 | 105.84 | 105.33
2017-10-14 18:30 | 108.04 | 107.55
2017-10-14 19:00 | 111.31 | 110.8
2017-10-14 19:30 | 109.32 | 108.96
2017-10-14 20:00 | 106.81 | 106.77
2017-10-14 20:30 | 135.48 | 135.47
2017-10-14 21:00 | 94.19 | 94.18
2017-10-14 21:30 | 91.68 | 91.61
2017-10-14 22:00 | 97.88 | 97.68
2017-10-14 22:30 | 113.37 | 113.12
2017-10-14 23:00 | 120.18 | 119.82
2017-10-14 23:30 | 103.51 | 102.9
2017-10-15 | 76.79 | 75.66
2017-10-15 00:30 | 31.99 | 29.62
2017-10-15 01:00 | 21.57 | 18.55
2017-10-15 01:30 | 22.68 | 19.86
2017-10-15 02:00 | 28.53 | 22.58
2017-10-15 02:30 | 17.97 | 6.89
2017-10-15 03:00 | 17.69 | 6.55
2017-10-15 03:30 | 20.2 | 10.68
2017-10-15 04:00 | 18.47 | 7.03
2017-10-15 04:30 | 16.1 | -2.02
2017-10-15 05:00 | 17.83 | -8.44
2017-10-15 05:30 | 20.19 | -15.08
2017-10-15 06:00 | 44.03 | -43.53
2017-10-15 06:30 | 19.74 | -16.25
2017-10-15 07:00 | 22.17 | 14.92
2017-10-15 07:30 | 34.92 | 28.38
2017-10-15 08:00 | 35.47 | 27.72
2017-10-15 08:30 | 29.24 | 28.01
2017-10-15 09:00 | 56.11 | 56.11
2017-10-15 09:30 | 76.32 | 76.32
2017-10-15 10:00 | 79.51 | 79.49
2017-10-15 10:30 | 79.36 | 79.29
2017-10-15 11:00 | 67.07 | 67.02
2017-10-15 11:30 | 60.1 | 60.08
2017-10-15 12:00 | 62.97 | 62.96
2017-10-15 12:30 | 65.47 | 65.46
2017-10-15 13:00 | 57.21 | 57.21
2017-10-15 13:30 | 62.91 | 62.91
2017-10-15 14:00 | 60.85 | 60.85
2017-10-15 14:30 | 60.89 | 60.89
2017-10-15 15:00 | 75.4 | 75.4
2017-10-15 15:30 | 77.78 | 77.78
2017-10-15 16:00 | 82.97 | 82.97
2017-10-15 16:30 | 85.04 | 85.04
2017-10-15 17:00 | 88.88 | 88.87
2017-10-15 17:30 | 100.02 | 99.99
2017-10-15 18:00 | 102.3 | 102.08
2017-10-15 18:30 | 121.25 | 113.16
2017-10-15 19:00 | 120.46 | 115.8
2017-10-15 19:30 | 118.59 | 114.32
2017-10-15 20:00 | 107.88 | 103.81
2017-10-15 20:30 | 78.56 | 73.22
2017-10-15 21:00 | 42.95 | 32.3
2017-10-15 21:30 | 28.91 | 23.77
2017-10-15 22:00 | 8.08 | 5.96
2017-10-15 22:30 | 24.63 | 23.59
2017-10-15 23:00 | 39 | 38.03
2017-10-15 23:30 | 13.6 | 9.07
2017-10-16 | 24.03 | -21.98
2017-10-16 00:30 | 36.49 | -35.28
2017-10-16 01:00 | 51.04 | -50.38
2017-10-16 01:30 | 55.6 | -55.13
2017-10-16 02:00 | 57.77 | -57.43
2017-10-16 02:30 | 46.65 | -45.96
2017-10-16 03:00 | 45.77 | -45.06
2017-10-16 03:30 | 43.84 | -43.1
2017-10-16 04:00 | 44.84 | -43.79
2017-10-16 04:30 | 46.81 | -45.98
2017-10-16 05:00 | 48.17 | -47.44
2017-10-16 05:30 | 42.99 | -42.26
2017-10-16 06:00 | 49.55 | -49.23
2017-10-16 06:30 | 50.32 | -48.71
2017-10-16 07:00 | 51.48 | -39.41
2017-10-16 07:30 | 46.63 | -29.12
2017-10-16 08:00 | 46.26 | -23.1
2017-10-16 08:30 | 51.16 | -24.42
2017-10-16 09:00 | 44.61 | -14.79
2017-10-16 09:30 | 27.3 | -8.92
2017-10-16 10:00 | 34.35 | -23
2017-10-16 10:30 | 28.23 | -10.67
2017-10-16 11:00 | 33.57 | -20.18
2017-10-16 11:30 | 82.73 | 81.83
2017-10-16 12:00 | 101.4 | 99.52
2017-10-16 12:30 | 108.57 | 102.89
2017-10-16 13:00 | 109.41 | 103.99
2017-10-16 13:30 | 102.94 | 97.16
2017-10-16 14:00 | 110.21 | 104.77
2017-10-16 14:30 | 112.46 | 107.23
2017-10-16 15:00 | 113.11 | 108.2
2017-10-16 15:30 | 107.76 | 103.01
2017-10-16 16:00 | 108.93 | 104.63
2017-10-16 16:30 | 112.88 | 108.84
2017-10-16 17:00 | 116.95 | 113.09
2017-10-16 17:30 | 117.06 | 113.35
2017-10-16 18:00 | 117.5 | 113.36
2017-10-16 18:30 | 134.59 | 124.45
2017-10-16 19:00 | 138.34 | 129.01
2017-10-16 19:30 | 134.06 | 125.51
2017-10-16 20:00 | 130.23 | 122.14
2017-10-16 20:30 | 113.78 | 105.82
2017-10-16 21:00 | 72.7 | 60.36
2017-10-16 21:30 | 49.16 | 36.99
2017-10-16 22:00 | 33.77 | 33.36
2017-10-16 22:30 | 59.89 | 59.81
2017-10-16 23:00 | 66.33 | 66.31
2017-10-16 23:30 | 38.89 | 38.88
2017-10-17 | 4.75 | 4.19
2017-10-17 00:30 | 20.25 | -18.53
2017-10-17 01:00 | 30.89 | -29.51
2017-10-17 01:30 | 36.3 | -35.08
2017-10-17 02:00 | 34.69 | -33.4
2017-10-17 02:30 | 33.98 | -32.69
2017-10-17 03:00 | 15.54 | -13.08
2017-10-17 03:30 | 40.63 | -39.52
2017-10-17 04:00 | 38.36 | -37.52
2017-10-17 04:30 | 22.87 | -21.84
2017-10-17 05:00 | 9.73 | -7.12
2017-10-17 05:30 | 14.77 | 13.28
2017-10-17 06:00 | 30.97 | 30.23
2017-10-17 06:30 | 51.67 | 50.58
2017-10-17 07:00 | 72.29 | 67.54
2017-10-17 07:30 | 91.37 | 81.84
2017-10-17 08:00 | 94.24 | 88.74
2017-10-17 08:30 | 69.79 | 60.09
2017-10-17 09:00 | 71.39 | 60.74
2017-10-17 09:30 | 71.32 | 60.02
2017-10-17 10:00 | 51.97 | 34.87
2017-10-17 10:30 | 54.39 | 36.7
2017-10-17 11:00 | 71.29 | 57.91
2017-10-17 11:30 | 76.55 | 65.04
2017-10-17 12:00 | 72.71 | 61.5
2017-10-17 12:30 | 81.43 | 71.91
2017-10-17 13:00 | 84.09 | 75.74
2017-10-17 13:30 | 92.2 | 84.28
2017-10-17 14:00 | 110.49 | 104.02
2017-10-17 14:30 | 113.14 | 106.96
2017-10-17 15:00 | 113.49 | 107.53
2017-10-17 15:30 | 111.32 | 105.54
2017-10-17 16:00 | 112.51 | 106.97
2017-10-17 16:30 | 114.39 | 109.26
2017-10-17 17:00 | 120.12 | 115.24
2017-10-17 17:30 | 123.92 | 119.05
2017-10-17 18:00 | 124.62 | 119.75
2017-10-17 18:30 | 130.69 | 125.47
2017-10-17 19:00 | 134.99 | 130.04
2017-10-17 19:30 | 129.8 | 125.44
2017-10-17 20:00 | 131.44 | 127.59
2017-10-17 20:30 | 122.7 | 122.35
2017-10-17 21:00 | 107.93 | 107.9
2017-10-17 21:30 | 99.9 | 99.79
2017-10-17 22:00 | 78.89 | 78.51
2017-10-17 22:30 | 110.11 | 109.67
2017-10-17 23:00 | 108.91 | 108.18
2017-10-17 23:30 | 70.66 | 69.05
2017-10-18 | 24.76 | 20.24
2017-10-18 00:30 | 12.19 | 1.77
2017-10-18 01:00 | 14.86 | -7.33
2017-10-18 01:30 | 18.54 | -12.83
2017-10-18 02:00 | 28.61 | -25.61
2017-10-18 02:30 | 21.81 | -17.1
2017-10-18 03:00 | 25.07 | -21.14
2017-10-18 03:30 | 48.99 | 46.72
2017-10-18 04:00 | 15.88 | 3.91
2017-10-18 04:30 | 14.91 | 0.66
2017-10-18 05:00 | 19.97 | -14.33
2017-10-18 05:30 | 13.53 | -3.88
2017-10-18 06:00 | 14.67 | 9.13
2017-10-18 06:30 | 25.32 | 21.07
2017-10-18 07:00 | 60.19 | 57.9
2017-10-18 07:30 | 96.75 | 95.78
2017-10-18 08:00 | 104.99 | 104.3
2017-10-18 08:30 | 103.48 | 102.98
2017-10-18 09:00 | 86.04 | 85.6
2017-10-18 09:30 | 67.97 | 67.88
2017-10-18 10:00 | 62.71 | 61.77
2017-10-18 10:30 | 41.92 | 40.17
2017-10-18 11:00 | 37.66 | 35.73
2017-10-18 11:30 | 48.65 | 47.38
2017-10-18 12:00 | 51.66 | 50.66
2017-10-18 12:30 | 57.77 | 56.98
2017-10-18 13:00 | 51.68 | 50.87
2017-10-18 13:30 | 43.74 | 42.68
2017-10-18 14:00 | 72.97 | 72.02
2017-10-18 14:30 | 39.95 | 37.44
2017-10-18 15:00 | 32.14 | 29.05
2017-10-18 15:30 | 30.68 | 27.83
2017-10-18 16:00 | 48.57 | 47.7
2017-10-18 16:30 | 68.33 | 68.06
2017-10-18 17:00 | 74.72 | 74.4
2017-10-18 17:30 | 77.12 | 76.85
2017-10-18 18:00 | 76.8 | 76.43
2017-10-18 18:30 | 81.84 | 81.34
2017-10-18 19:00 | 86.22 | 85.81
2017-10-18 19:30 | 83.86 | 83.65
2017-10-18 20:00 | 100.81 | 100.77
2017-10-18 20:30 | 105.52 | 105.52
2017-10-18 21:00 | 80.85 | 80.81
2017-10-18 21:30 | 76.54 | 75.98
2017-10-18 22:00 | 47.19 | 45.03
2017-10-18 22:30 | 26.58 | 22.89
2017-10-18 23:00 | 62.71 | 61.6
2017-10-18 23:30 | 27.95 | 26.12
2017-10-19 | 9.58 | 1.03
2017-10-19 00:30 | 14.06 | -9.74
2017-10-19 01:00 | 34.13 | -32.31
2017-10-19 01:30 | 45.54 | -44.11
2017-10-19 02:00 | 55.46 | -54.13
2017-10-19 02:30 | 58.06 | -56.74
2017-10-19 03:00 | 49.48 | -48.01
2017-10-19 03:30 | 53.72 | -52.37
2017-10-19 04:00 | 52.21 | -51.14
2017-10-19 04:30 | 49.9 | -48.84
2017-10-19 05:00 | 48.43 | -47.43
2017-10-19 05:30 | 36.21 | -34.63
2017-10-19 06:00 | 14.6 | -10.83
2017-10-19 06:30 | 17.65 | 14.3
2017-10-19 07:00 | 29.73 | 29.73
2017-10-19 07:30 | 57.89 | 57.78
2017-10-19 08:00 | 70.28 | 70.05
2017-10-19 08:30 | 70.08 | 69.59
2017-10-19 09:00 | 49.96 | 48.65
2017-10-19 09:30 | 34.12 | 30.77
2017-10-19 10:00 | 32.58 | 27.73
2017-10-19 10:30 | 28.63 | 22.6
2017-10-19 11:00 | 36.91 | 32.05
2017-10-19 11:30 | 27.16 | 19.94
2017-10-19 12:00 | 19.24 | 5.25
2017-10-19 12:30 | 28.4 | 21.36
2017-10-19 13:00 | 20.31 | 0.84
2017-10-19 13:30 | 19.36 | 2.51
2017-10-19 14:00 | 19.33 | 5.26
2017-10-19 14:30 | 18.15 | 1.88
2017-10-19 15:00 | 22.61 | 15.45
2017-10-19 15:30 | 19.68 | 11.83
2017-10-19 16:00 | 29.09 | 18.23
2017-10-19 16:30 | 53.65 | 33.05
2017-10-19 17:00 | 58.82 | 48.66
2017-10-19 17:30 | 68.57 | 66.05
2017-10-19 18:00 | 60.56 | 58.06
2017-10-19 18:30 | 90.17 | 87.83
2017-10-19 19:00 | 105.46 | 103.34
2017-10-19 19:30 | 87.82 | 85.8
2017-10-19 20:00 | 88.8 | 88
2017-10-19 20:30 | 108.89 | 108.26
2017-10-19 21:00 | 87.36 | 87.15
2017-10-19 21:30 | 71.31 | 71.24
2017-10-19 22:00 | 48.37 | 48
2017-10-19 22:30 | 46.59 | 45.87
2017-10-19 23:00 | 65.77 | 65.21
2017-10-19 23:30 | 45.64 | 44.41
2017-10-20 | 14.68 | -11.08
2017-10-20 00:30 | 29.22 | -27.86
2017-10-20 01:00 | 42.1 | -41.33
2017-10-20 01:30 | 50.74 | -50.17
2017-10-20 02:00 | 59.2 | -58.78
2017-10-20 02:30 | 57.02 | -56.49
2017-10-20 03:00 | 56.3 | -55.8
2017-10-20 03:30 | 56.95 | -56.46
2017-10-20 04:00 | 57.79 | -57.22
2017-10-20 04:30 | 52.48 | -51.72
2017-10-20 05:00 | 42.92 | -41.9
2017-10-20 05:30 | 34.34 | -33.08
2017-10-20 06:00 | 54.38 | -54.02
2017-10-20 06:30 | 47.2 | -47.19
2017-10-20 07:00 | 57.68 | -37.75
2017-10-20 07:30 | 59.66 | -26.32
2017-10-20 08:00 | 63.52 | -25.41
2017-10-20 08:30 | 66.07 | -23.59
2017-10-20 09:00 | 71.69 | -28.8
2017-10-20 09:30 | 73.46 | -28.48
2017-10-20 10:00 | 74.68 | -23.34
2017-10-20 10:30 | 74.81 | -21.49
2017-10-20 11:00 | 75.32 | -21.42
2017-10-20 11:30 | 74.79 | -19.56
2017-10-20 12:00 | 76.32 | -23.6
2017-10-20 12:30 | 76.38 | -23.27
2017-10-20 13:00 | 71.63 | -5.25
2017-10-20 13:30 | 73.6 | -17.37
2017-10-20 14:00 | 74.04 | -17.73
2017-10-20 14:30 | 72.37 | -15.05
2017-10-20 15:00 | 73.22 | -21.3
2017-10-20 15:30 | 72.2 | -22.75
2017-10-20 16:00 | 70.53 | -20.07
2017-10-20 16:30 | 69.02 | -17.13
2017-10-20 17:00 | 64.7 | 8.4
2017-10-20 17:30 | 109.93 | 93.07
2017-10-20 18:00 | 105.25 | 89.74
2017-10-20 18:30 | 103.54 | 86.13
2017-10-20 19:00 | 123.84 | 109.82
2017-10-20 19:30 | 112 | 97.01
2017-10-20 20:00 | 89.44 | 81.7
2017-10-20 20:30 | 71.4 | 67.37
2017-10-20 21:00 | 58.55 | 54.52
2017-10-20 21:30 | 48.58 | 44.28
2017-10-20 22:00 | 32.27 | 26.36
2017-10-20 22:30 | 43.01 | 39.6
2017-10-20 23:00 | 49.41 | 46.97
2017-10-20 23:30 | 29.41 | 26.33
2017-10-21 | 20.08 | -14.61
2017-10-21 00:30 | 36.95 | -34.11
2017-10-21 01:00 | 49.39 | -47.26
2017-10-21 01:30 | 62.42 | -60.53
2017-10-21 02:00 | 64.58 | -62.72
2017-10-21 02:30 | 63.81 | -62.04
2017-10-21 03:00 | 56.21 | -54.38
2017-10-21 03:30 | 47.15 | -45.73
2017-10-21 04:00 | 57.61 | -56.34
2017-10-21 04:30 | 61.89 | -60.65
2017-10-21 05:00 | 61.31 | -60.11
2017-10-21 05:30 | 58.63 | -57.55
2017-10-21 06:00 | 51.54 | -50.27
2017-10-21 06:30 | 42.65 | -40.85
2017-10-21 07:00 | 31.22 | -28.57
2017-10-21 07:30 | 34.06 | -30.75
2017-10-21 08:00 | 20.06 | -10.46
2017-10-21 08:30 | 28.41 | 20.31
2017-10-21 09:00 | 37.27 | 30.04
2017-10-21 09:30 | 67.26 | 37.49
2017-10-21 10:00 | 86.84 | 66.54
2017-10-21 10:30 | 88.07 | 68.86
2017-10-21 11:00 | 78.33 | 56.39
2017-10-21 11:30 | 68.58 | 42.35
2017-10-21 12:00 | 65.73 | 38.14
2017-10-21 12:30 | 65.01 | 38.36
2017-10-21 13:00 | 68.66 | 45.44
2017-10-21 13:30 | 59.1 | 50.72
2017-10-21 14:00 | 58.27 | 50.9
2017-10-21 14:30 | 61.9 | 54.94
2017-10-21 15:00 | 49.91 | 41.66
2017-10-21 15:30 | 55.13 | 48.15
2017-10-21 16:00 | 58.45 | 51.87
2017-10-21 16:30 | 64.36 | 58.5
2017-10-21 17:00 | 61.69 | 55.25
2017-10-21 17:30 | 71.26 | 65.63
2017-10-21 18:00 | 77.12 | 71.6
2017-10-21 18:30 | 89.1 | 83.01
2017-10-21 19:00 | 73.44 | 66.18
2017-10-21 19:30 | 63.37 | 55.76
2017-10-21 20:00 | 57.36 | 49.83
2017-10-21 20:30 | 65.54 | 59.89
2017-10-21 21:00 | 51.23 | 44.29
2017-10-21 21:30 | 31.91 | 31.35
2017-10-21 22:00 | 21.27 | 19.68
2017-10-21 22:30 | 32.02 | 30.65
2017-10-21 23:00 | 46.06 | 44.79
2017-10-21 23:30 | 24.69 | 21.92
2017-10-22 | 17.18 | -14.15
2017-10-22 00:30 | 25.34 | -23.4
2017-10-22 01:00 | 46.22 | -45.56
2017-10-22 01:30 | 57.3 | -56.99
2017-10-22 02:00 | 59.83 | -59.66
2017-10-22 02:30 | 59.81 | -59.64
2017-10-22 03:00 | 59.68 | -59.51
2017-10-22 03:30 | 60.73 | -60.53
2017-10-22 04:00 | 62.29 | -62.11
2017-10-22 04:30 | 61.6 | -61.38
2017-10-22 05:00 | 61.42 | -61.22
2017-10-22 05:30 | 61.62 | -61.5
2017-10-22 06:00 | 61 | -60.88
2017-10-22 06:30 | 57.77 | -57.62
2017-10-22 07:00 | 50.05 | -49.81
2017-10-22 07:30 | 54.04 | -53.86
2017-10-22 08:00 | 57.34 | -57.22
2017-10-22 08:30 | 47.39 | -47.24
2017-10-22 09:00 | 47.51 | -47.47
2017-10-22 09:30 | 45.39 | -45.38
2017-10-22 10:00 | 44.03 | -43.96
2017-10-22 10:30 | 42.97 | -42.8
2017-10-22 11:00 | 42.03 | -40.89
2017-10-22 11:30 | 44.78 | -37.52
2017-10-22 12:00 | 37.66 | -29.71
2017-10-22 12:30 | 37.6 | -29.63
2017-10-22 13:00 | 31.74 | -22.46
2017-10-22 13:30 | 29.85 | -19.86
2017-10-22 14:00 | 35.99 | -28.36
2017-10-22 14:30 | 24.71 | -13.43
2017-10-22 15:00 | 23.14 | -12.13
2017-10-22 15:30 | 19.39 | -5.59
2017-10-22 16:00 | 25.38 | -16.61
2017-10-22 16:30 | 21.59 | -11.2
2017-10-22 17:00 | 22.74 | -12.23
2017-10-22 17:30 | 19.1 | 2
2017-10-22 18:00 | 25.5 | 16.19
2017-10-22 18:30 | 54.03 | 42.89
2017-10-22 19:00 | 87.52 | 69.82
2017-10-22 19:30 | 77.72 | 58.64
2017-10-22 20:00 | 67.92 | 48.63
2017-10-22 20:30 | 59.27 | 37.28
2017-10-22 21:00 | 34.64 | 18.25
2017-10-22 21:30 | 18.36 | 12.67
2017-10-22 22:00 | 9.18 | -2.73
2017-10-22 22:30 | 8.06 | 2.57
2017-10-22 23:00 | 8.44 | 2.8
2017-10-22 23:30 | 21.54 | -20.16
2017-10-23 | 47.56 | -47.2
2017-10-23 00:30 | 55.44 | -55.28
2017-10-23 01:00 | 56.42 | -56.31
2017-10-23 01:30 | 56.43 | -56.32
2017-10-23 02:00 | 56.58 | -56.47
2017-10-23 02:30 | 57.12 | -57.03
2017-10-23 03:00 | 56.14 | -56.03
2017-10-23 03:30 | 55.81 | -55.71
2017-10-23 04:00 | 50 | -49.67
2017-10-23 04:30 | 53.57 | -53.14
2017-10-23 05:00 | 54.82 | -54.41
2017-10-23 05:30 | 56 | -55.72
2017-10-23 06:00 | 54.65 | -54.39
2017-10-23 06:30 | 43.77 | -42.73
2017-10-23 07:00 | 34.47 | -32.66
2017-10-23 07:30 | 27.41 | -20.34
2017-10-23 08:00 | 35.35 | -14.77
2017-10-23 08:30 | 49.38 | -15.86
2017-10-23 09:00 | 74.08 | -26.34
2017-10-23 09:30 | 67.55 | -24.87
2017-10-23 10:00 | 67.76 | -15.08
2017-10-23 10:30 | 69.29 | -10.38
2017-10-23 11:00 | 72.97 | -11.64
2017-10-23 11:30 | 71.01 | -13.28
2017-10-23 12:00 | 69.36 | -15.77
2017-10-23 12:30 | 70.13 | -27.76
2017-10-23 13:00 | 69.36 | -26.27
2017-10-23 13:30 | 70.4 | -31.17
2017-10-23 14:00 | 71.84 | -37.55
2017-10-23 14:30 | 78.24 | -50.14
2017-10-23 15:00 | 69.35 | -37.8
2017-10-23 15:30 | 65.08 | -27.88
2017-10-23 16:00 | 65.18 | -29.67
2017-10-23 16:30 | 64.8 | -31.91
2017-10-23 17:00 | 63.75 | -28.56
2017-10-23 17:30 | 55.54 | 4.67
2017-10-23 18:00 | 93.53 | 77.98
2017-10-23 18:30 | 97.87 | 81.16
2017-10-23 19:00 | 113.58 | 99.53
2017-10-23 19:30 | 95.23 | 79.69
2017-10-23 20:00 | 74.65 | 54.09
2017-10-23 20:30 | 64.73 | 40.99
2017-10-23 21:00 | 36.39 | 27.1
2017-10-23 21:30 | 22.09 | 17.23
2017-10-23 22:00 | 15.37 | -8.86
2017-10-23 22:30 | 9.94 | 1.16
2017-10-23 23:00 | 16.35 | 13.99
2017-10-23 23:30 | 9.63 | 3.98
2017-10-24 | 33.07 | -31.25
2017-10-24 00:30 | 48.35 | -46.83
2017-10-24 01:00 | 62.62 | -60.9
2017-10-24 01:30 | 62.58 | -60.8
2017-10-24 02:00 | 62.76 | -61.01
2017-10-24 02:30 | 63 | -61.22
2017-10-24 03:00 | 63.02 | -61.14
2017-10-24 03:30 | 62.94 | -61.38
2017-10-24 04:00 | 59.05 | -57.78
2017-10-24 04:30 | 56.87 | -55.77
2017-10-24 05:00 | 57.72 | -56.52
2017-10-24 05:30 | 59.35 | -57.79
2017-10-24 06:00 | 53.93 | -52.51
2017-10-24 06:30 | 46.63 | -45.64
2017-10-24 07:00 | 40.34 | -37.58
2017-10-24 07:30 | 33.43 | -26.1
2017-10-24 08:00 | 41.77 | -23.57
2017-10-24 08:30 | 47.56 | -29.86
2017-10-24 09:00 | 50.74 | -31.1
2017-10-24 09:30 | 53.94 | -33.14
2017-10-24 10:00 | 55.34 | -33.58
2017-10-24 10:30 | 57.37 | -36.2
2017-10-24 11:00 | 54.26 | -35.48
2017-10-24 11:30 | 52.96 | -34.94
2017-10-24 12:00 | 53.55 | -35.68
2017-10-24 12:30 | 52.39 | -34.06
2017-10-24 13:00 | 51.21 | -31.83
2017-10-24 13:30 | 50.29 | -31.2
2017-10-24 14:00 | 48.93 | -28.49
2017-10-24 14:30 | 48.66 | -27.86
2017-10-24 15:00 | 47.73 | -25.18
2017-10-24 15:30 | 18.78 | -9.75
2017-10-24 16:00 | 118.03 | 117.75
2017-10-24 16:30 | 115.98 | 115.5
2017-10-24 17:00 | 104.44 | 104.41
2017-10-24 17:30 | 51.51 | -43.25
2017-10-24 18:00 | 54.91 | -40.33
2017-10-24 18:30 | 55.27 | -39.57
2017-10-24 19:00 | 16.09 | 9.26
2017-10-24 19:30 | 79.36 | 79.36
2017-10-24 20:00 | 104.45 | 101.8
2017-10-24 20:30 | 120.92 | 120.66
2017-10-24 21:00 | 36.97 | 35.48
2017-10-24 21:30 | 27 | 23.33
2017-10-24 22:00 | 17.32 | 2.07
2017-10-24 22:30 | 28.26 | 18.51
2017-10-24 23:00 | 48.33 | 43.04
2017-10-24 23:30 | 23.18 | 15.47
2017-10-25 | 22.89 | -16.01
2017-10-25 00:30 | 36.81 | -33.74
2017-10-25 01:00 | 52.56 | -51.93
2017-10-25 01:30 | 48.55 | -47.68
2017-10-25 02:00 | 50.24 | -49.49
2017-10-25 02:30 | 49.01 | -48.18
2017-10-25 03:00 | 49.54 | -48.88
2017-10-25 03:30 | 51.04 | -50.45
2017-10-25 04:00 | 50.02 | -49.4
2017-10-25 04:30 | 52.2 | -51.57
2017-10-25 05:00 | 46.42 | -45.43
2017-10-25 05:30 | 58.1 | -57.94
2017-10-25 06:00 | 51.35 | -50.98
2017-10-25 06:30 | 45.21 | -44.7
2017-10-25 07:00 | 36.23 | -36.23
2017-10-25 07:30 | 35.68 | -24.59
2017-10-25 08:00 | 24.51 | -13.47
2017-10-25 08:30 | 31.15 | -19.74
2017-10-25 09:00 | 33.8 | -20.25
2017-10-25 09:30 | 36.79 | -23.56
2017-10-25 10:00 | 37.84 | -23.3
2017-10-25 10:30 | 40.17 | -24.16
2017-10-25 11:00 | 40.97 | -23.57
2017-10-25 11:30 | 35.41 | -21.73
2017-10-25 12:00 | 34.03 | -18.91
2017-10-25 12:30 | 32.91 | -15.43
2017-10-25 13:00 | 32.73 | -12.96
2017-10-25 13:30 | 31.73 | -9.46
2017-10-25 14:00 | 33.71 | -12.06
2017-10-25 14:30 | 34.18 | -9.2
2017-10-25 15:00 | 36.51 | -8.54
2017-10-25 15:30 | 32.04 | -5.23
2017-10-25 16:00 | 29.95 | -5.39
2017-10-25 16:30 | 28.59 | -7.78
2017-10-25 17:00 | 26.34 | 6.56
2017-10-25 17:30 | 22.31 | -7.64
2017-10-25 18:00 | 19.57 | -7.68
2017-10-25 18:30 | 20.81 | -3.23
2017-10-25 19:00 | 23.8 | 9.59
2017-10-25 19:30 | 65.57 | 64.9
2017-10-25 20:00 | 78.35 | 78.33
2017-10-25 20:30 | 61.16 | 60.69
2017-10-25 21:00 | 38.39 | 32.26
2017-10-25 21:30 | 20.84 | 19.91
2017-10-25 22:00 | 16.31 | 9.4
2017-10-25 22:30 | 39.87 | 35.48
2017-10-25 23:00 | 59.55 | 57.07
2017-10-25 23:30 | 29.93 | 25.43
2017-10-26 | 20.32 | -14.79
2017-10-26 00:30 | 37.74 | -35.57
2017-10-26 01:00 | 53.21 | -52.24
2017-10-26 01:30 | 58.77 | -58.03
2017-10-26 02:00 | 60.48 | -59.87
2017-10-26 02:30 | 60.08 | -59.49
2017-10-26 03:00 | 32.81 | -30.8
2017-10-26 03:30 | 19.2 | 10.24
2017-10-26 04:00 | 20.95 | 12.14
2017-10-26 04:30 | 21.49 | 12.57
2017-10-26 05:00 | 20.06 | 11.03
2017-10-26 05:30 | 18.54 | 10.26
2017-10-26 06:00 | 24.37 | 19.18
2017-10-26 06:30 | 29.9 | 27.82
2017-10-26 07:00 | 40.18 | 40.1
2017-10-26 07:30 | 53.04 | 52.9
2017-10-26 08:00 | 63.25 | 58.49
2017-10-26 08:30 | 62.48 | 53.94
2017-10-26 09:00 | 77.23 | 55.71
2017-10-26 09:30 | 71.2 | 29.5
2017-10-26 10:00 | 66.79 | 14.3
2017-10-26 10:30 | 66.69 | 13.73
2017-10-26 11:00 | 63.1 | 6.21
2017-10-26 11:30 | 64.68 | 9.18
2017-10-26 12:00 | 67.12 | 11.81
2017-10-26 12:30 | 68.27 | 15.43
2017-10-26 13:00 | 70.78 | 19.73
2017-10-26 13:30 | 69.96 | 23.91
2017-10-26 14:00 | 75.59 | 36.65
2017-10-26 14:30 | 86.16 | 53.45
2017-10-26 15:00 | 96.12 | 69.35
2017-10-26 15:30 | 104.28 | 79.32
2017-10-26 16:00 | 110.83 | 88.46
2017-10-26 16:30 | 92.67 | 66.89
2017-10-26 17:00 | 89.56 | 65.57
2017-10-26 17:30 | 85.54 | 62.3
2017-10-26 18:00 | 99.56 | 80.4
2017-10-26 18:30 | 116.58 | 102.31
2017-10-26 19:00 | 119.05 | 107.12
2017-10-26 19:30 | 95.82 | 91.36
2017-10-26 20:00 | 69.6 | 64.54
2017-10-26 20:30 | 58.04 | 52.09
2017-10-26 21:00 | 42.69 | 34.38
2017-10-26 21:30 | 24.86 | 11.72
2017-10-26 22:00 | 0.66 | -0.17
2017-10-26 22:30 | 34.75 | 31.34
2017-10-26 23:00 | 65.69 | 63.1
2017-10-26 23:30 | 53.91 | 49.55
2017-10-27 | 21.93 | 9.14
2017-10-27 00:30 | 29.48 | -25.65
2017-10-27 01:00 | 38.16 | -36.5
2017-10-27 01:30 | 37.7 | -35.92
2017-10-27 02:00 | 33.44 | -30.83
2017-10-27 02:30 | 37.33 | -35.07
2017-10-27 03:00 | 42.08 | -40.2
2017-10-27 03:30 | 38.27 | -36.12
2017-10-27 04:00 | 41.57 | -39.29
2017-10-27 04:30 | 35.22 | -32.06
2017-10-27 05:00 | 23.65 | -18.64
2017-10-27 05:30 | 26.42 | -23.07
2017-10-27 06:00 | 44.15 | -43.4
2017-10-27 06:30 | 43.73 | -43.72
2017-10-27 07:00 | 38.55 | -37.76
2017-10-27 07:30 | 28.23 | -26.93
2017-10-27 08:00 | 26.25 | -24.13
2017-10-27 08:30 | 32.32 | -26.61
2017-10-27 09:00 | 36.19 | -27.85
2017-10-27 09:30 | 38.82 | -30.07
2017-10-27 10:00 | 38.81 | -28.98
2017-10-27 10:30 | 40.15 | -28.73
2017-10-27 11:00 | 64.84 | -25.41
2017-10-27 11:30 | 66.5 | -26.06
2017-10-27 12:00 | 66 | -24.13
2017-10-27 12:30 | 65.99 | -24.24
2017-10-27 13:00 | 66.37 | -21.69
2017-10-27 13:30 | 63.66 | -12.5
2017-10-27 14:00 | 63.65 | 0.33
2017-10-27 14:30 | 64.83 | -0.34
2017-10-27 15:00 | 65.26 | -9.48
2017-10-27 15:30 | 62.46 | 4.52
2017-10-27 16:00 | 61.59 | 11.68
2017-10-27 16:30 | 72.64 | 45.96
2017-10-27 17:00 | 121.03 | 110.05
2017-10-27 17:30 | 112.76 | 109.53
2017-10-27 18:00 | 43.48 | 35.46
2017-10-27 18:30 | 103.9 | 100.61
2017-10-27 19:00 | 129.21 | 126.18
2017-10-27 19:30 | 121.99 | 119.62
2017-10-27 20:00 | 111.77 | 110.23
2017-10-27 20:30 | 103.15 | 102.5
2017-10-27 21:00 | 77.25 | 76.01
2017-10-27 21:30 | 62.32 | 62.26
2017-10-27 22:00 | 68.03 | 67.8
2017-10-27 22:30 | 81.79 | 81.4
2017-10-27 23:00 | 95.65 | 95.32
2017-10-27 23:30 | 64.29 | 63.25
2017-10-28 | 16.03 | 10.3
2017-10-28 00:30 | 17.35 | 12.24
2017-10-28 01:00 | 13.56 | 5.75
2017-10-28 01:30 | 15.08 | -10.24
2017-10-28 02:00 | 15.05 | -9.79
2017-10-28 02:30 | 18.11 | -13.43
2017-10-28 03:00 | 15.14 | -9.02
2017-10-28 03:30 | 14.41 | -7.63
2017-10-28 04:00 | 17.26 | -12.38
2017-10-28 04:30 | 22.98 | -19.59
2017-10-28 05:00 | 15.37 | -9.54
2017-10-28 05:30 | 18.52 | -14.33
2017-10-28 06:00 | 59.25 | -58.91
2017-10-28 06:30 | 42.15 | 40.44
2017-10-28 07:00 | 55.44 | 54.14
2017-10-28 07:30 | 55.87 | 55.03
2017-10-28 08:00 | 62.79 | 62.45
2017-10-28 08:30 | 73.07 | 73.05
2017-10-28 09:00 | 76.63 | 76.62
2017-10-28 09:30 | 76.93 | 76.85
2017-10-28 10:00 | 77.71 | 77.53
2017-10-28 10:30 | 78.64 | 78.32
2017-10-28 11:00 | 87.05 | 82.56
2017-10-28 11:30 | 81.08 | 76.44
2017-10-28 12:00 | 96.61 | 79.7
2017-10-28 12:30 | 99.3 | 80.09
2017-10-28 13:00 | 101.18 | 82.26
2017-10-28 13:30 | 103.61 | 84.99
2017-10-28 14:00 | 102.43 | 83.74
2017-10-28 14:30 | 106.8 | 89.05
2017-10-28 15:00 | 112.03 | 94.96
2017-10-28 15:30 | 115.89 | 101.55
2017-10-28 16:00 | 121.8 | 119.58
2017-10-28 16:30 | 104.21 | 101.4
2017-10-28 17:00 | 99.81 | 96.93
2017-10-28 17:30 | 98.88 | 96.39
2017-10-28 18:00 | 88.92 | 86.31
2017-10-28 18:30 | 100.04 | 97.01
2017-10-28 19:00 | 115.24 | 112.75
2017-10-28 19:30 | 110.95 | 108.72
2017-10-28 20:00 | 86.01 | 83.8
2017-10-28 20:30 | 82.88 | 82.8
2017-10-28 21:00 | 60.22 | 60.17
2017-10-28 21:30 | 66.52 | 66.52
2017-10-28 22:00 | 55.63 | 55.61
2017-10-28 22:30 | 74.34 | 74.32
2017-10-28 23:00 | 83.13 | 83.13
2017-10-28 23:30 | 60.35 | 60.24
2017-10-29 | 34.24 | 29.24
2017-10-29 00:30 | 16.13 | 5.91
2017-10-29 01:00 | 14.98 | -3.43
2017-10-29 01:30 | 14.61 | -5.54
2017-10-29 02:00 | 13.37 | -5.92
2017-10-29 02:30 | 11.94 | -4.99
2017-10-29 03:00 | 16.96 | 10.9
2017-10-29 03:30 | 46.75 | 43.54
2017-10-29 04:00 | 83.7 | 81.96
2017-10-29 04:30 | 28.68 | 19.01
2017-10-29 05:00 | 19.4 | 3.81
2017-10-29 05:30 | 18 | 6.18
2017-10-29 06:00 | 48.61 | -48.61
2017-10-29 06:30 | 36.35 | 33.34
2017-10-29 07:00 | 47.89 | 44.09
2017-10-29 07:30 | 55.9 | 51.3
2017-10-29 08:00 | 61.46 | 56.83
2017-10-29 08:30 | 67.55 | 65.42
2017-10-29 09:00 | 112.5 | 112.38
2017-10-29 09:30 | 129.36 | 129.14
2017-10-29 10:00 | 105.27 | 105.18
2017-10-29 10:30 | 108.61 | 108.48
2017-10-29 11:00 | 115.67 | 115.66
2017-10-29 11:30 | 97.06 | 96.96
2017-10-29 12:00 | 98.37 | 98.31
2017-10-29 12:30 | 103.22 | 103.19
2017-10-29 13:00 | 104.85 | 104.83
2017-10-29 13:30 | 112.46 | 112.46
2017-10-29 14:00 | 114.16 | 114.16
2017-10-29 14:30 | 114.61 | 114.61
2017-10-29 15:00 | 119.95 | 119.74
2017-10-29 15:30 | 124.96 | 124.07
2017-10-29 16:00 | 131 | 130.18
2017-10-29 16:30 | 133.19 | 132.39
2017-10-29 17:00 | 134.89 | 134.22
2017-10-29 17:30 | 132.24 | 131.68
2017-10-29 18:00 | 132.19 | 131.63
2017-10-29 18:30 | 136.12 | 135.37
2017-10-29 19:00 | 143.55 | 142.74
2017-10-29 19:30 | 140.02 | 139.77
2017-10-29 20:00 | 136.21 | 136.07
2017-10-29 20:30 | 127.52 | 127.46
2017-10-29 21:00 | 115.45 | 115.42
2017-10-29 21:30 | 111.16 | 110.23
2017-10-29 22:00 | 130.17 | 128.69
2017-10-29 22:30 | 138.67 | 137.68
2017-10-29 23:00 | 130.12 | 129.42
2017-10-29 23:30 | 94.82 | 94.19
2017-10-30 | 38.93 | 37.27
2017-10-30 00:30 | 44.62 | 44.27
2017-10-30 01:00 | 16.59 | 14.68
2017-10-30 01:30 | 12.68 | 9.86
2017-10-30 02:00 | 12.26 | 9.19
2017-10-30 02:30 | 13.59 | 10.9
2017-10-30 03:00 | 10.16 | 6.78
2017-10-30 03:30 | 9.61 | 5.58
2017-10-30 04:00 | 10.6 | 5.08
2017-10-30 04:30 | 9.06 | 1.69
2017-10-30 05:00 | 14.02 | 11.11
2017-10-30 05:30 | 17.7 | 15.82
2017-10-30 06:00 | 20.33 | -20.16
2017-10-30 06:30 | 75.7 | 75.69
2017-10-30 07:00 | 95.9 | 95.14
2017-10-30 07:30 | 123.28 | 114.78
2017-10-30 08:00 | 137.53 | 119.2
2017-10-30 08:30 | 141.01 | 122.15
2017-10-30 09:00 | 141.37 | 126.54
2017-10-30 09:30 | 140.34 | 124.47
2017-10-30 10:00 | 140.79 | 124.86
2017-10-30 10:30 | 145.74 | 129.66
2017-10-30 11:00 | 150.97 | 134.49
2017-10-30 11:30 | 152.48 | 135.45
2017-10-30 12:00 | 152.47 | 135.21
2017-10-30 12:30 | 147.15 | 130.47
2017-10-30 13:00 | 151.52 | 135.65
2017-10-30 13:30 | 161.85 | 147.22
2017-10-30 14:00 | 165.43 | 150.33
2017-10-30 14:30 | 182.44 | 170.32
2017-10-30 15:00 | 176.43 | 165.69
2017-10-30 15:30 | 163.47 | 153.47
2017-10-30 16:00 | 154.76 | 144.78
2017-10-30 16:30 | 151.14 | 140.93
2017-10-30 17:00 | 148.6 | 138.88
2017-10-30 17:30 | 144.62 | 137.16
2017-10-30 18:00 | 135.95 | 133.82
2017-10-30 18:30 | 139.82 | 137.37
2017-10-30 19:00 | 154.03 | 151.03
2017-10-30 19:30 | 153.49 | 150.93
2017-10-30 20:00 | 154.58 | 149.05
2017-10-30 20:30 | 143.77 | 140.7
2017-10-30 21:00 | 123.65 | 121.29
2017-10-30 21:30 | 100.57 | 98.73
2017-10-30 22:00 | 77.01 | 75.53
2017-10-30 22:30 | 81.69 | 80.7
2017-10-30 23:00 | 91.33 | 90.74
2017-10-30 23:30 | 76.77 | 76.16
2017-10-31 | 46.77 | 45.51
2017-10-31 00:30 | 24.38 | 24.34
2017-10-31 01:00 | 7.41 | 0.7
2017-10-31 01:30 | 7.21 | -1.13
2017-10-31 02:00 | 8.09 | 2.47
2017-10-31 02:30 | 7.52 | -0.16
2017-10-31 03:00 | 12.9 | -10.91
2017-10-31 03:30 | 15.68 | -14.14
2017-10-31 04:00 | 20.92 | -19.3
2017-10-31 04:30 | 18.35 | -16.58
2017-10-31 05:00 | 15.33 | 12.82
2017-10-31 05:30 | 16.8 | 14.8
2017-10-31 06:00 | 37.07 | 36.41
2017-10-31 06:30 | 81.92 | 81.89
2017-10-31 07:00 | 97.15 | 97.12
2017-10-31 07:30 | 111.27 | 110.76
2017-10-31 08:00 | 93.45 | 92.61
2017-10-31 08:30 | 82.86 | 81.29
2017-10-31 09:00 | 83.81 | 81.39
2017-10-31 09:30 | 88.7 | 86.19
2017-10-31 10:00 | 90.16 | 87.56
2017-10-31 10:30 | 88.6 | 85.72
2017-10-31 11:00 | 86.23 | 83.67
2017-10-31 11:30 | 83.3 | 80.77
2017-10-31 12:00 | 82.89 | 80.45
2017-10-31 12:30 | 84.91 | 82.85
2017-10-31 13:00 | 85.42 | 83.45
2017-10-31 13:30 | 82.15 | 80.1
2017-10-31 14:00 | 89.05 | 87.06
2017-10-31 14:30 | 94.59 | 92.01
2017-10-31 15:00 | 110.82 | 95.27
2017-10-31 15:30 | 101.32 | 85.44
2017-10-31 16:00 | 128.28 | 116.99
2017-10-31 16:30 | 132.04 | 121.61
2017-10-31 17:00 | 132.46 | 126.54
2017-10-31 17:30 | 100.41 | 96.26
2017-10-31 18:00 | 87.67 | 85.82
2017-10-31 18:30 | 85.09 | 84.67
2017-10-31 19:00 | 96.82 | 96.33
2017-10-31 19:30 | 91.23 | 90.85
2017-10-31 20:00 | 81.32 | 81.11
2017-10-31 20:30 | 77.12 | 76.35
2017-10-31 21:00 | 71.55 | 71.12
2017-10-31 21:30 | 66.23 | 66.23
2017-10-31 22:00 | 44.57 | 44.52
2017-10-31 22:30 | 63.51 | 63.37
2017-10-31 23:00 | 85.28 | 84.98
2017-10-31 23:30 | 68.85 | 68.37
2017-11-01 | 39.75 | 39.15
2017-11-01 00:30 | 15.04 | 13.97
2017-11-01 01:00 | 9.21 | -2.03
2017-11-01 01:30 | 19.44 | -7.06
2017-11-01 02:00 | 20.79 | -11.22
2017-11-01 02:30 | 20.84 | -11.86
2017-11-01 03:00 | 20.64 | -11.55
2017-11-01 03:30 | 19.47 | -8.49
2017-11-01 04:00 | 25.43 | -18.61
2017-11-01 04:30 | 23.97 | -15.75
2017-11-01 05:00 | 18.69 | -1.61
2017-11-01 05:30 | 22.55 | 12.3
2017-11-01 06:00 | 37.41 | 30.93
2017-11-01 06:30 | 17.78 | -10.91
2017-11-01 07:00 | 7.38 | -7.16
2017-11-01 07:30 | 37.31 | 36.2
2017-11-01 08:00 | 42.35 | 20.68
2017-11-01 08:30 | 84.83 | 54.49
2017-11-01 09:00 | 98.44 | 72.09
2017-11-01 09:30 | 113.53 | 91.58
2017-11-01 10:00 | 112.03 | 90.12
2017-11-01 10:30 | 87.92 | 56
2017-11-01 11:00 | 93.68 | 64.33
2017-11-01 11:30 | 91.61 | 60.68
2017-11-01 12:00 | 103.44 | 77.61
2017-11-01 12:30 | 110.2 | 86.48
2017-11-01 13:00 | 118.45 | 96.62
2017-11-01 13:30 | 126.07 | 105.84
2017-11-01 14:00 | 131.34 | 111.86
2017-11-01 14:30 | 137.83 | 119.86
2017-11-01 15:00 | 132.12 | 113.73
2017-11-01 15:30 | 131.24 | 113.46
2017-11-01 16:00 | 141.57 | 125.47
2017-11-01 16:30 | 146.17 | 131.5
2017-11-01 17:00 | 112.19 | 93
2017-11-01 17:30 | 108.54 | 90.18
2017-11-01 18:00 | 105.91 | 88.17
2017-11-01 18:30 | 109.39 | 92.14
2017-11-01 19:00 | 115.26 | 98.35
2017-11-01 19:30 | 112.75 | 97.95
2017-11-01 20:00 | 121.13 | 114.69
2017-11-01 20:30 | 105.44 | 98.69
2017-11-01 21:00 | 92.54 | 84.85
2017-11-01 21:30 | 68.88 | 68.86
2017-11-01 22:00 | 56.84 | 56.76
2017-11-01 22:30 | 89.61 | 89.48
2017-11-01 23:00 | 114.74 | 114.57
2017-11-01 23:30 | 86.14 | 85.82
2017-11-02 | 49.11 | 48.51
2017-11-02 00:30 | 20.13 | 19.21
2017-11-02 01:00 | 19.5 | -19.08
2017-11-02 01:30 | 24.63 | -24.37
2017-11-02 02:00 | 25.5 | -25.3
2017-11-02 02:30 | 26.12 | -25.95
2017-11-02 03:00 | 26.65 | -26.53
2017-11-02 03:30 | 27.74 | -27.6
2017-11-02 04:00 | 21.85 | -21.34
2017-11-02 04:30 | 21.57 | -19.53
2017-11-02 05:00 | 16.52 | -2.42
2017-11-02 05:30 | 17.56 | 5.49
2017-11-02 06:00 | 27.64 | 19.02
2017-11-02 06:30 | 25.32 | 16.55
2017-11-02 07:00 | 17.48 | 9.26
2017-11-02 07:30 | 26.91 | 12.41
2017-11-02 08:00 | 26.53 | 1.04
2017-11-02 08:30 | 31.08 | -1.32
2017-11-02 09:00 | 48.8 | -4.9
2017-11-02 09:30 | 55.02 | -10.06
2017-11-02 10:00 | 50.73 | -8.99
2017-11-02 10:30 | 49.38 | -8.32
2017-11-02 11:00 | 48.12 | -6.37
2017-11-02 11:30 | 48.72 | -8.52
2017-11-02 12:00 | 47.96 | -4.27
2017-11-02 12:30 | 48.52 | -7.4
2017-11-02 13:00 | 48.45 | -2.79
2017-11-02 13:30 | 48.73 | -2.15
2017-11-02 14:00 | 48.82 | 1.91
2017-11-02 14:30 | 51.9 | 17.35
2017-11-02 15:00 | 50.77 | 15.82
2017-11-02 15:30 | 56.75 | 33.57
2017-11-02 16:00 | 56.94 | 35.54
2017-11-02 16:30 | 63.04 | 47.48
2017-11-02 17:00 | 78.43 | 67.27
2017-11-02 17:30 | 84.31 | 75.11
2017-11-02 18:00 | 85.2 | 76.55
2017-11-02 18:30 | 96.61 | 88.49
2017-11-02 19:00 | 107.9 | 102.97
2017-11-02 19:30 | 101.79 | 101.01
2017-11-02 20:00 | 87.63 | 87.45
2017-11-02 20:30 | 83.07 | 82.92
2017-11-02 21:00 | 69.47 | 67.91
2017-11-02 21:30 | 46.83 | 41.73
2017-11-02 22:00 | 11.72 | 9.91
2017-11-02 22:30 | 19.89 | 19.43
2017-11-02 23:00 | 43.52 | 42.95
2017-11-02 23:30 | 31.85 | 30.6
2017-11-03 | 9.5 | -5.82
2017-11-03 00:30 | 24.8 | -23.92
2017-11-03 01:00 | 30.98 | -30.45
2017-11-03 01:30 | 33.32 | -32.99
2017-11-03 02:00 | 33.22 | -32.85
2017-11-03 02:30 | 33.4 | -32.95
2017-11-03 03:00 | 35.32 | -35.04
2017-11-03 03:30 | 35.62 | -35.3
2017-11-03 04:00 | 35.77 | -35.41
2017-11-03 04:30 | 34.14 | -33.62
2017-11-03 05:00 | 22.7 | -19.59
2017-11-03 05:30 | 33.19 | 23.05
2017-11-03 06:00 | 39.94 | 31.41
2017-11-03 06:30 | 54.39 | 49.2
2017-11-03 07:00 | 39.74 | 35.83
2017-11-03 07:30 | 11.84 | 10.93
2017-11-03 08:00 | 16.8 | 14.7
2017-11-03 08:30 | 35.4 | 21.79
2017-11-03 09:00 | 67.1 | 21.36
2017-11-03 09:30 | 71.57 | 20.23
2017-11-03 10:00 | 78.66 | 36.02
2017-11-03 10:30 | 76.77 | 21.04
2017-11-03 11:00 | 77.58 | 19.83
2017-11-03 11:30 | 81.04 | 31.9
2017-11-03 12:00 | 90.69 | 54.14
2017-11-03 12:30 | 83.53 | 43.29
2017-11-03 13:00 | 83.83 | 45.01
2017-11-03 13:30 | 85.67 | 49.26
2017-11-03 14:00 | 84.9 | 47.28
2017-11-03 14:30 | 87.02 | 51.83
2017-11-03 15:00 | 89.89 | 57.68
2017-11-03 15:30 | 84.96 | 52.59
2017-11-03 16:00 | 84.43 | 53.47
2017-11-03 16:30 | 101.02 | 78
2017-11-03 17:00 | 112.7 | 93.25
2017-11-03 17:30 | 107.12 | 88.93
2017-11-03 18:00 | 96.26 | 81.55
2017-11-03 18:30 | 88.91 | 79.86
2017-11-03 19:00 | 100.73 | 92.27
2017-11-03 19:30 | 93.58 | 85.04
2017-11-03 20:00 | 82.54 | 73.71
2017-11-03 20:30 | 70.02 | 59.27
2017-11-03 21:00 | 47.81 | 30.82
2017-11-03 21:30 | 36.91 | 14.5
2017-11-03 22:00 | 32.54 | 5.88
2017-11-03 22:30 | 36.24 | 33.79
2017-11-03 23:00 | 69.79 | 65.58
2017-11-03 23:30 | 66.97 | 62.14
2017-11-04 | 32.44 | 20.12
2017-11-04 00:30 | 27 | -11.16
2017-11-04 01:00 | 33.52 | -23.38
2017-11-04 01:30 | 34.21 | -25.22
2017-11-04 02:00 | 34.4 | -25.23
2017-11-04 02:30 | 34.79 | -26.14
2017-11-04 03:00 | 35.33 | -27.5
2017-11-04 03:30 | 37.85 | -31.04
2017-11-04 04:00 | 38.34 | -32.04
2017-11-04 04:30 | 39.01 | -32.46
2017-11-04 05:00 | 37.04 | -30.68
2017-11-04 05:30 | 36.1 | -29.93
2017-11-04 06:00 | 34.74 | -26.93
2017-11-04 06:30 | 35.88 | -27.94
2017-11-04 07:00 | 35.15 | -27.55
2017-11-04 07:30 | 29.23 | -22.14
2017-11-04 08:00 | 24.47 | -21.59
2017-11-04 08:30 | 17.95 | -16.87
2017-11-04 09:00 | 10.44 | -10.17
2017-11-04 09:30 | 32.23 | 31.58
2017-11-04 10:00 | 29.85 | 29.38
2017-11-04 10:30 | 25 | 23.18
2017-11-04 11:00 | 64.63 | 63.41
2017-11-04 11:30 | 40.03 | 37.5
2017-11-04 12:00 | 74.96 | 72.8
2017-11-04 12:30 | 70.46 | 68.92
2017-11-04 13:00 | 24.17 | 19.27
2017-11-04 13:30 | 45.46 | 43.37
2017-11-04 14:00 | 50.8 | 49.29
2017-11-04 14:30 | 84.85 | 83.98
2017-11-04 15:00 | 66.76 | 65.79
2017-11-04 15:30 | 86.75 | 86.05
2017-11-04 16:00 | 99.86 | 99.27
2017-11-04 16:30 | 116 | 115.52
2017-11-04 17:00 | 92.34 | 91.79
2017-11-04 17:30 | 90.43 | 90.02
2017-11-04 18:00 | 84.81 | 84.43
2017-11-04 18:30 | 86.86 | 86.41
2017-11-04 19:00 | 92.73 | 92.19
2017-11-04 19:30 | 94.62 | 94.23
2017-11-04 20:00 | 108.29 | 108.08
2017-11-04 20:30 | 102.04 | 101.61
2017-11-04 21:00 | 79.82 | 77.41
2017-11-04 21:30 | 72.51 | 69.55
2017-11-04 22:00 | 50.92 | 45.58
2017-11-04 22:30 | 63.5 | 59.9
2017-11-04 23:00 | 80.62 | 77.37
2017-11-04 23:30 | 57.94 | 52.58
2017-11-05 | 30.35 | 16.81
2017-11-05 00:30 | 25.08 | -2.02
2017-11-05 01:00 | 28.49 | -15.4
2017-11-05 01:30 | 35.01 | -26.12
2017-11-05 02:00 | 34.53 | -26.27
2017-11-05 02:30 | 34.23 | -26.99
2017-11-05 03:00 | 37.31 | -31.38
2017-11-05 03:30 | 38.9 | -33.68
2017-11-05 04:00 | 40.94 | -36.72
2017-11-05 04:30 | 40.04 | -35.5
2017-11-05 05:00 | 39.63 | -35.62
2017-11-05 05:30 | 45.06 | -44.26
2017-11-05 06:00 | 47.05 | -46.56
2017-11-05 06:30 | 40.28 | -38.44
2017-11-05 07:00 | 43.38 | -41.62
2017-11-05 07:30 | 47.6 | -47.33
2017-11-05 08:00 | 46.47 | -46.41
2017-11-05 08:30 | 33.35 | -33.2
2017-11-05 09:00 | 6.42 | 5.17
2017-11-05 09:30 | 36.16 | 35.78
2017-11-05 10:00 | 23.39 | 22.26
2017-11-05 10:30 | 29.03 | 27.97
2017-11-05 11:00 | 67.38 | 66.93
2017-11-05 11:30 | 27.18 | -11.03
2017-11-05 12:00 | 28.85 | -12.07
2017-11-05 12:30 | 30.94 | -15.66
2017-11-05 13:00 | 28.73 | -8.74
2017-11-05 13:30 | 27.45 | -0.38
2017-11-05 14:00 | 37.33 | 5.5
2017-11-05 14:30 | 67.23 | 29.25
2017-11-05 15:00 | 75.94 | 47.05
2017-11-05 15:30 | 87.4 | 63.92
2017-11-05 16:00 | 116.89 | 101.32
2017-11-05 16:30 | 99.93 | 81.97
2017-11-05 17:00 | 98.51 | 82.29
2017-11-05 17:30 | 97.71 | 83.69
2017-11-05 18:00 | 94.19 | 79.56
2017-11-05 18:30 | 95.78 | 80.78
2017-11-05 19:00 | 106.5 | 92.88
2017-11-05 19:30 | 102.53 | 91.88
2017-11-05 20:00 | 92 | 90.43
2017-11-05 20:30 | 87.64 | 87.5
2017-11-05 21:00 | 79.67 | 79.41
2017-11-05 21:30 | 77.97 | 77.41
2017-11-05 22:00 | 77.37 | 76.44
2017-11-05 22:30 | 67.7 | 66.28
2017-11-05 23:00 | 66.59 | 65.56
2017-11-05 23:30 | 60.8 | 59.79
2017-11-06 | 45.91 | 44.46
2017-11-06 00:30 | 31.31 | 29.61
2017-11-06 01:00 | 24.44 | 10.46
2017-11-06 01:30 | 27.93 | 6.85
2017-11-06 02:00 | 28.91 | 10.32
2017-11-06 02:30 | 29.3 | 11.11
2017-11-06 03:00 | 26.33 | -0.54
2017-11-06 03:30 | 29.25 | -13.4
2017-11-06 04:00 | 33.77 | -23.13
2017-11-06 04:30 | 35.08 | -24.71
2017-11-06 05:00 | 26.88 | 9.04
2017-11-06 05:30 | 29.2 | 14.35
2017-11-06 06:00 | 45.13 | 36.43
2017-11-06 06:30 | 46.73 | 40.36
2017-11-06 07:00 | 43.08 | 38.61
2017-11-06 07:30 | 59.04 | 56.22
2017-11-06 08:00 | 53.01 | 50.97
2017-11-06 08:30 | 63.83 | 63.61
2017-11-06 09:00 | 69.53 | 69.53
2017-11-06 09:30 | 75.94 | 75.94
2017-11-06 10:00 | 66.57 | 66.49
2017-11-06 10:30 | 58.76 | 58.62
2017-11-06 11:00 | 25.06 | 24.94
2017-11-06 11:30 | 23.27 | 23.14
2017-11-06 12:00 | 56.72 | 56.48
2017-11-06 12:30 | 79.81 | 79.61
2017-11-06 13:00 | 84.56 | 84.43
2017-11-06 13:30 | 92.84 | 92.61
2017-11-06 14:00 | 95.32 | 95.17
2017-11-06 14:30 | 96.51 | 96.34
2017-11-06 15:00 | 90.17 | 89.97
2017-11-06 15:30 | 84.82 | 84.51
2017-11-06 16:00 | 84.71 | 84.5
2017-11-06 16:30 | 95.39 | 95.1
2017-11-06 17:00 | 97.4 | 97.08
2017-11-06 17:30 | 96.08 | 95.78
2017-11-06 18:00 | 94.4 | 94.21
2017-11-06 18:30 | 98.05 | 98
2017-11-06 19:00 | 104.47 | 104.41
2017-11-06 19:30 | 102.83 | 102.72
2017-11-06 20:00 | 99.12 | 98.82
2017-11-06 20:30 | 97.12 | 96.51
2017-11-06 21:00 | 84.32 | 82.77
2017-11-06 21:30 | 80.07 | 77.93
2017-11-06 22:00 | 90.07 | 87.41
2017-11-06 22:30 | 89.99 | 88.34
2017-11-06 23:00 | 89.72 | 89.21
2017-11-06 23:30 | 59.37 | 58.46
2017-11-07 | 21.26 | 18.95
2017-11-07 00:30 | 8.67 | 1.35
2017-11-07 01:00 | 16.18 | -13.93
2017-11-07 01:30 | 17.76 | -15.73
2017-11-07 02:00 | 23.33 | -11.17
2017-11-07 02:30 | 25.97 | -11.3
2017-11-07 03:00 | 29.66 | -18.8
2017-11-07 03:30 | 30.06 | -19.42
2017-11-07 04:00 | 29.88 | -18.83
2017-11-07 04:30 | 28.01 | -13.93
2017-11-07 05:00 | 26.39 | -10.17
2017-11-07 05:30 | 25.06 | -8.18
2017-11-07 06:00 | 25.75 | 3.07
2017-11-07 06:30 | 26.16 | 13.02
2017-11-07 07:00 | 39.95 | 35.68
2017-11-07 07:30 | 38.99 | 38.25
2017-11-07 08:00 | 34.41 | 34.27
2017-11-07 08:30 | 45.93 | 45.9
2017-11-07 09:00 | 56.34 | 56.27
2017-11-07 09:30 | 59.43 | 59.32
2017-11-07 10:00 | 57.37 | 56.32
2017-11-07 10:30 | 71.32 | 57.69
2017-11-07 11:00 | 76.57 | 68.5
2017-11-07 11:30 | 96.71 | 91.96
2017-11-07 12:00 | 115.06 | 113.77
2017-11-07 12:30 | 129.52 | 129.51
2017-11-07 13:00 | 114.26 | 114.25
2017-11-07 13:30 | 104.13 | 104.12
2017-11-07 14:00 | 128.8 | 128.8
2017-11-07 14:30 | 136.5 | 136.5
2017-11-07 15:00 | 123.44 | 123.44
2017-11-07 15:30 | 84.93 | 84.93
2017-11-07 16:00 | 67.55 | 67.5
2017-11-07 16:30 | 63.53 | 63.44
2017-11-07 17:00 | 68.66 | 68.5
2017-11-07 17:30 | 77.02 | 77.02
2017-11-07 18:00 | 81.62 | 81.51
2017-11-07 18:30 | 88.64 | 88.44
2017-11-07 19:00 | 92.45 | 92.3
2017-11-07 19:30 | 72.54 | 72.19
2017-11-07 20:00 | 54.42 | 54.15
2017-11-07 20:30 | 58.3 | 57.82
2017-11-07 21:00 | 46.91 | 44.29
2017-11-07 21:30 | 29.21 | 23.88
2017-11-07 22:00 | 17.89 | 2.56
2017-11-07 22:30 | 30.59 | 24.49
2017-11-07 23:00 | 36.76 | 31.79
2017-11-07 23:30 | 16.8 | 4.08
2017-11-08 | 20.97 | -16.44
2017-11-08 00:30 | 27.03 | -25.29
2017-11-08 01:00 | 33.47 | -32.93
2017-11-08 01:30 | 34.51 | -34.28
2017-11-08 02:00 | 35.79 | -35.49
2017-11-08 02:30 | 36.6 | -36.08
2017-11-08 03:00 | 35.76 | -35.32
2017-11-08 03:30 | 35.75 | -35.45
2017-11-08 04:00 | 33.69 | -33.36
2017-11-08 04:30 | 31.45 | -30.61
2017-11-08 05:00 | 27.77 | -26.61
2017-11-08 05:30 | 22.83 | -20.85
2017-11-08 06:00 | 18.4 | -13.7
2017-11-08 06:30 | 14.23 | -0.22
2017-11-08 07:00 | 19.66 | 14.48
2017-11-08 07:30 | 28.83 | 28.79
2017-11-08 08:00 | 32.13 | 31.43
2017-11-08 08:30 | 21.43 | 18.69
2017-11-08 09:00 | 28.07 | 13.45
2017-11-08 09:30 | 31.57 | -2.08
2017-11-08 10:00 | 32.28 | -3.8
2017-11-08 10:30 | 34.95 | 13.63
2017-11-08 11:00 | 57.6 | 33.54
2017-11-08 11:30 | 42.38 | 24.42
2017-11-08 12:00 | 36.02 | 11.77
2017-11-08 12:30 | 34.74 | 1.86
2017-11-08 13:00 | 37.25 | 15.37
2017-11-08 13:30 | 45.39 | 30.62
2017-11-08 14:00 | 53.62 | 42.43
2017-11-08 14:30 | 51.17 | 40.35
2017-11-08 15:00 | 45.04 | 35.3
2017-11-08 15:30 | 40.05 | 39.11
2017-11-08 16:00 | 51.22 | 50.87
2017-11-08 16:30 | 63.24 | 63.11
2017-11-08 17:00 | 68.01 | 67.96
2017-11-08 17:30 | 81.21 | 81.21
2017-11-08 18:00 | 82.12 | 82.11
2017-11-08 18:30 | 89.55 | 85.89
2017-11-08 19:00 | 100.06 | 93.03
2017-11-08 19:30 | 98.52 | 92.13
2017-11-08 20:00 | 93.41 | 87.34
2017-11-08 20:30 | 91.36 | 86
2017-11-08 21:00 | 62.4 | 61.53
2017-11-08 21:30 | 47.37 | 46.83
2017-11-08 22:00 | 37.37 | 36.16
2017-11-08 22:30 | 43.79 | 42.29
2017-11-08 23:00 | 53.07 | 51.67
2017-11-08 23:30 | 38.22 | 35.86
2017-11-09 | 14.88 | 8.8
2017-11-09 00:30 | 13.14 | -8.37
2017-11-09 01:00 | 22.31 | -20.46
2017-11-09 01:30 | 24.57 | -23.1
2017-11-09 02:00 | 23.99 | -22.55
2017-11-09 02:30 | 24.42 | -23.14
2017-11-09 03:00 | 24.89 | -23.71
2017-11-09 03:30 | 25.27 | -24.05
2017-11-09 04:00 | 25.89 | -24.36
2017-11-09 04:30 | 28.05 | -26.44
2017-11-09 05:00 | 23.26 | -21.92
2017-11-09 05:30 | 18.21 | -16.68
2017-11-09 06:00 | 15.47 | -13.13
2017-11-09 06:30 | 8.61 | -1.29
2017-11-09 07:00 | 8.65 | 4.8
2017-11-09 07:30 | 9.91 | 9.17
2017-11-09 08:00 | 9 | 9
2017-11-09 08:30 | 18.32 | 8.29
2017-11-09 09:00 | 20.83 | 2.8
2017-11-09 09:30 | 22.3 | 3.79
2017-11-09 10:00 | 35.47 | 12.77
2017-11-09 10:30 | 42.97 | 17.31
2017-11-09 11:00 | 42.94 | 8.64
2017-11-09 11:30 | 42.98 | 7.86
2017-11-09 12:00 | 43.82 | -12.09
2017-11-09 12:30 | 48.29 | -23.49
2017-11-09 13:00 | 49.06 | 26.52
2017-11-09 13:30 | 43.02 | 6.67
2017-11-09 14:00 | 45.36 | -12.54
2017-11-09 14:30 | 43.98 | -5.25
2017-11-09 15:00 | 44.96 | -13.67
2017-11-09 15:30 | 41.32 | -6.17
2017-11-09 16:00 | 39.45 | 2.95
2017-11-09 16:30 | 40.68 | 11.13
2017-11-09 17:00 | 40.94 | 13.21
2017-11-09 17:30 | 44.65 | 23.74
2017-11-09 18:00 | 51.5 | 35.61
2017-11-09 18:30 | 62.93 | 50.49
2017-11-09 19:00 | 79.45 | 69.74
2017-11-09 19:30 | 72.04 | 62.17
2017-11-09 20:00 | 67.81 | 57.9
2017-11-09 20:30 | 78.23 | 74.26
2017-11-09 21:00 | 73.81 | 72.73
2017-11-09 21:30 | 58.94 | 58.1
2017-11-09 22:00 | 36.39 | 35.65
2017-11-09 22:30 | 32.15 | 31.24
2017-11-09 23:00 | 58.19 | 57.94
2017-11-09 23:30 | 55.23 | 55.08
2017-11-10 | 18.26 | 17.28
2017-11-10 00:30 | 8.79 | 6.43
2017-11-10 01:00 | 10.04 | -3.83
2017-11-10 01:30 | 19.46 | -17.51
2017-11-10 02:00 | 20.23 | -17.92
2017-11-10 02:30 | 22.21 | -20.33
2017-11-10 03:00 | 22.42 | -20.6
2017-11-10 03:30 | 23.45 | -21.82
2017-11-10 04:00 | 22.86 | -20.61
2017-11-10 04:30 | 23.52 | -21.14
2017-11-10 05:00 | 20.5 | -18.41
2017-11-10 05:30 | 15.49 | -12.72
2017-11-10 06:00 | 11.22 | -5.54
2017-11-10 06:30 | 13.39 | 9.41
2017-11-10 07:00 | 24.11 | 23.3
2017-11-10 07:30 | 36.94 | 34.68
2017-11-10 08:00 | 62.61 | 36.23
2017-11-10 08:30 | 69.62 | 40.99
2017-11-10 09:00 | 77.43 | 51.89
2017-11-10 09:30 | 78.36 | 53.3
2017-11-10 10:00 | 69.55 | 46.67
2017-11-10 10:30 | 65.03 | 39.9
2017-11-10 11:00 | 63.23 | 35.76
2017-11-10 11:30 | 59.58 | 31.05
2017-11-10 12:00 | 59.87 | 33.14
2017-11-10 12:30 | 53.89 | 22.1
2017-11-10 13:00 | 49.91 | 3.91
2017-11-10 13:30 | 50.89 | 8.55
2017-11-10 14:00 | 51.68 | 11.75
2017-11-10 14:30 | 52.79 | 18.71
2017-11-10 15:00 | 52.75 | 21.19
2017-11-10 15:30 | 49.82 | 17.59
2017-11-10 16:00 | 54.09 | 29.89
2017-11-10 16:30 | 73 | 58.84
2017-11-10 17:00 | 79.79 | 74.85
2017-11-10 17:30 | 93 | 91.19
2017-11-10 18:00 | 91.56 | 90.11
2017-11-10 18:30 | 92.66 | 91.1
2017-11-10 19:00 | 97.7 | 95.91
2017-11-10 19:30 | 90.91 | 89.26
2017-11-10 20:00 | 87.32 | 87.11
2017-11-10 20:30 | 91.34 | 90.14
2017-11-10 21:00 | 73.35 | 71.55
2017-11-10 21:30 | 65.45 | 63.02
2017-11-10 22:00 | 47.94 | 45.64
2017-11-10 22:30 | 45.01 | 43.06
2017-11-10 23:00 | 64.37 | 62.76
2017-11-10 23:30 | 35.58 | 32.14
2017-11-11 | 14.25 | -1.84
2017-11-11 00:30 | 21.8 | -17.34
2017-11-11 01:00 | 40.13 | -38.29
2017-11-11 01:30 | 46.45 | -44.94
2017-11-11 02:00 | 49.65 | -48.3
2017-11-11 02:30 | 58.18 | -57.25
2017-11-11 03:00 | 57.77 | -56.82
2017-11-11 03:30 | 60.51 | -59.67
2017-11-11 04:00 | 66.15 | -65.48
2017-11-11 04:30 | 66.98 | -66.34
2017-11-11 05:00 | 59.53 | -58.67
2017-11-11 05:30 | 55.26 | -54.18
2017-11-11 06:00 | 50.44 | -49.39
2017-11-11 06:30 | 36.46 | -34.77
2017-11-11 07:00 | 26.42 | -23.39
2017-11-11 07:30 | 13.82 | -6
2017-11-11 08:00 | 10.65 | -4.26
2017-11-11 08:30 | 7.09 | 0.27
2017-11-11 09:00 | 20.86 | 19.94
2017-11-11 09:30 | 17.89 | 17.16
2017-11-11 10:00 | 19.5 | 11.53
2017-11-11 10:30 | 17.6 | 7.06
2017-11-11 11:00 | 18.12 | 7.71
2017-11-11 11:30 | 20.52 | -11.61
2017-11-11 12:00 | 25.75 | -19.83
2017-11-11 12:30 | 16.56 | -5.98
2017-11-11 13:00 | 16.04 | 3.63
2017-11-11 13:30 | 16.27 | -4.77
2017-11-11 14:00 | 16.12 | -5.81
2017-11-11 14:30 | 14.78 | 2.37
2017-11-11 15:00 | 19.02 | 12.61
2017-11-11 15:30 | 27.45 | 24.33
2017-11-11 16:00 | 37.84 | 35.84
2017-11-11 16:30 | 57.95 | 56.96
2017-11-11 17:00 | 78.73 | 78.05
2017-11-11 17:30 | 78.8 | 78.12
2017-11-11 18:00 | 83.86 | 83.17
2017-11-11 18:30 | 89.57 | 88.62
2017-11-11 19:00 | 108.2 | 106.99
2017-11-11 19:30 | 96.14 | 94.81
2017-11-11 20:00 | 93.46 | 92.35
2017-11-11 20:30 | 88.77 | 87.92
2017-11-11 21:00 | 79.26 | 78.63
2017-11-11 21:30 | 78.45 | 78.23
2017-11-11 22:00 | 61.03 | 60.89
2017-11-11 22:30 | 72.99 | 72.95
2017-11-11 23:00 | 89.3 | 89.3
2017-11-11 23:30 | 65.45 | 65.43
2017-11-12 | 21.28 | 21.28
2017-11-12 00:30 | 13.85 | -3.22
2017-11-12 01:00 | 33.36 | -28.83
2017-11-12 01:30 | 39.61 | -36.06
2017-11-12 02:00 | 41.86 | -38.68
2017-11-12 02:30 | 46.11 | -43.4
2017-11-12 03:00 | 49.91 | -47.37
2017-11-12 03:30 | 56.45 | -54.32
2017-11-12 04:00 | 68.64 | -67.89
2017-11-12 04:30 | 66.52 | -65.72
2017-11-12 05:00 | 65.05 | -64.35
2017-11-12 05:30 | 74.9 | -74.65
2017-11-12 06:00 | 66.63 | -66.09
2017-11-12 06:30 | 52.29 | -50.87
2017-11-12 07:00 | 85.99 | -85.95
2017-11-12 07:30 | 88.07 | -88.05
2017-11-12 08:00 | 89.71 | -89.7
2017-11-12 08:30 | 88.61 | -88.61
2017-11-12 09:00 | 71.66 | -71.65
2017-11-12 09:30 | 31.17 | -30.96
2017-11-12 10:00 | 36.2 | -36.17
2017-11-12 10:30 | 62.96 | -61.31
2017-11-12 11:00 | 85.31 | -83.04
2017-11-12 11:30 | 84.01 | -81.82
2017-11-12 12:00 | 84.96 | -82.79
2017-11-12 12:30 | 84.81 | -82.62
2017-11-12 13:00 | 85.84 | -83.7
2017-11-12 13:30 | 85.27 | -83.13
2017-11-12 14:00 | 83.56 | -81.4
2017-11-12 14:30 | 75.99 | -73.77
2017-11-12 15:00 | 49.94 | -47
2017-11-12 15:30 | 26.4 | -21.53
2017-11-12 16:00 | 17.19 | -8.79
2017-11-12 16:30 | 18.97 | 13.44
2017-11-12 17:00 | 42.84 | 41.05
2017-11-12 17:30 | 55.14 | 53.85
2017-11-12 18:00 | 68.11 | 67.1
2017-11-12 18:30 | 85.48 | 84.56
2017-11-12 19:00 | 118.17 | 111.23
2017-11-12 19:30 | 111.96 | 102.95
2017-11-12 20:00 | 100.38 | 96.75
2017-11-12 20:30 | 96.87 | 94.88
2017-11-12 21:00 | 79.58 | 79.47
2017-11-12 21:30 | 62.61 | 60.79
2017-11-12 22:00 | 43.56 | 40.62
2017-11-12 22:30 | 34.79 | 30.48
2017-11-12 23:00 | 37.98 | 33.54
2017-11-12 23:30 | 24.46 | 16.26
2017-11-13 | 26.08 | -20.4
2017-11-13 00:30 | 44.27 | -41.75
2017-11-13 01:00 | 36.07 | -32.82
2017-11-13 01:30 | 45.63 | -43.11
2017-11-13 02:00 | 59.07 | -57.46
2017-11-13 02:30 | 60.08 | -58.55
2017-11-13 03:00 | 62.85 | -61.54
2017-11-13 03:30 | 64.65 | -63.47
2017-11-13 04:00 | 72.98 | -72.3
2017-11-13 04:30 | 51.28 | -49.18
2017-11-13 05:00 | 46.32 | -44.1
2017-11-13 05:30 | 51.97 | -49.94
2017-11-13 06:00 | 39.1 | -36.26
2017-11-13 06:30 | 20.66 | -15.84
2017-11-13 07:00 | 8.89 | 0.36
2017-11-13 07:30 | 19.06 | 18.52
2017-11-13 08:00 | 22.89 | 22.89
2017-11-13 08:30 | 33.3 | 25.08
2017-11-13 09:00 | 35.39 | 26.06
2017-11-13 09:30 | 37.77 | 27.12
2017-11-13 10:00 | 31.57 | 15.43
2017-11-13 10:30 | 40 | 2.91
2017-11-13 11:00 | 79.68 | -11.81
2017-11-13 11:30 | 64.23 | -1.89
2017-11-13 12:00 | 69.06 | -27.13
2017-11-13 12:30 | 72.78 | -33.96
2017-11-13 13:00 | 76 | -39.81
2017-11-13 13:30 | 65.43 | -15.73
2017-11-13 14:00 | 64.19 | -8.41
2017-11-13 14:30 | 62.54 | -1.28
2017-11-13 15:00 | 67.03 | -23.25
2017-11-13 15:30 | 72.85 | -36.31
2017-11-13 16:00 | 69.61 | -29.8
2017-11-13 16:30 | 63.93 | -16.93
2017-11-13 17:00 | 59.12 | 5.75
2017-11-13 17:30 | 70.77 | 45.32
2017-11-13 18:00 | 62.98 | 52.47
2017-11-13 18:30 | 70.28 | 63.91
2017-11-13 19:00 | 95.94 | 90.14
2017-11-13 19:30 | 81.76 | 75.36
2017-11-13 20:00 | 68.97 | 62.17
2017-11-13 20:30 | 70.45 | 64.55
2017-11-13 21:00 | 64.42 | 63.51
2017-11-13 21:30 | 54.42 | 54.02
2017-11-13 22:00 | 34.98 | 33.68
2017-11-13 22:30 | 55.22 | 53.84
2017-11-13 23:00 | 62.76 | 61.12
2017-11-13 23:30 | 43.98 | 40.96
2017-11-14 | 27.07 | 20.04
2017-11-14 00:30 | 17.72 | -0.86
2017-11-14 01:00 | 21.57 | 10.52
2017-11-14 01:30 | 21.34 | 6.93
2017-11-14 02:00 | 20.23 | -3.63
2017-11-14 02:30 | 22.05 | -9.78
2017-11-14 03:00 | 20.32 | -4.43
2017-11-14 03:30 | 20.33 | -4.48
2017-11-14 04:00 | 20.96 | -3.02
2017-11-14 04:30 | 20.3 | -0.92
2017-11-14 05:00 | 21.37 | 5.77
2017-11-14 05:30 | 26.89 | 17.02
2017-11-14 06:00 | 32.07 | 25.84
2017-11-14 06:30 | 42.98 | 40.82
2017-11-14 07:00 | 46.11 | 44.83
2017-11-14 07:30 | 50.09 | 49.81
2017-11-14 08:00 | 45.64 | 45.63
2017-11-14 08:30 | 48.08 | 47.96
2017-11-14 09:00 | 57.95 | 57.66
2017-11-14 09:30 | 62.05 | 47.84
2017-11-14 10:00 | 72.81 | 40.51
2017-11-14 10:30 | 64.69 | 20.99
2017-11-14 11:00 | 66.1 | 20.54
2017-11-14 11:30 | 68.71 | 27.69
2017-11-14 12:00 | 65.08 | 16.06
2017-11-14 12:30 | 64.27 | 13.8
2017-11-14 13:00 | 64.37 | 17.03
2017-11-14 13:30 | 63.29 | 9.87
2017-11-14 14:00 | 65.52 | 18.93
2017-11-14 14:30 | 68.18 | 27.24
2017-11-14 15:00 | 66.04 | 21.93
2017-11-14 15:30 | 74.15 | 41.75
2017-11-14 16:00 | 73.01 | 43
2017-11-14 16:30 | 82.47 | 59.83
2017-11-14 17:00 | 102.82 | 87.11
2017-11-14 17:30 | 114.52 | 102.09
2017-11-14 18:00 | 116.73 | 105.45
2017-11-14 18:30 | 120.66 | 110.33
2017-11-14 19:00 | 134.04 | 124.26
2017-11-14 19:30 | 127.23 | 123.91
2017-11-14 20:00 | 127.75 | 124.72
2017-11-14 20:30 | 121.69 | 119.04
2017-11-14 21:00 | 98.7 | 98.28
2017-11-14 21:30 | 73 | 72.11
2017-11-14 22:00 | 44.13 | 42.2
2017-11-14 22:30 | 43.68 | 41.57
2017-11-14 23:00 | 59.72 | 58.04
2017-11-14 23:30 | 43.31 | 40.34
2017-11-15 | 17.75 | 3.24
2017-11-15 00:30 | 19.23 | 0.58
2017-11-15 01:00 | 25.15 | -16.43
2017-11-15 01:30 | 27.52 | -20.02
2017-11-15 02:00 | 30.51 | -24.08
2017-11-15 02:30 | 29.35 | -22.4
2017-11-15 03:00 | 30.01 | -23.26
2017-11-15 03:30 | 29.51 | -22.5
2017-11-15 04:00 | 25.09 | -15.87
2017-11-15 04:30 | 23.72 | -13.33
2017-11-15 05:00 | 22.58 | -10.15
2017-11-15 05:30 | 19.01 | -0.45
2017-11-15 06:00 | 18.45 | 7.15
2017-11-15 06:30 | 25.31 | 23.87
2017-11-15 07:00 | 37.26 | 35.56
2017-11-15 07:30 | 55.29 | 36.9
2017-11-15 08:00 | 60.54 | 26.8
2017-11-15 08:30 | 61.11 | 21.78
2017-11-15 09:00 | 60.45 | 6.9
2017-11-15 09:30 | 61.61 | 1.33
2017-11-15 10:00 | 62.5 | 0.64
2017-11-15 10:30 | 65.22 | 0.16
2017-11-15 11:00 | 67.41 | 14.47
2017-11-15 11:30 | 67.44 | 14.74
2017-11-15 12:00 | 69.28 | 21.71
2017-11-15 12:30 | 80.89 | 48.08
2017-11-15 13:00 | 88.12 | 59.37
2017-11-15 13:30 | 93.98 | 67.74
2017-11-15 14:00 | 92.62 | 66.35
2017-11-15 14:30 | 108.9 | 87.64
2017-11-15 15:00 | 117.03 | 99.29
2017-11-15 15:30 | 93.92 | 74.38
2017-11-15 16:00 | 98.79 | 81.37
2017-11-15 16:30 | 108.36 | 93.76
2017-11-15 17:00 | 117.77 | 105.13
2017-11-15 17:30 | 124.49 | 113.43
2017-11-15 18:00 | 123.38 | 112.76
2017-11-15 18:30 | 125.62 | 115.02
2017-11-15 19:00 | 133.27 | 122.82
2017-11-15 19:30 | 130.72 | 121.08
2017-11-15 20:00 | 129.14 | 120.13
2017-11-15 20:30 | 131.06 | 122.68
2017-11-15 21:00 | 93.75 | 93.73
2017-11-15 21:30 | 71.63 | 71.06
2017-11-15 22:00 | 61.26 | 60.05
2017-11-15 22:30 | 78.98 | 77.76
2017-11-15 23:00 | 99.37 | 98.17
2017-11-15 23:30 | 66.03 | 64.36
2017-11-16 | 21.86 | 16.35
2017-11-16 00:30 | 12.5 | 1.64
2017-11-16 01:00 | 14.4 | -9.09
2017-11-16 01:30 | 24.73 | -22.59
2017-11-16 02:00 | 22.68 | -20.17
2017-11-16 02:30 | 23.51 | -20.88
2017-11-16 03:00 | 31.34 | -29.79
2017-11-16 03:30 | 41.42 | -40.35
2017-11-16 04:00 | 45.01 | -44.13
2017-11-16 04:30 | 39.71 | -38.24
2017-11-16 05:00 | 34.41 | -32.7
2017-11-16 05:30 | 22.95 | -20.87
2017-11-16 06:00 | 16.88 | -12.74
2017-11-16 06:30 | 9.33 | 6.65
2017-11-16 07:00 | 20.76 | 17.99
2017-11-16 07:30 | 29.39 | 23.63
2017-11-16 08:00 | 27.89 | 25.58
2017-11-16 08:30 | 25.69 | 19.5
2017-11-16 09:00 | 23.69 | 12.69
2017-11-16 09:30 | 36.84 | -13.94
2017-11-16 10:00 | 54.8 | 2.57
2017-11-16 10:30 | 54.9 | 8.67
2017-11-16 11:00 | 57 | 10.33
2017-11-16 11:30 | 55.94 | 1.98
2017-11-16 12:00 | 56.49 | 0.25
2017-11-16 12:30 | 55.56 | -0.75
2017-11-16 13:00 | 55.54 | 7.42
2017-11-16 13:30 | 55.21 | 5.69
2017-11-16 14:00 | 55.82 | 10.92
2017-11-16 14:30 | 57.48 | 21.02
2017-11-16 15:00 | 52.79 | 12.28
2017-11-16 15:30 | 49.96 | 3.76
2017-11-16 16:00 | 64.55 | 45.93
2017-11-16 16:30 | 75.02 | 61.66
2017-11-16 17:00 | 96.89 | 87.96
2017-11-16 17:30 | 101.42 | 95.08
2017-11-16 18:00 | 106.57 | 105.33
2017-11-16 18:30 | 109.56 | 108.02
2017-11-16 19:00 | 127 | 125.12
2017-11-16 19:30 | 127.54 | 125.97
2017-11-16 20:00 | 126.6 | 125.42
2017-11-16 20:30 | 143.47 | 142.68
2017-11-16 21:00 | 125.82 | 124.95
2017-11-16 21:30 | 88.13 | 87.41
2017-11-16 22:00 | 61.71 | 61.24
2017-11-16 22:30 | 66.84 | 66.66
2017-11-16 23:00 | 91.39 | 91.28
2017-11-16 23:30 | 75.89 | 75.12
2017-11-17 | 22.37 | 19.93
2017-11-17 00:30 | 10.9 | -6.18
2017-11-17 01:00 | 28.76 | -27.64
2017-11-17 01:30 | 41.91 | -41.34
2017-11-17 02:00 | 38.11 | -37.32
2017-11-17 02:30 | 42.84 | -42.14
2017-11-17 03:00 | 43.92 | -43.31
2017-11-17 03:30 | 43.1 | -42.4
2017-11-17 04:00 | 41.83 | -41.01
2017-11-17 04:30 | 31.51 | -29.75
2017-11-17 05:00 | 19.1 | -16.2
2017-11-17 05:30 | 9.65 | -3.6
2017-11-17 06:00 | 12.59 | 8.3
2017-11-17 06:30 | 27.92 | 27.14
2017-11-17 07:00 | 28.76 | 28.73
2017-11-17 07:30 | 61.89 | 39.97
2017-11-17 08:00 | 86.99 | 61.23
2017-11-17 08:30 | 78.51 | 45.5
2017-11-17 09:00 | 78.97 | 41.68
2017-11-17 09:30 | 75.89 | 34.56
2017-11-17 10:00 | 77.75 | 35.92
2017-11-17 10:30 | 78.12 | 36.36
2017-11-17 11:00 | 74.98 | 24.64
2017-11-17 11:30 | 75.85 | 23.77
2017-11-17 12:00 | 75.75 | 20.68
2017-11-17 12:30 | 77.18 | 25.08
2017-11-17 13:00 | 79.72 | 32.77
2017-11-17 13:30 | 78.97 | 30.96
2017-11-17 14:00 | 76.79 | 26.38
2017-11-17 14:30 | 78.44 | 32.43
2017-11-17 15:00 | 80.7 | 40.99
2017-11-17 15:30 | 85.82 | 51.64
2017-11-17 16:00 | 105.95 | 82.42
2017-11-17 16:30 | 110.21 | 89.73
2017-11-17 17:00 | 117.47 | 99.55
2017-11-17 17:30 | 117.54 | 101.74
2017-11-17 18:00 | 109.42 | 93.79
2017-11-17 18:30 | 108.69 | 92.8
2017-11-17 19:00 | 130.38 | 116.47
2017-11-17 19:30 | 137.32 | 124.63
2017-11-17 20:00 | 126.93 | 113.54
2017-11-17 20:30 | 111.49 | 97.22
2017-11-17 21:00 | 95.07 | 79.12
2017-11-17 21:30 | 74.32 | 54.98
2017-11-17 22:00 | 63.98 | 42.93
2017-11-17 22:30 | 34.54 | 29.45
2017-11-17 23:00 | 48.02 | 46.63
2017-11-17 23:30 | 36.05 | 34.64
2017-11-18 | 12.74 | -6.31
2017-11-18 00:30 | 27.77 | -25.12
2017-11-18 01:00 | 37.1 | -34.9
2017-11-18 01:30 | 45.69 | -43.89
2017-11-18 02:00 | 51.53 | -49.84
2017-11-18 02:30 | 51.06 | -49.4
2017-11-18 03:00 | 54.45 | -52.78
2017-11-18 03:30 | 56.84 | -55.33
2017-11-18 04:00 | 59.26 | -57.76
2017-11-18 04:30 | 56.81 | -55.32
2017-11-18 05:00 | 51.1 | -49.37
2017-11-18 05:30 | 46.89 | -45.12
2017-11-18 06:00 | 45.02 | -43.12
2017-11-18 06:30 | 37.12 | -34.76
2017-11-18 07:00 | 33.33 | -30.68
2017-11-18 07:30 | 21.1 | -15.51
2017-11-18 08:00 | 16.89 | -2.27
2017-11-18 08:30 | 19.45 | 1.93
2017-11-18 09:00 | 27.63 | 16.48
2017-11-18 09:30 | 33.71 | 22.29
2017-11-18 10:00 | 38.89 | 28.01
2017-11-18 10:30 | 44.25 | 35.32
2017-11-18 11:00 | 55.39 | 48.58
2017-11-18 11:30 | 40.21 | 30.14
2017-11-18 12:00 | 34.15 | 22.26
2017-11-18 12:30 | 36.76 | 26.72
2017-11-18 13:00 | 36.7 | 27.34
2017-11-18 13:30 | 37.6 | 28.66
2017-11-18 14:00 | 34.43 | 24.81
2017-11-18 14:30 | 34.97 | 26.51
2017-11-18 15:00 | 29.61 | 19
2017-11-18 15:30 | 34.45 | 26.49
2017-11-18 16:00 | 44.73 | 38.98
2017-11-18 16:30 | 38.67 | 31.72
2017-11-18 17:00 | 44.76 | 39.29
2017-11-18 17:30 | 48.89 | 44.19
2017-11-18 18:00 | 71.06 | 67.85
2017-11-18 18:30 | 78.86 | 75.47
2017-11-18 19:00 | 79.93 | 76.06
2017-11-18 19:30 | 68.37 | 64.42
2017-11-18 20:00 | 60.06 | 55.95
2017-11-18 20:30 | 57.91 | 54.23
2017-11-18 21:00 | 37.93 | 33.1
2017-11-18 21:30 | 27.5 | 21.73
2017-11-18 22:00 | 16.33 | 5.53
2017-11-18 22:30 | 16.86 | 9.31
2017-11-18 23:00 | 36.76 | 34.87
2017-11-18 23:30 | 26.1 | 24.42
2017-11-19 | 18.49 | -14.67
2017-11-19 00:30 | 38.05 | -35.6
2017-11-19 01:00 | 54.35 | -52.05
2017-11-19 01:30 | 57.8 | -55.51
2017-11-19 02:00 | 59.36 | -57.18
2017-11-19 02:30 | 58.55 | -56.48
2017-11-19 03:00 | 60.38 | -58.32
2017-11-19 03:30 | 63.59 | -61.51
2017-11-19 04:00 | 63.05 | -60.99
2017-11-19 04:30 | 61.51 | -60.78
2017-11-19 05:00 | 63.43 | -63.2
2017-11-19 05:30 | 58.95 | -58.7
2017-11-19 06:00 | 64.51 | -64.45
2017-11-19 06:30 | 58.05 | -57.97
2017-11-19 07:00 | 46.78 | -46.59
2017-11-19 07:30 | 57.73 | -57.67
2017-11-19 08:00 | 47.47 | -47.35
2017-11-19 08:30 | 34.39 | -34.32
2017-11-19 09:00 | 17.1 | -17.03
2017-11-19 09:30 | 12.27 | -12.26
2017-11-19 10:00 | 21.23 | -16.74
2017-11-19 10:30 | 28.35 | -15.66
2017-11-19 11:00 | 27.78 | -13.77
2017-11-19 11:30 | 32.28 | -20.63
2017-11-19 12:00 | 32.44 | -21.12
2017-11-19 12:30 | 44.28 | -36.52
2017-11-19 13:00 | 30.91 | -19.88
2017-11-19 13:30 | 23.93 | -2.97
2017-11-19 14:00 | 23.92 | -0.13
2017-11-19 14:30 | 24.86 | -6.92
2017-11-19 15:00 | 33.18 | -23.36
2017-11-19 15:30 | 28.32 | -17.13
2017-11-19 16:00 | 22.63 | -3.45
2017-11-19 16:30 | 28.44 | 19.61
2017-11-19 17:00 | 39.65 | 34.21
2017-11-19 17:30 | 53.97 | 50.78
2017-11-19 18:00 | 70.55 | 68.19
2017-11-19 18:30 | 66.92 | 64.02
2017-11-19 19:00 | 90.24 | 82.21
2017-11-19 19:30 | 87.56 | 78.15
2017-11-19 20:00 | 80.74 | 71.24
2017-11-19 20:30 | 83.49 | 75.41
2017-11-19 21:00 | 70.12 | 62.07
2017-11-19 21:30 | 50.94 | 40.99
2017-11-19 22:00 | 37.93 | 24.5
2017-11-19 22:30 | 37.04 | 25.11
2017-11-19 23:00 | 56.5 | 49.93
2017-11-19 23:30 | 21.57 | 16.53
2017-11-20 | 25.95 | -24.07
2017-11-20 00:30 | 49.47 | -48.04
2017-11-20 01:00 | 61.68 | -60.09
2017-11-20 01:30 | 61.46 | -59.78
2017-11-20 02:00 | 61.13 | -59.8
2017-11-20 02:30 | 66.17 | -64.89
2017-11-20 03:00 | 63.8 | -62.58
2017-11-20 03:30 | 60.89 | -59.78
2017-11-20 04:00 | 59.58 | -58.49
2017-11-20 04:30 | 56.89 | -55.99
2017-11-20 05:00 | 53.56 | -52.61
2017-11-20 05:30 | 44.87 | -43.67
2017-11-20 06:00 | 28.7 | -27.08
2017-11-20 06:30 | 11.3 | -4.21
2017-11-20 07:00 | 9.13 | 8.92
2017-11-20 07:30 | 37.86 | 37.7
2017-11-20 08:00 | 44.7 | 44.65
2017-11-20 08:30 | 29.4 | 29.32
2017-11-20 09:00 | 31.51 | 31.06
2017-11-20 09:30 | 15.39 | 13.32
2017-11-20 10:00 | 9.62 | 5.1
2017-11-20 10:30 | 14.2 | 11.38
2017-11-20 11:00 | 3.37 | 3.37
2017-11-20 11:30 | 6.59 | -5.98
2017-11-20 12:00 | 5.02 | -4.89
2017-11-20 12:30 | 1.59 | -1.58
2017-11-20 13:00 | 3.01 | 2.86
2017-11-20 13:30 | 18.01 | 17.85
2017-11-20 14:00 | 23.17 | 23.03
2017-11-20 14:30 | 35.76 | 35.38
2017-11-20 15:00 | 36.73 | 36.31
2017-11-20 15:30 | 18.16 | 17.54
2017-11-20 16:00 | 41.27 | 40.63
2017-11-20 16:30 | 35.47 | 34.65
2017-11-20 17:00 | 40.13 | 39.62
2017-11-20 17:30 | 40.74 | 40.27
2017-11-20 18:00 | 38.23 | 37.81
2017-11-20 18:30 | 41.82 | 41.57
2017-11-20 19:00 | 48.13 | 48.13
2017-11-20 19:30 | 46.57 | 46.54
2017-11-20 20:00 | 45.75 | 45.53
2017-11-20 20:30 | 40.15 | 39.67
2017-11-20 21:00 | 26.22 | 25.14
2017-11-20 21:30 | 22.77 | 20.23
2017-11-20 22:00 | 17.35 | 10.66
2017-11-20 22:30 | 15.6 | 8.94
2017-11-20 23:00 | 26.88 | 20.74
2017-11-20 23:30 | 24.39 | 15.71
2017-11-21 | 24.47 | -18.95
2017-11-21 00:30 | 44.25 | -42.47
2017-11-21 01:00 | 54.98 | -54.03
2017-11-21 01:30 | 59.09 | -58.34
2017-11-21 02:00 | 61.13 | -60.63
2017-11-21 02:30 | 57.53 | -56.77
2017-11-21 03:00 | 58.99 | -58.46
2017-11-21 03:30 | 58.7 | -58.16
2017-11-21 04:00 | 56.62 | -56
2017-11-21 04:30 | 52.14 | -51.14
2017-11-21 05:00 | 48.72 | -47.83
2017-11-21 05:30 | 34.68 | -32.83
2017-11-21 06:00 | 28.48 | -25.21
2017-11-21 06:30 | 25.95 | -22.61
2017-11-21 07:00 | 15.44 | -13.63
2017-11-21 07:30 | 5.61 | 0.34
2017-11-21 08:00 | 11.56 | 9.53
2017-11-21 08:30 | 8.42 | 6.37
2017-11-21 09:00 | 3.64 | 1.81
2017-11-21 09:30 | 11.95 | 11.79
2017-11-21 10:00 | 11.37 | 11.23
2017-11-21 10:30 | 19.87 | 19.87
2017-11-21 11:00 | 12.91 | 12.73
2017-11-21 11:30 | 28.72 | 28.71
2017-11-21 12:00 | 19.46 | 19.46
2017-11-21 12:30 | 10.2 | 10.2
2017-11-21 13:00 | 23.83 | 23.83
2017-11-21 13:30 | 15.87 | 15.82
2017-11-21 14:00 | 16.02 | 15.98
2017-11-21 14:30 | 12.77 | 12.67
2017-11-21 15:00 | 14.28 | 13.99
2017-11-21 15:30 | 17.33 | 16.85
2017-11-21 16:00 | 8.33 | -8.2
2017-11-21 16:30 | 35.52 | -33.41
2017-11-21 17:00 | 33.01 | -26.11
2017-11-21 17:30 | 30.57 | -21.79
2017-11-21 18:00 | 32.47 | -18.3
2017-11-21 18:30 | 19.86 | -15.27
2017-11-21 19:00 | 31.69 | 30.27
2017-11-21 19:30 | 28.46 | 26.4
2017-11-21 20:00 | 15.08 | 8.16
2017-11-21 20:30 | 26.59 | 26.07
2017-11-21 21:00 | 37.77 | 36.99
2017-11-21 21:30 | 39.96 | 38.25
2017-11-21 22:00 | 23.15 | 18.98
2017-11-21 22:30 | 23.94 | 20.81
2017-11-21 23:00 | 49.61 | 48.63
2017-11-21 23:30 | 35.44 | 34.04
2017-11-22 | 15.37 | -13.64
2017-11-22 00:30 | 45.21 | -44.94
2017-11-22 01:00 | 62.13 | -62.06
2017-11-22 01:30 | 58.11 | -57.97
2017-11-22 02:00 | 57.76 | -57.61
2017-11-22 02:30 | 55.96 | -55.79
2017-11-22 03:00 | 57.35 | -57.2
2017-11-22 03:30 | 57.76 | -57.57
2017-11-22 04:00 | 46.49 | -46.09
2017-11-22 04:30 | 32.33 | 29.34
2017-11-22 05:00 | 44.63 | -43.59
2017-11-22 05:30 | 31 | -29.41
2017-11-22 06:00 | 21.8 | -19.79
2017-11-22 06:30 | 15.62 | -13.66
2017-11-22 07:00 | 15.1 | -15
2017-11-22 07:30 | 8.63 | 6.88
2017-11-22 08:00 | 10.56 | 0.31
2017-11-22 08:30 | 35.75 | -15.94
2017-11-22 09:00 | 46.29 | -27.69
2017-11-22 09:30 | 40.99 | -28.21
2017-11-22 10:00 | 19.58 | -7.88
2017-11-22 10:30 | 26.57 | -19.04
2017-11-22 11:00 | 34.21 | -27.78
2017-11-22 11:30 | 36.78 | -30.83
2017-11-22 12:00 | 31.09 | -23.57
2017-11-22 12:30 | 34.47 | -28.03
2017-11-22 13:00 | 37.78 | -32.38
2017-11-22 13:30 | 42.6 | -37.85
2017-11-22 14:00 | 40.14 | -34.99
2017-11-22 14:30 | 33.77 | -27.58
2017-11-22 15:00 | 32.6 | -27.19
2017-11-22 15:30 | 18.6 | -11.14
2017-11-22 16:00 | 13.99 | -6.45
2017-11-22 16:30 | 15.21 | 11.45
2017-11-22 17:00 | 15.29 | -11.65
2017-11-22 17:30 | 7.1 | 3.39
2017-11-22 18:00 | 11.78 | 11.15
2017-11-22 18:30 | 33.11 | 32.97
2017-11-22 19:00 | 45.47 | 45.06
2017-11-22 19:30 | 10.53 | 7.53
2017-11-22 20:00 | 7.7 | -4.23
2017-11-22 20:30 | 30.59 | 30.58
2017-11-22 21:00 | 36.34 | 36.22
2017-11-22 21:30 | 19.2 | 18.65
2017-11-22 22:00 | 7.52 | 4.19
2017-11-22 22:30 | 11.98 | 8.58
2017-11-22 23:00 | 29.65 | 27.87
2017-11-22 23:30 | 14.88 | 10.34
2017-11-23 | 29.44 | -28.6
2017-11-23 00:30 | 49.02 | -48.88
2017-11-23 01:00 | 57.48 | -57.46
2017-11-23 01:30 | 56.82 | -56.81
2017-11-23 02:00 | 57.63 | -57.62
2017-11-23 02:30 | 59.07 | -59.07
2017-11-23 03:00 | 61.35 | -61.35
2017-11-23 03:30 | 61.79 | -61.78
2017-11-23 04:00 | 58.37 | -58.35
2017-11-23 04:30 | 58.05 | -58.02
2017-11-23 05:00 | 52.89 | -52.84
2017-11-23 05:30 | 42.04 | -41.87
2017-11-23 06:00 | 28.18 | -27.33
2017-11-23 06:30 | 20.81 | -20.24
2017-11-23 07:00 | 9.3 | -9.3
2017-11-23 07:30 | 8.14 | 3.99
2017-11-23 08:00 | 18.89 | 4.58
2017-11-23 08:30 | 13.62 | 3.7
2017-11-23 09:00 | 15.28 | 1.32
2017-11-23 09:30 | 17.9 | 0.44
2017-11-23 10:00 | 19.34 | -0.96
2017-11-23 10:30 | 23.41 | -10.15
2017-11-23 11:00 | 34.9 | -25.35
2017-11-23 11:30 | 36.67 | -27.27
2017-11-23 12:00 | 29.44 | -16.6
2017-11-23 12:30 | 32.36 | -21.28
2017-11-23 13:00 | 28.91 | -15.51
2017-11-23 13:30 | 24.67 | -4.44
2017-11-23 14:00 | 24.19 | 4.05
2017-11-23 14:30 | 24.7 | 4.67
2017-11-23 15:00 | 25.3 | 9.97
2017-11-23 15:30 | 23.03 | 8.06
2017-11-23 16:00 | 25.8 | 17.7
2017-11-23 16:30 | 30.78 | 25.71
2017-11-23 17:00 | 36.46 | 32.89
2017-11-23 17:30 | 41.96 | 40.16
2017-11-23 18:00 | 47.7 | 46.71
2017-11-23 18:30 | 58.47 | 58.05
2017-11-23 19:00 | 80.08 | 79.56
2017-11-23 19:30 | 77.83 | 77.34
2017-11-23 20:00 | 75 | 74.64
2017-11-23 20:30 | 78.79 | 78.67
2017-11-23 21:00 | 74.37 | 74.35
2017-11-23 21:30 | 45.17 | 44.82
2017-11-23 22:00 | 17.2 | 15.07
2017-11-23 22:30 | 20.22 | 16.73
2017-11-23 23:00 | 37.95 | 35.86
2017-11-23 23:30 | 38.89 | 36.23
2017-11-24 | 12.62 | -5.24
2017-11-24 00:30 | 33.77 | -32.41
2017-11-24 01:00 | 49.61 | -48.93
2017-11-24 01:30 | 46.33 | -45.53
2017-11-24 02:00 | 45.51 | -44.66
2017-11-24 02:30 | 56.35 | -56.06
2017-11-24 03:00 | 58.6 | -58.37
2017-11-24 03:30 | 54.71 | -54.39
2017-11-24 04:00 | 53.1 | -52.61
2017-11-24 04:30 | 47.1 | -46.39
2017-11-24 05:00 | 48.98 | -48.35
2017-11-24 05:30 | 38.94 | -37.66
2017-11-24 06:00 | 16.07 | -11.69
2017-11-24 06:30 | 7.46 | -1.03
2017-11-24 07:00 | 6.06 | -6.06
2017-11-24 07:30 | 20.68 | -7.72
2017-11-24 08:00 | 27 | -13.89
2017-11-24 08:30 | 45.62 | -41.1
2017-11-24 09:00 | 45.74 | -38.97
2017-11-24 09:30 | 28.09 | -14.01
2017-11-24 10:00 | 28.27 | -8.86
2017-11-24 10:30 | 31.08 | -9.96
2017-11-24 11:00 | 38.63 | -21.1
2017-11-24 11:30 | 41.62 | -24.38
2017-11-24 12:00 | 39.39 | -20.39
2017-11-24 12:30 | 41.32 | -23.97
2017-11-24 13:00 | 43.69 | -27.15
2017-11-24 13:30 | 37.01 | -13.73
2017-11-24 14:00 | 38.93 | -18
2017-11-24 14:30 | 33.94 | 9.62
2017-11-24 15:00 | 31.1 | 0.44
2017-11-24 15:30 | 35.17 | 21.37
2017-11-24 16:00 | 45.7 | 38.42
2017-11-24 16:30 | 51.72 | 46.99
2017-11-24 17:00 | 72.75 | 70.14
2017-11-24 17:30 | 78.61 | 77.27
2017-11-24 18:00 | 61.67 | 60.88
2017-11-24 18:30 | 53.46 | 52.93
2017-11-24 19:00 | 71.29 | 70.54
2017-11-24 19:30 | 74.61 | 74.07
2017-11-24 20:00 | 73.24 | 72.92
2017-11-24 20:30 | 85.54 | 85.41
2017-11-24 21:00 | 58.49 | 58.25
2017-11-24 21:30 | 10.35 | 9.73
2017-11-24 22:00 | 31.59 | -31.48
2017-11-24 22:30 | 11.25 | -11.23
2017-11-24 23:00 | 23.82 | -23.4
2017-11-24 23:30 | 50.88 | -50.71
2017-11-25 | 63.1 | -63.01
2017-11-25 00:30 | 68.36 | -68.33
2017-11-25 01:00 | 59.64 | -59.56
2017-11-25 01:30 | 43.89 | -43.76
2017-11-25 02:00 | 39.3 | -39.17
2017-11-25 02:30 | 47.51 | -47.2
2017-11-25 03:00 | 56.14 | -55.99
2017-11-25 03:30 | 57.62 | -57.47
2017-11-25 04:00 | 58.13 | -58
2017-11-25 04:30 | 47.73 | -47.51
2017-11-25 05:00 | 48.83 | -48.67
2017-11-25 05:30 | 51.68 | -51.56
2017-11-25 06:00 | 53.58 | -53.51
2017-11-25 06:30 | 48.47 | -48.4
2017-11-25 07:00 | 41.57 | -41.49
2017-11-25 07:30 | 37.76 | -37.75
2017-11-25 08:00 | 52.61 | -52.28
2017-11-25 08:30 | 52.95 | -47.34
2017-11-25 09:00 | 54.01 | -43.52
2017-11-25 09:30 | 40.38 | -36.15
2017-11-25 10:00 | 37.04 | -32.26
2017-11-25 10:30 | 35 | -29.36
2017-11-25 11:00 | 34.31 | -27.97
2017-11-25 11:30 | 33.93 | -27.27
2017-11-25 12:00 | 36.44 | -30
2017-11-25 12:30 | 33.55 | -26.61
2017-11-25 13:00 | 18.73 | 0
2017-11-25 13:30 | 18.53 | 0.81
2017-11-25 14:00 | 18.24 | -4.21
2017-11-25 14:30 | 18.42 | 5.58
2017-11-25 15:00 | 17.14 | 1.03
2017-11-25 15:30 | 18.36 | -5.07
2017-11-25 16:00 | 30.55 | -24.8
2017-11-25 16:30 | 30.92 | 26.97
2017-11-25 17:00 | 32.77 | 29.42
2017-11-25 17:30 | 48.01 | 46.46
2017-11-25 18:00 | 45.81 | 44.86
2017-11-25 18:30 | 52 | 51.32
2017-11-25 19:00 | 74.82 | 73.97
2017-11-25 19:30 | 77.7 | 77.03
2017-11-25 20:00 | 55.96 | 55.27
2017-11-25 20:30 | 59.86 | 59.51
2017-11-25 21:00 | 47.97 | 47.68
2017-11-25 21:30 | 29.14 | 28.97
2017-11-25 22:00 | 9.88 | 9.82
2017-11-25 22:30 | 1.48 | -1.47
2017-11-25 23:00 | 25.68 | 25
2017-11-25 23:30 | 23.05 | 20.17
2017-11-26 | 20.54 | -19.14
2017-11-26 00:30 | 50.7 | -50.36
2017-11-26 01:00 | 57.02 | -56.83
2017-11-26 01:30 | 50.59 | -50.3
2017-11-26 02:00 | 49.65 | -49.32
2017-11-26 02:30 | 54.63 | -54.31
2017-11-26 03:00 | 55.85 | -55.53
2017-11-26 03:30 | 51.63 | -51.22
2017-11-26 04:00 | 59.13 | -58.85
2017-11-26 04:30 | 59.45 | -59.22
2017-11-26 05:00 | 62.37 | -62.34
2017-11-26 05:30 | 62 | -61.98
2017-11-26 06:00 | 63.25 | -63.21
2017-11-26 06:30 | 63.59 | -63.52
2017-11-26 07:00 | 66.11 | -66.06
2017-11-26 07:30 | 62.85 | -62.8
2017-11-26 08:00 | 58.71 | -58.7
2017-11-26 08:30 | 50.56 | -49.22
2017-11-26 09:00 | 53.81 | -46.23
2017-11-26 09:30 | 49.5 | -39.34
2017-11-26 10:00 | 43.17 | -32.62
2017-11-26 10:30 | 40.86 | -30.22
2017-11-26 11:00 | 39.14 | -27.89
2017-11-26 11:30 | 35.56 | -32.26
2017-11-26 12:00 | 39.71 | -37.11
2017-11-26 12:30 | 36.54 | -33.52
2017-11-26 13:00 | 39.99 | -37.05
2017-11-26 13:30 | 39.19 | -36.1
2017-11-26 14:00 | 38.8 | -35.66
2017-11-26 14:30 | 34.38 | -31.17
2017-11-26 15:00 | 8.54 | -8.51
2017-11-26 15:30 | 8.68 | 7.78
2017-11-26 16:00 | 6.64 | -5.35
2017-11-26 16:30 | 26.12 | 24.96
2017-11-26 17:00 | 35.15 | 34.41
2017-11-26 17:30 | 66.12 | 65.81
2017-11-26 18:00 | 81.24 | 81.12
2017-11-26 18:30 | 103.19 | 103.14
2017-11-26 19:00 | 134.71 | 134.65
2017-11-26 19:30 | 125.96 | 125.93
2017-11-26 20:00 | 117.65 | 117.65
2017-11-26 20:30 | 134.31 | 134.24
2017-11-26 21:00 | 94.93 | 94.66
2017-11-26 21:30 | 86 | 85.36
2017-11-26 22:00 | 60.78 | 59.34
2017-11-26 22:30 | 45.93 | 43.6
2017-11-26 23:00 | 68.3 | 66.33
2017-11-26 23:30 | 45.05 | 42.42
2017-11-27 | 10.07 | -2.24
2017-11-27 00:30 | 28.6 | -27.38
2017-11-27 01:00 | 40.04 | -39.33
2017-11-27 01:30 | 39.87 | -39.06
2017-11-27 02:00 | 43.03 | -42.23
2017-11-27 02:30 | 40.17 | -39.41
2017-11-27 03:00 | 52.46 | -52.13
2017-11-27 03:30 | 48.28 | -47.86
2017-11-27 04:00 | 54.23 | -53.9
2017-11-27 04:30 | 54.94 | -54.57
2017-11-27 05:00 | 46.28 | -45.75
2017-11-27 05:30 | 40.47 | -40.15
2017-11-27 06:00 | 50.87 | -50.76
2017-11-27 06:30 | 47.37 | -47.31
2017-11-27 07:00 | 40.2 | -29.75
2017-11-27 07:30 | 17.08 | 3.33
2017-11-27 08:00 | 20.42 | 10.2
2017-11-27 08:30 | 24.81 | -1.24
2017-11-27 09:00 | 33.73 | 17.8
2017-11-27 09:30 | 36.4 | 19.92
2017-11-27 10:00 | 35.83 | 15.21
2017-11-27 10:30 | 37.94 | 13.66
2017-11-27 11:00 | 36.89 | 5.6
2017-11-27 11:30 | 41.84 | -11.17
2017-11-27 12:00 | 44.21 | -14.25
2017-11-27 12:30 | 38.9 | 1.02
2017-11-27 13:00 | 40.93 | 15.15
2017-11-27 13:30 | 44.49 | 23.23
2017-11-27 14:00 | 45.97 | 24.97
2017-11-27 14:30 | 58.94 | 44.21
2017-11-27 15:00 | 66.18 | 54.13
2017-11-27 15:30 | 71.35 | 61.46
2017-11-27 16:00 | 88.57 | 82.21
2017-11-27 16:30 | 96.86 | 91.97
2017-11-27 17:00 | 108.46 | 104.75
2017-11-27 17:30 | 115.11 | 114.65
2017-11-27 18:00 | 106.77 | 106.73
2017-11-27 18:30 | 122.03 | 121.94
2017-11-27 19:00 | 127.26 | 127.26
2017-11-27 19:30 | 127.56 | 127.55
2017-11-27 20:00 | 106.27 | 106.21
2017-11-27 20:30 | 106.59 | 106.43
2017-11-27 21:00 | 84.77 | 84.45
2017-11-27 21:30 | 61.42 | 61.34
2017-11-27 22:00 | 42.15 | 41.89
2017-11-27 22:30 | 31.27 | 30.69
2017-11-27 23:00 | 58.85 | 58.85
2017-11-27 23:30 | 57.78 | 57.76
2017-11-28 | 21.02 | 20.94
2017-11-28 00:30 | 8.03 | 5.57
2017-11-28 01:00 | 16.01 | -14.08
2017-11-28 01:30 | 23.52 | -21.78
2017-11-28 02:00 | 28.16 | -26.16
2017-11-28 02:30 | 25.59 | -23.28
2017-11-28 03:00 | 23.97 | -21.17
2017-11-28 03:30 | 18.63 | -15.02
2017-11-28 04:00 | 55.55 | -52.54
2017-11-28 04:30 | 63.88 | -60.18
2017-11-28 05:00 | 50.69 | -45.62
2017-11-28 05:30 | 66.32 | -61.84
2017-11-28 06:00 | 63.47 | -61.44
2017-11-28 06:30 | 48.47 | -47.47
2017-11-28 07:00 | 36.66 | -35.1
2017-11-28 07:30 | 28.99 | -27.12
2017-11-28 08:00 | 32.47 | -24.82
2017-11-28 08:30 | 36.78 | -22.65
2017-11-28 09:00 | 35.66 | -15.84
2017-11-28 09:30 | 45.69 | -15.24
2017-11-28 10:00 | 56.58 | -15.11
2017-11-28 10:30 | 57.93 | -14.61
2017-11-28 11:00 | 43.9 | -11.83
2017-11-28 11:30 | 33.44 | -13.51
2017-11-28 12:00 | 35.12 | -9.92
2017-11-28 12:30 | 34.6 | -6.15
2017-11-28 13:00 | 33.39 | -1.9
2017-11-28 13:30 | 33.36 | -2.42
2017-11-28 14:00 | 33.66 | -1.91
2017-11-28 14:30 | 35.04 | -5.49
2017-11-28 15:00 | 30.06 | 15.75
2017-11-28 15:30 | 12.6 | -0.92
2017-11-28 16:00 | 9.96 | 0.78
2017-11-28 16:30 | 10.97 | 4.53
2017-11-28 17:00 | 18.49 | 11.06
2017-11-28 17:30 | 19.37 | 9.11
2017-11-28 18:00 | 20.57 | 7.74
2017-11-28 18:30 | 23.11 | 8.97
2017-11-28 19:00 | 91.49 | 89.95
2017-11-28 19:30 | 125.79 | 125.56
2017-11-28 20:00 | 106.49 | 106.31
2017-11-28 20:30 | 91.6 | 91.39
2017-11-28 21:00 | 65.32 | 62.64
2017-11-28 21:30 | 70.46 | 68.07
2017-11-28 22:00 | 77.77 | 76.42
2017-11-28 22:30 | 72.17 | 71.23
2017-11-28 23:00 | 76.59 | 75.54
2017-11-28 23:30 | 71.02 | 69.78
2017-11-29 | 39.93 | 38.23
2017-11-29 00:30 | 18.07 | 15.44
2017-11-29 01:00 | 10.39 | 4.23
2017-11-29 01:30 | 21.55 | -19.21
2017-11-29 02:00 | 30.68 | -28.32
2017-11-29 02:30 | 37.01 | -34.81
2017-11-29 03:00 | 41.13 | -38.99
2017-11-29 03:30 | 44.91 | -43.06
2017-11-29 04:00 | 48.81 | -47.08
2017-11-29 04:30 | 50 | -48.38
2017-11-29 05:00 | 34.24 | -31.74
2017-11-29 05:30 | 19.55 | -14.58
2017-11-29 06:00 | 14.43 | 0.61
2017-11-29 06:30 | 18.18 | 7.35
2017-11-29 07:00 | 21.2 | 19.36
2017-11-29 07:30 | 67.82 | 67.8
2017-11-29 08:00 | 80.26 | 80.23
2017-11-29 08:30 | 63.4 | 63.16
2017-11-29 09:00 | 72.03 | 68.16
2017-11-29 09:30 | 70.84 | 66.27
2017-11-29 10:00 | 123.03 | 117.75
2017-11-29 10:30 | 134.15 | 128.78
2017-11-29 11:00 | 136.74 | 131.45
2017-11-29 11:30 | 140.47 | 135.23
2017-11-29 12:00 | 131.9 | 126.5
2017-11-29 12:30 | 121.85 | 115.88
2017-11-29 13:00 | 118.21 | 111.17
2017-11-29 13:30 | 116.74 | 110.79
2017-11-29 14:00 | 101.57 | 93
2017-11-29 14:30 | 86.67 | 78.81
2017-11-29 15:00 | 18.99 | 5.43
2017-11-29 15:30 | 58.37 | 58.02
2017-11-29 16:00 | 71.54 | 71.34
2017-11-29 16:30 | 72.6 | 72.46
2017-11-29 17:00 | 75.39 | 75.29
2017-11-29 17:30 | 103.3 | 102.86
2017-11-29 18:00 | 67.79 | 64.53
2017-11-29 18:30 | 62.46 | 60.67
2017-11-29 19:00 | 81.27 | 81.18
2017-11-29 19:30 | 62.35 | 62.16
2017-11-29 20:00 | 54.37 | 54.29
2017-11-29 20:30 | 61.11 | 61.1
2017-11-29 21:00 | 52.81 | 52.8
2017-11-29 21:30 | 44.71 | 44.71
2017-11-29 22:00 | 25.69 | 25.68
2017-11-29 22:30 | 24.57 | 23.25
2017-11-29 23:00 | 30.16 | 28.66
2017-11-29 23:30 | 21.66 | 19.78
2017-11-30 | 9.77 | 1.68
2017-11-30 00:30 | 24.68 | -22.95
2017-11-30 01:00 | 38.15 | -37.28
2017-11-30 01:30 | 49.47 | -49.04
2017-11-30 02:00 | 47.63 | -47.16
2017-11-30 02:30 | 49.04 | -48.72
2017-11-30 03:00 | 49.38 | -49.09
2017-11-30 03:30 | 43.74 | -43.27
2017-11-30 04:00 | 60.85 | -60.73
2017-11-30 04:30 | 60.22 | -60.05
2017-11-30 05:00 | 62.23 | -62.15
2017-11-30 05:30 | 60.55 | -60.45
2017-11-30 06:00 | 57.02 | -56.87
2017-11-30 06:30 | 46.89 | -46.68
2017-11-30 07:00 | 37.21 | -36.71
2017-11-30 07:30 | 38.01 | 37.94
2017-11-30 08:00 | 23.78 | -16.47
2017-11-30 08:30 | 27.19 | -16.38
2017-11-30 09:00 | 28.25 | -12.63
2017-11-30 09:30 | 36.29 | -9
2017-11-30 10:00 | 29.12 | -3.63
2017-11-30 10:30 | 29.29 | -0.25
2017-11-30 11:00 | 31.11 | -7.75
2017-11-30 11:30 | 33.59 | -12.81
2017-11-30 12:00 | 31.44 | -8.33
2017-11-30 12:30 | 47.5 | 39.04
2017-11-30 13:00 | 41.52 | 32.42
2017-11-30 13:30 | 39.58 | 29.81
2017-11-30 14:00 | 30.06 | 8.89
2017-11-30 14:30 | 30.3 | 5.11
2017-11-30 15:00 | 31.15 | 12.61
2017-11-30 15:30 | 42.81 | 36.22
2017-11-30 16:00 | 28.05 | 20.09
2017-11-30 16:30 | 58.12 | 56.98
2017-11-30 17:00 | 69.11 | 68.36
2017-11-30 17:30 | 92.51 | 92.06
2017-11-30 18:00 | 95.96 | 94.38
2017-11-30 18:30 | 108.37 | 107.59
2017-11-30 19:00 | 123.57 | 123.56
2017-11-30 19:30 | 125.5 | 125.5
2017-11-30 20:00 | 114.56 | 112.07
2017-11-30 20:30 | 104.78 | 102.04
2017-11-30 21:00 | 92.5 | 90.29
2017-11-30 21:30 | 72.81 | 71.15
2017-11-30 22:00 | 38.87 | 36.8
2017-11-30 22:30 | 37.72 | 36.16
2017-11-30 23:00 | 67.57 | 67.09
2017-11-30 23:30 | 38.02 | 36.14
2017-12-01 | 16.28 | -8.63
2017-12-01 00:30 | 26.42 | -22.61
2017-12-01 01:00 | 33.71 | -30.5
2017-12-01 01:30 | 34.61 | -31.84
2017-12-01 02:00 | 41.78 | -41.02
2017-12-01 02:30 | 51.83 | -51.19
2017-12-01 03:00 | 49.23 | -48.75
2017-12-01 03:30 | 43.64 | -43.06
2017-12-01 04:00 | 49.31 | -48.68
2017-12-01 04:30 | 54.17 | -53.64
2017-12-01 05:00 | 43.14 | -42.48
2017-12-01 05:30 | 39.39 | -38.8
2017-12-01 06:00 | 28.29 | -28.05
2017-12-01 06:30 | 15.97 | -15.79
2017-12-01 07:00 | 5.39 | 0.22
2017-12-01 07:30 | 33.2 | 32.59
2017-12-01 08:00 | 48.81 | 48.57
2017-12-01 08:30 | 32.3 | 27.47
2017-12-01 09:00 | 45.36 | 37.65
2017-12-01 09:30 | 48.76 | 41.34
2017-12-01 10:00 | 50.41 | 42.69
2017-12-01 10:30 | 47.76 | 38.64
2017-12-01 11:00 | 37.05 | 22.71
2017-12-01 11:30 | 62.12 | 55.08
2017-12-01 12:00 | 70.74 | 64.96
2017-12-01 12:30 | 66.58 | 60.59
2017-12-01 13:00 | 59.78 | 52.92
2017-12-01 13:30 | 64.46 | 58.09
2017-12-01 14:00 | 65.67 | 59
2017-12-01 14:30 | 78.02 | 72.49
2017-12-01 15:00 | 69.36 | 63.01
2017-12-01 15:30 | 68.88 | 63
2017-12-01 16:00 | 81.27 | 76.74
2017-12-01 16:30 | 98.14 | 94.95
2017-12-01 17:00 | 108.13 | 106.03
2017-12-01 17:30 | 126.09 | 125.19
2017-12-01 18:00 | 119.01 | 118.54
2017-12-01 18:30 | 115.96 | 115.73
2017-12-01 19:00 | 124.51 | 124.11
2017-12-01 19:30 | 121.24 | 120.84
2017-12-01 20:00 | 117.4 | 117.1
2017-12-01 20:30 | 121.17 | 119.44
2017-12-01 21:00 | 114.76 | 112.82
2017-12-01 21:30 | 100.63 | 99
2017-12-01 22:00 | 84.01 | 82.6
2017-12-01 22:30 | 78.44 | 77.41
2017-12-01 23:00 | 81.6 | 80.92
2017-12-01 23:30 | 46.46 | 45.85
2017-12-02 | 14.12 | 11.26
2017-12-02 00:30 | 21.77 | -17.94
2017-12-02 01:00 | 25.67 | -23.14
2017-12-02 01:30 | 28.35 | -26.59
2017-12-02 02:00 | 12.42 | -6.02
2017-12-02 02:30 | 15.54 | -11
2017-12-02 03:00 | 13.31 | -7.56
2017-12-02 03:30 | 13.19 | 5.67
2017-12-02 04:00 | 11.83 | 0.3
2017-12-02 04:30 | 12.03 | -1.75
2017-12-02 05:00 | 14.28 | -9.45
2017-12-02 05:30 | 17.58 | -14.4
2017-12-02 06:00 | 24.11 | -22.42
2017-12-02 06:30 | 25 | -23.91
2017-12-02 07:00 | 13.93 | -13.45
2017-12-02 07:30 | 10.03 | 9.98
2017-12-02 08:00 | 13.33 | 11.72
2017-12-02 08:30 | 40.63 | 26.49
2017-12-02 09:00 | 44.16 | 34.45
2017-12-02 09:30 | 46.61 | 41.57
2017-12-02 10:00 | 59.16 | 54.56
2017-12-02 10:30 | 59.34 | 54.83
2017-12-02 11:00 | 80.94 | 78.05
2017-12-02 11:30 | 69.56 | 66.78
2017-12-02 12:00 | 63.5 | 60.42
2017-12-02 12:30 | 63.15 | 60.21
2017-12-02 13:00 | 58.76 | 55.17
2017-12-02 13:30 | 62.31 | 59.11
2017-12-02 14:00 | 86.83 | 84.49
2017-12-02 14:30 | 109.5 | 107.67
2017-12-02 15:00 | 113.31 | 111.64
2017-12-02 15:30 | 111.84 | 110
2017-12-02 16:00 | 117.35 | 115.58
2017-12-02 16:30 | 120.54 | 118.93
2017-12-02 17:00 | 115.82 | 115.8
2017-12-02 17:30 | 114.33 | 114.31
2017-12-02 18:00 | 112.57 | 112.52
2017-12-02 18:30 | 113.41 | 113.32
2017-12-02 19:00 | 117.22 | 117.2
2017-12-02 19:30 | 117.37 | 117.33
2017-12-02 20:00 | 117.87 | 117.77
2017-12-02 20:30 | 113.62 | 113.52
2017-12-02 21:00 | 103.42 | 102.72
2017-12-02 21:30 | 103.6 | 102.77
2017-12-02 22:00 | 110.65 | 109.71
2017-12-02 22:30 | 121.42 | 121.34
2017-12-02 23:00 | 156.66 | 156.62
2017-12-02 23:30 | 123.04 | 122.91
2017-12-03 | 94.84 | 94.34
2017-12-03 00:30 | 66.08 | 65.18
2017-12-03 01:00 | 39.94 | 38.4
2017-12-03 01:30 | 37.47 | 35.54
2017-12-03 02:00 | 28.18 | 25.78
2017-12-03 02:30 | 35.37 | 33.28
2017-12-03 03:00 | 30.57 | 28.11
2017-12-03 03:30 | 24.32 | 21.27
2017-12-03 04:00 | 26.76 | 23.94
2017-12-03 04:30 | 38.92 | 36.75
2017-12-03 05:00 | 34.06 | 31.88
2017-12-03 05:30 | 33.43 | 30.27
2017-12-03 06:00 | 22.68 | 16.61
2017-12-03 06:30 | 30.03 | 23.4
2017-12-03 07:00 | 23.88 | 13.27
2017-12-03 07:30 | 34.44 | 26.41
2017-12-03 08:00 | 49.55 | 44.6
2017-12-03 08:30 | 56.12 | 56.08
2017-12-03 09:00 | 69.43 | 69.16
2017-12-03 09:30 | 104.38 | 101.05
2017-12-03 10:00 | 96.67 | 95.57
2017-12-03 10:30 | 91.59 | 89.83
2017-12-03 11:00 | 109.6 | 107.87
2017-12-03 11:30 | 143.04 | 141.57
2017-12-03 12:00 | 145.7 | 145.32
2017-12-03 12:30 | 152.19 | 152.17
2017-12-03 13:00 | 154.88 | 154.86
2017-12-03 13:30 | 155.92 | 155.9
2017-12-03 14:00 | 168.32 | 168.31
2017-12-03 14:30 | 164.83 | 164.81
2017-12-03 15:00 | 154.93 | 154.93
2017-12-03 15:30 | 153.44 | 153.43
2017-12-03 16:00 | 162.17 | 162.14
2017-12-03 16:30 | 128.34 | 128.31
2017-12-03 17:00 | 126.26 | 126.25
2017-12-03 17:30 | 124.29 | 124.29
2017-12-03 18:00 | 122.4 | 122.4
2017-12-03 18:30 | 126.73 | 126.73
2017-12-03 19:00 | 132.01 | 132.01
2017-12-03 19:30 | 131.69 | 131.69
2017-12-03 20:00 | 129.5 | 129.49
2017-12-03 20:30 | 122.18 | 122.15
2017-12-03 21:00 | 112.92 | 112.32
2017-12-03 21:30 | 109.72 | 108.93
2017-12-03 22:00 | 108.43 | 107.17
2017-12-03 22:30 | 109.5 | 108.34
2017-12-03 23:00 | 134.22 | 133.3
2017-12-03 23:30 | 104.42 | 103.1
2017-12-04 | 52.93 | 52.34
2017-12-04 00:30 | 25.18 | 23.43
2017-12-04 01:00 | 21.08 | 8.66
2017-12-04 01:30 | 18.3 | 2.21
2017-12-04 02:00 | 17.93 | -7.44
2017-12-04 02:30 | 23.22 | -17.91
2017-12-04 03:00 | 27.72 | -24.11
2017-12-04 03:30 | 28.64 | -25.44
2017-12-04 04:00 | 28.19 | -24.75
2017-12-04 04:30 | 16.48 | -4.51
2017-12-04 05:00 | 17.86 | 8.72
2017-12-04 05:30 | 22.77 | 15.87
2017-12-04 06:00 | 37.06 | 32.46
2017-12-04 06:30 | 46.2 | 45.67
2017-12-04 07:00 | 65.25 | 65.11
2017-12-04 07:30 | 85.9 | 85.08
2017-12-04 08:00 | 116.03 | 112.12
2017-12-04 08:30 | 120.59 | 118.52
2017-12-04 09:00 | 118.65 | 116.73
2017-12-04 09:30 | 108.9 | 106.76
2017-12-04 10:00 | 126.69 | 124.08
2017-12-04 10:30 | 125.67 | 122.9
2017-12-04 11:00 | 137.82 | 134.77
2017-12-04 11:30 | 140.17 | 137.36
2017-12-04 12:00 | 133.58 | 132.63
2017-12-04 12:30 | 129.7 | 128.64
2017-12-04 13:00 | 127.98 | 126.85
2017-12-04 13:30 | 126.12 | 125.09
2017-12-04 14:00 | 115.66 | 114.9
2017-12-04 14:30 | 84.48 | 84.16
2017-12-04 15:00 | 80.52 | 80.49
2017-12-04 15:30 | 77.5 | 77.43
2017-12-04 16:00 | 75.64 | 75.51
2017-12-04 16:30 | 75.55 | 75.52
2017-12-04 17:00 | 77.42 | 77.41
2017-12-04 17:30 | 78.63 | 78.63
2017-12-04 18:00 | 80.8 | 80.78
2017-12-04 18:30 | 79.59 | 79.45
2017-12-04 19:00 | 81.86 | 81.82
2017-12-04 19:30 | 83.71 | 83.62
2017-12-04 20:00 | 85.27 | 85.01
2017-12-04 20:30 | 101.05 | 100.59
2017-12-04 21:00 | 72.83 | 72.12
2017-12-04 21:30 | 63.57 | 62.2
2017-12-04 22:00 | 55.56 | 54.16
2017-12-04 22:30 | 56.51 | 55.8
2017-12-04 23:00 | 78.22 | 77.46
2017-12-04 23:30 | 49.16 | 47.71
2017-12-05 | 19.85 | 15.74
2017-12-05 00:30 | 11.34 | -1.52
2017-12-05 01:00 | 26.17 | -23.96
2017-12-05 01:30 | 35.53 | -33.87
2017-12-05 02:00 | 24.03 | -21.68
2017-12-05 02:30 | 15.41 | -6.96
2017-12-05 03:00 | 22.68 | -15.11
2017-12-05 03:30 | 27.53 | -22.84
2017-12-05 04:00 | 31.33 | -27.61
2017-12-05 04:30 | 25.64 | -20.28
2017-12-05 05:00 | 21.34 | -15.26
2017-12-05 05:30 | 16.24 | -5.71
2017-12-05 06:00 | 18.05 | 4.86
2017-12-05 06:30 | 18.12 | 16.27
2017-12-05 07:00 | 32.39 | 29.39
2017-12-05 07:30 | 46.82 | 44.54
2017-12-05 08:00 | 66.59 | 66.52
2017-12-05 08:30 | 79.46 | 79.3
2017-12-05 09:00 | 85.86 | 82.6
2017-12-05 09:30 | 76.98 | 72.46
2017-12-05 10:00 | 77.93 | 72.88
2017-12-05 10:30 | 75.95 | 70.46
2017-12-05 11:00 | 80.34 | 74.38
2017-12-05 11:30 | 79.63 | 72.03
2017-12-05 12:00 | 73.19 | 65.38
2017-12-05 12:30 | 74.8 | 67.18
2017-12-05 13:00 | 92 | 85.9
2017-12-05 13:30 | 103.03 | 97.5
2017-12-05 14:00 | 121.86 | 117.73
2017-12-05 14:30 | 131.42 | 128.13
2017-12-05 15:00 | 109.49 | 105.89
2017-12-05 15:30 | 95.16 | 91.42
2017-12-05 16:00 | 105.28 | 102.1
2017-12-05 16:30 | 113.34 | 110.83
2017-12-05 17:00 | 119.2 | 117.54
2017-12-05 17:30 | 107.69 | 106.66
2017-12-05 18:00 | 86.98 | 86.36
2017-12-05 18:30 | 88.69 | 88.27
2017-12-05 19:00 | 95.03 | 94.31
2017-12-05 19:30 | 117.53 | 116.99
2017-12-05 20:00 | 125.58 | 125.26
2017-12-05 20:30 | 114.87 | 114.78
2017-12-05 21:00 | 92.63 | 92.62
2017-12-05 21:30 | 83.03 | 83.01
2017-12-05 22:00 | 73.35 | 72.07
2017-12-05 22:30 | 72.14 | 69.09
2017-12-05 23:00 | 105.18 | 103.69
2017-12-05 23:30 | 95.17 | 94.46
2017-12-06 | 63.69 | 62.67
2017-12-06 00:30 | 39.42 | 37.93
2017-12-06 01:00 | 17.56 | 14.21
2017-12-06 01:30 | 10.09 | -0.62
2017-12-06 02:00 | 17.26 | -14.45
2017-12-06 02:30 | 18.15 | -15.41
2017-12-06 03:00 | 25.99 | -24.4
2017-12-06 03:30 | 28.35 | -26.97
2017-12-06 04:00 | 20.57 | -17.94
2017-12-06 04:30 | 12.37 | -3.86
2017-12-06 05:00 | 14.07 | -2.26
2017-12-06 05:30 | 18.87 | 5.52
2017-12-06 06:00 | 26.88 | 15.94
2017-12-06 06:30 | 24.93 | 11.24
2017-12-06 07:00 | 2.05 | 1.76
2017-12-06 07:30 | 9.15 | 8.71
2017-12-06 08:00 | 16.5 | 16.5
2017-12-06 08:30 | 28.87 | 16.44
2017-12-06 09:00 | 28.55 | 12.52
2017-12-06 09:30 | 28.42 | -0.05
2017-12-06 10:00 | 30.84 | 0.64
2017-12-06 10:30 | 35.77 | 25.51
2017-12-06 11:00 | 45.01 | 37.64
2017-12-06 11:30 | 30.27 | 18.89
2017-12-06 12:00 | 29.56 | 16.68
2017-12-06 12:30 | 36.64 | 28.06
2017-12-06 13:00 | 44.61 | 37.71
2017-12-06 13:30 | 51.62 | 45.88
2017-12-06 14:00 | 68.03 | 63.63
2017-12-06 14:30 | 84.61 | 83.39
2017-12-06 15:00 | 99.72 | 99.55
2017-12-06 15:30 | 118.59 | 118.47
2017-12-06 16:00 | 126.75 | 126.63
2017-12-06 16:30 | 131.74 | 131.63
2017-12-06 17:00 | 136.13 | 136.07
2017-12-06 17:30 | 133.94 | 133.89
2017-12-06 18:00 | 127.34 | 127.3
2017-12-06 18:30 | 125.22 | 124.52
2017-12-06 19:00 | 131.12 | 130.43
2017-12-06 19:30 | 133.51 | 132.59
2017-12-06 20:00 | 132.65 | 131.71
2017-12-06 20:30 | 125.77 | 125.61
2017-12-06 21:00 | 116.24 | 116.07
2017-12-06 21:30 | 98.11 | 97.78
2017-12-06 22:00 | 78.49 | 78.06
2017-12-06 22:30 | 78.62 | 78.18
2017-12-06 23:00 | 108.3 | 107.94
2017-12-06 23:30 | 86.16 | 85.62
2017-12-07 | 43.17 | 42.4
2017-12-07 00:30 | 7.37 | -3.38
2017-12-07 01:00 | 26.16 | -25.58
2017-12-07 01:30 | 20.01 | -19.04
2017-12-07 02:00 | 27.42 | -26.78
2017-12-07 02:30 | 50.45 | -50.23
2017-12-07 03:00 | 58.06 | -57.94
2017-12-07 03:30 | 60.24 | -60.11
2017-12-07 04:00 | 60.55 | -60.39
2017-12-07 04:30 | 54.29 | -53.93
2017-12-07 05:00 | 50.97 | -50.68
2017-12-07 05:30 | 31.61 | -31.04
2017-12-07 06:00 | 18.07 | -16.71
2017-12-07 06:30 | 8.47 | -8.07
2017-12-07 07:00 | 9.37 | -8.93
2017-12-07 07:30 | 27.51 | 13
2017-12-07 08:00 | 41.47 | 23.97
2017-12-07 08:30 | 60 | 47.26
2017-12-07 09:00 | 58.51 | 41.56
2017-12-07 09:30 | 51.18 | 36.48
2017-12-07 10:00 | 46.36 | 26.55
2017-12-07 10:30 | 47.87 | 24.85
2017-12-07 11:00 | 48.4 | 22.75
2017-12-07 11:30 | 45.59 | 17.01
2017-12-07 12:00 | 46.07 | 15.94
2017-12-07 12:30 | 47.67 | 18.4
2017-12-07 13:00 | 48.39 | 18.74
2017-12-07 13:30 | 50.2 | 19.9
2017-12-07 14:00 | 47.35 | 23.14
2017-12-07 14:30 | 42.8 | 28.8
2017-12-07 15:00 | 44.05 | 30.38
2017-12-07 15:30 | 45.71 | 33.04
2017-12-07 16:00 | 51.09 | 39.8
2017-12-07 16:30 | 54.08 | 44.36
2017-12-07 17:00 | 54.75 | 46.38
2017-12-07 17:30 | 49.54 | 41.7
2017-12-07 18:00 | 46.52 | 40.43
2017-12-07 18:30 | 45.02 | 40.5
2017-12-07 19:00 | 50.2 | 45.03
2017-12-07 19:30 | 52.74 | 47.98
2017-12-07 20:00 | 51.99 | 48.17
2017-12-07 20:30 | 48.75 | 43.4
2017-12-07 21:00 | 46.72 | 35.98
2017-12-07 21:30 | 45.83 | 27.71
2017-12-07 22:00 | 42.14 | 21.18
2017-12-07 22:30 | 33.51 | 10.21
2017-12-07 23:00 | 30.24 | 3.07
2017-12-07 23:30 | 16.15 | -10.66
2017-12-08 | 26.98 | -25.93
2017-12-08 00:30 | 37.13 | -34.81
2017-12-08 01:00 | 35.33 | -32.5
2017-12-08 01:30 | 32.78 | -29.45
2017-12-08 02:00 | 33.05 | -29.87
2017-12-08 02:30 | 33.27 | -30.47
2017-12-08 03:00 | 31.39 | -31.12
2017-12-08 03:30 | 31.84 | -31.16
2017-12-08 04:00 | 32.46 | -31.84
2017-12-08 04:30 | 32.48 | -31.82
2017-12-08 05:00 | 33.82 | -33.57
2017-12-08 05:30 | 31.98 | -31.72
2017-12-08 06:00 | 24.4 | -24.08
2017-12-08 06:30 | 13.84 | -13.72
2017-12-08 07:00 | 11.28 | -6.8
2017-12-08 07:30 | 27.03 | 5.68
2017-12-08 08:00 | 29.69 | 16.83
2017-12-08 08:30 | 33.8 | 18.17
2017-12-08 09:00 | 55.54 | 24.04
2017-12-08 09:30 | 61.78 | 25.19
2017-12-08 10:00 | 66.04 | 27.98
2017-12-08 10:30 | 72.52 | 32.4
2017-12-08 11:00 | 69.38 | 35.79
2017-12-08 11:30 | 73.18 | 48.62
2017-12-08 12:00 | 67.22 | 53.97
2017-12-08 12:30 | 57.22 | 56.28
2017-12-08 13:00 | 50.57 | 49.53
2017-12-08 13:30 | 37.35 | 32.39
2017-12-08 14:00 | 28.63 | 26.98
2017-12-08 14:30 | 26.87 | 25.8
2017-12-08 15:00 | 26.87 | 25.31
2017-12-08 15:30 | 27.4 | 22.31
2017-12-08 16:00 | 23.39 | 23.08
2017-12-08 16:30 | 22.85 | 22.16
2017-12-08 17:00 | 26.86 | 26.39
2017-12-08 17:30 | 27.45 | 26.47
2017-12-08 18:00 | 24.68 | 23.12
2017-12-08 18:30 | 20.8 | 20.46
2017-12-08 19:00 | 25.82 | 24.62
2017-12-08 19:30 | 26.35 | 25.79
2017-12-08 20:00 | 26.41 | 26.04
2017-12-08 20:30 | 22.6 | 22.59
2017-12-08 21:00 | 18.4 | 15.34
2017-12-08 21:30 | 15.38 | 10.73
2017-12-08 22:00 | 13.19 | 5.78
2017-12-08 22:30 | 11.62 | -1.03
2017-12-08 23:00 | 16.68 | -4.93
2017-12-08 23:30 | 24.88 | -14.81
2017-12-09 | 29.69 | -28.93
2017-12-09 00:30 | 37.18 | -35.99
2017-12-09 01:00 | 35.2 | -33.97
2017-12-09 01:30 | 34.34 | -32.99
2017-12-09 02:00 | 33.75 | -32.32
2017-12-09 02:30 | 34.13 | -31.5
2017-12-09 03:00 | 34.7 | -32.05
2017-12-09 03:30 | 34.78 | -32.01
2017-12-09 04:00 | 35.54 | -33.39
2017-12-09 04:30 | 36.21 | -34.43
2017-12-09 05:00 | 37.65 | -36.23
2017-12-09 05:30 | 37.44 | -36.21
2017-12-09 06:00 | 35.01 | -33.8
2017-12-09 06:30 | 32.49 | -31.12
2017-12-09 07:00 | 27.54 | -26.45
2017-12-09 07:30 | 19.94 | -19.91
2017-12-09 08:00 | 28.2 | -13.9
2017-12-09 08:30 | 29.17 | -6.56
2017-12-09 09:00 | 17.11 | 0.37
2017-12-09 09:30 | 5.53 | 4.08
2017-12-09 10:00 | 6.09 | 5.81
2017-12-09 10:30 | 7.75 | 7.75
2017-12-09 11:00 | 7.88 | 7.77
2017-12-09 11:30 | 7.99 | 7.96
2017-12-09 12:00 | 9.82 | 9.82
2017-12-09 12:30 | 9.6 | 9.58
2017-12-09 13:00 | 6.9 | 6.85
2017-12-09 13:30 | 9.88 | 9.88
2017-12-09 14:00 | 5.28 | 5.28
2017-12-09 14:30 | 6.64 | 6.54
2017-12-09 15:00 | 12.2 | 11.99
2017-12-09 15:30 | 19.87 | 19.75
2017-12-09 16:00 | 26.28 | 26.22
2017-12-09 16:30 | 25.86 | 25.78
2017-12-09 17:00 | 26.61 | 26.13
2017-12-09 17:30 | 27.09 | 26.83
2017-12-09 18:00 | 23.31 | 23.02
2017-12-09 18:30 | 27.33 | 19.38
2017-12-09 19:00 | 28.93 | 20.04
2017-12-09 19:30 | 20.21 | 17.28
2017-12-09 20:00 | 16.56 | 16.02
2017-12-09 20:30 | 13.93 | 10.45
2017-12-09 21:00 | 16.56 | 3.28
2017-12-09 21:30 | 18.53 | 3.23
2017-12-09 22:00 | 21.74 | 2.23
2017-12-09 22:30 | 21.34 | -1.52
2017-12-09 23:00 | 21.54 | -1.69
2017-12-09 23:30 | 21.84 | -7.24
2017-12-10 | 27.57 | -19.62
2017-12-10 00:30 | 34.36 | -28.45
2017-12-10 01:00 | 36.75 | -29.54
2017-12-10 01:30 | 37.6 | -30.42
2017-12-10 02:00 | 38.45 | -31.9
2017-12-10 02:30 | 39.4 | -33.45
2017-12-10 03:00 | 39.48 | -33.79
2017-12-10 03:30 | 41.69 | -35.23
2017-12-10 04:00 | 42.13 | -35.87
2017-12-10 04:30 | 42.48 | -36.5
2017-12-10 05:00 | 38.85 | -38.66
2017-12-10 05:30 | 38.9 | -38.88
2017-12-10 06:00 | 37.64 | -37.62
2017-12-10 06:30 | 35.78 | -35.5
2017-12-10 07:00 | 34.73 | -33.86
2017-12-10 07:30 | 31.03 | -30
2017-12-10 08:00 | 26.05 | -24.48
2017-12-10 08:30 | 21.34 | -17.67
2017-12-10 09:00 | 21.02 | -12.29
2017-12-10 09:30 | 16.98 | -8.25
2017-12-10 10:00 | 14.53 | -7.18
2017-12-10 10:30 | 2.2 | 1.13
2017-12-10 11:00 | 7.4 | 2.37
2017-12-10 11:30 | 9.04 | -2.47
2017-12-10 12:00 | 9.9 | -0.6
2017-12-10 12:30 | 10.36 | -2.73
2017-12-10 13:00 | 10.8 | -3.27
2017-12-10 13:30 | 10.75 | -3.17
2017-12-10 14:00 | 11.19 | -3.67
2017-12-10 14:30 | 10.12 | 1.52
2017-12-10 15:00 | 10.87 | 4.35
2017-12-10 15:30 | 13.93 | 8.71
2017-12-10 16:00 | 15.05 | 10.82
2017-12-10 16:30 | 16.18 | 12.04
2017-12-10 17:00 | 16.95 | 13.42
2017-12-10 17:30 | 14.32 | 11.77
2017-12-10 18:00 | 20.06 | 10.57
2017-12-10 18:30 | 21.38 | 10.12
2017-12-10 19:00 | 25.06 | 14.53
2017-12-10 19:30 | 23.87 | 18.13
2017-12-10 20:00 | 18.73 | 18.35
2017-12-10 20:30 | 17.14 | 16.37
2017-12-10 21:00 | 9.99 | 7.88
2017-12-10 21:30 | 7.95 | 6.95
2017-12-10 22:00 | 9.01 | 5.54
2017-12-10 22:30 | 8.44 | 0.26
2017-12-10 23:00 | 10.46 | -1.39
2017-12-10 23:30 | 16.44 | -9.82
2017-12-11 | 26.31 | -22.45
2017-12-11 00:30 | 32.34 | -29.96
2017-12-11 01:00 | 32.97 | -30.9
2017-12-11 01:30 | 32.89 | -30.81
2017-12-11 02:00 | 34.41 | -31.76
2017-12-11 02:30 | 35.43 | -32.61
2017-12-11 03:00 | 35.22 | -32.5
2017-12-11 03:30 | 35.66 | -32.92
2017-12-11 04:00 | 21.43 | -17.45
2017-12-11 04:30 | 18.08 | -13.93
2017-12-11 05:00 | 18.2 | -15.03
2017-12-11 05:30 | 19.06 | -16.75
2017-12-11 06:00 | 11.51 | -7.36
2017-12-11 06:30 | 15.18 | -15.16
2017-12-11 07:00 | 11.82 | -10.84
2017-12-11 07:30 | 17.98 | -2.21
2017-12-11 08:00 | 7 | 2.8
2017-12-11 08:30 | 10.59 | 6.42
2017-12-11 09:00 | 18.92 | 11.74
2017-12-11 09:30 | 21.25 | 13.74
2017-12-11 10:00 | 21.15 | 14.87
2017-12-11 10:30 | 24.69 | 19.32
2017-12-11 11:00 | 26.41 | 21.02
2017-12-11 11:30 | 25.83 | 20.98
2017-12-11 12:00 | 24.44 | 19.29
2017-12-11 12:30 | 24.43 | 19.88
2017-12-11 13:00 | 21.91 | 16.56
2017-12-11 13:30 | 19.98 | 14.6
2017-12-11 14:00 | 23.16 | 17.39
2017-12-11 14:30 | 24.22 | 19.6
2017-12-11 15:00 | 24.99 | 21.14
2017-12-11 15:30 | 26 | 22.88
2017-12-11 16:00 | 28.22 | 25.82
2017-12-11 16:30 | 28.15 | 26.65
2017-12-11 17:00 | 28.25 | 27.35
2017-12-11 17:30 | 26.37 | 25.39
2017-12-11 18:00 | 25.48 | 23.32
2017-12-11 18:30 | 28.14 | 24.79
2017-12-11 19:00 | 32.44 | 29.01
2017-12-11 19:30 | 35.21 | 31.43
2017-12-11 20:00 | 33.51 | 30.57
2017-12-11 20:30 | 33.65 | 25.76
2017-12-11 21:00 | 30.92 | 17.71
2017-12-11 21:30 | 21.01 | 11.68
2017-12-11 22:00 | 11.8 | 7.28
2017-12-11 22:30 | 7.81 | -1.41
2017-12-11 23:00 | 13.45 | -5.41
2017-12-11 23:30 | 20.43 | -16.86
2017-12-12 | 33.66 | -31.19
2017-12-12 00:30 | 42.85 | -40.02
2017-12-12 01:00 | 41.17 | -38.19
2017-12-12 01:30 | 37.14 | -34.69
2017-12-12 02:00 | 35.8 | -33.84
2017-12-12 02:30 | 36.09 | -34.18
2017-12-12 03:00 | 36.24 | -34.26
2017-12-12 03:30 | 36.61 | -34.77
2017-12-12 04:00 | 35.54 | -33.94
2017-12-12 04:30 | 35.22 | -33.67
2017-12-12 05:00 | 36.96 | -35.08
2017-12-12 05:30 | 37.59 | -35
2017-12-12 06:00 | 29.1 | -25.71
2017-12-12 06:30 | 23.06 | -16.86
2017-12-12 07:00 | 19.26 | -11.56
2017-12-12 07:30 | 21.88 | -1.92
2017-12-12 08:00 | 42.9 | 3.2
2017-12-12 08:30 | 52.66 | 8.14
2017-12-12 09:00 | 87.9 | 19.81
2017-12-12 09:30 | 88.86 | 19.34
2017-12-12 10:00 | 87.38 | 14.28
2017-12-12 10:30 | 89.28 | 14.03
2017-12-12 11:00 | 90.41 | 15.98
2017-12-12 11:30 | 89.53 | 12.88
2017-12-12 12:00 | 89.98 | 11.68
2017-12-12 12:30 | 90.16 | 11.79
2017-12-12 13:00 | 90.71 | 12.16
2017-12-12 13:30 | 90.98 | 13.45
2017-12-12 14:00 | 92.28 | 15.83
2017-12-12 14:30 | 93.93 | 19.79
2017-12-12 15:00 | 92.7 | 21.6
2017-12-12 15:30 | 92.79 | 23.56
2017-12-12 16:00 | 93.18 | 26.66
2017-12-12 16:30 | 92.37 | 28.49
2017-12-12 17:00 | 84.09 | 32.19
2017-12-12 17:30 | 71.89 | 30.87
2017-12-12 18:00 | 51.55 | 26.87
2017-12-12 18:30 | 48.81 | 27.3
2017-12-12 19:00 | 52.15 | 31.25
2017-12-12 19:30 | 53.27 | 33.01
2017-12-12 20:00 | 63.83 | 32.4
2017-12-12 20:30 | 59.77 | 26.92
2017-12-12 21:00 | 53.78 | 19.76
2017-12-12 21:30 | 48.05 | 13.85
2017-12-12 22:00 | 35.44 | 8.95
2017-12-12 22:30 | 7.5 | -0.44
2017-12-12 23:00 | 8.29 | -4.7
2017-12-12 23:30 | 17.37 | -16.78
2017-12-13 | 32.84 | -31.83
2017-12-13 00:30 | 41.61 | -39.51
2017-12-13 01:00 | 39.06 | -36.83
2017-12-13 01:30 | 36.45 | -34.22
2017-12-13 02:00 | 35.89 | -33.63
2017-12-13 02:30 | 36.52 | -34.34
2017-12-13 03:00 | 36.55 | -34.33
2017-12-13 03:30 | 36.02 | -34.07
2017-12-13 04:00 | 34.75 | -33.12
2017-12-13 04:30 | 34.22 | -32.71
2017-12-13 05:00 | 35.99 | -34.14
2017-12-13 05:30 | 36.68 | -34.4
2017-12-13 06:00 | 26.62 | -24.8
2017-12-13 06:30 | 19.5 | -16.34
2017-12-13 07:00 | 29.78 | -9.47
2017-12-13 07:30 | 55.76 | 2.52
2017-12-13 08:00 | 61 | 10.19
2017-12-13 08:30 | 68.46 | 10.99
2017-12-13 09:00 | 72.58 | 14.83
2017-12-13 09:30 | 75.22 | 17.18
2017-12-13 10:00 | 76.83 | 19.41
2017-12-13 10:30 | 75.81 | 16.33
2017-12-13 11:00 | 77.4 | 17.02
2017-12-13 11:30 | 92.8 | 18.67
2017-12-13 12:00 | 97.16 | 17.17
2017-12-13 12:30 | 96.38 | 17.63
2017-12-13 13:00 | 96.28 | 18.14
2017-12-13 13:30 | 97.24 | 19.31
2017-12-13 14:00 | 98.19 | 22.82
2017-12-13 14:30 | 99.73 | 26.79
2017-12-13 15:00 | 101.04 | 31.06
2017-12-13 15:30 | 101.24 | 33.11
2017-12-13 16:00 | 100.16 | 33.08
2017-12-13 16:30 | 98.92 | 33.25
2017-12-13 17:00 | 97.34 | 35.01
2017-12-13 17:30 | 92.58 | 32.46
2017-12-13 18:00 | 87.73 | 28.82
2017-12-13 18:30 | 67.09 | 28.07
2017-12-13 19:00 | 69.65 | 33.3
2017-12-13 19:30 | 71.57 | 35.03
2017-12-13 20:00 | 70.47 | 35.01
2017-12-13 20:30 | 65.16 | 30.05
2017-12-13 21:00 | 58.12 | 22.67
2017-12-13 21:30 | 38.64 | 16.88
2017-12-13 22:00 | 27.86 | 11.55
2017-12-13 22:30 | 2.1 | 1.13
2017-12-13 23:00 | 3.65 | -3.62
2017-12-13 23:30 | 16.29 | -15.84
2017-12-14 | 31.69 | -31.07
2017-12-14 00:30 | 38.94 | -38.45
2017-12-14 01:00 | 36.3 | -35.85
2017-12-14 01:30 | 33.6 | -33.27
2017-12-14 02:00 | 33.61 | -33.24
2017-12-14 02:30 | 34.03 | -33.57
2017-12-14 03:00 | 33.95 | -33.44
2017-12-14 03:30 | 34.07 | -33.48
2017-12-14 04:00 | 33.94 | -33.14
2017-12-14 04:30 | 33.18 | -32.43
2017-12-14 05:00 | 36.15 | -35.65
2017-12-14 05:30 | 34.74 | -34.37
2017-12-14 06:00 | 25.58 | -24.64
2017-12-14 06:30 | 15.63 | -15.4
2017-12-14 07:00 | 35.54 | -8.6
2017-12-14 07:30 | 43.31 | 3.09
2017-12-14 08:00 | 47.5 | 10.01
2017-12-14 08:30 | 53.22 | 10.99
2017-12-14 09:00 | 59.95 | 15.3
2017-12-14 09:30 | 65.59 | 15.97
2017-12-14 10:00 | 58.79 | 16.63
2017-12-14 10:30 | 59.69 | 19.13
2017-12-14 11:00 | 61.8 | 20.45
2017-12-14 11:30 | 63.2 | 21.6
2017-12-14 12:00 | 64.59 | 24.14
2017-12-14 12:30 | 64.25 | 23.17
2017-12-14 13:00 | 64.54 | 21.36
2017-12-14 13:30 | 65.68 | 21.35
2017-12-14 14:00 | 65.11 | 23.73
2017-12-14 14:30 | 66.83 | 27.97
2017-12-14 15:00 | 68.1 | 32.3
2017-12-14 15:30 | 68.8 | 33.82
2017-12-14 16:00 | 69.62 | 37.11
2017-12-14 16:30 | 69.4 | 39.38
2017-12-14 17:00 | 69.67 | 40.47
2017-12-14 17:30 | 64.92 | 36.87
2017-12-14 18:00 | 59.35 | 33.81
2017-12-14 18:30 | 42.2 | 33.66
2017-12-14 19:00 | 45.23 | 37.41
2017-12-14 19:30 | 49.11 | 40.63
2017-12-14 20:00 | 47.77 | 41.08
2017-12-14 20:30 | 43.46 | 37.09
2017-12-14 21:00 | 46.35 | 29.48
2017-12-14 21:30 | 40.32 | 24.26
2017-12-14 22:00 | 24.93 | 18.27
2017-12-14 22:30 | 9.35 | 7.4
2017-12-14 23:00 | 8.08 | 1.17
2017-12-14 23:30 | 12.17 | -9.65
2017-12-15 | 25.32 | -24.1
2017-12-15 00:30 | 33.76 | -32.64
2017-12-15 01:00 | 33.42 | -31.4
2017-12-15 01:30 | 28.89 | -28.11
2017-12-15 02:00 | 29.3 | -28.66
2017-12-15 02:30 | 29.93 | -29.29
2017-12-15 03:00 | 30.26 | -29.62
2017-12-15 03:30 | 30.61 | -29.97
2017-12-15 04:00 | 31.17 | -30.61
2017-12-15 04:30 | 31.04 | -30.45
2017-12-15 05:00 | 32.55 | -32.12
2017-12-15 05:30 | 31.11 | -30.72
2017-12-15 06:00 | 23.91 | -23.62
2017-12-15 06:30 | 12.13 | -12.08
2017-12-15 07:00 | 11.42 | 3.02
2017-12-15 07:30 | 19.77 | 19.42
2017-12-15 08:00 | 41.23 | 31.41
2017-12-15 08:30 | 46.8 | 33.33
2017-12-15 09:00 | 53.46 | 38.43
2017-12-15 09:30 | 57.28 | 39.79
2017-12-15 10:00 | 61.85 | 43.74
2017-12-15 10:30 | 62.63 | 43.01
2017-12-15 11:00 | 61.61 | 40.76
2017-12-15 11:30 | 62.71 | 41.47
2017-12-15 12:00 | 52.59 | 41.37
2017-12-15 12:30 | 44.57 | 39.38
2017-12-15 13:00 | 44.49 | 39.39
2017-12-15 13:30 | 84.34 | 82.5
2017-12-15 14:00 | 95.95 | 94.29
2017-12-15 14:30 | 100.44 | 98.79
2017-12-15 15:00 | 99.1 | 97.34
2017-12-15 15:30 | 134.59 | 133.29
2017-12-15 16:00 | 151.22 | 150.03
2017-12-15 16:30 | 142.13 | 140.81
2017-12-15 17:00 | 144.96 | 143.85
2017-12-15 17:30 | 142.99 | 142.71
2017-12-15 18:00 | 136.65 | 136.59
2017-12-15 18:30 | 132.34 | 130.44
2017-12-15 19:00 | 135.84 | 132.57
2017-12-15 19:30 | 137.1 | 133.25
2017-12-15 20:00 | 136.06 | 132.63
2017-12-15 20:30 | 128.83 | 128.54
2017-12-15 21:00 | 120.87 | 120.63
2017-12-15 21:30 | 112.89 | 112.69
2017-12-15 22:00 | 100.92 | 100.84
2017-12-15 22:30 | 98.03 | 98
2017-12-15 23:00 | 132.29 | 132.17
2017-12-15 23:30 | 96.38 | 95.96
2017-12-16 | 59.52 | 59.23
2017-12-16 00:30 | 35.88 | 35.35
2017-12-16 01:00 | 7.31 | 1.73
2017-12-16 01:30 | 8.91 | 4.69
2017-12-16 02:00 | 12.34 | -9.89
2017-12-16 02:30 | 18.41 | -16.73
2017-12-16 03:00 | 16.1 | -14.08
2017-12-16 03:30 | 20.14 | -18.69
2017-12-16 04:00 | 21.73 | -20.24
2017-12-16 04:30 | 17.5 | -15.53
2017-12-16 05:00 | 10.43 | -4.17
2017-12-16 05:30 | 13.55 | -8.22
2017-12-16 06:00 | 11.44 | -6.34
2017-12-16 06:30 | 8.94 | -6.9
2017-12-16 07:00 | 8.51 | -5.07
2017-12-16 07:30 | 10.86 | 3.46
2017-12-16 08:00 | 27.98 | 26.51
2017-12-16 08:30 | 28.64 | 28.59
2017-12-16 09:00 | 41.06 | 39.71
2017-12-16 09:30 | 45.93 | 27.68
2017-12-16 10:00 | 39.28 | 3.07
2017-12-16 10:30 | 43.03 | -16.66
2017-12-16 11:00 | 39.81 | -20.74
2017-12-16 11:30 | 33.76 | -5.63
2017-12-16 12:00 | 42.54 | -23.21
2017-12-16 12:30 | 38.54 | -12.98
2017-12-16 13:00 | 41.97 | 25.59
2017-12-16 13:30 | 43.57 | 28.42
2017-12-16 14:00 | 43.81 | 28.9
2017-12-16 14:30 | 43.53 | 27.81
2017-12-16 15:00 | 52.38 | 40.75
2017-12-16 15:30 | 49.5 | 36.97
2017-12-16 16:00 | 54.54 | 43.92
2017-12-16 16:30 | 59.16 | 49.88
2017-12-16 17:00 | 71.13 | 63.79
2017-12-16 17:30 | 82.68 | 77.93
2017-12-16 18:00 | 78.96 | 75.4
2017-12-16 18:30 | 86.47 | 84
2017-12-16 19:00 | 99.98 | 97.17
2017-12-16 19:30 | 113.36 | 110.85
2017-12-16 20:00 | 118.17 | 116.13
2017-12-16 20:30 | 117.9 | 117.65
2017-12-16 21:00 | 92.92 | 92.87
2017-12-16 21:30 | 88.87 | 88.83
2017-12-16 22:00 | 104.08 | 104.08
2017-12-16 22:30 | 128.94 | 128.92
2017-12-16 23:00 | 140.32 | 140.27
2017-12-16 23:30 | 96.03 | 95.83
2017-12-17 | 49.41 | 48.8
2017-12-17 00:30 | 27.64 | 26.77
2017-12-17 01:00 | 18.97 | 17.81
2017-12-17 01:30 | 16.84 | 16.17
2017-12-17 02:00 | 14.4 | 13.74
2017-12-17 02:30 | 13.21 | 12.31
2017-12-17 03:00 | 11.54 | 10.79
2017-12-17 03:30 | 11.85 | 10.81
2017-12-17 04:00 | 11.65 | 10.65
2017-12-17 04:30 | 10.49 | 9.18
2017-12-17 05:00 | 6.5 | 6.04
2017-12-17 05:30 | 6.16 | 5.72
2017-12-17 06:00 | 7.83 | 7.52
2017-12-17 06:30 | 12.55 | 12.25
2017-12-17 07:00 | 14.53 | 14.51
2017-12-17 07:30 | 18.31 | 18.24
2017-12-17 08:00 | 21.85 | 21.16
2017-12-17 08:30 | 30.04 | 29.37
2017-12-17 09:00 | 37.45 | 37.44
2017-12-17 09:30 | 41.18 | 41.17
2017-12-17 10:00 | 45.45 | 45.35
2017-12-17 10:30 | 51.83 | 51.56
2017-12-17 11:00 | 50.74 | 50.32
2017-12-17 11:30 | 51.45 | 51.01
2017-12-17 12:00 | 58.17 | 56.18
2017-12-17 12:30 | 57.4 | 55.1
2017-12-17 13:00 | 64.31 | 61.78
2017-12-17 13:30 | 66.8 | 64.45
2017-12-17 14:00 | 66.38 | 63.96
2017-12-17 14:30 | 69.96 | 67.79
2017-12-17 15:00 | 71.92 | 69.82
2017-12-17 15:30 | 86.22 | 84.92
2017-12-17 16:00 | 97.67 | 96.59
2017-12-17 16:30 | 118.1 | 117.18
2017-12-17 17:00 | 144.6 | 143.63
2017-12-17 17:30 | 152.18 | 151.04
2017-12-17 18:00 | 147.11 | 146.23
2017-12-17 18:30 | 151.13 | 150.2
2017-12-17 19:00 | 159.82 | 158.85
2017-12-17 19:30 | 161.34 | 160.28
2017-12-17 20:00 | 151.03 | 149.92
2017-12-17 20:30 | 134.04 | 132.79
2017-12-17 21:00 | 111.73 | 110.07
2017-12-17 21:30 | 93.47 | 93.46
2017-12-17 22:00 | 80.22 | 79.96
2017-12-17 22:30 | 85.51 | 85.17
2017-12-17 23:00 | 77.45 | 77
2017-12-17 23:30 | 39.72 | 39.25
2017-12-18 | 4.81 | 4.06
2017-12-18 00:30 | 5.03 | -2.12
2017-12-18 01:00 | 9.94 | -8.21
2017-12-18 01:30 | 12.32 | -10.46
2017-12-18 02:00 | 14.67 | -12.87
2017-12-18 02:30 | 15.58 | -13.63
2017-12-18 03:00 | 15.95 | -14.04
2017-12-18 03:30 | 16.71 | -14.86
2017-12-18 04:00 | 17.51 | -16.02
2017-12-18 04:30 | 17.97 | -16.73
2017-12-18 05:00 | 16 | -14.87
2017-12-18 05:30 | 9.8 | -8.33
2017-12-18 06:00 | 60.2 | 59.88
2017-12-18 06:30 | 83.97 | 83.96
2017-12-18 07:00 | 95.89 | 95.57
2017-12-18 07:30 | 107.59 | 107.1
2017-12-18 08:00 | 119.22 | 118.37
2017-12-18 08:30 | 120.33 | 119.02
2017-12-18 09:00 | 128.32 | 124.18
2017-12-18 09:30 | 142.01 | 126.64
2017-12-18 10:00 | 144.65 | 129.27
2017-12-18 10:30 | 142.21 | 126.8
2017-12-18 11:00 | 145.26 | 129.44
2017-12-18 11:30 | 149.25 | 134.06
2017-12-18 12:00 | 149.06 | 134.45
2017-12-18 12:30 | 148.72 | 134.19
2017-12-18 13:00 | 148.63 | 133.83
2017-12-18 13:30 | 150.43 | 134.94
2017-12-18 14:00 | 153.06 | 137.33
2017-12-18 14:30 | 156.13 | 140.61
2017-12-18 15:00 | 150.03 | 135.08
2017-12-18 15:30 | 97.16 | 71.44
2017-12-18 16:00 | 118.2 | 98.79
2017-12-18 16:30 | 107.94 | 86.63
2017-12-18 17:00 | 113.22 | 94.14
2017-12-18 17:30 | 122.13 | 107.82
2017-12-18 18:00 | 78.3 | 62.58
2017-12-18 18:30 | 89.44 | 85.54
2017-12-18 19:00 | 110.75 | 106.69
2017-12-18 19:30 | 118.6 | 114.69
2017-12-18 20:00 | 103.46 | 99.31
2017-12-18 20:30 | 82.71 | 75.67
2017-12-18 21:00 | 84.15 | 71.37
2017-12-18 21:30 | 85.58 | 73.88
2017-12-18 22:00 | 59.39 | 44.24
2017-12-18 22:30 | 56.21 | 43.39
2017-12-18 23:00 | 91.42 | 86.14
2017-12-18 23:30 | 57.16 | 51.83
2017-12-19 | 12.62 | 11.81
2017-12-19 00:30 | 8.95 | -7.35
2017-12-19 01:00 | 16.01 | -15.41
2017-12-19 01:30 | 16.04 | -15.12
2017-12-19 02:00 | 17.23 | -16.33
2017-12-19 02:30 | 17.81 | -16.57
2017-12-19 03:00 | 19.5 | -18.45
2017-12-19 03:30 | 19.54 | -18.33
2017-12-19 04:00 | 20.22 | -19.16
2017-12-19 04:30 | 19.09 | -18.05
2017-12-19 05:00 | 20.88 | -20.17
2017-12-19 05:30 | 20.09 | -19.63
2017-12-19 06:00 | 11.02 | -10.65
2017-12-19 06:30 | 4.14 | -1.55
2017-12-19 07:00 | 21.09 | 19.95
2017-12-19 07:30 | 24.05 | 22.04
2017-12-19 08:00 | 31.61 | 23.4
2017-12-19 08:30 | 44.51 | 27.93
2017-12-19 09:00 | 68.48 | 31.73
2017-12-19 09:30 | 71.21 | 32.43
2017-12-19 10:00 | 75 | 36.75
2017-12-19 10:30 | 75.66 | 38.42
2017-12-19 11:00 | 77.61 | 41.64
2017-12-19 11:30 | 82.63 | 48.35
2017-12-19 12:00 | 84.3 | 50.36
2017-12-19 12:30 | 87.72 | 55.11
2017-12-19 13:00 | 93.94 | 62.61
2017-12-19 13:30 | 87.44 | 55.24
2017-12-19 14:00 | 72.13 | 32.13
2017-12-19 14:30 | 71.94 | 50.69
2017-12-19 15:00 | 74.68 | 53.28
2017-12-19 15:30 | 77.35 | 54.99
2017-12-19 16:00 | 84.97 | 70.26
2017-12-19 16:30 | 89.54 | 85.65
2017-12-19 17:00 | 101.09 | 100.07
2017-12-19 17:30 | 101.99 | 101.32
2017-12-19 18:00 | 97.31 | 96.54
2017-12-19 18:30 | 96.87 | 89.61
2017-12-19 19:00 | 96.15 | 93.69
2017-12-19 19:30 | 100.28 | 98.34
2017-12-19 20:00 | 92.59 | 91.08
2017-12-19 20:30 | 98.57 | 97.98
2017-12-19 21:00 | 96.04 | 95.64
2017-12-19 21:30 | 89.45 | 89.32
2017-12-19 22:00 | 65.79 | 65.35
2017-12-19 22:30 | 79.58 | 78.89
2017-12-19 23:00 | 97.2 | 96.33
2017-12-19 23:30 | 70.41 | 69.57
2017-12-20 | 34.92 | 34.45
2017-12-20 00:30 | 14.06 | 12.14
2017-12-20 01:00 | 9.74 | -5.66
2017-12-20 01:30 | 18.46 | -16.47
2017-12-20 02:00 | 22 | -20.13
2017-12-20 02:30 | 24.38 | -22.45
2017-12-20 03:00 | 33.43 | -32.2
2017-12-20 03:30 | 35.2 | -34.05
2017-12-20 04:00 | 38.92 | -37.94
2017-12-20 04:30 | 35.2 | -34.19
2017-12-20 05:00 | 27.29 | -25.71
2017-12-20 05:30 | 16.97 | -14.76
2017-12-20 06:00 | 6.5 | -0.64
2017-12-20 06:30 | 14.67 | 14.1
2017-12-20 07:00 | 21.82 | 21.15
2017-12-20 07:30 | 18.62 | 12.73
2017-12-20 08:00 | 25.61 | -0.47
2017-12-20 08:30 | 49.77 | 44.5
2017-12-20 09:00 | 63.44 | 59.07
2017-12-20 09:30 | 66.25 | 51.84
2017-12-20 10:00 | 60.69 | 32.63
2017-12-20 10:30 | 71.61 | 49.44
2017-12-20 11:00 | 84.65 | 66.09
2017-12-20 11:30 | 101.05 | 85.67
2017-12-20 12:00 | 120.57 | 108.03
2017-12-20 12:30 | 113.53 | 99.9
2017-12-20 13:00 | 125.15 | 112.17
2017-12-20 13:30 | 102.95 | 85.55
2017-12-20 14:00 | 115 | 102.74
2017-12-20 14:30 | 138.46 | 128.62
2017-12-20 15:00 | 180.51 | 172.8
2017-12-20 15:30 | 218.19 | 211.86
2017-12-20 16:00 | 241.29 | 235.73
2017-12-20 16:30 | 260.79 | 255.99
2017-12-20 17:00 | 283.32 | 278.69
2017-12-20 17:30 | 278.23 | 276.83
2017-12-20 18:00 | 261.66 | 260.9
2017-12-20 18:30 | 253.28 | 251.38
2017-12-20 19:00 | 242.97 | 240.56
2017-12-20 19:30 | 233.29 | 232.57
2017-12-20 20:00 | 238.87 | 238.46
2017-12-20 20:30 | 239.35 | 239.09
2017-12-20 21:00 | 222.58 | 222.5
2017-12-20 21:30 | 192.07 | 191.72
2017-12-20 22:00 | 162.02 | 161.31
2017-12-20 22:30 | 152.81 | 152.81
2017-12-20 23:00 | 173.14 | 173.13
2017-12-20 23:30 | 139.9 | 139.73
2017-12-21 | 82.71 | 82.2
2017-12-21 00:30 | 53.16 | 52.94
2017-12-21 01:00 | 35.21 | 34.52
2017-12-21 01:30 | 42.69 | 41.73
2017-12-21 02:00 | 30.04 | 28.46
2017-12-21 02:30 | 17.2 | 14.21
2017-12-21 03:00 | 10.97 | -5.19
2017-12-21 03:30 | 14.99 | -11.44
2017-12-21 04:00 | 11.04 | -4.49
2017-12-21 04:30 | 11.67 | -6.38
2017-12-21 05:00 | 14.05 | 9.26
2017-12-21 05:30 | 40.02 | 38.55
2017-12-21 06:00 | 71.21 | 70.56
2017-12-21 06:30 | 88.75 | 88.7
2017-12-21 07:00 | 97.29 | 96.68
2017-12-21 07:30 | 109.26 | 108.66
2017-12-21 08:00 | 121.71 | 118.95
2017-12-21 08:30 | 141.13 | 127.83
2017-12-21 09:00 | 152.81 | 138.26
2017-12-21 09:30 | 151.35 | 134.85
2017-12-21 10:00 | 154.88 | 139.71
2017-12-21 10:30 | 153.56 | 145.08
2017-12-21 11:00 | 155.36 | 147.21
2017-12-21 11:30 | 153.5 | 145.67
2017-12-21 12:00 | 153.93 | 145.85
2017-12-21 12:30 | 157.86 | 149.39
2017-12-21 13:00 | 163.56 | 154.57
2017-12-21 13:30 | 158.89 | 149.14
2017-12-21 14:00 | 169.18 | 158.37
2017-12-21 14:30 | 177.03 | 166.78
2017-12-21 15:00 | 170.85 | 162.02
2017-12-21 15:30 | 267.02 | 261.8
2017-12-21 16:00 | 270.29 | 265.44
2017-12-21 16:30 | 269.15 | 267.7
2017-12-21 17:00 | 258.53 | 257.19
2017-12-21 17:30 | 254.71 | 253.84
2017-12-21 18:00 | 233.38 | 232.93
2017-12-21 18:30 | 245.89 | 245.6
2017-12-21 19:00 | 259.7 | 257.56
2017-12-21 19:30 | 248.68 | 247.95
2017-12-21 20:00 | 248.37 | 247.86
2017-12-21 20:30 | 234.93 | 234.62
2017-12-21 21:00 | 206.91 | 206.85
2017-12-21 21:30 | 202.16 | 202.12
2017-12-21 22:00 | 175.35 | 175.12
2017-12-21 22:30 | 189.09 | 188.85
2017-12-21 23:00 | 200.4 | 200.1
2017-12-21 23:30 | 164.93 | 164.74
2017-12-22 | 109.44 | 109.15
2017-12-22 00:30 | 68.84 | 68.67
2017-12-22 01:00 | 35.43 | 34.84
2017-12-22 01:30 | 18.07 | 16.33
2017-12-22 02:00 | 8.28 | 2.23
2017-12-22 02:30 | 8.19 | -0.86
2017-12-22 03:00 | 11.54 | -8.15
2017-12-22 03:30 | 12.39 | -9.1
2017-12-22 04:00 | 13.16 | -9.82
2017-12-22 04:30 | 10.87 | -6.4
2017-12-22 05:00 | 10.89 | -5.03
2017-12-22 05:30 | 11.49 | 7.4
2017-12-22 06:00 | 16.4 | 15.11
2017-12-22 06:30 | 25.95 | 25.69
2017-12-22 07:00 | 38.08 | 37.64
2017-12-22 07:30 | 56.39 | 55.45
2017-12-22 08:00 | 69.58 | 69.33
2017-12-22 08:30 | 81.9 | 81.9
2017-12-22 09:00 | 91.45 | 91.38
2017-12-22 09:30 | 111.89 | 109.68
2017-12-22 10:00 | 123.39 | 112.55
2017-12-22 10:30 | 111.2 | 98.45
2017-12-22 11:00 | 103.67 | 89.23
2017-12-22 11:30 | 108.25 | 93.64
2017-12-22 12:00 | 112.81 | 105.88
2017-12-22 12:30 | 126.46 | 120.22
2017-12-22 13:00 | 123.43 | 116.9
2017-12-22 13:30 | 110.04 | 103.06
2017-12-22 14:00 | 136.12 | 130.07
2017-12-22 14:30 | 169.38 | 163.57
2017-12-22 15:00 | 193.05 | 187.83
2017-12-22 15:30 | 187.24 | 182.67
2017-12-22 16:00 | 194.47 | 190.28
2017-12-22 16:30 | 201.29 | 197.69
2017-12-22 17:00 | 207.28 | 204.2
2017-12-22 17:30 | 206.2 | 204.01
2017-12-22 18:00 | 196.21 | 194.63
2017-12-22 18:30 | 186.9 | 186.82
2017-12-22 19:00 | 201.58 | 201.55
2017-12-22 19:30 | 197.42 | 197.4
2017-12-22 20:00 | 180.91 | 180.91
2017-12-22 20:30 | 158.6 | 158.57
2017-12-22 21:00 | 135.6 | 135.34
2017-12-22 21:30 | 125.15 | 125.04
2017-12-22 22:00 | 121.51 | 121.39
2017-12-22 22:30 | 129.7 | 129.7
2017-12-22 23:00 | 129.62 | 129.56
2017-12-22 23:30 | 102.49 | 102.47
2017-12-23 | 69.54 | 66.86
2017-12-23 00:30 | 51.01 | 47.37
2017-12-23 01:00 | 40.38 | 35.14
2017-12-23 01:30 | 35.63 | 29.95
2017-12-23 02:00 | 29.18 | 22.76
2017-12-23 02:30 | 26.74 | 20.29
2017-12-23 03:00 | 22.59 | 15.21
2017-12-23 03:30 | 19.36 | 8.58
2017-12-23 04:00 | 17.32 | 0.78
2017-12-23 04:30 | 17.97 | 5.83
2017-12-23 05:00 | 13.87 | -0.21
2017-12-23 05:30 | 11.52 | -1.5
2017-12-23 06:00 | 14.81 | -8.24
2017-12-23 06:30 | 16.39 | -6.73
2017-12-23 07:00 | 16.09 | 2.97
2017-12-23 07:30 | 27.13 | 21.72
2017-12-23 08:00 | 41.93 | 41.57
2017-12-23 08:30 | 67.33 | 67.04
2017-12-23 09:00 | 94.43 | 94.32
2017-12-23 09:30 | 86.4 | 86.39
2017-12-23 10:00 | 89.95 | 89.94
2017-12-23 10:30 | 90.24 | 90.21
2017-12-23 11:00 | 90.93 | 90.76
2017-12-23 11:30 | 97.96 | 89.46
2017-12-23 12:00 | 118.4 | 103.77
2017-12-23 12:30 | 118.57 | 104.01
2017-12-23 13:00 | 116.71 | 101.45
2017-12-23 13:30 | 133.4 | 125.19
2017-12-23 14:00 | 129.52 | 124.85
2017-12-23 14:30 | 122.92 | 118.32
2017-12-23 15:00 | 145.49 | 141.45
2017-12-23 15:30 | 135.12 | 130.37
2017-12-23 16:00 | 142.99 | 138.75
2017-12-23 16:30 | 173.91 | 170.39
2017-12-23 17:00 | 185.72 | 182.31
2017-12-23 17:30 | 179.4 | 176.19
2017-12-23 18:00 | 196.93 | 194.41
2017-12-23 18:30 | 218.08 | 216.13
2017-12-23 19:00 | 221.93 | 220.1
2017-12-23 19:30 | 217.57 | 215.46
2017-12-23 20:00 | 227.07 | 225.22
2017-12-23 20:30 | 216.44 | 214.93
2017-12-23 21:00 | 208.55 | 207.71
2017-12-23 21:30 | 210.69 | 210.53
2017-12-23 22:00 | 204.78 | 204.53
2017-12-23 22:30 | 192.8 | 192.42
2017-12-23 23:00 | 188.27 | 188.24
2017-12-23 23:30 | 171.8 | 171.5
2017-12-24 | 153.73 | 153.07
2017-12-24 00:30 | 139.9 | 138.7
2017-12-24 01:00 | 130.19 | 128.89
2017-12-24 01:30 | 122.89 | 121.51
2017-12-24 02:00 | 117.72 | 116.53
2017-12-24 02:30 | 114.63 | 113.6
2017-12-24 03:00 | 112.05 | 111.12
2017-12-24 03:30 | 110.87 | 110.01
2017-12-24 04:00 | 110.29 | 109.24
2017-12-24 04:30 | 110.18 | 109.17
2017-12-24 05:00 | 107.54 | 107.01
2017-12-24 05:30 | 109.28 | 108.86
2017-12-24 06:00 | 115.16 | 113.85
2017-12-24 06:30 | 101.95 | 99.26
2017-12-24 07:00 | 80.51 | 77.13
2017-12-24 07:30 | 92.46 | 90.13
2017-12-24 08:00 | 95.21 | 95.03
2017-12-24 08:30 | 96.35 | 96.13
2017-12-24 09:00 | 103.15 | 103.06
2017-12-24 09:30 | 106.5 | 106.5
2017-12-24 10:00 | 119.47 | 119.44
2017-12-24 10:30 | 118.74 | 118.28
2017-12-24 11:00 | 137.28 | 124.74
2017-12-24 11:30 | 143.61 | 128.46
2017-12-24 12:00 | 146.19 | 131.58
2017-12-24 12:30 | 148.09 | 136.3
2017-12-24 13:00 | 150.39 | 138.4
2017-12-24 13:30 | 153.92 | 141.78
2017-12-24 14:00 | 157.03 | 144.43
2017-12-24 14:30 | 160.1 | 147.52
2017-12-24 15:00 | 227.53 | 218.24
2017-12-24 15:30 | 248.16 | 239.31
2017-12-24 16:00 | 248.53 | 243.18
2017-12-24 16:30 | 249.54 | 248.12
2017-12-24 17:00 | 252.03 | 250.39
2017-12-24 17:30 | 253.35 | 252.01
2017-12-24 18:00 | 250.53 | 249.53
2017-12-24 18:30 | 242.57 | 242.29
2017-12-24 19:00 | 240.44 | 239.25
2017-12-24 19:30 | 243.9 | 241.32
2017-12-24 20:00 | 244.59 | 242.19
2017-12-24 20:30 | 241.73 | 239.35
2017-12-24 21:00 | 230.77 | 228.88
2017-12-24 21:30 | 225.18 | 223.58
2017-12-24 22:00 | 210.3 | 209.13
2017-12-24 22:30 | 204.44 | 203.6
2017-12-24 23:00 | 198.87 | 198.29
2017-12-24 23:30 | 180.29 | 179.85
2017-12-25 | 162.38 | 161.67
2017-12-25 00:30 | 145.13 | 145.13
2017-12-25 01:00 | 133.98 | 133.83
2017-12-25 01:30 | 126.45 | 126.22
2017-12-25 02:00 | 121.31 | 121
2017-12-25 02:30 | 118.25 | 117.91
2017-12-25 03:00 | 115.32 | 114.91
2017-12-25 03:30 | 115.49 | 112.92
2017-12-25 04:00 | 114.86 | 112.19
2017-12-25 04:30 | 116.11 | 113.47
2017-12-25 05:00 | 117.06 | 114.8
2017-12-25 05:30 | 119.91 | 117.96
2017-12-25 06:00 | 126.13 | 124.12
2017-12-25 06:30 | 138.14 | 136.06
2017-12-25 07:00 | 138.81 | 137.3
2017-12-25 07:30 | 84.91 | 84.87
2017-12-25 08:00 | 94.37 | 93.76
2017-12-25 08:30 | 98.05 | 97.78
2017-12-25 09:00 | 103.63 | 103.63
2017-12-25 09:30 | 105.37 | 104.58
2017-12-25 10:00 | 115.65 | 111.94
2017-12-25 10:30 | 118.07 | 113.94
2017-12-25 11:00 | 121.16 | 116.58
2017-12-25 11:30 | 125.12 | 120.19
2017-12-25 12:00 | 126.7 | 121.46
2017-12-25 12:30 | 128.83 | 123.41
2017-12-25 13:00 | 131.47 | 126.42
2017-12-25 13:30 | 133.28 | 128.08
2017-12-25 14:00 | 134.54 | 129.18
2017-12-25 14:30 | 135.13 | 129.8
2017-12-25 15:00 | 213.45 | 209.88
2017-12-25 15:30 | 223.74 | 220.38
2017-12-25 16:00 | 222.7 | 219.92
2017-12-25 16:30 | 222.08 | 221.13
2017-12-25 17:00 | 223.95 | 223.32
2017-12-25 17:30 | 223.25 | 223.14
2017-12-25 18:00 | 221.68 | 219.84
2017-12-25 18:30 | 218.94 | 216.38
2017-12-25 19:00 | 210.81 | 210.45
2017-12-25 19:30 | 204.18 | 203.84
2017-12-25 20:00 | 201.04 | 200.79
2017-12-25 20:30 | 197.73 | 197.31
2017-12-25 21:00 | 189.61 | 189.1
2017-12-25 21:30 | 186.83 | 186.22
2017-12-25 22:00 | 177.83 | 177.14
2017-12-25 22:30 | 178.01 | 177.35
2017-12-25 23:00 | 174.1 | 173.48
2017-12-25 23:30 | 160.21 | 159.78
2017-12-26 | 144.08 | 144.07
2017-12-26 00:30 | 119.27 | 118.95
2017-12-26 01:00 | 20.99 | 20.94
2017-12-26 01:30 | 22.64 | 22.22
2017-12-26 02:00 | 22.16 | 21.96
2017-12-26 02:30 | 21.86 | 21.74
2017-12-26 03:00 | 21 | 20.93
2017-12-26 03:30 | 20 | 19.98
2017-12-26 04:00 | 19 | 18.99
2017-12-26 04:30 | 19.54 | 19.52
2017-12-26 05:00 | 18.7 | 18.63
2017-12-26 05:30 | 18.59 | 18.33
2017-12-26 06:00 | 20.8 | 20.73
2017-12-26 06:30 | 25.39 | 25.31
2017-12-26 07:00 | 30.21 | 29.89
2017-12-26 07:30 | 37.79 | 36.89
2017-12-26 08:00 | 43.26 | 42.23
2017-12-26 08:30 | 51.9 | 50.9
2017-12-26 09:00 | 59.64 | 59.58
2017-12-26 09:30 | 53.68 | 53.62
2017-12-26 10:00 | 54.3 | 54.09
2017-12-26 10:30 | 55.06 | 54.77
2017-12-26 11:00 | 59.63 | 59.24
2017-12-26 11:30 | 70.05 | 69.69
2017-12-26 12:00 | 64.48 | 64.48
2017-12-26 12:30 | 69.28 | 69.27
2017-12-26 13:00 | 73.42 | 73.24
2017-12-26 13:30 | 62.02 | 61.79
2017-12-26 14:00 | 59.91 | 59.7
2017-12-26 14:30 | 65.24 | 65.06
2017-12-26 15:00 | 70.82 | 70.66
2017-12-26 15:30 | 78.74 | 78.54
2017-12-26 16:00 | 196.14 | 196.08
2017-12-26 16:30 | 191.45 | 191.44
2017-12-26 17:00 | 199.36 | 199.29
2017-12-26 17:30 | 201.31 | 201.25
2017-12-26 18:00 | 197.89 | 197.86
2017-12-26 18:30 | 193.98 | 193.95
2017-12-26 19:00 | 196.58 | 196.56
2017-12-26 19:30 | 192.64 | 192.64
2017-12-26 20:00 | 189.25 | 189.25
2017-12-26 20:30 | 182.78 | 182.78
2017-12-26 21:00 | 173.7 | 173.69
2017-12-26 21:30 | 167.08 | 167.06
2017-12-26 22:00 | 156.24 | 156.12
2017-12-26 22:30 | 156.91 | 156.65
2017-12-26 23:00 | 157.47 | 157.11
2017-12-26 23:30 | 143.22 | 142.58
2017-12-27 | 126.53 | 126.18
2017-12-27 00:30 | 117.73 | 117.51
2017-12-27 01:00 | 93.41 | 93.36
2017-12-27 01:30 | 49.88 | 49.88
2017-12-27 02:00 | 50.05 | 49.99
2017-12-27 02:30 | 50.03 | 50.03
2017-12-27 03:00 | 49.79 | 49.79
2017-12-27 03:30 | 48.92 | 48.89
2017-12-27 04:00 | 48.45 | 48.43
2017-12-27 04:30 | 48.1 | 48.07
2017-12-27 05:00 | 47.51 | 47.51
2017-12-27 05:30 | 47.37 | 47.36
2017-12-27 06:00 | 52.48 | 52.46
2017-12-27 06:30 | 59.51 | 59.04
2017-12-27 07:00 | 66.77 | 65.83
2017-12-27 07:30 | 77.23 | 76.3
2017-12-27 08:00 | 85.28 | 85.18
2017-12-27 08:30 | 90.5 | 90.5
2017-12-27 09:00 | 95.57 | 95.13
2017-12-27 09:30 | 102.6 | 102.38
2017-12-27 10:00 | 112.34 | 112.17
2017-12-27 10:30 | 113.44 | 113.23
2017-12-27 11:00 | 106.44 | 106.25
2017-12-27 11:30 | 136.46 | 136.3
2017-12-27 12:00 | 138.73 | 138.64
2017-12-27 12:30 | 146.94 | 146.84
2017-12-27 13:00 | 164.24 | 164.08
2017-12-27 13:30 | 186.39 | 186.34
2017-12-27 14:00 | 196.28 | 196.18
2017-12-27 14:30 | 201.72 | 201.49
2017-12-27 15:00 | 206.37 | 206.22
2017-12-27 15:30 | 213 | 212.87
2017-12-27 16:00 | 207.39 | 207.26
2017-12-27 16:30 | 216.36 | 216.23
2017-12-27 17:00 | 226.47 | 226.36
2017-12-27 17:30 | 219.43 | 219.12
2017-12-27 18:00 | 218.42 | 218.08
2017-12-27 18:30 | 218.37 | 217.99
2017-12-27 19:00 | 217.4 | 217
2017-12-27 19:30 | 216.15 | 215.65
2017-12-27 20:00 | 216.82 | 216.36
2017-12-27 20:30 | 206.76 | 206.61
2017-12-27 21:00 | 202.18 | 202.03
2017-12-27 21:30 | 197.5 | 197.21
2017-12-27 22:00 | 181.61 | 180.91
2017-12-27 22:30 | 181.73 | 180.78
2017-12-27 23:00 | 179.5 | 178.47
2017-12-27 23:30 | 154.79 | 153.43
2017-12-28 | 105.13 | 102.71
2017-12-28 00:30 | 74.4 | 71.39
2017-12-28 01:00 | 55.2 | 51.48
2017-12-28 01:30 | 74.25 | 71.16
2017-12-28 02:00 | 71.17 | 67.39
2017-12-28 02:30 | 63.16 | 59.15
2017-12-28 03:00 | 46.16 | 40.82
2017-12-28 03:30 | 38.23 | 31.97
2017-12-28 04:00 | 28.84 | 20.15
2017-12-28 04:30 | 27.19 | 17.16
2017-12-28 05:00 | 40.76 | 35.76
2017-12-28 05:30 | 47.53 | 43.48
2017-12-28 06:00 | 62.05 | 58.46
2017-12-28 06:30 | 85.2 | 81.98
2017-12-28 07:00 | 105.73 | 103.18
2017-12-28 07:30 | 104.58 | 102.84
2017-12-28 08:00 | 100.97 | 100.04
2017-12-28 08:30 | 114.38 | 113.93
2017-12-28 09:00 | 119.15 | 119.15
2017-12-28 09:30 | 126.27 | 126.21
2017-12-28 10:00 | 125.43 | 125.39
2017-12-28 10:30 | 126.23 | 126.21
2017-12-28 11:00 | 135.68 | 135.52
2017-12-28 11:30 | 143.08 | 142.96
2017-12-28 12:00 | 132.71 | 132.59
2017-12-28 12:30 | 145.28 | 145.21
2017-12-28 13:00 | 123.81 | 123.74
2017-12-28 13:30 | 101.15 | 101.09
2017-12-28 14:00 | 103.4 | 103.37
2017-12-28 14:30 | 101.8 | 101.79
2017-12-28 15:00 | 102.08 | 102.07
2017-12-28 15:30 | 127.46 | 127.46
2017-12-28 16:00 | 131.51 | 131.5
2017-12-28 16:30 | 147.13 | 147.12
2017-12-28 17:00 | 179.82 | 179.81
2017-12-28 17:30 | 212.38 | 212.37
2017-12-28 18:00 | 208.89 | 208.89
2017-12-28 18:30 | 198.92 | 198.87
2017-12-28 19:00 | 218.16 | 218.13
2017-12-28 19:30 | 220.46 | 220.45
2017-12-28 20:00 | 200.55 | 200.5
2017-12-28 20:30 | 212.83 | 212.71
2017-12-28 21:00 | 194.95 | 194.68
2017-12-28 21:30 | 165.45 | 164.65
2017-12-28 22:00 | 136.31 | 134.48
2017-12-28 22:30 | 163.4 | 162.22
2017-12-28 23:00 | 169.33 | 168.56
2017-12-28 23:30 | 136.79 | 136.6
2017-12-29 | 100.5 | 100
2017-12-29 00:30 | 70.64 | 69.54
2017-12-29 01:00 | 39.96 | 37.58
2017-12-29 01:30 | 46.73 | 38.73
2017-12-29 02:00 | 50.18 | 36.54
2017-12-29 02:30 | 53.54 | 41.58
2017-12-29 03:00 | 47.26 | 34.63
2017-12-29 03:30 | 44.84 | 31.52
2017-12-29 04:00 | 45.63 | 32.55
2017-12-29 04:30 | 34.24 | 13.57
2017-12-29 05:00 | 40.4 | 25.57
2017-12-29 05:30 | 51.34 | 40.82
2017-12-29 06:00 | 73.09 | 66
2017-12-29 06:30 | 90.25 | 85.06
2017-12-29 07:00 | 111.05 | 107.56
2017-12-29 07:30 | 101.69 | 100.8
2017-12-29 08:00 | 97.71 | 97.66
2017-12-29 08:30 | 86.71 | 86.62
2017-12-29 09:00 | 91.01 | 90.92
2017-12-29 09:30 | 98.38 | 98.37
2017-12-29 10:00 | 101.6 | 101.59
2017-12-29 10:30 | 109.9 | 109.78
2017-12-29 11:00 | 102.6 | 102.24
2017-12-29 11:30 | 113.29 | 112.88
2017-12-29 12:00 | 109.81 | 108.75
2017-12-29 12:30 | 120.91 | 117.32
2017-12-29 13:00 | 135.06 | 131.85
2017-12-29 13:30 | 138.97 | 131.71
2017-12-29 14:00 | 133.16 | 118.75
2017-12-29 14:30 | 133.29 | 118.5
2017-12-29 15:00 | 136.24 | 119.77
2017-12-29 15:30 | 147.05 | 132.07
2017-12-29 16:00 | 165.76 | 158.88
2017-12-29 16:30 | 191.49 | 189.25
2017-12-29 17:00 | 215.98 | 214.31
2017-12-29 17:30 | 242.92 | 241.48
2017-12-29 18:00 | 234.21 | 233.2
2017-12-29 18:30 | 241.29 | 241.29
2017-12-29 19:00 | 234.41 | 234.41
2017-12-29 19:30 | 230.88 | 230.87
2017-12-29 20:00 | 237.42 | 237.18
2017-12-29 20:30 | 240.41 | 235.86
2017-12-29 21:00 | 229.81 | 222.37
2017-12-29 21:30 | 229.61 | 221.81
2017-12-29 22:00 | 219.26 | 212.06
2017-12-29 22:30 | 212.93 | 206.25
2017-12-29 23:00 | 201.6 | 199.53
2017-12-29 23:30 | 166.3 | 165.5
2017-12-30 | 117.45 | 116.69
2017-12-30 00:30 | 120.54 | 120.07
2017-12-30 01:00 | 100.48 | 100.11
2017-12-30 01:30 | 99.61 | 99.36
2017-12-30 02:00 | 110.27 | 110.1
2017-12-30 02:30 | 108.67 | 108.52
2017-12-30 03:00 | 94.3 | 94.15
2017-12-30 03:30 | 84.65 | 84.48
2017-12-30 04:00 | 77.61 | 77.43
2017-12-30 04:30 | 93.77 | 93.66
2017-12-30 05:00 | 101.21 | 101.12
2017-12-30 05:30 | 109.77 | 109.69
2017-12-30 06:00 | 100.19 | 100.07
2017-12-30 06:30 | 97.12 | 96.88
2017-12-30 07:00 | 108.81 | 108.27
2017-12-30 07:30 | 110.58 | 109.25
2017-12-30 08:00 | 127.59 | 125.42
2017-12-30 08:30 | 170.41 | 153.88
2017-12-30 09:00 | 205.46 | 186.99
2017-12-30 09:30 | 214.14 | 196.23
2017-12-30 10:00 | 206.75 | 187.5
2017-12-30 10:30 | 219.45 | 200.51
2017-12-30 11:00 | 228.87 | 209.88
2017-12-30 11:30 | 226.97 | 207.56
2017-12-30 12:00 | 220.81 | 201.01
2017-12-30 12:30 | 222.48 | 202.53
2017-12-30 13:00 | 238.94 | 224.13
2017-12-30 13:30 | 237.33 | 228.9
2017-12-30 14:00 | 237.62 | 232.54
2017-12-30 14:30 | 217.5 | 214.97
2017-12-30 15:00 | 226.13 | 224.96
2017-12-30 15:30 | 228.69 | 227.7
2017-12-30 16:00 | 245.24 | 244.07
2017-12-30 16:30 | 255.63 | 252.4
2017-12-30 17:00 | 263.6 | 259.3
2017-12-30 17:30 | 262.47 | 258.47
2017-12-30 18:00 | 262.75 | 259.1
2017-12-30 18:30 | 260.79 | 257.4
2017-12-30 19:00 | 263.36 | 259.37
2017-12-30 19:30 | 263.23 | 258.99
2017-12-30 20:00 | 264.48 | 260.62
2017-12-30 20:30 | 260.29 | 257.13
2017-12-30 21:00 | 247.25 | 244.87
2017-12-30 21:30 | 239.54 | 237.63
2017-12-30 22:00 | 215.69 | 215.03
2017-12-30 22:30 | 208.26 | 208.24
2017-12-30 23:00 | 202.73 | 202.73
2017-12-30 23:30 | 157.12 | 157.12
2017-12-31 | 118.9 | 118.8
2017-12-31 00:30 | 121.92 | 121.43
2017-12-31 01:00 | 95.24 | 94.54
2017-12-31 01:30 | 86.96 | 83.28
2017-12-31 02:00 | 81.88 | 77.67
2017-12-31 02:30 | 71.95 | 66.93
2017-12-31 03:00 | 75.51 | 70.55
2017-12-31 03:30 | 72.59 | 66.9
2017-12-31 04:00 | 51.62 | 44.25
2017-12-31 04:30 | 65.37 | 60.08
2017-12-31 05:00 | 63.42 | 58.18
2017-12-31 05:30 | 46.54 | 40.83
2017-12-31 06:00 | 29.36 | 20.35
2017-12-31 06:30 | 43.48 | 36.79
2017-12-31 07:00 | 55.76 | 51.3
2017-12-31 07:30 | 74.24 | 71.85
2017-12-31 08:00 | 86.96 | 86.16
2017-12-31 08:30 | 115.86 | 115.41
2017-12-31 09:00 | 139.17 | 138.72
2017-12-31 09:30 | 154.56 | 154.42
2017-12-31 10:00 | 178.48 | 178.47
2017-12-31 10:30 | 209.26 | 209.07
2017-12-31 11:00 | 210.44 | 210.12
2017-12-31 11:30 | 206.63 | 206.28
2017-12-31 12:00 | 207.53 | 207
2017-12-31 12:30 | 220.9 | 220.11
2017-12-31 13:00 | 226.84 | 225.71
2017-12-31 13:30 | 232.66 | 231.49
2017-12-31 14:00 | 237.36 | 236.17
2017-12-31 14:30 | 243.62 | 242.32
2017-12-31 15:00 | 253.69 | 252.26
2017-12-31 15:30 | 249.11 | 247.8
2017-12-31 16:00 | 235.91 | 234.81
2017-12-31 16:30 | 214.56 | 213.88
2017-12-31 17:00 | 244.24 | 243.63
2017-12-31 17:30 | 238.81 | 237.57
2017-12-31 18:00 | 231.55 | 231.34
2017-12-31 18:30 | 232.41 | 232.28
2017-12-31 19:00 | 231.77 | 231.64
2017-12-31 19:30 | 228.42 | 228.35
2017-12-31 20:00 | 226.85 | 226.81
2017-12-31 20:30 | 207.52 | 207.52
2017-12-31 21:00 | 172.99 | 172.97
2017-12-31 21:30 | 155.9 | 155.82
2017-12-31 22:00 | 130.15 | 129.92
2017-12-31 22:30 | 137.88 | 137.68
2017-12-31 23:00 | 135.28 | 134.99
2017-12-31 23:30 | 94.41 | 94.1
2018-01-01 | 58.85 | 58.7
2018-01-01 00:30 | 26.5 | 25.88
2018-01-01 01:00 | 18.57 | 17.37
2018-01-01 01:30 | 16.19 | 15.81
2018-01-01 02:00 | 29.96 | 29.8
2018-01-01 02:30 | 40.48 | 40.19
2018-01-01 03:00 | 33.97 | 33.5
2018-01-01 03:30 | 28.02 | 27.35
2018-01-01 04:00 | 18.54 | 17.4
2018-01-01 04:30 | 11.81 | 10.08
2018-01-01 05:00 | 6.55 | -1.04
2018-01-01 05:30 | 9.11 | -5.19
2018-01-01 06:00 | 18.7 | -17.79
2018-01-01 06:30 | 11.33 | -10.64
2018-01-01 07:00 | 10.21 | -10.2
2018-01-01 07:30 | 23.61 | 10.62
2018-01-01 08:00 | 43.46 | 13.97
2018-01-01 08:30 | 55.93 | 32.34
2018-01-01 09:00 | 60.55 | 40.37
2018-01-01 09:30 | 63.98 | 57.08
2018-01-01 10:00 | 72.33 | 63.94
2018-01-01 10:30 | 85.85 | 78.38
2018-01-01 11:00 | 132.43 | 128.18
2018-01-01 11:30 | 144.73 | 140.53
2018-01-01 12:00 | 148.83 | 144.44
2018-01-01 12:30 | 148.1 | 143.48
2018-01-01 13:00 | 180.93 | 176.76
2018-01-01 13:30 | 193.78 | 189.67
2018-01-01 14:00 | 198.37 | 194.37
2018-01-01 14:30 | 195.82 | 191.79
2018-01-01 15:00 | 220.18 | 215.9
2018-01-01 15:30 | 195.12 | 190.69
2018-01-01 16:00 | 216.68 | 212.45
2018-01-01 16:30 | 246.9 | 243.2
2018-01-01 17:00 | 263.96 | 262.63
2018-01-01 17:30 | 264.16 | 263.12
2018-01-01 18:00 | 253.57 | 252.6
2018-01-01 18:30 | 250.7 | 249.91
2018-01-01 19:00 | 253.79 | 253.06
2018-01-01 19:30 | 249.85 | 248.98
2018-01-01 20:00 | 251.64 | 250.5
2018-01-01 20:30 | 242.26 | 241.7
2018-01-01 21:00 | 216.08 | 215.86
2018-01-01 21:30 | 212.04 | 212.01
2018-01-01 22:00 | 175.2 | 175.13
2018-01-01 22:30 | 187.36 | 187.23
2018-01-01 23:00 | 190.01 | 189.78
2018-01-01 23:30 | 168.85 | 168.85
2018-01-02 | 112.57 | 110.8
2018-01-02 00:30 | 87.05 | 83.83
2018-01-02 01:00 | 69.45 | 63.99
2018-01-02 01:30 | 51.75 | 44.45
2018-01-02 02:00 | 49.63 | 42.32
2018-01-02 02:30 | 47.77 | 40.67
2018-01-02 03:00 | 43.11 | 35.25
2018-01-02 03:30 | 42.68 | 34.89
2018-01-02 04:00 | 38.06 | 29.38
2018-01-02 04:30 | 44.84 | 37.78
2018-01-02 05:00 | 55.05 | 49.74
2018-01-02 05:30 | 63.19 | 58.86
2018-01-02 06:00 | 71.21 | 67
2018-01-02 06:30 | 94.93 | 91.84
2018-01-02 07:00 | 121.43 | 119.95
2018-01-02 07:30 | 101.43 | 101.07
2018-01-02 08:00 | 110.75 | 110.71
2018-01-02 08:30 | 140.02 | 139.8
2018-01-02 09:00 | 164.57 | 164.46
2018-01-02 09:30 | 179.76 | 179.54
2018-01-02 10:00 | 209.17 | 208.2
2018-01-02 10:30 | 224.74 | 223.47
2018-01-02 11:00 | 240.16 | 238.85
2018-01-02 11:30 | 233.88 | 232.46
2018-01-02 12:00 | 227.89 | 226.05
2018-01-02 12:30 | 240.54 | 238.24
2018-01-02 13:00 | 238.53 | 236.17
2018-01-02 13:30 | 259.99 | 257.92
2018-01-02 14:00 | 270.43 | 268.6
2018-01-02 14:30 | 282.52 | 280.75
2018-01-02 15:00 | 271.84 | 270.02
2018-01-02 15:30 | 260.02 | 258.83
2018-01-02 16:00 | 249.25 | 248.28
2018-01-02 16:30 | 249.89 | 244.88
2018-01-02 17:00 | 252.69 | 246.5
2018-01-02 17:30 | 245.97 | 239.22
2018-01-02 18:00 | 243.71 | 236.4
2018-01-02 18:30 | 237.1 | 229.97
2018-01-02 19:00 | 234.4 | 226.71
2018-01-02 19:30 | 236.14 | 233.32
2018-01-02 20:00 | 213.13 | 213.13
2018-01-02 20:30 | 195.89 | 195.85
2018-01-02 21:00 | 183.96 | 183.91
2018-01-02 21:30 | 176.55 | 176.54
2018-01-02 22:00 | 152.65 | 152.58
2018-01-02 22:30 | 155.43 | 155.29
2018-01-02 23:00 | 176.03 | 175.84
2018-01-02 23:30 | 152.25 | 151.84
2018-01-03 | 98.89 | 98.33
2018-01-03 00:30 | 75.81 | 75.61
2018-01-03 01:00 | 51.71 | 51.34
2018-01-03 01:30 | 42.32 | 41.79
2018-01-03 02:00 | 38.65 | 37.99
2018-01-03 02:30 | 35.37 | 34.52
2018-01-03 03:00 | 25.89 | 24.86
2018-01-03 03:30 | 25.95 | 24.56
2018-01-03 04:00 | 26.82 | 25.28
2018-01-03 04:30 | 33.43 | 32.09
2018-01-03 05:00 | 35.12 | 33.93
2018-01-03 05:30 | 35.98 | 34.74
2018-01-03 06:00 | 47.56 | 46.85
2018-01-03 06:30 | 72.36 | 72.25
2018-01-03 07:00 | 82.61 | 82.6
2018-01-03 07:30 | 80.61 | 80.48
2018-01-03 08:00 | 89.56 | 89.34
2018-01-03 08:30 | 100.75 | 100.74
2018-01-03 09:00 | 110.17 | 110.12
2018-01-03 09:30 | 121.26 | 121.11
2018-01-03 10:00 | 123.15 | 121.19
2018-01-03 10:30 | 135.04 | 133.87
2018-01-03 11:00 | 136.46 | 135.41
2018-01-03 11:30 | 143.65 | 142.7
2018-01-03 12:00 | 160.94 | 160.12
2018-01-03 12:30 | 172.94 | 172.11
2018-01-03 13:00 | 193.58 | 192.81
2018-01-03 13:30 | 217.64 | 216.76
2018-01-03 14:00 | 234.57 | 233.45
2018-01-03 14:30 | 243.78 | 242.43
2018-01-03 15:00 | 242.57 | 241.56
2018-01-03 15:30 | 237.23 | 236.32
2018-01-03 16:00 | 210.67 | 209.67
2018-01-03 16:30 | 208.4 | 207.25
2018-01-03 17:00 | 221 | 219.81
2018-01-03 17:30 | 234.54 | 233.21
2018-01-03 18:00 | 232.9 | 231.78
2018-01-03 18:30 | 218.36 | 218.14
2018-01-03 19:00 | 234.78 | 234.78
2018-01-03 19:30 | 238.48 | 238.47
2018-01-03 20:00 | 237.1 | 237.1
2018-01-03 20:30 | 217.26 | 217.26
2018-01-03 21:00 | 209.82 | 209.78
2018-01-03 21:30 | 197.22 | 197.1
2018-01-03 22:00 | 166.06 | 165.72
2018-01-03 22:30 | 171.05 | 170.55
2018-01-03 23:00 | 182.49 | 182.45
2018-01-03 23:30 | 140.8 | 140.38
2018-01-04 | 91.49 | 89.15
2018-01-04 00:30 | 74.28 | 70.38
2018-01-04 01:00 | 56.95 | 51.82
2018-01-04 01:30 | 43.7 | 37.21
2018-01-04 02:00 | 35.94 | 28.12
2018-01-04 02:30 | 41.19 | 34.78
2018-01-04 03:00 | 61.1 | 57.04
2018-01-04 03:30 | 32.59 | 24.62
2018-01-04 04:00 | 23.83 | 11.78
2018-01-04 04:30 | 27.63 | 17.61
2018-01-04 05:00 | 29.11 | 20.92
2018-01-04 05:30 | 32.51 | 25.68
2018-01-04 06:00 | 40.79 | 34.51
2018-01-04 06:30 | 49.95 | 44.88
2018-01-04 07:00 | 65.73 | 62.74
2018-01-04 07:30 | 70.11 | 69.23
2018-01-04 08:00 | 75.37 | 75.25
2018-01-04 08:30 | 75.44 | 75.44
2018-01-04 09:00 | 85.17 | 85.17
2018-01-04 09:30 | 91.82 | 91.81
2018-01-04 10:00 | 100.75 | 100.72
2018-01-04 10:30 | 115.68 | 115.63
2018-01-04 11:00 | 112.71 | 112.63
2018-01-04 11:30 | 138 | 137.92
2018-01-04 12:00 | 144.63 | 144.55
2018-01-04 12:30 | 154.6 | 154.52
2018-01-04 13:00 | 168.66 | 168.58
2018-01-04 13:30 | 171.19 | 171.1
2018-01-04 14:00 | 166.35 | 166.27
2018-01-04 14:30 | 174.03 | 173.96
2018-01-04 15:00 | 187.04 | 186.97
2018-01-04 15:30 | 182.19 | 182.14
2018-01-04 16:00 | 186.11 | 186.06
2018-01-04 16:30 | 208.38 | 208.33
2018-01-04 17:00 | 224.05 | 224.03
2018-01-04 17:30 | 224.72 | 224.66
2018-01-04 18:00 | 231.76 | 231.75
2018-01-04 18:30 | 227.66 | 227.65
2018-01-04 19:00 | 212.66 | 212.42
2018-01-04 19:30 | 218.62 | 218.59
2018-01-04 20:00 | 232.37 | 232.37
2018-01-04 20:30 | 224.66 | 224.64
2018-01-04 21:00 | 213.14 | 213.06
2018-01-04 21:30 | 198.31 | 198.31
2018-01-04 22:00 | 185.12 | 184.36
2018-01-04 22:30 | 181.01 | 180.11
2018-01-04 23:00 | 173.05 | 172.59
2018-01-04 23:30 | 164.48 | 163.42
2018-01-05 | 141.06 | 139.24
2018-01-05 00:30 | 107.9 | 105.29
2018-01-05 01:00 | 90.73 | 87.5
2018-01-05 01:30 | 77.6 | 73.69
2018-01-05 02:00 | 78.15 | 74.34
2018-01-05 02:30 | 70.81 | 66.79
2018-01-05 03:00 | 75.72 | 72.15
2018-01-05 03:30 | 64.81 | 60.6
2018-01-05 04:00 | 59.66 | 55.15
2018-01-05 04:30 | 63.66 | 59.55
2018-01-05 05:00 | 61.47 | 57.68
2018-01-05 05:30 | 63.54 | 59.88
2018-01-05 06:00 | 68.36 | 64.8
2018-01-05 06:30 | 86.22 | 83.35
2018-01-05 07:00 | 94.72 | 94.42
2018-01-05 07:30 | 112.91 | 112.88
2018-01-05 08:00 | 124.38 | 124.3
2018-01-05 08:30 | 121.56 | 121.12
2018-01-05 09:00 | 131.41 | 130.16
2018-01-05 09:30 | 140.02 | 138.86
2018-01-05 10:00 | 160.89 | 158.51
2018-01-05 10:30 | 154.11 | 151.05
2018-01-05 11:00 | 152.34 | 149.04
2018-01-05 11:30 | 156.71 | 153.46
2018-01-05 12:00 | 146.84 | 143.23
2018-01-05 12:30 | 145.22 | 141.34
2018-01-05 13:00 | 154.17 | 150.39
2018-01-05 13:30 | 160.08 | 156.27
2018-01-05 14:00 | 161.6 | 157.52
2018-01-05 14:30 | 167.15 | 163.05
2018-01-05 15:00 | 174.09 | 170.13
2018-01-05 15:30 | 174.65 | 170.87
2018-01-05 16:00 | 163.36 | 159.51
2018-01-05 16:30 | 178.04 | 174.67
2018-01-05 17:00 | 187.38 | 184.61
2018-01-05 17:30 | 187.01 | 184.97
2018-01-05 18:00 | 175.62 | 174.86
2018-01-05 18:30 | 180.03 | 179.89
2018-01-05 19:00 | 202.01 | 201.94
2018-01-05 19:30 | 213.71 | 213.67
2018-01-05 20:00 | 210.96 | 210.9
2018-01-05 20:30 | 191.49 | 191.36
2018-01-05 21:00 | 149.48 | 149.22
2018-01-05 21:30 | 146.4 | 146
2018-01-05 22:00 | 159.29 | 158.78
2018-01-05 22:30 | 166.22 | 165.62
2018-01-05 23:00 | 186.65 | 186.07
2018-01-05 23:30 | 143.75 | 142.72
2018-01-06 | 97.6 | 96.78
2018-01-06 00:30 | 70.45 | 70.09
2018-01-06 01:00 | 44.54 | 43.82
2018-01-06 01:30 | 34.6 | 33.58
2018-01-06 02:00 | 33.34 | 32.23
2018-01-06 02:30 | 37.22 | 36.15
2018-01-06 03:00 | 44.17 | 43.29
2018-01-06 03:30 | 52.6 | 51.82
2018-01-06 04:00 | 46.64 | 45.75
2018-01-06 04:30 | 51.26 | 50.4
2018-01-06 05:00 | 43.77 | 42.42
2018-01-06 05:30 | 39.94 | 38.61
2018-01-06 06:00 | 11.53 | 7.15
2018-01-06 06:30 | 7.32 | 1.98
2018-01-06 07:00 | 12.52 | 11.76
2018-01-06 07:30 | 23.87 | 23.17
2018-01-06 08:00 | 27.17 | 23.84
2018-01-06 08:30 | 46.84 | 46.03
2018-01-06 09:00 | 65.79 | 65.66
2018-01-06 09:30 | 74.01 | 73.99
2018-01-06 10:00 | 50.94 | 50.09
2018-01-06 10:30 | 71.76 | 67.6
2018-01-06 11:00 | 104.34 | 101.44
2018-01-06 11:30 | 93.2 | 90.37
2018-01-06 12:00 | 98.88 | 96.2
2018-01-06 12:30 | 78.87 | 75.25
2018-01-06 13:00 | 73.9 | 62.89
2018-01-06 13:30 | 96.94 | 77.97
2018-01-06 14:00 | 104.42 | 92.75
2018-01-06 14:30 | 127.76 | 124.11
2018-01-06 15:00 | 141.55 | 138.18
2018-01-06 15:30 | 125.52 | 121.4
2018-01-06 16:00 | 125.94 | 121.84
2018-01-06 16:30 | 158.41 | 155.08
2018-01-06 17:00 | 192.53 | 189.62
2018-01-06 17:30 | 206.41 | 203.87
2018-01-06 18:00 | 198.63 | 196.42
2018-01-06 18:30 | 192.09 | 190.45
2018-01-06 19:00 | 202.33 | 201
2018-01-06 19:30 | 205.08 | 203.55
2018-01-06 20:00 | 208.19 | 205.69
2018-01-06 20:30 | 199.93 | 197.64
2018-01-06 21:00 | 170.15 | 168.19
2018-01-06 21:30 | 145.27 | 143.06
2018-01-06 22:00 | 136.93 | 134.84
2018-01-06 22:30 | 152.42 | 150.86
2018-01-06 23:00 | 162.68 | 161.53
2018-01-06 23:30 | 139.68 | 138.57
2018-01-07 | 95.64 | 94.67
2018-01-07 00:30 | 58.98 | 57.87
2018-01-07 01:00 | 32.47 | 30.6
2018-01-07 01:30 | 18.77 | 14.91
2018-01-07 02:00 | 18.27 | 14.56
2018-01-07 02:30 | 7.45 | 4.76
2018-01-07 03:00 | 8.56 | 1.11
2018-01-07 03:30 | 8.95 | -1.77
2018-01-07 04:00 | 9.11 | -1.51
2018-01-07 04:30 | 9.53 | -1.78
2018-01-07 05:00 | 9.41 | 3.68
2018-01-07 05:30 | 11.77 | -8.45
2018-01-07 06:00 | 14 | -11.89
2018-01-07 06:30 | 18.96 | -17.52
2018-01-07 07:00 | 11.37 | -10.22
2018-01-07 07:30 | 5.99 | -5.7
2018-01-07 08:00 | 3.96 | -0.91
2018-01-07 08:30 | 29.03 | 8.46
2018-01-07 09:00 | 57.65 | 16.66
2018-01-07 09:30 | 70.95 | 25.54
2018-01-07 10:00 | 70.05 | 10.82
2018-01-07 10:30 | 68.41 | -1.37
2018-01-07 11:00 | 51.44 | -0.09
2018-01-07 11:30 | 51.85 | 17.24
2018-01-07 12:00 | 54 | 20.05
2018-01-07 12:30 | 57.2 | 26.65
2018-01-07 13:00 | 81.32 | 71.1
2018-01-07 13:30 | 110.25 | 105.17
2018-01-07 14:00 | 151.41 | 147.46
2018-01-07 14:30 | 109.63 | 103.47
2018-01-07 15:00 | 81.38 | 71.45
2018-01-07 15:30 | 96.62 | 87.8
2018-01-07 16:00 | 115.77 | 108.26
2018-01-07 16:30 | 118.39 | 111.37
2018-01-07 17:00 | 131.26 | 124.81
2018-01-07 17:30 | 146.54 | 134.34
2018-01-07 18:00 | 155.46 | 143.95
2018-01-07 18:30 | 165.51 | 155.87
2018-01-07 19:00 | 168.68 | 159.86
2018-01-07 19:30 | 176.88 | 167.94
2018-01-07 20:00 | 179.44 | 171.2
2018-01-07 20:30 | 171.28 | 166.87
2018-01-07 21:00 | 169.06 | 167.09
2018-01-07 21:30 | 154.49 | 154.15
2018-01-07 22:00 | 131.69 | 131.69
2018-01-07 22:30 | 125.02 | 125.01
2018-01-07 23:00 | 141.83 | 141.75
2018-01-07 23:30 | 124.39 | 124.13
2018-01-08 | 81.2 | 80.5
2018-01-08 00:30 | 37.85 | 35.58
2018-01-08 01:00 | 21.18 | 16.15
2018-01-08 01:30 | 17.32 | 13.28
2018-01-08 02:00 | 13.53 | 10.81
2018-01-08 02:30 | 11.1 | 7.3
2018-01-08 03:00 | 8.01 | -0.52
2018-01-08 03:30 | 8.39 | 1.96
2018-01-08 04:00 | 8.19 | -0.75
2018-01-08 04:30 | 9.3 | 4.96
2018-01-08 05:00 | 12.14 | 9.22
2018-01-08 05:30 | 23.06 | 21.75
2018-01-08 06:00 | 36.96 | 36.49
2018-01-08 06:30 | 51.31 | 51.29
2018-01-08 07:00 | 59.12 | 58.7
2018-01-08 07:30 | 50.96 | 50.62
2018-01-08 08:00 | 45.02 | 44.69
2018-01-08 08:30 | 66.46 | 63.17
2018-01-08 09:00 | 102.22 | 82.83
2018-01-08 09:30 | 109.95 | 90.54
2018-01-08 10:00 | 110.25 | 88.18
2018-01-08 10:30 | 115.96 | 94.04
2018-01-08 11:00 | 113.83 | 91.85
2018-01-08 11:30 | 119.92 | 102.09
2018-01-08 12:00 | 105.11 | 94.4
2018-01-08 12:30 | 90.01 | 83.98
2018-01-08 13:00 | 94.25 | 87.64
2018-01-08 13:30 | 95.15 | 88.24
2018-01-08 14:00 | 110.87 | 104.19
2018-01-08 14:30 | 135.71 | 129.91
2018-01-08 15:00 | 136.75 | 130.73
2018-01-08 15:30 | 158.37 | 152.81
2018-01-08 16:00 | 167.21 | 162.14
2018-01-08 16:30 | 186.11 | 181.59
2018-01-08 17:00 | 208.96 | 205.04
2018-01-08 17:30 | 206.99 | 203.83
2018-01-08 18:00 | 195.67 | 193.39
2018-01-08 18:30 | 193.98 | 192.5
2018-01-08 19:00 | 197.19 | 195.94
2018-01-08 19:30 | 199.77 | 198.32
2018-01-08 20:00 | 204.75 | 203.78
2018-01-08 20:30 | 216.66 | 216.14
2018-01-08 21:00 | 199.23 | 197.77
2018-01-08 21:30 | 178.54 | 178.4
2018-01-08 22:00 | 146.99 | 146.57
2018-01-08 22:30 | 156.38 | 155.2
2018-01-08 23:00 | 169.25 | 168.5
2018-01-08 23:30 | 137.92 | 137.31
2018-01-09 | 87.04 | 86.41
2018-01-09 00:30 | 56.66 | 56.12
2018-01-09 01:00 | 39.83 | 39.34
2018-01-09 01:30 | 34.86 | 34.49
2018-01-09 02:00 | 29.45 | 28.98
2018-01-09 02:30 | 45.74 | 42.68
2018-01-09 03:00 | 44.26 | 40.99
2018-01-09 03:30 | 48.04 | 44.98
2018-01-09 04:00 | 47.01 | 43.63
2018-01-09 04:30 | 50.63 | 47.71
2018-01-09 05:00 | 53.43 | 50.86
2018-01-09 05:30 | 65.74 | 63.77
2018-01-09 06:00 | 105.18 | 104.32
2018-01-09 06:30 | 124.29 | 124.24
2018-01-09 07:00 | 140.16 | 139.64
2018-01-09 07:30 | 165.1 | 154.87
2018-01-09 08:00 | 180.16 | 164.08
2018-01-09 08:30 | 187.54 | 169.29
2018-01-09 09:00 | 196.06 | 175.95
2018-01-09 09:30 | 198.44 | 178.15
2018-01-09 10:00 | 201.85 | 182.38
2018-01-09 10:30 | 196.55 | 183
2018-01-09 11:00 | 199.96 | 186.01
2018-01-09 11:30 | 200.25 | 185.51
2018-01-09 12:00 | 212.89 | 190.57
2018-01-09 12:30 | 217.02 | 194.07
2018-01-09 13:00 | 219.98 | 197.31
2018-01-09 13:30 | 209.45 | 199.77
2018-01-09 14:00 | 206.2 | 200.7
2018-01-09 14:30 | 219.82 | 215.28
2018-01-09 15:00 | 258.53 | 255.14
2018-01-09 15:30 | 269.22 | 265.83
2018-01-09 16:00 | 253.48 | 250.22
2018-01-09 16:30 | 245.77 | 242.61
2018-01-09 17:00 | 251.92 | 249.15
2018-01-09 17:30 | 263.03 | 260.9
2018-01-09 18:00 | 250.98 | 249.57
2018-01-09 18:30 | 261.02 | 260.21
2018-01-09 19:00 | 270.72 | 269.82
2018-01-09 19:30 | 262.33 | 261
2018-01-09 20:00 | 258.95 | 257.71
2018-01-09 20:30 | 246.35 | 245.45
2018-01-09 21:00 | 233.96 | 233.57
2018-01-09 21:30 | 197.42 | 197.36
2018-01-09 22:00 | 153.24 | 153.04
2018-01-09 22:30 | 170.37 | 170.37
2018-01-09 23:00 | 184.74 | 184.73
2018-01-09 23:30 | 143.06 | 142.86
2018-01-10 | 112.09 | 111.57
2018-01-10 00:30 | 86.14 | 85.92
2018-01-10 01:00 | 70.62 | 70.37
2018-01-10 01:30 | 58.17 | 57.77
2018-01-10 02:00 | 58.01 | 57.56
2018-01-10 02:30 | 56.7 | 56.13
2018-01-10 03:00 | 43.24 | 42.48
2018-01-10 03:30 | 39.56 | 38.75
2018-01-10 04:00 | 45.54 | 44.74
2018-01-10 04:30 | 49.95 | 49.32
2018-01-10 05:00 | 59.6 | 59.11
2018-01-10 05:30 | 63.78 | 63.41
2018-01-10 06:00 | 82.45 | 82.29
2018-01-10 06:30 | 84.11 | 84.03
2018-01-10 07:00 | 100.22 | 99.65
2018-01-10 07:30 | 92.99 | 92.95
2018-01-10 08:00 | 102.65 | 102.45
2018-01-10 08:30 | 116.84 | 116.61
2018-01-10 09:00 | 146.75 | 145.2
2018-01-10 09:30 | 159.42 | 152.59
2018-01-10 10:00 | 150.44 | 142.66
2018-01-10 10:30 | 163.27 | 155.66
2018-01-10 11:00 | 170.47 | 162.94
2018-01-10 11:30 | 163.09 | 155.45
2018-01-10 12:00 | 171.27 | 163.33
2018-01-10 12:30 | 181.53 | 178.48
2018-01-10 13:00 | 195.69 | 192.82
2018-01-10 13:30 | 208.56 | 205.64
2018-01-10 14:00 | 231.35 | 228.36
2018-01-10 14:30 | 247.3 | 244.22
2018-01-10 15:00 | 253.55 | 250.42
2018-01-10 15:30 | 270.59 | 267.3
2018-01-10 16:00 | 272.73 | 269.06
2018-01-10 16:30 | 281.74 | 278.44
2018-01-10 17:00 | 284.55 | 281.21
2018-01-10 17:30 | 287.1 | 284.39
2018-01-10 18:00 | 282.62 | 280.68
2018-01-10 18:30 | 270.13 | 268.94
2018-01-10 19:00 | 269.78 | 268.65
2018-01-10 19:30 | 270.83 | 269.63
2018-01-10 20:00 | 263.93 | 262.86
2018-01-10 20:30 | 259.55 | 258.51
2018-01-10 21:00 | 241.58 | 239.77
2018-01-10 21:30 | 238.47 | 237.39
2018-01-10 22:00 | 224.92 | 224.91
2018-01-10 22:30 | 206.67 | 206.59
2018-01-10 23:00 | 201.54 | 201.4
2018-01-10 23:30 | 173.95 | 173.79
2018-01-11 | 137.21 | 136.11
2018-01-11 00:30 | 108.89 | 106.75
2018-01-11 01:00 | 95.47 | 92.67
2018-01-11 01:30 | 85.66 | 82.32
2018-01-11 02:00 | 80.26 | 76.6
2018-01-11 02:30 | 79.39 | 75.62
2018-01-11 03:00 | 78.16 | 74.28
2018-01-11 03:30 | 71.76 | 67.52
2018-01-11 04:00 | 67.11 | 62.96
2018-01-11 04:30 | 77.19 | 73.92
2018-01-11 05:00 | 86.12 | 83.09
2018-01-11 05:30 | 91.81 | 88.96
2018-01-11 06:00 | 87.45 | 85.05
2018-01-11 06:30 | 113.91 | 113.61
2018-01-11 07:00 | 124.35 | 124.27
2018-01-11 07:30 | 109.7 | 109.69
2018-01-11 08:00 | 118.56 | 118.5
2018-01-11 08:30 | 124.77 | 123.33
2018-01-11 09:00 | 136.06 | 131.72
2018-01-11 09:30 | 132.34 | 127.43
2018-01-11 10:00 | 142.47 | 135.53
2018-01-11 10:30 | 146 | 136.77
2018-01-11 11:00 | 139.59 | 129.84
2018-01-11 11:30 | 141.8 | 131.01
2018-01-11 12:00 | 140.56 | 130.36
2018-01-11 12:30 | 139.45 | 128.97
2018-01-11 13:00 | 146.36 | 126.8
2018-01-11 13:30 | 152.16 | 123.75
2018-01-11 14:00 | 149.49 | 118.43
2018-01-11 14:30 | 148.38 | 117.87
2018-01-11 15:00 | 160.27 | 132.23
2018-01-11 15:30 | 187.41 | 167.16
2018-01-11 16:00 | 179.42 | 170.56
2018-01-11 16:30 | 178.05 | 170.13
2018-01-11 17:00 | 169.47 | 161.77
2018-01-11 17:30 | 161.2 | 153.42
2018-01-11 18:00 | 164.4 | 157.93
2018-01-11 18:30 | 163.15 | 161.13
2018-01-11 19:00 | 169.17 | 167.87
2018-01-11 19:30 | 172.59 | 171.17
2018-01-11 20:00 | 174.48 | 172.71
2018-01-11 20:30 | 170.51 | 167.33
2018-01-11 21:00 | 160.91 | 158.5
2018-01-11 21:30 | 151.85 | 150.5
2018-01-11 22:00 | 143.48 | 142.58
2018-01-11 22:30 | 167.52 | 167.48
2018-01-11 23:00 | 181.04 | 180.95
2018-01-11 23:30 | 132.57 | 130.44
2018-01-12 | 102.61 | 99.24
2018-01-12 00:30 | 102.62 | 98.76
2018-01-12 01:00 | 105.62 | 101.47
2018-01-12 01:30 | 108.18 | 104.11
2018-01-12 02:00 | 124.13 | 120.51
2018-01-12 02:30 | 124.34 | 120.52
2018-01-12 03:00 | 113.3 | 108.93
2018-01-12 03:30 | 108.05 | 103.45
2018-01-12 04:00 | 112.65 | 108.15
2018-01-12 04:30 | 106.71 | 102.13
2018-01-12 05:00 | 86.09 | 80.67
2018-01-12 05:30 | 103.64 | 99.44
2018-01-12 06:00 | 117.23 | 114.39
2018-01-12 06:30 | 155.39 | 154.4
2018-01-12 07:00 | 153.54 | 153.43
2018-01-12 07:30 | 117.53 | 117.26
2018-01-12 08:00 | 190.28 | 189.87
2018-01-12 08:30 | 216.69 | 216.07
2018-01-12 09:00 | 222.43 | 221.83
2018-01-12 09:30 | 222.89 | 222.59
2018-01-12 10:00 | 243.56 | 243.17
2018-01-12 10:30 | 247.55 | 247.11
2018-01-12 11:00 | 247.22 | 246.76
2018-01-12 11:30 | 252.95 | 250.39
2018-01-12 12:00 | 257.66 | 252.55
2018-01-12 12:30 | 257.48 | 252.2
2018-01-12 13:00 | 263.48 | 258.01
2018-01-12 13:30 | 266.65 | 260.95
2018-01-12 14:00 | 275.25 | 269.34
2018-01-12 14:30 | 280.97 | 275.08
2018-01-12 15:00 | 286.95 | 280.96
2018-01-12 15:30 | 290.09 | 284.2
2018-01-12 16:00 | 299.73 | 293.67
2018-01-12 16:30 | 301.93 | 295.76
2018-01-12 17:00 | 308.86 | 302.82
2018-01-12 17:30 | 306.14 | 300.9
2018-01-12 18:00 | 295.28 | 291.35
2018-01-12 18:30 | 284.24 | 283.08
2018-01-12 19:00 | 280.88 | 280.07
2018-01-12 19:30 | 279.47 | 278.56
2018-01-12 20:00 | 279.1 | 276.88
2018-01-12 20:30 | 266.69 | 264.78
2018-01-12 21:00 | 259.15 | 255.7
2018-01-12 21:30 | 248.18 | 245.16
2018-01-12 22:00 | 236.32 | 233.97
2018-01-12 22:30 | 221.61 | 219.37
2018-01-12 23:00 | 217.48 | 214.53
2018-01-12 23:30 | 200.69 | 198.61
2018-01-13 | 171.23 | 171.23
2018-01-13 00:30 | 141.31 | 141.22
2018-01-13 01:00 | 124.4 | 124.18
2018-01-13 01:30 | 87.96 | 87.35
2018-01-13 02:00 | 85.77 | 84.91
2018-01-13 02:30 | 84 | 83.13
2018-01-13 03:00 | 82.94 | 81.99
2018-01-13 03:30 | 81.74 | 80.91
2018-01-13 04:00 | 80.13 | 79.36
2018-01-13 04:30 | 79.2 | 78.42
2018-01-13 05:00 | 77.32 | 76.47
2018-01-13 05:30 | 76.37 | 75.5
2018-01-13 06:00 | 77.88 | 77.37
2018-01-13 06:30 | 82.55 | 82.46
2018-01-13 07:00 | 88.9 | 88.9
2018-01-13 07:30 | 77.18 | 75.76
2018-01-13 08:00 | 92.27 | 80.12
2018-01-13 08:30 | 136.06 | 125.44
2018-01-13 09:00 | 175.13 | 157.15
2018-01-13 09:30 | 191.5 | 172.8
2018-01-13 10:00 | 203.42 | 179.77
2018-01-13 10:30 | 230.21 | 210.51
2018-01-13 11:00 | 251.43 | 237.35
2018-01-13 11:30 | 251.42 | 249.41
2018-01-13 12:00 | 258.12 | 255.62
2018-01-13 12:30 | 238.19 | 235.2
2018-01-13 13:00 | 226.23 | 218.52
2018-01-13 13:30 | 273.05 | 264.81
2018-01-13 14:00 | 287.86 | 279.18
2018-01-13 14:30 | 285.8 | 277.23
2018-01-13 15:00 | 294.93 | 286.39
2018-01-13 15:30 | 305.68 | 297.63
2018-01-13 16:00 | 312.75 | 304.92
2018-01-13 16:30 | 320.68 | 309.29
2018-01-13 17:00 | 326.74 | 315.45
2018-01-13 17:30 | 321.68 | 311.86
2018-01-13 18:00 | 310.98 | 305.57
2018-01-13 18:30 | 304.69 | 300.19
2018-01-13 19:00 | 304.84 | 300.08
2018-01-13 19:30 | 302.3 | 297.22
2018-01-13 20:00 | 296.05 | 291.49
2018-01-13 20:30 | 284.45 | 280.54
2018-01-13 21:00 | 270.84 | 267.55
2018-01-13 21:30 | 254.95 | 254.27
2018-01-13 22:00 | 236.95 | 236.26
2018-01-13 22:30 | 232.73 | 232
2018-01-13 23:00 | 228.43 | 227.84
2018-01-13 23:30 | 207.2 | 206.76
2018-01-14 | 187.38 | 187.18
2018-01-14 00:30 | 173.11 | 172.97
2018-01-14 01:00 | 174.02 | 173.94
2018-01-14 01:30 | 170 | 169.88
2018-01-14 02:00 | 164.9 | 164.65
2018-01-14 02:30 | 161.09 | 160.82
2018-01-14 03:00 | 158.19 | 157.93
2018-01-14 03:30 | 156.19 | 155.95
2018-01-14 04:00 | 153.09 | 152.66
2018-01-14 04:30 | 152.97 | 152.45
2018-01-14 05:00 | 152.56 | 151.97
2018-01-14 05:30 | 152.24 | 151.48
2018-01-14 06:00 | 156.31 | 155.65
2018-01-14 06:30 | 163.84 | 163.47
2018-01-14 07:00 | 170.35 | 170.25
2018-01-14 07:30 | 180.07 | 180.07
2018-01-14 08:00 | 194.2 | 194.03
2018-01-14 08:30 | 203.34 | 203.3
2018-01-14 09:00 | 225.34 | 222.51
2018-01-14 09:30 | 241.33 | 238.52
2018-01-14 10:00 | 247.8 | 244.37
2018-01-14 10:30 | 250.4 | 246.33
2018-01-14 11:00 | 251.27 | 246.83
2018-01-14 11:30 | 253.83 | 249.31
2018-01-14 12:00 | 260.51 | 257.78
2018-01-14 12:30 | 266.62 | 264.34
2018-01-14 13:00 | 273.55 | 271.29
2018-01-14 13:30 | 274.18 | 272.66
2018-01-14 14:00 | 270.3 | 268.93
2018-01-14 14:30 | 276.33 | 275.02
2018-01-14 15:00 | 270.53 | 269.58
2018-01-14 15:30 | 264.95 | 264.36
2018-01-14 16:00 | 255.51 | 255.36
2018-01-14 16:30 | 242.09 | 242.06
2018-01-14 17:00 | 233.81 | 233.73
2018-01-14 17:30 | 226.15 | 226.04
2018-01-14 18:00 | 218.96 | 218.92
2018-01-14 18:30 | 214.13 | 214.02
2018-01-14 19:00 | 213.5 | 213.37
2018-01-14 19:30 | 210.76 | 210.75
2018-01-14 20:00 | 206.87 | 206.87
2018-01-14 20:30 | 198.92 | 198.9
2018-01-14 21:00 | 187.19 | 187.1
2018-01-14 21:30 | 177.14 | 176.97
2018-01-14 22:00 | 164.76 | 164.44
2018-01-14 22:30 | 162.68 | 162.17
2018-01-14 23:00 | 160.42 | 159.81
2018-01-14 23:30 | 144 | 143.42
2018-01-15 | 128.19 | 127.55
2018-01-15 00:30 | 116.13 | 115.25
2018-01-15 01:00 | 108.33 | 107.23
2018-01-15 01:30 | 105.44 | 101.57
2018-01-15 02:00 | 102.97 | 99.14
2018-01-15 02:30 | 101.39 | 97.48
2018-01-15 03:00 | 99.06 | 95.27
2018-01-15 03:30 | 99.34 | 95.52
2018-01-15 04:00 | 100.43 | 96.49
2018-01-15 04:30 | 104.06 | 100.09
2018-01-15 05:00 | 107.89 | 104.22
2018-01-15 05:30 | 109.4 | 105.49
2018-01-15 06:00 | 112.71 | 107.56
2018-01-15 06:30 | 116.12 | 112.17
2018-01-15 07:00 | 119.04 | 118
2018-01-15 07:30 | 127.19 | 127.15
2018-01-15 08:00 | 125.07 | 124.93
2018-01-15 08:30 | 136.39 | 136.3
2018-01-15 09:00 | 141.6 | 141.35
2018-01-15 09:30 | 143.86 | 143.39
2018-01-15 10:00 | 145.94 | 145.7
2018-01-15 10:30 | 146.55 | 146.49
2018-01-15 11:00 | 145.47 | 145.44
2018-01-15 11:30 | 147.38 | 147.35
2018-01-15 12:00 | 151.66 | 151.65
2018-01-15 12:30 | 148.5 | 148.47
2018-01-15 13:00 | 154.6 | 154.57
2018-01-15 13:30 | 160.17 | 160.14
2018-01-15 14:00 | 168.91 | 168.91
2018-01-15 14:30 | 174.89 | 174.58
2018-01-15 15:00 | 177.76 | 177.63
2018-01-15 15:30 | 174.99 | 174.98
2018-01-15 16:00 | 199.07 | 199.07
2018-01-15 16:30 | 206.55 | 206.53
2018-01-15 17:00 | 207.36 | 207.32
2018-01-15 17:30 | 217.06 | 217.04
2018-01-15 18:00 | 212.85 | 212.84
2018-01-15 18:30 | 204.69 | 204.57
2018-01-15 19:00 | 217.09 | 216.96
2018-01-15 19:30 | 218.04 | 217.96
2018-01-15 20:00 | 217.4 | 217.27
2018-01-15 20:30 | 208.2 | 208.11
2018-01-15 21:00 | 195.1 | 195.05
2018-01-15 21:30 | 175.78 | 175.75
2018-01-15 22:00 | 131.97 | 131.95
2018-01-15 22:30 | 127.91 | 127.81
2018-01-15 23:00 | 123.58 | 123.39
2018-01-15 23:30 | 102.03 | 101.57
2018-01-16 | 82.52 | 81.83
2018-01-16 00:30 | 53.24 | 52.13
2018-01-16 01:00 | 43.38 | 40.89
2018-01-16 01:30 | 37.91 | 30.78
2018-01-16 02:00 | 45.88 | 40.5
2018-01-16 02:30 | 34.07 | 26.77
2018-01-16 03:00 | 31.86 | 24.3
2018-01-16 03:30 | 25.25 | 14.94
2018-01-16 04:00 | 27.44 | 17.53
2018-01-16 04:30 | 27.87 | 17.66
2018-01-16 05:00 | 24.23 | 15.01
2018-01-16 05:30 | 49.99 | 46.23
2018-01-16 06:00 | 67.04 | 63.35
2018-01-16 06:30 | 80.22 | 77.25
2018-01-16 07:00 | 97.21 | 95.54
2018-01-16 07:30 | 97.73 | 97.71
2018-01-16 08:00 | 93.85 | 93.84
2018-01-16 08:30 | 97.9 | 97.85
2018-01-16 09:00 | 115.04 | 115.04
2018-01-16 09:30 | 115.89 | 115.87
2018-01-16 10:00 | 126.15 | 126.06
2018-01-16 10:30 | 98.29 | 98.11
2018-01-16 11:00 | 85.24 | 85.01
2018-01-16 11:30 | 115.69 | 115.4
2018-01-16 12:00 | 143.06 | 142.82
2018-01-16 12:30 | 137.71 | 137.48
2018-01-16 13:00 | 125.95 | 125.67
2018-01-16 13:30 | 137.82 | 137.52
2018-01-16 14:00 | 145.37 | 145.12
2018-01-16 14:30 | 152.18 | 151.95
2018-01-16 15:00 | 148.68 | 148.47
2018-01-16 15:30 | 172.97 | 172.82
2018-01-16 16:00 | 198.62 | 198.51
2018-01-16 16:30 | 202.95 | 202.88
2018-01-16 17:00 | 202.72 | 202.68
2018-01-16 17:30 | 146.59 | 146.59
2018-01-16 18:00 | 126.21 | 126.17
2018-01-16 18:30 | 178.45 | 178.3
2018-01-16 19:00 | 211.3 | 211.15
2018-01-16 19:30 | 212.54 | 212.33
2018-01-16 20:00 | 210.36 | 210.25
2018-01-16 20:30 | 204.18 | 203.91
2018-01-16 21:00 | 196.57 | 196.57
2018-01-16 21:30 | 186.38 | 186.37
2018-01-16 22:00 | 177.75 | 177.69
2018-01-16 22:30 | 172.95 | 172.83
2018-01-16 23:00 | 164.21 | 163.98
2018-01-16 23:30 | 144.02 | 143.5
2018-01-17 | 103.26 | 102.4
2018-01-17 00:30 | 62.64 | 60.41
2018-01-17 01:00 | 40.2 | 35.3
2018-01-17 01:30 | 32.62 | 26.66
2018-01-17 02:00 | 20.49 | 7.5
2018-01-17 02:30 | 18.31 | -3.8
2018-01-17 03:00 | 18.28 | -4.11
2018-01-17 03:30 | 21.66 | -13.42
2018-01-17 04:00 | 21.51 | -12.36
2018-01-17 04:30 | 19.8 | -7.28
2018-01-17 05:00 | 19.69 | 3.19
2018-01-17 05:30 | 26.41 | 18.12
2018-01-17 06:00 | 56.45 | 51.8
2018-01-17 06:30 | 73.36 | 70.73
2018-01-17 07:00 | 87.09 | 86.47
2018-01-17 07:30 | 85.21 | 83.54
2018-01-17 08:00 | 89.93 | 87.38
2018-01-17 08:30 | 85.28 | 81.08
2018-01-17 09:00 | 91.68 | 86.48
2018-01-17 09:30 | 82.85 | 78.54
2018-01-17 10:00 | 69.82 | 64.11
2018-01-17 10:30 | 62.77 | 55.55
2018-01-17 11:00 | 65.27 | 51.16
2018-01-17 11:30 | 75.2 | 53.93
2018-01-17 12:00 | 81.49 | 62.06
2018-01-17 12:30 | 88.95 | 71.58
2018-01-17 13:00 | 89.78 | 74.25
2018-01-17 13:30 | 100 | 86.17
2018-01-17 14:00 | 103.06 | 89.62
2018-01-17 14:30 | 105.94 | 93.07
2018-01-17 15:00 | 117.83 | 107.29
2018-01-17 15:30 | 137.85 | 129.88
2018-01-17 16:00 | 150.33 | 143.45
2018-01-17 16:30 | 149.22 | 143.03
2018-01-17 17:00 | 156.56 | 151.09
2018-01-17 17:30 | 173.32 | 169
2018-01-17 18:00 | 175.72 | 172.15
2018-01-17 18:30 | 169.56 | 166.62
2018-01-17 19:00 | 196.39 | 193.73
2018-01-17 19:30 | 208.51 | 205.63
2018-01-17 20:00 | 201.33 | 198.62
2018-01-17 20:30 | 197.89 | 195.6
2018-01-17 21:00 | 183.94 | 181.67
2018-01-17 21:30 | 142.14 | 142.14
2018-01-17 22:00 | 139.82 | 139.54
2018-01-17 22:30 | 128.25 | 127.71
2018-01-17 23:00 | 126.78 | 126.05
2018-01-17 23:30 | 102.54 | 101.27
2018-01-18 | 64.43 | 61.82
2018-01-18 00:30 | 48.53 | 45.3
2018-01-18 01:00 | 52.74 | 49.93
2018-01-18 01:30 | 55.52 | 53.05
2018-01-18 02:00 | 56.35 | 52.71
2018-01-18 02:30 | 17.78 | 0.06
2018-01-18 03:00 | 21.92 | 12.38
2018-01-18 03:30 | 26.29 | 18.91
2018-01-18 04:00 | 28.65 | 21.37
2018-01-18 04:30 | 19.6 | 5.58
2018-01-18 05:00 | 19.24 | 3.56
2018-01-18 05:30 | 18.89 | 5.56
2018-01-18 06:00 | 57.42 | 53.78
2018-01-18 06:30 | 103.18 | 102.23
2018-01-18 07:00 | 126.6 | 126.14
2018-01-18 07:30 | 142.9 | 141.79
2018-01-18 08:00 | 88.04 | 85.36
2018-01-18 08:30 | 100.35 | 90.79
2018-01-18 09:00 | 98.68 | 85.67
2018-01-18 09:30 | 118.89 | 107.1
2018-01-18 10:00 | 120.6 | 107.81
2018-01-18 10:30 | 120.87 | 107.01
2018-01-18 11:00 | 110.21 | 93.88
2018-01-18 11:30 | 108.38 | 97.72
2018-01-18 12:00 | 115.09 | 107.21
2018-01-18 12:30 | 97.51 | 87.97
2018-01-18 13:00 | 109.91 | 101.19
2018-01-18 13:30 | 120.97 | 114.08
2018-01-18 14:00 | 133.36 | 128.47
2018-01-18 14:30 | 148.56 | 143.91
2018-01-18 15:00 | 135.21 | 130.24
2018-01-18 15:30 | 190.71 | 187.16
2018-01-18 16:00 | 189.45 | 186.66
2018-01-18 16:30 | 117.28 | 113
2018-01-18 17:00 | 112.34 | 108.1
2018-01-18 17:30 | 144.14 | 141.61
2018-01-18 18:00 | 159.85 | 158.12
2018-01-18 18:30 | 191.69 | 190.44
2018-01-18 19:00 | 188.75 | 187.89
2018-01-18 19:30 | 178.32 | 177.35
2018-01-18 20:00 | 177.67 | 176.79
2018-01-18 20:30 | 169.35 | 169.22
2018-01-18 21:00 | 160.2 | 159.7
2018-01-18 21:30 | 150.76 | 150.14
2018-01-18 22:00 | 143.79 | 143.19
2018-01-18 22:30 | 133.25 | 132.58
2018-01-18 23:00 | 138.28 | 137.4
2018-01-18 23:30 | 128.95 | 127.61
2018-01-19 | 86.88 | 85.01
2018-01-19 00:30 | 41.42 | 39.43
2018-01-19 01:00 | 30.92 | 28.13
2018-01-19 01:30 | 26.13 | 22.79
2018-01-19 02:00 | 12.28 | 0.74
2018-01-19 02:30 | 11.07 | 1.25
2018-01-19 03:00 | 10.25 | 2.27
2018-01-19 03:30 | 12.01 | 5.21
2018-01-19 04:00 | 13.1 | -5.96
2018-01-19 04:30 | 24.54 | -21.72
2018-01-19 05:00 | 22.64 | -20.81
2018-01-19 05:30 | 12.76 | 9.02
2018-01-19 06:00 | 12.88 | 7.93
2018-01-19 06:30 | 32.68 | 31.43
2018-01-19 07:00 | 59.3 | 59.18
2018-01-19 07:30 | 85.01 | 84.96
2018-01-19 08:00 | 61.07 | 60.71
2018-01-19 08:30 | 56.3 | 49.09
2018-01-19 09:00 | 58.83 | 50.4
2018-01-19 09:30 | 53.14 | 41.86
2018-01-19 10:00 | 77.69 | 69.98
2018-01-19 10:30 | 80.95 | 73.18
2018-01-19 11:00 | 98.14 | 91.3
2018-01-19 11:30 | 162.1 | 158.04
2018-01-19 12:00 | 74.46 | 65.69
2018-01-19 12:30 | 115.6 | 110.81
2018-01-19 13:00 | 158.27 | 154.87
2018-01-19 13:30 | 37.46 | 11.7
2018-01-19 14:00 | 27.19 | 10.17
2018-01-19 14:30 | 28.83 | 13.91
2018-01-19 15:00 | 30.91 | 17.51
2018-01-19 15:30 | 33.18 | 19.95
2018-01-19 16:00 | 32.93 | 21.58
2018-01-19 16:30 | 33.77 | 24.35
2018-01-19 17:00 | 33.57 | 26.49
2018-01-19 17:30 | 33.83 | 24.12
2018-01-19 18:00 | 38.7 | 27.02
2018-01-19 18:30 | 24.83 | -1.65
2018-01-19 19:00 | 24.47 | -3.3
2018-01-19 19:30 | 44.69 | -2.92
2018-01-19 20:00 | 45.19 | -3.44
2018-01-19 20:30 | 144.92 | 142.93
2018-01-19 21:00 | 181.26 | 181.19
2018-01-19 21:30 | 167.72 | 167.48
2018-01-19 22:00 | 130.98 | 130.4
2018-01-19 22:30 | 126.04 | 125.43
2018-01-19 23:00 | 139.56 | 138.96
2018-01-19 23:30 | 102.95 | 102.57
2018-01-20 | 43.43 | 42.64
2018-01-20 00:30 | 8.33 | 2.95
2018-01-20 01:00 | 30.48 | -30.02
2018-01-20 01:30 | 59.87 | -59.76
2018-01-20 02:00 | 61.61 | -61.48
2018-01-20 02:30 | 62.75 | -62.62
2018-01-20 03:00 | 62.42 | -62.31
2018-01-20 03:30 | 62.23 | -62.07
2018-01-20 04:00 | 62.33 | -62.14
2018-01-20 04:30 | 61.78 | -61.56
2018-01-20 05:00 | 62.4 | -62.22
2018-01-20 05:30 | 61.12 | -60.94
2018-01-20 06:00 | 60.75 | -60.6
2018-01-20 06:30 | 59.62 | -59.52
2018-01-20 07:00 | 55.9 | -55.9
2018-01-20 07:30 | 49.21 | -49.03
2018-01-20 08:00 | 46.04 | -44.75
2018-01-20 08:30 | 51.43 | -38.33
2018-01-20 09:00 | 66.08 | -29.37
2018-01-20 09:30 | 84.73 | 54.8
2018-01-20 10:00 | 83.27 | 52.16
2018-01-20 10:30 | 83.24 | 48.33
2018-01-20 11:00 | 77.62 | 34.29
2018-01-20 11:30 | 78.64 | 36.08
2018-01-20 12:00 | 77.68 | 33.95
2018-01-20 12:30 | 79 | 36.71
2018-01-20 13:00 | 76.58 | 27.41
2018-01-20 13:30 | 76.1 | 27.32
2018-01-20 14:00 | 84.5 | 47.17
2018-01-20 14:30 | 91.36 | 58.12
2018-01-20 15:00 | 109.22 | 83.44
2018-01-20 15:30 | 117.61 | 94.27
2018-01-20 16:00 | 138.9 | 119.18
2018-01-20 16:30 | 166.52 | 153.45
2018-01-20 17:00 | 185.56 | 177.08
2018-01-20 17:30 | 185.6 | 177.8
2018-01-20 18:00 | 183.01 | 175.73
2018-01-20 18:30 | 180.88 | 174.25
2018-01-20 19:00 | 177.41 | 171.08
2018-01-20 19:30 | 181.75 | 175.14
2018-01-20 20:00 | 168.11 | 161.47
2018-01-20 20:30 | 164.78 | 158.88
2018-01-20 21:00 | 151.69 | 149.51
2018-01-20 21:30 | 139.88 | 137.83
2018-01-20 22:00 | 114.84 | 113.03
2018-01-20 22:30 | 121.39 | 119.98
2018-01-20 23:00 | 137.27 | 136.21
2018-01-20 23:30 | 119.9 | 119.07
2018-01-21 | 61.12 | 60
2018-01-21 00:30 | 23.41 | 21.74
2018-01-21 01:00 | 8.98 | -0.42
2018-01-21 01:30 | 11.06 | -6.77
2018-01-21 02:00 | 9.37 | -1.3
2018-01-21 02:30 | 9.86 | -1.86
2018-01-21 03:00 | 20.83 | -19.07
2018-01-21 03:30 | 17.98 | -15.8
2018-01-21 04:00 | 23.95 | -22.51
2018-01-21 04:30 | 18.06 | -15.66
2018-01-21 05:00 | 21.97 | -20.39
2018-01-21 05:30 | 26.7 | -25.6
2018-01-21 06:00 | 36.99 | -36.38
2018-01-21 06:30 | 32.1 | -31.38
2018-01-21 07:00 | 21.83 | -20.95
2018-01-21 07:30 | 9.66 | -8.91
2018-01-21 08:00 | 4.85 | 4.85
2018-01-21 08:30 | 22.19 | 21.58
2018-01-21 09:00 | 55.06 | 27.81
2018-01-21 09:30 | 71.35 | 34.5
2018-01-21 10:00 | 69.82 | 26.07
2018-01-21 10:30 | 68.26 | 15.3
2018-01-21 11:00 | 71.24 | 21.29
2018-01-21 11:30 | 81.48 | 44.61
2018-01-21 12:00 | 79.88 | 39.12
2018-01-21 12:30 | 78.14 | 35.45
2018-01-21 13:00 | 88.61 | 53.89
2018-01-21 13:30 | 92.8 | 61.15
2018-01-21 14:00 | 94.29 | 62.62
2018-01-21 14:30 | 84.7 | 54.78
2018-01-21 15:00 | 72.35 | 47.8
2018-01-21 15:30 | 92.75 | 77.01
2018-01-21 16:00 | 77.34 | 56.91
2018-01-21 16:30 | 91.03 | 75.01
2018-01-21 17:00 | 119.41 | 107.87
2018-01-21 17:30 | 119.18 | 108.92
2018-01-21 18:00 | 105.93 | 95.28
2018-01-21 18:30 | 132.98 | 125.82
2018-01-21 19:00 | 146.42 | 139.9
2018-01-21 19:30 | 175.01 | 169.06
2018-01-21 20:00 | 178.37 | 172.89
2018-01-21 20:30 | 195.03 | 190.43
2018-01-21 21:00 | 193.07 | 185.72
2018-01-21 21:30 | 168.97 | 161.52
2018-01-21 22:00 | 143.45 | 138.58
2018-01-21 22:30 | 151.78 | 151.62
2018-01-21 23:00 | 151.6 | 151.48
2018-01-21 23:30 | 122.11 | 122.01
2018-01-22 | 70.66 | 70.21
2018-01-22 00:30 | 38.57 | 37.49
2018-01-22 01:00 | 22.39 | 20.18
2018-01-22 01:30 | 19.89 | 17.14
2018-01-22 02:00 | 10.53 | 3.48
2018-01-22 02:30 | 15.26 | -12.25
2018-01-22 03:00 | 19.01 | -16.85
2018-01-22 03:30 | 18.53 | -16.01
2018-01-22 04:00 | 10.99 | -2.95
2018-01-22 04:30 | 13.27 | -8.45
2018-01-22 05:00 | 20.82 | -19.36
2018-01-22 05:30 | 12.56 | -10.59
2018-01-22 06:00 | 6.78 | 4.41
2018-01-22 06:30 | 41.46 | 41.46
2018-01-22 07:00 | 74.08 | 73.6
2018-01-22 07:30 | 101.22 | 78.55
2018-01-22 08:00 | 100.95 | 73.03
2018-01-22 08:30 | 89.88 | 66.73
2018-01-22 09:00 | 90.35 | 64.66
2018-01-22 09:30 | 88.8 | 55.14
2018-01-22 10:00 | 90.8 | 53.26
2018-01-22 10:30 | 81.66 | 35.26
2018-01-22 11:00 | 78.9 | 20.95
2018-01-22 11:30 | 78.34 | 21.81
2018-01-22 12:00 | 73.58 | 20.34
2018-01-22 12:30 | 73.65 | 21.1
2018-01-22 13:00 | 74.63 | 17.95
2018-01-22 13:30 | 76.27 | 40.69
2018-01-22 14:00 | 62.99 | 27.95
2018-01-22 14:30 | 62.83 | 30.2
2018-01-22 15:00 | 69.71 | 43.47
2018-01-22 15:30 | 66.82 | 38.38
2018-01-22 16:00 | 86.23 | 66.67
2018-01-22 16:30 | 110.04 | 97.15
2018-01-22 17:00 | 136.14 | 127.76
2018-01-22 17:30 | 148.32 | 143.16
2018-01-22 18:00 | 149.2 | 146.62
2018-01-22 18:30 | 142.68 | 140.64
2018-01-22 19:00 | 148.72 | 146.73
2018-01-22 19:30 | 155.09 | 152.79
2018-01-22 20:00 | 157.4 | 155.49
2018-01-22 20:30 | 152.17 | 150.8
2018-01-22 21:00 | 137.22 | 136.19
2018-01-22 21:30 | 110.41 | 109.99
2018-01-22 22:00 | 88.52 | 87.88
2018-01-22 22:30 | 109.1 | 108.49
2018-01-22 23:00 | 137.31 | 136.82
2018-01-22 23:30 | 109.85 | 108.93
2018-01-23 | 54.96 | 52.5
2018-01-23 00:30 | 23.32 | 16.37
2018-01-23 01:00 | 15.15 | 0.07
2018-01-23 01:30 | 9.74 | -5.71
2018-01-23 02:00 | 11.19 | -7.63
2018-01-23 02:30 | 15.82 | -13.43
2018-01-23 03:00 | 21.28 | -19.58
2018-01-23 03:30 | 21.37 | -19.55
2018-01-23 04:00 | 17.71 | -15.06
2018-01-23 04:30 | 14.19 | -11.04
2018-01-23 05:00 | 8.16 | 0.22
2018-01-23 05:30 | 12.63 | 9.55
2018-01-23 06:00 | 33.47 | 32.75
2018-01-23 06:30 | 113.37 | 113.37
2018-01-23 07:00 | 145.81 | 144.33
2018-01-23 07:30 | 168.12 | 161.12
2018-01-23 08:00 | 177.8 | 167.38
2018-01-23 08:30 | 180.52 | 168.05
2018-01-23 09:00 | 191.82 | 177.63
2018-01-23 09:30 | 191.15 | 183.73
2018-01-23 10:00 | 192.78 | 186.3
2018-01-23 10:30 | 108.37 | 97.98
2018-01-23 11:00 | 85.37 | 70.51
2018-01-23 11:30 | 95.74 | 81.86
2018-01-23 12:00 | 91.1 | 76.82
2018-01-23 12:30 | 94.82 | 80.84
2018-01-23 13:00 | 109.96 | 97.34
2018-01-23 13:30 | 118.15 | 106.88
2018-01-23 14:00 | 119.16 | 107.48
2018-01-23 14:30 | 124.7 | 113.19
2018-01-23 15:00 | 131.69 | 120.66
2018-01-23 15:30 | 140.4 | 130.38
2018-01-23 16:00 | 152.47 | 145.99
2018-01-23 16:30 | 180.82 | 176.99
2018-01-23 17:00 | 205.74 | 202.63
2018-01-23 17:30 | 210.97 | 208.78
2018-01-23 18:00 | 195.59 | 194.3
2018-01-23 18:30 | 187.05 | 185.96
2018-01-23 19:00 | 204.62 | 201.53
2018-01-23 19:30 | 203.84 | 200.45
2018-01-23 20:00 | 200.56 | 197.56
2018-01-23 20:30 | 193.93 | 191.81
2018-01-23 21:00 | 176.38 | 172.91
2018-01-23 21:30 | 159.64 | 155.47
2018-01-23 22:00 | 123.45 | 121.87
2018-01-23 22:30 | 136.51 | 136.49
2018-01-23 23:00 | 156.06 | 155.99
2018-01-23 23:30 | 125.12 | 124.87
2018-01-24 | 79.9 | 79.48
2018-01-24 00:30 | 43.66 | 43.5
2018-01-24 01:00 | 25.04 | 24.62
2018-01-24 01:30 | 10.27 | 9.39
2018-01-24 02:00 | 5.67 | 3.96
2018-01-24 02:30 | 4.24 | -0.8
2018-01-24 03:00 | 6.36 | -4.96
2018-01-24 03:30 | 10.43 | -9.6
2018-01-24 04:00 | 11.11 | -10.12
2018-01-24 04:30 | 5.43 | -2.42
2018-01-24 05:00 | 6.61 | 5.14
2018-01-24 05:30 | 17.45 | 17.01
2018-01-24 06:00 | 37.78 | 37.74
2018-01-24 06:30 | 55.77 | 55.73
2018-01-24 07:00 | 88.17 | 88.1
2018-01-24 07:30 | 90.12 | 90.11
2018-01-24 08:00 | 91.2 | 91
2018-01-24 08:30 | 94.22 | 93.73
2018-01-24 09:00 | 90.26 | 88.22
2018-01-24 09:30 | 112.2 | 99.24
2018-01-24 10:00 | 123.86 | 104.69
2018-01-24 10:30 | 113.11 | 89.98
2018-01-24 11:00 | 108.92 | 83.94
2018-01-24 11:30 | 96.69 | 67.18
2018-01-24 12:00 | 97.85 | 67.59
2018-01-24 12:30 | 107.15 | 80.12
2018-01-24 13:00 | 113.78 | 89.39
2018-01-24 13:30 | 113.36 | 87.52
2018-01-24 14:00 | 107.21 | 79.86
2018-01-24 14:30 | 110.45 | 83.61
2018-01-24 15:00 | 99.14 | 66.89
2018-01-24 15:30 | 124.7 | 101.53
2018-01-24 16:00 | 143.59 | 123.92
2018-01-24 16:30 | 163.41 | 147.84
2018-01-24 17:00 | 178.77 | 165.6
2018-01-24 17:30 | 189.1 | 179.17
2018-01-24 18:00 | 164.8 | 155.16
2018-01-24 18:30 | 172.76 | 164.53
2018-01-24 19:00 | 183.76 | 175.51
2018-01-24 19:30 | 208.11 | 200.52
2018-01-24 20:00 | 227.73 | 221.36
2018-01-24 20:30 | 230.06 | 227.58
2018-01-24 21:00 | 212.78 | 209.39
2018-01-24 21:30 | 184.01 | 180.8
2018-01-24 22:00 | 157.71 | 155.21
2018-01-24 22:30 | 172.94 | 172.9
2018-01-24 23:00 | 177.31 | 177.17
2018-01-24 23:30 | 163.33 | 163.02
2018-01-25 | 116.17 | 115.39
2018-01-25 00:30 | 88.47 | 87.45
2018-01-25 01:00 | 75.75 | 75.56
2018-01-25 01:30 | 69.52 | 69.24
2018-01-25 02:00 | 91.83 | 91.57
2018-01-25 02:30 | 66.78 | 66.71
2018-01-25 03:00 | 58.87 | 58.79
2018-01-25 03:30 | 44.29 | 44.2
2018-01-25 04:00 | 32.26 | 32.18
2018-01-25 04:30 | 38.86 | 38.81
2018-01-25 05:00 | 39.36 | 39.36
2018-01-25 05:30 | 64.24 | 64.24
2018-01-25 06:00 | 91.06 | 91.04
2018-01-25 06:30 | 113.29 | 113.29
2018-01-25 07:00 | 116.85 | 116.85
2018-01-25 07:30 | 123.19 | 120.74
2018-01-25 08:00 | 128.27 | 122.2
2018-01-25 08:30 | 155.8 | 148.75
2018-01-25 09:00 | 174.51 | 167.13
2018-01-25 09:30 | 170.2 | 162.33
2018-01-25 10:00 | 170.8 | 162.01
2018-01-25 10:30 | 170.71 | 161.76
2018-01-25 11:00 | 182.77 | 178.74
2018-01-25 11:30 | 178.27 | 174.61
2018-01-25 12:00 | 173 | 169.15
2018-01-25 12:30 | 179.47 | 175.6
2018-01-25 13:00 | 175.43 | 171.42
2018-01-25 13:30 | 171.31 | 167.12
2018-01-25 14:00 | 195.58 | 191.98
2018-01-25 14:30 | 177.6 | 173.54
2018-01-25 15:00 | 175.04 | 171.31
2018-01-25 15:30 | 179.65 | 176.31
2018-01-25 16:00 | 199.99 | 197.06
2018-01-25 16:30 | 270.54 | 268.42
2018-01-25 17:00 | 263.02 | 261.13
2018-01-25 17:30 | 246.62 | 245.25
2018-01-25 18:00 | 234.45 | 233.49
2018-01-25 18:30 | 237.49 | 236.68
2018-01-25 19:00 | 239.69 | 238.83
2018-01-25 19:30 | 250.21 | 249.11
2018-01-25 20:00 | 244.25 | 243.34
2018-01-25 20:30 | 244.09 | 243.88
2018-01-25 21:00 | 232.9 | 232.9
2018-01-25 21:30 | 202.51 | 202.44
2018-01-25 22:00 | 150.61 | 150.42
2018-01-25 22:30 | 163.52 | 163.41
2018-01-25 23:00 | 177.31 | 177.18
2018-01-25 23:30 | 145.23 | 144.99
2018-01-26 | 84.09 | 83.76
2018-01-26 00:30 | 67.11 | 66.92
2018-01-26 01:00 | 39.55 | 39.3
2018-01-26 01:30 | 30.35 | 29.89
2018-01-26 02:00 | 22.68 | 21.87
2018-01-26 02:30 | 17.88 | 16.48
2018-01-26 03:00 | 9.11 | 6.02
2018-01-26 03:30 | 5.9 | 1.06
2018-01-26 04:00 | 7.49 | -5.82
2018-01-26 04:30 | 12.38 | -11.19
2018-01-26 05:00 | 7.61 | -4.95
2018-01-26 05:30 | 8.71 | -5.67
2018-01-26 06:00 | 8.73 | -6.69
2018-01-26 06:30 | 3.95 | -3.22
2018-01-26 07:00 | 19.2 | 18.74
2018-01-26 07:30 | 31.97 | 30.44
2018-01-26 08:00 | 46.11 | 45.75
2018-01-26 08:30 | 75.43 | 75.43
2018-01-26 09:00 | 74.73 | 74.66
2018-01-26 09:30 | 77.75 | 77.08
2018-01-26 10:00 | 65.67 | 63.43
2018-01-26 10:30 | 66.81 | 63.66
2018-01-26 11:00 | 83.11 | 81.26
2018-01-26 11:30 | 100.85 | 99.63
2018-01-26 12:00 | 98.7 | 97.34
2018-01-26 12:30 | 98.89 | 97.44
2018-01-26 13:00 | 110.09 | 108.83
2018-01-26 13:30 | 105.13 | 103.64
2018-01-26 14:00 | 90.98 | 86.98
2018-01-26 14:30 | 93.56 | 89.44
2018-01-26 15:00 | 105.11 | 101.47
2018-01-26 15:30 | 113.05 | 109.99
2018-01-26 16:00 | 139.01 | 136.12
2018-01-26 16:30 | 172.23 | 169.76
2018-01-26 17:00 | 187.69 | 185.5
2018-01-26 17:30 | 214.29 | 212.6
2018-01-26 18:00 | 206.49 | 205.11
2018-01-26 18:30 | 188.3 | 187.34
2018-01-26 19:00 | 198.96 | 197.98
2018-01-26 19:30 | 207.59 | 206.32
2018-01-26 20:00 | 197.99 | 196.84
2018-01-26 20:30 | 195.69 | 194.85
2018-01-26 21:00 | 172.11 | 170.39
2018-01-26 21:30 | 146.73 | 144.23
2018-01-26 22:00 | 104.84 | 102.94
2018-01-26 22:30 | 108.69 | 107.77
2018-01-26 23:00 | 103.78 | 103.62
2018-01-26 23:30 | 72.38 | 72.22
2018-01-27 | 48.54 | 48.54
2018-01-27 00:30 | 49.35 | 47.98
2018-01-27 01:00 | 44.92 | 40.17
2018-01-27 01:30 | 39.69 | 34.81
2018-01-27 02:00 | 37.81 | 32.98
2018-01-27 02:30 | 28.55 | 22.05
2018-01-27 03:00 | 24.81 | 16.95
2018-01-27 03:30 | 31.13 | 25.1
2018-01-27 04:00 | 20.32 | 11.05
2018-01-27 04:30 | 26.88 | 20.65
2018-01-27 05:00 | 17.71 | 5.85
2018-01-27 05:30 | 17.5 | 0.07
2018-01-27 06:00 | 18.08 | 1.7
2018-01-27 06:30 | 17.37 | -0.59
2018-01-27 07:00 | 25.25 | 20.52
2018-01-27 07:30 | 32.14 | 31.93
2018-01-27 08:00 | 42.4 | 42.39
2018-01-27 08:30 | 68.33 | 68.06
2018-01-27 09:00 | 71.23 | 67.53
2018-01-27 09:30 | 60.26 | 34.95
2018-01-27 10:00 | 72.09 | 30.04
2018-01-27 10:30 | 77.05 | 36.7
2018-01-27 11:00 | 81.09 | 42.86
2018-01-27 11:30 | 86.05 | 49.89
2018-01-27 12:00 | 84.49 | 43.81
2018-01-27 12:30 | 90.31 | 42.09
2018-01-27 13:00 | 101.04 | 38.62
2018-01-27 13:30 | 103.08 | 41.32
2018-01-27 14:00 | 70.19 | 36.39
2018-01-27 14:30 | 66.91 | 54.13
2018-01-27 15:00 | 65.1 | 50.56
2018-01-27 15:30 | 76.29 | 63.46
2018-01-27 16:00 | 87.87 | 77.09
2018-01-27 16:30 | 92.86 | 82.94
2018-01-27 17:00 | 103.51 | 94.74
2018-01-27 17:30 | 95.39 | 87.22
2018-01-27 18:00 | 100.74 | 95.62
2018-01-27 18:30 | 133.98 | 131.8
2018-01-27 19:00 | 147.89 | 145.89
2018-01-27 19:30 | 165.72 | 163.62
2018-01-27 20:00 | 198.57 | 197.19
2018-01-27 20:30 | 214.49 | 213.58
2018-01-27 21:00 | 196.69 | 196.56
2018-01-27 21:30 | 200.29 | 200.2
2018-01-27 22:00 | 179.02 | 178.69
2018-01-27 22:30 | 152.29 | 151.77
2018-01-27 23:00 | 146.01 | 145.45
2018-01-27 23:30 | 128.34 | 127.81
2018-01-28 | 72.24 | 70.56
2018-01-28 00:30 | 47.45 | 47.24
2018-01-28 01:00 | 29.46 | 29.19
2018-01-28 01:30 | 16.17 | 15.44
2018-01-28 02:00 | 16.89 | 15.74
2018-01-28 02:30 | 23.65 | 22.4
2018-01-28 03:00 | 13 | 10.58
2018-01-28 03:30 | 9.26 | 5.34
2018-01-28 04:00 | 6.82 | -1.24
2018-01-28 04:30 | 9.09 | -7.25
2018-01-28 05:00 | 7.73 | -5.42
2018-01-28 05:30 | 11.52 | -10.12
2018-01-28 06:00 | 18.83 | -18.36
2018-01-28 06:30 | 17.79 | -17.53
2018-01-28 07:00 | 9.31 | -9.3
2018-01-28 07:30 | 6.78 | -4.99
2018-01-28 08:00 | 8.07 | 0.96
2018-01-28 08:30 | 12.26 | 12.23
2018-01-28 09:00 | 28.04 | 27.88
2018-01-28 09:30 | 32.59 | 32.16
2018-01-28 10:00 | 31.46 | 30.83
2018-01-28 10:30 | 56.63 | 40.88
2018-01-28 11:00 | 51.69 | 28.94
2018-01-28 11:30 | 45.64 | 25.65
2018-01-28 12:00 | 47.67 | 32.49
2018-01-28 12:30 | 37.92 | 11.88
2018-01-28 13:00 | 36.78 | 5.94
2018-01-28 13:30 | 39.32 | -4.46
2018-01-28 14:00 | 47.4 | 29.94
2018-01-28 14:30 | 60.05 | 47.7
2018-01-28 15:00 | 67.77 | 56.85
2018-01-28 15:30 | 108.38 | 101.96
2018-01-28 16:00 | 94.7 | 86.28
2018-01-28 16:30 | 102.59 | 100.69
2018-01-28 17:00 | 95.69 | 94.25
2018-01-28 17:30 | 110.86 | 109.99
2018-01-28 18:00 | 133.18 | 132.7
2018-01-28 18:30 | 121.48 | 121.16
2018-01-28 19:00 | 135.34 | 135.01
2018-01-28 19:30 | 153.89 | 153.48
2018-01-28 20:00 | 142.75 | 142.13
2018-01-28 20:30 | 140.31 | 138.34
2018-01-28 21:00 | 132.31 | 128.13
2018-01-28 21:30 | 116.66 | 111.76
2018-01-28 22:00 | 75.9 | 72.33
2018-01-28 22:30 | 87.1 | 87.01
2018-01-28 23:00 | 109.08 | 108.97
2018-01-28 23:30 | 84.06 | 83.57
2018-01-29 | 31.95 | 29.92
2018-01-29 00:30 | 11.36 | 9.34
2018-01-29 01:00 | 10.2 | -8.2
2018-01-29 01:30 | 21.78 | -21.04
2018-01-29 02:00 | 18.99 | -18.07
2018-01-29 02:30 | 21.86 | -21.01
2018-01-29 03:00 | 21.51 | -20.64
2018-01-29 03:30 | 21.07 | -20.12
2018-01-29 04:00 | 21.13 | -20.25
2018-01-29 04:30 | 24.74 | -24.15
2018-01-29 05:00 | 17.02 | -16.2
2018-01-29 05:30 | 5.19 | -1.66
2018-01-29 06:00 | 11.65 | 11.5
2018-01-29 06:30 | 61.18 | 60.96
2018-01-29 07:00 | 82.67 | 72.33
2018-01-29 07:30 | 78.7 | 62.98
2018-01-29 08:00 | 63.66 | 44.9
2018-01-29 08:30 | 71.77 | 56.03
2018-01-29 09:00 | 63.64 | 48.57
2018-01-29 09:30 | 74.26 | 60.9
2018-01-29 10:00 | 82.21 | 70.3
2018-01-29 10:30 | 87.37 | 76.28
2018-01-29 11:00 | 93.89 | 83.33
2018-01-29 11:30 | 62.26 | 44.15
2018-01-29 12:00 | 62.99 | 42.26
2018-01-29 12:30 | 68.62 | 49.65
2018-01-29 13:00 | 73.75 | 56.24
2018-01-29 13:30 | 87.6 | 73.23
2018-01-29 14:00 | 97.81 | 85.18
2018-01-29 14:30 | 112.75 | 101.96
2018-01-29 15:00 | 107.74 | 96.76
2018-01-29 15:30 | 107.69 | 97.75
2018-01-29 16:00 | 122.46 | 114.97
2018-01-29 16:30 | 131.93 | 126.11
2018-01-29 17:00 | 155.92 | 151.35
2018-01-29 17:30 | 167.97 | 165.11
2018-01-29 18:00 | 160.46 | 158.48
2018-01-29 18:30 | 160.2 | 158.6
2018-01-29 19:00 | 175.41 | 173.83
2018-01-29 19:30 | 181.68 | 180.08
2018-01-29 20:00 | 177.97 | 176.78
2018-01-29 20:30 | 182.3 | 182.3
2018-01-29 21:00 | 172.91 | 172.49
2018-01-29 21:30 | 163.34 | 163.06
2018-01-29 22:00 | 117.49 | 116.96
2018-01-29 22:30 | 133.23 | 132.86
2018-01-29 23:00 | 148.96 | 148.23
2018-01-29 23:30 | 113.71 | 113.05
2018-01-30 | 58.74 | 58.22
2018-01-30 00:30 | 39.1 | 38.08
2018-01-30 01:00 | 27.17 | 25.62
2018-01-30 01:30 | 25.5 | 23.63
2018-01-30 02:00 | 25.29 | 23.24
2018-01-30 02:30 | 24.45 | 22.06
2018-01-30 03:00 | 17.3 | 13.9
2018-01-30 03:30 | 13.8 | 9.33
2018-01-30 04:00 | 10.29 | -3.54
2018-01-30 04:30 | 10.49 | -4.99
2018-01-30 05:00 | 10.85 | 6.27
2018-01-30 05:30 | 19.23 | 17.44
2018-01-30 06:00 | 21.57 | 20.27
2018-01-30 06:30 | 49.16 | 49.06
2018-01-30 07:00 | 57.61 | 57.61
2018-01-30 07:30 | 45.61 | 45.6
2018-01-30 08:00 | 40.03 | 39.93
2018-01-30 08:30 | 55.89 | 44.58
2018-01-30 09:00 | 74.07 | 62.25
2018-01-30 09:30 | 85.35 | 73.59
2018-01-30 10:00 | 91.92 | 80.21
2018-01-30 10:30 | 106.92 | 97.79
2018-01-30 11:00 | 108.99 | 99.32
2018-01-30 11:30 | 106.66 | 95.61
2018-01-30 12:00 | 120.16 | 110.05
2018-01-30 12:30 | 116.4 | 105.8
2018-01-30 13:00 | 215.44 | 209.38
2018-01-30 13:30 | 190.82 | 184.75
2018-01-30 14:00 | 169.15 | 165.75
2018-01-30 14:30 | 161.47 | 159.52
2018-01-30 15:00 | 183.43 | 181.71
2018-01-30 15:30 | 186.91 | 185.33
2018-01-30 16:00 | 157.71 | 156.06
2018-01-30 16:30 | 172.07 | 170.88
2018-01-30 17:00 | 188.21 | 186.93
2018-01-30 17:30 | 188.97 | 188.17
2018-01-30 18:00 | 211.38 | 211.02
2018-01-30 18:30 | 188.81 | 187.15
2018-01-30 19:00 | 179.2 | 176.99
2018-01-30 19:30 | 173.23 | 170.37
2018-01-30 20:00 | 168.1 | 165.39
2018-01-30 20:30 | 169.49 | 167.51
2018-01-30 21:00 | 165.22 | 163.91
2018-01-30 21:30 | 142.48 | 141.45
2018-01-30 22:00 | 141.37 | 141.36
2018-01-30 22:30 | 156.02 | 155.66
2018-01-30 23:00 | 176.77 | 176.64
2018-01-30 23:30 | 161.39 | 161.23
2018-01-31 | 96.03 | 94.89
2018-01-31 00:30 | 78.03 | 77.62
2018-01-31 01:00 | 69.03 | 68.45
2018-01-31 01:30 | 105.92 | 105.51
2018-01-31 02:00 | 84.62 | 84.06
2018-01-31 02:30 | 89.06 | 88.51
2018-01-31 03:00 | 46.89 | 45.82
2018-01-31 03:30 | 62.72 | 61.53
2018-01-31 04:00 | 114.02 | 113.5
2018-01-31 04:30 | 116.51 | 116.03
2018-01-31 05:00 | 94.64 | 94.09
2018-01-31 05:30 | 121.86 | 121.67
2018-01-31 06:00 | 88.6 | 88.36
2018-01-31 06:30 | 68.05 | 68.05
2018-01-31 07:00 | 83.65 | 83.2
2018-01-31 07:30 | 87.71 | 81.86
2018-01-31 08:00 | 120.85 | 101.18
2018-01-31 08:30 | 129.63 | 101.57
2018-01-31 09:00 | 182.9 | 175.22
2018-01-31 09:30 | 179.47 | 171.12
2018-01-31 10:00 | 146.23 | 134.75
2018-01-31 10:30 | 192.14 | 182.42
2018-01-31 11:00 | 209.19 | 200.81
2018-01-31 11:30 | 200.56 | 193.97
2018-01-31 12:00 | 209.04 | 204.51
2018-01-31 12:30 | 234.15 | 230.68
2018-01-31 13:00 | 251.35 | 248.09
2018-01-31 13:30 | 259.53 | 256.43
2018-01-31 14:00 | 264.4 | 261.51
2018-01-31 14:30 | 265.68 | 262.95
2018-01-31 15:00 | 266.33 | 263.63
2018-01-31 15:30 | 274.9 | 272.3
2018-01-31 16:00 | 279.39 | 276.53
2018-01-31 16:30 | 278.31 | 275.55
2018-01-31 17:00 | 282.51 | 280.43
2018-01-31 17:30 | 271.09 | 269.76
2018-01-31 18:00 | 268.5 | 267.65
2018-01-31 18:30 | 264.85 | 261.41
2018-01-31 19:00 | 273.87 | 270.91
2018-01-31 19:30 | 259.49 | 255.97
2018-01-31 20:00 | 257.63 | 255.37
2018-01-31 20:30 | 240.59 | 238.34
2018-01-31 21:00 | 228.17 | 227.67
2018-01-31 21:30 | 217.53 | 217.4
2018-01-31 22:00 | 196.99 | 196.92
2018-01-31 22:30 | 191.89 | 191.89
2018-01-31 23:00 | 185.29 | 185.27
2018-01-31 23:30 | 163.29 | 163.03
2018-02-01 | 119.05 | 116.84
2018-02-01 00:30 | 98.27 | 95.36
2018-02-01 01:00 | 86.85 | 83.6
2018-02-01 01:30 | 76.86 | 73.21
2018-02-01 02:00 | 70.83 | 66.91
2018-02-01 02:30 | 65.62 | 61.56
2018-02-01 03:00 | 58.33 | 53.72
2018-02-01 03:30 | 49.59 | 44.24
2018-02-01 04:00 | 52.45 | 47.35
2018-02-01 04:30 | 56.75 | 52.1
2018-02-01 05:00 | 59.54 | 55.14
2018-02-01 05:30 | 57.23 | 53.04
2018-02-01 06:00 | 65.64 | 62.63
2018-02-01 06:30 | 86.55 | 85.87
2018-02-01 07:00 | 103.44 | 103.42
2018-02-01 07:30 | 96.72 | 96.46
2018-02-01 08:00 | 113.28 | 111.48
2018-02-01 08:30 | 137.02 | 135.38
2018-02-01 09:00 | 144.4 | 142.65
2018-02-01 09:30 | 152.5 | 150.34
2018-02-01 10:00 | 145.58 | 143.76
2018-02-01 10:30 | 115.15 | 113.73
2018-02-01 11:00 | 143.12 | 141.61
2018-02-01 11:30 | 132.34 | 131.06
2018-02-01 12:00 | 144.86 | 143.82
2018-02-01 12:30 | 145.49 | 144.19
2018-02-01 13:00 | 144.09 | 142.45
2018-02-01 13:30 | 136.82 | 135.26
2018-02-01 14:00 | 141.14 | 139.68
2018-02-01 14:30 | 160.77 | 159.52
2018-02-01 15:00 | 168.63 | 167.43
2018-02-01 15:30 | 161.02 | 159.8
2018-02-01 16:00 | 177.06 | 175.92
2018-02-01 16:30 | 180.48 | 179.34
2018-02-01 17:00 | 189.34 | 188.14
2018-02-01 17:30 | 161.11 | 159.78
2018-02-01 18:00 | 156.91 | 155.63
2018-02-01 18:30 | 160.77 | 160.59
2018-02-01 19:00 | 189.81 | 189.12
2018-02-01 19:30 | 168.95 | 168.23
2018-02-01 20:00 | 142.88 | 142.35
2018-02-01 20:30 | 138.32 | 138.32
2018-02-01 21:00 | 137.67 | 137.23
2018-02-01 21:30 | 138.11 | 137.48
2018-02-01 22:00 | 97.37 | 95.27
2018-02-01 22:30 | 97.24 | 95.09
2018-02-01 23:00 | 119.35 | 117.53
2018-02-01 23:30 | 82.05 | 80.39
2018-02-02 | 38.12 | 35.5
2018-02-02 00:30 | 12.01 | -2.54
2018-02-02 01:00 | 21.3 | -18.44
2018-02-02 01:30 | 19.18 | -15.77
2018-02-02 02:00 | 12 | -1.66
2018-02-02 02:30 | 14.79 | -8.6
2018-02-02 03:00 | 22.58 | -19.38
2018-02-02 03:30 | 25.27 | -22.25
2018-02-02 04:00 | 24.95 | -21.85
2018-02-02 04:30 | 21.59 | -17.54
2018-02-02 05:00 | 16.33 | -9.96
2018-02-02 05:30 | 13.14 | 1.46
2018-02-02 06:00 | 13.01 | 5.51
2018-02-02 06:30 | 14.12 | 11.74
2018-02-02 07:00 | 36.41 | 36.15
2018-02-02 07:30 | 53.73 | 51.31
2018-02-02 08:00 | 55.21 | 48.28
2018-02-02 08:30 | 65.78 | 45.53
2018-02-02 09:00 | 65.35 | 42.39
2018-02-02 09:30 | 77.46 | 59.3
2018-02-02 10:00 | 82.27 | 69.88
2018-02-02 10:30 | 81.3 | 68.58
2018-02-02 11:00 | 82.49 | 69.85
2018-02-02 11:30 | 90.35 | 80.74
2018-02-02 12:00 | 84.1 | 81.34
2018-02-02 12:30 | 87.39 | 85.1
2018-02-02 13:00 | 70.14 | 67.43
2018-02-02 13:30 | 69.39 | 66.71
2018-02-02 14:00 | 66.66 | 64.55
2018-02-02 14:30 | 89.31 | 88.21
2018-02-02 15:00 | 94.52 | 93.71
2018-02-02 15:30 | 105.31 | 104.81
2018-02-02 16:00 | 88.39 | 87.9
2018-02-02 16:30 | 108.91 | 108.58
2018-02-02 17:00 | 115.02 | 114.76
2018-02-02 17:30 | 124.37 | 124.03
2018-02-02 18:00 | 117.19 | 117.19
2018-02-02 18:30 | 122.57 | 122.42
2018-02-02 19:00 | 140.99 | 140.46
2018-02-02 19:30 | 131.95 | 130.97
2018-02-02 20:00 | 120.09 | 119.27
2018-02-02 20:30 | 119.67 | 119.23
2018-02-02 21:00 | 102.27 | 101.9
2018-02-02 21:30 | 61.84 | 61.47
2018-02-02 22:00 | 40.92 | 40.62
2018-02-02 22:30 | 54.4 | 54.25
2018-02-02 23:00 | 77.01 | 76.98
2018-02-02 23:30 | 59.93 | 59.89
2018-02-03 | 11.88 | 9.52
2018-02-03 00:30 | 8.89 | 3.61
2018-02-03 01:00 | 9.77 | -3.73
2018-02-03 01:30 | 13.93 | -10.87
2018-02-03 02:00 | 16.82 | -14.51
2018-02-03 02:30 | 18.39 | -16.25
2018-02-03 03:00 | 20.03 | -17.77
2018-02-03 03:30 | 20.69 | -19.3
2018-02-03 04:00 | 27.51 | -26.23
2018-02-03 04:30 | 38.32 | -36.24
2018-02-03 05:00 | 40.43 | -38.5
2018-02-03 05:30 | 33.59 | -30.96
2018-02-03 06:00 | 22.01 | -18.04
2018-02-03 06:30 | 13.6 | -1.98
2018-02-03 07:00 | 19.89 | 14.44
2018-02-03 07:30 | 49.15 | 47.47
2018-02-03 08:00 | 59.56 | 58.75
2018-02-03 08:30 | 79.95 | 79.71
2018-02-03 09:00 | 90.43 | 89.2
2018-02-03 09:30 | 96.04 | 94.76
2018-02-03 10:00 | 97.49 | 96.29
2018-02-03 10:30 | 100.09 | 98.8
2018-02-03 11:00 | 91.27 | 90.03
2018-02-03 11:30 | 97.98 | 96.79
2018-02-03 12:00 | 114.72 | 113.66
2018-02-03 12:30 | 118.83 | 117.82
2018-02-03 13:00 | 120.05 | 119.12
2018-02-03 13:30 | 113.46 | 112.42
2018-02-03 14:00 | 115.73 | 114.62
2018-02-03 14:30 | 115.6 | 114.54
2018-02-03 15:00 | 116.33 | 115.19
2018-02-03 15:30 | 111.68 | 110.45
2018-02-03 16:00 | 113.03 | 111.84
2018-02-03 16:30 | 114.53 | 113.39
2018-02-03 17:00 | 117.96 | 116.83
2018-02-03 17:30 | 117.63 | 116.57
2018-02-03 18:00 | 115.93 | 114.97
2018-02-03 18:30 | 118.01 | 117.01
2018-02-03 19:00 | 120.34 | 119.43
2018-02-03 19:30 | 123.33 | 122.49
2018-02-03 20:00 | 126.3 | 125.41
2018-02-03 20:30 | 121.61 | 121.21
2018-02-03 21:00 | 114.67 | 113.85
2018-02-03 21:30 | 110.48 | 110.03
2018-02-03 22:00 | 64.74 | 64.12
2018-02-03 22:30 | 53.43 | 52.83
2018-02-03 23:00 | 78.67 | 78.43
2018-02-03 23:30 | 65.91 | 65.73
2018-02-04 | 33.99 | 33.37
2018-02-04 00:30 | 4.86 | 0.92
2018-02-04 01:00 | 21.96 | -19.27
2018-02-04 01:30 | 30.95 | -29.44
2018-02-04 02:00 | 36.79 | -35.72
2018-02-04 02:30 | 42.11 | -41.21
2018-02-04 03:00 | 46.62 | -45.87
2018-02-04 03:30 | 44.83 | -43.93
2018-02-04 04:00 | 45.2 | -44.41
2018-02-04 04:30 | 49.04 | -48.28
2018-02-04 05:00 | 52.96 | -52.27
2018-02-04 05:30 | 57.74 | -57.29
2018-02-04 06:00 | 55.31 | -54.96
2018-02-04 06:30 | 35.42 | -34.53
2018-02-04 07:00 | 31.62 | -30.55
2018-02-04 07:30 | 30.49 | -29.44
2018-02-04 08:00 | 30.94 | -29.99
2018-02-04 08:30 | 18.33 | -17.27
2018-02-04 09:00 | 2.91 | -2.17
2018-02-04 09:30 | 4.29 | -4.22
2018-02-04 10:00 | 12.7 | 1.64
2018-02-04 10:30 | 25.09 | -5.54
2018-02-04 11:00 | 25.45 | -0.81
2018-02-04 11:30 | 26.15 | -6.02
2018-02-04 12:00 | 26.86 | -6.02
2018-02-04 12:30 | 28.24 | -10.32
2018-02-04 13:00 | 32.26 | -18.64
2018-02-04 13:30 | 34.12 | -21.66
2018-02-04 14:00 | 29.96 | -14.28
2018-02-04 14:30 | 27.48 | -6.91
2018-02-04 15:00 | 30.75 | -14.28
2018-02-04 15:30 | 27.83 | -8.05
2018-02-04 16:00 | 39.32 | 6.68
2018-02-04 16:30 | 58.87 | 10.05
2018-02-04 17:00 | 62.47 | 24.47
2018-02-04 17:30 | 68.26 | 39.33
2018-02-04 18:00 | 77.28 | 54.74
2018-02-04 18:30 | 90.41 | 73.68
2018-02-04 19:00 | 108.81 | 94.61
2018-02-04 19:30 | 125.35 | 113.49
2018-02-04 20:00 | 111.29 | 98.68
2018-02-04 20:30 | 97.52 | 84.02
2018-02-04 21:00 | 74.79 | 57.68
2018-02-04 21:30 | 64.99 | 44.9
2018-02-04 22:00 | 57.17 | 35.09
2018-02-04 22:30 | 45.77 | 45.56
2018-02-04 23:00 | 73.78 | 72.9
2018-02-04 23:30 | 60.19 | 58.89
2018-02-05 | 25.05 | 22.26
2018-02-05 00:30 | 14.29 | -10.42
2018-02-05 01:00 | 29.7 | -28.6
2018-02-05 01:30 | 46.41 | -45.89
2018-02-05 02:00 | 48.48 | -48.05
2018-02-05 02:30 | 41.32 | -40.73
2018-02-05 03:00 | 39.96 | -39.29
2018-02-05 03:30 | 43.41 | -42.76
2018-02-05 04:00 | 47.25 | -46.53
2018-02-05 04:30 | 53.76 | -53.18
2018-02-05 05:00 | 50.77 | -50.12
2018-02-05 05:30 | 49.85 | -49.36
2018-02-05 06:00 | 34.5 | -33.97
2018-02-05 06:30 | 9.26 | 8.32
2018-02-05 07:00 | 25.73 | 25.46
2018-02-05 07:30 | 28.8 | 28.18
2018-02-05 08:00 | 30.23 | 29.85
2018-02-05 08:30 | 16.49 | 16.48
2018-02-05 09:00 | 15.8 | 6.83
2018-02-05 09:30 | 46.4 | 10.47
2018-02-05 10:00 | 59.64 | 10.04
2018-02-05 10:30 | 60.84 | 6.02
2018-02-05 11:00 | 61.98 | 1.74
2018-02-05 11:30 | 62.41 | 6.28
2018-02-05 12:00 | 64.04 | 11.68
2018-02-05 12:30 | 63.29 | 2.41
2018-02-05 13:00 | 64.48 | 9.58
2018-02-05 13:30 | 63.96 | 4.95
2018-02-05 14:00 | 63.24 | 4.19
2018-02-05 14:30 | 63.79 | 14.78
2018-02-05 15:00 | 68.37 | 31.11
2018-02-05 15:30 | 68.13 | 34.4
2018-02-05 16:00 | 66.89 | 41.41
2018-02-05 16:30 | 61.74 | 35.61
2018-02-05 17:00 | 98.62 | 86.44
2018-02-05 17:30 | 111.97 | 107.72
2018-02-05 18:00 | 102.3 | 100.81
2018-02-05 18:30 | 108.45 | 107.41
2018-02-05 19:00 | 114.7 | 113.67
2018-02-05 19:30 | 118.17 | 117.23
2018-02-05 20:00 | 117.98 | 117.51
2018-02-05 20:30 | 116.84 | 116.19
2018-02-05 21:00 | 82.6 | 82.16
2018-02-05 21:30 | 79.98 | 77.88
2018-02-05 22:00 | 57.47 | 55.56
2018-02-05 22:30 | 51.54 | 50.09
2018-02-05 23:00 | 74.1 | 73.49
2018-02-05 23:30 | 49.18 | 48.59
2018-02-06 | 8.92 | -0.04
2018-02-06 00:30 | 33.13 | -31.22
2018-02-06 01:00 | 51.2 | -49.65
2018-02-06 01:30 | 58.5 | -56.93
2018-02-06 02:00 | 56.62 | -55.04
2018-02-06 02:30 | 56.58 | -56.58
2018-02-06 03:00 | 48.05 | -47.48
2018-02-06 03:30 | 32.73 | -31.45
2018-02-06 04:00 | 35.95 | -34.65
2018-02-06 04:30 | 32.69 | -31.02
2018-02-06 05:00 | 19.71 | -16.72
2018-02-06 05:30 | 9.89 | 0.45
2018-02-06 06:00 | 34.43 | 32.8
2018-02-06 06:30 | 59.32 | 58.81
2018-02-06 07:00 | 66.14 | 66.04
2018-02-06 07:30 | 74.15 | 72.17
2018-02-06 08:00 | 80.61 | 67.21
2018-02-06 08:30 | 87.58 | 59.43
2018-02-06 09:00 | 86.09 | 54.63
2018-02-06 09:30 | 88.53 | 55.52
2018-02-06 10:00 | 81.36 | 40.51
2018-02-06 10:30 | 83.93 | 43.59
2018-02-06 11:00 | 79.2 | 29.87
2018-02-06 11:30 | 76.87 | 20.53
2018-02-06 12:00 | 82.04 | 33.03
2018-02-06 12:30 | 84.1 | 39.18
2018-02-06 13:00 | 84.98 | 38.67
2018-02-06 13:30 | 86.59 | 40.42
2018-02-06 14:00 | 88.21 | 43.91
2018-02-06 14:30 | 90.42 | 49.62
2018-02-06 15:00 | 80.99 | 30.03
2018-02-06 15:30 | 78.02 | 23.34
2018-02-06 16:00 | 84.04 | 42.65
2018-02-06 16:30 | 94.84 | 62.85
2018-02-06 17:00 | 113.52 | 91.04
2018-02-06 17:30 | 120.3 | 102.28
2018-02-06 18:00 | 142.64 | 129.43
2018-02-06 18:30 | 157.98 | 147.54
2018-02-06 19:00 | 175.24 | 165.6
2018-02-06 19:30 | 173.87 | 163.89
2018-02-06 20:00 | 171.74 | 162.19
2018-02-06 20:30 | 162.16 | 153.33
2018-02-06 21:00 | 132.05 | 121.22
2018-02-06 21:30 | 115.77 | 104.36
2018-02-06 22:00 | 93.39 | 79.71
2018-02-06 22:30 | 95.65 | 83.42
2018-02-06 23:00 | 92.49 | 89.34
2018-02-06 23:30 | 62.43 | 61.38
2018-02-07 | 11.05 | 7.57
2018-02-07 00:30 | 24.93 | -24.03
2018-02-07 01:00 | 35.69 | -35.27
2018-02-07 01:30 | 42.3 | -42.14
2018-02-07 02:00 | 39.12 | -38.92
2018-02-07 02:30 | 32.16 | -31.84
2018-02-07 03:00 | 32.67 | -32.47
2018-02-07 03:30 | 32.47 | -32.19
2018-02-07 04:00 | 32.88 | -32.54
2018-02-07 04:30 | 39.91 | -39.62
2018-02-07 05:00 | 34.66 | -34.3
2018-02-07 05:30 | 17.09 | -16.35
2018-02-07 06:00 | 7.28 | 4.8
2018-02-07 06:30 | 44.69 | 44.67
2018-02-07 07:00 | 74.08 | 74.08
2018-02-07 07:30 | 87.76 | 86.7
2018-02-07 08:00 | 76.08 | 71.3
2018-02-07 08:30 | 55.93 | 46.42
2018-02-07 09:00 | 48.55 | 33.53
2018-02-07 09:30 | 53.95 | 39.49
2018-02-07 10:00 | 41.13 | 21.34
2018-02-07 10:30 | 36.77 | 12.25
2018-02-07 11:00 | 37.87 | 13.84
2018-02-07 11:30 | 40.1 | 12.67
2018-02-07 12:00 | 40.53 | 12.7
2018-02-07 12:30 | 40.59 | 12.66
2018-02-07 13:00 | 57.82 | -12.94
2018-02-07 13:30 | 100.34 | 72.09
2018-02-07 14:00 | 139.6 | 122.65
2018-02-07 14:30 | 136.73 | 120.91
2018-02-07 15:00 | 137.3 | 120.14
2018-02-07 15:30 | 176.73 | 164.52
2018-02-07 16:00 | 164.73 | 152.13
2018-02-07 16:30 | 136.25 | 120.36
2018-02-07 17:00 | 179.96 | 169.24
2018-02-07 17:30 | 183.91 | 174.55
2018-02-07 18:00 | 203.52 | 196.45
2018-02-07 18:30 | 172.72 | 166.05
2018-02-07 19:00 | 168.24 | 161.26
2018-02-07 19:30 | 154.05 | 146.94
2018-02-07 20:00 | 146.55 | 145.54
2018-02-07 20:30 | 142.25 | 141.48
2018-02-07 21:00 | 132.35 | 131.72
2018-02-07 21:30 | 126.36 | 125.94
2018-02-07 22:00 | 120.18 | 119.99
2018-02-07 22:30 | 110.73 | 110.63
2018-02-07 23:00 | 128.33 | 128.05
2018-02-07 23:30 | 102.42 | 102.12
2018-02-08 | 100.6 | 100.32
2018-02-08 00:30 | 88.26 | 88.02
2018-02-08 01:00 | 91.6 | 91.09
2018-02-08 01:30 | 98.12 | 97.09
2018-02-08 02:00 | 97.86 | 96.89
2018-02-08 02:30 | 98.4 | 97.35
2018-02-08 03:00 | 99.83 | 98.84
2018-02-08 03:30 | 100.21 | 99.18
2018-02-08 04:00 | 100.38 | 99.24
2018-02-08 04:30 | 100.96 | 99.76
2018-02-08 05:00 | 13.5 | -1.96
2018-02-08 05:30 | 14.16 | 9.18
2018-02-08 06:00 | 28.76 | 26.49
2018-02-08 06:30 | 69.25 | 68.74
2018-02-08 07:00 | 99.76 | 99.65
2018-02-08 07:30 | 128.86 | 128.57
2018-02-08 08:00 | 103.99 | 98.72
2018-02-08 08:30 | 111.96 | 92.86
2018-02-08 09:00 | 95.66 | 71.78
2018-02-08 09:30 | 92.25 | 69.72
2018-02-08 10:00 | 95.21 | 68.93
2018-02-08 10:30 | 96.09 | 67.7
2018-02-08 11:00 | 95.58 | 66.05
2018-02-08 11:30 | 96.49 | 66.9
2018-02-08 12:00 | 97.41 | 67.92
2018-02-08 12:30 | 87.02 | 55.89
2018-02-08 13:00 | 69.06 | -9.43
2018-02-08 13:30 | 73 | -19.5
2018-02-08 14:00 | 59.89 | 0.91
2018-02-08 14:30 | 58.2 | 23.73
2018-02-08 15:00 | 55.94 | 18.97
2018-02-08 15:30 | 53.03 | 9.48
2018-02-08 16:00 | 59.21 | 28.73
2018-02-08 16:30 | 68.6 | 47.73
2018-02-08 17:00 | 67.55 | 47.99
2018-02-08 17:30 | 80.2 | 66.78
2018-02-08 18:00 | 86.4 | 75.08
2018-02-08 18:30 | 90.42 | 81.36
2018-02-08 19:00 | 129.71 | 123.47
2018-02-08 19:30 | 150.13 | 144.83
2018-02-08 20:00 | 132.82 | 127.41
2018-02-08 20:30 | 103.16 | 97.33
2018-02-08 21:00 | 100.23 | 88.75
2018-02-08 21:30 | 98.63 | 88.1
2018-02-08 22:00 | 102.6 | 101.58
2018-02-08 22:30 | 103.28 | 103.16
2018-02-08 23:00 | 115.12 | 115.09
2018-02-08 23:30 | 89.11 | 89.11
2018-02-09 | 46.27 | 45.98
2018-02-09 00:30 | 11.52 | 2.27
2018-02-09 01:00 | 19.97 | -17.42
2018-02-09 01:30 | 26.09 | -24.26
2018-02-09 02:00 | 37.26 | -36.33
2018-02-09 02:30 | 32.09 | -30.97
2018-02-09 03:00 | 45.28 | -44.63
2018-02-09 03:30 | 45.75 | -45
2018-02-09 04:00 | 43.35 | -42.6
2018-02-09 04:30 | 30.15 | -28.84
2018-02-09 05:00 | 12.38 | -7.75
2018-02-09 05:30 | 10.22 | 4.02
2018-02-09 06:00 | 9.9 | 6.83
2018-02-09 06:30 | 23.37 | 23.25
2018-02-09 07:00 | 106.72 | 106.71
2018-02-09 07:30 | 153.32 | 151.13
2018-02-09 08:00 | 172.48 | 159.16
2018-02-09 08:30 | 172.42 | 160.01
2018-02-09 09:00 | 171.43 | 165.89
2018-02-09 09:30 | 169.39 | 162.9
2018-02-09 10:00 | 171.06 | 164.37
2018-02-09 10:30 | 168.37 | 162.93
2018-02-09 11:00 | 170.38 | 164.81
2018-02-09 11:30 | 169.06 | 163.22
2018-02-09 12:00 | 168.64 | 162.87
2018-02-09 12:30 | 169.45 | 163.71
2018-02-09 13:00 | 170.01 | 164.26
2018-02-09 13:30 | 172.94 | 167.16
2018-02-09 14:00 | 176.22 | 171.04
2018-02-09 14:30 | 178.96 | 173.83
2018-02-09 15:00 | 179.33 | 174.36
2018-02-09 15:30 | 139.42 | 134.55
2018-02-09 16:00 | 86.27 | 78.99
2018-02-09 16:30 | 109.55 | 104.49
2018-02-09 17:00 | 127.2 | 123.27
2018-02-09 17:30 | 138.01 | 135.18
2018-02-09 18:00 | 157.17 | 155.63
2018-02-09 18:30 | 140.39 | 139.64
2018-02-09 19:00 | 164.48 | 159.02
2018-02-09 19:30 | 158.03 | 146.67
2018-02-09 20:00 | 176.4 | 152.37
2018-02-09 20:30 | 180.65 | 158.63
2018-02-09 21:00 | 175.55 | 154.79
2018-02-09 21:30 | 160.55 | 139.63
2018-02-09 22:00 | 128.03 | 98.62
2018-02-09 22:30 | 129.64 | 100.57
2018-02-09 23:00 | 132.04 | 117.09
2018-02-09 23:30 | 107.62 | 98.21
2018-02-10 | 62.5 | 44.91
2018-02-10 00:30 | 43.99 | -0.96
2018-02-10 01:00 | 47.61 | -16.15
2018-02-10 01:30 | 49.67 | -19.63
2018-02-10 02:00 | 57.99 | -33.03
2018-02-10 02:30 | 61.82 | -39.46
2018-02-10 03:00 | 69.06 | -48.82
2018-02-10 03:30 | 72.43 | -53.22
2018-02-10 04:00 | 68.8 | -49.01
2018-02-10 04:30 | 65.42 | -44.67
2018-02-10 05:00 | 61.44 | -38.96
2018-02-10 05:30 | 58.81 | -34.44
2018-02-10 06:00 | 62.67 | -38.59
2018-02-10 06:30 | 58.13 | -31.75
2018-02-10 07:00 | 51.89 | -19.28
2018-02-10 07:30 | 55.48 | -18.45
2018-02-10 08:00 | 19.45 | -18.18
2018-02-10 08:30 | 11.56 | -4.47
2018-02-10 09:00 | 12.99 | 4.79
2018-02-10 09:30 | 21.76 | 7.69
2018-02-10 10:00 | 47.34 | 7
2018-02-10 10:30 | 71.35 | 13.55
2018-02-10 11:00 | 72.32 | 10.48
2018-02-10 11:30 | 73.15 | 7.87
2018-02-10 12:00 | 75.75 | 19.13
2018-02-10 12:30 | 81.07 | 33.09
2018-02-10 13:00 | 83.48 | 36.76
2018-02-10 13:30 | 111.13 | 82.52
2018-02-10 14:00 | 122.72 | 98.02
2018-02-10 14:30 | 125.73 | 102.09
2018-02-10 15:00 | 133.3 | 115.3
2018-02-10 15:30 | 159.25 | 144.03
2018-02-10 16:00 | 172.96 | 159.78
2018-02-10 16:30 | 185.16 | 177.4
2018-02-10 17:00 | 177.86 | 170.37
2018-02-10 17:30 | 169.53 | 162.93
2018-02-10 18:00 | 173.55 | 170.96
2018-02-10 18:30 | 182.24 | 180.93
2018-02-10 19:00 | 193.09 | 191.44
2018-02-10 19:30 | 197.02 | 195.36
2018-02-10 20:00 | 200.24 | 198.79
2018-02-10 20:30 | 193.23 | 191.45
2018-02-10 21:00 | 185.41 | 183.87
2018-02-10 21:30 | 178.61 | 178.59
2018-02-10 22:00 | 176.02 | 175.34
2018-02-10 22:30 | 170.91 | 169.99
2018-02-10 23:00 | 171.61 | 170.54
2018-02-10 23:30 | 158.8 | 157.7
2018-02-11 | 140.91 | 139.85
2018-02-11 00:30 | 131.27 | 128.8
2018-02-11 01:00 | 130.79 | 128.3
2018-02-11 01:30 | 130.3 | 127.99
2018-02-11 02:00 | 127.45 | 126.49
2018-02-11 02:30 | 125.63 | 125.16
2018-02-11 03:00 | 124.64 | 124.17
2018-02-11 03:30 | 123.12 | 122.66
2018-02-11 04:00 | 121.87 | 121.41
2018-02-11 04:30 | 120.62 | 120.15
2018-02-11 05:00 | 119.9 | 119.36
2018-02-11 05:30 | 119.08 | 118.49
2018-02-11 06:00 | 118.59 | 117.87
2018-02-11 06:30 | 118.72 | 118.09
2018-02-11 07:00 | 120.48 | 119.99
2018-02-11 07:30 | 127.14 | 126.92
2018-02-11 08:00 | 134.77 | 134.75
2018-02-11 08:30 | 143.6 | 143.52
2018-02-11 09:00 | 153.59 | 152.14
2018-02-11 09:30 | 162.56 | 160.61
2018-02-11 10:00 | 171.4 | 169.03
2018-02-11 10:30 | 182.31 | 175.67
2018-02-11 11:00 | 191.36 | 177.49
2018-02-11 11:30 | 195.84 | 181.3
2018-02-11 12:00 | 201.06 | 187.05
2018-02-11 12:30 | 201.41 | 191.45
2018-02-11 13:00 | 208.13 | 197.65
2018-02-11 13:30 | 213.21 | 205.36
2018-02-11 14:00 | 216.76 | 209.52
2018-02-11 14:30 | 223.45 | 215.72
2018-02-11 15:00 | 227.98 | 219.92
2018-02-11 15:30 | 232.92 | 224.78
2018-02-11 16:00 | 238.61 | 230.24
2018-02-11 16:30 | 244.42 | 231.53
2018-02-11 17:00 | 242.43 | 228.65
2018-02-11 17:30 | 235.19 | 222.48
2018-02-11 18:00 | 236.69 | 223.89
2018-02-11 18:30 | 231.09 | 216.47
2018-02-11 19:00 | 229.22 | 211.74
2018-02-11 19:30 | 213.09 | 207.15
2018-02-11 20:00 | 210.22 | 204.8
2018-02-11 20:30 | 204.17 | 199.38
2018-02-11 21:00 | 189.34 | 188.29
2018-02-11 21:30 | 183.56 | 183.22
2018-02-11 22:00 | 176.71 | 176.65
2018-02-11 22:30 | 168.22 | 168.21
2018-02-11 23:00 | 164.48 | 163.02
2018-02-11 23:30 | 151.29 | 149.14
2018-02-12 | 132.86 | 132.71
2018-02-12 00:30 | 123.07 | 122.98
2018-02-12 01:00 | 121.94 | 121.86
2018-02-12 01:30 | 121.24 | 121.11
2018-02-12 02:00 | 119.43 | 119.23
2018-02-12 02:30 | 118.16 | 117.84
2018-02-12 03:00 | 117.36 | 117.01
2018-02-12 03:30 | 115.6 | 115.19
2018-02-12 04:00 | 114.82 | 114.37
2018-02-12 04:30 | 114.45 | 114.01
2018-02-12 05:00 | 116.12 | 115.71
2018-02-12 05:30 | 116.84 | 116.48
2018-02-12 06:00 | 124.12 | 123.77
2018-02-12 06:30 | 138.73 | 136.96
2018-02-12 07:00 | 151.32 | 150.57
2018-02-12 07:30 | 166.94 | 166.71
2018-02-12 08:00 | 178.86 | 177.59
2018-02-12 08:30 | 188.2 | 181.2
2018-02-12 09:00 | 198.17 | 190.41
2018-02-12 09:30 | 204.61 | 195.55
2018-02-12 10:00 | 213.37 | 203.74
2018-02-12 10:30 | 213.41 | 202.95
2018-02-12 11:00 | 216.35 | 208.97
2018-02-12 11:30 | 219.66 | 214.76
2018-02-12 12:00 | 222.72 | 218.4
2018-02-12 12:30 | 223.46 | 219.15
2018-02-12 13:00 | 226.14 | 222.25
2018-02-12 13:30 | 230.79 | 226.65
2018-02-12 14:00 | 240.38 | 236.35
2018-02-12 14:30 | 259.03 | 255.03
2018-02-12 15:00 | 261.85 | 257.99
2018-02-12 15:30 | 270.79 | 266.78
2018-02-12 16:00 | 316.65 | 312.18
2018-02-12 16:30 | 327.67 | 322.89
2018-02-12 17:00 | 337.3 | 332.55
2018-02-12 17:30 | 341.24 | 337.08
2018-02-12 18:00 | 333.08 | 330.04
2018-02-12 18:30 | 326.39 | 324.2
2018-02-12 19:00 | 334.18 | 331.24
2018-02-12 19:30 | 335.36 | 332.5
2018-02-12 20:00 | 330.2 | 327.82
2018-02-12 20:30 | 312.76 | 310.88
2018-02-12 21:00 | 297.77 | 296.3
2018-02-12 21:30 | 278.1 | 277.8
2018-02-12 22:00 | 237.9 | 237.75
2018-02-12 22:30 | 235.23 | 234.9
2018-02-12 23:00 | 228.85 | 228.84
2018-02-12 23:30 | 188.88 | 188.26
2018-02-13 | 148.52 | 147.38
2018-02-13 00:30 | 126.39 | 125.17
2018-02-13 01:00 | 105.89 | 104.46
2018-02-13 01:30 | 95.64 | 93.08
2018-02-13 02:00 | 96.93 | 93.88
2018-02-13 02:30 | 92.42 | 89.07
2018-02-13 03:00 | 87.88 | 84.32
2018-02-13 03:30 | 83.5 | 79.72
2018-02-13 04:00 | 83.28 | 79.64
2018-02-13 04:30 | 89.26 | 86.07
2018-02-13 05:00 | 97.85 | 95.18
2018-02-13 05:30 | 130.46 | 129.05
2018-02-13 06:00 | 144.36 | 143.57
2018-02-13 06:30 | 173.7 | 173.05
2018-02-13 07:00 | 199.21 | 197.6
2018-02-13 07:30 | 233.18 | 230.99
2018-02-13 08:00 | 240.71 | 235.98
2018-02-13 08:30 | 261.8 | 252.1
2018-02-13 09:00 | 269.76 | 258.71
2018-02-13 09:30 | 258.36 | 245.9
2018-02-13 10:00 | 247.14 | 230.28
2018-02-13 10:30 | 256.87 | 235.35
2018-02-13 11:00 | 267.55 | 246.26
2018-02-13 11:30 | 284.48 | 265.16
2018-02-13 12:00 | 280.1 | 266.37
2018-02-13 12:30 | 266.67 | 258.57
2018-02-13 13:00 | 268.82 | 260.65
2018-02-13 13:30 | 270.71 | 262.13
2018-02-13 14:00 | 292.45 | 283.98
2018-02-13 14:30 | 305.03 | 296.19
2018-02-13 15:00 | 308.38 | 299.45
2018-02-13 15:30 | 319.01 | 310.09
2018-02-13 16:00 | 334.34 | 326.54
2018-02-13 16:30 | 344.24 | 338.24
2018-02-13 17:00 | 350.7 | 344.75
2018-02-13 17:30 | 344.45 | 339.59
2018-02-13 18:00 | 338.64 | 334.63
2018-02-13 18:30 | 339.21 | 335.37
2018-02-13 19:00 | 343.17 | 339.18
2018-02-13 19:30 | 318.31 | 315.43
2018-02-13 20:00 | 298.29 | 296.23
2018-02-13 20:30 | 269.65 | 268.34
2018-02-13 21:00 | 237.27 | 236.95
2018-02-13 21:30 | 211.54 | 211.39
2018-02-13 22:00 | 164.27 | 164.16
2018-02-13 22:30 | 170.85 | 167.92
2018-02-13 23:00 | 174.25 | 170.75
2018-02-13 23:30 | 125.71 | 121.59
2018-02-14 | 81.26 | 72.06
2018-02-14 00:30 | 66.69 | 55.23
2018-02-14 01:00 | 51.89 | 36.94
2018-02-14 01:30 | 49.67 | 34.96
2018-02-14 02:00 | 51.06 | 37.67
2018-02-14 02:30 | 46.2 | 31.72
2018-02-14 03:00 | 43.34 | 27.63
2018-02-14 03:30 | 51.27 | 39.18
2018-02-14 04:00 | 62.05 | 52.76
2018-02-14 04:30 | 44.55 | 28.97
2018-02-14 05:00 | 46.35 | 30.42
2018-02-14 05:30 | 52.03 | 37.01
2018-02-14 06:00 | 55.8 | 37.57
2018-02-14 06:30 | 113.22 | 81.61
2018-02-14 07:00 | 141.12 | 114.38
2018-02-14 07:30 | 156.4 | 131.08
2018-02-14 08:00 | 148.21 | 127.2
2018-02-14 08:30 | 153.33 | 132.32
2018-02-14 09:00 | 181.63 | 161.71
2018-02-14 09:30 | 202.73 | 182.17
2018-02-14 10:00 | 225.89 | 205.67
2018-02-14 10:30 | 244.63 | 217.28
2018-02-14 11:00 | 257.94 | 230.72
2018-02-14 11:30 | 264.99 | 237.71
2018-02-14 12:00 | 281.97 | 256.65
2018-02-14 12:30 | 295.05 | 270.97
2018-02-14 13:00 | 302.47 | 277.99
2018-02-14 13:30 | 311.52 | 286.83
2018-02-14 14:00 | 322.3 | 297.07
2018-02-14 14:30 | 326.57 | 303.73
2018-02-14 15:00 | 329.57 | 309.68
2018-02-14 15:30 | 338.19 | 318.62
2018-02-14 16:00 | 353.44 | 333.77
2018-02-14 16:30 | 366.21 | 347.13
2018-02-14 17:00 | 371.33 | 352.61
2018-02-14 17:30 | 368.56 | 351.47
2018-02-14 18:00 | 360.99 | 345.16
2018-02-14 18:30 | 353.58 | 339.23
2018-02-14 19:00 | 351.49 | 337.02
2018-02-14 19:30 | 346.69 | 332.63
2018-02-14 20:00 | 333.42 | 320.55
2018-02-14 20:30 | 326.03 | 314.82
2018-02-14 21:00 | 313.62 | 304.33
2018-02-14 21:30 | 289.96 | 281.95
2018-02-14 22:00 | 268.05 | 262.36
2018-02-14 22:30 | 245.21 | 239.8
2018-02-14 23:00 | 241.57 | 235.22
2018-02-14 23:30 | 217.39 | 211.81
2018-02-15 | 150.58 | 149.63
2018-02-15 00:30 | 108.52 | 107.64
2018-02-15 01:00 | 97.83 | 96.25
2018-02-15 01:30 | 88.83 | 85.96
2018-02-15 02:00 | 95.38 | 92.65
2018-02-15 02:30 | 103.21 | 101.13
2018-02-15 03:00 | 78.18 | 75.36
2018-02-15 03:30 | 64.33 | 60.61
2018-02-15 04:00 | 55.28 | 50.7
2018-02-15 04:30 | 59.36 | 54.8
2018-02-15 05:00 | 71.54 | 67.55
2018-02-15 05:30 | 68.55 | 62.8
2018-02-15 06:00 | 89.47 | 76.68
2018-02-15 06:30 | 136.07 | 119.52
2018-02-15 07:00 | 177.98 | 163.98
2018-02-15 07:30 | 201.29 | 182.74
2018-02-15 08:00 | 224.33 | 204.33
2018-02-15 08:30 | 241.21 | 220.9
2018-02-15 09:00 | 271.48 | 251.32
2018-02-15 09:30 | 300.37 | 281.52
2018-02-15 10:00 | 306.9 | 293.19
2018-02-15 10:30 | 306.89 | 292.57
2018-02-15 11:00 | 308.45 | 293.51
2018-02-15 11:30 | 309.54 | 294.61
2018-02-15 12:00 | 308.69 | 293.4
2018-02-15 12:30 | 310.9 | 295.99
2018-02-15 13:00 | 312.25 | 297.81
2018-02-15 13:30 | 316.88 | 302.49
2018-02-15 14:00 | 320.21 | 305.61
2018-02-15 14:30 | 324.85 | 310.11
2018-02-15 15:00 | 329.61 | 315.11
2018-02-15 15:30 | 335.61 | 321.45
2018-02-15 16:00 | 356.4 | 340.22
2018-02-15 16:30 | 356.13 | 341.46
2018-02-15 17:00 | 349.64 | 340.04
2018-02-15 17:30 | 344.94 | 336.14
2018-02-15 18:00 | 343.6 | 335.77
2018-02-15 18:30 | 339.28 | 332.19
2018-02-15 19:00 | 338.49 | 330.77
2018-02-15 19:30 | 338.08 | 330.54
2018-02-15 20:00 | 327.74 | 321.03
2018-02-15 20:30 | 323.38 | 318.34
2018-02-15 21:00 | 309.58 | 307.38
2018-02-15 21:30 | 281.98 | 279.45
2018-02-15 22:00 | 261.83 | 255.84
2018-02-15 22:30 | 236.5 | 232.22
2018-02-15 23:00 | 230.35 | 228.24
2018-02-15 23:30 | 213.53 | 211.2
2018-02-16 | 194.31 | 192.24
2018-02-16 00:30 | 177.94 | 177.09
2018-02-16 01:00 | 165.65 | 165.65
2018-02-16 01:30 | 157.53 | 157.53
2018-02-16 02:00 | 166.19 | 166.18
2018-02-16 02:30 | 161.64 | 161.63
2018-02-16 03:00 | 151.48 | 151.47
2018-02-16 03:30 | 147.64 | 147.63
2018-02-16 04:00 | 146.18 | 146.16
2018-02-16 04:30 | 148.21 | 148.21
2018-02-16 05:00 | 153.5 | 153.49
2018-02-16 05:30 | 164.82 | 164.38
2018-02-16 06:00 | 174.37 | 173.17
2018-02-16 06:30 | 197.85 | 193.98
2018-02-16 07:00 | 218.07 | 214.92
2018-02-16 07:30 | 236.96 | 234.24
2018-02-16 08:00 | 248.1 | 245.18
2018-02-16 08:30 | 257.98 | 254.61
2018-02-16 09:00 | 274.95 | 264.12
2018-02-16 09:30 | 282.78 | 271.83
2018-02-16 10:00 | 280.22 | 271.48
2018-02-16 10:30 | 283.32 | 274.24
2018-02-16 11:00 | 286.63 | 277.4
2018-02-16 11:30 | 289.33 | 280.17
2018-02-16 12:00 | 290.43 | 281
2018-02-16 12:30 | 290.9 | 281.45
2018-02-16 13:00 | 293.41 | 283.78
2018-02-16 13:30 | 300.34 | 289.03
2018-02-16 14:00 | 310.9 | 295.11
2018-02-16 14:30 | 316.72 | 301.3
2018-02-16 15:00 | 318.88 | 310.42
2018-02-16 15:30 | 337.46 | 328.92
2018-02-16 16:00 | 336.78 | 328.72
2018-02-16 16:30 | 338.88 | 331.41
2018-02-16 17:00 | 340.09 | 333.25
2018-02-16 17:30 | 327.03 | 321.64
2018-02-16 18:00 | 312.4 | 308.43
2018-02-16 18:30 | 297.84 | 294.86
2018-02-16 19:00 | 296.01 | 294.08
2018-02-16 19:30 | 293.02 | 291.36
2018-02-16 20:00 | 285.65 | 284.27
2018-02-16 20:30 | 271.11 | 269.67
2018-02-16 21:00 | 245.21 | 242.61
2018-02-16 21:30 | 206.37 | 204.2
2018-02-16 22:00 | 156.9 | 154.86
2018-02-16 22:30 | 182.91 | 181.63
2018-02-16 23:00 | 210.21 | 209.89
2018-02-16 23:30 | 180.32 | 179.46
2018-02-17 | 132.13 | 130.89
2018-02-17 00:30 | 97.94 | 96.67
2018-02-17 01:00 | 87.64 | 86.58
2018-02-17 01:30 | 72.89 | 71.37
2018-02-17 02:00 | 55.78 | 52.52
2018-02-17 02:30 | 43.35 | 39.08
2018-02-17 03:00 | 41.3 | 37.15
2018-02-17 03:30 | 42.8 | 38.77
2018-02-17 04:00 | 39.54 | 34.4
2018-02-17 04:30 | 45.21 | 40.17
2018-02-17 05:00 | 42.83 | 37.12
2018-02-17 05:30 | 40.33 | 33.76
2018-02-17 06:00 | 38.02 | 30.71
2018-02-17 06:30 | 53.3 | 46.92
2018-02-17 07:00 | 85.37 | 71.02
2018-02-17 07:30 | 106.35 | 82.42
2018-02-17 08:00 | 122.39 | 100.46
2018-02-17 08:30 | 138.1 | 118.9
2018-02-17 09:00 | 153.41 | 139.56
2018-02-17 09:30 | 155.43 | 142.5
2018-02-17 10:00 | 159.46 | 145.55
2018-02-17 10:30 | 159.99 | 145.24
2018-02-17 11:00 | 167.83 | 152.96
2018-02-17 11:30 | 169.19 | 153.97
2018-02-17 12:00 | 177.88 | 163.07
2018-02-17 12:30 | 173.69 | 158.41
2018-02-17 13:00 | 178.26 | 162.88
2018-02-17 13:30 | 182.73 | 166.79
2018-02-17 14:00 | 190.44 | 175.2
2018-02-17 14:30 | 203.94 | 189.61
2018-02-17 15:00 | 211.68 | 197.74
2018-02-17 15:30 | 226.44 | 213.32
2018-02-17 16:00 | 226.43 | 217.32
2018-02-17 16:30 | 238.1 | 231.14
2018-02-17 17:00 | 242.66 | 235.98
2018-02-17 17:30 | 262.34 | 256.62
2018-02-17 18:00 | 254.36 | 249.33
2018-02-17 18:30 | 247.68 | 243.74
2018-02-17 19:00 | 273.11 | 269.04
2018-02-17 19:30 | 270.95 | 267.08
2018-02-17 20:00 | 246.5 | 243.26
2018-02-17 20:30 | 230.52 | 229.7
2018-02-17 21:00 | 192.85 | 191.92
2018-02-17 21:30 | 177.26 | 176.65
2018-02-17 22:00 | 153.88 | 153.49
2018-02-17 22:30 | 169.44 | 168
2018-02-17 23:00 | 172.86 | 171.69
2018-02-17 23:30 | 151.52 | 150.68
2018-02-18 | 105.57 | 104.83
2018-02-18 00:30 | 71.92 | 71.36
2018-02-18 01:00 | 52.52 | 50.58
2018-02-18 01:30 | 43.13 | 40.6
2018-02-18 02:00 | 39.66 | 36.57
2018-02-18 02:30 | 37.5 | 34.22
2018-02-18 03:00 | 35.09 | 31.79
2018-02-18 03:30 | 33.66 | 30.55
2018-02-18 04:00 | 31.68 | 28.45
2018-02-18 04:30 | 30.65 | 26.9
2018-02-18 05:00 | 30.84 | 26.76
2018-02-18 05:30 | 30.29 | 26.02
2018-02-18 06:00 | 29.23 | 24.64
2018-02-18 06:30 | 29.5 | 24.2
2018-02-18 07:00 | 34.71 | 28.78
2018-02-18 07:30 | 41.7 | 33.99
2018-02-18 08:00 | 54.94 | 41.53
2018-02-18 08:30 | 85.49 | 49.39
2018-02-18 09:00 | 92.04 | 55.6
2018-02-18 09:30 | 101.29 | 66.81
2018-02-18 10:00 | 110.54 | 80.29
2018-02-18 10:30 | 104.14 | 81.15
2018-02-18 11:00 | 108.51 | 85.78
2018-02-18 11:30 | 109.06 | 90.25
2018-02-18 12:00 | 119.39 | 102
2018-02-18 12:30 | 119.04 | 101.25
2018-02-18 13:00 | 115.72 | 96.88
2018-02-18 13:30 | 129.67 | 112.84
2018-02-18 14:00 | 155.49 | 141.16
2018-02-18 14:30 | 152.4 | 137.66
2018-02-18 15:00 | 139.16 | 121.88
2018-02-18 15:30 | 139.63 | 121.46
2018-02-18 16:00 | 159.07 | 143.44
2018-02-18 16:30 | 190.98 | 178.7
2018-02-18 17:00 | 220.82 | 210.1
2018-02-18 17:30 | 230.17 | 220.93
2018-02-18 18:00 | 227.92 | 219.32
2018-02-18 18:30 | 226.62 | 219.03
2018-02-18 19:00 | 244.86 | 236.9
2018-02-18 19:30 | 242.65 | 235.18
2018-02-18 20:00 | 228.11 | 221.2
2018-02-18 20:30 | 221.22 | 215.51
2018-02-18 21:00 | 185.7 | 183.5
2018-02-18 21:30 | 153.7 | 152.44
2018-02-18 22:00 | 115.81 | 115.23
2018-02-18 22:30 | 107.87 | 107.86
2018-02-18 23:00 | 106.47 | 106.34
2018-02-18 23:30 | 100.75 | 100.38
2018-02-19 | 51.58 | 51.42
2018-02-19 00:30 | 28.88 | 28.86
2018-02-19 01:00 | 27.2 | 27.1
2018-02-19 01:30 | 26.03 | 25.92
2018-02-19 02:00 | 23.51 | 23.35
2018-02-19 02:30 | 21.21 | 21.02
2018-02-19 03:00 | 20.68 | 20.46
2018-02-19 03:30 | 20.53 | 20.28
2018-02-19 04:00 | 21.12 | 20.72
2018-02-19 04:30 | 21.77 | 21.41
2018-02-19 05:00 | 21.55 | 21.29
2018-02-19 05:30 | 22.77 | 22.73
2018-02-19 06:00 | 34.65 | 34.65
2018-02-19 06:30 | 72.02 | 71.89
2018-02-19 07:00 | 116.76 | 115.54
2018-02-19 07:30 | 125.73 | 115.82
2018-02-19 08:00 | 121.77 | 111.9
2018-02-19 08:30 | 122.82 | 113.28
2018-02-19 09:00 | 124.52 | 112.78
2018-02-19 09:30 | 134.57 | 124.17
2018-02-19 10:00 | 130.33 | 120.94
2018-02-19 10:30 | 124.6 | 113.95
2018-02-19 11:00 | 137.19 | 126.72
2018-02-19 11:30 | 137.81 | 126.54
2018-02-19 12:00 | 177.1 | 167.8
2018-02-19 12:30 | 189.38 | 180.73
2018-02-19 13:00 | 197 | 188.41
2018-02-19 13:30 | 209.69 | 201.24
2018-02-19 14:00 | 220.89 | 214.15
2018-02-19 14:30 | 233.88 | 229.92
2018-02-19 15:00 | 252.87 | 249.74
2018-02-19 15:30 | 259.61 | 256.64
2018-02-19 16:00 | 282.12 | 279.15
2018-02-19 16:30 | 284.48 | 281.34
2018-02-19 17:00 | 291.05 | 288.79
2018-02-19 17:30 | 289.75 | 287.83
2018-02-19 18:00 | 282.94 | 280.15
2018-02-19 18:30 | 281.13 | 273.7
2018-02-19 19:00 | 283.86 | 279.32
2018-02-19 19:30 | 279.74 | 275.48
2018-02-19 20:00 | 262.45 | 259.01
2018-02-19 20:30 | 261.75 | 258.37
2018-02-19 21:00 | 238.43 | 238.06
2018-02-19 21:30 | 227.95 | 225.36
2018-02-19 22:00 | 211.84 | 209.79
2018-02-19 22:30 | 203.64 | 201.9
2018-02-19 23:00 | 195.72 | 194.15
2018-02-19 23:30 | 158.2 | 156.67
2018-02-20 | 93.16 | 91.09
2018-02-20 00:30 | 73.17 | 67.65
2018-02-20 01:00 | 59.24 | 49.34
2018-02-20 01:30 | 52.93 | 41.75
2018-02-20 02:00 | 42.07 | 27.02
2018-02-20 02:30 | 40.01 | 24.12
2018-02-20 03:00 | 39.13 | 23.1
2018-02-20 03:30 | 38.71 | 22.41
2018-02-20 04:00 | 38.86 | 22.88
2018-02-20 04:30 | 38.62 | 22.02
2018-02-20 05:00 | 40.66 | 24.26
2018-02-20 05:30 | 58.9 | 46.2
2018-02-20 06:00 | 117.54 | 107.65
2018-02-20 06:30 | 134.25 | 123.05
2018-02-20 07:00 | 161.68 | 148.32
2018-02-20 07:30 | 175.7 | 161.74
2018-02-20 08:00 | 185.14 | 170.06
2018-02-20 08:30 | 194 | 176.3
2018-02-20 09:00 | 205.24 | 178.49
2018-02-20 09:30 | 197.84 | 168.7
2018-02-20 10:00 | 200.88 | 173.54
2018-02-20 10:30 | 209.15 | 183.18
2018-02-20 11:00 | 205.36 | 178.76
2018-02-20 11:30 | 200.59 | 174.55
2018-02-20 12:00 | 202.74 | 176.77
2018-02-20 12:30 | 205.79 | 179.93
2018-02-20 13:00 | 206.33 | 180.46
2018-02-20 13:30 | 207.86 | 182.33
2018-02-20 14:00 | 211.56 | 185.93
2018-02-20 14:30 | 206.22 | 180.01
2018-02-20 15:00 | 194.13 | 166.85
2018-02-20 15:30 | 194.29 | 167.6
2018-02-20 16:00 | 208.63 | 184.35
2018-02-20 16:30 | 202.58 | 178.85
2018-02-20 17:00 | 200.79 | 177.87
2018-02-20 17:30 | 206.41 | 188.46
2018-02-20 18:00 | 199.79 | 186.93
2018-02-20 18:30 | 197.16 | 185.91
2018-02-20 19:00 | 239.24 | 228.54
2018-02-20 19:30 | 231.65 | 221.24
2018-02-20 20:00 | 217.98 | 207.98
2018-02-20 20:30 | 196.77 | 186.99
2018-02-20 21:00 | 156.56 | 149.3
2018-02-20 21:30 | 133.25 | 127.65
2018-02-20 22:00 | 122.18 | 117.96
2018-02-20 22:30 | 118.99 | 118.48
2018-02-20 23:00 | 136.59 | 136.04
2018-02-20 23:30 | 113.53 | 113.52
2018-02-21 | 62.85 | 61.67
2018-02-21 00:30 | 34.58 | 32.61
2018-02-21 01:00 | 26.97 | 24.57
2018-02-21 01:30 | 27.5 | 25.59
2018-02-21 02:00 | 26.94 | 24.96
2018-02-21 02:30 | 24.99 | 23.29
2018-02-21 03:00 | 23.6 | 22.05
2018-02-21 03:30 | 24.7 | 23.32
2018-02-21 04:00 | 25.76 | 24.4
2018-02-21 04:30 | 28.52 | 27.18
2018-02-21 05:00 | 26.41 | 24.88
2018-02-21 05:30 | 47.8 | 46.95
2018-02-21 06:00 | 81.98 | 81.44
2018-02-21 06:30 | 114.74 | 114.52
2018-02-21 07:00 | 145.93 | 145.93
2018-02-21 07:30 | 154.64 | 154.58
2018-02-21 08:00 | 160.58 | 160.31
2018-02-21 08:30 | 161.41 | 160.19
2018-02-21 09:00 | 172.23 | 169.75
2018-02-21 09:30 | 176.68 | 174.45
2018-02-21 10:00 | 158.26 | 155.83
2018-02-21 10:30 | 146.73 | 144.03
2018-02-21 11:00 | 135.25 | 132.23
2018-02-21 11:30 | 136.25 | 133.18
2018-02-21 12:00 | 128.23 | 124.85
2018-02-21 12:30 | 128.33 | 125.08
2018-02-21 13:00 | 116.49 | 113.14
2018-02-21 13:30 | 107.82 | 104.19
2018-02-21 14:00 | 108.13 | 104.25
2018-02-21 14:30 | 135.49 | 132.18
2018-02-21 15:00 | 142.26 | 139.34
2018-02-21 15:30 | 137.49 | 134.88
2018-02-21 16:00 | 148.74 | 146.56
2018-02-21 16:30 | 164.71 | 163.08
2018-02-21 17:00 | 187.76 | 186.52
2018-02-21 17:30 | 178.3 | 177.43
2018-02-21 18:00 | 166.96 | 165.98
2018-02-21 18:30 | 170.37 | 167.98
2018-02-21 19:00 | 190.56 | 187.69
2018-02-21 19:30 | 183.34 | 180.6
2018-02-21 20:00 | 176.35 | 174.04
2018-02-21 20:30 | 168.27 | 166.99
2018-02-21 21:00 | 129.62 | 129.37
2018-02-21 21:30 | 112.73 | 112.35
2018-02-21 22:00 | 96.33 | 95.78
2018-02-21 22:30 | 97.35 | 96.94
2018-02-21 23:00 | 102.93 | 102.45
2018-02-21 23:30 | 67.83 | 67.11
2018-02-22 | 24.31 | 23.29
2018-02-22 00:30 | 12.4 | 11.68
2018-02-22 01:00 | 15.01 | 14.67
2018-02-22 01:30 | 15.52 | 15.15
2018-02-22 02:00 | 16.2 | 15.93
2018-02-22 02:30 | 16.33 | 15.84
2018-02-22 03:00 | 16.1 | 15.36
2018-02-22 03:30 | 15.63 | 14.7
2018-02-22 04:00 | 16.47 | 15.39
2018-02-22 04:30 | 16.53 | 15.46
2018-02-22 05:00 | 17.29 | 16.26
2018-02-22 05:30 | 24.78 | 24.46
2018-02-22 06:00 | 51.46 | 51.36
2018-02-22 06:30 | 86.06 | 86.06
2018-02-22 07:00 | 127.34 | 123.83
2018-02-22 07:30 | 128.45 | 121.77
2018-02-22 08:00 | 125.1 | 116.19
2018-02-22 08:30 | 123.29 | 111.62
2018-02-22 09:00 | 147.12 | 127.45
2018-02-22 09:30 | 160.51 | 140.64
2018-02-22 10:00 | 161.13 | 148.19
2018-02-22 10:30 | 159.41 | 146.38
2018-02-22 11:00 | 157.75 | 144.33
2018-02-22 11:30 | 140.85 | 125.69
2018-02-22 12:00 | 138.99 | 123.68
2018-02-22 12:30 | 136.04 | 120.46
2018-02-22 13:00 | 149.36 | 134.98
2018-02-22 13:30 | 153.77 | 140.19
2018-02-22 14:00 | 157.35 | 144.23
2018-02-22 14:30 | 147.65 | 134.19
2018-02-22 15:00 | 130.23 | 115.08
2018-02-22 15:30 | 135.66 | 122.66
2018-02-22 16:00 | 144.44 | 132.9
2018-02-22 16:30 | 151.08 | 140.77
2018-02-22 17:00 | 153.29 | 143.49
2018-02-22 17:30 | 155.99 | 147.08
2018-02-22 18:00 | 156.53 | 148.22
2018-02-22 18:30 | 174.55 | 167.99
2018-02-22 19:00 | 197.78 | 191.43
2018-02-22 19:30 | 184.87 | 178.73
2018-02-22 20:00 | 188.37 | 185.7
2018-02-22 20:30 | 197.76 | 193.61
2018-02-22 21:00 | 161.15 | 156.89
2018-02-22 21:30 | 133.63 | 129.11
2018-02-22 22:00 | 111.61 | 106.94
2018-02-22 22:30 | 105.81 | 101.38
2018-02-22 23:00 | 116.67 | 114.19
2018-02-22 23:30 | 78.88 | 78.69
2018-02-23 | 42.7 | 42.37
2018-02-23 00:30 | 28.35 | 27.75
2018-02-23 01:00 | 31.14 | 30.59
2018-02-23 01:30 | 20.79 | 20.14
2018-02-23 02:00 | 16.38 | 15.58
2018-02-23 02:30 | 15.11 | 14.24
2018-02-23 03:00 | 16.23 | 15.62
2018-02-23 03:30 | 17.75 | 16.94
2018-02-23 04:00 | 16.69 | 15.92
2018-02-23 04:30 | 17.1 | 16.15
2018-02-23 05:00 | 29.88 | 29.4
2018-02-23 05:30 | 56.5 | 56.36
2018-02-23 06:00 | 76.37 | 76.36
2018-02-23 06:30 | 113.57 | 113.57
2018-02-23 07:00 | 147.88 | 147.87
2018-02-23 07:30 | 171.23 | 171.2
2018-02-23 08:00 | 180.46 | 179.89
2018-02-23 08:30 | 178.34 | 176.39
2018-02-23 09:00 | 170.15 | 167.65
2018-02-23 09:30 | 191.8 | 188.79
2018-02-23 10:00 | 207.46 | 196.69
2018-02-23 10:30 | 215.86 | 198.76
2018-02-23 11:00 | 220.98 | 204.06
2018-02-23 11:30 | 229.32 | 213.62
2018-02-23 12:00 | 224.62 | 209.33
2018-02-23 12:30 | 220.56 | 205.21
2018-02-23 13:00 | 210.76 | 195.35
2018-02-23 13:30 | 207.9 | 192.58
2018-02-23 14:00 | 205.91 | 191.02
2018-02-23 14:30 | 203.22 | 191.09
2018-02-23 15:00 | 197.35 | 189.34
2018-02-23 15:30 | 188.68 | 180.52
2018-02-23 16:00 | 192.64 | 184.94
2018-02-23 16:30 | 183.24 | 175.49
2018-02-23 17:00 | 205.89 | 199.15
2018-02-23 17:30 | 225.16 | 219.17
2018-02-23 18:00 | 220.28 | 215.48
2018-02-23 18:30 | 213 | 210.07
2018-02-23 19:00 | 230.2 | 225.14
2018-02-23 19:30 | 209.36 | 204.31
2018-02-23 20:00 | 192.4 | 187.06
2018-02-23 20:30 | 191.55 | 186.13
2018-02-23 21:00 | 160.63 | 154.94
2018-02-23 21:30 | 136.89 | 131.3
2018-02-23 22:00 | 111.7 | 105.86
2018-02-23 22:30 | 128.7 | 124.11
2018-02-23 23:00 | 144.22 | 140.41
2018-02-23 23:30 | 124.86 | 121.17
2018-02-24 | 71.91 | 69.08
2018-02-24 00:30 | 49.25 | 48.96
2018-02-24 01:00 | 38.77 | 38.35
2018-02-24 01:30 | 37.69 | 37.2
2018-02-24 02:00 | 38.48 | 38.05
2018-02-24 02:30 | 30.5 | 30.08
2018-02-24 03:00 | 30.92 | 30.55
2018-02-24 03:30 | 34.21 | 33.78
2018-02-24 04:00 | 46.42 | 46.01
2018-02-24 04:30 | 46.44 | 45.98
2018-02-24 05:00 | 54.73 | 54.33
2018-02-24 05:30 | 54.58 | 54.25
2018-02-24 06:00 | 52.56 | 52.34
2018-02-24 06:30 | 63.09 | 62.96
2018-02-24 07:00 | 68.53 | 68.53
2018-02-24 07:30 | 77.88 | 74
2018-02-24 08:00 | 87.62 | 81.28
2018-02-24 08:30 | 127.5 | 117.64
2018-02-24 09:00 | 161.77 | 138.73
2018-02-24 09:30 | 172.12 | 150.24
2018-02-24 10:00 | 175.03 | 152.64
2018-02-24 10:30 | 188.93 | 172.94
2018-02-24 11:00 | 167.35 | 159.89
2018-02-24 11:30 | 156.37 | 148.43
2018-02-24 12:00 | 155.14 | 147.19
2018-02-24 12:30 | 147.51 | 140.96
2018-02-24 13:00 | 125.82 | 122.65
2018-02-24 13:30 | 133.97 | 131.09
2018-02-24 14:00 | 137.5 | 134.63
2018-02-24 14:30 | 150.48 | 147.65
2018-02-24 15:00 | 156.57 | 153.79
2018-02-24 15:30 | 161.76 | 159.14
2018-02-24 16:00 | 165.91 | 163.58
2018-02-24 16:30 | 174.1 | 172.54
2018-02-24 17:00 | 183.14 | 182.17
2018-02-24 17:30 | 180.53 | 178.92
2018-02-24 18:00 | 182.84 | 181.39
2018-02-24 18:30 | 200.63 | 199.28
2018-02-24 19:00 | 197.59 | 195.87
2018-02-24 19:30 | 191.08 | 189.6
2018-02-24 20:00 | 183.18 | 181.81
2018-02-24 20:30 | 159.26 | 157.86
2018-02-24 21:00 | 149.69 | 145.4
2018-02-24 21:30 | 153.89 | 151.94
2018-02-24 22:00 | 144.51 | 143.25
2018-02-24 22:30 | 157.89 | 156.94
2018-02-24 23:00 | 174.67 | 173.96
2018-02-24 23:30 | 151.68 | 151.16
2018-02-25 | 90.03 | 89.53
2018-02-25 00:30 | 56.92 | 56.05
2018-02-25 01:00 | 38.55 | 35.47
2018-02-25 01:30 | 31.52 | 27.55
2018-02-25 02:00 | 30 | 25.54
2018-02-25 02:30 | 27.96 | 23.36
2018-02-25 03:00 | 27.76 | 22.79
2018-02-25 03:30 | 25.28 | 20.15
2018-02-25 04:00 | 24.17 | 19.28
2018-02-25 04:30 | 23.22 | 18.16
2018-02-25 05:00 | 23.52 | 18.38
2018-02-25 05:30 | 22.2 | 17
2018-02-25 06:00 | 23.56 | 17.79
2018-02-25 06:30 | 29.93 | 25.65
2018-02-25 07:00 | 33.54 | 29.33
2018-02-25 07:30 | 40.79 | 35.26
2018-02-25 08:00 | 52.19 | 45.76
2018-02-25 08:30 | 92.05 | 79.16
2018-02-25 09:00 | 114.23 | 95.21
2018-02-25 09:30 | 124.63 | 103.33
2018-02-25 10:00 | 134 | 113.75
2018-02-25 10:30 | 137.77 | 119.31
2018-02-25 11:00 | 160.04 | 143.59
2018-02-25 11:30 | 176.15 | 160.82
2018-02-25 12:00 | 192.15 | 183.37
2018-02-25 12:30 | 207.48 | 199.53
2018-02-25 13:00 | 222.17 | 214.19
2018-02-25 13:30 | 236.64 | 228.67
2018-02-25 14:00 | 232.56 | 224.02
2018-02-25 14:30 | 235.91 | 226.99
2018-02-25 15:00 | 247.47 | 237.78
2018-02-25 15:30 | 252.03 | 242.05
2018-02-25 16:00 | 273.83 | 265.59
2018-02-25 16:30 | 280.65 | 274.86
2018-02-25 17:00 | 282.59 | 277.38
2018-02-25 17:30 | 275.87 | 271.32
2018-02-25 18:00 | 263.4 | 260.07
2018-02-25 18:30 | 256.07 | 253.88
2018-02-25 19:00 | 263.3 | 260.47
2018-02-25 19:30 | 257.17 | 254.52
2018-02-25 20:00 | 252.26 | 249.97
2018-02-25 20:30 | 243.59 | 241.94
2018-02-25 21:00 | 232.21 | 231.05
2018-02-25 21:30 | 221.3 | 221.26
2018-02-25 22:00 | 199.11 | 199.08
2018-02-25 22:30 | 198.1 | 198.08
2018-02-25 23:00 | 193.21 | 193.21
2018-02-25 23:30 | 170.15 | 170.13
2018-02-26 | 105.26 | 105.25
2018-02-26 00:30 | 76.65 | 76.58
2018-02-26 01:00 | 64.08 | 63.9
2018-02-26 01:30 | 66.79 | 66.53
2018-02-26 02:00 | 71.97 | 71.7
2018-02-26 02:30 | 62.8 | 62.45
2018-02-26 03:00 | 52.86 | 52.39
2018-02-26 03:30 | 63.28 | 62.85
2018-02-26 04:00 | 59.84 | 59.36
2018-02-26 04:30 | 39.32 | 38.82
2018-02-26 05:00 | 48.95 | 48.75
2018-02-26 05:30 | 71.82 | 71.81
2018-02-26 06:00 | 88.72 | 88.72
2018-02-26 06:30 | 131.44 | 131.3
2018-02-26 07:00 | 171.88 | 171.72
2018-02-26 07:30 | 193.22 | 191.11
2018-02-26 08:00 | 190.77 | 187.05
2018-02-26 08:30 | 200.3 | 195.16
2018-02-26 09:00 | 218.04 | 210.71
2018-02-26 09:30 | 233.27 | 220.69
2018-02-26 10:00 | 237.84 | 225.71
2018-02-26 10:30 | 247.39 | 237.36
2018-02-26 11:00 | 260.32 | 251.01
2018-02-26 11:30 | 262.72 | 253.42
2018-02-26 12:00 | 266.57 | 257.13
2018-02-26 12:30 | 264.7 | 255.88
2018-02-26 13:00 | 268.85 | 262.33
2018-02-26 13:30 | 277.96 | 271.58
2018-02-26 14:00 | 284.41 | 278
2018-02-26 14:30 | 289.85 | 283.54
2018-02-26 15:00 | 269.53 | 262.98
2018-02-26 15:30 | 290.4 | 283.76
2018-02-26 16:00 | 314.44 | 307.77
2018-02-26 16:30 | 330.55 | 321.85
2018-02-26 17:00 | 333.81 | 329.68
2018-02-26 17:30 | 328.68 | 326.63
2018-02-26 18:00 | 325.83 | 324.02
2018-02-26 18:30 | 313.76 | 311.98
2018-02-26 19:00 | 296.32 | 296.16
2018-02-26 19:30 | 276.16 | 275.93
2018-02-26 20:00 | 265.5 | 263.02
2018-02-26 20:30 | 246.57 | 246.56
2018-02-26 21:00 | 232.81 | 232.81
2018-02-26 21:30 | 211.95 | 211.84
2018-02-26 22:00 | 174.84 | 174.74
2018-02-26 22:30 | 164.39 | 164.03
2018-02-26 23:00 | 172.99 | 172.48
2018-02-26 23:30 | 130.32 | 129.7
2018-02-27 | 70.41 | 69.06
2018-02-27 00:30 | 50.6 | 47.16
2018-02-27 01:00 | 28.12 | 28.11
2018-02-27 01:30 | 25.67 | 25.08
2018-02-27 02:00 | 23.67 | 22.94
2018-02-27 02:30 | 23.23 | 22.43
2018-02-27 03:00 | 23.07 | 22.22
2018-02-27 03:30 | 22 | 21.06
2018-02-27 04:00 | 21.09 | 19.96
2018-02-27 04:30 | 21.43 | 20.36
2018-02-27 05:00 | 21.05 | 20.17
2018-02-27 05:30 | 30.98 | 30.66
2018-02-27 06:00 | 61.91 | 61.79
2018-02-27 06:30 | 95.25 | 93.24
2018-02-27 07:00 | 128.64 | 125.75
2018-02-27 07:30 | 154.19 | 136.19
2018-02-27 08:00 | 155.01 | 136.67
2018-02-27 08:30 | 148.52 | 135.74
2018-02-27 09:00 | 144.99 | 134.84
2018-02-27 09:30 | 144.21 | 133.46
2018-02-27 10:00 | 141.61 | 130.61
2018-02-27 10:30 | 124.48 | 112
2018-02-27 11:00 | 121.15 | 107.44
2018-02-27 11:30 | 126.28 | 112.56
2018-02-27 12:00 | 134.38 | 121.09
2018-02-27 12:30 | 117.49 | 102.2
2018-02-27 13:00 | 117.81 | 102.23
2018-02-27 13:30 | 125.55 | 110.11
2018-02-27 14:00 | 141.4 | 128.04
2018-02-27 14:30 | 173.85 | 163.11
2018-02-27 15:00 | 171.11 | 160.7
2018-02-27 15:30 | 164.16 | 154.02
2018-02-27 16:00 | 173.46 | 163.8
2018-02-27 16:30 | 179.89 | 171.3
2018-02-27 17:00 | 175.76 | 167.64
2018-02-27 17:30 | 187.61 | 180.91
2018-02-27 18:00 | 175.36 | 169.29
2018-02-27 18:30 | 184.57 | 179.68
2018-02-27 19:00 | 193.67 | 188.59
2018-02-27 19:30 | 189.74 | 185.16
2018-02-27 20:00 | 178.17 | 174
2018-02-27 20:30 | 173.41 | 171.62
2018-02-27 21:00 | 148.46 | 148.08
2018-02-27 21:30 | 122.44 | 121.97
2018-02-27 22:00 | 102.07 | 101.45
2018-02-27 22:30 | 99.85 | 99.26
2018-02-27 23:00 | 108.67 | 107.79
2018-02-27 23:30 | 83.97 | 82.96
2018-02-28 | 35.35 | 33.92
2018-02-28 00:30 | 12.56 | 11.31
2018-02-28 01:00 | 12.86 | 12.17
2018-02-28 01:30 | 15.7 | 15.42
2018-02-28 02:00 | 14.76 | 14.71
2018-02-28 02:30 | 15.12 | 15.1
2018-02-28 03:00 | 15.41 | 15.34
2018-02-28 03:30 | 14.73 | 14.62
2018-02-28 04:00 | 15.49 | 15.32
2018-02-28 04:30 | 15.67 | 15.43
2018-02-28 05:00 | 15.27 | 14.8
2018-02-28 05:30 | 20.09 | 19.17
2018-02-28 06:00 | 23.16 | 22.46
2018-02-28 06:30 | 37.53 | 37.52
2018-02-28 07:00 | 56.39 | 56.09
2018-02-28 07:30 | 86.64 | 85.9
2018-02-28 08:00 | 62.79 | 60.9
2018-02-28 08:30 | 76.4 | 61.44
2018-02-28 09:00 | 77.91 | 72.48
2018-02-28 09:30 | 81.46 | 76.36
2018-02-28 10:00 | 91.22 | 87.01
2018-02-28 10:30 | 76.75 | 72.01
2018-02-28 11:00 | 77.02 | 70.55
2018-02-28 11:30 | 82.75 | 76.48
2018-02-28 12:00 | 95.61 | 90.9
2018-02-28 12:30 | 104.49 | 99.66
2018-02-28 13:00 | 97.63 | 92.8
2018-02-28 13:30 | 104.64 | 100.75
2018-02-28 14:00 | 107.42 | 103.24
2018-02-28 14:30 | 122.73 | 118.58
2018-02-28 15:00 | 133.47 | 129.54
2018-02-28 15:30 | 139.69 | 136.27
2018-02-28 16:00 | 166.06 | 163.4
2018-02-28 16:30 | 183.91 | 182.66
2018-02-28 17:00 | 198.05 | 197.2
2018-02-28 17:30 | 215.9 | 215.26
2018-02-28 18:00 | 212.27 | 211.41
2018-02-28 18:30 | 212.46 | 208.53
2018-02-28 19:00 | 247.46 | 242.06
2018-02-28 19:30 | 240.38 | 236.98
2018-02-28 20:00 | 214.68 | 211.84
2018-02-28 20:30 | 184.39 | 182.8
2018-02-28 21:00 | 146.84 | 146.82
2018-02-28 21:30 | 134.27 | 134.26
2018-02-28 22:00 | 107.71 | 107.69
2018-02-28 22:30 | 98.33 | 98.2
2018-02-28 23:00 | 110.87 | 110.68
2018-02-28 23:30 | 75.06 | 74.59
2018-03-01 | 22.46 | 21.76
2018-03-01 00:30 | 13.07 | 12.59
2018-03-01 01:00 | 15.35 | 14.67
2018-03-01 01:30 | 17.65 | 16.95
2018-03-01 02:00 | 6.57 | 3.11
2018-03-01 02:30 | 16.87 | -15.33
2018-03-01 03:00 | 16.38 | -14.84
2018-03-01 03:30 | 16.54 | -14.87
2018-03-01 04:00 | 16.86 | -14.83
2018-03-01 04:30 | 16.4 | -14.55
2018-03-01 05:00 | 12.72 | -10.82
2018-03-01 05:30 | 16.82 | 15.82
2018-03-01 06:00 | 68.27 | 67.96
2018-03-01 06:30 | 91.52 | 91.4
2018-03-01 07:00 | 103.61 | 103.31
2018-03-01 07:30 | 117.98 | 117.41
2018-03-01 08:00 | 125.61 | 124.23
2018-03-01 08:30 | 132.11 | 123.74
2018-03-01 09:00 | 141.02 | 128.48
2018-03-01 09:30 | 144.41 | 129.27
2018-03-01 10:00 | 153.39 | 137.46
2018-03-01 10:30 | 159.69 | 142.61
2018-03-01 11:00 | 167.79 | 149.77
2018-03-01 11:30 | 173.86 | 155.13
2018-03-01 12:00 | 174.12 | 162.32
2018-03-01 12:30 | 179.14 | 167.41
2018-03-01 13:00 | 180.1 | 168.53
2018-03-01 13:30 | 190.4 | 178.28
2018-03-01 14:00 | 196.6 | 184.33
2018-03-01 14:30 | 199.03 | 189.4
2018-03-01 15:00 | 200.16 | 189.08
2018-03-01 15:30 | 208.56 | 193.35
2018-03-01 16:00 | 210.72 | 195.31
2018-03-01 16:30 | 213.97 | 198.4
2018-03-01 17:00 | 236.89 | 222.03
2018-03-01 17:30 | 296.25 | 284.5
2018-03-01 18:00 | 293.19 | 282.53
2018-03-01 18:30 | 290.81 | 281.09
2018-03-01 19:00 | 299.14 | 288.41
2018-03-01 19:30 | 298.12 | 287.99
2018-03-01 20:00 | 295.46 | 287.19
2018-03-01 20:30 | 284.48 | 279.75
2018-03-01 21:00 | 272.14 | 266.41
2018-03-01 21:30 | 259.81 | 253.71
2018-03-01 22:00 | 244.72 | 237.46
2018-03-01 22:30 | 232.58 | 225.99
2018-03-01 23:00 | 223.87 | 217.97
2018-03-01 23:30 | 191.07 | 189.41
2018-03-02 | 124.78 | 124.78
2018-03-02 00:30 | 96.84 | 96.72
2018-03-02 01:00 | 71.98 | 71.82
2018-03-02 01:30 | 50.75 | 50.54
2018-03-02 02:00 | 36.51 | 35.99
2018-03-02 02:30 | 45.97 | 45.34
2018-03-02 03:00 | 17.42 | 16.51
2018-03-02 03:30 | 31.94 | 31.23
2018-03-02 04:00 | 15.3 | 14.08
2018-03-02 04:30 | 35.34 | 34.78
2018-03-02 05:00 | 47.35 | 47.05
2018-03-02 05:30 | 69.87 | 69.86
2018-03-02 06:00 | 92.48 | 92.45
2018-03-02 06:30 | 111.14 | 111.13
2018-03-02 07:00 | 127.65 | 127.64
2018-03-02 07:30 | 137.12 | 135.92
2018-03-02 08:00 | 146.52 | 142.1
2018-03-02 08:30 | 149.6 | 143.37
2018-03-02 09:00 | 170.05 | 162.57
2018-03-02 09:30 | 188.62 | 176.12
2018-03-02 10:00 | 195.04 | 182.23
2018-03-02 10:30 | 206.42 | 193.53
2018-03-02 11:00 | 208.97 | 193.69
2018-03-02 11:30 | 225.51 | 206.79
2018-03-02 12:00 | 227.68 | 210.07
2018-03-02 12:30 | 229.82 | 213.53
2018-03-02 13:00 | 226.25 | 210.54
2018-03-02 13:30 | 213.6 | 198.04
2018-03-02 14:00 | 212.59 | 199.05
2018-03-02 14:30 | 217.62 | 204.64
2018-03-02 15:00 | 201.79 | 188.81
2018-03-02 15:30 | 191.9 | 179.01
2018-03-02 16:00 | 211.46 | 200.34
2018-03-02 16:30 | 208 | 197.55
2018-03-02 17:00 | 196.33 | 190.9
2018-03-02 17:30 | 191.79 | 187.32
2018-03-02 18:00 | 198.42 | 194.38
2018-03-02 18:30 | 196.54 | 192.06
2018-03-02 19:00 | 219.23 | 214.66
2018-03-02 19:30 | 215.76 | 211.66
2018-03-02 20:00 | 223.11 | 219.48
2018-03-02 20:30 | 229.02 | 225.8
2018-03-02 21:00 | 197.42 | 190.4
2018-03-02 21:30 | 165.93 | 158.27
2018-03-02 22:00 | 139.41 | 131.63
2018-03-02 22:30 | 135.84 | 128.76
2018-03-02 23:00 | 157.29 | 151.48
2018-03-02 23:30 | 140.94 | 140.94
2018-03-03 | 88.75 | 88.05
2018-03-03 00:30 | 60.92 | 60.42
2018-03-03 01:00 | 40.78 | 39.79
2018-03-03 01:30 | 18.23 | 15.77
2018-03-03 02:00 | 15.47 | 12.38
2018-03-03 02:30 | 12.81 | 8.05
2018-03-03 03:00 | 10.4 | 3.03
2018-03-03 03:30 | 10.47 | 0.18
2018-03-03 04:00 | 10.77 | 0.04
2018-03-03 04:30 | 12.8 | 6.1
2018-03-03 05:00 | 33.95 | 31.71
2018-03-03 05:30 | 29.94 | 27.83
2018-03-03 06:00 | 31.39 | 29.67
2018-03-03 06:30 | 39.44 | 38.62
2018-03-03 07:00 | 53.78 | 53.63
2018-03-03 07:30 | 43.18 | 42.57
2018-03-03 08:00 | 47.86 | 33.54
2018-03-03 08:30 | 76.34 | 54.38
2018-03-03 09:00 | 101.2 | 83.79
2018-03-03 09:30 | 115.23 | 98.56
2018-03-03 10:00 | 130.96 | 116.93
2018-03-03 10:30 | 137.63 | 124.16
2018-03-03 11:00 | 137.57 | 123.52
2018-03-03 11:30 | 125.11 | 109.59
2018-03-03 12:00 | 118.74 | 101.27
2018-03-03 12:30 | 126.59 | 108.96
2018-03-03 13:00 | 139.87 | 122.71
2018-03-03 13:30 | 155.07 | 135.09
2018-03-03 14:00 | 150.37 | 140
2018-03-03 14:30 | 145.67 | 134.17
2018-03-03 15:00 | 165.34 | 155.58
2018-03-03 15:30 | 182.36 | 173.6
2018-03-03 16:00 | 195.96 | 187.15
2018-03-03 16:30 | 206.15 | 198.06
2018-03-03 17:00 | 210.89 | 202.94
2018-03-03 17:30 | 220.45 | 213.4
2018-03-03 18:00 | 238.01 | 232.14
2018-03-03 18:30 | 249.69 | 244.05
2018-03-03 19:00 | 263.6 | 257.74
2018-03-03 19:30 | 254.53 | 249.45
2018-03-03 20:00 | 252.9 | 248.23
2018-03-03 20:30 | 236.94 | 232.69
2018-03-03 21:00 | 201.19 | 197.01
2018-03-03 21:30 | 180.46 | 175.18
2018-03-03 22:00 | 154.37 | 149.29
2018-03-03 22:30 | 190.33 | 183.45
2018-03-03 23:00 | 199.29 | 192.3
2018-03-03 23:30 | 166.55 | 159.4
2018-03-04 | 103.96 | 98.96
2018-03-04 00:30 | 74.02 | 72.03
2018-03-04 01:00 | 49.07 | 48.61
2018-03-04 01:30 | 41.51 | 40.7
2018-03-04 02:00 | 37.3 | 36.09
2018-03-04 02:30 | 31.84 | 30.27
2018-03-04 03:00 | 26.84 | 24.82
2018-03-04 03:30 | 18.06 | 14.79
2018-03-04 04:00 | 17.6 | 13.83
2018-03-04 04:30 | 20.24 | 16.88
2018-03-04 05:00 | 20.36 | 16.9
2018-03-04 05:30 | 19.01 | 15.89
2018-03-04 06:00 | 16.45 | 11.77
2018-03-04 06:30 | 14.23 | 10.83
2018-03-04 07:00 | 20.84 | 20.06
2018-03-04 07:30 | 30.64 | 30.64
2018-03-04 08:00 | 37.44 | 35.39
2018-03-04 08:30 | 74.85 | 47.12
2018-03-04 09:00 | 67.81 | 34.66
2018-03-04 09:30 | 78.21 | 45.26
2018-03-04 10:00 | 89.38 | 56.78
2018-03-04 10:30 | 108.96 | 80.38
2018-03-04 11:00 | 114.19 | 85.35
2018-03-04 11:30 | 115.99 | 90.59
2018-03-04 12:00 | 131.83 | 114.84
2018-03-04 12:30 | 163.22 | 149.29
2018-03-04 13:00 | 194.85 | 181.82
2018-03-04 13:30 | 232.11 | 218.71
2018-03-04 14:00 | 255.94 | 244.9
2018-03-04 14:30 | 288.35 | 277.35
2018-03-04 15:00 | 290.41 | 278.77
2018-03-04 15:30 | 288.51 | 276.8
2018-03-04 16:00 | 286.09 | 274.65
2018-03-04 16:30 | 289.09 | 278.28
2018-03-04 17:00 | 308.26 | 297.9
2018-03-04 17:30 | 309.61 | 299.87
2018-03-04 18:00 | 309.88 | 300.75
2018-03-04 18:30 | 307.91 | 302.02
2018-03-04 19:00 | 315.12 | 308.73
2018-03-04 19:30 | 305.09 | 299.34
2018-03-04 20:00 | 292.79 | 288.14
2018-03-04 20:30 | 269.39 | 265.49
2018-03-04 21:00 | 262.27 | 259.54
2018-03-04 21:30 | 238.89 | 237.19
2018-03-04 22:00 | 211.48 | 210.99
2018-03-04 22:30 | 216.04 | 215.94
2018-03-04 23:00 | 203.98 | 203.76
2018-03-04 23:30 | 149.94 | 149.51
2018-03-05 | 93.95 | 93.43
2018-03-05 00:30 | 72.56 | 71.42
2018-03-05 01:00 | 59.81 | 58.07
2018-03-05 01:30 | 46.46 | 43.39
2018-03-05 02:00 | 33.77 | 29.73
2018-03-05 02:30 | 23.95 | 22.3
2018-03-05 03:00 | 18.61 | 16.15
2018-03-05 03:30 | 19.48 | 17.15
2018-03-05 04:00 | 27.63 | 25.98
2018-03-05 04:30 | 34.01 | 32.76
2018-03-05 05:00 | 30.85 | 29.92
2018-03-05 05:30 | 48.86 | 48.67
2018-03-05 06:00 | 73.43 | 71.12
2018-03-05 06:30 | 103.33 | 98.19
2018-03-05 07:00 | 132.69 | 127.12
2018-03-05 07:30 | 158.42 | 152.32
2018-03-05 08:00 | 163.89 | 156.62
2018-03-05 08:30 | 168.58 | 159.68
2018-03-05 09:00 | 172.6 | 162.71
2018-03-05 09:30 | 186.21 | 167.38
2018-03-05 10:00 | 193.97 | 173.37
2018-03-05 10:30 | 193.32 | 170.42
2018-03-05 11:00 | 193.84 | 182.55
2018-03-05 11:30 | 204.68 | 194.49
2018-03-05 12:00 | 197.15 | 186.72
2018-03-05 12:30 | 183.56 | 173.17
2018-03-05 13:00 | 172.93 | 162.96
2018-03-05 13:30 | 187.94 | 178.64
2018-03-05 14:00 | 203.87 | 195.43
2018-03-05 14:30 | 197.6 | 188.76
2018-03-05 15:00 | 203.81 | 194.98
2018-03-05 15:30 | 221.86 | 213.53
2018-03-05 16:00 | 235.08 | 227.16
2018-03-05 16:30 | 250.28 | 243.12
2018-03-05 17:00 | 254.98 | 248.09
2018-03-05 17:30 | 258.76 | 252.85
2018-03-05 18:00 | 265.51 | 260.36
2018-03-05 18:30 | 265.89 | 260.57
2018-03-05 19:00 | 271.77 | 266.02
2018-03-05 19:30 | 260.65 | 255.58
2018-03-05 20:00 | 255.23 | 250.95
2018-03-05 20:30 | 235.56 | 233.7
2018-03-05 21:00 | 197.18 | 197.01
2018-03-05 21:30 | 173.37 | 173.1
2018-03-05 22:00 | 149.43 | 148.61
2018-03-05 22:30 | 138.3 | 137.29
2018-03-05 23:00 | 140.83 | 139.48
2018-03-05 23:30 | 103.97 | 101.62
2018-03-06 | 52.99 | 47.45
2018-03-06 00:30 | 25.1 | 21.07
2018-03-06 01:00 | 20.9 | 16.54
2018-03-06 01:30 | 16.1 | 8.11
2018-03-06 02:00 | 20.03 | 13.59
2018-03-06 02:30 | 34.97 | 31.29
2018-03-06 03:00 | 48.01 | 45.14
2018-03-06 03:30 | 45.25 | 42.15
2018-03-06 04:00 | 47.15 | 44.36
2018-03-06 04:30 | 22.87 | 18.09
2018-03-06 05:00 | 18.27 | 13.32
2018-03-06 05:30 | 29 | 27.7
2018-03-06 06:00 | 57.74 | 57.32
2018-03-06 06:30 | 90.28 | 89.28
2018-03-06 07:00 | 134.19 | 133.73
2018-03-06 07:30 | 144.39 | 144.23
2018-03-06 08:00 | 169.06 | 169.04
2018-03-06 08:30 | 171.3 | 171.28
2018-03-06 09:00 | 176.83 | 176.8
2018-03-06 09:30 | 190.17 | 190.02
2018-03-06 10:00 | 180.39 | 180.35
2018-03-06 10:30 | 167.08 | 167.06
2018-03-06 11:00 | 164.24 | 164.23
2018-03-06 11:30 | 158.87 | 158.87
2018-03-06 12:00 | 142.24 | 142.24
2018-03-06 12:30 | 138.31 | 138.26
2018-03-06 13:00 | 135.93 | 135.81
2018-03-06 13:30 | 138.21 | 138.14
2018-03-06 14:00 | 142.99 | 142.89
2018-03-06 14:30 | 123.72 | 123.57
2018-03-06 15:00 | 113.77 | 113.58
2018-03-06 15:30 | 108.15 | 107.89
2018-03-06 16:00 | 120.76 | 120.5
2018-03-06 16:30 | 111.46 | 111.15
2018-03-06 17:00 | 127.5 | 127.25
2018-03-06 17:30 | 146.67 | 146.46
2018-03-06 18:00 | 147.5 | 147.26
2018-03-06 18:30 | 151.28 | 151.1
2018-03-06 19:00 | 150.49 | 150.29
2018-03-06 19:30 | 141.41 | 141.04
2018-03-06 20:00 | 123.16 | 122.59
2018-03-06 20:30 | 114.08 | 113.54
2018-03-06 21:00 | 71.91 | 71.5
2018-03-06 21:30 | 57.05 | 56.57
2018-03-06 22:00 | 40.89 | 39.47
2018-03-06 22:30 | 67.9 | 66.63
2018-03-06 23:00 | 74.96 | 73.76
2018-03-06 23:30 | 40.34 | 38.05
2018-03-07 | 17.86 | -10.93
2018-03-07 00:30 | 36.72 | -33.55
2018-03-07 01:00 | 40.61 | -37.43
2018-03-07 01:30 | 49.92 | -47.32
2018-03-07 02:00 | 52.1 | -49.62
2018-03-07 02:30 | 45.26 | -42.13
2018-03-07 03:00 | 37.68 | -33.35
2018-03-07 03:30 | 42.4 | -38.87
2018-03-07 04:00 | 44.9 | -41.72
2018-03-07 04:30 | 47.18 | -44.68
2018-03-07 05:00 | 37.08 | -34.4
2018-03-07 05:30 | 16.78 | -12.86
2018-03-07 06:00 | 10.68 | 7.09
2018-03-07 06:30 | 5 | -4.72
2018-03-07 07:00 | 26.38 | 26.2
2018-03-07 07:30 | 45.01 | 33.16
2018-03-07 08:00 | 68.69 | 61.43
2018-03-07 08:30 | 107.98 | 102.25
2018-03-07 09:00 | 118.11 | 111.54
2018-03-07 09:30 | 112.71 | 105.22
2018-03-07 10:00 | 108.58 | 100.54
2018-03-07 10:30 | 85.61 | 73.85
2018-03-07 11:00 | 73.98 | 58.28
2018-03-07 11:30 | 87.95 | 75.28
2018-03-07 12:00 | 94.37 | 83.47
2018-03-07 12:30 | 68.97 | 54.52
2018-03-07 13:00 | 56.84 | 37.45
2018-03-07 13:30 | 61.04 | 43.24
2018-03-07 14:00 | 65.31 | 48.67
2018-03-07 14:30 | 73.78 | 60.77
2018-03-07 15:00 | 82.53 | 72.05
2018-03-07 15:30 | 89.46 | 80.69
2018-03-07 16:00 | 107.32 | 100.62
2018-03-07 16:30 | 123.94 | 118.62
2018-03-07 17:00 | 140.15 | 135.96
2018-03-07 17:30 | 148.29 | 145.08
2018-03-07 18:00 | 148.35 | 145.5
2018-03-07 18:30 | 155.92 | 153.17
2018-03-07 19:00 | 173.29 | 170.7
2018-03-07 19:30 | 157.31 | 155.03
2018-03-07 20:00 | 138.31 | 136.15
2018-03-07 20:30 | 137.5 | 137.24
2018-03-07 21:00 | 108.76 | 108.63
2018-03-07 21:30 | 97.83 | 96.9
2018-03-07 22:00 | 80.17 | 79.49
2018-03-07 22:30 | 74.13 | 73.54
2018-03-07 23:00 | 82.48 | 82.03
2018-03-07 23:30 | 60.33 | 60
2018-03-08 | 7.94 | 6.23
2018-03-08 00:30 | 22.79 | -22.5
2018-03-08 01:00 | 36.25 | -36.09
2018-03-08 01:30 | 45.79 | -45.67
2018-03-08 02:00 | 50.28 | -50.2
2018-03-08 02:30 | 37.49 | -37.44
2018-03-08 03:00 | 46.6 | -46.54
2018-03-08 03:30 | 46.91 | -46.83
2018-03-08 04:00 | 45.44 | -45.36
2018-03-08 04:30 | 30.8 | -30.72
2018-03-08 05:00 | 35.74 | -35.47
2018-03-08 05:30 | 18.38 | -17.15
2018-03-08 06:00 | 11.64 | 8.86
2018-03-08 06:30 | 55.38 | 54.14
2018-03-08 07:00 | 85.57 | 83.96
2018-03-08 07:30 | 112.21 | 110.09
2018-03-08 08:00 | 111.24 | 108.05
2018-03-08 08:30 | 103.4 | 95.3
2018-03-08 09:00 | 125.44 | 107.47
2018-03-08 09:30 | 111.62 | 90.56
2018-03-08 10:00 | 115.04 | 93.71
2018-03-08 10:30 | 102.19 | 76.86
2018-03-08 11:00 | 102.98 | 81.06
2018-03-08 11:30 | 88.94 | 62.29
2018-03-08 12:00 | 91.88 | 65.07
2018-03-08 12:30 | 100.79 | 78.52
2018-03-08 13:00 | 92.53 | 68.86
2018-03-08 13:30 | 79.51 | 49.73
2018-03-08 14:00 | 80.71 | 51.69
2018-03-08 14:30 | 77.66 | 47.58
2018-03-08 15:00 | 83.75 | 57.91
2018-03-08 15:30 | 85.57 | 61.9
2018-03-08 16:00 | 106.52 | 89.06
2018-03-08 16:30 | 105.38 | 89.15
2018-03-08 17:00 | 121.7 | 109.01
2018-03-08 17:30 | 146.57 | 137.09
2018-03-08 18:00 | 120.74 | 109.77
2018-03-08 18:30 | 143.31 | 133.33
2018-03-08 19:00 | 174.57 | 166.05
2018-03-08 19:30 | 160.27 | 152.33
2018-03-08 20:00 | 150.3 | 142.65
2018-03-08 20:30 | 162.71 | 156.37
2018-03-08 21:00 | 145.67 | 139.2
2018-03-08 21:30 | 103.52 | 101.78
2018-03-08 22:00 | 59.81 | 59.47
2018-03-08 22:30 | 55.47 | 55.31
2018-03-08 23:00 | 79.11 | 79.08
2018-03-08 23:30 | 61.36 | 61.34
2018-03-09 | 9.11 | 5.56
2018-03-09 00:30 | 20.91 | -19.2
2018-03-09 01:00 | 37.68 | -36.44
2018-03-09 01:30 | 48.82 | -47.78
2018-03-09 02:00 | 47.98 | -46.83
2018-03-09 02:30 | 50.69 | -49.7
2018-03-09 03:00 | 54.38 | -53.35
2018-03-09 03:30 | 56.21 | -55.28
2018-03-09 04:00 | 58.92 | -57.94
2018-03-09 04:30 | 48.39 | -47.38
2018-03-09 05:00 | 37.92 | -36.74
2018-03-09 05:30 | 17.65 | -15.39
2018-03-09 06:00 | 8.75 | 0.23
2018-03-09 06:30 | 53.94 | 52.83
2018-03-09 07:00 | 72.49 | 70.63
2018-03-09 07:30 | 91.68 | 88.7
2018-03-09 08:00 | 113.39 | 97.59
2018-03-09 08:30 | 108.07 | 87.19
2018-03-09 09:00 | 82.81 | 45.02
2018-03-09 09:30 | 80.45 | 36.31
2018-03-09 10:00 | 69.12 | 32.18
2018-03-09 10:30 | 69.69 | 47.2
2018-03-09 11:00 | 70.74 | 54.45
2018-03-09 11:30 | 57.25 | 37.18
2018-03-09 12:00 | 54.53 | 34.72
2018-03-09 12:30 | 50.97 | 29.42
2018-03-09 13:00 | 58.08 | 39.96
2018-03-09 13:30 | 58.17 | 40.64
2018-03-09 14:00 | 49.64 | 28.92
2018-03-09 14:30 | 44.62 | 18.16
2018-03-09 15:00 | 42.24 | 13.31
2018-03-09 15:30 | 46.1 | 25.11
2018-03-09 16:00 | 60.02 | 53.42
2018-03-09 16:30 | 71.85 | 70.51
2018-03-09 17:00 | 85.49 | 84.52
2018-03-09 17:30 | 94.37 | 93.96
2018-03-09 18:00 | 101.39 | 100.79
2018-03-09 18:30 | 94.37 | 93.73
2018-03-09 19:00 | 112.58 | 111.88
2018-03-09 19:30 | 119.62 | 119.37
2018-03-09 20:00 | 98.22 | 97.73
2018-03-09 20:30 | 89.41 | 81.76
2018-03-09 21:00 | 60.61 | 49.44
2018-03-09 21:30 | 52.92 | 40.76
2018-03-09 22:00 | 39.96 | 24.48
2018-03-09 22:30 | 45.09 | 34.31
2018-03-09 23:00 | 49.98 | 41.85
2018-03-09 23:30 | 34.04 | 22.74
2018-03-10 | 25.03 | -1.38
2018-03-10 00:30 | 23.85 | -22.15
2018-03-10 01:00 | 42.2 | -40.98
2018-03-10 01:30 | 56.3 | -55.24
2018-03-10 02:00 | 50.53 | -49.41
2018-03-10 02:30 | 52.85 | -51.83
2018-03-10 03:00 | 59.86 | -58.8
2018-03-10 03:30 | 55.02 | -53.98
2018-03-10 04:00 | 45.73 | -44.64
2018-03-10 04:30 | 48.57 | -47.58
2018-03-10 05:00 | 45.01 | -43.92
2018-03-10 05:30 | 34.69 | -33.46
2018-03-10 06:00 | 36.44 | -35.01
2018-03-10 06:30 | 30.29 | -28.48
2018-03-10 07:00 | 26.26 | -24.08
2018-03-10 07:30 | 17.32 | -10.41
2018-03-10 08:00 | 18.52 | 3.06
2018-03-10 08:30 | 23.32 | -1.32
2018-03-10 09:00 | 44.98 | 21.48
2018-03-10 09:30 | 47.02 | 18.91
2018-03-10 10:00 | 42.58 | 2.73
2018-03-10 10:30 | 45.26 | 15.58
2018-03-10 11:00 | 45.37 | 11.17
2018-03-10 11:30 | 46.18 | -10.52
2018-03-10 12:00 | 44.64 | -7.47
2018-03-10 12:30 | 45.91 | -10.22
2018-03-10 13:00 | 50.55 | 11.21
2018-03-10 13:30 | 55.88 | 5.77
2018-03-10 14:00 | 40.14 | -7.38
2018-03-10 14:30 | 28.83 | 13.68
2018-03-10 15:00 | 41.74 | 33.45
2018-03-10 15:30 | 55.2 | 50.19
2018-03-10 16:00 | 77.08 | 73.98
2018-03-10 16:30 | 88.68 | 86.28
2018-03-10 17:00 | 97.23 | 95.06
2018-03-10 17:30 | 101.77 | 99.95
2018-03-10 18:00 | 99.61 | 97.88
2018-03-10 18:30 | 106.97 | 105.18
2018-03-10 19:00 | 121.96 | 115.84
2018-03-10 19:30 | 110.73 | 104.56
2018-03-10 20:00 | 112.04 | 106.75
2018-03-10 20:30 | 112.26 | 107.85
2018-03-10 21:00 | 93.78 | 89.28
2018-03-10 21:30 | 74.36 | 68.7
2018-03-10 22:00 | 49.77 | 42.28
2018-03-10 22:30 | 44.99 | 37.01
2018-03-10 23:00 | 53.14 | 47.14
2018-03-10 23:30 | 43.72 | 38
2018-03-11 | 13.91 | -1.78
2018-03-11 00:30 | 25.86 | -25.75
2018-03-11 01:00 | 41.78 | -41.7
2018-03-11 01:30 | 53.56 | -53.48
2018-03-11 02:00 | 57.02 | -56.83
2018-03-11 02:30 | 63.19 | -63.15
2018-03-11 03:00 | 62.71 | -62.68
2018-03-11 03:30 | 63.38 | -63.35
2018-03-11 04:00 | 64.44 | -64.41
2018-03-11 04:30 | 58.96 | -58.95
2018-03-11 05:00 | 63.09 | -63.07
2018-03-11 05:30 | 59.91 | -59.89
2018-03-11 06:00 | 57.63 | -57.58
2018-03-11 06:30 | 54.9 | -54.81
2018-03-11 07:00 | 38.66 | -38.55
2018-03-11 07:30 | 28.25 | -27.76
2018-03-11 08:00 | 32.26 | -31.24
2018-03-11 08:30 | 36.29 | -26.11
2018-03-11 09:00 | 63.08 | -15.95
2018-03-11 09:30 | 67.52 | -10.36
2018-03-11 10:00 | 68.28 | 2.35
2018-03-11 10:30 | 68.15 | -1.78
2018-03-11 11:00 | 75.13 | -29.39
2018-03-11 11:30 | 72.32 | -20.16
2018-03-11 12:00 | 74.32 | -22.6
2018-03-11 12:30 | 79.53 | -36.22
2018-03-11 13:00 | 71.89 | -11.93
2018-03-11 13:30 | 68.84 | -3.13
2018-03-11 14:00 | 69.63 | -13.56
2018-03-11 14:30 | 68.15 | -2.86
2018-03-11 15:00 | 68.7 | 4.93
2018-03-11 15:30 | 69.4 | 13.75
2018-03-11 16:00 | 69.43 | 18.9
2018-03-11 16:30 | 72.92 | 31.54
2018-03-11 17:00 | 80.53 | 46.88
2018-03-11 17:30 | 88.76 | 59.65
2018-03-11 18:00 | 103.42 | 79.42
2018-03-11 18:30 | 124.42 | 103.96
2018-03-11 19:00 | 137.1 | 118.08
2018-03-11 19:30 | 130.88 | 113.33
2018-03-11 20:00 | 119.2 | 100.98
2018-03-11 20:30 | 113.01 | 94.74
2018-03-11 21:00 | 65.49 | 58.89
2018-03-11 21:30 | 59.52 | 53.39
2018-03-11 22:00 | 44.46 | 37.83
2018-03-11 22:30 | 52.3 | 47.41
2018-03-11 23:00 | 74.22 | 71.6
2018-03-11 23:30 | 53.3 | 50.18
2018-03-12 | 19.07 | 8.93
2018-03-12 00:30 | 24.78 | -18.1
2018-03-12 01:00 | 35.84 | -31.73
2018-03-12 01:30 | 42.11 | -38.77
2018-03-12 02:00 | 40.63 | -37.11
2018-03-12 02:30 | 38.49 | -34.81
2018-03-12 03:00 | 43.69 | -40.32
2018-03-12 03:30 | 44.09 | -40.64
2018-03-12 04:00 | 42.15 | -38.39
2018-03-12 04:30 | 35.31 | -30.84
2018-03-12 05:00 | 30.48 | -24.9
2018-03-12 05:30 | 31.26 | -23.26
2018-03-12 06:00 | 51.22 | 47.18
2018-03-12 06:30 | 76.72 | 70
2018-03-12 07:00 | 91.8 | 83.22
2018-03-12 07:30 | 100.21 | 92.27
2018-03-12 08:00 | 105.67 | 96.11
2018-03-12 08:30 | 101.71 | 93.12
2018-03-12 09:00 | 93.08 | 82.22
2018-03-12 09:30 | 94.51 | 82
2018-03-12 10:00 | 111.42 | 100.84
2018-03-12 10:30 | 108.84 | 98.61
2018-03-12 11:00 | 97.4 | 85.22
2018-03-12 11:30 | 101.47 | 89.03
2018-03-12 12:00 | 105.99 | 93.62
2018-03-12 12:30 | 111.36 | 99.94
2018-03-12 13:00 | 113.41 | 102.19
2018-03-12 13:30 | 113.65 | 102.11
2018-03-12 14:00 | 118.05 | 106.52
2018-03-12 14:30 | 122.19 | 111.47
2018-03-12 15:00 | 114.9 | 104.04
2018-03-12 15:30 | 107.54 | 98.17
2018-03-12 16:00 | 104.13 | 96.29
2018-03-12 16:30 | 119.43 | 113.12
2018-03-12 17:00 | 137.4 | 132.36
2018-03-12 17:30 | 153.56 | 149.83
2018-03-12 18:00 | 157.91 | 154.9
2018-03-12 18:30 | 173.12 | 170.35
2018-03-12 19:00 | 203.87 | 201.13
2018-03-12 19:30 | 182.89 | 180.56
2018-03-12 20:00 | 153.84 | 153.18
2018-03-12 20:30 | 138.11 | 137.7
2018-03-12 21:00 | 100.6 | 100.1
2018-03-12 21:30 | 64.68 | 64.26
2018-03-12 22:00 | 38.78 | 38.53
2018-03-12 22:30 | 55.31 | 55.17
2018-03-12 23:00 | 81.64 | 81.27
2018-03-12 23:30 | 56.16 | 55.87
2018-03-13 | 8.56 | 7.13
2018-03-13 00:30 | 12.22 | -11.81
2018-03-13 01:00 | 27.05 | -26.94
2018-03-13 01:30 | 37.88 | -37.77
2018-03-13 02:00 | 39.44 | -39.35
2018-03-13 02:30 | 40.18 | -40.12
2018-03-13 03:00 | 44.18 | -44.12
2018-03-13 03:30 | 46.64 | -46.57
2018-03-13 04:00 | 43.68 | -43.52
2018-03-13 04:30 | 40.47 | -37.14
2018-03-13 05:00 | 25.74 | -20.45
2018-03-13 05:30 | 14.51 | -7.13
2018-03-13 06:00 | 11.83 | -5.22
2018-03-13 06:30 | 31 | 30.51
2018-03-13 07:00 | 47.14 | 47.13
2018-03-13 07:30 | 79.3 | 69.19
2018-03-13 08:00 | 74.14 | 44.99
2018-03-13 08:30 | 80.46 | 49.75
2018-03-13 09:00 | 79.64 | 41.88
2018-03-13 09:30 | 85.01 | 50.83
2018-03-13 10:00 | 86.83 | 53.82
2018-03-13 10:30 | 88.05 | 54.33
2018-03-13 11:00 | 91.88 | 59.71
2018-03-13 11:30 | 93.23 | 60.54
2018-03-13 12:00 | 87.89 | 50.8
2018-03-13 12:30 | 85.36 | 46.23
2018-03-13 13:00 | 91.37 | 57.16
2018-03-13 13:30 | 89.56 | 55.62
2018-03-13 14:00 | 81.97 | 48.22
2018-03-13 14:30 | 87 | 56.37
2018-03-13 15:00 | 84.65 | 54.22
2018-03-13 15:30 | 107.28 | 86.85
2018-03-13 16:00 | 125.64 | 109.5
2018-03-13 16:30 | 132.14 | 117.13
2018-03-13 17:00 | 136.4 | 122.6
2018-03-13 17:30 | 135.09 | 122.53
2018-03-13 18:00 | 130.79 | 119.07
2018-03-13 18:30 | 150.62 | 140.46
2018-03-13 19:00 | 170.99 | 162.11
2018-03-13 19:30 | 162.05 | 153.84
2018-03-13 20:00 | 159.63 | 152.63
2018-03-13 20:30 | 151.89 | 145.32
2018-03-13 21:00 | 125.69 | 125.69
2018-03-13 21:30 | 103.16 | 102.74
2018-03-13 22:00 | 81.72 | 80.75
2018-03-13 22:30 | 80.54 | 79.28
2018-03-13 23:00 | 93.69 | 92.17
2018-03-13 23:30 | 67.85 | 64.8
2018-03-14 | 22.65 | 11.32
2018-03-14 00:30 | 25.15 | -15.2
2018-03-14 01:00 | 37.11 | -30.75
2018-03-14 01:30 | 40.97 | -35.13
2018-03-14 02:00 | 44.55 | -39.02
2018-03-14 02:30 | 38.97 | -31.91
2018-03-14 03:00 | 35.18 | -26.5
2018-03-14 03:30 | 34.38 | -25.88
2018-03-14 04:00 | 31.39 | -21.3
2018-03-14 04:30 | 36.18 | -28.98
2018-03-14 05:00 | 21.25 | -2.61
2018-03-14 05:30 | 28.83 | 22.81
2018-03-14 06:00 | 47.68 | 44.95
2018-03-14 06:30 | 73.77 | 72.84
2018-03-14 07:00 | 90.68 | 90.34
2018-03-14 07:30 | 106.17 | 104.78
2018-03-14 08:00 | 117.44 | 103.92
2018-03-14 08:30 | 114.95 | 98.84
2018-03-14 09:00 | 107.78 | 87.72
2018-03-14 09:30 | 100.01 | 74.49
2018-03-14 10:00 | 96.66 | 68.42
2018-03-14 10:30 | 94.99 | 63.15
2018-03-14 11:00 | 101.48 | 72.4
2018-03-14 11:30 | 117.39 | 93.97
2018-03-14 12:00 | 108.78 | 82.1
2018-03-14 12:30 | 92.41 | 59.16
2018-03-14 13:00 | 89.09 | 53.54
2018-03-14 13:30 | 95.67 | 63.05
2018-03-14 14:00 | 90.78 | 54.91
2018-03-14 14:30 | 90.37 | 53.55
2018-03-14 15:00 | 93.21 | 59.05
2018-03-14 15:30 | 94.09 | 62.68
2018-03-14 16:00 | 95.23 | 65.69
2018-03-14 16:30 | 107.98 | 83.94
2018-03-14 17:00 | 128.02 | 110.48
2018-03-14 17:30 | 141.58 | 127.84
2018-03-14 18:00 | 139.01 | 126.88
2018-03-14 18:30 | 159.75 | 149.04
2018-03-14 19:00 | 172.44 | 162.07
2018-03-14 19:30 | 160.09 | 150.36
2018-03-14 20:00 | 162.35 | 152.66
2018-03-14 20:30 | 160.02 | 150.75
2018-03-14 21:00 | 129.26 | 123.57
2018-03-14 21:30 | 110.18 | 108.68
2018-03-14 22:00 | 89.31 | 88.23
2018-03-14 22:30 | 89.22 | 88.53
2018-03-14 23:00 | 102.54 | 101.97
2018-03-14 23:30 | 77.11 | 76.68
2018-03-15 | 27.87 | 27.27
2018-03-15 00:30 | 5.9 | -4.1
2018-03-15 01:00 | 16.57 | -16.39
2018-03-15 01:30 | 15.15 | -15.05
2018-03-15 02:00 | 17.13 | -17.07
2018-03-15 02:30 | 4.81 | 4.81
2018-03-15 03:00 | 15.53 | -0.21
2018-03-15 03:30 | 19.4 | 2.89
2018-03-15 04:00 | 18.82 | -0.51
2018-03-15 04:30 | 19.49 | 6.95
2018-03-15 05:00 | 20.15 | 12.08
2018-03-15 05:30 | 32.92 | 30.53
2018-03-15 06:00 | 54.32 | 53.34
2018-03-15 06:30 | 69.89 | 69.78
2018-03-15 07:00 | 98.04 | 96.21
2018-03-15 07:30 | 95.19 | 90.21
2018-03-15 08:00 | 87.53 | 77.36
2018-03-15 08:30 | 82.34 | 74.29
2018-03-15 09:00 | 80.77 | 75.71
2018-03-15 09:30 | 82.92 | 77.1
2018-03-15 10:00 | 59.81 | 56.27
2018-03-15 10:30 | 49.45 | 47.58
2018-03-15 11:00 | 45.45 | 39.45
2018-03-15 11:30 | 50.63 | 50.61
2018-03-15 12:00 | 40.42 | 40.37
2018-03-15 12:30 | 40.56 | 40.54
2018-03-15 13:00 | 17.3 | 16.65
2018-03-15 13:30 | 21.62 | 21.05
2018-03-15 14:00 | 8.67 | 5.03
2018-03-15 14:30 | 21.36 | -13.1
2018-03-15 15:00 | 40.09 | -34.93
2018-03-15 15:30 | 34.99 | 32.59
2018-03-15 16:00 | 47.45 | 45.97
2018-03-15 16:30 | 70.11 | 69.91
2018-03-15 17:00 | 88.44 | 88.42
2018-03-15 17:30 | 108.12 | 108.11
2018-03-15 18:00 | 113 | 113
2018-03-15 18:30 | 111.78 | 111.76
2018-03-15 19:00 | 127.55 | 127.43
2018-03-15 19:30 | 118.24 | 118.23
2018-03-15 20:00 | 119.93 | 119.67
2018-03-15 20:30 | 120.28 | 119.74
2018-03-15 21:00 | 109.12 | 108.16
2018-03-15 21:30 | 106.13 | 104.54
2018-03-15 22:00 | 87.31 | 84.07
2018-03-15 22:30 | 84.1 | 82.52
2018-03-15 23:00 | 99.03 | 98.5
2018-03-15 23:30 | 79.26 | 78.38
2018-03-16 | 32.09 | 29.05
2018-03-16 00:30 | 15.61 | -4.85
2018-03-16 01:00 | 26.77 | -21.67
2018-03-16 01:30 | 25.43 | -19.2
2018-03-16 02:00 | 32.51 | -27.96
2018-03-16 02:30 | 34.08 | -29.42
2018-03-16 03:00 | 41.73 | -38.24
2018-03-16 03:30 | 37.72 | -33.55
2018-03-16 04:00 | 34.55 | -29.65
2018-03-16 04:30 | 32.2 | -27.23
2018-03-16 05:00 | 20.73 | -11.97
2018-03-16 05:30 | 19.05 | 12.37
2018-03-16 06:00 | 25.29 | 21.65
2018-03-16 06:30 | 44.8 | 44
2018-03-16 07:00 | 60.57 | 60.5
2018-03-16 07:30 | 66.71 | 66.28
2018-03-16 08:00 | 52.17 | 51.17
2018-03-16 08:30 | 30.71 | 30.4
2018-03-16 09:00 | 20.84 | 20.78
2018-03-16 09:30 | 11.38 | 11.21
2018-03-16 10:00 | 4.99 | -1.41
2018-03-16 10:30 | 6.78 | -3.47
2018-03-16 11:00 | 15.27 | 14.7
2018-03-16 11:30 | 23.61 | 23.33
2018-03-16 12:00 | 39.93 | 39.71
2018-03-16 12:30 | 30.46 | 28.7
2018-03-16 13:00 | 34.67 | 21.01
2018-03-16 13:30 | 50.14 | 24.46
2018-03-16 14:00 | 64.7 | 54.37
2018-03-16 14:30 | 74.48 | 66.64
2018-03-16 15:00 | 81.08 | 74.26
2018-03-16 15:30 | 92.7 | 86.96
2018-03-16 16:00 | 112.74 | 107.86
2018-03-16 16:30 | 132.45 | 128.52
2018-03-16 17:00 | 155.65 | 152.78
2018-03-16 17:30 | 158.82 | 156.91
2018-03-16 18:00 | 152.35 | 151.17
2018-03-16 18:30 | 151.31 | 150.26
2018-03-16 19:00 | 167.39 | 166.31
2018-03-16 19:30 | 149.98 | 149.01
2018-03-16 20:00 | 133.12 | 131.16
2018-03-16 20:30 | 122.78 | 117.43
2018-03-16 21:00 | 97.95 | 92.08
2018-03-16 21:30 | 80.06 | 74.36
2018-03-16 22:00 | 62.32 | 56.49
2018-03-16 22:30 | 105.49 | 101.98
2018-03-16 23:00 | 108.83 | 104.74
2018-03-16 23:30 | 83.08 | 78.71
2018-03-17 | 43.08 | 38.69
2018-03-17 00:30 | 17.94 | 16.99
2018-03-17 01:00 | 7.56 | -5.94
2018-03-17 01:30 | 20.74 | -20.31
2018-03-17 02:00 | 20.68 | -20.45
2018-03-17 02:30 | 17.9 | -17.7
2018-03-17 03:00 | 17.3 | -17.14
2018-03-17 03:30 | 19 | -18.85
2018-03-17 04:00 | 26.47 | -25.59
2018-03-17 04:30 | 30.8 | -25.61
2018-03-17 05:00 | 29.4 | -24.14
2018-03-17 05:30 | 27.52 | -22.87
2018-03-17 06:00 | 26.22 | -21.41
2018-03-17 06:30 | 14.33 | -4.48
2018-03-17 07:00 | 16.83 | 13.06
2018-03-17 07:30 | 22.31 | 21.79
2018-03-17 08:00 | 12.62 | 10.95
2018-03-17 08:30 | 26.49 | 4.51
2018-03-17 09:00 | 54.85 | 14.92
2018-03-17 09:30 | 64.57 | 11.04
2018-03-17 10:00 | 66.24 | 12.09
2018-03-17 10:30 | 66.18 | 8.75
2018-03-17 11:00 | 67.5 | 9.33
2018-03-17 11:30 | 68.32 | 14.43
2018-03-17 12:00 | 70.39 | 21.52
2018-03-17 12:30 | 71.1 | 22.89
2018-03-17 13:00 | 71.75 | 22.6
2018-03-17 13:30 | 69.67 | 6.97
2018-03-17 14:00 | 77.02 | 33.81
2018-03-17 14:30 | 75.44 | 29.65
2018-03-17 15:00 | 87.18 | 52.17
2018-03-17 15:30 | 90.74 | 69.61
2018-03-17 16:00 | 107.83 | 94.26
2018-03-17 16:30 | 148.96 | 139.41
2018-03-17 17:00 | 164.11 | 155.4
2018-03-17 17:30 | 176.46 | 169.16
2018-03-17 18:00 | 187.71 | 181.4
2018-03-17 18:30 | 203.6 | 197.32
2018-03-17 19:00 | 206.89 | 200.25
2018-03-17 19:30 | 188.38 | 182.26
2018-03-17 20:00 | 168.57 | 162.64
2018-03-17 20:30 | 152.15 | 144.19
2018-03-17 21:00 | 134.36 | 122.02
2018-03-17 21:30 | 121.16 | 108.92
2018-03-17 22:00 | 117.37 | 106.57
2018-03-17 22:30 | 115.65 | 105.61
2018-03-17 23:00 | 117.1 | 107.97
2018-03-17 23:30 | 100.75 | 100.67
2018-03-18 | 64.23 | 63.27
2018-03-18 00:30 | 51.59 | 49.8
2018-03-18 01:00 | 26.61 | 21.8
2018-03-18 01:30 | 18.63 | 9.12
2018-03-18 02:00 | 24.32 | 16.96
2018-03-18 02:30 | 22.37 | 13.01
2018-03-18 03:00 | 20.67 | 9.05
2018-03-18 03:30 | 18.55 | 0.98
2018-03-18 04:00 | 19.07 | -5.69
2018-03-18 04:30 | 18.79 | -1.42
2018-03-18 05:00 | 18.76 | -4.32
2018-03-18 05:30 | 24.64 | 16.43
2018-03-18 06:00 | 22.8 | 14.13
2018-03-18 06:30 | 17.83 | 7.27
2018-03-18 07:00 | 17.89 | 9.58
2018-03-18 07:30 | 58.74 | 57.3
2018-03-18 08:00 | 88.21 | 87.85
2018-03-18 08:30 | 84.53 | 84.51
2018-03-18 09:00 | 85.15 | 82.41
2018-03-18 09:30 | 89.97 | 86.41
2018-03-18 10:00 | 106.31 | 101.03
2018-03-18 10:30 | 130.03 | 120.28
2018-03-18 11:00 | 146.57 | 125.28
2018-03-18 11:30 | 172.88 | 150.1
2018-03-18 12:00 | 139.21 | 110.39
2018-03-18 12:30 | 132.18 | 101.08
2018-03-18 13:00 | 132.93 | 102.71
2018-03-18 13:30 | 137.82 | 108.55
2018-03-18 14:00 | 143.62 | 114.2
2018-03-18 14:30 | 148.25 | 119.47
2018-03-18 15:00 | 154.4 | 126.08
2018-03-18 15:30 | 166.64 | 139.75
2018-03-18 16:00 | 159.01 | 139.81
2018-03-18 16:30 | 181.77 | 165.79
2018-03-18 17:00 | 203.98 | 189.28
2018-03-18 17:30 | 214.32 | 201.02
2018-03-18 18:00 | 224.17 | 211.68
2018-03-18 18:30 | 222.52 | 209.24
2018-03-18 19:00 | 250.03 | 237.26
2018-03-18 19:30 | 224.49 | 212.22
2018-03-18 20:00 | 200.47 | 188.66
2018-03-18 20:30 | 189.98 | 179.9
2018-03-18 21:00 | 165.07 | 157.19
2018-03-18 21:30 | 172.09 | 163.24
2018-03-18 22:00 | 162.82 | 155.11
2018-03-18 22:30 | 167.91 | 161.17
2018-03-18 23:00 | 168.79 | 162.48
2018-03-18 23:30 | 114.93 | 110.93
2018-03-19 | 76.56 | 75.94
2018-03-19 00:30 | 57.17 | 55.81
2018-03-19 01:00 | 51.82 | 49.81
2018-03-19 01:30 | 40.85 | 38.1
2018-03-19 02:00 | 38.88 | 35.27
2018-03-19 02:30 | 29.15 | 23.99
2018-03-19 03:00 | 23.95 | 17.33
2018-03-19 03:30 | 20.16 | 11.44
2018-03-19 04:00 | 17.27 | 6.2
2018-03-19 04:30 | 14.62 | -2.18
2018-03-19 05:00 | 13.51 | 3.77
2018-03-19 05:30 | 25.28 | 23.44
2018-03-19 06:00 | 52.63 | 52.03
2018-03-19 06:30 | 84.18 | 84.12
2018-03-19 07:00 | 116.17 | 114.55
2018-03-19 07:30 | 130.68 | 115.98
2018-03-19 08:00 | 130.88 | 113.34
2018-03-19 08:30 | 124.63 | 102.13
2018-03-19 09:00 | 125.99 | 98.5
2018-03-19 09:30 | 162.78 | 128.25
2018-03-19 10:00 | 168.48 | 132.79
2018-03-19 10:30 | 175.54 | 140.59
2018-03-19 11:00 | 182.39 | 148.86
2018-03-19 11:30 | 188.58 | 159.32
2018-03-19 12:00 | 176.13 | 146.11
2018-03-19 12:30 | 169.93 | 138.36
2018-03-19 13:00 | 172.72 | 140.51
2018-03-19 13:30 | 184.89 | 153.63
2018-03-19 14:00 | 201.59 | 172.7
2018-03-19 14:30 | 209.78 | 187.37
2018-03-19 15:00 | 209.37 | 191.17
2018-03-19 15:30 | 221.59 | 204.43
2018-03-19 16:00 | 226.84 | 210.01
2018-03-19 16:30 | 230 | 213.18
2018-03-19 17:00 | 245.43 | 229.65
2018-03-19 17:30 | 236.92 | 235.46
2018-03-19 18:00 | 235.73 | 234.84
2018-03-19 18:30 | 238.74 | 237.74
2018-03-19 19:00 | 273.2 | 272.19
2018-03-19 19:30 | 269.22 | 268.72
2018-03-19 20:00 | 257.85 | 257.6
2018-03-19 20:30 | 241.48 | 241.19
2018-03-19 21:00 | 192.09 | 191.25
2018-03-19 21:30 | 157.55 | 157.08
2018-03-19 22:00 | 152.51 | 152.51
2018-03-19 22:30 | 154.86 | 154.69
2018-03-19 23:00 | 161.03 | 160.71
2018-03-19 23:30 | 125.76 | 125.16
2018-03-20 | 75.49 | 74.32
2018-03-20 00:30 | 44.37 | 43.85
2018-03-20 01:00 | 42.14 | 41.18
2018-03-20 01:30 | 29.74 | 27.99
2018-03-20 02:00 | 22.91 | 20.14
2018-03-20 02:30 | 14.48 | 9.7
2018-03-20 03:00 | 15.99 | 10.91
2018-03-20 03:30 | 15.34 | 9.89
2018-03-20 04:00 | 12.78 | -5.61
2018-03-20 04:30 | 11.22 | 2.51
2018-03-20 05:00 | 9.07 | -1.27
2018-03-20 05:30 | 42.48 | 41.94
2018-03-20 06:00 | 53.14 | 52.89
2018-03-20 06:30 | 68.82 | 68.38
2018-03-20 07:00 | 84.24 | 83.4
2018-03-20 07:30 | 87.65 | 87.64
2018-03-20 08:00 | 75.6 | 72.82
2018-03-20 08:30 | 97.58 | 81.68
2018-03-20 09:00 | 130.03 | 115.8
2018-03-20 09:30 | 133.83 | 121.78
2018-03-20 10:00 | 140.19 | 128.11
2018-03-20 10:30 | 136.11 | 122.69
2018-03-20 11:00 | 126.5 | 112.81
2018-03-20 11:30 | 117.58 | 102.77
2018-03-20 12:00 | 96.02 | 76.47
2018-03-20 12:30 | 70.04 | 57.29
2018-03-20 13:00 | 80.3 | 69.95
2018-03-20 13:30 | 95.65 | 86.85
2018-03-20 14:00 | 115.65 | 108.26
2018-03-20 14:30 | 130.48 | 123.79
2018-03-20 15:00 | 157.42 | 151.99
2018-03-20 15:30 | 176.45 | 171.78
2018-03-20 16:00 | 198.31 | 194.48
2018-03-20 16:30 | 213.26 | 210.05
2018-03-20 17:00 | 239.79 | 237.3
2018-03-20 17:30 | 245.27 | 245.06
2018-03-20 18:00 | 240.05 | 240.01
2018-03-20 18:30 | 235.84 | 235.73
2018-03-20 19:00 | 248.01 | 247.89
2018-03-20 19:30 | 233.24 | 233.12
2018-03-20 20:00 | 221.91 | 221.26
2018-03-20 20:30 | 201.18 | 200.45
2018-03-20 21:00 | 154.73 | 152.96
2018-03-20 21:30 | 140.17 | 137.15
2018-03-20 22:00 | 128.93 | 126.31
2018-03-20 22:30 | 131.56 | 129.52
2018-03-20 23:00 | 154.23 | 152.78
2018-03-20 23:30 | 117.93 | 116.17
2018-03-21 | 84.72 | 80.96
2018-03-21 00:30 | 71.92 | 68.3
2018-03-21 01:00 | 59.82 | 56.09
2018-03-21 01:30 | 62.08 | 58.88
2018-03-21 02:00 | 66.23 | 64.83
2018-03-21 02:30 | 45.26 | 45.26
2018-03-21 03:00 | 44.87 | 44.87
2018-03-21 03:30 | 46.65 | 46.65
2018-03-21 04:00 | 40.01 | 40
2018-03-21 04:30 | 43.81 | 43.78
2018-03-21 05:00 | 33.81 | 33.56
2018-03-21 05:30 | 51.73 | 51.26
2018-03-21 06:00 | 60.45 | 59.63
2018-03-21 06:30 | 95.57 | 93.18
2018-03-21 07:00 | 106.01 | 88.86
2018-03-21 07:30 | 127.98 | 99.64
2018-03-21 08:00 | 138 | 105.97
2018-03-21 08:30 | 139.14 | 104.18
2018-03-21 09:00 | 148.7 | 99.31
2018-03-21 09:30 | 154.1 | 101.44
2018-03-21 10:00 | 132.6 | 109.49
2018-03-21 10:30 | 100.91 | 96.74
2018-03-21 11:00 | 110.19 | 105.99
2018-03-21 11:30 | 114.22 | 110.78
2018-03-21 12:00 | 107.56 | 103.94
2018-03-21 12:30 | 117.99 | 114.45
2018-03-21 13:00 | 106.99 | 103.44
2018-03-21 13:30 | 108.21 | 104.63
2018-03-21 14:00 | 108.88 | 105.1
2018-03-21 14:30 | 109.07 | 105.76
2018-03-21 15:00 | 119.73 | 119.46
2018-03-21 15:30 | 134.19 | 134.18
2018-03-21 16:00 | 145.15 | 145.12
2018-03-21 16:30 | 156.93 | 156.92
2018-03-21 17:00 | 167.78 | 167.78
2018-03-21 17:30 | 170.56 | 170.55
2018-03-21 18:00 | 171.21 | 171.21
2018-03-21 18:30 | 180.59 | 180.58
2018-03-21 19:00 | 206.12 | 206.08
2018-03-21 19:30 | 188.32 | 188.31
2018-03-21 20:00 | 176.83 | 176.31
2018-03-21 20:30 | 147.56 | 146.72
2018-03-21 21:00 | 123.71 | 122.98
2018-03-21 21:30 | 115.03 | 114.52
2018-03-21 22:00 | 96.35 | 95.88
2018-03-21 22:30 | 88.75 | 88.15
2018-03-21 23:00 | 95.03 | 94.44
2018-03-21 23:30 | 73.22 | 72.73
2018-03-22 | 25.92 | 25.1
2018-03-22 00:30 | 4.44 | 1.15
2018-03-22 01:00 | 14.86 | -13.64
2018-03-22 01:30 | 12.14 | 9.82
2018-03-22 02:00 | 6.5 | 2.45
2018-03-22 02:30 | 13 | -12.29
2018-03-22 03:00 | 35.5 | -35.46
2018-03-22 03:30 | 43.12 | -43.11
2018-03-22 04:00 | 32.36 | -32.35
2018-03-22 04:30 | 13.34 | -13.22
2018-03-22 05:00 | 3.69 | 1.52
2018-03-22 05:30 | 28.38 | 27.83
2018-03-22 06:00 | 81.85 | 81.74
2018-03-22 06:30 | 102.2 | 102.01
2018-03-22 07:00 | 114.83 | 114.09
2018-03-22 07:30 | 136.04 | 132.33
2018-03-22 08:00 | 133.13 | 130.74
2018-03-22 08:30 | 126.92 | 124.75
2018-03-22 09:00 | 125.79 | 122.89
2018-03-22 09:30 | 128.54 | 120.48
2018-03-22 10:00 | 144.27 | 132.47
2018-03-22 10:30 | 164.49 | 153.95
2018-03-22 11:00 | 173.56 | 163.57
2018-03-22 11:30 | 174.83 | 167.07
2018-03-22 12:00 | 161.46 | 158.03
2018-03-22 12:30 | 155.42 | 151.72
2018-03-22 13:00 | 159.21 | 155.48
2018-03-22 13:30 | 157.11 | 153.27
2018-03-22 14:00 | 161.45 | 157.45
2018-03-22 14:30 | 156.22 | 152.78
2018-03-22 15:00 | 123 | 119.9
2018-03-22 15:30 | 127.46 | 124.68
2018-03-22 16:00 | 143.76 | 141.68
2018-03-22 16:30 | 162.85 | 161.31
2018-03-22 17:00 | 167.66 | 166.38
2018-03-22 17:30 | 158.2 | 157.19
2018-03-22 18:00 | 155.15 | 154.23
2018-03-22 18:30 | 170.79 | 169.72
2018-03-22 19:00 | 202.46 | 201.56
2018-03-22 19:30 | 188.18 | 187.51
2018-03-22 20:00 | 172.96 | 171.94
2018-03-22 20:30 | 160.26 | 159.32
2018-03-22 21:00 | 137.48 | 136.7
2018-03-22 21:30 | 118.61 | 117.94
2018-03-22 22:00 | 96.37 | 95.1
2018-03-22 22:30 | 99.73 | 98.59
2018-03-22 23:00 | 106.44 | 105.44
2018-03-22 23:30 | 69.92 | 68.87
2018-03-23 | 27.82 | 25.04
2018-03-23 00:30 | 13.89 | -4.67
2018-03-23 01:00 | 20.48 | -15.47
2018-03-23 01:30 | 13.76 | -13.27
2018-03-23 02:00 | 12.34 | -10.47
2018-03-23 02:30 | 15.54 | -14.21
2018-03-23 03:00 | 23.35 | -22.55
2018-03-23 03:30 | 27.3 | -26.58
2018-03-23 04:00 | 18.99 | -17.73
2018-03-23 04:30 | 11.12 | -8.2
2018-03-23 05:00 | 10.78 | 6.99
2018-03-23 05:30 | 15.87 | 13.81
2018-03-23 06:00 | 32.55 | 31.79
2018-03-23 06:30 | 58.2 | 58.05
2018-03-23 07:00 | 63.1 | 63.1
2018-03-23 07:30 | 84.23 | 83.2
2018-03-23 08:00 | 93.96 | 84.5
2018-03-23 08:30 | 85.09 | 72.73
2018-03-23 09:00 | 94.96 | 82.11
2018-03-23 09:30 | 103.14 | 89.39
2018-03-23 10:00 | 101.23 | 84.89
2018-03-23 10:30 | 109.8 | 93.96
2018-03-23 11:00 | 102.02 | 83.8
2018-03-23 11:30 | 108.88 | 97.36
2018-03-23 12:00 | 105.08 | 96.29
2018-03-23 12:30 | 89.35 | 79.94
2018-03-23 13:00 | 77.98 | 66.94
2018-03-23 13:30 | 54.23 | 35.79
2018-03-23 14:00 | 48.55 | 25.18
2018-03-23 14:30 | 58.7 | 41.6
2018-03-23 15:00 | 70.18 | 56.9
2018-03-23 15:30 | 97.36 | 89.16
2018-03-23 16:00 | 139.55 | 134.41
2018-03-23 16:30 | 147.47 | 143.1
2018-03-23 17:00 | 171.58 | 168.29
2018-03-23 17:30 | 166.62 | 164.11
2018-03-23 18:00 | 164.05 | 162.08
2018-03-23 18:30 | 171.04 | 168.96
2018-03-23 19:00 | 180.51 | 178.67
2018-03-23 19:30 | 162.21 | 160.53
2018-03-23 20:00 | 149.05 | 147.61
2018-03-23 20:30 | 129.13 | 127.98
2018-03-23 21:00 | 100 | 98.65
2018-03-23 21:30 | 79.94 | 74.92
2018-03-23 22:00 | 69.04 | 64.1
2018-03-23 22:30 | 80.82 | 80.71
2018-03-23 23:00 | 106.84 | 106.69
2018-03-23 23:30 | 89.91 | 89.49
2018-03-24 | 55.33 | 54.83
2018-03-24 00:30 | 25.09 | 24.17
2018-03-24 01:00 | 11.19 | 9.42
2018-03-24 01:30 | 6.59 | 3.15
2018-03-24 02:00 | 7.59 | 5.04
2018-03-24 02:30 | 6.15 | 2.23
2018-03-24 03:00 | 5.84 | 0.22
2018-03-24 03:30 | 6.36 | -2.64
2018-03-24 04:00 | 10.26 | -8.44
2018-03-24 04:30 | 16.56 | -15.54
2018-03-24 05:00 | 9.81 | -7.66
2018-03-24 05:30 | 10.9 | -8.86
2018-03-24 06:00 | 5.58 | -0.43
2018-03-24 06:30 | 7.9 | 5.95
2018-03-24 07:00 | 13.91 | 12.9
2018-03-24 07:30 | 28.01 | 27.87
2018-03-24 08:00 | 26.13 | 26.13
2018-03-24 08:30 | 16.5 | 15.64
2018-03-24 09:00 | 54.65 | 54.17
2018-03-24 09:30 | 63.15 | 62.87
2018-03-24 10:00 | 54.48 | 54.28
2018-03-24 10:30 | 58.73 | 58.59
2018-03-24 11:00 | 53.78 | 53.67
2018-03-24 11:30 | 61.66 | 61.59
2018-03-24 12:00 | 59 | 58.93
2018-03-24 12:30 | 55.67 | 55.6
2018-03-24 13:00 | 55.95 | 55.86
2018-03-24 13:30 | 57.42 | 57.32
2018-03-24 14:00 | 55.36 | 55.25
2018-03-24 14:30 | 54.16 | 54.09
2018-03-24 15:00 | 66.5 | 66.41
2018-03-24 15:30 | 81.79 | 81.71
2018-03-24 16:00 | 86.57 | 86.51
2018-03-24 16:30 | 104.36 | 104.26
2018-03-24 17:00 | 110.08 | 109.94
2018-03-24 17:30 | 122.69 | 122.38
2018-03-24 18:00 | 133.38 | 133.04
2018-03-24 18:30 | 140.25 | 140.08
2018-03-24 19:00 | 158.75 | 158.58
2018-03-24 19:30 | 150.1 | 149.75
2018-03-24 20:00 | 145.47 | 144.98
2018-03-24 20:30 | 146.93 | 146.57
2018-03-24 21:00 | 103.39 | 103.38
2018-03-24 21:30 | 98.6 | 98.59
2018-03-24 22:00 | 84.37 | 84.27
2018-03-24 22:30 | 88.23 | 88.04
2018-03-24 23:00 | 106.72 | 106.51
2018-03-24 23:30 | 93.53 | 93.09
2018-03-25 | 55.03 | 54.28
2018-03-25 00:30 | 36.19 | 34.98
2018-03-25 01:00 | 34.67 | 33
2018-03-25 01:30 | 22.29 | 19.66
2018-03-25 02:00 | 20.63 | 17.68
2018-03-25 02:30 | 13.75 | 8.89
2018-03-25 03:00 | 10.11 | 0.69
2018-03-25 03:30 | 17.56 | 13.96
2018-03-25 04:00 | 45.78 | 43.97
2018-03-25 04:30 | 34.02 | 31.54
2018-03-25 05:00 | 26.26 | 23.3
2018-03-25 05:30 | 11.49 | -3.62
2018-03-25 06:00 | 14.52 | -11.08
2018-03-25 06:30 | 9.42 | -0.66
2018-03-25 07:00 | 12.45 | 7.97
2018-03-25 07:30 | 20.28 | 18.74
2018-03-25 08:00 | 32.78 | 32.38
2018-03-25 08:30 | 49.51 | 49.5
2018-03-25 09:00 | 62.82 | 62.79
2018-03-25 09:30 | 79.57 | 79.42
2018-03-25 10:00 | 101.58 | 101.21
2018-03-25 10:30 | 102.65 | 102.23
2018-03-25 11:00 | 97.98 | 97.6
2018-03-25 11:30 | 94.98 | 94.68
2018-03-25 12:00 | 121.51 | 121.43
2018-03-25 12:30 | 106.04 | 105.85
2018-03-25 13:00 | 138.59 | 138.12
2018-03-25 13:30 | 149.76 | 149.75
2018-03-25 14:00 | 146.55 | 146.49
2018-03-25 14:30 | 102.68 | 102.1
2018-03-25 15:00 | 128.12 | 127.08
2018-03-25 15:30 | 120.43 | 119.54
2018-03-25 16:00 | 129.71 | 128.86
2018-03-25 16:30 | 135.12 | 134.38
2018-03-25 17:00 | 145.66 | 145.05
2018-03-25 17:30 | 166.45 | 165.97
2018-03-25 18:00 | 181.83 | 181.37
2018-03-25 18:30 | 193.48 | 192.31
2018-03-25 19:00 | 219.03 | 215.93
2018-03-25 19:30 | 208.09 | 206.61
2018-03-25 20:00 | 215.92 | 215.18
2018-03-25 20:30 | 202.69 | 201.02
2018-03-25 21:00 | 182.36 | 180.87
2018-03-25 21:30 | 186.82 | 184.7
2018-03-25 22:00 | 177.42 | 175.68
2018-03-25 22:30 | 165.06 | 164.61
2018-03-25 23:00 | 158.26 | 157.96
2018-03-25 23:30 | 131.29 | 131.05
2018-03-26 | 84.86 | 84.62
2018-03-26 00:30 | 51.52 | 51.1
2018-03-26 01:00 | 38.96 | 38.31
2018-03-26 01:30 | 41.77 | 41.15
2018-03-26 02:00 | 29.76 | 28.78
2018-03-26 02:30 | 25.95 | 22.75
2018-03-26 03:00 | 47.61 | 45.74
2018-03-26 03:30 | 42.55 | 40.41
2018-03-26 04:00 | 24.83 | 20.96
2018-03-26 04:30 | 13.44 | 2.82
2018-03-26 05:00 | 15.69 | 8.55
2018-03-26 05:30 | 12.7 | 11.82
2018-03-26 06:00 | 16.18 | 8.14
2018-03-26 06:30 | 46.53 | 43.31
2018-03-26 07:00 | 65.36 | 53.25
2018-03-26 07:30 | 109.18 | 65.4
2018-03-26 08:00 | 124.79 | 71.91
2018-03-26 08:30 | 127.75 | 68.93
2018-03-26 09:00 | 134.44 | 67.83
2018-03-26 09:30 | 116.38 | 82.86
2018-03-26 10:00 | 132.34 | 105.35
2018-03-26 10:30 | 151.96 | 128.76
2018-03-26 11:00 | 161.03 | 139.3
2018-03-26 11:30 | 161.88 | 140.9
2018-03-26 12:00 | 161.59 | 140.72
2018-03-26 12:30 | 180.42 | 161.53
2018-03-26 13:00 | 206.09 | 194.84
2018-03-26 13:30 | 231.91 | 222.06
2018-03-26 14:00 | 244.36 | 234.87
2018-03-26 14:30 | 250.44 | 240.76
2018-03-26 15:00 | 255.42 | 245.82
2018-03-26 15:30 | 257.48 | 248.56
2018-03-26 16:00 | 270.08 | 261.4
2018-03-26 16:30 | 271.92 | 263.03
2018-03-26 17:00 | 275.39 | 267.23
2018-03-26 17:30 | 275.5 | 268.47
2018-03-26 18:00 | 274.09 | 271.32
2018-03-26 18:30 | 280.31 | 277.47
2018-03-26 19:00 | 278.64 | 275.92
2018-03-26 19:30 | 264.92 | 263.72
2018-03-26 20:00 | 245.85 | 245.67
2018-03-26 20:30 | 236.54 | 236.46
2018-03-26 21:00 | 199.57 | 199.48
2018-03-26 21:30 | 164.18 | 163.9
2018-03-26 22:00 | 152.69 | 152.41
2018-03-26 22:30 | 148.85 | 148.65
2018-03-26 23:00 | 145.62 | 145.49
2018-03-26 23:30 | 114.59 | 114.2
2018-03-27 | 58.72 | 58.05
2018-03-27 00:30 | 25.5 | 24.34
2018-03-27 01:00 | 9.85 | 5.28
2018-03-27 01:30 | 8.5 | -0.88
2018-03-27 02:00 | 10.71 | 5.94
2018-03-27 02:30 | 9.61 | 2.88
2018-03-27 03:00 | 9.66 | -3.35
2018-03-27 03:30 | 11.16 | -7.01
2018-03-27 04:00 | 9.95 | -3.28
2018-03-27 04:30 | 9.48 | 1.66
2018-03-27 05:00 | 11.54 | 7.41
2018-03-27 05:30 | 14.94 | 14.14
2018-03-27 06:00 | 44.16 | 44.15
2018-03-27 06:30 | 90.86 | 90.1
2018-03-27 07:00 | 129.23 | 127.13
2018-03-27 07:30 | 152.03 | 152.03
2018-03-27 08:00 | 163.98 | 163.47
2018-03-27 08:30 | 184.54 | 184.15
2018-03-27 09:00 | 196.51 | 196.02
2018-03-27 09:30 | 201.69 | 200.95
2018-03-27 10:00 | 186.73 | 183.42
2018-03-27 10:30 | 130.28 | 125.37
2018-03-27 11:00 | 126.48 | 121.17
2018-03-27 11:30 | 130.93 | 126.07
2018-03-27 12:00 | 135.21 | 131.25
2018-03-27 12:30 | 133.17 | 128.97
2018-03-27 13:00 | 125.81 | 120.58
2018-03-27 13:30 | 120.13 | 108.92
2018-03-27 14:00 | 109.63 | 95.97
2018-03-27 14:30 | 117.43 | 109.57
2018-03-27 15:00 | 120.4 | 118.71
2018-03-27 15:30 | 124.68 | 123.54
2018-03-27 16:00 | 164.34 | 163.65
2018-03-27 16:30 | 220.57 | 220.31
2018-03-27 17:00 | 231.72 | 231.47
2018-03-27 17:30 | 229.4 | 229.07
2018-03-27 18:00 | 214.34 | 214.16
2018-03-27 18:30 | 235.8 | 235.29
2018-03-27 19:00 | 238.48 | 237.9
2018-03-27 19:30 | 220.37 | 219.27
2018-03-27 20:00 | 198.38 | 198.38
2018-03-27 20:30 | 182.66 | 182.57
2018-03-27 21:00 | 168.94 | 168.93
2018-03-27 21:30 | 131.9 | 131.77
2018-03-27 22:00 | 102.48 | 101.88
2018-03-27 22:30 | 144.33 | 143.76
2018-03-27 23:00 | 159.28 | 158.79
2018-03-27 23:30 | 139.15 | 138.32
2018-03-28 | 102.57 | 99.59
2018-03-28 00:30 | 74.17 | 70.35
2018-03-28 01:00 | 52.23 | 47.2
2018-03-28 01:30 | 42.79 | 36.7
2018-03-28 02:00 | 44.91 | 39.58
2018-03-28 02:30 | 60.42 | 56.43
2018-03-28 03:00 | 63.33 | 59.71
2018-03-28 03:30 | 56.86 | 52.64
2018-03-28 04:00 | 61.38 | 57.15
2018-03-28 04:30 | 46.82 | 40.76
2018-03-28 05:00 | 19.96 | -13.09
2018-03-28 05:30 | 60.47 | 58.46
2018-03-28 06:00 | 83.67 | 83.49
2018-03-28 06:30 | 94.98 | 94.94
2018-03-28 07:00 | 128.63 | 128.34
2018-03-28 07:30 | 149.13 | 145.63
2018-03-28 08:00 | 154.1 | 142.42
2018-03-28 08:30 | 148.77 | 139.58
2018-03-28 09:00 | 144.8 | 131.65
2018-03-28 09:30 | 147.82 | 131.21
2018-03-28 10:00 | 151.72 | 134.8
2018-03-28 10:30 | 154.31 | 132.23
2018-03-28 11:00 | 154.19 | 124.43
2018-03-28 11:30 | 151.44 | 120.83
2018-03-28 12:00 | 151.58 | 123
2018-03-28 12:30 | 150.96 | 122.7
2018-03-28 13:00 | 151.01 | 123.41
2018-03-28 13:30 | 133.9 | 128.96
2018-03-28 14:00 | 148.87 | 144.14
2018-03-28 14:30 | 152.11 | 147.27
2018-03-28 15:00 | 147.78 | 143.2
2018-03-28 15:30 | 150.73 | 146.56
2018-03-28 16:00 | 173.48 | 170.06
2018-03-28 16:30 | 176.46 | 173.4
2018-03-28 17:00 | 186.3 | 183.78
2018-03-28 17:30 | 182.9 | 180.92
2018-03-28 18:00 | 172.46 | 172.29
2018-03-28 18:30 | 185.46 | 185.43
2018-03-28 19:00 | 204.17 | 204.16
2018-03-28 19:30 | 195.04 | 195.01
2018-03-28 20:00 | 197.65 | 189.08
2018-03-28 20:30 | 189.67 | 176.59
2018-03-28 21:00 | 156.76 | 148.72
2018-03-28 21:30 | 131.76 | 124.88
2018-03-28 22:00 | 117.92 | 105.41
2018-03-28 22:30 | 107.7 | 100.46
2018-03-28 23:00 | 122.31 | 121.09
2018-03-28 23:30 | 94.6 | 94.02
2018-03-29 | 37.91 | 36.87
2018-03-29 00:30 | 11.63 | 4.13
2018-03-29 01:00 | 12.68 | -6.36
2018-03-29 01:30 | 19.16 | -15.28
2018-03-29 02:00 | 12.92 | -11.82
2018-03-29 02:30 | 15.51 | -12.68
2018-03-29 03:00 | 23.86 | -22.53
2018-03-29 03:30 | 26.18 | -24.88
2018-03-29 04:00 | 36.89 | -36.15
2018-03-29 04:30 | 25.56 | -24.06
2018-03-29 05:00 | 21.05 | -18.96
2018-03-29 05:30 | 5.6 | -1.12
2018-03-29 06:00 | 17.28 | 12.85
2018-03-29 06:30 | 56.68 | 54.55
2018-03-29 07:00 | 87.93 | 85.5
2018-03-29 07:30 | 92.61 | 92.54
2018-03-29 08:00 | 108.74 | 108.06
2018-03-29 08:30 | 98.23 | 97.69
2018-03-29 09:00 | 104.39 | 103.91
2018-03-29 09:30 | 92.43 | 91.41
2018-03-29 10:00 | 89.85 | 88.8
2018-03-29 10:30 | 74.92 | 73.73
2018-03-29 11:00 | 91.81 | 90.94
2018-03-29 11:30 | 109.24 | 108.43
2018-03-29 12:00 | 105.4 | 104.65
2018-03-29 12:30 | 114.17 | 113.39
2018-03-29 13:00 | 111.84 | 110.95
2018-03-29 13:30 | 115.52 | 114.57
2018-03-29 14:00 | 113.35 | 112.65
2018-03-29 14:30 | 114.43 | 113.86
2018-03-29 15:00 | 111.32 | 110.94
2018-03-29 15:30 | 109.72 | 109.42
2018-03-29 16:00 | 114.49 | 114.11
2018-03-29 16:30 | 125.71 | 125.43
2018-03-29 17:00 | 134.41 | 134.16
2018-03-29 17:30 | 158.93 | 158.62
2018-03-29 18:00 | 153.17 | 152.82
2018-03-29 18:30 | 168.55 | 168.16
2018-03-29 19:00 | 170.63 | 170.17
2018-03-29 19:30 | 149.58 | 149.17
2018-03-29 20:00 | 157.53 | 157.34
2018-03-29 20:30 | 179.32 | 179.19
2018-03-29 21:00 | 149.68 | 149.65
2018-03-29 21:30 | 119.32 | 119.09
2018-03-29 22:00 | 117.84 | 117.66
2018-03-29 22:30 | 130.76 | 130.67
2018-03-29 23:00 | 150.44 | 150.39
2018-03-29 23:30 | 120.86 | 120.83
2018-03-30 | 66.85 | 66.27
2018-03-30 00:30 | 24.41 | 23.8
2018-03-30 01:00 | 7.47 | 6.34
2018-03-30 01:30 | 7.14 | -6.82
2018-03-30 02:00 | 15.69 | -15.64
2018-03-30 02:30 | 28.41 | -28.23
2018-03-30 03:00 | 29.2 | -28.91
2018-03-30 03:30 | 32.12 | -31.77
2018-03-30 04:00 | 29.46 | -29.01
2018-03-30 04:30 | 28.4 | -27.94
2018-03-30 05:00 | 26.45 | -26.05
2018-03-30 05:30 | 23.04 | -22.86
2018-03-30 06:00 | 15.62 | -15.51
2018-03-30 06:30 | 12.13 | -12.07
2018-03-30 07:00 | 9.58 | -9.58
2018-03-30 07:30 | 9.44 | -9.43
2018-03-30 08:00 | 15.12 | -14.62
2018-03-30 08:30 | 9.14 | -7.98
2018-03-30 09:00 | 18.24 | 14.19
2018-03-30 09:30 | 22.01 | 18.51
2018-03-30 10:00 | 15.15 | 15.14
2018-03-30 10:30 | 20.61 | 18.78
2018-03-30 11:00 | 10.38 | -1.46
2018-03-30 11:30 | 17.48 | -14.1
2018-03-30 12:00 | 10.98 | -8.71
2018-03-30 12:30 | 6.28 | 4.76
2018-03-30 13:00 | 10.56 | 10.03
2018-03-30 13:30 | 14.78 | 14.74
2018-03-30 14:00 | 17.24 | 17.24
2018-03-30 14:30 | 28.12 | 28.09
2018-03-30 15:00 | 44.03 | 44.03
2018-03-30 15:30 | 48 | 47.98
2018-03-30 16:00 | 39.86 | 39.86
2018-03-30 16:30 | 44.72 | 44.7
2018-03-30 17:00 | 66.73 | 66.72
2018-03-30 17:30 | 73.76 | 73.74
2018-03-30 18:00 | 86.45 | 86.39
2018-03-30 18:30 | 101.34 | 101.3
2018-03-30 19:00 | 111.22 | 111.2
2018-03-30 19:30 | 107.44 | 107.41
2018-03-30 20:00 | 88.97 | 88.92
2018-03-30 20:30 | 100.66 | 100.63
2018-03-30 21:00 | 97.25 | 95.64
2018-03-30 21:30 | 84.34 | 81.87
2018-03-30 22:00 | 69.02 | 66.68
2018-03-30 22:30 | 81.39 | 79.79
2018-03-30 23:00 | 100.81 | 99.7
2018-03-30 23:30 | 76.29 | 75.4
2018-03-31 | 27.97 | 25.62
2018-03-31 00:30 | 13.37 | -5.58
2018-03-31 01:00 | 19.56 | -15
2018-03-31 01:30 | 20.4 | -16.31
2018-03-31 02:00 | 27.88 | -25.05
2018-03-31 02:30 | 26.71 | -26.53
2018-03-31 03:00 | 30.8 | -29.72
2018-03-31 03:30 | 39.78 | -39.02
2018-03-31 04:00 | 38.68 | -37.91
2018-03-31 04:30 | 32.31 | -31.23
2018-03-31 05:00 | 26.78 | -25.26
2018-03-31 05:30 | 18.05 | -15
2018-03-31 06:00 | 22.13 | -20.41
2018-03-31 06:30 | 15.82 | -13.45
2018-03-31 07:00 | 22.87 | -21.83
2018-03-31 07:30 | 10.57 | -9.08
2018-03-31 08:00 | 8.13 | -8.1
2018-03-31 08:30 | 8.06 | 5.66
2018-03-31 09:00 | 37.71 | 24.79
2018-03-31 09:30 | 45.83 | 34.08
2018-03-31 10:00 | 53.33 | 42.95
2018-03-31 10:30 | 60.82 | 51.08
2018-03-31 11:00 | 57.16 | 45.87
2018-03-31 11:30 | 58.55 | 47.43
2018-03-31 12:00 | 53.81 | 40.87
2018-03-31 12:30 | 53.7 | 40.65
2018-03-31 13:00 | 54.84 | 41.26
2018-03-31 13:30 | 64.94 | 54.19
2018-03-31 14:00 | 80.9 | 72.54
2018-03-31 14:30 | 96.93 | 90.34
2018-03-31 15:00 | 102.65 | 96.48
2018-03-31 15:30 | 121.21 | 89.66
2018-03-31 16:00 | 129.56 | 98.04
2018-03-31 16:30 | 123.71 | 90.17
2018-03-31 17:00 | 129.17 | 101.94
2018-03-31 17:30 | 120.26 | 93.66
2018-03-31 18:00 | 128.29 | 104.94
2018-03-31 18:30 | 130.64 | 106.35
2018-03-31 19:00 | 126.67 | 101.93
2018-03-31 19:30 | 114.59 | 90.81
2018-03-31 20:00 | 100.78 | 86.98
2018-03-31 20:30 | 108.68 | 102.29
2018-03-31 21:00 | 87.63 | 86.4
2018-03-31 21:30 | 83.6 | 81.54
2018-03-31 22:00 | 69.04 | 66.62
2018-03-31 22:30 | 75.08 | 73.32
2018-03-31 23:00 | 73.72 | 72.2
2018-03-31 23:30 | 50.49 | 48.92
2018-04-01 | 21.48 | 18.59
2018-04-01 00:30 | 11.04 | -2.92
2018-04-01 01:00 | 10.39 | 1.31
2018-04-01 01:30 | 14.14 | -9.27
2018-04-01 02:00 | 18.34 | -16.46
2018-04-01 02:30 | 19.41 | -16.99
2018-04-01 03:00 | 20.74 | -18.48
2018-04-01 03:30 | 32.74 | -31.59
2018-04-01 04:00 | 30.58 | -29.49
2018-04-01 04:30 | 31.07 | -29.91
2018-04-01 05:00 | 25.86 | -24.21
2018-04-01 05:30 | 15.68 | -11.84
2018-04-01 06:00 | 20.34 | -18.15
2018-04-01 06:30 | 10.66 | -5.08
2018-04-01 07:00 | 11.05 | 5.27
2018-04-01 07:30 | 13.18 | 10.78
2018-04-01 08:00 | 11.34 | 9.98
2018-04-01 08:30 | 20.56 | 20.56
2018-04-01 09:00 | 31.03 | 30.81
2018-04-01 09:30 | 63.05 | 60.29
2018-04-01 10:00 | 65.53 | 59.77
2018-04-01 10:30 | 67.59 | 61.54
2018-04-01 11:00 | 66.38 | 59.18
2018-04-01 11:30 | 62.89 | 54.9
2018-04-01 12:00 | 46.78 | 34.47
2018-04-01 12:30 | 49.06 | 37.53
2018-04-01 13:00 | 63.7 | 55.08
2018-04-01 13:30 | 54.58 | 43.46
2018-04-01 14:00 | 63.4 | 53.94
2018-04-01 14:30 | 85.07 | 56.12
2018-04-01 15:00 | 84.84 | 64.88
2018-04-01 15:30 | 84.32 | 74.48
2018-04-01 16:00 | 99.73 | 91.43
2018-04-01 16:30 | 104.96 | 97.46
2018-04-01 17:00 | 101.9 | 94.28
2018-04-01 17:30 | 98.06 | 90.74
2018-04-01 18:00 | 99.92 | 92.91
2018-04-01 18:30 | 112.97 | 106.12
2018-04-01 19:00 | 119.59 | 113.29
2018-04-01 19:30 | 107.64 | 101.5
2018-04-01 20:00 | 111.96 | 107.7
2018-04-01 20:30 | 120.85 | 120.22
2018-04-01 21:00 | 115.33 | 114.24
2018-04-01 21:30 | 105.53 | 104.22
2018-04-01 22:00 | 101.19 | 99.85
2018-04-01 22:30 | 124.96 | 123.69
2018-04-01 23:00 | 139.59 | 137.67
2018-04-01 23:30 | 103.81 | 101.03
2018-04-02 | 54.05 | 48.76
2018-04-02 00:30 | 30.22 | 22.39
2018-04-02 01:00 | 22.3 | 13.52
2018-04-02 01:30 | 16.29 | 2.19
2018-04-02 02:00 | 15.39 | -6.35
2018-04-02 02:30 | 17.25 | -11.84
2018-04-02 03:00 | 15.69 | -9.71
2018-04-02 03:30 | 21.12 | -18.23
2018-04-02 04:00 | 22.78 | -20.61
2018-04-02 04:30 | 23.41 | -21.11
2018-04-02 05:00 | 16.73 | -12.31
2018-04-02 05:30 | 14.23 | -2.19
2018-04-02 06:00 | 14.8 | 1.09
2018-04-02 06:30 | 15.62 | 4.56
2018-04-02 07:00 | 27.04 | 20.43
2018-04-02 07:30 | 35.7 | 28.55
2018-04-02 08:00 | 32.56 | 27.98
2018-04-02 08:30 | 38.98 | 38.93
2018-04-02 09:00 | 71.41 | 57.79
2018-04-02 09:30 | 88.04 | 75.6
2018-04-02 10:00 | 95.46 | 82.93
2018-04-02 10:30 | 88.23 | 73.65
2018-04-02 11:00 | 85.81 | 71.49
2018-04-02 11:30 | 82.21 | 69.9
2018-04-02 12:00 | 82.92 | 70.67
2018-04-02 12:30 | 84.3 | 73.21
2018-04-02 13:00 | 91.86 | 82.37
2018-04-02 13:30 | 91.27 | 81.53
2018-04-02 14:00 | 83.05 | 71.7
2018-04-02 14:30 | 85.49 | 73.9
2018-04-02 15:00 | 86.92 | 74.96
2018-04-02 15:30 | 111.67 | 103.35
2018-04-02 16:00 | 130.45 | 123.26
2018-04-02 16:30 | 143.7 | 137.84
2018-04-02 17:00 | 146.39 | 141.24
2018-04-02 17:30 | 129.68 | 124.34
2018-04-02 18:00 | 117.87 | 111.98
2018-04-02 18:30 | 141.58 | 136.24
2018-04-02 19:00 | 153.8 | 149.37
2018-04-02 19:30 | 138.66 | 135.52
2018-04-02 20:00 | 121.19 | 120.97
2018-04-02 20:30 | 126.05 | 125.12
2018-04-02 21:00 | 112.32 | 111
2018-04-02 21:30 | 99.35 | 97.75
2018-04-02 22:00 | 87.36 | 85.55
2018-04-02 22:30 | 78.83 | 76.52
2018-04-02 23:00 | 87.13 | 84.14
2018-04-02 23:30 | 69.2 | 65.03
2018-04-03 | 46.36 | 40.52
2018-04-03 00:30 | 19.6 | 5.36
2018-04-03 01:00 | 17.8 | -9.34
2018-04-03 01:30 | 22.34 | -17.48
2018-04-03 02:00 | 30.39 | -28.15
2018-04-03 02:30 | 30.33 | -28.39
2018-04-03 03:00 | 29.28 | -27.18
2018-04-03 03:30 | 24.25 | -20.29
2018-04-03 04:00 | 23.37 | -12.12
2018-04-03 04:30 | 25.77 | -14.61
2018-04-03 05:00 | 22.74 | -1.44
2018-04-03 05:30 | 27.08 | 12.79
2018-04-03 06:00 | 44.62 | 37.32
2018-04-03 06:30 | 74.6 | 71.23
2018-04-03 07:00 | 88.35 | 88.06
2018-04-03 07:30 | 83.6 | 83.48
2018-04-03 08:00 | 69.83 | 69.72
2018-04-03 08:30 | 78.45 | 78.45
2018-04-03 09:00 | 83.65 | 83.55
2018-04-03 09:30 | 75.03 | 73.76
2018-04-03 10:00 | 65.16 | 63.8
2018-04-03 10:30 | 50.92 | 48.95
2018-04-03 11:00 | 47.63 | 45.61
2018-04-03 11:30 | 39.84 | 37.18
2018-04-03 12:00 | 46.16 | 44.19
2018-04-03 12:30 | 52.64 | 51.23
2018-04-03 13:00 | 61.53 | 60.52
2018-04-03 13:30 | 70.88 | 69.94
2018-04-03 14:00 | 77.37 | 76.63
2018-04-03 14:30 | 73.52 | 72.71
2018-04-03 15:00 | 74.87 | 74.03
2018-04-03 15:30 | 85.29 | 84.78
2018-04-03 16:00 | 91.32 | 90.87
2018-04-03 16:30 | 92.33 | 91.68
2018-04-03 17:00 | 109.46 | 108.94
2018-04-03 17:30 | 114.5 | 113.69
2018-04-03 18:00 | 112.35 | 110.51
2018-04-03 18:30 | 127.4 | 124.98
2018-04-03 19:00 | 137.92 | 135.88
2018-04-03 19:30 | 132.75 | 129.76
2018-04-03 20:00 | 124.38 | 124.38
2018-04-03 20:30 | 124.89 | 124.82
2018-04-03 21:00 | 95.27 | 95.22
2018-04-03 21:30 | 87.35 | 87.15
2018-04-03 22:00 | 81.97 | 81.49
2018-04-03 22:30 | 91.34 | 91.3
2018-04-03 23:00 | 96.41 | 96.32
2018-04-03 23:30 | 74.08 | 73.82
2018-04-04 | 30.58 | 29.95
2018-04-04 00:30 | 10.51 | 8.96
2018-04-04 01:00 | 6.83 | 3.8
2018-04-04 01:30 | 7.1 | -4.96
2018-04-04 02:00 | 11.08 | -10.1
2018-04-04 02:30 | 14.77 | -13.87
2018-04-04 03:00 | 16.74 | -16.06
2018-04-04 03:30 | 20.17 | -19.51
2018-04-04 04:00 | 30 | -29.64
2018-04-04 04:30 | 26.19 | -25.76
2018-04-04 05:00 | 8.37 | -5.56
2018-04-04 05:30 | 21.11 | 20.07
2018-04-04 06:00 | 5.79 | -4.32
2018-04-04 06:30 | 78.6 | 78.44
2018-04-04 07:00 | 90.73 | 90.39
2018-04-04 07:30 | 105.39 | 104.72
2018-04-04 08:00 | 107.92 | 107.61
2018-04-04 08:30 | 115.91 | 115.82
2018-04-04 09:00 | 120.02 | 120.01
2018-04-04 09:30 | 114.62 | 114.61
2018-04-04 10:00 | 106.63 | 106.57
2018-04-04 10:30 | 96.4 | 96.34
2018-04-04 11:00 | 111.91 | 111.85
2018-04-04 11:30 | 122.27 | 122.21
2018-04-04 12:00 | 121.71 | 121.56
2018-04-04 12:30 | 110.41 | 110.22
2018-04-04 13:00 | 101.27 | 101.04
2018-04-04 13:30 | 104.87 | 104.67
2018-04-04 14:00 | 114.13 | 114.07
2018-04-04 14:30 | 113.85 | 113.82
2018-04-04 15:00 | 113.19 | 113.11
2018-04-04 15:30 | 126.88 | 126.85
2018-04-04 16:00 | 131.25 | 131.24
2018-04-04 16:30 | 134.42 | 134.41
2018-04-04 17:00 | 113.08 | 113.06
2018-04-04 17:30 | 52.58 | 52.13
2018-04-04 18:00 | 59.59 | 58.04
2018-04-04 18:30 | 89.54 | 87.06
2018-04-04 19:00 | 91.34 | 88.81
2018-04-04 19:30 | 77.28 | 74.9
2018-04-04 20:00 | 71.55 | 69.4
2018-04-04 20:30 | 58.02 | 57.87
2018-04-04 21:00 | 35.47 | 35.47
2018-04-04 21:30 | 32.39 | 32.29
2018-04-04 22:00 | 34.56 | 34.56
2018-04-04 22:30 | 33.59 | 33.53
2018-04-04 23:00 | 35.86 | 35.82
2018-04-04 23:30 | 13.6 | 13.4
2018-04-05 | 14.79 | -14.69
2018-04-05 00:30 | 16.36 | -16.18
2018-04-05 01:00 | 14.18 | -13.82
2018-04-05 01:30 | 29.3 | -29.14
2018-04-05 02:00 | 19.69 | -19.33
2018-04-05 02:30 | 32.37 | -32.2
2018-04-05 03:00 | 37.99 | -37.91
2018-04-05 03:30 | 35.05 | -34.94
2018-04-05 04:00 | 39.28 | -39.14
2018-04-05 04:30 | 32.62 | -32.39
2018-04-05 05:00 | 24.6 | -24.2
2018-04-05 05:30 | 18.77 | -18.32
2018-04-05 06:00 | 16.23 | 15.43
2018-04-05 06:30 | 73.65 | 73.53
2018-04-05 07:00 | 83.39 | 83.39
2018-04-05 07:30 | 101.61 | 101.49
2018-04-05 08:00 | 98.7 | 98.36
2018-04-05 08:30 | 105.16 | 104.81
2018-04-05 09:00 | 108.16 | 107.76
2018-04-05 09:30 | 104.65 | 103.96
2018-04-05 10:00 | 120.49 | 115.67
2018-04-05 10:30 | 117.22 | 112.04
2018-04-05 11:00 | 110.52 | 104.51
2018-04-05 11:30 | 125.21 | 114.39
2018-04-05 12:00 | 123.64 | 103.68
2018-04-05 12:30 | 120.64 | 100.19
2018-04-05 13:00 | 129.17 | 110.22
2018-04-05 13:30 | 134.42 | 117.55
2018-04-05 14:00 | 121.51 | 103.61
2018-04-05 14:30 | 122.84 | 105.31
2018-04-05 15:00 | 127.9 | 111.04
2018-04-05 15:30 | 127.62 | 110.87
2018-04-05 16:00 | 131.28 | 115.73
2018-04-05 16:30 | 134.84 | 120.62
2018-04-05 17:00 | 138.12 | 124.93
2018-04-05 17:30 | 149.01 | 138.01
2018-04-05 18:00 | 140.9 | 135.86
2018-04-05 18:30 | 142.63 | 137.63
2018-04-05 19:00 | 138.18 | 133.33
2018-04-05 19:30 | 116.36 | 111.15
2018-04-05 20:00 | 91.88 | 85.87
2018-04-05 20:30 | 81.94 | 75.63
2018-04-05 21:00 | 51.55 | 50
2018-04-05 21:30 | 40.14 | 39.79
2018-04-05 22:00 | 44.64 | 43.65
2018-04-05 22:30 | 32.67 | 31.68
2018-04-05 23:00 | 43.69 | 43.57
2018-04-05 23:30 | 6 | 4.74
2018-04-06 | 28.79 | -28.61
2018-04-06 00:30 | 40.64 | -40.53
2018-04-06 01:00 | 26.05 | -25.71
2018-04-06 01:30 | 32.49 | -32.22
2018-04-06 02:00 | 41.95 | -41.8
2018-04-06 02:30 | 41.12 | -40.97
2018-04-06 03:00 | 45.4 | -45.29
2018-04-06 03:30 | 40.29 | -40.11
2018-04-06 04:00 | 40.26 | -40.04
2018-04-06 04:30 | 40.45 | -40.23
2018-04-06 05:00 | 29.49 | -29.03
2018-04-06 05:30 | 16.71 | -15.72
2018-04-06 06:00 | 28.17 | 27.3
2018-04-06 06:30 | 67.64 | 67.4
2018-04-06 07:00 | 81.02 | 80.93
2018-04-06 07:30 | 88.45 | 88.45
2018-04-06 08:00 | 97.21 | 97.14
2018-04-06 08:30 | 102.53 | 102.29
2018-04-06 09:00 | 94.11 | 94.05
2018-04-06 09:30 | 98.86 | 98.85
2018-04-06 10:00 | 100.54 | 98.95
2018-04-06 10:30 | 106.12 | 102.46
2018-04-06 11:00 | 104.47 | 100.71
2018-04-06 11:30 | 98.24 | 94.27
2018-04-06 12:00 | 89.21 | 84.99
2018-04-06 12:30 | 85.44 | 85.37
2018-04-06 13:00 | 84.4 | 84.39
2018-04-06 13:30 | 84.01 | 83.98
2018-04-06 14:00 | 86.15 | 86.13
2018-04-06 14:30 | 95.72 | 95.69
2018-04-06 15:00 | 92.24 | 92.21
2018-04-06 15:30 | 62.29 | 62.29
2018-04-06 16:00 | 56.25 | 55.02
2018-04-06 16:30 | 62.75 | 59.52
2018-04-06 17:00 | 78.63 | 76.56
2018-04-06 17:30 | 60.75 | 56.73
2018-04-06 18:00 | 62.59 | 57.88
2018-04-06 18:30 | 84.54 | 81.3
2018-04-06 19:00 | 74.95 | 70.67
2018-04-06 19:30 | 49.57 | 49.55
2018-04-06 20:00 | 50.23 | 49.97
2018-04-06 20:30 | 50.01 | 49.61
2018-04-06 21:00 | 38.26 | 37.39
2018-04-06 21:30 | 35.59 | 34.22
2018-04-06 22:00 | 23.9 | 21.67
2018-04-06 22:30 | 31.34 | 29.57
2018-04-06 23:00 | 47.36 | 47.26
2018-04-06 23:30 | 14.92 | 14.05
2018-04-07 | 8.17 | -7.36
2018-04-07 00:30 | 17.48 | -17.11
2018-04-07 01:00 | 23.33 | -23.18
2018-04-07 01:30 | 36.71 | -36.65
2018-04-07 02:00 | 37.49 | -37.45
2018-04-07 02:30 | 41.26 | -41.21
2018-04-07 03:00 | 49.58 | -49.56
2018-04-07 03:30 | 51.31 | -51.29
2018-04-07 04:00 | 42.53 | -42.48
2018-04-07 04:30 | 36.53 | -36.42
2018-04-07 05:00 | 31.06 | -30.83
2018-04-07 05:30 | 29.27 | -28.96
2018-04-07 06:00 | 21.52 | -21.07
2018-04-07 06:30 | 15.46 | -14.86
2018-04-07 07:00 | 7.62 | -6.56
2018-04-07 07:30 | 7.81 | -7.63
2018-04-07 08:00 | 1.7 | 0.81
2018-04-07 08:30 | 7.93 | 5.47
2018-04-07 09:00 | 15.84 | 13.85
2018-04-07 09:30 | 45.89 | 3.92
2018-04-07 10:00 | 45.97 | 3.88
2018-04-07 10:30 | 37.33 | -7.91
2018-04-07 11:00 | 42.05 | -18.1
2018-04-07 11:30 | 45.14 | -22.71
2018-04-07 12:00 | 42.59 | -16.31
2018-04-07 12:30 | 44.33 | -20.75
2018-04-07 13:00 | 39.52 | -1.4
2018-04-07 13:30 | 39.26 | -3.04
2018-04-07 14:00 | 40.9 | -11.41
2018-04-07 14:30 | 40.61 | -10.87
2018-04-07 15:00 | 40.8 | -11.46
2018-04-07 15:30 | 40.18 | -9.82
2018-04-07 16:00 | 38.85 | -1.39
2018-04-07 16:30 | 39.51 | -6.68
2018-04-07 17:00 | 39.94 | -6.68
2018-04-07 17:30 | 45.61 | 28.08
2018-04-07 18:00 | 44.6 | 23.32
2018-04-07 18:30 | 29.08 | -4.63
2018-04-07 19:00 | 23.48 | 3.64
2018-04-07 19:30 | 28.22 | 1.27
2018-04-07 20:00 | 42.26 | 19.7
2018-04-07 20:30 | 54.68 | 38.33
2018-04-07 21:00 | 26.58 | 18.04
2018-04-07 21:30 | 8.73 | 5.85
2018-04-07 22:00 | 5.47 | 3.12
2018-04-07 22:30 | 32.83 | 32.81
2018-04-07 23:00 | 41.96 | 41.95
2018-04-07 23:30 | 16.69 | 16.33
2018-04-08 | 8.23 | -7.05
2018-04-08 00:30 | 8.96 | -7.39
2018-04-08 01:00 | 9.72 | -8.11
2018-04-08 01:30 | 40.22 | -40.11
2018-04-08 02:00 | 28.72 | -28.41
2018-04-08 02:30 | 33.49 | -33.23
2018-04-08 03:00 | 31.22 | -30.87
2018-04-08 03:30 | 22.69 | -22.02
2018-04-08 04:00 | 22.48 | -21.8
2018-04-08 04:30 | 15.73 | -14.42
2018-04-08 05:00 | 17.51 | -16.33
2018-04-08 05:30 | 8.47 | -4.61
2018-04-08 06:00 | 13.11 | 11.02
2018-04-08 06:30 | 37.59 | 36.82
2018-04-08 07:00 | 42.14 | 41.41
2018-04-08 07:30 | 80.69 | 80.28
2018-04-08 08:00 | 91.41 | 91.13
2018-04-08 08:30 | 95.39 | 95.28
2018-04-08 09:00 | 73.17 | 73.16
2018-04-08 09:30 | 8.05 | 5.89
2018-04-08 10:00 | 15.2 | 12.55
2018-04-08 10:30 | 77.49 | 76.97
2018-04-08 11:00 | 57.88 | 57
2018-04-08 11:30 | 38.34 | 36.38
2018-04-08 12:00 | 69 | 65.33
2018-04-08 12:30 | 60.26 | 53
2018-04-08 13:00 | 34.22 | 13.02
2018-04-08 13:30 | 37.36 | 20.25
2018-04-08 14:00 | 41.17 | 26.64
2018-04-08 14:30 | 41.03 | 25.65
2018-04-08 15:00 | 64.54 | 30.1
2018-04-08 15:30 | 73.98 | 36.51
2018-04-08 16:00 | 74.07 | 36.88
2018-04-08 16:30 | 82.19 | 52.84
2018-04-08 17:00 | 93.08 | 69.74
2018-04-08 17:30 | 100.06 | 78.97
2018-04-08 18:00 | 116.49 | 98.67
2018-04-08 18:30 | 116.25 | 113.2
2018-04-08 19:00 | 112.23 | 109.86
2018-04-08 19:30 | 91.72 | 91.72
2018-04-08 20:00 | 90.97 | 90.95
2018-04-08 20:30 | 82.34 | 82.34
2018-04-08 21:00 | 53.85 | 53.81
2018-04-08 21:30 | 31.94 | 31.84
2018-04-08 22:00 | 29.4 | 29.39
2018-04-08 22:30 | 74.09 | 74
2018-04-08 23:00 | 83.3 | 83.06
2018-04-08 23:30 | 45.77 | 45.36
2018-04-09 | 19.41 | 14.45
2018-04-09 00:30 | 16.87 | 11.53
2018-04-09 01:00 | 11.11 | 0.97
2018-04-09 01:30 | 12.75 | 5.74
2018-04-09 02:00 | 15.12 | 9.54
2018-04-09 02:30 | 13.86 | 7.38
2018-04-09 03:00 | 11.4 | -1.72
2018-04-09 03:30 | 12.15 | 3.81
2018-04-09 04:00 | 13.89 | -8.41
2018-04-09 04:30 | 11.73 | -2.73
2018-04-09 05:00 | 13.46 | 6.18
2018-04-09 05:30 | 26.2 | 22.87
2018-04-09 06:00 | 40.89 | 39.01
2018-04-09 06:30 | 53.41 | 53.24
2018-04-09 07:00 | 64.93 | 63.72
2018-04-09 07:30 | 92.94 | 81.67
2018-04-09 08:00 | 100.84 | 85.63
2018-04-09 08:30 | 105.97 | 90.64
2018-04-09 09:00 | 107.43 | 91.9
2018-04-09 09:30 | 108.32 | 94.58
2018-04-09 10:00 | 102.78 | 92.8
2018-04-09 10:30 | 102.05 | 91.29
2018-04-09 11:00 | 101.49 | 90.01
2018-04-09 11:30 | 99.56 | 87.66
2018-04-09 12:00 | 102.51 | 90.8
2018-04-09 12:30 | 101.33 | 89.33
2018-04-09 13:00 | 99.13 | 86.39
2018-04-09 13:30 | 105.18 | 93.16
2018-04-09 14:00 | 106.94 | 94.85
2018-04-09 14:30 | 114.44 | 103.27
2018-04-09 15:00 | 111.14 | 99.9
2018-04-09 15:30 | 114.52 | 104.1
2018-04-09 16:00 | 120.58 | 111.3
2018-04-09 16:30 | 128.05 | 119.82
2018-04-09 17:00 | 122.42 | 114.46
2018-04-09 17:30 | 88.45 | 78.29
2018-04-09 18:00 | 84.74 | 73.9
2018-04-09 18:30 | 94.12 | 84.79
2018-04-09 19:00 | 106.2 | 99.1
2018-04-09 19:30 | 109.89 | 104.39
2018-04-09 20:00 | 117.52 | 113.5
2018-04-09 20:30 | 108.35 | 107.47
2018-04-09 21:00 | 78.82 | 78.15
2018-04-09 21:30 | 64.41 | 63.12
2018-04-09 22:00 | 57.79 | 56.05
2018-04-09 22:30 | 49.03 | 47.43
2018-04-09 23:00 | 47.87 | 46.08
2018-04-09 23:30 | 19.89 | 17.33
2018-04-10 | 19.92 | -19.81
2018-04-10 00:30 | 18.23 | -16.82
2018-04-10 01:00 | 13.9 | -6.53
2018-04-10 01:30 | 14.11 | 6.33
2018-04-10 02:00 | 16.99 | 12.26
2018-04-10 02:30 | 15.55 | -10.31
2018-04-10 03:00 | 22.76 | -20.28
2018-04-10 03:30 | 16.89 | -12.81
2018-04-10 04:00 | 15.22 | -9.63
2018-04-10 04:30 | 15.62 | -8.85
2018-04-10 05:00 | 14.64 | -3.08
2018-04-10 05:30 | 17.61 | -3.06
2018-04-10 06:00 | 39.66 | 33.98
2018-04-10 06:30 | 62.72 | 58.75
2018-04-10 07:00 | 69.42 | 67.82
2018-04-10 07:30 | 86.17 | 84.07
2018-04-10 08:00 | 104.57 | 89.38
2018-04-10 08:30 | 112.77 | 96.62
2018-04-10 09:00 | 117.11 | 99.47
2018-04-10 09:30 | 128.73 | 101.27
2018-04-10 10:00 | 128.48 | 94.65
2018-04-10 10:30 | 130.63 | 101.26
2018-04-10 11:00 | 123.09 | 99.47
2018-04-10 11:30 | 118.93 | 100.35
2018-04-10 12:00 | 121.29 | 102.78
2018-04-10 12:30 | 121.52 | 102.99
2018-04-10 13:00 | 128.69 | 110.37
2018-04-10 13:30 | 138.05 | 120.66
2018-04-10 14:00 | 149.57 | 135.23
2018-04-10 14:30 | 144.32 | 135.52
2018-04-10 15:00 | 138.61 | 130.05
2018-04-10 15:30 | 144.92 | 137.32
2018-04-10 16:00 | 142.07 | 134.74
2018-04-10 16:30 | 142.21 | 135.68
2018-04-10 17:00 | 151.17 | 145.33
2018-04-10 17:30 | 139.65 | 137.53
2018-04-10 18:00 | 145.33 | 144.03
2018-04-10 18:30 | 147.27 | 145.94
2018-04-10 19:00 | 154.29 | 153.26
2018-04-10 19:30 | 143.23 | 142.58
2018-04-10 20:00 | 133.7 | 133.19
2018-04-10 20:30 | 124.02 | 123.88
2018-04-10 21:00 | 110.13 | 110.05
2018-04-10 21:30 | 104.39 | 104.36
2018-04-10 22:00 | 77.62 | 77.53
2018-04-10 22:30 | 71.25 | 70.68
2018-04-10 23:00 | 78.23 | 77.52
2018-04-10 23:30 | 37.94 | 37.45
2018-04-11 | 4.41 | -3.99
2018-04-11 00:30 | 19.06 | -6.75
2018-04-11 01:00 | 30.32 | -29.04
2018-04-11 01:30 | 42.3 | -42.12
2018-04-11 02:00 | 36.69 | -35.43
2018-04-11 02:30 | 25.22 | -22.86
2018-04-11 03:00 | 25.84 | -24.04
2018-04-11 03:30 | 27.58 | -25.97
2018-04-11 04:00 | 22.17 | -19.45
2018-04-11 04:30 | 16.18 | -10.14
2018-04-11 05:00 | 16.52 | 4.99
2018-04-11 05:30 | 23.76 | 14.72
2018-04-11 06:00 | 39.03 | 37.08
2018-04-11 06:30 | 60.52 | 60.33
2018-04-11 07:00 | 55.27 | 55.25
2018-04-11 07:30 | 69.35 | 69.34
2018-04-11 08:00 | 55.79 | 53.25
2018-04-11 08:30 | 58.73 | 49.76
2018-04-11 09:00 | 81.84 | 51.72
2018-04-11 09:30 | 79.56 | 45.82
2018-04-11 10:00 | 80.07 | 44.55
2018-04-11 10:30 | 77.03 | 37.32
2018-04-11 11:00 | 78.17 | 37.72
2018-04-11 11:30 | 74.03 | 25.85
2018-04-11 12:00 | 72.7 | 23.42
2018-04-11 12:30 | 71.05 | 19.23
2018-04-11 13:00 | 70.31 | 17.25
2018-04-11 13:30 | 69.14 | 8.82
2018-04-11 14:00 | 70.09 | -6.98
2018-04-11 14:30 | 69.83 | 11.86
2018-04-11 15:00 | 70.28 | -7.07
2018-04-11 15:30 | 69.96 | 14.46
2018-04-11 16:00 | 71.6 | 25.85
2018-04-11 16:30 | 77.02 | 43.05
2018-04-11 17:00 | 76.85 | 47.82
2018-04-11 17:30 | 86.22 | 63.9
2018-04-11 18:00 | 97.48 | 77.91
2018-04-11 18:30 | 112.41 | 95.61
2018-04-11 19:00 | 120.26 | 105.89
2018-04-11 19:30 | 109.35 | 100.19
2018-04-11 20:00 | 100.34 | 98.3
2018-04-11 20:30 | 97.27 | 95.74
2018-04-11 21:00 | 91.07 | 89.19
2018-04-11 21:30 | 83.61 | 81.28
2018-04-11 22:00 | 74.8 | 72.85
2018-04-11 22:30 | 85.69 | 84.56
2018-04-11 23:00 | 60.95 | 59.68
2018-04-11 23:30 | 25.18 | 22.1
2018-04-12 | 15.38 | -8.73
2018-04-12 00:30 | 17.8 | -12.07
2018-04-12 01:00 | 6.47 | -5.44
2018-04-12 01:30 | 6.81 | -1.6
2018-04-12 02:00 | 41.82 | -41.45
2018-04-12 02:30 | 55.79 | -55.57
2018-04-12 03:00 | 46.72 | -46.38
2018-04-12 03:30 | 40.51 | -40
2018-04-12 04:00 | 42.22 | -41.75
2018-04-12 04:30 | 34.33 | -33.62
2018-04-12 05:00 | 18.55 | -16.68
2018-04-12 05:30 | 11.54 | 7.49
2018-04-12 06:00 | 38.78 | 37.87
2018-04-12 06:30 | 64.91 | 64.56
2018-04-12 07:00 | 70.83 | 70.76
2018-04-12 07:30 | 83.42 | 83.41
2018-04-12 08:00 | 96.4 | 94.58
2018-04-12 08:30 | 122.22 | 105.04
2018-04-12 09:00 | 126.68 | 108.63
2018-04-12 09:30 | 125.14 | 105.64
2018-04-12 10:00 | 120.44 | 99.4
2018-04-12 10:30 | 112.11 | 94.12
2018-04-12 11:00 | 107.52 | 88.61
2018-04-12 11:30 | 104.76 | 84.36
2018-04-12 12:00 | 108.24 | 88.17
2018-04-12 12:30 | 108.67 | 89.28
2018-04-12 13:00 | 117.45 | 100.39
2018-04-12 13:30 | 117.26 | 100.04
2018-04-12 14:00 | 114.8 | 97.25
2018-04-12 14:30 | 118.57 | 101.53
2018-04-12 15:00 | 118.33 | 101.79
2018-04-12 15:30 | 126.64 | 111.31
2018-04-12 16:00 | 124.94 | 109.51
2018-04-12 16:30 | 164.02 | 153.17
2018-04-12 17:00 | 119.42 | 104.66
2018-04-12 17:30 | 97.17 | 79.21
2018-04-12 18:00 | 95.77 | 77.12
2018-04-12 18:30 | 79.41 | 65.67
2018-04-12 19:00 | 95.22 | 87.08
2018-04-12 19:30 | 80.43 | 77.21
2018-04-12 20:00 | 71.16 | 66.38
2018-04-12 20:30 | 71.73 | 64.67
2018-04-12 21:00 | 60.17 | 46.16
2018-04-12 21:30 | 54.63 | 41.84
2018-04-12 22:00 | 45.23 | 32.24
2018-04-12 22:30 | 36.67 | 20.97
2018-04-12 23:00 | 53.16 | 51.26
2018-04-12 23:30 | 31.11 | 30.19
2018-04-13 | 9.02 | 5.58
2018-04-13 00:30 | 15.36 | -14.03
2018-04-13 01:00 | 21.21 | -20.4
2018-04-13 01:30 | 38.31 | -37.92
2018-04-13 02:00 | 48.35 | -48.14
2018-04-13 02:30 | 55.37 | -55.23
2018-04-13 03:00 | 50.6 | -50.43
2018-04-13 03:30 | 44.22 | -43.94
2018-04-13 04:00 | 41.54 | -41.25
2018-04-13 04:30 | 29.54 | -28.93
2018-04-13 05:00 | 23.07 | -22.11
2018-04-13 05:30 | 12.55 | -10.31
2018-04-13 06:00 | 13.41 | 11.43
2018-04-13 06:30 | 56.24 | 55.56
2018-04-13 07:00 | 59.72 | 59.39
2018-04-13 07:30 | 83.98 | 81.12
2018-04-13 08:00 | 89.38 | 81.77
2018-04-13 08:30 | 98.95 | 93.1
2018-04-13 09:00 | 104.47 | 97.37
2018-04-13 09:30 | 108.97 | 101.53
2018-04-13 10:00 | 110.95 | 103.14
2018-04-13 10:30 | 106.61 | 97.41
2018-04-13 11:00 | 112.83 | 103.99
2018-04-13 11:30 | 108.46 | 99.03
2018-04-13 12:00 | 131.88 | 123.74
2018-04-13 12:30 | 166.93 | 160.51
2018-04-13 13:00 | 159.52 | 153.09
2018-04-13 13:30 | 103.31 | 93.76
2018-04-13 14:00 | 104.05 | 94.54
2018-04-13 14:30 | 106.4 | 97.07
2018-04-13 15:00 | 111.47 | 102.69
2018-04-13 15:30 | 116.68 | 108.79
2018-04-13 16:00 | 136.9 | 130.62
2018-04-13 16:30 | 126.78 | 120.26
2018-04-13 17:00 | 158.15 | 153.1
2018-04-13 17:30 | 133.61 | 128.53
2018-04-13 18:00 | 129.69 | 124.5
2018-04-13 18:30 | 146.2 | 141.59
2018-04-13 19:00 | 120.57 | 115.46
2018-04-13 19:30 | 107.62 | 102.26
2018-04-13 20:00 | 94.38 | 88.62
2018-04-13 20:30 | 82.47 | 76.85
2018-04-13 21:00 | 65.6 | 60.79
2018-04-13 21:30 | 37.98 | 37.65
2018-04-13 22:00 | 31.12 | 30.45
2018-04-13 22:30 | 36.94 | 36.06
2018-04-13 23:00 | 45.34 | 44.62
2018-04-13 23:30 | 36.03 | 34.4
2018-04-14 | 15.46 | 10.07
2018-04-14 00:30 | 12.15 | 1.25
2018-04-14 01:00 | 20.73 | -17.52
2018-04-14 01:30 | 25.95 | -23.34
2018-04-14 02:00 | 23.85 | -21.11
2018-04-14 02:30 | 16 | -8.02
2018-04-14 03:00 | 17.45 | 9.18
2018-04-14 03:30 | 25.46 | 20.67
2018-04-14 04:00 | 82.85 | 82.26
2018-04-14 04:30 | 83.63 | 82.67
2018-04-14 05:00 | 103.12 | 102.34
2018-04-14 05:30 | 106.86 | 106.06
2018-04-14 06:00 | 82.14 | 81.34
2018-04-14 06:30 | 34.81 | 33.55
2018-04-14 07:00 | 57.92 | 57.3
2018-04-14 07:30 | 36.8 | 36.59
2018-04-14 08:00 | 83.15 | 83.15
2018-04-14 08:30 | 103.62 | 102.2
2018-04-14 09:00 | 107.85 | 104.24
2018-04-14 09:30 | 101.67 | 89.44
2018-04-14 10:00 | 95.65 | 72.6
2018-04-14 10:30 | 97.37 | 74.8
2018-04-14 11:00 | 100.51 | 78.6
2018-04-14 11:30 | 97.55 | 75.55
2018-04-14 12:00 | 88.78 | 64.62
2018-04-14 12:30 | 83.25 | 57.33
2018-04-14 13:00 | 89.12 | 66.76
2018-04-14 13:30 | 122.42 | 107.72
2018-04-14 14:00 | 66.73 | 33.62
2018-04-14 14:30 | 101.3 | 84.28
2018-04-14 15:00 | 79.48 | 55.45
2018-04-14 15:30 | 72.69 | 43.55
2018-04-14 16:00 | 74.28 | 43.21
2018-04-14 16:30 | 91.44 | 69.04
2018-04-14 17:00 | 124.97 | 109.69
2018-04-14 17:30 | 134.34 | 120.8
2018-04-14 18:00 | 139.79 | 125.62
2018-04-14 18:30 | 170.14 | 158.2
2018-04-14 19:00 | 163.22 | 158.87
2018-04-14 19:30 | 188.42 | 188.22
2018-04-14 20:00 | 151.24 | 151.19
2018-04-14 20:30 | 102.3 | 99.72
2018-04-14 21:00 | 77.42 | 74.28
2018-04-14 21:30 | 66.2 | 63.13
2018-04-14 22:00 | 65.52 | 62.82
2018-04-14 22:30 | 80.48 | 78.59
2018-04-14 23:00 | 94.98 | 93.46
2018-04-14 23:30 | 99.19 | 98.49
2018-04-15 | 44.85 | 43.57
2018-04-15 00:30 | 55.9 | 54.98
2018-04-15 01:00 | 22.17 | 19.24
2018-04-15 01:30 | 30.7 | 30.34
2018-04-15 02:00 | 79.2 | 78.6
2018-04-15 02:30 | 41.52 | 40.55
2018-04-15 03:00 | 92.15 | 91.71
2018-04-15 03:30 | 89.13 | 88.86
2018-04-15 04:00 | 86.16 | 85.66
2018-04-15 04:30 | 98.93 | 98.52
2018-04-15 05:00 | 98.9 | 98.46
2018-04-15 05:30 | 92.72 | 92.08
2018-04-15 06:00 | 86.32 | 85.66
2018-04-15 06:30 | 33.85 | 31.59
2018-04-15 07:00 | 39.21 | 37.4
2018-04-15 07:30 | 45.72 | 44.49
2018-04-15 08:00 | 51.33 | 50.6
2018-04-15 08:30 | 57 | 56.83
2018-04-15 09:00 | 61.61 | 61.6
2018-04-15 09:30 | 64.25 | 64.12
2018-04-15 10:00 | 69.57 | 65.68
2018-04-15 10:30 | 71.9 | 66.08
2018-04-15 11:00 | 72.45 | 65.99
2018-04-15 11:30 | 85.44 | 69.05
2018-04-15 12:00 | 96.81 | 71.39
2018-04-15 12:30 | 99.63 | 74.46
2018-04-15 13:00 | 105.22 | 81.15
2018-04-15 13:30 | 112.29 | 89.27
2018-04-15 14:00 | 122.04 | 101.48
2018-04-15 14:30 | 128.36 | 111.42
2018-04-15 15:00 | 131.24 | 114.84
2018-04-15 15:30 | 135.87 | 120.43
2018-04-15 16:00 | 140.87 | 126.37
2018-04-15 16:30 | 146.19 | 132.69
2018-04-15 17:00 | 159.1 | 146.75
2018-04-15 17:30 | 198.47 | 189.18
2018-04-15 18:00 | 201.53 | 191.42
2018-04-15 18:30 | 203.39 | 193.46
2018-04-15 19:00 | 204.53 | 195.25
2018-04-15 19:30 | 196.76 | 188.04
2018-04-15 20:00 | 195.44 | 187.28
2018-04-15 20:30 | 183.94 | 182.75
2018-04-15 21:00 | 142.12 | 140.96
2018-04-15 21:30 | 121.64 | 120.64
2018-04-15 22:00 | 156.42 | 155.84
2018-04-15 22:30 | 98.25 | 97.93
2018-04-15 23:00 | 82.03 | 81.82
2018-04-15 23:30 | 59.73 | 59.17
2018-04-16 | 30.65 | 29.02
2018-04-16 00:30 | 29.67 | 28.05
2018-04-16 01:00 | 23.08 | 22.92
2018-04-16 01:30 | 87.88 | 87.5
2018-04-16 02:00 | 71.66 | 71.15
2018-04-16 02:30 | 35.36 | 34.02
2018-04-16 03:00 | 14.18 | 9.67
2018-04-16 03:30 | 13.69 | 8.44
2018-04-16 04:00 | 15.18 | 9.48
2018-04-16 04:30 | 16.55 | 11.04
2018-04-16 05:00 | 17.99 | 13.59
2018-04-16 05:30 | 22.15 | 19.01
2018-04-16 06:00 | 31.91 | 29.45
2018-04-16 06:30 | 42.06 | 40.59
2018-04-16 07:00 | 47.66 | 47.05
2018-04-16 07:30 | 42.77 | 40.77
2018-04-16 08:00 | 48.87 | 34.25
2018-04-16 08:30 | 73.84 | 37.72
2018-04-16 09:00 | 76.23 | 33.27
2018-04-16 09:30 | 78.16 | 35.99
2018-04-16 10:00 | 77.91 | 30.28
2018-04-16 10:30 | 66.53 | 16.32
2018-04-16 11:00 | 64.58 | 20.34
2018-04-16 11:30 | 64.48 | 22.36
2018-04-16 12:00 | 60.88 | 24.45
2018-04-16 12:30 | 60.88 | 26.47
2018-04-16 13:00 | 61.94 | 27.73
2018-04-16 13:30 | 72.86 | 47.86
2018-04-16 14:00 | 84.47 | 63.58
2018-04-16 14:30 | 111.36 | 97.1
2018-04-16 15:00 | 116.51 | 103.91
2018-04-16 15:30 | 138.37 | 127.93
2018-04-16 16:00 | 147.49 | 137.77
2018-04-16 16:30 | 158.01 | 149.44
2018-04-16 17:00 | 163.32 | 155.71
2018-04-16 17:30 | 150.25 | 143.61
2018-04-16 18:00 | 128.97 | 121.05
2018-04-16 18:30 | 121.8 | 113.72
2018-04-16 19:00 | 131.09 | 124.52
2018-04-16 19:30 | 102.67 | 101.33
2018-04-16 20:00 | 77.88 | 72.01
2018-04-16 20:30 | 56.91 | 49.41
2018-04-16 21:00 | 42.07 | 37.15
2018-04-16 21:30 | 34.59 | 31.77
2018-04-16 22:00 | 15.74 | 11.56
2018-04-16 22:30 | 9.37 | -2.04
2018-04-16 23:00 | 18.59 | 17.59
2018-04-16 23:30 | 18.74 | -17.9
2018-04-17 | 39.64 | -39.25
2018-04-17 00:30 | 37.97 | -36.41
2018-04-17 01:00 | 40.58 | -38.56
2018-04-17 01:30 | 33.71 | -31.32
2018-04-17 02:00 | 44.14 | -43.29
2018-04-17 02:30 | 45.61 | -45.15
2018-04-17 03:00 | 52.69 | -52.34
2018-04-17 03:30 | 45.55 | -44.97
2018-04-17 04:00 | 39.34 | -38.45
2018-04-17 04:30 | 20.01 | -17.11
2018-04-17 05:00 | 17.32 | -14.15
2018-04-17 05:30 | 11.55 | 5.74
2018-04-17 06:00 | 44.5 | 43.21
2018-04-17 06:30 | 64.71 | 64.12
2018-04-17 07:00 | 125.56 | 125.39
2018-04-17 07:30 | 157.03 | 156.97
2018-04-17 08:00 | 164.59 | 162.23
2018-04-17 08:30 | 163.39 | 160.14
2018-04-17 09:00 | 162.48 | 159.45
2018-04-17 09:30 | 163.77 | 159.73
2018-04-17 10:00 | 178.86 | 160.55
2018-04-17 10:30 | 177.38 | 152.57
2018-04-17 11:00 | 179.31 | 153.63
2018-04-17 11:30 | 182.3 | 156.28
2018-04-17 12:00 | 187.87 | 162.68
2018-04-17 12:30 | 189.92 | 165.47
2018-04-17 13:00 | 193.64 | 169.26
2018-04-17 13:30 | 197.39 | 173.19
2018-04-17 14:00 | 204.37 | 180.65
2018-04-17 14:30 | 206.25 | 182.85
2018-04-17 15:00 | 204.05 | 181.27
2018-04-17 15:30 | 185.75 | 164.42
2018-04-17 16:00 | 163.26 | 140.27
2018-04-17 16:30 | 162.81 | 141.05
2018-04-17 17:00 | 174.12 | 154.91
2018-04-17 17:30 | 157.86 | 138.71
2018-04-17 18:00 | 133.06 | 108.65
2018-04-17 18:30 | 130.33 | 105.86
2018-04-17 19:00 | 125.98 | 105.99
2018-04-17 19:30 | 122.27 | 110.77
2018-04-17 20:00 | 114.46 | 102.78
2018-04-17 20:30 | 94.15 | 81.34
2018-04-17 21:00 | 68.19 | 54.36
2018-04-17 21:30 | 32.51 | 32.39
2018-04-17 22:00 | 20.77 | 18.42
2018-04-17 22:30 | 19.71 | 18.33
2018-04-17 23:00 | 50.19 | 47.99
2018-04-17 23:30 | 18.34 | 12.15
2018-04-18 | 23.78 | -18.32
2018-04-18 00:30 | 36.88 | -33.44
2018-04-18 01:00 | 40.72 | -37.89
2018-04-18 01:30 | 50.53 | -48.24
2018-04-18 02:00 | 51.5 | -49.3
2018-04-18 02:30 | 48.89 | -46.94
2018-04-18 03:00 | 46.53 | -44.75
2018-04-18 03:30 | 44.74 | -43.08
2018-04-18 04:00 | 41.21 | -39.7
2018-04-18 04:30 | 36.18 | -34.78
2018-04-18 05:00 | 30.2 | -28.44
2018-04-18 05:30 | 13.87 | -9.14
2018-04-18 06:00 | 20.45 | -15.73
2018-04-18 06:30 | 70.76 | 69.31
2018-04-18 07:00 | 93.95 | 92.66
2018-04-18 07:30 | 106.01 | 104.17
2018-04-18 08:00 | 111.82 | 109.22
2018-04-18 08:30 | 116.73 | 113.47
2018-04-18 09:00 | 127.03 | 114.75
2018-04-18 09:30 | 138.38 | 111.63
2018-04-18 10:00 | 147.86 | 122.77
2018-04-18 10:30 | 140.69 | 113.72
2018-04-18 11:00 | 146.88 | 120.57
2018-04-18 11:30 | 128.79 | 98.17
2018-04-18 12:00 | 127.23 | 96.5
2018-04-18 12:30 | 126.06 | 95.01
2018-04-18 13:00 | 120.15 | 86.83
2018-04-18 13:30 | 119.09 | 85.21
2018-04-18 14:00 | 113.17 | 87.37
2018-04-18 14:30 | 108.49 | 87.07
2018-04-18 15:00 | 110.05 | 89.59
2018-04-18 15:30 | 109.74 | 90.07
2018-04-18 16:00 | 127.68 | 112.09
2018-04-18 16:30 | 121.07 | 105.39
2018-04-18 17:00 | 106.11 | 87.78
2018-04-18 17:30 | 97.93 | 78.24
2018-04-18 18:00 | 97.86 | 76.07
2018-04-18 18:30 | 102.59 | 82.28
2018-04-18 19:00 | 111.04 | 94.48
2018-04-18 19:30 | 88.34 | 68.02
2018-04-18 20:00 | 75.1 | 50.29
2018-04-18 20:30 | 65.36 | 36.39
2018-04-18 21:00 | 79.76 | 77.02
2018-04-18 21:30 | 50.3 | 50.12
2018-04-18 22:00 | 26.17 | 25.65
2018-04-18 22:30 | 16.81 | 15.41
2018-04-18 23:00 | 33.41 | 32.22
2018-04-18 23:30 | 16.89 | 13.55
2018-04-19 | 19.09 | -17.71
2018-04-19 00:30 | 26.67 | -25.92
2018-04-19 01:00 | 28.65 | -28.09
2018-04-19 01:30 | 36.9 | -36.47
2018-04-19 02:00 | 28 | -27.09
2018-04-19 02:30 | 33.7 | -32.92
2018-04-19 03:00 | 37.42 | -36.84
2018-04-19 03:30 | 31.51 | -30.65
2018-04-19 04:00 | 26.16 | -24.7
2018-04-19 04:30 | 17.36 | -13.56
2018-04-19 05:00 | 12.47 | -0.08
2018-04-19 05:30 | 19.12 | 14.8
2018-04-19 06:00 | 37.14 | 35.58
2018-04-19 06:30 | 75.74 | 75.33
2018-04-19 07:00 | 101.4 | 101.25
2018-04-19 07:30 | 111.16 | 110.74
2018-04-19 08:00 | 93.61 | 92.88
2018-04-19 08:30 | 85.88 | 85.57
2018-04-19 09:00 | 93.94 | 93.8
2018-04-19 09:30 | 85.05 | 85.01
2018-04-19 10:00 | 89.56 | 89.55
2018-04-19 10:30 | 88.93 | 87.48
2018-04-19 11:00 | 88.06 | 85.91
2018-04-19 11:30 | 89.48 | 87.6
2018-04-19 12:00 | 88.82 | 87.18
2018-04-19 12:30 | 86.39 | 84.86
2018-04-19 13:00 | 92.23 | 90.68
2018-04-19 13:30 | 90.85 | 89.19
2018-04-19 14:00 | 95.26 | 93.62
2018-04-19 14:30 | 95.44 | 93.79
2018-04-19 15:00 | 87.58 | 85.92
2018-04-19 15:30 | 78.04 | 77.02
2018-04-19 16:00 | 86.09 | 85.3
2018-04-19 16:30 | 76.85 | 76.26
2018-04-19 17:00 | 56.64 | 56.02
2018-04-19 17:30 | 46.48 | 45.6
2018-04-19 18:00 | 75.44 | 74.5
2018-04-19 18:30 | 76.95 | 76.28
2018-04-19 19:00 | 100.39 | 100.19
2018-04-19 19:30 | 135.03 | 134.91
2018-04-19 20:00 | 108.69 | 106.94
2018-04-19 20:30 | 91.98 | 89.4
2018-04-19 21:00 | 62.06 | 57.29
2018-04-19 21:30 | 49.86 | 49.85
2018-04-19 22:00 | 16.93 | 15.7
2018-04-19 22:30 | 26.86 | 25.85
2018-04-19 23:00 | 50.98 | 50.31
2018-04-19 23:30 | 40.05 | 39.23
2018-04-20 | 14.23 | 12.31
2018-04-20 00:30 | 13.53 | -12.47
2018-04-20 01:00 | 13.42 | -12.16
2018-04-20 01:30 | 15.86 | -14.71
2018-04-20 02:00 | 12.41 | -10.12
2018-04-20 02:30 | 16.85 | -14.83
2018-04-20 03:00 | 22.64 | -21.47
2018-04-20 03:30 | 14.91 | -12.72
2018-04-20 04:00 | 11.1 | -6.52
2018-04-20 04:30 | 18.59 | 15.27
2018-04-20 05:00 | 33.75 | 31.67
2018-04-20 05:30 | 57.42 | 56.13
2018-04-20 06:00 | 67.29 | 66.28
2018-04-20 06:30 | 90.83 | 90.31
2018-04-20 07:00 | 101.85 | 101.65
2018-04-20 07:30 | 129.26 | 129.18
2018-04-20 08:00 | 97.34 | 97.34
2018-04-20 08:30 | 82.75 | 82.72
2018-04-20 09:00 | 90.69 | 90.69
2018-04-20 09:30 | 98.11 | 98.07
2018-04-20 10:00 | 101.72 | 101.19
2018-04-20 10:30 | 100.25 | 96.38
2018-04-20 11:00 | 106.12 | 102.3
2018-04-20 11:30 | 105.24 | 101.68
2018-04-20 12:00 | 114.19 | 112.32
2018-04-20 12:30 | 133.44 | 131.94
2018-04-20 13:00 | 140.58 | 139.32
2018-04-20 13:30 | 137.06 | 136
2018-04-20 14:00 | 126.72 | 125.61
2018-04-20 14:30 | 128.15 | 126.69
2018-04-20 15:00 | 128.57 | 127.28
2018-04-20 15:30 | 127.98 | 126.98
2018-04-20 16:00 | 127 | 126.14
2018-04-20 16:30 | 127.43 | 126.67
2018-04-20 17:00 | 112.67 | 111.94
2018-04-20 17:30 | 113.75 | 113.09
2018-04-20 18:00 | 109.16 | 108.43
2018-04-20 18:30 | 97.19 | 96.61
2018-04-20 19:00 | 116.51 | 116.38
2018-04-20 19:30 | 127.59 | 127.5
2018-04-20 20:00 | 124.86 | 124.48
2018-04-20 20:30 | 96.97 | 96.32
2018-04-20 21:00 | 74.61 | 73.84
2018-04-20 21:30 | 68.36 | 66.77
2018-04-20 22:00 | 60.5 | 56.64
2018-04-20 22:30 | 77.58 | 74.57
2018-04-20 23:00 | 96.43 | 93.85
2018-04-20 23:30 | 67.17 | 63.76
2018-04-21 | 29.75 | 24.08
2018-04-21 00:30 | 18.7 | 13.17
2018-04-21 01:00 | 11.13 | -3.7
2018-04-21 01:30 | 10.76 | -3.41
2018-04-21 02:00 | 7.32 | 6.96
2018-04-21 02:30 | 21.02 | 19.39
2018-04-21 03:00 | 24.86 | 23.56
2018-04-21 03:30 | 20.21 | 18.19
2018-04-21 04:00 | 19.18 | 16.99
2018-04-21 04:30 | 22.63 | 21.7
2018-04-21 05:00 | 9.43 | 8.47
2018-04-21 05:30 | 15.43 | 15.24
2018-04-21 06:00 | 20.73 | 20.73
2018-04-21 06:30 | 25.06 | 21.91
2018-04-21 07:00 | 28.36 | 21.65
2018-04-21 07:30 | 23.76 | 14.22
2018-04-21 08:00 | 15.29 | 8.67
2018-04-21 08:30 | 22.15 | 22.05
2018-04-21 09:00 | 18.52 | 17.6
2018-04-21 09:30 | 9.05 | 0.03
2018-04-21 10:00 | 49.79 | 5
2018-04-21 10:30 | 61.1 | -2.75
2018-04-21 11:00 | 61.49 | 0.67
2018-04-21 11:30 | 62.06 | 5.72
2018-04-21 12:00 | 61.74 | 4.55
2018-04-21 12:30 | 61.75 | 15.97
2018-04-21 13:00 | 47.06 | 15.59
2018-04-21 13:30 | 41.33 | 16.39
2018-04-21 14:00 | 46.29 | 25.43
2018-04-21 14:30 | 59.72 | 45.77
2018-04-21 15:00 | 77.88 | 68.24
2018-04-21 15:30 | 83.6 | 74.94
2018-04-21 16:00 | 103.85 | 97.48
2018-04-21 16:30 | 112.27 | 107.07
2018-04-21 17:00 | 125.03 | 120.4
2018-04-21 17:30 | 146.22 | 142.39
2018-04-21 18:00 | 154.9 | 150.69
2018-04-21 18:30 | 170.71 | 167.08
2018-04-21 19:00 | 169.87 | 166.49
2018-04-21 19:30 | 148.27 | 144.91
2018-04-21 20:00 | 131.34 | 128
2018-04-21 20:30 | 108.36 | 106.39
2018-04-21 21:00 | 87.85 | 87.68
2018-04-21 21:30 | 71.96 | 71.61
2018-04-21 22:00 | 51.05 | 50.31
2018-04-21 22:30 | 73.95 | 73.24
2018-04-21 23:00 | 89.68 | 88.91
2018-04-21 23:30 | 62 | 60.68
2018-04-22 | 25.22 | 22.72
2018-04-22 00:30 | 9.86 | 3.13
2018-04-22 01:00 | 10.46 | -5.38
2018-04-22 01:30 | 13.37 | -10.16
2018-04-22 02:00 | 9.93 | -4.95
2018-04-22 02:30 | 12.2 | -4.65
2018-04-22 03:00 | 17.24 | -12.94
2018-04-22 03:30 | 15.13 | -9.6
2018-04-22 04:00 | 21.02 | -17.68
2018-04-22 04:30 | 12.68 | -2.41
2018-04-22 05:00 | 12.82 | -2.66
2018-04-22 05:30 | 15 | 7.18
2018-04-22 06:00 | 14.21 | 4.92
2018-04-22 06:30 | 12.16 | -1.1
2018-04-22 07:00 | 13.46 | -7.88
2018-04-22 07:30 | 15.15 | -11.85
2018-04-22 08:00 | 25.52 | -24.48
2018-04-22 08:30 | 15.85 | -14.76
2018-04-22 09:00 | 5.03 | -4.51
2018-04-22 09:30 | 2.29 | -2.29
2018-04-22 10:00 | 5.51 | 5.41
2018-04-22 10:30 | 5.65 | -5.42
2018-04-22 11:00 | 5.21 | -4.07
2018-04-22 11:30 | 5.62 | -4.73
2018-04-22 12:00 | 7.77 | -7.31
2018-04-22 12:30 | 8.82 | -8.25
2018-04-22 13:00 | 11.32 | -10.87
2018-04-22 13:30 | 22.03 | -21.71
2018-04-22 14:00 | 8.55 | -7.74
2018-04-22 14:30 | 4.69 | 2.76
2018-04-22 15:00 | 4.28 | 0.39
2018-04-22 15:30 | 16.19 | 14.7
2018-04-22 16:00 | 57.97 | 23.01
2018-04-22 16:30 | 67.4 | 46.05
2018-04-22 17:00 | 93.65 | 80.32
2018-04-22 17:30 | 117.98 | 108.04
2018-04-22 18:00 | 114.86 | 106.32
2018-04-22 18:30 | 125.68 | 121.01
2018-04-22 19:00 | 144.7 | 142.08
2018-04-22 19:30 | 123.41 | 123.38
2018-04-22 20:00 | 109.32 | 107.68
2018-04-22 20:30 | 97.82 | 95.83
2018-04-22 21:00 | 76.93 | 74.15
2018-04-22 21:30 | 64.85 | 61.07
2018-04-22 22:00 | 42.79 | 37.1
2018-04-22 22:30 | 34.89 | 28.55
2018-04-22 23:00 | 32.53 | 26.17
2018-04-22 23:30 | 15.03 | -3.06
2018-04-23 | 46.28 | -45.77
2018-04-23 00:30 | 52.71 | -52.59
2018-04-23 01:00 | 10.7 | -3.85
2018-04-23 01:30 | 14.95 | -12.74
2018-04-23 02:00 | 14.61 | -12.78
2018-04-23 02:30 | 16.58 | -9.98
2018-04-23 03:00 | 18.25 | -12.92
2018-04-23 03:30 | 15.9 | -8.99
2018-04-23 04:00 | 14.61 | 0.43
2018-04-23 04:30 | 30.06 | 24.85
2018-04-23 05:00 | 47.59 | 43.82
2018-04-23 05:30 | 42.22 | 36.82
2018-04-23 06:00 | 59.12 | 54.4
2018-04-23 06:30 | 77.73 | 76.29
2018-04-23 07:00 | 91.6 | 91.4
2018-04-23 07:30 | 107.2 | 106.36
2018-04-23 08:00 | 103.84 | 98.07
2018-04-23 08:30 | 92.7 | 84.86
2018-04-23 09:00 | 77.24 | 65.92
2018-04-23 09:30 | 69.52 | 55.35
2018-04-23 10:00 | 69.1 | 53.69
2018-04-23 10:30 | 74.01 | 58.87
2018-04-23 11:00 | 74.8 | 58.59
2018-04-23 11:30 | 72.31 | 56.5
2018-04-23 12:00 | 74.59 | 59.08
2018-04-23 12:30 | 75.33 | 62.47
2018-04-23 13:00 | 86.99 | 78.13
2018-04-23 13:30 | 106.89 | 99.94
2018-04-23 14:00 | 101.9 | 95.05
2018-04-23 14:30 | 116.39 | 110.29
2018-04-23 15:00 | 124.73 | 119.5
2018-04-23 15:30 | 122.46 | 117.73
2018-04-23 16:00 | 144.85 | 140.84
2018-04-23 16:30 | 148.5 | 145.07
2018-04-23 17:00 | 164.46 | 161.51
2018-04-23 17:30 | 161.8 | 159.08
2018-04-23 18:00 | 160.67 | 157.42
2018-04-23 18:30 | 165.15 | 162.3
2018-04-23 19:00 | 171.86 | 169.53
2018-04-23 19:30 | 175.66 | 173.16
2018-04-23 20:00 | 165.35 | 162.28
2018-04-23 20:30 | 141.06 | 139.53
2018-04-23 21:00 | 110.93 | 110.84
2018-04-23 21:30 | 92.35 | 92.09
2018-04-23 22:00 | 75.49 | 74.89
2018-04-23 22:30 | 62.67 | 62
2018-04-23 23:00 | 82.27 | 81.55
2018-04-23 23:30 | 50.13 | 48.67
2018-04-24 | 16.88 | 13.41
2018-04-24 00:30 | 9.23 | -0.43
2018-04-24 01:00 | 9.96 | 4.09
2018-04-24 01:30 | 11.61 | -8.05
2018-04-24 02:00 | 12.02 | -8.11
2018-04-24 02:30 | 14.81 | -12.2
2018-04-24 03:00 | 14.71 | -12.19
2018-04-24 03:30 | 11.67 | -7.71
2018-04-24 04:00 | 9.95 | 2.85
2018-04-24 04:30 | 38.3 | 36.53
2018-04-24 05:00 | 51.61 | 50.4
2018-04-24 05:30 | 66.94 | 66.15
2018-04-24 06:00 | 70.12 | 69.26
2018-04-24 06:30 | 72.39 | 71.82
2018-04-24 07:00 | 97.82 | 97.51
2018-04-24 07:30 | 104.03 | 103.98
2018-04-24 08:00 | 95.04 | 94.99
2018-04-24 08:30 | 71.83 | 70.88
2018-04-24 09:00 | 60.44 | 59.75
2018-04-24 09:30 | 41.72 | 41.11
2018-04-24 10:00 | 24.98 | 24.86
2018-04-24 10:30 | 16.57 | 16.57
2018-04-24 11:00 | 17.12 | 17.12
2018-04-24 11:30 | 17.74 | 17.74
2018-04-24 12:00 | 14.88 | 14.88
2018-04-24 12:30 | 32.95 | 32.93
2018-04-24 13:00 | 55.22 | 55.21
2018-04-24 13:30 | 62.58 | 54.28
2018-04-24 14:00 | 76.25 | 70.2
2018-04-24 14:30 | 84.83 | 80.35
2018-04-24 15:00 | 76.11 | 71.58
2018-04-24 15:30 | 82.61 | 78.96
2018-04-24 16:00 | 87.78 | 84.76
2018-04-24 16:30 | 83.11 | 80.49
2018-04-24 17:00 | 94.88 | 93.07
2018-04-24 17:30 | 83.36 | 81.22
2018-04-24 18:00 | 73.61 | 70.43
2018-04-24 18:30 | 59.94 | 56.56
2018-04-24 19:00 | 50.47 | 47.22
2018-04-24 19:30 | 77.04 | 76.86
2018-04-24 20:00 | 79.25 | 79.09
2018-04-24 20:30 | 80.03 | 80.01
2018-04-24 21:00 | 74.46 | 74.31
2018-04-24 21:30 | 75.57 | 75.23
2018-04-24 22:00 | 39.22 | 38.08
2018-04-24 22:30 | 61.07 | 59.85
2018-04-24 23:00 | 69.19 | 67.8
2018-04-24 23:30 | 38.31 | 36.25
2018-04-25 | 19.74 | -18.21
2018-04-25 00:30 | 25.15 | -24.22
2018-04-25 01:00 | 36.98 | -36.49
2018-04-25 01:30 | 41.94 | -41.46
2018-04-25 02:00 | 46.62 | -46.09
2018-04-25 02:30 | 40.57 | -39.93
2018-04-25 03:00 | 39.36 | -38.72
2018-04-25 03:30 | 34.91 | -33.99
2018-04-25 04:00 | 37.8 | -36.94
2018-04-25 04:30 | 35.44 | -34.36
2018-04-25 05:00 | 27.15 | -25.72
2018-04-25 05:30 | 12.01 | -7.14
2018-04-25 06:00 | 18.07 | -15.73
2018-04-25 06:30 | 9.93 | -5.06
2018-04-25 07:00 | 8.79 | 0.38
2018-04-25 07:30 | 11.11 | -6.76
2018-04-25 08:00 | 15.25 | -12.54
2018-04-25 08:30 | 14.5 | -12.13
2018-04-25 09:00 | 15.75 | -14.89
2018-04-25 09:30 | 5.06 | -4.56
2018-04-25 10:00 | 9.04 | -9.04
2018-04-25 10:30 | 9 | -8.61
2018-04-25 11:00 | 25.69 | -25.37
2018-04-25 11:30 | 30.55 | -30.34
2018-04-25 12:00 | 27.07 | -26.88
2018-04-25 12:30 | 22.67 | -22.47
2018-04-25 13:00 | 11.52 | -11.17
2018-04-25 13:30 | 17.48 | -17.23
2018-04-25 14:00 | 2.25 | 0.54
2018-04-25 14:30 | 14.47 | 14.45
2018-04-25 15:00 | 21.63 | 21.62
2018-04-25 15:30 | 22.36 | 22.36
2018-04-25 16:00 | 40.45 | 40.45
2018-04-25 16:30 | 74.09 | 74.07
2018-04-25 17:00 | 93.2 | 93.11
2018-04-25 17:30 | 107.51 | 106.94
2018-04-25 18:00 | 121.82 | 121.66
2018-04-25 18:30 | 108.53 | 108.4
2018-04-25 19:00 | 124.43 | 124.26
2018-04-25 19:30 | 118.56 | 118.19
2018-04-25 20:00 | 101.03 | 100.45
2018-04-25 20:30 | 86.25 | 85.27
2018-04-25 21:00 | 66.54 | 64.74
2018-04-25 21:30 | 57.99 | 57.37
2018-04-25 22:00 | 45.09 | 44
2018-04-25 22:30 | 58.54 | 57.52
2018-04-25 23:00 | 72.87 | 71.89
2018-04-25 23:30 | 44.1 | 42.48
2018-04-26 | 11.32 | -4.76
2018-04-26 00:30 | 13.86 | -10.09
2018-04-26 01:00 | 22.56 | -20.94
2018-04-26 01:30 | 31.12 | -30.03
2018-04-26 02:00 | 38.64 | -37.84
2018-04-26 02:30 | 39.36 | -38.68
2018-04-26 03:00 | 39.76 | -39.2
2018-04-26 03:30 | 30.37 | -29.3
2018-04-26 04:00 | 31.41 | -30.2
2018-04-26 04:30 | 29.35 | -27.8
2018-04-26 05:00 | 13.81 | -9.46
2018-04-26 05:30 | 12.82 | 8.01
2018-04-26 06:00 | 22.52 | 20.36
2018-04-26 06:30 | 53.82 | 53.03
2018-04-26 07:00 | 62.77 | 62.46
2018-04-26 07:30 | 62.58 | 62.55
2018-04-26 08:00 | 42.58 | 42.44
2018-04-26 08:30 | 26.84 | 12.66
2018-04-26 09:00 | 26.82 | 9.85
2018-04-26 09:30 | 28.74 | 9.11
2018-04-26 10:00 | 32.3 | 14.48
2018-04-26 10:30 | 36.95 | 22.12
2018-04-26 11:00 | 37.34 | 20.79
2018-04-26 11:30 | 36.6 | 17.58
2018-04-26 12:00 | 48.77 | 36.49
2018-04-26 12:30 | 78.76 | 72.87
2018-04-26 13:00 | 67.09 | 59.82
2018-04-26 13:30 | 52.93 | 42.96
2018-04-26 14:00 | 77.77 | 71.42
2018-04-26 14:30 | 133.86 | 130.44
2018-04-26 15:00 | 142.09 | 139.04
2018-04-26 15:30 | 141.63 | 139.03
2018-04-26 16:00 | 121.24 | 118.69
2018-04-26 16:30 | 116.46 | 114.08
2018-04-26 17:00 | 121.54 | 119.43
2018-04-26 17:30 | 104.42 | 102.27
2018-04-26 18:00 | 81.99 | 77.12
2018-04-26 18:30 | 92.27 | 88.55
2018-04-26 19:00 | 104.86 | 102.21
2018-04-26 19:30 | 114.7 | 113.13
2018-04-26 20:00 | 106.87 | 105.58
2018-04-26 20:30 | 87.82 | 87.41
2018-04-26 21:00 | 76.98 | 76.86
2018-04-26 21:30 | 76.09 | 76.09
2018-04-26 22:00 | 56.85 | 56.7
2018-04-26 22:30 | 47.41 | 47.34
2018-04-26 23:00 | 67.34 | 67.05
2018-04-26 23:30 | 27.31 | 18.83
2018-04-27 | 20.09 | -14.09
2018-04-27 00:30 | 20.75 | -17.72
2018-04-27 01:00 | 20.68 | -18.54
2018-04-27 01:30 | 21.54 | -19.9
2018-04-27 02:00 | 21.55 | -20.11
2018-04-27 02:30 | 20.32 | -18.85
2018-04-27 03:00 | 23.97 | -23.2
2018-04-27 03:30 | 28.9 | -28.42
2018-04-27 04:00 | 28.68 | -28.14
2018-04-27 04:30 | 14.19 | -11.53
2018-04-27 05:00 | 12.87 | 6.82
2018-04-27 05:30 | 26.56 | 19.89
2018-04-27 06:00 | 35.48 | 29.36
2018-04-27 06:30 | 56.24 | 52.52
2018-04-27 07:00 | 83.68 | 81.45
2018-04-27 07:30 | 86.87 | 86.72
2018-04-27 08:00 | 65.33 | 65.31
2018-04-27 08:30 | 44.83 | 44.61
2018-04-27 09:00 | 22.96 | 22.26
2018-04-27 09:30 | 13.7 | 13.56
2018-04-27 10:00 | 1.06 | -0.73
2018-04-27 10:30 | 9.58 | -9.58
2018-04-27 11:00 | 8.75 | -8.71
2018-04-27 11:30 | 3.7 | -3.55
2018-04-27 12:00 | 5.81 | -5.77
2018-04-27 12:30 | 5.09 | -4.96
2018-04-27 13:00 | 4.96 | 4.43
2018-04-27 13:30 | 12.57 | 12.45
2018-04-27 14:00 | 43.07 | 43.05
2018-04-27 14:30 | 64.34 | 64.28
2018-04-27 15:00 | 69.26 | 69.11
2018-04-27 15:30 | 82.03 | 81.68
2018-04-27 16:00 | 88.55 | 88.13
2018-04-27 16:30 | 91.59 | 90.94
2018-04-27 17:00 | 113.43 | 112.8
2018-04-27 17:30 | 121.96 | 121.51
2018-04-27 18:00 | 108.35 | 108.03
2018-04-27 18:30 | 108.26 | 108.02
2018-04-27 19:00 | 118.06 | 117.75
2018-04-27 19:30 | 116.03 | 115.49
2018-04-27 20:00 | 113.81 | 113.16
2018-04-27 20:30 | 101.22 | 100.29
2018-04-27 21:00 | 73.74 | 73.6
2018-04-27 21:30 | 70.47 | 70.19
2018-04-27 22:00 | 40.1 | 39.37
2018-04-27 22:30 | 44.32 | 43.31
2018-04-27 23:00 | 89.99 | 89.21
2018-04-27 23:30 | 61.84 | 60.03
2018-04-28 | 19.12 | 14.26
2018-04-28 00:30 | 15.61 | -12.81
2018-04-28 01:00 | 22.28 | -20.76
2018-04-28 01:30 | 9.25 | -2.07
2018-04-28 02:00 | 8.71 | -1.89
2018-04-28 02:30 | 9.13 | 0.6
2018-04-28 03:00 | 9.41 | 1.22
2018-04-28 03:30 | 13.4 | -2.47
2018-04-28 04:00 | 14.83 | -2.72
2018-04-28 04:30 | 15.5 | 2.48
2018-04-28 05:00 | 19.2 | 9.17
2018-04-28 05:30 | 20.7 | 9.4
2018-04-28 06:00 | 24.89 | 14.09
2018-04-28 06:30 | 27.51 | 18.43
2018-04-28 07:00 | 33.13 | 25.66
2018-04-28 07:30 | 27.06 | 16.44
2018-04-28 08:00 | 17.42 | 4.55
2018-04-28 08:30 | 26.36 | 21.04
2018-04-28 09:00 | 32.94 | 32.94
2018-04-28 09:30 | 17.68 | 17.15
2018-04-28 10:00 | 15.36 | 14.54
2018-04-28 10:30 | 19.37 | 18.74
2018-04-28 11:00 | 5.37 | -1.08
2018-04-28 11:30 | 14.88 | 14.1
2018-04-28 12:00 | 18.28 | 17.44
2018-04-28 12:30 | 8.1 | 6.63
2018-04-28 13:00 | 10.3 | 9.53
2018-04-28 13:30 | 28.94 | 28.73
2018-04-28 14:00 | 56.25 | 56.16
2018-04-28 14:30 | 62.79 | 62.78
2018-04-28 15:00 | 65.51 | 65.51
2018-04-28 15:30 | 78.26 | 78.26
2018-04-28 16:00 | 90.88 | 90.88
2018-04-28 16:30 | 89.83 | 89.83
2018-04-28 17:00 | 96.94 | 96.94
2018-04-28 17:30 | 97.6 | 97.6
2018-04-28 18:00 | 114.64 | 114.41
2018-04-28 18:30 | 133.36 | 132.92
2018-04-28 19:00 | 127.85 | 126.6
2018-04-28 19:30 | 139.35 | 137.99
2018-04-28 20:00 | 130.47 | 128.92
2018-04-28 20:30 | 123.92 | 123.21
2018-04-28 21:00 | 101.5 | 101.12
2018-04-28 21:30 | 88.54 | 87.86
2018-04-28 22:00 | 73.24 | 72.3
2018-04-28 22:30 | 95.35 | 94.5
2018-04-28 23:00 | 103.56 | 102.69
2018-04-28 23:30 | 74.4 | 73.16
2018-04-29 | 37.53 | 35.65
2018-04-29 00:30 | 27.86 | 25.57
2018-04-29 01:00 | 12.57 | 7.25
2018-04-29 01:30 | 17.14 | -12.11
2018-04-29 02:00 | 30.01 | -27.23
2018-04-29 02:30 | 27.57 | -25.04
2018-04-29 03:00 | 16.62 | -11.59
2018-04-29 03:30 | 16.43 | -11.46
2018-04-29 04:00 | 17.2 | -12.47
2018-04-29 04:30 | 13.49 | -5.7
2018-04-29 05:00 | 13.26 | 2.16
2018-04-29 05:30 | 14.22 | 2.08
2018-04-29 06:00 | 16.41 | 5.56
2018-04-29 06:30 | 21.11 | 15.42
2018-04-29 07:00 | 26.32 | 21.24
2018-04-29 07:30 | 21.37 | 12.93
2018-04-29 08:00 | 18.04 | 3.12
2018-04-29 08:30 | 22.6 | -13.45
2018-04-29 09:00 | 23.43 | -17.01
2018-04-29 09:30 | 25.95 | -24.16
2018-04-29 10:00 | 33.54 | -32.12
2018-04-29 10:30 | 26.28 | -24.58
2018-04-29 11:00 | 30.31 | -29.88
2018-04-29 11:30 | 24.58 | -23.76
2018-04-29 12:00 | 30.5 | -30.12
2018-04-29 12:30 | 28.64 | -28.5
2018-04-29 13:00 | 29.43 | -29.24
2018-04-29 13:30 | 21.86 | -21.44
2018-04-29 14:00 | 5.07 | -4.14
2018-04-29 14:30 | 15.64 | 15.58
2018-04-29 15:00 | 27.66 | 27.66
2018-04-29 15:30 | 29.34 | 29.33
2018-04-29 16:00 | 40.3 | 40.29
2018-04-29 16:30 | 63.22 | 63.21
2018-04-29 17:00 | 80.48 | 80.46
2018-04-29 17:30 | 103.55 | 103.54
2018-04-29 18:00 | 117.82 | 117.53
2018-04-29 18:30 | 137.08 | 136.79
2018-04-29 19:00 | 136.82 | 136.05
2018-04-29 19:30 | 146.03 | 144.83
2018-04-29 20:00 | 129.75 | 129.57
2018-04-29 20:30 | 118.22 | 117.94
2018-04-29 21:00 | 102.59 | 102.1
2018-04-29 21:30 | 97.13 | 96.28
2018-04-29 22:00 | 97.67 | 96.7
2018-04-29 22:30 | 126.79 | 125.95
2018-04-29 23:00 | 153.21 | 152.42
2018-04-29 23:30 | 103.65 | 102.19
2018-04-30 | 49.8 | 47.25
2018-04-30 00:30 | 25.18 | 20.73
2018-04-30 01:00 | 18.62 | 6.03
2018-04-30 01:30 | 18.39 | -0.47
2018-04-30 02:00 | 18.05 | -7.38
2018-04-30 02:30 | 16.28 | -0.95
2018-04-30 03:00 | 21.19 | 13.16
2018-04-30 03:30 | 23.86 | 16.96
2018-04-30 04:00 | 29.15 | 23.15
2018-04-30 04:30 | 33.22 | 27.42
2018-04-30 05:00 | 40.64 | 34.82
2018-04-30 05:30 | 62.8 | 58.39
2018-04-30 06:00 | 89.25 | 85.54
2018-04-30 06:30 | 106.37 | 103.41
2018-04-30 07:00 | 123.86 | 122.15
2018-04-30 07:30 | 138.12 | 137.81
2018-04-30 08:00 | 125.79 | 125.79
2018-04-30 08:30 | 89.3 | 89.29
2018-04-30 09:00 | 62.49 | 62.23
2018-04-30 09:30 | 52.85 | 51.93
2018-04-30 10:00 | 49.87 | 42.86
2018-04-30 10:30 | 70.07 | 63.68
2018-04-30 11:00 | 73.83 | 67.53
2018-04-30 11:30 | 80.28 | 74.42
2018-04-30 12:00 | 78.23 | 72.2
2018-04-30 12:30 | 73.98 | 68.13
2018-04-30 13:00 | 73.34 | 67.55
2018-04-30 13:30 | 88.72 | 84.13
2018-04-30 14:00 | 101.49 | 89.79
2018-04-30 14:30 | 116.46 | 101.21
2018-04-30 15:00 | 129.73 | 121.62
2018-04-30 15:30 | 132.89 | 128.12
2018-04-30 16:00 | 159.45 | 155.52
2018-04-30 16:30 | 168.27 | 164.77
2018-04-30 17:00 | 183.88 | 180.79
2018-04-30 17:30 | 189.39 | 186.32
2018-04-30 18:00 | 176.78 | 173.05
2018-04-30 18:30 | 170.22 | 166.65
2018-04-30 19:00 | 162.66 | 159.44
2018-04-30 19:30 | 146.7 | 144.2
2018-04-30 20:00 | 130.74 | 130.68
2018-04-30 20:30 | 119.23 | 119.04
2018-04-30 21:00 | 104.73 | 104.43
2018-04-30 21:30 | 101.76 | 101.2
2018-04-30 22:00 | 68.15 | 67.08
2018-04-30 22:30 | 60.71 | 59.29
2018-04-30 23:00 | 80.84 | 79.62
2018-04-30 23:30 | 45.94 | 43.83
2018-05-01 | 11.71 | 3.46
2018-05-01 00:30 | 9.07 | 0.85
2018-05-01 01:00 | 9.07 | -3.09
2018-05-01 01:30 | 9.34 | 3.22
2018-05-01 02:00 | 11.17 | -7.53
2018-05-01 02:30 | 15.56 | -13.18
2018-05-01 03:00 | 12.32 | -8.69
2018-05-01 03:30 | 10.14 | 2.9
2018-05-01 04:00 | 15.55 | 11.09
2018-05-01 04:30 | 23.73 | 20.36
2018-05-01 05:00 | 34.49 | 32.3
2018-05-01 05:30 | 31.05 | 28.92
2018-05-01 06:00 | 55.87 | 54.23
2018-05-01 06:30 | 69.88 | 68.6
2018-05-01 07:00 | 81.4 | 80.85
2018-05-01 07:30 | 93.08 | 92.89
2018-05-01 08:00 | 61.08 | 61.02
2018-05-01 08:30 | 40.55 | 40.55
2018-05-01 09:00 | 38.43 | 38.35
2018-05-01 09:30 | 34.27 | 33.84
2018-05-01 10:00 | 27.28 | 25.58
2018-05-01 10:30 | 23.7 | 18.97
2018-05-01 11:00 | 30.8 | 8.08
2018-05-01 11:30 | 34.88 | 18.12
2018-05-01 12:00 | 33.31 | 14.56
2018-05-01 12:30 | 31.57 | 8.68
2018-05-01 13:00 | 34.47 | -14.21
2018-05-01 13:30 | 52.54 | -22.86
2018-05-01 14:00 | 64.19 | 11.3
2018-05-01 14:30 | 75.42 | 46.44
2018-05-01 15:00 | 77.37 | 68.55
2018-05-01 15:30 | 86.9 | 79.76
2018-05-01 16:00 | 89.56 | 82.92
2018-05-01 16:30 | 104.18 | 98.73
2018-05-01 17:00 | 109.52 | 104.77
2018-05-01 17:30 | 105.22 | 99.51
2018-05-01 18:00 | 92.4 | 89.42
2018-05-01 18:30 | 86.41 | 84.73
2018-05-01 19:00 | 133.21 | 132.96
2018-05-01 19:30 | 140.1 | 139.87
2018-05-01 20:00 | 144.49 | 144.06
2018-05-01 20:30 | 129.28 | 128.52
2018-05-01 21:00 | 86.81 | 86.23
2018-05-01 21:30 | 72.61 | 71.86
2018-05-01 22:00 | 66.17 | 65.04
2018-05-01 22:30 | 64.9 | 63.5
2018-05-01 23:00 | 66.64 | 65.39
2018-05-01 23:30 | 18.96 | 15.65
2018-05-02 | 24.84 | -23.53
2018-05-02 00:30 | 30.31 | -29.41
2018-05-02 01:00 | 24.1 | -22.85
2018-05-02 01:30 | 25.94 | -24.8
2018-05-02 02:00 | 29.92 | -28.97
2018-05-02 02:30 | 27.97 | -26.89
2018-05-02 03:00 | 30.29 | -29.35
2018-05-02 03:30 | 31.58 | -30.51
2018-05-02 04:00 | 30.66 | -29.19
2018-05-02 04:30 | 19.02 | -15.76
2018-05-02 05:00 | 11.71 | -4.87
2018-05-02 05:30 | 32.46 | 30.37
2018-05-02 06:00 | 32.49 | 30.6
2018-05-02 06:30 | 12.9 | 12.81
2018-05-02 07:00 | 6.36 | -3.35
2018-05-02 07:30 | 25.42 | 24.43
2018-05-02 08:00 | 20.91 | 6.34
2018-05-02 08:30 | 22.9 | -3.06
2018-05-02 09:00 | 24.91 | 0.16
2018-05-02 09:30 | 37.35 | -25.47
2018-05-02 10:00 | 39.89 | -27.31
2018-05-02 10:30 | 36.17 | -21.77
2018-05-02 11:00 | 28.82 | 1.3
2018-05-02 11:30 | 39.89 | -26.61
2018-05-02 12:00 | 35.62 | -19.81
2018-05-02 12:30 | 42.12 | -29.42
2018-05-02 13:00 | 30.9 | -10.76
2018-05-02 13:30 | 38.48 | -22.95
2018-05-02 14:00 | 35.22 | 21.36
2018-05-02 14:30 | 31.64 | 16.71
2018-05-02 15:00 | 27.16 | 2.42
2018-05-02 15:30 | 26.56 | -3.02
2018-05-02 16:00 | 26.91 | -6.55
2018-05-02 16:30 | 25.23 | -4.99
2018-05-02 17:00 | 25.98 | -7.8
2018-05-02 17:30 | 25.72 | -3.34
2018-05-02 18:00 | 29.9 | -4.44
2018-05-02 18:30 | 28.06 | -3.73
2018-05-02 19:00 | 26.62 | 8.57
2018-05-02 19:30 | 36.23 | 32.23
2018-05-02 20:00 | 89.62 | 89.61
2018-05-02 20:30 | 98.46 | 98.42
2018-05-02 21:00 | 87.03 | 86.86
2018-05-02 21:30 | 70.03 | 69.64
2018-05-02 22:00 | 12.44 | 9.62
2018-05-02 22:30 | 71.72 | 70.69
2018-05-02 23:00 | 84.33 | 82.95
2018-05-02 23:30 | 16.96 | -12.67
2018-05-03 | 62.94 | -62.91
2018-05-03 00:30 | 68.96 | -68.95
2018-05-03 01:00 | 72.31 | -72.31
2018-05-03 01:30 | 71.52 | -71.52
2018-05-03 02:00 | 70.65 | -70.64
2018-05-03 02:30 | 66.49 | -66.48
2018-05-03 03:00 | 66.47 | -66.45
2018-05-03 03:30 | 60.18 | -59.98
2018-05-03 04:00 | 65.81 | -65.61
2018-05-03 04:30 | 55.79 | -55.38
2018-05-03 05:00 | 57.24 | -56.86
2018-05-03 05:30 | 15.76 | -12.61
2018-05-03 06:00 | 24.24 | 21.95
2018-05-03 06:30 | 96.29 | 95.81
2018-05-03 07:00 | 116.11 | 115.94
2018-05-03 07:30 | 117.95 | 117.91
2018-05-03 08:00 | 97.33 | 97.32
2018-05-03 08:30 | 53 | 35.01
2018-05-03 09:00 | 63.18 | 8.98
2018-05-03 09:30 | 65.75 | -13.28
2018-05-03 10:00 | 74.58 | -28.77
2018-05-03 10:30 | 110.47 | 89.68
2018-05-03 11:00 | 124.19 | 106.26
2018-05-03 11:30 | 118.06 | 98.58
2018-05-03 12:00 | 78.59 | 41
2018-05-03 12:30 | 71.9 | 15.25
2018-05-03 13:00 | 80.58 | 39.29
2018-05-03 13:30 | 92.59 | 60.64
2018-05-03 14:00 | 91.23 | 58.32
2018-05-03 14:30 | 128.12 | 107.86
2018-05-03 15:00 | 128.12 | 109.83
2018-05-03 15:30 | 116.91 | 98.06
2018-05-03 16:00 | 114.24 | 95.84
2018-05-03 16:30 | 108 | 89.66
2018-05-03 17:00 | 108.3 | 90.76
2018-05-03 17:30 | 98.87 | 77.86
2018-05-03 18:00 | 85.61 | 72.07
2018-05-03 18:30 | 69.54 | 66.24
2018-05-03 19:00 | 73.98 | 71.9
2018-05-03 19:30 | 80.81 | 80.79
2018-05-03 20:00 | 69.06 | 68.8
2018-05-03 20:30 | 110.69 | 110.64
2018-05-03 21:00 | 168.17 | 168.17
2018-05-03 21:30 | 152.22 | 152.18
2018-05-03 22:00 | 136.41 | 136.15
2018-05-03 22:30 | 146.57 | 146.12
2018-05-03 23:00 | 165.44 | 165
2018-05-03 23:30 | 128.36 | 127.74
2018-05-04 | 89.62 | 88.99
2018-05-04 00:30 | 80.16 | 79.46
2018-05-04 01:00 | 59.65 | 58.76
2018-05-04 01:30 | 61.05 | 58.76
2018-05-04 02:00 | 60.03 | 56.23
2018-05-04 02:30 | 67.98 | 64.67
2018-05-04 03:00 | 76.06 | 73.11
2018-05-04 03:30 | 78.03 | 75.09
2018-05-04 04:00 | 78.55 | 75.52
2018-05-04 04:30 | 79.17 | 75.91
2018-05-04 05:00 | 81.66 | 78.31
2018-05-04 05:30 | 101.03 | 97.87
2018-05-04 06:00 | 137.95 | 135.54
2018-05-04 06:30 | 149.11 | 147.01
2018-05-04 07:00 | 133.11 | 131.3
2018-05-04 07:30 | 150.03 | 149.86
2018-05-04 08:00 | 162.11 | 161.21
2018-05-04 08:30 | 169.98 | 160.92
2018-05-04 09:00 | 169.78 | 155.55
2018-05-04 09:30 | 162.33 | 146.55
2018-05-04 10:00 | 164.18 | 147.63
2018-05-04 10:30 | 161.06 | 143.33
2018-05-04 11:00 | 156.41 | 137.68
2018-05-04 11:30 | 136.86 | 114.54
2018-05-04 12:00 | 136.21 | 113.42
2018-05-04 12:30 | 133.78 | 110.85
2018-05-04 13:00 | 145.54 | 125.08
2018-05-04 13:30 | 162.57 | 144.16
2018-05-04 14:00 | 168.28 | 150.9
2018-05-04 14:30 | 172.02 | 155.44
2018-05-04 15:00 | 173.64 | 157.5
2018-05-04 15:30 | 176.93 | 161.76
2018-05-04 16:00 | 176.74 | 167.24
2018-05-04 16:30 | 173.12 | 166.34
2018-05-04 17:00 | 173.76 | 168.89
2018-05-04 17:30 | 169.16 | 167.15
2018-05-04 18:00 | 195.22 | 193.63
2018-05-04 18:30 | 216.81 | 216.11
2018-05-04 19:00 | 210 | 209.99
2018-05-04 19:30 | 191.14 | 191.14
2018-05-04 20:00 | 181.42 | 181.42
2018-05-04 20:30 | 158.5 | 157.96
2018-05-04 21:00 | 133.57 | 132
2018-05-04 21:30 | 129.11 | 127.19
2018-05-04 22:00 | 112.97 | 110.66
2018-05-04 22:30 | 128.49 | 126.42
2018-05-04 23:00 | 144.52 | 142.63
2018-05-04 23:30 | 106.6 | 104
2018-05-05 | 82.62 | 79.59
2018-05-05 00:30 | 75.23 | 72.54
2018-05-05 01:00 | 63.5 | 60.65
2018-05-05 01:30 | 49.44 | 46.31
2018-05-05 02:00 | 34.62 | 30.5
2018-05-05 02:30 | 31.28 | 26.79
2018-05-05 03:00 | 40.17 | 36.97
2018-05-05 03:30 | 39.12 | 35.84
2018-05-05 04:00 | 31.11 | 27.22
2018-05-05 04:30 | 27.4 | 22.79
2018-05-05 05:00 | 33.9 | 29.93
2018-05-05 05:30 | 45.09 | 41.65
2018-05-05 06:00 | 51.72 | 47.42
2018-05-05 06:30 | 60.42 | 56.59
2018-05-05 07:00 | 75.85 | 72.41
2018-05-05 07:30 | 68.76 | 64.26
2018-05-05 08:00 | 56.48 | 51.54
2018-05-05 08:30 | 59.55 | 59.22
2018-05-05 09:00 | 49.49 | 49.49
2018-05-05 09:30 | 42.89 | 42.73
2018-05-05 10:00 | 36.32 | 36.12
2018-05-05 10:30 | 35.5 | 35.23
2018-05-05 11:00 | 24.71 | 24.14
2018-05-05 11:30 | 24.63 | 24.19
2018-05-05 12:00 | 41.86 | 41.65
2018-05-05 12:30 | 41.5 | 41.39
2018-05-05 13:00 | 48.34 | 48.27
2018-05-05 13:30 | 52.76 | 52.73
2018-05-05 14:00 | 76.07 | 76.06
2018-05-05 14:30 | 85.82 | 85.81
2018-05-05 15:00 | 96.42 | 96.42
2018-05-05 15:30 | 107 | 107
2018-05-05 16:00 | 109.31 | 109.31
2018-05-05 16:30 | 126.2 | 126.2
2018-05-05 17:00 | 135.9 | 135.9
2018-05-05 17:30 | 140.38 | 140.34
2018-05-05 18:00 | 146.17 | 145.62
2018-05-05 18:30 | 136.65 | 136.1
2018-05-05 19:00 | 142.23 | 141.67
2018-05-05 19:30 | 126.65 | 125.3
2018-05-05 20:00 | 108.38 | 108.01
2018-05-05 20:30 | 107.57 | 107.31
2018-05-05 21:00 | 94.44 | 94.17
2018-05-05 21:30 | 80 | 79.48
2018-05-05 22:00 | 65.06 | 64.22
2018-05-05 22:30 | 87.55 | 86.77
2018-05-05 23:00 | 102.9 | 102.12
2018-05-05 23:30 | 77.42 | 76.27
2018-05-06 | 56.72 | 55.52
2018-05-06 00:30 | 28.84 | 26.93
2018-05-06 01:00 | 33.34 | 31.67
2018-05-06 01:30 | 28.21 | 24.32
2018-05-06 02:00 | 32.97 | 29
2018-05-06 02:30 | 30.58 | 26.62
2018-05-06 03:00 | 21.88 | 16.21
2018-05-06 03:30 | 13.78 | 2.11
2018-05-06 04:00 | 14.17 | -3.36
2018-05-06 04:30 | 13.76 | 0.68
2018-05-06 05:00 | 18.42 | 10.74
2018-05-06 05:30 | 31.08 | 26.21
2018-05-06 06:00 | 37.1 | 32.36
2018-05-06 06:30 | 42.92 | 39.62
2018-05-06 07:00 | 38.28 | 34.49
2018-05-06 07:30 | 43.48 | 38.76
2018-05-06 08:00 | 27.86 | 18.67
2018-05-06 08:30 | 27.21 | 14.99
2018-05-06 09:00 | 24.36 | 9.19
2018-05-06 09:30 | 19.24 | -0.08
2018-05-06 10:00 | 11.08 | -11.08
2018-05-06 10:30 | 8.51 | -8.41
2018-05-06 11:00 | 5.27 | -4.93
2018-05-06 11:30 | 5.8 | 5.76
2018-05-06 12:00 | 9.08 | 9.05
2018-05-06 12:30 | 39.41 | 39.41
2018-05-06 13:00 | 42.3 | 42.3
2018-05-06 13:30 | 39.52 | 39.52
2018-05-06 14:00 | 29.9 | 29.89
2018-05-06 14:30 | 39.12 | 39.11
2018-05-06 15:00 | 48.95 | 48.95
2018-05-06 15:30 | 48.09 | 48.09
2018-05-06 16:00 | 69.46 | 69.46
2018-05-06 16:30 | 73.21 | 73.2
2018-05-06 17:00 | 85.12 | 85.11
2018-05-06 17:30 | 108.8 | 108.8
2018-05-06 18:00 | 96.39 | 94.33
2018-05-06 18:30 | 100.3 | 97.77
2018-05-06 19:00 | 112.23 | 110.33
2018-05-06 19:30 | 122.71 | 121.59
2018-05-06 20:00 | 113.43 | 112.51
2018-05-06 20:30 | 96.19 | 95.39
2018-05-06 21:00 | 85.08 | 84.37
2018-05-06 21:30 | 77.35 | 76.82
2018-05-06 22:00 | 78.51 | 78.08
2018-05-06 22:30 | 120.88 | 120.79
2018-05-06 23:00 | 142.88 | 141.97
2018-05-06 23:30 | 100.54 | 99.21
2018-05-07 | 61 | 59.26
2018-05-07 00:30 | 47.42 | 44.12
2018-05-07 01:00 | 43.37 | 37.11
2018-05-07 01:30 | 40.09 | 36.51
2018-05-07 02:00 | 51.38 | 48.89
2018-05-07 02:30 | 64.45 | 62
2018-05-07 03:00 | 77.25 | 74.56
2018-05-07 03:30 | 80.78 | 78.69
2018-05-07 04:00 | 79.73 | 77.82
2018-05-07 04:30 | 71.65 | 71.57
2018-05-07 05:00 | 84.59 | 82.37
2018-05-07 05:30 | 67.6 | 63.95
2018-05-07 06:00 | 35.39 | 28.29
2018-05-07 06:30 | 23.15 | 14.57
2018-05-07 07:00 | 27.02 | 21.01
2018-05-07 07:30 | 30.54 | 24.57
2018-05-07 08:00 | 24.27 | 18.45
2018-05-07 08:30 | 29.43 | 23.64
2018-05-07 09:00 | 37.67 | 32.68
2018-05-07 09:30 | 37.33 | 34.3
2018-05-07 10:00 | 43.11 | 41.89
2018-05-07 10:30 | 29.19 | 28.09
2018-05-07 11:00 | 20.62 | 19.08
2018-05-07 11:30 | 26.54 | 24.64
2018-05-07 12:00 | 41.42 | 40.1
2018-05-07 12:30 | 41.66 | 40.35
2018-05-07 13:00 | 43.05 | 41.75
2018-05-07 13:30 | 58.9 | 58.13
2018-05-07 14:00 | 67.61 | 66.24
2018-05-07 14:30 | 73.51 | 71.85
2018-05-07 15:00 | 70.25 | 68.51
2018-05-07 15:30 | 73.51 | 71.71
2018-05-07 16:00 | 65.09 | 63.08
2018-05-07 16:30 | 68.21 | 66.34
2018-05-07 17:00 | 74.21 | 72.73
2018-05-07 17:30 | 89.58 | 89.06
2018-05-07 18:00 | 105.51 | 105.19
2018-05-07 18:30 | 92.41 | 91.95
2018-05-07 19:00 | 89.81 | 89.25
2018-05-07 19:30 | 65.81 | 64.8
2018-05-07 20:00 | 57.82 | 56.31
2018-05-07 20:30 | 49.79 | 48.19
2018-05-07 21:00 | 25.96 | 25.12
2018-05-07 21:30 | 19.01 | 17.36
2018-05-07 22:00 | 8.94 | -4.95
2018-05-07 22:30 | 20.4 | 18.34
2018-05-07 23:00 | 63.44 | 62.58
2018-05-07 23:30 | 42.35 | 40.88
2018-05-08 | 9.43 | -3.03
2018-05-08 00:30 | 20.38 | -18.89
2018-05-08 01:00 | 41.82 | -41.32
2018-05-08 01:30 | 45.3 | -44.87
2018-05-08 02:00 | 42.26 | -41.68
2018-05-08 02:30 | 41.41 | -40.87
2018-05-08 03:00 | 44.1 | -43.69
2018-05-08 03:30 | 41.52 | -41.01
2018-05-08 04:00 | 46.92 | -46.44
2018-05-08 04:30 | 35.85 | -34.96
2018-05-08 05:00 | 23.89 | -22.72
2018-05-08 05:30 | 13.06 | 9.29
2018-05-08 06:00 | 41.78 | 40.73
2018-05-08 06:30 | 53.5 | 52.91
2018-05-08 07:00 | 64.99 | 64.78
2018-05-08 07:30 | 75.9 | 75.86
2018-05-08 08:00 | 60.91 | 60.48
2018-05-08 08:30 | 50.8 | 50.56
2018-05-08 09:00 | 52.79 | 52.63
2018-05-08 09:30 | 46.25 | 46.25
2018-05-08 10:00 | 34.16 | 34.16
2018-05-08 10:30 | 24.84 | 24.84
2018-05-08 11:00 | 40 | 39.92
2018-05-08 11:30 | 50 | 49.88
2018-05-08 12:00 | 80.83 | 80.7
2018-05-08 12:30 | 61.58 | 61.52
2018-05-08 13:00 | 52.25 | 52.18
2018-05-08 13:30 | 61.1 | 61.02
2018-05-08 14:00 | 51.35 | 51.28
2018-05-08 14:30 | 66.64 | 66.51
2018-05-08 15:00 | 74.82 | 74.67
2018-05-08 15:30 | 71.43 | 71.25
2018-05-08 16:00 | 66.5 | 66.37
2018-05-08 16:30 | 64.99 | 64.86
2018-05-08 17:00 | 61.58 | 61.5
2018-05-08 17:30 | 56.46 | 56.38
2018-05-08 18:00 | 47.04 | 41.44
2018-05-08 18:30 | 27.25 | 25.34
2018-05-08 19:00 | 19.69 | 17.81
2018-05-08 19:30 | 16.02 | 15.1
2018-05-08 20:00 | 12.35 | 12.28
2018-05-08 20:30 | 9.52 | 9.52
2018-05-08 21:00 | 67.31 | 67.01
2018-05-08 21:30 | 47.51 | 46.44
2018-05-08 22:00 | 19.42 | 17.23
2018-05-08 22:30 | 19.2 | 16.65
2018-05-08 23:00 | 42.15 | 40.24
2018-05-08 23:30 | 14.82 | 5.62
2018-05-09 | 20.54 | -18.4
2018-05-09 00:30 | 39.81 | -39.57
2018-05-09 01:00 | 58.43 | -58.42
2018-05-09 01:30 | 53.96 | -53.95
2018-05-09 02:00 | 39.04 | -38.94
2018-05-09 02:30 | 37.8 | -37.74
2018-05-09 03:00 | 35.57 | -35.51
2018-05-09 03:30 | 38.07 | -38.03
2018-05-09 04:00 | 45.04 | -45.01
2018-05-09 04:30 | 33.45 | -33.06
2018-05-09 05:00 | 18.88 | -17.04
2018-05-09 05:30 | 15.77 | 3.87
2018-05-09 06:00 | 29.81 | 23.87
2018-05-09 06:30 | 36.7 | 32.62
2018-05-09 07:00 | 56.94 | 54.61
2018-05-09 07:30 | 67.35 | 67.06
2018-05-09 08:00 | 72.5 | 72.32
2018-05-09 08:30 | 68.24 | 67.8
2018-05-09 09:00 | 61.56 | 61.35
2018-05-09 09:30 | 50.43 | 50.31
2018-05-09 10:00 | 49.94 | 49.85
2018-05-09 10:30 | 53.89 | 53.78
2018-05-09 11:00 | 50.89 | 50.52
2018-05-09 11:30 | 48.63 | 48.27
2018-05-09 12:00 | 49.6 | 49.31
2018-05-09 12:30 | 56.86 | 56.45
2018-05-09 13:00 | 63 | 62.68
2018-05-09 13:30 | 65.79 | 65.53
2018-05-09 14:00 | 71.48 | 71.17
2018-05-09 14:30 | 70.74 | 70.21
2018-05-09 15:00 | 77.76 | 77.19
2018-05-09 15:30 | 91.29 | 90.68
2018-05-09 16:00 | 101.23 | 100.58
2018-05-09 16:30 | 119.19 | 118.45
2018-05-09 17:00 | 134.7 | 133.94
2018-05-09 17:30 | 109.14 | 108.32
2018-05-09 18:00 | 109.8 | 109.27
2018-05-09 18:30 | 132.01 | 131.4
2018-05-09 19:00 | 124.91 | 124.21
2018-05-09 19:30 | 99.08 | 97.85
2018-05-09 20:00 | 93.15 | 91.62
2018-05-09 20:30 | 116.39 | 115.27
2018-05-09 21:00 | 100.91 | 97.7
2018-05-09 21:30 | 79.17 | 72.66
2018-05-09 22:00 | 62.08 | 52.89
2018-05-09 22:30 | 85.44 | 78.73
2018-05-09 23:00 | 95.67 | 89.81
2018-05-09 23:30 | 56.01 | 46.9
2018-05-10 | 33.48 | 19.32
2018-05-10 00:30 | 24.63 | 0.89
2018-05-10 01:00 | 23.45 | -2.71
2018-05-10 01:30 | 22.94 | 1.41
2018-05-10 02:00 | 22.65 | -0.94
2018-05-10 02:30 | 23.01 | -1.44
2018-05-10 03:00 | 22.56 | -3.96
2018-05-10 03:30 | 16.86 | 12.85
2018-05-10 04:00 | 20.14 | 18.42
2018-05-10 04:30 | 21.04 | 18.79
2018-05-10 05:00 | 22.11 | 19.13
2018-05-10 05:30 | 33.35 | 29.27
2018-05-10 06:00 | 57.38 | 50.65
2018-05-10 06:30 | 70.21 | 63.19
2018-05-10 07:00 | 72.08 | 66.13
2018-05-10 07:30 | 90.49 | 86.69
2018-05-10 08:00 | 74.94 | 71.38
2018-05-10 08:30 | 68.41 | 65.82
2018-05-10 09:00 | 63.62 | 63.48
2018-05-10 09:30 | 65.6 | 65.01
2018-05-10 10:00 | 59.73 | 59.18
2018-05-10 10:30 | 68.29 | 67.68
2018-05-10 11:00 | 79.82 | 79.34
2018-05-10 11:30 | 88.18 | 87.39
2018-05-10 12:00 | 88.98 | 88.55
2018-05-10 12:30 | 85.71 | 85.31
2018-05-10 13:00 | 79.64 | 79.21
2018-05-10 13:30 | 77.67 | 77.63
2018-05-10 14:00 | 81.59 | 81.06
2018-05-10 14:30 | 87.1 | 86.63
2018-05-10 15:00 | 93.22 | 92.73
2018-05-10 15:30 | 98.33 | 97.81
2018-05-10 16:00 | 114.59 | 114.03
2018-05-10 16:30 | 120.78 | 120.11
2018-05-10 17:00 | 137.78 | 137.14
2018-05-10 17:30 | 142.3 | 142.12
2018-05-10 18:00 | 131.45 | 129.55
2018-05-10 18:30 | 129.41 | 129.41
2018-05-10 19:00 | 131.41 | 131.33
2018-05-10 19:30 | 125.76 | 125.48
2018-05-10 20:00 | 137.44 | 137.02
2018-05-10 20:30 | 138.56 | 138.56
2018-05-10 21:00 | 118.92 | 118.87
2018-05-10 21:30 | 94.47 | 91.24
2018-05-10 22:00 | 77.03 | 70.74
2018-05-10 22:30 | 71.82 | 64.94
2018-05-10 23:00 | 88.25 | 82.56
2018-05-10 23:30 | 75.1 | 68.96
2018-05-11 | 45.19 | 36.82
2018-05-11 00:30 | 23.74 | 6.72
2018-05-11 01:00 | 19.67 | -13.76
2018-05-11 01:30 | 25.63 | -21.38
2018-05-11 02:00 | 25.23 | -21.35
2018-05-11 02:30 | 27.22 | -24.31
2018-05-11 03:00 | 21.71 | -17.34
2018-05-11 03:30 | 13.84 | -3.51
2018-05-11 04:00 | 13.88 | -4.64
2018-05-11 04:30 | 14.53 | 1.83
2018-05-11 05:00 | 24.45 | 17.38
2018-05-11 05:30 | 33.07 | 26.49
2018-05-11 06:00 | 25.38 | 14.73
2018-05-11 06:30 | 42.41 | 36.2
2018-05-11 07:00 | 57.94 | 53.56
2018-05-11 07:30 | 69.89 | 66.9
2018-05-11 08:00 | 34 | 31.95
2018-05-11 08:30 | 11.56 | 10.16
2018-05-11 09:00 | 8.69 | 2.99
2018-05-11 09:30 | 19.97 | -17.22
2018-05-11 10:00 | 29.08 | -26.03
2018-05-11 10:30 | 36.29 | -32.9
2018-05-11 11:00 | 41.75 | -38.32
2018-05-11 11:30 | 41.23 | -37.9
2018-05-11 12:00 | 38.35 | -35.2
2018-05-11 12:30 | 27.22 | -23.71
2018-05-11 13:00 | 19.6 | -15.08
2018-05-11 13:30 | 17.66 | -12.09
2018-05-11 14:00 | 14.55 | -7.61
2018-05-11 14:30 | 11.25 | 7.11
2018-05-11 15:00 | 21.07 | 20.32
2018-05-11 15:30 | 18.27 | 17.61
2018-05-11 16:00 | 26.68 | 26.44
2018-05-11 16:30 | 32.83 | 32.72
2018-05-11 17:00 | 33.85 | 33.74
2018-05-11 17:30 | 41.71 | 41.53
2018-05-11 18:00 | 63.34 | 62.63
2018-05-11 18:30 | 61.14 | 59.46
2018-05-11 19:00 | 69.39 | 67.43
2018-05-11 19:30 | 83.66 | 82.63
2018-05-11 20:00 | 67.38 | 65.98
2018-05-11 20:30 | 69.74 | 68.96
2018-05-11 21:00 | 54.7 | 54.48
2018-05-11 21:30 | 44.13 | 43.48
2018-05-11 22:00 | 26.14 | 24.33
2018-05-11 22:30 | 30.14 | 28.02
2018-05-11 23:00 | 47.27 | 45.55
2018-05-11 23:30 | 33.49 | 30.94
2018-05-12 | 17.43 | 12.29
2018-05-12 00:30 | 12.83 | -6.52
2018-05-12 01:00 | 19.43 | -16.33
2018-05-12 01:30 | 20.12 | -16.77
2018-05-12 02:00 | 15.52 | -11.33
2018-05-12 02:30 | 18.37 | -15.47
2018-05-12 03:00 | 16.18 | -13.22
2018-05-12 03:30 | 11 | -5.08
2018-05-12 04:00 | 10.72 | 0.92
2018-05-12 04:30 | 18.63 | 13.9
2018-05-12 05:00 | 26.76 | 22.78
2018-05-12 05:30 | 26.62 | 21.5
2018-05-12 06:00 | 28.26 | 22.61
2018-05-12 06:30 | 30.06 | 24.65
2018-05-12 07:00 | 28.71 | 21.67
2018-05-12 07:30 | 25.42 | 15.82
2018-05-12 08:00 | 18.87 | 9.35
2018-05-12 08:30 | 15.73 | 1.47
2018-05-12 09:00 | 15.95 | -8.73
2018-05-12 09:30 | 33.52 | -32.69
2018-05-12 10:00 | 45.09 | -44.95
2018-05-12 10:30 | 44.67 | -44.34
2018-05-12 11:00 | 48.18 | -47.9
2018-05-12 11:30 | 51.17 | -50.85
2018-05-12 12:00 | 52.78 | -52.37
2018-05-12 12:30 | 54.77 | -54.32
2018-05-12 13:00 | 53.17 | -52.83
2018-05-12 13:30 | 48.73 | -48.34
2018-05-12 14:00 | 41.01 | -40.75
2018-05-12 14:30 | 35.87 | -35.66
2018-05-12 15:00 | 31.07 | -30.95
2018-05-12 15:30 | 25.29 | -25.22
2018-05-12 16:00 | 18.27 | -18.27
2018-05-12 16:30 | 5.62 | 5.24
2018-05-12 17:00 | 21.25 | 21.18
2018-05-12 17:30 | 36.95 | 36.85
2018-05-12 18:00 | 32.43 | 32.42
2018-05-12 18:30 | 30.13 | 30.13
2018-05-12 19:00 | 53.17 | 53.08
2018-05-12 19:30 | 56.31 | 55.94
2018-05-12 20:00 | 62.68 | 62.09
2018-05-12 20:30 | 57.49 | 56.37
2018-05-12 21:00 | 56.56 | 54.57
2018-05-12 21:30 | 49.44 | 46.65
2018-05-12 22:00 | 37.73 | 33.67
2018-05-12 22:30 | 56.4 | 53.19
2018-05-12 23:00 | 54.56 | 51.23
2018-05-12 23:30 | 20.65 | 15.54
2018-05-13 | 17.67 | -15.28
2018-05-13 00:30 | 20.87 | -19.28
2018-05-13 01:00 | 23.91 | -22.54
2018-05-13 01:30 | 27.7 | -25.86
2018-05-13 02:00 | 27.99 | -26.33
2018-05-13 02:30 | 32.72 | -31.51
2018-05-13 03:00 | 34.2 | -33.08
2018-05-13 03:30 | 39.73 | -38.93
2018-05-13 04:00 | 32.32 | -31.06
2018-05-13 04:30 | 28.36 | -26.7
2018-05-13 05:00 | 25.13 | -22.73
2018-05-13 05:30 | 22.54 | -19.38
2018-05-13 06:00 | 19.84 | -14.79
2018-05-13 06:30 | 13.99 | -3.46
2018-05-13 07:00 | 22.12 | 15.1
2018-05-13 07:30 | 28.85 | 21.74
2018-05-13 08:00 | 17.87 | 0.33
2018-05-13 08:30 | 32.38 | -31.22
2018-05-13 09:00 | 31.54 | -31.11
2018-05-13 09:30 | 25.98 | -25.61
2018-05-13 10:00 | 31.24 | -31.1
2018-05-13 10:30 | 46.28 | -46.26
2018-05-13 11:00 | 49.37 | -49.37
2018-05-13 11:30 | 46.54 | -46.54
2018-05-13 12:00 | 52.87 | -52.86
2018-05-13 12:30 | 54.23 | -54.23
2018-05-13 13:00 | 50.45 | -50.45
2018-05-13 13:30 | 41.44 | -41.44
2018-05-13 14:00 | 40.74 | -40.73
2018-05-13 14:30 | 35.43 | -35.41
2018-05-13 15:00 | 22.42 | -22.31
2018-05-13 15:30 | 12.61 | -12.21
2018-05-13 16:00 | 10.39 | 9.38
2018-05-13 16:30 | 32.55 | 32.01
2018-05-13 17:00 | 32.44 | 32.12
2018-05-13 17:30 | 34.59 | 34.56
2018-05-13 18:00 | 20.95 | 20.67
2018-05-13 18:30 | 23.8 | 23.46
2018-05-13 19:00 | 29.64 | 29.1
2018-05-13 19:30 | 39.81 | 38.83
2018-05-13 20:00 | 20.46 | 18.36
2018-05-13 20:30 | 16.79 | 13.94
2018-05-13 21:00 | 13.6 | 11.63
2018-05-13 21:30 | 22.97 | 21.15
2018-05-13 22:00 | 19.44 | 17.16
2018-05-13 22:30 | 27.87 | 26.08
2018-05-13 23:00 | 45.01 | 43.77
2018-05-13 23:30 | 20.92 | 18.33
2018-05-14 | 9.41 | -1.3
2018-05-14 00:30 | 18.18 | -16.1
2018-05-14 01:00 | 23.98 | -22.01
2018-05-14 01:30 | 34.4 | -33.18
2018-05-14 02:00 | 38.32 | -37.85
2018-05-14 02:30 | 44.92 | -44.67
2018-05-14 03:00 | 44.04 | -43.8
2018-05-14 03:30 | 43.92 | -43.71
2018-05-14 04:00 | 39.52 | -39.16
2018-05-14 04:30 | 32.33 | -31.49
2018-05-14 05:00 | 22.62 | -19.88
2018-05-14 05:30 | 22.2 | -16.49
2018-05-14 06:00 | 26.23 | 16.82
2018-05-14 06:30 | 40.18 | 34.6
2018-05-14 07:00 | 29.64 | 27.57
2018-05-14 07:30 | 39.88 | 39.81
2018-05-14 08:00 | 24.11 | 24
2018-05-14 08:30 | 15.87 | 15.87
2018-05-14 09:00 | 5.31 | -4.94
2018-05-14 09:30 | 10.59 | -10.4
2018-05-14 10:00 | 19.43 | -19.19
2018-05-14 10:30 | 20.7 | -20.58
2018-05-14 11:00 | 28.7 | -28.64
2018-05-14 11:30 | 34.98 | -34.8
2018-05-14 12:00 | 9.08 | -9.08
2018-05-14 12:30 | 13.51 | -13.48
2018-05-14 13:00 | 25.83 | -25.8
2018-05-14 13:30 | 24.33 | -24.3
2018-05-14 14:00 | 10.34 | -10.31
2018-05-14 14:30 | 4.58 | -4.58
2018-05-14 15:00 | 4.48 | -4.4
2018-05-14 15:30 | 2.28 | -2.18
2018-05-14 16:00 | 28 | 27.69
2018-05-14 16:30 | 45.62 | 45.17
2018-05-14 17:00 | 63.32 | 63.03
2018-05-14 17:30 | 76.23 | 76.19
2018-05-14 18:00 | 58.88 | 58.81
2018-05-14 18:30 | 51.14 | 51.05
2018-05-14 19:00 | 35.3 | 35.22
2018-05-14 19:30 | 35.27 | 35.26
2018-05-14 20:00 | 45.99 | 45.96
2018-05-14 20:30 | 33.6 | 33.59
2018-05-14 21:00 | 18.7 | 18.44
2018-05-14 21:30 | 20.09 | -19.83
2018-05-14 22:00 | 25.96 | -25.34
2018-05-14 22:30 | 17.59 | -16.07
2018-05-14 23:00 | 10.23 | -5.63
2018-05-14 23:30 | 31.54 | -30.47
2018-05-15 | 46.76 | -46.34
2018-05-15 00:30 | 57.14 | -56.94
2018-05-15 01:00 | 56.15 | -55.93
2018-05-15 01:30 | 57.64 | -57.5
2018-05-15 02:00 | 56.48 | -56.39
2018-05-15 02:30 | 60.1 | -60.01
2018-05-15 03:00 | 61.12 | -61
2018-05-15 03:30 | 58.91 | -58.73
2018-05-15 04:00 | 55.18 | -54.87
2018-05-15 04:30 | 42.16 | -40.88
2018-05-15 05:00 | 25.54 | -22.83
2018-05-15 05:30 | 14.07 | -5.06
2018-05-15 06:00 | 18.65 | 13.04
2018-05-15 06:30 | 12.86 | 8
2018-05-15 07:00 | 4.81 | 1.16
2018-05-15 07:30 | 23.84 | 23.84
2018-05-15 08:00 | 12.23 | 11.38
2018-05-15 08:30 | 26.87 | -6.05
2018-05-15 09:00 | 27.59 | -1.24
2018-05-15 09:30 | 29.31 | 6.05
2018-05-15 10:00 | 28.69 | -3.85
2018-05-15 10:30 | 29.02 | -9.31
2018-05-15 11:00 | 31.73 | -12.63
2018-05-15 11:30 | 34.87 | -18.23
2018-05-15 12:00 | 31.82 | -12.26
2018-05-15 12:30 | 31.72 | -11.06
2018-05-15 13:00 | 29.31 | -1.25
2018-05-15 13:30 | 29.92 | -0.55
2018-05-15 14:00 | 31.4 | 10.84
2018-05-15 14:30 | 35.46 | 19.53
2018-05-15 15:00 | 30.49 | 5.8
2018-05-15 15:30 | 33.49 | 5.17
2018-05-15 16:00 | 66.54 | 29.01
2018-05-15 16:30 | 70.01 | 38.9
2018-05-15 17:00 | 81.95 | 58.52
2018-05-15 17:30 | 91.22 | 69.13
2018-05-15 18:00 | 94.65 | 72.78
2018-05-15 18:30 | 72.49 | 43.15
2018-05-15 19:00 | 74.05 | 48.77
2018-05-15 19:30 | 67.41 | 41.02
2018-05-15 20:00 | 52.09 | 39.07
2018-05-15 20:30 | 33.12 | 29.95
2018-05-15 21:00 | 35.41 | 32.15
2018-05-15 21:30 | 21.17 | 15.81
2018-05-15 22:00 | 23.8 | -19.19
2018-05-15 22:30 | 11.73 | 0.19
2018-05-15 23:00 | 13.59 | 8.16
2018-05-15 23:30 | 17.89 | -13.87
2018-05-16 | 50.1 | -48.1
2018-05-16 00:30 | 52.65 | -50.63
2018-05-16 01:00 | 59.58 | -57.77
2018-05-16 01:30 | 57.76 | -57.72
2018-05-16 02:00 | 56.44 | -56.13
2018-05-16 02:30 | 46.87 | -46.33
2018-05-16 03:00 | 32.73 | -31.13
2018-05-16 03:30 | 33.76 | -32.15
2018-05-16 04:00 | 35.44 | -33.82
2018-05-16 04:30 | 26.77 | -23.78
2018-05-16 05:00 | 14.71 | -8.1
2018-05-16 05:30 | 25.18 | 21.55
2018-05-16 06:00 | 32.76 | 30.04
2018-05-16 06:30 | 22.64 | 20.43
2018-05-16 07:00 | 63.85 | 63.44
2018-05-16 07:30 | 111.88 | 111.84
2018-05-16 08:00 | 112.27 | 112.27
2018-05-16 08:30 | 102.89 | 102.89
2018-05-16 09:00 | 93.69 | 93.68
2018-05-16 09:30 | 79.04 | 79
2018-05-16 10:00 | 69.09 | 69
2018-05-16 10:30 | 63.85 | 63.72
2018-05-16 11:00 | 52.81 | 52.54
2018-05-16 11:30 | 50.7 | 50.42
2018-05-16 12:00 | 57.15 | 56.88
2018-05-16 12:30 | 66.48 | 66.3
2018-05-16 13:00 | 57.91 | 57.7
2018-05-16 13:30 | 60.28 | 60.04
2018-05-16 14:00 | 64.74 | 64.48
2018-05-16 14:30 | 71.1 | 70.88
2018-05-16 15:00 | 76.84 | 76.7
2018-05-16 15:30 | 79.85 | 79.76
2018-05-16 16:00 | 88.67 | 88.61
2018-05-16 16:30 | 94.29 | 94.29
2018-05-16 17:00 | 105.85 | 105.29
2018-05-16 17:30 | 120.13 | 120.01
2018-05-16 18:00 | 127.52 | 125.92
2018-05-16 18:30 | 124.92 | 124.9
2018-05-16 19:00 | 131.39 | 131.27
2018-05-16 19:30 | 130.29 | 130.09
2018-05-16 20:00 | 123.37 | 122.16
2018-05-16 20:30 | 124.27 | 122.88
2018-05-16 21:00 | 115.66 | 112.84
2018-05-16 21:30 | 108.87 | 105.88
2018-05-16 22:00 | 95.11 | 92.32
2018-05-16 22:30 | 85.56 | 82.76
2018-05-16 23:00 | 87.95 | 85.51
2018-05-16 23:30 | 68.59 | 65.56
2018-05-17 | 54.01 | 49.62
2018-05-17 00:30 | 41.87 | 35.53
2018-05-17 01:00 | 33.78 | 25.13
2018-05-17 01:30 | 27.1 | 16.55
2018-05-17 02:00 | 20.04 | 19.53
2018-05-17 02:30 | 27.08 | 27.07
2018-05-17 03:00 | 31.33 | 31.31
2018-05-17 03:30 | 34.38 | 34.38
2018-05-17 04:00 | 36.45 | 36.45
2018-05-17 04:30 | 39.47 | 39.46
2018-05-17 05:00 | 43.28 | 43.28
2018-05-17 05:30 | 51.52 | 51.5
2018-05-17 06:00 | 61.54 | 61.48
2018-05-17 06:30 | 70.87 | 70.77
2018-05-17 07:00 | 89.65 | 89.29
2018-05-17 07:30 | 99.13 | 99.12
2018-05-17 08:00 | 107.34 | 107.05
2018-05-17 08:30 | 107.96 | 107.4
2018-05-17 09:00 | 101.21 | 100.49
2018-05-17 09:30 | 81.41 | 79.61
2018-05-17 10:00 | 78.2 | 75.38
2018-05-17 10:30 | 74.14 | 70.85
2018-05-17 11:00 | 82.77 | 74.48
2018-05-17 11:30 | 84.92 | 74.52
2018-05-17 12:00 | 94.48 | 85.38
2018-05-17 12:30 | 94.97 | 86.17
2018-05-17 13:00 | 100.43 | 92.08
2018-05-17 13:30 | 104.88 | 96.94
2018-05-17 14:00 | 116.06 | 100.87
2018-05-17 14:30 | 118.79 | 95.11
2018-05-17 15:00 | 108.13 | 82.34
2018-05-17 15:30 | 119.64 | 98.8
2018-05-17 16:00 | 124.64 | 105.09
2018-05-17 16:30 | 129.68 | 110.86
2018-05-17 17:00 | 130.76 | 112.08
2018-05-17 17:30 | 139.78 | 122.51
2018-05-17 18:00 | 136.54 | 124.3
2018-05-17 18:30 | 97.37 | 79.76
2018-05-17 19:00 | 96.52 | 84.69
2018-05-17 19:30 | 87.52 | 81.81
2018-05-17 20:00 | 78.38 | 72.38
2018-05-17 20:30 | 54.74 | 46.33
2018-05-17 21:00 | 56.31 | 50.44
2018-05-17 21:30 | 28.78 | 28.58
2018-05-17 22:00 | 11.51 | 7.31
2018-05-17 22:30 | 14.04 | 8.61
2018-05-17 23:00 | 28.99 | 26.13
2018-05-17 23:30 | 10.73 | -3.81
2018-05-18 | 43.64 | -43.2
2018-05-18 00:30 | 53.93 | -53.49
2018-05-18 01:00 | 53.78 | -53.26
2018-05-18 01:30 | 57.88 | -57.45
2018-05-18 02:00 | 56.91 | -56.7
2018-05-18 02:30 | 55.54 | -54.83
2018-05-18 03:00 | 50.27 | -49.08
2018-05-18 03:30 | 51.19 | -50.13
2018-05-18 04:00 | 50.63 | -49.56
2018-05-18 04:30 | 50.64 | -49.65
2018-05-18 05:00 | 53.58 | -52.66
2018-05-18 05:30 | 38.75 | -36.51
2018-05-18 06:00 | 23.34 | -16.98
2018-05-18 06:30 | 17.6 | 6.44
2018-05-18 07:00 | 7.08 | -4.2
2018-05-18 07:30 | 34.66 | 34.4
2018-05-18 08:00 | 10.56 | 10.54
2018-05-18 08:30 | 22.01 | -9.41
2018-05-18 09:00 | 27.59 | -11.91
2018-05-18 09:30 | 31.14 | -16.34
2018-05-18 10:00 | 34.8 | -18.47
2018-05-18 10:30 | 38.93 | -24.4
2018-05-18 11:00 | 43 | -28.81
2018-05-18 11:30 | 47.67 | -34.79
2018-05-18 12:00 | 71.73 | -32.71
2018-05-18 12:30 | 72.04 | -31.54
2018-05-18 13:00 | 52.91 | -36.49
2018-05-18 13:30 | 47.74 | -35.96
2018-05-18 14:00 | 42.33 | -29.19
2018-05-18 14:30 | 35.98 | -21.19
2018-05-18 15:00 | 29.74 | -16.71
2018-05-18 15:30 | 27.78 | -15.14
2018-05-18 16:00 | 21.93 | 1.94
2018-05-18 16:30 | 32.16 | 24.64
2018-05-18 17:00 | 50.91 | 41.68
2018-05-18 17:30 | 89.51 | 72.65
2018-05-18 18:00 | 113.93 | 101.44
2018-05-18 18:30 | 89.68 | 78.74
2018-05-18 19:00 | 76.99 | 72.13
2018-05-18 19:30 | 62.57 | 57.53
2018-05-18 20:00 | 47.91 | 47.8
2018-05-18 20:30 | 10.82 | 8.62
2018-05-18 21:00 | 47.07 | -46.98
2018-05-18 21:30 | 19.19 | -17.1
2018-05-18 22:00 | 21.78 | -19.33
2018-05-18 22:30 | 18.94 | -15.22
2018-05-18 23:00 | 15.73 | 8.12
2018-05-18 23:30 | 23.23 | -19.59
2018-05-19 | 48.58 | -47.54
2018-05-19 00:30 | 86.75 | -86.73
2018-05-19 01:00 | 94.74 | -94.74
2018-05-19 01:30 | 87.35 | -87.35
2018-05-19 02:00 | 71.54 | -71.44
2018-05-19 02:30 | 67.4 | -67.21
2018-05-19 03:00 | 65.62 | -64.09
2018-05-19 03:30 | 67.07 | -65.58
2018-05-19 04:00 | 68.61 | -67.45
2018-05-19 04:30 | 64.48 | -62.69
2018-05-19 05:00 | 62.97 | -60.84
2018-05-19 05:30 | 62.18 | -59.62
2018-05-19 06:00 | 62.79 | -59.77
2018-05-19 06:30 | 53.27 | -48.56
2018-05-19 07:00 | 39.4 | -31.12
2018-05-19 07:30 | 48.31 | -44.31
2018-05-19 08:00 | 81 | -81
2018-05-19 08:30 | 76.56 | -76.56
2018-05-19 09:00 | 85.64 | -85.56
2018-05-19 09:30 | 83.59 | -83.44
2018-05-19 10:00 | 85.62 | -85.43
2018-05-19 10:30 | 93.3 | -93.1
2018-05-19 11:00 | 99.41 | -99.18
2018-05-19 11:30 | 93.81 | -93.69
2018-05-19 12:00 | 77.55 | -77.5
2018-05-19 12:30 | 92.22 | -92.11
2018-05-19 13:00 | 71.2 | -71.19
2018-05-19 13:30 | 44.25 | -44.18
2018-05-19 14:00 | 40.75 | -40.67
2018-05-19 14:30 | 32.06 | -31.91
2018-05-19 15:00 | 4.53 | -1.16
2018-05-19 15:30 | 8.89 | -7.71
2018-05-19 16:00 | 4.94 | 2.11
2018-05-19 16:30 | 16.54 | 15.86
2018-05-19 17:00 | 37.76 | 37.56
2018-05-19 17:30 | 49.74 | 49.58
2018-05-19 18:00 | 59.55 | 57.41
2018-05-19 18:30 | 67.02 | 64.85
2018-05-19 19:00 | 57.14 | 54.08
2018-05-19 19:30 | 45.77 | 40.86
2018-05-19 20:00 | 43.74 | 37.38
2018-05-19 20:30 | 34.85 | 32.75
2018-05-19 21:00 | 13.6 | 7.45
2018-05-19 21:30 | 18.16 | -13.62
2018-05-19 22:00 | 51.89 | -51.43
2018-05-19 22:30 | 13.08 | 4.45
2018-05-19 23:00 | 27.14 | 22.67
2018-05-19 23:30 | 19.85 | 10.82
2018-05-20 | 29.91 | -26.57
2018-05-20 00:30 | 34.14 | -26.89
2018-05-20 01:00 | 35.02 | -26.64
2018-05-20 01:30 | 41.26 | -35.31
2018-05-20 02:00 | 52.76 | -49.05
2018-05-20 02:30 | 46.42 | -41.94
2018-05-20 03:00 | 44.82 | -40.23
2018-05-20 03:30 | 46.3 | -41.83
2018-05-20 04:00 | 46.95 | -42.73
2018-05-20 04:30 | 37.92 | -32.12
2018-05-20 05:00 | 24.81 | -11.98
2018-05-20 05:30 | 24.11 | -7.54
2018-05-20 06:00 | 24.24 | -3.01
2018-05-20 06:30 | 24.08 | -4.44
2018-05-20 07:00 | 24.04 | -0.51
2018-05-20 07:30 | 27.04 | -9.36
2018-05-20 08:00 | 36.12 | -24.91
2018-05-20 08:30 | 41.55 | -30.69
2018-05-20 09:00 | 44.09 | -40.81
2018-05-20 09:30 | 53 | -52.08
2018-05-20 10:00 | 59.27 | -58.71
2018-05-20 10:30 | 62.19 | -61.94
2018-05-20 11:00 | 46.35 | -45.99
2018-05-20 11:30 | 50.24 | -49.93
2018-05-20 12:00 | 43.19 | -42.9
2018-05-20 12:30 | 47.96 | -47.71
2018-05-20 13:00 | 59.75 | -59.64
2018-05-20 13:30 | 56.98 | -56.83
2018-05-20 14:00 | 49.15 | -48.94
2018-05-20 14:30 | 28.96 | -28.41
2018-05-20 15:00 | 15 | -13.62
2018-05-20 15:30 | 7.45 | 2.33
2018-05-20 16:00 | 7.24 | 2.82
2018-05-20 16:30 | 8.11 | 4.62
2018-05-20 17:00 | 16.66 | 15.85
2018-05-20 17:30 | 29.63 | 29.63
2018-05-20 18:00 | 73.13 | 73.12
2018-05-20 18:30 | 62.68 | 62.66
2018-05-20 19:00 | 64.04 | 63.39
2018-05-20 19:30 | 60.34 | 56.9
2018-05-20 20:00 | 39.74 | 33.91
2018-05-20 20:30 | 27.95 | 19.36
2018-05-20 21:00 | 14.29 | 8.78
2018-05-20 21:30 | 13.49 | -3.96
2018-05-20 22:00 | 13.62 | -4.54
2018-05-20 22:30 | 32.76 | 28.83
2018-05-20 23:00 | 62.03 | 59.37
2018-05-20 23:30 | 43.74 | 39.75
2018-05-21 | 16.48 | -4.97
2018-05-21 00:30 | 30.62 | -21.28
2018-05-21 01:00 | 41.28 | -36.47
2018-05-21 01:30 | 50.06 | -46.97
2018-05-21 02:00 | 51.23 | -48.99
2018-05-21 02:30 | 42.69 | -42.42
2018-05-21 03:00 | 36.13 | -36.12
2018-05-21 03:30 | 20.58 | -20.56
2018-05-21 04:00 | 13.31 | -13.31
2018-05-21 04:30 | 4.94 | 4.53
2018-05-21 05:00 | 17.42 | 16.78
2018-05-21 05:30 | 22.49 | 20.6
2018-05-21 06:00 | 26.66 | 21.82
2018-05-21 06:30 | 27.66 | 21.75
2018-05-21 07:00 | 51.08 | 44.42
2018-05-21 07:30 | 73.18 | 69.15
2018-05-21 08:00 | 49.14 | 48.8
2018-05-21 08:30 | 16.09 | 15.7
2018-05-21 09:00 | 15.31 | -14.55
2018-05-21 09:30 | 20.29 | -19.57
2018-05-21 10:00 | 24.13 | -23.3
2018-05-21 10:30 | 27.4 | -26.47
2018-05-21 11:00 | 32.9 | -31.71
2018-05-21 11:30 | 33.37 | -32.12
2018-05-21 12:00 | 12.83 | -9.85
2018-05-21 12:30 | 16 | -13.82
2018-05-21 13:00 | 11.29 | -7.74
2018-05-21 13:30 | 10.03 | -3.04
2018-05-21 14:00 | 15.63 | 10.8
2018-05-21 14:30 | 21.6 | 19.78
2018-05-21 15:00 | 26.32 | 25.6
2018-05-21 15:30 | 37.25 | 37.11
2018-05-21 16:00 | 53.72 | 53.66
2018-05-21 16:30 | 53.06 | 53.04
2018-05-21 17:00 | 70.81 | 70.8
2018-05-21 17:30 | 59.38 | 58.19
2018-05-21 18:00 | 59.65 | 58.94
2018-05-21 18:30 | 52.93 | 52.01
2018-05-21 19:00 | 48.84 | 47.61
2018-05-21 19:30 | 51.97 | 51.51
2018-05-21 20:00 | 29.28 | 29.11
2018-05-21 20:30 | 22.49 | 21.93
2018-05-21 21:00 | 7.5 | 2
2018-05-21 21:30 | 11.04 | 3.75
2018-05-21 22:00 | 52.06 | -51.14
2018-05-21 22:30 | 28.33 | -25.19
2018-05-21 23:00 | 18.95 | 12.43
2018-05-21 23:30 | 17.87 | 8
2018-05-22 | 36.38 | -34.12
2018-05-22 00:30 | 39.89 | -37.86
2018-05-22 01:00 | 60.97 | -59.32
2018-05-22 01:30 | 51.08 | -48.61
2018-05-22 02:00 | 43.94 | -41.06
2018-05-22 02:30 | 31.23 | -26.68
2018-05-22 03:00 | 33.61 | -28.15
2018-05-22 03:30 | 31.88 | -24.72
2018-05-22 04:00 | 30.01 | -21.32
2018-05-22 04:30 | 25.93 | -12.83
2018-05-22 05:00 | 24.19 | -0.79
2018-05-22 05:30 | 35.26 | 23.23
2018-05-22 06:00 | 63.35 | 55.98
2018-05-22 06:30 | 78.25 | 72.13
2018-05-22 07:00 | 74.58 | 71.02
2018-05-22 07:30 | 77.18 | 77.13
2018-05-22 08:00 | 48.07 | 48.05
2018-05-22 08:30 | 4.85 | 4.75
2018-05-22 09:00 | 22.07 | -21.5
2018-05-22 09:30 | 59.25 | -58.62
2018-05-22 10:00 | 64.5 | -64
2018-05-22 10:30 | 74.75 | -74.19
2018-05-22 11:00 | 73.42 | -72.78
2018-05-22 11:30 | 41.13 | -40.67
2018-05-22 12:00 | 23.02 | -22.94
2018-05-22 12:30 | 21.17 | -21.09
2018-05-22 13:00 | 21.86 | -21.72
2018-05-22 13:30 | 16.93 | -16.69
2018-05-22 14:00 | 3.15 | -0.5
2018-05-22 14:30 | 6.03 | 5.67
2018-05-22 15:00 | 2.99 | 1.08
2018-05-22 15:30 | 18.92 | 18.61
2018-05-22 16:00 | 36.23 | 28.73
2018-05-22 16:30 | 27.59 | 17.64
2018-05-22 17:00 | 53.36 | 40.44
2018-05-22 17:30 | 71.28 | 61.75
2018-05-22 18:00 | 89.43 | 80.26
2018-05-22 18:30 | 69.27 | 58.9
2018-05-22 19:00 | 74.41 | 65.91
2018-05-22 19:30 | 66.57 | 58.02
2018-05-22 20:00 | 56.13 | 46.94
2018-05-22 20:30 | 52.59 | -39.48
2018-05-22 21:00 | 23.59 | -16.17
2018-05-22 21:30 | 14.38 | -4.31
2018-05-22 22:00 | 8.05 | -2.51
2018-05-22 22:30 | 29.99 | -27.17
2018-05-22 23:00 | 17.85 | 8.49
2018-05-22 23:30 | 20.7 | -13.01
2018-05-23 | 31.67 | -27.28
2018-05-23 00:30 | 52.59 | -51.44
2018-05-23 01:00 | 60.83 | -60.34
2018-05-23 01:30 | 84.97 | -84.91
2018-05-23 02:00 | 81.05 | -80.95
2018-05-23 02:30 | 66.05 | -65.76
2018-05-23 03:00 | 71.17 | -71.12
2018-05-23 03:30 | 58.88 | -58.27
2018-05-23 04:00 | 53.14 | -53.11
2018-05-23 04:30 | 38 | -37.97
2018-05-23 05:00 | 19.29 | -18.66
2018-05-23 05:30 | 13.83 | -7.75
2018-05-23 06:00 | 37.04 | 30.51
2018-05-23 06:30 | 63.67 | 57.67
2018-05-23 07:00 | 74.51 | 69.3
2018-05-23 07:30 | 102.25 | 101.53
2018-05-23 08:00 | 17.93 | 11.51
2018-05-23 08:30 | 119.38 | -96.73
2018-05-23 09:00 | 113.43 | -100.9
2018-05-23 09:30 | 116.64 | -108.33
2018-05-23 10:00 | 120.08 | -111.73
2018-05-23 10:30 | 111.86 | -102.63
2018-05-23 11:00 | 119.23 | -110.18
2018-05-23 11:30 | 127.04 | -118.64
2018-05-23 12:00 | 129.85 | -121.82
2018-05-23 12:30 | 122.67 | -114.48
2018-05-23 13:00 | 122.13 | -113.9
2018-05-23 13:30 | 118.99 | -110.03
2018-05-23 14:00 | 116.32 | -106.42
2018-05-23 14:30 | 110.16 | -99.36
2018-05-23 15:00 | 43.29 | 23.41
2018-05-23 15:30 | 40.77 | 21.37
2018-05-23 16:00 | 49.87 | 37.13
2018-05-23 16:30 | 56.78 | 46.54
2018-05-23 17:00 | 68.81 | 60.15
2018-05-23 17:30 | 79.42 | 70.41
2018-05-23 18:00 | 84.02 | 75.15
2018-05-23 18:30 | 85.02 | 77.67
2018-05-23 19:00 | 91.87 | 86.05
2018-05-23 19:30 | 90.01 | 84.9
2018-05-23 20:00 | 90.7 | 86.14
2018-05-23 20:30 | 80.98 | 76.87
2018-05-23 21:00 | 50.37 | 49.18
2018-05-23 21:30 | 30.89 | 24.95
2018-05-23 22:00 | 26.79 | 13.55
2018-05-23 22:30 | 25.83 | -15.52
2018-05-23 23:00 | 28.72 | 15.74
2018-05-23 23:30 | 22.39 | -5.9
2018-05-24 | 32.73 | -25.54
2018-05-24 00:30 | 47.83 | -45.09
2018-05-24 01:00 | 52.74 | -50.87
2018-05-24 01:30 | 54.68 | -53.1
2018-05-24 02:00 | 56.58 | -55.37
2018-05-24 02:30 | 46.49 | -44.17
2018-05-24 03:00 | 40.51 | -36.24
2018-05-24 03:30 | 30 | -18.84
2018-05-24 04:00 | 25.64 | -9.21
2018-05-24 04:30 | 26.04 | 1.51
2018-05-24 05:00 | 37.58 | 24.8
2018-05-24 05:30 | 42.47 | 29.81
2018-05-24 06:00 | 50.29 | 39.99
2018-05-24 06:30 | 41.15 | 33.53
2018-05-24 07:00 | 31.21 | 28.64
2018-05-24 07:30 | 50.53 | 50.2
2018-05-24 08:00 | 35.64 | 35.51
2018-05-24 08:30 | 17.71 | 17.48
2018-05-24 09:00 | 13.85 | -12.23
2018-05-24 09:30 | 22.17 | -19.85
2018-05-24 10:00 | 17.64 | -14.04
2018-05-24 10:30 | 11.9 | -9.61
2018-05-24 11:00 | 24.74 | -23.99
2018-05-24 11:30 | 25.28 | -24.42
2018-05-24 12:00 | 14.49 | -12.89
2018-05-24 12:30 | 7.6 | -3.9
2018-05-24 13:00 | 6.9 | -2.69
2018-05-24 13:30 | 10.73 | 8.75
2018-05-24 14:00 | 25.38 | 24.37
2018-05-24 14:30 | 24.47 | 23.42
2018-05-24 15:00 | 31.17 | 30.79
2018-05-24 15:30 | 30.1 | 29.91
2018-05-24 16:00 | 39.47 | 39.39
2018-05-24 16:30 | 49.9 | 49.89
2018-05-24 17:00 | 55.42 | 54.87
2018-05-24 17:30 | 74.5 | 52.66
2018-05-24 18:00 | 69.49 | 34.42
2018-05-24 18:30 | 88.97 | 68.81
2018-05-24 19:00 | 100.05 | 86.76
2018-05-24 19:30 | 103.4 | 98.4
2018-05-24 20:00 | 96.54 | 91.62
2018-05-24 20:30 | 85.45 | 80.8
2018-05-24 21:00 | 69.73 | 69.31
2018-05-24 21:30 | 56.3 | 55.23
2018-05-24 22:00 | 29.72 | 26.19
2018-05-24 22:30 | 44.52 | 41.4
2018-05-24 23:00 | 54.61 | 51.86
2018-05-24 23:30 | 25.15 | 19.26
2018-05-25 | 18.02 | -7.04
2018-05-25 00:30 | 29.56 | -25.35
2018-05-25 01:00 | 38.16 | -35.54
2018-05-25 01:30 | 33.68 | -30.01
2018-05-25 02:00 | 42.83 | -35.77
2018-05-25 02:30 | 40.21 | -32.68
2018-05-25 03:00 | 36.71 | -27.91
2018-05-25 03:30 | 36.43 | -27.5
2018-05-25 04:00 | 35.54 | -26.06
2018-05-25 04:30 | 28.15 | -10.04
2018-05-25 05:00 | 28.03 | 0.73
2018-05-25 05:30 | 38.93 | 24.05
2018-05-25 06:00 | 56.29 | 46.8
2018-05-25 06:30 | 56.83 | 49.08
2018-05-25 07:00 | 72.77 | 70.16
2018-05-25 07:30 | 86.5 | 86.25
2018-05-25 08:00 | 83.6 | 83.53
2018-05-25 08:30 | 75.5 | 75.5
2018-05-25 09:00 | 50.52 | 50.48
2018-05-25 09:30 | 36.15 | 35.82
2018-05-25 10:00 | 18.02 | 17.26
2018-05-25 10:30 | 9.02 | 7.17
2018-05-25 11:00 | 11.72 | 10.06
2018-05-25 11:30 | 18.46 | 16.99
2018-05-25 12:00 | 16.53 | 15.14
2018-05-25 12:30 | 15 | 13.63
2018-05-25 13:00 | 6.78 | -2.11
2018-05-25 13:30 | 20.91 | 19.96
2018-05-25 14:00 | 30.88 | 30.41
2018-05-25 14:30 | 28.22 | 27.78
2018-05-25 15:00 | 34.43 | 34.22
2018-05-25 15:30 | 34.65 | 34.53
2018-05-25 16:00 | 47.42 | 47.35
2018-05-25 16:30 | 66.17 | 66.16
2018-05-25 17:00 | 78.21 | 77.37
2018-05-25 17:30 | 97.87 | 97.57
2018-05-25 18:00 | 63.93 | 63.61
2018-05-25 18:30 | 59.5 | 59.07
2018-05-25 19:00 | 63.9 | 63.37
2018-05-25 19:30 | 65.13 | 64.39
2018-05-25 20:00 | 40.98 | 40.96
2018-05-25 20:30 | 38.23 | 38.09
2018-05-25 21:00 | 33.49 | 33.26
2018-05-25 21:30 | 37.77 | 37.17
2018-05-25 22:00 | 20 | 17.92
2018-05-25 22:30 | 23.48 | 20.96
2018-05-25 23:00 | 51.7 | 50.03
2018-05-25 23:30 | 32.03 | 28.56
2018-05-26 | 16.2 | 3.65
2018-05-26 00:30 | 25.61 | -20.69
2018-05-26 01:00 | 41.3 | -39.08
2018-05-26 01:30 | 29.57 | -25.44
2018-05-26 02:00 | 27.1 | -19.2
2018-05-26 02:30 | 28.97 | -22.19
2018-05-26 03:00 | 29.01 | -22.23
2018-05-26 03:30 | 28.54 | -20.39
2018-05-26 04:00 | 27.96 | -19.38
2018-05-26 04:30 | 33.26 | -26.43
2018-05-26 05:00 | 27.78 | -16.51
2018-05-26 05:30 | 26.21 | -10.28
2018-05-26 06:00 | 27.59 | 7.79
2018-05-26 06:30 | 32.97 | 17.48
2018-05-26 07:00 | 28.56 | 6.91
2018-05-26 07:30 | 26.08 | -1.5
2018-05-26 08:00 | 25.53 | -6.94
2018-05-26 08:30 | 40.93 | -40.04
2018-05-26 09:00 | 15.25 | -15.11
2018-05-26 09:30 | 3.28 | -2.17
2018-05-26 10:00 | 44.19 | 44.11
2018-05-26 10:30 | 19.41 | 19.03
2018-05-26 11:00 | 21.1 | 20.35
2018-05-26 11:30 | 10.11 | 8.48
2018-05-26 12:00 | 6.99 | 3.26
2018-05-26 12:30 | 7.59 | -3.91
2018-05-26 13:00 | 10.83 | -7.69
2018-05-26 13:30 | 9.47 | 4.91
2018-05-26 14:00 | 25.5 | 23.98
2018-05-26 14:30 | 41.09 | 40.08
2018-05-26 15:00 | 45.58 | 44.62
2018-05-26 15:30 | 62.41 | 61.66
2018-05-26 16:00 | 72.24 | 71.6
2018-05-26 16:30 | 83.07 | 82.61
2018-05-26 17:00 | 85.08 | 84.85
2018-05-26 17:30 | 89.32 | 89.31
2018-05-26 18:00 | 84.59 | 84.58
2018-05-26 18:30 | 76.63 | 76.58
2018-05-26 19:00 | 89.68 | 89.62
2018-05-26 19:30 | 98.92 | 98.79
2018-05-26 20:00 | 94.06 | 93.81
2018-05-26 20:30 | 93.08 | 92.73
2018-05-26 21:00 | 106.61 | 106.12
2018-05-26 21:30 | 94.26 | 93.44
2018-05-26 22:00 | 75.92 | 74.5
2018-05-26 22:30 | 100.4 | 99.08
2018-05-26 23:00 | 108.2 | 106.74
2018-05-26 23:30 | 83.78 | 81.53
2018-05-27 | 56.41 | 52.76
2018-05-27 00:30 | 37.3 | 26.62
2018-05-27 01:00 | 27.58 | 5.09
2018-05-27 01:30 | 25.2 | -2.1
2018-05-27 02:00 | 16.33 | -1.95
2018-05-27 02:30 | 8.54 | -7.52
2018-05-27 03:00 | 10.82 | -10.15
2018-05-27 03:30 | 6.94 | -4.96
2018-05-27 04:00 | 9.04 | -7.73
2018-05-27 04:30 | 8.84 | -7.41
2018-05-27 05:00 | 4.98 | -0.38
2018-05-27 05:30 | 7.88 | -4.86
2018-05-27 06:00 | 15.39 | 12.83
2018-05-27 06:30 | 9.79 | 4.41
2018-05-27 07:00 | 16.52 | 13.84
2018-05-27 07:30 | 26.86 | 24.04
2018-05-27 08:00 | 28.24 | 23.78
2018-05-27 08:30 | 28.66 | 22.02
2018-05-27 09:00 | 25.8 | 17.72
2018-05-27 09:30 | 20.07 | 10.36
2018-05-27 10:00 | 16.49 | -0.96
2018-05-27 10:30 | 20.91 | -12.96
2018-05-27 11:00 | 21.99 | -13.87
2018-05-27 11:30 | 18.68 | -4.49
2018-05-27 12:00 | 16.57 | -4.44
2018-05-27 12:30 | 19.02 | -11.41
2018-05-27 13:00 | 20.89 | -14.81
2018-05-27 13:30 | 16.7 | -6.97
2018-05-27 14:00 | 16.33 | 4.12
2018-05-27 14:30 | 19.66 | 11.28
2018-05-27 15:00 | 29.31 | 23.84
2018-05-27 15:30 | 38.53 | 34.51
2018-05-27 16:00 | 64.78 | 62.81
2018-05-27 16:30 | 63.05 | 62.06
2018-05-27 17:00 | 61.36 | 61.09
2018-05-27 17:30 | 92.76 | 92.75
2018-05-27 18:00 | 127.81 | 127.8
2018-05-27 18:30 | 128.07 | 128.02
2018-05-27 19:00 | 117.83 | 117.81
2018-05-27 19:30 | 104.5 | 103.54
2018-05-27 20:00 | 100 | 96.9
2018-05-27 20:30 | 90.89 | 87.23
2018-05-27 21:00 | 65.65 | 60.26
2018-05-27 21:30 | 78.56 | 73.49
2018-05-27 22:00 | 94.85 | 90.45
2018-05-27 22:30 | 112.95 | 108.7
2018-05-27 23:00 | 113.13 | 108.63
2018-05-27 23:30 | 84.01 | 78.22
2018-05-28 | 46.63 | 36.23
2018-05-28 00:30 | 32.37 | 19.5
2018-05-28 01:00 | 24.5 | 2.98
2018-05-28 01:30 | 16.32 | -5.66
2018-05-28 02:00 | 11.21 | -6.8
2018-05-28 02:30 | 10.61 | 2.55
2018-05-28 03:00 | 12.84 | 6.76
2018-05-28 03:30 | 14.03 | 8.52
2018-05-28 04:00 | 14.91 | 9.48
2018-05-28 04:30 | 12.48 | 4.95
2018-05-28 05:00 | 18.1 | 12.63
2018-05-28 05:30 | 38.9 | 35.4
2018-05-28 06:00 | 65.57 | 62.97
2018-05-28 06:30 | 92.49 | 91.37
2018-05-28 07:00 | 108.49 | 105.62
2018-05-28 07:30 | 100.53 | 99.16
2018-05-28 08:00 | 84.62 | 83.93
2018-05-28 08:30 | 62.07 | 61.57
2018-05-28 09:00 | 61.24 | 60.76
2018-05-28 09:30 | 57.79 | 57.29
2018-05-28 10:00 | 46.36 | 45.54
2018-05-28 10:30 | 43.6 | 43.54
2018-05-28 11:00 | 78.8 | 78.72
2018-05-28 11:30 | 91.29 | 91.26
2018-05-28 12:00 | 75.76 | 75.75
2018-05-28 12:30 | 57.25 | 57.14
2018-05-28 13:00 | 102.36 | 102.36
2018-05-28 13:30 | 120.89 | 120.89
2018-05-28 14:00 | 115.78 | 115.78
2018-05-28 14:30 | 105.75 | 105.74
2018-05-28 15:00 | 108.04 | 108.04
2018-05-28 15:30 | 105.51 | 105.51
2018-05-28 16:00 | 90.43 | 90.41
2018-05-28 16:30 | 82.33 | 82.26
2018-05-28 17:00 | 99.04 | 98.95
2018-05-28 17:30 | 115.26 | 115.25
2018-05-28 18:00 | 117.22 | 117.16
2018-05-28 18:30 | 103.53 | 103.51
2018-05-28 19:00 | 87.09 | 87.09
2018-05-28 19:30 | 78.72 | 78.62
2018-05-28 20:00 | 68.03 | 67.66
2018-05-28 20:30 | 68.54 | 67.91
2018-05-28 21:00 | 74.86 | 74.82
2018-05-28 21:30 | 80.14 | 80.03
2018-05-28 22:00 | 72.77 | 69.68
2018-05-28 22:30 | 79.03 | 75.88
2018-05-28 23:00 | 101.26 | 98.14
2018-05-28 23:30 | 67.85 | 63.53
2018-05-29 | 37.45 | 29.49
2018-05-29 00:30 | 21.94 | 8.44
2018-05-29 01:00 | 20.83 | -12.52
2018-05-29 01:30 | 26.59 | -22.15
2018-05-29 02:00 | 25.64 | -20.21
2018-05-29 02:30 | 26.78 | -21.02
2018-05-29 03:00 | 22.41 | -13.59
2018-05-29 03:30 | 19.96 | -2.25
2018-05-29 04:00 | 23.58 | 23.45
2018-05-29 04:30 | 19.93 | 19.92
2018-05-29 05:00 | 40.06 | 40.05
2018-05-29 05:30 | 62.3 | 62.27
2018-05-29 06:00 | 73.11 | 73.08
2018-05-29 06:30 | 81.63 | 81.6
2018-05-29 07:00 | 116.73 | 116.68
2018-05-29 07:30 | 114.23 | 114.23
2018-05-29 08:00 | 103.09 | 103.08
2018-05-29 08:30 | 78.71 | 78.59
2018-05-29 09:00 | 67.21 | 66.91
2018-05-29 09:30 | 57.83 | 57.29
2018-05-29 10:00 | 65.52 | 65.08
2018-05-29 10:30 | 57.45 | 56.75
2018-05-29 11:00 | 51.16 | 50.2
2018-05-29 11:30 | 59.28 | 58.4
2018-05-29 12:00 | 69.33 | 68.68
2018-05-29 12:30 | 75.77 | 75.39
2018-05-29 13:00 | 78.85 | 78.49
2018-05-29 13:30 | 96.07 | 95.85
2018-05-29 14:00 | 83.7 | 83.51
2018-05-29 14:30 | 84.07 | 83.85
2018-05-29 15:00 | 79.99 | 79.8
2018-05-29 15:30 | 84.2 | 84.08
2018-05-29 16:00 | 76.2 | 76.06
2018-05-29 16:30 | 78.69 | 78.49
2018-05-29 17:00 | 112.04 | 111.88
2018-05-29 17:30 | 148.78 | 147.32
2018-05-29 18:00 | 144 | 142.53
2018-05-29 18:30 | 131.78 | 131.7
2018-05-29 19:00 | 128.34 | 128.31
2018-05-29 19:30 | 106.28 | 106.27
2018-05-29 20:00 | 93.85 | 92.39
2018-05-29 20:30 | 65.97 | 64.23
2018-05-29 21:00 | 68.86 | 68.56
2018-05-29 21:30 | 61.43 | 61.28
2018-05-29 22:00 | 51.72 | 51.71
2018-05-29 22:30 | 39.84 | 36.73
2018-05-29 23:00 | 62.67 | 59.24
2018-05-29 23:30 | 36.62 | 32.35
2018-05-30 | 18.05 | 7.53
2018-05-30 00:30 | 18.76 | -10.01
2018-05-30 01:00 | 27.31 | -22.62
2018-05-30 01:30 | 34.91 | -32.43
2018-05-30 02:00 | 30.63 | -27.05
2018-05-30 02:30 | 34.92 | -32.02
2018-05-30 03:00 | 33.81 | -30.78
2018-05-30 03:30 | 40.78 | -38.92
2018-05-30 04:00 | 42.29 | -40.5
2018-05-30 04:30 | 34.93 | -31.78
2018-05-30 05:00 | 23.49 | -15.33
2018-05-30 05:30 | 22.84 | 6.48
2018-05-30 06:00 | 54.15 | 49.14
2018-05-30 06:30 | 68.98 | 66.3
2018-05-30 07:00 | 55.91 | 55.53
2018-05-30 07:30 | 79.74 | 79.42
2018-05-30 08:00 | 47.37 | 46.29
2018-05-30 08:30 | 34.51 | 30.1
2018-05-30 09:00 | 38.26 | 17.84
2018-05-30 09:30 | 36.8 | 1.1
2018-05-30 10:00 | 37.67 | 10.02
2018-05-30 10:30 | 38.09 | 1.28
2018-05-30 11:00 | 41.88 | -7.47
2018-05-30 11:30 | 41.33 | -3.45
2018-05-30 12:00 | 43.95 | -11.24
2018-05-30 12:30 | 42.32 | -5.33
2018-05-30 13:00 | 44 | -10.19
2018-05-30 13:30 | 43.27 | -3.43
2018-05-30 14:00 | 43.58 | 2.77
2018-05-30 14:30 | 44.07 | 9.97
2018-05-30 15:00 | 53.97 | 35.47
2018-05-30 15:30 | 70.91 | 59.31
2018-05-30 16:00 | 91.55 | 83.64
2018-05-30 16:30 | 95.14 | 87.96
2018-05-30 17:00 | 93.56 | 85.71
2018-05-30 17:30 | 100.06 | 91.44
2018-05-30 18:00 | 121.85 | 114.62
2018-05-30 18:30 | 119.88 | 113.9
2018-05-30 19:00 | 130.28 | 125.51
2018-05-30 19:30 | 148.21 | 144.54
2018-05-30 20:00 | 133.78 | 130.15
2018-05-30 20:30 | 110.75 | 109.32
2018-05-30 21:00 | 95.59 | 94.6
2018-05-30 21:30 | 79.39 | 78.66
2018-05-30 22:00 | 64.41 | 64.03
2018-05-30 22:30 | 74.99 | 74.78
2018-05-30 23:00 | 101.62 | 101.55
2018-05-30 23:30 | 61.88 | 61.84
2018-05-31 | 24.25 | 24.18
2018-05-31 00:30 | 14.85 | 7.66
2018-05-31 01:00 | 17.85 | -9.79
2018-05-31 01:30 | 25.73 | -21.35
2018-05-31 02:00 | 26.88 | -22.71
2018-05-31 02:30 | 27.1 | -22.66
2018-05-31 03:00 | 29 | -25
2018-05-31 03:30 | 29.58 | -25.33
2018-05-31 04:00 | 28.19 | -22.97
2018-05-31 04:30 | 21.35 | -11.53
2018-05-31 05:00 | 19.02 | 7.01
2018-05-31 05:30 | 43.66 | 39.76
2018-05-31 06:00 | 82.44 | 80.9
2018-05-31 06:30 | 101.2 | 100.5
2018-05-31 07:00 | 99.13 | 99.09
2018-05-31 07:30 | 130.01 | 128.76
2018-05-31 08:00 | 128.49 | 126.93
2018-05-31 08:30 | 97.71 | 95.35
2018-05-31 09:00 | 66.41 | 62.74
2018-05-31 09:30 | 60.54 | 56.69
2018-05-31 10:00 | 57.7 | 53.02
2018-05-31 10:30 | 44.79 | 38.55
2018-05-31 11:00 | 35.33 | 26.14
2018-05-31 11:30 | 29.05 | 16.61
2018-05-31 12:00 | 27.1 | 12.06
2018-05-31 12:30 | 28.3 | 16.17
2018-05-31 13:00 | 28.23 | 14.86
2018-05-31 13:30 | 32.71 | 22.6
2018-05-31 14:00 | 38.62 | 30.13
2018-05-31 14:30 | 45.75 | 39.19
2018-05-31 15:00 | 47.87 | 41.53
2018-05-31 15:30 | 73.47 | 69.97
2018-05-31 16:00 | 96.65 | 94.13
2018-05-31 16:30 | 105.59 | 103.35
2018-05-31 17:00 | 116.89 | 112.26
2018-05-31 17:30 | 134.24 | 113.77
2018-05-31 18:00 | 126.87 | 99.9
2018-05-31 18:30 | 130.32 | 105.15
2018-05-31 19:00 | 132.07 | 108.02
2018-05-31 19:30 | 117.56 | 94.51
2018-05-31 20:00 | 120.11 | 107.76
2018-05-31 20:30 | 117.3 | 105.57
2018-05-31 21:00 | 105.97 | 94.98
2018-05-31 21:30 | 84.62 | 72.72
2018-05-31 22:00 | 71.01 | 61.21
2018-05-31 22:30 | 62.84 | 61.71
2018-05-31 23:00 | 81.69 | 80.43
2018-05-31 23:30 | 51.12 | 48.45
2018-06-01 | 17.54 | 4.62
2018-06-01 00:30 | 27.7 | -23.02
2018-06-01 01:00 | 41.81 | -40.04
2018-06-01 01:30 | 36.65 | -34.33
2018-06-01 02:00 | 25.57 | -21.53
2018-06-01 02:30 | 30.59 | -26.93
2018-06-01 03:00 | 32.07 | -28.89
2018-06-01 03:30 | 31.65 | -28.1
2018-06-01 04:00 | 25.81 | -21.45
2018-06-01 04:30 | 26.59 | -21.96
2018-06-01 05:00 | 18.75 | -11.35
2018-06-01 05:30 | 22.78 | 16.22
2018-06-01 06:00 | 48.74 | 46.86
2018-06-01 06:30 | 88.25 | 87.76
2018-06-01 07:00 | 89.43 | 89.36
2018-06-01 07:30 | 111.13 | 106.07
2018-06-01 08:00 | 92.64 | 76.82
2018-06-01 08:30 | 80.57 | 61.11
2018-06-01 09:00 | 61.69 | 32.66
2018-06-01 09:30 | 55.26 | 15.12
2018-06-01 10:00 | 57.05 | 11.79
2018-06-01 10:30 | 55.55 | 8.4
2018-06-01 11:00 | 55.62 | 2.59
2018-06-01 11:30 | 58.09 | -13.1
2018-06-01 12:00 | 46.64 | -19.05
2018-06-01 12:30 | 32.62 | -21.03
2018-06-01 13:00 | 30.41 | -16.49
2018-06-01 13:30 | 26.34 | -8.01
2018-06-01 14:00 | 25.53 | -0.22
2018-06-01 14:30 | 26.3 | 5.2
2018-06-01 15:00 | 31.08 | 18.72
2018-06-01 15:30 | 41.15 | 34.07
2018-06-01 16:00 | 50.19 | 44.02
2018-06-01 16:30 | 61.56 | 56.74
2018-06-01 17:00 | 89.3 | 74.21
2018-06-01 17:30 | 96.53 | 74.68
2018-06-01 18:00 | 98.58 | 76.37
2018-06-01 18:30 | 99.2 | 78.85
2018-06-01 19:00 | 104.69 | 87.15
2018-06-01 19:30 | 109.53 | 96.88
2018-06-01 20:00 | 98.36 | 95.83
2018-06-01 20:30 | 74.25 | 71.32
2018-06-01 21:00 | 74.69 | 72.21
2018-06-01 21:30 | 87.08 | 85.62
2018-06-01 22:00 | 67.27 | 65.91
2018-06-01 22:30 | 62.47 | 61.27
2018-06-01 23:00 | 86.02 | 85.37
2018-06-01 23:30 | 47.94 | 46.96
2018-06-02 | 25.5 | 24.13
2018-06-02 00:30 | 7.69 | 2.34
2018-06-02 01:00 | 18.35 | -15.32
2018-06-02 01:30 | 35.19 | -33.02
2018-06-02 02:00 | 26.78 | -24.5
2018-06-02 02:30 | 23.21 | -20.89
2018-06-02 03:00 | 26.19 | -22.25
2018-06-02 03:30 | 26.18 | -23.05
2018-06-02 04:00 | 24.82 | -19.81
2018-06-02 04:30 | 21.78 | -16.86
2018-06-02 05:00 | 16.59 | -8.9
2018-06-02 05:30 | 14.75 | -7.61
2018-06-02 06:00 | 17.62 | 12.62
2018-06-02 06:30 | 30.81 | 28.84
2018-06-02 07:00 | 36.45 | 35.14
2018-06-02 07:30 | 36.92 | 36.87
2018-06-02 08:00 | 31.21 | 26.49
2018-06-02 08:30 | 24.94 | 11.6
2018-06-02 09:00 | 24.72 | 6.83
2018-06-02 09:30 | 31.59 | -18.44
2018-06-02 10:00 | 30.84 | -16.35
2018-06-02 10:30 | 34.72 | -22.69
2018-06-02 11:00 | 35.79 | -25.65
2018-06-02 11:30 | 39.82 | -32.38
2018-06-02 12:00 | 42.3 | -35.82
2018-06-02 12:30 | 45.12 | -39.33
2018-06-02 13:00 | 33.3 | -27.04
2018-06-02 13:30 | 37.27 | -31.74
2018-06-02 14:00 | 44.29 | -39.16
2018-06-02 14:30 | 28.51 | -20.25
2018-06-02 15:00 | 19.79 | -5.7
2018-06-02 15:30 | 19.7 | 7.87
2018-06-02 16:00 | 20.25 | 15.52
2018-06-02 16:30 | 26.63 | 26.57
2018-06-02 17:00 | 33.09 | 33.07
2018-06-02 17:30 | 55.17 | 54.56
2018-06-02 18:00 | 75.05 | 70.13
2018-06-02 18:30 | 94.37 | 75.38
2018-06-02 19:00 | 102.49 | 87.58
2018-06-02 19:30 | 88.91 | 82.32
2018-06-02 20:00 | 65.75 | 65.72
2018-06-02 20:30 | 33.88 | 33.86
2018-06-02 21:00 | 53.1 | 53.06
2018-06-02 21:30 | 61.64 | 61.49
2018-06-02 22:00 | 53.57 | 53.17
2018-06-02 22:30 | 81.54 | 81.13
2018-06-02 23:00 | 89.98 | 89.33
2018-06-02 23:30 | 77.03 | 75.95
2018-06-03 | 43.73 | 40.66
2018-06-03 00:30 | 21.64 | 13.9
2018-06-03 01:00 | 18.02 | -7.03
2018-06-03 01:30 | 24.17 | -18.17
2018-06-03 02:00 | 29.69 | -26.65
2018-06-03 02:30 | 36.68 | -35.92
2018-06-03 03:00 | 33.48 | -32.76
2018-06-03 03:30 | 31.68 | -30.96
2018-06-03 04:00 | 31.48 | -30.94
2018-06-03 04:30 | 19.91 | -18.39
2018-06-03 05:00 | 13.08 | -9.6
2018-06-03 05:30 | 13.18 | -8.36
2018-06-03 06:00 | 12.04 | -1.71
2018-06-03 06:30 | 15.62 | 9.18
2018-06-03 07:00 | 27.21 | 24.01
2018-06-03 07:30 | 36.9 | 34.12
2018-06-03 08:00 | 39.21 | 36.5
2018-06-03 08:30 | 32.01 | 29.31
2018-06-03 09:00 | 19.77 | 18.67
2018-06-03 09:30 | 8.36 | 6.12
2018-06-03 10:00 | 5.49 | 0.01
2018-06-03 10:30 | 11.48 | -10.31
2018-06-03 11:00 | 28.35 | -28.18
2018-06-03 11:30 | 31.26 | -31.02
2018-06-03 12:00 | 26.52 | -25.94
2018-06-03 12:30 | 23.06 | -22
2018-06-03 13:00 | 20.24 | -18.99
2018-06-03 13:30 | 22.22 | -21.17
2018-06-03 14:00 | 19.6 | -18.33
2018-06-03 14:30 | 11.14 | 7
2018-06-03 15:00 | 28.75 | 26.81
2018-06-03 15:30 | 28.89 | 26.66
2018-06-03 16:00 | 32.72 | 32.07
2018-06-03 16:30 | 41.4 | 41.4
2018-06-03 17:00 | 60.9 | 60.88
2018-06-03 17:30 | 96.06 | 95.86
2018-06-03 18:00 | 106.51 | 103.8
2018-06-03 18:30 | 110.46 | 107.31
2018-06-03 19:00 | 111.86 | 109.14
2018-06-03 19:30 | 108.16 | 106.04
2018-06-03 20:00 | 91.79 | 89.71
2018-06-03 20:30 | 62.9 | 60.09
2018-06-03 21:00 | 63.06 | 60.83
2018-06-03 21:30 | 48.76 | 46.6
2018-06-03 22:00 | 35.01 | 32.89
2018-06-03 22:30 | 63.57 | 62.56
2018-06-03 23:00 | 72.75 | 71.35
2018-06-03 23:30 | 43.41 | 40.72
2018-06-04 | 25.36 | 19.76
2018-06-04 00:30 | 15.05 | 0.42
2018-06-04 01:00 | 21.3 | -17.69
2018-06-04 01:30 | 32.62 | -31.22
2018-06-04 02:00 | 38.93 | -38.41
2018-06-04 02:30 | 37.03 | -36.3
2018-06-04 03:00 | 37.14 | -36.39
2018-06-04 03:30 | 34.02 | -33.43
2018-06-04 04:00 | 24.93 | -23.56
2018-06-04 04:30 | 19.01 | -15.07
2018-06-04 05:00 | 15.86 | 7.28
2018-06-04 05:30 | 21.72 | 14.47
2018-06-04 06:00 | 37.21 | 33.29
2018-06-04 06:30 | 43.09 | 41.57
2018-06-04 07:00 | 131.61 | 131.55
2018-06-04 07:30 | 173.32 | 173.1
2018-06-04 08:00 | 172.02 | 171.4
2018-06-04 08:30 | 160.9 | 160.23
2018-06-04 09:00 | 155.11 | 154.45
2018-06-04 09:30 | 141.47 | 140.9
2018-06-04 10:00 | 137.25 | 136.48
2018-06-04 10:30 | 134.4 | 133.8
2018-06-04 11:00 | 139.82 | 139.21
2018-06-04 11:30 | 133.39 | 132.84
2018-06-04 12:00 | 124.2 | 123.59
2018-06-04 12:30 | 120.56 | 119.89
2018-06-04 13:00 | 120.27 | 119.51
2018-06-04 13:30 | 129.42 | 128.68
2018-06-04 14:00 | 131.55 | 130.86
2018-06-04 14:30 | 137.93 | 137.27
2018-06-04 15:00 | 143.51 | 142.95
2018-06-04 15:30 | 135.15 | 134.93
2018-06-04 16:00 | 54.98 | 54.79
2018-06-04 16:30 | 51.23 | 51.19
2018-06-04 17:00 | 62.98 | 62.93
2018-06-04 17:30 | 81.11 | 81.08
2018-06-04 18:00 | 89.61 | 89.4
2018-06-04 18:30 | 83.94 | 83.81
2018-06-04 19:00 | 80.81 | 80.74
2018-06-04 19:30 | 73.29 | 73.28
2018-06-04 20:00 | 65.97 | 65.97
2018-06-04 20:30 | 41.63 | 41.58
2018-06-04 21:00 | 57.98 | 57.97
2018-06-04 21:30 | 69.52 | 69.46
2018-06-04 22:00 | 59.56 | 59.14
2018-06-04 22:30 | 47.26 | 46.61
2018-06-04 23:00 | 68.78 | 67.89
2018-06-04 23:30 | 34.84 | 32.87
2018-06-05 | 12.03 | 1.51
2018-06-05 00:30 | 21.44 | -18.43
2018-06-05 01:00 | 30.09 | -28.8
2018-06-05 01:30 | 35.03 | -34.7
2018-06-05 02:00 | 45.28 | -45.21
2018-06-05 02:30 | 49.28 | -49.28
2018-06-05 03:00 | 36.89 | -36.73
2018-06-05 03:30 | 31.84 | -31.44
2018-06-05 04:00 | 20.26 | -18.26
2018-06-05 04:30 | 15.39 | -1.6
2018-06-05 05:00 | 29.56 | 22.85
2018-06-05 05:30 | 33.46 | 25.49
2018-06-05 06:00 | 40.77 | 34.68
2018-06-05 06:30 | 48.74 | 46.52
2018-06-05 07:00 | 58.39 | 57.24
2018-06-05 07:30 | 77.62 | 77.52
2018-06-05 08:00 | 55.52 | 54.06
2018-06-05 08:30 | 33.78 | 30.1
2018-06-05 09:00 | 27.59 | 23.62
2018-06-05 09:30 | 20.32 | -0.77
2018-06-05 10:00 | 24.53 | -13.06
2018-06-05 10:30 | 32.14 | -25.6
2018-06-05 11:00 | 37.49 | -30.78
2018-06-05 11:30 | 30.09 | -23.88
2018-06-05 12:00 | 25.83 | -19.23
2018-06-05 12:30 | 14.43 | 8.24
2018-06-05 13:00 | 23.14 | 22.28
2018-06-05 13:30 | 20.71 | 19.81
2018-06-05 14:00 | 16.43 | 15.33
2018-06-05 14:30 | 25.11 | 24.57
2018-06-05 15:00 | 49.42 | 49.09
2018-06-05 15:30 | 54.72 | 52.68
2018-06-05 16:00 | 49.72 | 47.46
2018-06-05 16:30 | 42.93 | 40.89
2018-06-05 17:00 | 39.79 | 38.13
2018-06-05 17:30 | 36.56 | 31.47
2018-06-05 18:00 | 136.51 | 134.86
2018-06-05 18:30 | 106.61 | 105.06
2018-06-05 19:00 | 97.79 | 97.69
2018-06-05 19:30 | 115.92 | 115.78
2018-06-05 20:00 | 63.44 | 63.44
2018-06-05 20:30 | 82.03 | 82
2018-06-05 21:00 | 93.31 | 93.07
2018-06-05 21:30 | 88.95 | 88.31
2018-06-05 22:00 | 86.48 | 85.26
2018-06-05 22:30 | 82.32 | 80.59
2018-06-05 23:00 | 99.41 | 97.49
2018-06-05 23:30 | 70 | 66.86
2018-06-06 | 41.25 | 34.69
2018-06-06 00:30 | 27.59 | 12.68
2018-06-06 01:00 | 24.28 | 2.12
2018-06-06 01:30 | 22.43 | -0.67
2018-06-06 02:00 | 22.38 | 3.25
2018-06-06 02:30 | 23.42 | 4.92
2018-06-06 03:00 | 25.68 | 10.46
2018-06-06 03:30 | 27.72 | 14.43
2018-06-06 04:00 | 42.43 | 31.25
2018-06-06 04:30 | 61.65 | 51.76
2018-06-06 05:00 | 81.57 | 74.76
2018-06-06 05:30 | 99.63 | 93.77
2018-06-06 06:00 | 104.44 | 99.26
2018-06-06 06:30 | 101.09 | 99.22
2018-06-06 07:00 | 84.01 | 83.34
2018-06-06 07:30 | 114.41 | 114.36
2018-06-06 08:00 | 76.58 | 76.57
2018-06-06 08:30 | 38.77 | 38.76
2018-06-06 09:00 | 6.13 | -4.3
2018-06-06 09:30 | 69.14 | -62.24
2018-06-06 10:00 | 45.53 | -36.6
2018-06-06 10:30 | 41.02 | -30.56
2018-06-06 11:00 | 45.36 | -36.22
2018-06-06 11:30 | 42.83 | -32.72
2018-06-06 12:00 | 44.71 | -34.43
2018-06-06 12:30 | 61.46 | -54.5
2018-06-06 13:00 | 31 | 17.84
2018-06-06 13:30 | 39.34 | 31.86
2018-06-06 14:00 | 35.88 | 27.52
2018-06-06 14:30 | 35.68 | 26.85
2018-06-06 15:00 | 36.45 | 28.13
2018-06-06 15:30 | 25.89 | 9.77
2018-06-06 16:00 | 25.24 | 1.76
2018-06-06 16:30 | 43.42 | 6.19
2018-06-06 17:00 | 61.13 | -44.29
2018-06-06 17:30 | 58.37 | 40.79
2018-06-06 18:00 | 81.31 | 71.6
2018-06-06 18:30 | 90.62 | 82.79
2018-06-06 19:00 | 103.36 | 97.39
2018-06-06 19:30 | 93.82 | 87.8
2018-06-06 20:00 | 79.54 | 72.94
2018-06-06 20:30 | 67.39 | 60.42
2018-06-06 21:00 | 42.25 | 40.71
2018-06-06 21:30 | 54.06 | 53.57
2018-06-06 22:00 | 44.91 | 43.67
2018-06-06 22:30 | 62.5 | 60.9
2018-06-06 23:00 | 72.23 | 70.23
2018-06-06 23:30 | 44.78 | 40.88
2018-06-07 | 21.88 | 8.76
2018-06-07 00:30 | 22.45 | -3.83
2018-06-07 01:00 | 29.15 | 10.3
2018-06-07 01:30 | 37.06 | 24.88
2018-06-07 02:00 | 41.1 | 30.74
2018-06-07 02:30 | 41.36 | 31.08
2018-06-07 03:00 | 41.07 | 30.31
2018-06-07 03:30 | 40.72 | 30.18
2018-06-07 04:00 | 44.53 | 34.56
2018-06-07 04:30 | 71.67 | 66.11
2018-06-07 05:00 | 86.92 | 80.41
2018-06-07 05:30 | 119.23 | 114.38
2018-06-07 06:00 | 120.65 | 116.45
2018-06-07 06:30 | 98.03 | 95.16
2018-06-07 07:00 | 82.76 | 80.6
2018-06-07 07:30 | 97.98 | 97.53
2018-06-07 08:00 | 86.07 | 85.29
2018-06-07 08:30 | 67.11 | 66.38
2018-06-07 09:00 | 64.87 | 64.17
2018-06-07 09:30 | 62.43 | 61.74
2018-06-07 10:00 | 65.41 | 64.58
2018-06-07 10:30 | 47.8 | 46.35
2018-06-07 11:00 | 13.05 | 6.87
2018-06-07 11:30 | 21.14 | 16.98
2018-06-07 12:00 | 6.77 | 6.45
2018-06-07 12:30 | 6.23 | 2.62
2018-06-07 13:00 | 6.71 | -0.19
2018-06-07 13:30 | 14.8 | 14.46
2018-06-07 14:00 | 10.07 | -9.62
2018-06-07 14:30 | 12.07 | -10.81
2018-06-07 15:00 | 7.47 | -5.9
2018-06-07 15:30 | 4.62 | 2.63
2018-06-07 16:00 | 29.35 | 28.81
2018-06-07 16:30 | 46.14 | 43.11
2018-06-07 17:00 | 47.27 | 44.78
2018-06-07 17:30 | 38.2 | 37.73
2018-06-07 18:00 | 47.51 | 45.21
2018-06-07 18:30 | 75.42 | 74.81
2018-06-07 19:00 | 46.6 | 45.75
2018-06-07 19:30 | 75.39 | 75.27
2018-06-07 20:00 | 92.74 | 92.65
2018-06-07 20:30 | 92.52 | 92.51
2018-06-07 21:00 | 64.95 | 64.93
2018-06-07 21:30 | 39.85 | 39.49
2018-06-07 22:00 | 8.21 | -1.77
2018-06-07 22:30 | 18.8 | 15.64
2018-06-07 23:00 | 43.63 | 41.41
2018-06-07 23:30 | 14.01 | -0.06
2018-06-08 | 29.23 | -25.64
2018-06-08 00:30 | 53.59 | -52.77
2018-06-08 01:00 | 42.04 | -39.42
2018-06-08 01:30 | 35.5 | -32.02
2018-06-08 02:00 | 39.5 | -36.76
2018-06-08 02:30 | 34.6 | -30.14
2018-06-08 03:00 | 43.33 | -41.26
2018-06-08 03:30 | 39.43 | -35.73
2018-06-08 04:00 | 32.13 | -24.46
2018-06-08 04:30 | 29.5 | -11.03
2018-06-08 05:00 | 32.71 | 14.66
2018-06-08 05:30 | 36.14 | 21.12
2018-06-08 06:00 | 48.65 | 39.63
2018-06-08 06:30 | 66.94 | 62.42
2018-06-08 07:00 | 68.78 | 68.3
2018-06-08 07:30 | 91.74 | 91.45
2018-06-08 08:00 | 76.73 | 75.58
2018-06-08 08:30 | 60.74 | 59.59
2018-06-08 09:00 | 52.51 | 51.32
2018-06-08 09:30 | 71.08 | 69.89
2018-06-08 10:00 | 60.84 | 59.42
2018-06-08 10:30 | 77.63 | 76.77
2018-06-08 11:00 | 123.68 | 122.96
2018-06-08 11:30 | 40.66 | 40.49
2018-06-08 12:00 | 33.41 | 33.18
2018-06-08 12:30 | 41.33 | 41.18
2018-06-08 13:00 | 56.78 | 56.61
2018-06-08 13:30 | 55.62 | 55.49
2018-06-08 14:00 | 28.63 | 28.21
2018-06-08 14:30 | 37.99 | -1.86
2018-06-08 15:00 | 35.92 | 5.1
2018-06-08 15:30 | 53.35 | -37.98
2018-06-08 16:00 | 81.26 | -76.17
2018-06-08 16:30 | 73.23 | -68.33
2018-06-08 17:00 | 69.4 | -63.85
2018-06-08 17:30 | 49.58 | -21.95
2018-06-08 18:00 | 85.1 | -47.2
2018-06-08 18:30 | 89.27 | -57.82
2018-06-08 19:00 | 86.71 | -56.08
2018-06-08 19:30 | 76.98 | -47.07
2018-06-08 20:00 | 87.18 | -63.41
2018-06-08 20:30 | 86.64 | -64.48
2018-06-08 21:00 | 46.33 | -21.01
2018-06-08 21:30 | 50.29 | -40.33
2018-06-08 22:00 | 72.29 | -65.77
2018-06-08 22:30 | 9.56 | 4.04
2018-06-08 23:00 | 33.64 | 24.07
2018-06-08 23:30 | 21.89 | -3.82
2018-06-09 | 53.26 | -50.74
2018-06-09 00:30 | 75.91 | -75.9
2018-06-09 01:00 | 86.32 | -85.6
2018-06-09 01:30 | 56.14 | -55.34
2018-06-09 02:00 | 50.71 | -48.57
2018-06-09 02:30 | 52.82 | -50.85
2018-06-09 03:00 | 54.94 | -53.42
2018-06-09 03:30 | 55.05 | -53.69
2018-06-09 04:00 | 56.98 | -55.33
2018-06-09 04:30 | 55.72 | -53.26
2018-06-09 05:00 | 56.8 | -54.21
2018-06-09 05:30 | 52.3 | -48.7
2018-06-09 06:00 | 38.04 | -31.48
2018-06-09 06:30 | 29.44 | -16.71
2018-06-09 07:00 | 25.09 | 2.98
2018-06-09 07:30 | 23.53 | 1.56
2018-06-09 08:00 | 20.3 | 17.03
2018-06-09 08:30 | 20.43 | 19.78
2018-06-09 09:00 | 2.69 | 2.17
2018-06-09 09:30 | 47.91 | -47.47
2018-06-09 10:00 | 60.56 | -59.89
2018-06-09 10:30 | 58.62 | -55.44
2018-06-09 11:00 | 81.58 | -75.72
2018-06-09 11:30 | 84.69 | -79.43
2018-06-09 12:00 | 80.54 | -75.06
2018-06-09 12:30 | 90.63 | -85.98
2018-06-09 13:00 | 97.37 | -93.47
2018-06-09 13:30 | 93.59 | -89.69
2018-06-09 14:00 | 88.72 | -84.41
2018-06-09 14:30 | 70.71 | -66.87
2018-06-09 15:00 | 70.37 | -66.9
2018-06-09 15:30 | 51.98 | -48.2
2018-06-09 16:00 | 22.35 | -14.81
2018-06-09 16:30 | 17.97 | 7.08
2018-06-09 17:00 | 20.64 | 6.21
2018-06-09 17:30 | 55.72 | -6.8
2018-06-09 18:00 | 52.67 | 38.22
2018-06-09 18:30 | 43.56 | 27.15
2018-06-09 19:00 | 33.08 | 5.73
2018-06-09 19:30 | 42.16 | -33.45
2018-06-09 20:00 | 33.07 | -22.12
2018-06-09 20:30 | 46.5 | -39.31
2018-06-09 21:00 | 33.85 | -27.46
2018-06-09 21:30 | 18.99 | -11.57
2018-06-09 22:00 | 25.81 | -22.11
2018-06-09 22:30 | 10.89 | 9.09
2018-06-09 23:00 | 28.69 | 25.81
2018-06-09 23:30 | 13.63 | -2.92
2018-06-10 | 25.44 | -20.36
2018-06-10 00:30 | 46.66 | -43.38
2018-06-10 01:00 | 52.11 | -48.47
2018-06-10 01:30 | 46.5 | -42.34
2018-06-10 02:00 | 45.45 | -41.59
2018-06-10 02:30 | 47.41 | -43.09
2018-06-10 03:00 | 47.55 | -42.73
2018-06-10 03:30 | 52.69 | -48.97
2018-06-10 04:00 | 50.7 | -46.65
2018-06-10 04:30 | 52.19 | -48.47
2018-06-10 05:00 | 53.85 | -50.3
2018-06-10 05:30 | 42.37 | -35.75
2018-06-10 06:00 | 30.92 | -16.96
2018-06-10 06:30 | 38.25 | -27.55
2018-06-10 07:00 | 36.96 | -26.73
2018-06-10 07:30 | 33.14 | -19.34
2018-06-10 08:00 | 32.64 | -18.5
2018-06-10 08:30 | 32.68 | -21.68
2018-06-10 09:00 | 35.33 | -32.06
2018-06-10 09:30 | 59.24 | -59.24
2018-06-10 10:00 | 61.82 | -61.73
2018-06-10 10:30 | 68.08 | -68.03
2018-06-10 11:00 | 41.36 | -41.18
2018-06-10 11:30 | 64.34 | -64.34
2018-06-10 12:00 | 41.02 | -40.65
2018-06-10 12:30 | 44.01 | -43.62
2018-06-10 13:00 | 36.39 | -35.85
2018-06-10 13:30 | 36.45 | -35.81
2018-06-10 14:00 | 28.31 | -27.44
2018-06-10 14:30 | 18.52 | -16.86
2018-06-10 15:00 | 8.87 | 3.35
2018-06-10 15:30 | 22.75 | 21.18
2018-06-10 16:00 | 45.68 | 44.68
2018-06-10 16:30 | 44.27 | 43.27
2018-06-10 17:00 | 71.86 | 71.55
2018-06-10 17:30 | 99.43 | 99.43
2018-06-10 18:00 | 117.33 | 117.28
2018-06-10 18:30 | 119.02 | 118.74
2018-06-10 19:00 | 122.8 | 122.47
2018-06-10 19:30 | 117.01 | 116.93
2018-06-10 20:00 | 121.7 | 119.45
2018-06-10 20:30 | 104.42 | 101.46
2018-06-10 21:00 | 97.85 | 94.3
2018-06-10 21:30 | 67.63 | 61.86
2018-06-10 22:00 | 42.26 | 32.49
2018-06-10 22:30 | 60.73 | 53.86
2018-06-10 23:00 | 75.37 | 69.93
2018-06-10 23:30 | 59.42 | 52.95
2018-06-11 | 32.32 | 19.18
2018-06-11 00:30 | 24.76 | -2.36
2018-06-11 01:00 | 36.44 | -28.27
2018-06-11 01:30 | 39.56 | -33.82
2018-06-11 02:00 | 42.18 | -37.81
2018-06-11 02:30 | 39.88 | -34.98
2018-06-11 03:00 | 38.62 | -33.55
2018-06-11 03:30 | 35.51 | -29.38
2018-06-11 04:00 | 32.57 | -23.77
2018-06-11 04:30 | 27.84 | -10.06
2018-06-11 05:00 | 26.95 | 1.02
2018-06-11 05:30 | 40.68 | 28.75
2018-06-11 06:00 | 64.51 | 61.42
2018-06-11 06:30 | 125.76 | 125.25
2018-06-11 07:00 | 177.76 | 177.57
2018-06-11 07:30 | 198.14 | 198.09
2018-06-11 08:00 | 173 | 172.07
2018-06-11 08:30 | 134.16 | 133.07
2018-06-11 09:00 | 93.84 | 92.04
2018-06-11 09:30 | 83.72 | 81.9
2018-06-11 10:00 | 96.5 | 94.98
2018-06-11 10:30 | 84.43 | 82.61
2018-06-11 11:00 | 77.54 | 75.41
2018-06-11 11:30 | 84.68 | 82.91
2018-06-11 12:00 | 90.95 | 89.34
2018-06-11 12:30 | 127.89 | 126.76
2018-06-11 13:00 | 81.41 | 79.61
2018-06-11 13:30 | 90.19 | 88.47
2018-06-11 14:00 | 96.98 | 95.38
2018-06-11 14:30 | 104.88 | 103.5
2018-06-11 15:00 | 112.12 | 110.88
2018-06-11 15:30 | 136.39 | 135.48
2018-06-11 16:00 | 155.31 | 154.47
2018-06-11 16:30 | 146.53 | 144.09
2018-06-11 17:00 | 155.7 | 147.67
2018-06-11 17:30 | 154.79 | 145.07
2018-06-11 18:00 | 172.62 | 163.01
2018-06-11 18:30 | 166.04 | 156.71
2018-06-11 19:00 | 165.38 | 156.3
2018-06-11 19:30 | 149.22 | 140.15
2018-06-11 20:00 | 152.04 | 151.88
2018-06-11 20:30 | 168.38 | 167.4
2018-06-11 21:00 | 139.45 | 137.8
2018-06-11 21:30 | 134.21 | 132.15
2018-06-11 22:00 | 143.1 | 140.59
2018-06-11 22:30 | 145.91 | 143.26
2018-06-11 23:00 | 138.57 | 135.55
2018-06-11 23:30 | 100.6 | 96.59
2018-06-12 | 55.61 | 48.09
2018-06-12 00:30 | 44.25 | 34.13
2018-06-12 01:00 | 28.45 | 8.08
2018-06-12 01:30 | 25.59 | -3.33
2018-06-12 02:00 | 26.98 | -10.54
2018-06-12 02:30 | 26.76 | -9.9
2018-06-12 03:00 | 25.4 | -5.99
2018-06-12 03:30 | 28.86 | -15.25
2018-06-12 04:00 | 28.06 | -12.12
2018-06-12 04:30 | 26.49 | -3.85
2018-06-12 05:00 | 49.69 | 40.89
2018-06-12 05:30 | 67.36 | 60.93
2018-06-12 06:00 | 102.13 | 98.46
2018-06-12 06:30 | 112.87 | 110.59
2018-06-12 07:00 | 134.43 | 133.58
2018-06-12 07:30 | 166.23 | 165.79
2018-06-12 08:00 | 132.86 | 132.35
2018-06-12 08:30 | 82.05 | 81.18
2018-06-12 09:00 | 48.46 | 46.67
2018-06-12 09:30 | 44.6 | 43.43
2018-06-12 10:00 | 17.94 | 14.84
2018-06-12 10:30 | 35.79 | 34.77
2018-06-12 11:00 | 42.73 | 42.55
2018-06-12 11:30 | 2.91 | -0.05
2018-06-12 12:00 | 8.05 | -7.46
2018-06-12 12:30 | 4.45 | -1.77
2018-06-12 13:00 | 6.11 | 5.36
2018-06-12 13:30 | 8.08 | 7.5
2018-06-12 14:00 | 28.32 | 28.11
2018-06-12 14:30 | 33.35 | 33.34
2018-06-12 15:00 | 49.1 | 48.63
2018-06-12 15:30 | 78.17 | 77.98
2018-06-12 16:00 | 116.54 | 116.5
2018-06-12 16:30 | 135.49 | 135.31
2018-06-12 17:00 | 133.09 | 132.91
2018-06-12 17:30 | 138.17 | 138.16
2018-06-12 18:00 | 134.75 | 134.71
2018-06-12 18:30 | 119.9 | 119.83
2018-06-12 19:00 | 149.23 | 149.18
2018-06-12 19:30 | 146.29 | 146.29
2018-06-12 20:00 | 130.39 | 130.38
2018-06-12 20:30 | 111.75 | 111.69
2018-06-12 21:00 | 100.86 | 100.85
2018-06-12 21:30 | 83.73 | 83.69
2018-06-12 22:00 | 86.59 | 86.36
2018-06-12 22:30 | 101.55 | 101.07
2018-06-12 23:00 | 107.59 | 106.98
2018-06-12 23:30 | 75.72 | 74.92
2018-06-13 | 37.9 | 35.62
2018-06-13 00:30 | 16.28 | 2.75
2018-06-13 01:00 | 25.18 | -19.48
2018-06-13 01:30 | 20.17 | -15.63
2018-06-13 02:00 | 20.2 | -15.31
2018-06-13 02:30 | 20.57 | -16.43
2018-06-13 03:00 | 16.26 | -9.23
2018-06-13 03:30 | 15.62 | -7.27
2018-06-13 04:00 | 17.19 | -9.73
2018-06-13 04:30 | 16.39 | 3.59
2018-06-13 05:00 | 33.82 | 28.33
2018-06-13 05:30 | 70 | 66.65
2018-06-13 06:00 | 101.71 | 99.56
2018-06-13 06:30 | 118.05 | 117.15
2018-06-13 07:00 | 126.83 | 126.59
2018-06-13 07:30 | 138.36 | 137.91
2018-06-13 08:00 | 131.14 | 130.48
2018-06-13 08:30 | 112.19 | 111.33
2018-06-13 09:00 | 105.02 | 104
2018-06-13 09:30 | 96.31 | 95.21
2018-06-13 10:00 | 92.79 | 91.42
2018-06-13 10:30 | 105.32 | 104.31
2018-06-13 11:00 | 96.64 | 96.28
2018-06-13 11:30 | 103.59 | 103.59
2018-06-13 12:00 | 106.29 | 106.07
2018-06-13 12:30 | 109.3 | 109.17
2018-06-13 13:00 | 116.48 | 116.35
2018-06-13 13:30 | 112.43 | 112.37
2018-06-13 14:00 | 118.92 | 118.85
2018-06-13 14:30 | 130.22 | 130.14
2018-06-13 15:00 | 120.69 | 120.61
2018-06-13 15:30 | 117.17 | 117.14
2018-06-13 16:00 | 125.33 | 125.32
2018-06-13 16:30 | 138.53 | 138.52
2018-06-13 17:00 | 149.39 | 149.33
2018-06-13 17:30 | 149.04 | 148.68
2018-06-13 18:00 | 105.21 | 104.73
2018-06-13 18:30 | 103.43 | 103.14
2018-06-13 19:00 | 100.36 | 100.11
2018-06-13 19:30 | 89.01 | 88.63
2018-06-13 20:00 | 79.04 | 78.71
2018-06-13 20:30 | 74.19 | 74.08
2018-06-13 21:00 | 44.92 | 44.92
2018-06-13 21:30 | 43.81 | 43.32
2018-06-13 22:00 | 37.28 | 36.29
2018-06-13 22:30 | 51.14 | 50
2018-06-13 23:00 | 76.9 | 75.75
2018-06-13 23:30 | 60.85 | 58.82
2018-06-14 | 33.16 | 27.62
2018-06-14 00:30 | 15.92 | 4.29
2018-06-14 01:00 | 18.14 | -12.84
2018-06-14 01:30 | 17.65 | -13.53
2018-06-14 02:00 | 17.75 | -14.22
2018-06-14 02:30 | 23.77 | -21.65
2018-06-14 03:00 | 16.88 | -13.12
2018-06-14 03:30 | 12.51 | -4.72
2018-06-14 04:00 | 11.54 | -0.92
2018-06-14 04:30 | 19.8 | 13.71
2018-06-14 05:00 | 33.71 | 28.98
2018-06-14 05:30 | 52.92 | 48.41
2018-06-14 06:00 | 78.98 | 75.95
2018-06-14 06:30 | 88.06 | 86.14
2018-06-14 07:00 | 82.16 | 81.32
2018-06-14 07:30 | 119.3 | 119.3
2018-06-14 08:00 | 122.78 | 122.77
2018-06-14 08:30 | 112.69 | 112.64
2018-06-14 09:00 | 110.06 | 109.95
2018-06-14 09:30 | 100.31 | 100.21
2018-06-14 10:00 | 104.17 | 104.05
2018-06-14 10:30 | 102.96 | 102.77
2018-06-14 11:00 | 106.17 | 105.99
2018-06-14 11:30 | 101.43 | 101.22
2018-06-14 12:00 | 96.07 | 95.86
2018-06-14 12:30 | 94.12 | 93.95
2018-06-14 13:00 | 102.67 | 102.5
2018-06-14 13:30 | 104.5 | 104.34
2018-06-14 14:00 | 106.47 | 106.32
2018-06-14 14:30 | 104.84 | 104.69
2018-06-14 15:00 | 116.54 | 116.41
2018-06-14 15:30 | 125.64 | 125.53
2018-06-14 16:00 | 139.21 | 139.1
2018-06-14 16:30 | 137.37 | 136.77
2018-06-14 17:00 | 132.26 | 131.7
2018-06-14 17:30 | 136.64 | 136.46
2018-06-14 18:00 | 138.19 | 138.14
2018-06-14 18:30 | 146.29 | 146.25
2018-06-14 19:00 | 138.82 | 138.73
2018-06-14 19:30 | 123.66 | 123.32
2018-06-14 20:00 | 117.68 | 117.21
2018-06-14 20:30 | 112.67 | 112.06
2018-06-14 21:00 | 95.3 | 94.12
2018-06-14 21:30 | 90.08 | 89.05
2018-06-14 22:00 | 69.36 | 68.27
2018-06-14 22:30 | 84.11 | 82.88
2018-06-14 23:00 | 101.43 | 100.14
2018-06-14 23:30 | 67.7 | 65.47
2018-06-15 | 32.82 | 28.86
2018-06-15 00:30 | 14.36 | 9.07
2018-06-15 01:00 | 8.73 | -1.96
2018-06-15 01:30 | 14.52 | 10.7
2018-06-15 02:00 | 15.04 | 11.69
2018-06-15 02:30 | 10.33 | 5.45
2018-06-15 03:00 | 13.49 | 9.98
2018-06-15 03:30 | 22.74 | 20.72
2018-06-15 04:00 | 40.42 | 39.16
2018-06-15 04:30 | 54.53 | 52.75
2018-06-15 05:00 | 72.79 | 71.04
2018-06-15 05:30 | 94.93 | 92.85
2018-06-15 06:00 | 94.72 | 91.72
2018-06-15 06:30 | 105.46 | 102.99
2018-06-15 07:00 | 105.16 | 103.39
2018-06-15 07:30 | 112.68 | 112.58
2018-06-15 08:00 | 108.68 | 108.2
2018-06-15 08:30 | 99.48 | 99.05
2018-06-15 09:00 | 93.5 | 93.01
2018-06-15 09:30 | 78.21 | 77.55
2018-06-15 10:00 | 77.76 | 77.14
2018-06-15 10:30 | 68.26 | 68.26
2018-06-15 11:00 | 65.35 | 65.34
2018-06-15 11:30 | 67.42 | 67.4
2018-06-15 12:00 | 69.36 | 69.34
2018-06-15 12:30 | 69.24 | 69.22
2018-06-15 13:00 | 67.82 | 67.8
2018-06-15 13:30 | 69.19 | 69.18
2018-06-15 14:00 | 85.48 | 85.47
2018-06-15 14:30 | 82.96 | 82.94
2018-06-15 15:00 | 86.5 | 86.5
2018-06-15 15:30 | 104.27 | 104.2
2018-06-15 16:00 | 106.73 | 106.62
2018-06-15 16:30 | 109.29 | 109.19
2018-06-15 17:00 | 115.34 | 115.27
2018-06-15 17:30 | 81.52 | 80.66
2018-06-15 18:00 | 76.29 | 75.55
2018-06-15 18:30 | 96.74 | 96.14
2018-06-15 19:00 | 96.34 | 95.51
2018-06-15 19:30 | 100.66 | 99.59
2018-06-15 20:00 | 102.63 | 100.99
2018-06-15 20:30 | 93.98 | 92.04
2018-06-15 21:00 | 84.56 | 83.69
2018-06-15 21:30 | 80.34 | 79.37
2018-06-15 22:00 | 72.94 | 71.35
2018-06-15 22:30 | 89.5 | 87.9
2018-06-15 23:00 | 109.17 | 107.46
2018-06-15 23:30 | 87.22 | 84.7
2018-06-16 | 56.39 | 49.7
2018-06-16 00:30 | 38.42 | 25.53
2018-06-16 01:00 | 33.77 | 20.67
2018-06-16 01:30 | 31.3 | 19.48
2018-06-16 02:00 | 26.07 | 10.88
2018-06-16 02:30 | 27.14 | 11.59
2018-06-16 03:00 | 33.96 | 23.03
2018-06-16 03:30 | 43.1 | 41.37
2018-06-16 04:00 | 46.9 | 45.5
2018-06-16 04:30 | 46.99 | 45.21
2018-06-16 05:00 | 80.59 | 79.58
2018-06-16 05:30 | 123.47 | 122.86
2018-06-16 06:00 | 133.36 | 132.26
2018-06-16 06:30 | 146.84 | 145.73
2018-06-16 07:00 | 128.29 | 128.23
2018-06-16 07:30 | 160.29 | 159.48
2018-06-16 08:00 | 156.67 | 156.1
2018-06-16 08:30 | 137.43 | 136.95
2018-06-16 09:00 | 124.99 | 124.49
2018-06-16 09:30 | 92.76 | 92.07
2018-06-16 10:00 | 96.14 | 95.44
2018-06-16 10:30 | 89.23 | 88.52
2018-06-16 11:00 | 78.81 | 77.96
2018-06-16 11:30 | 84.44 | 83.59
2018-06-16 12:00 | 79.77 | 78.79
2018-06-16 12:30 | 76.85 | 75.82
2018-06-16 13:00 | 75.81 | 74.81
2018-06-16 13:30 | 72.12 | 71.07
2018-06-16 14:00 | 87.71 | 86.64
2018-06-16 14:30 | 91.31 | 90.24
2018-06-16 15:00 | 88.58 | 87.56
2018-06-16 15:30 | 96.07 | 95.12
2018-06-16 16:00 | 105.56 | 104.66
2018-06-16 16:30 | 113.26 | 112.59
2018-06-16 17:00 | 125.58 | 125.25
2018-06-16 17:30 | 133.71 | 132.6
2018-06-16 18:00 | 140.45 | 139.29
2018-06-16 18:30 | 149 | 147.87
2018-06-16 19:00 | 154.53 | 153.33
2018-06-16 19:30 | 144.65 | 143.21
2018-06-16 20:00 | 143.7 | 142.98
2018-06-16 20:30 | 131.47 | 131.17
2018-06-16 21:00 | 105.54 | 105.03
2018-06-16 21:30 | 101.37 | 100.59
2018-06-16 22:00 | 83.29 | 81.96
2018-06-16 22:30 | 122.7 | 121.57
2018-06-16 23:00 | 138.55 | 137.5
2018-06-16 23:30 | 114.58 | 113.04
2018-06-17 | 79.16 | 76.29
2018-06-17 00:30 | 57.8 | 53.95
2018-06-17 01:00 | 30.88 | 24.22
2018-06-17 01:30 | 29.48 | 22.66
2018-06-17 02:00 | 24.59 | 16.13
2018-06-17 02:30 | 26.4 | 14.33
2018-06-17 03:00 | 30.48 | 10.02
2018-06-17 03:30 | 32.21 | 14.48
2018-06-17 04:00 | 41.09 | 29.31
2018-06-17 04:30 | 65.85 | 58.76
2018-06-17 05:00 | 73.06 | 66.35
2018-06-17 05:30 | 68.38 | 60.56
2018-06-17 06:00 | 54.55 | 43.35
2018-06-17 06:30 | 71.08 | 61.92
2018-06-17 07:00 | 84.86 | 78.18
2018-06-17 07:30 | 101.99 | 95.94
2018-06-17 08:00 | 115.23 | 110.15
2018-06-17 08:30 | 98.43 | 93.69
2018-06-17 09:00 | 78.16 | 72.51
2018-06-17 09:30 | 68.78 | 62.33
2018-06-17 10:00 | 51.61 | 41.93
2018-06-17 10:30 | 37.94 | 23.68
2018-06-17 11:00 | 28.87 | -1.03
2018-06-17 11:30 | 33.32 | -19.18
2018-06-17 12:00 | 36.88 | -25.82
2018-06-17 12:30 | 37.33 | -26.55
2018-06-17 13:00 | 32.61 | -18.99
2018-06-17 13:30 | 32.88 | -19.73
2018-06-17 14:00 | 27.99 | -2.84
2018-06-17 14:30 | 30.04 | 7.74
2018-06-17 15:00 | 33.01 | 13.97
2018-06-17 15:30 | 54.08 | 44.19
2018-06-17 16:00 | 65.87 | 58.29
2018-06-17 16:30 | 104.19 | 101.15
2018-06-17 17:00 | 139.45 | 139.22
2018-06-17 17:30 | 175.94 | 175.35
2018-06-17 18:00 | 184.86 | 184.57
2018-06-17 18:30 | 190.51 | 190.26
2018-06-17 19:00 | 188.89 | 188.59
2018-06-17 19:30 | 182.6 | 182.17
2018-06-17 20:00 | 187.59 | 187.03
2018-06-17 20:30 | 184.72 | 184.42
2018-06-17 21:00 | 170.94 | 170.49
2018-06-17 21:30 | 145.61 | 145.36
2018-06-17 22:00 | 128.91 | 128.81
2018-06-17 22:30 | 142.89 | 142.88
2018-06-17 23:00 | 155.55 | 155.55
2018-06-17 23:30 | 113.03 | 113
2018-06-18 | 77.58 | 77.46
2018-06-18 00:30 | 59.78 | 55.48
2018-06-18 01:00 | 51.07 | 40.32
2018-06-18 01:30 | 42.56 | 29.43
2018-06-18 02:00 | 38.63 | 26.44
2018-06-18 02:30 | 32.14 | 16.17
2018-06-18 03:00 | 29.41 | 10.52
2018-06-18 03:30 | 33.91 | 19.47
2018-06-18 04:00 | 43.11 | 32.08
2018-06-18 04:30 | 51.47 | 41.44
2018-06-18 05:00 | 72 | 64.19
2018-06-18 05:30 | 102.82 | 97.55
2018-06-18 06:00 | 126.27 | 122.49
2018-06-18 06:30 | 144 | 143.42
2018-06-18 07:00 | 165.99 | 165.99
2018-06-18 07:30 | 194.3 | 194.23
2018-06-18 08:00 | 141.36 | 141.22
2018-06-18 08:30 | 112.5 | 112.31
2018-06-18 09:00 | 104.94 | 104.86
2018-06-18 09:30 | 87.86 | 87.85
2018-06-18 10:00 | 84.87 | 84.86
2018-06-18 10:30 | 73.48 | 73.15
2018-06-18 11:00 | 71.38 | 71.37
2018-06-18 11:30 | 69.29 | 69.26
2018-06-18 12:00 | 68.41 | 68.38
2018-06-18 12:30 | 76.88 | 76.82
2018-06-18 13:00 | 66.13 | 66.05
2018-06-18 13:30 | 78.26 | 78.2
2018-06-18 14:00 | 79.98 | 79.95
2018-06-18 14:30 | 85.77 | 85.72
2018-06-18 15:00 | 85.28 | 85.2
2018-06-18 15:30 | 90.1 | 90.02
2018-06-18 16:00 | 106.65 | 106
2018-06-18 16:30 | 143.41 | 140.53
2018-06-18 17:00 | 154.64 | 151.48
2018-06-18 17:30 | 154.65 | 148.43
2018-06-18 18:00 | 167.92 | 160.3
2018-06-18 18:30 | 177.02 | 170.33
2018-06-18 19:00 | 190.38 | 184.54
2018-06-18 19:30 | 177.92 | 174.14
2018-06-18 20:00 | 166.1 | 164.79
2018-06-18 20:30 | 150.44 | 149.21
2018-06-18 21:00 | 180.09 | 177.5
2018-06-18 21:30 | 171.31 | 169.48
2018-06-18 22:00 | 135.11 | 133.75
2018-06-18 22:30 | 144.42 | 144.37
2018-06-18 23:00 | 142.65 | 141.79
2018-06-18 23:30 | 96.99 | 95.32
2018-06-19 | 55.81 | 51.99
2018-06-19 00:30 | 42.8 | 37.12
2018-06-19 01:00 | 23.61 | 12.06
2018-06-19 01:30 | 19.06 | -0.55
2018-06-19 02:00 | 18.27 | -5.2
2018-06-19 02:30 | 23.25 | -15.23
2018-06-19 03:00 | 22.95 | -14.98
2018-06-19 03:30 | 31.78 | -26.63
2018-06-19 04:00 | 31.01 | -25.7
2018-06-19 04:30 | 20.33 | -6.32
2018-06-19 05:00 | 24.38 | 12.76
2018-06-19 05:30 | 48.61 | 45.03
2018-06-19 06:00 | 81.96 | 80.68
2018-06-19 06:30 | 115.31 | 115.02
2018-06-19 07:00 | 130.19 | 130
2018-06-19 07:30 | 171.17 | 171.01
2018-06-19 08:00 | 140.75 | 140.47
2018-06-19 08:30 | 123.65 | 123.33
2018-06-19 09:00 | 108.11 | 107.68
2018-06-19 09:30 | 94.25 | 93.25
2018-06-19 10:00 | 94.69 | 93.36
2018-06-19 10:30 | 80.99 | 80.68
2018-06-19 11:00 | 68.31 | 66.46
2018-06-19 11:30 | 59.55 | 57.15
2018-06-19 12:00 | 56.37 | 53.74
2018-06-19 12:30 | 48.56 | 45.41
2018-06-19 13:00 | 45.25 | 41.7
2018-06-19 13:30 | 55.11 | 52.04
2018-06-19 14:00 | 58.84 | 55.9
2018-06-19 14:30 | 68.96 | 66.33
2018-06-19 15:00 | 64.82 | 61.89
2018-06-19 15:30 | 71.39 | 68.55
2018-06-19 16:00 | 90.89 | 88.65
2018-06-19 16:30 | 98.19 | 96.4
2018-06-19 17:00 | 110.87 | 109.87
2018-06-19 17:30 | 131.81 | 130.56
2018-06-19 18:00 | 158.14 | 150.64
2018-06-19 18:30 | 159.19 | 152.02
2018-06-19 19:00 | 172.46 | 166.51
2018-06-19 19:30 | 157.88 | 156.21
2018-06-19 20:00 | 161.16 | 159.7
2018-06-19 20:30 | 159.82 | 158.84
2018-06-19 21:00 | 162.15 | 162.15
2018-06-19 21:30 | 154.28 | 154.28
2018-06-19 22:00 | 127.09 | 127.08
2018-06-19 22:30 | 95.57 | 95.51
2018-06-19 23:00 | 93.73 | 93.13
2018-06-19 23:30 | 60.33 | 55.94
2018-06-20 | 46.01 | 39.81
2018-06-20 00:30 | 42.34 | 34.66
2018-06-20 01:00 | 25.92 | 10.29
2018-06-20 01:30 | 24.44 | -10.6
2018-06-20 02:00 | 32.49 | -23.83
2018-06-20 02:30 | 25.24 | -10.83
2018-06-20 03:00 | 30.61 | 14.72
2018-06-20 03:30 | 41.88 | 31.34
2018-06-20 04:00 | 46.62 | 38.45
2018-06-20 04:30 | 34.17 | 23.11
2018-06-20 05:00 | 42.11 | 33.86
2018-06-20 05:30 | 66.05 | 58.84
2018-06-20 06:00 | 113.4 | 109.53
2018-06-20 06:30 | 153.79 | 152.16
2018-06-20 07:00 | 158.87 | 158.82
2018-06-20 07:30 | 164.81 | 164.39
2018-06-20 08:00 | 132.71 | 132.32
2018-06-20 08:30 | 110.63 | 110.19
2018-06-20 09:00 | 95.63 | 94.89
2018-06-20 09:30 | 89.46 | 88.38
2018-06-20 10:00 | 82.66 | 81.48
2018-06-20 10:30 | 73.39 | 71.8
2018-06-20 11:00 | 60.77 | 59.59
2018-06-20 11:30 | 58.73 | 58.69
2018-06-20 12:00 | 57.54 | 57.54
2018-06-20 12:30 | 52.6 | 52.59
2018-06-20 13:00 | 56.53 | 56.52
2018-06-20 13:30 | 60.5 | 60.5
2018-06-20 14:00 | 65.1 | 65.09
2018-06-20 14:30 | 69.11 | 69.11
2018-06-20 15:00 | 66.06 | 66.06
2018-06-20 15:30 | 67.5 | 67.49
2018-06-20 16:00 | 74.56 | 74.53
2018-06-20 16:30 | 82.08 | 81.54
2018-06-20 17:00 | 79.33 | 79.3
2018-06-20 17:30 | 95.11 | 92.55
2018-06-20 18:00 | 86.71 | 82.72
2018-06-20 18:30 | 74.36 | 70.03
2018-06-20 19:00 | 89.74 | 86.47
2018-06-20 19:30 | 96.07 | 93.79
2018-06-20 20:00 | 100.11 | 98.45
2018-06-20 20:30 | 93.69 | 92.31
2018-06-20 21:00 | 89.27 | 89.2
2018-06-20 21:30 | 106.12 | 106.02
2018-06-20 22:00 | 99.63 | 98.93
2018-06-20 22:30 | 100.18 | 99.02
2018-06-20 23:00 | 129.26 | 128.1
2018-06-20 23:30 | 95.84 | 93.79
2018-06-21 | 60.52 | 57.03
2018-06-21 00:30 | 37.88 | 32.45
2018-06-21 01:00 | 21.88 | 12.2
2018-06-21 01:30 | 20.25 | -8.3
2018-06-21 02:00 | 24.22 | -15.99
2018-06-21 02:30 | 24.76 | -16.45
2018-06-21 03:00 | 28.14 | -21.13
2018-06-21 03:30 | 22.33 | -12.09
2018-06-21 04:00 | 19.41 | 4.19
2018-06-21 04:30 | 24.22 | 13.81
2018-06-21 05:00 | 41.23 | 35.78
2018-06-21 05:30 | 60.07 | 56.88
2018-06-21 06:00 | 79.42 | 77.83
2018-06-21 06:30 | 110.7 | 110.32
2018-06-21 07:00 | 124.88 | 124.43
2018-06-21 07:30 | 154.81 | 150.95
2018-06-21 08:00 | 103.97 | 88.38
2018-06-21 08:30 | 68.65 | -28.26
2018-06-21 09:00 | 97.47 | -72.21
2018-06-21 09:30 | 96.69 | -72.52
2018-06-21 10:00 | 59.38 | -17.51
2018-06-21 10:30 | 70.65 | -40.88
2018-06-21 11:00 | 104.05 | -83.46
2018-06-21 11:30 | 112.47 | -93.42
2018-06-21 12:00 | 119.07 | -100.92
2018-06-21 12:30 | 101.37 | -81.01
2018-06-21 13:00 | 88.75 | -66.28
2018-06-21 13:30 | 62.86 | -29.55
2018-06-21 14:00 | 54.12 | -1.8
2018-06-21 14:30 | 52.08 | 5.58
2018-06-21 15:00 | 62.09 | -32.39
2018-06-21 15:30 | 85.83 | -64.93
2018-06-21 16:00 | 52.48 | -4.87
2018-06-21 16:30 | 55.42 | 23.47
2018-06-21 17:00 | 70.69 | 46.86
2018-06-21 17:30 | 72.03 | 28.31
2018-06-21 18:00 | 83.28 | -25.42
2018-06-21 18:30 | 99.48 | -40.7
2018-06-21 19:00 | 87.85 | -21.21
2018-06-21 19:30 | 83.3 | -18.11
2018-06-21 20:00 | 79.6 | 26.09
2018-06-21 20:30 | 75.98 | -13.72
2018-06-21 21:00 | 58.81 | 0.42
2018-06-21 21:30 | 60.65 | 49.72
2018-06-21 22:00 | 53.44 | 52.39
2018-06-21 22:30 | 30.83 | 27.21
2018-06-21 23:00 | 51.95 | 49.43
2018-06-21 23:30 | 28.41 | 22.81
2018-06-22 | 21.46 | -10.39
2018-06-22 00:30 | 41.26 | -36.68
2018-06-22 01:00 | 52.45 | -49.41
2018-06-22 01:30 | 57.04 | -54.66
2018-06-22 02:00 | 57.41 | -55.08
2018-06-22 02:30 | 61.92 | -60.05
2018-06-22 03:00 | 55.98 | -53.63
2018-06-22 03:30 | 48.83 | -45.46
2018-06-22 04:00 | 44.36 | -40.67
2018-06-22 04:30 | 26.18 | -17.69
2018-06-22 05:00 | 33.16 | 26.02
2018-06-22 05:30 | 48.93 | 43.52
2018-06-22 06:00 | 41.87 | 37.37
2018-06-22 06:30 | 34.73 | 32.47
2018-06-22 07:00 | 34.01 | 33.02
2018-06-22 07:30 | 42.94 | 40.49
2018-06-22 08:00 | 42.67 | 23.97
2018-06-22 08:30 | 61.18 | -26.76
2018-06-22 09:00 | 38.2 | 2.84
2018-06-22 09:30 | 29.03 | -1.4
2018-06-22 10:00 | 34.18 | -17.5
2018-06-22 10:30 | 69.91 | -61.31
2018-06-22 11:00 | 53.62 | -42.05
2018-06-22 11:30 | 63.7 | -53.06
2018-06-22 12:00 | 38.38 | -22.36
2018-06-22 12:30 | 17.38 | -17.37
2018-06-22 13:00 | 23.56 | -23.52
2018-06-22 13:30 | 24.65 | -24.62
2018-06-22 14:00 | 18.37 | -18.32
2018-06-22 14:30 | 13.99 | -13.93
2018-06-22 15:00 | 17.25 | -14.43
2018-06-22 15:30 | 22.81 | -6.41
2018-06-22 16:00 | 48.43 | -3.75
2018-06-22 16:30 | 50.56 | -9.88
2018-06-22 17:00 | 52.9 | 19.02
2018-06-22 17:30 | 57.45 | 18.48
2018-06-22 18:00 | 64.58 | 25.75
2018-06-22 18:30 | 58.31 | 1.1
2018-06-22 19:00 | 70.57 | -37.63
2018-06-22 19:30 | 87.21 | -63.26
2018-06-22 20:00 | 57.39 | -17.57
2018-06-22 20:30 | 57.11 | -21
2018-06-22 21:00 | 54.7 | -20.92
2018-06-22 21:30 | 93.75 | -77.58
2018-06-22 22:00 | 64.06 | -51.72
2018-06-22 22:30 | 10.21 | 4.07
2018-06-22 23:00 | 35.2 | 32.46
2018-06-22 23:30 | 19.59 | 10.85
2018-06-23 | 21.49 | -11.68
2018-06-23 00:30 | 28.83 | -22.02
2018-06-23 01:00 | 34.46 | -28.98
2018-06-23 01:30 | 38.85 | -33.43
2018-06-23 02:00 | 50.66 | -47.18
2018-06-23 02:30 | 50.26 | -46.6
2018-06-23 03:00 | 41.66 | -37.26
2018-06-23 03:30 | 28.46 | -21.12
2018-06-23 04:00 | 28.45 | -21.31
2018-06-23 04:30 | 21.18 | -6.19
2018-06-23 05:00 | 23.02 | 6.58
2018-06-23 05:30 | 32.97 | 24.73
2018-06-23 06:00 | 46.39 | 41.54
2018-06-23 06:30 | 32.77 | 26.46
2018-06-23 07:00 | 36.22 | 31.79
2018-06-23 07:30 | 41.48 | 38.77
2018-06-23 08:00 | 16.22 | 12.65
2018-06-23 08:30 | 8.49 | -5.92
2018-06-23 09:00 | 10.71 | -9.51
2018-06-23 09:30 | 87.48 | -84.6
2018-06-23 10:00 | 85.41 | -82.07
2018-06-23 10:30 | 92.36 | -89.36
2018-06-23 11:00 | 91.25 | -88.49
2018-06-23 11:30 | 72.82 | -70.6
2018-06-23 12:00 | 41.09 | -39.31
2018-06-23 12:30 | 31.18 | -29.59
2018-06-23 13:00 | 24.08 | -22.75
2018-06-23 13:30 | 22.68 | -21.29
2018-06-23 14:00 | 14.02 | -12.31
2018-06-23 14:30 | 6.91 | 1.97
2018-06-23 15:00 | 7.81 | 4.35
2018-06-23 15:30 | 38.81 | 38.39
2018-06-23 16:00 | 20.37 | 18.72
2018-06-23 16:30 | 91.03 | 90.71
2018-06-23 17:00 | 36.15 | 34.22
2018-06-23 17:30 | 64.46 | 60.8
2018-06-23 18:00 | 92.07 | 77.91
2018-06-23 18:30 | 98.59 | 85.11
2018-06-23 19:00 | 113.35 | 103.78
2018-06-23 19:30 | 98.05 | 94.87
2018-06-23 20:00 | 77.96 | 77.76
2018-06-23 20:30 | 53.43 | 53.21
2018-06-23 21:00 | 38.91 | 38.39
2018-06-23 21:30 | 36.86 | 36.13
2018-06-23 22:00 | 18.85 | 16.92
2018-06-23 22:30 | 23.34 | 20.89
2018-06-23 23:00 | 39.26 | 37.55
2018-06-23 23:30 | 24.45 | 20.51
2018-06-24 | 16.69 | 4.88
2018-06-24 00:30 | 18.17 | 3.89
2018-06-24 01:00 | 18.05 | -3.71
2018-06-24 01:30 | 20.83 | -12.64
2018-06-24 02:00 | 25.76 | -20.31
2018-06-24 02:30 | 22.92 | -8.55
2018-06-24 03:00 | 26.01 | -16.34
2018-06-24 03:30 | 40.04 | -35.03
2018-06-24 04:00 | 42.41 | -37.54
2018-06-24 04:30 | 37.12 | -31.06
2018-06-24 05:00 | 25.98 | -15.56
2018-06-24 05:30 | 23.06 | 2.28
2018-06-24 06:00 | 27.08 | 6.42
2018-06-24 06:30 | 26.96 | 13.13
2018-06-24 07:00 | 36.9 | 30.67
2018-06-24 07:30 | 52.39 | 49.02
2018-06-24 08:00 | 42.49 | 39.32
2018-06-24 08:30 | 17.97 | 12.27
2018-06-24 09:00 | 12.17 | -5.25
2018-06-24 09:30 | 21.33 | -19.17
2018-06-24 10:00 | 18.97 | -16.69
2018-06-24 10:30 | 18.85 | -16.09
2018-06-24 11:00 | 18.55 | -15.52
2018-06-24 11:30 | 25.65 | -23.39
2018-06-24 12:00 | 22.66 | -20.19
2018-06-24 12:30 | 24.3 | -21.79
2018-06-24 13:00 | 24.03 | -21.5
2018-06-24 13:30 | 31.44 | -29.66
2018-06-24 14:00 | 46.97 | -46.07
2018-06-24 14:30 | 21.37 | -18.83
2018-06-24 15:00 | 19.67 | -16.9
2018-06-24 15:30 | 11.94 | -5.45
2018-06-24 16:00 | 21.05 | 18.75
2018-06-24 16:30 | 29.52 | 28.48
2018-06-24 17:00 | 28.74 | 28.73
2018-06-24 17:30 | 73.69 | 72.12
2018-06-24 18:00 | 85.84 | 76.44
2018-06-24 18:30 | 85.21 | 80.54
2018-06-24 19:00 | 86.22 | 84.67
2018-06-24 19:30 | 91.96 | 90.89
2018-06-24 20:00 | 79.69 | 78.65
2018-06-24 20:30 | 67.4 | 66.84
2018-06-24 21:00 | 47.16 | 47.09
2018-06-24 21:30 | 51.09 | 51.08
2018-06-24 22:00 | 47.94 | 47.25
2018-06-24 22:30 | 67.42 | 64.26
2018-06-24 23:00 | 88.71 | 85.82
2018-06-24 23:30 | 73.94 | 70.71
2018-06-25 | 51.66 | 46.72
2018-06-25 00:30 | 49.44 | 43.64
2018-06-25 01:00 | 43.2 | 35.76
2018-06-25 01:30 | 36.92 | 23.81
2018-06-25 02:00 | 33.28 | 15.57
2018-06-25 02:30 | 30.97 | 9.64
2018-06-25 03:00 | 29.09 | -4.07
2018-06-25 03:30 | 29.16 | -3.13
2018-06-25 04:00 | 30.71 | -12.33
2018-06-25 04:30 | 30.5 | -9.84
2018-06-25 05:00 | 30.26 | 4.55
2018-06-25 05:30 | 51.3 | 41.22
2018-06-25 06:00 | 53.02 | 45.47
2018-06-25 06:30 | 34.67 | 32.19
2018-06-25 07:00 | 28.46 | 28.44
2018-06-25 07:30 | 128.8 | 127.59
2018-06-25 08:00 | 74.06 | 73.63
2018-06-25 08:30 | 68.67 | 67.94
2018-06-25 09:00 | 87.16 | 86.69
2018-06-25 09:30 | 99.87 | 99.54
2018-06-25 10:00 | 86.59 | 86.29
2018-06-25 10:30 | 55.79 | 49.82
2018-06-25 11:00 | 45.35 | 38.18
2018-06-25 11:30 | 38.61 | 29.88
2018-06-25 12:00 | 26.45 | 10.81
2018-06-25 12:30 | 30.85 | 20.55
2018-06-25 13:00 | 42.58 | 35.94
2018-06-25 13:30 | 55.69 | 51.21
2018-06-25 14:00 | 48.3 | 43.09
2018-06-25 14:30 | 46.97 | 41.3
2018-06-25 15:00 | 40.52 | 33.92
2018-06-25 15:30 | 50.41 | 45.93
2018-06-25 16:00 | 91.52 | 89.43
2018-06-25 16:30 | 90.07 | 89.82
2018-06-25 17:00 | 87.28 | 87.22
2018-06-25 17:30 | 104.72 | 104.06
2018-06-25 18:00 | 82.16 | 80.97
2018-06-25 18:30 | 73.82 | 73.06
2018-06-25 19:00 | 65.09 | 64.51
2018-06-25 19:30 | 81.08 | 80.94
2018-06-25 20:00 | 85.85 | 85.82
2018-06-25 20:30 | 78.59 | 78.59
2018-06-25 21:00 | 62.69 | 62.6
2018-06-25 21:30 | 52.63 | 51.24
2018-06-25 22:00 | 33.43 | 30.59
2018-06-25 22:30 | 41.78 | -40.69
2018-06-25 23:00 | 38.46 | 38.02
2018-06-25 23:30 | 42.69 | 42.36
2018-06-26 | 42.83 | 37.61
2018-06-26 00:30 | 24.94 | 14.64
2018-06-26 01:00 | 19.2 | -4.54
2018-06-26 01:30 | 18.83 | -2.66
2018-06-26 02:00 | 18.74 | 1.15
2018-06-26 02:30 | 19.28 | -3.38
2018-06-26 03:00 | 19.51 | -2.12
2018-06-26 03:30 | 23.65 | -2.8
2018-06-26 04:00 | 28.3 | 6.34
2018-06-26 04:30 | 31.52 | 12
2018-06-26 05:00 | 49.86 | 40.18
2018-06-26 05:30 | 71.01 | 64.12
2018-06-26 06:00 | 79.45 | 73.86
2018-06-26 06:30 | 67.32 | 62.16
2018-06-26 07:00 | 46.87 | 45.52
2018-06-26 07:30 | 84.92 | 84.87
2018-06-26 08:00 | 90.15 | 90.15
2018-06-26 08:30 | 85.89 | 85.87
2018-06-26 09:00 | 74.56 | 74.56
2018-06-26 09:30 | 64.59 | 64.59
2018-06-26 10:00 | 56.16 | 56.16
2018-06-26 10:30 | 53.3 | 53.3
2018-06-26 11:00 | 45.36 | 45.35
2018-06-26 11:30 | 37.12 | 37.12
2018-06-26 12:00 | 43.91 | 43.91
2018-06-26 12:30 | 49.23 | 49.23
2018-06-26 13:00 | 49.43 | 49.42
2018-06-26 13:30 | 58.5 | 58.5
2018-06-26 14:00 | 50.81 | 50.81
2018-06-26 14:30 | 51.18 | 51.17
2018-06-26 15:00 | 56.12 | 56.1
2018-06-26 15:30 | 71.37 | 71.35
2018-06-26 16:00 | 74.33 | 74.31
2018-06-26 16:30 | 83.84 | 83.72
2018-06-26 17:00 | 118.71 | 106.81
2018-06-26 17:30 | 135.37 | 122.7
2018-06-26 18:00 | 137.61 | 124.94
2018-06-26 18:30 | 137.18 | 124.91
2018-06-26 19:00 | 136.87 | 125.18
2018-06-26 19:30 | 127.05 | 116.35
2018-06-26 20:00 | 116.38 | 112.32
2018-06-26 20:30 | 111.71 | 107.65
2018-06-26 21:00 | 97.76 | 94.55
2018-06-26 21:30 | 81.05 | 80.48
2018-06-26 22:00 | 66.15 | 65.2
2018-06-26 22:30 | 65.7 | 64.32
2018-06-26 23:00 | 63.65 | 61.83
2018-06-26 23:30 | 51.58 | 48.77
2018-06-27 | 42.71 | 39.37
2018-06-27 00:30 | 28.88 | 24.73
2018-06-27 01:00 | 17.76 | 10.14
2018-06-27 01:30 | 14.83 | 5.56
2018-06-27 02:00 | 14.22 | 1.51
2018-06-27 02:30 | 13.66 | -0.74
2018-06-27 03:00 | 13.35 | -3.32
2018-06-27 03:30 | 14.31 | -4.76
2018-06-27 04:00 | 14.93 | -4.28
2018-06-27 04:30 | 16.59 | -0.21
2018-06-27 05:00 | 17.6 | 7.71
2018-06-27 05:30 | 41.33 | 37.98
2018-06-27 06:00 | 67.38 | 65.38
2018-06-27 06:30 | 52.38 | 51.13
2018-06-27 07:00 | 65.29 | 64.82
2018-06-27 07:30 | 87.51 | 87.5
2018-06-27 08:00 | 93.52 | 93.26
2018-06-27 08:30 | 95.07 | 94.61
2018-06-27 09:00 | 88.59 | 88.1
2018-06-27 09:30 | 79.45 | 78.88
2018-06-27 10:00 | 77.4 | 76.58
2018-06-27 10:30 | 80.99 | 80.29
2018-06-27 11:00 | 85.18 | 84.58
2018-06-27 11:30 | 83.22 | 82.52
2018-06-27 12:00 | 79.52 | 78.7
2018-06-27 12:30 | 79.69 | 78.9
2018-06-27 13:00 | 81.37 | 80.65
2018-06-27 13:30 | 79.11 | 78.35
2018-06-27 14:00 | 78.89 | 78.02
2018-06-27 14:30 | 82.05 | 81.32
2018-06-27 15:00 | 81.57 | 80.95
2018-06-27 15:30 | 89.13 | 88.57
2018-06-27 16:00 | 95.45 | 94.95
2018-06-27 16:30 | 104.46 | 104.14
2018-06-27 17:00 | 120.91 | 120.86
2018-06-27 17:30 | 142.64 | 142.56
2018-06-27 18:00 | 138.87 | 138.11
2018-06-27 18:30 | 135.9 | 135.19
2018-06-27 19:00 | 133.91 | 133.5
2018-06-27 19:30 | 128.3 | 128.16
2018-06-27 20:00 | 122.89 | 122.84
2018-06-27 20:30 | 116.82 | 116.81
2018-06-27 21:00 | 100.23 | 99.91
2018-06-27 21:30 | 89.47 | 89.21
2018-06-27 22:00 | 74.63 | 73.9
2018-06-27 22:30 | 72.29 | 71.19
2018-06-27 23:00 | 72 | 70.63
2018-06-27 23:30 | 58.84 | 56.02
2018-06-28 | 41.23 | 35.84
2018-06-28 00:30 | 32.81 | 25.34
2018-06-28 01:00 | 24.37 | 15.99
2018-06-28 01:30 | 19.08 | 9.53
2018-06-28 02:00 | 18.2 | 7.69
2018-06-28 02:30 | 18.45 | 4.88
2018-06-28 03:00 | 18.74 | 2.55
2018-06-28 03:30 | 19.52 | 2.92
2018-06-28 04:00 | 20.43 | 4.17
2018-06-28 04:30 | 22.56 | 7.62
2018-06-28 05:00 | 23.91 | 11.38
2018-06-28 05:30 | 30.61 | 23.15
2018-06-28 06:00 | 48.64 | 45.56
2018-06-28 06:30 | 61.48 | 60.3
2018-06-28 07:00 | 70.12 | 69.55
2018-06-28 07:30 | 85.38 | 85.38
2018-06-28 08:00 | 93.2 | 86.28
2018-06-28 08:30 | 98.21 | 83.61
2018-06-28 09:00 | 89.83 | 75.31
2018-06-28 09:30 | 71.88 | 64.81
2018-06-28 10:00 | 75.97 | 69.11
2018-06-28 10:30 | 71.09 | 63.48
2018-06-28 11:00 | 69.19 | 60.94
2018-06-28 11:30 | 67.54 | 59.26
2018-06-28 12:00 | 71.07 | 63
2018-06-28 12:30 | 67.16 | 59.11
2018-06-28 13:00 | 60.12 | 51.8
2018-06-28 13:30 | 54.75 | 45.88
2018-06-28 14:00 | 53.88 | 45.01
2018-06-28 14:30 | 56.08 | 47.11
2018-06-28 15:00 | 56.77 | 49.42
2018-06-28 15:30 | 29.6 | -6.68
2018-06-28 16:00 | 42.65 | -29.78
2018-06-28 16:30 | 31.22 | 11.2
2018-06-28 17:00 | 39.68 | -19.78
2018-06-28 17:30 | 40.41 | 21.06
2018-06-28 18:00 | 31.6 | -15.18
2018-06-28 18:30 | 27.92 | -13.08
2018-06-28 19:00 | 67.55 | 65.08
2018-06-28 19:30 | 68.59 | 66.46
2018-06-28 20:00 | 65.07 | 65.05
2018-06-28 20:30 | 55.93 | 54.67
2018-06-28 21:00 | 45.16 | 43.18
2018-06-28 21:30 | 54.07 | 52.7
2018-06-28 22:00 | 56.93 | 55.91
2018-06-28 22:30 | 56.19 | 54.82
2018-06-28 23:00 | 68.36 | 66.88
2018-06-28 23:30 | 39.93 | 37.15
2018-06-29 | 17.79 | 8.01
2018-06-29 00:30 | 22.38 | 10.75
2018-06-29 01:00 | 22.54 | 7.43
2018-06-29 01:30 | 23.35 | 7.52
2018-06-29 02:00 | 23.84 | 10.19
2018-06-29 02:30 | 28.38 | 14.92
2018-06-29 03:00 | 31.63 | 14.06
2018-06-29 03:30 | 31.82 | 14.36
2018-06-29 04:00 | 30.97 | 11.94
2018-06-29 04:30 | 36.74 | 21.75
2018-06-29 05:00 | 57.86 | 48.76
2018-06-29 05:30 | 83.6 | 77.52
2018-06-29 06:00 | 98.92 | 93.64
2018-06-29 06:30 | 117.93 | 114.44
2018-06-29 07:00 | 104.38 | 103.69
2018-06-29 07:30 | 108.79 | 108.63
2018-06-29 08:00 | 79.02 | 78.96
2018-06-29 08:30 | 68.58 | 68.56
2018-06-29 09:00 | 66.55 | 66.53
2018-06-29 09:30 | 24.86 | 24.81
2018-06-29 10:00 | 21.62 | 21.61
2018-06-29 10:30 | 16.14 | 16.14
2018-06-29 11:00 | 25.63 | 25.62
2018-06-29 11:30 | 25.75 | 25.72
2018-06-29 12:00 | 20.25 | 20.21
2018-06-29 12:30 | 13.98 | 13.9
2018-06-29 13:00 | 23.09 | 23.09
2018-06-29 13:30 | 25.44 | 25.43
2018-06-29 14:00 | 32.73 | 32.71
2018-06-29 14:30 | 37.68 | 37.68
2018-06-29 15:00 | 44.02 | 44.02
2018-06-29 15:30 | 63.4 | 63.39
2018-06-29 16:00 | 55.86 | 55.84
2018-06-29 16:30 | 49.06 | 48.95
2018-06-29 17:00 | 52.93 | 52.92
2018-06-29 17:30 | 58.41 | 58.22
2018-06-29 18:00 | 65.02 | 63.58
2018-06-29 18:30 | 44.2 | 41.23
2018-06-29 19:00 | 62.1 | 61.95
2018-06-29 19:30 | 92.11 | 91.06
2018-06-29 20:00 | 105.64 | 105.44
2018-06-29 20:30 | 81.16 | 80.94
2018-06-29 21:00 | 68.14 | 67.95
2018-06-29 21:30 | 56.7 | 56.31
2018-06-29 22:00 | 52.24 | 51.38
2018-06-29 22:30 | 58.17 | 57.19
2018-06-29 23:00 | 74.21 | 73.07
2018-06-29 23:30 | 38.42 | 35.92
2018-06-30 | 17.69 | 8.04
2018-06-30 00:30 | 20.53 | 9.92
2018-06-30 01:00 | 21.47 | 11.84
2018-06-30 01:30 | 21.76 | 12.45
2018-06-30 02:00 | 27.63 | 13.66
2018-06-30 02:30 | 28.13 | 6.41
2018-06-30 03:00 | 26.33 | -1.34
2018-06-30 03:30 | 26.53 | -1.68
2018-06-30 04:00 | 26.59 | 0.93
2018-06-30 04:30 | 27.59 | 3.08
2018-06-30 05:00 | 28.84 | 6.82
2018-06-30 05:30 | 35.31 | 18.12
2018-06-30 06:00 | 41.76 | 27.19
2018-06-30 06:30 | 55.56 | 44.75
2018-06-30 07:00 | 54.31 | 43.61
2018-06-30 07:30 | 52.9 | 43.39
2018-06-30 08:00 | 18.15 | 1.95
2018-06-30 08:30 | 10.9 | -8.83
2018-06-30 09:00 | 4.62 | -0.75
2018-06-30 09:30 | 2.8 | -2.72
2018-06-30 10:00 | 7.09 | 7.06
2018-06-30 10:30 | 15.8 | 15.75
2018-06-30 11:00 | 12.84 | 12.73
2018-06-30 11:30 | 9.38 | 9.01
2018-06-30 12:00 | 8.03 | 7.35
2018-06-30 12:30 | 7.57 | -6.8
2018-06-30 13:00 | 4.42 | 0.54
2018-06-30 13:30 | 8.93 | 7.58
2018-06-30 14:00 | 21.27 | 19.3
2018-06-30 14:30 | 26.88 | 24.94
2018-06-30 15:00 | 42.08 | 40.61
2018-06-30 15:30 | 55.75 | 54.67
2018-06-30 16:00 | 48.03 | 46.92
2018-06-30 16:30 | 54.21 | 53.29
2018-06-30 17:00 | 39.79 | 39.21
2018-06-30 17:30 | 53.75 | 49.94
2018-06-30 18:00 | 85.64 | 66.73
2018-06-30 18:30 | 78.69 | 59.89
2018-06-30 19:00 | 68.07 | 58.25
2018-06-30 19:30 | 57.14 | 50.49
2018-06-30 20:00 | 38.94 | 38.63
2018-06-30 20:30 | 11.11 | 9.82
2018-06-30 21:00 | 7.83 | -5.92
2018-06-30 21:30 | 17.84 | -16.39
2018-06-30 22:00 | 34.46 | -34.07
2018-06-30 22:30 | 12.04 | -9.06
2018-06-30 23:00 | 9.83 | 7.91
2018-06-30 23:30 | 5.67 | 4.69
2018-07-01 | 14.11 | -14.11
2018-07-01 00:30 | 17.47 | -8.74
2018-07-01 01:00 | 16.27 | -7.01
2018-07-01 01:30 | 18.69 | -11.53
2018-07-01 02:00 | 22.56 | -14.42
2018-07-01 02:30 | 29.11 | -18.64
2018-07-01 03:00 | 29.97 | -20.5
2018-07-01 03:30 | 33.32 | -25.88
2018-07-01 04:00 | 30.58 | -22.32
2018-07-01 04:30 | 24.79 | -11.22
2018-07-01 05:00 | 25.37 | -11.56
2018-07-01 05:30 | 24.51 | 0.17
2018-07-01 06:00 | 25.61 | 0.42
2018-07-01 06:30 | 27.11 | 4.97
2018-07-01 07:00 | 27.29 | 6.54
2018-07-01 07:30 | 38.93 | 25.91
2018-07-01 08:00 | 29.92 | 1.07
2018-07-01 08:30 | 25.81 | -6.11
2018-07-01 09:00 | 22.82 | 2.76
2018-07-01 09:30 | 11.64 | 0.58
2018-07-01 10:00 | 8.57 | 2.82
2018-07-01 10:30 | 18.44 | 17.25
2018-07-01 11:00 | 24.9 | 24.17
2018-07-01 11:30 | 61.61 | 60.94
2018-07-01 12:00 | 82.25 | 81.75
2018-07-01 12:30 | 90.97 | 90.4
2018-07-01 13:00 | 97.12 | 96.53
2018-07-01 13:30 | 108.44 | 107.87
2018-07-01 14:00 | 119.36 | 118.86
2018-07-01 14:30 | 130.92 | 130.49
2018-07-01 15:00 | 124.09 | 123.63
2018-07-01 15:30 | 124.23 | 123.82
2018-07-01 16:00 | 108.09 | 107.6
2018-07-01 16:30 | 70.76 | 70.24
2018-07-01 17:00 | 87.21 | 87.03
2018-07-01 17:30 | 88.66 | 86.94
2018-07-01 18:00 | 94.99 | 79.39
2018-07-01 18:30 | 84.9 | 68.11
2018-07-01 19:00 | 91.96 | 87.16
2018-07-01 19:30 | 120.4 | 117.72
2018-07-01 20:00 | 123.47 | 120.93
2018-07-01 20:30 | 121.28 | 119.04
2018-07-01 21:00 | 93.36 | 93.35
2018-07-01 21:30 | 83.66 | 82.72
2018-07-01 22:00 | 62.93 | 61.15
2018-07-01 22:30 | 69.01 | 67.01
2018-07-01 23:00 | 84.19 | 82.31
2018-07-01 23:30 | 81.93 | 79.62
2018-07-02 | 88.98 | 86.93
2018-07-02 00:30 | 64.45 | 61.87
2018-07-02 01:00 | 43.36 | 34.52
2018-07-02 01:30 | 36.99 | 27.3
2018-07-02 02:00 | 34.85 | 24.9
2018-07-02 02:30 | 32.82 | 23.29
2018-07-02 03:00 | 25.65 | 9.97
2018-07-02 03:30 | 26.79 | 11.92
2018-07-02 04:00 | 28.46 | 15.67
2018-07-02 04:30 | 31.31 | 17.92
2018-07-02 05:00 | 41.19 | 30.8
2018-07-02 05:30 | 71.57 | 65.35
2018-07-02 06:00 | 87.32 | 81.23
2018-07-02 06:30 | 84.26 | 79.14
2018-07-02 07:00 | 69.52 | 64.67
2018-07-02 07:30 | 88.81 | 87.77
2018-07-02 08:00 | 54.21 | 54.1
2018-07-02 08:30 | 14.69 | 7.03
2018-07-02 09:00 | 31.5 | 31
2018-07-02 09:30 | 38.94 | 38.12
2018-07-02 10:00 | 47.54 | 47.18
2018-07-02 10:30 | 60.37 | 59.63
2018-07-02 11:00 | 52.82 | 52.01
2018-07-02 11:30 | 44.63 | 43.23
2018-07-02 12:00 | 57.6 | 56.15
2018-07-02 12:30 | 64.48 | 63.15
2018-07-02 13:00 | 81.29 | 80.26
2018-07-02 13:30 | 99.22 | 98.22
2018-07-02 14:00 | 98.57 | 97.63
2018-07-02 14:30 | 94.73 | 93.5
2018-07-02 15:00 | 86.3 | 85.17
2018-07-02 15:30 | 99.25 | 98.18
2018-07-02 16:00 | 111.43 | 110.31
2018-07-02 16:30 | 77.14 | 75.79
2018-07-02 17:00 | 69.84 | 67.7
2018-07-02 17:30 | 105.04 | 104.79
2018-07-02 18:00 | 99.21 | 97.44
2018-07-02 18:30 | 104.92 | 103.83
2018-07-02 19:00 | 129.22 | 128.92
2018-07-02 19:30 | 128.47 | 128.43
2018-07-02 20:00 | 123.08 | 123
2018-07-02 20:30 | 111.65 | 111.37
2018-07-02 21:00 | 112.48 | 109.82
2018-07-02 21:30 | 108.14 | 104.88
2018-07-02 22:00 | 103.98 | 100.05
2018-07-02 22:30 | 125.14 | 121.94
2018-07-02 23:00 | 151.93 | 149.25
2018-07-02 23:30 | 138.78 | 135.99
2018-07-03 | 107.18 | 103.41
2018-07-03 00:30 | 88.47 | 84.41
2018-07-03 01:00 | 76.33 | 72.33
2018-07-03 01:30 | 81.45 | 78.06
2018-07-03 02:00 | 79.21 | 74.79
2018-07-03 02:30 | 73.98 | 67.26
2018-07-03 03:00 | 61.74 | 53.75
2018-07-03 03:30 | 60.56 | 51.97
2018-07-03 04:00 | 61.27 | 52.37
2018-07-03 04:30 | 80.64 | 73.47
2018-07-03 05:00 | 93.99 | 87.69
2018-07-03 05:30 | 113.14 | 108.1
2018-07-03 06:00 | 135.59 | 131.57
2018-07-03 06:30 | 158.55 | 155.8
2018-07-03 07:00 | 152.14 | 151.13
2018-07-03 07:30 | 160.13 | 159.97
2018-07-03 08:00 | 140.62 | 140.52
2018-07-03 08:30 | 120.76 | 120.75
2018-07-03 09:00 | 112.56 | 112.55
2018-07-03 09:30 | 96.74 | 96.71
2018-07-03 10:00 | 70.35 | 70.3
2018-07-03 10:30 | 71.66 | 71.59
2018-07-03 11:00 | 81.93 | 81.83
2018-07-03 11:30 | 75.59 | 75.46
2018-07-03 12:00 | 58.79 | 58.63
2018-07-03 12:30 | 98.64 | 98.57
2018-07-03 13:00 | 125 | 124.95
2018-07-03 13:30 | 111.15 | 111.09
2018-07-03 14:00 | 125.18 | 125.11
2018-07-03 14:30 | 143.9 | 143.84
2018-07-03 15:00 | 148.58 | 148.53
2018-07-03 15:30 | 157.26 | 157.18
2018-07-03 16:00 | 173.03 | 172.96
2018-07-03 16:30 | 176.89 | 176.83
2018-07-03 17:00 | 175.25 | 175.2
2018-07-03 17:30 | 184.03 | 182.35
2018-07-03 18:00 | 195.41 | 187.23
2018-07-03 18:30 | 189.71 | 181.9
2018-07-03 19:00 | 191.56 | 184.41
2018-07-03 19:30 | 157.19 | 154.48
2018-07-03 20:00 | 147.64 | 147.63
2018-07-03 20:30 | 152.95 | 152.77
2018-07-03 21:00 | 165.63 | 165.35
2018-07-03 21:30 | 157.66 | 157.12
2018-07-03 22:00 | 155.48 | 154.65
2018-07-03 22:30 | 179.23 | 178.31
2018-07-03 23:00 | 178.95 | 177.95
2018-07-03 23:30 | 162.09 | 160.6
2018-07-04 | 129.54 | 127.64
2018-07-04 00:30 | 104.09 | 101.86
2018-07-04 01:00 | 88.52 | 85.07
2018-07-04 01:30 | 68.7 | 63
2018-07-04 02:00 | 52.71 | 45.22
2018-07-04 02:30 | 68.55 | 63.26
2018-07-04 03:00 | 54.8 | 47.68
2018-07-04 03:30 | 67.45 | 61.97
2018-07-04 04:00 | 62.56 | 56.17
2018-07-04 04:30 | 79.72 | 74.51
2018-07-04 05:00 | 98.56 | 94.27
2018-07-04 05:30 | 111.82 | 107.74
2018-07-04 06:00 | 129.65 | 125.59
2018-07-04 06:30 | 114.06 | 109.55
2018-07-04 07:00 | 117.68 | 114.3
2018-07-04 07:30 | 124.26 | 123.99
2018-07-04 08:00 | 111.49 | 111.41
2018-07-04 08:30 | 91.63 | 91.61
2018-07-04 09:00 | 91.4 | 91.39
2018-07-04 09:30 | 101.85 | 101.84
2018-07-04 10:00 | 98.47 | 98.47
2018-07-04 10:30 | 106.11 | 106.1
2018-07-04 11:00 | 122.09 | 122.07
2018-07-04 11:30 | 107.79 | 107.77
2018-07-04 12:00 | 98.2 | 98.2
2018-07-04 12:30 | 92.33 | 92.32
2018-07-04 13:00 | 86.59 | 86.59
2018-07-04 13:30 | 90.16 | 90.15
2018-07-04 14:00 | 96.38 | 96.37
2018-07-04 14:30 | 101.1 | 101.08
2018-07-04 15:00 | 96.47 | 96.46
2018-07-04 15:30 | 87.71 | 87.71
2018-07-04 16:00 | 88.22 | 88.21
2018-07-04 16:30 | 93.37 | 93.32
2018-07-04 17:00 | 159.55 | 159.54
2018-07-04 17:30 | 160.92 | 160.55
2018-07-04 18:00 | 168.45 | 158.8
2018-07-04 18:30 | 165.13 | 156.47
2018-07-04 19:00 | 162.81 | 155.07
2018-07-04 19:30 | 161.54 | 159.11
2018-07-04 20:00 | 167.08 | 164.86
2018-07-04 20:30 | 180.38 | 178.6
2018-07-04 21:00 | 172.75 | 171.96
2018-07-04 21:30 | 148.01 | 145.86
2018-07-04 22:00 | 160.9 | 158.9
2018-07-04 22:30 | 168.13 | 166.21
2018-07-04 23:00 | 176.28 | 174.24
2018-07-04 23:30 | 145.56 | 143.04
2018-07-05 | 107.98 | 104.22
2018-07-05 00:30 | 98.13 | 95.53
2018-07-05 01:00 | 58.68 | 51.63
2018-07-05 01:30 | 75.88 | 71.38
2018-07-05 02:00 | 89.89 | 86.46
2018-07-05 02:30 | 87.92 | 84.15
2018-07-05 03:00 | 76.47 | 71.86
2018-07-05 03:30 | 76.85 | 72.14
2018-07-05 04:00 | 88.54 | 84.93
2018-07-05 04:30 | 88.93 | 84.3
2018-07-05 05:00 | 110.07 | 106.27
2018-07-05 05:30 | 123.86 | 120.24
2018-07-05 06:00 | 121.67 | 117.91
2018-07-05 06:30 | 141.21 | 138.47
2018-07-05 07:00 | 139.11 | 136.4
2018-07-05 07:30 | 128.8 | 127
2018-07-05 08:00 | 125.06 | 124.97
2018-07-05 08:30 | 116.05 | 116.01
2018-07-05 09:00 | 128.17 | 128.17
2018-07-05 09:30 | 120.41 | 120.41
2018-07-05 10:00 | 131.05 | 131.03
2018-07-05 10:30 | 117.94 | 117.92
2018-07-05 11:00 | 138.58 | 138.54
2018-07-05 11:30 | 148.34 | 148.3
2018-07-05 12:00 | 151.47 | 151.44
2018-07-05 12:30 | 153.05 | 153.03
2018-07-05 13:00 | 167.84 | 167.8
2018-07-05 13:30 | 174.18 | 174.16
2018-07-05 14:00 | 166.93 | 166.9
2018-07-05 14:30 | 150.94 | 150.91
2018-07-05 15:00 | 155.47 | 155.45
2018-07-05 15:30 | 146.99 | 146.99
2018-07-05 16:00 | 187.1 | 187.09
2018-07-05 16:30 | 186.53 | 186.53
2018-07-05 17:00 | 201.79 | 201.79
2018-07-05 17:30 | 196.93 | 196.71
2018-07-05 18:00 | 203.77 | 203.5
2018-07-05 18:30 | 213.33 | 213.11
2018-07-05 19:00 | 214.46 | 214.12
2018-07-05 19:30 | 206.72 | 206.22
2018-07-05 20:00 | 204.13 | 203.68
2018-07-05 20:30 | 199.71 | 199.65
2018-07-05 21:00 | 199.47 | 199.3
2018-07-05 21:30 | 190.59 | 190.31
2018-07-05 22:00 | 175.28 | 174.74
2018-07-05 22:30 | 176.51 | 175.87
2018-07-05 23:00 | 172.27 | 171.53
2018-07-05 23:30 | 165.47 | 164.47
2018-07-06 | 128.84 | 127.19
2018-07-06 00:30 | 111.58 | 109.57
2018-07-06 01:00 | 94.54 | 92.13
2018-07-06 01:30 | 74.8 | 72.04
2018-07-06 02:00 | 70.11 | 66.15
2018-07-06 02:30 | 62.17 | 54.82
2018-07-06 03:00 | 56.4 | 48.31
2018-07-06 03:30 | 62.19 | 55.04
2018-07-06 04:00 | 53.44 | 44.45
2018-07-06 04:30 | 59.64 | 51.01
2018-07-06 05:00 | 74.77 | 67.69
2018-07-06 05:30 | 101.41 | 95.87
2018-07-06 06:00 | 117.63 | 112.7
2018-07-06 06:30 | 136.07 | 132.54
2018-07-06 07:00 | 142.1 | 138.9
2018-07-06 07:30 | 145.63 | 144.03
2018-07-06 08:00 | 148.3 | 148.27
2018-07-06 08:30 | 150.19 | 150.19
2018-07-06 09:00 | 159.96 | 159.96
2018-07-06 09:30 | 145.45 | 145.44
2018-07-06 10:00 | 146.04 | 146.02
2018-07-06 10:30 | 159.67 | 159.63
2018-07-06 11:00 | 165.49 | 165.42
2018-07-06 11:30 | 165.09 | 165.01
2018-07-06 12:00 | 163.22 | 163.15
2018-07-06 12:30 | 165.56 | 165.55
2018-07-06 13:00 | 147.09 | 147.06
2018-07-06 13:30 | 155.04 | 154.98
2018-07-06 14:00 | 155.73 | 155.68
2018-07-06 14:30 | 152.41 | 152.38
2018-07-06 15:00 | 153.5 | 153.48
2018-07-06 15:30 | 185.14 | 185.12
2018-07-06 16:00 | 190.18 | 190.18
2018-07-06 16:30 | 190.95 | 190.95
2018-07-06 17:00 | 200.59 | 200.58
2018-07-06 17:30 | 204.34 | 202.94
2018-07-06 18:00 | 195.5 | 187.42
2018-07-06 18:30 | 179.5 | 175.86
2018-07-06 19:00 | 190.74 | 188.02
2018-07-06 19:30 | 185.84 | 183.25
2018-07-06 20:00 | 185.79 | 183.51
2018-07-06 20:30 | 198.65 | 196.76
2018-07-06 21:00 | 191.82 | 191.82
2018-07-06 21:30 | 188.59 | 186.85
2018-07-06 22:00 | 162.78 | 160.58
2018-07-06 22:30 | 171.16 | 169.44
2018-07-06 23:00 | 182.79 | 181
2018-07-06 23:30 | 153.21 | 151.05
2018-07-07 | 114.7 | 111.13
2018-07-07 00:30 | 97.74 | 93.51
2018-07-07 01:00 | 72.15 | 66.74
2018-07-07 01:30 | 62.06 | 56.33
2018-07-07 02:00 | 52.11 | 45.27
2018-07-07 02:30 | 51.78 | 44.82
2018-07-07 03:00 | 32.36 | 20.85
2018-07-07 03:30 | 55.36 | 48.45
2018-07-07 04:00 | 47.97 | 36.96
2018-07-07 04:30 | 40.7 | 26.35
2018-07-07 05:00 | 51.55 | 40.74
2018-07-07 05:30 | 58.17 | 48.09
2018-07-07 06:00 | 77.51 | 69.92
2018-07-07 06:30 | 89.87 | 82.74
2018-07-07 07:00 | 102.66 | 96.56
2018-07-07 07:30 | 110.68 | 104.77
2018-07-07 08:00 | 113.71 | 108.04
2018-07-07 08:30 | 126.22 | 122.05
2018-07-07 09:00 | 132.23 | 130.07
2018-07-07 09:30 | 131.78 | 131.66
2018-07-07 10:00 | 152.21 | 152.13
2018-07-07 10:30 | 151.07 | 151
2018-07-07 11:00 | 140.47 | 140.37
2018-07-07 11:30 | 133.67 | 133.52
2018-07-07 12:00 | 126.56 | 126.42
2018-07-07 12:30 | 131.22 | 131.09
2018-07-07 13:00 | 149.63 | 149.47
2018-07-07 13:30 | 158 | 157.83
2018-07-07 14:00 | 144.76 | 144.52
2018-07-07 14:30 | 133.83 | 133.57
2018-07-07 15:00 | 132.64 | 132.4
2018-07-07 15:30 | 148.14 | 147.86
2018-07-07 16:00 | 146.28 | 146.02
2018-07-07 16:30 | 143.48 | 143.25
2018-07-07 17:00 | 151.18 | 151
2018-07-07 17:30 | 155.65 | 155.59
2018-07-07 18:00 | 154.54 | 154.53
2018-07-07 18:30 | 155.49 | 155.46
2018-07-07 19:00 | 158.04 | 157.99
2018-07-07 19:30 | 157.1 | 156.98
2018-07-07 20:00 | 165.32 | 165.11
2018-07-07 20:30 | 166.03 | 165.69
2018-07-07 21:00 | 155.34 | 154.81
2018-07-07 21:30 | 147.85 | 147.11
2018-07-07 22:00 | 134.83 | 133.85
2018-07-07 22:30 | 156.08 | 155.12
2018-07-07 23:00 | 170.82 | 169.73
2018-07-07 23:30 | 141.43 | 139.62
2018-07-08 | 109.65 | 106.98
2018-07-08 00:30 | 96.52 | 93.13
2018-07-08 01:00 | 84.07 | 77.94
2018-07-08 01:30 | 71.3 | 64.42
2018-07-08 02:00 | 68.6 | 61.94
2018-07-08 02:30 | 75.5 | 69.39
2018-07-08 03:00 | 85.08 | 80.02
2018-07-08 03:30 | 79.38 | 73.89
2018-07-08 04:00 | 76.78 | 71.02
2018-07-08 04:30 | 84.14 | 78.8
2018-07-08 05:00 | 71.35 | 63.86
2018-07-08 05:30 | 77.98 | 71.09
2018-07-08 06:00 | 77.85 | 70.05
2018-07-08 06:30 | 95.29 | 89.04
2018-07-08 07:00 | 106.26 | 101.21
2018-07-08 07:30 | 121 | 115.99
2018-07-08 08:00 | 110.8 | 105.34
2018-07-08 08:30 | 107.88 | 102.04
2018-07-08 09:00 | 103.96 | 98.05
2018-07-08 09:30 | 105.28 | 99.56
2018-07-08 10:00 | 120.68 | 115.73
2018-07-08 10:30 | 125.37 | 120.57
2018-07-08 11:00 | 122.89 | 118.05
2018-07-08 11:30 | 89.99 | 83.62
2018-07-08 12:00 | 31.09 | -11.51
2018-07-08 12:30 | 32.19 | -18.95
2018-07-08 13:00 | 30.73 | -16.37
2018-07-08 13:30 | 29.35 | -13.69
2018-07-08 14:00 | 27.27 | -3.46
2018-07-08 14:30 | 28.5 | 5.51
2018-07-08 15:00 | 34.92 | 20.71
2018-07-08 15:30 | 59.51 | 51.92
2018-07-08 16:00 | 96.15 | 91.63
2018-07-08 16:30 | 113.68 | 109.86
2018-07-08 17:00 | 129.79 | 128.14
2018-07-08 17:30 | 150.4 | 150.37
2018-07-08 18:00 | 166.81 | 165.69
2018-07-08 18:30 | 171.49 | 162.86
2018-07-08 19:00 | 176.69 | 168.49
2018-07-08 19:30 | 157.5 | 150.36
2018-07-08 20:00 | 161.07 | 158.49
2018-07-08 20:30 | 184.25 | 183.43
2018-07-08 21:00 | 163.61 | 163.47
2018-07-08 21:30 | 158.54 | 158.25
2018-07-08 22:00 | 142.37 | 141.75
2018-07-08 22:30 | 147.3 | 146.44
2018-07-08 23:00 | 170.04 | 168.97
2018-07-08 23:30 | 152.82 | 151.25
2018-07-09 | 123.96 | 121.77
2018-07-09 00:30 | 90.8 | 87.93
2018-07-09 01:00 | 62.29 | 56.24
2018-07-09 01:30 | 50.26 | 41.08
2018-07-09 02:00 | 52.03 | 43.79
2018-07-09 02:30 | 49.89 | 40.86
2018-07-09 03:00 | 42.64 | 31.76
2018-07-09 03:30 | 43.56 | 32.61
2018-07-09 04:00 | 43.84 | 32.95
2018-07-09 04:30 | 62.96 | 54.27
2018-07-09 05:00 | 91.49 | 85.46
2018-07-09 05:30 | 110.02 | 104.65
2018-07-09 06:00 | 143.98 | 140.07
2018-07-09 06:30 | 166.6 | 164.21
2018-07-09 07:00 | 147.21 | 146.25
2018-07-09 07:30 | 174.81 | 174.79
2018-07-09 08:00 | 174.98 | 174.98
2018-07-09 08:30 | 154.99 | 154.96
2018-07-09 09:00 | 116.53 | 116.51
2018-07-09 09:30 | 88.37 | 88.36
2018-07-09 10:00 | 70.12 | 70.12
2018-07-09 10:30 | 73.98 | 73.98
2018-07-09 11:00 | 80.27 | 80.25
2018-07-09 11:30 | 89.37 | 89.35
2018-07-09 12:00 | 51.03 | 51.03
2018-07-09 12:30 | 38.49 | 38.49
2018-07-09 13:00 | 56.01 | 56.01
2018-07-09 13:30 | 85.73 | 85.72
2018-07-09 14:00 | 97.08 | 97.07
2018-07-09 14:30 | 68.15 | 68.15
2018-07-09 15:00 | 75.01 | 75
2018-07-09 15:30 | 92.43 | 92.39
2018-07-09 16:00 | 95.48 | 95.45
2018-07-09 16:30 | 101.21 | 101.18
2018-07-09 17:00 | 127.06 | 126.54
2018-07-09 17:30 | 146.49 | 146.42
2018-07-09 18:00 | 126.53 | 126.36
2018-07-09 18:30 | 134.86 | 133.38
2018-07-09 19:00 | 143 | 141.81
2018-07-09 19:30 | 155.33 | 154.8
2018-07-09 20:00 | 181.61 | 181.59
2018-07-09 20:30 | 133.34 | 133.31
2018-07-09 21:00 | 115.03 | 115.03
2018-07-09 21:30 | 116.22 | 116.2
2018-07-09 22:00 | 119.13 | 119.05
2018-07-09 22:30 | 153.29 | 150.96
2018-07-09 23:00 | 148.4 | 145.6
2018-07-09 23:30 | 112.44 | 108.81
2018-07-10 | 70.82 | 64.64
2018-07-10 00:30 | 64.39 | 58.21
2018-07-10 01:00 | 50.35 | 44.32
2018-07-10 01:30 | 40.27 | 33.99
2018-07-10 02:00 | 38.39 | 25.09
2018-07-10 02:30 | 44.63 | 34.17
2018-07-10 03:00 | 41.07 | 28.92
2018-07-10 03:30 | 33.69 | 17.81
2018-07-10 04:00 | 32.37 | 15.04
2018-07-10 04:30 | 36.68 | 20.29
2018-07-10 05:00 | 58.36 | 48.31
2018-07-10 05:30 | 86.65 | 79.63
2018-07-10 06:00 | 113.15 | 108.44
2018-07-10 06:30 | 113.03 | 108.91
2018-07-10 07:00 | 69.8 | 68.54
2018-07-10 07:30 | 100.46 | 100.37
2018-07-10 08:00 | 67.86 | 67.12
2018-07-10 08:30 | 50.17 | 48.05
2018-07-10 09:00 | 55.47 | 55.24
2018-07-10 09:30 | 30.66 | 30.49
2018-07-10 10:00 | 13.88 | 12.91
2018-07-10 10:30 | 3.26 | 1.06
2018-07-10 11:00 | 10.04 | 3.36
2018-07-10 11:30 | 8.89 | 3.68
2018-07-10 12:00 | 6.15 | 5.74
2018-07-10 12:30 | 19.98 | 19.96
2018-07-10 13:00 | 33.6 | 33.6
2018-07-10 13:30 | 37.87 | 37.87
2018-07-10 14:00 | 56.1 | 56.1
2018-07-10 14:30 | 79.16 | 79.16
2018-07-10 15:00 | 80.3 | 80.29
2018-07-10 15:30 | 84.23 | 84.22
2018-07-10 16:00 | 92.34 | 92.3
2018-07-10 16:30 | 92.04 | 91.98
2018-07-10 17:00 | 104.58 | 103.13
2018-07-10 17:30 | 124.32 | 123.79
2018-07-10 18:00 | 149.2 | 145.31
2018-07-10 18:30 | 149.04 | 145.84
2018-07-10 19:00 | 161.27 | 160.04
2018-07-10 19:30 | 162.74 | 161.76
2018-07-10 20:00 | 139.62 | 138.82
2018-07-10 20:30 | 132.59 | 132
2018-07-10 21:00 | 135.01 | 134.84
2018-07-10 21:30 | 130.35 | 129.57
2018-07-10 22:00 | 111.81 | 110.98
2018-07-10 22:30 | 102.27 | 101.48
2018-07-10 23:00 | 109.32 | 108.58
2018-07-10 23:30 | 85.4 | 81.39
2018-07-11 | 56.4 | 48.44
2018-07-11 00:30 | 57.19 | 50.35
2018-07-11 01:00 | 39.46 | 30.45
2018-07-11 01:30 | 27.16 | 13.04
2018-07-11 02:00 | 29.87 | 18.88
2018-07-11 02:30 | 27.31 | 14.87
2018-07-11 03:00 | 29.46 | 18.25
2018-07-11 03:30 | 30.8 | 19.68
2018-07-11 04:00 | 33.13 | 22.38
2018-07-11 04:30 | 41.06 | 31.57
2018-07-11 05:00 | 59.54 | 52.45
2018-07-11 05:30 | 89.12 | 83.78
2018-07-11 06:00 | 105.7 | 100.98
2018-07-11 06:30 | 98.12 | 95.81
2018-07-11 07:00 | 79.55 | 79.21
2018-07-11 07:30 | 124.39 | 124.39
2018-07-11 08:00 | 120.08 | 119.8
2018-07-11 08:30 | 87.02 | 85.95
2018-07-11 09:00 | 58.17 | 56.53
2018-07-11 09:30 | 40.42 | 38
2018-07-11 10:00 | 36.11 | 33.18
2018-07-11 10:30 | 27.95 | 26.07
2018-07-11 11:00 | 34.37 | 34.37
2018-07-11 11:30 | 40.43 | 40.43
2018-07-11 12:00 | 61.82 | 61.82
2018-07-11 12:30 | 76.91 | 76.9
2018-07-11 13:00 | 86.3 | 86.29
2018-07-11 13:30 | 92.59 | 92.58
2018-07-11 14:00 | 103.57 | 103.55
2018-07-11 14:30 | 115.85 | 115.84
2018-07-11 15:00 | 117.1 | 117.06
2018-07-11 15:30 | 119.74 | 119.69
2018-07-11 16:00 | 121.27 | 121.2
2018-07-11 16:30 | 125.88 | 125.81
2018-07-11 17:00 | 144.61 | 143.98
2018-07-11 17:30 | 124.12 | 123.38
2018-07-11 18:00 | 113.43 | 113.28
2018-07-11 18:30 | 107.91 | 107.74
2018-07-11 19:00 | 132.08 | 131.91
2018-07-11 19:30 | 136.01 | 135.68
2018-07-11 20:00 | 121.31 | 120.84
2018-07-11 20:30 | 122.99 | 122.27
2018-07-11 21:00 | 96.4 | 96.34
2018-07-11 21:30 | 102.37 | 102.12
2018-07-11 22:00 | 96.46 | 95.86
2018-07-11 22:30 | 83.19 | 82.13
2018-07-11 23:00 | 105.44 | 104.14
2018-07-11 23:30 | 66.58 | 63.89
2018-07-12 | 20.35 | 12.27
2018-07-12 00:30 | 16.13 | 6.7
2018-07-12 01:00 | 15.09 | 4.44
2018-07-12 01:30 | 17.15 | 2.98
2018-07-12 02:00 | 19.1 | 1.07
2018-07-12 02:30 | 20.24 | -7.37
2018-07-12 03:00 | 22.23 | -12.77
2018-07-12 03:30 | 20.25 | -6.29
2018-07-12 04:00 | 20.03 | -2.5
2018-07-12 04:30 | 27.38 | 14.49
2018-07-12 05:00 | 39.53 | 31.1
2018-07-12 05:30 | 61.02 | 55.09
2018-07-12 06:00 | 71.46 | 65.24
2018-07-12 06:30 | 55.13 | 48.29
2018-07-12 07:00 | 22.28 | 15.57
2018-07-12 07:30 | 47.32 | 45.37
2018-07-12 08:00 | 47.85 | 46.63
2018-07-12 08:30 | 54.57 | -50.79
2018-07-12 09:00 | 55.99 | -40
2018-07-12 09:30 | 78.91 | -72.37
2018-07-12 10:00 | 65.74 | -59.46
2018-07-12 10:30 | 13.21 | 13.14
2018-07-12 11:00 | 16.5 | 15.84
2018-07-12 11:30 | 9.13 | 7.16
2018-07-12 12:00 | 8.19 | 4.14
2018-07-12 12:30 | 8.3 | 7.15
2018-07-12 13:00 | 5.45 | 4.93
2018-07-12 13:30 | 25.72 | 25.61
2018-07-12 14:00 | 37.52 | 37.47
2018-07-12 14:30 | 49.11 | 49.09
2018-07-12 15:00 | 41.25 | 41.22
2018-07-12 15:30 | 72.82 | 72.82
2018-07-12 16:00 | 70.17 | 70.16
2018-07-12 16:30 | 47.2 | 46.91
2018-07-12 17:00 | 59.72 | 57.34
2018-07-12 17:30 | 79.42 | 77.5
2018-07-12 18:00 | 48.79 | 42.04
2018-07-12 18:30 | 29.2 | 9.94
2018-07-12 19:00 | 81.56 | 78.77
2018-07-12 19:30 | 81.88 | 79.9
2018-07-12 20:00 | 37.2 | 31.73
2018-07-12 20:30 | 20.39 | 7.71
2018-07-12 21:00 | 21.19 | -11.87
2018-07-12 21:30 | 24.21 | -23.12
2018-07-12 22:00 | 32.22 | 30.41
2018-07-12 22:30 | 18.32 | 16.69
2018-07-12 23:00 | 17.67 | 13.77
2018-07-12 23:30 | 24.8 | -21.97
2018-07-13 | 67.92 | -67.75
2018-07-13 00:30 | 26.57 | -24.62
2018-07-13 01:00 | 21.02 | -18.28
2018-07-13 01:30 | 15.41 | -10.38
2018-07-13 02:00 | 13.23 | -6.35
2018-07-13 02:30 | 19.73 | -12.87
2018-07-13 03:00 | 25.28 | -17.04
2018-07-13 03:30 | 23.83 | -14.03
2018-07-13 04:00 | 21.59 | -6.93
2018-07-13 04:30 | 23.67 | 7.22
2018-07-13 05:00 | 36.19 | 27.11
2018-07-13 05:30 | 69.98 | 64.77
2018-07-13 06:00 | 88.92 | 83.62
2018-07-13 06:30 | 73.79 | 67.87
2018-07-13 07:00 | 53.92 | 51.43
2018-07-13 07:30 | 78.7 | 77.63
2018-07-13 08:00 | 43.26 | 40.22
2018-07-13 08:30 | 26.07 | 25.49
2018-07-13 09:00 | 11.83 | -9.44
2018-07-13 09:30 | 4.24 | -0.41
2018-07-13 10:00 | 7.24 | -6.33
2018-07-13 10:30 | 9.24 | 5.98
2018-07-13 11:00 | 14.51 | -12.59
2018-07-13 11:30 | 6.37 | 0.52
2018-07-13 12:00 | 11.41 | 10.79
2018-07-13 12:30 | 4.39 | 4.13
2018-07-13 13:00 | 18.04 | 17.98
2018-07-13 13:30 | 25.36 | 25.35
2018-07-13 14:00 | 34.88 | 34.87
2018-07-13 14:30 | 45.2 | 45.2
2018-07-13 15:00 | 68.01 | 68
2018-07-13 15:30 | 107.5 | 107.45
2018-07-13 16:00 | 122.73 | 122.66
2018-07-13 16:30 | 129.03 | 128.97
2018-07-13 17:00 | 132.71 | 132.69
2018-07-13 17:30 | 145 | 141.5
2018-07-13 18:00 | 140.44 | 135.34
2018-07-13 18:30 | 133.27 | 127.76
2018-07-13 19:00 | 103.93 | 96.3
2018-07-13 19:30 | 117.58 | 112.01
2018-07-13 20:00 | 127.92 | 123.38
2018-07-13 20:30 | 130.92 | 126.9
2018-07-13 21:00 | 81.17 | 75.19
2018-07-13 21:30 | 65.62 | 59.02
2018-07-13 22:00 | 56.39 | 50.14
2018-07-13 22:30 | 45.04 | 42.96
2018-07-13 23:00 | 45.31 | 44.07
2018-07-13 23:30 | 36.09 | 34.27
2018-07-14 | 20.68 | 16.06
2018-07-14 00:30 | 24.53 | 19.9
2018-07-14 01:00 | 13.3 | 1.11
2018-07-14 01:30 | 15.01 | 6.86
2018-07-14 02:00 | 13.52 | 6.3
2018-07-14 02:30 | 16.13 | 10.46
2018-07-14 03:00 | 27.09 | 6.35
2018-07-14 03:30 | 26.74 | -3.24
2018-07-14 04:00 | 26.68 | 0.18
2018-07-14 04:30 | 32.1 | 15.21
2018-07-14 05:00 | 44.46 | 33.67
2018-07-14 05:30 | 64.56 | 56.72
2018-07-14 06:00 | 83.11 | 76.52
2018-07-14 06:30 | 95.74 | 89.03
2018-07-14 07:00 | 98.49 | 92.06
2018-07-14 07:30 | 100.04 | 95.23
2018-07-14 08:00 | 78.93 | 77.79
2018-07-14 08:30 | 50.93 | 50.76
2018-07-14 09:00 | 22.49 | 19.51
2018-07-14 09:30 | 14.48 | -8.09
2018-07-14 10:00 | 22.13 | -19.49
2018-07-14 10:30 | 11.48 | -1.68
2018-07-14 11:00 | 5.53 | -0.47
2018-07-14 11:30 | 7.5 | 0.76
2018-07-14 12:00 | 37.1 | 35.04
2018-07-14 12:30 | 24.19 | 20.86
2018-07-14 13:00 | 21.7 | -18.55
2018-07-14 13:30 | 20.13 | -16.36
2018-07-14 14:00 | 14.27 | -5.65
2018-07-14 14:30 | 25.79 | -23.39
2018-07-14 15:00 | 11.9 | -0.65
2018-07-14 15:30 | 28.25 | 25.19
2018-07-14 16:00 | 59.33 | 58.06
2018-07-14 16:30 | 87.19 | 86.48
2018-07-14 17:00 | 77.01 | 76.65
2018-07-14 17:30 | 63.49 | 63.42
2018-07-14 18:00 | 90.86 | 73.98
2018-07-14 18:30 | 87.88 | 66.61
2018-07-14 19:00 | 101.86 | 84.65
2018-07-14 19:30 | 109.88 | 95.31
2018-07-14 20:00 | 116.31 | 103.39
2018-07-14 20:30 | 109 | 103.34
2018-07-14 21:00 | 93.45 | 89.36
2018-07-14 21:30 | 128.67 | 128.53
2018-07-14 22:00 | 137.85 | 137.52
2018-07-14 22:30 | 156.07 | 155.64
2018-07-14 23:00 | 161.44 | 160.7
2018-07-14 23:30 | 129.83 | 128.55
2018-07-15 | 74.41 | 71.5
2018-07-15 00:30 | 87.05 | 84.9
2018-07-15 01:00 | 79.1 | 76.85
2018-07-15 01:30 | 78.7 | 76.13
2018-07-15 02:00 | 74.64 | 69.4
2018-07-15 02:30 | 70.08 | 64.58
2018-07-15 03:00 | 63.19 | 56.95
2018-07-15 03:30 | 58.66 | 51.88
2018-07-15 04:00 | 55.37 | 48.05
2018-07-15 04:30 | 62.31 | 55.7
2018-07-15 05:00 | 70.05 | 64.03
2018-07-15 05:30 | 70.78 | 64.27
2018-07-15 06:00 | 70.29 | 63.12
2018-07-15 06:30 | 93.07 | 87.16
2018-07-15 07:00 | 103.89 | 98.18
2018-07-15 07:30 | 123.88 | 119.08
2018-07-15 08:00 | 121.89 | 118.57
2018-07-15 08:30 | 102.22 | 99.55
2018-07-15 09:00 | 87.36 | 86.58
2018-07-15 09:30 | 56.14 | 54.98
2018-07-15 10:00 | 39.18 | 37.31
2018-07-15 10:30 | 31.02 | 28.43
2018-07-15 11:00 | 41.93 | 40.03
2018-07-15 11:30 | 28.62 | 26.01
2018-07-15 12:00 | 14.68 | 10.4
2018-07-15 12:30 | 33.88 | 32.14
2018-07-15 13:00 | 28.86 | 26.73
2018-07-15 13:30 | 24.46 | 21.94
2018-07-15 14:00 | 34.09 | 32.01
2018-07-15 14:30 | 58.89 | 57.48
2018-07-15 15:00 | 55.04 | 53.39
2018-07-15 15:30 | 80.4 | 79.27
2018-07-15 16:00 | 118.22 | 117.46
2018-07-15 16:30 | 122.93 | 122.37
2018-07-15 17:00 | 139.82 | 139.63
2018-07-15 17:30 | 167.84 | 167.82
2018-07-15 18:00 | 168.26 | 167.8
2018-07-15 18:30 | 157.99 | 157.82
2018-07-15 19:00 | 153.89 | 153.75
2018-07-15 19:30 | 161.4 | 161.34
2018-07-15 20:00 | 160.89 | 160.85
2018-07-15 20:30 | 173.97 | 173.97
2018-07-15 21:00 | 153.52 | 153.44
2018-07-15 21:30 | 121.44 | 121.13
2018-07-15 22:00 | 112.9 | 111.6
2018-07-15 22:30 | 127.84 | 125.42
2018-07-15 23:00 | 146.18 | 144.77
2018-07-15 23:30 | 113.49 | 111.3
2018-07-16 | 83.55 | 80.45
2018-07-16 00:30 | 85.31 | 82.03
2018-07-16 01:00 | 69.92 | 66.02
2018-07-16 01:30 | 63.51 | 59.82
2018-07-16 02:00 | 57.77 | 53.68
2018-07-16 02:30 | 53.89 | 49.6
2018-07-16 03:00 | 59.61 | 55.62
2018-07-16 03:30 | 55.12 | 46.57
2018-07-16 04:00 | 53.89 | 43.78
2018-07-16 04:30 | 61.49 | 52.19
2018-07-16 05:00 | 82.4 | 75.19
2018-07-16 05:30 | 120.67 | 115.79
2018-07-16 06:00 | 149.03 | 146.06
2018-07-16 06:30 | 150.96 | 149.83
2018-07-16 07:00 | 149.61 | 149.52
2018-07-16 07:30 | 174.53 | 173.2
2018-07-16 08:00 | 161.16 | 152.18
2018-07-16 08:30 | 98.75 | 83.92
2018-07-16 09:00 | 49.72 | 38.96
2018-07-16 09:30 | 38.45 | 23.22
2018-07-16 10:00 | 31.91 | 11.32
2018-07-16 10:30 | 31.75 | 12.22
2018-07-16 11:00 | 34.22 | 17.26
2018-07-16 11:30 | 30.09 | -2.34
2018-07-16 12:00 | 31.64 | -8.97
2018-07-16 12:30 | 29.19 | -1.61
2018-07-16 13:00 | 1.9 | 0.95
2018-07-16 13:30 | 9.69 | 9.4
2018-07-16 14:00 | 13.61 | 13.47
2018-07-16 14:30 | 18.59 | 18.49
2018-07-16 15:00 | 39.01 | 38.84
2018-07-16 15:30 | 72.83 | 72.66
2018-07-16 16:00 | 90.26 | 90.15
2018-07-16 16:30 | 91.65 | 91.53
2018-07-16 17:00 | 80.46 | 79.72
2018-07-16 17:30 | 91.79 | 90.44
2018-07-16 18:00 | 108.64 | 106.48
2018-07-16 18:30 | 131.23 | 129.63
2018-07-16 19:00 | 131.09 | 129.7
2018-07-16 19:30 | 128.74 | 127.62
2018-07-16 20:00 | 132.49 | 131.54
2018-07-16 20:30 | 158 | 157.62
2018-07-16 21:00 | 142.57 | 142.08
2018-07-16 21:30 | 134.22 | 133
2018-07-16 22:00 | 117.51 | 115.35
2018-07-16 22:30 | 124.18 | 122.26
2018-07-16 23:00 | 147.95 | 146.86
2018-07-16 23:30 | 120.56 | 119.13
2018-07-17 | 89.02 | 87.02
2018-07-17 00:30 | 76.42 | 73.96
2018-07-17 01:00 | 63.95 | 60.75
2018-07-17 01:30 | 63.04 | 59.94
2018-07-17 02:00 | 68.61 | 65.64
2018-07-17 02:30 | 65.8 | 62.69
2018-07-17 03:00 | 73.25 | 67.08
2018-07-17 03:30 | 77.59 | 71.24
2018-07-17 04:00 | 82.68 | 76.08
2018-07-17 04:30 | 95.83 | 91.35
2018-07-17 05:00 | 116.53 | 113.62
2018-07-17 05:30 | 141.5 | 139.29
2018-07-17 06:00 | 169.44 | 168.24
2018-07-17 06:30 | 198.19 | 197.91
2018-07-17 07:00 | 217.53 | 217.38
2018-07-17 07:30 | 248.37 | 248.36
2018-07-17 08:00 | 231.56 | 231.55
2018-07-17 08:30 | 171.79 | 171.7
2018-07-17 09:00 | 106.53 | 106.48
2018-07-17 09:30 | 94.23 | 94.12
2018-07-17 10:00 | 89.93 | 89.73
2018-07-17 10:30 | 88.81 | 88.53
2018-07-17 11:00 | 67.95 | 67.95
2018-07-17 11:30 | 58.99 | 58.98
2018-07-17 12:00 | 53.88 | 53.86
2018-07-17 12:30 | 60.38 | 60.37
2018-07-17 13:00 | 66.87 | 66.87
2018-07-17 13:30 | 83.98 | 83.97
2018-07-17 14:00 | 75.31 | 75.31
2018-07-17 14:30 | 81.6 | 81.6
2018-07-17 15:00 | 80.39 | 80.39
2018-07-17 15:30 | 112.9 | 112.9
2018-07-17 16:00 | 137.48 | 137.47
2018-07-17 16:30 | 143.03 | 143.02
2018-07-17 17:00 | 145.98 | 143.19
2018-07-17 17:30 | 164.21 | 160.05
2018-07-17 18:00 | 191.18 | 186.53
2018-07-17 18:30 | 208.86 | 206.84
2018-07-17 19:00 | 218.46 | 216.61
2018-07-17 19:30 | 210.25 | 208.72
2018-07-17 20:00 | 205.46 | 204.16
2018-07-17 20:30 | 209.69 | 209.62
2018-07-17 21:00 | 207.72 | 207.48
2018-07-17 21:30 | 195.11 | 194.72
2018-07-17 22:00 | 181.59 | 181.1
2018-07-17 22:30 | 174.79 | 174.62
2018-07-17 23:00 | 174.64 | 174.45
2018-07-17 23:30 | 131.34 | 130.86
2018-07-18 | 96.34 | 95.41
2018-07-18 00:30 | 102.12 | 101.12
2018-07-18 01:00 | 72.56 | 71.7
2018-07-18 01:30 | 59.61 | 58.6
2018-07-18 02:00 | 59.37 | 58.42
2018-07-18 02:30 | 60.59 | 59.5
2018-07-18 03:00 | 76.42 | 75.1
2018-07-18 03:30 | 81.32 | 80.04
2018-07-18 04:00 | 90.55 | 89.15
2018-07-18 04:30 | 106.14 | 104.76
2018-07-18 05:00 | 125.98 | 124.89
2018-07-18 05:30 | 141.22 | 140.55
2018-07-18 06:00 | 156.65 | 156.36
2018-07-18 06:30 | 178.41 | 178.41
2018-07-18 07:00 | 200.67 | 199.94
2018-07-18 07:30 | 243.08 | 236.86
2018-07-18 08:00 | 216.25 | 211.84
2018-07-18 08:30 | 166.27 | 164.58
2018-07-18 09:00 | 129.31 | 127.78
2018-07-18 09:30 | 98.06 | 96.41
2018-07-18 10:00 | 84.25 | 84.19
2018-07-18 10:30 | 78.64 | 78.64
2018-07-18 11:00 | 72.29 | 72.27
2018-07-18 11:30 | 63.45 | 63.45
2018-07-18 12:00 | 73.35 | 73.35
2018-07-18 12:30 | 62.47 | 62.46
2018-07-18 13:00 | 56.93 | 56.84
2018-07-18 13:30 | 61.95 | 61.87
2018-07-18 14:00 | 84.03 | 83.95
2018-07-18 14:30 | 102.91 | 102.84
2018-07-18 15:00 | 113.99 | 113.93
2018-07-18 15:30 | 146.17 | 146.14
2018-07-18 16:00 | 147.92 | 147.92
2018-07-18 16:30 | 153.22 | 153.21
2018-07-18 17:00 | 158.8 | 155.69
2018-07-18 17:30 | 168.5 | 158.19
2018-07-18 18:00 | 196.18 | 186.05
2018-07-18 18:30 | 208.98 | 200
2018-07-18 19:00 | 217.76 | 209.27
2018-07-18 19:30 | 201.02 | 192.41
2018-07-18 20:00 | 201.48 | 193.24
2018-07-18 20:30 | 216.14 | 209.01
2018-07-18 21:00 | 186.45 | 182.7
2018-07-18 21:30 | 162.48 | 161.56
2018-07-18 22:00 | 156.1 | 155.5
2018-07-18 22:30 | 165.63 | 165.26
2018-07-18 23:00 | 168.04 | 167.74
2018-07-18 23:30 | 135.23 | 135.01
2018-07-19 | 85.93 | 85.91
2018-07-19 00:30 | 98.24 | 96.95
2018-07-19 01:00 | 82.55 | 81.19
2018-07-19 01:30 | 81.5 | 80.18
2018-07-19 02:00 | 73.55 | 71.36
2018-07-19 02:30 | 77.03 | 74.71
2018-07-19 03:00 | 77.64 | 75.38
2018-07-19 03:30 | 86.58 | 84.55
2018-07-19 04:00 | 92.73 | 90.77
2018-07-19 04:30 | 105.89 | 103.76
2018-07-19 05:00 | 123.64 | 121.5
2018-07-19 05:30 | 153.72 | 151.82
2018-07-19 06:00 | 167.74 | 166.26
2018-07-19 06:30 | 182.36 | 181.76
2018-07-19 07:00 | 185.45 | 185.39
2018-07-19 07:30 | 228.07 | 227.61
2018-07-19 08:00 | 194.7 | 193.7
2018-07-19 08:30 | 130.84 | 130.67
2018-07-19 09:00 | 92.86 | 92.55
2018-07-19 09:30 | 39.54 | 39
2018-07-19 10:00 | 18.95 | 17.82
2018-07-19 10:30 | 23.46 | 23.02
2018-07-19 11:00 | 14.74 | 13.29
2018-07-19 11:30 | 17.41 | 16.53
2018-07-19 12:00 | 31.12 | 30.77
2018-07-19 12:30 | 38.46 | 38.24
2018-07-19 13:00 | 32.96 | 32.83
2018-07-19 13:30 | 22.65 | 22.35
2018-07-19 14:00 | 44.69 | 44.55
2018-07-19 14:30 | 71.07 | 70.97
2018-07-19 15:00 | 72.64 | 72.59
2018-07-19 15:30 | 79.48 | 79.44
2018-07-19 16:00 | 108.72 | 108.71
2018-07-19 16:30 | 90.64 | 90.61
2018-07-19 17:00 | 91.53 | 91.44
2018-07-19 17:30 | 79.43 | 76.95
2018-07-19 18:00 | 140.67 | 124.39
2018-07-19 18:30 | 147.4 | 132.7
2018-07-19 19:00 | 163.25 | 150.59
2018-07-19 19:30 | 159.61 | 147.06
2018-07-19 20:00 | 165.68 | 154.34
2018-07-19 20:30 | 163.25 | 152.71
2018-07-19 21:00 | 134.69 | 129.51
2018-07-19 21:30 | 104.45 | 100.59
2018-07-19 22:00 | 83.62 | 80.13
2018-07-19 22:30 | 92.64 | 90.84
2018-07-19 23:00 | 99.64 | 98.41
2018-07-19 23:30 | 79.41 | 77.34
2018-07-20 | 38.52 | 33.16
2018-07-20 00:30 | 43.3 | 38.45
2018-07-20 01:00 | 29.5 | 24.27
2018-07-20 01:30 | 28.78 | 24.59
2018-07-20 02:00 | 42.14 | 39.69
2018-07-20 02:30 | 42.25 | 40.12
2018-07-20 03:00 | 43.59 | 41.67
2018-07-20 03:30 | 52.08 | 50.27
2018-07-20 04:00 | 51.45 | 49.51
2018-07-20 04:30 | 63.76 | 61.85
2018-07-20 05:00 | 56.01 | 52.92
2018-07-20 05:30 | 81.38 | 78.37
2018-07-20 06:00 | 88.33 | 85.72
2018-07-20 06:30 | 98.52 | 98.45
2018-07-20 07:00 | 124.65 | 124.65
2018-07-20 07:30 | 135.86 | 135.86
2018-07-20 08:00 | 120.37 | 120.32
2018-07-20 08:30 | 81.54 | 80.39
2018-07-20 09:00 | 47.53 | 44.98
2018-07-20 09:30 | 31.07 | 25.61
2018-07-20 10:00 | 31.61 | 27.26
2018-07-20 10:30 | 48.73 | 47.33
2018-07-20 11:00 | 51.78 | 50.05
2018-07-20 11:30 | 62.88 | 62.75
2018-07-20 12:00 | 64.66 | 64.58
2018-07-20 12:30 | 66.36 | 66.2
2018-07-20 13:00 | 94.27 | 94.13
2018-07-20 13:30 | 80.61 | 80.44
2018-07-20 14:00 | 85.38 | 85.25
2018-07-20 14:30 | 106.01 | 105.87
2018-07-20 15:00 | 109.57 | 109.43
2018-07-20 15:30 | 102.32 | 102.24
2018-07-20 16:00 | 105.08 | 105.03
2018-07-20 16:30 | 109.55 | 109.49
2018-07-20 17:00 | 92.65 | 92.49
2018-07-20 17:30 | 80.38 | 80.29
2018-07-20 18:00 | 84.29 | 82.34
2018-07-20 18:30 | 99.34 | 96.88
2018-07-20 19:00 | 108.84 | 107.32
2018-07-20 19:30 | 103.27 | 103.27
2018-07-20 20:00 | 87.26 | 87.13
2018-07-20 20:30 | 73.21 | 73.13
2018-07-20 21:00 | 39.91 | 39.89
2018-07-20 21:30 | 46.35 | 46.29
2018-07-20 22:00 | 47.49 | 47.17
2018-07-20 22:30 | 47.24 | 46.71
2018-07-20 23:00 | 36.12 | 35.16
2018-07-20 23:30 | 18.31 | 15.51
2018-07-21 | 15 | -11.45
2018-07-21 00:30 | 13.53 | 6.41
2018-07-21 01:00 | 11.42 | -2.52
2018-07-21 01:30 | 12.21 | -2.15
2018-07-21 02:00 | 12.85 | -0.91
2018-07-21 02:30 | 13.27 | -1.49
2018-07-21 03:00 | 12.7 | 0.66
2018-07-21 03:30 | 13.09 | -0.23
2018-07-21 04:00 | 13.97 | 3.7
2018-07-21 04:30 | 16.26 | 7.95
2018-07-21 05:00 | 21.4 | 16.45
2018-07-21 05:30 | 31.9 | 28.69
2018-07-21 06:00 | 44.09 | 42.13
2018-07-21 06:30 | 51.69 | 49.71
2018-07-21 07:00 | 54.46 | 52.43
2018-07-21 07:30 | 55.92 | 54.5
2018-07-21 08:00 | 61.36 | 60.67
2018-07-21 08:30 | 48.22 | 47.92
2018-07-21 09:00 | 13.76 | 7.74
2018-07-21 09:30 | 36.27 | -29.93
2018-07-21 10:00 | 37.46 | -31.64
2018-07-21 10:30 | 38.81 | -33.48
2018-07-21 11:00 | 43.34 | -38.8
2018-07-21 11:30 | 45.32 | -41.57
2018-07-21 12:00 | 47.72 | -44.45
2018-07-21 12:30 | 40.36 | -37
2018-07-21 13:00 | 34.8 | -31.01
2018-07-21 13:30 | 29.34 | -25.37
2018-07-21 14:00 | 45.8 | -42.88
2018-07-21 14:30 | 39.38 | -36.59
2018-07-21 15:00 | 15.79 | -10.27
2018-07-21 15:30 | 13.55 | -4.91
2018-07-21 16:00 | 33.3 | 31.17
2018-07-21 16:30 | 74.12 | 73.11
2018-07-21 17:00 | 73.53 | 71.73
2018-07-21 17:30 | 81.67 | 61.44
2018-07-21 18:00 | 83.2 | 58.2
2018-07-21 18:30 | 93 | 68.91
2018-07-21 19:00 | 101 | 80.29
2018-07-21 19:30 | 115.23 | 99.29
2018-07-21 20:00 | 108.27 | 91.3
2018-07-21 20:30 | 110.71 | 95.66
2018-07-21 21:00 | 107.15 | 93.23
2018-07-21 21:30 | 93.63 | 86.7
2018-07-21 22:00 | 66.63 | 64.42
2018-07-21 22:30 | 75.27 | 73.92
2018-07-21 23:00 | 76.44 | 75.49
2018-07-21 23:30 | 44.78 | 43.54
2018-07-22 | 20.41 | 18.73
2018-07-22 00:30 | 41.43 | 41.08
2018-07-22 01:00 | 37.36 | 33.39
2018-07-22 01:30 | 24.54 | 18.45
2018-07-22 02:00 | 19.76 | 12.34
2018-07-22 02:30 | 15.52 | 1.52
2018-07-22 03:00 | 15.79 | -5.64
2018-07-22 03:30 | 17.3 | -8.53
2018-07-22 04:00 | 19.41 | -12.6
2018-07-22 04:30 | 17.92 | -11.26
2018-07-22 05:00 | 17.08 | -10.54
2018-07-22 05:30 | 23.48 | 18.93
2018-07-22 06:00 | 36.79 | 33.62
2018-07-22 06:30 | 50.27 | 47.68
2018-07-22 07:00 | 51.75 | 49.36
2018-07-22 07:30 | 77.01 | 75.77
2018-07-22 08:00 | 59.57 | 58.49
2018-07-22 08:30 | 46.55 | 45.86
2018-07-22 09:00 | 28.31 | 27.88
2018-07-22 09:30 | 13.42 | -13.34
2018-07-22 10:00 | 17.17 | -17.09
2018-07-22 10:30 | 12.91 | -12.67
2018-07-22 11:00 | 8.39 | 6.89
2018-07-22 11:30 | 24.2 | 23.22
2018-07-22 12:00 | 9.59 | 6.42
2018-07-22 12:30 | 12.73 | 10.12
2018-07-22 13:00 | 10.28 | -8.91
2018-07-22 13:30 | 7.58 | 3.32
2018-07-22 14:00 | 16.72 | 14.96
2018-07-22 14:30 | 12.55 | 9.71
2018-07-22 15:00 | 10.29 | -7.23
2018-07-22 15:30 | 14.97 | 12.15
2018-07-22 16:00 | 43.35 | 42.41
2018-07-22 16:30 | 62.93 | 62.26
2018-07-22 17:00 | 83.86 | 83.65
2018-07-22 17:30 | 108.08 | 104.98
2018-07-22 18:00 | 133.55 | 119.64
2018-07-22 18:30 | 136.72 | 122.77
2018-07-22 19:00 | 140.43 | 127.08
2018-07-22 19:30 | 141.34 | 128.84
2018-07-22 20:00 | 142.19 | 130.38
2018-07-22 20:30 | 139.35 | 128.4
2018-07-22 21:00 | 128 | 119.63
2018-07-22 21:30 | 97.14 | 94.2
2018-07-22 22:00 | 88.65 | 86
2018-07-22 22:30 | 102.33 | 101.89
2018-07-22 23:00 | 103.9 | 102.98
2018-07-22 23:30 | 68.76 | 66.97
2018-07-23 | 51.88 | 48.77
2018-07-23 00:30 | 45.94 | 42.4
2018-07-23 01:00 | 38.84 | 35.16
2018-07-23 01:30 | 16.93 | 7.69
2018-07-23 02:00 | 18.14 | 10.79
2018-07-23 02:30 | 17.22 | 8.38
2018-07-23 03:00 | 19.27 | 11.47
2018-07-23 03:30 | 19.97 | 12.33
2018-07-23 04:00 | 26.8 | 20.9
2018-07-23 04:30 | 35.97 | 30.98
2018-07-23 05:00 | 56.61 | 53.48
2018-07-23 05:30 | 81.5 | 79.93
2018-07-23 06:00 | 91.34 | 90.4
2018-07-23 06:30 | 105.56 | 105.19
2018-07-23 07:00 | 128.57 | 128.19
2018-07-23 07:30 | 188.27 | 187.95
2018-07-23 08:00 | 190.57 | 188.88
2018-07-23 08:30 | 180.06 | 178.24
2018-07-23 09:00 | 167.65 | 165.84
2018-07-23 09:30 | 154.56 | 153.87
2018-07-23 10:00 | 147.13 | 146.75
2018-07-23 10:30 | 134.8 | 134.37
2018-07-23 11:00 | 132.05 | 131.03
2018-07-23 11:30 | 133.22 | 130.3
2018-07-23 12:00 | 135.47 | 132.59
2018-07-23 12:30 | 138.52 | 135.99
2018-07-23 13:00 | 138.25 | 135.75
2018-07-23 13:30 | 141.29 | 138.79
2018-07-23 14:00 | 144.76 | 142.45
2018-07-23 14:30 | 146.42 | 144.06
2018-07-23 15:00 | 146.52 | 144.23
2018-07-23 15:30 | 147.95 | 145.85
2018-07-23 16:00 | 148.31 | 146.14
2018-07-23 16:30 | 154.25 | 151.55
2018-07-23 17:00 | 164.86 | 159.71
2018-07-23 17:30 | 122.39 | 115.13
2018-07-23 18:00 | 138.94 | 121.58
2018-07-23 18:30 | 149.58 | 133.55
2018-07-23 19:00 | 154.42 | 139.26
2018-07-23 19:30 | 151.29 | 136.92
2018-07-23 20:00 | 150.76 | 136.97
2018-07-23 20:30 | 147.24 | 134.23
2018-07-23 21:00 | 134.98 | 122.19
2018-07-23 21:30 | 132.17 | 120.95
2018-07-23 22:00 | 117.18 | 109.44
2018-07-23 22:30 | 95.2 | 91.83
2018-07-23 23:00 | 105.88 | 105.33
2018-07-23 23:30 | 86.36 | 85.85
2018-07-24 | 62.62 | 61.81
2018-07-24 00:30 | 60.51 | 59.72
2018-07-24 01:00 | 46.96 | 46.38
2018-07-24 01:30 | 40.71 | 40.17
2018-07-24 02:00 | 44.49 | 43.94
2018-07-24 02:30 | 48.28 | 47.65
2018-07-24 03:00 | 51.98 | 51.32
2018-07-24 03:30 | 48.28 | 47.52
2018-07-24 04:00 | 56.72 | 55.84
2018-07-24 04:30 | 67.5 | 66.55
2018-07-24 05:00 | 71.97 | 71.09
2018-07-24 05:30 | 80.38 | 79.58
2018-07-24 06:00 | 90.56 | 90.3
2018-07-24 06:30 | 105.04 | 105.04
2018-07-24 07:00 | 126.9 | 126.9
2018-07-24 07:30 | 142.1 | 141.87
2018-07-24 08:00 | 140.61 | 140.21
2018-07-24 08:30 | 132 | 131.64
2018-07-24 09:00 | 122.2 | 121.9
2018-07-24 09:30 | 102.3 | 101.95
2018-07-24 10:00 | 88.53 | 87.62
2018-07-24 10:30 | 85.98 | 82.78
2018-07-24 11:00 | 86.1 | 80.81
2018-07-24 11:30 | 70.8 | 64.5
2018-07-24 12:00 | 79.42 | 74.14
2018-07-24 12:30 | 67.98 | 61.84
2018-07-24 13:00 | 89.78 | 85.35
2018-07-24 13:30 | 80.16 | 74.96
2018-07-24 14:00 | 92.1 | 88.18
2018-07-24 14:30 | 98.53 | 95.41
2018-07-24 15:00 | 99.93 | 97.1
2018-07-24 15:30 | 101.29 | 98.75
2018-07-24 16:00 | 103.73 | 101.79
2018-07-24 16:30 | 108.3 | 106.6
2018-07-24 17:00 | 117.19 | 113.32
2018-07-24 17:30 | 125.16 | 120.17
2018-07-24 18:00 | 131.41 | 125.29
2018-07-24 18:30 | 131.49 | 125.62
2018-07-24 19:00 | 135.39 | 130.02
2018-07-24 19:30 | 135.36 | 131.09
2018-07-24 20:00 | 136.44 | 132.72
2018-07-24 20:30 | 137.98 | 134.83
2018-07-24 21:00 | 126.11 | 126.1
2018-07-24 21:30 | 115.68 | 115.38
2018-07-24 22:00 | 107.21 | 106.78
2018-07-24 22:30 | 104.66 | 104.02
2018-07-24 23:00 | 111.27 | 110.46
2018-07-24 23:30 | 92.21 | 91.23
2018-07-25 | 73.79 | 72.32
2018-07-25 00:30 | 56.44 | 54.57
2018-07-25 01:00 | 47.88 | 45.46
2018-07-25 01:30 | 37.7 | 35.17
2018-07-25 02:00 | 39.31 | 36.98
2018-07-25 02:30 | 45.07 | 43.51
2018-07-25 03:00 | 41.63 | 40.16
2018-07-25 03:30 | 43.76 | 42.37
2018-07-25 04:00 | 51.48 | 49.83
2018-07-25 04:30 | 66.41 | 64.53
2018-07-25 05:00 | 69.85 | 67.61
2018-07-25 05:30 | 79.32 | 76.23
2018-07-25 06:00 | 88.72 | 86.43
2018-07-25 06:30 | 100.64 | 100.26
2018-07-25 07:00 | 121.3 | 121
2018-07-25 07:30 | 139.34 | 134.65
2018-07-25 08:00 | 142.26 | 137.16
2018-07-25 08:30 | 137.56 | 132.08
2018-07-25 09:00 | 134.52 | 129.12
2018-07-25 09:30 | 129.67 | 124.2
2018-07-25 10:00 | 130.7 | 125.38
2018-07-25 10:30 | 115.6 | 109.59
2018-07-25 11:00 | 108.04 | 101.87
2018-07-25 11:30 | 97.95 | 91.49
2018-07-25 12:00 | 92.27 | 85.5
2018-07-25 12:30 | 83.81 | 76.48
2018-07-25 13:00 | 79.33 | 72.27
2018-07-25 13:30 | 83.25 | 76.36
2018-07-25 14:00 | 96.04 | 90.22
2018-07-25 14:30 | 105.74 | 100.23
2018-07-25 15:00 | 112.55 | 107.54
2018-07-25 15:30 | 107.1 | 102.15
2018-07-25 16:00 | 111.58 | 107.03
2018-07-25 16:30 | 113.07 | 108.81
2018-07-25 17:00 | 116.95 | 112.54
2018-07-25 17:30 | 123.31 | 118.04
2018-07-25 18:00 | 128.19 | 121.46
2018-07-25 18:30 | 127.17 | 120.99
2018-07-25 19:00 | 131.25 | 125.57
2018-07-25 19:30 | 131.56 | 126.53
2018-07-25 20:00 | 132.3 | 127.81
2018-07-25 20:30 | 132.73 | 128.95
2018-07-25 21:00 | 125.57 | 122.56
2018-07-25 21:30 | 144.96 | 143.67
2018-07-25 22:00 | 135.97 | 135.53
2018-07-25 22:30 | 123.99 | 123.45
2018-07-25 23:00 | 132.13 | 131.41
2018-07-25 23:30 | 114.96 | 113.85
2018-07-26 | 77.22 | 75.46
2018-07-26 00:30 | 67.59 | 65.73
2018-07-26 01:00 | 50.18 | 47.9
2018-07-26 01:30 | 44.36 | 41.85
2018-07-26 02:00 | 47.94 | 45.68
2018-07-26 02:30 | 38.52 | 36.03
2018-07-26 03:00 | 30.68 | 27.71
2018-07-26 03:30 | 40.17 | 37.7
2018-07-26 04:00 | 38.19 | 35.53
2018-07-26 04:30 | 54.42 | 52.03
2018-07-26 05:00 | 69.34 | 66.89
2018-07-26 05:30 | 112.7 | 110.52
2018-07-26 06:00 | 146.09 | 144.49
2018-07-26 06:30 | 144.46 | 143.18
2018-07-26 07:00 | 138.65 | 138.16
2018-07-26 07:30 | 152.92 | 152.59
2018-07-26 08:00 | 126.43 | 126.12
2018-07-26 08:30 | 83.3 | 82.89
2018-07-26 09:00 | 61.77 | 61.2
2018-07-26 09:30 | 49.16 | 48.01
2018-07-26 10:00 | 34.17 | 32.34
2018-07-26 10:30 | 38.82 | 37.27
2018-07-26 11:00 | 33.92 | 32.22
2018-07-26 11:30 | 36.07 | 34.02
2018-07-26 12:00 | 31.25 | 29.15
2018-07-26 12:30 | 35.51 | 33.29
2018-07-26 13:00 | 46.81 | 45.13
2018-07-26 13:30 | 52.96 | 51.3
2018-07-26 14:00 | 62.66 | 61.32
2018-07-26 14:30 | 81.93 | 80.86
2018-07-26 15:00 | 93.56 | 92.59
2018-07-26 15:30 | 103.17 | 102.2
2018-07-26 16:00 | 132.08 | 131.36
2018-07-26 16:30 | 140.33 | 139.6
2018-07-26 17:00 | 146.49 | 145.86
2018-07-26 17:30 | 138.99 | 138.55
2018-07-26 18:00 | 111.77 | 111.77
2018-07-26 18:30 | 85.78 | 82.74
2018-07-26 19:00 | 102.53 | 100.42
2018-07-26 19:30 | 123.18 | 123.13
2018-07-26 20:00 | 126.2 | 126.03
2018-07-26 20:30 | 103.64 | 103.45
2018-07-26 21:00 | 108.99 | 108.72
2018-07-26 21:30 | 96.83 | 96.58
2018-07-26 22:00 | 92.65 | 92.58
2018-07-26 22:30 | 87.61 | 86.03
2018-07-26 23:00 | 89.85 | 87.66
2018-07-26 23:30 | 57.19 | 55.32
2018-07-27 | 34.86 | 33.01
2018-07-27 00:30 | 47.16 | 45.14
2018-07-27 01:00 | 43.04 | 41.15
2018-07-27 01:30 | 44.31 | 42.8
2018-07-27 02:00 | 75.99 | 75.58
2018-07-27 02:30 | 82.37 | 82.37
2018-07-27 03:00 | 79.22 | 79.22
2018-07-27 03:30 | 59.74 | 58.73
2018-07-27 04:00 | 25.61 | 23.1
2018-07-27 04:30 | 74.79 | 73.42
2018-07-27 05:00 | 81.39 | 78.87
2018-07-27 05:30 | 101 | 98.32
2018-07-27 06:00 | 123.54 | 121.07
2018-07-27 06:30 | 129.83 | 127.71
2018-07-27 07:00 | 136.47 | 134.91
2018-07-27 07:30 | 141.86 | 141.79
2018-07-27 08:00 | 119.43 | 119.43
2018-07-27 08:30 | 105.76 | 105.75
2018-07-27 09:00 | 99.87 | 99.86
2018-07-27 09:30 | 70.37 | 70.33
2018-07-27 10:00 | 50.51 | 50.45
2018-07-27 10:30 | 50.58 | 50.52
2018-07-27 11:00 | 39.74 | 39.54
2018-07-27 11:30 | 22.19 | 21.69
2018-07-27 12:00 | 38.77 | 38.35
2018-07-27 12:30 | 122.39 | 122.27
2018-07-27 13:00 | 55.74 | 55.37
2018-07-27 13:30 | 54.89 | 54.89
2018-07-27 14:00 | 89.22 | 89.22
2018-07-27 14:30 | 85.94 | 85.92
2018-07-27 15:00 | 120.25 | 120.24
2018-07-27 15:30 | 131.97 | 131.97
2018-07-27 16:00 | 125.42 | 125.34
2018-07-27 16:30 | 108.36 | 108.25
2018-07-27 17:00 | 117.94 | 117.93
2018-07-27 17:30 | 136.69 | 136.69
2018-07-27 18:00 | 128.27 | 127.26
2018-07-27 18:30 | 115.54 | 115.46
2018-07-27 19:00 | 123.07 | 122.82
2018-07-27 19:30 | 112.12 | 111.65
2018-07-27 20:00 | 93.09 | 92.29
2018-07-27 20:30 | 95.24 | 94.44
2018-07-27 21:00 | 99.66 | 95.78
2018-07-27 21:30 | 83.12 | 81.29
2018-07-27 22:00 | 60.7 | 59.18
2018-07-27 22:30 | 104.01 | 102.98
2018-07-27 23:00 | 63.72 | 61.47
2018-07-27 23:30 | 51.4 | 48
2018-07-28 | 22.64 | 14.86
2018-07-28 00:30 | 32.76 | 27.02
2018-07-28 01:00 | 26.78 | 19.65
2018-07-28 01:30 | 25.52 | 15.85
2018-07-28 02:00 | 32.6 | 17.2
2018-07-28 02:30 | 32.98 | 17.98
2018-07-28 03:00 | 29.79 | 13.2
2018-07-28 03:30 | 30.55 | 13.49
2018-07-28 04:00 | 32.08 | 16.53
2018-07-28 04:30 | 37.24 | 23.91
2018-07-28 05:00 | 47.98 | 37.65
2018-07-28 05:30 | 65.17 | 57.36
2018-07-28 06:00 | 76.28 | 69.02
2018-07-28 06:30 | 86.98 | 80.48
2018-07-28 07:00 | 100.34 | 94.85
2018-07-28 07:30 | 95.28 | 89.81
2018-07-28 08:00 | 73.09 | 66.05
2018-07-28 08:30 | 50.87 | 42.91
2018-07-28 09:00 | 42.7 | 34.18
2018-07-28 09:30 | 32.24 | 20.82
2018-07-28 10:00 | 19.27 | 1.54
2018-07-28 10:30 | 20.68 | -8.4
2018-07-28 11:00 | 21.65 | -6.4
2018-07-28 11:30 | 22.28 | 1.13
2018-07-28 12:00 | 23.09 | 3.93
2018-07-28 12:30 | 23.88 | 5.39
2018-07-28 13:00 | 28.44 | 14.97
2018-07-28 13:30 | 40.45 | 31.86
2018-07-28 14:00 | 70.82 | 65.57
2018-07-28 14:30 | 40.45 | 31.5
2018-07-28 15:00 | 62.33 | 56.84
2018-07-28 15:30 | 112.99 | 109.92
2018-07-28 16:00 | 117.17 | 113.26
2018-07-28 16:30 | 117.26 | 114.48
2018-07-28 17:00 | 100.24 | 99.8
2018-07-28 17:30 | 90.02 | 89.69
2018-07-28 18:00 | 101.43 | 101.24
2018-07-28 18:30 | 119.67 | 119.54
2018-07-28 19:00 | 125.28 | 125.15
2018-07-28 19:30 | 121.45 | 120.5
2018-07-28 20:00 | 114.15 | 112.48
2018-07-28 20:30 | 122.16 | 121.82
2018-07-28 21:00 | 122.24 | 121.61
2018-07-28 21:30 | 135.71 | 134.85
2018-07-28 22:00 | 134.49 | 133.45
2018-07-28 22:30 | 146.28 | 145.62
2018-07-28 23:00 | 140.59 | 139.6
2018-07-28 23:30 | 141.92 | 140.74
2018-07-29 | 103.35 | 101.22
2018-07-29 00:30 | 92.97 | 90.54
2018-07-29 01:00 | 82.34 | 79.69
2018-07-29 01:30 | 77.53 | 72.43
2018-07-29 02:00 | 63.47 | 57.23
2018-07-29 02:30 | 49.43 | 41.59
2018-07-29 03:00 | 40.17 | 30.59
2018-07-29 03:30 | 53.36 | 47.14
2018-07-29 04:00 | 69.7 | 65.26
2018-07-29 04:30 | 66.03 | 60.99
2018-07-29 05:00 | 76.84 | 71.43
2018-07-29 05:30 | 81.03 | 75.51
2018-07-29 06:00 | 79.11 | 73.21
2018-07-29 06:30 | 67.43 | 58.99
2018-07-29 07:00 | 77.39 | 70.46
2018-07-29 07:30 | 96.4 | 90.35
2018-07-29 08:00 | 97.82 | 91.46
2018-07-29 08:30 | 92.07 | 86.21
2018-07-29 09:00 | 81.21 | 75.28
2018-07-29 09:30 | 66.09 | 58.61
2018-07-29 10:00 | 71.73 | 65.05
2018-07-29 10:30 | 49.3 | 39.2
2018-07-29 11:00 | 34.33 | 19.84
2018-07-29 11:30 | 27.16 | -0.75
2018-07-29 12:00 | 34.01 | 20.01
2018-07-29 12:30 | 90.01 | 85.97
2018-07-29 13:00 | 51.64 | 43.87
2018-07-29 13:30 | 95.62 | 91.81
2018-07-29 14:00 | 39.14 | 27.21
2018-07-29 14:30 | 37.52 | 25.63
2018-07-29 15:00 | 41.56 | 30.82
2018-07-29 15:30 | 59.83 | 52.94
2018-07-29 16:00 | 96.31 | 92.21
2018-07-29 16:30 | 121.5 | 119.69
2018-07-29 17:00 | 163.96 | 163.76
2018-07-29 17:30 | 181.91 | 181.86
2018-07-29 18:00 | 182.95 | 182.29
2018-07-29 18:30 | 196.5 | 195.8
2018-07-29 19:00 | 193.08 | 192.28
2018-07-29 19:30 | 179.22 | 178.1
2018-07-29 20:00 | 167.1 | 166.41
2018-07-29 20:30 | 156.48 | 156.09
2018-07-29 21:00 | 141.89 | 141.32
2018-07-29 21:30 | 133.44 | 132.49
2018-07-29 22:00 | 124.08 | 122.84
2018-07-29 22:30 | 127.88 | 126.51
2018-07-29 23:00 | 127.25 | 125.69
2018-07-29 23:30 | 99.53 | 97.16
2018-07-30 | 74.28 | 70.72
2018-07-30 00:30 | 87.99 | 85.44
2018-07-30 01:00 | 61.5 | 57.43
2018-07-30 01:30 | 29.62 | 22.45
2018-07-30 02:00 | 39.18 | 34.61
2018-07-30 02:30 | 41.6 | 32.08
2018-07-30 03:00 | 41.67 | 30.52
2018-07-30 03:30 | 42.18 | 31.07
2018-07-30 04:00 | 43.72 | 32.28
2018-07-30 04:30 | 46.71 | 35.21
2018-07-30 05:00 | 50.93 | 39.73
2018-07-30 05:30 | 60.82 | 50.78
2018-07-30 06:00 | 90.48 | 83.98
2018-07-30 06:30 | 130.58 | 127.17
2018-07-30 07:00 | 125.94 | 123.99
2018-07-30 07:30 | 136.23 | 135.77
2018-07-30 08:00 | 89.28 | 88.97
2018-07-30 08:30 | 58.61 | 58.49
2018-07-30 09:00 | 58.14 | 58.01
2018-07-30 09:30 | 42.01 | 41.89
2018-07-30 10:00 | 34.77 | 34.63
2018-07-30 10:30 | 36.37 | 36.24
2018-07-30 11:00 | 36.31 | 36.21
2018-07-30 11:30 | 25.07 | 24.86
2018-07-30 12:00 | 28.49 | 28.31
2018-07-30 12:30 | 29.13 | 28.86
2018-07-30 13:00 | 61.36 | 61.21
2018-07-30 13:30 | 30.23 | 30.06
2018-07-30 14:00 | 50.51 | 50.37
2018-07-30 14:30 | 73.67 | 73.59
2018-07-30 15:00 | 107.92 | 107.82
2018-07-30 15:30 | 120.07 | 119.93
2018-07-30 16:00 | 152.11 | 151.94
2018-07-30 16:30 | 148.7 | 148.58
2018-07-30 17:00 | 171.25 | 171.2
2018-07-30 17:30 | 170.09 | 170.07
2018-07-30 18:00 | 168.36 | 163.57
2018-07-30 18:30 | 170.37 | 162.1
2018-07-30 19:00 | 171.98 | 164.29
2018-07-30 19:30 | 173.72 | 170.22
2018-07-30 20:00 | 179.77 | 178.09
2018-07-30 20:30 | 180.43 | 180.37
2018-07-30 21:00 | 165.45 | 165.01
2018-07-30 21:30 | 148.24 | 147.68
2018-07-30 22:00 | 153.94 | 153.27
2018-07-30 22:30 | 145.03 | 144.01
2018-07-30 23:00 | 140.2 | 139.05
2018-07-30 23:30 | 103.5 | 101.86
2018-07-31 | 77.35 | 75.4
2018-07-31 00:30 | 63.85 | 61.87
2018-07-31 01:00 | 56.98 | 54.61
2018-07-31 01:30 | 51.25 | 48.95
2018-07-31 02:00 | 53.17 | 51
2018-07-31 02:30 | 61.75 | 56.64
2018-07-31 03:00 | 58.42 | 52.11
2018-07-31 03:30 | 58.71 | 52.05
2018-07-31 04:00 | 67.38 | 61.47
2018-07-31 04:30 | 75.69 | 69.84
2018-07-31 05:00 | 87.77 | 82.26
2018-07-31 05:30 | 119.44 | 115.48
2018-07-31 06:00 | 130.45 | 126.07
2018-07-31 06:30 | 144.13 | 140.98
2018-07-31 07:00 | 116.23 | 115.26
2018-07-31 07:30 | 113.12 | 112.65
2018-07-31 08:00 | 110.98 | 110.16
2018-07-31 08:30 | 104.45 | 104.26
2018-07-31 09:00 | 76.51 | 75.99
2018-07-31 09:30 | 41.36 | 40.49
2018-07-31 10:00 | 24.18 | 23.49
2018-07-31 10:30 | 21.01 | 19.22
2018-07-31 11:00 | 12.01 | 11.99
2018-07-31 11:30 | 35.68 | 35.66
2018-07-31 12:00 | 75.54 | 75.5
2018-07-31 12:30 | 115.19 | 115.15
2018-07-31 13:00 | 96.72 | 96.64
2018-07-31 13:30 | 117.92 | 117.86
2018-07-31 14:00 | 122.3 | 122.26
2018-07-31 14:30 | 85.6 | 85.51
2018-07-31 15:00 | 81.69 | 81.55
2018-07-31 15:30 | 114.55 | 114.43
2018-07-31 16:00 | 134.5 | 134.37
2018-07-31 16:30 | 136.42 | 136.29
2018-07-31 17:00 | 164.26 | 164.19
2018-07-31 17:30 | 174.95 | 174.68
2018-07-31 18:00 | 153.84 | 146.19
2018-07-31 18:30 | 171.47 | 170.69
2018-07-31 19:00 | 169.31 | 168.89
2018-07-31 19:30 | 170.65 | 170.36
2018-07-31 20:00 | 164.53 | 164.03
2018-07-31 20:30 | 150.53 | 149.73
2018-07-31 21:00 | 140.23 | 139.07
2018-07-31 21:30 | 158.03 | 156.73
2018-07-31 22:00 | 171.9 | 171.41
2018-07-31 22:30 | 175.06 | 174.51
2018-07-31 23:00 | 167.64 | 166.87
2018-07-31 23:30 | 150.28 | 149.19
2018-08-01 | 104.3 | 102.43
2018-08-01 00:30 | 100.2 | 98.11
2018-08-01 01:00 | 70.17 | 67.44
2018-08-01 01:30 | 46.01 | 41.99
2018-08-01 02:00 | 44.66 | 40.45
2018-08-01 02:30 | 48.19 | 44.19
2018-08-01 03:00 | 65.56 | 62.57
2018-08-01 03:30 | 74.16 | 71.44
2018-08-01 04:00 | 85.9 | 83.18
2018-08-01 04:30 | 105.47 | 103.12
2018-08-01 05:00 | 117.56 | 115.55
2018-08-01 05:30 | 96.54 | 94.17
2018-08-01 06:00 | 124.16 | 122.91
2018-08-01 06:30 | 127.53 | 127.04
2018-08-01 07:00 | 138.64 | 138.6
2018-08-01 07:30 | 141.66 | 138.66
2018-08-01 08:00 | 110.92 | 106.1
2018-08-01 08:30 | 94.14 | 89.37
2018-08-01 09:00 | 76.65 | 70.93
2018-08-01 09:30 | 58.22 | 50.87
2018-08-01 10:00 | 42.21 | 31.74
2018-08-01 10:30 | 31.32 | 28.2
2018-08-01 11:00 | 19.65 | 19.47
2018-08-01 11:30 | 2.36 | 1.66
2018-08-01 12:00 | 1.65 | -0.24
2018-08-01 12:30 | 3.58 | 2.76
2018-08-01 13:00 | 4.99 | 4.13
2018-08-01 13:30 | 6.51 | 6.15
2018-08-01 14:00 | 15.32 | 15.17
2018-08-01 14:30 | 36.6 | 36.52
2018-08-01 15:00 | 45.62 | 45.54
2018-08-01 15:30 | 62.5 | 62.37
2018-08-01 16:00 | 80.67 | 80.55
2018-08-01 16:30 | 86.07 | 85.91
2018-08-01 17:00 | 90.76 | 90.75
2018-08-01 17:30 | 96.27 | 92.04
2018-08-01 18:00 | 108.35 | 102.84
2018-08-01 18:30 | 109.03 | 103.97
2018-08-01 19:00 | 99.72 | 94.34
2018-08-01 19:30 | 108.84 | 104.55
2018-08-01 20:00 | 120.09 | 116.76
2018-08-01 20:30 | 142.89 | 140.47
2018-08-01 21:00 | 122.42 | 120.3
2018-08-01 21:30 | 118.06 | 116.62
2018-08-01 22:00 | 93.08 | 91.82
2018-08-01 22:30 | 87.52 | 87.24
2018-08-01 23:00 | 99.33 | 94.67
2018-08-01 23:30 | 62.7 | 55.81
2018-08-02 | 36.63 | 24.11
2018-08-02 00:30 | 42.5 | 31.74
2018-08-02 01:00 | 41.84 | 31.5
2018-08-02 01:30 | 32.63 | 19.6
2018-08-02 02:00 | 33.7 | 22.19
2018-08-02 02:30 | 41.88 | 32.88
2018-08-02 03:00 | 62.09 | 55.04
2018-08-02 03:30 | 75.66 | 69.18
2018-08-02 04:00 | 88.04 | 82.87
2018-08-02 04:30 | 94.54 | 89.01
2018-08-02 05:00 | 116.28 | 111.75
2018-08-02 05:30 | 136.86 | 132.52
2018-08-02 06:00 | 159.09 | 155.54
2018-08-02 06:30 | 175.6 | 173.24
2018-08-02 07:00 | 157.19 | 156.42
2018-08-02 07:30 | 177.81 | 177.09
2018-08-02 08:00 | 150.32 | 147.46
2018-08-02 08:30 | 133.66 | 132.86
2018-08-02 09:00 | 106.31 | 106.23
2018-08-02 09:30 | 80.4 | 80.24
2018-08-02 10:00 | 63.96 | 63.8
2018-08-02 10:30 | 62.98 | 62.86
2018-08-02 11:00 | 54.56 | 54.41
2018-08-02 11:30 | 48.06 | 47.96
2018-08-02 12:00 | 75.01 | 74.96
2018-08-02 12:30 | 46.21 | 45.77
2018-08-02 13:00 | 62.1 | 61.79
2018-08-02 13:30 | 55.12 | 54.87
2018-08-02 14:00 | 72.84 | 72.64
2018-08-02 14:30 | 91.79 | 91.68
2018-08-02 15:00 | 105.18 | 105.05
2018-08-02 15:30 | 133.5 | 133.38
2018-08-02 16:00 | 144.33 | 144.17
2018-08-02 16:30 | 143.8 | 143.64
2018-08-02 17:00 | 151.56 | 151.37
2018-08-02 17:30 | 138.23 | 137.18
2018-08-02 18:00 | 169.87 | 169.48
2018-08-02 18:30 | 181.55 | 181.24
2018-08-02 19:00 | 185.99 | 185.72
2018-08-02 19:30 | 173.01 | 172.63
2018-08-02 20:00 | 157.03 | 156.32
2018-08-02 20:30 | 158.28 | 157.41
2018-08-02 21:00 | 152.04 | 150.84
2018-08-02 21:30 | 132.05 | 130.28
2018-08-02 22:00 | 113.16 | 112
2018-08-02 22:30 | 109.18 | 108.33
2018-08-02 23:00 | 100.74 | 99.53
2018-08-02 23:30 | 65.57 | 63.39
2018-08-03 | 28.52 | 22.43
2018-08-03 00:30 | 28.47 | 22.05
2018-08-03 01:00 | 18.53 | 8.25
2018-08-03 01:30 | 15.4 | 0.34
2018-08-03 02:00 | 15.78 | -0.27
2018-08-03 02:30 | 25.41 | 19.35
2018-08-03 03:00 | 29.43 | 24.13
2018-08-03 03:30 | 26.38 | 19.75
2018-08-03 04:00 | 32.55 | 26.82
2018-08-03 04:30 | 48.12 | 44
2018-08-03 05:00 | 66.52 | 63.58
2018-08-03 05:30 | 104.06 | 102.03
2018-08-03 06:00 | 124.87 | 123.41
2018-08-03 06:30 | 144.08 | 143.33
2018-08-03 07:00 | 144.77 | 144.25
2018-08-03 07:30 | 178.17 | 178.1
2018-08-03 08:00 | 131.71 | 131.65
2018-08-03 08:30 | 101.12 | 101.08
2018-08-03 09:00 | 83.82 | 83.77
2018-08-03 09:30 | 71.46 | 71.4
2018-08-03 10:00 | 77.23 | 77.18
2018-08-03 10:30 | 74.51 | 74.51
2018-08-03 11:00 | 75.53 | 75.53
2018-08-03 11:30 | 85.9 | 85.9
2018-08-03 12:00 | 91.17 | 91.17
2018-08-03 12:30 | 86.28 | 86.27
2018-08-03 13:00 | 87.22 | 87.21
2018-08-03 13:30 | 97.18 | 97.17
2018-08-03 14:00 | 108.13 | 108.12
2018-08-03 14:30 | 120.6 | 120.57
2018-08-03 15:00 | 114.67 | 114.61
2018-08-03 15:30 | 118.2 | 118.14
2018-08-03 16:00 | 129.15 | 129.08
2018-08-03 16:30 | 125.96 | 125.84
2018-08-03 17:00 | 122.61 | 122.52
2018-08-03 17:30 | 142.74 | 142.73
2018-08-03 18:00 | 183.1 | 178.41
2018-08-03 18:30 | 186.7 | 182.63
2018-08-03 19:00 | 159.22 | 156.64
2018-08-03 19:30 | 184.38 | 182.44
2018-08-03 20:00 | 191.73 | 190
2018-08-03 20:30 | 203.83 | 202.97
2018-08-03 21:00 | 178.83 | 178.5
2018-08-03 21:30 | 168.83 | 168.31
2018-08-03 22:00 | 167.97 | 167.28
2018-08-03 22:30 | 171.57 | 170.72
2018-08-03 23:00 | 177.37 | 176.39
2018-08-03 23:30 | 142.41 | 140.96
2018-08-04 | 87.68 | 85.48
2018-08-04 00:30 | 106.02 | 104.51
2018-08-04 01:00 | 87.76 | 85.81
2018-08-04 01:30 | 87.05 | 83.21
2018-08-04 02:00 | 99.9 | 96.31
2018-08-04 02:30 | 96.06 | 92.18
2018-08-04 03:00 | 94.2 | 90.48
2018-08-04 03:30 | 99.54 | 96.05
2018-08-04 04:00 | 99.14 | 95.38
2018-08-04 04:30 | 99.14 | 95.48
2018-08-04 05:00 | 113.64 | 108.7
2018-08-04 05:30 | 122.27 | 117.61
2018-08-04 06:00 | 116.67 | 111.64
2018-08-04 06:30 | 119.26 | 113.92
2018-08-04 07:00 | 138.69 | 134.15
2018-08-04 07:30 | 156.63 | 153.02
2018-08-04 08:00 | 152.06 | 149.05
2018-08-04 08:30 | 134.34 | 131.17
2018-08-04 09:00 | 116.94 | 113.56
2018-08-04 09:30 | 109.81 | 106.8
2018-08-04 10:00 | 99.45 | 95.93
2018-08-04 10:30 | 77.91 | 72.82
2018-08-04 11:00 | 68.61 | 62.78
2018-08-04 11:30 | 58.34 | 51.16
2018-08-04 12:00 | 51.1 | 42.65
2018-08-04 12:30 | 91.19 | 87.28
2018-08-04 13:00 | 100.51 | 96.83
2018-08-04 13:30 | 39.78 | 27.82
2018-08-04 14:00 | 71.88 | 67.23
2018-08-04 14:30 | 67.97 | 62.28
2018-08-04 15:00 | 101.04 | 96.96
2018-08-04 15:30 | 107.93 | 103.62
2018-08-04 16:00 | 128.86 | 125.62
2018-08-04 16:30 | 149.41 | 146.89
2018-08-04 17:00 | 168.03 | 167.67
2018-08-04 17:30 | 184.93 | 184.81
2018-08-04 18:00 | 173.48 | 173.46
2018-08-04 18:30 | 151.24 | 151.2
2018-08-04 19:00 | 153.12 | 153.05
2018-08-04 19:30 | 156.64 | 156.5
2018-08-04 20:00 | 160.55 | 160.35
2018-08-04 20:30 | 162.6 | 162.32
2018-08-04 21:00 | 159.14 | 158.83
2018-08-04 21:30 | 166.12 | 165.69
2018-08-04 22:00 | 159.4 | 158.74
2018-08-04 22:30 | 154.8 | 153.98
2018-08-04 23:00 | 140.78 | 139.69
2018-08-04 23:30 | 131.03 | 129.63
2018-08-05 | 103.28 | 101.01
2018-08-05 00:30 | 97.55 | 95.33
2018-08-05 01:00 | 86.07 | 80.57
2018-08-05 01:30 | 94.13 | 89.74
2018-08-05 02:00 | 92.44 | 88.27
2018-08-05 02:30 | 104.08 | 100.76
2018-08-05 03:00 | 92.91 | 91.48
2018-08-05 03:30 | 75.05 | 75.05
2018-08-05 04:00 | 71.11 | 71.08
2018-08-05 04:30 | 72.4 | 72.39
2018-08-05 05:00 | 74.07 | 74.07
2018-08-05 05:30 | 80.37 | 79.93
2018-08-05 06:00 | 84.61 | 84.52
2018-08-05 06:30 | 100.12 | 99.83
2018-08-05 07:00 | 111.61 | 111.54
2018-08-05 07:30 | 126.93 | 125.93
2018-08-05 08:00 | 100.89 | 100
2018-08-05 08:30 | 114.92 | 114.05
2018-08-05 09:00 | 102.18 | 99.36
2018-08-05 09:30 | 94.58 | 89.95
2018-08-05 10:00 | 118.49 | 115.03
2018-08-05 10:30 | 68.21 | 61.14
2018-08-05 11:00 | 103.49 | 98.6
2018-08-05 11:30 | 99.88 | 94.72
2018-08-05 12:00 | 69.9 | 61.87
2018-08-05 12:30 | 65.89 | 58.7
2018-08-05 13:00 | 90.06 | 86.06
2018-08-05 13:30 | 79.04 | 72.09
2018-08-05 14:00 | 96.48 | 91.24
2018-08-05 14:30 | 78.91 | 72.22
2018-08-05 15:00 | 89.69 | 85.19
2018-08-05 15:30 | 118.49 | 116.68
2018-08-05 16:00 | 131.77 | 129.47
2018-08-05 16:30 | 137.6 | 134.09
2018-08-05 17:00 | 156.84 | 154.01
2018-08-05 17:30 | 191.94 | 190.24
2018-08-05 18:00 | 201.6 | 200.29
2018-08-05 18:30 | 214.57 | 212.36
2018-08-05 19:00 | 207.56 | 205.6
2018-08-05 19:30 | 204.54 | 203.83
2018-08-05 20:00 | 195.03 | 195
2018-08-05 20:30 | 184.68 | 184.56
2018-08-05 21:00 | 163.04 | 160.54
2018-08-05 21:30 | 160.17 | 157.37
2018-08-05 22:00 | 155.21 | 152.12
2018-08-05 22:30 | 165.62 | 162.74
2018-08-05 23:00 | 167.75 | 164.76
2018-08-05 23:30 | 143.68 | 140.24
2018-08-06 | 103.97 | 99.16
2018-08-06 00:30 | 100.2 | 96.15
2018-08-06 01:00 | 89.65 | 85.98
2018-08-06 01:30 | 80.22 | 76.42
2018-08-06 02:00 | 87.94 | 84.17
2018-08-06 02:30 | 87.16 | 83.17
2018-08-06 03:00 | 92.38 | 88.57
2018-08-06 03:30 | 72.2 | 67.52
2018-08-06 04:00 | 99.24 | 95.42
2018-08-06 04:30 | 92.2 | 89.24
2018-08-06 05:00 | 116.4 | 111.87
2018-08-06 05:30 | 132.99 | 128.64
2018-08-06 06:00 | 146.8 | 142.91
2018-08-06 06:30 | 161.28 | 158.82
2018-08-06 07:00 | 179.92 | 177.87
2018-08-06 07:30 | 189.88 | 189.31
2018-08-06 08:00 | 159.15 | 158.66
2018-08-06 08:30 | 113.46 | 112.64
2018-08-06 09:00 | 78.27 | 77.86
2018-08-06 09:30 | 51.77 | 51.57
2018-08-06 10:00 | 30.26 | 29.68
2018-08-06 10:30 | 24.59 | 24.29
2018-08-06 11:00 | 28.14 | 27.33
2018-08-06 11:30 | 17.48 | 15.47
2018-08-06 12:00 | 30.46 | 29.3
2018-08-06 12:30 | 24.71 | 23.17
2018-08-06 13:00 | 38.2 | 38.2
2018-08-06 13:30 | 77.93 | 77.91
2018-08-06 14:00 | 94.99 | 94.97
2018-08-06 14:30 | 101.64 | 101.63
2018-08-06 15:00 | 119.4 | 119.39
2018-08-06 15:30 | 138.1 | 138.1
2018-08-06 16:00 | 158.41 | 158.41
2018-08-06 16:30 | 141.87 | 141.87
2018-08-06 17:00 | 146.03 | 146.02
2018-08-06 17:30 | 147.97 | 147.96
2018-08-06 18:00 | 135.12 | 135.06
2018-08-06 18:30 | 93.25 | 93.24
2018-08-06 19:00 | 90.36 | 90.36
2018-08-06 19:30 | 116.32 | 116.15
2018-08-06 20:00 | 105.74 | 105.53
2018-08-06 20:30 | 98.18 | 97.83
2018-08-06 21:00 | 94.85 | 94.41
2018-08-06 21:30 | 114.92 | 114.25
2018-08-06 22:00 | 102.2 | 100.9
2018-08-06 22:30 | 95.53 | 93.67
2018-08-06 23:00 | 106.72 | 104.79
2018-08-06 23:30 | 73.06 | 69.68
2018-08-07 | 43.41 | 37.44
2018-08-07 00:30 | 59.83 | 54.4
2018-08-07 01:00 | 53.21 | 44.58
2018-08-07 01:30 | 53.26 | 45.38
2018-08-07 02:00 | 62.22 | 55.75
2018-08-07 02:30 | 79.98 | 75.13
2018-08-07 03:00 | 97.29 | 94.14
2018-08-07 03:30 | 104.2 | 100.33
2018-08-07 04:00 | 83.12 | 78.63
2018-08-07 04:30 | 100.11 | 95.86
2018-08-07 05:00 | 116.59 | 111.87
2018-08-07 05:30 | 108.94 | 103.14
2018-08-07 06:00 | 132.55 | 128.39
2018-08-07 06:30 | 157.66 | 156.24
2018-08-07 07:00 | 150.78 | 150.25
2018-08-07 07:30 | 137.31 | 137.06
2018-08-07 08:00 | 128.58 | 128.47
2018-08-07 08:30 | 108.16 | 108.04
2018-08-07 09:00 | 108.69 | 108.57
2018-08-07 09:30 | 70.1 | 69.85
2018-08-07 10:00 | 73.53 | 73.34
2018-08-07 10:30 | 73.41 | 73.29
2018-08-07 11:00 | 77.76 | 77.64
2018-08-07 11:30 | 87.37 | 87.32
2018-08-07 12:00 | 102.3 | 102.26
2018-08-07 12:30 | 105.54 | 105.52
2018-08-07 13:00 | 124.34 | 124.31
2018-08-07 13:30 | 136.69 | 136.67
2018-08-07 14:00 | 143.56 | 143.53
2018-08-07 14:30 | 147 | 146.98
2018-08-07 15:00 | 147.83 | 147.8
2018-08-07 15:30 | 156.92 | 156.87
2018-08-07 16:00 | 170.34 | 170.29
2018-08-07 16:30 | 152.57 | 152.44
2018-08-07 17:00 | 145.7 | 145.6
2018-08-07 17:30 | 129.87 | 129.85
2018-08-07 18:00 | 129.48 | 129.37
2018-08-07 18:30 | 138.25 | 137.71
2018-08-07 19:00 | 139.12 | 138.56
2018-08-07 19:30 | 144.46 | 143.78
2018-08-07 20:00 | 120.21 | 119.21
2018-08-07 20:30 | 122.83 | 122.42
2018-08-07 21:00 | 123.75 | 123.51
2018-08-07 21:30 | 113.9 | 113.37
2018-08-07 22:00 | 107.14 | 106.25
2018-08-07 22:30 | 114.34 | 113.27
2018-08-07 23:00 | 116.3 | 114.87
2018-08-07 23:30 | 51.58 | 47.64
2018-08-08 | 26.57 | 18.49
2018-08-08 00:30 | 34.05 | 28.11
2018-08-08 01:00 | 35.81 | 30.68
2018-08-08 01:30 | 50.61 | 46.44
2018-08-08 02:00 | 58.59 | 55.18
2018-08-08 02:30 | 89.08 | 86.67
2018-08-08 03:00 | 87.88 | 84.9
2018-08-08 03:30 | 90.26 | 85.88
2018-08-08 04:00 | 92.19 | 87.52
2018-08-08 04:30 | 90.22 | 87.77
2018-08-08 05:00 | 97.35 | 94.94
2018-08-08 05:30 | 118.44 | 113.94
2018-08-08 06:00 | 131.65 | 129.87
2018-08-08 06:30 | 140.8 | 140.68
2018-08-08 07:00 | 140.64 | 140.52
2018-08-08 07:30 | 158.5 | 150.5
2018-08-08 08:00 | 134.13 | 116.87
2018-08-08 08:30 | 109.68 | 87.22
2018-08-08 09:00 | 82.72 | 64.59
2018-08-08 09:30 | 61.73 | 41.96
2018-08-08 10:00 | 43.55 | 23.72
2018-08-08 10:30 | 27.89 | 24.4
2018-08-08 11:00 | 29.01 | 25.18
2018-08-08 11:30 | 25.21 | 21.06
2018-08-08 12:00 | 20.8 | 15.79
2018-08-08 12:30 | 45.83 | 43.81
2018-08-08 13:00 | 33.87 | 31.36
2018-08-08 13:30 | 49.41 | 47.78
2018-08-08 14:00 | 83.78 | 82.79
2018-08-08 14:30 | 74.82 | 73.83
2018-08-08 15:00 | 95.16 | 94.47
2018-08-08 15:30 | 102.03 | 101.38
2018-08-08 16:00 | 97.71 | 97.17
2018-08-08 16:30 | 82.67 | 82.1
2018-08-08 17:00 | 98.33 | 92.27
2018-08-08 17:30 | 113.02 | 104.95
2018-08-08 18:00 | 107.38 | 95.29
2018-08-08 18:30 | 92.82 | 77.68
2018-08-08 19:00 | 103.51 | 90.63
2018-08-08 19:30 | 122.52 | 112.57
2018-08-08 20:00 | 124.71 | 115.32
2018-08-08 20:30 | 110.59 | 100.91
2018-08-08 21:00 | 93.41 | 88.09
2018-08-08 21:30 | 99.75 | 95.44
2018-08-08 22:00 | 85.86 | 82.08
2018-08-08 22:30 | 96.75 | 94.17
2018-08-08 23:00 | 99.96 | 98.16
2018-08-08 23:30 | 56.9 | 53.83
2018-08-09 | 26.7 | 20.31
2018-08-09 00:30 | 19.9 | 19.85
2018-08-09 01:00 | 27.16 | 26.99
2018-08-09 01:30 | 45.33 | 40.15
2018-08-09 02:00 | 66.13 | 62.37
2018-08-09 02:30 | 78.31 | 75.28
2018-08-09 03:00 | 96.62 | 94.19
2018-08-09 03:30 | 91.07 | 87.77
2018-08-09 04:00 | 90.11 | 86.65
2018-08-09 04:30 | 99.03 | 95.7
2018-08-09 05:00 | 107.96 | 104.97
2018-08-09 05:30 | 125.86 | 123.5
2018-08-09 06:00 | 130.73 | 129.36
2018-08-09 06:30 | 129.99 | 129.83
2018-08-09 07:00 | 135.28 | 134.41
2018-08-09 07:30 | 110.44 | 99.99
2018-08-09 08:00 | 79.44 | 62.63
2018-08-09 08:30 | 80.31 | 63.52
2018-08-09 09:00 | 67.2 | 47.76
2018-08-09 09:30 | 41.93 | 26.91
2018-08-09 10:00 | 22.18 | 16.07
2018-08-09 10:30 | 15.2 | 2.28
2018-08-09 11:00 | 14.83 | 2.13
2018-08-09 11:30 | 31.73 | 28.14
2018-08-09 12:00 | 71.66 | 70.26
2018-08-09 12:30 | 87.7 | 86.79
2018-08-09 13:00 | 114.66 | 113.76
2018-08-09 13:30 | 41.97 | 39.94
2018-08-09 14:00 | 106.09 | 105.25
2018-08-09 14:30 | 48.18 | 46.46
2018-08-09 15:00 | 44.2 | 42.74
2018-08-09 15:30 | 49.72 | 48.58
2018-08-09 16:00 | 60.62 | 59.72
2018-08-09 16:30 | 71.79 | 71.04
2018-08-09 17:00 | 80.7 | 76.43
2018-08-09 17:30 | 86.28 | 73.97
2018-08-09 18:00 | 92.93 | 77.34
2018-08-09 18:30 | 93.31 | 76.69
2018-08-09 19:00 | 102.72 | 88.54
2018-08-09 19:30 | 95.45 | 81.82
2018-08-09 20:00 | 86.55 | 71.9
2018-08-09 20:30 | 92.94 | 81.43
2018-08-09 21:00 | 83.46 | 72.61
2018-08-09 21:30 | 97.53 | 90.1
2018-08-09 22:00 | 76.01 | 75.31
2018-08-09 22:30 | 70.05 | 70.05
2018-08-09 23:00 | 85.41 | 85.39
2018-08-09 23:30 | 95.55 | 95.47
2018-08-10 | 40.08 | 39.96
2018-08-10 00:30 | 30.06 | 29.88
2018-08-10 01:00 | 23.29 | 23.13
2018-08-10 01:30 | 16.42 | 16.25
2018-08-10 02:00 | 14.72 | 14.42
2018-08-10 02:30 | 25.63 | 11.83
2018-08-10 03:00 | 24.92 | 9.6
2018-08-10 03:30 | 24.22 | 9.47
2018-08-10 04:00 | 24.08 | 9.72
2018-08-10 04:30 | 25.48 | 11.85
2018-08-10 05:00 | 28.72 | 17.07
2018-08-10 05:30 | 36.35 | 27.94
2018-08-10 06:00 | 127.43 | 125.47
2018-08-10 06:30 | 126.91 | 125.83
2018-08-10 07:00 | 77.58 | 77.11
2018-08-10 07:30 | 91.14 | 89.69
2018-08-10 08:00 | 96 | 94.3
2018-08-10 08:30 | 82.66 | 80.73
2018-08-10 09:00 | 83.03 | 81.37
2018-08-10 09:30 | 68.69 | 66.95
2018-08-10 10:00 | 48.75 | 46.08
2018-08-10 10:30 | 55.37 | 53.05
2018-08-10 11:00 | 58.7 | 55.5
2018-08-10 11:30 | 75.23 | 73.01
2018-08-10 12:00 | 76.63 | 74.49
2018-08-10 12:30 | 72.23 | 70.43
2018-08-10 13:00 | 64.22 | 62.59
2018-08-10 13:30 | 70.85 | 69.55
2018-08-10 14:00 | 83 | 81.84
2018-08-10 14:30 | 87.83 | 86.85
2018-08-10 15:00 | 96.92 | 96.01
2018-08-10 15:30 | 102.27 | 101.65
2018-08-10 16:00 | 124.1 | 123.65
2018-08-10 16:30 | 106.99 | 106.58
2018-08-10 17:00 | 118.82 | 118.46
2018-08-10 17:30 | 122.95 | 122.65
2018-08-10 18:00 | 123.77 | 123.7
2018-08-10 18:30 | 138.01 | 137.95
2018-08-10 19:00 | 145.6 | 145.54
2018-08-10 19:30 | 140.85 | 140.72
2018-08-10 20:00 | 134.32 | 133.89
2018-08-10 20:30 | 132.26 | 131.91
2018-08-10 21:00 | 126.76 | 126.54
2018-08-10 21:30 | 125.41 | 125.31
2018-08-10 22:00 | 111.22 | 111.19
2018-08-10 22:30 | 130.19 | 130.17
2018-08-10 23:00 | 131.14 | 131.14
2018-08-10 23:30 | 89.95 | 89.95
2018-08-11 | 51.52 | 51.47
2018-08-11 00:30 | 51.95 | 51.91
2018-08-11 01:00 | 59.67 | 59.66
2018-08-11 01:30 | 64.13 | 64.12
2018-08-11 02:00 | 70.33 | 68.45
2018-08-11 02:30 | 70.28 | 66.67
2018-08-11 03:00 | 69.36 | 65.6
2018-08-11 03:30 | 62.65 | 58.46
2018-08-11 04:00 | 67.95 | 64.27
2018-08-11 04:30 | 68.08 | 63.99
2018-08-11 05:00 | 79.53 | 76.09
2018-08-11 05:30 | 87.11 | 83.73
2018-08-11 06:00 | 94.82 | 91.67
2018-08-11 06:30 | 102.39 | 99.27
2018-08-11 07:00 | 109.7 | 106.71
2018-08-11 07:30 | 101.61 | 99.07
2018-08-11 08:00 | 80.05 | 78.1
2018-08-11 08:30 | 81.23 | 79.72
2018-08-11 09:00 | 69.85 | 68.55
2018-08-11 09:30 | 59.72 | 59.7
2018-08-11 10:00 | 56.99 | 56.29
2018-08-11 10:30 | 48.62 | 47.85
2018-08-11 11:00 | 45.82 | 45.09
2018-08-11 11:30 | 13.27 | 11.73
2018-08-11 12:00 | 7.74 | 4.9
2018-08-11 12:30 | 18.81 | 18.1
2018-08-11 13:00 | 13.39 | 12.77
2018-08-11 13:30 | 31.61 | 31.35
2018-08-11 14:00 | 22.71 | 22.58
2018-08-11 14:30 | 33.51 | 33.37
2018-08-11 15:00 | 34.45 | 34.34
2018-08-11 15:30 | 55.1 | 55.05
2018-08-11 16:00 | 73.85 | 73.83
2018-08-11 16:30 | 84 | 83.98
2018-08-11 17:00 | 95.49 | 95.44
2018-08-11 17:30 | 114.44 | 114.32
2018-08-11 18:00 | 146.73 | 146.48
2018-08-11 18:30 | 165.36 | 165.14
2018-08-11 19:00 | 170.46 | 170.3
2018-08-11 19:30 | 161.32 | 161.19
2018-08-11 20:00 | 174.23 | 174.12
2018-08-11 20:30 | 161.12 | 161.05
2018-08-11 21:00 | 131.71 | 131.67
2018-08-11 21:30 | 111.98 | 111.98
2018-08-11 22:00 | 90.83 | 90.82
2018-08-11 22:30 | 112.23 | 112.21
2018-08-11 23:00 | 119.01 | 118.97
2018-08-11 23:30 | 81.49 | 81.37
2018-08-12 | 57.85 | 57.6
2018-08-12 00:30 | 89 | 88
2018-08-12 01:00 | 70.87 | 66.06
2018-08-12 01:30 | 41.75 | 33.43
2018-08-12 02:00 | 36.42 | 26.54
2018-08-12 02:30 | 36.51 | 26.9
2018-08-12 03:00 | 36.47 | 27.63
2018-08-12 03:30 | 36.91 | 27.69
2018-08-12 04:00 | 34.85 | 25.17
2018-08-12 04:30 | 34.65 | 24.25
2018-08-12 05:00 | 41.72 | 33.85
2018-08-12 05:30 | 46.25 | 38.68
2018-08-12 06:00 | 46.04 | 38.82
2018-08-12 06:30 | 56.55 | 50.81
2018-08-12 07:00 | 56.57 | 51.08
2018-08-12 07:30 | 54.1 | 48.37
2018-08-12 08:00 | 37.04 | 30.23
2018-08-12 08:30 | 32.21 | 25.6
2018-08-12 09:00 | 24.84 | 16.58
2018-08-12 09:30 | 16.86 | 0.82
2018-08-12 10:00 | 16.36 | -5.31
2018-08-12 10:30 | 23.61 | -19.29
2018-08-12 11:00 | 66.7 | -66.26
2018-08-12 11:30 | 74.19 | -73.92
2018-08-12 12:00 | 75.17 | -74.86
2018-08-12 12:30 | 73.71 | -73.36
2018-08-12 13:00 | 64.18 | -63.74
2018-08-12 13:30 | 27.72 | -25.34
2018-08-12 14:00 | 17.19 | 8.41
2018-08-12 14:30 | 16.64 | 2.72
2018-08-12 15:00 | 25.74 | 18.82
2018-08-12 15:30 | 53.07 | 49.77
2018-08-12 16:00 | 102.9 | 101.06
2018-08-12 16:30 | 113.78 | 112.19
2018-08-12 17:00 | 107.54 | 106.06
2018-08-12 17:30 | 101.28 | 99.9
2018-08-12 18:00 | 125.99 | 125.97
2018-08-12 18:30 | 151.55 | 151.34
2018-08-12 19:00 | 150.38 | 150.13
2018-08-12 19:30 | 137.26 | 136.83
2018-08-12 20:00 | 139.57 | 139.02
2018-08-12 20:30 | 136.34 | 135.65
2018-08-12 21:00 | 116.44 | 115.46
2018-08-12 21:30 | 108.31 | 106.89
2018-08-12 22:00 | 104.7 | 102.83
2018-08-12 22:30 | 115.78 | 113.88
2018-08-12 23:00 | 128.21 | 126.21
2018-08-12 23:30 | 108.38 | 105.79
2018-08-13 | 80.78 | 77.07
2018-08-13 00:30 | 73.99 | 69.94
2018-08-13 01:00 | 89.24 | 87.73
2018-08-13 01:30 | 81.69 | 78.38
2018-08-13 02:00 | 70.75 | 65.58
2018-08-13 02:30 | 31.44 | 21.63
2018-08-13 03:00 | 40.26 | 34.08
2018-08-13 03:30 | 42.81 | 35.75
2018-08-13 04:00 | 44.36 | 37.14
2018-08-13 04:30 | 49.19 | 41.73
2018-08-13 05:00 | 86.16 | 81.55
2018-08-13 05:30 | 107.22 | 102.55
2018-08-13 06:00 | 130.21 | 126.19
2018-08-13 06:30 | 141.6 | 139.05
2018-08-13 07:00 | 126.58 | 126.22
2018-08-13 07:30 | 124.64 | 124.58
2018-08-13 08:00 | 78.93 | 78.48
2018-08-13 08:30 | 34.04 | 32.49
2018-08-13 09:00 | 21.82 | 19.73
2018-08-13 09:30 | 8.5 | 1.68
2018-08-13 10:00 | 16.2 | -13.66
2018-08-13 10:30 | 8.8 | -8.65
2018-08-13 11:00 | 12.06 | -11.43
2018-08-13 11:30 | 13.12 | -12.43
2018-08-13 12:00 | 11.62 | -10.6
2018-08-13 12:30 | 15.41 | -14.89
2018-08-13 13:00 | 7.15 | -3.12
2018-08-13 13:30 | 8.92 | 1.63
2018-08-13 14:00 | 13.7 | 10.57
2018-08-13 14:30 | 22.7 | 21.02
2018-08-13 15:00 | 10.77 | 7.42
2018-08-13 15:30 | 23.77 | 22.01
2018-08-13 16:00 | 40.47 | 38.96
2018-08-13 16:30 | 29.77 | 29.53
2018-08-13 17:00 | 42.97 | 42.87
2018-08-13 17:30 | 83.53 | 83.42
2018-08-13 18:00 | 124.74 | 123.32
2018-08-13 18:30 | 116.3 | 112.94
2018-08-13 19:00 | 107.05 | 103.92
2018-08-13 19:30 | 138.81 | 137.07
2018-08-13 20:00 | 143.09 | 141.57
2018-08-13 20:30 | 125.85 | 125.58
2018-08-13 21:00 | 91.98 | 91.52
2018-08-13 21:30 | 63.95 | 59.37
2018-08-13 22:00 | 49.18 | 25.29
2018-08-13 22:30 | 61.82 | 56.55
2018-08-13 23:00 | 66.56 | 66.54
2018-08-13 23:30 | 34.16 | 32.43
2018-08-14 | 36.62 | -36.05
2018-08-14 00:30 | 11.06 | -1.09
2018-08-14 01:00 | 17.71 | -14.92
2018-08-14 01:30 | 31.27 | -30.26
2018-08-14 02:00 | 35.8 | -35.04
2018-08-14 02:30 | 53.65 | 51.87
2018-08-14 03:00 | 34.61 | 32.02
2018-08-14 03:30 | 17.07 | 10.47
2018-08-14 04:00 | 19.02 | 12.01
2018-08-14 04:30 | 22.89 | 16.36
2018-08-14 05:00 | 24.29 | 19.48
2018-08-14 05:30 | 32.95 | 30.31
2018-08-14 06:00 | 100.34 | 99.7
2018-08-14 06:30 | 107.67 | 107.52
2018-08-14 07:00 | 110.3 | 109.68
2018-08-14 07:30 | 125.08 | 118.27
2018-08-14 08:00 | 133.37 | 108.26
2018-08-14 08:30 | 96.12 | 70.58
2018-08-14 09:00 | 75.45 | 51.5
2018-08-14 09:30 | 77.69 | 54.46
2018-08-14 10:00 | 60.82 | 24.84
2018-08-14 10:30 | 61.97 | 51.82
2018-08-14 11:00 | 127.3 | 127.21
2018-08-14 11:30 | 17.85 | 17.55
2018-08-14 12:00 | 7.7 | 6.9
2018-08-14 12:30 | 5.12 | 4.33
2018-08-14 13:00 | 5.19 | 3.99
2018-08-14 13:30 | 4.79 | 2.63
2018-08-14 14:00 | 5 | 2.73
2018-08-14 14:30 | 10.48 | 9.45
2018-08-14 15:00 | 14.27 | 13.71
2018-08-14 15:30 | 19.92 | 19.1
2018-08-14 16:00 | 35.8 | 28.91
2018-08-14 16:30 | 46.07 | 41.36
2018-08-14 17:00 | 86.83 | 70.61
2018-08-14 17:30 | 92.26 | 77.8
2018-08-14 18:00 | 95.68 | 89.02
2018-08-14 18:30 | 117.96 | 117.12
2018-08-14 19:00 | 124.46 | 123.86
2018-08-14 19:30 | 121.12 | 120.71
2018-08-14 20:00 | 124.05 | 123.57
2018-08-14 20:30 | 118.13 | 117.34
2018-08-14 21:00 | 102.81 | 102.27
2018-08-14 21:30 | 112.42 | 111.68
2018-08-14 22:00 | 89.57 | 88.81
2018-08-14 22:30 | 92.06 | 91.66
2018-08-14 23:00 | 106.63 | 106.39
2018-08-14 23:30 | 86.55 | 86.37
2018-08-15 | 36.01 | 35.73
2018-08-15 00:30 | 36.26 | 35.79
2018-08-15 01:00 | 52.69 | 50.8
2018-08-15 01:30 | 71.53 | 70.49
2018-08-15 02:00 | 81.88 | 80.53
2018-08-15 02:30 | 35.67 | 31
2018-08-15 03:00 | 34.79 | 29.65
2018-08-15 03:30 | 34.81 | 29.76
2018-08-15 04:00 | 36.62 | 31.31
2018-08-15 04:30 | 40.13 | 35.16
2018-08-15 05:00 | 45.29 | 40.56
2018-08-15 05:30 | 88.34 | 85.41
2018-08-15 06:00 | 122.43 | 120.59
2018-08-15 06:30 | 109.12 | 108.7
2018-08-15 07:00 | 103.27 | 103.18
2018-08-15 07:30 | 113.94 | 100.57
2018-08-15 08:00 | 106.71 | 93.44
2018-08-15 08:30 | 83.86 | 76.75
2018-08-15 09:00 | 77.14 | 69.82
2018-08-15 09:30 | 57.52 | 47.12
2018-08-15 10:00 | 40.35 | 23.71
2018-08-15 10:30 | 22.78 | 18.32
2018-08-15 11:00 | 23.17 | 20.35
2018-08-15 11:30 | 21.14 | 17.22
2018-08-15 12:00 | 42.22 | 40.12
2018-08-15 12:30 | 88.52 | 87.48
2018-08-15 13:00 | 88.53 | 87.36
2018-08-15 13:30 | 80.2 | 78.9
2018-08-15 14:00 | 105.49 | 104.93
2018-08-15 14:30 | 122.8 | 122.5
2018-08-15 15:00 | 116.73 | 116.28
2018-08-15 15:30 | 62.37 | 61.32
2018-08-15 16:00 | 65.57 | 65.57
2018-08-15 16:30 | 77.12 | 77.12
2018-08-15 17:00 | 88.8 | 88.79
2018-08-15 17:30 | 93.44 | 93.4
2018-08-15 18:00 | 110.09 | 110.06
2018-08-15 18:30 | 126.62 | 125.23
2018-08-15 19:00 | 132.48 | 131.26
2018-08-15 19:30 | 116.02 | 114.6
2018-08-15 20:00 | 122.63 | 118.18
2018-08-15 20:30 | 125.54 | 121.76
2018-08-15 21:00 | 117.66 | 114.28
2018-08-15 21:30 | 94.57 | 91.42
2018-08-15 22:00 | 93.47 | 93.47
2018-08-15 22:30 | 76.66 | 74.42
2018-08-15 23:00 | 72.58 | 70.37
2018-08-15 23:30 | 36.95 | 33.62
2018-08-16 | 15.04 | 5.8
2018-08-16 00:30 | 35.83 | 33.14
2018-08-16 01:00 | 38.57 | 36.11
2018-08-16 01:30 | 41.05 | 39.05
2018-08-16 02:00 | 47 | 44.83
2018-08-16 02:30 | 58.51 | 57.32
2018-08-16 03:00 | 80.1 | 79.71
2018-08-16 03:30 | 72.21 | 71.27
2018-08-16 04:00 | 56.24 | 52.25
2018-08-16 04:30 | 60.59 | 56.33
2018-08-16 05:00 | 81.7 | 77.96
2018-08-16 05:30 | 97.95 | 95
2018-08-16 06:00 | 94.92 | 93.67
2018-08-16 06:30 | 91.76 | 91.08
2018-08-16 07:00 | 119.1 | 119.08
2018-08-16 07:30 | 121.63 | 114.3
2018-08-16 08:00 | 89.33 | 68.92
2018-08-16 08:30 | 63.56 | 25.83
2018-08-16 09:00 | 60.06 | 16.04
2018-08-16 09:30 | 56.88 | -0.51
2018-08-16 10:00 | 56.54 | -6.65
2018-08-16 10:30 | 41.18 | 12.83
2018-08-16 11:00 | 30.12 | 13.31
2018-08-16 11:30 | 8.25 | 6.35
2018-08-16 12:00 | 11.65 | -6.63
2018-08-16 12:30 | 24.81 | 3.42
2018-08-16 13:00 | 28.03 | 13.04
2018-08-16 13:30 | 26.6 | 7.73
2018-08-16 14:00 | 31.52 | 18.96
2018-08-16 14:30 | 41.81 | 33.49
2018-08-16 15:00 | 51.3 | 45.21
2018-08-16 15:30 | 75.53 | 71.92
2018-08-16 16:00 | 81.22 | 78.34
2018-08-16 16:30 | 78.3 | 68.1
2018-08-16 17:00 | 55.9 | 44.47
2018-08-16 17:30 | 67.01 | 57.66
2018-08-16 18:00 | 68.93 | 54.43
2018-08-16 18:30 | 63.67 | 45.39
2018-08-16 19:00 | 86.37 | 75.4
2018-08-16 19:30 | 76.06 | 65.16
2018-08-16 20:00 | 43.18 | 16.83
2018-08-16 20:30 | 43.37 | 21.63
2018-08-16 21:00 | 37.56 | 15.62
2018-08-16 21:30 | 21.04 | 18.84
2018-08-16 22:00 | 16.37 | 16.3
2018-08-16 22:30 | 34.85 | 33.45
2018-08-16 23:00 | 55.45 | 53.21
2018-08-16 23:30 | 38.35 | 35.76
2018-08-17 | 10.71 | 2.27
2018-08-17 00:30 | 15.35 | 12.12
2018-08-17 01:00 | 17.03 | 13.8
2018-08-17 01:30 | 11.14 | 7.99
2018-08-17 02:00 | 17.24 | 13.75
2018-08-17 02:30 | 24.48 | 20.28
2018-08-17 03:00 | 19.41 | 17.2
2018-08-17 03:30 | 30.73 | 30.62
2018-08-17 04:00 | 29.92 | 29.83
2018-08-17 04:30 | 38.47 | 38.47
2018-08-17 05:00 | 58.9 | 58.89
2018-08-17 05:30 | 79.08 | 78.92
2018-08-17 06:00 | 80.98 | 80.76
2018-08-17 06:30 | 93.52 | 93.19
2018-08-17 07:00 | 104.16 | 103.88
2018-08-17 07:30 | 86.94 | 82.82
2018-08-17 08:00 | 68.26 | 61.04
2018-08-17 08:30 | 47.25 | 34.56
2018-08-17 09:00 | 36.83 | 14.36
2018-08-17 09:30 | 33.37 | 7.79
2018-08-17 10:00 | 26.31 | 8.67
2018-08-17 10:30 | 31.18 | 22.17
2018-08-17 11:00 | 30.29 | 19.82
2018-08-17 11:30 | 49.39 | 44.44
2018-08-17 12:00 | 73.18 | 70.01
2018-08-17 12:30 | 77.01 | 74.37
2018-08-17 13:00 | 75.68 | 73.01
2018-08-17 13:30 | 88.49 | 86.15
2018-08-17 14:00 | 103.36 | 101.37
2018-08-17 14:30 | 114.6 | 112.64
2018-08-17 15:00 | 123.16 | 121.1
2018-08-17 15:30 | 139.55 | 137.8
2018-08-17 16:00 | 139.28 | 138.17
2018-08-17 16:30 | 130.24 | 129.32
2018-08-17 17:00 | 126.55 | 125.65
2018-08-17 17:30 | 95.25 | 93.81
2018-08-17 18:00 | 81.44 | 74.4
2018-08-17 18:30 | 102.71 | 73.76
2018-08-17 19:00 | 94.42 | 68.17
2018-08-17 19:30 | 81.48 | 64.93
2018-08-17 20:00 | 75.05 | 57.5
2018-08-17 20:30 | 50.48 | 12.36
2018-08-17 21:00 | 37.16 | 5.38
2018-08-17 21:30 | 20.27 | 13.96
2018-08-17 22:00 | 13.26 | 4.59
2018-08-17 22:30 | 11.5 | -0.63
2018-08-17 23:00 | 27.14 | 25.45
2018-08-17 23:30 | 14.22 | 12.09
2018-08-18 | 4.73 | -0.28
2018-08-18 00:30 | 5.58 | -3.9
2018-08-18 01:00 | 10.74 | 10.72
2018-08-18 01:30 | 23.94 | 17.56
2018-08-18 02:00 | 32.91 | 30.1
2018-08-18 02:30 | 77.96 | 76.2
2018-08-18 03:00 | 77.87 | 75.75
2018-08-18 03:30 | 60.96 | 59.17
2018-08-18 04:00 | 48.88 | 46.01
2018-08-18 04:30 | 59.65 | 57.08
2018-08-18 05:00 | 62.28 | 59.73
2018-08-18 05:30 | 65.98 | 63.47
2018-08-18 06:00 | 69.44 | 66.85
2018-08-18 06:30 | 70.49 | 68.03
2018-08-18 07:00 | 93.39 | 91.51
2018-08-18 07:30 | 82.93 | 81.38
2018-08-18 08:00 | 40.75 | 39.45
2018-08-18 08:30 | 27.84 | 26.77
2018-08-18 09:00 | 28.98 | 28.18
2018-08-18 09:30 | 62.03 | 61.68
2018-08-18 10:00 | 108.61 | 108.37
2018-08-18 10:30 | 98.34 | 97.98
2018-08-18 11:00 | 58.04 | 57.53
2018-08-18 11:30 | 63.4 | 63
2018-08-18 12:00 | 89.89 | 89.56
2018-08-18 12:30 | 88.02 | 87.6
2018-08-18 13:00 | 87.44 | 86.98
2018-08-18 13:30 | 88.62 | 88.16
2018-08-18 14:00 | 51.41 | 50.9
2018-08-18 14:30 | 60.26 | 59.89
2018-08-18 15:00 | 84.95 | 84.48
2018-08-18 15:30 | 79.13 | 78.53
2018-08-18 16:00 | 96.13 | 95.68
2018-08-18 16:30 | 99.17 | 98.76
2018-08-18 17:00 | 107.02 | 106.75
2018-08-18 17:30 | 109.13 | 109.03
2018-08-18 18:00 | 112.98 | 111.52
2018-08-18 18:30 | 125.11 | 114.51
2018-08-18 19:00 | 126.18 | 116.3
2018-08-18 19:30 | 110.67 | 100.2
2018-08-18 20:00 | 81.16 | 78.65
2018-08-18 20:30 | 74.57 | 73.43
2018-08-18 21:00 | 65.41 | 64.24
2018-08-18 21:30 | 65.85 | 65.09
2018-08-18 22:00 | 64.35 | 63.88
2018-08-18 22:30 | 69.01 | 68.73
2018-08-18 23:00 | 70.48 | 70.32
2018-08-18 23:30 | 48.96 | 48.82
2018-08-19 | 62.16 | 62.16
2018-08-19 00:30 | 80.81 | 79.88
2018-08-19 01:00 | 75.29 | 73.32
2018-08-19 01:30 | 67.54 | 65.3
2018-08-19 02:00 | 84.04 | 82.12
2018-08-19 02:30 | 87.42 | 85.64
2018-08-19 03:00 | 61.63 | 59.21
2018-08-19 03:30 | 86.11 | 84.25
2018-08-19 04:00 | 85.77 | 83.88
2018-08-19 04:30 | 86.73 | 84.96
2018-08-19 05:00 | 88.36 | 86.5
2018-08-19 05:30 | 92.16 | 90.35
2018-08-19 06:00 | 70.61 | 68.31
2018-08-19 06:30 | 63.45 | 61.48
2018-08-19 07:00 | 70.46 | 68.4
2018-08-19 07:30 | 72.69 | 70.65
2018-08-19 08:00 | 33.39 | 29.84
2018-08-19 08:30 | 31.01 | 27.61
2018-08-19 09:00 | 26.64 | 23.09
2018-08-19 09:30 | 9.64 | -2.39
2018-08-19 10:00 | 12.16 | -8.65
2018-08-19 10:30 | 16.56 | -14.91
2018-08-19 11:00 | 26.06 | -25.38
2018-08-19 11:30 | 37.23 | -36.95
2018-08-19 12:00 | 31.32 | -31.04
2018-08-19 12:30 | 34.69 | -34.45
2018-08-19 13:00 | 32.89 | -32.59
2018-08-19 13:30 | 38.03 | -37.81
2018-08-19 14:00 | 7.53 | -4.64
2018-08-19 14:30 | 43.82 | 43.03
2018-08-19 15:00 | 8.83 | -6.12
2018-08-19 15:30 | 8.83 | -6.31
2018-08-19 16:00 | 15.17 | 12.9
2018-08-19 16:30 | 33.47 | 32.14
2018-08-19 17:00 | 26.47 | 26.08
2018-08-19 17:30 | 43.39 | 40.58
2018-08-19 18:00 | 80.27 | 76.26
2018-08-19 18:30 | 123.64 | 116.43
2018-08-19 19:00 | 126.92 | 118.97
2018-08-19 19:30 | 112.96 | 104.73
2018-08-19 20:00 | 97.7 | 88.73
2018-08-19 20:30 | 82.41 | 72.3
2018-08-19 21:00 | 70.73 | 60.22
2018-08-19 21:30 | 61.65 | 51.48
2018-08-19 22:00 | 52 | 42.18
2018-08-19 22:30 | 51.87 | 43.61
2018-08-19 23:00 | 59.76 | 52.99
2018-08-19 23:30 | 48.72 | 40.61
2018-08-20 | 29.31 | 27.16
2018-08-20 00:30 | 19.23 | 17.9
2018-08-20 01:00 | 13.27 | 10.86
2018-08-20 01:30 | 10.08 | 5.79
2018-08-20 02:00 | 11.08 | 7.11
2018-08-20 02:30 | 13.34 | 10.67
2018-08-20 03:00 | 10.43 | 10.34
2018-08-20 03:30 | 15.72 | 12.75
2018-08-20 04:00 | 17.66 | 14.47
2018-08-20 04:30 | 39.57 | 37.53
2018-08-20 05:00 | 49.89 | 47.71
2018-08-20 05:30 | 66.79 | 64.89
2018-08-20 06:00 | 68.5 | 67.36
2018-08-20 06:30 | 65.7 | 65.7
2018-08-20 07:00 | 85.31 | 85.24
2018-08-20 07:30 | 84.95 | 84.73
2018-08-20 08:00 | 76.68 | 76.48
2018-08-20 08:30 | 68.33 | 68.12
2018-08-20 09:00 | 61.04 | 60.74
2018-08-20 09:30 | 50.59 | 50.35
2018-08-20 10:00 | 42.32 | 42.25
2018-08-20 10:30 | 28.3 | 28.21
2018-08-20 11:00 | 31.61 | 31.05
2018-08-20 11:30 | 32.37 | 32.2
2018-08-20 12:00 | 31.31 | 31.16
2018-08-20 12:30 | 30.88 | 30.68
2018-08-20 13:00 | 31.83 | 31.44
2018-08-20 13:30 | 34.88 | 34.41
2018-08-20 14:00 | 38.81 | 38.32
2018-08-20 14:30 | 42.28 | 41.92
2018-08-20 15:00 | 43.43 | 43.13
2018-08-20 15:30 | 49.04 | 48.67
2018-08-20 16:00 | 53.92 | 53.59
2018-08-20 16:30 | 54.21 | 54.03
2018-08-20 17:00 | 75.39 | 75.32
2018-08-20 17:30 | 90.16 | 89.95
2018-08-20 18:00 | 55.5 | 53.84
2018-08-20 18:30 | 78.87 | 68.45
2018-08-20 19:00 | 103.78 | 99.93
2018-08-20 19:30 | 95.58 | 93
2018-08-20 20:00 | 84.43 | 84.42
2018-08-20 20:30 | 83.28 | 83.22
2018-08-20 21:00 | 65.13 | 64.97
2018-08-20 21:30 | 79.87 | 79.46
2018-08-20 22:00 | 74.8 | 74.29
2018-08-20 22:30 | 96.23 | 95.68
2018-08-20 23:00 | 99.56 | 99.56
2018-08-20 23:30 | 57.61 | 53.99
2018-08-21 | 27.68 | 21.1
2018-08-21 00:30 | 33.3 | 28.43
2018-08-21 01:00 | 52.9 | 50.98
2018-08-21 01:30 | 25.93 | 22.43
2018-08-21 02:00 | 25.67 | 22.23
2018-08-21 02:30 | 51.65 | 49.96
2018-08-21 03:00 | 57.27 | 55.65
2018-08-21 03:30 | 75.16 | 73.72
2018-08-21 04:00 | 80.67 | 79.06
2018-08-21 04:30 | 93.13 | 91.55
2018-08-21 05:00 | 128.32 | 126.95
2018-08-21 05:30 | 110.13 | 107.96
2018-08-21 06:00 | 92.74 | 90.64
2018-08-21 06:30 | 107.53 | 107
2018-08-21 07:00 | 126.34 | 126.22
2018-08-21 07:30 | 113.28 | 113.25
2018-08-21 08:00 | 21.03 | 15.93
2018-08-21 08:30 | 36.19 | 35.8
2018-08-21 09:00 | 34.24 | 34.01
2018-08-21 09:30 | 9.68 | 9.52
2018-08-21 10:00 | 15.06 | -15
2018-08-21 10:30 | 3.96 | -2.66
2018-08-21 11:00 | 6.45 | -6.45
2018-08-21 11:30 | 4.14 | -0.22
2018-08-21 12:00 | 5.87 | 3.57
2018-08-21 12:30 | 9.53 | 8.56
2018-08-21 13:00 | 7.63 | 6.38
2018-08-21 13:30 | 9.91 | 9.07
2018-08-21 14:00 | 14.95 | 14.44
2018-08-21 14:30 | 22.54 | 22.24
2018-08-21 15:00 | 25.22 | 24.98
2018-08-21 15:30 | 24.57 | 24.46
2018-08-21 16:00 | 40.05 | 40.01
2018-08-21 16:30 | 44.65 | 44.65
2018-08-21 17:00 | 63.69 | 63.69
2018-08-21 17:30 | 81.86 | 81.86
2018-08-21 18:00 | 89.34 | 89.34
2018-08-21 18:30 | 101.46 | 99.24
2018-08-21 19:00 | 115.86 | 114.01
2018-08-21 19:30 | 106.23 | 106.18
2018-08-21 20:00 | 85.83 | 85.73
2018-08-21 20:30 | 78.11 | 77.97
2018-08-21 21:00 | 67.71 | 67.71
2018-08-21 21:30 | 95.35 | 95.14
2018-08-21 22:00 | 81.43 | 80.7
2018-08-21 22:30 | 89.56 | 88.52
2018-08-21 23:00 | 75.91 | 74.11
2018-08-21 23:30 | 38.03 | 34.1
2018-08-22 | 18.09 | 2.82
2018-08-22 00:30 | 23.85 | 3.52
2018-08-22 01:00 | 27.24 | 12.77
2018-08-22 01:30 | 25.93 | 11.47
2018-08-22 02:00 | 35.06 | 26.76
2018-08-22 02:30 | 51.05 | 44.36
2018-08-22 03:00 | 57.89 | 50.61
2018-08-22 03:30 | 60.84 | 53.7
2018-08-22 04:00 | 65.17 | 57.89
2018-08-22 04:30 | 69.57 | 62.22
2018-08-22 05:00 | 74.25 | 66.68
2018-08-22 05:30 | 83.21 | 76.45
2018-08-22 06:00 | 91.2 | 86.3
2018-08-22 06:30 | 126.95 | 125.17
2018-08-22 07:00 | 198.28 | 198.13
2018-08-22 07:30 | 167.76 | 167.74
2018-08-22 08:00 | 116.1 | 115.69
2018-08-22 08:30 | 94.91 | 94.34
2018-08-22 09:00 | 95.5 | 94.68
2018-08-22 09:30 | 57.49 | 55.75
2018-08-22 10:00 | 31.23 | 26.99
2018-08-22 10:30 | 22.29 | 18.52
2018-08-22 11:00 | 12.84 | 11.5
2018-08-22 11:30 | 21.75 | 20.63
2018-08-22 12:00 | 30.11 | 21.58
2018-08-22 12:30 | 24.84 | 12.94
2018-08-22 13:00 | 20.57 | 0.03
2018-08-22 13:30 | 20.25 | -4.57
2018-08-22 14:00 | 20.68 | 7.92
2018-08-22 14:30 | 32.28 | 26.04
2018-08-22 15:00 | 47.47 | 42.91
2018-08-22 15:30 | 60.92 | 57.22
2018-08-22 16:00 | 94.76 | 92.04
2018-08-22 16:30 | 116.05 | 113.82
2018-08-22 17:00 | 137.68 | 135.89
2018-08-22 17:30 | 148.39 | 147.38
2018-08-22 18:00 | 124.72 | 124.09
2018-08-22 18:30 | 109.08 | 107.08
2018-08-22 19:00 | 115.17 | 114.4
2018-08-22 19:30 | 127.02 | 126.94
2018-08-22 20:00 | 134.19 | 134.08
2018-08-22 20:30 | 138.34 | 138.12
2018-08-22 21:00 | 136.42 | 136.4
2018-08-22 21:30 | 134.06 | 133.81
2018-08-22 22:00 | 122.09 | 121.49
2018-08-22 22:30 | 139.2 | 138.42
2018-08-22 23:00 | 153.49 | 152.5
2018-08-22 23:30 | 105.28 | 103.4
2018-08-23 | 60.33 | 56.31
2018-08-23 00:30 | 73.18 | 68.29
2018-08-23 01:00 | 64.22 | 59.1
2018-08-23 01:30 | 63.62 | 58.96
2018-08-23 02:00 | 63.18 | 58.05
2018-08-23 02:30 | 57.05 | 50.04
2018-08-23 03:00 | 49.55 | 41.04
2018-08-23 03:30 | 50.96 | 43.15
2018-08-23 04:00 | 68.96 | 67.77
2018-08-23 04:30 | 79.2 | 77.98
2018-08-23 05:00 | 106.77 | 105.85
2018-08-23 05:30 | 121.58 | 120.54
2018-08-23 06:00 | 155.54 | 154.83
2018-08-23 06:30 | 109.85 | 108.48
2018-08-23 07:00 | 79.77 | 79.61
2018-08-23 07:30 | 164.14 | 164.11
2018-08-23 08:00 | 119.44 | 118.81
2018-08-23 08:30 | 75.89 | 74.72
2018-08-23 09:00 | 66.47 | 64.95
2018-08-23 09:30 | 47.97 | 45.75
2018-08-23 10:00 | 23.93 | 21.28
2018-08-23 10:30 | 11.14 | 11.14
2018-08-23 11:00 | 21.4 | 21.4
2018-08-23 11:30 | 27.52 | 27.51
2018-08-23 12:00 | 30.04 | 30
2018-08-23 12:30 | 29.96 | 29.94
2018-08-23 13:00 | 36.41 | 36.4
2018-08-23 13:30 | 40.16 | 40.15
2018-08-23 14:00 | 33.62 | 33.62
2018-08-23 14:30 | 46.46 | 46.46
2018-08-23 15:00 | 71.88 | 71.88
2018-08-23 15:30 | 81.39 | 81.36
2018-08-23 16:00 | 88.67 | 88.64
2018-08-23 16:30 | 79.15 | 79.11
2018-08-23 17:00 | 94.16 | 94.1
2018-08-23 17:30 | 71.54 | 71.53
2018-08-23 18:00 | 71.45 | 71.11
2018-08-23 18:30 | 74.96 | 74.58
2018-08-23 19:00 | 82.29 | 82.07
2018-08-23 19:30 | 80.88 | 80.46
2018-08-23 20:00 | 89.98 | 89.41
2018-08-23 20:30 | 105.37 | 104.7
2018-08-23 21:00 | 100.01 | 99.45
2018-08-23 21:30 | 111.71 | 111.5
2018-08-23 22:00 | 104.24 | 103.68
2018-08-23 22:30 | 99.66 | 98.87
2018-08-23 23:00 | 103.75 | 102.73
2018-08-23 23:30 | 83.27 | 81.59
2018-08-24 | 47.95 | 44.44
2018-08-24 00:30 | 42.38 | 35.95
2018-08-24 01:00 | 38.11 | 29.41
2018-08-24 01:30 | 33.12 | 23.66
2018-08-24 02:00 | 35.62 | 27.48
2018-08-24 02:30 | 50.48 | 43.17
2018-08-24 03:00 | 45.65 | 35.99
2018-08-24 03:30 | 39.47 | 27.71
2018-08-24 04:00 | 49.31 | 39.86
2018-08-24 04:30 | 63.67 | 56.3
2018-08-24 05:00 | 69.87 | 62.24
2018-08-24 05:30 | 77.17 | 69.58
2018-08-24 06:00 | 84.46 | 77.84
2018-08-24 06:30 | 93.21 | 88.24
2018-08-24 07:00 | 112.3 | 109.01
2018-08-24 07:30 | 119.5 | 117.76
2018-08-24 08:00 | 114.57 | 112.92
2018-08-24 08:30 | 86.29 | 84.41
2018-08-24 09:00 | 71.7 | 69.49
2018-08-24 09:30 | 64.36 | 64.3
2018-08-24 10:00 | 53.41 | 53.09
2018-08-24 10:30 | 62.17 | 61.97
2018-08-24 11:00 | 65.99 | 65.78
2018-08-24 11:30 | 72.99 | 72.82
2018-08-24 12:00 | 64.62 | 64.46
2018-08-24 12:30 | 72.82 | 72.72
2018-08-24 13:00 | 93.65 | 93.56
2018-08-24 13:30 | 85.76 | 85.53
2018-08-24 14:00 | 105.55 | 105.28
2018-08-24 14:30 | 101.07 | 100.95
2018-08-24 15:00 | 92.34 | 92.3
2018-08-24 15:30 | 92.8 | 92.79
2018-08-24 16:00 | 95.75 | 95.73
2018-08-24 16:30 | 101.53 | 101.49
2018-08-24 17:00 | 107.36 | 106.98
2018-08-24 17:30 | 110.55 | 110.37
2018-08-24 18:00 | 92.99 | 92.93
2018-08-24 18:30 | 83.81 | 83.81
2018-08-24 19:00 | 86.56 | 86.53
2018-08-24 19:30 | 98.86 | 98.76
2018-08-24 20:00 | 109.74 | 109.53
2018-08-24 20:30 | 116.29 | 115.9
2018-08-24 21:00 | 110.54 | 109.87
2018-08-24 21:30 | 105.99 | 104.76
2018-08-24 22:00 | 95.08 | 94.67
2018-08-24 22:30 | 96.51 | 95.97
2018-08-24 23:00 | 102.84 | 102.13
2018-08-24 23:30 | 77.98 | 76.86
2018-08-25 | 43.23 | 40.81
2018-08-25 00:30 | 43.52 | 40.88
2018-08-25 01:00 | 35.95 | 33.3
2018-08-25 01:30 | 30.83 | 28.41
2018-08-25 02:00 | 20.89 | 17.68
2018-08-25 02:30 | 9.79 | -0.19
2018-08-25 03:00 | 12.09 | -8.01
2018-08-25 03:30 | 22.31 | -21.04
2018-08-25 04:00 | 26.91 | -25.98
2018-08-25 04:30 | 14.48 | -11.6
2018-08-25 05:00 | 16.39 | -13.65
2018-08-25 05:30 | 12.6 | -5.33
2018-08-25 06:00 | 17.28 | 9.13
2018-08-25 06:30 | 21.91 | 15.72
2018-08-25 07:00 | 27.65 | 22.02
2018-08-25 07:30 | 26.68 | 20.53
2018-08-25 08:00 | 7.8 | 5.42
2018-08-25 08:30 | 5.45 | -5.41
2018-08-25 09:00 | 25.61 | -24.98
2018-08-25 09:30 | 35.42 | -34.79
2018-08-25 10:00 | 13.1 | -12.95
2018-08-25 10:30 | 9.8 | -9.78
2018-08-25 11:00 | 22.59 | -22.56
2018-08-25 11:30 | 20.12 | -20.11
2018-08-25 12:00 | 57.13 | 55.9
2018-08-25 12:30 | 11.81 | -8.4
2018-08-25 13:00 | 12.95 | -10.29
2018-08-25 13:30 | 2.66 | 2.23
2018-08-25 14:00 | 14.94 | 3.36
2018-08-25 14:30 | 28.13 | 24.07
2018-08-25 15:00 | 79.85 | 79.37
2018-08-25 15:30 | 36.59 | 36.21
2018-08-25 16:00 | 14.47 | -14.43
2018-08-25 16:30 | 24.86 | -24.37
2018-08-25 17:00 | 3.95 | -3.4
2018-08-25 17:30 | 45.08 | 45.07
2018-08-25 18:00 | 35.14 | 17.22
2018-08-25 18:30 | 43.29 | 17.48
2018-08-25 19:00 | 42.06 | 11.76
2018-08-25 19:30 | 47.54 | 28.49
2018-08-25 20:00 | 33.48 | 28.34
2018-08-25 20:30 | 55.49 | 55.41
2018-08-25 21:00 | 73.83 | 73.11
2018-08-25 21:30 | 69.37 | 68.64
2018-08-25 22:00 | 22.26 | 21.26
2018-08-25 22:30 | 26.44 | 26.02
2018-08-25 23:00 | 37.08 | 36.53
2018-08-25 23:30 | 23.19 | -21.31
2018-08-26 | 31.72 | -30.04
2018-08-26 00:30 | 37.99 | -36.41
2018-08-26 01:00 | 39.87 | -38.61
2018-08-26 01:30 | 38.93 | -38.18
2018-08-26 02:00 | 24.41 | -24.23
2018-08-26 02:30 | 35.61 | -35.61
2018-08-26 03:00 | 38.92 | -38.91
2018-08-26 03:30 | 40.23 | -40.19
2018-08-26 04:00 | 39.99 | -39.94
2018-08-26 04:30 | 23.89 | -23.84
2018-08-26 05:00 | 7.46 | -4.89
2018-08-26 05:30 | 32.83 | -29.58
2018-08-26 06:00 | 40.82 | -38.26
2018-08-26 06:30 | 38.31 | -34.93
2018-08-26 07:00 | 40.77 | -36.5
2018-08-26 07:30 | 46.91 | -41.42
2018-08-26 08:00 | 40.81 | -38.83
2018-08-26 08:30 | 38.05 | -36.2
2018-08-26 09:00 | 33.41 | -33.16
2018-08-26 09:30 | 33.51 | -33.39
2018-08-26 10:00 | 27.8 | -27.49
2018-08-26 10:30 | 23.86 | -23.51
2018-08-26 11:00 | 12.79 | 12.76
2018-08-26 11:30 | 49.52 | 49.5
2018-08-26 12:00 | 40.16 | 40.15
2018-08-26 12:30 | 50.86 | 50.52
2018-08-26 13:00 | 41.09 | 40.6
2018-08-26 13:30 | 33.12 | 32.39
2018-08-26 14:00 | 13.66 | -13.25
2018-08-26 14:30 | 30.92 | -30.79
2018-08-26 15:00 | 30.15 | -30
2018-08-26 15:30 | 33.49 | -33.29
2018-08-26 16:00 | 38.28 | -38.23
2018-08-26 16:30 | 47.69 | -47.53
2018-08-26 17:00 | 48.59 | -48.45
2018-08-26 17:30 | 42.63 | -38.92
2018-08-26 18:00 | 24.8 | 23.36
2018-08-26 18:30 | 32.6 | 29.35
2018-08-26 19:00 | 63.99 | 63.64
2018-08-26 19:30 | 74.03 | 74.01
2018-08-26 20:00 | 75.68 | 75.68
2018-08-26 20:30 | 77.6 | 77.47
2018-08-26 21:00 | 73.91 | 73.44
2018-08-26 21:30 | 64.61 | 63.54
2018-08-26 22:00 | 56.99 | 55.26
2018-08-26 22:30 | 56.62 | 54.55
2018-08-26 23:00 | 64.92 | 62.44
2018-08-26 23:30 | 48.26 | 44.36
2018-08-27 | 25.77 | 15.81
2018-08-27 00:30 | 25.38 | 18.26
2018-08-27 01:00 | 13.52 | 0.09
2018-08-27 01:30 | 15.16 | -6.8
2018-08-27 02:00 | 10.27 | 7.88
2018-08-27 02:30 | 5.8 | 0.9
2018-08-27 03:00 | 9.86 | 8.77
2018-08-27 03:30 | 16.83 | 16.41
2018-08-27 04:00 | 20.71 | 20.59
2018-08-27 04:30 | 25.74 | 23.85
2018-08-27 05:00 | 33.09 | 25.83
2018-08-27 05:30 | 39.09 | 32.63
2018-08-27 06:00 | 45.15 | 41.47
2018-08-27 06:30 | 50.58 | 49.01
2018-08-27 07:00 | 63.63 | 63
2018-08-27 07:30 | 79.14 | 79.06
2018-08-27 08:00 | 78.49 | 78.48
2018-08-27 08:30 | 57.1 | 57.1
2018-08-27 09:00 | 27.66 | 27.66
2018-08-27 09:30 | 13.16 | 12.96
2018-08-27 10:00 | 5.95 | -2.22
2018-08-27 10:30 | 4.75 | 1.9
2018-08-27 11:00 | 20.1 | -18.8
2018-08-27 11:30 | 26.5 | -25.66
2018-08-27 12:00 | 31.23 | -30.47
2018-08-27 12:30 | 27.49 | -27.12
2018-08-27 13:00 | 21.17 | -20.61
2018-08-27 13:30 | 12.78 | -11.76
2018-08-27 14:00 | 5.67 | 2.6
2018-08-27 14:30 | 11.59 | 10.87
2018-08-27 15:00 | 11.38 | 11.09
2018-08-27 15:30 | 20.62 | 20.57
2018-08-27 16:00 | 56.73 | 56.72
2018-08-27 16:30 | 44.88 | 44.84
2018-08-27 17:00 | 62.6 | 62.55
2018-08-27 17:30 | 55.23 | 55.16
2018-08-27 18:00 | 48.03 | 47.18
2018-08-27 18:30 | 71.23 | 70.5
2018-08-27 19:00 | 79.05 | 78.24
2018-08-27 19:30 | 49.57 | 46.75
2018-08-27 20:00 | 73.29 | 72.31
2018-08-27 20:30 | 63.33 | 62.63
2018-08-27 21:00 | 69.64 | 69.64
2018-08-27 21:30 | 82.76 | 82.62
2018-08-27 22:00 | 68.88 | 68.43
2018-08-27 22:30 | 76.99 | 76.17
2018-08-27 23:00 | 72.16 | 70.87
2018-08-27 23:30 | 26.22 | 21.79
2018-08-28 | 18.6 | -11.3
2018-08-28 00:30 | 19.13 | -12.49
2018-08-28 01:00 | 20.97 | -16.27
2018-08-28 01:30 | 20.93 | -16.97
2018-08-28 02:00 | 10.97 | -7.86
2018-08-28 02:30 | 11.56 | -10.45
2018-08-28 03:00 | 15.35 | 13.53
2018-08-28 03:30 | 28.11 | 26.56
2018-08-28 04:00 | 39.59 | 37.4
2018-08-28 04:30 | 33.83 | 29.9
2018-08-28 05:00 | 43.07 | 39.66
2018-08-28 05:30 | 47.12 | 41.72
2018-08-28 06:00 | 55.61 | 51.71
2018-08-28 06:30 | 87.72 | 85.69
2018-08-28 07:00 | 44.72 | 43.65
2018-08-28 07:30 | 35.42 | 35.39
2018-08-28 08:00 | 2.97 | -2.49
2018-08-28 08:30 | 18.73 | -18.53
2018-08-28 09:00 | 16.08 | -15.67
2018-08-28 09:30 | 22 | -21.34
2018-08-28 10:00 | 25.74 | -25.03
2018-08-28 10:30 | 11.86 | -10.58
2018-08-28 11:00 | 7.15 | -4.94
2018-08-28 11:30 | 6.62 | 4.22
2018-08-28 12:00 | 9.26 | 7.8
2018-08-28 12:30 | 7.38 | 6.54
2018-08-28 13:00 | 4 | 1.51
2018-08-28 13:30 | 6.97 | -6.34
2018-08-28 14:00 | 4.62 | -3.63
2018-08-28 14:30 | 13.02 | 12.8
2018-08-28 15:00 | 19.33 | 19.29
2018-08-28 15:30 | 42.82 | 42.82
2018-08-28 16:00 | 61.4 | 61.39
2018-08-28 16:30 | 66.45 | 66.44
2018-08-28 17:00 | 63.93 | 62.37
2018-08-28 17:30 | 77.27 | 71.25
2018-08-28 18:00 | 74.64 | 66.5
2018-08-28 18:30 | 64.37 | 52.41
2018-08-28 19:00 | 72.35 | 62.7
2018-08-28 19:30 | 37.21 | 8.15
2018-08-28 20:00 | 61.37 | 52.28
2018-08-28 20:30 | 49.67 | 40.38
2018-08-28 21:00 | 54.23 | 54.08
2018-08-28 21:30 | 53.75 | 53.27
2018-08-28 22:00 | 45.53 | 44.31
2018-08-28 22:30 | 66.05 | 64.68
2018-08-28 23:00 | 68.95 | 67.35
2018-08-28 23:30 | 28.93 | 24.59
2018-08-29 | 16.56 | -12.04
2018-08-29 00:30 | 15.9 | 7.86
2018-08-29 01:00 | 14.49 | 7.65
2018-08-29 01:30 | 12.89 | -3.6
2018-08-29 02:00 | 13.13 | -6.74
2018-08-29 02:30 | 7.59 | 0.17
2018-08-29 03:00 | 15.83 | -15.09
2018-08-29 03:30 | 7.19 | 3.77
2018-08-29 04:00 | 25.64 | 24.58
2018-08-29 04:30 | 107.79 | 107.21
2018-08-29 05:00 | 87.86 | 86.38
2018-08-29 05:30 | 110.5 | 108.44
2018-08-29 06:00 | 101.43 | 98.48
2018-08-29 06:30 | 79.02 | 77.36
2018-08-29 07:00 | 103.35 | 103.1
2018-08-29 07:30 | 71.48 | 71.44
2018-08-29 08:00 | 63.35 | 63.23
2018-08-29 08:30 | 26.66 | -7.88
2018-08-29 09:00 | 28.5 | -13.28
2018-08-29 09:30 | 33.3 | 25.96
2018-08-29 10:00 | 52.54 | 48.92
2018-08-29 10:30 | 20.51 | 5.59
2018-08-29 11:00 | 21.21 | -4.1
2018-08-29 11:30 | 24.87 | 13.6
2018-08-29 12:00 | 30.3 | 23.54
2018-08-29 12:30 | 63.55 | 60.86
2018-08-29 13:00 | 107.75 | 106.22
2018-08-29 13:30 | 87.59 | 85.79
2018-08-29 14:00 | 73.64 | 71.39
2018-08-29 14:30 | 61.09 | 58.04
2018-08-29 15:00 | 75.44 | 73.79
2018-08-29 15:30 | 112.32 | 111.29
2018-08-29 16:00 | 123.16 | 122.49
2018-08-29 16:30 | 91.24 | 90.31
2018-08-29 17:00 | 59.07 | 56.32
2018-08-29 17:30 | 108.19 | 106.65
2018-08-29 18:00 | 80.72 | 71.65
2018-08-29 18:30 | 32.03 | 15.57
2018-08-29 19:00 | 19.82 | 3.8
2018-08-29 19:30 | 58.09 | 57.57
2018-08-29 20:00 | 118.55 | 116.96
2018-08-29 20:30 | 106.48 | 104.88
2018-08-29 21:00 | 110 | 108.91
2018-08-29 21:30 | 108.26 | 107.41
2018-08-29 22:00 | 96.32 | 95.93
2018-08-29 22:30 | 92.76 | 92.76
2018-08-29 23:00 | 79.97 | 78.26
2018-08-29 23:30 | 80.45 | 79.45
2018-08-30 | 33.45 | 32.29
2018-08-30 00:30 | 9.78 | -9.72
2018-08-30 01:00 | 2.66 | -1.41
2018-08-30 01:30 | 8.89 | 7.92
2018-08-30 02:00 | 29.76 | 29.24
2018-08-30 02:30 | 14.1 | 13.42
2018-08-30 03:00 | 84.05 | 83.67
2018-08-30 03:30 | 110.26 | 109.89
2018-08-30 04:00 | 107.37 | 106.98
2018-08-30 04:30 | 74.6 | 73.77
2018-08-30 05:00 | 114.02 | 113.23
2018-08-30 05:30 | 93.39 | 90.77
2018-08-30 06:00 | 80.13 | 75.91
2018-08-30 06:30 | 81.75 | 79.31
2018-08-30 07:00 | 75.33 | 74.82
2018-08-30 07:30 | 76.82 | 76.76
2018-08-30 08:00 | 42.84 | 42.84
2018-08-30 08:30 | 11.65 | 11.26
2018-08-30 09:00 | 7.02 | -6.37
2018-08-30 09:30 | 26.86 | -26.56
2018-08-30 10:00 | 21.72 | -21.42
2018-08-30 10:30 | 34.57 | -34.05
2018-08-30 11:00 | 27.19 | -26.59
2018-08-30 11:30 | 33.7 | -33.12
2018-08-30 12:00 | 34.47 | -33.96
2018-08-30 12:30 | 34.87 | -34.47
2018-08-30 13:00 | 34.11 | -33.69
2018-08-30 13:30 | 33.14 | -32.64
2018-08-30 14:00 | 16.66 | -16.13
2018-08-30 14:30 | 5.81 | -4.12
2018-08-30 15:00 | 6.64 | 6.42
2018-08-30 15:30 | 15.97 | 15.94
2018-08-30 16:00 | 41.3 | 41.3
2018-08-30 16:30 | 40.31 | 40.29
2018-08-30 17:00 | 55.73 | 55.7
2018-08-30 17:30 | 69.85 | 69.77
2018-08-30 18:00 | 80.15 | 76.79
2018-08-30 18:30 | 98.4 | 81.03
2018-08-30 19:00 | 108.38 | 97.61
2018-08-30 19:30 | 97.17 | 92.04
2018-08-30 20:00 | 75.38 | 68.71
2018-08-30 20:30 | 68.96 | 63.17
2018-08-30 21:00 | 40.47 | 40.29
2018-08-30 21:30 | 58.16 | 57.83
2018-08-30 22:00 | 70.29 | 69.53
2018-08-30 22:30 | 72.59 | 71.43
2018-08-30 23:00 | 73.63 | 72.19
2018-08-30 23:30 | 54.59 | 51.64
2018-08-31 | 18.3 | 9.99
2018-08-31 00:30 | 29.87 | 27.04
2018-08-31 01:00 | 18.93 | 15.61
2018-08-31 01:30 | 14.07 | 10.58
2018-08-31 02:00 | 8.75 | -1.66
2018-08-31 02:30 | 20.48 | 18.33
2018-08-31 03:00 | 24.5 | 22.97
2018-08-31 03:30 | 17.72 | 15.35
2018-08-31 04:00 | 17.98 | 15.45
2018-08-31 04:30 | 37.25 | 33.98
2018-08-31 05:00 | 53.6 | 50.82
2018-08-31 05:30 | 85.7 | 83.63
2018-08-31 06:00 | 92.92 | 90.51
2018-08-31 06:30 | 69.29 | 65.92
2018-08-31 07:00 | 34.3 | 29.65
2018-08-31 07:30 | 20.06 | -17.25
2018-08-31 08:00 | 43.91 | -43.49
2018-08-31 08:30 | 38.5 | -38.11
2018-08-31 09:00 | 37.02 | -36.84
2018-08-31 09:30 | 44.53 | -44.48
2018-08-31 10:00 | 43.6 | -43.58
2018-08-31 10:30 | 52.49 | -52.48
2018-08-31 11:00 | 51.69 | -51.68
2018-08-31 11:30 | 52.97 | -52.97
2018-08-31 12:00 | 54.22 | -54.22
2018-08-31 12:30 | 54.67 | -54.67
2018-08-31 13:00 | 54.25 | -54.24
2018-08-31 13:30 | 52.23 | -52.23
2018-08-31 14:00 | 48.76 | -48.75
2018-08-31 14:30 | 46.87 | -46.87
2018-08-31 15:00 | 38.61 | -38.55
2018-08-31 15:30 | 16.48 | -16.22
2018-08-31 16:00 | 16.6 | 16.04
2018-08-31 16:30 | 10.11 | 9.33
2018-08-31 17:00 | 19.97 | 19.47
2018-08-31 17:30 | 30.27 | 29.99
2018-08-31 18:00 | 59.29 | 59.27
2018-08-31 18:30 | 59.29 | 59.22
2018-08-31 19:00 | 60.78 | 60.71
2018-08-31 19:30 | 47.17 | 47.12
2018-08-31 20:00 | 32.44 | 32.44
2018-08-31 20:30 | 20.16 | 20.16
2018-08-31 21:00 | 20.25 | -20.19
2018-08-31 21:30 | 5.06 | -0.04
2018-08-31 22:00 | 10.8 | 3.57
2018-08-31 22:30 | 12.93 | 5.79
2018-08-31 23:00 | 29.4 | -27.8
2018-08-31 23:30 | 39.55 | -38.46
2018-09-01 | 49.56 | -49.08
2018-09-01 00:30 | 13.49 | -7.45
2018-09-01 01:00 | 11.45 | -2.5
2018-09-01 01:30 | 11.06 | -0.87
2018-09-01 02:00 | 16.19 | -13.93
2018-09-01 02:30 | 10.91 | 5.04
2018-09-01 03:00 | 27.48 | 24.6
2018-09-01 03:30 | 42.93 | 39.91
2018-09-01 04:00 | 53.13 | 50.68
2018-09-01 04:30 | 42.33 | 39.05
2018-09-01 05:00 | 49.49 | 46.45
2018-09-01 05:30 | 40.55 | 35.99
2018-09-01 06:00 | 34.87 | 29.1
2018-09-01 06:30 | 19.56 | 11.81
2018-09-01 07:00 | 21.73 | 13.85
2018-09-01 07:30 | 19.16 | 6.19
2018-09-01 08:00 | 17.67 | -8.86
2018-09-01 08:30 | 14.87 | -12.93
2018-09-01 09:00 | 15.13 | -13.74
2018-09-01 09:30 | 42.29 | -42.25
2018-09-01 10:00 | 30.8 | -30.78
2018-09-01 10:30 | 21.43 | -21.36
2018-09-01 11:00 | 13.69 | -13.58
2018-09-01 11:30 | 4.5 | 1.83
2018-09-01 12:00 | 5.14 | 1.55
2018-09-01 12:30 | 11.86 | 10.72
2018-09-01 13:00 | 5.45 | -3.03
2018-09-01 13:30 | 77.97 | 77.69
2018-09-01 14:00 | 54.41 | 54
2018-09-01 14:30 | 85.73 | 85.45
2018-09-01 15:00 | 27.65 | 26.82
2018-09-01 15:30 | 52.08 | 51.54
2018-09-01 16:00 | 61.31 | 60.94
2018-09-01 16:30 | 51.73 | 51.44
2018-09-01 17:00 | 79.36 | 79.24
2018-09-01 17:30 | 103.4 | 103.29
2018-09-01 18:00 | 93.88 | 93.25
2018-09-01 18:30 | 109.4 | 97.75
2018-09-01 19:00 | 111.85 | 101.26
2018-09-01 19:30 | 98.52 | 95.06
2018-09-01 20:00 | 96.69 | 96.43
2018-09-01 20:30 | 85.42 | 85.02
2018-09-01 21:00 | 62.46 | 61.68
2018-09-01 21:30 | 52.11 | 50.75
2018-09-01 22:00 | 36.36 | 33.88
2018-09-01 22:30 | 70.92 | 68.91
2018-09-01 23:00 | 78.45 | 76.45
2018-09-01 23:30 | 49.91 | 46.77
2018-09-02 | 25.19 | 19.85
2018-09-02 00:30 | 35.27 | 32.11
2018-09-02 01:00 | 46.78 | 44.12
2018-09-02 01:30 | 36.27 | 33.03
2018-09-02 02:00 | 33.08 | 29.79
2018-09-02 02:30 | 38.32 | 35.79
2018-09-02 03:00 | 28.41 | 25.23
2018-09-02 03:30 | 22.2 | 18.19
2018-09-02 04:00 | 13.38 | 5.61
2018-09-02 04:30 | 12.18 | 2.08
2018-09-02 05:00 | 22.93 | 18.81
2018-09-02 05:30 | 19.02 | 12.71
2018-09-02 06:00 | 17.08 | 10.66
2018-09-02 06:30 | 33.66 | 31.1
2018-09-02 07:00 | 34.14 | 30.77
2018-09-02 07:30 | 23.58 | 18.33
2018-09-02 08:00 | 16.35 | 2.74
2018-09-02 08:30 | 16.36 | -11.89
2018-09-02 09:00 | 31.29 | -29.71
2018-09-02 09:30 | 44.86 | -44.53
2018-09-02 10:00 | 47.46 | -47.36
2018-09-02 10:30 | 45.31 | -45.23
2018-09-02 11:00 | 42.38 | -42.26
2018-09-02 11:30 | 42.78 | -42.73
2018-09-02 12:00 | 44.67 | -44.62
2018-09-02 12:30 | 31.38 | -31.26
2018-09-02 13:00 | 24.43 | -24.08
2018-09-02 13:30 | 24.81 | -24.5
2018-09-02 14:00 | 9.53 | -8.47
2018-09-02 14:30 | 9.25 | 5.81
2018-09-02 15:00 | 8.14 | -3.53
2018-09-02 15:30 | 11.85 | -9.24
2018-09-02 16:00 | 12.52 | 9.14
2018-09-02 16:30 | 14.25 | 11.19
2018-09-02 17:00 | 56.61 | 55.75
2018-09-02 17:30 | 97.12 | 96.73
2018-09-02 18:00 | 95.14 | 95.13
2018-09-02 18:30 | 95.16 | 88.77
2018-09-02 19:00 | 86.57 | 71.45
2018-09-02 19:30 | 103.98 | 100.06
2018-09-02 20:00 | 96.27 | 96.16
2018-09-02 20:30 | 76.78 | 76.16
2018-09-02 21:00 | 70.67 | 69.78
2018-09-02 21:30 | 69.51 | 68.09
2018-09-02 22:00 | 59.07 | 56.97
2018-09-02 22:30 | 83.16 | 81.25
2018-09-02 23:00 | 77.72 | 75.71
2018-09-02 23:30 | 62 | 58.94
2018-09-03 | 32.33 | 26.71
2018-09-03 00:30 | 40 | 36.12
2018-09-03 01:00 | 31.29 | 26.09
2018-09-03 01:30 | 29.69 | 24.5
2018-09-03 02:00 | 32.29 | 29.04
2018-09-03 02:30 | 41.67 | 39.38
2018-09-03 03:00 | 34.16 | 31.15
2018-09-03 03:30 | 25.75 | 21.26
2018-09-03 04:00 | 28.31 | 24.16
2018-09-03 04:30 | 45.03 | 42.05
2018-09-03 05:00 | 53.71 | 50.88
2018-09-03 05:30 | 72.81 | 69.61
2018-09-03 06:00 | 87.01 | 83.42
2018-09-03 06:30 | 92.54 | 89.3
2018-09-03 07:00 | 68.6 | 67.42
2018-09-03 07:30 | 52.76 | 52.65
2018-09-03 08:00 | 30.38 | 26.98
2018-09-03 08:30 | 27.76 | -9.88
2018-09-03 09:00 | 33.7 | 22.06
2018-09-03 09:30 | 32.37 | 19.16
2018-09-03 10:00 | 30.32 | 17.75
2018-09-03 10:30 | 38.47 | 30.58
2018-09-03 11:00 | 55.75 | 50.85
2018-09-03 11:30 | 49.57 | 44.08
2018-09-03 12:00 | 56.05 | 52.36
2018-09-03 12:30 | 53.83 | 50.12
2018-09-03 13:00 | 44.55 | 40.16
2018-09-03 13:30 | 42.15 | 37
2018-09-03 14:00 | 58.17 | 54.47
2018-09-03 14:30 | 57.75 | 53.86
2018-09-03 15:00 | 88.13 | 85.84
2018-09-03 15:30 | 82.62 | 80.1
2018-09-03 16:00 | 79.07 | 76.96
2018-09-03 16:30 | 85.91 | 84.18
2018-09-03 17:00 | 63.9 | 62.98
2018-09-03 17:30 | 91.84 | 91.82
2018-09-03 18:00 | 84.32 | 83.92
2018-09-03 18:30 | 117.44 | 112.7
2018-09-03 19:00 | 116.99 | 115.71
2018-09-03 19:30 | 102.64 | 101.71
2018-09-03 20:00 | 180.42 | 180.4
2018-09-03 20:30 | 149.45 | 149.38
2018-09-03 21:00 | 93.32 | 92.38
2018-09-03 21:30 | 94.99 | 94.46
2018-09-03 22:00 | 84.89 | 84.54
2018-09-03 22:30 | 87.14 | 86.98
2018-09-03 23:00 | 96.02 | 95.97
2018-09-03 23:30 | 76.18 | 76.17
2018-09-04 | 31.94 | 30.63
2018-09-04 00:30 | 34.16 | 29.88
2018-09-04 01:00 | 21.36 | 14.65
2018-09-04 01:30 | 14.91 | 4.29
2018-09-04 02:00 | 21.46 | 16.22
2018-09-04 02:30 | 35.97 | 32.79
2018-09-04 03:00 | 33.65 | 30.43
2018-09-04 03:30 | 40.16 | 37.24
2018-09-04 04:00 | 52.96 | 50.37
2018-09-04 04:30 | 71.8 | 69.62
2018-09-04 05:00 | 93.3 | 91.75
2018-09-04 05:30 | 92.24 | 90.75
2018-09-04 06:00 | 99.3 | 97.85
2018-09-04 06:30 | 94.85 | 93.83
2018-09-04 07:00 | 83.81 | 83.36
2018-09-04 07:30 | 110.19 | 109.82
2018-09-04 08:00 | 114.89 | 103.14
2018-09-04 08:30 | 99.98 | 83.68
2018-09-04 09:00 | 107.09 | 91.94
2018-09-04 09:30 | 92.99 | 77.92
2018-09-04 10:00 | 63.96 | 54.61
2018-09-04 10:30 | 60.07 | 49.73
2018-09-04 11:00 | 63.16 | 53.96
2018-09-04 11:30 | 55.81 | 45.63
2018-09-04 12:00 | 45.68 | 45.39
2018-09-04 12:30 | 69.78 | 69.78
2018-09-04 13:00 | 65.49 | 65.49
2018-09-04 13:30 | 115.33 | 115.33
2018-09-04 14:00 | 152.94 | 152.94
2018-09-04 14:30 | 166.66 | 166.64
2018-09-04 15:00 | 171.98 | 171.98
2018-09-04 15:30 | 144.24 | 144.23
2018-09-04 16:00 | 123.34 | 123.33
2018-09-04 16:30 | 100.3 | 98.22
2018-09-04 17:00 | 122.05 | 110.44
2018-09-04 17:30 | 123.29 | 111.5
2018-09-04 18:00 | 121.91 | 106.7
2018-09-04 18:30 | 138.69 | 124.69
2018-09-04 19:00 | 142.99 | 130.02
2018-09-04 19:30 | 139.98 | 128.42
2018-09-04 20:00 | 150.61 | 140.98
2018-09-04 20:30 | 149.67 | 141.07
2018-09-04 21:00 | 98.22 | 85.58
2018-09-04 21:30 | 92.06 | 80.65
2018-09-04 22:00 | 89.51 | 87.1
2018-09-04 22:30 | 98.69 | 97.82
2018-09-04 23:00 | 120.01 | 118.81
2018-09-04 23:30 | 78.02 | 75.89
2018-09-05 | 36.68 | 32.95
2018-09-05 00:30 | 30.01 | 26.37
2018-09-05 01:00 | 18.51 | 13.74
2018-09-05 01:30 | 12.27 | 4.31
2018-09-05 02:00 | 17.15 | 9.88
2018-09-05 02:30 | 26.9 | 23.54
2018-09-05 03:00 | 39.62 | 38.33
2018-09-05 03:30 | 62.94 | 62.1
2018-09-05 04:00 | 75.24 | 74.4
2018-09-05 04:30 | 78.46 | 77.44
2018-09-05 05:00 | 103.4 | 102.28
2018-09-05 05:30 | 102.26 | 100.28
2018-09-05 06:00 | 108.25 | 105.84
2018-09-05 06:30 | 95.18 | 93.85
2018-09-05 07:00 | 83.15 | 82.94
2018-09-05 07:30 | 99.03 | 94.48
2018-09-05 08:00 | 96.37 | 78.93
2018-09-05 08:30 | 74.89 | 48.55
2018-09-05 09:00 | 110.7 | 94.62
2018-09-05 09:30 | 86.14 | 65.54
2018-09-05 10:00 | 55.81 | 39.84
2018-09-05 10:30 | 60.85 | 58.64
2018-09-05 11:00 | 52.15 | 52.09
2018-09-05 11:30 | 56.05 | 56
2018-09-05 12:00 | 49.39 | 49.31
2018-09-05 12:30 | 46.84 | 46.79
2018-09-05 13:00 | 50.07 | 49.95
2018-09-05 13:30 | 54 | 53.87
2018-09-05 14:00 | 70.87 | 70.76
2018-09-05 14:30 | 79.2 | 79.12
2018-09-05 15:00 | 81.64 | 81.6
2018-09-05 15:30 | 81.47 | 81.45
2018-09-05 16:00 | 94.78 | 94.78
2018-09-05 16:30 | 96.77 | 96.76
2018-09-05 17:00 | 101.64 | 100.37
2018-09-05 17:30 | 82.67 | 82.28
2018-09-05 18:00 | 98.04 | 96.86
2018-09-05 18:30 | 100 | 97.34
2018-09-05 19:00 | 123.44 | 122.12
2018-09-05 19:30 | 122.07 | 121.33
2018-09-05 20:00 | 129.24 | 121.2
2018-09-05 20:30 | 123.08 | 122.26
2018-09-05 21:00 | 116.31 | 116.06
2018-09-05 21:30 | 96.73 | 96.5
2018-09-05 22:00 | 84.37 | 84.28
2018-09-05 22:30 | 127.03 | 127.03
2018-09-05 23:00 | 159.44 | 159.42
2018-09-05 23:30 | 83.68 | 83.61
2018-09-06 | 37.8 | 37.09
2018-09-06 00:30 | 30.28 | 29.89
2018-09-06 01:00 | 19.19 | 18.93
2018-09-06 01:30 | 10.86 | 10.71
2018-09-06 02:00 | 32.37 | 32.12
2018-09-06 02:30 | 25.51 | 25.08
2018-09-06 03:00 | 2.94 | -1.69
2018-09-06 03:30 | 2.62 | -0.47
2018-09-06 04:00 | 7.75 | -7.25
2018-09-06 04:30 | 20.41 | 19.52
2018-09-06 05:00 | 35.52 | 34.88
2018-09-06 05:30 | 80.89 | 80.35
2018-09-06 06:00 | 70.63 | 70.03
2018-09-06 06:30 | 68.33 | 67.92
2018-09-06 07:00 | 13.42 | 8.42
2018-09-06 07:30 | 26.59 | 12.89
2018-09-06 08:00 | 28.86 | -12.75
2018-09-06 08:30 | 39.15 | -27.19
2018-09-06 09:00 | 28.5 | -7.68
2018-09-06 09:30 | 26.93 | 0.29
2018-09-06 10:00 | 35.3 | 24.36
2018-09-06 10:30 | 67.92 | 63.15
2018-09-06 11:00 | 38.4 | 30.62
2018-09-06 11:30 | 91.2 | 85.45
2018-09-06 12:00 | 70.93 | 63.5
2018-09-06 12:30 | 40.33 | 25.43
2018-09-06 13:00 | 36.25 | 16.4
2018-09-06 13:30 | 87.71 | 81.57
2018-09-06 14:00 | 55.38 | 43.71
2018-09-06 14:30 | 106.9 | 101.52
2018-09-06 15:00 | 65.9 | 57.64
2018-09-06 15:30 | 49.65 | 39.93
2018-09-06 16:00 | 61.76 | 54
2018-09-06 16:30 | 72.42 | 65.4
2018-09-06 17:00 | 83.35 | 78.25
2018-09-06 17:30 | 56.08 | 49.47
2018-09-06 18:00 | 79.14 | 72.55
2018-09-06 18:30 | 105 | 99.17
2018-09-06 19:00 | 120.2 | 115.58
2018-09-06 19:30 | 100.5 | 95.56
2018-09-06 20:00 | 124.89 | 121.79
2018-09-06 20:30 | 93.95 | 91.36
2018-09-06 21:00 | 78.89 | 77.88
2018-09-06 21:30 | 95.58 | 95.1
2018-09-06 22:00 | 86.11 | 85.81
2018-09-06 22:30 | 88.85 | 88.75
2018-09-06 23:00 | 97.35 | 97.34
2018-09-06 23:30 | 85.08 | 85.08
2018-09-07 | 65.59 | 64.88
2018-09-07 00:30 | 28.35 | 22.77
2018-09-07 01:00 | 15.46 | 3.84
2018-09-07 01:30 | 18.07 | -11.78
2018-09-07 02:00 | 58.85 | 57.03
2018-09-07 02:30 | 33.34 | 29.85
2018-09-07 03:00 | 102.21 | 101.71
2018-09-07 03:30 | 85.15 | 84.9
2018-09-07 04:00 | 60.92 | 60.57
2018-09-07 04:30 | 24.66 | 24.1
2018-09-07 05:00 | 44.89 | 43.86
2018-09-07 05:30 | 88.58 | 87.46
2018-09-07 06:00 | 80.41 | 78.5
2018-09-07 06:30 | 75.07 | 72.75
2018-09-07 07:00 | 71.05 | 69.86
2018-09-07 07:30 | 72.59 | 72.08
2018-09-07 08:00 | 46.96 | 45.07
2018-09-07 08:30 | 53.23 | -11.65
2018-09-07 09:00 | 58.26 | -20.45
2018-09-07 09:30 | 61.88 | -26.09
2018-09-07 10:00 | 57.9 | 1.83
2018-09-07 10:30 | 58.83 | 15.45
2018-09-07 11:00 | 58.34 | 6.27
2018-09-07 11:30 | 61.51 | 22.75
2018-09-07 12:00 | 57.65 | 2.21
2018-09-07 12:30 | 57.21 | -5.03
2018-09-07 13:00 | 58.31 | -10.17
2018-09-07 13:30 | 75.42 | -47.43
2018-09-07 14:00 | 63.84 | -26.66
2018-09-07 14:30 | 60.99 | -18.97
2018-09-07 15:00 | 56.84 | -6.51
2018-09-07 15:30 | 57.37 | 18.34
2018-09-07 16:00 | 68.37 | 43.14
2018-09-07 16:30 | 63.73 | 36.1
2018-09-07 17:00 | 74.86 | 54.05
2018-09-07 17:30 | 73.31 | 51.52
2018-09-07 18:00 | 72.53 | 47.66
2018-09-07 18:30 | 73.28 | 48.9
2018-09-07 19:00 | 72.92 | 49.22
2018-09-07 19:30 | 66.88 | 45.39
2018-09-07 20:00 | 62.13 | 39.94
2018-09-07 20:30 | 42.77 | -7.64
2018-09-07 21:00 | 45.96 | -21.39
2018-09-07 21:30 | 45.67 | -11.61
2018-09-07 22:00 | 25.24 | -5.52
2018-09-07 22:30 | 34.22 | -33.71
2018-09-07 23:00 | 30.56 | -29.36
2018-09-07 23:30 | 43.14 | -42.52
2018-09-08 | 54.49 | -53.82
2018-09-08 00:30 | 60.11 | -59.31
2018-09-08 01:00 | 64.24 | -63.44
2018-09-08 01:30 | 66.28 | -65.53
2018-09-08 02:00 | 64.26 | -64.23
2018-09-08 02:30 | 62.06 | -61.99
2018-09-08 03:00 | 60.11 | -60.03
2018-09-08 03:30 | 59.43 | -59.33
2018-09-08 04:00 | 59.02 | -58.93
2018-09-08 04:30 | 57.77 | -57.65
2018-09-08 05:00 | 56.44 | -56.27
2018-09-08 05:30 | 56.84 | -56.63
2018-09-08 06:00 | 56.29 | -56.04
2018-09-08 06:30 | 54.69 | -54.38
2018-09-08 07:00 | 53.5 | -52.94
2018-09-08 07:30 | 49.03 | -48.23
2018-09-08 08:00 | 44.78 | -44.44
2018-09-08 08:30 | 41.02 | -40.67
2018-09-08 09:00 | 35.57 | 33.11
2018-09-08 09:30 | 56.09 | 55.86
2018-09-08 10:00 | 34.76 | 34.61
2018-09-08 10:30 | 67.13 | 67.13
2018-09-08 11:00 | 74.51 | 73.5
2018-09-08 11:30 | 62.8 | 62.53
2018-09-08 12:00 | 35.23 | 33.14
2018-09-08 12:30 | 14.61 | 10.06
2018-09-08 13:00 | 11.02 | 0.62
2018-09-08 13:30 | 17.47 | 13.28
2018-09-08 14:00 | 61.15 | 58.9
2018-09-08 14:30 | 119.07 | 118.12
2018-09-08 15:00 | 106.24 | 104.89
2018-09-08 15:30 | 76.88 | 74.98
2018-09-08 16:00 | 68.8 | 66.68
2018-09-08 16:30 | 72.81 | 70.38
2018-09-08 17:00 | 48.82 | 47.99
2018-09-08 17:30 | 48.36 | 46.43
2018-09-08 18:00 | 39.17 | 35.68
2018-09-08 18:30 | 63.39 | 60.39
2018-09-08 19:00 | 73.98 | 71.78
2018-09-08 19:30 | 52.86 | 49.85
2018-09-08 20:00 | 42.54 | 39.41
2018-09-08 20:30 | 24.14 | 16.82
2018-09-08 21:00 | 29.02 | 28.38
2018-09-08 21:30 | 26.37 | 25.11
2018-09-08 22:00 | 18.48 | 17.35
2018-09-08 22:30 | 28.77 | 26.97
2018-09-08 23:00 | 22.18 | 19.98
2018-09-08 23:30 | 9.35 | 6.21
2018-09-09 | 29.39 | -29.39
2018-09-09 00:30 | 38.06 | -37.96
2018-09-09 01:00 | 33.55 | -33.48
2018-09-09 01:30 | 24.77 | -20.32
2018-09-09 02:00 | 18.7 | -6.16
2018-09-09 02:30 | 14.88 | 2.88
2018-09-09 03:00 | 15.49 | 0.26
2018-09-09 03:30 | 17.93 | 8.68
2018-09-09 04:00 | 17.39 | -2.24
2018-09-09 04:30 | 14.34 | -2.44
2018-09-09 05:00 | 13.95 | -5.62
2018-09-09 05:30 | 71.38 | 70.93
2018-09-09 06:00 | 79.57 | 78.24
2018-09-09 06:30 | 63.68 | 63.1
2018-09-09 07:00 | 58.33 | 58.16
2018-09-09 07:30 | 69.46 | 69.46
2018-09-09 08:00 | 13.39 | 12.33
2018-09-09 08:30 | 82.48 | 82.43
2018-09-09 09:00 | 7.2 | 2.13
2018-09-09 09:30 | 9.99 | -8.19
2018-09-09 10:00 | 28.19 | -25.97
2018-09-09 10:30 | 27.71 | -25.92
2018-09-09 11:00 | 18.19 | -14.53
2018-09-09 11:30 | 26.79 | -24.7
2018-09-09 12:00 | 60.55 | 59.08
2018-09-09 12:30 | 13.52 | 3.82
2018-09-09 13:00 | 15.95 | -10.1
2018-09-09 13:30 | 18.29 | 12.34
2018-09-09 14:00 | 20.25 | 14.54
2018-09-09 14:30 | 64.71 | 62.62
2018-09-09 15:00 | 44.9 | 41.49
2018-09-09 15:30 | 72.37 | 70.07
2018-09-09 16:00 | 89.6 | 87.81
2018-09-09 16:30 | 90.1 | 88.17
2018-09-09 17:00 | 116.61 | 115.21
2018-09-09 17:30 | 103.77 | 103.77
2018-09-09 18:00 | 101.13 | 100.88
2018-09-09 18:30 | 106.74 | 106.73
2018-09-09 19:00 | 110.56 | 110.53
2018-09-09 19:30 | 108.39 | 108.24
2018-09-09 20:00 | 109.57 | 109.56
2018-09-09 20:30 | 108.28 | 108.09
2018-09-09 21:00 | 98.28 | 98.19
2018-09-09 21:30 | 80.15 | 80.12
2018-09-09 22:00 | 69.07 | 69.07
2018-09-09 22:30 | 68.03 | 68.02
2018-09-09 23:00 | 83.13 | 83.09
2018-09-09 23:30 | 38.48 | 38.41
2018-09-10 | 7.39 | 7.35
2018-09-10 00:30 | 23.73 | 23.72
2018-09-10 01:00 | 17.21 | 17.09
2018-09-10 01:30 | 25.13 | 25.08
2018-09-10 02:00 | 11.53 | 11.42
2018-09-10 02:30 | 11.9 | 9.98
2018-09-10 03:00 | 17.53 | -0.71
2018-09-10 03:30 | 18.16 | 2.73
2018-09-10 04:00 | 21.25 | 10.41
2018-09-10 04:30 | 23.64 | 13.72
2018-09-10 05:00 | 27 | 18.33
2018-09-10 05:30 | 30.73 | 22.54
2018-09-10 06:00 | 41.74 | 36.94
2018-09-10 06:30 | 31.98 | 26.11
2018-09-10 07:00 | 24.15 | 23.84
2018-09-10 07:30 | 17.97 | 17.28
2018-09-10 08:00 | 6.12 | -6.11
2018-09-10 08:30 | 26.6 | -26.45
2018-09-10 09:00 | 30.38 | -30.38
2018-09-10 09:30 | 35.35 | -35.35
2018-09-10 10:00 | 38.39 | -38.38
2018-09-10 10:30 | 45.43 | -45.43
2018-09-10 11:00 | 41.27 | -41.26
2018-09-10 11:30 | 18.83 | -18.51
2018-09-10 12:00 | 10.27 | -5.36
2018-09-10 12:30 | 13.05 | -8.17
2018-09-10 13:00 | 11.46 | -4.35
2018-09-10 13:30 | 11.14 | -3.77
2018-09-10 14:00 | 17.52 | -15.01
2018-09-10 14:30 | 17.79 | -16.33
2018-09-10 15:00 | 6.17 | -1.17
2018-09-10 15:30 | 7.68 | 0.16
2018-09-10 16:00 | 23.3 | 21.35
2018-09-10 16:30 | 27.71 | 26.5
2018-09-10 17:00 | 55.54 | 54.92
2018-09-10 17:30 | 83.55 | 83.14
2018-09-10 18:00 | 71.6 | 71.5
2018-09-10 18:30 | 98.99 | 98.98
2018-09-10 19:00 | 99.74 | 99.74
2018-09-10 19:30 | 30.16 | 28.09
2018-09-10 20:00 | 63.36 | 63.33
2018-09-10 20:30 | 79.43 | 79.27
2018-09-10 21:00 | 71.33 | 70.76
2018-09-10 21:30 | 63.98 | 62.9
2018-09-10 22:00 | 18.65 | 13.63
2018-09-10 22:30 | 34.65 | 31.08
2018-09-10 23:00 | 37.58 | 34.32
2018-09-10 23:30 | 27.21 | -25.03
2018-09-11 | 44.51 | -44.1
2018-09-11 00:30 | 17.46 | -14.5
2018-09-11 01:00 | 14.99 | -12.12
2018-09-11 01:30 | 6.76 | -0.18
2018-09-11 02:00 | 9.78 | -8.36
2018-09-11 02:30 | 5.39 | -3.69
2018-09-11 03:00 | 13.43 | 2.3
2018-09-11 03:30 | 16.56 | 3.76
2018-09-11 04:00 | 57.56 | 56.06
2018-09-11 04:30 | 36.05 | 35.14
2018-09-11 05:00 | 48.26 | 47.19
2018-09-11 05:30 | 58.07 | 58.06
2018-09-11 06:00 | 72.51 | 72.46
2018-09-11 06:30 | 69.69 | 69.56
2018-09-11 07:00 | 53.2 | 52.43
2018-09-11 07:30 | 50.96 | 49.15
2018-09-11 08:00 | 47.59 | 45.2
2018-09-11 08:30 | 25.17 | 19.65
2018-09-11 09:00 | 30.26 | 27
2018-09-11 09:30 | 11.04 | 3.07
2018-09-11 10:00 | 7.92 | 6.49
2018-09-11 10:30 | 5.1 | 3.89
2018-09-11 11:00 | 9.6 | 9.01
2018-09-11 11:30 | 19.81 | 19.52
2018-09-11 12:00 | 31.46 | 31.26
2018-09-11 12:30 | 10.53 | 9.36
2018-09-11 13:00 | 15.64 | 14.95
2018-09-11 13:30 | 31.74 | 31.59
2018-09-11 14:00 | 30.94 | 30.76
2018-09-11 14:30 | 33.96 | 33.83
2018-09-11 15:00 | 40.32 | 40.23
2018-09-11 15:30 | 29.83 | 29.65
2018-09-11 16:00 | 40.87 | 40.83
2018-09-11 16:30 | 84.13 | 84.07
2018-09-11 17:00 | 74.51 | 74.3
2018-09-11 17:30 | 72.13 | 71.75
2018-09-11 18:00 | 85.11 | 83.85
2018-09-11 18:30 | 102.95 | 101
2018-09-11 19:00 | 112.36 | 110.49
2018-09-11 19:30 | 91.33 | 89
2018-09-11 20:00 | 105.19 | 103.81
2018-09-11 20:30 | 87.16 | 85.57
2018-09-11 21:00 | 76.88 | 75.87
2018-09-11 21:30 | 72.78 | 72.57
2018-09-11 22:00 | 71.88 | 69.96
2018-09-11 22:30 | 88.16 | 86.35
2018-09-11 23:00 | 94.86 | 93.12
2018-09-11 23:30 | 56.64 | 54.85
2018-09-12 | 16.94 | 14.65
2018-09-12 00:30 | 10.87 | 9.78
2018-09-12 01:00 | 13.74 | 12.05
2018-09-12 01:30 | 15.27 | 12.06
2018-09-12 02:00 | 16.47 | 14.04
2018-09-12 02:30 | 61.67 | 60.68
2018-09-12 03:00 | 15.85 | 7.47
2018-09-12 03:30 | 16.54 | 8.64
2018-09-12 04:00 | 22.72 | 17.03
2018-09-12 04:30 | 44.3 | 40.78
2018-09-12 05:00 | 57.08 | 53.68
2018-09-12 05:30 | 55.24 | 50.87
2018-09-12 06:00 | 68.76 | 64.84
2018-09-12 06:30 | 69.03 | 65.21
2018-09-12 07:00 | 35.48 | 31.98
2018-09-12 07:30 | 37.79 | 34.07
2018-09-12 08:00 | 14.23 | 11.09
2018-09-12 08:30 | 2.77 | -1.66
2018-09-12 09:00 | 9.71 | -8.82
2018-09-12 09:30 | 9.14 | 8.17
2018-09-12 10:00 | 21.64 | 21.17
2018-09-12 10:30 | 34.87 | 34.68
2018-09-12 11:00 | 23.87 | 23.54
2018-09-12 11:30 | 47 | 46.82
2018-09-12 12:00 | 16.21 | 15.39
2018-09-12 12:30 | 12.83 | 12.21
2018-09-12 13:00 | 19.78 | 19.31
2018-09-12 13:30 | 21.73 | 21.42
2018-09-12 14:00 | 22.61 | 22.2
2018-09-12 14:30 | 33.48 | 33.32
2018-09-12 15:00 | 44.58 | 44.48
2018-09-12 15:30 | 52.87 | 52.83
2018-09-12 16:00 | 54.21 | 54.13
2018-09-12 16:30 | 53.98 | 53.97
2018-09-12 17:00 | 62.9 | 62.9
2018-09-12 17:30 | 56.28 | 56.28
2018-09-12 18:00 | 60.34 | 60.31
2018-09-12 18:30 | 75.36 | 75.33
2018-09-12 19:00 | 69.87 | 69.81
2018-09-12 19:30 | 57.14 | 57.01
2018-09-12 20:00 | 49.05 | 48.81
2018-09-12 20:30 | 51.71 | 51.69
2018-09-12 21:00 | 30.36 | 30.2
2018-09-12 21:30 | 27.01 | 25.96
2018-09-12 22:00 | 13.85 | 9.65
2018-09-12 22:30 | 10.45 | 2.93
2018-09-12 23:00 | 16.58 | 13.22
2018-09-12 23:30 | 11.41 | -5.31
2018-09-13 | 24.08 | -22.5
2018-09-13 00:30 | 19.03 | -16.24
2018-09-13 01:00 | 32.43 | -31.43
2018-09-13 01:30 | 34.69 | -33.81
2018-09-13 02:00 | 18.18 | -15.75
2018-09-13 02:30 | 36.18 | 34.44
2018-09-13 03:00 | 39.53 | 38.06
2018-09-13 03:30 | 11.48 | -0.68
2018-09-13 04:00 | 12.03 | -1.43
2018-09-13 04:30 | 13.84 | 3.78
2018-09-13 05:00 | 19.6 | 11.73
2018-09-13 05:30 | 39.88 | 34.36
2018-09-13 06:00 | 90.35 | 88.27
2018-09-13 06:30 | 53.49 | 50.19
2018-09-13 07:00 | 17.94 | 12.64
2018-09-13 07:30 | 20.74 | 20.09
2018-09-13 08:00 | 27.91 | -2.04
2018-09-13 08:30 | 33.76 | -13.74
2018-09-13 09:00 | 31.36 | -0.94
2018-09-13 09:30 | 35.27 | 14.65
2018-09-13 10:00 | 35.15 | 11.36
2018-09-13 10:30 | 35.6 | 10.38
2018-09-13 11:00 | 43.13 | 26.25
2018-09-13 11:30 | 40.7 | 19.51
2018-09-13 12:00 | 37.17 | 5.12
2018-09-13 12:30 | 41.69 | 20.76
2018-09-13 13:00 | 48.69 | 32.48
2018-09-13 13:30 | 49.33 | 33.21
2018-09-13 14:00 | 55.07 | 41.42
2018-09-13 14:30 | 59.93 | 47.83
2018-09-13 15:00 | 69.18 | 59.47
2018-09-13 15:30 | 63.29 | 52.93
2018-09-13 16:00 | 80.48 | 73.33
2018-09-13 16:30 | 75.22 | 68.94
2018-09-13 17:00 | 85.47 | 80.34
2018-09-13 17:30 | 94.59 | 90.53
2018-09-13 18:00 | 96.76 | 91.89
2018-09-13 18:30 | 100.5 | 95.41
2018-09-13 19:00 | 104.27 | 99.53
2018-09-13 19:30 | 101.98 | 97.86
2018-09-13 20:00 | 85.63 | 81.17
2018-09-13 20:30 | 74.79 | 73.68
2018-09-13 21:00 | 59.25 | 58.68
2018-09-13 21:30 | 50.38 | 48.98
2018-09-13 22:00 | 40.65 | 37.63
2018-09-13 22:30 | 45.43 | 42.74
2018-09-13 23:00 | 48.59 | 45.63
2018-09-13 23:30 | 25 | 19.27
2018-09-14 | 14.99 | 4.01
2018-09-14 00:30 | 25.79 | 21.61
2018-09-14 01:00 | 28.3 | 24.55
2018-09-14 01:30 | 21.12 | 14.23
2018-09-14 02:00 | 20.09 | 12.61
2018-09-14 02:30 | 15.06 | -0.63
2018-09-14 03:00 | 15.02 | 3.45
2018-09-14 03:30 | 16.9 | 7.04
2018-09-14 04:00 | 17.61 | -11.07
2018-09-14 04:30 | 19.61 | 11.38
2018-09-14 05:00 | 59.14 | 56.26
2018-09-14 05:30 | 54.23 | 50.65
2018-09-14 06:00 | 92.39 | 90.39
2018-09-14 06:30 | 109.78 | 108.21
2018-09-14 07:00 | 86.1 | 85.01
2018-09-14 07:30 | 98.62 | 98.01
2018-09-14 08:00 | 91.5 | 91.08
2018-09-14 08:30 | 76.56 | 76.35
2018-09-14 09:00 | 85.28 | 85.23
2018-09-14 09:30 | 51.17 | 49.19
2018-09-14 10:00 | 62.24 | 58.41
2018-09-14 10:30 | 71.79 | 68.24
2018-09-14 11:00 | 72.43 | 68.63
2018-09-14 11:30 | 91.59 | 88.85
2018-09-14 12:00 | 111.71 | 109.29
2018-09-14 12:30 | 82.54 | 79.34
2018-09-14 13:00 | 69.33 | 65.57
2018-09-14 13:30 | 96.99 | 94.51
2018-09-14 14:00 | 82.64 | 79.68
2018-09-14 14:30 | 92.72 | 90.29
2018-09-14 15:00 | 83.35 | 80.66
2018-09-14 15:30 | 79.51 | 76.92
2018-09-14 16:00 | 125.21 | 123.91
2018-09-14 16:30 | 151.93 | 150.97
2018-09-14 17:00 | 111.97 | 110.83
2018-09-14 17:30 | 107.24 | 106.17
2018-09-14 18:00 | 96.35 | 94.99
2018-09-14 18:30 | 108.33 | 99.42
2018-09-14 19:00 | 110.3 | 98.84
2018-09-14 19:30 | 116.31 | 106.58
2018-09-14 20:00 | 120.36 | 112.25
2018-09-14 20:30 | 113.49 | 112.89
2018-09-14 21:00 | 99.78 | 99.22
2018-09-14 21:30 | 86.8 | 85.85
2018-09-14 22:00 | 74.9 | 73.44
2018-09-14 22:30 | 72.04 | 70.16
2018-09-14 23:00 | 86.35 | 84.54
2018-09-14 23:30 | 61.33 | 58.47
2018-09-15 | 44.38 | 41.15
2018-09-15 00:30 | 17.77 | 8.98
2018-09-15 01:00 | 14.68 | -4.17
2018-09-15 01:30 | 17.59 | -14.99
2018-09-15 02:00 | 70.09 | 68.5
2018-09-15 02:30 | 73.41 | 71.59
2018-09-15 03:00 | 52.78 | 51.25
2018-09-15 03:30 | 38.83 | 38.56
2018-09-15 04:00 | 41.97 | 41.58
2018-09-15 04:30 | 69.92 | 69.76
2018-09-15 05:00 | 72.3 | 72.1
2018-09-15 05:30 | 30.74 | 29.85
2018-09-15 06:00 | 79.65 | 79.33
2018-09-15 06:30 | 80.96 | 80.34
2018-09-15 07:00 | 67.37 | 66.15
2018-09-15 07:30 | 88 | 86.39
2018-09-15 08:00 | 40.79 | 37.46
2018-09-15 08:30 | 16.56 | 13.47
2018-09-15 09:00 | 10.2 | 6.26
2018-09-15 09:30 | 5.54 | -0.75
2018-09-15 10:00 | 10.54 | -9.66
2018-09-15 10:30 | 56.58 | 56.32
2018-09-15 11:00 | 3.33 | -0.69
2018-09-15 11:30 | 54 | 53.81
2018-09-15 12:00 | 38.42 | 38.18
2018-09-15 12:30 | 46.17 | 45.9
2018-09-15 13:00 | 15.03 | 14.59
2018-09-15 13:30 | 70.37 | 70.12
2018-09-15 14:00 | 9.79 | 9.33
2018-09-15 14:30 | 26.92 | 26.66
2018-09-15 15:00 | 89.81 | 89.6
2018-09-15 15:30 | 76.59 | 76.34
2018-09-15 16:00 | 36.95 | 36.72
2018-09-15 16:30 | 48.73 | 48.54
2018-09-15 17:00 | 73.57 | 73.46
2018-09-15 17:30 | 91.49 | 91.39
2018-09-15 18:00 | 68.64 | 68.01
2018-09-15 18:30 | 110.56 | 98.83
2018-09-15 19:00 | 102.84 | 90.03
2018-09-15 19:30 | 89.12 | 75.4
2018-09-15 20:00 | 87.12 | 85.72
2018-09-15 20:30 | 102.06 | 101.28
2018-09-15 21:00 | 86.65 | 86.06
2018-09-15 21:30 | 89.02 | 88.68
2018-09-15 22:00 | 60.64 | 60.37
2018-09-15 22:30 | 73.65 | 73.55
2018-09-15 23:00 | 90.87 | 90.81
2018-09-15 23:30 | 60.9 | 60.9
2018-09-16 | 32.88 | 32.85
2018-09-16 00:30 | 30.22 | 29.36
2018-09-16 01:00 | 24 | 17.41
2018-09-16 01:30 | 26 | 20.43
2018-09-16 02:00 | 41.51 | 38.29
2018-09-16 02:30 | 42.32 | 39.26
2018-09-16 03:00 | 54.53 | 52.24
2018-09-16 03:30 | 48.75 | 46.94
2018-09-16 04:00 | 37.55 | 36.55
2018-09-16 04:30 | 11 | -9.28
2018-09-16 05:00 | 49.96 | 49.46
2018-09-16 05:30 | 72.09 | 71.78
2018-09-16 06:00 | 50.78 | 50.42
2018-09-16 06:30 | 27.39 | 25.01
2018-09-16 07:00 | 6.98 | 1.67
2018-09-16 07:30 | 37.86 | 36.34
2018-09-16 08:00 | 43.28 | 40.78
2018-09-16 08:30 | 26.5 | 24.32
2018-09-16 09:00 | 49.24 | 47.82
2018-09-16 09:30 | 13.21 | 5.7
2018-09-16 10:00 | 10.51 | -6.55
2018-09-16 10:30 | 11.65 | -8.99
2018-09-16 11:00 | 20.92 | -19.82
2018-09-16 11:30 | 17.81 | 15.72
2018-09-16 12:00 | 77 | 76.06
2018-09-16 12:30 | 76.86 | 75.96
2018-09-16 13:00 | 83.68 | 82.78
2018-09-16 13:30 | 85.51 | 84.48
2018-09-16 14:00 | 54.39 | 52.93
2018-09-16 14:30 | 85.44 | 84.4
2018-09-16 15:00 | 55.24 | 53.84
2018-09-16 15:30 | 52.68 | 51.17
2018-09-16 16:00 | 30.6 | 27.33
2018-09-16 16:30 | 50.88 | 49.05
2018-09-16 17:00 | 84.89 | 83.89
2018-09-16 17:30 | 90.07 | 89.48
2018-09-16 18:00 | 83.58 | 83.58
2018-09-16 18:30 | 91.76 | 90.37
2018-09-16 19:00 | 90.89 | 89.71
2018-09-16 19:30 | 63.39 | 62.24
2018-09-16 20:00 | 44.23 | 42.92
2018-09-16 20:30 | 53.46 | 52.62
2018-09-16 21:00 | 38.52 | 37.55
2018-09-16 21:30 | 35.82 | 35.4
2018-09-16 22:00 | 25.15 | 24.85
2018-09-16 22:30 | 25.93 | 25.81
2018-09-16 23:00 | 40.21 | 40.19
2018-09-16 23:30 | 11.84 | 11.75
2018-09-17 | 2.29 | 0.85
2018-09-17 00:30 | 18.52 | -5.76
2018-09-17 01:00 | 27.61 | -22.28
2018-09-17 01:30 | 24.47 | -18.23
2018-09-17 02:00 | 28.38 | -24.01
2018-09-17 02:30 | 22.93 | -16.68
2018-09-17 03:00 | 15.8 | -1.39
2018-09-17 03:30 | 18.96 | 9.18
2018-09-17 04:00 | 18.04 | 6.84
2018-09-17 04:30 | 28.57 | -23.54
2018-09-17 05:00 | 18.75 | -4.16
2018-09-17 05:30 | 20.99 | 11.22
2018-09-17 06:00 | 37.99 | 32.95
2018-09-17 06:30 | 41.66 | 37.38
2018-09-17 07:00 | 117.73 | 116.72
2018-09-17 07:30 | 144.49 | 144.27
2018-09-17 08:00 | 148.85 | 148.85
2018-09-17 08:30 | 144.81 | 144.81
2018-09-17 09:00 | 141.01 | 141
2018-09-17 09:30 | 133.81 | 133.77
2018-09-17 10:00 | 131.14 | 131.05
2018-09-17 10:30 | 123.08 | 122.96
2018-09-17 11:00 | 121.4 | 121.23
2018-09-17 11:30 | 118.38 | 118.21
2018-09-17 12:00 | 121.5 | 121.34
2018-09-17 12:30 | 129.29 | 129.14
2018-09-17 13:00 | 131.84 | 131.67
2018-09-17 13:30 | 135.87 | 135.74
2018-09-17 14:00 | 138.76 | 138.61
2018-09-17 14:30 | 135.77 | 135.66
2018-09-17 15:00 | 138.63 | 138.53
2018-09-17 15:30 | 139.41 | 139.35
2018-09-17 16:00 | 135.5 | 135.5
2018-09-17 16:30 | 96.22 | 96.22
2018-09-17 17:00 | 109.18 | 107.17
2018-09-17 17:30 | 105.45 | 92.54
2018-09-17 18:00 | 110.52 | 96.94
2018-09-17 18:30 | 122.12 | 108.87
2018-09-17 19:00 | 117.26 | 104.04
2018-09-17 19:30 | 105.26 | 91.92
2018-09-17 20:00 | 95.4 | 81.27
2018-09-17 20:30 | 87.27 | 72.86
2018-09-17 21:00 | 75.05 | 64.79
2018-09-17 21:30 | 69.84 | 69.08
2018-09-17 22:00 | 59.69 | 59.1
2018-09-17 22:30 | 73.59 | 73.25
2018-09-17 23:00 | 60.79 | 60.44
2018-09-17 23:30 | 32.84 | 32.09
2018-09-18 | 17.72 | 15.53
2018-09-18 00:30 | 13.67 | 9.3
2018-09-18 01:00 | 19.69 | 16.75
2018-09-18 01:30 | 14.49 | 10.92
2018-09-18 02:00 | 10.44 | -2.4
2018-09-18 02:30 | 10.09 | 1.29
2018-09-18 03:00 | 10.83 | 3.61
2018-09-18 03:30 | 30.57 | 30.15
2018-09-18 04:00 | 23.8 | 22.43
2018-09-18 04:30 | 23.56 | 21.36
2018-09-18 05:00 | 95.41 | 94.97
2018-09-18 05:30 | 85.63 | 84.82
2018-09-18 06:00 | 94.35 | 93.2
2018-09-18 06:30 | 75.97 | 74.58
2018-09-18 07:00 | 59.52 | 58.83
2018-09-18 07:30 | 62.64 | 62.58
2018-09-18 08:00 | 58.97 | 57.97
2018-09-18 08:30 | 57.5 | 54.17
2018-09-18 09:00 | 65.56 | 62.3
2018-09-18 09:30 | 55.94 | 50.68
2018-09-18 10:00 | 57.82 | 52.08
2018-09-18 10:30 | 48.76 | 41.31
2018-09-18 11:00 | 60.81 | 54.65
2018-09-18 11:30 | 64.08 | 58.5
2018-09-18 12:00 | 52.36 | 45.65
2018-09-18 12:30 | 48.61 | 42.4
2018-09-18 13:00 | 45.96 | 39.05
2018-09-18 13:30 | 46.15 | 39.67
2018-09-18 14:00 | 48.9 | 42.49
2018-09-18 14:30 | 49.9 | 43.85
2018-09-18 15:00 | 49.81 | 44.05
2018-09-18 15:30 | 64.87 | 60.9
2018-09-18 16:00 | 62.34 | 58.73
2018-09-18 16:30 | 89.49 | 87.24
2018-09-18 17:00 | 104.45 | 102.86
2018-09-18 17:30 | 106.41 | 105.26
2018-09-18 18:00 | 108.25 | 106.5
2018-09-18 18:30 | 113.25 | 100.77
2018-09-18 19:00 | 115.6 | 104.13
2018-09-18 19:30 | 124.49 | 115.15
2018-09-18 20:00 | 119.55 | 116.97
2018-09-18 20:30 | 118.2 | 116.21
2018-09-18 21:00 | 100.48 | 99.98
2018-09-18 21:30 | 94.22 | 93.53
2018-09-18 22:00 | 85.56 | 84.43
2018-09-18 22:30 | 77.19 | 75.58
2018-09-18 23:00 | 82.99 | 81.31
2018-09-18 23:30 | 58.56 | 56.26
2018-09-19 | 23.98 | 18.58
2018-09-19 00:30 | 30.65 | 27.25
2018-09-19 01:00 | 21.64 | 17.24
2018-09-19 01:30 | 14.63 | -5.37
2018-09-19 02:00 | 16.26 | -8.74
2018-09-19 02:30 | 15.57 | -7.57
2018-09-19 03:00 | 14.32 | -3.7
2018-09-19 03:30 | 15.1 | 3.69
2018-09-19 04:00 | 17.38 | 7.37
2018-09-19 04:30 | 18.57 | 8.08
2018-09-19 05:00 | 22.16 | 15.33
2018-09-19 05:30 | 59.05 | 56.76
2018-09-19 06:00 | 76.47 | 74.5
2018-09-19 06:30 | 58.75 | 56.65
2018-09-19 07:00 | 41.24 | 39.91
2018-09-19 07:30 | 37.74 | 37.16
2018-09-19 08:00 | 9.42 | 9.39
2018-09-19 08:30 | 19.57 | -12.78
2018-09-19 09:00 | 35.22 | -25.88
2018-09-19 09:30 | 25.58 | -12.15
2018-09-19 10:00 | 24.99 | -9.33
2018-09-19 10:30 | 22.97 | 3.8
2018-09-19 11:00 | 29.37 | 19.03
2018-09-19 11:30 | 26.37 | 12.49
2018-09-19 12:00 | 23.95 | -3.49
2018-09-19 12:30 | 23.09 | 0.08
2018-09-19 13:00 | 23.3 | 1.04
2018-09-19 13:30 | 40.34 | 33.32
2018-09-19 14:00 | 36.45 | 29.42
2018-09-19 14:30 | 58.57 | 54.72
2018-09-19 15:00 | 75.2 | 72.38
2018-09-19 15:30 | 98.06 | 93.85
2018-09-19 16:00 | 96.9 | 92.37
2018-09-19 16:30 | 102.04 | 98
2018-09-19 17:00 | 110.36 | 106.69
2018-09-19 17:30 | 104.77 | 101.2
2018-09-19 18:00 | 113.27 | 109.67
2018-09-19 18:30 | 116.16 | 111.79
2018-09-19 19:00 | 126.94 | 122.82
2018-09-19 19:30 | 134.42 | 129
2018-09-19 20:00 | 128.39 | 120.04
2018-09-19 20:30 | 119.01 | 114.53
2018-09-19 21:00 | 105.13 | 105.08
2018-09-19 21:30 | 77.23 | 77.02
2018-09-19 22:00 | 67.69 | 67.05
2018-09-19 22:30 | 60.36 | 59.41
2018-09-19 23:00 | 35.71 | 33.82
2018-09-19 23:30 | 13.46 | -8.18
2018-09-20 | 42.64 | -41.92
2018-09-20 00:30 | 31.17 | -30.38
2018-09-20 01:00 | 43.29 | -42.91
2018-09-20 01:30 | 54.92 | -54.74
2018-09-20 02:00 | 60.26 | -60.2
2018-09-20 02:30 | 49.7 | -49.64
2018-09-20 03:00 | 50.51 | -50.51
2018-09-20 03:30 | 47.63 | -47.63
2018-09-20 04:00 | 51.16 | -51.15
2018-09-20 04:30 | 34.46 | -34.39
2018-09-20 05:00 | 18.82 | -17.99
2018-09-20 05:30 | 10.95 | -2.75
2018-09-20 06:00 | 19.37 | 13.25
2018-09-20 06:30 | 27.4 | 21.08
2018-09-20 07:00 | 39.65 | 37.62
2018-09-20 07:30 | 58.93 | 58.92
2018-09-20 08:00 | 58.27 | 58.22
2018-09-20 08:30 | 57.35 | 57.07
2018-09-20 09:00 | 51.3 | 50.43
2018-09-20 09:30 | 42.89 | 41.63
2018-09-20 10:00 | 44.5 | 34.84
2018-09-20 10:30 | 37.24 | 22.66
2018-09-20 11:00 | 35.93 | 20.31
2018-09-20 11:30 | 33.99 | 26.12
2018-09-20 12:00 | 33.98 | 31.38
2018-09-20 12:30 | 55.2 | 53.84
2018-09-20 13:00 | 53.54 | 52.03
2018-09-20 13:30 | 48.67 | 47.25
2018-09-20 14:00 | 52.36 | 50.97
2018-09-20 14:30 | 138.8 | 138.4
2018-09-20 15:00 | 108.04 | 107.69
2018-09-20 15:30 | 80.38 | 80.04
2018-09-20 16:00 | 118.23 | 118.1
2018-09-20 16:30 | 114.28 | 114.17
2018-09-20 17:00 | 126.09 | 126.05
2018-09-20 17:30 | 107.5 | 107.49
2018-09-20 18:00 | 109.17 | 109.13
2018-09-20 18:30 | 112.59 | 112.57
2018-09-20 19:00 | 115.99 | 115.77
2018-09-20 19:30 | 109.98 | 109.97
2018-09-20 20:00 | 101.96 | 101.96
2018-09-20 20:30 | 99.89 | 98.46
2018-09-20 21:00 | 107.48 | 105.89
2018-09-20 21:30 | 140.63 | 139.16
2018-09-20 22:00 | 63.67 | 60.41
2018-09-20 22:30 | 61.52 | 58.8
2018-09-20 23:00 | 98.22 | 95.59
2018-09-20 23:30 | 64.64 | 61.26
2018-09-21 | 27.06 | 22.35
2018-09-21 00:30 | 9.64 | -0.46
2018-09-21 01:00 | 17 | -15
2018-09-21 01:30 | 42.27 | -42.02
2018-09-21 02:00 | 48.58 | -48.51
2018-09-21 02:30 | 51.26 | -51.24
2018-09-21 03:00 | 48.66 | -48.66
2018-09-21 03:30 | 41.46 | -38.47
2018-09-21 04:00 | 47.44 | -44.69
2018-09-21 04:30 | 44.79 | -42.24
2018-09-21 05:00 | 8.22 | 1.34
2018-09-21 05:30 | 12.19 | 11.87
2018-09-21 06:00 | 9.57 | 9.13
2018-09-21 06:30 | 99.45 | 97.59
2018-09-21 07:00 | 48.48 | 46.64
2018-09-21 07:30 | 7.98 | 5.76
2018-09-21 08:00 | 8.89 | -8.61
2018-09-21 08:30 | 10.64 | -10.44
2018-09-21 09:00 | 7.03 | 6.52
2018-09-21 09:30 | 29.28 | -28.63
2018-09-21 10:00 | 34.44 | -33.82
2018-09-21 10:30 | 40.64 | -39.95
2018-09-21 11:00 | 29.14 | -28.18
2018-09-21 11:30 | 31.33 | -19.41
2018-09-21 12:00 | 28.87 | -10.54
2018-09-21 12:30 | 25.12 | -2.3
2018-09-21 13:00 | 26.31 | -9.99
2018-09-21 13:30 | 23.25 | -2.35
2018-09-21 14:00 | 28.56 | -15.39
2018-09-21 14:30 | 23.27 | -4.55
2018-09-21 15:00 | 20.85 | 2.17
2018-09-21 15:30 | 20.43 | 7.5
2018-09-21 16:00 | 44.36 | 40.78
2018-09-21 16:30 | 60.69 | 58.35
2018-09-21 17:00 | 60.29 | 58.65
2018-09-21 17:30 | 49.04 | 47.14
2018-09-21 18:00 | 54.39 | 52.43
2018-09-21 18:30 | 80.98 | 75.22
2018-09-21 19:00 | 86.59 | 82.53
2018-09-21 19:30 | 63.8 | 62.94
2018-09-21 20:00 | 97.36 | 97.22
2018-09-21 20:30 | 72.11 | 71.91
2018-09-21 21:00 | 33.1 | 32.53
2018-09-21 21:30 | 17.67 | 15.81
2018-09-21 22:00 | 12.12 | -7.43
2018-09-21 22:30 | 33.7 | -32.48
2018-09-21 23:00 | 13.56 | 3.79
2018-09-21 23:30 | 20.3 | -15.63
2018-09-22 | 43.11 | -42.31
2018-09-22 00:30 | 22.24 | -18.07
2018-09-22 01:00 | 29.68 | -27.11
2018-09-22 01:30 | 39.39 | -38.06
2018-09-22 02:00 | 48.02 | -47.24
2018-09-22 02:30 | 48.38 | -47.57
2018-09-22 03:00 | 56 | -55.65
2018-09-22 03:30 | 53.65 | -53.14
2018-09-22 04:00 | 51.75 | -51.09
2018-09-22 04:30 | 42.52 | -41.29
2018-09-22 05:00 | 28.53 | -24.88
2018-09-22 05:30 | 28.54 | -24.54
2018-09-22 06:00 | 30.05 | -26.68
2018-09-22 06:30 | 19.62 | -13.13
2018-09-22 07:00 | 16.97 | -9.45
2018-09-22 07:30 | 18.66 | -13.31
2018-09-22 08:00 | 25.41 | -22.93
2018-09-22 08:30 | 22.06 | -19.58
2018-09-22 09:00 | 15.62 | -13.15
2018-09-22 09:30 | 10.88 | -8.11
2018-09-22 10:00 | 13.61 | -12.32
2018-09-22 10:30 | 10.77 | -9.29
2018-09-22 11:00 | 14.76 | 13.62
2018-09-22 11:30 | 25.02 | 24.14
2018-09-22 12:00 | 20.76 | 19.46
2018-09-22 12:30 | 13.22 | 10.45
2018-09-22 13:00 | 14.83 | 11.46
2018-09-22 13:30 | 18.87 | 16.13
2018-09-22 14:00 | 17.21 | 14.47
2018-09-22 14:30 | 27.14 | 25.11
2018-09-22 15:00 | 33.09 | 31.36
2018-09-22 15:30 | 53.2 | 52.01
2018-09-22 16:00 | 62.25 | 61.38
2018-09-22 16:30 | 57.14 | 56.32
2018-09-22 17:00 | 82.14 | 81.65
2018-09-22 17:30 | 95.79 | 95.33
2018-09-22 18:00 | 74.83 | 74.34
2018-09-22 18:30 | 92.99 | 92.78
2018-09-22 19:00 | 100.13 | 99.87
2018-09-22 19:30 | 98.53 | 98.14
2018-09-22 20:00 | 100.55 | 100.01
2018-09-22 20:30 | 100.84 | 100.09
2018-09-22 21:00 | 85.44 | 84.48
2018-09-22 21:30 | 78.72 | 77.53
2018-09-22 22:00 | 61.09 | 59.25
2018-09-22 22:30 | 67.01 | 65
2018-09-22 23:00 | 52.07 | 49.49
2018-09-22 23:30 | 18.75 | 10.73
2018-09-23 | 15.57 | 4.19
2018-09-23 00:30 | 37.34 | 33.45
2018-09-23 01:00 | 38.54 | 34.82
2018-09-23 01:30 | 37.36 | 33.39
2018-09-23 02:00 | 23.83 | 19.55
2018-09-23 02:30 | 40.21 | 38.39
2018-09-23 03:00 | 12.18 | -4.51
2018-09-23 03:30 | 29.46 | 28.77
2018-09-23 04:00 | 6.48 | 1.83
2018-09-23 04:30 | 12.97 | -11.24
2018-09-23 05:00 | 7.75 | 2.44
2018-09-23 05:30 | 18.71 | 16.94
2018-09-23 06:00 | 19 | 18.5
2018-09-23 06:30 | 25.82 | 25.15
2018-09-23 07:00 | 14.04 | 11.67
2018-09-23 07:30 | 10.06 | -2.87
2018-09-23 08:00 | 14.12 | -7.19
2018-09-23 08:30 | 19.88 | -17.01
2018-09-23 09:00 | 20.75 | -17.8
2018-09-23 09:30 | 16.2 | 5.79
2018-09-23 10:00 | 16.5 | -5.36
2018-09-23 10:30 | 21.43 | -15.64
2018-09-23 11:00 | 25.25 | -20.83
2018-09-23 11:30 | 24 | -18.74
2018-09-23 12:00 | 21.84 | -15.08
2018-09-23 12:30 | 22.81 | -17.07
2018-09-23 13:00 | 18.64 | -9.81
2018-09-23 13:30 | 16.95 | -3.21
2018-09-23 14:00 | 19.81 | 8.08
2018-09-23 14:30 | 53.04 | 48.01
2018-09-23 15:00 | 39.1 | 31.44
2018-09-23 15:30 | 48.44 | 42.9
2018-09-23 16:00 | 54.95 | 51.48
2018-09-23 16:30 | 60.89 | 59.91
2018-09-23 17:00 | 59.6 | 59.05
2018-09-23 17:30 | 76.44 | 76.01
2018-09-23 18:00 | 89.67 | 89.4
2018-09-23 18:30 | 96.33 | 96.22
2018-09-23 19:00 | 99.65 | 99.46
2018-09-23 19:30 | 88.61 | 88.25
2018-09-23 20:00 | 86.01 | 85.42
2018-09-23 20:30 | 74 | 73.17
2018-09-23 21:00 | 70.21 | 69.08
2018-09-23 21:30 | 70.85 | 69.27
2018-09-23 22:00 | 57.26 | 54.78
2018-09-23 22:30 | 56.06 | 53.18
2018-09-23 23:00 | 71.69 | 69.43
2018-09-23 23:30 | 33.34 | 28.08
2018-09-24 | 19.93 | -12.24
2018-09-24 00:30 | 16.34 | 3.88
2018-09-24 01:00 | 15.9 | -2.64
2018-09-24 01:30 | 14.72 | -0.61
2018-09-24 02:00 | 15.73 | 2.3
2018-09-24 02:30 | 17.43 | 2.36
2018-09-24 03:00 | 17.23 | 3.26
2018-09-24 03:30 | 17.83 | 3.14
2018-09-24 04:00 | 19.82 | 6.31
2018-09-24 04:30 | 28.86 | 20.94
2018-09-24 05:00 | 42.11 | 37.36
2018-09-24 05:30 | 70.83 | 68.23
2018-09-24 06:00 | 66.66 | 63.98
2018-09-24 06:30 | 82.21 | 80.01
2018-09-24 07:00 | 66.41 | 63.94
2018-09-24 07:30 | 53.52 | 51.79
2018-09-24 08:00 | 16.88 | 16.72
2018-09-24 08:30 | 22.26 | 11.92
2018-09-24 09:00 | 117.44 | 116.3
2018-09-24 09:30 | 132.34 | 130.16
2018-09-24 10:00 | 133.47 | 130.86
2018-09-24 10:30 | 118.23 | 114.66
2018-09-24 11:00 | 117.54 | 113.85
2018-09-24 11:30 | 115.02 | 111.16
2018-09-24 12:00 | 122.48 | 118.87
2018-09-24 12:30 | 122.75 | 119.2
2018-09-24 13:00 | 128.31 | 124.9
2018-09-24 13:30 | 128.07 | 124.88
2018-09-24 14:00 | 137.28 | 134.38
2018-09-24 14:30 | 129.54 | 126.45
2018-09-24 15:00 | 130.49 | 127.74
2018-09-24 15:30 | 98.06 | 95.76
2018-09-24 16:00 | 72.87 | 70.71
2018-09-24 16:30 | 89.41 | 87.81
2018-09-24 17:00 | 96.36 | 94.93
2018-09-24 17:30 | 83.34 | 81.8
2018-09-24 18:00 | 80.83 | 77.18
2018-09-24 18:30 | 84.92 | 76.22
2018-09-24 19:00 | 70.87 | 64.92
2018-09-24 19:30 | 63.13 | 61.75
2018-09-24 20:00 | 65.29 | 64.36
2018-09-24 20:30 | 50.01 | 49.19
2018-09-24 21:00 | 34.85 | 34.1
2018-09-24 21:30 | 33.39 | 32.91
2018-09-24 22:00 | 36.11 | 32.02
2018-09-24 22:30 | 29.6 | 24.74
2018-09-24 23:00 | 43.31 | 40.09
2018-09-24 23:30 | 33.55 | 29.17
2018-09-25 | 15.34 | 4.9
2018-09-25 00:30 | 15.65 | 6.94
2018-09-25 01:00 | 15.35 | -6.74
2018-09-25 01:30 | 21.13 | -16.49
2018-09-25 02:00 | 23.22 | -18.52
2018-09-25 02:30 | 23.93 | -18.87
2018-09-25 03:00 | 23.69 | -18.81
2018-09-25 03:30 | 25.64 | -20.51
2018-09-25 04:00 | 30.24 | -24.56
2018-09-25 04:30 | 22.9 | -14.2
2018-09-25 05:00 | 19.71 | -7.53
2018-09-25 05:30 | 27.61 | 19.63
2018-09-25 06:00 | 58 | 54.97
2018-09-25 06:30 | 47.21 | 43.75
2018-09-25 07:00 | 47.85 | 45.25
2018-09-25 07:30 | 47.39 | 46.42
2018-09-25 08:00 | 42.97 | 42.75
2018-09-25 08:30 | 63.63 | 63.6
2018-09-25 09:00 | 39.75 | 38.16
2018-09-25 09:30 | 25.58 | 15.63
2018-09-25 10:00 | 27.98 | 18.65
2018-09-25 10:30 | 29.45 | 19.75
2018-09-25 11:00 | 49.34 | -42.41
2018-09-25 11:30 | 55.74 | -49.8
2018-09-25 12:00 | 46.94 | -39.51
2018-09-25 12:30 | 32.92 | -20.84
2018-09-25 13:00 | 25.2 | 0.4
2018-09-25 13:30 | 25.07 | 9.08
2018-09-25 14:00 | 25.65 | 11.74
2018-09-25 14:30 | 28.82 | 17.59
2018-09-25 15:00 | 30.59 | 20.8
2018-09-25 15:30 | 27.71 | 18.02
2018-09-25 16:00 | 21.67 | 6.83
2018-09-25 16:30 | 23.63 | -9.77
2018-09-25 17:00 | 49.84 | -15.24
2018-09-25 17:30 | 57.39 | -16.86
2018-09-25 18:00 | 58.89 | 20.54
2018-09-25 18:30 | 56.38 | 6.75
2018-09-25 19:00 | 55.98 | -9.19
2018-09-25 19:30 | 61.1 | 44.53
2018-09-25 20:00 | 72 | 70.29
2018-09-25 20:30 | 77.26 | 76.11
2018-09-25 21:00 | 66.03 | 65.05
2018-09-25 21:30 | 56.11 | 55.44
2018-09-25 22:00 | 61.03 | 60.77
2018-09-25 22:30 | 52.19 | 52.05
2018-09-25 23:00 | 64.2 | 64.16
2018-09-25 23:30 | 32.46 | 32.4
2018-09-26 | 8.24 | 8.22
2018-09-26 00:30 | 19.14 | 8.69
2018-09-26 01:00 | 25.29 | -20.27
2018-09-26 01:30 | 59.48 | -58.85
2018-09-26 02:00 | 62.3 | -62.12
2018-09-26 02:30 | 59.42 | -59.25
2018-09-26 03:00 | 19.26 | -14.56
2018-09-26 03:30 | 24.26 | -18.8
2018-09-26 04:00 | 22.62 | -14.97
2018-09-26 04:30 | 18.03 | -0.03
2018-09-26 05:00 | 21.74 | 13.01
2018-09-26 05:30 | 47.18 | 43.88
2018-09-26 06:00 | 69.77 | 67.97
2018-09-26 06:30 | 72.86 | 71.24
2018-09-26 07:00 | 69.41 | 68.34
2018-09-26 07:30 | 57.1 | 56.9
2018-09-26 08:00 | 49.63 | 49.58
2018-09-26 08:30 | 56.53 | 55.83
2018-09-26 09:00 | 53.38 | 53.04
2018-09-26 09:30 | 50.68 | 50.17
2018-09-26 10:00 | 49.73 | 49.44
2018-09-26 10:30 | 36.37 | 36.25
2018-09-26 11:00 | 37.74 | 37.64
2018-09-26 11:30 | 49.78 | 49.7
2018-09-26 12:00 | 46.33 | 46.25
2018-09-26 12:30 | 40.31 | 40.15
2018-09-26 13:00 | 38.18 | 37.89
2018-09-26 13:30 | 42.31 | 39.16
2018-09-26 14:00 | 45.04 | 38.02
2018-09-26 14:30 | 58.5 | 53.23
2018-09-26 15:00 | 59.17 | 39.4
2018-09-26 15:30 | 71.62 | 45.83
2018-09-26 16:00 | 74.52 | 53.5
2018-09-26 16:30 | 74.29 | 53.51
2018-09-26 17:00 | 76.64 | 56.44
2018-09-26 17:30 | 78.86 | 58.07
2018-09-26 18:00 | 84.28 | 63.99
2018-09-26 18:30 | 86.16 | 65.8
2018-09-26 19:00 | 92.67 | 75.1
2018-09-26 19:30 | 85.35 | 66.4
2018-09-26 20:00 | 84.7 | 67.6
2018-09-26 20:30 | 65.72 | 63.38
2018-09-26 21:00 | 60.01 | 58.02
2018-09-26 21:30 | 52.14 | 50.58
2018-09-26 22:00 | 43.08 | 41.96
2018-09-26 22:30 | 41.63 | 40.75
2018-09-26 23:00 | 47.83 | 47.37
2018-09-26 23:30 | 33.15 | 32.66
2018-09-27 | 20.2 | 18.68
2018-09-27 00:30 | 10.59 | 6.07
2018-09-27 01:00 | 8.79 | -0.4
2018-09-27 01:30 | 7.65 | -6.01
2018-09-27 02:00 | 6.85 | -3.62
2018-09-27 02:30 | 6.36 | 1.09
2018-09-27 03:00 | 17.58 | 15.08
2018-09-27 03:30 | 11.26 | 5.04
2018-09-27 04:00 | 17.52 | 13.69
2018-09-27 04:30 | 17.51 | 13.71
2018-09-27 05:00 | 13.97 | 9.6
2018-09-27 05:30 | 21.8 | 18.1
2018-09-27 06:00 | 25.69 | 22.5
2018-09-27 06:30 | 38.19 | 35.39
2018-09-27 07:00 | 44.07 | 43.44
2018-09-27 07:30 | 51.32 | 51.21
2018-09-27 08:00 | 51.38 | 51.34
2018-09-27 08:30 | 52.19 | 50.98
2018-09-27 09:00 | 53.71 | 48.81
2018-09-27 09:30 | 52.61 | 46.18
2018-09-27 10:00 | 54.93 | 48.34
2018-09-27 10:30 | 64.7 | 59.01
2018-09-27 11:00 | 78.53 | 73.27
2018-09-27 11:30 | 94.86 | 90.52
2018-09-27 12:00 | 101.87 | 98.38
2018-09-27 12:30 | 96.74 | 92.95
2018-09-27 13:00 | 99.63 | 96.18
2018-09-27 13:30 | 104.41 | 101.09
2018-09-27 14:00 | 103.32 | 100.43
2018-09-27 14:30 | 92.25 | 89.09
2018-09-27 15:00 | 108.55 | 106.32
2018-09-27 15:30 | 114.31 | 112.4
2018-09-27 16:00 | 97.65 | 95.76
2018-09-27 16:30 | 98.85 | 97.2
2018-09-27 17:00 | 147.98 | 146.89
2018-09-27 17:30 | 155.33 | 154.25
2018-09-27 18:00 | 117.23 | 114.17
2018-09-27 18:30 | 121.26 | 112.97
2018-09-27 19:00 | 123.9 | 118.39
2018-09-27 19:30 | 117.09 | 116.21
2018-09-27 20:00 | 119.06 | 119.05
2018-09-27 20:30 | 133.63 | 133.38
2018-09-27 21:00 | 125.34 | 124.93
2018-09-27 21:30 | 116.43 | 115.91
2018-09-27 22:00 | 107 | 106.45
2018-09-27 22:30 | 104.85 | 104.29
2018-09-27 23:00 | 112.95 | 112.28
2018-09-27 23:30 | 94.87 | 94.19
2018-09-28 | 76.67 | 76.25
2018-09-28 00:30 | 63.66 | 63.21
2018-09-28 01:00 | 55.33 | 54.95
2018-09-28 01:30 | 50.51 | 49.74
2018-09-28 02:00 | 24.97 | 23.25
2018-09-28 02:30 | 11.3 | 7.07
2018-09-28 03:00 | 8.56 | 2.11
2018-09-28 03:30 | 9.69 | 3.65
2018-09-28 04:00 | 9.56 | 3.78
2018-09-28 04:30 | 11.52 | 6.44
2018-09-28 05:00 | 14.37 | 10.35
2018-09-28 05:30 | 27.07 | 24.89
2018-09-28 06:00 | 51.46 | 50.22
2018-09-28 06:30 | 81.45 | 80.6
2018-09-28 07:00 | 58.48 | 58.11
2018-09-28 07:30 | 48.91 | 48.91
2018-09-28 08:00 | 47.79 | 47.65
2018-09-28 08:30 | 40.61 | 35.93
2018-09-28 09:00 | 48.67 | 40.08
2018-09-28 09:30 | 51.51 | 42.72
2018-09-28 10:00 | 42.8 | 31.06
2018-09-28 10:30 | 48.73 | 38.23
2018-09-28 11:00 | 60.04 | 51.92
2018-09-28 11:30 | 39.91 | 26.07
2018-09-28 12:00 | 36.9 | 20.96
2018-09-28 12:30 | 36.93 | 20.56
2018-09-28 13:00 | 39 | 23.12
2018-09-28 13:30 | 41.55 | 27.43
2018-09-28 14:00 | 44.86 | 30.96
2018-09-28 14:30 | 61.11 | 53.1
2018-09-28 15:00 | 81.82 | 76.05
2018-09-28 15:30 | 98.41 | 93.53
2018-09-28 16:00 | 104.54 | 102.35
2018-09-28 16:30 | 132.41 | 131.96
2018-09-28 17:00 | 143.74 | 143.4
2018-09-28 17:30 | 140.73 | 140.51
2018-09-28 18:00 | 116.92 | 116.66
2018-09-28 18:30 | 109.65 | 109.14
2018-09-28 19:00 | 113.09 | 112.66
2018-09-28 19:30 | 113.13 | 112.85
2018-09-28 20:00 | 133.23 | 133.1
2018-09-28 20:30 | 139.37 | 139.34
2018-09-28 21:00 | 111.79 | 111.79
2018-09-28 21:30 | 102.41 | 102.39
2018-09-28 22:00 | 100.97 | 100.9
2018-09-28 22:30 | 112.06 | 111.91
2018-09-28 23:00 | 135.18 | 134.95
2018-09-28 23:30 | 108.63 | 108.57
2018-09-29 | 97.61 | 97.58
2018-09-29 00:30 | 78.88 | 78.87
2018-09-29 01:00 | 80.43 | 79.7
2018-09-29 01:30 | 64.09 | 61.79
2018-09-29 02:00 | 58.17 | 55.37
2018-09-29 02:30 | 45.08 | 41.42
2018-09-29 03:00 | 50.99 | 48.09
2018-09-29 03:30 | 30.38 | 23.88
2018-09-29 04:00 | 51.59 | 48.56
2018-09-29 04:30 | 52.95 | 49.77
2018-09-29 05:00 | 40.42 | 35.92
2018-09-29 05:30 | 64.73 | 62.15
2018-09-29 06:00 | 72.26 | 69.7
2018-09-29 06:30 | 81.31 | 79.12
2018-09-29 07:00 | 62.23 | 59.57
2018-09-29 07:30 | 50.86 | 47.07
2018-09-29 08:00 | 47.2 | 42.82
2018-09-29 08:30 | 43.58 | 35.24
2018-09-29 09:00 | 61.94 | 57.17
2018-09-29 09:30 | 55.07 | 50.22
2018-09-29 10:00 | 45.74 | 39.55
2018-09-29 10:30 | 44.5 | 38.51
2018-09-29 11:00 | 46.78 | 41.28
2018-09-29 11:30 | 47.37 | 42.15
2018-09-29 12:00 | 49.9 | 45.52
2018-09-29 12:30 | 42.2 | 36.68
2018-09-29 13:00 | 38.94 | 33.11
2018-09-29 13:30 | 41.57 | 36.57
2018-09-29 14:00 | 53.76 | 50.69
2018-09-29 14:30 | 81.64 | 79.74
2018-09-29 15:00 | 124.27 | 123.78
2018-09-29 15:30 | 143.79 | 143.76
2018-09-29 16:00 | 159.85 | 159.85
2018-09-29 16:30 | 162.29 | 162.29
2018-09-29 17:00 | 151.32 | 151.32
2018-09-29 17:30 | 132.21 | 130.31
2018-09-29 18:00 | 112.34 | 110.65
2018-09-29 18:30 | 136.53 | 136.08
2018-09-29 19:00 | 140.49 | 140.08
2018-09-29 19:30 | 130.99 | 130.54
2018-09-29 20:00 | 120.53 | 120.2
2018-09-29 20:30 | 122.42 | 122.39
2018-09-29 21:00 | 105.55 | 105.55
2018-09-29 21:30 | 103.58 | 103.54
2018-09-29 22:00 | 86.89 | 86.77
2018-09-29 22:30 | 87.08 | 86.88
2018-09-29 23:00 | 79.42 | 79.14
2018-09-29 23:30 | 38.89 | 38.27
2018-09-30 | 22.82 | 21.26
2018-09-30 00:30 | 26.48 | 24.92
2018-09-30 01:00 | 20.24 | 17.95
2018-09-30 01:30 | 26.21 | 24.36
2018-09-30 02:00 | 18.74 | 16.4
2018-09-30 02:30 | 20.67 | 18.25
2018-09-30 03:00 | 12.09 | 8.55
2018-09-30 03:30 | 12.01 | 8.64
2018-09-30 04:00 | 12.08 | 8.76
2018-09-30 04:30 | 15.76 | 13.06
2018-09-30 05:00 | 17.26 | 14.67
2018-09-30 05:30 | 16.83 | 14.64
2018-09-30 06:00 | 14.85 | 12.25
2018-09-30 06:30 | 13.91 | 11.65
2018-09-30 07:00 | 16.12 | 14.5
2018-09-30 07:30 | 21.15 | 19.93
2018-09-30 08:00 | 28.16 | 27.5
2018-09-30 08:30 | 39.78 | 39.38
2018-09-30 09:00 | 75.99 | 75.87
2018-09-30 09:30 | 91.74 | 91.7
2018-09-30 10:00 | 114.13 | 114.12
2018-09-30 10:30 | 93.84 | 93.84
2018-09-30 11:00 | 99.54 | 99.54
2018-09-30 11:30 | 131.46 | 131.45
2018-09-30 12:00 | 114.87 | 114.87
2018-09-30 12:30 | 108.58 | 108.57
2018-09-30 13:00 | 97.49 | 97.48
2018-09-30 13:30 | 79.64 | 79.6
2018-09-30 14:00 | 61.21 | 61.13
2018-09-30 14:30 | 71.89 | 71.8
2018-09-30 15:00 | 72.57 | 72.52
2018-09-30 15:30 | 69.95 | 69.85
2018-09-30 16:00 | 57.56 | 57.41
2018-09-30 16:30 | 73.06 | 72.95
2018-09-30 17:00 | 87.33 | 87.22
2018-09-30 17:30 | 89.94 | 89.88
2018-09-30 18:00 | 90.32 | 90.11
2018-09-30 18:30 | 107.81 | 97.9
2018-09-30 19:00 | 134.39 | 122.61
2018-09-30 19:30 | 150.95 | 141.63
2018-09-30 20:00 | 149.22 | 141.89
2018-09-30 20:30 | 141.18 | 138.71
2018-09-30 21:00 | 127.31 | 126.43
2018-09-30 21:30 | 125.4 | 125.06
2018-09-30 22:00 | 105.05 | 104.51
2018-09-30 22:30 | 115.25 | 114.64
2018-09-30 23:00 | 124.2 | 123.5
2018-09-30 23:30 | 93.45 | 92.6
2018-10-01 | 57.51 | 56.08
2018-10-01 00:30 | 41.58 | 39.56
2018-10-01 01:00 | 24.09 | 20.58
2018-10-01 01:30 | 16.77 | 11.79
2018-10-01 02:00 | 11.44 | 2.9
2018-10-01 02:30 | 11.65 | 4.38
2018-10-01 03:00 | 11.42 | 4.4
2018-10-01 03:30 | 18.83 | 16.13
2018-10-01 04:00 | 16.88 | 16.88
2018-10-01 04:30 | 18.88 | 18.86
2018-10-01 05:00 | 27.01 | 26.93
2018-10-01 05:30 | 9.83 | 9.81
2018-10-01 06:00 | 12.75 | 12.66
2018-10-01 06:30 | 17.58 | 17.58
2018-10-01 07:00 | 17.71 | 17.71
2018-10-01 07:30 | 26.35 | 26.31
2018-10-01 08:00 | 30.57 | 30.57
2018-10-01 08:30 | 36.78 | 36.74
2018-10-01 09:00 | 39.55 | 39.03
2018-10-01 09:30 | 33.14 | 32.45
2018-10-01 10:00 | 38.03 | 37.6
2018-10-01 10:30 | 27.18 | 26.72
2018-10-01 11:00 | 28.44 | 28.13
2018-10-01 11:30 | 25.29 | 25.08
2018-10-01 12:00 | 31.59 | 31.44
2018-10-01 12:30 | 32.27 | 32.22
2018-10-01 13:00 | 29.15 | 29.15
2018-10-01 13:30 | 27.47 | 27.46
2018-10-01 14:00 | 30.92 | 30.92
2018-10-01 14:30 | 31.78 | 31.77
2018-10-01 15:00 | 33.97 | 33.97
2018-10-01 15:30 | 36.45 | 36.44
2018-10-01 16:00 | 44.25 | 44.24
2018-10-01 16:30 | 46.87 | 46.86
2018-10-01 17:00 | 64.07 | 64.07
2018-10-01 17:30 | 89.32 | 89.32
2018-10-01 18:00 | 101.41 | 100.51
2018-10-01 18:30 | 116.07 | 100.38
2018-10-01 19:00 | 113.82 | 98.49
2018-10-01 19:30 | 117.66 | 104.39
2018-10-01 20:00 | 130.22 | 119.62
2018-10-01 20:30 | 133.22 | 127.66
2018-10-01 21:00 | 100.44 | 100.15
2018-10-01 21:30 | 86.56 | 86.09
2018-10-01 22:00 | 64.59 | 63.76
2018-10-01 22:30 | 61.18 | 60.16
2018-10-01 23:00 | 65.71 | 64.68
2018-10-01 23:30 | 49.15 | 48.08
2018-10-02 | 19.93 | 17.82
2018-10-02 00:30 | 12.72 | 8.6
2018-10-02 01:00 | 9.67 | -1.03
2018-10-02 01:30 | 9.8 | -1.3
2018-10-02 02:00 | 9.52 | -3.4
2018-10-02 02:30 | 9.51 | 1.26
2018-10-02 03:00 | 9.67 | 3.45
2018-10-02 03:30 | 10.41 | 4.64
2018-10-02 04:00 | 11.74 | 7.72
2018-10-02 04:30 | 13.26 | 10.02
2018-10-02 05:00 | 13.99 | 10.83
2018-10-02 05:30 | 16.17 | 13.31
2018-10-02 06:00 | 31.04 | 29.55
2018-10-02 06:30 | 31.64 | 30.66
2018-10-02 07:00 | 39.47 | 39.11
2018-10-02 07:30 | 50.93 | 50.77
2018-10-02 08:00 | 51.56 | 51.55
2018-10-02 08:30 | 50.87 | 50.86
2018-10-02 09:00 | 42.45 | 42.28
2018-10-02 09:30 | 50 | 49.67
2018-10-02 10:00 | 51.27 | 50.96
2018-10-02 10:30 | 37.82 | 37.07
2018-10-02 11:00 | 38.4 | 37.81
2018-10-02 11:30 | 36.24 | 35.59
2018-10-02 12:00 | 36.14 | 35.49
2018-10-02 12:30 | 37.71 | 37.24
2018-10-02 13:00 | 26.49 | 25.65
2018-10-02 13:30 | 32.91 | 31.05
2018-10-02 14:00 | 40.49 | 38.89
2018-10-02 14:30 | 46.61 | 45.2
2018-10-02 15:00 | 53.64 | 52.56
2018-10-02 15:30 | 49.24 | 48.09
2018-10-02 16:00 | 55.45 | 51.64
2018-10-02 16:30 | 73.26 | 68.1
2018-10-02 17:00 | 97.57 | 94.06
2018-10-02 17:30 | 105.49 | 95.99
2018-10-02 18:00 | 118.21 | 103.01
2018-10-02 18:30 | 122.64 | 105.99
2018-10-02 19:00 | 128.28 | 121.33
2018-10-02 19:30 | 127.14 | 121.13
2018-10-02 20:00 | 147.75 | 143.09
2018-10-02 20:30 | 132.04 | 127.62
2018-10-02 21:00 | 115.94 | 112.67
2018-10-02 21:30 | 95.21 | 95.2
2018-10-02 22:00 | 89.36 | 89.35
2018-10-02 22:30 | 91.22 | 91.22
2018-10-02 23:00 | 91.26 | 91.25
2018-10-02 23:30 | 46.65 | 46.55
2018-10-03 | 33.61 | 33.23
2018-10-03 00:30 | 39.81 | 39.62
2018-10-03 01:00 | 31.82 | 31.75
2018-10-03 01:30 | 31.53 | 31.2
2018-10-03 02:00 | 7.34 | 7.33
2018-10-03 02:30 | 9.93 | 9.93
2018-10-03 03:00 | 29.06 | 28.41
2018-10-03 03:30 | 33.32 | 29.48
2018-10-03 04:00 | 40.55 | 35.56
2018-10-03 04:30 | 57.14 | 53.98
2018-10-03 05:00 | 70.96 | 68.84
2018-10-03 05:30 | 92.91 | 91.47
2018-10-03 06:00 | 115.99 | 114.68
2018-10-03 06:30 | 128.61 | 128.53
2018-10-03 07:00 | 117.18 | 117.11
2018-10-03 07:30 | 106.99 | 106.91
2018-10-03 08:00 | 98.23 | 98.15
2018-10-03 08:30 | 84.04 | 83.9
2018-10-03 09:00 | 130.64 | 130.59
2018-10-03 09:30 | 144.32 | 143.41
2018-10-03 10:00 | 140.46 | 136.92
2018-10-03 10:30 | 130.02 | 126.17
2018-10-03 11:00 | 129.38 | 125.36
2018-10-03 11:30 | 126.36 | 122.39
2018-10-03 12:00 | 126.99 | 123.26
2018-10-03 12:30 | 127.16 | 123.4
2018-10-03 13:00 | 129.16 | 125.65
2018-10-03 13:30 | 133.41 | 130.18
2018-10-03 14:00 | 137.66 | 134.67
2018-10-03 14:30 | 73.09 | 69.03
2018-10-03 15:00 | 54.24 | 48.47
2018-10-03 15:30 | 54.89 | 50.36
2018-10-03 16:00 | 57.5 | 53.68
2018-10-03 16:30 | 72.39 | 69.83
2018-10-03 17:00 | 85.4 | 82.57
2018-10-03 17:30 | 91.95 | 88.05
2018-10-03 18:00 | 96.55 | 91.69
2018-10-03 18:30 | 97.43 | 91.81
2018-10-03 19:00 | 102.19 | 96.27
2018-10-03 19:30 | 105.04 | 99.14
2018-10-03 20:00 | 115.54 | 110.81
2018-10-03 20:30 | 114.15 | 110.1
2018-10-03 21:00 | 95.43 | 91.08
2018-10-03 21:30 | 99.62 | 95.66
2018-10-03 22:00 | 92 | 91.01
2018-10-03 22:30 | 89.98 | 89.97
2018-10-03 23:00 | 85.12 | 85.11
2018-10-03 23:30 | 42.83 | 42.75
2018-10-04 | 20.57 | 20.09
2018-10-04 00:30 | 27.11 | 26.74
2018-10-04 01:00 | 12.62 | 11.23
2018-10-04 01:30 | 14.95 | 13.87
2018-10-04 02:00 | 21.06 | 21.03
2018-10-04 02:30 | 32.31 | 32.29
2018-10-04 03:00 | 32.38 | 32.35
2018-10-04 03:30 | 35.53 | 35.39
2018-10-04 04:00 | 32.96 | 32.82
2018-10-04 04:30 | 47.13 | 47.12
2018-10-04 05:00 | 42.27 | 42.25
2018-10-04 05:30 | 51.04 | 50.96
2018-10-04 06:00 | 84.95 | 84.91
2018-10-04 06:30 | 88.28 | 88.17
2018-10-04 07:00 | 109.88 | 109.87
2018-10-04 07:30 | 146.12 | 143.16
2018-10-04 08:00 | 146.24 | 142.5
2018-10-04 08:30 | 147.93 | 144.16
2018-10-04 09:00 | 143.17 | 139.44
2018-10-04 09:30 | 140.19 | 136.35
2018-10-04 10:00 | 138.41 | 134.85
2018-10-04 10:30 | 130.37 | 126.45
2018-10-04 11:00 | 129.85 | 125.68
2018-10-04 11:30 | 129.41 | 125.32
2018-10-04 12:00 | 129.7 | 125.79
2018-10-04 12:30 | 130.57 | 126.53
2018-10-04 13:00 | 133.2 | 129.45
2018-10-04 13:30 | 136.41 | 133.07
2018-10-04 14:00 | 145.58 | 142.81
2018-10-04 14:30 | 144.31 | 141.38
2018-10-04 15:00 | 144.61 | 141.73
2018-10-04 15:30 | 144.29 | 141.57
2018-10-04 16:00 | 145.67 | 143.09
2018-10-04 16:30 | 153.38 | 150.98
2018-10-04 17:00 | 156.79 | 154.33
2018-10-04 17:30 | 160.85 | 158
2018-10-04 18:00 | 158.28 | 156.69
2018-10-04 18:30 | 126.4 | 123.56
2018-10-04 19:00 | 124.19 | 120.63
2018-10-04 19:30 | 126.92 | 123.54
2018-10-04 20:00 | 157.47 | 154.64
2018-10-04 20:30 | 120.66 | 117.18
2018-10-04 21:00 | 120.34 | 117.24
2018-10-04 21:30 | 126.71 | 124.33
2018-10-04 22:00 | 109.51 | 109.31
2018-10-04 22:30 | 112.23 | 112.23
2018-10-04 23:00 | 124.4 | 124.38
2018-10-04 23:30 | 98.59 | 98.58
2018-10-05 | 65.46 | 65.46
2018-10-05 00:30 | 57.8 | 57.77
2018-10-05 01:00 | 42.53 | 42.52
2018-10-05 01:30 | 38.92 | 38.92
2018-10-05 02:00 | 31.46 | 31.45
2018-10-05 02:30 | 34.18 | 34.17
2018-10-05 03:00 | 41.76 | 41.76
2018-10-05 03:30 | 60.31 | 60.3
2018-10-05 04:00 | 61.74 | 61.74
2018-10-05 04:30 | 81.94 | 81.94
2018-10-05 05:00 | 76.83 | 76.82
2018-10-05 05:30 | 108.04 | 108.04
2018-10-05 06:00 | 121.82 | 121.59
2018-10-05 06:30 | 110.76 | 110.26
2018-10-05 07:00 | 123.99 | 123.73
2018-10-05 07:30 | 109.86 | 101.88
2018-10-05 08:00 | 104.06 | 88.15
2018-10-05 08:30 | 90.25 | 68.71
2018-10-05 09:00 | 101.71 | 81.58
2018-10-05 09:30 | 122.97 | 105.67
2018-10-05 10:00 | 152.46 | 138.54
2018-10-05 10:30 | 150.33 | 134.41
2018-10-05 11:00 | 161.68 | 146.54
2018-10-05 11:30 | 152.98 | 137.08
2018-10-05 12:00 | 165 | 150.42
2018-10-05 12:30 | 156.56 | 141.13
2018-10-05 13:00 | 151.86 | 136.65
2018-10-05 13:30 | 150.23 | 135.14
2018-10-05 14:00 | 152.95 | 138.17
2018-10-05 14:30 | 162.91 | 149.25
2018-10-05 15:00 | 151.31 | 139.66
2018-10-05 15:30 | 163.69 | 153.54
2018-10-05 16:00 | 153.31 | 142.77
2018-10-05 16:30 | 160.6 | 150.82
2018-10-05 17:00 | 182.48 | 174.39
2018-10-05 17:30 | 165.94 | 157.4
2018-10-05 18:00 | 162.3 | 153.76
2018-10-05 18:30 | 169.65 | 161.14
2018-10-05 19:00 | 167.29 | 158.9
2018-10-05 19:30 | 148.98 | 140.35
2018-10-05 20:00 | 139.39 | 130.36
2018-10-05 20:30 | 134.01 | 125.14
2018-10-05 21:00 | 112.72 | 103
2018-10-05 21:30 | 94.08 | 86.34
2018-10-05 22:00 | 62.63 | 62.08
2018-10-05 22:30 | 60.02 | 59.65
2018-10-05 23:00 | 72.1 | 71.9
2018-10-05 23:30 | 33.86 | 33.55
2018-10-06 | 7.08 | -6.08
2018-10-06 00:30 | 15.73 | -15.39
2018-10-06 01:00 | 14.04 | -13.86
2018-10-06 01:30 | 11.79 | -11.65
2018-10-06 02:00 | 16.44 | -16.4
2018-10-06 02:30 | 25.45 | -25.42
2018-10-06 03:00 | 30.46 | -30.41
2018-10-06 03:30 | 27.08 | -27.06
2018-10-06 04:00 | 27.31 | -27.28
2018-10-06 04:30 | 21.64 | -21.6
2018-10-06 05:00 | 20.49 | -20.43
2018-10-06 05:30 | 20.7 | -20.58
2018-10-06 06:00 | 8.6 | 8.47
2018-10-06 06:30 | 23.62 | 23.48
2018-10-06 07:00 | 17.88 | 17.46
2018-10-06 07:30 | 30.99 | 30.21
2018-10-06 08:00 | 31.98 | 30.41
2018-10-06 08:30 | 41.51 | 39.46
2018-10-06 09:00 | 46.22 | 42.75
2018-10-06 09:30 | 40.98 | 8.85
2018-10-06 10:00 | 42.83 | 16.97
2018-10-06 10:30 | 21.92 | -0.42
2018-10-06 11:00 | 22.74 | 2.51
2018-10-06 11:30 | 22.11 | 6.26
2018-10-06 12:00 | 38.77 | 33.35
2018-10-06 12:30 | 37.48 | 32.11
2018-10-06 13:00 | 50.58 | 47.24
2018-10-06 13:30 | 55.55 | 52.34
2018-10-06 14:00 | 47.47 | 43.93
2018-10-06 14:30 | 46.41 | 42.95
2018-10-06 15:00 | 22 | -9.28
2018-10-06 15:30 | 33.81 | -26.02
2018-10-06 16:00 | 41.71 | 38
2018-10-06 16:30 | 81.06 | 79.6
2018-10-06 17:00 | 102.69 | 101.39
2018-10-06 17:30 | 95.46 | 93.86
2018-10-06 18:00 | 81.67 | 79.32
2018-10-06 18:30 | 66.29 | 55.32
2018-10-06 19:00 | 65.76 | 54.96
2018-10-06 19:30 | 110.5 | 110.22
2018-10-06 20:00 | 115.97 | 115.97
2018-10-06 20:30 | 94.19 | 94.15
2018-10-06 21:00 | 64.76 | 64.63
2018-10-06 21:30 | 47.94 | 47.48
2018-10-06 22:00 | 38.23 | 37.16
2018-10-06 22:30 | 47.38 | 46.15
2018-10-06 23:00 | 81.93 | 80.92
2018-10-06 23:30 | 83.59 | 82.29
2018-10-07 | 63.48 | 61.35
2018-10-07 00:30 | 35.53 | 30.69
2018-10-07 01:00 | 19.42 | 16.77
2018-10-07 01:30 | 8.4 | 2.51
2018-10-07 02:00 | 14.13 | -12.69
2018-10-07 02:30 | 23.12 | -22.65
2018-10-07 03:00 | 22.79 | -22.24
2018-10-07 03:30 | 29.94 | -29.73
2018-10-07 04:00 | 25.49 | -24.93
2018-10-07 04:30 | 22.11 | -21.43
2018-10-07 05:00 | 19.46 | -18.6
2018-10-07 05:30 | 10.34 | -8.38
2018-10-07 06:00 | 6.54 | -2.53
2018-10-07 06:30 | 8.06 | 3.8
2018-10-07 07:00 | 6.23 | -0.01
2018-10-07 07:30 | 9.11 | 6.52
2018-10-07 08:00 | 11.59 | 8.7
2018-10-07 08:30 | 22.07 | 19.56
2018-10-07 09:00 | 18.96 | 15.15
2018-10-07 09:30 | 13.64 | 8.05
2018-10-07 10:00 | 16.37 | 10.65
2018-10-07 10:30 | 21.65 | 16.81
2018-10-07 11:00 | 16.44 | 11.49
2018-10-07 11:30 | 12.57 | 6.49
2018-10-07 12:00 | 10.82 | -4.06
2018-10-07 12:30 | 11.97 | -7.66
2018-10-07 13:00 | 14.35 | -11.65
2018-10-07 13:30 | 14.67 | -11.67
2018-10-07 14:00 | 12.71 | -8.67
2018-10-07 14:30 | 21.39 | 18.83
2018-10-07 15:00 | 30.97 | 28.89
2018-10-07 15:30 | 37.7 | 35.3
2018-10-07 16:00 | 73.46 | 72.03
2018-10-07 16:30 | 85.19 | 84.03
2018-10-07 17:00 | 86.54 | 85.31
2018-10-07 17:30 | 85.81 | 84.79
2018-10-07 18:00 | 109.52 | 109.45
2018-10-07 18:30 | 146.7 | 146.15
2018-10-07 19:00 | 160.38 | 159.82
2018-10-07 19:30 | 142.68 | 142.14
2018-10-07 20:00 | 137.52 | 137.09
2018-10-07 20:30 | 145.99 | 145.99
2018-10-07 21:00 | 132.65 | 132.2
2018-10-07 21:30 | 124.27 | 123.63
2018-10-07 22:00 | 119.27 | 118.35
2018-10-07 22:30 | 122.63 | 121.81
2018-10-07 23:00 | 124.32 | 123.42
2018-10-07 23:30 | 102.62 | 101.66
2018-10-08 | 59.65 | 58.18
2018-10-08 00:30 | 27.26 | 24.48
2018-10-08 01:00 | 10.59 | -4.99
2018-10-08 01:30 | 10.26 | -4.33
2018-10-08 02:00 | 11.57 | -7.42
2018-10-08 02:30 | 15.36 | -13.32
2018-10-08 03:00 | 17.26 | -15.65
2018-10-08 03:30 | 16.77 | -15.45
2018-10-08 04:00 | 9.88 | -7.45
2018-10-08 04:30 | 23.06 | -23.03
2018-10-08 05:00 | 9.34 | -8.94
2018-10-08 05:30 | 4.96 | 0.11
2018-10-08 06:00 | 14.7 | 12.23
2018-10-08 06:30 | 44.83 | 43.37
2018-10-08 07:00 | 54.53 | 53.78
2018-10-08 07:30 | 62.47 | 62.34
2018-10-08 08:00 | 47.84 | 47.6
2018-10-08 08:30 | 17.98 | 16.17
2018-10-08 09:00 | 112.73 | 112.5
2018-10-08 09:30 | 115.4 | 115.13
2018-10-08 10:00 | 135.14 | 134.33
2018-10-08 10:30 | 133.33 | 132.47
2018-10-08 11:00 | 133.36 | 132.61
2018-10-08 11:30 | 137.01 | 136.2
2018-10-08 12:00 | 134.22 | 133.47
2018-10-08 12:30 | 140.48 | 139.81
2018-10-08 13:00 | 148.75 | 148.14
2018-10-08 13:30 | 159.84 | 159.31
2018-10-08 14:00 | 165.21 | 164.76
2018-10-08 14:30 | 166.54 | 165.92
2018-10-08 15:00 | 153.06 | 152.02
2018-10-08 15:30 | 137.05 | 135.96
2018-10-08 16:00 | 100.68 | 100.68
2018-10-08 16:30 | 75.3 | 75.08
2018-10-08 17:00 | 87.49 | 87.3
2018-10-08 17:30 | 80.66 | 80.53
2018-10-08 18:00 | 97.74 | 97.64
2018-10-08 18:30 | 124.96 | 124.96
2018-10-08 19:00 | 136.47 | 136.47
2018-10-08 19:30 | 118.34 | 118.34
2018-10-08 20:00 | 114.09 | 114.08
2018-10-08 20:30 | 96.32 | 96.24
2018-10-08 21:00 | 90.98 | 90.86
2018-10-08 21:30 | 83.01 | 82.75
2018-10-08 22:00 | 44.6 | 43.7
2018-10-08 22:30 | 50.07 | 48.99
2018-10-08 23:00 | 63.41 | 62.4
2018-10-08 23:30 | 39.14 | 37.19
2018-10-09 | 24.32 | 19.83
2018-10-09 00:30 | 25.21 | 19.59
2018-10-09 01:00 | 18 | -10.49
2018-10-09 01:30 | 29.4 | -26.09
2018-10-09 02:00 | 15.26 | -9.29
2018-10-09 02:30 | 10.43 | 3.61
2018-10-09 03:00 | 19.08 | 15.51
2018-10-09 03:30 | 16.43 | 12.44
2018-10-09 04:00 | 10.87 | 7.44
2018-10-09 04:30 | 6.28 | 2.9
2018-10-09 05:00 | 8.75 | 1.89
2018-10-09 05:30 | 25.78 | 23.91
2018-10-09 06:00 | 57.76 | 56.86
2018-10-09 06:30 | 82.16 | 81.34
2018-10-09 07:00 | 62.53 | 61.42
2018-10-09 07:30 | 79.12 | 78.08
2018-10-09 08:00 | 121.46 | 121.07
2018-10-09 08:30 | 131.54 | 131.23
2018-10-09 09:00 | 122.15 | 121.11
2018-10-09 09:30 | 122.64 | 117.13
2018-10-09 10:00 | 131.63 | 126.2
2018-10-09 10:30 | 149.86 | 144.58
2018-10-09 11:00 | 148.17 | 142.75
2018-10-09 11:30 | 151.19 | 145.79
2018-10-09 12:00 | 150.17 | 144.94
2018-10-09 12:30 | 146.61 | 141.29
2018-10-09 13:00 | 138.19 | 132.45
2018-10-09 13:30 | 148.12 | 142.58
2018-10-09 14:00 | 159.6 | 154.41
2018-10-09 14:30 | 165.95 | 160.87
2018-10-09 15:00 | 143.03 | 138.72
2018-10-09 15:30 | 115.32 | 111.68
2018-10-09 16:00 | 133.74 | 131.04
2018-10-09 16:30 | 147.09 | 144.85
2018-10-09 17:00 | 161.68 | 159.84
2018-10-09 17:30 | 185.02 | 183.53
2018-10-09 18:00 | 180.63 | 179.03
2018-10-09 18:30 | 184.03 | 182.14
2018-10-09 19:00 | 201.31 | 199.69
2018-10-09 19:30 | 171.56 | 170.12
2018-10-09 20:00 | 164.33 | 163.18
2018-10-09 20:30 | 157.79 | 156.75
2018-10-09 21:00 | 117.28 | 115.84
2018-10-09 21:30 | 110.83 | 109.82
2018-10-09 22:00 | 117.92 | 117.28
2018-10-09 22:30 | 130.23 | 129.8
2018-10-09 23:00 | 129.41 | 129.11
2018-10-09 23:30 | 110.45 | 110.27
2018-10-10 | 65.01 | 64.96
2018-10-10 00:30 | 55.94 | 53.1
2018-10-10 01:00 | 35.09 | 29.88
2018-10-10 01:30 | 26.99 | 19.51
2018-10-10 02:00 | 31.19 | 26.41
2018-10-10 02:30 | 28.18 | 23.81
2018-10-10 03:00 | 58.01 | 55.84
2018-10-10 03:30 | 74.1 | 71.75
2018-10-10 04:00 | 80.4 | 78.58
2018-10-10 04:30 | 88.83 | 87.26
2018-10-10 05:00 | 67.43 | 64.82
2018-10-10 05:30 | 55.6 | 52.18
2018-10-10 06:00 | 61.74 | 59.22
2018-10-10 06:30 | 66.28 | 64.67
2018-10-10 07:00 | 28.08 | 27.34
2018-10-10 07:30 | 44.55 | 44.55
2018-10-10 08:00 | 122.63 | 122.59
2018-10-10 08:30 | 144.67 | 144.09
2018-10-10 09:00 | 146.38 | 144.7
2018-10-10 09:30 | 144.69 | 138.52
2018-10-10 10:00 | 147.33 | 140.82
2018-10-10 10:30 | 148.88 | 141.86
2018-10-10 11:00 | 149.31 | 143.22
2018-10-10 11:30 | 148.42 | 143.4
2018-10-10 12:00 | 151.4 | 146.35
2018-10-10 12:30 | 155 | 150.03
2018-10-10 13:00 | 157.77 | 152.94
2018-10-10 13:30 | 159.51 | 154.29
2018-10-10 14:00 | 161.14 | 158.19
2018-10-10 14:30 | 165.57 | 163.82
2018-10-10 15:00 | 170.74 | 168.43
2018-10-10 15:30 | 179.2 | 177.55
2018-10-10 16:00 | 176.23 | 174.77
2018-10-10 16:30 | 181.14 | 179.94
2018-10-10 17:00 | 209.44 | 208.51
2018-10-10 17:30 | 215.74 | 215.15
2018-10-10 18:00 | 211.37 | 210.88
2018-10-10 18:30 | 210.23 | 209.43
2018-10-10 19:00 | 213.91 | 212.6
2018-10-10 19:30 | 192.49 | 192.33
2018-10-10 20:00 | 171.5 | 171.39
2018-10-10 20:30 | 167.4 | 167.31
2018-10-10 21:00 | 164.65 | 164.63
2018-10-10 21:30 | 156.35 | 156.26
2018-10-10 22:00 | 155.48 | 155.28
2018-10-10 22:30 | 147.14 | 146.9
2018-10-10 23:00 | 155.05 | 154.72
2018-10-10 23:30 | 109.5 | 108.91
2018-10-11 | 65.77 | 64.32
2018-10-11 00:30 | 66.67 | 64.56
2018-10-11 01:00 | 60.44 | 57.38
2018-10-11 01:30 | 56.78 | 53.39
2018-10-11 02:00 | 62.23 | 59
2018-10-11 02:30 | 72.48 | 70.01
2018-10-11 03:00 | 85.48 | 83.65
2018-10-11 03:30 | 93.15 | 91.6
2018-10-11 04:00 | 94.46 | 93.19
2018-10-11 04:30 | 71.67 | 69.79
2018-10-11 05:00 | 67.83 | 65.57
2018-10-11 05:30 | 45.22 | 41.53
2018-10-11 06:00 | 40.79 | 36.82
2018-10-11 06:30 | 45.59 | 43.02
2018-10-11 07:00 | 34.66 | 34.43
2018-10-11 07:30 | 49.16 | 49.16
2018-10-11 08:00 | 67.2 | 67.18
2018-10-11 08:30 | 99.2 | 99.1
2018-10-11 09:00 | 81.31 | 81.06
2018-10-11 09:30 | 81.04 | 80.61
2018-10-11 10:00 | 81.3 | 67.58
2018-10-11 10:30 | 94.3 | 70.4
2018-10-11 11:00 | 108.86 | 88.73
2018-10-11 11:30 | 136.27 | 121.06
2018-10-11 12:00 | 146.76 | 133.54
2018-10-11 12:30 | 172.07 | 167.28
2018-10-11 13:00 | 185.32 | 181.16
2018-10-11 13:30 | 193.03 | 188.89
2018-10-11 14:00 | 177.01 | 174.13
2018-10-11 14:30 | 160.23 | 160.18
2018-10-11 15:00 | 162.3 | 162.21
2018-10-11 15:30 | 160 | 159.95
2018-10-11 16:00 | 167.18 | 167.16
2018-10-11 16:30 | 169.94 | 169.94
2018-10-11 17:00 | 148.47 | 148.46
2018-10-11 17:30 | 142.55 | 142.53
2018-10-11 18:00 | 107.51 | 106.71
2018-10-11 18:30 | 86.48 | 79.43
2018-10-11 19:00 | 149.53 | 138.96
2018-10-11 19:30 | 73.49 | 47.65
2018-10-11 20:00 | 57.43 | 13.26
2018-10-11 20:30 | 48.66 | 13.92
2018-10-11 21:00 | 122.25 | 122.04
2018-10-11 21:30 | 114.8 | 114.62
2018-10-11 22:00 | 138.21 | 137.95
2018-10-11 22:30 | 150.62 | 150.27
2018-10-11 23:00 | 152.39 | 151.92
2018-10-11 23:30 | 125.74 | 124.85
2018-10-12 | 85.12 | 83.48
2018-10-12 00:30 | 72.93 | 70.69
2018-10-12 01:00 | 87.7 | 85.61
2018-10-12 01:30 | 81.36 | 78.81
2018-10-12 02:00 | 73.44 | 70.54
2018-10-12 02:30 | 70.72 | 67.56
2018-10-12 03:00 | 74.77 | 71.45
2018-10-12 03:30 | 82.62 | 79.96
2018-10-12 04:00 | 76.36 | 73.78
2018-10-12 04:30 | 95.66 | 93.85
2018-10-12 05:00 | 96.11 | 94.3
2018-10-12 05:30 | 74.47 | 72.86
2018-10-12 06:00 | 50.54 | 48.18
2018-10-12 06:30 | 49.47 | 48.35
2018-10-12 07:00 | 56.97 | 56.72
2018-10-12 07:30 | 101.78 | 101.77
2018-10-12 08:00 | 119.07 | 117.73
2018-10-12 08:30 | 135 | 131.98
2018-10-12 09:00 | 144.45 | 141.03
2018-10-12 09:30 | 143.15 | 139.43
2018-10-12 10:00 | 147.84 | 144.1
2018-10-12 10:30 | 119.54 | 114.75
2018-10-12 11:00 | 96.86 | 89.59
2018-10-12 11:30 | 119.86 | 108.5
2018-10-12 12:00 | 112.6 | 101.9
2018-10-12 12:30 | 147.6 | 139.66
2018-10-12 13:00 | 156.84 | 149.22
2018-10-12 13:30 | 164.56 | 157.52
2018-10-12 14:00 | 121.81 | 113.09
2018-10-12 14:30 | 128.53 | 120.78
2018-10-12 15:00 | 126.32 | 118.82
2018-10-12 15:30 | 135.04 | 128.74
2018-10-12 16:00 | 135.31 | 129.63
2018-10-12 16:30 | 141.15 | 135.94
2018-10-12 17:00 | 151.82 | 146.79
2018-10-12 17:30 | 159.9 | 155.16
2018-10-12 18:00 | 150.02 | 143.72
2018-10-12 18:30 | 167.21 | 157.44
2018-10-12 19:00 | 172.16 | 163.09
2018-10-12 19:30 | 149.89 | 142.05
2018-10-12 20:00 | 174.57 | 172.13
2018-10-12 20:30 | 182.28 | 182.26
2018-10-12 21:00 | 161.17 | 161.04
2018-10-12 21:30 | 162.53 | 162.28
2018-10-12 22:00 | 126.85 | 126.31
2018-10-12 22:30 | 134.29 | 133.68
2018-10-12 23:00 | 117.14 | 116.34
2018-10-12 23:30 | 99.87 | 98.67
2018-10-13 | 74.44 | 72.45
2018-10-13 00:30 | 60.43 | 57.73
2018-10-13 01:00 | 63.17 | 60.35
2018-10-13 01:30 | 68.55 | 65.55
2018-10-13 02:00 | 56.78 | 54.1
2018-10-13 02:30 | 45.19 | 42.06
2018-10-13 03:00 | 37.9 | 34.15
2018-10-13 03:30 | 38.83 | 35.26
2018-10-13 04:00 | 50.33 | 48.35
2018-10-13 04:30 | 46.45 | 44.1
2018-10-13 05:00 | 58.56 | 56.84
2018-10-13 05:30 | 63.51 | 61.53
2018-10-13 06:00 | 63.87 | 61.3
2018-10-13 06:30 | 18.89 | 12.01
2018-10-13 07:00 | 12.43 | -5.7
2018-10-13 07:30 | 10.8 | -5.96
2018-10-13 08:00 | 91.38 | 91.01
2018-10-13 08:30 | 112.09 | 111.97
2018-10-13 09:00 | 157.77 | 157.74
2018-10-13 09:30 | 173.58 | 173.58
2018-10-13 10:00 | 176.6 | 176.6
2018-10-13 10:30 | 162.54 | 162.54
2018-10-13 11:00 | 167.74 | 167.74
2018-10-13 11:30 | 148.04 | 148.04
2018-10-13 12:00 | 116.37 | 116.35
2018-10-13 12:30 | 127.42 | 127.41
2018-10-13 13:00 | 129.53 | 129.5
2018-10-13 13:30 | 141.94 | 141.9
2018-10-13 14:00 | 139.15 | 139.1
2018-10-13 14:30 | 138.15 | 138.09
2018-10-13 15:00 | 138.02 | 137.96
2018-10-13 15:30 | 143.11 | 143.01
2018-10-13 16:00 | 128.62 | 128.48
2018-10-13 16:30 | 132.84 | 132.73
2018-10-13 17:00 | 179.89 | 179.85
2018-10-13 17:30 | 164.57 | 164.53
2018-10-13 18:00 | 148.55 | 148.39
2018-10-13 18:30 | 155.66 | 154.28
2018-10-13 19:00 | 168.17 | 160.53
2018-10-13 19:30 | 166.47 | 161.02
2018-10-13 20:00 | 177.25 | 175.23
2018-10-13 20:30 | 154.07 | 152.16
2018-10-13 21:00 | 98.66 | 98.6
2018-10-13 21:30 | 99.56 | 98.97
2018-10-13 22:00 | 84.82 | 83.86
2018-10-13 22:30 | 91.75 | 90.63
2018-10-13 23:00 | 113.21 | 112.15
2018-10-13 23:30 | 101.54 | 100.09
2018-10-14 | 56.01 | 53.04
2018-10-14 00:30 | 50.33 | 46.41
2018-10-14 01:00 | 25.67 | 15.92
2018-10-14 01:30 | 19.81 | 13.55
2018-10-14 02:00 | 16.48 | 10.54
2018-10-14 02:30 | 16.62 | 10.8
2018-10-14 03:00 | 32.45 | 29.36
2018-10-14 03:30 | 15.57 | 9.29
2018-10-14 04:00 | 16.07 | 10.41
2018-10-14 04:30 | 32.81 | 29.88
2018-10-14 05:00 | 43.03 | 40.68
2018-10-14 05:30 | 24.48 | 21
2018-10-14 06:00 | 14.67 | 8.99
2018-10-14 06:30 | 14.15 | 8.34
2018-10-14 07:00 | 14.7 | 9.69
2018-10-14 07:30 | 22.13 | 20.33
2018-10-14 08:00 | 30.2 | 29.27
2018-10-14 08:30 | 53.23 | 53.03
2018-10-14 09:00 | 67.32 | 67.25
2018-10-14 09:30 | 84.2 | 84.2
2018-10-14 10:00 | 96.03 | 95.94
2018-10-14 10:30 | 110.57 | 108.27
2018-10-14 11:00 | 87.29 | 84.46
2018-10-14 11:30 | 91.45 | 88.84
2018-10-14 12:00 | 107.22 | 105.08
2018-10-14 12:30 | 105.57 | 103.48
2018-10-14 13:00 | 102.19 | 100.19
2018-10-14 13:30 | 96.33 | 94.12
2018-10-14 14:00 | 94.07 | 91.67
2018-10-14 14:30 | 114.65 | 112.57
2018-10-14 15:00 | 101.38 | 99.04
2018-10-14 15:30 | 117.74 | 115.7
2018-10-14 16:00 | 127.3 | 125.62
2018-10-14 16:30 | 130.31 | 128.51
2018-10-14 17:00 | 116.32 | 111.72
2018-10-14 17:30 | 133.22 | 128.27
2018-10-14 18:00 | 150.9 | 146.02
2018-10-14 18:30 | 153.23 | 148.59
2018-10-14 19:00 | 143.13 | 138.46
2018-10-14 19:30 | 130.31 | 125.74
2018-10-14 20:00 | 145.02 | 141.38
2018-10-14 20:30 | 148.65 | 148.56
2018-10-14 21:00 | 152.43 | 152.34
2018-10-14 21:30 | 141.69 | 141.57
2018-10-14 22:00 | 111.69 | 111.47
2018-10-14 22:30 | 113.99 | 113.84
2018-10-14 23:00 | 107.32 | 107.11
2018-10-14 23:30 | 71.83 | 71.74
2018-10-15 | 32.26 | 32.22
2018-10-15 00:30 | 33.66 | 33.62
2018-10-15 01:00 | 24.84 | 24.83
2018-10-15 01:30 | 16.11 | 16.1
2018-10-15 02:00 | 9.27 | 7.61
2018-10-15 02:30 | 16.02 | 14.19
2018-10-15 03:00 | 27.82 | 26.07
2018-10-15 03:30 | 30 | 28.55
2018-10-15 04:00 | 31.31 | 30.07
2018-10-15 04:30 | 35.27 | 34.62
2018-10-15 05:00 | 45.68 | 45.21
2018-10-15 05:30 | 33.96 | 33.66
2018-10-15 06:00 | 22.9 | 22.88
2018-10-15 06:30 | 62.15 | 62.12
2018-10-15 07:00 | 77.8 | 77.77
2018-10-15 07:30 | 124.44 | 124.34
2018-10-15 08:00 | 150.07 | 149.82
2018-10-15 08:30 | 144.57 | 144.07
2018-10-15 09:00 | 137.19 | 136.32
2018-10-15 09:30 | 132.12 | 130.09
2018-10-15 10:00 | 137.02 | 135.39
2018-10-15 10:30 | 144.75 | 142.9
2018-10-15 11:00 | 133.69 | 132.57
2018-10-15 11:30 | 133.22 | 132.66
2018-10-15 12:00 | 129.71 | 129.33
2018-10-15 12:30 | 114.01 | 113.83
2018-10-15 13:00 | 93.11 | 92.93
2018-10-15 13:30 | 85.11 | 84.97
2018-10-15 14:00 | 78.69 | 78.59
2018-10-15 14:30 | 91.96 | 91.91
2018-10-15 15:00 | 90.35 | 90.3
2018-10-15 15:30 | 104.69 | 104.68
2018-10-15 16:00 | 107.49 | 107.49
2018-10-15 16:30 | 127.38 | 127.37
2018-10-15 17:00 | 127.31 | 127.27
2018-10-15 17:30 | 154.65 | 154.57
2018-10-15 18:00 | 160.79 | 160.6
2018-10-15 18:30 | 185.04 | 184.62
2018-10-15 19:00 | 202.35 | 201.91
2018-10-15 19:30 | 183.89 | 183.83
2018-10-15 20:00 | 157.31 | 157.31
2018-10-15 20:30 | 167.25 | 163.66
2018-10-15 21:00 | 141.49 | 137.23
2018-10-15 21:30 | 137.67 | 134.12
2018-10-15 22:00 | 116.56 | 113.24
2018-10-15 22:30 | 103.88 | 100.24
2018-10-15 23:00 | 109.75 | 106.39
2018-10-15 23:30 | 113.76 | 110.9
2018-10-16 | 58.42 | 53.32
2018-10-16 00:30 | 43.8 | 42.52
2018-10-16 01:00 | 33.94 | 33.91
2018-10-16 01:30 | 55.99 | 55.97
2018-10-16 02:00 | 44.62 | 44.61
2018-10-16 02:30 | 52.82 | 52.8
2018-10-16 03:00 | 59.05 | 59.04
2018-10-16 03:30 | 61.75 | 61.74
2018-10-16 04:00 | 33.71 | 33.59
2018-10-16 04:30 | 27.28 | 26.99
2018-10-16 05:00 | 42.2 | 41.94
2018-10-16 05:30 | 26.19 | 25.47
2018-10-16 06:00 | 24.22 | 22.47
2018-10-16 06:30 | 47.75 | 45.82
2018-10-16 07:00 | 70.25 | 68.1
2018-10-16 07:30 | 95.72 | 86.8
2018-10-16 08:00 | 100.41 | 90.24
2018-10-16 08:30 | 84.29 | 70.57
2018-10-16 09:00 | 76.06 | 59.33
2018-10-16 09:30 | 69.96 | 49.66
2018-10-16 10:00 | 73.52 | 52.79
2018-10-16 10:30 | 74.04 | 52.8
2018-10-16 11:00 | 69.43 | 44.76
2018-10-16 11:30 | 67.21 | 41.1
2018-10-16 12:00 | 71.25 | 47.05
2018-10-16 12:30 | 78.19 | 57.58
2018-10-16 13:00 | 78.06 | 59.17
2018-10-16 13:30 | 59.33 | 32.74
2018-10-16 14:00 | 55.11 | 23.89
2018-10-16 14:30 | 57.81 | 30.28
2018-10-16 15:00 | 64.11 | 42.79
2018-10-16 15:30 | 91.11 | 78.71
2018-10-16 16:00 | 91.21 | 80.35
2018-10-16 16:30 | 81.45 | 70.14
2018-10-16 17:00 | 108.25 | 100.58
2018-10-16 17:30 | 125.12 | 118.74
2018-10-16 18:00 | 143.61 | 138.2
2018-10-16 18:30 | 167.23 | 162.17
2018-10-16 19:00 | 200.4 | 196.25
2018-10-16 19:30 | 174.04 | 170.03
2018-10-16 20:00 | 149.73 | 145.49
2018-10-16 20:30 | 128.11 | 123.99
2018-10-16 21:00 | 115.04 | 111.51
2018-10-16 21:30 | 113.76 | 112.31
2018-10-16 22:00 | 95.26 | 94.59
2018-10-16 22:30 | 90.5 | 89.65
2018-10-16 23:00 | 70.63 | 69.36
2018-10-16 23:30 | 47.37 | 45.5
2018-10-17 | 14.47 | -5.18
2018-10-17 00:30 | 16.19 | -4.42
2018-10-17 01:00 | 18.73 | -8.47
2018-10-17 01:30 | 17.83 | -6.53
2018-10-17 02:00 | 16.98 | -0.39
2018-10-17 02:30 | 18.45 | 6.92
2018-10-17 03:00 | 26.2 | 15.12
2018-10-17 03:30 | 20.61 | 0.84
2018-10-17 04:00 | 19.45 | -7.28
2018-10-17 04:30 | 18.43 | -7.28
2018-10-17 05:00 | 18.71 | 2.08
2018-10-17 05:30 | 18.2 | 0.69
2018-10-17 06:00 | 17.98 | 16.35
2018-10-17 06:30 | 13.04 | 12.14
2018-10-17 07:00 | 5.96 | 5.56
2018-10-17 07:30 | 40.99 | 40.56
2018-10-17 08:00 | 43.89 | 43.83
2018-10-17 08:30 | 36.14 | 36.05
2018-10-17 09:00 | 39.97 | 39.66
2018-10-17 09:30 | 26.23 | 25.9
2018-10-17 10:00 | 20.22 | 19.58
2018-10-17 10:30 | 13.9 | 12.5
2018-10-17 11:00 | 16.34 | 15.65
2018-10-17 11:30 | 23.95 | 23.33
2018-10-17 12:00 | 10.39 | 9.04
2018-10-17 12:30 | 9.13 | 7.54
2018-10-17 13:00 | 8.43 | 6.83
2018-10-17 13:30 | 11.36 | 9.54
2018-10-17 14:00 | 7.27 | 1.21
2018-10-17 14:30 | 23.83 | -21.29
2018-10-17 15:00 | 7.81 | 1.96
2018-10-17 15:30 | 47.29 | 47.29
2018-10-17 16:00 | 43.36 | 43.36
2018-10-17 16:30 | 43.17 | 43.17
2018-10-17 17:00 | 72.99 | 72.98
2018-10-17 17:30 | 89.27 | 89.27
2018-10-17 18:00 | 76.75 | 76.73
2018-10-17 18:30 | 94.93 | 94.89
2018-10-17 19:00 | 106.48 | 106.45
2018-10-17 19:30 | 104.79 | 104.79
2018-10-17 20:00 | 91.64 | 90.64
2018-10-17 20:30 | 91.44 | 88.46
2018-10-17 21:00 | 68.32 | 64.5
2018-10-17 21:30 | 53.37 | 49.72
2018-10-17 22:00 | 25.43 | 19.05
2018-10-17 22:30 | 28.56 | 24.97
2018-10-17 23:00 | 26.35 | 23.85
2018-10-17 23:30 | 11.19 | -4.36
2018-10-18 | 36.37 | -35.11
2018-10-18 00:30 | 42.29 | -42.29
2018-10-18 01:00 | 42.13 | -40.39
2018-10-18 01:30 | 38.28 | -36.07
2018-10-18 02:00 | 43.4 | -41.12
2018-10-18 02:30 | 62.56 | -61.53
2018-10-18 03:00 | 62.73 | -61.67
2018-10-18 03:30 | 63.19 | -62.07
2018-10-18 04:00 | 62.85 | -61.77
2018-10-18 04:30 | 62.56 | -61.59
2018-10-18 05:00 | 45.98 | -44.77
2018-10-18 05:30 | 50.31 | -49.54
2018-10-18 06:00 | 50.43 | -50.04
2018-10-18 06:30 | 42.75 | -42.71
2018-10-18 07:00 | 33.78 | -32.58
2018-10-18 07:30 | 12.11 | -10.29
2018-10-18 08:00 | 14.93 | -13.22
2018-10-18 08:30 | 15.29 | -11.51
2018-10-18 09:00 | 20.54 | -16.63
2018-10-18 09:30 | 24.5 | -20.5
2018-10-18 10:00 | 34.24 | -28.93
2018-10-18 10:30 | 33.75 | -28.34
2018-10-18 11:00 | 31.91 | -26.06
2018-10-18 11:30 | 31.01 | -25.11
2018-10-18 12:00 | 33.32 | -27.9
2018-10-18 12:30 | 21.45 | -15.57
2018-10-18 13:00 | 12.58 | -4.77
2018-10-18 13:30 | 26.12 | -20.38
2018-10-18 14:00 | 25.35 | -19.17
2018-10-18 14:30 | 25.43 | -19.15
2018-10-18 15:00 | 25.13 | -15.21
2018-10-18 15:30 | 22.74 | -7.98
2018-10-18 16:00 | 25.63 | -15.48
2018-10-18 16:30 | 23.08 | -14.48
2018-10-18 17:00 | 37.6 | 35.2
2018-10-18 17:30 | 18 | 13.22
2018-10-18 18:00 | 15.84 | -5.92
2018-10-18 18:30 | 33.02 | 9.4
2018-10-18 19:00 | 81.46 | 77.55
2018-10-18 19:30 | 28.07 | 14.34
2018-10-18 20:00 | 76.13 | 75.63
2018-10-18 20:30 | 50.34 | 45.37
2018-10-18 21:00 | 37.07 | 32.36
2018-10-18 21:30 | 20.92 | -4.56
2018-10-18 22:00 | 13.26 | -2.69
2018-10-18 22:30 | 16.02 | 15.76
2018-10-18 23:00 | 10.88 | 9.78
2018-10-18 23:30 | 13.07 | -11.34
2018-10-19 | 40.96 | -40.42
2018-10-19 00:30 | 45.95 | -45.26
2018-10-19 01:00 | 47.95 | -46.6
2018-10-19 01:30 | 46.1 | -44.53
2018-10-19 02:00 | 58.57 | -57.65
2018-10-19 02:30 | 57.53 | -56.6
2018-10-19 03:00 | 56.42 | -55.14
2018-10-19 03:30 | 51.86 | -50.45
2018-10-19 04:00 | 53.24 | -51.96
2018-10-19 04:30 | 42.45 | -40.66
2018-10-19 05:00 | 43.38 | -41.77
2018-10-19 05:30 | 41.91 | -40.37
2018-10-19 06:00 | 91 | 89.82
2018-10-19 06:30 | 111.52 | 111.36
2018-10-19 07:00 | 117.86 | 117.83
2018-10-19 07:30 | 131.05 | 130.6
2018-10-19 08:00 | 134.1 | 133.53
2018-10-19 08:30 | 129.82 | 129.26
2018-10-19 09:00 | 131.34 | 130.62
2018-10-19 09:30 | 120.48 | 119.77
2018-10-19 10:00 | 121.02 | 120.32
2018-10-19 10:30 | 124.38 | 123.47
2018-10-19 11:00 | 129.07 | 128.16
2018-10-19 11:30 | 137.54 | 136.37
2018-10-19 12:00 | 137.77 | 135.7
2018-10-19 12:30 | 134.84 | 132.75
2018-10-19 13:00 | 86.27 | 84.76
2018-10-19 13:30 | 19.82 | 9.42
2018-10-19 14:00 | 30.86 | 24.03
2018-10-19 14:30 | 52.28 | 51.07
2018-10-19 15:00 | 23.09 | 23.06
2018-10-19 15:30 | 32.41 | 32.33
2018-10-19 16:00 | 31.16 | 31.03
2018-10-19 16:30 | 17.77 | -16.14
2018-10-19 17:00 | 50.96 | 50.96
2018-10-19 17:30 | 94.45 | 94.32
2018-10-19 18:00 | 86.92 | 86.82
2018-10-19 18:30 | 105.9 | 105.88
2018-10-19 19:00 | 119.54 | 119.53
2018-10-19 19:30 | 115.83 | 115.76
2018-10-19 20:00 | 117.59 | 117.59
2018-10-19 20:30 | 130.3 | 130.29
2018-10-19 21:00 | 119.09 | 119.09
2018-10-19 21:30 | 98.22 | 98.2
2018-10-19 22:00 | 89.11 | 88.94
2018-10-19 22:30 | 94.02 | 93.72
2018-10-19 23:00 | 110.08 | 109.67
2018-10-19 23:30 | 89.16 | 88.34
2018-10-20 | 44.94 | 42.74
2018-10-20 00:30 | 62.52 | 60.42
2018-10-20 01:00 | 64.45 | 62.3
2018-10-20 01:30 | 68.48 | 66.64
2018-10-20 02:00 | 73.37 | 71.68
2018-10-20 02:30 | 75.39 | 73.28
2018-10-20 03:00 | 74.28 | 73.74
2018-10-20 03:30 | 80.09 | 80.07
2018-10-20 04:00 | 82.37 | 82.35
2018-10-20 04:30 | 72.76 | 72.74
2018-10-20 05:00 | 66.72 | 66.7
2018-10-20 05:30 | 71.42 | 71.35
2018-10-20 06:00 | 38.47 | 38.34
2018-10-20 06:30 | 10.7 | 9.74
2018-10-20 07:00 | 26.49 | -23.76
2018-10-20 07:30 | 35.92 | -33.19
2018-10-20 08:00 | 28.64 | -28.63
2018-10-20 08:30 | 13.21 | -12.79
2018-10-20 09:00 | 5.54 | -1.26
2018-10-20 09:30 | 7.74 | -6.65
2018-10-20 10:00 | 21.72 | -20.32
2018-10-20 10:30 | 28.86 | -28.65
2018-10-20 11:00 | 33.12 | -32.92
2018-10-20 11:30 | 25.8 | -25.53
2018-10-20 12:00 | 3.66 | -0.46
2018-10-20 12:30 | 10.18 | -6.96
2018-10-20 13:00 | 8.99 | 3.49
2018-10-20 13:30 | 11.17 | 7.04
2018-10-20 14:00 | 31.46 | 29.98
2018-10-20 14:30 | 45.74 | 44.36
2018-10-20 15:00 | 60.67 | 59.41
2018-10-20 15:30 | 54.1 | 52.92
2018-10-20 16:00 | 63.22 | 61.91
2018-10-20 16:30 | 82.48 | 81.46
2018-10-20 17:00 | 103.31 | 102.5
2018-10-20 17:30 | 108.82 | 108.17
2018-10-20 18:00 | 129.46 | 129.06
2018-10-20 18:30 | 130.41 | 130.37
2018-10-20 19:00 | 135.68 | 135.48
2018-10-20 19:30 | 151.95 | 151.93
2018-10-20 20:00 | 69.46 | 68.42
2018-10-20 20:30 | 34.41 | 30.25
2018-10-20 21:00 | 32.56 | 32.43
2018-10-20 21:30 | 74.59 | 73.7
2018-10-20 22:00 | 92.69 | 91.62
2018-10-20 22:30 | 70.53 | 69.5
2018-10-20 23:00 | 70.09 | 69.01
2018-10-20 23:30 | 53.88 | 52.78
2018-10-21 | 42.74 | 41.28
2018-10-21 00:30 | 52.25 | 50.67
2018-10-21 01:00 | 51.55 | 50
2018-10-21 01:30 | 43.14 | 40.67
2018-10-21 02:00 | 33.07 | 32.87
2018-10-21 02:30 | 47.99 | 47.83
2018-10-21 03:00 | 38.24 | 38.08
2018-10-21 03:30 | 33.36 | 33.23
2018-10-21 04:00 | 37.77 | 37.66
2018-10-21 04:30 | 41.08 | 40.95
2018-10-21 05:00 | 33.53 | 33.4
2018-10-21 05:30 | 22.42 | 22.07
2018-10-21 06:00 | 17.46 | 16.97
2018-10-21 06:30 | 24.48 | 24.01
2018-10-21 07:00 | 12.46 | 11.8
2018-10-21 07:30 | 15.88 | 15.01
2018-10-21 08:00 | 15.35 | 14.67
2018-10-21 08:30 | 26.02 | 25.95
2018-10-21 09:00 | 47.66 | 46.96
2018-10-21 09:30 | 10.86 | 10.83
2018-10-21 10:00 | 18.54 | -17.7
2018-10-21 10:30 | 37.99 | -37.95
2018-10-21 11:00 | 18.44 | -15
2018-10-21 11:30 | 19.54 | 18.62
2018-10-21 12:00 | 53.82 | 53.62
2018-10-21 12:30 | 83.52 | 83.44
2018-10-21 13:00 | 66.88 | 66.83
2018-10-21 13:30 | 67.57 | 67.54
2018-10-21 14:00 | 114.22 | 114.21
2018-10-21 14:30 | 144.17 | 144.09
2018-10-21 15:00 | 134.79 | 134.68
2018-10-21 15:30 | 138.56 | 138.44
2018-10-21 16:00 | 117.31 | 117.18
2018-10-21 16:30 | 136.75 | 136.69
2018-10-21 17:00 | 127.25 | 127.21
2018-10-21 17:30 | 122.24 | 122.23
2018-10-21 18:00 | 124.83 | 124.83
2018-10-21 18:30 | 146.35 | 146.34
2018-10-21 19:00 | 149.82 | 149.81
2018-10-21 19:30 | 135.05 | 135.05
2018-10-21 20:00 | 105.13 | 105.1
2018-10-21 20:30 | 127.81 | 127.72
2018-10-21 21:00 | 112.06 | 111.83
2018-10-21 21:30 | 111.79 | 111.4
2018-10-21 22:00 | 103.85 | 103.15
2018-10-21 22:30 | 115.57 | 114.58
2018-10-21 23:00 | 134.99 | 134.2
2018-10-21 23:30 | 112.01 | 111.18
2018-10-22 | 69.15 | 67.97
2018-10-22 00:30 | 52.39 | 51.1
2018-10-22 01:00 | 16.76 | 14.76
2018-10-22 01:30 | 11.36 | 8
2018-10-22 02:00 | 13.93 | 10.17
2018-10-22 02:30 | 25.59 | 23.85
2018-10-22 03:00 | 63.05 | 62.97
2018-10-22 03:30 | 87.67 | 87.64
2018-10-22 04:00 | 94.31 | 94.1
2018-10-22 04:30 | 98.37 | 97.39
2018-10-22 05:00 | 90.83 | 89.46
2018-10-22 05:30 | 102.88 | 100.25
2018-10-22 06:00 | 112.45 | 110.47
2018-10-22 06:30 | 100.54 | 100.43
2018-10-22 07:00 | 81.73 | 81.4
2018-10-22 07:30 | 109.37 | 105.28
2018-10-22 08:00 | 123.93 | 118.66
2018-10-22 08:30 | 141.76 | 130.55
2018-10-22 09:00 | 146.49 | 130.11
2018-10-22 09:30 | 160.56 | 129.18
2018-10-22 10:00 | 145.79 | 109.2
2018-10-22 10:30 | 123.39 | 101.9
2018-10-22 11:00 | 105.18 | 101.83
2018-10-22 11:30 | 136.76 | 131.68
2018-10-22 12:00 | 149.33 | 141.83
2018-10-22 12:30 | 157.17 | 150.28
2018-10-22 13:00 | 163.1 | 156.26
2018-10-22 13:30 | 162.54 | 155.38
2018-10-22 14:00 | 156.94 | 150.02
2018-10-22 14:30 | 172.37 | 166.18
2018-10-22 15:00 | 180.51 | 174.73
2018-10-22 15:30 | 185.18 | 179.62
2018-10-22 16:00 | 190.63 | 185.53
2018-10-22 16:30 | 195.42 | 190.94
2018-10-22 17:00 | 205.38 | 201.49
2018-10-22 17:30 | 204.87 | 201.29
2018-10-22 18:00 | 208.51 | 205.36
2018-10-22 18:30 | 216.74 | 213.38
2018-10-22 19:00 | 218.89 | 215.4
2018-10-22 19:30 | 213.8 | 210.86
2018-10-22 20:00 | 198.19 | 195.5
2018-10-22 20:30 | 185.25 | 183.5
2018-10-22 21:00 | 162.44 | 162.28
2018-10-22 21:30 | 156.57 | 155.4
2018-10-22 22:00 | 146.99 | 145.53
2018-10-22 22:30 | 158.34 | 156.95
2018-10-22 23:00 | 151.73 | 150.34
2018-10-22 23:30 | 139.3 | 138.11
2018-10-23 | 110.44 | 108.95
2018-10-23 00:30 | 87.57 | 85.82
2018-10-23 01:00 | 63.06 | 60.6
2018-10-23 01:30 | 55.75 | 53.12
2018-10-23 02:00 | 44.68 | 41.26
2018-10-23 02:30 | 50.47 | 47.61
2018-10-23 03:00 | 44.39 | 41.16
2018-10-23 03:30 | 53.47 | 50.96
2018-10-23 04:00 | 56.06 | 54.11
2018-10-23 04:30 | 81.86 | 80.7
2018-10-23 05:00 | 112.57 | 111.79
2018-10-23 05:30 | 107.22 | 106.31
2018-10-23 06:00 | 90 | 88.82
2018-10-23 06:30 | 91.91 | 90.45
2018-10-23 07:00 | 85.43 | 84.58
2018-10-23 07:30 | 111.85 | 111.48
2018-10-23 08:00 | 131.19 | 131.01
2018-10-23 08:30 | 135.84 | 135.74
2018-10-23 09:00 | 139.41 | 139.39
2018-10-23 09:30 | 128.45 | 128.44
2018-10-23 10:00 | 113.93 | 113.93
2018-10-23 10:30 | 123.6 | 123.6
2018-10-23 11:00 | 135.33 | 135.33
2018-10-23 11:30 | 126.83 | 126.83
2018-10-23 12:00 | 123.54 | 123.54
2018-10-23 12:30 | 132.63 | 132.63
2018-10-23 13:00 | 130.2 | 130.2
2018-10-23 13:30 | 137.52 | 137.52
2018-10-23 14:00 | 150.36 | 150.36
2018-10-23 14:30 | 165.21 | 165.21
2018-10-23 15:00 | 168.02 | 168.02
2018-10-23 15:30 | 174.91 | 174.91
2018-10-23 16:00 | 166.52 | 166.51
2018-10-23 16:30 | 184.56 | 184.55
2018-10-23 17:00 | 195.73 | 195.71
2018-10-23 17:30 | 207.43 | 207.43
2018-10-23 18:00 | 210.69 | 210.69
2018-10-23 18:30 | 217.21 | 217.18
2018-10-23 19:00 | 203.43 | 203.41
2018-10-23 19:30 | 150.43 | 150.39
2018-10-23 20:00 | 170.24 | 170.19
2018-10-23 20:30 | 174 | 173.92
2018-10-23 21:00 | 173.81 | 173.74
2018-10-23 21:30 | 134.23 | 134.22
2018-10-23 22:00 | 132.7 | 132.59
2018-10-23 22:30 | 129.26 | 129.03
2018-10-23 23:00 | 122.3 | 121.92
2018-10-23 23:30 | 115.38 | 114.77
2018-10-24 | 93.25 | 92.03
2018-10-24 00:30 | 53.12 | 50.76
2018-10-24 01:00 | 37.84 | 34.17
2018-10-24 01:30 | 36.39 | 33.19
2018-10-24 02:00 | 25.52 | 21.4
2018-10-24 02:30 | 19.11 | 14.16
2018-10-24 03:00 | 21.62 | 17.11
2018-10-24 03:30 | 25.54 | 22.23
2018-10-24 04:00 | 26.82 | 24.41
2018-10-24 04:30 | 37.36 | 35.62
2018-10-24 05:00 | 45.81 | 44.1
2018-10-24 05:30 | 53.27 | 51.78
2018-10-24 06:00 | 18.35 | 14.32
2018-10-24 06:30 | 36.41 | 36.3
2018-10-24 07:00 | 41.82 | 41
2018-10-24 07:30 | 52.81 | 51.92
2018-10-24 08:00 | 58.58 | 56.9
2018-10-24 08:30 | 62.9 | 57.19
2018-10-24 09:00 | 80.39 | 56.41
2018-10-24 09:30 | 93.87 | 55.68
2018-10-24 10:00 | 96.09 | 56.35
2018-10-24 10:30 | 100.05 | 59.61
2018-10-24 11:00 | 99.85 | 63.21
2018-10-24 11:30 | 107.01 | 84.03
2018-10-24 12:00 | 104.2 | 80.4
2018-10-24 12:30 | 125.75 | 106.79
2018-10-24 13:00 | 129.85 | 111.57
2018-10-24 13:30 | 151.18 | 135.51
2018-10-24 14:00 | 153.43 | 139.17
2018-10-24 14:30 | 154.63 | 148.54
2018-10-24 15:00 | 164.67 | 160.18
2018-10-24 15:30 | 182.43 | 178.41
2018-10-24 16:00 | 208.55 | 205.09
2018-10-24 16:30 | 229.5 | 226.62
2018-10-24 17:00 | 226.22 | 223.72
2018-10-24 17:30 | 226.39 | 224.29
2018-10-24 18:00 | 199.26 | 198.89
2018-10-24 18:30 | 200.09 | 199.89
2018-10-24 19:00 | 200.07 | 199.86
2018-10-24 19:30 | 221.18 | 221.1
2018-10-24 20:00 | 216.54 | 216.42
2018-10-24 20:30 | 212.47 | 212.09
2018-10-24 21:00 | 200.51 | 200.43
2018-10-24 21:30 | 188.95 | 188.95
2018-10-24 22:00 | 167.04 | 167.01
2018-10-24 22:30 | 157.94 | 157.89
2018-10-24 23:00 | 153.23 | 153.11
2018-10-24 23:30 | 119.62 | 119.24
2018-10-25 | 75.21 | 74.48
2018-10-25 00:30 | 31.61 | 29.3
2018-10-25 01:00 | 31.73 | 28.71
2018-10-25 01:30 | 29.95 | 27.15
2018-10-25 02:00 | 19.42 | 15.66
2018-10-25 02:30 | 9.68 | 0.52
2018-10-25 03:00 | 12.14 | -8.23
2018-10-25 03:30 | 9.74 | -4.12
2018-10-25 04:00 | 11.51 | -9.19
2018-10-25 04:30 | 14.44 | -13.47
2018-10-25 05:00 | 6.37 | -0.16
2018-10-25 05:30 | 13.37 | -12.31
2018-10-25 06:00 | 12.87 | 9.73
2018-10-25 06:30 | 36.29 | 36.2
2018-10-25 07:00 | 52.23 | 41.41
2018-10-25 07:30 | 73.04 | 59.41
2018-10-25 08:00 | 78.82 | 63.93
2018-10-25 08:30 | 86.04 | 70.03
2018-10-25 09:00 | 96.35 | 82.59
2018-10-25 09:30 | 97.96 | 83.03
2018-10-25 10:00 | 79.82 | 57.04
2018-10-25 10:30 | 83.99 | 61.11
2018-10-25 11:00 | 88.31 | 66.93
2018-10-25 11:30 | 83.36 | 60.13
2018-10-25 12:00 | 80.01 | 55.25
2018-10-25 12:30 | 86.28 | 64.23
2018-10-25 13:00 | 84.5 | 62.28
2018-10-25 13:30 | 83.17 | 60.01
2018-10-25 14:00 | 85.41 | 65.77
2018-10-25 14:30 | 100.29 | 84.41
2018-10-25 15:00 | 120.66 | 108.43
2018-10-25 15:30 | 91.39 | 74.54
2018-10-25 16:00 | 137.1 | 127.06
2018-10-25 16:30 | 188.28 | 181.43
2018-10-25 17:00 | 219.35 | 214.08
2018-10-25 17:30 | 215.98 | 211.25
2018-10-25 18:00 | 221.36 | 216.72
2018-10-25 18:30 | 226.27 | 221.43
2018-10-25 19:00 | 229.6 | 225.02
2018-10-25 19:30 | 172.48 | 167.13
2018-10-25 20:00 | 104.79 | 95.88
2018-10-25 20:30 | 125.72 | 119.81
2018-10-25 21:00 | 110.28 | 104.55
2018-10-25 21:30 | 111.86 | 111.54
2018-10-25 22:00 | 90.22 | 90.09
2018-10-25 22:30 | 95.05 | 94.82
2018-10-25 23:00 | 83.59 | 83.16
2018-10-25 23:30 | 48.72 | 47.61
2018-10-26 | 31.67 | 29.18
2018-10-26 00:30 | 32.75 | 29.39
2018-10-26 01:00 | 35.92 | 32.24
2018-10-26 01:30 | 44.1 | 40.61
2018-10-26 02:00 | 27.69 | 19.97
2018-10-26 02:30 | 17.06 | 1.32
2018-10-26 03:00 | 18.13 | 8.83
2018-10-26 03:30 | 18.8 | 10.8
2018-10-26 04:00 | 18.12 | 10.08
2018-10-26 04:30 | 19.61 | 12.57
2018-10-26 05:00 | 19.95 | 12.43
2018-10-26 05:30 | 15.25 | -2.36
2018-10-26 06:00 | 32.57 | -31.18
2018-10-26 06:30 | 27.06 | -24.83
2018-10-26 07:00 | 29.08 | -18.21
2018-10-26 07:30 | 57.65 | 2.82
2018-10-26 08:00 | 66.8 | 3.31
2018-10-26 08:30 | 70.99 | 4.01
2018-10-26 09:00 | 57.24 | 2.84
2018-10-26 09:30 | 41.96 | 9.8
2018-10-26 10:00 | 35.72 | 7.34
2018-10-26 10:30 | 39.81 | 16.8
2018-10-26 11:00 | 49.9 | 32.69
2018-10-26 11:30 | 53.98 | 37.45
2018-10-26 12:00 | 57.73 | 42.65
2018-10-26 12:30 | 84.63 | 74.96
2018-10-26 13:00 | 98.34 | 89.35
2018-10-26 13:30 | 111.25 | 103
2018-10-26 14:00 | 136.2 | 129.39
2018-10-26 14:30 | 168.69 | 162.8
2018-10-26 15:00 | 183.3 | 178.01
2018-10-26 15:30 | 194.61 | 190.18
2018-10-26 16:00 | 210.12 | 206.28
2018-10-26 16:30 | 185.24 | 181.31
2018-10-26 17:00 | 189.43 | 186.09
2018-10-26 17:30 | 158.08 | 156.74
2018-10-26 18:00 | 129.15 | 128.65
2018-10-26 18:30 | 129.69 | 128.79
2018-10-26 19:00 | 141.8 | 140.83
2018-10-26 19:30 | 119.55 | 117.78
2018-10-26 20:00 | 133.37 | 131.76
2018-10-26 20:30 | 113.93 | 113.46
2018-10-26 21:00 | 98.86 | 98.86
2018-10-26 21:30 | 85.11 | 85.06
2018-10-26 22:00 | 62.4 | 62.12
2018-10-26 22:30 | 72.26 | 71.74
2018-10-26 23:00 | 83.04 | 82.14
2018-10-26 23:30 | 56.06 | 54.21
2018-10-27 | 57.23 | 56.07
2018-10-27 00:30 | 53.31 | 52.75
2018-10-27 01:00 | 47.76 | 46.98
2018-10-27 01:30 | 30.12 | 24.95
2018-10-27 02:00 | 23.89 | 13.78
2018-10-27 02:30 | 19.01 | 5.87
2018-10-27 03:00 | 17.28 | -1.49
2018-10-27 03:30 | 17.16 | 3.07
2018-10-27 04:00 | 17.19 | 5.72
2018-10-27 04:30 | 16.53 | 4.06
2018-10-27 05:00 | 17.77 | 8.09
2018-10-27 05:30 | 14.43 | -0.36
2018-10-27 06:00 | 14.85 | 1.71
2018-10-27 06:30 | 15.3 | 1.96
2018-10-27 07:00 | 15.91 | -4.59
2018-10-27 07:30 | 9.55 | -8.26
2018-10-27 08:00 | 21.09 | -7.79
2018-10-27 08:30 | 9.79 | 3.4
2018-10-27 09:00 | 8.7 | 8.67
2018-10-27 09:30 | 11.18 | 9.24
2018-10-27 10:00 | 5.64 | 0.92
2018-10-27 10:30 | 5.47 | -4.48
2018-10-27 11:00 | 4.58 | 0.85
2018-10-27 11:30 | 28.19 | 27.25
2018-10-27 12:00 | 30.62 | 29.7
2018-10-27 12:30 | 39.45 | 38.41
2018-10-27 13:00 | 40.17 | 38.88
2018-10-27 13:30 | 55.95 | 54.94
2018-10-27 14:00 | 64.89 | 63.98
2018-10-27 14:30 | 71.08 | 70.13
2018-10-27 15:00 | 80.59 | 79.65
2018-10-27 15:30 | 81.7 | 80.79
2018-10-27 16:00 | 90.36 | 89.54
2018-10-27 16:30 | 108.07 | 107.36
2018-10-27 17:00 | 116.25 | 115.73
2018-10-27 17:30 | 107.86 | 107.36
2018-10-27 18:00 | 102.37 | 101.97
2018-10-27 18:30 | 103.94 | 103.62
2018-10-27 19:00 | 101.64 | 101.32
2018-10-27 19:30 | 76.91 | 76.54
2018-10-27 20:00 | 73.27 | 72.83
2018-10-27 20:30 | 75.66 | 75.47
2018-10-27 21:00 | 63.13 | 63.13
2018-10-27 21:30 | 57.09 | 57.01
2018-10-27 22:00 | 58.99 | 58.73
2018-10-27 22:30 | 53.28 | 52.82
2018-10-27 23:00 | 60.56 | 59.99
2018-10-27 23:30 | 69.04 | 68.17
2018-10-28 | 51.73 | 49.74
2018-10-28 00:30 | 42.06 | 39.32
2018-10-28 01:00 | 29.43 | 25.53
2018-10-28 01:30 | 15.58 | 9.15
2018-10-28 02:00 | 13.21 | 4.14
2018-10-28 02:30 | 12.05 | -2.66
2018-10-28 03:00 | 14.41 | -9.08
2018-10-28 03:30 | 13.2 | -7.56
2018-10-28 04:00 | 15.68 | -12.09
2018-10-28 04:30 | 11.11 | -4.61
2018-10-28 05:00 | 10.52 | -9.6
2018-10-28 05:30 | 19.58 | -16.52
2018-10-28 06:00 | 24.68 | -22.2
2018-10-28 06:30 | 30.91 | -28.78
2018-10-28 07:00 | 43.39 | -41.41
2018-10-28 07:30 | 31.52 | -29.1
2018-10-28 08:00 | 36.85 | -36.85
2018-10-28 08:30 | 19.33 | -19.09
2018-10-28 09:00 | 9.87 | 6.99
2018-10-28 09:30 | 11.81 | -10.47
2018-10-28 10:00 | 26.3 | 26.28
2018-10-28 10:30 | 12.5 | 12.5
2018-10-28 11:00 | 29.01 | -26.78
2018-10-28 11:30 | 28.65 | -26.15
2018-10-28 12:00 | 14.28 | -8.66
2018-10-28 12:30 | 12.52 | -5.66
2018-10-28 13:00 | 13.37 | 7.91
2018-10-28 13:30 | 22.2 | 19.2
2018-10-28 14:00 | 49.25 | 47.96
2018-10-28 14:30 | 86.6 | 85.97
2018-10-28 15:00 | 97.65 | 97.2
2018-10-28 15:30 | 106.72 | 106.36
2018-10-28 16:00 | 97.02 | 96.96
2018-10-28 16:30 | 120.73 | 120.32
2018-10-28 17:00 | 146.95 | 146.72
2018-10-28 17:30 | 142.21 | 141.99
2018-10-28 18:00 | 153.87 | 153.71
2018-10-28 18:30 | 166.72 | 166.6
2018-10-28 19:00 | 175.9 | 175.8
2018-10-28 19:30 | 150.95 | 150.78
2018-10-28 20:00 | 140.26 | 140.25
2018-10-28 20:30 | 154.42 | 154.22
2018-10-28 21:00 | 157.47 | 157.44
2018-10-28 21:30 | 157.32 | 156.65
2018-10-28 22:00 | 140.32 | 139.4
2018-10-28 22:30 | 140.72 | 139.93
2018-10-28 23:00 | 150.29 | 149.56
2018-10-28 23:30 | 128.97 | 128.28
2018-10-29 | 90.36 | 89.21
2018-10-29 00:30 | 74.84 | 73.6
2018-10-29 01:00 | 63.4 | 61.86
2018-10-29 01:30 | 50.95 | 49.12
2018-10-29 02:00 | 45.99 | 45.95
2018-10-29 02:30 | 41.28 | 41.26
2018-10-29 03:00 | 56.3 | 56.27
2018-10-29 03:30 | 66.94 | 66.91
2018-10-29 04:00 | 72.56 | 72.47
2018-10-29 04:30 | 76.42 | 76.29
2018-10-29 05:00 | 70.71 | 70.66
2018-10-29 05:30 | 41.54 | 41.36
2018-10-29 06:00 | 66.68 | 66.42
2018-10-29 06:30 | 86.45 | 86.42
2018-10-29 07:00 | 96.46 | 95.85
2018-10-29 07:30 | 132.65 | 132.54
2018-10-29 08:00 | 141.44 | 141.43
2018-10-29 08:30 | 135.17 | 135.16
2018-10-29 09:00 | 132.81 | 132.81
2018-10-29 09:30 | 142 | 142
2018-10-29 10:00 | 129.62 | 129.61
2018-10-29 10:30 | 114.56 | 114.56
2018-10-29 11:00 | 128.7 | 128.7
2018-10-29 11:30 | 133.92 | 133.92
2018-10-29 12:00 | 142.18 | 142.18
2018-10-29 12:30 | 165.9 | 165.9
2018-10-29 13:00 | 171.9 | 171.87
2018-10-29 13:30 | 164.79 | 164.75
2018-10-29 14:00 | 171.83 | 171.81
2018-10-29 14:30 | 180.36 | 180.32
2018-10-29 15:00 | 163.56 | 163.47
2018-10-29 15:30 | 147.78 | 147.61
2018-10-29 16:00 | 138.99 | 138.79
2018-10-29 16:30 | 145.97 | 145.78
2018-10-29 17:00 | 148.46 | 148.2
2018-10-29 17:30 | 156.8 | 156.63
2018-10-29 18:00 | 150.24 | 150.02
2018-10-29 18:30 | 161.06 | 160.98
2018-10-29 19:00 | 168.69 | 168.65
2018-10-29 19:30 | 166.2 | 166.13
2018-10-29 20:00 | 180.14 | 180.12
2018-10-29 20:30 | 196.16 | 196.15
2018-10-29 21:00 | 185.28 | 185.22
2018-10-29 21:30 | 174.85 | 174.68
2018-10-29 22:00 | 166.38 | 166.06
2018-10-29 22:30 | 158.29 | 157.78
2018-10-29 23:00 | 156.53 | 155.82
2018-10-29 23:30 | 145.5 | 144.41
2018-10-30 | 120.94 | 119.56
2018-10-30 00:30 | 114.76 | 113.64
2018-10-30 01:00 | 111.35 | 110.03
2018-10-30 01:30 | 94.52 | 92.85
2018-10-30 02:00 | 84.01 | 82.15
2018-10-30 02:30 | 79.68 | 78.13
2018-10-30 03:00 | 67.42 | 67.41
2018-10-30 03:30 | 75.64 | 75.62
2018-10-30 04:00 | 82.96 | 82.91
2018-10-30 04:30 | 99.97 | 99.89
2018-10-30 05:00 | 107.17 | 107.11
2018-10-30 05:30 | 110.54 | 110.48
2018-10-30 06:00 | 89.75 | 89.61
2018-10-30 06:30 | 82.32 | 82.18
2018-10-30 07:00 | 70.56 | 70.12
2018-10-30 07:30 | 75.6 | 75.59
2018-10-30 08:00 | 95.88 | 95.77
2018-10-30 08:30 | 122.11 | 121.85
2018-10-30 09:00 | 135.35 | 135.03
2018-10-30 09:30 | 137.42 | 135.07
2018-10-30 10:00 | 145.52 | 141.85
2018-10-30 10:30 | 127.72 | 123.48
2018-10-30 11:00 | 123.91 | 120.96
2018-10-30 11:30 | 120.95 | 118.72
2018-10-30 12:00 | 120.51 | 118.31
2018-10-30 12:30 | 122.63 | 120.4
2018-10-30 13:00 | 118.56 | 116.3
2018-10-30 13:30 | 105.58 | 102.97
2018-10-30 14:00 | 116.49 | 114
2018-10-30 14:30 | 118.13 | 115.69
2018-10-30 15:00 | 82.59 | 78.99
2018-10-30 15:30 | 86.74 | 79.09
2018-10-30 16:00 | 127.42 | 120.44
2018-10-30 16:30 | 111.54 | 103.96
2018-10-30 17:00 | 127.69 | 121.45
2018-10-30 17:30 | 128.66 | 123.22
2018-10-30 18:00 | 131.86 | 127.27
2018-10-30 18:30 | 156.54 | 152.48
2018-10-30 19:00 | 165.65 | 161.35
2018-10-30 19:30 | 154.92 | 150.98
2018-10-30 20:00 | 138.97 | 135.21
2018-10-30 20:30 | 146.54 | 144.82
2018-10-30 21:00 | 133.17 | 132.81
2018-10-30 21:30 | 123.53 | 122.41
2018-10-30 22:00 | 95.21 | 93.6
2018-10-30 22:30 | 104.12 | 102.82
2018-10-30 23:00 | 119.35 | 118.17
2018-10-30 23:30 | 96.04 | 94.92
2018-10-31 | 71.86 | 70.57
2018-10-31 00:30 | 79.54 | 78.55
2018-10-31 01:00 | 79.84 | 78.88
2018-10-31 01:30 | 64.57 | 62.18
2018-10-31 02:00 | 65.52 | 62.86
2018-10-31 02:30 | 46.79 | 43.09
2018-10-31 03:00 | 42.21 | 38.31
2018-10-31 03:30 | 44.17 | 40.55
2018-10-31 04:00 | 35.51 | 32.05
2018-10-31 04:30 | 43.32 | 40.91
2018-10-31 05:00 | 57.95 | 56.22
2018-10-31 05:30 | 46.4 | 43.68
2018-10-31 06:00 | 43.56 | 40.91
2018-10-31 06:30 | 59.98 | 59.93
2018-10-31 07:00 | 80.45 | 80.42
2018-10-31 07:30 | 114 | 113.93
2018-10-31 08:00 | 85.75 | 85.21
2018-10-31 08:30 | 68.25 | 67.33
2018-10-31 09:00 | 58.26 | 56.78
2018-10-31 09:30 | 49.21 | 46.69
2018-10-31 10:00 | 50.82 | 47.34
2018-10-31 10:30 | 48.74 | 45.11
2018-10-31 11:00 | 50.16 | 47.06
2018-10-31 11:30 | 49.85 | 46.71
2018-10-31 12:00 | 53.51 | 50.81
2018-10-31 12:30 | 57.32 | 54.72
2018-10-31 13:00 | 60.49 | 58.18
2018-10-31 13:30 | 63.81 | 61.79
2018-10-31 14:00 | 65.5 | 64.71
2018-10-31 14:30 | 49.58 | 49.14
2018-10-31 15:00 | 70.8 | 70.61
2018-10-31 15:30 | 65.72 | 65.54
2018-10-31 16:00 | 89.75 | 89.71
2018-10-31 16:30 | 114.76 | 114.75
2018-10-31 17:00 | 131.5 | 131.5
2018-10-31 17:30 | 142.28 | 142.28
2018-10-31 18:00 | 146.27 | 146.26
2018-10-31 18:30 | 154.57 | 154.57
2018-10-31 19:00 | 184.04 | 184.04
2018-10-31 19:30 | 166.46 | 166.46
2018-10-31 20:00 | 171.72 | 171.71
2018-10-31 20:30 | 166.68 | 166.66
2018-10-31 21:00 | 182.97 | 182.97
2018-10-31 21:30 | 178.58 | 178.54
2018-10-31 22:00 | 168.25 | 168.01
2018-10-31 22:30 | 165.44 | 165.08
2018-10-31 23:00 | 149.09 | 148.78
2018-10-31 23:30 | 149.87 | 149.23
2018-11-01 | 136.14 | 135.24
2018-11-01 00:30 | 121.48 | 120.81
2018-11-01 01:00 | 115.73 | 114.96
2018-11-01 01:30 | 92.72 | 91.39
2018-11-01 02:00 | 82.49 | 81.02
2018-11-01 02:30 | 83.49 | 82.11
2018-11-01 03:00 | 71.08 | 69.37
2018-11-01 03:30 | 82.9 | 81.53
2018-11-01 04:00 | 90.81 | 89.91
2018-11-01 04:30 | 79.76 | 78.67
2018-11-01 05:00 | 86.86 | 85.99
2018-11-01 05:30 | 100.67 | 99.95
2018-11-01 06:00 | 79.46 | 78.26
2018-11-01 06:30 | 85.92 | 85.77
2018-11-01 07:00 | 83.23 | 83.23
2018-11-01 07:30 | 109.56 | 109.34
2018-11-01 08:00 | 106.72 | 106.15
2018-11-01 08:30 | 105.17 | 94.49
2018-11-01 09:00 | 103.95 | 78.16
2018-11-01 09:30 | 115.25 | 91.68
2018-11-01 10:00 | 108.94 | 81.88
2018-11-01 10:30 | 129.33 | 107.37
2018-11-01 11:00 | 127.98 | 104.97
2018-11-01 11:30 | 106.99 | 77.02
2018-11-01 12:00 | 95.51 | 58.57
2018-11-01 12:30 | 98.82 | 65.32
2018-11-01 13:00 | 83.48 | 42.56
2018-11-01 13:30 | 81.16 | 36.53
2018-11-01 14:00 | 83.65 | 41.94
2018-11-01 14:30 | 98.42 | 66.97
2018-11-01 15:00 | 109.22 | 82.48
2018-11-01 15:30 | 101.75 | 73.8
2018-11-01 16:00 | 120.6 | 98.87
2018-11-01 16:30 | 133.07 | 114.65
2018-11-01 17:00 | 136 | 118.76
2018-11-01 17:30 | 137.63 | 121.7
2018-11-01 18:00 | 136.67 | 121.86
2018-11-01 18:30 | 151.61 | 138.19
2018-11-01 19:00 | 169.68 | 157.28
2018-11-01 19:30 | 139.51 | 125.32
2018-11-01 20:00 | 126.55 | 112.12
2018-11-01 20:30 | 138.7 | 131.56
2018-11-01 21:00 | 141.68 | 140.51
2018-11-01 21:30 | 159.5 | 159.48
2018-11-01 22:00 | 144.8 | 144.61
2018-11-01 22:30 | 156.54 | 156.21
2018-11-01 23:00 | 161.63 | 161.23
2018-11-01 23:30 | 147.89 | 147.15
2018-11-02 | 127.19 | 126.25
2018-11-02 00:30 | 101.65 | 100.31
2018-11-02 01:00 | 76.71 | 74.88
2018-11-02 01:30 | 64.14 | 62.01
2018-11-02 02:00 | 67.7 | 65.52
2018-11-02 02:30 | 93.87 | 92.39
2018-11-02 03:00 | 87.82 | 86.16
2018-11-02 03:30 | 91.21 | 89.73
2018-11-02 04:00 | 91.34 | 89.85
2018-11-02 04:30 | 98.3 | 97.1
2018-11-02 05:00 | 84.01 | 82.56
2018-11-02 05:30 | 77.69 | 76.26
2018-11-02 06:00 | 68.39 | 66.46
2018-11-02 06:30 | 79.33 | 77.85
2018-11-02 07:00 | 76.71 | 75.78
2018-11-02 07:30 | 70.96 | 70.85
2018-11-02 08:00 | 81.86 | 81.81
2018-11-02 08:30 | 83.22 | 83.21
2018-11-02 09:00 | 99.24 | 99.24
2018-11-02 09:30 | 81.98 | 81.98
2018-11-02 10:00 | 36.2 | 36.12
2018-11-02 10:30 | 25.82 | 25.67
2018-11-02 11:00 | 18.89 | 18.53
2018-11-02 11:30 | 71.75 | 71.63
2018-11-02 12:00 | 51.51 | 51.46
2018-11-02 12:30 | 39.79 | 39.75
2018-11-02 13:00 | 87.68 | 87.66
2018-11-02 13:30 | 18.87 | 18.15
2018-11-02 14:00 | 25.73 | 25.03
2018-11-02 14:30 | 47.6 | 47.41
2018-11-02 15:00 | 26.58 | 26.31
2018-11-02 15:30 | 39.78 | 39.69
2018-11-02 16:00 | 66.86 | 66.86
2018-11-02 16:30 | 86.17 | 86.17
2018-11-02 17:00 | 119.64 | 119.63
2018-11-02 17:30 | 131.96 | 131.9
2018-11-02 18:00 | 140.32 | 140.14
2018-11-02 18:30 | 167.64 | 167.57
2018-11-02 19:00 | 183.84 | 183.8
2018-11-02 19:30 | 176.08 | 176.01
2018-11-02 20:00 | 179.33 | 179.16
2018-11-02 20:30 | 179.7 | 179.51
2018-11-02 21:00 | 183.47 | 183.44
2018-11-02 21:30 | 176.19 | 176.13
2018-11-02 22:00 | 168.35 | 168.2
2018-11-02 22:30 | 161.21 | 161.02
2018-11-02 23:00 | 161.23 | 160.98
2018-11-02 23:30 | 154.12 | 153.69
2018-11-03 | 134.95 | 134.27
2018-11-03 00:30 | 122.14 | 121.32
2018-11-03 01:00 | 118.16 | 117.25
2018-11-03 01:30 | 107.92 | 106.72
2018-11-03 02:00 | 99.29 | 97.99
2018-11-03 02:30 | 98.73 | 97.56
2018-11-03 03:00 | 102.66 | 101.67
2018-11-03 03:30 | 103.84 | 102.82
2018-11-03 04:00 | 104.22 | 103.08
2018-11-03 04:30 | 104.44 | 103.24
2018-11-03 05:00 | 105.52 | 104.61
2018-11-03 05:30 | 107.2 | 106.35
2018-11-03 06:00 | 112.85 | 112.01
2018-11-03 06:30 | 111.55 | 110.76
2018-11-03 07:00 | 96.73 | 95.38
2018-11-03 07:30 | 87.72 | 86.12
2018-11-03 08:00 | 83.51 | 81.58
2018-11-03 08:30 | 85.14 | 83.76
2018-11-03 09:00 | 83.82 | 82.59
2018-11-03 09:30 | 78.15 | 78.03
2018-11-03 10:00 | 64.14 | 63.77
2018-11-03 10:30 | 70.79 | 70.39
2018-11-03 11:00 | 84.3 | 83.96
2018-11-03 11:30 | 94.51 | 94.13
2018-11-03 12:00 | 95.27 | 94.91
2018-11-03 12:30 | 104.09 | 103.7
2018-11-03 13:00 | 107.16 | 106.73
2018-11-03 13:30 | 124.3 | 123.96
2018-11-03 14:00 | 134.79 | 134.38
2018-11-03 14:30 | 165.49 | 162.69
2018-11-03 15:00 | 174.56 | 171.99
2018-11-03 15:30 | 171.85 | 169.25
2018-11-03 16:00 | 189.36 | 179.91
2018-11-03 16:30 | 203.49 | 194.86
2018-11-03 17:00 | 212.05 | 203.66
2018-11-03 17:30 | 212.29 | 204.13
2018-11-03 18:00 | 207.77 | 202.75
2018-11-03 18:30 | 205.93 | 202.57
2018-11-03 19:00 | 214.13 | 210.66
2018-11-03 19:30 | 208.25 | 205.23
2018-11-03 20:00 | 202.02 | 199.16
2018-11-03 20:30 | 187.65 | 184.99
2018-11-03 21:00 | 179.89 | 179.64
2018-11-03 21:30 | 177.84 | 177.82
2018-11-03 22:00 | 169.37 | 169.28
2018-11-03 22:30 | 165.35 | 165.25
2018-11-03 23:00 | 140.24 | 140.18
2018-11-03 23:30 | 143.97 | 143.64
2018-11-04 | 140.36 | 139.74
2018-11-04 00:30 | 130.81 | 129.92
2018-11-04 01:00 | 123.83 | 122.61
2018-11-04 01:30 | 97.8 | 95.98
2018-11-04 02:00 | 76.13 | 73.74
2018-11-04 02:30 | 63.17 | 60.28
2018-11-04 03:00 | 78.44 | 76.23
2018-11-04 03:30 | 77.31 | 75.23
2018-11-04 04:00 | 58.4 | 55.62
2018-11-04 04:30 | 94.53 | 93.15
2018-11-04 05:00 | 103.36 | 102.28
2018-11-04 05:30 | 105.05 | 104.16
2018-11-04 06:00 | 109.54 | 108.66
2018-11-04 06:30 | 88.86 | 87.49
2018-11-04 07:00 | 82.61 | 80.74
2018-11-04 07:30 | 88.23 | 86.23
2018-11-04 08:00 | 85.26 | 83.19
2018-11-04 08:30 | 93.48 | 91.37
2018-11-04 09:00 | 107.12 | 105.53
2018-11-04 09:30 | 118.38 | 118.34
2018-11-04 10:00 | 133.28 | 133.04
2018-11-04 10:30 | 136.82 | 136.48
2018-11-04 11:00 | 127.47 | 126.99
2018-11-04 11:30 | 142.18 | 141.67
2018-11-04 12:00 | 156.08 | 155.51
2018-11-04 12:30 | 153.8 | 153.14
2018-11-04 13:00 | 170.27 | 166.78
2018-11-04 13:30 | 179.59 | 174.3
2018-11-04 14:00 | 189.14 | 177.74
2018-11-04 14:30 | 193.83 | 182.39
2018-11-04 15:00 | 192.89 | 180.76
2018-11-04 15:30 | 199.18 | 187.15
2018-11-04 16:00 | 218.44 | 208.23
2018-11-04 16:30 | 210.08 | 205.21
2018-11-04 17:00 | 207.34 | 205.03
2018-11-04 17:30 | 224.13 | 222.49
2018-11-04 18:00 | 226.81 | 225.49
2018-11-04 18:30 | 230.23 | 228.76
2018-11-04 19:00 | 226.34 | 224.35
2018-11-04 19:30 | 220.86 | 219.16
2018-11-04 20:00 | 218.71 | 215.43
2018-11-04 20:30 | 211.01 | 207.42
2018-11-04 21:00 | 202.7 | 199.75
2018-11-04 21:30 | 179.95 | 179.94
2018-11-04 22:00 | 169.01 | 168.95
2018-11-04 22:30 | 145.75 | 145.72
2018-11-04 23:00 | 157.25 | 157.14
2018-11-04 23:30 | 154.56 | 154.25
2018-11-05 | 141.74 | 141.17
2018-11-05 00:30 | 128.75 | 127.96
2018-11-05 01:00 | 125.95 | 124.99
2018-11-05 01:30 | 110.08 | 108.35
2018-11-05 02:00 | 113.94 | 112.37
2018-11-05 02:30 | 111.66 | 110.26
2018-11-05 03:00 | 90.44 | 88.48
2018-11-05 03:30 | 96.06 | 94.4
2018-11-05 04:00 | 97.37 | 96.13
2018-11-05 04:30 | 77.73 | 76.13
2018-11-05 05:00 | 96.81 | 95.5
2018-11-05 05:30 | 117.64 | 116.6
2018-11-05 06:00 | 123.34 | 122.38
2018-11-05 06:30 | 137.36 | 136.91
2018-11-05 07:00 | 109.69 | 109.58
2018-11-05 07:30 | 135.64 | 134.29
2018-11-05 08:00 | 160.32 | 153.61
2018-11-05 08:30 | 168.98 | 161.76
2018-11-05 09:00 | 170.74 | 161.52
2018-11-05 09:30 | 165.89 | 155.52
2018-11-05 10:00 | 167.2 | 156.24
2018-11-05 10:30 | 171.71 | 160.88
2018-11-05 11:00 | 174.22 | 163.05
2018-11-05 11:30 | 175.74 | 165.7
2018-11-05 12:00 | 176.51 | 170.52
2018-11-05 12:30 | 182.23 | 176.63
2018-11-05 13:00 | 189.12 | 183.09
2018-11-05 13:30 | 192.18 | 186
2018-11-05 14:00 | 197.16 | 190.7
2018-11-05 14:30 | 203.25 | 196.69
2018-11-05 15:00 | 207.61 | 202.15
2018-11-05 15:30 | 231.27 | 226.69
2018-11-05 16:00 | 230.55 | 225.22
2018-11-05 16:30 | 258.43 | 254.3
2018-11-05 17:00 | 271.06 | 267.58
2018-11-05 17:30 | 270.01 | 267.08
2018-11-05 18:00 | 265.86 | 263.36
2018-11-05 18:30 | 263.29 | 260.96
2018-11-05 19:00 | 270.24 | 267.56
2018-11-05 19:30 | 254.3 | 252.32
2018-11-05 20:00 | 233.08 | 231.76
2018-11-05 20:30 | 240.85 | 240.2
2018-11-05 21:00 | 220.48 | 220.47
2018-11-05 21:30 | 203.18 | 203.17
2018-11-05 22:00 | 191.74 | 191.7
2018-11-05 22:30 | 172.14 | 172.08
2018-11-05 23:00 | 174.03 | 173.76
2018-11-05 23:30 | 160.53 | 160.21
2018-11-06 | 150.6 | 150.09
2018-11-06 00:30 | 127.7 | 127.3
2018-11-06 01:00 | 118.85 | 118.28
2018-11-06 01:30 | 119.9 | 119.14
2018-11-06 02:00 | 117.34 | 116.48
2018-11-06 02:30 | 120.07 | 119.17
2018-11-06 03:00 | 119.41 | 118.38
2018-11-06 03:30 | 118.77 | 117.92
2018-11-06 04:00 | 120.29 | 119.63
2018-11-06 04:30 | 122.05 | 121.44
2018-11-06 05:00 | 123.38 | 122.8
2018-11-06 05:30 | 135.48 | 134.87
2018-11-06 06:00 | 147.84 | 147.24
2018-11-06 06:30 | 158.58 | 158.57
2018-11-06 07:00 | 166.01 | 165.83
2018-11-06 07:30 | 171.79 | 169.72
2018-11-06 08:00 | 193.51 | 181.4
2018-11-06 08:30 | 175.3 | 160
2018-11-06 09:00 | 171.54 | 154.03
2018-11-06 09:30 | 186.27 | 168
2018-11-06 10:00 | 209.13 | 191.75
2018-11-06 10:30 | 216.03 | 198.26
2018-11-06 11:00 | 206.67 | 189.22
2018-11-06 11:30 | 228.9 | 216.97
2018-11-06 12:00 | 231.95 | 219.04
2018-11-06 12:30 | 231.88 | 218.95
2018-11-06 13:00 | 226.35 | 212.94
2018-11-06 13:30 | 226.93 | 213.3
2018-11-06 14:00 | 240.52 | 227.04
2018-11-06 14:30 | 252.58 | 241.71
2018-11-06 15:00 | 250.65 | 240.15
2018-11-06 15:30 | 236.59 | 224.93
2018-11-06 16:00 | 228.67 | 217.12
2018-11-06 16:30 | 221.24 | 209.97
2018-11-06 17:00 | 209.82 | 199.22
2018-11-06 17:30 | 204.23 | 194.95
2018-11-06 18:00 | 205.6 | 201.31
2018-11-06 18:30 | 217.37 | 214.46
2018-11-06 19:00 | 237.35 | 234.57
2018-11-06 19:30 | 256.87 | 254.9
2018-11-06 20:00 | 225.62 | 224.13
2018-11-06 20:30 | 246.07 | 244.92
2018-11-06 21:00 | 228.78 | 228.39
2018-11-06 21:30 | 210.31 | 210.17
2018-11-06 22:00 | 207.56 | 207.27
2018-11-06 22:30 | 183.6 | 183.2
2018-11-06 23:00 | 181.21 | 180.89
2018-11-06 23:30 | 166.68 | 166.06
2018-11-07 | 136.85 | 136.37
2018-11-07 00:30 | 143.37 | 143
2018-11-07 01:00 | 119.73 | 119.49
2018-11-07 01:30 | 103.8 | 103.58
2018-11-07 02:00 | 94.73 | 94.42
2018-11-07 02:30 | 96.61 | 96.09
2018-11-07 03:00 | 114.64 | 113.92
2018-11-07 03:30 | 115.79 | 115.03
2018-11-07 04:00 | 108.97 | 108.33
2018-11-07 04:30 | 98.14 | 97.75
2018-11-07 05:00 | 101.91 | 101.5
2018-11-07 05:30 | 127.86 | 127.43
2018-11-07 06:00 | 142.26 | 142.05
2018-11-07 06:30 | 134.05 | 134.02
2018-11-07 07:00 | 103.66 | 103.38
2018-11-07 07:30 | 118.81 | 118.78
2018-11-07 08:00 | 126.12 | 126.01
2018-11-07 08:30 | 136.15 | 135.62
2018-11-07 09:00 | 153.24 | 145.64
2018-11-07 09:30 | 195.58 | 182.87
2018-11-07 10:00 | 187.15 | 173.2
2018-11-07 10:30 | 211.49 | 199.5
2018-11-07 11:00 | 221.29 | 211.46
2018-11-07 11:30 | 209.24 | 199.09
2018-11-07 12:00 | 223.94 | 213.96
2018-11-07 12:30 | 224.94 | 215.02
2018-11-07 13:00 | 229.47 | 219.57
2018-11-07 13:30 | 219.54 | 208.93
2018-11-07 14:00 | 227.16 | 215.6
2018-11-07 14:30 | 172.54 | 159.17
2018-11-07 15:00 | 170.22 | 157.89
2018-11-07 15:30 | 166.45 | 153.33
2018-11-07 16:00 | 178.95 | 165.91
2018-11-07 16:30 | 178.22 | 166.22
2018-11-07 17:00 | 184.35 | 173.42
2018-11-07 17:30 | 177.21 | 167.06
2018-11-07 18:00 | 170.08 | 161.13
2018-11-07 18:30 | 162.75 | 159.37
2018-11-07 19:00 | 194.52 | 191.53
2018-11-07 19:30 | 255.1 | 253.5
2018-11-07 20:00 | 248.25 | 246.97
2018-11-07 20:30 | 231.64 | 230.82
2018-11-07 21:00 | 208.07 | 208.07
2018-11-07 21:30 | 190.63 | 190.62
2018-11-07 22:00 | 196 | 195.92
2018-11-07 22:30 | 180.96 | 180.78
2018-11-07 23:00 | 174.67 | 174.32
2018-11-07 23:30 | 165.09 | 164.53
2018-11-08 | 148.19 | 147.41
2018-11-08 00:30 | 107.11 | 106.65
2018-11-08 01:00 | 99.91 | 99.53
2018-11-08 01:30 | 110.04 | 109.43
2018-11-08 02:00 | 88.36 | 87.85
2018-11-08 02:30 | 86.69 | 86.14
2018-11-08 03:00 | 88.52 | 87.95
2018-11-08 03:30 | 102.53 | 101.87
2018-11-08 04:00 | 107.94 | 107.3
2018-11-08 04:30 | 105.73 | 105.24
2018-11-08 05:00 | 98.84 | 98.53
2018-11-08 05:30 | 111.08 | 110.86
2018-11-08 06:00 | 142.36 | 142.18
2018-11-08 06:30 | 159.66 | 159.64
2018-11-08 07:00 | 175.27 | 175.22
2018-11-08 07:30 | 204.9 | 203.3
2018-11-08 08:00 | 205.4 | 203.86
2018-11-08 08:30 | 205.28 | 203.12
2018-11-08 09:00 | 205.22 | 203.09
2018-11-08 09:30 | 205.97 | 203.21
2018-11-08 10:00 | 203.73 | 200.77
2018-11-08 10:30 | 208.11 | 205.58
2018-11-08 11:00 | 206.71 | 204.37
2018-11-08 11:30 | 207.34 | 205.14
2018-11-08 12:00 | 192.19 | 190.38
2018-11-08 12:30 | 185.16 | 183.45
2018-11-08 13:00 | 136.7 | 136.45
2018-11-08 13:30 | 136.85 | 136.82
2018-11-08 14:00 | 152.59 | 152.55
2018-11-08 14:30 | 156.36 | 156.28
2018-11-08 15:00 | 128 | 127.75
2018-11-08 15:30 | 136.73 | 136.45
2018-11-08 16:00 | 155.47 | 155.25
2018-11-08 16:30 | 169.5 | 169.34
2018-11-08 17:00 | 192.19 | 192.09
2018-11-08 17:30 | 196.43 | 196.37
2018-11-08 18:00 | 187.88 | 187.86
2018-11-08 18:30 | 183.77 | 183.76
2018-11-08 19:00 | 204.32 | 203.02
2018-11-08 19:30 | 191.73 | 187.34
2018-11-08 20:00 | 189.94 | 187.18
2018-11-08 20:30 | 179.96 | 179.33
2018-11-08 21:00 | 157.1 | 157.07
2018-11-08 21:30 | 118.81 | 118.71
2018-11-08 22:00 | 82.33 | 81.99
2018-11-08 22:30 | 88.95 | 88.39
2018-11-08 23:00 | 80.57 | 79.7
2018-11-08 23:30 | 58.2 | 56.75
2018-11-09 | 49.79 | 47.67
2018-11-09 00:30 | 41.49 | 38.27
2018-11-09 01:00 | 34.87 | 30.6
2018-11-09 01:30 | 21.01 | 12.84
2018-11-09 02:00 | 17.75 | 6.74
2018-11-09 02:30 | 17.35 | -6.3
2018-11-09 03:00 | 17.68 | -7.89
2018-11-09 03:30 | 17.43 | -7.98
2018-11-09 04:00 | 22.95 | -18.04
2018-11-09 04:30 | 17.17 | 6.71
2018-11-09 05:00 | 15.12 | 2.82
2018-11-09 05:30 | 16.89 | -11.69
2018-11-09 06:00 | 20.23 | -16.21
2018-11-09 06:30 | 22.73 | 20.63
2018-11-09 07:00 | 16 | 15.45
2018-11-09 07:30 | 29.94 | 29.87
2018-11-09 08:00 | 53.6 | 53.46
2018-11-09 08:30 | 45.9 | 45.73
2018-11-09 09:00 | 40.46 | 40.39
2018-11-09 09:30 | 56.63 | 56.61
2018-11-09 10:00 | 53.28 | 53.22
2018-11-09 10:30 | 65.81 | 65.77
2018-11-09 11:00 | 76.8 | 76.77
2018-11-09 11:30 | 112.09 | 112.06
2018-11-09 12:00 | 97.92 | 97.87
2018-11-09 12:30 | 108.95 | 108.91
2018-11-09 13:00 | 112.21 | 112.15
2018-11-09 13:30 | 110.33 | 110.25
2018-11-09 14:00 | 106.47 | 106.39
2018-11-09 14:30 | 107.43 | 107.35
2018-11-09 15:00 | 102.82 | 102.56
2018-11-09 15:30 | 101.01 | 100.61
2018-11-09 16:00 | 112.64 | 112.29
2018-11-09 16:30 | 110.19 | 109.74
2018-11-09 17:00 | 137.53 | 137.11
2018-11-09 17:30 | 147.1 | 146.72
2018-11-09 18:00 | 150.25 | 149.93
2018-11-09 18:30 | 164.17 | 164.01
2018-11-09 19:00 | 187.95 | 187.85
2018-11-09 19:30 | 168.34 | 168.21
2018-11-09 20:00 | 156.66 | 156.66
2018-11-09 20:30 | 170.07 | 170.07
2018-11-09 21:00 | 169.34 | 169.3
2018-11-09 21:30 | 166.76 | 166.68
2018-11-09 22:00 | 152.46 | 152.21
2018-11-09 22:30 | 155.95 | 155.61
2018-11-09 23:00 | 155.72 | 155.25
2018-11-09 23:30 | 116.13 | 115.33
2018-11-10 | 99.18 | 97.92
2018-11-10 00:30 | 96.38 | 95
2018-11-10 01:00 | 89.53 | 88.07
2018-11-10 01:30 | 72.11 | 70.2
2018-11-10 02:00 | 57.82 | 55.47
2018-11-10 02:30 | 53.98 | 51.69
2018-11-10 03:00 | 50.13 | 47.76
2018-11-10 03:30 | 38.18 | 35.02
2018-11-10 04:00 | 31.04 | 27.24
2018-11-10 04:30 | 33.44 | 30.07
2018-11-10 05:00 | 32.64 | 30.31
2018-11-10 05:30 | 28.56 | 26.27
2018-11-10 06:00 | 38.17 | 35.94
2018-11-10 06:30 | 23.84 | 19.23
2018-11-10 07:00 | 20.16 | 13.86
2018-11-10 07:30 | 23.9 | 19.22
2018-11-10 08:00 | 27.53 | 25.78
2018-11-10 08:30 | 25.06 | 21.89
2018-11-10 09:00 | 38.93 | 37.38
2018-11-10 09:30 | 48.44 | 48.4
2018-11-10 10:00 | 64.39 | 64.35
2018-11-10 10:30 | 59.1 | 59.04
2018-11-10 11:00 | 55.4 | 55.31
2018-11-10 11:30 | 40.74 | 40.63
2018-11-10 12:00 | 46.39 | 46.32
2018-11-10 12:30 | 52.16 | 52.12
2018-11-10 13:00 | 44.31 | 44.27
2018-11-10 13:30 | 45.27 | 45.21
2018-11-10 14:00 | 46.7 | 46.62
2018-11-10 14:30 | 56.35 | 56.29
2018-11-10 15:00 | 74.84 | 74.79
2018-11-10 15:30 | 95.67 | 95.63
2018-11-10 16:00 | 120.67 | 120.65
2018-11-10 16:30 | 139.36 | 139.16
2018-11-10 17:00 | 138.44 | 137.6
2018-11-10 17:30 | 158.41 | 157.84
2018-11-10 18:00 | 154.86 | 154.37
2018-11-10 18:30 | 148.53 | 148.05
2018-11-10 19:00 | 181.71 | 181.44
2018-11-10 19:30 | 174.09 | 173.82
2018-11-10 20:00 | 174.19 | 174.15
2018-11-10 20:30 | 160.12 | 160.08
2018-11-10 21:00 | 149.88 | 149.78
2018-11-10 21:30 | 160.36 | 160.19
2018-11-10 22:00 | 145.98 | 145.65
2018-11-10 22:30 | 158.04 | 157.65
2018-11-10 23:00 | 156.74 | 156.22
2018-11-10 23:30 | 134.81 | 134.09
2018-11-11 | 121.02 | 119.75
2018-11-11 00:30 | 110.2 | 108.58
2018-11-11 01:00 | 103.48 | 101.56
2018-11-11 01:30 | 108.26 | 106.47
2018-11-11 02:00 | 108.68 | 107.11
2018-11-11 02:30 | 102.07 | 100.51
2018-11-11 03:00 | 95.68 | 94.04
2018-11-11 03:30 | 79.83 | 77.88
2018-11-11 04:00 | 74.25 | 72.22
2018-11-11 04:30 | 61.59 | 59.21
2018-11-11 05:00 | 53.29 | 51.26
2018-11-11 05:30 | 66.25 | 64.91
2018-11-11 06:00 | 44.96 | 42.67
2018-11-11 06:30 | 40.62 | 37.25
2018-11-11 07:00 | 28.29 | 22.42
2018-11-11 07:30 | 22.04 | 13.6
2018-11-11 08:00 | 16.34 | 3.35
2018-11-11 08:30 | 17.75 | 10.43
2018-11-11 09:00 | 11.51 | -3.44
2018-11-11 09:30 | 13.82 | -6.18
2018-11-11 10:00 | 13.96 | 3.16
2018-11-11 10:30 | 22 | 16.08
2018-11-11 11:00 | 40.33 | 36.69
2018-11-11 11:30 | 41.96 | 38.51
2018-11-11 12:00 | 43.29 | 39.97
2018-11-11 12:30 | 33.11 | 28.63
2018-11-11 13:00 | 28.82 | 23.48
2018-11-11 13:30 | 35.24 | 30.87
2018-11-11 14:00 | 48.4 | 45.14
2018-11-11 14:30 | 59.86 | 58.36
2018-11-11 15:00 | 47.77 | 47.77
2018-11-11 15:30 | 78.92 | 78.92
2018-11-11 16:00 | 91.36 | 91.36
2018-11-11 16:30 | 107.42 | 107.42
2018-11-11 17:00 | 128.38 | 128.38
2018-11-11 17:30 | 141.95 | 141.95
2018-11-11 18:00 | 154.9 | 154.89
2018-11-11 18:30 | 177.66 | 177.66
2018-11-11 19:00 | 200.4 | 200.33
2018-11-11 19:30 | 189.71 | 189.71
2018-11-11 20:00 | 187.98 | 187.89
2018-11-11 20:30 | 186.7 | 186.51
2018-11-11 21:00 | 174.62 | 174.4
2018-11-11 21:30 | 166.53 | 166.19
2018-11-11 22:00 | 149.05 | 148.51
2018-11-11 22:30 | 154.91 | 154.3
2018-11-11 23:00 | 147.47 | 146.65
2018-11-11 23:30 | 127.39 | 126.28
2018-11-12 | 88.28 | 86.42
2018-11-12 00:30 | 70.78 | 68.35
2018-11-12 01:00 | 47.26 | 44.37
2018-11-12 01:30 | 35.54 | 31.66
2018-11-12 02:00 | 33.23 | 29.42
2018-11-12 02:30 | 25.01 | 20.3
2018-11-12 03:00 | 23.34 | 18.41
2018-11-12 03:30 | 21.39 | 16.27
2018-11-12 04:00 | 19.98 | 15.76
2018-11-12 04:30 | 36.81 | 34.75
2018-11-12 05:00 | 54.2 | 52.85
2018-11-12 05:30 | 73.91 | 72.73
2018-11-12 06:00 | 72.65 | 71.13
2018-11-12 06:30 | 79.77 | 78.11
2018-11-12 07:00 | 73.14 | 72.62
2018-11-12 07:30 | 92.46 | 92.36
2018-11-12 08:00 | 100.07 | 100.06
2018-11-12 08:30 | 74.99 | 74.97
2018-11-12 09:00 | 59.18 | 59.18
2018-11-12 09:30 | 46.58 | 46.58
2018-11-12 10:00 | 44.29 | 44.29
2018-11-12 10:30 | 57.07 | 57.07
2018-11-12 11:00 | 54.41 | 54.4
2018-11-12 11:30 | 69.24 | 69.22
2018-11-12 12:00 | 84.4 | 84.33
2018-11-12 12:30 | 66.83 | 66.74
2018-11-12 13:00 | 52.65 | 52.57
2018-11-12 13:30 | 47.77 | 47.7
2018-11-12 14:00 | 48.04 | 47.94
2018-11-12 14:30 | 74.25 | 74.18
2018-11-12 15:00 | 66.9 | 66.81
2018-11-12 15:30 | 55.55 | 55.48
2018-11-12 16:00 | 80.46 | 80.33
2018-11-12 16:30 | 79.51 | 79.35
2018-11-12 17:00 | 108.18 | 108.01
2018-11-12 17:30 | 125.58 | 125.46
2018-11-12 18:00 | 162.14 | 162.11
2018-11-12 18:30 | 195.41 | 195.41
2018-11-12 19:00 | 216.2 | 216.19
2018-11-12 19:30 | 208.83 | 208.83
2018-11-12 20:00 | 196.16 | 196.16
2018-11-12 20:30 | 193.23 | 193.21
2018-11-12 21:00 | 184.55 | 184.42
2018-11-12 21:30 | 170.81 | 170.12
2018-11-12 22:00 | 146.28 | 145.3
2018-11-12 22:30 | 141.3 | 139.99
2018-11-12 23:00 | 137.73 | 136.39
2018-11-12 23:30 | 138.84 | 138.01
2018-11-13 | 97.36 | 96.15
2018-11-13 00:30 | 94.27 | 93.12
2018-11-13 01:00 | 88.58 | 87.08
2018-11-13 01:30 | 77.75 | 75.93
2018-11-13 02:00 | 67.33 | 65.3
2018-11-13 02:30 | 59.79 | 57.6
2018-11-13 03:00 | 58.6 | 56.11
2018-11-13 03:30 | 49.1 | 44.61
2018-11-13 04:00 | 41.13 | 37.25
2018-11-13 04:30 | 27.25 | 23.67
2018-11-13 05:00 | 47.06 | 45.25
2018-11-13 05:30 | 60.06 | 58.52
2018-11-13 06:00 | 74.57 | 73.19
2018-11-13 06:30 | 89.35 | 88.83
2018-11-13 07:00 | 68.94 | 68.08
2018-11-13 07:30 | 67.15 | 67.15
2018-11-13 08:00 | 58.48 | 58.19
2018-11-13 08:30 | 62.52 | 61.84
2018-11-13 09:00 | 76.19 | 71.57
2018-11-13 09:30 | 92.93 | 78.98
2018-11-13 10:00 | 78.07 | 63.49
2018-11-13 10:30 | 65.73 | 46.6
2018-11-13 11:00 | 68.26 | 48.94
2018-11-13 11:30 | 73.69 | 56.32
2018-11-13 12:00 | 70.68 | 52.5
2018-11-13 12:30 | 72.79 | 55.4
2018-11-13 13:00 | 69.51 | 51.42
2018-11-13 13:30 | 78.62 | 63.18
2018-11-13 14:00 | 96.66 | 84.88
2018-11-13 14:30 | 111.17 | 101.02
2018-11-13 15:00 | 121.79 | 113.11
2018-11-13 15:30 | 124.15 | 115.92
2018-11-13 16:00 | 115.84 | 107.23
2018-11-13 16:30 | 115.56 | 107.22
2018-11-13 17:00 | 155.22 | 149.43
2018-11-13 17:30 | 181.33 | 177.12
2018-11-13 18:00 | 193.53 | 190.25
2018-11-13 18:30 | 201.91 | 199.01
2018-11-13 19:00 | 219.77 | 216.58
2018-11-13 19:30 | 210.74 | 207.78
2018-11-13 20:00 | 195.51 | 192.83
2018-11-13 20:30 | 194.73 | 192.48
2018-11-13 21:00 | 167.65 | 167.63
2018-11-13 21:30 | 164.87 | 164.13
2018-11-13 22:00 | 143.98 | 142.98
2018-11-13 22:30 | 155.14 | 154.28
2018-11-13 23:00 | 161.09 | 160.36
2018-11-13 23:30 | 139.71 | 139.03
2018-11-14 | 100.71 | 99.71
2018-11-14 00:30 | 81.43 | 80.27
2018-11-14 01:00 | 96.21 | 95.4
2018-11-14 01:30 | 85.66 | 83.33
2018-11-14 02:00 | 64.32 | 61.12
2018-11-14 02:30 | 33.87 | 29.17
2018-11-14 03:00 | 18.51 | 11.2
2018-11-14 03:30 | 23.42 | 18.6
2018-11-14 04:00 | 15.46 | 9.32
2018-11-14 04:30 | 14.42 | 8.92
2018-11-14 05:00 | 19.15 | 15.39
2018-11-14 05:30 | 17.11 | 12.18
2018-11-14 06:00 | 22.1 | 18.43
2018-11-14 06:30 | 27.8 | 26.67
2018-11-14 07:00 | 36.18 | 36.04
2018-11-14 07:30 | 44.68 | 44.53
2018-11-14 08:00 | 24.74 | 22.56
2018-11-14 08:30 | 43.56 | 31.91
2018-11-14 09:00 | 49.71 | 34.09
2018-11-14 09:30 | 67 | 54.87
2018-11-14 10:00 | 101.77 | 94.68
2018-11-14 10:30 | 101.4 | 94.34
2018-11-14 11:00 | 106.25 | 99.13
2018-11-14 11:30 | 117.63 | 111.14
2018-11-14 12:00 | 129.58 | 123.69
2018-11-14 12:30 | 132.79 | 129.23
2018-11-14 13:00 | 136.54 | 132.99
2018-11-14 13:30 | 150.75 | 147.46
2018-11-14 14:00 | 165.82 | 165.61
2018-11-14 14:30 | 181.64 | 181.46
2018-11-14 15:00 | 185.09 | 184.94
2018-11-14 15:30 | 193.58 | 193.37
2018-11-14 16:00 | 198.05 | 197.88
2018-11-14 16:30 | 201.02 | 200.91
2018-11-14 17:00 | 200.61 | 200.56
2018-11-14 17:30 | 207.76 | 207.75
2018-11-14 18:00 | 207.27 | 207.2
2018-11-14 18:30 | 213.76 | 213.63
2018-11-14 19:00 | 214.51 | 214.14
2018-11-14 19:30 | 211.24 | 210.94
2018-11-14 20:00 | 204.46 | 204.43
2018-11-14 20:30 | 182.99 | 182.96
2018-11-14 21:00 | 166.96 | 166.75
2018-11-14 21:30 | 177.02 | 176.32
2018-11-14 22:00 | 152.61 | 151.46
2018-11-14 22:30 | 151.89 | 150.58
2018-11-14 23:00 | 146.15 | 144.75
2018-11-14 23:30 | 113.52 | 111.88
2018-11-15 | 73.77 | 71.68
2018-11-15 00:30 | 77.83 | 76.23
2018-11-15 01:00 | 84.12 | 82.69
2018-11-15 01:30 | 91.22 | 90.09
2018-11-15 02:00 | 96.97 | 95.99
2018-11-15 02:30 | 89.08 | 88.04
2018-11-15 03:00 | 86.7 | 85.68
2018-11-15 03:30 | 88.08 | 87.26
2018-11-15 04:00 | 93.89 | 93.29
2018-11-15 04:30 | 73.36 | 71.96
2018-11-15 05:00 | 84.02 | 83.01
2018-11-15 05:30 | 81.36 | 80.24
2018-11-15 06:00 | 75.11 | 73.82
2018-11-15 06:30 | 76.37 | 75.46
2018-11-15 07:00 | 69.47 | 68.81
2018-11-15 07:30 | 93.2 | 93.16
2018-11-15 08:00 | 93.05 | 93.05
2018-11-15 08:30 | 81.7 | 81.67
2018-11-15 09:00 | 52.32 | 51.9
2018-11-15 09:30 | 56.45 | 55.92
2018-11-15 10:00 | 65.14 | 62.37
2018-11-15 10:30 | 54.75 | 42.68
2018-11-15 11:00 | 58.15 | 41.99
2018-11-15 11:30 | 53.91 | 35.26
2018-11-15 12:00 | 56.59 | 40.33
2018-11-15 12:30 | 80.57 | 69.49
2018-11-15 13:00 | 118.01 | 111.38
2018-11-15 13:30 | 137.47 | 132.19
2018-11-15 14:00 | 151.46 | 146.69
2018-11-15 14:30 | 185.88 | 181.77
2018-11-15 15:00 | 187.44 | 183.8
2018-11-15 15:30 | 189.75 | 186.6
2018-11-15 16:00 | 208.42 | 205.37
2018-11-15 16:30 | 210.38 | 207.13
2018-11-15 17:00 | 220.71 | 217.9
2018-11-15 17:30 | 223.19 | 221
2018-11-15 18:00 | 219.26 | 217.28
2018-11-15 18:30 | 222.55 | 220.93
2018-11-15 19:00 | 210.47 | 207.82
2018-11-15 19:30 | 211.24 | 209.14
2018-11-15 20:00 | 220.84 | 219.65
2018-11-15 20:30 | 215.21 | 215.19
2018-11-15 21:00 | 197.61 | 197.35
2018-11-15 21:30 | 189.2 | 189.18
2018-11-15 22:00 | 178.48 | 178.39
2018-11-15 22:30 | 175.18 | 175.01
2018-11-15 23:00 | 168.2 | 167.99
2018-11-15 23:30 | 122.01 | 121.48
2018-11-16 | 79.4 | 78.21
2018-11-16 00:30 | 69.38 | 67.59
2018-11-16 01:00 | 72.93 | 70.94
2018-11-16 01:30 | 65.69 | 63.34
2018-11-16 02:00 | 67.32 | 65.03
2018-11-16 02:30 | 61.49 | 58.97
2018-11-16 03:00 | 55.9 | 53.17
2018-11-16 03:30 | 60.34 | 57.91
2018-11-16 04:00 | 48.42 | 45.56
2018-11-16 04:30 | 50.29 | 47.75
2018-11-16 05:00 | 49.42 | 46.7
2018-11-16 05:30 | 42.95 | 40.34
2018-11-16 06:00 | 36.81 | 34.68
2018-11-16 06:30 | 45.47 | 45.24
2018-11-16 07:00 | 49.56 | 49.52
2018-11-16 07:30 | 60.87 | 59.1
2018-11-16 08:00 | 92.6 | 70.19
2018-11-16 08:30 | 95.94 | 69.23
2018-11-16 09:00 | 93.68 | 62.03
2018-11-16 09:30 | 94.19 | 64.93
2018-11-16 10:00 | 85.2 | 51.52
2018-11-16 10:30 | 81.97 | 45.68
2018-11-16 11:00 | 77.66 | 38.3
2018-11-16 11:30 | 79.24 | 42.86
2018-11-16 12:00 | 85.35 | 55.27
2018-11-16 12:30 | 100.44 | 76.59
2018-11-16 13:00 | 123.69 | 106.18
2018-11-16 13:30 | 142.29 | 127.35
2018-11-16 14:00 | 159.67 | 146.31
2018-11-16 14:30 | 178.88 | 166.97
2018-11-16 15:00 | 183.24 | 171.95
2018-11-16 15:30 | 168.83 | 156.98
2018-11-16 16:00 | 194.2 | 184.02
2018-11-16 16:30 | 219.47 | 210.64
2018-11-16 17:00 | 228.44 | 220.03
2018-11-16 17:30 | 226.97 | 219.87
2018-11-16 18:00 | 219.11 | 216.77
2018-11-16 18:30 | 216.02 | 213.9
2018-11-16 19:00 | 220.61 | 217.98
2018-11-16 19:30 | 218.38 | 215.94
2018-11-16 20:00 | 211.56 | 211.47
2018-11-16 20:30 | 207 | 206.99
2018-11-16 21:00 | 195.54 | 195.51
2018-11-16 21:30 | 180.92 | 180.92
2018-11-16 22:00 | 158.11 | 158.11
2018-11-16 22:30 | 144.47 | 144.44
2018-11-16 23:00 | 135.54 | 135.48
2018-11-16 23:30 | 106.17 | 105.91
2018-11-17 | 57.17 | 56.36
2018-11-17 00:30 | 52.79 | 51.55
2018-11-17 01:00 | 69.05 | 67.81
2018-11-17 01:30 | 62.39 | 60.77
2018-11-17 02:00 | 46.12 | 43.74
2018-11-17 02:30 | 31.58 | 27.98
2018-11-17 03:00 | 23.74 | 19.14
2018-11-17 03:30 | 22.53 | 16.67
2018-11-17 04:00 | 23.43 | 17.65
2018-11-17 04:30 | 46.51 | 43.81
2018-11-17 05:00 | 64.45 | 62.29
2018-11-17 05:30 | 89.88 | 88.59
2018-11-17 06:00 | 94.11 | 92.78
2018-11-17 06:30 | 86.74 | 84.9
2018-11-17 07:00 | 58.61 | 55.78
2018-11-17 07:30 | 44 | 41.53
2018-11-17 08:00 | 34.72 | 34.72
2018-11-17 08:30 | 65.89 | 65.81
2018-11-17 09:00 | 72.28 | 71.9
2018-11-17 09:30 | 52.96 | 44.53
2018-11-17 10:00 | 66.03 | 58.1
2018-11-17 10:30 | 60.02 | 50.29
2018-11-17 11:00 | 74.95 | 66.74
2018-11-17 11:30 | 87.6 | 80.93
2018-11-17 12:00 | 94.11 | 88.2
2018-11-17 12:30 | 116.96 | 112.3
2018-11-17 13:00 | 130.88 | 123.89
2018-11-17 13:30 | 122.98 | 104.88
2018-11-17 14:00 | 134.89 | 118.58
2018-11-17 14:30 | 148.94 | 134.11
2018-11-17 15:00 | 180.77 | 168.18
2018-11-17 15:30 | 195.9 | 184.27
2018-11-17 16:00 | 210.86 | 200.68
2018-11-17 16:30 | 220.53 | 210.87
2018-11-17 17:00 | 216.6 | 206.95
2018-11-17 17:30 | 210.24 | 200.44
2018-11-17 18:00 | 206.5 | 196.13
2018-11-17 18:30 | 210.38 | 201.19
2018-11-17 19:00 | 207.24 | 199.91
2018-11-17 19:30 | 197.86 | 194.83
2018-11-17 20:00 | 189.44 | 189.07
2018-11-17 20:30 | 181.24 | 181.23
2018-11-17 21:00 | 176.35 | 176.32
2018-11-17 21:30 | 169.04 | 168.98
2018-11-17 22:00 | 140.96 | 140.76
2018-11-17 22:30 | 151.03 | 150.75
2018-11-17 23:00 | 147.59 | 147.23
2018-11-17 23:30 | 114.39 | 113.74
2018-11-18 | 73.4 | 72.07
2018-11-18 00:30 | 68.21 | 66.32
2018-11-18 01:00 | 68.82 | 66.17
2018-11-18 01:30 | 70.77 | 67.95
2018-11-18 02:00 | 61.38 | 58.34
2018-11-18 02:30 | 49.11 | 45.43
2018-11-18 03:00 | 35.85 | 30.63
2018-11-18 03:30 | 43.21 | 39.16
2018-11-18 04:00 | 42.76 | 38.67
2018-11-18 04:30 | 45.31 | 41.7
2018-11-18 05:00 | 46.83 | 43.95
2018-11-18 05:30 | 47.67 | 45.21
2018-11-18 06:00 | 48.34 | 46.01
2018-11-18 06:30 | 40.11 | 36.95
2018-11-18 07:00 | 30 | 24.94
2018-11-18 07:30 | 31.04 | 25.71
2018-11-18 08:00 | 45.22 | 42.13
2018-11-18 08:30 | 70.52 | 69.75
2018-11-18 09:00 | 82.7 | 81.96
2018-11-18 09:30 | 66.93 | 65.58
2018-11-18 10:00 | 55.67 | 54.18
2018-11-18 10:30 | 58.96 | 58.96
2018-11-18 11:00 | 60.45 | 60.38
2018-11-18 11:30 | 60.94 | 60.65
2018-11-18 12:00 | 69.95 | 69.46
2018-11-18 12:30 | 50.36 | 49.78
2018-11-18 13:00 | 21.55 | 21.11
2018-11-18 13:30 | 23.21 | 22.78
2018-11-18 14:00 | 53.31 | 52.66
2018-11-18 14:30 | 54.94 | 54.21
2018-11-18 15:00 | 56.96 | 56.43
2018-11-18 15:30 | 55.23 | 54.66
2018-11-18 16:00 | 83.42 | 83.13
2018-11-18 16:30 | 121 | 120.77
2018-11-18 17:00 | 133.87 | 133.84
2018-11-18 17:30 | 144.56 | 144.43
2018-11-18 18:00 | 168.03 | 167.72
2018-11-18 18:30 | 184.43 | 184.08
2018-11-18 19:00 | 199.16 | 198.73
2018-11-18 19:30 | 190.81 | 190.42
2018-11-18 20:00 | 176.71 | 176.46
2018-11-18 20:30 | 159.91 | 159.74
2018-11-18 21:00 | 146.74 | 146.69
2018-11-18 21:30 | 153.25 | 152.28
2018-11-18 22:00 | 131.75 | 130.08
2018-11-18 22:30 | 137.27 | 135.8
2018-11-18 23:00 | 124.78 | 123.07
2018-11-18 23:30 | 101.17 | 99.5
2018-11-19 | 67.57 | 65.41
2018-11-19 00:30 | 61.63 | 59.69
2018-11-19 01:00 | 54.51 | 52.52
2018-11-19 01:30 | 61.94 | 60.27
2018-11-19 02:00 | 73.91 | 72.58
2018-11-19 02:30 | 74.04 | 71.71
2018-11-19 03:00 | 66.96 | 64.21
2018-11-19 03:30 | 58.46 | 55.4
2018-11-19 04:00 | 63.4 | 61.01
2018-11-19 04:30 | 58.54 | 56
2018-11-19 05:00 | 75.26 | 73.68
2018-11-19 05:30 | 91.13 | 89.4
2018-11-19 06:00 | 76.81 | 74.19
2018-11-19 06:30 | 87.53 | 85.56
2018-11-19 07:00 | 74.45 | 73.43
2018-11-19 07:30 | 81.45 | 80.56
2018-11-19 08:00 | 79.68 | 79.54
2018-11-19 08:30 | 66.97 | 66.57
2018-11-19 09:00 | 59.28 | 54.67
2018-11-19 09:30 | 89.21 | 62.14
2018-11-19 10:00 | 84.63 | 53.73
2018-11-19 10:30 | 104.61 | 81.33
2018-11-19 11:00 | 115.85 | 95.84
2018-11-19 11:30 | 111.2 | 99.99
2018-11-19 12:00 | 98.32 | 87.06
2018-11-19 12:30 | 75.87 | 60.63
2018-11-19 13:00 | 64.66 | 44.61
2018-11-19 13:30 | 75.19 | 58.72
2018-11-19 14:00 | 97.86 | 85.81
2018-11-19 14:30 | 110.2 | 99.87
2018-11-19 15:00 | 123.68 | 114.88
2018-11-19 15:30 | 111.28 | 101.67
2018-11-19 16:00 | 117.6 | 109.42
2018-11-19 16:30 | 135.58 | 129.3
2018-11-19 17:00 | 131.24 | 125.38
2018-11-19 17:30 | 143.7 | 138.95
2018-11-19 18:00 | 187.24 | 184.03
2018-11-19 18:30 | 201.2 | 198.53
2018-11-19 19:00 | 213.65 | 210.35
2018-11-19 19:30 | 206.51 | 203.48
2018-11-19 20:00 | 199.46 | 196.86
2018-11-19 20:30 | 187.14 | 187.09
2018-11-19 21:00 | 183.44 | 183.42
2018-11-19 21:30 | 173.62 | 173.53
2018-11-19 22:00 | 164.56 | 164.32
2018-11-19 22:30 | 156 | 155.61
2018-11-19 23:00 | 157.47 | 156.87
2018-11-19 23:30 | 120.93 | 119.92
2018-11-20 | 83.25 | 81.13
2018-11-20 00:30 | 78.36 | 75.86
2018-11-20 01:00 | 60.11 | 56.56
2018-11-20 01:30 | 72.44 | 69.85
2018-11-20 02:00 | 83.51 | 81.41
2018-11-20 02:30 | 86.32 | 84.38
2018-11-20 03:00 | 59.05 | 56.07
2018-11-20 03:30 | 46.3 | 42.07
2018-11-20 04:00 | 46.56 | 43.19
2018-11-20 04:30 | 51.91 | 49.21
2018-11-20 05:00 | 54.01 | 51.7
2018-11-20 05:30 | 58.25 | 55.52
2018-11-20 06:00 | 56.15 | 52.99
2018-11-20 06:30 | 83.82 | 81.57
2018-11-20 07:00 | 77.06 | 75.82
2018-11-20 07:30 | 79.61 | 78.63
2018-11-20 08:00 | 71.95 | 71.87
2018-11-20 08:30 | 60.56 | 59.74
2018-11-20 09:00 | 63.71 | 62.5
2018-11-20 09:30 | 68.78 | 68.77
2018-11-20 10:00 | 65.27 | 65.27
2018-11-20 10:30 | 67.65 | 67.65
2018-11-20 11:00 | 63.5 | 63.48
2018-11-20 11:30 | 57.91 | 57.88
2018-11-20 12:00 | 54.5 | 54.47
2018-11-20 12:30 | 45.43 | 45.4
2018-11-20 13:00 | 59.77 | 59.75
2018-11-20 13:30 | 66.4 | 66.38
2018-11-20 14:00 | 85.11 | 85.09
2018-11-20 14:30 | 83.52 | 83.49
2018-11-20 15:00 | 87.51 | 87.5
2018-11-20 15:30 | 122.83 | 122.83
2018-11-20 16:00 | 152 | 152
2018-11-20 16:30 | 145.44 | 145.42
2018-11-20 17:00 | 122.01 | 121.99
2018-11-20 17:30 | 122.77 | 122.77
2018-11-20 18:00 | 121.94 | 121.93
2018-11-20 18:30 | 122.72 | 122.68
2018-11-20 19:00 | 130.63 | 130.52
2018-11-20 19:30 | 128.32 | 128.14
2018-11-20 20:00 | 128.1 | 128.09
2018-11-20 20:30 | 155.32 | 155.31
2018-11-20 21:00 | 117.61 | 117.52
2018-11-20 21:30 | 112.99 | 112.45
2018-11-20 22:00 | 153.98 | 153.25
2018-11-20 22:30 | 151.52 | 150.8
2018-11-20 23:00 | 153.14 | 152.32
2018-11-20 23:30 | 129.2 | 127.76
2018-11-21 | 83.45 | 81.91
2018-11-21 00:30 | 94.09 | 92.56
2018-11-21 01:00 | 97.67 | 96.26
2018-11-21 01:30 | 108.13 | 106.91
2018-11-21 02:00 | 102.92 | 101.64
2018-11-21 02:30 | 95.24 | 93.82
2018-11-21 03:00 | 89.69 | 88.03
2018-11-21 03:30 | 79.21 | 77.14
2018-11-21 04:00 | 84.04 | 82.46
2018-11-21 04:30 | 83.28 | 81.88
2018-11-21 05:00 | 77.98 | 76.5
2018-11-21 05:30 | 114.79 | 113.86
2018-11-21 06:00 | 122.87 | 121.82
2018-11-21 06:30 | 146.85 | 146.2
2018-11-21 07:00 | 151.59 | 151.54
2018-11-21 07:30 | 149.21 | 149.18
2018-11-21 08:00 | 124.14 | 123.79
2018-11-21 08:30 | 108.52 | 101.9
2018-11-21 09:00 | 112.94 | 91.07
2018-11-21 09:30 | 112.32 | 88.58
2018-11-21 10:00 | 115.25 | 91.24
2018-11-21 10:30 | 125.04 | 102.22
2018-11-21 11:00 | 139.07 | 118.47
2018-11-21 11:30 | 151.26 | 134.99
2018-11-21 12:00 | 172.2 | 158.1
2018-11-21 12:30 | 181.6 | 168.24
2018-11-21 13:00 | 192.27 | 179.32
2018-11-21 13:30 | 200.83 | 188.95
2018-11-21 14:00 | 207.09 | 195.52
2018-11-21 14:30 | 224 | 212.37
2018-11-21 15:00 | 200.6 | 187.3
2018-11-21 15:30 | 156.12 | 140.35
2018-11-21 16:00 | 156.13 | 140.83
2018-11-21 16:30 | 157.96 | 143.49
2018-11-21 17:00 | 155.66 | 141.93
2018-11-21 17:30 | 153.75 | 141.16
2018-11-21 18:00 | 150.77 | 139.1
2018-11-21 18:30 | 152.66 | 141.19
2018-11-21 19:00 | 159.56 | 147.55
2018-11-21 19:30 | 153.83 | 142.49
2018-11-21 20:00 | 156.34 | 146.13
2018-11-21 20:30 | 148.76 | 139.44
2018-11-21 21:00 | 137.97 | 129.02
2018-11-21 21:30 | 119.57 | 119.56
2018-11-21 22:00 | 125.25 | 124.88
2018-11-21 22:30 | 140.51 | 139.86
2018-11-21 23:00 | 152.01 | 151.33
2018-11-21 23:30 | 108.23 | 107.69
2018-11-22 | 77.64 | 76.71
2018-11-22 00:30 | 68.46 | 67.04
2018-11-22 01:00 | 84.2 | 82.76
2018-11-22 01:30 | 126.13 | 124.85
2018-11-22 02:00 | 126.17 | 125.16
2018-11-22 02:30 | 123.15 | 122.14
2018-11-22 03:00 | 123.67 | 122.68
2018-11-22 03:30 | 123.66 | 122.72
2018-11-22 04:00 | 123.9 | 123.01
2018-11-22 04:30 | 126.39 | 125.57
2018-11-22 05:00 | 121.58 | 120.77
2018-11-22 05:30 | 119.4 | 118.72
2018-11-22 06:00 | 91.7 | 91.25
2018-11-22 06:30 | 83.22 | 83.21
2018-11-22 07:00 | 86.49 | 86.19
2018-11-22 07:30 | 94.6 | 86.46
2018-11-22 08:00 | 102.59 | 93.33
2018-11-22 08:30 | 96.84 | 91.18
2018-11-22 09:00 | 105.33 | 99.5
2018-11-22 09:30 | 94.17 | 86.54
2018-11-22 10:00 | 101.01 | 90.46
2018-11-22 10:30 | 89.84 | 81.79
2018-11-22 11:00 | 123.65 | 110.38
2018-11-22 11:30 | 166.24 | 163.06
2018-11-22 12:00 | 184.7 | 183.83
2018-11-22 12:30 | 172.78 | 172.09
2018-11-22 13:00 | 156.36 | 155.77
2018-11-22 13:30 | 144.33 | 143.61
2018-11-22 14:00 | 143.13 | 142.63
2018-11-22 14:30 | 157.13 | 155.77
2018-11-22 15:00 | 161.53 | 158.75
2018-11-22 15:30 | 177.25 | 174.6
2018-11-22 16:00 | 202.04 | 199.27
2018-11-22 16:30 | 215.76 | 206.19
2018-11-22 17:00 | 207.2 | 196.63
2018-11-22 17:30 | 155.68 | 142.85
2018-11-22 18:00 | 149.17 | 137.04
2018-11-22 18:30 | 147.54 | 136.26
2018-11-22 19:00 | 153.05 | 141.06
2018-11-22 19:30 | 154.8 | 143.85
2018-11-22 20:00 | 151.51 | 141.67
2018-11-22 20:30 | 147.1 | 137.83
2018-11-22 21:00 | 132.22 | 125.17
2018-11-22 21:30 | 120.36 | 120.21
2018-11-22 22:00 | 160.98 | 160.75
2018-11-22 22:30 | 157.06 | 156.66
2018-11-22 23:00 | 154.08 | 153.63
2018-11-22 23:30 | 133 | 132.72
2018-11-23 | 108.63 | 108.12
2018-11-23 00:30 | 108.02 | 107.21
2018-11-23 01:00 | 110.68 | 109.57
2018-11-23 01:30 | 121.21 | 120.11
2018-11-23 02:00 | 115.05 | 113.83
2018-11-23 02:30 | 106.91 | 105.58
2018-11-23 03:00 | 109.44 | 108.06
2018-11-23 03:30 | 109.4 | 108
2018-11-23 04:00 | 111.67 | 110.27
2018-11-23 04:30 | 113.74 | 112.44
2018-11-23 05:00 | 116.16 | 114.77
2018-11-23 05:30 | 121.24 | 120.06
2018-11-23 06:00 | 108.8 | 107.8
2018-11-23 06:30 | 113.63 | 113.17
2018-11-23 07:00 | 104.89 | 104.75
2018-11-23 07:30 | 109.19 | 109.18
2018-11-23 08:00 | 139.38 | 139.32
2018-11-23 08:30 | 126.01 | 126.01
2018-11-23 09:00 | 117.21 | 117.11
2018-11-23 09:30 | 117.21 | 117.14
2018-11-23 10:00 | 91.18 | 91.13
2018-11-23 10:30 | 86.51 | 86.5
2018-11-23 11:00 | 85.94 | 85.94
2018-11-23 11:30 | 66.86 | 66.86
2018-11-23 12:00 | 80.71 | 80.71
2018-11-23 12:30 | 88.54 | 88.54
2018-11-23 13:00 | 92.65 | 92.65
2018-11-23 13:30 | 118.95 | 118.93
2018-11-23 14:00 | 149.5 | 149.48
2018-11-23 14:30 | 155.36 | 155.32
2018-11-23 15:00 | 171.06 | 171.05
2018-11-23 15:30 | 173.02 | 173.02
2018-11-23 16:00 | 179.01 | 179.01
2018-11-23 16:30 | 177.04 | 177.04
2018-11-23 17:00 | 145.66 | 145.63
2018-11-23 17:30 | 125.5 | 125.48
2018-11-23 18:00 | 120.31 | 120.31
2018-11-23 18:30 | 118.2 | 118.19
2018-11-23 19:00 | 124.29 | 124.28
2018-11-23 19:30 | 123.97 | 123.94
2018-11-23 20:00 | 129.87 | 129.83
2018-11-23 20:30 | 167.5 | 167.48
2018-11-23 21:00 | 117.47 | 116.99
2018-11-23 21:30 | 151.51 | 151.07
2018-11-23 22:00 | 160.96 | 160.29
2018-11-23 22:30 | 160.79 | 159.95
2018-11-23 23:00 | 159.87 | 159
2018-11-23 23:30 | 145.45 | 144.54
2018-11-24 | 123.29 | 122.47
2018-11-24 00:30 | 113.18 | 112.12
2018-11-24 01:00 | 107.96 | 106.45
2018-11-24 01:30 | 90.89 | 88.68
2018-11-24 02:00 | 93.19 | 90.85
2018-11-24 02:30 | 89.1 | 86.58
2018-11-24 03:00 | 87.5 | 85.05
2018-11-24 03:30 | 105.88 | 104.03
2018-11-24 04:00 | 109.03 | 107.19
2018-11-24 04:30 | 83.54 | 81.11
2018-11-24 05:00 | 74.12 | 71.76
2018-11-24 05:30 | 65.13 | 63
2018-11-24 06:00 | 65.87 | 63.74
2018-11-24 06:30 | 51.92 | 49.54
2018-11-24 07:00 | 25.95 | 21.61
2018-11-24 07:30 | 18.27 | 15.13
2018-11-24 08:00 | 17.01 | 10.28
2018-11-24 08:30 | 18.23 | 13.58
2018-11-24 09:00 | 24.83 | 22.25
2018-11-24 09:30 | 22.03 | 21.33
2018-11-24 10:00 | 17.91 | 16.97
2018-11-24 10:30 | 25.43 | 24.59
2018-11-24 11:00 | 38.02 | 37.43
2018-11-24 11:30 | 15.02 | 12.61
2018-11-24 12:00 | 23.03 | 21.34
2018-11-24 12:30 | 21.28 | 19.57
2018-11-24 13:00 | 25.42 | 23.85
2018-11-24 13:30 | 43.62 | 42.72
2018-11-24 14:00 | 53.98 | 53.12
2018-11-24 14:30 | 67.35 | 66.65
2018-11-24 15:00 | 80.07 | 80.06
2018-11-24 15:30 | 108.94 | 108.56
2018-11-24 16:00 | 130.03 | 129.77
2018-11-24 16:30 | 147.27 | 147.06
2018-11-24 17:00 | 161.2 | 161.01
2018-11-24 17:30 | 122.18 | 121.95
2018-11-24 18:00 | 103.02 | 102.72
2018-11-24 18:30 | 103.02 | 102.7
2018-11-24 19:00 | 108.61 | 108.38
2018-11-24 19:30 | 109.2 | 108.97
2018-11-24 20:00 | 156.01 | 155.85
2018-11-24 20:30 | 165.8 | 165.73
2018-11-24 21:00 | 125.6 | 125.6
2018-11-24 21:30 | 151.01 | 151
2018-11-24 22:00 | 142.91 | 142.81
2018-11-24 22:30 | 158.67 | 158.52
2018-11-24 23:00 | 159.12 | 158.86
2018-11-24 23:30 | 133.26 | 132.76
2018-11-25 | 104.44 | 103.53
2018-11-25 00:30 | 87.31 | 86.01
2018-11-25 01:00 | 68.95 | 67.25
2018-11-25 01:30 | 63.07 | 60.97
2018-11-25 02:00 | 41.06 | 37.71
2018-11-25 02:30 | 29.4 | 23.95
2018-11-25 03:00 | 28.5 | 22.62
2018-11-25 03:30 | 27.41 | 20.77
2018-11-25 04:00 | 24.26 | 16.69
2018-11-25 04:30 | 35.02 | 32.6
2018-11-25 05:00 | 55.87 | 55.8
2018-11-25 05:30 | 65.41 | 65.4
2018-11-25 06:00 | 54.31 | 54.25
2018-11-25 06:30 | 36.37 | 36.15
2018-11-25 07:00 | 15.66 | 15.66
2018-11-25 07:30 | 11.44 | 11.33
2018-11-25 08:00 | 21.76 | 21.63
2018-11-25 08:30 | 19.64 | 19.59
2018-11-25 09:00 | 25.08 | 24.95
2018-11-25 09:30 | 43.91 | 43.45
2018-11-25 10:00 | 48.7 | 47.93
2018-11-25 10:30 | 52.47 | 51.55
2018-11-25 11:00 | 63.29 | 62.59
2018-11-25 11:30 | 89.05 | 89.02
2018-11-25 12:00 | 80.21 | 80.2
2018-11-25 12:30 | 71.35 | 71.35
2018-11-25 13:00 | 102.91 | 102.83
2018-11-25 13:30 | 134.48 | 134.4
2018-11-25 14:00 | 168.95 | 168.94
2018-11-25 14:30 | 186.04 | 185.51
2018-11-25 15:00 | 184.76 | 184.31
2018-11-25 15:30 | 183.86 | 183.5
2018-11-25 16:00 | 190.72 | 190.43
2018-11-25 16:30 | 190.7 | 190.5
2018-11-25 17:00 | 191.64 | 191.45
2018-11-25 17:30 | 184.47 | 184.3
2018-11-25 18:00 | 178.72 | 178.56
2018-11-25 18:30 | 180.98 | 180.84
2018-11-25 19:00 | 189 | 188.7
2018-11-25 19:30 | 194.66 | 194.4
2018-11-25 20:00 | 204.89 | 204.72
2018-11-25 20:30 | 203.62 | 203.54
2018-11-25 21:00 | 185.94 | 185.93
2018-11-25 21:30 | 183.06 | 183.06
2018-11-25 22:00 | 156.97 | 156.92
2018-11-25 22:30 | 154.74 | 154.67
2018-11-25 23:00 | 161.14 | 161.02
2018-11-25 23:30 | 146.66 | 146.43
2018-11-26 | 137.35 | 136.94
2018-11-26 00:30 | 125.42 | 124.96
2018-11-26 01:00 | 112.23 | 111.71
2018-11-26 01:30 | 91.75 | 91.42
2018-11-26 02:00 | 82.49 | 82.42
2018-11-26 02:30 | 91.79 | 91.74
2018-11-26 03:00 | 78.91 | 78.83
2018-11-26 03:30 | 75.23 | 75.17
2018-11-26 04:00 | 72.95 | 72.91
2018-11-26 04:30 | 75.63 | 75.61
2018-11-26 05:00 | 87.22 | 87.22
2018-11-26 05:30 | 82.35 | 82.33
2018-11-26 06:00 | 73.45 | 73.44
2018-11-26 06:30 | 81.84 | 81.83
2018-11-26 07:00 | 65.93 | 65.82
2018-11-26 07:30 | 81.96 | 81.29
2018-11-26 08:00 | 107.96 | 107.52
2018-11-26 08:30 | 99.95 | 99.39
2018-11-26 09:00 | 89.24 | 88.16
2018-11-26 09:30 | 98.88 | 97.81
2018-11-26 10:00 | 101.03 | 100.16
2018-11-26 10:30 | 106.93 | 106.03
2018-11-26 11:00 | 119.6 | 118.7
2018-11-26 11:30 | 125.18 | 124.34
2018-11-26 12:00 | 127.42 | 126.66
2018-11-26 12:30 | 143.83 | 143.26
2018-11-26 13:00 | 145.91 | 145.29
2018-11-26 13:30 | 164.85 | 164.27
2018-11-26 14:00 | 185.34 | 184.87
2018-11-26 14:30 | 188.45 | 187.98
2018-11-26 15:00 | 188.44 | 187.95
2018-11-26 15:30 | 197.24 | 196.87
2018-11-26 16:00 | 210.24 | 209.98
2018-11-26 16:30 | 209.78 | 209.6
2018-11-26 17:00 | 200.43 | 200.33
2018-11-26 17:30 | 185.07 | 184.92
2018-11-26 18:00 | 139.49 | 139.23
2018-11-26 18:30 | 158.7 | 158.38
2018-11-26 19:00 | 137.95 | 137.47
2018-11-26 19:30 | 166.89 | 166.33
2018-11-26 20:00 | 194.39 | 194.19
2018-11-26 20:30 | 202.03 | 201.85
2018-11-26 21:00 | 181.06 | 181.04
2018-11-26 21:30 | 181.28 | 181.22
2018-11-26 22:00 | 160.48 | 160.33
2018-11-26 22:30 | 150.91 | 150.73
2018-11-26 23:00 | 133.13 | 132.85
2018-11-26 23:30 | 98.78 | 98.55
2018-11-27 | 60.16 | 59.91
2018-11-27 00:30 | 49.79 | 49.63
2018-11-27 01:00 | 44.03 | 43.87
2018-11-27 01:30 | 30.27 | 30.17
2018-11-27 02:00 | 23.8 | 23.76
2018-11-27 02:30 | 26.25 | 26.22
2018-11-27 03:00 | 26.36 | 26.36
2018-11-27 03:30 | 24.81 | 24.81
2018-11-27 04:00 | 29.74 | 29.69
2018-11-27 04:30 | 40.48 | 40.45
2018-11-27 05:00 | 62.96 | 62.92
2018-11-27 05:30 | 48.85 | 48.84
2018-11-27 06:00 | 74.39 | 74.39
2018-11-27 06:30 | 74.13 | 74.11
2018-11-27 07:00 | 77.51 | 77.39
2018-11-27 07:30 | 71.92 | 63.73
2018-11-27 08:00 | 77.08 | 65.4
2018-11-27 08:30 | 93.09 | 71.8
2018-11-27 09:00 | 97.47 | 74.78
2018-11-27 09:30 | 114.08 | 89.42
2018-11-27 10:00 | 120.15 | 92.74
2018-11-27 10:30 | 118.15 | 90.48
2018-11-27 11:00 | 126.23 | 99.75
2018-11-27 11:30 | 128.98 | 103.28
2018-11-27 12:00 | 134.17 | 109.69
2018-11-27 12:30 | 136.84 | 113.07
2018-11-27 13:00 | 134.3 | 109.88
2018-11-27 13:30 | 131.38 | 105.49
2018-11-27 14:00 | 137.4 | 113.06
2018-11-27 14:30 | 142.67 | 119.38
2018-11-27 15:00 | 134.87 | 109.94
2018-11-27 15:30 | 132.01 | 106.94
2018-11-27 16:00 | 115.18 | 86.26
2018-11-27 16:30 | 105.66 | 86.59
2018-11-27 17:00 | 97.93 | 92.05
2018-11-27 17:30 | 97.6 | 93.08
2018-11-27 18:00 | 90.55 | 90
2018-11-27 18:30 | 94.89 | 90.91
2018-11-27 19:00 | 105.71 | 98.09
2018-11-27 19:30 | 104.62 | 96.75
2018-11-27 20:00 | 145.73 | 141.22
2018-11-27 20:30 | 156.37 | 152.65
2018-11-27 21:00 | 127.91 | 125.17
2018-11-27 21:30 | 141.78 | 139.71
2018-11-27 22:00 | 150.73 | 150.33
2018-11-27 22:30 | 144.49 | 144.49
2018-11-27 23:00 | 146.75 | 146.75
2018-11-27 23:30 | 130.33 | 130.32
2018-11-28 | 75.13 | 75.08
2018-11-28 00:30 | 39.4 | 37.24
2018-11-28 01:00 | 41.72 | 39.66
2018-11-28 01:30 | 56.19 | 54.76
2018-11-28 02:00 | 57.57 | 56.3
2018-11-28 02:30 | 58.67 | 57.5
2018-11-28 03:00 | 67.48 | 66.56
2018-11-28 03:30 | 63.16 | 62.29
2018-11-28 04:00 | 56.52 | 55.49
2018-11-28 04:30 | 53.93 | 52.9
2018-11-28 05:00 | 43.02 | 41.68
2018-11-28 05:30 | 49.16 | 47.99
2018-11-28 06:00 | 42.82 | 41.8
2018-11-28 06:30 | 61.22 | 61.19
2018-11-28 07:00 | 66.91 | 66.78
2018-11-28 07:30 | 85.87 | 81.77
2018-11-28 08:00 | 125.01 | 104.08
2018-11-28 08:30 | 144.45 | 124.86
2018-11-28 09:00 | 154.84 | 135.02
2018-11-28 09:30 | 167.36 | 150.98
2018-11-28 10:00 | 166.5 | 152.67
2018-11-28 10:30 | 159 | 144.41
2018-11-28 11:00 | 154.44 | 140.52
2018-11-28 11:30 | 158.25 | 144.87
2018-11-28 12:00 | 164.94 | 151.28
2018-11-28 12:30 | 160.11 | 146.82
2018-11-28 13:00 | 154.56 | 145.44
2018-11-28 13:30 | 153.41 | 148.19
2018-11-28 14:00 | 190.98 | 186.27
2018-11-28 14:30 | 186.51 | 181.33
2018-11-28 15:00 | 187.06 | 182.13
2018-11-28 15:30 | 191.13 | 186.01
2018-11-28 16:00 | 183.29 | 177.93
2018-11-28 16:30 | 163.32 | 157.08
2018-11-28 17:00 | 125.4 | 117.2
2018-11-28 17:30 | 119.54 | 111.01
2018-11-28 18:00 | 112.95 | 103.98
2018-11-28 18:30 | 110.29 | 102.37
2018-11-28 19:00 | 110.45 | 104.23
2018-11-28 19:30 | 109.1 | 104.16
2018-11-28 20:00 | 105.69 | 104.09
2018-11-28 20:30 | 98.68 | 98.27
2018-11-28 21:00 | 85.36 | 84.36
2018-11-28 21:30 | 86.07 | 84.91
2018-11-28 22:00 | 83.79 | 82.68
2018-11-28 22:30 | 81.23 | 80.65
2018-11-28 23:00 | 47.1 | 47.1
2018-11-28 23:30 | 27.3 | 27.24
2018-11-29 | 16.02 | 16.02
2018-11-29 00:30 | 11.98 | 8.6
2018-11-29 01:00 | 11.94 | 9.55
2018-11-29 01:30 | 35.73 | 35.55
2018-11-29 02:00 | 51.35 | 51.27
2018-11-29 02:30 | 50.69 | 50.6
2018-11-29 03:00 | 49.38 | 49.21
2018-11-29 03:30 | 40.71 | 40.25
2018-11-29 04:00 | 16.43 | 14.44
2018-11-29 04:30 | 16.32 | 13.64
2018-11-29 05:00 | 20.59 | 17.3
2018-11-29 05:30 | 20.95 | 17.38
2018-11-29 06:00 | 21.23 | 15.91
2018-11-29 06:30 | 39.25 | 36.2
2018-11-29 07:00 | 60.47 | 57.74
2018-11-29 07:30 | 84.28 | 81.75
2018-11-29 08:00 | 71.21 | 68.36
2018-11-29 08:30 | 43.08 | 38.92
2018-11-29 09:00 | 48.18 | 45.14
2018-11-29 09:30 | 42.65 | 38.47
2018-11-29 10:00 | 73.89 | 57.99
2018-11-29 10:30 | 71.74 | 57
2018-11-29 11:00 | 81 | 66.73
2018-11-29 11:30 | 96.79 | 84.93
2018-11-29 12:00 | 102.57 | 91.48
2018-11-29 12:30 | 112.23 | 102.24
2018-11-29 13:00 | 124.95 | 116.15
2018-11-29 13:30 | 130.53 | 122.21
2018-11-29 14:00 | 152.84 | 145.62
2018-11-29 14:30 | 110.33 | 100.41
2018-11-29 15:00 | 102.2 | 91.88
2018-11-29 15:30 | 101.97 | 92.04
2018-11-29 16:00 | 104.03 | 96.7
2018-11-29 16:30 | 104.04 | 97.41
2018-11-29 17:00 | 102.8 | 96.45
2018-11-29 17:30 | 99.34 | 94.94
2018-11-29 18:00 | 93 | 92.14
2018-11-29 18:30 | 89.5 | 88.8
2018-11-29 19:00 | 87.13 | 86.18
2018-11-29 19:30 | 94.11 | 93.24
2018-11-29 20:00 | 100.79 | 100.24
2018-11-29 20:30 | 101.01 | 96.21
2018-11-29 21:00 | 95.65 | 88.79
2018-11-29 21:30 | 90.47 | 84.46
2018-11-29 22:00 | 79.51 | 79.29
2018-11-29 22:30 | 81.61 | 81.21
2018-11-29 23:00 | 77.29 | 76.85
2018-11-29 23:30 | 50.02 | 49.36
2018-11-30 | 15.67 | 15.18
2018-11-30 00:30 | 16.87 | 16.09
2018-11-30 01:00 | 7.09 | 4.3
2018-11-30 01:30 | 8.32 | 5.29
2018-11-30 02:00 | 7.28 | 2.49
2018-11-30 02:30 | 7.13 | 2.29
2018-11-30 03:00 | 6.99 | 1.67
2018-11-30 03:30 | 6.89 | 1.29
2018-11-30 04:00 | 6.68 | 0.35
2018-11-30 04:30 | 6.67 | 0.59
2018-11-30 05:00 | 7.08 | -2.22
2018-11-30 05:30 | 10.88 | 9.03
2018-11-30 06:00 | 8.61 | 7.63
2018-11-30 06:30 | 18.84 | 16.82
2018-11-30 07:00 | 29.08 | 22.83
2018-11-30 07:30 | 33.5 | 32.38
2018-11-30 08:00 | 41.46 | 39.85
2018-11-30 08:30 | 39.74 | 37.04
2018-11-30 09:00 | 42.68 | 39.13
2018-11-30 09:30 | 49.73 | 36.21
2018-11-30 10:00 | 51.71 | 38.31
2018-11-30 10:30 | 90.22 | 80.9
2018-11-30 11:00 | 136.26 | 130.01
2018-11-30 11:30 | 115.65 | 109.93
2018-11-30 12:00 | 137.72 | 133.78
2018-11-30 12:30 | 147.72 | 144.22
2018-11-30 13:00 | 147.23 | 144.13
2018-11-30 13:30 | 116.33 | 111.93
2018-11-30 14:00 | 136.58 | 132.63
2018-11-30 14:30 | 155.5 | 152.33
2018-11-30 15:00 | 138.97 | 135.72
2018-11-30 15:30 | 100.79 | 96.32
2018-11-30 16:00 | 99.95 | 95.58
2018-11-30 16:30 | 102.98 | 98.92
2018-11-30 17:00 | 103.95 | 100.3
2018-11-30 17:30 | 101.35 | 98.06
2018-11-30 18:00 | 96.31 | 93.41
2018-11-30 18:30 | 93.89 | 91.05
2018-11-30 19:00 | 102.48 | 94.41
2018-11-30 19:30 | 104.9 | 96.65
2018-11-30 20:00 | 103.77 | 96.06
2018-11-30 20:30 | 99.6 | 92
2018-11-30 21:00 | 92.27 | 84.84
2018-11-30 21:30 | 88.87 | 82.27
2018-11-30 22:00 | 88.08 | 82.53
2018-11-30 22:30 | 81.62 | 78.44
2018-11-30 23:00 | 81.18 | 79.98
2018-11-30 23:30 | 67.18 | 66.01
2018-12-01 | 50.19 | 48.84
2018-12-01 00:30 | 44.29 | 42.67
2018-12-01 01:00 | 38.28 | 36.67
2018-12-01 01:30 | 38.11 | 36.69
2018-12-01 02:00 | 31.17 | 29.61
2018-12-01 02:30 | 24.49 | 22.43
2018-12-01 03:00 | 21.46 | 19.12
2018-12-01 03:30 | 38.87 | 38.52
2018-12-01 04:00 | 40.37 | 39.5
2018-12-01 04:30 | 28.86 | 27.69
2018-12-01 05:00 | 40.01 | 38.95
2018-12-01 05:30 | 45.43 | 44.61
2018-12-01 06:00 | 47.03 | 46.48
2018-12-01 06:30 | 44.09 | 43.85
2018-12-01 07:00 | 27.94 | 27.93
2018-12-01 07:30 | 37.32 | 37.12
2018-12-01 08:00 | 61.23 | 56.75
2018-12-01 08:30 | 84.78 | 62.3
2018-12-01 09:00 | 109.67 | 88.69
2018-12-01 09:30 | 137.37 | 120.35
2018-12-01 10:00 | 154.64 | 139.93
2018-12-01 10:30 | 161.67 | 146.78
2018-12-01 11:00 | 160.07 | 148.53
2018-12-01 11:30 | 161.09 | 151.46
2018-12-01 12:00 | 164.11 | 154.38
2018-12-01 12:30 | 167.8 | 158.09
2018-12-01 13:00 | 172.37 | 162.66
2018-12-01 13:30 | 177.18 | 167.18
2018-12-01 14:00 | 171.72 | 161.09
2018-12-01 14:30 | 161.87 | 150.06
2018-12-01 15:00 | 127.24 | 111.22
2018-12-01 15:30 | 110.48 | 91.45
2018-12-01 16:00 | 113.79 | 95.48
2018-12-01 16:30 | 119 | 97.5
2018-12-01 17:00 | 122.48 | 94.92
2018-12-01 17:30 | 112.32 | 83.14
2018-12-01 18:00 | 104.21 | 74.29
2018-12-01 18:30 | 101.77 | 74.61
2018-12-01 19:00 | 107.69 | 81.42
2018-12-01 19:30 | 110.78 | 85.5
2018-12-01 20:00 | 114.42 | 92.29
2018-12-01 20:30 | 108.52 | 87.42
2018-12-01 21:00 | 98.4 | 80.14
2018-12-01 21:30 | 90.91 | 80.61
2018-12-01 22:00 | 83.42 | 79.61
2018-12-01 22:30 | 86.5 | 86.36
2018-12-01 23:00 | 97.34 | 97.21
2018-12-01 23:30 | 110.74 | 110.71
2018-12-02 | 87.17 | 87.09
2018-12-02 00:30 | 90.56 | 90.31
2018-12-02 01:00 | 94.57 | 94.36
2018-12-02 01:30 | 81.22 | 80.93
2018-12-02 02:00 | 74.69 | 74.27
2018-12-02 02:30 | 92.99 | 92.64
2018-12-02 03:00 | 81.73 | 81.3
2018-12-02 03:30 | 73.28 | 72.73
2018-12-02 04:00 | 65.74 | 65.07
2018-12-02 04:30 | 66.85 | 66.15
2018-12-02 05:00 | 62.97 | 62.2
2018-12-02 05:30 | 44.97 | 43.97
2018-12-02 06:00 | 47.29 | 46.83
2018-12-02 06:30 | 28.83 | 28.46
2018-12-02 07:00 | 16.86 | 16.74
2018-12-02 07:30 | 20.09 | 20.06
2018-12-02 08:00 | 35.91 | 21.14
2018-12-02 08:30 | 67.37 | 30.14
2018-12-02 09:00 | 77.46 | 44.79
2018-12-02 09:30 | 118.2 | 99.7
2018-12-02 10:00 | 166.09 | 152.22
2018-12-02 10:30 | 169.46 | 155.5
2018-12-02 11:00 | 158.81 | 148.42
2018-12-02 11:30 | 155.84 | 144.75
2018-12-02 12:00 | 141.18 | 127.57
2018-12-02 12:30 | 120.73 | 98.18
2018-12-02 13:00 | 167.87 | 147.07
2018-12-02 13:30 | 163.41 | 141.18
2018-12-02 14:00 | 123.24 | 93.6
2018-12-02 14:30 | 127.73 | 98.87
2018-12-02 15:00 | 131.52 | 102.61
2018-12-02 15:30 | 136.39 | 96.39
2018-12-02 16:00 | 140.35 | 100.73
2018-12-02 16:30 | 129.61 | 85.18
2018-12-02 17:00 | 122.56 | 74.29
2018-12-02 17:30 | 116.75 | 71.99
2018-12-02 18:00 | 115.13 | 72.63
2018-12-02 18:30 | 115.97 | 76.22
2018-12-02 19:00 | 124.38 | 86.68
2018-12-02 19:30 | 110.8 | 97.09
2018-12-02 20:00 | 116.55 | 112.49
2018-12-02 20:30 | 116.74 | 113.91
2018-12-02 21:00 | 82.71 | 78.86
2018-12-02 21:30 | 84.99 | 81.29
2018-12-02 22:00 | 95.53 | 92.72
2018-12-02 22:30 | 90.72 | 85.31
2018-12-02 23:00 | 88.91 | 82.78
2018-12-02 23:30 | 78.65 | 72.93
2018-12-03 | 60.53 | 60.53
2018-12-03 00:30 | 53.8 | 51.07
2018-12-03 01:00 | 74.49 | 73.35
2018-12-03 01:30 | 115.03 | 114.37
2018-12-03 02:00 | 107.59 | 106.9
2018-12-03 02:30 | 111.51 | 110.95
2018-12-03 03:00 | 112.18 | 111.54
2018-12-03 03:30 | 108.76 | 108.1
2018-12-03 04:00 | 78.33 | 77.46
2018-12-03 04:30 | 82.54 | 82.11
2018-12-03 05:00 | 67.63 | 67.03
2018-12-03 05:30 | 54.56 | 53.44
2018-12-03 06:00 | 44.43 | 43.47
2018-12-03 06:30 | 65.82 | 55.67
2018-12-03 07:00 | 78.09 | 63.82
2018-12-03 07:30 | 85.7 | 70.9
2018-12-03 08:00 | 92.46 | 77.31
2018-12-03 08:30 | 103.33 | 78.85
2018-12-03 09:00 | 99.93 | 80.32
2018-12-03 09:30 | 94.41 | 75.59
2018-12-03 10:00 | 98.65 | 81.19
2018-12-03 10:30 | 98.74 | 80.81
2018-12-03 11:00 | 100.82 | 83.42
2018-12-03 11:30 | 140.41 | 128.19
2018-12-03 12:00 | 140.01 | 127.87
2018-12-03 12:30 | 119.83 | 105.57
2018-12-03 13:00 | 130.03 | 117.53
2018-12-03 13:30 | 111.44 | 96.23
2018-12-03 14:00 | 102.04 | 85.18
2018-12-03 14:30 | 103.33 | 86.65
2018-12-03 15:00 | 132.53 | 119.01
2018-12-03 15:30 | 142.46 | 129.62
2018-12-03 16:00 | 135.15 | 122.09
2018-12-03 16:30 | 132.38 | 119.62
2018-12-03 17:00 | 129.88 | 117.94
2018-12-03 17:30 | 118.86 | 108.35
2018-12-03 18:00 | 107.45 | 104.5
2018-12-03 18:30 | 108.21 | 106.12
2018-12-03 19:00 | 120.05 | 117.53
2018-12-03 19:30 | 128.46 | 125.69
2018-12-03 20:00 | 142.12 | 137
2018-12-03 20:30 | 136.81 | 132.14
2018-12-03 21:00 | 122.74 | 118.34
2018-12-03 21:30 | 113.03 | 112.86
2018-12-03 22:00 | 108.99 | 108.91
2018-12-03 22:30 | 103.87 | 103.83
2018-12-03 23:00 | 97.18 | 97.13
2018-12-03 23:30 | 59.77 | 59.61
2018-12-04 | 26.34 | 25.78
2018-12-04 00:30 | 26.77 | 26.04
2018-12-04 01:00 | 41.06 | 40.2
2018-12-04 01:30 | 42.23 | 40.7
2018-12-04 02:00 | 49.09 | 47.83
2018-12-04 02:30 | 79 | 78.22
2018-12-04 03:00 | 84.13 | 83.4
2018-12-04 03:30 | 65.62 | 64.85
2018-12-04 04:00 | 31.06 | 29.97
2018-12-04 04:30 | 27.14 | 26.03
2018-12-04 05:00 | 12.8 | 10.79
2018-12-04 05:30 | 13.26 | 11.9
2018-12-04 06:00 | 21.18 | 20.58
2018-12-04 06:30 | 42.49 | 42.47
2018-12-04 07:00 | 38.42 | 37.92
2018-12-04 07:30 | 55.62 | 54.17
2018-12-04 08:00 | 74.18 | 73.58
2018-12-04 08:30 | 82 | 78.95
2018-12-04 09:00 | 96.8 | 88.61
2018-12-04 09:30 | 112.44 | 103.81
2018-12-04 10:00 | 115.15 | 109.16
2018-12-04 10:30 | 116.25 | 110.11
2018-12-04 11:00 | 122.33 | 116.43
2018-12-04 11:30 | 131.26 | 125.85
2018-12-04 12:00 | 126.42 | 120.93
2018-12-04 12:30 | 118.9 | 113.55
2018-12-04 13:00 | 122.2 | 116.53
2018-12-04 13:30 | 135.7 | 130.31
2018-12-04 14:00 | 144.04 | 138.88
2018-12-04 14:30 | 150.11 | 145.2
2018-12-04 15:00 | 141.16 | 136.49
2018-12-04 15:30 | 131.2 | 126.99
2018-12-04 16:00 | 126.78 | 123.13
2018-12-04 16:30 | 118.74 | 115.5
2018-12-04 17:00 | 118.15 | 115.31
2018-12-04 17:30 | 111.65 | 109.06
2018-12-04 18:00 | 108.29 | 105.94
2018-12-04 18:30 | 105.86 | 102.37
2018-12-04 19:00 | 83.2 | 77.49
2018-12-04 19:30 | 87.13 | 82.53
2018-12-04 20:00 | 97.33 | 94.32
2018-12-04 20:30 | 96.4 | 94.67
2018-12-04 21:00 | 73.65 | 73.21
2018-12-04 21:30 | 77.53 | 77.44
2018-12-04 22:00 | 74.25 | 74.25
2018-12-04 22:30 | 64.09 | 64.09
2018-12-04 23:00 | 59.96 | 59.92
2018-12-04 23:30 | 46.49 | 46.45
2018-12-05 | 32.04 | 31.85
2018-12-05 00:30 | 23.14 | 22.77
2018-12-05 01:00 | 24.68 | 24.03
2018-12-05 01:30 | 68.23 | 67.62
2018-12-05 02:00 | 85 | 84.41
2018-12-05 02:30 | 96.6 | 96.18
2018-12-05 03:00 | 95.05 | 94.68
2018-12-05 03:30 | 94.36 | 94.04
2018-12-05 04:00 | 89.78 | 89.59
2018-12-05 04:30 | 73.65 | 73.5
2018-12-05 05:00 | 78.42 | 78.3
2018-12-05 05:30 | 40.01 | 39.98
2018-12-05 06:00 | 29.42 | 29.4
2018-12-05 06:30 | 83.84 | 80.26
2018-12-05 07:00 | 98.79 | 93
2018-12-05 07:30 | 106.98 | 104.2
2018-12-05 08:00 | 108.16 | 106.07
2018-12-05 08:30 | 105.05 | 102.95
2018-12-05 09:00 | 108.2 | 105.77
2018-12-05 09:30 | 105.76 | 94.38
2018-12-05 10:00 | 120.65 | 104.07
2018-12-05 10:30 | 131.71 | 116.61
2018-12-05 11:00 | 142.31 | 128.81
2018-12-05 11:30 | 129.99 | 122.59
2018-12-05 12:00 | 128.14 | 122.67
2018-12-05 12:30 | 133.27 | 127.84
2018-12-05 13:00 | 137.47 | 132.67
2018-12-05 13:30 | 133.21 | 128.49
2018-12-05 14:00 | 139.06 | 134.38
2018-12-05 14:30 | 134.15 | 129.67
2018-12-05 15:00 | 109.51 | 105.41
2018-12-05 15:30 | 77.02 | 71.46
2018-12-05 16:00 | 82.3 | 77.35
2018-12-05 16:30 | 84.23 | 79.74
2018-12-05 17:00 | 87.45 | 83.66
2018-12-05 17:30 | 83.35 | 80.2
2018-12-05 18:00 | 82.36 | 79.98
2018-12-05 18:30 | 81.5 | 81.46
2018-12-05 19:00 | 90.33 | 90.19
2018-12-05 19:30 | 91.07 | 90.98
2018-12-05 20:00 | 87.83 | 87.63
2018-12-05 20:30 | 85.53 | 81.82
2018-12-05 21:00 | 75.12 | 71.89
2018-12-05 21:30 | 68.49 | 67.62
2018-12-05 22:00 | 64.66 | 64.45
2018-12-05 22:30 | 66.52 | 66.34
2018-12-05 23:00 | 57.77 | 57.53
2018-12-05 23:30 | 33.09 | 32.9
2018-12-06 | 1.72 | 1.32
2018-12-06 00:30 | 16.77 | 15.87
2018-12-06 01:00 | 20.65 | 19.58
2018-12-06 01:30 | 41.11 | 40.26
2018-12-06 02:00 | 60.22 | 59.54
2018-12-06 02:30 | 60.45 | 59.83
2018-12-06 03:00 | 69.68 | 69.29
2018-12-06 03:30 | 71.85 | 71.52
2018-12-06 04:00 | 78.26 | 78.03
2018-12-06 04:30 | 87.63 | 87.46
2018-12-06 05:00 | 87.65 | 87.57
2018-12-06 05:30 | 79.84 | 79.8
2018-12-06 06:00 | 55.29 | 55.26
2018-12-06 06:30 | 64.03 | 64.03
2018-12-06 07:00 | 101.16 | 101.16
2018-12-06 07:30 | 119.86 | 118.73
2018-12-06 08:00 | 133.7 | 131.65
2018-12-06 08:30 | 99.64 | 96.32
2018-12-06 09:00 | 100.93 | 98.08
2018-12-06 09:30 | 111.23 | 110.82
2018-12-06 10:00 | 69.77 | 69.11
2018-12-06 10:30 | 56.7 | 55.73
2018-12-06 11:00 | 53.52 | 52.35
2018-12-06 11:30 | 53.01 | 51.83
2018-12-06 12:00 | 56.6 | 55.85
2018-12-06 12:30 | 53.03 | 52.17
2018-12-06 13:00 | 47.92 | 47.11
2018-12-06 13:30 | 42.11 | 40.55
2018-12-06 14:00 | 64.64 | 63.84
2018-12-06 14:30 | 79.25 | 79.17
2018-12-06 15:00 | 88.78 | 88.63
2018-12-06 15:30 | 99.04 | 98.84
2018-12-06 16:00 | 107.42 | 107.18
2018-12-06 16:30 | 118.28 | 118.02
2018-12-06 17:00 | 77.67 | 77.34
2018-12-06 17:30 | 73.89 | 73.66
2018-12-06 18:00 | 74.01 | 73.75
2018-12-06 18:30 | 75.39 | 75.2
2018-12-06 19:00 | 81.31 | 81.28
2018-12-06 19:30 | 84.88 | 84.84
2018-12-06 20:00 | 86.29 | 86.12
2018-12-06 20:30 | 83.69 | 83.34
2018-12-06 21:00 | 76.35 | 75.5
2018-12-06 21:30 | 69.33 | 68.1
2018-12-06 22:00 | 97.51 | 96.73
2018-12-06 22:30 | 106.77 | 105.88
2018-12-06 23:00 | 114.29 | 113.43
2018-12-06 23:30 | 103.19 | 101.97
2018-12-07 | 89.35 | 87.34
2018-12-07 00:30 | 73.97 | 71.3
2018-12-07 01:00 | 53.3 | 49.97
2018-12-07 01:30 | 38.3 | 34.95
2018-12-07 02:00 | 56.62 | 54.42
2018-12-07 02:30 | 61.47 | 59.61
2018-12-07 03:00 | 61.17 | 59.28
2018-12-07 03:30 | 68.14 | 66.45
2018-12-07 04:00 | 74.64 | 72.38
2018-12-07 04:30 | 86.72 | 85.15
2018-12-07 05:00 | 95.96 | 94.85
2018-12-07 05:30 | 91.94 | 90.53
2018-12-07 06:00 | 84.77 | 82.84
2018-12-07 06:30 | 78.52 | 77.1
2018-12-07 07:00 | 82.26 | 81.46
2018-12-07 07:30 | 97.86 | 97.75
2018-12-07 08:00 | 100.11 | 100.1
2018-12-07 08:30 | 109.1 | 106.16
2018-12-07 09:00 | 109.25 | 103.13
2018-12-07 09:30 | 99.96 | 92.33
2018-12-07 10:00 | 111.61 | 104.47
2018-12-07 10:30 | 96.29 | 87.81
2018-12-07 11:00 | 70.92 | 57.82
2018-12-07 11:30 | 57.57 | 39.43
2018-12-07 12:00 | 58.5 | 40.8
2018-12-07 12:30 | 69.04 | 54.87
2018-12-07 13:00 | 65.34 | 50.75
2018-12-07 13:30 | 92.83 | 83.45
2018-12-07 14:00 | 102.97 | 95.06
2018-12-07 14:30 | 92.75 | 84.31
2018-12-07 15:00 | 139 | 134.15
2018-12-07 15:30 | 131.59 | 127.05
2018-12-07 16:00 | 92.42 | 86.05
2018-12-07 16:30 | 141.92 | 138.39
2018-12-07 17:00 | 108.38 | 103.99
2018-12-07 17:30 | 91.14 | 85.78
2018-12-07 18:00 | 80.49 | 75.2
2018-12-07 18:30 | 93.62 | 92.81
2018-12-07 19:00 | 118.22 | 118.19
2018-12-07 19:30 | 118.93 | 118.9
2018-12-07 20:00 | 131.83 | 131.82
2018-12-07 20:30 | 164.06 | 164.06
2018-12-07 21:00 | 111.98 | 111.95
2018-12-07 21:30 | 80.37 | 80.23
2018-12-07 22:00 | 102.26 | 101.95
2018-12-07 22:30 | 107.98 | 107.64
2018-12-07 23:00 | 130.67 | 130.29
2018-12-07 23:30 | 113.12 | 111.84
2018-12-08 | 68.82 | 66.33
2018-12-08 00:30 | 58.84 | 56.11
2018-12-08 01:00 | 36.85 | 32.6
2018-12-08 01:30 | 27.15 | 27.09
2018-12-08 02:00 | 26.4 | 26.34
2018-12-08 02:30 | 28.42 | 28.18
2018-12-08 03:00 | 54.38 | 54.01
2018-12-08 03:30 | 68.69 | 65.49
2018-12-08 04:00 | 67.12 | 63.56
2018-12-08 04:30 | 74.69 | 71.44
2018-12-08 05:00 | 84.27 | 81.43
2018-12-08 05:30 | 73.45 | 70.11
2018-12-08 06:00 | 60.51 | 56.97
2018-12-08 06:30 | 65.66 | 63.07
2018-12-08 07:00 | 75.74 | 73.98
2018-12-08 07:30 | 80.49 | 79.79
2018-12-08 08:00 | 82.23 | 82.02
2018-12-08 08:30 | 86.86 | 85.41
2018-12-08 09:00 | 85.09 | 83.26
2018-12-08 09:30 | 91.74 | 89.62
2018-12-08 10:00 | 73.44 | 70.45
2018-12-08 10:30 | 77.64 | 66.44
2018-12-08 11:00 | 69.74 | 54.81
2018-12-08 11:30 | 89.69 | 54.78
2018-12-08 12:00 | 95.04 | 59.05
2018-12-08 12:30 | 89.38 | 51.61
2018-12-08 13:00 | 87.07 | 50.27
2018-12-08 13:30 | 94.3 | 61.89
2018-12-08 14:00 | 88.11 | 70.71
2018-12-08 14:30 | 85.78 | 69.16
2018-12-08 15:00 | 77.49 | 59.13
2018-12-08 15:30 | 81.4 | 64.84
2018-12-08 16:00 | 91.29 | 76.39
2018-12-08 16:30 | 88.77 | 73.34
2018-12-08 17:00 | 100.12 | 86.71
2018-12-08 17:30 | 111.34 | 99.86
2018-12-08 18:00 | 112.44 | 101.48
2018-12-08 18:30 | 132.79 | 123.69
2018-12-08 19:00 | 149.47 | 140.61
2018-12-08 19:30 | 153.89 | 145.13
2018-12-08 20:00 | 172.82 | 165.45
2018-12-08 20:30 | 159.75 | 158.43
2018-12-08 21:00 | 111.13 | 110.32
2018-12-08 21:30 | 107.46 | 106.76
2018-12-08 22:00 | 115.93 | 115.5
2018-12-08 22:30 | 137.7 | 137.4
2018-12-08 23:00 | 141.96 | 141.75
2018-12-08 23:30 | 114.4 | 114.25
2018-12-09 | 95.08 | 95.01
2018-12-09 00:30 | 95.9 | 95.87
2018-12-09 01:00 | 71.77 | 71.76
2018-12-09 01:30 | 57.84 | 56.18
2018-12-09 02:00 | 77.35 | 74.39
2018-12-09 02:30 | 60.93 | 57.15
2018-12-09 03:00 | 55.75 | 51.32
2018-12-09 03:30 | 53.5 | 48.93
2018-12-09 04:00 | 52.7 | 48.21
2018-12-09 04:30 | 51.81 | 47.16
2018-12-09 05:00 | 60.2 | 56.16
2018-12-09 05:30 | 60.09 | 56.16
2018-12-09 06:00 | 54.33 | 50.23
2018-12-09 06:30 | 54.59 | 51.38
2018-12-09 07:00 | 49.14 | 46.38
2018-12-09 07:30 | 58.86 | 57.4
2018-12-09 08:00 | 49.02 | 48.03
2018-12-09 08:30 | 47.17 | 47.1
2018-12-09 09:00 | 56.66 | 54.43
2018-12-09 09:30 | 73.65 | 71.45
2018-12-09 10:00 | 46.59 | 42.18
2018-12-09 10:30 | 38.2 | 31.52
2018-12-09 11:00 | 41.94 | 27.4
2018-12-09 11:30 | 52.36 | 30.66
2018-12-09 12:00 | 38.1 | 23.65
2018-12-09 12:30 | 43.72 | 40.4
2018-12-09 13:00 | 25.61 | 17.36
2018-12-09 13:30 | 27.21 | 17.85
2018-12-09 14:00 | 38.96 | 32.55
2018-12-09 14:30 | 48.89 | 44.55
2018-12-09 15:00 | 59.13 | 55.94
2018-12-09 15:30 | 61.54 | 58.66
2018-12-09 16:00 | 82.56 | 80.75
2018-12-09 16:30 | 86.09 | 84.44
2018-12-09 17:00 | 78.72 | 76.85
2018-12-09 17:30 | 74.57 | 73.18
2018-12-09 18:00 | 70.29 | 68.93
2018-12-09 18:30 | 70.9 | 69.74
2018-12-09 19:00 | 73.28 | 71.87
2018-12-09 19:30 | 79.03 | 77.55
2018-12-09 20:00 | 91.44 | 90.53
2018-12-09 20:30 | 92.95 | 92.3
2018-12-09 21:00 | 69.82 | 69.2
2018-12-09 21:30 | 80.74 | 80.41
2018-12-09 22:00 | 93.22 | 93.12
2018-12-09 22:30 | 90.34 | 90.34
2018-12-09 23:00 | 94.54 | 94.44
2018-12-09 23:30 | 80.21 | 79.93
2018-12-10 | 38.12 | 37.14
2018-12-10 00:30 | 30.48 | 28.49
2018-12-10 01:00 | 20.87 | 17.45
2018-12-10 01:30 | 13.44 | 5.73
2018-12-10 02:00 | 22.34 | 19.79
2018-12-10 02:30 | 36.71 | 35.46
2018-12-10 03:00 | 37.72 | 37.37
2018-12-10 03:30 | 35.79 | 35.73
2018-12-10 04:00 | 40.2 | 40.04
2018-12-10 04:30 | 26.79 | 26.46
2018-12-10 05:00 | 32.87 | 32.58
2018-12-10 05:30 | 34.45 | 34.07
2018-12-10 06:00 | 30.16 | 29.1
2018-12-10 06:30 | 51.82 | 50.31
2018-12-10 07:00 | 49.97 | 48.95
2018-12-10 07:30 | 77.96 | 76.73
2018-12-10 08:00 | 89.95 | 89.69
2018-12-10 08:30 | 93.27 | 92.9
2018-12-10 09:00 | 94.06 | 93.55
2018-12-10 09:30 | 82.21 | 81.42
2018-12-10 10:00 | 58.85 | 56.74
2018-12-10 10:30 | 73.04 | 59.87
2018-12-10 11:00 | 80.94 | 53.3
2018-12-10 11:30 | 92.49 | 70.37
2018-12-10 12:00 | 91.4 | 69.51
2018-12-10 12:30 | 96.05 | 75.61
2018-12-10 13:00 | 96.29 | 75.1
2018-12-10 13:30 | 97.03 | 75.52
2018-12-10 14:00 | 112.27 | 94.59
2018-12-10 14:30 | 118.16 | 101.34
2018-12-10 15:00 | 117.58 | 100.83
2018-12-10 15:30 | 111.26 | 92.31
2018-12-10 16:00 | 101.7 | 82.07
2018-12-10 16:30 | 95.61 | 77.43
2018-12-10 17:00 | 99.92 | 83.38
2018-12-10 17:30 | 82.64 | 64.11
2018-12-10 18:00 | 71.56 | 51.17
2018-12-10 18:30 | 69.07 | 58.79
2018-12-10 19:00 | 74.4 | 69.4
2018-12-10 19:30 | 77.1 | 72.38
2018-12-10 20:00 | 88.78 | 85.63
2018-12-10 20:30 | 94.29 | 92.41
2018-12-10 21:00 | 67.95 | 67.95
2018-12-10 21:30 | 75.61 | 75.13
2018-12-10 22:00 | 87.03 | 86.87
2018-12-10 22:30 | 85.85 | 85.79
2018-12-10 23:00 | 85.17 | 85.1
2018-12-10 23:30 | 65.03 | 64.88
2018-12-11 | 47.95 | 47.62
2018-12-11 00:30 | 42.27 | 39.1
2018-12-11 01:00 | 40.27 | 36.96
2018-12-11 01:30 | 46.86 | 44.39
2018-12-11 02:00 | 47.47 | 44.89
2018-12-11 02:30 | 40.3 | 37.54
2018-12-11 03:00 | 35.52 | 32.5
2018-12-11 03:30 | 37.81 | 35.3
2018-12-11 04:00 | 24.31 | 21.3
2018-12-11 04:30 | 17.3 | 13.6
2018-12-11 05:00 | 37.76 | 36.21
2018-12-11 05:30 | 51.17 | 49.9
2018-12-11 06:00 | 49.8 | 48.37
2018-12-11 06:30 | 50.74 | 48.87
2018-12-11 07:00 | 69.99 | 69.23
2018-12-11 07:30 | 85.88 | 85.81
2018-12-11 08:00 | 84.97 | 82.85
2018-12-11 08:30 | 99.77 | 75.5
2018-12-11 09:00 | 102.4 | 76.94
2018-12-11 09:30 | 103.04 | 75.55
2018-12-11 10:00 | 97.8 | 66.97
2018-12-11 10:30 | 101.59 | 70.13
2018-12-11 11:00 | 110.15 | 80.32
2018-12-11 11:30 | 117.22 | 89.5
2018-12-11 12:00 | 111.49 | 80.02
2018-12-11 12:30 | 121.02 | 92.96
2018-12-11 13:00 | 119.65 | 91.03
2018-12-11 13:30 | 124.6 | 96.63
2018-12-11 14:00 | 132.44 | 106.34
2018-12-11 14:30 | 139.96 | 115.14
2018-12-11 15:00 | 117.34 | 86.29
2018-12-11 15:30 | 88.41 | 36.57
2018-12-11 16:00 | 85.85 | 52.36
2018-12-11 16:30 | 83.88 | 53.41
2018-12-11 17:00 | 79.06 | 52.17
2018-12-11 17:30 | 69.88 | 45.21
2018-12-11 18:00 | 67.94 | 44.08
2018-12-11 18:30 | 66.56 | 58.87
2018-12-11 19:00 | 75.16 | 69.07
2018-12-11 19:30 | 78.45 | 72.21
2018-12-11 20:00 | 87.73 | 83.6
2018-12-11 20:30 | 92.71 | 89.94
2018-12-11 21:00 | 71.76 | 71.57
2018-12-11 21:30 | 81.83 | 80.85
2018-12-11 22:00 | 92.36 | 92.3
2018-12-11 22:30 | 89.89 | 89.85
2018-12-11 23:00 | 88.79 | 88.68
2018-12-11 23:30 | 62.92 | 62.53
2018-12-12 | 44.3 | 43.37
2018-12-12 00:30 | 40.09 | 38.48
2018-12-12 01:00 | 41.11 | 38.99
2018-12-12 01:30 | 42.06 | 39.51
2018-12-12 02:00 | 36.06 | 32.65
2018-12-12 02:30 | 31.08 | 26.99
2018-12-12 03:00 | 15.66 | 5.94
2018-12-12 03:30 | 14.9 | -6.04
2018-12-12 04:00 | 14.06 | -5.7
2018-12-12 04:30 | 20.03 | 14.55
2018-12-12 05:00 | 28.51 | 25.51
2018-12-12 05:30 | 29.37 | 28.5
2018-12-12 06:00 | 43.84 | 42.61
2018-12-12 06:30 | 65.59 | 64.73
2018-12-12 07:00 | 78.91 | 78.21
2018-12-12 07:30 | 96.01 | 96
2018-12-12 08:00 | 98.57 | 98.54
2018-12-12 08:30 | 67.97 | 67.95
2018-12-12 09:00 | 72.26 | 72.26
2018-12-12 09:30 | 70.54 | 70.32
2018-12-12 10:00 | 61.11 | 61.02
2018-12-12 10:30 | 50.55 | 50.48
2018-12-12 11:00 | 55.38 | 55.28
2018-12-12 11:30 | 70.04 | 62.98
2018-12-12 12:00 | 76.68 | 68.33
2018-12-12 12:30 | 86.76 | 79.46
2018-12-12 13:00 | 79.47 | 71.68
2018-12-12 13:30 | 82.63 | 74.55
2018-12-12 14:00 | 90.43 | 82.87
2018-12-12 14:30 | 110.89 | 104.91
2018-12-12 15:00 | 104.53 | 98.19
2018-12-12 15:30 | 92.26 | 84.87
2018-12-12 16:00 | 79.13 | 70.78
2018-12-12 16:30 | 72.33 | 63.55
2018-12-12 17:00 | 86.33 | 79.7
2018-12-12 17:30 | 82.35 | 76.92
2018-12-12 18:00 | 74.95 | 70.28
2018-12-12 18:30 | 75.15 | 71.44
2018-12-12 19:00 | 90.14 | 86.46
2018-12-12 19:30 | 94.15 | 91.33
2018-12-12 20:00 | 106.59 | 104.57
2018-12-12 20:30 | 108.91 | 108.54
2018-12-12 21:00 | 88.65 | 87.26
2018-12-12 21:30 | 96.46 | 95.15
2018-12-12 22:00 | 105.21 | 103.58
2018-12-12 22:30 | 96.92 | 96.24
2018-12-12 23:00 | 97.29 | 96.51
2018-12-12 23:30 | 75.06 | 73.84
2018-12-13 | 59.11 | 57.24
2018-12-13 00:30 | 51.13 | 48.63
2018-12-13 01:00 | 56.99 | 54.33
2018-12-13 01:30 | 64.4 | 61.31
2018-12-13 02:00 | 66.73 | 60.65
2018-12-13 02:30 | 54.91 | 45.1
2018-12-13 03:00 | 45.37 | 33.86
2018-12-13 03:30 | 42.79 | 32.1
2018-12-13 04:00 | 40.85 | 29.27
2018-12-13 04:30 | 38.2 | 25.26
2018-12-13 05:00 | 48.72 | 39.71
2018-12-13 05:30 | 64.86 | 58.17
2018-12-13 06:00 | 59.54 | 52.55
2018-12-13 06:30 | 78.29 | 73.7
2018-12-13 07:00 | 87.22 | 84.48
2018-12-13 07:30 | 78.16 | 75.74
2018-12-13 08:00 | 66.4 | 66.4
2018-12-13 08:30 | 72.84 | 62.75
2018-12-13 09:00 | 98.17 | 86.51
2018-12-13 09:30 | 101.58 | 89.39
2018-12-13 10:00 | 99.4 | 88.46
2018-12-13 10:30 | 95.68 | 85.7
2018-12-13 11:00 | 103.87 | 94.51
2018-12-13 11:30 | 94.54 | 83.39
2018-12-13 12:00 | 106.74 | 96.51
2018-12-13 12:30 | 123.04 | 114.65
2018-12-13 13:00 | 130.44 | 122.75
2018-12-13 13:30 | 133.84 | 125.89
2018-12-13 14:00 | 129.81 | 121.09
2018-12-13 14:30 | 122.4 | 112.27
2018-12-13 15:00 | 110.86 | 99.51
2018-12-13 15:30 | 99.89 | 87.3
2018-12-13 16:00 | 131.1 | 121.44
2018-12-13 16:30 | 134.56 | 126.05
2018-12-13 17:00 | 116.89 | 108.52
2018-12-13 17:30 | 108.12 | 99.9
2018-12-13 18:00 | 77.71 | 66.85
2018-12-13 18:30 | 78.79 | 69.38
2018-12-13 19:00 | 88.22 | 78.62
2018-12-13 19:30 | 92.85 | 84.81
2018-12-13 20:00 | 102.03 | 95.66
2018-12-13 20:30 | 109.47 | 104.54
2018-12-13 21:00 | 89.51 | 83.12
2018-12-13 21:30 | 94.08 | 89.22
2018-12-13 22:00 | 100.98 | 100.91
2018-12-13 22:30 | 98.13 | 96.69
2018-12-13 23:00 | 102.31 | 100.61
2018-12-13 23:30 | 76.3 | 74.61
2018-12-14 | 60.44 | 58.61
2018-12-14 00:30 | 50.57 | 48.92
2018-12-14 01:00 | 54.24 | 54.15
2018-12-14 01:30 | 70.43 | 67.27
2018-12-14 02:00 | 71.68 | 68.49
2018-12-14 02:30 | 70.69 | 67.42
2018-12-14 03:00 | 69.32 | 65.85
2018-12-14 03:30 | 68.58 | 65.05
2018-12-14 04:00 | 67.43 | 63.98
2018-12-14 04:30 | 68.41 | 65.33
2018-12-14 05:00 | 67.67 | 64.59
2018-12-14 05:30 | 65.42 | 62.8
2018-12-14 06:00 | 55.69 | 53.61
2018-12-14 06:30 | 59.92 | 58.79
2018-12-14 07:00 | 70.88 | 69.91
2018-12-14 07:30 | 74.63 | 73.84
2018-12-14 08:00 | 73.11 | 72.93
2018-12-14 08:30 | 57.37 | 56.92
2018-12-14 09:00 | 64.85 | 64.22
2018-12-14 09:30 | 62.7 | 60.92
2018-12-14 10:00 | 51.64 | 49.47
2018-12-14 10:30 | 65.32 | 64.29
2018-12-14 11:00 | 62.53 | 62.1
2018-12-14 11:30 | 75.7 | 75.54
2018-12-14 12:00 | 79.93 | 79.88
2018-12-14 12:30 | 73.93 | 73.83
2018-12-14 13:00 | 94.18 | 94.06
2018-12-14 13:30 | 134.7 | 134.54
2018-12-14 14:00 | 150.18 | 146.73
2018-12-14 14:30 | 179.68 | 169.57
2018-12-14 15:00 | 221.18 | 217.83
2018-12-14 15:30 | 216.94 | 213.59
2018-12-14 16:00 | 144.53 | 138.47
2018-12-14 16:30 | 151.33 | 140.91
2018-12-14 17:00 | 163.84 | 160.18
2018-12-14 17:30 | 196.75 | 194.5
2018-12-14 18:00 | 196.63 | 196.51
2018-12-14 18:30 | 196.23 | 196.23
2018-12-14 19:00 | 202.02 | 201.96
2018-12-14 19:30 | 207.61 | 207.15
2018-12-14 20:00 | 216.9 | 216.49
2018-12-14 20:30 | 220.08 | 219.8
2018-12-14 21:00 | 196.23 | 196.11
2018-12-14 21:30 | 188.27 | 188.2
2018-12-14 22:00 | 156.29 | 156.25
2018-12-14 22:30 | 148.03 | 147.92
2018-12-14 23:00 | 141.69 | 141.38
2018-12-14 23:30 | 98.91 | 98.43
2018-12-15 | 72.18 | 71.93
2018-12-15 00:30 | 46.3 | 45.68
2018-12-15 01:00 | 38.3 | 33.89
2018-12-15 01:30 | 34.23 | 29.21
2018-12-15 02:00 | 28.54 | 22.71
2018-12-15 02:30 | 17.9 | 8.96
2018-12-15 03:00 | 17.04 | 8.09
2018-12-15 03:30 | 14.17 | 2.02
2018-12-15 04:00 | 14.54 | -6.8
2018-12-15 04:30 | 12.44 | -2.88
2018-12-15 05:00 | 14.3 | 6.78
2018-12-15 05:30 | 16.17 | 11.12
2018-12-15 06:00 | 19.72 | 14.82
2018-12-15 06:30 | 20.52 | 16.3
2018-12-15 07:00 | 13.29 | 9.52
2018-12-15 07:30 | 4.9 | 1.86
2018-12-15 08:00 | 25.39 | 22.75
2018-12-15 08:30 | 46.6 | 45.7
2018-12-15 09:00 | 55.04 | 54.77
2018-12-15 09:30 | 54.85 | 54.34
2018-12-15 10:00 | 64.65 | 64.1
2018-12-15 10:30 | 78.81 | 68.9
2018-12-15 11:00 | 84.75 | 58.48
2018-12-15 11:30 | 107.37 | 87.86
2018-12-15 12:00 | 113.11 | 95.26
2018-12-15 12:30 | 113.26 | 95.48
2018-12-15 13:00 | 124.55 | 108.6
2018-12-15 13:30 | 145.48 | 131.79
2018-12-15 14:00 | 156.81 | 144.86
2018-12-15 14:30 | 158.5 | 146.21
2018-12-15 15:00 | 180.4 | 169.55
2018-12-15 15:30 | 175.12 | 164.2
2018-12-15 16:00 | 184.54 | 174.74
2018-12-15 16:30 | 192.57 | 184.41
2018-12-15 17:00 | 170.4 | 161.3
2018-12-15 17:30 | 139.78 | 135.79
2018-12-15 18:00 | 133.45 | 130.25
2018-12-15 18:30 | 129.17 | 128.77
2018-12-15 19:00 | 165.37 | 165.02
2018-12-15 19:30 | 191.71 | 191.41
2018-12-15 20:00 | 197.14 | 196.93
2018-12-15 20:30 | 183.6 | 183.48
2018-12-15 21:00 | 149.32 | 149.3
2018-12-15 21:30 | 148.04 | 148.04
2018-12-15 22:00 | 132.27 | 132.27
2018-12-15 22:30 | 138.7 | 138.69
2018-12-15 23:00 | 145.36 | 145.35
2018-12-15 23:30 | 105.86 | 105.82
2018-12-16 | 62.99 | 62.85
2018-12-16 00:30 | 33.22 | 32.66
2018-12-16 01:00 | 12.36 | 10.94
2018-12-16 01:30 | 11.05 | 7.93
2018-12-16 02:00 | 13.75 | -4.41
2018-12-16 02:30 | 12.78 | -6.05
2018-12-16 03:00 | 11.39 | -1.63
2018-12-16 03:30 | 13.26 | -8.41
2018-12-16 04:00 | 11.7 | -4.49
2018-12-16 04:30 | 12.53 | 1.31
2018-12-16 05:00 | 17.27 | 11.72
2018-12-16 05:30 | 17.54 | 13.18
2018-12-16 06:00 | 16.25 | 11.2
2018-12-16 06:30 | 18.9 | 14.41
2018-12-16 07:00 | 23.11 | 18.86
2018-12-16 07:30 | 34.64 | 32.78
2018-12-16 08:00 | 41.67 | 41.26
2018-12-16 08:30 | 63.32 | 63.03
2018-12-16 09:00 | 102.3 | 94.61
2018-12-16 09:30 | 113.17 | 105.39
2018-12-16 10:00 | 118.82 | 110.05
2018-12-16 10:30 | 122.61 | 114
2018-12-16 11:00 | 117.97 | 108.96
2018-12-16 11:30 | 109.65 | 100.33
2018-12-16 12:00 | 101.55 | 91.31
2018-12-16 12:30 | 106.48 | 96.94
2018-12-16 13:00 | 100.87 | 91.33
2018-12-16 13:30 | 86.19 | 75.43
2018-12-16 14:00 | 82.94 | 71.85
2018-12-16 14:30 | 85.46 | 74.82
2018-12-16 15:00 | 63.25 | 47.81
2018-12-16 15:30 | 66.45 | 52.48
2018-12-16 16:00 | 52.62 | 32.44
2018-12-16 16:30 | 64.75 | 50.68
2018-12-16 17:00 | 68.97 | 55.97
2018-12-16 17:30 | 92.12 | 83.25
2018-12-16 18:00 | 89.67 | 80.42
2018-12-16 18:30 | 93.22 | 84.63
2018-12-16 19:00 | 104.71 | 96.79
2018-12-16 19:30 | 96.81 | 88.73
2018-12-16 20:00 | 91.55 | 83.52
2018-12-16 20:30 | 84.26 | 76.48
2018-12-16 21:00 | 59.72 | 51.8
2018-12-16 21:30 | 38.01 | 36.48
2018-12-16 22:00 | 29.65 | 28.68
2018-12-16 22:30 | 40.05 | 38.79
2018-12-16 23:00 | 52.28 | 50.99
2018-12-16 23:30 | 43.58 | 42.16
2018-12-17 | 16.37 | 13.71
2018-12-17 00:30 | 9 | 5.24
2018-12-17 01:00 | 12.31 | -10.63
2018-12-17 01:30 | 25.36 | -25.07
2018-12-17 02:00 | 32.35 | -32.11
2018-12-17 02:30 | 19.2 | -18.55
2018-12-17 03:00 | 19.63 | -19.13
2018-12-17 03:30 | 23.74 | -23.56
2018-12-17 04:00 | 14.18 | -13.85
2018-12-17 04:30 | 3.68 | -1.87
2018-12-17 05:00 | 25.52 | 24.72
2018-12-17 05:30 | 22.18 | 19.06
2018-12-17 06:00 | 29.85 | 27.67
2018-12-17 06:30 | 27.15 | 26.91
2018-12-17 07:00 | 40.08 | 40.05
2018-12-17 07:30 | 56.65 | 56.63
2018-12-17 08:00 | 74.97 | 73.8
2018-12-17 08:30 | 72.73 | 67.71
2018-12-17 09:00 | 80.31 | 74.35
2018-12-17 09:30 | 109.59 | 104.39
2018-12-17 10:00 | 86.64 | 80.04
2018-12-17 10:30 | 106.88 | 100.31
2018-12-17 11:00 | 106.63 | 98.31
2018-12-17 11:30 | 115.82 | 107.49
2018-12-17 12:00 | 98.25 | 88.17
2018-12-17 12:30 | 100.78 | 91.47
2018-12-17 13:00 | 100.81 | 92.06
2018-12-17 13:30 | 123.97 | 117.2
2018-12-17 14:00 | 113.86 | 106.33
2018-12-17 14:30 | 122.48 | 115.86
2018-12-17 15:00 | 88.94 | 80.96
2018-12-17 15:30 | 97.62 | 90.87
2018-12-17 16:00 | 83.38 | 76.11
2018-12-17 16:30 | 91.92 | 86.27
2018-12-17 17:00 | 116.51 | 112.69
2018-12-17 17:30 | 113.78 | 110.77
2018-12-17 18:00 | 119.34 | 118.84
2018-12-17 18:30 | 133.04 | 133
2018-12-17 19:00 | 170.59 | 170.57
2018-12-17 19:30 | 177.78 | 177.75
2018-12-17 20:00 | 167.88 | 167.79
2018-12-17 20:30 | 157.67 | 157.54
2018-12-17 21:00 | 125.82 | 125.55
2018-12-17 21:30 | 122.07 | 121.62
2018-12-17 22:00 | 82.42 | 82.21
2018-12-17 22:30 | 87.78 | 87.45
2018-12-17 23:00 | 108.94 | 108.53
2018-12-17 23:30 | 80.16 | 79.3
2018-12-18 | 38.97 | 36.4
2018-12-18 00:30 | 32.94 | 28.9
2018-12-18 01:00 | 16.07 | 8.96
2018-12-18 01:30 | 13.78 | -2.68
2018-12-18 02:00 | 13.83 | -1.22
2018-12-18 02:30 | 14.19 | -1.96
2018-12-18 03:00 | 13.89 | -2.74
2018-12-18 03:30 | 13.84 | -5.21
2018-12-18 04:00 | 14.4 | -7.75
2018-12-18 04:30 | 13.94 | -7.87
2018-12-18 05:00 | 11.83 | -0.86
2018-12-18 05:30 | 11.75 | -7.66
2018-12-18 06:00 | 17.06 | 15.34
2018-12-18 06:30 | 42.13 | 42.04
2018-12-18 07:00 | 53.34 | 53.24
2018-12-18 07:30 | 77.05 | 76.99
2018-12-18 08:00 | 73.61 | 73.6
2018-12-18 08:30 | 84.41 | 84.36
2018-12-18 09:00 | 101.5 | 99
2018-12-18 09:30 | 106.04 | 101.91
2018-12-18 10:00 | 84.62 | 74.56
2018-12-18 10:30 | 95.33 | 70.99
2018-12-18 11:00 | 90.4 | 63.57
2018-12-18 11:30 | 91.74 | 64.49
2018-12-18 12:00 | 96.18 | 70.97
2018-12-18 12:30 | 95.6 | 70.44
2018-12-18 13:00 | 107.85 | 86.24
2018-12-18 13:30 | 108.3 | 86.75
2018-12-18 14:00 | 112.98 | 92.11
2018-12-18 14:30 | 113.68 | 92.98
2018-12-18 15:00 | 121.75 | 101.79
2018-12-18 15:30 | 125.83 | 106.16
2018-12-18 16:00 | 172.02 | 160.14
2018-12-18 16:30 | 186.52 | 175.74
2018-12-18 17:00 | 164.34 | 152.48
2018-12-18 17:30 | 159.8 | 148.43
2018-12-18 18:00 | 150.15 | 143.4
2018-12-18 18:30 | 145.23 | 142.25
2018-12-18 19:00 | 150.04 | 147.02
2018-12-18 19:30 | 156.35 | 152.91
2018-12-18 20:00 | 203.02 | 200.63
2018-12-18 20:30 | 209.64 | 207.97
2018-12-18 21:00 | 173.05 | 172.88
2018-12-18 21:30 | 186.48 | 186.37
2018-12-18 22:00 | 170.93 | 170.84
2018-12-18 22:30 | 176.2 | 176.09
2018-12-18 23:00 | 133.34 | 133.25
2018-12-18 23:30 | 101.72 | 101.39
2018-12-19 | 69.98 | 69.6
2018-12-19 00:30 | 51.34 | 51.16
2018-12-19 01:00 | 33.69 | 33.54
2018-12-19 01:30 | 26.94 | 26.82
2018-12-19 02:00 | 31.97 | 31.93
2018-12-19 02:30 | 24.59 | 24.55
2018-12-19 03:00 | 21.55 | 21.49
2018-12-19 03:30 | 20.18 | 20.08
2018-12-19 04:00 | 39.85 | 39.85
2018-12-19 04:30 | 18.78 | 18.78
2018-12-19 05:00 | 11.78 | 11.78
2018-12-19 05:30 | 8 | 6.84
2018-12-19 06:00 | 21.49 | 20.09
2018-12-19 06:30 | 35.35 | 32.53
2018-12-19 07:00 | 59.08 | 42.8
2018-12-19 07:30 | 83.88 | 73.06
2018-12-19 08:00 | 99.27 | 88.01
2018-12-19 08:30 | 118.61 | 107.28
2018-12-19 09:00 | 132.75 | 114.7
2018-12-19 09:30 | 119.55 | 102.01
2018-12-19 10:00 | 119.6 | 101.46
2018-12-19 10:30 | 117.79 | 98.31
2018-12-19 11:00 | 119.95 | 100.55
2018-12-19 11:30 | 108.45 | 86.83
2018-12-19 12:00 | 111.01 | 90.53
2018-12-19 12:30 | 117.18 | 98.11
2018-12-19 13:00 | 106.98 | 97.27
2018-12-19 13:30 | 102.69 | 92
2018-12-19 14:00 | 113.75 | 103.94
2018-12-19 14:30 | 108.5 | 96.55
2018-12-19 15:00 | 88.79 | 73.65
2018-12-19 15:30 | 88.95 | 76.84
2018-12-19 16:00 | 131.98 | 124.47
2018-12-19 16:30 | 150.86 | 144.8
2018-12-19 17:00 | 161.51 | 156.47
2018-12-19 17:30 | 162.58 | 158.47
2018-12-19 18:00 | 157.31 | 154.09
2018-12-19 18:30 | 151.65 | 149.35
2018-12-19 19:00 | 154.47 | 152.05
2018-12-19 19:30 | 161.36 | 158.87
2018-12-19 20:00 | 190.8 | 189.18
2018-12-19 20:30 | 190.93 | 190.31
2018-12-19 21:00 | 159.87 | 159.87
2018-12-19 21:30 | 150.44 | 150.44
2018-12-19 22:00 | 135.72 | 135.41
2018-12-19 22:30 | 169.55 | 169.37
2018-12-19 23:00 | 167.99 | 167.91
2018-12-19 23:30 | 122.05 | 121.99
2018-12-20 | 91.17 | 91
2018-12-20 00:30 | 82.48 | 82.4
2018-12-20 01:00 | 59.05 | 59.04
2018-12-20 01:30 | 60.14 | 60.14
2018-12-20 02:00 | 74.01 | 74.01
2018-12-20 02:30 | 72.41 | 72.41
2018-12-20 03:00 | 67.13 | 67.13
2018-12-20 03:30 | 67.47 | 67.47
2018-12-20 04:00 | 65.75 | 65.75
2018-12-20 04:30 | 57.3 | 57.29
2018-12-20 05:00 | 68.19 | 68.19
2018-12-20 05:30 | 60.18 | 60.16
2018-12-20 06:00 | 48.69 | 48.48
2018-12-20 06:30 | 59.96 | 58.85
2018-12-20 07:00 | 59.62 | 59.61
2018-12-20 07:30 | 107.55 | 107.13
2018-12-20 08:00 | 110.62 | 110.56
2018-12-20 08:30 | 124.6 | 123.46
2018-12-20 09:00 | 131.69 | 125.76
2018-12-20 09:30 | 141.13 | 135.13
2018-12-20 10:00 | 135.94 | 129.1
2018-12-20 10:30 | 127.16 | 120.84
2018-12-20 11:00 | 125.56 | 117.96
2018-12-20 11:30 | 141.5 | 134.48
2018-12-20 12:00 | 182.84 | 177.18
2018-12-20 12:30 | 172.41 | 165.52
2018-12-20 13:00 | 225.26 | 219.94
2018-12-20 13:30 | 206.82 | 200.83
2018-12-20 14:00 | 197.9 | 187.43
2018-12-20 14:30 | 196.82 | 182.68
2018-12-20 15:00 | 198.05 | 183.13
2018-12-20 15:30 | 136.78 | 112.8
2018-12-20 16:00 | 142.06 | 102.39
2018-12-20 16:30 | 143.12 | 104.43
2018-12-20 17:00 | 130.95 | 88.56
2018-12-20 17:30 | 118.93 | 76.08
2018-12-20 18:00 | 116.86 | 79.62
2018-12-20 18:30 | 120.61 | 90.93
2018-12-20 19:00 | 135.27 | 109.4
2018-12-20 19:30 | 143.8 | 118.93
2018-12-20 20:00 | 148.22 | 133.46
2018-12-20 20:30 | 157.04 | 148.11
2018-12-20 21:00 | 142.86 | 136.32
2018-12-20 21:30 | 154.92 | 153.96
2018-12-20 22:00 | 149.23 | 149.22
2018-12-20 22:30 | 138.62 | 137.76
2018-12-20 23:00 | 131.05 | 130.43
2018-12-20 23:30 | 115.5 | 115.28
2018-12-21 | 105.56 | 104.99
2018-12-21 00:30 | 112.78 | 111.55
2018-12-21 01:00 | 95.92 | 94.31
2018-12-21 01:30 | 87.26 | 86.32
2018-12-21 02:00 | 93.11 | 92.08
2018-12-21 02:30 | 93.43 | 92.33
2018-12-21 03:00 | 79.3 | 77.9
2018-12-21 03:30 | 73.77 | 72.26
2018-12-21 04:00 | 68.94 | 67.44
2018-12-21 04:30 | 68.58 | 67.26
2018-12-21 05:00 | 77.85 | 76.69
2018-12-21 05:30 | 72.79 | 71.9
2018-12-21 06:00 | 59.9 | 59.3
2018-12-21 06:30 | 92.05 | 92.01
2018-12-21 07:00 | 108.83 | 108.77
2018-12-21 07:30 | 129.04 | 128.66
2018-12-21 08:00 | 158.11 | 150.28
2018-12-21 08:30 | 180.66 | 168.95
2018-12-21 09:00 | 205.33 | 193.63
2018-12-21 09:30 | 211.22 | 202.13
2018-12-21 10:00 | 215.11 | 205.7
2018-12-21 10:30 | 241.45 | 232.07
2018-12-21 11:00 | 223.94 | 212.64
2018-12-21 11:30 | 252.65 | 241.82
2018-12-21 12:00 | 265.36 | 254.71
2018-12-21 12:30 | 263 | 252.38
2018-12-21 13:00 | 255 | 244.13
2018-12-21 13:30 | 207.63 | 193.5
2018-12-21 14:00 | 198.32 | 181.53
2018-12-21 14:30 | 210.85 | 187.8
2018-12-21 15:00 | 217.67 | 192.02
2018-12-21 15:30 | 197.95 | 173.11
2018-12-21 16:00 | 192.84 | 162.74
2018-12-21 16:30 | 209.36 | 182.27
2018-12-21 17:00 | 239.91 | 218.2
2018-12-21 17:30 | 265.29 | 248.51
2018-12-21 18:00 | 225.51 | 213.96
2018-12-21 18:30 | 205.49 | 202.96
2018-12-21 19:00 | 202.86 | 200.74
2018-12-21 19:30 | 198.18 | 197.33
2018-12-21 20:00 | 182.7 | 182.64
2018-12-21 20:30 | 182.98 | 182.92
2018-12-21 21:00 | 179.59 | 179.56
2018-12-21 21:30 | 172.3 | 172.13
2018-12-21 22:00 | 140.45 | 140.09
2018-12-21 22:30 | 125.07 | 124.49
2018-12-21 23:00 | 133.98 | 133.59
2018-12-21 23:30 | 106.31 | 106.18
2018-12-22 | 100.9 | 100.3
2018-12-22 00:30 | 121.16 | 120.78
2018-12-22 01:00 | 107.1 | 106.75
2018-12-22 01:30 | 103.5 | 102.92
2018-12-22 02:00 | 106.57 | 105.93
2018-12-22 02:30 | 87.42 | 86.57
2018-12-22 03:00 | 55.13 | 53.68
2018-12-22 03:30 | 60.83 | 59.39
2018-12-22 04:00 | 47.19 | 45.4
2018-12-22 04:30 | 54.53 | 53.06
2018-12-22 05:00 | 66.85 | 65.61
2018-12-22 05:30 | 56.33 | 54.01
2018-12-22 06:00 | 49.58 | 46.26
2018-12-22 06:30 | 57.47 | 54.57
2018-12-22 07:00 | 56.22 | 54.48
2018-12-22 07:30 | 58.9 | 56.93
2018-12-22 08:00 | 69.93 | 69.56
2018-12-22 08:30 | 96.42 | 96.39
2018-12-22 09:00 | 119.22 | 119.03
2018-12-22 09:30 | 129.14 | 128.09
2018-12-22 10:00 | 129.96 | 126.4
2018-12-22 10:30 | 122.56 | 118.54
2018-12-22 11:00 | 139.02 | 135.33
2018-12-22 11:30 | 158.01 | 154.16
2018-12-22 12:00 | 183.09 | 179.24
2018-12-22 12:30 | 214.86 | 212.33
2018-12-22 13:00 | 220.06 | 217.58
2018-12-22 13:30 | 229.77 | 226.9
2018-12-22 14:00 | 210.44 | 207.13
2018-12-22 14:30 | 112.98 | 105.5
2018-12-22 15:00 | 164.27 | 156.98
2018-12-22 15:30 | 195.57 | 188.69
2018-12-22 16:00 | 202.05 | 196.42
2018-12-22 16:30 | 191.22 | 187.89
2018-12-22 17:00 | 176.8 | 174.8
2018-12-22 17:30 | 145.06 | 144.77
2018-12-22 18:00 | 135.24 | 131.5
2018-12-22 18:30 | 135.25 | 129.58
2018-12-22 19:00 | 132.17 | 125.1
2018-12-22 19:30 | 131.07 | 123.79
2018-12-22 20:00 | 129.15 | 121.73
2018-12-22 20:30 | 126.2 | 119.13
2018-12-22 21:00 | 119.21 | 113.13
2018-12-22 21:30 | 115.09 | 110.03
2018-12-22 22:00 | 117.27 | 114.15
2018-12-22 22:30 | 139.13 | 136.06
2018-12-22 23:00 | 146.32 | 143.43
2018-12-22 23:30 | 133.47 | 129.86
2018-12-23 | 122.89 | 122.12
2018-12-23 00:30 | 108.93 | 108.33
2018-12-23 01:00 | 101.76 | 101.16
2018-12-23 01:30 | 99.8 | 99.11
2018-12-23 02:00 | 98.96 | 98.64
2018-12-23 02:30 | 99.23 | 98.87
2018-12-23 03:00 | 94.23 | 93.91
2018-12-23 03:30 | 92.68 | 92.3
2018-12-23 04:00 | 91.65 | 91.22
2018-12-23 04:30 | 93.93 | 93.41
2018-12-23 05:00 | 91.13 | 90.4
2018-12-23 05:30 | 89.5 | 88.64
2018-12-23 06:00 | 90.53 | 89.83
2018-12-23 06:30 | 91.78 | 91.1
2018-12-23 07:00 | 92.93 | 92.36
2018-12-23 07:30 | 97.4 | 97.02
2018-12-23 08:00 | 101.12 | 100.85
2018-12-23 08:30 | 110.84 | 110.6
2018-12-23 09:00 | 114.93 | 114.78
2018-12-23 09:30 | 115.01 | 114.93
2018-12-23 10:00 | 123.68 | 123.5
2018-12-23 10:30 | 123.21 | 122.76
2018-12-23 11:00 | 128.26 | 127.79
2018-12-23 11:30 | 130.8 | 130.28
2018-12-23 12:00 | 132.92 | 132.44
2018-12-23 12:30 | 135.2 | 134.77
2018-12-23 13:00 | 135.77 | 135.34
2018-12-23 13:30 | 134.54 | 134.11
2018-12-23 14:00 | 138.02 | 137.57
2018-12-23 14:30 | 134.74 | 134.28
2018-12-23 15:00 | 136.55 | 136.12
2018-12-23 15:30 | 133.85 | 133.47
2018-12-23 16:00 | 136.1 | 135.74
2018-12-23 16:30 | 137.08 | 136.75
2018-12-23 17:00 | 140.52 | 140.1
2018-12-23 17:30 | 144.77 | 144.2
2018-12-23 18:00 | 146.74 | 146.22
2018-12-23 18:30 | 148.82 | 148.19
2018-12-23 19:00 | 153.11 | 152.43
2018-12-23 19:30 | 155.39 | 154.84
2018-12-23 20:00 | 162.01 | 161.35
2018-12-23 20:30 | 156.72 | 156.06
2018-12-23 21:00 | 149.67 | 149.04
2018-12-23 21:30 | 145.31 | 144.89
2018-12-23 22:00 | 142.53 | 142.14
2018-12-23 22:30 | 140.8 | 140.42
2018-12-23 23:00 | 141.03 | 140.87
2018-12-23 23:30 | 127.89 | 127.82
2018-12-24 | 113.02 | 112.92
2018-12-24 00:30 | 100.46 | 100.24
2018-12-24 01:00 | 100.43 | 100.23
2018-12-24 01:30 | 96.41 | 96.17
2018-12-24 02:00 | 93.76 | 93.53
2018-12-24 02:30 | 90.13 | 90.03
2018-12-24 03:00 | 90.8 | 90.45
2018-12-24 03:30 | 89.15 | 88.74
2018-12-24 04:00 | 91.99 | 91.52
2018-12-24 04:30 | 94.55 | 94.05
2018-12-24 05:00 | 92.6 | 91.95
2018-12-24 05:30 | 93.42 | 92.93
2018-12-24 06:00 | 98.11 | 97.67
2018-12-24 06:30 | 101.78 | 101.44
2018-12-24 07:00 | 108.18 | 108
2018-12-24 07:30 | 111.98 | 111.89
2018-12-24 08:00 | 129.17 | 128.99
2018-12-24 08:30 | 125.59 | 125.17
2018-12-24 09:00 | 134.98 | 134.21
2018-12-24 09:30 | 136.77 | 135.73
2018-12-24 10:00 | 127.57 | 126.43
2018-12-24 10:30 | 129.94 | 128.68
2018-12-24 11:00 | 140.87 | 139.68
2018-12-24 11:30 | 144.24 | 143.03
2018-12-24 12:00 | 137.23 | 136.04
2018-12-24 12:30 | 112.55 | 111.58
2018-12-24 13:00 | 46.83 | 44.15
2018-12-24 13:30 | 44.09 | 41.02
2018-12-24 14:00 | 44.1 | 40.9
2018-12-24 14:30 | 48.25 | 45.07
2018-12-24 15:00 | 54.4 | 51.49
2018-12-24 15:30 | 69.37 | 53.44
2018-12-24 16:00 | 86.15 | 71.39
2018-12-24 16:30 | 92.37 | 82.65
2018-12-24 17:00 | 113.99 | 113.55
2018-12-24 17:30 | 126.52 | 126.28
2018-12-24 18:00 | 137.24 | 137.15
2018-12-24 18:30 | 142.9 | 139.16
2018-12-24 19:00 | 151.1 | 146.4
2018-12-24 19:30 | 153.29 | 148.48
2018-12-24 20:00 | 148.45 | 143.41
2018-12-24 20:30 | 141.44 | 138.93
2018-12-24 21:00 | 122.38 | 122.36
2018-12-24 21:30 | 121.72 | 121.64
2018-12-24 22:00 | 110.05 | 109.9
2018-12-24 22:30 | 128.81 | 128.75
2018-12-24 23:00 | 140.27 | 140.21
2018-12-24 23:30 | 99.62 | 99.56
2018-12-25 | 51.52 | 51.47
2018-12-25 00:30 | 23.08 | 23.04
2018-12-25 01:00 | 3.9 | 1.38
2018-12-25 01:30 | 4.18 | -0.34
2018-12-25 02:00 | 5.14 | -0.55
2018-12-25 02:30 | 3.05 | -0.7
2018-12-25 03:00 | 10.73 | -0.86
2018-12-25 03:30 | 11.54 | -1.7
2018-12-25 04:00 | 11.49 | -2.09
2018-12-25 04:30 | 11.54 | -2.04
2018-12-25 05:00 | 10.08 | -3.66
2018-12-25 05:30 | 22.26 | -20.03
2018-12-25 06:00 | 28.69 | -26.51
2018-12-25 06:30 | 23.47 | -20.14
2018-12-25 07:00 | 19.22 | -15.77
2018-12-25 07:30 | 10.17 | -7.17
2018-12-25 08:00 | 5.94 | -3.18
2018-12-25 08:30 | 1.74 | 0.22
2018-12-25 09:00 | 4.92 | 4.89
2018-12-25 09:30 | 18.44 | 0.54
2018-12-25 10:00 | 21.88 | 3.41
2018-12-25 10:30 | 22.5 | 2.08
2018-12-25 11:00 | 22.76 | 2.97
2018-12-25 11:30 | 23.14 | 2.9
2018-12-25 12:00 | 23.46 | 3.48
2018-12-25 12:30 | 23.02 | 4.31
2018-12-25 13:00 | 22.93 | 5.69
2018-12-25 13:30 | 23.11 | 5.76
2018-12-25 14:00 | 22.97 | 6.42
2018-12-25 14:30 | 23.72 | 8.09
2018-12-25 15:00 | 23.8 | 7.57
2018-12-25 15:30 | 24.77 | 9.86
2018-12-25 16:00 | 26.76 | 11.96
2018-12-25 16:30 | 27.89 | 14.1
2018-12-25 17:00 | 29.7 | 16.75
2018-12-25 17:30 | 29.44 | 16.25
2018-12-25 18:00 | 33.15 | 24.07
2018-12-25 18:30 | 52.81 | 49.2
2018-12-25 19:00 | 78.54 | 76.32
2018-12-25 19:30 | 82.46 | 79.65
2018-12-25 20:00 | 93.91 | 91.64
2018-12-25 20:30 | 81.46 | 79.12
2018-12-25 21:00 | 72.36 | 70.26
2018-12-25 21:30 | 70.35 | 68.74
2018-12-25 22:00 | 62.68 | 61.33
2018-12-25 22:30 | 78.71 | 77.9
2018-12-25 23:00 | 75.27 | 74.64
2018-12-25 23:30 | 58.29 | 57.7
2018-12-26 | 25.57 | 24.55
2018-12-26 00:30 | 14.86 | 13.66
2018-12-26 01:00 | 6.52 | -3.01
2018-12-26 01:30 | 15.57 | -14.47
2018-12-26 02:00 | 17.04 | -16.67
2018-12-26 02:30 | 23.04 | -18.66
2018-12-26 03:00 | 21.31 | -16.53
2018-12-26 03:30 | 22.53 | -17.84
2018-12-26 04:00 | 24.73 | -20.81
2018-12-26 04:30 | 26.83 | -23.51
2018-12-26 05:00 | 27.2 | -24.49
2018-12-26 05:30 | 27.17 | -24.88
2018-12-26 06:00 | 17.45 | -12.35
2018-12-26 06:30 | 18.24 | -14.52
2018-12-26 07:00 | 17.67 | -15.47
2018-12-26 07:30 | 10.73 | -10.13
2018-12-26 08:00 | 2.47 | -2.47
2018-12-26 08:30 | 8.9 | 1.84
2018-12-26 09:00 | 25.74 | 5.01
2018-12-26 09:30 | 27.78 | 0.58
2018-12-26 10:00 | 28.79 | 1.98
2018-12-26 10:30 | 30.35 | 0.36
2018-12-26 11:00 | 30.81 | 0.85
2018-12-26 11:30 | 32.68 | 0.03
2018-12-26 12:00 | 63.03 | 2.42
2018-12-26 12:30 | 66.88 | 9.08
2018-12-26 13:00 | 70.9 | 24.06
2018-12-26 13:30 | 76.62 | 38.49
2018-12-26 14:00 | 81.16 | 47.11
2018-12-26 14:30 | 85.38 | 53.37
2018-12-26 15:00 | 86.43 | 55.39
2018-12-26 15:30 | 89.15 | 58.99
2018-12-26 16:00 | 91.78 | 61.61
2018-12-26 16:30 | 86.55 | 59.47
2018-12-26 17:00 | 76.84 | 56.09
2018-12-26 17:30 | 78.4 | 58.79
2018-12-26 18:00 | 83.2 | 67.41
2018-12-26 18:30 | 80.21 | 66.14
2018-12-26 19:00 | 87.53 | 75.86
2018-12-26 19:30 | 101.28 | 90.87
2018-12-26 20:00 | 108.54 | 99.78
2018-12-26 20:30 | 105.61 | 100.22
2018-12-26 21:00 | 122.35 | 119.59
2018-12-26 21:30 | 113.15 | 110.65
2018-12-26 22:00 | 100.02 | 97.94
2018-12-26 22:30 | 116.53 | 115.18
2018-12-26 23:00 | 118.6 | 117.56
2018-12-26 23:30 | 85.81 | 84.75
2018-12-27 | 31.83 | 28.88
2018-12-27 00:30 | 17.52 | 12.39
2018-12-27 01:00 | 9.14 | 8.76
2018-12-27 01:30 | 10.29 | 8.56
2018-12-27 02:00 | 9.89 | 7.73
2018-12-27 02:30 | 9.74 | 7.36
2018-12-27 03:00 | 8.58 | 6.04
2018-12-27 03:30 | 6.43 | 3.57
2018-12-27 04:00 | 14.92 | 13.46
2018-12-27 04:30 | 16.15 | 15.02
2018-12-27 05:00 | 21.79 | 20.83
2018-12-27 05:30 | 25.09 | 24.26
2018-12-27 06:00 | 25.66 | 25.06
2018-12-27 06:30 | 37.09 | 36.17
2018-12-27 07:00 | 21.9 | 21.29
2018-12-27 07:30 | 21.75 | 21.75
2018-12-27 08:00 | 29.13 | 28.89
2018-12-27 08:30 | 35.34 | 34.25
2018-12-27 09:00 | 53.24 | 43.39
2018-12-27 09:30 | 60.16 | 38.27
2018-12-27 10:00 | 81.79 | 43.72
2018-12-27 10:30 | 82.74 | 44.43
2018-12-27 11:00 | 84.69 | 46.31
2018-12-27 11:30 | 87.42 | 49.88
2018-12-27 12:00 | 89.64 | 53.03
2018-12-27 12:30 | 92.07 | 56.9
2018-12-27 13:00 | 90.94 | 55.32
2018-12-27 13:30 | 88.62 | 54.78
2018-12-27 14:00 | 73.78 | -18.29
2018-12-27 14:30 | 71.06 | -2.16
2018-12-27 15:00 | 70.77 | -5.61
2018-12-27 15:30 | 71.74 | -6.49
2018-12-27 16:00 | 76.33 | 27.01
2018-12-27 16:30 | 65.83 | 22.55
2018-12-27 17:00 | 72.95 | 51.1
2018-12-27 17:30 | 85.26 | 68.12
2018-12-27 18:00 | 102.5 | 93.46
2018-12-27 18:30 | 112.72 | 110.01
2018-12-27 19:00 | 153.7 | 151.76
2018-12-27 19:30 | 164.08 | 161.96
2018-12-27 20:00 | 186.33 | 184.65
2018-12-27 20:30 | 185.58 | 185.16
2018-12-27 21:00 | 166.9 | 166.29
2018-12-27 21:30 | 156.63 | 156.47
2018-12-27 22:00 | 155.37 | 155.33
2018-12-27 22:30 | 136.42 | 136.29
2018-12-27 23:00 | 119.5 | 119.16
2018-12-27 23:30 | 89.28 | 88.55
2018-12-28 | 57.78 | 56.21
2018-12-28 00:30 | 35.39 | 32.38
2018-12-28 01:00 | 18.62 | 11.55
2018-12-28 01:30 | 15.25 | 1.96
2018-12-28 02:00 | 15.79 | 1.72
2018-12-28 02:30 | 19.69 | 10.69
2018-12-28 03:00 | 28.78 | 22.66
2018-12-28 03:30 | 46.47 | 42.99
2018-12-28 04:00 | 42.21 | 38.47
2018-12-28 04:30 | 33.49 | 28.79
2018-12-28 05:00 | 24.31 | 17.18
2018-12-28 05:30 | 18.4 | 8.55
2018-12-28 06:00 | 14.97 | -6.3
2018-12-28 06:30 | 9.76 | -2.55
2018-12-28 07:00 | 5.93 | -1.46
2018-12-28 07:30 | 7.93 | -7.83
2018-12-28 08:00 | 12.54 | -12.53
2018-12-28 08:30 | 3.62 | -2.98
2018-12-28 09:00 | 3.4 | 1.44
2018-12-28 09:30 | 10 | -5.09
2018-12-28 10:00 | 16.88 | -13.73
2018-12-28 10:30 | 19.18 | -16.04
2018-12-28 11:00 | 22.14 | -19.68
2018-12-28 11:30 | 23.26 | -21.27
2018-12-28 12:00 | 25.03 | -22.98
2018-12-28 12:30 | 15.31 | -12.68
2018-12-28 13:00 | 14.99 | -12.4
2018-12-28 13:30 | 24.38 | 18.99
2018-12-28 14:00 | 57.93 | 3.33
2018-12-28 14:30 | 59.15 | 2.84
2018-12-28 15:00 | 59.78 | -5.11
2018-12-28 15:30 | 59.27 | -3.34
2018-12-28 16:00 | 75.39 | 49.94
2018-12-28 16:30 | 76.38 | 53.26
2018-12-28 17:00 | 80.74 | 59.88
2018-12-28 17:30 | 88.58 | 71.2
2018-12-28 18:00 | 99.58 | 91.11
2018-12-28 18:30 | 103.21 | 100.18
2018-12-28 19:00 | 117.71 | 115.47
2018-12-28 19:30 | 123.78 | 121.33
2018-12-28 20:00 | 141.84 | 139.1
2018-12-28 20:30 | 160.03 | 157.72
2018-12-28 21:00 | 154.16 | 152.15
2018-12-28 21:30 | 130 | 128.24
2018-12-28 22:00 | 113.05 | 111.69
2018-12-28 22:30 | 130.44 | 129.62
2018-12-28 23:00 | 147.6 | 147.09
2018-12-28 23:30 | 110.3 | 109.96
2018-12-29 | 65.02 | 64.69
2018-12-29 00:30 | 26.14 | 25.47
2018-12-29 01:00 | 26.85 | 21.61
2018-12-29 01:30 | 22.73 | 15.47
2018-12-29 02:00 | 28.62 | 22.54
2018-12-29 02:30 | 30.46 | 24.38
2018-12-29 03:00 | 42.02 | 37.65
2018-12-29 03:30 | 31.69 | 25.77
2018-12-29 04:00 | 22.23 | 12.63
2018-12-29 04:30 | 31.24 | 25
2018-12-29 05:00 | 31.17 | 24.63
2018-12-29 05:30 | 44.72 | 40.22
2018-12-29 06:00 | 18.57 | -1.12
2018-12-29 06:30 | 19.22 | -6.48
2018-12-29 07:00 | 20.01 | -8.91
2018-12-29 07:30 | 16.31 | -11.62
2018-12-29 08:00 | 6.58 | -3.81
2018-12-29 08:30 | 7.51 | 3.59
2018-12-29 09:00 | 25.29 | 1.29
2018-12-29 09:30 | 47.3 | -11.53
2018-12-29 10:00 | 68.48 | -6.28
2018-12-29 10:30 | 70.98 | -13.21
2018-12-29 11:00 | 74.83 | 21.98
2018-12-29 11:30 | 87.74 | 49.22
2018-12-29 12:00 | 87.65 | 47.99
2018-12-29 12:30 | 89.98 | 51.94
2018-12-29 13:00 | 92.26 | 54.51
2018-12-29 13:30 | 95.05 | 58.44
2018-12-29 14:00 | 97.27 | 61.4
2018-12-29 14:30 | 101.73 | 67.17
2018-12-29 15:00 | 103.3 | 70.08
2018-12-29 15:30 | 109.61 | 79.86
2018-12-29 16:00 | 124.91 | 99.42
2018-12-29 16:30 | 113.76 | 95.47
2018-12-29 17:00 | 148.44 | 136.64
2018-12-29 17:30 | 165.7 | 155.58
2018-12-29 18:00 | 174.52 | 166.17
2018-12-29 18:30 | 183.39 | 176.33
2018-12-29 19:00 | 195.8 | 189.01
2018-12-29 19:30 | 202.94 | 195.88
2018-12-29 20:00 | 206.8 | 200.23
2018-12-29 20:30 | 205 | 201.34
2018-12-29 21:00 | 179.15 | 177.24
2018-12-29 21:30 | 176.93 | 176.89
2018-12-29 22:00 | 148.14 | 148.11
2018-12-29 22:30 | 136.9 | 136.89
2018-12-29 23:00 | 149.27 | 149.23
2018-12-29 23:30 | 141.92 | 141.91
2018-12-30 | 95.59 | 95.52
2018-12-30 00:30 | 81.33 | 81.12
2018-12-30 01:00 | 45.16 | 44.55
2018-12-30 01:30 | 37.47 | 36.58
2018-12-30 02:00 | 37.76 | 36.67
2018-12-30 02:30 | 42.83 | 41.7
2018-12-30 03:00 | 31.84 | 30.33
2018-12-30 03:30 | 40.14 | 38.8
2018-12-30 04:00 | 46.69 | 45.5
2018-12-30 04:30 | 53.87 | 52.84
2018-12-30 05:00 | 55.49 | 54.31
2018-12-30 05:30 | 52.15 | 50.89
2018-12-30 06:00 | 49.2 | 48.18
2018-12-30 06:30 | 44.36 | 43.87
2018-12-30 07:00 | 15.6 | 15.37
2018-12-30 07:30 | 19.75 | 19.74
2018-12-30 08:00 | 26.47 | 26.21
2018-12-30 08:30 | 33.11 | 32.11
2018-12-30 09:00 | 43.54 | 38.09
2018-12-30 09:30 | 66.03 | 48.14
2018-12-30 10:00 | 86.04 | 49.91
2018-12-30 10:30 | 91.04 | 56.2
2018-12-30 11:00 | 91 | 55.34
2018-12-30 11:30 | 91.34 | 54.78
2018-12-30 12:00 | 92.87 | 56.47
2018-12-30 12:30 | 93.26 | 56.79
2018-12-30 13:00 | 94.13 | 58.71
2018-12-30 13:30 | 94.86 | 60.52
2018-12-30 14:00 | 98.5 | 65.41
2018-12-30 14:30 | 101.79 | 69.42
2018-12-30 15:00 | 103.19 | 70.87
2018-12-30 15:30 | 101.35 | 75.5
2018-12-30 16:00 | 125.13 | 110.34
2018-12-30 16:30 | 139.51 | 126.48
2018-12-30 17:00 | 127.54 | 112.66
2018-12-30 17:30 | 113.8 | 97.21
2018-12-30 18:00 | 109.65 | 92.56
2018-12-30 18:30 | 108.75 | 92.76
2018-12-30 19:00 | 116.99 | 103.25
2018-12-30 19:30 | 123.58 | 110.29
2018-12-30 20:00 | 130.41 | 120.21
2018-12-30 20:30 | 134.91 | 127.01
2018-12-30 21:00 | 112.43 | 102.52
2018-12-30 21:30 | 119.34 | 111.52
2018-12-30 22:00 | 117.99 | 111.87
2018-12-30 22:30 | 104.25 | 97.84
2018-12-30 23:00 | 90.62 | 84.12
2018-12-30 23:30 | 73.7 | 73.26
2018-12-31 | 66.06 | 65.68
2018-12-31 00:30 | 59.47 | 59.16
2018-12-31 01:00 | 41.06 | 40.84
2018-12-31 01:30 | 33.99 | 33.84
2018-12-31 02:00 | 35.77 | 35.65
2018-12-31 02:30 | 29.5 | 29.45
2018-12-31 03:00 | 37.04 | 36.97
2018-12-31 03:30 | 35.77 | 35.74
2018-12-31 04:00 | 35.86 | 35.85
2018-12-31 04:30 | 37.28 | 37.28
2018-12-31 05:00 | 27.24 | 27.24
2018-12-31 05:30 | 19.39 | 19.28
2018-12-31 06:00 | 22.65 | 22.54
2018-12-31 06:30 | 34.99 | 34.96
2018-12-31 07:00 | 37.13 | 37.05
2018-12-31 07:30 | 40.34 | 39.21
2018-12-31 08:00 | 52.52 | 50.97
2018-12-31 08:30 | 58.39 | 55.98
2018-12-31 09:00 | 61.51 | 60.42
2018-12-31 09:30 | 56.35 | 54.83
2018-12-31 10:00 | 63.31 | 61.87
2018-12-31 10:30 | 63.22 | 61.92
2018-12-31 11:00 | 63.43 | 62.03
2018-12-31 11:30 | 64.46 | 62.23
2018-12-31 12:00 | 65.94 | 63.54
2018-12-31 12:30 | 69.12 | 66.82
2018-12-31 13:00 | 71.81 | 69.65
2018-12-31 13:30 | 74.27 | 72.11
2018-12-31 14:00 | 75.98 | 74.05
2018-12-31 14:30 | 80.02 | 77.94
2018-12-31 15:00 | 84.19 | 82.3
2018-12-31 15:30 | 99.64 | 98.22
2018-12-31 16:00 | 135.59 | 134.79
2018-12-31 16:30 | 130.39 | 129.48
2018-12-31 17:00 | 124.55 | 123.26
2018-12-31 17:30 | 118.7 | 116.77
2018-12-31 18:00 | 111.39 | 109.54
2018-12-31 18:30 | 110.12 | 108.19
2018-12-31 19:00 | 114.93 | 113.15
2018-12-31 19:30 | 115.41 | 113.77
2018-12-31 20:00 | 121.46 | 119.9
2018-12-31 20:30 | 119.58 | 118.97
2018-12-31 21:00 | 99.42 | 99.14
2018-12-31 21:30 | 109.67 | 109.55
2018-12-31 22:00 | 109.56 | 109.54
2018-12-31 22:30 | 144.92 | 144.92
2018-12-31 23:00 | 169.92 | 169.92
2018-12-31 23:30 | 151.65 | 151.6
2019-01-01 | 109.09 | 108.99
2019-01-01 00:30 | 92.13 | 92.05
2019-01-01 01:00 | 77.05 | 76.91
2019-01-01 01:30 | 63.69 | 63.46
2019-01-01 02:00 | 57.64 | 57.31
2019-01-01 02:30 | 58.37 | 58.19
2019-01-01 03:00 | 40.33 | 40.2
2019-01-01 03:30 | 45.55 | 45.46
2019-01-01 04:00 | 50.84 | 50.76
2019-01-01 04:30 | 59.06 | 58.98
2019-01-01 05:00 | 51.68 | 51.67
2019-01-01 05:30 | 55.43 | 55.43
2019-01-01 06:00 | 48.83 | 48.83
2019-01-01 06:30 | 54.54 | 54.5
2019-01-01 07:00 | 36.13 | 36.06
2019-01-01 07:30 | 32.44 | 32.11
2019-01-01 08:00 | 33.36 | 33.34
2019-01-01 08:30 | 38.98 | 38.95
2019-01-01 09:00 | 48.23 | 44.79
2019-01-01 09:30 | 49.7 | 43.75
2019-01-01 10:00 | 52.86 | 48.21
2019-01-01 10:30 | 53.6 | 51.43
2019-01-01 11:00 | 54.69 | 54
2019-01-01 11:30 | 55.83 | 55.13
2019-01-01 12:00 | 60.44 | 59.72
2019-01-01 12:30 | 66.18 | 65.47
2019-01-01 13:00 | 71.69 | 71
2019-01-01 13:30 | 75.7 | 74.96
2019-01-01 14:00 | 78.52 | 77.75
2019-01-01 14:30 | 72.78 | 71.81
2019-01-01 15:00 | 74.83 | 73.55
2019-01-01 15:30 | 91.41 | 90.45
2019-01-01 16:00 | 128.93 | 125.55
2019-01-01 16:30 | 157.05 | 151.74
2019-01-01 17:00 | 177.81 | 173.39
2019-01-01 17:30 | 216.84 | 213.24
2019-01-01 18:00 | 229.78 | 226.59
2019-01-01 18:30 | 229.41 | 228.74
2019-01-01 19:00 | 220.26 | 219.9
2019-01-01 19:30 | 222.91 | 222.43
2019-01-01 20:00 | 229.12 | 228.66
2019-01-01 20:30 | 209.81 | 209.52
2019-01-01 21:00 | 192.12 | 191.99
2019-01-01 21:30 | 167.14 | 166.28
2019-01-01 22:00 | 148.02 | 147.14
2019-01-01 22:30 | 147.03 | 146.68
2019-01-01 23:00 | 160.38 | 160.35
2019-01-01 23:30 | 127.91 | 127.83
2019-01-02 | 77.64 | 77.51
2019-01-02 00:30 | 64.34 | 64.29
2019-01-02 01:00 | 58.67 | 58.63
2019-01-02 01:30 | 59.19 | 59.16
2019-01-02 02:00 | 56.35 | 56.29
2019-01-02 02:30 | 46.22 | 45.94
2019-01-02 03:00 | 39.98 | 39.74
2019-01-02 03:30 | 39.82 | 39.72
2019-01-02 04:00 | 45.85 | 45.81
2019-01-02 04:30 | 42.33 | 42.32
2019-01-02 05:00 | 43.15 | 43.12
2019-01-02 05:30 | 26.67 | 26.62
2019-01-02 06:00 | 17.81 | 17.65
2019-01-02 06:30 | 51.42 | 51.41
2019-01-02 07:00 | 126.68 | 126.61
2019-01-02 07:30 | 138.1 | 137.98
2019-01-02 08:00 | 149.65 | 149.57
2019-01-02 08:30 | 146.73 | 146.43
2019-01-02 09:00 | 88.34 | 72.06
2019-01-02 09:30 | 90.44 | 71.57
2019-01-02 10:00 | 90.98 | 71.55
2019-01-02 10:30 | 70.24 | 43.3
2019-01-02 11:00 | 61.04 | 20.82
2019-01-02 11:30 | 67.08 | 35.65
2019-01-02 12:00 | 65.96 | 32.47
2019-01-02 12:30 | 61.99 | 21.08
2019-01-02 13:00 | 62.06 | 6.03
2019-01-02 13:30 | 69.31 | 34.25
2019-01-02 14:00 | 78.15 | 52.75
2019-01-02 14:30 | 96.03 | 76.28
2019-01-02 15:00 | 111.31 | 94.55
2019-01-02 15:30 | 134.3 | 120.79
2019-01-02 16:00 | 173.36 | 163.05
2019-01-02 16:30 | 193.71 | 185.01
2019-01-02 17:00 | 195.93 | 187.79
2019-01-02 17:30 | 200.37 | 193.31
2019-01-02 18:00 | 199.38 | 193.52
2019-01-02 18:30 | 194.88 | 189.53
2019-01-02 19:00 | 206.3 | 201.81
2019-01-02 19:30 | 224.19 | 219.87
2019-01-02 20:00 | 232.19 | 228.28
2019-01-02 20:30 | 201.51 | 197.79
2019-01-02 21:00 | 183.12 | 176.52
2019-01-02 21:30 | 168.1 | 160.85
2019-01-02 22:00 | 151.36 | 144.67
2019-01-02 22:30 | 167.16 | 163.98
2019-01-02 23:00 | 161.11 | 160.67
2019-01-02 23:30 | 126.39 | 125.64
2019-01-03 | 89.89 | 88.62
2019-01-03 00:30 | 90.72 | 89.02
2019-01-03 01:00 | 63.58 | 60.77
2019-01-03 01:30 | 53.21 | 49.34
2019-01-03 02:00 | 51.88 | 47.46
2019-01-03 02:30 | 41.54 | 35.8
2019-01-03 03:00 | 40.19 | 34.14
2019-01-03 03:30 | 47.1 | 41.99
2019-01-03 04:00 | 44.71 | 39.29
2019-01-03 04:30 | 53.38 | 48.92
2019-01-03 05:00 | 55.71 | 51.54
2019-01-03 05:30 | 54.53 | 50.65
2019-01-03 06:00 | 42.16 | 38.17
2019-01-03 06:30 | 61.32 | 59.68
2019-01-03 07:00 | 56.79 | 56.5
2019-01-03 07:30 | 51.76 | 51.76
2019-01-03 08:00 | 54.19 | 53.98
2019-01-03 08:30 | 49.43 | 49.22
2019-01-03 09:00 | 50.13 | 49.99
2019-01-03 09:30 | 81.19 | 81.19
2019-01-03 10:00 | 90.18 | 90.15
2019-01-03 10:30 | 81.13 | 80.45
2019-01-03 11:00 | 74.94 | 67.61
2019-01-03 11:30 | 78.61 | 71.15
2019-01-03 12:00 | 84.47 | 76.89
2019-01-03 12:30 | 89.76 | 82.51
2019-01-03 13:00 | 97.18 | 89.94
2019-01-03 13:30 | 109.14 | 102.58
2019-01-03 14:00 | 113.74 | 107.19
2019-01-03 14:30 | 117.18 | 110.45
2019-01-03 15:00 | 122.23 | 115.82
2019-01-03 15:30 | 146.59 | 141.39
2019-01-03 16:00 | 142.67 | 137.52
2019-01-03 16:30 | 161.47 | 158.77
2019-01-03 17:00 | 188.6 | 186.54
2019-01-03 17:30 | 211.05 | 209.32
2019-01-03 18:00 | 239.82 | 238.4
2019-01-03 18:30 | 249.66 | 248.66
2019-01-03 19:00 | 245.47 | 244.59
2019-01-03 19:30 | 252.9 | 251.89
2019-01-03 20:00 | 252.25 | 251.4
2019-01-03 20:30 | 249.53 | 248.82
2019-01-03 21:00 | 235.78 | 235.73
2019-01-03 21:30 | 211.72 | 211.72
2019-01-03 22:00 | 196.06 | 196.05
2019-01-03 22:30 | 200.53 | 200.53
2019-01-03 23:00 | 194.58 | 194.08
2019-01-03 23:30 | 173.22 | 172.75
2019-01-04 | 137.15 | 133.51
2019-01-04 00:30 | 119.2 | 114.69
2019-01-04 01:00 | 91.67 | 85.09
2019-01-04 01:30 | 84.54 | 77.2
2019-01-04 02:00 | 92.87 | 86.21
2019-01-04 02:30 | 87.56 | 80.66
2019-01-04 03:00 | 80.06 | 72.58
2019-01-04 03:30 | 92.51 | 86.37
2019-01-04 04:00 | 86.29 | 79.81
2019-01-04 04:30 | 78.82 | 72.14
2019-01-04 05:00 | 87.92 | 82.51
2019-01-04 05:30 | 65.89 | 58.79
2019-01-04 06:00 | 74.05 | 67.94
2019-01-04 06:30 | 53.81 | 46.8
2019-01-04 07:00 | 61.95 | 57.91
2019-01-04 07:30 | 43.2 | 43.17
2019-01-04 08:00 | 27.68 | 27.68
2019-01-04 08:30 | 28.52 | 28.07
2019-01-04 09:00 | 42.33 | 42.32
2019-01-04 09:30 | 43.8 | 43.73
2019-01-04 10:00 | 17.49 | 17.39
2019-01-04 10:30 | 14.56 | 14.56
2019-01-04 11:00 | 3.24 | 2.99
2019-01-04 11:30 | 2.15 | 1.47
2019-01-04 12:00 | 18.8 | -11.29
2019-01-04 12:30 | 55.27 | -8.7
2019-01-04 13:00 | 55.04 | -0.73
2019-01-04 13:30 | 76.1 | 66.36
2019-01-04 14:00 | 109.76 | 104.39
2019-01-04 14:30 | 59.89 | 44.52
2019-01-04 15:00 | 81.46 | 69.9
2019-01-04 15:30 | 184.1 | 179.35
2019-01-04 16:00 | 210.2 | 205.97
2019-01-04 16:30 | 151.8 | 146.15
2019-01-04 17:00 | 194.53 | 190.11
2019-01-04 17:30 | 204.33 | 200.8
2019-01-04 18:00 | 210.46 | 207.84
2019-01-04 18:30 | 218.24 | 216.49
2019-01-04 19:00 | 210.12 | 208.46
2019-01-04 19:30 | 208.79 | 206.89
2019-01-04 20:00 | 206.07 | 204.32
2019-01-04 20:30 | 202.97 | 201.09
2019-01-04 21:00 | 194.09 | 189.81
2019-01-04 21:30 | 181.43 | 177.08
2019-01-04 22:00 | 150.32 | 146.12
2019-01-04 22:30 | 155.54 | 152.11
2019-01-04 23:00 | 154.92 | 152
2019-01-04 23:30 | 95.85 | 93.13
2019-01-05 | 50 | 45.04
2019-01-05 00:30 | 60.89 | 54.74
2019-01-05 01:00 | 69.51 | 63.46
2019-01-05 01:30 | 75.93 | 70.78
2019-01-05 02:00 | 65.18 | 59.44
2019-01-05 02:30 | 52.08 | 45.01
2019-01-05 03:00 | 48.92 | 41.55
2019-01-05 03:30 | 39.42 | 30.6
2019-01-05 04:00 | 40.83 | 33.13
2019-01-05 04:30 | 43.63 | 36.12
2019-01-05 05:00 | 36.86 | 26.49
2019-01-05 05:30 | 24.23 | -0.83
2019-01-05 06:00 | 27.06 | 10.38
2019-01-05 06:30 | 26.19 | 5.55
2019-01-05 07:00 | 24.28 | -5.99
2019-01-05 07:30 | 18.37 | -16.51
2019-01-05 08:00 | 22.07 | -20.68
2019-01-05 08:30 | 25.4 | -1.33
2019-01-05 09:00 | 54.31 | 10.63
2019-01-05 09:30 | 71.11 | 14.89
2019-01-05 10:00 | 73.29 | 17.29
2019-01-05 10:30 | 73.09 | 5.94
2019-01-05 11:00 | 78.4 | 27.35
2019-01-05 11:30 | 78.53 | 32.93
2019-01-05 12:00 | 62.66 | 22.91
2019-01-05 12:30 | 61.91 | 21.48
2019-01-05 13:00 | 68.24 | 36.74
2019-01-05 13:30 | 76.4 | 52.11
2019-01-05 14:00 | 85.95 | 65.34
2019-01-05 14:30 | 126.64 | 113.13
2019-01-05 15:00 | 126.49 | 112.61
2019-01-05 15:30 | 143.58 | 133.22
2019-01-05 16:00 | 154.14 | 145.8
2019-01-05 16:30 | 186.48 | 179.35
2019-01-05 17:00 | 208.97 | 202.71
2019-01-05 17:30 | 218.22 | 214
2019-01-05 18:00 | 234.21 | 232.8
2019-01-05 18:30 | 237.88 | 236.8
2019-01-05 19:00 | 241.58 | 240.51
2019-01-05 19:30 | 246.33 | 245.12
2019-01-05 20:00 | 246.03 | 244.97
2019-01-05 20:30 | 222.42 | 222.08
2019-01-05 21:00 | 212.54 | 212.54
2019-01-05 21:30 | 189.12 | 188.82
2019-01-05 22:00 | 146.8 | 146.07
2019-01-05 22:30 | 161.89 | 160.94
2019-01-05 23:00 | 171.79 | 170.53
2019-01-05 23:30 | 137.83 | 137.41
2019-01-06 | 103.59 | 103.24
2019-01-06 00:30 | 110.15 | 109.54
2019-01-06 01:00 | 95.51 | 94.59
2019-01-06 01:30 | 81.54 | 80.29
2019-01-06 02:00 | 80.12 | 78.27
2019-01-06 02:30 | 75.12 | 72.93
2019-01-06 03:00 | 79.74 | 77.51
2019-01-06 03:30 | 66.87 | 64.12
2019-01-06 04:00 | 58.09 | 54.83
2019-01-06 04:30 | 48.32 | 44.51
2019-01-06 05:00 | 56.89 | 53.49
2019-01-06 05:30 | 53.65 | 48.47
2019-01-06 06:00 | 62.17 | 53.66
2019-01-06 06:30 | 57.42 | 48.09
2019-01-06 07:00 | 46.77 | 35.11
2019-01-06 07:30 | 47.81 | 37.99
2019-01-06 08:00 | 39.21 | 35.9
2019-01-06 08:30 | 51.32 | 51.32
2019-01-06 09:00 | 64.66 | 64.5
2019-01-06 09:30 | 67.42 | 60.56
2019-01-06 10:00 | 96.13 | 72.97
2019-01-06 10:30 | 111.81 | 91.08
2019-01-06 11:00 | 123.36 | 104.28
2019-01-06 11:30 | 127.72 | 108.09
2019-01-06 12:00 | 128.75 | 123.02
2019-01-06 12:30 | 133.52 | 131.88
2019-01-06 13:00 | 151.4 | 149.82
2019-01-06 13:30 | 167.11 | 165.51
2019-01-06 14:00 | 186.47 | 184.89
2019-01-06 14:30 | 196.57 | 194.85
2019-01-06 15:00 | 211.91 | 210.16
2019-01-06 15:30 | 230.67 | 228.9
2019-01-06 16:00 | 239.47 | 237.53
2019-01-06 16:30 | 238.23 | 236.41
2019-01-06 17:00 | 241.95 | 240.21
2019-01-06 17:30 | 243.74 | 242.06
2019-01-06 18:00 | 236.32 | 234.62
2019-01-06 18:30 | 238.06 | 236.72
2019-01-06 19:00 | 239.8 | 238.5
2019-01-06 19:30 | 242.13 | 240.42
2019-01-06 20:00 | 244.59 | 243.15
2019-01-06 20:30 | 242.42 | 241.4
2019-01-06 21:00 | 233.16 | 231.73
2019-01-06 21:30 | 228.48 | 226.65
2019-01-06 22:00 | 211.32 | 209.98
2019-01-06 22:30 | 205.83 | 205.66
2019-01-06 23:00 | 202.43 | 202.04
2019-01-06 23:30 | 186.97 | 186.35
2019-01-07 | 148.18 | 146.82
2019-01-07 00:30 | 134.66 | 132.72
2019-01-07 01:00 | 116.11 | 113.43
2019-01-07 01:30 | 111.09 | 108.31
2019-01-07 02:00 | 104.57 | 102.34
2019-01-07 02:30 | 100.2 | 95.68
2019-01-07 03:00 | 99.62 | 94.11
2019-01-07 03:30 | 98.96 | 93.75
2019-01-07 04:00 | 99.05 | 94.44
2019-01-07 04:30 | 89.38 | 84.23
2019-01-07 05:00 | 81.76 | 76.02
2019-01-07 05:30 | 95.33 | 90.49
2019-01-07 06:00 | 105.48 | 101.57
2019-01-07 06:30 | 132.31 | 131.21
2019-01-07 07:00 | 159.16 | 159.15
2019-01-07 07:30 | 163.27 | 162.99
2019-01-07 08:00 | 186.36 | 176.76
2019-01-07 08:30 | 189.47 | 179.98
2019-01-07 09:00 | 202 | 191.88
2019-01-07 09:30 | 210.25 | 199.1
2019-01-07 10:00 | 188.18 | 176.86
2019-01-07 10:30 | 180.89 | 179.12
2019-01-07 11:00 | 176.03 | 174.55
2019-01-07 11:30 | 159.11 | 157.32
2019-01-07 12:00 | 142.53 | 140.58
2019-01-07 12:30 | 169.84 | 168.09
2019-01-07 13:00 | 174.75 | 172.82
2019-01-07 13:30 | 182.72 | 180.85
2019-01-07 14:00 | 223.04 | 221.4
2019-01-07 14:30 | 240.42 | 238.94
2019-01-07 15:00 | 211.76 | 210.45
2019-01-07 15:30 | 219.16 | 218.17
2019-01-07 16:00 | 222.13 | 221.24
2019-01-07 16:30 | 216.51 | 215.83
2019-01-07 17:00 | 216.98 | 216.87
2019-01-07 17:30 | 224.72 | 223.7
2019-01-07 18:00 | 231.83 | 230.54
2019-01-07 18:30 | 241.11 | 239.95
2019-01-07 19:00 | 246.58 | 245.9
2019-01-07 19:30 | 245.14 | 244.72
2019-01-07 20:00 | 243.64 | 243.08
2019-01-07 20:30 | 237.61 | 236.86
2019-01-07 21:00 | 220.21 | 219.44
2019-01-07 21:30 | 201.8 | 201
2019-01-07 22:00 | 190.13 | 189.47
2019-01-07 22:30 | 196.52 | 196
2019-01-07 23:00 | 194.47 | 193.97
2019-01-07 23:30 | 169.46 | 169.46
2019-01-08 | 140.27 | 140.16
2019-01-08 00:30 | 122.37 | 122.2
2019-01-08 01:00 | 91.13 | 90.82
2019-01-08 01:30 | 74.79 | 74.43
2019-01-08 02:00 | 81.84 | 81.48
2019-01-08 02:30 | 83.68 | 83.45
2019-01-08 03:00 | 80.08 | 79.22
2019-01-08 03:30 | 75.81 | 74.3
2019-01-08 04:00 | 69.8 | 67.95
2019-01-08 04:30 | 80.16 | 78.53
2019-01-08 05:00 | 100 | 98.97
2019-01-08 05:30 | 110.14 | 109.31
2019-01-08 06:00 | 113.16 | 112.43
2019-01-08 06:30 | 140.85 | 140.44
2019-01-08 07:00 | 146.03 | 146.01
2019-01-08 07:30 | 148.13 | 147.79
2019-01-08 08:00 | 144.37 | 144.26
2019-01-08 08:30 | 147.66 | 147.54
2019-01-08 09:00 | 137.71 | 137.65
2019-01-08 09:30 | 139.98 | 139.2
2019-01-08 10:00 | 165.46 | 164.65
2019-01-08 10:30 | 206.95 | 206.2
2019-01-08 11:00 | 193.2 | 192.14
2019-01-08 11:30 | 198.98 | 198.14
2019-01-08 12:00 | 186.8 | 186.6
2019-01-08 12:30 | 155.9 | 155.83
2019-01-08 13:00 | 138.6 | 138.48
2019-01-08 13:30 | 171.26 | 169.39
2019-01-08 14:00 | 185.44 | 176.91
2019-01-08 14:30 | 190.23 | 182.75
2019-01-08 15:00 | 175.32 | 167.55
2019-01-08 15:30 | 161.35 | 154.8
2019-01-08 16:00 | 189.25 | 186.94
2019-01-08 16:30 | 204.24 | 202.23
2019-01-08 17:00 | 209.19 | 207.42
2019-01-08 17:30 | 220.92 | 219.53
2019-01-08 18:00 | 227.99 | 227.04
2019-01-08 18:30 | 236.85 | 236.14
2019-01-08 19:00 | 241.47 | 240.74
2019-01-08 19:30 | 237.75 | 236.91
2019-01-08 20:00 | 238.19 | 237.48
2019-01-08 20:30 | 227.35 | 227.35
2019-01-08 21:00 | 224.25 | 222.85
2019-01-08 21:30 | 201.8 | 200.42
2019-01-08 22:00 | 179.49 | 178.45
2019-01-08 22:30 | 192.4 | 191.85
2019-01-08 23:00 | 189.41 | 189
2019-01-08 23:30 | 155 | 154.5
2019-01-09 | 127.29 | 127.29
2019-01-09 00:30 | 121.41 | 121.4
2019-01-09 01:00 | 100.49 | 100.48
2019-01-09 01:30 | 107.88 | 107.88
2019-01-09 02:00 | 111.82 | 111.82
2019-01-09 02:30 | 95.8 | 95.8
2019-01-09 03:00 | 97.5 | 97.5
2019-01-09 03:30 | 95.66 | 95.65
2019-01-09 04:00 | 76.25 | 76.18
2019-01-09 04:30 | 62.76 | 62.71
2019-01-09 05:00 | 65.59 | 65.59
2019-01-09 05:30 | 79.2 | 79.19
2019-01-09 06:00 | 90.29 | 90.27
2019-01-09 06:30 | 127.07 | 127.07
2019-01-09 07:00 | 136.59 | 136.02
2019-01-09 07:30 | 152.61 | 141.69
2019-01-09 08:00 | 188.71 | 173.3
2019-01-09 08:30 | 196.01 | 182.14
2019-01-09 09:00 | 191.81 | 176.89
2019-01-09 09:30 | 193.89 | 177.59
2019-01-09 10:00 | 188.5 | 175.11
2019-01-09 10:30 | 191.63 | 180.57
2019-01-09 11:00 | 184.93 | 173.24
2019-01-09 11:30 | 183.96 | 172.23
2019-01-09 12:00 | 179.16 | 167.04
2019-01-09 12:30 | 172.19 | 159.52
2019-01-09 13:00 | 156.76 | 149.74
2019-01-09 13:30 | 164.44 | 159.04
2019-01-09 14:00 | 180.84 | 175.59
2019-01-09 14:30 | 186.37 | 181.29
2019-01-09 15:00 | 185.54 | 180.15
2019-01-09 15:30 | 203.63 | 198.57
2019-01-09 16:00 | 220.54 | 216
2019-01-09 16:30 | 248.52 | 244.69
2019-01-09 17:00 | 260.08 | 256.67
2019-01-09 17:30 | 259.04 | 256.18
2019-01-09 18:00 | 256.93 | 253.65
2019-01-09 18:30 | 255.37 | 250.51
2019-01-09 19:00 | 264.43 | 259.94
2019-01-09 19:30 | 259.2 | 254.06
2019-01-09 20:00 | 263.11 | 258.61
2019-01-09 20:30 | 246.82 | 242.63
2019-01-09 21:00 | 231.14 | 227.05
2019-01-09 21:30 | 227.24 | 223.49
2019-01-09 22:00 | 214.19 | 211.76
2019-01-09 22:30 | 189.38 | 188.98
2019-01-09 23:00 | 200.05 | 199.63
2019-01-09 23:30 | 181.36 | 180.99
2019-01-10 | 142.44 | 142.34
2019-01-10 00:30 | 129.67 | 129.53
2019-01-10 01:00 | 119.87 | 119.61
2019-01-10 01:30 | 121.99 | 121.56
2019-01-10 02:00 | 122.38 | 122.13
2019-01-10 02:30 | 116.31 | 116.23
2019-01-10 03:00 | 104.87 | 104.76
2019-01-10 03:30 | 115.28 | 115.21
2019-01-10 04:00 | 116.43 | 116.38
2019-01-10 04:30 | 126.57 | 126.53
2019-01-10 05:00 | 114.07 | 114.05
2019-01-10 05:30 | 134.19 | 134.19
2019-01-10 06:00 | 147.13 | 147.12
2019-01-10 06:30 | 159.75 | 159.56
2019-01-10 07:00 | 143.86 | 143.27
2019-01-10 07:30 | 165.15 | 161.51
2019-01-10 08:00 | 181.54 | 176.7
2019-01-10 08:30 | 198.26 | 192.76
2019-01-10 09:00 | 214.54 | 208.78
2019-01-10 09:30 | 191.75 | 187.64
2019-01-10 10:00 | 195.12 | 191.43
2019-01-10 10:30 | 188.56 | 184.16
2019-01-10 11:00 | 184.04 | 179.18
2019-01-10 11:30 | 171.29 | 167.17
2019-01-10 12:00 | 204.41 | 198.18
2019-01-10 12:30 | 196.61 | 193
2019-01-10 13:00 | 203.6 | 200.42
2019-01-10 13:30 | 211.23 | 207.78
2019-01-10 14:00 | 230.55 | 226.91
2019-01-10 14:30 | 244.51 | 240.71
2019-01-10 15:00 | 249.48 | 245.99
2019-01-10 15:30 | 247.56 | 244.27
2019-01-10 16:00 | 250.32 | 247.19
2019-01-10 16:30 | 256.45 | 253.25
2019-01-10 17:00 | 270.64 | 267.52
2019-01-10 17:30 | 273.02 | 270.24
2019-01-10 18:00 | 259.36 | 256.83
2019-01-10 18:30 | 240.17 | 238.24
2019-01-10 19:00 | 212.65 | 210.74
2019-01-10 19:30 | 161.13 | 158.48
2019-01-10 20:00 | 162.06 | 159.74
2019-01-10 20:30 | 155.91 | 153.41
2019-01-10 21:00 | 149.89 | 145.45
2019-01-10 21:30 | 137.97 | 134.81
2019-01-10 22:00 | 130.34 | 128.27
2019-01-10 22:30 | 117.77 | 115.98
2019-01-10 23:00 | 111.27 | 108.7
2019-01-10 23:30 | 93.98 | 93.38
2019-01-11 | 80.76 | 74.92
2019-01-11 00:30 | 132.93 | 129.57
2019-01-11 01:00 | 111.46 | 107.14
2019-01-11 01:30 | 95.9 | 90.55
2019-01-11 02:00 | 94.6 | 89.15
2019-01-11 02:30 | 87.26 | 81.66
2019-01-11 03:00 | 81.91 | 76.16
2019-01-11 03:30 | 98.56 | 94.43
2019-01-11 04:00 | 96.33 | 92.36
2019-01-11 04:30 | 101.34 | 97.67
2019-01-11 05:00 | 92.59 | 88.45
2019-01-11 05:30 | 93.39 | 89.27
2019-01-11 06:00 | 111.06 | 107.71
2019-01-11 06:30 | 135.31 | 135.07
2019-01-11 07:00 | 158.76 | 158.75
2019-01-11 07:30 | 145.88 | 145.7
2019-01-11 08:00 | 162.06 | 156.46
2019-01-11 08:30 | 156.13 | 148.39
2019-01-11 09:00 | 168.89 | 160.99
2019-01-11 09:30 | 158.95 | 148.45
2019-01-11 10:00 | 150.93 | 132.99
2019-01-11 10:30 | 139.15 | 118.89
2019-01-11 11:00 | 134.89 | 113.54
2019-01-11 11:30 | 118.75 | 93.08
2019-01-11 12:00 | 113.7 | 85.99
2019-01-11 12:30 | 122.15 | 96.86
2019-01-11 13:00 | 122.98 | 97.66
2019-01-11 13:30 | 84.14 | 57.24
2019-01-11 14:00 | 82.59 | 59.82
2019-01-11 14:30 | 96.25 | 77.65
2019-01-11 15:00 | 94.98 | 75.89
2019-01-11 15:30 | 126.31 | 113.03
2019-01-11 16:00 | 185.09 | 176.67
2019-01-11 16:30 | 228.77 | 222.23
2019-01-11 17:00 | 264.42 | 258.74
2019-01-11 17:30 | 263.91 | 261.81
2019-01-11 18:00 | 258.32 | 256.48
2019-01-11 18:30 | 252.34 | 249.58
2019-01-11 19:00 | 250.68 | 248.25
2019-01-11 19:30 | 251.58 | 248.93
2019-01-11 20:00 | 247.95 | 245.56
2019-01-11 20:30 | 238.91 | 236.72
2019-01-11 21:00 | 227.82 | 226.1
2019-01-11 21:30 | 190.2 | 188.64
2019-01-11 22:00 | 180.78 | 180.44
2019-01-11 22:30 | 187.49 | 186.63
2019-01-11 23:00 | 194.22 | 193.36
2019-01-11 23:30 | 174.62 | 173.37
2019-01-12 | 139.06 | 136.26
2019-01-12 00:30 | 122.81 | 119.83
2019-01-12 01:00 | 97.83 | 93.91
2019-01-12 01:30 | 86.37 | 81.86
2019-01-12 02:00 | 76.44 | 71.31
2019-01-12 02:30 | 100.34 | 97.02
2019-01-12 03:00 | 116.46 | 112.65
2019-01-12 03:30 | 86.32 | 80.78
2019-01-12 04:00 | 68.37 | 61.3
2019-01-12 04:30 | 69.6 | 63.07
2019-01-12 05:00 | 73.06 | 67.27
2019-01-12 05:30 | 72.49 | 67.4
2019-01-12 06:00 | 73.92 | 68.92
2019-01-12 06:30 | 77.2 | 72
2019-01-12 07:00 | 50.26 | 41.88
2019-01-12 07:30 | 43.1 | 36.1
2019-01-12 08:00 | 37.29 | 34.5
2019-01-12 08:30 | 48.65 | 48.59
2019-01-12 09:00 | 64.71 | 64.45
2019-01-12 09:30 | 70.77 | 70.76
2019-01-12 10:00 | 74.84 | 74.47
2019-01-12 10:30 | 52.12 | 51.79
2019-01-12 11:00 | 36.19 | 35.9
2019-01-12 11:30 | 34.11 | 33.82
2019-01-12 12:00 | 35.94 | 35.63
2019-01-12 12:30 | 34.73 | 34.45
2019-01-12 13:00 | 31.62 | 31.4
2019-01-12 13:30 | 43.45 | 43.33
2019-01-12 14:00 | 72.03 | 71.99
2019-01-12 14:30 | 95.72 | 95.72
2019-01-12 15:00 | 97.1 | 97.1
2019-01-12 15:30 | 100.33 | 100.28
2019-01-12 16:00 | 115.36 | 112.47
2019-01-12 16:30 | 140.23 | 131.72
2019-01-12 17:00 | 134.74 | 125.78
2019-01-12 17:30 | 150.22 | 145.67
2019-01-12 18:00 | 141.86 | 139.84
2019-01-12 18:30 | 166.1 | 165.91
2019-01-12 19:00 | 144.18 | 143.73
2019-01-12 19:30 | 149.16 | 148.84
2019-01-12 20:00 | 150.45 | 150.03
2019-01-12 20:30 | 151.32 | 150.72
2019-01-12 21:00 | 146.17 | 145.43
2019-01-12 21:30 | 153.43 | 152.3
2019-01-12 22:00 | 153.7 | 152.1
2019-01-12 22:30 | 177.04 | 175.8
2019-01-12 23:00 | 163.77 | 162.76
2019-01-12 23:30 | 135.8 | 135.22
2019-01-13 | 106.1 | 104.97
2019-01-13 00:30 | 87.24 | 85.55
2019-01-13 01:00 | 69.28 | 66.77
2019-01-13 01:30 | 60.94 | 57.83
2019-01-13 02:00 | 50.49 | 46.69
2019-01-13 02:30 | 50.61 | 45.7
2019-01-13 03:00 | 48.72 | 41.11
2019-01-13 03:30 | 58.99 | 49.24
2019-01-13 04:00 | 60.49 | 51.11
2019-01-13 04:30 | 69.08 | 61.22
2019-01-13 05:00 | 73.52 | 66.7
2019-01-13 05:30 | 57.43 | 49.43
2019-01-13 06:00 | 50.58 | 40.89
2019-01-13 06:30 | 49.46 | 38.88
2019-01-13 07:00 | 41.04 | 29.24
2019-01-13 07:30 | 45.55 | 33.44
2019-01-13 08:00 | 42.64 | 33.5
2019-01-13 08:30 | 38.53 | 36.3
2019-01-13 09:00 | 38.43 | 38.38
2019-01-13 09:30 | 50.32 | 50.03
2019-01-13 10:00 | 57.59 | 57.07
2019-01-13 10:30 | 66.2 | 64.48
2019-01-13 11:00 | 77.42 | 70.44
2019-01-13 11:30 | 83.08 | 76.48
2019-01-13 12:00 | 85.59 | 78.89
2019-01-13 12:30 | 112.56 | 107.51
2019-01-13 13:00 | 112.7 | 107.36
2019-01-13 13:30 | 115.64 | 110.09
2019-01-13 14:00 | 133.99 | 119.27
2019-01-13 14:30 | 153.79 | 139.35
2019-01-13 15:00 | 173.96 | 161.56
2019-01-13 15:30 | 160.04 | 146.18
2019-01-13 16:00 | 174.87 | 161.86
2019-01-13 16:30 | 187.4 | 175.47
2019-01-13 17:00 | 223.48 | 213.25
2019-01-13 17:30 | 241.7 | 232.31
2019-01-13 18:00 | 248.69 | 240.08
2019-01-13 18:30 | 248 | 240.33
2019-01-13 19:00 | 243.49 | 235.88
2019-01-13 19:30 | 246.5 | 238.51
2019-01-13 20:00 | 245.52 | 238.04
2019-01-13 20:30 | 235.9 | 230.48
2019-01-13 21:00 | 215.77 | 213.26
2019-01-13 21:30 | 207.3 | 205.22
2019-01-13 22:00 | 195.83 | 195.78
2019-01-13 22:30 | 190.59 | 190.32
2019-01-13 23:00 | 185.09 | 184.75
2019-01-13 23:30 | 157.73 | 157.09
2019-01-14 | 109.85 | 108.63
2019-01-14 00:30 | 84.27 | 82.18
2019-01-14 01:00 | 67.65 | 64.64
2019-01-14 01:30 | 70.15 | 67.08
2019-01-14 02:00 | 73.02 | 69.77
2019-01-14 02:30 | 61.69 | 57.91
2019-01-14 03:00 | 58 | 54
2019-01-14 03:30 | 53.72 | 49.38
2019-01-14 04:00 | 43.86 | 38.87
2019-01-14 04:30 | 31.99 | 25.21
2019-01-14 05:00 | 52.97 | 49.15
2019-01-14 05:30 | 74.66 | 72.18
2019-01-14 06:00 | 95.46 | 94.05
2019-01-14 06:30 | 96.07 | 95.76
2019-01-14 07:00 | 94.17 | 94.17
2019-01-14 07:30 | 96.86 | 96.74
2019-01-14 08:00 | 104.14 | 103.87
2019-01-14 08:30 | 107.26 | 107.25
2019-01-14 09:00 | 85.92 | 85.83
2019-01-14 09:30 | 77.94 | 77.81
2019-01-14 10:00 | 53.11 | 51.61
2019-01-14 10:30 | 48.4 | 27.13
2019-01-14 11:00 | 67.5 | 43.63
2019-01-14 11:30 | 65.31 | 39.58
2019-01-14 12:00 | 63.3 | 34.37
2019-01-14 12:30 | 58.54 | 21.08
2019-01-14 13:00 | 59.7 | 21.37
2019-01-14 13:30 | 63.58 | 25.17
2019-01-14 14:00 | 69.57 | 36.88
2019-01-14 14:30 | 70.77 | 39.18
2019-01-14 15:00 | 78.35 | 52.4
2019-01-14 15:30 | 72.82 | 42.1
2019-01-14 16:00 | 75.72 | 45.84
2019-01-14 16:30 | 79.89 | 53.24
2019-01-14 17:00 | 95.29 | 75.43
2019-01-14 17:30 | 127.8 | 116.26
2019-01-14 18:00 | 134.1 | 129.43
2019-01-14 18:30 | 117.87 | 116.05
2019-01-14 19:00 | 111.57 | 109.59
2019-01-14 19:30 | 77.41 | 71.99
2019-01-14 20:00 | 80.15 | 75.53
2019-01-14 20:30 | 82.78 | 79.81
2019-01-14 21:00 | 105.44 | 104.6
2019-01-14 21:30 | 118.4 | 117.61
2019-01-14 22:00 | 127.68 | 127.32
2019-01-14 22:30 | 87.91 | 87.65
2019-01-14 23:00 | 106.69 | 106.6
2019-01-14 23:30 | 87.21 | 87.16
2019-01-15 | 61.35 | 59.34
2019-01-15 00:30 | 44.05 | 41.34
2019-01-15 01:00 | 35.23 | 30.81
2019-01-15 01:30 | 41.82 | 37.38
2019-01-15 02:00 | 46.67 | 41.82
2019-01-15 02:30 | 37.99 | 31.81
2019-01-15 03:00 | 44.34 | 38.84
2019-01-15 03:30 | 45.47 | 36.94
2019-01-15 04:00 | 41.41 | 31.55
2019-01-15 04:30 | 44.4 | 35.67
2019-01-15 05:00 | 44.82 | 35.91
2019-01-15 05:30 | 45.2 | 36.52
2019-01-15 06:00 | 48.94 | 40.79
2019-01-15 06:30 | 61.08 | 55.47
2019-01-15 07:00 | 76.23 | 75.66
2019-01-15 07:30 | 90.55 | 90.36
2019-01-15 08:00 | 86.9 | 86.69
2019-01-15 08:30 | 55.1 | 55.1
2019-01-15 09:00 | 43.55 | 42.99
2019-01-15 09:30 | 39.86 | 30.31
2019-01-15 10:00 | 74.86 | 34.46
2019-01-15 10:30 | 73.63 | 30.64
2019-01-15 11:00 | 73.86 | 30.05
2019-01-15 11:30 | 73.92 | 28.07
2019-01-15 12:00 | 73.54 | 22.63
2019-01-15 12:30 | 74.77 | 27
2019-01-15 13:00 | 68.61 | 26.03
2019-01-15 13:30 | 70.88 | 28.47
2019-01-15 14:00 | 74.94 | 35.05
2019-01-15 14:30 | 78.34 | 41.89
2019-01-15 15:00 | 83.24 | 50.05
2019-01-15 15:30 | 86.62 | 54.26
2019-01-15 16:00 | 70.61 | -3.04
2019-01-15 16:30 | 80.47 | -32.61
2019-01-15 17:00 | 75.29 | -15.06
2019-01-15 17:30 | 73.71 | -21.78
2019-01-15 18:00 | 66.93 | -15.04
2019-01-15 18:30 | 59.02 | 17.88
2019-01-15 19:00 | 84.78 | 78.45
2019-01-15 19:30 | 99.55 | 85.75
2019-01-15 20:00 | 58.74 | 31.2
2019-01-15 20:30 | 54 | 33.73
2019-01-15 21:00 | 129.47 | 129.46
2019-01-15 21:30 | 120.77 | 120.29
2019-01-15 22:00 | 112.08 | 111.47
2019-01-15 22:30 | 103.03 | 102.13
2019-01-15 23:00 | 119.07 | 118.13
2019-01-15 23:30 | 105.39 | 103.66
2019-01-16 | 85.87 | 84.82
2019-01-16 00:30 | 75.49 | 74.14
2019-01-16 01:00 | 58.06 | 55.97
2019-01-16 01:30 | 33.55 | 29.22
2019-01-16 02:00 | 25.49 | 18.98
2019-01-16 02:30 | 25.93 | 19.28
2019-01-16 03:00 | 25.52 | 18.27
2019-01-16 03:30 | 19.2 | 8.29
2019-01-16 04:00 | 16.99 | -0.77
2019-01-16 04:30 | 16.47 | -1.38
2019-01-16 05:00 | 16.92 | 3.68
2019-01-16 05:30 | 17.74 | 7.72
2019-01-16 06:00 | 30.49 | 27.62
2019-01-16 06:30 | 29.92 | 29.5
2019-01-16 07:00 | 45.13 | 45.13
2019-01-16 07:30 | 31.63 | 31.6
2019-01-16 08:00 | 47.75 | 47.74
2019-01-16 08:30 | 32.08 | 13.7
2019-01-16 09:00 | 51.27 | -31.08
2019-01-16 09:30 | 42.58 | 10.72
2019-01-16 10:00 | 52.8 | 29.49
2019-01-16 10:30 | 48.52 | 10.26
2019-01-16 11:00 | 50.25 | -9.15
2019-01-16 11:30 | 63.74 | 42.12
2019-01-16 12:00 | 55.86 | 26
2019-01-16 12:30 | 53.22 | 20.63
2019-01-16 13:00 | 49.33 | 11.63
2019-01-16 13:30 | 49.73 | -4.94
2019-01-16 14:00 | 75.6 | -42.92
2019-01-16 14:30 | 68.85 | 3.7
2019-01-16 15:00 | 79.28 | -38.21
2019-01-16 15:30 | 74.05 | -16.74
2019-01-16 16:00 | 75.82 | 21.57
2019-01-16 16:30 | 74.37 | 15.28
2019-01-16 17:00 | 76.27 | -13.37
2019-01-16 17:30 | 123.18 | 104.86
2019-01-16 18:00 | 138.56 | 126.83
2019-01-16 18:30 | 161.08 | 157.65
2019-01-16 19:00 | 170.26 | 167.25
2019-01-16 19:30 | 173.02 | 169.92
2019-01-16 20:00 | 156.05 | 153.07
2019-01-16 20:30 | 59.63 | 51.93
2019-01-16 21:00 | 110.9 | 108.91
2019-01-16 21:30 | 170.08 | 170.07
2019-01-16 22:00 | 187.62 | 187.49
2019-01-16 22:30 | 164.6 | 164.5
2019-01-16 23:00 | 160.59 | 160.4
2019-01-16 23:30 | 139.37 | 138.28
2019-01-17 | 96.79 | 95.14
2019-01-17 00:30 | 58.81 | 54.75
2019-01-17 01:00 | 50.02 | 41.53
2019-01-17 01:30 | 55.33 | 47.84
2019-01-17 02:00 | 42.38 | 32.65
2019-01-17 02:30 | 50.46 | 42.92
2019-01-17 03:00 | 50.44 | 41.47
2019-01-17 03:30 | 37.89 | 26.32
2019-01-17 04:00 | 42.39 | 34.38
2019-01-17 04:30 | 41.03 | 32.94
2019-01-17 05:00 | 32.04 | 20.1
2019-01-17 05:30 | 29.46 | 15.05
2019-01-17 06:00 | 23.53 | 2.34
2019-01-17 06:30 | 36.26 | 33.39
2019-01-17 07:00 | 36.21 | 35.24
2019-01-17 07:30 | 36.98 | 36.33
2019-01-17 08:00 | 43.64 | 39.19
2019-01-17 08:30 | 63.78 | 55.08
2019-01-17 09:00 | 46.41 | 33.35
2019-01-17 09:30 | 76.83 | 69.78
2019-01-17 10:00 | 85.25 | 78.4
2019-01-17 10:30 | 74.74 | 66.54
2019-01-17 11:00 | 63.61 | 53.18
2019-01-17 11:30 | 65.7 | 55.68
2019-01-17 12:00 | 55.41 | 41.6
2019-01-17 12:30 | 72.35 | -54.81
2019-01-17 13:00 | 47.38 | -5.15
2019-01-17 13:30 | 60.45 | -40.3
2019-01-17 14:00 | 87.8 | -62.96
2019-01-17 14:30 | 71.78 | -26.02
2019-01-17 15:00 | 84.01 | -52.06
2019-01-17 15:30 | 64.08 | 5.65
2019-01-17 16:00 | 74.82 | -42.1
2019-01-17 16:30 | 72.59 | -31.26
2019-01-17 17:00 | 63.46 | -2.79
2019-01-17 17:30 | 61.37 | -12.95
2019-01-17 18:00 | 94.6 | 80.16
2019-01-17 18:30 | 98.31 | 86.42
2019-01-17 19:00 | 159.16 | 154.5
2019-01-17 19:30 | 142 | 140
2019-01-17 20:00 | 128.29 | 125.67
2019-01-17 20:30 | 123.5 | 118.22
2019-01-17 21:00 | 123.88 | 119.79
2019-01-17 21:30 | 131.46 | 129.3
2019-01-17 22:00 | 121.04 | 121.04
2019-01-17 22:30 | 109.78 | 108.36
2019-01-17 23:00 | 104.72 | 103.83
2019-01-17 23:30 | 103.35 | 101.83
2019-01-18 | 77.84 | 76.4
2019-01-18 00:30 | 79.99 | 78.47
2019-01-18 01:00 | 58.13 | 55.58
2019-01-18 01:30 | 55.35 | 52.26
2019-01-18 02:00 | 37.61 | 32.68
2019-01-18 02:30 | 28.81 | 21.41
2019-01-18 03:00 | 19.63 | 0.82
2019-01-18 03:30 | 19.92 | -5.63
2019-01-18 04:00 | 21.02 | -8.62
2019-01-18 04:30 | 20.17 | 7.42
2019-01-18 05:00 | 26.9 | 19.62
2019-01-18 05:30 | 37.64 | 32.88
2019-01-18 06:00 | 28.86 | 24.56
2019-01-18 06:30 | 57.13 | 56
2019-01-18 07:00 | 85.93 | 85.67
2019-01-18 07:30 | 77.13 | 75.47
2019-01-18 08:00 | 95.91 | 75.65
2019-01-18 08:30 | 100.1 | 73.92
2019-01-18 09:00 | 112.76 | 86.67
2019-01-18 09:30 | 115.15 | 84.83
2019-01-18 10:00 | 94.66 | 55.51
2019-01-18 10:30 | 95.83 | 57.67
2019-01-18 11:00 | 110.25 | 77.88
2019-01-18 11:30 | 110.76 | 77.66
2019-01-18 12:00 | 123.91 | 95.05
2019-01-18 12:30 | 151.4 | 126.95
2019-01-18 13:00 | 163.55 | 140.95
2019-01-18 13:30 | 173.11 | 151.11
2019-01-18 14:00 | 190.1 | 158.9
2019-01-18 14:30 | 188.65 | 156.93
2019-01-18 15:00 | 197.67 | 170.35
2019-01-18 15:30 | 168.84 | 158.41
2019-01-18 16:00 | 183.14 | 168.91
2019-01-18 16:30 | 188.87 | 175.03
2019-01-18 17:00 | 174.83 | 160.81
2019-01-18 17:30 | 180.77 | 167.9
2019-01-18 18:00 | 178.29 | 166.96
2019-01-18 18:30 | 178.71 | 169.75
2019-01-18 19:00 | 190.26 | 184.03
2019-01-18 19:30 | 176.93 | 173.42
2019-01-18 20:00 | 163.08 | 159.84
2019-01-18 20:30 | 156.89 | 154.45
2019-01-18 21:00 | 119.17 | 117.08
2019-01-18 21:30 | 111.66 | 109.3
2019-01-18 22:00 | 93.48 | 91.65
2019-01-18 22:30 | 116.4 | 114.42
2019-01-18 23:00 | 128.15 | 126.8
2019-01-18 23:30 | 106.52 | 105.54
2019-01-19 | 87.19 | 86.41
2019-01-19 00:30 | 76.96 | 76.41
2019-01-19 01:00 | 74.96 | 74.65
2019-01-19 01:30 | 65.5 | 63.65
2019-01-19 02:00 | 52 | 49.6
2019-01-19 02:30 | 49.5 | 46.8
2019-01-19 03:00 | 51.1 | 48.28
2019-01-19 03:30 | 53.56 | 50.78
2019-01-19 04:00 | 28.32 | 23.15
2019-01-19 04:30 | 31.98 | 27.67
2019-01-19 05:00 | 28.55 | 23.51
2019-01-19 05:30 | 25.55 | 19.47
2019-01-19 06:00 | 22.19 | 16.74
2019-01-19 06:30 | 27.93 | 25.76
2019-01-19 07:00 | 29.12 | 28.47
2019-01-19 07:30 | 35.96 | 35.96
2019-01-19 08:00 | 47.37 | 42.24
2019-01-19 08:30 | 83.87 | 57.68
2019-01-19 09:00 | 84.19 | 52.42
2019-01-19 09:30 | 80.78 | 39.77
2019-01-19 10:00 | 83.09 | 42.17
2019-01-19 10:30 | 71.57 | 33.76
2019-01-19 11:00 | 76 | 47
2019-01-19 11:30 | 100.48 | 80.78
2019-01-19 12:00 | 111.26 | 96
2019-01-19 12:30 | 124.27 | 111.72
2019-01-19 13:00 | 133.11 | 121.09
2019-01-19 13:30 | 156.04 | 145.11
2019-01-19 14:00 | 173.44 | 162.84
2019-01-19 14:30 | 188.41 | 178.15
2019-01-19 15:00 | 202.09 | 192.39
2019-01-19 15:30 | 225.72 | 216.56
2019-01-19 16:00 | 241.48 | 232.32
2019-01-19 16:30 | 271.98 | 263.49
2019-01-19 17:00 | 270.76 | 266
2019-01-19 17:30 | 274.95 | 270.73
2019-01-19 18:00 | 272.45 | 268.68
2019-01-19 18:30 | 272.26 | 269.54
2019-01-19 19:00 | 264.49 | 261.83
2019-01-19 19:30 | 260.43 | 257.4
2019-01-19 20:00 | 255.65 | 252.91
2019-01-19 20:30 | 247.86 | 245.9
2019-01-19 21:00 | 243.78 | 240.57
2019-01-19 21:30 | 234.04 | 231.03
2019-01-19 22:00 | 208.23 | 204.97
2019-01-19 22:30 | 216.41 | 213.16
2019-01-19 23:00 | 211.79 | 208.99
2019-01-19 23:30 | 169.18 | 168.82
2019-01-20 | 144.86 | 142.97
2019-01-20 00:30 | 125.72 | 123.96
2019-01-20 01:00 | 118.49 | 116.55
2019-01-20 01:30 | 143.34 | 142.06
2019-01-20 02:00 | 141.02 | 139.83
2019-01-20 02:30 | 129.55 | 128.33
2019-01-20 03:00 | 110.49 | 108.96
2019-01-20 03:30 | 106.74 | 105.14
2019-01-20 04:00 | 89.86 | 87.99
2019-01-20 04:30 | 88.07 | 86.3
2019-01-20 05:00 | 86.39 | 84.55
2019-01-20 05:30 | 91.13 | 88.53
2019-01-20 06:00 | 77.14 | 74.16
2019-01-20 06:30 | 68.04 | 64.52
2019-01-20 07:00 | 53.4 | 51.88
2019-01-20 07:30 | 64.21 | 63.86
2019-01-20 08:00 | 73.73 | 73.73
2019-01-20 08:30 | 92.79 | 92.72
2019-01-20 09:00 | 104.93 | 101.81
2019-01-20 09:30 | 118.5 | 114.45
2019-01-20 10:00 | 123.79 | 119.15
2019-01-20 10:30 | 120.77 | 104.8
2019-01-20 11:00 | 131.49 | 99.57
2019-01-20 11:30 | 125.21 | 91.79
2019-01-20 12:00 | 133.11 | 105.62
2019-01-20 12:30 | 137.75 | 110.62
2019-01-20 13:00 | 142.39 | 122.7
2019-01-20 13:30 | 147.76 | 138.95
2019-01-20 14:00 | 156.81 | 147.94
2019-01-20 14:30 | 170.94 | 162.73
2019-01-20 15:00 | 188.32 | 180.04
2019-01-20 15:30 | 214.5 | 207.17
2019-01-20 16:00 | 229.01 | 221.94
2019-01-20 16:30 | 238.39 | 231.27
2019-01-20 17:00 | 242.67 | 235.66
2019-01-20 17:30 | 237.79 | 231.36
2019-01-20 18:00 | 236.92 | 230.65
2019-01-20 18:30 | 235.57 | 230.04
2019-01-20 19:00 | 236.29 | 230.75
2019-01-20 19:30 | 243.22 | 232.75
2019-01-20 20:00 | 243.29 | 233.3
2019-01-20 20:30 | 236.81 | 227.88
2019-01-20 21:00 | 238.75 | 230.77
2019-01-20 21:30 | 232.88 | 226.31
2019-01-20 22:00 | 214.27 | 213.5
2019-01-20 22:30 | 203.16 | 202.63
2019-01-20 23:00 | 197.92 | 197.45
2019-01-20 23:30 | 172.82 | 172.56
2019-01-21 | 145.06 | 144.62
2019-01-21 00:30 | 121.7 | 121.22
2019-01-21 01:00 | 90.78 | 90.38
2019-01-21 01:30 | 96.27 | 96.08
2019-01-21 02:00 | 94.39 | 94.26
2019-01-21 02:30 | 80.48 | 80.35
2019-01-21 03:00 | 76.49 | 76.35
2019-01-21 03:30 | 67.63 | 67.48
2019-01-21 04:00 | 54.02 | 53.76
2019-01-21 04:30 | 67.6 | 67.33
2019-01-21 05:00 | 73.29 | 72.94
2019-01-21 05:30 | 70.69 | 70.27
2019-01-21 06:00 | 82.25 | 81.55
2019-01-21 06:30 | 134.94 | 132.83
2019-01-21 07:00 | 155.86 | 151.72
2019-01-21 07:30 | 140.72 | 133.33
2019-01-21 08:00 | 130.7 | 117.57
2019-01-21 08:30 | 123.51 | 108.49
2019-01-21 09:00 | 125.12 | 107.55
2019-01-21 09:30 | 131.31 | 113.34
2019-01-21 10:00 | 132.02 | 115.81
2019-01-21 10:30 | 134.87 | 118.55
2019-01-21 11:00 | 134.06 | 117.65
2019-01-21 11:30 | 133.48 | 116.94
2019-01-21 12:00 | 129.56 | 112.55
2019-01-21 12:30 | 136.61 | 120.29
2019-01-21 13:00 | 132.09 | 113.68
2019-01-21 13:30 | 117.72 | 95.39
2019-01-21 14:00 | 131.32 | 110.93
2019-01-21 14:30 | 136.8 | 116.18
2019-01-21 15:00 | 151.8 | 133.35
2019-01-21 15:30 | 179.48 | 164.39
2019-01-21 16:00 | 196.91 | 182.87
2019-01-21 16:30 | 220.82 | 209.18
2019-01-21 17:00 | 241.77 | 231.27
2019-01-21 17:30 | 253.7 | 245.25
2019-01-21 18:00 | 250.65 | 243.17
2019-01-21 18:30 | 269.81 | 264.47
2019-01-21 19:00 | 232.67 | 226.94
2019-01-21 19:30 | 231.25 | 225.19
2019-01-21 20:00 | 223.11 | 217.49
2019-01-21 20:30 | 234.27 | 230.14
2019-01-21 21:00 | 232.61 | 232.6
2019-01-21 21:30 | 231.73 | 231.73
2019-01-21 22:00 | 207.05 | 206.99
2019-01-21 22:30 | 208.55 | 208.55
2019-01-21 23:00 | 207.43 | 207.42
2019-01-21 23:30 | 186.24 | 186.07
2019-01-22 | 169.36 | 169.2
2019-01-22 00:30 | 147.72 | 147.39
2019-01-22 01:00 | 134.29 | 133.75
2019-01-22 01:30 | 126.57 | 125.68
2019-01-22 02:00 | 92.46 | 91.07
2019-01-22 02:30 | 71.65 | 69.77
2019-01-22 03:00 | 61.88 | 59.71
2019-01-22 03:30 | 55.35 | 53.21
2019-01-22 04:00 | 56.89 | 55.05
2019-01-22 04:30 | 62.15 | 60.6
2019-01-22 05:00 | 80.02 | 78.89
2019-01-22 05:30 | 83.72 | 82.82
2019-01-22 06:00 | 85.62 | 85.09
2019-01-22 06:30 | 122.27 | 122.17
2019-01-22 07:00 | 152.02 | 151.97
2019-01-22 07:30 | 159.12 | 150.91
2019-01-22 08:00 | 153.26 | 137.62
2019-01-22 08:30 | 156.51 | 139.98
2019-01-22 09:00 | 154.45 | 136.86
2019-01-22 09:30 | 137.54 | 114.77
2019-01-22 10:00 | 124.08 | 95.66
2019-01-22 10:30 | 123.36 | 83.69
2019-01-22 11:00 | 123.78 | 89.76
2019-01-22 11:30 | 130.66 | 99.14
2019-01-22 12:00 | 114.91 | 80
2019-01-22 12:30 | 108.16 | 68.16
2019-01-22 13:00 | 126.61 | 92.14
2019-01-22 13:30 | 130.95 | 93.02
2019-01-22 14:00 | 135.11 | 98.67
2019-01-22 14:30 | 115.37 | 64.97
2019-01-22 15:00 | 104.49 | 37.6
2019-01-22 15:30 | 124.46 | 78.1
2019-01-22 16:00 | 118.63 | 48.06
2019-01-22 16:30 | 120.64 | 35
2019-01-22 17:00 | 161.26 | 115.83
2019-01-22 17:30 | 182.45 | 151.82
2019-01-22 18:00 | 158.73 | 133.6
2019-01-22 18:30 | 164.83 | 146.14
2019-01-22 19:00 | 140.99 | 118.22
2019-01-22 19:30 | 162.75 | 142.81
2019-01-22 20:00 | 199.13 | 184.91
2019-01-22 20:30 | 215.22 | 209.8
2019-01-22 21:00 | 196.84 | 192
2019-01-22 21:30 | 166.64 | 163.04
2019-01-22 22:00 | 149.21 | 148.93
2019-01-22 22:30 | 156.52 | 156.42
2019-01-22 23:00 | 176.58 | 176.19
2019-01-22 23:30 | 140.73 | 140.66
2019-01-23 | 94.21 | 94.03
2019-01-23 00:30 | 93.89 | 93.48
2019-01-23 01:00 | 102.57 | 101.94
2019-01-23 01:30 | 100.42 | 99.83
2019-01-23 02:00 | 80.18 | 79.35
2019-01-23 02:30 | 69.75 | 68.76
2019-01-23 03:00 | 54.23 | 52.87
2019-01-23 03:30 | 54.5 | 53.09
2019-01-23 04:00 | 56.87 | 55.64
2019-01-23 04:30 | 80.54 | 79.71
2019-01-23 05:00 | 87.53 | 86.58
2019-01-23 05:30 | 89.89 | 89.2
2019-01-23 06:00 | 91.56 | 91.28
2019-01-23 06:30 | 138.96 | 138.96
2019-01-23 07:00 | 164.83 | 163.21
2019-01-23 07:30 | 178.34 | 172.08
2019-01-23 08:00 | 202.67 | 180.32
2019-01-23 08:30 | 194.28 | 169.12
2019-01-23 09:00 | 177.21 | 158.5
2019-01-23 09:30 | 164.51 | 157.27
2019-01-23 10:00 | 149.9 | 141.24
2019-01-23 10:30 | 117.62 | 103.93
2019-01-23 11:00 | 129.9 | 102.62
2019-01-23 11:30 | 125.9 | 94.9
2019-01-23 12:00 | 118.31 | 89.03
2019-01-23 12:30 | 123.02 | 96.12
2019-01-23 13:00 | 145.81 | 123.61
2019-01-23 13:30 | 145.23 | 122.12
2019-01-23 14:00 | 153.47 | 130.21
2019-01-23 14:30 | 177.66 | 156.99
2019-01-23 15:00 | 195.62 | 176.83
2019-01-23 15:30 | 205.42 | 184.81
2019-01-23 16:00 | 234.13 | 209.17
2019-01-23 16:30 | 219.2 | 194.16
2019-01-23 17:00 | 209.79 | 187.51
2019-01-23 17:30 | 192.04 | 175.58
2019-01-23 18:00 | 177.34 | 166.39
2019-01-23 18:30 | 205.77 | 197.44
2019-01-23 19:00 | 245.97 | 238.75
2019-01-23 19:30 | 281.14 | 274.48
2019-01-23 20:00 | 286.22 | 280.16
2019-01-23 20:30 | 263.01 | 260.84
2019-01-23 21:00 | 252.41 | 249.35
2019-01-23 21:30 | 243.7 | 240.67
2019-01-23 22:00 | 209.99 | 206.39
2019-01-23 22:30 | 214.9 | 211.77
2019-01-23 23:00 | 215.11 | 212.5
2019-01-23 23:30 | 194.16 | 193.93
2019-01-24 | 172.79 | 172.5
2019-01-24 00:30 | 156.65 | 155.59
2019-01-24 01:00 | 139.95 | 138.65
2019-01-24 01:30 | 128.28 | 126.94
2019-01-24 02:00 | 110.34 | 108.82
2019-01-24 02:30 | 108.3 | 106.86
2019-01-24 03:00 | 106.2 | 104.67
2019-01-24 03:30 | 96.79 | 95.33
2019-01-24 04:00 | 99.42 | 98.44
2019-01-24 04:30 | 104.11 | 103.34
2019-01-24 05:00 | 118.9 | 118.24
2019-01-24 05:30 | 118.55 | 117.85
2019-01-24 06:00 | 117.87 | 117.29
2019-01-24 06:30 | 139.29 | 138.79
2019-01-24 07:00 | 157.17 | 151.5
2019-01-24 07:30 | 174.08 | 166.64
2019-01-24 08:00 | 180.89 | 175.19
2019-01-24 08:30 | 186.77 | 178.98
2019-01-24 09:00 | 192.18 | 182.73
2019-01-24 09:30 | 196.89 | 186.63
2019-01-24 10:00 | 201.08 | 192.73
2019-01-24 10:30 | 202.4 | 195.07
2019-01-24 11:00 | 197.9 | 190.46
2019-01-24 11:30 | 169.65 | 160.97
2019-01-24 12:00 | 164.74 | 155.74
2019-01-24 12:30 | 206.43 | 198.81
2019-01-24 13:00 | 211.14 | 203.4
2019-01-24 13:30 | 211.53 | 202.91
2019-01-24 14:00 | 219.34 | 211.27
2019-01-24 14:30 | 155.82 | 144.42
2019-01-24 15:00 | 147.84 | 134.55
2019-01-24 15:30 | 199.82 | 190.4
2019-01-24 16:00 | 185.03 | 168.54
2019-01-24 16:30 | 195.71 | 182.51
2019-01-24 17:00 | 194.53 | 182.23
2019-01-24 17:30 | 196.73 | 186.8
2019-01-24 18:00 | 243.06 | 240.54
2019-01-24 18:30 | 271.62 | 269.57
2019-01-24 19:00 | 272.09 | 269.88
2019-01-24 19:30 | 254.28 | 251.88
2019-01-24 20:00 | 246.57 | 244.47
2019-01-24 20:30 | 277.89 | 277.02
2019-01-24 21:00 | 266.95 | 266.9
2019-01-24 21:30 | 213.68 | 213.68
2019-01-24 22:00 | 179.76 | 179.6
2019-01-24 22:30 | 208.56 | 208.1
2019-01-24 23:00 | 215.69 | 215.62
2019-01-24 23:30 | 192.49 | 192.35
2019-01-25 | 151.1 | 150.75
2019-01-25 00:30 | 127.18 | 126.75
2019-01-25 01:00 | 106.32 | 105.86
2019-01-25 01:30 | 94.92 | 94.43
2019-01-25 02:00 | 76.79 | 76.22
2019-01-25 02:30 | 67.17 | 66.54
2019-01-25 03:00 | 64.64 | 64.01
2019-01-25 03:30 | 48.82 | 48.17
2019-01-25 04:00 | 54.05 | 53.56
2019-01-25 04:30 | 72.07 | 71.71
2019-01-25 05:00 | 70.94 | 70.54
2019-01-25 05:30 | 84.08 | 83.58
2019-01-25 06:00 | 78.3 | 77.83
2019-01-25 06:30 | 125.78 | 125.44
2019-01-25 07:00 | 126.61 | 126.37
2019-01-25 07:30 | 122.27 | 122.22
2019-01-25 08:00 | 131.3 | 130.64
2019-01-25 08:30 | 139.71 | 135.03
2019-01-25 09:00 | 169.2 | 148.35
2019-01-25 09:30 | 172.87 | 151.77
2019-01-25 10:00 | 180.99 | 159.51
2019-01-25 10:30 | 193.81 | 173.09
2019-01-25 11:00 | 158.76 | 131.99
2019-01-25 11:30 | 154.53 | 130.37
2019-01-25 12:00 | 125.36 | 94.37
2019-01-25 12:30 | 94.32 | 35.41
2019-01-25 13:00 | 148.98 | 122.03
2019-01-25 13:30 | 161.86 | 138.57
2019-01-25 14:00 | 149.89 | 124.23
2019-01-25 14:30 | 88.76 | 3.23
2019-01-25 15:00 | 95.49 | 26.86
2019-01-25 15:30 | 107.6 | 59.24
2019-01-25 16:00 | 147.92 | 119.82
2019-01-25 16:30 | 161.64 | 137.22
2019-01-25 17:00 | 160.8 | 136.35
2019-01-25 17:30 | 160.04 | 138.71
2019-01-25 18:00 | 157.01 | 139.44
2019-01-25 18:30 | 86.11 | 51.57
2019-01-25 19:00 | 73.46 | 24.46
2019-01-25 19:30 | 74.43 | -6.82
2019-01-25 20:00 | 70.83 | -3.58
2019-01-25 20:30 | 141.64 | 133.75
2019-01-25 21:00 | 98.38 | 88.24
2019-01-25 21:30 | 118 | 116.03
2019-01-25 22:00 | 122.5 | 121.54
2019-01-25 22:30 | 144.51 | 143.06
2019-01-25 23:00 | 160.32 | 160.24
2019-01-25 23:30 | 149.59 | 149.55
2019-01-26 | 126.51 | 126.49
2019-01-26 00:30 | 139.88 | 139.75
2019-01-26 01:00 | 127.79 | 127.71
2019-01-26 01:30 | 117.04 | 116.25
2019-01-26 02:00 | 108.05 | 107.22
2019-01-26 02:30 | 98.92 | 97.94
2019-01-26 03:00 | 85.47 | 84.22
2019-01-26 03:30 | 86.66 | 85.29
2019-01-26 04:00 | 79.62 | 78.06
2019-01-26 04:30 | 72.02 | 70.28
2019-01-26 05:00 | 74.78 | 73.15
2019-01-26 05:30 | 70.19 | 68.45
2019-01-26 06:00 | 62.19 | 59.96
2019-01-26 06:30 | 67.15 | 65.83
2019-01-26 07:00 | 61.48 | 60.69
2019-01-26 07:30 | 74.62 | 74.6
2019-01-26 08:00 | 73.01 | 71.54
2019-01-26 08:30 | 97.52 | 93.53
2019-01-26 09:00 | 109.06 | 98.8
2019-01-26 09:30 | 119.35 | 84.97
2019-01-26 10:00 | 98.95 | 49.28
2019-01-26 10:30 | 92.42 | -31.2
2019-01-26 11:00 | 104.9 | -63.12
2019-01-26 11:30 | 93.35 | -43.74
2019-01-26 12:00 | 108.2 | -67.73
2019-01-26 12:30 | 106.53 | -62.89
2019-01-26 13:00 | 110.86 | -67.89
2019-01-26 13:30 | 115.62 | -73.52
2019-01-26 14:00 | 103.75 | -53.68
2019-01-26 14:30 | 89.96 | -19.25
2019-01-26 15:00 | 105.83 | -52.61
2019-01-26 15:30 | 99.84 | -49.01
2019-01-26 16:00 | 74.26 | -36.96
2019-01-26 16:30 | 62.85 | -3.73
2019-01-26 17:00 | 77.7 | -38.3
2019-01-26 17:30 | 63.96 | -9.16
2019-01-26 18:00 | 98.32 | 84.94
2019-01-26 18:30 | 110.87 | 107.41
2019-01-26 19:00 | 108.2 | 104.58
2019-01-26 19:30 | 109.36 | 105.34
2019-01-26 20:00 | 118.25 | 115.16
2019-01-26 20:30 | 114.45 | 108.75
2019-01-26 21:00 | 118.27 | 112.36
2019-01-26 21:30 | 111.59 | 106.72
2019-01-26 22:00 | 106.57 | 102.99
2019-01-26 22:30 | 125.27 | 125.09
2019-01-26 23:00 | 128.52 | 128.14
2019-01-26 23:30 | 110.43 | 109.7
2019-01-27 | 77.53 | 76.39
2019-01-27 00:30 | 60.8 | 59.71
2019-01-27 01:00 | 44.78 | 42.74
2019-01-27 01:30 | 37.25 | 34.51
2019-01-27 02:00 | 37.63 | 34.52
2019-01-27 02:30 | 28.78 | 24.22
2019-01-27 03:00 | 26.39 | 21
2019-01-27 03:30 | 23.16 | 16.75
2019-01-27 04:00 | 18.96 | 9.56
2019-01-27 04:30 | 17.56 | 6.02
2019-01-27 05:00 | 25.23 | 19
2019-01-27 05:30 | 19.5 | 9.87
2019-01-27 06:00 | 16.53 | 1.99
2019-01-27 06:30 | 15.4 | -8.14
2019-01-27 07:00 | 40.24 | -39.68
2019-01-27 07:30 | 29.81 | -29.79
2019-01-27 08:00 | 20.43 | -20.24
2019-01-27 08:30 | 7.34 | 6.02
2019-01-27 09:00 | 15.28 | 13.79
2019-01-27 09:30 | 23.36 | 22.94
2019-01-27 10:00 | 23.1 | 23.08
2019-01-27 10:30 | 15.45 | 15.26
2019-01-27 11:00 | 14.76 | 14.12
2019-01-27 11:30 | 9.07 | -1.78
2019-01-27 12:00 | 43.78 | -2.65
2019-01-27 12:30 | 58.62 | 16.39
2019-01-27 13:00 | 62.06 | 21.94
2019-01-27 13:30 | 66.5 | 30.75
2019-01-27 14:00 | 77.88 | 50.93
2019-01-27 14:30 | 84.53 | 60.09
2019-01-27 15:00 | 85.41 | 60.53
2019-01-27 15:30 | 89.74 | 65.34
2019-01-27 16:00 | 126.47 | 110.48
2019-01-27 16:30 | 150.06 | 137.17
2019-01-27 17:00 | 168.08 | 156.55
2019-01-27 17:30 | 180.04 | 171.83
2019-01-27 18:00 | 186.39 | 182.91
2019-01-27 18:30 | 180.78 | 179.13
2019-01-27 19:00 | 169.69 | 168.17
2019-01-27 19:30 | 156.6 | 154.76
2019-01-27 20:00 | 141.78 | 140.06
2019-01-27 20:30 | 131.33 | 131.07
2019-01-27 21:00 | 111.6 | 111.6
2019-01-27 21:30 | 102.79 | 102.79
2019-01-27 22:00 | 99.26 | 99.17
2019-01-27 22:30 | 117.12 | 116.93
2019-01-27 23:00 | 124.18 | 123.81
2019-01-27 23:30 | 96.76 | 96.45
2019-01-28 | 50.98 | 50.5
2019-01-28 00:30 | 45.37 | 44.36
2019-01-28 01:00 | 39.15 | 37.29
2019-01-28 01:30 | 39.11 | 36.41
2019-01-28 02:00 | 48.22 | 45.37
2019-01-28 02:30 | 41.45 | 37.9
2019-01-28 03:00 | 34.52 | 30
2019-01-28 03:30 | 27.3 | 21.48
2019-01-28 04:00 | 16.31 | -1.67
2019-01-28 04:30 | 16.14 | 2.17
2019-01-28 05:00 | 15.63 | -1.21
2019-01-28 05:30 | 63.14 | -62.29
2019-01-28 06:00 | 73.93 | -73.48
2019-01-28 06:30 | 10.73 | 4.97
2019-01-28 07:00 | 14.37 | 13.25
2019-01-28 07:30 | 30.8 | 30.78
2019-01-28 08:00 | 44.26 | 44.19
2019-01-28 08:30 | 55.31 | 53.6
2019-01-28 09:00 | 55.98 | 55
2019-01-28 09:30 | 69.92 | 69.55
2019-01-28 10:00 | 70.58 | 70.39
2019-01-28 10:30 | 49.15 | 49.06
2019-01-28 11:00 | 42.31 | 42.27
2019-01-28 11:30 | 22.44 | 22.42
2019-01-28 12:00 | 17.88 | 8.1
2019-01-28 12:30 | 40.68 | 32.32
2019-01-28 13:00 | 41.04 | 19.92
2019-01-28 13:30 | 87.25 | 35.19
2019-01-28 14:00 | 89.04 | 39.88
2019-01-28 14:30 | 98.47 | 56.53
2019-01-28 15:00 | 91.27 | 39.12
2019-01-28 15:30 | 96.08 | 43.38
2019-01-28 16:00 | 106.33 | 60.36
2019-01-28 16:30 | 98.36 | 33.11
2019-01-28 17:00 | 150.41 | 119.79
2019-01-28 17:30 | 172.82 | 147.63
2019-01-28 18:00 | 179.22 | 156.29
2019-01-28 18:30 | 171.2 | 153.28
2019-01-28 19:00 | 174.52 | 162.45
2019-01-28 19:30 | 183.44 | 171.3
2019-01-28 20:00 | 207.69 | 197.86
2019-01-28 20:30 | 227.09 | 221.76
2019-01-28 21:00 | 203.03 | 200.96
2019-01-28 21:30 | 167.04 | 165.46
2019-01-28 22:00 | 148 | 147.37
2019-01-28 22:30 | 162.84 | 162.8
2019-01-28 23:00 | 173.78 | 173.43
2019-01-28 23:30 | 139.01 | 138.99
2019-01-29 | 103.27 | 103.14
2019-01-29 00:30 | 84.73 | 84.47
2019-01-29 01:00 | 72.77 | 72.28
2019-01-29 01:30 | 68.73 | 68.06
2019-01-29 02:00 | 78.54 | 77.84
2019-01-29 02:30 | 69.02 | 68.2
2019-01-29 03:00 | 56.08 | 54.9
2019-01-29 03:30 | 69.32 | 68.35
2019-01-29 04:00 | 65.58 | 64.68
2019-01-29 04:30 | 65.63 | 64.65
2019-01-29 05:00 | 74.66 | 73.68
2019-01-29 05:30 | 84.05 | 83.22
2019-01-29 06:00 | 90.33 | 89.96
2019-01-29 06:30 | 100.23 | 100.22
2019-01-29 07:00 | 92.78 | 92.71
2019-01-29 07:30 | 103.24 | 102.98
2019-01-29 08:00 | 95.62 | 84.26
2019-01-29 08:30 | 118.51 | 112.88
2019-01-29 09:00 | 106.27 | 98.43
2019-01-29 09:30 | 99.33 | 88.86
2019-01-29 10:00 | 105.47 | 95.29
2019-01-29 10:30 | 93.54 | 70.12
2019-01-29 11:00 | 76.72 | 38.53
2019-01-29 11:30 | 73.42 | 12.04
2019-01-29 12:00 | 74.53 | 18.81
2019-01-29 12:30 | 92.19 | 57.54
2019-01-29 13:00 | 90.97 | 53.05
2019-01-29 13:30 | 87 | 28.87
2019-01-29 14:00 | 82.42 | 18.86
2019-01-29 14:30 | 83.01 | 18.86
2019-01-29 15:00 | 83.7 | 21.75
2019-01-29 15:30 | 87.48 | 28.92
2019-01-29 16:00 | 131.8 | 109.16
2019-01-29 16:30 | 129.98 | 107.43
2019-01-29 17:00 | 153.14 | 126.61
2019-01-29 17:30 | 118.19 | 100.45
2019-01-29 18:00 | 148.82 | 138.2
2019-01-29 18:30 | 109.54 | 103.56
2019-01-29 19:00 | 79.91 | 72.89
2019-01-29 19:30 | 139.55 | 135.71
2019-01-29 20:00 | 157.61 | 155.27
2019-01-29 20:30 | 147.35 | 145.29
2019-01-29 21:00 | 139.94 | 139.93
2019-01-29 21:30 | 166.75 | 166.75
2019-01-29 22:00 | 133.18 | 133.18
2019-01-29 22:30 | 134.24 | 134.21
2019-01-29 23:00 | 127.52 | 127.42
2019-01-29 23:30 | 89.34 | 89.17
2019-01-30 | 46.29 | 44.76
2019-01-30 00:30 | 39.45 | 36.11
2019-01-30 01:00 | 24.88 | 18.96
2019-01-30 01:30 | 35.14 | 30.13
2019-01-30 02:00 | 35.48 | 30.51
2019-01-30 02:30 | 36.75 | 32.19
2019-01-30 03:00 | 33.64 | 28.74
2019-01-30 03:30 | 31.65 | 26.82
2019-01-30 04:00 | 20.54 | 15.57
2019-01-30 04:30 | 28.88 | 25.85
2019-01-30 05:00 | 48.2 | 46.83
2019-01-30 05:30 | 51.08 | 50.25
2019-01-30 06:00 | 47.07 | 46.59
2019-01-30 06:30 | 69.13 | 69.12
2019-01-30 07:00 | 97.86 | 97.31
2019-01-30 07:30 | 106.54 | 102.88
2019-01-30 08:00 | 88.37 | 82.31
2019-01-30 08:30 | 100.75 | 84.98
2019-01-30 09:00 | 85.32 | 56.52
2019-01-30 09:30 | 70.72 | 1.03
2019-01-30 10:00 | 64.94 | 3.72
2019-01-30 10:30 | 64.96 | 5.17
2019-01-30 11:00 | 66.9 | 5.77
2019-01-30 11:30 | 70.73 | 15.94
2019-01-30 12:00 | 89.33 | 36.31
2019-01-30 12:30 | 89.83 | 16.32
2019-01-30 13:00 | 92.08 | 21.75
2019-01-30 13:30 | 96.3 | 17.4
2019-01-30 14:00 | 113.79 | 32.7
2019-01-30 14:30 | 100.69 | 61.22
2019-01-30 15:00 | 79.8 | 27.69
2019-01-30 15:30 | 85.68 | 41.58
2019-01-30 16:00 | 129.69 | 105.63
2019-01-30 16:30 | 160.11 | 141.43
2019-01-30 17:00 | 181.58 | 165.38
2019-01-30 17:30 | 169.91 | 154.19
2019-01-30 18:00 | 172.7 | 162.27
2019-01-30 18:30 | 197.31 | 193.43
2019-01-30 19:00 | 166.88 | 161.51
2019-01-30 19:30 | 167.22 | 162.27
2019-01-30 20:00 | 175.1 | 171.24
2019-01-30 20:30 | 176.54 | 174.59
2019-01-30 21:00 | 158.18 | 157.84
2019-01-30 21:30 | 154.16 | 153.97
2019-01-30 22:00 | 157.57 | 157.46
2019-01-30 22:30 | 169.05 | 168.92
2019-01-30 23:00 | 196.98 | 196.8
2019-01-30 23:30 | 181.44 | 181
2019-01-31 | 167.86 | 167.69
2019-01-31 00:30 | 151.47 | 151.13
2019-01-31 01:00 | 136.72 | 136.07
2019-01-31 01:30 | 142.2 | 141.23
2019-01-31 02:00 | 132.56 | 131.44
2019-01-31 02:30 | 117.46 | 116.21
2019-01-31 03:00 | 102.33 | 100.86
2019-01-31 03:30 | 88.49 | 86.94
2019-01-31 04:00 | 93.49 | 92.35
2019-01-31 04:30 | 98.55 | 97.65
2019-01-31 05:00 | 109.66 | 108.75
2019-01-31 05:30 | 104.69 | 103.64
2019-01-31 06:00 | 110.31 | 109.5
2019-01-31 06:30 | 122.67 | 122.59
2019-01-31 07:00 | 121.97 | 121.76
2019-01-31 07:30 | 163.37 | 163.36
2019-01-31 08:00 | 166.03 | 164.86
2019-01-31 08:30 | 159.64 | 157.3
2019-01-31 09:00 | 165.2 | 157.19
2019-01-31 09:30 | 196.05 | 187.17
2019-01-31 10:00 | 197.56 | 187.95
2019-01-31 10:30 | 196.57 | 185.93
2019-01-31 11:00 | 209.75 | 198.73
2019-01-31 11:30 | 188.38 | 175.61
2019-01-31 12:00 | 155.68 | 140.59
2019-01-31 12:30 | 128.77 | 109.52
2019-01-31 13:00 | 146.75 | 127.47
2019-01-31 13:30 | 157.85 | 128.89
2019-01-31 14:00 | 160.11 | 130.18
2019-01-31 14:30 | 149.78 | 118.8
2019-01-31 15:00 | 139.93 | 106.45
2019-01-31 15:30 | 157.19 | 126.96
2019-01-31 16:00 | 171.27 | 144.07
2019-01-31 16:30 | 151.14 | 118.33
2019-01-31 17:00 | 140.47 | 102.82
2019-01-31 17:30 | 187.97 | 165.45
2019-01-31 18:00 | 220.44 | 204.22
2019-01-31 18:30 | 234.8 | 220.79
2019-01-31 19:00 | 230.94 | 216.29
2019-01-31 19:30 | 251.88 | 237.52
2019-01-31 20:00 | 237.31 | 223.76
2019-01-31 20:30 | 245.67 | 238.91
2019-01-31 21:00 | 239.68 | 230.32
2019-01-31 21:30 | 233.99 | 226.43
2019-01-31 22:00 | 220.7 | 213.75
2019-01-31 22:30 | 222.73 | 217.01
2019-01-31 23:00 | 218.28 | 212.03
2019-01-31 23:30 | 184.22 | 184.08
2019-02-01 | 150.52 | 150.37
2019-02-01 00:30 | 138.13 | 137.88
2019-02-01 01:00 | 125.07 | 124.76
2019-02-01 01:30 | 107.87 | 107.39
2019-02-01 02:00 | 105.82 | 105.15
2019-02-01 02:30 | 103 | 102.22
2019-02-01 03:00 | 91.53 | 90.49
2019-02-01 03:30 | 98.23 | 97.33
2019-02-01 04:00 | 93.86 | 92.88
2019-02-01 04:30 | 97.42 | 96.59
2019-02-01 05:00 | 104.16 | 103.46
2019-02-01 05:30 | 89.83 | 89.28
2019-02-01 06:00 | 112.45 | 112.16
2019-02-01 06:30 | 134.55 | 134.2
2019-02-01 07:00 | 157.04 | 146.15
2019-02-01 07:30 | 177.05 | 161.45
2019-02-01 08:00 | 180.01 | 168.06
2019-02-01 08:30 | 183.38 | 171.71
2019-02-01 09:00 | 181.42 | 168.94
2019-02-01 09:30 | 182.7 | 171.55
2019-02-01 10:00 | 191.74 | 180.13
2019-02-01 10:30 | 196.26 | 184.32
2019-02-01 11:00 | 199.11 | 187.4
2019-02-01 11:30 | 196.97 | 184.48
2019-02-01 12:00 | 195 | 181.65
2019-02-01 12:30 | 194.4 | 180.81
2019-02-01 13:00 | 179.25 | 164.98
2019-02-01 13:30 | 159.74 | 147.29
2019-02-01 14:00 | 153.63 | 142.88
2019-02-01 14:30 | 172.86 | 161.66
2019-02-01 15:00 | 181.66 | 171.79
2019-02-01 15:30 | 228.54 | 222.23
2019-02-01 16:00 | 265.64 | 260.85
2019-02-01 16:30 | 262.65 | 258.08
2019-02-01 17:00 | 258.64 | 255.1
2019-02-01 17:30 | 251.71 | 250.7
2019-02-01 18:00 | 248.42 | 247.6
2019-02-01 18:30 | 242.54 | 242.08
2019-02-01 19:00 | 242.23 | 241.58
2019-02-01 19:30 | 246.61 | 245.89
2019-02-01 20:00 | 239.34 | 238.69
2019-02-01 20:30 | 245.63 | 245.29
2019-02-01 21:00 | 234.79 | 234.34
2019-02-01 21:30 | 171.37 | 170.79
2019-02-01 22:00 | 183.12 | 182.98
2019-02-01 22:30 | 210.68 | 210.63
2019-02-01 23:00 | 203.07 | 203.07
2019-02-01 23:30 | 173.02 | 173.02
2019-02-02 | 141.17 | 141.06
2019-02-02 00:30 | 124.69 | 124.17
2019-02-02 01:00 | 100.29 | 99.31
2019-02-02 01:30 | 72.53 | 71
2019-02-02 02:00 | 65.37 | 63.63
2019-02-02 02:30 | 48.21 | 46.33
2019-02-02 03:00 | 33.48 | 31.04
2019-02-02 03:30 | 34.25 | 32
2019-02-02 04:00 | 24.97 | 22.62
2019-02-02 04:30 | 57.53 | 56.12
2019-02-02 05:00 | 73.46 | 72.4
2019-02-02 05:30 | 80.4 | 79.62
2019-02-02 06:00 | 88.06 | 87.51
2019-02-02 06:30 | 63.35 | 62.71
2019-02-02 07:00 | 77.37 | 76.84
2019-02-02 07:30 | 90.08 | 89.78
2019-02-02 08:00 | 97.72 | 97.29
2019-02-02 08:30 | 124.23 | 123.65
2019-02-02 09:00 | 140.04 | 139.48
2019-02-02 09:30 | 113.91 | 112.99
2019-02-02 10:00 | 114.68 | 113.82
2019-02-02 10:30 | 118.58 | 117.96
2019-02-02 11:00 | 115.65 | 107.03
2019-02-02 11:30 | 122.59 | 110.44
2019-02-02 12:00 | 135.47 | 124.74
2019-02-02 12:30 | 133.51 | 122.69
2019-02-02 13:00 | 134.42 | 123.3
2019-02-02 13:30 | 124.86 | 112.35
2019-02-02 14:00 | 153.12 | 142.5
2019-02-02 14:30 | 162.07 | 151.86
2019-02-02 15:00 | 176.29 | 166.59
2019-02-02 15:30 | 184.26 | 175
2019-02-02 16:00 | 215.11 | 207.1
2019-02-02 16:30 | 224.02 | 216.62
2019-02-02 17:00 | 239.13 | 232.09
2019-02-02 17:30 | 222.27 | 215.27
2019-02-02 18:00 | 210.41 | 204.02
2019-02-02 18:30 | 217.55 | 212.01
2019-02-02 19:00 | 235.56 | 230.29
2019-02-02 19:30 | 231.86 | 226.25
2019-02-02 20:00 | 210.75 | 205.02
2019-02-02 20:30 | 212.4 | 203.27
2019-02-02 21:00 | 211.75 | 203.66
2019-02-02 21:30 | 172.89 | 164.03
2019-02-02 22:00 | 184.62 | 181.97
2019-02-02 22:30 | 167.82 | 167.77
2019-02-02 23:00 | 173.39 | 173.32
2019-02-02 23:30 | 136.25 | 136.09
2019-02-03 | 115.56 | 115.18
2019-02-03 00:30 | 107.55 | 106.9
2019-02-03 01:00 | 91.46 | 90.48
2019-02-03 01:30 | 87.57 | 86.38
2019-02-03 02:00 | 84.18 | 82.71
2019-02-03 02:30 | 69.83 | 67.67
2019-02-03 03:00 | 54.57 | 51.64
2019-02-03 03:30 | 51.59 | 48.55
2019-02-03 04:00 | 45.05 | 41.67
2019-02-03 04:30 | 59.7 | 57.37
2019-02-03 05:00 | 66.63 | 64.49
2019-02-03 05:30 | 55.41 | 52.88
2019-02-03 06:00 | 96.25 | 94.83
2019-02-03 06:30 | 94.38 | 93.15
2019-02-03 07:00 | 87.66 | 86.66
2019-02-03 07:30 | 94.22 | 93.6
2019-02-03 08:00 | 54.53 | 54.06
2019-02-03 08:30 | 52.55 | 52.53
2019-02-03 09:00 | 66.53 | 66.53
2019-02-03 09:30 | 59.23 | 59.14
2019-02-03 10:00 | 63.15 | 62.79
2019-02-03 10:30 | 97.31 | 94.8
2019-02-03 11:00 | 83.35 | 77.15
2019-02-03 11:30 | 65.52 | 57.01
2019-02-03 12:00 | 63.85 | 54.43
2019-02-03 12:30 | 58.95 | 48.19
2019-02-03 13:00 | 52.32 | 38.3
2019-02-03 13:30 | 57.57 | 37.07
2019-02-03 14:00 | 82.6 | 45.34
2019-02-03 14:30 | 81.82 | 38.12
2019-02-03 15:00 | 84.89 | 44.23
2019-02-03 15:30 | 88.62 | 51.89
2019-02-03 16:00 | 83.78 | 61.53
2019-02-03 16:30 | 91.61 | 71.34
2019-02-03 17:00 | 99.15 | 80.24
2019-02-03 17:30 | 102.41 | 85.87
2019-02-03 18:00 | 107.51 | 93.41
2019-02-03 18:30 | 118.52 | 107.22
2019-02-03 19:00 | 111.15 | 98.56
2019-02-03 19:30 | 108.84 | 95.03
2019-02-03 20:00 | 104.25 | 90.37
2019-02-03 20:30 | 95.62 | 83.32
2019-02-03 21:00 | 76.3 | 70.35
2019-02-03 21:30 | 70.07 | 59.31
2019-02-03 22:00 | 57.11 | 46.23
2019-02-03 22:30 | 68.61 | 61.28
2019-02-03 23:00 | 67.92 | 62
2019-02-03 23:30 | 30.27 | 30.06
2019-02-04 | 11.24 | 8.61
2019-02-04 00:30 | 11.47 | 5.98
2019-02-04 01:00 | 11.12 | -2.14
2019-02-04 01:30 | 13.94 | -7.01
2019-02-04 02:00 | 15.29 | -8.75
2019-02-04 02:30 | 16.58 | -10.98
2019-02-04 03:00 | 17.78 | -12.6
2019-02-04 03:30 | 18.13 | -13.37
2019-02-04 04:00 | 16.35 | -11.17
2019-02-04 04:30 | 16.63 | -12.66
2019-02-04 05:00 | 11.53 | 2.03
2019-02-04 05:30 | 12.68 | 8.42
2019-02-04 06:00 | 13.01 | -11.28
2019-02-04 06:30 | 26.54 | 26.48
2019-02-04 07:00 | 50.55 | 41.84
2019-02-04 07:30 | 79.93 | 50.99
2019-02-04 08:00 | 83.88 | 50.39
2019-02-04 08:30 | 83.94 | 41.78
2019-02-04 09:00 | 87.78 | 43.05
2019-02-04 09:30 | 93.44 | 46.83
2019-02-04 10:00 | 95.22 | 48.7
2019-02-04 10:30 | 96.94 | 46.86
2019-02-04 11:00 | 105.59 | 40.72
2019-02-04 11:30 | 113.34 | 44.32
2019-02-04 12:00 | 107.73 | 31.53
2019-02-04 12:30 | 106.16 | 21.02
2019-02-04 13:00 | 108.28 | 24.5
2019-02-04 13:30 | 108.75 | 22.11
2019-02-04 14:00 | 110.17 | 23.98
2019-02-04 14:30 | 121.78 | 20.31
2019-02-04 15:00 | 95.86 | 31.22
2019-02-04 15:30 | 94.09 | 45.14
2019-02-04 16:00 | 90.58 | 34.89
2019-02-04 16:30 | 99.47 | 54.79
2019-02-04 17:00 | 87.16 | 27.25
2019-02-04 17:30 | 86.44 | 34.92
2019-02-04 18:00 | 80.89 | 25.2
2019-02-04 18:30 | 99.31 | 85.15
2019-02-04 19:00 | 132.54 | 129.8
2019-02-04 19:30 | 154.97 | 152.77
2019-02-04 20:00 | 138 | 135.62
2019-02-04 20:30 | 140.57 | 137.63
2019-02-04 21:00 | 143.53 | 143.47
2019-02-04 21:30 | 130.15 | 130.12
2019-02-04 22:00 | 94.47 | 94.42
2019-02-04 22:30 | 98.17 | 98.14
2019-02-04 23:00 | 104.93 | 104.87
2019-02-04 23:30 | 83.69 | 83.62
2019-02-05 | 50.06 | 49.73
2019-02-05 00:30 | 41.46 | 41.41
2019-02-05 01:00 | 31.84 | 29.56
2019-02-05 01:30 | 27.54 | 24.07
2019-02-05 02:00 | 45.65 | 43.23
2019-02-05 02:30 | 49.05 | 46.55
2019-02-05 03:00 | 48.82 | 46.38
2019-02-05 03:30 | 44.27 | 41.65
2019-02-05 04:00 | 36.52 | 33.85
2019-02-05 04:30 | 21.29 | 17.11
2019-02-05 05:00 | 26.27 | 23.18
2019-02-05 05:30 | 23.65 | 21.29
2019-02-05 06:00 | 24.15 | 22.92
2019-02-05 06:30 | 38.62 | 38.62
2019-02-05 07:00 | 84.29 | 69.03
2019-02-05 07:30 | 89.16 | 63.13
2019-02-05 08:00 | 94.27 | 65.53
2019-02-05 08:30 | 104.16 | 75.2
2019-02-05 09:00 | 107.39 | 74.73
2019-02-05 09:30 | 107.73 | 72.27
2019-02-05 10:00 | 101.95 | 78.27
2019-02-05 10:30 | 101.72 | 76.18
2019-02-05 11:00 | 103 | 77.29
2019-02-05 11:30 | 103.26 | 78.2
2019-02-05 12:00 | 106.94 | 82.53
2019-02-05 12:30 | 114.75 | 91.84
2019-02-05 13:00 | 127.74 | 107.67
2019-02-05 13:30 | 121.13 | 99.06
2019-02-05 14:00 | 127.22 | 105.53
2019-02-05 14:30 | 128.83 | 107.16
2019-02-05 15:00 | 134.03 | 114.53
2019-02-05 15:30 | 138.87 | 120.75
2019-02-05 16:00 | 138.35 | 120.66
2019-02-05 16:30 | 129.17 | 110.99
2019-02-05 17:00 | 131.54 | 114.01
2019-02-05 17:30 | 129.12 | 113.77
2019-02-05 18:00 | 149.73 | 138.61
2019-02-05 18:30 | 156.22 | 147.18
2019-02-05 19:00 | 160.6 | 151.18
2019-02-05 19:30 | 165.06 | 155.83
2019-02-05 20:00 | 177.02 | 165.06
2019-02-05 20:30 | 173.86 | 162.67
2019-02-05 21:00 | 173.98 | 163.86
2019-02-05 21:30 | 139.95 | 128.39
2019-02-05 22:00 | 114.1 | 104.95
2019-02-05 22:30 | 99.92 | 98.33
2019-02-05 23:00 | 95 | 93.53
2019-02-05 23:30 | 57.83 | 55.79
2019-02-06 | 54.45 | 53.11
2019-02-06 00:30 | 51.73 | 50.87
2019-02-06 01:00 | 49.08 | 48.32
2019-02-06 01:30 | 51.14 | 50.35
2019-02-06 02:00 | 52.42 | 51.7
2019-02-06 02:30 | 45.54 | 44.9
2019-02-06 03:00 | 32.51 | 31.6
2019-02-06 03:30 | 33.38 | 32.56
2019-02-06 04:00 | 38.29 | 37.4
2019-02-06 04:30 | 51.86 | 51.14
2019-02-06 05:00 | 51.84 | 50.97
2019-02-06 05:30 | 50.75 | 49.45
2019-02-06 06:00 | 62.35 | 60.83
2019-02-06 06:30 | 110.78 | 108.74
2019-02-06 07:00 | 149.72 | 145.91
2019-02-06 07:30 | 172 | 167.17
2019-02-06 08:00 | 165.68 | 159.53
2019-02-06 08:30 | 136.26 | 126.8
2019-02-06 09:00 | 127.18 | 115.5
2019-02-06 09:30 | 140.12 | 118.06
2019-02-06 10:00 | 103.39 | 78.12
2019-02-06 10:30 | 94.83 | 77.83
2019-02-06 11:00 | 102.46 | 87.16
2019-02-06 11:30 | 72.57 | 47.14
2019-02-06 12:00 | 70.24 | 41.44
2019-02-06 12:30 | 63.85 | 25.65
2019-02-06 13:00 | 67.03 | 33.73
2019-02-06 13:30 | 64.08 | 24.73
2019-02-06 14:00 | 64.79 | 22.5
2019-02-06 14:30 | 83.8 | 58.81
2019-02-06 15:00 | 83.71 | 57.74
2019-02-06 15:30 | 94.22 | 73.3
2019-02-06 16:00 | 67.38 | 24.16
2019-02-06 16:30 | 69.41 | 28.15
2019-02-06 17:00 | 131.07 | 119.2
2019-02-06 17:30 | 154.47 | 146.81
2019-02-06 18:00 | 151.7 | 146.07
2019-02-06 18:30 | 143.61 | 142.24
2019-02-06 19:00 | 160.35 | 158.78
2019-02-06 19:30 | 159.18 | 157.47
2019-02-06 20:00 | 148.31 | 146.99
2019-02-06 20:30 | 138.02 | 135.97
2019-02-06 21:00 | 126.65 | 123.12
2019-02-06 21:30 | 119.5 | 116.75
2019-02-06 22:00 | 96.97 | 94.59
2019-02-06 22:30 | 89.15 | 89.04
2019-02-06 23:00 | 95.3 | 94.45
2019-02-06 23:30 | 78.9 | 77.31
2019-02-07 | 62.47 | 60.88
2019-02-07 00:30 | 55.46 | 54.33
2019-02-07 01:00 | 46.18 | 44.32
2019-02-07 01:30 | 38.18 | 35.53
2019-02-07 02:00 | 52.65 | 50.43
2019-02-07 02:30 | 43.7 | 41.05
2019-02-07 03:00 | 29.55 | 25.59
2019-02-07 03:30 | 30.74 | 27
2019-02-07 04:00 | 39.02 | 36.19
2019-02-07 04:30 | 24.97 | 20.37
2019-02-07 05:00 | 35.28 | 32.69
2019-02-07 05:30 | 38.89 | 36.89
2019-02-07 06:00 | 44.1 | 43.05
2019-02-07 06:30 | 81.94 | 81.86
2019-02-07 07:00 | 80.59 | 79.77
2019-02-07 07:30 | 112.86 | 94.59
2019-02-07 08:00 | 109.14 | 87.52
2019-02-07 08:30 | 104.44 | 77.09
2019-02-07 09:00 | 91.19 | 35.8
2019-02-07 09:30 | 101.78 | 32.8
2019-02-07 10:00 | 93.42 | 21.67
2019-02-07 10:30 | 94.16 | 9.37
2019-02-07 11:00 | 96.92 | 9.16
2019-02-07 11:30 | 53.24 | 12.55
2019-02-07 12:00 | 83.78 | 72.09
2019-02-07 12:30 | 73.85 | 61.17
2019-02-07 13:00 | 75.06 | 61.36
2019-02-07 13:30 | 46.53 | 7.75
2019-02-07 14:00 | 80.05 | 66.28
2019-02-07 14:30 | 103.79 | 93.52
2019-02-07 15:00 | 82.51 | 69.38
2019-02-07 15:30 | 45.46 | 11.26
2019-02-07 16:00 | 45.8 | 17.78
2019-02-07 16:30 | 76.23 | 67.34
2019-02-07 17:00 | 88.66 | 82.77
2019-02-07 17:30 | 119.73 | 116.93
2019-02-07 18:00 | 130.28 | 128.4
2019-02-07 18:30 | 154.55 | 152.94
2019-02-07 19:00 | 163.11 | 158.19
2019-02-07 19:30 | 152.99 | 147.7
2019-02-07 20:00 | 133.76 | 127.33
2019-02-07 20:30 | 141.88 | 136.81
2019-02-07 21:00 | 142.19 | 138.36
2019-02-07 21:30 | 135.75 | 132.73
2019-02-07 22:00 | 106.61 | 106.42
2019-02-07 22:30 | 109.22 | 108.69
2019-02-07 23:00 | 103.44 | 102.66
2019-02-07 23:30 | 75.44 | 75.09
2019-02-08 | 53.34 | 52.6
2019-02-08 00:30 | 47.16 | 45.64
2019-02-08 01:00 | 41.2 | 39.13
2019-02-08 01:30 | 31.95 | 28.27
2019-02-08 02:00 | 22.14 | 16.55
2019-02-08 02:30 | 19.72 | 12.79
2019-02-08 03:00 | 18.88 | 11.12
2019-02-08 03:30 | 17.37 | 8.99
2019-02-08 04:00 | 21.32 | 14.77
2019-02-08 04:30 | 26.56 | 22.24
2019-02-08 05:00 | 38.61 | 35.87
2019-02-08 05:30 | 52.58 | 51.17
2019-02-08 06:00 | 62.66 | 61.73
2019-02-08 06:30 | 84.23 | 84.12
2019-02-08 07:00 | 103.33 | 103.33
2019-02-08 07:30 | 124.71 | 124.7
2019-02-08 08:00 | 126.6 | 126.59
2019-02-08 08:30 | 127.92 | 127.68
2019-02-08 09:00 | 122.04 | 118.63
2019-02-08 09:30 | 138.64 | 124.29
2019-02-08 10:00 | 126.26 | 110.76
2019-02-08 10:30 | 103.37 | 81.62
2019-02-08 11:00 | 114.28 | 94.76
2019-02-08 11:30 | 117.93 | 98.04
2019-02-08 12:00 | 111.54 | 90.59
2019-02-08 12:30 | 116.07 | 95.96
2019-02-08 13:00 | 105.23 | 82.4
2019-02-08 13:30 | 99.18 | 73.12
2019-02-08 14:00 | 107.61 | 83.82
2019-02-08 14:30 | 139.69 | 121.68
2019-02-08 15:00 | 152.15 | 135.75
2019-02-08 15:30 | 148.6 | 132.58
2019-02-08 16:00 | 151.35 | 135.17
2019-02-08 16:30 | 146.87 | 130.67
2019-02-08 17:00 | 188.64 | 176.27
2019-02-08 17:30 | 210.41 | 201.11
2019-02-08 18:00 | 234.03 | 227.58
2019-02-08 18:30 | 243.79 | 241.17
2019-02-08 19:00 | 248.71 | 246.67
2019-02-08 19:30 | 254.17 | 251.87
2019-02-08 20:00 | 244.56 | 242.43
2019-02-08 20:30 | 249.59 | 247.94
2019-02-08 21:00 | 213.93 | 212.6
2019-02-08 21:30 | 177.21 | 176.14
2019-02-08 22:00 | 156.89 | 156.86
2019-02-08 22:30 | 143.01 | 142.97
2019-02-08 23:00 | 131.66 | 131.58
2019-02-08 23:30 | 104.65 | 104.4
2019-02-09 | 92.72 | 92.44
2019-02-09 00:30 | 101.58 | 101.17
2019-02-09 01:00 | 84.29 | 82.34
2019-02-09 01:30 | 104.24 | 102.58
2019-02-09 02:00 | 100.94 | 98.89
2019-02-09 02:30 | 102.93 | 101.07
2019-02-09 03:00 | 108.64 | 106.99
2019-02-09 03:30 | 108.07 | 106.74
2019-02-09 04:00 | 100.06 | 98.74
2019-02-09 04:30 | 110.87 | 109.56
2019-02-09 05:00 | 108.47 | 107
2019-02-09 05:30 | 103.49 | 102.12
2019-02-09 06:00 | 90.69 | 89.32
2019-02-09 06:30 | 118.96 | 117.77
2019-02-09 07:00 | 134.67 | 133.44
2019-02-09 07:30 | 136.7 | 135.48
2019-02-09 08:00 | 131.92 | 131.84
2019-02-09 08:30 | 142.62 | 142.3
2019-02-09 09:00 | 162.88 | 160.97
2019-02-09 09:30 | 198.5 | 186.15
2019-02-09 10:00 | 195.48 | 182.07
2019-02-09 10:30 | 192.89 | 179.22
2019-02-09 11:00 | 197.4 | 183.64
2019-02-09 11:30 | 191.09 | 176.23
2019-02-09 12:00 | 194.33 | 179.34
2019-02-09 12:30 | 198.72 | 183.94
2019-02-09 13:00 | 221.24 | 207.67
2019-02-09 13:30 | 224.38 | 210.76
2019-02-09 14:00 | 232.37 | 218.6
2019-02-09 14:30 | 225.94 | 220.61
2019-02-09 15:00 | 237.27 | 232.72
2019-02-09 15:30 | 240.08 | 235.84
2019-02-09 16:00 | 241.62 | 237.28
2019-02-09 16:30 | 252.44 | 248.21
2019-02-09 17:00 | 251.74 | 247.44
2019-02-09 17:30 | 246.75 | 242.95
2019-02-09 18:00 | 218.25 | 214.42
2019-02-09 18:30 | 157.91 | 153.68
2019-02-09 19:00 | 157.25 | 152.93
2019-02-09 19:30 | 158.3 | 153.72
2019-02-09 20:00 | 159.75 | 155.81
2019-02-09 20:30 | 151.39 | 151.05
2019-02-09 21:00 | 142.86 | 142.72
2019-02-09 21:30 | 136.49 | 136.22
2019-02-09 22:00 | 133.7 | 133.67
2019-02-09 22:30 | 129.02 | 129
2019-02-09 23:00 | 126.51 | 126.44
2019-02-09 23:30 | 186.43 | 186.19
2019-02-10 | 177.4 | 177.32
2019-02-10 00:30 | 164.18 | 163.95
2019-02-10 01:00 | 154.8 | 154.53
2019-02-10 01:30 | 150.46 | 150.25
2019-02-10 02:00 | 148.09 | 147.96
2019-02-10 02:30 | 135.75 | 135.65
2019-02-10 03:00 | 129.05 | 128.97
2019-02-10 03:30 | 135.89 | 135.8
2019-02-10 04:00 | 132.52 | 132.45
2019-02-10 04:30 | 129.64 | 129.58
2019-02-10 05:00 | 137.16 | 137.1
2019-02-10 05:30 | 137.25 | 137.19
2019-02-10 06:00 | 126.22 | 126.06
2019-02-10 06:30 | 118.82 | 117.88
2019-02-10 07:00 | 105.78 | 105.19
2019-02-10 07:30 | 93.12 | 92.98
2019-02-10 08:00 | 97.82 | 97.81
2019-02-10 08:30 | 112.04 | 109.18
2019-02-10 09:00 | 161.84 | 157.85
2019-02-10 09:30 | 215.95 | 207.87
2019-02-10 10:00 | 235.44 | 227.86
2019-02-10 10:30 | 254.79 | 247.83
2019-02-10 11:00 | 256.04 | 249.01
2019-02-10 11:30 | 259.8 | 252.63
2019-02-10 12:00 | 254.83 | 247.21
2019-02-10 12:30 | 260.83 | 253.36
2019-02-10 13:00 | 261.8 | 253.99
2019-02-10 13:30 | 259.38 | 251.01
2019-02-10 14:00 | 268.06 | 259.47
2019-02-10 14:30 | 259.38 | 249.23
2019-02-10 15:00 | 269.21 | 258.94
2019-02-10 15:30 | 282.49 | 267.32
2019-02-10 16:00 | 300.93 | 288.8
2019-02-10 16:30 | 290.95 | 283.2
2019-02-10 17:00 | 249.95 | 240.59
2019-02-10 17:30 | 247.72 | 238.8
2019-02-10 18:00 | 249.62 | 241.27
2019-02-10 18:30 | 248.08 | 243.42
2019-02-10 19:00 | 254.09 | 250.23
2019-02-10 19:30 | 251.45 | 247.83
2019-02-10 20:00 | 246.78 | 243.51
2019-02-10 20:30 | 235.87 | 232.95
2019-02-10 21:00 | 226.2 | 224.03
2019-02-10 21:30 | 216.28 | 215.49
2019-02-10 22:00 | 187.44 | 187.34
2019-02-10 22:30 | 191.07 | 190.91
2019-02-10 23:00 | 188.9 | 188.28
2019-02-10 23:30 | 165.09 | 163.8
2019-02-11 | 133.03 | 131.18
2019-02-11 00:30 | 111.78 | 109.37
2019-02-11 01:00 | 88.06 | 84.84
2019-02-11 01:30 | 71.01 | 67.56
2019-02-11 02:00 | 54.43 | 50.32
2019-02-11 02:30 | 52.38 | 48.45
2019-02-11 03:00 | 52.07 | 48.71
2019-02-11 03:30 | 41.9 | 38.27
2019-02-11 04:00 | 50.21 | 47.58
2019-02-11 04:30 | 59.36 | 57.29
2019-02-11 05:00 | 85.67 | 83.99
2019-02-11 05:30 | 113.92 | 112.8
2019-02-11 06:00 | 105.71 | 104.63
2019-02-11 06:30 | 151.29 | 150.94
2019-02-11 07:00 | 188.45 | 188.31
2019-02-11 07:30 | 184.52 | 184.51
2019-02-11 08:00 | 186.15 | 186.15
2019-02-11 08:30 | 179.84 | 179.82
2019-02-11 09:00 | 200.61 | 200
2019-02-11 09:30 | 224.76 | 220.36
2019-02-11 10:00 | 223.52 | 218.71
2019-02-11 10:30 | 218.93 | 213.9
2019-02-11 11:00 | 218.9 | 213.86
2019-02-11 11:30 | 217.17 | 212.02
2019-02-11 12:00 | 217.76 | 212.95
2019-02-11 12:30 | 216.56 | 211.93
2019-02-11 13:00 | 221.29 | 216.5
2019-02-11 13:30 | 227.54 | 224.16
2019-02-11 14:00 | 232.81 | 229.37
2019-02-11 14:30 | 235.11 | 231.49
2019-02-11 15:00 | 240.23 | 236.61
2019-02-11 15:30 | 243.64 | 240.03
2019-02-11 16:00 | 256.78 | 253.36
2019-02-11 16:30 | 271.15 | 267.83
2019-02-11 17:00 | 277.08 | 273.98
2019-02-11 17:30 | 278.42 | 275.82
2019-02-11 18:00 | 276.76 | 274.64
2019-02-11 18:30 | 251.19 | 249.67
2019-02-11 19:00 | 264.84 | 262.96
2019-02-11 19:30 | 269.28 | 267.69
2019-02-11 20:00 | 262.25 | 261.05
2019-02-11 20:30 | 236.74 | 236.37
2019-02-11 21:00 | 204.47 | 203.75
2019-02-11 21:30 | 190 | 189.4
2019-02-11 22:00 | 192.39 | 192.09
2019-02-11 22:30 | 191.97 | 191.68
2019-02-11 23:00 | 180.54 | 180.3
2019-02-11 23:30 | 169.23 | 168.93
2019-02-12 | 164.86 | 163.52
2019-02-12 00:30 | 151.61 | 150.31
2019-02-12 01:00 | 146.96 | 145.16
2019-02-12 01:30 | 142.5 | 140.61
2019-02-12 02:00 | 123.2 | 122.17
2019-02-12 02:30 | 139.43 | 137.42
2019-02-12 03:00 | 137.26 | 135.25
2019-02-12 03:30 | 134.54 | 133.09
2019-02-12 04:00 | 130.61 | 129.11
2019-02-12 04:30 | 123.31 | 121.61
2019-02-12 05:00 | 133.49 | 131.85
2019-02-12 05:30 | 134.78 | 133.43
2019-02-12 06:00 | 151.33 | 150.28
2019-02-12 06:30 | 160.61 | 160.12
2019-02-12 07:00 | 186.31 | 186.17
2019-02-12 07:30 | 207.04 | 206.94
2019-02-12 08:00 | 211.39 | 210.92
2019-02-12 08:30 | 213.21 | 212.73
2019-02-12 09:00 | 228.68 | 224.5
2019-02-12 09:30 | 283.79 | 273.05
2019-02-12 10:00 | 302 | 291.31
2019-02-12 10:30 | 317.92 | 309.66
2019-02-12 11:00 | 322.92 | 315.13
2019-02-12 11:30 | 328.54 | 319.95
2019-02-12 12:00 | 331.97 | 321.91
2019-02-12 12:30 | 344.82 | 333.92
2019-02-12 13:00 | 353.23 | 342.16
2019-02-12 13:30 | 354.28 | 344.32
2019-02-12 14:00 | 351.79 | 337.97
2019-02-12 14:30 | 262.2 | 242.18
2019-02-12 15:00 | 205.02 | 193.14
2019-02-12 15:30 | 186.3 | 176.03
2019-02-12 16:00 | 188.53 | 177.05
2019-02-12 16:30 | 239.14 | 229.87
2019-02-12 17:00 | 284.79 | 277.27
2019-02-12 17:30 | 299.95 | 293.88
2019-02-12 18:00 | 274.49 | 272.08
2019-02-12 18:30 | 316.58 | 313.77
2019-02-12 19:00 | 331.77 | 328.71
2019-02-12 19:30 | 315.33 | 312.34
2019-02-12 20:00 | 319.36 | 316.81
2019-02-12 20:30 | 309.14 | 306.61
2019-02-12 21:00 | 293.09 | 291.21
2019-02-12 21:30 | 276.83 | 275.22
2019-02-12 22:00 | 258.12 | 257.98
2019-02-12 22:30 | 230.93 | 230.54
2019-02-12 23:00 | 219.49 | 219.03
2019-02-12 23:30 | 208.24 | 207.82
2019-02-13 | 195.85 | 195.45
2019-02-13 00:30 | 181.08 | 181.04
2019-02-13 01:00 | 172.3 | 172.08
2019-02-13 01:30 | 158.7 | 158.33
2019-02-13 02:00 | 160.15 | 159.76
2019-02-13 02:30 | 163.27 | 162.94
2019-02-13 03:00 | 160.08 | 159.8
2019-02-13 03:30 | 157.5 | 157.21
2019-02-13 04:00 | 153.81 | 153.52
2019-02-13 04:30 | 152.61 | 152.38
2019-02-13 05:00 | 155.34 | 155.11
2019-02-13 05:30 | 161.67 | 161.49
2019-02-13 06:00 | 141.39 | 141.1
2019-02-13 06:30 | 153.43 | 153.35
2019-02-13 07:00 | 189.43 | 189.41
2019-02-13 07:30 | 213.81 | 213.8
2019-02-13 08:00 | 193.6 | 193.51
2019-02-13 08:30 | 175.48 | 170.35
2019-02-13 09:00 | 179.78 | 173.25
2019-02-13 09:30 | 224.57 | 213.67
2019-02-13 10:00 | 241.98 | 230.91
2019-02-13 10:30 | 245.33 | 233.32
2019-02-13 11:00 | 252.58 | 238.15
2019-02-13 11:30 | 257.07 | 240.99
2019-02-13 12:00 | 265.98 | 248.99
2019-02-13 12:30 | 270.11 | 253.02
2019-02-13 13:00 | 276.73 | 259.18
2019-02-13 13:30 | 285.57 | 262.25
2019-02-13 14:00 | 290.99 | 268.36
2019-02-13 14:30 | 290.66 | 269.3
2019-02-13 15:00 | 296.73 | 275.88
2019-02-13 15:30 | 305.65 | 285.19
2019-02-13 16:00 | 346.67 | 329.06
2019-02-13 16:30 | 372.58 | 356.3
2019-02-13 17:00 | 381.01 | 364.98
2019-02-13 17:30 | 380.41 | 365.54
2019-02-13 18:00 | 375.27 | 363.37
2019-02-13 18:30 | 363.45 | 356.04
2019-02-13 19:00 | 357.99 | 350.72
2019-02-13 19:30 | 351.42 | 344.27
2019-02-13 20:00 | 341.12 | 332.94
2019-02-13 20:30 | 333.86 | 329.61
2019-02-13 21:00 | 318.65 | 314.53
2019-02-13 21:30 | 295.49 | 294.78
2019-02-13 22:00 | 267.31 | 267.07
2019-02-13 22:30 | 245.95 | 245.75
2019-02-13 23:00 | 241.55 | 238.49
2019-02-13 23:30 | 221.52 | 218.16
2019-02-14 | 199.05 | 199.05
2019-02-14 00:30 | 185.51 | 185.47
2019-02-14 01:00 | 176.37 | 176.32
2019-02-14 01:30 | 168.1 | 168
2019-02-14 02:00 | 165.51 | 165.33
2019-02-14 02:30 | 161.03 | 160.89
2019-02-14 03:00 | 159.52 | 159.33
2019-02-14 03:30 | 158.51 | 158.28
2019-02-14 04:00 | 158.99 | 158.77
2019-02-14 04:30 | 159.43 | 159.24
2019-02-14 05:00 | 161.99 | 161.88
2019-02-14 05:30 | 169.65 | 169.61
2019-02-14 06:00 | 168.82 | 168.77
2019-02-14 06:30 | 117.07 | 117.07
2019-02-14 07:00 | 122.91 | 118.19
2019-02-14 07:30 | 223.82 | 213.29
2019-02-14 08:00 | 214.05 | 201.85
2019-02-14 08:30 | 204.26 | 190.83
2019-02-14 09:00 | 205.93 | 193.02
2019-02-14 09:30 | 203.96 | 190.93
2019-02-14 10:00 | 216.55 | 204.08
2019-02-14 10:30 | 209.14 | 196.21
2019-02-14 11:00 | 202.93 | 189.94
2019-02-14 11:30 | 209.65 | 197.12
2019-02-14 12:00 | 221.59 | 209.42
2019-02-14 12:30 | 208.97 | 197.32
2019-02-14 13:00 | 209.65 | 197.76
2019-02-14 13:30 | 217.12 | 205.81
2019-02-14 14:00 | 204.18 | 192.62
2019-02-14 14:30 | 214.35 | 203.05
2019-02-14 15:00 | 209.5 | 198.39
2019-02-14 15:30 | 213.56 | 202.71
2019-02-14 16:00 | 218.15 | 207.68
2019-02-14 16:30 | 214.45 | 204.66
2019-02-14 17:00 | 218.68 | 209.86
2019-02-14 17:30 | 216.29 | 208.01
2019-02-14 18:00 | 216.34 | 208.99
2019-02-14 18:30 | 212.42 | 208.32
2019-02-14 19:00 | 215.89 | 211.93
2019-02-14 19:30 | 214.36 | 210.62
2019-02-14 20:00 | 208.79 | 205.51
2019-02-14 20:30 | 195.87 | 192.87
2019-02-14 21:00 | 183.25 | 183.25
2019-02-14 21:30 | 176.63 | 176.45
2019-02-14 22:00 | 167.04 | 166.6
2019-02-14 22:30 | 158.9 | 158.47
2019-02-14 23:00 | 151.49 | 150.99
2019-02-14 23:30 | 140.95 | 140.6
2019-02-15 | 132.51 | 132.07
2019-02-15 00:30 | 122.88 | 122.24
2019-02-15 01:00 | 114.85 | 114.07
2019-02-15 01:30 | 101.65 | 100.62
2019-02-15 02:00 | 100.11 | 99.01
2019-02-15 02:30 | 99.09 | 97.79
2019-02-15 03:00 | 100.63 | 97.37
2019-02-15 03:30 | 90.45 | 87.52
2019-02-15 04:00 | 91.56 | 90.39
2019-02-15 04:30 | 88.23 | 87.12
2019-02-15 05:00 | 103.86 | 103.01
2019-02-15 05:30 | 114.5 | 114
2019-02-15 06:00 | 130.61 | 130.22
2019-02-15 06:30 | 141.72 | 141.72
2019-02-15 07:00 | 149.84 | 149.06
2019-02-15 07:30 | 165.14 | 162.34
2019-02-15 08:00 | 173.46 | 165.55
2019-02-15 08:30 | 159.39 | 147.18
2019-02-15 09:00 | 145.52 | 130.89
2019-02-15 09:30 | 133.95 | 117.27
2019-02-15 10:00 | 128.01 | 109.45
2019-02-15 10:30 | 136.42 | 117.99
2019-02-15 11:00 | 136.48 | 118.64
2019-02-15 11:30 | 132.75 | 119.98
2019-02-15 12:00 | 123.24 | 109.39
2019-02-15 12:30 | 111.6 | 96.17
2019-02-15 13:00 | 137.27 | 130.51
2019-02-15 13:30 | 129.13 | 124.01
2019-02-15 14:00 | 130.66 | 125.29
2019-02-15 14:30 | 142.47 | 137.42
2019-02-15 15:00 | 152.98 | 148.45
2019-02-15 15:30 | 157.86 | 153.57
2019-02-15 16:00 | 176.14 | 166.95
2019-02-15 16:30 | 176.57 | 167.78
2019-02-15 17:00 | 205 | 197.87
2019-02-15 17:30 | 228.13 | 223.46
2019-02-15 18:00 | 219.72 | 215.86
2019-02-15 18:30 | 208.41 | 206.58
2019-02-15 19:00 | 214.34 | 213.64
2019-02-15 19:30 | 207.16 | 206.5
2019-02-15 20:00 | 220.41 | 219.84
2019-02-15 20:30 | 213.3 | 213.14
2019-02-15 21:00 | 208.99 | 208.7
2019-02-15 21:30 | 201.07 | 200.74
2019-02-15 22:00 | 180.61 | 180.43
2019-02-15 22:30 | 179.24 | 178.99
2019-02-15 23:00 | 184.67 | 184.34
2019-02-15 23:30 | 169.05 | 168.56
2019-02-16 | 133.69 | 132.94
2019-02-16 00:30 | 117.3 | 116.16
2019-02-16 01:00 | 107.17 | 105.7
2019-02-16 01:30 | 103.33 | 101.51
2019-02-16 02:00 | 93.25 | 91.05
2019-02-16 02:30 | 90.15 | 87.73
2019-02-16 03:00 | 76.97 | 73.99
2019-02-16 03:30 | 87.65 | 85.08
2019-02-16 04:00 | 94.48 | 91.94
2019-02-16 04:30 | 85.9 | 83.28
2019-02-16 05:00 | 98.35 | 96.04
2019-02-16 05:30 | 109.53 | 107.7
2019-02-16 06:00 | 100.46 | 98.42
2019-02-16 06:30 | 98.15 | 96.5
2019-02-16 07:00 | 97.61 | 96.4
2019-02-16 07:30 | 103.01 | 102.38
2019-02-16 08:00 | 94.66 | 94.38
2019-02-16 08:30 | 90.82 | 90.71
2019-02-16 09:00 | 94.2 | 91.69
2019-02-16 09:30 | 92.18 | 88.77
2019-02-16 10:00 | 87.3 | 81.61
2019-02-16 10:30 | 77.38 | 77.13
2019-02-16 11:00 | 47.96 | 47.72
2019-02-16 11:30 | 63.37 | 63.19
2019-02-16 12:00 | 84.87 | 84.78
2019-02-16 12:30 | 87.95 | 87.81
2019-02-16 13:00 | 89.28 | 89.07
2019-02-16 13:30 | 100.8 | 100.64
2019-02-16 14:00 | 108.42 | 108.27
2019-02-16 14:30 | 95.75 | 95.51
2019-02-16 15:00 | 80.78 | 80.46
2019-02-16 15:30 | 87.11 | 86.67
2019-02-16 16:00 | 88.52 | 88.05
2019-02-16 16:30 | 90.93 | 90.48
2019-02-16 17:00 | 110.88 | 110.48
2019-02-16 17:30 | 114.72 | 114.25
2019-02-16 18:00 | 140.42 | 140.06
2019-02-16 18:30 | 151.78 | 151.43
2019-02-16 19:00 | 168.12 | 167.76
2019-02-16 19:30 | 175.77 | 175.42
2019-02-16 20:00 | 175.99 | 175.58
2019-02-16 20:30 | 159.88 | 159.34
2019-02-16 21:00 | 150.36 | 149.94
2019-02-16 21:30 | 167.56 | 167.54
2019-02-16 22:00 | 176.3 | 176.23
2019-02-16 22:30 | 166.64 | 166.5
2019-02-16 23:00 | 174.03 | 173.79
2019-02-16 23:30 | 160.13 | 159.68
2019-02-17 | 124.82 | 123.71
2019-02-17 00:30 | 111.22 | 109.81
2019-02-17 01:00 | 81.78 | 79.08
2019-02-17 01:30 | 63.96 | 59.64
2019-02-17 02:00 | 49.31 | 44.2
2019-02-17 02:30 | 46.34 | 41.48
2019-02-17 03:00 | 35.53 | 29.65
2019-02-17 03:30 | 41.89 | 37.16
2019-02-17 04:00 | 52.15 | 48.45
2019-02-17 04:30 | 83.62 | 81.25
2019-02-17 05:00 | 88.76 | 86.32
2019-02-17 05:30 | 70.64 | 67.64
2019-02-17 06:00 | 63.12 | 60.04
2019-02-17 06:30 | 62.18 | 58.9
2019-02-17 07:00 | 57.05 | 52.86
2019-02-17 07:30 | 64.33 | 59.5
2019-02-17 08:00 | 54.18 | 49.51
2019-02-17 08:30 | 55.02 | 51.69
2019-02-17 09:00 | 52.04 | 50.41
2019-02-17 09:30 | 45.38 | 45.08
2019-02-17 10:00 | 39.4 | 38.65
2019-02-17 10:30 | 37.5 | 35.76
2019-02-17 11:00 | 45.08 | 32.37
2019-02-17 11:30 | 37.06 | 19.14
2019-02-17 12:00 | 37.07 | 16.81
2019-02-17 12:30 | 40.64 | 23.35
2019-02-17 13:00 | 42.47 | 26.01
2019-02-17 13:30 | 54.97 | 43.58
2019-02-17 14:00 | 53.05 | 40.61
2019-02-17 14:30 | 64.09 | 54.23
2019-02-17 15:00 | 62.8 | 52.6
2019-02-17 15:30 | 61.91 | 50.81
2019-02-17 16:00 | 67 | 57.26
2019-02-17 16:30 | 75.25 | 53.58
2019-02-17 17:00 | 95.21 | 67.46
2019-02-17 17:30 | 117.51 | 97.42
2019-02-17 18:00 | 147.78 | 133
2019-02-17 18:30 | 163.32 | 151.01
2019-02-17 19:00 | 189.15 | 178.49
2019-02-17 19:30 | 189.08 | 178.6
2019-02-17 20:00 | 178.17 | 168.05
2019-02-17 20:30 | 187.96 | 179.44
2019-02-17 21:00 | 195.29 | 191.67
2019-02-17 21:30 | 186.72 | 185.68
2019-02-17 22:00 | 172.41 | 172.36
2019-02-17 22:30 | 181.47 | 181.4
2019-02-17 23:00 | 176.96 | 176.84
2019-02-17 23:30 | 162.31 | 162.02
2019-02-18 | 142.83 | 142.28
2019-02-18 00:30 | 118.47 | 117.5
2019-02-18 01:00 | 91.51 | 90.1
2019-02-18 01:30 | 75.82 | 73.96
2019-02-18 02:00 | 67.88 | 65.62
2019-02-18 02:30 | 53.36 | 50.43
2019-02-18 03:00 | 63.17 | 60.32
2019-02-18 03:30 | 67.07 | 64.29
2019-02-18 04:00 | 67.02 | 64.69
2019-02-18 04:30 | 66.59 | 64.19
2019-02-18 05:00 | 83.87 | 81.81
2019-02-18 05:30 | 86.38 | 83.98
2019-02-18 06:00 | 93.77 | 91.5
2019-02-18 06:30 | 136.05 | 134.89
2019-02-18 07:00 | 149.8 | 148.97
2019-02-18 07:30 | 128.7 | 128.68
2019-02-18 08:00 | 142.04 | 141.61
2019-02-18 08:30 | 166.41 | 158.76
2019-02-18 09:00 | 181.08 | 161.66
2019-02-18 09:30 | 173.99 | 163.75
2019-02-18 10:00 | 191.34 | 182.65
2019-02-18 10:30 | 190.78 | 181.71
2019-02-18 11:00 | 193.52 | 184.07
2019-02-18 11:30 | 189.21 | 179.75
2019-02-18 12:00 | 188.35 | 179.11
2019-02-18 12:30 | 192.19 | 183.02
2019-02-18 13:00 | 192.38 | 184.1
2019-02-18 13:30 | 130.06 | 118.51
2019-02-18 14:00 | 119.62 | 106.74
2019-02-18 14:30 | 123.67 | 112.75
2019-02-18 15:00 | 122.74 | 116.98
2019-02-18 15:30 | 108.46 | 101.56
2019-02-18 16:00 | 126.59 | 120.45
2019-02-18 16:30 | 143.36 | 137.94
2019-02-18 17:00 | 178.12 | 173.88
2019-02-18 17:30 | 178.86 | 175.56
2019-02-18 18:00 | 195.55 | 193.23
2019-02-18 18:30 | 208.24 | 207.03
2019-02-18 19:00 | 228.91 | 227.61
2019-02-18 19:30 | 239.88 | 238.64
2019-02-18 20:00 | 245.58 | 242.79
2019-02-18 20:30 | 235.83 | 235.17
2019-02-18 21:00 | 224.64 | 224.64
2019-02-18 21:30 | 212.84 | 212.76
2019-02-18 22:00 | 198.8 | 198.71
2019-02-18 22:30 | 186.18 | 186.14
2019-02-18 23:00 | 175.67 | 175.6
2019-02-18 23:30 | 166.64 | 166.41
2019-02-19 | 153.61 | 153.02
2019-02-19 00:30 | 135.95 | 134.84
2019-02-19 01:00 | 126.14 | 124.59
2019-02-19 01:30 | 108.49 | 106.46
2019-02-19 02:00 | 92.63 | 90.14
2019-02-19 02:30 | 88.3 | 86.09
2019-02-19 03:00 | 93.01 | 90.92
2019-02-19 03:30 | 106.54 | 105.05
2019-02-19 04:00 | 94.65 | 93.24
2019-02-19 04:30 | 95.74 | 94.37
2019-02-19 05:00 | 103.74 | 102.45
2019-02-19 05:30 | 97.66 | 96.12
2019-02-19 06:00 | 107.75 | 106.35
2019-02-19 06:30 | 132.68 | 132.68
2019-02-19 07:00 | 144.93 | 144.62
2019-02-19 07:30 | 167.78 | 159.13
2019-02-19 08:00 | 177.89 | 164.1
2019-02-19 08:30 | 181.21 | 165.18
2019-02-19 09:00 | 184.77 | 168.71
2019-02-19 09:30 | 183.58 | 167.8
2019-02-19 10:00 | 189.08 | 173.1
2019-02-19 10:30 | 193.16 | 176.53
2019-02-19 11:00 | 191.64 | 180.57
2019-02-19 11:30 | 192.48 | 181.75
2019-02-19 12:00 | 194.08 | 183.28
2019-02-19 12:30 | 197.88 | 187.02
2019-02-19 13:00 | 204.76 | 193.35
2019-02-19 13:30 | 208.12 | 196.89
2019-02-19 14:00 | 212.53 | 201.28
2019-02-19 14:30 | 217.6 | 205.98
2019-02-19 15:00 | 218.26 | 206.3
2019-02-19 15:30 | 221.46 | 209.55
2019-02-19 16:00 | 229.23 | 216.75
2019-02-19 16:30 | 234.03 | 223.7
2019-02-19 17:00 | 277.91 | 269.18
2019-02-19 17:30 | 294.74 | 287.36
2019-02-19 18:00 | 281.93 | 275.97
2019-02-19 18:30 | 284.51 | 279.64
2019-02-19 19:00 | 289.28 | 284.06
2019-02-19 19:30 | 279.66 | 274.58
2019-02-19 20:00 | 259.68 | 255.31
2019-02-19 20:30 | 231.82 | 230.15
2019-02-19 21:00 | 211.79 | 211.69
2019-02-19 21:30 | 200.4 | 200.4
2019-02-19 22:00 | 189.66 | 189.6
2019-02-19 22:30 | 191.28 | 191.04
2019-02-19 23:00 | 169.08 | 168.68
2019-02-19 23:30 | 150.15 | 149.4
2019-02-20 | 132.27 | 131.15
2019-02-20 00:30 | 127 | 125.42
2019-02-20 01:00 | 127.54 | 125.65
2019-02-20 01:30 | 128.23 | 126.69
2019-02-20 02:00 | 127.21 | 125.89
2019-02-20 02:30 | 125.79 | 124.55
2019-02-20 03:00 | 118.63 | 117.23
2019-02-20 03:30 | 120.1 | 118.82
2019-02-20 04:00 | 126.9 | 125.7
2019-02-20 04:30 | 126.31 | 125.28
2019-02-20 05:00 | 141.59 | 140.88
2019-02-20 05:30 | 145.79 | 145.39
2019-02-20 06:00 | 128.68 | 128.24
2019-02-20 06:30 | 113.71 | 113.61
2019-02-20 07:00 | 120.61 | 120.51
2019-02-20 07:30 | 137.53 | 136.62
2019-02-20 08:00 | 155.37 | 146.86
2019-02-20 08:30 | 158.62 | 146.99
2019-02-20 09:00 | 142.44 | 126.25
2019-02-20 09:30 | 144.75 | 125.93
2019-02-20 10:00 | 149.94 | 130.83
2019-02-20 10:30 | 155.12 | 133.55
2019-02-20 11:00 | 163.6 | 134.57
2019-02-20 11:30 | 160.14 | 136.41
2019-02-20 12:00 | 160.29 | 136.72
2019-02-20 12:30 | 175.16 | 154.11
2019-02-20 13:00 | 202.94 | 184.8
2019-02-20 13:30 | 224.61 | 210.33
2019-02-20 14:00 | 258.97 | 246.27
2019-02-20 14:30 | 274.44 | 262.36
2019-02-20 15:00 | 278.18 | 265.7
2019-02-20 15:30 | 277.53 | 265.31
2019-02-20 16:00 | 295.98 | 284.14
2019-02-20 16:30 | 300.85 | 289.83
2019-02-20 17:00 | 303.23 | 293.5
2019-02-20 17:30 | 301.69 | 293.07
2019-02-20 18:00 | 295.73 | 291.54
2019-02-20 18:30 | 281.6 | 280.4
2019-02-20 19:00 | 292.18 | 290.97
2019-02-20 19:30 | 289.23 | 288.13
2019-02-20 20:00 | 281.92 | 280.86
2019-02-20 20:30 | 269.4 | 268.78
2019-02-20 21:00 | 258.3 | 257.91
2019-02-20 21:30 | 245.53 | 244.8
2019-02-20 22:00 | 225.17 | 224.4
2019-02-20 22:30 | 212.08 | 211.9
2019-02-20 23:00 | 203.6 | 203.6
2019-02-20 23:30 | 186.84 | 186.76
2019-02-21 | 173.11 | 172.68
2019-02-21 00:30 | 164.3 | 163.63
2019-02-21 01:00 | 147.71 | 146.97
2019-02-21 01:30 | 133.24 | 132.3
2019-02-21 02:00 | 121.13 | 120
2019-02-21 02:30 | 111.03 | 109.65
2019-02-21 03:00 | 107.12 | 105.54
2019-02-21 03:30 | 103.59 | 101.93
2019-02-21 04:00 | 104.53 | 102.98
2019-02-21 04:30 | 109.46 | 108.18
2019-02-21 05:00 | 118.62 | 117.57
2019-02-21 05:30 | 128.98 | 128.37
2019-02-21 06:00 | 142.62 | 142.22
2019-02-21 06:30 | 157.34 | 157.29
2019-02-21 07:00 | 173.06 | 173.04
2019-02-21 07:30 | 194.82 | 194.18
2019-02-21 08:00 | 205.69 | 203.35
2019-02-21 08:30 | 201.87 | 193.62
2019-02-21 09:00 | 209.19 | 199.61
2019-02-21 09:30 | 225.71 | 216.84
2019-02-21 10:00 | 220.52 | 211.76
2019-02-21 10:30 | 211.51 | 202.41
2019-02-21 11:00 | 213.56 | 204.99
2019-02-21 11:30 | 224.94 | 216.09
2019-02-21 12:00 | 220.43 | 211.39
2019-02-21 12:30 | 216.49 | 207.36
2019-02-21 13:00 | 223.33 | 214.3
2019-02-21 13:30 | 237.88 | 228.67
2019-02-21 14:00 | 230.45 | 221.16
2019-02-21 14:30 | 255.91 | 247.03
2019-02-21 15:00 | 232.69 | 223.35
2019-02-21 15:30 | 244.61 | 235.45
2019-02-21 16:00 | 252.85 | 243.36
2019-02-21 16:30 | 279.66 | 270.69
2019-02-21 17:00 | 302.4 | 293.98
2019-02-21 17:30 | 288.36 | 281.54
2019-02-21 18:00 | 290.99 | 285.28
2019-02-21 18:30 | 283.23 | 278.2
2019-02-21 19:00 | 289.99 | 285.11
2019-02-21 19:30 | 279.91 | 278.29
2019-02-21 20:00 | 272.95 | 271.93
2019-02-21 20:30 | 254.18 | 254.16
2019-02-21 21:00 | 247.5 | 247.47
2019-02-21 21:30 | 233.1 | 232.88
2019-02-21 22:00 | 214.28 | 213.91
2019-02-21 22:30 | 204.92 | 204.6
2019-02-21 23:00 | 198.8 | 198.27
2019-02-21 23:30 | 180.86 | 180.64
2019-02-22 | 169.6 | 169.21
2019-02-22 00:30 | 148.26 | 147.72
2019-02-22 01:00 | 134.43 | 133.63
2019-02-22 01:30 | 144.47 | 143.64
2019-02-22 02:00 | 137.8 | 136.88
2019-02-22 02:30 | 138.54 | 137.49
2019-02-22 03:00 | 139.99 | 138.83
2019-02-22 03:30 | 138.33 | 137.15
2019-02-22 04:00 | 137.4 | 136.21
2019-02-22 04:30 | 133.61 | 132.44
2019-02-22 05:00 | 137.08 | 135.9
2019-02-22 05:30 | 149.5 | 148.73
2019-02-22 06:00 | 150.54 | 149.9
2019-02-22 06:30 | 154.75 | 154.44
2019-02-22 07:00 | 152.61 | 152.53
2019-02-22 07:30 | 163.82 | 163.81
2019-02-22 08:00 | 154.2 | 153.97
2019-02-22 08:30 | 148.4 | 148.27
2019-02-22 09:00 | 158.39 | 158.38
2019-02-22 09:30 | 181.68 | 181.68
2019-02-22 10:00 | 172.8 | 172.79
2019-02-22 10:30 | 150.13 | 150.13
2019-02-22 11:00 | 140.21 | 140.21
2019-02-22 11:30 | 183.02 | 183.01
2019-02-22 12:00 | 200.96 | 200.95
2019-02-22 12:30 | 194.01 | 193.99
2019-02-22 13:00 | 196.97 | 196.95
2019-02-22 13:30 | 179.21 | 179.2
2019-02-22 14:00 | 187.34 | 187.33
2019-02-22 14:30 | 177.56 | 177.52
2019-02-22 15:00 | 183.42 | 183.3
2019-02-22 15:30 | 198.79 | 198.6
2019-02-22 16:00 | 213.23 | 212.98
2019-02-22 16:30 | 213.35 | 213.05
2019-02-22 17:00 | 218.86 | 218.43
2019-02-22 17:30 | 221.6 | 221.26
2019-02-22 18:00 | 219.44 | 219.19
2019-02-22 18:30 | 215.53 | 215.13
2019-02-22 19:00 | 220.78 | 220.44
2019-02-22 19:30 | 216.82 | 216.53
2019-02-22 20:00 | 213.67 | 212.98
2019-02-22 20:30 | 192.66 | 192.38
2019-02-22 21:00 | 169.44 | 169.12
2019-02-22 21:30 | 146.15 | 146.03
2019-02-22 22:00 | 128.47 | 128.22
2019-02-22 22:30 | 144.43 | 144.12
2019-02-22 23:00 | 162.07 | 161.62
2019-02-22 23:30 | 131.75 | 130.88
2019-02-23 | 98.2 | 96.72
2019-02-23 00:30 | 87.27 | 85.31
2019-02-23 01:00 | 79.96 | 76.09
2019-02-23 01:30 | 84.79 | 77.7
2019-02-23 02:00 | 78.1 | 70.08
2019-02-23 02:30 | 76.89 | 68.76
2019-02-23 03:00 | 71.61 | 62.76
2019-02-23 03:30 | 70.6 | 62.08
2019-02-23 04:00 | 75.28 | 67.48
2019-02-23 04:30 | 73.05 | 65.5
2019-02-23 05:00 | 80.73 | 74.02
2019-02-23 05:30 | 54.5 | 44.37
2019-02-23 06:00 | 56.18 | 46.72
2019-02-23 06:30 | 42.68 | 29.3
2019-02-23 07:00 | 35.37 | 16.83
2019-02-23 07:30 | 32.99 | 16.51
2019-02-23 08:00 | 39.73 | 29.64
2019-02-23 08:30 | 59.37 | 54.56
2019-02-23 09:00 | 53.56 | 52.57
2019-02-23 09:30 | 65.3 | 65.24
2019-02-23 10:00 | 51.23 | 51.1
2019-02-23 10:30 | 44.91 | 44.72
2019-02-23 11:00 | 52.91 | 51.08
2019-02-23 11:30 | 38.63 | 36.08
2019-02-23 12:00 | 45.7 | 43.68
2019-02-23 12:30 | 42.28 | 40.11
2019-02-23 13:00 | 55.04 | 53.42
2019-02-23 13:30 | 79.93 | 78.75
2019-02-23 14:00 | 95.97 | 94.98
2019-02-23 14:30 | 109.27 | 108.53
2019-02-23 15:00 | 134.8 | 134.26
2019-02-23 15:30 | 155.17 | 154.55
2019-02-23 16:00 | 154.39 | 153.71
2019-02-23 16:30 | 165.68 | 165.13
2019-02-23 17:00 | 153.87 | 153.25
2019-02-23 17:30 | 178.15 | 177.56
2019-02-23 18:00 | 179.07 | 178.37
2019-02-23 18:30 | 192.21 | 191.41
2019-02-23 19:00 | 205.81 | 205.26
2019-02-23 19:30 | 191.05 | 190.35
2019-02-23 20:00 | 193.66 | 192.72
2019-02-23 20:30 | 182.92 | 182.86
2019-02-23 21:00 | 162.54 | 162.4
2019-02-23 21:30 | 166.69 | 166.44
2019-02-23 22:00 | 145.94 | 145.46
2019-02-23 22:30 | 156.33 | 155.72
2019-02-23 23:00 | 158.08 | 157.32
2019-02-23 23:30 | 130.15 | 128.92
2019-02-24 | 91.98 | 89.57
2019-02-24 00:30 | 69.19 | 59.88
2019-02-24 01:00 | 58.38 | 46.08
2019-02-24 01:30 | 52.51 | 38.67
2019-02-24 02:00 | 67.33 | 57.18
2019-02-24 02:30 | 70.12 | 60.13
2019-02-24 03:00 | 63.71 | 52.86
2019-02-24 03:30 | 61.42 | 50.63
2019-02-24 04:00 | 57.83 | 46.21
2019-02-24 04:30 | 56.89 | 44.99
2019-02-24 05:00 | 65.77 | 56.05
2019-02-24 05:30 | 67.47 | 58.49
2019-02-24 06:00 | 53.77 | 42.62
2019-02-24 06:30 | 49.14 | 36.7
2019-02-24 07:00 | 48.11 | 33.22
2019-02-24 07:30 | 38.84 | 23.17
2019-02-24 08:00 | 32.19 | 16.93
2019-02-24 08:30 | 37.48 | 26.42
2019-02-24 09:00 | 68.72 | 64.8
2019-02-24 09:30 | 97.52 | 97.48
2019-02-24 10:00 | 76.61 | 76.54
2019-02-24 10:30 | 44.61 | 44.59
2019-02-24 11:00 | 36.3 | 36.29
2019-02-24 11:30 | 18.92 | 18.78
2019-02-24 12:00 | 13.28 | 13.16
2019-02-24 12:30 | 7.54 | -7.25
2019-02-24 13:00 | 3.66 | 2.66
2019-02-24 13:30 | 3.64 | -1.58
2019-02-24 14:00 | 9.28 | 8.7
2019-02-24 14:30 | 29.03 | 28.85
2019-02-24 15:00 | 60.01 | 59.99
2019-02-24 15:30 | 83.94 | 83.93
2019-02-24 16:00 | 120.35 | 120.35
2019-02-24 16:30 | 135.77 | 135.77
2019-02-24 17:00 | 161.3 | 160.68
2019-02-24 17:30 | 174.26 | 173.12
2019-02-24 18:00 | 172.38 | 171.22
2019-02-24 18:30 | 166.11 | 164.93
2019-02-24 19:00 | 179.03 | 178.19
2019-02-24 19:30 | 160.5 | 159.44
2019-02-24 20:00 | 152.34 | 150.76
2019-02-24 20:30 | 163.22 | 161.75
2019-02-24 21:00 | 154.09 | 153.76
2019-02-24 21:30 | 144.28 | 143.7
2019-02-24 22:00 | 134.11 | 133.12
2019-02-24 22:30 | 129.36 | 128.26
2019-02-24 23:00 | 131.96 | 130.64
2019-02-24 23:30 | 101.28 | 99.03
2019-02-25 | 50.3 | 44.69
2019-02-25 00:30 | 41.45 | 25.38
2019-02-25 01:00 | 35.57 | 11.57
2019-02-25 01:30 | 32.98 | 3.15
2019-02-25 02:00 | 34.08 | 5.76
2019-02-25 02:30 | 33.5 | 5.19
2019-02-25 03:00 | 34.16 | 7.81
2019-02-25 03:30 | 32.06 | 4.95
2019-02-25 04:00 | 32.51 | 11.65
2019-02-25 04:30 | 38.04 | 22.47
2019-02-25 05:00 | 45.36 | 34.13
2019-02-25 05:30 | 59.35 | 51.6
2019-02-25 06:00 | 51.26 | 42.94
2019-02-25 06:30 | 79.8 | 76.18
2019-02-25 07:00 | 80.96 | 80.54
2019-02-25 07:30 | 78.2 | 77.9
2019-02-25 08:00 | 80.97 | 80.28
2019-02-25 08:30 | 79.84 | 79.61
2019-02-25 09:00 | 76.94 | 76.82
2019-02-25 09:30 | 65.12 | 65
2019-02-25 10:00 | 55.92 | 55.88
2019-02-25 10:30 | 62.7 | 62.6
2019-02-25 11:00 | 54.7 | 54.61
2019-02-25 11:30 | 30.75 | 30.62
2019-02-25 12:00 | 35.47 | 35.3
2019-02-25 12:30 | 37 | 36.99
2019-02-25 13:00 | 59.64 | 59.52
2019-02-25 13:30 | 59.96 | 59.91
2019-02-25 14:00 | 66.81 | 66.74
2019-02-25 14:30 | 87.55 | 87.46
2019-02-25 15:00 | 95.49 | 95.33
2019-02-25 15:30 | 103.57 | 103.21
2019-02-25 16:00 | 125.48 | 125.12
2019-02-25 16:30 | 114.92 | 114.44
2019-02-25 17:00 | 122.74 | 121.96
2019-02-25 17:30 | 143.23 | 142.18
2019-02-25 18:00 | 158.69 | 157.82
2019-02-25 18:30 | 146.11 | 145.13
2019-02-25 19:00 | 162.81 | 162.23
2019-02-25 19:30 | 198.87 | 198.24
2019-02-25 20:00 | 173.45 | 172.4
2019-02-25 20:30 | 155.4 | 154.59
2019-02-25 21:00 | 143.09 | 142.84
2019-02-25 21:30 | 128.26 | 127.81
2019-02-25 22:00 | 109.61 | 108.68
2019-02-25 22:30 | 105.36 | 104.15
2019-02-25 23:00 | 113.14 | 111.72
2019-02-25 23:30 | 81.24 | 78.55
2019-02-26 | 47.78 | 41.29
2019-02-26 00:30 | 39.04 | 23.07
2019-02-26 01:00 | 33.31 | 9.13
2019-02-26 01:30 | 35.13 | 12.27
2019-02-26 02:00 | 36.51 | 15.12
2019-02-26 02:30 | 34.03 | 7.91
2019-02-26 03:00 | 33.98 | 8.98
2019-02-26 03:30 | 34.92 | 13.27
2019-02-26 04:00 | 56 | 46.14
2019-02-26 04:30 | 47.71 | 37.27
2019-02-26 05:00 | 56.99 | 48.3
2019-02-26 05:30 | 49.63 | 39.96
2019-02-26 06:00 | 47.31 | 38.59
2019-02-26 06:30 | 68.09 | 63.72
2019-02-26 07:00 | 70.2 | 66.98
2019-02-26 07:30 | 77.14 | 76.86
2019-02-26 08:00 | 76.9 | 76.88
2019-02-26 08:30 | 72.47 | 72.39
2019-02-26 09:00 | 76.22 | 75.96
2019-02-26 09:30 | 71.14 | 70.66
2019-02-26 10:00 | 59.48 | 58.29
2019-02-26 10:30 | 81.54 | 77.85
2019-02-26 11:00 | 81.73 | 75.46
2019-02-26 11:30 | 79.2 | 72.54
2019-02-26 12:00 | 72.37 | 65.04
2019-02-26 12:30 | 67.25 | 59.46
2019-02-26 13:00 | 78.23 | 71.45
2019-02-26 13:30 | 83.21 | 76.51
2019-02-26 14:00 | 114.11 | 95.62
2019-02-26 14:30 | 118.85 | 100.91
2019-02-26 15:00 | 114.4 | 96.1
2019-02-26 15:30 | 109.33 | 90.91
2019-02-26 16:00 | 96 | 74.66
2019-02-26 16:30 | 95.02 | 74.97
2019-02-26 17:00 | 122.63 | 108.98
2019-02-26 17:30 | 135.93 | 126.59
2019-02-26 18:00 | 154 | 150.86
2019-02-26 18:30 | 183.06 | 180.76
2019-02-26 19:00 | 213.19 | 210.54
2019-02-26 19:30 | 200.95 | 198.54
2019-02-26 20:00 | 187 | 185.08
2019-02-26 20:30 | 171.41 | 171.29
2019-02-26 21:00 | 160.26 | 159.99
2019-02-26 21:30 | 151.59 | 151.11
2019-02-26 22:00 | 134.1 | 133.17
2019-02-26 22:30 | 142.12 | 141.01
2019-02-26 23:00 | 135.94 | 134.28
2019-02-26 23:30 | 102.26 | 97.62
2019-02-27 | 67.99 | 60.52
2019-02-27 00:30 | 86.97 | 80.54
2019-02-27 01:00 | 88.89 | 81.82
2019-02-27 01:30 | 84.86 | 77.24
2019-02-27 02:00 | 78.5 | 69.96
2019-02-27 02:30 | 82.77 | 74.55
2019-02-27 03:00 | 83.74 | 75.97
2019-02-27 03:30 | 79.85 | 71.81
2019-02-27 04:00 | 70.67 | 62.56
2019-02-27 04:30 | 65.18 | 56.73
2019-02-27 05:00 | 80.63 | 74.29
2019-02-27 05:30 | 63.35 | 55.45
2019-02-27 06:00 | 58.51 | 50.72
2019-02-27 06:30 | 84.42 | 80.69
2019-02-27 07:00 | 105.95 | 103.95
2019-02-27 07:30 | 101.9 | 100.28
2019-02-27 08:00 | 98.76 | 98.45
2019-02-27 08:30 | 85.54 | 85.04
2019-02-27 09:00 | 61.69 | 61.32
2019-02-27 09:30 | 58.47 | 58.36
2019-02-27 10:00 | 40.39 | 40.32
2019-02-27 10:30 | 64.62 | 64.46
2019-02-27 11:00 | 61.74 | 61.73
2019-02-27 11:30 | 89.93 | 89.92
2019-02-27 12:00 | 110.37 | 110.35
2019-02-27 12:30 | 94.02 | 93.93
2019-02-27 13:00 | 82.37 | 82.2
2019-02-27 13:30 | 86.62 | 86.52
2019-02-27 14:00 | 101.91 | 101.66
2019-02-27 14:30 | 110.52 | 110.23
2019-02-27 15:00 | 104.48 | 103.92
2019-02-27 15:30 | 103.36 | 102.58
2019-02-27 16:00 | 101.52 | 100.69
2019-02-27 16:30 | 140 | 139.16
2019-02-27 17:00 | 132.9 | 131.88
2019-02-27 17:30 | 133.95 | 132.8
2019-02-27 18:00 | 148.49 | 148.26
2019-02-27 18:30 | 168.85 | 168.75
2019-02-27 19:00 | 191.67 | 191.4
2019-02-27 19:30 | 179.39 | 179.2
2019-02-27 20:00 | 191.64 | 191.62
2019-02-27 20:30 | 176 | 175.51
2019-02-27 21:00 | 152.36 | 151.43
2019-02-27 21:30 | 121.77 | 120.15
2019-02-27 22:00 | 108.74 | 105.29
2019-02-27 22:30 | 121.7 | 118.94
2019-02-27 23:00 | 127.45 | 124.82
2019-02-27 23:30 | 92.31 | 88.71
2019-02-28 | 61.05 | 56.07
2019-02-28 00:30 | 48.26 | 41.49
2019-02-28 01:00 | 42.22 | 33.69
2019-02-28 01:30 | 39.14 | 28.88
2019-02-28 02:00 | 35.74 | 23.39
2019-02-28 02:30 | 34.66 | 21.65
2019-02-28 03:00 | 34.91 | 21.23
2019-02-28 03:30 | 41.55 | 31.15
2019-02-28 04:00 | 47.05 | 38.41
2019-02-28 04:30 | 39.41 | 30.34
2019-02-28 05:00 | 45.33 | 39.05
2019-02-28 05:30 | 31.56 | 24.52
2019-02-28 06:00 | 41.5 | 36.99
2019-02-28 06:30 | 35.88 | 35.73
2019-02-28 07:00 | 62.85 | 61.67
2019-02-28 07:30 | 95.14 | 88.15
2019-02-28 08:00 | 87.88 | 79.27
2019-02-28 08:30 | 79.66 | 59.52
2019-02-28 09:00 | 105.23 | 55.56
2019-02-28 09:30 | 92.18 | 13.8
2019-02-28 10:00 | 68.97 | -23.97
2019-02-28 10:30 | 65.02 | -10.67
2019-02-28 11:00 | 70.24 | 24.54
2019-02-28 11:30 | 66.98 | 19.72
2019-02-28 12:00 | 68.11 | 19.11
2019-02-28 12:30 | 69.19 | 21.83
2019-02-28 13:00 | 66.73 | -3.22
2019-02-28 13:30 | 67.25 | -3.6
2019-02-28 14:00 | 67.47 | 11.66
2019-02-28 14:30 | 68.82 | 16.5
2019-02-28 15:00 | 83.32 | -36.98
2019-02-28 15:30 | 84.4 | 19.52
2019-02-28 16:00 | 94.2 | 49.7
2019-02-28 16:30 | 99.49 | 61.65
2019-02-28 17:00 | 121.23 | 94.7
2019-02-28 17:30 | 122.2 | 104.23
2019-02-28 18:00 | 132.62 | 120.86
2019-02-28 18:30 | 152.62 | 142.59
2019-02-28 19:00 | 183.27 | 173.84
2019-02-28 19:30 | 173.04 | 164.1
2019-02-28 20:00 | 157.12 | 148.39
2019-02-28 20:30 | 152.89 | 151.44
2019-02-28 21:00 | 141.56 | 140.73
2019-02-28 21:30 | 117.12 | 116.62
2019-02-28 22:00 | 95.25 | 95.05
2019-02-28 22:30 | 88.53 | 88.44
2019-02-28 23:00 | 85.15 | 85.12
2019-02-28 23:30 | 28.95 | 25.05
2019-03-01 | 22.27 | -14.78
2019-03-01 00:30 | 73.17 | -72.13
2019-03-01 01:00 | 77.06 | -75.88
2019-03-01 01:30 | 65.47 | -63.02
2019-03-01 02:00 | 48.43 | -43.5
2019-03-01 02:30 | 40.37 | -33.8
2019-03-01 03:00 | 38.63 | -31.03
2019-03-01 03:30 | 26.34 | -11.91
2019-03-01 04:00 | 22.67 | -6.03
2019-03-01 04:30 | 24.18 | 9.51
2019-03-01 05:00 | 20.14 | 1.85
2019-03-01 05:30 | 16.12 | -2.19
2019-03-01 06:00 | 18.09 | -12.05
2019-03-01 06:30 | 32.25 | -31.69
2019-03-01 07:00 | 16.45 | -16.13
2019-03-01 07:30 | 29.85 | 6.61
2019-03-01 08:00 | 58.98 | -15.87
2019-03-01 08:30 | 67.22 | 34.64
2019-03-01 09:00 | 63.76 | -4.14
2019-03-01 09:30 | 68.56 | 17.79
2019-03-01 10:00 | 69.63 | -17.7
2019-03-01 10:30 | 69.78 | -9.87
2019-03-01 11:00 | 97.78 | -62.26
2019-03-01 11:30 | 93.48 | -58.46
2019-03-01 12:00 | 83.72 | -42.34
2019-03-01 12:30 | 86.29 | -49.45
2019-03-01 13:00 | 92.03 | -57.54
2019-03-01 13:30 | 69.52 | 4.13
2019-03-01 14:00 | 69.08 | 3.59
2019-03-01 14:30 | 70.63 | -4.03
2019-03-01 15:00 | 69.86 | 16.61
2019-03-01 15:30 | 75.83 | 42.1
2019-03-01 16:00 | 79.12 | 50.8
2019-03-01 16:30 | 71.3 | 38.35
2019-03-01 17:00 | 72.5 | 42.3
2019-03-01 17:30 | 84.9 | 64.74
2019-03-01 18:00 | 86.2 | 68.75
2019-03-01 18:30 | 97.15 | 82.29
2019-03-01 19:00 | 98.8 | 83.21
2019-03-01 19:30 | 92.67 | 77.42
2019-03-01 20:00 | 89.25 | 74.81
2019-03-01 20:30 | 82.55 | 74.29
2019-03-01 21:00 | 62.92 | 58.78
2019-03-01 21:30 | 39.54 | 38.42
2019-03-01 22:00 | 30.81 | 28.56
2019-03-01 22:30 | 41.7 | 39.75
2019-03-01 23:00 | 56.98 | 55.11
2019-03-01 23:30 | 45.6 | 42.24
2019-03-02 | 24.15 | 14.33
2019-03-02 00:30 | 21.5 | -2.72
2019-03-02 01:00 | 26.56 | -14.01
2019-03-02 01:30 | 29.61 | -18.46
2019-03-02 02:00 | 25.05 | -8.55
2019-03-02 02:30 | 33.18 | -23.48
2019-03-02 03:00 | 40.6 | -33.52
2019-03-02 03:30 | 49.97 | -44.64
2019-03-02 04:00 | 42.45 | -35.65
2019-03-02 04:30 | 44.24 | -38.23
2019-03-02 05:00 | 40.36 | -33.55
2019-03-02 05:30 | 30.79 | -22.73
2019-03-02 06:00 | 31.47 | -24.37
2019-03-02 06:30 | 20.76 | -9.14
2019-03-02 07:00 | 21.74 | -14.59
2019-03-02 07:30 | 24.93 | -22.65
2019-03-02 08:00 | 27.13 | -26.34
2019-03-02 08:30 | 76.97 | -74.48
2019-03-02 09:00 | 34 | -12.47
2019-03-02 09:30 | 32.88 | 2.79
2019-03-02 10:00 | 37.34 | -10.33
2019-03-02 10:30 | 47.5 | -27.14
2019-03-02 11:00 | 38.24 | 16.05
2019-03-02 11:30 | 41.87 | -21.68
2019-03-02 12:00 | 63.35 | -51.25
2019-03-02 12:30 | 60.14 | -50.45
2019-03-02 13:00 | 51.43 | -44.92
2019-03-02 13:30 | 37.3 | -28.37
2019-03-02 14:00 | 43.72 | -36.04
2019-03-02 14:30 | 21.83 | 4.33
2019-03-02 15:00 | 20.93 | 9.87
2019-03-02 15:30 | 22.61 | 14.74
2019-03-02 16:00 | 47.98 | 45.45
2019-03-02 16:30 | 44.81 | 42.28
2019-03-02 17:00 | 65.27 | 63.22
2019-03-02 17:30 | 99.64 | 98.23
2019-03-02 18:00 | 133.79 | 132.98
2019-03-02 18:30 | 146.2 | 145.46
2019-03-02 19:00 | 165.17 | 164.2
2019-03-02 19:30 | 126.43 | 125.43
2019-03-02 20:00 | 141.89 | 141.26
2019-03-02 20:30 | 122.62 | 122.07
2019-03-02 21:00 | 88.79 | 88.3
2019-03-02 21:30 | 101.69 | 101.49
2019-03-02 22:00 | 56.48 | 56.26
2019-03-02 22:30 | 81.46 | 81.4
2019-03-02 23:00 | 74.84 | 74.81
2019-03-02 23:30 | 79.15 | 79.02
2019-03-03 | 54.29 | 49.61
2019-03-03 00:30 | 28.49 | 17.69
2019-03-03 01:00 | 55.63 | 49.44
2019-03-03 01:30 | 60.58 | 54.83
2019-03-03 02:00 | 58.96 | 52.63
2019-03-03 02:30 | 57.95 | 51.44
2019-03-03 03:00 | 56.94 | 50.32
2019-03-03 03:30 | 28.59 | -15.35
2019-03-03 04:00 | 29.64 | -17.32
2019-03-03 04:30 | 31.39 | -20
2019-03-03 05:00 | 27.69 | -13.63
2019-03-03 05:30 | 32.12 | -23.4
2019-03-03 06:00 | 44.04 | -38.62
2019-03-03 06:30 | 43.84 | -39.66
2019-03-03 07:00 | 61.57 | -59.84
2019-03-03 07:30 | 50.04 | -48.79
2019-03-03 08:00 | 11.76 | -0.06
2019-03-03 08:30 | 33.64 | -33.3
2019-03-03 09:00 | 15.36 | -15.21
2019-03-03 09:30 | 9.76 | 9.62
2019-03-03 10:00 | 2.58 | 1.41
2019-03-03 10:30 | 2.81 | -1.16
2019-03-03 11:00 | 6.7 | -5.53
2019-03-03 11:30 | 10.11 | -9.42
2019-03-03 12:00 | 5.42 | -4.25
2019-03-03 12:30 | 13.43 | -12.85
2019-03-03 13:00 | 21.19 | -20.51
2019-03-03 13:30 | 8.64 | 2.31
2019-03-03 14:00 | 26.1 | 14.61
2019-03-03 14:30 | 21.18 | 0.18
2019-03-03 15:00 | 46.46 | -39.43
2019-03-03 15:30 | 52.54 | -45.62
2019-03-03 16:00 | 49.59 | -38
2019-03-03 16:30 | 14.64 | 11.09
2019-03-03 17:00 | 11.84 | 9.55
2019-03-03 17:30 | 25.34 | 24.91
2019-03-03 18:00 | 66.34 | 65.52
2019-03-03 18:30 | 72.77 | 72.36
2019-03-03 19:00 | 83.96 | 83.7
2019-03-03 19:30 | 93 | 92.53
2019-03-03 20:00 | 87.29 | 86.5
2019-03-03 20:30 | 84.14 | 82.8
2019-03-03 21:00 | 99.75 | 98.42
2019-03-03 21:30 | 75.36 | 75.34
2019-03-03 22:00 | 58.64 | 54.19
2019-03-03 22:30 | 77.93 | 72.23
2019-03-03 23:00 | 83.95 | 78.07
2019-03-03 23:30 | 58.01 | 48.83
2019-03-04 | 34.86 | 14.67
2019-03-04 00:30 | 33.15 | -10.01
2019-03-04 01:00 | 48.52 | -38.12
2019-03-04 01:30 | 39.37 | -30.46
2019-03-04 02:00 | 45.9 | -39.79
2019-03-04 02:30 | 47.6 | -42.16
2019-03-04 03:00 | 50.04 | -44.82
2019-03-04 03:30 | 53.36 | -49.15
2019-03-04 04:00 | 34.83 | -26.31
2019-03-04 04:30 | 47.6 | -43.43
2019-03-04 05:00 | 28.72 | -20.85
2019-03-04 05:30 | 18.07 | -0.27
2019-03-04 06:00 | 16.46 | 3.59
2019-03-04 06:30 | 19.64 | 17.25
2019-03-04 07:00 | 28.8 | 28.63
2019-03-04 07:30 | 53.62 | 21.97
2019-03-04 08:00 | 66.6 | 15.25
2019-03-04 08:30 | 69.69 | 8.72
2019-03-04 09:00 | 73.45 | 15.1
2019-03-04 09:30 | 110.38 | -49.16
2019-03-04 10:00 | 109.22 | -49.37
2019-03-04 10:30 | 121.97 | -69.68
2019-03-04 11:00 | 119.17 | -64.45
2019-03-04 11:30 | 109.7 | -48.09
2019-03-04 12:00 | 127.84 | -80.07
2019-03-04 12:30 | 147.04 | -99.17
2019-03-04 13:00 | 147.68 | -92.35
2019-03-04 13:30 | 147.02 | -91.42
2019-03-04 14:00 | 144.46 | -86.18
2019-03-04 14:30 | 141.49 | -81.49
2019-03-04 15:00 | 118.65 | -67.56
2019-03-04 15:30 | 120.6 | -79.06
2019-03-04 16:00 | 102.8 | -51.68
2019-03-04 16:30 | 97.16 | -38.6
2019-03-04 17:00 | 78.21 | 47.62
2019-03-04 17:30 | 103.83 | 87.05
2019-03-04 18:00 | 113.03 | 100.86
2019-03-04 18:30 | 122.19 | 111.16
2019-03-04 19:00 | 149.54 | 138.47
2019-03-04 19:30 | 130.07 | 119.1
2019-03-04 20:00 | 107.83 | 96.31
2019-03-04 20:30 | 116.1 | 111.46
2019-03-04 21:00 | 94.17 | 93.31
2019-03-04 21:30 | 82.21 | 81.68
2019-03-04 22:00 | 74.68 | 74.29
2019-03-04 22:30 | 71.98 | 71.68
2019-03-04 23:00 | 76.67 | 76.2
2019-03-04 23:30 | 62.93 | 61.88
2019-03-05 | 28.58 | 25.09
2019-03-05 00:30 | 17.73 | 8.07
2019-03-05 01:00 | 18.41 | -7.57
2019-03-05 01:30 | 22.39 | -13.16
2019-03-05 02:00 | 24.8 | -17.05
2019-03-05 02:30 | 28.24 | -22.03
2019-03-05 03:00 | 30.53 | -24.94
2019-03-05 03:30 | 48.66 | -46.12
2019-03-05 04:00 | 24.03 | -17.06
2019-03-05 04:30 | 16.76 | -2.68
2019-03-05 05:00 | 17.36 | 6.34
2019-03-05 05:30 | 15.37 | 8.39
2019-03-05 06:00 | 46.93 | -46.74
2019-03-05 06:30 | 17.56 | 17.26
2019-03-05 07:00 | 40.94 | 40.94
2019-03-05 07:30 | 44.41 | 14.53
2019-03-05 08:00 | 108.53 | -81.78
2019-03-05 08:30 | 107.7 | -92.8
2019-03-05 09:00 | 94.75 | -80.07
2019-03-05 09:30 | 86.81 | -69.49
2019-03-05 10:00 | 75.04 | -55.46
2019-03-05 10:30 | 41.11 | -22.18
2019-03-05 11:00 | 44.36 | -31.99
2019-03-05 11:30 | 39.22 | -25.2
2019-03-05 12:00 | 34.5 | -19.38
2019-03-05 12:30 | 38.14 | -23.09
2019-03-05 13:00 | 42.27 | -28.49
2019-03-05 13:30 | 70.75 | -61.02
2019-03-05 14:00 | 30.21 | 4.21
2019-03-05 14:30 | 36.91 | 22.87
2019-03-05 15:00 | 47.85 | 38.55
2019-03-05 15:30 | 49.05 | 39.72
2019-03-05 16:00 | 71.25 | 65.67
2019-03-05 16:30 | 81.95 | 76.95
2019-03-05 17:00 | 92.49 | 88.5
2019-03-05 17:30 | 94.95 | 92.28
2019-03-05 18:00 | 103.3 | 101.59
2019-03-05 18:30 | 107.46 | 105.93
2019-03-05 19:00 | 147.13 | 144.85
2019-03-05 19:30 | 134.79 | 132.06
2019-03-05 20:00 | 115.76 | 112.74
2019-03-05 20:30 | 127.24 | 125.48
2019-03-05 21:00 | 101.11 | 99.8
2019-03-05 21:30 | 61.08 | 60.35
2019-03-05 22:00 | 48.33 | 45.94
2019-03-05 22:30 | 69.57 | 67.56
2019-03-05 23:00 | 102.56 | 100.92
2019-03-05 23:30 | 68.94 | 68.08
2019-03-06 | 21.56 | 18.41
2019-03-06 00:30 | 21.46 | 15.83
2019-03-06 01:00 | 31.03 | 26.25
2019-03-06 01:30 | 32.01 | 26.96
2019-03-06 02:00 | 25.43 | 17.47
2019-03-06 02:30 | 24.93 | 16.58
2019-03-06 03:00 | 50.21 | 46.16
2019-03-06 03:30 | 58.98 | 55.66
2019-03-06 04:00 | 61.48 | 58.5
2019-03-06 04:30 | 66.07 | 63.57
2019-03-06 05:00 | 80.26 | 78.37
2019-03-06 05:30 | 93.56 | 92.44
2019-03-06 06:00 | 66.52 | 65.34
2019-03-06 06:30 | 39.48 | 39.25
2019-03-06 07:00 | 66.94 | 66.92
2019-03-06 07:30 | 70.08 | 70.08
2019-03-06 08:00 | 41.11 | 41.07
2019-03-06 08:30 | 53.39 | 49.59
2019-03-06 09:00 | 87.7 | 77.19
2019-03-06 09:30 | 89.81 | 72.81
2019-03-06 10:00 | 105.33 | 90
2019-03-06 10:30 | 100.02 | 82.67
2019-03-06 11:00 | 113.06 | 98.47
2019-03-06 11:30 | 126.89 | 114.1
2019-03-06 12:00 | 114.32 | 98.89
2019-03-06 12:30 | 104.63 | 85.22
2019-03-06 13:00 | 113.81 | 95.88
2019-03-06 13:30 | 116.48 | 99.3
2019-03-06 14:00 | 141.77 | 127.99
2019-03-06 14:30 | 169.85 | 158.73
2019-03-06 15:00 | 184.9 | 174.44
2019-03-06 15:30 | 186.99 | 176.26
2019-03-06 16:00 | 245.91 | 236.93
2019-03-06 16:30 | 263.83 | 255.8
2019-03-06 17:00 | 266.83 | 259.01
2019-03-06 17:30 | 254.58 | 247.4
2019-03-06 18:00 | 226.73 | 219.92
2019-03-06 18:30 | 220.86 | 214.43
2019-03-06 19:00 | 228.92 | 221.37
2019-03-06 19:30 | 202.55 | 195.08
2019-03-06 20:00 | 188.54 | 181.99
2019-03-06 20:30 | 181.08 | 178.53
2019-03-06 21:00 | 158.54 | 154.24
2019-03-06 21:30 | 143.12 | 138.74
2019-03-06 22:00 | 128.24 | 124.89
2019-03-06 22:30 | 125.63 | 124.99
2019-03-06 23:00 | 116.55 | 116.52
2019-03-06 23:30 | 77.29 | 77.28
2019-03-07 | 47.69 | 47.37
2019-03-07 00:30 | 40.6 | 39.84
2019-03-07 01:00 | 58.5 | 57.72
2019-03-07 01:30 | 72.33 | 71.31
2019-03-07 02:00 | 62.3 | 60.78
2019-03-07 02:30 | 47.06 | 45.02
2019-03-07 03:00 | 33.5 | 30.38
2019-03-07 03:30 | 30.12 | 26.49
2019-03-07 04:00 | 28.76 | 24.98
2019-03-07 04:30 | 26.05 | 22.29
2019-03-07 05:00 | 30.4 | 28
2019-03-07 05:30 | 18.58 | 17.12
2019-03-07 06:00 | 15.91 | 15.13
2019-03-07 06:30 | 39.57 | 39.57
2019-03-07 07:00 | 78.75 | 78.51
2019-03-07 07:30 | 95.05 | 94.97
2019-03-07 08:00 | 92.35 | 92.34
2019-03-07 08:30 | 100.47 | 89.76
2019-03-07 09:00 | 95.16 | 89.58
2019-03-07 09:30 | 97.34 | 90.23
2019-03-07 10:00 | 103.38 | 94.7
2019-03-07 10:30 | 135.28 | 127.89
2019-03-07 11:00 | 143.92 | 137.3
2019-03-07 11:30 | 140.47 | 135.69
2019-03-07 12:00 | 134.91 | 130.01
2019-03-07 12:30 | 150.15 | 145.57
2019-03-07 13:00 | 166.07 | 161.43
2019-03-07 13:30 | 197.44 | 192.67
2019-03-07 14:00 | 204.69 | 200.03
2019-03-07 14:30 | 197.03 | 192.13
2019-03-07 15:00 | 208.14 | 203.55
2019-03-07 15:30 | 214.5 | 210.05
2019-03-07 16:00 | 226.58 | 222.27
2019-03-07 16:30 | 224.85 | 220.99
2019-03-07 17:00 | 230.52 | 226.85
2019-03-07 17:30 | 242.3 | 239.54
2019-03-07 18:00 | 238.83 | 236.83
2019-03-07 18:30 | 243.6 | 241.56
2019-03-07 19:00 | 251.48 | 248.89
2019-03-07 19:30 | 253.63 | 251.72
2019-03-07 20:00 | 241.26 | 238.82
2019-03-07 20:30 | 244.09 | 241.92
2019-03-07 21:00 | 236.21 | 232.7
2019-03-07 21:30 | 225.86 | 223.05
2019-03-07 22:00 | 204.13 | 201.87
2019-03-07 22:30 | 169.22 | 166.69
2019-03-07 23:00 | 156.49 | 154.09
2019-03-07 23:30 | 130.71 | 130.45
2019-03-08 | 89.76 | 87.54
2019-03-08 00:30 | 75.16 | 71.96
2019-03-08 01:00 | 50.1 | 44.83
2019-03-08 01:30 | 47.64 | 41.32
2019-03-08 02:00 | 41.49 | 34.26
2019-03-08 02:30 | 33.35 | 24.83
2019-03-08 03:00 | 41.48 | 34.92
2019-03-08 03:30 | 55.46 | 50.81
2019-03-08 04:00 | 42.62 | 37.19
2019-03-08 04:30 | 45.63 | 41.25
2019-03-08 05:00 | 62.1 | 59.03
2019-03-08 05:30 | 78.76 | 76.85
2019-03-08 06:00 | 68.66 | 67.2
2019-03-08 06:30 | 84.98 | 84.96
2019-03-08 07:00 | 92.19 | 92.15
2019-03-08 07:30 | 97.45 | 97.45
2019-03-08 08:00 | 98.35 | 98.34
2019-03-08 08:30 | 96.89 | 91.79
2019-03-08 09:00 | 118.47 | 102.69
2019-03-08 09:30 | 118.44 | 100.55
2019-03-08 10:00 | 133.07 | 116.41
2019-03-08 10:30 | 121.9 | 103.18
2019-03-08 11:00 | 119.67 | 98.93
2019-03-08 11:30 | 138.7 | 120.33
2019-03-08 12:00 | 143.23 | 125.87
2019-03-08 12:30 | 117.13 | 96.46
2019-03-08 13:00 | 122.85 | 105.06
2019-03-08 13:30 | 133.92 | 118.27
2019-03-08 14:00 | 140.09 | 125.39
2019-03-08 14:30 | 140.22 | 126.09
2019-03-08 15:00 | 137.67 | 123.76
2019-03-08 15:30 | 121.85 | 106.36
2019-03-08 16:00 | 113.47 | 96.58
2019-03-08 16:30 | 112.91 | 96.13
2019-03-08 17:00 | 124.43 | 110.03
2019-03-08 17:30 | 127.46 | 115.99
2019-03-08 18:00 | 135.8 | 132.52
2019-03-08 18:30 | 143.07 | 140.72
2019-03-08 19:00 | 153.26 | 150.34
2019-03-08 19:30 | 141.01 | 138.51
2019-03-08 20:00 | 136.14 | 132.19
2019-03-08 20:30 | 129.12 | 125.78
2019-03-08 21:00 | 114.11 | 110.91
2019-03-08 21:30 | 114.11 | 111.89
2019-03-08 22:00 | 103.2 | 101.34
2019-03-08 22:30 | 100.05 | 96.31
2019-03-08 23:00 | 116.75 | 113.4
2019-03-08 23:30 | 93.98 | 93.77
2019-03-09 | 70.3 | 67.13
2019-03-09 00:30 | 38.43 | 32.19
2019-03-09 01:00 | 19.99 | -0.14
2019-03-09 01:30 | 21.23 | -3.98
2019-03-09 02:00 | 22.82 | -10.4
2019-03-09 02:30 | 30.84 | -25.07
2019-03-09 03:00 | 33.69 | -28.84
2019-03-09 03:30 | 31.36 | -26.41
2019-03-09 04:00 | 30.28 | -25.02
2019-03-09 04:30 | 26.78 | -21.28
2019-03-09 05:00 | 22.49 | -15.01
2019-03-09 05:30 | 22.32 | -15.68
2019-03-09 06:00 | 25.36 | -21.62
2019-03-09 06:30 | 25.28 | -22.92
2019-03-09 07:00 | 18.98 | -16.34
2019-03-09 07:30 | 22.01 | -21.1
2019-03-09 08:00 | 45.09 | -44.93
2019-03-09 08:30 | 26.58 | -23.25
2019-03-09 09:00 | 14.07 | 14
2019-03-09 09:30 | 10.18 | 10.06
2019-03-09 10:00 | 12.31 | -10.11
2019-03-09 10:30 | 14 | 12.65
2019-03-09 11:00 | 28.57 | 28.12
2019-03-09 11:30 | 33.02 | 32.54
2019-03-09 12:00 | 30.28 | 29.53
2019-03-09 12:30 | 33.52 | 32.92
2019-03-09 13:00 | 39.68 | 39.04
2019-03-09 13:30 | 74.26 | 73.97
2019-03-09 14:00 | 82.47 | 81.04
2019-03-09 14:30 | 111.35 | 104.72
2019-03-09 15:00 | 128.34 | 122.27
2019-03-09 15:30 | 159.77 | 154.67
2019-03-09 16:00 | 192.34 | 187.9
2019-03-09 16:30 | 205.17 | 200.82
2019-03-09 17:00 | 201.9 | 197.28
2019-03-09 17:30 | 205.02 | 200.96
2019-03-09 18:00 | 203.61 | 200.29
2019-03-09 18:30 | 199.43 | 196.14
2019-03-09 19:00 | 203.8 | 200.17
2019-03-09 19:30 | 203.54 | 201.33
2019-03-09 20:00 | 185.91 | 185.62
2019-03-09 20:30 | 180.93 | 180.8
2019-03-09 21:00 | 184.18 | 184.12
2019-03-09 21:30 | 180.78 | 180.77
2019-03-09 22:00 | 158.5 | 158.49
2019-03-09 22:30 | 174.11 | 174.11
2019-03-09 23:00 | 155.19 | 155.18
2019-03-09 23:30 | 115.66 | 114.43
2019-03-10 | 76.01 | 73.2
2019-03-10 00:30 | 59.03 | 54.9
2019-03-10 01:00 | 41.81 | 35.26
2019-03-10 01:30 | 35.32 | 27.19
2019-03-10 02:00 | 33.64 | 24.44
2019-03-10 02:30 | 26.41 | 14.25
2019-03-10 03:00 | 25.81 | 13.36
2019-03-10 03:30 | 23.85 | 9.62
2019-03-10 04:00 | 23.28 | 9.78
2019-03-10 04:30 | 24.56 | 13.63
2019-03-10 05:00 | 41.56 | 35.05
2019-03-10 05:30 | 55.58 | 50.74
2019-03-10 06:00 | 50.98 | 46.2
2019-03-10 06:30 | 44.9 | 40.39
2019-03-10 07:00 | 35.55 | 30.7
2019-03-10 07:30 | 37.49 | 34.04
2019-03-10 08:00 | 18.56 | 13.06
2019-03-10 08:30 | 28.69 | 26.89
2019-03-10 09:00 | 51.56 | 51.32
2019-03-10 09:30 | 65.75 | 65.71
2019-03-10 10:00 | 54.6 | 54.59
2019-03-10 10:30 | 77.55 | 77.26
2019-03-10 11:00 | 53.4 | 53.35
2019-03-10 11:30 | 68.93 | 68.3
2019-03-10 12:00 | 82.48 | 81.68
2019-03-10 12:30 | 92.49 | 91.56
2019-03-10 13:00 | 129.27 | 128.39
2019-03-10 13:30 | 155.38 | 154.47
2019-03-10 14:00 | 176.77 | 175.99
2019-03-10 14:30 | 192.18 | 191.74
2019-03-10 15:00 | 217.98 | 217.42
2019-03-10 15:30 | 228.33 | 227.66
2019-03-10 16:00 | 241.19 | 239.71
2019-03-10 16:30 | 249.93 | 246.4
2019-03-10 17:00 | 261.17 | 257.76
2019-03-10 17:30 | 264.93 | 261.89
2019-03-10 18:00 | 266.9 | 264.23
2019-03-10 18:30 | 267.11 | 264.33
2019-03-10 19:00 | 272.63 | 269.49
2019-03-10 19:30 | 266.83 | 264.31
2019-03-10 20:00 | 249.39 | 249.08
2019-03-10 20:30 | 220.47 | 220.42
2019-03-10 21:00 | 191.64 | 191.62
2019-03-10 21:30 | 189.54 | 189.43
2019-03-10 22:00 | 183.5 | 183.12
2019-03-10 22:30 | 180.95 | 180.6
2019-03-10 23:00 | 168.61 | 168.33
2019-03-10 23:30 | 130.03 | 129.96
2019-03-11 | 91.74 | 91.48
2019-03-11 00:30 | 89.33 | 88.95
2019-03-11 01:00 | 89.39 | 88.83
2019-03-11 01:30 | 97.26 | 96.6
2019-03-11 02:00 | 96.3 | 95.46
2019-03-11 02:30 | 83.57 | 82.52
2019-03-11 03:00 | 72.99 | 71.76
2019-03-11 03:30 | 56.43 | 54.86
2019-03-11 04:00 | 58.45 | 56.94
2019-03-11 04:30 | 56.14 | 54.86
2019-03-11 05:00 | 72.18 | 71.37
2019-03-11 05:30 | 74.71 | 74.39
2019-03-11 06:00 | 81.82 | 81.68
2019-03-11 06:30 | 101.21 | 99.12
2019-03-11 07:00 | 117.27 | 112.84
2019-03-11 07:30 | 136.69 | 129.53
2019-03-11 08:00 | 149.37 | 137.37
2019-03-11 08:30 | 153.12 | 138.95
2019-03-11 09:00 | 153.8 | 137.99
2019-03-11 09:30 | 155.53 | 138.25
2019-03-11 10:00 | 174.89 | 152.53
2019-03-11 10:30 | 183.84 | 165.6
2019-03-11 11:00 | 184.44 | 168.91
2019-03-11 11:30 | 181.24 | 164.87
2019-03-11 12:00 | 191.68 | 176.52
2019-03-11 12:30 | 185.9 | 177.59
2019-03-11 13:00 | 199.32 | 190.01
2019-03-11 13:30 | 214.88 | 202.28
2019-03-11 14:00 | 211.61 | 199.75
2019-03-11 14:30 | 214.72 | 201.65
2019-03-11 15:00 | 203.7 | 194.33
2019-03-11 15:30 | 208.05 | 199.36
2019-03-11 16:00 | 251.84 | 244.94
2019-03-11 16:30 | 282.62 | 281.62
2019-03-11 17:00 | 277.96 | 277.4
2019-03-11 17:30 | 281.26 | 280.32
2019-03-11 18:00 | 292.4 | 290.89
2019-03-11 18:30 | 296.66 | 295.54
2019-03-11 19:00 | 302.54 | 301.41
2019-03-11 19:30 | 285.5 | 284.5
2019-03-11 20:00 | 261.07 | 259.98
2019-03-11 20:30 | 236.82 | 236.82
2019-03-11 21:00 | 201.98 | 201.89
2019-03-11 21:30 | 188.74 | 188.74
2019-03-11 22:00 | 179.63 | 179.17
2019-03-11 22:30 | 176.9 | 176.49
2019-03-11 23:00 | 176.23 | 175.78
2019-03-11 23:30 | 135.74 | 135.62
2019-03-12 | 90.34 | 90.34
2019-03-12 00:30 | 97.92 | 97.88
2019-03-12 01:00 | 108.29 | 108.15
2019-03-12 01:30 | 103.07 | 102.67
2019-03-12 02:00 | 106.14 | 105.21
2019-03-12 02:30 | 118.88 | 118.21
2019-03-12 03:00 | 125.65 | 125.04
2019-03-12 03:30 | 126.41 | 125.89
2019-03-12 04:00 | 102.41 | 101.95
2019-03-12 04:30 | 94.23 | 93.82
2019-03-12 05:00 | 82.03 | 81.61
2019-03-12 05:30 | 86.41 | 85.07
2019-03-12 06:00 | 94.44 | 91.06
2019-03-12 06:30 | 108.85 | 104.92
2019-03-12 07:00 | 118.83 | 115.29
2019-03-12 07:30 | 137.02 | 134.44
2019-03-12 08:00 | 142.17 | 140.29
2019-03-12 08:30 | 140.76 | 138.55
2019-03-12 09:00 | 146.18 | 143.26
2019-03-12 09:30 | 141.32 | 137.96
2019-03-12 10:00 | 150.57 | 146.29
2019-03-12 10:30 | 156.61 | 153.6
2019-03-12 11:00 | 160.89 | 158.86
2019-03-12 11:30 | 167.35 | 164.9
2019-03-12 12:00 | 174.93 | 172.27
2019-03-12 12:30 | 186.38 | 183.02
2019-03-12 13:00 | 192.89 | 189.55
2019-03-12 13:30 | 191.14 | 187.76
2019-03-12 14:00 | 199.15 | 195.32
2019-03-12 14:30 | 212.42 | 205.68
2019-03-12 15:00 | 304.12 | 298.59
2019-03-12 15:30 | 312.14 | 306.38
2019-03-12 16:00 | 325.02 | 318.99
2019-03-12 16:30 | 316.21 | 310.41
2019-03-12 17:00 | 327.75 | 322.07
2019-03-12 17:30 | 333.58 | 328.7
2019-03-12 18:00 | 331.69 | 327.86
2019-03-12 18:30 | 321.31 | 318.82
2019-03-12 19:00 | 328.47 | 325.71
2019-03-12 19:30 | 308.55 | 306.52
2019-03-12 20:00 | 272.81 | 271.73
2019-03-12 20:30 | 278.92 | 277.87
2019-03-12 21:00 | 262.37 | 260.99
2019-03-12 21:30 | 244.83 | 241.94
2019-03-12 22:00 | 210.27 | 207.58
2019-03-12 22:30 | 195.03 | 194.93
2019-03-12 23:00 | 211.99 | 211.99
2019-03-12 23:30 | 192.56 | 192.56
2019-03-13 | 148.96 | 148.95
2019-03-13 00:30 | 139.25 | 139.17
2019-03-13 01:00 | 137.75 | 137.57
2019-03-13 01:30 | 107.96 | 107.51
2019-03-13 02:00 | 88.16 | 87.4
2019-03-13 02:30 | 62.88 | 61.82
2019-03-13 03:00 | 53.83 | 52.55
2019-03-13 03:30 | 45.95 | 44.33
2019-03-13 04:00 | 43.61 | 42.04
2019-03-13 04:30 | 44.44 | 43.09
2019-03-13 05:00 | 64.89 | 63.95
2019-03-13 05:30 | 61.37 | 60.92
2019-03-13 06:00 | 64.87 | 64.71
2019-03-13 06:30 | 100.8 | 100.8
2019-03-13 07:00 | 103.93 | 103.85
2019-03-13 07:30 | 120.66 | 120.66
2019-03-13 08:00 | 138.77 | 137.66
2019-03-13 08:30 | 145.85 | 141.05
2019-03-13 09:00 | 150.41 | 145.08
2019-03-13 09:30 | 163.08 | 156.09
2019-03-13 10:00 | 172.17 | 164.27
2019-03-13 10:30 | 179.87 | 171.88
2019-03-13 11:00 | 184.74 | 176.52
2019-03-13 11:30 | 196.91 | 188.88
2019-03-13 12:00 | 202.51 | 194.79
2019-03-13 12:30 | 223.27 | 216.08
2019-03-13 13:00 | 243.24 | 236.3
2019-03-13 13:30 | 252.85 | 245.76
2019-03-13 14:00 | 271.56 | 264.57
2019-03-13 14:30 | 272.81 | 266.01
2019-03-13 15:00 | 274.67 | 268.12
2019-03-13 15:30 | 279.02 | 272.86
2019-03-13 16:00 | 286.01 | 279.72
2019-03-13 16:30 | 294.58 | 290.95
2019-03-13 17:00 | 298.36 | 296.03
2019-03-13 17:30 | 296.09 | 294.51
2019-03-13 18:00 | 286.46 | 284.02
2019-03-13 18:30 | 284.49 | 279.32
2019-03-13 19:00 | 284.82 | 281.93
2019-03-13 19:30 | 275.8 | 273.73
2019-03-13 20:00 | 267.59 | 265.98
2019-03-13 20:30 | 254.93 | 253.24
2019-03-13 21:00 | 236.47 | 235.55
2019-03-13 21:30 | 226.15 | 225.03
2019-03-13 22:00 | 214.75 | 214.55
2019-03-13 22:30 | 207.41 | 207.34
2019-03-13 23:00 | 200.64 | 200.44
2019-03-13 23:30 | 183.52 | 182.97
2019-03-14 | 163.2 | 162.34
2019-03-14 00:30 | 155.13 | 153.99
2019-03-14 01:00 | 150.25 | 148.8
2019-03-14 01:30 | 141.14 | 139.42
2019-03-14 02:00 | 112.41 | 110.06
2019-03-14 02:30 | 107.4 | 104.96
2019-03-14 03:00 | 112.6 | 110.38
2019-03-14 03:30 | 93.3 | 90.7
2019-03-14 04:00 | 75.88 | 72.81
2019-03-14 04:30 | 91.04 | 88.91
2019-03-14 05:00 | 111.08 | 109.57
2019-03-14 05:30 | 129.3 | 128.27
2019-03-14 06:00 | 100.88 | 99.64
2019-03-14 06:30 | 124.42 | 124.41
2019-03-14 07:00 | 123.89 | 123.88
2019-03-14 07:30 | 116.94 | 116.85
2019-03-14 08:00 | 109.93 | 109.89
2019-03-14 08:30 | 113.15 | 112.77
2019-03-14 09:00 | 120.44 | 116.68
2019-03-14 09:30 | 124.92 | 118.09
2019-03-14 10:00 | 125.21 | 117.88
2019-03-14 10:30 | 125.45 | 117.5
2019-03-14 11:00 | 129.59 | 121.04
2019-03-14 11:30 | 154.08 | 146.82
2019-03-14 12:00 | 157.02 | 149.81
2019-03-14 12:30 | 168.35 | 161.47
2019-03-14 13:00 | 173.82 | 166.89
2019-03-14 13:30 | 184.48 | 177.46
2019-03-14 14:00 | 186.43 | 181.67
2019-03-14 14:30 | 219.76 | 217.01
2019-03-14 15:00 | 241.1 | 238.83
2019-03-14 15:30 | 246.68 | 244.58
2019-03-14 16:00 | 253.84 | 252.23
2019-03-14 16:30 | 224.75 | 222.95
2019-03-14 17:00 | 229.08 | 227.34
2019-03-14 17:30 | 219.83 | 218.49
2019-03-14 18:00 | 230.91 | 230.17
2019-03-14 18:30 | 246.75 | 245.65
2019-03-14 19:00 | 256.45 | 255.35
2019-03-14 19:30 | 245.27 | 244.44
2019-03-14 20:00 | 236.57 | 236.11
2019-03-14 20:30 | 215.49 | 215.14
2019-03-14 21:00 | 194.08 | 193.09
2019-03-14 21:30 | 165.73 | 164.76
2019-03-14 22:00 | 125.09 | 124.57
2019-03-14 22:30 | 104.3 | 103.93
2019-03-14 23:00 | 98.12 | 97.14
2019-03-14 23:30 | 61.98 | 60.32
2019-03-15 | 23.8 | 21.21
2019-03-15 00:30 | 25.39 | 22.79
2019-03-15 01:00 | 23.19 | 20.34
2019-03-15 01:30 | 14.58 | 10.53
2019-03-15 02:00 | 12.78 | 8.4
2019-03-15 02:30 | 15.03 | 12
2019-03-15 03:00 | 23.28 | 21.25
2019-03-15 03:30 | 30.44 | 27.92
2019-03-15 04:00 | 28.57 | 25.85
2019-03-15 04:30 | 42.56 | 41
2019-03-15 05:00 | 65.3 | 63.45
2019-03-15 05:30 | 37.52 | 33.02
2019-03-15 06:00 | 20.95 | 17.42
2019-03-15 06:30 | 16.43 | 15.47
2019-03-15 07:00 | 33.14 | 32.12
2019-03-15 07:30 | 37.25 | 37.25
2019-03-15 08:00 | 46.32 | 33.32
2019-03-15 08:30 | 44.83 | 28.26
2019-03-15 09:00 | 50.81 | 30.73
2019-03-15 09:30 | 56.34 | 33.94
2019-03-15 10:00 | 70.23 | 51.33
2019-03-15 10:30 | 82.01 | 57.32
2019-03-15 11:00 | 98.47 | 68.03
2019-03-15 11:30 | 103.29 | 71.88
2019-03-15 12:00 | 129.42 | 105.53
2019-03-15 12:30 | 167.31 | 147.98
2019-03-15 13:00 | 200.77 | 184.51
2019-03-15 13:30 | 196.05 | 180.49
2019-03-15 14:00 | 223.26 | 207.39
2019-03-15 14:30 | 249.4 | 236.3
2019-03-15 15:00 | 279.16 | 268.16
2019-03-15 15:30 | 268.16 | 257.26
2019-03-15 16:00 | 241.53 | 235.15
2019-03-15 16:30 | 233.35 | 227.67
2019-03-15 17:00 | 221.79 | 216.12
2019-03-15 17:30 | 219.07 | 213.59
2019-03-15 18:00 | 190.4 | 182.1
2019-03-15 18:30 | 171.84 | 165.61
2019-03-15 19:00 | 162.83 | 161.03
2019-03-15 19:30 | 145.15 | 143.93
2019-03-15 20:00 | 147.63 | 147.25
2019-03-15 20:30 | 153.53 | 153.51
2019-03-15 21:00 | 135.54 | 135.47
2019-03-15 21:30 | 130.68 | 129.44
2019-03-15 22:00 | 127.68 | 126.94
2019-03-15 22:30 | 168.63 | 168.21
2019-03-15 23:00 | 174.59 | 174.27
2019-03-15 23:30 | 112.92 | 112.8
2019-03-16 | 56.02 | 54
2019-03-16 00:30 | 73.4 | 70.79
2019-03-16 01:00 | 84.31 | 81.67
2019-03-16 01:30 | 111.67 | 109.7
2019-03-16 02:00 | 109.22 | 106.98
2019-03-16 02:30 | 96.16 | 93.61
2019-03-16 03:00 | 108.41 | 106.12
2019-03-16 03:30 | 97.62 | 95.08
2019-03-16 04:00 | 89.09 | 86.3
2019-03-16 04:30 | 92.76 | 90.27
2019-03-16 05:00 | 111.88 | 110.13
2019-03-16 05:30 | 105.21 | 103.32
2019-03-16 06:00 | 79.05 | 76.81
2019-03-16 06:30 | 55.77 | 53.41
2019-03-16 07:00 | 32.47 | 28.75
2019-03-16 07:30 | 34.71 | 34.7
2019-03-16 08:00 | 43.29 | 40.73
2019-03-16 08:30 | 70.66 | 60.91
2019-03-16 09:00 | 80 | 70.05
2019-03-16 09:30 | 78.37 | 67.62
2019-03-16 10:00 | 66.45 | 53.1
2019-03-16 10:30 | 104.14 | 74.22
2019-03-16 11:00 | 77.34 | 66.99
2019-03-16 11:30 | 75.96 | 65.37
2019-03-16 12:00 | 74.16 | 63.04
2019-03-16 12:30 | 76.21 | 65.97
2019-03-16 13:00 | 77.67 | 67.19
2019-03-16 13:30 | 82.4 | 72.37
2019-03-16 14:00 | 76.07 | 65.78
2019-03-16 14:30 | 52.63 | 35.46
2019-03-16 15:00 | 74.13 | 64.28
2019-03-16 15:30 | 80.93 | 76.93
2019-03-16 16:00 | 82.02 | 80.8
2019-03-16 16:30 | 98.95 | 97.94
2019-03-16 17:00 | 101.07 | 100.03
2019-03-16 17:30 | 81.73 | 80.46
2019-03-16 18:00 | 88.5 | 87.49
2019-03-16 18:30 | 95.68 | 94.29
2019-03-16 19:00 | 124.78 | 123.65
2019-03-16 19:30 | 137.41 | 137.39
2019-03-16 20:00 | 141.95 | 141.95
2019-03-16 20:30 | 139.83 | 139.83
2019-03-16 21:00 | 102.15 | 102.13
2019-03-16 21:30 | 99.15 | 99.06
2019-03-16 22:00 | 94.29 | 94.01
2019-03-16 22:30 | 115.39 | 114.99
2019-03-16 23:00 | 135.56 | 135.13
2019-03-16 23:30 | 127.38 | 126.71
2019-03-17 | 91.76 | 89.57
2019-03-17 00:30 | 53.03 | 48.93
2019-03-17 01:00 | 32.9 | 25.8
2019-03-17 01:30 | 40.78 | 35.14
2019-03-17 02:00 | 32.68 | 24.22
2019-03-17 02:30 | 19.79 | -3.9
2019-03-17 03:00 | 21.4 | -8.89
2019-03-17 03:30 | 24.31 | -12.8
2019-03-17 04:00 | 20.38 | -7.66
2019-03-17 04:30 | 19.22 | 8.96
2019-03-17 05:00 | 26.99 | 21.24
2019-03-17 05:30 | 57.3 | 55.01
2019-03-17 06:00 | 43.51 | 40.28
2019-03-17 06:30 | 19.08 | 10.6
2019-03-17 07:00 | 15.83 | 0.03
2019-03-17 07:30 | 19.66 | -14.77
2019-03-17 08:00 | 8.73 | 4.24
2019-03-17 08:30 | 24.86 | 22.65
2019-03-17 09:00 | 53.18 | 53.11
2019-03-17 09:30 | 64.83 | 64.68
2019-03-17 10:00 | 62.94 | 61.71
2019-03-17 10:30 | 46.77 | 38.04
2019-03-17 11:00 | 45.66 | 35.69
2019-03-17 11:30 | 37.57 | 24.94
2019-03-17 12:00 | 36.49 | 23.24
2019-03-17 12:30 | 46.93 | 25.74
2019-03-17 13:00 | 50.43 | 32.63
2019-03-17 13:30 | 92.47 | 83.05
2019-03-17 14:00 | 109.77 | 101.49
2019-03-17 14:30 | 122.01 | 113.97
2019-03-17 15:00 | 137.47 | 130.48
2019-03-17 15:30 | 151.84 | 146.13
2019-03-17 16:00 | 151.68 | 146.65
2019-03-17 16:30 | 142.89 | 137.8
2019-03-17 17:00 | 155.1 | 150.36
2019-03-17 17:30 | 132.94 | 126.73
2019-03-17 18:00 | 141.68 | 135.6
2019-03-17 18:30 | 157.25 | 151.67
2019-03-17 19:00 | 155.27 | 150.06
2019-03-17 19:30 | 134.62 | 131.54
2019-03-17 20:00 | 118.49 | 118.33
2019-03-17 20:30 | 122.95 | 122.9
2019-03-17 21:00 | 133.96 | 133.96
2019-03-17 21:30 | 142.64 | 142.63
2019-03-17 22:00 | 142.28 | 142.14
2019-03-17 22:30 | 153.1 | 152.88
2019-03-17 23:00 | 165.05 | 164.82
2019-03-17 23:30 | 154.59 | 154.24
2019-03-18 | 135.16 | 133.34
2019-03-18 00:30 | 113.64 | 110.68
2019-03-18 01:00 | 98.48 | 95
2019-03-18 01:30 | 91.78 | 87.97
2019-03-18 02:00 | 83.51 | 79.29
2019-03-18 02:30 | 93.19 | 89.74
2019-03-18 03:00 | 108.71 | 105.97
2019-03-18 03:30 | 115.95 | 113.57
2019-03-18 04:00 | 104.63 | 102.18
2019-03-18 04:30 | 108.83 | 106.63
2019-03-18 05:00 | 121.29 | 119.32
2019-03-18 05:30 | 97.39 | 94.63
2019-03-18 06:00 | 103.74 | 101.65
2019-03-18 06:30 | 128.45 | 127.29
2019-03-18 07:00 | 147.06 | 146.53
2019-03-18 07:30 | 144.74 | 144.72
2019-03-18 08:00 | 142.39 | 142.3
2019-03-18 08:30 | 142.31 | 141.87
2019-03-18 09:00 | 125.44 | 124.57
2019-03-18 09:30 | 129.14 | 127.71
2019-03-18 10:00 | 133.7 | 131.77
2019-03-18 10:30 | 145.19 | 142.98
2019-03-18 11:00 | 165.06 | 162.48
2019-03-18 11:30 | 187.63 | 185.33
2019-03-18 12:00 | 184.93 | 182.52
2019-03-18 12:30 | 175.81 | 173.28
2019-03-18 13:00 | 191.87 | 190.56
2019-03-18 13:30 | 242.33 | 241.68
2019-03-18 14:00 | 206.38 | 205.79
2019-03-18 14:30 | 217.69 | 217.02
2019-03-18 15:00 | 196.76 | 195.18
2019-03-18 15:30 | 185.94 | 183.72
2019-03-18 16:00 | 193.04 | 190.52
2019-03-18 16:30 | 199.27 | 197.72
2019-03-18 17:00 | 203.08 | 201.81
2019-03-18 17:30 | 212.73 | 211.5
2019-03-18 18:00 | 199.65 | 198.1
2019-03-18 18:30 | 194.71 | 192.72
2019-03-18 19:00 | 209.83 | 207.81
2019-03-18 19:30 | 207.93 | 207.89
2019-03-18 20:00 | 215.96 | 215.69
2019-03-18 20:30 | 220.74 | 220.34
2019-03-18 21:00 | 196.79 | 196.69
2019-03-18 21:30 | 179.73 | 179.59
2019-03-18 22:00 | 160.82 | 159.24
2019-03-18 22:30 | 152.22 | 150.53
2019-03-18 23:00 | 166.2 | 164.65
2019-03-18 23:30 | 145.51 | 143.98
2019-03-19 | 110.48 | 108.57
2019-03-19 00:30 | 100.66 | 98.42
2019-03-19 01:00 | 103.69 | 101.61
2019-03-19 01:30 | 102.62 | 100.72
2019-03-19 02:00 | 68.24 | 65.2
2019-03-19 02:30 | 60.72 | 57.41
2019-03-19 03:00 | 51.61 | 47.83
2019-03-19 03:30 | 49.29 | 45.42
2019-03-19 04:00 | 45.49 | 42.11
2019-03-19 04:30 | 55.7 | 53.21
2019-03-19 05:00 | 68.37 | 66.21
2019-03-19 05:30 | 86.35 | 84.66
2019-03-19 06:00 | 95.63 | 94.05
2019-03-19 06:30 | 98.01 | 96.07
2019-03-19 07:00 | 109.88 | 108.64
2019-03-19 07:30 | 120.65 | 120.53
2019-03-19 08:00 | 105.99 | 105.97
2019-03-19 08:30 | 100.62 | 100.49
2019-03-19 09:00 | 83.75 | 83.53
2019-03-19 09:30 | 86.2 | 86.15
2019-03-19 10:00 | 90.53 | 90.4
2019-03-19 10:30 | 98.09 | 97.98
2019-03-19 11:00 | 101.27 | 101.12
2019-03-19 11:30 | 116.97 | 115.17
2019-03-19 12:00 | 126.53 | 121.3
2019-03-19 12:30 | 140.04 | 135.37
2019-03-19 13:00 | 148.72 | 144.35
2019-03-19 13:30 | 164.51 | 161.44
2019-03-19 14:00 | 169.27 | 166.74
2019-03-19 14:30 | 196.69 | 194.07
2019-03-19 15:00 | 207.7 | 204.68
2019-03-19 15:30 | 228.29 | 225.61
2019-03-19 16:00 | 249.97 | 248.16
2019-03-19 16:30 | 230.36 | 229.58
2019-03-19 17:00 | 250.15 | 249.5
2019-03-19 17:30 | 266.61 | 265.76
2019-03-19 18:00 | 247.95 | 246.67
2019-03-19 18:30 | 229.67 | 227.8
2019-03-19 19:00 | 250.75 | 248.7
2019-03-19 19:30 | 230.73 | 229
2019-03-19 20:00 | 240.72 | 239.44
2019-03-19 20:30 | 242.14 | 240.31
2019-03-19 21:00 | 218.69 | 217.67
2019-03-19 21:30 | 215.56 | 215.45
2019-03-19 22:00 | 190.39 | 189.96
2019-03-19 22:30 | 185.83 | 185.71
2019-03-19 23:00 | 183.08 | 182.94
2019-03-19 23:30 | 163.98 | 163.83
2019-03-20 | 119.46 | 118.92
2019-03-20 00:30 | 106.59 | 105.75
2019-03-20 01:00 | 100.84 | 99.63
2019-03-20 01:30 | 92.42 | 90.84
2019-03-20 02:00 | 85.14 | 83.32
2019-03-20 02:30 | 66.73 | 64.47
2019-03-20 03:00 | 49.21 | 46.18
2019-03-20 03:30 | 34.6 | 30.55
2019-03-20 04:00 | 35.26 | 31.41
2019-03-20 04:30 | 38.54 | 35.63
2019-03-20 05:00 | 60.77 | 58.98
2019-03-20 05:30 | 79.39 | 78.57
2019-03-20 06:00 | 64.3 | 63.66
2019-03-20 06:30 | 74.52 | 74.41
2019-03-20 07:00 | 80.44 | 80.44
2019-03-20 07:30 | 100.53 | 93.62
2019-03-20 08:00 | 108.32 | 87.13
2019-03-20 08:30 | 119.77 | 97.52
2019-03-20 09:00 | 123.19 | 98.52
2019-03-20 09:30 | 125.29 | 103.06
2019-03-20 10:00 | 137.42 | 116.21
2019-03-20 10:30 | 140.38 | 118.36
2019-03-20 11:00 | 149.98 | 128.77
2019-03-20 11:30 | 144.68 | 122.31
2019-03-20 12:00 | 154.29 | 133.41
2019-03-20 12:30 | 196.21 | 177.2
2019-03-20 13:00 | 200.79 | 175.67
2019-03-20 13:30 | 186.11 | 159.69
2019-03-20 14:00 | 192.63 | 165.73
2019-03-20 14:30 | 230.63 | 207.9
2019-03-20 15:00 | 240.35 | 219.62
2019-03-20 15:30 | 243.08 | 224.27
2019-03-20 16:00 | 239.82 | 228.36
2019-03-20 16:30 | 205.73 | 197.57
2019-03-20 17:00 | 212.23 | 204.52
2019-03-20 17:30 | 209.84 | 203.07
2019-03-20 18:00 | 209.12 | 203.36
2019-03-20 18:30 | 235.37 | 229.98
2019-03-20 19:00 | 267.23 | 262.47
2019-03-20 19:30 | 227.51 | 223.08
2019-03-20 20:00 | 228.75 | 227.42
2019-03-20 20:30 | 206.6 | 205.64
2019-03-20 21:00 | 185.22 | 185.21
2019-03-20 21:30 | 173.38 | 173.24
2019-03-20 22:00 | 155.54 | 155.14
2019-03-20 22:30 | 163.14 | 162.82
2019-03-20 23:00 | 174.67 | 174.3
2019-03-20 23:30 | 162.55 | 161.97
2019-03-21 | 133.07 | 132.04
2019-03-21 00:30 | 110.51 | 109.83
2019-03-21 01:00 | 112.75 | 111.83
2019-03-21 01:30 | 122.07 | 121.14
2019-03-21 02:00 | 111.81 | 110.67
2019-03-21 02:30 | 92.56 | 91.19
2019-03-21 03:00 | 84.2 | 82.66
2019-03-21 03:30 | 92.96 | 91.72
2019-03-21 04:00 | 111.86 | 110.68
2019-03-21 04:30 | 107.57 | 106.51
2019-03-21 05:00 | 119.71 | 118.9
2019-03-21 05:30 | 129.08 | 128.67
2019-03-21 06:00 | 116.79 | 116.58
2019-03-21 06:30 | 116.95 | 116.94
2019-03-21 07:00 | 135.08 | 134.58
2019-03-21 07:30 | 172.95 | 168.07
2019-03-21 08:00 | 157.05 | 143.21
2019-03-21 08:30 | 155.13 | 139.32
2019-03-21 09:00 | 141.61 | 122.26
2019-03-21 09:30 | 147.44 | 127.24
2019-03-21 10:00 | 129.54 | 110.18
2019-03-21 10:30 | 125.64 | 104.94
2019-03-21 11:00 | 127.28 | 105.61
2019-03-21 11:30 | 127.43 | 104.29
2019-03-21 12:00 | 133.94 | 112.07
2019-03-21 12:30 | 138.15 | 118.15
2019-03-21 13:00 | 125.4 | 101.79
2019-03-21 13:30 | 125.2 | 100.43
2019-03-21 14:00 | 138.87 | 115.79
2019-03-21 14:30 | 168.72 | 149.52
2019-03-21 15:00 | 206.06 | 190.8
2019-03-21 15:30 | 223.21 | 211.51
2019-03-21 16:00 | 227.37 | 215.86
2019-03-21 16:30 | 233.33 | 223.13
2019-03-21 17:00 | 270.43 | 262.77
2019-03-21 17:30 | 255.21 | 248.3
2019-03-21 18:00 | 247.7 | 240.86
2019-03-21 18:30 | 260.08 | 253.42
2019-03-21 19:00 | 276.38 | 270.28
2019-03-21 19:30 | 245.69 | 240.34
2019-03-21 20:00 | 217.03 | 214.33
2019-03-21 20:30 | 214.12 | 211.17
2019-03-21 21:00 | 220.55 | 219.73
2019-03-21 21:30 | 187.85 | 187.84
2019-03-21 22:00 | 149.4 | 149.39
2019-03-21 22:30 | 166.66 | 166.66
2019-03-21 23:00 | 172.85 | 172.85
2019-03-21 23:30 | 125.69 | 125.67
2019-03-22 | 98.59 | 98.46
2019-03-22 00:30 | 94.47 | 94.06
2019-03-22 01:00 | 90.71 | 89.15
2019-03-22 01:30 | 98.08 | 96.49
2019-03-22 02:00 | 86.7 | 84.78
2019-03-22 02:30 | 81 | 78.94
2019-03-22 03:00 | 73.6 | 71.03
2019-03-22 03:30 | 81.77 | 79.55
2019-03-22 04:00 | 74.08 | 71.71
2019-03-22 04:30 | 67.13 | 64.68
2019-03-22 05:00 | 77.48 | 75.62
2019-03-22 05:30 | 87.22 | 86.07
2019-03-22 06:00 | 77.06 | 76.35
2019-03-22 06:30 | 93.91 | 93.64
2019-03-22 07:00 | 103.25 | 103.21
2019-03-22 07:30 | 122.27 | 121.69
2019-03-22 08:00 | 143.73 | 143.58
2019-03-22 08:30 | 147.08 | 144.92
2019-03-22 09:00 | 158.93 | 155.26
2019-03-22 09:30 | 157.75 | 153.6
2019-03-22 10:00 | 149.57 | 146.75
2019-03-22 10:30 | 139 | 135.59
2019-03-22 11:00 | 139.39 | 135.69
2019-03-22 11:30 | 118.51 | 113.79
2019-03-22 12:00 | 112.71 | 107.66
2019-03-22 12:30 | 128.95 | 124.57
2019-03-22 13:00 | 109.96 | 104.53
2019-03-22 13:30 | 118.51 | 113.31
2019-03-22 14:00 | 112.52 | 106.04
2019-03-22 14:30 | 119.91 | 113.37
2019-03-22 15:00 | 142.83 | 137.52
2019-03-22 15:30 | 156.42 | 151.84
2019-03-22 16:00 | 172.17 | 168.16
2019-03-22 16:30 | 189.94 | 186.83
2019-03-22 17:00 | 193.66 | 191.08
2019-03-22 17:30 | 181.99 | 179.97
2019-03-22 18:00 | 177.17 | 175.18
2019-03-22 18:30 | 177.96 | 176.16
2019-03-22 19:00 | 191.82 | 190.43
2019-03-22 19:30 | 171.83 | 171.55
2019-03-22 20:00 | 175.13 | 175.1
2019-03-22 20:30 | 172.11 | 172.11
2019-03-22 21:00 | 139.5 | 139.5
2019-03-22 21:30 | 123.75 | 123.75
2019-03-22 22:00 | 97.53 | 97.53
2019-03-22 22:30 | 127.06 | 126.42
2019-03-22 23:00 | 144.03 | 143.23
2019-03-22 23:30 | 110.1 | 108.67
2019-03-23 | 85.28 | 82.77
2019-03-23 00:30 | 83.37 | 82.11
2019-03-23 01:00 | 66.71 | 64.97
2019-03-23 01:30 | 61.38 | 59.34
2019-03-23 02:00 | 61.38 | 58.91
2019-03-23 02:30 | 59.57 | 56.73
2019-03-23 03:00 | 58.02 | 54.98
2019-03-23 03:30 | 58.77 | 54
2019-03-23 04:00 | 40.34 | 26.5
2019-03-23 04:30 | 38.2 | 23.62
2019-03-23 05:00 | 43.94 | 32.24
2019-03-23 05:30 | 49.17 | 39.05
2019-03-23 06:00 | 50.58 | 42.13
2019-03-23 06:30 | 49.23 | 41.03
2019-03-23 07:00 | 39.26 | 28.97
2019-03-23 07:30 | 42.6 | 35.89
2019-03-23 08:00 | 38.86 | 36.22
2019-03-23 08:30 | 37.25 | 36.74
2019-03-23 09:00 | 41.33 | 40.25
2019-03-23 09:30 | 58.49 | 49.71
2019-03-23 10:00 | 71.12 | 40.18
2019-03-23 10:30 | 83.31 | 47.94
2019-03-23 11:00 | 97.73 | 68.56
2019-03-23 11:30 | 117.64 | 94.24
2019-03-23 12:00 | 127.25 | 104.94
2019-03-23 12:30 | 125.42 | 104.4
2019-03-23 13:00 | 121.94 | 105.63
2019-03-23 13:30 | 135.28 | 119.46
2019-03-23 14:00 | 142.71 | 130.75
2019-03-23 14:30 | 142.6 | 138.75
2019-03-23 15:00 | 157.36 | 152.98
2019-03-23 15:30 | 171.61 | 168.29
2019-03-23 16:00 | 203.01 | 200.28
2019-03-23 16:30 | 228.92 | 226.3
2019-03-23 17:00 | 231.9 | 229.64
2019-03-23 17:30 | 241.5 | 239.92
2019-03-23 18:00 | 260.49 | 259.49
2019-03-23 18:30 | 262.02 | 260.85
2019-03-23 19:00 | 269.87 | 268.75
2019-03-23 19:30 | 241.43 | 240.75
2019-03-23 20:00 | 201.48 | 201.18
2019-03-23 20:30 | 180.86 | 180.73
2019-03-23 21:00 | 164.37 | 164.37
2019-03-23 21:30 | 162.73 | 162.46
2019-03-23 22:00 | 158.55 | 157.93
2019-03-23 22:30 | 146.01 | 145.25
2019-03-23 23:00 | 137.95 | 136.66
2019-03-23 23:30 | 122.56 | 121.9
2019-03-24 | 84.4 | 82.99
2019-03-24 00:30 | 52.1 | 48.82
2019-03-24 01:00 | 35.48 | 29.36
2019-03-24 01:30 | 42.45 | 40.57
2019-03-24 02:00 | 43.79 | 41.66
2019-03-24 02:30 | 22.68 | 18.12
2019-03-24 03:00 | 13.65 | -3.32
2019-03-24 03:30 | 35.02 | -32.68
2019-03-24 04:00 | 41.5 | -39.7
2019-03-24 04:30 | 31.62 | -29.05
2019-03-24 05:00 | 14.72 | 3.68
2019-03-24 05:30 | 18.71 | 13.31
2019-03-24 06:00 | 13.29 | 3.44
2019-03-24 06:30 | 12.08 | 2.9
2019-03-24 07:00 | 8.91 | -1.61
2019-03-24 07:30 | 5.95 | 2.21
2019-03-24 08:00 | 10.03 | 10.03
2019-03-24 08:30 | 20.2 | 18.87
2019-03-24 09:00 | 39.57 | 25.43
2019-03-24 09:30 | 52.88 | 20.8
2019-03-24 10:00 | 63.83 | 35
2019-03-24 10:30 | 74.32 | 56.92
2019-03-24 11:00 | 83.06 | 72.15
2019-03-24 11:30 | 106.18 | 96.67
2019-03-24 12:00 | 128.14 | 119.33
2019-03-24 12:30 | 152 | 143.4
2019-03-24 13:00 | 146.62 | 137.85
2019-03-24 13:30 | 161.03 | 156.32
2019-03-24 14:00 | 172.67 | 167.52
2019-03-24 14:30 | 190.17 | 186.98
2019-03-24 15:00 | 224.92 | 221.87
2019-03-24 15:30 | 257.36 | 254.08
2019-03-24 16:00 | 286.13 | 282.67
2019-03-24 16:30 | 307.61 | 304.09
2019-03-24 17:00 | 310.05 | 306.77
2019-03-24 17:30 | 309.48 | 306.72
2019-03-24 18:00 | 304.85 | 302.55
2019-03-24 18:30 | 306.21 | 303.59
2019-03-24 19:00 | 305.37 | 302.88
2019-03-24 19:30 | 296.03 | 294.46
2019-03-24 20:00 | 281.86 | 281.03
2019-03-24 20:30 | 267.45 | 265.25
2019-03-24 21:00 | 252.16 | 250.41
2019-03-24 21:30 | 235.38 | 233.6
2019-03-24 22:00 | 217.36 | 217.33
2019-03-24 22:30 | 210.02 | 209.88
2019-03-24 23:00 | 202.69 | 202.55
2019-03-24 23:30 | 185.21 | 185.13
2019-03-25 | 153.15 | 152.53
2019-03-25 00:30 | 154.96 | 152.86
2019-03-25 01:00 | 151.75 | 149.4
2019-03-25 01:30 | 147.34 | 144.81
2019-03-25 02:00 | 143.67 | 141.19
2019-03-25 02:30 | 134.55 | 133.29
2019-03-25 03:00 | 125.26 | 123.96
2019-03-25 03:30 | 124.27 | 123.19
2019-03-25 04:00 | 131.83 | 131.07
2019-03-25 04:30 | 125.12 | 124.34
2019-03-25 05:00 | 134.33 | 133.64
2019-03-25 05:30 | 152.56 | 151.93
2019-03-25 06:00 | 154.52 | 154.09
2019-03-25 06:30 | 136.84 | 136.8
2019-03-25 07:00 | 158.9 | 158.84
2019-03-25 07:30 | 147.38 | 147.31
2019-03-25 08:00 | 135.7 | 135.17
2019-03-25 08:30 | 137.89 | 135.99
2019-03-25 09:00 | 113.55 | 111.17
2019-03-25 09:30 | 126.65 | 120.9
2019-03-25 10:00 | 119.81 | 109.74
2019-03-25 10:30 | 119.2 | 107.69
2019-03-25 11:00 | 133.45 | 123.89
2019-03-25 11:30 | 159.98 | 157.24
2019-03-25 12:00 | 189.8 | 187.07
2019-03-25 12:30 | 226.74 | 224.66
2019-03-25 13:00 | 235.49 | 233.52
2019-03-25 13:30 | 239.77 | 237.92
2019-03-25 14:00 | 273.84 | 270.86
2019-03-25 14:30 | 299.12 | 296.11
2019-03-25 15:00 | 295.92 | 293.57
2019-03-25 15:30 | 298.71 | 297.44
2019-03-25 16:00 | 295.91 | 294.94
2019-03-25 16:30 | 293.38 | 292.75
2019-03-25 17:00 | 283.55 | 283.11
2019-03-25 17:30 | 280.34 | 279.79
2019-03-25 18:00 | 282.33 | 280.89
2019-03-25 18:30 | 298.04 | 296.45
2019-03-25 19:00 | 297.43 | 296.07
2019-03-25 19:30 | 266.75 | 265.84
2019-03-25 20:00 | 244.69 | 243.94
2019-03-25 20:30 | 235.07 | 234.29
2019-03-25 21:00 | 216.08 | 213.37
2019-03-25 21:30 | 204.47 | 201.39
2019-03-25 22:00 | 185.91 | 182.44
2019-03-25 22:30 | 191.02 | 187.52
2019-03-25 23:00 | 203.54 | 203.01
2019-03-25 23:30 | 162.45 | 162.45
2019-03-26 | 113.21 | 113.16
2019-03-26 00:30 | 120.91 | 120.78
2019-03-26 01:00 | 121.55 | 121.4
2019-03-26 01:30 | 135.02 | 134.82
2019-03-26 02:00 | 134.91 | 134.67
2019-03-26 02:30 | 124.44 | 124.14
2019-03-26 03:00 | 115.77 | 115.48
2019-03-26 03:30 | 108.57 | 108.22
2019-03-26 04:00 | 118.17 | 117.83
2019-03-26 04:30 | 119.18 | 118.9
2019-03-26 05:00 | 133.06 | 132.91
2019-03-26 05:30 | 131.46 | 131.43
2019-03-26 06:00 | 111.39 | 111.39
2019-03-26 06:30 | 138.52 | 138.45
2019-03-26 07:00 | 159.25 | 158.82
2019-03-26 07:30 | 182.48 | 172.27
2019-03-26 08:00 | 178.31 | 164.84
2019-03-26 08:30 | 178.29 | 161.98
2019-03-26 09:00 | 193.32 | 177.31
2019-03-26 09:30 | 214.85 | 205.28
2019-03-26 10:00 | 212.05 | 202.33
2019-03-26 10:30 | 215.55 | 205.53
2019-03-26 11:00 | 211.1 | 200.85
2019-03-26 11:30 | 225.85 | 216.06
2019-03-26 12:00 | 236.18 | 226.82
2019-03-26 12:30 | 241.49 | 232.22
2019-03-26 13:00 | 236.73 | 227.13
2019-03-26 13:30 | 246.67 | 236.86
2019-03-26 14:00 | 258.5 | 249.1
2019-03-26 14:30 | 245 | 235.59
2019-03-26 15:00 | 230.63 | 221.47
2019-03-26 15:30 | 228.56 | 219.34
2019-03-26 16:00 | 225.74 | 216.56
2019-03-26 16:30 | 214.83 | 205.82
2019-03-26 17:00 | 224.42 | 216.61
2019-03-26 17:30 | 226.23 | 219.77
2019-03-26 18:00 | 225.69 | 219.04
2019-03-26 18:30 | 220.72 | 213.8
2019-03-26 19:00 | 231.65 | 225.52
2019-03-26 19:30 | 229.23 | 227.35
2019-03-26 20:00 | 222.97 | 221.54
2019-03-26 20:30 | 203.79 | 203.04
2019-03-26 21:00 | 173.16 | 173.15
2019-03-26 21:30 | 134.91 | 134.88
2019-03-26 22:00 | 104.34 | 104.19
2019-03-26 22:30 | 124.96 | 124.67
2019-03-26 23:00 | 132.18 | 131.81
2019-03-26 23:30 | 113.68 | 112.71
2019-03-27 | 67.8 | 66.87
2019-03-27 00:30 | 50.69 | 49.74
2019-03-27 01:00 | 34.24 | 32.5
2019-03-27 01:30 | 19.5 | 16.17
2019-03-27 02:00 | 13.17 | 7.72
2019-03-27 02:30 | 10.02 | -0.59
2019-03-27 03:00 | 15.17 | -11.8
2019-03-27 03:30 | 12.54 | -8.21
2019-03-27 04:00 | 11.98 | -8.04
2019-03-27 04:30 | 8.81 | -0.59
2019-03-27 05:00 | 22.9 | 20.85
2019-03-27 05:30 | 53.06 | 52.42
2019-03-27 06:00 | 58.52 | 58.11
2019-03-27 06:30 | 71.12 | 71.04
2019-03-27 07:00 | 118.46 | 118.46
2019-03-27 07:30 | 144.02 | 143.86
2019-03-27 08:00 | 156.53 | 156.42
2019-03-27 08:30 | 161.72 | 161.72
2019-03-27 09:00 | 162.28 | 162.27
2019-03-27 09:30 | 160.46 | 160.37
2019-03-27 10:00 | 135.46 | 135.37
2019-03-27 10:30 | 151.01 | 150.87
2019-03-27 11:00 | 140.31 | 140.17
2019-03-27 11:30 | 151.38 | 151.26
2019-03-27 12:00 | 140.37 | 140.33
2019-03-27 12:30 | 142.3 | 142.24
2019-03-27 13:00 | 141.98 | 141.94
2019-03-27 13:30 | 128.6 | 128.6
2019-03-27 14:00 | 126.31 | 126.31
2019-03-27 14:30 | 132.79 | 132.79
2019-03-27 15:00 | 119.9 | 119.9
2019-03-27 15:30 | 104.08 | 104.07
2019-03-27 16:00 | 119.92 | 119.9
2019-03-27 16:30 | 124.27 | 124.18
2019-03-27 17:00 | 128.39 | 128.28
2019-03-27 17:30 | 123.35 | 123.3
2019-03-27 18:00 | 118.43 | 118.42
2019-03-27 18:30 | 135.89 | 135.88
2019-03-27 19:00 | 141.98 | 141.98
2019-03-27 19:30 | 117 | 116.98
2019-03-27 20:00 | 102.76 | 102.68
2019-03-27 20:30 | 112.2 | 112.03
2019-03-27 21:00 | 84.67 | 84.13
2019-03-27 21:30 | 61.17 | 60.56
2019-03-27 22:00 | 45.53 | 44.45
2019-03-27 22:30 | 50.9 | 49.49
2019-03-27 23:00 | 55.13 | 53.89
2019-03-27 23:30 | 50.08 | 48.43
2019-03-28 | 21.29 | 16.07
2019-03-28 00:30 | 19.09 | -12.54
2019-03-28 01:00 | 34.88 | -32
2019-03-28 01:30 | 37.02 | -34.17
2019-03-28 02:00 | 39.75 | -37.1
2019-03-28 02:30 | 29.69 | -25.37
2019-03-28 03:00 | 51.39 | -49.8
2019-03-28 03:30 | 43.8 | -41.83
2019-03-28 04:00 | 51.65 | -50.31
2019-03-28 04:30 | 49.98 | -48.47
2019-03-28 05:00 | 30.71 | -27.57
2019-03-28 05:30 | 15.9 | -10.5
2019-03-28 06:00 | 13.96 | -10.64
2019-03-28 06:30 | 32.05 | 31.41
2019-03-28 07:00 | 58.28 | 58.2
2019-03-28 07:30 | 74.48 | 74.38
2019-03-28 08:00 | 83.11 | 79.21
2019-03-28 08:30 | 92.74 | 68.51
2019-03-28 09:00 | 88.87 | 59.83
2019-03-28 09:30 | 96.89 | 69.03
2019-03-28 10:00 | 81.83 | 42.93
2019-03-28 10:30 | 75.24 | -17.81
2019-03-28 11:00 | 73.51 | -11
2019-03-28 11:30 | 81.13 | 36.88
2019-03-28 12:00 | 77.82 | 29.58
2019-03-28 12:30 | 84.05 | 43.02
2019-03-28 13:00 | 85.82 | 47.11
2019-03-28 13:30 | 97.78 | 68.52
2019-03-28 14:00 | 94.9 | 66.41
2019-03-28 14:30 | 87.59 | 54.55
2019-03-28 15:00 | 82.74 | 46.73
2019-03-28 15:30 | 76.94 | 37.29
2019-03-28 16:00 | 80.67 | 46.82
2019-03-28 16:30 | 81.04 | 48.41
2019-03-28 17:00 | 92.93 | 67.63
2019-03-28 17:30 | 104.45 | 84.23
2019-03-28 18:00 | 117.06 | 99.17
2019-03-28 18:30 | 129.98 | 113.36
2019-03-28 19:00 | 113.56 | 94.57
2019-03-28 19:30 | 113.9 | 98.9
2019-03-28 20:00 | 97.77 | 90.28
2019-03-28 20:30 | 95.21 | 88.67
2019-03-28 21:00 | 101.89 | 97.32
2019-03-28 21:30 | 83.26 | 78.26
2019-03-28 22:00 | 46.69 | 46.55
2019-03-28 22:30 | 55.08 | 54.86
2019-03-28 23:00 | 70.26 | 69.88
2019-03-28 23:30 | 47.6 | 46.68
2019-03-29 | 25.28 | 22.55
2019-03-29 00:30 | 12.5 | -3.32
2019-03-29 01:00 | 34.42 | -32.92
2019-03-29 01:30 | 32.85 | -30.82
2019-03-29 02:00 | 27.24 | -24.23
2019-03-29 02:30 | 30 | -27.3
2019-03-29 03:00 | 24.77 | -21
2019-03-29 03:30 | 29.86 | -27.33
2019-03-29 04:00 | 35.73 | -34.08
2019-03-29 04:30 | 22.72 | -19.53
2019-03-29 05:00 | 13.38 | -5.29
2019-03-29 05:30 | 10.1 | 1.57
2019-03-29 06:00 | 15.84 | 13.7
2019-03-29 06:30 | 29.23 | 29
2019-03-29 07:00 | 39.61 | 39.58
2019-03-29 07:30 | 68.76 | 68.5
2019-03-29 08:00 | 71.3 | 66.7
2019-03-29 08:30 | 80.29 | 67.61
2019-03-29 09:00 | 82.86 | 43.37
2019-03-29 09:30 | 89.26 | 51.85
2019-03-29 10:00 | 78.18 | 25.47
2019-03-29 10:30 | 80.46 | 29.29
2019-03-29 11:00 | 65.65 | 25.64
2019-03-29 11:30 | 93.03 | 71.38
2019-03-29 12:00 | 78.99 | 50.72
2019-03-29 12:30 | 74.14 | 43.01
2019-03-29 13:00 | 74.73 | 41.84
2019-03-29 13:30 | 76.13 | 43.18
2019-03-29 14:00 | 74.54 | 43.25
2019-03-29 14:30 | 88.65 | 64.91
2019-03-29 15:00 | 91.81 | 69.83
2019-03-29 15:30 | 94.86 | 75.26
2019-03-29 16:00 | 110.97 | 94.76
2019-03-29 16:30 | 113.74 | 98.44
2019-03-29 17:00 | 117.92 | 103.8
2019-03-29 17:30 | 133.65 | 123.41
2019-03-29 18:00 | 130.44 | 120.85
2019-03-29 18:30 | 137.62 | 128.27
2019-03-29 19:00 | 139.4 | 134.28
2019-03-29 19:30 | 124.96 | 122.66
2019-03-29 20:00 | 125.44 | 123.39
2019-03-29 20:30 | 130.25 | 129.63
2019-03-29 21:00 | 127.76 | 127.53
2019-03-29 21:30 | 105.66 | 105.22
2019-03-29 22:00 | 118.88 | 118.33
2019-03-29 22:30 | 160.05 | 159.66
2019-03-29 23:00 | 173.56 | 173.11
2019-03-29 23:30 | 140.46 | 140.09
2019-03-30 | 106.78 | 106.19
2019-03-30 00:30 | 98.02 | 97.32
2019-03-30 01:00 | 86.47 | 85.43
2019-03-30 01:30 | 91.88 | 90.8
2019-03-30 02:00 | 87.85 | 86.62
2019-03-30 02:30 | 89.1 | 87.81
2019-03-30 03:00 | 73.06 | 71.41
2019-03-30 03:30 | 66.64 | 64.87
2019-03-30 04:00 | 57.74 | 55.74
2019-03-30 04:30 | 67.25 | 65.51
2019-03-30 05:00 | 78.9 | 77.53
2019-03-30 05:30 | 100.25 | 99.38
2019-03-30 06:00 | 97.49 | 96.81
2019-03-30 06:30 | 104.74 | 104.23
2019-03-30 07:00 | 86.56 | 86.13
2019-03-30 07:30 | 69.7 | 69.58
2019-03-30 08:00 | 63.94 | 63.94
2019-03-30 08:30 | 67.94 | 67.7
2019-03-30 09:00 | 110.32 | 110.31
2019-03-30 09:30 | 134.34 | 134.33
2019-03-30 10:00 | 151.79 | 151.79
2019-03-30 10:30 | 178.26 | 178.26
2019-03-30 11:00 | 183.9 | 183.9
2019-03-30 11:30 | 191.61 | 191.61
2019-03-30 12:00 | 202.82 | 202.81
2019-03-30 12:30 | 204.72 | 204.71
2019-03-30 13:00 | 199.15 | 199.12
2019-03-30 13:30 | 190.22 | 190.03
2019-03-30 14:00 | 195.54 | 195.4
2019-03-30 14:30 | 197.13 | 196.88
2019-03-30 15:00 | 197.74 | 197.61
2019-03-30 15:30 | 199.75 | 199.74
2019-03-30 16:00 | 203.11 | 203.1
2019-03-30 16:30 | 210.99 | 210.99
2019-03-30 17:00 | 215.4 | 215.4
2019-03-30 17:30 | 216.72 | 216.72
2019-03-30 18:00 | 210.37 | 210.35
2019-03-30 18:30 | 214.19 | 214.06
2019-03-30 19:00 | 212.77 | 212.65
2019-03-30 19:30 | 172.61 | 172.37
2019-03-30 20:00 | 187.84 | 187.65
2019-03-30 20:30 | 179.96 | 179.86
2019-03-30 21:00 | 149.07 | 149.05
2019-03-30 21:30 | 148.34 | 148.25
2019-03-30 22:00 | 156.33 | 156.16
2019-03-30 22:30 | 169.12 | 168.86
2019-03-30 23:00 | 172.36 | 172.01
2019-03-30 23:30 | 158.92 | 158.41
2019-03-31 | 120.54 | 119.61
2019-03-31 00:30 | 105.71 | 104.35
2019-03-31 01:00 | 80.66 | 78.6
2019-03-31 01:30 | 67.83 | 65.76
2019-03-31 02:00 | 60.48 | 58.61
2019-03-31 02:30 | 57.37 | 55.5
2019-03-31 03:00 | 43.86 | 41.59
2019-03-31 03:30 | 32.31 | 29.85
2019-03-31 04:00 | 14.53 | 4.61
2019-03-31 04:30 | 23.72 | 18.32
2019-03-31 05:00 | 18.76 | 12.63
2019-03-31 05:30 | 15.96 | 8.03
2019-03-31 06:00 | 12.66 | 3.34
2019-03-31 06:30 | 10.04 | -1.23
2019-03-31 07:00 | 20.71 | -19.5
2019-03-31 07:30 | 24.51 | -23.86
2019-03-31 08:00 | 20.87 | -20.43
2019-03-31 08:30 | 14.41 | -14.21
2019-03-31 09:00 | 25.88 | -25.8
2019-03-31 09:30 | 41.19 | -41.19
2019-03-31 10:00 | 44.11 | -44.08
2019-03-31 10:30 | 41.77 | -41.69
2019-03-31 11:00 | 41.67 | -41.65
2019-03-31 11:30 | 42.91 | -42.9
2019-03-31 12:00 | 43.39 | -43.39
2019-03-31 12:30 | 44.27 | -44.26
2019-03-31 13:00 | 45.16 | -45.15
2019-03-31 13:30 | 43.22 | -43.2
2019-03-31 14:00 | 41.86 | -41.82
2019-03-31 14:30 | 31.35 | -31.24
2019-03-31 15:00 | 17.4 | -16.45
2019-03-31 15:30 | 8.1 | -0.32
2019-03-31 16:00 | 24.11 | 21.91
2019-03-31 16:30 | 40.17 | 39.46
2019-03-31 17:00 | 52.12 | 52.11
2019-03-31 17:30 | 57.8 | 57.77
2019-03-31 18:00 | 81.54 | 81.51
2019-03-31 18:30 | 108.79 | 108.75
2019-03-31 19:00 | 95.33 | 95.23
2019-03-31 19:30 | 72.9 | 72.8
2019-03-31 20:00 | 73.09 | 72.84
2019-03-31 20:30 | 65.88 | 65.6
2019-03-31 21:00 | 50.87 | 50.39
2019-03-31 21:30 | 39.24 | 38.21
2019-03-31 22:00 | 20.65 | 17.9
2019-03-31 22:30 | 24.17 | 20.96
2019-03-31 23:00 | 30.21 | 26.74
2019-03-31 23:30 | 18.26 | 10.38
2019-04-01 | 20.62 | 11.18
2019-04-01 00:30 | 17 | -11.36
2019-04-01 01:00 | 37.13 | -36.72
2019-04-01 01:30 | 45.29 | -45.12
2019-04-01 02:00 | 44.16 | -44.02
2019-04-01 02:30 | 28.3 | -27.85
2019-04-01 03:00 | 23.6 | -23.01
2019-04-01 03:30 | 24.2 | -23.81
2019-04-01 04:00 | 22.37 | -22.14
2019-04-01 04:30 | 27.32 | -27.1
2019-04-01 05:00 | 21.87 | -21.17
2019-04-01 05:30 | 19.16 | -17.43
2019-04-01 06:00 | 38.01 | -37.84
2019-04-01 06:30 | 18.2 | -17.04
2019-04-01 07:00 | 34.93 | -29.69
2019-04-01 07:30 | 23.77 | -20.67
2019-04-01 08:00 | 23.32 | 22.52
2019-04-01 08:30 | 20.9 | -18.23
2019-04-01 09:00 | 27.34 | -24.34
2019-04-01 09:30 | 8.74 | -1.7
2019-04-01 10:00 | 15.38 | -12.35
2019-04-01 10:30 | 21.59 | -17.77
2019-04-01 11:00 | 23.7 | -18.71
2019-04-01 11:30 | 28.84 | -25.11
2019-04-01 12:00 | 30.62 | -27.45
2019-04-01 12:30 | 29.55 | -26.14
2019-04-01 13:00 | 29.92 | -27.02
2019-04-01 13:30 | 26.39 | -23.17
2019-04-01 14:00 | 19.54 | -15.64
2019-04-01 14:30 | 12.2 | -6.75
2019-04-01 15:00 | 7.55 | 1.5
2019-04-01 15:30 | 12.66 | 11.29
2019-04-01 16:00 | 41.16 | 41.05
2019-04-01 16:30 | 49.32 | 49.29
2019-04-01 17:00 | 58.25 | 58.24
2019-04-01 17:30 | 55.1 | 55.08
2019-04-01 18:00 | 69.56 | 69.51
2019-04-01 18:30 | 88.46 | 88.31
2019-04-01 19:00 | 98.88 | 98.83
2019-04-01 19:30 | 88.16 | 88.15
2019-04-01 20:00 | 92.84 | 92.83
2019-04-01 20:30 | 69.05 | 68.99
2019-04-01 21:00 | 48.7 | 48.4
2019-04-01 21:30 | 39.52 | 38.8
2019-04-01 22:00 | 20.07 | 18.18
2019-04-01 22:30 | 17.52 | 14.74
2019-04-01 23:00 | 17.28 | 13.28
2019-04-01 23:30 | 26.05 | -24.02
2019-04-02 | 14.35 | -4.49
2019-04-02 00:30 | 22.04 | -17.08
2019-04-02 01:00 | 44.82 | -43.33
2019-04-02 01:30 | 39.08 | -36.68
2019-04-02 02:00 | 47.29 | -45.55
2019-04-02 02:30 | 32.95 | -29.04
2019-04-02 03:00 | 44.4 | -41.87
2019-04-02 03:30 | 36 | -32.71
2019-04-02 04:00 | 44.81 | -42.87
2019-04-02 04:30 | 36.98 | -34.66
2019-04-02 05:00 | 26.02 | -22.1
2019-04-02 05:30 | 15.84 | -8.13
2019-04-02 06:00 | 97.28 | 96.43
2019-04-02 06:30 | 124.11 | 123.9
2019-04-02 07:00 | 135.55 | 135.51
2019-04-02 07:30 | 149.24 | 148.59
2019-04-02 08:00 | 155.95 | 155.35
2019-04-02 08:30 | 148.03 | 147.48
2019-04-02 09:00 | 137.6 | 136.68
2019-04-02 09:30 | 132.26 | 130.55
2019-04-02 10:00 | 150.15 | 148.55
2019-04-02 10:30 | 142.36 | 140.77
2019-04-02 11:00 | 155.11 | 153.63
2019-04-02 11:30 | 143.6 | 142.2
2019-04-02 12:00 | 151.13 | 149.75
2019-04-02 12:30 | 141.16 | 139.54
2019-04-02 13:00 | 142.81 | 141.23
2019-04-02 13:30 | 159.92 | 158.62
2019-04-02 14:00 | 145.07 | 143.72
2019-04-02 14:30 | 145.42 | 144.18
2019-04-02 15:00 | 159.15 | 158.3
2019-04-02 15:30 | 160.93 | 160.11
2019-04-02 16:00 | 153.92 | 153.52
2019-04-02 16:30 | 112.81 | 112.59
2019-04-02 17:00 | 92.82 | 92.56
2019-04-02 17:30 | 102.27 | 101.83
2019-04-02 18:00 | 112.28 | 111.57
2019-04-02 18:30 | 131.25 | 130.43
2019-04-02 19:00 | 144.59 | 143.85
2019-04-02 19:30 | 118.89 | 117.82
2019-04-02 20:00 | 118.92 | 118.18
2019-04-02 20:30 | 122.43 | 122.24
2019-04-02 21:00 | 115.73 | 115.35
2019-04-02 21:30 | 108.33 | 107.85
2019-04-02 22:00 | 81.6 | 80.89
2019-04-02 22:30 | 64.14 | 63.37
2019-04-02 23:00 | 78.54 | 77.24
2019-04-02 23:30 | 35.69 | 34.55
2019-04-03 | 9.5 | 6.39
2019-04-03 00:30 | 25.84 | -21.83
2019-04-03 01:00 | 30.65 | -26.9
2019-04-03 01:30 | 35.02 | -31.13
2019-04-03 02:00 | 37.21 | -33.25
2019-04-03 02:30 | 37.49 | -33.14
2019-04-03 03:00 | 42.23 | -37.04
2019-04-03 03:30 | 38.35 | -33.26
2019-04-03 04:00 | 36 | -30.49
2019-04-03 04:30 | 31.8 | -25.84
2019-04-03 05:00 | 20.27 | -10.81
2019-04-03 05:30 | 17.21 | 11.43
2019-04-03 06:00 | 17.89 | 12.71
2019-04-03 06:30 | 27.06 | 24.66
2019-04-03 07:00 | 44.98 | 44.93
2019-04-03 07:30 | 35.76 | 35.7
2019-04-03 08:00 | 19.02 | -11.78
2019-04-03 08:30 | 27.75 | 26.46
2019-04-03 09:00 | 33.99 | 32.8
2019-04-03 09:30 | 36.52 | 34.75
2019-04-03 10:00 | 52.94 | 45.99
2019-04-03 10:30 | 47.3 | 36.51
2019-04-03 11:00 | 41.86 | 28.85
2019-04-03 11:30 | 32.52 | 6.02
2019-04-03 12:00 | 35.78 | -11.66
2019-04-03 12:30 | 33.9 | 1.22
2019-04-03 13:00 | 38.82 | 19.57
2019-04-03 13:30 | 48.48 | 33.8
2019-04-03 14:00 | 50.33 | 40.21
2019-04-03 14:30 | 50.37 | 42.85
2019-04-03 15:00 | 47.7 | 41.5
2019-04-03 15:30 | 46.1 | 40.27
2019-04-03 16:00 | 67.79 | 64.84
2019-04-03 16:30 | 82.44 | 80.59
2019-04-03 17:00 | 71.57 | 69.64
2019-04-03 17:30 | 91.08 | 90.01
2019-04-03 18:00 | 126.17 | 125.36
2019-04-03 18:30 | 133.63 | 132.85
2019-04-03 19:00 | 140.28 | 139.64
2019-04-03 19:30 | 112.02 | 111.12
2019-04-03 20:00 | 93.89 | 92.48
2019-04-03 20:30 | 99.75 | 99.39
2019-04-03 21:00 | 100.71 | 100.37
2019-04-03 21:30 | 92.38 | 91.72
2019-04-03 22:00 | 81.37 | 80.14
2019-04-03 22:30 | 71.71 | 70.11
2019-04-03 23:00 | 65.12 | 62.87
2019-04-03 23:30 | 34.91 | 30.12
2019-04-04 | 22.66 | 11.92
2019-04-04 00:30 | 25.19 | -16.19
2019-04-04 01:00 | 31.24 | -23.24
2019-04-04 01:30 | 30.76 | -21.97
2019-04-04 02:00 | 33.89 | -25.73
2019-04-04 02:30 | 26.33 | -13.27
2019-04-04 03:00 | 38.8 | -32.18
2019-04-04 03:30 | 41.92 | -35.94
2019-04-04 04:00 | 38.48 | -31.85
2019-04-04 04:30 | 28.36 | -18.71
2019-04-04 05:00 | 21.22 | -5.05
2019-04-04 05:30 | 37.11 | 31.89
2019-04-04 06:00 | 40.92 | 37.01
2019-04-04 06:30 | 37.77 | 35.03
2019-04-04 07:00 | 34.93 | 33.33
2019-04-04 07:30 | 37.31 | 36.43
2019-04-04 08:00 | 40.74 | 15.11
2019-04-04 08:30 | 57.28 | 4.03
2019-04-04 09:00 | 74.42 | -40.58
2019-04-04 09:30 | 91.1 | -63.55
2019-04-04 10:00 | 103.49 | -77.1
2019-04-04 10:30 | 107.37 | -81.44
2019-04-04 11:00 | 89.4 | -56.94
2019-04-04 11:30 | 87.61 | -53.16
2019-04-04 12:00 | 75.34 | -29.6
2019-04-04 12:30 | 67.41 | -0.48
2019-04-04 13:00 | 76.9 | -34.96
2019-04-04 13:30 | 84.37 | -45.4
2019-04-04 14:00 | 68.78 | -10.74
2019-04-04 14:30 | 69.66 | 16.96
2019-04-04 15:00 | 69.62 | 22.59
2019-04-04 15:30 | 65.29 | 10.05
2019-04-04 16:00 | 68.25 | 30.56
2019-04-04 16:30 | 82.09 | 57.87
2019-04-04 17:00 | 88.94 | 69.57
2019-04-04 17:30 | 95.07 | 78.32
2019-04-04 18:00 | 100.81 | 84.39
2019-04-04 18:30 | 118.14 | 103.94
2019-04-04 19:00 | 121.88 | 109.01
2019-04-04 19:30 | 98.97 | 84
2019-04-04 20:00 | 99.96 | 86.3
2019-04-04 20:30 | 113.87 | 105.51
2019-04-04 21:00 | 119.24 | 118.43
2019-04-04 21:30 | 112.64 | 112.2
2019-04-04 22:00 | 83.34 | 83.05
2019-04-04 22:30 | 51.11 | 50.79
2019-04-04 23:00 | 46.45 | 46.26
2019-04-04 23:30 | 26.09 | 25.93
2019-04-05 | 4.23 | -3.34
2019-04-05 00:30 | 59.39 | -59.18
2019-04-05 01:00 | 65.26 | -65.13
2019-04-05 01:30 | 32.6 | -25.84
2019-04-05 02:00 | 28.99 | -20.39
2019-04-05 02:30 | 25.98 | -15.15
2019-04-05 03:00 | 25.08 | -12.98
2019-04-05 03:30 | 25.77 | -14.78
2019-04-05 04:00 | 29.34 | -20.67
2019-04-05 04:30 | 21.32 | -5.75
2019-04-05 05:00 | 20.08 | 4.34
2019-04-05 05:30 | 39.54 | 35.22
2019-04-05 06:00 | 52.37 | 49.78
2019-04-05 06:30 | 41.22 | 39.14
2019-04-05 07:00 | 23.32 | 21.84
2019-04-05 07:30 | 41.61 | 41.6
2019-04-05 08:00 | 31.97 | 24.11
2019-04-05 08:30 | 29.28 | -9.63
2019-04-05 09:00 | 69.47 | -32.15
2019-04-05 09:30 | 104.79 | -58.95
2019-04-05 10:00 | 112.21 | -68.94
2019-04-05 10:30 | 110.98 | -65.56
2019-04-05 11:00 | 122.36 | -81.41
2019-04-05 11:30 | 114.6 | -69.81
2019-04-05 12:00 | 122.53 | -82.3
2019-04-05 12:30 | 97.18 | -44
2019-04-05 13:00 | 110.48 | -68.17
2019-04-05 13:30 | 108.78 | -59.94
2019-04-05 14:00 | 87.21 | 1.69
2019-04-05 14:30 | 80.25 | -5.47
2019-04-05 15:00 | 85.53 | -48.33
2019-04-05 15:30 | 64.53 | -2.49
2019-04-05 16:00 | 62.46 | 18.78
2019-04-05 16:30 | 62.1 | 48.69
2019-04-05 17:00 | 85.8 | 77.7
2019-04-05 17:30 | 116.43 | 115.05
2019-04-05 18:00 | 130.41 | 130.34
2019-04-05 18:30 | 136.6 | 136.5
2019-04-05 19:00 | 144.26 | 144.21
2019-04-05 19:30 | 134.17 | 134.17
2019-04-05 20:00 | 123.33 | 123.3
2019-04-05 20:30 | 114.18 | 114.09
2019-04-05 21:00 | 94.24 | 94.02
2019-04-05 21:30 | 73.31 | 72.81
2019-04-05 22:00 | 83.74 | 82.89
2019-04-05 22:30 | 87.51 | 86.39
2019-04-05 23:00 | 73.28 | 71.63
2019-04-05 23:30 | 35.27 | 31.02
2019-04-06 | 22.66 | 11.46
2019-04-06 00:30 | 24.74 | -7.45
2019-04-06 01:00 | 30.79 | -20.53
2019-04-06 01:30 | 23.97 | 0.87
2019-04-06 02:00 | 23.3 | -6.14
2019-04-06 02:30 | 26.09 | 10.44
2019-04-06 03:00 | 33.6 | 23.47
2019-04-06 03:30 | 31.39 | 30.35
2019-04-06 04:00 | 23 | 22.24
2019-04-06 04:30 | 23.69 | 22.64
2019-04-06 05:00 | 41.24 | 40.6
2019-04-06 05:30 | 15.98 | 14.23
2019-04-06 06:00 | 12.02 | 1.57
2019-04-06 06:30 | 19.79 | 3.37
2019-04-06 07:00 | 19.03 | 6.27
2019-04-06 07:30 | 15.7 | -4.34
2019-04-06 08:00 | 20.17 | -17.09
2019-04-06 08:30 | 8.79 | -6.27
2019-04-06 09:00 | 2.43 | -2.42
2019-04-06 09:30 | 1.91 | -1.66
2019-04-06 10:00 | 3.95 | 3.39
2019-04-06 10:30 | 3.94 | 3.27
2019-04-06 11:00 | 1.2 | -1.05
2019-04-06 11:30 | 6.15 | -6.12
2019-04-06 12:00 | 15.75 | -15.64
2019-04-06 12:30 | 10.94 | -10.75
2019-04-06 13:00 | 6.18 | 6.1
2019-04-06 13:30 | 20.85 | 20.85
2019-04-06 14:00 | 19.68 | 19.68
2019-04-06 14:30 | 17.71 | 17.7
2019-04-06 15:00 | 23.87 | 23.87
2019-04-06 15:30 | 26.78 | 26.77
2019-04-06 16:00 | 9.97 | -0.45
2019-04-06 16:30 | 30.67 | 26.36
2019-04-06 17:00 | 66.3 | 64.11
2019-04-06 17:30 | 71.98 | 69.99
2019-04-06 18:00 | 86.57 | 85.16
2019-04-06 18:30 | 113.92 | 112.96
2019-04-06 19:00 | 115.73 | 114.5
2019-04-06 19:30 | 99.43 | 97.49
2019-04-06 20:00 | 85.66 | 82.64
2019-04-06 20:30 | 97.51 | 95.26
2019-04-06 21:00 | 89.93 | 89.36
2019-04-06 21:30 | 86.02 | 85.11
2019-04-06 22:00 | 61.48 | 59.81
2019-04-06 22:30 | 63.56 | 61.62
2019-04-06 23:00 | 57.33 | 54.77
2019-04-06 23:30 | 71.38 | 68.88
2019-04-07 | 57.75 | 54.18
2019-04-07 00:30 | 37.49 | 29.19
2019-04-07 01:00 | 26.21 | -6.65
2019-04-07 01:30 | 31.51 | -20.45
2019-04-07 02:00 | 39.8 | -32.8
2019-04-07 02:30 | 38.55 | -31.52
2019-04-07 03:00 | 41.32 | -34.98
2019-04-07 03:30 | 39.6 | -32.96
2019-04-07 04:00 | 45.57 | -40.3
2019-04-07 04:30 | 35.16 | -26.64
2019-04-07 05:00 | 31.79 | -21.37
2019-04-07 05:30 | 29.21 | -15.53
2019-04-07 06:00 | 27.58 | -13.66
2019-04-07 06:30 | 24.48 | -7.81
2019-04-07 07:00 | 24.63 | -7.16
2019-04-07 07:30 | 26.68 | -12.96
2019-04-07 08:00 | 28.31 | -16.92
2019-04-07 08:30 | 15.77 | -9.82
2019-04-07 09:00 | 8.31 | -4.21
2019-04-07 09:30 | 4.77 | -1.69
2019-04-07 10:00 | 7.19 | -6.76
2019-04-07 10:30 | 7.67 | -7.45
2019-04-07 11:00 | 2.34 | -0.36
2019-04-07 11:30 | 3.61 | 2.91
2019-04-07 12:00 | 2.39 | 1.2
2019-04-07 12:30 | 21.68 | 21.62
2019-04-07 13:00 | 11.98 | 11.67
2019-04-07 13:30 | 28.28 | 28.19
2019-04-07 14:00 | 37.93 | 37.89
2019-04-07 14:30 | 64.07 | 64.02
2019-04-07 15:00 | 105.46 | 105.43
2019-04-07 15:30 | 121.95 | 121.94
2019-04-07 16:00 | 134.78 | 134.77
2019-04-07 16:30 | 127.03 | 127
2019-04-07 17:00 | 133.28 | 132.41
2019-04-07 17:30 | 149.6 | 148.46
2019-04-07 18:00 | 135.59 | 134.47
2019-04-07 18:30 | 137.47 | 136.58
2019-04-07 19:00 | 121.41 | 120.21
2019-04-07 19:30 | 107.05 | 105.45
2019-04-07 20:00 | 114.65 | 112.79
2019-04-07 20:30 | 96.93 | 95.86
2019-04-07 21:00 | 84.96 | 84.37
2019-04-07 21:30 | 74.75 | 73.83
2019-04-07 22:00 | 72.59 | 71.22
2019-04-07 22:30 | 82.94 | 81.38
2019-04-07 23:00 | 101.62 | 100.06
2019-04-07 23:30 | 77.34 | 75.09
2019-04-08 | 75.71 | 72.79
2019-04-08 00:30 | 49.37 | 43.29
2019-04-08 01:00 | 40.86 | 25.8
2019-04-08 01:30 | 31.31 | 7.97
2019-04-08 02:00 | 30.93 | 7.63
2019-04-08 02:30 | 40.19 | 26.15
2019-04-08 03:00 | 41.3 | 28.2
2019-04-08 03:30 | 35.04 | 18.21
2019-04-08 04:00 | 29 | 5.25
2019-04-08 04:30 | 45.41 | 34.88
2019-04-08 05:00 | 64.17 | 56.54
2019-04-08 05:30 | 96.9 | 91.79
2019-04-08 06:00 | 100.85 | 96.3
2019-04-08 06:30 | 102.09 | 98.23
2019-04-08 07:00 | 79.78 | 75.77
2019-04-08 07:30 | 85.14 | 84.06
2019-04-08 08:00 | 69.17 | 69.17
2019-04-08 08:30 | 70.3 | 70.1
2019-04-08 09:00 | 60.18 | 52.45
2019-04-08 09:30 | 54.81 | 42.69
2019-04-08 10:00 | 52.14 | 38.56
2019-04-08 10:30 | 48.18 | 31.63
2019-04-08 11:00 | 52.71 | 36.23
2019-04-08 11:30 | 79.24 | 35.47
2019-04-08 12:00 | 80.06 | 37.72
2019-04-08 12:30 | 83.84 | 46.41
2019-04-08 13:00 | 84.84 | 47.84
2019-04-08 13:30 | 101.2 | 72.51
2019-04-08 14:00 | 131.55 | 110.89
2019-04-08 14:30 | 146.13 | 127.59
2019-04-08 15:00 | 148.01 | 130.5
2019-04-08 15:30 | 154.87 | 139.34
2019-04-08 16:00 | 155.91 | 141.07
2019-04-08 16:30 | 168.99 | 155.94
2019-04-08 17:00 | 201.82 | 191.61
2019-04-08 17:30 | 211.64 | 202.88
2019-04-08 18:00 | 208.04 | 199.07
2019-04-08 18:30 | 173.21 | 162.26
2019-04-08 19:00 | 159.4 | 148.83
2019-04-08 19:30 | 141.27 | 132.36
2019-04-08 20:00 | 141.66 | 141.66
2019-04-08 20:30 | 137.34 | 137.3
2019-04-08 21:00 | 125.35 | 125.17
2019-04-08 21:30 | 103.75 | 103.27
2019-04-08 22:00 | 80.58 | 79.64
2019-04-08 22:30 | 71.29 | 69.81
2019-04-08 23:00 | 85 | 83.32
2019-04-08 23:30 | 78.3 | 76.63
2019-04-09 | 50.96 | 48.2
2019-04-09 00:30 | 49.14 | 45.42
2019-04-09 01:00 | 44.47 | 39.75
2019-04-09 01:30 | 45.36 | 40.38
2019-04-09 02:00 | 37.63 | 30.89
2019-04-09 02:30 | 51.06 | 40.4
2019-04-09 03:00 | 53.6 | 43.54
2019-04-09 03:30 | 44.54 | 32.51
2019-04-09 04:00 | 49.76 | 39
2019-04-09 04:30 | 40.96 | 26.92
2019-04-09 05:00 | 63.93 | 56.03
2019-04-09 05:30 | 104.27 | 99.41
2019-04-09 06:00 | 118.15 | 114.25
2019-04-09 06:30 | 118.56 | 115.11
2019-04-09 07:00 | 128.7 | 126.48
2019-04-09 07:30 | 131.36 | 131.31
2019-04-09 08:00 | 134.05 | 133.95
2019-04-09 08:30 | 144.32 | 143.82
2019-04-09 09:00 | 134.61 | 131.93
2019-04-09 09:30 | 57.88 | 21.26
2019-04-09 10:00 | 65.26 | 18.12
2019-04-09 10:30 | 57.44 | 34.34
2019-04-09 11:00 | 49.91 | 13.04
2019-04-09 11:30 | 52.93 | -15.74
2019-04-09 12:00 | 53.63 | 17.92
2019-04-09 12:30 | 56.75 | 24.84
2019-04-09 13:00 | 57.37 | 23.84
2019-04-09 13:30 | 69.48 | 45.95
2019-04-09 14:00 | 82.78 | 65.46
2019-04-09 14:30 | 86.27 | 76.84
2019-04-09 15:00 | 83.89 | 77.31
2019-04-09 15:30 | 112.72 | 108.43
2019-04-09 16:00 | 122.55 | 119
2019-04-09 16:30 | 101.49 | 97.5
2019-04-09 17:00 | 159.37 | 157.43
2019-04-09 17:30 | 202.21 | 201.17
2019-04-09 18:00 | 175.28 | 174.03
2019-04-09 18:30 | 160.67 | 159.47
2019-04-09 19:00 | 156.14 | 155.03
2019-04-09 19:30 | 125.94 | 125.61
2019-04-09 20:00 | 137.34 | 136.28
2019-04-09 20:30 | 133.65 | 132.36
2019-04-09 21:00 | 116.78 | 114.77
2019-04-09 21:30 | 134.38 | 132.3
2019-04-09 22:00 | 116.02 | 115.4
2019-04-09 22:30 | 77.96 | 76.92
2019-04-09 23:00 | 101.49 | 100.36
2019-04-09 23:30 | 85.13 | 83.66
2019-04-10 | 58.97 | 56.67
2019-04-10 00:30 | 38.32 | 34.08
2019-04-10 01:00 | 25.75 | 18.05
2019-04-10 01:30 | 18.77 | -2.45
2019-04-10 02:00 | 24.03 | -14.83
2019-04-10 02:30 | 26.37 | -18.15
2019-04-10 03:00 | 42.89 | -38.82
2019-04-10 03:30 | 50.55 | -47.44
2019-04-10 04:00 | 52.45 | -49.58
2019-04-10 04:30 | 24.49 | -16.67
2019-04-10 05:00 | 23.77 | 14.36
2019-04-10 05:30 | 53.78 | 50.69
2019-04-10 06:00 | 81.82 | 80.21
2019-04-10 06:30 | 93.33 | 92.52
2019-04-10 07:00 | 89.28 | 88.91
2019-04-10 07:30 | 116.54 | 116.52
2019-04-10 08:00 | 148.81 | 148.7
2019-04-10 08:30 | 157.64 | 151.56
2019-04-10 09:00 | 112.7 | 95.9
2019-04-10 09:30 | 77.07 | 43.18
2019-04-10 10:00 | 72.38 | 32.81
2019-04-10 10:30 | 89.17 | 60.68
2019-04-10 11:00 | 88 | 57.89
2019-04-10 11:30 | 82 | 48.57
2019-04-10 12:00 | 90.92 | 62.19
2019-04-10 12:30 | 80.4 | 46.83
2019-04-10 13:00 | 86.68 | 58.33
2019-04-10 13:30 | 101.03 | 78.28
2019-04-10 14:00 | 115.14 | 95.49
2019-04-10 14:30 | 116.55 | 96.85
2019-04-10 15:00 | 118.71 | 98.61
2019-04-10 15:30 | 120.67 | 101.57
2019-04-10 16:00 | 124.28 | 106.67
2019-04-10 16:30 | 123.96 | 109.17
2019-04-10 17:00 | 118.21 | 105.31
2019-04-10 17:30 | 102.84 | 89.08
2019-04-10 18:00 | 80.9 | 62.98
2019-04-10 18:30 | 99.11 | 86.07
2019-04-10 19:00 | 114.29 | 107.33
2019-04-10 19:30 | 115.72 | 113.61
2019-04-10 20:00 | 99.95 | 97.75
2019-04-10 20:30 | 104.63 | 103.9
2019-04-10 21:00 | 107.2 | 106.85
2019-04-10 21:30 | 102.21 | 101.77
2019-04-10 22:00 | 92.58 | 91.84
2019-04-10 22:30 | 72.3 | 71.02
2019-04-10 23:00 | 79.6 | 78.03
2019-04-10 23:30 | 77.66 | 75.76
2019-04-11 | 37.07 | 32.85
2019-04-11 00:30 | 42.88 | 38.49
2019-04-11 01:00 | 25.77 | 16.67
2019-04-11 01:30 | 21.23 | 7.57
2019-04-11 02:00 | 20.46 | -6.78
2019-04-11 02:30 | 21.93 | -9.98
2019-04-11 03:00 | 22.73 | -11.95
2019-04-11 03:30 | 20.44 | 1.24
2019-04-11 04:00 | 20.71 | 0.63
2019-04-11 04:30 | 31.41 | 23.4
2019-04-11 05:00 | 34.65 | 28.32
2019-04-11 05:30 | 60.25 | 57.47
2019-04-11 06:00 | 41.85 | 38.76
2019-04-11 06:30 | 79.2 | 78.06
2019-04-11 07:00 | 108.52 | 108.1
2019-04-11 07:30 | 100.31 | 100.17
2019-04-11 08:00 | 104.04 | 104.04
2019-04-11 08:30 | 120.27 | 120.12
2019-04-11 09:00 | 49.73 | 26.45
2019-04-11 09:30 | 79.98 | 53.42
2019-04-11 10:00 | 79.9 | 53.1
2019-04-11 10:30 | 87.98 | 66.19
2019-04-11 11:00 | 87.11 | 76
2019-04-11 11:30 | 77.12 | 67.43
2019-04-11 12:00 | 87.53 | 87.05
2019-04-11 12:30 | 70.25 | 69.56
2019-04-11 13:00 | 47.04 | 43.93
2019-04-11 13:30 | 48.2 | 36.72
2019-04-11 14:00 | 40.88 | 24.89
2019-04-11 14:30 | 65.35 | 14.77
2019-04-11 15:00 | 75.42 | 43.89
2019-04-11 15:30 | 88.05 | 65.99
2019-04-11 16:00 | 95.48 | 76.99
2019-04-11 16:30 | 93.44 | 76.14
2019-04-11 17:00 | 116.78 | 104.32
2019-04-11 17:30 | 128.46 | 118.21
2019-04-11 18:00 | 123.14 | 112.31
2019-04-11 18:30 | 125.99 | 115.26
2019-04-11 19:00 | 137.6 | 129.06
2019-04-11 19:30 | 127.51 | 124.81
2019-04-11 20:00 | 132.61 | 130.43
2019-04-11 20:30 | 115.78 | 113.88
2019-04-11 21:00 | 88.15 | 87.86
2019-04-11 21:30 | 71.82 | 70.25
2019-04-11 22:00 | 19.83 | -15.79
2019-04-11 22:30 | 13.36 | -3.64
2019-04-11 23:00 | 35.69 | -33.33
2019-04-11 23:30 | 73.68 | -73.56
2019-04-12 | 81.64 | -81.46
2019-04-12 00:30 | 83.47 | -83.03
2019-04-12 01:00 | 50.44 | -47.63
2019-04-12 01:30 | 28.31 | -19.91
2019-04-12 02:00 | 40.43 | -35.55
2019-04-12 02:30 | 75.99 | -74.36
2019-04-12 03:00 | 58.18 | -55.54
2019-04-12 03:30 | 39.5 | -34.13
2019-04-12 04:00 | 56.37 | -52.52
2019-04-12 04:30 | 31.17 | -20.18
2019-04-12 05:00 | 30.01 | 2.84
2019-04-12 05:30 | 35.82 | 15.81
2019-04-12 06:00 | 43.94 | 31.14
2019-04-12 06:30 | 53.75 | 46.14
2019-04-12 07:00 | 51.28 | 45
2019-04-12 07:30 | 30.27 | 28.66
2019-04-12 08:00 | 50.1 | -43.95
2019-04-12 08:30 | 61.05 | -25.23
2019-04-12 09:00 | 61.58 | -19.86
2019-04-12 09:30 | 63.75 | -19.69
2019-04-12 10:00 | 75.85 | -41.72
2019-04-12 10:30 | 102.04 | -74.32
2019-04-12 11:00 | 92.03 | -60.95
2019-04-12 11:30 | 63.12 | -6.66
2019-04-12 12:00 | 80.43 | -48.58
2019-04-12 12:30 | 81.26 | -50.47
2019-04-12 13:00 | 98.57 | -73.82
2019-04-12 13:30 | 68.96 | -32.75
2019-04-12 14:00 | 51.58 | -18.01
2019-04-12 14:30 | 51.08 | -30.52
2019-04-12 15:00 | 41.67 | 19.32
2019-04-12 15:30 | 52.93 | 39.82
2019-04-12 16:00 | 54.23 | 43.33
2019-04-12 16:30 | 54.09 | 43.54
2019-04-12 17:00 | 78.99 | 71.29
2019-04-12 17:30 | 93.27 | 87.08
2019-04-12 18:00 | 89.27 | 82.35
2019-04-12 18:30 | 96.62 | 90.09
2019-04-12 19:00 | 99.04 | 93.3
2019-04-12 19:30 | 84.4 | 78.69
2019-04-12 20:00 | 77.12 | 71.89
2019-04-12 20:30 | 69.65 | 68.19
2019-04-12 21:00 | 54.55 | 54.23
2019-04-12 21:30 | 54.57 | 54.01
2019-04-12 22:00 | 34.51 | 33.18
2019-04-12 22:30 | 39.67 | 37.7
2019-04-12 23:00 | 32.19 | 29.11
2019-04-12 23:30 | 48.01 | -47.47
2019-04-13 | 74.76 | -74.72
2019-04-13 00:30 | 45.29 | -43.33
2019-04-13 01:00 | 25.69 | -20.46
2019-04-13 01:30 | 31.19 | -26.68
2019-04-13 02:00 | 42.01 | -38.79
2019-04-13 02:30 | 60.62 | -58.91
2019-04-13 03:00 | 80.93 | -80.77
2019-04-13 03:30 | 72.51 | -72.12
2019-04-13 04:00 | 78.87 | -78.63
2019-04-13 04:30 | 43.13 | -40.36
2019-04-13 05:00 | 28.4 | -23.59
2019-04-13 05:30 | 35.63 | -32.01
2019-04-13 06:00 | 38.26 | -35.2
2019-04-13 06:30 | 41.71 | -39.23
2019-04-13 07:00 | 71.76 | -71.42
2019-04-13 07:30 | 87.88 | -87.8
2019-04-13 08:00 | 89.7 | -89.48
2019-04-13 08:30 | 92.2 | -90.5
2019-04-13 09:00 | 99.71 | -94.46
2019-04-13 09:30 | 105.43 | -99.92
2019-04-13 10:00 | 109 | -103.37
2019-04-13 10:30 | 102.48 | -96.26
2019-04-13 11:00 | 103.61 | -97.18
2019-04-13 11:30 | 95.03 | -84.29
2019-04-13 12:00 | 115.68 | -106.67
2019-04-13 12:30 | 98.95 | -88.84
2019-04-13 13:00 | 95.96 | -84.85
2019-04-13 13:30 | 94.55 | -82.89
2019-04-13 14:00 | 96.68 | -85.51
2019-04-13 14:30 | 73.67 | -61.27
2019-04-13 15:00 | 72.96 | -60.93
2019-04-13 15:30 | 92.05 | -82.45
2019-04-13 16:00 | 85.79 | -75.7
2019-04-13 16:30 | 49.91 | -31.86
2019-04-13 17:00 | 52.45 | 40.84
2019-04-13 17:30 | 72.44 | 64.81
2019-04-13 18:00 | 98.4 | 92.37
2019-04-13 18:30 | 128.19 | 123.56
2019-04-13 19:00 | 123.61 | 119.23
2019-04-13 19:30 | 99.46 | 94.74
2019-04-13 20:00 | 71.89 | 69.68
2019-04-13 20:30 | 59.19 | 59.02
2019-04-13 21:00 | 33.76 | 33.32
2019-04-13 21:30 | 29.5 | 28.64
2019-04-13 22:00 | 21.93 | 20.24
2019-04-13 22:30 | 43.77 | 42.46
2019-04-13 23:00 | 47.2 | 45.52
2019-04-13 23:30 | 38.94 | 36.18
2019-04-14 | 26.75 | 20.59
2019-04-14 00:30 | 25.27 | 16.99
2019-04-14 01:00 | 19.48 | 2.34
2019-04-14 01:30 | 26.2 | -18.36
2019-04-14 02:00 | 59.88 | -58.91
2019-04-14 02:30 | 66.11 | -65.76
2019-04-14 03:00 | 60.05 | -59.62
2019-04-14 03:30 | 60.62 | -59.17
2019-04-14 04:00 | 52.51 | -50.29
2019-04-14 04:30 | 50.9 | -49.04
2019-04-14 05:00 | 29.41 | -24.15
2019-04-14 05:30 | 25.91 | -17.47
2019-04-14 06:00 | 31.7 | -26.27
2019-04-14 06:30 | 30.82 | -25.03
2019-04-14 07:00 | 30.61 | -25.85
2019-04-14 07:30 | 42.69 | -41.7
2019-04-14 08:00 | 83.01 | -82.84
2019-04-14 08:30 | 90.5 | -89.8
2019-04-14 09:00 | 89.63 | -89.02
2019-04-14 09:30 | 95.97 | -95.44
2019-04-14 10:00 | 95.75 | -93.87
2019-04-14 10:30 | 99.44 | -95.02
2019-04-14 11:00 | 99.53 | -95.1
2019-04-14 11:30 | 88.95 | -83.62
2019-04-14 12:00 | 85.94 | -80.51
2019-04-14 12:30 | 95.26 | -90.53
2019-04-14 13:00 | 88.8 | -85.84
2019-04-14 13:30 | 107.43 | -106.3
2019-04-14 14:00 | 87.2 | -85.98
2019-04-14 14:30 | 80.07 | -78.65
2019-04-14 15:00 | 90 | -86.5
2019-04-14 15:30 | 102.89 | -99.33
2019-04-14 16:00 | 58.74 | -57.5
2019-04-14 16:30 | 14.79 | 12.26
2019-04-14 17:00 | 33.73 | 32.09
2019-04-14 17:30 | 65.45 | 64.75
2019-04-14 18:00 | 91.66 | 91.27
2019-04-14 18:30 | 96.52 | 96.2
2019-04-14 19:00 | 96.72 | 96.4
2019-04-14 19:30 | 75.35 | 75.03
2019-04-14 20:00 | 52.9 | 52.63
2019-04-14 20:30 | 52.99 | 52.55
2019-04-14 21:00 | 20.8 | 19.65
2019-04-14 21:30 | 37.54 | -37.41
2019-04-14 22:00 | 80.8 | -80.56
2019-04-14 22:30 | 43.1 | -42.95
2019-04-14 23:00 | 30.75 | -29.55
2019-04-14 23:30 | 21.72 | -18.49
2019-04-15 | 19.54 | -11.69
2019-04-15 00:30 | 25.43 | -19.34
2019-04-15 01:00 | 21.19 | -19.62
2019-04-15 01:30 | 54.08 | -53.9
2019-04-15 02:00 | 63.84 | -63.84
2019-04-15 02:30 | 77.21 | -76.01
2019-04-15 03:00 | 84.02 | -81.35
2019-04-15 03:30 | 82.37 | -79.85
2019-04-15 04:00 | 81.23 | -78.79
2019-04-15 04:30 | 39.42 | -39.34
2019-04-15 05:00 | 18.21 | -16.57
2019-04-15 05:30 | 14.87 | -10.37
2019-04-15 06:00 | 15.33 | -9.96
2019-04-15 06:30 | 18.77 | 13.43
2019-04-15 07:00 | 25.38 | 23.53
2019-04-15 07:30 | 34.05 | -32.94
2019-04-15 08:00 | 94.96 | -86.93
2019-04-15 08:30 | 110.18 | -88.35
2019-04-15 09:00 | 110.54 | -86.55
2019-04-15 09:30 | 122.45 | -102.47
2019-04-15 10:00 | 122.07 | -104.17
2019-04-15 10:30 | 125.5 | -107.81
2019-04-15 11:00 | 122.53 | -104.69
2019-04-15 11:30 | 123.26 | -106.29
2019-04-15 12:00 | 116.95 | -96.7
2019-04-15 12:30 | 123.96 | -106.69
2019-04-15 13:00 | 98.97 | -76.66
2019-04-15 13:30 | 58.89 | -33.82
2019-04-15 14:00 | 39.27 | 9.97
2019-04-15 14:30 | 46.23 | 26.89
2019-04-15 15:00 | 44.51 | 24.62
2019-04-15 15:30 | 71.52 | 62.26
2019-04-15 16:00 | 106.4 | 100.76
2019-04-15 16:30 | 81.73 | 74.99
2019-04-15 17:00 | 95.88 | 90.8
2019-04-15 17:30 | 106.24 | 102.18
2019-04-15 18:00 | 143.44 | 140.15
2019-04-15 18:30 | 169.63 | 166.97
2019-04-15 19:00 | 180.2 | 178.08
2019-04-15 19:30 | 154.38 | 152.69
2019-04-15 20:00 | 151.28 | 150.9
2019-04-15 20:30 | 129.32 | 128.75
2019-04-15 21:00 | 86.01 | 85.57
2019-04-15 21:30 | 72.68 | 72.37
2019-04-15 22:00 | 25.84 | 25.47
2019-04-15 22:30 | 29.04 | 26.79
2019-04-15 23:00 | 34.72 | 31.76
2019-04-15 23:30 | 36.78 | -36.77
2019-04-16 | 77.19 | -76.67
2019-04-16 00:30 | 61.99 | -61.78
2019-04-16 01:00 | 31.12 | -28.24
2019-04-16 01:30 | 25.6 | -21.08
2019-04-16 02:00 | 27.56 | -23.32
2019-04-16 02:30 | 30.42 | -26.56
2019-04-16 03:00 | 32.27 | -28.76
2019-04-16 03:30 | 24.06 | -17.75
2019-04-16 04:00 | 16.65 | -13.78
2019-04-16 04:30 | 14.42 | 2.2
2019-04-16 05:00 | 25.22 | 17.34
2019-04-16 05:30 | 32.82 | 27.17
2019-04-16 06:00 | 24.38 | 18.24
2019-04-16 06:30 | 50.66 | 48.05
2019-04-16 07:00 | 54.88 | 52.66
2019-04-16 07:30 | 40.32 | 39.68
2019-04-16 08:00 | 5.41 | 5.22
2019-04-16 08:30 | 20.43 | -18.69
2019-04-16 09:00 | 65.74 | -59.44
2019-04-16 09:30 | 86.58 | -81.03
2019-04-16 10:00 | 65.29 | -57.83
2019-04-16 10:30 | 48.34 | -33.71
2019-04-16 11:00 | 49.89 | -33.96
2019-04-16 11:30 | 33.84 | -8.93
2019-04-16 12:00 | 49.38 | -34.14
2019-04-16 12:30 | 49.95 | -34.13
2019-04-16 13:00 | 33.74 | -6.06
2019-04-16 13:30 | 46.13 | -29.18
2019-04-16 14:00 | 35.54 | -7.36
2019-04-16 14:30 | 31.96 | 10.33
2019-04-16 15:00 | 36.52 | 25.28
2019-04-16 15:30 | 59.7 | 54.46
2019-04-16 16:00 | 54.34 | 48.82
2019-04-16 16:30 | 73.37 | 69.79
2019-04-16 17:00 | 100.95 | 98.86
2019-04-16 17:30 | 105.21 | 103.56
2019-04-16 18:00 | 138.05 | 136.61
2019-04-16 18:30 | 144.58 | 143.26
2019-04-16 19:00 | 142.99 | 142.46
2019-04-16 19:30 | 120.94 | 120.91
2019-04-16 20:00 | 104.32 | 103.94
2019-04-16 20:30 | 115.95 | 115.64
2019-04-16 21:00 | 95.16 | 95.01
2019-04-16 21:30 | 92.68 | 92.24
2019-04-16 22:00 | 68.66 | 67.75
2019-04-16 22:30 | 75.26 | 74.12
2019-04-16 23:00 | 81.72 | 80.29
2019-04-16 23:30 | 48.72 | 46.04
2019-04-17 | 21.91 | 14.91
2019-04-17 00:30 | 27.03 | 16.39
2019-04-17 01:00 | 25.69 | -15.64
2019-04-17 01:30 | 19.94 | -4.76
2019-04-17 02:00 | 23.59 | -14.33
2019-04-17 02:30 | 27.5 | -19.92
2019-04-17 03:00 | 21 | -8.95
2019-04-17 03:30 | 20.23 | -1.9
2019-04-17 04:00 | 34.58 | 27.25
2019-04-17 04:30 | 49.37 | 43.47
2019-04-17 05:00 | 56.76 | 51.85
2019-04-17 05:30 | 57.1 | 53.43
2019-04-17 06:00 | 47.31 | 43.96
2019-04-17 06:30 | 50.28 | 48.16
2019-04-17 07:00 | 68.65 | 68.15
2019-04-17 07:30 | 78.4 | 78.17
2019-04-17 08:00 | 87.69 | 86.97
2019-04-17 08:30 | 54.57 | 54.54
2019-04-17 09:00 | 56.66 | -47.87
2019-04-17 09:30 | 63.05 | -52.73
2019-04-17 10:00 | 64.91 | -53.16
2019-04-17 10:30 | 70.51 | -57.64
2019-04-17 11:00 | 63.67 | -47.51
2019-04-17 11:30 | 61.8 | -44.74
2019-04-17 12:00 | 56.48 | -41.47
2019-04-17 12:30 | 33.68 | -9.75
2019-04-17 13:00 | 49.68 | -35.99
2019-04-17 13:30 | 52.54 | -45.78
2019-04-17 14:00 | 20.01 | -10.2
2019-04-17 14:30 | 57.19 | -45.15
2019-04-17 15:00 | 25.63 | 14.19
2019-04-17 15:30 | 24.8 | 20.33
2019-04-17 16:00 | 29.47 | 27.71
2019-04-17 16:30 | 52.5 | 52.23
2019-04-17 17:00 | 85.41 | 85.38
2019-04-17 17:30 | 101.38 | 101.35
2019-04-17 18:00 | 115.8 | 115.8
2019-04-17 18:30 | 122.72 | 122.65
2019-04-17 19:00 | 138.57 | 138.46
2019-04-17 19:30 | 133.07 | 132.96
2019-04-17 20:00 | 122.45 | 122.43
2019-04-17 20:30 | 99.46 | 99.23
2019-04-17 21:00 | 69.72 | 67.27
2019-04-17 21:30 | 59.3 | 57.39
2019-04-17 22:00 | 40.05 | 38.69
2019-04-17 22:30 | 55.33 | 53.76
2019-04-17 23:00 | 60.22 | 58.36
2019-04-17 23:30 | 27.46 | 22.68
2019-04-18 | 34.42 | -31.27
2019-04-18 00:30 | 20 | 3.49
2019-04-18 01:00 | 28.75 | 18.35
2019-04-18 01:30 | 33.98 | 24.96
2019-04-18 02:00 | 33.81 | 24.69
2019-04-18 02:30 | 27.46 | 14.73
2019-04-18 03:00 | 22.66 | 0.25
2019-04-18 03:30 | 24.38 | 9.05
2019-04-18 04:00 | 28.93 | 18.72
2019-04-18 04:30 | 36.71 | 29.39
2019-04-18 05:00 | 50.95 | 46.18
2019-04-18 05:30 | 78.86 | 76.02
2019-04-18 06:00 | 96.81 | 94.84
2019-04-18 06:30 | 80.26 | 78.36
2019-04-18 07:00 | 61.48 | 60.21
2019-04-18 07:30 | 37.52 | 37.14
2019-04-18 08:00 | 45.58 | -44.83
2019-04-18 08:30 | 72.11 | -69.42
2019-04-18 09:00 | 77.37 | -74.92
2019-04-18 09:30 | 85.76 | -81.9
2019-04-18 10:00 | 69.99 | -68.13
2019-04-18 10:30 | 89.85 | -87.33
2019-04-18 11:00 | 89.29 | -84.06
2019-04-18 11:30 | 32.43 | -15.43
2019-04-18 12:00 | 28.4 | 4.48
2019-04-18 12:30 | 65.23 | -56
2019-04-18 13:00 | 90.69 | -82.67
2019-04-18 13:30 | 73.17 | -64.59
2019-04-18 14:00 | 33.56 | -14.6
2019-04-18 14:30 | 31.43 | 13.95
2019-04-18 15:00 | 58.8 | -47.45
2019-04-18 15:30 | 33.44 | 19.47
2019-04-18 16:00 | 64.33 | 60.18
2019-04-18 16:30 | 70.68 | 67.51
2019-04-18 17:00 | 99.78 | 97.89
2019-04-18 17:30 | 96.61 | 95.05
2019-04-18 18:00 | 117.85 | 116.27
2019-04-18 18:30 | 131.83 | 130.53
2019-04-18 19:00 | 130.17 | 129.1
2019-04-18 19:30 | 136.29 | 136.22
2019-04-18 20:00 | 129.8 | 129.79
2019-04-18 20:30 | 117.68 | 117.65
2019-04-18 21:00 | 77.58 | 77.51
2019-04-18 21:30 | 83.19 | 82.93
2019-04-18 22:00 | 102.82 | 102.33
2019-04-18 22:30 | 110.58 | 109.85
2019-04-18 23:00 | 131.51 | 130.68
2019-04-18 23:30 | 108.65 | 107.37
2019-04-19 | 63.44 | 60.77
2019-04-19 00:30 | 57.28 | 53.35
2019-04-19 01:00 | 42.26 | 36.09
2019-04-19 01:30 | 28.82 | 18.07
2019-04-19 02:00 | 24.88 | 9.51
2019-04-19 02:30 | 23.54 | -6.84
2019-04-19 03:00 | 28.03 | -18.34
2019-04-19 03:30 | 25.56 | -11.45
2019-04-19 04:00 | 28.25 | -16.5
2019-04-19 04:30 | 24.27 | -7.39
2019-04-19 05:00 | 24.47 | 7.52
2019-04-19 05:30 | 25.39 | 11.04
2019-04-19 06:00 | 23.5 | 6.97
2019-04-19 06:30 | 26.04 | 13.22
2019-04-19 07:00 | 26.85 | 15.73
2019-04-19 07:30 | 21.86 | -14.29
2019-04-19 08:00 | 66.33 | -66.31
2019-04-19 08:30 | 48.38 | -48.35
2019-04-19 09:00 | 62.56 | -62.48
2019-04-19 09:30 | 69.18 | -68.76
2019-04-19 10:00 | 73.38 | -72.92
2019-04-19 10:30 | 56.69 | -56.15
2019-04-19 11:00 | 15.21 | 15.02
2019-04-19 11:30 | 20.38 | 20.37
2019-04-19 12:00 | 20.61 | 20.34
2019-04-19 12:30 | 30.63 | 29.92
2019-04-19 13:00 | 20.08 | 19.21
2019-04-19 13:30 | 15.92 | 15.07
2019-04-19 14:00 | 12.88 | 11.77
2019-04-19 14:30 | 43.05 | -43.05
2019-04-19 15:00 | 37.15 | 36.41
2019-04-19 15:30 | 40.03 | 39.14
2019-04-19 16:00 | 51.38 | 50.7
2019-04-19 16:30 | 40.24 | 39.49
2019-04-19 17:00 | 66.46 | 66.24
2019-04-19 17:30 | 83.78 | 83.6
2019-04-19 18:00 | 105.85 | 105.42
2019-04-19 18:30 | 114.75 | 113.35
2019-04-19 19:00 | 115.09 | 113.66
2019-04-19 19:30 | 121.75 | 119.93
2019-04-19 20:00 | 127.22 | 124.75
2019-04-19 20:30 | 105.87 | 104.66
2019-04-19 21:00 | 98.85 | 98.04
2019-04-19 21:30 | 88.2 | 87.07
2019-04-19 22:00 | 78.45 | 76.96
2019-04-19 22:30 | 91.23 | 89.83
2019-04-19 23:00 | 84.95 | 83.1
2019-04-19 23:30 | 47.11 | 43.38
2019-04-20 | 21.91 | 9.63
2019-04-20 00:30 | 22.19 | 7.57
2019-04-20 01:00 | 22.71 | 5.76
2019-04-20 01:30 | 22.66 | 1.51
2019-04-20 02:00 | 23.59 | -6.98
2019-04-20 02:30 | 24.43 | -7.85
2019-04-20 03:00 | 25.22 | -10.92
2019-04-20 03:30 | 24.73 | -9.1
2019-04-20 04:00 | 23.75 | -0.34
2019-04-20 04:30 | 25.99 | 1.42
2019-04-20 05:00 | 29.47 | 11.74
2019-04-20 05:30 | 29.31 | 13.63
2019-04-20 06:00 | 27.66 | 11.82
2019-04-20 06:30 | 31.11 | 18.81
2019-04-20 07:00 | 31.34 | 21.27
2019-04-20 07:30 | 36.06 | 30.14
2019-04-20 08:00 | 19.24 | -13.06
2019-04-20 08:30 | 23.63 | -22.21
2019-04-20 09:00 | 22.47 | 18.08
2019-04-20 09:30 | 54.29 | 51.91
2019-04-20 10:00 | 51.89 | 49.22
2019-04-20 10:30 | 56.06 | 53.38
2019-04-20 11:00 | 39.46 | 35.31
2019-04-20 11:30 | 47.62 | 44.24
2019-04-20 12:00 | 58.85 | 56.11
2019-04-20 12:30 | 47.81 | 44.77
2019-04-20 13:00 | 41.91 | 37.89
2019-04-20 13:30 | 47.45 | 43.94
2019-04-20 14:00 | 42 | 37.94
2019-04-20 14:30 | 60 | 57.48
2019-04-20 15:00 | 53.3 | 50.55
2019-04-20 15:30 | 77.8 | 76.23
2019-04-20 16:00 | 96.37 | 95.08
2019-04-20 16:30 | 78.2 | 76.58
2019-04-20 17:00 | 92.38 | 90.88
2019-04-20 17:30 | 127.43 | 126.19
2019-04-20 18:00 | 153.38 | 145.23
2019-04-20 18:30 | 144.12 | 140.13
2019-04-20 19:00 | 144.55 | 141.84
2019-04-20 19:30 | 138.79 | 136.39
2019-04-20 20:00 | 145.07 | 144.98
2019-04-20 20:30 | 149.11 | 148.94
2019-04-20 21:00 | 153.23 | 152.96
2019-04-20 21:30 | 160.15 | 159.77
2019-04-20 22:00 | 138.57 | 137.94
2019-04-20 22:30 | 145.02 | 144.32
2019-04-20 23:00 | 140.82 | 139.81
2019-04-20 23:30 | 86.99 | 85.04
2019-04-21 | 64.27 | 61.17
2019-04-21 00:30 | 55.57 | 51.22
2019-04-21 01:00 | 60.26 | 54.37
2019-04-21 01:30 | 53.85 | 47.3
2019-04-21 02:00 | 33.79 | 21.92
2019-04-21 02:30 | 36.81 | 27.07
2019-04-21 03:00 | 28.41 | 13.2
2019-04-21 03:30 | 26.13 | 7.35
2019-04-21 04:00 | 27.54 | -12.47
2019-04-21 04:30 | 26.2 | 7.48
2019-04-21 05:00 | 24.59 | 0.23
2019-04-21 05:30 | 24.66 | 0.65
2019-04-21 06:00 | 24.75 | 5.97
2019-04-21 06:30 | 29.46 | 17.03
2019-04-21 07:00 | 36.02 | 26.88
2019-04-21 07:30 | 28.32 | 19.34
2019-04-21 08:00 | 24.25 | 17.62
2019-04-21 08:30 | 15.32 | 10.85
2019-04-21 09:00 | 39.73 | -39.68
2019-04-21 09:30 | 6.01 | -5.41
2019-04-21 10:00 | 9.95 | -9.62
2019-04-21 10:30 | 6.04 | -5.7
2019-04-21 11:00 | 60.45 | -60.26
2019-04-21 11:30 | 5.65 | -5.63
2019-04-21 12:00 | 13.86 | 13.84
2019-04-21 12:30 | 9.77 | 9.65
2019-04-21 13:00 | 16.36 | -16.3
2019-04-21 13:30 | 2.61 | -1.83
2019-04-21 14:00 | 6.74 | 6.36
2019-04-21 14:30 | 74.31 | -74.04
2019-04-21 15:00 | 17.87 | -17.86
2019-04-21 15:30 | 20.98 | -20.93
2019-04-21 16:00 | 28.66 | 28.66
2019-04-21 16:30 | 29.97 | 27.57
2019-04-21 17:00 | 61.25 | 58.14
2019-04-21 17:30 | 75.47 | 73.06
2019-04-21 18:00 | 89.32 | 87.79
2019-04-21 18:30 | 95.61 | 94.22
2019-04-21 19:00 | 100.16 | 99.45
2019-04-21 19:30 | 98.69 | 98.66
2019-04-21 20:00 | 97.38 | 94.69
2019-04-21 20:30 | 98.64 | 95.18
2019-04-21 21:00 | 124.77 | 121.98
2019-04-21 21:30 | 123.89 | 120.92
2019-04-21 22:00 | 110.86 | 106.13
2019-04-21 22:30 | 114.75 | 110.08
2019-04-21 23:00 | 113.16 | 108.14
2019-04-21 23:30 | 79.68 | 72.84
2019-04-22 | 54.42 | 44.03
2019-04-22 00:30 | 37.09 | 27.98
2019-04-22 01:00 | 22.15 | 17.36
2019-04-22 01:30 | 14.43 | -8.56
2019-04-22 02:00 | 15.1 | -11.59
2019-04-22 02:30 | 14.59 | -11.37
2019-04-22 03:00 | 13.42 | -9.84
2019-04-22 03:30 | 9.46 | -1.55
2019-04-22 04:00 | 10.34 | -4.98
2019-04-22 04:30 | 20.41 | -18.76
2019-04-22 05:00 | 22.21 | -20.1
2019-04-22 05:30 | 13.14 | -7.51
2019-04-22 06:00 | 11.11 | 0.84
2019-04-22 06:30 | 16.41 | 12.53
2019-04-22 07:00 | 22.71 | 19.66
2019-04-22 07:30 | 19.92 | 16.24
2019-04-22 08:00 | 55.8 | -55.8
2019-04-22 08:30 | 36.24 | -34.08
2019-04-22 09:00 | 33.43 | -30.79
2019-04-22 09:30 | 9.97 | -1.78
2019-04-22 10:00 | 5.39 | 4.61
2019-04-22 10:30 | 38.87 | 38.84
2019-04-22 11:00 | 30.58 | 30.56
2019-04-22 11:30 | 4.37 | -4.05
2019-04-22 12:00 | 22.76 | 22.71
2019-04-22 12:30 | 11.98 | 11.84
2019-04-22 13:00 | 9.3 | 9.17
2019-04-22 13:30 | 14.11 | 13.91
2019-04-22 14:00 | 35.78 | 35.71
2019-04-22 14:30 | 11.23 | 11.15
2019-04-22 15:00 | 31.7 | 31.66
2019-04-22 15:30 | 46.79 | 46.77
2019-04-22 16:00 | 64.42 | 64.4
2019-04-22 16:30 | 77.71 | 76.26
2019-04-22 17:00 | 92.31 | 90.38
2019-04-22 17:30 | 126.45 | 125.31
2019-04-22 18:00 | 141.15 | 140.48
2019-04-22 18:30 | 144.7 | 144.06
2019-04-22 19:00 | 145.33 | 144.65
2019-04-22 19:30 | 133.22 | 133.03
2019-04-22 20:00 | 138.8 | 138.57
2019-04-22 20:30 | 119.26 | 118.12
2019-04-22 21:00 | 94.94 | 90.72
2019-04-22 21:30 | 87.85 | 83.02
2019-04-22 22:00 | 87.88 | 82.58
2019-04-22 22:30 | 78.33 | 72.47
2019-04-22 23:00 | 86.1 | 80.44
2019-04-22 23:30 | 70.1 | 63.77
2019-04-23 | 48.66 | 39.01
2019-04-23 00:30 | 39.58 | 27.4
2019-04-23 01:00 | 29.79 | 5.35
2019-04-23 01:30 | 29.34 | -1.07
2019-04-23 02:00 | 27.07 | -4.43
2019-04-23 02:30 | 22.67 | -20.17
2019-04-23 03:00 | 21.58 | -19.38
2019-04-23 03:30 | 15.22 | -11.38
2019-04-23 04:00 | 15.93 | -11.92
2019-04-23 04:30 | 29.84 | 27.18
2019-04-23 05:00 | 25.54 | 21.97
2019-04-23 05:30 | 44.36 | 41.92
2019-04-23 06:00 | 64.41 | 62.53
2019-04-23 06:30 | 97.41 | 96.03
2019-04-23 07:00 | 107.54 | 106.16
2019-04-23 07:30 | 111.4 | 109.07
2019-04-23 08:00 | 70.64 | 67.43
2019-04-23 08:30 | 50.79 | 47.84
2019-04-23 09:00 | 16.61 | 13.09
2019-04-23 09:30 | 34.36 | 33.06
2019-04-23 10:00 | 32.13 | 31.23
2019-04-23 10:30 | 54.73 | 53.97
2019-04-23 11:00 | 49.56 | 48.91
2019-04-23 11:30 | 57.57 | 57.03
2019-04-23 12:00 | 59.28 | 58.82
2019-04-23 12:30 | 54.07 | 53.37
2019-04-23 13:00 | 49.97 | 49.14
2019-04-23 13:30 | 48.97 | 48.15
2019-04-23 14:00 | 63.1 | 62.1
2019-04-23 14:30 | 94.87 | 94.07
2019-04-23 15:00 | 116.83 | 115.79
2019-04-23 15:30 | 125.21 | 123.84
2019-04-23 16:00 | 136.52 | 135.09
2019-04-23 16:30 | 126.31 | 124.63
2019-04-23 17:00 | 133.91 | 132.46
2019-04-23 17:30 | 139.05 | 138.22
2019-04-23 18:00 | 162.65 | 162.5
2019-04-23 18:30 | 154.12 | 154.03
2019-04-23 19:00 | 157.19 | 157.11
2019-04-23 19:30 | 137.36 | 137.22
2019-04-23 20:00 | 126.21 | 125.77
2019-04-23 20:30 | 132.57 | 131.76
2019-04-23 21:00 | 107.51 | 106.35
2019-04-23 21:30 | 103.45 | 102.11
2019-04-23 22:00 | 105.74 | 104.89
2019-04-23 22:30 | 91.57 | 90.63
2019-04-23 23:00 | 98.33 | 97.2
2019-04-23 23:30 | 82.79 | 81.16
2019-04-24 | 51.77 | 48.38
2019-04-24 00:30 | 36.92 | 29.92
2019-04-24 01:00 | 23.33 | 6.94
2019-04-24 01:30 | 23.29 | 4.65
2019-04-24 02:00 | 25.99 | -14.12
2019-04-24 02:30 | 28.97 | -16.81
2019-04-24 03:00 | 33.15 | -14.08
2019-04-24 03:30 | 35.64 | -19.7
2019-04-24 04:00 | 36.71 | -22.08
2019-04-24 04:30 | 33.71 | 12.48
2019-04-24 05:00 | 37.9 | 20.44
2019-04-24 05:30 | 52.66 | 41.61
2019-04-24 06:00 | 78.97 | 71.89
2019-04-24 06:30 | 108.08 | 103.54
2019-04-24 07:00 | 120.03 | 118.56
2019-04-24 07:30 | 127.51 | 127.21
2019-04-24 08:00 | 112.64 | 112.5
2019-04-24 08:30 | 86.95 | 86.94
2019-04-24 09:00 | 74.16 | 73.68
2019-04-24 09:30 | 85.05 | 70.99
2019-04-24 10:00 | 80.55 | 54.76
2019-04-24 10:30 | 94.35 | 72.89
2019-04-24 11:00 | 82.54 | 55.79
2019-04-24 11:30 | 82.9 | 57.26
2019-04-24 12:00 | 83.45 | 57.79
2019-04-24 12:30 | 89.03 | 65.45
2019-04-24 13:00 | 104.35 | 85.18
2019-04-24 13:30 | 106.83 | 88.73
2019-04-24 14:00 | 112.53 | 95.53
2019-04-24 14:30 | 124.28 | 108.87
2019-04-24 15:00 | 125.07 | 110.24
2019-04-24 15:30 | 131.05 | 117.92
2019-04-24 16:00 | 137.57 | 126.47
2019-04-24 16:30 | 135.58 | 124.58
2019-04-24 17:00 | 144.97 | 135.25
2019-04-24 17:30 | 152.02 | 143.13
2019-04-24 18:00 | 152.42 | 142.7
2019-04-24 18:30 | 157.87 | 150.33
2019-04-24 19:00 | 161.71 | 159.22
2019-04-24 19:30 | 141.92 | 141.92
2019-04-24 20:00 | 143.71 | 143.57
2019-04-24 20:30 | 148.64 | 148.46
2019-04-24 21:00 | 121.73 | 121.44
2019-04-24 21:30 | 112.06 | 111.45
2019-04-24 22:00 | 93.78 | 92.76
2019-04-24 22:30 | 102.14 | 100.93
2019-04-24 23:00 | 126.37 | 125.22
2019-04-24 23:30 | 96.54 | 94.69
2019-04-25 | 72.23 | 68.99
2019-04-25 00:30 | 53.22 | 42.99
2019-04-25 01:00 | 42.32 | 24.14
2019-04-25 01:30 | 36.68 | 13.33
2019-04-25 02:00 | 34.05 | 7.82
2019-04-25 02:30 | 33.1 | 4.91
2019-04-25 03:00 | 32.22 | 1.46
2019-04-25 03:30 | 34.34 | 8.86
2019-04-25 04:00 | 47.18 | 33.16
2019-04-25 04:30 | 50.78 | 37.82
2019-04-25 05:00 | 53.3 | 41.17
2019-04-25 05:30 | 55.95 | 44.46
2019-04-25 06:00 | 60.93 | 50.28
2019-04-25 06:30 | 62.54 | 52.48
2019-04-25 07:00 | 74.49 | 66.17
2019-04-25 07:30 | 67 | 57.7
2019-04-25 08:00 | 43.4 | 28.53
2019-04-25 08:30 | 41.56 | 25.99
2019-04-25 09:00 | 43.1 | 28.21
2019-04-25 09:30 | 38.96 | 26.68
2019-04-25 10:00 | 30.76 | 16.93
2019-04-25 10:30 | 28.55 | 13.1
2019-04-25 11:00 | 39.41 | 27.99
2019-04-25 11:30 | 47.64 | 38.87
2019-04-25 12:00 | 69.66 | 64.45
2019-04-25 12:30 | 71.29 | 66.04
2019-04-25 13:00 | 71.87 | 66.5
2019-04-25 13:30 | 81.68 | 77.02
2019-04-25 14:00 | 82.14 | 77.41
2019-04-25 14:30 | 71.42 | 65.96
2019-04-25 15:00 | 68.02 | 62.27
2019-04-25 15:30 | 102.23 | 98.43
2019-04-25 16:00 | 116.93 | 113.64
2019-04-25 16:30 | 142.68 | 139.99
2019-04-25 17:00 | 138.93 | 138.25
2019-04-25 17:30 | 166.18 | 166.12
2019-04-25 18:00 | 186.33 | 186.32
2019-04-25 18:30 | 175.8 | 175.79
2019-04-25 19:00 | 177 | 176.97
2019-04-25 19:30 | 187.34 | 187.24
2019-04-25 20:00 | 184.51 | 184.34
2019-04-25 20:30 | 167.78 | 167.46
2019-04-25 21:00 | 143.65 | 143.1
2019-04-25 21:30 | 134.86 | 134.1
2019-04-25 22:00 | 119.92 | 118.73
2019-04-25 22:30 | 113.91 | 112.44
2019-04-25 23:00 | 111.41 | 109.64
2019-04-25 23:30 | 87.23 | 84.82
2019-04-26 | 55.62 | 51.36
2019-04-26 00:30 | 45.44 | 35.83
2019-04-26 01:00 | 41.99 | 26.98
2019-04-26 01:30 | 35.34 | 10.12
2019-04-26 02:00 | 32.22 | 1.21
2019-04-26 02:30 | 46.7 | 33.34
2019-04-26 03:00 | 53.43 | 51.25
2019-04-26 03:30 | 58.52 | 56.45
2019-04-26 04:00 | 74.04 | 72.49
2019-04-26 04:30 | 91.88 | 90.57
2019-04-26 05:00 | 86.76 | 85.12
2019-04-26 05:30 | 103.65 | 102.11
2019-04-26 06:00 | 121.94 | 120.43
2019-04-26 06:30 | 124.22 | 122.66
2019-04-26 07:00 | 126.49 | 125.29
2019-04-26 07:30 | 125.42 | 124.8
2019-04-26 08:00 | 109.43 | 109.13
2019-04-26 08:30 | 103.18 | 102.14
2019-04-26 09:00 | 90.28 | 87.67
2019-04-26 09:30 | 101.34 | 93.66
2019-04-26 10:00 | 117.81 | 104.72
2019-04-26 10:30 | 157.18 | 147.1
2019-04-26 11:00 | 159.74 | 149.72
2019-04-26 11:30 | 150.99 | 140.26
2019-04-26 12:00 | 144.56 | 133.52
2019-04-26 12:30 | 159.73 | 149.68
2019-04-26 13:00 | 170.68 | 161.28
2019-04-26 13:30 | 168.68 | 159.15
2019-04-26 14:00 | 145.83 | 135.01
2019-04-26 14:30 | 160.48 | 150.39
2019-04-26 15:00 | 194.81 | 186.53
2019-04-26 15:30 | 191.63 | 183.66
2019-04-26 16:00 | 193.34 | 185.61
2019-04-26 16:30 | 205.72 | 198.46
2019-04-26 17:00 | 190.97 | 183.63
2019-04-26 17:30 | 197.52 | 190.59
2019-04-26 18:00 | 206.02 | 198.58
2019-04-26 18:30 | 210.62 | 203.84
2019-04-26 19:00 | 203.98 | 197.6
2019-04-26 19:30 | 187.98 | 184.82
2019-04-26 20:00 | 192.53 | 192.06
2019-04-26 20:30 | 190.78 | 190.45
2019-04-26 21:00 | 176.97 | 176.71
2019-04-26 21:30 | 166.12 | 165.96
2019-04-26 22:00 | 144.87 | 144.79
2019-04-26 22:30 | 150.43 | 150.41
2019-04-26 23:00 | 166.81 | 166.8
2019-04-26 23:30 | 141.2 | 141.06
2019-04-27 | 103.91 | 101.54
2019-04-27 00:30 | 93.55 | 90.56
2019-04-27 01:00 | 79.89 | 75.95
2019-04-27 01:30 | 66.72 | 61.81
2019-04-27 02:00 | 53.41 | 47.15
2019-04-27 02:30 | 49.87 | 42.96
2019-04-27 03:00 | 47.42 | 37.67
2019-04-27 03:30 | 50.87 | 38.34
2019-04-27 04:00 | 48.33 | 35.13
2019-04-27 04:30 | 49.37 | 35.97
2019-04-27 05:00 | 49.07 | 35.36
2019-04-27 05:30 | 59.18 | 48.21
2019-04-27 06:00 | 75.23 | 67.07
2019-04-27 06:30 | 90.33 | 83.79
2019-04-27 07:00 | 102.37 | 96.44
2019-04-27 07:30 | 94.7 | 88.8
2019-04-27 08:00 | 68.64 | 60.9
2019-04-27 08:30 | 53.91 | 52.86
2019-04-27 09:00 | 36.24 | 35.92
2019-04-27 09:30 | 19.94 | 18.99
2019-04-27 10:00 | 26.89 | 18.84
2019-04-27 10:30 | 20.68 | 4.3
2019-04-27 11:00 | 24.75 | -13.53
2019-04-27 11:30 | 25.79 | -14.9
2019-04-27 12:00 | 43.05 | -35.71
2019-04-27 12:30 | 28.92 | -18.5
2019-04-27 13:00 | 22.65 | -7.49
2019-04-27 13:30 | 21.68 | -5.48
2019-04-27 14:00 | 24.16 | 13.29
2019-04-27 14:30 | 37.3 | 31.81
2019-04-27 15:00 | 64.88 | 62.49
2019-04-27 15:30 | 82.53 | 80.79
2019-04-27 16:00 | 113.14 | 111.89
2019-04-27 16:30 | 128.15 | 127.07
2019-04-27 17:00 | 137.73 | 136.66
2019-04-27 17:30 | 148.13 | 147.1
2019-04-27 18:00 | 167.18 | 162.88
2019-04-27 18:30 | 173.29 | 166.47
2019-04-27 19:00 | 173.58 | 168.48
2019-04-27 19:30 | 161.78 | 160.19
2019-04-27 20:00 | 160.21 | 160.12
2019-04-27 20:30 | 165.64 | 165.35
2019-04-27 21:00 | 156.95 | 156.46
2019-04-27 21:30 | 153.66 | 153
2019-04-27 22:00 | 126.58 | 125.49
2019-04-27 22:30 | 123.37 | 122.07
2019-04-27 23:00 | 142.56 | 141.16
2019-04-27 23:30 | 108.66 | 106.44
2019-04-28 | 88.34 | 85.35
2019-04-28 00:30 | 78.99 | 75.22
2019-04-28 01:00 | 62.02 | 56.83
2019-04-28 01:30 | 55.62 | 49.4
2019-04-28 02:00 | 46.89 | 36.5
2019-04-28 02:30 | 44.65 | 30.76
2019-04-28 03:00 | 41.09 | 25.88
2019-04-28 03:30 | 35.88 | 17.19
2019-04-28 04:00 | 37.27 | 20.1
2019-04-28 04:30 | 44.58 | 31.34
2019-04-28 05:00 | 54.57 | 44.4
2019-04-28 05:30 | 64.22 | 55.61
2019-04-28 06:00 | 69.17 | 61.27
2019-04-28 06:30 | 76.69 | 70.04
2019-04-28 07:00 | 76.19 | 69.31
2019-04-28 07:30 | 61.8 | 52.62
2019-04-28 08:00 | 37.54 | 18.63
2019-04-28 08:30 | 32.12 | 6.1
2019-04-28 09:00 | 36.88 | 19.67
2019-04-28 09:30 | 29.74 | 13.34
2019-04-28 10:00 | 28.98 | 16.37
2019-04-28 10:30 | 24.87 | 9.62
2019-04-28 11:00 | 22.78 | 4.37
2019-04-28 11:30 | 14.14 | -4.5
2019-04-28 12:00 | 14.45 | -14.41
2019-04-28 12:30 | 30.83 | -30.83
2019-04-28 13:00 | 9.56 | -9.5
2019-04-28 13:30 | 4.74 | 4.67
2019-04-28 14:00 | 5.97 | 5.91
2019-04-28 14:30 | 0.16 | -0.04
2019-04-28 15:00 | 27.92 | 27.9
2019-04-28 15:30 | 66.81 | 66.81
2019-04-28 16:00 | 133.03 | 133.03
2019-04-28 16:30 | 123.94 | 123.94
2019-04-28 17:00 | 143.22 | 143.22
2019-04-28 17:30 | 160.7 | 160.7
2019-04-28 18:00 | 193.94 | 193.79
2019-04-28 18:30 | 158.29 | 157.74
2019-04-28 19:00 | 158.92 | 158.08
2019-04-28 19:30 | 145.04 | 143.83
2019-04-28 20:00 | 125.28 | 124.34
2019-04-28 20:30 | 138.53 | 138.21
2019-04-28 21:00 | 115.72 | 115.14
2019-04-28 21:30 | 96.1 | 95.12
2019-04-28 22:00 | 84.07 | 82.46
2019-04-28 22:30 | 88.09 | 86.17
2019-04-28 23:00 | 88.91 | 86.19
2019-04-28 23:30 | 83.66 | 79.56
2019-04-29 | 53.7 | 41.17
2019-04-29 00:30 | 49.39 | 37.17
2019-04-29 01:00 | 44.91 | 30.98
2019-04-29 01:30 | 37.28 | 19.32
2019-04-29 02:00 | 31.53 | 5.45
2019-04-29 02:30 | 31.85 | 9.51
2019-04-29 03:00 | 39.78 | 25.55
2019-04-29 03:30 | 39.42 | 23.97
2019-04-29 04:00 | 36.91 | 19.19
2019-04-29 04:30 | 48.54 | 36.54
2019-04-29 05:00 | 65.16 | 56.37
2019-04-29 05:30 | 95.48 | 89.32
2019-04-29 06:00 | 121.68 | 117.09
2019-04-29 06:30 | 148.7 | 145.15
2019-04-29 07:00 | 156.03 | 153.96
2019-04-29 07:30 | 158.02 | 157.66
2019-04-29 08:00 | 145.62 | 145.48
2019-04-29 08:30 | 128.6 | 128.54
2019-04-29 09:00 | 99.77 | 99.76
2019-04-29 09:30 | 91.26 | 91.07
2019-04-29 10:00 | 94.62 | 86.33
2019-04-29 10:30 | 111.75 | 97.89
2019-04-29 11:00 | 112.21 | 98.79
2019-04-29 11:30 | 109.9 | 95.93
2019-04-29 12:00 | 108.74 | 94.81
2019-04-29 12:30 | 110.22 | 96.55
2019-04-29 13:00 | 116.16 | 103.38
2019-04-29 13:30 | 125.28 | 112.8
2019-04-29 14:00 | 134.31 | 122.58
2019-04-29 14:30 | 127.31 | 114.63
2019-04-29 15:00 | 118.31 | 105.31
2019-04-29 15:30 | 128.51 | 117.51
2019-04-29 16:00 | 146.67 | 137.51
2019-04-29 16:30 | 160.23 | 152.14
2019-04-29 17:00 | 195.01 | 188.39
2019-04-29 17:30 | 224.58 | 218.58
2019-04-29 18:00 | 237.28 | 230.71
2019-04-29 18:30 | 234.68 | 228.83
2019-04-29 19:00 | 227.61 | 222.75
2019-04-29 19:30 | 199.17 | 197.66
2019-04-29 20:00 | 202.8 | 202.8
2019-04-29 20:30 | 200.85 | 200.56
2019-04-29 21:00 | 176.44 | 175.88
2019-04-29 21:30 | 155.82 | 155.15
2019-04-29 22:00 | 133.7 | 132.69
2019-04-29 22:30 | 126.14 | 124.8
2019-04-29 23:00 | 138.05 | 136.55
2019-04-29 23:30 | 121.25 | 119.32
2019-04-30 | 98.36 | 95.55
2019-04-30 00:30 | 89.86 | 86.46
2019-04-30 01:00 | 65.18 | 59.71
2019-04-30 01:30 | 69.52 | 64.4
2019-04-30 02:00 | 61.7 | 55.88
2019-04-30 02:30 | 49.42 | 41.92
2019-04-30 03:00 | 42.66 | 33.83
2019-04-30 03:30 | 65.06 | 59.73
2019-04-30 04:00 | 64.43 | 58.52
2019-04-30 04:30 | 72.52 | 67.68
2019-04-30 05:00 | 76.65 | 72.12
2019-04-30 05:30 | 103.41 | 100.64
2019-04-30 06:00 | 136.26 | 134.64
2019-04-30 06:30 | 160.96 | 160.41
2019-04-30 07:00 | 177.08 | 176.83
2019-04-30 07:30 | 185.45 | 185.41
2019-04-30 08:00 | 165.63 | 165.59
2019-04-30 08:30 | 145.41 | 145.4
2019-04-30 09:00 | 127.42 | 127.4
2019-04-30 09:30 | 120.9 | 120.86
2019-04-30 10:00 | 112.73 | 112.73
2019-04-30 10:30 | 110.73 | 110.72
2019-04-30 11:00 | 109.68 | 109.68
2019-04-30 11:30 | 139.16 | 139.1
2019-04-30 12:00 | 154.03 | 153.97
2019-04-30 12:30 | 146.78 | 146.77
2019-04-30 13:00 | 159.8 | 159.79
2019-04-30 13:30 | 164.7 | 164.68
2019-04-30 14:00 | 156.08 | 156.07
2019-04-30 14:30 | 169.27 | 169.27
2019-04-30 15:00 | 164.48 | 164.47
2019-04-30 15:30 | 169.81 | 169.8
2019-04-30 16:00 | 181.36 | 181.36
2019-04-30 16:30 | 174.17 | 174.17
2019-04-30 17:00 | 174.7 | 174.59
2019-04-30 17:30 | 182.18 | 181.53
2019-04-30 18:00 | 217.41 | 216.61
2019-04-30 18:30 | 205.77 | 205.18
2019-04-30 19:00 | 198.62 | 198.2
2019-04-30 19:30 | 201.52 | 201.01
2019-04-30 20:00 | 193.19 | 193.19
2019-04-30 20:30 | 179.36 | 179.34
2019-04-30 21:00 | 161.14 | 161.05
2019-04-30 21:30 | 141.79 | 141.68
2019-04-30 22:00 | 127.37 | 127
2019-04-30 22:30 | 137.73 | 137.44
2019-04-30 23:00 | 139.35 | 138.99
2019-04-30 23:30 | 122.08 | 121.9
2019-05-01 | 91.31 | 91.27
2019-05-01 00:30 | 87.27 | 86.25
2019-05-01 01:00 | 77 | 75.9
2019-05-01 01:30 | 56.07 | 54.61
2019-05-01 02:00 | 53.19 | 51.62
2019-05-01 02:30 | 61.97 | 60.5
2019-05-01 03:00 | 65.72 | 64.3
2019-05-01 03:30 | 73.95 | 72.65
2019-05-01 04:00 | 84.09 | 83.03
2019-05-01 04:30 | 81.26 | 80.83
2019-05-01 05:00 | 83.81 | 83.28
2019-05-01 05:30 | 117.12 | 116.57
2019-05-01 06:00 | 142.46 | 142.02
2019-05-01 06:30 | 140.68 | 140.21
2019-05-01 07:00 | 166.35 | 166.3
2019-05-01 07:30 | 182.64 | 180.99
2019-05-01 08:00 | 179.7 | 176.29
2019-05-01 08:30 | 156.71 | 152.15
2019-05-01 09:00 | 138.15 | 132.63
2019-05-01 09:30 | 133.58 | 127.5
2019-05-01 10:00 | 100.89 | 91.82
2019-05-01 10:30 | 96.89 | 86.1
2019-05-01 11:00 | 84.01 | 71.54
2019-05-01 11:30 | 80.12 | 66.38
2019-05-01 12:00 | 60.44 | 37.57
2019-05-01 12:30 | 74.08 | 57.78
2019-05-01 13:00 | 103.13 | 92.49
2019-05-01 13:30 | 110.25 | 99.31
2019-05-01 14:00 | 96.53 | 83.47
2019-05-01 14:30 | 103.32 | 90.92
2019-05-01 15:00 | 133.29 | 124.17
2019-05-01 15:30 | 145.37 | 137.94
2019-05-01 16:00 | 163.85 | 157.6
2019-05-01 16:30 | 190.11 | 185.06
2019-05-01 17:00 | 220.45 | 216.26
2019-05-01 17:30 | 222.75 | 218.36
2019-05-01 18:00 | 213.6 | 209.11
2019-05-01 18:30 | 201.73 | 197.76
2019-05-01 19:00 | 207.14 | 203.66
2019-05-01 19:30 | 186.24 | 182.96
2019-05-01 20:00 | 187.4 | 184.63
2019-05-01 20:30 | 183.68 | 181.61
2019-05-01 21:00 | 167.11 | 166.89
2019-05-01 21:30 | 152.27 | 151.99
2019-05-01 22:00 | 142.71 | 142.24
2019-05-01 22:30 | 152.25 | 151.74
2019-05-01 23:00 | 153.97 | 153.46
2019-05-01 23:30 | 126.38 | 125.58
2019-05-02 | 97.11 | 95.72
2019-05-02 00:30 | 83.64 | 81.8
2019-05-02 01:00 | 82.53 | 80.41
2019-05-02 01:30 | 73.74 | 71.25
2019-05-02 02:00 | 68.31 | 65.48
2019-05-02 02:30 | 56.61 | 53.11
2019-05-02 03:00 | 64.83 | 62.05
2019-05-02 03:30 | 58.02 | 55.23
2019-05-02 04:00 | 48.41 | 45.76
2019-05-02 04:30 | 61.93 | 60
2019-05-02 05:00 | 82.82 | 81.24
2019-05-02 05:30 | 129.81 | 128.82
2019-05-02 06:00 | 143.39 | 142.64
2019-05-02 06:30 | 160.61 | 159.99
2019-05-02 07:00 | 173.1 | 172.96
2019-05-02 07:30 | 176.16 | 176.15
2019-05-02 08:00 | 160.56 | 160.42
2019-05-02 08:30 | 142.4 | 142.06
2019-05-02 09:00 | 156.9 | 156.31
2019-05-02 09:30 | 128.24 | 126.82
2019-05-02 10:00 | 125.28 | 123.7
2019-05-02 10:30 | 117.88 | 116.3
2019-05-02 11:00 | 111.59 | 109.89
2019-05-02 11:30 | 107.01 | 105.05
2019-05-02 12:00 | 155.89 | 153.4
2019-05-02 12:30 | 121.28 | 113.46
2019-05-02 13:00 | 97.13 | 87.31
2019-05-02 13:30 | 103.51 | 94.16
2019-05-02 14:00 | 123.11 | 115.05
2019-05-02 14:30 | 131.32 | 123.89
2019-05-02 15:00 | 142.98 | 136.64
2019-05-02 15:30 | 143.92 | 138.23
2019-05-02 16:00 | 167.62 | 163.17
2019-05-02 16:30 | 175.94 | 172.09
2019-05-02 17:00 | 179.2 | 175.57
2019-05-02 17:30 | 207.82 | 202.8
2019-05-02 18:00 | 244.66 | 233.89
2019-05-02 18:30 | 244.93 | 234.77
2019-05-02 19:00 | 237.68 | 228.07
2019-05-02 19:30 | 221.4 | 217.29
2019-05-02 20:00 | 220.23 | 216.23
2019-05-02 20:30 | 211.6 | 209.15
2019-05-02 21:00 | 165.39 | 165.35
2019-05-02 21:30 | 163.29 | 163.29
2019-05-02 22:00 | 156.17 | 156.13
2019-05-02 22:30 | 144.81 | 144.72
2019-05-02 23:00 | 146.43 | 146.26
2019-05-02 23:30 | 127.85 | 127.69
2019-05-03 | 99.44 | 99.21
2019-05-03 00:30 | 81.25 | 80.98
2019-05-03 01:00 | 54.07 | 53.63
2019-05-03 01:30 | 51.67 | 51.24
2019-05-03 02:00 | 48.87 | 48.08
2019-05-03 02:30 | 49.11 | 48.26
2019-05-03 03:00 | 54.95 | 54.19
2019-05-03 03:30 | 64.32 | 63.67
2019-05-03 04:00 | 64.85 | 64.27
2019-05-03 04:30 | 81.4 | 81.4
2019-05-03 05:00 | 107.69 | 107.69
2019-05-03 05:30 | 133.31 | 133.31
2019-05-03 06:00 | 142.14 | 142.13
2019-05-03 06:30 | 158.92 | 158.91
2019-05-03 07:00 | 173.11 | 172.1
2019-05-03 07:30 | 160.56 | 158.82
2019-05-03 08:00 | 136.08 | 133.81
2019-05-03 08:30 | 142.58 | 138.59
2019-05-03 09:00 | 118.3 | 114.19
2019-05-03 09:30 | 122.22 | 117.97
2019-05-03 10:00 | 120.22 | 116.08
2019-05-03 10:30 | 110.04 | 106.5
2019-05-03 11:00 | 130.19 | 127.4
2019-05-03 11:30 | 124.37 | 119.41
2019-05-03 12:00 | 104.07 | 97.94
2019-05-03 12:30 | 120.24 | 116.24
2019-05-03 13:00 | 119.11 | 115.79
2019-05-03 13:30 | 108.02 | 104.2
2019-05-03 14:00 | 120.48 | 116.6
2019-05-03 14:30 | 135.08 | 131.38
2019-05-03 15:00 | 125.64 | 122.07
2019-05-03 15:30 | 149.9 | 147.03
2019-05-03 16:00 | 173.82 | 171.17
2019-05-03 16:30 | 190.72 | 188.14
2019-05-03 17:00 | 201.14 | 198.57
2019-05-03 17:30 | 201.56 | 198.83
2019-05-03 18:00 | 218.94 | 215.82
2019-05-03 18:30 | 204.14 | 200.52
2019-05-03 19:00 | 205.55 | 202.33
2019-05-03 19:30 | 186.08 | 182.71
2019-05-03 20:00 | 173.14 | 169.73
2019-05-03 20:30 | 152.88 | 149.32
2019-05-03 21:00 | 135.88 | 135.63
2019-05-03 21:30 | 145.94 | 145.83
2019-05-03 22:00 | 124.22 | 124.19
2019-05-03 22:30 | 118.61 | 118.57
2019-05-03 23:00 | 122.55 | 122.52
2019-05-03 23:30 | 112.22 | 112.02
2019-05-04 | 99.68 | 99.56
2019-05-04 00:30 | 96.35 | 96.28
2019-05-04 01:00 | 102.82 | 102.72
2019-05-04 01:30 | 81.89 | 81.78
2019-05-04 02:00 | 73.2 | 71.6
2019-05-04 02:30 | 56.79 | 54.65
2019-05-04 03:00 | 50.7 | 46.85
2019-05-04 03:30 | 55.99 | 52.4
2019-05-04 04:00 | 54.83 | 51.18
2019-05-04 04:30 | 72.17 | 69.34
2019-05-04 05:00 | 90.91 | 88.72
2019-05-04 05:30 | 107.11 | 105.25
2019-05-04 06:00 | 128.4 | 126.85
2019-05-04 06:30 | 131.79 | 130.35
2019-05-04 07:00 | 141.46 | 139.69
2019-05-04 07:30 | 154.94 | 154.54
2019-05-04 08:00 | 150.89 | 150.88
2019-05-04 08:30 | 148.51 | 148.49
2019-05-04 09:00 | 153.98 | 153.92
2019-05-04 09:30 | 161.71 | 161.57
2019-05-04 10:00 | 166.51 | 166.26
2019-05-04 10:30 | 160.65 | 160.19
2019-05-04 11:00 | 185.24 | 184.74
2019-05-04 11:30 | 188.94 | 188.35
2019-05-04 12:00 | 184.29 | 183.8
2019-05-04 12:30 | 183.12 | 182.64
2019-05-04 13:00 | 191.14 | 190.52
2019-05-04 13:30 | 182.64 | 182.04
2019-05-04 14:00 | 186.42 | 185.96
2019-05-04 14:30 | 195.75 | 195.3
2019-05-04 15:00 | 199.38 | 198.86
2019-05-04 15:30 | 195.72 | 194.78
2019-05-04 16:00 | 187.16 | 185.97
2019-05-04 16:30 | 192.14 | 191.28
2019-05-04 17:00 | 197.59 | 196.83
2019-05-04 17:30 | 201.39 | 200.59
2019-05-04 18:00 | 200 | 199.53
2019-05-04 18:30 | 188.1 | 187.63
2019-05-04 19:00 | 172.29 | 171.93
2019-05-04 19:30 | 169.12 | 168.76
2019-05-04 20:00 | 167.53 | 167.07
2019-05-04 20:30 | 166.71 | 166.62
2019-05-04 21:00 | 162.02 | 161.99
2019-05-04 21:30 | 157.35 | 157.29
2019-05-04 22:00 | 150.65 | 150.57
2019-05-04 22:30 | 151.96 | 151.88
2019-05-04 23:00 | 160.35 | 160.23
2019-05-04 23:30 | 137.52 | 137.41
2019-05-05 | 104.84 | 104.81
2019-05-05 00:30 | 106.07 | 105.88
2019-05-05 01:00 | 97.95 | 97.78
2019-05-05 01:30 | 80.4 | 80.37
2019-05-05 02:00 | 70.15 | 68.2
2019-05-05 02:30 | 69.16 | 66.34
2019-05-05 03:00 | 70.99 | 69.47
2019-05-05 03:30 | 72.06 | 71.96
2019-05-05 04:00 | 89.73 | 89.62
2019-05-05 04:30 | 95.58 | 95.45
2019-05-05 05:00 | 98.58 | 98.46
2019-05-05 05:30 | 103.01 | 102.89
2019-05-05 06:00 | 106.08 | 105.97
2019-05-05 06:30 | 104.52 | 104.34
2019-05-05 07:00 | 94.56 | 94.54
2019-05-05 07:30 | 85.76 | 85.76
2019-05-05 08:00 | 84.44 | 84.43
2019-05-05 08:30 | 86.5 | 86.48
2019-05-05 09:00 | 79.79 | 79.77
2019-05-05 09:30 | 61.25 | 61.25
2019-05-05 10:00 | 37.52 | 37.43
2019-05-05 10:30 | 34.73 | 34.69
2019-05-05 11:00 | 31.08 | 31.05
2019-05-05 11:30 | 31.29 | 31.14
2019-05-05 12:00 | 29.59 | 29.45
2019-05-05 12:30 | 29.8 | 29.64
2019-05-05 13:00 | 29.28 | 29.08
2019-05-05 13:30 | 31.65 | 31.49
2019-05-05 14:00 | 33.45 | 33.33
2019-05-05 14:30 | 30.54 | 30.53
2019-05-05 15:00 | 33.44 | 33.08
2019-05-05 15:30 | 39.21 | 38.54
2019-05-05 16:00 | 55.46 | 55.07
2019-05-05 16:30 | 80.27 | 80.12
2019-05-05 17:00 | 105.2 | 105.07
2019-05-05 17:30 | 129.76 | 129.59
2019-05-05 18:00 | 160.62 | 157.74
2019-05-05 18:30 | 155.56 | 151.75
2019-05-05 19:00 | 149.67 | 145.72
2019-05-05 19:30 | 131.09 | 128.6
2019-05-05 20:00 | 124.23 | 124.23
2019-05-05 20:30 | 111.23 | 111.23
2019-05-05 21:00 | 108.24 | 108.22
2019-05-05 21:30 | 124.11 | 124.04
2019-05-05 22:00 | 116.47 | 116.37
2019-05-05 22:30 | 126.55 | 126.38
2019-05-05 23:00 | 124.24 | 124.01
2019-05-05 23:30 | 118.51 | 118.33
2019-05-06 | 102.38 | 102.1
2019-05-06 00:30 | 80.71 | 79.67
2019-05-06 01:00 | 64.85 | 63.5
2019-05-06 01:30 | 57.39 | 57.09
2019-05-06 02:00 | 44.89 | 44.15
2019-05-06 02:30 | 43.91 | 41.89
2019-05-06 03:00 | 42.88 | 40.84
2019-05-06 03:30 | 55.15 | 53.52
2019-05-06 04:00 | 51.31 | 49.6
2019-05-06 04:30 | 54.68 | 53.12
2019-05-06 05:00 | 62.59 | 61.2
2019-05-06 05:30 | 70.8 | 69.4
2019-05-06 06:00 | 82.49 | 81.3
2019-05-06 06:30 | 63.66 | 62.17
2019-05-06 07:00 | 36.59 | 34.58
2019-05-06 07:30 | 27.82 | 25.94
2019-05-06 08:00 | 19.83 | 19.26
2019-05-06 08:30 | 27.77 | 25.31
2019-05-06 09:00 | 30.29 | 27.42
2019-05-06 09:30 | 29.04 | 25.57
2019-05-06 10:00 | 28.25 | 24.08
2019-05-06 10:30 | 24.18 | 18.35
2019-05-06 11:00 | 28.28 | 22.83
2019-05-06 11:30 | 28.5 | 22.77
2019-05-06 12:00 | 28.84 | 23.02
2019-05-06 12:30 | 29.43 | 23.49
2019-05-06 13:00 | 30.15 | 24.32
2019-05-06 13:30 | 33.44 | 28.14
2019-05-06 14:00 | 38.97 | 34.51
2019-05-06 14:30 | 48.26 | 43.82
2019-05-06 15:00 | 46.85 | 42.89
2019-05-06 15:30 | 50.12 | 44.36
2019-05-06 16:00 | 61.18 | 48.58
2019-05-06 16:30 | 64.29 | 54.42
2019-05-06 17:00 | 81.8 | 60.2
2019-05-06 17:30 | 101.86 | 75.72
2019-05-06 18:00 | 130.59 | 109.31
2019-05-06 18:30 | 131.77 | 111.31
2019-05-06 19:00 | 134.9 | 116.1
2019-05-06 19:30 | 129.01 | 111.79
2019-05-06 20:00 | 119.52 | 116.06
2019-05-06 20:30 | 106.56 | 105.94
2019-05-06 21:00 | 83.71 | 82.88
2019-05-06 21:30 | 76.86 | 76.64
2019-05-06 22:00 | 87.68 | 87.32
2019-05-06 22:30 | 88.7 | 88.25
2019-05-06 23:00 | 89.3 | 88.77
2019-05-06 23:30 | 73.94 | 73.37
2019-05-07 | 46.72 | 45.89
2019-05-07 00:30 | 37.92 | 36.79
2019-05-07 01:00 | 14.22 | 11.66
2019-05-07 01:30 | 7.82 | 2.18
2019-05-07 02:00 | 9.39 | 5.58
2019-05-07 02:30 | 12.51 | 10.21
2019-05-07 03:00 | 13.91 | 11.93
2019-05-07 03:30 | 22.36 | 21.03
2019-05-07 04:00 | 36.3 | 35.36
2019-05-07 04:30 | 53.06 | 52.33
2019-05-07 05:00 | 85.06 | 84.42
2019-05-07 05:30 | 121.79 | 121.33
2019-05-07 06:00 | 141.77 | 141.51
2019-05-07 06:30 | 133.94 | 133.79
2019-05-07 07:00 | 122.73 | 122.68
2019-05-07 07:30 | 99.87 | 98.33
2019-05-07 08:00 | 89.4 | 85.99
2019-05-07 08:30 | 89.46 | 85.67
2019-05-07 09:00 | 81.85 | 77.1
2019-05-07 09:30 | 62.34 | 54.42
2019-05-07 10:00 | 60.89 | 51.7
2019-05-07 10:30 | 52.43 | 41.06
2019-05-07 11:00 | 53.09 | 41.73
2019-05-07 11:30 | 50.99 | 38.75
2019-05-07 12:00 | 49.69 | 37.45
2019-05-07 12:30 | 50.59 | 38.19
2019-05-07 13:00 | 53.74 | 42.21
2019-05-07 13:30 | 57.51 | 46.87
2019-05-07 14:00 | 60.36 | 51.31
2019-05-07 14:30 | 74.19 | 67.02
2019-05-07 15:00 | 96.4 | 91.26
2019-05-07 15:30 | 118.32 | 114.55
2019-05-07 16:00 | 137.99 | 135.13
2019-05-07 16:30 | 165.8 | 157.58
2019-05-07 17:00 | 174.83 | 164.54
2019-05-07 17:30 | 163.52 | 152.04
2019-05-07 18:00 | 159.15 | 146.68
2019-05-07 18:30 | 159.15 | 147.78
2019-05-07 19:00 | 179.62 | 170.33
2019-05-07 19:30 | 151.25 | 140.93
2019-05-07 20:00 | 140.26 | 129.47
2019-05-07 20:30 | 143.3 | 135.72
2019-05-07 21:00 | 107.27 | 106.82
2019-05-07 21:30 | 79.59 | 79.58
2019-05-07 22:00 | 79.48 | 79.47
2019-05-07 22:30 | 86.64 | 86.6
2019-05-07 23:00 | 104.49 | 104.38
2019-05-07 23:30 | 117.23 | 117.15
2019-05-08 | 119.95 | 119.78
2019-05-08 00:30 | 116.92 | 116.62
2019-05-08 01:00 | 99.97 | 99.53
2019-05-08 01:30 | 66.29 | 65.53
2019-05-08 02:00 | 45.79 | 44.79
2019-05-08 02:30 | 45.76 | 44.85
2019-05-08 03:00 | 52.24 | 51.54
2019-05-08 03:30 | 63.14 | 62.49
2019-05-08 04:00 | 81.69 | 81.32
2019-05-08 04:30 | 92.48 | 92.17
2019-05-08 05:00 | 98.16 | 97.78
2019-05-08 05:30 | 133.24 | 133
2019-05-08 06:00 | 139.83 | 139.75
2019-05-08 06:30 | 159.62 | 159.55
2019-05-08 07:00 | 160.96 | 160.92
2019-05-08 07:30 | 166.34 | 165.6
2019-05-08 08:00 | 170.34 | 167.69
2019-05-08 08:30 | 167.71 | 164.53
2019-05-08 09:00 | 160.48 | 157.06
2019-05-08 09:30 | 148.5 | 144.72
2019-05-08 10:00 | 140.45 | 136.65
2019-05-08 10:30 | 129.43 | 124.75
2019-05-08 11:00 | 132.02 | 127.09
2019-05-08 11:30 | 130.17 | 125.1
2019-05-08 12:00 | 130.44 | 127.94
2019-05-08 12:30 | 131.08 | 129.15
2019-05-08 13:00 | 136.04 | 134.11
2019-05-08 13:30 | 143.12 | 141.18
2019-05-08 14:00 | 151.84 | 149.85
2019-05-08 14:30 | 156.12 | 154.17
2019-05-08 15:00 | 157.92 | 156.39
2019-05-08 15:30 | 161.18 | 159.93
2019-05-08 16:00 | 169.35 | 168.42
2019-05-08 16:30 | 172.46 | 171.24
2019-05-08 17:00 | 176.1 | 174.65
2019-05-08 17:30 | 178.39 | 176.68
2019-05-08 18:00 | 187.66 | 186.87
2019-05-08 18:30 | 181.15 | 180.11
2019-05-08 19:00 | 183.1 | 181.48
2019-05-08 19:30 | 180.43 | 177.34
2019-05-08 20:00 | 186.01 | 183.66
2019-05-08 20:30 | 177.84 | 176.52
2019-05-08 21:00 | 156.6 | 156.49
2019-05-08 21:30 | 153.14 | 153.05
2019-05-08 22:00 | 137.14 | 137
2019-05-08 22:30 | 144.49 | 144.33
2019-05-08 23:00 | 152.55 | 152.49
2019-05-08 23:30 | 124.4 | 124.33
2019-05-09 | 87.83 | 87.7
2019-05-09 00:30 | 71.38 | 69.62
2019-05-09 01:00 | 61.49 | 57.53
2019-05-09 01:30 | 52.9 | 48.04
2019-05-09 02:00 | 46.28 | 40.23
2019-05-09 02:30 | 46.01 | 39.54
2019-05-09 03:00 | 43.26 | 35.7
2019-05-09 03:30 | 37.15 | 27.61
2019-05-09 04:00 | 40.93 | 32.62
2019-05-09 04:30 | 64.51 | 60.04
2019-05-09 05:00 | 87.39 | 85.05
2019-05-09 05:30 | 121.21 | 120.13
2019-05-09 06:00 | 145.08 | 144.29
2019-05-09 06:30 | 157.82 | 156.81
2019-05-09 07:00 | 154.05 | 154
2019-05-09 07:30 | 167.06 | 166.98
2019-05-09 08:00 | 167.16 | 167.01
2019-05-09 08:30 | 161.94 | 161.73
2019-05-09 09:00 | 154.71 | 154.46
2019-05-09 09:30 | 143.81 | 143.5
2019-05-09 10:00 | 143.8 | 143.43
2019-05-09 10:30 | 134.03 | 133.39
2019-05-09 11:00 | 135.1 | 134.29
2019-05-09 11:30 | 130.75 | 129.84
2019-05-09 12:00 | 131.54 | 130.72
2019-05-09 12:30 | 133.6 | 132.8
2019-05-09 13:00 | 140.96 | 138.42
2019-05-09 13:30 | 151.5 | 147.43
2019-05-09 14:00 | 158.54 | 154.55
2019-05-09 14:30 | 171.35 | 160.23
2019-05-09 15:00 | 174.26 | 162.25
2019-05-09 15:30 | 175.83 | 164.4
2019-05-09 16:00 | 179.78 | 168.96
2019-05-09 16:30 | 183.93 | 173.45
2019-05-09 17:00 | 186.62 | 176.78
2019-05-09 17:30 | 189.88 | 180.74
2019-05-09 18:00 | 189.15 | 179.76
2019-05-09 18:30 | 171.21 | 161.52
2019-05-09 19:00 | 178.24 | 169
2019-05-09 19:30 | 158.64 | 153.16
2019-05-09 20:00 | 146.43 | 146.15
2019-05-09 20:30 | 136.92 | 136.91
2019-05-09 21:00 | 120.89 | 120.89
2019-05-09 21:30 | 115.38 | 115.37
2019-05-09 22:00 | 113.81 | 113.76
2019-05-09 22:30 | 126.02 | 125.93
2019-05-09 23:00 | 118.4 | 118.26
2019-05-09 23:30 | 96.16 | 96.05
2019-05-10 | 85.98 | 85.8
2019-05-10 00:30 | 89.27 | 88.98
2019-05-10 01:00 | 100.34 | 99.89
2019-05-10 01:30 | 91.6 | 91.12
2019-05-10 02:00 | 99.51 | 99.45
2019-05-10 02:30 | 102.6 | 102.54
2019-05-10 03:00 | 77.8 | 77.75
2019-05-10 03:30 | 79.83 | 79.77
2019-05-10 04:00 | 83.11 | 83.04
2019-05-10 04:30 | 86.19 | 86.14
2019-05-10 05:00 | 84.41 | 84.38
2019-05-10 05:30 | 126.92 | 126.89
2019-05-10 06:00 | 143.11 | 143.1
2019-05-10 06:30 | 151.27 | 151.25
2019-05-10 07:00 | 162.48 | 162.44
2019-05-10 07:30 | 183.47 | 183.46
2019-05-10 08:00 | 167.52 | 167.48
2019-05-10 08:30 | 136.89 | 136.49
2019-05-10 09:00 | 92.56 | 91.14
2019-05-10 09:30 | 67.77 | 65.39
2019-05-10 10:00 | 62 | 60.24
2019-05-10 10:30 | 63.81 | 62.25
2019-05-10 11:00 | 63.86 | 62.25
2019-05-10 11:30 | 57.84 | 55.85
2019-05-10 12:00 | 59.18 | 57.33
2019-05-10 12:30 | 56.34 | 54.51
2019-05-10 13:00 | 60.71 | 58.41
2019-05-10 13:30 | 80.71 | 71.04
2019-05-10 14:00 | 96.3 | 89.28
2019-05-10 14:30 | 127.58 | 123.17
2019-05-10 15:00 | 160.54 | 157.18
2019-05-10 15:30 | 199.79 | 197.68
2019-05-10 16:00 | 207.3 | 205.58
2019-05-10 16:30 | 192.38 | 190.71
2019-05-10 17:00 | 182.63 | 180.95
2019-05-10 17:30 | 182.75 | 180.96
2019-05-10 18:00 | 185.41 | 183.57
2019-05-10 18:30 | 180.46 | 179.04
2019-05-10 19:00 | 181.19 | 179.97
2019-05-10 19:30 | 178.12 | 177.17
2019-05-10 20:00 | 177.65 | 176.92
2019-05-10 20:30 | 176.76 | 176.2
2019-05-10 21:00 | 170.06 | 169.69
2019-05-10 21:30 | 162.76 | 162.55
2019-05-10 22:00 | 120.45 | 120.33
2019-05-10 22:30 | 104.63 | 104.58
2019-05-10 23:00 | 113.62 | 113.44
2019-05-10 23:30 | 97.76 | 95.82
2019-05-11 | 87.07 | 84.37
2019-05-11 00:30 | 88 | 86.17
2019-05-11 01:00 | 82.88 | 80.98
2019-05-11 01:30 | 85.47 | 83.21
2019-05-11 02:00 | 86.21 | 83.48
2019-05-11 02:30 | 74.04 | 73.39
2019-05-11 03:00 | 66.56 | 65.82
2019-05-11 03:30 | 59.56 | 58.84
2019-05-11 04:00 | 61.16 | 60.49
2019-05-11 04:30 | 93.21 | 92.84
2019-05-11 05:00 | 89.19 | 88.72
2019-05-11 05:30 | 91.22 | 90.73
2019-05-11 06:00 | 92.8 | 92.43
2019-05-11 06:30 | 105.44 | 105.21
2019-05-11 07:00 | 93.27 | 92.99
2019-05-11 07:30 | 53.26 | 53.04
2019-05-11 08:00 | 13.04 | 12.63
2019-05-11 08:30 | 9.94 | -7.07
2019-05-11 09:00 | 11.46 | 8.53
2019-05-11 09:30 | 26.09 | 22.94
2019-05-11 10:00 | 42.96 | -42.95
2019-05-11 10:30 | 80.95 | -79.33
2019-05-11 11:00 | 74.1 | -73.27
2019-05-11 11:30 | 83.61 | -82.48
2019-05-11 12:00 | 84.12 | -83.13
2019-05-11 12:30 | 85.53 | -84.38
2019-05-11 13:00 | 73.97 | -72.93
2019-05-11 13:30 | 49.02 | -47.24
2019-05-11 14:00 | 10.25 | -8.38
2019-05-11 14:30 | 10.27 | 9.46
2019-05-11 15:00 | 11.56 | 11.02
2019-05-11 15:30 | 27.78 | 27.63
2019-05-11 16:00 | 55.19 | 55.19
2019-05-11 16:30 | 84.86 | 84.86
2019-05-11 17:00 | 104.92 | 104.92
2019-05-11 17:30 | 148.69 | 148.67
2019-05-11 18:00 | 147.95 | 147.34
2019-05-11 18:30 | 141.58 | 139.61
2019-05-11 19:00 | 161.41 | 159.83
2019-05-11 19:30 | 151.46 | 150.81
2019-05-11 20:00 | 153.85 | 153.84
2019-05-11 20:30 | 137.6 | 137.59
2019-05-11 21:00 | 121.43 | 121.4
2019-05-11 21:30 | 108.21 | 108.16
2019-05-11 22:00 | 89.65 | 89.59
2019-05-11 22:30 | 91.6 | 91.55
2019-05-11 23:00 | 92.57 | 92.46
2019-05-11 23:30 | 77.81 | 77.78
2019-05-12 | 41.04 | 41.03
2019-05-12 00:30 | 57.9 | 57.89
2019-05-12 01:00 | 59.08 | 57.4
2019-05-12 01:30 | 54.84 | 53.29
2019-05-12 02:00 | 52.75 | 51.19
2019-05-12 02:30 | 59.32 | 57.89
2019-05-12 03:00 | 41.01 | 39.04
2019-05-12 03:30 | 32.24 | 29.61
2019-05-12 04:00 | 41.72 | 39.73
2019-05-12 04:30 | 42.2 | 40.25
2019-05-12 05:00 | 47.94 | 46.26
2019-05-12 05:30 | 54.47 | 53.08
2019-05-12 06:00 | 70.12 | 69.17
2019-05-12 06:30 | 89.91 | 89.27
2019-05-12 07:00 | 100.32 | 100.05
2019-05-12 07:30 | 98.8 | 98.58
2019-05-12 08:00 | 94.77 | 94.17
2019-05-12 08:30 | 100.74 | 100.7
2019-05-12 09:00 | 103.28 | 103.28
2019-05-12 09:30 | 93.15 | 93.15
2019-05-12 10:00 | 93.62 | 93.61
2019-05-12 10:30 | 60.59 | 60.58
2019-05-12 11:00 | 1.46 | 0.85
2019-05-12 11:30 | 13.47 | -13.24
2019-05-12 12:00 | 29.63 | -29.46
2019-05-12 12:30 | 44.23 | -43.84
2019-05-12 13:00 | 24.64 | -24.63
2019-05-12 13:30 | 5.99 | -5.99
2019-05-12 14:00 | 5.53 | 5.32
2019-05-12 14:30 | 31.73 | 31.57
2019-05-12 15:00 | 35.47 | 35.21
2019-05-12 15:30 | 42.25 | 42.03
2019-05-12 16:00 | 75.09 | 74.87
2019-05-12 16:30 | 77.68 | 77.43
2019-05-12 17:00 | 77.2 | 77.03
2019-05-12 17:30 | 117.24 | 117.2
2019-05-12 18:00 | 161.52 | 159.97
2019-05-12 18:30 | 160.94 | 159.14
2019-05-12 19:00 | 149.57 | 147.74
2019-05-12 19:30 | 134.18 | 132.39
2019-05-12 20:00 | 120.17 | 118.2
2019-05-12 20:30 | 113.79 | 113.13
2019-05-12 21:00 | 92.78 | 92.78
2019-05-12 21:30 | 81.14 | 81.14
2019-05-12 22:00 | 69.49 | 69.48
2019-05-12 22:30 | 91.58 | 91.52
2019-05-12 23:00 | 110.38 | 110.25
2019-05-12 23:30 | 100.29 | 100.11
2019-05-13 | 46.84 | 46.55
2019-05-13 00:30 | 61.36 | 61.36
2019-05-13 01:00 | 59.44 | 57.92
2019-05-13 01:30 | 64.51 | 63.07
2019-05-13 02:00 | 62.81 | 61.33
2019-05-13 02:30 | 62.76 | 61.35
2019-05-13 03:00 | 71.24 | 69.93
2019-05-13 03:30 | 71.46 | 70.1
2019-05-13 04:00 | 78.45 | 77.03
2019-05-13 04:30 | 83.01 | 81.72
2019-05-13 05:00 | 91.21 | 90.29
2019-05-13 05:30 | 128.34 | 127.73
2019-05-13 06:00 | 138.21 | 137.44
2019-05-13 06:30 | 154.48 | 153.68
2019-05-13 07:00 | 144.25 | 143.86
2019-05-13 07:30 | 153.82 | 153.8
2019-05-13 08:00 | 136.25 | 136.2
2019-05-13 08:30 | 106.94 | 106.93
2019-05-13 09:00 | 93.13 | 93.09
2019-05-13 09:30 | 103.02 | 102.97
2019-05-13 10:00 | 121.66 | 121.63
2019-05-13 10:30 | 107.71 | 107.71
2019-05-13 11:00 | 142.43 | 142.43
2019-05-13 11:30 | 144.5 | 144.5
2019-05-13 12:00 | 139.74 | 139.73
2019-05-13 12:30 | 144.97 | 144.97
2019-05-13 13:00 | 146.18 | 145.84
2019-05-13 13:30 | 135.75 | 135.13
2019-05-13 14:00 | 154.48 | 154.48
2019-05-13 14:30 | 154.21 | 154.21
2019-05-13 15:00 | 145.19 | 145.19
2019-05-13 15:30 | 137.47 | 137.47
2019-05-13 16:00 | 137.71 | 137.71
2019-05-13 16:30 | 149.03 | 149.03
2019-05-13 17:00 | 160.04 | 160.03
2019-05-13 17:30 | 156.67 | 156.65
2019-05-13 18:00 | 158.81 | 158.67
2019-05-13 18:30 | 139.94 | 139.94
2019-05-13 19:00 | 137.88 | 137.6
2019-05-13 19:30 | 133.07 | 132.67
2019-05-13 20:00 | 125.56 | 124.92
2019-05-13 20:30 | 120.5 | 119.47
2019-05-13 21:00 | 108.01 | 106.51
2019-05-13 21:30 | 101.74 | 99.82
2019-05-13 22:00 | 88.38 | 84.43
2019-05-13 22:30 | 96.01 | 91.88
2019-05-13 23:00 | 101.93 | 98.06
2019-05-13 23:30 | 73.03 | 68.69
2019-05-14 | 42.86 | 38.02
2019-05-14 00:30 | 62.89 | 62.66
2019-05-14 01:00 | 61.76 | 61.52
2019-05-14 01:30 | 55.24 | 55.02
2019-05-14 02:00 | 50.63 | 50.38
2019-05-14 02:30 | 48.47 | 48.21
2019-05-14 03:00 | 49.12 | 48.88
2019-05-14 03:30 | 43.68 | 43.47
2019-05-14 04:00 | 37.98 | 37.86
2019-05-14 04:30 | 61.05 | 60.9
2019-05-14 05:00 | 78.33 | 77.95
2019-05-14 05:30 | 112.44 | 112.05
2019-05-14 06:00 | 119.99 | 119.68
2019-05-14 06:30 | 120.81 | 120.76
2019-05-14 07:00 | 141.91 | 141.56
2019-05-14 07:30 | 162.66 | 162.62
2019-05-14 08:00 | 173.62 | 173.22
2019-05-14 08:30 | 171.82 | 171.33
2019-05-14 09:00 | 174 | 173.45
2019-05-14 09:30 | 170.45 | 169.8
2019-05-14 10:00 | 164.48 | 163.73
2019-05-14 10:30 | 137.29 | 136.59
2019-05-14 11:00 | 127.78 | 127.05
2019-05-14 11:30 | 126.55 | 125.88
2019-05-14 12:00 | 131.61 | 130.98
2019-05-14 12:30 | 128.13 | 127.44
2019-05-14 13:00 | 131.58 | 130.9
2019-05-14 13:30 | 142.3 | 141.69
2019-05-14 14:00 | 143.82 | 143.29
2019-05-14 14:30 | 153.71 | 151.24
2019-05-14 15:00 | 155.13 | 154.01
2019-05-14 15:30 | 159.46 | 158.74
2019-05-14 16:00 | 164.59 | 164.38
2019-05-14 16:30 | 163.84 | 163.39
2019-05-14 17:00 | 158.71 | 158.21
2019-05-14 17:30 | 131.88 | 131.69
2019-05-14 18:00 | 123.34 | 123.33
2019-05-14 18:30 | 122.87 | 122.87
2019-05-14 19:00 | 125.74 | 125.74
2019-05-14 19:30 | 119.78 | 119.77
2019-05-14 20:00 | 135.03 | 135.01
2019-05-14 20:30 | 123.31 | 123.13
2019-05-14 21:00 | 110.82 | 109.87
2019-05-14 21:30 | 108.62 | 107.28
2019-05-14 22:00 | 95.49 | 94
2019-05-14 22:30 | 78.95 | 76.72
2019-05-14 23:00 | 86.82 | 83.95
2019-05-14 23:30 | 69.19 | 63.89
2019-05-15 | 53.35 | 43.38
2019-05-15 00:30 | 53.14 | 51.29
2019-05-15 01:00 | 42.12 | 39.63
2019-05-15 01:30 | 37.96 | 35.48
2019-05-15 02:00 | 34.35 | 31.58
2019-05-15 02:30 | 45.64 | 43.78
2019-05-15 03:00 | 41.53 | 40.15
2019-05-15 03:30 | 38.7 | 37.8
2019-05-15 04:00 | 52.86 | 52.12
2019-05-15 04:30 | 75.31 | 74.72
2019-05-15 05:00 | 91.72 | 91.2
2019-05-15 05:30 | 122.11 | 121.9
2019-05-15 06:00 | 139.88 | 139.84
2019-05-15 06:30 | 129.07 | 128.7
2019-05-15 07:00 | 143.4 | 142.78
2019-05-15 07:30 | 166.81 | 166.73
2019-05-15 08:00 | 164.99 | 164.72
2019-05-15 08:30 | 160.89 | 160.52
2019-05-15 09:00 | 157.62 | 157.09
2019-05-15 09:30 | 156.07 | 155.6
2019-05-15 10:00 | 154.23 | 153.71
2019-05-15 10:30 | 147.22 | 146.61
2019-05-15 11:00 | 146.84 | 146.3
2019-05-15 11:30 | 144.41 | 143.87
2019-05-15 12:00 | 143.31 | 142.72
2019-05-15 12:30 | 148.11 | 147.58
2019-05-15 13:00 | 148.25 | 147.75
2019-05-15 13:30 | 153.7 | 153.2
2019-05-15 14:00 | 151.58 | 150.98
2019-05-15 14:30 | 156.33 | 155.92
2019-05-15 15:00 | 138.72 | 138.58
2019-05-15 15:30 | 139.44 | 139.43
2019-05-15 16:00 | 145.41 | 145.41
2019-05-15 16:30 | 122.59 | 122.57
2019-05-15 17:00 | 114.3 | 114.27
2019-05-15 17:30 | 108.32 | 107.98
2019-05-15 18:00 | 99.14 | 99.05
2019-05-15 18:30 | 71.5 | 71.46
2019-05-15 19:00 | 84.87 | 84.86
2019-05-15 19:30 | 92.56 | 92.47
2019-05-15 20:00 | 93.1 | 92.84
2019-05-15 20:30 | 123.28 | 123.08
2019-05-15 21:00 | 114.97 | 114.16
2019-05-15 21:30 | 95.3 | 93.68
2019-05-15 22:00 | 63.12 | 60.58
2019-05-15 22:30 | 70.63 | 67.92
2019-05-15 23:00 | 65.66 | 62.27
2019-05-15 23:30 | 33.49 | 26.43
2019-05-16 | 19.63 | -1.43
2019-05-16 00:30 | 24.04 | 18.78
2019-05-16 01:00 | 18.86 | 12.09
2019-05-16 01:30 | 14.76 | 1.07
2019-05-16 02:00 | 18.63 | -11.91
2019-05-16 02:30 | 18.49 | -9.01
2019-05-16 03:00 | 15.65 | -3.75
2019-05-16 03:30 | 14.98 | -5.55
2019-05-16 04:00 | 14.51 | -2.18
2019-05-16 04:30 | 16.65 | 4.78
2019-05-16 05:00 | 23.57 | 15.47
2019-05-16 05:30 | 49.47 | 45.3
2019-05-16 06:00 | 75.91 | 73.5
2019-05-16 06:30 | 77.78 | 75.52
2019-05-16 07:00 | 81.99 | 79.51
2019-05-16 07:30 | 129.41 | 128.79
2019-05-16 08:00 | 110.28 | 110.21
2019-05-16 08:30 | 58.88 | 58.81
2019-05-16 09:00 | 10.9 | -0.94
2019-05-16 09:30 | 31.42 | 5.34
2019-05-16 10:00 | 33.53 | -9.93
2019-05-16 10:30 | 40.16 | 29.16
2019-05-16 11:00 | 54.97 | 46.93
2019-05-16 11:30 | 52.42 | 43.28
2019-05-16 12:00 | 39.92 | 26.36
2019-05-16 12:30 | 33.74 | -11.96
2019-05-16 13:00 | 31.61 | -9.01
2019-05-16 13:30 | 29.11 | 12.61
2019-05-16 14:00 | 36.09 | 25.62
2019-05-16 14:30 | 40.63 | 30.97
2019-05-16 15:00 | 73.75 | 69.64
2019-05-16 15:30 | 95.49 | 92.64
2019-05-16 16:00 | 125.07 | 123.3
2019-05-16 16:30 | 116.63 | 115.5
2019-05-16 17:00 | 121.38 | 120.36
2019-05-16 17:30 | 105.84 | 100.74
2019-05-16 18:00 | 136.51 | 126.45
2019-05-16 18:30 | 117.9 | 113.12
2019-05-16 19:00 | 138.2 | 135.42
2019-05-16 19:30 | 123.66 | 120.21
2019-05-16 20:00 | 110.71 | 107.6
2019-05-16 20:30 | 94.31 | 91.24
2019-05-16 21:00 | 63.75 | 60.04
2019-05-16 21:30 | 33.84 | 31.68
2019-05-16 22:00 | 40.77 | 40.71
2019-05-16 22:30 | 56.26 | 56.18
2019-05-16 23:00 | 64.48 | 64.33
2019-05-16 23:30 | 40.47 | 40.37
2019-05-17 | 24.75 | 24.42
2019-05-17 00:30 | 24.81 | 24.23
2019-05-17 01:00 | 10.97 | 8.71
2019-05-17 01:30 | 9.31 | 5.27
2019-05-17 02:00 | 12.31 | 8.76
2019-05-17 02:30 | 12.63 | 8.9
2019-05-17 03:00 | 9.22 | -1.43
2019-05-17 03:30 | 10.78 | 4.3
2019-05-17 04:00 | 12.97 | 8.61
2019-05-17 04:30 | 14.57 | 11.13
2019-05-17 05:00 | 24.69 | 23.25
2019-05-17 05:30 | 50.19 | 49.76
2019-05-17 06:00 | 66.47 | 66.3
2019-05-17 06:30 | 109.62 | 109.62
2019-05-17 07:00 | 109.8 | 109.79
2019-05-17 07:30 | 104.2 | 101.32
2019-05-17 08:00 | 102.25 | 98.13
2019-05-17 08:30 | 108.6 | 103.98
2019-05-17 09:00 | 102.39 | 96.29
2019-05-17 09:30 | 83.72 | 63.87
2019-05-17 10:00 | 87.4 | 31.28
2019-05-17 10:30 | 84.15 | 1.95
2019-05-17 11:00 | 72.84 | 20.87
2019-05-17 11:30 | 91.97 | 59.13
2019-05-17 12:00 | 106.19 | 80.41
2019-05-17 12:30 | 90.51 | 59.57
2019-05-17 13:00 | 64.55 | 51.39
2019-05-17 13:30 | 64.23 | 53.63
2019-05-17 14:00 | 58.3 | 45.16
2019-05-17 14:30 | 60.92 | 48.41
2019-05-17 15:00 | 61.26 | 49.21
2019-05-17 15:30 | 52.26 | 38.18
2019-05-17 16:00 | 77.43 | 62.61
2019-05-17 16:30 | 70.99 | -16.76
2019-05-17 17:00 | 66.17 | 40.97
2019-05-17 17:30 | 64.72 | -27.31
2019-05-17 18:00 | 61.81 | 27.35
2019-05-17 18:30 | 71.32 | -39.9
2019-05-17 19:00 | 54.55 | -6.71
2019-05-17 19:30 | 59.7 | -26.92
2019-05-17 20:00 | 59.75 | -30.03
2019-05-17 20:30 | 69.82 | -47.11
2019-05-17 21:00 | 33.97 | -31.2
2019-05-17 21:30 | 9.1 | 5.28
2019-05-17 22:00 | 10.96 | 1.49
2019-05-17 22:30 | 44.71 | 41.8
2019-05-17 23:00 | 52.23 | 49.24
2019-05-17 23:30 | 22.45 | -18.77
2019-05-18 | 51.18 | -50.99
2019-05-18 00:30 | 23.48 | 10.76
2019-05-18 01:00 | 26.21 | 13.51
2019-05-18 01:30 | 23.06 | 1.88
2019-05-18 02:00 | 24.6 | 5.09
2019-05-18 02:30 | 27.14 | -11.01
2019-05-18 03:00 | 25.8 | -6.67
2019-05-18 03:30 | 24.32 | -4.76
2019-05-18 04:00 | 23.91 | -0.89
2019-05-18 04:30 | 25.08 | 4.16
2019-05-18 05:00 | 25.04 | 3.35
2019-05-18 05:30 | 26.56 | 10.97
2019-05-18 06:00 | 32.58 | 20.41
2019-05-18 06:30 | 37.06 | 27.05
2019-05-18 07:00 | 30.89 | 19.68
2019-05-18 07:30 | 21.85 | -19.45
2019-05-18 08:00 | 44.15 | -44.07
2019-05-18 08:30 | 66.59 | -64.14
2019-05-18 09:00 | 66.6 | -62.32
2019-05-18 09:30 | 42.71 | -37.33
2019-05-18 10:00 | 21.07 | -11.96
2019-05-18 10:30 | 20.61 | 12.89
2019-05-18 11:00 | 17.34 | 5.31
2019-05-18 11:30 | 19.86 | 11.66
2019-05-18 12:00 | 16.31 | -1.5
2019-05-18 12:30 | 19.59 | 12.15
2019-05-18 13:00 | 22.53 | 16.93
2019-05-18 13:30 | 17.7 | 9.73
2019-05-18 14:00 | 14.99 | 5.63
2019-05-18 14:30 | 27.31 | 23.99
2019-05-18 15:00 | 26.97 | 23.3
2019-05-18 15:30 | 35.54 | 33.16
2019-05-18 16:00 | 38.48 | 36.04
2019-05-18 16:30 | 27.69 | 23.23
2019-05-18 17:00 | 51.24 | 46.85
2019-05-18 17:30 | 64.08 | 57.57
2019-05-18 18:00 | 83 | 77.7
2019-05-18 18:30 | 72.52 | 67.05
2019-05-18 19:00 | 85.6 | 81.83
2019-05-18 19:30 | 86.16 | 83.26
2019-05-18 20:00 | 90.24 | 90.22
2019-05-18 20:30 | 87.51 | 86.61
2019-05-18 21:00 | 77.44 | 76.23
2019-05-18 21:30 | 85.8 | 84.36
2019-05-18 22:00 | 78.19 | 76.29
2019-05-18 22:30 | 88.86 | 86.76
2019-05-18 23:00 | 104.97 | 102.83
2019-05-18 23:30 | 77.05 | 73.45
2019-05-19 | 51.62 | 45.4
2019-05-19 00:30 | 45.49 | 38.04
2019-05-19 01:00 | 26.06 | 8.7
2019-05-19 01:30 | 24.59 | -7.29
2019-05-19 02:00 | 29.88 | -19.39
2019-05-19 02:30 | 39.67 | -33.57
2019-05-19 03:00 | 71.03 | -69.55
2019-05-19 03:30 | 29.33 | 13.52
2019-05-19 04:00 | 25.96 | -1.62
2019-05-19 04:30 | 29.18 | -14.5
2019-05-19 05:00 | 28.67 | -12.05
2019-05-19 05:30 | 26.9 | 4.07
2019-05-19 06:00 | 32.65 | 21.15
2019-05-19 06:30 | 44.75 | 38.14
2019-05-19 07:00 | 51.01 | 45.44
2019-05-19 07:30 | 50.46 | 44.34
2019-05-19 08:00 | 32.39 | 20.67
2019-05-19 08:30 | 33 | 22.36
2019-05-19 09:00 | 26.99 | 15.45
2019-05-19 09:30 | 27.01 | 16.66
2019-05-19 10:00 | 27.04 | 15.15
2019-05-19 10:30 | 21.54 | -3.44
2019-05-19 11:00 | 12.98 | -11.26
2019-05-19 11:30 | 5.68 | -2.03
2019-05-19 12:00 | 6.96 | 4.02
2019-05-19 12:30 | 6.32 | -3.82
2019-05-19 13:00 | 7.22 | 4.22
2019-05-19 13:30 | 5.61 | -1.5
2019-05-19 14:00 | 5.76 | -1.53
2019-05-19 14:30 | 14.3 | -13.62
2019-05-19 15:00 | 21.36 | 20.47
2019-05-19 15:30 | 36.71 | 36.2
2019-05-19 16:00 | 55.35 | 54.81
2019-05-19 16:30 | 46.93 | 46.35
2019-05-19 17:00 | 68.56 | 68.12
2019-05-19 17:30 | 96.44 | 96.38
2019-05-19 18:00 | 128.38 | 128.35
2019-05-19 18:30 | 126.76 | 126.66
2019-05-19 19:00 | 124.15 | 123.97
2019-05-19 19:30 | 105.24 | 104.85
2019-05-19 20:00 | 106.64 | 106.16
2019-05-19 20:30 | 110.24 | 109.69
2019-05-19 21:00 | 83.78 | 82.85
2019-05-19 21:30 | 67.06 | 65.6
2019-05-19 22:00 | 57.36 | 55.22
2019-05-19 22:30 | 78.66 | 76.42
2019-05-19 23:00 | 84.86 | 82.46
2019-05-19 23:30 | 73.15 | 70.19
2019-05-20 | 47.04 | 41.68
2019-05-20 00:30 | 39.31 | 32.38
2019-05-20 01:00 | 30.71 | 20.44
2019-05-20 01:30 | 28.98 | 16.96
2019-05-20 02:00 | 27.01 | 12.16
2019-05-20 02:30 | 24.58 | 5.32
2019-05-20 03:00 | 24.37 | -4.37
2019-05-20 03:30 | 24.36 | -1.99
2019-05-20 04:00 | 23.71 | -2.39
2019-05-20 04:30 | 24.28 | 7.28
2019-05-20 05:00 | 27.87 | 16.19
2019-05-20 05:30 | 45.42 | 40.5
2019-05-20 06:00 | 60.7 | 57.89
2019-05-20 06:30 | 77.93 | 76.27
2019-05-20 07:00 | 69.05 | 67.77
2019-05-20 07:30 | 59.25 | 58.48
2019-05-20 08:00 | 35.44 | 22.3
2019-05-20 08:30 | 84.58 | -68.53
2019-05-20 09:00 | 108.96 | -86.2
2019-05-20 09:30 | 84.41 | -54.77
2019-05-20 10:00 | 81.82 | -51.48
2019-05-20 10:30 | 92.5 | -66.24
2019-05-20 11:00 | 107.51 | -84.88
2019-05-20 11:30 | 103.04 | -92.49
2019-05-20 12:00 | 95.41 | -90.99
2019-05-20 12:30 | 83.04 | -78.71
2019-05-20 13:00 | 44.73 | -38.82
2019-05-20 13:30 | 22.45 | 14.33
2019-05-20 14:00 | 29.78 | 29.31
2019-05-20 14:30 | 44.19 | 43.66
2019-05-20 15:00 | 55.61 | 55.44
2019-05-20 15:30 | 80.6 | 80.43
2019-05-20 16:00 | 96.93 | 96.82
2019-05-20 16:30 | 86.37 | 86.1
2019-05-20 17:00 | 92.34 | 91.63
2019-05-20 17:30 | 107.39 | 106.92
2019-05-20 18:00 | 120.72 | 120.37
2019-05-20 18:30 | 114.86 | 114.52
2019-05-20 19:00 | 98.75 | 98.34
2019-05-20 19:30 | 93.31 | 92.91
2019-05-20 20:00 | 80.32 | 79.87
2019-05-20 20:30 | 108.11 | 107.57
2019-05-20 21:00 | 83.38 | 82.39
2019-05-20 21:30 | 65.6 | 63.76
2019-05-20 22:00 | 58.09 | 55.14
2019-05-20 22:30 | 57.01 | 53.52
2019-05-20 23:00 | 69.46 | 66.08
2019-05-20 23:30 | 71.4 | 67.9
2019-05-21 | 42.61 | 35.6
2019-05-21 00:30 | 40.01 | 32.4
2019-05-21 01:00 | 26.42 | 11.48
2019-05-21 01:30 | 26.48 | 9.87
2019-05-21 02:00 | 26.97 | 8.27
2019-05-21 02:30 | 26.04 | 5.02
2019-05-21 03:00 | 25.27 | -1.77
2019-05-21 03:30 | 25.48 | -2.25
2019-05-21 04:00 | 24.91 | -0.73
2019-05-21 04:30 | 29.7 | 15.73
2019-05-21 05:00 | 40.27 | 32.19
2019-05-21 05:30 | 63.1 | 58.95
2019-05-21 06:00 | 97.95 | 95.72
2019-05-21 06:30 | 115.8 | 114.73
2019-05-21 07:00 | 104.04 | 103.02
2019-05-21 07:30 | 103.07 | 102.47
2019-05-21 08:00 | 82.22 | 81.91
2019-05-21 08:30 | 66.17 | 66.1
2019-05-21 09:00 | 79.73 | 79.67
2019-05-21 09:30 | 47.68 | 47.67
2019-05-21 10:00 | 36.15 | 32.59
2019-05-21 10:30 | 28.42 | 19.33
2019-05-21 11:00 | 32.71 | 24.64
2019-05-21 11:30 | 33.51 | 25.4
2019-05-21 12:00 | 23.95 | 7.86
2019-05-21 12:30 | 27.32 | 16.01
2019-05-21 13:00 | 36.69 | 29.29
2019-05-21 13:30 | 38.34 | 31.34
2019-05-21 14:00 | 42.33 | 36.01
2019-05-21 14:30 | 37.96 | 30.55
2019-05-21 15:00 | 46.54 | 41.28
2019-05-21 15:30 | 69.23 | 66.32
2019-05-21 16:00 | 103.83 | 102.03
2019-05-21 16:30 | 86.69 | 80.68
2019-05-21 17:00 | 106.07 | 94.03
2019-05-21 17:30 | 127.96 | 118.14
2019-05-21 18:00 | 139.55 | 135.03
2019-05-21 18:30 | 135.7 | 135.39
2019-05-21 19:00 | 130.22 | 130.21
2019-05-21 19:30 | 130.62 | 129.51
2019-05-21 20:00 | 125.11 | 123.65
2019-05-21 20:30 | 118.84 | 118
2019-05-21 21:00 | 97.84 | 96.74
2019-05-21 21:30 | 82.35 | 80.51
2019-05-21 22:00 | 79.35 | 77.03
2019-05-21 22:30 | 74.17 | 71.43
2019-05-21 23:00 | 100.69 | 98.17
2019-05-21 23:30 | 96.1 | 93.17
2019-05-22 | 66.32 | 61.54
2019-05-22 00:30 | 44.19 | 35.98
2019-05-22 01:00 | 28.49 | 11.4
2019-05-22 01:30 | 27.3 | 4.52
2019-05-22 02:00 | 46.18 | -39.31
2019-05-22 02:30 | 41.54 | -33.93
2019-05-22 03:00 | 37.73 | -29.72
2019-05-22 03:30 | 33.17 | -23.16
2019-05-22 04:00 | 35.01 | -25.91
2019-05-22 04:30 | 25.8 | -7.33
2019-05-22 05:00 | 27.8 | 12.73
2019-05-22 05:30 | 45.74 | 39.48
2019-05-22 06:00 | 74.67 | 71.65
2019-05-22 06:30 | 61.98 | 59.36
2019-05-22 07:00 | 34.37 | 31.07
2019-05-22 07:30 | 44.52 | 44.49
2019-05-22 08:00 | 48.34 | 47.02
2019-05-22 08:30 | 71.45 | 70.2
2019-05-22 09:00 | 59.2 | 52.22
2019-05-22 09:30 | 40.26 | 27.04
2019-05-22 10:00 | 31.51 | -0.11
2019-05-22 10:30 | 43.67 | -24.73
2019-05-22 11:00 | 84.51 | -60.75
2019-05-22 11:30 | 56.38 | 7.45
2019-05-22 12:00 | 60.68 | 26.06
2019-05-22 12:30 | 55.53 | 11.44
2019-05-22 13:00 | 56.27 | 17.81
2019-05-22 13:30 | 55.74 | 10.71
2019-05-22 14:00 | 65.97 | 37.63
2019-05-22 14:30 | 55.13 | 1.83
2019-05-22 15:00 | 61.95 | 30.63
2019-05-22 15:30 | 87.28 | 70.99
2019-05-22 16:00 | 103.88 | 91.35
2019-05-22 16:30 | 93.24 | 78.99
2019-05-22 17:00 | 98.01 | 84.6
2019-05-22 17:30 | 116.69 | 104.78
2019-05-22 18:00 | 118.73 | 106.83
2019-05-22 18:30 | 110.17 | 98.68
2019-05-22 19:00 | 107.32 | 96.33
2019-05-22 19:30 | 107.69 | 99.48
2019-05-22 20:00 | 104.07 | 103.6
2019-05-22 20:30 | 105.25 | 104.93
2019-05-22 21:00 | 82.8 | 82.6
2019-05-22 21:30 | 62.32 | 62.27
2019-05-22 22:00 | 36.62 | 36.54
2019-05-22 22:30 | 40.33 | 40.31
2019-05-22 23:00 | 46.24 | 46.22
2019-05-22 23:30 | 31.25 | -31.24
2019-05-23 | 63.17 | -63.11
2019-05-23 00:30 | 32.04 | -31.9
2019-05-23 01:00 | 70.33 | -70.33
2019-05-23 01:30 | 45.47 | -45.43
2019-05-23 02:00 | 34.08 | -23.02
2019-05-23 02:30 | 36.08 | -24.62
2019-05-23 03:00 | 34.74 | -22.75
2019-05-23 03:30 | 30.03 | -13.64
2019-05-23 04:00 | 27.54 | -5.19
2019-05-23 04:30 | 26.58 | -0.08
2019-05-23 05:00 | 28.27 | 11.98
2019-05-23 05:30 | 29.46 | 18.22
2019-05-23 06:00 | 26.64 | 17.96
2019-05-23 06:30 | 60.91 | 58.99
2019-05-23 07:00 | 93.41 | 92.55
2019-05-23 07:30 | 106.27 | 105.62
2019-05-23 08:00 | 92.97 | 89.54
2019-05-23 08:30 | 38.98 | 25.5
2019-05-23 09:00 | 48.91 | -35.03
2019-05-23 09:30 | 107.9 | -91.35
2019-05-23 10:00 | 109.85 | -90.82
2019-05-23 10:30 | 116.48 | -97.6
2019-05-23 11:00 | 75.78 | -47.62
2019-05-23 11:30 | 61.37 | -21.2
2019-05-23 12:00 | 60.31 | -16.9
2019-05-23 12:30 | 55.01 | 3.53
2019-05-23 13:00 | 54.68 | 10
2019-05-23 13:30 | 56.39 | 15.41
2019-05-23 14:00 | 57.09 | 19.01
2019-05-23 14:30 | 63.75 | 35.09
2019-05-23 15:00 | 63.66 | 36.2
2019-05-23 15:30 | 69.85 | 47.39
2019-05-23 16:00 | 82.36 | 64.91
2019-05-23 16:30 | 96.24 | 82.69
2019-05-23 17:00 | 99.42 | 87.25
2019-05-23 17:30 | 111.32 | 99.12
2019-05-23 18:00 | 126.65 | 115.75
2019-05-23 18:30 | 129.66 | 119.92
2019-05-23 19:00 | 133.62 | 124.82
2019-05-23 19:30 | 142.98 | 135.59
2019-05-23 20:00 | 119.14 | 110.6
2019-05-23 20:30 | 120.09 | 112.63
2019-05-23 21:00 | 95.51 | 94.48
2019-05-23 21:30 | 73.29 | 73.28
2019-05-23 22:00 | 49.34 | 49.34
2019-05-23 22:30 | 42.52 | 42.52
2019-05-23 23:00 | 29.5 | 29.5
2019-05-23 23:30 | 14.79 | -14.62
2019-05-24 | 57.27 | -57.11
2019-05-24 00:30 | 10.28 | -9.87
2019-05-24 01:00 | 13.9 | -13.05
2019-05-24 01:30 | 26.96 | -26.55
2019-05-24 02:00 | 40.06 | -39.92
2019-05-24 02:30 | 35.87 | -35.65
2019-05-24 03:00 | 36.43 | -31.15
2019-05-24 03:30 | 31 | -18.5
2019-05-24 04:00 | 26.61 | -8.77
2019-05-24 04:30 | 26.14 | 7.5
2019-05-24 05:00 | 39.8 | 31.35
2019-05-24 05:30 | 54.23 | 49.19
2019-05-24 06:00 | 60.72 | 57.13
2019-05-24 06:30 | 63.79 | 61.23
2019-05-24 07:00 | 80.2 | 78.76
2019-05-24 07:30 | 87.43 | 87.35
2019-05-24 08:00 | 43.14 | 19.56
2019-05-24 08:30 | 104.48 | -87.3
2019-05-24 09:00 | 93.7 | -74.27
2019-05-24 09:30 | 110.87 | -92.58
2019-05-24 10:00 | 108.92 | -90.11
2019-05-24 10:30 | 117.75 | -98.74
2019-05-24 11:00 | 113.33 | -94.22
2019-05-24 11:30 | 122.23 | -103.88
2019-05-24 12:00 | 119.19 | -100.06
2019-05-24 12:30 | 78.34 | -50.77
2019-05-24 13:00 | 55.36 | -11.46
2019-05-24 13:30 | 53.54 | 4.44
2019-05-24 14:00 | 55.72 | 15.32
2019-05-24 14:30 | 58.74 | 24.45
2019-05-24 15:00 | 59.16 | 27.71
2019-05-24 15:30 | 65.02 | 40.31
2019-05-24 16:00 | 85.07 | 68.86
2019-05-24 16:30 | 79.43 | 61.76
2019-05-24 17:00 | 96.01 | 82.19
2019-05-24 17:30 | 132.17 | 123.85
2019-05-24 18:00 | 137.79 | 129.35
2019-05-24 18:30 | 121.31 | 111.26
2019-05-24 19:00 | 119.42 | 109.89
2019-05-24 19:30 | 96.89 | 95.86
2019-05-24 20:00 | 92.2 | 91.45
2019-05-24 20:30 | 92.74 | 92.21
2019-05-24 21:00 | 86.2 | 85.82
2019-05-24 21:30 | 78.13 | 77.94
2019-05-24 22:00 | 63.55 | 63.45
2019-05-24 22:30 | 69.75 | 69.72
2019-05-24 23:00 | 61.58 | 61.58
2019-05-24 23:30 | 35.73 | 35.71
2019-05-25 | 14.42 | 14.26
2019-05-25 00:30 | 17.4 | 16.9
2019-05-25 01:00 | 6.59 | 5.01
2019-05-25 01:30 | 4.88 | -0.34
2019-05-25 02:00 | 26.49 | 4.8
2019-05-25 02:30 | 29.63 | 12.15
2019-05-25 03:00 | 45.74 | 36.52
2019-05-25 03:30 | 55.84 | 48.53
2019-05-25 04:00 | 51.04 | 42.8
2019-05-25 04:30 | 61.26 | 54.66
2019-05-25 05:00 | 66.24 | 60.33
2019-05-25 05:30 | 72.25 | 66.73
2019-05-25 06:00 | 80.22 | 75.58
2019-05-25 06:30 | 78.08 | 73.87
2019-05-25 07:00 | 77.17 | 72.95
2019-05-25 07:30 | 57.56 | 53.15
2019-05-25 08:00 | 30.48 | 24.39
2019-05-25 08:30 | 19.05 | 12.59
2019-05-25 09:00 | 15.11 | 9.69
2019-05-25 09:30 | 25.38 | 23.1
2019-05-25 10:00 | 39.8 | 38.43
2019-05-25 10:30 | 40.2 | 39.01
2019-05-25 11:00 | 42.71 | 41.56
2019-05-25 11:30 | 65.31 | 64.47
2019-05-25 12:00 | 77.15 | 76.34
2019-05-25 12:30 | 86.6 | 85.84
2019-05-25 13:00 | 93.04 | 92.3
2019-05-25 13:30 | 91.51 | 90.77
2019-05-25 14:00 | 111.73 | 111.11
2019-05-25 14:30 | 117 | 116.49
2019-05-25 15:00 | 111.15 | 110.61
2019-05-25 15:30 | 108.72 | 108.2
2019-05-25 16:00 | 110.13 | 109.66
2019-05-25 16:30 | 102.54 | 102.25
2019-05-25 17:00 | 117.86 | 117.28
2019-05-25 17:30 | 128.18 | 127.24
2019-05-25 18:00 | 119.41 | 112.22
2019-05-25 18:30 | 122.74 | 114.81
2019-05-25 19:00 | 118.4 | 110.87
2019-05-25 19:30 | 112.56 | 107.66
2019-05-25 20:00 | 105.29 | 103.89
2019-05-25 20:30 | 105.41 | 104.3
2019-05-25 21:00 | 85.49 | 84.47
2019-05-25 21:30 | 77.44 | 76.99
2019-05-25 22:00 | 76.02 | 73.35
2019-05-25 22:30 | 95.63 | 93.18
2019-05-25 23:00 | 106.26 | 103.66
2019-05-25 23:30 | 90.69 | 87.33
2019-05-26 | 64.89 | 59.42
2019-05-26 00:30 | 69.29 | 63.36
2019-05-26 01:00 | 54.81 | 46.46
2019-05-26 01:30 | 57.63 | 49.71
2019-05-26 02:00 | 61.03 | 53.5
2019-05-26 02:30 | 60.85 | 53.23
2019-05-26 03:00 | 48.53 | 38.85
2019-05-26 03:30 | 46.8 | 36.48
2019-05-26 04:00 | 43.8 | 32.32
2019-05-26 04:30 | 48.31 | 38.62
2019-05-26 05:00 | 55.2 | 46.56
2019-05-26 05:30 | 66.12 | 59.52
2019-05-26 06:00 | 76.76 | 71.59
2019-05-26 06:30 | 88.64 | 84.78
2019-05-26 07:00 | 91.99 | 88.36
2019-05-26 07:30 | 84.45 | 81.23
2019-05-26 08:00 | 53.66 | 49.46
2019-05-26 08:30 | 39.81 | 35.17
2019-05-26 09:00 | 44.21 | 40.91
2019-05-26 09:30 | 36.48 | 33.78
2019-05-26 10:00 | 54.24 | 52.61
2019-05-26 10:30 | 40.62 | 38.84
2019-05-26 11:00 | 36.36 | 34.69
2019-05-26 11:30 | 35.62 | 33.86
2019-05-26 12:00 | 28.79 | 26.87
2019-05-26 12:30 | 32.84 | 31.31
2019-05-26 13:00 | 39.55 | 38.28
2019-05-26 13:30 | 47.9 | 46.85
2019-05-26 14:00 | 82.67 | 82.14
2019-05-26 14:30 | 123.4 | 123.19
2019-05-26 15:00 | 130.15 | 129.66
2019-05-26 15:30 | 123.6 | 123.2
2019-05-26 16:00 | 155.64 | 155.35
2019-05-26 16:30 | 179.78 | 179.57
2019-05-26 17:00 | 188.53 | 188.33
2019-05-26 17:30 | 206.47 | 206.08
2019-05-26 18:00 | 201.26 | 200.85
2019-05-26 18:30 | 200.85 | 200.52
2019-05-26 19:00 | 201.39 | 201.16
2019-05-26 19:30 | 193.42 | 193.3
2019-05-26 20:00 | 183.04 | 183
2019-05-26 20:30 | 173.57 | 173.56
2019-05-26 21:00 | 140.52 | 140.51
2019-05-26 21:30 | 122.08 | 122.08
2019-05-26 22:00 | 103.05 | 103.04
2019-05-26 22:30 | 109.59 | 109.55
2019-05-26 23:00 | 128.47 | 128.35
2019-05-26 23:30 | 104.68 | 104.49
2019-05-27 | 80.49 | 80.19
2019-05-27 00:30 | 82.27 | 81.54
2019-05-27 01:00 | 89.36 | 85.04
2019-05-27 01:30 | 81.39 | 76.49
2019-05-27 02:00 | 79.97 | 74.98
2019-05-27 02:30 | 76.48 | 71.36
2019-05-27 03:00 | 73.27 | 67.04
2019-05-27 03:30 | 65.78 | 58.93
2019-05-27 04:00 | 69.54 | 63.26
2019-05-27 04:30 | 80.79 | 75.88
2019-05-27 05:00 | 94.73 | 90.81
2019-05-27 05:30 | 115.99 | 113.4
2019-05-27 06:00 | 141.44 | 139.7
2019-05-27 06:30 | 155.15 | 154.12
2019-05-27 07:00 | 154.44 | 153.81
2019-05-27 07:30 | 151.95 | 151.57
2019-05-27 08:00 | 123.82 | 123.73
2019-05-27 08:30 | 70.02 | 68.78
2019-05-27 09:00 | 61.81 | 60.07
2019-05-27 09:30 | 44.15 | 41.14
2019-05-27 10:00 | 35.79 | 29.44
2019-05-27 10:30 | 22.14 | -0.31
2019-05-27 11:00 | 34.08 | -23.08
2019-05-27 11:30 | 70.82 | -59.35
2019-05-27 12:00 | 70.82 | -53.64
2019-05-27 12:30 | 45.09 | 17.26
2019-05-27 13:00 | 46.26 | 24.79
2019-05-27 13:30 | 56.73 | 41.2
2019-05-27 14:00 | 60.62 | 46.16
2019-05-27 14:30 | 65.02 | 51.61
2019-05-27 15:00 | 102.27 | 94.78
2019-05-27 15:30 | 121.86 | 116.06
2019-05-27 16:00 | 153.33 | 149.05
2019-05-27 16:30 | 151.25 | 147.18
2019-05-27 17:00 | 150.99 | 147.45
2019-05-27 17:30 | 145.94 | 133.79
2019-05-27 18:00 | 156.66 | 140.73
2019-05-27 18:30 | 136.18 | 119.05
2019-05-27 19:00 | 135.93 | 121.74
2019-05-27 19:30 | 77.04 | 63.21
2019-05-27 20:00 | 108.24 | 99.73
2019-05-27 20:30 | 113.44 | 106.12
2019-05-27 21:00 | 96.81 | 95.28
2019-05-27 21:30 | 97.02 | 97.01
2019-05-27 22:00 | 102.43 | 102.41
2019-05-27 22:30 | 98.41 | 98.41
2019-05-27 23:00 | 108.75 | 108.75
2019-05-27 23:30 | 81.12 | 81.1
2019-05-28 | 68.28 | 68.21
2019-05-28 00:30 | 74.27 | 74.06
2019-05-28 01:00 | 67.9 | 63.05
2019-05-28 01:30 | 72.83 | 68.13
2019-05-28 02:00 | 77.93 | 73.42
2019-05-28 02:30 | 71.61 | 67.32
2019-05-28 03:00 | 68.41 | 63.64
2019-05-28 03:30 | 75.62 | 71.69
2019-05-28 04:00 | 76.06 | 72.37
2019-05-28 04:30 | 84.85 | 81.61
2019-05-28 05:00 | 109.67 | 107.22
2019-05-28 05:30 | 119.24 | 117.32
2019-05-28 06:00 | 148.73 | 147.64
2019-05-28 06:30 | 163.93 | 163.24
2019-05-28 07:00 | 168.44 | 168
2019-05-28 07:30 | 163.23 | 162.94
2019-05-28 08:00 | 132.18 | 131.91
2019-05-28 08:30 | 86.67 | 86.33
2019-05-28 09:00 | 78.71 | 78.45
2019-05-28 09:30 | 58.07 | 57.81
2019-05-28 10:00 | 42.15 | 41.79
2019-05-28 10:30 | 41.49 | 41.27
2019-05-28 11:00 | 33.33 | 33.15
2019-05-28 11:30 | 8.87 | -8.3
2019-05-28 12:00 | 36.21 | -35.03
2019-05-28 12:30 | 38.55 | -31.6
2019-05-28 13:00 | 28.26 | -19.55
2019-05-28 13:30 | 19.24 | -4.03
2019-05-28 14:00 | 27.37 | 21.08
2019-05-28 14:30 | 49.78 | 46.95
2019-05-28 15:00 | 72.94 | 71.31
2019-05-28 15:30 | 109.05 | 108.1
2019-05-28 16:00 | 140.33 | 139.57
2019-05-28 16:30 | 143.96 | 143.29
2019-05-28 17:00 | 152.32 | 151.59
2019-05-28 17:30 | 168.19 | 167.26
2019-05-28 18:00 | 201.91 | 201.07
2019-05-28 18:30 | 201.26 | 200.49
2019-05-28 19:00 | 201.83 | 201.2
2019-05-28 19:30 | 176.97 | 176.48
2019-05-28 20:00 | 165.54 | 165.2
2019-05-28 20:30 | 160.38 | 160.15
2019-05-28 21:00 | 159.05 | 158.87
2019-05-28 21:30 | 150.94 | 150.89
2019-05-28 22:00 | 143.61 | 143.61
2019-05-28 22:30 | 138.6 | 138.59
2019-05-28 23:00 | 145.76 | 145.72
2019-05-28 23:30 | 101.4 | 99.77
2019-05-29 | 58.33 | 52.52
2019-05-29 00:30 | 44.21 | 35.29
2019-05-29 01:00 | 36.94 | 26.18
2019-05-29 01:30 | 36.2 | 25.81
2019-05-29 02:00 | 33.4 | 19.68
2019-05-29 02:30 | 39.2 | 28.21
2019-05-29 03:00 | 43.85 | 34.89
2019-05-29 03:30 | 60.5 | 53.95
2019-05-29 04:00 | 83.88 | 78.88
2019-05-29 04:30 | 99 | 94.56
2019-05-29 05:00 | 126.38 | 122.99
2019-05-29 05:30 | 141.57 | 138.86
2019-05-29 06:00 | 151.01 | 148.49
2019-05-29 06:30 | 162.79 | 161.42
2019-05-29 07:00 | 195.95 | 195.04
2019-05-29 07:30 | 178.38 | 178.26
2019-05-29 08:00 | 171.02 | 170.93
2019-05-29 08:30 | 167.27 | 166.91
2019-05-29 09:00 | 160.58 | 160.29
2019-05-29 09:30 | 149.97 | 149.73
2019-05-29 10:00 | 143.49 | 143.26
2019-05-29 10:30 | 130.97 | 130.72
2019-05-29 11:00 | 127.1 | 126.81
2019-05-29 11:30 | 125.49 | 125.2
2019-05-29 12:00 | 127.78 | 127.49
2019-05-29 12:30 | 130.75 | 130.47
2019-05-29 13:00 | 134.3 | 133.99
2019-05-29 13:30 | 137.96 | 137.64
2019-05-29 14:00 | 143.36 | 143.01
2019-05-29 14:30 | 147.15 | 146.79
2019-05-29 15:00 | 148.42 | 148.07
2019-05-29 15:30 | 151.41 | 151.19
2019-05-29 16:00 | 143.04 | 143.03
2019-05-29 16:30 | 120.48 | 120.48
2019-05-29 17:00 | 128.26 | 125.18
2019-05-29 17:30 | 158.92 | 155.31
2019-05-29 18:00 | 185.14 | 181.55
2019-05-29 18:30 | 168.1 | 164.52
2019-05-29 19:00 | 170.85 | 167.75
2019-05-29 19:30 | 169.03 | 166.3
2019-05-29 20:00 | 177.94 | 175.69
2019-05-29 20:30 | 184.36 | 182.62
2019-05-29 21:00 | 156.59 | 156.04
2019-05-29 21:30 | 123.65 | 123.09
2019-05-29 22:00 | 108.16 | 107.06
2019-05-29 22:30 | 115.36 | 114.25
2019-05-29 23:00 | 116.96 | 115.52
2019-05-29 23:30 | 65.51 | 62.58
2019-05-30 | 31.73 | 25.09
2019-05-30 00:30 | 23.71 | 12.59
2019-05-30 01:00 | 28.06 | 18.32
2019-05-30 01:30 | 22.86 | 8.31
2019-05-30 02:00 | 14.33 | 6.95
2019-05-30 02:30 | 20.99 | 15.06
2019-05-30 03:00 | 24.76 | 20.48
2019-05-30 03:30 | 32.25 | 29
2019-05-30 04:00 | 57.86 | 55.77
2019-05-30 04:30 | 79.7 | 78.14
2019-05-30 05:00 | 97.53 | 96.3
2019-05-30 05:30 | 98.29 | 97
2019-05-30 06:00 | 133.75 | 132.88
2019-05-30 06:30 | 163.25 | 162.83
2019-05-30 07:00 | 188.98 | 188.85
2019-05-30 07:30 | 149.9 | 149.89
2019-05-30 08:00 | 134.57 | 134.45
2019-05-30 08:30 | 127.49 | 127.13
2019-05-30 09:00 | 119.43 | 119.15
2019-05-30 09:30 | 110.75 | 110.43
2019-05-30 10:00 | 106.66 | 106.3
2019-05-30 10:30 | 94.04 | 93.66
2019-05-30 11:00 | 92.69 | 92.31
2019-05-30 11:30 | 89.01 | 88.64
2019-05-30 12:00 | 90.8 | 90.42
2019-05-30 12:30 | 92.23 | 91.87
2019-05-30 13:00 | 95.55 | 95.17
2019-05-30 13:30 | 100.82 | 100.56
2019-05-30 14:00 | 103.55 | 103.28
2019-05-30 14:30 | 108.74 | 108.46
2019-05-30 15:00 | 107.93 | 107.89
2019-05-30 15:30 | 108.92 | 108.91
2019-05-30 16:00 | 119.6 | 119.58
2019-05-30 16:30 | 141.84 | 141.79
2019-05-30 17:00 | 135.22 | 134.93
2019-05-30 17:30 | 140.18 | 140.17
2019-05-30 18:00 | 147.3 | 146.4
2019-05-30 18:30 | 148.37 | 147.35
2019-05-30 19:00 | 154.56 | 153.72
2019-05-30 19:30 | 154.4 | 153.59
2019-05-30 20:00 | 161.98 | 161.96
2019-05-30 20:30 | 145.32 | 145.13
2019-05-30 21:00 | 144.48 | 144.11
2019-05-30 21:30 | 136.27 | 135.66
2019-05-30 22:00 | 124.61 | 123.41
2019-05-30 22:30 | 114.72 | 113.14
2019-05-30 23:00 | 116.22 | 114.31
2019-05-30 23:30 | 70.25 | 66.6
2019-05-31 | 30.92 | 21.37
2019-05-31 00:30 | 26.96 | 15.57
2019-05-31 01:00 | 22 | 7.55
2019-05-31 01:30 | 21.33 | 4.37
2019-05-31 02:00 | 24.21 | 11.56
2019-05-31 02:30 | 25.98 | 21.84
2019-05-31 03:00 | 43.65 | 40.69
2019-05-31 03:30 | 59.63 | 57.43
2019-05-31 04:00 | 92 | 90.64
2019-05-31 04:30 | 101.72 | 100.46
2019-05-31 05:00 | 114.36 | 113.23
2019-05-31 05:30 | 114.02 | 112.79
2019-05-31 06:00 | 146.48 | 145.63
2019-05-31 06:30 | 165.48 | 165.01
2019-05-31 07:00 | 193.63 | 193.6
2019-05-31 07:30 | 210.23 | 210.23
2019-05-31 08:00 | 181.55 | 181.48
2019-05-31 08:30 | 131.57 | 131.4
2019-05-31 09:00 | 100.94 | 100.62
2019-05-31 09:30 | 102.82 | 102.46
2019-05-31 10:00 | 72.62 | 72.62
2019-05-31 10:30 | 47.38 | 47.36
2019-05-31 11:00 | 28.76 | 28.72
2019-05-31 11:30 | 13.69 | 13.62
2019-05-31 12:00 | 13.2 | 13.19
2019-05-31 12:30 | 6.56 | 6.56
2019-05-31 13:00 | 19.08 | 19.05
2019-05-31 13:30 | 34.2 | 34.08
2019-05-31 14:00 | 37.8 | 37
2019-05-31 14:30 | 52.33 | 51.78
2019-05-31 15:00 | 87.55 | 87.11
2019-05-31 15:30 | 109.11 | 108.72
2019-05-31 16:00 | 153.55 | 153.3
2019-05-31 16:30 | 167.19 | 166.98
2019-05-31 17:00 | 174.7 | 174.7
2019-05-31 17:30 | 190.21 | 190.18
2019-05-31 18:00 | 217.61 | 217.5
2019-05-31 18:30 | 202.42 | 202.24
2019-05-31 19:00 | 202.17 | 201.95
2019-05-31 19:30 | 184.83 | 184.74
2019-05-31 20:00 | 186.65 | 186.63
2019-05-31 20:30 | 191.36 | 191.35
2019-05-31 21:00 | 184.31 | 184.31
2019-05-31 21:30 | 161.86 | 161.45
2019-05-31 22:00 | 154.13 | 152.71
2019-05-31 22:30 | 153.58 | 152.37
2019-05-31 23:00 | 162.58 | 161.08
2019-05-31 23:30 | 132.15 | 129.92
2019-06-01 | 99.71 | 96.64
2019-06-01 00:30 | 92.24 | 88.12
2019-06-01 01:00 | 73.53 | 67.79
2019-06-01 01:30 | 53.42 | 45.06
2019-06-01 02:00 | 43.56 | 33.16
2019-06-01 02:30 | 35.66 | 21.65
2019-06-01 03:00 | 41.28 | 27.06
2019-06-01 03:30 | 54.18 | 43.77
2019-06-01 04:00 | 68.17 | 60.04
2019-06-01 04:30 | 84.8 | 78.48
2019-06-01 05:00 | 113.38 | 108.86
2019-06-01 05:30 | 133.98 | 130.61
2019-06-01 06:00 | 142.17 | 139.4
2019-06-01 06:30 | 154.82 | 152.71
2019-06-01 07:00 | 167.37 | 165.76
2019-06-01 07:30 | 181.16 | 180.19
2019-06-01 08:00 | 173.36 | 172.61
2019-06-01 08:30 | 156.24 | 155.64
2019-06-01 09:00 | 125 | 124.92
2019-06-01 09:30 | 76.04 | 75.89
2019-06-01 10:00 | 49.34 | 49.21
2019-06-01 10:30 | 29.04 | 28.82
2019-06-01 11:00 | 13.07 | 12.46
2019-06-01 11:30 | 48.02 | -47.44
2019-06-01 12:00 | 85.39 | -84.65
2019-06-01 12:30 | 77.1 | -76.36
2019-06-01 13:00 | 8.47 | -7.36
2019-06-01 13:30 | 5.47 | 3.43
2019-06-01 14:00 | 24.04 | 23.71
2019-06-01 14:30 | 47.54 | 47.44
2019-06-01 15:00 | 65.08 | 65.03
2019-06-01 15:30 | 108.97 | 108.93
2019-06-01 16:00 | 143.91 | 143.88
2019-06-01 16:30 | 137.88 | 137.79
2019-06-01 17:00 | 145.98 | 145.98
2019-06-01 17:30 | 144.47 | 143.42
2019-06-01 18:00 | 140.69 | 139.71
2019-06-01 18:30 | 120.98 | 119.62
2019-06-01 19:00 | 125.12 | 123.4
2019-06-01 19:30 | 143.04 | 142.59
2019-06-01 20:00 | 151.07 | 150.89
2019-06-01 20:30 | 142.75 | 142.5
2019-06-01 21:00 | 136.7 | 136.69
2019-06-01 21:30 | 142.55 | 142.07
2019-06-01 22:00 | 156.35 | 155.84
2019-06-01 22:30 | 172.5 | 172
2019-06-01 23:00 | 178.25 | 178
2019-06-01 23:30 | 167.82 | 166.11
2019-06-02 | 154.07 | 151.72
2019-06-02 00:30 | 142.34 | 139.46
2019-06-02 01:00 | 134.27 | 131.18
2019-06-02 01:30 | 127.29 | 124.03
2019-06-02 02:00 | 120.88 | 117.14
2019-06-02 02:30 | 114.5 | 110.7
2019-06-02 03:00 | 106.35 | 102.72
2019-06-02 03:30 | 102.65 | 98.69
2019-06-02 04:00 | 97.58 | 93.68
2019-06-02 04:30 | 98.69 | 94.92
2019-06-02 05:00 | 100.94 | 97.37
2019-06-02 05:30 | 105.4 | 102.16
2019-06-02 06:00 | 110.22 | 107.31
2019-06-02 06:30 | 118.06 | 115.52
2019-06-02 07:00 | 124.91 | 122.69
2019-06-02 07:30 | 111.21 | 108.56
2019-06-02 08:00 | 21.46 | 2.95
2019-06-02 08:30 | 18.68 | 4
2019-06-02 09:00 | 26.34 | 20.96
2019-06-02 09:30 | 29.84 | 26.13
2019-06-02 10:00 | 39.91 | 37.5
2019-06-02 10:30 | 55.89 | 54.1
2019-06-02 11:00 | 56.4 | 55.04
2019-06-02 11:30 | 48.46 | 46.73
2019-06-02 12:00 | 36.58 | 33.73
2019-06-02 12:30 | 32.99 | 29.92
2019-06-02 13:00 | 61.28 | 59.41
2019-06-02 13:30 | 71.29 | 69.79
2019-06-02 14:00 | 85.81 | 84.6
2019-06-02 14:30 | 90.38 | 89.29
2019-06-02 15:00 | 95.33 | 94.3
2019-06-02 15:30 | 99.11 | 98.02
2019-06-02 16:00 | 126.87 | 125.94
2019-06-02 16:30 | 133.3 | 133
2019-06-02 17:00 | 137.15 | 136.96
2019-06-02 17:30 | 181.98 | 178.44
2019-06-02 18:00 | 194.63 | 189.61
2019-06-02 18:30 | 205.71 | 201.27
2019-06-02 19:00 | 207.88 | 203.83
2019-06-02 19:30 | 177.42 | 173.33
2019-06-02 20:00 | 158.25 | 156.51
2019-06-02 20:30 | 151.52 | 151.5
2019-06-02 21:00 | 154.64 | 154.64
2019-06-02 21:30 | 146.12 | 146.12
2019-06-02 22:00 | 122.99 | 122.96
2019-06-02 22:30 | 130.41 | 130.35
2019-06-02 23:00 | 123.79 | 123.64
2019-06-02 23:30 | 93.91 | 93.68
2019-06-03 | 55.09 | 54.58
2019-06-03 00:30 | 71.9 | 68.76
2019-06-03 01:00 | 53.66 | 44.55
2019-06-03 01:30 | 48.6 | 37.87
2019-06-03 02:00 | 75.17 | 68.07
2019-06-03 02:30 | 76.19 | 69.1
2019-06-03 03:00 | 82.13 | 75.65
2019-06-03 03:30 | 83.27 | 76.9
2019-06-03 04:00 | 97.72 | 92.63
2019-06-03 04:30 | 93.93 | 88.87
2019-06-03 05:00 | 106.59 | 102.47
2019-06-03 05:30 | 124.31 | 121.23
2019-06-03 06:00 | 128.36 | 126.05
2019-06-03 06:30 | 161.06 | 159.92
2019-06-03 07:00 | 174.92 | 174.04
2019-06-03 07:30 | 181.47 | 181.44
2019-06-03 08:00 | 168 | 167.77
2019-06-03 08:30 | 120.96 | 120.38
2019-06-03 09:00 | 100.88 | 100.04
2019-06-03 09:30 | 89.88 | 88.79
2019-06-03 10:00 | 65.43 | 63.94
2019-06-03 10:30 | 67.2 | 65.92
2019-06-03 11:00 | 53.28 | 51.47
2019-06-03 11:30 | 52.96 | 51.21
2019-06-03 12:00 | 43.39 | 41.03
2019-06-03 12:30 | 41.58 | 39.28
2019-06-03 13:00 | 50.02 | 48.07
2019-06-03 13:30 | 53.64 | 51.88
2019-06-03 14:00 | 71.08 | 69.7
2019-06-03 14:30 | 73.96 | 72.83
2019-06-03 15:00 | 69.77 | 68.67
2019-06-03 15:30 | 116.55 | 116
2019-06-03 16:00 | 113.48 | 112.98
2019-06-03 16:30 | 97.51 | 96.95
2019-06-03 17:00 | 120.44 | 118.91
2019-06-03 17:30 | 150.56 | 146.59
2019-06-03 18:00 | 173.13 | 160.15
2019-06-03 18:30 | 152.72 | 138.59
2019-06-03 19:00 | 138.17 | 131.42
2019-06-03 19:30 | 149.88 | 144.32
2019-06-03 20:00 | 137.55 | 132.08
2019-06-03 20:30 | 141.65 | 137.07
2019-06-03 21:00 | 123.64 | 118.77
2019-06-03 21:30 | 118.04 | 116.89
2019-06-03 22:00 | 120.46 | 120.4
2019-06-03 22:30 | 107.79 | 107.66
2019-06-03 23:00 | 105.33 | 105.1
2019-06-03 23:30 | 71.93 | 71.64
2019-06-04 | 26.06 | 25.29
2019-06-04 00:30 | 36.56 | 35.74
2019-06-04 01:00 | 26.16 | 24.99
2019-06-04 01:30 | 20.88 | 19.36
2019-06-04 02:00 | 28.13 | 16.16
2019-06-04 02:30 | 28.15 | 0.51
2019-06-04 03:00 | 29.57 | 7.11
2019-06-04 03:30 | 32.66 | 15.85
2019-06-04 04:00 | 39.17 | 27.4
2019-06-04 04:30 | 46.45 | 37.01
2019-06-04 05:00 | 59.6 | 53.1
2019-06-04 05:30 | 91.69 | 88.24
2019-06-04 06:00 | 138.73 | 137.14
2019-06-04 06:30 | 180.15 | 179.49
2019-06-04 07:00 | 195.18 | 194.89
2019-06-04 07:30 | 189 | 188.7
2019-06-04 08:00 | 210.88 | 210.43
2019-06-04 08:30 | 197.11 | 196.66
2019-06-04 09:00 | 177.28 | 176.92
2019-06-04 09:30 | 140.68 | 140.63
2019-06-04 10:00 | 138.98 | 138.89
2019-06-04 10:30 | 52.47 | 52.24
2019-06-04 11:00 | 12.59 | -7.44
2019-06-04 11:30 | 50.86 | -47.72
2019-06-04 12:00 | 66.5 | -61.23
2019-06-04 12:30 | 72.14 | -71.12
2019-06-04 13:00 | 52.92 | -52.89
2019-06-04 13:30 | 29.84 | 29.58
2019-06-04 14:00 | 113.05 | 112.84
2019-06-04 14:30 | 130.3 | 130.13
2019-06-04 15:00 | 122.32 | 122.26
2019-06-04 15:30 | 130.43 | 130.42
2019-06-04 16:00 | 167.41 | 167.34
2019-06-04 16:30 | 208.18 | 207.73
2019-06-04 17:00 | 220.26 | 219.9
2019-06-04 17:30 | 237.4 | 237.32
2019-06-04 18:00 | 233.08 | 233.08
2019-06-04 18:30 | 231.31 | 231.31
2019-06-04 19:00 | 240.93 | 240.92
2019-06-04 19:30 | 252.28 | 252.25
2019-06-04 20:00 | 242.8 | 242.7
2019-06-04 20:30 | 247.75 | 247.58
2019-06-04 21:00 | 230.84 | 230.5
2019-06-04 21:30 | 205.73 | 205.06
2019-06-04 22:00 | 182.59 | 181.66
2019-06-04 22:30 | 172.6 | 171.6
2019-06-04 23:00 | 162.68 | 161.25
2019-06-04 23:30 | 113.59 | 111.56
2019-06-05 | 58.37 | 53.64
2019-06-05 00:30 | 47.62 | 40.47
2019-06-05 01:00 | 42.03 | 32.71
2019-06-05 01:30 | 46.36 | 37.51
2019-06-05 02:00 | 46.61 | 38.82
2019-06-05 02:30 | 38.89 | 31.56
2019-06-05 03:00 | 51.99 | 46.85
2019-06-05 03:30 | 62.07 | 58.05
2019-06-05 04:00 | 67.4 | 63.98
2019-06-05 04:30 | 54.25 | 49.98
2019-06-05 05:00 | 98.05 | 94.97
2019-06-05 05:30 | 145.06 | 143.19
2019-06-05 06:00 | 151.96 | 150.9
2019-06-05 06:30 | 179.85 | 179.34
2019-06-05 07:00 | 197.99 | 197.97
2019-06-05 07:30 | 221.71 | 216.85
2019-06-05 08:00 | 219.04 | 213.84
2019-06-05 08:30 | 198.87 | 193.29
2019-06-05 09:00 | 149.42 | 144.68
2019-06-05 09:30 | 126.19 | 125.47
2019-06-05 10:00 | 87.54 | 86.55
2019-06-05 10:30 | 24.58 | 18.93
2019-06-05 11:00 | 38.73 | 35.36
2019-06-05 11:30 | 70.64 | 69.32
2019-06-05 12:00 | 26.48 | 22.23
2019-06-05 12:30 | 31.12 | 27.73
2019-06-05 13:00 | 18.19 | 1.54
2019-06-05 13:30 | 93.61 | 92.54
2019-06-05 14:00 | 105.96 | 105.17
2019-06-05 14:30 | 113.42 | 112.66
2019-06-05 15:00 | 152.74 | 152.09
2019-06-05 15:30 | 160.18 | 159.54
2019-06-05 16:00 | 95.6 | 94.57
2019-06-05 16:30 | 92.83 | 85.04
2019-06-05 17:00 | 179.47 | 173.4
2019-06-05 17:30 | 136.07 | 125.98
2019-06-05 18:00 | 143.29 | 132.59
2019-06-05 18:30 | 128.98 | 117.39
2019-06-05 19:00 | 158.07 | 149.33
2019-06-05 19:30 | 162.83 | 155.07
2019-06-05 20:00 | 181.98 | 175.97
2019-06-05 20:30 | 176.94 | 171.47
2019-06-05 21:00 | 99.49 | 97.78
2019-06-05 21:30 | 109.68 | 109.56
2019-06-05 22:00 | 79.29 | 79.27
2019-06-05 22:30 | 103.99 | 103.99
2019-06-05 23:00 | 122.53 | 122.52
2019-06-05 23:30 | 86.26 | 86.26
2019-06-06 | 35 | 34.94
2019-06-06 00:30 | 3.44 | 1.94
2019-06-06 01:00 | 21.72 | -21.51
2019-06-06 01:30 | 9.42 | -8.15
2019-06-06 02:00 | 13.46 | -12.17
2019-06-06 02:30 | 15.86 | -14.77
2019-06-06 03:00 | 15.46 | -6.96
2019-06-06 03:30 | 30.19 | -16.17
2019-06-06 04:00 | 26.65 | -6.3
2019-06-06 04:30 | 31.1 | 17.19
2019-06-06 05:00 | 30.45 | 17.98
2019-06-06 05:30 | 31.47 | 22.5
2019-06-06 06:00 | 82.08 | 79.81
2019-06-06 06:30 | 161.03 | 161.03
2019-06-06 07:00 | 177.75 | 177.46
2019-06-06 07:30 | 204.95 | 202.53
2019-06-06 08:00 | 198.44 | 195.46
2019-06-06 08:30 | 168.96 | 167.93
2019-06-06 09:00 | 146.12 | 146.12
2019-06-06 09:30 | 129.1 | 129.08
2019-06-06 10:00 | 122.7 | 122.68
2019-06-06 10:30 | 106.62 | 106.61
2019-06-06 11:00 | 91.68 | 91.68
2019-06-06 11:30 | 17.14 | 17.03
2019-06-06 12:00 | 2.69 | 2.31
2019-06-06 12:30 | 29.94 | 29.85
2019-06-06 13:00 | 55.17 | 55.11
2019-06-06 13:30 | 114.39 | 114.36
2019-06-06 14:00 | 54.62 | 54.57
2019-06-06 14:30 | 42.2 | 42.17
2019-06-06 15:00 | 55.15 | 55.11
2019-06-06 15:30 | 59.53 | 59.45
2019-06-06 16:00 | 60.92 | 60.79
2019-06-06 16:30 | 64.28 | 64.18
2019-06-06 17:00 | 70.97 | 70.96
2019-06-06 17:30 | 125.14 | 125.14
2019-06-06 18:00 | 203.68 | 203.67
2019-06-06 18:30 | 214.82 | 214.8
2019-06-06 19:00 | 202.74 | 202.74
2019-06-06 19:30 | 177.05 | 177.05
2019-06-06 20:00 | 187.41 | 187.33
2019-06-06 20:30 | 116.11 | 116.02
2019-06-06 21:00 | 63.18 | -53.46
2019-06-06 21:30 | 16.93 | -9.27
2019-06-06 22:00 | 8.64 | -8.32
2019-06-06 22:30 | 55.22 | 53.06
2019-06-06 23:00 | 75.35 | 73.37
2019-06-06 23:30 | 50.36 | 46.83
2019-06-07 | 18.91 | 4.55
2019-06-07 00:30 | 21.33 | 7.14
2019-06-07 01:00 | 21.83 | -17.25
2019-06-07 01:30 | 22.27 | -18.17
2019-06-07 02:00 | 16.6 | -8.13
2019-06-07 02:30 | 16.19 | 4.34
2019-06-07 03:00 | 23.23 | 16.93
2019-06-07 03:30 | 32.68 | 28.12
2019-06-07 04:00 | 42.39 | 38.46
2019-06-07 04:30 | 65.77 | 61.71
2019-06-07 05:00 | 82.69 | 79.44
2019-06-07 05:30 | 112.19 | 109.47
2019-06-07 06:00 | 119.15 | 116.55
2019-06-07 06:30 | 117.34 | 115.63
2019-06-07 07:00 | 149.15 | 148.83
2019-06-07 07:30 | 166.75 | 166.68
2019-06-07 08:00 | 166.37 | 166.35
2019-06-07 08:30 | 127.12 | 127.1
2019-06-07 09:00 | 124.43 | 124.39
2019-06-07 09:30 | 92.8 | 92.74
2019-06-07 10:00 | 48.86 | 48.78
2019-06-07 10:30 | 19.37 | -19.2
2019-06-07 11:00 | 68.32 | -67.65
2019-06-07 11:30 | 17.87 | 17.87
2019-06-07 12:00 | 94.14 | 94.11
2019-06-07 12:30 | 98.54 | 98.47
2019-06-07 13:00 | 112.29 | 112.24
2019-06-07 13:30 | 144.67 | 144.61
2019-06-07 14:00 | 146.2 | 146.13
2019-06-07 14:30 | 163.5 | 163.44
2019-06-07 15:00 | 140.36 | 140.25
2019-06-07 15:30 | 136.47 | 136.35
2019-06-07 16:00 | 144.51 | 144.38
2019-06-07 16:30 | 126.62 | 126.49
2019-06-07 17:00 | 160.32 | 160.25
2019-06-07 17:30 | 171.18 | 171.15
2019-06-07 18:00 | 147.33 | 147.31
2019-06-07 18:30 | 98.42 | 98.34
2019-06-07 19:00 | 43.36 | -36.99
2019-06-07 19:30 | 55.4 | -50.22
2019-06-07 20:00 | 6.67 | -1.74
2019-06-07 20:30 | 114.16 | 114
2019-06-07 21:00 | 115.78 | 115.21
2019-06-07 21:30 | 96.32 | 95.42
2019-06-07 22:00 | 74.77 | 73.45
2019-06-07 22:30 | 114.8 | 113.98
2019-06-07 23:00 | 129.99 | 128.87
2019-06-07 23:30 | 91.9 | 90.85
2019-06-08 | 25.7 | 25.69
2019-06-08 00:30 | 9.29 | 8.18
2019-06-08 01:00 | 15.06 | 3.71
2019-06-08 01:30 | 14.93 | 1.74
2019-06-08 02:00 | 15.62 | 1.67
2019-06-08 02:30 | 17.3 | 4.37
2019-06-08 03:00 | 26 | 17.83
2019-06-08 03:30 | 28.5 | 20.85
2019-06-08 04:00 | 43.09 | 38.26
2019-06-08 04:30 | 67.55 | 64.66
2019-06-08 05:00 | 89.9 | 86.71
2019-06-08 05:30 | 83.04 | 78.66
2019-06-08 06:00 | 74.01 | 68.92
2019-06-08 06:30 | 65.61 | 60.26
2019-06-08 07:00 | 55.85 | 49.83
2019-06-08 07:30 | 67.79 | 64.66
2019-06-08 08:00 | 110.64 | 108.87
2019-06-08 08:30 | 138.35 | 137.03
2019-06-08 09:00 | 154.03 | 153.14
2019-06-08 09:30 | 129 | 128.8
2019-06-08 10:00 | 147.56 | 147.37
2019-06-08 10:30 | 180.73 | 180.65
2019-06-08 11:00 | 160.96 | 160.84
2019-06-08 11:30 | 134.34 | 134.1
2019-06-08 12:00 | 122.92 | 122.61
2019-06-08 12:30 | 156.61 | 156.37
2019-06-08 13:00 | 139.91 | 139.58
2019-06-08 13:30 | 137.46 | 137.06
2019-06-08 14:00 | 162.04 | 161.82
2019-06-08 14:30 | 186.92 | 186.76
2019-06-08 15:00 | 189.02 | 188.88
2019-06-08 15:30 | 182.23 | 182.11
2019-06-08 16:00 | 151.58 | 151.46
2019-06-08 16:30 | 110.72 | 110.65
2019-06-08 17:00 | 139.12 | 139.04
2019-06-08 17:30 | 154.5 | 152.96
2019-06-08 18:00 | 84.52 | 80.36
2019-06-08 18:30 | 44.53 | 12.59
2019-06-08 19:00 | 60.43 | 46.91
2019-06-08 19:30 | 33.45 | 30.87
2019-06-08 20:00 | 73.02 | 73.01
2019-06-08 20:30 | 85.96 | 85.94
2019-06-08 21:00 | 38.46 | 38.21
2019-06-08 21:30 | 5.59 | 2.6
2019-06-08 22:00 | 24.15 | 22.81
2019-06-08 22:30 | 79.67 | 78.33
2019-06-08 23:00 | 92.86 | 90.88
2019-06-08 23:30 | 58.25 | 56.11
2019-06-09 | 28.92 | 24.85
2019-06-09 00:30 | 25.99 | 25.12
2019-06-09 01:00 | 17.18 | 17.13
2019-06-09 01:30 | 29.79 | 29.79
2019-06-09 02:00 | 20.44 | 20.41
2019-06-09 02:30 | 29.92 | 28.69
2019-06-09 03:00 | 49.94 | 44.15
2019-06-09 03:30 | 66.55 | 57.97
2019-06-09 04:00 | 72.05 | 63.57
2019-06-09 04:30 | 86.76 | 80.22
2019-06-09 05:00 | 94.26 | 88.31
2019-06-09 05:30 | 96.27 | 90.46
2019-06-09 06:00 | 97.86 | 92.54
2019-06-09 06:30 | 100.17 | 95.59
2019-06-09 07:00 | 90.15 | 85.17
2019-06-09 07:30 | 60.55 | 54.27
2019-06-09 08:00 | 51.4 | 47.74
2019-06-09 08:30 | 33.26 | 33.26
2019-06-09 09:00 | 27.75 | 27.7
2019-06-09 09:30 | 22.78 | 22.61
2019-06-09 10:00 | 36.05 | 35.94
2019-06-09 10:30 | 27.16 | 26.98
2019-06-09 11:00 | 10.81 | 10.27
2019-06-09 11:30 | 13.54 | 13.14
2019-06-09 12:00 | 35.11 | 35.02
2019-06-09 12:30 | 33.28 | 33.16
2019-06-09 13:00 | 43.93 | 43.85
2019-06-09 13:30 | 71.68 | 71.64
2019-06-09 14:00 | 78.4 | 78.37
2019-06-09 14:30 | 79.53 | 79.5
2019-06-09 15:00 | 82.9 | 82.88
2019-06-09 15:30 | 76.04 | 76
2019-06-09 16:00 | 82.05 | 81.82
2019-06-09 16:30 | 65.58 | 61.24
2019-06-09 17:00 | 84.53 | 80.61
2019-06-09 17:30 | 148.72 | 141.95
2019-06-09 18:00 | 174.73 | 167.56
2019-06-09 18:30 | 169.63 | 162.43
2019-06-09 19:00 | 145.06 | 137.36
2019-06-09 19:30 | 126.3 | 118.09
2019-06-09 20:00 | 112.35 | 103.69
2019-06-09 20:30 | 109.34 | 101.12
2019-06-09 21:00 | 86.01 | 76.5
2019-06-09 21:30 | 80.84 | 71.98
2019-06-09 22:00 | 71.65 | 62.53
2019-06-09 22:30 | 91.53 | 85.22
2019-06-09 23:00 | 98.01 | 92.8
2019-06-09 23:30 | 83.85 | 80.09
2019-06-10 | 61.71 | 60.86
2019-06-10 00:30 | 85.4 | 84.94
2019-06-10 01:00 | 99.85 | 99.43
2019-06-10 01:30 | 68.75 | 68.74
2019-06-10 02:00 | 57.56 | 56.19
2019-06-10 02:30 | 84.33 | 83.27
2019-06-10 03:00 | 91.29 | 90.28
2019-06-10 03:30 | 88.98 | 86.97
2019-06-10 04:00 | 70.26 | 63
2019-06-10 04:30 | 70.76 | 64.57
2019-06-10 05:00 | 67.59 | 61.92
2019-06-10 05:30 | 80.42 | 76.49
2019-06-10 06:00 | 116.49 | 114.23
2019-06-10 06:30 | 166.49 | 166.32
2019-06-10 07:00 | 193.4 | 193.13
2019-06-10 07:30 | 208.43 | 208.28
2019-06-10 08:00 | 197.21 | 197.07
2019-06-10 08:30 | 167.22 | 167.05
2019-06-10 09:00 | 133.17 | 132.97
2019-06-10 09:30 | 96.79 | 96.61
2019-06-10 10:00 | 95.4 | 95.24
2019-06-10 10:30 | 87.25 | 87.08
2019-06-10 11:00 | 69.97 | 69.88
2019-06-10 11:30 | 81.01 | 80.98
2019-06-10 12:00 | 92.36 | 92.33
2019-06-10 12:30 | 104.84 | 104.76
2019-06-10 13:00 | 101.08 | 100.99
2019-06-10 13:30 | 105.87 | 105.79
2019-06-10 14:00 | 115.88 | 115.81
2019-06-10 14:30 | 131.18 | 131.14
2019-06-10 15:00 | 141.55 | 141.49
2019-06-10 15:30 | 151.76 | 151.7
2019-06-10 16:00 | 175.24 | 175.17
2019-06-10 16:30 | 180.37 | 180.32
2019-06-10 17:00 | 177.62 | 177.59
2019-06-10 17:30 | 194.4 | 189.83
2019-06-10 18:00 | 210.65 | 203.42
2019-06-10 18:30 | 184.07 | 176.52
2019-06-10 19:00 | 169.91 | 163.62
2019-06-10 19:30 | 143.6 | 141.03
2019-06-10 20:00 | 137.43 | 135.29
2019-06-10 20:30 | 126.93 | 126.71
2019-06-10 21:00 | 114.49 | 114.01
2019-06-10 21:30 | 106.22 | 105.44
2019-06-10 22:00 | 87.75 | 86.62
2019-06-10 22:30 | 106.18 | 104.91
2019-06-10 23:00 | 112.68 | 111.12
2019-06-10 23:30 | 74.09 | 71.5
2019-06-11 | 53.85 | 49.47
2019-06-11 00:30 | 47.24 | 40.18
2019-06-11 01:00 | 35.91 | 24.06
2019-06-11 01:30 | 31.3 | 17.71
2019-06-11 02:00 | 24.84 | 9.05
2019-06-11 02:30 | 26 | 11.92
2019-06-11 03:00 | 45.94 | 38.7
2019-06-11 03:30 | 51.38 | 43.26
2019-06-11 04:00 | 63.31 | 57.11
2019-06-11 04:30 | 71.42 | 65.87
2019-06-11 05:00 | 87.14 | 82.17
2019-06-11 05:30 | 92.21 | 87.24
2019-06-11 06:00 | 95.15 | 90.63
2019-06-11 06:30 | 118.86 | 115.84
2019-06-11 07:00 | 144.84 | 142.97
2019-06-11 07:30 | 173.86 | 173.66
2019-06-11 08:00 | 146.16 | 145.99
2019-06-11 08:30 | 167.22 | 167.15
2019-06-11 09:00 | 113.88 | 113.83
2019-06-11 09:30 | 46.22 | 46.13
2019-06-11 10:00 | 17.46 | 17.46
2019-06-11 10:30 | 21.77 | 21.76
2019-06-11 11:00 | 8.75 | -8.6
2019-06-11 11:30 | 5.02 | 4.83
2019-06-11 12:00 | 3.09 | 2.76
2019-06-11 12:30 | 7.08 | 7.04
2019-06-11 13:00 | 17.08 | 17.07
2019-06-11 13:30 | 36.62 | 36.59
2019-06-11 14:00 | 56.89 | 56.85
2019-06-11 14:30 | 68.53 | 68.44
2019-06-11 15:00 | 92.47 | 92.44
2019-06-11 15:30 | 117.56 | 117.56
2019-06-11 16:00 | 129.37 | 129.37
2019-06-11 16:30 | 113.52 | 113.52
2019-06-11 17:00 | 115.2 | 114.65
2019-06-11 17:30 | 145.04 | 144.85
2019-06-11 18:00 | 154.67 | 154.62
2019-06-11 18:30 | 138.42 | 138.38
2019-06-11 19:00 | 138.67 | 138.6
2019-06-11 19:30 | 138.49 | 138.38
2019-06-11 20:00 | 126.84 | 126.8
2019-06-11 20:30 | 125.73 | 125.6
2019-06-11 21:00 | 99.09 | 98.64
2019-06-11 21:30 | 88.04 | 87.07
2019-06-11 22:00 | 103.96 | 102.57
2019-06-11 22:30 | 125.62 | 124.26
2019-06-11 23:00 | 132.73 | 131.26
2019-06-11 23:30 | 95.13 | 92.69
2019-06-12 | 75.99 | 73.06
2019-06-12 00:30 | 69.5 | 66.78
2019-06-12 01:00 | 74.94 | 71.56
2019-06-12 01:30 | 69.92 | 65.57
2019-06-12 02:00 | 66.35 | 62.18
2019-06-12 02:30 | 65.43 | 64.83
2019-06-12 03:00 | 63.4 | 62.78
2019-06-12 03:30 | 61.08 | 60.44
2019-06-12 04:00 | 51.51 | 50.62
2019-06-12 04:30 | 67.79 | 67.16
2019-06-12 05:00 | 88.07 | 87.52
2019-06-12 05:30 | 122.64 | 122.11
2019-06-12 06:00 | 144.05 | 143.67
2019-06-12 06:30 | 169.37 | 169
2019-06-12 07:00 | 179.55 | 178.62
2019-06-12 07:30 | 196.31 | 195.81
2019-06-12 08:00 | 143.54 | 142.79
2019-06-12 08:30 | 86.86 | 86.64
2019-06-12 09:00 | 41.02 | 41.01
2019-06-12 09:30 | 42.19 | -39.12
2019-06-12 10:00 | 82.61 | -75.7
2019-06-12 10:30 | 29.92 | -16.62
2019-06-12 11:00 | 36.84 | -26.83
2019-06-12 11:30 | 23.74 | 4.05
2019-06-12 12:00 | 26.28 | 12.14
2019-06-12 12:30 | 34.12 | 25.63
2019-06-12 13:00 | 41.61 | 36.07
2019-06-12 13:30 | 47.68 | 43.36
2019-06-12 14:00 | 67.4 | 64.5
2019-06-12 14:30 | 101.31 | 99.5
2019-06-12 15:00 | 111.66 | 110.07
2019-06-12 15:30 | 128.94 | 127.77
2019-06-12 16:00 | 152.54 | 151.64
2019-06-12 16:30 | 134.25 | 133.28
2019-06-12 17:00 | 111.3 | 108.84
2019-06-12 17:30 | 109.63 | 103.43
2019-06-12 18:00 | 116.33 | 110.88
2019-06-12 18:30 | 94.06 | 87.97
2019-06-12 19:00 | 99.05 | 94.23
2019-06-12 19:30 | 98.64 | 94.73
2019-06-12 20:00 | 110.66 | 107.74
2019-06-12 20:30 | 105.37 | 103.06
2019-06-12 21:00 | 70.03 | 69.15
2019-06-12 21:30 | 52.33 | 50.37
2019-06-12 22:00 | 45.42 | 42.34
2019-06-12 22:30 | 51.67 | 48.86
2019-06-12 23:00 | 72.51 | 69.96
2019-06-12 23:30 | 41.09 | 35.86
2019-06-13 | 26.4 | 18.5
2019-06-13 00:30 | 39.44 | 34.93
2019-06-13 01:00 | 42.56 | 37.96
2019-06-13 01:30 | 58.41 | 54.78
2019-06-13 02:00 | 62.22 | 59.88
2019-06-13 02:30 | 50.07 | 49.43
2019-06-13 03:00 | 51.23 | 43.83
2019-06-13 03:30 | 48.23 | 40.5
2019-06-13 04:00 | 48.76 | 40.77
2019-06-13 04:30 | 62.61 | 56.62
2019-06-13 05:00 | 81.02 | 76.23
2019-06-13 05:30 | 109.41 | 105.8
2019-06-13 06:00 | 138.44 | 135.98
2019-06-13 06:30 | 140.38 | 138.97
2019-06-13 07:00 | 140.42 | 140.42
2019-06-13 07:30 | 164.3 | 164.12
2019-06-13 08:00 | 159.31 | 158.92
2019-06-13 08:30 | 166.88 | 166.41
2019-06-13 09:00 | 70.91 | 67.32
2019-06-13 09:30 | 40.16 | -38.33
2019-06-13 10:00 | 19 | -16.03
2019-06-13 10:30 | 34.11 | 33.72
2019-06-13 11:00 | 47.22 | 47.19
2019-06-13 11:30 | 58.45 | 58.44
2019-06-13 12:00 | 32.29 | 32.24
2019-06-13 12:30 | 60.8 | 60.73
2019-06-13 13:00 | 93.61 | 93.58
2019-06-13 13:30 | 76.79 | 76.77
2019-06-13 14:00 | 82.71 | 82.7
2019-06-13 14:30 | 104.25 | 104.22
2019-06-13 15:00 | 81.95 | 81.94
2019-06-13 15:30 | 91.59 | 91.59
2019-06-13 16:00 | 100.83 | 100.83
2019-06-13 16:30 | 94.68 | 94.66
2019-06-13 17:00 | 115.82 | 115.82
2019-06-13 17:30 | 127.02 | 126.04
2019-06-13 18:00 | 130.59 | 116.7
2019-06-13 18:30 | 130.53 | 121.66
2019-06-13 19:00 | 140.61 | 136.1
2019-06-13 19:30 | 127.43 | 123.4
2019-06-13 20:00 | 114.2 | 112.23
2019-06-13 20:30 | 100.42 | 100.38
2019-06-13 21:00 | 71.08 | 70.93
2019-06-13 21:30 | 63.29 | 62.55
2019-06-13 22:00 | 40.85 | 38.71
2019-06-13 22:30 | 38.51 | 35.57
2019-06-13 23:00 | 48.44 | 45.29
2019-06-13 23:30 | 31.78 | 27.1
2019-06-14 | 29.39 | 21.86
2019-06-14 00:30 | 32 | 26.86
2019-06-14 01:00 | 29.08 | 24.57
2019-06-14 01:30 | 28.86 | 24.49
2019-06-14 02:00 | 31.4 | 27.4
2019-06-14 02:30 | 40.17 | 36.68
2019-06-14 03:00 | 50.6 | 48.78
2019-06-14 03:30 | 62.22 | 62.22
2019-06-14 04:00 | 74.86 | 74.83
2019-06-14 04:30 | 92.35 | 92.33
2019-06-14 05:00 | 112.37 | 112.35
2019-06-14 05:30 | 109.29 | 109.22
2019-06-14 06:00 | 115.69 | 115.57
2019-06-14 06:30 | 120.64 | 119.41
2019-06-14 07:00 | 108.57 | 106.93
2019-06-14 07:30 | 113.29 | 113.07
2019-06-14 08:00 | 63.31 | 63.19
2019-06-14 08:30 | 31.19 | 30.97
2019-06-14 09:00 | 39.1 | 39.04
2019-06-14 09:30 | 6.03 | 4.39
2019-06-14 10:00 | 33.4 | -32.52
2019-06-14 10:30 | 17.98 | 16.94
2019-06-14 11:00 | 23.01 | 21.91
2019-06-14 11:30 | 24.34 | 23.36
2019-06-14 12:00 | 32.51 | 31.82
2019-06-14 12:30 | 37.48 | 37.34
2019-06-14 13:00 | 47.1 | 47.03
2019-06-14 13:30 | 60.35 | 60.31
2019-06-14 14:00 | 61.63 | 61.56
2019-06-14 14:30 | 92.11 | 92.1
2019-06-14 15:00 | 80.41 | 80.41
2019-06-14 15:30 | 87.76 | 87.75
2019-06-14 16:00 | 80.91 | 80.91
2019-06-14 16:30 | 60.27 | 60.24
2019-06-14 17:00 | 47.36 | 47.19
2019-06-14 17:30 | 93.47 | 93.24
2019-06-14 18:00 | 87.45 | 87.28
2019-06-14 18:30 | 70.31 | 70.23
2019-06-14 19:00 | 88.13 | 88.12
2019-06-14 19:30 | 66.13 | 66.12
2019-06-14 20:00 | 42.83 | 42.8
2019-06-14 20:30 | 49.99 | 49.84
2019-06-14 21:00 | 41.6 | 41.17
2019-06-14 21:30 | 23.52 | 22.09
2019-06-14 22:00 | 24.97 | 22.37
2019-06-14 22:30 | 41.65 | 39.06
2019-06-14 23:00 | 62.06 | 59.64
2019-06-14 23:30 | 41.48 | 37.28
2019-06-15 | 23.37 | 12.82
2019-06-15 00:30 | 21.03 | 2.1
2019-06-15 01:00 | 25.9 | -14.2
2019-06-15 01:30 | 32.62 | -24.14
2019-06-15 02:00 | 36.46 | -28.25
2019-06-15 02:30 | 37.04 | -27.75
2019-06-15 03:00 | 33.31 | -27.17
2019-06-15 03:30 | 26.23 | -18.64
2019-06-15 04:00 | 15.88 | -4.15
2019-06-15 04:30 | 8.66 | 8.28
2019-06-15 05:00 | 17.77 | 17.61
2019-06-15 05:30 | 12.53 | 12.29
2019-06-15 06:00 | 24.41 | 24.13
2019-06-15 06:30 | 22.29 | 22.19
2019-06-15 07:00 | 26.31 | 26.26
2019-06-15 07:30 | 52.18 | 52.08
2019-06-15 08:00 | 101.61 | 101.61
2019-06-15 08:30 | 151.47 | 151.47
2019-06-15 09:00 | 159.19 | 159.18
2019-06-15 09:30 | 131.6 | 131.59
2019-06-15 10:00 | 43.03 | 42.41
2019-06-15 10:30 | 14.55 | -11.58
2019-06-15 11:00 | 37.55 | -37.52
2019-06-15 11:30 | 34.02 | -33.95
2019-06-15 12:00 | 17.16 | -17.12
2019-06-15 12:30 | 19.81 | -19.65
2019-06-15 13:00 | 27.76 | -27.67
2019-06-15 13:30 | 7.17 | 6.42
2019-06-15 14:00 | 22.78 | 22.45
2019-06-15 14:30 | 45.59 | 45.43
2019-06-15 15:00 | 64.9 | 64.67
2019-06-15 15:30 | 77.49 | 77.22
2019-06-15 16:00 | 95.61 | 95.22
2019-06-15 16:30 | 85.25 | 84.9
2019-06-15 17:00 | 89.24 | 89.04
2019-06-15 17:30 | 83.2 | 83.1
2019-06-15 18:00 | 93.04 | 92.95
2019-06-15 18:30 | 81.75 | 81.75
2019-06-15 19:00 | 70.54 | 69.68
2019-06-15 19:30 | 76.64 | 75.92
2019-06-15 20:00 | 68.52 | 67.94
2019-06-15 20:30 | 46.85 | 45.86
2019-06-15 21:00 | 40.16 | 38.52
2019-06-15 21:30 | 45.12 | 42.62
2019-06-15 22:00 | 55.01 | 52.58
2019-06-15 22:30 | 59.11 | 56.72
2019-06-15 23:00 | 67.3 | 64.2
2019-06-15 23:30 | 51.4 | 47.95
2019-06-16 | 30.55 | 24.97
2019-06-16 00:30 | 23.39 | 22.23
2019-06-16 01:00 | 11.29 | 8.91
2019-06-16 01:30 | 6.08 | 0.57
2019-06-16 02:00 | 17.13 | -16.52
2019-06-16 02:30 | 13.07 | -11.83
2019-06-16 03:00 | 3.77 | -2.82
2019-06-16 03:30 | 20.22 | 11.99
2019-06-16 04:00 | 31.69 | 4.91
2019-06-16 04:30 | 33.38 | 11.74
2019-06-16 05:00 | 36.63 | 18.93
2019-06-16 05:30 | 42.64 | 29.93
2019-06-16 06:00 | 51.76 | 42.27
2019-06-16 06:30 | 42.83 | 32.03
2019-06-16 07:00 | 51.28 | 42.62
2019-06-16 07:30 | 41.34 | 32.13
2019-06-16 08:00 | 33.33 | 23.99
2019-06-16 08:30 | 19.09 | -18.55
2019-06-16 09:00 | 28.2 | 27.83
2019-06-16 09:30 | 36.96 | 36.27
2019-06-16 10:00 | 61.74 | 61.35
2019-06-16 10:30 | 43.47 | 36.6
2019-06-16 11:00 | 48.46 | 37.93
2019-06-16 11:30 | 74.68 | 69.41
2019-06-16 12:00 | 51.49 | 43.49
2019-06-16 12:30 | 40.68 | -25.75
2019-06-16 13:00 | 28.77 | 0.89
2019-06-16 13:30 | 29.78 | 8.87
2019-06-16 14:00 | 32.56 | 16.55
2019-06-16 14:30 | 28.69 | 5.63
2019-06-16 15:00 | 43.65 | 35.12
2019-06-16 15:30 | 73.25 | 69.05
2019-06-16 16:00 | 97.58 | 92.57
2019-06-16 16:30 | 142.87 | 137.86
2019-06-16 17:00 | 108.03 | 99.93
2019-06-16 17:30 | 85.6 | 72.94
2019-06-16 18:00 | 85.79 | 73.37
2019-06-16 18:30 | 80.59 | 67.86
2019-06-16 19:00 | 84.3 | 73.5
2019-06-16 19:30 | 92.36 | 84.05
2019-06-16 20:00 | 105.96 | 99.69
2019-06-16 20:30 | 100.3 | 98.69
2019-06-16 21:00 | 88.27 | 87.54
2019-06-16 21:30 | 76.13 | 75.54
2019-06-16 22:00 | 50.5 | 49.68
2019-06-16 22:30 | 53.29 | 51.42
2019-06-16 23:00 | 58.07 | 53.9
2019-06-16 23:30 | 44.13 | 38.09
2019-06-17 | 39.59 | 32.53
2019-06-17 00:30 | 46.72 | 40.02
2019-06-17 01:00 | 39.51 | 30.52
2019-06-17 01:30 | 40.58 | 31.76
2019-06-17 02:00 | 33.23 | 22.57
2019-06-17 02:30 | 38.27 | 28.97
2019-06-17 03:00 | 27.8 | 12.64
2019-06-17 03:30 | 29.99 | 17.49
2019-06-17 04:00 | 35.46 | 26.31
2019-06-17 04:30 | 53.3 | 47.93
2019-06-17 05:00 | 64.48 | 60.53
2019-06-17 05:30 | 95.3 | 93.11
2019-06-17 06:00 | 133.11 | 131.82
2019-06-17 06:30 | 149.94 | 149.25
2019-06-17 07:00 | 176.79 | 176.42
2019-06-17 07:30 | 197.76 | 197.61
2019-06-17 08:00 | 174.34 | 173.79
2019-06-17 08:30 | 130.94 | 130.19
2019-06-17 09:00 | 99.68 | 98.7
2019-06-17 09:30 | 84.6 | 83.05
2019-06-17 10:00 | 53.94 | 51.04
2019-06-17 10:30 | 33.51 | 28.29
2019-06-17 11:00 | 21.05 | 8.6
2019-06-17 11:30 | 19.22 | 3.99
2019-06-17 12:00 | 19.01 | 1.08
2019-06-17 12:30 | 21.13 | -8.58
2019-06-17 13:00 | 18.4 | 2.33
2019-06-17 13:30 | 19.67 | -5.17
2019-06-17 14:00 | 20.1 | 1.7
2019-06-17 14:30 | 30.9 | 25.05
2019-06-17 15:00 | 39.79 | 36.9
2019-06-17 15:30 | 65.21 | 63.84
2019-06-17 16:00 | 69.34 | 65.43
2019-06-17 16:30 | 108.53 | 99.3
2019-06-17 17:00 | 112.19 | 104.71
2019-06-17 17:30 | 143.65 | 141.51
2019-06-17 18:00 | 163.77 | 161.46
2019-06-17 18:30 | 135 | 132.49
2019-06-17 19:00 | 157.81 | 155.92
2019-06-17 19:30 | 133.01 | 131.07
2019-06-17 20:00 | 155.73 | 154.04
2019-06-17 20:30 | 152.27 | 151.99
2019-06-17 21:00 | 130.67 | 130.66
2019-06-17 21:30 | 119.01 | 118.97
2019-06-17 22:00 | 114.93 | 114.92
2019-06-17 22:30 | 110.11 | 110.03
2019-06-17 23:00 | 120.45 | 120.32
2019-06-17 23:30 | 99.61 | 99.51
2019-06-18 | 72.54 | 72.3
2019-06-18 00:30 | 77.28 | 77.03
2019-06-18 01:00 | 70.61 | 64.87
2019-06-18 01:30 | 75.46 | 69.38
2019-06-18 02:00 | 85.55 | 79.85
2019-06-18 02:30 | 73.6 | 66.73
2019-06-18 03:00 | 70.25 | 62.74
2019-06-18 03:30 | 77.91 | 71.4
2019-06-18 04:00 | 101.41 | 96.62
2019-06-18 04:30 | 127 | 123.57
2019-06-18 05:00 | 127.18 | 123.83
2019-06-18 05:30 | 144.76 | 142.35
2019-06-18 06:00 | 157.3 | 155.79
2019-06-18 06:30 | 170.17 | 169.6
2019-06-18 07:00 | 168.96 | 168.96
2019-06-18 07:30 | 183.83 | 182.23
2019-06-18 08:00 | 189.59 | 183.31
2019-06-18 08:30 | 174.44 | 169.93
2019-06-18 09:00 | 159.24 | 157.36
2019-06-18 09:30 | 155.62 | 155.09
2019-06-18 10:00 | 140.8 | 140.38
2019-06-18 10:30 | 122.55 | 122.11
2019-06-18 11:00 | 121.68 | 121.26
2019-06-18 11:30 | 122.62 | 122.28
2019-06-18 12:00 | 118.09 | 117.74
2019-06-18 12:30 | 120.27 | 119.92
2019-06-18 13:00 | 131.04 | 130.7
2019-06-18 13:30 | 136.67 | 136.34
2019-06-18 14:00 | 140.18 | 139.87
2019-06-18 14:30 | 145.52 | 145.2
2019-06-18 15:00 | 148.5 | 148.21
2019-06-18 15:30 | 149.38 | 149.12
2019-06-18 16:00 | 152.1 | 152.06
2019-06-18 16:30 | 143.75 | 143.73
2019-06-18 17:00 | 158.17 | 158.14
2019-06-18 17:30 | 172.32 | 172.25
2019-06-18 18:00 | 185.54 | 185.52
2019-06-18 18:30 | 182.88 | 182.87
2019-06-18 19:00 | 174.64 | 174.62
2019-06-18 19:30 | 168.64 | 168.59
2019-06-18 20:00 | 167.87 | 167.82
2019-06-18 20:30 | 156.13 | 155.77
2019-06-18 21:00 | 154.22 | 153.66
2019-06-18 21:30 | 150.82 | 149.91
2019-06-18 22:00 | 145.51 | 144.19
2019-06-18 22:30 | 143.88 | 142.34
2019-06-18 23:00 | 169.1 | 167.54
2019-06-18 23:30 | 144.77 | 142.79
2019-06-19 | 129.8 | 127.07
2019-06-19 00:30 | 108.09 | 104.99
2019-06-19 01:00 | 72.76 | 67.84
2019-06-19 01:30 | 61.95 | 56.38
2019-06-19 02:00 | 40.27 | 31.08
2019-06-19 02:30 | 41.19 | 32.62
2019-06-19 03:00 | 38.95 | 30.05
2019-06-19 03:30 | 38.54 | 29.84
2019-06-19 04:00 | 35.74 | 27.45
2019-06-19 04:30 | 52.92 | 47.04
2019-06-19 05:00 | 80.36 | 75.93
2019-06-19 05:30 | 97.79 | 93.66
2019-06-19 06:00 | 149.08 | 146.9
2019-06-19 06:30 | 176.89 | 176.86
2019-06-19 07:00 | 167.1 | 167.05
2019-06-19 07:30 | 183.33 | 179.31
2019-06-19 08:00 | 192.73 | 178.34
2019-06-19 08:30 | 182.25 | 170.1
2019-06-19 09:00 | 163.78 | 161.25
2019-06-19 09:30 | 156.12 | 154.25
2019-06-19 10:00 | 151.15 | 145.49
2019-06-19 10:30 | 140.93 | 134.64
2019-06-19 11:00 | 144.33 | 137.96
2019-06-19 11:30 | 135.06 | 128.33
2019-06-19 12:00 | 131.77 | 124.84
2019-06-19 12:30 | 132.71 | 125.86
2019-06-19 13:00 | 135.67 | 128.93
2019-06-19 13:30 | 142.43 | 136.22
2019-06-19 14:00 | 150.47 | 144.69
2019-06-19 14:30 | 153.21 | 143.89
2019-06-19 15:00 | 152.97 | 142.44
2019-06-19 15:30 | 90.58 | 76.95
2019-06-19 16:00 | 113.73 | 103.57
2019-06-19 16:30 | 120.93 | 111.97
2019-06-19 17:00 | 147.23 | 139.37
2019-06-19 17:30 | 141.66 | 132.69
2019-06-19 18:00 | 114.09 | 100.94
2019-06-19 18:30 | 89.35 | 70.55
2019-06-19 19:00 | 82.64 | 70.35
2019-06-19 19:30 | 36.23 | 4.05
2019-06-19 20:00 | 81.21 | 76.33
2019-06-19 20:30 | 79.29 | 78.25
2019-06-19 21:00 | 57.64 | 57.07
2019-06-19 21:30 | 59.49 | 58.69
2019-06-19 22:00 | 63.31 | 61.92
2019-06-19 22:30 | 84.46 | 82.85
2019-06-19 23:00 | 100.67 | 98.8
2019-06-19 23:30 | 85.94 | 83.64
2019-06-20 | 80.9 | 80.53
2019-06-20 00:30 | 91.45 | 91.38
2019-06-20 01:00 | 84.43 | 84.34
2019-06-20 01:30 | 56.08 | 55.87
2019-06-20 02:00 | 38.78 | 38.52
2019-06-20 02:30 | 31.41 | 31.11
2019-06-20 03:00 | 35.13 | 34.93
2019-06-20 03:30 | 34.8 | 34.62
2019-06-20 04:00 | 30.69 | 30.42
2019-06-20 04:30 | 51.21 | 51.09
2019-06-20 05:00 | 72.67 | 72.65
2019-06-20 05:30 | 107.34 | 107.25
2019-06-20 06:00 | 152.78 | 152.39
2019-06-20 06:30 | 173.05 | 172.03
2019-06-20 07:00 | 186.55 | 186.22
2019-06-20 07:30 | 189.7 | 189.6
2019-06-20 08:00 | 206.78 | 206.18
2019-06-20 08:30 | 191.71 | 190.99
2019-06-20 09:00 | 177.19 | 176.33
2019-06-20 09:30 | 175.6 | 174.71
2019-06-20 10:00 | 116.22 | 115.03
2019-06-20 10:30 | 109.82 | 108.48
2019-06-20 11:00 | 112.76 | 111.79
2019-06-20 11:30 | 64.93 | 64.85
2019-06-20 12:00 | 48.34 | 48.24
2019-06-20 12:30 | 63.47 | 63.41
2019-06-20 13:00 | 110.07 | 110.04
2019-06-20 13:30 | 119.55 | 119.52
2019-06-20 14:00 | 130.84 | 130.82
2019-06-20 14:30 | 132.44 | 132.41
2019-06-20 15:00 | 115.15 | 115.1
2019-06-20 15:30 | 129.7 | 129.65
2019-06-20 16:00 | 154.58 | 154.5
2019-06-20 16:30 | 126 | 125.93
2019-06-20 17:00 | 104.58 | 98.9
2019-06-20 17:30 | 117.65 | 104.52
2019-06-20 18:00 | 121.3 | 105.62
2019-06-20 18:30 | 118.15 | 110.34
2019-06-20 19:00 | 108.92 | 102.54
2019-06-20 19:30 | 111.77 | 106.96
2019-06-20 20:00 | 117.71 | 113.97
2019-06-20 20:30 | 102.04 | 100.38
2019-06-20 21:00 | 93.12 | 92.88
2019-06-20 21:30 | 94.15 | 93.35
2019-06-20 22:00 | 97.33 | 95.71
2019-06-20 22:30 | 82.64 | 80.47
2019-06-20 23:00 | 105.41 | 102.89
2019-06-20 23:30 | 102.16 | 98.39
2019-06-21 | 91.29 | 86.81
2019-06-21 00:30 | 76.27 | 72.48
2019-06-21 01:00 | 60 | 59.7
2019-06-21 01:30 | 36.12 | 35.65
2019-06-21 02:00 | 12.19 | 10.44
2019-06-21 02:30 | 9.7 | 6.76
2019-06-21 03:00 | 12.56 | 9.97
2019-06-21 03:30 | 10.38 | 7.01
2019-06-21 04:00 | 10.2 | 7.05
2019-06-21 04:30 | 27.46 | 26.25
2019-06-21 05:00 | 42.56 | 41.61
2019-06-21 05:30 | 67.96 | 67.3
2019-06-21 06:00 | 109.86 | 109.47
2019-06-21 06:30 | 118.11 | 117.94
2019-06-21 07:00 | 121.01 | 120.98
2019-06-21 07:30 | 150.9 | 150.58
2019-06-21 08:00 | 175.08 | 174.91
2019-06-21 08:30 | 149.68 | 149.53
2019-06-21 09:00 | 135.76 | 135.61
2019-06-21 09:30 | 159.11 | 158.85
2019-06-21 10:00 | 66.93 | 64.07
2019-06-21 10:30 | 19.62 | 8.27
2019-06-21 11:00 | 20 | -9.89
2019-06-21 11:30 | 30.32 | -26.15
2019-06-21 12:00 | 27.47 | -22.6
2019-06-21 12:30 | 20.83 | -11.42
2019-06-21 13:00 | 88.94 | -88.92
2019-06-21 13:30 | 100.97 | -100.62
2019-06-21 14:00 | 39.43 | -39.43
2019-06-21 14:30 | 5.94 | 5.56
2019-06-21 15:00 | 20.04 | 19.62
2019-06-21 15:30 | 41.96 | 41.55
2019-06-21 16:00 | 73.36 | 72.99
2019-06-21 16:30 | 79.37 | 79.09
2019-06-21 17:00 | 70.31 | 70.17
2019-06-21 17:30 | 97.97 | 97.91
2019-06-21 18:00 | 96.84 | 96.68
2019-06-21 18:30 | 88.17 | 88.03
2019-06-21 19:00 | 112.59 | 112.23
2019-06-21 19:30 | 125.99 | 125.97
2019-06-21 20:00 | 121.02 | 120.72
2019-06-21 20:30 | 128.67 | 128.46
2019-06-21 21:00 | 119.26 | 119.18
2019-06-21 21:30 | 105.49 | 105.49
2019-06-21 22:00 | 97.49 | 96.22
2019-06-21 22:30 | 114.68 | 113.45
2019-06-21 23:00 | 112.22 | 110.56
2019-06-21 23:30 | 83.07 | 80.46
2019-06-22 | 60.93 | 56.48
2019-06-22 00:30 | 66.03 | 61.39
2019-06-22 01:00 | 50.14 | 43.81
2019-06-22 01:30 | 38.81 | 30
2019-06-22 02:00 | 32.94 | 19.8
2019-06-22 02:30 | 28.66 | 10.19
2019-06-22 03:00 | 30.16 | 12.42
2019-06-22 03:30 | 38.32 | 25.77
2019-06-22 04:00 | 44.29 | 33.16
2019-06-22 04:30 | 43.86 | 32.82
2019-06-22 05:00 | 49.85 | 40.2
2019-06-22 05:30 | 63.78 | 55.88
2019-06-22 06:00 | 82.44 | 77.11
2019-06-22 06:30 | 93.18 | 89.12
2019-06-22 07:00 | 96.31 | 92.39
2019-06-22 07:30 | 105.57 | 102.8
2019-06-22 08:00 | 104.8 | 102.47
2019-06-22 08:30 | 107.37 | 105.4
2019-06-22 09:00 | 106.77 | 104.72
2019-06-22 09:30 | 12.46 | 2.32
2019-06-22 10:00 | 22.94 | -17.89
2019-06-22 10:30 | 57.26 | -57.1
2019-06-22 11:00 | 75.01 | -75.01
2019-06-22 11:30 | 82.85 | -82.84
2019-06-22 12:00 | 86.57 | -86.56
2019-06-22 12:30 | 58.61 | -58.11
2019-06-22 13:00 | 82.6 | -82.6
2019-06-22 13:30 | 78.36 | -78.34
2019-06-22 14:00 | 54.77 | -54.39
2019-06-22 14:30 | 70.39 | -70.38
2019-06-22 15:00 | 36.92 | -35.65
2019-06-22 15:30 | 12.07 | 0.75
2019-06-22 16:00 | 40.55 | 38.77
2019-06-22 16:30 | 59.21 | 58.4
2019-06-22 17:00 | 73.41 | 73.06
2019-06-22 17:30 | 91.55 | 88.05
2019-06-22 18:00 | 118.92 | 106.53
2019-06-22 18:30 | 117.74 | 109.53
2019-06-22 19:00 | 137.89 | 134.44
2019-06-22 19:30 | 136.79 | 135.4
2019-06-22 20:00 | 134.58 | 134.54
2019-06-22 20:30 | 134.88 | 134.76
2019-06-22 21:00 | 126.23 | 125.94
2019-06-22 21:30 | 130.24 | 129.8
2019-06-22 22:00 | 127.4 | 126.69
2019-06-22 22:30 | 145.88 | 145.09
2019-06-22 23:00 | 162.83 | 161.7
2019-06-22 23:30 | 137.79 | 136.05
2019-06-23 | 120.76 | 118.21
2019-06-23 00:30 | 108.26 | 104.41
2019-06-23 01:00 | 93.44 | 88.92
2019-06-23 01:30 | 74.52 | 68.76
2019-06-23 02:00 | 57.42 | 49.7
2019-06-23 02:30 | 43.51 | 32.95
2019-06-23 03:00 | 42.02 | 31.08
2019-06-23 03:30 | 46.07 | 36.48
2019-06-23 04:00 | 52.89 | 44.53
2019-06-23 04:30 | 65.98 | 59.85
2019-06-23 05:00 | 72.99 | 67.3
2019-06-23 05:30 | 81.44 | 76.26
2019-06-23 06:00 | 96.29 | 91.79
2019-06-23 06:30 | 91.38 | 86.5
2019-06-23 07:00 | 90.51 | 85.58
2019-06-23 07:30 | 90.74 | 87.4
2019-06-23 08:00 | 87.26 | 84.1
2019-06-23 08:30 | 57.67 | 54.74
2019-06-23 09:00 | 37.17 | 33.45
2019-06-23 09:30 | 22.89 | 16.4
2019-06-23 10:00 | 26.27 | 20.54
2019-06-23 10:30 | 27.88 | 21.06
2019-06-23 11:00 | 30.3 | 24.63
2019-06-23 11:30 | 21.74 | -18.47
2019-06-23 12:00 | 15.28 | -11.62
2019-06-23 12:30 | 30.3 | -28.87
2019-06-23 13:00 | 23.01 | -20.66
2019-06-23 13:30 | 14.81 | -10.65
2019-06-23 14:00 | 12.64 | 2.45
2019-06-23 14:30 | 23.29 | 19.76
2019-06-23 15:00 | 27.18 | 24.42
2019-06-23 15:30 | 47.35 | 45.79
2019-06-23 16:00 | 61.45 | 60.38
2019-06-23 16:30 | 81.74 | 81
2019-06-23 17:00 | 103.13 | 102.88
2019-06-23 17:30 | 147.47 | 147.36
2019-06-23 18:00 | 173.33 | 169.2
2019-06-23 18:30 | 170.38 | 161.74
2019-06-23 19:00 | 156.99 | 149.3
2019-06-23 19:30 | 151.47 | 149.06
2019-06-23 20:00 | 139.81 | 137.63
2019-06-23 20:30 | 132.11 | 131.82
2019-06-23 21:00 | 119.81 | 119.14
2019-06-23 21:30 | 115.12 | 114.2
2019-06-23 22:00 | 127.07 | 126.02
2019-06-23 22:30 | 156.99 | 155.76
2019-06-23 23:00 | 164.6 | 162.98
2019-06-23 23:30 | 140.97 | 138.82
2019-06-24 | 130.16 | 126.96
2019-06-24 00:30 | 123.93 | 120.64
2019-06-24 01:00 | 80.24 | 74.17
2019-06-24 01:30 | 62.05 | 53.57
2019-06-24 02:00 | 51.62 | 40.74
2019-06-24 02:30 | 47.05 | 35.34
2019-06-24 03:00 | 49.37 | 38.64
2019-06-24 03:30 | 54.85 | 45.78
2019-06-24 04:00 | 63.2 | 56.47
2019-06-24 04:30 | 75.51 | 69.85
2019-06-24 05:00 | 88.31 | 82.97
2019-06-24 05:30 | 119.47 | 115.05
2019-06-24 06:00 | 144.21 | 141.81
2019-06-24 06:30 | 157.09 | 155.95
2019-06-24 07:00 | 197.43 | 196.68
2019-06-24 07:30 | 198.34 | 198.34
2019-06-24 08:00 | 215.7 | 215.7
2019-06-24 08:30 | 182.47 | 182.46
2019-06-24 09:00 | 131.83 | 131.8
2019-06-24 09:30 | 96.02 | 96.01
2019-06-24 10:00 | 71.11 | 71.11
2019-06-24 10:30 | 56.49 | 56.49
2019-06-24 11:00 | 61.72 | 61.71
2019-06-24 11:30 | 49.32 | 49.32
2019-06-24 12:00 | 18.85 | 18.83
2019-06-24 12:30 | 16.1 | 16.1
2019-06-24 13:00 | 21.81 | 21.81
2019-06-24 13:30 | 42.92 | 42.92
2019-06-24 14:00 | 72.26 | 72.26
2019-06-24 14:30 | 75.54 | 75.53
2019-06-24 15:00 | 96.73 | 96.71
2019-06-24 15:30 | 133.56 | 133.55
2019-06-24 16:00 | 160.42 | 160.42
2019-06-24 16:30 | 167.88 | 167.88
2019-06-24 17:00 | 155.97 | 147.03
2019-06-24 17:30 | 172.93 | 165.74
2019-06-24 18:00 | 192.02 | 185.87
2019-06-24 18:30 | 189.23 | 184.71
2019-06-24 19:00 | 184.86 | 183.53
2019-06-24 19:30 | 179.39 | 178.53
2019-06-24 20:00 | 164.84 | 164.84
2019-06-24 20:30 | 176.94 | 176.76
2019-06-24 21:00 | 169.32 | 169.32
2019-06-24 21:30 | 176.27 | 176.07
2019-06-24 22:00 | 170.9 | 170.39
2019-06-24 22:30 | 155.74 | 154.78
2019-06-24 23:00 | 172.21 | 171.09
2019-06-24 23:30 | 150.77 | 149.12
2019-06-25 | 107.36 | 104.51
2019-06-25 00:30 | 86.67 | 83.6
2019-06-25 01:00 | 71.86 | 68.1
2019-06-25 01:30 | 51.69 | 46.57
2019-06-25 02:00 | 44.39 | 38.72
2019-06-25 02:30 | 46.73 | 40.71
2019-06-25 03:00 | 47.93 | 42.19
2019-06-25 03:30 | 49.64 | 43.64
2019-06-25 04:00 | 48.69 | 41.68
2019-06-25 04:30 | 82.14 | 78.26
2019-06-25 05:00 | 109.31 | 106.13
2019-06-25 05:30 | 139.59 | 137.43
2019-06-25 06:00 | 143.14 | 141.96
2019-06-25 06:30 | 169.16 | 168.57
2019-06-25 07:00 | 190.48 | 190
2019-06-25 07:30 | 126.69 | 126.56
2019-06-25 08:00 | 181.3 | 181.18
2019-06-25 08:30 | 167.33 | 167.29
2019-06-25 09:00 | 144.54 | 144.54
2019-06-25 09:30 | 91.67 | 91.67
2019-06-25 10:00 | 68.5 | 68.49
2019-06-25 10:30 | 44.48 | 44.43
2019-06-25 11:00 | 60.82 | 60.75
2019-06-25 11:30 | 61.08 | 61.06
2019-06-25 12:00 | 55.72 | 55.72
2019-06-25 12:30 | 58.2 | 58.2
2019-06-25 13:00 | 57.34 | 57.33
2019-06-25 13:30 | 63.22 | 63.22
2019-06-25 14:00 | 73.34 | 73.34
2019-06-25 14:30 | 70.44 | 70.44
2019-06-25 15:00 | 104.94 | 104.94
2019-06-25 15:30 | 128.37 | 128.36
2019-06-25 16:00 | 178.43 | 178.43
2019-06-25 16:30 | 179.67 | 179.65
2019-06-25 17:00 | 173.78 | 173.75
2019-06-25 17:30 | 181.87 | 181.67
2019-06-25 18:00 | 174.23 | 172.79
2019-06-25 18:30 | 156.97 | 155.64
2019-06-25 19:00 | 155.86 | 155.34
2019-06-25 19:30 | 146.5 | 146.42
2019-06-25 20:00 | 159.62 | 159.62
2019-06-25 20:30 | 170.7 | 170.19
2019-06-25 21:00 | 161.85 | 160.95
2019-06-25 21:30 | 153.04 | 151.74
2019-06-25 22:00 | 159.9 | 158.38
2019-06-25 22:30 | 136.95 | 136.03
2019-06-25 23:00 | 147.59 | 146.48
2019-06-25 23:30 | 113.59 | 111.59
2019-06-26 | 78.18 | 74.34
2019-06-26 00:30 | 77.57 | 73.35
2019-06-26 01:00 | 71.43 | 66.95
2019-06-26 01:30 | 59.67 | 54.3
2019-06-26 02:00 | 50.65 | 42.94
2019-06-26 02:30 | 49.61 | 40.29
2019-06-26 03:00 | 43.68 | 32.22
2019-06-26 03:30 | 47.03 | 36.84
2019-06-26 04:00 | 62.83 | 55.47
2019-06-26 04:30 | 84.8 | 80.26
2019-06-26 05:00 | 102.91 | 99.67
2019-06-26 05:30 | 130.89 | 127.51
2019-06-26 06:00 | 152.85 | 150.1
2019-06-26 06:30 | 165.24 | 163.53
2019-06-26 07:00 | 186.55 | 185.51
2019-06-26 07:30 | 195.09 | 195.05
2019-06-26 08:00 | 220.91 | 220.91
2019-06-26 08:30 | 225.98 | 225.95
2019-06-26 09:00 | 221.54 | 221.4
2019-06-26 09:30 | 218.84 | 218.68
2019-06-26 10:00 | 215.84 | 215.72
2019-06-26 10:30 | 192.27 | 192.15
2019-06-26 11:00 | 186.37 | 186.26
2019-06-26 11:30 | 197.51 | 197.42
2019-06-26 12:00 | 183.28 | 183.22
2019-06-26 12:30 | 162.79 | 162.76
2019-06-26 13:00 | 160.02 | 160
2019-06-26 13:30 | 170.46 | 170.44
2019-06-26 14:00 | 169.53 | 169.49
2019-06-26 14:30 | 176.97 | 176.86
2019-06-26 15:00 | 186.86 | 186.79
2019-06-26 15:30 | 186.04 | 185.98
2019-06-26 16:00 | 210.94 | 210.86
2019-06-26 16:30 | 216.02 | 215.97
2019-06-26 17:00 | 226.32 | 224.48
2019-06-26 17:30 | 228.61 | 220.45
2019-06-26 18:00 | 230.69 | 222.08
2019-06-26 18:30 | 227.51 | 219.45
2019-06-26 19:00 | 228.2 | 220.97
2019-06-26 19:30 | 215.47 | 211.23
2019-06-26 20:00 | 213.91 | 211.91
2019-06-26 20:30 | 205.11 | 205.1
2019-06-26 21:00 | 194.77 | 194.58
2019-06-26 21:30 | 184.25 | 183.92
2019-06-26 22:00 | 171.05 | 170.35
2019-06-26 22:30 | 175.8 | 174.88
2019-06-26 23:00 | 177.46 | 176.23
2019-06-26 23:30 | 156.59 | 154.79
2019-06-27 | 113.24 | 110.1
2019-06-27 00:30 | 78.47 | 73.68
2019-06-27 01:00 | 48.26 | 40.8
2019-06-27 01:30 | 42.37 | 33.52
2019-06-27 02:00 | 49.1 | 40.57
2019-06-27 02:30 | 60.48 | 52.91
2019-06-27 03:00 | 72.85 | 66.18
2019-06-27 03:30 | 77.3 | 71.04
2019-06-27 04:00 | 77.94 | 71.53
2019-06-27 04:30 | 93.65 | 88.43
2019-06-27 05:00 | 107.81 | 103.54
2019-06-27 05:30 | 133.5 | 130.36
2019-06-27 06:00 | 149.65 | 147.39
2019-06-27 06:30 | 165.88 | 164.43
2019-06-27 07:00 | 168.55 | 167.37
2019-06-27 07:30 | 168.54 | 168.31
2019-06-27 08:00 | 149.93 | 149.86
2019-06-27 08:30 | 148.53 | 148.49
2019-06-27 09:00 | 143.71 | 143.66
2019-06-27 09:30 | 122.43 | 122.37
2019-06-27 10:00 | 109.52 | 109.46
2019-06-27 10:30 | 104.82 | 104.8
2019-06-27 11:00 | 98.25 | 98.22
2019-06-27 11:30 | 108.64 | 108.6
2019-06-27 12:00 | 75.29 | 75.22
2019-06-27 12:30 | 54.8 | 54.57
2019-06-27 13:00 | 52.09 | 51.74
2019-06-27 13:30 | 65.34 | 65.11
2019-06-27 14:00 | 86.17 | 86.02
2019-06-27 14:30 | 117.78 | 117.63
2019-06-27 15:00 | 140.25 | 140.13
2019-06-27 15:30 | 142.52 | 142.4
2019-06-27 16:00 | 169.09 | 168.99
2019-06-27 16:30 | 168.69 | 168.6
2019-06-27 17:00 | 168.26 | 168.21
2019-06-27 17:30 | 160.78 | 160.58
2019-06-27 18:00 | 170.98 | 170.96
2019-06-27 18:30 | 173.29 | 173.28
2019-06-27 19:00 | 181.27 | 181.24
2019-06-27 19:30 | 174.81 | 174.66
2019-06-27 20:00 | 175.1 | 174.72
2019-06-27 20:30 | 174 | 173.43
2019-06-27 21:00 | 155.06 | 154.16
2019-06-27 21:30 | 148.86 | 148.36
2019-06-27 22:00 | 155.95 | 155.09
2019-06-27 22:30 | 176.43 | 175.31
2019-06-27 23:00 | 168.89 | 167.57
2019-06-27 23:30 | 165.5 | 163.93
2019-06-28 | 157.41 | 155.56
2019-06-28 00:30 | 143.01 | 141.09
2019-06-28 01:00 | 114.58 | 112.15
2019-06-28 01:30 | 104.76 | 101.99
2019-06-28 02:00 | 93.17 | 89.33
2019-06-28 02:30 | 97.54 | 93.3
2019-06-28 03:00 | 88 | 82.53
2019-06-28 03:30 | 92.36 | 87.57
2019-06-28 04:00 | 93.94 | 89.25
2019-06-28 04:30 | 104.55 | 100.46
2019-06-28 05:00 | 119.69 | 116.4
2019-06-28 05:30 | 137.07 | 134.63
2019-06-28 06:00 | 142.24 | 140.63
2019-06-28 06:30 | 161.34 | 160.63
2019-06-28 07:00 | 170.65 | 170.16
2019-06-28 07:30 | 198.5 | 198.38
2019-06-28 08:00 | 197.66 | 197.36
2019-06-28 08:30 | 170.44 | 170.03
2019-06-28 09:00 | 143.31 | 142.67
2019-06-28 09:30 | 130.07 | 129.07
2019-06-28 10:00 | 143.69 | 143.53
2019-06-28 10:30 | 147.65 | 147.65
2019-06-28 11:00 | 123.76 | 123.69
2019-06-28 11:30 | 100.84 | 100.68
2019-06-28 12:00 | 64.94 | 64.55
2019-06-28 12:30 | 45.61 | 45.23
2019-06-28 13:00 | 60.15 | 59.83
2019-06-28 13:30 | 62.1 | 61.78
2019-06-28 14:00 | 102.07 | 101.88
2019-06-28 14:30 | 131.62 | 131.46
2019-06-28 15:00 | 131.73 | 131.48
2019-06-28 15:30 | 144.43 | 144.17
2019-06-28 16:00 | 150.82 | 150.5
2019-06-28 16:30 | 154.54 | 154.34
2019-06-28 17:00 | 162.97 | 162.9
2019-06-28 17:30 | 178.37 | 177.43
2019-06-28 18:00 | 189.97 | 183.94
2019-06-28 18:30 | 188.51 | 181.85
2019-06-28 19:00 | 192.88 | 190.63
2019-06-28 19:30 | 185.58 | 183.55
2019-06-28 20:00 | 182.9 | 181.05
2019-06-28 20:30 | 180.68 | 179.22
2019-06-28 21:00 | 187.45 | 187.45
2019-06-28 21:30 | 194.54 | 194.11
2019-06-28 22:00 | 182.68 | 182.04
2019-06-28 22:30 | 168.54 | 167.78
2019-06-28 23:00 | 165.45 | 164.48
2019-06-28 23:30 | 170.05 | 168.72
2019-06-29 | 133.29 | 131.1
2019-06-29 00:30 | 123.48 | 121.16
2019-06-29 01:00 | 119.37 | 117.21
2019-06-29 01:30 | 112.62 | 110.01
2019-06-29 02:00 | 99.16 | 95.46
2019-06-29 02:30 | 103.03 | 100.07
2019-06-29 03:00 | 93.91 | 93.38
2019-06-29 03:30 | 99.06 | 98.71
2019-06-29 04:00 | 106.36 | 106.04
2019-06-29 04:30 | 110.78 | 110.58
2019-06-29 05:00 | 112.89 | 112.75
2019-06-29 05:30 | 116.95 | 116.74
2019-06-29 06:00 | 113.47 | 112.89
2019-06-29 06:30 | 132.71 | 132.4
2019-06-29 07:00 | 138.46 | 138.27
2019-06-29 07:30 | 151.36 | 151.31
2019-06-29 08:00 | 157.98 | 157.88
2019-06-29 08:30 | 127.66 | 127.62
2019-06-29 09:00 | 112.95 | 111.78
2019-06-29 09:30 | 112.72 | 110.53
2019-06-29 10:00 | 93.72 | 91.04
2019-06-29 10:30 | 69.25 | 65.43
2019-06-29 11:00 | 65.2 | 61.07
2019-06-29 11:30 | 54.53 | 48.76
2019-06-29 12:00 | 53.59 | 47.1
2019-06-29 12:30 | 37.57 | 27.98
2019-06-29 13:00 | 53.2 | 47.26
2019-06-29 13:30 | 51.15 | 43.86
2019-06-29 14:00 | 71.59 | 66.68
2019-06-29 14:30 | 84.65 | 80.47
2019-06-29 15:00 | 97.43 | 93.76
2019-06-29 15:30 | 110.39 | 107.22
2019-06-29 16:00 | 122.16 | 119.29
2019-06-29 16:30 | 139.01 | 136.74
2019-06-29 17:00 | 170.36 | 168.93
2019-06-29 17:30 | 205.05 | 204.57
2019-06-29 18:00 | 210 | 209.82
2019-06-29 18:30 | 207.14 | 206.89
2019-06-29 19:00 | 205.26 | 205
2019-06-29 19:30 | 200.95 | 200.43
2019-06-29 20:00 | 197.41 | 196.67
2019-06-29 20:30 | 196.5 | 195.59
2019-06-29 21:00 | 185.04 | 183.87
2019-06-29 21:30 | 169.44 | 168.25
2019-06-29 22:00 | 162.21 | 160.78
2019-06-29 22:30 | 155.51 | 154.34
2019-06-29 23:00 | 155.99 | 154.36
2019-06-29 23:30 | 160.08 | 158.23
2019-06-30 | 145.01 | 142.38
2019-06-30 00:30 | 133.61 | 133.09
2019-06-30 01:00 | 121.22 | 121.06
2019-06-30 01:30 | 110.61 | 110.3
2019-06-30 02:00 | 94.93 | 93.75
2019-06-30 02:30 | 88.49 | 82.02
2019-06-30 03:00 | 83.43 | 82.02
2019-06-30 03:30 | 78.94 | 77.98
2019-06-30 04:00 | 101.46 | 96.55
2019-06-30 04:30 | 103.01 | 97.63
2019-06-30 05:00 | 113.81 | 109.27
2019-06-30 05:30 | 108.59 | 103.38
2019-06-30 06:00 | 110.71 | 105.71
2019-06-30 06:30 | 125.68 | 121.66
2019-06-30 07:00 | 133.29 | 129.8
2019-06-30 07:30 | 139.59 | 137.01
2019-06-30 08:00 | 134.91 | 131.93
2019-06-30 08:30 | 108.89 | 105.34
2019-06-30 09:00 | 76.8 | 71.27
2019-06-30 09:30 | 53.66 | 46.15
2019-06-30 10:00 | 33.44 | 21.76
2019-06-30 10:30 | 22.34 | 17.87
2019-06-30 11:00 | 39.47 | 35.67
2019-06-30 11:30 | 27.31 | 22.29
2019-06-30 12:00 | 22.23 | 15.59
2019-06-30 12:30 | 16.63 | 7.39
2019-06-30 13:00 | 20.55 | 12.56
2019-06-30 13:30 | 26.29 | 20.38
2019-06-30 14:00 | 38.46 | 33.95
2019-06-30 14:30 | 54.03 | 50.9
2019-06-30 15:00 | 38.53 | 34.98
2019-06-30 15:30 | 63.44 | 61.18
2019-06-30 16:00 | 102.33 | 100.73
2019-06-30 16:30 | 114.54 | 114.1
2019-06-30 17:00 | 107.34 | 106.96
2019-06-30 17:30 | 138.67 | 136.89
2019-06-30 18:00 | 174.55 | 171.5
2019-06-30 18:30 | 174.4 | 171.53
2019-06-30 19:00 | 171.04 | 168.93
2019-06-30 19:30 | 137.92 | 137.75
2019-06-30 20:00 | 126.78 | 126.68
2019-06-30 20:30 | 118.58 | 118.55
2019-06-30 21:00 | 122.82 | 122.57
2019-06-30 21:30 | 152.76 | 152.57
2019-06-30 22:00 | 158.1 | 157.89
2019-06-30 22:30 | 162.71 | 162.67
2019-06-30 23:00 | 163.47 | 163.31
2019-06-30 23:30 | 131.51 | 131.19
2019-07-01 | 89.17 | 88.53
2019-07-01 00:30 | 95.91 | 95.39
2019-07-01 01:00 | 85.51 | 84.96
2019-07-01 01:30 | 69.3 | 69.3
2019-07-01 02:00 | 56.9 | 56.41
2019-07-01 02:30 | 61.29 | 61.01
2019-07-01 03:00 | 50.85 | 50.44
2019-07-01 03:30 | 53.55 | 53.12
2019-07-01 04:00 | 82.39 | 82.06
2019-07-01 04:30 | 110.12 | 109.76
2019-07-01 05:00 | 118.55 | 118.21
2019-07-01 05:30 | 128.43 | 128.21
2019-07-01 06:00 | 117.46 | 117.34
2019-07-01 06:30 | 152.76 | 152.31
2019-07-01 07:00 | 149.66 | 149.02
2019-07-01 07:30 | 156.17 | 156.11
2019-07-01 08:00 | 132.04 | 131.19
2019-07-01 08:30 | 91.21 | 89.62
2019-07-01 09:00 | 95.53 | 93.86
2019-07-01 09:30 | 100.3 | 98.34
2019-07-01 10:00 | 110.76 | 107.77
2019-07-01 10:30 | 133.53 | 126.51
2019-07-01 11:00 | 141.07 | 134.23
2019-07-01 11:30 | 155.45 | 149.38
2019-07-01 12:00 | 151.91 | 146.11
2019-07-01 12:30 | 137.63 | 131.92
2019-07-01 13:00 | 140.65 | 135.45
2019-07-01 13:30 | 144.55 | 139.47
2019-07-01 14:00 | 138.64 | 133.37
2019-07-01 14:30 | 134.25 | 128.67
2019-07-01 15:00 | 147.95 | 142.91
2019-07-01 15:30 | 140.59 | 135.58
2019-07-01 16:00 | 164.89 | 160.83
2019-07-01 16:30 | 163.12 | 159.07
2019-07-01 17:00 | 179.36 | 171.77
2019-07-01 17:30 | 192.34 | 183.37
2019-07-01 18:00 | 207.13 | 199.12
2019-07-01 18:30 | 196.62 | 190.39
2019-07-01 19:00 | 189.11 | 186.23
2019-07-01 19:30 | 171 | 168.4
2019-07-01 20:00 | 166.84 | 164.45
2019-07-01 20:30 | 172.28 | 171.16
2019-07-01 21:00 | 157.11 | 156.96
2019-07-01 21:30 | 161.28 | 160.99
2019-07-01 22:00 | 154.11 | 153.56
2019-07-01 22:30 | 164.63 | 163.98
2019-07-01 23:00 | 170.84 | 170.17
2019-07-01 23:30 | 154.74 | 153.82
2019-07-02 | 133.32 | 131.63
2019-07-02 00:30 | 122.76 | 120.61
2019-07-02 01:00 | 104.6 | 102.92
2019-07-02 01:30 | 90.75 | 89.23
2019-07-02 02:00 | 81.81 | 79.97
2019-07-02 02:30 | 80.89 | 79.04
2019-07-02 03:00 | 78.88 | 76.93
2019-07-02 03:30 | 84.8 | 83.31
2019-07-02 04:00 | 77.12 | 75.44
2019-07-02 04:30 | 91.53 | 90.01
2019-07-02 05:00 | 111.87 | 110.64
2019-07-02 05:30 | 127.62 | 126.41
2019-07-02 06:00 | 140.65 | 139.86
2019-07-02 06:30 | 139.41 | 138.72
2019-07-02 07:00 | 122.85 | 122.73
2019-07-02 07:30 | 133.43 | 133.38
2019-07-02 08:00 | 111.86 | 111.86
2019-07-02 08:30 | 85.01 | 84.96
2019-07-02 09:00 | 77.61 | 77.5
2019-07-02 09:30 | 82.42 | 82.19
2019-07-02 10:00 | 69.52 | 69.5
2019-07-02 10:30 | 65.42 | 65.4
2019-07-02 11:00 | 62.9 | 62.88
2019-07-02 11:30 | 75.26 | 75.24
2019-07-02 12:00 | 74.67 | 74.6
2019-07-02 12:30 | 72.91 | 72.81
2019-07-02 13:00 | 82.24 | 82.15
2019-07-02 13:30 | 81.72 | 81.67
2019-07-02 14:00 | 95.85 | 95.81
2019-07-02 14:30 | 100.47 | 100.42
2019-07-02 15:00 | 93.08 | 93.04
2019-07-02 15:30 | 100.19 | 100.16
2019-07-02 16:00 | 125.4 | 125.38
2019-07-02 16:30 | 156.36 | 156.35
2019-07-02 17:00 | 145.56 | 145.55
2019-07-02 17:30 | 129.9 | 129.81
2019-07-02 18:00 | 116.16 | 115.92
2019-07-02 18:30 | 104.88 | 104.81
2019-07-02 19:00 | 35.91 | 33.5
2019-07-02 19:30 | 88.87 | 88.72
2019-07-02 20:00 | 79.3 | 79.25
2019-07-02 20:30 | 111.07 | 111.02
2019-07-02 21:00 | 95.68 | 95.54
2019-07-02 21:30 | 85.14 | 84.77
2019-07-02 22:00 | 81.67 | 80.98
2019-07-02 22:30 | 79.01 | 78.03
2019-07-02 23:00 | 97.62 | 96.67
2019-07-02 23:30 | 81.78 | 80.72
2019-07-03 | 78.43 | 77.21
2019-07-03 00:30 | 81.8 | 80.6
2019-07-03 01:00 | 71.28 | 71.17
2019-07-03 01:30 | 66.42 | 66.25
2019-07-03 02:00 | 46.96 | 46.58
2019-07-03 02:30 | 37.97 | 37.58
2019-07-03 03:00 | 39.04 | 38.65
2019-07-03 03:30 | 41.59 | 41.36
2019-07-03 04:00 | 46.52 | 46.33
2019-07-03 04:30 | 71 | 70.82
2019-07-03 05:00 | 93.79 | 93.5
2019-07-03 05:30 | 103.7 | 102.92
2019-07-03 06:00 | 124.35 | 123.64
2019-07-03 06:30 | 118.49 | 117.97
2019-07-03 07:00 | 117.21 | 116.92
2019-07-03 07:30 | 124.02 | 123.91
2019-07-03 08:00 | 60.06 | 60.04
2019-07-03 08:30 | 37.97 | 29.91
2019-07-03 09:00 | 73.52 | 72.08
2019-07-03 09:30 | 75.08 | 74.7
2019-07-03 10:00 | 64.25 | 64.11
2019-07-03 10:30 | 47.21 | 47.14
2019-07-03 11:00 | 57.02 | 56.97
2019-07-03 11:30 | 69.28 | 69.26
2019-07-03 12:00 | 65.93 | 65.9
2019-07-03 12:30 | 68.09 | 68
2019-07-03 13:00 | 72.44 | 72.26
2019-07-03 13:30 | 80.41 | 80.25
2019-07-03 14:00 | 91.56 | 91.43
2019-07-03 14:30 | 98.22 | 98.1
2019-07-03 15:00 | 116.72 | 116.66
2019-07-03 15:30 | 128.79 | 128.77
2019-07-03 16:00 | 135.43 | 135.42
2019-07-03 16:30 | 123.22 | 123.22
2019-07-03 17:00 | 124.2 | 124.2
2019-07-03 17:30 | 133.93 | 132.64
2019-07-03 18:00 | 164.24 | 159.36
2019-07-03 18:30 | 166.09 | 161.68
2019-07-03 19:00 | 162.4 | 158.35
2019-07-03 19:30 | 148.32 | 144.58
2019-07-03 20:00 | 147.85 | 147.57
2019-07-03 20:30 | 148.13 | 148.07
2019-07-03 21:00 | 131.91 | 131.78
2019-07-03 21:30 | 141.65 | 141.55
2019-07-03 22:00 | 136.81 | 136.63
2019-07-03 22:30 | 139.59 | 139.36
2019-07-03 23:00 | 148.13 | 147.85
2019-07-03 23:30 | 125.33 | 125.22
2019-07-04 | 106.29 | 106.14
2019-07-04 00:30 | 90.88 | 90.68
2019-07-04 01:00 | 83.37 | 83.22
2019-07-04 01:30 | 71.4 | 71.28
2019-07-04 02:00 | 71.63 | 71.48
2019-07-04 02:30 | 72.04 | 71.86
2019-07-04 03:00 | 72.29 | 72.08
2019-07-04 03:30 | 78.68 | 78.51
2019-07-04 04:00 | 82.76 | 82.32
2019-07-04 04:30 | 88.15 | 87.42
2019-07-04 05:00 | 111.66 | 111.14
2019-07-04 05:30 | 127.81 | 127.4
2019-07-04 06:00 | 132.72 | 132.16
2019-07-04 06:30 | 118.12 | 117.05
2019-07-04 07:00 | 114.5 | 114.17
2019-07-04 07:30 | 138.53 | 138.49
2019-07-04 08:00 | 124.21 | 124.16
2019-07-04 08:30 | 120.46 | 120.43
2019-07-04 09:00 | 121.08 | 121.02
2019-07-04 09:30 | 94.68 | 94.61
2019-07-04 10:00 | 87.32 | 87.2
2019-07-04 10:30 | 82.38 | 82.2
2019-07-04 11:00 | 86.43 | 86.18
2019-07-04 11:30 | 87.27 | 86.97
2019-07-04 12:00 | 88.71 | 88.38
2019-07-04 12:30 | 87.44 | 87.15
2019-07-04 13:00 | 90.54 | 90.32
2019-07-04 13:30 | 97.4 | 97.26
2019-07-04 14:00 | 111.94 | 111.81
2019-07-04 14:30 | 131.29 | 131.22
2019-07-04 15:00 | 140.26 | 140.24
2019-07-04 15:30 | 150.38 | 150.37
2019-07-04 16:00 | 150.17 | 150.17
2019-07-04 16:30 | 144.06 | 144.06
2019-07-04 17:00 | 132.48 | 132.48
2019-07-04 17:30 | 126.77 | 126.67
2019-07-04 18:00 | 131.76 | 131.09
2019-07-04 18:30 | 143.98 | 143.92
2019-07-04 19:00 | 141.92 | 141.9
2019-07-04 19:30 | 140.25 | 140.25
2019-07-04 20:00 | 149.72 | 149.68
2019-07-04 20:30 | 142.09 | 141.97
2019-07-04 21:00 | 130.48 | 130.13
2019-07-04 21:30 | 117.51 | 117.04
2019-07-04 22:00 | 117.2 | 116.71
2019-07-04 22:30 | 115.13 | 114.46
2019-07-04 23:00 | 137.05 | 136.32
2019-07-04 23:30 | 107.79 | 106.92
2019-07-05 | 71.75 | 70.28
2019-07-05 00:30 | 57.62 | 57.08
2019-07-05 01:00 | 43.46 | 42.83
2019-07-05 01:30 | 39.3 | 38.73
2019-07-05 02:00 | 39.48 | 38.71
2019-07-05 02:30 | 41.23 | 40.4
2019-07-05 03:00 | 44.4 | 43.51
2019-07-05 03:30 | 61.87 | 61.09
2019-07-05 04:00 | 81.75 | 80.94
2019-07-05 04:30 | 86.91 | 86.15
2019-07-05 05:00 | 80.55 | 79.6
2019-07-05 05:30 | 91.1 | 90.01
2019-07-05 06:00 | 103.89 | 102.77
2019-07-05 06:30 | 99.75 | 98.61
2019-07-05 07:00 | 83.68 | 82.89
2019-07-05 07:30 | 96.29 | 95.79
2019-07-05 08:00 | 98.63 | 98.4
2019-07-05 08:30 | 112.28 | 112.27
2019-07-05 09:00 | 132.2 | 132.18
2019-07-05 09:30 | 124.31 | 124.29
2019-07-05 10:00 | 107.21 | 107.2
2019-07-05 10:30 | 103 | 102.96
2019-07-05 11:00 | 102.17 | 102.13
2019-07-05 11:30 | 111.79 | 111.75
2019-07-05 12:00 | 99.43 | 99.4
2019-07-05 12:30 | 101.69 | 101.68
2019-07-05 13:00 | 117.97 | 117.96
2019-07-05 13:30 | 113.3 | 113.3
2019-07-05 14:00 | 104.08 | 104.08
2019-07-05 14:30 | 117.82 | 117.82
2019-07-05 15:00 | 135.48 | 135.48
2019-07-05 15:30 | 155.71 | 155.71
2019-07-05 16:00 | 164.83 | 164.82
2019-07-05 16:30 | 161.08 | 161.07
2019-07-05 17:00 | 154.12 | 154.12
2019-07-05 17:30 | 150.73 | 150.67
2019-07-05 18:00 | 156.98 | 156.85
2019-07-05 18:30 | 153.82 | 153.6
2019-07-05 19:00 | 156.81 | 156.63
2019-07-05 19:30 | 159.25 | 159.23
2019-07-05 20:00 | 163.63 | 163.63
2019-07-05 20:30 | 152.27 | 152.24
2019-07-05 21:00 | 129.02 | 128.93
2019-07-05 21:30 | 133.16 | 133
2019-07-05 22:00 | 143.14 | 142.86
2019-07-05 22:30 | 151.22 | 150.8
2019-07-05 23:00 | 163.11 | 162.48
2019-07-05 23:30 | 141.52 | 140.65
2019-07-06 | 117.67 | 116.89
2019-07-06 00:30 | 104.39 | 104.02
2019-07-06 01:00 | 90.66 | 90.3
2019-07-06 01:30 | 79.48 | 79.15
2019-07-06 02:00 | 68.24 | 67.73
2019-07-06 02:30 | 65.53 | 64.94
2019-07-06 03:00 | 61.88 | 61.23
2019-07-06 03:30 | 46.2 | 44.8
2019-07-06 04:00 | 61.97 | 59.93
2019-07-06 04:30 | 72.04 | 70.58
2019-07-06 05:00 | 84.17 | 82.93
2019-07-06 05:30 | 99.96 | 98.85
2019-07-06 06:00 | 109.84 | 108.9
2019-07-06 06:30 | 112.27 | 111.24
2019-07-06 07:00 | 102.28 | 101
2019-07-06 07:30 | 117.49 | 116.44
2019-07-06 08:00 | 106 | 104.55
2019-07-06 08:30 | 112.55 | 111.9
2019-07-06 09:00 | 117.22 | 116.6
2019-07-06 09:30 | 134.1 | 133.61
2019-07-06 10:00 | 124.27 | 123.79
2019-07-06 10:30 | 116.87 | 116.29
2019-07-06 11:00 | 100.62 | 99.36
2019-07-06 11:30 | 108.85 | 108.02
2019-07-06 12:00 | 108.72 | 107.78
2019-07-06 12:30 | 103.3 | 102.19
2019-07-06 13:00 | 112.33 | 111.31
2019-07-06 13:30 | 121.19 | 120.17
2019-07-06 14:00 | 119.39 | 118.4
2019-07-06 14:30 | 123.77 | 122.82
2019-07-06 15:00 | 117.26 | 116.21
2019-07-06 15:30 | 139.27 | 138.34
2019-07-06 16:00 | 135.56 | 134.41
2019-07-06 16:30 | 136.14 | 135.15
2019-07-06 17:00 | 147.43 | 147.1
2019-07-06 17:30 | 165.25 | 165.25
2019-07-06 18:00 | 179.13 | 179.12
2019-07-06 18:30 | 179.22 | 179.21
2019-07-06 19:00 | 175.18 | 175.18
2019-07-06 19:30 | 161 | 161
2019-07-06 20:00 | 155.14 | 155.12
2019-07-06 20:30 | 148.8 | 148.78
2019-07-06 21:00 | 132.68 | 132.61
2019-07-06 21:30 | 129.84 | 129.63
2019-07-06 22:00 | 120.99 | 120.6
2019-07-06 22:30 | 138.69 | 138.25
2019-07-06 23:00 | 155.86 | 155.33
2019-07-06 23:30 | 131.1 | 130.42
2019-07-07 | 107.45 | 106.38
2019-07-07 00:30 | 100.34 | 99.87
2019-07-07 01:00 | 87.37 | 87.03
2019-07-07 01:30 | 70.39 | 69.81
2019-07-07 02:00 | 59.63 | 58.89
2019-07-07 02:30 | 68.97 | 68.24
2019-07-07 03:00 | 80.13 | 78.67
2019-07-07 03:30 | 73.68 | 72
2019-07-07 04:00 | 70.91 | 69.2
2019-07-07 04:30 | 83.13 | 81.76
2019-07-07 05:00 | 90.28 | 89.05
2019-07-07 05:30 | 99.68 | 98.59
2019-07-07 06:00 | 107.15 | 106.31
2019-07-07 06:30 | 87.54 | 86.48
2019-07-07 07:00 | 91.79 | 90.78
2019-07-07 07:30 | 99.94 | 99.13
2019-07-07 08:00 | 99.31 | 98.71
2019-07-07 08:30 | 85.2 | 84.96
2019-07-07 09:00 | 72.96 | 72.93
2019-07-07 09:30 | 79.85 | 79.79
2019-07-07 10:00 | 74.62 | 74.57
2019-07-07 10:30 | 49.47 | 49.43
2019-07-07 11:00 | 66.76 | 66.76
2019-07-07 11:30 | 65.11 | 65.09
2019-07-07 12:00 | 74.78 | 74.69
2019-07-07 12:30 | 71.75 | 71.72
2019-07-07 13:00 | 71.21 | 71.13
2019-07-07 13:30 | 71.12 | 71
2019-07-07 14:00 | 82.58 | 82.47
2019-07-07 14:30 | 96.58 | 96.54
2019-07-07 15:00 | 84.34 | 84.27
2019-07-07 15:30 | 84.81 | 84.72
2019-07-07 16:00 | 105.18 | 104.99
2019-07-07 16:30 | 115.29 | 115.25
2019-07-07 17:00 | 141.3 | 139.91
2019-07-07 17:30 | 145.42 | 143.6
2019-07-07 18:00 | 158.05 | 155.63
2019-07-07 18:30 | 161.41 | 158.71
2019-07-07 19:00 | 162.22 | 159.66
2019-07-07 19:30 | 159.26 | 156.74
2019-07-07 20:00 | 164.41 | 162.11
2019-07-07 20:30 | 148.65 | 147.15
2019-07-07 21:00 | 134.39 | 134.39
2019-07-07 21:30 | 130.83 | 130.82
2019-07-07 22:00 | 118.78 | 118.76
2019-07-07 22:30 | 130.72 | 130.68
2019-07-07 23:00 | 145.39 | 145.24
2019-07-07 23:30 | 135.5 | 135.29
2019-07-08 | 107.08 | 106.82
2019-07-08 00:30 | 98.98 | 98.78
2019-07-08 01:00 | 73.71 | 73.47
2019-07-08 01:30 | 76.78 | 76.63
2019-07-08 02:00 | 70.54 | 69.29
2019-07-08 02:30 | 63.19 | 61.81
2019-07-08 03:00 | 67.65 | 66.53
2019-07-08 03:30 | 67.51 | 66.3
2019-07-08 04:00 | 71.8 | 70.27
2019-07-08 04:30 | 79.48 | 78.14
2019-07-08 05:00 | 98.9 | 98.2
2019-07-08 05:30 | 110.26 | 109.91
2019-07-08 06:00 | 135.61 | 135.41
2019-07-08 06:30 | 143.97 | 143.75
2019-07-08 07:00 | 146.73 | 146.67
2019-07-08 07:30 | 162.82 | 162.76
2019-07-08 08:00 | 168.72 | 168.54
2019-07-08 08:30 | 168.74 | 167.66
2019-07-08 09:00 | 149.98 | 143.99
2019-07-08 09:30 | 141.1 | 139.08
2019-07-08 10:00 | 140.5 | 139.37
2019-07-08 10:30 | 135.14 | 133.98
2019-07-08 11:00 | 131.51 | 130.3
2019-07-08 11:30 | 118.95 | 117.6
2019-07-08 12:00 | 122.59 | 121.46
2019-07-08 12:30 | 127.43 | 126.32
2019-07-08 13:00 | 128.24 | 127.19
2019-07-08 13:30 | 129.9 | 128.82
2019-07-08 14:00 | 127.05 | 126
2019-07-08 14:30 | 126.81 | 125.72
2019-07-08 15:00 | 132.22 | 131.26
2019-07-08 15:30 | 133.97 | 133.13
2019-07-08 16:00 | 132.16 | 131.86
2019-07-08 16:30 | 118.36 | 118.24
2019-07-08 17:00 | 113.76 | 113.31
2019-07-08 17:30 | 140.05 | 136.41
2019-07-08 18:00 | 141.53 | 137.38
2019-07-08 18:30 | 135.07 | 131.12
2019-07-08 19:00 | 133.94 | 130.33
2019-07-08 19:30 | 123.78 | 121.97
2019-07-08 20:00 | 119.36 | 119.3
2019-07-08 20:30 | 106.98 | 106.81
2019-07-08 21:00 | 93.06 | 91.27
2019-07-08 21:30 | 85.56 | 84.02
2019-07-08 22:00 | 82.2 | 80.83
2019-07-08 22:30 | 85.44 | 84.57
2019-07-08 23:00 | 97.53 | 96.99
2019-07-08 23:30 | 78.72 | 78.22
2019-07-09 | 54.57 | 54
2019-07-09 00:30 | 50.82 | 50.41
2019-07-09 01:00 | 47.78 | 47.49
2019-07-09 01:30 | 42.31 | 40.95
2019-07-09 02:00 | 29.42 | 26.99
2019-07-09 02:30 | 31.25 | 28.92
2019-07-09 03:00 | 35.7 | 33.52
2019-07-09 03:30 | 36.06 | 33.92
2019-07-09 04:00 | 40.75 | 38.9
2019-07-09 04:30 | 56.56 | 55.24
2019-07-09 05:00 | 60.67 | 59.55
2019-07-09 05:30 | 69.19 | 68.48
2019-07-09 06:00 | 83.01 | 82.67
2019-07-09 06:30 | 99.32 | 99.27
2019-07-09 07:00 | 89.32 | 89
2019-07-09 07:30 | 94.1 | 90.75
2019-07-09 08:00 | 104.1 | 75.96
2019-07-09 08:30 | 99.32 | 60.76
2019-07-09 09:00 | 99.71 | 61.31
2019-07-09 09:30 | 97.66 | 58.44
2019-07-09 10:00 | 63.4 | 44.96
2019-07-09 10:30 | 51.43 | 31.25
2019-07-09 11:00 | 51.51 | 31.08
2019-07-09 11:30 | 53.58 | 34.02
2019-07-09 12:00 | 52.24 | 32.39
2019-07-09 12:30 | 53.9 | 35.35
2019-07-09 13:00 | 59.91 | 44.06
2019-07-09 13:30 | 63.31 | 47.92
2019-07-09 14:00 | 70.36 | 57.22
2019-07-09 14:30 | 70.63 | 57.93
2019-07-09 15:00 | 66.97 | 53.68
2019-07-09 15:30 | 75.99 | 64.8
2019-07-09 16:00 | 81.31 | 71.61
2019-07-09 16:30 | 80.31 | 70.48
2019-07-09 17:00 | 106.15 | 76.52
2019-07-09 17:30 | 115.22 | 92.33
2019-07-09 18:00 | 111.35 | 103.45
2019-07-09 18:30 | 105.29 | 99.5
2019-07-09 19:00 | 103.33 | 98.03
2019-07-09 19:30 | 97.25 | 92.06
2019-07-09 20:00 | 75.84 | 74.67
2019-07-09 20:30 | 83.92 | 83.19
2019-07-09 21:00 | 81.15 | 80.04
2019-07-09 21:30 | 89 | 86.56
2019-07-09 22:00 | 68.88 | 66.24
2019-07-09 22:30 | 50.9 | 47.64
2019-07-09 23:00 | 52.24 | 52.19
2019-07-09 23:30 | 36.08 | 36.05
2019-07-10 | 23.29 | 23.28
2019-07-10 00:30 | 21.85 | 21.83
2019-07-10 01:00 | 17.42 | 15.6
2019-07-10 01:30 | 19.52 | 16.68
2019-07-10 02:00 | 17.48 | 14.21
2019-07-10 02:30 | 16.92 | 13.66
2019-07-10 03:00 | 23.64 | 21.32
2019-07-10 03:30 | 37.36 | 35.38
2019-07-10 04:00 | 46.49 | 44.82
2019-07-10 04:30 | 53.12 | 51.84
2019-07-10 05:00 | 52.4 | 51.15
2019-07-10 05:30 | 61.68 | 60.88
2019-07-10 06:00 | 58.26 | 57.96
2019-07-10 06:30 | 58.81 | 57.32
2019-07-10 07:00 | 115.49 | 114.38
2019-07-10 07:30 | 142.71 | 138.61
2019-07-10 08:00 | 161.16 | 145.23
2019-07-10 08:30 | 166.99 | 147.59
2019-07-10 09:00 | 164.98 | 145.04
2019-07-10 09:30 | 153.59 | 138.29
2019-07-10 10:00 | 142.36 | 129.16
2019-07-10 10:30 | 128.51 | 114.93
2019-07-10 11:00 | 118.02 | 113.74
2019-07-10 11:30 | 111.61 | 108.46
2019-07-10 12:00 | 112.45 | 109.36
2019-07-10 12:30 | 115.4 | 112.32
2019-07-10 13:00 | 118.73 | 115.78
2019-07-10 13:30 | 122.38 | 119.52
2019-07-10 14:00 | 127.08 | 124.3
2019-07-10 14:30 | 130.47 | 127.84
2019-07-10 15:00 | 131.15 | 128.59
2019-07-10 15:30 | 129.85 | 127.82
2019-07-10 16:00 | 128.41 | 126.95
2019-07-10 16:30 | 113.63 | 111
2019-07-10 17:00 | 104.37 | 85.74
2019-07-10 17:30 | 126.38 | 102.79
2019-07-10 18:00 | 147.37 | 126.72
2019-07-10 18:30 | 140.36 | 119.21
2019-07-10 19:00 | 135.95 | 114.27
2019-07-10 19:30 | 117.98 | 93.19
2019-07-10 20:00 | 82.88 | 40.8
2019-07-10 20:30 | 104.24 | 77.67
2019-07-10 21:00 | 81.76 | 45.63
2019-07-10 21:30 | 91.44 | 63.64
2019-07-10 22:00 | 81.87 | 60.39
2019-07-10 22:30 | 61.1 | 42.53
2019-07-10 23:00 | 72.34 | 62.61
2019-07-10 23:30 | 50.59 | 50.42
2019-07-11 | 45.51 | 45.46
2019-07-11 00:30 | 60.32 | 58.99
2019-07-11 01:00 | 55.05 | 52.7
2019-07-11 01:30 | 49.52 | 46.69
2019-07-11 02:00 | 57.34 | 54.81
2019-07-11 02:30 | 65.52 | 63.15
2019-07-11 03:00 | 74.68 | 72.23
2019-07-11 03:30 | 84.4 | 81.7
2019-07-11 04:00 | 96.23 | 93.94
2019-07-11 04:30 | 94.01 | 91.57
2019-07-11 05:00 | 104.17 | 101.9
2019-07-11 05:30 | 101.07 | 98.52
2019-07-11 06:00 | 119.01 | 118.28
2019-07-11 06:30 | 114.56 | 114.26
2019-07-11 07:00 | 99.87 | 99.04
2019-07-11 07:30 | 122.34 | 122.11
2019-07-11 08:00 | 97.7 | 97.69
2019-07-11 08:30 | 58.77 | 58.66
2019-07-11 09:00 | 80.22 | 80.14
2019-07-11 09:30 | 65.86 | 65.8
2019-07-11 10:00 | 63.96 | 63.6
2019-07-11 10:30 | 53.31 | 50.06
2019-07-11 11:00 | 49.78 | 46
2019-07-11 11:30 | 44.08 | 39.65
2019-07-11 12:00 | 39.36 | 34.43
2019-07-11 12:30 | 41.01 | 36.59
2019-07-11 13:00 | 42.2 | 37.94
2019-07-11 13:30 | 46.41 | 42.64
2019-07-11 14:00 | 59.23 | 56.31
2019-07-11 14:30 | 65.12 | 62.32
2019-07-11 15:00 | 82.57 | 80.51
2019-07-11 15:30 | 105.37 | 104.32
2019-07-11 16:00 | 95.83 | 94.66
2019-07-11 16:30 | 79.58 | 78.29
2019-07-11 17:00 | 83.93 | 82.46
2019-07-11 17:30 | 53.95 | 14.58
2019-07-11 18:00 | 38.06 | 19.26
2019-07-11 18:30 | 68.48 | 64.56
2019-07-11 19:00 | 98.05 | 97.39
2019-07-11 19:30 | 82.09 | 81.56
2019-07-11 20:00 | 64.32 | 63.81
2019-07-11 20:30 | 81.07 | 81.07
2019-07-11 21:00 | 15.64 | 15.58
2019-07-11 21:30 | 57.07 | 56.51
2019-07-11 22:00 | 73.71 | 72.38
2019-07-11 22:30 | 79.27 | 77.07
2019-07-11 23:00 | 88.38 | 87.08
2019-07-11 23:30 | 83.2 | 81.56
2019-07-12 | 69.1 | 66.7
2019-07-12 00:30 | 68.36 | 65.7
2019-07-12 01:00 | 71.59 | 69.06
2019-07-12 01:30 | 70.65 | 67.89
2019-07-12 02:00 | 65.58 | 62.21
2019-07-12 02:30 | 69.61 | 63.79
2019-07-12 03:00 | 68.54 | 59.9
2019-07-12 03:30 | 77.45 | 70.08
2019-07-12 04:00 | 63.43 | 54.18
2019-07-12 04:30 | 79.62 | 72.63
2019-07-12 05:00 | 104.55 | 99.52
2019-07-12 05:30 | 105.81 | 100.98
2019-07-12 06:00 | 124.58 | 120.9
2019-07-12 06:30 | 126.43 | 125.5
2019-07-12 07:00 | 122.82 | 122.77
2019-07-12 07:30 | 133.18 | 132.58
2019-07-12 08:00 | 124.41 | 123.57
2019-07-12 08:30 | 125.49 | 124.54
2019-07-12 09:00 | 110.56 | 109.49
2019-07-12 09:30 | 105.88 | 104.9
2019-07-12 10:00 | 104.55 | 103.58
2019-07-12 10:30 | 81.31 | 80.09
2019-07-12 11:00 | 19.45 | 12.72
2019-07-12 11:30 | 16.85 | -2.12
2019-07-12 12:00 | 19.15 | 10.44
2019-07-12 12:30 | 18.45 | 6.73
2019-07-12 13:00 | 21.4 | 13.26
2019-07-12 13:30 | 24.05 | 17.86
2019-07-12 14:00 | 28.97 | 23.76
2019-07-12 14:30 | 34.04 | 29.63
2019-07-12 15:00 | 36.65 | 32.85
2019-07-12 15:30 | 53.83 | 51.81
2019-07-12 16:00 | 84.03 | 82.85
2019-07-12 16:30 | 85.47 | 84.41
2019-07-12 17:00 | 88.81 | 87.68
2019-07-12 17:30 | 117.27 | 105.74
2019-07-12 18:00 | 136.59 | 117.29
2019-07-12 18:30 | 143.51 | 125.8
2019-07-12 19:00 | 134.46 | 115.8
2019-07-12 19:30 | 122.36 | 102.72
2019-07-12 20:00 | 116.36 | 96.51
2019-07-12 20:30 | 114.06 | 101.65
2019-07-12 21:00 | 114.32 | 113.95
2019-07-12 21:30 | 102.9 | 102.68
2019-07-12 22:00 | 89.9 | 89.6
2019-07-12 22:30 | 87.37 | 87.04
2019-07-12 23:00 | 108.6 | 108.43
2019-07-12 23:30 | 92.55 | 92.43
2019-07-13 | 72.75 | 72.71
2019-07-13 00:30 | 73.46 | 73.42
2019-07-13 01:00 | 66.41 | 66.35
2019-07-13 01:30 | 64.54 | 62.57
2019-07-13 02:00 | 75.77 | 74.1
2019-07-13 02:30 | 76.64 | 75
2019-07-13 03:00 | 90.14 | 88.08
2019-07-13 03:30 | 91.34 | 87.74
2019-07-13 04:00 | 102.93 | 100.01
2019-07-13 04:30 | 103.41 | 100.61
2019-07-13 05:00 | 107.24 | 104.53
2019-07-13 05:30 | 110.09 | 107.52
2019-07-13 06:00 | 105.84 | 102.91
2019-07-13 06:30 | 96.8 | 94.27
2019-07-13 07:00 | 86.41 | 83.79
2019-07-13 07:30 | 80.58 | 78.99
2019-07-13 08:00 | 64.95 | 64.42
2019-07-13 08:30 | 70.75 | 70.48
2019-07-13 09:00 | 41.61 | 41.61
2019-07-13 09:30 | 18.04 | 8.61
2019-07-13 10:00 | 22.21 | 16.1
2019-07-13 10:30 | 33.31 | 29.92
2019-07-13 11:00 | 33.21 | 30
2019-07-13 11:30 | 28.14 | -23.15
2019-07-13 12:00 | 46.04 | -42.55
2019-07-13 12:30 | 46.98 | -43.31
2019-07-13 13:00 | 48.3 | -44.64
2019-07-13 13:30 | 33.19 | -28.31
2019-07-13 14:00 | 20.52 | -12.96
2019-07-13 14:30 | 18.56 | -8.51
2019-07-13 15:00 | 20.77 | 14.68
2019-07-13 15:30 | 41.33 | 38.9
2019-07-13 16:00 | 67.98 | 66.65
2019-07-13 16:30 | 94.56 | 93.55
2019-07-13 17:00 | 90.9 | 89.66
2019-07-13 17:30 | 109.55 | 106.33
2019-07-13 18:00 | 154.6 | 137.85
2019-07-13 18:30 | 160.86 | 145.7
2019-07-13 19:00 | 155.81 | 140.39
2019-07-13 19:30 | 140.5 | 124.54
2019-07-13 20:00 | 106.55 | 105.75
2019-07-13 20:30 | 90.77 | 89.98
2019-07-13 21:00 | 97.53 | 97.01
2019-07-13 21:30 | 86.63 | 86.25
2019-07-13 22:00 | 77.75 | 77.53
2019-07-13 22:30 | 78.81 | 78.66
2019-07-13 23:00 | 87.11 | 86.97
2019-07-13 23:30 | 79.26 | 79.19
2019-07-14 | 82.56 | 82.55
2019-07-14 00:30 | 91.34 | 91.34
2019-07-14 01:00 | 88.11 | 87.31
2019-07-14 01:30 | 79.21 | 75.89
2019-07-14 02:00 | 77.34 | 73.83
2019-07-14 02:30 | 77.74 | 74.17
2019-07-14 03:00 | 85.79 | 82.66
2019-07-14 03:30 | 89.46 | 86.47
2019-07-14 04:00 | 100.59 | 97.39
2019-07-14 04:30 | 107.13 | 104.32
2019-07-14 05:00 | 115.43 | 112.86
2019-07-14 05:30 | 115.67 | 113.3
2019-07-14 06:00 | 123.23 | 121.47
2019-07-14 06:30 | 111.57 | 109.93
2019-07-14 07:00 | 95.36 | 93.63
2019-07-14 07:30 | 85.68 | 84.68
2019-07-14 08:00 | 84.07 | 83.45
2019-07-14 08:30 | 93.15 | 92.79
2019-07-14 09:00 | 97.98 | 97.17
2019-07-14 09:30 | 96.19 | 95.31
2019-07-14 10:00 | 50.79 | 49.08
2019-07-14 10:30 | 38.59 | 36.39
2019-07-14 11:00 | 25.46 | 21.97
2019-07-14 11:30 | 21.77 | 17.67
2019-07-14 12:00 | 22.92 | 19.67
2019-07-14 12:30 | 21.37 | 18.01
2019-07-14 13:00 | 23.97 | 21.41
2019-07-14 13:30 | 24.44 | 22.07
2019-07-14 14:00 | 32.78 | 30.92
2019-07-14 14:30 | 45.79 | 44.49
2019-07-14 15:00 | 52.86 | 51.72
2019-07-14 15:30 | 72.5 | 71.66
2019-07-14 16:00 | 90.71 | 90.01
2019-07-14 16:30 | 98.96 | 98.23
2019-07-14 17:00 | 104.66 | 102.89
2019-07-14 17:30 | 161.56 | 154.05
2019-07-14 18:00 | 213.7 | 198.07
2019-07-14 18:30 | 231.76 | 217.16
2019-07-14 19:00 | 234.3 | 220.48
2019-07-14 19:30 | 220 | 205.97
2019-07-14 20:00 | 206.9 | 192.72
2019-07-14 20:30 | 210.84 | 197.79
2019-07-14 21:00 | 195.56 | 187.28
2019-07-14 21:30 | 179.09 | 173.22
2019-07-14 22:00 | 172.21 | 168.13
2019-07-14 22:30 | 162.32 | 161.99
2019-07-14 23:00 | 177.73 | 177.05
2019-07-14 23:30 | 165.63 | 164.81
2019-07-15 | 152.69 | 151.69
2019-07-15 00:30 | 155.09 | 154.1
2019-07-15 01:00 | 139.99 | 138.95
2019-07-15 01:30 | 131.14 | 130.17
2019-07-15 02:00 | 128.07 | 126.95
2019-07-15 02:30 | 128.05 | 127.26
2019-07-15 03:00 | 123.32 | 122.84
2019-07-15 03:30 | 124.82 | 124.36
2019-07-15 04:00 | 126.34 | 125.94
2019-07-15 04:30 | 130.85 | 130.47
2019-07-15 05:00 | 137.05 | 136.54
2019-07-15 05:30 | 148.89 | 148.24
2019-07-15 06:00 | 169.32 | 168.81
2019-07-15 06:30 | 189.34 | 189.27
2019-07-15 07:00 | 222.33 | 221.88
2019-07-15 07:30 | 242.89 | 239.16
2019-07-15 08:00 | 235.22 | 233.41
2019-07-15 08:30 | 213.91 | 213.52
2019-07-15 09:00 | 190.72 | 190.68
2019-07-15 09:30 | 173.28 | 173.23
2019-07-15 10:00 | 100.8 | 100.68
2019-07-15 10:30 | 86.64 | 86.34
2019-07-15 11:00 | 72.98 | 72.54
2019-07-15 11:30 | 58.17 | 57.71
2019-07-15 12:00 | 63.44 | 63.06
2019-07-15 12:30 | 63.67 | 63.35
2019-07-15 13:00 | 59.02 | 58.66
2019-07-15 13:30 | 68.13 | 67.84
2019-07-15 14:00 | 79.09 | 78.75
2019-07-15 14:30 | 95.6 | 95.29
2019-07-15 15:00 | 95.23 | 94.88
2019-07-15 15:30 | 118.57 | 118.2
2019-07-15 16:00 | 150.73 | 150.46
2019-07-15 16:30 | 178.69 | 178.54
2019-07-15 17:00 | 186.28 | 186.18
2019-07-15 17:30 | 204.12 | 203.37
2019-07-15 18:00 | 233.37 | 232.94
2019-07-15 18:30 | 230.58 | 230.46
2019-07-15 19:00 | 234.5 | 233.31
2019-07-15 19:30 | 215.03 | 214.64
2019-07-15 20:00 | 205.59 | 204.22
2019-07-15 20:30 | 209.26 | 207.1
2019-07-15 21:00 | 177.94 | 175.99
2019-07-15 21:30 | 197.12 | 195.81
2019-07-15 22:00 | 167.77 | 166.84
2019-07-15 22:30 | 136.08 | 136.07
2019-07-15 23:00 | 146.26 | 145.7
2019-07-15 23:30 | 144.65 | 143.98
2019-07-16 | 127.49 | 126.61
2019-07-16 00:30 | 137.03 | 136.01
2019-07-16 01:00 | 126.37 | 124.94
2019-07-16 01:30 | 116.09 | 114.82
2019-07-16 02:00 | 128.46 | 127.82
2019-07-16 02:30 | 129.26 | 128.63
2019-07-16 03:00 | 127.02 | 126.37
2019-07-16 03:30 | 125.92 | 125.37
2019-07-16 04:00 | 127.43 | 126.86
2019-07-16 04:30 | 133.54 | 133.02
2019-07-16 05:00 | 141.17 | 140.31
2019-07-16 05:30 | 154.51 | 153.48
2019-07-16 06:00 | 175 | 174.46
2019-07-16 06:30 | 190.96 | 190.93
2019-07-16 07:00 | 222.25 | 222.25
2019-07-16 07:30 | 251.89 | 251.36
2019-07-16 08:00 | 167.17 | 164.27
2019-07-16 08:30 | 184.04 | 179.02
2019-07-16 09:00 | 193.85 | 189.57
2019-07-16 09:30 | 148.41 | 143.66
2019-07-16 10:00 | 140.76 | 135.99
2019-07-16 10:30 | 100.28 | 94
2019-07-16 11:00 | 116.77 | 115.04
2019-07-16 11:30 | 54.13 | 53.71
2019-07-16 12:00 | 51.28 | 50.87
2019-07-16 12:30 | 67.59 | 67.27
2019-07-16 13:00 | 62.77 | 62.39
2019-07-16 13:30 | 75.16 | 74.84
2019-07-16 14:00 | 79.83 | 79.5
2019-07-16 14:30 | 92.13 | 91.85
2019-07-16 15:00 | 110.73 | 110.48
2019-07-16 15:30 | 129.96 | 129.7
2019-07-16 16:00 | 149.05 | 148.99
2019-07-16 16:30 | 154.91 | 154.91
2019-07-16 17:00 | 165.08 | 165.08
2019-07-16 17:30 | 179.7 | 176.56
2019-07-16 18:00 | 204.73 | 197.26
2019-07-16 18:30 | 223.6 | 218.95
2019-07-16 19:00 | 241.72 | 237.45
2019-07-16 19:30 | 231.01 | 226.88
2019-07-16 20:00 | 215.73 | 211.87
2019-07-16 20:30 | 202.83 | 199.25
2019-07-16 21:00 | 173.23 | 172.91
2019-07-16 21:30 | 163.65 | 163.38
2019-07-16 22:00 | 136.44 | 136.4
2019-07-16 22:30 | 131.05 | 130.8
2019-07-16 23:00 | 138.99 | 138.5
2019-07-16 23:30 | 132.31 | 131.69
2019-07-17 | 123.39 | 122.5
2019-07-17 00:30 | 114.88 | 113.9
2019-07-17 01:00 | 96.88 | 95.62
2019-07-17 01:30 | 86.16 | 84.42
2019-07-17 02:00 | 73.72 | 71.59
2019-07-17 02:30 | 72.53 | 71.19
2019-07-17 03:00 | 90.97 | 89.85
2019-07-17 03:30 | 108.84 | 107.96
2019-07-17 04:00 | 117.56 | 116.92
2019-07-17 04:30 | 132.07 | 131.51
2019-07-17 05:00 | 139.21 | 138.6
2019-07-17 05:30 | 154.68 | 153.98
2019-07-17 06:00 | 171.55 | 171.16
2019-07-17 06:30 | 201.73 | 201.72
2019-07-17 07:00 | 228.34 | 228.34
2019-07-17 07:30 | 246.89 | 246.88
2019-07-17 08:00 | 238.35 | 236.4
2019-07-17 08:30 | 197.1 | 188.33
2019-07-17 09:00 | 180.82 | 179.53
2019-07-17 09:30 | 167.37 | 167.21
2019-07-17 10:00 | 150.25 | 150.15
2019-07-17 10:30 | 118.81 | 118.72
2019-07-17 11:00 | 78.2 | 78.19
2019-07-17 11:30 | 77.25 | 77.24
2019-07-17 12:00 | 79.24 | 79.24
2019-07-17 12:30 | 83.83 | 83.83
2019-07-17 13:00 | 93.08 | 93.08
2019-07-17 13:30 | 103.17 | 103.17
2019-07-17 14:00 | 110.76 | 110.76
2019-07-17 14:30 | 130.93 | 130.93
2019-07-17 15:00 | 135.95 | 135.95
2019-07-17 15:30 | 148.98 | 148.98
2019-07-17 16:00 | 146 | 145.99
2019-07-17 16:30 | 165.95 | 165.94
2019-07-17 17:00 | 197.93 | 197.92
2019-07-17 17:30 | 210.01 | 204.58
2019-07-17 18:00 | 223.36 | 215.11
2019-07-17 18:30 | 235.24 | 227.78
2019-07-17 19:00 | 247.51 | 240.65
2019-07-17 19:30 | 239 | 232.4
2019-07-17 20:00 | 244.02 | 238.02
2019-07-17 20:30 | 234.97 | 229.22
2019-07-17 21:00 | 216.61 | 212.13
2019-07-17 21:30 | 216.2 | 215.13
2019-07-17 22:00 | 199.73 | 199.36
2019-07-17 22:30 | 195.64 | 195.19
2019-07-17 23:00 | 192.79 | 192.16
2019-07-17 23:30 | 177.89 | 177.14
2019-07-18 | 162.73 | 161.78
2019-07-18 00:30 | 149.93 | 148.84
2019-07-18 01:00 | 130.06 | 128.56
2019-07-18 01:30 | 117.27 | 115.85
2019-07-18 02:00 | 109.57 | 108.55
2019-07-18 02:30 | 111.52 | 110.5
2019-07-18 03:00 | 103.55 | 102.37
2019-07-18 03:30 | 99.62 | 98.43
2019-07-18 04:00 | 97.96 | 96.64
2019-07-18 04:30 | 124.25 | 123.28
2019-07-18 05:00 | 131.61 | 130.62
2019-07-18 05:30 | 151.13 | 150.28
2019-07-18 06:00 | 160.71 | 160.23
2019-07-18 06:30 | 190.63 | 190.63
2019-07-18 07:00 | 219.13 | 216.9
2019-07-18 07:30 | 238.43 | 235.52
2019-07-18 08:00 | 218.24 | 214.31
2019-07-18 08:30 | 198.32 | 193.95
2019-07-18 09:00 | 162.87 | 158.41
2019-07-18 09:30 | 90.07 | 82.72
2019-07-18 10:00 | 95.76 | 95.73
2019-07-18 10:30 | 92.36 | 92.31
2019-07-18 11:00 | 78.51 | 78.45
2019-07-18 11:30 | 63.41 | 63.36
2019-07-18 12:00 | 52.75 | 52.7
2019-07-18 12:30 | 52.64 | 52.61
2019-07-18 13:00 | 57.69 | 57.67
2019-07-18 13:30 | 74.07 | 74.04
2019-07-18 14:00 | 93.69 | 93.67
2019-07-18 14:30 | 113.45 | 113.44
2019-07-18 15:00 | 125.35 | 125.34
2019-07-18 15:30 | 125.5 | 125.5
2019-07-18 16:00 | 149.81 | 149.81
2019-07-18 16:30 | 158.05 | 158.05
2019-07-18 17:00 | 183.39 | 183.38
2019-07-18 17:30 | 191.5 | 189.22
2019-07-18 18:00 | 229.2 | 220.65
2019-07-18 18:30 | 237.05 | 228.74
2019-07-18 19:00 | 252.38 | 244.58
2019-07-18 19:30 | 255.69 | 248.43
2019-07-18 20:00 | 258.78 | 251.8
2019-07-18 20:30 | 256.64 | 250.3
2019-07-18 21:00 | 240.04 | 234.04
2019-07-18 21:30 | 217.11 | 213.91
2019-07-18 22:00 | 186.06 | 185.8
2019-07-18 22:30 | 189.87 | 189.68
2019-07-18 23:00 | 196.99 | 196.91
2019-07-18 23:30 | 184.4 | 184.36
2019-07-19 | 165.25 | 164.75
2019-07-19 00:30 | 153.89 | 153.04
2019-07-19 01:00 | 129.42 | 128.84
2019-07-19 01:30 | 122.11 | 121.74
2019-07-19 02:00 | 94.6 | 93.86
2019-07-19 02:30 | 78.52 | 77.44
2019-07-19 03:00 | 77.25 | 76.22
2019-07-19 03:30 | 85.21 | 84.24
2019-07-19 04:00 | 88.06 | 87.24
2019-07-19 04:30 | 103.8 | 103.08
2019-07-19 05:00 | 132.72 | 132.14
2019-07-19 05:30 | 153.05 | 152.47
2019-07-19 06:00 | 170.25 | 169.72
2019-07-19 06:30 | 194.38 | 194.23
2019-07-19 07:00 | 220.62 | 220.62
2019-07-19 07:30 | 251.28 | 245.14
2019-07-19 08:00 | 237.4 | 230.02
2019-07-19 08:30 | 209.5 | 203.73
2019-07-19 09:00 | 181.66 | 177.4
2019-07-19 09:30 | 164.58 | 162.44
2019-07-19 10:00 | 118.5 | 118.28
2019-07-19 10:30 | 100.25 | 100.2
2019-07-19 11:00 | 86.4 | 86.39
2019-07-19 11:30 | 67.94 | 67.94
2019-07-19 12:00 | 70.88 | 70.87
2019-07-19 12:30 | 73.13 | 73.11
2019-07-19 13:00 | 81.6 | 81.59
2019-07-19 13:30 | 79.94 | 79.92
2019-07-19 14:00 | 92.45 | 92.44
2019-07-19 14:30 | 96.7 | 96.68
2019-07-19 15:00 | 97.94 | 97.91
2019-07-19 15:30 | 108.77 | 108.72
2019-07-19 16:00 | 134.2 | 134.15
2019-07-19 16:30 | 145.19 | 145.12
2019-07-19 17:00 | 182.72 | 182.71
2019-07-19 17:30 | 192.79 | 192.79
2019-07-19 18:00 | 197.4 | 197.4
2019-07-19 18:30 | 200.54 | 200.53
2019-07-19 19:00 | 205.02 | 204.88
2019-07-19 19:30 | 182.87 | 182.77
2019-07-19 20:00 | 183.04 | 182.97
2019-07-19 20:30 | 206.64 | 206.62
2019-07-19 21:00 | 179.58 | 179.58
2019-07-19 21:30 | 166.16 | 165.9
2019-07-19 22:00 | 154.64 | 154.18
2019-07-19 22:30 | 158.95 | 158.57
2019-07-19 23:00 | 152.25 | 151.97
2019-07-19 23:30 | 132.81 | 132.6
2019-07-20 | 126.27 | 126.05
2019-07-20 00:30 | 111.41 | 109.77
2019-07-20 01:00 | 96.26 | 94.02
2019-07-20 01:30 | 81.45 | 78.85
2019-07-20 02:00 | 58.44 | 55.32
2019-07-20 02:30 | 54.07 | 50.64
2019-07-20 03:00 | 60.73 | 57.89
2019-07-20 03:30 | 70.42 | 68.06
2019-07-20 04:00 | 83.41 | 81.48
2019-07-20 04:30 | 87.27 | 85.57
2019-07-20 05:00 | 92.69 | 91
2019-07-20 05:30 | 118.94 | 117.67
2019-07-20 06:00 | 130.54 | 129.18
2019-07-20 06:30 | 140.07 | 138.6
2019-07-20 07:00 | 153.87 | 152.87
2019-07-20 07:30 | 167.47 | 166.9
2019-07-20 08:00 | 151.3 | 150.24
2019-07-20 08:30 | 137.17 | 134.62
2019-07-20 09:00 | 126.98 | 124.93
2019-07-20 09:30 | 113.23 | 113.19
2019-07-20 10:00 | 101.28 | 100.92
2019-07-20 10:30 | 84.64 | 84.02
2019-07-20 11:00 | 71.58 | 70.37
2019-07-20 11:30 | 57.46 | 55.84
2019-07-20 12:00 | 48.65 | 46.51
2019-07-20 12:30 | 40.84 | 38.58
2019-07-20 13:00 | 42.48 | 40.2
2019-07-20 13:30 | 40.93 | 38.42
2019-07-20 14:00 | 66.77 | 64.55
2019-07-20 14:30 | 79.03 | 76.8
2019-07-20 15:00 | 86.64 | 84.48
2019-07-20 15:30 | 80.72 | 77.83
2019-07-20 16:00 | 104.09 | 101.97
2019-07-20 16:30 | 135.72 | 134.32
2019-07-20 17:00 | 150.46 | 149.88
2019-07-20 17:30 | 165.32 | 165.29
2019-07-20 18:00 | 154.35 | 153.36
2019-07-20 18:30 | 157.97 | 156.46
2019-07-20 19:00 | 155.18 | 153.68
2019-07-20 19:30 | 148.62 | 147.33
2019-07-20 20:00 | 144.07 | 142.86
2019-07-20 20:30 | 137.1 | 136.05
2019-07-20 21:00 | 125.01 | 124.15
2019-07-20 21:30 | 125.72 | 125.15
2019-07-20 22:00 | 123.88 | 123.52
2019-07-20 22:30 | 146.51 | 146.26
2019-07-20 23:00 | 158.79 | 158.64
2019-07-20 23:30 | 148.13 | 148.05
2019-07-21 | 100.96 | 100.85
2019-07-21 00:30 | 105.56 | 103.76
2019-07-21 01:00 | 119.89 | 118.18
2019-07-21 01:30 | 116.4 | 115.19
2019-07-21 02:00 | 100.59 | 99.38
2019-07-21 02:30 | 104.01 | 102.94
2019-07-21 03:00 | 107.13 | 106.12
2019-07-21 03:30 | 103.45 | 102.05
2019-07-21 04:00 | 108.88 | 107.64
2019-07-21 04:30 | 107.22 | 105.9
2019-07-21 05:00 | 110.57 | 109.18
2019-07-21 05:30 | 125.27 | 124.07
2019-07-21 06:00 | 131.58 | 130.44
2019-07-21 06:30 | 140.88 | 139.79
2019-07-21 07:00 | 146.54 | 145.45
2019-07-21 07:30 | 140.2 | 138.77
2019-07-21 08:00 | 121.93 | 120.31
2019-07-21 08:30 | 83.16 | 82.33
2019-07-21 09:00 | 65.12 | 64.4
2019-07-21 09:30 | 61.49 | 60.8
2019-07-21 10:00 | 52.22 | 51.42
2019-07-21 10:30 | 51.41 | 50.41
2019-07-21 11:00 | 44.98 | 43.78
2019-07-21 11:30 | 51.55 | 50.12
2019-07-21 12:00 | 51.6 | 50.21
2019-07-21 12:30 | 62.18 | 60.42
2019-07-21 13:00 | 55.41 | 51.8
2019-07-21 13:30 | 42.13 | 38.04
2019-07-21 14:00 | 54.69 | 51.64
2019-07-21 14:30 | 65.99 | 63.36
2019-07-21 15:00 | 65.38 | 62.3
2019-07-21 15:30 | 76.65 | 74.1
2019-07-21 16:00 | 120.02 | 118.87
2019-07-21 16:30 | 119.04 | 118.37
2019-07-21 17:00 | 139.76 | 139.51
2019-07-21 17:30 | 149.1 | 149.09
2019-07-21 18:00 | 173.21 | 166.83
2019-07-21 18:30 | 194.64 | 186.52
2019-07-21 19:00 | 195.16 | 187.44
2019-07-21 19:30 | 183.99 | 176.44
2019-07-21 20:00 | 174.48 | 167.04
2019-07-21 20:30 | 159.26 | 151.71
2019-07-21 21:00 | 137.16 | 136.06
2019-07-21 21:30 | 151.65 | 151.37
2019-07-21 22:00 | 146.27 | 145.76
2019-07-21 22:30 | 152.09 | 151.43
2019-07-21 23:00 | 161.16 | 160.36
2019-07-21 23:30 | 143.74 | 142.44
2019-07-22 | 128.42 | 126.8
2019-07-22 00:30 | 117.87 | 116.33
2019-07-22 01:00 | 108.93 | 107.88
2019-07-22 01:30 | 96.8 | 95.77
2019-07-22 02:00 | 94.35 | 93.17
2019-07-22 02:30 | 91.24 | 90.04
2019-07-22 03:00 | 81.68 | 80.2
2019-07-22 03:30 | 77.02 | 75.47
2019-07-22 04:00 | 80.25 | 78.79
2019-07-22 04:30 | 95.5 | 94.47
2019-07-22 05:00 | 114.92 | 113.92
2019-07-22 05:30 | 139.26 | 138.16
2019-07-22 06:00 | 155.06 | 154.02
2019-07-22 06:30 | 158.2 | 157.48
2019-07-22 07:00 | 169.99 | 169.94
2019-07-22 07:30 | 192.16 | 192.16
2019-07-22 08:00 | 170.2 | 170.17
2019-07-22 08:30 | 136.53 | 136.5
2019-07-22 09:00 | 117.41 | 117.3
2019-07-22 09:30 | 90.37 | 90.36
2019-07-22 10:00 | 74.68 | 74.65
2019-07-22 10:30 | 44.61 | 44.61
2019-07-22 11:00 | 17.75 | 17.73
2019-07-22 11:30 | 39.25 | 39.24
2019-07-22 12:00 | 59.42 | 59.36
2019-07-22 12:30 | 59.12 | 59.05
2019-07-22 13:00 | 71.77 | 71.73
2019-07-22 13:30 | 78.49 | 78.45
2019-07-22 14:00 | 94.86 | 94.84
2019-07-22 14:30 | 106.41 | 106.39
2019-07-22 15:00 | 112.94 | 112.92
2019-07-22 15:30 | 110.67 | 110.67
2019-07-22 16:00 | 127.66 | 127.66
2019-07-22 16:30 | 120.75 | 120.75
2019-07-22 17:00 | 136.59 | 136.58
2019-07-22 17:30 | 162.31 | 160.81
2019-07-22 18:00 | 184.98 | 179.53
2019-07-22 18:30 | 200.05 | 184.77
2019-07-22 19:00 | 195.15 | 183.99
2019-07-22 19:30 | 181.29 | 173.99
2019-07-22 20:00 | 164.96 | 160.73
2019-07-22 20:30 | 151.07 | 148.84
2019-07-22 21:00 | 144.61 | 142.73
2019-07-22 21:30 | 134.51 | 133.43
2019-07-22 22:00 | 120.55 | 119.57
2019-07-22 22:30 | 129.06 | 127.98
2019-07-22 23:00 | 146.26 | 145.31
2019-07-22 23:30 | 138.06 | 136.94
2019-07-23 | 114.83 | 113.35
2019-07-23 00:30 | 118.69 | 117.59
2019-07-23 01:00 | 105.38 | 104.63
2019-07-23 01:30 | 101.19 | 100.49
2019-07-23 02:00 | 87.21 | 86.06
2019-07-23 02:30 | 87.26 | 86.08
2019-07-23 03:00 | 102.9 | 101.87
2019-07-23 03:30 | 114.31 | 113.37
2019-07-23 04:00 | 115.89 | 114.97
2019-07-23 04:30 | 113.71 | 112.53
2019-07-23 05:00 | 112.44 | 111.04
2019-07-23 05:30 | 137.99 | 136.77
2019-07-23 06:00 | 155.03 | 153.93
2019-07-23 06:30 | 166.01 | 165.34
2019-07-23 07:00 | 178.46 | 178.31
2019-07-23 07:30 | 197.55 | 197.55
2019-07-23 08:00 | 185.29 | 185.29
2019-07-23 08:30 | 158.88 | 158.88
2019-07-23 09:00 | 140.37 | 140.37
2019-07-23 09:30 | 117.5 | 117.25
2019-07-23 10:00 | 94.96 | 94.96
2019-07-23 10:30 | 73.15 | 73.15
2019-07-23 11:00 | 70.73 | 70.72
2019-07-23 11:30 | 59.72 | 59.72
2019-07-23 12:00 | 61.07 | 61.06
2019-07-23 12:30 | 63.23 | 63.23
2019-07-23 13:00 | 67.98 | 67.97
2019-07-23 13:30 | 72.68 | 72.68
2019-07-23 14:00 | 106.47 | 106.46
2019-07-23 14:30 | 101.54 | 101.52
2019-07-23 15:00 | 120.81 | 120.8
2019-07-23 15:30 | 138.71 | 138.7
2019-07-23 16:00 | 142.77 | 142.76
2019-07-23 16:30 | 160.59 | 160.57
2019-07-23 17:00 | 168.14 | 168.13
2019-07-23 17:30 | 183.73 | 183.23
2019-07-23 18:00 | 178.7 | 174.98
2019-07-23 18:30 | 195.71 | 182.45
2019-07-23 19:00 | 208.14 | 201.63
2019-07-23 19:30 | 188.45 | 183.55
2019-07-23 20:00 | 186.92 | 185.18
2019-07-23 20:30 | 177.07 | 176.42
2019-07-23 21:00 | 167.16 | 166.85
2019-07-23 21:30 | 167.52 | 166.97
2019-07-23 22:00 | 164.59 | 163.91
2019-07-23 22:30 | 158.2 | 157.37
2019-07-23 23:00 | 172.69 | 171.69
2019-07-23 23:30 | 161.43 | 160.26
2019-07-24 | 146.42 | 145.14
2019-07-24 00:30 | 133.65 | 132.05
2019-07-24 01:00 | 122.1 | 120.55
2019-07-24 01:30 | 103.69 | 102.67
2019-07-24 02:00 | 87.1 | 85.68
2019-07-24 02:30 | 83.23 | 81.69
2019-07-24 03:00 | 91.67 | 90.29
2019-07-24 03:30 | 87.39 | 85.79
2019-07-24 04:00 | 88.47 | 86.85
2019-07-24 04:30 | 95.32 | 93.54
2019-07-24 05:00 | 109.16 | 107.47
2019-07-24 05:30 | 132.78 | 130.94
2019-07-24 06:00 | 147.85 | 146.34
2019-07-24 06:30 | 176.1 | 175.28
2019-07-24 07:00 | 167.45 | 167.25
2019-07-24 07:30 | 180.04 | 175.97
2019-07-24 08:00 | 185.57 | 175.5
2019-07-24 08:30 | 177.52 | 167.26
2019-07-24 09:00 | 163.44 | 158.01
2019-07-24 09:30 | 152.33 | 147.63
2019-07-24 10:00 | 141.07 | 140.9
2019-07-24 10:30 | 127.37 | 127.2
2019-07-24 11:00 | 123.04 | 122.85
2019-07-24 11:30 | 119.47 | 119.27
2019-07-24 12:00 | 120.93 | 120.71
2019-07-24 12:30 | 121.74 | 121.54
2019-07-24 13:00 | 124.85 | 124.62
2019-07-24 13:30 | 131.24 | 131
2019-07-24 14:00 | 135.47 | 135.39
2019-07-24 14:30 | 91.88 | 91.87
2019-07-24 15:00 | 75.8 | 75.8
2019-07-24 15:30 | 84.32 | 84.32
2019-07-24 16:00 | 123.3 | 123.3
2019-07-24 16:30 | 143.51 | 143.51
2019-07-24 17:00 | 153.75 | 153.75
2019-07-24 17:30 | 147.17 | 146.11
2019-07-24 18:00 | 153.11 | 149.28
2019-07-24 18:30 | 145.53 | 143.65
2019-07-24 19:00 | 150.28 | 149.67
2019-07-24 19:30 | 151.01 | 149.87
2019-07-24 20:00 | 148.73 | 146.22
2019-07-24 20:30 | 142.06 | 139.92
2019-07-24 21:00 | 124.72 | 124.43
2019-07-24 21:30 | 113.33 | 112.76
2019-07-24 22:00 | 111.08 | 110.06
2019-07-24 22:30 | 105.4 | 104.18
2019-07-24 23:00 | 124.88 | 123.76
2019-07-24 23:30 | 106.49 | 104.97
2019-07-25 | 98.52 | 96.63
2019-07-25 00:30 | 79.22 | 76.36
2019-07-25 01:00 | 61.91 | 58.19
2019-07-25 01:30 | 49.17 | 44.48
2019-07-25 02:00 | 42.51 | 38.25
2019-07-25 02:30 | 37.8 | 34.74
2019-07-25 03:00 | 34.4 | 31.19
2019-07-25 03:30 | 48.99 | 46.67
2019-07-25 04:00 | 50.24 | 47.84
2019-07-25 04:30 | 46.24 | 42.86
2019-07-25 05:00 | 71.02 | 68.28
2019-07-25 05:30 | 102.12 | 99.85
2019-07-25 06:00 | 127.3 | 125.82
2019-07-25 06:30 | 134.27 | 133.71
2019-07-25 07:00 | 150.31 | 150.03
2019-07-25 07:30 | 171.5 | 171.06
2019-07-25 08:00 | 171.13 | 170.21
2019-07-25 08:30 | 162.95 | 161.63
2019-07-25 09:00 | 154.04 | 152.97
2019-07-25 09:30 | 141.34 | 140.26
2019-07-25 10:00 | 132 | 131.92
2019-07-25 10:30 | 114.42 | 114.3
2019-07-25 11:00 | 118.53 | 118.39
2019-07-25 11:30 | 103.21 | 103.02
2019-07-25 12:00 | 109.57 | 109.37
2019-07-25 12:30 | 110.59 | 110.39
2019-07-25 13:00 | 110.22 | 110.02
2019-07-25 13:30 | 115.4 | 115.24
2019-07-25 14:00 | 121.11 | 120.98
2019-07-25 14:30 | 130 | 129.87
2019-07-25 15:00 | 134.11 | 134.02
2019-07-25 15:30 | 138.32 | 138.31
2019-07-25 16:00 | 99.22 | 99.15
2019-07-25 16:30 | 112.39 | 112.3
2019-07-25 17:00 | 131.15 | 131.1
2019-07-25 17:30 | 122.91 | 122.91
2019-07-25 18:00 | 149.3 | 149.1
2019-07-25 18:30 | 155.42 | 155.19
2019-07-25 19:00 | 160.88 | 160.76
2019-07-25 19:30 | 151.61 | 151.47
2019-07-25 20:00 | 137.05 | 136.93
2019-07-25 20:30 | 123.25 | 123.25
2019-07-25 21:00 | 102.33 | 102.3
2019-07-25 21:30 | 104.39 | 104.18
2019-07-25 22:00 | 99.11 | 98.56
2019-07-25 22:30 | 119.23 | 118.4
2019-07-25 23:00 | 141.45 | 140.47
2019-07-25 23:30 | 127.95 | 126.74
2019-07-26 | 108.25 | 106.61
2019-07-26 00:30 | 106.44 | 104.41
2019-07-26 01:00 | 89.08 | 86.77
2019-07-26 01:30 | 80.82 | 78.56
2019-07-26 02:00 | 67.49 | 64.39
2019-07-26 02:30 | 63.85 | 60.29
2019-07-26 03:00 | 60.9 | 57.35
2019-07-26 03:30 | 63.27 | 59.66
2019-07-26 04:00 | 67.38 | 64.04
2019-07-26 04:30 | 77.26 | 73.97
2019-07-26 05:00 | 92.69 | 89.93
2019-07-26 05:30 | 116.45 | 114.58
2019-07-26 06:00 | 139.8 | 138.6
2019-07-26 06:30 | 150.94 | 150.47
2019-07-26 07:00 | 148.25 | 148.02
2019-07-26 07:30 | 137.66 | 137.62
2019-07-26 08:00 | 124.3 | 124.28
2019-07-26 08:30 | 68.28 | 68.28
2019-07-26 09:00 | 127.46 | 127.46
2019-07-26 09:30 | 147 | 146.97
2019-07-26 10:00 | 146.91 | 146.91
2019-07-26 10:30 | 112.15 | 112.13
2019-07-26 11:00 | 118.26 | 118.21
2019-07-26 11:30 | 105.6 | 105.39
2019-07-26 12:00 | 103.07 | 102.9
2019-07-26 12:30 | 58.76 | 58.73
2019-07-26 13:00 | 59.32 | 59.32
2019-07-26 13:30 | 107.26 | 107.26
2019-07-26 14:00 | 118.83 | 118.72
2019-07-26 14:30 | 123.73 | 123.71
2019-07-26 15:00 | 85.16 | 85
2019-07-26 15:30 | 107.9 | 107.64
2019-07-26 16:00 | 144.49 | 144.35
2019-07-26 16:30 | 145.18 | 145.11
2019-07-26 17:00 | 167.62 | 167.57
2019-07-26 17:30 | 197.81 | 197.76
2019-07-26 18:00 | 155.72 | 155.53
2019-07-26 18:30 | 159.88 | 159.5
2019-07-26 19:00 | 154.42 | 153.92
2019-07-26 19:30 | 137.1 | 136.61
2019-07-26 20:00 | 122.67 | 122.58
2019-07-26 20:30 | 111.72 | 111.52
2019-07-26 21:00 | 104.63 | 104.27
2019-07-26 21:30 | 91.11 | 90.3
2019-07-26 22:00 | 85.04 | 83.67
2019-07-26 22:30 | 94.29 | 92.67
2019-07-26 23:00 | 104.76 | 102.95
2019-07-26 23:30 | 93.47 | 91.05
2019-07-27 | 86.3 | 83
2019-07-27 00:30 | 75.72 | 71.02
2019-07-27 01:00 | 77.89 | 73.37
2019-07-27 01:30 | 46.08 | 38.46
2019-07-27 02:00 | 25.42 | 5.29
2019-07-27 02:30 | 24.86 | -3.61
2019-07-27 03:00 | 26 | 8.96
2019-07-27 03:30 | 31.27 | 19.19
2019-07-27 04:00 | 31.71 | 19.66
2019-07-27 04:30 | 44.48 | 36.31
2019-07-27 05:00 | 64.82 | 59.05
2019-07-27 05:30 | 79.87 | 75.12
2019-07-27 06:00 | 90.67 | 86.38
2019-07-27 06:30 | 85.6 | 81.79
2019-07-27 07:00 | 85.37 | 81.65
2019-07-27 07:30 | 80.93 | 77.85
2019-07-27 08:00 | 82.05 | 79.81
2019-07-27 08:30 | 72.57 | 70.44
2019-07-27 09:00 | 57.19 | 54.9
2019-07-27 09:30 | 54.01 | 51.94
2019-07-27 10:00 | 40.36 | 37.65
2019-07-27 10:30 | 26.55 | 22.32
2019-07-27 11:00 | 16.05 | 7.94
2019-07-27 11:30 | 56.08 | -55.46
2019-07-27 12:00 | 90.11 | -90.08
2019-07-27 12:30 | 75.74 | -75.6
2019-07-27 13:00 | 65.31 | -64.99
2019-07-27 13:30 | 36.88 | -35.9
2019-07-27 14:00 | 11.63 | -1.39
2019-07-27 14:30 | 21.21 | 17.88
2019-07-27 15:00 | 33.36 | 30.74
2019-07-27 15:30 | 42.6 | 40.55
2019-07-27 16:00 | 67.38 | 66.11
2019-07-27 16:30 | 90.74 | 89.75
2019-07-27 17:00 | 114.86 | 113.92
2019-07-27 17:30 | 128.27 | 127.47
2019-07-27 18:00 | 137.83 | 137.66
2019-07-27 18:30 | 143.06 | 142.87
2019-07-27 19:00 | 150.38 | 150.15
2019-07-27 19:30 | 144.69 | 144.29
2019-07-27 20:00 | 151.09 | 150.62
2019-07-27 20:30 | 134.79 | 134.02
2019-07-27 21:00 | 110.74 | 109.55
2019-07-27 21:30 | 105.1 | 103.4
2019-07-27 22:00 | 91.65 | 89.26
2019-07-27 22:30 | 109.32 | 106.95
2019-07-27 23:00 | 116.9 | 114.38
2019-07-27 23:30 | 119.13 | 116.35
2019-07-28 | 105.85 | 101.8
2019-07-28 00:30 | 98.7 | 94.68
2019-07-28 01:00 | 82.57 | 79.13
2019-07-28 01:30 | 62.2 | 57.75
2019-07-28 02:00 | 50.62 | 45.62
2019-07-28 02:30 | 46.96 | 41.94
2019-07-28 03:00 | 44.68 | 39.55
2019-07-28 03:30 | 44.49 | 39.48
2019-07-28 04:00 | 41.39 | 36.03
2019-07-28 04:30 | 51.45 | 47.22
2019-07-28 05:00 | 57.24 | 53.19
2019-07-28 05:30 | 63.37 | 59.22
2019-07-28 06:00 | 71.82 | 67.6
2019-07-28 06:30 | 82.31 | 78.37
2019-07-28 07:00 | 80.58 | 76.43
2019-07-28 07:30 | 78.99 | 74.52
2019-07-28 08:00 | 68.85 | 64.17
2019-07-28 08:30 | 62.53 | 58.1
2019-07-28 09:00 | 44.43 | 40.04
2019-07-28 09:30 | 32.62 | 30.2
2019-07-28 10:00 | 22.09 | 21.39
2019-07-28 10:30 | 18.58 | 15.68
2019-07-28 11:00 | 49.4 | -48.62
2019-07-28 11:30 | 15.09 | -14.74
2019-07-28 12:00 | 8.81 | 8.69
2019-07-28 12:30 | 12.27 | 12.15
2019-07-28 13:00 | 15.95 | 15.79
2019-07-28 13:30 | 30.24 | 29.73
2019-07-28 14:00 | 48.45 | 47.5
2019-07-28 14:30 | 69.14 | 68.45
2019-07-28 15:00 | 84 | 83.5
2019-07-28 15:30 | 72.82 | 72.35
2019-07-28 16:00 | 92.52 | 92.05
2019-07-28 16:30 | 96.7 | 96.26
2019-07-28 17:00 | 109.34 | 108.7
2019-07-28 17:30 | 128.38 | 128.09
2019-07-28 18:00 | 139.74 | 135.44
2019-07-28 18:30 | 154.61 | 147.94
2019-07-28 19:00 | 142.72 | 136.98
2019-07-28 19:30 | 127.09 | 125.38
2019-07-28 20:00 | 116.36 | 114.79
2019-07-28 20:30 | 105.28 | 103.79
2019-07-28 21:00 | 89.66 | 89.33
2019-07-28 21:30 | 85.53 | 84.12
2019-07-28 22:00 | 97.41 | 95.81
2019-07-28 22:30 | 119.43 | 117.94
2019-07-28 23:00 | 136.35 | 134.84
2019-07-28 23:30 | 119.23 | 117.64
2019-07-29 | 92.74 | 90.34
2019-07-29 00:30 | 73.48 | 69.77
2019-07-29 01:00 | 60.62 | 58.6
2019-07-29 01:30 | 36.69 | 35.16
2019-07-29 02:00 | 29.53 | 27.98
2019-07-29 02:30 | 47.61 | 46.75
2019-07-29 03:00 | 61.06 | 60.49
2019-07-29 03:30 | 67.76 | 67.25
2019-07-29 04:00 | 79.15 | 78.72
2019-07-29 04:30 | 88.38 | 87.81
2019-07-29 05:00 | 100.33 | 99.63
2019-07-29 05:30 | 112.6 | 111.56
2019-07-29 06:00 | 124.28 | 122.91
2019-07-29 06:30 | 139.64 | 138.32
2019-07-29 07:00 | 170.42 | 170.14
2019-07-29 07:30 | 179.28 | 179.26
2019-07-29 08:00 | 164.04 | 164.03
2019-07-29 08:30 | 138.49 | 138.49
2019-07-29 09:00 | 116.61 | 116.6
2019-07-29 09:30 | 100.94 | 100.94
2019-07-29 10:00 | 94.25 | 94.25
2019-07-29 10:30 | 76.78 | 76.78
2019-07-29 11:00 | 70.95 | 70.95
2019-07-29 11:30 | 82.59 | 82.59
2019-07-29 12:00 | 93.17 | 93.17
2019-07-29 12:30 | 95.85 | 95.84
2019-07-29 13:00 | 102.15 | 102.15
2019-07-29 13:30 | 109.77 | 109.77
2019-07-29 14:00 | 119.17 | 119.17
2019-07-29 14:30 | 117.74 | 117.73
2019-07-29 15:00 | 93.73 | 93.71
2019-07-29 15:30 | 108.44 | 108.42
2019-07-29 16:00 | 144.93 | 144.89
2019-07-29 16:30 | 152.16 | 152.11
2019-07-29 17:00 | 152.26 | 152.11
2019-07-29 17:30 | 169.08 | 169
2019-07-29 18:00 | 187.18 | 187.17
2019-07-29 18:30 | 187.1 | 187.09
2019-07-29 19:00 | 188.83 | 188.83
2019-07-29 19:30 | 186.45 | 186.44
2019-07-29 20:00 | 183.29 | 183.25
2019-07-29 20:30 | 169.64 | 169.58
2019-07-29 21:00 | 175.4 | 175.26
2019-07-29 21:30 | 158.26 | 157.89
2019-07-29 22:00 | 140.32 | 139.52
2019-07-29 22:30 | 141.46 | 140.42
2019-07-29 23:00 | 159.33 | 158.09
2019-07-29 23:30 | 142.74 | 141.15
2019-07-30 | 118.11 | 115.8
2019-07-30 00:30 | 109.06 | 106.44
2019-07-30 01:00 | 91.83 | 89.06
2019-07-30 01:30 | 76.84 | 73.41
2019-07-30 02:00 | 50.97 | 45.39
2019-07-30 02:30 | 43.39 | 36.18
2019-07-30 03:00 | 51.01 | 44.51
2019-07-30 03:30 | 59.35 | 53.59
2019-07-30 04:00 | 64.51 | 58.84
2019-07-30 04:30 | 75.21 | 70.31
2019-07-30 05:00 | 90.97 | 87.23
2019-07-30 05:30 | 122.89 | 120.61
2019-07-30 06:00 | 147.44 | 146.55
2019-07-30 06:30 | 163.65 | 163.3
2019-07-30 07:00 | 178.48 | 178.26
2019-07-30 07:30 | 200.65 | 200.59
2019-07-30 08:00 | 190.12 | 189.97
2019-07-30 08:30 | 153.78 | 153.43
2019-07-30 09:00 | 121.86 | 121.24
2019-07-30 09:30 | 97.62 | 96.84
2019-07-30 10:00 | 83.08 | 82.01
2019-07-30 10:30 | 60.56 | 59.4
2019-07-30 11:00 | 41.56 | 40.41
2019-07-30 11:30 | 33.63 | 33.55
2019-07-30 12:00 | 31.43 | 31.37
2019-07-30 12:30 | 42.72 | 42.67
2019-07-30 13:00 | 58.87 | 58.83
2019-07-30 13:30 | 54.52 | 54.45
2019-07-30 14:00 | 58.93 | 58.86
2019-07-30 14:30 | 79.97 | 79.92
2019-07-30 15:00 | 83.51 | 83.43
2019-07-30 15:30 | 85.24 | 85.15
2019-07-30 16:00 | 120.63 | 120.51
2019-07-30 16:30 | 140.94 | 140.86
2019-07-30 17:00 | 143.82 | 143.75
2019-07-30 17:30 | 152.24 | 152.23
2019-07-30 18:00 | 140.1 | 135.38
2019-07-30 18:30 | 137.27 | 133.05
2019-07-30 19:00 | 138.85 | 135.25
2019-07-30 19:30 | 117.88 | 114.47
2019-07-30 20:00 | 121.78 | 121.78
2019-07-30 20:30 | 135.31 | 135.21
2019-07-30 21:00 | 136.82 | 136.56
2019-07-30 21:30 | 145.76 | 145.24
2019-07-30 22:00 | 138.82 | 137.89
2019-07-30 22:30 | 142.43 | 141.29
2019-07-30 23:00 | 160.22 | 158.92
2019-07-30 23:30 | 152.82 | 151.98
2019-07-31 | 139.65 | 139.02
2019-07-31 00:30 | 117.68 | 116.86
2019-07-31 01:00 | 107.41 | 106.68
2019-07-31 01:30 | 95.78 | 95.11
2019-07-31 02:00 | 75.97 | 74.78
2019-07-31 02:30 | 72.76 | 71.29
2019-07-31 03:00 | 77.67 | 76.74
2019-07-31 03:30 | 75.57 | 75.51
2019-07-31 04:00 | 71.24 | 71.2
2019-07-31 04:30 | 85.53 | 85.47
2019-07-31 05:00 | 102.42 | 102.38
2019-07-31 05:30 | 123.73 | 123.72
2019-07-31 06:00 | 140.58 | 140.46
2019-07-31 06:30 | 149.21 | 148.82
2019-07-31 07:00 | 148.13 | 147.72
2019-07-31 07:30 | 141.37 | 141.33
2019-07-31 08:00 | 94.96 | 94.95
2019-07-31 08:30 | 128.77 | 128.76
2019-07-31 09:00 | 134.49 | 134.49
2019-07-31 09:30 | 107.95 | 107.95
2019-07-31 10:00 | 95.9 | 95.89
2019-07-31 10:30 | 77.29 | 77.26
2019-07-31 11:00 | 57.99 | 57.96
2019-07-31 11:30 | 30.8 | 30.73
2019-07-31 12:00 | 41.81 | 41.74
2019-07-31 12:30 | 47.36 | 47.24
2019-07-31 13:00 | 58.67 | 58.6
2019-07-31 13:30 | 75.84 | 75.73
2019-07-31 14:00 | 93.29 | 93.19
2019-07-31 14:30 | 97.95 | 97.88
2019-07-31 15:00 | 107.02 | 106.88
2019-07-31 15:30 | 111.08 | 110.94
2019-07-31 16:00 | 118.85 | 118.68
2019-07-31 16:30 | 134.63 | 134.46
2019-07-31 17:00 | 161.01 | 160.88
2019-07-31 17:30 | 189.45 | 189.25
2019-07-31 18:00 | 204.52 | 202.72
2019-07-31 18:30 | 206.65 | 204.58
2019-07-31 19:00 | 190.44 | 188.93
2019-07-31 19:30 | 166.38 | 164.97
2019-07-31 20:00 | 160.71 | 159.49
2019-07-31 20:30 | 177.2 | 176.45
2019-07-31 21:00 | 176.69 | 176.54
2019-07-31 21:30 | 155.87 | 155.43
2019-07-31 22:00 | 141.65 | 140.96
2019-07-31 22:30 | 122.95 | 121.93
2019-07-31 23:00 | 138.13 | 136.99
2019-07-31 23:30 | 124.84 | 123.87
2019-08-01 | 105.11 | 105.11
2019-08-01 00:30 | 85.83 | 85.7
2019-08-01 01:00 | 61.96 | 61.54
2019-08-01 01:30 | 52.4 | 51.75
2019-08-01 02:00 | 31.75 | 30.85
2019-08-01 02:30 | 46.07 | 45.23
2019-08-01 03:00 | 40.28 | 39.2
2019-08-01 03:30 | 39.09 | 38.21
2019-08-01 04:00 | 42.59 | 41.78
2019-08-01 04:30 | 48.36 | 47.92
2019-08-01 05:00 | 55.33 | 55.17
2019-08-01 05:30 | 79.93 | 79.92
2019-08-01 06:00 | 102.45 | 102.45
2019-08-01 06:30 | 90.74 | 90.71
2019-08-01 07:00 | 105.33 | 104.92
2019-08-01 07:30 | 152.05 | 151.96
2019-08-01 08:00 | 140.14 | 140.01
2019-08-01 08:30 | 137.05 | 137
2019-08-01 09:00 | 113.67 | 113.6
2019-08-01 09:30 | 91.49 | 91.35
2019-08-01 10:00 | 67.39 | 67.18
2019-08-01 10:30 | 51.93 | 51.36
2019-08-01 11:00 | 56.87 | 56.42
2019-08-01 11:30 | 67.19 | 66.9
2019-08-01 12:00 | 71.68 | 71.17
2019-08-01 12:30 | 79.25 | 78.88
2019-08-01 13:00 | 94.1 | 93.88
2019-08-01 13:30 | 97.73 | 97.39
2019-08-01 14:00 | 95.32 | 95.06
2019-08-01 14:30 | 92.17 | 91.78
2019-08-01 15:00 | 101.39 | 100.85
2019-08-01 15:30 | 98.48 | 97.71
2019-08-01 16:00 | 117.27 | 116.72
2019-08-01 16:30 | 127.74 | 127.12
2019-08-01 17:00 | 125.51 | 125.3
2019-08-01 17:30 | 108.67 | 107.89
2019-08-01 18:00 | 131.55 | 130.36
2019-08-01 18:30 | 150.44 | 149.14
2019-08-01 19:00 | 156.78 | 155.49
2019-08-01 19:30 | 139.3 | 137.92
2019-08-01 20:00 | 124.49 | 123.22
2019-08-01 20:30 | 123.99 | 122.87
2019-08-01 21:00 | 67.71 | 65.19
2019-08-01 21:30 | 77.04 | 75.22
2019-08-01 22:00 | 68.71 | 67.65
2019-08-01 22:30 | 71.02 | 70.19
2019-08-01 23:00 | 102.98 | 101.99
2019-08-01 23:30 | 88.93 | 87.32
2019-08-02 | 69.27 | 67.02
2019-08-02 00:30 | 64.81 | 61.95
2019-08-02 01:00 | 60.33 | 57.38
2019-08-02 01:30 | 50.12 | 46.06
2019-08-02 02:00 | 35.76 | 29.79
2019-08-02 02:30 | 36.63 | 33.64
2019-08-02 03:00 | 40.04 | 38.2
2019-08-02 03:30 | 49.03 | 47.46
2019-08-02 04:00 | 49.35 | 47.71
2019-08-02 04:30 | 54.58 | 52.62
2019-08-02 05:00 | 74.83 | 72.96
2019-08-02 05:30 | 92.84 | 90.91
2019-08-02 06:00 | 101.54 | 99.29
2019-08-02 06:30 | 102.92 | 101.66
2019-08-02 07:00 | 118.28 | 117.93
2019-08-02 07:30 | 145.68 | 145.67
2019-08-02 08:00 | 96.59 | 96.59
2019-08-02 08:30 | 22.1 | 7.12
2019-08-02 09:00 | 57.5 | 53.44
2019-08-02 09:30 | 33.5 | 26.93
2019-08-02 10:00 | 27.94 | 20
2019-08-02 10:30 | 21.99 | -5.9
2019-08-02 11:00 | 23.83 | 10.96
2019-08-02 11:30 | 29.17 | 21.1
2019-08-02 12:00 | 33.7 | 26.88
2019-08-02 12:30 | 46.31 | 42.01
2019-08-02 13:00 | 55.5 | 52.32
2019-08-02 13:30 | 67.45 | 64.97
2019-08-02 14:00 | 70.09 | 67.73
2019-08-02 14:30 | 91.27 | 89.57
2019-08-02 15:00 | 106.75 | 105.54
2019-08-02 15:30 | 121.12 | 120.24
2019-08-02 16:00 | 133.73 | 133.01
2019-08-02 16:30 | 128.97 | 128.26
2019-08-02 17:00 | 122.33 | 121.38
2019-08-02 17:30 | 121.17 | 119
2019-08-02 18:00 | 139.6 | 128.39
2019-08-02 18:30 | 135.52 | 124.4
2019-08-02 19:00 | 139.7 | 129.37
2019-08-02 19:30 | 125.44 | 114.62
2019-08-02 20:00 | 99.72 | 86.27
2019-08-02 20:30 | 70.21 | 50.64
2019-08-02 21:00 | 106.86 | 103.77
2019-08-02 21:30 | 100.71 | 98.32
2019-08-02 22:00 | 107.14 | 107
2019-08-02 22:30 | 102.56 | 101.5
2019-08-02 23:00 | 127.3 | 126.28
2019-08-02 23:30 | 118.39 | 117.21
2019-08-03 | 108.7 | 107.13
2019-08-03 00:30 | 103.59 | 101.47
2019-08-03 01:00 | 89.61 | 86.84
2019-08-03 01:30 | 81.32 | 78.98
2019-08-03 02:00 | 61.66 | 59.34
2019-08-03 02:30 | 59.16 | 56.69
2019-08-03 03:00 | 62.85 | 60.46
2019-08-03 03:30 | 62.47 | 60.11
2019-08-03 04:00 | 55.85 | 53.3
2019-08-03 04:30 | 42.37 | 38.37
2019-08-03 05:00 | 76.18 | 74
2019-08-03 05:30 | 92.83 | 90.61
2019-08-03 06:00 | 102.69 | 100.28
2019-08-03 06:30 | 103.05 | 100.97
2019-08-03 07:00 | 112.87 | 110.87
2019-08-03 07:30 | 96.58 | 95.06
2019-08-03 08:00 | 84.22 | 83.04
2019-08-03 08:30 | 66.75 | 65.37
2019-08-03 09:00 | 63.68 | 62.3
2019-08-03 09:30 | 62.71 | 61.28
2019-08-03 10:00 | 52.42 | 50.82
2019-08-03 10:30 | 32.54 | 29.7
2019-08-03 11:00 | 17.29 | 11.72
2019-08-03 11:30 | 19.12 | -18.16
2019-08-03 12:00 | 10.87 | -5.23
2019-08-03 12:30 | 15.11 | 11.18
2019-08-03 13:00 | 15.11 | 11.53
2019-08-03 13:30 | 24.56 | 22.37
2019-08-03 14:00 | 35.73 | 33.37
2019-08-03 14:30 | 46.63 | 44.74
2019-08-03 15:00 | 58.58 | 55.33
2019-08-03 15:30 | 74.76 | 72.19
2019-08-03 16:00 | 89.49 | 87.46
2019-08-03 16:30 | 92.68 | 90.97
2019-08-03 17:00 | 90.35 | 89.21
2019-08-03 17:30 | 83.43 | 82.81
2019-08-03 18:00 | 101.22 | 96.63
2019-08-03 18:30 | 111.64 | 107.46
2019-08-03 19:00 | 111.28 | 107.32
2019-08-03 19:30 | 102.84 | 98.98
2019-08-03 20:00 | 97.83 | 94.1
2019-08-03 20:30 | 90.64 | 86.96
2019-08-03 21:00 | 70.75 | 69.76
2019-08-03 21:30 | 74.74 | 74.05
2019-08-03 22:00 | 67.71 | 66.61
2019-08-03 22:30 | 80.47 | 79.3
2019-08-03 23:00 | 81.21 | 79.8
2019-08-03 23:30 | 71.41 | 69.46
2019-08-04 | 80.14 | 77.76
2019-08-04 00:30 | 88.37 | 85.57
2019-08-04 01:00 | 76.27 | 73.16
2019-08-04 01:30 | 55.59 | 53.34
2019-08-04 02:00 | 45.12 | 42.8
2019-08-04 02:30 | 57.5 | 55.67
2019-08-04 03:00 | 61.17 | 59.88
2019-08-04 03:30 | 56.81 | 55.55
2019-08-04 04:00 | 53.26 | 51.9
2019-08-04 04:30 | 48.47 | 46.86
2019-08-04 05:00 | 49.85 | 48.29
2019-08-04 05:30 | 54.91 | 52.81
2019-08-04 06:00 | 60 | 57.5
2019-08-04 06:30 | 70 | 67.6
2019-08-04 07:00 | 67.62 | 65.15
2019-08-04 07:30 | 68.37 | 65.79
2019-08-04 08:00 | 49.45 | 46.65
2019-08-04 08:30 | 45.96 | 44.4
2019-08-04 09:00 | 17.1 | 14.72
2019-08-04 09:30 | 5.75 | -3.33
2019-08-04 10:00 | 35 | -35
2019-08-04 10:30 | 41.27 | -41.27
2019-08-04 11:00 | 42.29 | -42.29
2019-08-04 11:30 | 21.34 | -20.33
2019-08-04 12:00 | 52.59 | -52.57
2019-08-04 12:30 | 54.56 | -54.56
2019-08-04 13:00 | 53.25 | -53.25
2019-08-04 13:30 | 20.65 | -19.33
2019-08-04 14:00 | 10.8 | -4.45
2019-08-04 14:30 | 15.38 | 10.81
2019-08-04 15:00 | 15.15 | -12.81
2019-08-04 15:30 | 11.94 | -10.31
2019-08-04 16:00 | 27.95 | 25.97
2019-08-04 16:30 | 47.77 | 46.01
2019-08-04 17:00 | 17.03 | 15.38
2019-08-04 17:30 | 12.59 | 12.53
2019-08-04 18:00 | 69.84 | 69.77
2019-08-04 18:30 | 68.38 | 68.05
2019-08-04 19:00 | 104.03 | 104.03
2019-08-04 19:30 | 33.88 | 33.48
2019-08-04 20:00 | 60.16 | 60.14
2019-08-04 20:30 | 72.22 | 72.16
2019-08-04 21:00 | 82.53 | 82.21
2019-08-04 21:30 | 76.55 | 75.87
2019-08-04 22:00 | 73.89 | 72.82
2019-08-04 22:30 | 91.27 | 89.82
2019-08-04 23:00 | 95.89 | 94.23
2019-08-04 23:30 | 79.58 | 77.3
2019-08-05 | 69.49 | 66.36
2019-08-05 00:30 | 55.21 | 52.15
2019-08-05 01:00 | 33.8 | 30.33
2019-08-05 01:30 | 19.45 | 14.3
2019-08-05 02:00 | 19.35 | 14.58
2019-08-05 02:30 | 19.61 | 15.41
2019-08-05 03:00 | 24.46 | 21.31
2019-08-05 03:30 | 30.03 | 27.52
2019-08-05 04:00 | 35.7 | 33.67
2019-08-05 04:30 | 43.01 | 40.57
2019-08-05 05:00 | 56.41 | 53.93
2019-08-05 05:30 | 73.72 | 71.21
2019-08-05 06:00 | 87.94 | 85.97
2019-08-05 06:30 | 95.81 | 94.8
2019-08-05 07:00 | 100.01 | 99.62
2019-08-05 07:30 | 115.4 | 115.4
2019-08-05 08:00 | 42.87 | 42.58
2019-08-05 08:30 | 12.14 | 5.06
2019-08-05 09:00 | 10.81 | -5.04
2019-08-05 09:30 | 26.83 | -25.04
2019-08-05 10:00 | 12.05 | -9.55
2019-08-05 10:30 | 23.72 | -22.91
2019-08-05 11:00 | 6.27 | 4.78
2019-08-05 11:30 | 11.4 | -10.43
2019-08-05 12:00 | 22.16 | -21.6
2019-08-05 12:30 | 40.38 | -39.93
2019-08-05 13:00 | 21.99 | -21.51
2019-08-05 13:30 | 2.6 | 0.93
2019-08-05 14:00 | 5.08 | 4.31
2019-08-05 14:30 | 22.7 | 22.64
2019-08-05 15:00 | 44.38 | 44.38
2019-08-05 15:30 | 58.56 | 58.53
2019-08-05 16:00 | 74.94 | 74.93
2019-08-05 16:30 | 82.3 | 82.29
2019-08-05 17:00 | 95.45 | 95.26
2019-08-05 17:30 | 94.49 | 94.35
2019-08-05 18:00 | 115.03 | 115.03
2019-08-05 18:30 | 126.15 | 126.14
2019-08-05 19:00 | 129.04 | 129.04
2019-08-05 19:30 | 119.07 | 119.07
2019-08-05 20:00 | 110.36 | 110.31
2019-08-05 20:30 | 115.73 | 115.68
2019-08-05 21:00 | 92.54 | 92.38
2019-08-05 21:30 | 83.12 | 82.32
2019-08-05 22:00 | 60.54 | 60.52
2019-08-05 22:30 | 61.96 | 59.91
2019-08-05 23:00 | 70.9 | 68.66
2019-08-05 23:30 | 51.11 | 48.85
2019-08-06 | 40.21 | 37.97
2019-08-06 00:30 | 63.35 | 62.1
2019-08-06 01:00 | 64.69 | 63.66
2019-08-06 01:30 | 50.97 | 49.91
2019-08-06 02:00 | 32.22 | 30.75
2019-08-06 02:30 | 30.59 | 30.58
2019-08-06 03:00 | 51.32 | 50.26
2019-08-06 03:30 | 66.34 | 65.68
2019-08-06 04:00 | 78.34 | 76.66
2019-08-06 04:30 | 90.29 | 86.85
2019-08-06 05:00 | 103.9 | 100.82
2019-08-06 05:30 | 116.74 | 114.06
2019-08-06 06:00 | 127.05 | 124.97
2019-08-06 06:30 | 97.87 | 97.86
2019-08-06 07:00 | 104.75 | 104.3
2019-08-06 07:30 | 117.36 | 117.12
2019-08-06 08:00 | 53.81 | 51.98
2019-08-06 08:30 | 23.32 | -7.31
2019-08-06 09:00 | 25.25 | -9.58
2019-08-06 09:30 | 20.81 | -5.84
2019-08-06 10:00 | 36.91 | -24.71
2019-08-06 10:30 | 35.46 | -30.82
2019-08-06 11:00 | 43.62 | -39.24
2019-08-06 11:30 | 31.55 | -26.7
2019-08-06 12:00 | 18.7 | -12.52
2019-08-06 12:30 | 12.98 | 0.36
2019-08-06 13:00 | 12.29 | 3.78
2019-08-06 13:30 | 17.56 | 13.19
2019-08-06 14:00 | 31.37 | 31.12
2019-08-06 14:30 | 41.79 | 41.78
2019-08-06 15:00 | 56.31 | 56.31
2019-08-06 15:30 | 86.1 | 86.1
2019-08-06 16:00 | 96 | 95.99
2019-08-06 16:30 | 104.08 | 104.07
2019-08-06 17:00 | 118.11 | 118.11
2019-08-06 17:30 | 113 | 112.9
2019-08-06 18:00 | 132.18 | 132.17
2019-08-06 18:30 | 132.58 | 132.58
2019-08-06 19:00 | 131.6 | 131.6
2019-08-06 19:30 | 112.05 | 112.03
2019-08-06 20:00 | 96.83 | 96.78
2019-08-06 20:30 | 70.68 | 70.67
2019-08-06 21:00 | 78.59 | 78.58
2019-08-06 21:30 | 57.4 | 57.38
2019-08-06 22:00 | 55.62 | 55.59
2019-08-06 22:30 | 87.82 | 87.34
2019-08-06 23:00 | 96.61 | 95.22
2019-08-06 23:30 | 66.17 | 64.86
2019-08-07 | 55.88 | 54.7
2019-08-07 00:30 | 60.59 | 59.62
2019-08-07 01:00 | 49.39 | 48.46
2019-08-07 01:30 | 39.5 | 38.61
2019-08-07 02:00 | 29.8 | 28.59
2019-08-07 02:30 | 31.33 | 31.11
2019-08-07 03:00 | 23.37 | 23.28
2019-08-07 03:30 | 33.08 | 26.82
2019-08-07 04:00 | 44.73 | 39.57
2019-08-07 04:30 | 61.81 | 58.11
2019-08-07 05:00 | 72.33 | 69.16
2019-08-07 05:30 | 95.68 | 93.75
2019-08-07 06:00 | 107.34 | 106.23
2019-08-07 06:30 | 93.66 | 93.35
2019-08-07 07:00 | 90.57 | 87.83
2019-08-07 07:30 | 92.57 | 86.57
2019-08-07 08:00 | 121.36 | 116.22
2019-08-07 08:30 | 101.87 | 94.99
2019-08-07 09:00 | 93.99 | 85.89
2019-08-07 09:30 | 123.66 | 117.98
2019-08-07 10:00 | 133.82 | 128.63
2019-08-07 10:30 | 111.95 | 111.39
2019-08-07 11:00 | 90.35 | 90.25
2019-08-07 11:30 | 63.13 | 63.04
2019-08-07 12:00 | 36.06 | 36.01
2019-08-07 12:30 | 63.7 | 63.66
2019-08-07 13:00 | 82.78 | 82.78
2019-08-07 13:30 | 80.11 | 80.11
2019-08-07 14:00 | 107.13 | 107.12
2019-08-07 14:30 | 117.2 | 117.19
2019-08-07 15:00 | 112.62 | 112.62
2019-08-07 15:30 | 126.79 | 126.79
2019-08-07 16:00 | 166.69 | 166.69
2019-08-07 16:30 | 155.53 | 153.84
2019-08-07 17:00 | 153.64 | 144.65
2019-08-07 17:30 | 155.04 | 144.98
2019-08-07 18:00 | 167.1 | 157.23
2019-08-07 18:30 | 165.15 | 155.8
2019-08-07 19:00 | 165.94 | 157.21
2019-08-07 19:30 | 162.03 | 154.13
2019-08-07 20:00 | 150.68 | 142.88
2019-08-07 20:30 | 138.51 | 131.91
2019-08-07 21:00 | 122.54 | 120.47
2019-08-07 21:30 | 112 | 111.38
2019-08-07 22:00 | 98.2 | 96.88
2019-08-07 22:30 | 96.69 | 95.05
2019-08-07 23:00 | 98.96 | 97.02
2019-08-07 23:30 | 89.19 | 87.07
2019-08-08 | 79.6 | 76.91
2019-08-08 00:30 | 78.49 | 75.44
2019-08-08 01:00 | 75.03 | 72.29
2019-08-08 01:30 | 58.89 | 54.42
2019-08-08 02:00 | 44.02 | 37.62
2019-08-08 02:30 | 41.79 | 35.14
2019-08-08 03:00 | 36.49 | 28.89
2019-08-08 03:30 | 33.26 | 23.57
2019-08-08 04:00 | 42.43 | 35.34
2019-08-08 04:30 | 62.28 | 57.29
2019-08-08 05:00 | 74.58 | 70.25
2019-08-08 05:30 | 96.41 | 93
2019-08-08 06:00 | 107.26 | 104.81
2019-08-08 06:30 | 104.59 | 103.35
2019-08-08 07:00 | 108.1 | 107.33
2019-08-08 07:30 | 121.28 | 121.17
2019-08-08 08:00 | 107.07 | 97.25
2019-08-08 08:30 | 96.61 | 84.98
2019-08-08 09:00 | 75.11 | 59.42
2019-08-08 09:30 | 55.38 | -24.86
2019-08-08 10:00 | 49.07 | -3.22
2019-08-08 10:30 | 51.78 | -15.07
2019-08-08 11:00 | 67.17 | -44.14
2019-08-08 11:30 | 41.02 | -35.45
2019-08-08 12:00 | 22.99 | 14.32
2019-08-08 12:30 | 30.13 | 24.66
2019-08-08 13:00 | 41.32 | 37.41
2019-08-08 13:30 | 47.07 | 43.63
2019-08-08 14:00 | 47.55 | 43.93
2019-08-08 14:30 | 54.66 | 51.18
2019-08-08 15:00 | 69.81 | 67.24
2019-08-08 15:30 | 91.39 | 89.45
2019-08-08 16:00 | 117.83 | 116.65
2019-08-08 16:30 | 116.92 | 114.55
2019-08-08 17:00 | 128.75 | 120.72
2019-08-08 17:30 | 139.79 | 131.94
2019-08-08 18:00 | 132.76 | 122.4
2019-08-08 18:30 | 145.48 | 135.47
2019-08-08 19:00 | 158.75 | 150.39
2019-08-08 19:30 | 161.58 | 154.25
2019-08-08 20:00 | 160.85 | 154.51
2019-08-08 20:30 | 142.32 | 139.23
2019-08-08 21:00 | 120.41 | 120.1
2019-08-08 21:30 | 109.39 | 109.2
2019-08-08 22:00 | 108.44 | 108.38
2019-08-08 22:30 | 112.74 | 112.72
2019-08-08 23:00 | 131.18 | 131.18
2019-08-08 23:30 | 112.64 | 112.61
2019-08-09 | 88.05 | 87.94
2019-08-09 00:30 | 78.22 | 75.22
2019-08-09 01:00 | 72.08 | 67.86
2019-08-09 01:30 | 66.18 | 61.87
2019-08-09 02:00 | 64.85 | 60.57
2019-08-09 02:30 | 56.16 | 51.12
2019-08-09 03:00 | 58.18 | 53.38
2019-08-09 03:30 | 68.13 | 64.11
2019-08-09 04:00 | 68.15 | 64.1
2019-08-09 04:30 | 69.93 | 65.65
2019-08-09 05:00 | 84.32 | 80.53
2019-08-09 05:30 | 114.86 | 112.33
2019-08-09 06:00 | 124.63 | 122.53
2019-08-09 06:30 | 130.63 | 129.32
2019-08-09 07:00 | 155.46 | 154.77
2019-08-09 07:30 | 163.48 | 163.45
2019-08-09 08:00 | 124.48 | 123.77
2019-08-09 08:30 | 87.2 | 86.07
2019-08-09 09:00 | 59.47 | 57.67
2019-08-09 09:30 | 19.21 | 7.54
2019-08-09 10:00 | 35.18 | 30.78
2019-08-09 10:30 | 31.7 | 26.56
2019-08-09 11:00 | 19.94 | 8.45
2019-08-09 11:30 | 26.78 | 20.17
2019-08-09 12:00 | 36.66 | -31.05
2019-08-09 12:30 | 52.58 | -48.71
2019-08-09 13:00 | 53.81 | -50.04
2019-08-09 13:30 | 47.07 | -42.67
2019-08-09 14:00 | 31.64 | -25.21
2019-08-09 14:30 | 37 | 32.88
2019-08-09 15:00 | 29.71 | 24.98
2019-08-09 15:30 | 50.39 | 48.17
2019-08-09 16:00 | 74.94 | 73.76
2019-08-09 16:30 | 78.02 | 76.91
2019-08-09 17:00 | 90.11 | 86.13
2019-08-09 17:30 | 71.31 | 54.49
2019-08-09 18:00 | 52.16 | 3.4
2019-08-09 18:30 | 57.21 | -13.78
2019-08-09 19:00 | 54.16 | 1.12
2019-08-09 19:30 | 76.78 | 60.77
2019-08-09 20:00 | 113.28 | 104.63
2019-08-09 20:30 | 65.69 | 49.82
2019-08-09 21:00 | 43.25 | 0.33
2019-08-09 21:30 | 41.59 | -7.37
2019-08-09 22:00 | 14.58 | -14.33
2019-08-09 22:30 | 15.61 | -13.31
2019-08-09 23:00 | 66.18 | 64.12
2019-08-09 23:30 | 70.59 | 67.88
2019-08-10 | 54.96 | 51.18
2019-08-10 00:30 | 47.74 | 41.99
2019-08-10 01:00 | 45.32 | 38.98
2019-08-10 01:30 | 42.17 | 35.93
2019-08-10 02:00 | 39.18 | 32.93
2019-08-10 02:30 | 34.87 | 27.88
2019-08-10 03:00 | 28.24 | 19.36
2019-08-10 03:30 | 29.2 | 20.71
2019-08-10 04:00 | 39.71 | 33.86
2019-08-10 04:30 | 51.99 | 45.36
2019-08-10 05:00 | 61.73 | 55.34
2019-08-10 05:30 | 75.28 | 70.46
2019-08-10 06:00 | 79.89 | 75.48
2019-08-10 06:30 | 69.45 | 64.49
2019-08-10 07:00 | 61.23 | 56.29
2019-08-10 07:30 | 59.29 | 55.34
2019-08-10 08:00 | 32.02 | 27.46
2019-08-10 08:30 | 29.91 | -28.54
2019-08-10 09:00 | 28.98 | -27.92
2019-08-10 09:30 | 40.59 | -40
2019-08-10 10:00 | 37.21 | -36.43
2019-08-10 10:30 | 37.63 | -36.81
2019-08-10 11:00 | 47.15 | -46.49
2019-08-10 11:30 | 49.9 | -49.29
2019-08-10 12:00 | 49.39 | -48.77
2019-08-10 12:30 | 54.01 | -53.41
2019-08-10 13:00 | 52.64 | -52.02
2019-08-10 13:30 | 52.53 | -51.87
2019-08-10 14:00 | 42.68 | -41.77
2019-08-10 14:30 | 36.54 | -35.33
2019-08-10 15:00 | 40.2 | -39.17
2019-08-10 15:30 | 29.41 | -28
2019-08-10 16:00 | 39.61 | -38.87
2019-08-10 16:30 | 26.04 | -24.96
2019-08-10 17:00 | 5.18 | -1.9
2019-08-10 17:30 | 47.02 | 46.68
2019-08-10 18:00 | 13.61 | 12.1
2019-08-10 18:30 | 80.51 | 75.3
2019-08-10 19:00 | 71.78 | 69.98
2019-08-10 19:30 | 46.25 | 45.62
2019-08-10 20:00 | 67.44 | 66.68
2019-08-10 20:30 | 20.92 | 20.91
2019-08-10 21:00 | 37.26 | 37.13
2019-08-10 21:30 | 17.41 | 15.24
2019-08-10 22:00 | 42.46 | 40.99
2019-08-10 22:30 | 92.89 | 91.79
2019-08-10 23:00 | 107.19 | 106.03
2019-08-10 23:30 | 84.54 | 83.31
2019-08-11 | 64.75 | 63.26
2019-08-11 00:30 | 78.4 | 76.54
2019-08-11 01:00 | 72.32 | 70.67
2019-08-11 01:30 | 60.51 | 58.85
2019-08-11 02:00 | 58.29 | 56.92
2019-08-11 02:30 | 49.71 | 48.37
2019-08-11 03:00 | 36.14 | 34.04
2019-08-11 03:30 | 45.99 | 44.18
2019-08-11 04:00 | 56.94 | 54.49
2019-08-11 04:30 | 56.63 | 53.46
2019-08-11 05:00 | 60.41 | 57.3
2019-08-11 05:30 | 70.5 | 68.08
2019-08-11 06:00 | 83.92 | 81.46
2019-08-11 06:30 | 83.44 | 80.71
2019-08-11 07:00 | 85.43 | 82.4
2019-08-11 07:30 | 79.26 | 76.09
2019-08-11 08:00 | 12.49 | -8
2019-08-11 08:30 | 43.24 | -42.94
2019-08-11 09:00 | 41.25 | -41.01
2019-08-11 09:30 | 39.72 | -39.51
2019-08-11 10:00 | 40.4 | -40.15
2019-08-11 10:30 | 34.77 | -34.4
2019-08-11 11:00 | 45.01 | -44.65
2019-08-11 11:30 | 48.8 | -48.36
2019-08-11 12:00 | 50.4 | -49.94
2019-08-11 12:30 | 52.35 | -51.91
2019-08-11 13:00 | 51.96 | -51.45
2019-08-11 13:30 | 51.31 | -50.79
2019-08-11 14:00 | 49.65 | -49.16
2019-08-11 14:30 | 44.1 | -43.48
2019-08-11 15:00 | 46.45 | -45.82
2019-08-11 15:30 | 35.98 | -35.21
2019-08-11 16:00 | 34.03 | -33.4
2019-08-11 16:30 | 20.34 | -19.52
2019-08-11 17:00 | 30.18 | 29.57
2019-08-11 17:30 | 92.62 | 92.56
2019-08-11 18:00 | 138.18 | 132.74
2019-08-11 18:30 | 149.19 | 139.08
2019-08-11 19:00 | 173.82 | 165.53
2019-08-11 19:30 | 169.34 | 161.41
2019-08-11 20:00 | 158.86 | 150.98
2019-08-11 20:30 | 142.99 | 139.09
2019-08-11 21:00 | 116.91 | 116.25
2019-08-11 21:30 | 108.71 | 108.32
2019-08-11 22:00 | 107.4 | 107.2
2019-08-11 22:30 | 126.28 | 126.21
2019-08-11 23:00 | 132.85 | 132.84
2019-08-11 23:30 | 133.04 | 131.5
2019-08-12 | 109.71 | 107.26
2019-08-12 00:30 | 99.41 | 96.61
2019-08-12 01:00 | 87.38 | 84.34
2019-08-12 01:30 | 72.57 | 70.32
2019-08-12 02:00 | 69.48 | 67.56
2019-08-12 02:30 | 55.1 | 52.75
2019-08-12 03:00 | 54.91 | 52.65
2019-08-12 03:30 | 62.89 | 60.85
2019-08-12 04:00 | 62.06 | 59.89
2019-08-12 04:30 | 68.14 | 65.68
2019-08-12 05:00 | 84.28 | 81.77
2019-08-12 05:30 | 108.42 | 106.14
2019-08-12 06:00 | 130.7 | 128.73
2019-08-12 06:30 | 123.95 | 122.72
2019-08-12 07:00 | 123.35 | 123.19
2019-08-12 07:30 | 127.33 | 121.88
2019-08-12 08:00 | 70.06 | 42.74
2019-08-12 08:30 | 75.36 | 50.68
2019-08-12 09:00 | 77.51 | 70.5
2019-08-12 09:30 | 34.06 | 1.06
2019-08-12 10:00 | 33.46 | 7.2
2019-08-12 10:30 | 28.89 | 22.5
2019-08-12 11:00 | 12.67 | 12.64
2019-08-12 11:30 | 12.58 | -12.58
2019-08-12 12:00 | 42.41 | -42.34
2019-08-12 12:30 | 39.17 | -39.14
2019-08-12 13:00 | 44.13 | -44.07
2019-08-12 13:30 | 19.1 | -19.04
2019-08-12 14:00 | 2.97 | 2.82
2019-08-12 14:30 | 7.86 | 7.79
2019-08-12 15:00 | 7.72 | 7.68
2019-08-12 15:30 | 30.33 | 30.25
2019-08-12 16:00 | 64.77 | 64.69
2019-08-12 16:30 | 97.74 | 97.66
2019-08-12 17:00 | 99.84 | 99.78
2019-08-12 17:30 | 120.18 | 111.47
2019-08-12 18:00 | 137.48 | 123.7
2019-08-12 18:30 | 154.28 | 141.38
2019-08-12 19:00 | 145.09 | 131.93
2019-08-12 19:30 | 127.69 | 114.17
2019-08-12 20:00 | 113.25 | 98.65
2019-08-12 20:30 | 67.49 | 37.79
2019-08-12 21:00 | 104.74 | 92.63
2019-08-12 21:30 | 103.85 | 101.25
2019-08-12 22:00 | 93.02 | 92.98
2019-08-12 22:30 | 97.7 | 96.09
2019-08-12 23:00 | 95.79 | 93.8
2019-08-12 23:30 | 62.75 | 60.86
2019-08-13 | 49.5 | 47.72
2019-08-13 00:30 | 64.98 | 63.71
2019-08-13 01:00 | 66.63 | 65.54
2019-08-13 01:30 | 67.27 | 66.56
2019-08-13 02:00 | 56.18 | 55.47
2019-08-13 02:30 | 53.96 | 52.77
2019-08-13 03:00 | 42.67 | 40.93
2019-08-13 03:30 | 40.78 | 38.76
2019-08-13 04:00 | 46.95 | 45.07
2019-08-13 04:30 | 77.47 | 75.95
2019-08-13 05:00 | 93.74 | 92.31
2019-08-13 05:30 | 120.25 | 118.96
2019-08-13 06:00 | 131.93 | 130.35
2019-08-13 06:30 | 121.19 | 120.15
2019-08-13 07:00 | 129.82 | 129.64
2019-08-13 07:30 | 119.31 | 114.24
2019-08-13 08:00 | 78.21 | 55.78
2019-08-13 08:30 | 85.09 | 75.37
2019-08-13 09:00 | 60.18 | 58.68
2019-08-13 09:30 | 34.14 | 29.65
2019-08-13 10:00 | 41.53 | 37.49
2019-08-13 10:30 | 40.72 | 37.41
2019-08-13 11:00 | 22.94 | -8.97
2019-08-13 11:30 | 30.5 | -19.6
2019-08-13 12:00 | 26.24 | -13.63
2019-08-13 12:30 | 22.99 | 11.5
2019-08-13 13:00 | 25.31 | 18.36
2019-08-13 13:30 | 26.49 | 20.04
2019-08-13 14:00 | 36.48 | 32.18
2019-08-13 14:30 | 40.84 | 37.08
2019-08-13 15:00 | 30.51 | 25.32
2019-08-13 15:30 | 41.69 | 38.25
2019-08-13 16:00 | 53.89 | 51.93
2019-08-13 16:30 | 80.99 | 79.76
2019-08-13 17:00 | 95.24 | 88.99
2019-08-13 17:30 | 70.63 | 63.56
2019-08-13 18:00 | 60.25 | 7.13
2019-08-13 18:30 | 135.25 | 122.04
2019-08-13 19:00 | 65.88 | 26.04
2019-08-13 19:30 | 60.09 | 8.3
2019-08-13 20:00 | 59.42 | 13.92
2019-08-13 20:30 | 59.37 | 22.89
2019-08-13 21:00 | 91.17 | 85.14
2019-08-13 21:30 | 89.68 | 86.68
2019-08-13 22:00 | 67.67 | 67.61
2019-08-13 22:30 | 65.9 | 64.46
2019-08-13 23:00 | 87.66 | 86.41
2019-08-13 23:30 | 65.13 | 63.08
2019-08-14 | 41.03 | 36.89
2019-08-14 00:30 | 33.31 | 28.12
2019-08-14 01:00 | 18.99 | 9.5
2019-08-14 01:30 | 15.46 | 3.47
2019-08-14 02:00 | 17.76 | 7.75
2019-08-14 02:30 | 20.37 | 11.42
2019-08-14 03:00 | 22.14 | 13.29
2019-08-14 03:30 | 21.85 | 9.47
2019-08-14 04:00 | 27.83 | 18.58
2019-08-14 04:30 | 37.63 | 31.58
2019-08-14 05:00 | 43.65 | 38.65
2019-08-14 05:30 | 63.54 | 60.82
2019-08-14 06:00 | 74.6 | 73.14
2019-08-14 06:30 | 68.51 | 67.76
2019-08-14 07:00 | 72.79 | 72.76
2019-08-14 07:30 | 57.94 | 19.11
2019-08-14 08:00 | 74.7 | 0.87
2019-08-14 08:30 | 60.04 | -3.11
2019-08-14 09:00 | 38.84 | -0.29
2019-08-14 09:30 | 6.91 | -1.62
2019-08-14 10:00 | 5.29 | -0.39
2019-08-14 10:30 | 32.69 | -32.06
2019-08-14 11:00 | 38.16 | -37.61
2019-08-14 11:30 | 34.78 | -34.42
2019-08-14 12:00 | 32.01 | -31.32
2019-08-14 12:30 | 29.59 | -26.3
2019-08-14 13:00 | 44 | -33.73
2019-08-14 13:30 | 40.4 | -29.23
2019-08-14 14:00 | 43.46 | -34.2
2019-08-14 14:30 | 32.29 | -20.93
2019-08-14 15:00 | 38.19 | -31.14
2019-08-14 15:30 | 29.87 | -21.96
2019-08-14 16:00 | 50.33 | 46.74
2019-08-14 16:30 | 71.69 | 69.25
2019-08-14 17:00 | 80.61 | 78.19
2019-08-14 17:30 | 93.36 | 91.04
2019-08-14 18:00 | 103.11 | 86.61
2019-08-14 18:30 | 112.8 | 96.4
2019-08-14 19:00 | 126.36 | 112.69
2019-08-14 19:30 | 106.46 | 90.8
2019-08-14 20:00 | 82.35 | 61.49
2019-08-14 20:30 | 68.63 | 42.5
2019-08-14 21:00 | 88.23 | 74.75
2019-08-14 21:30 | 105.96 | 103.47
2019-08-14 22:00 | 101.27 | 100.77
2019-08-14 22:30 | 93.11 | 92.16
2019-08-14 23:00 | 96.99 | 95.84
2019-08-14 23:30 | 97.82 | 96.55
2019-08-15 | 71.98 | 70.09
2019-08-15 00:30 | 79.34 | 77.41
2019-08-15 01:00 | 68.85 | 66
2019-08-15 01:30 | 56.91 | 54.76
2019-08-15 02:00 | 50.15 | 48.31
2019-08-15 02:30 | 56.55 | 54.94
2019-08-15 03:00 | 60.7 | 59.19
2019-08-15 03:30 | 69.51 | 68.2
2019-08-15 04:00 | 75.19 | 73.96
2019-08-15 04:30 | 83.65 | 82.45
2019-08-15 05:00 | 94.71 | 93.51
2019-08-15 05:30 | 133.69 | 132.74
2019-08-15 06:00 | 157.51 | 156.68
2019-08-15 06:30 | 151.94 | 151.33
2019-08-15 07:00 | 169.94 | 169.84
2019-08-15 07:30 | 159.96 | 159.95
2019-08-15 08:00 | 113 | 111.42
2019-08-15 08:30 | 94.8 | 92.72
2019-08-15 09:00 | 77.61 | 74.97
2019-08-15 09:30 | 59.2 | 54.56
2019-08-15 10:00 | 54.92 | 49.34
2019-08-15 10:30 | 43.82 | 35.51
2019-08-15 11:00 | 42.22 | 33.54
2019-08-15 11:30 | 38.15 | 28.64
2019-08-15 12:00 | 39.59 | 30.44
2019-08-15 12:30 | 40.91 | 31.99
2019-08-15 13:00 | 43.7 | 35.83
2019-08-15 13:30 | 51.59 | 44.95
2019-08-15 14:00 | 53.68 | 49.46
2019-08-15 14:30 | 48.04 | 43.84
2019-08-15 15:00 | 62.05 | 59.04
2019-08-15 15:30 | 85.94 | 84.3
2019-08-15 16:00 | 99.84 | 98.68
2019-08-15 16:30 | 118.11 | 117.07
2019-08-15 17:00 | 128.43 | 127.44
2019-08-15 17:30 | 143.23 | 142.24
2019-08-15 18:00 | 153.6 | 151.77
2019-08-15 18:30 | 164.46 | 162.4
2019-08-15 19:00 | 162.64 | 160.67
2019-08-15 19:30 | 135.94 | 134.09
2019-08-15 20:00 | 125.18 | 123.42
2019-08-15 20:30 | 103.63 | 101.82
2019-08-15 21:00 | 108.9 | 107.58
2019-08-15 21:30 | 112.37 | 111.68
2019-08-15 22:00 | 105.32 | 104.96
2019-08-15 22:30 | 100.17 | 100.01
2019-08-15 23:00 | 110.62 | 110.56
2019-08-15 23:30 | 91.08 | 91
2019-08-16 | 78.65 | 75.58
2019-08-16 00:30 | 93.64 | 90.98
2019-08-16 01:00 | 89.34 | 87.41
2019-08-16 01:30 | 82.05 | 80.55
2019-08-16 02:00 | 67.88 | 66.2
2019-08-16 02:30 | 47.21 | 44.83
2019-08-16 03:00 | 44.97 | 42.38
2019-08-16 03:30 | 55.11 | 52.81
2019-08-16 04:00 | 64.91 | 62.9
2019-08-16 04:30 | 78.17 | 76.18
2019-08-16 05:00 | 85.58 | 83.26
2019-08-16 05:30 | 116.91 | 114.84
2019-08-16 06:00 | 147.79 | 146.42
2019-08-16 06:30 | 134.06 | 133.17
2019-08-16 07:00 | 139.17 | 138.7
2019-08-16 07:30 | 152.99 | 152.89
2019-08-16 08:00 | 116.66 | 116.61
2019-08-16 08:30 | 88.08 | 88.06
2019-08-16 09:00 | 14.92 | 13.24
2019-08-16 09:30 | 42.5 | 42.48
2019-08-16 10:00 | 26.09 | 26.07
2019-08-16 10:30 | 34.59 | -34.08
2019-08-16 11:00 | 43.54 | -42.97
2019-08-16 11:30 | 46.35 | -45.7
2019-08-16 12:00 | 48.07 | -47.55
2019-08-16 12:30 | 34.35 | -33.89
2019-08-16 13:00 | 7.55 | 6.94
2019-08-16 13:30 | 23.76 | 23.63
2019-08-16 14:00 | 26.54 | 26.47
2019-08-16 14:30 | 39.63 | 39.6
2019-08-16 15:00 | 62.66 | 62.66
2019-08-16 15:30 | 78.9 | 78.89
2019-08-16 16:00 | 94.66 | 94.65
2019-08-16 16:30 | 107.32 | 107.28
2019-08-16 17:00 | 124.24 | 123.58
2019-08-16 17:30 | 128.29 | 127.31
2019-08-16 18:00 | 127.34 | 123.24
2019-08-16 18:30 | 129.1 | 118.85
2019-08-16 19:00 | 115.77 | 104.59
2019-08-16 19:30 | 114.6 | 104.12
2019-08-16 20:00 | 119.19 | 109.43
2019-08-16 20:30 | 123.9 | 115.29
2019-08-16 21:00 | 110.32 | 110.29
2019-08-16 21:30 | 96.95 | 96.33
2019-08-16 22:00 | 98.09 | 97.23
2019-08-16 22:30 | 94.08 | 92.91
2019-08-16 23:00 | 112.07 | 110.82
2019-08-16 23:30 | 104.85 | 103.45
2019-08-17 | 71.72 | 68.97
2019-08-17 00:30 | 61.9 | 58.29
2019-08-17 01:00 | 39.99 | 34.53
2019-08-17 01:30 | 29.23 | 22.4
2019-08-17 02:00 | 23.6 | 10.9
2019-08-17 02:30 | 29.76 | 20.9
2019-08-17 03:00 | 41.86 | 35.9
2019-08-17 03:30 | 34.71 | 27.57
2019-08-17 04:00 | 32.45 | 24.34
2019-08-17 04:30 | 42.01 | 35.9
2019-08-17 05:00 | 44 | 37.94
2019-08-17 05:30 | 63.53 | 59.1
2019-08-17 06:00 | 64.13 | 59.93
2019-08-17 06:30 | 74.11 | 70.55
2019-08-17 07:00 | 94.66 | 92.17
2019-08-17 07:30 | 83.08 | 80.83
2019-08-17 08:00 | 59.83 | 57.84
2019-08-17 08:30 | 49.75 | 48.15
2019-08-17 09:00 | 39.16 | 37.63
2019-08-17 09:30 | 11.95 | 9.75
2019-08-17 10:00 | 39.06 | -39.01
2019-08-17 10:30 | 4.08 | -0.18
2019-08-17 11:00 | 30.6 | -30.49
2019-08-17 11:30 | 47.16 | -47.15
2019-08-17 12:00 | 48.24 | -48.23
2019-08-17 12:30 | 49.24 | -49.23
2019-08-17 13:00 | 38.4 | -38.35
2019-08-17 13:30 | 50.35 | -50.33
2019-08-17 14:00 | 20.99 | -20.77
2019-08-17 14:30 | 12.76 | -12.36
2019-08-17 15:00 | 11.29 | 10.45
2019-08-17 15:30 | 20.24 | -20.09
2019-08-17 16:00 | 19.69 | 19.34
2019-08-17 16:30 | 38.8 | 38.53
2019-08-17 17:00 | 59.17 | 58.96
2019-08-17 17:30 | 85.13 | 85
2019-08-17 18:00 | 96.16 | 95.44
2019-08-17 18:30 | 100.06 | 98.46
2019-08-17 19:00 | 106.83 | 105.63
2019-08-17 19:30 | 103.39 | 102.57
2019-08-17 20:00 | 135.78 | 135.42
2019-08-17 20:30 | 136.96 | 136.71
2019-08-17 21:00 | 128.34 | 128.16
2019-08-17 21:30 | 131.28 | 131.18
2019-08-17 22:00 | 128.6 | 128.58
2019-08-17 22:30 | 155.05 | 155.04
2019-08-17 23:00 | 160.36 | 160.36
2019-08-17 23:30 | 133.18 | 133.17
2019-08-18 | 100.58 | 100.23
2019-08-18 00:30 | 96.62 | 93.53
2019-08-18 01:00 | 86 | 82.89
2019-08-18 01:30 | 71.22 | 67.38
2019-08-18 02:00 | 72.65 | 68.96
2019-08-18 02:30 | 73.17 | 69.48
2019-08-18 03:00 | 79.55 | 76.22
2019-08-18 03:30 | 89.98 | 86.5
2019-08-18 04:00 | 93.17 | 89.54
2019-08-18 04:30 | 91.56 | 87.87
2019-08-18 05:00 | 88.17 | 84.19
2019-08-18 05:30 | 91.24 | 87.48
2019-08-18 06:00 | 93.72 | 90.02
2019-08-18 06:30 | 75.65 | 71.15
2019-08-18 07:00 | 77.67 | 73.59
2019-08-18 07:30 | 59.9 | 55.15
2019-08-18 08:00 | 36.47 | 30.7
2019-08-18 08:30 | 19.56 | 11.77
2019-08-18 09:00 | 39.97 | -39.09
2019-08-18 09:30 | 43.51 | -43.06
2019-08-18 10:00 | 36.75 | -36.22
2019-08-18 10:30 | 9.45 | 4.11
2019-08-18 11:00 | 11.14 | 5.8
2019-08-18 11:30 | 10.19 | 2.62
2019-08-18 12:00 | 46.5 | -45.99
2019-08-18 12:30 | 35.68 | -34.86
2019-08-18 13:00 | 11.58 | 2.09
2019-08-18 13:30 | 12.12 | 3.35
2019-08-18 14:00 | 12.66 | 4.74
2019-08-18 14:30 | 11.77 | -5.41
2019-08-18 15:00 | 11.02 | -4.68
2019-08-18 15:30 | 36.55 | -36.03
2019-08-18 16:00 | 27.54 | 25.58
2019-08-18 16:30 | 84.03 | 82.97
2019-08-18 17:00 | 107.21 | 106.49
2019-08-18 17:30 | 137.58 | 137.06
2019-08-18 18:00 | 173.65 | 173.61
2019-08-18 18:30 | 194.42 | 193.86
2019-08-18 19:00 | 204.57 | 204.1
2019-08-18 19:30 | 187.22 | 186.92
2019-08-18 20:00 | 174.06 | 173.82
2019-08-18 20:30 | 171.72 | 171.56
2019-08-18 21:00 | 164.59 | 164.49
2019-08-18 21:30 | 153.84 | 153.82
2019-08-18 22:00 | 156.96 | 156.96
2019-08-18 22:30 | 157.67 | 157.66
2019-08-18 23:00 | 157.89 | 157.86
2019-08-18 23:30 | 151.49 | 151.43
2019-08-19 | 126.02 | 125.88
2019-08-19 00:30 | 122.58 | 121.55
2019-08-19 01:00 | 89.89 | 86.27
2019-08-19 01:30 | 86.47 | 83.52
2019-08-19 02:00 | 74.67 | 71.43
2019-08-19 02:30 | 69.74 | 66.36
2019-08-19 03:00 | 66.14 | 63.62
2019-08-19 03:30 | 68.26 | 66.94
2019-08-19 04:00 | 71.92 | 70.56
2019-08-19 04:30 | 84.37 | 82.99
2019-08-19 05:00 | 95.91 | 94.58
2019-08-19 05:30 | 116.88 | 115.59
2019-08-19 06:00 | 136.73 | 135.59
2019-08-19 06:30 | 139.74 | 139.11
2019-08-19 07:00 | 141.29 | 140.9
2019-08-19 07:30 | 138.19 | 138.03
2019-08-19 08:00 | 124.8 | 124.75
2019-08-19 08:30 | 106.31 | 106.29
2019-08-19 09:00 | 70.32 | 70.32
2019-08-19 09:30 | 43.46 | 43.46
2019-08-19 10:00 | 36.64 | -26.92
2019-08-19 10:30 | 45.36 | -36.54
2019-08-19 11:00 | 39.86 | -29.6
2019-08-19 11:30 | 47.68 | -39.16
2019-08-19 12:00 | 52.6 | -44.9
2019-08-19 12:30 | 49.63 | -41.56
2019-08-19 13:00 | 50.74 | -42.56
2019-08-19 13:30 | 42.28 | -31.73
2019-08-19 14:00 | 42.98 | -31.88
2019-08-19 14:30 | 34.99 | -19.77
2019-08-19 15:00 | 29.68 | 12.09
2019-08-19 15:30 | 57.94 | 50.62
2019-08-19 16:00 | 71.62 | 66.51
2019-08-19 16:30 | 105.07 | 102.3
2019-08-19 17:00 | 113.59 | 111.78
2019-08-19 17:30 | 113.28 | 111.64
2019-08-19 18:00 | 120.76 | 117.65
2019-08-19 18:30 | 146.84 | 134.58
2019-08-19 19:00 | 97.1 | 66.48
2019-08-19 19:30 | 74.11 | 24.85
2019-08-19 20:00 | 82.69 | 55.78
2019-08-19 20:30 | 50.15 | 15.56
2019-08-19 21:00 | 57.59 | 37.52
2019-08-19 21:30 | 94.73 | 94.71
2019-08-19 22:00 | 89.27 | 88.11
2019-08-19 22:30 | 87.71 | 86.27
2019-08-19 23:00 | 94.23 | 92.56
2019-08-19 23:30 | 77.02 | 74.73
2019-08-20 | 61.34 | 58.1
2019-08-20 00:30 | 49.71 | 45.78
2019-08-20 01:00 | 41.16 | 36.99
2019-08-20 01:30 | 36.98 | 32.23
2019-08-20 02:00 | 41.21 | 36.84
2019-08-20 02:30 | 84.66 | 82.21
2019-08-20 03:00 | 82.4 | 79.86
2019-08-20 03:30 | 77.41 | 74.47
2019-08-20 04:00 | 81.99 | 79.01
2019-08-20 04:30 | 103.95 | 101.51
2019-08-20 05:00 | 111.06 | 108.85
2019-08-20 05:30 | 131.98 | 130.15
2019-08-20 06:00 | 146.85 | 145.61
2019-08-20 06:30 | 150.58 | 149.79
2019-08-20 07:00 | 163.48 | 163.14
2019-08-20 07:30 | 152.5 | 152
2019-08-20 08:00 | 124.25 | 122.66
2019-08-20 08:30 | 84.17 | 81.57
2019-08-20 09:00 | 67.85 | 64.43
2019-08-20 09:30 | 56.65 | 52.37
2019-08-20 10:00 | 51.33 | 46.91
2019-08-20 10:30 | 39.49 | 33.46
2019-08-20 11:00 | 38.67 | 32.69
2019-08-20 11:30 | 33.73 | 29.12
2019-08-20 12:00 | 34.34 | 29.81
2019-08-20 12:30 | 33.35 | 28.86
2019-08-20 13:00 | 35.04 | 31.09
2019-08-20 13:30 | 38.64 | 34.94
2019-08-20 14:00 | 39.04 | 35.62
2019-08-20 14:30 | 39.87 | 36.67
2019-08-20 15:00 | 43.99 | 39.51
2019-08-20 15:30 | 44.84 | 40.86
2019-08-20 16:00 | 52.21 | 49.06
2019-08-20 16:30 | 82.6 | 80.88
2019-08-20 17:00 | 121.82 | 120.62
2019-08-20 17:30 | 134.4 | 130.36
2019-08-20 18:00 | 166.67 | 156.92
2019-08-20 18:30 | 164.52 | 153.7
2019-08-20 19:00 | 174.94 | 165.12
2019-08-20 19:30 | 188.34 | 179.95
2019-08-20 20:00 | 181.98 | 173.85
2019-08-20 20:30 | 188.66 | 181.48
2019-08-20 21:00 | 169.82 | 166.5
2019-08-20 21:30 | 173.89 | 173.77
2019-08-20 22:00 | 171.26 | 171.08
2019-08-20 22:30 | 181.3 | 181.13
2019-08-20 23:00 | 175.51 | 175.28
2019-08-20 23:30 | 165.9 | 165.5
2019-08-21 | 133.21 | 132.96
2019-08-21 00:30 | 127.3 | 127.26
2019-08-21 01:00 | 113.85 | 113.85
2019-08-21 01:30 | 89.86 | 89.86
2019-08-21 02:00 | 88.91 | 88.91
2019-08-21 02:30 | 89.05 | 89.05
2019-08-21 03:00 | 86.9 | 86.9
2019-08-21 03:30 | 88.81 | 88.81
2019-08-21 04:00 | 91.93 | 91.91
2019-08-21 04:30 | 106.85 | 106.81
2019-08-21 05:00 | 122.76 | 122.67
2019-08-21 05:30 | 140.54 | 140.44
2019-08-21 06:00 | 153.25 | 153.24
2019-08-21 06:30 | 181.47 | 181.47
2019-08-21 07:00 | 177.16 | 177.16
2019-08-21 07:30 | 183.24 | 183.14
2019-08-21 08:00 | 162.21 | 162.08
2019-08-21 08:30 | 119.34 | 119.21
2019-08-21 09:00 | 80.01 | 79.88
2019-08-21 09:30 | 54.07 | 53.74
2019-08-21 10:00 | 42.14 | 42.02
2019-08-21 10:30 | 27.11 | 27.11
2019-08-21 11:00 | 25.25 | 25.25
2019-08-21 11:30 | 21.63 | 21.63
2019-08-21 12:00 | 20.68 | 20.68
2019-08-21 12:30 | 22.51 | 22.51
2019-08-21 13:00 | 25.4 | 25.39
2019-08-21 13:30 | 24.8 | 24.79
2019-08-21 14:00 | 14.87 | 14.86
2019-08-21 14:30 | 20.36 | 20.35
2019-08-21 15:00 | 35.33 | 35.29
2019-08-21 15:30 | 60.76 | 60.57
2019-08-21 16:00 | 82.54 | 82.46
2019-08-21 16:30 | 110.89 | 110.86
2019-08-21 17:00 | 138.45 | 138.43
2019-08-21 17:30 | 159.07 | 158.99
2019-08-21 18:00 | 193.31 | 193.01
2019-08-21 18:30 | 175.17 | 174.7
2019-08-21 19:00 | 181.24 | 180.65
2019-08-21 19:30 | 177.31 | 176.57
2019-08-21 20:00 | 175.97 | 175.11
2019-08-21 20:30 | 175.62 | 175.1
2019-08-21 21:00 | 163.4 | 163.26
2019-08-21 21:30 | 159.5 | 159.46
2019-08-21 22:00 | 156.87 | 156.77
2019-08-21 22:30 | 154.87 | 154.71
2019-08-21 23:00 | 167.6 | 167.44
2019-08-21 23:30 | 145.17 | 144.84
2019-08-22 | 105.73 | 105.06
2019-08-22 00:30 | 98.29 | 98.25
2019-08-22 01:00 | 88.02 | 88.01
2019-08-22 01:30 | 71.53 | 71.52
2019-08-22 02:00 | 68.3 | 68.29
2019-08-22 02:30 | 70.47 | 70.46
2019-08-22 03:00 | 71.78 | 71.76
2019-08-22 03:30 | 72.95 | 72.88
2019-08-22 04:00 | 76.7 | 76.64
2019-08-22 04:30 | 80.51 | 80.46
2019-08-22 05:00 | 99.28 | 99.24
2019-08-22 05:30 | 131.56 | 131.56
2019-08-22 06:00 | 142.62 | 142.61
2019-08-22 06:30 | 165.08 | 165.03
2019-08-22 07:00 | 187.06 | 187
2019-08-22 07:30 | 181.59 | 181.42
2019-08-22 08:00 | 151.36 | 151.22
2019-08-22 08:30 | 117.1 | 116.94
2019-08-22 09:00 | 97.41 | 97.27
2019-08-22 09:30 | 49.19 | 48.62
2019-08-22 10:00 | 44.4 | 43.83
2019-08-22 10:30 | 33.84 | 33.14
2019-08-22 11:00 | 31.74 | 31.12
2019-08-22 11:30 | 29.31 | 28.61
2019-08-22 12:00 | 30.55 | 29.86
2019-08-22 12:30 | 29.58 | 28.98
2019-08-22 13:00 | 32.43 | 31.88
2019-08-22 13:30 | 35.66 | 35.11
2019-08-22 14:00 | 17.47 | 17.41
2019-08-22 14:30 | 14.16 | -10.24
2019-08-22 15:00 | 49.63 | 49.47
2019-08-22 15:30 | 68.3 | 68.26
2019-08-22 16:00 | 91.72 | 91.72
2019-08-22 16:30 | 115.5 | 115.5
2019-08-22 17:00 | 133 | 133
2019-08-22 17:30 | 117.82 | 117.81
2019-08-22 18:00 | 61.23 | 56.61
2019-08-22 18:30 | 73.49 | 40.32
2019-08-22 19:00 | 67.09 | 31.86
2019-08-22 19:30 | 58.71 | 45.51
2019-08-22 20:00 | 104.96 | 100.23
2019-08-22 20:30 | 56.89 | 54.96
2019-08-22 21:00 | 73.04 | 72.91
2019-08-22 21:30 | 71.61 | 71.2
2019-08-22 22:00 | 92.67 | 91.89
2019-08-22 22:30 | 85.02 | 84.06
2019-08-22 23:00 | 95.68 | 94.54
2019-08-22 23:30 | 58.62 | 57.11
2019-08-23 | 45.71 | 43.27
2019-08-23 00:30 | 39.49 | 38.63
2019-08-23 01:00 | 22.79 | 21.47
2019-08-23 01:30 | 7.46 | 3.95
2019-08-23 02:00 | 7.02 | -4.06
2019-08-23 02:30 | 14.19 | 11.96
2019-08-23 03:00 | 19.43 | 17.95
2019-08-23 03:30 | 23.27 | 22.17
2019-08-23 04:00 | 20.31 | 18.83
2019-08-23 04:30 | 17.79 | 16.28
2019-08-23 05:00 | 25.9 | 24.43
2019-08-23 05:30 | 52.17 | 51.08
2019-08-23 06:00 | 81.71 | 80.8
2019-08-23 06:30 | 62.71 | 61.21
2019-08-23 07:00 | 60.76 | 59.78
2019-08-23 07:30 | 32.34 | 32.31
2019-08-23 08:00 | 24.57 | -7.31
2019-08-23 08:30 | 22.03 | -11.05
2019-08-23 09:00 | 18.34 | -11.43
2019-08-23 09:30 | 29.65 | -27.42
2019-08-23 10:00 | 20.8 | -18.31
2019-08-23 10:30 | 44.13 | -43.3
2019-08-23 11:00 | 48.64 | -48.35
2019-08-23 11:30 | 47.67 | -47.36
2019-08-23 12:00 | 43.35 | -43.03
2019-08-23 12:30 | 51.95 | -51.75
2019-08-23 13:00 | 47.91 | -47.79
2019-08-23 13:30 | 27.07 | -27.02
2019-08-23 14:00 | 17.72 | -17.71
2019-08-23 14:30 | 32.87 | -32.82
2019-08-23 15:00 | 34.95 | -34.93
2019-08-23 15:30 | 27.95 | -27.95
2019-08-23 16:00 | 18.89 | -18.89
2019-08-23 16:30 | 42.52 | 42.36
2019-08-23 17:00 | 27.82 | 27.72
2019-08-23 17:30 | 3.81 | 3.46
2019-08-23 18:00 | 37.13 | 26.29
2019-08-23 18:30 | 102.47 | 96.49
2019-08-23 19:00 | 102.04 | 97.17
2019-08-23 19:30 | 79.34 | 73.56
2019-08-23 20:00 | 92.62 | 92.6
2019-08-23 20:30 | 68.43 | 68.27
2019-08-23 21:00 | 73.57 | 73.38
2019-08-23 21:30 | 71.82 | 71.26
2019-08-23 22:00 | 51.78 | 50.55
2019-08-23 22:30 | 75.02 | 73.54
2019-08-23 23:00 | 94.88 | 93.23
2019-08-23 23:30 | 88.98 | 87.3
2019-08-24 | 67.61 | 64.2
2019-08-24 00:30 | 20.51 | 8.82
2019-08-24 01:00 | 34.9 | 31.74
2019-08-24 01:30 | 37.74 | 35.02
2019-08-24 02:00 | 45.09 | 42.94
2019-08-24 02:30 | 46.12 | 44.18
2019-08-24 03:00 | 42.2 | 41.89
2019-08-24 03:30 | 32.59 | 31.57
2019-08-24 04:00 | 40.84 | 39.97
2019-08-24 04:30 | 44.11 | 43.46
2019-08-24 05:00 | 45.15 | 44.74
2019-08-24 05:30 | 53.67 | 53.52
2019-08-24 06:00 | 66.72 | 66.7
2019-08-24 06:30 | 69.42 | 69.42
2019-08-24 07:00 | 65.44 | 65.43
2019-08-24 07:30 | 54.77 | 54.67
2019-08-24 08:00 | 19.46 | 16.51
2019-08-24 08:30 | 12.52 | -11.48
2019-08-24 09:00 | 12.28 | 11.42
2019-08-24 09:30 | 20.62 | 18.25
2019-08-24 10:00 | 16.68 | 12.73
2019-08-24 10:30 | 15.14 | -12.32
2019-08-24 11:00 | 10.83 | -3.93
2019-08-24 11:30 | 44.71 | -44.18
2019-08-24 12:00 | 17.13 | -14.93
2019-08-24 12:30 | 47.91 | 44.92
2019-08-24 13:00 | 30.1 | -26.58
2019-08-24 13:30 | 70.17 | -70.14
2019-08-24 14:00 | 69.63 | -69.63
2019-08-24 14:30 | 59.29 | -59.29
2019-08-24 15:00 | 12.69 | 7.22
2019-08-24 15:30 | 9.32 | -6.24
2019-08-24 16:00 | 28.82 | 26.77
2019-08-24 16:30 | 41.16 | 39.63
2019-08-24 17:00 | 75.37 | 74.48
2019-08-24 17:30 | 126.38 | 125.86
2019-08-24 18:00 | 162.23 | 162.13
2019-08-24 18:30 | 184.97 | 184.92
2019-08-24 19:00 | 195.36 | 195.31
2019-08-24 19:30 | 181.24 | 181.12
2019-08-24 20:00 | 172.56 | 172.31
2019-08-24 20:30 | 166.04 | 165.64
2019-08-24 21:00 | 161.13 | 160.62
2019-08-24 21:30 | 148.6 | 147.97
2019-08-24 22:00 | 124.76 | 123.94
2019-08-24 22:30 | 119.57 | 118.79
2019-08-24 23:00 | 111.82 | 110.77
2019-08-24 23:30 | 81.42 | 80.23
2019-08-25 | 48.93 | 47.07
2019-08-25 00:30 | 36.87 | 34.25
2019-08-25 01:00 | 20.49 | 14.99
2019-08-25 01:30 | 10.33 | -8.4
2019-08-25 02:00 | 10.35 | 7.89
2019-08-25 02:30 | 10.78 | 8.22
2019-08-25 03:00 | 17.93 | 14.15
2019-08-25 03:30 | 20.75 | 17.43
2019-08-25 04:00 | 15.65 | 10.64
2019-08-25 04:30 | 20.57 | 17.62
2019-08-25 05:00 | 29.11 | 27.36
2019-08-25 05:30 | 34.58 | 33.68
2019-08-25 06:00 | 39.75 | 39.15
2019-08-25 06:30 | 26.25 | 24.79
2019-08-25 07:00 | 29.75 | 28.88
2019-08-25 07:30 | 23.55 | 22.9
2019-08-25 08:00 | 40.14 | -33.52
2019-08-25 08:30 | 56.79 | -48.84
2019-08-25 09:00 | 39.57 | -39.57
2019-08-25 09:30 | 44.65 | -44.35
2019-08-25 10:00 | 19.54 | -17.82
2019-08-25 10:30 | 28.6 | -27.53
2019-08-25 11:00 | 50.16 | -49.81
2019-08-25 11:30 | 53.06 | -52.74
2019-08-25 12:00 | 55.9 | -55.67
2019-08-25 12:30 | 58.82 | -58.55
2019-08-25 13:00 | 57.67 | -57.43
2019-08-25 13:30 | 49.02 | -48.73
2019-08-25 14:00 | 49.72 | -49.48
2019-08-25 14:30 | 28.7 | -27.65
2019-08-25 15:00 | 36.41 | -35.63
2019-08-25 15:30 | 49.41 | -48.99
2019-08-25 16:00 | 12.36 | -10.74
2019-08-25 16:30 | 22.47 | 20.9
2019-08-25 17:00 | 9.38 | -9.38
2019-08-25 17:30 | 22.99 | -15.64
2019-08-25 18:00 | 29.75 | -3.22
2019-08-25 18:30 | 54.66 | 6.02
2019-08-25 19:00 | 52.19 | -11.69
2019-08-25 19:30 | 27.09 | -16.52
2019-08-25 20:00 | 25.42 | -15.61
2019-08-25 20:30 | 24.09 | -15.92
2019-08-25 21:00 | 26.84 | -21.3
2019-08-25 21:30 | 20.54 | -16.55
2019-08-25 22:00 | 12.69 | -11.29
2019-08-25 22:30 | 42.61 | 42.52
2019-08-25 23:00 | 44.2 | 44.19
2019-08-25 23:30 | 24.68 | 24.68
2019-08-26 | 13.76 | -6.6
2019-08-26 00:30 | 16.98 | 2.38
2019-08-26 01:00 | 46.02 | -44.67
2019-08-26 01:30 | 50.29 | -49.04
2019-08-26 02:00 | 22.57 | -16.63
2019-08-26 02:30 | 33.87 | -30.7
2019-08-26 03:00 | 58.41 | -57.52
2019-08-26 03:30 | 54.98 | -53.91
2019-08-26 04:00 | 55.11 | -54.08
2019-08-26 04:30 | 36.19 | -33.07
2019-08-26 05:00 | 18.46 | -0.83
2019-08-26 05:30 | 26.4 | 17.1
2019-08-26 06:00 | 39.48 | 34.45
2019-08-26 06:30 | 23.41 | 18.37
2019-08-26 07:00 | 17.13 | 16.08
2019-08-26 07:30 | 25.31 | -17.87
2019-08-26 08:00 | 46.23 | -41.34
2019-08-26 08:30 | 51.55 | -46.51
2019-08-26 09:00 | 55.3 | -50.34
2019-08-26 09:30 | 59.85 | -54.95
2019-08-26 10:00 | 64.39 | -59.72
2019-08-26 10:30 | 73.14 | -68.78
2019-08-26 11:00 | 73.52 | -69.02
2019-08-26 11:30 | 76.1 | -71.61
2019-08-26 12:00 | 73.22 | -68.5
2019-08-26 12:30 | 69.51 | -64.34
2019-08-26 13:00 | 59.79 | -53.95
2019-08-26 13:30 | 50.76 | -43.2
2019-08-26 14:00 | 48.76 | -41.4
2019-08-26 14:30 | 29.65 | -18.89
2019-08-26 15:00 | 33.72 | -25.82
2019-08-26 15:30 | 35.17 | 30.36
2019-08-26 16:00 | 39.63 | 36.29
2019-08-26 16:30 | 17.51 | 3.52
2019-08-26 17:00 | 46.96 | -20.69
2019-08-26 17:30 | 66.73 | -41.16
2019-08-26 18:00 | 55.14 | -0.42
2019-08-26 18:30 | 58.39 | 19.21
2019-08-26 19:00 | 57.9 | -16.94
2019-08-26 19:30 | 63.13 | -31.61
2019-08-26 20:00 | 61.04 | -29.66
2019-08-26 20:30 | 25.9 | -10.63
2019-08-26 21:00 | 25.69 | -20.81
2019-08-26 21:30 | 44.71 | -42.79
2019-08-26 22:00 | 52.01 | -50.94
2019-08-26 22:30 | 40.25 | -39.42
2019-08-26 23:00 | 33.1 | 33.05
2019-08-26 23:30 | 20.49 | -20.46
2019-08-27 | 66.57 | -66.5
2019-08-27 00:30 | 22.3 | -18.1
2019-08-27 01:00 | 28.16 | -23.17
2019-08-27 01:30 | 20.74 | -12.91
2019-08-27 02:00 | 72.77 | -72.12
2019-08-27 02:30 | 75.16 | -74.56
2019-08-27 03:00 | 70.88 | -70.16
2019-08-27 03:30 | 51.63 | -49.93
2019-08-27 04:00 | 48.56 | -46.36
2019-08-27 04:30 | 28.8 | -23
2019-08-27 05:00 | 23.62 | -15.69
2019-08-27 05:30 | 43.33 | -40.71
2019-08-27 06:00 | 18.84 | -9.86
2019-08-27 06:30 | 22.12 | 15.88
2019-08-27 07:00 | 14.79 | 9.81
2019-08-27 07:30 | 21.26 | -14.73
2019-08-27 08:00 | 52.75 | -34.89
2019-08-27 08:30 | 31.71 | -11.62
2019-08-27 09:00 | 57.07 | 57.06
2019-08-27 09:30 | 55.51 | 52.92
2019-08-27 10:00 | 56.77 | 55.1
2019-08-27 10:30 | 23.19 | 19.03
2019-08-27 11:00 | 22.84 | -22.64
2019-08-27 11:30 | 66.45 | -66.29
2019-08-27 12:00 | 64.23 | -63.89
2019-08-27 12:30 | 63.62 | -58.22
2019-08-27 13:00 | 63.13 | -57.25
2019-08-27 13:30 | 43.21 | -33.04
2019-08-27 14:00 | 35.27 | 20.53
2019-08-27 14:30 | 68.65 | 65.93
2019-08-27 15:00 | 65.01 | 62.27
2019-08-27 15:30 | 57.08 | 54.15
2019-08-27 16:00 | 67.48 | 65.62
2019-08-27 16:30 | 59.91 | 58.13
2019-08-27 17:00 | 51.27 | 48.96
2019-08-27 17:30 | 58.61 | 56.54
2019-08-27 18:00 | 107.89 | 105.82
2019-08-27 18:30 | 134.63 | 124.18
2019-08-27 19:00 | 125.84 | 118.51
2019-08-27 19:30 | 49.57 | 39.52
2019-08-27 20:00 | 32.56 | -10.76
2019-08-27 20:30 | 31.81 | -13.55
2019-08-27 21:00 | 37.4 | -25.61
2019-08-27 21:30 | 25.73 | 24.41
2019-08-27 22:00 | 44.21 | 41.73
2019-08-27 22:30 | 13.9 | 4.76
2019-08-27 23:00 | 13.57 | -3.91
2019-08-27 23:30 | 52.7 | -51.95
2019-08-28 | 72.4 | -72.16
2019-08-28 00:30 | 82.43 | -82.34
2019-08-28 01:00 | 87.48 | -87.43
2019-08-28 01:30 | 89.32 | -89.3
2019-08-28 02:00 | 86.16 | -86.13
2019-08-28 02:30 | 80.33 | -80.17
2019-08-28 03:00 | 79.13 | -78.78
2019-08-28 03:30 | 31.7 | -29.15
2019-08-28 04:00 | 29.27 | -27.69
2019-08-28 04:30 | 19.61 | -16.54
2019-08-28 05:00 | 13.48 | -4.18
2019-08-28 05:30 | 18.4 | 6.86
2019-08-28 06:00 | 21.67 | 13.76
2019-08-28 06:30 | 38.22 | 35.93
2019-08-28 07:00 | 44.89 | 41.98
2019-08-28 07:30 | 45.05 | 44.4
2019-08-28 08:00 | 41.04 | 40.78
2019-08-28 08:30 | 39.93 | 39.51
2019-08-28 09:00 | 33.54 | 33.23
2019-08-28 09:30 | 30.49 | 30.29
2019-08-28 10:00 | 34.89 | 34.77
2019-08-28 10:30 | 34.01 | 34.01
2019-08-28 11:00 | 49.46 | 49.44
2019-08-28 11:30 | 66.8 | 66.8
2019-08-28 12:00 | 65.92 | 65.9
2019-08-28 12:30 | 55.53 | 55.48
2019-08-28 13:00 | 50.02 | 49.87
2019-08-28 13:30 | 51.36 | 51.2
2019-08-28 14:00 | 76.55 | 76.45
2019-08-28 14:30 | 77.3 | 77.2
2019-08-28 15:00 | 70.11 | 69.91
2019-08-28 15:30 | 78.11 | 77.83
2019-08-28 16:00 | 83.21 | 82.87
2019-08-28 16:30 | 80.5 | 80.16
2019-08-28 17:00 | 62.61 | 62.47
2019-08-28 17:30 | 42.23 | 42.18
2019-08-28 18:00 | 55.01 | 45.5
2019-08-28 18:30 | 72.7 | 47.85
2019-08-28 19:00 | 73.79 | 52.23
2019-08-28 19:30 | 40.3 | 11.46
2019-08-28 20:00 | 46.93 | -35.21
2019-08-28 20:30 | 34.08 | 20.54
2019-08-28 21:00 | 36.08 | -23.39
2019-08-28 21:30 | 33.3 | -23.35
2019-08-28 22:00 | 9.67 | -6.39
2019-08-28 22:30 | 55.59 | 51.26
2019-08-28 23:00 | 57.63 | 53.58
2019-08-28 23:30 | 29.04 | 23.46
2019-08-29 | 29.36 | -29.08
2019-08-29 00:30 | 76.03 | -75.1
2019-08-29 01:00 | 86.88 | -85.46
2019-08-29 01:30 | 88.81 | -87.8
2019-08-29 02:00 | 81.23 | -80.41
2019-08-29 02:30 | 68.5 | -68.36
2019-08-29 03:00 | 49.9 | -49.87
2019-08-29 03:30 | 26.45 | -26.44
2019-08-29 04:00 | 30.77 | -30.75
2019-08-29 04:30 | 8.15 | -6.77
2019-08-29 05:00 | 5.7 | 0.43
2019-08-29 05:30 | 16.01 | 4.81
2019-08-29 06:00 | 33.65 | 28.11
2019-08-29 06:30 | 37.58 | 33.56
2019-08-29 07:00 | 56.16 | 56.13
2019-08-29 07:30 | 60.21 | 59.5
2019-08-29 08:00 | 44.96 | 43.23
2019-08-29 08:30 | 18.59 | 11.61
2019-08-29 09:00 | 19.35 | 11.61
2019-08-29 09:30 | 18.78 | 12.9
2019-08-29 10:00 | 45.49 | 43.36
2019-08-29 10:30 | 55.21 | 53.49
2019-08-29 11:00 | 28.18 | 23.93
2019-08-29 11:30 | 34 | 29.06
2019-08-29 12:00 | 36.56 | 33.09
2019-08-29 12:30 | 25.15 | -20.81
2019-08-29 13:00 | 21.39 | -14.65
2019-08-29 13:30 | 20.86 | -9.59
2019-08-29 14:00 | 28.51 | 21.92
2019-08-29 14:30 | 25.49 | 19.71
2019-08-29 15:00 | 26.18 | 22.66
2019-08-29 15:30 | 22.13 | 18.54
2019-08-29 16:00 | 19.37 | 14.83
2019-08-29 16:30 | 37.44 | 36
2019-08-29 17:00 | 21.85 | 18.55
2019-08-29 17:30 | 44.43 | 42.53
2019-08-29 18:00 | 109.71 | 106.9
2019-08-29 18:30 | 96.68 | 91.59
2019-08-29 19:00 | 96.61 | 91.9
2019-08-29 19:30 | 91.39 | 88.59
2019-08-29 20:00 | 94.53 | 94.43
2019-08-29 20:30 | 60.51 | 60.4
2019-08-29 21:00 | 54.54 | -54.11
2019-08-29 21:30 | 60.32 | 60.19
2019-08-29 22:00 | 62.3 | 59.2
2019-08-29 22:30 | 44.93 | 40.58
2019-08-29 23:00 | 59.87 | 56.63
2019-08-29 23:30 | 44.45 | 42.17
2019-08-30 | 21.81 | 18.35
2019-08-30 00:30 | 27.88 | -27.6
2019-08-30 01:00 | 3.5 | 0.41
2019-08-30 01:30 | 81.12 | -80.93
2019-08-30 02:00 | 60.92 | -60.82
2019-08-30 02:30 | 32.42 | -32.41
2019-08-30 03:00 | 24.74 | -24.68
2019-08-30 03:30 | 25.34 | -25.27
2019-08-30 04:00 | 30.99 | -30.95
2019-08-30 04:30 | 21.73 | -21.54
2019-08-30 05:00 | 6.62 | 2.23
2019-08-30 05:30 | 18.3 | 14.9
2019-08-30 06:00 | 35.74 | 32.49
2019-08-30 06:30 | 25.77 | 22.19
2019-08-30 07:00 | 23.4 | 19.42
2019-08-30 07:30 | 21.08 | 16.87
2019-08-30 08:00 | 20.11 | 8.07
2019-08-30 08:30 | 26.82 | 16.05
2019-08-30 09:00 | 45.54 | 40.55
2019-08-30 09:30 | 44.07 | 38.77
2019-08-30 10:00 | 36.41 | 28.95
2019-08-30 10:30 | 23.34 | 4.45
2019-08-30 11:00 | 24.13 | 13.24
2019-08-30 11:30 | 25.09 | 13.69
2019-08-30 12:00 | 26.02 | 17.71
2019-08-30 12:30 | 29.53 | 19.68
2019-08-30 13:00 | 34.9 | 27.27
2019-08-30 13:30 | 38.71 | 32.06
2019-08-30 14:00 | 28.83 | 21.55
2019-08-30 14:30 | 26.1 | 15.61
2019-08-30 15:00 | 20.41 | 9.19
2019-08-30 15:30 | 30.33 | 23.97
2019-08-30 16:00 | 35.67 | 28.04
2019-08-30 16:30 | 42.91 | 36.28
2019-08-30 17:00 | 49.68 | 43.14
2019-08-30 17:30 | 46.55 | 44.55
2019-08-30 18:00 | 31.25 | 30.99
2019-08-30 18:30 | 24.14 | 24.09
2019-08-30 19:00 | 24.4 | -20.04
2019-08-30 19:30 | 52.28 | -49.08
2019-08-30 20:00 | 53.45 | -51.17
2019-08-30 20:30 | 50.3 | -48.61
2019-08-30 21:00 | 49.18 | -47.15
2019-08-30 21:30 | 55.9 | -54.03
2019-08-30 22:00 | 44.06 | -42.45
2019-08-30 22:30 | 26.06 | -24.71
2019-08-30 23:00 | 24.67 | -23.46
2019-08-30 23:30 | 61.56 | -60.95
2019-08-31 | 76.46 | -76.27
2019-08-31 00:30 | 49.8 | -49.12
2019-08-31 01:00 | 19.4 | -15.4
2019-08-31 01:30 | 49.17 | -48.71
2019-08-31 02:00 | 5.88 | 2.12
2019-08-31 02:30 | 6.91 | -5.14
2019-08-31 03:00 | 4.53 | -1.68
2019-08-31 03:30 | 6.79 | 4.53
2019-08-31 04:00 | 14.84 | 14.8
2019-08-31 04:30 | 29.35 | 26.23
2019-08-31 05:00 | 35.37 | 34.33
2019-08-31 05:30 | 53.54 | 53.04
2019-08-31 06:00 | 57.29 | 56.92
2019-08-31 06:30 | 38.81 | 38.38
2019-08-31 07:00 | 23.82 | 23.17
2019-08-31 07:30 | 10.29 | 8.87
2019-08-31 08:00 | 9.69 | -4.92
2019-08-31 08:30 | 9.02 | -1.42
2019-08-31 09:00 | 36.33 | -35.54
2019-08-31 09:30 | 77.08 | -76.89
2019-08-31 10:00 | 80.42 | -80.25
2019-08-31 10:30 | 77.92 | -77.76
2019-08-31 11:00 | 83.7 | -83.57
2019-08-31 11:30 | 80.73 | -80.51
2019-08-31 12:00 | 79.76 | -79.66
2019-08-31 12:30 | 76.62 | -76.54
2019-08-31 13:00 | 76.63 | -76.55
2019-08-31 13:30 | 74.13 | -74.06
2019-08-31 14:00 | 72.37 | -72.29
2019-08-31 14:30 | 71.78 | -71.66
2019-08-31 15:00 | 62.44 | -62.28
2019-08-31 15:30 | 27.08 | -25.77
2019-08-31 16:00 | 14.8 | 10.77
2019-08-31 16:30 | 29.53 | 27.33
2019-08-31 17:00 | 57.37 | 56.27
2019-08-31 17:30 | 50.15 | 48.99
2019-08-31 18:00 | 52.33 | 52.3
2019-08-31 18:30 | 33.04 | 27.84
2019-08-31 19:00 | 43.4 | 40.33
2019-08-31 19:30 | 17.05 | 8.39
2019-08-31 20:00 | 26.97 | -22.83
2019-08-31 20:30 | 13.25 | 6.57
2019-08-31 21:00 | 40.32 | -38.45
2019-08-31 21:30 | 17.38 | -14.86
2019-08-31 22:00 | 35.79 | 35.46
2019-08-31 22:30 | 59.56 | 59.51
2019-08-31 23:00 | 65.24 | 65.21
2019-08-31 23:30 | 43.47 | 43.46
2019-09-01 | 9.02 | -8.53
2019-09-01 00:30 | 28.07 | 22.98
2019-09-01 01:00 | 34.44 | 28.33
2019-09-01 01:30 | 34.35 | 28.2
2019-09-01 02:00 | 32.83 | 27.08
2019-09-01 02:30 | 23.9 | 14.67
2019-09-01 03:00 | 22.68 | -13.5
2019-09-01 03:30 | 19.52 | -5.9
2019-09-01 04:00 | 20.84 | 8.25
2019-09-01 04:30 | 26.97 | 18.53
2019-09-01 05:00 | 38.29 | 33.07
2019-09-01 05:30 | 54.06 | 50.33
2019-09-01 06:00 | 59.89 | 56.56
2019-09-01 06:30 | 52.54 | 48.82
2019-09-01 07:00 | 55.11 | 51.54
2019-09-01 07:30 | 33.09 | 27.68
2019-09-01 08:00 | 16.66 | 5.38
2019-09-01 08:30 | 15.92 | 6.16
2019-09-01 09:00 | 43.94 | -42.84
2019-09-01 09:30 | 68.89 | -68.86
2019-09-01 10:00 | 73.73 | -72.28
2019-09-01 10:30 | 75.17 | -73.63
2019-09-01 11:00 | 81.31 | -79.9
2019-09-01 11:30 | 83.31 | -81.78
2019-09-01 12:00 | 84.13 | -82.62
2019-09-01 12:30 | 85.23 | -83.76
2019-09-01 13:00 | 85.9 | -84.33
2019-09-01 13:30 | 90.95 | -89.6
2019-09-01 14:00 | 97.57 | -96.4
2019-09-01 14:30 | 95.6 | -94.44
2019-09-01 15:00 | 94.13 | -92.9
2019-09-01 15:30 | 69.18 | -67.81
2019-09-01 16:00 | 73.27 | -71.84
2019-09-01 16:30 | 73.61 | -72.06
2019-09-01 17:00 | 39.9 | -25.49
2019-09-01 17:30 | 32.71 | 32.23
2019-09-01 18:00 | 71.51 | 71.03
2019-09-01 18:30 | 96.31 | 95.44
2019-09-01 19:00 | 98.09 | 97.29
2019-09-01 19:30 | 80.69 | 80.43
2019-09-01 20:00 | 69.49 | 69.37
2019-09-01 20:30 | 13.52 | 5.76
2019-09-01 21:00 | 56.61 | -52.07
2019-09-01 21:30 | 22.99 | -22.98
2019-09-01 22:00 | 16.59 | -16.05
2019-09-01 22:30 | 7.96 | 0.5
2019-09-01 23:00 | 21.94 | 19.53
2019-09-01 23:30 | 27.4 | 25.93
2019-09-02 | 21.34 | 19.05
2019-09-02 00:30 | 9.08 | 4.8
2019-09-02 01:00 | 10.94 | -9.23
2019-09-02 01:30 | 12.87 | -11.46
2019-09-02 02:00 | 5.47 | 1.25
2019-09-02 02:30 | 9.4 | 7.26
2019-09-02 03:00 | 10.25 | 9.96
2019-09-02 03:30 | 17.85 | 14.97
2019-09-02 04:00 | 33.63 | 32.5
2019-09-02 04:30 | 36.25 | 35.46
2019-09-02 05:00 | 47.38 | 47.05
2019-09-02 05:30 | 58.68 | 58.67
2019-09-02 06:00 | 70.14 | 70.12
2019-09-02 06:30 | 57.75 | 57.75
2019-09-02 07:00 | 48.33 | 47.43
2019-09-02 07:30 | 58.73 | 58.48
2019-09-02 08:00 | 44.72 | 44.72
2019-09-02 08:30 | 39.51 | 39.48
2019-09-02 09:00 | 33.31 | 33.22
2019-09-02 09:30 | 25.42 | 25.17
2019-09-02 10:00 | 23.6 | 23.14
2019-09-02 10:30 | 13.66 | 12.47
2019-09-02 11:00 | 12.87 | 11.68
2019-09-02 11:30 | 13.38 | 11.62
2019-09-02 12:00 | 12.48 | 10.84
2019-09-02 12:30 | 10.22 | 8.37
2019-09-02 13:00 | 12.68 | 11.06
2019-09-02 13:30 | 14.98 | 14.25
2019-09-02 14:00 | 23.89 | 22.53
2019-09-02 14:30 | 32.19 | 31.33
2019-09-02 15:00 | 33.5 | 32.91
2019-09-02 15:30 | 46.76 | 46.52
2019-09-02 16:00 | 63.64 | 63.46
2019-09-02 16:30 | 67.55 | 67.45
2019-09-02 17:00 | 63.43 | 63.39
2019-09-02 17:30 | 61.99 | 61.77
2019-09-02 18:00 | 96.04 | 95.59
2019-09-02 18:30 | 110.29 | 110.03
2019-09-02 19:00 | 91.18 | 91.16
2019-09-02 19:30 | 53.05 | 52.85
2019-09-02 20:00 | 56.93 | 56.71
2019-09-02 20:30 | 64.67 | 64.5
2019-09-02 21:00 | 50.32 | 50.08
2019-09-02 21:30 | 59.59 | 59.11
2019-09-02 22:00 | 45.72 | 44.83
2019-09-02 22:30 | 46.67 | 45.56
2019-09-02 23:00 | 60.15 | 59.15
2019-09-02 23:30 | 32.58 | 31.35
2019-09-03 | 23.99 | 22.56
2019-09-03 00:30 | 20.51 | 20.14
2019-09-03 01:00 | 20.7 | 20.41
2019-09-03 01:30 | 12.85 | 11.83
2019-09-03 02:00 | 19.5 | 19.5
2019-09-03 02:30 | 20.48 | 20.41
2019-09-03 03:00 | 19.15 | 19.02
2019-09-03 03:30 | 20.83 | 20.65
2019-09-03 04:00 | 18.7 | 18.54
2019-09-03 04:30 | 19.72 | 19.48
2019-09-03 05:00 | 31.85 | 31.41
2019-09-03 05:30 | 53.85 | 53
2019-09-03 06:00 | 60.5 | 60.02
2019-09-03 06:30 | 60.09 | 60.07
2019-09-03 07:00 | 51.4 | 51.4
2019-09-03 07:30 | 51.63 | 49.13
2019-09-03 08:00 | 54.38 | 46.13
2019-09-03 08:30 | 51.78 | 43.06
2019-09-03 09:00 | 36.32 | 34
2019-09-03 09:30 | 28.77 | 28.32
2019-09-03 10:00 | 23.58 | 23.45
2019-09-03 10:30 | 12.06 | 11.93
2019-09-03 11:00 | 10.31 | 10.18
2019-09-03 11:30 | 8.05 | 7.95
2019-09-03 12:00 | 11.64 | 11.6
2019-09-03 12:30 | 6.21 | 6.2
2019-09-03 13:00 | 6.41 | 6.32
2019-09-03 13:30 | 13.05 | 13.04
2019-09-03 14:00 | 17.74 | 17.7
2019-09-03 14:30 | 23.86 | 23.85
2019-09-03 15:00 | 26.79 | 26.78
2019-09-03 15:30 | 29.09 | 29.01
2019-09-03 16:00 | 43.09 | 43.03
2019-09-03 16:30 | 67.92 | 67.91
2019-09-03 17:00 | 77.73 | 77.73
2019-09-03 17:30 | 70.14 | 70.14
2019-09-03 18:00 | 98.06 | 98.03
2019-09-03 18:30 | 103.1 | 103.03
2019-09-03 19:00 | 104.58 | 104.55
2019-09-03 19:30 | 66.77 | 66.64
2019-09-03 20:00 | 51.43 | 51.11
2019-09-03 20:30 | 52.21 | 52.15
2019-09-03 21:00 | 54.4 | 54.4
2019-09-03 21:30 | 38.55 | 38.54
2019-09-03 22:00 | 29.8 | 29.64
2019-09-03 22:30 | 29 | 27.62
2019-09-03 23:00 | 41.35 | 39.78
2019-09-03 23:30 | 21.4 | 18.95
2019-09-04 | 9.21 | 3.2
2019-09-04 00:30 | 4.88 | -2.25
2019-09-04 01:00 | 10.65 | -8.35
2019-09-04 01:30 | 11.41 | -9.23
2019-09-04 02:00 | 13.58 | -10.88
2019-09-04 02:30 | 9.04 | -6.34
2019-09-04 03:00 | 6.78 | -6.29
2019-09-04 03:30 | 2.25 | 0.49
2019-09-04 04:00 | 6.88 | 6.74
2019-09-04 04:30 | 20.18 | 20.17
2019-09-04 05:00 | 31.99 | 31.81
2019-09-04 05:30 | 53.98 | 53.66
2019-09-04 06:00 | 54.57 | 54.17
2019-09-04 06:30 | 68.83 | 68.65
2019-09-04 07:00 | 52.24 | 52.05
2019-09-04 07:30 | 114.88 | 114.81
2019-09-04 08:00 | 142.55 | 141.96
2019-09-04 08:30 | 110.53 | 109.39
2019-09-04 09:00 | 111.17 | 111.16
2019-09-04 09:30 | 108.3 | 108.29
2019-09-04 10:00 | 109.72 | 109.62
2019-09-04 10:30 | 107.42 | 107.31
2019-09-04 11:00 | 103.44 | 103.3
2019-09-04 11:30 | 103.02 | 102.74
2019-09-04 12:00 | 103.38 | 103.19
2019-09-04 12:30 | 103.4 | 103.2
2019-09-04 13:00 | 60.32 | 60.11
2019-09-04 13:30 | 82.57 | 82.44
2019-09-04 14:00 | 124.31 | 124.22
2019-09-04 14:30 | 128.37 | 128.34
2019-09-04 15:00 | 134.53 | 134.52
2019-09-04 15:30 | 141.24 | 141.24
2019-09-04 16:00 | 148.42 | 148.41
2019-09-04 16:30 | 149.53 | 149.51
2019-09-04 17:00 | 157.13 | 157.08
2019-09-04 17:30 | 159.05 | 158.97
2019-09-04 18:00 | 138.25 | 138.19
2019-09-04 18:30 | 124.64 | 124.61
2019-09-04 19:00 | 114.04 | 114
2019-09-04 19:30 | 105.75 | 105.72
2019-09-04 20:00 | 91.27 | 91.24
2019-09-04 20:30 | 69.22 | 69.21
2019-09-04 21:00 | 82.67 | 82.62
2019-09-04 21:30 | 78.27 | 78.11
2019-09-04 22:00 | 63.19 | 62.99
2019-09-04 22:30 | 52.39 | 52.13
2019-09-04 23:00 | 59.97 | 59.55
2019-09-04 23:30 | 45.38 | 44.85
2019-09-05 | 17.03 | 15.77
2019-09-05 00:30 | 12.52 | 12.51
2019-09-05 01:00 | 5.38 | -0.96
2019-09-05 01:30 | 10.18 | -7.39
2019-09-05 02:00 | 9.09 | -4.86
2019-09-05 02:30 | 7.75 | -1.34
2019-09-05 03:00 | 6.9 | 0.98
2019-09-05 03:30 | 7.4 | 3.26
2019-09-05 04:00 | 7.77 | 4.76
2019-09-05 04:30 | 9.13 | 7.48
2019-09-05 05:00 | 10.07 | 9.6
2019-09-05 05:30 | 13.97 | 13.96
2019-09-05 06:00 | 23.49 | 23.48
2019-09-05 06:30 | 54.04 | 54.04
2019-09-05 07:00 | 64.03 | 64.03
2019-09-05 07:30 | 112.93 | 112.91
2019-09-05 08:00 | 111.28 | 111.28
2019-09-05 08:30 | 109.59 | 109.58
2019-09-05 09:00 | 97.77 | 97.77
2019-09-05 09:30 | 89.63 | 89.62
2019-09-05 10:00 | 93.78 | 93.77
2019-09-05 10:30 | 86.39 | 86.38
2019-09-05 11:00 | 107.3 | 107.17
2019-09-05 11:30 | 104.98 | 104.73
2019-09-05 12:00 | 102.59 | 101.99
2019-09-05 12:30 | 106.48 | 105.99
2019-09-05 13:00 | 120.02 | 119.98
2019-09-05 13:30 | 117.28 | 117.26
2019-09-05 14:00 | 116.84 | 116.57
2019-09-05 14:30 | 126.77 | 126.49
2019-09-05 15:00 | 133.19 | 132.93
2019-09-05 15:30 | 140.46 | 140.26
2019-09-05 16:00 | 150.44 | 150.35
2019-09-05 16:30 | 152.83 | 152.77
2019-09-05 17:00 | 125.99 | 125.97
2019-09-05 17:30 | 108.38 | 108.37
2019-09-05 18:00 | 108.06 | 108.01
2019-09-05 18:30 | 123.78 | 123.67
2019-09-05 19:00 | 124.59 | 124.44
2019-09-05 19:30 | 105.22 | 105.01
2019-09-05 20:00 | 102.49 | 102.49
2019-09-05 20:30 | 103.17 | 103.14
2019-09-05 21:00 | 74.8 | 74.65
2019-09-05 21:30 | 69.71 | 69.36
2019-09-05 22:00 | 55.9 | 55.29
2019-09-05 22:30 | 55.19 | 54.4
2019-09-05 23:00 | 47.13 | 45.71
2019-09-05 23:30 | 15.4 | 12.81
2019-09-06 | 12.93 | 7.07
2019-09-06 00:30 | 38.28 | 37.15
2019-09-06 01:00 | 40.93 | 40.34
2019-09-06 01:30 | 36.56 | 36.11
2019-09-06 02:00 | 38.48 | 38
2019-09-06 02:30 | 51.85 | 51.32
2019-09-06 03:00 | 47.3 | 46.8
2019-09-06 03:30 | 45.31 | 44.92
2019-09-06 04:00 | 50.18 | 49.46
2019-09-06 04:30 | 56.93 | 56.3
2019-09-06 05:00 | 76.43 | 76.05
2019-09-06 05:30 | 89.44 | 89.23
2019-09-06 06:00 | 105.3 | 105.14
2019-09-06 06:30 | 67.58 | 66.95
2019-09-06 07:00 | 108.89 | 108.84
2019-09-06 07:30 | 116.06 | 115.77
2019-09-06 08:00 | 86.98 | 86.74
2019-09-06 08:30 | 57.37 | 57.15
2019-09-06 09:00 | 6.67 | 3.56
2019-09-06 09:30 | 11.11 | -8
2019-09-06 10:00 | 8.29 | 1.75
2019-09-06 10:30 | 17.03 | -13.93
2019-09-06 11:00 | 25.6 | -23.03
2019-09-06 11:30 | 21.85 | -18.33
2019-09-06 12:00 | 28.9 | -25.85
2019-09-06 12:30 | 27.06 | -23.59
2019-09-06 13:00 | 14.43 | 7.58
2019-09-06 13:30 | 15.86 | 9.66
2019-09-06 14:00 | 19.04 | 16.87
2019-09-06 14:30 | 61.07 | 60.79
2019-09-06 15:00 | 78.53 | 78.47
2019-09-06 15:30 | 89.41 | 89.38
2019-09-06 16:00 | 114.13 | 114.12
2019-09-06 16:30 | 117.52 | 117.5
2019-09-06 17:00 | 137.91 | 137.89
2019-09-06 17:30 | 131.23 | 131.21
2019-09-06 18:00 | 121.46 | 121.33
2019-09-06 18:30 | 132.56 | 132.29
2019-09-06 19:00 | 152.53 | 152.31
2019-09-06 19:30 | 165.67 | 165.61
2019-09-06 20:00 | 156.31 | 156.31
2019-09-06 20:30 | 139.34 | 139.31
2019-09-06 21:00 | 118.11 | 117.99
2019-09-06 21:30 | 117.59 | 117.34
2019-09-06 22:00 | 108.24 | 107.79
2019-09-06 22:30 | 119.02 | 118.47
2019-09-06 23:00 | 146.78 | 146.22
2019-09-06 23:30 | 116.76 | 115.98
2019-09-07 | 83.57 | 82.32
2019-09-07 00:30 | 81.96 | 80.29
2019-09-07 01:00 | 73.43 | 73.14
2019-09-07 01:30 | 71.05 | 70.78
2019-09-07 02:00 | 62.05 | 61.67
2019-09-07 02:30 | 60.66 | 60.24
2019-09-07 03:00 | 63.73 | 63.21
2019-09-07 03:30 | 72.8 | 72.27
2019-09-07 04:00 | 70.3 | 69.4
2019-09-07 04:30 | 71.73 | 69.92
2019-09-07 05:00 | 75.54 | 73.73
2019-09-07 05:30 | 85.97 | 84.29
2019-09-07 06:00 | 87.25 | 85.68
2019-09-07 06:30 | 62.46 | 60.28
2019-09-07 07:00 | 57.44 | 54.76
2019-09-07 07:30 | 40.46 | 37.44
2019-09-07 08:00 | 23.26 | 20.9
2019-09-07 08:30 | 27.42 | -27.42
2019-09-07 09:00 | 38.01 | -37.97
2019-09-07 09:30 | 38.86 | -38.83
2019-09-07 10:00 | 41.94 | -41.93
2019-09-07 10:30 | 41.14 | -41.06
2019-09-07 11:00 | 16.45 | 10.4
2019-09-07 11:30 | 14.79 | 3.04
2019-09-07 12:00 | 32.19 | 26.25
2019-09-07 12:30 | 52.15 | -51.4
2019-09-07 13:00 | 61.62 | -61.6
2019-09-07 13:30 | 58.21 | -58.13
2019-09-07 14:00 | 47.36 | -47.11
2019-09-07 14:30 | 11.45 | -7.88
2019-09-07 15:00 | 23.67 | 19.65
2019-09-07 15:30 | 31.47 | 27.62
2019-09-07 16:00 | 14.6 | 9.17
2019-09-07 16:30 | 26.29 | 25.13
2019-09-07 17:00 | 85.36 | 84.45
2019-09-07 17:30 | 89.88 | 88.73
2019-09-07 18:00 | 82.21 | 81.68
2019-09-07 18:30 | 97.11 | 97.1
2019-09-07 19:00 | 99.64 | 99.61
2019-09-07 19:30 | 90.18 | 90.07
2019-09-07 20:00 | 95.25 | 95.01
2019-09-07 20:30 | 90.53 | 90.11
2019-09-07 21:00 | 76.44 | 75.76
2019-09-07 21:30 | 65.17 | 63.75
2019-09-07 22:00 | 59.18 | 57.1
2019-09-07 22:30 | 64.28 | 61.96
2019-09-07 23:00 | 72.98 | 70.63
2019-09-07 23:30 | 67.27 | 64.63
2019-09-08 | 54.11 | 52.03
2019-09-08 00:30 | 43.69 | 41.74
2019-09-08 01:00 | 60.31 | 59.19
2019-09-08 01:30 | 53.88 | 53.77
2019-09-08 02:00 | 63.11 | 62.94
2019-09-08 02:30 | 66.21 | 66.05
2019-09-08 03:00 | 64.11 | 63.9
2019-09-08 03:30 | 62.77 | 62.55
2019-09-08 04:00 | 63.98 | 63.2
2019-09-08 04:30 | 63.93 | 62.77
2019-09-08 05:00 | 67.53 | 66.13
2019-09-08 05:30 | 65.72 | 63.46
2019-09-08 06:00 | 62.95 | 60.91
2019-09-08 06:30 | 47.63 | 44.93
2019-09-08 07:00 | 27.84 | 22.26
2019-09-08 07:30 | 36.33 | -35.93
2019-09-08 08:00 | 48.57 | -48.17
2019-09-08 08:30 | 47.56 | -46.81
2019-09-08 09:00 | 47.13 | -46.59
2019-09-08 09:30 | 46.58 | -46.15
2019-09-08 10:00 | 39.71 | -39.17
2019-09-08 10:30 | 48.03 | -47.7
2019-09-08 11:00 | 58.56 | -58.33
2019-09-08 11:30 | 63.54 | -63.35
2019-09-08 12:00 | 60.41 | -60.26
2019-09-08 12:30 | 57.06 | -56.84
2019-09-08 13:00 | 65.84 | -65.68
2019-09-08 13:30 | 61.54 | -61.41
2019-09-08 14:00 | 59.57 | -59.44
2019-09-08 14:30 | 60.41 | -60.28
2019-09-08 15:00 | 54.54 | -54.44
2019-09-08 15:30 | 45.58 | -45.58
2019-09-08 16:00 | 35.48 | -31.52
2019-09-08 16:30 | 25.78 | -20.02
2019-09-08 17:00 | 32.39 | 29.17
2019-09-08 17:30 | 71.3 | 71.27
2019-09-08 18:00 | 53.58 | 53.45
2019-09-08 18:30 | 117.95 | 117.92
2019-09-08 19:00 | 117.41 | 117.3
2019-09-08 19:30 | 103.74 | 103.49
2019-09-08 20:00 | 102.63 | 102.15
2019-09-08 20:30 | 97.76 | 97.1
2019-09-08 21:00 | 76.68 | 75.61
2019-09-08 21:30 | 85.79 | 84.47
2019-09-08 22:00 | 75.68 | 73.74
2019-09-08 22:30 | 90.03 | 87.97
2019-09-08 23:00 | 104.61 | 102.46
2019-09-08 23:30 | 91.06 | 88.43
2019-09-09 | 57.42 | 55.07
2019-09-09 00:30 | 56.52 | 54.71
2019-09-09 01:00 | 46.43 | 44.69
2019-09-09 01:30 | 36.69 | 34.32
2019-09-09 02:00 | 34.53 | 32.01
2019-09-09 02:30 | 39.81 | 37.51
2019-09-09 03:00 | 38.31 | 36.08
2019-09-09 03:30 | 44.45 | 44.07
2019-09-09 04:00 | 48.3 | 48.08
2019-09-09 04:30 | 52.16 | 52.07
2019-09-09 05:00 | 45.21 | 45.21
2019-09-09 05:30 | 77.24 | 77.21
2019-09-09 06:00 | 87.78 | 86.53
2019-09-09 06:30 | 82.67 | 81.61
2019-09-09 07:00 | 98.89 | 98.45
2019-09-09 07:30 | 107.51 | 107.12
2019-09-09 08:00 | 90.38 | 90.24
2019-09-09 08:30 | 10.27 | 10.13
2019-09-09 09:00 | 19.76 | -19.17
2019-09-09 09:30 | 27.33 | -26.9
2019-09-09 10:00 | 31.29 | -30.64
2019-09-09 10:30 | 44.73 | -44.37
2019-09-09 11:00 | 50.51 | -50.19
2019-09-09 11:30 | 51.47 | -51.07
2019-09-09 12:00 | 51.18 | -50.76
2019-09-09 12:30 | 49.23 | -48.78
2019-09-09 13:00 | 46.45 | -45.96
2019-09-09 13:30 | 44.75 | -44.09
2019-09-09 14:00 | 40.91 | -40.23
2019-09-09 14:30 | 38.13 | -37.35
2019-09-09 15:00 | 36.09 | -35.6
2019-09-09 15:30 | 32.52 | -32.25
2019-09-09 16:00 | 30.4 | -30.17
2019-09-09 16:30 | 29.75 | -25.54
2019-09-09 17:00 | 37.81 | -11.85
2019-09-09 17:30 | 52 | 50.66
2019-09-09 18:00 | 84.42 | 78.73
2019-09-09 18:30 | 105.29 | 99.91
2019-09-09 19:00 | 137.71 | 134.31
2019-09-09 19:30 | 66.01 | 58.99
2019-09-09 20:00 | 30.03 | -0.11
2019-09-09 20:30 | 26.11 | -5.19
2019-09-09 21:00 | 7.61 | -7.49
2019-09-09 21:30 | 6.18 | -4.64
2019-09-09 22:00 | 38.51 | 36.65
2019-09-09 22:30 | 22.08 | 19.39
2019-09-09 23:00 | 31.96 | 29.3
2019-09-09 23:30 | 35.08 | -34.61
2019-09-10 | 44.28 | -43.96
2019-09-10 00:30 | 33.42 | -31.81
2019-09-10 01:00 | 32.18 | -27.92
2019-09-10 01:30 | 45.78 | -43.95
2019-09-10 02:00 | 46.9 | -45.09
2019-09-10 02:30 | 53.16 | -52.07
2019-09-10 03:00 | 51.41 | -50.19
2019-09-10 03:30 | 48.6 | -47.28
2019-09-10 04:00 | 46.82 | -45.74
2019-09-10 04:30 | 45.78 | -44.7
2019-09-10 05:00 | 48.09 | -46.87
2019-09-10 05:30 | 40.03 | -38.49
2019-09-10 06:00 | 22.96 | -19.87
2019-09-10 06:30 | 24.49 | -23.89
2019-09-10 07:00 | 80.37 | 79.53
2019-09-10 07:30 | 55.27 | 54.79
2019-09-10 08:00 | 18.44 | -8.08
2019-09-10 08:30 | 25.75 | -15.46
2019-09-10 09:00 | 29.08 | -20.81
2019-09-10 09:30 | 35.63 | -28.5
2019-09-10 10:00 | 42.59 | -36.27
2019-09-10 10:30 | 54.21 | -49.84
2019-09-10 11:00 | 53.99 | -49.7
2019-09-10 11:30 | 55.63 | -51.59
2019-09-10 12:00 | 55.4 | -51.28
2019-09-10 12:30 | 51.99 | -47.76
2019-09-10 13:00 | 51.88 | -47.71
2019-09-10 13:30 | 44.94 | -39.97
2019-09-10 14:00 | 43.19 | -38.15
2019-09-10 14:30 | 49.58 | -45.34
2019-09-10 15:00 | 47.78 | -43.09
2019-09-10 15:30 | 39.93 | -34.69
2019-09-10 16:00 | 35.56 | -30.1
2019-09-10 16:30 | 33.37 | -24.93
2019-09-10 17:00 | 33.43 | 13.17
2019-09-10 17:30 | 33.65 | 16.15
2019-09-10 18:00 | 34.08 | -3.29
2019-09-10 18:30 | 38.32 | 16.01
2019-09-10 19:00 | 36.79 | -4.93
2019-09-10 19:30 | 35.11 | -7.9
2019-09-10 20:00 | 33.18 | -8.39
2019-09-10 20:30 | 30.92 | -7.69
2019-09-10 21:00 | 19.63 | -14.1
2019-09-10 21:30 | 24.74 | -23.75
2019-09-10 22:00 | 33.01 | -32.28
2019-09-10 22:30 | 35.75 | -35.31
2019-09-10 23:00 | 31.86 | -31.62
2019-09-10 23:30 | 44.34 | -43.87
2019-09-11 | 54.31 | -53.71
2019-09-11 00:30 | 56.77 | -56.14
2019-09-11 01:00 | 49.84 | -49.7
2019-09-11 01:30 | 47.45 | -47.45
2019-09-11 02:00 | 51.79 | -51.7
2019-09-11 02:30 | 51.56 | -51.38
2019-09-11 03:00 | 50.73 | -50.56
2019-09-11 03:30 | 50.08 | -49.89
2019-09-11 04:00 | 48.02 | -47.68
2019-09-11 04:30 | 46.66 | -46.35
2019-09-11 05:00 | 49.14 | -49
2019-09-11 05:30 | 49.72 | -49.67
2019-09-11 06:00 | 45.41 | -45.28
2019-09-11 06:30 | 29.72 | -29.45
2019-09-11 07:00 | 42.97 | 42.72
2019-09-11 07:30 | 4.5 | 3.33
2019-09-11 08:00 | 16.3 | -14.8
2019-09-11 08:30 | 29.39 | -28.28
2019-09-11 09:00 | 30.41 | -28.85
2019-09-11 09:30 | 13.67 | -8.65
2019-09-11 10:00 | 25.32 | -23.62
2019-09-11 10:30 | 22.27 | 21.21
2019-09-11 11:00 | 44.1 | 43.72
2019-09-11 11:30 | 27.31 | 26.75
2019-09-11 12:00 | 23.14 | 22.77
2019-09-11 12:30 | 26.28 | 26.11
2019-09-11 13:00 | 27.21 | 27.15
2019-09-11 13:30 | 18.41 | 18.34
2019-09-11 14:00 | 17.88 | 17.72
2019-09-11 14:30 | 36.04 | 36.01
2019-09-11 15:00 | 44.74 | 44.74
2019-09-11 15:30 | 48.33 | 48.29
2019-09-11 16:00 | 54.1 | 54.02
2019-09-11 16:30 | 40.33 | 40.22
2019-09-11 17:00 | 72.15 | 72.05
2019-09-11 17:30 | 94.7 | 94.64
2019-09-11 18:00 | 115.18 | 115.18
2019-09-11 18:30 | 128.01 | 128.01
2019-09-11 19:00 | 129.61 | 129.61
2019-09-11 19:30 | 107.58 | 107.57
2019-09-11 20:00 | 98.78 | 98.72
2019-09-11 20:30 | 44.37 | 44.32
2019-09-11 21:00 | 16.98 | -0.44
2019-09-11 21:30 | 19.5 | -14.97
2019-09-11 22:00 | 27.7 | 26.96
2019-09-11 22:30 | 49.29 | 49.11
2019-09-11 23:00 | 73 | 72.98
2019-09-11 23:30 | 49.13 | 46.35
2019-09-12 | 19.35 | 0.09
2019-09-12 00:30 | 19.87 | 5.65
2019-09-12 01:00 | 11.67 | 0.44
2019-09-12 01:30 | 10.48 | -0.45
2019-09-12 02:00 | 10.24 | -2.27
2019-09-12 02:30 | 10.1 | -0.66
2019-09-12 03:00 | 9.95 | 0.89
2019-09-12 03:30 | 11.16 | 4.53
2019-09-12 04:00 | 22.69 | 19.8
2019-09-12 04:30 | 35.1 | 32.65
2019-09-12 05:00 | 45.38 | 42.82
2019-09-12 05:30 | 60.88 | 58.08
2019-09-12 06:00 | 68.9 | 66.24
2019-09-12 06:30 | 68.85 | 66.67
2019-09-12 07:00 | 107.4 | 107.06
2019-09-12 07:30 | 96.55 | 96.47
2019-09-12 08:00 | 66.77 | 66.72
2019-09-12 08:30 | 56.99 | 56.98
2019-09-12 09:00 | 57.13 | 57.12
2019-09-12 09:30 | 48.59 | 48.59
2019-09-12 10:00 | 43.12 | 43.06
2019-09-12 10:30 | 32.97 | 32.95
2019-09-12 11:00 | 26.69 | 26.66
2019-09-12 11:30 | 12.44 | 12.39
2019-09-12 12:00 | 48.03 | -47.85
2019-09-12 12:30 | 27.46 | -27.41
2019-09-12 13:00 | 53.15 | -53.06
2019-09-12 13:30 | 28.37 | -28.24
2019-09-12 14:00 | 27.01 | -26.89
2019-09-12 14:30 | 21.7 | -21.5
2019-09-12 15:00 | 38.52 | -38.41
2019-09-12 15:30 | 24.82 | -24.68
2019-09-12 16:00 | 31.92 | -31.82
2019-09-12 16:30 | 50.69 | -27.12
2019-09-12 17:00 | 50.11 | -7.56
2019-09-12 17:30 | 69.25 | 64.06
2019-09-12 18:00 | 77.44 | 71.74
2019-09-12 18:30 | 90.99 | 84.42
2019-09-12 19:00 | 99.71 | 93.84
2019-09-12 19:30 | 35.8 | 12.91
2019-09-12 20:00 | 47.47 | -31.28
2019-09-12 20:30 | 53.45 | -41.47
2019-09-12 21:00 | 57.77 | -48.51
2019-09-12 21:30 | 63.42 | -57.03
2019-09-12 22:00 | 69.29 | -64.79
2019-09-12 22:30 | 68.12 | -64.28
2019-09-12 23:00 | 59.53 | -58.98
2019-09-12 23:30 | 60.94 | -60.89
2019-09-13 | 67.99 | -67.91
2019-09-13 00:30 | 71.69 | -71.61
2019-09-13 01:00 | 63.02 | -62.81
2019-09-13 01:30 | 64.91 | -64.69
2019-09-13 02:00 | 62.8 | -62.61
2019-09-13 02:30 | 57.52 | -57.22
2019-09-13 03:00 | 60.25 | -60.07
2019-09-13 03:30 | 58.3 | -58.05
2019-09-13 04:00 | 59.59 | -59.24
2019-09-13 04:30 | 58.83 | -58.2
2019-09-13 05:00 | 59.02 | -58.32
2019-09-13 05:30 | 56.96 | -55.99
2019-09-13 06:00 | 47.65 | -46.54
2019-09-13 06:30 | 44.51 | -43.64
2019-09-13 07:00 | 29.84 | -29.05
2019-09-13 07:30 | 26.47 | -26.26
2019-09-13 08:00 | 27.1 | -27.07
2019-09-13 08:30 | 29.73 | -29.73
2019-09-13 09:00 | 32.04 | -32
2019-09-13 09:30 | 37.85 | -37.72
2019-09-13 10:00 | 41.97 | -41.78
2019-09-13 10:30 | 50.82 | -50.49
2019-09-13 11:00 | 50.2 | -49.72
2019-09-13 11:30 | 52.33 | -51.81
2019-09-13 12:00 | 51.14 | -50.59
2019-09-13 12:30 | 49.69 | -49.13
2019-09-13 13:00 | 48.27 | -47.64
2019-09-13 13:30 | 44.04 | -43.4
2019-09-13 14:00 | 39.54 | -39.07
2019-09-13 14:30 | 25.08 | -24.71
2019-09-13 15:00 | 25.24 | -25.02
2019-09-13 15:30 | 34.44 | -34.23
2019-09-13 16:00 | 30.18 | -29.27
2019-09-13 16:30 | 28.61 | -15.83
2019-09-13 17:00 | 29.65 | -19.08
2019-09-13 17:30 | 30.9 | -21.46
2019-09-13 18:00 | 24.38 | 9.95
2019-09-13 18:30 | 57.74 | 52.71
2019-09-13 19:00 | 27.25 | 12.4
2019-09-13 19:30 | 28.1 | -15.05
2019-09-13 20:00 | 25.12 | -13.69
2019-09-13 20:30 | 25.34 | -16.57
2019-09-13 21:00 | 27.65 | -21.79
2019-09-13 21:30 | 32.56 | -29.2
2019-09-13 22:00 | 38.99 | -37.02
2019-09-13 22:30 | 32.83 | -31.38
2019-09-13 23:00 | 30.8 | -29.51
2019-09-13 23:30 | 43.82 | -43.13
2019-09-14 | 52.54 | -52.25
2019-09-14 00:30 | 58.48 | -58.29
2019-09-14 01:00 | 63.15 | -63.13
2019-09-14 01:30 | 61.82 | -61.42
2019-09-14 02:00 | 53.95 | -53.38
2019-09-14 02:30 | 51.57 | -51.01
2019-09-14 03:00 | 49.62 | -48.74
2019-09-14 03:30 | 49.82 | -48.78
2019-09-14 04:00 | 50.92 | -49.96
2019-09-14 04:30 | 40.16 | -37.43
2019-09-14 05:00 | 34.21 | -30.23
2019-09-14 05:30 | 22.63 | -15.28
2019-09-14 06:00 | 33.73 | -30.45
2019-09-14 06:30 | 43.55 | -41.65
2019-09-14 07:00 | 47.52 | -46.09
2019-09-14 07:30 | 45.76 | -44.31
2019-09-14 08:00 | 44.99 | -43.63
2019-09-14 08:30 | 42.13 | -41.28
2019-09-14 09:00 | 40.23 | -39.81
2019-09-14 09:30 | 39.98 | -39.75
2019-09-14 10:00 | 40.92 | -40.75
2019-09-14 10:30 | 40.11 | -40.01
2019-09-14 11:00 | 46.92 | -46.87
2019-09-14 11:30 | 49.27 | -49.25
2019-09-14 12:00 | 47.91 | -47.88
2019-09-14 12:30 | 51.98 | -51.97
2019-09-14 13:00 | 51.88 | -51.88
2019-09-14 13:30 | 49.53 | -49.53
2019-09-14 14:00 | 44.2 | -44.2
2019-09-14 14:30 | 34.93 | -34.93
2019-09-14 15:00 | 39.28 | -39.28
2019-09-14 15:30 | 27.37 | -27.36
2019-09-14 16:00 | 35.07 | -35.06
2019-09-14 16:30 | 31.23 | -22.67
2019-09-14 17:00 | 53.26 | 46.96
2019-09-14 17:30 | 34.72 | 14.09
2019-09-14 18:00 | 31.29 | 5.9
2019-09-14 18:30 | 33.02 | 7.24
2019-09-14 19:00 | 59.46 | 51.54
2019-09-14 19:30 | 30.11 | -8.79
2019-09-14 20:00 | 30.29 | -22.49
2019-09-14 20:30 | 27.92 | -20.75
2019-09-14 21:00 | 31.82 | -26.75
2019-09-14 21:30 | 16.78 | -10.39
2019-09-14 22:00 | 37.52 | -35.45
2019-09-14 22:30 | 23.6 | -21.5
2019-09-14 23:00 | 9.08 | 6.11
2019-09-14 23:30 | 19.69 | 19.32
2019-09-15 | 26.42 | -26
2019-09-15 00:30 | 15.18 | -3.31
2019-09-15 01:00 | 45.85 | -44.35
2019-09-15 01:30 | 38.3 | -35.74
2019-09-15 02:00 | 42.66 | -40.55
2019-09-15 02:30 | 33.44 | -29.35
2019-09-15 03:00 | 42.61 | -39.96
2019-09-15 03:30 | 20.7 | -12.91
2019-09-15 04:00 | 19.1 | -17.77
2019-09-15 04:30 | 22.13 | -21.05
2019-09-15 05:00 | 16.35 | -14.48
2019-09-15 05:30 | 15.17 | -12.61
2019-09-15 06:00 | 19.78 | -19.03
2019-09-15 06:30 | 41.43 | -41.4
2019-09-15 07:00 | 47.68 | -47.48
2019-09-15 07:30 | 46.92 | -46.78
2019-09-15 08:00 | 44.9 | -44.7
2019-09-15 08:30 | 46.41 | -45.92
2019-09-15 09:00 | 42.27 | -41.89
2019-09-15 09:30 | 44.02 | -43.86
2019-09-15 10:00 | 44.12 | -44.04
2019-09-15 10:30 | 43.89 | -43.83
2019-09-15 11:00 | 48.5 | -48.49
2019-09-15 11:30 | 51.59 | -51.59
2019-09-15 12:00 | 51.01 | -51.01
2019-09-15 12:30 | 51.61 | -51.59
2019-09-15 13:00 | 51.98 | -51.97
2019-09-15 13:30 | 54.38 | -54.38
2019-09-15 14:00 | 52.02 | -52.02
2019-09-15 14:30 | 46.89 | -46.85
2019-09-15 15:00 | 46.72 | -46.7
2019-09-15 15:30 | 42.1 | -42.09
2019-09-15 16:00 | 5.87 | 2.66
2019-09-15 16:30 | 28.76 | 27.69
2019-09-15 17:00 | 55.08 | 54.39
2019-09-15 17:30 | 66.51 | 66.21
2019-09-15 18:00 | 66.4 | 66.27
2019-09-15 18:30 | 90.54 | 90.53
2019-09-15 19:00 | 96.08 | 96.06
2019-09-15 19:30 | 79.82 | 79.69
2019-09-15 20:00 | 52.03 | 51.77
2019-09-15 20:30 | 55.23 | 54.65
2019-09-15 21:00 | 42.69 | 41.73
2019-09-15 21:30 | 56.14 | 54.86
2019-09-15 22:00 | 65.1 | 63.55
2019-09-15 22:30 | 87.36 | 85.59
2019-09-15 23:00 | 91.24 | 89.23
2019-09-15 23:30 | 54.7 | 51.44
2019-09-16 | 33.75 | 27.89
2019-09-16 00:30 | 32.32 | 27.12
2019-09-16 01:00 | 24.08 | 21.48
2019-09-16 01:30 | 15.19 | 11.34
2019-09-16 02:00 | 9.31 | 3.04
2019-09-16 02:30 | 12.87 | 8.83
2019-09-16 03:00 | 13.93 | 10.66
2019-09-16 03:30 | 18.18 | 15.92
2019-09-16 04:00 | 30.41 | 28.53
2019-09-16 04:30 | 30.25 | 27.74
2019-09-16 05:00 | 28.93 | 25.68
2019-09-16 05:30 | 34.92 | 32
2019-09-16 06:00 | 47.81 | 46.53
2019-09-16 06:30 | 53.97 | 52.6
2019-09-16 07:00 | 72.65 | 71.66
2019-09-16 07:30 | 76.12 | 75.78
2019-09-16 08:00 | 59.18 | 59.02
2019-09-16 08:30 | 31.93 | 31.92
2019-09-16 09:00 | 8.7 | -7.59
2019-09-16 09:30 | 10.06 | 9.44
2019-09-16 10:00 | 33.67 | -33.03
2019-09-16 10:30 | 41.18 | -40.17
2019-09-16 11:00 | 40.63 | -39.24
2019-09-16 11:30 | 38.97 | -37.31
2019-09-16 12:00 | 48.56 | -37.4
2019-09-16 12:30 | 46.67 | -34.29
2019-09-16 13:00 | 37.79 | -20.86
2019-09-16 13:30 | 41.12 | -24.44
2019-09-16 14:00 | 41.96 | -26.16
2019-09-16 14:30 | 39.24 | -21.95
2019-09-16 15:00 | 54.45 | -23.03
2019-09-16 15:30 | 65.86 | -20.89
2019-09-16 16:00 | 62.63 | -12.95
2019-09-16 16:30 | 63.66 | 23.55
2019-09-16 17:00 | 92.16 | 71.72
2019-09-16 17:30 | 110.05 | 95.6
2019-09-16 18:00 | 111.62 | 96.92
2019-09-16 18:30 | 130.15 | 116.73
2019-09-16 19:00 | 92.86 | 73.11
2019-09-16 19:30 | 61.75 | 22.99
2019-09-16 20:00 | 69.58 | 65.58
2019-09-16 20:30 | 84.56 | 84.56
2019-09-16 21:00 | 63.7 | 63.63
2019-09-16 21:30 | 64.08 | 63.82
2019-09-16 22:00 | 46.27 | 45.79
2019-09-16 22:30 | 30.28 | 29.81
2019-09-16 23:00 | 49.15 | 48.57
2019-09-16 23:30 | 35.77 | 34.96
2019-09-17 | 8.94 | 5.45
2019-09-17 00:30 | 11.73 | 7.21
2019-09-17 01:00 | 12.89 | 3.03
2019-09-17 01:30 | 15.22 | 6.51
2019-09-17 02:00 | 12.5 | 4.1
2019-09-17 02:30 | 6.92 | -6.12
2019-09-17 03:00 | 8.72 | -8.64
2019-09-17 03:30 | 25.49 | -24.53
2019-09-17 04:00 | 26.31 | -24.56
2019-09-17 04:30 | 3.57 | 1.93
2019-09-17 05:00 | 31.62 | 31.6
2019-09-17 05:30 | 39.6 | 39.46
2019-09-17 06:00 | 59.29 | 59.26
2019-09-17 06:30 | 76.65 | 76.56
2019-09-17 07:00 | 63.5 | 63.13
2019-09-17 07:30 | 60.77 | 60.59
2019-09-17 08:00 | 96.06 | 96.05
2019-09-17 08:30 | 69.72 | 69.65
2019-09-17 09:00 | 52.69 | 52.2
2019-09-17 09:30 | 53.75 | 53.05
2019-09-17 10:00 | 50.81 | 49.95
2019-09-17 10:30 | 43.29 | 41.98
2019-09-17 11:00 | 43.04 | 41.67
2019-09-17 11:30 | 39.75 | 38.08
2019-09-17 12:00 | 45.96 | 44.39
2019-09-17 12:30 | 47.99 | 43.08
2019-09-17 13:00 | 51.24 | 40.64
2019-09-17 13:30 | 57.53 | 40.83
2019-09-17 14:00 | 76.87 | 49.14
2019-09-17 14:30 | 60.59 | 45.99
2019-09-17 15:00 | 62.3 | 48.67
2019-09-17 15:30 | 74.81 | 63.42
2019-09-17 16:00 | 100.27 | 92.24
2019-09-17 16:30 | 105.92 | 98.36
2019-09-17 17:00 | 104.03 | 95.91
2019-09-17 17:30 | 103.96 | 95.23
2019-09-17 18:00 | 106.43 | 97.61
2019-09-17 18:30 | 101.23 | 92.89
2019-09-17 19:00 | 103.51 | 95.97
2019-09-17 19:30 | 89.8 | 82.1
2019-09-17 20:00 | 87.27 | 80.27
2019-09-17 20:30 | 87.36 | 81.64
2019-09-17 21:00 | 74.66 | 72.45
2019-09-17 21:30 | 70.74 | 70.72
2019-09-17 22:00 | 54.9 | 54.88
2019-09-17 22:30 | 54.69 | 54.67
2019-09-17 23:00 | 58.91 | 58.91
2019-09-17 23:30 | 45.61 | 45.58
2019-09-18 | 31.48 | 31.44
2019-09-18 00:30 | 20.58 | 20.55
2019-09-18 01:00 | 14.66 | 14.3
2019-09-18 01:30 | 11.07 | 10.71
2019-09-18 02:00 | 15.16 | 14.83
2019-09-18 02:30 | 18.78 | 18.49
2019-09-18 03:00 | 21.17 | 20.93
2019-09-18 03:30 | 22.35 | 22.21
2019-09-18 04:00 | 24.36 | 24.3
2019-09-18 04:30 | 27.01 | 26.97
2019-09-18 05:00 | 28.42 | 28.27
2019-09-18 05:30 | 33.7 | 33.58
2019-09-18 06:00 | 50.51 | 50.47
2019-09-18 06:30 | 57.83 | 57.81
2019-09-18 07:00 | 60.26 | 60.22
2019-09-18 07:30 | 68.53 | 68.27
2019-09-18 08:00 | 67.75 | 67.14
2019-09-18 08:30 | 61.71 | 61.14
2019-09-18 09:00 | 57.31 | 56.62
2019-09-18 09:30 | 52.89 | 52.06
2019-09-18 10:00 | 50.56 | 49.61
2019-09-18 10:30 | 44.5 | 43.09
2019-09-18 11:00 | 44.79 | 43.16
2019-09-18 11:30 | 43.32 | 41.52
2019-09-18 12:00 | 44.65 | 42.94
2019-09-18 12:30 | 45.56 | 43.93
2019-09-18 13:00 | 46.1 | 44.84
2019-09-18 13:30 | 48.81 | 47.51
2019-09-18 14:00 | 51.19 | 49.84
2019-09-18 14:30 | 52.35 | 51.08
2019-09-18 15:00 | 49.71 | 48.54
2019-09-18 15:30 | 51.44 | 50.48
2019-09-18 16:00 | 56.72 | 55.95
2019-09-18 16:30 | 70.34 | 69.75
2019-09-18 17:00 | 83.01 | 80.72
2019-09-18 17:30 | 94.71 | 91.4
2019-09-18 18:00 | 99.07 | 95.79
2019-09-18 18:30 | 124.95 | 111.77
2019-09-18 19:00 | 118.33 | 104.46
2019-09-18 19:30 | 94.05 | 80.31
2019-09-18 20:00 | 89.12 | 83.09
2019-09-18 20:30 | 101.53 | 96.96
2019-09-18 21:00 | 94.09 | 90.07
2019-09-18 21:30 | 73.79 | 73.2
2019-09-18 22:00 | 68.27 | 68.23
2019-09-18 22:30 | 63.97 | 63.93
2019-09-18 23:00 | 71.14 | 71.06
2019-09-18 23:30 | 46.96 | 46.94
2019-09-19 | 37.16 | 37.11
2019-09-19 00:30 | 35.25 | 35.19
2019-09-19 01:00 | 38.37 | 38.24
2019-09-19 01:30 | 25.07 | 24.88
2019-09-19 02:00 | 20.32 | 20.12
2019-09-19 02:30 | 26.3 | 26.23
2019-09-19 03:00 | 31.59 | 31.51
2019-09-19 03:30 | 38.58 | 38.49
2019-09-19 04:00 | 50.25 | 49.82
2019-09-19 04:30 | 56.77 | 56.22
2019-09-19 05:00 | 60.45 | 60.02
2019-09-19 05:30 | 75.9 | 75.55
2019-09-19 06:00 | 78.25 | 77.92
2019-09-19 06:30 | 82.3 | 82.2
2019-09-19 07:00 | 92.94 | 92.93
2019-09-19 07:30 | 86.88 | 86.83
2019-09-19 08:00 | 73.03 | 72.87
2019-09-19 08:30 | 65.39 | 65.07
2019-09-19 09:00 | 60.67 | 60.14
2019-09-19 09:30 | 54.13 | 53.34
2019-09-19 10:00 | 52.05 | 50.9
2019-09-19 10:30 | 55.55 | 45.42
2019-09-19 11:00 | 56.32 | 45.57
2019-09-19 11:30 | 53.94 | 42.72
2019-09-19 12:00 | 54.14 | 43.25
2019-09-19 12:30 | 53.12 | 43.08
2019-09-19 13:00 | 28.24 | -0.81
2019-09-19 13:30 | 30.59 | -13.09
2019-09-19 14:00 | 27.92 | 1.05
2019-09-19 14:30 | 40.85 | 32.02
2019-09-19 15:00 | 53.22 | 47.29
2019-09-19 15:30 | 50.87 | 46.53
2019-09-19 16:00 | 51.86 | 47.78
2019-09-19 16:30 | 44.21 | 39.49
2019-09-19 17:00 | 92.27 | 78.81
2019-09-19 17:30 | 106.6 | 93.82
2019-09-19 18:00 | 117.82 | 105.7
2019-09-19 18:30 | 128.74 | 116.59
2019-09-19 19:00 | 133.46 | 122.34
2019-09-19 19:30 | 112.81 | 108.01
2019-09-19 20:00 | 110.54 | 106.63
2019-09-19 20:30 | 103.81 | 100.2
2019-09-19 21:00 | 48.68 | 47.32
2019-09-19 21:30 | 47.8 | 47.3
2019-09-19 22:00 | 54.79 | 53.92
2019-09-19 22:30 | 71.48 | 70.43
2019-09-19 23:00 | 81.02 | 79.78
2019-09-19 23:30 | 58.24 | 55.8
2019-09-20 | 31.3 | 26.19
2019-09-20 00:30 | 41.4 | 38.32
2019-09-20 01:00 | 44.51 | 43.58
2019-09-20 01:30 | 29.61 | 27.55
2019-09-20 02:00 | 22.41 | 19.79
2019-09-20 02:30 | 31.54 | 29.74
2019-09-20 03:00 | 31.12 | 29.3
2019-09-20 03:30 | 35.76 | 33.47
2019-09-20 04:00 | 28.06 | 25.73
2019-09-20 04:30 | 30.86 | 29.28
2019-09-20 05:00 | 45.97 | 45.07
2019-09-20 05:30 | 57.94 | 57.03
2019-09-20 06:00 | 74.83 | 74.15
2019-09-20 06:30 | 57.41 | 56.55
2019-09-20 07:00 | 55.98 | 55.22
2019-09-20 07:30 | 70.46 | 69.5
2019-09-20 08:00 | 53.56 | 52.88
2019-09-20 08:30 | 45.75 | 45.36
2019-09-20 09:00 | 32.76 | 32.65
2019-09-20 09:30 | 19.88 | 19.86
2019-09-20 10:00 | 14.76 | 14.75
2019-09-20 10:30 | 5.01 | -3.35
2019-09-20 11:00 | 28.96 | -28.48
2019-09-20 11:30 | 37.51 | -36.56
2019-09-20 12:00 | 38.11 | -36.28
2019-09-20 12:30 | 24.62 | 22.04
2019-09-20 13:00 | 41.9 | 40.39
2019-09-20 13:30 | 45.22 | 43.95
2019-09-20 14:00 | 49.12 | 48.07
2019-09-20 14:30 | 52.85 | 51.86
2019-09-20 15:00 | 54.72 | 54.14
2019-09-20 15:30 | 20.95 | -10.82
2019-09-20 16:00 | 53.22 | 34.92
2019-09-20 16:30 | 72.84 | 64.99
2019-09-20 17:00 | 88.12 | 82.15
2019-09-20 17:30 | 96.89 | 92.02
2019-09-20 18:00 | 106.17 | 101.53
2019-09-20 18:30 | 122.77 | 118.45
2019-09-20 19:00 | 123.64 | 119.66
2019-09-20 19:30 | 115.08 | 111.16
2019-09-20 20:00 | 107.87 | 104.25
2019-09-20 20:30 | 96.35 | 96.34
2019-09-20 21:00 | 79.92 | 79.59
2019-09-20 21:30 | 73.98 | 73.3
2019-09-20 22:00 | 81.35 | 80.48
2019-09-20 22:30 | 74.83 | 73.49
2019-09-20 23:00 | 79.05 | 77.51
2019-09-20 23:30 | 20.79 | 15.41
2019-09-21 | 43.81 | -42.58
2019-09-21 00:30 | 26.38 | 19.82
2019-09-21 01:00 | 24.72 | 17.66
2019-09-21 01:30 | 24.13 | 17.07
2019-09-21 02:00 | 22.54 | 18.43
2019-09-21 02:30 | 13.46 | 10.7
2019-09-21 03:00 | 16.89 | 12.3
2019-09-21 03:30 | 11.59 | 0.69
2019-09-21 04:00 | 19.24 | -16.52
2019-09-21 04:30 | 21.13 | -19.05
2019-09-21 05:00 | 16.43 | 10.57
2019-09-21 05:30 | 17.47 | 12.38
2019-09-21 06:00 | 19.46 | 15.9
2019-09-21 06:30 | 32.03 | 29.51
2019-09-21 07:00 | 25.51 | 22.04
2019-09-21 07:30 | 12.23 | -9.96
2019-09-21 08:00 | 6.94 | -4.93
2019-09-21 08:30 | 8.09 | -4.76
2019-09-21 09:00 | 26.29 | -26.05
2019-09-21 09:30 | 38.19 | -38.19
2019-09-21 10:00 | 41.98 | -41.98
2019-09-21 10:30 | 42.68 | -42.65
2019-09-21 11:00 | 39.52 | -39.46
2019-09-21 11:30 | 40.93 | -40.9
2019-09-21 12:00 | 40.34 | -40.33
2019-09-21 12:30 | 51.13 | -51.08
2019-09-21 13:00 | 45.01 | -45
2019-09-21 13:30 | 22.3 | -22.28
2019-09-21 14:00 | 45.27 | -45.27
2019-09-21 14:30 | 55.16 | -55.13
2019-09-21 15:00 | 34.08 | -34.06
2019-09-21 15:30 | 41.38 | -41.33
2019-09-21 16:00 | 36.16 | -36.09
2019-09-21 16:30 | 12.3 | -12.23
2019-09-21 17:00 | 58.25 | 58.22
2019-09-21 17:30 | 62.93 | 62.89
2019-09-21 18:00 | 73.68 | 73.62
2019-09-21 18:30 | 87.3 | 87.29
2019-09-21 19:00 | 94.01 | 93.98
2019-09-21 19:30 | 78.88 | 78.73
2019-09-21 20:00 | 69.94 | 69.79
2019-09-21 20:30 | 58.51 | 58.19
2019-09-21 21:00 | 50.48 | 49.9
2019-09-21 21:30 | 53.41 | 52.46
2019-09-21 22:00 | 15.31 | 12.12
2019-09-21 22:30 | 50.35 | 48.66
2019-09-21 23:00 | 47.64 | 45.3
2019-09-21 23:30 | 16.72 | -12.49
2019-09-22 | 35.81 | -33.86
2019-09-22 00:30 | 57.25 | -56.43
2019-09-22 01:00 | 57.58 | -56.88
2019-09-22 01:30 | 20.88 | -15.25
2019-09-22 02:00 | 27.41 | -23.93
2019-09-22 02:30 | 17.52 | -5.33
2019-09-22 03:00 | 12.38 | 5.24
2019-09-22 03:30 | 16.73 | 14.28
2019-09-22 04:00 | 21.76 | 19.79
2019-09-22 04:30 | 20.3 | 18.49
2019-09-22 05:00 | 31.72 | 30.39
2019-09-22 05:30 | 36.23 | 35.11
2019-09-22 06:00 | 33.74 | 32.51
2019-09-22 06:30 | 11.65 | 10.53
2019-09-22 07:00 | 7.13 | 5.14
2019-09-22 07:30 | 15.27 | -15.2
2019-09-22 08:00 | 30.8 | -29.63
2019-09-22 08:30 | 42.14 | -41.42
2019-09-22 09:00 | 42.96 | -42.66
2019-09-22 09:30 | 12.1 | -11.98
2019-09-22 10:00 | 12.26 | -12.23
2019-09-22 10:30 | 5.02 | -4.85
2019-09-22 11:00 | 19.43 | -19.33
2019-09-22 11:30 | 29.49 | -29.39
2019-09-22 12:00 | 32.9 | -32.84
2019-09-22 12:30 | 31.92 | -31.86
2019-09-22 13:00 | 35.92 | -35.9
2019-09-22 13:30 | 43.02 | -43.01
2019-09-22 14:00 | 50.99 | -50.98
2019-09-22 14:30 | 47.9 | -47.86
2019-09-22 15:00 | 37.13 | -37.1
2019-09-22 15:30 | 25.47 | -25.44
2019-09-22 16:00 | 17.56 | -17.49
2019-09-22 16:30 | 31.01 | 31
2019-09-22 17:00 | 82.55 | 82.55
2019-09-22 17:30 | 104.58 | 104.57
2019-09-22 18:00 | 119.3 | 119.3
2019-09-22 18:30 | 143.17 | 143.13
2019-09-22 19:00 | 139.31 | 139.3
2019-09-22 19:30 | 120.14 | 120.14
2019-09-22 20:00 | 111.31 | 111.26
2019-09-22 20:30 | 103.32 | 103.18
2019-09-22 21:00 | 89.37 | 89.1
2019-09-22 21:30 | 78.92 | 78.4
2019-09-22 22:00 | 60.7 | 59.76
2019-09-22 22:30 | 63.95 | 62.83
2019-09-22 23:00 | 66.71 | 65.38
2019-09-22 23:30 | 51.64 | 50.03
2019-09-23 | 33.59 | 30.8
2019-09-23 00:30 | 25.95 | 20.77
2019-09-23 01:00 | 16.38 | 1.65
2019-09-23 01:30 | 16.19 | -1.68
2019-09-23 02:00 | 18.07 | 8.09
2019-09-23 02:30 | 27.05 | 21.2
2019-09-23 03:00 | 23.24 | 15.83
2019-09-23 03:30 | 16.47 | 3.68
2019-09-23 04:00 | 18.63 | 10.91
2019-09-23 04:30 | 25.92 | 21.29
2019-09-23 05:00 | 29.86 | 25.58
2019-09-23 05:30 | 30.94 | 26.24
2019-09-23 06:00 | 44.97 | 42.17
2019-09-23 06:30 | 70.64 | 69.26
2019-09-23 07:00 | 50.81 | 49.57
2019-09-23 07:30 | 50.1 | 49.82
2019-09-23 08:00 | 42.97 | 42.95
2019-09-23 08:30 | 38.38 | 36.84
2019-09-23 09:00 | 39.28 | 30.56
2019-09-23 09:30 | 42.1 | 32.98
2019-09-23 10:00 | 32.96 | 14.84
2019-09-23 10:30 | 12.11 | -7.91
2019-09-23 11:00 | 17.12 | -15.55
2019-09-23 11:30 | 25.41 | -23.5
2019-09-23 12:00 | 11.5 | -8.04
2019-09-23 12:30 | 16.16 | -13.85
2019-09-23 13:00 | 11.17 | -10.64
2019-09-23 13:30 | 2.23 | 2.22
2019-09-23 14:00 | 24.06 | 24.04
2019-09-23 14:30 | 39.11 | 39.11
2019-09-23 15:00 | 64.94 | 64.93
2019-09-23 15:30 | 103.11 | 103.09
2019-09-23 16:00 | 130.36 | 130.3
2019-09-23 16:30 | 141.79 | 141.79
2019-09-23 17:00 | 152.53 | 152.37
2019-09-23 17:30 | 160.52 | 160.5
2019-09-23 18:00 | 160.52 | 160.22
2019-09-23 18:30 | 158.47 | 157.83
2019-09-23 19:00 | 147.28 | 146.93
2019-09-23 19:30 | 129.52 | 129.43
2019-09-23 20:00 | 116.61 | 116.59
2019-09-23 20:30 | 113.78 | 113.76
2019-09-23 21:00 | 96.33 | 96.21
2019-09-23 21:30 | 86.69 | 86.37
2019-09-23 22:00 | 73.97 | 73.27
2019-09-23 22:30 | 56.1 | 54.69
2019-09-23 23:00 | 67.3 | 65.83
2019-09-23 23:30 | 53.68 | 51.92
2019-09-24 | 41.59 | 38.76
2019-09-24 00:30 | 29.05 | 24.38
2019-09-24 01:00 | 20.64 | 11.5
2019-09-24 01:30 | 19.62 | 6.04
2019-09-24 02:00 | 19.1 | 3.24
2019-09-24 02:30 | 19.33 | 3.93
2019-09-24 03:00 | 21.37 | 9.73
2019-09-24 03:30 | 30.25 | 23.6
2019-09-24 04:00 | 31.08 | 24.57
2019-09-24 04:30 | 31.01 | 25.25
2019-09-24 05:00 | 25.28 | 17.41
2019-09-24 05:30 | 38.23 | 33.91
2019-09-24 06:00 | 39.47 | 35.32
2019-09-24 06:30 | 12.4 | 4.11
2019-09-24 07:00 | 37.1 | -35.9
2019-09-24 07:30 | 17.24 | 2.85
2019-09-24 08:00 | 121.49 | 120.78
2019-09-24 08:30 | 107.22 | 105.5
2019-09-24 09:00 | 102.99 | 99.64
2019-09-24 09:30 | 96.11 | 95.39
2019-09-24 10:00 | 93.98 | 92.63
2019-09-24 10:30 | 90.01 | 87.25
2019-09-24 11:00 | 63.07 | 45.33
2019-09-24 11:30 | 46.56 | 17.86
2019-09-24 12:00 | 58.03 | -36.2
2019-09-24 12:30 | 58.93 | -33.8
2019-09-24 13:00 | 50.15 | -24.42
2019-09-24 13:30 | 47.28 | -19.78
2019-09-24 14:00 | 40.78 | 12.05
2019-09-24 14:30 | 42.59 | 21.73
2019-09-24 15:00 | 56 | 43.99
2019-09-24 15:30 | 66.62 | 56.76
2019-09-24 16:00 | 72.93 | 65.46
2019-09-24 16:30 | 74.37 | 67.93
2019-09-24 17:00 | 102.51 | 98.04
2019-09-24 17:30 | 107.44 | 102.46
2019-09-24 18:00 | 118.72 | 113.46
2019-09-24 18:30 | 132.34 | 127.19
2019-09-24 19:00 | 149.85 | 145.65
2019-09-24 19:30 | 124.58 | 120.39
2019-09-24 20:00 | 112.1 | 108.03
2019-09-24 20:30 | 97.2 | 93.11
2019-09-24 21:00 | 74.64 | 74.28
2019-09-24 21:30 | 67.2 | 66.83
2019-09-24 22:00 | 65.58 | 65.11
2019-09-24 22:30 | 62.02 | 61.4
2019-09-24 23:00 | 62.08 | 61.36
2019-09-24 23:30 | 39.55 | 38.68
2019-09-25 | 11.06 | 8.43
2019-09-25 00:30 | 30.26 | 29.03
2019-09-25 01:00 | 18.82 | 16.26
2019-09-25 01:30 | 9.38 | 1.94
2019-09-25 02:00 | 8.61 | 1.49
2019-09-25 02:30 | 8.01 | 0.94
2019-09-25 03:00 | 11.67 | 7.93
2019-09-25 03:30 | 19.6 | 17.3
2019-09-25 04:00 | 13.67 | 10.33
2019-09-25 04:30 | 16.62 | 14.16
2019-09-25 05:00 | 23.24 | 21.87
2019-09-25 05:30 | 40.52 | 39.48
2019-09-25 06:00 | 37.92 | 36.74
2019-09-25 06:30 | 41.22 | 40.47
2019-09-25 07:00 | 41.29 | 41.04
2019-09-25 07:30 | 44.49 | 44.49
2019-09-25 08:00 | 113.05 | 113
2019-09-25 08:30 | 49.38 | 49.03
2019-09-25 09:00 | 37.57 | 37.23
2019-09-25 09:30 | 116.93 | 116.9
2019-09-25 10:00 | 120.29 | 120.24
2019-09-25 10:30 | 87.17 | 86.91
2019-09-25 11:00 | 11.78 | -1.25
2019-09-25 11:30 | 29.77 | -9.68
2019-09-25 12:00 | 24.91 | 0.36
2019-09-25 12:30 | 42.59 | 32.83
2019-09-25 13:00 | 41.61 | 35.07
2019-09-25 13:30 | 23.03 | -5.07
2019-09-25 14:00 | 35.62 | 25.58
2019-09-25 14:30 | 43.04 | 34.4
2019-09-25 15:00 | 64.85 | 58.42
2019-09-25 15:30 | 84.27 | 79.65
2019-09-25 16:00 | 93.23 | 89.39
2019-09-25 16:30 | 85.11 | 81.8
2019-09-25 17:00 | 97.99 | 81.23
2019-09-25 17:30 | 94.59 | 78.02
2019-09-25 18:00 | 102.94 | 87.51
2019-09-25 18:30 | 95.58 | 77.23
2019-09-25 19:00 | 115.19 | 100.73
2019-09-25 19:30 | 89.84 | 71.58
2019-09-25 20:00 | 82.19 | 71.51
2019-09-25 20:30 | 33.12 | 3.46
2019-09-25 21:00 | 30.79 | 26.32
2019-09-25 21:30 | 6.06 | -6.05
2019-09-25 22:00 | 30.78 | -30.77
2019-09-25 22:30 | 13.51 | 12.98
2019-09-25 23:00 | 30.95 | -30.94
2019-09-25 23:30 | 26.64 | -26.62
2019-09-26 | 46.3 | -46.24
2019-09-26 00:30 | 58.32 | -58.14
2019-09-26 01:00 | 34.19 | -34.1
2019-09-26 01:30 | 65.07 | -65.07
2019-09-26 02:00 | 63.85 | -63.84
2019-09-26 02:30 | 60.4 | -60.39
2019-09-26 03:00 | 55.97 | -55.97
2019-09-26 03:30 | 39.18 | -39.04
2019-09-26 04:00 | 48.18 | -48.13
2019-09-26 04:30 | 32.93 | -32.57
2019-09-26 05:00 | 30.62 | -30.05
2019-09-26 05:30 | 9.21 | -4.66
2019-09-26 06:00 | 11.25 | 7.65
2019-09-26 06:30 | 26.1 | 24.75
2019-09-26 07:00 | 41.49 | 41.01
2019-09-26 07:30 | 50.63 | 50.55
2019-09-26 08:00 | 53.34 | 53.34
2019-09-26 08:30 | 62.63 | 61.75
2019-09-26 09:00 | 59.65 | 59.62
2019-09-26 09:30 | 67.3 | 67.15
2019-09-26 10:00 | 86.55 | 86.55
2019-09-26 10:30 | 65.62 | 65.59
2019-09-26 11:00 | 39.51 | 39.38
2019-09-26 11:30 | 44.95 | 44.88
2019-09-26 12:00 | 49.3 | 49.27
2019-09-26 12:30 | 51.88 | 51.84
2019-09-26 13:00 | 47.4 | 47.33
2019-09-26 13:30 | 48.63 | 48.47
2019-09-26 14:00 | 62.06 | 61.86
2019-09-26 14:30 | 49.87 | 49.79
2019-09-26 15:00 | 49.45 | 49.39
2019-09-26 15:30 | 50.04 | 49.96
2019-09-26 16:00 | 71.65 | 71.46
2019-09-26 16:30 | 69.8 | 69.08
2019-09-26 17:00 | 75.44 | 74.96
2019-09-26 17:30 | 96.28 | 96.13
2019-09-26 18:00 | 94.07 | 93.9
2019-09-26 18:30 | 98.79 | 98.18
2019-09-26 19:00 | 95.21 | 93.39
2019-09-26 19:30 | 81.8 | 79.64
2019-09-26 20:00 | 81.94 | 80.15
2019-09-26 20:30 | 76.56 | 75.03
2019-09-26 21:00 | 61.2 | 61.08
2019-09-26 21:30 | 53.6 | 53.55
2019-09-26 22:00 | 43.74 | 43.55
2019-09-26 22:30 | 43.06 | 42.79
2019-09-26 23:00 | 49.46 | 48.99
2019-09-26 23:30 | 30.06 | 29.52
2019-09-27 | 15.07 | 12.64
2019-09-27 00:30 | 12.67 | 6.51
2019-09-27 01:00 | 14.89 | -11.74
2019-09-27 01:30 | 8.84 | -1.4
2019-09-27 02:00 | 8.39 | 1.4
2019-09-27 02:30 | 8.57 | 7.12
2019-09-27 03:00 | 3.84 | 1.94
2019-09-27 03:30 | 3.18 | -0.61
2019-09-27 04:00 | 6.51 | 5.79
2019-09-27 04:30 | 9.7 | 9.57
2019-09-27 05:00 | 21.09 | 21.08
2019-09-27 05:30 | 18.82 | 18.56
2019-09-27 06:00 | 24.09 | 23.94
2019-09-27 06:30 | 23.03 | 22.51
2019-09-27 07:00 | 46.33 | 46.06
2019-09-27 07:30 | 56.95 | 56.89
2019-09-27 08:00 | 48.68 | 48.68
2019-09-27 08:30 | 44.66 | 44.45
2019-09-27 09:00 | 29.3 | 28.42
2019-09-27 09:30 | 24.08 | 22.37
2019-09-27 10:00 | 22.88 | 20.06
2019-09-27 10:30 | 27.08 | -22.11
2019-09-27 11:00 | 48.37 | -41.9
2019-09-27 11:30 | 43.31 | -30.64
2019-09-27 12:00 | 23.73 | -8.21
2019-09-27 12:30 | 26.26 | -13.57
2019-09-27 13:00 | 26.03 | -15.38
2019-09-27 13:30 | 20.09 | 10.95
2019-09-27 14:00 | 25.87 | 24.14
2019-09-27 14:30 | 21.42 | 19.83
2019-09-27 15:00 | 22.01 | 20.9
2019-09-27 15:30 | 56.82 | 56.67
2019-09-27 16:00 | 75.99 | 75.9
2019-09-27 16:30 | 87.46 | 87.41
2019-09-27 17:00 | 95.69 | 95.68
2019-09-27 17:30 | 97.69 | 97.68
2019-09-27 18:00 | 53.04 | 52.49
2019-09-27 18:30 | 21.3 | -2.22
2019-09-27 19:00 | 27.28 | 18.75
2019-09-27 19:30 | 23.43 | 11.81
2019-09-27 20:00 | 54.17 | 53.76
2019-09-27 20:30 | 80.36 | 80.3
2019-09-27 21:00 | 54.53 | 54.38
2019-09-27 21:30 | 36.37 | 35.86
2019-09-27 22:00 | 26.95 | -26.94
2019-09-27 22:30 | 22.01 | -21.96
2019-09-27 23:00 | 19.96 | -19.71
2019-09-27 23:30 | 45.17 | -44.69
2019-09-28 | 37.67 | -37.35
2019-09-28 00:30 | 7.08 | 3.08
2019-09-28 01:00 | 6.58 | 1.83
2019-09-28 01:30 | 11.29 | -6.9
2019-09-28 02:00 | 20.09 | -17.69
2019-09-28 02:30 | 24.57 | -22.05
2019-09-28 03:00 | 28.64 | -26.01
2019-09-28 03:30 | 16.52 | -9.17
2019-09-28 04:00 | 26.57 | -3.78
2019-09-28 04:30 | 26.24 | -2.17
2019-09-28 05:00 | 25.45 | -1.17
2019-09-28 05:30 | 25.22 | -5.6
2019-09-28 06:00 | 27.8 | -7.25
2019-09-28 06:30 | 57.74 | -46.61
2019-09-28 07:00 | 51.45 | -39.27
2019-09-28 07:30 | 61.35 | -51.94
2019-09-28 08:00 | 56.49 | -50.41
2019-09-28 08:30 | 47.81 | -45.82
2019-09-28 09:00 | 38.3 | -35.91
2019-09-28 09:30 | 45.16 | -42.78
2019-09-28 10:00 | 44.62 | -42.68
2019-09-28 10:30 | 43.24 | -41.71
2019-09-28 11:00 | 45.9 | -44.55
2019-09-28 11:30 | 37.14 | -35.98
2019-09-28 12:00 | 38.59 | -37.72
2019-09-28 12:30 | 43.86 | -43.33
2019-09-28 13:00 | 24.04 | -23.97
2019-09-28 13:30 | 30.39 | 30.03
2019-09-28 14:00 | 39.08 | 37.92
2019-09-28 14:30 | 23.64 | 22.87
2019-09-28 15:00 | 31.74 | 31.33
2019-09-28 15:30 | 17.54 | 16
2019-09-28 16:00 | 20.76 | -18.41
2019-09-28 16:30 | 24.4 | -22.32
2019-09-28 17:00 | 20.68 | -17.24
2019-09-28 17:30 | 12.74 | 8.83
2019-09-28 18:00 | 10.29 | 4.36
2019-09-28 18:30 | 12.18 | -0.07
2019-09-28 19:00 | 33.27 | -16.19
2019-09-28 19:30 | 35.41 | -19.19
2019-09-28 20:00 | 33.34 | -19.54
2019-09-28 20:30 | 30.82 | -20.62
2019-09-28 21:00 | 32.35 | -25.55
2019-09-28 21:30 | 35.18 | -30.3
2019-09-28 22:00 | 42.82 | -39.71
2019-09-28 22:30 | 34.37 | -34.35
2019-09-28 23:00 | 29.13 | -29.08
2019-09-28 23:30 | 41.44 | -41.43
2019-09-29 | 52.87 | -52.86
2019-09-29 00:30 | 56.95 | -56.27
2019-09-29 01:00 | 63.47 | -60.34
2019-09-29 01:30 | 64.02 | -60.65
2019-09-29 02:00 | 63.04 | -59.42
2019-09-29 02:30 | 46.86 | -44.32
2019-09-29 03:00 | 40.71 | -39.42
2019-09-29 03:30 | 25.96 | -24.58
2019-09-29 04:00 | 23.33 | -22.13
2019-09-29 04:30 | 23.74 | -22.4
2019-09-29 05:00 | 12.74 | -11.21
2019-09-29 05:30 | 12.31 | -9.09
2019-09-29 06:00 | 28.14 | -5.56
2019-09-29 06:30 | 36.67 | -22.72
2019-09-29 07:00 | 63.56 | -54.3
2019-09-29 07:30 | 61.17 | -53.77
2019-09-29 08:00 | 60.67 | -54.18
2019-09-29 08:30 | 50.64 | -50.62
2019-09-29 09:00 | 45.56 | -44.68
2019-09-29 09:30 | 45.04 | -44.52
2019-09-29 10:00 | 45.94 | -45.88
2019-09-29 10:30 | 50.17 | -50.16
2019-09-29 11:00 | 53.12 | -53.11
2019-09-29 11:30 | 50.52 | -50.51
2019-09-29 12:00 | 53.12 | -53.12
2019-09-29 12:30 | 53.63 | -53.63
2019-09-29 13:00 | 53.4 | -53.39
2019-09-29 13:30 | 53.64 | -53.63
2019-09-29 14:00 | 53.86 | -53.85
2019-09-29 14:30 | 33.33 | -33.25
2019-09-29 15:00 | 7.21 | -5.5
2019-09-29 15:30 | 5.02 | 0.08
2019-09-29 16:00 | 5.13 | -2.72
2019-09-29 16:30 | 29.07 | -29.07
2019-09-29 17:00 | 42.41 | 42.36
2019-09-29 17:30 | 14.72 | 14.64
2019-09-29 18:00 | 62.34 | 62.34
2019-09-29 18:30 | 82.46 | 82.38
2019-09-29 19:00 | 75.46 | 75.44
2019-09-29 19:30 | 9.58 | 8.82
2019-09-29 20:00 | 21.38 | -20.56
2019-09-29 20:30 | 20.99 | -20.55
2019-09-29 21:00 | 25.73 | -25.54
2019-09-29 21:30 | 31.96 | -31.9
2019-09-29 22:00 | 40.13 | -40.1
2019-09-29 22:30 | 37.14 | -37.11
2019-09-29 23:00 | 28.7 | -28.63
2019-09-29 23:30 | 46.46 | -44.29
2019-09-30 | 54.45 | -51.74
2019-09-30 00:30 | 38.41 | -35.5
2019-09-30 01:00 | 46.5 | -44.48
2019-09-30 01:30 | 52.59 | -51.02
2019-09-30 02:00 | 53.31 | -51.33
2019-09-30 02:30 | 40.25 | -29.61
2019-09-30 03:00 | 37.85 | -26.62
2019-09-30 03:30 | 59.18 | -48.83
2019-09-30 04:00 | 62.9 | -52.61
2019-09-30 04:30 | 54.96 | -44.78
2019-09-30 05:00 | 36.73 | -26.05
2019-09-30 05:30 | 23.87 | -2.53
2019-09-30 06:00 | 30.29 | 19.49
2019-09-30 06:30 | 28.85 | 20.14
2019-09-30 07:00 | 39.77 | 39.75
2019-09-30 07:30 | 47.39 | 47.38
2019-09-30 08:00 | 45.66 | 45.58
2019-09-30 08:30 | 37.63 | 37.31
2019-09-30 09:00 | 24.9 | 22.98
2019-09-30 09:30 | 25.55 | -19.96
2019-09-30 10:00 | 24.92 | 22.75
2019-09-30 10:30 | 18.89 | 16.28
2019-09-30 11:00 | 14.7 | 10.41
2019-09-30 11:30 | 22.12 | -16.94
2019-09-30 12:00 | 13.07 | -3.51
2019-09-30 12:30 | 12.04 | 3.78
2019-09-30 13:00 | 12.76 | 7.42
2019-09-30 13:30 | 19.66 | 17.11
2019-09-30 14:00 | 23.17 | 21.19
2019-09-30 14:30 | 33.18 | 32
2019-09-30 15:00 | 55.79 | 55.3
2019-09-30 15:30 | 78.18 | 77.83
2019-09-30 16:00 | 83.22 | 82.97
2019-09-30 16:30 | 87.89 | 87.79
2019-09-30 17:00 | 101.37 | 101.29
2019-09-30 17:30 | 92.69 | 92.5
2019-09-30 18:00 | 90.45 | 90.07
2019-09-30 18:30 | 106.31 | 105.5
2019-09-30 19:00 | 50.28 | 45.31
2019-09-30 19:30 | 31.27 | -3.78
2019-09-30 20:00 | 30.15 | 0.02
2019-09-30 20:30 | 30.32 | -7.12
2019-09-30 21:00 | 32.28 | -14.79
2019-09-30 21:30 | 27.74 | -12.82
2019-09-30 22:00 | 31.3 | -29.47
2019-09-30 22:30 | 27.28 | -26.97
2019-09-30 23:00 | 25.97 | -25.78
2019-09-30 23:30 | 38.57 | -38.38
2019-10-01 | 46.81 | -46.6
2019-10-01 00:30 | 50.45 | -50.1
2019-10-01 01:00 | 54 | -53.6
2019-10-01 01:30 | 54.88 | -54.44
2019-10-01 02:00 | 51.76 | -51.58
2019-10-01 02:30 | 39.76 | -39.74
2019-10-01 03:00 | 48.72 | -48.69
2019-10-01 03:30 | 48.78 | -48.74
2019-10-01 04:00 | 35.97 | -35.93
2019-10-01 04:30 | 39.69 | -39.68
2019-10-01 05:00 | 47.1 | -47.1
2019-10-01 05:30 | 33.63 | -33.5
2019-10-01 06:00 | 4.93 | -2.03
2019-10-01 06:30 | 19.35 | 18.84
2019-10-01 07:00 | 16.96 | -16.91
2019-10-01 07:30 | 41.88 | 41.85
2019-10-01 08:00 | 57.69 | 57.68
2019-10-01 08:30 | 57.47 | 57.38
2019-10-01 09:00 | 16.32 | 10.15
2019-10-01 09:30 | 39.27 | -23.17
2019-10-01 10:00 | 35.99 | -16.71
2019-10-01 10:30 | 33.53 | -10.37
2019-10-01 11:00 | 32.58 | 2.99
2019-10-01 11:30 | 33.17 | 7.86
2019-10-01 12:00 | 31.96 | -1.48
2019-10-01 12:30 | 52.21 | -40.55
2019-10-01 13:00 | 43.15 | -29.24
2019-10-01 13:30 | 31.51 | 8.67
2019-10-01 14:00 | 34.11 | -13.25
2019-10-01 14:30 | 31.3 | -5.96
2019-10-01 15:00 | 37.93 | -21.95
2019-10-01 15:30 | 29.22 | -0.36
2019-10-01 16:00 | 59.24 | 53.79
2019-10-01 16:30 | 60.53 | 55.96
2019-10-01 17:00 | 51.53 | 33.94
2019-10-01 17:30 | 59.12 | -11.71
2019-10-01 18:00 | 58.87 | -9.94
2019-10-01 18:30 | 61.75 | -6.66
2019-10-01 19:00 | 60.65 | -3.26
2019-10-01 19:30 | 57.68 | 0.54
2019-10-01 20:00 | 57.21 | -0.06
2019-10-01 20:30 | 31.36 | -6.53
2019-10-01 21:00 | 25.78 | -13.3
2019-10-01 21:30 | 28.53 | -20.74
2019-10-01 22:00 | 34.58 | -30.03
2019-10-01 22:30 | 25.44 | -21.71
2019-10-01 23:00 | 28.98 | -26.82
2019-10-01 23:30 | 44.4 | -43.09
2019-10-02 | 55.95 | -54.66
2019-10-02 00:30 | 61.1 | -60.55
2019-10-02 01:00 | 63.41 | -63.32
2019-10-02 01:30 | 64.2 | -64.07
2019-10-02 02:00 | 61.67 | -61.56
2019-10-02 02:30 | 60.95 | -60.85
2019-10-02 03:00 | 60.81 | -60.69
2019-10-02 03:30 | 58.94 | -58.84
2019-10-02 04:00 | 52.96 | -52.91
2019-10-02 04:30 | 10.53 | -8.48
2019-10-02 05:00 | 19.63 | 17.19
2019-10-02 05:30 | 17.94 | 13.62
2019-10-02 06:00 | 20.5 | -18.88
2019-10-02 06:30 | 42.49 | -42.48
2019-10-02 07:00 | 27.8 | -27.79
2019-10-02 07:30 | 38.95 | 38.87
2019-10-02 08:00 | 11.45 | 11.38
2019-10-02 08:30 | 7.45 | -3.8
2019-10-02 09:00 | 23.1 | -20.82
2019-10-02 09:30 | 21.22 | -18.63
2019-10-02 10:00 | 34.25 | -32.3
2019-10-02 10:30 | 35.77 | -33.6
2019-10-02 11:00 | 36.46 | -34.34
2019-10-02 11:30 | 43.6 | -41.61
2019-10-02 12:00 | 51.2 | -49.37
2019-10-02 12:30 | 37.94 | -35.66
2019-10-02 13:00 | 48.2 | -46.26
2019-10-02 13:30 | 44.02 | -41.83
2019-10-02 14:00 | 41.37 | -38.93
2019-10-02 14:30 | 39.1 | -36.66
2019-10-02 15:00 | 38.18 | -35.9
2019-10-02 15:30 | 31.82 | -29.46
2019-10-02 16:00 | 32.57 | 31.47
2019-10-02 16:30 | 46.5 | 46
2019-10-02 17:00 | 62.14 | 60.98
2019-10-02 17:30 | 59.15 | 20.4
2019-10-02 18:00 | 59.82 | -14.66
2019-10-02 18:30 | 61.27 | -10.2
2019-10-02 19:00 | 61.3 | -0.96
2019-10-02 19:30 | 54.5 | 2.41
2019-10-02 20:00 | 80.94 | 80.09
2019-10-02 20:30 | 76.49 | 76.45
2019-10-02 21:00 | 81 | 80.91
2019-10-02 21:30 | 66.29 | 66.04
2019-10-02 22:00 | 52.66 | 52
2019-10-02 22:30 | 48.38 | 47.64
2019-10-02 23:00 | 35.46 | 34.41
2019-10-02 23:30 | 29.33 | -29.19
2019-10-03 | 46.29 | -46.27
2019-10-03 00:30 | 50.79 | -50.78
2019-10-03 01:00 | 53.7 | -53.64
2019-10-03 01:30 | 54.28 | -54.18
2019-10-03 02:00 | 46.78 | -46.76
2019-10-03 02:30 | 29.84 | -29.72
2019-10-03 03:00 | 28.06 | -26.26
2019-10-03 03:30 | 35.29 | -32.38
2019-10-03 04:00 | 30.14 | -27.03
2019-10-03 04:30 | 19.82 | -16.72
2019-10-03 05:00 | 8.98 | -3.15
2019-10-03 05:30 | 7.48 | -1.85
2019-10-03 06:00 | 6.9 | 1.72
2019-10-03 06:30 | 19.48 | 19.05
2019-10-03 07:00 | 21.68 | 21.27
2019-10-03 07:30 | 6.54 | 4.63
2019-10-03 08:00 | 24.82 | -23.64
2019-10-03 08:30 | 24.44 | -22.86
2019-10-03 09:00 | 10.42 | 6.26
2019-10-03 09:30 | 11.52 | 7.04
2019-10-03 10:00 | 11.25 | 5.48
2019-10-03 10:30 | 11.41 | -3.8
2019-10-03 11:00 | 12.17 | -2.61
2019-10-03 11:30 | 23.7 | -19.72
2019-10-03 12:00 | 37.57 | -34.73
2019-10-03 12:30 | 41.43 | -38.34
2019-10-03 13:00 | 40.15 | -36.78
2019-10-03 13:30 | 36.59 | -32.73
2019-10-03 14:00 | 37.71 | -27.58
2019-10-03 14:30 | 34.13 | 8.71
2019-10-03 15:00 | 32.73 | 11.18
2019-10-03 15:30 | 31.46 | 2.71
2019-10-03 16:00 | 48.11 | 38.93
2019-10-03 16:30 | 56.58 | 49.3
2019-10-03 17:00 | 65.52 | 60.13
2019-10-03 17:30 | 30.84 | -12.32
2019-10-03 18:00 | 40.04 | -13.48
2019-10-03 18:30 | 64.24 | -6.63
2019-10-03 19:00 | 63.85 | 9.57
2019-10-03 19:30 | 59.2 | 27.3
2019-10-03 20:00 | 68.72 | 68.66
2019-10-03 20:30 | 66.7 | 66.67
2019-10-03 21:00 | 80.75 | 80.72
2019-10-03 21:30 | 66.42 | 66.29
2019-10-03 22:00 | 0.9 | -0.32
2019-10-03 22:30 | 22.87 | -22.65
2019-10-03 23:00 | 3.2 | 2.91
2019-10-03 23:30 | 15.45 | -15.27
2019-10-04 | 44.4 | -44.39
2019-10-04 00:30 | 45.46 | -45.45
2019-10-04 01:00 | 34.11 | -34.07
2019-10-04 01:30 | 20.04 | -19.63
2019-10-04 02:00 | 11.59 | -10.36
2019-10-04 02:30 | 20.57 | -20.15
2019-10-04 03:00 | 4.86 | -1.55
2019-10-04 03:30 | 3.08 | 1.18
2019-10-04 04:00 | 10.87 | 10.62
2019-10-04 04:30 | 16.12 | 16.08
2019-10-04 05:00 | 19.87 | 19.86
2019-10-04 05:30 | 14.56 | 14.54
2019-10-04 06:00 | 19.12 | 19.07
2019-10-04 06:30 | 21.92 | 21.92
2019-10-04 07:00 | 27.32 | 27.22
2019-10-04 07:30 | 28.9 | 28.61
2019-10-04 08:00 | 20.01 | 19.61
2019-10-04 08:30 | 20.56 | -18.54
2019-10-04 09:00 | 27.55 | -25.17
2019-10-04 09:30 | 22.53 | -18.67
2019-10-04 10:00 | 33.52 | -30.4
2019-10-04 10:30 | 49.66 | -38.15
2019-10-04 11:00 | 61.26 | -37.16
2019-10-04 11:30 | 62.84 | -39.55
2019-10-04 12:00 | 61.56 | -37.65
2019-10-04 12:30 | 60.51 | -37.46
2019-10-04 13:00 | 59.48 | -35.77
2019-10-04 13:30 | 59.24 | -35.8
2019-10-04 14:00 | 55.16 | -29.24
2019-10-04 14:30 | 54.37 | -29.65
2019-10-04 15:00 | 52.89 | -28.11
2019-10-04 15:30 | 51.68 | -26.61
2019-10-04 16:00 | 42.53 | -7.15
2019-10-04 16:30 | 44.8 | 19.84
2019-10-04 17:00 | 43.66 | 18.15
2019-10-04 17:30 | 43.63 | -18.88
2019-10-04 18:00 | 35.72 | 4.21
2019-10-04 18:30 | 43.53 | -16.49
2019-10-04 19:00 | 74.86 | 65.44
2019-10-04 19:30 | 55.87 | 44.65
2019-10-04 20:00 | 33.16 | -5.65
2019-10-04 20:30 | 35.13 | -14.74
2019-10-04 21:00 | 48.31 | 48.31
2019-10-04 21:30 | 11.12 | 10.05
2019-10-04 22:00 | 34.38 | -34.19
2019-10-04 22:30 | 12.17 | -11.77
2019-10-04 23:00 | 12.24 | -11.74
2019-10-04 23:30 | 44.04 | -44.03
2019-10-05 | 55.37 | -55.34
2019-10-05 00:30 | 60.17 | -60
2019-10-05 01:00 | 63.91 | -63.61
2019-10-05 01:30 | 34.53 | -34.53
2019-10-05 02:00 | 16.32 | -15.87
2019-10-05 02:30 | 6.03 | -5.64
2019-10-05 03:00 | 12.42 | -12.12
2019-10-05 03:30 | 3.61 | 3.12
2019-10-05 04:00 | 4.78 | -4.2
2019-10-05 04:30 | 13.65 | 13.58
2019-10-05 05:00 | 12.97 | 12.91
2019-10-05 05:30 | 17.27 | 17.14
2019-10-05 06:00 | 11.88 | 11.29
2019-10-05 06:30 | 28.32 | -26.77
2019-10-05 07:00 | 57.22 | -54.78
2019-10-05 07:30 | 55.08 | -53.24
2019-10-05 08:00 | 53.52 | -52.11
2019-10-05 08:30 | 52.25 | -49.68
2019-10-05 09:00 | 48.97 | -45.62
2019-10-05 09:30 | 48.88 | -45.7
2019-10-05 10:00 | 50.03 | -46.99
2019-10-05 10:30 | 51.56 | -48.41
2019-10-05 11:00 | 51.35 | -48.49
2019-10-05 11:30 | 49.18 | -48.22
2019-10-05 12:00 | 42.29 | -41.43
2019-10-05 12:30 | 47.87 | -47.13
2019-10-05 13:00 | 46.22 | -45.5
2019-10-05 13:30 | 42.98 | -42.37
2019-10-05 14:00 | 37.15 | -36.5
2019-10-05 14:30 | 34.69 | -34.05
2019-10-05 15:00 | 29.17 | -28.74
2019-10-05 15:30 | 50.08 | -49.68
2019-10-05 16:00 | 36.98 | -36.35
2019-10-05 16:30 | 30.42 | -28.35
2019-10-05 17:00 | 33.68 | 4.92
2019-10-05 17:30 | 59.09 | 57.95
2019-10-05 18:00 | 61.86 | 61.32
2019-10-05 18:30 | 88.04 | 87.49
2019-10-05 19:00 | 90.93 | 90.51
2019-10-05 19:30 | 65.34 | 64.38
2019-10-05 20:00 | 49.55 | 48.28
2019-10-05 20:30 | 46.28 | 45.35
2019-10-05 21:00 | 32.49 | 31.62
2019-10-05 21:30 | 26.69 | 26.01
2019-10-05 22:00 | 20.71 | 20.35
2019-10-05 22:30 | 15.65 | 15.41
2019-10-05 23:00 | 23.74 | 23.68
2019-10-05 23:30 | 2.07 | 1.81
2019-10-06 | 42.51 | -42.37
2019-10-06 00:30 | 4.92 | -4.8
2019-10-06 01:00 | 9.6 | 9.58
2019-10-06 01:30 | 23.04 | 23.01
2019-10-06 02:00 | 9.01 | 8.88
2019-10-06 02:30 | 6.1 | 5.93
2019-10-06 03:00 | 4.74 | 4.66
2019-10-06 03:30 | 3.33 | 3.3
2019-10-06 04:00 | 4.6 | 4.59
2019-10-06 04:30 | 11.09 | 11.08
2019-10-06 05:00 | 12.11 | 12.11
2019-10-06 05:30 | 13.22 | 13.22
2019-10-06 06:00 | 20.12 | 20.11
2019-10-06 06:30 | 11.15 | 11.12
2019-10-06 07:00 | 16.23 | -16.09
2019-10-06 07:30 | 59.16 | -58.77
2019-10-06 08:00 | 51.71 | -51.32
2019-10-06 08:30 | 54.68 | -54.16
2019-10-06 09:00 | 20.76 | -19.6
2019-10-06 09:30 | 58.71 | -57.47
2019-10-06 10:00 | 15.81 | -11.89
2019-10-06 10:30 | 17.88 | -13.98
2019-10-06 11:00 | 59.9 | -58.17
2019-10-06 11:30 | 57.2 | -55.16
2019-10-06 12:00 | 61.32 | -59.37
2019-10-06 12:30 | 24.3 | -20.19
2019-10-06 13:00 | 58.99 | -57.03
2019-10-06 13:30 | 55.46 | -53.29
2019-10-06 14:00 | 25.87 | -22.28
2019-10-06 14:30 | 14.2 | -6.07
2019-10-06 15:00 | 28.01 | -24.3
2019-10-06 15:30 | 40.93 | -22.19
2019-10-06 16:00 | 38.08 | 17.23
2019-10-06 16:30 | 48.33 | -31.1
2019-10-06 17:00 | 42.11 | 24.8
2019-10-06 17:30 | 62.84 | 54.1
2019-10-06 18:00 | 84.76 | 78.44
2019-10-06 18:30 | 106.86 | 101.03
2019-10-06 19:00 | 107.91 | 103.71
2019-10-06 19:30 | 103.49 | 102.44
2019-10-06 20:00 | 89.91 | 88.84
2019-10-06 20:30 | 84.72 | 83.82
2019-10-06 21:00 | 63.6 | 62.59
2019-10-06 21:30 | 39.48 | 38.27
2019-10-06 22:00 | 26.43 | 25.13
2019-10-06 22:30 | 29.76 | 28.88
2019-10-06 23:00 | 25.6 | 24.81
2019-10-06 23:30 | 4.74 | -0.4
2019-10-07 | 25.47 | -24.52
2019-10-07 00:30 | 12.5 | -10.12
2019-10-07 01:00 | 10.07 | -8.05
2019-10-07 01:30 | 10.09 | -0.08
2019-10-07 02:00 | 39.23 | -38.76
2019-10-07 02:30 | 48.58 | -48.39
2019-10-07 03:00 | 21.41 | -20.09
2019-10-07 03:30 | 4.9 | -0.97
2019-10-07 04:00 | 4.9 | -3.09
2019-10-07 04:30 | 3.46 | -0.91
2019-10-07 05:00 | 2.84 | -1
2019-10-07 05:30 | 5.09 | -2.29
2019-10-07 06:00 | 8.97 | -6.32
2019-10-07 06:30 | 14.86 | -13.98
2019-10-07 07:00 | 54.34 | -52.36
2019-10-07 07:30 | 50.66 | -49.95
2019-10-07 08:00 | 45.05 | -45
2019-10-07 08:30 | 40.32 | -40.29
2019-10-07 09:00 | 39.18 | -39.17
2019-10-07 09:30 | 40.59 | -40.47
2019-10-07 10:00 | 38.42 | -38.09
2019-10-07 10:30 | 36.14 | -35.27
2019-10-07 11:00 | 42.31 | -41.23
2019-10-07 11:30 | 40.59 | -39.29
2019-10-07 12:00 | 40.01 | -38.44
2019-10-07 12:30 | 37.84 | -36.35
2019-10-07 13:00 | 35 | -33.18
2019-10-07 13:30 | 20.54 | -14.25
2019-10-07 14:00 | 29.77 | 3.92
2019-10-07 14:30 | 45.58 | 35.05
2019-10-07 15:00 | 48.27 | 37.09
2019-10-07 15:30 | 72.53 | 65.59
2019-10-07 16:00 | 79.16 | 74.54
2019-10-07 16:30 | 91.85 | 91.2
2019-10-07 17:00 | 123.98 | 123.52
2019-10-07 17:30 | 154.13 | 153.66
2019-10-07 18:00 | 173.66 | 173.08
2019-10-07 18:30 | 178.2 | 177.49
2019-10-07 19:00 | 174.65 | 174.13
2019-10-07 19:30 | 143.08 | 143.07
2019-10-07 20:00 | 118.99 | 118.98
2019-10-07 20:30 | 106.35 | 106.35
2019-10-07 21:00 | 61.09 | 61.05
2019-10-07 21:30 | 16.84 | -16.77
2019-10-07 22:00 | 25.6 | -25.59
2019-10-07 22:30 | 3.13 | -0.45
2019-10-07 23:00 | 30.7 | 29.96
2019-10-07 23:30 | 8.8 | -8.22
2019-10-08 | 57.06 | -57.01
2019-10-08 00:30 | 37.37 | -37.37
2019-10-08 01:00 | 25.64 | -25.21
2019-10-08 01:30 | 8.02 | -4.22
2019-10-08 02:00 | 10.98 | 8.27
2019-10-08 02:30 | 12.56 | 9.5
2019-10-08 03:00 | 9.78 | -1.61
2019-10-08 03:30 | 10.22 | -2.49
2019-10-08 04:00 | 13.04 | -8.11
2019-10-08 04:30 | 13.51 | -8.97
2019-10-08 05:00 | 14.4 | -9.78
2019-10-08 05:30 | 13.11 | 7.08
2019-10-08 06:00 | 27.76 | 25.04
2019-10-08 06:30 | 38.69 | 37.77
2019-10-08 07:00 | 35.25 | 35.17
2019-10-08 07:30 | 16.23 | 14.24
2019-10-08 08:00 | 37.39 | -23.62
2019-10-08 08:30 | 40.41 | -23.3
2019-10-08 09:00 | 42.96 | -22.09
2019-10-08 09:30 | 55.88 | -8.38
2019-10-08 10:00 | 93.41 | -6.33
2019-10-08 10:30 | 121.51 | 81.09
2019-10-08 11:00 | 141.1 | 107.81
2019-10-08 11:30 | 141.13 | 119.07
2019-10-08 12:00 | 130.83 | 109.93
2019-10-08 12:30 | 168.91 | 153.13
2019-10-08 13:00 | 200.39 | 188.36
2019-10-08 13:30 | 213.38 | 202.84
2019-10-08 14:00 | 202.2 | 191.45
2019-10-08 14:30 | 207.75 | 197.39
2019-10-08 15:00 | 190.4 | 179.5
2019-10-08 15:30 | 185.57 | 175.04
2019-10-08 16:00 | 186.65 | 176.85
2019-10-08 16:30 | 172.34 | 161.16
2019-10-08 17:00 | 226.24 | 217.48
2019-10-08 17:30 | 169.25 | 158.31
2019-10-08 18:00 | 112.81 | 96.27
2019-10-08 18:30 | 115.36 | 98.62
2019-10-08 19:00 | 123.07 | 108.15
2019-10-08 19:30 | 142.73 | 135.07
2019-10-08 20:00 | 129.29 | 125.25
2019-10-08 20:30 | 114.96 | 114.29
2019-10-08 21:00 | 114.36 | 114.35
2019-10-08 21:30 | 114.73 | 114.73
2019-10-08 22:00 | 102.9 | 102.9
2019-10-08 22:30 | 90.71 | 90.69
2019-10-08 23:00 | 74.3 | 74.29
2019-10-08 23:30 | 46.25 | 46.23
2019-10-09 | 18.96 | 18.95
2019-10-09 00:30 | 8.89 | 8.79
2019-10-09 01:00 | 9.39 | 9
2019-10-09 01:30 | 14.11 | 14.1
2019-10-09 02:00 | 14.84 | 14.8
2019-10-09 02:30 | 14.74 | 14.68
2019-10-09 03:00 | 11.35 | 10.52
2019-10-09 03:30 | 11.63 | 11.32
2019-10-09 04:00 | 14.93 | 14.82
2019-10-09 04:30 | 16.91 | 16.85
2019-10-09 05:00 | 16.55 | 16.52
2019-10-09 05:30 | 18.32 | 18.32
2019-10-09 06:00 | 26.82 | 26.8
2019-10-09 06:30 | 37.82 | 37.78
2019-10-09 07:00 | 45.35 | 45.03
2019-10-09 07:30 | 54.2 | 53.87
2019-10-09 08:00 | 61.01 | 60.51
2019-10-09 08:30 | 96.56 | 96.13
2019-10-09 09:00 | 80.36 | 79.5
2019-10-09 09:30 | 74.88 | 73.75
2019-10-09 10:00 | 84.41 | 83.29
2019-10-09 10:30 | 73.29 | 71.76
2019-10-09 11:00 | 45.81 | 42.92
2019-10-09 11:30 | 42.6 | 38.27
2019-10-09 12:00 | 44.62 | 40.02
2019-10-09 12:30 | 45.86 | 41.38
2019-10-09 13:00 | 48.33 | 44.88
2019-10-09 13:30 | 46.68 | 44.14
2019-10-09 14:00 | 48.12 | 46.78
2019-10-09 14:30 | 52.03 | 51
2019-10-09 15:00 | 52.9 | 52
2019-10-09 15:30 | 57.61 | 57.05
2019-10-09 16:00 | 60.83 | 60.32
2019-10-09 16:30 | 67.28 | 66.91
2019-10-09 17:00 | 80.74 | 80.47
2019-10-09 17:30 | 65.39 | 64.84
2019-10-09 18:00 | 88.16 | 87.73
2019-10-09 18:30 | 106.23 | 101.19
2019-10-09 19:00 | 127.13 | 116.57
2019-10-09 19:30 | 118.52 | 113.23
2019-10-09 20:00 | 103.94 | 103.63
2019-10-09 20:30 | 82.27 | 82.25
2019-10-09 21:00 | 61 | 60.91
2019-10-09 21:30 | 52.49 | 52.2
2019-10-09 22:00 | 48.58 | 48.48
2019-10-09 22:30 | 39.78 | 39.63
2019-10-09 23:00 | 36.42 | 36.25
2019-10-09 23:30 | 28.42 | 28.21
2019-10-10 | 16.79 | 16.64
2019-10-10 00:30 | 7.96 | 5.29
2019-10-10 01:00 | 7.04 | 3.21
2019-10-10 01:30 | 8.16 | 5.68
2019-10-10 02:00 | 14.54 | 5.36
2019-10-10 02:30 | 24.67 | 4.98
2019-10-10 03:00 | 23.08 | 5.38
2019-10-10 03:30 | 22.97 | 5.48
2019-10-10 04:00 | 22.45 | 5.49
2019-10-10 04:30 | 21.84 | 5.91
2019-10-10 05:00 | 20.66 | 6.44
2019-10-10 05:30 | 21.11 | 7.71
2019-10-10 06:00 | 25.3 | 18.31
2019-10-10 06:30 | 35.08 | 32.27
2019-10-10 07:00 | 42.69 | 42.56
2019-10-10 07:30 | 52.61 | 52.42
2019-10-10 08:00 | 54.81 | 54.59
2019-10-10 08:30 | 48.71 | 48.43
2019-10-10 09:00 | 44.47 | 44
2019-10-10 09:30 | 32.05 | 31.27
2019-10-10 10:00 | 34.16 | 33.39
2019-10-10 10:30 | 36.34 | 35.12
2019-10-10 11:00 | 34.74 | 33.41
2019-10-10 11:30 | 34.47 | 32.88
2019-10-10 12:00 | 47.44 | 46.36
2019-10-10 12:30 | 54.03 | 53.28
2019-10-10 13:00 | 72.11 | 68.24
2019-10-10 13:30 | 79.72 | 74.93
2019-10-10 14:00 | 62.3 | 56.81
2019-10-10 14:30 | 50.76 | 43.25
2019-10-10 15:00 | 70.18 | 64.25
2019-10-10 15:30 | 77.24 | 72.12
2019-10-10 16:00 | 73.85 | 69.15
2019-10-10 16:30 | 63.4 | 58.28
2019-10-10 17:00 | 61.12 | 56.22
2019-10-10 17:30 | 37.91 | 21.85
2019-10-10 18:00 | 36.88 | 3.02
2019-10-10 18:30 | 69.58 | 58.84
2019-10-10 19:00 | 88.31 | 80.56
2019-10-10 19:30 | 88.38 | 82.92
2019-10-10 20:00 | 62.23 | 58.7
2019-10-10 20:30 | 38.26 | 37.09
2019-10-10 21:00 | 1.21 | 1.1
2019-10-10 21:30 | 15.72 | 15.47
2019-10-10 22:00 | 25.48 | -25.48
2019-10-10 22:30 | 14.91 | -14.73
2019-10-10 23:00 | 20.62 | -20.51
2019-10-10 23:30 | 46.63 | -46.6
2019-10-11 | 58.87 | -56.31
2019-10-11 00:30 | 55.22 | -51.48
2019-10-11 01:00 | 64.65 | -60.42
2019-10-11 01:30 | 65.3 | -60.65
2019-10-11 02:00 | 66.3 | -61.04
2019-10-11 02:30 | 64.92 | -59.97
2019-10-11 03:00 | 64.44 | -59.49
2019-10-11 03:30 | 64.83 | -59.88
2019-10-11 04:00 | 63.75 | -59
2019-10-11 04:30 | 62.26 | -57.98
2019-10-11 05:00 | 63.13 | -59.28
2019-10-11 05:30 | 63.42 | -59.6
2019-10-11 06:00 | 58.57 | -55.02
2019-10-11 06:30 | 47.03 | -44.28
2019-10-11 07:00 | 36.9 | -36.72
2019-10-11 07:30 | 11.11 | 11.09
2019-10-11 08:00 | 38.5 | 38.48
2019-10-11 08:30 | 48.75 | 48.64
2019-10-11 09:00 | 34.15 | 33.72
2019-10-11 09:30 | 18.93 | 17.98
2019-10-11 10:00 | 17.11 | 15.55
2019-10-11 10:30 | 11.95 | 6.01
2019-10-11 11:00 | 56.75 | 55.97
2019-10-11 11:30 | 23.7 | 21.22
2019-10-11 12:00 | 23.92 | 21.74
2019-10-11 12:30 | 54.98 | 47.65
2019-10-11 13:00 | 87.63 | 83.48
2019-10-11 13:30 | 81.72 | 77.54
2019-10-11 14:00 | 78.86 | 75.21
2019-10-11 14:30 | 39.18 | 33.71
2019-10-11 15:00 | 45.95 | 42.2
2019-10-11 15:30 | 81.73 | 79.94
2019-10-11 16:00 | 98.33 | 96.84
2019-10-11 16:30 | 88.99 | 87.23
2019-10-11 17:00 | 103.98 | 102.56
2019-10-11 17:30 | 108.04 | 106.78
2019-10-11 18:00 | 107.6 | 106.27
2019-10-11 18:30 | 116.79 | 114.31
2019-10-11 19:00 | 119.35 | 115.5
2019-10-11 19:30 | 106.33 | 102.5
2019-10-11 20:00 | 97.36 | 97.34
2019-10-11 20:30 | 92.05 | 91.81
2019-10-11 21:00 | 73.01 | 72.52
2019-10-11 21:30 | 60.02 | 59.17
2019-10-11 22:00 | 45.21 | 44.03
2019-10-11 22:30 | 58.24 | 57.21
2019-10-11 23:00 | 61.9 | 60.85
2019-10-11 23:30 | 42.11 | 40.98
2019-10-12 | 46.23 | -46.2
2019-10-12 00:30 | 37.32 | -37.29
2019-10-12 01:00 | 58.52 | -58.49
2019-10-12 01:30 | 60.33 | -60.29
2019-10-12 02:00 | 50.35 | -50.33
2019-10-12 02:30 | 28.36 | -28.3
2019-10-12 03:00 | 6.86 | -0.43
2019-10-12 03:30 | 32.43 | -31.97
2019-10-12 04:00 | 37.35 | -37.04
2019-10-12 04:30 | 10.07 | -5.63
2019-10-12 05:00 | 12.08 | 7.79
2019-10-12 05:30 | 22.1 | -20.82
2019-10-12 06:00 | 17.98 | -16.92
2019-10-12 06:30 | 15.19 | 11.28
2019-10-12 07:00 | 32.06 | 29.76
2019-10-12 07:30 | 54.86 | 53.32
2019-10-12 08:00 | 71.8 | 71.01
2019-10-12 08:30 | 89.1 | 88.94
2019-10-12 09:00 | 88.89 | 88.8
2019-10-12 09:30 | 89.62 | 89.58
2019-10-12 10:00 | 93.51 | 92.74
2019-10-12 10:30 | 102.85 | 101.38
2019-10-12 11:00 | 112.45 | 111.2
2019-10-12 11:30 | 116.17 | 115
2019-10-12 12:00 | 111.93 | 110.91
2019-10-12 12:30 | 74.55 | 73.26
2019-10-12 13:00 | 25.8 | 22.42
2019-10-12 13:30 | 16.27 | 9.95
2019-10-12 14:00 | 19.46 | 15.3
2019-10-12 14:30 | 26.14 | 23.87
2019-10-12 15:00 | 27.61 | 25.95
2019-10-12 15:30 | 30.46 | 29.23
2019-10-12 16:00 | 50.37 | 49.63
2019-10-12 16:30 | 72.63 | 71.99
2019-10-12 17:00 | 96.9 | 96.34
2019-10-12 17:30 | 117.59 | 117.04
2019-10-12 18:00 | 140.5 | 139.87
2019-10-12 18:30 | 159.41 | 158.42
2019-10-12 19:00 | 160.43 | 159.59
2019-10-12 19:30 | 164.12 | 163.58
2019-10-12 20:00 | 154.2 | 153.8
2019-10-12 20:30 | 141.34 | 140.99
2019-10-12 21:00 | 132.82 | 132.55
2019-10-12 21:30 | 121.57 | 121.42
2019-10-12 22:00 | 111.36 | 111.32
2019-10-12 22:30 | 127.18 | 127.17
2019-10-12 23:00 | 140.64 | 140.64
2019-10-12 23:30 | 133.57 | 133.56
2019-10-13 | 98.28 | 97.41
2019-10-13 00:30 | 76.36 | 74.6
2019-10-13 01:00 | 58.76 | 56.63
2019-10-13 01:30 | 43.58 | 40.58
2019-10-13 02:00 | 39.05 | 35.75
2019-10-13 02:30 | 48.89 | 46.34
2019-10-13 03:00 | 65.72 | 65.19
2019-10-13 03:30 | 61.55 | 61.46
2019-10-13 04:00 | 51.74 | 51.64
2019-10-13 04:30 | 54.49 | 54.42
2019-10-13 05:00 | 58.54 | 58.47
2019-10-13 05:30 | 53.23 | 53.23
2019-10-13 06:00 | 52.52 | 52.52
2019-10-13 06:30 | 46.43 | 46.43
2019-10-13 07:00 | 35.68 | 35.68
2019-10-13 07:30 | 35.98 | 35.92
2019-10-13 08:00 | 34.44 | 34.29
2019-10-13 08:30 | 31.27 | 30.9
2019-10-13 09:00 | 53.04 | 52.53
2019-10-13 09:30 | 68.98 | 68.47
2019-10-13 10:00 | 72.98 | 72.41
2019-10-13 10:30 | 57.88 | 57.37
2019-10-13 11:00 | 11.56 | 10.77
2019-10-13 11:30 | 13.96 | 12.22
2019-10-13 12:00 | 23.6 | 22.31
2019-10-13 12:30 | 32.87 | 31.68
2019-10-13 13:00 | 28.75 | 27.31
2019-10-13 13:30 | 24.52 | 22.56
2019-10-13 14:00 | 40.58 | 39.18
2019-10-13 14:30 | 47.12 | 45.76
2019-10-13 15:00 | 48.71 | 47.39
2019-10-13 15:30 | 69.78 | 68.73
2019-10-13 16:00 | 71.04 | 69.95
2019-10-13 16:30 | 91.6 | 90.77
2019-10-13 17:00 | 107.21 | 106.67
2019-10-13 17:30 | 117.14 | 116.69
2019-10-13 18:00 | 139.83 | 139.58
2019-10-13 18:30 | 159.2 | 159.14
2019-10-13 19:00 | 158.17 | 158.13
2019-10-13 19:30 | 132.96 | 132.84
2019-10-13 20:00 | 131.5 | 131.29
2019-10-13 20:30 | 129.24 | 128.89
2019-10-13 21:00 | 111.78 | 111.14
2019-10-13 21:30 | 97.45 | 96.34
2019-10-13 22:00 | 88.05 | 86.4
2019-10-13 22:30 | 82.68 | 80.94
2019-10-13 23:00 | 91.91 | 90.56
2019-10-13 23:30 | 74.18 | 72.48
2019-10-14 | 49.85 | 47.68
2019-10-14 00:30 | 43.19 | 40.12
2019-10-14 01:00 | 50.18 | 47.61
2019-10-14 01:30 | 53.67 | 51.35
2019-10-14 02:00 | 53.51 | 51.56
2019-10-14 02:30 | 43.34 | 41.01
2019-10-14 03:00 | 41.54 | 39.28
2019-10-14 03:30 | 33.35 | 30.36
2019-10-14 04:00 | 31.13 | 28.01
2019-10-14 04:30 | 21.82 | 17.48
2019-10-14 05:00 | 26.5 | 22.86
2019-10-14 05:30 | 39.12 | 37.03
2019-10-14 06:00 | 48.17 | 46.19
2019-10-14 06:30 | 40.95 | 37.91
2019-10-14 07:00 | 46.54 | 44.79
2019-10-14 07:30 | 59.82 | 59.21
2019-10-14 08:00 | 52.63 | 52.3
2019-10-14 08:30 | 70.25 | 70.25
2019-10-14 09:00 | 56.29 | 55.46
2019-10-14 09:30 | 62.15 | 55.27
2019-10-14 10:00 | 63.3 | 56.03
2019-10-14 10:30 | 69.68 | 62.64
2019-10-14 11:00 | 64.77 | 57.21
2019-10-14 11:30 | 81.02 | 75.26
2019-10-14 12:00 | 68.98 | 62.41
2019-10-14 12:30 | 62.4 | 55.2
2019-10-14 13:00 | 60.16 | 52.73
2019-10-14 13:30 | 59.68 | 52.09
2019-10-14 14:00 | 58.31 | 50.17
2019-10-14 14:30 | 67.27 | 62.21
2019-10-14 15:00 | 75.18 | 71.12
2019-10-14 15:30 | 100.1 | 97.39
2019-10-14 16:00 | 118.76 | 116.57
2019-10-14 16:30 | 146.36 | 144.77
2019-10-14 17:00 | 165.21 | 161.54
2019-10-14 17:30 | 171.32 | 168.77
2019-10-14 18:00 | 184.87 | 182.57
2019-10-14 18:30 | 202.03 | 199.5
2019-10-14 19:00 | 207 | 204.46
2019-10-14 19:30 | 200.51 | 198.44
2019-10-14 20:00 | 188.1 | 187.79
2019-10-14 20:30 | 179.99 | 179.85
2019-10-14 21:00 | 177.24 | 176.99
2019-10-14 21:30 | 161.09 | 160.64
2019-10-14 22:00 | 139.33 | 138.6
2019-10-14 22:30 | 142.03 | 141.24
2019-10-14 23:00 | 144.87 | 144.03
2019-10-14 23:30 | 120.87 | 119.91
2019-10-15 | 85.86 | 84.85
2019-10-15 00:30 | 65.36 | 64.54
2019-10-15 01:00 | 47.46 | 46.42
2019-10-15 01:30 | 33.17 | 32.85
2019-10-15 02:00 | 26.73 | 26.72
2019-10-15 02:30 | 30.56 | 30.56
2019-10-15 03:00 | 44.65 | 44.64
2019-10-15 03:30 | 31.97 | 31.97
2019-10-15 04:00 | 33.5 | 33.46
2019-10-15 04:30 | 35.02 | 34.86
2019-10-15 05:00 | 51.04 | 50.88
2019-10-15 05:30 | 67.5 | 67.27
2019-10-15 06:00 | 76.11 | 75.72
2019-10-15 06:30 | 87.18 | 86.65
2019-10-15 07:00 | 118.05 | 117.69
2019-10-15 07:30 | 166.28 | 166.24
2019-10-15 08:00 | 171.03 | 171.01
2019-10-15 08:30 | 155.75 | 155.75
2019-10-15 09:00 | 140.96 | 140.93
2019-10-15 09:30 | 141.35 | 141.28
2019-10-15 10:00 | 116.87 | 116.74
2019-10-15 10:30 | 117.41 | 117.24
2019-10-15 11:00 | 120.83 | 120.63
2019-10-15 11:30 | 120.17 | 119.91
2019-10-15 12:00 | 67.15 | 61.2
2019-10-15 12:30 | 61.93 | 43.8
2019-10-15 13:00 | 112.52 | 104.32
2019-10-15 13:30 | 52.77 | 27.84
2019-10-15 14:00 | 58.13 | 38.5
2019-10-15 14:30 | 70.86 | 57.01
2019-10-15 15:00 | 46.43 | 16.84
2019-10-15 15:30 | 56.68 | 38.05
2019-10-15 16:00 | 92.29 | 83.73
2019-10-15 16:30 | 99.89 | 92.99
2019-10-15 17:00 | 127.31 | 122.16
2019-10-15 17:30 | 149.1 | 145.24
2019-10-15 18:00 | 171.09 | 169.35
2019-10-15 18:30 | 190.32 | 189.24
2019-10-15 19:00 | 206.95 | 205.57
2019-10-15 19:30 | 193.2 | 192.04
2019-10-15 20:00 | 198.86 | 197.87
2019-10-15 20:30 | 186.12 | 185.24
2019-10-15 21:00 | 163.84 | 163.15
2019-10-15 21:30 | 143.29 | 142.93
2019-10-15 22:00 | 115.62 | 115.35
2019-10-15 22:30 | 112.85 | 112.68
2019-10-15 23:00 | 107.32 | 107.26
2019-10-15 23:30 | 80.07 | 78.74
2019-10-16 | 49.6 | 47.79
2019-10-16 00:30 | 44.22 | 42.65
2019-10-16 01:00 | 37.73 | 36.29
2019-10-16 01:30 | 32.75 | 31.14
2019-10-16 02:00 | 26.19 | 24.48
2019-10-16 02:30 | 23.02 | 20.93
2019-10-16 03:00 | 21.22 | 19.05
2019-10-16 03:30 | 21.4 | 19.08
2019-10-16 04:00 | 22.4 | 19.96
2019-10-16 04:30 | 32.2 | 30.18
2019-10-16 05:00 | 48.66 | 47.28
2019-10-16 05:30 | 56.09 | 54.99
2019-10-16 06:00 | 51.83 | 50.58
2019-10-16 06:30 | 51.52 | 50.65
2019-10-16 07:00 | 54.05 | 53.77
2019-10-16 07:30 | 58.72 | 58.62
2019-10-16 08:00 | 60.58 | 60.25
2019-10-16 08:30 | 53.43 | 46.85
2019-10-16 09:00 | 47.8 | 36.27
2019-10-16 09:30 | 79.14 | 71.9
2019-10-16 10:00 | 96.19 | 89.71
2019-10-16 10:30 | 93.28 | 86.13
2019-10-16 11:00 | 90.85 | 83.03
2019-10-16 11:30 | 70.88 | 60.51
2019-10-16 12:00 | 67.4 | 56.96
2019-10-16 12:30 | 71.93 | 62.2
2019-10-16 13:00 | 68.84 | 58.36
2019-10-16 13:30 | 71.9 | 61.31
2019-10-16 14:00 | 86.63 | 76.64
2019-10-16 14:30 | 84 | 74.45
2019-10-16 15:00 | 97.9 | 90.21
2019-10-16 15:30 | 102.64 | 95.87
2019-10-16 16:00 | 131.29 | 126.47
2019-10-16 16:30 | 153.43 | 149.56
2019-10-16 17:00 | 174.81 | 171.67
2019-10-16 17:30 | 197.55 | 195.08
2019-10-16 18:00 | 215.8 | 213.9
2019-10-16 18:30 | 222.77 | 220.63
2019-10-16 19:00 | 226.46 | 224.35
2019-10-16 19:30 | 215.05 | 213.4
2019-10-16 20:00 | 193.51 | 192.06
2019-10-16 20:30 | 185.69 | 184.37
2019-10-16 21:00 | 167.79 | 166.83
2019-10-16 21:30 | 142.64 | 141.92
2019-10-16 22:00 | 113.53 | 113.01
2019-10-16 22:30 | 116.49 | 116.18
2019-10-16 23:00 | 112.09 | 111.78
2019-10-16 23:30 | 90.56 | 90.36
2019-10-17 | 57 | 55.84
2019-10-17 00:30 | 43.87 | 42.87
2019-10-17 01:00 | 38.66 | 38.2
2019-10-17 01:30 | 45.09 | 45.03
2019-10-17 02:00 | 65.83 | 65.81
2019-10-17 02:30 | 80.35 | 80.33
2019-10-17 03:00 | 75.18 | 75.15
2019-10-17 03:30 | 81.41 | 81.37
2019-10-17 04:00 | 72.05 | 71.99
2019-10-17 04:30 | 74.25 | 74.24
2019-10-17 05:00 | 61.18 | 61.15
2019-10-17 05:30 | 84.98 | 84.97
2019-10-17 06:00 | 89.65 | 89.59
2019-10-17 06:30 | 80.34 | 80.25
2019-10-17 07:00 | 89.03 | 88.92
2019-10-17 07:30 | 120.32 | 120.28
2019-10-17 08:00 | 101.26 | 101.12
2019-10-17 08:30 | 89.13 | 88.59
2019-10-17 09:00 | 99.89 | 99.06
2019-10-17 09:30 | 96.76 | 95.57
2019-10-17 10:00 | 102.12 | 95.12
2019-10-17 10:30 | 120.13 | 113.56
2019-10-17 11:00 | 105.92 | 98.34
2019-10-17 11:30 | 96.08 | 87.35
2019-10-17 12:00 | 88.06 | 78.51
2019-10-17 12:30 | 72.88 | 60.71
2019-10-17 13:00 | 89.3 | 79.75
2019-10-17 13:30 | 124.71 | 105.75
2019-10-17 14:00 | 144.08 | 124.93
2019-10-17 14:30 | 163.14 | 146.94
2019-10-17 15:00 | 178.1 | 164.31
2019-10-17 15:30 | 184.7 | 171.94
2019-10-17 16:00 | 214.45 | 203.72
2019-10-17 16:30 | 227.09 | 217.27
2019-10-17 17:00 | 235.31 | 226.55
2019-10-17 17:30 | 211.51 | 211.05
2019-10-17 18:00 | 200.53 | 200.49
2019-10-17 18:30 | 198.08 | 197.93
2019-10-17 19:00 | 212.25 | 210.69
2019-10-17 19:30 | 188.2 | 186.71
2019-10-17 20:00 | 184.91 | 183.59
2019-10-17 20:30 | 174.99 | 173.88
2019-10-17 21:00 | 176.59 | 175.81
2019-10-17 21:30 | 147.62 | 147.14
2019-10-17 22:00 | 121.75 | 121.42
2019-10-17 22:30 | 111.69 | 111.15
2019-10-17 23:00 | 109.91 | 109.15
2019-10-17 23:30 | 90.25 | 89.21
2019-10-18 | 73.01 | 72.24
2019-10-18 00:30 | 65.22 | 65.17
2019-10-18 01:00 | 62.19 | 62.15
2019-10-18 01:30 | 75.78 | 75.77
2019-10-18 02:00 | 73.92 | 73.9
2019-10-18 02:30 | 73.12 | 73.09
2019-10-18 03:00 | 75.3 | 75.27
2019-10-18 03:30 | 71.91 | 71.87
2019-10-18 04:00 | 69.89 | 69.85
2019-10-18 04:30 | 68.79 | 68.78
2019-10-18 05:00 | 65.07 | 65.07
2019-10-18 05:30 | 83 | 83
2019-10-18 06:00 | 79.34 | 79.3
2019-10-18 06:30 | 69.18 | 68.93
2019-10-18 07:00 | 79.58 | 79.33
2019-10-18 07:30 | 91.91 | 91.91
2019-10-18 08:00 | 86.39 | 86.34
2019-10-18 08:30 | 89.32 | 89.16
2019-10-18 09:00 | 67.39 | 66.83
2019-10-18 09:30 | 99.85 | 99.21
2019-10-18 10:00 | 99 | 98.28
2019-10-18 10:30 | 98.36 | 97.53
2019-10-18 11:00 | 111.48 | 110.65
2019-10-18 11:30 | 120.3 | 119.51
2019-10-18 12:00 | 123.98 | 123.21
2019-10-18 12:30 | 128.71 | 128.05
2019-10-18 13:00 | 130.84 | 130.17
2019-10-18 13:30 | 132.7 | 132.01
2019-10-18 14:00 | 142.28 | 138.74
2019-10-18 14:30 | 151.11 | 148.16
2019-10-18 15:00 | 153.56 | 150.99
2019-10-18 15:30 | 147.08 | 144.49
2019-10-18 16:00 | 168.32 | 166.16
2019-10-18 16:30 | 185.08 | 183.26
2019-10-18 17:00 | 195.93 | 194.38
2019-10-18 17:30 | 199.46 | 198.11
2019-10-18 18:00 | 190.39 | 189.32
2019-10-18 18:30 | 199.73 | 198.54
2019-10-18 19:00 | 208.53 | 207.32
2019-10-18 19:30 | 191.18 | 190.06
2019-10-18 20:00 | 171.8 | 170.8
2019-10-18 20:30 | 166.71 | 165.88
2019-10-18 21:00 | 164.14 | 163.55
2019-10-18 21:30 | 162.44 | 162.03
2019-10-18 22:00 | 142.12 | 141.84
2019-10-18 22:30 | 132.14 | 131.49
2019-10-18 23:00 | 120.23 | 119.37
2019-10-18 23:30 | 88.18 | 86.85
2019-10-19 | 52.54 | 51.21
2019-10-19 00:30 | 52.42 | 52.38
2019-10-19 01:00 | 68.3 | 68.29
2019-10-19 01:30 | 59.13 | 59.1
2019-10-19 02:00 | 75.19 | 75.19
2019-10-19 02:30 | 84.68 | 84.68
2019-10-19 03:00 | 85.38 | 85.38
2019-10-19 03:30 | 90.13 | 89.09
2019-10-19 04:00 | 88.13 | 86.95
2019-10-19 04:30 | 84.67 | 83.64
2019-10-19 05:00 | 76.82 | 75.66
2019-10-19 05:30 | 82.95 | 81.32
2019-10-19 06:00 | 70.06 | 68.53
2019-10-19 06:30 | 52.34 | 51.36
2019-10-19 07:00 | 48.24 | 46.56
2019-10-19 07:30 | 59.96 | 59.96
2019-10-19 08:00 | 71.92 | 71.7
2019-10-19 08:30 | 82.46 | 82.27
2019-10-19 09:00 | 110.47 | 110.44
2019-10-19 09:30 | 128.06 | 128.04
2019-10-19 10:00 | 142.8 | 141.36
2019-10-19 10:30 | 130.93 | 129.29
2019-10-19 11:00 | 137.33 | 135.64
2019-10-19 11:30 | 142.26 | 140.85
2019-10-19 12:00 | 123.04 | 121.58
2019-10-19 12:30 | 117.59 | 115.87
2019-10-19 13:00 | 85.12 | 85.06
2019-10-19 13:30 | 38.34 | 38.2
2019-10-19 14:00 | 47.68 | 47.53
2019-10-19 14:30 | 46.84 | 46.72
2019-10-19 15:00 | 44.92 | 44.82
2019-10-19 15:30 | 49.26 | 48.57
2019-10-19 16:00 | 57.84 | 53.37
2019-10-19 16:30 | 62.87 | 58.41
2019-10-19 17:00 | 64.49 | 59.84
2019-10-19 17:30 | 64.18 | 59.63
2019-10-19 18:00 | 62.99 | 59
2019-10-19 18:30 | 179.41 | 177.78
2019-10-19 19:00 | 174.84 | 173.2
2019-10-19 19:30 | 154.44 | 152.87
2019-10-19 20:00 | 163.51 | 162.29
2019-10-19 20:30 | 145.29 | 144.19
2019-10-19 21:00 | 138.1 | 137.28
2019-10-19 21:30 | 119.05 | 118.48
2019-10-19 22:00 | 101.02 | 100.84
2019-10-19 22:30 | 99.45 | 98.72
2019-10-19 23:00 | 102.84 | 102.03
2019-10-19 23:30 | 85.46 | 84.23
2019-10-20 | 57.48 | 55.5
2019-10-20 00:30 | 58.62 | 57.22
2019-10-20 01:00 | 70.94 | 69.76
2019-10-20 01:30 | 63.24 | 62.07
2019-10-20 02:00 | 61.31 | 60.31
2019-10-20 02:30 | 59.36 | 58.86
2019-10-20 03:00 | 48.26 | 48.26
2019-10-20 03:30 | 48.51 | 48.49
2019-10-20 04:00 | 43.08 | 43.06
2019-10-20 04:30 | 43.86 | 43.86
2019-10-20 05:00 | 43.39 | 43.38
2019-10-20 05:30 | 45.81 | 45.64
2019-10-20 06:00 | 40.87 | 40.38
2019-10-20 06:30 | 15.91 | 15.71
2019-10-20 07:00 | 6.43 | 6.43
2019-10-20 07:30 | 6.63 | -6.51
2019-10-20 08:00 | 24.23 | -24.23
2019-10-20 08:30 | 53.44 | -53.41
2019-10-20 09:00 | 35.22 | -35.21
2019-10-20 09:30 | 29.39 | -29.36
2019-10-20 10:00 | 50.66 | -50.63
2019-10-20 10:30 | 26.57 | -26.57
2019-10-20 11:00 | 46.46 | -46.39
2019-10-20 11:30 | 32.35 | -32.22
2019-10-20 12:00 | 36.55 | -36.44
2019-10-20 12:30 | 46.99 | -46.86
2019-10-20 13:00 | 47.35 | -47.23
2019-10-20 13:30 | 40.57 | -40.45
2019-10-20 14:00 | 2.1 | -2.08
2019-10-20 14:30 | 9.16 | 8.89
2019-10-20 15:00 | 20.6 | 20.41
2019-10-20 15:30 | 26.25 | 26.09
2019-10-20 16:00 | 35.54 | 35.38
2019-10-20 16:30 | 52.48 | 52.33
2019-10-20 17:00 | 60.7 | 60.61
2019-10-20 17:30 | 85.19 | 85.12
2019-10-20 18:00 | 111.23 | 111.17
2019-10-20 18:30 | 112.35 | 111.01
2019-10-20 19:00 | 125.54 | 115.45
2019-10-20 19:30 | 118.76 | 113.26
2019-10-20 20:00 | 115.72 | 113.44
2019-10-20 20:30 | 107.2 | 105
2019-10-20 21:00 | 94.58 | 92.63
2019-10-20 21:30 | 86.76 | 86.76
2019-10-20 22:00 | 64.89 | 64.66
2019-10-20 22:30 | 69.36 | 69.01
2019-10-20 23:00 | 60.31 | 59.79
2019-10-20 23:30 | 48.51 | 47.88
2019-10-21 | 14.59 | -14.59
2019-10-21 00:30 | 16.89 | 16.37
2019-10-21 01:00 | 18.95 | 18.48
2019-10-21 01:30 | 17.94 | 17.39
2019-10-21 02:00 | 26.13 | 25.63
2019-10-21 02:30 | 32.47 | 32.05
2019-10-21 03:00 | 32.47 | 31.97
2019-10-21 03:30 | 32.77 | 32.14
2019-10-21 04:00 | 29.02 | 28.44
2019-10-21 04:30 | 28.63 | 28.11
2019-10-21 05:00 | 39.24 | 38.91
2019-10-21 05:30 | 65.38 | 65.26
2019-10-21 06:00 | 60.42 | 60.32
2019-10-21 06:30 | 30.62 | 30.48
2019-10-21 07:00 | 30.21 | 30.15
2019-10-21 07:30 | 49.1 | 49.07
2019-10-21 08:00 | 62.34 | 62.31
2019-10-21 08:30 | 65.81 | 65.8
2019-10-21 09:00 | 63.67 | 63.58
2019-10-21 09:30 | 62.61 | 62.43
2019-10-21 10:00 | 56.89 | 56.64
2019-10-21 10:30 | 51.52 | 51.2
2019-10-21 11:00 | 39.23 | 38.74
2019-10-21 11:30 | 34.52 | 33.95
2019-10-21 12:00 | 33.35 | 32.77
2019-10-21 12:30 | 35.62 | 35.1
2019-10-21 13:00 | 40.18 | 39.79
2019-10-21 13:30 | 44.02 | 43.64
2019-10-21 14:00 | 34.56 | 33.88
2019-10-21 14:30 | 44.47 | 43.93
2019-10-21 15:00 | 51.39 | 51.35
2019-10-21 15:30 | 80.82 | 80.82
2019-10-21 16:00 | 110.5 | 110.5
2019-10-21 16:30 | 128.04 | 128.02
2019-10-21 17:00 | 148.96 | 148.94
2019-10-21 17:30 | 174.38 | 173.26
2019-10-21 18:00 | 188.13 | 186.88
2019-10-21 18:30 | 206.79 | 205.27
2019-10-21 19:00 | 203.71 | 199.33
2019-10-21 19:30 | 196.47 | 191.4
2019-10-21 20:00 | 184.98 | 184.9
2019-10-21 20:30 | 183.42 | 183.41
2019-10-21 21:00 | 164.13 | 164.05
2019-10-21 21:30 | 144.63 | 144.41
2019-10-21 22:00 | 113.19 | 112.65
2019-10-21 22:30 | 110.53 | 109.71
2019-10-21 23:00 | 101.4 | 100.48
2019-10-21 23:30 | 70.23 | 69.04
2019-10-22 | 44.59 | 42.55
2019-10-22 00:30 | 40.11 | 37.68
2019-10-22 01:00 | 40.78 | 38.49
2019-10-22 01:30 | 41.58 | 39.45
2019-10-22 02:00 | 51.79 | 50.27
2019-10-22 02:30 | 44.04 | 42.05
2019-10-22 03:00 | 46.1 | 43.53
2019-10-22 03:30 | 44.73 | 41.91
2019-10-22 04:00 | 34.26 | 30.88
2019-10-22 04:30 | 26.68 | 21.83
2019-10-22 05:00 | 26.42 | 22.7
2019-10-22 05:30 | 38.07 | 36.1
2019-10-22 06:00 | 43.98 | 42.56
2019-10-22 06:30 | 36.63 | 35.66
2019-10-22 07:00 | 41.9 | 41.5
2019-10-22 07:30 | 52.4 | 52.4
2019-10-22 08:00 | 49.63 | 44.16
2019-10-22 08:30 | 49.52 | 40.93
2019-10-22 09:00 | 65.35 | 58.67
2019-10-22 09:30 | 82.53 | 79.33
2019-10-22 10:00 | 127.5 | 125.95
2019-10-22 10:30 | 147.42 | 145.45
2019-10-22 11:00 | 146.96 | 144.79
2019-10-22 11:30 | 104.49 | 101.92
2019-10-22 12:00 | 83.53 | 79.55
2019-10-22 12:30 | 91.09 | 87.07
2019-10-22 13:00 | 65.88 | 61.42
2019-10-22 13:30 | 66.48 | 62.03
2019-10-22 14:00 | 70.68 | 66.96
2019-10-22 14:30 | 78.38 | 75.49
2019-10-22 15:00 | 82.84 | 80.62
2019-10-22 15:30 | 90.79 | 89.06
2019-10-22 16:00 | 110.91 | 109.7
2019-10-22 16:30 | 122.2 | 120.27
2019-10-22 17:00 | 152.68 | 151.11
2019-10-22 17:30 | 165.33 | 164.09
2019-10-22 18:00 | 166.47 | 165.41
2019-10-22 18:30 | 179.62 | 178.44
2019-10-22 19:00 | 188.86 | 187.63
2019-10-22 19:30 | 172.18 | 171.07
2019-10-22 20:00 | 180.37 | 179.39
2019-10-22 20:30 | 187.23 | 186.36
2019-10-22 21:00 | 179.79 | 179.02
2019-10-22 21:30 | 156.9 | 156.06
2019-10-22 22:00 | 137.66 | 137.56
2019-10-22 22:30 | 132.15 | 132.15
2019-10-22 23:00 | 121.5 | 121.5
2019-10-22 23:30 | 104.6 | 104.58
2019-10-23 | 92.81 | 92.77
2019-10-23 00:30 | 90.76 | 90.68
2019-10-23 01:00 | 69.02 | 68.97
2019-10-23 01:30 | 65.74 | 65.72
2019-10-23 02:00 | 65.1 | 65.09
2019-10-23 02:30 | 62.09 | 62.08
2019-10-23 03:00 | 59.1 | 59.1
2019-10-23 03:30 | 59.8 | 59.8
2019-10-23 04:00 | 63.93 | 63.91
2019-10-23 04:30 | 60.44 | 60.4
2019-10-23 05:00 | 63.33 | 63.28
2019-10-23 05:30 | 70.71 | 70.68
2019-10-23 06:00 | 82.01 | 81.84
2019-10-23 06:30 | 83.93 | 83.91
2019-10-23 07:00 | 83.92 | 83.77
2019-10-23 07:30 | 93.38 | 93.18
2019-10-23 08:00 | 101.16 | 101.03
2019-10-23 08:30 | 122.43 | 122.25
2019-10-23 09:00 | 125.63 | 125.5
2019-10-23 09:30 | 120.75 | 120.55
2019-10-23 10:00 | 103.73 | 103.45
2019-10-23 10:30 | 97.01 | 96.6
2019-10-23 11:00 | 98.17 | 97.45
2019-10-23 11:30 | 94.53 | 93.52
2019-10-23 12:00 | 93.09 | 92.09
2019-10-23 12:30 | 95.38 | 94.53
2019-10-23 13:00 | 90.2 | 89.75
2019-10-23 13:30 | 80.99 | 79.82
2019-10-23 14:00 | 81.29 | 80.76
2019-10-23 14:30 | 87.78 | 86.85
2019-10-23 15:00 | 89.57 | 88.64
2019-10-23 15:30 | 99.99 | 98.67
2019-10-23 16:00 | 116.89 | 116.37
2019-10-23 16:30 | 107.26 | 107.13
2019-10-23 17:00 | 69.91 | 69.39
2019-10-23 17:30 | 82.5 | 82.12
2019-10-23 18:00 | 79.97 | 79.74
2019-10-23 18:30 | 98.43 | 98.17
2019-10-23 19:00 | 122.31 | 122.04
2019-10-23 19:30 | 122.49 | 122.34
2019-10-23 20:00 | 128.62 | 128.57
2019-10-23 20:30 | 122.66 | 122.65
2019-10-23 21:00 | 114.22 | 114.22
2019-10-23 21:30 | 111.07 | 110.97
2019-10-23 22:00 | 97.37 | 97.14
2019-10-23 22:30 | 78.45 | 77.82
2019-10-23 23:00 | 66.67 | 65.89
2019-10-23 23:30 | 44.92 | 44.22
2019-10-24 | 20.13 | 19.16
2019-10-24 00:30 | 22.45 | 22.45
2019-10-24 01:00 | 23.1 | 17.5
2019-10-24 01:30 | 20.93 | 12.28
2019-10-24 02:00 | 22.8 | 15.5
2019-10-24 02:30 | 24.55 | 18.18
2019-10-24 03:00 | 31.69 | 27.22
2019-10-24 03:30 | 32.56 | 28.22
2019-10-24 04:00 | 31.3 | 28.09
2019-10-24 04:30 | 31.15 | 29.15
2019-10-24 05:00 | 32.72 | 30.78
2019-10-24 05:30 | 26.15 | 23.93
2019-10-24 06:00 | 27.15 | 26.24
2019-10-24 06:30 | 32.1 | 32.01
2019-10-24 07:00 | 33 | 32.98
2019-10-24 07:30 | 42.69 | 42.69
2019-10-24 08:00 | 38.04 | 37.75
2019-10-24 08:30 | 24.26 | 24.26
2019-10-24 09:00 | 32 | 31.55
2019-10-24 09:30 | 25.09 | 23.99
2019-10-24 10:00 | 22.35 | 19.73
2019-10-24 10:30 | 20.17 | 17.83
2019-10-24 11:00 | 19.72 | 19.72
2019-10-24 11:30 | 19.63 | 19.05
2019-10-24 12:00 | 30.85 | 30.49
2019-10-24 12:30 | 33.02 | 32.35
2019-10-24 13:00 | 31.77 | 31.57
2019-10-24 13:30 | 35.19 | 34.87
2019-10-24 14:00 | 35.39 | 35.39
2019-10-24 14:30 | 42.95 | 42.54
2019-10-24 15:00 | 43.43 | 43.03
2019-10-24 15:30 | 44.64 | 44.38
2019-10-24 16:00 | 56.12 | 56.01
2019-10-24 16:30 | 72.38 | 72.33
2019-10-24 17:00 | 98.5 | 98.49
2019-10-24 17:30 | 104.01 | 104
2019-10-24 18:00 | 127.95 | 127.95
2019-10-24 18:30 | 157.53 | 157.52
2019-10-24 19:00 | 190.83 | 190.81
2019-10-24 19:30 | 176.12 | 176.11
2019-10-24 20:00 | 196.57 | 196.56
2019-10-24 20:30 | 184.47 | 184.38
2019-10-24 21:00 | 168.31 | 168.15
2019-10-24 21:30 | 147.11 | 146.67
2019-10-24 22:00 | 121.41 | 120.29
2019-10-24 22:30 | 129.51 | 127.84
2019-10-24 23:00 | 106.53 | 104.13
2019-10-24 23:30 | 85.44 | 83.26
2019-10-25 | 64.52 | 63.65
2019-10-25 00:30 | 62.02 | 61.77
2019-10-25 01:00 | 70.29 | 69.99
2019-10-25 01:30 | 74.22 | 73.92
2019-10-25 02:00 | 73.33 | 72.95
2019-10-25 02:30 | 71.77 | 71.34
2019-10-25 03:00 | 86.85 | 86.45
2019-10-25 03:30 | 93.97 | 93.56
2019-10-25 04:00 | 91.65 | 91.28
2019-10-25 04:30 | 83.37 | 83.07
2019-10-25 05:00 | 76.41 | 76.08
2019-10-25 05:30 | 90.51 | 90.12
2019-10-25 06:00 | 79.13 | 79.02
2019-10-25 06:30 | 67.24 | 67.24
2019-10-25 07:00 | 65.33 | 65.33
2019-10-25 07:30 | 78.9 | 78.88
2019-10-25 08:00 | 65.08 | 65.05
2019-10-25 08:30 | 62.45 | 61.03
2019-10-25 09:00 | 43.74 | 41.51
2019-10-25 09:30 | 41.27 | 39.87
2019-10-25 10:00 | 34.57 | 33.08
2019-10-25 10:30 | 33.71 | 32.54
2019-10-25 11:00 | 24.95 | 24.59
2019-10-25 11:30 | 23.52 | 21.68
2019-10-25 12:00 | 20.73 | 19.04
2019-10-25 12:30 | 17.51 | 15.65
2019-10-25 13:00 | 31.7 | 30.88
2019-10-25 13:30 | 12.41 | 10.12
2019-10-25 14:00 | 12.15 | 7.8
2019-10-25 14:30 | 38.13 | 37.33
2019-10-25 15:00 | 48.43 | 48.02
2019-10-25 15:30 | 63.29 | 63.08
2019-10-25 16:00 | 68.44 | 68.32
2019-10-25 16:30 | 98.98 | 98.92
2019-10-25 17:00 | 151.19 | 151.17
2019-10-25 17:30 | 165.97 | 165.96
2019-10-25 18:00 | 155.78 | 155.75
2019-10-25 18:30 | 157.11 | 157.09
2019-10-25 19:00 | 161.13 | 161.12
2019-10-25 19:30 | 166.9 | 166.85
2019-10-25 20:00 | 139.8 | 139.64
2019-10-25 20:30 | 136.49 | 136.22
2019-10-25 21:00 | 120.44 | 119.98
2019-10-25 21:30 | 145.74 | 145.03
2019-10-25 22:00 | 124.89 | 123.71
2019-10-25 22:30 | 121.26 | 119.84
2019-10-25 23:00 | 131.9 | 130.38
2019-10-25 23:30 | 112.21 | 110.65
2019-10-26 | 86.75 | 84.84
2019-10-26 00:30 | 87.78 | 86.65
2019-10-26 01:00 | 91.01 | 90.88
2019-10-26 01:30 | 108.74 | 108.6
2019-10-26 02:00 | 96.52 | 96.39
2019-10-26 02:30 | 90.07 | 89.92
2019-10-26 03:00 | 76.67 | 76.58
2019-10-26 03:30 | 77 | 76.91
2019-10-26 04:00 | 75.36 | 75.27
2019-10-26 04:30 | 79.96 | 79.85
2019-10-26 05:00 | 72.03 | 71.84
2019-10-26 05:30 | 85.79 | 85.47
2019-10-26 06:00 | 62.87 | 62.47
2019-10-26 06:30 | 42.47 | 42.09
2019-10-26 07:00 | 22.91 | 22.89
2019-10-26 07:30 | 27.44 | 22.95
2019-10-26 08:00 | 21.14 | 15.25
2019-10-26 08:30 | 17.46 | 9.07
2019-10-26 09:00 | 9.66 | -5.69
2019-10-26 09:30 | 67.17 | -67.16
2019-10-26 10:00 | 74.31 | -74.27
2019-10-26 10:30 | 62.07 | -62.02
2019-10-26 11:00 | 52.79 | -52.77
2019-10-26 11:30 | 41.14 | -41.14
2019-10-26 12:00 | 19.4 | -19.04
2019-10-26 12:30 | 3.55 | -1.47
2019-10-26 13:00 | 3.45 | 1.96
2019-10-26 13:30 | 10.2 | 9.77
2019-10-26 14:00 | 18.97 | 18.76
2019-10-26 14:30 | 36.06 | 35.9
2019-10-26 15:00 | 63.92 | 63.77
2019-10-26 15:30 | 89.4 | 89.29
2019-10-26 16:00 | 91.94 | 91.85
2019-10-26 16:30 | 107.77 | 107.71
2019-10-26 17:00 | 140.34 | 140.27
2019-10-26 17:30 | 153.51 | 153.34
2019-10-26 18:00 | 169.24 | 169
2019-10-26 18:30 | 188.73 | 188.6
2019-10-26 19:00 | 199.01 | 198.89
2019-10-26 19:30 | 184.53 | 184.35
2019-10-26 20:00 | 168.77 | 168.63
2019-10-26 20:30 | 154.59 | 154.33
2019-10-26 21:00 | 147.96 | 147.55
2019-10-26 21:30 | 117.5 | 116.74
2019-10-26 22:00 | 116.73 | 115.6
2019-10-26 22:30 | 114.57 | 113.29
2019-10-26 23:00 | 102.43 | 100.72
2019-10-26 23:30 | 76.56 | 73.8
2019-10-27 | 48.98 | 43.97
2019-10-27 00:30 | 44.63 | 40.02
2019-10-27 01:00 | 41.56 | 37.77
2019-10-27 01:30 | 36.13 | 32.04
2019-10-27 02:00 | 26.72 | 21.15
2019-10-27 02:30 | 23.49 | 17.42
2019-10-27 03:00 | 22.04 | 15.6
2019-10-27 03:30 | 20.34 | 13.28
2019-10-27 04:00 | 15.62 | 8.04
2019-10-27 04:30 | 19.24 | 12.22
2019-10-27 05:00 | 14.22 | 1.22
2019-10-27 05:30 | 9.55 | 4.05
2019-10-27 06:00 | 8.08 | -0.98
2019-10-27 06:30 | 12.89 | -9.51
2019-10-27 07:00 | 19.26 | -16.2
2019-10-27 07:30 | 20.96 | -16.2
2019-10-27 08:00 | 23.56 | -20.58
2019-10-27 08:30 | 54.81 | -54.79
2019-10-27 09:00 | 36.98 | -36.97
2019-10-27 09:30 | 57.41 | -57.37
2019-10-27 10:00 | 19.6 | -19.59
2019-10-27 10:30 | 16.23 | -16.13
2019-10-27 11:00 | 25.62 | -25.45
2019-10-27 11:30 | 22.98 | -22.82
2019-10-27 12:00 | 26.92 | -26.76
2019-10-27 12:30 | 26.24 | -26.14
2019-10-27 13:00 | 7.88 | -7.87
2019-10-27 13:30 | 7.21 | 7.06
2019-10-27 14:00 | 14.4 | 14.12
2019-10-27 14:30 | 31.39 | 31.2
2019-10-27 15:00 | 46.32 | 46.14
2019-10-27 15:30 | 66.19 | 65.98
2019-10-27 16:00 | 78.15 | 77.88
2019-10-27 16:30 | 59.21 | 58.82
2019-10-27 17:00 | 86.18 | 85.96
2019-10-27 17:30 | 102.96 | 102.75
2019-10-27 18:00 | 104.81 | 104.58
2019-10-27 18:30 | 115.56 | 115.47
2019-10-27 19:00 | 125.48 | 125.42
2019-10-27 19:30 | 103.78 | 103.65
2019-10-27 20:00 | 87.82 | 87.57
2019-10-27 20:30 | 72.77 | 72.38
2019-10-27 21:00 | 42.42 | 41.3
2019-10-27 21:30 | 23.21 | -21.72
2019-10-27 22:00 | 27.17 | -25.94
2019-10-27 22:30 | 49.44 | -49.07
2019-10-27 23:00 | 35.71 | 31.8
2019-10-27 23:30 | 39.12 | -37.4
2019-10-28 | 82.14 | -82.01
2019-10-28 00:30 | 65.36 | -65.27
2019-10-28 01:00 | 45.4 | -44.26
2019-10-28 01:30 | 17.86 | -14.49
2019-10-28 02:00 | 13.86 | -12.21
2019-10-28 02:30 | 17.05 | -15.89
2019-10-28 03:00 | 12.7 | -10.41
2019-10-28 03:30 | 12.54 | -9.69
2019-10-28 04:00 | 25.53 | -24.63
2019-10-28 04:30 | 10.8 | -5.7
2019-10-28 05:00 | 10.58 | 3.43
2019-10-28 05:30 | 16.43 | 12.72
2019-10-28 06:00 | 18.87 | 14.25
2019-10-28 06:30 | 34.98 | 31.6
2019-10-28 07:00 | 55.64 | 55.03
2019-10-28 07:30 | 71.1 | 71.03
2019-10-28 08:00 | 61.77 | 61.6
2019-10-28 08:30 | 56.84 | 56.02
2019-10-28 09:00 | 49.22 | 47.52
2019-10-28 09:30 | 48.95 | 46.33
2019-10-28 10:00 | 52.58 | 48.53
2019-10-28 10:30 | 64.86 | 51.56
2019-10-28 11:00 | 56.46 | 42.05
2019-10-28 11:30 | 72.86 | 61.85
2019-10-28 12:00 | 58.66 | 44.28
2019-10-28 12:30 | 69.17 | 57.37
2019-10-28 13:00 | 70.3 | 58.95
2019-10-28 13:30 | 38.09 | -6.19
2019-10-28 14:00 | 40.55 | -16.9
2019-10-28 14:30 | 68.89 | 19.27
2019-10-28 15:00 | 80.68 | 56.62
2019-10-28 15:30 | 70.69 | 58.03
2019-10-28 16:00 | 61.93 | 48.2
2019-10-28 16:30 | 66.99 | 55.82
2019-10-28 17:00 | 93.79 | 86.83
2019-10-28 17:30 | 103.88 | 98.54
2019-10-28 18:00 | 123.45 | 119.06
2019-10-28 18:30 | 139 | 134.72
2019-10-28 19:00 | 158.89 | 155.41
2019-10-28 19:30 | 127.52 | 126.94
2019-10-28 20:00 | 105.56 | 105.35
2019-10-28 20:30 | 104.34 | 103.99
2019-10-28 21:00 | 87.2 | 86.55
2019-10-28 21:30 | 68.34 | 67.09
2019-10-28 22:00 | 14.12 | -3.36
2019-10-28 22:30 | 27.8 | -23.74
2019-10-28 23:00 | 31.12 | -27.95
2019-10-28 23:30 | 48.75 | -47.29
2019-10-29 | 37.64 | -35.26
2019-10-29 00:30 | 8.92 | -6.04
2019-10-29 01:00 | 8.58 | -6.59
2019-10-29 01:30 | 21.49 | -21
2019-10-29 02:00 | 12.04 | -5.97
2019-10-29 02:30 | 10.47 | -1.91
2019-10-29 03:00 | 11.32 | 3.95
2019-10-29 03:30 | 10.94 | -0.09
2019-10-29 04:00 | 11.21 | -0.49
2019-10-29 04:30 | 21.25 | -18.42
2019-10-29 05:00 | 11.49 | 3.81
2019-10-29 05:30 | 21.49 | 18.19
2019-10-29 06:00 | 25.97 | 21.31
2019-10-29 06:30 | 31.27 | 27.18
2019-10-29 07:00 | 39.57 | 37.33
2019-10-29 07:30 | 56.44 | 56.31
2019-10-29 08:00 | 38.11 | 37.92
2019-10-29 08:30 | 52.62 | -37.41
2019-10-29 09:00 | 79.49 | -40.11
2019-10-29 09:30 | 48.07 | -4.05
2019-10-29 10:00 | 44.89 | -8.03
2019-10-29 10:30 | 44.92 | -1.76
2019-10-29 11:00 | 61.11 | -38.33
2019-10-29 11:30 | 54.3 | -27.31
2019-10-29 12:00 | 46.79 | -4.18
2019-10-29 12:30 | 46.82 | 6.92
2019-10-29 13:00 | 55.04 | -28.94
2019-10-29 13:30 | 53.52 | -25.72
2019-10-29 14:00 | 56.88 | -32.13
2019-10-29 14:30 | 49.97 | -24.41
2019-10-29 15:00 | 77.15 | -62.31
2019-10-29 15:30 | 87.72 | -73.96
2019-10-29 16:00 | 45.09 | -17.51
2019-10-29 16:30 | 85.69 | -72.86
2019-10-29 17:00 | 74.6 | -62.03
2019-10-29 17:30 | 40.89 | 21.87
2019-10-29 18:00 | 46.78 | -30.56
2019-10-29 18:30 | 59.45 | 48.75
2019-10-29 19:00 | 71.55 | 63.74
2019-10-29 19:30 | 44.8 | -28.16
2019-10-29 20:00 | 25.36 | 15.21
2019-10-29 20:30 | 62.75 | -58.6
2019-10-29 21:00 | 57.04 | -53.84
2019-10-29 21:30 | 44.17 | -41.52
2019-10-29 22:00 | 73.56 | -72.09
2019-10-29 22:30 | 85.84 | -84.42
2019-10-29 23:00 | 71.45 | -70.51
2019-10-29 23:30 | 84.17 | -82.83
2019-10-30 | 89.99 | -88.74
2019-10-30 00:30 | 39.63 | -38.87
2019-10-30 01:00 | 63.45 | -62.55
2019-10-30 01:30 | 53.36 | -53.27
2019-10-30 02:00 | 36.03 | -35.15
2019-10-30 02:30 | 17.13 | -12.67
2019-10-30 03:00 | 19.89 | -15.97
2019-10-30 03:30 | 22.34 | -19.08
2019-10-30 04:00 | 26.83 | -24.61
2019-10-30 04:30 | 35.77 | -34.81
2019-10-30 05:00 | 51.62 | -51.59
2019-10-30 05:30 | 11.14 | -4.46
2019-10-30 06:00 | 9.6 | 2.18
2019-10-30 06:30 | 13.83 | 11.69
2019-10-30 07:00 | 22.85 | 17.96
2019-10-30 07:30 | 51.39 | 47.6
2019-10-30 08:00 | 49.33 | 33.02
2019-10-30 08:30 | 45.98 | -0.43
2019-10-30 09:00 | 49.69 | -7.58
2019-10-30 09:30 | 56.55 | 24.22
2019-10-30 10:00 | 48.5 | -1.04
2019-10-30 10:30 | 53.59 | -21.26
2019-10-30 11:00 | 51.29 | 23.77
2019-10-30 11:30 | 62.94 | 45.55
2019-10-30 12:00 | 51.29 | 24.58
2019-10-30 12:30 | 47.66 | 10.79
2019-10-30 13:00 | 47.41 | 11.21
2019-10-30 13:30 | 50 | 20.61
2019-10-30 14:00 | 64.2 | 46.44
2019-10-30 14:30 | 49.16 | 17.33
2019-10-30 15:00 | 49.09 | -17.76
2019-10-30 15:30 | 50.27 | -22.93
2019-10-30 16:00 | 49.04 | -22.33
2019-10-30 16:30 | 60.32 | 46.7
2019-10-30 17:00 | 44.11 | -17.12
2019-10-30 17:30 | 42.95 | -16.92
2019-10-30 18:00 | 39.85 | -13.08
2019-10-30 18:30 | 40.39 | -10.93
2019-10-30 19:00 | 66.84 | 56.22
2019-10-30 19:30 | 37.71 | -8.82
2019-10-30 20:00 | 41.13 | 32.93
2019-10-30 20:30 | 68.67 | 68.67
2019-10-30 21:00 | 71.07 | 71.03
2019-10-30 21:30 | 67.06 | 66.86
2019-10-30 22:00 | 53.11 | 52.55
2019-10-30 22:30 | 52.29 | 51.66
2019-10-30 23:00 | 46.88 | 46.2
2019-10-30 23:30 | 30.04 | 28
2019-10-31 | 13.59 | 10.85
2019-10-31 00:30 | 9.07 | 9.03
2019-10-31 01:00 | 10.18 | 9.88
2019-10-31 01:30 | 4.03 | 1.38
2019-10-31 02:00 | 6.94 | -4.65
2019-10-31 02:30 | 10.24 | -8.72
2019-10-31 03:00 | 5.3 | -0.68
2019-10-31 03:30 | 11.96 | 11.16
2019-10-31 04:00 | 29.47 | 29.09
2019-10-31 04:30 | 35.16 | 35.02
2019-10-31 05:00 | 38.37 | 38.21
2019-10-31 05:30 | 42.98 | 42.87
2019-10-31 06:00 | 39.62 | 39.62
2019-10-31 06:30 | 18.97 | 18.85
2019-10-31 07:00 | 45.07 | -43.44
2019-10-31 07:30 | 12.09 | 7.35
2019-10-31 08:00 | 20.47 | -17.96
2019-10-31 08:30 | 14.25 | 10.13
2019-10-31 09:00 | 26.89 | 24.68
2019-10-31 09:30 | 29.92 | 27.77
2019-10-31 10:00 | 39.17 | -35.89
2019-10-31 10:30 | 42.78 | -39.46
2019-10-31 11:00 | 35.27 | -30.8
2019-10-31 11:30 | 44.35 | -40.57
2019-10-31 12:00 | 42.74 | -38.65
2019-10-31 12:30 | 39.45 | -34.86
2019-10-31 13:00 | 38.08 | -33.35
2019-10-31 13:30 | 36.8 | -31.38
2019-10-31 14:00 | 23.34 | -14.28
2019-10-31 14:30 | 33.44 | 28.44
2019-10-31 15:00 | 32.81 | 28.72
2019-10-31 15:30 | 40.79 | 37.92
2019-10-31 16:00 | 38.22 | 35.81
2019-10-31 16:30 | 51.91 | 50.69
2019-10-31 17:00 | 72.71 | 72.04
2019-10-31 17:30 | 90.39 | 90.13
2019-10-31 18:00 | 94.54 | 94.42
2019-10-31 18:30 | 104.61 | 104.44
2019-10-31 19:00 | 119.8 | 119.6
2019-10-31 19:30 | 140.69 | 140.61
2019-10-31 20:00 | 128.49 | 128.46
2019-10-31 20:30 | 146.19 | 146.19
2019-10-31 21:00 | 142.29 | 142.28
2019-10-31 21:30 | 121.88 | 121.77
2019-10-31 22:00 | 118.94 | 118.74
2019-10-31 22:30 | 99.21 | 98.85
2019-10-31 23:00 | 105.59 | 105.1
2019-10-31 23:30 | 81.1 | 81.04
2019-11-01 | 60.04 | 60.02
2019-11-01 00:30 | 62.7 | 62.69
2019-11-01 01:00 | 58.37 | 58.36
2019-11-01 01:30 | 48.32 | 48.29
2019-11-01 02:00 | 51.43 | 51.41
2019-11-01 02:30 | 48.38 | 48.34
2019-11-01 03:00 | 33.08 | 32.97
2019-11-01 03:30 | 35.39 | 35.29
2019-11-01 04:00 | 48.06 | 48
2019-11-01 04:30 | 53.64 | 53.61
2019-11-01 05:00 | 74.53 | 74.48
2019-11-01 05:30 | 91.04 | 91.02
2019-11-01 06:00 | 92.77 | 92.66
2019-11-01 06:30 | 78.01 | 77.53
2019-11-01 07:00 | 84.42 | 84.24
2019-11-01 07:30 | 103.69 | 103.67
2019-11-01 08:00 | 112.28 | 110.87
2019-11-01 08:30 | 102.23 | 99.43
2019-11-01 09:00 | 92.97 | 88.97
2019-11-01 09:30 | 105.88 | 101.95
2019-11-01 10:00 | 100.83 | 96.66
2019-11-01 10:30 | 99.51 | 94.99
2019-11-01 11:00 | 106.48 | 102.27
2019-11-01 11:30 | 93.37 | 88.73
2019-11-01 12:00 | 90.75 | 85.75
2019-11-01 12:30 | 93.01 | 88.02
2019-11-01 13:00 | 103.51 | 99.36
2019-11-01 13:30 | 79.12 | 73.96
2019-11-01 14:00 | 85 | 80.73
2019-11-01 14:30 | 86.8 | 83.32
2019-11-01 15:00 | 79.64 | 75.79
2019-11-01 15:30 | 70.45 | 66.86
2019-11-01 16:00 | 46.98 | 41.01
2019-11-01 16:30 | 49.81 | 44.12
2019-11-01 17:00 | 84.18 | 81.6
2019-11-01 17:30 | 104.21 | 102.53
2019-11-01 18:00 | 124.87 | 123.79
2019-11-01 18:30 | 134.73 | 133.59
2019-11-01 19:00 | 154.14 | 152.96
2019-11-01 19:30 | 141.66 | 140.68
2019-11-01 20:00 | 139.6 | 138.84
2019-11-01 20:30 | 153.79 | 153.39
2019-11-01 21:00 | 150.86 | 150.54
2019-11-01 21:30 | 129.79 | 129.57
2019-11-01 22:00 | 116.47 | 116.35
2019-11-01 22:30 | 107.17 | 107.12
2019-11-01 23:00 | 118.6 | 118.58
2019-11-01 23:30 | 113.45 | 113.45
2019-11-02 | 81.04 | 80.66
2019-11-02 00:30 | 79.24 | 76.53
2019-11-02 01:00 | 62.21 | 58.79
2019-11-02 01:30 | 71.52 | 68.27
2019-11-02 02:00 | 62.77 | 57.42
2019-11-02 02:30 | 49.23 | 42.9
2019-11-02 03:00 | 49.04 | 42.77
2019-11-02 03:30 | 50.42 | 44.25
2019-11-02 04:00 | 37.96 | 29.34
2019-11-02 04:30 | 48.69 | 41.96
2019-11-02 05:00 | 61.14 | 56.42
2019-11-02 05:30 | 55.93 | 50.95
2019-11-02 06:00 | 43.28 | 36.7
2019-11-02 06:30 | 21.47 | 6.5
2019-11-02 07:00 | 49.42 | -48.56
2019-11-02 07:30 | 54.06 | -53.97
2019-11-02 08:00 | 26.92 | -26.5
2019-11-02 08:30 | 21.4 | 20.63
2019-11-02 09:00 | 57.69 | 57.54
2019-11-02 09:30 | 72.71 | 72.61
2019-11-02 10:00 | 76.55 | 76.5
2019-11-02 10:30 | 60.72 | 60.45
2019-11-02 11:00 | 44.13 | 40.74
2019-11-02 11:30 | 47.01 | 44.17
2019-11-02 12:00 | 30.08 | 25.11
2019-11-02 12:30 | 55.63 | -51.47
2019-11-02 13:00 | 46.8 | -42.03
2019-11-02 13:30 | 66.35 | -62.85
2019-11-02 14:00 | 37.85 | -31.97
2019-11-02 14:30 | 82.78 | -79.22
2019-11-02 15:00 | 93.24 | -89.67
2019-11-02 15:30 | 98.49 | -94.68
2019-11-02 16:00 | 71.14 | -66.64
2019-11-02 16:30 | 21.24 | -4.64
2019-11-02 17:00 | 56.22 | 53.41
2019-11-02 17:30 | 61.87 | 59.61
2019-11-02 18:00 | 89.38 | 88.17
2019-11-02 18:30 | 107.37 | 106.22
2019-11-02 19:00 | 128.94 | 127.74
2019-11-02 19:30 | 118.09 | 117.06
2019-11-02 20:00 | 112.22 | 111.37
2019-11-02 20:30 | 115.66 | 115.64
2019-11-02 21:00 | 97.04 | 96.64
2019-11-02 21:30 | 77.46 | 76.73
2019-11-02 22:00 | 58.98 | 57.62
2019-11-02 22:30 | 74.01 | 72.38
2019-11-02 23:00 | 84.34 | 82.65
2019-11-02 23:30 | 55.6 | 52.65
2019-11-03 | 31.01 | 24.14
2019-11-03 00:30 | 29.03 | 21.87
2019-11-03 01:00 | 34 | 27.72
2019-11-03 01:30 | 31.45 | 24.85
2019-11-03 02:00 | 31.31 | 25.27
2019-11-03 02:30 | 31.91 | 26.28
2019-11-03 03:00 | 24.38 | 17.39
2019-11-03 03:30 | 18.28 | 5.97
2019-11-03 04:00 | 17.81 | -3.85
2019-11-03 04:30 | 17.43 | 1.69
2019-11-03 05:00 | 17.03 | -0.58
2019-11-03 05:30 | 18.62 | 2.99
2019-11-03 06:00 | 17.29 | -2.14
2019-11-03 06:30 | 71.35 | -71.24
2019-11-03 07:00 | 62.72 | -62.55
2019-11-03 07:30 | 87.67 | -86.31
2019-11-03 08:00 | 90.24 | -84.62
2019-11-03 08:30 | 97.05 | -88.87
2019-11-03 09:00 | 36.06 | -13.88
2019-11-03 09:30 | 36.95 | 16.25
2019-11-03 10:00 | 35.86 | 10.23
2019-11-03 10:30 | 35.63 | 2.8
2019-11-03 11:00 | 70.95 | -59.72
2019-11-03 11:30 | 92.1 | -81.11
2019-11-03 12:00 | 84.72 | -72.69
2019-11-03 12:30 | 83.14 | -70.97
2019-11-03 13:00 | 91.71 | -80.3
2019-11-03 13:30 | 70.06 | -55.94
2019-11-03 14:00 | 48.62 | -29.1
2019-11-03 14:30 | 71.88 | -58.2
2019-11-03 15:00 | 99.25 | -83.06
2019-11-03 15:30 | 56.75 | -1.43
2019-11-03 16:00 | 63.35 | -26.42
2019-11-03 16:30 | 67.58 | 34.65
2019-11-03 17:00 | 104.6 | 80.09
2019-11-03 17:30 | 141 | 124.85
2019-11-03 18:00 | 173.26 | 166.83
2019-11-03 18:30 | 197.03 | 192.48
2019-11-03 19:00 | 197.83 | 195.95
2019-11-03 19:30 | 179.23 | 179.12
2019-11-03 20:00 | 168.89 | 168.74
2019-11-03 20:30 | 160.29 | 159.99
2019-11-03 21:00 | 134.47 | 133.9
2019-11-03 21:30 | 121.11 | 120.26
2019-11-03 22:00 | 106.44 | 105.09
2019-11-03 22:30 | 101.47 | 99.77
2019-11-03 23:00 | 104.39 | 102.46
2019-11-03 23:30 | 82.25 | 79.46
2019-11-04 | 42.11 | 36.48
2019-11-04 00:30 | 47.09 | 42.53
2019-11-04 01:00 | 59.67 | 56.35
2019-11-04 01:30 | 77.87 | 76.85
2019-11-04 02:00 | 77.73 | 76.5
2019-11-04 02:30 | 80.37 | 79
2019-11-04 03:00 | 71.95 | 69.64
2019-11-04 03:30 | 63.9 | 61.1
2019-11-04 04:00 | 60.86 | 57.9
2019-11-04 04:30 | 74.42 | 71.82
2019-11-04 05:00 | 68.15 | 64.96
2019-11-04 05:30 | 72.75 | 69.23
2019-11-04 06:00 | 60.23 | 56.21
2019-11-04 06:30 | 61.92 | 59.78
2019-11-04 07:00 | 58.36 | 56.95
2019-11-04 07:30 | 94.03 | 94.03
2019-11-04 08:00 | 121.12 | 121.03
2019-11-04 08:30 | 138.98 | 133.42
2019-11-04 09:00 | 131.26 | 124.67
2019-11-04 09:30 | 103.22 | 100.53
2019-11-04 10:00 | 87.57 | 84.55
2019-11-04 10:30 | 84.42 | 80.41
2019-11-04 11:00 | 102.45 | 90.81
2019-11-04 11:30 | 120.65 | 110.5
2019-11-04 12:00 | 130 | 120.73
2019-11-04 12:30 | 142.39 | 133.89
2019-11-04 13:00 | 156.54 | 152.85
2019-11-04 13:30 | 150.13 | 146.99
2019-11-04 14:00 | 147.64 | 144.5
2019-11-04 14:30 | 147.26 | 143.96
2019-11-04 15:00 | 149.74 | 146.59
2019-11-04 15:30 | 186.6 | 184.11
2019-11-04 16:00 | 182.61 | 180.6
2019-11-04 16:30 | 192.5 | 191.01
2019-11-04 17:00 | 210.33 | 209.47
2019-11-04 17:30 | 221.55 | 221.55
2019-11-04 18:00 | 222.14 | 222.14
2019-11-04 18:30 | 228.89 | 228.8
2019-11-04 19:00 | 236.56 | 236.49
2019-11-04 19:30 | 219.9 | 219.81
2019-11-04 20:00 | 203.12 | 202.86
2019-11-04 20:30 | 213.26 | 213
2019-11-04 21:00 | 184.25 | 183.68
2019-11-04 21:30 | 156.97 | 156.64
2019-11-04 22:00 | 124.69 | 123.96
2019-11-04 22:30 | 102.82 | 101.63
2019-11-04 23:00 | 105.71 | 104.42
2019-11-04 23:30 | 82.03 | 79.94
2019-11-05 | 46.69 | 42.78
2019-11-05 00:30 | 51.32 | 48.8
2019-11-05 01:00 | 46.03 | 43.36
2019-11-05 01:30 | 50.82 | 48.88
2019-11-05 02:00 | 42.84 | 40.96
2019-11-05 02:30 | 39 | 37.18
2019-11-05 03:00 | 28.68 | 26.18
2019-11-05 03:30 | 39.63 | 37.66
2019-11-05 04:00 | 43.93 | 42.15
2019-11-05 04:30 | 42.9 | 40.93
2019-11-05 05:00 | 50.23 | 49.06
2019-11-05 05:30 | 36.69 | 34.61
2019-11-05 06:00 | 39.1 | 36.37
2019-11-05 06:30 | 29.22 | 28.44
2019-11-05 07:00 | 42.55 | 42.52
2019-11-05 07:30 | 54.49 | 54.15
2019-11-05 08:00 | 32.78 | 32.31
2019-11-05 08:30 | 39.57 | -34.87
2019-11-05 09:00 | 29.28 | -19.63
2019-11-05 09:30 | 37.03 | 30.85
2019-11-05 10:00 | 71.05 | 67.69
2019-11-05 10:30 | 88.23 | 87.27
2019-11-05 11:00 | 114.33 | 114.27
2019-11-05 11:30 | 115.3 | 114.99
2019-11-05 12:00 | 94.39 | 92.53
2019-11-05 12:30 | 90.1 | 88.69
2019-11-05 13:00 | 94.43 | 91.93
2019-11-05 13:30 | 95.71 | 93.74
2019-11-05 14:00 | 83.13 | 81.31
2019-11-05 14:30 | 85.17 | 80.35
2019-11-05 15:00 | 80.06 | 75.66
2019-11-05 15:30 | 95.35 | 95.14
2019-11-05 16:00 | 112.34 | 111.28
2019-11-05 16:30 | 138.82 | 137.74
2019-11-05 17:00 | 151.59 | 151.04
2019-11-05 17:30 | 178.54 | 178.23
2019-11-05 18:00 | 171.27 | 170.84
2019-11-05 18:30 | 169.54 | 169.17
2019-11-05 19:00 | 176.55 | 176.19
2019-11-05 19:30 | 148.29 | 147.89
2019-11-05 20:00 | 135.23 | 134.83
2019-11-05 20:30 | 141.37 | 141.35
2019-11-05 21:00 | 119.25 | 119.07
2019-11-05 21:30 | 98.38 | 97.1
2019-11-05 22:00 | 82.72 | 80.2
2019-11-05 22:30 | 85.36 | 82.42
2019-11-05 23:00 | 82.21 | 78.88
2019-11-05 23:30 | 67.46 | 63.77
2019-11-06 | 36.88 | 33.58
2019-11-06 00:30 | 47.88 | 47.5
2019-11-06 01:00 | 50.99 | 50.78
2019-11-06 01:30 | 46.36 | 46.08
2019-11-06 02:00 | 35.53 | 34.26
2019-11-06 02:30 | 32.06 | 30.33
2019-11-06 03:00 | 27.19 | 25.16
2019-11-06 03:30 | 30.46 | 28.48
2019-11-06 04:00 | 35.54 | 33.82
2019-11-06 04:30 | 47.92 | 46.47
2019-11-06 05:00 | 56.19 | 55.32
2019-11-06 05:30 | 48.18 | 46.58
2019-11-06 06:00 | 53.57 | 51.72
2019-11-06 06:30 | 44.01 | 43.54
2019-11-06 07:00 | 28.27 | 25.69
2019-11-06 07:30 | 31.13 | 28.7
2019-11-06 08:00 | 10.11 | 5.83
2019-11-06 08:30 | 16.15 | -15.97
2019-11-06 09:00 | 10.21 | 9.46
2019-11-06 09:30 | 35.49 | 35.21
2019-11-06 10:00 | 15.35 | 13.2
2019-11-06 10:30 | 36.58 | 35.25
2019-11-06 11:00 | 45.96 | 44.78
2019-11-06 11:30 | 50.17 | 49.46
2019-11-06 12:00 | 64.45 | 64.1
2019-11-06 12:30 | 40.61 | 40.11
2019-11-06 13:00 | 34.16 | 33.48
2019-11-06 13:30 | 50.63 | 50.04
2019-11-06 14:00 | 66.38 | 65.98
2019-11-06 14:30 | 89.15 | 88.87
2019-11-06 15:00 | 85.42 | 85.2
2019-11-06 15:30 | 103.57 | 103.44
2019-11-06 16:00 | 131.9 | 131.84
2019-11-06 16:30 | 135.97 | 135.92
2019-11-06 17:00 | 144.07 | 144.04
2019-11-06 17:30 | 168.25 | 168.25
2019-11-06 18:00 | 193.92 | 193.9
2019-11-06 18:30 | 194.24 | 193.91
2019-11-06 19:00 | 205.49 | 205.26
2019-11-06 19:30 | 191.32 | 191.14
2019-11-06 20:00 | 183.02 | 182.63
2019-11-06 20:30 | 182.86 | 182.2
2019-11-06 21:00 | 173.67 | 172.91
2019-11-06 21:30 | 164.73 | 164.07
2019-11-06 22:00 | 166.29 | 165.45
2019-11-06 22:30 | 160.36 | 159.41
2019-11-06 23:00 | 156.14 | 154.83
2019-11-06 23:30 | 132.7 | 132.42
2019-11-07 | 100.81 | 100.81
2019-11-07 00:30 | 97.61 | 96.15
2019-11-07 01:00 | 89.88 | 89.56
2019-11-07 01:30 | 88.42 | 88.24
2019-11-07 02:00 | 87.14 | 86.9
2019-11-07 02:30 | 90.31 | 90.1
2019-11-07 03:00 | 90.91 | 90.72
2019-11-07 03:30 | 91.2 | 91.1
2019-11-07 04:00 | 86.55 | 86.52
2019-11-07 04:30 | 93.02 | 92.95
2019-11-07 05:00 | 97.51 | 97.32
2019-11-07 05:30 | 109.53 | 109.41
2019-11-07 06:00 | 87.14 | 87.12
2019-11-07 06:30 | 56.97 | 56.29
2019-11-07 07:00 | 66.31 | 64
2019-11-07 07:30 | 52.45 | 50.38
2019-11-07 08:00 | 39.64 | 39.25
2019-11-07 08:30 | 13.2 | 1.41
2019-11-07 09:00 | 25.94 | -1.31
2019-11-07 09:30 | 29.03 | 0.81
2019-11-07 10:00 | 30.22 | 7.23
2019-11-07 10:30 | 34.49 | 15.19
2019-11-07 11:00 | 47.13 | 18.6
2019-11-07 11:30 | 55.6 | 19.26
2019-11-07 12:00 | 81.39 | 42.88
2019-11-07 12:30 | 73.75 | 46.73
2019-11-07 13:00 | 75.16 | 56.36
2019-11-07 13:30 | 92.27 | 62.75
2019-11-07 14:00 | 117.48 | 96.44
2019-11-07 14:30 | 110.85 | 89.35
2019-11-07 15:00 | 111.93 | 91.11
2019-11-07 15:30 | 111.67 | 91.86
2019-11-07 16:00 | 70.68 | 13.13
2019-11-07 16:30 | 87.91 | 58.29
2019-11-07 17:00 | 178.36 | 168.98
2019-11-07 17:30 | 213.3 | 209.9
2019-11-07 18:00 | 216.18 | 216.09
2019-11-07 18:30 | 221.77 | 221.6
2019-11-07 19:00 | 229.75 | 229.75
2019-11-07 19:30 | 218.77 | 218.72
2019-11-07 20:00 | 216.62 | 216.62
2019-11-07 20:30 | 204.83 | 204.8
2019-11-07 21:00 | 198.42 | 198.31
2019-11-07 21:30 | 175.29 | 174.94
2019-11-07 22:00 | 158.68 | 157.89
2019-11-07 22:30 | 154.27 | 153.16
2019-11-07 23:00 | 143.12 | 141.56
2019-11-07 23:30 | 116.24 | 114.46
2019-11-08 | 99.23 | 97.45
2019-11-08 00:30 | 98.72 | 97.34
2019-11-08 01:00 | 106.89 | 105.66
2019-11-08 01:30 | 114 | 112.88
2019-11-08 02:00 | 110.9 | 109.72
2019-11-08 02:30 | 98.08 | 98.04
2019-11-08 03:00 | 106.27 | 106.15
2019-11-08 03:30 | 97.07 | 96.94
2019-11-08 04:00 | 102.07 | 101.94
2019-11-08 04:30 | 96.24 | 96.1
2019-11-08 05:00 | 97.39 | 97.13
2019-11-08 05:30 | 91.78 | 91.51
2019-11-08 06:00 | 81.13 | 81.01
2019-11-08 06:30 | 71.05 | 71.01
2019-11-08 07:00 | 57.97 | 57.78
2019-11-08 07:30 | 67.46 | 65.59
2019-11-08 08:00 | 77.51 | 76.27
2019-11-08 08:30 | 77.95 | 77.78
2019-11-08 09:00 | 75.83 | 74.98
2019-11-08 09:30 | 64.92 | -36.99
2019-11-08 10:00 | 78.81 | 40.25
2019-11-08 10:30 | 103.78 | 77.84
2019-11-08 11:00 | 156.62 | 140.47
2019-11-08 11:30 | 175.11 | 159.93
2019-11-08 12:00 | 177.62 | 164.45
2019-11-08 12:30 | 189.35 | 177.53
2019-11-08 13:00 | 197.34 | 185.84
2019-11-08 13:30 | 201.7 | 190.14
2019-11-08 14:00 | 204.04 | 192.83
2019-11-08 14:30 | 217.87 | 206.81
2019-11-08 15:00 | 221.22 | 217.89
2019-11-08 15:30 | 238.72 | 236.03
2019-11-08 16:00 | 248.62 | 245.54
2019-11-08 16:30 | 257.76 | 254.59
2019-11-08 17:00 | 267.8 | 264.84
2019-11-08 17:30 | 263.96 | 261.68
2019-11-08 18:00 | 256.6 | 255.19
2019-11-08 18:30 | 250.72 | 249.62
2019-11-08 19:00 | 253.22 | 251.96
2019-11-08 19:30 | 246.97 | 246.43
2019-11-08 20:00 | 204.43 | 204.03
2019-11-08 20:30 | 96.08 | 96.02
2019-11-08 21:00 | 4.87 | -0.9
2019-11-08 21:30 | 41.12 | -40.43
2019-11-08 22:00 | 77.86 | -77.31
2019-11-08 22:30 | 77.3 | -77.14
2019-11-08 23:00 | 65.79 | -65.73
2019-11-08 23:30 | 82.89 | -80.18
2019-11-09 | 95.65 | -94.82
2019-11-09 00:30 | 79.07 | -79.05
2019-11-09 01:00 | 72.36 | -72.09
2019-11-09 01:30 | 88.94 | -88.91
2019-11-09 02:00 | 81.3 | -81.29
2019-11-09 02:30 | 69.84 | -69.48
2019-11-09 03:00 | 85.98 | -85.96
2019-11-09 03:30 | 85.68 | -85.68
2019-11-09 04:00 | 85.53 | -85.53
2019-11-09 04:30 | 81.78 | -81.76
2019-11-09 05:00 | 81 | -80.98
2019-11-09 05:30 | 70.8 | -69.93
2019-11-09 06:00 | 88.62 | -85.76
2019-11-09 06:30 | 91.28 | -88.71
2019-11-09 07:00 | 91.51 | -90.91
2019-11-09 07:30 | 82.6 | -82.56
2019-11-09 08:00 | 56.75 | -56.75
2019-11-09 08:30 | 64.06 | -63.88
2019-11-09 09:00 | 97.69 | -96.78
2019-11-09 09:30 | 85.38 | -84.06
2019-11-09 10:00 | 89.12 | -87.28
2019-11-09 10:30 | 92.8 | -90.3
2019-11-09 11:00 | 90.42 | -88.25
2019-11-09 11:30 | 92.15 | -90.29
2019-11-09 12:00 | 92.1 | -90.27
2019-11-09 12:30 | 47.43 | -46.71
2019-11-09 13:00 | 44.86 | -44.26
2019-11-09 13:30 | 42.99 | -42.5
2019-11-09 14:00 | 42.49 | -42.46
2019-11-09 14:30 | 38.47 | -38.45
2019-11-09 15:00 | 59.03 | -58.92
2019-11-09 15:30 | 101.27 | -99.19
2019-11-09 16:00 | 94.16 | -91.86
2019-11-09 16:30 | 33.94 | -33.68
2019-11-09 17:00 | 27.43 | -27.03
2019-11-09 17:30 | 37.13 | 36.96
2019-11-09 18:00 | 87.29 | 86.9
2019-11-09 18:30 | 61.84 | 61.21
2019-11-09 19:00 | 46.73 | 45.11
2019-11-09 19:30 | 28.27 | 22.94
2019-11-09 20:00 | 75.5 | 75.47
2019-11-09 20:30 | 15.82 | 14.52
2019-11-09 21:00 | 20.55 | -20.5
2019-11-09 21:30 | 30.59 | -30.31
2019-11-09 22:00 | 66.54 | -66.54
2019-11-09 22:30 | 35.79 | -34.65
2019-11-09 23:00 | 31.64 | -29.65
2019-11-09 23:30 | 67.04 | -66.41
2019-11-10 | 82.7 | -82.62
2019-11-10 00:30 | 83.91 | -83.86
2019-11-10 01:00 | 82.88 | -82.84
2019-11-10 01:30 | 87.8 | -87.8
2019-11-10 02:00 | 84.14 | -84.13
2019-11-10 02:30 | 68.01 | -67.8
2019-11-10 03:00 | 68.38 | -68.34
2019-11-10 03:30 | 72.45 | -72.17
2019-11-10 04:00 | 62.96 | -62.9
2019-11-10 04:30 | 72.92 | -72.63
2019-11-10 05:00 | 68.19 | -67.79
2019-11-10 05:30 | 84.2 | -82.6
2019-11-10 06:00 | 92.59 | -88.55
2019-11-10 06:30 | 93.77 | -89.85
2019-11-10 07:00 | 91.56 | -88.2
2019-11-10 07:30 | 87.69 | -85.24
2019-11-10 08:00 | 99.29 | -96.53
2019-11-10 08:30 | 103 | -100.91
2019-11-10 09:00 | 100.96 | -99.41
2019-11-10 09:30 | 101.06 | -99.86
2019-11-10 10:00 | 102.51 | -101.7
2019-11-10 10:30 | 103.98 | -103.74
2019-11-10 11:00 | 74.36 | -74.3
2019-11-10 11:30 | 72.49 | -72.44
2019-11-10 12:00 | 71.45 | -71.39
2019-11-10 12:30 | 70.72 | -70.66
2019-11-10 13:00 | 68.08 | -68.01
2019-11-10 13:30 | 64.98 | -64.92
2019-11-10 14:00 | 63.85 | -63.79
2019-11-10 14:30 | 61.96 | -61.87
2019-11-10 15:00 | 60.37 | -60.24
2019-11-10 15:30 | 57.64 | -57.51
2019-11-10 16:00 | 54.63 | -54.57
2019-11-10 16:30 | 51.63 | -51.48
2019-11-10 17:00 | 50.71 | -50.5
2019-11-10 17:30 | 65.94 | -64.64
2019-11-10 18:00 | 67.66 | -65.56
2019-11-10 18:30 | 62.93 | -60.12
2019-11-10 19:00 | 57.74 | -54.22
2019-11-10 19:30 | 60.97 | -56.64
2019-11-10 20:00 | 59.28 | -53.18
2019-11-10 20:30 | 14.98 | 14.23
2019-11-10 21:00 | 11.94 | 10.73
2019-11-10 21:30 | 8.47 | -4.69
2019-11-10 22:00 | 60.11 | -60.09
2019-11-10 22:30 | 58.04 | -58
2019-11-10 23:00 | 20.87 | -18.04
2019-11-10 23:30 | 13.06 | -1.91
2019-11-11 | 64.89 | -64.87
2019-11-11 00:30 | 23.74 | -20.93
2019-11-11 01:00 | 46.41 | -45.64
2019-11-11 01:30 | 61.71 | -61.52
2019-11-11 02:00 | 47.53 | -47.41
2019-11-11 02:30 | 54.76 | -54.08
2019-11-11 03:00 | 72.31 | -70.19
2019-11-11 03:30 | 70.51 | -68.58
2019-11-11 04:00 | 61.33 | -59.94
2019-11-11 04:30 | 4.28 | 3.27
2019-11-11 05:00 | 10.4 | 10.34
2019-11-11 05:30 | 62 | -59.62
2019-11-11 06:00 | 51.13 | -50.27
2019-11-11 06:30 | 71.01 | -68.65
2019-11-11 07:00 | 67.59 | -67.31
2019-11-11 07:30 | 64.49 | -63.88
2019-11-11 08:00 | 61.14 | -59.82
2019-11-11 08:30 | 63.84 | -60.98
2019-11-11 09:00 | 60.5 | -58.51
2019-11-11 09:30 | 66.02 | -63.23
2019-11-11 10:00 | 64.33 | -61.2
2019-11-11 10:30 | 63.57 | -60.13
2019-11-11 11:00 | 62.67 | -58.76
2019-11-11 11:30 | 62.94 | -58.96
2019-11-11 12:00 | 63.31 | -59.25
2019-11-11 12:30 | 61.47 | -57.34
2019-11-11 13:00 | 61.37 | -57.27
2019-11-11 13:30 | 60.49 | -56.41
2019-11-11 14:00 | 60.46 | -56.42
2019-11-11 14:30 | 60.43 | -50.66
2019-11-11 15:00 | 71.64 | -49.91
2019-11-11 15:30 | 70.2 | -49.73
2019-11-11 16:00 | 68.74 | -48.04
2019-11-11 16:30 | 55.55 | -30.37
2019-11-11 17:00 | 26.18 | 2.47
2019-11-11 17:30 | 160.47 | 160.12
2019-11-11 18:00 | 181.21 | 181.2
2019-11-11 18:30 | 198.03 | 196.88
2019-11-11 19:00 | 214.34 | 212.78
2019-11-11 19:30 | 205.72 | 204.5
2019-11-11 20:00 | 195.47 | 195.46
2019-11-11 20:30 | 189.38 | 189.35
2019-11-11 21:00 | 174.41 | 174.32
2019-11-11 21:30 | 151.13 | 150.89
2019-11-11 22:00 | 139.75 | 139.3
2019-11-11 22:30 | 119.89 | 119.31
2019-11-11 23:00 | 122.18 | 121.45
2019-11-11 23:30 | 102.62 | 101.54
2019-11-12 | 83.46 | 81.87
2019-11-12 00:30 | 99.47 | 98.4
2019-11-12 01:00 | 93.8 | 92.59
2019-11-12 01:30 | 100.6 | 99.34
2019-11-12 02:00 | 88.11 | 87.4
2019-11-12 02:30 | 83.18 | 83.04
2019-11-12 03:00 | 83.07 | 82.96
2019-11-12 03:30 | 82.37 | 82.29
2019-11-12 04:00 | 85.87 | 85.83
2019-11-12 04:30 | 80.97 | 80.89
2019-11-12 05:00 | 85.03 | 85.03
2019-11-12 05:30 | 43.31 | 43.3
2019-11-12 06:00 | 21.43 | 21.41
2019-11-12 06:30 | 32.4 | -32.18
2019-11-12 07:00 | 39.97 | -38.39
2019-11-12 07:30 | 25.44 | 7.18
2019-11-12 08:00 | 22.69 | -15.82
2019-11-12 08:30 | 31.19 | -23.84
2019-11-12 09:00 | 35.05 | -25.09
2019-11-12 09:30 | 40.41 | -27.88
2019-11-12 10:00 | 35.5 | -25.34
2019-11-12 10:30 | 32.94 | -24.26
2019-11-12 11:00 | 29.09 | -20.03
2019-11-12 11:30 | 20.97 | -5.32
2019-11-12 12:00 | 31.13 | -22.16
2019-11-12 12:30 | 28.92 | -18.08
2019-11-12 13:00 | 19.76 | 0.93
2019-11-12 13:30 | 121.08 | 120.87
2019-11-12 14:00 | 144.86 | 144.74
2019-11-12 14:30 | 158.09 | 157.99
2019-11-12 15:00 | 138.18 | 138.09
2019-11-12 15:30 | 169 | 168.79
2019-11-12 16:00 | 174.58 | 174.34
2019-11-12 16:30 | 166.32 | 166.11
2019-11-12 17:00 | 200.38 | 198.64
2019-11-12 17:30 | 191.16 | 189.45
2019-11-12 18:00 | 206.14 | 204.93
2019-11-12 18:30 | 228.64 | 227.89
2019-11-12 19:00 | 244.65 | 243.88
2019-11-12 19:30 | 227.47 | 227.18
2019-11-12 20:00 | 212 | 211.86
2019-11-12 20:30 | 220.18 | 220.17
2019-11-12 21:00 | 199.57 | 199.34
2019-11-12 21:30 | 181.4 | 181.29
2019-11-12 22:00 | 158.46 | 158.44
2019-11-12 22:30 | 149.79 | 149.79
2019-11-12 23:00 | 148.05 | 147.97
2019-11-12 23:30 | 130.99 | 130.9
2019-11-13 | 116.37 | 116.33
2019-11-13 00:30 | 123.42 | 123.41
2019-11-13 01:00 | 124.4 | 124.39
2019-11-13 01:30 | 115.04 | 115.04
2019-11-13 02:00 | 114.04 | 114.04
2019-11-13 02:30 | 113.66 | 113.66
2019-11-13 03:00 | 112.68 | 112.67
2019-11-13 03:30 | 109.05 | 109.02
2019-11-13 04:00 | 105.9 | 105.87
2019-11-13 04:30 | 99.18 | 99.15
2019-11-13 05:00 | 98.02 | 98.02
2019-11-13 05:30 | 94.97 | 94.97
2019-11-13 06:00 | 90.59 | 90.59
2019-11-13 06:30 | 64.45 | 60.3
2019-11-13 07:00 | 70.14 | 62.07
2019-11-13 07:30 | 55.92 | 16.72
2019-11-13 08:00 | 47.06 | -19.62
2019-11-13 08:30 | 51.92 | -22.08
2019-11-13 09:00 | 49.64 | 6.45
2019-11-13 09:30 | 87.88 | 70.78
2019-11-13 10:00 | 78.25 | -12.73
2019-11-13 10:30 | 80.76 | 22.11
2019-11-13 11:00 | 122.76 | 97.73
2019-11-13 11:30 | 139.49 | 118.55
2019-11-13 12:00 | 150.42 | 131.29
2019-11-13 12:30 | 158.63 | 140.76
2019-11-13 13:00 | 152.59 | 134.17
2019-11-13 13:30 | 130.85 | 111.72
2019-11-13 14:00 | 125.98 | 106.4
2019-11-13 14:30 | 134.22 | 115.76
2019-11-13 15:00 | 131.33 | 113.88
2019-11-13 15:30 | 134.85 | 118.84
2019-11-13 16:00 | 137.64 | 123
2019-11-13 16:30 | 131.36 | 128.5
2019-11-13 17:00 | 135.85 | 133.7
2019-11-13 17:30 | 133.6 | 132.44
2019-11-13 18:00 | 109.48 | 109.48
2019-11-13 18:30 | 121.53 | 121.5
2019-11-13 19:00 | 128.22 | 128.19
2019-11-13 19:30 | 116.83 | 116.79
2019-11-13 20:00 | 41.43 | 39.54
2019-11-13 20:30 | 56.31 | 55.89
2019-11-13 21:00 | 12.57 | 2.18
2019-11-13 21:30 | 83.49 | 83.48
2019-11-13 22:00 | 43.27 | 42.68
2019-11-13 22:30 | 74.94 | 74.29
2019-11-13 23:00 | 70.98 | 70.09
2019-11-13 23:30 | 55.31 | 53.93
2019-11-14 | 12.75 | 6.1
2019-11-14 00:30 | 35.91 | 34.08
2019-11-14 01:00 | 31.82 | 29.84
2019-11-14 01:30 | 28.23 | 25.81
2019-11-14 02:00 | 26.3 | 23.56
2019-11-14 02:30 | 24.82 | 21.9
2019-11-14 03:00 | 23.07 | 20.1
2019-11-14 03:30 | 23.9 | 20.82
2019-11-14 04:00 | 23.65 | 20.74
2019-11-14 04:30 | 26.6 | 23.65
2019-11-14 05:00 | 10.63 | 4.53
2019-11-14 05:30 | 37.91 | -37.74
2019-11-14 06:00 | 12.6 | -12.34
2019-11-14 06:30 | 47.57 | -47.48
2019-11-14 07:00 | 44.22 | -38.55
2019-11-14 07:30 | 39.57 | -29.29
2019-11-14 08:00 | 41.11 | -27.26
2019-11-14 08:30 | 68.81 | -27.52
2019-11-14 09:00 | 91.91 | -27.98
2019-11-14 09:30 | 95.34 | -33.57
2019-11-14 10:00 | 93.14 | -22.56
2019-11-14 10:30 | 96.72 | -31.14
2019-11-14 11:00 | 94.68 | -20.15
2019-11-14 11:30 | 92.81 | -9.6
2019-11-14 12:00 | 91.22 | 11.04
2019-11-14 12:30 | 94.92 | -26.91
2019-11-14 13:00 | 90.72 | -14.02
2019-11-14 13:30 | 95.04 | 32.69
2019-11-14 14:00 | 114.47 | 71.7
2019-11-14 14:30 | 121.13 | 81.85
2019-11-14 15:00 | 123 | 86.78
2019-11-14 15:30 | 126.97 | 94.37
2019-11-14 16:00 | 130.31 | 99.69
2019-11-14 16:30 | 140.08 | 113.47
2019-11-14 17:00 | 147.19 | 122.58
2019-11-14 17:30 | 147.75 | 124.91
2019-11-14 18:00 | 149.04 | 127.57
2019-11-14 18:30 | 151.8 | 130.72
2019-11-14 19:00 | 159.08 | 138.04
2019-11-14 19:30 | 154.97 | 134.31
2019-11-14 20:00 | 125.65 | 100.15
2019-11-14 20:30 | 121.84 | 107.37
2019-11-14 21:00 | 117.61 | 105.55
2019-11-14 21:30 | 92.77 | 79.03
2019-11-14 22:00 | 58.96 | 37.55
2019-11-14 22:30 | 40.6 | 38.99
2019-11-14 23:00 | 2.01 | -1.2
2019-11-14 23:30 | 40.52 | -38.37
2019-11-15 | 56.41 | -54.95
2019-11-15 00:30 | 8.25 | 0.48
2019-11-15 01:00 | 28.36 | 27.55
2019-11-15 01:30 | 30.35 | 30.14
2019-11-15 02:00 | 31.55 | 26.6
2019-11-15 02:30 | 29.8 | 24.56
2019-11-15 03:00 | 28.98 | 23.4
2019-11-15 03:30 | 29.48 | 23.72
2019-11-15 04:00 | 28.76 | 24.25
2019-11-15 04:30 | 30.58 | 26.73
2019-11-15 05:00 | 15.73 | 9.12
2019-11-15 05:30 | 10.57 | -3.56
2019-11-15 06:00 | 12.89 | -11.06
2019-11-15 06:30 | 43.98 | -42.81
2019-11-15 07:00 | 49.63 | -34.42
2019-11-15 07:30 | 46.65 | -22.59
2019-11-15 08:00 | 48.51 | -19.41
2019-11-15 08:30 | 52.53 | -19.38
2019-11-15 09:00 | 72.03 | -17.42
2019-11-15 09:30 | 76.89 | -19.76
2019-11-15 10:00 | 78.31 | -18.99
2019-11-15 10:30 | 80.64 | -18.05
2019-11-15 11:00 | 79 | -4.99
2019-11-15 11:30 | 103.34 | 72.36
2019-11-15 12:00 | 113.98 | 86.48
2019-11-15 12:30 | 117.96 | 91.2
2019-11-15 13:00 | 122.59 | 96.72
2019-11-15 13:30 | 115.07 | 97.33
2019-11-15 14:00 | 81.04 | 54.41
2019-11-15 14:30 | 87.86 | 69.31
2019-11-15 15:00 | 129.95 | 119.65
2019-11-15 15:30 | 145.33 | 136.54
2019-11-15 16:00 | 159.11 | 150.82
2019-11-15 16:30 | 163.13 | 155.49
2019-11-15 17:00 | 168.04 | 161.18
2019-11-15 17:30 | 164.15 | 158.38
2019-11-15 18:00 | 158.02 | 153.36
2019-11-15 18:30 | 155.13 | 147.75
2019-11-15 19:00 | 162.16 | 152.87
2019-11-15 19:30 | 157.96 | 149.1
2019-11-15 20:00 | 151.93 | 143.32
2019-11-15 20:30 | 138.97 | 135.01
2019-11-15 21:00 | 120.93 | 120.16
2019-11-15 21:30 | 113.06 | 112.58
2019-11-15 22:00 | 101.49 | 101.25
2019-11-15 22:30 | 96.54 | 96.39
2019-11-15 23:00 | 93.6 | 93.54
2019-11-15 23:30 | 78.99 | 78.99
2019-11-16 | 60.04 | 60.04
2019-11-16 00:30 | 51.46 | 51.36
2019-11-16 01:00 | 45.45 | 45.43
2019-11-16 01:30 | 39.77 | 39.77
2019-11-16 02:00 | 37.74 | 35.03
2019-11-16 02:30 | 36.87 | 31.23
2019-11-16 03:00 | 35.74 | 29.78
2019-11-16 03:30 | 35.19 | 28.98
2019-11-16 04:00 | 33.85 | 27.27
2019-11-16 04:30 | 34.3 | 27.38
2019-11-16 05:00 | 30.74 | 26.01
2019-11-16 05:30 | 29.98 | 27.44
2019-11-16 06:00 | 33.73 | 30.56
2019-11-16 06:30 | 36.96 | 32.14
2019-11-16 07:00 | 28.27 | 19.27
2019-11-16 07:30 | 23.56 | -20.12
2019-11-16 08:00 | 3.94 | -3.83
2019-11-16 08:30 | 6.08 | -0.11
2019-11-16 09:00 | 18.03 | -14.04
2019-11-16 09:30 | 41.35 | 39.2
2019-11-16 10:00 | 57.32 | 48.46
2019-11-16 10:30 | 79.45 | 74.79
2019-11-16 11:00 | 93.25 | 86.85
2019-11-16 11:30 | 97.68 | 91
2019-11-16 12:00 | 101.16 | 94.16
2019-11-16 12:30 | 105.76 | 99.13
2019-11-16 13:00 | 109.63 | 106.63
2019-11-16 13:30 | 115.7 | 115.65
2019-11-16 14:00 | 121.56 | 121.28
2019-11-16 14:30 | 130.83 | 128.47
2019-11-16 15:00 | 137.25 | 134.98
2019-11-16 15:30 | 142.56 | 140.2
2019-11-16 16:00 | 152.04 | 149.8
2019-11-16 16:30 | 159.47 | 157.23
2019-11-16 17:00 | 164.19 | 162.07
2019-11-16 17:30 | 161.98 | 160.32
2019-11-16 18:00 | 141.12 | 139.83
2019-11-16 18:30 | 131.73 | 131.67
2019-11-16 19:00 | 133.76 | 133.63
2019-11-16 19:30 | 124.56 | 124.52
2019-11-16 20:00 | 116.43 | 116.32
2019-11-16 20:30 | 108.01 | 107.87
2019-11-16 21:00 | 94.79 | 94.1
2019-11-16 21:30 | 87.57 | 86.76
2019-11-16 22:00 | 76.31 | 75.77
2019-11-16 22:30 | 73.44 | 72.78
2019-11-16 23:00 | 70.47 | 69.71
2019-11-16 23:30 | 59.85 | 58.73
2019-11-17 | 43.49 | 41.18
2019-11-17 00:30 | 34.65 | 31.07
2019-11-17 01:00 | 83.14 | 81.34
2019-11-17 01:30 | 73.65 | 71.43
2019-11-17 02:00 | 35.15 | 30.27
2019-11-17 02:30 | 32.65 | 27.64
2019-11-17 03:00 | 31.03 | 25.92
2019-11-17 03:30 | 31.07 | 25.55
2019-11-17 04:00 | 29.77 | 24.12
2019-11-17 04:30 | 30.16 | 24.4
2019-11-17 05:00 | 24.3 | 20.97
2019-11-17 05:30 | 23.46 | 21.23
2019-11-17 06:00 | 23.86 | 21.43
2019-11-17 06:30 | 26.33 | 22.84
2019-11-17 07:00 | 30.51 | 25.37
2019-11-17 07:30 | 35.38 | 29.44
2019-11-17 08:00 | 37.44 | 31.02
2019-11-17 08:30 | 42.97 | 37.36
2019-11-17 09:00 | 46.75 | 43.6
2019-11-17 09:30 | 48.25 | 48.23
2019-11-17 10:00 | 50.72 | 50.54
2019-11-17 10:30 | 52.56 | 52.26
2019-11-17 11:00 | 54.03 | 53.55
2019-11-17 11:30 | 55.78 | 55.17
2019-11-17 12:00 | 58.8 | 58.16
2019-11-17 12:30 | 68 | 67.97
2019-11-17 13:00 | 75.94 | 75.61
2019-11-17 13:30 | 85.79 | 85.55
2019-11-17 14:00 | 99.19 | 99.13
2019-11-17 14:30 | 135.42 | 134.66
2019-11-17 15:00 | 116.59 | 115.66
2019-11-17 15:30 | 109.82 | 109.61
2019-11-17 16:00 | 117.84 | 117.81
2019-11-17 16:30 | 122.22 | 122.14
2019-11-17 17:00 | 128.6 | 128.54
2019-11-17 17:30 | 129.08 | 128.93
2019-11-17 18:00 | 118.31 | 118.03
2019-11-17 18:30 | 121.48 | 121.24
2019-11-17 19:00 | 129.36 | 129.26
2019-11-17 19:30 | 123.71 | 123.5
2019-11-17 20:00 | 115.26 | 114.82
2019-11-17 20:30 | 85.85 | 85.37
2019-11-17 21:00 | 69.28 | 68.56
2019-11-17 21:30 | 88.13 | 85.88
2019-11-17 22:00 | 88.59 | 86.2
2019-11-17 22:30 | 82.79 | 79.8
2019-11-17 23:00 | 79.44 | 76.04
2019-11-17 23:30 | 66.08 | 63.73
2019-11-18 | 47.79 | 47.57
2019-11-18 00:30 | 37.39 | 37.36
2019-11-18 01:00 | 32.79 | 32.79
2019-11-18 01:30 | 27.98 | 27.95
2019-11-18 02:00 | 25.29 | 25.27
2019-11-18 02:30 | 24.02 | 23.98
2019-11-18 03:00 | 22.36 | 22.31
2019-11-18 03:30 | 22.71 | 22.63
2019-11-18 04:00 | 22.85 | 22.79
2019-11-18 04:30 | 25.18 | 25.15
2019-11-18 05:00 | 27.55 | 27.26
2019-11-18 05:30 | 33.19 | 33.09
2019-11-18 06:00 | 40.22 | 40.19
2019-11-18 06:30 | 51.07 | 50.82
2019-11-18 07:00 | 59.6 | 59.52
2019-11-18 07:30 | 67.94 | 67.91
2019-11-18 08:00 | 71.96 | 71.92
2019-11-18 08:30 | 75.43 | 71.45
2019-11-18 09:00 | 82.92 | 66.8
2019-11-18 09:30 | 84.98 | 60.2
2019-11-18 10:00 | 84.26 | 57.43
2019-11-18 10:30 | 85.1 | 57.25
2019-11-18 11:00 | 82.43 | 53.77
2019-11-18 11:30 | 81.56 | 51.81
2019-11-18 12:00 | 82.44 | 52.65
2019-11-18 12:30 | 84.92 | 55.63
2019-11-18 13:00 | 87.67 | 58.97
2019-11-18 13:30 | 89.6 | 61.86
2019-11-18 14:00 | 92.58 | 65.46
2019-11-18 14:30 | 95.5 | 69.62
2019-11-18 15:00 | 94.84 | 69.83
2019-11-18 15:30 | 96.09 | 72.5
2019-11-18 16:00 | 110 | 90.91
2019-11-18 16:30 | 127.49 | 111.8
2019-11-18 17:00 | 136.5 | 122.49
2019-11-18 17:30 | 147.78 | 136.08
2019-11-18 18:00 | 194.25 | 186.21
2019-11-18 18:30 | 199.76 | 192.3
2019-11-18 19:00 | 222.19 | 214.82
2019-11-18 19:30 | 209.32 | 202.66
2019-11-18 20:00 | 191.67 | 189.11
2019-11-18 20:30 | 186.4 | 186.39
2019-11-18 21:00 | 164.57 | 164.43
2019-11-18 21:30 | 135.93 | 135.65
2019-11-18 22:00 | 114.93 | 114.32
2019-11-18 22:30 | 99.1 | 98.23
2019-11-18 23:00 | 97.87 | 96.82
2019-11-18 23:30 | 55.36 | 53.07
2019-11-19 | 24.67 | 17.26
2019-11-19 00:30 | 22.36 | 11.71
2019-11-19 01:00 | 26.54 | 17.02
2019-11-19 01:30 | 32.01 | 23.61
2019-11-19 02:00 | 35.14 | 27.56
2019-11-19 02:30 | 41.97 | 35.93
2019-11-19 03:00 | 40.19 | 33.56
2019-11-19 03:30 | 44.56 | 38.96
2019-11-19 04:00 | 38.44 | 31.9
2019-11-19 04:30 | 30.49 | 22.42
2019-11-19 05:00 | 37.26 | 30.55
2019-11-19 05:30 | 42.73 | 37.07
2019-11-19 06:00 | 43.23 | 39.33
2019-11-19 06:30 | 38.06 | 36.35
2019-11-19 07:00 | 29.56 | 29.23
2019-11-19 07:30 | 54.24 | 54.2
2019-11-19 08:00 | 58.06 | 53.83
2019-11-19 08:30 | 44.06 | -6.74
2019-11-19 09:00 | 89.72 | -53.75
2019-11-19 09:30 | 86.15 | -45.25
2019-11-19 10:00 | 85.36 | -40.99
2019-11-19 10:30 | 68.2 | 32.26
2019-11-19 11:00 | 75.37 | 48
2019-11-19 11:30 | 84.99 | 60.8
2019-11-19 12:00 | 92.04 | 69.91
2019-11-19 12:30 | 99.48 | 79.36
2019-11-19 13:00 | 110.33 | 97.06
2019-11-19 13:30 | 116.27 | 105.24
2019-11-19 14:00 | 116.4 | 115.14
2019-11-19 14:30 | 136.26 | 135.31
2019-11-19 15:00 | 141.47 | 140.65
2019-11-19 15:30 | 102.77 | 101.74
2019-11-19 16:00 | 173.5 | 172.73
2019-11-19 16:30 | 217.68 | 215.83
2019-11-19 17:00 | 232.03 | 230.49
2019-11-19 17:30 | 236.61 | 235.41
2019-11-19 18:00 | 164.46 | 163.4
2019-11-19 18:30 | 167.5 | 166.59
2019-11-19 19:00 | 175.75 | 174.61
2019-11-19 19:30 | 179.85 | 179.12
2019-11-19 20:00 | 185.48 | 185.42
2019-11-19 20:30 | 187.52 | 187.4
2019-11-19 21:00 | 170.4 | 170.08
2019-11-19 21:30 | 168.71 | 168.37
2019-11-19 22:00 | 161.9 | 161.74
2019-11-19 22:30 | 138.46 | 138.3
2019-11-19 23:00 | 141.98 | 141.9
2019-11-19 23:30 | 111.17 | 111.15
2019-11-20 | 92.35 | 92.34
2019-11-20 00:30 | 91.78 | 91.76
2019-11-20 01:00 | 100.01 | 100
2019-11-20 01:30 | 98.65 | 98.28
2019-11-20 02:00 | 98.5 | 96.2
2019-11-20 02:30 | 95.31 | 92.86
2019-11-20 03:00 | 94.2 | 91.67
2019-11-20 03:30 | 94.65 | 92.25
2019-11-20 04:00 | 97.32 | 95.03
2019-11-20 04:30 | 100.38 | 98.47
2019-11-20 05:00 | 104.47 | 102.49
2019-11-20 05:30 | 105.51 | 103.91
2019-11-20 06:00 | 114.09 | 113.13
2019-11-20 06:30 | 104.53 | 104.28
2019-11-20 07:00 | 106.69 | 106.67
2019-11-20 07:30 | 130.01 | 129.55
2019-11-20 08:00 | 121.75 | 121.67
2019-11-20 08:30 | 113.56 | 113.47
2019-11-20 09:00 | 103.6 | 103.2
2019-11-20 09:30 | 123.19 | 122.77
2019-11-20 10:00 | 139.57 | 139.25
2019-11-20 10:30 | 150.76 | 150.35
2019-11-20 11:00 | 166.98 | 165.4
2019-11-20 11:30 | 164.19 | 158.13
2019-11-20 12:00 | 141.19 | 134.06
2019-11-20 12:30 | 144.52 | 137.45
2019-11-20 13:00 | 149.66 | 142.68
2019-11-20 13:30 | 155.01 | 148.23
2019-11-20 14:00 | 163.57 | 156.59
2019-11-20 14:30 | 168.57 | 161.25
2019-11-20 15:00 | 168.44 | 161.34
2019-11-20 15:30 | 173.55 | 168.44
2019-11-20 16:00 | 174.03 | 169.17
2019-11-20 16:30 | 182.74 | 177.97
2019-11-20 17:00 | 178.83 | 175.06
2019-11-20 17:30 | 175.5 | 172.91
2019-11-20 18:00 | 168.72 | 166.86
2019-11-20 18:30 | 166.68 | 166.17
2019-11-20 19:00 | 171.19 | 170.8
2019-11-20 19:30 | 168.87 | 168.53
2019-11-20 20:00 | 165.27 | 165.07
2019-11-20 20:30 | 157.53 | 157.46
2019-11-20 21:00 | 150.14 | 145.75
2019-11-20 21:30 | 142.78 | 135.91
2019-11-20 22:00 | 128.18 | 128.12
2019-11-20 22:30 | 116.68 | 116.49
2019-11-20 23:00 | 111.46 | 111.23
2019-11-20 23:30 | 98.36 | 98.25
2019-11-21 | 84.14 | 84.11
2019-11-21 00:30 | 73.6 | 73.57
2019-11-21 01:00 | 72.83 | 71.95
2019-11-21 01:30 | 75.6 | 74.81
2019-11-21 02:00 | 74.39 | 73.69
2019-11-21 02:30 | 73.41 | 72.73
2019-11-21 03:00 | 73.94 | 72.72
2019-11-21 03:30 | 73.3 | 72.2
2019-11-21 04:00 | 71.43 | 70.23
2019-11-21 04:30 | 70.27 | 68.96
2019-11-21 05:00 | 66.39 | 65.47
2019-11-21 05:30 | 73.07 | 72.26
2019-11-21 06:00 | 81.46 | 80.65
2019-11-21 06:30 | 88.83 | 88.44
2019-11-21 07:00 | 89.28 | 89.28
2019-11-21 07:30 | 118.37 | 118.23
2019-11-21 08:00 | 116.8 | 115.38
2019-11-21 08:30 | 110.42 | 108.32
2019-11-21 09:00 | 94.71 | 92.67
2019-11-21 09:30 | 92.85 | 90.8
2019-11-21 10:00 | 83.76 | 81.78
2019-11-21 10:30 | 89.07 | 87.33
2019-11-21 11:00 | 87.97 | 86.32
2019-11-21 11:30 | 68.49 | 66.05
2019-11-21 12:00 | 47.66 | 42.81
2019-11-21 12:30 | 26.73 | 8.48
2019-11-21 13:00 | 46.13 | 42.66
2019-11-21 13:30 | 76.67 | 75.2
2019-11-21 14:00 | 91.44 | 90.48
2019-11-21 14:30 | 105.52 | 104.84
2019-11-21 15:00 | 96.94 | 96.34
2019-11-21 15:30 | 118.54 | 117.89
2019-11-21 16:00 | 144.04 | 143.31
2019-11-21 16:30 | 151.15 | 150.55
2019-11-21 17:00 | 150.38 | 150.06
2019-11-21 17:30 | 147.65 | 147.21
2019-11-21 18:00 | 144.94 | 144.48
2019-11-21 18:30 | 146.29 | 146.01
2019-11-21 19:00 | 148.95 | 148.64
2019-11-21 19:30 | 147.76 | 147.33
2019-11-21 20:00 | 148.25 | 147.95
2019-11-21 20:30 | 144.82 | 144.67
2019-11-21 21:00 | 135.6 | 135.38
2019-11-21 21:30 | 126.06 | 125.24
2019-11-21 22:00 | 118.65 | 118.16
2019-11-21 22:30 | 109.79 | 109.29
2019-11-21 23:00 | 105.64 | 105.13
2019-11-21 23:30 | 94.87 | 94.09
2019-11-22 | 79.91 | 78.43
2019-11-22 00:30 | 69.47 | 68.5
2019-11-22 01:00 | 71.16 | 70.06
2019-11-22 01:30 | 71.52 | 70.55
2019-11-22 02:00 | 71.94 | 71.07
2019-11-22 02:30 | 70.38 | 69.53
2019-11-22 03:00 | 70.5 | 69.59
2019-11-22 03:30 | 69.95 | 69.22
2019-11-22 04:00 | 69.01 | 68.33
2019-11-22 04:30 | 68.94 | 68.29
2019-11-22 05:00 | 66.93 | 66.32
2019-11-22 05:30 | 71.77 | 71.14
2019-11-22 06:00 | 78.13 | 77.35
2019-11-22 06:30 | 83.07 | 82.45
2019-11-22 07:00 | 80.81 | 80.66
2019-11-22 07:30 | 91.31 | 91.27
2019-11-22 08:00 | 78.42 | 78.31
2019-11-22 08:30 | 63.62 | 63.62
2019-11-22 09:00 | 37.52 | 36.63
2019-11-22 09:30 | 58.25 | 54.53
2019-11-22 10:00 | 69.56 | 66.13
2019-11-22 10:30 | 69.85 | 66.1
2019-11-22 11:00 | 62.21 | 57.3
2019-11-22 11:30 | 83.43 | 66.6
2019-11-22 12:00 | 95.96 | 79.72
2019-11-22 12:30 | 88.37 | 70.48
2019-11-22 13:00 | 91.16 | 73.96
2019-11-22 13:30 | 96.73 | 80.42
2019-11-22 14:00 | 100.96 | 85.97
2019-11-22 14:30 | 122.78 | 110.81
2019-11-22 15:00 | 130.61 | 126.38
2019-11-22 15:30 | 141.94 | 138.42
2019-11-22 16:00 | 141.61 | 138.16
2019-11-22 16:30 | 138.14 | 135.23
2019-11-22 17:00 | 137.11 | 134.37
2019-11-22 17:30 | 129.49 | 127.32
2019-11-22 18:00 | 121.51 | 119.79
2019-11-22 18:30 | 117.84 | 116.36
2019-11-22 19:00 | 122.38 | 120.48
2019-11-22 19:30 | 123.96 | 122.55
2019-11-22 20:00 | 122.4 | 122.24
2019-11-22 20:30 | 123.58 | 123.55
2019-11-22 21:00 | 109.6 | 109.52
2019-11-22 21:30 | 113.9 | 113.11
2019-11-22 22:00 | 119.44 | 118.63
2019-11-22 22:30 | 111.15 | 110.4
2019-11-22 23:00 | 108.7 | 108.13
2019-11-22 23:30 | 96.74 | 96.41
2019-11-23 | 82.21 | 82.07
2019-11-23 00:30 | 73.37 | 73.34
2019-11-23 01:00 | 75.45 | 75.44
2019-11-23 01:30 | 77.27 | 77.25
2019-11-23 02:00 | 77.46 | 77.41
2019-11-23 02:30 | 74.3 | 74.24
2019-11-23 03:00 | 71.65 | 71.58
2019-11-23 03:30 | 69.96 | 69.89
2019-11-23 04:00 | 70.39 | 70.32
2019-11-23 04:30 | 69.63 | 69.56
2019-11-23 05:00 | 67.87 | 67.69
2019-11-23 05:30 | 68.41 | 68.26
2019-11-23 06:00 | 68.83 | 68.77
2019-11-23 06:30 | 57.79 | 57.79
2019-11-23 07:00 | 41.07 | 40.81
2019-11-23 07:30 | 37.19 | 35.83
2019-11-23 08:00 | 73.96 | 47.87
2019-11-23 08:30 | 83.55 | 48.24
2019-11-23 09:00 | 75.76 | 26.93
2019-11-23 09:30 | 81.07 | 36.04
2019-11-23 10:00 | 78.06 | 20.05
2019-11-23 10:30 | 78.05 | -8.39
2019-11-23 11:00 | 79.92 | -0.6
2019-11-23 11:30 | 83.09 | 25.83
2019-11-23 12:00 | 83.05 | 26.28
2019-11-23 12:30 | 83.07 | 26.72
2019-11-23 13:00 | 86.06 | 38.67
2019-11-23 13:30 | 90.75 | 49.14
2019-11-23 14:00 | 93.91 | 54.6
2019-11-23 14:30 | 109.46 | 78.64
2019-11-23 15:00 | 121.79 | 95.22
2019-11-23 15:30 | 132.09 | 107.89
2019-11-23 16:00 | 139.55 | 116.64
2019-11-23 16:30 | 148.59 | 127.11
2019-11-23 17:00 | 140.5 | 117.52
2019-11-23 17:30 | 135.04 | 112.01
2019-11-23 18:00 | 130.62 | 108.01
2019-11-23 18:30 | 133.29 | 111.88
2019-11-23 19:00 | 139.9 | 118.53
2019-11-23 19:30 | 142.59 | 122.99
2019-11-23 20:00 | 144.54 | 126.74
2019-11-23 20:30 | 129.06 | 119.94
2019-11-23 21:00 | 104.71 | 103.85
2019-11-23 21:30 | 108.82 | 108.05
2019-11-23 22:00 | 106.97 | 106.49
2019-11-23 22:30 | 103.01 | 102.63
2019-11-23 23:00 | 103.03 | 102.77
2019-11-23 23:30 | 92.93 | 92.77
2019-11-24 | 78.92 | 78.89
2019-11-24 00:30 | 70.09 | 70.09
2019-11-24 01:00 | 71.61 | 71.58
2019-11-24 01:30 | 71.37 | 71.28
2019-11-24 02:00 | 70.23 | 70.07
2019-11-24 02:30 | 69.11 | 68.92
2019-11-24 03:00 | 68.04 | 67.81
2019-11-24 03:30 | 67.24 | 67.01
2019-11-24 04:00 | 63.36 | 63.11
2019-11-24 04:30 | 63 | 62.71
2019-11-24 05:00 | 61.57 | 61.16
2019-11-24 05:30 | 62.39 | 61.9
2019-11-24 06:00 | 62.18 | 61.75
2019-11-24 06:30 | 38.35 | 38.08
2019-11-24 07:00 | 20.35 | 20.31
2019-11-24 07:30 | 13.88 | 13.68
2019-11-24 08:00 | 7.65 | 5.07
2019-11-24 08:30 | 16.84 | -9.03
2019-11-24 09:00 | 21.3 | 10.29
2019-11-24 09:30 | 33.32 | 25.67
2019-11-24 10:00 | 33.64 | 24.81
2019-11-24 10:30 | 38.55 | 30.08
2019-11-24 11:00 | 47.53 | 41.23
2019-11-24 11:30 | 44.97 | 38.22
2019-11-24 12:00 | 46.52 | 39.65
2019-11-24 12:30 | 44.87 | 37.67
2019-11-24 13:00 | 42.36 | 34.47
2019-11-24 13:30 | 53.18 | 46.99
2019-11-24 14:00 | 65.51 | 60.83
2019-11-24 14:30 | 82.38 | 78.76
2019-11-24 15:00 | 114 | 111.3
2019-11-24 15:30 | 133.18 | 126.38
2019-11-24 16:00 | 146.67 | 128.82
2019-11-24 16:30 | 136.51 | 117.71
2019-11-24 17:00 | 134.58 | 116.02
2019-11-24 17:30 | 126.86 | 107.72
2019-11-24 18:00 | 122.38 | 103.15
2019-11-24 18:30 | 125.83 | 107.19
2019-11-24 19:00 | 136.23 | 117.5
2019-11-24 19:30 | 139.87 | 122.67
2019-11-24 20:00 | 142.03 | 126.83
2019-11-24 20:30 | 133.85 | 126.12
2019-11-24 21:00 | 119.9 | 111.88
2019-11-24 21:30 | 107.73 | 107.08
2019-11-24 22:00 | 106.02 | 105.85
2019-11-24 22:30 | 99.96 | 99.84
2019-11-24 23:00 | 99.13 | 99.04
2019-11-24 23:30 | 89.01 | 88.99
2019-11-25 | 75.71 | 75.71
2019-11-25 00:30 | 67.1 | 67.07
2019-11-25 01:00 | 68.08 | 68
2019-11-25 01:30 | 69.12 | 67.72
2019-11-25 02:00 | 70.53 | 66.36
2019-11-25 02:30 | 68.81 | 64.51
2019-11-25 03:00 | 68.02 | 63.8
2019-11-25 03:30 | 68.18 | 64.13
2019-11-25 04:00 | 67.9 | 63.94
2019-11-25 04:30 | 66.24 | 62.25
2019-11-25 05:00 | 66.34 | 62.26
2019-11-25 05:30 | 68.26 | 64.56
2019-11-25 06:00 | 74.3 | 71.82
2019-11-25 06:30 | 82.59 | 81.69
2019-11-25 07:00 | 75.01 | 74.91
2019-11-25 07:30 | 86.8 | 84.89
2019-11-25 08:00 | 101.66 | 84.59
2019-11-25 08:30 | 100.46 | 81.2
2019-11-25 09:00 | 102.5 | 82.08
2019-11-25 09:30 | 99.05 | 76.32
2019-11-25 10:00 | 105.93 | 83.65
2019-11-25 10:30 | 94.3 | 66.83
2019-11-25 11:00 | 84.71 | 50.41
2019-11-25 11:30 | 79.35 | 38.83
2019-11-25 12:00 | 84.66 | 46.07
2019-11-25 12:30 | 73.12 | 23.16
2019-11-25 13:00 | 73.29 | -18.73
2019-11-25 13:30 | 74.16 | -21.07
2019-11-25 14:00 | 72.85 | 24.89
2019-11-25 14:30 | 88.16 | 59.98
2019-11-25 15:00 | 95.16 | 69.93
2019-11-25 15:30 | 118.75 | 100.59
2019-11-25 16:00 | 141.21 | 126.41
2019-11-25 16:30 | 149.1 | 135.76
2019-11-25 17:00 | 143.15 | 129.7
2019-11-25 17:30 | 129.55 | 115.85
2019-11-25 18:00 | 122.48 | 109.94
2019-11-25 18:30 | 123.11 | 112.23
2019-11-25 19:00 | 131.88 | 120.45
2019-11-25 19:30 | 135.8 | 125.7
2019-11-25 20:00 | 142.21 | 131.07
2019-11-25 20:30 | 137.06 | 126.35
2019-11-25 21:00 | 125.61 | 120.29
2019-11-25 21:30 | 123.7 | 120.62
2019-11-25 22:00 | 114.34 | 114.33
2019-11-25 22:30 | 104.69 | 104.29
2019-11-25 23:00 | 100.98 | 100.38
2019-11-25 23:30 | 88.87 | 88.02
2019-11-26 | 74.97 | 73.55
2019-11-26 00:30 | 67.03 | 65
2019-11-26 01:00 | 69.7 | 67.38
2019-11-26 01:30 | 73.24 | 70.9
2019-11-26 02:00 | 72.82 | 70.15
2019-11-26 02:30 | 72.85 | 69.72
2019-11-26 03:00 | 73.09 | 70.09
2019-11-26 03:30 | 73.14 | 70.03
2019-11-26 04:00 | 71.99 | 68.81
2019-11-26 04:30 | 71.1 | 68.07
2019-11-26 05:00 | 70.55 | 66.99
2019-11-26 05:30 | 70.22 | 67.45
2019-11-26 06:00 | 77.41 | 75.86
2019-11-26 06:30 | 82.79 | 82.34
2019-11-26 07:00 | 85.6 | 77.63
2019-11-26 07:30 | 106.28 | 89.42
2019-11-26 08:00 | 129.38 | 112.39
2019-11-26 08:30 | 122.8 | 100.56
2019-11-26 09:00 | 137.24 | 121.09
2019-11-26 09:30 | 141.43 | 124.8
2019-11-26 10:00 | 131.87 | 113.28
2019-11-26 10:30 | 111.45 | 88.29
2019-11-26 11:00 | 111.22 | 87.24
2019-11-26 11:30 | 109.53 | 83.52
2019-11-26 12:00 | 115.81 | 90.98
2019-11-26 12:30 | 129.09 | 107.52
2019-11-26 13:00 | 137.9 | 116.71
2019-11-26 13:30 | 151.37 | 132.69
2019-11-26 14:00 | 155.19 | 137.05
2019-11-26 14:30 | 162.32 | 144.26
2019-11-26 15:00 | 162.38 | 144.41
2019-11-26 15:30 | 154.62 | 135.83
2019-11-26 16:00 | 148.48 | 128.66
2019-11-26 16:30 | 140.22 | 126.08
2019-11-26 17:00 | 132.54 | 119.08
2019-11-26 17:30 | 120.56 | 107.31
2019-11-26 18:00 | 111.5 | 99.86
2019-11-26 18:30 | 114.65 | 104.69
2019-11-26 19:00 | 125.88 | 116.06
2019-11-26 19:30 | 126.6 | 122.18
2019-11-26 20:00 | 134.33 | 132.29
2019-11-26 20:30 | 138.57 | 135.87
2019-11-26 21:00 | 123.69 | 119.26
2019-11-26 21:30 | 119.08 | 118.67
2019-11-26 22:00 | 124.49 | 123.71
2019-11-26 22:30 | 114.78 | 114.17
2019-11-26 23:00 | 110.09 | 109.55
2019-11-26 23:30 | 97.64 | 96.66
2019-11-27 | 84.18 | 82.96
2019-11-27 00:30 | 74 | 73.11
2019-11-27 01:00 | 76.31 | 75.79
2019-11-27 01:30 | 78.35 | 78.19
2019-11-27 02:00 | 77.15 | 75.91
2019-11-27 02:30 | 74.34 | 72.81
2019-11-27 03:00 | 74.76 | 73.25
2019-11-27 03:30 | 72.51 | 70.94
2019-11-27 04:00 | 71.44 | 69.85
2019-11-27 04:30 | 69.02 | 67.56
2019-11-27 05:00 | 67.67 | 65.9
2019-11-27 05:30 | 66.61 | 65.34
2019-11-27 06:00 | 60.2 | 59.57
2019-11-27 06:30 | 79.73 | 77.58
2019-11-27 07:00 | 83.06 | 80.09
2019-11-27 07:30 | 97.77 | 94.24
2019-11-27 08:00 | 107.09 | 97.86
2019-11-27 08:30 | 135.44 | 118.09
2019-11-27 09:00 | 142.2 | 122.99
2019-11-27 09:30 | 138.24 | 117.23
2019-11-27 10:00 | 169.04 | 151.74
2019-11-27 10:30 | 192.75 | 177.46
2019-11-27 11:00 | 190.65 | 174.98
2019-11-27 11:30 | 195.68 | 180.25
2019-11-27 12:00 | 198.73 | 183.54
2019-11-27 12:30 | 197.35 | 184.98
2019-11-27 13:00 | 193.51 | 181.31
2019-11-27 13:30 | 198.34 | 186.1
2019-11-27 14:00 | 200.15 | 188.37
2019-11-27 14:30 | 213.46 | 202.61
2019-11-27 15:00 | 219.66 | 209.8
2019-11-27 15:30 | 210.82 | 201.6
2019-11-27 16:00 | 205.76 | 196.73
2019-11-27 16:30 | 195.11 | 186.37
2019-11-27 17:00 | 211.98 | 204.55
2019-11-27 17:30 | 209.73 | 203.28
2019-11-27 18:00 | 210.17 | 203.43
2019-11-27 18:30 | 221.21 | 214.06
2019-11-27 19:00 | 226.73 | 219.68
2019-11-27 19:30 | 202.81 | 199.49
2019-11-27 20:00 | 200.21 | 197.13
2019-11-27 20:30 | 193.49 | 190.67
2019-11-27 21:00 | 180.12 | 180.06
2019-11-27 21:30 | 166.2 | 166.14
2019-11-27 22:00 | 145.53 | 145.34
2019-11-27 22:30 | 147.27 | 146.99
2019-11-27 23:00 | 134.59 | 134.24
2019-11-27 23:30 | 109.52 | 109.06
2019-11-28 | 105.55 | 105.46
2019-11-28 00:30 | 109.13 | 109.01
2019-11-28 01:00 | 99.91 | 99.73
2019-11-28 01:30 | 100.31 | 100.07
2019-11-28 02:00 | 102.9 | 102.63
2019-11-28 02:30 | 101.53 | 101.25
2019-11-28 03:00 | 98.64 | 98.32
2019-11-28 03:30 | 92.36 | 92.05
2019-11-28 04:00 | 84.75 | 84.43
2019-11-28 04:30 | 79.79 | 79.55
2019-11-28 05:00 | 90.82 | 90.67
2019-11-28 05:30 | 92.16 | 92.05
2019-11-28 06:00 | 93.18 | 93.12
2019-11-28 06:30 | 104.92 | 104.91
2019-11-28 07:00 | 115.52 | 115.27
2019-11-28 07:30 | 146.2 | 145.09
2019-11-28 08:00 | 158.2 | 157.39
2019-11-28 08:30 | 165.5 | 164.64
2019-11-28 09:00 | 169.12 | 168.1
2019-11-28 09:30 | 157.02 | 155.84
2019-11-28 10:00 | 155.47 | 154.24
2019-11-28 10:30 | 151.36 | 150.62
2019-11-28 11:00 | 134.19 | 133.53
2019-11-28 11:30 | 122.72 | 121.99
2019-11-28 12:00 | 124.24 | 123.31
2019-11-28 12:30 | 115.91 | 114.88
2019-11-28 13:00 | 132.98 | 132.05
2019-11-28 13:30 | 136.84 | 135.59
2019-11-28 14:00 | 133.97 | 132.37
2019-11-28 14:30 | 136.04 | 133.19
2019-11-28 15:00 | 161.39 | 155.99
2019-11-28 15:30 | 166.3 | 161.32
2019-11-28 16:00 | 183.83 | 179.78
2019-11-28 16:30 | 207.75 | 204.51
2019-11-28 17:00 | 209.42 | 206.53
2019-11-28 17:30 | 206.54 | 204.04
2019-11-28 18:00 | 219 | 216.81
2019-11-28 18:30 | 230.15 | 228.29
2019-11-28 19:00 | 244.1 | 242.03
2019-11-28 19:30 | 237.48 | 235.77
2019-11-28 20:00 | 226.93 | 225.39
2019-11-28 20:30 | 228.89 | 228.83
2019-11-28 21:00 | 206.5 | 206.5
2019-11-28 21:30 | 184.57 | 184.56
2019-11-28 22:00 | 164.72 | 164.69
2019-11-28 22:30 | 147.9 | 147.85
2019-11-28 23:00 | 142.02 | 141.86
2019-11-28 23:30 | 127.95 | 127.58
2019-11-29 | 113.23 | 112.68
2019-11-29 00:30 | 118.32 | 117.86
2019-11-29 01:00 | 102 | 101.35
2019-11-29 01:30 | 108.22 | 107.28
2019-11-29 02:00 | 111.55 | 110.43
2019-11-29 02:30 | 107.4 | 106.19
2019-11-29 03:00 | 104.42 | 103.15
2019-11-29 03:30 | 100.75 | 99.48
2019-11-29 04:00 | 90.99 | 89.62
2019-11-29 04:30 | 102.17 | 101.16
2019-11-29 05:00 | 100.89 | 99.88
2019-11-29 05:30 | 100.21 | 99.36
2019-11-29 06:00 | 97.08 | 96.52
2019-11-29 06:30 | 90.01 | 89.95
2019-11-29 07:00 | 81.95 | 81.49
2019-11-29 07:30 | 105.39 | 104.79
2019-11-29 08:00 | 132.29 | 131.56
2019-11-29 08:30 | 134.84 | 133.92
2019-11-29 09:00 | 136.74 | 135.49
2019-11-29 09:30 | 139.34 | 138.38
2019-11-29 10:00 | 132.74 | 131.82
2019-11-29 10:30 | 111.59 | 110.71
2019-11-29 11:00 | 98.06 | 96.95
2019-11-29 11:30 | 86.96 | 85.92
2019-11-29 12:00 | 93.8 | 92.86
2019-11-29 12:30 | 102.96 | 102.13
2019-11-29 13:00 | 101.5 | 100.66
2019-11-29 13:30 | 100.7 | 99.86
2019-11-29 14:00 | 122.35 | 120.81
2019-11-29 14:30 | 136.71 | 129.91
2019-11-29 15:00 | 122.95 | 115.86
2019-11-29 15:30 | 132.72 | 126.17
2019-11-29 16:00 | 137.11 | 130.89
2019-11-29 16:30 | 140.36 | 134.29
2019-11-29 17:00 | 175.61 | 171.58
2019-11-29 17:30 | 177.87 | 174.78
2019-11-29 18:00 | 175.55 | 173.35
2019-11-29 18:30 | 178.86 | 175.71
2019-11-29 19:00 | 147.84 | 141.28
2019-11-29 19:30 | 142.99 | 136.56
2019-11-29 20:00 | 142.32 | 136.42
2019-11-29 20:30 | 182.22 | 177.97
2019-11-29 21:00 | 164.93 | 161.31
2019-11-29 21:30 | 146.6 | 146.59
2019-11-29 22:00 | 141.22 | 141.22
2019-11-29 22:30 | 147.24 | 147.23
2019-11-29 23:00 | 140.82 | 140.79
2019-11-29 23:30 | 98.03 | 97.88
2019-11-30 | 78.28 | 77.89
2019-11-30 00:30 | 99.6 | 99.09
2019-11-30 01:00 | 102.79 | 102.1
2019-11-30 01:30 | 100.43 | 99.63
2019-11-30 02:00 | 109.65 | 108.72
2019-11-30 02:30 | 107.35 | 106.41
2019-11-30 03:00 | 111.91 | 110.85
2019-11-30 03:30 | 109.31 | 108.27
2019-11-30 04:00 | 103.06 | 101.89
2019-11-30 04:30 | 92.25 | 90.82
2019-11-30 05:00 | 96.39 | 95.13
2019-11-30 05:30 | 86.07 | 84.88
2019-11-30 06:00 | 71.56 | 70.15
2019-11-30 06:30 | 54.74 | 53.46
2019-11-30 07:00 | 33.49 | 32.57
2019-11-30 07:30 | 36.65 | 36.63
2019-11-30 08:00 | 24.09 | -21.55
2019-11-30 08:30 | 11.87 | -3.15
2019-11-30 09:00 | 39.43 | 38.85
2019-11-30 09:30 | 80.94 | 80.83
2019-11-30 10:00 | 101.32 | 101.3
2019-11-30 10:30 | 109.78 | 109.75
2019-11-30 11:00 | 125.32 | 125.28
2019-11-30 11:30 | 130.79 | 130.74
2019-11-30 12:00 | 140.81 | 140.77
2019-11-30 12:30 | 142.56 | 142.53
2019-11-30 13:00 | 161.16 | 161.12
2019-11-30 13:30 | 180.41 | 180.36
2019-11-30 14:00 | 185.48 | 185.31
2019-11-30 14:30 | 196.18 | 192.9
2019-11-30 15:00 | 202.29 | 199.18
2019-11-30 15:30 | 217.22 | 214.3
2019-11-30 16:00 | 228.17 | 225.23
2019-11-30 16:30 | 217.86 | 214.81
2019-11-30 17:00 | 171.66 | 169.34
2019-11-30 17:30 | 145.75 | 143.98
2019-11-30 18:00 | 141.29 | 137.86
2019-11-30 18:30 | 140.93 | 136.39
2019-11-30 19:00 | 146.08 | 141.27
2019-11-30 19:30 | 144.97 | 140.59
2019-11-30 20:00 | 142.48 | 138.66
2019-11-30 20:30 | 209.25 | 208.05
2019-11-30 21:00 | 199.36 | 199.36
2019-11-30 21:30 | 199.2 | 199.18
2019-11-30 22:00 | 191.5 | 191.4
2019-11-30 22:30 | 170.97 | 170.96
2019-11-30 23:00 | 167.49 | 167.44
2019-11-30 23:30 | 170.28 | 170.04
2019-12-01 | 156.38 | 156.13
2019-12-01 00:30 | 134.1 | 133.77
2019-12-01 01:00 | 136.99 | 136.37
2019-12-01 01:30 | 133.01 | 132.28
2019-12-01 02:00 | 126.51 | 125.72
2019-12-01 02:30 | 131.6 | 130.63
2019-12-01 03:00 | 122.68 | 121.77
2019-12-01 03:30 | 125.72 | 124.65
2019-12-01 04:00 | 125.7 | 124.68
2019-12-01 04:30 | 124.97 | 123.9
2019-12-01 05:00 | 123.87 | 122.9
2019-12-01 05:30 | 122.74 | 121.84
2019-12-01 06:00 | 110.01 | 109.08
2019-12-01 06:30 | 81.67 | 80.45
2019-12-01 07:00 | 68.12 | 67.05
2019-12-01 07:30 | 53.16 | 52.51
2019-12-01 08:00 | 45.5 | 45.29
2019-12-01 08:30 | 78.82 | 78.82
2019-12-01 09:00 | 81.32 | 81.25
2019-12-01 09:30 | 82.66 | 82.49
2019-12-01 10:00 | 70.23 | 69.83
2019-12-01 10:30 | 83.18 | 82.49
2019-12-01 11:00 | 100.94 | 100.46
2019-12-01 11:30 | 136.57 | 136.56
2019-12-01 12:00 | 140.64 | 140.64
2019-12-01 12:30 | 161.22 | 161.21
2019-12-01 13:00 | 172.85 | 172.85
2019-12-01 13:30 | 189.14 | 189.13
2019-12-01 14:00 | 206.37 | 206.32
2019-12-01 14:30 | 188.31 | 188.28
2019-12-01 15:00 | 129.09 | 129.08
2019-12-01 15:30 | 112.08 | 112.03
2019-12-01 16:00 | 152.71 | 152.63
2019-12-01 16:30 | 203.24 | 203.24
2019-12-01 17:00 | 203.15 | 203.08
2019-12-01 17:30 | 202.66 | 202.55
2019-12-01 18:00 | 207.94 | 207.88
2019-12-01 18:30 | 203.19 | 202.92
2019-12-01 19:00 | 209.05 | 208.9
2019-12-01 19:30 | 210.95 | 210.91
2019-12-01 20:00 | 202.79 | 202.66
2019-12-01 20:30 | 186.35 | 186.02
2019-12-01 21:00 | 175.49 | 175.42
2019-12-01 21:30 | 157.77 | 157.64
2019-12-01 22:00 | 165.41 | 165.37
2019-12-01 22:30 | 145.95 | 145.93
2019-12-01 23:00 | 142.81 | 142.78
2019-12-01 23:30 | 154.15 | 153.9
2019-12-02 | 144.25 | 143.78
2019-12-02 00:30 | 123.47 | 123.03
2019-12-02 01:00 | 127.93 | 127.21
2019-12-02 01:30 | 127.32 | 126.47
2019-12-02 02:00 | 115.02 | 114.44
2019-12-02 02:30 | 114.28 | 113.45
2019-12-02 03:00 | 111.29 | 110.29
2019-12-02 03:30 | 118.85 | 117.62
2019-12-02 04:00 | 118.53 | 117.35
2019-12-02 04:30 | 123.81 | 122.63
2019-12-02 05:00 | 124.59 | 123.58
2019-12-02 05:30 | 130.18 | 129.31
2019-12-02 06:00 | 139.64 | 138.91
2019-12-02 06:30 | 144.93 | 144.7
2019-12-02 07:00 | 135.16 | 135.15
2019-12-02 07:30 | 153.02 | 152.91
2019-12-02 08:00 | 147.06 | 146.46
2019-12-02 08:30 | 130.84 | 129.5
2019-12-02 09:00 | 138.8 | 136.99
2019-12-02 09:30 | 141.27 | 140.16
2019-12-02 10:00 | 129.07 | 128.67
2019-12-02 10:30 | 119.16 | 118.7
2019-12-02 11:00 | 119.14 | 118.67
2019-12-02 11:30 | 119.33 | 118.86
2019-12-02 12:00 | 116.45 | 115.95
2019-12-02 12:30 | 113.24 | 112.81
2019-12-02 13:00 | 118.76 | 118.25
2019-12-02 13:30 | 122.11 | 121.37
2019-12-02 14:00 | 139.97 | 137.03
2019-12-02 14:30 | 202.31 | 198.65
2019-12-02 15:00 | 210.6 | 206.96
2019-12-02 15:30 | 215.11 | 211.14
2019-12-02 16:00 | 223.74 | 219.33
2019-12-02 16:30 | 233.89 | 229.62
2019-12-02 17:00 | 249.73 | 245.52
2019-12-02 17:30 | 253.51 | 249.95
2019-12-02 18:00 | 251.7 | 248.94
2019-12-02 18:30 | 248.08 | 246.04
2019-12-02 19:00 | 251.92 | 249.7
2019-12-02 19:30 | 246.76 | 244.55
2019-12-02 20:00 | 245.13 | 243.61
2019-12-02 20:30 | 220.55 | 219.67
2019-12-02 21:00 | 200.94 | 198.47
2019-12-02 21:30 | 189.63 | 185.85
2019-12-02 22:00 | 172.31 | 168.23
2019-12-02 22:30 | 167.82 | 167.16
2019-12-02 23:00 | 167.68 | 167.28
2019-12-02 23:30 | 158.4 | 158.01
2019-12-03 | 142.75 | 142.73
2019-12-03 00:30 | 130.99 | 130.98
2019-12-03 01:00 | 128.54 | 128.51
2019-12-03 01:30 | 128.88 | 128.83
2019-12-03 02:00 | 124.77 | 124.76
2019-12-03 02:30 | 121.89 | 121.88
2019-12-03 03:00 | 118.56 | 117.66
2019-12-03 03:30 | 121.42 | 120.37
2019-12-03 04:00 | 111.89 | 110.51
2019-12-03 04:30 | 114.73 | 113.62
2019-12-03 05:00 | 123.54 | 122.73
2019-12-03 05:30 | 127.16 | 126.21
2019-12-03 06:00 | 127.49 | 126.5
2019-12-03 06:30 | 129.71 | 129.13
2019-12-03 07:00 | 128.13 | 128.05
2019-12-03 07:30 | 120.57 | 119.48
2019-12-03 08:00 | 109.73 | 107.15
2019-12-03 08:30 | 109.25 | 104.8
2019-12-03 09:00 | 109.95 | 97.97
2019-12-03 09:30 | 127.03 | 100.45
2019-12-03 10:00 | 130.99 | 98.73
2019-12-03 10:30 | 150.35 | 122.92
2019-12-03 11:00 | 161.55 | 136.35
2019-12-03 11:30 | 168.56 | 147.8
2019-12-03 12:00 | 174.36 | 154.19
2019-12-03 12:30 | 181.06 | 161.46
2019-12-03 13:00 | 188.61 | 169.63
2019-12-03 13:30 | 189.45 | 174.65
2019-12-03 14:00 | 186.97 | 179.13
2019-12-03 14:30 | 199.04 | 192.3
2019-12-03 15:00 | 205.85 | 199.21
2019-12-03 15:30 | 212.37 | 205.81
2019-12-03 16:00 | 225.15 | 219.05
2019-12-03 16:30 | 231.12 | 225.39
2019-12-03 17:00 | 226.39 | 223.6
2019-12-03 17:30 | 231.54 | 229.88
2019-12-03 18:00 | 228.89 | 228.46
2019-12-03 18:30 | 226.1 | 225.62
2019-12-03 19:00 | 237 | 236.61
2019-12-03 19:30 | 236.55 | 236.22
2019-12-03 20:00 | 234.07 | 233.84
2019-12-03 20:30 | 225.24 | 223.51
2019-12-03 21:00 | 217.55 | 212.25
2019-12-03 21:30 | 202.66 | 201.01
2019-12-03 22:00 | 191.28 | 191.17
2019-12-03 22:30 | 176.97 | 176.51
2019-12-03 23:00 | 171 | 170.83
2019-12-03 23:30 | 157.64 | 157.63
2019-12-04 | 142.83 | 142.83
2019-12-04 00:30 | 133.01 | 133
2019-12-04 01:00 | 127.65 | 127.59
2019-12-04 01:30 | 124.28 | 124.17
2019-12-04 02:00 | 121.54 | 121.42
2019-12-04 02:30 | 120.73 | 120.66
2019-12-04 03:00 | 119.47 | 119.37
2019-12-04 03:30 | 120.01 | 119.94
2019-12-04 04:00 | 112.99 | 112.94
2019-12-04 04:30 | 117.67 | 117.65
2019-12-04 05:00 | 115.37 | 115.37
2019-12-04 05:30 | 111.23 | 111.2
2019-12-04 06:00 | 112.79 | 112.71
2019-12-04 06:30 | 119.83 | 118.89
2019-12-04 07:00 | 128.14 | 125.84
2019-12-04 07:30 | 134.42 | 127.42
2019-12-04 08:00 | 138.87 | 135.22
2019-12-04 08:30 | 139.83 | 136.71
2019-12-04 09:00 | 144.96 | 141.87
2019-12-04 09:30 | 138.75 | 135.54
2019-12-04 10:00 | 142.81 | 139.74
2019-12-04 10:30 | 142.74 | 139.16
2019-12-04 11:00 | 145.3 | 141.5
2019-12-04 11:30 | 145.49 | 141.91
2019-12-04 12:00 | 146.64 | 143.47
2019-12-04 12:30 | 149.08 | 146.02
2019-12-04 13:00 | 152.1 | 149.26
2019-12-04 13:30 | 152.44 | 149.8
2019-12-04 14:00 | 155.09 | 152.47
2019-12-04 14:30 | 166.63 | 166.26
2019-12-04 15:00 | 195.46 | 195.2
2019-12-04 15:30 | 204.59 | 204.33
2019-12-04 16:00 | 218.54 | 217.57
2019-12-04 16:30 | 235.72 | 228.23
2019-12-04 17:00 | 236.01 | 228.87
2019-12-04 17:30 | 229.07 | 226.41
2019-12-04 18:00 | 224.99 | 224.07
2019-12-04 18:30 | 223.62 | 223.5
2019-12-04 19:00 | 222.27 | 222.02
2019-12-04 19:30 | 233.04 | 232.91
2019-12-04 20:00 | 232 | 231.95
2019-12-04 20:30 | 222.75 | 222.75
2019-12-04 21:00 | 212.12 | 212.06
2019-12-04 21:30 | 196.63 | 196.63
2019-12-04 22:00 | 184.08 | 184.06
2019-12-04 22:30 | 176.72 | 176.63
2019-12-04 23:00 | 174.55 | 174.37
2019-12-04 23:30 | 136.52 | 136.18
2019-12-05 | 118.47 | 117.97
2019-12-05 00:30 | 132.42 | 131.87
2019-12-05 01:00 | 129.15 | 128.91
2019-12-05 01:30 | 124.39 | 124.28
2019-12-05 02:00 | 121.71 | 121.63
2019-12-05 02:30 | 119.59 | 119.55
2019-12-05 03:00 | 118.94 | 118.9
2019-12-05 03:30 | 109.81 | 109.74
2019-12-05 04:00 | 97.22 | 97.13
2019-12-05 04:30 | 97.69 | 97.58
2019-12-05 05:00 | 104.14 | 104.13
2019-12-05 05:30 | 100.52 | 100.46
2019-12-05 06:00 | 95.45 | 95.13
2019-12-05 06:30 | 88.82 | 88.15
2019-12-05 07:00 | 88.28 | 87.91
2019-12-05 07:30 | 104.49 | 104.49
2019-12-05 08:00 | 106.43 | 106.43
2019-12-05 08:30 | 96.53 | 96.53
2019-12-05 09:00 | 94.03 | 93.98
2019-12-05 09:30 | 104.51 | 104.31
2019-12-05 10:00 | 119.77 | 119.56
2019-12-05 10:30 | 141.43 | 141.12
2019-12-05 11:00 | 161.28 | 160.87
2019-12-05 11:30 | 164.88 | 164.47
2019-12-05 12:00 | 166.14 | 165.78
2019-12-05 12:30 | 169.09 | 168.72
2019-12-05 13:00 | 170.76 | 169.99
2019-12-05 13:30 | 187.42 | 183.46
2019-12-05 14:00 | 210.44 | 201.67
2019-12-05 14:30 | 223.08 | 214.76
2019-12-05 15:00 | 232.1 | 224.19
2019-12-05 15:30 | 242.9 | 235.22
2019-12-05 16:00 | 253.49 | 247.15
2019-12-05 16:30 | 232.05 | 225.49
2019-12-05 17:00 | 269.93 | 264.33
2019-12-05 17:30 | 266.85 | 264.7
2019-12-05 18:00 | 262.94 | 261.75
2019-12-05 18:30 | 254.37 | 253.82
2019-12-05 19:00 | 256.26 | 255.93
2019-12-05 19:30 | 247 | 246.97
2019-12-05 20:00 | 239.16 | 239.16
2019-12-05 20:30 | 232.58 | 232.57
2019-12-05 21:00 | 213.48 | 213.48
2019-12-05 21:30 | 211.64 | 211.64
2019-12-05 22:00 | 186.56 | 186.35
2019-12-05 22:30 | 176.75 | 176.37
2019-12-05 23:00 | 159.71 | 159.15
2019-12-05 23:30 | 138.6 | 137.77
2019-12-06 | 109.51 | 107.2
2019-12-06 00:30 | 104.74 | 102.35
2019-12-06 01:00 | 102.87 | 100.66
2019-12-06 01:30 | 123.07 | 121.79
2019-12-06 02:00 | 118.74 | 118.74
2019-12-06 02:30 | 117.92 | 117.89
2019-12-06 03:00 | 112.32 | 112.29
2019-12-06 03:30 | 110.05 | 109.99
2019-12-06 04:00 | 114.41 | 114.38
2019-12-06 04:30 | 117.79 | 117.76
2019-12-06 05:00 | 114.08 | 113.99
2019-12-06 05:30 | 108.46 | 108.44
2019-12-06 06:00 | 93.65 | 93.58
2019-12-06 06:30 | 81.81 | 81.46
2019-12-06 07:00 | 73.12 | 72.85
2019-12-06 07:30 | 82.85 | 82.85
2019-12-06 08:00 | 84.34 | 83.78
2019-12-06 08:30 | 113.13 | 108.65
2019-12-06 09:00 | 123.21 | 118.96
2019-12-06 09:30 | 138.89 | 135.03
2019-12-06 10:00 | 162.5 | 154.6
2019-12-06 10:30 | 195.02 | 183.99
2019-12-06 11:00 | 212 | 201.6
2019-12-06 11:30 | 223.77 | 213.18
2019-12-06 12:00 | 231.35 | 220.26
2019-12-06 12:30 | 236.2 | 224.83
2019-12-06 13:00 | 239.52 | 229.49
2019-12-06 13:30 | 215.37 | 207.99
2019-12-06 14:00 | 226.67 | 219.18
2019-12-06 14:30 | 266.02 | 259
2019-12-06 15:00 | 273.47 | 266.43
2019-12-06 15:30 | 281.53 | 274.4
2019-12-06 16:00 | 289.73 | 282.18
2019-12-06 16:30 | 293.32 | 285.79
2019-12-06 17:00 | 296.75 | 289.27
2019-12-06 17:30 | 291.82 | 285.15
2019-12-06 18:00 | 286.11 | 280.44
2019-12-06 18:30 | 283.3 | 278.87
2019-12-06 19:00 | 282.23 | 278.48
2019-12-06 19:30 | 282.69 | 279.15
2019-12-06 20:00 | 272.22 | 270.5
2019-12-06 20:30 | 268.91 | 268.12
2019-12-06 21:00 | 250.6 | 250.4
2019-12-06 21:30 | 232.78 | 232.61
2019-12-06 22:00 | 226.71 | 226.41
2019-12-06 22:30 | 224.99 | 224.63
2019-12-06 23:00 | 214.74 | 214.48
2019-12-06 23:30 | 193.67 | 192.87
2019-12-07 | 165.35 | 164.91
2019-12-07 00:30 | 160.06 | 159.63
2019-12-07 01:00 | 150.22 | 149.63
2019-12-07 01:30 | 126.01 | 125.07
2019-12-07 02:00 | 113.47 | 112.39
2019-12-07 02:30 | 123.28 | 121.95
2019-12-07 03:00 | 132.17 | 130.68
2019-12-07 03:30 | 133.44 | 131.87
2019-12-07 04:00 | 132.47 | 130.78
2019-12-07 04:30 | 131.53 | 129.78
2019-12-07 05:00 | 121.63 | 119.87
2019-12-07 05:30 | 121.13 | 119.52
2019-12-07 06:00 | 118.07 | 116.43
2019-12-07 06:30 | 95.26 | 93.45
2019-12-07 07:00 | 78.62 | 77.25
2019-12-07 07:30 | 77.96 | 77.62
2019-12-07 08:00 | 92.18 | 92.17
2019-12-07 08:30 | 119.77 | 118.72
2019-12-07 09:00 | 157.27 | 154.47
2019-12-07 09:30 | 199.35 | 188.73
2019-12-07 10:00 | 215.84 | 205.04
2019-12-07 10:30 | 219.43 | 209.82
2019-12-07 11:00 | 220.79 | 210.77
2019-12-07 11:30 | 220.4 | 210.06
2019-12-07 12:00 | 223 | 212.82
2019-12-07 12:30 | 226.97 | 217.09
2019-12-07 13:00 | 230.29 | 220.45
2019-12-07 13:30 | 232.72 | 222.59
2019-12-07 14:00 | 234.11 | 223.75
2019-12-07 14:30 | 238.53 | 228.13
2019-12-07 15:00 | 237.22 | 226.75
2019-12-07 15:30 | 205.49 | 198.34
2019-12-07 16:00 | 214.74 | 209.19
2019-12-07 16:30 | 235.95 | 233.7
2019-12-07 17:00 | 252.37 | 250.74
2019-12-07 17:30 | 253.78 | 252.7
2019-12-07 18:00 | 239.32 | 238.96
2019-12-07 18:30 | 239.76 | 239.76
2019-12-07 19:00 | 239.73 | 239.71
2019-12-07 19:30 | 239.72 | 239.71
2019-12-07 20:00 | 234.77 | 234.77
2019-12-07 20:30 | 225.68 | 225.62
2019-12-07 21:00 | 212.12 | 212.02
2019-12-07 21:30 | 204.38 | 204.34
2019-12-07 22:00 | 194.86 | 194.76
2019-12-07 22:30 | 190.41 | 190.34
2019-12-07 23:00 | 188.64 | 188.49
2019-12-07 23:30 | 170.69 | 170.1
2019-12-08 | 153.72 | 151.05
2019-12-08 00:30 | 138.23 | 136.22
2019-12-08 01:00 | 132.37 | 130.42
2019-12-08 01:30 | 127.78 | 125.82
2019-12-08 02:00 | 120.5 | 118.84
2019-12-08 02:30 | 129.02 | 127.13
2019-12-08 03:00 | 127.29 | 125.43
2019-12-08 03:30 | 123.02 | 121.11
2019-12-08 04:00 | 125.26 | 123.49
2019-12-08 04:30 | 125.44 | 123.7
2019-12-08 05:00 | 122.5 | 121.3
2019-12-08 05:30 | 123.71 | 122.64
2019-12-08 06:00 | 113.73 | 112.17
2019-12-08 06:30 | 96.29 | 93.6
2019-12-08 07:00 | 66.05 | 60.76
2019-12-08 07:30 | 55.53 | 51.39
2019-12-08 08:00 | 52.13 | 47.8
2019-12-08 08:30 | 62.04 | 61.7
2019-12-08 09:00 | 88.84 | 88.84
2019-12-08 09:30 | 109.28 | 109.23
2019-12-08 10:00 | 118.22 | 118.1
2019-12-08 10:30 | 117.28 | 117.13
2019-12-08 11:00 | 100.18 | 99.97
2019-12-08 11:30 | 98.37 | 98.07
2019-12-08 12:00 | 105.72 | 105.33
2019-12-08 12:30 | 112.07 | 111.64
2019-12-08 13:00 | 119.87 | 119.43
2019-12-08 13:30 | 116.61 | 114.68
2019-12-08 14:00 | 125.42 | 121.37
2019-12-08 14:30 | 145.89 | 142.11
2019-12-08 15:00 | 155.38 | 143.26
2019-12-08 15:30 | 183.72 | 172.08
2019-12-08 16:00 | 197.6 | 187.24
2019-12-08 16:30 | 206.26 | 196.79
2019-12-08 17:00 | 225.59 | 217.07
2019-12-08 17:30 | 225.85 | 217.89
2019-12-08 18:00 | 222.38 | 214.83
2019-12-08 18:30 | 231.89 | 224.89
2019-12-08 19:00 | 232.85 | 225.61
2019-12-08 19:30 | 234.59 | 227.6
2019-12-08 20:00 | 229.97 | 225.1
2019-12-08 20:30 | 214.77 | 213.81
2019-12-08 21:00 | 193.91 | 192.93
2019-12-08 21:30 | 187.09 | 187.09
2019-12-08 22:00 | 162.29 | 162.22
2019-12-08 22:30 | 161.65 | 161.56
2019-12-08 23:00 | 162.1 | 161.96
2019-12-08 23:30 | 159.52 | 159.19
2019-12-09 | 149.45 | 148.82
2019-12-09 00:30 | 138.47 | 137.58
2019-12-09 01:00 | 132.94 | 131.48
2019-12-09 01:30 | 127.61 | 126.03
2019-12-09 02:00 | 132.36 | 130.69
2019-12-09 02:30 | 126.27 | 124.4
2019-12-09 03:00 | 126.68 | 124.58
2019-12-09 03:30 | 127.14 | 125.12
2019-12-09 04:00 | 127.98 | 126
2019-12-09 04:30 | 124.45 | 122.29
2019-12-09 05:00 | 128.55 | 127.05
2019-12-09 05:30 | 110.89 | 108.84
2019-12-09 06:00 | 113.43 | 111.54
2019-12-09 06:30 | 140.69 | 139.57
2019-12-09 07:00 | 134.03 | 133.65
2019-12-09 07:30 | 124.74 | 124.54
2019-12-09 08:00 | 124.77 | 121.52
2019-12-09 08:30 | 117.61 | 115.64
2019-12-09 09:00 | 128.42 | 126.42
2019-12-09 09:30 | 122.01 | 119.49
2019-12-09 10:00 | 131.48 | 128.71
2019-12-09 10:30 | 136.33 | 133.45
2019-12-09 11:00 | 160.5 | 151.98
2019-12-09 11:30 | 179.05 | 169.82
2019-12-09 12:00 | 190.72 | 181.52
2019-12-09 12:30 | 204.55 | 195.91
2019-12-09 13:00 | 217 | 208.88
2019-12-09 13:30 | 236.93 | 229.11
2019-12-09 14:00 | 241.87 | 234.02
2019-12-09 14:30 | 228.11 | 219.99
2019-12-09 15:00 | 249.31 | 242.11
2019-12-09 15:30 | 256.1 | 249.44
2019-12-09 16:00 | 256.94 | 250.58
2019-12-09 16:30 | 266.34 | 263.54
2019-12-09 17:00 | 264.34 | 262.44
2019-12-09 17:30 | 266.15 | 264.62
2019-12-09 18:00 | 253.12 | 251.77
2019-12-09 18:30 | 244.27 | 244.16
2019-12-09 19:00 | 257.31 | 256.93
2019-12-09 19:30 | 257.16 | 256.19
2019-12-09 20:00 | 247.52 | 246.69
2019-12-09 20:30 | 232.95 | 232.25
2019-12-09 21:00 | 216.53 | 216.27
2019-12-09 21:30 | 204.82 | 204.74
2019-12-09 22:00 | 193.8 | 193.74
2019-12-09 22:30 | 193.87 | 193.77
2019-12-09 23:00 | 188.66 | 187.99
2019-12-09 23:30 | 176.28 | 175.96
2019-12-10 | 158.7 | 158.44
2019-12-10 00:30 | 147.88 | 147.79
2019-12-10 01:00 | 134.21 | 134.19
2019-12-10 01:30 | 136.28 | 136.27
2019-12-10 02:00 | 136.18 | 136.17
2019-12-10 02:30 | 130.73 | 130.72
2019-12-10 03:00 | 124.45 | 122.85
2019-12-10 03:30 | 121.42 | 119.76
2019-12-10 04:00 | 126.1 | 124.51
2019-12-10 04:30 | 116.08 | 114.43
2019-12-10 05:00 | 120.86 | 119.32
2019-12-10 05:30 | 134.64 | 133.46
2019-12-10 06:00 | 147.53 | 146.8
2019-12-10 06:30 | 149.82 | 149.52
2019-12-10 07:00 | 153.58 | 152.77
2019-12-10 07:30 | 172.02 | 162.37
2019-12-10 08:00 | 181.48 | 171.15
2019-12-10 08:30 | 200.29 | 190.42
2019-12-10 09:00 | 209.15 | 199.3
2019-12-10 09:30 | 230.82 | 220.84
2019-12-10 10:00 | 227.71 | 216.92
2019-12-10 10:30 | 228.45 | 217.44
2019-12-10 11:00 | 218.96 | 206.98
2019-12-10 11:30 | 215.52 | 202.67
2019-12-10 12:00 | 230.5 | 217.86
2019-12-10 12:30 | 230.08 | 221.36
2019-12-10 13:00 | 236.7 | 228.09
2019-12-10 13:30 | 240.27 | 231.67
2019-12-10 14:00 | 242.96 | 234.03
2019-12-10 14:30 | 251.51 | 242.57
2019-12-10 15:00 | 259.6 | 250.63
2019-12-10 15:30 | 274.33 | 265.89
2019-12-10 16:00 | 283.82 | 275.33
2019-12-10 16:30 | 292.02 | 279.63
2019-12-10 17:00 | 291.95 | 280.39
2019-12-10 17:30 | 289.46 | 279.24
2019-12-10 18:00 | 285.25 | 276.5
2019-12-10 18:30 | 276.13 | 271.84
2019-12-10 19:00 | 276.37 | 272
2019-12-10 19:30 | 265.64 | 261.3
2019-12-10 20:00 | 251.89 | 247.92
2019-12-10 20:30 | 237.59 | 235.76
2019-12-10 21:00 | 216.97 | 216.97
2019-12-10 21:30 | 201.8 | 201.79
2019-12-10 22:00 | 190.12 | 190.12
2019-12-10 22:30 | 183.34 | 183.3
2019-12-10 23:00 | 181.76 | 181.44
2019-12-10 23:30 | 176.16 | 175.39
2019-12-11 | 163.39 | 162.71
2019-12-11 00:30 | 132.99 | 132.44
2019-12-11 01:00 | 145.5 | 144.68
2019-12-11 01:30 | 138.09 | 137.07
2019-12-11 02:00 | 137.45 | 136.29
2019-12-11 02:30 | 140.65 | 139.39
2019-12-11 03:00 | 140.19 | 138.92
2019-12-11 03:30 | 139.16 | 137.85
2019-12-11 04:00 | 123.51 | 121.94
2019-12-11 04:30 | 123.86 | 122.35
2019-12-11 05:00 | 135.44 | 134.04
2019-12-11 05:30 | 143.14 | 142.08
2019-12-11 06:00 | 153.57 | 152.97
2019-12-11 06:30 | 145.21 | 144.94
2019-12-11 07:00 | 145.52 | 145.5
2019-12-11 07:30 | 168.74 | 157.99
2019-12-11 08:00 | 174.8 | 162.06
2019-12-11 08:30 | 178.36 | 165.93
2019-12-11 09:00 | 195.52 | 183.51
2019-12-11 09:30 | 206.51 | 193.49
2019-12-11 10:00 | 219.05 | 205.62
2019-12-11 10:30 | 238.51 | 224.9
2019-12-11 11:00 | 250.42 | 231.05
2019-12-11 11:30 | 242.49 | 230.15
2019-12-11 12:00 | 228.08 | 222.87
2019-12-11 12:30 | 222.09 | 215.7
2019-12-11 13:00 | 228.88 | 222.53
2019-12-11 13:30 | 237.54 | 231.18
2019-12-11 14:00 | 242.39 | 235.43
2019-12-11 14:30 | 249.75 | 242.99
2019-12-11 15:00 | 264.24 | 257.58
2019-12-11 15:30 | 285.96 | 276.03
2019-12-11 16:00 | 290.37 | 279.85
2019-12-11 16:30 | 281.12 | 272.16
2019-12-11 17:00 | 281.36 | 273.5
2019-12-11 17:30 | 281.4 | 274.49
2019-12-11 18:00 | 273.98 | 269.74
2019-12-11 18:30 | 266.27 | 264.58
2019-12-11 19:00 | 272.38 | 270.56
2019-12-11 19:30 | 265.74 | 264.11
2019-12-11 20:00 | 264.88 | 263.59
2019-12-11 20:30 | 248.88 | 248.51
2019-12-11 21:00 | 235.1 | 235.1
2019-12-11 21:30 | 218.97 | 218.96
2019-12-11 22:00 | 204.44 | 204.02
2019-12-11 22:30 | 193.73 | 193.4
2019-12-11 23:00 | 181.74 | 181.49
2019-12-11 23:30 | 164.23 | 163.65
2019-12-12 | 157.04 | 155.96
2019-12-12 00:30 | 144.25 | 143.15
2019-12-12 01:00 | 138.22 | 137.17
2019-12-12 01:30 | 138.1 | 136.99
2019-12-12 02:00 | 136.37 | 135.28
2019-12-12 02:30 | 136.75 | 135.57
2019-12-12 03:00 | 134.28 | 133.04
2019-12-12 03:30 | 136.37 | 135.18
2019-12-12 04:00 | 133.85 | 132.54
2019-12-12 04:30 | 134.39 | 133.15
2019-12-12 05:00 | 131.61 | 130.36
2019-12-12 05:30 | 138.09 | 137.09
2019-12-12 06:00 | 147.59 | 146.93
2019-12-12 06:30 | 154.92 | 154.7
2019-12-12 07:00 | 172.04 | 172.02
2019-12-12 07:30 | 184.69 | 184.61
2019-12-12 08:00 | 190.81 | 190.54
2019-12-12 08:30 | 189.04 | 188.22
2019-12-12 09:00 | 196.61 | 195.58
2019-12-12 09:30 | 198.58 | 197.77
2019-12-12 10:00 | 197.76 | 196.7
2019-12-12 10:30 | 202.43 | 199.39
2019-12-12 11:00 | 203.07 | 199.65
2019-12-12 11:30 | 202.9 | 199.19
2019-12-12 12:00 | 204.88 | 200.88
2019-12-12 12:30 | 212 | 207.89
2019-12-12 13:00 | 220.07 | 216.04
2019-12-12 13:30 | 227.73 | 223.19
2019-12-12 14:00 | 235.96 | 231.08
2019-12-12 14:30 | 244.78 | 240.04
2019-12-12 15:00 | 251.45 | 246.73
2019-12-12 15:30 | 260.02 | 254.91
2019-12-12 16:00 | 271.96 | 267.06
2019-12-12 16:30 | 288.54 | 283.65
2019-12-12 17:00 | 291.63 | 287.29
2019-12-12 17:30 | 284.99 | 281.64
2019-12-12 18:00 | 280.88 | 278.42
2019-12-12 18:30 | 272.3 | 270.49
2019-12-12 19:00 | 271.19 | 269.19
2019-12-12 19:30 | 266.67 | 264.6
2019-12-12 20:00 | 266.67 | 264.92
2019-12-12 20:30 | 256.35 | 254
2019-12-12 21:00 | 240.86 | 239.74
2019-12-12 21:30 | 224.42 | 223.95
2019-12-12 22:00 | 213.8 | 213.55
2019-12-12 22:30 | 201.76 | 201.63
2019-12-12 23:00 | 195.15 | 195.13
2019-12-12 23:30 | 184.08 | 184.07
2019-12-13 | 169.1 | 169.01
2019-12-13 00:30 | 158.55 | 158.26
2019-12-13 01:00 | 152.47 | 151.94
2019-12-13 01:30 | 149.39 | 148.79
2019-12-13 02:00 | 145.33 | 144.46
2019-12-13 02:30 | 142.45 | 140.8
2019-12-13 03:00 | 141.8 | 140.18
2019-12-13 03:30 | 141.42 | 139.81
2019-12-13 04:00 | 142.38 | 140.87
2019-12-13 04:30 | 143.93 | 142.63
2019-12-13 05:00 | 145.96 | 144.86
2019-12-13 05:30 | 151 | 149.84
2019-12-13 06:00 | 158.12 | 156.98
2019-12-13 06:30 | 155.81 | 155.78
2019-12-13 07:00 | 167.82 | 167.82
2019-12-13 07:30 | 190.83 | 190.82
2019-12-13 08:00 | 196.28 | 196.25
2019-12-13 08:30 | 207.07 | 207.04
2019-12-13 09:00 | 234.81 | 233.49
2019-12-13 09:30 | 248.04 | 245.47
2019-12-13 10:00 | 243.23 | 240.66
2019-12-13 10:30 | 230.68 | 228.04
2019-12-13 11:00 | 230.57 | 227.72
2019-12-13 11:30 | 242.87 | 240.01
2019-12-13 12:00 | 242.37 | 239.61
2019-12-13 12:30 | 238.33 | 236.06
2019-12-13 13:00 | 228.84 | 227.51
2019-12-13 13:30 | 213.07 | 213.04
2019-12-13 14:00 | 203.89 | 203.89
2019-12-13 14:30 | 216.73 | 216.73
2019-12-13 15:00 | 224 | 223.99
2019-12-13 15:30 | 210.57 | 210.56
2019-12-13 16:00 | 196.99 | 196.98
2019-12-13 16:30 | 192.17 | 192.17
2019-12-13 17:00 | 195.42 | 195.41
2019-12-13 17:30 | 206.69 | 206.65
2019-12-13 18:00 | 205.48 | 205.4
2019-12-13 18:30 | 206.02 | 205.87
2019-12-13 19:00 | 218.13 | 218.03
2019-12-13 19:30 | 216.06 | 215.95
2019-12-13 20:00 | 211.63 | 211.46
2019-12-13 20:30 | 203.58 | 203.3
2019-12-13 21:00 | 195.84 | 195.47
2019-12-13 21:30 | 192.17 | 191.73
2019-12-13 22:00 | 185.41 | 184.72
2019-12-13 22:30 | 179.95 | 179.16
2019-12-13 23:00 | 178.9 | 177.98
2019-12-13 23:30 | 163.71 | 162.91
2019-12-14 | 130.18 | 129.02
2019-12-14 00:30 | 127.62 | 126.35
2019-12-14 01:00 | 129.91 | 128.53
2019-12-14 01:30 | 128.95 | 127.32
2019-12-14 02:00 | 127.95 | 126.33
2019-12-14 02:30 | 126.12 | 124.26
2019-12-14 03:00 | 122.98 | 120.82
2019-12-14 03:30 | 123.91 | 121.73
2019-12-14 04:00 | 122.41 | 120.58
2019-12-14 04:30 | 123.8 | 121.89
2019-12-14 05:00 | 122.91 | 121.12
2019-12-14 05:30 | 117.63 | 115.83
2019-12-14 06:00 | 112.32 | 110.61
2019-12-14 06:30 | 110.82 | 109.24
2019-12-14 07:00 | 106.67 | 105.36
2019-12-14 07:30 | 125.4 | 124.8
2019-12-14 08:00 | 123.34 | 123.06
2019-12-14 08:30 | 130.31 | 130.31
2019-12-14 09:00 | 126.98 | 126.97
2019-12-14 09:30 | 141.43 | 140.38
2019-12-14 10:00 | 155.9 | 153.71
2019-12-14 10:30 | 167.62 | 167.24
2019-12-14 11:00 | 173.39 | 172.92
2019-12-14 11:30 | 164.64 | 164.19
2019-12-14 12:00 | 163.65 | 163.19
2019-12-14 12:30 | 164.6 | 164.08
2019-12-14 13:00 | 166.68 | 166.11
2019-12-14 13:30 | 161.27 | 160.67
2019-12-14 14:00 | 172.38 | 171.69
2019-12-14 14:30 | 192.14 | 191.43
2019-12-14 15:00 | 201.7 | 200.87
2019-12-14 15:30 | 221.16 | 215.19
2019-12-14 16:00 | 228.78 | 222.63
2019-12-14 16:30 | 243.13 | 237.38
2019-12-14 17:00 | 248.34 | 242.44
2019-12-14 17:30 | 245.31 | 239.68
2019-12-14 18:00 | 245.93 | 240.84
2019-12-14 18:30 | 240.03 | 237.95
2019-12-14 19:00 | 241.88 | 240.28
2019-12-14 19:30 | 242.91 | 241.29
2019-12-14 20:00 | 238.92 | 237.5
2019-12-14 20:30 | 233.62 | 232.45
2019-12-14 21:00 | 222.81 | 222.02
2019-12-14 21:30 | 216.15 | 215.56
2019-12-14 22:00 | 206.29 | 206.12
2019-12-14 22:30 | 199.07 | 198.5
2019-12-14 23:00 | 195.54 | 194.89
2019-12-14 23:30 | 184.88 | 184.53
2019-12-15 | 160.81 | 160.42
2019-12-15 00:30 | 155.9 | 155.46
2019-12-15 01:00 | 151.41 | 150.84
2019-12-15 01:30 | 146 | 145.28
2019-12-15 02:00 | 142.73 | 141.89
2019-12-15 02:30 | 138.13 | 137.14
2019-12-15 03:00 | 122.74 | 121.5
2019-12-15 03:30 | 110.12 | 108.63
2019-12-15 04:00 | 98.77 | 97.16
2019-12-15 04:30 | 90.17 | 88.43
2019-12-15 05:00 | 90.69 | 88.99
2019-12-15 05:30 | 83.71 | 81.94
2019-12-15 06:00 | 79.65 | 77.85
2019-12-15 06:30 | 79.7 | 78.17
2019-12-15 07:00 | 60.33 | 59.07
2019-12-15 07:30 | 61.26 | 60.82
2019-12-15 08:00 | 66.12 | 64.58
2019-12-15 08:30 | 83.45 | 80.57
2019-12-15 09:00 | 102.6 | 88.93
2019-12-15 09:30 | 117.71 | 102.67
2019-12-15 10:00 | 141.57 | 127.76
2019-12-15 10:30 | 154.24 | 140.27
2019-12-15 11:00 | 164.74 | 150.82
2019-12-15 11:30 | 171.21 | 157.54
2019-12-15 12:00 | 187.68 | 175.03
2019-12-15 12:30 | 190.91 | 178.09
2019-12-15 13:00 | 195.65 | 182.68
2019-12-15 13:30 | 206.78 | 194.27
2019-12-15 14:00 | 224.14 | 212.58
2019-12-15 14:30 | 237.96 | 229.55
2019-12-15 15:00 | 251.16 | 244.38
2019-12-15 15:30 | 243.81 | 239.66
2019-12-15 16:00 | 247.17 | 244.28
2019-12-15 16:30 | 257.4 | 254.21
2019-12-15 17:00 | 260.52 | 257.83
2019-12-15 17:30 | 258.75 | 256.58
2019-12-15 18:00 | 259.86 | 258.18
2019-12-15 18:30 | 252.58 | 252.05
2019-12-15 19:00 | 254.34 | 254.33
2019-12-15 19:30 | 251.04 | 251.04
2019-12-15 20:00 | 249.05 | 249.05
2019-12-15 20:30 | 241.37 | 241.37
2019-12-15 21:00 | 228.46 | 228.44
2019-12-15 21:30 | 212.94 | 212.92
2019-12-15 22:00 | 197.57 | 197.45
2019-12-15 22:30 | 195.78 | 195.49
2019-12-15 23:00 | 191.77 | 191.37
2019-12-15 23:30 | 179.03 | 178.87
2019-12-16 | 164.17 | 164.16
2019-12-16 00:30 | 153.99 | 153.97
2019-12-16 01:00 | 149.63 | 147.75
2019-12-16 01:30 | 140.85 | 138.65
2019-12-16 02:00 | 124.25 | 121.91
2019-12-16 02:30 | 126.44 | 124.81
2019-12-16 03:00 | 118.94 | 117.19
2019-12-16 03:30 | 111.58 | 109.78
2019-12-16 04:00 | 106.31 | 104.54
2019-12-16 04:30 | 101.61 | 100.16
2019-12-16 05:00 | 113.17 | 112.1
2019-12-16 05:30 | 122.24 | 121.25
2019-12-16 06:00 | 124.58 | 123.81
2019-12-16 06:30 | 116.74 | 116.32
2019-12-16 07:00 | 114.67 | 114.66
2019-12-16 07:30 | 129.74 | 129.48
2019-12-16 08:00 | 130.54 | 130.51
2019-12-16 08:30 | 148.55 | 148.34
2019-12-16 09:00 | 172.06 | 171.24
2019-12-16 09:30 | 217.25 | 216.18
2019-12-16 10:00 | 239.34 | 238.34
2019-12-16 10:30 | 244.48 | 243.2
2019-12-16 11:00 | 253.15 | 251.76
2019-12-16 11:30 | 254.93 | 252.59
2019-12-16 12:00 | 264.34 | 259.15
2019-12-16 12:30 | 267.67 | 263.57
2019-12-16 13:00 | 271.77 | 267.42
2019-12-16 13:30 | 277.84 | 273.31
2019-12-16 14:00 | 277.35 | 273.2
2019-12-16 14:30 | 280.33 | 276.33
2019-12-16 15:00 | 303.55 | 299.58
2019-12-16 15:30 | 298.62 | 295.41
2019-12-16 16:00 | 293.35 | 291.3
2019-12-16 16:30 | 286.64 | 285.17
2019-12-16 17:00 | 285.35 | 284.56
2019-12-16 17:30 | 279.69 | 279.42
2019-12-16 18:00 | 267.64 | 267.33
2019-12-16 18:30 | 261.96 | 261.95
2019-12-16 19:00 | 257.06 | 257.06
2019-12-16 19:30 | 244.16 | 244.15
2019-12-16 20:00 | 225.98 | 225.98
2019-12-16 20:30 | 230.08 | 230.08
2019-12-16 21:00 | 223.86 | 223.86
2019-12-16 21:30 | 208.54 | 208.54
2019-12-16 22:00 | 197.97 | 197.92
2019-12-16 22:30 | 174.96 | 174.81
2019-12-16 23:00 | 174.37 | 174.14
2019-12-16 23:30 | 159.99 | 159.57
2019-12-17 | 140.55 | 139.46
2019-12-17 00:30 | 140.51 | 139.38
2019-12-17 01:00 | 134.1 | 132.55
2019-12-17 01:30 | 131.51 | 129.96
2019-12-17 02:00 | 128.86 | 127.4
2019-12-17 02:30 | 123.05 | 121.48
2019-12-17 03:00 | 137.32 | 135.92
2019-12-17 03:30 | 124.3 | 122.92
2019-12-17 04:00 | 109.1 | 107.54
2019-12-17 04:30 | 98.23 | 96.5
2019-12-17 05:00 | 88.74 | 87.05
2019-12-17 05:30 | 92.72 | 91.13
2019-12-17 06:00 | 100.95 | 99.28
2019-12-17 06:30 | 99.83 | 97.85
2019-12-17 07:00 | 110.43 | 109.17
2019-12-17 07:30 | 112.17 | 111.42
2019-12-17 08:00 | 118.9 | 118.49
2019-12-17 08:30 | 119.97 | 119.18
2019-12-17 09:00 | 124.2 | 122.88
2019-12-17 09:30 | 140.55 | 139.23
2019-12-17 10:00 | 145.7 | 141.23
2019-12-17 10:30 | 127.44 | 121.77
2019-12-17 11:00 | 114.13 | 107.97
2019-12-17 11:30 | 95.05 | 87.19
2019-12-17 12:00 | 88.84 | 80.46
2019-12-17 12:30 | 92.38 | 84.34
2019-12-17 13:00 | 101.87 | 94.82
2019-12-17 13:30 | 109.27 | 102.89
2019-12-17 14:00 | 106.17 | 99.44
2019-12-17 14:30 | 144.22 | 129.95
2019-12-17 15:00 | 133.93 | 124.8
2019-12-17 15:30 | 136.57 | 128.03
2019-12-17 16:00 | 156.44 | 149.59
2019-12-17 16:30 | 167.4 | 161.13
2019-12-17 17:00 | 184.04 | 178.67
2019-12-17 17:30 | 193.62 | 189.03
2019-12-17 18:00 | 206.62 | 205.23
2019-12-17 18:30 | 214.99 | 211.94
2019-12-17 19:00 | 227.79 | 225.09
2019-12-17 19:30 | 227.77 | 224.97
2019-12-17 20:00 | 223.06 | 221.12
2019-12-17 20:30 | 211.3 | 211.29
2019-12-17 21:00 | 201.81 | 201.44
2019-12-17 21:30 | 192.25 | 191.65
2019-12-17 22:00 | 171.6 | 170.64
2019-12-17 22:30 | 167.81 | 167.1
2019-12-17 23:00 | 172.1 | 171.33
2019-12-17 23:30 | 158.91 | 157.88
2019-12-18 | 130.76 | 129.16
2019-12-18 00:30 | 129.62 | 128
2019-12-18 01:00 | 123.47 | 121.61
2019-12-18 01:30 | 121.58 | 119.58
2019-12-18 02:00 | 116.32 | 114.21
2019-12-18 02:30 | 119.92 | 117.94
2019-12-18 03:00 | 119.25 | 117.22
2019-12-18 03:30 | 118.53 | 116.69
2019-12-18 04:00 | 116.63 | 114.82
2019-12-18 04:30 | 109.11 | 107.34
2019-12-18 05:00 | 112.37 | 110.95
2019-12-18 05:30 | 112.08 | 110.7
2019-12-18 06:00 | 110.05 | 108.51
2019-12-18 06:30 | 95.98 | 94.55
2019-12-18 07:00 | 89.24 | 88.2
2019-12-18 07:30 | 95.31 | 94.7
2019-12-18 08:00 | 74.08 | 74.08
2019-12-18 08:30 | 75.32 | 74.67
2019-12-18 09:00 | 102.53 | 101.81
2019-12-18 09:30 | 94.48 | 93.27
2019-12-18 10:00 | 92.07 | 90.44
2019-12-18 10:30 | 88.67 | 84.73
2019-12-18 11:00 | 89.9 | 81.32
2019-12-18 11:30 | 95.13 | 86.96
2019-12-18 12:00 | 89.84 | 81.56
2019-12-18 12:30 | 91.98 | 85.03
2019-12-18 13:00 | 95.27 | 88.58
2019-12-18 13:30 | 99.04 | 92.52
2019-12-18 14:00 | 88.63 | 80.71
2019-12-18 14:30 | 105.36 | 96.7
2019-12-18 15:00 | 116.83 | 95.94
2019-12-18 15:30 | 126.93 | 108.05
2019-12-18 16:00 | 145.4 | 129.74
2019-12-18 16:30 | 160.38 | 146.43
2019-12-18 17:00 | 177.88 | 165.71
2019-12-18 17:30 | 189.14 | 179.42
2019-12-18 18:00 | 204.71 | 201.17
2019-12-18 18:30 | 216.73 | 213.95
2019-12-18 19:00 | 227.98 | 225.13
2019-12-18 19:30 | 227.38 | 224.46
2019-12-18 20:00 | 219.53 | 216.99
2019-12-18 20:30 | 203.98 | 202.91
2019-12-18 21:00 | 174.53 | 174.51
2019-12-18 21:30 | 165.85 | 164.88
2019-12-18 22:00 | 148.34 | 146.98
2019-12-18 22:30 | 151.94 | 150.75
2019-12-18 23:00 | 156.98 | 155.76
2019-12-18 23:30 | 139.89 | 138.61
2019-12-19 | 108.19 | 106.03
2019-12-19 00:30 | 90.2 | 87.65
2019-12-19 01:00 | 85.27 | 82.19
2019-12-19 01:30 | 77.31 | 73.78
2019-12-19 02:00 | 75.43 | 71.85
2019-12-19 02:30 | 69.66 | 65.86
2019-12-19 03:00 | 76.29 | 72.99
2019-12-19 03:30 | 74.98 | 71.66
2019-12-19 04:00 | 74.53 | 71.28
2019-12-19 04:30 | 65.24 | 61.88
2019-12-19 05:00 | 68.66 | 66.16
2019-12-19 05:30 | 69.38 | 67.13
2019-12-19 06:00 | 83.48 | 81.33
2019-12-19 06:30 | 73.97 | 71.87
2019-12-19 07:00 | 62.29 | 60.49
2019-12-19 07:30 | 60.18 | 59.08
2019-12-19 08:00 | 57.16 | 57.15
2019-12-19 08:30 | 71.12 | 70.7
2019-12-19 09:00 | 77.89 | 77.31
2019-12-19 09:30 | 75.01 | 74.1
2019-12-19 10:00 | 63.7 | 62.1
2019-12-19 10:30 | 53.34 | 50.77
2019-12-19 11:00 | 44.22 | 40.15
2019-12-19 11:30 | 49.42 | 13.16
2019-12-19 12:00 | 73.74 | -5.4
2019-12-19 12:30 | 73.87 | 2.02
2019-12-19 13:00 | 83.48 | -30.41
2019-12-19 13:30 | 92.11 | -43.82
2019-12-19 14:00 | 93.94 | 56.21
2019-12-19 14:30 | 104.47 | 72.67
2019-12-19 15:00 | 84.21 | 36.48
2019-12-19 15:30 | 95.91 | 60.35
2019-12-19 16:00 | 132.18 | 110.52
2019-12-19 16:30 | 150.29 | 131.99
2019-12-19 17:00 | 173.28 | 157.68
2019-12-19 17:30 | 198.95 | 186.35
2019-12-19 18:00 | 212.38 | 205
2019-12-19 18:30 | 229.22 | 225.36
2019-12-19 19:00 | 240.72 | 236.78
2019-12-19 19:30 | 238.45 | 234.52
2019-12-19 20:00 | 225.92 | 222.21
2019-12-19 20:30 | 215.59 | 212.96
2019-12-19 21:00 | 201.16 | 201.15
2019-12-19 21:30 | 192.44 | 191.57
2019-12-19 22:00 | 170.26 | 169.44
2019-12-19 22:30 | 173.73 | 172.99
2019-12-19 23:00 | 167.82 | 166.88
2019-12-19 23:30 | 143.5 | 142.14
2019-12-20 | 121.69 | 119.67
2019-12-20 00:30 | 112.39 | 110.21
2019-12-20 01:00 | 102.73 | 100.1
2019-12-20 01:30 | 96.25 | 93.33
2019-12-20 02:00 | 83.52 | 80.01
2019-12-20 02:30 | 69.02 | 64.96
2019-12-20 03:00 | 71.43 | 67.7
2019-12-20 03:30 | 80.86 | 77.72
2019-12-20 04:00 | 72.43 | 69.05
2019-12-20 04:30 | 72.54 | 69.55
2019-12-20 05:00 | 71.22 | 68.56
2019-12-20 05:30 | 78.57 | 76.24
2019-12-20 06:00 | 94.21 | 92.01
2019-12-20 06:30 | 77.23 | 74.95
2019-12-20 07:00 | 61.71 | 60.74
2019-12-20 07:30 | 61.48 | 60.13
2019-12-20 08:00 | 67.98 | 62.69
2019-12-20 08:30 | 62.05 | 51.97
2019-12-20 09:00 | 81.84 | 52.01
2019-12-20 09:30 | 89.62 | 60.51
2019-12-20 10:00 | 99.45 | 72.17
2019-12-20 10:30 | 106.86 | 80.41
2019-12-20 11:00 | 110.19 | 84.18
2019-12-20 11:30 | 106.43 | 78.44
2019-12-20 12:00 | 104.47 | 74.74
2019-12-20 12:30 | 119.79 | 95.37
2019-12-20 13:00 | 131.72 | 110.07
2019-12-20 13:30 | 138.72 | 118.74
2019-12-20 14:00 | 153.51 | 135.44
2019-12-20 14:30 | 166.29 | 149.62
2019-12-20 15:00 | 150.84 | 132.29
2019-12-20 15:30 | 168.46 | 152.36
2019-12-20 16:00 | 177.45 | 162.01
2019-12-20 16:30 | 177.75 | 162.73
2019-12-20 17:00 | 189.9 | 176.17
2019-12-20 17:30 | 209.7 | 198.38
2019-12-20 18:00 | 227.45 | 218.09
2019-12-20 18:30 | 226.95 | 218.42
2019-12-20 19:00 | 229.66 | 220.83
2019-12-20 19:30 | 231.65 | 222.83
2019-12-20 20:00 | 213.48 | 204.57
2019-12-20 20:30 | 197.37 | 193.77
2019-12-20 21:00 | 189.03 | 185.92
2019-12-20 21:30 | 165.82 | 163.03
2019-12-20 22:00 | 148.56 | 147.92
2019-12-20 22:30 | 154.8 | 154.74
2019-12-20 23:00 | 146.38 | 146.27
2019-12-20 23:30 | 129.31 | 128.96
2019-12-21 | 109.39 | 108.58
2019-12-21 00:30 | 115.77 | 114.55
2019-12-21 01:00 | 115.75 | 114.09
2019-12-21 01:30 | 95.73 | 93.43
2019-12-21 02:00 | 106.04 | 103.44
2019-12-21 02:30 | 109.51 | 106.99
2019-12-21 03:00 | 104.67 | 102.03
2019-12-21 03:30 | 103.26 | 100.63
2019-12-21 04:00 | 102.12 | 99.56
2019-12-21 04:30 | 101.65 | 99.36
2019-12-21 05:00 | 111.99 | 110.33
2019-12-21 05:30 | 115.64 | 114.11
2019-12-21 06:00 | 102.9 | 100.94
2019-12-21 06:30 | 85.9 | 83.6
2019-12-21 07:00 | 67.38 | 64.94
2019-12-21 07:30 | 59.76 | 56.95
2019-12-21 08:00 | 55.04 | 54.62
2019-12-21 08:30 | 60.33 | 60.26
2019-12-21 09:00 | 67.44 | 67.22
2019-12-21 09:30 | 87.37 | 86.9
2019-12-21 10:00 | 96.59 | 95.97
2019-12-21 10:30 | 97.42 | 92.28
2019-12-21 11:00 | 100.35 | 87.81
2019-12-21 11:30 | 110.75 | 89.9
2019-12-21 12:00 | 116.05 | 95.96
2019-12-21 12:30 | 107.14 | 84.39
2019-12-21 13:00 | 112.83 | 91.8
2019-12-21 13:30 | 127.2 | 108.51
2019-12-21 14:00 | 129.04 | 109.71
2019-12-21 14:30 | 131.55 | 112.33
2019-12-21 15:00 | 132.85 | 113.59
2019-12-21 15:30 | 140.15 | 121.6
2019-12-21 16:00 | 161.09 | 144.7
2019-12-21 16:30 | 172.32 | 157
2019-12-21 17:00 | 200.04 | 187.09
2019-12-21 17:30 | 235.11 | 224.59
2019-12-21 18:00 | 253.2 | 244.12
2019-12-21 18:30 | 250.49 | 242.03
2019-12-21 19:00 | 251.11 | 242.33
2019-12-21 19:30 | 248.85 | 239.56
2019-12-21 20:00 | 245.62 | 236.85
2019-12-21 20:30 | 239.09 | 231.34
2019-12-21 21:00 | 220.07 | 216.42
2019-12-21 21:30 | 209.42 | 206.86
2019-12-21 22:00 | 194.25 | 193.73
2019-12-21 22:30 | 192.37 | 192.36
2019-12-21 23:00 | 185.03 | 184.94
2019-12-21 23:30 | 172.99 | 172.79
2019-12-22 | 160.88 | 160.4
2019-12-22 00:30 | 142.63 | 141.79
2019-12-22 01:00 | 139.23 | 138.04
2019-12-22 01:30 | 133.72 | 132.22
2019-12-22 02:00 | 133.86 | 132.16
2019-12-22 02:30 | 131.43 | 129.56
2019-12-22 03:00 | 128.8 | 127.06
2019-12-22 03:30 | 124.3 | 122.44
2019-12-22 04:00 | 113.93 | 111.92
2019-12-22 04:30 | 112.19 | 110.21
2019-12-22 05:00 | 116.1 | 114.16
2019-12-22 05:30 | 112.95 | 110.86
2019-12-22 06:00 | 110.92 | 108.97
2019-12-22 06:30 | 78.05 | 76.01
2019-12-22 07:00 | 49.22 | 47.01
2019-12-22 07:30 | 40.15 | 38.96
2019-12-22 08:00 | 41.14 | 40.84
2019-12-22 08:30 | 45.49 | 45.49
2019-12-22 09:00 | 50.74 | 50.69
2019-12-22 09:30 | 79.48 | 79.32
2019-12-22 10:00 | 94.85 | 94.59
2019-12-22 10:30 | 110.25 | 108.88
2019-12-22 11:00 | 129.91 | 126.48
2019-12-22 11:30 | 139.36 | 135.98
2019-12-22 12:00 | 148.01 | 144.62
2019-12-22 12:30 | 158.67 | 155.44
2019-12-22 13:00 | 178.22 | 175.27
2019-12-22 13:30 | 191.83 | 188.99
2019-12-22 14:00 | 207.2 | 197.09
2019-12-22 14:30 | 206.63 | 195.69
2019-12-22 15:00 | 205.77 | 194.57
2019-12-22 15:30 | 217.83 | 207.37
2019-12-22 16:00 | 235.25 | 225.7
2019-12-22 16:30 | 238.82 | 229.61
2019-12-22 17:00 | 242.21 | 233.37
2019-12-22 17:30 | 241.02 | 232.68
2019-12-22 18:00 | 230.56 | 227.99
2019-12-22 18:30 | 221.47 | 219.4
2019-12-22 19:00 | 223.54 | 221.37
2019-12-22 19:30 | 222.89 | 220.76
2019-12-22 20:00 | 222.86 | 220.96
2019-12-22 20:30 | 217.18 | 215.53
2019-12-22 21:00 | 205.61 | 204.3
2019-12-22 21:30 | 195.32 | 194.34
2019-12-22 22:00 | 190.56 | 190
2019-12-22 22:30 | 185.09 | 184.7
2019-12-22 23:00 | 183.93 | 183.63
2019-12-22 23:30 | 172.7 | 172.53
2019-12-23 | 156.47 | 156.41
2019-12-23 00:30 | 145.49 | 144.6
2019-12-23 01:00 | 140 | 138.62
2019-12-23 01:30 | 135.73 | 134.05
2019-12-23 02:00 | 131.16 | 129.31
2019-12-23 02:30 | 124.3 | 122.34
2019-12-23 03:00 | 121.91 | 119.8
2019-12-23 03:30 | 115 | 112.78
2019-12-23 04:00 | 109.32 | 106.94
2019-12-23 04:30 | 115.2 | 113.16
2019-12-23 05:00 | 121.84 | 120.15
2019-12-23 05:30 | 128.7 | 127.19
2019-12-23 06:00 | 142.03 | 140.9
2019-12-23 06:30 | 139.96 | 139.4
2019-12-23 07:00 | 138.06 | 137.86
2019-12-23 07:30 | 151.9 | 151.89
2019-12-23 08:00 | 139.25 | 139.23
2019-12-23 08:30 | 145.55 | 145.43
2019-12-23 09:00 | 158.57 | 155.97
2019-12-23 09:30 | 159.38 | 156.36
2019-12-23 10:00 | 155.42 | 151.91
2019-12-23 10:30 | 149.54 | 141.09
2019-12-23 11:00 | 146.51 | 129.89
2019-12-23 11:30 | 138.27 | 119.84
2019-12-23 12:00 | 154.24 | 136.72
2019-12-23 12:30 | 168.34 | 151.5
2019-12-23 13:00 | 188.29 | 172.6
2019-12-23 13:30 | 206.25 | 191.32
2019-12-23 14:00 | 216 | 203.96
2019-12-23 14:30 | 223.21 | 211.84
2019-12-23 15:00 | 214.19 | 201.86
2019-12-23 15:30 | 226.1 | 214.32
2019-12-23 16:00 | 227.67 | 216.3
2019-12-23 16:30 | 226.82 | 216.16
2019-12-23 17:00 | 227.02 | 216.5
2019-12-23 17:30 | 227.85 | 218.4
2019-12-23 18:00 | 246.26 | 238.08
2019-12-23 18:30 | 259.09 | 252.11
2019-12-23 19:00 | 251.51 | 243.59
2019-12-23 19:30 | 254.85 | 247.17
2019-12-23 20:00 | 255.83 | 248.52
2019-12-23 20:30 | 251.09 | 244.37
2019-12-23 21:00 | 238.54 | 236.46
2019-12-23 21:30 | 227.64 | 226.7
2019-12-23 22:00 | 214.58 | 213.65
2019-12-23 22:30 | 209.04 | 207.95
2019-12-23 23:00 | 209.42 | 208.65
2019-12-23 23:30 | 187.66 | 187.23
2019-12-24 | 156.8 | 156.53
2019-12-24 00:30 | 146.72 | 146.6
2019-12-24 01:00 | 122.54 | 122.54
2019-12-24 01:30 | 102.39 | 100.88
2019-12-24 02:00 | 109.77 | 108.18
2019-12-24 02:30 | 114.74 | 113.2
2019-12-24 03:00 | 107.72 | 105.94
2019-12-24 03:30 | 98.34 | 96.37
2019-12-24 04:00 | 99.55 | 97.56
2019-12-24 04:30 | 88.09 | 86.2
2019-12-24 05:00 | 108.3 | 106.83
2019-12-24 05:30 | 127.17 | 126.08
2019-12-24 06:00 | 124.52 | 123.63
2019-12-24 06:30 | 119.23 | 118.87
2019-12-24 07:00 | 119.66 | 119.63
2019-12-24 07:30 | 146.3 | 146.16
2019-12-24 08:00 | 165.98 | 163.35
2019-12-24 08:30 | 170.06 | 158.45
2019-12-24 09:00 | 185.28 | 164.71
2019-12-24 09:30 | 203.98 | 184
2019-12-24 10:00 | 208.98 | 194.41
2019-12-24 10:30 | 197.89 | 189.59
2019-12-24 11:00 | 203.69 | 195.48
2019-12-24 11:30 | 194.88 | 186.64
2019-12-24 12:00 | 171.57 | 162.85
2019-12-24 12:30 | 181.85 | 173.83
2019-12-24 13:00 | 170.25 | 161.65
2019-12-24 13:30 | 172.55 | 164.27
2019-12-24 14:00 | 189.7 | 181.55
2019-12-24 14:30 | 198.04 | 190.41
2019-12-24 15:00 | 190.48 | 182.55
2019-12-24 15:30 | 205.46 | 197.67
2019-12-24 16:00 | 227.92 | 220.14
2019-12-24 16:30 | 256.95 | 251.3
2019-12-24 17:00 | 252.88 | 252.05
2019-12-24 17:30 | 246.81 | 246.51
2019-12-24 18:00 | 238.91 | 238.57
2019-12-24 18:30 | 234.83 | 234.33
2019-12-24 19:00 | 235.66 | 235.1
2019-12-24 19:30 | 228.78 | 228.25
2019-12-24 20:00 | 223.15 | 222.88
2019-12-24 20:30 | 219.1 | 219.02
2019-12-24 21:00 | 211.05 | 210.88
2019-12-24 21:30 | 204.68 | 204.43
2019-12-24 22:00 | 195.96 | 195.48
2019-12-24 22:30 | 191.56 | 190.94
2019-12-24 23:00 | 188.84 | 188.03
2019-12-24 23:30 | 159.72 | 158.45
2019-12-25 | 130.83 | 129.21
2019-12-25 00:30 | 125.83 | 125.74
2019-12-25 01:00 | 107.45 | 107.35
2019-12-25 01:30 | 90.71 | 90.54
2019-12-25 02:00 | 92.64 | 92.44
2019-12-25 02:30 | 100.02 | 99.85
2019-12-25 03:00 | 107.56 | 107.52
2019-12-25 03:30 | 103.94 | 102.81
2019-12-25 04:00 | 96.86 | 95.59
2019-12-25 04:30 | 90.89 | 89.45
2019-12-25 05:00 | 83.6 | 81.87
2019-12-25 05:30 | 88.77 | 86.95
2019-12-25 06:00 | 87.33 | 85.5
2019-12-25 06:30 | 76.41 | 74.36
2019-12-25 07:00 | 72.29 | 71.06
2019-12-25 07:30 | 80.17 | 79.75
2019-12-25 08:00 | 85.7 | 85.21
2019-12-25 08:30 | 84.28 | 84.15
2019-12-25 09:00 | 82.08 | 82.02
2019-12-25 09:30 | 80.72 | 80.66
2019-12-25 10:00 | 84.36 | 84.32
2019-12-25 10:30 | 97.61 | 97.52
2019-12-25 11:00 | 88.92 | 88.74
2019-12-25 11:30 | 79.37 | 79.21
2019-12-25 12:00 | 91.35 | 91.25
2019-12-25 12:30 | 81.26 | 81.1
2019-12-25 13:00 | 48.43 | 48.2
2019-12-25 13:30 | 33.35 | 32.87
2019-12-25 14:00 | 29.61 | 29.25
2019-12-25 14:30 | 31.75 | 31.56
2019-12-25 15:00 | 8.25 | -8.21
2019-12-25 15:30 | 22.03 | 21.88
2019-12-25 16:00 | 78.33 | 78.06
2019-12-25 16:30 | 85.42 | 85.23
2019-12-25 17:00 | 105.26 | 105.07
2019-12-25 17:30 | 120.45 | 120.24
2019-12-25 18:00 | 152.17 | 151.98
2019-12-25 18:30 | 176 | 175.79
2019-12-25 19:00 | 180.96 | 180.84
2019-12-25 19:30 | 187.81 | 187.77
2019-12-25 20:00 | 191.39 | 191.36
2019-12-25 20:30 | 187.92 | 187.85
2019-12-25 21:00 | 182.59 | 182.46
2019-12-25 21:30 | 176.45 | 176.25
2019-12-25 22:00 | 160.37 | 159.99
2019-12-25 22:30 | 171.44 | 171.03
2019-12-25 23:00 | 169.75 | 169.23
2019-12-25 23:30 | 146.58 | 145.67
2019-12-26 | 118.21 | 116.34
2019-12-26 00:30 | 106.4 | 104.21
2019-12-26 01:00 | 98.65 | 95.92
2019-12-26 01:30 | 93.13 | 92.27
2019-12-26 02:00 | 85.3 | 85.27
2019-12-26 02:30 | 83.63 | 83.61
2019-12-26 03:00 | 89.01 | 88.99
2019-12-26 03:30 | 87.52 | 87.5
2019-12-26 04:00 | 77.21 | 77.19
2019-12-26 04:30 | 71.61 | 71.6
2019-12-26 05:00 | 65.72 | 65.71
2019-12-26 05:30 | 67.76 | 67.74
2019-12-26 06:00 | 65.72 | 65.72
2019-12-26 06:30 | 44.78 | 44.78
2019-12-26 07:00 | 40.68 | 40.68
2019-12-26 07:30 | 63.78 | 63.77
2019-12-26 08:00 | 63.66 | 63.66
2019-12-26 08:30 | 82.71 | 82.69
2019-12-26 09:00 | 83.02 | 83
2019-12-26 09:30 | 93.84 | 93.82
2019-12-26 10:00 | 91.23 | 91.23
2019-12-26 10:30 | 95.5 | 94.18
2019-12-26 11:00 | 78.28 | 76.62
2019-12-26 11:30 | 57.88 | 55.68
2019-12-26 12:00 | 55.04 | 52.84
2019-12-26 12:30 | 51.07 | 48.73
2019-12-26 13:00 | 35.78 | 32.9
2019-12-26 13:30 | 40.31 | 37.72
2019-12-26 14:00 | 52.17 | 50.2
2019-12-26 14:30 | 67.5 | 66
2019-12-26 15:00 | 69.22 | 67.95
2019-12-26 15:30 | 86.58 | 85.57
2019-12-26 16:00 | 115.08 | 114.34
2019-12-26 16:30 | 121.29 | 120.75
2019-12-26 17:00 | 151.04 | 150.83
2019-12-26 17:30 | 176.18 | 176.02
2019-12-26 18:00 | 202.28 | 202.18
2019-12-26 18:30 | 203.97 | 203.93
2019-12-26 19:00 | 206.55 | 206.53
2019-12-26 19:30 | 208.78 | 208.71
2019-12-26 20:00 | 207.39 | 207.35
2019-12-26 20:30 | 204.85 | 204.84
2019-12-26 21:00 | 190.8 | 190.8
2019-12-26 21:30 | 175.63 | 175.58
2019-12-26 22:00 | 158.14 | 157.9
2019-12-26 22:30 | 171 | 170.74
2019-12-26 23:00 | 178.26 | 177.93
2019-12-26 23:30 | 164.66 | 163.86
2019-12-27 | 130.42 | 128.7
2019-12-27 00:30 | 130.41 | 128.83
2019-12-27 01:00 | 121.37 | 119.26
2019-12-27 01:30 | 110.74 | 109.91
2019-12-27 02:00 | 102.08 | 100.5
2019-12-27 02:30 | 96.85 | 92.82
2019-12-27 03:00 | 96.12 | 92.01
2019-12-27 03:30 | 90.64 | 86.25
2019-12-27 04:00 | 88.13 | 83.53
2019-12-27 04:30 | 96.57 | 92.55
2019-12-27 05:00 | 94.7 | 90.87
2019-12-27 05:30 | 92.23 | 88.36
2019-12-27 06:00 | 87.1 | 83.14
2019-12-27 06:30 | 70.53 | 66.85
2019-12-27 07:00 | 59.52 | 56.38
2019-12-27 07:30 | 60.28 | 60.05
2019-12-27 08:00 | 73.7 | 73.04
2019-12-27 08:30 | 100.32 | 96.61
2019-12-27 09:00 | 106.82 | 100.81
2019-12-27 09:30 | 105.65 | 98.53
2019-12-27 10:00 | 132.69 | 126.29
2019-12-27 10:30 | 130.8 | 124.03
2019-12-27 11:00 | 128.87 | 122.28
2019-12-27 11:30 | 132.25 | 125.14
2019-12-27 12:00 | 113.87 | 105.39
2019-12-27 12:30 | 88.3 | 77.14
2019-12-27 13:00 | 89.37 | 77.8
2019-12-27 13:30 | 80.97 | 67.51
2019-12-27 14:00 | 88.67 | 76.07
2019-12-27 14:30 | 97.68 | 86.09
2019-12-27 15:00 | 105.02 | 86.99
2019-12-27 15:30 | 116.63 | 100.35
2019-12-27 16:00 | 128.33 | 120.43
2019-12-27 16:30 | 151.52 | 144.99
2019-12-27 17:00 | 163.86 | 157.84
2019-12-27 17:30 | 178.55 | 173.7
2019-12-27 18:00 | 184.7 | 180.41
2019-12-27 18:30 | 189.21 | 185.63
2019-12-27 19:00 | 200.96 | 197.6
2019-12-27 19:30 | 204.17 | 200.58
2019-12-27 20:00 | 198.21 | 195.39
2019-12-27 20:30 | 192.71 | 192.68
2019-12-27 21:00 | 179.91 | 179.91
2019-12-27 21:30 | 181.77 | 181.77
2019-12-27 22:00 | 177.55 | 177.53
2019-12-27 22:30 | 181.13 | 181.08
2019-12-27 23:00 | 177.51 | 177.37
2019-12-27 23:30 | 165.68 | 165.36
2019-12-28 | 131.99 | 131.54
2019-12-28 00:30 | 126.85 | 126.36
2019-12-28 01:00 | 126.33 | 125.73
2019-12-28 01:30 | 107.9 | 107.22
2019-12-28 02:00 | 104.52 | 103.78
2019-12-28 02:30 | 104.8 | 104.12
2019-12-28 03:00 | 91.95 | 91.48
2019-12-28 03:30 | 83.58 | 83.44
2019-12-28 04:00 | 80.1 | 79.97
2019-12-28 04:30 | 66.36 | 66.17
2019-12-28 05:00 | 70.64 | 70.35
2019-12-28 05:30 | 79.34 | 78.95
2019-12-28 06:00 | 83.95 | 83.71
2019-12-28 06:30 | 62.38 | 62.15
2019-12-28 07:00 | 44.13 | 43.69
2019-12-28 07:30 | 49.54 | 49.17
2019-12-28 08:00 | 58.33 | 58.01
2019-12-28 08:30 | 78.95 | 78.63
2019-12-28 09:00 | 66.7 | 66.21
2019-12-28 09:30 | 78.84 | 78.44
2019-12-28 10:00 | 46.5 | 45.75
2019-12-28 10:30 | 47.48 | 46.71
2019-12-28 11:00 | 36.98 | 36.09
2019-12-28 11:30 | 16.39 | 14.5
2019-12-28 12:00 | 30.17 | 29.09
2019-12-28 12:30 | 25.99 | 24.69
2019-12-28 13:00 | 35.45 | 35.27
2019-12-28 13:30 | 37.74 | 35.73
2019-12-28 14:00 | 47.65 | 46.18
2019-12-28 14:30 | 58.96 | 57.64
2019-12-28 15:00 | 59.66 | 58.36
2019-12-28 15:30 | 69.56 | 69.37
2019-12-28 16:00 | 76.84 | 76.68
2019-12-28 16:30 | 109.35 | 109.24
2019-12-28 17:00 | 124.96 | 124.86
2019-12-28 17:30 | 142.58 | 142.51
2019-12-28 18:00 | 143.02 | 142.95
2019-12-28 18:30 | 154.95 | 154.88
2019-12-28 19:00 | 173.63 | 173.58
2019-12-28 19:30 | 192.99 | 192.98
2019-12-28 20:00 | 191.38 | 191.34
2019-12-28 20:30 | 206.02 | 205.97
2019-12-28 21:00 | 197.37 | 197.3
2019-12-28 21:30 | 197.71 | 197.71
2019-12-28 22:00 | 187.46 | 187.42
2019-12-28 22:30 | 184.28 | 184.2
2019-12-28 23:00 | 179.47 | 179.32
2019-12-28 23:30 | 165.82 | 165.51
2019-12-29 | 153.57 | 152.98
2019-12-29 00:30 | 141.33 | 140.87
2019-12-29 01:00 | 136.57 | 136.03
2019-12-29 01:30 | 131.39 | 130.7
2019-12-29 02:00 | 127.35 | 126.27
2019-12-29 02:30 | 118.35 | 117.05
2019-12-29 03:00 | 106.11 | 106.11
2019-12-29 03:30 | 102.83 | 102.83
2019-12-29 04:00 | 109.95 | 109.95
2019-12-29 04:30 | 108.36 | 108.36
2019-12-29 05:00 | 95 | 94.97
2019-12-29 05:30 | 94.79 | 94.72
2019-12-29 06:00 | 90.41 | 90.34
2019-12-29 06:30 | 68.04 | 68.03
2019-12-29 07:00 | 51.79 | 51.78
2019-12-29 07:30 | 43.58 | 43.54
2019-12-29 08:00 | 32.3 | 31.99
2019-12-29 08:30 | 36.65 | 36.56
2019-12-29 09:00 | 33.47 | 31.81
2019-12-29 09:30 | 38.82 | 37.06
2019-12-29 10:00 | 45.76 | 44.27
2019-12-29 10:30 | 39.02 | 39.01
2019-12-29 11:00 | 25.4 | 23.59
2019-12-29 11:30 | 25.36 | 23.36
2019-12-29 12:00 | 20.13 | 18.15
2019-12-29 12:30 | 22.4 | 20.46
2019-12-29 13:00 | 35.43 | 34.41
2019-12-29 13:30 | 53.84 | 53.31
2019-12-29 14:00 | 70.49 | 70.15
2019-12-29 14:30 | 71.77 | 71.56
2019-12-29 15:00 | 63.57 | 63.35
2019-12-29 15:30 | 71.28 | 71.12
2019-12-29 16:00 | 99.12 | 99.03
2019-12-29 16:30 | 99.25 | 99.12
2019-12-29 17:00 | 126.2 | 125.99
2019-12-29 17:30 | 149.33 | 148.96
2019-12-29 18:00 | 154.42 | 153.95
2019-12-29 18:30 | 153.03 | 152.38
2019-12-29 19:00 | 182.93 | 182.37
2019-12-29 19:30 | 188.6 | 188.03
2019-12-29 20:00 | 194.13 | 193.55
2019-12-29 20:30 | 185.51 | 185.38
2019-12-29 21:00 | 159.46 | 159.12
2019-12-29 21:30 | 148.46 | 147.88
2019-12-29 22:00 | 131.21 | 130.51
2019-12-29 22:30 | 132.43 | 131.76
2019-12-29 23:00 | 147.25 | 146.67
2019-12-29 23:30 | 141.26 | 140.81
2019-12-30 | 112.79 | 111.75
2019-12-30 00:30 | 98.97 | 97.97
2019-12-30 01:00 | 85.88 | 84.76
2019-12-30 01:30 | 87.77 | 86.73
2019-12-30 02:00 | 89.23 | 88.22
2019-12-30 02:30 | 87.89 | 86.81
2019-12-30 03:00 | 89.9 | 87.14
2019-12-30 03:30 | 92.23 | 89.69
2019-12-30 04:00 | 94.86 | 92.49
2019-12-30 04:30 | 94.75 | 92.42
2019-12-30 05:00 | 95.86 | 93.9
2019-12-30 05:30 | 99.77 | 97.92
2019-12-30 06:00 | 105.38 | 103.55
2019-12-30 06:30 | 91.32 | 88.9
2019-12-30 07:00 | 71.26 | 69.18
2019-12-30 07:30 | 63.1 | 62.86
2019-12-30 08:00 | 55.32 | 55.31
2019-12-30 08:30 | 63.78 | 63.49
2019-12-30 09:00 | 67.98 | 67.47
2019-12-30 09:30 | 77.48 | 76.57
2019-12-30 10:00 | 71.62 | 71.48
2019-12-30 10:30 | 76.17 | 76.16
2019-12-30 11:00 | 71.64 | 71.64
2019-12-30 11:30 | 49.2 | 49.19
2019-12-30 12:00 | 49.5 | 49.5
2019-12-30 12:30 | 58.42 | 58.41
2019-12-30 13:00 | 49.26 | 49.24
2019-12-30 13:30 | 60.27 | 60.2
2019-12-30 14:00 | 80.15 | 80.07
2019-12-30 14:30 | 85.85 | 85.76
2019-12-30 15:00 | 80.04 | 79.95
2019-12-30 15:30 | 129.33 | 129.27
2019-12-30 16:00 | 160.69 | 160.59
2019-12-30 16:30 | 179.71 | 179.57
2019-12-30 17:00 | 186.25 | 186.05
2019-12-30 17:30 | 217.6 | 217.4
2019-12-30 18:00 | 215.29 | 215.21
2019-12-30 18:30 | 231.99 | 231.97
2019-12-30 19:00 | 238.38 | 238.35
2019-12-30 19:30 | 240.04 | 240.03
2019-12-30 20:00 | 237.64 | 237.64
2019-12-30 20:30 | 231.11 | 231.1
2019-12-30 21:00 | 224.31 | 223.99
2019-12-30 21:30 | 217.24 | 217.04
2019-12-30 22:00 | 205.54 | 205.46
2019-12-30 22:30 | 202.39 | 202.38
2019-12-30 23:00 | 196.11 | 196.11
2019-12-30 23:30 | 181.28 | 181.23
2019-12-31 | 163.97 | 163.8
2019-12-31 00:30 | 149.34 | 148.79
2019-12-31 01:00 | 142.54 | 141.73
2019-12-31 01:30 | 141.31 | 140.39
2019-12-31 02:00 | 139.02 | 138.05
2019-12-31 02:30 | 136.62 | 135.5
2019-12-31 03:00 | 133.68 | 132.45
2019-12-31 03:30 | 132.67 | 131.45
2019-12-31 04:00 | 120.87 | 119.48
2019-12-31 04:30 | 107.57 | 106.02
2019-12-31 05:00 | 105.92 | 104.25
2019-12-31 05:30 | 108.18 | 106.58
2019-12-31 06:00 | 117.57 | 116.31
2019-12-31 06:30 | 106.27 | 105.4
2019-12-31 07:00 | 87.93 | 87.28
2019-12-31 07:30 | 73.16 | 72.94
2019-12-31 08:00 | 71.68 | 71.68
2019-12-31 08:30 | 77.34 | 77.27
2019-12-31 09:00 | 82.58 | 82.39
2019-12-31 09:30 | 104.06 | 104.02
2019-12-31 10:00 | 123.1 | 123.1
2019-12-31 10:30 | 121.81 | 121.81
2019-12-31 11:00 | 117.17 | 117.16
2019-12-31 11:30 | 122.49 | 122.45
2019-12-31 12:00 | 121.41 | 121.4
2019-12-31 12:30 | 119.26 | 119.26
2019-12-31 13:00 | 135.98 | 135.98
2019-12-31 13:30 | 145.43 | 145.42
2019-12-31 14:00 | 150.96 | 150.96
2019-12-31 14:30 | 143.89 | 143.88
2019-12-31 15:00 | 128.78 | 128.75
2019-12-31 15:30 | 126.12 | 124.03
2019-12-31 16:00 | 138.69 | 134.28
2019-12-31 16:30 | 156.22 | 152.47
2019-12-31 17:00 | 179.75 | 176.23
2019-12-31 17:30 | 188.57 | 185.64
2019-12-31 18:00 | 215.31 | 212.42
2019-12-31 18:30 | 228.37 | 226.99
2019-12-31 19:00 | 225.56 | 225.2
2019-12-31 19:30 | 224.31 | 224.28
2019-12-31 20:00 | 219.34 | 219.24
2019-12-31 20:30 | 211.15 | 211.08
2019-12-31 21:00 | 205.13 | 205.02
2019-12-31 21:30 | 190.53 | 190.5
2019-12-31 22:00 | 185.64 | 185.64
2019-12-31 22:30 | 191.97 | 191.97
2019-12-31 23:00 | 196.19 | 196.18
2019-12-31 23:30 | 184.52 | 184.52
2020-01-01 | 161.9 | 161.88
2020-01-01 00:30 | 148.49 | 148.44
2020-01-01 01:00 | 143.75 | 143.63
2020-01-01 01:30 | 139.05 | 138.91
2020-01-01 02:00 | 134.32 | 133.96
2020-01-01 02:30 | 132.32 | 131.36
2020-01-01 03:00 | 130.45 | 129.24
2020-01-01 03:30 | 128.85 | 127.58
2020-01-01 04:00 | 126.77 | 125.43
2020-01-01 04:30 | 125.55 | 124.13
2020-01-01 05:00 | 114.82 | 113.8
2020-01-01 05:30 | 113.75 | 112.72
2020-01-01 06:00 | 112.39 | 111.35
2020-01-01 06:30 | 88.74 | 87.41
2020-01-01 07:00 | 63.38 | 61.52
2020-01-01 07:30 | 36.36 | 31.68
2020-01-01 08:00 | 36.82 | 31.88
2020-01-01 08:30 | 51.8 | 36.26
2020-01-01 09:00 | 65.03 | 52.53
2020-01-01 09:30 | 67.11 | 53.98
2020-01-01 10:00 | 79.19 | 68.44
2020-01-01 10:30 | 78.49 | 68.58
2020-01-01 11:00 | 93.2 | 86.23
2020-01-01 11:30 | 104.54 | 98.26
2020-01-01 12:00 | 114.15 | 108.75
2020-01-01 12:30 | 102.57 | 96.43
2020-01-01 13:00 | 116.27 | 110.95
2020-01-01 13:30 | 129.45 | 126.48
2020-01-01 14:00 | 153.04 | 152.25
2020-01-01 14:30 | 168.07 | 167.29
2020-01-01 15:00 | 184.43 | 183.58
2020-01-01 15:30 | 202.31 | 201.32
2020-01-01 16:00 | 218.53 | 217.54
2020-01-01 16:30 | 228.04 | 227.2
2020-01-01 17:00 | 238.51 | 237.46
2020-01-01 17:30 | 248.56 | 247.44
2020-01-01 18:00 | 251.93 | 251.03
2020-01-01 18:30 | 249.08 | 248.24
2020-01-01 19:00 | 249.53 | 246.52
2020-01-01 19:30 | 250.24 | 246.8
2020-01-01 20:00 | 246.21 | 242.98
2020-01-01 20:30 | 235.76 | 232.42
2020-01-01 21:00 | 222.23 | 221.32
2020-01-01 21:30 | 215.66 | 215.25
2020-01-01 22:00 | 205.04 | 204.88
2020-01-01 22:30 | 200.66 | 200.58
2020-01-01 23:00 | 196.37 | 196.34
2020-01-01 23:30 | 175.58 | 175.58
2020-01-02 | 161.95 | 161.87
2020-01-02 00:30 | 148.18 | 148.03
2020-01-02 01:00 | 143.05 | 142.9
2020-01-02 01:30 | 137.63 | 137.63
2020-01-02 02:00 | 134.14 | 134.12
2020-01-02 02:30 | 133.64 | 133.61
2020-01-02 03:00 | 129.48 | 129.45
2020-01-02 03:30 | 125.74 | 125.59
2020-01-02 04:00 | 125.4 | 125.28
2020-01-02 04:30 | 128.45 | 128.41
2020-01-02 05:00 | 129.8 | 129.75
2020-01-02 05:30 | 133.1 | 133.1
2020-01-02 06:00 | 134.35 | 134.35
2020-01-02 06:30 | 132.75 | 132.75
2020-01-02 07:00 | 120.25 | 120.21
2020-01-02 07:30 | 117.25 | 117.24
2020-01-02 08:00 | 122.2 | 121.98
2020-01-02 08:30 | 133.8 | 132.47
2020-01-02 09:00 | 143.07 | 135.73
2020-01-02 09:30 | 149.12 | 138.15
2020-01-02 10:00 | 145.39 | 134
2020-01-02 10:30 | 136.43 | 123.65
2020-01-02 11:00 | 132.31 | 118.56
2020-01-02 11:30 | 135.76 | 122.2
2020-01-02 12:00 | 149.29 | 136.32
2020-01-02 12:30 | 163.66 | 151.31
2020-01-02 13:00 | 173.49 | 162.25
2020-01-02 13:30 | 193.71 | 184.05
2020-01-02 14:00 | 214.76 | 205.94
2020-01-02 14:30 | 224.96 | 216.13
2020-01-02 15:00 | 212.83 | 203.25
2020-01-02 15:30 | 226.64 | 217.25
2020-01-02 16:00 | 241.92 | 232.75
2020-01-02 16:30 | 258.78 | 250.04
2020-01-02 17:00 | 253.64 | 248.82
2020-01-02 17:30 | 269.76 | 265.67
2020-01-02 18:00 | 277.34 | 273.67
2020-01-02 18:30 | 272.1 | 270.66
2020-01-02 19:00 | 270.88 | 270.23
2020-01-02 19:30 | 268.84 | 268.14
2020-01-02 20:00 | 265.67 | 265.17
2020-01-02 20:30 | 254.55 | 254.27
2020-01-02 21:00 | 241.08 | 240.83
2020-01-02 21:30 | 227.45 | 227.45
2020-01-02 22:00 | 215.04 | 214.99
2020-01-02 22:30 | 211.2 | 211.2
2020-01-02 23:00 | 205.59 | 205.58
2020-01-02 23:30 | 181.92 | 181.77
2020-01-03 | 146.69 | 146.31
2020-01-03 00:30 | 155.08 | 154.55
2020-01-03 01:00 | 150.6 | 149.83
2020-01-03 01:30 | 146.48 | 145.47
2020-01-03 02:00 | 143.18 | 142.04
2020-01-03 02:30 | 140.84 | 139.53
2020-01-03 03:00 | 139.15 | 137.79
2020-01-03 03:30 | 138.41 | 136.98
2020-01-03 04:00 | 137.96 | 136.51
2020-01-03 04:30 | 139.39 | 138.02
2020-01-03 05:00 | 139.27 | 137.85
2020-01-03 05:30 | 141.83 | 140.57
2020-01-03 06:00 | 143.9 | 142.96
2020-01-03 06:30 | 136.23 | 135.78
2020-01-03 07:00 | 125.49 | 125.39
2020-01-03 07:30 | 124.91 | 124.9
2020-01-03 08:00 | 140.22 | 139.99
2020-01-03 08:30 | 148.7 | 148.07
2020-01-03 09:00 | 156.32 | 155.31
2020-01-03 09:30 | 161.05 | 159.56
2020-01-03 10:00 | 162.21 | 160.37
2020-01-03 10:30 | 142.94 | 140.41
2020-01-03 11:00 | 137.79 | 135.43
2020-01-03 11:30 | 127.67 | 127.15
2020-01-03 12:00 | 127.56 | 126.87
2020-01-03 12:30 | 129.21 | 128.4
2020-01-03 13:00 | 137.8 | 136.99
2020-01-03 13:30 | 158.23 | 157.43
2020-01-03 14:00 | 157.91 | 157.07
2020-01-03 14:30 | 166.14 | 165.28
2020-01-03 15:00 | 167.61 | 166.72
2020-01-03 15:30 | 187.61 | 186.73
2020-01-03 16:00 | 197.98 | 197.2
2020-01-03 16:30 | 188.66 | 187.9
2020-01-03 17:00 | 203.36 | 200.77
2020-01-03 17:30 | 228.91 | 224.46
2020-01-03 18:00 | 231.71 | 228.12
2020-01-03 18:30 | 234.01 | 231.19
2020-01-03 19:00 | 244.52 | 242.03
2020-01-03 19:30 | 244.73 | 242.15
2020-01-03 20:00 | 241.15 | 238.92
2020-01-03 20:30 | 238.92 | 237.31
2020-01-03 21:00 | 223.66 | 223.65
2020-01-03 21:30 | 225.76 | 225.75
2020-01-03 22:00 | 202.85 | 202.79
2020-01-03 22:30 | 206.96 | 206.95
2020-01-03 23:00 | 202.26 | 202.24
2020-01-03 23:30 | 185.14 | 185.07
2020-01-04 | 147.88 | 147.61
2020-01-04 00:30 | 152.03 | 151.48
2020-01-04 01:00 | 143.16 | 142.32
2020-01-04 01:30 | 145.89 | 144.86
2020-01-04 02:00 | 138.6 | 137.39
2020-01-04 02:30 | 140.06 | 138.74
2020-01-04 03:00 | 137.43 | 136.01
2020-01-04 03:30 | 137.13 | 135.71
2020-01-04 04:00 | 135.18 | 133.59
2020-01-04 04:30 | 135.16 | 133.69
2020-01-04 05:00 | 128.3 | 126.56
2020-01-04 05:30 | 128.46 | 126.82
2020-01-04 06:00 | 125.9 | 124.43
2020-01-04 06:30 | 111.46 | 110.39
2020-01-04 07:00 | 95.94 | 95.33
2020-01-04 07:30 | 92.2 | 92.05
2020-01-04 08:00 | 88.78 | 88.78
2020-01-04 08:30 | 100.68 | 100.53
2020-01-04 09:00 | 121.28 | 120.99
2020-01-04 09:30 | 115.02 | 114.45
2020-01-04 10:00 | 103.61 | 98.58
2020-01-04 10:30 | 102.56 | 96.59
2020-01-04 11:00 | 99.63 | 93.01
2020-01-04 11:30 | 82.8 | 73.84
2020-01-04 12:00 | 76.56 | 65.38
2020-01-04 12:30 | 90.36 | 83.45
2020-01-04 13:00 | 91.97 | 89.01
2020-01-04 13:30 | 106.37 | 103.66
2020-01-04 14:00 | 119.28 | 116.72
2020-01-04 14:30 | 116.19 | 113.26
2020-01-04 15:00 | 112.06 | 108.67
2020-01-04 15:30 | 131.88 | 120.03
2020-01-04 16:00 | 67.04 | 21.89
2020-01-04 16:30 | 88.79 | -43.53
2020-01-04 17:00 | 89.68 | -30.43
2020-01-04 17:30 | 86.85 | -27.42
2020-01-04 18:00 | 81.12 | -14.81
2020-01-04 18:30 | 156.24 | 145.81
2020-01-04 19:00 | 173.36 | 164.5
2020-01-04 19:30 | 171.26 | 162.18
2020-01-04 20:00 | 116.6 | 103.46
2020-01-04 20:30 | 110.98 | 98.56
2020-01-04 21:00 | 155.69 | 152.72
2020-01-04 21:30 | 189.48 | 187.31
2020-01-04 22:00 | 191.06 | 189.4
2020-01-04 22:30 | 204.8 | 203.68
2020-01-04 23:00 | 194.04 | 193.21
2020-01-04 23:30 | 171.12 | 170.57
2020-01-05 | 140.54 | 140.29
2020-01-05 00:30 | 141.8 | 141.78
2020-01-05 01:00 | 121.82 | 120.67
2020-01-05 01:30 | 114.78 | 113.39
2020-01-05 02:00 | 105.52 | 103.94
2020-01-05 02:30 | 82.34 | 80.14
2020-01-05 03:00 | 71.48 | 68.83
2020-01-05 03:30 | 88.35 | 86.1
2020-01-05 04:00 | 86.81 | 84.45
2020-01-05 04:30 | 83.77 | 81.32
2020-01-05 05:00 | 80.47 | 77.56
2020-01-05 05:30 | 84.69 | 81.73
2020-01-05 06:00 | 86.28 | 83.48
2020-01-05 06:30 | 69.12 | 66.71
2020-01-05 07:00 | 47.89 | 45.6
2020-01-05 07:30 | 31.19 | 29.92
2020-01-05 08:00 | 35.31 | 34.99
2020-01-05 08:30 | 42.89 | 42.89
2020-01-05 09:00 | 25.86 | -15.9
2020-01-05 09:30 | 69.85 | -46.51
2020-01-05 10:00 | 75.14 | -43.34
2020-01-05 10:30 | 69.98 | 25.83
2020-01-05 11:00 | 88.59 | 60.94
2020-01-05 11:30 | 65.17 | 42.13
2020-01-05 12:00 | 71.66 | 51.14
2020-01-05 12:30 | 96.08 | 81.9
2020-01-05 13:00 | 105.6 | 91.83
2020-01-05 13:30 | 129.61 | 118.33
2020-01-05 14:00 | 157.4 | 147.95
2020-01-05 14:30 | 191.89 | 183.54
2020-01-05 15:00 | 184.68 | 180.17
2020-01-05 15:30 | 201.35 | 197.68
2020-01-05 16:00 | 232.46 | 229.22
2020-01-05 16:30 | 249.65 | 246.61
2020-01-05 17:00 | 254.72 | 252.02
2020-01-05 17:30 | 257.67 | 255.33
2020-01-05 18:00 | 256.93 | 254.76
2020-01-05 18:30 | 255.32 | 253.4
2020-01-05 19:00 | 254.12 | 252.36
2020-01-05 19:30 | 252.73 | 250.82
2020-01-05 20:00 | 247.75 | 246.15
2020-01-05 20:30 | 235.41 | 234.14
2020-01-05 21:00 | 220.76 | 219.93
2020-01-05 21:30 | 212.66 | 212.61
2020-01-05 22:00 | 206.13 | 205.91
2020-01-05 22:30 | 192.41 | 192.22
2020-01-05 23:00 | 192.59 | 192.37
2020-01-05 23:30 | 180.02 | 180.02
2020-01-06 | 165.75 | 165.12
2020-01-06 00:30 | 154.79 | 154.03
2020-01-06 01:00 | 142.17 | 141.02
2020-01-06 01:30 | 126.49 | 125.11
2020-01-06 02:00 | 116.54 | 114.99
2020-01-06 02:30 | 112.45 | 110.75
2020-01-06 03:00 | 110.78 | 109.04
2020-01-06 03:30 | 109.14 | 107.36
2020-01-06 04:00 | 113.28 | 111.55
2020-01-06 04:30 | 111 | 109.51
2020-01-06 05:00 | 117.86 | 116.47
2020-01-06 05:30 | 118.18 | 116.98
2020-01-06 06:00 | 132.4 | 131.71
2020-01-06 06:30 | 127.12 | 126.92
2020-01-06 07:00 | 129.08 | 129.08
2020-01-06 07:30 | 115.98 | 115.79
2020-01-06 08:00 | 111.85 | 111.85
2020-01-06 08:30 | 139.23 | 139.22
2020-01-06 09:00 | 143.03 | 142.94
2020-01-06 09:30 | 170.02 | 168.21
2020-01-06 10:00 | 162.66 | 157.82
2020-01-06 10:30 | 168.38 | 162.85
2020-01-06 11:00 | 159.86 | 153.41
2020-01-06 11:30 | 171.79 | 165.63
2020-01-06 12:00 | 165.75 | 159.27
2020-01-06 12:30 | 183.84 | 177.85
2020-01-06 13:00 | 197.51 | 192.52
2020-01-06 13:30 | 216.96 | 213.13
2020-01-06 14:00 | 236.56 | 232.75
2020-01-06 14:30 | 247.42 | 243.23
2020-01-06 15:00 | 241.4 | 237.11
2020-01-06 15:30 | 246.72 | 242.12
2020-01-06 16:00 | 259.87 | 255.59
2020-01-06 16:30 | 277.61 | 273.39
2020-01-06 17:00 | 284.93 | 280.94
2020-01-06 17:30 | 283.66 | 280.46
2020-01-06 18:00 | 280.44 | 277.85
2020-01-06 18:30 | 276.19 | 274.29
2020-01-06 19:00 | 277.77 | 275.94
2020-01-06 19:30 | 277.8 | 275.63
2020-01-06 20:00 | 272.1 | 270.37
2020-01-06 20:30 | 260.64 | 259.33
2020-01-06 21:00 | 247.85 | 247.16
2020-01-06 21:30 | 235.6 | 235.47
2020-01-06 22:00 | 202.04 | 202.02
2020-01-06 22:30 | 210.99 | 210.99
2020-01-06 23:00 | 207.23 | 207.01
2020-01-06 23:30 | 189.32 | 188.93
2020-01-07 | 155.96 | 155.18
2020-01-07 00:30 | 155.23 | 154.49
2020-01-07 01:00 | 139.44 | 138.71
2020-01-07 01:30 | 138.7 | 137.84
2020-01-07 02:00 | 135.09 | 134.07
2020-01-07 02:30 | 133.75 | 132.69
2020-01-07 03:00 | 130.97 | 129.85
2020-01-07 03:30 | 124.43 | 123.28
2020-01-07 04:00 | 114.72 | 113.52
2020-01-07 04:30 | 117.13 | 116.19
2020-01-07 05:00 | 123.22 | 122.36
2020-01-07 05:30 | 139.91 | 139.28
2020-01-07 06:00 | 142.93 | 142.54
2020-01-07 06:30 | 142.44 | 142.38
2020-01-07 07:00 | 152.07 | 152.05
2020-01-07 07:30 | 155.79 | 154.12
2020-01-07 08:00 | 168.44 | 165.08
2020-01-07 08:30 | 182.33 | 172.78
2020-01-07 09:00 | 185.99 | 172.64
2020-01-07 09:30 | 194.99 | 182.59
2020-01-07 10:00 | 203.26 | 192.8
2020-01-07 10:30 | 189.55 | 177.33
2020-01-07 11:00 | 198.71 | 186.49
2020-01-07 11:30 | 190.85 | 178.08
2020-01-07 12:00 | 186.82 | 173.6
2020-01-07 12:30 | 184.32 | 170.54
2020-01-07 13:00 | 195.42 | 181.64
2020-01-07 13:30 | 215.35 | 202.66
2020-01-07 14:00 | 247.69 | 235.75
2020-01-07 14:30 | 255.07 | 242.92
2020-01-07 15:00 | 226.28 | 213.19
2020-01-07 15:30 | 209.71 | 195.77
2020-01-07 16:00 | 222.76 | 209.53
2020-01-07 16:30 | 218.69 | 201.73
2020-01-07 17:00 | 242.92 | 223.38
2020-01-07 17:30 | 231.74 | 229.84
2020-01-07 18:00 | 239.8 | 238.69
2020-01-07 18:30 | 229.61 | 229.6
2020-01-07 19:00 | 241.94 | 241.93
2020-01-07 19:30 | 237.93 | 237.92
2020-01-07 20:00 | 224.86 | 224.64
2020-01-07 20:30 | 232.72 | 232.18
2020-01-07 21:00 | 229.7 | 228.8
2020-01-07 21:30 | 210.95 | 210.59
2020-01-07 22:00 | 185.52 | 185.44
2020-01-07 22:30 | 189.98 | 189.88
2020-01-07 23:00 | 190.8 | 190.7
2020-01-07 23:30 | 176.69 | 176.35
2020-01-08 | 137.66 | 136.98
2020-01-08 00:30 | 140.49 | 139.99
2020-01-08 01:00 | 122.58 | 121.73
2020-01-08 01:30 | 118.44 | 117.42
2020-01-08 02:00 | 109.99 | 108.81
2020-01-08 02:30 | 113.54 | 112.5
2020-01-08 03:00 | 113.15 | 112.01
2020-01-08 03:30 | 114.03 | 113.15
2020-01-08 04:00 | 113.47 | 112.66
2020-01-08 04:30 | 106.15 | 105.25
2020-01-08 05:00 | 107.35 | 106.51
2020-01-08 05:30 | 110.04 | 109.43
2020-01-08 06:00 | 118.7 | 118.28
2020-01-08 06:30 | 109.61 | 109.21
2020-01-08 07:00 | 114.54 | 114.33
2020-01-08 07:30 | 104.85 | 104.23
2020-01-08 08:00 | 117.08 | 116.24
2020-01-08 08:30 | 126.36 | 125.5
2020-01-08 09:00 | 139.43 | 137.66
2020-01-08 09:30 | 150.59 | 149.11
2020-01-08 10:00 | 157.22 | 156.45
2020-01-08 10:30 | 166.91 | 166.5
2020-01-08 11:00 | 162.22 | 161.8
2020-01-08 11:30 | 153.73 | 153.22
2020-01-08 12:00 | 160.65 | 160.09
2020-01-08 12:30 | 150.38 | 149.73
2020-01-08 13:00 | 148.74 | 148.08
2020-01-08 13:30 | 161.83 | 161.12
2020-01-08 14:00 | 173.06 | 167.26
2020-01-08 14:30 | 184.38 | 178.69
2020-01-08 15:00 | 184.57 | 178.53
2020-01-08 15:30 | 207.63 | 202.55
2020-01-08 16:00 | 221.19 | 217.76
2020-01-08 16:30 | 245.62 | 242.63
2020-01-08 17:00 | 274.35 | 271.63
2020-01-08 17:30 | 291.24 | 289.02
2020-01-08 18:00 | 288.75 | 287.09
2020-01-08 18:30 | 282.05 | 281.99
2020-01-08 19:00 | 281.75 | 281.7
2020-01-08 19:30 | 278.54 | 278.5
2020-01-08 20:00 | 271.81 | 271.76
2020-01-08 20:30 | 256.48 | 256.44
2020-01-08 21:00 | 247.53 | 247.52
2020-01-08 21:30 | 237.79 | 237.7
2020-01-08 22:00 | 218.1 | 217.95
2020-01-08 22:30 | 200.98 | 200.91
2020-01-08 23:00 | 185.09 | 185.08
2020-01-08 23:30 | 165.61 | 164.52
2020-01-09 | 131.65 | 129.82
2020-01-09 00:30 | 131.67 | 128.77
2020-01-09 01:00 | 129.39 | 126.85
2020-01-09 01:30 | 113.24 | 112.88
2020-01-09 02:00 | 112.44 | 112.32
2020-01-09 02:30 | 114.78 | 114.66
2020-01-09 03:00 | 112.31 | 112.2
2020-01-09 03:30 | 111.87 | 111.72
2020-01-09 04:00 | 111.92 | 111.78
2020-01-09 04:30 | 93.76 | 93.52
2020-01-09 05:00 | 89.15 | 88.91
2020-01-09 05:30 | 95.51 | 95.25
2020-01-09 06:00 | 111.08 | 110.82
2020-01-09 06:30 | 119.24 | 119.15
2020-01-09 07:00 | 127.49 | 127.18
2020-01-09 07:30 | 125.19 | 124.89
2020-01-09 08:00 | 123.06 | 122.1
2020-01-09 08:30 | 136.81 | 135.88
2020-01-09 09:00 | 140.6 | 139.88
2020-01-09 09:30 | 142 | 141.52
2020-01-09 10:00 | 138.84 | 138.8
2020-01-09 10:30 | 141.15 | 140.98
2020-01-09 11:00 | 138.03 | 137.76
2020-01-09 11:30 | 142.41 | 141.96
2020-01-09 12:00 | 138.82 | 138.3
2020-01-09 12:30 | 156.34 | 155.85
2020-01-09 13:00 | 174.71 | 174.22
2020-01-09 13:30 | 194.55 | 193.99
2020-01-09 14:00 | 207.29 | 207.07
2020-01-09 14:30 | 216.87 | 216.86
2020-01-09 15:00 | 206.51 | 206.48
2020-01-09 15:30 | 221.11 | 221.06
2020-01-09 16:00 | 248.78 | 248.68
2020-01-09 16:30 | 270.23 | 270.2
2020-01-09 17:00 | 284.62 | 284.61
2020-01-09 17:30 | 284.91 | 284.91
2020-01-09 18:00 | 284.41 | 284.41
2020-01-09 18:30 | 284.36 | 284.35
2020-01-09 19:00 | 286.51 | 286.5
2020-01-09 19:30 | 285.43 | 285.43
2020-01-09 20:00 | 279.06 | 279.06
2020-01-09 20:30 | 270.06 | 270.02
2020-01-09 21:00 | 260.15 | 259.82
2020-01-09 21:30 | 247.71 | 247.47
2020-01-09 22:00 | 220.25 | 219.57
2020-01-09 22:30 | 211.81 | 211.25
2020-01-09 23:00 | 206.98 | 206.44
2020-01-09 23:30 | 165.99 | 165.99
2020-01-10 | 136.27 | 135.62
2020-01-10 00:30 | 141.06 | 140.75
2020-01-10 01:00 | 137.75 | 137.57
2020-01-10 01:30 | 129.26 | 129.15
2020-01-10 02:00 | 123.57 | 123.5
2020-01-10 02:30 | 118.41 | 118.29
2020-01-10 03:00 | 115.54 | 114.24
2020-01-10 03:30 | 106.95 | 105.4
2020-01-10 04:00 | 113.63 | 112.18
2020-01-10 04:30 | 120.6 | 119.5
2020-01-10 05:00 | 128.93 | 128.09
2020-01-10 05:30 | 132.86 | 132.14
2020-01-10 06:00 | 130.62 | 130.17
2020-01-10 06:30 | 140.25 | 140.21
2020-01-10 07:00 | 146.5 | 146.42
2020-01-10 07:30 | 151.27 | 148.21
2020-01-10 08:00 | 167.13 | 154.67
2020-01-10 08:30 | 188.52 | 176.93
2020-01-10 09:00 | 189.27 | 184.8
2020-01-10 09:30 | 194.51 | 189.5
2020-01-10 10:00 | 180.79 | 175.04
2020-01-10 10:30 | 168.08 | 161.3
2020-01-10 11:00 | 154.13 | 146.54
2020-01-10 11:30 | 153.59 | 147.71
2020-01-10 12:00 | 157.33 | 154.15
2020-01-10 12:30 | 168.35 | 165.58
2020-01-10 13:00 | 166.34 | 163.37
2020-01-10 13:30 | 165.4 | 161.95
2020-01-10 14:00 | 174.41 | 170.95
2020-01-10 14:30 | 182.9 | 179.4
2020-01-10 15:00 | 182.32 | 178.26
2020-01-10 15:30 | 194.99 | 190.85
2020-01-10 16:00 | 208.6 | 204.62
2020-01-10 16:30 | 225.4 | 222.02
2020-01-10 17:00 | 260.33 | 257.35
2020-01-10 17:30 | 255.42 | 252.99
2020-01-10 18:00 | 245.77 | 243.69
2020-01-10 18:30 | 252.13 | 250.68
2020-01-10 19:00 | 258.52 | 257.21
2020-01-10 19:30 | 259.21 | 257.83
2020-01-10 20:00 | 247.06 | 246
2020-01-10 20:30 | 245.65 | 245.05
2020-01-10 21:00 | 246.3 | 246.22
2020-01-10 21:30 | 229.65 | 229.56
2020-01-10 22:00 | 211.52 | 210.69
2020-01-10 22:30 | 215.24 | 214.49
2020-01-10 23:00 | 204.23 | 203.73
2020-01-10 23:30 | 169.99 | 169.83
2020-01-11 | 148.47 | 148.45
2020-01-11 00:30 | 169.27 | 169.24
2020-01-11 01:00 | 172.21 | 172.13
2020-01-11 01:30 | 162.36 | 162.19
2020-01-11 02:00 | 136.61 | 136.36
2020-01-11 02:30 | 133.76 | 133.4
2020-01-11 03:00 | 132.32 | 131.88
2020-01-11 03:30 | 131.37 | 130.88
2020-01-11 04:00 | 130.26 | 129.75
2020-01-11 04:30 | 128.18 | 127.71
2020-01-11 05:00 | 126.6 | 126.08
2020-01-11 05:30 | 125.93 | 125.33
2020-01-11 06:00 | 126.14 | 125.7
2020-01-11 06:30 | 128.84 | 128.67
2020-01-11 07:00 | 102.46 | 102.46
2020-01-11 07:30 | 86.18 | 86
2020-01-11 08:00 | 89.02 | 88.19
2020-01-11 08:30 | 105.1 | 98.47
2020-01-11 09:00 | 131.88 | 125.46
2020-01-11 09:30 | 174.73 | 163.74
2020-01-11 10:00 | 181.3 | 169.66
2020-01-11 10:30 | 181.5 | 163.95
2020-01-11 11:00 | 190.5 | 178.47
2020-01-11 11:30 | 181.17 | 168.65
2020-01-11 12:00 | 209.65 | 197.71
2020-01-11 12:30 | 271.69 | 261.91
2020-01-11 13:00 | 280.35 | 272.62
2020-01-11 13:30 | 276.02 | 269.05
2020-01-11 14:00 | 265.4 | 258.53
2020-01-11 14:30 | 267.79 | 261.51
2020-01-11 15:00 | 269.8 | 264.42
2020-01-11 15:30 | 265.98 | 263.44
2020-01-11 16:00 | 265.44 | 262.76
2020-01-11 16:30 | 257.41 | 254.95
2020-01-11 17:00 | 259.4 | 256.65
2020-01-11 17:30 | 258.64 | 256.16
2020-01-11 18:00 | 258.59 | 256.23
2020-01-11 18:30 | 255.74 | 253.4
2020-01-11 19:00 | 250.83 | 248.63
2020-01-11 19:30 | 239.63 | 238.07
2020-01-11 20:00 | 230.95 | 229.48
2020-01-11 20:30 | 226.78 | 226.63
2020-01-11 21:00 | 225.98 | 225.96
2020-01-11 21:30 | 221.7 | 221.69
2020-01-11 22:00 | 217.88 | 217.87
2020-01-11 22:30 | 212.15 | 212.15
2020-01-11 23:00 | 213.47 | 212.35
2020-01-11 23:30 | 186.03 | 185.17
2020-01-12 | 156.08 | 155.49
2020-01-12 00:30 | 160.68 | 160.38
2020-01-12 01:00 | 144.56 | 144.34
2020-01-12 01:30 | 127.75 | 127.39
2020-01-12 02:00 | 127.16 | 126.19
2020-01-12 02:30 | 123.79 | 122.69
2020-01-12 03:00 | 121.14 | 119.97
2020-01-12 03:30 | 121.67 | 120.4
2020-01-12 04:00 | 120.53 | 119.25
2020-01-12 04:30 | 118.26 | 117.1
2020-01-12 05:00 | 116.81 | 115.56
2020-01-12 05:30 | 117.48 | 116.18
2020-01-12 06:00 | 108.17 | 106.78
2020-01-12 06:30 | 93.8 | 92.62
2020-01-12 07:00 | 90.48 | 89.68
2020-01-12 07:30 | 108.29 | 108
2020-01-12 08:00 | 111.48 | 111.38
2020-01-12 08:30 | 107.14 | 107.13
2020-01-12 09:00 | 113.67 | 113.66
2020-01-12 09:30 | 123.31 | 123.27
2020-01-12 10:00 | 123.86 | 123.78
2020-01-12 10:30 | 101.73 | 101.58
2020-01-12 11:00 | 70.07 | 69.85
2020-01-12 11:30 | 110.09 | 109.74
2020-01-12 12:00 | 132.28 | 132.08
2020-01-12 12:30 | 143.44 | 143.31
2020-01-12 13:00 | 149.9 | 149.75
2020-01-12 13:30 | 179.98 | 179.87
2020-01-12 14:00 | 181.71 | 181.62
2020-01-12 14:30 | 177.49 | 177.44
2020-01-12 15:00 | 154.78 | 154.77
2020-01-12 15:30 | 162.58 | 162.57
2020-01-12 16:00 | 173 | 172.99
2020-01-12 16:30 | 157.92 | 157.9
2020-01-12 17:00 | 170.05 | 170.03
2020-01-12 17:30 | 195.74 | 195.74
2020-01-12 18:00 | 189.55 | 189.55
2020-01-12 18:30 | 194.01 | 194.01
2020-01-12 19:00 | 214.93 | 214.92
2020-01-12 19:30 | 215.41 | 215.41
2020-01-12 20:00 | 203.23 | 203.23
2020-01-12 20:30 | 188.6 | 188.55
2020-01-12 21:00 | 167.89 | 167.75
2020-01-12 21:30 | 150.62 | 150.4
2020-01-12 22:00 | 135.3 | 134.87
2020-01-12 22:30 | 148.36 | 147.84
2020-01-12 23:00 | 154.97 | 154.34
2020-01-12 23:30 | 137.36 | 136.41
2020-01-13 | 104.86 | 103.2
2020-01-13 00:30 | 102.84 | 101.48
2020-01-13 01:00 | 93.01 | 91.43
2020-01-13 01:30 | 88.13 | 86.28
2020-01-13 02:00 | 10.45 | 7.83
2020-01-13 02:30 | 89.96 | 88.2
2020-01-13 03:00 | 83.6 | 81.58
2020-01-13 03:30 | 87.09 | 85.46
2020-01-13 04:00 | 83.72 | 82.13
2020-01-13 04:30 | 84.17 | 82.84
2020-01-13 05:00 | 83.33 | 82.15
2020-01-13 05:30 | 90.36 | 89.38
2020-01-13 06:00 | 101.03 | 100.31
2020-01-13 06:30 | 114.28 | 113.76
2020-01-13 07:00 | 116.29 | 115.9
2020-01-13 07:30 | 112.88 | 112.87
2020-01-13 08:00 | 120.74 | 120.61
2020-01-13 08:30 | 137.21 | 137.16
2020-01-13 09:00 | 136.52 | 136.52
2020-01-13 09:30 | 149.5 | 149.44
2020-01-13 10:00 | 148.54 | 148.41
2020-01-13 10:30 | 134.86 | 134.86
2020-01-13 11:00 | 122.53 | 122.53
2020-01-13 11:30 | 120.52 | 120.52
2020-01-13 12:00 | 108.79 | 108.79
2020-01-13 12:30 | 95.87 | 95.81
2020-01-13 13:00 | 99.66 | 99.58
2020-01-13 13:30 | 144.47 | 144.46
2020-01-13 14:00 | 145.61 | 145.59
2020-01-13 14:30 | 150.54 | 150.54
2020-01-13 15:00 | 130.2 | 130.19
2020-01-13 15:30 | 127.66 | 127.65
2020-01-13 16:00 | 153.32 | 153.32
2020-01-13 16:30 | 183.86 | 183.85
2020-01-13 17:00 | 210.52 | 210.52
2020-01-13 17:30 | 209.91 | 209.91
2020-01-13 18:00 | 223.76 | 223.76
2020-01-13 18:30 | 226.4 | 226.4
2020-01-13 19:00 | 227.23 | 227.23
2020-01-13 19:30 | 225.98 | 225.98
2020-01-13 20:00 | 223.84 | 223.84
2020-01-13 20:30 | 218.33 | 218.3
2020-01-13 21:00 | 206.85 | 206.58
2020-01-13 21:30 | 192.93 | 192.55
2020-01-13 22:00 | 177.82 | 177.47
2020-01-13 22:30 | 183.99 | 183.7
2020-01-13 23:00 | 171.64 | 171.2
2020-01-13 23:30 | 145.6 | 144.8
2020-01-14 | 104.3 | 102.63
2020-01-14 00:30 | 101.06 | 99.05
2020-01-14 01:00 | 90.42 | 87.95
2020-01-14 01:30 | 82.15 | 79.46
2020-01-14 02:00 | 70.89 | 67.86
2020-01-14 02:30 | 69.12 | 65.99
2020-01-14 03:00 | 78.45 | 75.76
2020-01-14 03:30 | 78.9 | 76.22
2020-01-14 04:00 | 70.64 | 66.92
2020-01-14 04:30 | 70.69 | 67.5
2020-01-14 05:00 | 71.27 | 68.53
2020-01-14 05:30 | 88.67 | 86.69
2020-01-14 06:00 | 99.06 | 97.51
2020-01-14 06:30 | 115.63 | 115.13
2020-01-14 07:00 | 111.14 | 111.01
2020-01-14 07:30 | 112.32 | 112.31
2020-01-14 08:00 | 122.51 | 118.25
2020-01-14 08:30 | 142.55 | 128.63
2020-01-14 09:00 | 146.04 | 131.47
2020-01-14 09:30 | 157.18 | 143.33
2020-01-14 10:00 | 154.04 | 140.01
2020-01-14 10:30 | 153.1 | 138.62
2020-01-14 11:00 | 143.4 | 130.14
2020-01-14 11:30 | 102.37 | 95.48
2020-01-14 12:00 | 96.89 | 89.6
2020-01-14 12:30 | 127.46 | 121.41
2020-01-14 13:00 | 141.83 | 135.89
2020-01-14 13:30 | 142 | 135.7
2020-01-14 14:00 | 153.08 | 146.51
2020-01-14 14:30 | 168.04 | 161.49
2020-01-14 15:00 | 154.35 | 146.29
2020-01-14 15:30 | 179.65 | 172.06
2020-01-14 16:00 | 180.7 | 173.25
2020-01-14 16:30 | 197.71 | 187.04
2020-01-14 17:00 | 221.95 | 215.74
2020-01-14 17:30 | 228.85 | 226.64
2020-01-14 18:00 | 235.71 | 234.76
2020-01-14 18:30 | 240.87 | 240.85
2020-01-14 19:00 | 250.89 | 250.88
2020-01-14 19:30 | 253.82 | 253.8
2020-01-14 20:00 | 248.41 | 248.2
2020-01-14 20:30 | 236.26 | 235.79
2020-01-14 21:00 | 220.48 | 220.45
2020-01-14 21:30 | 192.38 | 192.2
2020-01-14 22:00 | 185.89 | 185.52
2020-01-14 22:30 | 180.51 | 180.35
2020-01-14 23:00 | 159.91 | 159.68
2020-01-14 23:30 | 140.65 | 140.19
2020-01-15 | 112.94 | 112
2020-01-15 00:30 | 100.18 | 98.88
2020-01-15 01:00 | 90.13 | 88.38
2020-01-15 01:30 | 81.16 | 78.95
2020-01-15 02:00 | 74.47 | 72.07
2020-01-15 02:30 | 73.33 | 71.01
2020-01-15 03:00 | 73.48 | 71.12
2020-01-15 03:30 | 84.78 | 82.64
2020-01-15 04:00 | 80.59 | 78.24
2020-01-15 04:30 | 74.54 | 72.19
2020-01-15 05:00 | 81.44 | 79.68
2020-01-15 05:30 | 94.31 | 93.09
2020-01-15 06:00 | 111.08 | 110.34
2020-01-15 06:30 | 116.72 | 116.41
2020-01-15 07:00 | 120.85 | 120.81
2020-01-15 07:30 | 102.72 | 101.41
2020-01-15 08:00 | 97.27 | 93.38
2020-01-15 08:30 | 134.17 | 116.1
2020-01-15 09:00 | 157.21 | 142.26
2020-01-15 09:30 | 164.28 | 148.42
2020-01-15 10:00 | 167.07 | 149.8
2020-01-15 10:30 | 157.57 | 138.51
2020-01-15 11:00 | 147.25 | 126.2
2020-01-15 11:30 | 146.01 | 123.32
2020-01-15 12:00 | 145.1 | 121.86
2020-01-15 12:30 | 165.58 | 145.42
2020-01-15 13:00 | 174.42 | 155.3
2020-01-15 13:30 | 193.32 | 167.32
2020-01-15 14:00 | 203.94 | 178.66
2020-01-15 14:30 | 225.98 | 197.4
2020-01-15 15:00 | 238.89 | 207.68
2020-01-15 15:30 | 244.61 | 237.65
2020-01-15 16:00 | 257.14 | 251.43
2020-01-15 16:30 | 270.84 | 265.53
2020-01-15 17:00 | 274.04 | 269.33
2020-01-15 17:30 | 262.34 | 258.08
2020-01-15 18:00 | 274.42 | 272.78
2020-01-15 18:30 | 268.11 | 267.46
2020-01-15 19:00 | 274.92 | 274.28
2020-01-15 19:30 | 275.06 | 274.25
2020-01-15 20:00 | 270.17 | 269.52
2020-01-15 20:30 | 260.03 | 259.83
2020-01-15 21:00 | 241.92 | 241.92
2020-01-15 21:30 | 228 | 227.48
2020-01-15 22:00 | 198.6 | 197.15
2020-01-15 22:30 | 202.87 | 201.14
2020-01-15 23:00 | 186.6 | 186.59
2020-01-15 23:30 | 164.05 | 164.02
2020-01-16 | 131.06 | 131.05
2020-01-16 00:30 | 130.01 | 129.98
2020-01-16 01:00 | 115.88 | 115.87
2020-01-16 01:30 | 102.96 | 102.96
2020-01-16 02:00 | 103.21 | 103.19
2020-01-16 02:30 | 103.87 | 103.87
2020-01-16 03:00 | 108.84 | 108.84
2020-01-16 03:30 | 104.97 | 104.97
2020-01-16 04:00 | 101.26 | 101.24
2020-01-16 04:30 | 106.21 | 106.11
2020-01-16 05:00 | 105.64 | 105.53
2020-01-16 05:30 | 95.87 | 95.73
2020-01-16 06:00 | 104.31 | 104.14
2020-01-16 06:30 | 108.14 | 107.89
2020-01-16 07:00 | 119.46 | 118.88
2020-01-16 07:30 | 129.74 | 129.57
2020-01-16 08:00 | 141.33 | 139.05
2020-01-16 08:30 | 151.42 | 142.72
2020-01-16 09:00 | 158.04 | 148.44
2020-01-16 09:30 | 166.11 | 155.65
2020-01-16 10:00 | 174.13 | 163.37
2020-01-16 10:30 | 190.46 | 179.7
2020-01-16 11:00 | 216.29 | 200.44
2020-01-16 11:30 | 213.91 | 197.97
2020-01-16 12:00 | 212.63 | 197.1
2020-01-16 12:30 | 213.32 | 197.76
2020-01-16 13:00 | 223.02 | 208.41
2020-01-16 13:30 | 243.24 | 228.63
2020-01-16 14:00 | 261.29 | 247.45
2020-01-16 14:30 | 258.49 | 244.53
2020-01-16 15:00 | 243.58 | 229.55
2020-01-16 15:30 | 234.66 | 220.64
2020-01-16 16:00 | 230.74 | 217.5
2020-01-16 16:30 | 215.46 | 201.75
2020-01-16 17:00 | 219.72 | 206.86
2020-01-16 17:30 | 225.83 | 214.02
2020-01-16 18:00 | 237.47 | 226.65
2020-01-16 18:30 | 242.06 | 231.67
2020-01-16 19:00 | 251.52 | 241.12
2020-01-16 19:30 | 253.12 | 243.25
2020-01-16 20:00 | 251.11 | 246.32
2020-01-16 20:30 | 249.3 | 246.53
2020-01-16 21:00 | 224.5 | 223.41
2020-01-16 21:30 | 201.31 | 201.15
2020-01-16 22:00 | 193.27 | 192.99
2020-01-16 22:30 | 194.57 | 194.27
2020-01-16 23:00 | 192.39 | 192.11
2020-01-16 23:30 | 164.5 | 164.32
2020-01-17 | 133.82 | 133.52
2020-01-17 00:30 | 138.9 | 138.61
2020-01-17 01:00 | 125.3 | 124.86
2020-01-17 01:30 | 111.87 | 111.37
2020-01-17 02:00 | 101.57 | 100.75
2020-01-17 02:30 | 104.75 | 104.08
2020-01-17 03:00 | 105.66 | 104.97
2020-01-17 03:30 | 102.75 | 102.18
2020-01-17 04:00 | 100.24 | 99.72
2020-01-17 04:30 | 102.63 | 102.24
2020-01-17 05:00 | 111.56 | 111.3
2020-01-17 05:30 | 112.55 | 112.38
2020-01-17 06:00 | 118.54 | 118.38
2020-01-17 06:30 | 130.13 | 129.76
2020-01-17 07:00 | 136.66 | 136.49
2020-01-17 07:30 | 143.66 | 141.62
2020-01-17 08:00 | 139.65 | 139.64
2020-01-17 08:30 | 145.94 | 145.74
2020-01-17 09:00 | 158.19 | 156.51
2020-01-17 09:30 | 168.48 | 166.45
2020-01-17 10:00 | 186.29 | 180.76
2020-01-17 10:30 | 203.84 | 194.69
2020-01-17 11:00 | 210.38 | 201.66
2020-01-17 11:30 | 208.83 | 200.47
2020-01-17 12:00 | 192.44 | 190.06
2020-01-17 12:30 | 182.08 | 180.43
2020-01-17 13:00 | 183.77 | 181.8
2020-01-17 13:30 | 194.96 | 192.93
2020-01-17 14:00 | 212.83 | 210.79
2020-01-17 14:30 | 221.83 | 219.87
2020-01-17 15:00 | 221.47 | 219.68
2020-01-17 15:30 | 248.64 | 247.78
2020-01-17 16:00 | 258.31 | 256.3
2020-01-17 16:30 | 252.72 | 250.71
2020-01-17 17:00 | 261.76 | 259.84
2020-01-17 17:30 | 262.11 | 260.45
2020-01-17 18:00 | 260.31 | 259.11
2020-01-17 18:30 | 257.53 | 257.36
2020-01-17 19:00 | 259.08 | 259
2020-01-17 19:30 | 256.39 | 256.31
2020-01-17 20:00 | 253.58 | 253.4
2020-01-17 20:30 | 248.07 | 247.88
2020-01-17 21:00 | 229.26 | 229.1
2020-01-17 21:30 | 210.7 | 210.65
2020-01-17 22:00 | 184.94 | 184.94
2020-01-17 22:30 | 182.13 | 181.97
2020-01-17 23:00 | 183.58 | 183.58
2020-01-17 23:30 | 163.19 | 163.07
2020-01-18 | 135.86 | 135.67
2020-01-18 00:30 | 126.63 | 126.55
2020-01-18 01:00 | 121.62 | 120.9
2020-01-18 01:30 | 130.54 | 129.77
2020-01-18 02:00 | 111.94 | 110.99
2020-01-18 02:30 | 112.34 | 111.34
2020-01-18 03:00 | 106.43 | 105.41
2020-01-18 03:30 | 93.95 | 92.8
2020-01-18 04:00 | 80.75 | 79.61
2020-01-18 04:30 | 85.54 | 84.53
2020-01-18 05:00 | 78.08 | 76.8
2020-01-18 05:30 | 77.5 | 76.55
2020-01-18 06:00 | 80.39 | 79.62
2020-01-18 06:30 | 68.75 | 68.16
2020-01-18 07:00 | 60.84 | 60.63
2020-01-18 07:30 | 69.21 | 67.75
2020-01-18 08:00 | 50.58 | 13.35
2020-01-18 08:30 | 57.98 | 23.25
2020-01-18 09:00 | 59.31 | 14.15
2020-01-18 09:30 | 52.07 | 27.48
2020-01-18 10:00 | 57.94 | 42.87
2020-01-18 10:30 | 62.82 | 49.99
2020-01-18 11:00 | 43.1 | -10.68
2020-01-18 11:30 | 40.14 | 11.8
2020-01-18 12:00 | 83.32 | 74.87
2020-01-18 12:30 | 90.66 | 83.56
2020-01-18 13:00 | 94.54 | 87.39
2020-01-18 13:30 | 100.11 | 93.19
2020-01-18 14:00 | 109.2 | 102.31
2020-01-18 14:30 | 120.52 | 114.22
2020-01-18 15:00 | 100.86 | 93.7
2020-01-18 15:30 | 107.53 | 103.91
2020-01-18 16:00 | 146.79 | 144.33
2020-01-18 16:30 | 185.05 | 182.8
2020-01-18 17:00 | 188.08 | 185.86
2020-01-18 17:30 | 165.96 | 156.8
2020-01-18 18:00 | 145.93 | 141.58
2020-01-18 18:30 | 178.55 | 175.08
2020-01-18 19:00 | 236.68 | 233.6
2020-01-18 19:30 | 239.81 | 236.49
2020-01-18 20:00 | 235.85 | 232.63
2020-01-18 20:30 | 231.1 | 228.19
2020-01-18 21:00 | 217.23 | 214.65
2020-01-18 21:30 | 197.36 | 195.49
2020-01-18 22:00 | 177.13 | 177.11
2020-01-18 22:30 | 188.48 | 188.44
2020-01-18 23:00 | 181.44 | 181.36
2020-01-18 23:30 | 161.37 | 161.17
2020-01-19 | 133.85 | 133.39
2020-01-19 00:30 | 127.14 | 126.44
2020-01-19 01:00 | 116.98 | 116.01
2020-01-19 01:30 | 95.64 | 94.26
2020-01-19 02:00 | 83.18 | 81.51
2020-01-19 02:30 | 81.97 | 80.26
2020-01-19 03:00 | 78.35 | 76.43
2020-01-19 03:30 | 81.76 | 79.94
2020-01-19 04:00 | 78.58 | 76.6
2020-01-19 04:30 | 74.41 | 72.3
2020-01-19 05:00 | 67.68 | 65.5
2020-01-19 05:30 | 58.55 | 56.37
2020-01-19 06:00 | 59.24 | 58.11
2020-01-19 06:30 | 38.65 | 36.64
2020-01-19 07:00 | 12.56 | 7.91
2020-01-19 07:30 | 58.82 | -57.88
2020-01-19 08:00 | 55.16 | -54
2020-01-19 08:30 | 36.83 | -27.87
2020-01-19 09:00 | 51.96 | 42.21
2020-01-19 09:30 | 78.73 | 71.23
2020-01-19 10:00 | 102.21 | 86.58
2020-01-19 10:30 | 102.94 | 75.4
2020-01-19 11:00 | 78.71 | -13.48
2020-01-19 11:30 | 105.91 | 76.3
2020-01-19 12:00 | 114.35 | 88.33
2020-01-19 12:30 | 117.73 | 92.65
2020-01-19 13:00 | 125.97 | 102.05
2020-01-19 13:30 | 134.9 | 112.83
2020-01-19 14:00 | 154.2 | 134.29
2020-01-19 14:30 | 179.6 | 161.75
2020-01-19 15:00 | 172.99 | 160.37
2020-01-19 15:30 | 147.24 | 135.74
2020-01-19 16:00 | 188.43 | 183.64
2020-01-19 16:30 | 210.84 | 207.31
2020-01-19 17:00 | 205.6 | 202.12
2020-01-19 17:30 | 215.66 | 212.67
2020-01-19 18:00 | 226.13 | 223.51
2020-01-19 18:30 | 236.43 | 234.25
2020-01-19 19:00 | 269.63 | 267.53
2020-01-19 19:30 | 272.16 | 270.01
2020-01-19 20:00 | 268.73 | 266.96
2020-01-19 20:30 | 260.45 | 259.53
2020-01-19 21:00 | 246.3 | 246.29
2020-01-19 21:30 | 225.66 | 225.56
2020-01-19 22:00 | 196.36 | 196.19
2020-01-19 22:30 | 192.72 | 192.49
2020-01-19 23:00 | 172.9 | 172.48
2020-01-19 23:30 | 149.72 | 149.22
2020-01-20 | 130.1 | 129.43
2020-01-20 00:30 | 126.52 | 125.93
2020-01-20 01:00 | 115.03 | 114.44
2020-01-20 01:30 | 116.31 | 115.55
2020-01-20 02:00 | 113.08 | 112.35
2020-01-20 02:30 | 118.73 | 117.93
2020-01-20 03:00 | 111.97 | 110.95
2020-01-20 03:30 | 113.21 | 112.25
2020-01-20 04:00 | 112.64 | 111.73
2020-01-20 04:30 | 105.99 | 105.36
2020-01-20 05:00 | 107.6 | 107.08
2020-01-20 05:30 | 113.76 | 113.44
2020-01-20 06:00 | 121.27 | 121.11
2020-01-20 06:30 | 131.94 | 131.89
2020-01-20 07:00 | 130.02 | 129.98
2020-01-20 07:30 | 161.2 | 161.19
2020-01-20 08:00 | 160.16 | 156.49
2020-01-20 08:30 | 168.64 | 158.7
2020-01-20 09:00 | 193.86 | 183.32
2020-01-20 09:30 | 204.66 | 193.23
2020-01-20 10:00 | 212.07 | 200.42
2020-01-20 10:30 | 220.36 | 209.95
2020-01-20 11:00 | 232.2 | 222.39
2020-01-20 11:30 | 241.49 | 231.53
2020-01-20 12:00 | 237.18 | 226.4
2020-01-20 12:30 | 237.49 | 226.26
2020-01-20 13:00 | 261.94 | 251.12
2020-01-20 13:30 | 236.4 | 228.31
2020-01-20 14:00 | 284.66 | 279.24
2020-01-20 14:30 | 288.45 | 281.63
2020-01-20 15:00 | 329.6 | 321.43
2020-01-20 15:30 | 348.63 | 342.37
2020-01-20 16:00 | 304.44 | 302.58
2020-01-20 16:30 | 293.53 | 292.44
2020-01-20 17:00 | 294.86 | 294.38
2020-01-20 17:30 | 294.7 | 294.48
2020-01-20 18:00 | 275.01 | 275
2020-01-20 18:30 | 278.21 | 278.18
2020-01-20 19:00 | 287.71 | 287.61
2020-01-20 19:30 | 283.22 | 283.12
2020-01-20 20:00 | 269.16 | 268.91
2020-01-20 20:30 | 265.28 | 265.04
2020-01-20 21:00 | 245.23 | 245.15
2020-01-20 21:30 | 228.2 | 227.98
2020-01-20 22:00 | 220.69 | 220.39
2020-01-20 22:30 | 204.16 | 203.93
2020-01-20 23:00 | 187.3 | 187.25
2020-01-20 23:30 | 154.86 | 154.8
2020-01-21 | 123.6 | 123
2020-01-21 00:30 | 154.21 | 153.67
2020-01-21 01:00 | 162.6 | 161.77
2020-01-21 01:30 | 149.92 | 149.05
2020-01-21 02:00 | 142.08 | 141.19
2020-01-21 02:30 | 140.38 | 139.52
2020-01-21 03:00 | 150.63 | 149.91
2020-01-21 03:30 | 155.23 | 154.61
2020-01-21 04:00 | 150.85 | 150.24
2020-01-21 04:30 | 147.8 | 147.16
2020-01-21 05:00 | 136.58 | 135.92
2020-01-21 05:30 | 140.61 | 140.07
2020-01-21 06:00 | 154.99 | 154.45
2020-01-21 06:30 | 160.67 | 160.53
2020-01-21 07:00 | 182.44 | 181.94
2020-01-21 07:30 | 190.97 | 190.73
2020-01-21 08:00 | 203.98 | 203.94
2020-01-21 08:30 | 207.09 | 207.09
2020-01-21 09:00 | 207.56 | 207.53
2020-01-21 09:30 | 205.47 | 205.38
2020-01-21 10:00 | 204.57 | 204.34
2020-01-21 10:30 | 225.08 | 221.07
2020-01-21 11:00 | 239.15 | 235.27
2020-01-21 11:30 | 246.68 | 242.31
2020-01-21 12:00 | 242.18 | 236.69
2020-01-21 12:30 | 234.51 | 229.04
2020-01-21 13:00 | 242.96 | 236.65
2020-01-21 13:30 | 250.73 | 244.01
2020-01-21 14:00 | 283.93 | 277.67
2020-01-21 14:30 | 281.13 | 273.12
2020-01-21 15:00 | 293.21 | 284.35
2020-01-21 15:30 | 317.94 | 308.98
2020-01-21 16:00 | 349.48 | 340.38
2020-01-21 16:30 | 358.89 | 351
2020-01-21 17:00 | 353.38 | 347.18
2020-01-21 17:30 | 328.16 | 324.98
2020-01-21 18:00 | 314.07 | 312.04
2020-01-21 18:30 | 302.51 | 301.56
2020-01-21 19:00 | 298.71 | 297.9
2020-01-21 19:30 | 289.83 | 289.08
2020-01-21 20:00 | 288.52 | 287.91
2020-01-21 20:30 | 277.84 | 277.4
2020-01-21 21:00 | 263.29 | 263.12
2020-01-21 21:30 | 250.84 | 250.78
2020-01-21 22:00 | 224.11 | 224.1
2020-01-21 22:30 | 206.28 | 206.09
2020-01-21 23:00 | 199.82 | 199.66
2020-01-21 23:30 | 181.5 | 181.39
2020-01-22 | 144.06 | 144.01
2020-01-22 00:30 | 144.91 | 144.89
2020-01-22 01:00 | 138.41 | 138.31
2020-01-22 01:30 | 131.01 | 130.87
2020-01-22 02:00 | 140.67 | 140.52
2020-01-22 02:30 | 149.07 | 148.91
2020-01-22 03:00 | 141.87 | 141.72
2020-01-22 03:30 | 149.26 | 149.11
2020-01-22 04:00 | 150.09 | 149.93
2020-01-22 04:30 | 126.68 | 126.48
2020-01-22 05:00 | 140.2 | 140.08
2020-01-22 05:30 | 150.59 | 150.57
2020-01-22 06:00 | 153.87 | 153.86
2020-01-22 06:30 | 76.41 | 76.07
2020-01-22 07:00 | 82.3 | 80.78
2020-01-22 07:30 | 136.86 | 135.91
2020-01-22 08:00 | 163.03 | 162.94
2020-01-22 08:30 | 202.73 | 202.57
2020-01-22 09:00 | 214.61 | 214.22
2020-01-22 09:30 | 221.2 | 220.64
2020-01-22 10:00 | 220.54 | 220.08
2020-01-22 10:30 | 225.74 | 225.44
2020-01-22 11:00 | 226.28 | 225.88
2020-01-22 11:30 | 225.2 | 220.67
2020-01-22 12:00 | 241.98 | 236.93
2020-01-22 12:30 | 268.18 | 263.17
2020-01-22 13:00 | 275.17 | 269.87
2020-01-22 13:30 | 284.51 | 278.58
2020-01-22 14:00 | 302.12 | 296.04
2020-01-22 14:30 | 289.21 | 282.72
2020-01-22 15:00 | 282.01 | 274.76
2020-01-22 15:30 | 295.18 | 287.18
2020-01-22 16:00 | 309.2 | 300.38
2020-01-22 16:30 | 313.27 | 304.06
2020-01-22 17:00 | 307.51 | 298.99
2020-01-22 17:30 | 321.46 | 314.82
2020-01-22 18:00 | 309.73 | 304.77
2020-01-22 18:30 | 290.2 | 288.04
2020-01-22 19:00 | 308.32 | 306
2020-01-22 19:30 | 311.58 | 309.49
2020-01-22 20:00 | 309.5 | 307.94
2020-01-22 20:30 | 298.97 | 297.65
2020-01-22 21:00 | 274.57 | 274.21
2020-01-22 21:30 | 268.96 | 268.92
2020-01-22 22:00 | 266.11 | 266.1
2020-01-22 22:30 | 250.69 | 250.69
2020-01-22 23:00 | 244.5 | 243.9
2020-01-22 23:30 | 214.47 | 214.08
2020-01-23 | 191.42 | 191.41
2020-01-23 00:30 | 191.68 | 191.68
2020-01-23 01:00 | 186.21 | 186.19
2020-01-23 01:30 | 174.6 | 174.55
2020-01-23 02:00 | 173.73 | 173.67
2020-01-23 02:30 | 161.37 | 161.29
2020-01-23 03:00 | 152.31 | 152.2
2020-01-23 03:30 | 145.74 | 145.61
2020-01-23 04:00 | 138.84 | 138.7
2020-01-23 04:30 | 143.46 | 143.35
2020-01-23 05:00 | 168.35 | 168.3
2020-01-23 05:30 | 181.45 | 181.44
2020-01-23 06:00 | 189.05 | 189.05
2020-01-23 06:30 | 197.57 | 197.54
2020-01-23 07:00 | 209.11 | 209.11
2020-01-23 07:30 | 230.44 | 230.43
2020-01-23 08:00 | 251.94 | 251.9
2020-01-23 08:30 | 267.31 | 264.95
2020-01-23 09:00 | 265.61 | 260.96
2020-01-23 09:30 | 274.32 | 268.94
2020-01-23 10:00 | 279.92 | 274.3
2020-01-23 10:30 | 276.34 | 270.21
2020-01-23 11:00 | 254.66 | 248.22
2020-01-23 11:30 | 235.73 | 228.14
2020-01-23 12:00 | 245.05 | 237.66
2020-01-23 12:30 | 223.83 | 216.36
2020-01-23 13:00 | 212.68 | 205.06
2020-01-23 13:30 | 197.8 | 188.88
2020-01-23 14:00 | 152.85 | 134.56
2020-01-23 14:30 | 178.07 | 163.63
2020-01-23 15:00 | 208.24 | 197.13
2020-01-23 15:30 | 247.4 | 237.79
2020-01-23 16:00 | 233.29 | 222.9
2020-01-23 16:30 | 236.8 | 226.8
2020-01-23 17:00 | 228.54 | 218.8
2020-01-23 17:30 | 235.67 | 226.43
2020-01-23 18:00 | 270.94 | 264.94
2020-01-23 18:30 | 281.34 | 278.88
2020-01-23 19:00 | 254.36 | 251.54
2020-01-23 19:30 | 290.34 | 287.88
2020-01-23 20:00 | 277.01 | 275.08
2020-01-23 20:30 | 268.43 | 268
2020-01-23 21:00 | 265.16 | 265.16
2020-01-23 21:30 | 270.16 | 270.14
2020-01-23 22:00 | 253.7 | 253.69
2020-01-23 22:30 | 247.67 | 246.68
2020-01-23 23:00 | 239.19 | 239.04
2020-01-23 23:30 | 197.31 | 197.25
2020-01-24 | 156.02 | 155.58
2020-01-24 00:30 | 162.56 | 162.39
2020-01-24 01:00 | 166.32 | 166.01
2020-01-24 01:30 | 152.96 | 152.66
2020-01-24 02:00 | 141.21 | 140.96
2020-01-24 02:30 | 127.98 | 127.74
2020-01-24 03:00 | 110.23 | 109.98
2020-01-24 03:30 | 105.18 | 104.87
2020-01-24 04:00 | 107.16 | 106.82
2020-01-24 04:30 | 97.92 | 97.42
2020-01-24 05:00 | 113.1 | 112.6
2020-01-24 05:30 | 124.59 | 123.97
2020-01-24 06:00 | 131.44 | 131.41
2020-01-24 06:30 | 126.07 | 126.02
2020-01-24 07:00 | 129.25 | 129.16
2020-01-24 07:30 | 149.46 | 149.29
2020-01-24 08:00 | 165.36 | 165.36
2020-01-24 08:30 | 197.86 | 192.62
2020-01-24 09:00 | 234.83 | 226.96
2020-01-24 09:30 | 267.98 | 260.38
2020-01-24 10:00 | 290.58 | 282.56
2020-01-24 10:30 | 294.53 | 286.01
2020-01-24 11:00 | 290.33 | 282.37
2020-01-24 11:30 | 295.29 | 286.88
2020-01-24 12:00 | 288.67 | 279.18
2020-01-24 12:30 | 293.55 | 284.81
2020-01-24 13:00 | 291.1 | 283.16
2020-01-24 13:30 | 297.49 | 289.59
2020-01-24 14:00 | 288.02 | 278.73
2020-01-24 14:30 | 294.16 | 284.05
2020-01-24 15:00 | 303.42 | 293.54
2020-01-24 15:30 | 314.07 | 303.06
2020-01-24 16:00 | 337.47 | 323.68
2020-01-24 16:30 | 345.18 | 331.92
2020-01-24 17:00 | 348.21 | 335
2020-01-24 17:30 | 341.84 | 330.84
2020-01-24 18:00 | 338.8 | 332.41
2020-01-24 18:30 | 319.25 | 316.76
2020-01-24 19:00 | 306.55 | 304.72
2020-01-24 19:30 | 293.19 | 291.24
2020-01-24 20:00 | 291.03 | 289.35
2020-01-24 20:30 | 275.33 | 274.27
2020-01-24 21:00 | 275.27 | 275.27
2020-01-24 21:30 | 273.88 | 273.88
2020-01-24 22:00 | 250.14 | 250.13
2020-01-24 22:30 | 252.51 | 251.56
2020-01-24 23:00 | 241.5 | 240.47
2020-01-24 23:30 | 210.9 | 209.83
2020-01-25 | 168.24 | 167.01
2020-01-25 00:30 | 172.89 | 172.46
2020-01-25 01:00 | 171.58 | 171.24
2020-01-25 01:30 | 156.15 | 155.76
2020-01-25 02:00 | 140.72 | 140.29
2020-01-25 02:30 | 134.93 | 134.49
2020-01-25 03:00 | 132.47 | 132.46
2020-01-25 03:30 | 129.6 | 129.06
2020-01-25 04:00 | 126.37 | 125.6
2020-01-25 04:30 | 119.81 | 118.98
2020-01-25 05:00 | 121.44 | 120.8
2020-01-25 05:30 | 115.66 | 114.33
2020-01-25 06:00 | 128.72 | 127.44
2020-01-25 06:30 | 120.74 | 119.22
2020-01-25 07:00 | 125.7 | 125.69
2020-01-25 07:30 | 147.58 | 147.51
2020-01-25 08:00 | 160.54 | 160.46
2020-01-25 08:30 | 190.13 | 189.46
2020-01-25 09:00 | 206.35 | 202.75
2020-01-25 09:30 | 235.75 | 231.44
2020-01-25 10:00 | 242.57 | 237.94
2020-01-25 10:30 | 228.55 | 223.66
2020-01-25 11:00 | 215.76 | 210.33
2020-01-25 11:30 | 234.33 | 228.11
2020-01-25 12:00 | 229.03 | 223
2020-01-25 12:30 | 213.17 | 207.19
2020-01-25 13:00 | 212.88 | 207.73
2020-01-25 13:30 | 220.24 | 215.4
2020-01-25 14:00 | 225.64 | 221.11
2020-01-25 14:30 | 217.67 | 212.91
2020-01-25 15:00 | 245.02 | 240.74
2020-01-25 15:30 | 228 | 223.85
2020-01-25 16:00 | 230.43 | 226.62
2020-01-25 16:30 | 234.18 | 230.55
2020-01-25 17:00 | 225.07 | 221.28
2020-01-25 17:30 | 209.52 | 205.82
2020-01-25 18:00 | 212.11 | 208.88
2020-01-25 18:30 | 210.22 | 207.21
2020-01-25 19:00 | 227.14 | 224.05
2020-01-25 19:30 | 233.21 | 229.96
2020-01-25 20:00 | 230.56 | 227.49
2020-01-25 20:30 | 220.4 | 217.73
2020-01-25 21:00 | 193.05 | 188.01
2020-01-25 21:30 | 182.55 | 176.83
2020-01-25 22:00 | 169.13 | 163.86
2020-01-25 22:30 | 179.55 | 175.11
2020-01-25 23:00 | 193.54 | 190.03
2020-01-25 23:30 | 174.77 | 174.7
2020-01-26 | 141.89 | 141.89
2020-01-26 00:30 | 142.34 | 142.28
2020-01-26 01:00 | 129.68 | 129.5
2020-01-26 01:30 | 115.16 | 114.86
2020-01-26 02:00 | 100.93 | 100.47
2020-01-26 02:30 | 95.71 | 95.19
2020-01-26 03:00 | 99.28 | 98.67
2020-01-26 03:30 | 96.59 | 95.96
2020-01-26 04:00 | 113.37 | 112.78
2020-01-26 04:30 | 108.35 | 107.8
2020-01-26 05:00 | 92.14 | 91.42
2020-01-26 05:30 | 84.69 | 83.83
2020-01-26 06:00 | 90.14 | 89.46
2020-01-26 06:30 | 78.53 | 78.01
2020-01-26 07:00 | 78.49 | 78.23
2020-01-26 07:30 | 58.98 | 58.94
2020-01-26 08:00 | 60.85 | 60.84
2020-01-26 08:30 | 66.1 | 65.52
2020-01-26 09:00 | 88.23 | 87.25
2020-01-26 09:30 | 115.71 | 113.18
2020-01-26 10:00 | 128.49 | 106.98
2020-01-26 10:30 | 120.83 | 95.29
2020-01-26 11:00 | 118.85 | 91.87
2020-01-26 11:30 | 119.63 | 92.36
2020-01-26 12:00 | 119.39 | 92.2
2020-01-26 12:30 | 128.24 | 103.01
2020-01-26 13:00 | 126.41 | 100.37
2020-01-26 13:30 | 141.42 | 118.62
2020-01-26 14:00 | 154.76 | 133.82
2020-01-26 14:30 | 151.87 | 135.71
2020-01-26 15:00 | 132.82 | 118.23
2020-01-26 15:30 | 151.41 | 138.67
2020-01-26 16:00 | 175.99 | 164.96
2020-01-26 16:30 | 169.27 | 158.02
2020-01-26 17:00 | 160.42 | 148.65
2020-01-26 17:30 | 171.61 | 161.39
2020-01-26 18:00 | 179.52 | 170.36
2020-01-26 18:30 | 191.62 | 183.57
2020-01-26 19:00 | 199.12 | 191.29
2020-01-26 19:30 | 203.55 | 195.51
2020-01-26 20:00 | 193.81 | 185.83
2020-01-26 20:30 | 198.83 | 190.18
2020-01-26 21:00 | 200.94 | 189.95
2020-01-26 21:30 | 201.21 | 190.94
2020-01-26 22:00 | 188.74 | 178.82
2020-01-26 22:30 | 199.51 | 192.09
2020-01-26 23:00 | 181.92 | 180.45
2020-01-26 23:30 | 155.48 | 154.23
2020-01-27 | 135.43 | 134.5
2020-01-27 00:30 | 120.55 | 119.8
2020-01-27 01:00 | 106.12 | 105.48
2020-01-27 01:30 | 92.39 | 91.76
2020-01-27 02:00 | 82.84 | 82.25
2020-01-27 02:30 | 79.12 | 78.52
2020-01-27 03:00 | 77.26 | 76.71
2020-01-27 03:30 | 73.74 | 73.22
2020-01-27 04:00 | 72.21 | 71.67
2020-01-27 04:30 | 74.21 | 73.66
2020-01-27 05:00 | 72.3 | 71.73
2020-01-27 05:30 | 70.56 | 70
2020-01-27 06:00 | 63.26 | 62.68
2020-01-27 06:30 | 48.96 | 47.4
2020-01-27 07:00 | 61.84 | 59.57
2020-01-27 07:30 | 75.82 | 72.74
2020-01-27 08:00 | 84.81 | 75.71
2020-01-27 08:30 | 96.29 | 74.24
2020-01-27 09:00 | 100.62 | 78.19
2020-01-27 09:30 | 108.28 | 85.55
2020-01-27 10:00 | 105.11 | 80.38
2020-01-27 10:30 | 88.9 | 66.6
2020-01-27 11:00 | 63.41 | 23.89
2020-01-27 11:30 | 76.86 | 50.26
2020-01-27 12:00 | 94.12 | 73.77
2020-01-27 12:30 | 102.12 | 84.07
2020-01-27 13:00 | 115.67 | 100.18
2020-01-27 13:30 | 126.96 | 112.19
2020-01-27 14:00 | 145.91 | 132.94
2020-01-27 14:30 | 152.97 | 140.3
2020-01-27 15:00 | 156.02 | 142.45
2020-01-27 15:30 | 172.33 | 160.84
2020-01-27 16:00 | 173.35 | 166.03
2020-01-27 16:30 | 194.57 | 187.74
2020-01-27 17:00 | 209.08 | 202.38
2020-01-27 17:30 | 228.77 | 222.83
2020-01-27 18:00 | 218.66 | 213.22
2020-01-27 18:30 | 226.48 | 222.11
2020-01-27 19:00 | 236.74 | 232.63
2020-01-27 19:30 | 227.36 | 222.98
2020-01-27 20:00 | 222.64 | 218.5
2020-01-27 20:30 | 228.75 | 227.31
2020-01-27 21:00 | 199.74 | 199.72
2020-01-27 21:30 | 168.13 | 167.54
2020-01-27 22:00 | 135.38 | 135.12
2020-01-27 22:30 | 135.84 | 135.84
2020-01-27 23:00 | 127.71 | 127.7
2020-01-27 23:30 | 112.37 | 112.36
2020-01-28 | 82.59 | 82.49
2020-01-28 00:30 | 80.7 | 80.41
2020-01-28 01:00 | 71.05 | 70.53
2020-01-28 01:30 | 63.94 | 63.31
2020-01-28 02:00 | 64.04 | 63.27
2020-01-28 02:30 | 61.9 | 61.1
2020-01-28 03:00 | 59.84 | 59.12
2020-01-28 03:30 | 59.26 | 58.56
2020-01-28 04:00 | 45.64 | 44.84
2020-01-28 04:30 | 49.6 | 48.93
2020-01-28 05:00 | 55.42 | 54.87
2020-01-28 05:30 | 73.08 | 72.72
2020-01-28 06:00 | 85.44 | 85.3
2020-01-28 06:30 | 93.4 | 93.35
2020-01-28 07:00 | 104.66 | 102.47
2020-01-28 07:30 | 137.85 | 137.66
2020-01-28 08:00 | 151.03 | 150.7
2020-01-28 08:30 | 136.34 | 135.49
2020-01-28 09:00 | 129.19 | 128.03
2020-01-28 09:30 | 156.32 | 154.44
2020-01-28 10:00 | 152.1 | 147.82
2020-01-28 10:30 | 146.29 | 140.91
2020-01-28 11:00 | 132.73 | 126.44
2020-01-28 11:30 | 119.06 | 112.41
2020-01-28 12:00 | 105.36 | 97.28
2020-01-28 12:30 | 80.85 | 68.27
2020-01-28 13:00 | 107.87 | 98.99
2020-01-28 13:30 | 75.99 | 57.3
2020-01-28 14:00 | 82.27 | 20.37
2020-01-28 14:30 | 123.78 | 91.44
2020-01-28 15:00 | 94.59 | 41.48
2020-01-28 15:30 | 128.16 | 95.76
2020-01-28 16:00 | 106.57 | 60.53
2020-01-28 16:30 | 47.01 | -7.84
2020-01-28 17:00 | 101.69 | 95.89
2020-01-28 17:30 | 174.7 | 174.17
2020-01-28 18:00 | 90.38 | 86.38
2020-01-28 18:30 | 76.13 | 66.97
2020-01-28 19:00 | 212.08 | 211.15
2020-01-28 19:30 | 238.25 | 236.61
2020-01-28 20:00 | 222.9 | 221.49
2020-01-28 20:30 | 227.63 | 227.53
2020-01-28 21:00 | 223.8 | 223.19
2020-01-28 21:30 | 204.58 | 204.53
2020-01-28 22:00 | 173.92 | 173.78
2020-01-28 22:30 | 165.01 | 164.86
2020-01-28 23:00 | 152.09 | 151.95
2020-01-28 23:30 | 104.15 | 104.09
2020-01-29 | 64.09 | 63.88
2020-01-29 00:30 | 79.48 | 79.14
2020-01-29 01:00 | 84.31 | 83.76
2020-01-29 01:30 | 88.85 | 88.16
2020-01-29 02:00 | 92.51 | 91.66
2020-01-29 02:30 | 84.35 | 83.35
2020-01-29 03:00 | 79.16 | 78
2020-01-29 03:30 | 76.36 | 75.3
2020-01-29 04:00 | 78.26 | 77.25
2020-01-29 04:30 | 80.38 | 79.6
2020-01-29 05:00 | 98.63 | 98.08
2020-01-29 05:30 | 107.11 | 106.74
2020-01-29 06:00 | 93.36 | 93.2
2020-01-29 06:30 | 111.18 | 111.16
2020-01-29 07:00 | 135.64 | 132.09
2020-01-29 07:30 | 187.42 | 181.19
2020-01-29 08:00 | 183.69 | 179.8
2020-01-29 08:30 | 184.41 | 179.48
2020-01-29 09:00 | 179.92 | 173.6
2020-01-29 09:30 | 208.19 | 201.41
2020-01-29 10:00 | 213.26 | 199.32
2020-01-29 10:30 | 216.21 | 201.78
2020-01-29 11:00 | 215.17 | 200
2020-01-29 11:30 | 209.09 | 197.31
2020-01-29 12:00 | 195.94 | 184.26
2020-01-29 12:30 | 206.21 | 194.17
2020-01-29 13:00 | 196.61 | 183.51
2020-01-29 13:30 | 208.15 | 194.92
2020-01-29 14:00 | 236.84 | 224.96
2020-01-29 14:30 | 247.71 | 235.99
2020-01-29 15:00 | 248.29 | 236.33
2020-01-29 15:30 | 263.37 | 251.67
2020-01-29 16:00 | 304.48 | 290.69
2020-01-29 16:30 | 311.44 | 297.13
2020-01-29 17:00 | 332.07 | 318.28
2020-01-29 17:30 | 343.77 | 331.39
2020-01-29 18:00 | 348.61 | 337.39
2020-01-29 18:30 | 337.16 | 327.44
2020-01-29 19:00 | 332.45 | 323.23
2020-01-29 19:30 | 325.98 | 317.31
2020-01-29 20:00 | 325.68 | 321.26
2020-01-29 20:30 | 312.01 | 310
2020-01-29 21:00 | 293.08 | 292.46
2020-01-29 21:30 | 275.54 | 275.53
2020-01-29 22:00 | 232.85 | 232.84
2020-01-29 22:30 | 219.48 | 219.45
2020-01-29 23:00 | 214.24 | 214.19
2020-01-29 23:30 | 177.95 | 177.91
2020-01-30 | 148.67 | 148.65
2020-01-30 00:30 | 147.51 | 147.44
2020-01-30 01:00 | 150.8 | 150.64
2020-01-30 01:30 | 143.43 | 143.27
2020-01-30 02:00 | 143.04 | 142.83
2020-01-30 02:30 | 139.98 | 139.69
2020-01-30 03:00 | 132.21 | 131.84
2020-01-30 03:30 | 125.22 | 124.78
2020-01-30 04:00 | 122.42 | 121.92
2020-01-30 04:30 | 125.9 | 125.51
2020-01-30 05:00 | 138.22 | 137.93
2020-01-30 05:30 | 137.79 | 137.6
2020-01-30 06:00 | 125.08 | 124.96
2020-01-30 06:30 | 134.45 | 134.17
2020-01-30 07:00 | 162.39 | 156.98
2020-01-30 07:30 | 210.93 | 198.66
2020-01-30 08:00 | 215.93 | 201.46
2020-01-30 08:30 | 180.95 | 168.73
2020-01-30 09:00 | 157.31 | 144.72
2020-01-30 09:30 | 193.21 | 182.24
2020-01-30 10:00 | 196.85 | 184.82
2020-01-30 10:30 | 186.39 | 172.59
2020-01-30 11:00 | 179.72 | 167.49
2020-01-30 11:30 | 178.64 | 166.69
2020-01-30 12:00 | 166.4 | 152.8
2020-01-30 12:30 | 150.07 | 134.99
2020-01-30 13:00 | 142.03 | 125.68
2020-01-30 13:30 | 125.04 | 104.28
2020-01-30 14:00 | 83.2 | -12.25
2020-01-30 14:30 | 67.69 | -30.52
2020-01-30 15:00 | 34.8 | -12.19
2020-01-30 15:30 | 35.83 | 4.82
2020-01-30 16:00 | 177.17 | 169.33
2020-01-30 16:30 | 121.16 | 111.48
2020-01-30 17:00 | 127.16 | 118.32
2020-01-30 17:30 | 45.67 | 27.1
2020-01-30 18:00 | 98.18 | 89.59
2020-01-30 18:30 | 199.16 | 198.57
2020-01-30 19:00 | 246.14 | 245.82
2020-01-30 19:30 | 188.9 | 188.45
2020-01-30 20:00 | 116.4 | 114.7
2020-01-30 20:30 | 166.4 | 165.73
2020-01-30 21:00 | 229.23 | 229.12
2020-01-30 21:30 | 215.47 | 215.42
2020-01-30 22:00 | 189.8 | 189.8
2020-01-30 22:30 | 166.3 | 166.29
2020-01-30 23:00 | 159.22 | 159.12
2020-01-30 23:30 | 128.54 | 128.54
2020-01-31 | 90.11 | 90.08
2020-01-31 00:30 | 107.95 | 107.83
2020-01-31 01:00 | 98.85 | 98.52
2020-01-31 01:30 | 100.97 | 100.48
2020-01-31 02:00 | 107.1 | 106.55
2020-01-31 02:30 | 98.65 | 97.97
2020-01-31 03:00 | 100.34 | 99.61
2020-01-31 03:30 | 93.45 | 92.72
2020-01-31 04:00 | 94.66 | 93.89
2020-01-31 04:30 | 100.77 | 100.19
2020-01-31 05:00 | 107.09 | 106.64
2020-01-31 05:30 | 112.85 | 112.52
2020-01-31 06:00 | 111.16 | 110.99
2020-01-31 06:30 | 96.16 | 96.16
2020-01-31 07:00 | 90.44 | 90.44
2020-01-31 07:30 | 112.7 | 111.87
2020-01-31 08:00 | 106.5 | 99.72
2020-01-31 08:30 | 73.11 | 56.81
2020-01-31 09:00 | 63.59 | 43.62
2020-01-31 09:30 | 65.42 | -6.48
2020-01-31 10:00 | 78.24 | 4.95
2020-01-31 10:30 | 93.63 | 58.6
2020-01-31 11:00 | 97.89 | 65.74
2020-01-31 11:30 | 96.94 | 63.7
2020-01-31 12:00 | 60.19 | -12.93
2020-01-31 12:30 | 59.19 | -44
2020-01-31 13:00 | 49.67 | -29.36
2020-01-31 13:30 | 52.68 | -24.23
2020-01-31 14:00 | 57.47 | -36.46
2020-01-31 14:30 | 45.06 | 1.69
2020-01-31 15:00 | 29.35 | -2.28
2020-01-31 15:30 | 36.95 | -17.85
2020-01-31 16:00 | 87.06 | 72.68
2020-01-31 16:30 | 68.59 | 14.57
2020-01-31 17:00 | 74.41 | 11.25
2020-01-31 17:30 | 150.13 | 134.38
2020-01-31 18:00 | 48.33 | 9.25
2020-01-31 18:30 | 70.6 | 66.28
2020-01-31 19:00 | 40.67 | 33.04
2020-01-31 19:30 | 201.09 | 199.28
2020-01-31 20:00 | 219.78 | 218.5
2020-01-31 20:30 | 185.34 | 183.96
2020-01-31 21:00 | 186.51 | 185.63
2020-01-31 21:30 | 168.09 | 167.05
2020-01-31 22:00 | 177.45 | 175.45
2020-01-31 22:30 | 178.39 | 178.33
2020-01-31 23:00 | 189.25 | 189.2
2020-01-31 23:30 | 156.43 | 156.35
2020-02-01 | 131.7 | 131.7
2020-02-01 00:30 | 120.59 | 120.44
2020-02-01 01:00 | 113.56 | 113.27
2020-02-01 01:30 | 103.73 | 103.22
2020-02-01 02:00 | 85.44 | 84.73
2020-02-01 02:30 | 65.97 | 64.89
2020-02-01 03:00 | 63.44 | 62.24
2020-02-01 03:30 | 58.17 | 56.87
2020-02-01 04:00 | 68.73 | 67.52
2020-02-01 04:30 | 67.74 | 66.58
2020-02-01 05:00 | 77.48 | 76.4
2020-02-01 05:30 | 70.61 | 69.37
2020-02-01 06:00 | 77.31 | 76.3
2020-02-01 06:30 | 33.42 | 32.56
2020-02-01 07:00 | 54.6 | 54.57
2020-02-01 07:30 | 28.89 | 27.81
2020-02-01 08:00 | 78.82 | -45.4
2020-02-01 08:30 | 113.53 | -66.14
2020-02-01 09:00 | 101.49 | -36.04
2020-02-01 09:30 | 100.94 | -37.83
2020-02-01 10:00 | 104.73 | -42.88
2020-02-01 10:30 | 101.43 | -28.95
2020-02-01 11:00 | 97.69 | -0.94
2020-02-01 11:30 | 99.38 | -14
2020-02-01 12:00 | 104.64 | -34.7
2020-02-01 12:30 | 104.51 | -32.82
2020-02-01 13:00 | 104.51 | -32.3
2020-02-01 13:30 | 107.79 | -30.95
2020-02-01 14:00 | 120.04 | -21.12
2020-02-01 14:30 | 119.26 | -13.73
2020-02-01 15:00 | 178.72 | 136.12
2020-02-01 15:30 | 180.71 | 148.94
2020-02-01 16:00 | 151.25 | 116.12
2020-02-01 16:30 | 127.44 | 89.51
2020-02-01 17:00 | 100.31 | 62.19
2020-02-01 17:30 | 68.5 | 0.92
2020-02-01 18:00 | 72.6 | 26.05
2020-02-01 18:30 | 169.11 | 156.55
2020-02-01 19:00 | 114.26 | 92.2
2020-02-01 19:30 | 110.08 | 92.83
2020-02-01 20:00 | 119.69 | 110.06
2020-02-01 20:30 | 47.08 | 4.35
2020-02-01 21:00 | 90.23 | 74.8
2020-02-01 21:30 | 132.81 | 128.01
2020-02-01 22:00 | 102.22 | 98.54
2020-02-01 22:30 | 133.41 | 133.31
2020-02-01 23:00 | 132.7 | 132.62
2020-02-01 23:30 | 121.76 | 121.74
2020-02-02 | 93.89 | 93.89
2020-02-02 00:30 | 82.35 | 82.25
2020-02-02 01:00 | 54.66 | 54.29
2020-02-02 01:30 | 42.01 | 41.31
2020-02-02 02:00 | 62.59 | 61.81
2020-02-02 02:30 | 60.41 | 59.4
2020-02-02 03:00 | 59.05 | 57.88
2020-02-02 03:30 | 58.93 | 57.74
2020-02-02 04:00 | 68.7 | 67.54
2020-02-02 04:30 | 74.34 | 73.31
2020-02-02 05:00 | 73.63 | 72.5
2020-02-02 05:30 | 68.34 | 66.79
2020-02-02 06:00 | 65.55 | 63.92
2020-02-02 06:30 | 50.52 | 49.55
2020-02-02 07:00 | 40.01 | 39.55
2020-02-02 07:30 | 28.21 | 28.21
2020-02-02 08:00 | 12.66 | -0.28
2020-02-02 08:30 | 35.29 | -2.44
2020-02-02 09:00 | 90.23 | -53.75
2020-02-02 09:30 | 76.08 | 31.14
2020-02-02 10:00 | 84.34 | 44.05
2020-02-02 10:30 | 89.39 | 49.54
2020-02-02 11:00 | 85.59 | 40.52
2020-02-02 11:30 | 101.88 | 67.04
2020-02-02 12:00 | 115.63 | 85.05
2020-02-02 12:30 | 134.46 | 108.69
2020-02-02 13:00 | 145.34 | 123.87
2020-02-02 13:30 | 167.79 | 148.83
2020-02-02 14:00 | 197.84 | 181.06
2020-02-02 14:30 | 201.77 | 184.49
2020-02-02 15:00 | 207.45 | 190.07
2020-02-02 15:30 | 233.31 | 215.41
2020-02-02 16:00 | 253.08 | 237.2
2020-02-02 16:30 | 288.46 | 273.79
2020-02-02 17:00 | 310.05 | 295.56
2020-02-02 17:30 | 323.75 | 309.77
2020-02-02 18:00 | 320.9 | 306.92
2020-02-02 18:30 | 316.05 | 305.23
2020-02-02 19:00 | 307.3 | 302.09
2020-02-02 19:30 | 306.93 | 301.51
2020-02-02 20:00 | 296.38 | 291.96
2020-02-02 20:30 | 285.75 | 282.53
2020-02-02 21:00 | 269.82 | 267.98
2020-02-02 21:30 | 243.96 | 242.29
2020-02-02 22:00 | 240.84 | 238.06
2020-02-02 22:30 | 225.69 | 223.1
2020-02-02 23:00 | 220.27 | 218.11
2020-02-02 23:30 | 216.7 | 215.34
2020-02-03 | 178.3 | 178.23
2020-02-03 00:30 | 171.33 | 170.58
2020-02-03 01:00 | 168.15 | 167.3
2020-02-03 01:30 | 155.14 | 154.21
2020-02-03 02:00 | 146.73 | 145.71
2020-02-03 02:30 | 136.8 | 135.79
2020-02-03 03:00 | 139.79 | 138.88
2020-02-03 03:30 | 140.36 | 139.57
2020-02-03 04:00 | 149.37 | 148.83
2020-02-03 04:30 | 157.57 | 157.13
2020-02-03 05:00 | 167.54 | 167.15
2020-02-03 05:30 | 172.95 | 172.59
2020-02-03 06:00 | 182.52 | 182.31
2020-02-03 06:30 | 186.94 | 186.86
2020-02-03 07:00 | 200.6 | 200.6
2020-02-03 07:30 | 204.45 | 204.42
2020-02-03 08:00 | 217.7 | 214.46
2020-02-03 08:30 | 221.89 | 211.06
2020-02-03 09:00 | 227.18 | 216.82
2020-02-03 09:30 | 247.62 | 237.43
2020-02-03 10:00 | 232.51 | 220.58
2020-02-03 10:30 | 242.62 | 230.24
2020-02-03 11:00 | 267.64 | 255.19
2020-02-03 11:30 | 276.81 | 264.81
2020-02-03 12:00 | 285.81 | 273.99
2020-02-03 12:30 | 287.41 | 275.05
2020-02-03 13:00 | 291.87 | 278.53
2020-02-03 13:30 | 290.82 | 272.64
2020-02-03 14:00 | 306.86 | 284.47
2020-02-03 14:30 | 311.97 | 289.55
2020-02-03 15:00 | 321.92 | 305.59
2020-02-03 15:30 | 332.34 | 316.74
2020-02-03 16:00 | 341.46 | 327.05
2020-02-03 16:30 | 354.73 | 343.63
2020-02-03 17:00 | 372.92 | 361.9
2020-02-03 17:30 | 371.53 | 361.93
2020-02-03 18:00 | 367.7 | 359.4
2020-02-03 18:30 | 356.76 | 349.48
2020-02-03 19:00 | 355.71 | 348.3
2020-02-03 19:30 | 345.14 | 338.43
2020-02-03 20:00 | 324.94 | 322.58
2020-02-03 20:30 | 297.95 | 297.25
2020-02-03 21:00 | 277.14 | 276.96
2020-02-03 21:30 | 254.08 | 254.07
2020-02-03 22:00 | 229 | 228.9
2020-02-03 22:30 | 220.04 | 219.98
2020-02-03 23:00 | 204.68 | 204.66
2020-02-03 23:30 | 197.23 | 196.91
2020-02-04 | 190.11 | 189.75
2020-02-04 00:30 | 172.69 | 172.57
2020-02-04 01:00 | 170.28 | 169.33
2020-02-04 01:30 | 166.09 | 165.12
2020-02-04 02:00 | 162.14 | 161.36
2020-02-04 02:30 | 160.14 | 159.5
2020-02-04 03:00 | 158.36 | 157.7
2020-02-04 03:30 | 158.59 | 157.96
2020-02-04 04:00 | 154.57 | 153.91
2020-02-04 04:30 | 160.44 | 160
2020-02-04 05:00 | 163.7 | 163.37
2020-02-04 05:30 | 169.49 | 169.34
2020-02-04 06:00 | 177.24 | 177.17
2020-02-04 06:30 | 188.62 | 188.6
2020-02-04 07:00 | 206.29 | 205.61
2020-02-04 07:30 | 236.35 | 227.38
2020-02-04 08:00 | 242.4 | 232.56
2020-02-04 08:30 | 233.68 | 222.47
2020-02-04 09:00 | 209.41 | 199.87
2020-02-04 09:30 | 205.93 | 197
2020-02-04 10:00 | 210.33 | 201.14
2020-02-04 10:30 | 213.04 | 203.78
2020-02-04 11:00 | 213.79 | 204.61
2020-02-04 11:30 | 198.28 | 190.83
2020-02-04 12:00 | 181.24 | 176.9
2020-02-04 12:30 | 193.55 | 189.46
2020-02-04 13:00 | 193.32 | 189.21
2020-02-04 13:30 | 186.68 | 182.71
2020-02-04 14:00 | 193.7 | 189.77
2020-02-04 14:30 | 192.42 | 188.58
2020-02-04 15:00 | 198.85 | 195.27
2020-02-04 15:30 | 197.98 | 194.91
2020-02-04 16:00 | 215.59 | 212.86
2020-02-04 16:30 | 225.47 | 224.85
2020-02-04 17:00 | 226.4 | 226.39
2020-02-04 17:30 | 226.16 | 226.16
2020-02-04 18:00 | 226.34 | 226.34
2020-02-04 18:30 | 225.55 | 225.55
2020-02-04 19:00 | 219.35 | 219.35
2020-02-04 19:30 | 220.68 | 220.67
2020-02-04 20:00 | 221.05 | 221.01
2020-02-04 20:30 | 209.6 | 209.51
2020-02-04 21:00 | 204.25 | 204
2020-02-04 21:30 | 198.13 | 197.85
2020-02-04 22:00 | 173.04 | 172.58
2020-02-04 22:30 | 179.52 | 179.09
2020-02-04 23:00 | 174.4 | 173.9
2020-02-04 23:30 | 139.53 | 138.77
2020-02-05 | 104.67 | 103.53
2020-02-05 00:30 | 101.05 | 99.58
2020-02-05 01:00 | 109.09 | 107.52
2020-02-05 01:30 | 96.6 | 94.45
2020-02-05 02:00 | 90.34 | 87.66
2020-02-05 02:30 | 87.74 | 85.08
2020-02-05 03:00 | 83.35 | 80.38
2020-02-05 03:30 | 77.02 | 73.85
2020-02-05 04:00 | 78.48 | 75.39
2020-02-05 04:30 | 81.87 | 79.2
2020-02-05 05:00 | 87.02 | 84.66
2020-02-05 05:30 | 103.08 | 101.64
2020-02-05 06:00 | 121.43 | 120.44
2020-02-05 06:30 | 121.06 | 120.62
2020-02-05 07:00 | 145.23 | 145.12
2020-02-05 07:30 | 157.76 | 157.76
2020-02-05 08:00 | 152.59 | 152.56
2020-02-05 08:30 | 148.35 | 148.23
2020-02-05 09:00 | 163.93 | 162.48
2020-02-05 09:30 | 193.54 | 192.91
2020-02-05 10:00 | 192.84 | 192.72
2020-02-05 10:30 | 176.61 | 176.52
2020-02-05 11:00 | 161.21 | 161.14
2020-02-05 11:30 | 148.87 | 148.79
2020-02-05 12:00 | 145.3 | 145.23
2020-02-05 12:30 | 145.45 | 145.43
2020-02-05 13:00 | 142.86 | 142.86
2020-02-05 13:30 | 149.95 | 149.93
2020-02-05 14:00 | 168.6 | 168.58
2020-02-05 14:30 | 174.11 | 174.09
2020-02-05 15:00 | 163.18 | 163.17
2020-02-05 15:30 | 150.67 | 150.66
2020-02-05 16:00 | 173.22 | 173.22
2020-02-05 16:30 | 195.07 | 195.07
2020-02-05 17:00 | 212.06 | 212.05
2020-02-05 17:30 | 218.41 | 218.37
2020-02-05 18:00 | 221.6 | 221.45
2020-02-05 18:30 | 218.72 | 218.2
2020-02-05 19:00 | 221.88 | 221.32
2020-02-05 19:30 | 220.62 | 220.11
2020-02-05 20:00 | 217.85 | 217.51
2020-02-05 20:30 | 211.3 | 210.82
2020-02-05 21:00 | 171.74 | 171.74
2020-02-05 21:30 | 153.67 | 153.67
2020-02-05 22:00 | 134.22 | 134.21
2020-02-05 22:30 | 124.29 | 124.29
2020-02-05 23:00 | 119.31 | 119.31
2020-02-05 23:30 | 97.77 | 97.69
2020-02-06 | 73.08 | 72.9
2020-02-06 00:30 | 82.51 | 82.1
2020-02-06 01:00 | 83.91 | 83.48
2020-02-06 01:30 | 68.85 | 68.56
2020-02-06 02:00 | 63.29 | 62.98
2020-02-06 02:30 | 60.19 | 59.87
2020-02-06 03:00 | 62.71 | 62.34
2020-02-06 03:30 | 61.54 | 61.3
2020-02-06 04:00 | 65.18 | 64.94
2020-02-06 04:30 | 72.65 | 72.42
2020-02-06 05:00 | 80.57 | 80.44
2020-02-06 05:30 | 92.93 | 92.89
2020-02-06 06:00 | 106.85 | 106.82
2020-02-06 06:30 | 104.14 | 104.14
2020-02-06 07:00 | 116.21 | 116.2
2020-02-06 07:30 | 162.48 | 162.3
2020-02-06 08:00 | 168.75 | 168.55
2020-02-06 08:30 | 162.57 | 162.37
2020-02-06 09:00 | 169.5 | 169.37
2020-02-06 09:30 | 185 | 184.77
2020-02-06 10:00 | 177.45 | 177.18
2020-02-06 10:30 | 157.4 | 157.03
2020-02-06 11:00 | 139.2 | 138.76
2020-02-06 11:30 | 131.22 | 130.94
2020-02-06 12:00 | 159.2 | 159.03
2020-02-06 12:30 | 163.09 | 162.92
2020-02-06 13:00 | 181.79 | 181.65
2020-02-06 13:30 | 201.57 | 201.47
2020-02-06 14:00 | 199.49 | 199.35
2020-02-06 14:30 | 193.61 | 193.41
2020-02-06 15:00 | 182.49 | 182.3
2020-02-06 15:30 | 191.03 | 190.83
2020-02-06 16:00 | 195.12 | 194.93
2020-02-06 16:30 | 185.96 | 185.81
2020-02-06 17:00 | 189.24 | 189.09
2020-02-06 17:30 | 202.51 | 202.05
2020-02-06 18:00 | 220.35 | 219.83
2020-02-06 18:30 | 222.39 | 221.71
2020-02-06 19:00 | 231.91 | 231.15
2020-02-06 19:30 | 226.28 | 225.58
2020-02-06 20:00 | 219.41 | 218.98
2020-02-06 20:30 | 213.66 | 213.55
2020-02-06 21:00 | 202.2 | 201.98
2020-02-06 21:30 | 193.33 | 193.11
2020-02-06 22:00 | 180.15 | 179.91
2020-02-06 22:30 | 162.5 | 162.28
2020-02-06 23:00 | 172.26 | 172.02
2020-02-06 23:30 | 142.42 | 141.94
2020-02-07 | 107.01 | 106.4
2020-02-07 00:30 | 98.64 | 98.25
2020-02-07 01:00 | 98.45 | 97.35
2020-02-07 01:30 | 95.72 | 94.14
2020-02-07 02:00 | 89.45 | 87.85
2020-02-07 02:30 | 88.02 | 86.43
2020-02-07 03:00 | 87.3 | 85.74
2020-02-07 03:30 | 87.88 | 86.39
2020-02-07 04:00 | 82.67 | 81.01
2020-02-07 04:30 | 86.46 | 85.01
2020-02-07 05:00 | 102.29 | 101.08
2020-02-07 05:30 | 113.41 | 112.09
2020-02-07 06:00 | 127.71 | 126.61
2020-02-07 06:30 | 132.05 | 130.98
2020-02-07 07:00 | 142.5 | 141.65
2020-02-07 07:30 | 150.98 | 150.97
2020-02-07 08:00 | 162.37 | 162.17
2020-02-07 08:30 | 143.71 | 143.4
2020-02-07 09:00 | 134.27 | 133.81
2020-02-07 09:30 | 121.35 | 120.89
2020-02-07 10:00 | 134.88 | 134.65
2020-02-07 10:30 | 153.83 | 153.74
2020-02-07 11:00 | 129.95 | 129.78
2020-02-07 11:30 | 141.36 | 141.15
2020-02-07 12:00 | 147.25 | 147.09
2020-02-07 12:30 | 150.63 | 150.45
2020-02-07 13:00 | 126.91 | 126.85
2020-02-07 13:30 | 123.49 | 123.45
2020-02-07 14:00 | 129.85 | 129.82
2020-02-07 14:30 | 162.69 | 162.67
2020-02-07 15:00 | 169.01 | 169
2020-02-07 15:30 | 167.24 | 167.23
2020-02-07 16:00 | 178.21 | 178.19
2020-02-07 16:30 | 194.33 | 194.33
2020-02-07 17:00 | 221.01 | 221.01
2020-02-07 17:30 | 231.93 | 231.91
2020-02-07 18:00 | 235.16 | 235.15
2020-02-07 18:30 | 227.57 | 227.56
2020-02-07 19:00 | 219.64 | 219.44
2020-02-07 19:30 | 227.64 | 227.59
2020-02-07 20:00 | 227.01 | 226.98
2020-02-07 20:30 | 221.61 | 221.57
2020-02-07 21:00 | 212.76 | 212.72
2020-02-07 21:30 | 208.6 | 208.6
2020-02-07 22:00 | 194.2 | 194.16
2020-02-07 22:30 | 176.89 | 176.83
2020-02-07 23:00 | 186.44 | 186.37
2020-02-07 23:30 | 156.12 | 155.91
2020-02-08 | 126.19 | 125.32
2020-02-08 00:30 | 119.65 | 118.67
2020-02-08 01:00 | 118.91 | 117.97
2020-02-08 01:30 | 124.4 | 123.59
2020-02-08 02:00 | 111.43 | 110.25
2020-02-08 02:30 | 108.57 | 107.37
2020-02-08 03:00 | 107.72 | 106.41
2020-02-08 03:30 | 106.23 | 105.05
2020-02-08 04:00 | 105.03 | 103.86
2020-02-08 04:30 | 105.76 | 104.74
2020-02-08 05:00 | 115.06 | 114.13
2020-02-08 05:30 | 123.72 | 123.01
2020-02-08 06:00 | 123.34 | 122.62
2020-02-08 06:30 | 113.32 | 112.27
2020-02-08 07:00 | 104.73 | 103.3
2020-02-08 07:30 | 108.78 | 107.84
2020-02-08 08:00 | 120.87 | 120.84
2020-02-08 08:30 | 140.49 | 140.37
2020-02-08 09:00 | 146.18 | 146.05
2020-02-08 09:30 | 150.35 | 150.32
2020-02-08 10:00 | 132.58 | 132.58
2020-02-08 10:30 | 116.51 | 116.51
2020-02-08 11:00 | 110.5 | 110.5
2020-02-08 11:30 | 118.03 | 118
2020-02-08 12:00 | 131.79 | 131.69
2020-02-08 12:30 | 112.82 | 112.76
2020-02-08 13:00 | 98.99 | 98.95
2020-02-08 13:30 | 122.1 | 122.1
2020-02-08 14:00 | 159.42 | 159.39
2020-02-08 14:30 | 180.34 | 180.12
2020-02-08 15:00 | 156.83 | 156.7
2020-02-08 15:30 | 178.48 | 178.38
2020-02-08 16:00 | 206.73 | 206.63
2020-02-08 16:30 | 205.83 | 205.71
2020-02-08 17:00 | 225.22 | 225.03
2020-02-08 17:30 | 222.98 | 222.68
2020-02-08 18:00 | 218.06 | 217.61
2020-02-08 18:30 | 217.58 | 216.97
2020-02-08 19:00 | 226.65 | 226.13
2020-02-08 19:30 | 220.56 | 219.88
2020-02-08 20:00 | 217.32 | 216.75
2020-02-08 20:30 | 207.63 | 207.07
2020-02-08 21:00 | 200.35 | 199.96
2020-02-08 21:30 | 191.2 | 190.73
2020-02-08 22:00 | 179.45 | 179.28
2020-02-08 22:30 | 181.47 | 181.46
2020-02-08 23:00 | 191.01 | 191
2020-02-08 23:30 | 184.43 | 184.4
2020-02-09 | 164.42 | 164.31
2020-02-09 00:30 | 156.22 | 156.01
2020-02-09 01:00 | 139.62 | 139.14
2020-02-09 01:30 | 142.23 | 141.68
2020-02-09 02:00 | 138.65 | 138.04
2020-02-09 02:30 | 132.6 | 131.87
2020-02-09 03:00 | 119.69 | 119.58
2020-02-09 03:30 | 110.67 | 110.58
2020-02-09 04:00 | 103.17 | 103.07
2020-02-09 04:30 | 104.18 | 104.1
2020-02-09 05:00 | 104.21 | 104.13
2020-02-09 05:30 | 104.34 | 104.29
2020-02-09 06:00 | 99.54 | 99.49
2020-02-09 06:30 | 99.79 | 99.77
2020-02-09 07:00 | 78.59 | 78.58
2020-02-09 07:30 | 77.8 | 77.8
2020-02-09 08:00 | 77.11 | 77.05
2020-02-09 08:30 | 88.68 | 88.67
2020-02-09 09:00 | 79.3 | 79.14
2020-02-09 09:30 | 85.33 | 84.65
2020-02-09 10:00 | 117.58 | 116.64
2020-02-09 10:30 | 145.28 | 140.68
2020-02-09 11:00 | 171.87 | 159.96
2020-02-09 11:30 | 185.58 | 174.53
2020-02-09 12:00 | 183.29 | 171.75
2020-02-09 12:30 | 168.84 | 156.04
2020-02-09 13:00 | 162.98 | 155.28
2020-02-09 13:30 | 167.33 | 163.02
2020-02-09 14:00 | 152.3 | 148.34
2020-02-09 14:30 | 161.81 | 157.67
2020-02-09 15:00 | 178.58 | 175.05
2020-02-09 15:30 | 184.66 | 181.23
2020-02-09 16:00 | 206.86 | 203.4
2020-02-09 16:30 | 208.07 | 204.57
2020-02-09 17:00 | 222.11 | 218.5
2020-02-09 17:30 | 228.3 | 224.84
2020-02-09 18:00 | 226.41 | 222.8
2020-02-09 18:30 | 227.8 | 224.33
2020-02-09 19:00 | 233.1 | 229.22
2020-02-09 19:30 | 232.49 | 228.66
2020-02-09 20:00 | 226.94 | 223.39
2020-02-09 20:30 | 211.93 | 208.9
2020-02-09 21:00 | 202.69 | 200.07
2020-02-09 21:30 | 194.52 | 191.91
2020-02-09 22:00 | 181.16 | 180.08
2020-02-09 22:30 | 189.67 | 189.45
2020-02-09 23:00 | 190.21 | 190.12
2020-02-09 23:30 | 174.48 | 174.41
2020-02-10 | 146.35 | 146.21
2020-02-10 00:30 | 136.14 | 135.68
2020-02-10 01:00 | 122.99 | 121.44
2020-02-10 01:30 | 130.45 | 128.5
2020-02-10 02:00 | 139.1 | 137.08
2020-02-10 02:30 | 134.24 | 131.8
2020-02-10 03:00 | 123.58 | 120.68
2020-02-10 03:30 | 117.14 | 112.89
2020-02-10 04:00 | 98.17 | 92.98
2020-02-10 04:30 | 96.51 | 91.54
2020-02-10 05:00 | 102.34 | 98.17
2020-02-10 05:30 | 108.57 | 105.2
2020-02-10 06:00 | 119.94 | 119.89
2020-02-10 06:30 | 110.62 | 110.59
2020-02-10 07:00 | 120.27 | 120.27
2020-02-10 07:30 | 160.33 | 160.19
2020-02-10 08:00 | 160.65 | 158.33
2020-02-10 08:30 | 151 | 147.83
2020-02-10 09:00 | 172.67 | 169.1
2020-02-10 09:30 | 189.29 | 185.18
2020-02-10 10:00 | 192.29 | 188.74
2020-02-10 10:30 | 197.65 | 193.85
2020-02-10 11:00 | 203.41 | 199.16
2020-02-10 11:30 | 230.53 | 226.44
2020-02-10 12:00 | 249.99 | 246.06
2020-02-10 12:30 | 228.29 | 224.69
2020-02-10 13:00 | 215.44 | 211.54
2020-02-10 13:30 | 216.28 | 212.19
2020-02-10 14:00 | 199.92 | 195.62
2020-02-10 14:30 | 208.28 | 204.46
2020-02-10 15:00 | 216.78 | 213.32
2020-02-10 15:30 | 200.24 | 196.87
2020-02-10 16:00 | 231.36 | 228.14
2020-02-10 16:30 | 233.45 | 230.5
2020-02-10 17:00 | 237.66 | 235.1
2020-02-10 17:30 | 260.57 | 258.7
2020-02-10 18:00 | 271.99 | 270.35
2020-02-10 18:30 | 271.56 | 270.04
2020-02-10 19:00 | 263.35 | 261.4
2020-02-10 19:30 | 261.92 | 260.38
2020-02-10 20:00 | 259.14 | 257.95
2020-02-10 20:30 | 250.39 | 249
2020-02-10 21:00 | 241.56 | 239.78
2020-02-10 21:30 | 229.62 | 226.24
2020-02-10 22:00 | 209.89 | 208.4
2020-02-10 22:30 | 171.77 | 171.53
2020-02-10 23:00 | 162.28 | 162.1
2020-02-10 23:30 | 128.98 | 128.89
2020-02-11 | 108.07 | 108.06
2020-02-11 00:30 | 94.22 | 94.07
2020-02-11 01:00 | 86.73 | 86.43
2020-02-11 01:30 | 60.48 | 59.77
2020-02-11 02:00 | 69.27 | 68.62
2020-02-11 02:30 | 64.29 | 63.82
2020-02-11 03:00 | 55.34 | 54.7
2020-02-11 03:30 | 54.53 | 53.98
2020-02-11 04:00 | 52.98 | 52.35
2020-02-11 04:30 | 67.88 | 67.28
2020-02-11 05:00 | 82.03 | 81.58
2020-02-11 05:30 | 110.32 | 110.13
2020-02-11 06:00 | 138.12 | 138.08
2020-02-11 06:30 | 144.8 | 144.76
2020-02-11 07:00 | 136.24 | 135.96
2020-02-11 07:30 | 164.45 | 163.83
2020-02-11 08:00 | 162.82 | 162.24
2020-02-11 08:30 | 137.21 | 136.52
2020-02-11 09:00 | 120.79 | 118.31
2020-02-11 09:30 | 132.65 | 127.96
2020-02-11 10:00 | 125.71 | 119.97
2020-02-11 10:30 | 128.86 | 122.55
2020-02-11 11:00 | 164.67 | 158.71
2020-02-11 11:30 | 174.6 | 168.69
2020-02-11 12:00 | 172.23 | 166.1
2020-02-11 12:30 | 169.96 | 163.61
2020-02-11 13:00 | 169 | 162.27
2020-02-11 13:30 | 199.64 | 191.99
2020-02-11 14:00 | 194.66 | 181.56
2020-02-11 14:30 | 200.54 | 192.08
2020-02-11 15:00 | 174.64 | 165.38
2020-02-11 15:30 | 159.41 | 149.78
2020-02-11 16:00 | 187.38 | 179.56
2020-02-11 16:30 | 192.03 | 184.21
2020-02-11 17:00 | 202.61 | 194.88
2020-02-11 17:30 | 224.46 | 217.98
2020-02-11 18:00 | 238.42 | 233.15
2020-02-11 18:30 | 255.01 | 252.88
2020-02-11 19:00 | 290.05 | 287.99
2020-02-11 19:30 | 284.29 | 282.18
2020-02-11 20:00 | 266.84 | 264.84
2020-02-11 20:30 | 273.26 | 272.23
2020-02-11 21:00 | 235.9 | 235.9
2020-02-11 21:30 | 233.61 | 233.52
2020-02-11 22:00 | 195.85 | 195.64
2020-02-11 22:30 | 190.69 | 190.68
2020-02-11 23:00 | 189.48 | 189.46
2020-02-11 23:30 | 151.52 | 151.49
2020-02-12 | 133.99 | 133.96
2020-02-12 00:30 | 126.38 | 126.38
2020-02-12 01:00 | 116.76 | 116.66
2020-02-12 01:30 | 115.33 | 115.2
2020-02-12 02:00 | 118.2 | 118.05
2020-02-12 02:30 | 115.67 | 115.48
2020-02-12 03:00 | 116.7 | 116.7
2020-02-12 03:30 | 106.4 | 106.38
2020-02-12 04:00 | 105.4 | 105.39
2020-02-12 04:30 | 106.66 | 106.62
2020-02-12 05:00 | 109.02 | 109.01
2020-02-12 05:30 | 112.4 | 112.4
2020-02-12 06:00 | 120.02 | 120.02
2020-02-12 06:30 | 121.21 | 121.11
2020-02-12 07:00 | 125.87 | 120.72
2020-02-12 07:30 | 147.53 | 139.72
2020-02-12 08:00 | 168.72 | 155.41
2020-02-12 08:30 | 171.52 | 148.34
2020-02-12 09:00 | 172.41 | 148.16
2020-02-12 09:30 | 194.74 | 174.13
2020-02-12 10:00 | 195.32 | 174.71
2020-02-12 10:30 | 189.19 | 167.56
2020-02-12 11:00 | 202.75 | 182.59
2020-02-12 11:30 | 202.79 | 182.32
2020-02-12 12:00 | 178.68 | 156.71
2020-02-12 12:30 | 180.54 | 160.12
2020-02-12 13:00 | 188.95 | 169.93
2020-02-12 13:30 | 182.51 | 164.81
2020-02-12 14:00 | 183.3 | 167.19
2020-02-12 14:30 | 178.07 | 161.93
2020-02-12 15:00 | 169.43 | 152.78
2020-02-12 15:30 | 162.62 | 157.89
2020-02-12 16:00 | 173.81 | 170.56
2020-02-12 16:30 | 178.1 | 175
2020-02-12 17:00 | 191.65 | 189.11
2020-02-12 17:30 | 198.76 | 196.51
2020-02-12 18:00 | 203.46 | 202.03
2020-02-12 18:30 | 222.75 | 220.73
2020-02-12 19:00 | 244.45 | 241.35
2020-02-12 19:30 | 237.09 | 233.6
2020-02-12 20:00 | 236.84 | 233.43
2020-02-12 20:30 | 224.29 | 221.33
2020-02-12 21:00 | 202.37 | 200.7
2020-02-12 21:30 | 209.39 | 207.75
2020-02-12 22:00 | 182.38 | 181.24
2020-02-12 22:30 | 175.76 | 174.82
2020-02-12 23:00 | 168.86 | 168.18
2020-02-12 23:30 | 176.1 | 175.73
2020-02-13 | 149.4 | 149.33
2020-02-13 00:30 | 133.13 | 133.12
2020-02-13 01:00 | 117.58 | 117.58
2020-02-13 01:30 | 123.12 | 123.1
2020-02-13 02:00 | 112.63 | 112.54
2020-02-13 02:30 | 116.14 | 116.04
2020-02-13 03:00 | 110.22 | 110.1
2020-02-13 03:30 | 108.98 | 108.89
2020-02-13 04:00 | 109.05 | 109
2020-02-13 04:30 | 113.24 | 113.22
2020-02-13 05:00 | 117.34 | 117.34
2020-02-13 05:30 | 108.03 | 108.03
2020-02-13 06:00 | 101.91 | 101.85
2020-02-13 06:30 | 131.83 | 131.77
2020-02-13 07:00 | 143.39 | 143.27
2020-02-13 07:30 | 149.89 | 149.6
2020-02-13 08:00 | 148.91 | 147.97
2020-02-13 08:30 | 154.25 | 152.66
2020-02-13 09:00 | 146.16 | 144.3
2020-02-13 09:30 | 150.99 | 147.16
2020-02-13 10:00 | 161.8 | 156.98
2020-02-13 10:30 | 153.21 | 148
2020-02-13 11:00 | 157.6 | 152.55
2020-02-13 11:30 | 156.05 | 151.1
2020-02-13 12:00 | 141.21 | 135.93
2020-02-13 12:30 | 133.51 | 128.09
2020-02-13 13:00 | 112.57 | 106.31
2020-02-13 13:30 | 140.21 | 135.14
2020-02-13 14:00 | 137.73 | 132.92
2020-02-13 14:30 | 130.48 | 125.94
2020-02-13 15:00 | 78.6 | 70.13
2020-02-13 15:30 | 84.12 | 76.34
2020-02-13 16:00 | 106.24 | 100.87
2020-02-13 16:30 | 66.06 | 57.06
2020-02-13 17:00 | 98.24 | 92.69
2020-02-13 17:30 | 159.6 | 156.95
2020-02-13 18:00 | 171.12 | 168.78
2020-02-13 18:30 | 192.44 | 190.38
2020-02-13 19:00 | 197.48 | 195.01
2020-02-13 19:30 | 187.34 | 185.26
2020-02-13 20:00 | 188.15 | 186.49
2020-02-13 20:30 | 188.78 | 187.58
2020-02-13 21:00 | 184.76 | 183.39
2020-02-13 21:30 | 161.34 | 158.27
2020-02-13 22:00 | 147.83 | 145.41
2020-02-13 22:30 | 152.25 | 149.97
2020-02-13 23:00 | 150.68 | 150.68
2020-02-13 23:30 | 122.68 | 122.59
2020-02-14 | 96.55 | 96.44
2020-02-14 00:30 | 85.92 | 85.87
2020-02-14 01:00 | 73.44 | 73.44
2020-02-14 01:30 | 68.77 | 68.77
2020-02-14 02:00 | 42.64 | 41.71
2020-02-14 02:30 | 24.04 | 20
2020-02-14 03:00 | 24.45 | 20.77
2020-02-14 03:30 | 22.17 | 17.56
2020-02-14 04:00 | 26.87 | 22.78
2020-02-14 04:30 | 35.79 | 32.97
2020-02-14 05:00 | 46.66 | 44.53
2020-02-14 05:30 | 58.4 | 56.9
2020-02-14 06:00 | 68.11 | 67.66
2020-02-14 06:30 | 65.24 | 65.23
2020-02-14 07:00 | 42.09 | 41.75
2020-02-14 07:30 | 65.15 | 64.09
2020-02-14 08:00 | 34.69 | -25.72
2020-02-14 08:30 | 49.46 | -37.97
2020-02-14 09:00 | 49.2 | -34.38
2020-02-14 09:30 | 53.83 | -34.99
2020-02-14 10:00 | 49.13 | -20.25
2020-02-14 10:30 | 67.65 | 50.76
2020-02-14 11:00 | 90.57 | 77.79
2020-02-14 11:30 | 103.37 | 91.49
2020-02-14 12:00 | 103.28 | 91.34
2020-02-14 12:30 | 103.64 | 91.89
2020-02-14 13:00 | 107.79 | 96.87
2020-02-14 13:30 | 131.81 | 122.84
2020-02-14 14:00 | 147.47 | 139.72
2020-02-14 14:30 | 168.58 | 162.24
2020-02-14 15:00 | 161.68 | 155.64
2020-02-14 15:30 | 167.44 | 161.41
2020-02-14 16:00 | 196.66 | 190.96
2020-02-14 16:30 | 232.53 | 227.6
2020-02-14 17:00 | 244.02 | 239.73
2020-02-14 17:30 | 246.31 | 243.01
2020-02-14 18:00 | 246.97 | 244.28
2020-02-14 18:30 | 254.22 | 251.96
2020-02-14 19:00 | 261.58 | 259.08
2020-02-14 19:30 | 258.7 | 256.17
2020-02-14 20:00 | 256.23 | 254.08
2020-02-14 20:30 | 237.48 | 236.13
2020-02-14 21:00 | 223.89 | 223.65
2020-02-14 21:30 | 186.74 | 186.66
2020-02-14 22:00 | 166.98 | 166.93
2020-02-14 22:30 | 168.41 | 168.4
2020-02-14 23:00 | 161.66 | 161.66
2020-02-14 23:30 | 137.8 | 137.78
2020-02-15 | 102.96 | 102.93
2020-02-15 00:30 | 103.37 | 103.21
2020-02-15 01:00 | 98.57 | 98.2
2020-02-15 01:30 | 110.41 | 110
2020-02-15 02:00 | 108.21 | 107.87
2020-02-15 02:30 | 107.19 | 106.93
2020-02-15 03:00 | 107.32 | 107.05
2020-02-15 03:30 | 97.7 | 97.43
2020-02-15 04:00 | 97.51 | 97.24
2020-02-15 04:30 | 96.9 | 96.57
2020-02-15 05:00 | 99.48 | 99.11
2020-02-15 05:30 | 100.45 | 100.13
2020-02-15 06:00 | 98.51 | 98.25
2020-02-15 06:30 | 91.91 | 91.88
2020-02-15 07:00 | 80.45 | 80.44
2020-02-15 07:30 | 83.62 | 83.59
2020-02-15 08:00 | 79.12 | 77.91
2020-02-15 08:30 | 85.48 | 79.34
2020-02-15 09:00 | 90.97 | 84.21
2020-02-15 09:30 | 104.13 | 97.06
2020-02-15 10:00 | 132.45 | 124.34
2020-02-15 10:30 | 143.89 | 129.62
2020-02-15 11:00 | 165.92 | 152.7
2020-02-15 11:30 | 166.33 | 154.57
2020-02-15 12:00 | 178.61 | 172.08
2020-02-15 12:30 | 186.46 | 179.83
2020-02-15 13:00 | 191.59 | 180.05
2020-02-15 13:30 | 210.88 | 200.99
2020-02-15 14:00 | 228.07 | 218.39
2020-02-15 14:30 | 238.91 | 228.78
2020-02-15 15:00 | 233.85 | 222.62
2020-02-15 15:30 | 261.45 | 250.19
2020-02-15 16:00 | 291.02 | 279.84
2020-02-15 16:30 | 308.25 | 293.18
2020-02-15 17:00 | 294.78 | 278.56
2020-02-15 17:30 | 303.82 | 288.26
2020-02-15 18:00 | 313.81 | 299.19
2020-02-15 18:30 | 291.21 | 276.68
2020-02-15 19:00 | 311.79 | 298.46
2020-02-15 19:30 | 309.82 | 297.42
2020-02-15 20:00 | 300.33 | 289.31
2020-02-15 20:30 | 286.65 | 280.97
2020-02-15 21:00 | 271.78 | 267.09
2020-02-15 21:30 | 262.05 | 255.25
2020-02-15 22:00 | 247.58 | 240.83
2020-02-15 22:30 | 239.03 | 232.61
2020-02-15 23:00 | 234.13 | 226.99
2020-02-15 23:30 | 211.28 | 203.93
2020-02-16 | 176.42 | 176.37
2020-02-16 00:30 | 178.63 | 178.63
2020-02-16 01:00 | 170.17 | 170.14
2020-02-16 01:30 | 155.57 | 155.5
2020-02-16 02:00 | 161.1 | 160.94
2020-02-16 02:30 | 158.66 | 158.45
2020-02-16 03:00 | 156.47 | 156.19
2020-02-16 03:30 | 154.35 | 154.06
2020-02-16 04:00 | 151.7 | 151.4
2020-02-16 04:30 | 151.43 | 151.12
2020-02-16 05:00 | 151.63 | 151.34
2020-02-16 05:30 | 145.32 | 145.08
2020-02-16 06:00 | 134.95 | 134.94
2020-02-16 06:30 | 128.52 | 128.47
2020-02-16 07:00 | 121.8 | 121.8
2020-02-16 07:30 | 117.48 | 117.47
2020-02-16 08:00 | 112.51 | 108.17
2020-02-16 08:30 | 145.11 | 131.46
2020-02-16 09:00 | 153.39 | 138.3
2020-02-16 09:30 | 173.69 | 158.9
2020-02-16 10:00 | 177.85 | 162.33
2020-02-16 10:30 | 188.15 | 172.05
2020-02-16 11:00 | 198.09 | 181.29
2020-02-16 11:30 | 200 | 182.98
2020-02-16 12:00 | 205.2 | 191.63
2020-02-16 12:30 | 209.21 | 198.41
2020-02-16 13:00 | 206.99 | 195.42
2020-02-16 13:30 | 231.46 | 220.4
2020-02-16 14:00 | 257.46 | 246.75
2020-02-16 14:30 | 271.86 | 260.81
2020-02-16 15:00 | 277.94 | 262.07
2020-02-16 15:30 | 300.25 | 283.77
2020-02-16 16:00 | 309.57 | 293.4
2020-02-16 16:30 | 313.85 | 299.67
2020-02-16 17:00 | 323.11 | 309.27
2020-02-16 17:30 | 323.84 | 310.7
2020-02-16 18:00 | 318.88 | 306.42
2020-02-16 18:30 | 312.42 | 301.01
2020-02-16 19:00 | 316.81 | 305.34
2020-02-16 19:30 | 309.3 | 297.96
2020-02-16 20:00 | 299.93 | 289.27
2020-02-16 20:30 | 285.05 | 279.63
2020-02-16 21:00 | 268.89 | 260.5
2020-02-16 21:30 | 254.4 | 246.44
2020-02-16 22:00 | 240.26 | 232.86
2020-02-16 22:30 | 227.4 | 221.8
2020-02-16 23:00 | 214.6 | 213
2020-02-16 23:30 | 204.65 | 203.59
2020-02-17 | 182.43 | 181.66
2020-02-17 00:30 | 172.5 | 171.98
2020-02-17 01:00 | 169.29 | 168.91
2020-02-17 01:30 | 162.89 | 162.54
2020-02-17 02:00 | 160.22 | 159.69
2020-02-17 02:30 | 158.45 | 157.84
2020-02-17 03:00 | 157.11 | 156.53
2020-02-17 03:30 | 156.74 | 156.16
2020-02-17 04:00 | 155.9 | 155.31
2020-02-17 04:30 | 133.4 | 132.73
2020-02-17 05:00 | 134.34 | 133.54
2020-02-17 05:30 | 131.93 | 130.94
2020-02-17 06:00 | 119.26 | 117.98
2020-02-17 06:30 | 124.89 | 123.93
2020-02-17 07:00 | 137.09 | 136.71
2020-02-17 07:30 | 165.56 | 164
2020-02-17 08:00 | 184.91 | 175.09
2020-02-17 08:30 | 172.32 | 159.23
2020-02-17 09:00 | 157.19 | 144.11
2020-02-17 09:30 | 153.6 | 143.7
2020-02-17 10:00 | 165.74 | 155.83
2020-02-17 10:30 | 155.89 | 144.57
2020-02-17 11:00 | 149.42 | 139.45
2020-02-17 11:30 | 153.23 | 147.26
2020-02-17 12:00 | 163.09 | 157.27
2020-02-17 12:30 | 180.06 | 174.66
2020-02-17 13:00 | 191.25 | 185.98
2020-02-17 13:30 | 192.56 | 187.31
2020-02-17 14:00 | 190.79 | 185.14
2020-02-17 14:30 | 202.62 | 197.19
2020-02-17 15:00 | 212.84 | 207.69
2020-02-17 15:30 | 224.03 | 218.82
2020-02-17 16:00 | 226.28 | 220.66
2020-02-17 16:30 | 233.43 | 227.83
2020-02-17 17:00 | 283.92 | 275.12
2020-02-17 17:30 | 315.29 | 307.82
2020-02-17 18:00 | 310.57 | 304
2020-02-17 18:30 | 301.03 | 295.82
2020-02-17 19:00 | 316.15 | 310.31
2020-02-17 19:30 | 316.12 | 310.98
2020-02-17 20:00 | 302.86 | 301.16
2020-02-17 20:30 | 281.16 | 280.19
2020-02-17 21:00 | 246.93 | 246.08
2020-02-17 21:30 | 240.88 | 239.58
2020-02-17 22:00 | 206.29 | 204.24
2020-02-17 22:30 | 193.91 | 190.23
2020-02-17 23:00 | 195.33 | 191.52
2020-02-17 23:30 | 181.34 | 181.2
2020-02-18 | 151.21 | 151.2
2020-02-18 00:30 | 140.23 | 140.12
2020-02-18 01:00 | 134.49 | 134.24
2020-02-18 01:30 | 126.17 | 125.99
2020-02-18 02:00 | 128.4 | 128.4
2020-02-18 02:30 | 126.63 | 126.63
2020-02-18 03:00 | 117.86 | 117.86
2020-02-18 03:30 | 123.91 | 123.9
2020-02-18 04:00 | 123.49 | 123.44
2020-02-18 04:30 | 128.45 | 128.38
2020-02-18 05:00 | 138.65 | 138.56
2020-02-18 05:30 | 135.58 | 135.45
2020-02-18 06:00 | 126.15 | 126.04
2020-02-18 06:30 | 137.69 | 137.48
2020-02-18 07:00 | 162.15 | 161.6
2020-02-18 07:30 | 177.62 | 175.37
2020-02-18 08:00 | 179.94 | 176.48
2020-02-18 08:30 | 194.6 | 193.07
2020-02-18 09:00 | 189.72 | 188.27
2020-02-18 09:30 | 197.17 | 194.3
2020-02-18 10:00 | 197.12 | 195.38
2020-02-18 10:30 | 194.99 | 193.15
2020-02-18 11:00 | 193.02 | 190.9
2020-02-18 11:30 | 166.78 | 164.42
2020-02-18 12:00 | 176.11 | 172.79
2020-02-18 12:30 | 195.69 | 185.72
2020-02-18 13:00 | 174.74 | 166.37
2020-02-18 13:30 | 178.37 | 168.84
2020-02-18 14:00 | 178.96 | 169.47
2020-02-18 14:30 | 189.32 | 180.37
2020-02-18 15:00 | 185.06 | 175.55
2020-02-18 15:30 | 210.33 | 201.14
2020-02-18 16:00 | 236.98 | 227.88
2020-02-18 16:30 | 281.44 | 272.82
2020-02-18 17:00 | 314.59 | 305.2
2020-02-18 17:30 | 325.89 | 313.92
2020-02-18 18:00 | 332.78 | 322.05
2020-02-18 18:30 | 335.78 | 326.4
2020-02-18 19:00 | 338.51 | 328.06
2020-02-18 19:30 | 339.12 | 329.25
2020-02-18 20:00 | 332.88 | 324.26
2020-02-18 20:30 | 315.43 | 310.15
2020-02-18 21:00 | 294.85 | 291.98
2020-02-18 21:30 | 271.85 | 270.5
2020-02-18 22:00 | 247.28 | 246.41
2020-02-18 22:30 | 234.99 | 229.39
2020-02-18 23:00 | 227.55 | 219.73
2020-02-18 23:30 | 213.18 | 204.89
2020-02-19 | 195.02 | 192.83
2020-02-19 00:30 | 176.54 | 176.52
2020-02-19 01:00 | 172.71 | 172.71
2020-02-19 01:30 | 161.16 | 161.15
2020-02-19 02:00 | 161.72 | 161.72
2020-02-19 02:30 | 160.98 | 160.98
2020-02-19 03:00 | 160.89 | 160.89
2020-02-19 03:30 | 160.96 | 160.96
2020-02-19 04:00 | 162.95 | 162.94
2020-02-19 04:30 | 165.06 | 165.04
2020-02-19 05:00 | 167.4 | 167.36
2020-02-19 05:30 | 162.53 | 162.42
2020-02-19 06:00 | 168.63 | 168.16
2020-02-19 06:30 | 161.61 | 158.17
2020-02-19 07:00 | 167.47 | 161.64
2020-02-19 07:30 | 207.74 | 200.53
2020-02-19 08:00 | 215.61 | 205.87
2020-02-19 08:30 | 199.48 | 189.69
2020-02-19 09:00 | 207.39 | 197.09
2020-02-19 09:30 | 246.91 | 236.57
2020-02-19 10:00 | 248.78 | 238.5
2020-02-19 10:30 | 251.26 | 242.58
2020-02-19 11:00 | 260.48 | 250.44
2020-02-19 11:30 | 272.09 | 261.17
2020-02-19 12:00 | 273.32 | 263.15
2020-02-19 12:30 | 276.56 | 266.11
2020-02-19 13:00 | 283.28 | 272.09
2020-02-19 13:30 | 282.99 | 272.02
2020-02-19 14:00 | 291.09 | 280.01
2020-02-19 14:30 | 304.63 | 293.91
2020-02-19 15:00 | 310 | 299.38
2020-02-19 15:30 | 320.73 | 310.33
2020-02-19 16:00 | 345.04 | 332.39
2020-02-19 16:30 | 358.1 | 341.96
2020-02-19 17:00 | 373.68 | 357.35
2020-02-19 17:30 | 381.41 | 366.15
2020-02-19 18:00 | 377.44 | 363.11
2020-02-19 18:30 | 373.85 | 360.7
2020-02-19 19:00 | 372.33 | 358.88
2020-02-19 19:30 | 358.26 | 345.25
2020-02-19 20:00 | 330.65 | 319.06
2020-02-19 20:30 | 310.64 | 301.59
2020-02-19 21:00 | 281.35 | 277.05
2020-02-19 21:30 | 260.81 | 259.48
2020-02-19 22:00 | 230.68 | 229.3
2020-02-19 22:30 | 195 | 193.02
2020-02-19 23:00 | 182.84 | 180.94
2020-02-19 23:30 | 163.7 | 163.44
2020-02-20 | 142.67 | 142.57
2020-02-20 00:30 | 152.41 | 152.33
2020-02-20 01:00 | 140.51 | 140.51
2020-02-20 01:30 | 144.02 | 144.01
2020-02-20 02:00 | 132.69 | 132.66
2020-02-20 02:30 | 122.85 | 122.81
2020-02-20 03:00 | 114.98 | 114.92
2020-02-20 03:30 | 115.81 | 115.7
2020-02-20 04:00 | 112.5 | 112.4
2020-02-20 04:30 | 112.72 | 112.64
2020-02-20 05:00 | 103.68 | 103.63
2020-02-20 05:30 | 120.41 | 120.41
2020-02-20 06:00 | 125.69 | 125.68
2020-02-20 06:30 | 137.8 | 137.64
2020-02-20 07:00 | 154.2 | 154.06
2020-02-20 07:30 | 163.9 | 163.6
2020-02-20 08:00 | 148.59 | 147.09
2020-02-20 08:30 | 138.05 | 132.79
2020-02-20 09:00 | 147.29 | 133.99
2020-02-20 09:30 | 159.37 | 155.03
2020-02-20 10:00 | 173.95 | 169.64
2020-02-20 10:30 | 170.05 | 165.41
2020-02-20 11:00 | 166.52 | 159.59
2020-02-20 11:30 | 174.45 | 167.72
2020-02-20 12:00 | 193.27 | 187.22
2020-02-20 12:30 | 200.02 | 193.89
2020-02-20 13:00 | 204.98 | 198.62
2020-02-20 13:30 | 237.41 | 231.7
2020-02-20 14:00 | 245.03 | 240.19
2020-02-20 14:30 | 245.05 | 240.34
2020-02-20 15:00 | 238.27 | 233.48
2020-02-20 15:30 | 225.95 | 221.27
2020-02-20 16:00 | 226.15 | 221.73
2020-02-20 16:30 | 246.07 | 241.85
2020-02-20 17:00 | 270.67 | 266.76
2020-02-20 17:30 | 293.77 | 290.42
2020-02-20 18:00 | 301.73 | 299.15
2020-02-20 18:30 | 300.32 | 297.88
2020-02-20 19:00 | 306.82 | 304.4
2020-02-20 19:30 | 301.49 | 299.33
2020-02-20 20:00 | 293.26 | 291.83
2020-02-20 20:30 | 279.08 | 278.95
2020-02-20 21:00 | 261.14 | 261.08
2020-02-20 21:30 | 244.08 | 244.05
2020-02-20 22:00 | 230.8 | 230.76
2020-02-20 22:30 | 222.74 | 222.52
2020-02-20 23:00 | 211.64 | 211.06
2020-02-20 23:30 | 195.21 | 194.69
2020-02-21 | 167.18 | 167.13
2020-02-21 00:30 | 166.43 | 166.43
2020-02-21 01:00 | 159.03 | 159.03
2020-02-21 01:30 | 146.58 | 146.56
2020-02-21 02:00 | 146.29 | 146.25
2020-02-21 02:30 | 139.73 | 139.69
2020-02-21 03:00 | 137.58 | 137.54
2020-02-21 03:30 | 136.56 | 136.53
2020-02-21 04:00 | 137.96 | 137.95
2020-02-21 04:30 | 144.47 | 144.41
2020-02-21 05:00 | 148.96 | 148.91
2020-02-21 05:30 | 160.53 | 160.51
2020-02-21 06:00 | 168.94 | 168.92
2020-02-21 06:30 | 181.12 | 181.08
2020-02-21 07:00 | 192.07 | 191.76
2020-02-21 07:30 | 207.27 | 206.95
2020-02-21 08:00 | 208.83 | 208.19
2020-02-21 08:30 | 206.36 | 204.19
2020-02-21 09:00 | 206.54 | 204.4
2020-02-21 09:30 | 210.75 | 208.82
2020-02-21 10:00 | 215.88 | 213.7
2020-02-21 10:30 | 213.65 | 211.31
2020-02-21 11:00 | 211.94 | 209.25
2020-02-21 11:30 | 210.11 | 207.17
2020-02-21 12:00 | 217.87 | 215.17
2020-02-21 12:30 | 232.7 | 228.59
2020-02-21 13:00 | 241.01 | 231.94
2020-02-21 13:30 | 234.21 | 226.62
2020-02-21 14:00 | 237.46 | 233.32
2020-02-21 14:30 | 247.62 | 243.55
2020-02-21 15:00 | 233.24 | 229.42
2020-02-21 15:30 | 241.69 | 238.38
2020-02-21 16:00 | 252.43 | 249.53
2020-02-21 16:30 | 258.63 | 256.01
2020-02-21 17:00 | 262.34 | 260.14
2020-02-21 17:30 | 256.56 | 254.82
2020-02-21 18:00 | 258.8 | 257.91
2020-02-21 18:30 | 250.03 | 248.67
2020-02-21 19:00 | 252.4 | 251.15
2020-02-21 19:30 | 252.5 | 251.24
2020-02-21 20:00 | 249.59 | 248.35
2020-02-21 20:30 | 240.61 | 239.67
2020-02-21 21:00 | 229.04 | 228.92
2020-02-21 21:30 | 220.03 | 219.94
2020-02-21 22:00 | 207.76 | 207.69
2020-02-21 22:30 | 207.87 | 207.79
2020-02-21 23:00 | 204.69 | 204.62
2020-02-21 23:30 | 187.55 | 187.53
2020-02-22 | 170.34 | 170.33
2020-02-22 00:30 | 158.33 | 158.33
2020-02-22 01:00 | 149.41 | 149.41
2020-02-22 01:30 | 142.95 | 142.94
2020-02-22 02:00 | 138.99 | 138.99
2020-02-22 02:30 | 135.96 | 135.96
2020-02-22 03:00 | 133.48 | 133.48
2020-02-22 03:30 | 132.65 | 132.6
2020-02-22 04:00 | 131.69 | 131.63
2020-02-22 04:30 | 132.71 | 132.68
2020-02-22 05:00 | 133.76 | 133.72
2020-02-22 05:30 | 137.58 | 137.56
2020-02-22 06:00 | 140.89 | 140.87
2020-02-22 06:30 | 89.89 | 89.73
2020-02-22 07:00 | 87.17 | 87.12
2020-02-22 07:30 | 98.71 | 98.7
2020-02-22 08:00 | 97.75 | 97.54
2020-02-22 08:30 | 123.7 | 123.18
2020-02-22 09:00 | 141.65 | 140.46
2020-02-22 09:30 | 173.55 | 166.19
2020-02-22 10:00 | 186.55 | 179.67
2020-02-22 10:30 | 187.69 | 180.67
2020-02-22 11:00 | 169.34 | 162.75
2020-02-22 11:30 | 161.84 | 157.7
2020-02-22 12:00 | 169.98 | 166.05
2020-02-22 12:30 | 172.51 | 169.82
2020-02-22 13:00 | 169.36 | 166.97
2020-02-22 13:30 | 180.41 | 178.1
2020-02-22 14:00 | 184.47 | 182.47
2020-02-22 14:30 | 197.02 | 193.59
2020-02-22 15:00 | 191.51 | 186.11
2020-02-22 15:30 | 178.45 | 172.78
2020-02-22 16:00 | 185.12 | 179.8
2020-02-22 16:30 | 185.57 | 180.23
2020-02-22 17:00 | 198.71 | 193.48
2020-02-22 17:30 | 197.86 | 192.95
2020-02-22 18:00 | 199.89 | 195.21
2020-02-22 18:30 | 203.28 | 198.87
2020-02-22 19:00 | 220.21 | 215.17
2020-02-22 19:30 | 214.68 | 209.66
2020-02-22 20:00 | 204.7 | 199.9
2020-02-22 20:30 | 201.65 | 197.56
2020-02-22 21:00 | 185.48 | 183.32
2020-02-22 21:30 | 169.78 | 167.82
2020-02-22 22:00 | 152.09 | 150.32
2020-02-22 22:30 | 159.55 | 158.03
2020-02-22 23:00 | 166.49 | 165.26
2020-02-22 23:30 | 145.93 | 144.91
2020-02-23 | 124.69 | 123.8
2020-02-23 00:30 | 117.49 | 116.91
2020-02-23 01:00 | 106.68 | 106.35
2020-02-23 01:30 | 99.11 | 99.09
2020-02-23 02:00 | 101.32 | 100.95
2020-02-23 02:30 | 95.41 | 95.02
2020-02-23 03:00 | 95.31 | 94.91
2020-02-23 03:30 | 89.95 | 89.56
2020-02-23 04:00 | 82.13 | 81.71
2020-02-23 04:30 | 77.97 | 77.56
2020-02-23 05:00 | 74.39 | 73.96
2020-02-23 05:30 | 62.3 | 61.88
2020-02-23 06:00 | 56.77 | 56.4
2020-02-23 06:30 | 59.02 | 58.69
2020-02-23 07:00 | 61.6 | 61.38
2020-02-23 07:30 | 63.92 | 63.72
2020-02-23 08:00 | 63.62 | 63.6
2020-02-23 08:30 | 87.55 | 86.48
2020-02-23 09:00 | 102.43 | 100.82
2020-02-23 09:30 | 130.56 | 129.35
2020-02-23 10:00 | 143.93 | 143.1
2020-02-23 10:30 | 165.1 | 164.51
2020-02-23 11:00 | 176.33 | 175.65
2020-02-23 11:30 | 161.61 | 160.87
2020-02-23 12:00 | 168.68 | 168.1
2020-02-23 12:30 | 163.98 | 163.42
2020-02-23 13:00 | 147.08 | 146.56
2020-02-23 13:30 | 150.56 | 150.01
2020-02-23 14:00 | 149.21 | 148.51
2020-02-23 14:30 | 141.09 | 140.5
2020-02-23 15:00 | 123.96 | 123.34
2020-02-23 15:30 | 123.9 | 123.31
2020-02-23 16:00 | 139.03 | 138.54
2020-02-23 16:30 | 149.11 | 148.61
2020-02-23 17:00 | 158.15 | 157.73
2020-02-23 17:30 | 175.16 | 174.58
2020-02-23 18:00 | 189.45 | 188.86
2020-02-23 18:30 | 199.97 | 199.17
2020-02-23 19:00 | 222.21 | 221.1
2020-02-23 19:30 | 215.87 | 214.98
2020-02-23 20:00 | 204.3 | 203.67
2020-02-23 20:30 | 196.81 | 196.59
2020-02-23 21:00 | 174.02 | 173.96
2020-02-23 21:30 | 167.71 | 167.7
2020-02-23 22:00 | 150.7 | 150.7
2020-02-23 22:30 | 149.64 | 149.63
2020-02-23 23:00 | 150.2 | 150.18
2020-02-23 23:30 | 130.96 | 130.93
2020-02-24 | 103.68 | 103.57
2020-02-24 00:30 | 95.18 | 95.03
2020-02-24 01:00 | 81.5 | 81.3
2020-02-24 01:30 | 71.36 | 71.13
2020-02-24 02:00 | 61.64 | 61.4
2020-02-24 02:30 | 62.23 | 61.99
2020-02-24 03:00 | 63.02 | 62.72
2020-02-24 03:30 | 65.04 | 64.8
2020-02-24 04:00 | 64.59 | 64.39
2020-02-24 04:30 | 78.67 | 78.53
2020-02-24 05:00 | 87.52 | 87.44
2020-02-24 05:30 | 92.69 | 92.65
2020-02-24 06:00 | 96.56 | 96.52
2020-02-24 06:30 | 102.4 | 102.4
2020-02-24 07:00 | 119.73 | 119.7
2020-02-24 07:30 | 171.55 | 170.09
2020-02-24 08:00 | 184.87 | 180.94
2020-02-24 08:30 | 196.45 | 188.3
2020-02-24 09:00 | 193.64 | 185.3
2020-02-24 09:30 | 210.49 | 202.22
2020-02-24 10:00 | 232.63 | 224.43
2020-02-24 10:30 | 234.54 | 226.53
2020-02-24 11:00 | 227.44 | 219.29
2020-02-24 11:30 | 202.79 | 194.09
2020-02-24 12:00 | 172.21 | 162.61
2020-02-24 12:30 | 167.62 | 157.46
2020-02-24 13:00 | 147.89 | 136.52
2020-02-24 13:30 | 137.78 | 125.63
2020-02-24 14:00 | 133.19 | 121.03
2020-02-24 14:30 | 120.91 | 106.61
2020-02-24 15:00 | 120.81 | 106.91
2020-02-24 15:30 | 137.57 | 126.23
2020-02-24 16:00 | 162.14 | 153.57
2020-02-24 16:30 | 176.3 | 175.5
2020-02-24 17:00 | 183.31 | 182.61
2020-02-24 17:30 | 198.83 | 198.35
2020-02-24 18:00 | 197.74 | 197.36
2020-02-24 18:30 | 198.36 | 196.95
2020-02-24 19:00 | 219.52 | 217.38
2020-02-24 19:30 | 204.46 | 201.95
2020-02-24 20:00 | 191.73 | 189.34
2020-02-24 20:30 | 174.76 | 172.95
2020-02-24 21:00 | 161.26 | 159.03
2020-02-24 21:30 | 156.33 | 154.01
2020-02-24 22:00 | 149.9 | 148.45
2020-02-24 22:30 | 149.77 | 149.7
2020-02-24 23:00 | 152.15 | 152.06
2020-02-24 23:30 | 125.64 | 125.47
2020-02-25 | 99.46 | 99.2
2020-02-25 00:30 | 89.67 | 89.63
2020-02-25 01:00 | 75.82 | 75.8
2020-02-25 01:30 | 71.51 | 68.91
2020-02-25 02:00 | 67.44 | 64.26
2020-02-25 02:30 | 63.71 | 60.09
2020-02-25 03:00 | 60.67 | 57.18
2020-02-25 03:30 | 59.52 | 55.81
2020-02-25 04:00 | 72.49 | 69.31
2020-02-25 04:30 | 72.37 | 69.05
2020-02-25 05:00 | 75.71 | 72.81
2020-02-25 05:30 | 83.49 | 81.25
2020-02-25 06:00 | 91.08 | 89.13
2020-02-25 06:30 | 85.95 | 83.37
2020-02-25 07:00 | 92.81 | 91.62
2020-02-25 07:30 | 121.15 | 120.07
2020-02-25 08:00 | 122.31 | 120.86
2020-02-25 08:30 | 101.23 | 100.03
2020-02-25 09:00 | 98.68 | 97.68
2020-02-25 09:30 | 112.64 | 111.58
2020-02-25 10:00 | 109.65 | 108.15
2020-02-25 10:30 | 117.14 | 115.91
2020-02-25 11:00 | 110.46 | 109.11
2020-02-25 11:30 | 107.33 | 105.68
2020-02-25 12:00 | 130.84 | 128.88
2020-02-25 12:30 | 189.8 | 187.32
2020-02-25 13:00 | 202.37 | 199.57
2020-02-25 13:30 | 196.59 | 192.03
2020-02-25 14:00 | 186.78 | 182.1
2020-02-25 14:30 | 185.27 | 180.16
2020-02-25 15:00 | 187.45 | 182.55
2020-02-25 15:30 | 197.28 | 193.11
2020-02-25 16:00 | 201.28 | 196.62
2020-02-25 16:30 | 201.77 | 196.77
2020-02-25 17:00 | 203.83 | 198.71
2020-02-25 17:30 | 203.04 | 197.55
2020-02-25 18:00 | 203.51 | 197.43
2020-02-25 18:30 | 210.02 | 198.88
2020-02-25 19:00 | 218.34 | 206.98
2020-02-25 19:30 | 217.75 | 205.9
2020-02-25 20:00 | 205.97 | 201.93
2020-02-25 20:30 | 196.72 | 194.31
2020-02-25 21:00 | 184.91 | 182.37
2020-02-25 21:30 | 176.83 | 174.15
2020-02-25 22:00 | 174.06 | 171
2020-02-25 22:30 | 162.36 | 159.38
2020-02-25 23:00 | 155.65 | 155.24
2020-02-25 23:30 | 142.48 | 142.13
2020-02-26 | 127.22 | 126.77
2020-02-26 00:30 | 118.23 | 117.53
2020-02-26 01:00 | 118.8 | 118.17
2020-02-26 01:30 | 121.49 | 120.94
2020-02-26 02:00 | 120.44 | 119.91
2020-02-26 02:30 | 120.35 | 119.79
2020-02-26 03:00 | 120.24 | 119.71
2020-02-26 03:30 | 119.83 | 119.15
2020-02-26 04:00 | 119.48 | 118.62
2020-02-26 04:30 | 119.86 | 118.81
2020-02-26 05:00 | 122.31 | 121.22
2020-02-26 05:30 | 124.6 | 123.65
2020-02-26 06:00 | 131.85 | 130.84
2020-02-26 06:30 | 144.77 | 144.06
2020-02-26 07:00 | 154.31 | 153.6
2020-02-26 07:30 | 170.49 | 166.25
2020-02-26 08:00 | 187.38 | 174.71
2020-02-26 08:30 | 190.36 | 175.8
2020-02-26 09:00 | 198.08 | 182.43
2020-02-26 09:30 | 202.36 | 185.7
2020-02-26 10:00 | 202.92 | 194.24
2020-02-26 10:30 | 199.7 | 191.98
2020-02-26 11:00 | 209.07 | 200.96
2020-02-26 11:30 | 220.36 | 212.1
2020-02-26 12:00 | 213.55 | 204.87
2020-02-26 12:30 | 202.97 | 193.31
2020-02-26 13:00 | 202.84 | 192.73
2020-02-26 13:30 | 204.49 | 193.78
2020-02-26 14:00 | 204.68 | 193.71
2020-02-26 14:30 | 212.94 | 201.82
2020-02-26 15:00 | 219.3 | 207.58
2020-02-26 15:30 | 227.19 | 215.65
2020-02-26 16:00 | 225.96 | 214.86
2020-02-26 16:30 | 224.71 | 214.38
2020-02-26 17:00 | 223.59 | 216.95
2020-02-26 17:30 | 217.42 | 214.85
2020-02-26 18:00 | 216.76 | 213.56
2020-02-26 18:30 | 222.3 | 218.43
2020-02-26 19:00 | 230.12 | 225.61
2020-02-26 19:30 | 226.91 | 222.12
2020-02-26 20:00 | 223.2 | 218.92
2020-02-26 20:30 | 213.89 | 209.87
2020-02-26 21:00 | 205.09 | 197.69
2020-02-26 21:30 | 191.6 | 189.19
2020-02-26 22:00 | 185.27 | 182.57
2020-02-26 22:30 | 169.43 | 168.4
2020-02-26 23:00 | 163.93 | 163.41
2020-02-26 23:30 | 149.85 | 149.57
2020-02-27 | 133.7 | 133.46
2020-02-27 00:30 | 123.24 | 122.98
2020-02-27 01:00 | 123.76 | 123.62
2020-02-27 01:30 | 124.74 | 124.56
2020-02-27 02:00 | 122.93 | 122.9
2020-02-27 02:30 | 120.59 | 120.56
2020-02-27 03:00 | 119.34 | 119.31
2020-02-27 03:30 | 118.44 | 118.39
2020-02-27 04:00 | 117.48 | 117.42
2020-02-27 04:30 | 117.78 | 117.72
2020-02-27 05:00 | 118.74 | 118.67
2020-02-27 05:30 | 121.86 | 121.77
2020-02-27 06:00 | 123.97 | 123.82
2020-02-27 06:30 | 132.82 | 132.58
2020-02-27 07:00 | 153.66 | 148.28
2020-02-27 07:30 | 177.52 | 170.63
2020-02-27 08:00 | 192.13 | 184.56
2020-02-27 08:30 | 189.53 | 180.87
2020-02-27 09:00 | 175.07 | 168.98
2020-02-27 09:30 | 169.12 | 164.86
2020-02-27 10:00 | 169.39 | 164.93
2020-02-27 10:30 | 178.57 | 173.88
2020-02-27 11:00 | 172.37 | 167.62
2020-02-27 11:30 | 174.7 | 169.82
2020-02-27 12:00 | 178.49 | 173.29
2020-02-27 12:30 | 188.55 | 184.68
2020-02-27 13:00 | 184.95 | 181.65
2020-02-27 13:30 | 169.59 | 166.9
2020-02-27 14:00 | 196.31 | 193.09
2020-02-27 14:30 | 198.34 | 194.66
2020-02-27 15:00 | 175.8 | 172.46
2020-02-27 15:30 | 187.92 | 184.69
2020-02-27 16:00 | 177.17 | 174
2020-02-27 16:30 | 175.66 | 172.93
2020-02-27 17:00 | 189.52 | 186.99
2020-02-27 17:30 | 185.32 | 183.09
2020-02-27 18:00 | 180.24 | 178.42
2020-02-27 18:30 | 180.25 | 178.59
2020-02-27 19:00 | 186.46 | 184.56
2020-02-27 19:30 | 185.43 | 183.65
2020-02-27 20:00 | 183.64 | 181.81
2020-02-27 20:30 | 180.45 | 178.39
2020-02-27 21:00 | 169.18 | 167.47
2020-02-27 21:30 | 162.9 | 160.69
2020-02-27 22:00 | 157.02 | 153.92
2020-02-27 22:30 | 144.99 | 142.12
2020-02-27 23:00 | 139.68 | 138.68
2020-02-27 23:30 | 126.41 | 126.4
2020-02-28 | 111.78 | 111.77
2020-02-28 00:30 | 102.78 | 102.76
2020-02-28 01:00 | 105.17 | 105.16
2020-02-28 01:30 | 108.14 | 108.11
2020-02-28 02:00 | 107.79 | 107.75
2020-02-28 02:30 | 105.95 | 105.91
2020-02-28 03:00 | 102.32 | 102.27
2020-02-28 03:30 | 102.65 | 102.6
2020-02-28 04:00 | 101.28 | 101.23
2020-02-28 04:30 | 101.08 | 101.01
2020-02-28 05:00 | 102.37 | 102.32
2020-02-28 05:30 | 105.68 | 105.64
2020-02-28 06:00 | 110.75 | 110.7
2020-02-28 06:30 | 123.2 | 123.02
2020-02-28 07:00 | 137.49 | 137.16
2020-02-28 07:30 | 147.3 | 146.7
2020-02-28 08:00 | 155.57 | 152.34
2020-02-28 08:30 | 155.26 | 152.18
2020-02-28 09:00 | 158.92 | 155.77
2020-02-28 09:30 | 156.01 | 152.66
2020-02-28 10:00 | 148.79 | 146.41
2020-02-28 10:30 | 158.41 | 155.32
2020-02-28 11:00 | 169.45 | 165.6
2020-02-28 11:30 | 173.47 | 169.7
2020-02-28 12:00 | 175.28 | 171.54
2020-02-28 12:30 | 179.07 | 175.34
2020-02-28 13:00 | 187.72 | 183.92
2020-02-28 13:30 | 223.2 | 219.03
2020-02-28 14:00 | 221.32 | 219.19
2020-02-28 14:30 | 212.4 | 210.04
2020-02-28 15:00 | 201.22 | 199.14
2020-02-28 15:30 | 204.76 | 202.64
2020-02-28 16:00 | 199.28 | 196.73
2020-02-28 16:30 | 193.59 | 190.75
2020-02-28 17:00 | 193.26 | 189.96
2020-02-28 17:30 | 192.64 | 189.21
2020-02-28 18:00 | 191.29 | 187.98
2020-02-28 18:30 | 190.68 | 187.33
2020-02-28 19:00 | 197.64 | 194.63
2020-02-28 19:30 | 200.04 | 197.3
2020-02-28 20:00 | 200.84 | 198.1
2020-02-28 20:30 | 195.24 | 192.64
2020-02-28 21:00 | 182.87 | 181.21
2020-02-28 21:30 | 172.4 | 172.03
2020-02-28 22:00 | 166.32 | 166.18
2020-02-28 22:30 | 155.51 | 155.2
2020-02-28 23:00 | 151.58 | 151.24
2020-02-28 23:30 | 139.39 | 138.9
2020-02-29 | 128.89 | 128.48
2020-02-29 00:30 | 117.31 | 117.22
2020-02-29 01:00 | 115.45 | 115.37
2020-02-29 01:30 | 119.71 | 119.62
2020-02-29 02:00 | 115.42 | 115.39
2020-02-29 02:30 | 112.88 | 112.85
2020-02-29 03:00 | 110.65 | 110.61
2020-02-29 03:30 | 111.74 | 111.69
2020-02-29 04:00 | 110.5 | 110.45
2020-02-29 04:30 | 109.47 | 109.4
2020-02-29 05:00 | 109.13 | 109.07
2020-02-29 05:30 | 108.56 | 108.47
2020-02-29 06:00 | 108.22 | 108.09
2020-02-29 06:30 | 109.56 | 109.45
2020-02-29 07:00 | 113.98 | 113.88
2020-02-29 07:30 | 125.84 | 125.74
2020-02-29 08:00 | 128.38 | 128.1
2020-02-29 08:30 | 130.86 | 130.34
2020-02-29 09:00 | 132.15 | 131.37
2020-02-29 09:30 | 135.52 | 134.48
2020-02-29 10:00 | 145 | 143.61
2020-02-29 10:30 | 158.49 | 156.81
2020-02-29 11:00 | 145.85 | 143.67
2020-02-29 11:30 | 139.26 | 136.56
2020-02-29 12:00 | 169.2 | 167.31
2020-02-29 12:30 | 209.36 | 207.02
2020-02-29 13:00 | 200.46 | 196.63
2020-02-29 13:30 | 191.17 | 187.66
2020-02-29 14:00 | 173.76 | 170.16
2020-02-29 14:30 | 164.3 | 160.42
2020-02-29 15:00 | 168.64 | 164.64
2020-02-29 15:30 | 173.74 | 169.36
2020-02-29 16:00 | 173.39 | 169.18
2020-02-29 16:30 | 177.87 | 173.68
2020-02-29 17:00 | 175.12 | 170.81
2020-02-29 17:30 | 171.96 | 167.9
2020-02-29 18:00 | 169.49 | 165.95
2020-02-29 18:30 | 169.27 | 166.21
2020-02-29 19:00 | 175.69 | 172.36
2020-02-29 19:30 | 173.51 | 170.53
2020-02-29 20:00 | 169.74 | 167.32
2020-02-29 20:30 | 161.47 | 160.52
2020-02-29 21:00 | 153.08 | 152
2020-02-29 21:30 | 150.1 | 149.2
2020-02-29 22:00 | 147.75 | 147.46
2020-02-29 22:30 | 144.43 | 144.39
2020-02-29 23:00 | 144.63 | 144.62
2020-02-29 23:30 | 132.92 | 132.92
2020-03-01 | 119.77 | 119.77
Formulas:
Date/Time = [Date/Time, row above]+30/24/60

## 24. Historic ratings
PQ Rating (MVA) |  | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer | 2019 Winter | 2019/20 Summer
|  | 750 | 500 | 500 | 500 | 500 | 800
Transformers | H004T01 | 250 | 250 | 250 | 250 | 250 | 250
| H004T02 | 250
| H004T03 | 250 | 250 | 250 | 250 | 250 | 250
| H004T05 | [5 empty] | 300

## 26. Unplanned outages
Unplanned Outage Date/Time | Element Affected | Element Type | Outage Cause | Outage Duration (mins) | Customer Outage Duration (mins) | MW Lost (Instantaneous) | MW Minutes
2017-03-03 11:24 | 0835 - S003 Greenbank to H004 Mudgeeraba | FEEDER | HV Maint | 192.5833
2017-03-29 08:40 | 0758 - H004 Mudgeeraba to T174 Terranora | FEEDER | Human Error | 15.4333 | 15.43 | 35 | 540.17
2017-10-24 15:12 | 0757 - H004 Mudgeeraba to T174 Terranora | FEEDER | HV Equipment malfunction or failure | 24.6333 | 31.37 | 85 | 2403.58
2017-10-24 15:12 | 0758 - H004 Mudgeeraba to T174 Terranora | FEEDER | HV Equipment malfunction or failure | 24.6333
2017-10-24 15:12 | H004 110KV 2 CAPACITOR | CAPACITOR | HV Equipment malfunction or failure | 127.8833
2017-10-24 15:12 | H004 110KV 4 TRANSFORMER | TRANSFORMER | HV Equipment malfunction or failure | 31.6167
2017-10-24 15:12 | H004 275KV 3 TRANSFORMER | TRANSFORMER | HV Equipment malfunction or failure | 21.6833
2017-10-24 15:12 | H004 275KV 5 TRANSFORMER | TRANSFORMER | HV Equipment malfunction or failure | 22.0667
2018-02-01 10:04 | H004 275KV 1 TRANSFORMER | TRANSFORMER | Secondary system malfunction or failure | 25.6833
2018-02-16 07:41 | 0758 - H004 Mudgeeraba to T174 Terranora | FEEDER | HV Maint | 365.8833
2019-02-13 15:18 | H004 275KV 4 CAPACITOR | CAPACITOR | HV Maint | 537250.4533
2019-03-15 18:26 | 0758 - H004 Mudgeeraba to T174 Terranora | FEEDER | Storm | 0.23333
2019-10-23 07:58 | H004 275KV 1 TRANSFORMER | TRANSFORMER | HV equipt maintenance | 1654.05