## Cover Page
AER Rule | Field Name | Value(s)
1 | Constrained connection point ID | Redbank Plains
2 | Constraint primary driver | Asset condition
3 | Constraint investment type | Asset renewal
4 | Constrained connection point latitude (decimal degrees) | -27.641
| Constrained connection point longitude (decimal degrees) | 152.851
5 | Affect on residential customers
| Annual Energy | Not available
| Maximum Demand | Not available
6,7 | Effect on industrial and commercial customers
| Annual Energy | Not available
| Maximum Demand | Not available
8 | Load profile (maximum day, MVA)
50% PoE
Load profile (minimum day, MVA)
Minimum demand data (MVA)
| Max. demand, maximum demand day (MVA) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| 10% PoE | 33.2757 | 33.788 | 33.9473 | 34.4218 | 35.159 | 35.9713 | 36.5751 | 37.3431 | 38.1111 | 38.8948 | 41.6923
| 50% PoE | 27.2 | 27.6 | 27.7 | 28.1 | 28.7 | 29.4 | 29.8 | 30.5 | 31.1 | 31.7 | 33.98
9 | Max. demand, minimum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Maximum demand data | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 13.406
10 | Load profile (maximum day, MW)
Load profile 50%
| Max. demand, maximum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| 10% PoE | 31.7091 | 32.1973 | 32.3491 | 32.8012 | 33.5037 | 34.2778 | 34.8531 | 35.585 | 36.3168 | 37.0637 | 41.6243
| 50% PoE | 25.9 | 26.3 | 26.4 | 26.8 | 27.3 | 28 | 28.4 | 29 | 29.6 | 30.2 | 33.916
11 | Load profile (minimum day, MW)
Minimum demand data (MW)
| Min. demand, minimum demand day (MW) | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Mininum demand data | -0.3 | -1.1 | -1.8 | -2.5 | -3.1 | -4 | -5 | -6 | -7 | -8 | -4.832
12 | Voltage Level (kV) | 110/11
13 | Maximum load at risk per year | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Load at risk (MW, peak) | 0 | 0 | 0 | 28.8995 | 28.8995 | 29.5713 | 30.0803 | 30.728 | 31.3849 | 32.7374 | 33.3898
| Load at risk (MVA, peak) | 0 | 0 | 0 | 32.1105 | 32.1105 | 32.857 | 33.4225 | 34.1422 | 34.8721 | 36.3749 | 37.0997
14 | Load duration curve
15 | Preferred investment | Redbank Plains 110kV primary plant and 110_11kV transformer reinvestments
16 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Capital cost ($m, nominal) |  |  |  | 8
17 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Operating cost ($m, nominal) |  |  |  | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16
18 | Preferred investment cost accuracy | 0.3
19 | Preferred investment proposed timing | 2024-06-30
20 | Demand reduction to defer the investment by 1 year
21 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Annual deferral value ($m, nominal)
22 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Load transfer capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Historic load trace
24 | Historic ratings
25 | Limitation asset | Primary plant, 110/11kV transformer
26 | Unplanned outages
27 | Maximum fault level (kA) | 20.7
28 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Economic cost ($m) | 0 | 0 | 0 | 2.7803 | 2.7826 | 2.7848 | 5.925 | 5.935 | 5.9486 | 5.972 | 5.9795
29 | VCR ($m/MWh) | 0.04003
30 |  | Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
| Annual unserved energy (MWh) | 0 | 0 | 0 | 69.4565 | 69.5122 | 69.5679 | 148.0133 | 148.2626 | 148.6044 | 149.1882 | 149.3759

## 8. Load profile max (50% PoE)
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:30 | 10.5 | 10.5 | 10.5 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 10.3 | 7.008
1:00 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9.8 | 6.672
1:30 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.4 | 6.34
2:00 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 8.9 | 6.066
2:30 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.6 | 5.91
3:00 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.3 | 5.768
3:30 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.4 | 8.2 | 5.658
4:00 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8 | 5.548
4:30 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 7.9 | 5.604
5:00 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.1 | 5.498
5:30 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.1 | 5.55
6:00 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.5 | 5.574
6:30 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.1 | 5.188
7:00 | 9.5 | 9.5 | 9.4 | 9.4 | 9.4 | 9.3 | 9.2 | 9.1 | 9.1 | 8.8 | 4.982
7:30 | 9.7 | 9.6 | 9.5 | 9.3 | 9.3 | 9.1 | 8.9 | 8.8 | 8.6 | 8.3 | 5.156
8:00 | 9.8 | 9.5 | 9.3 | 9.1 | 9 | 8.7 | 8.4 | 8.2 | 7.9 | 7.4 | 4.854
8:30 | 9.9 | 9.5 | 9.2 | 8.8 | 8.6 | 8.1 | 7.6 | 7.1 | 6.7 | 6.1 | 2.428
9:00 | 10.2 | 9.7 | 9.3 | 8.9 | 8.5 | 8 | 7.3 | 6.7 | 6.1 | 5.4 | 2.734
9:30 | 10.7 | 10.1 | 9.6 | 9 | 8.6 | 7.9 | 7.1 | 6.4 | 5.7 | 4.9 | 2.596
10:00 | 10.4 | 9.8 | 9.2 | 8.6 | 8.1 | 7.3 | 6.5 | 5.6 | 4.8 | 3.8 | 2.492
10:30 | 11.2 | 10.5 | 9.8 | 9.1 | 8.6 | 7.7 | 6.8 | 5.8 | 4.9 | 3.8 | 2.868
11:00 | 11.8 | 11.1 | 10.4 | 9.7 | 9 | 8.2 | 7.1 | 6.1 | 5.1 | 4.1 | 3.464
11:30 | 13 | 12.2 | 11.5 | 10.8 | 10.1 | 9.2 | 8.2 | 7.1 | 6.1 | 4.9 | 4.526
12:00 | 14.1 | 13.4 | 12.6 | 11.9 | 11.2 | 10.3 | 9.2 | 8.1 | 7.1 | 5.8 | 5.146
12:30 | 15.6 | 14.8 | 14.1 | 13.4 | 12.7 | 11.8 | 10.8 | 9.7 | 8.7 | 7.5 | 5.312
13:00 | 16.5 | 15.8 | 15.1 | 14.4 | 13.8 | 13 | 12 | 11 | 10 | 8.8 | 6.296
13:30 | 17.4 | 16.7 | 16.1 | 15.4 | 14.8 | 14 | 13.1 | 12.1 | 11.2 | 10 | 7.982
14:00 | 18.2 | 17.5 | 16.9 | 16.3 | 15.7 | 14.9 | 14 | 13.1 | 12.2 | 10.9 | 8.282
14:30 | 18.9 | 18.3 | 17.7 | 17.1 | 16.6 | 15.9 | 15.1 | 14.2 | 13.4 | 12.3 | 9.462
15:00 | 20 | 19.4 | 18.9 | 18.4 | 17.9 | 17.3 | 16.5 | 15.7 | 15 | 13.9 | 11.524
15:30 | 21.9 | 21.5 | 21 | 20.5 | 20.1 | 19.6 | 18.9 | 18.3 | 17.6 | 16.6 | 13.37
16:00 | 23.1 | 22.7 | 22.3 | 21.9 | 21.6 | 21.2 | 20.7 | 20.1 | 19.6 | 18.9 | 21.618
16:30 | 24.8 | 24.5 | 24.3 | 24 | 23.7 | 23.4 | 23 | 22.6 | 22.5 | 22.6 | 27.448
17:00 | 26 | 25.8 | 25.6 | 25.4 | 25.2 | 25 | 25 | 25.2 | 25.3 | 25.5 | 31.026
17:30 | 26.9 | 27.1 | 27 | 26.8 | 27 | 27.4 | 27.5 | 27.9 | 28.2 | 28.5 | 33.98
18:00 | 27.1 | 27.4 | 27.4 | 27.4 | 27.9 | 28.4 | 28.8 | 29.3 | 29.7 | 30.2 | 30.37
18:30 | 27.2 | 27.6 | 27.7 | 28.1 | 28.7 | 29.4 | 29.8 | 30.5 | 31.1 | 31.7 | 23.132
19:00 | 27 | 27.3 | 27.3 | 27.3 | 27.8 | 28.5 | 29 | 29.6 | 30.2 | 30.8 | 22.688
19:30 | 27 | 27.2 | 27.2 | 27.3 | 27.8 | 28.5 | 29 | 29.6 | 30.2 | 30.8 | 22.592
20:00 | 26.3 | 26.3 | 26.3 | 26.3 | 26.4 | 27 | 27.5 | 28.1 | 28.7 | 29.3 | 20.006
20:30 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | 26.1 | 26.6 | 27.2 | 27.8 | 28.4 | 21.608
21:00 | 24.3 | 24.3 | 24.3 | 24.4 | 24.4 | 24.4 | 24.5 | 25.1 | 25.7 | 26.3 | 19.47
21:30 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.7 | 22.6 | 22.6 | 23.2 | 23.7 | 18.098
22:00 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.8 | 15.326
22:30 | 17.8 | 17.8 | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | 17.5 | 12.868
23:00 | 16.4 | 16.4 | 16.4 | 16.4 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.1 | 11.542
23:30 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.8 | 14.5 | 10.526
0:00 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.1 | 8.04

## 8. Load profile min
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:30 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 6.122
1:00 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6.334
1:30 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 5.394
2:00 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 5.122
2:30 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 5.056
3:00 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.894
3:30 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 5.062
4:00 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 5.126
4:30 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 5.38
5:00 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 6.252
5:30 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 7.08
6:00 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 7.592
6:30 | 5.2 | 5.2 | 5.1 | 5.1 | 5.1 | 5.1 | 5 | 5 | 5 | 4.9 | 9.73
7:00 | 4.7 | 4.6 | 4.5 | 4.4 | 4.3 | 4.2 | 4.1 | 4 | 3.8 | 3.7 | 11.142
7:30 | 4 | 3.8 | 3.6 | 3.4 | 3.3 | 3 | 2.8 | 2.5 | 2.3 | 2 | 11.83
8:00 | 3 | 2.7 | 2.5 | 2.2 | 1.9 | 1.6 | 1.2 | 0.8 | 0.5 | 0 | 9.634
8:30 | 2.2 | 1.8 | 1.4 | 1 | 0.6 | 0.1 | -0.4 | -1 | -1.5 | -2.1 | 5.886
9:00 | 1.5 | 1 | 0.5 | 0 | -0.4 | -1 | -1.7 | -2.4 | -3.1 | -3.7 | 3.718
9:30 | 0.9 | 0.3 | -0.3 | -0.8 | -1.3 | -2 | -2.8 | -3.6 | -4.4 | -5.1 | 2.068
10:00 | 0.5 | -0.2 | -0.8 | -1.4 | -2 | -2.8 | -3.7 | -4.6 | -5.4 | -6.3 | 0.042
10:30 | -0.1 | -0.8 | -1.5 | -2.2 | -2.8 | -3.6 | -4.6 | -5.6 | -6.5 | -7.6 | 1.294
11:00 | -0.3 | -1 | -1.7 | -2.4 | -3 | -3.9 | -4.9 | -5.9 | -6.8 | -7.8 | 2.136
11:30 | -0.3 | -1.1 | -1.8 | -2.5 | -3.2 | -4.1 | -5.1 | -6.1 | -7.1 | -8.1 | 3.522
12:00 | -0.3 | -1 | -1.7 | -2.5 | -3.1 | -4 | -5 | -6 | -7 | -8.1 | 3.012
12:30 | -0.2 | -0.9 | -1.6 | -2.3 | -2.9 | -3.7 | -4.7 | -5.7 | -6.6 | -7.7 | 0.002
13:00 | 0 | -0.7 | -1.4 | -2.1 | -2.7 | -3.6 | -4.5 | -5.5 | -6.5 | -7.5 | 0.914
13:30 | 0.4 | -0.3 | -1 | -1.6 | -2.2 | -3 | -4 | -4.9 | -5.8 | -6.8 | 1.222
14:00 | 0.9 | 0.3 | -0.3 | -1 | -1.5 | -2.3 | -3.2 | -4.1 | -4.9 | -5.9 | 0.37
14:30 | 1.5 | 0.9 | 0.4 | -0.2 | -0.7 | -1.4 | -2.2 | -3 | -3.8 | -4.6 | 0.162
15:00 | 2.2 | 1.7 | 1.2 | 0.7 | 0.3 | -0.4 | -1.1 | -1.8 | -2.5 | -3.2 | 1.478
15:30 | 3.3 | 2.9 | 2.5 | 2.1 | 1.7 | 1.2 | 0.6 | 0 | -0.5 | -1.1 | 1.762
16:00 | 4.4 | 4.1 | 3.7 | 3.4 | 3.1 | 2.7 | 2.3 | 1.9 | 1.4 | 1 | 3.278
16:30 | 5.8 | 5.6 | 5.4 | 5.1 | 4.9 | 4.7 | 4.4 | 4.1 | 3.9 | 3.6 | 5.988
17:00 | 7.1 | 7 | 6.9 | 6.7 | 6.6 | 6.5 | 6.3 | 6.1 | 6 | 5.8 | 7.182
17:30 | 8.3 | 8.3 | 8.2 | 8.2 | 8.1 | 8.1 | 8 | 8 | 7.9 | 7.9 | 10.198
18:00 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.5 | 12.14
18:30 | 10.7 | 10.7 | 10.7 | 10.7 | 10.6 | 10.6 | 10.7 | 10.7 | 10.7 | 10.7 | 13.134
19:00 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 13.406
19:30 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 12.828
20:00 | 10.8 | 10.8 | 10.8 | 10.8 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 12.81
20:30 | 10.5 | 10.5 | 10.5 | 10.5 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 12.926
21:00 | 10 | 10 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.8 | 12.27
21:30 | 9.3 | 9.3 | 9.3 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 11.236
22:00 | 8.6 | 8.6 | 8.6 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 11.108
22:30 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9.392
23:00 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 9
23:30 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 8.086
0:00 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.906

## 10. Load profile (50% PoE)
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:30 | 10.1 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 9.9 | 6.994
1:00 | 9.6 | 9.6 | 9.6 | 9.6 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.4 | 6.66
1:30 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9 | 6.328
2:00 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.6 | 6.054
2:30 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.3 | 5.898
3:00 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8 | 5.758
3:30 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 7.9 | 5.648
4:00 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.7 | 5.538
4:30 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.7 | 5.594
5:00 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.8 | 5.488
5:30 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7.8 | 5.54
6:00 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.2 | 5.564
6:30 | 8.8 | 8.8 | 8.8 | 8.8 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 8.7 | 5.178
7:00 | 9.2 | 9.1 | 9.1 | 9 | 9 | 9 | 8.9 | 8.8 | 8.8 | 8.5 | 4.972
7:30 | 9.3 | 9.2 | 9.1 | 9 | 8.9 | 8.8 | 8.6 | 8.4 | 8.3 | 8 | 5.146
8:00 | 9.4 | 9.2 | 9 | 8.8 | 8.6 | 8.4 | 8.1 | 7.8 | 7.6 | 7.1 | 4.844
8:30 | 9.5 | 9.1 | 8.8 | 8.5 | 8.2 | 7.8 | 7.3 | 6.8 | 6.4 | 5.8 | 2.424
9:00 | 9.8 | 9.3 | 8.9 | 8.5 | 8.2 | 7.6 | 7 | 6.4 | 5.8 | 5.2 | 2.728
9:30 | 10.2 | 9.6 | 9.1 | 8.6 | 8.2 | 7.6 | 6.8 | 6.1 | 5.4 | 4.7 | 2.592
10:00 | 10 | 9.4 | 8.8 | 8.2 | 7.7 | 7 | 6.2 | 5.3 | 4.5 | 3.6 | 2.488
10:30 | 10.6 | 10 | 9.3 | 8.7 | 8.2 | 7.4 | 6.4 | 5.5 | 4.7 | 3.6 | 2.862
11:00 | 11.3 | 10.6 | 9.9 | 9.2 | 8.6 | 7.8 | 6.8 | 5.8 | 4.9 | 3.9 | 3.458
11:30 | 12.3 | 11.6 | 10.9 | 10.2 | 9.6 | 8.8 | 7.8 | 6.8 | 5.8 | 4.7 | 4.518
12:00 | 13.5 | 12.7 | 12 | 11.3 | 10.7 | 9.8 | 8.7 | 7.7 | 6.7 | 5.5 | 5.136
12:30 | 14.8 | 14.1 | 13.4 | 12.7 | 12.1 | 11.3 | 10.3 | 9.2 | 8.3 | 7.1 | 5.302
13:00 | 15.7 | 15 | 14.3 | 13.7 | 13.1 | 12.3 | 11.4 | 10.4 | 9.5 | 8.4 | 6.284
13:30 | 16.6 | 15.9 | 15.3 | 14.7 | 14.1 | 13.3 | 12.4 | 11.5 | 10.7 | 9.5 | 7.966
14:00 | 17.3 | 16.7 | 16.1 | 15.5 | 15 | 14.2 | 13.3 | 12.4 | 11.6 | 10.4 | 8.266
14:30 | 17.9 | 17.4 | 16.8 | 16.3 | 15.8 | 15.1 | 14.3 | 13.5 | 12.8 | 11.7 | 9.444
15:00 | 19 | 18.5 | 18 | 17.5 | 17.1 | 16.4 | 15.7 | 15 | 14.3 | 13.3 | 11.502
15:30 | 20.9 | 20.4 | 20 | 19.6 | 19.2 | 18.6 | 18 | 17.4 | 16.8 | 15.8 | 13.344
16:00 | 22 | 21.6 | 21.3 | 20.9 | 20.6 | 20.2 | 19.7 | 19.2 | 18.7 | 18.1 | 21.578
16:30 | 23.7 | 23.4 | 23.1 | 22.9 | 22.6 | 22.3 | 21.9 | 21.5 | 21.5 | 21.6 | 27.396
17:00 | 24.8 | 24.6 | 24.4 | 24.2 | 24.1 | 23.8 | 23.8 | 24 | 24.2 | 24.4 | 30.968
17:30 | 25.7 | 25.8 | 25.7 | 25.6 | 25.7 | 26.1 | 26.3 | 26.6 | 26.9 | 27.2 | 33.916
18:00 | 25.8 | 26.2 | 26.2 | 26.1 | 26.6 | 27.1 | 27.5 | 27.9 | 28.4 | 28.9 | 30.312
18:30 | 25.9 | 26.3 | 26.4 | 26.8 | 27.3 | 28 | 28.4 | 29 | 29.6 | 30.2 | 23.088
19:00 | 25.7 | 26 | 26 | 26 | 26.5 | 27.1 | 27.6 | 28.2 | 28.7 | 29.3 | 22.646
19:30 | 25.7 | 25.9 | 25.9 | 25.9 | 26.5 | 27.1 | 27.6 | 28.2 | 28.7 | 29.3 | 22.55
20:00 | 25.1 | 25.1 | 25.1 | 25.1 | 25.2 | 25.8 | 26.3 | 26.8 | 27.4 | 28 | 19.968
20:30 | 24.5 | 24.5 | 24.5 | 24.6 | 24.6 | 24.9 | 25.4 | 26 | 26.5 | 27.1 | 21.568
21:00 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.4 | 24 | 24.6 | 25.1 | 19.434
21:30 | 21.6 | 21.6 | 21.6 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 22.2 | 22.6 | 18.064
22:00 | 19.6 | 19.6 | 19.6 | 19.6 | 19.7 | 19.7 | 19.6 | 19.6 | 19.6 | 19.9 | 15.298
22:30 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 16.8 | 12.844
23:00 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 15.5 | 11.52
23:30 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 13.9 | 10.506
0:00 | 12.8 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.6 | 8.024

## 11. Load profile min
| Year 0 (FY 2021) | Year 1 (FY 2022) | Year 2 (FY 2023) | Year 3 (FY 2024) | Year 4 (FY 2025) | Year 5 (FY 2026) | Year 6 (FY 2027) | Year 7 (FY 2028) | Year 8 (FY 2029) | Year 9 (FY 2030) | Year 10 (FY 2031)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:30 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.724
1:00 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4.9 | 4.9 | 5.134
1:30 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.6 | 4.6 | 4.776
2:00 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.516
2:30 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.508
3:00 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.534
3:30 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 5.348
4:00 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 5.43
4:30 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 5.772
5:00 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 6.36
5:30 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 6.26
6:00 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 6.452
6:30 | 5.1 | 5.1 | 5 | 5 | 5 | 4.9 | 4.9 | 4.9 | 4.8 | 4.8 | 7.95
7:00 | 4.6 | 4.5 | 4.4 | 4.3 | 4.2 | 4.1 | 4 | 3.9 | 3.8 | 3.6 | 8.142
7:30 | 3.9 | 3.7 | 3.5 | 3.3 | 3.2 | 3 | 2.7 | 2.4 | 2.2 | 2 | 7.002
8:00 | 3 | 2.7 | 2.4 | 2.1 | 1.9 | 1.6 | 1.2 | 0.8 | 0.4 | 0 | 5.084
8:30 | 2.2 | 1.7 | 1.3 | 0.9 | 0.6 | 0.1 | -0.4 | -1 | -1.5 | -2 | 2.786
9:00 | 1.5 | 0.9 | 0.5 | 0 | -0.4 | -1 | -1.7 | -2.4 | -3 | -3.6 | 0.596
9:30 | 0.9 | 0.3 | -0.3 | -0.8 | -1.3 | -2 | -2.8 | -3.6 | -4.3 | -5 | -1.208
10:00 | 0.5 | -0.2 | -0.8 | -1.4 | -1.9 | -2.7 | -3.6 | -4.4 | -5.3 | -6.1 | -2.576
10:30 | -0.1 | -0.8 | -1.5 | -2.1 | -2.7 | -3.5 | -4.5 | -5.4 | -6.3 | -7.3 | -3.384
11:00 | -0.3 | -1 | -1.7 | -2.4 | -3 | -3.8 | -4.8 | -5.8 | -6.7 | -7.6 | -4.832
11:30 | -0.3 | -1.1 | -1.8 | -2.5 | -3.1 | -4 | -5 | -6 | -7 | -8 | -4.14
12:00 | -0.3 | -1 | -1.7 | -2.4 | -3 | -3.9 | -4.9 | -5.9 | -6.9 | -7.9 | -4.224
12:30 | -0.2 | -0.9 | -1.5 | -2.2 | -2.8 | -3.7 | -4.7 | -5.6 | -6.6 | -7.6 | -3.776
13:00 | 0 | -0.7 | -1.4 | -2.1 | -2.7 | -3.5 | -4.5 | -5.5 | -6.4 | -7.5 | -3.566
13:30 | 0.4 | -0.3 | -1 | -1.6 | -2.2 | -3 | -4 | -4.9 | -5.8 | -6.8 | -3.036
14:00 | 0.9 | 0.3 | -0.3 | -1 | -1.5 | -2.3 | -3.2 | -4.1 | -4.9 | -5.9 | -2.41
14:30 | 1.5 | 0.9 | 0.4 | -0.2 | -0.7 | -1.4 | -2.2 | -3 | -3.8 | -4.6 | -1.324
15:00 | 2.2 | 1.7 | 1.2 | 0.7 | 0.3 | -0.4 | -1.1 | -1.8 | -2.5 | -3.2 | -0.466
15:30 | 3.3 | 2.9 | 2.5 | 2.1 | 1.7 | 1.2 | 0.6 | 0 | -0.5 | -1.1 | 1.646
16:00 | 4.4 | 4.1 | 3.7 | 3.4 | 3.1 | 2.7 | 2.3 | 1.9 | 1.4 | 1 | 3.306
16:30 | 5.8 | 5.6 | 5.3 | 5.1 | 4.9 | 4.7 | 4.4 | 4.1 | 3.8 | 3.6 | 4.638
17:00 | 7.1 | 7 | 6.9 | 6.7 | 6.6 | 6.5 | 6.3 | 6.1 | 6 | 5.8 | 8.006
17:30 | 8.3 | 8.3 | 8.2 | 8.2 | 8.1 | 8.1 | 8 | 8 | 7.9 | 7.9 | 9.138
18:00 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.5 | 12.158
18:30 | 10.7 | 10.7 | 10.7 | 10.7 | 10.6 | 10.6 | 10.7 | 10.7 | 10.7 | 10.7 | 12.338
19:00 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 12.622
19:30 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 12.462
20:00 | 10.8 | 10.8 | 10.8 | 10.8 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 12.186
20:30 | 10.5 | 10.5 | 10.5 | 10.5 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 11.798
21:00 | 10 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.8 | 11.416
21:30 | 9.3 | 9.3 | 9.3 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 10.702
22:00 | 8.6 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9.4
22:30 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9.448
23:00 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.6 | 7.91
23:30 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.836
0:00 | 6 | 6 | 6 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 6.46

## 23. Historic load trace
Date/Time | Load (MVA) | Load (MW)
2017-03-01 00:30 | 5.39 | 5.37
2017-03-01 01:00 | 5.19 | 5.17
2017-03-01 01:30 | 5.02 | 5
2017-03-01 02:00 | 4.79 | 4.78
2017-03-01 02:30 | 4.68 | 4.67
2017-03-01 03:00 | 4.59 | 4.57
2017-03-01 03:30 | 4.57 | 4.56
2017-03-01 04:00 | 4.55 | 4.54
2017-03-01 04:30 | 4.66 | 4.64
2017-03-01 05:00 | 4.86 | 4.85
2017-03-01 05:30 | 5.16 | 5.14
2017-03-01 06:00 | 5.36 | 5.34
2017-03-01 06:30 | 5.7 | 5.69
2017-03-01 07:00 | 5.8 | 5.79
2017-03-01 07:30 | 5.8 | 5.79
2017-03-01 08:00 | 5.45 | 5.43
2017-03-01 08:30 | 4.87 | 4.84
2017-03-01 09:00 | 4.68 | 4.63
2017-03-01 09:30 | 4.78 | 4.71
2017-03-01 10:00 | 5.24 | 5.15
2017-03-01 10:30 | 5.61 | 5.52
2017-03-01 11:00 | 5.83 | 5.7
2017-03-01 11:30 | 5.84 | 5.68
2017-03-01 12:00 | 6.61 | 6.45
2017-03-01 12:30 | 6.89 | 6.71
2017-03-01 13:00 | 7.66 | 7.47
2017-03-01 13:30 | 8.43 | 8.24
2017-03-01 14:00 | 9.36 | 9.19
2017-03-01 14:30 | 9.77 | 9.6
2017-03-01 15:00 | 9.28 | 9.08
2017-03-01 15:30 | 9.43 | 9.21
2017-03-01 16:00 | 10.53 | 10.33
2017-03-01 16:30 | 11.13 | 10.94
2017-03-01 17:00 | 11.81 | 11.65
2017-03-01 17:30 | 12.75 | 12.6
2017-03-01 18:00 | 12.94 | 12.81
2017-03-01 18:30 | 13.04 | 12.9
2017-03-01 19:00 | 13.73 | 13.55
2017-03-01 19:30 | 13.62 | 13.44
2017-03-01 20:00 | 13.72 | 13.56
2017-03-01 20:30 | 13.34 | 13.19
2017-03-01 21:00 | 12.46 | 12.34
2017-03-01 21:30 | 11.47 | 11.36
2017-03-01 22:00 | 10.42 | 10.35
2017-03-01 22:30 | 9.63 | 9.57
2017-03-01 23:00 | 8.94 | 8.9
2017-03-01 23:30 | 7.63 | 7.6
2017-03-02 | 6.67 | 6.64
2017-03-02 00:30 | 6.21 | 6.19
2017-03-02 01:00 | 6.01 | 5.99
2017-03-02 01:30 | 5.65 | 5.63
2017-03-02 02:00 | 5.38 | 5.36
2017-03-02 02:30 | 5.25 | 5.23
2017-03-02 03:00 | 5.17 | 5.15
2017-03-02 03:30 | 5.1 | 5.08
2017-03-02 04:00 | 5.1 | 5.08
2017-03-02 04:30 | 5.2 | 5.19
2017-03-02 05:00 | 5.32 | 5.3
2017-03-02 05:30 | 5.58 | 5.56
2017-03-02 06:00 | 5.66 | 5.65
2017-03-02 06:30 | 5.91 | 5.9
2017-03-02 07:00 | 6.32 | 6.31
2017-03-02 07:30 | 6.72 | 6.7
2017-03-02 08:00 | 6.15 | 6.12
2017-03-02 08:30 | 5.61 | 5.57
2017-03-02 09:00 | 5.04 | 4.99
2017-03-02 09:30 | 5.98 | 5.91
2017-03-02 10:00 | 6.39 | 6.32
2017-03-02 10:30 | 6.01 | 5.92
2017-03-02 11:00 | 6.44 | 6.33
2017-03-02 11:30 | 6.22 | 6.06
2017-03-02 12:00 | 7.05 | 6.87
2017-03-02 12:30 | 7.27 | 7.07
2017-03-02 13:00 | 9.73 | 9.56
2017-03-02 13:30 | 10.15 | 9.99
2017-03-02 14:00 | 8.62 | 8.4
2017-03-02 14:30 | 9.2 | 8.96
2017-03-02 15:00 | 9.5 | 9.27
2017-03-02 15:30 | 10.47 | 10.24
2017-03-02 16:00 | 11.2 | 10.98
2017-03-02 16:30 | 12.21 | 11.99
2017-03-02 17:00 | 12.91 | 12.72
2017-03-02 17:30 | 13.54 | 13.36
2017-03-02 18:00 | 13.72 | 13.55
2017-03-02 18:30 | 14.15 | 13.96
2017-03-02 19:00 | 14.89 | 14.65
2017-03-02 19:30 | 14.63 | 14.4
2017-03-02 20:00 | 14.57 | 14.37
2017-03-02 20:30 | 14.11 | 13.93
2017-03-02 21:00 | 13.1 | 12.94
2017-03-02 21:30 | 11.84 | 11.72
2017-03-02 22:00 | 10.62 | 10.53
2017-03-02 22:30 | 9.78 | 9.71
2017-03-02 23:00 | 9.15 | 9.1
2017-03-02 23:30 | 7.83 | 7.79
2017-03-03 | 6.98 | 6.95
2017-03-03 00:30 | 6.35 | 6.32
2017-03-03 01:00 | 6.12 | 6.09
2017-03-03 01:30 | 5.81 | 5.79
2017-03-03 02:00 | 5.49 | 5.47
2017-03-03 02:30 | 5.33 | 5.31
2017-03-03 03:00 | 5.25 | 5.23
2017-03-03 03:30 | 5.19 | 5.17
2017-03-03 04:00 | 5.2 | 5.18
2017-03-03 04:30 | 5.33 | 5.31
2017-03-03 05:00 | 5.45 | 5.42
2017-03-03 05:30 | 5.7 | 5.68
2017-03-03 06:00 | 5.8 | 5.78
2017-03-03 06:30 | 6.09 | 6.07
2017-03-03 07:00 | 5.97 | 5.96
2017-03-03 07:30 | 6.28 | 6.26
2017-03-03 08:00 | 6.03 | 5.99
2017-03-03 08:30 | 5.71 | 5.65
2017-03-03 09:00 | 5.44 | 5.36
2017-03-03 09:30 | 5.71 | 5.6
2017-03-03 10:00 | 6 | 5.85
2017-03-03 10:30 | 6.35 | 6.17
2017-03-03 11:00 | 6.83 | 6.66
2017-03-03 11:30 | 7.33 | 7.12
2017-03-03 12:00 | 8.27 | 8.07
2017-03-03 12:30 | 8.51 | 8.29
2017-03-03 13:00 | 8.28 | 7.99
2017-03-03 13:30 | 9.68 | 9.41
2017-03-03 14:00 | 9.16 | 8.87
2017-03-03 14:30 | 9.43 | 9.13
2017-03-03 15:00 | 10.14 | 9.84
2017-03-03 15:30 | 11.06 | 10.77
2017-03-03 16:00 | 11.98 | 11.71
2017-03-03 16:30 | 12.94 | 12.69
2017-03-03 17:00 | 13.59 | 13.38
2017-03-03 17:30 | 13.88 | 13.68
2017-03-03 18:00 | 13.75 | 13.57
2017-03-03 18:30 | 13.54 | 13.37
2017-03-03 19:00 | 14.18 | 13.96
2017-03-03 19:30 | 14.05 | 13.83
2017-03-03 20:00 | 13.91 | 13.7
2017-03-03 20:30 | 13.64 | 13.44
2017-03-03 21:00 | 12.65 | 12.48
2017-03-03 21:30 | 11.97 | 11.82
2017-03-03 22:00 | 11.11 | 10.98
2017-03-03 22:30 | 10.59 | 10.49
2017-03-03 23:00 | 10.21 | 10.12
2017-03-03 23:30 | 9.13 | 9.05
2017-03-04 | 8.24 | 8.17
2017-03-04 00:30 | 7.51 | 7.46
2017-03-04 01:00 | 7.29 | 7.24
2017-03-04 01:30 | 6.8 | 6.75
2017-03-04 02:00 | 6.47 | 6.43
2017-03-04 02:30 | 6.32 | 6.28
2017-03-04 03:00 | 6.1 | 6.06
2017-03-04 03:30 | 6.08 | 6.04
2017-03-04 04:00 | 5.98 | 5.93
2017-03-04 04:30 | 5.87 | 5.83
2017-03-04 05:00 | 5.82 | 5.78
2017-03-04 05:30 | 5.82 | 5.78
2017-03-04 06:00 | 5.73 | 5.69
2017-03-04 06:30 | 5.82 | 5.78
2017-03-04 07:00 | 6.1 | 6.06
2017-03-04 07:30 | 6.06 | 6.02
2017-03-04 08:00 | 6.11 | 6.06
2017-03-04 08:30 | 6.88 | 6.82
2017-03-04 09:00 | 7.07 | 7
2017-03-04 09:30 | 8.64 | 8.57
2017-03-04 10:00 | 8.56 | 8.48
2017-03-04 10:30 | 8.63 | 8.53
2017-03-04 11:00 | 8.55 | 8.43
2017-03-04 11:30 | 9.79 | 9.68
2017-03-04 12:00 | 9.4 | 9.27
2017-03-04 12:30 | 8.24 | 8.06
2017-03-04 13:00 | 9.59 | 9.4
2017-03-04 13:30 | 10.01 | 9.82
2017-03-04 14:00 | 10.61 | 10.41
2017-03-04 14:30 | 11.68 | 11.46
2017-03-04 15:00 | 12.54 | 12.35
2017-03-04 15:30 | 12.03 | 11.85
2017-03-04 16:00 | 11.45 | 11.29
2017-03-04 16:30 | 12 | 11.85
2017-03-04 17:00 | 12.03 | 11.9
2017-03-04 17:30 | 12.14 | 12.01
2017-03-04 18:00 | 12.21 | 12.07
2017-03-04 18:30 | 12.6 | 12.42
2017-03-04 19:00 | 12.67 | 12.5
2017-03-04 19:30 | 12.34 | 12.17
2017-03-04 20:00 | 12.34 | 12.17
2017-03-04 20:30 | 12.04 | 11.88
2017-03-04 21:00 | 11.41 | 11.28
2017-03-04 21:30 | 10.76 | 10.65
2017-03-04 22:00 | 10.18 | 10.09
2017-03-04 22:30 | 9.8 | 9.72
2017-03-04 23:00 | 9.44 | 9.39
2017-03-04 23:30 | 8.54 | 8.48
2017-03-05 | 7.61 | 7.57
2017-03-05 00:30 | 7.02 | 6.99
2017-03-05 01:00 | 6.83 | 6.8
2017-03-05 01:30 | 6.34 | 6.31
2017-03-05 02:00 | 5.97 | 5.93
2017-03-05 02:30 | 5.71 | 5.68
2017-03-05 03:00 | 5.61 | 5.58
2017-03-05 03:30 | 5.52 | 5.5
2017-03-05 04:00 | 5.4 | 5.38
2017-03-05 04:30 | 5.41 | 5.38
2017-03-05 05:00 | 5.34 | 5.31
2017-03-05 05:30 | 5.35 | 5.33
2017-03-05 06:00 | 5.4 | 5.38
2017-03-05 06:30 | 5.35 | 5.33
2017-03-05 07:00 | 5.07 | 5.05
2017-03-05 07:30 | 5.48 | 5.46
2017-03-05 08:00 | 6.02 | 5.99
2017-03-05 08:30 | 7.34 | 7.3
2017-03-05 09:00 | 6.89 | 6.83
2017-03-05 09:30 | 6.66 | 6.59
2017-03-05 10:00 | 7.28 | 7.18
2017-03-05 10:30 | 7.64 | 7.53
2017-03-05 11:00 | 8.14 | 8
2017-03-05 11:30 | 9 | 8.83
2017-03-05 12:00 | 8.71 | 8.5
2017-03-05 12:30 | 9.75 | 9.54
2017-03-05 13:00 | 10.57 | 10.33
2017-03-05 13:30 | 11.18 | 10.91
2017-03-05 14:00 | 12.69 | 12.43
2017-03-05 14:30 | 13.35 | 13.08
2017-03-05 15:00 | 13.96 | 13.69
2017-03-05 15:30 | 14.56 | 14.29
2017-03-05 16:00 | 15.05 | 14.77
2017-03-05 16:30 | 15.5 | 15.21
2017-03-05 17:00 | 16.02 | 15.75
2017-03-05 17:30 | 16.72 | 16.45
2017-03-05 18:00 | 16.68 | 16.43
2017-03-05 18:30 | 16.34 | 16.09
2017-03-05 19:00 | 16.43 | 16.15
2017-03-05 19:30 | 15.99 | 15.71
2017-03-05 20:00 | 15.32 | 15.07
2017-03-05 20:30 | 14.9 | 14.67
2017-03-05 21:00 | 13.97 | 13.77
2017-03-05 21:30 | 12.91 | 12.74
2017-03-05 22:00 | 11.76 | 11.62
2017-03-05 22:30 | 11.03 | 10.92
2017-03-05 23:00 | 10.35 | 10.26
2017-03-05 23:30 | 9.14 | 9.06
2017-03-06 | 8.11 | 8.05
2017-03-06 00:30 | 7.38 | 7.33
2017-03-06 01:00 | 7.04 | 6.99
2017-03-06 01:30 | 6.6 | 6.55
2017-03-06 02:00 | 6.18 | 6.14
2017-03-06 02:30 | 5.99 | 5.95
2017-03-06 03:00 | 5.82 | 5.78
2017-03-06 03:30 | 5.82 | 5.79
2017-03-06 04:00 | 5.74 | 5.71
2017-03-06 04:30 | 5.72 | 5.68
2017-03-06 05:00 | 5.81 | 5.77
2017-03-06 05:30 | 6.07 | 6.04
2017-03-06 06:00 | 6.12 | 6.09
2017-03-06 06:30 | 6.31 | 6.29
2017-03-06 07:00 | 6.49 | 6.47
2017-03-06 07:30 | 6.66 | 6.63
2017-03-06 08:00 | 6.46 | 6.42
2017-03-06 08:30 | 6.03 | 5.97
2017-03-06 09:00 | 6.02 | 5.92
2017-03-06 09:30 | 6.43 | 6.31
2017-03-06 10:00 | 6.61 | 6.48
2017-03-06 10:30 | 6.78 | 6.62
2017-03-06 11:00 | 6.81 | 6.64
2017-03-06 11:30 | 7.56 | 7.37
2017-03-06 12:00 | 7.64 | 7.41
2017-03-06 12:30 | 8.46 | 8.17
2017-03-06 13:00 | 8.98 | 8.67
2017-03-06 13:30 | 9.51 | 9.2
2017-03-06 14:00 | 10.38 | 10.07
2017-03-06 14:30 | 11.7 | 11.42
2017-03-06 15:00 | 12.36 | 12.08
2017-03-06 15:30 | 12.35 | 12.06
2017-03-06 16:00 | 13.28 | 13
2017-03-06 16:30 | 14.58 | 14.28
2017-03-06 17:00 | 15.17 | 14.89
2017-03-06 17:30 | 15.49 | 15.22
2017-03-06 18:00 | 15.65 | 15.41
2017-03-06 18:30 | 15.56 | 15.33
2017-03-06 19:00 | 16.04 | 15.78
2017-03-06 19:30 | 15.61 | 15.38
2017-03-06 20:00 | 15.17 | 14.94
2017-03-06 20:30 | 14.59 | 14.39
2017-03-06 21:00 | 13.61 | 13.43
2017-03-06 21:30 | 12.38 | 12.24
2017-03-06 22:00 | 11.35 | 11.23
2017-03-06 22:30 | 10.22 | 10.15
2017-03-06 23:00 | 9.27 | 9.23
2017-03-06 23:30 | 8.16 | 8.11
2017-03-07 | 7.17 | 7.13
2017-03-07 00:30 | 6.54 | 6.5
2017-03-07 01:00 | 6.22 | 6.18
2017-03-07 01:30 | 5.89 | 5.86
2017-03-07 02:00 | 5.59 | 5.56
2017-03-07 02:30 | 5.51 | 5.48
2017-03-07 03:00 | 5.4 | 5.38
2017-03-07 03:30 | 5.44 | 5.41
2017-03-07 04:00 | 5.44 | 5.41
2017-03-07 04:30 | 5.51 | 5.48
2017-03-07 05:00 | 5.51 | 5.48
2017-03-07 05:30 | 5.76 | 5.73
2017-03-07 06:00 | 5.94 | 5.92
2017-03-07 06:30 | 6.07 | 6.06
2017-03-07 07:00 | 6.47 | 6.45
2017-03-07 07:30 | 6.73 | 6.71
2017-03-07 08:00 | 6.5 | 6.48
2017-03-07 08:30 | 5.71 | 5.65
2017-03-07 09:00 | 5.47 | 5.38
2017-03-07 09:30 | 5.46 | 5.37
2017-03-07 10:00 | 5.63 | 5.53
2017-03-07 10:30 | 5.07 | 4.93
2017-03-07 11:00 | 5.37 | 5.21
2017-03-07 11:30 | 5.61 | 5.41
2017-03-07 12:00 | 6.1 | 5.9
2017-03-07 12:30 | 6.48 | 6.28
2017-03-07 13:00 | 6.91 | 6.71
2017-03-07 13:30 | 7.52 | 7.29
2017-03-07 14:00 | 8.53 | 8.29
2017-03-07 14:30 | 9.11 | 8.87
2017-03-07 15:00 | 10.17 | 9.94
2017-03-07 15:30 | 11.51 | 11.26
2017-03-07 16:00 | 12.66 | 12.41
2017-03-07 16:30 | 12.92 | 12.68
2017-03-07 17:00 | 13.67 | 13.45
2017-03-07 17:30 | 13.94 | 13.75
2017-03-07 18:00 | 13.59 | 13.41
2017-03-07 18:30 | 13.71 | 13.53
2017-03-07 19:00 | 14.75 | 14.53
2017-03-07 19:30 | 14.43 | 14.21
2017-03-07 20:00 | 14 | 13.8
2017-03-07 20:30 | 13.34 | 13.18
2017-03-07 21:00 | 12.24 | 12.13
2017-03-07 21:30 | 11.26 | 11.17
2017-03-07 22:00 | 10.14 | 10.07
2017-03-07 22:30 | 9.2 | 9.16
2017-03-07 23:00 | 8.39 | 8.36
2017-03-07 23:30 | 7.14 | 7.12
2017-03-08 | 6.27 | 6.25
2017-03-08 00:30 | 5.65 | 5.64
2017-03-08 01:00 | 5.47 | 5.46
2017-03-08 01:30 | 5.17 | 5.16
2017-03-08 02:00 | 4.95 | 4.93
2017-03-08 02:30 | 4.82 | 4.8
2017-03-08 03:00 | 4.69 | 4.67
2017-03-08 03:30 | 4.7 | 4.69
2017-03-08 04:00 | 4.82 | 4.8
2017-03-08 04:30 | 4.82 | 4.8
2017-03-08 05:00 | 4.98 | 4.95
2017-03-08 05:30 | 5.27 | 5.25
2017-03-08 06:00 | 5.48 | 5.47
2017-03-08 06:30 | 5.97 | 5.96
2017-03-08 07:00 | 6.11 | 6.11
2017-03-08 07:30 | 6.31 | 6.3
2017-03-08 08:00 | 6.28 | 6.26
2017-03-08 08:30 | 5.76 | 5.73
2017-03-08 09:00 | 5.18 | 5.15
2017-03-08 09:30 | 5.43 | 5.4
2017-03-08 10:00 | 5.55 | 5.53
2017-03-08 10:30 | 5.57 | 5.53
2017-03-08 11:00 | 5.52 | 5.49
2017-03-08 11:30 | 4.7 | 4.66
2017-03-08 12:00 | 4.97 | 4.93
2017-03-08 12:30 | 4.84 | 4.81
2017-03-08 13:00 | 5.34 | 5.29
2017-03-08 13:30 | 4.93 | 4.87
2017-03-08 14:00 | 5.32 | 5.25
2017-03-08 14:30 | 6.42 | 6.34
2017-03-08 15:00 | 8.05 | 7.99
2017-03-08 15:30 | 7.87 | 7.82
2017-03-08 16:00 | 8.33 | 8.28
2017-03-08 16:30 | 9.1 | 9.05
2017-03-08 17:00 | 9.56 | 9.52
2017-03-08 17:30 | 9.69 | 9.64
2017-03-08 18:00 | 10.43 | 10.38
2017-03-08 18:30 | 11.32 | 11.24
2017-03-08 19:00 | 12.4 | 12.29
2017-03-08 19:30 | 12.17 | 12.06
2017-03-08 20:00 | 12.17 | 12.06
2017-03-08 20:30 | 11.93 | 11.84
2017-03-08 21:00 | 11.15 | 11.08
2017-03-08 21:30 | 10.38 | 10.32
2017-03-08 22:00 | 9.27 | 9.23
2017-03-08 22:30 | 8.65 | 8.63
2017-03-08 23:00 | 8.04 | 8.03
2017-03-08 23:30 | 6.9 | 6.89
2017-03-09 | 6.1 | 6.09
2017-03-09 00:30 | 5.58 | 5.57
2017-03-09 01:00 | 5.36 | 5.35
2017-03-09 01:30 | 5.05 | 5.04
2017-03-09 02:00 | 4.77 | 4.76
2017-03-09 02:30 | 4.67 | 4.66
2017-03-09 03:00 | 4.62 | 4.62
2017-03-09 03:30 | 4.67 | 4.66
2017-03-09 04:00 | 4.68 | 4.67
2017-03-09 04:30 | 4.84 | 4.83
2017-03-09 05:00 | 4.95 | 4.94
2017-03-09 05:30 | 5.33 | 5.32
2017-03-09 06:00 | 5.42 | 5.41
2017-03-09 06:30 | 5.72 | 5.71
2017-03-09 07:00 | 5.78 | 5.78
2017-03-09 07:30 | 5.9 | 5.89
2017-03-09 08:00 | 5.7 | 5.68
2017-03-09 08:30 | 5.35 | 5.34
2017-03-09 09:00 | 4.82 | 4.8
2017-03-09 09:30 | 4.42 | 4.4
2017-03-09 10:00 | 4.01 | 3.97
2017-03-09 10:30 | 3.89 | 3.82
2017-03-09 11:00 | 3.83 | 3.76
2017-03-09 11:30 | 4.33 | 4.23
2017-03-09 12:00 | 5.6 | 5.52
2017-03-09 12:30 | 5.67 | 5.56
2017-03-09 13:00 | 6.39 | 6.27
2017-03-09 13:30 | 6.9 | 6.77
2017-03-09 14:00 | 7.55 | 7.44
2017-03-09 14:30 | 7.01 | 6.88
2017-03-09 15:00 | 7.31 | 7.16
2017-03-09 15:30 | 9.1 | 8.98
2017-03-09 16:00 | 9.39 | 9.27
2017-03-09 16:30 | 10.52 | 10.4
2017-03-09 17:00 | 10.65 | 10.55
2017-03-09 17:30 | 11.14 | 11.04
2017-03-09 18:00 | 11.46 | 11.36
2017-03-09 18:30 | 12.04 | 11.93
2017-03-09 19:00 | 12.88 | 12.74
2017-03-09 19:30 | 12.58 | 12.45
2017-03-09 20:00 | 12.36 | 12.24
2017-03-09 20:30 | 12.07 | 11.98
2017-03-09 21:00 | 11.32 | 11.24
2017-03-09 21:30 | 10.49 | 10.44
2017-03-09 22:00 | 9.5 | 9.47
2017-03-09 22:30 | 9.06 | 9.03
2017-03-09 23:00 | 8.36 | 8.34
2017-03-09 23:30 | 7.03 | 7.01
2017-03-10 | 6.15 | 6.14
2017-03-10 00:30 | 5.62 | 5.61
2017-03-10 01:00 | 5.39 | 5.38
2017-03-10 01:30 | 5.11 | 5.1
2017-03-10 02:00 | 4.84 | 4.83
2017-03-10 02:30 | 4.7 | 4.69
2017-03-10 03:00 | 4.69 | 4.68
2017-03-10 03:30 | 4.73 | 4.72
2017-03-10 04:00 | 4.63 | 4.62
2017-03-10 04:30 | 4.79 | 4.78
2017-03-10 05:00 | 4.9 | 4.89
2017-03-10 05:30 | 5.07 | 5.05
2017-03-10 06:00 | 5.25 | 5.24
2017-03-10 06:30 | 5.44 | 5.43
2017-03-10 07:00 | 5.57 | 5.57
2017-03-10 07:30 | 5.69 | 5.67
2017-03-10 08:00 | 5.03 | 5.02
2017-03-10 08:30 | 4.56 | 4.54
2017-03-10 09:00 | 4.09 | 4.06
2017-03-10 09:30 | 3.93 | 3.89
2017-03-10 10:00 | 3.73 | 3.68
2017-03-10 10:30 | 3.81 | 3.72
2017-03-10 11:00 | 3.88 | 3.78
2017-03-10 11:30 | 4.06 | 3.95
2017-03-10 12:00 | 4.34 | 4.21
2017-03-10 12:30 | 4.58 | 4.47
2017-03-10 13:00 | 5.04 | 4.89
2017-03-10 13:30 | 5.91 | 5.75
2017-03-10 14:00 | 6.41 | 6.23
2017-03-10 14:30 | 6.89 | 6.72
2017-03-10 15:00 | 7.54 | 7.38
2017-03-10 15:30 | 8.45 | 8.28
2017-03-10 16:00 | 9.85 | 9.67
2017-03-10 16:30 | 10.82 | 10.65
2017-03-10 17:00 | 11.38 | 11.24
2017-03-10 17:30 | 11.64 | 11.52
2017-03-10 18:00 | 11.51 | 11.4
2017-03-10 18:30 | 11.67 | 11.55
2017-03-10 19:00 | 12.32 | 12.17
2017-03-10 19:30 | 12 | 11.86
2017-03-10 20:00 | 11.9 | 11.78
2017-03-10 20:30 | 11.52 | 11.41
2017-03-10 21:00 | 10.65 | 10.57
2017-03-10 21:30 | 9.92 | 9.85
2017-03-10 22:00 | 9.14 | 9.09
2017-03-10 22:30 | 8.72 | 8.69
2017-03-10 23:00 | 8.36 | 8.33
2017-03-10 23:30 | 7.27 | 7.25
2017-03-11 | 6.4 | 6.39
2017-03-11 00:30 | 5.89 | 5.88
2017-03-11 01:00 | 5.59 | 5.58
2017-03-11 01:30 | 5.31 | 5.3
2017-03-11 02:00 | 5.17 | 5.15
2017-03-11 02:30 | 5.07 | 5.06
2017-03-11 03:00 | 5 | 4.98
2017-03-11 03:30 | 4.85 | 4.84
2017-03-11 04:00 | 4.82 | 4.8
2017-03-11 04:30 | 4.78 | 4.76
2017-03-11 05:00 | 4.91 | 4.89
2017-03-11 05:30 | 4.92 | 4.9
2017-03-11 06:00 | 4.79 | 4.77
2017-03-11 06:30 | 4.8 | 4.78
2017-03-11 07:00 | 4.76 | 4.74
2017-03-11 07:30 | 4.95 | 4.92
2017-03-11 08:00 | 5.12 | 5.09
2017-03-11 08:30 | 4.96 | 4.93
2017-03-11 09:00 | 4.89 | 4.84
2017-03-11 09:30 | 5.04 | 4.98
2017-03-11 10:00 | 5.07 | 5.02
2017-03-11 10:30 | 5.09 | 5
2017-03-11 11:00 | 5.15 | 5.04
2017-03-11 11:30 | 5.48 | 5.36
2017-03-11 12:00 | 6.56 | 6.42
2017-03-11 12:30 | 7.02 | 6.88
2017-03-11 13:00 | 7.13 | 6.98
2017-03-11 13:30 | 8.01 | 7.85
2017-03-11 14:00 | 8.75 | 8.59
2017-03-11 14:30 | 9.38 | 9.2
2017-03-11 15:00 | 10.3 | 10.12
2017-03-11 15:30 | 11.57 | 11.42
2017-03-11 16:00 | 11.39 | 11.25
2017-03-11 16:30 | 10.86 | 10.7
2017-03-11 17:00 | 11.4 | 11.26
2017-03-11 17:30 | 11.51 | 11.39
2017-03-11 18:00 | 11.57 | 11.46
2017-03-11 18:30 | 11.38 | 11.28
2017-03-11 19:00 | 11.65 | 11.53
2017-03-11 19:30 | 11.3 | 11.19
2017-03-11 20:00 | 11.08 | 10.97
2017-03-11 20:30 | 10.72 | 10.64
2017-03-11 21:00 | 10.12 | 10.05
2017-03-11 21:30 | 9.59 | 9.53
2017-03-11 22:00 | 9.05 | 9.01
2017-03-11 22:30 | 8.8 | 8.77
2017-03-11 23:00 | 8.57 | 8.54
2017-03-11 23:30 | 7.66 | 7.64
2017-03-12 | 6.83 | 6.8
2017-03-12 00:30 | 6.18 | 6.17
2017-03-12 01:00 | 5.92 | 5.9
2017-03-12 01:30 | 5.6 | 5.58
2017-03-12 02:00 | 5.33 | 5.31
2017-03-12 02:30 | 5.22 | 5.2
2017-03-12 03:00 | 5.01 | 4.99
2017-03-12 03:30 | 5.1 | 5.08
2017-03-12 04:00 | 5.03 | 5.01
2017-03-12 04:30 | 4.87 | 4.85
2017-03-12 05:00 | 4.85 | 4.83
2017-03-12 05:30 | 4.97 | 4.95
2017-03-12 06:00 | 4.8 | 4.78
2017-03-12 06:30 | 4.87 | 4.85
2017-03-12 07:00 | 4.93 | 4.92
2017-03-12 07:30 | 4.99 | 4.97
2017-03-12 08:00 | 5.03 | 5
2017-03-12 08:30 | 5.76 | 5.73
2017-03-12 09:00 | 6.2 | 6.15
2017-03-12 09:30 | 6.48 | 6.42
2017-03-12 10:00 | 6.25 | 6.19
2017-03-12 10:30 | 6.65 | 6.57
2017-03-12 11:00 | 6.93 | 6.83
2017-03-12 11:30 | 7.13 | 7
2017-03-12 12:00 | 7.77 | 7.61
2017-03-12 12:30 | 8.65 | 8.46
2017-03-12 13:00 | 9.34 | 9.12
2017-03-12 13:30 | 9.82 | 9.59
2017-03-12 14:00 | 10.67 | 10.44
2017-03-12 14:30 | 11.45 | 11.21
2017-03-12 15:00 | 12.22 | 11.96
2017-03-12 15:30 | 13.05 | 12.8
2017-03-12 16:00 | 13.96 | 13.71
2017-03-12 16:30 | 14.78 | 14.53
2017-03-12 17:00 | 15.84 | 15.58
2017-03-12 17:30 | 16.03 | 15.76
2017-03-12 18:00 | 15.98 | 15.73
2017-03-12 18:30 | 15.83 | 15.57
2017-03-12 19:00 | 15.97 | 15.72
2017-03-12 19:30 | 15.63 | 15.38
2017-03-12 20:00 | 15.24 | 14.98
2017-03-12 20:30 | 14.65 | 14.43
2017-03-12 21:00 | 13.66 | 13.48
2017-03-12 21:30 | 12.67 | 12.51
2017-03-12 22:00 | 11.64 | 11.5
2017-03-12 22:30 | 10.91 | 10.82
2017-03-12 23:00 | 10.12 | 10.04
2017-03-12 23:30 | 8.93 | 8.86
2017-03-13 | 7.8 | 7.75
2017-03-13 00:30 | 7.12 | 7.08
2017-03-13 01:00 | 6.77 | 6.73
2017-03-13 01:30 | 6.34 | 6.31
2017-03-13 02:00 | 6.1 | 6.07
2017-03-13 02:30 | 5.93 | 5.9
2017-03-13 03:00 | 5.79 | 5.75
2017-03-13 03:30 | 5.85 | 5.81
2017-03-13 04:00 | 5.82 | 5.79
2017-03-13 04:30 | 5.82 | 5.78
2017-03-13 05:00 | 5.85 | 5.82
2017-03-13 05:30 | 6.22 | 6.19
2017-03-13 06:00 | 6.49 | 6.46
2017-03-13 06:30 | 6.98 | 6.96
2017-03-13 07:00 | 7.59 | 7.57
2017-03-13 07:30 | 8.67 | 8.64
2017-03-13 08:00 | 9.26 | 9.22
2017-03-13 08:30 | 8.9 | 8.87
2017-03-13 09:00 | 8.71 | 8.68
2017-03-13 09:30 | 8.64 | 8.61
2017-03-13 10:00 | 8.39 | 8.36
2017-03-13 10:30 | 7.18 | 7.14
2017-03-13 11:00 | 6.39 | 6.34
2017-03-13 11:30 | 6.89 | 6.83
2017-03-13 12:00 | 6.47 | 6.4
2017-03-13 12:30 | 7.58 | 7.52
2017-03-13 13:00 | 7.74 | 7.67
2017-03-13 13:30 | 8.55 | 8.47
2017-03-13 14:00 | 8.95 | 8.89
2017-03-13 14:30 | 9.1 | 9.04
2017-03-13 15:00 | 8.78 | 8.71
2017-03-13 15:30 | 9.68 | 9.62
2017-03-13 16:00 | 10.3 | 10.24
2017-03-13 16:30 | 10.84 | 10.78
2017-03-13 17:00 | 11.06 | 11
2017-03-13 17:30 | 11.4 | 11.34
2017-03-13 18:00 | 12 | 11.95
2017-03-13 18:30 | 12.63 | 12.56
2017-03-13 19:00 | 13.58 | 13.47
2017-03-13 19:30 | 13.38 | 13.27
2017-03-13 20:00 | 14.16 | 14.08
2017-03-13 20:30 | 14.12 | 14.05
2017-03-13 21:00 | 13.25 | 13.19
2017-03-13 21:30 | 11.85 | 11.79
2017-03-13 22:00 | 10.47 | 10.41
2017-03-13 22:30 | 9.55 | 9.52
2017-03-13 23:00 | 8.87 | 8.85
2017-03-13 23:30 | 7.78 | 7.75
2017-03-14 | 6.89 | 6.87
2017-03-14 00:30 | 6.36 | 6.34
2017-03-14 01:00 | 6.15 | 6.13
2017-03-14 01:30 | 5.83 | 5.82
2017-03-14 02:00 | 5.63 | 5.61
2017-03-14 02:30 | 5.5 | 5.49
2017-03-14 03:00 | 5.45 | 5.43
2017-03-14 03:30 | 5.46 | 5.44
2017-03-14 04:00 | 5.33 | 5.32
2017-03-14 04:30 | 5.54 | 5.52
2017-03-14 05:00 | 5.64 | 5.63
2017-03-14 05:30 | 6.03 | 6.02
2017-03-14 06:00 | 6.59 | 6.58
2017-03-14 06:30 | 6.92 | 6.91
2017-03-14 07:00 | 7.62 | 7.62
2017-03-14 07:30 | 7.99 | 7.98
2017-03-14 08:00 | 8.09 | 8.06
2017-03-14 08:30 | 8.08 | 8.05
2017-03-14 09:00 | 7.84 | 7.8
2017-03-14 09:30 | 7.87 | 7.83
2017-03-14 10:00 | 7.12 | 7.06
2017-03-14 10:30 | 7.49 | 7.43
2017-03-14 11:00 | 9.39 | 9.33
2017-03-14 11:30 | 9.21 | 9.16
2017-03-14 12:00 | 6.17 | 6.09
2017-03-14 12:30 | 8.34 | 8.28
2017-03-14 13:00 | 8.69 | 8.63
2017-03-14 13:30 | 8.47 | 8.41
2017-03-14 14:00 | 7.25 | 7.17
2017-03-14 14:30 | 6.79 | 6.68
2017-03-14 15:00 | 6.69 | 6.6
2017-03-14 15:30 | 8.01 | 7.93
2017-03-14 16:00 | 9.36 | 9.28
2017-03-14 16:30 | 10.31 | 10.25
2017-03-14 17:00 | 11.17 | 11.12
2017-03-14 17:30 | 11.43 | 11.38
2017-03-14 18:00 | 11.96 | 11.89
2017-03-14 18:30 | 13.03 | 12.92
2017-03-14 19:00 | 13.52 | 13.41
2017-03-14 19:30 | 13.13 | 13.01
2017-03-14 20:00 | 13.25 | 13.14
2017-03-14 20:30 | 12.79 | 12.71
2017-03-14 21:00 | 11.91 | 11.84
2017-03-14 21:30 | 11.24 | 11.18
2017-03-14 22:00 | 10.4 | 10.36
2017-03-14 22:30 | 9.35 | 9.32
2017-03-14 23:00 | 8.54 | 8.52
2017-03-14 23:30 | 7.47 | 7.45
2017-03-15 | 6.66 | 6.64
2017-03-15 00:30 | 6.12 | 6.11
2017-03-15 01:00 | 5.88 | 5.86
2017-03-15 01:30 | 5.63 | 5.62
2017-03-15 02:00 | 5.45 | 5.44
2017-03-15 02:30 | 5.34 | 5.33
2017-03-15 03:00 | 5.28 | 5.27
2017-03-15 03:30 | 5.41 | 5.39
2017-03-15 04:00 | 5.25 | 5.24
2017-03-15 04:30 | 5.59 | 5.58
2017-03-15 05:00 | 5.74 | 5.72
2017-03-15 05:30 | 6.06 | 6.05
2017-03-15 06:00 | 6.37 | 6.35
2017-03-15 06:30 | 6.53 | 6.52
2017-03-15 07:00 | 7.58 | 7.58
2017-03-15 07:30 | 7.85 | 7.84
2017-03-15 08:00 | 8.45 | 8.44
2017-03-15 08:30 | 8.05 | 8.04
2017-03-15 09:00 | 7.93 | 7.9
2017-03-15 09:30 | 8.93 | 8.91
2017-03-15 10:00 | 8.91 | 8.88
2017-03-15 10:30 | 8.43 | 8.41
2017-03-15 11:00 | 7.41 | 7.37
2017-03-15 11:30 | 9.33 | 9.28
2017-03-15 12:00 | 9.81 | 9.77
2017-03-15 12:30 | 9.01 | 8.97
2017-03-15 13:00 | 9.06 | 9
2017-03-15 13:30 | 9.7 | 9.65
2017-03-15 14:00 | 9.5 | 9.45
2017-03-15 14:30 | 8.7 | 8.65
2017-03-15 15:00 | 8.86 | 8.82
2017-03-15 15:30 | 8.67 | 8.63
2017-03-15 16:00 | 9.22 | 9.18
2017-03-15 16:30 | 9.92 | 9.88
2017-03-15 17:00 | 10.33 | 10.29
2017-03-15 17:30 | 10.95 | 10.91
2017-03-15 18:00 | 11.51 | 11.47
2017-03-15 18:30 | 12.31 | 12.24
2017-03-15 19:00 | 13.21 | 13.11
2017-03-15 19:30 | 12.76 | 12.67
2017-03-15 20:00 | 12.64 | 12.56
2017-03-15 20:30 | 12.51 | 12.44
2017-03-15 21:00 | 11.83 | 11.77
2017-03-15 21:30 | 10.87 | 10.82
2017-03-15 22:00 | 10.01 | 9.98
2017-03-15 22:30 | 9.14 | 9.12
2017-03-15 23:00 | 8.59 | 8.58
2017-03-15 23:30 | 7.54 | 7.52
2017-03-16 | 6.72 | 6.7
2017-03-16 00:30 | 6 | 5.99
2017-03-16 01:00 | 5.84 | 5.82
2017-03-16 01:30 | 5.59 | 5.58
2017-03-16 02:00 | 5.46 | 5.45
2017-03-16 02:30 | 5.25 | 5.24
2017-03-16 03:00 | 5.17 | 5.15
2017-03-16 03:30 | 5.24 | 5.23
2017-03-16 04:00 | 5.23 | 5.22
2017-03-16 04:30 | 5.3 | 5.29
2017-03-16 05:00 | 5.49 | 5.48
2017-03-16 05:30 | 5.9 | 5.88
2017-03-16 06:00 | 6.6 | 6.59
2017-03-16 06:30 | 6.93 | 6.93
2017-03-16 07:00 | 7.32 | 7.31
2017-03-16 07:30 | 7.85 | 7.85
2017-03-16 08:00 | 7.45 | 7.45
2017-03-16 08:30 | 6.72 | 6.71
2017-03-16 09:00 | 6.47 | 6.45
2017-03-16 09:30 | 6.36 | 6.32
2017-03-16 10:00 | 6.4 | 6.36
2017-03-16 10:30 | 6.43 | 6.39
2017-03-16 11:00 | 5.15 | 5.08
2017-03-16 11:30 | 5.02 | 4.92
2017-03-16 12:00 | 6 | 5.9
2017-03-16 12:30 | 6.31 | 6.2
2017-03-16 13:00 | 7.34 | 7.21
2017-03-16 13:30 | 7.74 | 7.6
2017-03-16 14:00 | 9.08 | 8.95
2017-03-16 14:30 | 9.62 | 9.48
2017-03-16 15:00 | 10.45 | 10.32
2017-03-16 15:30 | 10.48 | 10.34
2017-03-16 16:00 | 10.64 | 10.48
2017-03-16 16:30 | 11.82 | 11.65
2017-03-16 17:00 | 12.47 | 12.32
2017-03-16 17:30 | 12.48 | 12.34
2017-03-16 18:00 | 12.77 | 12.63
2017-03-16 18:30 | 13.64 | 13.46
2017-03-16 19:00 | 14.4 | 14.2
2017-03-16 19:30 | 14.08 | 13.91
2017-03-16 20:00 | 14.14 | 13.99
2017-03-16 20:30 | 13.67 | 13.56
2017-03-16 21:00 | 12.66 | 12.56
2017-03-16 21:30 | 11.81 | 11.72
2017-03-16 22:00 | 10.62 | 10.54
2017-03-16 22:30 | 9.93 | 9.87
2017-03-16 23:00 | 9.41 | 9.36
2017-03-16 23:30 | 8.13 | 8.1
2017-03-17 | 7.48 | 7.45
2017-03-17 00:30 | 6.96 | 6.94
2017-03-17 01:00 | 6.64 | 6.62
2017-03-17 01:30 | 6.34 | 6.32
2017-03-17 02:00 | 6.05 | 6.04
2017-03-17 02:30 | 5.84 | 5.82
2017-03-17 03:00 | 5.75 | 5.74
2017-03-17 03:30 | 5.68 | 5.66
2017-03-17 04:00 | 5.61 | 5.59
2017-03-17 04:30 | 5.73 | 5.71
2017-03-17 05:00 | 5.75 | 5.74
2017-03-17 05:30 | 6.06 | 6.05
2017-03-17 06:00 | 6.23 | 6.22
2017-03-17 06:30 | 6.43 | 6.42
2017-03-17 07:00 | 6.56 | 6.55
2017-03-17 07:30 | 6.88 | 6.87
2017-03-17 08:00 | 6.45 | 6.43
2017-03-17 08:30 | 5.77 | 5.74
2017-03-17 09:00 | 5.49 | 5.44
2017-03-17 09:30 | 5.66 | 5.58
2017-03-17 10:00 | 5.87 | 5.77
2017-03-17 10:30 | 6.24 | 6.1
2017-03-17 11:00 | 6.65 | 6.49
2017-03-17 11:30 | 7.16 | 6.96
2017-03-17 12:00 | 7.79 | 7.57
2017-03-17 12:30 | 8.64 | 8.39
2017-03-17 13:00 | 9.41 | 9.14
2017-03-17 13:30 | 10.6 | 10.36
2017-03-17 14:00 | 12.18 | 11.96
2017-03-17 14:30 | 12.35 | 12.14
2017-03-17 15:00 | 12.18 | 12.01
2017-03-17 15:30 | 9.41 | 9.22
2017-03-17 16:00 | 11.14 | 10.99
2017-03-17 16:30 | 11.41 | 11.28
2017-03-17 17:00 | 11.13 | 11.02
2017-03-17 17:30 | 11.45 | 11.35
2017-03-17 18:00 | 11.44 | 11.36
2017-03-17 18:30 | 11.88 | 11.77
2017-03-17 19:00 | 12.43 | 12.3
2017-03-17 19:30 | 12.22 | 12.09
2017-03-17 20:00 | 12.14 | 12.03
2017-03-17 20:30 | 11.75 | 11.65
2017-03-17 21:00 | 11.46 | 11.37
2017-03-17 21:30 | 11.09 | 11.01
2017-03-17 22:00 | 9.48 | 9.42
2017-03-17 22:30 | 9.02 | 8.99
2017-03-17 23:00 | 8.59 | 8.57
2017-03-17 23:30 | 7.58 | 7.56
2017-03-18 | 6.83 | 6.81
2017-03-18 00:30 | 6.26 | 6.24
2017-03-18 01:00 | 6.02 | 6
2017-03-18 01:30 | 5.68 | 5.66
2017-03-18 02:00 | 5.39 | 5.37
2017-03-18 02:30 | 5.19 | 5.18
2017-03-18 03:00 | 5.04 | 5.03
2017-03-18 03:30 | 5.07 | 5.06
2017-03-18 04:00 | 5.08 | 5.07
2017-03-18 04:30 | 5.15 | 5.13
2017-03-18 05:00 | 5.15 | 5.14
2017-03-18 05:30 | 5.17 | 5.15
2017-03-18 06:00 | 5.23 | 5.21
2017-03-18 06:30 | 5.45 | 5.43
2017-03-18 07:00 | 5.38 | 5.36
2017-03-18 07:30 | 5.72 | 5.7
2017-03-18 08:00 | 6.2 | 6.17
2017-03-18 08:30 | 6.46 | 6.43
2017-03-18 09:00 | 6.38 | 6.33
2017-03-18 09:30 | 6.31 | 6.25
2017-03-18 10:00 | 6.35 | 6.28
2017-03-18 10:30 | 6.12 | 6.03
2017-03-18 11:00 | 7.63 | 7.53
2017-03-18 11:30 | 7.07 | 6.95
2017-03-18 12:00 | 8.65 | 8.53
2017-03-18 12:30 | 8.52 | 8.39
2017-03-18 13:00 | 8.78 | 8.63
2017-03-18 13:30 | 8.99 | 8.81
2017-03-18 14:00 | 10.14 | 9.97
2017-03-18 14:30 | 11.7 | 11.51
2017-03-18 15:00 | 11.23 | 11.01
2017-03-18 15:30 | 12.38 | 12.16
2017-03-18 16:00 | 13.19 | 12.98
2017-03-18 16:30 | 13.64 | 13.44
2017-03-18 17:00 | 14.24 | 14.05
2017-03-18 17:30 | 14.11 | 13.93
2017-03-18 18:00 | 13.9 | 13.73
2017-03-18 18:30 | 14.07 | 13.87
2017-03-18 19:00 | 14.28 | 14.06
2017-03-18 19:30 | 13.98 | 13.76
2017-03-18 20:00 | 13.89 | 13.68
2017-03-18 20:30 | 13.4 | 13.21
2017-03-18 21:00 | 12.78 | 12.6
2017-03-18 21:30 | 12.07 | 11.92
2017-03-18 22:00 | 11.24 | 11.1
2017-03-18 22:30 | 10.82 | 10.7
2017-03-18 23:00 | 10.31 | 10.23
2017-03-18 23:30 | 9.14 | 9.07
2017-03-19 | 8.06 | 8.01
2017-03-19 00:30 | 7.15 | 7.11
2017-03-19 01:00 | 6.73 | 6.7
2017-03-19 01:30 | 6.36 | 6.33
2017-03-19 02:00 | 6 | 5.97
2017-03-19 02:30 | 5.69 | 5.67
2017-03-19 03:00 | 5.58 | 5.55
2017-03-19 03:30 | 5.56 | 5.54
2017-03-19 04:00 | 5.39 | 5.37
2017-03-19 04:30 | 5.38 | 5.36
2017-03-19 05:00 | 5.32 | 5.3
2017-03-19 05:30 | 5.39 | 5.36
2017-03-19 06:00 | 5.3 | 5.27
2017-03-19 06:30 | 5.38 | 5.36
2017-03-19 07:00 | 5.54 | 5.52
2017-03-19 07:30 | 5.91 | 5.89
2017-03-19 08:00 | 6.32 | 6.3
2017-03-19 08:30 | 6.12 | 6.09
2017-03-19 09:00 | 7.51 | 7.47
2017-03-19 09:30 | 8.79 | 8.75
2017-03-19 10:00 | 7.34 | 7.3
2017-03-19 10:30 | 7.02 | 6.96
2017-03-19 11:00 | 7.35 | 7.28
2017-03-19 11:30 | 7.67 | 7.59
2017-03-19 12:00 | 8.3 | 8.2
2017-03-19 12:30 | 8.62 | 8.49
2017-03-19 13:00 | 10.1 | 9.97
2017-03-19 13:30 | 9.77 | 9.62
2017-03-19 14:00 | 10.33 | 10.18
2017-03-19 14:30 | 10.22 | 10.05
2017-03-19 15:00 | 10.81 | 10.63
2017-03-19 15:30 | 11.71 | 11.53
2017-03-19 16:00 | 12.44 | 12.26
2017-03-19 16:30 | 12.79 | 12.62
2017-03-19 17:00 | 13.17 | 13.01
2017-03-19 17:30 | 13.94 | 13.8
2017-03-19 18:00 | 13.91 | 13.78
2017-03-19 18:30 | 14.07 | 13.91
2017-03-19 19:00 | 14.16 | 14
2017-03-19 19:30 | 13.59 | 13.43
2017-03-19 20:00 | 13.14 | 13
2017-03-19 20:30 | 12.61 | 12.48
2017-03-19 21:00 | 11.77 | 11.67
2017-03-19 21:30 | 10.84 | 10.76
2017-03-19 22:00 | 10.01 | 9.95
2017-03-19 22:30 | 9.42 | 9.37
2017-03-19 23:00 | 9.01 | 8.97
2017-03-19 23:30 | 7.89 | 7.86
2017-03-20 | 7.04 | 7
2017-03-20 00:30 | 6.26 | 6.23
2017-03-20 01:00 | 6.07 | 6.03
2017-03-20 01:30 | 5.79 | 5.76
2017-03-20 02:00 | 5.63 | 5.61
2017-03-20 02:30 | 5.51 | 5.49
2017-03-20 03:00 | 5.31 | 5.29
2017-03-20 03:30 | 5.27 | 5.25
2017-03-20 04:00 | 5.24 | 5.22
2017-03-20 04:30 | 5.36 | 5.34
2017-03-20 05:00 | 5.47 | 5.45
2017-03-20 05:30 | 5.87 | 5.84
2017-03-20 06:00 | 6.49 | 6.47
2017-03-20 06:30 | 6.73 | 6.72
2017-03-20 07:00 | 7.6 | 7.59
2017-03-20 07:30 | 8.51 | 8.49
2017-03-20 08:00 | 8.26 | 8.24
2017-03-20 08:30 | 7.08 | 7.05
2017-03-20 09:00 | 7.68 | 7.64
2017-03-20 09:30 | 7.96 | 7.91
2017-03-20 10:00 | 8.15 | 8.09
2017-03-20 10:30 | 7.28 | 7.21
2017-03-20 11:00 | 7.33 | 7.24
2017-03-20 11:30 | 8.89 | 8.81
2017-03-20 12:00 | 8.73 | 8.66
2017-03-20 12:30 | 8.22 | 8.14
2017-03-20 13:00 | 9.36 | 9.29
2017-03-20 13:30 | 9.28 | 9.21
2017-03-20 14:00 | 9.18 | 9.12
2017-03-20 14:30 | 9.21 | 9.15
2017-03-20 15:00 | 9.4 | 9.34
2017-03-20 15:30 | 9.74 | 9.69
2017-03-20 16:00 | 9.83 | 9.8
2017-03-20 16:30 | 10.47 | 10.44
2017-03-20 17:00 | 10.75 | 10.71
2017-03-20 17:30 | 10.79 | 10.76
2017-03-20 18:00 | 11.17 | 11.13
2017-03-20 18:30 | 12.11 | 12.05
2017-03-20 19:00 | 12.14 | 12.08
2017-03-20 19:30 | 11.67 | 11.61
2017-03-20 20:00 | 11.67 | 11.62
2017-03-20 20:30 | 11.46 | 11.41
2017-03-20 21:00 | 10.65 | 10.61
2017-03-20 21:30 | 9.83 | 9.8
2017-03-20 22:00 | 9.16 | 9.12
2017-03-20 22:30 | 8.57 | 8.55
2017-03-20 23:00 | 8.37 | 8.35
2017-03-20 23:30 | 7.33 | 7.31
2017-03-21 | 6.51 | 6.49
2017-03-21 00:30 | 5.72 | 5.7
2017-03-21 01:00 | 5.68 | 5.67
2017-03-21 01:30 | 5.32 | 5.3
2017-03-21 02:00 | 5.15 | 5.14
2017-03-21 02:30 | 4.98 | 4.96
2017-03-21 03:00 | 4.92 | 4.91
2017-03-21 03:30 | 5.04 | 5.02
2017-03-21 04:00 | 5.06 | 5.04
2017-03-21 04:30 | 5.22 | 5.2
2017-03-21 05:00 | 5.27 | 5.25
2017-03-21 05:30 | 5.74 | 5.72
2017-03-21 06:00 | 6.19 | 6.17
2017-03-21 06:30 | 6.43 | 6.41
2017-03-21 07:00 | 6.96 | 6.95
2017-03-21 07:30 | 7.68 | 7.67
2017-03-21 08:00 | 7.36 | 7.35
2017-03-21 08:30 | 7.04 | 7.02
2017-03-21 09:00 | 6.97 | 6.95
2017-03-21 09:30 | 6.59 | 6.56
2017-03-21 10:00 | 6.68 | 6.65
2017-03-21 10:30 | 6.86 | 6.81
2017-03-21 11:00 | 7.21 | 7.16
2017-03-21 11:30 | 6.82 | 6.74
2017-03-21 12:00 | 8.03 | 7.96
2017-03-21 12:30 | 7.98 | 7.9
2017-03-21 13:00 | 8.12 | 8.05
2017-03-21 13:30 | 7.95 | 7.88
2017-03-21 14:00 | 8.21 | 8.14
2017-03-21 14:30 | 8.81 | 8.74
2017-03-21 15:00 | 8.66 | 8.58
2017-03-21 15:30 | 8.8 | 8.72
2017-03-21 16:00 | 10.13 | 10.05
2017-03-21 16:30 | 10.71 | 10.63
2017-03-21 17:00 | 11.24 | 11.16
2017-03-21 17:30 | 11.94 | 11.87
2017-03-21 18:00 | 12.63 | 12.54
2017-03-21 18:30 | 13.71 | 13.57
2017-03-21 19:00 | 14.19 | 14.05
2017-03-21 19:30 | 13.71 | 13.58
2017-03-21 20:00 | 13.55 | 13.44
2017-03-21 20:30 | 13.18 | 13.08
2017-03-21 21:00 | 12.27 | 12.19
2017-03-21 21:30 | 11.37 | 11.3
2017-03-21 22:00 | 10.56 | 10.49
2017-03-21 22:30 | 9.66 | 9.61
2017-03-21 23:00 | 8.9 | 8.87
2017-03-21 23:30 | 7.75 | 7.72
2017-03-22 | 6.84 | 6.81
2017-03-22 00:30 | 6.23 | 6.2
2017-03-22 01:00 | 5.97 | 5.94
2017-03-22 01:30 | 5.69 | 5.67
2017-03-22 02:00 | 5.62 | 5.6
2017-03-22 02:30 | 5.38 | 5.35
2017-03-22 03:00 | 5.23 | 5.21
2017-03-22 03:30 | 5.25 | 5.23
2017-03-22 04:00 | 5.23 | 5.2
2017-03-22 04:30 | 5.34 | 5.32
2017-03-22 05:00 | 5.71 | 5.69
2017-03-22 05:30 | 5.97 | 5.95
2017-03-22 06:00 | 6.26 | 6.24
2017-03-22 06:30 | 6.96 | 6.95
2017-03-22 07:00 | 7.47 | 7.47
2017-03-22 07:30 | 8.07 | 8.06
2017-03-22 08:00 | 8.39 | 8.38
2017-03-22 08:30 | 7.96 | 7.94
2017-03-22 09:00 | 7.22 | 7.21
2017-03-22 09:30 | 7.41 | 7.39
2017-03-22 10:00 | 6.88 | 6.85
2017-03-22 10:30 | 6.7 | 6.65
2017-03-22 11:00 | 7.18 | 7.13
2017-03-22 11:30 | 7.94 | 7.9
2017-03-22 12:00 | 7.2 | 7.16
2017-03-22 12:30 | 7.95 | 7.91
2017-03-22 13:00 | 9.25 | 9.21
2017-03-22 13:30 | 9.01 | 8.97
2017-03-22 14:00 | 8.36 | 8.33
2017-03-22 14:30 | 8.05 | 8.03
2017-03-22 15:00 | 7.52 | 7.5
2017-03-22 15:30 | 7.4 | 7.38
2017-03-22 16:00 | 8.23 | 8.2
2017-03-22 16:30 | 8.77 | 8.74
2017-03-22 17:00 | 9.5 | 9.48
2017-03-22 17:30 | 10.25 | 10.22
2017-03-22 18:00 | 11.02 | 10.97
2017-03-22 18:30 | 11.95 | 11.86
2017-03-22 19:00 | 12.44 | 12.34
2017-03-22 19:30 | 12.05 | 11.96
2017-03-22 20:00 | 12.04 | 11.96
2017-03-22 20:30 | 11.75 | 11.68
2017-03-22 21:00 | 11.1 | 11.04
2017-03-22 21:30 | 10.09 | 10.04
2017-03-22 22:00 | 9.13 | 9.1
2017-03-22 22:30 | 8.75 | 8.71
2017-03-22 23:00 | 8.5 | 8.47
2017-03-22 23:30 | 7.39 | 7.37
2017-03-23 | 6.49 | 6.47
2017-03-23 00:30 | 5.92 | 5.91
2017-03-23 01:00 | 5.74 | 5.73
2017-03-23 01:30 | 5.37 | 5.36
2017-03-23 02:00 | 5.15 | 5.14
2017-03-23 02:30 | 5.12 | 5.11
2017-03-23 03:00 | 5.06 | 5.05
2017-03-23 03:30 | 5.02 | 5
2017-03-23 04:00 | 5.04 | 5.03
2017-03-23 04:30 | 5.22 | 5.2
2017-03-23 05:00 | 5.33 | 5.31
2017-03-23 05:30 | 5.76 | 5.74
2017-03-23 06:00 | 6.59 | 6.59
2017-03-23 06:30 | 6.98 | 6.98
2017-03-23 07:00 | 7.46 | 7.46
2017-03-23 07:30 | 8 | 7.99
2017-03-23 08:00 | 7.85 | 7.84
2017-03-23 08:30 | 7.62 | 7.6
2017-03-23 09:00 | 7.19 | 7.18
2017-03-23 09:30 | 7.13 | 7.1
2017-03-23 10:00 | 6.98 | 6.94
2017-03-23 10:30 | 6.35 | 6.29
2017-03-23 11:00 | 6.71 | 6.64
2017-03-23 11:30 | 6.9 | 6.81
2017-03-23 12:00 | 7.92 | 7.84
2017-03-23 12:30 | 8.49 | 8.42
2017-03-23 13:00 | 7.21 | 7.12
2017-03-23 13:30 | 7.36 | 7.27
2017-03-23 14:00 | 8.01 | 7.91
2017-03-23 14:30 | 8.16 | 8.05
2017-03-23 15:00 | 8.53 | 8.42
2017-03-23 15:30 | 9.34 | 9.23
2017-03-23 16:00 | 9.73 | 9.63
2017-03-23 16:30 | 10.33 | 10.24
2017-03-23 17:00 | 11.06 | 10.98
2017-03-23 17:30 | 11.51 | 11.43
2017-03-23 18:00 | 11.97 | 11.89
2017-03-23 18:30 | 12.84 | 12.71
2017-03-23 19:00 | 13.58 | 13.43
2017-03-23 19:30 | 13.25 | 13.11
2017-03-23 20:00 | 13.05 | 12.92
2017-03-23 20:30 | 12.84 | 12.73
2017-03-23 21:00 | 12.06 | 11.96
2017-03-23 21:30 | 11.01 | 10.93
2017-03-23 22:00 | 10.09 | 10.03
2017-03-23 22:30 | 9.57 | 9.53
2017-03-23 23:00 | 9.06 | 9.03
2017-03-23 23:30 | 8.17 | 8.14
2017-03-24 | 7.14 | 7.12
2017-03-24 00:30 | 6.52 | 6.5
2017-03-24 01:00 | 6.25 | 6.23
2017-03-24 01:30 | 5.91 | 5.9
2017-03-24 02:00 | 5.67 | 5.66
2017-03-24 02:30 | 5.56 | 5.54
2017-03-24 03:00 | 5.48 | 5.47
2017-03-24 03:30 | 5.46 | 5.45
2017-03-24 04:00 | 5.43 | 5.42
2017-03-24 04:30 | 5.55 | 5.53
2017-03-24 05:00 | 5.7 | 5.68
2017-03-24 05:30 | 5.96 | 5.94
2017-03-24 06:00 | 6.2 | 6.18
2017-03-24 06:30 | 6.48 | 6.47
2017-03-24 07:00 | 6.81 | 6.8
2017-03-24 07:30 | 7.12 | 7.11
2017-03-24 08:00 | 7.7 | 7.69
2017-03-24 08:30 | 7.26 | 7.24
2017-03-24 09:00 | 6.29 | 6.25
2017-03-24 09:30 | 6.28 | 6.21
2017-03-24 10:00 | 6.27 | 6.18
2017-03-24 10:30 | 6.42 | 6.3
2017-03-24 11:00 | 7.55 | 7.44
2017-03-24 11:30 | 8.27 | 8.16
2017-03-24 12:00 | 7.86 | 7.73
2017-03-24 12:30 | 8.19 | 8.06
2017-03-24 13:00 | 8.72 | 8.59
2017-03-24 13:30 | 8.41 | 8.26
2017-03-24 14:00 | 8.82 | 8.65
2017-03-24 14:30 | 9.22 | 9.05
2017-03-24 15:00 | 9.33 | 9.16
2017-03-24 15:30 | 9.86 | 9.71
2017-03-24 16:00 | 10.39 | 10.24
2017-03-24 16:30 | 11.5 | 11.35
2017-03-24 17:00 | 11.94 | 11.81
2017-03-24 17:30 | 12.05 | 11.94
2017-03-24 18:00 | 12.12 | 12.01
2017-03-24 18:30 | 12.85 | 12.7
2017-03-24 19:00 | 13.15 | 13.01
2017-03-24 19:30 | 12.89 | 12.75
2017-03-24 20:00 | 12.69 | 12.57
2017-03-24 20:30 | 12.29 | 12.18
2017-03-24 21:00 | 11.48 | 11.39
2017-03-24 21:30 | 10.68 | 10.6
2017-03-24 22:00 | 9.66 | 9.61
2017-03-24 22:30 | 9.34 | 9.3
2017-03-24 23:00 | 8.97 | 8.95
2017-03-24 23:30 | 7.93 | 7.91
2017-03-25 | 7.07 | 7.05
2017-03-25 00:30 | 6.41 | 6.4
2017-03-25 01:00 | 6.16 | 6.15
2017-03-25 01:30 | 5.77 | 5.76
2017-03-25 02:00 | 5.34 | 5.33
2017-03-25 02:30 | 5.23 | 5.22
2017-03-25 03:00 | 5.1 | 5.09
2017-03-25 03:30 | 5.05 | 5.04
2017-03-25 04:00 | 5.01 | 5
2017-03-25 04:30 | 5.1 | 5.08
2017-03-25 05:00 | 5.1 | 5.08
2017-03-25 05:30 | 5.13 | 5.11
2017-03-25 06:00 | 5.07 | 5.05
2017-03-25 06:30 | 5.28 | 5.27
2017-03-25 07:00 | 5.21 | 5.2
2017-03-25 07:30 | 5.58 | 5.56
2017-03-25 08:00 | 5.61 | 5.58
2017-03-25 08:30 | 5.92 | 5.9
2017-03-25 09:00 | 5.97 | 5.93
2017-03-25 09:30 | 6.56 | 6.52
2017-03-25 10:00 | 6.72 | 6.67
2017-03-25 10:30 | 6.22 | 6.15
2017-03-25 11:00 | 6.61 | 6.54
2017-03-25 11:30 | 7.35 | 7.28
2017-03-25 12:00 | 7.73 | 7.64
2017-03-25 12:30 | 8.68 | 8.61
2017-03-25 13:00 | 7.59 | 7.5
2017-03-25 13:30 | 7.13 | 7.02
2017-03-25 14:00 | 7.7 | 7.58
2017-03-25 14:30 | 8.38 | 8.27
2017-03-25 15:00 | 8.64 | 8.53
2017-03-25 15:30 | 8.99 | 8.88
2017-03-25 16:00 | 9.71 | 9.61
2017-03-25 16:30 | 10.83 | 10.72
2017-03-25 17:00 | 10.93 | 10.85
2017-03-25 17:30 | 10.96 | 10.89
2017-03-25 18:00 | 11.05 | 10.98
2017-03-25 18:30 | 11.54 | 11.44
2017-03-25 19:00 | 11.68 | 11.59
2017-03-25 19:30 | 11.21 | 11.13
2017-03-25 20:00 | 10.95 | 10.88
2017-03-25 20:30 | 10.67 | 10.61
2017-03-25 21:00 | 9.99 | 9.93
2017-03-25 21:30 | 9.44 | 9.39
2017-03-25 22:00 | 8.95 | 8.91
2017-03-25 22:30 | 8.7 | 8.68
2017-03-25 23:00 | 8.51 | 8.49
2017-03-25 23:30 | 7.61 | 7.59
2017-03-26 | 6.76 | 6.74
2017-03-26 00:30 | 6.1 | 6.08
2017-03-26 01:00 | 5.96 | 5.94
2017-03-26 01:30 | 5.56 | 5.55
2017-03-26 02:00 | 5.27 | 5.26
2017-03-26 02:30 | 4.98 | 4.97
2017-03-26 03:00 | 4.87 | 4.85
2017-03-26 03:30 | 4.95 | 4.93
2017-03-26 04:00 | 4.8 | 4.79
2017-03-26 04:30 | 4.78 | 4.77
2017-03-26 05:00 | 4.7 | 4.68
2017-03-26 05:30 | 4.75 | 4.74
2017-03-26 06:00 | 4.7 | 4.68
2017-03-26 06:30 | 4.78 | 4.77
2017-03-26 07:00 | 4.72 | 4.7
2017-03-26 07:30 | 4.91 | 4.9
2017-03-26 08:00 | 5.13 | 5.11
2017-03-26 08:30 | 5.77 | 5.75
2017-03-26 09:00 | 5.82 | 5.79
2017-03-26 09:30 | 6.35 | 6.32
2017-03-26 10:00 | 6.23 | 6.18
2017-03-26 10:30 | 6.59 | 6.53
2017-03-26 11:00 | 6.45 | 6.38
2017-03-26 11:30 | 6.38 | 6.27
2017-03-26 12:00 | 6.87 | 6.73
2017-03-26 12:30 | 7.55 | 7.4
2017-03-26 13:00 | 9.13 | 8.98
2017-03-26 13:30 | 10.17 | 10.02
2017-03-26 14:00 | 10.6 | 10.44
2017-03-26 14:30 | 10.79 | 10.61
2017-03-26 15:00 | 12.4 | 12.22
2017-03-26 15:30 | 12.38 | 12.19
2017-03-26 16:00 | 13.07 | 12.89
2017-03-26 16:30 | 13.94 | 13.76
2017-03-26 17:00 | 14.82 | 14.65
2017-03-26 17:30 | 15.08 | 14.93
2017-03-26 18:00 | 15.09 | 14.92
2017-03-26 18:30 | 15.38 | 15.18
2017-03-26 19:00 | 15 | 14.81
2017-03-26 19:30 | 14.15 | 13.98
2017-03-26 20:00 | 13.68 | 13.52
2017-03-26 20:30 | 13.04 | 12.91
2017-03-26 21:00 | 12.22 | 12.1
2017-03-26 21:30 | 11.25 | 11.16
2017-03-26 22:00 | 10.2 | 10.13
2017-03-26 22:30 | 9.61 | 9.56
2017-03-26 23:00 | 9.07 | 9.03
2017-03-26 23:30 | 7.85 | 7.82
2017-03-27 | 7 | 6.98
2017-03-27 00:30 | 6.46 | 6.44
2017-03-27 01:00 | 6.17 | 6.14
2017-03-27 01:30 | 5.74 | 5.72
2017-03-27 02:00 | 5.44 | 5.42
2017-03-27 02:30 | 5.32 | 5.3
2017-03-27 03:00 | 5.28 | 5.26
2017-03-27 03:30 | 5.3 | 5.28
2017-03-27 04:00 | 5.32 | 5.3
2017-03-27 04:30 | 5.46 | 5.44
2017-03-27 05:00 | 5.47 | 5.45
2017-03-27 05:30 | 5.78 | 5.75
2017-03-27 06:00 | 6.51 | 6.5
2017-03-27 06:30 | 7.03 | 7.03
2017-03-27 07:00 | 7.18 | 7.18
2017-03-27 07:30 | 7.59 | 7.58
2017-03-27 08:00 | 7.48 | 7.46
2017-03-27 08:30 | 6.85 | 6.82
2017-03-27 09:00 | 7.01 | 6.97
2017-03-27 09:30 | 6.65 | 6.59
2017-03-27 10:00 | 6.12 | 6.03
2017-03-27 10:30 | 6.06 | 5.96
2017-03-27 11:00 | 6.72 | 6.61
2017-03-27 11:30 | 7.06 | 6.93
2017-03-27 12:00 | 7.57 | 7.43
2017-03-27 12:30 | 8.31 | 8.17
2017-03-27 13:00 | 9.49 | 9.37
2017-03-27 13:30 | 9.74 | 9.63
2017-03-27 14:00 | 9.87 | 9.75
2017-03-27 14:30 | 9.27 | 9.12
2017-03-27 15:00 | 9.56 | 9.42
2017-03-27 15:30 | 10.61 | 10.49
2017-03-27 16:00 | 10.55 | 10.42
2017-03-27 16:30 | 11.49 | 11.35
2017-03-27 17:00 | 12.73 | 12.6
2017-03-27 17:30 | 12.95 | 12.83
2017-03-27 18:00 | 13.01 | 12.91
2017-03-27 18:30 | 13.59 | 13.45
2017-03-27 19:00 | 14.09 | 13.93
2017-03-27 19:30 | 13.49 | 13.35
2017-03-27 20:00 | 13.02 | 12.9
2017-03-27 20:30 | 12.61 | 12.5
2017-03-27 21:00 | 11.67 | 11.58
2017-03-27 21:30 | 10.74 | 10.68
2017-03-27 22:00 | 9.58 | 9.53
2017-03-27 22:30 | 8.89 | 8.86
2017-03-27 23:00 | 8.41 | 8.38
2017-03-27 23:30 | 7.32 | 7.3
2017-03-28 | 6.49 | 6.48
2017-03-28 00:30 | 5.84 | 5.82
2017-03-28 01:00 | 5.6 | 5.58
2017-03-28 01:30 | 5.29 | 5.28
2017-03-28 02:00 | 5.1 | 5.09
2017-03-28 02:30 | 4.92 | 4.9
2017-03-28 03:00 | 4.79 | 4.78
2017-03-28 03:30 | 4.78 | 4.77
2017-03-28 04:00 | 4.87 | 4.86
2017-03-28 04:30 | 4.93 | 4.92
2017-03-28 05:00 | 5.06 | 5.04
2017-03-28 05:30 | 5.52 | 5.5
2017-03-28 06:00 | 6.28 | 6.27
2017-03-28 06:30 | 6.63 | 6.63
2017-03-28 07:00 | 6.64 | 6.64
2017-03-28 07:30 | 6.92 | 6.92
2017-03-28 08:00 | 6.63 | 6.63
2017-03-28 08:30 | 6.13 | 6.11
2017-03-28 09:00 | 5.78 | 5.74
2017-03-28 09:30 | 5.95 | 5.9
2017-03-28 10:00 | 5.81 | 5.75
2017-03-28 10:30 | 6.09 | 5.99
2017-03-28 11:00 | 6.34 | 6.22
2017-03-28 11:30 | 6.56 | 6.44
2017-03-28 12:00 | 6.76 | 6.62
2017-03-28 12:30 | 7.04 | 6.89
2017-03-28 13:00 | 7.54 | 7.38
2017-03-28 13:30 | 8.15 | 7.98
2017-03-28 14:00 | 8.62 | 8.45
2017-03-28 14:30 | 9.18 | 9.01
2017-03-28 15:00 | 10.1 | 9.94
2017-03-28 15:30 | 11.03 | 10.87
2017-03-28 16:00 | 12 | 11.82
2017-03-28 16:30 | 12.67 | 12.49
2017-03-28 17:00 | 13.55 | 13.39
2017-03-28 17:30 | 13.69 | 13.55
2017-03-28 18:00 | 13.53 | 13.4
2017-03-28 18:30 | 14.22 | 14.03
2017-03-28 19:00 | 14.58 | 14.39
2017-03-28 19:30 | 14.11 | 13.94
2017-03-28 20:00 | 13.8 | 13.65
2017-03-28 20:30 | 13.4 | 13.27
2017-03-28 21:00 | 12.36 | 12.27
2017-03-28 21:30 | 11.26 | 11.18
2017-03-28 22:00 | 10.06 | 9.99
2017-03-28 22:30 | 9.39 | 9.34
2017-03-28 23:00 | 8.89 | 8.86
2017-03-28 23:30 | 7.65 | 7.62
2017-03-29 | 6.79 | 6.77
2017-03-29 00:30 | 6.1 | 6.08
2017-03-29 01:00 | 5.94 | 5.92
2017-03-29 01:30 | 5.76 | 5.74
2017-03-29 02:00 | 5.42 | 5.4
2017-03-29 02:30 | 5.28 | 5.26
2017-03-29 03:00 | 5.2 | 5.18
2017-03-29 03:30 | 5.19 | 5.17
2017-03-29 04:00 | 5.24 | 5.22
2017-03-29 04:30 | 5.26 | 5.24
2017-03-29 05:00 | 5.33 | 5.31
2017-03-29 05:30 | 5.77 | 5.75
2017-03-29 06:00 | 6.53 | 6.52
2017-03-29 06:30 | 6.97 | 6.96
2017-03-29 07:00 | 7.16 | 7.15
2017-03-29 07:30 | 7.49 | 7.49
2017-03-29 08:00 | 7.28 | 7.27
2017-03-29 08:30 | 6.66 | 6.63
2017-03-29 09:00 | 6.15 | 6.11
2017-03-29 09:30 | 7.08 | 7.01
2017-03-29 10:00 | 8.65 | 8.58
2017-03-29 10:30 | 9 | 8.93
2017-03-29 11:00 | 9.64 | 9.6
2017-03-29 11:30 | 10.39 | 10.31
2017-03-29 12:00 | 9.46 | 9.39
2017-03-29 12:30 | 8.67 | 8.57
2017-03-29 13:00 | 8.66 | 8.55
2017-03-29 13:30 | 9.27 | 9.15
2017-03-29 14:00 | 10.04 | 9.93
2017-03-29 14:30 | 10.23 | 10.13
2017-03-29 15:00 | 10.14 | 10.05
2017-03-29 15:30 | 10.32 | 10.24
2017-03-29 16:00 | 10.48 | 10.39
2017-03-29 16:30 | 11.42 | 11.34
2017-03-29 17:00 | 11.65 | 11.57
2017-03-29 17:30 | 12.55 | 12.45
2017-03-29 18:00 | 12.64 | 12.53
2017-03-29 18:30 | 13.33 | 13.2
2017-03-29 19:00 | 13.69 | 13.55
2017-03-29 19:30 | 13.32 | 13.17
2017-03-29 20:00 | 13.26 | 13.14
2017-03-29 20:30 | 13.13 | 13.01
2017-03-29 21:00 | 12.19 | 12.09
2017-03-29 21:30 | 11.05 | 10.97
2017-03-29 22:00 | 10.08 | 10.01
2017-03-29 22:30 | 9.39 | 9.35
2017-03-29 23:00 | 8.95 | 8.91
2017-03-29 23:30 | 7.9 | 7.87
2017-03-30 | 7.08 | 7.04
2017-03-30 00:30 | 6.57 | 6.53
2017-03-30 01:00 | 6.4 | 6.36
2017-03-30 01:30 | 5.98 | 5.95
2017-03-30 02:00 | 5.82 | 5.78
2017-03-30 02:30 | 5.59 | 5.56
2017-03-30 03:00 | 5.4 | 5.36
2017-03-30 03:30 | 5.47 | 5.44
2017-03-30 04:00 | 5.48 | 5.44
2017-03-30 04:30 | 5.49 | 5.46
2017-03-30 05:00 | 5.71 | 5.67
2017-03-30 05:30 | 6.05 | 6.01
2017-03-30 06:00 | 6.68 | 6.65
2017-03-30 06:30 | 7.28 | 7.25
2017-03-30 07:00 | 7.65 | 7.63
2017-03-30 07:30 | 8.4 | 8.37
2017-03-30 08:00 | 8.49 | 8.47
2017-03-30 08:30 | 8.11 | 8.09
2017-03-30 09:00 | 8.18 | 8.15
2017-03-30 09:30 | 8.84 | 8.81
2017-03-30 10:00 | 8.67 | 8.63
2017-03-30 10:30 | 8.73 | 8.69
2017-03-30 11:00 | 9.18 | 9.15
2017-03-30 11:30 | 9.74 | 9.71
2017-03-30 12:00 | 9.69 | 9.66
2017-03-30 12:30 | 9.76 | 9.72
2017-03-30 13:00 | 10.08 | 10.03
2017-03-30 13:30 | 10.15 | 10.11
2017-03-30 14:00 | 10.61 | 10.57
2017-03-30 14:30 | 10.55 | 10.51
2017-03-30 15:00 | 10.32 | 10.28
2017-03-30 15:30 | 10.57 | 10.54
2017-03-30 16:00 | 11.04 | 11.02
2017-03-30 16:30 | 10.87 | 10.84
2017-03-30 17:00 | 11.35 | 11.32
2017-03-30 17:30 | 11.75 | 11.72
2017-03-30 18:00 | 11.92 | 11.89
2017-03-30 18:30 | 12.23 | 12.18
2017-03-30 19:00 | 12.47 | 12.42
2017-03-30 19:30 | 12.14 | 12.1
2017-03-30 20:00 | 11.81 | 11.77
2017-03-30 20:30 | 11.65 | 11.62
2017-03-30 21:00 | 10.97 | 10.94
2017-03-30 21:30 | 10.13 | 10.1
2017-03-30 22:00 | 9.38 | 9.36
2017-03-30 22:30 | 9 | 8.98
2017-03-30 23:00 | 8.7 | 8.67
2017-03-30 23:30 | 7.63 | 7.61
2017-03-31 | 6.73 | 6.72
2017-03-31 00:30 | 6.11 | 6.09
2017-03-31 01:00 | 5.99 | 5.96
2017-03-31 01:30 | 5.69 | 5.67
2017-03-31 02:00 | 5.59 | 5.57
2017-03-31 02:30 | 5.42 | 5.4
2017-03-31 03:00 | 5.31 | 5.29
2017-03-31 03:30 | 5.29 | 5.26
2017-03-31 04:00 | 5.31 | 5.29
2017-03-31 04:30 | 5.34 | 5.32
2017-03-31 05:00 | 5.48 | 5.45
2017-03-31 05:30 | 5.65 | 5.62
2017-03-31 06:00 | 5.79 | 5.76
2017-03-31 06:30 | 5.93 | 5.9
2017-03-31 07:00 | 5.75 | 5.72
2017-03-31 07:30 | 6.11 | 6.08
2017-03-31 08:00 | 5.68 | 5.64
2017-03-31 08:30 | 6.48 | 6.44
2017-03-31 09:00 | 6.25 | 6.21
2017-03-31 09:30 | 6.05 | 5.99
2017-03-31 10:00 | 6.16 | 6.11
2017-03-31 10:30 | 5.21 | 5.14
2017-03-31 11:00 | 4.8 | 4.71
2017-03-31 11:30 | 4.55 | 4.45
2017-03-31 12:00 | 4.89 | 4.8
2017-03-31 12:30 | 5.51 | 5.44
2017-03-31 13:00 | 5.95 | 5.88
2017-03-31 13:30 | 7.32 | 7.26
2017-03-31 14:00 | 7.1 | 7.04
2017-03-31 14:30 | 7.41 | 7.35
2017-03-31 15:00 | 7.82 | 7.77
2017-03-31 15:30 | 7.89 | 7.84
2017-03-31 16:00 | 8.17 | 8.12
2017-03-31 16:30 | 8.46 | 8.42
2017-03-31 17:00 | 8.7 | 8.66
2017-03-31 17:30 | 9.33 | 9.29
2017-03-31 18:00 | 9.69 | 9.65
2017-03-31 18:30 | 10.58 | 10.52
2017-03-31 19:00 | 10.89 | 10.83
2017-03-31 19:30 | 10.53 | 10.48
2017-03-31 20:00 | 10.31 | 10.27
2017-03-31 20:30 | 10.1 | 10.06
2017-03-31 21:00 | 9.48 | 9.44
2017-03-31 21:30 | 8.8 | 8.76
2017-03-31 22:00 | 8.16 | 8.13
2017-03-31 22:30 | 7.85 | 7.83
2017-03-31 23:00 | 7.83 | 7.8
2017-03-31 23:30 | 6.83 | 6.81
2017-04-01 | 6.08 | 6.05
2017-04-01 00:30 | 5.48 | 5.46
2017-04-01 01:00 | 5.14 | 5.12
2017-04-01 01:30 | 4.91 | 4.89
2017-04-01 02:00 | 4.61 | 4.58
2017-04-01 02:30 | 4.38 | 4.36
2017-04-01 03:00 | 4.3 | 4.27
2017-04-01 03:30 | 4.36 | 4.34
2017-04-01 04:00 | 4.25 | 4.22
2017-04-01 04:30 | 4.3 | 4.27
2017-04-01 05:00 | 4.34 | 4.31
2017-04-01 05:30 | 4.4 | 4.36
2017-04-01 06:00 | 4.38 | 4.35
2017-04-01 06:30 | 4.5 | 4.47
2017-04-01 07:00 | 4.67 | 4.63
2017-04-01 07:30 | 4.64 | 4.6
2017-04-01 08:00 | 4.84 | 4.79
2017-04-01 08:30 | 4.96 | 4.92
2017-04-01 09:00 | 4.76 | 4.7
2017-04-01 09:30 | 4.77 | 4.7
2017-04-01 10:00 | 4.79 | 4.72
2017-04-01 10:30 | 4.5 | 4.42
2017-04-01 11:00 | 4.62 | 4.54
2017-04-01 11:30 | 4.95 | 4.86
2017-04-01 12:00 | 4.92 | 4.84
2017-04-01 12:30 | 4.91 | 4.82
2017-04-01 13:00 | 5.02 | 4.92
2017-04-01 13:30 | 5.09 | 5
2017-04-01 14:00 | 5.81 | 5.72
2017-04-01 14:30 | 6.14 | 6.06
2017-04-01 15:00 | 6.72 | 6.64
2017-04-01 15:30 | 7.52 | 7.45
2017-04-01 16:00 | 8.23 | 8.16
2017-04-01 16:30 | 8.88 | 8.82
2017-04-01 17:00 | 9.45 | 9.39
2017-04-01 17:30 | 9.63 | 9.59
2017-04-01 18:00 | 9.86 | 9.82
2017-04-01 18:30 | 10.5 | 10.44
2017-04-01 19:00 | 10.63 | 10.58
2017-04-01 19:30 | 10.07 | 10.02
2017-04-01 20:00 | 9.91 | 9.87
2017-04-01 20:30 | 9.66 | 9.63
2017-04-01 21:00 | 9.14 | 9.11
2017-04-01 21:30 | 8.49 | 8.46
2017-04-01 22:00 | 7.97 | 7.94
2017-04-01 22:30 | 7.81 | 7.78
2017-04-01 23:00 | 7.68 | 7.65
2017-04-01 23:30 | 6.78 | 6.76
2017-04-02 | 5.99 | 5.97
2017-04-02 00:30 | 5.36 | 5.34
2017-04-02 01:00 | 5.26 | 5.23
2017-04-02 01:30 | 4.92 | 4.9
2017-04-02 02:00 | 4.68 | 4.66
2017-04-02 02:30 | 4.4 | 4.37
2017-04-02 03:00 | 4.29 | 4.26
2017-04-02 03:30 | 4.31 | 4.28
2017-04-02 04:00 | 4.25 | 4.22
2017-04-02 04:30 | 4.29 | 4.25
2017-04-02 05:00 | 4.27 | 4.24
2017-04-02 05:30 | 4.26 | 4.23
2017-04-02 06:00 | 4.35 | 4.32
2017-04-02 06:30 | 4.42 | 4.39
2017-04-02 07:00 | 4.51 | 4.48
2017-04-02 07:30 | 4.57 | 4.54
2017-04-02 08:00 | 4.61 | 4.58
2017-04-02 08:30 | 4.93 | 4.9
2017-04-02 09:00 | 4.5 | 4.47
2017-04-02 09:30 | 5.06 | 5.01
2017-04-02 10:00 | 5.79 | 5.75
2017-04-02 10:30 | 5.71 | 5.66
2017-04-02 11:00 | 5.34 | 5.28
2017-04-02 11:30 | 5.57 | 5.51
2017-04-02 12:00 | 6.18 | 6.14
2017-04-02 12:30 | 6.1 | 6.05
2017-04-02 13:00 | 5.61 | 5.56
2017-04-02 13:30 | 5.29 | 5.23
2017-04-02 14:00 | 5.88 | 5.83
2017-04-02 14:30 | 5.41 | 5.35
2017-04-02 15:00 | 6.36 | 6.31
2017-04-02 15:30 | 6.41 | 6.36
2017-04-02 16:00 | 7.2 | 7.15
2017-04-02 16:30 | 8.04 | 7.99
2017-04-02 17:00 | 8.72 | 8.68
2017-04-02 17:30 | 9.52 | 9.48
2017-04-02 18:00 | 9.87 | 9.84
2017-04-02 18:30 | 10.66 | 10.62
2017-04-02 19:00 | 10.8 | 10.76
2017-04-02 19:30 | 10.17 | 10.15
2017-04-02 20:00 | 9.84 | 9.81
2017-04-02 20:30 | 9.61 | 9.59
2017-04-02 21:00 | 9.03 | 9
2017-04-02 21:30 | 8.35 | 8.32
2017-04-02 22:00 | 7.75 | 7.73
2017-04-02 22:30 | 7.42 | 7.4
2017-04-02 23:00 | 7.21 | 7.19
2017-04-02 23:30 | 6.42 | 6.4
2017-04-03 | 5.55 | 5.53
2017-04-03 00:30 | 4.99 | 4.97
2017-04-03 01:00 | 4.74 | 4.72
2017-04-03 01:30 | 4.35 | 4.33
2017-04-03 02:00 | 4.19 | 4.17
2017-04-03 02:30 | 4.01 | 3.98
2017-04-03 03:00 | 3.88 | 3.86
2017-04-03 03:30 | 4.01 | 3.98
2017-04-03 04:00 | 3.98 | 3.95
2017-04-03 04:30 | 4.17 | 4.15
2017-04-03 05:00 | 4.3 | 4.27
2017-04-03 05:30 | 4.71 | 4.69
2017-04-03 06:00 | 5.42 | 5.41
2017-04-03 06:30 | 5.66 | 5.65
2017-04-03 07:00 | 6.31 | 6.29
2017-04-03 07:30 | 6.83 | 6.82
2017-04-03 08:00 | 6.23 | 6.22
2017-04-03 08:30 | 5.93 | 5.92
2017-04-03 09:00 | 5.53 | 5.52
2017-04-03 09:30 | 5.3 | 5.28
2017-04-03 10:00 | 5.51 | 5.49
2017-04-03 10:30 | 6.54 | 6.53
2017-04-03 11:00 | 5.25 | 5.24
2017-04-03 11:30 | 5.43 | 5.42
2017-04-03 12:00 | 6.05 | 6.04
2017-04-03 12:30 | 7.12 | 7.11
2017-04-03 13:00 | 7.46 | 7.45
2017-04-03 13:30 | 6.83 | 6.81
2017-04-03 14:00 | 5.68 | 5.65
2017-04-03 14:30 | 7.22 | 7.2
2017-04-03 15:00 | 7.64 | 7.62
2017-04-03 15:30 | 7.81 | 7.8
2017-04-03 16:00 | 7.51 | 7.5
2017-04-03 16:30 | 8.52 | 8.51
2017-04-03 17:00 | 9.59 | 9.58
2017-04-03 17:30 | 10.63 | 10.62
2017-04-03 18:00 | 11.59 | 11.58
2017-04-03 18:30 | 12.45 | 12.42
2017-04-03 19:00 | 12.53 | 12.51
2017-04-03 19:30 | 11.93 | 11.9
2017-04-03 20:00 | 11.76 | 11.74
2017-04-03 20:30 | 11.61 | 11.6
2017-04-03 21:00 | 10.96 | 10.95
2017-04-03 21:30 | 10.04 | 10.03
2017-04-03 22:00 | 9.29 | 9.28
2017-04-03 22:30 | 8.8 | 8.8
2017-04-03 23:00 | 8.24 | 8.23
2017-04-03 23:30 | 7.31 | 7.3
2017-04-04 | 6.57 | 6.56
2017-04-04 00:30 | 5.9 | 5.89
2017-04-04 01:00 | 5.66 | 5.65
2017-04-04 01:30 | 5.38 | 5.37
2017-04-04 02:00 | 5.2 | 5.19
2017-04-04 02:30 | 5.08 | 5.06
2017-04-04 03:00 | 4.99 | 4.97
2017-04-04 03:30 | 5.32 | 5.3
2017-04-04 04:00 | 5.36 | 5.35
2017-04-04 04:30 | 5.54 | 5.52
2017-04-04 05:00 | 5.77 | 5.76
2017-04-04 05:30 | 6.02 | 6.01
2017-04-04 06:00 | 6.57 | 6.56
2017-04-04 06:30 | 6.75 | 6.73
2017-04-04 07:00 | 7.12 | 7.1
2017-04-04 07:30 | 6.9 | 6.89
2017-04-04 08:00 | 6.24 | 6.23
2017-04-04 08:30 | 5.83 | 5.82
2017-04-04 09:00 | 5.49 | 5.48
2017-04-04 09:30 | 5.28 | 5.28
2017-04-04 10:00 | 4.87 | 4.86
2017-04-04 10:30 | 5.23 | 5.21
2017-04-04 11:00 | 5.64 | 5.62
2017-04-04 11:30 | 5.4 | 5.37
2017-04-04 12:00 | 6.78 | 6.77
2017-04-04 12:30 | 6.22 | 6.21
2017-04-04 13:00 | 7.61 | 7.6
2017-04-04 13:30 | 7.21 | 7.19
2017-04-04 14:00 | 7.01 | 7
2017-04-04 14:30 | 7.7 | 7.69
2017-04-04 15:00 | 6.71 | 6.7
2017-04-04 15:30 | 7.57 | 7.56
2017-04-04 16:00 | 8.23 | 8.22
2017-04-04 16:30 | 8.31 | 8.3
2017-04-04 17:00 | 8.95 | 8.94
2017-04-04 17:30 | 10.11 | 10.1
2017-04-04 18:00 | 10.85 | 10.84
2017-04-04 18:30 | 12.02 | 11.99
2017-04-04 19:00 | 12.41 | 12.38
2017-04-04 19:30 | 11.72 | 11.7
2017-04-04 20:00 | 11.64 | 11.62
2017-04-04 20:30 | 11.54 | 11.53
2017-04-04 21:00 | 10.99 | 10.98
2017-04-04 21:30 | 10.07 | 10.06
2017-04-04 22:00 | 9.28 | 9.27
2017-04-04 22:30 | 8.48 | 8.47
2017-04-04 23:00 | 8.06 | 8.05
2017-04-04 23:30 | 7.12 | 7.11
2017-04-05 | 6.32 | 6.31
2017-04-05 00:30 | 5.75 | 5.74
2017-04-05 01:00 | 5.53 | 5.51
2017-04-05 01:30 | 5.29 | 5.27
2017-04-05 02:00 | 5.1 | 5.08
2017-04-05 02:30 | 5.01 | 5
2017-04-05 03:00 | 4.88 | 4.86
2017-04-05 03:30 | 4.98 | 4.97
2017-04-05 04:00 | 4.94 | 4.92
2017-04-05 04:30 | 5.12 | 5.11
2017-04-05 05:00 | 5.39 | 5.38
2017-04-05 05:30 | 5.84 | 5.83
2017-04-05 06:00 | 6.55 | 6.54
2017-04-05 06:30 | 6.8 | 6.78
2017-04-05 07:00 | 6.61 | 6.59
2017-04-05 07:30 | 6.42 | 6.4
2017-04-05 08:00 | 6.16 | 6.15
2017-04-05 08:30 | 5.91 | 5.9
2017-04-05 09:00 | 5.65 | 5.64
2017-04-05 09:30 | 5 | 4.99
2017-04-05 10:00 | 5.11 | 5.1
2017-04-05 10:30 | 5 | 4.98
2017-04-05 11:00 | 5.34 | 5.32
2017-04-05 11:30 | 5.34 | 5.33
2017-04-05 12:00 | 5.14 | 5.12
2017-04-05 12:30 | 4.62 | 4.6
2017-04-05 13:00 | 5.31 | 5.3
2017-04-05 13:30 | 6.38 | 6.37
2017-04-05 14:00 | 7.05 | 7.04
2017-04-05 14:30 | 7.94 | 7.93
2017-04-05 15:00 | 7.54 | 7.53
2017-04-05 15:30 | 7.3 | 7.29
2017-04-05 16:00 | 8.55 | 8.54
2017-04-05 16:30 | 8.82 | 8.82
2017-04-05 17:00 | 8.89 | 8.88
2017-04-05 17:30 | 10.26 | 10.26
2017-04-05 18:00 | 11.29 | 11.29
2017-04-05 18:30 | 11.99 | 11.97
2017-04-05 19:00 | 12.24 | 12.21
2017-04-05 19:30 | 11.76 | 11.75
2017-04-05 20:00 | 11.5 | 11.49
2017-04-05 20:30 | 11.56 | 11.55
2017-04-05 21:00 | 11.05 | 11.04
2017-04-05 21:30 | 10.41 | 10.4
2017-04-05 22:00 | 9.34 | 9.34
2017-04-05 22:30 | 8.72 | 8.71
2017-04-05 23:00 | 8.15 | 8.14
2017-04-05 23:30 | 7.05 | 7.04
2017-04-06 | 6.27 | 6.26
2017-04-06 00:30 | 5.69 | 5.67
2017-04-06 01:00 | 5.37 | 5.36
2017-04-06 01:30 | 5.25 | 5.24
2017-04-06 02:00 | 5.02 | 5
2017-04-06 02:30 | 4.85 | 4.83
2017-04-06 03:00 | 4.85 | 4.83
2017-04-06 03:30 | 4.85 | 4.83
2017-04-06 04:00 | 4.87 | 4.85
2017-04-06 04:30 | 5.06 | 5.05
2017-04-06 05:00 | 5.28 | 5.27
2017-04-06 05:30 | 5.7 | 5.69
2017-04-06 06:00 | 6.46 | 6.45
2017-04-06 06:30 | 6.84 | 6.83
2017-04-06 07:00 | 7.04 | 7.03
2017-04-06 07:30 | 7.22 | 7.21
2017-04-06 08:00 | 7.04 | 7.03
2017-04-06 08:30 | 6.76 | 6.75
2017-04-06 09:00 | 5.59 | 5.57
2017-04-06 09:30 | 6.41 | 6.4
2017-04-06 10:00 | 6.39 | 6.38
2017-04-06 10:30 | 6.1 | 6.09
2017-04-06 11:00 | 6.22 | 6.21
2017-04-06 11:30 | 7.37 | 7.36
2017-04-06 12:00 | 6.74 | 6.73
2017-04-06 12:30 | 6.48 | 6.47
2017-04-06 13:00 | 7.01 | 7.01
2017-04-06 13:30 | 7.65 | 7.64
2017-04-06 14:00 | 7.24 | 7.23
2017-04-06 14:30 | 7.18 | 7.17
2017-04-06 15:00 | 7.63 | 7.62
2017-04-06 15:30 | 7.64 | 7.63
2017-04-06 16:00 | 7.91 | 7.9
2017-04-06 16:30 | 8.9 | 8.89
2017-04-06 17:00 | 9.27 | 9.26
2017-04-06 17:30 | 10.07 | 10.06
2017-04-06 18:00 | 10.87 | 10.86
2017-04-06 18:30 | 11.82 | 11.8
2017-04-06 19:00 | 12.05 | 12.03
2017-04-06 19:30 | 11.65 | 11.63
2017-04-06 20:00 | 11.77 | 11.75
2017-04-06 20:30 | 11.51 | 11.51
2017-04-06 21:00 | 10.98 | 10.98
2017-04-06 21:30 | 10.24 | 10.24
2017-04-06 22:00 | 9.1 | 9.09
2017-04-06 22:30 | 8.55 | 8.54
2017-04-06 23:00 | 8.17 | 8.16
2017-04-06 23:30 | 7.27 | 7.26
2017-04-07 | 6.39 | 6.38
2017-04-07 00:30 | 5.83 | 5.81
2017-04-07 01:00 | 5.56 | 5.55
2017-04-07 01:30 | 5.29 | 5.27
2017-04-07 02:00 | 5.12 | 5.11
2017-04-07 02:30 | 4.99 | 4.97
2017-04-07 03:00 | 4.94 | 4.92
2017-04-07 03:30 | 4.99 | 4.98
2017-04-07 04:00 | 4.99 | 4.96
2017-04-07 04:30 | 5.06 | 5.04
2017-04-07 05:00 | 5.36 | 5.34
2017-04-07 05:30 | 5.67 | 5.66
2017-04-07 06:00 | 5.94 | 5.92
2017-04-07 06:30 | 6.21 | 6.18
2017-04-07 07:00 | 6.13 | 6.09
2017-04-07 07:30 | 5.99 | 5.96
2017-04-07 08:00 | 5.58 | 5.55
2017-04-07 08:30 | 5.36 | 5.34
2017-04-07 09:00 | 5.05 | 5.03
2017-04-07 09:30 | 4.73 | 4.71
2017-04-07 10:00 | 4.49 | 4.46
2017-04-07 10:30 | 4.16 | 4.13
2017-04-07 11:00 | 4.09 | 4.05
2017-04-07 11:30 | 4.32 | 4.28
2017-04-07 12:00 | 4.16 | 4.12
2017-04-07 12:30 | 4.63 | 4.6
2017-04-07 13:00 | 4.88 | 4.85
2017-04-07 13:30 | 5.61 | 5.58
2017-04-07 14:00 | 5.61 | 5.59
2017-04-07 14:30 | 6.54 | 6.52
2017-04-07 15:00 | 6.32 | 6.3
2017-04-07 15:30 | 6.24 | 6.22
2017-04-07 16:00 | 6.54 | 6.52
2017-04-07 16:30 | 8.33 | 8.31
2017-04-07 17:00 | 9.03 | 9.02
2017-04-07 17:30 | 8.95 | 8.93
2017-04-07 18:00 | 8.55 | 8.53
2017-04-07 18:30 | 9.28 | 9.26
2017-04-07 19:00 | 9.75 | 9.73
2017-04-07 19:30 | 9.53 | 9.51
2017-04-07 20:00 | 10.49 | 10.48
2017-04-07 20:30 | 10.33 | 10.32
2017-04-07 21:00 | 9.69 | 9.68
2017-04-07 21:30 | 9.44 | 9.43
2017-04-07 22:00 | 8.58 | 8.57
2017-04-07 22:30 | 7.38 | 7.36
2017-04-07 23:00 | 7.26 | 7.25
2017-04-07 23:30 | 6.42 | 6.41
2017-04-08 | 5.7 | 5.69
2017-04-08 00:30 | 4.95 | 4.94
2017-04-08 01:00 | 4.62 | 4.61
2017-04-08 01:30 | 4.3 | 4.28
2017-04-08 02:00 | 4.02 | 4.01
2017-04-08 02:30 | 3.96 | 3.94
2017-04-08 03:00 | 3.82 | 3.81
2017-04-08 03:30 | 3.82 | 3.8
2017-04-08 04:00 | 3.8 | 3.78
2017-04-08 04:30 | 3.86 | 3.84
2017-04-08 05:00 | 3.89 | 3.87
2017-04-08 05:30 | 3.99 | 3.97
2017-04-08 06:00 | 4.05 | 4.03
2017-04-08 06:30 | 4.17 | 4.13
2017-04-08 07:00 | 4.3 | 4.25
2017-04-08 07:30 | 4.33 | 4.29
2017-04-08 08:00 | 4.29 | 4.26
2017-04-08 08:30 | 4.43 | 4.41
2017-04-08 09:00 | 4.29 | 4.26
2017-04-08 09:30 | 4.04 | 3.99
2017-04-08 10:00 | 3.78 | 3.73
2017-04-08 10:30 | 4.32 | 4.27
2017-04-08 11:00 | 4.32 | 4.27
2017-04-08 11:30 | 4.18 | 4.12
2017-04-08 12:00 | 4.04 | 3.98
2017-04-08 12:30 | 4.69 | 4.63
2017-04-08 13:00 | 5.15 | 5.11
2017-04-08 13:30 | 4.63 | 4.58
2017-04-08 14:00 | 5.33 | 5.29
2017-04-08 14:30 | 6.05 | 6.02
2017-04-08 15:00 | 5.89 | 5.86
2017-04-08 15:30 | 6.58 | 6.54
2017-04-08 16:00 | 6.72 | 6.69
2017-04-08 16:30 | 7.27 | 7.25
2017-04-08 17:00 | 7.71 | 7.68
2017-04-08 17:30 | 8.17 | 8.15
2017-04-08 18:00 | 8.72 | 8.7
2017-04-08 18:30 | 9.33 | 9.31
2017-04-08 19:00 | 9.44 | 9.41
2017-04-08 19:30 | 9 | 8.98
2017-04-08 20:00 | 8.75 | 8.73
2017-04-08 20:30 | 8.66 | 8.64
2017-04-08 21:00 | 8.3 | 8.28
2017-04-08 21:30 | 7.76 | 7.74
2017-04-08 22:00 | 7.46 | 7.44
2017-04-08 22:30 | 7.2 | 7.19
2017-04-08 23:00 | 7.11 | 7.1
2017-04-08 23:30 | 6.28 | 6.26
2017-04-09 | 5.52 | 5.51
2017-04-09 00:30 | 4.89 | 4.88
2017-04-09 01:00 | 4.71 | 4.69
2017-04-09 01:30 | 4.32 | 4.3
2017-04-09 02:00 | 4.03 | 4.01
2017-04-09 02:30 | 3.84 | 3.83
2017-04-09 03:00 | 3.77 | 3.75
2017-04-09 03:30 | 3.86 | 3.84
2017-04-09 04:00 | 3.73 | 3.71
2017-04-09 04:30 | 3.83 | 3.81
2017-04-09 05:00 | 3.83 | 3.81
2017-04-09 05:30 | 3.89 | 3.86
2017-04-09 06:00 | 3.97 | 3.94
2017-04-09 06:30 | 4.14 | 4.1
2017-04-09 07:00 | 4.29 | 4.24
2017-04-09 07:30 | 4.55 | 4.51
2017-04-09 08:00 | 4.46 | 4.42
2017-04-09 08:30 | 4.25 | 4.22
2017-04-09 09:00 | 4.28 | 4.25
2017-04-09 09:30 | 4.22 | 4.18
2017-04-09 10:00 | 4.43 | 4.39
2017-04-09 10:30 | 4.23 | 4.18
2017-04-09 11:00 | 4.53 | 4.49
2017-04-09 11:30 | 4.37 | 4.32
2017-04-09 12:00 | 5.28 | 5.23
2017-04-09 12:30 | 5.25 | 5.2
2017-04-09 13:00 | 4.56 | 4.5
2017-04-09 13:30 | 5.31 | 5.26
2017-04-09 14:00 | 5.59 | 5.54
2017-04-09 14:30 | 5.88 | 5.83
2017-04-09 15:00 | 7.04 | 7.01
2017-04-09 15:30 | 7.68 | 7.65
2017-04-09 16:00 | 8.1 | 8.07
2017-04-09 16:30 | 8.37 | 8.34
2017-04-09 17:00 | 8.62 | 8.6
2017-04-09 17:30 | 9.33 | 9.31
2017-04-09 18:00 | 9.95 | 9.92
2017-04-09 18:30 | 10.61 | 10.57
2017-04-09 19:00 | 10.48 | 10.45
2017-04-09 19:30 | 9.96 | 9.94
2017-04-09 20:00 | 9.64 | 9.62
2017-04-09 20:30 | 9.48 | 9.46
2017-04-09 21:00 | 8.92 | 8.9
2017-04-09 21:30 | 8.21 | 8.2
2017-04-09 22:00 | 7.65 | 7.63
2017-04-09 22:30 | 7.25 | 7.23
2017-04-09 23:00 | 7.07 | 7.06
2017-04-09 23:30 | 6.25 | 6.24
2017-04-10 | 5.5 | 5.49
2017-04-10 00:30 | 4.88 | 4.87
2017-04-10 01:00 | 4.58 | 4.57
2017-04-10 01:30 | 4.28 | 4.26
2017-04-10 02:00 | 4.09 | 4.07
2017-04-10 02:30 | 4 | 3.98
2017-04-10 03:00 | 3.91 | 3.89
2017-04-10 03:30 | 3.92 | 3.9
2017-04-10 04:00 | 3.94 | 3.92
2017-04-10 04:30 | 4.11 | 4.09
2017-04-10 05:00 | 4.3 | 4.28
2017-04-10 05:30 | 4.56 | 4.54
2017-04-10 06:00 | 4.85 | 4.83
2017-04-10 06:30 | 5.16 | 5.13
2017-04-10 07:00 | 5.19 | 5.17
2017-04-10 07:30 | 5.49 | 5.48
2017-04-10 08:00 | 5.56 | 5.54
2017-04-10 08:30 | 5.45 | 5.44
2017-04-10 09:00 | 4.73 | 4.7
2017-04-10 09:30 | 4 | 3.96
2017-04-10 10:00 | 3.91 | 3.85
2017-04-10 10:30 | 4.19 | 4.12
2017-04-10 11:00 | 4.61 | 4.56
2017-04-10 11:30 | 5.14 | 5.1
2017-04-10 12:00 | 4.65 | 4.6
2017-04-10 12:30 | 4.18 | 4.13
2017-04-10 13:00 | 3.88 | 3.82
2017-04-10 13:30 | 4.12 | 4.05
2017-04-10 14:00 | 4.42 | 4.35
2017-04-10 14:30 | 4.73 | 4.66
2017-04-10 15:00 | 5.09 | 5.04
2017-04-10 15:30 | 5.86 | 5.8
2017-04-10 16:00 | 6.52 | 6.48
2017-04-10 16:30 | 7.15 | 7.12
2017-04-10 17:00 | 8.1 | 8.08
2017-04-10 17:30 | 8.7 | 8.68
2017-04-10 18:00 | 9.46 | 9.44
2017-04-10 18:30 | 10.5 | 10.47
2017-04-10 19:00 | 10.55 | 10.53
2017-04-10 19:30 | 10.06 | 10.05
2017-04-10 20:00 | 9.78 | 9.76
2017-04-10 20:30 | 9.46 | 9.44
2017-04-10 21:00 | 8.96 | 8.94
2017-04-10 21:30 | 8.23 | 8.21
2017-04-10 22:00 | 7.53 | 7.51
2017-04-10 22:30 | 7.19 | 7.17
2017-04-10 23:00 | 6.95 | 6.94
2017-04-10 23:30 | 6.05 | 6.04
2017-04-11 | 5.29 | 5.27
2017-04-11 00:30 | 4.69 | 4.67
2017-04-11 01:00 | 4.59 | 4.57
2017-04-11 01:30 | 4.23 | 4.21
2017-04-11 02:00 | 3.89 | 3.86
2017-04-11 02:30 | 3.72 | 3.69
2017-04-11 03:00 | 3.66 | 3.63
2017-04-11 03:30 | 3.69 | 3.66
2017-04-11 04:00 | 3.72 | 3.7
2017-04-11 04:30 | 3.98 | 3.96
2017-04-11 05:00 | 4.15 | 4.12
2017-04-11 05:30 | 4.49 | 4.47
2017-04-11 06:00 | 5.02 | 5.01
2017-04-11 06:30 | 5.33 | 5.3
2017-04-11 07:00 | 5.39 | 5.35
2017-04-11 07:30 | 5.14 | 5.11
2017-04-11 08:00 | 4.74 | 4.71
2017-04-11 08:30 | 4.16 | 4.14
2017-04-11 09:00 | 3.7 | 3.67
2017-04-11 09:30 | 3.35 | 3.32
2017-04-11 10:00 | 3.25 | 3.22
2017-04-11 10:30 | 3.15 | 3.11
2017-04-11 11:00 | 2.96 | 2.91
2017-04-11 11:30 | 2.86 | 2.81
2017-04-11 12:00 | 2.82 | 2.77
2017-04-11 12:30 | 3.01 | 2.97
2017-04-11 13:00 | 3.18 | 3.14
2017-04-11 13:30 | 3.21 | 3.15
2017-04-11 14:00 | 3.43 | 3.37
2017-04-11 14:30 | 3.75 | 3.7
2017-04-11 15:00 | 4.17 | 4.13
2017-04-11 15:30 | 4.88 | 4.84
2017-04-11 16:00 | 5.65 | 5.61
2017-04-11 16:30 | 6.64 | 6.61
2017-04-11 17:00 | 7.66 | 7.63
2017-04-11 17:30 | 8.3 | 8.28
2017-04-11 18:00 | 9.03 | 9.01
2017-04-11 18:30 | 10.29 | 10.26
2017-04-11 19:00 | 10.27 | 10.24
2017-04-11 19:30 | 9.85 | 9.83
2017-04-11 20:00 | 9.87 | 9.85
2017-04-11 20:30 | 9.62 | 9.61
2017-04-11 21:00 | 9.01 | 9
2017-04-11 21:30 | 8.27 | 8.25
2017-04-11 22:00 | 7.53 | 7.52
2017-04-11 22:30 | 7.27 | 7.25
2017-04-11 23:00 | 7.08 | 7.06
2017-04-11 23:30 | 6.19 | 6.18
2017-04-12 | 5.4 | 5.38
2017-04-12 00:30 | 4.93 | 4.91
2017-04-12 01:00 | 4.66 | 4.64
2017-04-12 01:30 | 4.29 | 4.27
2017-04-12 02:00 | 3.98 | 3.96
2017-04-12 02:30 | 3.88 | 3.86
2017-04-12 03:00 | 3.79 | 3.77
2017-04-12 03:30 | 3.89 | 3.86
2017-04-12 04:00 | 3.91 | 3.88
2017-04-12 04:30 | 4.01 | 3.98
2017-04-12 05:00 | 4.31 | 4.29
2017-04-12 05:30 | 4.5 | 4.48
2017-04-12 06:00 | 5.05 | 5.03
2017-04-12 06:30 | 5.5 | 5.48
2017-04-12 07:00 | 5.53 | 5.51
2017-04-12 07:30 | 5.44 | 5.43
2017-04-12 08:00 | 4.94 | 4.93
2017-04-12 08:30 | 4.51 | 4.49
2017-04-12 09:00 | 4.09 | 4.07
2017-04-12 09:30 | 3.88 | 3.86
2017-04-12 10:00 | 3.72 | 3.69
2017-04-12 10:30 | 3.6 | 3.57
2017-04-12 11:00 | 3.47 | 3.42
2017-04-12 11:30 | 3.73 | 3.67
2017-04-12 12:00 | 4.76 | 4.72
2017-04-12 12:30 | 4.89 | 4.85
2017-04-12 13:00 | 4.49 | 4.44
2017-04-12 13:30 | 4.84 | 4.79
2017-04-12 14:00 | 4.77 | 4.71
2017-04-12 14:30 | 5.17 | 5.11
2017-04-12 15:00 | 5.51 | 5.46
2017-04-12 15:30 | 6.23 | 6.18
2017-04-12 16:00 | 7.05 | 7.01
2017-04-12 16:30 | 7.29 | 7.26
2017-04-12 17:00 | 8.27 | 8.25
2017-04-12 17:30 | 8.95 | 8.92
2017-04-12 18:00 | 9.48 | 9.45
2017-04-12 18:30 | 10.18 | 10.14
2017-04-12 19:00 | 10.48 | 10.45
2017-04-12 19:30 | 9.94 | 9.91
2017-04-12 20:00 | 9.8 | 9.77
2017-04-12 20:30 | 9.7 | 9.67
2017-04-12 21:00 | 9.19 | 9.17
2017-04-12 21:30 | 8.54 | 8.51
2017-04-12 22:00 | 7.95 | 7.93
2017-04-12 22:30 | 7.54 | 7.52
2017-04-12 23:00 | 7.33 | 7.31
2017-04-12 23:30 | 6.41 | 6.39
2017-04-13 | 5.57 | 5.54
2017-04-13 00:30 | 5.16 | 5.14
2017-04-13 01:00 | 4.87 | 4.85
2017-04-13 01:30 | 4.54 | 4.52
2017-04-13 02:00 | 4.34 | 4.31
2017-04-13 02:30 | 4.17 | 4.15
2017-04-13 03:00 | 4.07 | 4.05
2017-04-13 03:30 | 4.07 | 4.04
2017-04-13 04:00 | 4.07 | 4.05
2017-04-13 04:30 | 4.24 | 4.22
2017-04-13 05:00 | 4.42 | 4.4
2017-04-13 05:30 | 4.8 | 4.77
2017-04-13 06:00 | 5.6 | 5.59
2017-04-13 06:30 | 5.77 | 5.76
2017-04-13 07:00 | 5.73 | 5.72
2017-04-13 07:30 | 5.49 | 5.48
2017-04-13 08:00 | 5.49 | 5.48
2017-04-13 08:30 | 5.29 | 5.27
2017-04-13 09:00 | 4.94 | 4.92
2017-04-13 09:30 | 4.69 | 4.66
2017-04-13 10:00 | 4.21 | 4.18
2017-04-13 10:30 | 4.21 | 4.16
2017-04-13 11:00 | 3.57 | 3.51
2017-04-13 11:30 | 3.26 | 3.19
2017-04-13 12:00 | 3.37 | 3.29
2017-04-13 12:30 | 4.14 | 4.09
2017-04-13 13:00 | 4.12 | 4.07
2017-04-13 13:30 | 4.43 | 4.38
2017-04-13 14:00 | 4.72 | 4.67
2017-04-13 14:30 | 5.61 | 5.57
2017-04-13 15:00 | 5.92 | 5.89
2017-04-13 15:30 | 6.28 | 6.25
2017-04-13 16:00 | 5.97 | 5.93
2017-04-13 16:30 | 6.49 | 6.46
2017-04-13 17:00 | 7.65 | 7.62
2017-04-13 17:30 | 7.96 | 7.93
2017-04-13 18:00 | 8.55 | 8.53
2017-04-13 18:30 | 9.26 | 9.23
2017-04-13 19:00 | 9.58 | 9.54
2017-04-13 19:30 | 9.37 | 9.34
2017-04-13 20:00 | 9.15 | 9.13
2017-04-13 20:30 | 9.01 | 8.98
2017-04-13 21:00 | 8.7 | 8.68
2017-04-13 21:30 | 8.19 | 8.17
2017-04-13 22:00 | 7.7 | 7.68
2017-04-13 22:30 | 7.53 | 7.51
2017-04-13 23:00 | 7.43 | 7.42
2017-04-13 23:30 | 6.5 | 6.49
2017-04-14 | 5.64 | 5.62
2017-04-14 00:30 | 5.14 | 5.13
2017-04-14 01:00 | 4.91 | 4.89
2017-04-14 01:30 | 4.6 | 4.59
2017-04-14 02:00 | 4.34 | 4.32
2017-04-14 02:30 | 4.11 | 4.09
2017-04-14 03:00 | 4.05 | 4.02
2017-04-14 03:30 | 3.98 | 3.96
2017-04-14 04:00 | 3.89 | 3.87
2017-04-14 04:30 | 3.84 | 3.82
2017-04-14 05:00 | 3.88 | 3.86
2017-04-14 05:30 | 4.01 | 3.99
2017-04-14 06:00 | 4.1 | 4.08
2017-04-14 06:30 | 4.13 | 4.09
2017-04-14 07:00 | 4.29 | 4.23
2017-04-14 07:30 | 4.37 | 4.32
2017-04-14 08:00 | 4.44 | 4.4
2017-04-14 08:30 | 4.52 | 4.49
2017-04-14 09:00 | 3.9 | 3.87
2017-04-14 09:30 | 4.22 | 4.19
2017-04-14 10:00 | 5.15 | 5.13
2017-04-14 10:30 | 5.02 | 5
2017-04-14 11:00 | 4.92 | 4.9
2017-04-14 11:30 | 4.84 | 4.82
2017-04-14 12:00 | 4.33 | 4.31
2017-04-14 12:30 | 5.68 | 5.66
2017-04-14 13:00 | 4.99 | 4.97
2017-04-14 13:30 | 5.53 | 5.52
2017-04-14 14:00 | 4.78 | 4.76
2017-04-14 14:30 | 4.16 | 4.14
2017-04-14 15:00 | 4.87 | 4.85
2017-04-14 15:30 | 5.76 | 5.74
2017-04-14 16:00 | 6.25 | 6.23
2017-04-14 16:30 | 6.31 | 6.29
2017-04-14 17:00 | 7.41 | 7.4
2017-04-14 17:30 | 7.89 | 7.87
2017-04-14 18:00 | 8.4 | 8.39
2017-04-14 18:30 | 8.86 | 8.84
2017-04-14 19:00 | 8.84 | 8.83
2017-04-14 19:30 | 8.41 | 8.39
2017-04-14 20:00 | 8.31 | 8.29
2017-04-14 20:30 | 8.34 | 8.32
2017-04-14 21:00 | 7.89 | 7.87
2017-04-14 21:30 | 7.5 | 7.48
2017-04-14 22:00 | 7.08 | 7.06
2017-04-14 22:30 | 6.98 | 6.96
2017-04-14 23:00 | 6.9 | 6.89
2017-04-14 23:30 | 6.09 | 6.07
2017-04-15 | 5.4 | 5.38
2017-04-15 00:30 | 4.93 | 4.91
2017-04-15 01:00 | 4.72 | 4.7
2017-04-15 01:30 | 4.39 | 4.37
2017-04-15 02:00 | 4.18 | 4.16
2017-04-15 02:30 | 3.98 | 3.96
2017-04-15 03:00 | 3.9 | 3.88
2017-04-15 03:30 | 3.95 | 3.93
2017-04-15 04:00 | 3.85 | 3.82
2017-04-15 04:30 | 3.86 | 3.84
2017-04-15 05:00 | 3.91 | 3.88
2017-04-15 05:30 | 3.95 | 3.92
2017-04-15 06:00 | 4.11 | 4.08
2017-04-15 06:30 | 4.16 | 4.12
2017-04-15 07:00 | 4.25 | 4.2
2017-04-15 07:30 | 4.22 | 4.17
2017-04-15 08:00 | 4.07 | 4.04
2017-04-15 08:30 | 4.07 | 4.03
2017-04-15 09:00 | 4.1 | 4.06
2017-04-15 09:30 | 3.95 | 3.89
2017-04-15 10:00 | 3.86 | 3.8
2017-04-15 10:30 | 4.21 | 4.16
2017-04-15 11:00 | 4.57 | 4.52
2017-04-15 11:30 | 4.89 | 4.84
2017-04-15 12:00 | 4.61 | 4.56
2017-04-15 12:30 | 4.23 | 4.17
2017-04-15 13:00 | 3.67 | 3.6
2017-04-15 13:30 | 3.92 | 3.84
2017-04-15 14:00 | 4.54 | 4.48
2017-04-15 14:30 | 5.09 | 5.03
2017-04-15 15:00 | 5.02 | 4.96
2017-04-15 15:30 | 6.73 | 6.7
2017-04-15 16:00 | 7.18 | 7.15
2017-04-15 16:30 | 7.37 | 7.33
2017-04-15 17:00 | 7.69 | 7.66
2017-04-15 17:30 | 7.96 | 7.94
2017-04-15 18:00 | 8.52 | 8.49
2017-04-15 18:30 | 9.11 | 9.09
2017-04-15 19:00 | 9.01 | 8.98
2017-04-15 19:30 | 8.64 | 8.62
2017-04-15 20:00 | 8.49 | 8.47
2017-04-15 20:30 | 8.31 | 8.29
2017-04-15 21:00 | 8 | 7.97
2017-04-15 21:30 | 7.51 | 7.48
2017-04-15 22:00 | 7.17 | 7.15
2017-04-15 22:30 | 7.04 | 7.02
2017-04-15 23:00 | 7.03 | 7.01
2017-04-15 23:30 | 6.22 | 6.2
2017-04-16 | 5.37 | 5.35
2017-04-16 00:30 | 4.9 | 4.88
2017-04-16 01:00 | 4.61 | 4.59
2017-04-16 01:30 | 4.27 | 4.25
2017-04-16 02:00 | 4.1 | 4.08
2017-04-16 02:30 | 3.97 | 3.95
2017-04-16 03:00 | 3.87 | 3.84
2017-04-16 03:30 | 3.89 | 3.87
2017-04-16 04:00 | 3.74 | 3.72
2017-04-16 04:30 | 3.7 | 3.68
2017-04-16 05:00 | 3.72 | 3.69
2017-04-16 05:30 | 3.8 | 3.78
2017-04-16 06:00 | 3.81 | 3.78
2017-04-16 06:30 | 4.02 | 3.96
2017-04-16 07:00 | 4.09 | 4.02
2017-04-16 07:30 | 4.19 | 4.14
2017-04-16 08:00 | 4.3 | 4.26
2017-04-16 08:30 | 4.04 | 4.01
2017-04-16 09:00 | 4.1 | 4.07
2017-04-16 09:30 | 4.22 | 4.19
2017-04-16 10:00 | 3.83 | 3.79
2017-04-16 10:30 | 3.98 | 3.94
2017-04-16 11:00 | 4.23 | 4.2
2017-04-16 11:30 | 3.75 | 3.71
2017-04-16 12:00 | 4.23 | 4.19
2017-04-16 12:30 | 3.35 | 3.3
2017-04-16 13:00 | 3.75 | 3.69
2017-04-16 13:30 | 5.28 | 5.24
2017-04-16 14:00 | 4.72 | 4.68
2017-04-16 14:30 | 4.83 | 4.79
2017-04-16 15:00 | 5.31 | 5.27
2017-04-16 15:30 | 5.66 | 5.63
2017-04-16 16:00 | 5.91 | 5.88
2017-04-16 16:30 | 6.48 | 6.45
2017-04-16 17:00 | 7.25 | 7.23
2017-04-16 17:30 | 7.76 | 7.74
2017-04-16 18:00 | 8.38 | 8.36
2017-04-16 18:30 | 8.84 | 8.82
2017-04-16 19:00 | 8.9 | 8.88
2017-04-16 19:30 | 8.44 | 8.42
2017-04-16 20:00 | 8.4 | 8.38
2017-04-16 20:30 | 8.29 | 8.27
2017-04-16 21:00 | 7.82 | 7.8
2017-04-16 21:30 | 7.47 | 7.45
2017-04-16 22:00 | 6.94 | 6.92
2017-04-16 22:30 | 6.78 | 6.77
2017-04-16 23:00 | 6.81 | 6.79
2017-04-16 23:30 | 5.94 | 5.93
2017-04-17 | 5.14 | 5.13
2017-04-17 00:30 | 4.62 | 4.6
2017-04-17 01:00 | 4.43 | 4.41
2017-04-17 01:30 | 4.15 | 4.13
2017-04-17 02:00 | 3.93 | 3.91
2017-04-17 02:30 | 3.85 | 3.82
2017-04-17 03:00 | 3.66 | 3.64
2017-04-17 03:30 | 3.75 | 3.73
2017-04-17 04:00 | 3.73 | 3.71
2017-04-17 04:30 | 3.74 | 3.71
2017-04-17 05:00 | 3.75 | 3.73
2017-04-17 05:30 | 3.81 | 3.78
2017-04-17 06:00 | 3.85 | 3.83
2017-04-17 06:30 | 3.89 | 3.83
2017-04-17 07:00 | 3.87 | 3.79
2017-04-17 07:30 | 3.95 | 3.89
2017-04-17 08:00 | 3.92 | 3.87
2017-04-17 08:30 | 3.91 | 3.87
2017-04-17 09:00 | 3.88 | 3.84
2017-04-17 09:30 | 3.93 | 3.9
2017-04-17 10:00 | 3.83 | 3.79
2017-04-17 10:30 | 3.9 | 3.85
2017-04-17 11:00 | 4.07 | 4.03
2017-04-17 11:30 | 4.06 | 4.01
2017-04-17 12:00 | 3.79 | 3.74
2017-04-17 12:30 | 4.15 | 4.1
2017-04-17 13:00 | 4.85 | 4.81
2017-04-17 13:30 | 5.54 | 5.49
2017-04-17 14:00 | 5.07 | 5.02
2017-04-17 14:30 | 6.02 | 5.99
2017-04-17 15:00 | 5.44 | 5.41
2017-04-17 15:30 | 6.74 | 6.71
2017-04-17 16:00 | 6.28 | 6.26
2017-04-17 16:30 | 7.36 | 7.33
2017-04-17 17:00 | 8.57 | 8.55
2017-04-17 17:30 | 9.54 | 9.51
2017-04-17 18:00 | 10.27 | 10.24
2017-04-17 18:30 | 10.73 | 10.71
2017-04-17 19:00 | 10.58 | 10.56
2017-04-17 19:30 | 9.86 | 9.84
2017-04-17 20:00 | 9.61 | 9.59
2017-04-17 20:30 | 9.48 | 9.46
2017-04-17 21:00 | 8.79 | 8.77
2017-04-17 21:30 | 8.15 | 8.13
2017-04-17 22:00 | 7.48 | 7.46
2017-04-17 22:30 | 7.18 | 7.16
2017-04-17 23:00 | 6.92 | 6.91
2017-04-17 23:30 | 5.9 | 5.88
2017-04-18 | 5.18 | 5.17
2017-04-18 00:30 | 4.67 | 4.65
2017-04-18 01:00 | 4.38 | 4.36
2017-04-18 01:30 | 4.16 | 4.14
2017-04-18 02:00 | 3.92 | 3.9
2017-04-18 02:30 | 3.8 | 3.78
2017-04-18 03:00 | 3.82 | 3.8
2017-04-18 03:30 | 3.81 | 3.79
2017-04-18 04:00 | 3.85 | 3.83
2017-04-18 04:30 | 4.02 | 4
2017-04-18 05:00 | 4.12 | 4.09
2017-04-18 05:30 | 4.57 | 4.55
2017-04-18 06:00 | 5.35 | 5.34
2017-04-18 06:30 | 6.05 | 6.04
2017-04-18 07:00 | 6.37 | 6.36
2017-04-18 07:30 | 6.43 | 6.42
2017-04-18 08:00 | 5.91 | 5.9
2017-04-18 08:30 | 5.05 | 5.04
2017-04-18 09:00 | 4.43 | 4.42
2017-04-18 09:30 | 4.3 | 4.28
2017-04-18 10:00 | 4.16 | 4.14
2017-04-18 10:30 | 3.68 | 3.65
2017-04-18 11:00 | 3.66 | 3.63
2017-04-18 11:30 | 4.18 | 4.15
2017-04-18 12:00 | 3.83 | 3.81
2017-04-18 12:30 | 4.27 | 4.25
2017-04-18 13:00 | 5.05 | 5.03
2017-04-18 13:30 | 5.09 | 5.07
2017-04-18 14:00 | 6.56 | 6.56
2017-04-18 14:30 | 6.52 | 6.52
2017-04-18 15:00 | 7 | 6.99
2017-04-18 15:30 | 6.98 | 6.97
2017-04-18 16:00 | 6.29 | 6.28
2017-04-18 16:30 | 7.34 | 7.33
2017-04-18 17:00 | 8.59 | 8.58
2017-04-18 17:30 | 9.45 | 9.44
2017-04-18 18:00 | 10.62 | 10.58
2017-04-18 18:30 | 11.07 | 11.03
2017-04-18 19:00 | 11.02 | 10.98
2017-04-18 19:30 | 10.63 | 10.59
2017-04-18 20:00 | 10.37 | 10.34
2017-04-18 20:30 | 10.26 | 10.24
2017-04-18 21:00 | 9.7 | 9.69
2017-04-18 21:30 | 8.8 | 8.79
2017-04-18 22:00 | 8.04 | 8.03
2017-04-18 22:30 | 7.66 | 7.65
2017-04-18 23:00 | 7.03 | 7.01
2017-04-18 23:30 | 6.01 | 5.99
2017-04-19 | 5.18 | 5.16
2017-04-19 00:30 | 4.57 | 4.56
2017-04-19 01:00 | 4.4 | 4.38
2017-04-19 01:30 | 4.19 | 4.17
2017-04-19 02:00 | 3.97 | 3.95
2017-04-19 02:30 | 3.84 | 3.82
2017-04-19 03:00 | 3.71 | 3.69
2017-04-19 03:30 | 3.81 | 3.79
2017-04-19 04:00 | 3.86 | 3.84
2017-04-19 04:30 | 4.04 | 4.02
2017-04-19 05:00 | 4.26 | 4.24
2017-04-19 05:30 | 4.62 | 4.61
2017-04-19 06:00 | 5.14 | 5.12
2017-04-19 06:30 | 5.77 | 5.75
2017-04-19 07:00 | 6.2 | 6.19
2017-04-19 07:30 | 6.28 | 6.27
2017-04-19 08:00 | 5.81 | 5.8
2017-04-19 08:30 | 5.02 | 5.01
2017-04-19 09:00 | 4.34 | 4.32
2017-04-19 09:30 | 4.03 | 4.01
2017-04-19 10:00 | 3.72 | 3.7
2017-04-19 10:30 | 3.58 | 3.55
2017-04-19 11:00 | 4.04 | 4.02
2017-04-19 11:30 | 4.23 | 4.21
2017-04-19 12:00 | 4.24 | 4.23
2017-04-19 12:30 | 4.77 | 4.76
2017-04-19 13:00 | 4 | 3.97
2017-04-19 13:30 | 5.36 | 5.34
2017-04-19 14:00 | 4.08 | 4.05
2017-04-19 14:30 | 4.41 | 4.39
2017-04-19 15:00 | 5.09 | 5.06
2017-04-19 15:30 | 5.4 | 5.38
2017-04-19 16:00 | 6.27 | 6.25
2017-04-19 16:30 | 7.27 | 7.25
2017-04-19 17:00 | 8.19 | 8.18
2017-04-19 17:30 | 8.97 | 8.96
2017-04-19 18:00 | 10.08 | 10.06
2017-04-19 18:30 | 10.86 | 10.82
2017-04-19 19:00 | 10.9 | 10.86
2017-04-19 19:30 | 10.52 | 10.49
2017-04-19 20:00 | 10.42 | 10.39
2017-04-19 20:30 | 10.32 | 10.3
2017-04-19 21:00 | 9.67 | 9.66
2017-04-19 21:30 | 9.04 | 9.03
2017-04-19 22:00 | 8.1 | 8.08
2017-04-19 22:30 | 7.61 | 7.6
2017-04-19 23:00 | 7.27 | 7.26
2017-04-19 23:30 | 6.24 | 6.23
2017-04-20 | 5.33 | 5.31
2017-04-20 00:30 | 4.64 | 4.62
2017-04-20 01:00 | 4.5 | 4.48
2017-04-20 01:30 | 4.22 | 4.2
2017-04-20 02:00 | 3.96 | 3.94
2017-04-20 02:30 | 3.86 | 3.84
2017-04-20 03:00 | 3.79 | 3.77
2017-04-20 03:30 | 3.85 | 3.82
2017-04-20 04:00 | 3.87 | 3.85
2017-04-20 04:30 | 4.07 | 4.04
2017-04-20 05:00 | 4.34 | 4.32
2017-04-20 05:30 | 4.78 | 4.76
2017-04-20 06:00 | 5.13 | 5.11
2017-04-20 06:30 | 5.49 | 5.47
2017-04-20 07:00 | 5.83 | 5.82
2017-04-20 07:30 | 5.91 | 5.89
2017-04-20 08:00 | 5.47 | 5.45
2017-04-20 08:30 | 4.65 | 4.62
2017-04-20 09:00 | 4.56 | 4.53
2017-04-20 09:30 | 4.31 | 4.28
2017-04-20 10:00 | 4.75 | 4.72
2017-04-20 10:30 | 4.31 | 4.27
2017-04-20 11:00 | 3.75 | 3.7
2017-04-20 11:30 | 3.71 | 3.66
2017-04-20 12:00 | 4.35 | 4.31
2017-04-20 12:30 | 3.09 | 3.05
2017-04-20 13:00 | 3.18 | 3.14
2017-04-20 13:30 | 3.33 | 3.3
2017-04-20 14:00 | 4.01 | 3.98
2017-04-20 14:30 | 3.99 | 3.97
2017-04-20 15:00 | 4.74 | 4.72
2017-04-20 15:30 | 6.12 | 6.1
2017-04-20 16:00 | 6.84 | 6.84
2017-04-20 16:30 | 7.13 | 7.11
2017-04-20 17:00 | 7.92 | 7.91
2017-04-20 17:30 | 9.09 | 9.08
2017-04-20 18:00 | 9.99 | 9.96
2017-04-20 18:30 | 10.33 | 10.3
2017-04-20 19:00 | 10.49 | 10.46
2017-04-20 19:30 | 10.13 | 10.11
2017-04-20 20:00 | 9.97 | 9.96
2017-04-20 20:30 | 10.02 | 10.01
2017-04-20 21:00 | 9.61 | 9.6
2017-04-20 21:30 | 8.82 | 8.81
2017-04-20 22:00 | 8.13 | 8.12
2017-04-20 22:30 | 7.68 | 7.67
2017-04-20 23:00 | 7.2 | 7.19
2017-04-20 23:30 | 6.25 | 6.24
2017-04-21 | 5.26 | 5.25
2017-04-21 00:30 | 4.63 | 4.62
2017-04-21 01:00 | 4.45 | 4.44
2017-04-21 01:30 | 4.22 | 4.2
2017-04-21 02:00 | 4.02 | 4
2017-04-21 02:30 | 3.82 | 3.8
2017-04-21 03:00 | 3.74 | 3.72
2017-04-21 03:30 | 3.86 | 3.84
2017-04-21 04:00 | 3.79 | 3.76
2017-04-21 04:30 | 4.04 | 4.02
2017-04-21 05:00 | 4.23 | 4.21
2017-04-21 05:30 | 4.77 | 4.75
2017-04-21 06:00 | 5.13 | 5.11
2017-04-21 06:30 | 5.53 | 5.51
2017-04-21 07:00 | 5.9 | 5.88
2017-04-21 07:30 | 6.27 | 6.25
2017-04-21 08:00 | 5.89 | 5.88
2017-04-21 08:30 | 4.63 | 4.61
2017-04-21 09:00 | 4.04 | 4.02
2017-04-21 09:30 | 4.02 | 4
2017-04-21 10:00 | 3.51 | 3.48
2017-04-21 10:30 | 3.01 | 2.98
2017-04-21 11:00 | 3.61 | 3.58
2017-04-21 11:30 | 3.29 | 3.25
2017-04-21 12:00 | 3.18 | 3.13
2017-04-21 12:30 | 3.18 | 3.13
2017-04-21 13:00 | 3.01 | 2.97
2017-04-21 13:30 | 3.97 | 3.94
2017-04-21 14:00 | 5.21 | 5.19
2017-04-21 14:30 | 5.54 | 5.52
2017-04-21 15:00 | 5.7 | 5.68
2017-04-21 15:30 | 5.57 | 5.55
2017-04-21 16:00 | 6.18 | 6.16
2017-04-21 16:30 | 6.39 | 6.37
2017-04-21 17:00 | 7.12 | 7.1
2017-04-21 17:30 | 7.92 | 7.89
2017-04-21 18:00 | 8.91 | 8.89
2017-04-21 18:30 | 9.42 | 9.4
2017-04-21 19:00 | 9.59 | 9.57
2017-04-21 19:30 | 9.15 | 9.13
2017-04-21 20:00 | 9.21 | 9.19
2017-04-21 20:30 | 9.05 | 9.03
2017-04-21 21:00 | 8.69 | 8.67
2017-04-21 21:30 | 8.26 | 8.24
2017-04-21 22:00 | 7.63 | 7.62
2017-04-21 22:30 | 7.27 | 7.26
2017-04-21 23:00 | 7.15 | 7.14
2017-04-21 23:30 | 6.31 | 6.29
2017-04-22 | 5.5 | 5.49
2017-04-22 00:30 | 4.99 | 4.97
2017-04-22 01:00 | 4.73 | 4.72
2017-04-22 01:30 | 4.46 | 4.44
2017-04-22 02:00 | 4.11 | 4.09
2017-04-22 02:30 | 4.03 | 4.01
2017-04-22 03:00 | 3.85 | 3.83
2017-04-22 03:30 | 3.88 | 3.86
2017-04-22 04:00 | 3.95 | 3.93
2017-04-22 04:30 | 3.86 | 3.84
2017-04-22 05:00 | 3.88 | 3.86
2017-04-22 05:30 | 4 | 3.98
2017-04-22 06:00 | 4.22 | 4.2
2017-04-22 06:30 | 4.34 | 4.31
2017-04-22 07:00 | 4.66 | 4.63
2017-04-22 07:30 | 5.23 | 5.21
2017-04-22 08:00 | 5.76 | 5.74
2017-04-22 08:30 | 5.88 | 5.86
2017-04-22 09:00 | 5.2 | 5.17
2017-04-22 09:30 | 5.66 | 5.63
2017-04-22 10:00 | 4.84 | 4.81
2017-04-22 10:30 | 4.82 | 4.78
2017-04-22 11:00 | 4.11 | 4.05
2017-04-22 11:30 | 4.58 | 4.54
2017-04-22 12:00 | 4.57 | 4.53
2017-04-22 12:30 | 4.61 | 4.56
2017-04-22 13:00 | 5.97 | 5.93
2017-04-22 13:30 | 5.68 | 5.65
2017-04-22 14:00 | 5.59 | 5.56
2017-04-22 14:30 | 5.84 | 5.81
2017-04-22 15:00 | 5.66 | 5.63
2017-04-22 15:30 | 6.11 | 6.09
2017-04-22 16:00 | 6.28 | 6.26
2017-04-22 16:30 | 7.15 | 7.13
2017-04-22 17:00 | 7.55 | 7.53
2017-04-22 17:30 | 8.31 | 8.3
2017-04-22 18:00 | 9.12 | 9.1
2017-04-22 18:30 | 9.27 | 9.26
2017-04-22 19:00 | 9.33 | 9.32
2017-04-22 19:30 | 9.03 | 9.02
2017-04-22 20:00 | 8.88 | 8.87
2017-04-22 20:30 | 8.72 | 8.7
2017-04-22 21:00 | 8.33 | 8.31
2017-04-22 21:30 | 7.8 | 7.79
2017-04-22 22:00 | 7.43 | 7.41
2017-04-22 22:30 | 7.2 | 7.19
2017-04-22 23:00 | 7.23 | 7.22
2017-04-22 23:30 | 6.39 | 6.38
2017-04-23 | 5.54 | 5.53
2017-04-23 00:30 | 4.96 | 4.95
2017-04-23 01:00 | 4.69 | 4.68
2017-04-23 01:30 | 4.2 | 4.19
2017-04-23 02:00 | 4.03 | 4.01
2017-04-23 02:30 | 3.83 | 3.81
2017-04-23 03:00 | 3.87 | 3.84
2017-04-23 03:30 | 3.89 | 3.87
2017-04-23 04:00 | 3.86 | 3.84
2017-04-23 04:30 | 3.84 | 3.82
2017-04-23 05:00 | 3.8 | 3.78
2017-04-23 05:30 | 3.85 | 3.83
2017-04-23 06:00 | 4.12 | 4.1
2017-04-23 06:30 | 4.16 | 4.1
2017-04-23 07:00 | 4.21 | 4.14
2017-04-23 07:30 | 4.26 | 4.21
2017-04-23 08:00 | 4.36 | 4.31
2017-04-23 08:30 | 4.49 | 4.46
2017-04-23 09:00 | 4.48 | 4.45
2017-04-23 09:30 | 4.36 | 4.33
2017-04-23 10:00 | 4.13 | 4.09
2017-04-23 10:30 | 3.94 | 3.9
2017-04-23 11:00 | 4.02 | 3.97
2017-04-23 11:30 | 4.02 | 3.98
2017-04-23 12:00 | 4.02 | 3.97
2017-04-23 12:30 | 5.56 | 5.53
2017-04-23 13:00 | 4.99 | 4.95
2017-04-23 13:30 | 4.35 | 4.3
2017-04-23 14:00 | 5.42 | 5.38
2017-04-23 14:30 | 5.73 | 5.7
2017-04-23 15:00 | 5.38 | 5.34
2017-04-23 15:30 | 5.8 | 5.77
2017-04-23 16:00 | 7 | 6.98
2017-04-23 16:30 | 7.59 | 7.57
2017-04-23 17:00 | 8.2 | 8.19
2017-04-23 17:30 | 9.09 | 9.07
2017-04-23 18:00 | 10.05 | 10.03
2017-04-23 18:30 | 10.58 | 10.56
2017-04-23 19:00 | 10.17 | 10.15
2017-04-23 19:30 | 9.62 | 9.61
2017-04-23 20:00 | 9.39 | 9.37
2017-04-23 20:30 | 9.34 | 9.33
2017-04-23 21:00 | 8.81 | 8.8
2017-04-23 21:30 | 8.11 | 8.09
2017-04-23 22:00 | 7.43 | 7.41
2017-04-23 22:30 | 6.97 | 6.96
2017-04-23 23:00 | 6.8 | 6.79
2017-04-23 23:30 | 6.01 | 6
2017-04-24 | 5.26 | 5.24
2017-04-24 00:30 | 4.66 | 4.65
2017-04-24 01:00 | 4.41 | 4.39
2017-04-24 01:30 | 4.1 | 4.08
2017-04-24 02:00 | 3.85 | 3.83
2017-04-24 02:30 | 3.74 | 3.72
2017-04-24 03:00 | 3.77 | 3.75
2017-04-24 03:30 | 3.78 | 3.76
2017-04-24 04:00 | 3.82 | 3.8
2017-04-24 04:30 | 3.89 | 3.87
2017-04-24 05:00 | 4.12 | 4.1
2017-04-24 05:30 | 4.49 | 4.47
2017-04-24 06:00 | 4.82 | 4.81
2017-04-24 06:30 | 5.11 | 5.08
2017-04-24 07:00 | 5.4 | 5.38
2017-04-24 07:30 | 5.7 | 5.68
2017-04-24 08:00 | 5.4 | 5.38
2017-04-24 08:30 | 4.69 | 4.66
2017-04-24 09:00 | 3.98 | 3.94
2017-04-24 09:30 | 4.01 | 3.98
2017-04-24 10:00 | 3.51 | 3.47
2017-04-24 10:30 | 3.68 | 3.64
2017-04-24 11:00 | 3.34 | 3.29
2017-04-24 11:30 | 3.03 | 2.97
2017-04-24 12:00 | 3.2 | 3.15
2017-04-24 12:30 | 3.38 | 3.35
2017-04-24 13:00 | 3.48 | 3.44
2017-04-24 13:30 | 4.21 | 4.17
2017-04-24 14:00 | 4.83 | 4.8
2017-04-24 14:30 | 5.41 | 5.38
2017-04-24 15:00 | 6.42 | 6.39
2017-04-24 15:30 | 5.58 | 5.54
2017-04-24 16:00 | 6.18 | 6.14
2017-04-24 16:30 | 6.86 | 6.83
2017-04-24 17:00 | 7.79 | 7.77
2017-04-24 17:30 | 8.64 | 8.61
2017-04-24 18:00 | 9.74 | 9.71
2017-04-24 18:30 | 10.11 | 10.08
2017-04-24 19:00 | 10.24 | 10.21
2017-04-24 19:30 | 9.86 | 9.84
2017-04-24 20:00 | 9.82 | 9.8
2017-04-24 20:30 | 9.59 | 9.57
2017-04-24 21:00 | 9.08 | 9.06
2017-04-24 21:30 | 8.38 | 8.36
2017-04-24 22:00 | 7.7 | 7.68
2017-04-24 22:30 | 7.52 | 7.5
2017-04-24 23:00 | 7.3 | 7.29
2017-04-24 23:30 | 6.46 | 6.44
2017-04-25 | 5.57 | 5.55
2017-04-25 00:30 | 4.9 | 4.89
2017-04-25 01:00 | 4.56 | 4.54
2017-04-25 01:30 | 4.32 | 4.3
2017-04-25 02:00 | 4.05 | 4.04
2017-04-25 02:30 | 3.88 | 3.86
2017-04-25 03:00 | 3.78 | 3.76
2017-04-25 03:30 | 3.79 | 3.77
2017-04-25 04:00 | 3.84 | 3.82
2017-04-25 04:30 | 3.83 | 3.81
2017-04-25 05:00 | 3.79 | 3.77
2017-04-25 05:30 | 3.9 | 3.88
2017-04-25 06:00 | 3.92 | 3.89
2017-04-25 06:30 | 3.91 | 3.84
2017-04-25 07:00 | 3.96 | 3.87
2017-04-25 07:30 | 3.97 | 3.89
2017-04-25 08:00 | 3.87 | 3.81
2017-04-25 08:30 | 3.41 | 3.35
2017-04-25 09:00 | 4.53 | 4.49
2017-04-25 09:30 | 4.21 | 4.18
2017-04-25 10:00 | 4.88 | 4.86
2017-04-25 10:30 | 3.5 | 3.48
2017-04-25 11:00 | 3.5 | 3.48
2017-04-25 11:30 | 3.63 | 3.6
2017-04-25 12:00 | 3.5 | 3.47
2017-04-25 12:30 | 3.64 | 3.61
2017-04-25 13:00 | 3.76 | 3.72
2017-04-25 13:30 | 3.89 | 3.86
2017-04-25 14:00 | 4.58 | 4.55
2017-04-25 14:30 | 4.86 | 4.84
2017-04-25 15:00 | 5.1 | 5.08
2017-04-25 15:30 | 5.57 | 5.55
2017-04-25 16:00 | 6.39 | 6.38
2017-04-25 16:30 | 7.15 | 7.14
2017-04-25 17:00 | 8.02 | 8
2017-04-25 17:30 | 8.77 | 8.76
2017-04-25 18:00 | 9.73 | 9.71
2017-04-25 18:30 | 10.15 | 10.13
2017-04-25 19:00 | 10.12 | 10.11
2017-04-25 19:30 | 9.66 | 9.65
2017-04-25 20:00 | 9.44 | 9.43
2017-04-25 20:30 | 9.28 | 9.27
2017-04-25 21:00 | 8.69 | 8.68
2017-04-25 21:30 | 7.98 | 7.96
2017-04-25 22:00 | 7.36 | 7.35
2017-04-25 22:30 | 7.15 | 7.14
2017-04-25 23:00 | 6.98 | 6.96
2017-04-25 23:30 | 6.14 | 6.13
2017-04-26 | 5.25 | 5.24
2017-04-26 00:30 | 4.67 | 4.65
2017-04-26 01:00 | 4.49 | 4.47
2017-04-26 01:30 | 4.22 | 4.21
2017-04-26 02:00 | 4.11 | 4.09
2017-04-26 02:30 | 4.01 | 3.99
2017-04-26 03:00 | 3.93 | 3.91
2017-04-26 03:30 | 3.84 | 3.82
2017-04-26 04:00 | 3.86 | 3.84
2017-04-26 04:30 | 4.06 | 4.04
2017-04-26 05:00 | 4.28 | 4.25
2017-04-26 05:30 | 4.74 | 4.72
2017-04-26 06:00 | 5.1 | 5.09
2017-04-26 06:30 | 5.56 | 5.54
2017-04-26 07:00 | 5.73 | 5.71
2017-04-26 07:30 | 6.38 | 6.36
2017-04-26 08:00 | 6.11 | 6.09
2017-04-26 08:30 | 6.01 | 5.98
2017-04-26 09:00 | 6.14 | 6.12
2017-04-26 09:30 | 6.59 | 6.57
2017-04-26 10:00 | 6.07 | 6.04
2017-04-26 10:30 | 5.9 | 5.88
2017-04-26 11:00 | 6.46 | 6.44
2017-04-26 11:30 | 6.61 | 6.59
2017-04-26 12:00 | 6.7 | 6.68
2017-04-26 12:30 | 6.61 | 6.59
2017-04-26 13:00 | 5.74 | 5.72
2017-04-26 13:30 | 6.3 | 6.28
2017-04-26 14:00 | 6.45 | 6.42
2017-04-26 14:30 | 7.15 | 7.14
2017-04-26 15:00 | 6.84 | 6.83
2017-04-26 15:30 | 6.47 | 6.45
2017-04-26 16:00 | 7.37 | 7.36
2017-04-26 16:30 | 8.28 | 8.27
2017-04-26 17:00 | 9.35 | 9.34
2017-04-26 17:30 | 10.36 | 10.35
2017-04-26 18:00 | 10.93 | 10.9
2017-04-26 18:30 | 11.23 | 11.19
2017-04-26 19:00 | 11.35 | 11.33
2017-04-26 19:30 | 10.85 | 10.83
2017-04-26 20:00 | 10.78 | 10.77
2017-04-26 20:30 | 10.72 | 10.71
2017-04-26 21:00 | 10.27 | 10.26
2017-04-26 21:30 | 9.4 | 9.39
2017-04-26 22:00 | 8.59 | 8.58
2017-04-26 22:30 | 8.23 | 8.22
2017-04-26 23:00 | 7.74 | 7.73
2017-04-26 23:30 | 6.51 | 6.49
2017-04-27 | 5.46 | 5.44
2017-04-27 00:30 | 4.88 | 4.86
2017-04-27 01:00 | 4.63 | 4.61
2017-04-27 01:30 | 4.35 | 4.33
2017-04-27 02:00 | 4.15 | 4.13
2017-04-27 02:30 | 3.93 | 3.91
2017-04-27 03:00 | 3.83 | 3.81
2017-04-27 03:30 | 3.9 | 3.88
2017-04-27 04:00 | 3.98 | 3.95
2017-04-27 04:30 | 4.2 | 4.18
2017-04-27 05:00 | 4.4 | 4.39
2017-04-27 05:30 | 5.25 | 5.23
2017-04-27 06:00 | 5.75 | 5.74
2017-04-27 06:30 | 6.15 | 6.13
2017-04-27 07:00 | 6.68 | 6.67
2017-04-27 07:30 | 6.91 | 6.91
2017-04-27 08:00 | 6.81 | 6.81
2017-04-27 08:30 | 6.35 | 6.34
2017-04-27 09:00 | 5.34 | 5.33
2017-04-27 09:30 | 4.73 | 4.72
2017-04-27 10:00 | 4.42 | 4.41
2017-04-27 10:30 | 4.12 | 4.11
2017-04-27 11:00 | 4.08 | 4.07
2017-04-27 11:30 | 3.94 | 3.94
2017-04-27 12:00 | 3.82 | 3.81
2017-04-27 12:30 | 3.62 | 3.62
2017-04-27 13:00 | 3.76 | 3.75
2017-04-27 13:30 | 3.57 | 3.56
2017-04-27 14:00 | 3.39 | 3.38
2017-04-27 14:30 | 3.79 | 3.78
2017-04-27 15:00 | 4.2 | 4.19
2017-04-27 15:30 | 4.88 | 4.88
2017-04-27 16:00 | 5.92 | 5.91
2017-04-27 16:30 | 6.97 | 6.96
2017-04-27 17:00 | 7.88 | 7.88
2017-04-27 17:30 | 9.01 | 9.01
2017-04-27 18:00 | 10.02 | 10
2017-04-27 18:30 | 10.3 | 10.28
2017-04-27 19:00 | 10.59 | 10.58
2017-04-27 19:30 | 10.48 | 10.46
2017-04-27 20:00 | 10.5 | 10.48
2017-04-27 20:30 | 10.41 | 10.4
2017-04-27 21:00 | 10.01 | 10.01
2017-04-27 21:30 | 9.31 | 9.3
2017-04-27 22:00 | 8.58 | 8.58
2017-04-27 22:30 | 8.07 | 8.06
2017-04-27 23:00 | 7.78 | 7.77
2017-04-27 23:30 | 6.67 | 6.66
2017-04-28 | 5.67 | 5.66
2017-04-28 00:30 | 5.04 | 5.03
2017-04-28 01:00 | 4.72 | 4.71
2017-04-28 01:30 | 4.4 | 4.38
2017-04-28 02:00 | 4.18 | 4.16
2017-04-28 02:30 | 3.99 | 3.97
2017-04-28 03:00 | 3.95 | 3.93
2017-04-28 03:30 | 4 | 3.97
2017-04-28 04:00 | 4.01 | 3.99
2017-04-28 04:30 | 4.23 | 4.21
2017-04-28 05:00 | 4.56 | 4.54
2017-04-28 05:30 | 5.11 | 5.1
2017-04-28 06:00 | 5.48 | 5.46
2017-04-28 06:30 | 5.86 | 5.84
2017-04-28 07:00 | 6.43 | 6.41
2017-04-28 07:30 | 6.93 | 6.91
2017-04-28 08:00 | 5.98 | 5.96
2017-04-28 08:30 | 5.02 | 4.99
2017-04-28 09:00 | 4.07 | 4.04
2017-04-28 09:30 | 3.65 | 3.62
2017-04-28 10:00 | 3.44 | 3.41
2017-04-28 10:30 | 3.61 | 3.59
2017-04-28 11:00 | 2.39 | 2.34
2017-04-28 11:30 | 2.37 | 2.3
2017-04-28 12:00 | 2.85 | 2.81
2017-04-28 12:30 | 3 | 2.96
2017-04-28 13:00 | 2.84 | 2.8
2017-04-28 13:30 | 4.47 | 4.45
2017-04-28 14:00 | 4.42 | 4.39
2017-04-28 14:30 | 4.16 | 4.14
2017-04-28 15:00 | 3.94 | 3.91
2017-04-28 15:30 | 5.75 | 5.73
2017-04-28 16:00 | 6.05 | 6.03
2017-04-28 16:30 | 6.74 | 6.72
2017-04-28 17:00 | 7.13 | 7.12
2017-04-28 17:30 | 7.95 | 7.93
2017-04-28 18:00 | 9 | 8.99
2017-04-28 18:30 | 9.39 | 9.37
2017-04-28 19:00 | 9.67 | 9.65
2017-04-28 19:30 | 9.48 | 9.47
2017-04-28 20:00 | 9.48 | 9.47
2017-04-28 20:30 | 9.52 | 9.5
2017-04-28 21:00 | 8.97 | 8.96
2017-04-28 21:30 | 8.42 | 8.41
2017-04-28 22:00 | 7.9 | 7.89
2017-04-28 22:30 | 7.55 | 7.54
2017-04-28 23:00 | 7.47 | 7.46
2017-04-28 23:30 | 6.52 | 6.51
2017-04-29 | 5.68 | 5.67
2017-04-29 00:30 | 5.07 | 5.06
2017-04-29 01:00 | 4.81 | 4.79
2017-04-29 01:30 | 4.43 | 4.41
2017-04-29 02:00 | 4.12 | 4.1
2017-04-29 02:30 | 4.05 | 4.03
2017-04-29 03:00 | 3.93 | 3.91
2017-04-29 03:30 | 3.91 | 3.89
2017-04-29 04:00 | 3.92 | 3.9
2017-04-29 04:30 | 4 | 3.98
2017-04-29 05:00 | 3.99 | 3.97
2017-04-29 05:30 | 4.23 | 4.21
2017-04-29 06:00 | 4.42 | 4.4
2017-04-29 06:30 | 4.53 | 4.5
2017-04-29 07:00 | 4.73 | 4.68
2017-04-29 07:30 | 4.82 | 4.78
2017-04-29 08:00 | 4.7 | 4.66
2017-04-29 08:30 | 4.67 | 4.65
2017-04-29 09:00 | 4.32 | 4.3
2017-04-29 09:30 | 4.18 | 4.15
2017-04-29 10:00 | 3.92 | 3.89
2017-04-29 10:30 | 3.62 | 3.58
2017-04-29 11:00 | 3.35 | 3.31
2017-04-29 11:30 | 3.23 | 3.18
2017-04-29 12:00 | 3.23 | 3.18
2017-04-29 12:30 | 3.2 | 3.15
2017-04-29 13:00 | 3.43 | 3.38
2017-04-29 13:30 | 3.5 | 3.45
2017-04-29 14:00 | 3.92 | 3.88
2017-04-29 14:30 | 4.34 | 4.3
2017-04-29 15:00 | 4.63 | 4.6
2017-04-29 15:30 | 5.36 | 5.34
2017-04-29 16:00 | 6.03 | 6
2017-04-29 16:30 | 6.87 | 6.85
2017-04-29 17:00 | 7.58 | 7.56
2017-04-29 17:30 | 8.19 | 8.17
2017-04-29 18:00 | 8.86 | 8.84
2017-04-29 18:30 | 9.05 | 9.03
2017-04-29 19:00 | 9.03 | 9
2017-04-29 19:30 | 8.69 | 8.67
2017-04-29 20:00 | 8.55 | 8.53
2017-04-29 20:30 | 8.58 | 8.56
2017-04-29 21:00 | 8.2 | 8.18
2017-04-29 21:30 | 7.7 | 7.68
2017-04-29 22:00 | 7.3 | 7.29
2017-04-29 22:30 | 7.23 | 7.21
2017-04-29 23:00 | 7.2 | 7.18
2017-04-29 23:30 | 6.48 | 6.47
2017-04-30 | 5.68 | 5.67
2017-04-30 00:30 | 5 | 4.99
2017-04-30 01:00 | 4.76 | 4.74
2017-04-30 01:30 | 4.45 | 4.43
2017-04-30 02:00 | 4.22 | 4.21
2017-04-30 02:30 | 4.02 | 4
2017-04-30 03:00 | 3.92 | 3.9
2017-04-30 03:30 | 3.93 | 3.91
2017-04-30 04:00 | 3.89 | 3.87
2017-04-30 04:30 | 3.89 | 3.87
2017-04-30 05:00 | 3.82 | 3.8
2017-04-30 05:30 | 4.06 | 4.04
2017-04-30 06:00 | 4.12 | 4.1
2017-04-30 06:30 | 4.17 | 4.13
2017-04-30 07:00 | 4.43 | 4.37
2017-04-30 07:30 | 4.63 | 4.58
2017-04-30 08:00 | 4.64 | 4.6
2017-04-30 08:30 | 4.59 | 4.56
2017-04-30 09:00 | 4.57 | 4.54
2017-04-30 09:30 | 4.42 | 4.39
2017-04-30 10:00 | 4.09 | 4.06
2017-04-30 10:30 | 3.74 | 3.71
2017-04-30 11:00 | 3.73 | 3.7
2017-04-30 11:30 | 3.9 | 3.86
2017-04-30 12:00 | 3.69 | 3.65
2017-04-30 12:30 | 4.25 | 4.22
2017-04-30 13:00 | 4 | 3.97
2017-04-30 13:30 | 4.52 | 4.49
2017-04-30 14:00 | 4.74 | 4.71
2017-04-30 14:30 | 5.03 | 5.01
2017-04-30 15:00 | 5.72 | 5.71
2017-04-30 15:30 | 5.61 | 5.59
2017-04-30 16:00 | 6.33 | 6.31
2017-04-30 16:30 | 6.93 | 6.91
2017-04-30 17:00 | 7.7 | 7.68
2017-04-30 17:30 | 8.49 | 8.47
2017-04-30 18:00 | 10.08 | 10.06
2017-04-30 18:30 | 10.63 | 10.62
2017-04-30 19:00 | 10.36 | 10.35
2017-04-30 19:30 | 9.89 | 9.89
2017-04-30 20:00 | 9.82 | 9.81
2017-04-30 20:30 | 9.71 | 9.7
2017-04-30 21:00 | 9.36 | 9.35
2017-04-30 21:30 | 8.97 | 8.97
2017-04-30 22:00 | 8.45 | 8.45
2017-04-30 22:30 | 8.4 | 8.39
2017-04-30 23:00 | 8.36 | 8.35
2017-04-30 23:30 | 7.51 | 7.5
2017-05-01 | 6.7 | 6.69
2017-05-01 00:30 | 6.13 | 6.12
2017-05-01 01:00 | 5.7 | 5.68
2017-05-01 01:30 | 5.44 | 5.42
2017-05-01 02:00 | 5.22 | 5.2
2017-05-01 02:30 | 5.07 | 5.05
2017-05-01 03:00 | 4.89 | 4.87
2017-05-01 03:30 | 4.87 | 4.84
2017-05-01 04:00 | 4.84 | 4.81
2017-05-01 04:30 | 4.85 | 4.82
2017-05-01 05:00 | 5 | 4.98
2017-05-01 05:30 | 5.01 | 4.99
2017-05-01 06:00 | 5.19 | 5.16
2017-05-01 06:30 | 5.24 | 5.18
2017-05-01 07:00 | 5.25 | 5.17
2017-05-01 07:30 | 5.23 | 5.15
2017-05-01 08:00 | 5.28 | 5.22
2017-05-01 08:30 | 5.32 | 5.26
2017-05-01 09:00 | 5.16 | 5.11
2017-05-01 09:30 | 5.09 | 5.06
2017-05-01 10:00 | 4.89 | 4.87
2017-05-01 10:30 | 4.65 | 4.63
2017-05-01 11:00 | 3.72 | 3.7
2017-05-01 11:30 | 3.84 | 3.82
2017-05-01 12:00 | 3.63 | 3.61
2017-05-01 12:30 | 3.51 | 3.48
2017-05-01 13:00 | 3.57 | 3.54
2017-05-01 13:30 | 4.3 | 4.28
2017-05-01 14:00 | 3.75 | 3.73
2017-05-01 14:30 | 4.54 | 4.52
2017-05-01 15:00 | 5.08 | 5.07
2017-05-01 15:30 | 5.41 | 5.4
2017-05-01 16:00 | 6.08 | 6.06
2017-05-01 16:30 | 6.97 | 6.96
2017-05-01 17:00 | 7.95 | 7.94
2017-05-01 17:30 | 9.23 | 9.22
2017-05-01 18:00 | 10.19 | 10.18
2017-05-01 18:30 | 10.43 | 10.42
2017-05-01 19:00 | 10.31 | 10.3
2017-05-01 19:30 | 9.83 | 9.82
2017-05-01 20:00 | 9.59 | 9.58
2017-05-01 20:30 | 9.58 | 9.57
2017-05-01 21:00 | 9.02 | 9.01
2017-05-01 21:30 | 8.21 | 8.2
2017-05-01 22:00 | 7.62 | 7.61
2017-05-01 22:30 | 7.14 | 7.13
2017-05-01 23:00 | 6.97 | 6.96
2017-05-01 23:30 | 6.17 | 6.15
2017-05-02 | 5.24 | 5.22
2017-05-02 00:30 | 4.66 | 4.65
2017-05-02 01:00 | 4.42 | 4.41
2017-05-02 01:30 | 4.09 | 4.08
2017-05-02 02:00 | 3.92 | 3.9
2017-05-02 02:30 | 3.97 | 3.95
2017-05-02 03:00 | 3.87 | 3.85
2017-05-02 03:30 | 3.84 | 3.81
2017-05-02 04:00 | 3.84 | 3.82
2017-05-02 04:30 | 4.05 | 4.03
2017-05-02 05:00 | 4.31 | 4.29
2017-05-02 05:30 | 4.95 | 4.95
2017-05-02 06:00 | 5.37 | 5.36
2017-05-02 06:30 | 5.75 | 5.73
2017-05-02 07:00 | 6.55 | 6.53
2017-05-02 07:30 | 6.76 | 6.74
2017-05-02 08:00 | 6.51 | 6.5
2017-05-02 08:30 | 5.48 | 5.47
2017-05-02 09:00 | 4.7 | 4.7
2017-05-02 09:30 | 4.77 | 4.76
2017-05-02 10:00 | 3.75 | 3.74
2017-05-02 10:30 | 3.63 | 3.61
2017-05-02 11:00 | 3.61 | 3.59
2017-05-02 11:30 | 3.47 | 3.45
2017-05-02 12:00 | 3.74 | 3.72
2017-05-02 12:30 | 4.84 | 4.82
2017-05-02 13:00 | 4.35 | 4.32
2017-05-02 13:30 | 4.76 | 4.74
2017-05-02 14:00 | 4.3 | 4.29
2017-05-02 14:30 | 4.77 | 4.76
2017-05-02 15:00 | 5.06 | 5.04
2017-05-02 15:30 | 5.65 | 5.64
2017-05-02 16:00 | 6.6 | 6.59
2017-05-02 16:30 | 7.56 | 7.54
2017-05-02 17:00 | 8.33 | 8.31
2017-05-02 17:30 | 9.36 | 9.35
2017-05-02 18:00 | 10.39 | 10.36
2017-05-02 18:30 | 10.61 | 10.58
2017-05-02 19:00 | 10.71 | 10.68
2017-05-02 19:30 | 10.24 | 10.22
2017-05-02 20:00 | 10.08 | 10.06
2017-05-02 20:30 | 10.06 | 10.05
2017-05-02 21:00 | 9.47 | 9.46
2017-05-02 21:30 | 8.66 | 8.65
2017-05-02 22:00 | 8.04 | 8.03
2017-05-02 22:30 | 7.66 | 7.64
2017-05-02 23:00 | 7.31 | 7.3
2017-05-02 23:30 | 6.24 | 6.23
2017-05-03 | 5.4 | 5.39
2017-05-03 00:30 | 4.75 | 4.74
2017-05-03 01:00 | 4.58 | 4.56
2017-05-03 01:30 | 4.35 | 4.33
2017-05-03 02:00 | 4.12 | 4.1
2017-05-03 02:30 | 3.98 | 3.96
2017-05-03 03:00 | 3.94 | 3.93
2017-05-03 03:30 | 3.96 | 3.94
2017-05-03 04:00 | 3.98 | 3.97
2017-05-03 04:30 | 4.2 | 4.18
2017-05-03 05:00 | 4.35 | 4.33
2017-05-03 05:30 | 4.87 | 4.85
2017-05-03 06:00 | 5.32 | 5.3
2017-05-03 06:30 | 5.67 | 5.66
2017-05-03 07:00 | 6.03 | 6.02
2017-05-03 07:30 | 6.14 | 6.12
2017-05-03 08:00 | 5.54 | 5.52
2017-05-03 08:30 | 4.82 | 4.8
2017-05-03 09:00 | 4.17 | 4.14
2017-05-03 09:30 | 3.76 | 3.72
2017-05-03 10:00 | 3.5 | 3.46
2017-05-03 10:30 | 3.34 | 3.28
2017-05-03 11:00 | 3.97 | 3.93
2017-05-03 11:30 | 4.25 | 4.22
2017-05-03 12:00 | 3.35 | 3.31
2017-05-03 12:30 | 3.4 | 3.36
2017-05-03 13:00 | 3.6 | 3.56
2017-05-03 13:30 | 4.31 | 4.28
2017-05-03 14:00 | 4.32 | 4.28
2017-05-03 14:30 | 4.92 | 4.89
2017-05-03 15:00 | 6.1 | 6.08
2017-05-03 15:30 | 6.46 | 6.44
2017-05-03 16:00 | 6.58 | 6.56
2017-05-03 16:30 | 7.34 | 7.32
2017-05-03 17:00 | 8.26 | 8.24
2017-05-03 17:30 | 8.94 | 8.93
2017-05-03 18:00 | 9.91 | 9.88
2017-05-03 18:30 | 10.22 | 10.19
2017-05-03 19:00 | 10.19 | 10.17
2017-05-03 19:30 | 10.02 | 10
2017-05-03 20:00 | 9.88 | 9.86
2017-05-03 20:30 | 9.82 | 9.8
2017-05-03 21:00 | 9.33 | 9.31
2017-05-03 21:30 | 8.57 | 8.55
2017-05-03 22:00 | 7.76 | 7.75
2017-05-03 22:30 | 7.45 | 7.43
2017-05-03 23:00 | 7.2 | 7.19
2017-05-03 23:30 | 6.26 | 6.24
2017-05-04 | 5.43 | 5.41
2017-05-04 00:30 | 4.78 | 4.76
2017-05-04 01:00 | 4.53 | 4.51
2017-05-04 01:30 | 4.21 | 4.19
2017-05-04 02:00 | 4.12 | 4.1
2017-05-04 02:30 | 4.02 | 4
2017-05-04 03:00 | 3.91 | 3.89
2017-05-04 03:30 | 3.93 | 3.91
2017-05-04 04:00 | 3.96 | 3.94
2017-05-04 04:30 | 4.14 | 4.11
2017-05-04 05:00 | 4.45 | 4.43
2017-05-04 05:30 | 4.78 | 4.76
2017-05-04 06:00 | 5.46 | 5.45
2017-05-04 06:30 | 6.28 | 6.27
2017-05-04 07:00 | 6.66 | 6.66
2017-05-04 07:30 | 7.11 | 7.11
2017-05-04 08:00 | 6.54 | 6.54
2017-05-04 08:30 | 5.68 | 5.67
2017-05-04 09:00 | 4.91 | 4.9
2017-05-04 09:30 | 4.98 | 4.97
2017-05-04 10:00 | 4.36 | 4.35
2017-05-04 10:30 | 4.04 | 4.03
2017-05-04 11:00 | 4.99 | 4.98
2017-05-04 11:30 | 5.31 | 5.3
2017-05-04 12:00 | 5.92 | 5.91
2017-05-04 12:30 | 5.61 | 5.59
2017-05-04 13:00 | 6.71 | 6.7
2017-05-04 13:30 | 6.03 | 6.02
2017-05-04 14:00 | 5.26 | 5.24
2017-05-04 14:30 | 5.07 | 5.06
2017-05-04 15:00 | 5.7 | 5.68
2017-05-04 15:30 | 6.13 | 6.11
2017-05-04 16:00 | 7.05 | 7.04
2017-05-04 16:30 | 7.5 | 7.49
2017-05-04 17:00 | 7.95 | 7.94
2017-05-04 17:30 | 8.93 | 8.92
2017-05-04 18:00 | 9.75 | 9.73
2017-05-04 18:30 | 10.12 | 10.1
2017-05-04 19:00 | 10.15 | 10.14
2017-05-04 19:30 | 9.97 | 9.96
2017-05-04 20:00 | 9.98 | 9.97
2017-05-04 20:30 | 9.81 | 9.8
2017-05-04 21:00 | 9.25 | 9.24
2017-05-04 21:30 | 8.74 | 8.72
2017-05-04 22:00 | 8.09 | 8.08
2017-05-04 22:30 | 7.71 | 7.7
2017-05-04 23:00 | 7.41 | 7.4
2017-05-04 23:30 | 6.29 | 6.28
2017-05-05 | 5.39 | 5.38
2017-05-05 00:30 | 4.82 | 4.81
2017-05-05 01:00 | 4.6 | 4.58
2017-05-05 01:30 | 4.3 | 4.28
2017-05-05 02:00 | 4.04 | 4.03
2017-05-05 02:30 | 3.9 | 3.88
2017-05-05 03:00 | 3.84 | 3.82
2017-05-05 03:30 | 3.98 | 3.96
2017-05-05 04:00 | 3.93 | 3.91
2017-05-05 04:30 | 4.17 | 4.15
2017-05-05 05:00 | 4.47 | 4.45
2017-05-05 05:30 | 4.92 | 4.9
2017-05-05 06:00 | 5.28 | 5.27
2017-05-05 06:30 | 5.75 | 5.73
2017-05-05 07:00 | 6.29 | 6.28
2017-05-05 07:30 | 6.37 | 6.36
2017-05-05 08:00 | 5.9 | 5.88
2017-05-05 08:30 | 4.87 | 4.85
2017-05-05 09:00 | 4.09 | 4.07
2017-05-05 09:30 | 3.69 | 3.66
2017-05-05 10:00 | 3.36 | 3.33
2017-05-05 10:30 | 3.21 | 3.17
2017-05-05 11:00 | 3.35 | 3.32
2017-05-05 11:30 | 2.87 | 2.83
2017-05-05 12:00 | 3.78 | 3.74
2017-05-05 12:30 | 3.43 | 3.4
2017-05-05 13:00 | 3.85 | 3.82
2017-05-05 13:30 | 3.48 | 3.45
2017-05-05 14:00 | 5.28 | 5.26
2017-05-05 14:30 | 4.21 | 4.19
2017-05-05 15:00 | 5.23 | 5.21
2017-05-05 15:30 | 4.74 | 4.71
2017-05-05 16:00 | 5.97 | 5.94
2017-05-05 16:30 | 6.53 | 6.51
2017-05-05 17:00 | 7.75 | 7.74
2017-05-05 17:30 | 8.16 | 8.14
2017-05-05 18:00 | 9.04 | 9.02
2017-05-05 18:30 | 9.45 | 9.44
2017-05-05 19:00 | 9.6 | 9.59
2017-05-05 19:30 | 9.41 | 9.4
2017-05-05 20:00 | 9.39 | 9.37
2017-05-05 20:30 | 9.23 | 9.22
2017-05-05 21:00 | 8.76 | 8.75
2017-05-05 21:30 | 8.27 | 8.26
2017-05-05 22:00 | 7.76 | 7.74
2017-05-05 22:30 | 7.55 | 7.54
2017-05-05 23:00 | 7.48 | 7.46
2017-05-05 23:30 | 6.69 | 6.67
2017-05-06 | 5.81 | 5.8
2017-05-06 00:30 | 5.21 | 5.19
2017-05-06 01:00 | 4.87 | 4.86
2017-05-06 01:30 | 4.4 | 4.38
2017-05-06 02:00 | 4.26 | 4.24
2017-05-06 02:30 | 4.1 | 4.08
2017-05-06 03:00 | 3.97 | 3.95
2017-05-06 03:30 | 4.02 | 4
2017-05-06 04:00 | 3.95 | 3.92
2017-05-06 04:30 | 3.91 | 3.88
2017-05-06 05:00 | 4.07 | 4.05
2017-05-06 05:30 | 4.24 | 4.21
2017-05-06 06:00 | 4.42 | 4.4
2017-05-06 06:30 | 4.56 | 4.52
2017-05-06 07:00 | 4.84 | 4.8
2017-05-06 07:30 | 4.91 | 4.86
2017-05-06 08:00 | 4.99 | 4.96
2017-05-06 08:30 | 4.89 | 4.86
2017-05-06 09:00 | 4.65 | 4.63
2017-05-06 09:30 | 4.67 | 4.65
2017-05-06 10:00 | 4.5 | 4.47
2017-05-06 10:30 | 3.82 | 3.79
2017-05-06 11:00 | 3.67 | 3.63
2017-05-06 11:30 | 3.9 | 3.87
2017-05-06 12:00 | 3.68 | 3.64
2017-05-06 12:30 | 3.86 | 3.82
2017-05-06 13:00 | 5.17 | 5.14
2017-05-06 13:30 | 5 | 4.97
2017-05-06 14:00 | 5.13 | 5.1
2017-05-06 14:30 | 4.79 | 4.76
2017-05-06 15:00 | 4.93 | 4.91
2017-05-06 15:30 | 6.23 | 6.21
2017-05-06 16:00 | 6.35 | 6.33
2017-05-06 16:30 | 6.86 | 6.84
2017-05-06 17:00 | 7.63 | 7.62
2017-05-06 17:30 | 8.33 | 8.32
2017-05-06 18:00 | 9.16 | 9.14
2017-05-06 18:30 | 9.19 | 9.17
2017-05-06 19:00 | 9.25 | 9.23
2017-05-06 19:30 | 8.89 | 8.87
2017-05-06 20:00 | 8.86 | 8.85
2017-05-06 20:30 | 8.79 | 8.77
2017-05-06 21:00 | 8.44 | 8.43
2017-05-06 21:30 | 8.07 | 8.05
2017-05-06 22:00 | 7.47 | 7.46
2017-05-06 22:30 | 7.33 | 7.32
2017-05-06 23:00 | 7.35 | 7.34
2017-05-06 23:30 | 6.53 | 6.52
2017-05-07 | 5.71 | 5.7
2017-05-07 00:30 | 5.2 | 5.19
2017-05-07 01:00 | 4.88 | 4.86
2017-05-07 01:30 | 4.5 | 4.48
2017-05-07 02:00 | 4.19 | 4.17
2017-05-07 02:30 | 3.99 | 3.97
2017-05-07 03:00 | 3.88 | 3.86
2017-05-07 03:30 | 3.89 | 3.87
2017-05-07 04:00 | 3.85 | 3.82
2017-05-07 04:30 | 3.93 | 3.9
2017-05-07 05:00 | 3.95 | 3.93
2017-05-07 05:30 | 4.05 | 4.03
2017-05-07 06:00 | 4.17 | 4.15
2017-05-07 06:30 | 4.23 | 4.19
2017-05-07 07:00 | 4.67 | 4.62
2017-05-07 07:30 | 5.03 | 4.98
2017-05-07 08:00 | 5.22 | 5.18
2017-05-07 08:30 | 5.31 | 5.28
2017-05-07 09:00 | 5.48 | 5.45
2017-05-07 09:30 | 5.03 | 5.01
2017-05-07 10:00 | 4.71 | 4.68
2017-05-07 10:30 | 4.26 | 4.23
2017-05-07 11:00 | 4 | 3.97
2017-05-07 11:30 | 3.92 | 3.89
2017-05-07 12:00 | 3.89 | 3.86
2017-05-07 12:30 | 3.86 | 3.83
2017-05-07 13:00 | 4.02 | 3.98
2017-05-07 13:30 | 4.18 | 4.15
2017-05-07 14:00 | 4.5 | 4.47
2017-05-07 14:30 | 5.45 | 5.43
2017-05-07 15:00 | 5.47 | 5.45
2017-05-07 15:30 | 5.96 | 5.94
2017-05-07 16:00 | 6.7 | 6.67
2017-05-07 16:30 | 7.55 | 7.54
2017-05-07 17:00 | 8.74 | 8.73
2017-05-07 17:30 | 9.71 | 9.7
2017-05-07 18:00 | 10.58 | 10.56
2017-05-07 18:30 | 10.61 | 10.6
2017-05-07 19:00 | 10.37 | 10.36
2017-05-07 19:30 | 9.76 | 9.75
2017-05-07 20:00 | 9.64 | 9.62
2017-05-07 20:30 | 9.47 | 9.46
2017-05-07 21:00 | 9.01 | 8.99
2017-05-07 21:30 | 8.36 | 8.35
2017-05-07 22:00 | 7.58 | 7.57
2017-05-07 22:30 | 7.32 | 7.31
2017-05-07 23:00 | 7.16 | 7.15
2017-05-07 23:30 | 6.32 | 6.3
2017-05-08 | 5.43 | 5.41
2017-05-08 00:30 | 4.84 | 4.82
2017-05-08 01:00 | 4.51 | 4.49
2017-05-08 01:30 | 4.23 | 4.21
2017-05-08 02:00 | 3.92 | 3.9
2017-05-08 02:30 | 3.8 | 3.78
2017-05-08 03:00 | 3.71 | 3.69
2017-05-08 03:30 | 3.87 | 3.85
2017-05-08 04:00 | 3.9 | 3.88
2017-05-08 04:30 | 4.1 | 4.08
2017-05-08 05:00 | 4.35 | 4.33
2017-05-08 05:30 | 4.94 | 4.93
2017-05-08 06:00 | 5.93 | 5.93
2017-05-08 06:30 | 6.56 | 6.55
2017-05-08 07:00 | 7.14 | 7.14
2017-05-08 07:30 | 7.73 | 7.72
2017-05-08 08:00 | 7.49 | 7.49
2017-05-08 08:30 | 6.99 | 6.98
2017-05-08 09:00 | 5.25 | 5.24
2017-05-08 09:30 | 4.47 | 4.45
2017-05-08 10:00 | 5.47 | 5.46
2017-05-08 10:30 | 5.02 | 5
2017-05-08 11:00 | 5.29 | 5.28
2017-05-08 11:30 | 5.57 | 5.56
2017-05-08 12:00 | 5.11 | 5.1
2017-05-08 12:30 | 5.16 | 5.15
2017-05-08 13:00 | 5.15 | 5.13
2017-05-08 13:30 | 5.6 | 5.58
2017-05-08 14:00 | 5.84 | 5.82
2017-05-08 14:30 | 5.64 | 5.62
2017-05-08 15:00 | 6.11 | 6.09
2017-05-08 15:30 | 6.31 | 6.29
2017-05-08 16:00 | 7.26 | 7.24
2017-05-08 16:30 | 8.41 | 8.39
2017-05-08 17:00 | 9.16 | 9.14
2017-05-08 17:30 | 10.13 | 10.11
2017-05-08 18:00 | 10.85 | 10.84
2017-05-08 18:30 | 10.98 | 10.96
2017-05-08 19:00 | 10.89 | 10.87
2017-05-08 19:30 | 10.35 | 10.33
2017-05-08 20:00 | 10.2 | 10.19
2017-05-08 20:30 | 10.23 | 10.22
2017-05-08 21:00 | 9.71 | 9.69
2017-05-08 21:30 | 8.87 | 8.86
2017-05-08 22:00 | 8.21 | 8.19
2017-05-08 22:30 | 7.93 | 7.91
2017-05-08 23:00 | 7.55 | 7.53
2017-05-08 23:30 | 6.64 | 6.62
2017-05-09 | 5.68 | 5.67
2017-05-09 00:30 | 5.07 | 5.05
2017-05-09 01:00 | 4.71 | 4.69
2017-05-09 01:30 | 4.27 | 4.25
2017-05-09 02:00 | 4.02 | 4
2017-05-09 02:30 | 3.88 | 3.86
2017-05-09 03:00 | 3.84 | 3.82
2017-05-09 03:30 | 3.85 | 3.83
2017-05-09 04:00 | 3.91 | 3.89
2017-05-09 04:30 | 4.15 | 4.13
2017-05-09 05:00 | 4.48 | 4.46
2017-05-09 05:30 | 5.03 | 5.02
2017-05-09 06:00 | 5.69 | 5.68
2017-05-09 06:30 | 6.19 | 6.18
2017-05-09 07:00 | 6.89 | 6.88
2017-05-09 07:30 | 7.43 | 7.42
2017-05-09 08:00 | 7.37 | 7.37
2017-05-09 08:30 | 6.33 | 6.32
2017-05-09 09:00 | 5.27 | 5.26
2017-05-09 09:30 | 4.86 | 4.85
2017-05-09 10:00 | 4.85 | 4.84
2017-05-09 10:30 | 4.28 | 4.27
2017-05-09 11:00 | 5 | 4.99
2017-05-09 11:30 | 5.12 | 5.11
2017-05-09 12:00 | 4.15 | 4.14
2017-05-09 12:30 | 3.79 | 3.79
2017-05-09 13:00 | 3.79 | 3.78
2017-05-09 13:30 | 3.27 | 3.24
2017-05-09 14:00 | 3.91 | 3.88
2017-05-09 14:30 | 4.64 | 4.62
2017-05-09 15:00 | 4.41 | 4.38
2017-05-09 15:30 | 5.5 | 5.48
2017-05-09 16:00 | 6.91 | 6.89
2017-05-09 16:30 | 7.68 | 7.67
2017-05-09 17:00 | 8.56 | 8.55
2017-05-09 17:30 | 9.66 | 9.64
2017-05-09 18:00 | 10.57 | 10.55
2017-05-09 18:30 | 10.7 | 10.67
2017-05-09 19:00 | 10.7 | 10.68
2017-05-09 19:30 | 10.34 | 10.32
2017-05-09 20:00 | 10.3 | 10.28
2017-05-09 20:30 | 10.15 | 10.14
2017-05-09 21:00 | 9.61 | 9.6
2017-05-09 21:30 | 8.73 | 8.72
2017-05-09 22:00 | 8.08 | 8.07
2017-05-09 22:30 | 7.74 | 7.73
2017-05-09 23:00 | 7.3 | 7.29
2017-05-09 23:30 | 6.44 | 6.42
2017-05-10 | 5.49 | 5.47
2017-05-10 00:30 | 4.83 | 4.81
2017-05-10 01:00 | 4.63 | 4.61
2017-05-10 01:30 | 4.27 | 4.25
2017-05-10 02:00 | 4.1 | 4.07
2017-05-10 02:30 | 4.01 | 3.99
2017-05-10 03:00 | 3.88 | 3.86
2017-05-10 03:30 | 3.95 | 3.92
2017-05-10 04:00 | 4.02 | 4
2017-05-10 04:30 | 4.23 | 4.2
2017-05-10 05:00 | 4.46 | 4.44
2017-05-10 05:30 | 5.09 | 5.07
2017-05-10 06:00 | 6.46 | 6.46
2017-05-10 06:30 | 7.42 | 7.42
2017-05-10 07:00 | 7.21 | 7.19
2017-05-10 07:30 | 7.72 | 7.72
2017-05-10 08:00 | 7.87 | 7.86
2017-05-10 08:30 | 6.95 | 6.94
2017-05-10 09:00 | 7.19 | 7.19
2017-05-10 09:30 | 7.07 | 7.06
2017-05-10 10:00 | 6.91 | 6.91
2017-05-10 10:30 | 7.28 | 7.28
2017-05-10 11:00 | 7.4 | 7.4
2017-05-10 11:30 | 7.38 | 7.37
2017-05-10 12:00 | 6.99 | 6.98
2017-05-10 12:30 | 7.23 | 7.22
2017-05-10 13:00 | 6.79 | 6.79
2017-05-10 13:30 | 6.13 | 6.12
2017-05-10 14:00 | 6.33 | 6.32
2017-05-10 14:30 | 6.64 | 6.63
2017-05-10 15:00 | 6.55 | 6.54
2017-05-10 15:30 | 6.95 | 6.93
2017-05-10 16:00 | 7.66 | 7.65
2017-05-10 16:30 | 8.18 | 8.17
2017-05-10 17:00 | 9.02 | 9.01
2017-05-10 17:30 | 10.19 | 10.18
2017-05-10 18:00 | 10.79 | 10.77
2017-05-10 18:30 | 10.98 | 10.96
2017-05-10 19:00 | 11.16 | 11.15
2017-05-10 19:30 | 10.87 | 10.86
2017-05-10 20:00 | 10.95 | 10.93
2017-05-10 20:30 | 10.81 | 10.8
2017-05-10 21:00 | 10.19 | 10.18
2017-05-10 21:30 | 9.37 | 9.36
2017-05-10 22:00 | 8.59 | 8.58
2017-05-10 22:30 | 8.01 | 8
2017-05-10 23:00 | 7.55 | 7.54
2017-05-10 23:30 | 6.62 | 6.61
2017-05-11 | 5.59 | 5.58
2017-05-11 00:30 | 5.04 | 5.03
2017-05-11 01:00 | 4.78 | 4.77
2017-05-11 01:30 | 4.45 | 4.44
2017-05-11 02:00 | 4.27 | 4.25
2017-05-11 02:30 | 4.01 | 3.99
2017-05-11 03:00 | 3.91 | 3.89
2017-05-11 03:30 | 3.98 | 3.95
2017-05-11 04:00 | 4.07 | 4.05
2017-05-11 04:30 | 4.27 | 4.26
2017-05-11 05:00 | 4.56 | 4.55
2017-05-11 05:30 | 5.1 | 5.09
2017-05-11 06:00 | 6.14 | 6.13
2017-05-11 06:30 | 6.96 | 6.95
2017-05-11 07:00 | 7.54 | 7.54
2017-05-11 07:30 | 7.55 | 7.54
2017-05-11 08:00 | 7.1 | 7.09
2017-05-11 08:30 | 6.15 | 6.14
2017-05-11 09:00 | 5.34 | 5.33
2017-05-11 09:30 | 4.91 | 4.9
2017-05-11 10:00 | 4.39 | 4.38
2017-05-11 10:30 | 4.09 | 4.08
2017-05-11 11:00 | 3.79 | 3.78
2017-05-11 11:30 | 3.81 | 3.79
2017-05-11 12:00 | 3.71 | 3.7
2017-05-11 12:30 | 3.44 | 3.43
2017-05-11 13:00 | 3.26 | 3.25
2017-05-11 13:30 | 3.42 | 3.38
2017-05-11 14:00 | 3.78 | 3.74
2017-05-11 14:30 | 3.94 | 3.91
2017-05-11 15:00 | 4.51 | 4.49
2017-05-11 15:30 | 4.84 | 4.82
2017-05-11 16:00 | 5.86 | 5.85
2017-05-11 16:30 | 6.82 | 6.8
2017-05-11 17:00 | 7.76 | 7.75
2017-05-11 17:30 | 8.73 | 8.73
2017-05-11 18:00 | 9.79 | 9.77
2017-05-11 18:30 | 10.17 | 10.15
2017-05-11 19:00 | 10.44 | 10.42
2017-05-11 19:30 | 9.96 | 9.95
2017-05-11 20:00 | 10.09 | 10.08
2017-05-11 20:30 | 10.09 | 10.08
2017-05-11 21:00 | 9.75 | 9.74
2017-05-11 21:30 | 9.09 | 9.08
2017-05-11 22:00 | 8.48 | 8.47
2017-05-11 22:30 | 8.12 | 8.1
2017-05-11 23:00 | 7.64 | 7.63
2017-05-11 23:30 | 6.73 | 6.72
2017-05-12 | 5.81 | 5.8
2017-05-12 00:30 | 5.11 | 5.1
2017-05-12 01:00 | 4.79 | 4.77
2017-05-12 01:30 | 4.45 | 4.43
2017-05-12 02:00 | 4.15 | 4.13
2017-05-12 02:30 | 4.01 | 4
2017-05-12 03:00 | 3.97 | 3.95
2017-05-12 03:30 | 4.03 | 4.01
2017-05-12 04:00 | 4.05 | 4.03
2017-05-12 04:30 | 4.22 | 4.2
2017-05-12 05:00 | 4.55 | 4.53
2017-05-12 05:30 | 4.97 | 4.95
2017-05-12 06:00 | 5.45 | 5.44
2017-05-12 06:30 | 5.97 | 5.95
2017-05-12 07:00 | 6.68 | 6.67
2017-05-12 07:30 | 7.07 | 7.06
2017-05-12 08:00 | 7.2 | 7.18
2017-05-12 08:30 | 6.43 | 6.41
2017-05-12 09:00 | 6.02 | 6
2017-05-12 09:30 | 5.3 | 5.28
2017-05-12 10:00 | 4.32 | 4.29
2017-05-12 10:30 | 3.74 | 3.69
2017-05-12 11:00 | 3.77 | 3.73
2017-05-12 11:30 | 4.64 | 4.61
2017-05-12 12:00 | 3.95 | 3.93
2017-05-12 12:30 | 3.6 | 3.57
2017-05-12 13:00 | 5.28 | 5.26
2017-05-12 13:30 | 5.81 | 5.78
2017-05-12 14:00 | 5.35 | 5.33
2017-05-12 14:30 | 5.87 | 5.85
2017-05-12 15:00 | 5.85 | 5.83
2017-05-12 15:30 | 5.74 | 5.71
2017-05-12 16:00 | 6.45 | 6.43
2017-05-12 16:30 | 7.27 | 7.25
2017-05-12 17:00 | 8.25 | 8.23
2017-05-12 17:30 | 9.26 | 9.24
2017-05-12 18:00 | 9.66 | 9.65
2017-05-12 18:30 | 9.76 | 9.74
2017-05-12 19:00 | 9.97 | 9.95
2017-05-12 19:30 | 9.69 | 9.68
2017-05-12 20:00 | 9.59 | 9.58
2017-05-12 20:30 | 9.69 | 9.68
2017-05-12 21:00 | 9.28 | 9.27
2017-05-12 21:30 | 8.77 | 8.76
2017-05-12 22:00 | 8.14 | 8.12
2017-05-12 22:30 | 7.79 | 7.78
2017-05-12 23:00 | 7.79 | 7.78
2017-05-12 23:30 | 6.87 | 6.86
2017-05-13 | 6.02 | 6
2017-05-13 00:30 | 5.34 | 5.32
2017-05-13 01:00 | 5.01 | 4.99
2017-05-13 01:30 | 4.59 | 4.58
2017-05-13 02:00 | 4.33 | 4.31
2017-05-13 02:30 | 4.19 | 4.17
2017-05-13 03:00 | 4.06 | 4.04
2017-05-13 03:30 | 4.25 | 4.22
2017-05-13 04:00 | 4.12 | 4.09
2017-05-13 04:30 | 4.13 | 4.11
2017-05-13 05:00 | 4.21 | 4.19
2017-05-13 05:30 | 4.22 | 4.19
2017-05-13 06:00 | 4.42 | 4.39
2017-05-13 06:30 | 4.59 | 4.56
2017-05-13 07:00 | 4.9 | 4.86
2017-05-13 07:30 | 5.46 | 5.43
2017-05-13 08:00 | 5.9 | 5.88
2017-05-13 08:30 | 6.25 | 6.23
2017-05-13 09:00 | 6.74 | 6.72
2017-05-13 09:30 | 6.37 | 6.35
2017-05-13 10:00 | 5.2 | 5.17
2017-05-13 10:30 | 4.44 | 4.41
2017-05-13 11:00 | 5.23 | 5.2
2017-05-13 11:30 | 4.3 | 4.27
2017-05-13 12:00 | 5.27 | 5.24
2017-05-13 12:30 | 6.66 | 6.64
2017-05-13 13:00 | 7.6 | 7.57
2017-05-13 13:30 | 6.97 | 6.95
2017-05-13 14:00 | 7.03 | 7.01
2017-05-13 14:30 | 6.91 | 6.89
2017-05-13 15:00 | 7.38 | 7.36
2017-05-13 15:30 | 7.34 | 7.32
2017-05-13 16:00 | 7.83 | 7.81
2017-05-13 16:30 | 7.95 | 7.93
2017-05-13 17:00 | 8.64 | 8.63
2017-05-13 17:30 | 9.35 | 9.33
2017-05-13 18:00 | 10.07 | 10.05
2017-05-13 18:30 | 10.14 | 10.12
2017-05-13 19:00 | 9.89 | 9.87
2017-05-13 19:30 | 9.47 | 9.46
2017-05-13 20:00 | 9.41 | 9.39
2017-05-13 20:30 | 9.42 | 9.4
2017-05-13 21:00 | 8.99 | 8.97
2017-05-13 21:30 | 8.54 | 8.52
2017-05-13 22:00 | 8 | 7.98
2017-05-13 22:30 | 7.79 | 7.78
2017-05-13 23:00 | 7.67 | 7.66
2017-05-13 23:30 | 6.89 | 6.88
2017-05-14 | 6.12 | 6.11
2017-05-14 00:30 | 5.37 | 5.36
2017-05-14 01:00 | 5.08 | 5.07
2017-05-14 01:30 | 4.65 | 4.64
2017-05-14 02:00 | 4.26 | 4.24
2017-05-14 02:30 | 4.17 | 4.16
2017-05-14 03:00 | 3.99 | 3.97
2017-05-14 03:30 | 3.87 | 3.85
2017-05-14 04:00 | 3.94 | 3.92
2017-05-14 04:30 | 3.95 | 3.93
2017-05-14 05:00 | 4 | 3.97
2017-05-14 05:30 | 4.1 | 4.07
2017-05-14 06:00 | 4.26 | 4.23
2017-05-14 06:30 | 4.54 | 4.51
2017-05-14 07:00 | 4.9 | 4.86
2017-05-14 07:30 | 5.53 | 5.49
2017-05-14 08:00 | 6.01 | 5.98
2017-05-14 08:30 | 6.75 | 6.73
2017-05-14 09:00 | 7.11 | 7.09
2017-05-14 09:30 | 6.96 | 6.94
2017-05-14 10:00 | 6.4 | 6.38
2017-05-14 10:30 | 6.64 | 6.61
2017-05-14 11:00 | 6.75 | 6.73
2017-05-14 11:30 | 6.82 | 6.8
2017-05-14 12:00 | 6.3 | 6.28
2017-05-14 12:30 | 6.05 | 6.03
2017-05-14 13:00 | 6.11 | 6.09
2017-05-14 13:30 | 6.54 | 6.52
2017-05-14 14:00 | 6.9 | 6.88
2017-05-14 14:30 | 6.73 | 6.71
2017-05-14 15:00 | 6.72 | 6.7
2017-05-14 15:30 | 7.29 | 7.28
2017-05-14 16:00 | 7.66 | 7.64
2017-05-14 16:30 | 8.3 | 8.28
2017-05-14 17:00 | 9.23 | 9.22
2017-05-14 17:30 | 10.23 | 10.21
2017-05-14 18:00 | 10.64 | 10.62
2017-05-14 18:30 | 10.52 | 10.5
2017-05-14 19:00 | 10.3 | 10.28
2017-05-14 19:30 | 9.86 | 9.84
2017-05-14 20:00 | 9.8 | 9.78
2017-05-14 20:30 | 9.81 | 9.79
2017-05-14 21:00 | 9.35 | 9.34
2017-05-14 21:30 | 8.69 | 8.68
2017-05-14 22:00 | 8.07 | 8.06
2017-05-14 22:30 | 7.58 | 7.57
2017-05-14 23:00 | 7.33 | 7.32
2017-05-14 23:30 | 6.56 | 6.55
2017-05-15 | 5.69 | 5.68
2017-05-15 00:30 | 5.09 | 5.07
2017-05-15 01:00 | 4.8 | 4.78
2017-05-15 01:30 | 4.39 | 4.37
2017-05-15 02:00 | 4.13 | 4.11
2017-05-15 02:30 | 3.95 | 3.93
2017-05-15 03:00 | 3.89 | 3.87
2017-05-15 03:30 | 4.03 | 4.01
2017-05-15 04:00 | 3.96 | 3.94
2017-05-15 04:30 | 4.21 | 4.18
2017-05-15 05:00 | 4.51 | 4.49
2017-05-15 05:30 | 4.97 | 4.95
2017-05-15 06:00 | 5.94 | 5.93
2017-05-15 06:30 | 6.65 | 6.64
2017-05-15 07:00 | 7.21 | 7.2
2017-05-15 07:30 | 7.73 | 7.72
2017-05-15 08:00 | 7.22 | 7.21
2017-05-15 08:30 | 6.27 | 6.25
2017-05-15 09:00 | 5.55 | 5.54
2017-05-15 09:30 | 5.21 | 5.19
2017-05-15 10:00 | 4.77 | 4.75
2017-05-15 10:30 | 4.41 | 4.39
2017-05-15 11:00 | 4.17 | 4.15
2017-05-15 11:30 | 3.97 | 3.95
2017-05-15 12:00 | 3.89 | 3.88
2017-05-15 12:30 | 4.3 | 4.29
2017-05-15 13:00 | 6.01 | 6.01
2017-05-15 13:30 | 4.28 | 4.25
2017-05-15 14:00 | 3.95 | 3.92
2017-05-15 14:30 | 4.52 | 4.5
2017-05-15 15:00 | 4.88 | 4.86
2017-05-15 15:30 | 5.28 | 5.26
2017-05-15 16:00 | 6.22 | 6.2
2017-05-15 16:30 | 7.32 | 7.31
2017-05-15 17:00 | 8.33 | 8.32
2017-05-15 17:30 | 9.55 | 9.54
2017-05-15 18:00 | 10.59 | 10.57
2017-05-15 18:30 | 10.72 | 10.7
2017-05-15 19:00 | 10.68 | 10.67
2017-05-15 19:30 | 10.38 | 10.37
2017-05-15 20:00 | 10.15 | 10.14
2017-05-15 20:30 | 10.12 | 10.1
2017-05-15 21:00 | 9.63 | 9.62
2017-05-15 21:30 | 8.8 | 8.78
2017-05-15 22:00 | 7.98 | 7.97
2017-05-15 22:30 | 7.58 | 7.57
2017-05-15 23:00 | 7.38 | 7.37
2017-05-15 23:30 | 6.46 | 6.45
2017-05-16 | 5.75 | 5.74
2017-05-16 00:30 | 4.97 | 4.95
2017-05-16 01:00 | 4.63 | 4.61
2017-05-16 01:30 | 4.39 | 4.37
2017-05-16 02:00 | 4.17 | 4.16
2017-05-16 02:30 | 4.07 | 4.05
2017-05-16 03:00 | 3.95 | 3.92
2017-05-16 03:30 | 3.87 | 3.85
2017-05-16 04:00 | 4.04 | 4.01
2017-05-16 04:30 | 4.17 | 4.16
2017-05-16 05:00 | 4.48 | 4.46
2017-05-16 05:30 | 5.35 | 5.34
2017-05-16 06:00 | 6.32 | 6.31
2017-05-16 06:30 | 7.06 | 7.06
2017-05-16 07:00 | 7.54 | 7.53
2017-05-16 07:30 | 7.7 | 7.69
2017-05-16 08:00 | 7.23 | 7.22
2017-05-16 08:30 | 6.09 | 6.08
2017-05-16 09:00 | 5.2 | 5.19
2017-05-16 09:30 | 4.64 | 4.63
2017-05-16 10:00 | 4.22 | 4.21
2017-05-16 10:30 | 3.86 | 3.84
2017-05-16 11:00 | 3.52 | 3.5
2017-05-16 11:30 | 3.52 | 3.51
2017-05-16 12:00 | 4.49 | 4.48
2017-05-16 12:30 | 4.43 | 4.43
2017-05-16 13:00 | 4.41 | 4.41
2017-05-16 13:30 | 4.35 | 4.34
2017-05-16 14:00 | 3.72 | 3.69
2017-05-16 14:30 | 4.1 | 4.07
2017-05-16 15:00 | 4.36 | 4.33
2017-05-16 15:30 | 4.94 | 4.91
2017-05-16 16:00 | 5.93 | 5.91
2017-05-16 16:30 | 6.86 | 6.84
2017-05-16 17:00 | 7.98 | 7.97
2017-05-16 17:30 | 9.17 | 9.16
2017-05-16 18:00 | 10.31 | 10.29
2017-05-16 18:30 | 10.61 | 10.59
2017-05-16 19:00 | 10.69 | 10.67
2017-05-16 19:30 | 10.2 | 10.18
2017-05-16 20:00 | 10.1 | 10.09
2017-05-16 20:30 | 10.14 | 10.13
2017-05-16 21:00 | 9.66 | 9.65
2017-05-16 21:30 | 8.77 | 8.76
2017-05-16 22:00 | 8.11 | 8.1
2017-05-16 22:30 | 7.75 | 7.74
2017-05-16 23:00 | 7.35 | 7.34
2017-05-16 23:30 | 6.45 | 6.44
2017-05-17 | 5.63 | 5.62
2017-05-17 00:30 | 4.88 | 4.87
2017-05-17 01:00 | 4.56 | 4.54
2017-05-17 01:30 | 4.35 | 4.33
2017-05-17 02:00 | 4.14 | 4.12
2017-05-17 02:30 | 4.01 | 4
2017-05-17 03:00 | 3.92 | 3.9
2017-05-17 03:30 | 3.98 | 3.96
2017-05-17 04:00 | 4.03 | 4.01
2017-05-17 04:30 | 4.25 | 4.23
2017-05-17 05:00 | 4.62 | 4.6
2017-05-17 05:30 | 5.2 | 5.19
2017-05-17 06:00 | 6.04 | 6.04
2017-05-17 06:30 | 6.8 | 6.8
2017-05-17 07:00 | 7.38 | 7.38
2017-05-17 07:30 | 7.71 | 7.7
2017-05-17 08:00 | 7.1 | 7.1
2017-05-17 08:30 | 6.05 | 6.04
2017-05-17 09:00 | 5.46 | 5.45
2017-05-17 09:30 | 5.25 | 5.24
2017-05-17 10:00 | 4.87 | 4.86
2017-05-17 10:30 | 4.33 | 4.32
2017-05-17 11:00 | 3.65 | 3.64
2017-05-17 11:30 | 3.49 | 3.48
2017-05-17 12:00 | 3.6 | 3.59
2017-05-17 12:30 | 3.67 | 3.66
2017-05-17 13:00 | 4.13 | 4.11
2017-05-17 13:30 | 3.92 | 3.91
2017-05-17 14:00 | 4.73 | 4.72
2017-05-17 14:30 | 5.25 | 5.24
2017-05-17 15:00 | 4.82 | 4.81
2017-05-17 15:30 | 5.34 | 5.33
2017-05-17 16:00 | 5.82 | 5.81
2017-05-17 16:30 | 6.76 | 6.75
2017-05-17 17:00 | 7.99 | 7.97
2017-05-17 17:30 | 9.08 | 9.07
2017-05-17 18:00 | 10.2 | 10.18
2017-05-17 18:30 | 10.34 | 10.32
2017-05-17 19:00 | 10.54 | 10.52
2017-05-17 19:30 | 10.3 | 10.29
2017-05-17 20:00 | 10.15 | 10.14
2017-05-17 20:30 | 10.15 | 10.14
2017-05-17 21:00 | 9.66 | 9.65
2017-05-17 21:30 | 8.88 | 8.87
2017-05-17 22:00 | 8.07 | 8.06
2017-05-17 22:30 | 7.57 | 7.56
2017-05-17 23:00 | 7.39 | 7.38
2017-05-17 23:30 | 6.49 | 6.48
2017-05-18 | 5.65 | 5.64
2017-05-18 00:30 | 4.97 | 4.95
2017-05-18 01:00 | 4.73 | 4.71
2017-05-18 01:30 | 4.34 | 4.32
2017-05-18 02:00 | 4.12 | 4.1
2017-05-18 02:30 | 4.01 | 3.99
2017-05-18 03:00 | 3.97 | 3.95
2017-05-18 03:30 | 3.94 | 3.92
2017-05-18 04:00 | 3.99 | 3.97
2017-05-18 04:30 | 4.13 | 4.11
2017-05-18 05:00 | 4.47 | 4.46
2017-05-18 05:30 | 5.09 | 5.08
2017-05-18 06:00 | 6.09 | 6.08
2017-05-18 06:30 | 6.73 | 6.72
2017-05-18 07:00 | 7.25 | 7.25
2017-05-18 07:30 | 7.89 | 7.88
2017-05-18 08:00 | 7.79 | 7.79
2017-05-18 08:30 | 7.12 | 7.11
2017-05-18 09:00 | 6.95 | 6.94
2017-05-18 09:30 | 6.17 | 6.16
2017-05-18 10:00 | 5.77 | 5.75
2017-05-18 10:30 | 5.79 | 5.78
2017-05-18 11:00 | 5.91 | 5.9
2017-05-18 11:30 | 5.43 | 5.42
2017-05-18 12:00 | 5.45 | 5.44
2017-05-18 12:30 | 5.01 | 5
2017-05-18 13:00 | 5.22 | 5.22
2017-05-18 13:30 | 5.14 | 5.13
2017-05-18 14:00 | 5.13 | 5.12
2017-05-18 14:30 | 5.21 | 5.2
2017-05-18 15:00 | 5.6 | 5.59
2017-05-18 15:30 | 5.73 | 5.71
2017-05-18 16:00 | 6.42 | 6.4
2017-05-18 16:30 | 7.05 | 7.04
2017-05-18 17:00 | 8.1 | 8.09
2017-05-18 17:30 | 9.33 | 9.32
2017-05-18 18:00 | 9.92 | 9.9
2017-05-18 18:30 | 10.07 | 10.05
2017-05-18 19:00 | 10.24 | 10.22
2017-05-18 19:30 | 9.89 | 9.88
2017-05-18 20:00 | 9.88 | 9.87
2017-05-18 20:30 | 9.93 | 9.92
2017-05-18 21:00 | 9.44 | 9.43
2017-05-18 21:30 | 8.71 | 8.7
2017-05-18 22:00 | 8.09 | 8.08
2017-05-18 22:30 | 7.64 | 7.63
2017-05-18 23:00 | 7.51 | 7.5
2017-05-18 23:30 | 6.74 | 6.73
2017-05-19 | 5.77 | 5.76
2017-05-19 00:30 | 5.13 | 5.12
2017-05-19 01:00 | 4.87 | 4.86
2017-05-19 01:30 | 4.46 | 4.45
2017-05-19 02:00 | 4.23 | 4.22
2017-05-19 02:30 | 4.06 | 4.05
2017-05-19 03:00 | 3.94 | 3.92
2017-05-19 03:30 | 4 | 3.98
2017-05-19 04:00 | 3.96 | 3.94
2017-05-19 04:30 | 4.03 | 4.01
2017-05-19 05:00 | 4.31 | 4.29
2017-05-19 05:30 | 4.69 | 4.67
2017-05-19 06:00 | 5.01 | 4.99
2017-05-19 06:30 | 5.49 | 5.47
2017-05-19 07:00 | 5.67 | 5.65
2017-05-19 07:30 | 6.03 | 6.01
2017-05-19 08:00 | 6.06 | 6.04
2017-05-19 08:30 | 6.48 | 6.46
2017-05-19 09:00 | 6.73 | 6.72
2017-05-19 09:30 | 6.59 | 6.57
2017-05-19 10:00 | 6.66 | 6.64
2017-05-19 10:30 | 6.99 | 6.97
2017-05-19 11:00 | 6.54 | 6.52
2017-05-19 11:30 | 6.38 | 6.35
2017-05-19 12:00 | 7.14 | 7.12
2017-05-19 12:30 | 7.21 | 7.19
2017-05-19 13:00 | 7.1 | 7.08
2017-05-19 13:30 | 6.82 | 6.8
2017-05-19 14:00 | 6.95 | 6.93
2017-05-19 14:30 | 6.91 | 6.89
2017-05-19 15:00 | 7.19 | 7.17
2017-05-19 15:30 | 7.6 | 7.58
2017-05-19 16:00 | 7.9 | 7.88
2017-05-19 16:30 | 8.23 | 8.21
2017-05-19 17:00 | 8.96 | 8.95
2017-05-19 17:30 | 10.02 | 10.01
2017-05-19 18:00 | 10.26 | 10.25
2017-05-19 18:30 | 10.05 | 10.04
2017-05-19 19:00 | 10.02 | 10.01
2017-05-19 19:30 | 9.75 | 9.74
2017-05-19 20:00 | 9.69 | 9.68
2017-05-19 20:30 | 9.62 | 9.61
2017-05-19 21:00 | 9.18 | 9.16
2017-05-19 21:30 | 8.62 | 8.61
2017-05-19 22:00 | 8.03 | 8.02
2017-05-19 22:30 | 7.87 | 7.86
2017-05-19 23:00 | 7.74 | 7.73
2017-05-19 23:30 | 7.01 | 7
2017-05-20 | 6.19 | 6.18
2017-05-20 00:30 | 5.42 | 5.41
2017-05-20 01:00 | 4.93 | 4.91
2017-05-20 01:30 | 4.6 | 4.58
2017-05-20 02:00 | 4.36 | 4.34
2017-05-20 02:30 | 4.24 | 4.22
2017-05-20 03:00 | 4 | 3.98
2017-05-20 03:30 | 4 | 3.98
2017-05-20 04:00 | 3.93 | 3.91
2017-05-20 04:30 | 3.98 | 3.95
2017-05-20 05:00 | 4.06 | 4.04
2017-05-20 05:30 | 4.26 | 4.23
2017-05-20 06:00 | 4.38 | 4.35
2017-05-20 06:30 | 4.64 | 4.61
2017-05-20 07:00 | 4.91 | 4.88
2017-05-20 07:30 | 5.41 | 5.39
2017-05-20 08:00 | 5.56 | 5.54
2017-05-20 08:30 | 5.63 | 5.61
2017-05-20 09:00 | 5.46 | 5.44
2017-05-20 09:30 | 5.4 | 5.37
2017-05-20 10:00 | 5.27 | 5.24
2017-05-20 10:30 | 5.29 | 5.26
2017-05-20 11:00 | 5.32 | 5.29
2017-05-20 11:30 | 5.84 | 5.82
2017-05-20 12:00 | 5.91 | 5.88
2017-05-20 12:30 | 6.03 | 6
2017-05-20 13:00 | 5.71 | 5.68
2017-05-20 13:30 | 6.37 | 6.34
2017-05-20 14:00 | 5.49 | 5.46
2017-05-20 14:30 | 5.04 | 5
2017-05-20 15:00 | 5.37 | 5.34
2017-05-20 15:30 | 6.02 | 5.99
2017-05-20 16:00 | 6.57 | 6.54
2017-05-20 16:30 | 7.25 | 7.23
2017-05-20 17:00 | 8.12 | 8.11
2017-05-20 17:30 | 9.07 | 9.05
2017-05-20 18:00 | 9.78 | 9.76
2017-05-20 18:30 | 9.81 | 9.79
2017-05-20 19:00 | 9.72 | 9.7
2017-05-20 19:30 | 9.29 | 9.27
2017-05-20 20:00 | 9.26 | 9.24
2017-05-20 20:30 | 9.29 | 9.27
2017-05-20 21:00 | 8.85 | 8.83
2017-05-20 21:30 | 8.35 | 8.33
2017-05-20 22:00 | 7.87 | 7.85
2017-05-20 22:30 | 7.67 | 7.65
2017-05-20 23:00 | 7.74 | 7.73
2017-05-20 23:30 | 6.97 | 6.96
2017-05-21 | 6.17 | 6.16
2017-05-21 00:30 | 5.46 | 5.44
2017-05-21 01:00 | 5.05 | 5.03
2017-05-21 01:30 | 4.64 | 4.62
2017-05-21 02:00 | 4.41 | 4.39
2017-05-21 02:30 | 4.21 | 4.18
2017-05-21 03:00 | 4.11 | 4.08
2017-05-21 03:30 | 3.94 | 3.92
2017-05-21 04:00 | 4.07 | 4.04
2017-05-21 04:30 | 4.08 | 4.05
2017-05-21 05:00 | 4.05 | 4.02
2017-05-21 05:30 | 4.08 | 4.05
2017-05-21 06:00 | 4.26 | 4.23
2017-05-21 06:30 | 4.57 | 4.54
2017-05-21 07:00 | 4.69 | 4.65
2017-05-21 07:30 | 5.19 | 5.15
2017-05-21 08:00 | 5.66 | 5.64
2017-05-21 08:30 | 6.08 | 6.06
2017-05-21 09:00 | 6.59 | 6.57
2017-05-21 09:30 | 7.01 | 6.98
2017-05-21 10:00 | 7.14 | 7.12
2017-05-21 10:30 | 7.17 | 7.15
2017-05-21 11:00 | 7.41 | 7.39
2017-05-21 11:30 | 7.32 | 7.3
2017-05-21 12:00 | 6.7 | 6.68
2017-05-21 12:30 | 5.64 | 5.6
2017-05-21 13:00 | 4.79 | 4.75
2017-05-21 13:30 | 4.93 | 4.9
2017-05-21 14:00 | 5.23 | 5.2
2017-05-21 14:30 | 5.42 | 5.39
2017-05-21 15:00 | 5.96 | 5.93
2017-05-21 15:30 | 6.65 | 6.63
2017-05-21 16:00 | 7.31 | 7.29
2017-05-21 16:30 | 8.17 | 8.15
2017-05-21 17:00 | 8.98 | 8.97
2017-05-21 17:30 | 10.13 | 10.12
2017-05-21 18:00 | 10.98 | 10.96
2017-05-21 18:30 | 10.89 | 10.87
2017-05-21 19:00 | 10.55 | 10.53
2017-05-21 19:30 | 10.05 | 10.04
2017-05-21 20:00 | 9.88 | 9.86
2017-05-21 20:30 | 9.79 | 9.78
2017-05-21 21:00 | 9.32 | 9.31
2017-05-21 21:30 | 8.55 | 8.54
2017-05-21 22:00 | 7.96 | 7.95
2017-05-21 22:30 | 7.64 | 7.63
2017-05-21 23:00 | 7.37 | 7.36
2017-05-21 23:30 | 6.53 | 6.52
2017-05-22 | 5.63 | 5.62
2017-05-22 00:30 | 5.01 | 5
2017-05-22 01:00 | 4.64 | 4.63
2017-05-22 01:30 | 4.34 | 4.32
2017-05-22 02:00 | 4.09 | 4.07
2017-05-22 02:30 | 4.02 | 4
2017-05-22 03:00 | 3.96 | 3.93
2017-05-22 03:30 | 3.93 | 3.91
2017-05-22 04:00 | 3.98 | 3.96
2017-05-22 04:30 | 4.14 | 4.12
2017-05-22 05:00 | 4.39 | 4.37
2017-05-22 05:30 | 4.89 | 4.88
2017-05-22 06:00 | 5.9 | 5.9
2017-05-22 06:30 | 6.26 | 6.24
2017-05-22 07:00 | 6.65 | 6.64
2017-05-22 07:30 | 7.6 | 7.59
2017-05-22 08:00 | 7.59 | 7.59
2017-05-22 08:30 | 7.04 | 7.04
2017-05-22 09:00 | 6.48 | 6.47
2017-05-22 09:30 | 6.51 | 6.51
2017-05-22 10:00 | 6.23 | 6.22
2017-05-22 10:30 | 5.76 | 5.75
2017-05-22 11:00 | 4.63 | 4.62
2017-05-22 11:30 | 4.06 | 4.05
2017-05-22 12:00 | 3.95 | 3.94
2017-05-22 12:30 | 4.16 | 4.15
2017-05-22 13:00 | 4.3 | 4.28
2017-05-22 13:30 | 4.59 | 4.56
2017-05-22 14:00 | 4.7 | 4.67
2017-05-22 14:30 | 5.01 | 4.99
2017-05-22 15:00 | 5.92 | 5.9
2017-05-22 15:30 | 6.8 | 6.78
2017-05-22 16:00 | 6.9 | 6.88
2017-05-22 16:30 | 7.74 | 7.72
2017-05-22 17:00 | 8.88 | 8.86
2017-05-22 17:30 | 10.33 | 10.31
2017-05-22 18:00 | 11.08 | 11.05
2017-05-22 18:30 | 11.14 | 11.12
2017-05-22 19:00 | 11.12 | 11.09
2017-05-22 19:30 | 10.6 | 10.59
2017-05-22 20:00 | 10.45 | 10.43
2017-05-22 20:30 | 10.54 | 10.53
2017-05-22 21:00 | 10.03 | 10.01
2017-05-22 21:30 | 9.23 | 9.22
2017-05-22 22:00 | 8.31 | 8.3
2017-05-22 22:30 | 7.73 | 7.72
2017-05-22 23:00 | 7.51 | 7.5
2017-05-22 23:30 | 6.6 | 6.59
2017-05-23 | 5.8 | 5.78
2017-05-23 00:30 | 5.06 | 5.04
2017-05-23 01:00 | 4.7 | 4.68
2017-05-23 01:30 | 4.3 | 4.28
2017-05-23 02:00 | 4.13 | 4.11
2017-05-23 02:30 | 3.91 | 3.89
2017-05-23 03:00 | 3.86 | 3.84
2017-05-23 03:30 | 3.96 | 3.94
2017-05-23 04:00 | 4.03 | 4.01
2017-05-23 04:30 | 4.17 | 4.15
2017-05-23 05:00 | 4.5 | 4.48
2017-05-23 05:30 | 5.02 | 5
2017-05-23 06:00 | 5.86 | 5.85
2017-05-23 06:30 | 6.6 | 6.59
2017-05-23 07:00 | 7.23 | 7.22
2017-05-23 07:30 | 7.53 | 7.52
2017-05-23 08:00 | 7.13 | 7.12
2017-05-23 08:30 | 5.97 | 5.96
2017-05-23 09:00 | 5.33 | 5.32
2017-05-23 09:30 | 4.88 | 4.87
2017-05-23 10:00 | 4.54 | 4.52
2017-05-23 10:30 | 4.17 | 4.16
2017-05-23 11:00 | 3.95 | 3.94
2017-05-23 11:30 | 3.88 | 3.87
2017-05-23 12:00 | 4.03 | 4.02
2017-05-23 12:30 | 4.03 | 4.02
2017-05-23 13:00 | 4.2 | 4.18
2017-05-23 13:30 | 4.18 | 4.15
2017-05-23 14:00 | 4.29 | 4.27
2017-05-23 14:30 | 4.42 | 4.4
2017-05-23 15:00 | 4.8 | 4.78
2017-05-23 15:30 | 5.49 | 5.47
2017-05-23 16:00 | 6.48 | 6.47
2017-05-23 16:30 | 7.51 | 7.49
2017-05-23 17:00 | 8.35 | 8.33
2017-05-23 17:30 | 9.75 | 9.73
2017-05-23 18:00 | 10.73 | 10.7
2017-05-23 18:30 | 10.88 | 10.86
2017-05-23 19:00 | 10.86 | 10.84
2017-05-23 19:30 | 10.48 | 10.46
2017-05-23 20:00 | 10.37 | 10.35
2017-05-23 20:30 | 10.41 | 10.4
2017-05-23 21:00 | 9.83 | 9.82
2017-05-23 21:30 | 9.14 | 9.12
2017-05-23 22:00 | 8.2 | 8.19
2017-05-23 22:30 | 7.74 | 7.73
2017-05-23 23:00 | 7.48 | 7.47
2017-05-23 23:30 | 6.73 | 6.71
2017-05-24 | 5.74 | 5.72
2017-05-24 00:30 | 5.01 | 4.99
2017-05-24 01:00 | 4.63 | 4.62
2017-05-24 01:30 | 4.32 | 4.31
2017-05-24 02:00 | 4.13 | 4.11
2017-05-24 02:30 | 3.97 | 3.95
2017-05-24 03:00 | 3.84 | 3.82
2017-05-24 03:30 | 3.88 | 3.86
2017-05-24 04:00 | 3.95 | 3.93
2017-05-24 04:30 | 4.16 | 4.14
2017-05-24 05:00 | 4.44 | 4.41
2017-05-24 05:30 | 4.97 | 4.95
2017-05-24 06:00 | 5.94 | 5.93
2017-05-24 06:30 | 6.68 | 6.68
2017-05-24 07:00 | 7.21 | 7.2
2017-05-24 07:30 | 7.87 | 7.87
2017-05-24 08:00 | 7.7 | 7.69
2017-05-24 08:30 | 7.28 | 7.27
2017-05-24 09:00 | 6.62 | 6.61
2017-05-24 09:30 | 6.29 | 6.28
2017-05-24 10:00 | 6.57 | 6.56
2017-05-24 10:30 | 6.37 | 6.37
2017-05-24 11:00 | 5.33 | 5.32
2017-05-24 11:30 | 4.13 | 4.12
2017-05-24 12:00 | 3.69 | 3.67
2017-05-24 12:30 | 3.55 | 3.53
2017-05-24 13:00 | 3.84 | 3.82
2017-05-24 13:30 | 4.2 | 4.18
2017-05-24 14:00 | 4.22 | 4.2
2017-05-24 14:30 | 4.47 | 4.45
2017-05-24 15:00 | 4.86 | 4.84
2017-05-24 15:30 | 5.47 | 5.45
2017-05-24 16:00 | 6.44 | 6.43
2017-05-24 16:30 | 7.26 | 7.24
2017-05-24 17:00 | 8.31 | 8.3
2017-05-24 17:30 | 9.54 | 9.52
2017-05-24 18:00 | 10.52 | 10.49
2017-05-24 18:30 | 10.87 | 10.84
2017-05-24 19:00 | 10.9 | 10.88
2017-05-24 19:30 | 10.63 | 10.61
2017-05-24 20:00 | 10.61 | 10.6
2017-05-24 20:30 | 10.65 | 10.64
2017-05-24 21:00 | 10.17 | 10.15
2017-05-24 21:30 | 9.45 | 9.44
2017-05-24 22:00 | 8.67 | 8.66
2017-05-24 22:30 | 7.91 | 7.9
2017-05-24 23:00 | 7.62 | 7.61
2017-05-24 23:30 | 6.63 | 6.61
2017-05-25 | 5.64 | 5.63
2017-05-25 00:30 | 5 | 4.98
2017-05-25 01:00 | 4.7 | 4.68
2017-05-25 01:30 | 4.48 | 4.46
2017-05-25 02:00 | 4.22 | 4.2
2017-05-25 02:30 | 4.06 | 4.04
2017-05-25 03:00 | 3.98 | 3.96
2017-05-25 03:30 | 3.88 | 3.86
2017-05-25 04:00 | 4 | 3.98
2017-05-25 04:30 | 4.21 | 4.19
2017-05-25 05:00 | 4.54 | 4.52
2017-05-25 05:30 | 5.14 | 5.13
2017-05-25 06:00 | 5.91 | 5.9
2017-05-25 06:30 | 6.41 | 6.4
2017-05-25 07:00 | 7 | 6.99
2017-05-25 07:30 | 7.3 | 7.3
2017-05-25 08:00 | 6.66 | 6.65
2017-05-25 08:30 | 5.7 | 5.69
2017-05-25 09:00 | 4.94 | 4.93
2017-05-25 09:30 | 4.51 | 4.5
2017-05-25 10:00 | 3.99 | 3.97
2017-05-25 10:30 | 3.95 | 3.94
2017-05-25 11:00 | 3.65 | 3.64
2017-05-25 11:30 | 3.52 | 3.51
2017-05-25 12:00 | 3.43 | 3.41
2017-05-25 12:30 | 3.46 | 3.45
2017-05-25 13:00 | 3.72 | 3.7
2017-05-25 13:30 | 4.05 | 4.04
2017-05-25 14:00 | 4.01 | 4
2017-05-25 14:30 | 3.99 | 3.98
2017-05-25 15:00 | 4.32 | 4.31
2017-05-25 15:30 | 5.2 | 5.18
2017-05-25 16:00 | 6.12 | 6.11
2017-05-25 16:30 | 6.95 | 6.94
2017-05-25 17:00 | 7.95 | 7.94
2017-05-25 17:30 | 9.06 | 9.05
2017-05-25 18:00 | 9.84 | 9.83
2017-05-25 18:30 | 9.99 | 9.97
2017-05-25 19:00 | 10.19 | 10.18
2017-05-25 19:30 | 9.99 | 9.98
2017-05-25 20:00 | 9.96 | 9.95
2017-05-25 20:30 | 10.16 | 10.14
2017-05-25 21:00 | 9.73 | 9.71
2017-05-25 21:30 | 8.99 | 8.98
2017-05-25 22:00 | 8.32 | 8.31
2017-05-25 22:30 | 7.9 | 7.89
2017-05-25 23:00 | 7.62 | 7.61
2017-05-25 23:30 | 6.74 | 6.73
2017-05-26 | 5.86 | 5.85
2017-05-26 00:30 | 5.08 | 5.06
2017-05-26 01:00 | 4.62 | 4.61
2017-05-26 01:30 | 4.37 | 4.36
2017-05-26 02:00 | 4.09 | 4.08
2017-05-26 02:30 | 3.94 | 3.92
2017-05-26 03:00 | 3.85 | 3.82
2017-05-26 03:30 | 3.94 | 3.92
2017-05-26 04:00 | 3.91 | 3.89
2017-05-26 04:30 | 4.15 | 4.13
2017-05-26 05:00 | 4.47 | 4.46
2017-05-26 05:30 | 4.97 | 4.96
2017-05-26 06:00 | 5.47 | 5.45
2017-05-26 06:30 | 5.98 | 5.96
2017-05-26 07:00 | 6.56 | 6.54
2017-05-26 07:30 | 6.87 | 6.86
2017-05-26 08:00 | 6.34 | 6.32
2017-05-26 08:30 | 5.35 | 5.33
2017-05-26 09:00 | 5.42 | 5.4
2017-05-26 09:30 | 5.12 | 5.1
2017-05-26 10:00 | 3.84 | 3.82
2017-05-26 10:30 | 3.42 | 3.39
2017-05-26 11:00 | 3.21 | 3.18
2017-05-26 11:30 | 3.05 | 3.02
2017-05-26 12:00 | 3.16 | 3.14
2017-05-26 12:30 | 3.21 | 3.18
2017-05-26 13:00 | 3.22 | 3.2
2017-05-26 13:30 | 3.41 | 3.39
2017-05-26 14:00 | 3.93 | 3.9
2017-05-26 14:30 | 4.02 | 4.01
2017-05-26 15:00 | 4.49 | 4.48
2017-05-26 15:30 | 5.06 | 5.05
2017-05-26 16:00 | 6.11 | 6.09
2017-05-26 16:30 | 7.01 | 6.99
2017-05-26 17:00 | 7.71 | 7.69
2017-05-26 17:30 | 8.56 | 8.54
2017-05-26 18:00 | 9.4 | 9.38
2017-05-26 18:30 | 9.67 | 9.66
2017-05-26 19:00 | 9.72 | 9.71
2017-05-26 19:30 | 9.47 | 9.46
2017-05-26 20:00 | 9.46 | 9.45
2017-05-26 20:30 | 9.46 | 9.45
2017-05-26 21:00 | 9.17 | 9.16
2017-05-26 21:30 | 8.69 | 8.68
2017-05-26 22:00 | 8 | 7.98
2017-05-26 22:30 | 7.72 | 7.71
2017-05-26 23:00 | 7.63 | 7.61
2017-05-26 23:30 | 6.86 | 6.85
2017-05-27 | 6.03 | 6.02
2017-05-27 00:30 | 5.31 | 5.29
2017-05-27 01:00 | 5.01 | 4.99
2017-05-27 01:30 | 4.61 | 4.59
2017-05-27 02:00 | 4.37 | 4.35
2017-05-27 02:30 | 4.2 | 4.18
2017-05-27 03:00 | 4.04 | 4.02
2017-05-27 03:30 | 4.01 | 3.99
2017-05-27 04:00 | 4.03 | 4.01
2017-05-27 04:30 | 4.03 | 4
2017-05-27 05:00 | 4.16 | 4.14
2017-05-27 05:30 | 4.37 | 4.34
2017-05-27 06:00 | 4.55 | 4.53
2017-05-27 06:30 | 4.62 | 4.59
2017-05-27 07:00 | 5.12 | 5.09
2017-05-27 07:30 | 5.48 | 5.44
2017-05-27 08:00 | 5.6 | 5.57
2017-05-27 08:30 | 5.58 | 5.56
2017-05-27 09:00 | 5.44 | 5.42
2017-05-27 09:30 | 5.24 | 5.21
2017-05-27 10:00 | 4.85 | 4.83
2017-05-27 10:30 | 4.48 | 4.46
2017-05-27 11:00 | 4.26 | 4.23
2017-05-27 11:30 | 4.11 | 4.07
2017-05-27 12:00 | 3.99 | 3.95
2017-05-27 12:30 | 4.47 | 4.43
2017-05-27 13:00 | 4.32 | 4.28
2017-05-27 13:30 | 4.6 | 4.57
2017-05-27 14:00 | 5.95 | 5.93
2017-05-27 14:30 | 5.56 | 5.53
2017-05-27 15:00 | 5.05 | 5.03
2017-05-27 15:30 | 5.82 | 5.8
2017-05-27 16:00 | 6.84 | 6.83
2017-05-27 16:30 | 7.36 | 7.34
2017-05-27 17:00 | 8.07 | 8.05
2017-05-27 17:30 | 9.05 | 9.03
2017-05-27 18:00 | 9.69 | 9.67
2017-05-27 18:30 | 9.66 | 9.64
2017-05-27 19:00 | 9.5 | 9.49
2017-05-27 19:30 | 9.02 | 9.01
2017-05-27 20:00 | 8.91 | 8.89
2017-05-27 20:30 | 8.86 | 8.84
2017-05-27 21:00 | 8.63 | 8.62
2017-05-27 21:30 | 8.14 | 8.13
2017-05-27 22:00 | 7.73 | 7.72
2017-05-27 22:30 | 7.52 | 7.51
2017-05-27 23:00 | 7.55 | 7.53
2017-05-27 23:30 | 6.8 | 6.78
2017-05-28 | 5.93 | 5.92
2017-05-28 00:30 | 5.38 | 5.37
2017-05-28 01:00 | 5.03 | 5.01
2017-05-28 01:30 | 4.62 | 4.6
2017-05-28 02:00 | 4.38 | 4.36
2017-05-28 02:30 | 4.15 | 4.13
2017-05-28 03:00 | 4.11 | 4.09
2017-05-28 03:30 | 4.1 | 4.08
2017-05-28 04:00 | 4.06 | 4.04
2017-05-28 04:30 | 4.04 | 4.02
2017-05-28 05:00 | 4.05 | 4.03
2017-05-28 05:30 | 4.25 | 4.22
2017-05-28 06:00 | 4.35 | 4.33
2017-05-28 06:30 | 4.5 | 4.47
2017-05-28 07:00 | 4.65 | 4.61
2017-05-28 07:30 | 5.25 | 5.21
2017-05-28 08:00 | 5.75 | 5.72
2017-05-28 08:30 | 6.27 | 6.25
2017-05-28 09:00 | 6.74 | 6.72
2017-05-28 09:30 | 6.47 | 6.45
2017-05-28 10:00 | 6.49 | 6.47
2017-05-28 10:30 | 5.63 | 5.61
2017-05-28 11:00 | 4.54 | 4.51
2017-05-28 11:30 | 5.11 | 5.08
2017-05-28 12:00 | 5 | 4.98
2017-05-28 12:30 | 4.39 | 4.35
2017-05-28 13:00 | 4.69 | 4.66
2017-05-28 13:30 | 4.7 | 4.67
2017-05-28 14:00 | 5.19 | 5.16
2017-05-28 14:30 | 5.62 | 5.59
2017-05-28 15:00 | 5.52 | 5.5
2017-05-28 15:30 | 6.48 | 6.47
2017-05-28 16:00 | 7.61 | 7.59
2017-05-28 16:30 | 8.03 | 8.02
2017-05-28 17:00 | 8.93 | 8.92
2017-05-28 17:30 | 10.08 | 10.07
2017-05-28 18:00 | 10.88 | 10.86
2017-05-28 18:30 | 10.63 | 10.62
2017-05-28 19:00 | 10.42 | 10.41
2017-05-28 19:30 | 10.13 | 10.11
2017-05-28 20:00 | 9.93 | 9.91
2017-05-28 20:30 | 9.77 | 9.76
2017-05-28 21:00 | 9.12 | 9.11
2017-05-28 21:30 | 8.45 | 8.44
2017-05-28 22:00 | 7.92 | 7.91
2017-05-28 22:30 | 7.49 | 7.47
2017-05-28 23:00 | 7.33 | 7.32
2017-05-28 23:30 | 6.54 | 6.52
2017-05-29 | 5.71 | 5.7
2017-05-29 00:30 | 5 | 4.98
2017-05-29 01:00 | 4.66 | 4.64
2017-05-29 01:30 | 4.46 | 4.44
2017-05-29 02:00 | 4.13 | 4.1
2017-05-29 02:30 | 3.96 | 3.94
2017-05-29 03:00 | 3.79 | 3.76
2017-05-29 03:30 | 3.78 | 3.76
2017-05-29 04:00 | 3.98 | 3.96
2017-05-29 04:30 | 4.13 | 4.11
2017-05-29 05:00 | 4.47 | 4.45
2017-05-29 05:30 | 5.14 | 5.13
2017-05-29 06:00 | 5.84 | 5.83
2017-05-29 06:30 | 6.49 | 6.48
2017-05-29 07:00 | 7.18 | 7.17
2017-05-29 07:30 | 7.57 | 7.57
2017-05-29 08:00 | 7.14 | 7.13
2017-05-29 08:30 | 6.24 | 6.24
2017-05-29 09:00 | 5.32 | 5.31
2017-05-29 09:30 | 4.88 | 4.86
2017-05-29 10:00 | 4.37 | 4.36
2017-05-29 10:30 | 4.17 | 4.16
2017-05-29 11:00 | 3.85 | 3.83
2017-05-29 11:30 | 3.73 | 3.72
2017-05-29 12:00 | 3.72 | 3.71
2017-05-29 12:30 | 3.75 | 3.74
2017-05-29 13:00 | 3.88 | 3.86
2017-05-29 13:30 | 3.81 | 3.78
2017-05-29 14:00 | 4.01 | 3.99
2017-05-29 14:30 | 4.39 | 4.38
2017-05-29 15:00 | 4.78 | 4.77
2017-05-29 15:30 | 5.27 | 5.26
2017-05-29 16:00 | 6.28 | 6.27
2017-05-29 16:30 | 7.12 | 7.11
2017-05-29 17:00 | 8.21 | 8.2
2017-05-29 17:30 | 9.59 | 9.57
2017-05-29 18:00 | 10.65 | 10.64
2017-05-29 18:30 | 10.64 | 10.62
2017-05-29 19:00 | 10.81 | 10.8
2017-05-29 19:30 | 10.44 | 10.43
2017-05-29 20:00 | 10.3 | 10.28
2017-05-29 20:30 | 10.1 | 10.08
2017-05-29 21:00 | 9.68 | 9.67
2017-05-29 21:30 | 8.94 | 8.92
2017-05-29 22:00 | 8.33 | 8.31
2017-05-29 22:30 | 7.89 | 7.88
2017-05-29 23:00 | 7.43 | 7.42
2017-05-29 23:30 | 6.57 | 6.56
2017-05-30 | 5.7 | 5.69
2017-05-30 00:30 | 4.98 | 4.96
2017-05-30 01:00 | 4.68 | 4.67
2017-05-30 01:30 | 4.38 | 4.37
2017-05-30 02:00 | 4.08 | 4.06
2017-05-30 02:30 | 3.98 | 3.96
2017-05-30 03:00 | 3.95 | 3.93
2017-05-30 03:30 | 3.99 | 3.97
2017-05-30 04:00 | 4.09 | 4.06
2017-05-30 04:30 | 4.29 | 4.27
2017-05-30 05:00 | 4.64 | 4.62
2017-05-30 05:30 | 5.23 | 5.22
2017-05-30 06:00 | 6.05 | 6.05
2017-05-30 06:30 | 6.94 | 6.93
2017-05-30 07:00 | 7.68 | 7.68
2017-05-30 07:30 | 8.3 | 8.29
2017-05-30 08:00 | 7.34 | 7.33
2017-05-30 08:30 | 6.52 | 6.52
2017-05-30 09:00 | 5.41 | 5.4
2017-05-30 09:30 | 5.12 | 5.11
2017-05-30 10:00 | 4.75 | 4.74
2017-05-30 10:30 | 4.02 | 4.01
2017-05-30 11:00 | 3.73 | 3.72
2017-05-30 11:30 | 3.79 | 3.78
2017-05-30 12:00 | 3.79 | 3.78
2017-05-30 12:30 | 3.42 | 3.41
2017-05-30 13:00 | 3.53 | 3.51
2017-05-30 13:30 | 3.46 | 3.44
2017-05-30 14:00 | 3.84 | 3.82
2017-05-30 14:30 | 4.14 | 4.12
2017-05-30 15:00 | 4.47 | 4.46
2017-05-30 15:30 | 5.07 | 5.06
2017-05-30 16:00 | 6.05 | 6.04
2017-05-30 16:30 | 6.82 | 6.81
2017-05-30 17:00 | 7.9 | 7.88
2017-05-30 17:30 | 9.62 | 9.61
2017-05-30 18:00 | 10.54 | 10.53
2017-05-30 18:30 | 10.71 | 10.69
2017-05-30 19:00 | 10.94 | 10.93
2017-05-30 19:30 | 10.66 | 10.65
2017-05-30 20:00 | 10.55 | 10.54
2017-05-30 20:30 | 10.57 | 10.56
2017-05-30 21:00 | 9.99 | 9.98
2017-05-30 21:30 | 9.25 | 9.24
2017-05-30 22:00 | 8.43 | 8.42
2017-05-30 22:30 | 7.95 | 7.94
2017-05-30 23:00 | 7.76 | 7.75
2017-05-30 23:30 | 6.82 | 6.81
2017-05-31 | 6.01 | 6
2017-05-31 00:30 | 5.34 | 5.33
2017-05-31 01:00 | 4.92 | 4.9
2017-05-31 01:30 | 4.68 | 4.66
2017-05-31 02:00 | 4.39 | 4.37
2017-05-31 02:30 | 4.2 | 4.19
2017-05-31 03:00 | 4.14 | 4.12
2017-05-31 03:30 | 4.23 | 4.21
2017-05-31 04:00 | 4.26 | 4.24
2017-05-31 04:30 | 4.64 | 4.62
2017-05-31 05:00 | 4.96 | 4.95
2017-05-31 05:30 | 5.76 | 5.75
2017-05-31 06:00 | 6.85 | 6.84
2017-05-31 06:30 | 7.57 | 7.57
2017-05-31 07:00 | 8.33 | 8.32
2017-05-31 07:30 | 8.87 | 8.87
2017-05-31 08:00 | 8.26 | 8.26
2017-05-31 08:30 | 6.97 | 6.97
2017-05-31 09:00 | 6.1 | 6.1
2017-05-31 09:30 | 5.33 | 5.33
2017-05-31 10:00 | 4.81 | 4.8
2017-05-31 10:30 | 4.31 | 4.31
2017-05-31 11:00 | 3.79 | 3.79
2017-05-31 11:30 | 3.6 | 3.6
2017-05-31 12:00 | 3.48 | 3.48
2017-05-31 12:30 | 3.59 | 3.59
2017-05-31 13:00 | 3.68 | 3.68
2017-05-31 13:30 | 3.4 | 3.39
2017-05-31 14:00 | 3.5 | 3.49
2017-05-31 14:30 | 4.25 | 4.24
2017-05-31 15:00 | 4.51 | 4.5
2017-05-31 15:30 | 4.82 | 4.81
2017-05-31 16:00 | 5.73 | 5.72
2017-05-31 16:30 | 6.81 | 6.79
2017-05-31 17:00 | 8.16 | 8.15
2017-05-31 17:30 | 9.81 | 9.8
2017-05-31 18:00 | 10.94 | 10.93
2017-05-31 18:30 | 11.16 | 11.14
2017-05-31 19:00 | 11.53 | 11.51
2017-05-31 19:30 | 11.26 | 11.25
2017-05-31 20:00 | 11.26 | 11.25
2017-05-31 20:30 | 11.37 | 11.36
2017-05-31 21:00 | 10.72 | 10.71
2017-05-31 21:30 | 10.04 | 10.03
2017-05-31 22:00 | 9.31 | 9.3
2017-05-31 22:30 | 8.87 | 8.86
2017-05-31 23:00 | 8.56 | 8.55
2017-05-31 23:30 | 7.48 | 7.47
2017-06-01 | 6.53 | 6.52
2017-06-01 00:30 | 5.78 | 5.77
2017-06-01 01:00 | 5.43 | 5.42
2017-06-01 01:30 | 5.02 | 5.01
2017-06-01 02:00 | 4.77 | 4.76
2017-06-01 02:30 | 4.54 | 4.53
2017-06-01 03:00 | 4.49 | 4.47
2017-06-01 03:30 | 4.6 | 4.59
2017-06-01 04:00 | 4.69 | 4.67
2017-06-01 04:30 | 4.94 | 4.93
2017-06-01 05:00 | 5.34 | 5.33
2017-06-01 05:30 | 6.11 | 6.09
2017-06-01 06:00 | 7.48 | 7.47
2017-06-01 06:30 | 8.33 | 8.32
2017-06-01 07:00 | 9.25 | 9.24
2017-06-01 07:30 | 9.53 | 9.52
2017-06-01 08:00 | 9.08 | 9.08
2017-06-01 08:30 | 7.56 | 7.55
2017-06-01 09:00 | 6.44 | 6.43
2017-06-01 09:30 | 5.58 | 5.57
2017-06-01 10:00 | 4.89 | 4.88
2017-06-01 10:30 | 4.31 | 4.3
2017-06-01 11:00 | 4.06 | 4.05
2017-06-01 11:30 | 3.79 | 3.78
2017-06-01 12:00 | 3.59 | 3.58
2017-06-01 12:30 | 3.6 | 3.59
2017-06-01 13:00 | 3.66 | 3.65
2017-06-01 13:30 | 3.44 | 3.43
2017-06-01 14:00 | 3.52 | 3.51
2017-06-01 14:30 | 3.81 | 3.8
2017-06-01 15:00 | 4.28 | 4.27
2017-06-01 15:30 | 5.08 | 5.07
2017-06-01 16:00 | 6.04 | 6.03
2017-06-01 16:30 | 7.05 | 7.04
2017-06-01 17:00 | 8.36 | 8.35
2017-06-01 17:30 | 9.93 | 9.92
2017-06-01 18:00 | 10.99 | 10.97
2017-06-01 18:30 | 11.15 | 11.14
2017-06-01 19:00 | 11.56 | 11.55
2017-06-01 19:30 | 11.45 | 11.44
2017-06-01 20:00 | 11.55 | 11.53
2017-06-01 20:30 | 11.65 | 11.64
2017-06-01 21:00 | 11.22 | 11.21
2017-06-01 21:30 | 10.33 | 10.32
2017-06-01 22:00 | 9.6 | 9.58
2017-06-01 22:30 | 9.06 | 9.05
2017-06-01 23:00 | 8.68 | 8.66
2017-06-01 23:30 | 7.57 | 7.56
2017-06-02 | 6.6 | 6.59
2017-06-02 00:30 | 5.97 | 5.96
2017-06-02 01:00 | 5.54 | 5.53
2017-06-02 01:30 | 5.24 | 5.23
2017-06-02 02:00 | 4.83 | 4.82
2017-06-02 02:30 | 4.79 | 4.77
2017-06-02 03:00 | 4.7 | 4.68
2017-06-02 03:30 | 4.67 | 4.65
2017-06-02 04:00 | 4.75 | 4.73
2017-06-02 04:30 | 5.14 | 5.13
2017-06-02 05:00 | 5.67 | 5.65
2017-06-02 05:30 | 6.35 | 6.34
2017-06-02 06:00 | 7.08 | 7.06
2017-06-02 06:30 | 7.73 | 7.71
2017-06-02 07:00 | 8.7 | 8.69
2017-06-02 07:30 | 9.08 | 9.06
2017-06-02 08:00 | 8.37 | 8.35
2017-06-02 08:30 | 6.94 | 6.92
2017-06-02 09:00 | 5.78 | 5.76
2017-06-02 09:30 | 5.01 | 4.99
2017-06-02 10:00 | 4.39 | 4.37
2017-06-02 10:30 | 3.82 | 3.79
2017-06-02 11:00 | 3.49 | 3.46
2017-06-02 11:30 | 3.25 | 3.21
2017-06-02 12:00 | 3.09 | 3.06
2017-06-02 12:30 | 3.04 | 3.01
2017-06-02 13:00 | 2.96 | 2.94
2017-06-02 13:30 | 3.16 | 3.14
2017-06-02 14:00 | 3.59 | 3.57
2017-06-02 14:30 | 3.97 | 3.95
2017-06-02 15:00 | 4.35 | 4.34
2017-06-02 15:30 | 4.97 | 4.95
2017-06-02 16:00 | 5.98 | 5.97
2017-06-02 16:30 | 6.98 | 6.96
2017-06-02 17:00 | 8.1 | 8.09
2017-06-02 17:30 | 9.46 | 9.45
2017-06-02 18:00 | 10.35 | 10.34
2017-06-02 18:30 | 10.5 | 10.48
2017-06-02 19:00 | 10.67 | 10.65
2017-06-02 19:30 | 10.64 | 10.62
2017-06-02 20:00 | 10.79 | 10.78
2017-06-02 20:30 | 10.93 | 10.92
2017-06-02 21:00 | 10.67 | 10.66
2017-06-02 21:30 | 10.11 | 10.11
2017-06-02 22:00 | 9.42 | 9.41
2017-06-02 22:30 | 9.05 | 9.04
2017-06-02 23:00 | 8.8 | 8.79
2017-06-02 23:30 | 7.98 | 7.97
2017-06-03 | 7.02 | 7.01
2017-06-03 00:30 | 6.21 | 6.2
2017-06-03 01:00 | 5.87 | 5.86
2017-06-03 01:30 | 5.5 | 5.49
2017-06-03 02:00 | 5.1 | 5.09
2017-06-03 02:30 | 4.8 | 4.79
2017-06-03 03:00 | 4.67 | 4.65
2017-06-03 03:30 | 4.68 | 4.66
2017-06-03 04:00 | 4.68 | 4.66
2017-06-03 04:30 | 4.92 | 4.9
2017-06-03 05:00 | 5 | 4.99
2017-06-03 05:30 | 5.37 | 5.35
2017-06-03 06:00 | 5.61 | 5.6
2017-06-03 06:30 | 5.88 | 5.86
2017-06-03 07:00 | 6.42 | 6.41
2017-06-03 07:30 | 7.17 | 7.16
2017-06-03 08:00 | 7.54 | 7.53
2017-06-03 08:30 | 7.37 | 7.36
2017-06-03 09:00 | 6.91 | 6.89
2017-06-03 09:30 | 6.37 | 6.35
2017-06-03 10:00 | 5.77 | 5.75
2017-06-03 10:30 | 5.18 | 5.15
2017-06-03 11:00 | 4.52 | 4.49
2017-06-03 11:30 | 4.38 | 4.35
2017-06-03 12:00 | 4.41 | 4.38
2017-06-03 12:30 | 4.14 | 4.11
2017-06-03 13:00 | 4.21 | 4.17
2017-06-03 13:30 | 4.67 | 4.65
2017-06-03 14:00 | 4.62 | 4.6
2017-06-03 14:30 | 4.87 | 4.85
2017-06-03 15:00 | 5.2 | 5.19
2017-06-03 15:30 | 5.76 | 5.74
2017-06-03 16:00 | 6.47 | 6.45
2017-06-03 16:30 | 7.35 | 7.33
2017-06-03 17:00 | 8.53 | 8.51
2017-06-03 17:30 | 9.62 | 9.61
2017-06-03 18:00 | 10.17 | 10.15
2017-06-03 18:30 | 10.18 | 10.16
2017-06-03 19:00 | 10.21 | 10.19
2017-06-03 19:30 | 9.89 | 9.88
2017-06-03 20:00 | 10.08 | 10.07
2017-06-03 20:30 | 10.15 | 10.14
2017-06-03 21:00 | 9.76 | 9.75
2017-06-03 21:30 | 9.29 | 9.28
2017-06-03 22:00 | 8.97 | 8.96
2017-06-03 22:30 | 8.68 | 8.67
2017-06-03 23:00 | 8.51 | 8.5
2017-06-03 23:30 | 7.82 | 7.8
2017-06-04 | 6.97 | 6.96
2017-06-04 00:30 | 6.18 | 6.17
2017-06-04 01:00 | 5.7 | 5.68
2017-06-04 01:30 | 5.28 | 5.26
2017-06-04 02:00 | 4.94 | 4.92
2017-06-04 02:30 | 4.78 | 4.77
2017-06-04 03:00 | 4.76 | 4.75
2017-06-04 03:30 | 4.61 | 4.59
2017-06-04 04:00 | 4.56 | 4.54
2017-06-04 04:30 | 4.61 | 4.59
2017-06-04 05:00 | 4.72 | 4.7
2017-06-04 05:30 | 4.86 | 4.85
2017-06-04 06:00 | 5.08 | 5.06
2017-06-04 06:30 | 5.31 | 5.29
2017-06-04 07:00 | 5.78 | 5.76
2017-06-04 07:30 | 6.27 | 6.25
2017-06-04 08:00 | 6.57 | 6.55
2017-06-04 08:30 | 6.76 | 6.74
2017-06-04 09:00 | 6.44 | 6.43
2017-06-04 09:30 | 6.32 | 6.3
2017-06-04 10:00 | 5.73 | 5.71
2017-06-04 10:30 | 5.23 | 5.21
2017-06-04 11:00 | 4.86 | 4.84
2017-06-04 11:30 | 4.6 | 4.57
2017-06-04 12:00 | 4.52 | 4.5
2017-06-04 12:30 | 4.68 | 4.65
2017-06-04 13:00 | 4.7 | 4.68
2017-06-04 13:30 | 5.15 | 5.12
2017-06-04 14:00 | 5.46 | 5.44
2017-06-04 14:30 | 5.38 | 5.36
2017-06-04 15:00 | 6.18 | 6.17
2017-06-04 15:30 | 6.89 | 6.87
2017-06-04 16:00 | 7.25 | 7.24
2017-06-04 16:30 | 8.23 | 8.22
2017-06-04 17:00 | 9.37 | 9.35
2017-06-04 17:30 | 10.77 | 10.76
2017-06-04 18:00 | 11.71 | 11.7
2017-06-04 18:30 | 11.57 | 11.56
2017-06-04 19:00 | 11.46 | 11.44
2017-06-04 19:30 | 11 | 10.99
2017-06-04 20:00 | 10.87 | 10.86
2017-06-04 20:30 | 10.87 | 10.86
2017-06-04 21:00 | 10.46 | 10.45
2017-06-04 21:30 | 9.82 | 9.8
2017-06-04 22:00 | 9.2 | 9.18
2017-06-04 22:30 | 8.48 | 8.46
2017-06-04 23:00 | 8.25 | 8.23
2017-06-04 23:30 | 7.32 | 7.31
2017-06-05 | 6.32 | 6.31
2017-06-05 00:30 | 5.73 | 5.72
2017-06-05 01:00 | 5.31 | 5.3
2017-06-05 01:30 | 4.95 | 4.94
2017-06-05 02:00 | 4.61 | 4.59
2017-06-05 02:30 | 4.49 | 4.47
2017-06-05 03:00 | 4.43 | 4.41
2017-06-05 03:30 | 4.49 | 4.48
2017-06-05 04:00 | 4.55 | 4.54
2017-06-05 04:30 | 4.9 | 4.89
2017-06-05 05:00 | 5.32 | 5.3
2017-06-05 05:30 | 6.13 | 6.12
2017-06-05 06:00 | 6.92 | 6.91
2017-06-05 06:30 | 7.88 | 7.87
2017-06-05 07:00 | 8.63 | 8.62
2017-06-05 07:30 | 9.37 | 9.36
2017-06-05 08:00 | 8.75 | 8.74
2017-06-05 08:30 | 7.6 | 7.59
2017-06-05 09:00 | 6.33 | 6.33
2017-06-05 09:30 | 5.79 | 5.78
2017-06-05 10:00 | 5.12 | 5.11
2017-06-05 10:30 | 4.53 | 4.52
2017-06-05 11:00 | 4.14 | 4.13
2017-06-05 11:30 | 3.9 | 3.89
2017-06-05 12:00 | 3.77 | 3.76
2017-06-05 12:30 | 3.78 | 3.77
2017-06-05 13:00 | 3.71 | 3.7
2017-06-05 13:30 | 3.9 | 3.89
2017-06-05 14:00 | 4.41 | 4.4
2017-06-05 14:30 | 5.11 | 5.11
2017-06-05 15:00 | 5.05 | 5.04
2017-06-05 15:30 | 5.67 | 5.67
2017-06-05 16:00 | 6.75 | 6.75
2017-06-05 16:30 | 7.83 | 7.82
2017-06-05 17:00 | 9.56 | 9.55
2017-06-05 17:30 | 11.44 | 11.43
2017-06-05 18:00 | 12.31 | 12.28
2017-06-05 18:30 | 12.46 | 12.43
2017-06-05 19:00 | 12.53 | 12.5
2017-06-05 19:30 | 12.14 | 12.12
2017-06-05 20:00 | 12.01 | 11.99
2017-06-05 20:30 | 12.02 | 12.01
2017-06-05 21:00 | 11.4 | 11.39
2017-06-05 21:30 | 10.81 | 10.8
2017-06-05 22:00 | 9.76 | 9.75
2017-06-05 22:30 | 8.78 | 8.77
2017-06-05 23:00 | 8.29 | 8.28
2017-06-05 23:30 | 7.3 | 7.28
2017-06-06 | 6.36 | 6.34
2017-06-06 00:30 | 5.65 | 5.64
2017-06-06 01:00 | 5.25 | 5.24
2017-06-06 01:30 | 4.85 | 4.84
2017-06-06 02:00 | 4.57 | 4.55
2017-06-06 02:30 | 4.37 | 4.35
2017-06-06 03:00 | 4.37 | 4.35
2017-06-06 03:30 | 4.42 | 4.4
2017-06-06 04:00 | 4.51 | 4.49
2017-06-06 04:30 | 4.81 | 4.8
2017-06-06 05:00 | 5.21 | 5.19
2017-06-06 05:30 | 6.11 | 6.1
2017-06-06 06:00 | 7.14 | 7.13
2017-06-06 06:30 | 7.84 | 7.83
2017-06-06 07:00 | 8.8 | 8.8
2017-06-06 07:30 | 9.4 | 9.39
2017-06-06 08:00 | 8.65 | 8.65
2017-06-06 08:30 | 7.33 | 7.33
2017-06-06 09:00 | 6.2 | 6.19
2017-06-06 09:30 | 6.04 | 6.03
2017-06-06 10:00 | 4.94 | 4.93
2017-06-06 10:30 | 4.54 | 4.54
2017-06-06 11:00 | 4.41 | 4.4
2017-06-06 11:30 | 3.98 | 3.97
2017-06-06 12:00 | 3.7 | 3.69
2017-06-06 12:30 | 3.77 | 3.76
2017-06-06 13:00 | 3.57 | 3.56
2017-06-06 13:30 | 3.91 | 3.9
2017-06-06 14:00 | 4.27 | 4.26
2017-06-06 14:30 | 4.92 | 4.91
2017-06-06 15:00 | 4.97 | 4.97
2017-06-06 15:30 | 5.58 | 5.58
2017-06-06 16:00 | 6.63 | 6.62
2017-06-06 16:30 | 7.82 | 7.82
2017-06-06 17:00 | 9.39 | 9.39
2017-06-06 17:30 | 11.3 | 11.28
2017-06-06 18:00 | 12.5 | 12.47
2017-06-06 18:30 | 12.86 | 12.83
2017-06-06 19:00 | 13.23 | 13.2
2017-06-06 19:30 | 13.07 | 13.04
2017-06-06 20:00 | 13.13 | 13.11
2017-06-06 20:30 | 13.22 | 13.21
2017-06-06 21:00 | 12.59 | 12.57
2017-06-06 21:30 | 11.75 | 11.74
2017-06-06 22:00 | 10.58 | 10.57
2017-06-06 22:30 | 9.95 | 9.94
2017-06-06 23:00 | 9.09 | 9.08
2017-06-06 23:30 | 8.04 | 8.03
2017-06-07 | 6.97 | 6.95
2017-06-07 00:30 | 6.04 | 6.03
2017-06-07 01:00 | 5.73 | 5.72
2017-06-07 01:30 | 5.32 | 5.31
2017-06-07 02:00 | 5.11 | 5.09
2017-06-07 02:30 | 4.91 | 4.89
2017-06-07 03:00 | 4.79 | 4.77
2017-06-07 03:30 | 4.82 | 4.81
2017-06-07 04:00 | 4.97 | 4.95
2017-06-07 04:30 | 5.3 | 5.28
2017-06-07 05:00 | 5.94 | 5.93
2017-06-07 05:30 | 6.73 | 6.72
2017-06-07 06:00 | 8 | 7.99
2017-06-07 06:30 | 9.19 | 9.18
2017-06-07 07:00 | 10.14 | 10.14
2017-06-07 07:30 | 10.63 | 10.63
2017-06-07 08:00 | 9.97 | 9.96
2017-06-07 08:30 | 8.32 | 8.31
2017-06-07 09:00 | 6.91 | 6.91
2017-06-07 09:30 | 5.91 | 5.89
2017-06-07 10:00 | 5.06 | 5.05
2017-06-07 10:30 | 4.7 | 4.69
2017-06-07 11:00 | 4.42 | 4.42
2017-06-07 11:30 | 4.18 | 4.17
2017-06-07 12:00 | 3.9 | 3.89
2017-06-07 12:30 | 3.78 | 3.77
2017-06-07 13:00 | 3.86 | 3.86
2017-06-07 13:30 | 3.95 | 3.95
2017-06-07 14:00 | 4.06 | 4.05
2017-06-07 14:30 | 4.42 | 4.41
2017-06-07 15:00 | 5.22 | 5.22
2017-06-07 15:30 | 5.98 | 5.96
2017-06-07 16:00 | 7.19 | 7.18
2017-06-07 16:30 | 8.62 | 8.61
2017-06-07 17:00 | 9.41 | 9.41
2017-06-07 17:30 | 11.48 | 11.47
2017-06-07 18:00 | 12.52 | 12.49
2017-06-07 18:30 | 13.08 | 13.05
2017-06-07 19:00 | 13.61 | 13.58
2017-06-07 19:30 | 13.59 | 13.56
2017-06-07 20:00 | 13.57 | 13.54
2017-06-07 20:30 | 13.67 | 13.65
2017-06-07 21:00 | 13.1 | 13.08
2017-06-07 21:30 | 12.14 | 12.13
2017-06-07 22:00 | 11.11 | 11.1
2017-06-07 22:30 | 9.87 | 9.86
2017-06-07 23:00 | 9.09 | 9.08
2017-06-07 23:30 | 8.09 | 8.07
2017-06-08 | 6.99 | 6.98
2017-06-08 00:30 | 6.21 | 6.2
2017-06-08 01:00 | 5.78 | 5.77
2017-06-08 01:30 | 5.46 | 5.45
2017-06-08 02:00 | 5.17 | 5.16
2017-06-08 02:30 | 5.04 | 5.03
2017-06-08 03:00 | 4.9 | 4.89
2017-06-08 03:30 | 4.99 | 4.98
2017-06-08 04:00 | 5.07 | 5.06
2017-06-08 04:30 | 5.38 | 5.37
2017-06-08 05:00 | 5.98 | 5.97
2017-06-08 05:30 | 7.01 | 7
2017-06-08 06:00 | 8.33 | 8.32
2017-06-08 06:30 | 9.19 | 9.18
2017-06-08 07:00 | 10.44 | 10.43
2017-06-08 07:30 | 10.96 | 10.96
2017-06-08 08:00 | 10.14 | 10.14
2017-06-08 08:30 | 8.57 | 8.57
2017-06-08 09:00 | 7.33 | 7.32
2017-06-08 09:30 | 6.41 | 6.4
2017-06-08 10:00 | 5.7 | 5.69
2017-06-08 10:30 | 5.03 | 5.02
2017-06-08 11:00 | 4.49 | 4.47
2017-06-08 11:30 | 4.2 | 4.18
2017-06-08 12:00 | 4.12 | 4.1
2017-06-08 12:30 | 4.09 | 4.08
2017-06-08 13:00 | 4.55 | 4.54
2017-06-08 13:30 | 5.22 | 5.22
2017-06-08 14:00 | 5.58 | 5.57
2017-06-08 14:30 | 5.91 | 5.91
2017-06-08 15:00 | 6.27 | 6.27
2017-06-08 15:30 | 6.85 | 6.84
2017-06-08 16:00 | 7.77 | 7.77
2017-06-08 16:30 | 8.01 | 8
2017-06-08 17:00 | 9.22 | 9.21
2017-06-08 17:30 | 10.97 | 10.96
2017-06-08 18:00 | 11.97 | 11.94
2017-06-08 18:30 | 12.47 | 12.45
2017-06-08 19:00 | 12.92 | 12.89
2017-06-08 19:30 | 12.88 | 12.86
2017-06-08 20:00 | 13.12 | 13.1
2017-06-08 20:30 | 13.33 | 13.31
2017-06-08 21:00 | 12.9 | 12.88
2017-06-08 21:30 | 12.1 | 12.08
2017-06-08 22:00 | 11.3 | 11.29
2017-06-08 22:30 | 10.26 | 10.25
2017-06-08 23:00 | 9.59 | 9.58
2017-06-08 23:30 | 8.31 | 8.3
2017-06-09 | 7.26 | 7.25
2017-06-09 00:30 | 6.43 | 6.42
2017-06-09 01:00 | 5.95 | 5.94
2017-06-09 01:30 | 5.59 | 5.58
2017-06-09 02:00 | 5.26 | 5.25
2017-06-09 02:30 | 4.98 | 4.97
2017-06-09 03:00 | 4.85 | 4.84
2017-06-09 03:30 | 4.93 | 4.92
2017-06-09 04:00 | 5.02 | 5
2017-06-09 04:30 | 5.37 | 5.36
2017-06-09 05:00 | 5.96 | 5.95
2017-06-09 05:30 | 7.09 | 7.08
2017-06-09 06:00 | 7.33 | 7.32
2017-06-09 06:30 | 8.25 | 8.24
2017-06-09 07:00 | 9.23 | 9.22
2017-06-09 07:30 | 9.88 | 9.87
2017-06-09 08:00 | 9.5 | 9.48
2017-06-09 08:30 | 7.6 | 7.59
2017-06-09 09:00 | 6.34 | 6.32
2017-06-09 09:30 | 5.53 | 5.5
2017-06-09 10:00 | 4.97 | 4.94
2017-06-09 10:30 | 4.3 | 4.27
2017-06-09 11:00 | 3.87 | 3.84
2017-06-09 11:30 | 3.67 | 3.64
2017-06-09 12:00 | 4.36 | 4.33
2017-06-09 12:30 | 4.58 | 4.55
2017-06-09 13:00 | 4.59 | 4.57
2017-06-09 13:30 | 5.48 | 5.46
2017-06-09 14:00 | 5.47 | 5.45
2017-06-09 14:30 | 5.07 | 5.05
2017-06-09 15:00 | 6.09 | 6.07
2017-06-09 15:30 | 6.2 | 6.18
2017-06-09 16:00 | 6.88 | 6.86
2017-06-09 16:30 | 7.43 | 7.42
2017-06-09 17:00 | 8.43 | 8.41
2017-06-09 17:30 | 9.68 | 9.67
2017-06-09 18:00 | 10.34 | 10.32
2017-06-09 18:30 | 10.71 | 10.69
2017-06-09 19:00 | 10.96 | 10.94
2017-06-09 19:30 | 10.79 | 10.77
2017-06-09 20:00 | 10.68 | 10.67
2017-06-09 20:30 | 10.8 | 10.79
2017-06-09 21:00 | 10.41 | 10.4
2017-06-09 21:30 | 9.73 | 9.73
2017-06-09 22:00 | 9.21 | 9.2
2017-06-09 22:30 | 8.83 | 8.82
2017-06-09 23:00 | 8.63 | 8.61
2017-06-09 23:30 | 7.83 | 7.82
2017-06-10 | 6.88 | 6.87
2017-06-10 00:30 | 6.06 | 6.04
2017-06-10 01:00 | 5.71 | 5.7
2017-06-10 01:30 | 5.21 | 5.19
2017-06-10 02:00 | 4.84 | 4.82
2017-06-10 02:30 | 4.52 | 4.51
2017-06-10 03:00 | 4.45 | 4.44
2017-06-10 03:30 | 4.47 | 4.45
2017-06-10 04:00 | 4.35 | 4.33
2017-06-10 04:30 | 4.36 | 4.34
2017-06-10 05:00 | 4.47 | 4.44
2017-06-10 05:30 | 4.71 | 4.69
2017-06-10 06:00 | 4.97 | 4.95
2017-06-10 06:30 | 5.09 | 5.07
2017-06-10 07:00 | 5.57 | 5.55
2017-06-10 07:30 | 6.16 | 6.14
2017-06-10 08:00 | 6.35 | 6.32
2017-06-10 08:30 | 6.28 | 6.26
2017-06-10 09:00 | 6.29 | 6.27
2017-06-10 09:30 | 5.83 | 5.81
2017-06-10 10:00 | 5.43 | 5.4
2017-06-10 10:30 | 5.16 | 5.14
2017-06-10 11:00 | 5.04 | 5.01
2017-06-10 11:30 | 4.78 | 4.76
2017-06-10 12:00 | 5.07 | 5.04
2017-06-10 12:30 | 6.05 | 6.03
2017-06-10 13:00 | 6.05 | 6.02
2017-06-10 13:30 | 6.27 | 6.25
2017-06-10 14:00 | 5.27 | 5.24
2017-06-10 14:30 | 6.23 | 6.21
2017-06-10 15:00 | 6.22 | 6.21
2017-06-10 15:30 | 6.85 | 6.83
2017-06-10 16:00 | 7.12 | 7.11
2017-06-10 16:30 | 7.54 | 7.53
2017-06-10 17:00 | 8.46 | 8.45
2017-06-10 17:30 | 9.66 | 9.65
2017-06-10 18:00 | 10.37 | 10.36
2017-06-10 18:30 | 10.23 | 10.22
2017-06-10 19:00 | 10.33 | 10.32
2017-06-10 19:30 | 10.1 | 10.09
2017-06-10 20:00 | 10.07 | 10.06
2017-06-10 20:30 | 10.1 | 10.09
2017-06-10 21:00 | 9.63 | 9.63
2017-06-10 21:30 | 9.11 | 9.1
2017-06-10 22:00 | 8.54 | 8.53
2017-06-10 22:30 | 8.34 | 8.33
2017-06-10 23:00 | 8.32 | 8.31
2017-06-10 23:30 | 7.45 | 7.44
2017-06-11 | 6.47 | 6.46
2017-06-11 00:30 | 5.79 | 5.78
2017-06-11 01:00 | 5.48 | 5.46
2017-06-11 01:30 | 4.87 | 4.86
2017-06-11 02:00 | 4.55 | 4.53
2017-06-11 02:30 | 4.37 | 4.35
2017-06-11 03:00 | 4.21 | 4.19
2017-06-11 03:30 | 4.17 | 4.15
2017-06-11 04:00 | 4.13 | 4.11
2017-06-11 04:30 | 4.15 | 4.13
2017-06-11 05:00 | 4.17 | 4.14
2017-06-11 05:30 | 4.31 | 4.29
2017-06-11 06:00 | 4.44 | 4.41
2017-06-11 06:30 | 4.6 | 4.58
2017-06-11 07:00 | 4.85 | 4.81
2017-06-11 07:30 | 5.5 | 5.47
2017-06-11 08:00 | 6.29 | 6.27
2017-06-11 08:30 | 6.31 | 6.29
2017-06-11 09:00 | 6.72 | 6.7
2017-06-11 09:30 | 7.35 | 7.33
2017-06-11 10:00 | 7.88 | 7.86
2017-06-11 10:30 | 8.17 | 8.16
2017-06-11 11:00 | 8.28 | 8.27
2017-06-11 11:30 | 8.2 | 8.18
2017-06-11 12:00 | 7.96 | 7.95
2017-06-11 12:30 | 7.69 | 7.67
2017-06-11 13:00 | 8.16 | 8.15
2017-06-11 13:30 | 7.97 | 7.95
2017-06-11 14:00 | 8.48 | 8.46
2017-06-11 14:30 | 8.54 | 8.52
2017-06-11 15:00 | 7.95 | 7.93
2017-06-11 15:30 | 7.36 | 7.34
2017-06-11 16:00 | 8.58 | 8.56
2017-06-11 16:30 | 9.51 | 9.49
2017-06-11 17:00 | 10.39 | 10.37
2017-06-11 17:30 | 11.47 | 11.46
2017-06-11 18:00 | 12.13 | 12.12
2017-06-11 18:30 | 11.88 | 11.86
2017-06-11 19:00 | 11.8 | 11.79
2017-06-11 19:30 | 11.32 | 11.3
2017-06-11 20:00 | 11.19 | 11.17
2017-06-11 20:30 | 11.06 | 11.05
2017-06-11 21:00 | 10.55 | 10.54
2017-06-11 21:30 | 9.92 | 9.91
2017-06-11 22:00 | 9.23 | 9.21
2017-06-11 22:30 | 8.62 | 8.6
2017-06-11 23:00 | 8.32 | 8.3
2017-06-11 23:30 | 7.41 | 7.39
2017-06-12 | 6.44 | 6.42
2017-06-12 00:30 | 5.7 | 5.68
2017-06-12 01:00 | 5.29 | 5.28
2017-06-12 01:30 | 4.88 | 4.87
2017-06-12 02:00 | 4.56 | 4.54
2017-06-12 02:30 | 4.34 | 4.32
2017-06-12 03:00 | 4.22 | 4.2
2017-06-12 03:30 | 4.33 | 4.32
2017-06-12 04:00 | 4.34 | 4.32
2017-06-12 04:30 | 4.58 | 4.56
2017-06-12 05:00 | 4.88 | 4.86
2017-06-12 05:30 | 5.47 | 5.46
2017-06-12 06:00 | 6.22 | 6.21
2017-06-12 06:30 | 7.16 | 7.15
2017-06-12 07:00 | 7.95 | 7.94
2017-06-12 07:30 | 8.79 | 8.79
2017-06-12 08:00 | 8.94 | 8.94
2017-06-12 08:30 | 7.67 | 7.66
2017-06-12 09:00 | 6.4 | 6.39
2017-06-12 09:30 | 5.64 | 5.62
2017-06-12 10:00 | 5.69 | 5.67
2017-06-12 10:30 | 5.65 | 5.63
2017-06-12 11:00 | 5.25 | 5.23
2017-06-12 11:30 | 5.66 | 5.64
2017-06-12 12:00 | 6.44 | 6.43
2017-06-12 12:30 | 5.48 | 5.47
2017-06-12 13:00 | 5 | 4.99
2017-06-12 13:30 | 5.88 | 5.87
2017-06-12 14:00 | 6.01 | 6
2017-06-12 14:30 | 5.24 | 5.23
2017-06-12 15:00 | 5.79 | 5.78
2017-06-12 15:30 | 6.29 | 6.28
2017-06-12 16:00 | 7.14 | 7.13
2017-06-12 16:30 | 8.18 | 8.18
2017-06-12 17:00 | 9.82 | 9.82
2017-06-12 17:30 | 11.35 | 11.33
2017-06-12 18:00 | 12.2 | 12.18
2017-06-12 18:30 | 12.35 | 12.33
2017-06-12 19:00 | 12.44 | 12.42
2017-06-12 19:30 | 12 | 11.98
2017-06-12 20:00 | 11.93 | 11.92
2017-06-12 20:30 | 11.86 | 11.85
2017-06-12 21:00 | 11.14 | 11.12
2017-06-12 21:30 | 10.22 | 10.2
2017-06-12 22:00 | 9.12 | 9.1
2017-06-12 22:30 | 8.55 | 8.53
2017-06-12 23:00 | 8.2 | 8.18
2017-06-12 23:30 | 7.29 | 7.28
2017-06-13 | 6.29 | 6.27
2017-06-13 00:30 | 5.58 | 5.56
2017-06-13 01:00 | 5.08 | 5.06
2017-06-13 01:30 | 4.71 | 4.7
2017-06-13 02:00 | 4.57 | 4.55
2017-06-13 02:30 | 4.3 | 4.28
2017-06-13 03:00 | 4.14 | 4.12
2017-06-13 03:30 | 4.11 | 4.09
2017-06-13 04:00 | 4.23 | 4.21
2017-06-13 04:30 | 4.55 | 4.53
2017-06-13 05:00 | 4.83 | 4.81
2017-06-13 05:30 | 5.53 | 5.52
2017-06-13 06:00 | 6.45 | 6.44
2017-06-13 06:30 | 7.02 | 7.01
2017-06-13 07:00 | 7.68 | 7.67
2017-06-13 07:30 | 8.36 | 8.35
2017-06-13 08:00 | 8.67 | 8.67
2017-06-13 08:30 | 7.9 | 7.9
2017-06-13 09:00 | 7.61 | 7.61
2017-06-13 09:30 | 7.44 | 7.44
2017-06-13 10:00 | 7.62 | 7.61
2017-06-13 10:30 | 7.09 | 7.09
2017-06-13 11:00 | 6.97 | 6.96
2017-06-13 11:30 | 7.18 | 7.17
2017-06-13 12:00 | 6.83 | 6.82
2017-06-13 12:30 | 7.25 | 7.24
2017-06-13 13:00 | 7.05 | 7.04
2017-06-13 13:30 | 7.13 | 7.12
2017-06-13 14:00 | 7.24 | 7.22
2017-06-13 14:30 | 7.1 | 7.09
2017-06-13 15:00 | 7.08 | 7.07
2017-06-13 15:30 | 7.35 | 7.34
2017-06-13 16:00 | 8.26 | 8.24
2017-06-13 16:30 | 9.03 | 9.01
2017-06-13 17:00 | 10.33 | 10.31
2017-06-13 17:30 | 11.89 | 11.87
2017-06-13 18:00 | 12.47 | 12.45
2017-06-13 18:30 | 12.53 | 12.5
2017-06-13 19:00 | 12.59 | 12.57
2017-06-13 19:30 | 12.1 | 12.09
2017-06-13 20:00 | 12.04 | 12.02
2017-06-13 20:30 | 12 | 11.99
2017-06-13 21:00 | 11.57 | 11.56
2017-06-13 21:30 | 10.46 | 10.45
2017-06-13 22:00 | 9.55 | 9.54
2017-06-13 22:30 | 8.96 | 8.95
2017-06-13 23:00 | 8.54 | 8.53
2017-06-13 23:30 | 7.47 | 7.46
2017-06-14 | 6.49 | 6.48
2017-06-14 00:30 | 5.59 | 5.58
2017-06-14 01:00 | 5.21 | 5.19
2017-06-14 01:30 | 4.83 | 4.82
2017-06-14 02:00 | 4.6 | 4.58
2017-06-14 02:30 | 4.37 | 4.35
2017-06-14 03:00 | 4.27 | 4.25
2017-06-14 03:30 | 4.31 | 4.29
2017-06-14 04:00 | 4.45 | 4.43
2017-06-14 04:30 | 4.63 | 4.61
2017-06-14 05:00 | 4.87 | 4.85
2017-06-14 05:30 | 5.63 | 5.62
2017-06-14 06:00 | 6.45 | 6.44
2017-06-14 06:30 | 7.08 | 7.07
2017-06-14 07:00 | 7.58 | 7.57
2017-06-14 07:30 | 8.11 | 8.1
2017-06-14 08:00 | 7.76 | 7.75
2017-06-14 08:30 | 6.97 | 6.96
2017-06-14 09:00 | 6.35 | 6.34
2017-06-14 09:30 | 5.36 | 5.35
2017-06-14 10:00 | 5.82 | 5.82
2017-06-14 10:30 | 6.35 | 6.34
2017-06-14 11:00 | 6.85 | 6.85
2017-06-14 11:30 | 6.85 | 6.84
2017-06-14 12:00 | 6.37 | 6.37
2017-06-14 12:30 | 6.59 | 6.59
2017-06-14 13:00 | 5.97 | 5.96
2017-06-14 13:30 | 6.44 | 6.43
2017-06-14 14:00 | 6.49 | 6.48
2017-06-14 14:30 | 6.9 | 6.89
2017-06-14 15:00 | 7.09 | 7.08
2017-06-14 15:30 | 7.4 | 7.38
2017-06-14 16:00 | 8.4 | 8.39
2017-06-14 16:30 | 9.06 | 9.04
2017-06-14 17:00 | 9.86 | 9.84
2017-06-14 17:30 | 11.17 | 11.15
2017-06-14 18:00 | 12.14 | 12.12
2017-06-14 18:30 | 12.19 | 12.17
2017-06-14 19:00 | 12.24 | 12.22
2017-06-14 19:30 | 11.88 | 11.86
2017-06-14 20:00 | 11.74 | 11.72
2017-06-14 20:30 | 11.87 | 11.86
2017-06-14 21:00 | 11.19 | 11.17
2017-06-14 21:30 | 10.22 | 10.2
2017-06-14 22:00 | 9.1 | 9.09
2017-06-14 22:30 | 8.63 | 8.62
2017-06-14 23:00 | 8.36 | 8.34
2017-06-14 23:30 | 7.31 | 7.29
2017-06-15 | 6.39 | 6.38
2017-06-15 00:30 | 5.52 | 5.5
2017-06-15 01:00 | 5.17 | 5.16
2017-06-15 01:30 | 4.91 | 4.9
2017-06-15 02:00 | 4.57 | 4.55
2017-06-15 02:30 | 4.38 | 4.36
2017-06-15 03:00 | 4.32 | 4.3
2017-06-15 03:30 | 4.37 | 4.35
2017-06-15 04:00 | 4.35 | 4.33
2017-06-15 04:30 | 4.61 | 4.59
2017-06-15 05:00 | 5 | 4.98
2017-06-15 05:30 | 5.86 | 5.85
2017-06-15 06:00 | 6.66 | 6.65
2017-06-15 06:30 | 7.22 | 7.21
2017-06-15 07:00 | 8.04 | 8.04
2017-06-15 07:30 | 8.93 | 8.92
2017-06-15 08:00 | 8.16 | 8.15
2017-06-15 08:30 | 7.19 | 7.18
2017-06-15 09:00 | 6.72 | 6.71
2017-06-15 09:30 | 6.19 | 6.17
2017-06-15 10:00 | 5.6 | 5.59
2017-06-15 10:30 | 4.68 | 4.66
2017-06-15 11:00 | 4.32 | 4.31
2017-06-15 11:30 | 4.45 | 4.44
2017-06-15 12:00 | 5.98 | 5.97
2017-06-15 12:30 | 6.06 | 6.05
2017-06-15 13:00 | 5.92 | 5.91
2017-06-15 13:30 | 5.36 | 5.33
2017-06-15 14:00 | 5.5 | 5.48
2017-06-15 14:30 | 5.86 | 5.84
2017-06-15 15:00 | 6.1 | 6.09
2017-06-15 15:30 | 6.35 | 6.33
2017-06-15 16:00 | 7.32 | 7.3
2017-06-15 16:30 | 8.26 | 8.23
2017-06-15 17:00 | 9.12 | 9.1
2017-06-15 17:30 | 10.54 | 10.52
2017-06-15 18:00 | 10.88 | 10.85
2017-06-15 18:30 | 11.14 | 11.11
2017-06-15 19:00 | 11.35 | 11.32
2017-06-15 19:30 | 10.99 | 10.97
2017-06-15 20:00 | 10.92 | 10.91
2017-06-15 20:30 | 11.17 | 11.16
2017-06-15 21:00 | 10.63 | 10.62
2017-06-15 21:30 | 10.01 | 9.99
2017-06-15 22:00 | 9.26 | 9.24
2017-06-15 22:30 | 8.79 | 8.78
2017-06-15 23:00 | 8.47 | 8.46
2017-06-15 23:30 | 7.4 | 7.39
2017-06-16 | 6.52 | 6.51
2017-06-16 00:30 | 5.76 | 5.75
2017-06-16 01:00 | 5.45 | 5.44
2017-06-16 01:30 | 5.18 | 5.17
2017-06-16 02:00 | 4.73 | 4.72
2017-06-16 02:30 | 4.5 | 4.48
2017-06-16 03:00 | 4.39 | 4.37
2017-06-16 03:30 | 4.37 | 4.35
2017-06-16 04:00 | 4.42 | 4.4
2017-06-16 04:30 | 4.66 | 4.64
2017-06-16 05:00 | 5.04 | 5.03
2017-06-16 05:30 | 5.85 | 5.84
2017-06-16 06:00 | 6.62 | 6.61
2017-06-16 06:30 | 7.3 | 7.3
2017-06-16 07:00 | 7.88 | 7.87
2017-06-16 07:30 | 8.61 | 8.6
2017-06-16 08:00 | 8.02 | 8.02
2017-06-16 08:30 | 6.92 | 6.91
2017-06-16 09:00 | 5.87 | 5.86
2017-06-16 09:30 | 5.26 | 5.25
2017-06-16 10:00 | 5.34 | 5.33
2017-06-16 10:30 | 5.18 | 5.16
2017-06-16 11:00 | 4.14 | 4.13
2017-06-16 11:30 | 5.48 | 5.46
2017-06-16 12:00 | 5.62 | 5.6
2017-06-16 12:30 | 5.8 | 5.78
2017-06-16 13:00 | 5.43 | 5.41
2017-06-16 13:30 | 4.92 | 4.89
2017-06-16 14:00 | 6.24 | 6.22
2017-06-16 14:30 | 5.94 | 5.92
2017-06-16 15:00 | 6.65 | 6.63
2017-06-16 15:30 | 6.51 | 6.49
2017-06-16 16:00 | 7.55 | 7.53
2017-06-16 16:30 | 8.05 | 8.04
2017-06-16 17:00 | 8.84 | 8.83
2017-06-16 17:30 | 9.86 | 9.84
2017-06-16 18:00 | 10.42 | 10.4
2017-06-16 18:30 | 10.56 | 10.54
2017-06-16 19:00 | 10.74 | 10.71
2017-06-16 19:30 | 10.51 | 10.49
2017-06-16 20:00 | 10.43 | 10.42
2017-06-16 20:30 | 10.44 | 10.43
2017-06-16 21:00 | 10.21 | 10.19
2017-06-16 21:30 | 9.52 | 9.5
2017-06-16 22:00 | 8.96 | 8.95
2017-06-16 22:30 | 8.57 | 8.56
2017-06-16 23:00 | 8.36 | 8.34
2017-06-16 23:30 | 7.42 | 7.41
2017-06-17 | 6.71 | 6.7
2017-06-17 00:30 | 5.87 | 5.85
2017-06-17 01:00 | 5.52 | 5.5
2017-06-17 01:30 | 5.11 | 5.09
2017-06-17 02:00 | 4.73 | 4.71
2017-06-17 02:30 | 4.46 | 4.45
2017-06-17 03:00 | 4.3 | 4.28
2017-06-17 03:30 | 4.34 | 4.33
2017-06-17 04:00 | 4.28 | 4.26
2017-06-17 04:30 | 4.33 | 4.32
2017-06-17 05:00 | 4.4 | 4.38
2017-06-17 05:30 | 4.6 | 4.58
2017-06-17 06:00 | 4.64 | 4.62
2017-06-17 06:30 | 4.9 | 4.87
2017-06-17 07:00 | 5.12 | 5.1
2017-06-17 07:30 | 5.86 | 5.84
2017-06-17 08:00 | 6.33 | 6.31
2017-06-17 08:30 | 6.63 | 6.61
2017-06-17 09:00 | 6.89 | 6.87
2017-06-17 09:30 | 6.59 | 6.57
2017-06-17 10:00 | 6.4 | 6.38
2017-06-17 10:30 | 6.3 | 6.27
2017-06-17 11:00 | 7.03 | 7.01
2017-06-17 11:30 | 6.25 | 6.22
2017-06-17 12:00 | 5.99 | 5.97
2017-06-17 12:30 | 6.34 | 6.32
2017-06-17 13:00 | 5.97 | 5.94
2017-06-17 13:30 | 6.18 | 6.16
2017-06-17 14:00 | 6.09 | 6.06
2017-06-17 14:30 | 6.72 | 6.7
2017-06-17 15:00 | 6.66 | 6.64
2017-06-17 15:30 | 6.45 | 6.43
2017-06-17 16:00 | 7.52 | 7.5
2017-06-17 16:30 | 7.76 | 7.75
2017-06-17 17:00 | 8.68 | 8.67
2017-06-17 17:30 | 9.89 | 9.87
2017-06-17 18:00 | 10.35 | 10.33
2017-06-17 18:30 | 10.22 | 10.19
2017-06-17 19:00 | 10.04 | 10.02
2017-06-17 19:30 | 9.72 | 9.7
2017-06-17 20:00 | 9.68 | 9.66
2017-06-17 20:30 | 9.83 | 9.82
2017-06-17 21:00 | 9.25 | 9.23
2017-06-17 21:30 | 8.78 | 8.76
2017-06-17 22:00 | 8.26 | 8.24
2017-06-17 22:30 | 8.1 | 8.09
2017-06-17 23:00 | 8.06 | 8.05
2017-06-17 23:30 | 7.23 | 7.21
2017-06-18 | 6.39 | 6.37
2017-06-18 00:30 | 5.68 | 5.66
2017-06-18 01:00 | 5.32 | 5.3
2017-06-18 01:30 | 4.9 | 4.89
2017-06-18 02:00 | 4.57 | 4.55
2017-06-18 02:30 | 4.37 | 4.35
2017-06-18 03:00 | 4.29 | 4.27
2017-06-18 03:30 | 4.27 | 4.25
2017-06-18 04:00 | 4.04 | 4.02
2017-06-18 04:30 | 4.08 | 4.06
2017-06-18 05:00 | 4.17 | 4.14
2017-06-18 05:30 | 4.35 | 4.32
2017-06-18 06:00 | 4.49 | 4.46
2017-06-18 06:30 | 4.7 | 4.68
2017-06-18 07:00 | 4.94 | 4.9
2017-06-18 07:30 | 5.44 | 5.41
2017-06-18 08:00 | 5.75 | 5.72
2017-06-18 08:30 | 6.09 | 6.07
2017-06-18 09:00 | 6.05 | 6.03
2017-06-18 09:30 | 6.06 | 6.04
2017-06-18 10:00 | 6.06 | 6.04
2017-06-18 10:30 | 6.35 | 6.33
2017-06-18 11:00 | 5.82 | 5.8
2017-06-18 11:30 | 5.23 | 5.21
2017-06-18 12:00 | 4.73 | 4.71
2017-06-18 12:30 | 4.69 | 4.66
2017-06-18 13:00 | 4.92 | 4.9
2017-06-18 13:30 | 5.02 | 5
2017-06-18 14:00 | 5.66 | 5.64
2017-06-18 14:30 | 5.86 | 5.83
2017-06-18 15:00 | 5.84 | 5.83
2017-06-18 15:30 | 6.32 | 6.3
2017-06-18 16:00 | 7.13 | 7.12
2017-06-18 16:30 | 8.04 | 8.02
2017-06-18 17:00 | 9.1 | 9.08
2017-06-18 17:30 | 10.45 | 10.44
2017-06-18 18:00 | 11.35 | 11.33
2017-06-18 18:30 | 11.28 | 11.27
2017-06-18 19:00 | 11.23 | 11.22
2017-06-18 19:30 | 10.77 | 10.75
2017-06-18 20:00 | 10.72 | 10.71
2017-06-18 20:30 | 10.75 | 10.74
2017-06-18 21:00 | 10.15 | 10.14
2017-06-18 21:30 | 9.43 | 9.42
2017-06-18 22:00 | 8.65 | 8.63
2017-06-18 22:30 | 8.31 | 8.29
2017-06-18 23:00 | 7.96 | 7.95
2017-06-18 23:30 | 7.14 | 7.13
2017-06-19 | 6.34 | 6.32
2017-06-19 00:30 | 5.63 | 5.61
2017-06-19 01:00 | 5.19 | 5.17
2017-06-19 01:30 | 4.73 | 4.71
2017-06-19 02:00 | 4.38 | 4.36
2017-06-19 02:30 | 4.33 | 4.31
2017-06-19 03:00 | 4.18 | 4.16
2017-06-19 03:30 | 4.32 | 4.3
2017-06-19 04:00 | 4.31 | 4.29
2017-06-19 04:30 | 4.6 | 4.58
2017-06-19 05:00 | 4.97 | 4.95
2017-06-19 05:30 | 5.71 | 5.7
2017-06-19 06:00 | 6.72 | 6.72
2017-06-19 06:30 | 7.01 | 7
2017-06-19 07:00 | 7.31 | 7.3
2017-06-19 07:30 | 7.79 | 7.78
2017-06-19 08:00 | 7.74 | 7.73
2017-06-19 08:30 | 6.91 | 6.91
2017-06-19 09:00 | 5.54 | 5.53
2017-06-19 09:30 | 5.61 | 5.59
2017-06-19 10:00 | 5.2 | 5.18
2017-06-19 10:30 | 4.43 | 4.4
2017-06-19 11:00 | 3.98 | 3.96
2017-06-19 11:30 | 4.34 | 4.32
2017-06-19 12:00 | 4.12 | 4.1
2017-06-19 12:30 | 4.76 | 4.75
2017-06-19 13:00 | 6.07 | 6.07
2017-06-19 13:30 | 5.32 | 5.31
2017-06-19 14:00 | 5.49 | 5.47
2017-06-19 14:30 | 5.86 | 5.85
2017-06-19 15:00 | 6.39 | 6.37
2017-06-19 15:30 | 6.63 | 6.62
2017-06-19 16:00 | 7.47 | 7.46
2017-06-19 16:30 | 8.35 | 8.34
2017-06-19 17:00 | 9.71 | 9.7
2017-06-19 17:30 | 11.23 | 11.22
2017-06-19 18:00 | 12.17 | 12.15
2017-06-19 18:30 | 12.22 | 12.19
2017-06-19 19:00 | 12.31 | 12.29
2017-06-19 19:30 | 11.96 | 11.93
2017-06-19 20:00 | 11.98 | 11.96
2017-06-19 20:30 | 11.86 | 11.85
2017-06-19 21:00 | 11.14 | 11.13
2017-06-19 21:30 | 10.28 | 10.28
2017-06-19 22:00 | 9.43 | 9.43
2017-06-19 22:30 | 8.66 | 8.65
2017-06-19 23:00 | 8.01 | 8
2017-06-19 23:30 | 6.97 | 6.95
2017-06-20 | 6.17 | 6.16
2017-06-20 00:30 | 5.39 | 5.38
2017-06-20 01:00 | 5 | 4.99
2017-06-20 01:30 | 4.71 | 4.69
2017-06-20 02:00 | 4.29 | 4.27
2017-06-20 02:30 | 4.15 | 4.14
2017-06-20 03:00 | 4.11 | 4.09
2017-06-20 03:30 | 4.13 | 4.11
2017-06-20 04:00 | 4.25 | 4.23
2017-06-20 04:30 | 4.52 | 4.5
2017-06-20 05:00 | 4.76 | 4.74
2017-06-20 05:30 | 5.35 | 5.33
2017-06-20 06:00 | 6.07 | 6.06
2017-06-20 06:30 | 6.78 | 6.77
2017-06-20 07:00 | 7.7 | 7.7
2017-06-20 07:30 | 8.22 | 8.21
2017-06-20 08:00 | 7.84 | 7.83
2017-06-20 08:30 | 6.89 | 6.88
2017-06-20 09:00 | 5.76 | 5.75
2017-06-20 09:30 | 5.74 | 5.73
2017-06-20 10:00 | 5 | 4.99
2017-06-20 10:30 | 4.88 | 4.87
2017-06-20 11:00 | 4.39 | 4.37
2017-06-20 11:30 | 5.64 | 5.63
2017-06-20 12:00 | 5.92 | 5.91
2017-06-20 12:30 | 4.72 | 4.72
2017-06-20 13:00 | 5.62 | 5.61
2017-06-20 13:30 | 4.94 | 4.94
2017-06-20 14:00 | 6.02 | 6.01
2017-06-20 14:30 | 6.08 | 6.07
2017-06-20 15:00 | 6.42 | 6.42
2017-06-20 15:30 | 6.04 | 6.04
2017-06-20 16:00 | 6.97 | 6.96
2017-06-20 16:30 | 7.9 | 7.89
2017-06-20 17:00 | 9.09 | 9.08
2017-06-20 17:30 | 10.85 | 10.83
2017-06-20 18:00 | 11.66 | 11.64
2017-06-20 18:30 | 11.73 | 11.71
2017-06-20 19:00 | 11.83 | 11.81
2017-06-20 19:30 | 11.58 | 11.56
2017-06-20 20:00 | 11.67 | 11.65
2017-06-20 20:30 | 11.76 | 11.75
2017-06-20 21:00 | 11.11 | 11.1
2017-06-20 21:30 | 10.3 | 10.3
2017-06-20 22:00 | 9.57 | 9.57
2017-06-20 22:30 | 8.77 | 8.77
2017-06-20 23:00 | 8.24 | 8.23
2017-06-20 23:30 | 7.13 | 7.12
2017-06-21 | 6.22 | 6.21
2017-06-21 00:30 | 5.52 | 5.51
2017-06-21 01:00 | 5.04 | 5.03
2017-06-21 01:30 | 4.7 | 4.69
2017-06-21 02:00 | 4.42 | 4.41
2017-06-21 02:30 | 4.31 | 4.29
2017-06-21 03:00 | 4.21 | 4.19
2017-06-21 03:30 | 4.4 | 4.38
2017-06-21 04:00 | 4.44 | 4.42
2017-06-21 04:30 | 4.74 | 4.72
2017-06-21 05:00 | 5.16 | 5.14
2017-06-21 05:30 | 5.97 | 5.96
2017-06-21 06:00 | 7.06 | 7.05
2017-06-21 06:30 | 7.58 | 7.57
2017-06-21 07:00 | 8.36 | 8.35
2017-06-21 07:30 | 8.84 | 8.83
2017-06-21 08:00 | 8.39 | 8.38
2017-06-21 08:30 | 7.67 | 7.66
2017-06-21 09:00 | 6.61 | 6.61
2017-06-21 09:30 | 6.02 | 6.01
2017-06-21 10:00 | 5.35 | 5.34
2017-06-21 10:30 | 5.02 | 5.01
2017-06-21 11:00 | 4.7 | 4.69
2017-06-21 11:30 | 4.46 | 4.45
2017-06-21 12:00 | 4.46 | 4.44
2017-06-21 12:30 | 4.37 | 4.36
2017-06-21 13:00 | 4.47 | 4.46
2017-06-21 13:30 | 5.05 | 5.03
2017-06-21 14:00 | 5.3 | 5.29
2017-06-21 14:30 | 4.76 | 4.74
2017-06-21 15:00 | 5.21 | 5.19
2017-06-21 15:30 | 5.72 | 5.71
2017-06-21 16:00 | 6.74 | 6.73
2017-06-21 16:30 | 8.09 | 8.08
2017-06-21 17:00 | 9.22 | 9.22
2017-06-21 17:30 | 10.86 | 10.85
2017-06-21 18:00 | 11.55 | 11.53
2017-06-21 18:30 | 11.84 | 11.82
2017-06-21 19:00 | 12.02 | 12
2017-06-21 19:30 | 11.77 | 11.76
2017-06-21 20:00 | 11.8 | 11.79
2017-06-21 20:30 | 12.02 | 12.01
2017-06-21 21:00 | 11.17 | 11.17
2017-06-21 21:30 | 10.44 | 10.43
2017-06-21 22:00 | 9.68 | 9.68
2017-06-21 22:30 | 9.21 | 9.2
2017-06-21 23:00 | 8.98 | 8.97
2017-06-21 23:30 | 7.98 | 7.97
2017-06-22 | 6.94 | 6.93
2017-06-22 00:30 | 6.09 | 6.08
2017-06-22 01:00 | 5.66 | 5.65
2017-06-22 01:30 | 5.27 | 5.26
2017-06-22 02:00 | 5.02 | 5.01
2017-06-22 02:30 | 4.78 | 4.77
2017-06-22 03:00 | 4.67 | 4.65
2017-06-22 03:30 | 4.63 | 4.62
2017-06-22 04:00 | 4.69 | 4.67
2017-06-22 04:30 | 5.01 | 5
2017-06-22 05:00 | 5.34 | 5.32
2017-06-22 05:30 | 5.97 | 5.96
2017-06-22 06:00 | 6.76 | 6.76
2017-06-22 06:30 | 8.02 | 8.01
2017-06-22 07:00 | 9.51 | 9.51
2017-06-22 07:30 | 9.14 | 9.14
2017-06-22 08:00 | 8.72 | 8.71
2017-06-22 08:30 | 8.41 | 8.41
2017-06-22 09:00 | 7.29 | 7.28
2017-06-22 09:30 | 5.64 | 5.63
2017-06-22 10:00 | 4.96 | 4.95
2017-06-22 10:30 | 4.5 | 4.48
2017-06-22 11:00 | 4.26 | 4.24
2017-06-22 11:30 | 4.23 | 4.22
2017-06-22 12:00 | 4.22 | 4.21
2017-06-22 12:30 | 4.47 | 4.47
2017-06-22 13:00 | 4.7 | 4.69
2017-06-22 13:30 | 4.94 | 4.93
2017-06-22 14:00 | 5.76 | 5.75
2017-06-22 14:30 | 5.21 | 5.2
2017-06-22 15:00 | 6.1 | 6.09
2017-06-22 15:30 | 6.8 | 6.79
2017-06-22 16:00 | 7.46 | 7.45
2017-06-22 16:30 | 8.03 | 8.02
2017-06-22 17:00 | 8.97 | 8.97
2017-06-22 17:30 | 10.52 | 10.51
2017-06-22 18:00 | 11.78 | 11.75
2017-06-22 18:30 | 11.96 | 11.94
2017-06-22 19:00 | 12.21 | 12.19
2017-06-22 19:30 | 11.86 | 11.84
2017-06-22 20:00 | 12.23 | 12.22
2017-06-22 20:30 | 12.39 | 12.38
2017-06-22 21:00 | 12.06 | 12.05
2017-06-22 21:30 | 11.01 | 11
2017-06-22 22:00 | 10.07 | 10.06
2017-06-22 22:30 | 9.56 | 9.55
2017-06-22 23:00 | 9.06 | 9.05
2017-06-22 23:30 | 8 | 7.99
2017-06-23 | 7.09 | 7.09
2017-06-23 00:30 | 6.33 | 6.32
2017-06-23 01:00 | 6 | 5.99
2017-06-23 01:30 | 5.53 | 5.52
2017-06-23 02:00 | 5.21 | 5.2
2017-06-23 02:30 | 5.03 | 5.02
2017-06-23 03:00 | 5.04 | 5.03
2017-06-23 03:30 | 5.03 | 5.01
2017-06-23 04:00 | 5.18 | 5.16
2017-06-23 04:30 | 5.42 | 5.41
2017-06-23 05:00 | 5.81 | 5.8
2017-06-23 05:30 | 6.52 | 6.51
2017-06-23 06:00 | 7.23 | 7.22
2017-06-23 06:30 | 7.9 | 7.9
2017-06-23 07:00 | 8.66 | 8.65
2017-06-23 07:30 | 9.24 | 9.23
2017-06-23 08:00 | 8.69 | 8.68
2017-06-23 08:30 | 8.1 | 8.09
2017-06-23 09:00 | 6.61 | 6.61
2017-06-23 09:30 | 5.94 | 5.92
2017-06-23 10:00 | 5.43 | 5.41
2017-06-23 10:30 | 4.81 | 4.79
2017-06-23 11:00 | 4.44 | 4.43
2017-06-23 11:30 | 4.17 | 4.15
2017-06-23 12:00 | 3.88 | 3.86
2017-06-23 12:30 | 3.79 | 3.77
2017-06-23 13:00 | 3.86 | 3.85
2017-06-23 13:30 | 3.91 | 3.89
2017-06-23 14:00 | 4.25 | 4.24
2017-06-23 14:30 | 4.49 | 4.47
2017-06-23 15:00 | 4.83 | 4.81
2017-06-23 15:30 | 5.57 | 5.56
2017-06-23 16:00 | 6.38 | 6.37
2017-06-23 16:30 | 7.3 | 7.29
2017-06-23 17:00 | 8.37 | 8.36
2017-06-23 17:30 | 9.58 | 9.57
2017-06-23 18:00 | 10.7 | 10.69
2017-06-23 18:30 | 11 | 10.99
2017-06-23 19:00 | 10.93 | 10.92
2017-06-23 19:30 | 10.76 | 10.75
2017-06-23 20:00 | 10.88 | 10.87
2017-06-23 20:30 | 11.14 | 11.13
2017-06-23 21:00 | 10.8 | 10.79
2017-06-23 21:30 | 10.23 | 10.22
2017-06-23 22:00 | 9.67 | 9.66
2017-06-23 22:30 | 9.17 | 9.16
2017-06-23 23:00 | 8.87 | 8.86
2017-06-23 23:30 | 7.99 | 7.98
2017-06-24 | 7.08 | 7.07
2017-06-24 00:30 | 6.26 | 6.24
2017-06-24 01:00 | 5.87 | 5.86
2017-06-24 01:30 | 5.51 | 5.49
2017-06-24 02:00 | 5.13 | 5.12
2017-06-24 02:30 | 4.93 | 4.92
2017-06-24 03:00 | 4.76 | 4.74
2017-06-24 03:30 | 4.78 | 4.77
2017-06-24 04:00 | 4.65 | 4.63
2017-06-24 04:30 | 4.76 | 4.74
2017-06-24 05:00 | 4.98 | 4.96
2017-06-24 05:30 | 5.21 | 5.19
2017-06-24 06:00 | 5.46 | 5.44
2017-06-24 06:30 | 5.74 | 5.72
2017-06-24 07:00 | 6.17 | 6.15
2017-06-24 07:30 | 6.81 | 6.8
2017-06-24 08:00 | 7.19 | 7.18
2017-06-24 08:30 | 7.37 | 7.36
2017-06-24 09:00 | 6.83 | 6.81
2017-06-24 09:30 | 6.76 | 6.74
2017-06-24 10:00 | 6.18 | 6.15
2017-06-24 10:30 | 5.72 | 5.7
2017-06-24 11:00 | 5.03 | 5
2017-06-24 11:30 | 4.67 | 4.64
2017-06-24 12:00 | 4.3 | 4.27
2017-06-24 12:30 | 4.21 | 4.18
2017-06-24 13:00 | 4.45 | 4.42
2017-06-24 13:30 | 4.4 | 4.37
2017-06-24 14:00 | 4.71 | 4.68
2017-06-24 14:30 | 4.95 | 4.93
2017-06-24 15:00 | 5.19 | 5.17
2017-06-24 15:30 | 5.8 | 5.78
2017-06-24 16:00 | 6.35 | 6.33
2017-06-24 16:30 | 7.24 | 7.22
2017-06-24 17:00 | 8.21 | 8.19
2017-06-24 17:30 | 9.17 | 9.15
2017-06-24 18:00 | 9.98 | 9.96
2017-06-24 18:30 | 10.17 | 10.15
2017-06-24 19:00 | 10.04 | 10.02
2017-06-24 19:30 | 9.9 | 9.88
2017-06-24 20:00 | 9.96 | 9.95
2017-06-24 20:30 | 10.07 | 10.06
2017-06-24 21:00 | 9.65 | 9.64
2017-06-24 21:30 | 9.05 | 9.04
2017-06-24 22:00 | 8.71 | 8.69
2017-06-24 22:30 | 8.56 | 8.54
2017-06-24 23:00 | 8.57 | 8.55
2017-06-24 23:30 | 7.72 | 7.71
2017-06-25 | 6.91 | 6.9
2017-06-25 00:30 | 6.18 | 6.16
2017-06-25 01:00 | 5.83 | 5.81
2017-06-25 01:30 | 5.27 | 5.26
2017-06-25 02:00 | 4.93 | 4.91
2017-06-25 02:30 | 4.71 | 4.69
2017-06-25 03:00 | 4.56 | 4.54
2017-06-25 03:30 | 4.63 | 4.61
2017-06-25 04:00 | 4.56 | 4.54
2017-06-25 04:30 | 4.53 | 4.51
2017-06-25 05:00 | 4.67 | 4.65
2017-06-25 05:30 | 4.84 | 4.82
2017-06-25 06:00 | 5.1 | 5.08
2017-06-25 06:30 | 5.3 | 5.28
2017-06-25 07:00 | 5.67 | 5.64
2017-06-25 07:30 | 6.31 | 6.29
2017-06-25 08:00 | 6.66 | 6.64
2017-06-25 08:30 | 6.58 | 6.56
2017-06-25 09:00 | 6.55 | 6.54
2017-06-25 09:30 | 6.4 | 6.38
2017-06-25 10:00 | 6.26 | 6.24
2017-06-25 10:30 | 5.64 | 5.62
2017-06-25 11:00 | 5.2 | 5.17
2017-06-25 11:30 | 4.99 | 4.97
2017-06-25 12:00 | 4.64 | 4.61
2017-06-25 12:30 | 4.51 | 4.48
2017-06-25 13:00 | 4.57 | 4.54
2017-06-25 13:30 | 4.67 | 4.64
2017-06-25 14:00 | 4.9 | 4.87
2017-06-25 14:30 | 5.24 | 5.22
2017-06-25 15:00 | 5.7 | 5.69
2017-06-25 15:30 | 6.2 | 6.19
2017-06-25 16:00 | 6.85 | 6.83
2017-06-25 16:30 | 7.59 | 7.57
2017-06-25 17:00 | 8.79 | 8.78
2017-06-25 17:30 | 10.11 | 10.1
2017-06-25 18:00 | 11.01 | 10.99
2017-06-25 18:30 | 11 | 10.99
2017-06-25 19:00 | 10.77 | 10.76
2017-06-25 19:30 | 10.33 | 10.32
2017-06-25 20:00 | 10.31 | 10.3
2017-06-25 20:30 | 10.34 | 10.33
2017-06-25 21:00 | 9.87 | 9.86
2017-06-25 21:30 | 9.3 | 9.29
2017-06-25 22:00 | 8.68 | 8.66
2017-06-25 22:30 | 8.32 | 8.31
2017-06-25 23:00 | 8.03 | 8.01
2017-06-25 23:30 | 7.1 | 7.09
2017-06-26 | 6.36 | 6.34
2017-06-26 00:30 | 5.6 | 5.59
2017-06-26 01:00 | 5.17 | 5.16
2017-06-26 01:30 | 4.88 | 4.86
2017-06-26 02:00 | 4.53 | 4.51
2017-06-26 02:30 | 4.34 | 4.33
2017-06-26 03:00 | 4.21 | 4.19
2017-06-26 03:30 | 4.38 | 4.36
2017-06-26 04:00 | 4.38 | 4.36
2017-06-26 04:30 | 4.68 | 4.66
2017-06-26 05:00 | 4.94 | 4.92
2017-06-26 05:30 | 5.53 | 5.51
2017-06-26 06:00 | 6.42 | 6.41
2017-06-26 06:30 | 7.07 | 7.07
2017-06-26 07:00 | 7.41 | 7.4
2017-06-26 07:30 | 7.71 | 7.7
2017-06-26 08:00 | 7.34 | 7.33
2017-06-26 08:30 | 7.02 | 7.01
2017-06-26 09:00 | 6.32 | 6.31
2017-06-26 09:30 | 5.81 | 5.8
2017-06-26 10:00 | 5.4 | 5.38
2017-06-26 10:30 | 5 | 4.99
2017-06-26 11:00 | 4.68 | 4.66
2017-06-26 11:30 | 4.18 | 4.15
2017-06-26 12:00 | 3.86 | 3.83
2017-06-26 12:30 | 4.16 | 4.14
2017-06-26 13:00 | 4.3 | 4.28
2017-06-26 13:30 | 4.42 | 4.4
2017-06-26 14:00 | 4.85 | 4.82
2017-06-26 14:30 | 5.47 | 5.45
2017-06-26 15:00 | 5.87 | 5.85
2017-06-26 15:30 | 6.39 | 6.38
2017-06-26 16:00 | 7.01 | 7
2017-06-26 16:30 | 8.06 | 8.05
2017-06-26 17:00 | 9.26 | 9.25
2017-06-26 17:30 | 10.73 | 10.72
2017-06-26 18:00 | 11.7 | 11.68
2017-06-26 18:30 | 11.57 | 11.56
2017-06-26 19:00 | 11.68 | 11.67
2017-06-26 19:30 | 11.39 | 11.38
2017-06-26 20:00 | 11.49 | 11.48
2017-06-26 20:30 | 11.68 | 11.67
2017-06-26 21:00 | 11.14 | 11.14
2017-06-26 21:30 | 10.36 | 10.35
2017-06-26 22:00 | 9.6 | 9.59
2017-06-26 22:30 | 8.92 | 8.91
2017-06-26 23:00 | 8.42 | 8.41
2017-06-26 23:30 | 7.52 | 7.5
2017-06-27 | 6.53 | 6.51
2017-06-27 00:30 | 5.77 | 5.75
2017-06-27 01:00 | 5.42 | 5.4
2017-06-27 01:30 | 5.07 | 5.05
2017-06-27 02:00 | 4.69 | 4.67
2017-06-27 02:30 | 4.55 | 4.53
2017-06-27 03:00 | 4.46 | 4.45
2017-06-27 03:30 | 4.47 | 4.45
2017-06-27 04:00 | 4.59 | 4.57
2017-06-27 04:30 | 4.79 | 4.77
2017-06-27 05:00 | 5.17 | 5.15
2017-06-27 05:30 | 5.88 | 5.86
2017-06-27 06:00 | 6.67 | 6.66
2017-06-27 06:30 | 7.37 | 7.36
2017-06-27 07:00 | 7.73 | 7.72
2017-06-27 07:30 | 7.88 | 7.88
2017-06-27 08:00 | 7.82 | 7.82
2017-06-27 08:30 | 7.8 | 7.79
2017-06-27 09:00 | 7.9 | 7.88
2017-06-27 09:30 | 8 | 7.99
2017-06-27 10:00 | 7.35 | 7.33
2017-06-27 10:30 | 6.75 | 6.74
2017-06-27 11:00 | 5.98 | 5.97
2017-06-27 11:30 | 5.72 | 5.7
2017-06-27 12:00 | 5.48 | 5.46
2017-06-27 12:30 | 6.07 | 6.05
2017-06-27 13:00 | 6.19 | 6.18
2017-06-27 13:30 | 5.71 | 5.69
2017-06-27 14:00 | 6.47 | 6.46
2017-06-27 14:30 | 5.73 | 5.72
2017-06-27 15:00 | 6.08 | 6.08
2017-06-27 15:30 | 6.92 | 6.92
2017-06-27 16:00 | 7.34 | 7.33
2017-06-27 16:30 | 7.92 | 7.92
2017-06-27 17:00 | 9.24 | 9.24
2017-06-27 17:30 | 10.95 | 10.94
2017-06-27 18:00 | 11.89 | 11.87
2017-06-27 18:30 | 12.1 | 12.08
2017-06-27 19:00 | 12.33 | 12.31
2017-06-27 19:30 | 11.82 | 11.8
2017-06-27 20:00 | 11.71 | 11.7
2017-06-27 20:30 | 11.91 | 11.89
2017-06-27 21:00 | 11.35 | 11.34
2017-06-27 21:30 | 10.53 | 10.52
2017-06-27 22:00 | 9.89 | 9.88
2017-06-27 22:30 | 9.18 | 9.17
2017-06-27 23:00 | 8.45 | 8.44
2017-06-27 23:30 | 7.49 | 7.49
2017-06-28 | 6.52 | 6.52
2017-06-28 00:30 | 5.72 | 5.71
2017-06-28 01:00 | 5.39 | 5.39
2017-06-28 01:30 | 5.02 | 5.01
2017-06-28 02:00 | 4.7 | 4.69
2017-06-28 02:30 | 4.45 | 4.44
2017-06-28 03:00 | 4.36 | 4.35
2017-06-28 03:30 | 4.37 | 4.35
2017-06-28 04:00 | 4.41 | 4.39
2017-06-28 04:30 | 4.64 | 4.63
2017-06-28 05:00 | 5.04 | 5.04
2017-06-28 05:30 | 5.64 | 5.64
2017-06-28 06:00 | 6.4 | 6.4
2017-06-28 06:30 | 7.2 | 7.19
2017-06-28 07:00 | 7.33 | 7.32
2017-06-28 07:30 | 7.35 | 7.35
2017-06-28 08:00 | 6.95 | 6.95
2017-06-28 08:30 | 6.71 | 6.71
2017-06-28 09:00 | 6.39 | 6.38
2017-06-28 09:30 | 5.91 | 5.9
2017-06-28 10:00 | 5.64 | 5.62
2017-06-28 10:30 | 5.01 | 4.99
2017-06-28 11:00 | 4.62 | 4.59
2017-06-28 11:30 | 4.48 | 4.46
2017-06-28 12:00 | 4.43 | 4.4
2017-06-28 12:30 | 4.35 | 4.33
2017-06-28 13:00 | 4.65 | 4.63
2017-06-28 13:30 | 4.93 | 4.91
2017-06-28 14:00 | 5.46 | 5.45
2017-06-28 14:30 | 5.93 | 5.91
2017-06-28 15:00 | 5.83 | 5.82
2017-06-28 15:30 | 6.22 | 6.21
2017-06-28 16:00 | 7.26 | 7.25
2017-06-28 16:30 | 7.72 | 7.71
2017-06-28 17:00 | 8.81 | 8.8
2017-06-28 17:30 | 10.11 | 10.1
2017-06-28 18:00 | 11.05 | 11.03
2017-06-28 18:30 | 11.35 | 11.33
2017-06-28 19:00 | 11.4 | 11.39
2017-06-28 19:30 | 11.16 | 11.15
2017-06-28 20:00 | 11.16 | 11.15
2017-06-28 20:30 | 11.28 | 11.27
2017-06-28 21:00 | 10.85 | 10.84
2017-06-28 21:30 | 10.12 | 10.12
2017-06-28 22:00 | 9.52 | 9.52
2017-06-28 22:30 | 8.69 | 8.69
2017-06-28 23:00 | 7.98 | 7.98
2017-06-28 23:30 | 6.93 | 6.93
2017-06-29 | 6 | 6
2017-06-29 00:30 | 5.21 | 5.2
2017-06-29 01:00 | 4.88 | 4.87
2017-06-29 01:30 | 4.63 | 4.61
2017-06-29 02:00 | 4.35 | 4.34
2017-06-29 02:30 | 4.2 | 4.19
2017-06-29 03:00 | 4.04 | 4.02
2017-06-29 03:30 | 4.15 | 4.14
2017-06-29 04:00 | 4.13 | 4.12
2017-06-29 04:30 | 4.31 | 4.3
2017-06-29 05:00 | 4.64 | 4.64
2017-06-29 05:30 | 5.27 | 5.26
2017-06-29 06:00 | 6.27 | 6.26
2017-06-29 06:30 | 6.73 | 6.72
2017-06-29 07:00 | 7.02 | 7.01
2017-06-29 07:30 | 6.99 | 6.98
2017-06-29 08:00 | 6.6 | 6.59
2017-06-29 08:30 | 6.26 | 6.25
2017-06-29 09:00 | 5.8 | 5.79
2017-06-29 09:30 | 5.3 | 5.29
2017-06-29 10:00 | 5.04 | 5.03
2017-06-29 10:30 | 4.58 | 4.56
2017-06-29 11:00 | 4.37 | 4.36
2017-06-29 11:30 | 4.14 | 4.13
2017-06-29 12:00 | 4.02 | 4
2017-06-29 12:30 | 4.09 | 4.08
2017-06-29 13:00 | 4.14 | 4.13
2017-06-29 13:30 | 4.24 | 4.23
2017-06-29 14:00 | 4.61 | 4.6
2017-06-29 14:30 | 4.95 | 4.93
2017-06-29 15:00 | 5.52 | 5.5
2017-06-29 15:30 | 5.92 | 5.9
2017-06-29 16:00 | 6.99 | 6.98
2017-06-29 16:30 | 7.57 | 7.56
2017-06-29 17:00 | 8.6 | 8.59
2017-06-29 17:30 | 9.89 | 9.87
2017-06-29 18:00 | 10.65 | 10.63
2017-06-29 18:30 | 10.71 | 10.68
2017-06-29 19:00 | 10.91 | 10.88
2017-06-29 19:30 | 10.6 | 10.58
2017-06-29 20:00 | 10.58 | 10.56
2017-06-29 20:30 | 10.6 | 10.59
2017-06-29 21:00 | 10.25 | 10.24
2017-06-29 21:30 | 9.72 | 9.71
2017-06-29 22:00 | 9.15 | 9.15
2017-06-29 22:30 | 8.48 | 8.47
2017-06-29 23:00 | 7.85 | 7.84
2017-06-29 23:30 | 6.92 | 6.91
2017-06-30 | 6.12 | 6.11
2017-06-30 00:30 | 5.41 | 5.4
2017-06-30 01:00 | 5.01 | 5
2017-06-30 01:30 | 4.7 | 4.69
2017-06-30 02:00 | 4.31 | 4.29
2017-06-30 02:30 | 4.01 | 3.99
2017-06-30 03:00 | 3.91 | 3.89
2017-06-30 03:30 | 3.95 | 3.93
2017-06-30 04:00 | 3.99 | 3.97
2017-06-30 04:30 | 4.1 | 4.08
2017-06-30 05:00 | 4.42 | 4.4
2017-06-30 05:30 | 4.87 | 4.85
2017-06-30 06:00 | 5.36 | 5.35
2017-06-30 06:30 | 5.83 | 5.82
2017-06-30 07:00 | 6.01 | 6
2017-06-30 07:30 | 6.2 | 6.18
2017-06-30 08:00 | 6.14 | 6.13
2017-06-30 08:30 | 5.46 | 5.44
2017-06-30 09:00 | 5 | 4.96
2017-06-30 09:30 | 4.77 | 4.74
2017-06-30 10:00 | 4.66 | 4.62
2017-06-30 10:30 | 5.08 | 5.06
2017-06-30 11:00 | 4.98 | 4.96
2017-06-30 11:30 | 4.69 | 4.67
2017-06-30 12:00 | 3.72 | 3.69
2017-06-30 12:30 | 3.42 | 3.39
2017-06-30 13:00 | 3.47 | 3.44
2017-06-30 13:30 | 3.54 | 3.5
2017-06-30 14:00 | 3.88 | 3.84
2017-06-30 14:30 | 4.3 | 4.27
2017-06-30 15:00 | 5.54 | 5.53
2017-06-30 15:30 | 6.34 | 6.33
2017-06-30 16:00 | 7.04 | 7.03
2017-06-30 16:30 | 8.04 | 8.03
2017-06-30 17:00 | 8.05 | 8.03
2017-06-30 17:30 | 8.79 | 8.78
2017-06-30 18:00 | 9.72 | 9.71
2017-06-30 18:30 | 9.91 | 9.89
2017-06-30 19:00 | 10.24 | 10.23
2017-06-30 19:30 | 10.11 | 10.1
2017-06-30 20:00 | 10.26 | 10.25
2017-06-30 20:30 | 10.34 | 10.33
2017-06-30 21:00 | 10.16 | 10.15
2017-06-30 21:30 | 9.75 | 9.74
2017-06-30 22:00 | 9.21 | 9.2
2017-06-30 22:30 | 8.81 | 8.8
2017-06-30 23:00 | 8.69 | 8.68
2017-06-30 23:30 | 7.83 | 7.82
2017-07-01 | 7 | 6.99
2017-07-01 00:30 | 6.24 | 6.23
2017-07-01 01:00 | 5.77 | 5.76
2017-07-01 01:30 | 5.47 | 5.46
2017-07-01 02:00 | 5.02 | 5
2017-07-01 02:30 | 4.75 | 4.73
2017-07-01 03:00 | 4.57 | 4.56
2017-07-01 03:30 | 4.67 | 4.65
2017-07-01 04:00 | 4.7 | 4.69
2017-07-01 04:30 | 4.79 | 4.77
2017-07-01 05:00 | 4.88 | 4.86
2017-07-01 05:30 | 5.17 | 5.14
2017-07-01 06:00 | 5.5 | 5.48
2017-07-01 06:30 | 5.66 | 5.64
2017-07-01 07:00 | 6.12 | 6.11
2017-07-01 07:30 | 6.68 | 6.66
2017-07-01 08:00 | 6.8 | 6.79
2017-07-01 08:30 | 6.89 | 6.87
2017-07-01 09:00 | 6.72 | 6.7
2017-07-01 09:30 | 6.48 | 6.46
2017-07-01 10:00 | 5.96 | 5.94
2017-07-01 10:30 | 5.29 | 5.27
2017-07-01 11:00 | 4.84 | 4.81
2017-07-01 11:30 | 4.59 | 4.57
2017-07-01 12:00 | 4.34 | 4.32
2017-07-01 12:30 | 4.09 | 4.07
2017-07-01 13:00 | 4.1 | 4.07
2017-07-01 13:30 | 4.2 | 4.17
2017-07-01 14:00 | 4.47 | 4.44
2017-07-01 14:30 | 4.72 | 4.69
2017-07-01 15:00 | 5.07 | 5.05
2017-07-01 15:30 | 5.66 | 5.65
2017-07-01 16:00 | 6.39 | 6.37
2017-07-01 16:30 | 7.29 | 7.28
2017-07-01 17:00 | 8.53 | 8.52
2017-07-01 17:30 | 9.94 | 9.93
2017-07-01 18:00 | 11.01 | 11
2017-07-01 18:30 | 11.32 | 11.3
2017-07-01 19:00 | 11.57 | 11.56
2017-07-01 19:30 | 11.43 | 11.42
2017-07-01 20:00 | 11.57 | 11.55
2017-07-01 20:30 | 11.79 | 11.77
2017-07-01 21:00 | 11.47 | 11.46
2017-07-01 21:30 | 10.95 | 10.94
2017-07-01 22:00 | 10.47 | 10.46
2017-07-01 22:30 | 10.18 | 10.17
2017-07-01 23:00 | 9.9 | 9.89
2017-07-01 23:30 | 8.98 | 8.97
2017-07-02 | 8.06 | 8.05
2017-07-02 00:30 | 7.3 | 7.29
2017-07-02 01:00 | 6.83 | 6.81
2017-07-02 01:30 | 6.23 | 6.22
2017-07-02 02:00 | 5.82 | 5.8
2017-07-02 02:30 | 5.44 | 5.42
2017-07-02 03:00 | 5.25 | 5.24
2017-07-02 03:30 | 5.3 | 5.28
2017-07-02 04:00 | 5.3 | 5.28
2017-07-02 04:30 | 5.32 | 5.31
2017-07-02 05:00 | 5.46 | 5.44
2017-07-02 05:30 | 5.52 | 5.51
2017-07-02 06:00 | 5.81 | 5.79
2017-07-02 06:30 | 6.2 | 6.19
2017-07-02 07:00 | 6.71 | 6.7
2017-07-02 07:30 | 7.48 | 7.46
2017-07-02 08:00 | 7.95 | 7.94
2017-07-02 08:30 | 8.36 | 8.35
2017-07-02 09:00 | 8.09 | 8.07
2017-07-02 09:30 | 7.8 | 7.79
2017-07-02 10:00 | 7.16 | 7.14
2017-07-02 10:30 | 6.45 | 6.43
2017-07-02 11:00 | 5.83 | 5.8
2017-07-02 11:30 | 5.35 | 5.32
2017-07-02 12:00 | 4.94 | 4.92
2017-07-02 12:30 | 4.76 | 4.73
2017-07-02 13:00 | 4.72 | 4.7
2017-07-02 13:30 | 4.75 | 4.72
2017-07-02 14:00 | 4.86 | 4.84
2017-07-02 14:30 | 5.12 | 5.1
2017-07-02 15:00 | 5.5 | 5.48
2017-07-02 15:30 | 6.04 | 6.02
2017-07-02 16:00 | 6.82 | 6.81
2017-07-02 16:30 | 7.98 | 7.96
2017-07-02 17:00 | 9.34 | 9.33
2017-07-02 17:30 | 10.92 | 10.91
2017-07-02 18:00 | 12.24 | 12.23
2017-07-02 18:30 | 12.37 | 12.36
2017-07-02 19:00 | 12.48 | 12.46
2017-07-02 19:30 | 12.18 | 12.17
2017-07-02 20:00 | 12.17 | 12.16
2017-07-02 20:30 | 12.21 | 12.2
2017-07-02 21:00 | 11.79 | 11.78
2017-07-02 21:30 | 11.1 | 11.09
2017-07-02 22:00 | 10.37 | 10.36
2017-07-02 22:30 | 9.68 | 9.67
2017-07-02 23:00 | 9.32 | 9.31
2017-07-02 23:30 | 8.21 | 8.2
2017-07-03 | 7.17 | 7.16
2017-07-03 00:30 | 6.36 | 6.35
2017-07-03 01:00 | 5.92 | 5.9
2017-07-03 01:30 | 5.58 | 5.56
2017-07-03 02:00 | 5.23 | 5.22
2017-07-03 02:30 | 5.05 | 5.04
2017-07-03 03:00 | 4.96 | 4.95
2017-07-03 03:30 | 5.02 | 5
2017-07-03 04:00 | 5.08 | 5.07
2017-07-03 04:30 | 5.39 | 5.38
2017-07-03 05:00 | 5.77 | 5.75
2017-07-03 05:30 | 6.5 | 6.48
2017-07-03 06:00 | 7.83 | 7.82
2017-07-03 06:30 | 9.07 | 9.07
2017-07-03 07:00 | 9.61 | 9.6
2017-07-03 07:30 | 9.98 | 9.98
2017-07-03 08:00 | 9.6 | 9.59
2017-07-03 08:30 | 9.02 | 9.01
2017-07-03 09:00 | 7.06 | 7.04
2017-07-03 09:30 | 6.16 | 6.13
2017-07-03 10:00 | 5.56 | 5.54
2017-07-03 10:30 | 5.03 | 5.01
2017-07-03 11:00 | 4.66 | 4.64
2017-07-03 11:30 | 4.27 | 4.25
2017-07-03 12:00 | 4.08 | 4.06
2017-07-03 12:30 | 4.1 | 4.08
2017-07-03 13:00 | 3.97 | 3.95
2017-07-03 13:30 | 4.32 | 4.29
2017-07-03 14:00 | 5.24 | 5.23
2017-07-03 14:30 | 5.97 | 5.96
2017-07-03 15:00 | 6.07 | 6.06
2017-07-03 15:30 | 6.02 | 6.01
2017-07-03 16:00 | 7.03 | 7.03
2017-07-03 16:30 | 8.28 | 8.28
2017-07-03 17:00 | 9.51 | 9.51
2017-07-03 17:30 | 10.73 | 10.72
2017-07-03 18:00 | 12.15 | 12.13
2017-07-03 18:30 | 12.45 | 12.43
2017-07-03 19:00 | 12.41 | 12.39
2017-07-03 19:30 | 12.16 | 12.14
2017-07-03 20:00 | 11.98 | 11.96
2017-07-03 20:30 | 12.07 | 12.06
2017-07-03 21:00 | 11.52 | 11.51
2017-07-03 21:30 | 10.75 | 10.74
2017-07-03 22:00 | 9.91 | 9.9
2017-07-03 22:30 | 9.08 | 9.07
2017-07-03 23:00 | 8.44 | 8.43
2017-07-03 23:30 | 7.44 | 7.43
2017-07-04 | 6.57 | 6.56
2017-07-04 00:30 | 5.68 | 5.67
2017-07-04 01:00 | 5.28 | 5.27
2017-07-04 01:30 | 4.98 | 4.97
2017-07-04 02:00 | 4.64 | 4.63
2017-07-04 02:30 | 4.39 | 4.37
2017-07-04 03:00 | 4.29 | 4.27
2017-07-04 03:30 | 4.31 | 4.29
2017-07-04 04:00 | 4.32 | 4.3
2017-07-04 04:30 | 4.57 | 4.55
2017-07-04 05:00 | 4.92 | 4.9
2017-07-04 05:30 | 5.42 | 5.4
2017-07-04 06:00 | 5.96 | 5.94
2017-07-04 06:30 | 6.39 | 6.38
2017-07-04 07:00 | 6.62 | 6.61
2017-07-04 07:30 | 6.84 | 6.83
2017-07-04 08:00 | 6.59 | 6.58
2017-07-04 08:30 | 5.82 | 5.8
2017-07-04 09:00 | 5.4 | 5.38
2017-07-04 09:30 | 5.02 | 5
2017-07-04 10:00 | 4.64 | 4.62
2017-07-04 10:30 | 4.14 | 4.12
2017-07-04 11:00 | 3.77 | 3.75
2017-07-04 11:30 | 3.6 | 3.58
2017-07-04 12:00 | 3.56 | 3.54
2017-07-04 12:30 | 3.69 | 3.67
2017-07-04 13:00 | 3.64 | 3.61
2017-07-04 13:30 | 3.7 | 3.68
2017-07-04 14:00 | 4.22 | 4.2
2017-07-04 14:30 | 5.16 | 5.15
2017-07-04 15:00 | 4.97 | 4.95
2017-07-04 15:30 | 5.73 | 5.72
2017-07-04 16:00 | 6.52 | 6.51
2017-07-04 16:30 | 7.42 | 7.41
2017-07-04 17:00 | 8.71 | 8.7
2017-07-04 17:30 | 10 | 9.99
2017-07-04 18:00 | 11.09 | 11.07
2017-07-04 18:30 | 11.43 | 11.4
2017-07-04 19:00 | 11.37 | 11.34
2017-07-04 19:30 | 11.04 | 11.02
2017-07-04 20:00 | 10.83 | 10.81
2017-07-04 20:30 | 10.85 | 10.84
2017-07-04 21:00 | 10.51 | 10.5
2017-07-04 21:30 | 9.85 | 9.84
2017-07-04 22:00 | 9.07 | 9.06
2017-07-04 22:30 | 8.48 | 8.47
2017-07-04 23:00 | 8.09 | 8.08
2017-07-04 23:30 | 7.25 | 7.24
2017-07-05 | 6.34 | 6.33
2017-07-05 00:30 | 5.65 | 5.64
2017-07-05 01:00 | 5.28 | 5.27
2017-07-05 01:30 | 4.93 | 4.92
2017-07-05 02:00 | 4.61 | 4.6
2017-07-05 02:30 | 4.31 | 4.3
2017-07-05 03:00 | 4.26 | 4.24
2017-07-05 03:30 | 4.35 | 4.33
2017-07-05 04:00 | 4.46 | 4.44
2017-07-05 04:30 | 4.73 | 4.71
2017-07-05 05:00 | 5 | 4.98
2017-07-05 05:30 | 5.69 | 5.67
2017-07-05 06:00 | 6.26 | 6.25
2017-07-05 06:30 | 6.76 | 6.74
2017-07-05 07:00 | 6.98 | 6.97
2017-07-05 07:30 | 7.09 | 7.07
2017-07-05 08:00 | 6.48 | 6.47
2017-07-05 08:30 | 5.95 | 5.93
2017-07-05 09:00 | 5.44 | 5.42
2017-07-05 09:30 | 4.97 | 4.96
2017-07-05 10:00 | 4.45 | 4.43
2017-07-05 10:30 | 3.99 | 3.97
2017-07-05 11:00 | 3.62 | 3.6
2017-07-05 11:30 | 3.44 | 3.41
2017-07-05 12:00 | 3.37 | 3.34
2017-07-05 12:30 | 3.29 | 3.26
2017-07-05 13:00 | 3.5 | 3.47
2017-07-05 13:30 | 3.57 | 3.54
2017-07-05 14:00 | 4.27 | 4.25
2017-07-05 14:30 | 4.82 | 4.8
2017-07-05 15:00 | 5.06 | 5.05
2017-07-05 15:30 | 6 | 5.99
2017-07-05 16:00 | 6.99 | 6.98
2017-07-05 16:30 | 8.21 | 8.2
2017-07-05 17:00 | 10.13 | 10.12
2017-07-05 17:30 | 10.54 | 10.53
2017-07-05 18:00 | 10.94 | 10.92
2017-07-05 18:30 | 11.08 | 11.07
2017-07-05 19:00 | 11.3 | 11.29
2017-07-05 19:30 | 10.91 | 10.9
2017-07-05 20:00 | 10.85 | 10.84
2017-07-05 20:30 | 10.71 | 10.7
2017-07-05 21:00 | 10.32 | 10.3
2017-07-05 21:30 | 9.49 | 9.48
2017-07-05 22:00 | 8.78 | 8.77
2017-07-05 22:30 | 8.3 | 8.29
2017-07-05 23:00 | 8.12 | 8.11
2017-07-05 23:30 | 7.12 | 7.1
2017-07-06 | 6.26 | 6.25
2017-07-06 00:30 | 5.46 | 5.45
2017-07-06 01:00 | 5.14 | 5.12
2017-07-06 01:30 | 4.75 | 4.73
2017-07-06 02:00 | 4.52 | 4.5
2017-07-06 02:30 | 4.37 | 4.35
2017-07-06 03:00 | 4.24 | 4.22
2017-07-06 03:30 | 4.28 | 4.26
2017-07-06 04:00 | 4.32 | 4.31
2017-07-06 04:30 | 4.52 | 4.5
2017-07-06 05:00 | 4.86 | 4.84
2017-07-06 05:30 | 5.45 | 5.44
2017-07-06 06:00 | 5.97 | 5.95
2017-07-06 06:30 | 6.34 | 6.33
2017-07-06 07:00 | 6.63 | 6.62
2017-07-06 07:30 | 6.86 | 6.85
2017-07-06 08:00 | 6.5 | 6.49
2017-07-06 08:30 | 5.91 | 5.9
2017-07-06 09:00 | 5.43 | 5.41
2017-07-06 09:30 | 5.09 | 5.07
2017-07-06 10:00 | 4.53 | 4.51
2017-07-06 10:30 | 4.1 | 4.08
2017-07-06 11:00 | 3.72 | 3.7
2017-07-06 11:30 | 3.45 | 3.44
2017-07-06 12:00 | 3.27 | 3.25
2017-07-06 12:30 | 3.34 | 3.32
2017-07-06 13:00 | 3.19 | 3.17
2017-07-06 13:30 | 3.35 | 3.32
2017-07-06 14:00 | 3.57 | 3.55
2017-07-06 14:30 | 3.92 | 3.9
2017-07-06 15:00 | 4.62 | 4.61
2017-07-06 15:30 | 5.23 | 5.21
2017-07-06 16:00 | 6.33 | 6.32
2017-07-06 16:30 | 7.09 | 7.08
2017-07-06 17:00 | 7.88 | 7.87
2017-07-06 17:30 | 9.13 | 9.12
2017-07-06 18:00 | 10.33 | 10.32
2017-07-06 18:30 | 10.76 | 10.75
2017-07-06 19:00 | 11.12 | 11.11
2017-07-06 19:30 | 10.99 | 10.98
2017-07-06 20:00 | 11.1 | 11.09
2017-07-06 20:30 | 11.13 | 11.12
2017-07-06 21:00 | 10.94 | 10.93
2017-07-06 21:30 | 10.54 | 10.53
2017-07-06 22:00 | 9.82 | 9.81
2017-07-06 22:30 | 9.3 | 9.29
2017-07-06 23:00 | 8.89 | 8.88
2017-07-06 23:30 | 7.9 | 7.89
2017-07-07 | 6.82 | 6.81
2017-07-07 00:30 | 6.06 | 6.05
2017-07-07 01:00 | 5.62 | 5.61
2017-07-07 01:30 | 5.24 | 5.23
2017-07-07 02:00 | 4.92 | 4.9
2017-07-07 02:30 | 4.67 | 4.65
2017-07-07 03:00 | 4.52 | 4.5
2017-07-07 03:30 | 4.58 | 4.56
2017-07-07 04:00 | 4.67 | 4.65
2017-07-07 04:30 | 4.84 | 4.82
2017-07-07 05:00 | 5.16 | 5.14
2017-07-07 05:30 | 5.84 | 5.83
2017-07-07 06:00 | 6.56 | 6.55
2017-07-07 06:30 | 7.1 | 7.09
2017-07-07 07:00 | 7.39 | 7.38
2017-07-07 07:30 | 7.74 | 7.73
2017-07-07 08:00 | 8.26 | 8.25
2017-07-07 08:30 | 8.43 | 8.43
2017-07-07 09:00 | 8.58 | 8.57
2017-07-07 09:30 | 8.71 | 8.7
2017-07-07 10:00 | 8.94 | 8.93
2017-07-07 10:30 | 8.63 | 8.61
2017-07-07 11:00 | 8.72 | 8.7
2017-07-07 11:30 | 8.77 | 8.76
2017-07-07 12:00 | 9.16 | 9.14
2017-07-07 12:30 | 9.23 | 9.21
2017-07-07 13:00 | 8.65 | 8.63
2017-07-07 13:30 | 8.7 | 8.68
2017-07-07 14:00 | 8.15 | 8.14
2017-07-07 14:30 | 8.19 | 8.18
2017-07-07 15:00 | 8.53 | 8.52
2017-07-07 15:30 | 8.79 | 8.77
2017-07-07 16:00 | 8.83 | 8.82
2017-07-07 16:30 | 9.2 | 9.19
2017-07-07 17:00 | 10.14 | 10.13
2017-07-07 17:30 | 11.11 | 11.09
2017-07-07 18:00 | 12.28 | 12.26
2017-07-07 18:30 | 12.71 | 12.69
2017-07-07 19:00 | 13.08 | 13.06
2017-07-07 19:30 | 12.89 | 12.87
2017-07-07 20:00 | 12.97 | 12.95
2017-07-07 20:30 | 12.94 | 12.92
2017-07-07 21:00 | 12.4 | 12.39
2017-07-07 21:30 | 11.63 | 11.62
2017-07-07 22:00 | 10.84 | 10.83
2017-07-07 22:30 | 10.29 | 10.28
2017-07-07 23:00 | 9.87 | 9.86
2017-07-07 23:30 | 8.77 | 8.76
2017-07-08 | 7.78 | 7.77
2017-07-08 00:30 | 6.85 | 6.84
2017-07-08 01:00 | 6.4 | 6.39
2017-07-08 01:30 | 5.85 | 5.84
2017-07-08 02:00 | 5.48 | 5.46
2017-07-08 02:30 | 5.21 | 5.19
2017-07-08 03:00 | 5.06 | 5.04
2017-07-08 03:30 | 5.08 | 5.06
2017-07-08 04:00 | 5 | 4.98
2017-07-08 04:30 | 5 | 4.99
2017-07-08 05:00 | 5.17 | 5.15
2017-07-08 05:30 | 5.41 | 5.39
2017-07-08 06:00 | 5.72 | 5.71
2017-07-08 06:30 | 6 | 5.98
2017-07-08 07:00 | 6.3 | 6.28
2017-07-08 07:30 | 7.05 | 7.03
2017-07-08 08:00 | 7.24 | 7.22
2017-07-08 08:30 | 7.19 | 7.18
2017-07-08 09:00 | 6.94 | 6.93
2017-07-08 09:30 | 6.62 | 6.6
2017-07-08 10:00 | 6.11 | 6.09
2017-07-08 10:30 | 5.6 | 5.57
2017-07-08 11:00 | 5.1 | 5.08
2017-07-08 11:30 | 4.68 | 4.65
2017-07-08 12:00 | 4.4 | 4.37
2017-07-08 12:30 | 4.17 | 4.14
2017-07-08 13:00 | 4.11 | 4.08
2017-07-08 13:30 | 4.15 | 4.12
2017-07-08 14:00 | 4.51 | 4.49
2017-07-08 14:30 | 4.78 | 4.76
2017-07-08 15:00 | 5.11 | 5.09
2017-07-08 15:30 | 5.58 | 5.57
2017-07-08 16:00 | 6.34 | 6.32
2017-07-08 16:30 | 7.1 | 7.09
2017-07-08 17:00 | 8.34 | 8.32
2017-07-08 17:30 | 9.61 | 9.6
2017-07-08 18:00 | 10.76 | 10.75
2017-07-08 18:30 | 11.12 | 11.11
2017-07-08 19:00 | 11.46 | 11.45
2017-07-08 19:30 | 11.41 | 11.4
2017-07-08 20:00 | 11.51 | 11.5
2017-07-08 20:30 | 11.73 | 11.72
2017-07-08 21:00 | 11.43 | 11.42
2017-07-08 21:30 | 10.94 | 10.93
2017-07-08 22:00 | 10.35 | 10.34
2017-07-08 22:30 | 10.05 | 10.05
2017-07-08 23:00 | 9.98 | 9.97
2017-07-08 23:30 | 9 | 8.99
2017-07-09 | 8.19 | 8.18
2017-07-09 00:30 | 7.39 | 7.38
2017-07-09 01:00 | 6.73 | 6.71
2017-07-09 01:30 | 6.24 | 6.23
2017-07-09 02:00 | 5.97 | 5.96
2017-07-09 02:30 | 5.64 | 5.62
2017-07-09 03:00 | 5.57 | 5.56
2017-07-09 03:30 | 5.55 | 5.53
2017-07-09 04:00 | 5.36 | 5.34
2017-07-09 04:30 | 5.39 | 5.38
2017-07-09 05:00 | 5.4 | 5.39
2017-07-09 05:30 | 5.63 | 5.62
2017-07-09 06:00 | 5.87 | 5.85
2017-07-09 06:30 | 6.15 | 6.13
2017-07-09 07:00 | 6.68 | 6.66
2017-07-09 07:30 | 7.4 | 7.39
2017-07-09 08:00 | 8.15 | 8.14
2017-07-09 08:30 | 8.22 | 8.21
2017-07-09 09:00 | 8.16 | 8.15
2017-07-09 09:30 | 8.83 | 8.82
2017-07-09 10:00 | 9.06 | 9.05
2017-07-09 10:30 | 7.2 | 7.18
2017-07-09 11:00 | 6.61 | 6.59
2017-07-09 11:30 | 5.81 | 5.79
2017-07-09 12:00 | 5.36 | 5.34
2017-07-09 12:30 | 5.14 | 5.12
2017-07-09 13:00 | 5.06 | 5.03
2017-07-09 13:30 | 5.01 | 4.98
2017-07-09 14:00 | 5.23 | 5.21
2017-07-09 14:30 | 5.31 | 5.29
2017-07-09 15:00 | 6.37 | 6.35
2017-07-09 15:30 | 7.51 | 7.49
2017-07-09 16:00 | 8.17 | 8.16
2017-07-09 16:30 | 8.97 | 8.95
2017-07-09 17:00 | 10.14 | 10.13
2017-07-09 17:30 | 11.75 | 11.74
2017-07-09 18:00 | 12.83 | 12.81
2017-07-09 18:30 | 13.06 | 13.04
2017-07-09 19:00 | 13.15 | 13.12
2017-07-09 19:30 | 12.68 | 12.67
2017-07-09 20:00 | 12.65 | 12.63
2017-07-09 20:30 | 12.7 | 12.69
2017-07-09 21:00 | 12.18 | 12.17
2017-07-09 21:30 | 11.33 | 11.32
2017-07-09 22:00 | 10.33 | 10.32
2017-07-09 22:30 | 9.68 | 9.67
2017-07-09 23:00 | 9.21 | 9.2
2017-07-09 23:30 | 8.09 | 8.08
2017-07-10 | 7.19 | 7.18
2017-07-10 00:30 | 6.35 | 6.34
2017-07-10 01:00 | 5.92 | 5.91
2017-07-10 01:30 | 5.53 | 5.52
2017-07-10 02:00 | 5.12 | 5.11
2017-07-10 02:30 | 4.91 | 4.89
2017-07-10 03:00 | 4.71 | 4.69
2017-07-10 03:30 | 4.79 | 4.78
2017-07-10 04:00 | 4.89 | 4.87
2017-07-10 04:30 | 5.17 | 5.15
2017-07-10 05:00 | 5.49 | 5.47
2017-07-10 05:30 | 6.55 | 6.54
2017-07-10 06:00 | 7.48 | 7.48
2017-07-10 06:30 | 8.34 | 8.33
2017-07-10 07:00 | 9.11 | 9.11
2017-07-10 07:30 | 10.24 | 10.24
2017-07-10 08:00 | 10 | 10
2017-07-10 08:30 | 8.06 | 8.06
2017-07-10 09:00 | 7.91 | 7.9
2017-07-10 09:30 | 6.15 | 6.14
2017-07-10 10:00 | 6.4 | 6.4
2017-07-10 10:30 | 6.63 | 6.63
2017-07-10 11:00 | 5.85 | 5.85
2017-07-10 11:30 | 6.2 | 6.2
2017-07-10 12:00 | 6.35 | 6.35
2017-07-10 12:30 | 6.11 | 6.1
2017-07-10 13:00 | 6.15 | 6.15
2017-07-10 13:30 | 6 | 5.99
2017-07-10 14:00 | 5.4 | 5.39
2017-07-10 14:30 | 6.07 | 6.06
2017-07-10 15:00 | 6.23 | 6.22
2017-07-10 15:30 | 6.89 | 6.88
2017-07-10 16:00 | 8.04 | 8.04
2017-07-10 16:30 | 9.24 | 9.23
2017-07-10 17:00 | 10.34 | 10.33
2017-07-10 17:30 | 11.84 | 11.82
2017-07-10 18:00 | 12.74 | 12.72
2017-07-10 18:30 | 13.05 | 13.02
2017-07-10 19:00 | 13.19 | 13.16
2017-07-10 19:30 | 12.97 | 12.95
2017-07-10 20:00 | 12.71 | 12.69
2017-07-10 20:30 | 12.64 | 12.62
2017-07-10 21:00 | 12.1 | 12.09
2017-07-10 21:30 | 11.11 | 11.1
2017-07-10 22:00 | 10.23 | 10.22
2017-07-10 22:30 | 9.48 | 9.47
2017-07-10 23:00 | 8.96 | 8.95
2017-07-10 23:30 | 7.81 | 7.8
2017-07-11 | 6.78 | 6.77
2017-07-11 00:30 | 6.08 | 6.07
2017-07-11 01:00 | 5.68 | 5.67
2017-07-11 01:30 | 5.2 | 5.19
2017-07-11 02:00 | 4.8 | 4.79
2017-07-11 02:30 | 4.59 | 4.58
2017-07-11 03:00 | 4.43 | 4.41
2017-07-11 03:30 | 4.6 | 4.58
2017-07-11 04:00 | 4.62 | 4.6
2017-07-11 04:30 | 4.85 | 4.83
2017-07-11 05:00 | 5.22 | 5.21
2017-07-11 05:30 | 6.03 | 6.02
2017-07-11 06:00 | 7.03 | 7.02
2017-07-11 06:30 | 7.85 | 7.85
2017-07-11 07:00 | 8.57 | 8.56
2017-07-11 07:30 | 9.27 | 9.27
2017-07-11 08:00 | 8.95 | 8.94
2017-07-11 08:30 | 7.52 | 7.51
2017-07-11 09:00 | 6.63 | 6.62
2017-07-11 09:30 | 5.9 | 5.9
2017-07-11 10:00 | 5.44 | 5.43
2017-07-11 10:30 | 5.05 | 5.04
2017-07-11 11:00 | 4.62 | 4.62
2017-07-11 11:30 | 4.39 | 4.39
2017-07-11 12:00 | 4.56 | 4.56
2017-07-11 12:30 | 4.54 | 4.53
2017-07-11 13:00 | 4.81 | 4.81
2017-07-11 13:30 | 5.04 | 5.03
2017-07-11 14:00 | 4.77 | 4.76
2017-07-11 14:30 | 4.82 | 4.81
2017-07-11 15:00 | 5.22 | 5.21
2017-07-11 15:30 | 4.96 | 4.95
2017-07-11 16:00 | 6.34 | 6.33
2017-07-11 16:30 | 7.17 | 7.16
2017-07-11 17:00 | 8.47 | 8.46
2017-07-11 17:30 | 9.91 | 9.9
2017-07-11 18:00 | 11.33 | 11.31
2017-07-11 18:30 | 11.94 | 11.91
2017-07-11 19:00 | 12.23 | 12.21
2017-07-11 19:30 | 12.02 | 12
2017-07-11 20:00 | 11.99 | 11.98
2017-07-11 20:30 | 12.07 | 12.06
2017-07-11 21:00 | 11.69 | 11.68
2017-07-11 21:30 | 10.95 | 10.95
2017-07-11 22:00 | 10.19 | 10.18
2017-07-11 22:30 | 9.5 | 9.49
2017-07-11 23:00 | 8.84 | 8.83
2017-07-11 23:30 | 7.82 | 7.81
2017-07-12 | 6.99 | 6.98
2017-07-12 00:30 | 6.24 | 6.23
2017-07-12 01:00 | 5.82 | 5.81
2017-07-12 01:30 | 5.52 | 5.51
2017-07-12 02:00 | 5.28 | 5.27
2017-07-12 02:30 | 4.97 | 4.95
2017-07-12 03:00 | 4.8 | 4.78
2017-07-12 03:30 | 4.94 | 4.93
2017-07-12 04:00 | 4.97 | 4.95
2017-07-12 04:30 | 5.32 | 5.3
2017-07-12 05:00 | 5.91 | 5.89
2017-07-12 05:30 | 6.82 | 6.81
2017-07-12 06:00 | 7.87 | 7.87
2017-07-12 06:30 | 8.75 | 8.75
2017-07-12 07:00 | 9.68 | 9.68
2017-07-12 07:30 | 11.6 | 11.6
2017-07-12 08:00 | 11.3 | 11.3
2017-07-12 08:30 | 9.56 | 9.56
2017-07-12 09:00 | 8.31 | 8.31
2017-07-12 09:30 | 7.45 | 7.45
2017-07-12 10:00 | 6.69 | 6.69
2017-07-12 10:30 | 6.18 | 6.18
2017-07-12 11:00 | 5.91 | 5.9
2017-07-12 11:30 | 5.41 | 5.4
2017-07-12 12:00 | 5.13 | 5.12
2017-07-12 12:30 | 5.02 | 5.01
2017-07-12 13:00 | 4.12 | 4.12
2017-07-12 13:30 | 4.14 | 4.13
2017-07-12 14:00 | 4.08 | 4.06
2017-07-12 14:30 | 4.47 | 4.46
2017-07-12 15:00 | 4.82 | 4.81
2017-07-12 15:30 | 5.31 | 5.3
2017-07-12 16:00 | 6.14 | 6.13
2017-07-12 16:30 | 7.16 | 7.15
2017-07-12 17:00 | 8.46 | 8.46
2017-07-12 17:30 | 9.9 | 9.89
2017-07-12 18:00 | 11.48 | 11.46
2017-07-12 18:30 | 12.13 | 12.11
2017-07-12 19:00 | 12.53 | 12.51
2017-07-12 19:30 | 12.5 | 12.48
2017-07-12 20:00 | 12.67 | 12.65
2017-07-12 20:30 | 12.9 | 12.88
2017-07-12 21:00 | 12.19 | 12.17
2017-07-12 21:30 | 11.42 | 11.41
2017-07-12 22:00 | 10.47 | 10.46
2017-07-12 22:30 | 10.07 | 10.07
2017-07-12 23:00 | 9.51 | 9.5
2017-07-12 23:30 | 8.43 | 8.42
2017-07-13 | 7.44 | 7.44
2017-07-13 00:30 | 6.49 | 6.48
2017-07-13 01:00 | 5.98 | 5.97
2017-07-13 01:30 | 5.53 | 5.52
2017-07-13 02:00 | 5.27 | 5.26
2017-07-13 02:30 | 5.05 | 5.03
2017-07-13 03:00 | 4.94 | 4.92
2017-07-13 03:30 | 4.97 | 4.95
2017-07-13 04:00 | 4.91 | 4.89
2017-07-13 04:30 | 5.26 | 5.24
2017-07-13 05:00 | 5.68 | 5.66
2017-07-13 05:30 | 6.84 | 6.83
2017-07-13 06:00 | 7.82 | 7.81
2017-07-13 06:30 | 8.72 | 8.71
2017-07-13 07:00 | 9.94 | 9.94
2017-07-13 07:30 | 10.74 | 10.74
2017-07-13 08:00 | 9.97 | 9.96
2017-07-13 08:30 | 8.57 | 8.56
2017-07-13 09:00 | 7.45 | 7.44
2017-07-13 09:30 | 6.72 | 6.71
2017-07-13 10:00 | 6.03 | 6.01
2017-07-13 10:30 | 5.26 | 5.25
2017-07-13 11:00 | 4.48 | 4.47
2017-07-13 11:30 | 4.53 | 4.52
2017-07-13 12:00 | 4.19 | 4.18
2017-07-13 12:30 | 4.42 | 4.41
2017-07-13 13:00 | 5.1 | 5.08
2017-07-13 13:30 | 4.9 | 4.88
2017-07-13 14:00 | 4.3 | 4.26
2017-07-13 14:30 | 4.28 | 4.25
2017-07-13 15:00 | 5.52 | 5.5
2017-07-13 15:30 | 5.73 | 5.72
2017-07-13 16:00 | 6.37 | 6.35
2017-07-13 16:30 | 7.35 | 7.33
2017-07-13 17:00 | 8.5 | 8.49
2017-07-13 17:30 | 9.88 | 9.88
2017-07-13 18:00 | 11.44 | 11.42
2017-07-13 18:30 | 12.04 | 12.02
2017-07-13 19:00 | 12.38 | 12.36
2017-07-13 19:30 | 12.18 | 12.17
2017-07-13 20:00 | 12.44 | 12.43
2017-07-13 20:30 | 12.64 | 12.63
2017-07-13 21:00 | 12.36 | 12.35
2017-07-13 21:30 | 11.58 | 11.57
2017-07-13 22:00 | 10.73 | 10.72
2017-07-13 22:30 | 9.94 | 9.93
2017-07-13 23:00 | 9.53 | 9.52
2017-07-13 23:30 | 8.5 | 8.49
2017-07-14 | 7.45 | 7.44
2017-07-14 00:30 | 6.64 | 6.63
2017-07-14 01:00 | 6.19 | 6.18
2017-07-14 01:30 | 5.75 | 5.74
2017-07-14 02:00 | 5.5 | 5.48
2017-07-14 02:30 | 5.14 | 5.13
2017-07-14 03:00 | 5.07 | 5.05
2017-07-14 03:30 | 5.08 | 5.07
2017-07-14 04:00 | 5.16 | 5.15
2017-07-14 04:30 | 5.44 | 5.42
2017-07-14 05:00 | 5.95 | 5.93
2017-07-14 05:30 | 6.78 | 6.76
2017-07-14 06:00 | 7.49 | 7.48
2017-07-14 06:30 | 8.37 | 8.36
2017-07-14 07:00 | 9.4 | 9.39
2017-07-14 07:30 | 10.31 | 10.3
2017-07-14 08:00 | 9.65 | 9.64
2017-07-14 08:30 | 8.14 | 8.12
2017-07-14 09:00 | 6.88 | 6.86
2017-07-14 09:30 | 6.12 | 6.09
2017-07-14 10:00 | 5.38 | 5.35
2017-07-14 10:30 | 5.02 | 5
2017-07-14 11:00 | 4.54 | 4.52
2017-07-14 11:30 | 4.18 | 4.15
2017-07-14 12:00 | 3.67 | 3.64
2017-07-14 12:30 | 3.32 | 3.29
2017-07-14 13:00 | 3.24 | 3.21
2017-07-14 13:30 | 3.48 | 3.46
2017-07-14 14:00 | 3.81 | 3.78
2017-07-14 14:30 | 4.04 | 4.03
2017-07-14 15:00 | 4.29 | 4.27
2017-07-14 15:30 | 4.96 | 4.95
2017-07-14 16:00 | 6.06 | 6.05
2017-07-14 16:30 | 6.93 | 6.92
2017-07-14 17:00 | 8.16 | 8.15
2017-07-14 17:30 | 9.23 | 9.22
2017-07-14 18:00 | 10.36 | 10.35
2017-07-14 18:30 | 10.94 | 10.93
2017-07-14 19:00 | 11.3 | 11.29
2017-07-14 19:30 | 11.22 | 11.21
2017-07-14 20:00 | 11.28 | 11.27
2017-07-14 20:30 | 11.47 | 11.46
2017-07-14 21:00 | 11.07 | 11.06
2017-07-14 21:30 | 10.43 | 10.42
2017-07-14 22:00 | 9.86 | 9.85
2017-07-14 22:30 | 9.43 | 9.42
2017-07-14 23:00 | 9.06 | 9.06
2017-07-14 23:30 | 8.21 | 8.2
2017-07-15 | 7.24 | 7.23
2017-07-15 00:30 | 6.51 | 6.5
2017-07-15 01:00 | 6.08 | 6.07
2017-07-15 01:30 | 5.65 | 5.64
2017-07-15 02:00 | 5.39 | 5.37
2017-07-15 02:30 | 5.07 | 5.05
2017-07-15 03:00 | 4.89 | 4.88
2017-07-15 03:30 | 4.9 | 4.89
2017-07-15 04:00 | 4.91 | 4.89
2017-07-15 04:30 | 4.97 | 4.95
2017-07-15 05:00 | 5.06 | 5.04
2017-07-15 05:30 | 5.3 | 5.29
2017-07-15 06:00 | 5.51 | 5.49
2017-07-15 06:30 | 5.94 | 5.92
2017-07-15 07:00 | 6.62 | 6.6
2017-07-15 07:30 | 7.22 | 7.21
2017-07-15 08:00 | 7.46 | 7.45
2017-07-15 08:30 | 7.36 | 7.34
2017-07-15 09:00 | 7.06 | 7.05
2017-07-15 09:30 | 6.56 | 6.54
2017-07-15 10:00 | 7.4 | 7.39
2017-07-15 10:30 | 6.93 | 6.92
2017-07-15 11:00 | 6.33 | 6.31
2017-07-15 11:30 | 5.08 | 5.06
2017-07-15 12:00 | 4.34 | 4.31
2017-07-15 12:30 | 4.13 | 4.09
2017-07-15 13:00 | 4.64 | 4.61
2017-07-15 13:30 | 4.8 | 4.77
2017-07-15 14:00 | 5.25 | 5.21
2017-07-15 14:30 | 5.19 | 5.15
2017-07-15 15:00 | 5.72 | 5.7
2017-07-15 15:30 | 6.25 | 6.23
2017-07-15 16:00 | 6.28 | 6.26
2017-07-15 16:30 | 7.27 | 7.25
2017-07-15 17:00 | 8.55 | 8.54
2017-07-15 17:30 | 9.73 | 9.72
2017-07-15 18:00 | 10.28 | 10.27
2017-07-15 18:30 | 10.03 | 10.02
2017-07-15 19:00 | 10.08 | 10.06
2017-07-15 19:30 | 9.97 | 9.95
2017-07-15 20:00 | 9.99 | 9.98
2017-07-15 20:30 | 9.83 | 9.82
2017-07-15 21:00 | 9.42 | 9.41
2017-07-15 21:30 | 8.84 | 8.83
2017-07-15 22:00 | 8.54 | 8.52
2017-07-15 22:30 | 8.34 | 8.33
2017-07-15 23:00 | 8.22 | 8.21
2017-07-15 23:30 | 7.49 | 7.48
2017-07-16 | 6.64 | 6.63
2017-07-16 00:30 | 5.94 | 5.93
2017-07-16 01:00 | 5.5 | 5.48
2017-07-16 01:30 | 5.1 | 5.09
2017-07-16 02:00 | 4.87 | 4.86
2017-07-16 02:30 | 4.51 | 4.5
2017-07-16 03:00 | 4.37 | 4.35
2017-07-16 03:30 | 4.27 | 4.25
2017-07-16 04:00 | 4.16 | 4.14
2017-07-16 04:30 | 4.18 | 4.17
2017-07-16 05:00 | 4.3 | 4.28
2017-07-16 05:30 | 4.5 | 4.48
2017-07-16 06:00 | 4.66 | 4.64
2017-07-16 06:30 | 4.77 | 4.75
2017-07-16 07:00 | 5.07 | 5.05
2017-07-16 07:30 | 5.62 | 5.6
2017-07-16 08:00 | 6.04 | 6.01
2017-07-16 08:30 | 6.71 | 6.69
2017-07-16 09:00 | 6.66 | 6.64
2017-07-16 09:30 | 6.09 | 6.08
2017-07-16 10:00 | 7.3 | 7.29
2017-07-16 10:30 | 6.09 | 6.07
2017-07-16 11:00 | 5.81 | 5.79
2017-07-16 11:30 | 5.89 | 5.87
2017-07-16 12:00 | 5.46 | 5.44
2017-07-16 12:30 | 5.12 | 5.1
2017-07-16 13:00 | 5.41 | 5.4
2017-07-16 13:30 | 4.71 | 4.69
2017-07-16 14:00 | 5.3 | 5.28
2017-07-16 14:30 | 5.32 | 5.3
2017-07-16 15:00 | 5.54 | 5.52
2017-07-16 15:30 | 6.08 | 6.06
2017-07-16 16:00 | 6.74 | 6.72
2017-07-16 16:30 | 7.76 | 7.74
2017-07-16 17:00 | 9.07 | 9.06
2017-07-16 17:30 | 10.12 | 10.1
2017-07-16 18:00 | 11.39 | 11.38
2017-07-16 18:30 | 11.67 | 11.66
2017-07-16 19:00 | 11.55 | 11.54
2017-07-16 19:30 | 11.11 | 11.1
2017-07-16 20:00 | 11.04 | 11.03
2017-07-16 20:30 | 11.15 | 11.14
2017-07-16 21:00 | 10.67 | 10.66
2017-07-16 21:30 | 9.88 | 9.87
2017-07-16 22:00 | 9.31 | 9.3
2017-07-16 22:30 | 8.78 | 8.77
2017-07-16 23:00 | 8.42 | 8.42
2017-07-16 23:30 | 7.56 | 7.55
2017-07-17 | 6.58 | 6.57
2017-07-17 00:30 | 5.78 | 5.77
2017-07-17 01:00 | 5.45 | 5.44
2017-07-17 01:30 | 5.11 | 5.09
2017-07-17 02:00 | 4.84 | 4.82
2017-07-17 02:30 | 4.65 | 4.64
2017-07-17 03:00 | 4.43 | 4.41
2017-07-17 03:30 | 4.51 | 4.5
2017-07-17 04:00 | 4.59 | 4.57
2017-07-17 04:30 | 4.85 | 4.83
2017-07-17 05:00 | 5.33 | 5.31
2017-07-17 05:30 | 6.16 | 6.15
2017-07-17 06:00 | 7.04 | 7.03
2017-07-17 06:30 | 8.02 | 8.01
2017-07-17 07:00 | 8.69 | 8.68
2017-07-17 07:30 | 9.15 | 9.15
2017-07-17 08:00 | 8.7 | 8.7
2017-07-17 08:30 | 7.46 | 7.46
2017-07-17 09:00 | 6.43 | 6.42
2017-07-17 09:30 | 5.95 | 5.95
2017-07-17 10:00 | 5.38 | 5.37
2017-07-17 10:30 | 4.88 | 4.87
2017-07-17 11:00 | 4.41 | 4.39
2017-07-17 11:30 | 4.16 | 4.14
2017-07-17 12:00 | 3.91 | 3.9
2017-07-17 12:30 | 4.02 | 4.01
2017-07-17 13:00 | 4.3 | 4.29
2017-07-17 13:30 | 4.27 | 4.26
2017-07-17 14:00 | 4.66 | 4.64
2017-07-17 14:30 | 4.85 | 4.84
2017-07-17 15:00 | 5.2 | 5.2
2017-07-17 15:30 | 5.64 | 5.63
2017-07-17 16:00 | 6.67 | 6.66
2017-07-17 16:30 | 7.53 | 7.52
2017-07-17 17:00 | 8.76 | 8.75
2017-07-17 17:30 | 10.38 | 10.37
2017-07-17 18:00 | 11.82 | 11.8
2017-07-17 18:30 | 12.16 | 12.13
2017-07-17 19:00 | 12.23 | 12.21
2017-07-17 19:30 | 11.86 | 11.84
2017-07-17 20:00 | 11.63 | 11.62
2017-07-17 20:30 | 11.56 | 11.55
2017-07-17 21:00 | 11.22 | 11.21
2017-07-17 21:30 | 10.49 | 10.48
2017-07-17 22:00 | 9.69 | 9.69
2017-07-17 22:30 | 8.9 | 8.89
2017-07-17 23:00 | 8.17 | 8.16
2017-07-17 23:30 | 7.2 | 7.19
2017-07-18 | 6.16 | 6.15
2017-07-18 00:30 | 5.5 | 5.49
2017-07-18 01:00 | 5.13 | 5.12
2017-07-18 01:30 | 4.77 | 4.75
2017-07-18 02:00 | 4.51 | 4.49
2017-07-18 02:30 | 4.31 | 4.3
2017-07-18 03:00 | 4.2 | 4.18
2017-07-18 03:30 | 4.25 | 4.24
2017-07-18 04:00 | 4.32 | 4.31
2017-07-18 04:30 | 4.47 | 4.46
2017-07-18 05:00 | 4.83 | 4.81
2017-07-18 05:30 | 5.65 | 5.64
2017-07-18 06:00 | 6.65 | 6.64
2017-07-18 06:30 | 7.24 | 7.23
2017-07-18 07:00 | 7.75 | 7.74
2017-07-18 07:30 | 8.39 | 8.38
2017-07-18 08:00 | 8.22 | 8.21
2017-07-18 08:30 | 7.17 | 7.16
2017-07-18 09:00 | 5.91 | 5.9
2017-07-18 09:30 | 5.21 | 5.19
2017-07-18 10:00 | 4.67 | 4.65
2017-07-18 10:30 | 4.24 | 4.22
2017-07-18 11:00 | 3.85 | 3.83
2017-07-18 11:30 | 3.75 | 3.73
2017-07-18 12:00 | 3.68 | 3.66
2017-07-18 12:30 | 3.57 | 3.55
2017-07-18 13:00 | 3.75 | 3.73
2017-07-18 13:30 | 4.02 | 4
2017-07-18 14:00 | 4.47 | 4.45
2017-07-18 14:30 | 4.9 | 4.89
2017-07-18 15:00 | 4.96 | 4.95
2017-07-18 15:30 | 5.65 | 5.64
2017-07-18 16:00 | 6.63 | 6.62
2017-07-18 16:30 | 7.58 | 7.57
2017-07-18 17:00 | 8.69 | 8.68
2017-07-18 17:30 | 9.77 | 9.76
2017-07-18 18:00 | 11.04 | 11.01
2017-07-18 18:30 | 11.61 | 11.58
2017-07-18 19:00 | 11.81 | 11.78
2017-07-18 19:30 | 11.56 | 11.54
2017-07-18 20:00 | 11.44 | 11.42
2017-07-18 20:30 | 11.48 | 11.47
2017-07-18 21:00 | 10.92 | 10.91
2017-07-18 21:30 | 10.08 | 10.07
2017-07-18 22:00 | 9.48 | 9.47
2017-07-18 22:30 | 8.57 | 8.56
2017-07-18 23:00 | 7.91 | 7.9
2017-07-18 23:30 | 6.94 | 6.93
2017-07-19 | 6.04 | 6.03
2017-07-19 00:30 | 5.29 | 5.27
2017-07-19 01:00 | 4.96 | 4.94
2017-07-19 01:30 | 4.71 | 4.69
2017-07-19 02:00 | 4.39 | 4.38
2017-07-19 02:30 | 4.14 | 4.12
2017-07-19 03:00 | 4.17 | 4.16
2017-07-19 03:30 | 4.15 | 4.13
2017-07-19 04:00 | 4.21 | 4.19
2017-07-19 04:30 | 4.25 | 4.23
2017-07-19 05:00 | 4.66 | 4.65
2017-07-19 05:30 | 5.28 | 5.27
2017-07-19 06:00 | 6.26 | 6.25
2017-07-19 06:30 | 7.12 | 7.11
2017-07-19 07:00 | 7.59 | 7.58
2017-07-19 07:30 | 8.11 | 8.1
2017-07-19 08:00 | 7.57 | 7.56
2017-07-19 08:30 | 6.32 | 6.31
2017-07-19 09:00 | 5.59 | 5.58
2017-07-19 09:30 | 5.01 | 5
2017-07-19 10:00 | 4.44 | 4.42
2017-07-19 10:30 | 3.9 | 3.88
2017-07-19 11:00 | 3.53 | 3.51
2017-07-19 11:30 | 3.4 | 3.38
2017-07-19 12:00 | 3.31 | 3.29
2017-07-19 12:30 | 3.29 | 3.28
2017-07-19 13:00 | 3.24 | 3.23
2017-07-19 13:30 | 3.33 | 3.32
2017-07-19 14:00 | 3.88 | 3.86
2017-07-19 14:30 | 5.45 | 5.44
2017-07-19 15:00 | 5.04 | 5.03
2017-07-19 15:30 | 5.83 | 5.82
2017-07-19 16:00 | 6.79 | 6.78
2017-07-19 16:30 | 7.53 | 7.52
2017-07-19 17:00 | 8.89 | 8.88
2017-07-19 17:30 | 10.5 | 10.49
2017-07-19 18:00 | 12.04 | 12.03
2017-07-19 18:30 | 12.87 | 12.85
2017-07-19 19:00 | 13.3 | 13.28
2017-07-19 19:30 | 13.16 | 13.13
2017-07-19 20:00 | 13.23 | 13.21
2017-07-19 20:30 | 13.27 | 13.25
2017-07-19 21:00 | 12.86 | 12.84
2017-07-19 21:30 | 12.01 | 12
2017-07-19 22:00 | 10.96 | 10.95
2017-07-19 22:30 | 9.91 | 9.9
2017-07-19 23:00 | 9.1 | 9.09
2017-07-19 23:30 | 7.89 | 7.88
2017-07-20 | 6.85 | 6.84
2017-07-20 00:30 | 6.17 | 6.15
2017-07-20 01:00 | 5.74 | 5.73
2017-07-20 01:30 | 5.32 | 5.31
2017-07-20 02:00 | 5.12 | 5.11
2017-07-20 02:30 | 4.8 | 4.78
2017-07-20 03:00 | 4.83 | 4.82
2017-07-20 03:30 | 4.81 | 4.79
2017-07-20 04:00 | 4.84 | 4.82
2017-07-20 04:30 | 5.17 | 5.15
2017-07-20 05:00 | 5.71 | 5.69
2017-07-20 05:30 | 6.45 | 6.44
2017-07-20 06:00 | 7.36 | 7.35
2017-07-20 06:30 | 8.15 | 8.14
2017-07-20 07:00 | 9.06 | 9.05
2017-07-20 07:30 | 9.56 | 9.55
2017-07-20 08:00 | 8.88 | 8.87
2017-07-20 08:30 | 7.34 | 7.33
2017-07-20 09:00 | 6.12 | 6.11
2017-07-20 09:30 | 5.25 | 5.24
2017-07-20 10:00 | 4.5 | 4.48
2017-07-20 10:30 | 3.99 | 3.96
2017-07-20 11:00 | 3.56 | 3.53
2017-07-20 11:30 | 3.31 | 3.29
2017-07-20 12:00 | 3.13 | 3.11
2017-07-20 12:30 | 2.96 | 2.94
2017-07-20 13:00 | 2.88 | 2.86
2017-07-20 13:30 | 3.15 | 3.13
2017-07-20 14:00 | 3.96 | 3.94
2017-07-20 14:30 | 4.27 | 4.26
2017-07-20 15:00 | 4.63 | 4.63
2017-07-20 15:30 | 5.21 | 5.2
2017-07-20 16:00 | 6.19 | 6.18
2017-07-20 16:30 | 7.13 | 7.13
2017-07-20 17:00 | 8.57 | 8.56
2017-07-20 17:30 | 9.93 | 9.92
2017-07-20 18:00 | 11.45 | 11.42
2017-07-20 18:30 | 12.25 | 12.22
2017-07-20 19:00 | 12.93 | 12.9
2017-07-20 19:30 | 12.79 | 12.76
2017-07-20 20:00 | 12.88 | 12.86
2017-07-20 20:30 | 13.14 | 13.12
2017-07-20 21:00 | 12.65 | 12.64
2017-07-20 21:30 | 11.81 | 11.8
2017-07-20 22:00 | 10.98 | 10.98
2017-07-20 22:30 | 10.18 | 10.18
2017-07-20 23:00 | 9.47 | 9.46
2017-07-20 23:30 | 8.41 | 8.4
2017-07-21 | 7.49 | 7.48
2017-07-21 00:30 | 6.72 | 6.71
2017-07-21 01:00 | 6.21 | 6.2
2017-07-21 01:30 | 5.71 | 5.7
2017-07-21 02:00 | 5.37 | 5.35
2017-07-21 02:30 | 5.15 | 5.13
2017-07-21 03:00 | 5.11 | 5.1
2017-07-21 03:30 | 5.17 | 5.15
2017-07-21 04:00 | 5.2 | 5.19
2017-07-21 04:30 | 5.63 | 5.61
2017-07-21 05:00 | 6.14 | 6.13
2017-07-21 05:30 | 7.16 | 7.15
2017-07-21 06:00 | 8.42 | 8.41
2017-07-21 06:30 | 9.17 | 9.16
2017-07-21 07:00 | 10.14 | 10.13
2017-07-21 07:30 | 10.94 | 10.93
2017-07-21 08:00 | 10.23 | 10.22
2017-07-21 08:30 | 8.56 | 8.55
2017-07-21 09:00 | 7.42 | 7.41
2017-07-21 09:30 | 6.69 | 6.68
2017-07-21 10:00 | 5.81 | 5.8
2017-07-21 10:30 | 4.88 | 4.85
2017-07-21 11:00 | 4.34 | 4.3
2017-07-21 11:30 | 3.96 | 3.92
2017-07-21 12:00 | 3.45 | 3.4
2017-07-21 12:30 | 3.19 | 3.17
2017-07-21 13:00 | 3.17 | 3.14
2017-07-21 13:30 | 3.25 | 3.21
2017-07-21 14:00 | 3.52 | 3.48
2017-07-21 14:30 | 3.8 | 3.77
2017-07-21 15:00 | 4.21 | 4.19
2017-07-21 15:30 | 4.8 | 4.77
2017-07-21 16:00 | 5.75 | 5.73
2017-07-21 16:30 | 6.91 | 6.89
2017-07-21 17:00 | 8.11 | 8.1
2017-07-21 17:30 | 9.46 | 9.45
2017-07-21 18:00 | 11 | 10.99
2017-07-21 18:30 | 11.73 | 11.72
2017-07-21 19:00 | 12.47 | 12.45
2017-07-21 19:30 | 12.26 | 12.24
2017-07-21 20:00 | 12.4 | 12.38
2017-07-21 20:30 | 12.74 | 12.72
2017-07-21 21:00 | 12.57 | 12.56
2017-07-21 21:30 | 12 | 11.99
2017-07-21 22:00 | 11.59 | 11.57
2017-07-21 22:30 | 10.97 | 10.96
2017-07-21 23:00 | 10.38 | 10.37
2017-07-21 23:30 | 9.52 | 9.51
2017-07-22 | 8.44 | 8.43
2017-07-22 00:30 | 7.44 | 7.43
2017-07-22 01:00 | 6.95 | 6.94
2017-07-22 01:30 | 6.47 | 6.46
2017-07-22 02:00 | 6.08 | 6.07
2017-07-22 02:30 | 5.85 | 5.83
2017-07-22 03:00 | 5.66 | 5.65
2017-07-22 03:30 | 5.66 | 5.65
2017-07-22 04:00 | 5.57 | 5.56
2017-07-22 04:30 | 5.71 | 5.7
2017-07-22 05:00 | 5.84 | 5.82
2017-07-22 05:30 | 6.17 | 6.15
2017-07-22 06:00 | 6.56 | 6.55
2017-07-22 06:30 | 7.09 | 7.07
2017-07-22 07:00 | 7.81 | 7.8
2017-07-22 07:30 | 8.87 | 8.86
2017-07-22 08:00 | 9.32 | 9.31
2017-07-22 08:30 | 9.27 | 9.26
2017-07-22 09:00 | 8.86 | 8.84
2017-07-22 09:30 | 7.95 | 7.93
2017-07-22 10:00 | 7.19 | 7.16
2017-07-22 10:30 | 6.34 | 6.31
2017-07-22 11:00 | 5.66 | 5.64
2017-07-22 11:30 | 5.25 | 5.23
2017-07-22 12:00 | 4.87 | 4.84
2017-07-22 12:30 | 4.63 | 4.59
2017-07-22 13:00 | 4.5 | 4.46
2017-07-22 13:30 | 4.49 | 4.46
2017-07-22 14:00 | 4.72 | 4.69
2017-07-22 14:30 | 4.91 | 4.88
2017-07-22 15:00 | 5.2 | 5.18
2017-07-22 15:30 | 5.79 | 5.77
2017-07-22 16:00 | 6.4 | 6.39
2017-07-22 16:30 | 7.15 | 7.14
2017-07-22 17:00 | 8.21 | 8.19
2017-07-22 17:30 | 9.51 | 9.5
2017-07-22 18:00 | 10.74 | 10.73
2017-07-22 18:30 | 11.28 | 11.27
2017-07-22 19:00 | 11.73 | 11.72
2017-07-22 19:30 | 11.6 | 11.59
2017-07-22 20:00 | 11.6 | 11.59
2017-07-22 20:30 | 11.79 | 11.78
2017-07-22 21:00 | 11.43 | 11.42
2017-07-22 21:30 | 11.01 | 10.99
2017-07-22 22:00 | 10.65 | 10.64
2017-07-22 22:30 | 10.27 | 10.26
2017-07-22 23:00 | 10.14 | 10.12
2017-07-22 23:30 | 9.27 | 9.26
2017-07-23 | 8.32 | 8.31
2017-07-23 00:30 | 7.37 | 7.36
2017-07-23 01:00 | 6.88 | 6.86
2017-07-23 01:30 | 6.39 | 6.38
2017-07-23 02:00 | 5.92 | 5.91
2017-07-23 02:30 | 5.7 | 5.69
2017-07-23 03:00 | 5.61 | 5.59
2017-07-23 03:30 | 5.5 | 5.49
2017-07-23 04:00 | 5.46 | 5.44
2017-07-23 04:30 | 5.45 | 5.44
2017-07-23 05:00 | 5.52 | 5.51
2017-07-23 05:30 | 5.67 | 5.65
2017-07-23 06:00 | 6.04 | 6.03
2017-07-23 06:30 | 6.36 | 6.35
2017-07-23 07:00 | 6.85 | 6.83
2017-07-23 07:30 | 7.59 | 7.58
2017-07-23 08:00 | 8.13 | 8.12
2017-07-23 08:30 | 8.23 | 8.22
2017-07-23 09:00 | 7.95 | 7.94
2017-07-23 09:30 | 7.54 | 7.52
2017-07-23 10:00 | 6.82 | 6.81
2017-07-23 10:30 | 6.25 | 6.23
2017-07-23 11:00 | 5.65 | 5.62
2017-07-23 11:30 | 5.16 | 5.13
2017-07-23 12:00 | 4.87 | 4.84
2017-07-23 12:30 | 4.54 | 4.51
2017-07-23 13:00 | 4.47 | 4.45
2017-07-23 13:30 | 4.52 | 4.49
2017-07-23 14:00 | 4.67 | 4.64
2017-07-23 14:30 | 4.97 | 4.95
2017-07-23 15:00 | 5.39 | 5.37
2017-07-23 15:30 | 5.88 | 5.87
2017-07-23 16:00 | 6.59 | 6.58
2017-07-23 16:30 | 7.63 | 7.61
2017-07-23 17:00 | 8.85 | 8.84
2017-07-23 17:30 | 10.15 | 10.14
2017-07-23 18:00 | 11.49 | 11.48
2017-07-23 18:30 | 12.15 | 12.13
2017-07-23 19:00 | 12.56 | 12.54
2017-07-23 19:30 | 12.33 | 12.31
2017-07-23 20:00 | 12.35 | 12.34
2017-07-23 20:30 | 12.65 | 12.64
2017-07-23 21:00 | 12.2 | 12.19
2017-07-23 21:30 | 11.39 | 11.38
2017-07-23 22:00 | 10.6 | 10.58
2017-07-23 22:30 | 10.1 | 10.09
2017-07-23 23:00 | 9.63 | 9.62
2017-07-23 23:30 | 8.61 | 8.6
2017-07-24 | 7.59 | 7.57
2017-07-24 00:30 | 6.84 | 6.83
2017-07-24 01:00 | 6.4 | 6.39
2017-07-24 01:30 | 5.94 | 5.92
2017-07-24 02:00 | 5.56 | 5.54
2017-07-24 02:30 | 5.34 | 5.33
2017-07-24 03:00 | 5.23 | 5.22
2017-07-24 03:30 | 5.33 | 5.32
2017-07-24 04:00 | 5.5 | 5.49
2017-07-24 04:30 | 5.83 | 5.82
2017-07-24 05:00 | 6.4 | 6.39
2017-07-24 05:30 | 7.47 | 7.47
2017-07-24 06:00 | 8.7 | 8.69
2017-07-24 06:30 | 9.7 | 9.69
2017-07-24 07:00 | 10.87 | 10.86
2017-07-24 07:30 | 11.71 | 11.7
2017-07-24 08:00 | 10.92 | 10.91
2017-07-24 08:30 | 9.19 | 9.18
2017-07-24 09:00 | 7.93 | 7.92
2017-07-24 09:30 | 7.01 | 7
2017-07-24 10:00 | 5.96 | 5.95
2017-07-24 10:30 | 6.36 | 6.35
2017-07-24 11:00 | 5.83 | 5.82
2017-07-24 11:30 | 5.39 | 5.38
2017-07-24 12:00 | 5.15 | 5.15
2017-07-24 12:30 | 4.96 | 4.96
2017-07-24 13:00 | 4.92 | 4.91
2017-07-24 13:30 | 4.7 | 4.69
2017-07-24 14:00 | 4.72 | 4.72
2017-07-24 14:30 | 4.56 | 4.55
2017-07-24 15:00 | 4.95 | 4.95
2017-07-24 15:30 | 5.44 | 5.43
2017-07-24 16:00 | 6.46 | 6.45
2017-07-24 16:30 | 7.55 | 7.54
2017-07-24 17:00 | 8.72 | 8.71
2017-07-24 17:30 | 10.23 | 10.23
2017-07-24 18:00 | 12.02 | 12.01
2017-07-24 18:30 | 12.77 | 12.75
2017-07-24 19:00 | 13.16 | 13.14
2017-07-24 19:30 | 12.84 | 12.82
2017-07-24 20:00 | 13.02 | 13
2017-07-24 20:30 | 13.23 | 13.22
2017-07-24 21:00 | 12.73 | 12.72
2017-07-24 21:30 | 11.96 | 11.95
2017-07-24 22:00 | 11.11 | 11.1
2017-07-24 22:30 | 10.19 | 10.18
2017-07-24 23:00 | 9.38 | 9.36
2017-07-24 23:30 | 8.27 | 8.25
2017-07-25 | 7.23 | 7.22
2017-07-25 00:30 | 6.5 | 6.49
2017-07-25 01:00 | 6.01 | 6
2017-07-25 01:30 | 5.63 | 5.62
2017-07-25 02:00 | 5.43 | 5.42
2017-07-25 02:30 | 5.13 | 5.11
2017-07-25 03:00 | 5.08 | 5.07
2017-07-25 03:30 | 5.19 | 5.18
2017-07-25 04:00 | 5.3 | 5.29
2017-07-25 04:30 | 5.67 | 5.66
2017-07-25 05:00 | 6.26 | 6.25
2017-07-25 05:30 | 7.19 | 7.17
2017-07-25 06:00 | 8.21 | 8.19
2017-07-25 06:30 | 9.24 | 9.23
2017-07-25 07:00 | 10.62 | 10.62
2017-07-25 07:30 | 11.52 | 11.52
2017-07-25 08:00 | 10.7 | 10.69
2017-07-25 08:30 | 8.83 | 8.83
2017-07-25 09:00 | 7.32 | 7.31
2017-07-25 09:30 | 6.41 | 6.4
2017-07-25 10:00 | 5.55 | 5.53
2017-07-25 10:30 | 5.02 | 5
2017-07-25 11:00 | 4.25 | 4.23
2017-07-25 11:30 | 3.93 | 3.91
2017-07-25 12:00 | 3.86 | 3.84
2017-07-25 12:30 | 3.74 | 3.72
2017-07-25 13:00 | 3.66 | 3.64
2017-07-25 13:30 | 3.7 | 3.69
2017-07-25 14:00 | 4.03 | 4.02
2017-07-25 14:30 | 4.33 | 4.32
2017-07-25 15:00 | 4.62 | 4.61
2017-07-25 15:30 | 5.23 | 5.23
2017-07-25 16:00 | 6.28 | 6.27
2017-07-25 16:30 | 7.47 | 7.46
2017-07-25 17:00 | 8.78 | 8.77
2017-07-25 17:30 | 10.22 | 10.21
2017-07-25 18:00 | 11.99 | 11.97
2017-07-25 18:30 | 12.89 | 12.87
2017-07-25 19:00 | 13.49 | 13.46
2017-07-25 19:30 | 13.37 | 13.35
2017-07-25 20:00 | 13.53 | 13.51
2017-07-25 20:30 | 13.68 | 13.66
2017-07-25 21:00 | 13.19 | 13.17
2017-07-25 21:30 | 12.18 | 12.17
2017-07-25 22:00 | 11.43 | 11.42
2017-07-25 22:30 | 10.27 | 10.27
2017-07-25 23:00 | 9.55 | 9.54
2017-07-25 23:30 | 8.51 | 8.5
2017-07-26 | 7.55 | 7.54
2017-07-26 00:30 | 6.71 | 6.7
2017-07-26 01:00 | 6.29 | 6.28
2017-07-26 01:30 | 5.87 | 5.86
2017-07-26 02:00 | 5.56 | 5.55
2017-07-26 02:30 | 5.35 | 5.34
2017-07-26 03:00 | 5.33 | 5.32
2017-07-26 03:30 | 5.41 | 5.4
2017-07-26 04:00 | 5.51 | 5.5
2017-07-26 04:30 | 5.95 | 5.94
2017-07-26 05:00 | 6.49 | 6.47
2017-07-26 05:30 | 7.45 | 7.44
2017-07-26 06:00 | 8.54 | 8.53
2017-07-26 06:30 | 9.88 | 9.87
2017-07-26 07:00 | 10.94 | 10.94
2017-07-26 07:30 | 11.44 | 11.43
2017-07-26 08:00 | 10.35 | 10.34
2017-07-26 08:30 | 8.82 | 8.81
2017-07-26 09:00 | 7.66 | 7.65
2017-07-26 09:30 | 6.67 | 6.65
2017-07-26 10:00 | 5.66 | 5.64
2017-07-26 10:30 | 4.95 | 4.93
2017-07-26 11:00 | 4.46 | 4.45
2017-07-26 11:30 | 4.05 | 4.03
2017-07-26 12:00 | 3.88 | 3.86
2017-07-26 12:30 | 3.84 | 3.83
2017-07-26 13:00 | 3.76 | 3.75
2017-07-26 13:30 | 3.86 | 3.85
2017-07-26 14:00 | 4.06 | 4.04
2017-07-26 14:30 | 4.34 | 4.33
2017-07-26 15:00 | 4.66 | 4.64
2017-07-26 15:30 | 5.4 | 5.38
2017-07-26 16:00 | 6.41 | 6.4
2017-07-26 16:30 | 7.29 | 7.28
2017-07-26 17:00 | 8.52 | 8.52
2017-07-26 17:30 | 9.81 | 9.8
2017-07-26 18:00 | 11.42 | 11.4
2017-07-26 18:30 | 12.15 | 12.12
2017-07-26 19:00 | 12.66 | 12.64
2017-07-26 19:30 | 12.6 | 12.58
2017-07-26 20:00 | 12.69 | 12.67
2017-07-26 20:30 | 13.02 | 13.01
2017-07-26 21:00 | 12.6 | 12.59
2017-07-26 21:30 | 11.72 | 11.71
2017-07-26 22:00 | 10.95 | 10.94
2017-07-26 22:30 | 10 | 9.99
2017-07-26 23:00 | 9.27 | 9.26
2017-07-26 23:30 | 8.07 | 8.06
2017-07-27 | 7.18 | 7.17
2017-07-27 00:30 | 6.49 | 6.48
2017-07-27 01:00 | 6.09 | 6.07
2017-07-27 01:30 | 5.69 | 5.68
2017-07-27 02:00 | 5.36 | 5.35
2017-07-27 02:30 | 5.14 | 5.13
2017-07-27 03:00 | 5.08 | 5.06
2017-07-27 03:30 | 5.09 | 5.07
2017-07-27 04:00 | 5.08 | 5.06
2017-07-27 04:30 | 5.45 | 5.43
2017-07-27 05:00 | 6.06 | 6.04
2017-07-27 05:30 | 7.1 | 7.08
2017-07-27 06:00 | 8.41 | 8.41
2017-07-27 06:30 | 9.3 | 9.3
2017-07-27 07:00 | 10.3 | 10.3
2017-07-27 07:30 | 10.93 | 10.92
2017-07-27 08:00 | 10.29 | 10.28
2017-07-27 08:30 | 8.75 | 8.74
2017-07-27 09:00 | 7.34 | 7.33
2017-07-27 09:30 | 6.49 | 6.48
2017-07-27 10:00 | 5.55 | 5.54
2017-07-27 10:30 | 4.88 | 4.87
2017-07-27 11:00 | 4.46 | 4.45
2017-07-27 11:30 | 3.98 | 3.97
2017-07-27 12:00 | 3.59 | 3.57
2017-07-27 12:30 | 3.73 | 3.72
2017-07-27 13:00 | 3.46 | 3.45
2017-07-27 13:30 | 3.53 | 3.52
2017-07-27 14:00 | 3.94 | 3.93
2017-07-27 14:30 | 4.35 | 4.33
2017-07-27 15:00 | 4.71 | 4.69
2017-07-27 15:30 | 5.4 | 5.38
2017-07-27 16:00 | 6.37 | 6.35
2017-07-27 16:30 | 7.45 | 7.44
2017-07-27 17:00 | 8.5 | 8.49
2017-07-27 17:30 | 9.74 | 9.74
2017-07-27 18:00 | 11.22 | 11.2
2017-07-27 18:30 | 11.84 | 11.82
2017-07-27 19:00 | 12.24 | 12.22
2017-07-27 19:30 | 12.16 | 12.14
2017-07-27 20:00 | 12.27 | 12.25
2017-07-27 20:30 | 12.55 | 12.54
2017-07-27 21:00 | 12.29 | 12.28
2017-07-27 21:30 | 11.66 | 11.65
2017-07-27 22:00 | 11.01 | 11
2017-07-27 22:30 | 10 | 9.99
2017-07-27 23:00 | 9.36 | 9.35
2017-07-27 23:30 | 8.2 | 8.19
2017-07-28 | 7.18 | 7.17
2017-07-28 00:30 | 6.36 | 6.34
2017-07-28 01:00 | 5.91 | 5.9
2017-07-28 01:30 | 5.54 | 5.53
2017-07-28 02:00 | 5.35 | 5.34
2017-07-28 02:30 | 5.12 | 5.1
2017-07-28 03:00 | 5 | 4.99
2017-07-28 03:30 | 5.16 | 5.15
2017-07-28 04:00 | 5.2 | 5.18
2017-07-28 04:30 | 5.46 | 5.44
2017-07-28 05:00 | 5.93 | 5.91
2017-07-28 05:30 | 6.71 | 6.7
2017-07-28 06:00 | 7.42 | 7.41
2017-07-28 06:30 | 8.34 | 8.33
2017-07-28 07:00 | 9.28 | 9.28
2017-07-28 07:30 | 10.07 | 10.06
2017-07-28 08:00 | 9.21 | 9.2
2017-07-28 08:30 | 7.52 | 7.51
2017-07-28 09:00 | 6.64 | 6.63
2017-07-28 09:30 | 5.71 | 5.69
2017-07-28 10:00 | 4.98 | 4.96
2017-07-28 10:30 | 4.61 | 4.6
2017-07-28 11:00 | 4.02 | 4.01
2017-07-28 11:30 | 3.43 | 3.41
2017-07-28 12:00 | 3.26 | 3.24
2017-07-28 12:30 | 3.12 | 3.1
2017-07-28 13:00 | 3.26 | 3.24
2017-07-28 13:30 | 3.61 | 3.58
2017-07-28 14:00 | 3.49 | 3.47
2017-07-28 14:30 | 3.81 | 3.78
2017-07-28 15:00 | 4.2 | 4.18
2017-07-28 15:30 | 4.77 | 4.75
2017-07-28 16:00 | 5.67 | 5.65
2017-07-28 16:30 | 6.72 | 6.7
2017-07-28 17:00 | 7.7 | 7.69
2017-07-28 17:30 | 8.69 | 8.68
2017-07-28 18:00 | 9.85 | 9.83
2017-07-28 18:30 | 10.39 | 10.38
2017-07-28 19:00 | 10.83 | 10.81
2017-07-28 19:30 | 10.7 | 10.68
2017-07-28 20:00 | 10.65 | 10.64
2017-07-28 20:30 | 10.79 | 10.78
2017-07-28 21:00 | 10.6 | 10.6
2017-07-28 21:30 | 10.08 | 10.07
2017-07-28 22:00 | 9.6 | 9.59
2017-07-28 22:30 | 9.2 | 9.19
2017-07-28 23:00 | 8.93 | 8.91
2017-07-28 23:30 | 8.12 | 8.1
2017-07-29 | 7.23 | 7.21
2017-07-29 00:30 | 6.41 | 6.4
2017-07-29 01:00 | 5.95 | 5.94
2017-07-29 01:30 | 5.54 | 5.53
2017-07-29 02:00 | 5.19 | 5.17
2017-07-29 02:30 | 4.96 | 4.94
2017-07-29 03:00 | 4.88 | 4.87
2017-07-29 03:30 | 4.84 | 4.82
2017-07-29 04:00 | 4.8 | 4.78
2017-07-29 04:30 | 4.97 | 4.95
2017-07-29 05:00 | 5.08 | 5.06
2017-07-29 05:30 | 5.4 | 5.39
2017-07-29 06:00 | 5.72 | 5.71
2017-07-29 06:30 | 6.08 | 6.07
2017-07-29 07:00 | 6.91 | 6.89
2017-07-29 07:30 | 7.57 | 7.56
2017-07-29 08:00 | 7.7 | 7.69
2017-07-29 08:30 | 7.65 | 7.64
2017-07-29 09:00 | 7.13 | 7.11
2017-07-29 09:30 | 6.62 | 6.6
2017-07-29 10:00 | 5.82 | 5.79
2017-07-29 10:30 | 5.21 | 5.18
2017-07-29 11:00 | 4.64 | 4.61
2017-07-29 11:30 | 4.38 | 4.34
2017-07-29 12:00 | 4.08 | 4.05
2017-07-29 12:30 | 3.9 | 3.87
2017-07-29 13:00 | 3.86 | 3.82
2017-07-29 13:30 | 4.04 | 4
2017-07-29 14:00 | 4.16 | 4.13
2017-07-29 14:30 | 4.41 | 4.38
2017-07-29 15:00 | 4.67 | 4.64
2017-07-29 15:30 | 5.3 | 5.28
2017-07-29 16:00 | 6.06 | 6.04
2017-07-29 16:30 | 6.86 | 6.84
2017-07-29 17:00 | 7.92 | 7.91
2017-07-29 17:30 | 8.94 | 8.92
2017-07-29 18:00 | 10.04 | 10.03
2017-07-29 18:30 | 10.43 | 10.42
2017-07-29 19:00 | 10.6 | 10.58
2017-07-29 19:30 | 10.4 | 10.39
2017-07-29 20:00 | 10.38 | 10.37
2017-07-29 20:30 | 10.62 | 10.61
2017-07-29 21:00 | 10.35 | 10.34
2017-07-29 21:30 | 9.9 | 9.89
2017-07-29 22:00 | 9.4 | 9.39
2017-07-29 22:30 | 9.29 | 9.28
2017-07-29 23:00 | 9.11 | 9.1
2017-07-29 23:30 | 8.39 | 8.38
2017-07-30 | 7.52 | 7.51
2017-07-30 00:30 | 6.78 | 6.77
2017-07-30 01:00 | 6.3 | 6.29
2017-07-30 01:30 | 5.81 | 5.79
2017-07-30 02:00 | 5.55 | 5.54
2017-07-30 02:30 | 5.26 | 5.25
2017-07-30 03:00 | 5.15 | 5.14
2017-07-30 03:30 | 5.09 | 5.08
2017-07-30 04:00 | 5.02 | 5.01
2017-07-30 04:30 | 5.05 | 5.04
2017-07-30 05:00 | 5.2 | 5.18
2017-07-30 05:30 | 5.44 | 5.42
2017-07-30 06:00 | 5.74 | 5.73
2017-07-30 06:30 | 6.05 | 6.03
2017-07-30 07:00 | 6.69 | 6.67
2017-07-30 07:30 | 7.29 | 7.28
2017-07-30 08:00 | 7.67 | 7.66
2017-07-30 08:30 | 7.89 | 7.88
2017-07-30 09:00 | 7.67 | 7.66
2017-07-30 09:30 | 7.16 | 7.15
2017-07-30 10:00 | 6.36 | 6.35
2017-07-30 10:30 | 5.7 | 5.68
2017-07-30 11:00 | 5.28 | 5.26
2017-07-30 11:30 | 4.96 | 4.93
2017-07-30 12:00 | 4.57 | 4.54
2017-07-30 12:30 | 4.39 | 4.36
2017-07-30 13:00 | 4.28 | 4.26
2017-07-30 13:30 | 4.27 | 4.24
2017-07-30 14:00 | 4.39 | 4.36
2017-07-30 14:30 | 4.71 | 4.68
2017-07-30 15:00 | 5.06 | 5.04
2017-07-30 15:30 | 5.7 | 5.68
2017-07-30 16:00 | 6.42 | 6.4
2017-07-30 16:30 | 7.35 | 7.34
2017-07-30 17:00 | 8.56 | 8.55
2017-07-30 17:30 | 9.88 | 9.86
2017-07-30 18:00 | 10.99 | 10.97
2017-07-30 18:30 | 11.36 | 11.35
2017-07-30 19:00 | 11.47 | 11.46
2017-07-30 19:30 | 11.16 | 11.16
2017-07-30 20:00 | 11.01 | 11
2017-07-30 20:30 | 10.93 | 10.92
2017-07-30 21:00 | 10.49 | 10.49
2017-07-30 21:30 | 9.7 | 9.69
2017-07-30 22:00 | 8.96 | 8.95
2017-07-30 22:30 | 8.58 | 8.57
2017-07-30 23:00 | 8.32 | 8.31
2017-07-30 23:30 | 7.5 | 7.49
2017-07-31 | 6.59 | 6.58
2017-07-31 00:30 | 5.81 | 5.8
2017-07-31 01:00 | 5.46 | 5.45
2017-07-31 01:30 | 5.02 | 5.01
2017-07-31 02:00 | 4.7 | 4.68
2017-07-31 02:30 | 4.49 | 4.47
2017-07-31 03:00 | 4.4 | 4.38
2017-07-31 03:30 | 4.5 | 4.48
2017-07-31 04:00 | 4.53 | 4.51
2017-07-31 04:30 | 4.65 | 4.63
2017-07-31 05:00 | 5.15 | 5.14
2017-07-31 05:30 | 5.91 | 5.89
2017-07-31 06:00 | 6.53 | 6.51
2017-07-31 06:30 | 7.21 | 7.2
2017-07-31 07:00 | 7.95 | 7.94
2017-07-31 07:30 | 8.4 | 8.39
2017-07-31 08:00 | 7.9 | 7.89
2017-07-31 08:30 | 6.89 | 6.88
2017-07-31 09:00 | 5.57 | 5.56
2017-07-31 09:30 | 4.95 | 4.94
2017-07-31 10:00 | 4.35 | 4.33
2017-07-31 10:30 | 4.23 | 4.22
2017-07-31 11:00 | 3.94 | 3.93
2017-07-31 11:30 | 3.69 | 3.68
2017-07-31 12:00 | 3.49 | 3.47
2017-07-31 12:30 | 3.5 | 3.48
2017-07-31 13:00 | 3.46 | 3.45
2017-07-31 13:30 | 3.69 | 3.68
2017-07-31 14:00 | 4.12 | 4.11
2017-07-31 14:30 | 4.56 | 4.54
2017-07-31 15:00 | 4.87 | 4.85
2017-07-31 15:30 | 5.58 | 5.57
2017-07-31 16:00 | 6.53 | 6.52
2017-07-31 16:30 | 7.49 | 7.48
2017-07-31 17:00 | 8.77 | 8.77
2017-07-31 17:30 | 9.99 | 9.98
2017-07-31 18:00 | 11.39 | 11.37
2017-07-31 18:30 | 11.89 | 11.87
2017-07-31 19:00 | 12.14 | 12.12
2017-07-31 19:30 | 11.83 | 11.82
2017-07-31 20:00 | 11.65 | 11.64
2017-07-31 20:30 | 11.8 | 11.79
2017-07-31 21:00 | 11.18 | 11.18
2017-07-31 21:30 | 10.25 | 10.25
2017-07-31 22:00 | 9.52 | 9.51
2017-07-31 22:30 | 8.71 | 8.69
2017-07-31 23:00 | 8.21 | 8.19
2017-07-31 23:30 | 7.2 | 7.19
2017-08-01 | 6.4 | 6.39
2017-08-01 00:30 | 5.61 | 5.59
2017-08-01 01:00 | 5.29 | 5.28
2017-08-01 01:30 | 4.9 | 4.88
2017-08-01 02:00 | 4.62 | 4.6
2017-08-01 02:30 | 4.5 | 4.48
2017-08-01 03:00 | 4.4 | 4.38
2017-08-01 03:30 | 4.52 | 4.5
2017-08-01 04:00 | 4.52 | 4.5
2017-08-01 04:30 | 4.81 | 4.79
2017-08-01 05:00 | 5.26 | 5.24
2017-08-01 05:30 | 6.05 | 6.04
2017-08-01 06:00 | 7.2 | 7.19
2017-08-01 06:30 | 8.25 | 8.25
2017-08-01 07:00 | 9.11 | 9.1
2017-08-01 07:30 | 9.72 | 9.71
2017-08-01 08:00 | 9.02 | 9.01
2017-08-01 08:30 | 7.53 | 7.52
2017-08-01 09:00 | 6.22 | 6.21
2017-08-01 09:30 | 5.49 | 5.48
2017-08-01 10:00 | 4.82 | 4.8
2017-08-01 10:30 | 4.36 | 4.35
2017-08-01 11:00 | 3.86 | 3.84
2017-08-01 11:30 | 3.68 | 3.66
2017-08-01 12:00 | 3.45 | 3.43
2017-08-01 12:30 | 3.32 | 3.31
2017-08-01 13:00 | 3.36 | 3.35
2017-08-01 13:30 | 3.62 | 3.6
2017-08-01 14:00 | 3.94 | 3.92
2017-08-01 14:30 | 4.2 | 4.18
2017-08-01 15:00 | 4.51 | 4.5
2017-08-01 15:30 | 5.19 | 5.18
2017-08-01 16:00 | 6.42 | 6.41
2017-08-01 16:30 | 7.47 | 7.46
2017-08-01 17:00 | 8.66 | 8.66
2017-08-01 17:30 | 9.93 | 9.93
2017-08-01 18:00 | 11.32 | 11.31
2017-08-01 18:30 | 12.1 | 12.07
2017-08-01 19:00 | 12.53 | 12.51
2017-08-01 19:30 | 12.35 | 12.33
2017-08-01 20:00 | 12.26 | 12.24
2017-08-01 20:30 | 12.43 | 12.42
2017-08-01 21:00 | 12.11 | 12.1
2017-08-01 21:30 | 11.35 | 11.34
2017-08-01 22:00 | 10.49 | 10.49
2017-08-01 22:30 | 9.47 | 9.46
2017-08-01 23:00 | 8.82 | 8.81
2017-08-01 23:30 | 7.79 | 7.78
2017-08-02 | 6.88 | 6.87
2017-08-02 00:30 | 6.09 | 6.08
2017-08-02 01:00 | 5.69 | 5.68
2017-08-02 01:30 | 5.33 | 5.32
2017-08-02 02:00 | 5.08 | 5.07
2017-08-02 02:30 | 4.92 | 4.9
2017-08-02 03:00 | 4.81 | 4.79
2017-08-02 03:30 | 4.94 | 4.92
2017-08-02 04:00 | 5.04 | 5.02
2017-08-02 04:30 | 5.38 | 5.37
2017-08-02 05:00 | 5.88 | 5.86
2017-08-02 05:30 | 6.85 | 6.84
2017-08-02 06:00 | 7.67 | 7.66
2017-08-02 06:30 | 9.07 | 9.06
2017-08-02 07:00 | 10.1 | 10.09
2017-08-02 07:30 | 10.6 | 10.6
2017-08-02 08:00 | 9.99 | 9.98
2017-08-02 08:30 | 9.44 | 9.44
2017-08-02 09:00 | 8.46 | 8.45
2017-08-02 09:30 | 7.5 | 7.5
2017-08-02 10:00 | 6.76 | 6.75
2017-08-02 10:30 | 6.15 | 6.14
2017-08-02 11:00 | 5.58 | 5.57
2017-08-02 11:30 | 5.15 | 5.14
2017-08-02 12:00 | 5.21 | 5.2
2017-08-02 12:30 | 5.05 | 5.05
2017-08-02 13:00 | 5.1 | 5.09
2017-08-02 13:30 | 5.26 | 5.25
2017-08-02 14:00 | 5.46 | 5.46
2017-08-02 14:30 | 5.52 | 5.51
2017-08-02 15:00 | 4.68 | 4.67
2017-08-02 15:30 | 5.3 | 5.29
2017-08-02 16:00 | 6.33 | 6.32
2017-08-02 16:30 | 7.37 | 7.36
2017-08-02 17:00 | 8.64 | 8.63
2017-08-02 17:30 | 10.02 | 10.02
2017-08-02 18:00 | 11.45 | 11.44
2017-08-02 18:30 | 12.19 | 12.17
2017-08-02 19:00 | 12.75 | 12.73
2017-08-02 19:30 | 12.8 | 12.78
2017-08-02 20:00 | 12.83 | 12.81
2017-08-02 20:30 | 12.9 | 12.89
2017-08-02 21:00 | 12.5 | 12.49
2017-08-02 21:30 | 11.62 | 11.61
2017-08-02 22:00 | 10.53 | 10.53
2017-08-02 22:30 | 9.49 | 9.48
2017-08-02 23:00 | 8.78 | 8.77
2017-08-02 23:30 | 7.8 | 7.79
2017-08-03 | 6.73 | 6.72
2017-08-03 00:30 | 6.03 | 6.01
2017-08-03 01:00 | 5.68 | 5.67
2017-08-03 01:30 | 5.34 | 5.33
2017-08-03 02:00 | 4.99 | 4.98
2017-08-03 02:30 | 4.88 | 4.87
2017-08-03 03:00 | 4.75 | 4.73
2017-08-03 03:30 | 4.77 | 4.76
2017-08-03 04:00 | 4.83 | 4.81
2017-08-03 04:30 | 5.21 | 5.19
2017-08-03 05:00 | 5.64 | 5.62
2017-08-03 05:30 | 6.49 | 6.47
2017-08-03 06:00 | 7.16 | 7.15
2017-08-03 06:30 | 8.2 | 8.19
2017-08-03 07:00 | 9.12 | 9.11
2017-08-03 07:30 | 9.64 | 9.63
2017-08-03 08:00 | 8.94 | 8.93
2017-08-03 08:30 | 8.12 | 8.11
2017-08-03 09:00 | 6.45 | 6.43
2017-08-03 09:30 | 5.32 | 5.3
2017-08-03 10:00 | 4.94 | 4.92
2017-08-03 10:30 | 4.44 | 4.41
2017-08-03 11:00 | 3.79 | 3.75
2017-08-03 11:30 | 3.76 | 3.73
2017-08-03 12:00 | 3.4 | 3.37
2017-08-03 12:30 | 4.86 | 4.85
2017-08-03 13:00 | 4.73 | 4.72
2017-08-03 13:30 | 4.99 | 4.98
2017-08-03 14:00 | 4.77 | 4.76
2017-08-03 14:30 | 5.24 | 5.23
2017-08-03 15:00 | 5.34 | 5.33
2017-08-03 15:30 | 5.92 | 5.91
2017-08-03 16:00 | 6.41 | 6.4
2017-08-03 16:30 | 7.43 | 7.43
2017-08-03 17:00 | 8.59 | 8.58
2017-08-03 17:30 | 9.79 | 9.79
2017-08-03 18:00 | 11.21 | 11.2
2017-08-03 18:30 | 11.94 | 11.92
2017-08-03 19:00 | 12.29 | 12.26
2017-08-03 19:30 | 12.1 | 12.08
2017-08-03 20:00 | 12.2 | 12.18
2017-08-03 20:30 | 12.28 | 12.27
2017-08-03 21:00 | 11.97 | 11.96
2017-08-03 21:30 | 11.04 | 11.04
2017-08-03 22:00 | 10.26 | 10.25
2017-08-03 22:30 | 9.36 | 9.35
2017-08-03 23:00 | 8.62 | 8.61
2017-08-03 23:30 | 7.62 | 7.61
2017-08-04 | 6.58 | 6.56
2017-08-04 00:30 | 5.9 | 5.88
2017-08-04 01:00 | 5.52 | 5.5
2017-08-04 01:30 | 5.15 | 5.13
2017-08-04 02:00 | 4.77 | 4.75
2017-08-04 02:30 | 4.62 | 4.6
2017-08-04 03:00 | 4.42 | 4.4
2017-08-04 03:30 | 4.61 | 4.59
2017-08-04 04:00 | 4.73 | 4.71
2017-08-04 04:30 | 4.91 | 4.89
2017-08-04 05:00 | 5.11 | 5.09
2017-08-04 05:30 | 5.72 | 5.71
2017-08-04 06:00 | 6.46 | 6.44
2017-08-04 06:30 | 7.58 | 7.58
2017-08-04 07:00 | 8.32 | 8.32
2017-08-04 07:30 | 8.72 | 8.71
2017-08-04 08:00 | 8.01 | 8
2017-08-04 08:30 | 8.13 | 8.12
2017-08-04 09:00 | 7.1 | 7.09
2017-08-04 09:30 | 6.52 | 6.51
2017-08-04 10:00 | 5.95 | 5.94
2017-08-04 10:30 | 4.11 | 4.09
2017-08-04 11:00 | 3.04 | 3.01
2017-08-04 11:30 | 2.72 | 2.69
2017-08-04 12:00 | 2.52 | 2.49
2017-08-04 12:30 | 2.55 | 2.52
2017-08-04 13:00 | 2.58 | 2.55
2017-08-04 13:30 | 2.78 | 2.75
2017-08-04 14:00 | 3.11 | 3.08
2017-08-04 14:30 | 3.45 | 3.43
2017-08-04 15:00 | 3.83 | 3.81
2017-08-04 15:30 | 4.41 | 4.39
2017-08-04 16:00 | 5.26 | 5.25
2017-08-04 16:30 | 6.29 | 6.28
2017-08-04 17:00 | 7.51 | 7.5
2017-08-04 17:30 | 8.35 | 8.34
2017-08-04 18:00 | 9.35 | 9.34
2017-08-04 18:30 | 10.06 | 10.05
2017-08-04 19:00 | 10.57 | 10.55
2017-08-04 19:30 | 10.59 | 10.57
2017-08-04 20:00 | 10.65 | 10.64
2017-08-04 20:30 | 10.64 | 10.63
2017-08-04 21:00 | 10.32 | 10.3
2017-08-04 21:30 | 9.9 | 9.89
2017-08-04 22:00 | 9.52 | 9.51
2017-08-04 22:30 | 9.26 | 9.25
2017-08-04 23:00 | 9.02 | 9
2017-08-04 23:30 | 8.2 | 8.19
2017-08-05 | 7.21 | 7.2
2017-08-05 00:30 | 6.53 | 6.51
2017-08-05 01:00 | 6.14 | 6.13
2017-08-05 01:30 | 5.75 | 5.74
2017-08-05 02:00 | 5.34 | 5.32
2017-08-05 02:30 | 5.13 | 5.12
2017-08-05 03:00 | 4.92 | 4.91
2017-08-05 03:30 | 4.95 | 4.94
2017-08-05 04:00 | 5.03 | 5.01
2017-08-05 04:30 | 5.07 | 5.05
2017-08-05 05:00 | 5.26 | 5.24
2017-08-05 05:30 | 5.5 | 5.48
2017-08-05 06:00 | 5.71 | 5.7
2017-08-05 06:30 | 6.23 | 6.21
2017-08-05 07:00 | 7.05 | 7.03
2017-08-05 07:30 | 7.65 | 7.64
2017-08-05 08:00 | 7.67 | 7.65
2017-08-05 08:30 | 7.43 | 7.42
2017-08-05 09:00 | 6.88 | 6.86
2017-08-05 09:30 | 6.39 | 6.37
2017-08-05 10:00 | 5.75 | 5.73
2017-08-05 10:30 | 5.06 | 5.04
2017-08-05 11:00 | 4.5 | 4.47
2017-08-05 11:30 | 4.11 | 4.08
2017-08-05 12:00 | 3.8 | 3.76
2017-08-05 12:30 | 3.62 | 3.58
2017-08-05 13:00 | 3.54 | 3.51
2017-08-05 13:30 | 3.65 | 3.61
2017-08-05 14:00 | 3.85 | 3.82
2017-08-05 14:30 | 4.22 | 4.19
2017-08-05 15:00 | 4.53 | 4.51
2017-08-05 15:30 | 5.05 | 5.03
2017-08-05 16:00 | 5.73 | 5.71
2017-08-05 16:30 | 6.6 | 6.58
2017-08-05 17:00 | 7.67 | 7.65
2017-08-05 17:30 | 8.54 | 8.53
2017-08-05 18:00 | 9.65 | 9.64
2017-08-05 18:30 | 10.17 | 10.16
2017-08-05 19:00 | 10.5 | 10.48
2017-08-05 19:30 | 10.44 | 10.42
2017-08-05 20:00 | 10.62 | 10.6
2017-08-05 20:30 | 10.81 | 10.8
2017-08-05 21:00 | 10.74 | 10.73
2017-08-05 21:30 | 10.22 | 10.21
2017-08-05 22:00 | 9.76 | 9.75
2017-08-05 22:30 | 9.57 | 9.56
2017-08-05 23:00 | 9.36 | 9.35
2017-08-05 23:30 | 8.57 | 8.56
2017-08-06 | 7.76 | 7.75
2017-08-06 00:30 | 6.92 | 6.91
2017-08-06 01:00 | 6.43 | 6.41
2017-08-06 01:30 | 6.06 | 6.05
2017-08-06 02:00 | 5.54 | 5.52
2017-08-06 02:30 | 5.32 | 5.31
2017-08-06 03:00 | 5.13 | 5.11
2017-08-06 03:30 | 5.16 | 5.15
2017-08-06 04:00 | 5.08 | 5.07
2017-08-06 04:30 | 5.21 | 5.19
2017-08-06 05:00 | 5.28 | 5.26
2017-08-06 05:30 | 5.43 | 5.41
2017-08-06 06:00 | 5.67 | 5.66
2017-08-06 06:30 | 6.02 | 6
2017-08-06 07:00 | 6.65 | 6.63
2017-08-06 07:30 | 7.36 | 7.35
2017-08-06 08:00 | 7.91 | 7.9
2017-08-06 08:30 | 8.1 | 8.09
2017-08-06 09:00 | 7.72 | 7.71
2017-08-06 09:30 | 7.1 | 7.09
2017-08-06 10:00 | 6.25 | 6.23
2017-08-06 10:30 | 5.74 | 5.72
2017-08-06 11:00 | 5.14 | 5.12
2017-08-06 11:30 | 5.77 | 5.75
2017-08-06 12:00 | 7.11 | 7.1
2017-08-06 12:30 | 5.8 | 5.78
2017-08-06 13:00 | 4.79 | 4.76
2017-08-06 13:30 | 4.5 | 4.47
2017-08-06 14:00 | 4.6 | 4.57
2017-08-06 14:30 | 4.85 | 4.82
2017-08-06 15:00 | 6.13 | 6.11
2017-08-06 15:30 | 6.89 | 6.87
2017-08-06 16:00 | 7.15 | 7.14
2017-08-06 16:30 | 8.12 | 8.11
2017-08-06 17:00 | 9.47 | 9.46
2017-08-06 17:30 | 10.55 | 10.54
2017-08-06 18:00 | 11.49 | 11.48
2017-08-06 18:30 | 11.47 | 11.46
2017-08-06 19:00 | 11.3 | 11.29
2017-08-06 19:30 | 10.94 | 10.93
2017-08-06 20:00 | 10.76 | 10.75
2017-08-06 20:30 | 10.62 | 10.61
2017-08-06 21:00 | 10.14 | 10.13
2017-08-06 21:30 | 9.33 | 9.32
2017-08-06 22:00 | 8.74 | 8.72
2017-08-06 22:30 | 8.23 | 8.21
2017-08-06 23:00 | 7.91 | 7.9
2017-08-06 23:30 | 7.04 | 7.03
2017-08-07 | 6.23 | 6.22
2017-08-07 00:30 | 5.49 | 5.47
2017-08-07 01:00 | 5 | 4.99
2017-08-07 01:30 | 4.69 | 4.67
2017-08-07 02:00 | 4.4 | 4.38
2017-08-07 02:30 | 4.12 | 4.1
2017-08-07 03:00 | 4.01 | 3.99
2017-08-07 03:30 | 4.21 | 4.19
2017-08-07 04:00 | 4.28 | 4.26
2017-08-07 04:30 | 4.52 | 4.5
2017-08-07 05:00 | 4.71 | 4.7
2017-08-07 05:30 | 5.59 | 5.58
2017-08-07 06:00 | 6.68 | 6.68
2017-08-07 06:30 | 7.62 | 7.62
2017-08-07 07:00 | 9.04 | 9.04
2017-08-07 07:30 | 9.44 | 9.43
2017-08-07 08:00 | 8.94 | 8.94
2017-08-07 08:30 | 8.12 | 8.11
2017-08-07 09:00 | 7.09 | 7.08
2017-08-07 09:30 | 6.84 | 6.83
2017-08-07 10:00 | 6.09 | 6.09
2017-08-07 10:30 | 5.75 | 5.74
2017-08-07 11:00 | 5.63 | 5.62
2017-08-07 11:30 | 5.04 | 5.04
2017-08-07 12:00 | 4.8 | 4.8
2017-08-07 12:30 | 4.84 | 4.83
2017-08-07 13:00 | 3.86 | 3.85
2017-08-07 13:30 | 3.77 | 3.76
2017-08-07 14:00 | 4.06 | 4.05
2017-08-07 14:30 | 4.37 | 4.36
2017-08-07 15:00 | 4.7 | 4.69
2017-08-07 15:30 | 5.3 | 5.29
2017-08-07 16:00 | 6.34 | 6.34
2017-08-07 16:30 | 7.4 | 7.39
2017-08-07 17:00 | 8.53 | 8.52
2017-08-07 17:30 | 9.86 | 9.85
2017-08-07 18:00 | 11.23 | 11.22
2017-08-07 18:30 | 11.84 | 11.82
2017-08-07 19:00 | 11.95 | 11.93
2017-08-07 19:30 | 11.84 | 11.83
2017-08-07 20:00 | 11.61 | 11.6
2017-08-07 20:30 | 11.71 | 11.7
2017-08-07 21:00 | 11.36 | 11.35
2017-08-07 21:30 | 10.5 | 10.49
2017-08-07 22:00 | 9.36 | 9.36
2017-08-07 22:30 | 8.78 | 8.77
2017-08-07 23:00 | 8.38 | 8.36
2017-08-07 23:30 | 7.43 | 7.42
2017-08-08 | 6.49 | 6.48
2017-08-08 00:30 | 5.81 | 5.8
2017-08-08 01:00 | 5.44 | 5.43
2017-08-08 01:30 | 5.1 | 5.08
2017-08-08 02:00 | 4.76 | 4.75
2017-08-08 02:30 | 4.6 | 4.58
2017-08-08 03:00 | 4.46 | 4.44
2017-08-08 03:30 | 4.67 | 4.66
2017-08-08 04:00 | 4.75 | 4.73
2017-08-08 04:30 | 5.11 | 5.09
2017-08-08 05:00 | 5.59 | 5.57
2017-08-08 05:30 | 6.52 | 6.51
2017-08-08 06:00 | 7.22 | 7.21
2017-08-08 06:30 | 8.09 | 8.08
2017-08-08 07:00 | 9.04 | 9.04
2017-08-08 07:30 | 9.49 | 9.48
2017-08-08 08:00 | 8.48 | 8.47
2017-08-08 08:30 | 6.87 | 6.87
2017-08-08 09:00 | 5.61 | 5.6
2017-08-08 09:30 | 4.94 | 4.92
2017-08-08 10:00 | 4.26 | 4.24
2017-08-08 10:30 | 3.71 | 3.69
2017-08-08 11:00 | 3.35 | 3.33
2017-08-08 11:30 | 3.1 | 3.08
2017-08-08 12:00 | 2.78 | 2.76
2017-08-08 12:30 | 2.71 | 2.69
2017-08-08 13:00 | 2.68 | 2.66
2017-08-08 13:30 | 2.95 | 2.94
2017-08-08 14:00 | 3.59 | 3.59
2017-08-08 14:30 | 3.92 | 3.92
2017-08-08 15:00 | 4.38 | 4.38
2017-08-08 15:30 | 5.01 | 5.01
2017-08-08 16:00 | 6.03 | 6.03
2017-08-08 16:30 | 7.16 | 7.16
2017-08-08 17:00 | 8.48 | 8.48
2017-08-08 17:30 | 9.85 | 9.84
2017-08-08 18:00 | 11.54 | 11.53
2017-08-08 18:30 | 12.58 | 12.55
2017-08-08 19:00 | 13.04 | 13.02
2017-08-08 19:30 | 12.91 | 12.89
2017-08-08 20:00 | 12.87 | 12.85
2017-08-08 20:30 | 13 | 12.98
2017-08-08 21:00 | 12.77 | 12.76
2017-08-08 21:30 | 11.97 | 11.96
2017-08-08 22:00 | 11.01 | 11
2017-08-08 22:30 | 9.94 | 9.93
2017-08-08 23:00 | 9.17 | 9.15
2017-08-08 23:30 | 8.12 | 8.1
2017-08-09 | 7.12 | 7.11
2017-08-09 00:30 | 6.44 | 6.42
2017-08-09 01:00 | 6 | 5.99
2017-08-09 01:30 | 5.62 | 5.6
2017-08-09 02:00 | 5.29 | 5.28
2017-08-09 02:30 | 5.04 | 5.03
2017-08-09 03:00 | 4.96 | 4.94
2017-08-09 03:30 | 5.16 | 5.15
2017-08-09 04:00 | 5.16 | 5.15
2017-08-09 04:30 | 5.56 | 5.55
2017-08-09 05:00 | 6.15 | 6.13
2017-08-09 05:30 | 7.06 | 7.05
2017-08-09 06:00 | 8.42 | 8.42
2017-08-09 06:30 | 9.58 | 9.58
2017-08-09 07:00 | 10.5 | 10.5
2017-08-09 07:30 | 10.75 | 10.74
2017-08-09 08:00 | 10.1 | 10.1
2017-08-09 08:30 | 8.47 | 8.47
2017-08-09 09:00 | 6.99 | 6.98
2017-08-09 09:30 | 6.04 | 6.03
2017-08-09 10:00 | 5.24 | 5.23
2017-08-09 10:30 | 4.59 | 4.59
2017-08-09 11:00 | 4.11 | 4.11
2017-08-09 11:30 | 3.77 | 3.77
2017-08-09 12:00 | 3.41 | 3.4
2017-08-09 12:30 | 3.3 | 3.3
2017-08-09 13:00 | 3.39 | 3.38
2017-08-09 13:30 | 3.43 | 3.43
2017-08-09 14:00 | 3.68 | 3.68
2017-08-09 14:30 | 4.08 | 4.08
2017-08-09 15:00 | 4.39 | 4.38
2017-08-09 15:30 | 5.11 | 5.11
2017-08-09 16:00 | 6.03 | 6.02
2017-08-09 16:30 | 7.11 | 7.1
2017-08-09 17:00 | 8.4 | 8.4
2017-08-09 17:30 | 9.66 | 9.66
2017-08-09 18:00 | 11.36 | 11.34
2017-08-09 18:30 | 12.31 | 12.28
2017-08-09 19:00 | 12.79 | 12.76
2017-08-09 19:30 | 12.96 | 12.93
2017-08-09 20:00 | 12.96 | 12.94
2017-08-09 20:30 | 13.03 | 13.02
2017-08-09 21:00 | 12.67 | 12.66
2017-08-09 21:30 | 11.76 | 11.75
2017-08-09 22:00 | 10.79 | 10.78
2017-08-09 22:30 | 9.74 | 9.73
2017-08-09 23:00 | 9.16 | 9.15
2017-08-09 23:30 | 8.13 | 8.11
2017-08-10 | 7.12 | 7.11
2017-08-10 00:30 | 6.34 | 6.33
2017-08-10 01:00 | 5.87 | 5.86
2017-08-10 01:30 | 5.59 | 5.58
2017-08-10 02:00 | 5.33 | 5.31
2017-08-10 02:30 | 5.13 | 5.12
2017-08-10 03:00 | 5.03 | 5.02
2017-08-10 03:30 | 5.12 | 5.1
2017-08-10 04:00 | 5.18 | 5.16
2017-08-10 04:30 | 5.6 | 5.59
2017-08-10 05:00 | 6.09 | 6.07
2017-08-10 05:30 | 7.17 | 7.17
2017-08-10 06:00 | 8.46 | 8.45
2017-08-10 06:30 | 9.32 | 9.32
2017-08-10 07:00 | 10.44 | 10.44
2017-08-10 07:30 | 10.85 | 10.85
2017-08-10 08:00 | 10.15 | 10.15
2017-08-10 08:30 | 8.25 | 8.25
2017-08-10 09:00 | 6.91 | 6.91
2017-08-10 09:30 | 6.02 | 6.02
2017-08-10 10:00 | 4.88 | 4.87
2017-08-10 10:30 | 4.08 | 4.06
2017-08-10 11:00 | 3.6 | 3.59
2017-08-10 11:30 | 3.19 | 3.17
2017-08-10 12:00 | 3.46 | 3.45
2017-08-10 12:30 | 3.24 | 3.23
2017-08-10 13:00 | 3.26 | 3.25
2017-08-10 13:30 | 3.38 | 3.37
2017-08-10 14:00 | 3.67 | 3.66
2017-08-10 14:30 | 4.28 | 4.27
2017-08-10 15:00 | 4.6 | 4.6
2017-08-10 15:30 | 5.27 | 5.27
2017-08-10 16:00 | 6.34 | 6.33
2017-08-10 16:30 | 7.33 | 7.33
2017-08-10 17:00 | 8.46 | 8.45
2017-08-10 17:30 | 9.41 | 9.4
2017-08-10 18:00 | 10.9 | 10.88
2017-08-10 18:30 | 11.65 | 11.62
2017-08-10 19:00 | 11.94 | 11.91
2017-08-10 19:30 | 11.92 | 11.9
2017-08-10 20:00 | 11.87 | 11.86
2017-08-10 20:30 | 12.05 | 12.04
2017-08-10 21:00 | 11.64 | 11.62
2017-08-10 21:30 | 10.83 | 10.82
2017-08-10 22:00 | 10.09 | 10.08
2017-08-10 22:30 | 9.23 | 9.22
2017-08-10 23:00 | 8.6 | 8.58
2017-08-10 23:30 | 7.51 | 7.49
2017-08-11 | 6.64 | 6.63
2017-08-11 00:30 | 5.92 | 5.91
2017-08-11 01:00 | 5.59 | 5.58
2017-08-11 01:30 | 5.28 | 5.26
2017-08-11 02:00 | 4.97 | 4.96
2017-08-11 02:30 | 4.75 | 4.73
2017-08-11 03:00 | 4.7 | 4.68
2017-08-11 03:30 | 4.73 | 4.71
2017-08-11 04:00 | 4.74 | 4.72
2017-08-11 04:30 | 5.03 | 5.02
2017-08-11 05:00 | 5.48 | 5.47
2017-08-11 05:30 | 6.24 | 6.23
2017-08-11 06:00 | 6.97 | 6.96
2017-08-11 06:30 | 8.11 | 8.1
2017-08-11 07:00 | 8.99 | 8.98
2017-08-11 07:30 | 9.19 | 9.18
2017-08-11 08:00 | 8.18 | 8.17
2017-08-11 08:30 | 6.97 | 6.96
2017-08-11 09:00 | 5.92 | 5.9
2017-08-11 09:30 | 5.02 | 5
2017-08-11 10:00 | 4.17 | 4.14
2017-08-11 10:30 | 3.65 | 3.61
2017-08-11 11:00 | 3.28 | 3.23
2017-08-11 11:30 | 3.02 | 2.97
2017-08-11 12:00 | 2.82 | 2.77
2017-08-11 12:30 | 2.79 | 2.76
2017-08-11 13:00 | 2.91 | 2.89
2017-08-11 13:30 | 3.11 | 3.07
2017-08-11 14:00 | 3.5 | 3.46
2017-08-11 14:30 | 3.86 | 3.82
2017-08-11 15:00 | 4.29 | 4.26
2017-08-11 15:30 | 4.85 | 4.82
2017-08-11 16:00 | 6.27 | 6.25
2017-08-11 16:30 | 7.44 | 7.43
2017-08-11 17:00 | 7.63 | 7.61
2017-08-11 17:30 | 8.3 | 8.28
2017-08-11 18:00 | 9.18 | 9.17
2017-08-11 18:30 | 9.69 | 9.67
2017-08-11 19:00 | 10.01 | 9.99
2017-08-11 19:30 | 9.79 | 9.78
2017-08-11 20:00 | 9.79 | 9.77
2017-08-11 20:30 | 9.96 | 9.94
2017-08-11 21:00 | 9.61 | 9.6
2017-08-11 21:30 | 8.98 | 8.97
2017-08-11 22:00 | 8.32 | 8.31
2017-08-11 22:30 | 8.3 | 8.29
2017-08-11 23:00 | 8.15 | 8.13
2017-08-11 23:30 | 7.42 | 7.41
2017-08-12 | 6.48 | 6.47
2017-08-12 00:30 | 5.81 | 5.8
2017-08-12 01:00 | 5.52 | 5.5
2017-08-12 01:30 | 5.13 | 5.12
2017-08-12 02:00 | 4.82 | 4.8
2017-08-12 02:30 | 4.53 | 4.51
2017-08-12 03:00 | 4.49 | 4.48
2017-08-12 03:30 | 4.41 | 4.39
2017-08-12 04:00 | 4.37 | 4.35
2017-08-12 04:30 | 4.55 | 4.53
2017-08-12 05:00 | 4.6 | 4.58
2017-08-12 05:30 | 4.86 | 4.85
2017-08-12 06:00 | 5.12 | 5.11
2017-08-12 06:30 | 5.37 | 5.35
2017-08-12 07:00 | 5.83 | 5.8
2017-08-12 07:30 | 6.14 | 6.11
2017-08-12 08:00 | 6.27 | 6.25
2017-08-12 08:30 | 6.03 | 6.01
2017-08-12 09:00 | 5.7 | 5.68
2017-08-12 09:30 | 5.01 | 4.98
2017-08-12 10:00 | 5.76 | 5.74
2017-08-12 10:30 | 6.84 | 6.82
2017-08-12 11:00 | 5.91 | 5.89
2017-08-12 11:30 | 4.02 | 3.99
2017-08-12 12:00 | 5.31 | 5.28
2017-08-12 12:30 | 5.1 | 5.07
2017-08-12 13:00 | 4.86 | 4.83
2017-08-12 13:30 | 4.62 | 4.6
2017-08-12 14:00 | 4.41 | 4.38
2017-08-12 14:30 | 4.59 | 4.56
2017-08-12 15:00 | 4.63 | 4.6
2017-08-12 15:30 | 5.2 | 5.17
2017-08-12 16:00 | 5.87 | 5.85
2017-08-12 16:30 | 6.64 | 6.62
2017-08-12 17:00 | 7.58 | 7.57
2017-08-12 17:30 | 8.2 | 8.19
2017-08-12 18:00 | 9.1 | 9.08
2017-08-12 18:30 | 9.62 | 9.6
2017-08-12 19:00 | 9.66 | 9.64
2017-08-12 19:30 | 9.39 | 9.38
2017-08-12 20:00 | 9.37 | 9.35
2017-08-12 20:30 | 9.45 | 9.44
2017-08-12 21:00 | 9.23 | 9.22
2017-08-12 21:30 | 8.71 | 8.7
2017-08-12 22:00 | 8.38 | 8.37
2017-08-12 22:30 | 8.24 | 8.23
2017-08-12 23:00 | 8.24 | 8.23
2017-08-12 23:30 | 7.38 | 7.37
2017-08-13 | 6.47 | 6.46
2017-08-13 00:30 | 5.89 | 5.87
2017-08-13 01:00 | 5.54 | 5.53
2017-08-13 01:30 | 5.14 | 5.13
2017-08-13 02:00 | 4.84 | 4.82
2017-08-13 02:30 | 4.57 | 4.55
2017-08-13 03:00 | 4.39 | 4.37
2017-08-13 03:30 | 4.33 | 4.31
2017-08-13 04:00 | 4.25 | 4.23
2017-08-13 04:30 | 4.39 | 4.37
2017-08-13 05:00 | 4.43 | 4.41
2017-08-13 05:30 | 4.54 | 4.53
2017-08-13 06:00 | 4.75 | 4.73
2017-08-13 06:30 | 4.95 | 4.92
2017-08-13 07:00 | 5.38 | 5.34
2017-08-13 07:30 | 5.52 | 5.49
2017-08-13 08:00 | 5.95 | 5.92
2017-08-13 08:30 | 5.96 | 5.94
2017-08-13 09:00 | 5.8 | 5.78
2017-08-13 09:30 | 5.55 | 5.53
2017-08-13 10:00 | 4.93 | 4.9
2017-08-13 10:30 | 4.61 | 4.58
2017-08-13 11:00 | 4.21 | 4.18
2017-08-13 11:30 | 4.04 | 4.01
2017-08-13 12:00 | 3.9 | 3.86
2017-08-13 12:30 | 3.85 | 3.81
2017-08-13 13:00 | 3.69 | 3.66
2017-08-13 13:30 | 3.75 | 3.71
2017-08-13 14:00 | 4.12 | 4.08
2017-08-13 14:30 | 4.48 | 4.45
2017-08-13 15:00 | 4.93 | 4.91
2017-08-13 15:30 | 5.5 | 5.48
2017-08-13 16:00 | 6.17 | 6.15
2017-08-13 16:30 | 7 | 6.99
2017-08-13 17:00 | 8.15 | 8.14
2017-08-13 17:30 | 9.2 | 9.19
2017-08-13 18:00 | 10.3 | 10.28
2017-08-13 18:30 | 10.99 | 10.98
2017-08-13 19:00 | 10.96 | 10.95
2017-08-13 19:30 | 10.46 | 10.45
2017-08-13 20:00 | 10.33 | 10.32
2017-08-13 20:30 | 10.14 | 10.13
2017-08-13 21:00 | 9.65 | 9.63
2017-08-13 21:30 | 9.05 | 9.04
2017-08-13 22:00 | 8.48 | 8.47
2017-08-13 22:30 | 7.97 | 7.96
2017-08-13 23:00 | 7.73 | 7.72
2017-08-13 23:30 | 6.93 | 6.93
2017-08-14 | 6 | 5.99
2017-08-14 00:30 | 5.32 | 5.31
2017-08-14 01:00 | 5.05 | 5.04
2017-08-14 01:30 | 4.7 | 4.68
2017-08-14 02:00 | 4.35 | 4.33
2017-08-14 02:30 | 4.21 | 4.19
2017-08-14 03:00 | 4.13 | 4.11
2017-08-14 03:30 | 4.25 | 4.23
2017-08-14 04:00 | 4.25 | 4.23
2017-08-14 04:30 | 4.48 | 4.46
2017-08-14 05:00 | 4.68 | 4.67
2017-08-14 05:30 | 5.56 | 5.54
2017-08-14 06:00 | 6.37 | 6.36
2017-08-14 06:30 | 7.23 | 7.23
2017-08-14 07:00 | 8.1 | 8.1
2017-08-14 07:30 | 8.48 | 8.48
2017-08-14 08:00 | 8.16 | 8.16
2017-08-14 08:30 | 7.1 | 7.09
2017-08-14 09:00 | 5.78 | 5.78
2017-08-14 09:30 | 5.58 | 5.57
2017-08-14 10:00 | 5.03 | 5.02
2017-08-14 10:30 | 4.07 | 4.06
2017-08-14 11:00 | 3.88 | 3.87
2017-08-14 11:30 | 3.72 | 3.7
2017-08-14 12:00 | 3.65 | 3.64
2017-08-14 12:30 | 3.56 | 3.56
2017-08-14 13:00 | 3.44 | 3.43
2017-08-14 13:30 | 5.57 | 5.56
2017-08-14 14:00 | 4.31 | 4.31
2017-08-14 14:30 | 3.89 | 3.88
2017-08-14 15:00 | 6.11 | 6.11
2017-08-14 15:30 | 5.88 | 5.88
2017-08-14 16:00 | 5.98 | 5.97
2017-08-14 16:30 | 6.91 | 6.9
2017-08-14 17:00 | 7.89 | 7.88
2017-08-14 17:30 | 9.02 | 9.01
2017-08-14 18:00 | 10.89 | 10.87
2017-08-14 18:30 | 11.46 | 11.44
2017-08-14 19:00 | 11.46 | 11.44
2017-08-14 19:30 | 11.04 | 11.03
2017-08-14 20:00 | 10.77 | 10.76
2017-08-14 20:30 | 10.78 | 10.77
2017-08-14 21:00 | 10.36 | 10.35
2017-08-14 21:30 | 9.56 | 9.55
2017-08-14 22:00 | 8.69 | 8.68
2017-08-14 22:30 | 8.31 | 8.3
2017-08-14 23:00 | 7.93 | 7.92
2017-08-14 23:30 | 7.06 | 7.05
2017-08-15 | 6.04 | 6.03
2017-08-15 00:30 | 5.38 | 5.37
2017-08-15 01:00 | 5.03 | 5.02
2017-08-15 01:30 | 4.72 | 4.7
2017-08-15 02:00 | 4.42 | 4.4
2017-08-15 02:30 | 4.26 | 4.23
2017-08-15 03:00 | 4.15 | 4.13
2017-08-15 03:30 | 4.23 | 4.22
2017-08-15 04:00 | 4.28 | 4.26
2017-08-15 04:30 | 4.55 | 4.53
2017-08-15 05:00 | 4.91 | 4.89
2017-08-15 05:30 | 5.66 | 5.65
2017-08-15 06:00 | 6.37 | 6.36
2017-08-15 06:30 | 7.02 | 7.01
2017-08-15 07:00 | 7.7 | 7.69
2017-08-15 07:30 | 7.9 | 7.9
2017-08-15 08:00 | 7.78 | 7.78
2017-08-15 08:30 | 6.45 | 6.45
2017-08-15 09:00 | 5.45 | 5.45
2017-08-15 09:30 | 4.75 | 4.75
2017-08-15 10:00 | 4.39 | 4.38
2017-08-15 10:30 | 4.98 | 4.98
2017-08-15 11:00 | 4.67 | 4.66
2017-08-15 11:30 | 4.48 | 4.48
2017-08-15 12:00 | 4.35 | 4.34
2017-08-15 12:30 | 4.49 | 4.49
2017-08-15 13:00 | 4.47 | 4.47
2017-08-15 13:30 | 4.63 | 4.63
2017-08-15 14:00 | 5.11 | 5.11
2017-08-15 14:30 | 5.56 | 5.55
2017-08-15 15:00 | 5.89 | 5.88
2017-08-15 15:30 | 6.29 | 6.28
2017-08-15 16:00 | 7.47 | 7.47
2017-08-15 16:30 | 8.45 | 8.45
2017-08-15 17:00 | 8.99 | 8.99
2017-08-15 17:30 | 9.26 | 9.26
2017-08-15 18:00 | 10.34 | 10.32
2017-08-15 18:30 | 10.9 | 10.87
2017-08-15 19:00 | 11.52 | 11.5
2017-08-15 19:30 | 11.24 | 11.22
2017-08-15 20:00 | 11.09 | 11.08
2017-08-15 20:30 | 11.19 | 11.18
2017-08-15 21:00 | 10.51 | 10.5
2017-08-15 21:30 | 9.75 | 9.74
2017-08-15 22:00 | 9.05 | 9.05
2017-08-15 22:30 | 8.51 | 8.5
2017-08-15 23:00 | 7.95 | 7.94
2017-08-15 23:30 | 6.87 | 6.86
2017-08-16 | 5.98 | 5.97
2017-08-16 00:30 | 5.37 | 5.35
2017-08-16 01:00 | 5.07 | 5.05
2017-08-16 01:30 | 4.68 | 4.67
2017-08-16 02:00 | 4.37 | 4.35
2017-08-16 02:30 | 4.22 | 4.2
2017-08-16 03:00 | 4.14 | 4.12
2017-08-16 03:30 | 4.23 | 4.21
2017-08-16 04:00 | 4.13 | 4.11
2017-08-16 04:30 | 4.37 | 4.35
2017-08-16 05:00 | 4.57 | 4.56
2017-08-16 05:30 | 5.24 | 5.23
2017-08-16 06:00 | 6.17 | 6.17
2017-08-16 06:30 | 6.56 | 6.55
2017-08-16 07:00 | 7 | 6.98
2017-08-16 07:30 | 7.3 | 7.29
2017-08-16 08:00 | 7.05 | 7.05
2017-08-16 08:30 | 6.38 | 6.37
2017-08-16 09:00 | 5.61 | 5.6
2017-08-16 09:30 | 5 | 4.99
2017-08-16 10:00 | 4.39 | 4.37
2017-08-16 10:30 | 3.99 | 3.97
2017-08-16 11:00 | 4.47 | 4.46
2017-08-16 11:30 | 4.65 | 4.64
2017-08-16 12:00 | 4.08 | 4.07
2017-08-16 12:30 | 4.15 | 4.14
2017-08-16 13:00 | 4.3 | 4.29
2017-08-16 13:30 | 4.5 | 4.49
2017-08-16 14:00 | 4.93 | 4.92
2017-08-16 14:30 | 5.46 | 5.45
2017-08-16 15:00 | 5.8 | 5.79
2017-08-16 15:30 | 6.44 | 6.43
2017-08-16 16:00 | 7.31 | 7.3
2017-08-16 16:30 | 8.43 | 8.41
2017-08-16 17:00 | 9.35 | 9.34
2017-08-16 17:30 | 10.19 | 10.17
2017-08-16 18:00 | 11.12 | 11.08
2017-08-16 18:30 | 11.63 | 11.59
2017-08-16 19:00 | 11.8 | 11.77
2017-08-16 19:30 | 11.44 | 11.41
2017-08-16 20:00 | 11.25 | 11.23
2017-08-16 20:30 | 11.19 | 11.17
2017-08-16 21:00 | 10.69 | 10.67
2017-08-16 21:30 | 9.66 | 9.65
2017-08-16 22:00 | 8.89 | 8.89
2017-08-16 22:30 | 8.2 | 8.2
2017-08-16 23:00 | 7.66 | 7.65
2017-08-16 23:30 | 6.55 | 6.54
2017-08-17 | 5.71 | 5.7
2017-08-17 00:30 | 5.08 | 5.06
2017-08-17 01:00 | 4.81 | 4.79
2017-08-17 01:30 | 4.49 | 4.47
2017-08-17 02:00 | 4.21 | 4.2
2017-08-17 02:30 | 4.04 | 4.03
2017-08-17 03:00 | 3.93 | 3.91
2017-08-17 03:30 | 3.98 | 3.96
2017-08-17 04:00 | 4.02 | 4
2017-08-17 04:30 | 4.22 | 4.2
2017-08-17 05:00 | 4.41 | 4.39
2017-08-17 05:30 | 4.85 | 4.83
2017-08-17 06:00 | 5.38 | 5.36
2017-08-17 06:30 | 5.8 | 5.79
2017-08-17 07:00 | 6.37 | 6.36
2017-08-17 07:30 | 6.49 | 6.47
2017-08-17 08:00 | 6.1 | 6.08
2017-08-17 08:30 | 5.16 | 5.14
2017-08-17 09:00 | 4.45 | 4.42
2017-08-17 09:30 | 4.01 | 3.97
2017-08-17 10:00 | 3.68 | 3.63
2017-08-17 10:30 | 3.54 | 3.47
2017-08-17 11:00 | 3.25 | 3.18
2017-08-17 11:30 | 3.24 | 3.17
2017-08-17 12:00 | 3.22 | 3.15
2017-08-17 12:30 | 3.21 | 3.16
2017-08-17 13:00 | 3.44 | 3.4
2017-08-17 13:30 | 3.94 | 3.89
2017-08-17 14:00 | 4.28 | 4.23
2017-08-17 14:30 | 4.79 | 4.75
2017-08-17 15:00 | 5.33 | 5.29
2017-08-17 15:30 | 6.15 | 6.12
2017-08-17 16:00 | 6.87 | 6.84
2017-08-17 16:30 | 7.63 | 7.6
2017-08-17 17:00 | 8.35 | 8.33
2017-08-17 17:30 | 9.06 | 9.04
2017-08-17 18:00 | 10.1 | 10.07
2017-08-17 18:30 | 10.75 | 10.71
2017-08-17 19:00 | 10.97 | 10.94
2017-08-17 19:30 | 10.83 | 10.8
2017-08-17 20:00 | 10.65 | 10.63
2017-08-17 20:30 | 10.52 | 10.51
2017-08-17 21:00 | 9.99 | 9.98
2017-08-17 21:30 | 9.15 | 9.14
2017-08-17 22:00 | 8.4 | 8.38
2017-08-17 22:30 | 7.9 | 7.89
2017-08-17 23:00 | 7.58 | 7.56
2017-08-17 23:30 | 6.64 | 6.63
2017-08-18 | 5.83 | 5.81
2017-08-18 00:30 | 5.18 | 5.17
2017-08-18 01:00 | 4.77 | 4.75
2017-08-18 01:30 | 4.5 | 4.48
2017-08-18 02:00 | 4.25 | 4.23
2017-08-18 02:30 | 4.11 | 4.09
2017-08-18 03:00 | 4.05 | 4.03
2017-08-18 03:30 | 4.04 | 4.01
2017-08-18 04:00 | 4.13 | 4.11
2017-08-18 04:30 | 4.26 | 4.23
2017-08-18 05:00 | 4.57 | 4.55
2017-08-18 05:30 | 5.05 | 5.04
2017-08-18 06:00 | 5.62 | 5.61
2017-08-18 06:30 | 6 | 5.98
2017-08-18 07:00 | 6.53 | 6.51
2017-08-18 07:30 | 6.52 | 6.5
2017-08-18 08:00 | 5.99 | 5.97
2017-08-18 08:30 | 5.21 | 5.19
2017-08-18 09:00 | 4.28 | 4.25
2017-08-18 09:30 | 3.83 | 3.8
2017-08-18 10:00 | 3.39 | 3.36
2017-08-18 10:30 | 3.06 | 3.02
2017-08-18 11:00 | 2.75 | 2.7
2017-08-18 11:30 | 2.61 | 2.55
2017-08-18 12:00 | 2.47 | 2.42
2017-08-18 12:30 | 2.38 | 2.35
2017-08-18 13:00 | 2.47 | 2.44
2017-08-18 13:30 | 2.63 | 2.59
2017-08-18 14:00 | 3.11 | 3.06
2017-08-18 14:30 | 3.35 | 3.33
2017-08-18 15:00 | 3.69 | 3.67
2017-08-18 15:30 | 4.55 | 4.53
2017-08-18 16:00 | 5.61 | 5.59
2017-08-18 16:30 | 6.58 | 6.57
2017-08-18 17:00 | 7.56 | 7.55
2017-08-18 17:30 | 8.2 | 8.19
2017-08-18 18:00 | 8.96 | 8.95
2017-08-18 18:30 | 9.7 | 9.69
2017-08-18 19:00 | 10.03 | 10.02
2017-08-18 19:30 | 9.8 | 9.79
2017-08-18 20:00 | 9.81 | 9.8
2017-08-18 20:30 | 9.93 | 9.92
2017-08-18 21:00 | 9.51 | 9.51
2017-08-18 21:30 | 8.88 | 8.87
2017-08-18 22:00 | 8.4 | 8.39
2017-08-18 22:30 | 8.18 | 8.17
2017-08-18 23:00 | 8.11 | 8.1
2017-08-18 23:30 | 7.31 | 7.3
2017-08-19 | 6.49 | 6.48
2017-08-19 00:30 | 5.69 | 5.68
2017-08-19 01:00 | 5.35 | 5.34
2017-08-19 01:30 | 4.86 | 4.84
2017-08-19 02:00 | 4.59 | 4.57
2017-08-19 02:30 | 4.41 | 4.39
2017-08-19 03:00 | 4.26 | 4.24
2017-08-19 03:30 | 4.29 | 4.27
2017-08-19 04:00 | 4.26 | 4.24
2017-08-19 04:30 | 4.3 | 4.28
2017-08-19 05:00 | 4.37 | 4.34
2017-08-19 05:30 | 4.66 | 4.65
2017-08-19 06:00 | 4.82 | 4.81
2017-08-19 06:30 | 5 | 4.96
2017-08-19 07:00 | 5.43 | 5.38
2017-08-19 07:30 | 5.65 | 5.61
2017-08-19 08:00 | 5.58 | 5.55
2017-08-19 08:30 | 5.5 | 5.47
2017-08-19 09:00 | 5.16 | 5.13
2017-08-19 09:30 | 4.99 | 4.96
2017-08-19 10:00 | 4.5 | 4.47
2017-08-19 10:30 | 4.08 | 4.05
2017-08-19 11:00 | 3.64 | 3.6
2017-08-19 11:30 | 3.41 | 3.36
2017-08-19 12:00 | 3.27 | 3.23
2017-08-19 12:30 | 3.14 | 3.09
2017-08-19 13:00 | 3.22 | 3.17
2017-08-19 13:30 | 3.15 | 3.11
2017-08-19 14:00 | 3.39 | 3.35
2017-08-19 14:30 | 3.64 | 3.61
2017-08-19 15:00 | 4.18 | 4.16
2017-08-19 15:30 | 4.84 | 4.82
2017-08-19 16:00 | 5.48 | 5.46
2017-08-19 16:30 | 6.37 | 6.35
2017-08-19 17:00 | 7.38 | 7.37
2017-08-19 17:30 | 8.43 | 8.42
2017-08-19 18:00 | 9.41 | 9.39
2017-08-19 18:30 | 10.2 | 10.19
2017-08-19 19:00 | 10.58 | 10.57
2017-08-19 19:30 | 10.39 | 10.38
2017-08-19 20:00 | 10.5 | 10.49
2017-08-19 20:30 | 10.72 | 10.71
2017-08-19 21:00 | 10.26 | 10.25
2017-08-19 21:30 | 9.79 | 9.78
2017-08-19 22:00 | 9.47 | 9.45
2017-08-19 22:30 | 9.2 | 9.19
2017-08-19 23:00 | 9.11 | 9.09
2017-08-19 23:30 | 8.3 | 8.29
2017-08-20 | 7.44 | 7.43
2017-08-20 00:30 | 6.6 | 6.59
2017-08-20 01:00 | 6.2 | 6.19
2017-08-20 01:30 | 5.76 | 5.75
2017-08-20 02:00 | 5.43 | 5.41
2017-08-20 02:30 | 5.19 | 5.18
2017-08-20 03:00 | 5.03 | 5.02
2017-08-20 03:30 | 5.06 | 5.05
2017-08-20 04:00 | 4.95 | 4.93
2017-08-20 04:30 | 5.1 | 5.09
2017-08-20 05:00 | 5.19 | 5.17
2017-08-20 05:30 | 5.45 | 5.43
2017-08-20 06:00 | 5.67 | 5.66
2017-08-20 06:30 | 5.75 | 5.72
2017-08-20 07:00 | 6.18 | 6.15
2017-08-20 07:30 | 6.48 | 6.46
2017-08-20 08:00 | 6.76 | 6.74
2017-08-20 08:30 | 6.82 | 6.81
2017-08-20 09:00 | 6.62 | 6.61
2017-08-20 09:30 | 6.24 | 6.22
2017-08-20 10:00 | 5.67 | 5.65
2017-08-20 10:30 | 5.15 | 5.13
2017-08-20 11:00 | 4.76 | 4.73
2017-08-20 11:30 | 4.34 | 4.31
2017-08-20 12:00 | 4 | 3.97
2017-08-20 12:30 | 3.86 | 3.83
2017-08-20 13:00 | 3.8 | 3.77
2017-08-20 13:30 | 3.81 | 3.78
2017-08-20 14:00 | 4.12 | 4.09
2017-08-20 14:30 | 4.34 | 4.31
2017-08-20 15:00 | 4.71 | 4.69
2017-08-20 15:30 | 5.27 | 5.25
2017-08-20 16:00 | 5.97 | 5.95
2017-08-20 16:30 | 6.98 | 6.97
2017-08-20 17:00 | 8.28 | 8.27
2017-08-20 17:30 | 9.28 | 9.27
2017-08-20 18:00 | 10.65 | 10.64
2017-08-20 18:30 | 11.7 | 11.69
2017-08-20 19:00 | 11.89 | 11.88
2017-08-20 19:30 | 11.55 | 11.54
2017-08-20 20:00 | 11.47 | 11.46
2017-08-20 20:30 | 11.56 | 11.55
2017-08-20 21:00 | 11.26 | 11.25
2017-08-20 21:30 | 10.63 | 10.61
2017-08-20 22:00 | 9.78 | 9.77
2017-08-20 22:30 | 9.17 | 9.16
2017-08-20 23:00 | 8.76 | 8.75
2017-08-20 23:30 | 7.82 | 7.81
2017-08-21 | 6.95 | 6.94
2017-08-21 00:30 | 6.22 | 6.21
2017-08-21 01:00 | 5.8 | 5.79
2017-08-21 01:30 | 5.5 | 5.49
2017-08-21 02:00 | 5.18 | 5.16
2017-08-21 02:30 | 5.03 | 5.02
2017-08-21 03:00 | 4.84 | 4.82
2017-08-21 03:30 | 4.92 | 4.9
2017-08-21 04:00 | 4.97 | 4.95
2017-08-21 04:30 | 5.33 | 5.31
2017-08-21 05:00 | 5.77 | 5.76
2017-08-21 05:30 | 6.89 | 6.88
2017-08-21 06:00 | 7.97 | 7.96
2017-08-21 06:30 | 8.87 | 8.87
2017-08-21 07:00 | 9.6 | 9.6
2017-08-21 07:30 | 9.96 | 9.95
2017-08-21 08:00 | 9.16 | 9.16
2017-08-21 08:30 | 7.62 | 7.62
2017-08-21 09:00 | 7.68 | 7.68
2017-08-21 09:30 | 6.36 | 6.36
2017-08-21 10:00 | 5.4 | 5.39
2017-08-21 10:30 | 4.62 | 4.61
2017-08-21 11:00 | 4.1 | 4.09
2017-08-21 11:30 | 3.86 | 3.84
2017-08-21 12:00 | 3.94 | 3.93
2017-08-21 12:30 | 3.3 | 3.29
2017-08-21 13:00 | 3.48 | 3.47
2017-08-21 13:30 | 3.93 | 3.92
2017-08-21 14:00 | 5.01 | 5.01
2017-08-21 14:30 | 4.88 | 4.88
2017-08-21 15:00 | 4.85 | 4.84
2017-08-21 15:30 | 5.79 | 5.79
2017-08-21 16:00 | 7.68 | 7.67
2017-08-21 16:30 | 8.4 | 8.4
2017-08-21 17:00 | 9.6 | 9.6
2017-08-21 17:30 | 10.71 | 10.71
2017-08-21 18:00 | 11.91 | 11.9
2017-08-21 18:30 | 12.53 | 12.5
2017-08-21 19:00 | 12.68 | 12.65
2017-08-21 19:30 | 12.38 | 12.36
2017-08-21 20:00 | 12.27 | 12.25
2017-08-21 20:30 | 12.24 | 12.23
2017-08-21 21:00 | 11.72 | 11.72
2017-08-21 21:30 | 10.78 | 10.78
2017-08-21 22:00 | 9.81 | 9.8
2017-08-21 22:30 | 9.08 | 9.07
2017-08-21 23:00 | 8.31 | 8.3
2017-08-21 23:30 | 7.15 | 7.14
2017-08-22 | 6.26 | 6.25
2017-08-22 00:30 | 5.58 | 5.57
2017-08-22 01:00 | 5.23 | 5.22
2017-08-22 01:30 | 4.83 | 4.81
2017-08-22 02:00 | 4.51 | 4.49
2017-08-22 02:30 | 4.33 | 4.31
2017-08-22 03:00 | 4.28 | 4.26
2017-08-22 03:30 | 4.33 | 4.31
2017-08-22 04:00 | 4.38 | 4.36
2017-08-22 04:30 | 4.65 | 4.63
2017-08-22 05:00 | 5.07 | 5.05
2017-08-22 05:30 | 5.95 | 5.94
2017-08-22 06:00 | 6.69 | 6.68
2017-08-22 06:30 | 7.13 | 7.12
2017-08-22 07:00 | 7.5 | 7.49
2017-08-22 07:30 | 7.91 | 7.91
2017-08-22 08:00 | 7.24 | 7.24
2017-08-22 08:30 | 5.89 | 5.88
2017-08-22 09:00 | 5.34 | 5.33
2017-08-22 09:30 | 5.53 | 5.52
2017-08-22 10:00 | 4.77 | 4.76
2017-08-22 10:30 | 5.07 | 5.06
2017-08-22 11:00 | 4.57 | 4.56
2017-08-22 11:30 | 4.09 | 4.08
2017-08-22 12:00 | 3.29 | 3.27
2017-08-22 12:30 | 3.18 | 3.17
2017-08-22 13:00 | 3.33 | 3.3
2017-08-22 13:30 | 3.62 | 3.59
2017-08-22 14:00 | 3.62 | 3.61
2017-08-22 14:30 | 3.96 | 3.95
2017-08-22 15:00 | 4.5 | 4.49
2017-08-22 15:30 | 5.32 | 5.3
2017-08-22 16:00 | 6.28 | 6.26
2017-08-22 16:30 | 7.15 | 7.14
2017-08-22 17:00 | 8.18 | 8.18
2017-08-22 17:30 | 9.27 | 9.26
2017-08-22 18:00 | 10.4 | 10.39
2017-08-22 18:30 | 11.44 | 11.42
2017-08-22 19:00 | 11.73 | 11.71
2017-08-22 19:30 | 11.42 | 11.4
2017-08-22 20:00 | 11.2 | 11.19
2017-08-22 20:30 | 11.32 | 11.31
2017-08-22 21:00 | 10.86 | 10.85
2017-08-22 21:30 | 10.06 | 10.05
2017-08-22 22:00 | 9.23 | 9.23
2017-08-22 22:30 | 8.32 | 8.31
2017-08-22 23:00 | 7.71 | 7.7
2017-08-22 23:30 | 6.79 | 6.77
2017-08-23 | 5.93 | 5.92
2017-08-23 00:30 | 5.26 | 5.24
2017-08-23 01:00 | 4.87 | 4.86
2017-08-23 01:30 | 4.55 | 4.54
2017-08-23 02:00 | 4.33 | 4.31
2017-08-23 02:30 | 4.2 | 4.19
2017-08-23 03:00 | 4.08 | 4.06
2017-08-23 03:30 | 4.14 | 4.13
2017-08-23 04:00 | 4.2 | 4.18
2017-08-23 04:30 | 4.54 | 4.52
2017-08-23 05:00 | 4.75 | 4.73
2017-08-23 05:30 | 5.31 | 5.29
2017-08-23 06:00 | 5.93 | 5.92
2017-08-23 06:30 | 6.42 | 6.4
2017-08-23 07:00 | 7.23 | 7.22
2017-08-23 07:30 | 7.47 | 7.46
2017-08-23 08:00 | 7.49 | 7.48
2017-08-23 08:30 | 6.63 | 6.62
2017-08-23 09:00 | 6.7 | 6.69
2017-08-23 09:30 | 5.79 | 5.78
2017-08-23 10:00 | 5.02 | 5
2017-08-23 10:30 | 5.62 | 5.6
2017-08-23 11:00 | 5.48 | 5.47
2017-08-23 11:30 | 4.49 | 4.48
2017-08-23 12:00 | 3.42 | 3.4
2017-08-23 12:30 | 3.25 | 3.24
2017-08-23 13:00 | 3.3 | 3.29
2017-08-23 13:30 | 3.46 | 3.45
2017-08-23 14:00 | 3.75 | 3.73
2017-08-23 14:30 | 4.04 | 4.02
2017-08-23 15:00 | 4.27 | 4.26
2017-08-23 15:30 | 5.02 | 5.01
2017-08-23 16:00 | 6.05 | 6.04
2017-08-23 16:30 | 7.19 | 7.18
2017-08-23 17:00 | 8.32 | 8.31
2017-08-23 17:30 | 9.33 | 9.32
2017-08-23 18:00 | 10.52 | 10.51
2017-08-23 18:30 | 11.31 | 11.29
2017-08-23 19:00 | 11.57 | 11.54
2017-08-23 19:30 | 11.31 | 11.29
2017-08-23 20:00 | 11.1 | 11.09
2017-08-23 20:30 | 11.09 | 11.08
2017-08-23 21:00 | 10.6 | 10.59
2017-08-23 21:30 | 9.85 | 9.84
2017-08-23 22:00 | 8.98 | 8.97
2017-08-23 22:30 | 8.18 | 8.17
2017-08-23 23:00 | 7.63 | 7.62
2017-08-23 23:30 | 6.75 | 6.74
2017-08-24 | 5.88 | 5.87
2017-08-24 00:30 | 5.16 | 5.15
2017-08-24 01:00 | 4.79 | 4.77
2017-08-24 01:30 | 4.6 | 4.58
2017-08-24 02:00 | 4.26 | 4.24
2017-08-24 02:30 | 4.05 | 4.03
2017-08-24 03:00 | 3.94 | 3.92
2017-08-24 03:30 | 3.96 | 3.94
2017-08-24 04:00 | 3.96 | 3.94
2017-08-24 04:30 | 4.22 | 4.2
2017-08-24 05:00 | 4.53 | 4.51
2017-08-24 05:30 | 5.45 | 5.44
2017-08-24 06:00 | 6.14 | 6.13
2017-08-24 06:30 | 6.77 | 6.76
2017-08-24 07:00 | 7.26 | 7.25
2017-08-24 07:30 | 7.75 | 7.75
2017-08-24 08:00 | 7.32 | 7.31
2017-08-24 08:30 | 7.33 | 7.32
2017-08-24 09:00 | 6.24 | 6.23
2017-08-24 09:30 | 7.29 | 7.28
2017-08-24 10:00 | 7.17 | 7.17
2017-08-24 10:30 | 6.36 | 6.35
2017-08-24 11:00 | 5.81 | 5.81
2017-08-24 11:30 | 4.04 | 4.03
2017-08-24 12:00 | 4.89 | 4.88
2017-08-24 12:30 | 4.21 | 4.21
2017-08-24 13:00 | 3.59 | 3.58
2017-08-24 13:30 | 4.61 | 4.61
2017-08-24 14:00 | 4.35 | 4.34
2017-08-24 14:30 | 5.01 | 5
2017-08-24 15:00 | 7.18 | 7.18
2017-08-24 15:30 | 6.6 | 6.6
2017-08-24 16:00 | 7.14 | 7.13
2017-08-24 16:30 | 7.45 | 7.44
2017-08-24 17:00 | 8.35 | 8.34
2017-08-24 17:30 | 8.89 | 8.88
2017-08-24 18:00 | 9.77 | 9.76
2017-08-24 18:30 | 10.55 | 10.53
2017-08-24 19:00 | 10.88 | 10.86
2017-08-24 19:30 | 10.6 | 10.59
2017-08-24 20:00 | 10.6 | 10.59
2017-08-24 20:30 | 10.88 | 10.87
2017-08-24 21:00 | 10.42 | 10.41
2017-08-24 21:30 | 9.66 | 9.65
2017-08-24 22:00 | 8.84 | 8.83
2017-08-24 22:30 | 8.47 | 8.46
2017-08-24 23:00 | 8.21 | 8.2
2017-08-24 23:30 | 7.24 | 7.22
2017-08-25 | 6.3 | 6.29
2017-08-25 00:30 | 5.52 | 5.5
2017-08-25 01:00 | 5.12 | 5.11
2017-08-25 01:30 | 4.75 | 4.73
2017-08-25 02:00 | 4.46 | 4.44
2017-08-25 02:30 | 4.32 | 4.3
2017-08-25 03:00 | 4.22 | 4.19
2017-08-25 03:30 | 4.34 | 4.32
2017-08-25 04:00 | 4.35 | 4.33
2017-08-25 04:30 | 4.67 | 4.65
2017-08-25 05:00 | 4.96 | 4.94
2017-08-25 05:30 | 5.61 | 5.59
2017-08-25 06:00 | 6.13 | 6.12
2017-08-25 06:30 | 6.83 | 6.81
2017-08-25 07:00 | 7.3 | 7.28
2017-08-25 07:30 | 7.76 | 7.74
2017-08-25 08:00 | 7.38 | 7.36
2017-08-25 08:30 | 6 | 5.98
2017-08-25 09:00 | 4.89 | 4.86
2017-08-25 09:30 | 4.42 | 4.4
2017-08-25 10:00 | 4.41 | 4.38
2017-08-25 10:30 | 3.63 | 3.6
2017-08-25 11:00 | 3.68 | 3.65
2017-08-25 11:30 | 3.96 | 3.93
2017-08-25 12:00 | 3.93 | 3.91
2017-08-25 12:30 | 3.5 | 3.48
2017-08-25 13:00 | 3.83 | 3.81
2017-08-25 13:30 | 3.54 | 3.52
2017-08-25 14:00 | 4.81 | 4.79
2017-08-25 14:30 | 4.59 | 4.57
2017-08-25 15:00 | 3.98 | 3.96
2017-08-25 15:30 | 4.36 | 4.34
2017-08-25 16:00 | 6.32 | 6.31
2017-08-25 16:30 | 7.02 | 7.01
2017-08-25 17:00 | 7.6 | 7.59
2017-08-25 17:30 | 8.36 | 8.35
2017-08-25 18:00 | 9.15 | 9.13
2017-08-25 18:30 | 10.22 | 10.21
2017-08-25 19:00 | 10.76 | 10.75
2017-08-25 19:30 | 10.68 | 10.67
2017-08-25 20:00 | 10.77 | 10.76
2017-08-25 20:30 | 11.01 | 11
2017-08-25 21:00 | 10.58 | 10.56
2017-08-25 21:30 | 10 | 9.98
2017-08-25 22:00 | 9.35 | 9.34
2017-08-25 22:30 | 9.06 | 9.04
2017-08-25 23:00 | 8.88 | 8.87
2017-08-25 23:30 | 7.84 | 7.82
2017-08-26 | 6.88 | 6.87
2017-08-26 00:30 | 6.22 | 6.21
2017-08-26 01:00 | 5.71 | 5.69
2017-08-26 01:30 | 5.36 | 5.35
2017-08-26 02:00 | 5.04 | 5.02
2017-08-26 02:30 | 4.85 | 4.83
2017-08-26 03:00 | 4.72 | 4.7
2017-08-26 03:30 | 4.69 | 4.67
2017-08-26 04:00 | 4.71 | 4.69
2017-08-26 04:30 | 4.81 | 4.79
2017-08-26 05:00 | 4.97 | 4.95
2017-08-26 05:30 | 5.11 | 5.1
2017-08-26 06:00 | 5.28 | 5.26
2017-08-26 06:30 | 5.57 | 5.54
2017-08-26 07:00 | 6.01 | 5.97
2017-08-26 07:30 | 6.25 | 6.23
2017-08-26 08:00 | 6.15 | 6.13
2017-08-26 08:30 | 5.87 | 5.85
2017-08-26 09:00 | 5.5 | 5.48
2017-08-26 09:30 | 5.28 | 5.26
2017-08-26 10:00 | 4.7 | 4.67
2017-08-26 10:30 | 4.2 | 4.17
2017-08-26 11:00 | 3.85 | 3.8
2017-08-26 11:30 | 3.82 | 3.78
2017-08-26 12:00 | 3.74 | 3.68
2017-08-26 12:30 | 3.64 | 3.58
2017-08-26 13:00 | 3.52 | 3.47
2017-08-26 13:30 | 3.53 | 3.49
2017-08-26 14:00 | 3.51 | 3.46
2017-08-26 14:30 | 3.94 | 3.89
2017-08-26 15:00 | 4.23 | 4.2
2017-08-26 15:30 | 4.67 | 4.64
2017-08-26 16:00 | 5.31 | 5.28
2017-08-26 16:30 | 6.1 | 6.08
2017-08-26 17:00 | 7.12 | 7.11
2017-08-26 17:30 | 8.01 | 8
2017-08-26 18:00 | 8.9 | 8.88
2017-08-26 18:30 | 9.64 | 9.63
2017-08-26 19:00 | 9.97 | 9.96
2017-08-26 19:30 | 9.66 | 9.65
2017-08-26 20:00 | 9.8 | 9.78
2017-08-26 20:30 | 9.86 | 9.85
2017-08-26 21:00 | 9.52 | 9.51
2017-08-26 21:30 | 9.02 | 9.01
2017-08-26 22:00 | 8.72 | 8.71
2017-08-26 22:30 | 8.47 | 8.46
2017-08-26 23:00 | 8.34 | 8.32
2017-08-26 23:30 | 7.57 | 7.56
2017-08-27 | 6.8 | 6.79
2017-08-27 00:30 | 6.09 | 6.07
2017-08-27 01:00 | 5.73 | 5.71
2017-08-27 01:30 | 5.25 | 5.24
2017-08-27 02:00 | 4.91 | 4.89
2017-08-27 02:30 | 4.69 | 4.67
2017-08-27 03:00 | 4.56 | 4.53
2017-08-27 03:30 | 4.53 | 4.5
2017-08-27 04:00 | 4.52 | 4.5
2017-08-27 04:30 | 4.59 | 4.57
2017-08-27 05:00 | 4.63 | 4.61
2017-08-27 05:30 | 4.86 | 4.85
2017-08-27 06:00 | 4.92 | 4.9
2017-08-27 06:30 | 5.11 | 5.06
2017-08-27 07:00 | 5.53 | 5.48
2017-08-27 07:30 | 5.99 | 5.96
2017-08-27 08:00 | 6.51 | 6.49
2017-08-27 08:30 | 6.67 | 6.65
2017-08-27 09:00 | 6.94 | 6.93
2017-08-27 09:30 | 5.96 | 5.95
2017-08-27 10:00 | 5.11 | 5.09
2017-08-27 10:30 | 4.5 | 4.48
2017-08-27 11:00 | 5.91 | 5.89
2017-08-27 11:30 | 4.35 | 4.32
2017-08-27 12:00 | 4.02 | 3.98
2017-08-27 12:30 | 4.26 | 4.23
2017-08-27 13:00 | 6.35 | 6.33
2017-08-27 13:30 | 5.67 | 5.65
2017-08-27 14:00 | 5.44 | 5.42
2017-08-27 14:30 | 4.78 | 4.76
2017-08-27 15:00 | 5.21 | 5.19
2017-08-27 15:30 | 5.13 | 5.1
2017-08-27 16:00 | 5.93 | 5.92
2017-08-27 16:30 | 7.1 | 7.09
2017-08-27 17:00 | 8.03 | 8.02
2017-08-27 17:30 | 8.96 | 8.95
2017-08-27 18:00 | 9.96 | 9.95
2017-08-27 18:30 | 10.86 | 10.85
2017-08-27 19:00 | 11.22 | 11.2
2017-08-27 19:30 | 10.76 | 10.75
2017-08-27 20:00 | 10.7 | 10.69
2017-08-27 20:30 | 10.63 | 10.62
2017-08-27 21:00 | 10.24 | 10.23
2017-08-27 21:30 | 9.65 | 9.64
2017-08-27 22:00 | 9.05 | 9.04
2017-08-27 22:30 | 8.59 | 8.58
2017-08-27 23:00 | 8.25 | 8.24
2017-08-27 23:30 | 7.22 | 7.21
2017-08-28 | 6.39 | 6.38
2017-08-28 00:30 | 5.78 | 5.76
2017-08-28 01:00 | 5.34 | 5.33
2017-08-28 01:30 | 4.99 | 4.98
2017-08-28 02:00 | 4.7 | 4.68
2017-08-28 02:30 | 4.48 | 4.46
2017-08-28 03:00 | 4.4 | 4.38
2017-08-28 03:30 | 4.52 | 4.5
2017-08-28 04:00 | 4.62 | 4.59
2017-08-28 04:30 | 4.99 | 4.97
2017-08-28 05:00 | 5.39 | 5.38
2017-08-28 05:30 | 6.3 | 6.29
2017-08-28 06:00 | 7.58 | 7.57
2017-08-28 06:30 | 8.44 | 8.44
2017-08-28 07:00 | 9.05 | 9.05
2017-08-28 07:30 | 9.1 | 9.1
2017-08-28 08:00 | 8.07 | 8.06
2017-08-28 08:30 | 6.78 | 6.78
2017-08-28 09:00 | 5.61 | 5.6
2017-08-28 09:30 | 4.81 | 4.8
2017-08-28 10:00 | 4.3 | 4.3
2017-08-28 10:30 | 3.8 | 3.79
2017-08-28 11:00 | 3.58 | 3.56
2017-08-28 11:30 | 3.29 | 3.28
2017-08-28 12:00 | 3.06 | 3.05
2017-08-28 12:30 | 3.03 | 3.02
2017-08-28 13:00 | 2.97 | 2.96
2017-08-28 13:30 | 2.98 | 2.97
2017-08-28 14:00 | 3.34 | 3.33
2017-08-28 14:30 | 3.57 | 3.55
2017-08-28 15:00 | 3.91 | 3.9
2017-08-28 15:30 | 4.64 | 4.63
2017-08-28 16:00 | 5.65 | 5.64
2017-08-28 16:30 | 6.85 | 6.85
2017-08-28 17:00 | 8.02 | 8.02
2017-08-28 17:30 | 9.51 | 9.5
2017-08-28 18:00 | 10.82 | 10.81
2017-08-28 18:30 | 12.16 | 12.14
2017-08-28 19:00 | 12.59 | 12.58
2017-08-28 19:30 | 12.29 | 12.27
2017-08-28 20:00 | 12.14 | 12.13
2017-08-28 20:30 | 12.28 | 12.27
2017-08-28 21:00 | 11.78 | 11.78
2017-08-28 21:30 | 11.01 | 11
2017-08-28 22:00 | 10.17 | 10.16
2017-08-28 22:30 | 9.25 | 9.24
2017-08-28 23:00 | 8.73 | 8.71
2017-08-28 23:30 | 7.69 | 7.67
2017-08-29 | 6.75 | 6.74
2017-08-29 00:30 | 5.99 | 5.97
2017-08-29 01:00 | 5.66 | 5.65
2017-08-29 01:30 | 5.23 | 5.22
2017-08-29 02:00 | 4.95 | 4.93
2017-08-29 02:30 | 4.75 | 4.73
2017-08-29 03:00 | 4.68 | 4.66
2017-08-29 03:30 | 4.82 | 4.81
2017-08-29 04:00 | 4.85 | 4.84
2017-08-29 04:30 | 5.29 | 5.27
2017-08-29 05:00 | 5.68 | 5.66
2017-08-29 05:30 | 6.53 | 6.52
2017-08-29 06:00 | 7.96 | 7.96
2017-08-29 06:30 | 8.88 | 8.88
2017-08-29 07:00 | 9.81 | 9.81
2017-08-29 07:30 | 9.75 | 9.75
2017-08-29 08:00 | 8.72 | 8.72
2017-08-29 08:30 | 6.93 | 6.93
2017-08-29 09:00 | 5.62 | 5.61
2017-08-29 09:30 | 4.65 | 4.63
2017-08-29 10:00 | 4.2 | 4.19
2017-08-29 10:30 | 3.72 | 3.72
2017-08-29 11:00 | 3.35 | 3.34
2017-08-29 11:30 | 3.01 | 3
2017-08-29 12:00 | 2.94 | 2.93
2017-08-29 12:30 | 2.91 | 2.9
2017-08-29 13:00 | 2.92 | 2.9
2017-08-29 13:30 | 3.09 | 3.06
2017-08-29 14:00 | 3.33 | 3.32
2017-08-29 14:30 | 3.57 | 3.56
2017-08-29 15:00 | 3.89 | 3.87
2017-08-29 15:30 | 4.64 | 4.63
2017-08-29 16:00 | 5.6 | 5.59
2017-08-29 16:30 | 6.7 | 6.69
2017-08-29 17:00 | 7.91 | 7.9
2017-08-29 17:30 | 9.09 | 9.08
2017-08-29 18:00 | 10.57 | 10.56
2017-08-29 18:30 | 11.76 | 11.74
2017-08-29 19:00 | 12.19 | 12.17
2017-08-29 19:30 | 11.87 | 11.85
2017-08-29 20:00 | 11.66 | 11.64
2017-08-29 20:30 | 11.49 | 11.48
2017-08-29 21:00 | 10.94 | 10.93
2017-08-29 21:30 | 10.08 | 10.07
2017-08-29 22:00 | 9.26 | 9.25
2017-08-29 22:30 | 8.66 | 8.64
2017-08-29 23:00 | 8.24 | 8.22
2017-08-29 23:30 | 7.15 | 7.14
2017-08-30 | 6.3 | 6.28
2017-08-30 00:30 | 5.58 | 5.57
2017-08-30 01:00 | 5.32 | 5.3
2017-08-30 01:30 | 5.02 | 5
2017-08-30 02:00 | 4.76 | 4.74
2017-08-30 02:30 | 4.42 | 4.4
2017-08-30 03:00 | 4.35 | 4.33
2017-08-30 03:30 | 4.42 | 4.39
2017-08-30 04:00 | 4.56 | 4.54
2017-08-30 04:30 | 4.87 | 4.85
2017-08-30 05:00 | 5.31 | 5.3
2017-08-30 05:30 | 6.05 | 6.03
2017-08-30 06:00 | 6.77 | 6.76
2017-08-30 06:30 | 7.48 | 7.47
2017-08-30 07:00 | 7.89 | 7.88
2017-08-30 07:30 | 7.93 | 7.92
2017-08-30 08:00 | 7.22 | 7.21
2017-08-30 08:30 | 5.64 | 5.62
2017-08-30 09:00 | 4.6 | 4.58
2017-08-30 09:30 | 3.86 | 3.85
2017-08-30 10:00 | 3.36 | 3.34
2017-08-30 10:30 | 2.85 | 2.83
2017-08-30 11:00 | 2.96 | 2.94
2017-08-30 11:30 | 3.48 | 3.47
2017-08-30 12:00 | 3.31 | 3.29
2017-08-30 12:30 | 3.31 | 3.29
2017-08-30 13:00 | 3.29 | 3.27
2017-08-30 13:30 | 2.67 | 2.64
2017-08-30 14:00 | 2.57 | 2.54
2017-08-30 14:30 | 2.94 | 2.91
2017-08-30 15:00 | 3.41 | 3.39
2017-08-30 15:30 | 4.06 | 4.04
2017-08-30 16:00 | 5.15 | 5.13
2017-08-30 16:30 | 6.16 | 6.14
2017-08-30 17:00 | 7.36 | 7.35
2017-08-30 17:30 | 8.43 | 8.42
2017-08-30 18:00 | 9.7 | 9.69
2017-08-30 18:30 | 10.74 | 10.73
2017-08-30 19:00 | 11.32 | 11.31
2017-08-30 19:30 | 11.08 | 11.07
2017-08-30 20:00 | 11.16 | 11.15
2017-08-30 20:30 | 11.29 | 11.28
2017-08-30 21:00 | 10.88 | 10.87
2017-08-30 21:30 | 10.06 | 10.05
2017-08-30 22:00 | 9.33 | 9.32
2017-08-30 22:30 | 8.86 | 8.85
2017-08-30 23:00 | 8.64 | 8.63
2017-08-30 23:30 | 7.55 | 7.54
2017-08-31 | 6.49 | 6.48
2017-08-31 00:30 | 5.89 | 5.88
2017-08-31 01:00 | 5.55 | 5.53
2017-08-31 01:30 | 5.14 | 5.13
2017-08-31 02:00 | 4.85 | 4.83
2017-08-31 02:30 | 4.67 | 4.64
2017-08-31 03:00 | 4.66 | 4.64
2017-08-31 03:30 | 4.76 | 4.74
2017-08-31 04:00 | 4.8 | 4.78
2017-08-31 04:30 | 5.22 | 5.21
2017-08-31 05:00 | 5.68 | 5.66
2017-08-31 05:30 | 6.38 | 6.37
2017-08-31 06:00 | 7.05 | 7.03
2017-08-31 06:30 | 7.93 | 7.92
2017-08-31 07:00 | 8.71 | 8.7
2017-08-31 07:30 | 8.62 | 8.62
2017-08-31 08:00 | 7.61 | 7.6
2017-08-31 08:30 | 6.09 | 6.08
2017-08-31 09:00 | 4.76 | 4.75
2017-08-31 09:30 | 5.42 | 5.4
2017-08-31 10:00 | 4.88 | 4.86
2017-08-31 10:30 | 4.47 | 4.45
2017-08-31 11:00 | 3.94 | 3.92
2017-08-31 11:30 | 2.53 | 2.5
2017-08-31 12:00 | 2.41 | 2.37
2017-08-31 12:30 | 2.62 | 2.59
2017-08-31 13:00 | 3 | 2.98
2017-08-31 13:30 | 3 | 2.97
2017-08-31 14:00 | 3.14 | 3.11
2017-08-31 14:30 | 3.43 | 3.41
2017-08-31 15:00 | 3.79 | 3.77
2017-08-31 15:30 | 4.2 | 4.17
2017-08-31 16:00 | 5.36 | 5.35
2017-08-31 16:30 | 6.3 | 6.29
2017-08-31 17:00 | 7.49 | 7.48
2017-08-31 17:30 | 8.49 | 8.48
2017-08-31 18:00 | 9.65 | 9.64
2017-08-31 18:30 | 10.74 | 10.72
2017-08-31 19:00 | 11.04 | 11.02
2017-08-31 19:30 | 11.03 | 11.01
2017-08-31 20:00 | 10.95 | 10.94
2017-08-31 20:30 | 11.04 | 11.03
2017-08-31 21:00 | 10.71 | 10.7
2017-08-31 21:30 | 10.04 | 10.03
2017-08-31 22:00 | 9.3 | 9.28
2017-08-31 22:30 | 8.71 | 8.7
2017-08-31 23:00 | 8.45 | 8.44
2017-08-31 23:30 | 7.39 | 7.38
2017-09-01 | 6.37 | 6.36
2017-09-01 00:30 | 5.69 | 5.68
2017-09-01 01:00 | 5.34 | 5.32
2017-09-01 01:30 | 4.9 | 4.88
2017-09-01 02:00 | 4.63 | 4.62
2017-09-01 02:30 | 4.5 | 4.48
2017-09-01 03:00 | 4.45 | 4.43
2017-09-01 03:30 | 4.51 | 4.49
2017-09-01 04:00 | 4.53 | 4.51
2017-09-01 04:30 | 4.84 | 4.83
2017-09-01 05:00 | 5.24 | 5.23
2017-09-01 05:30 | 5.96 | 5.95
2017-09-01 06:00 | 6.45 | 6.44
2017-09-01 06:30 | 7.3 | 7.29
2017-09-01 07:00 | 8 | 7.99
2017-09-01 07:30 | 7.87 | 7.86
2017-09-01 08:00 | 6.86 | 6.85
2017-09-01 08:30 | 5.66 | 5.65
2017-09-01 09:00 | 4.28 | 4.26
2017-09-01 09:30 | 3.67 | 3.65
2017-09-01 10:00 | 3.21 | 3.17
2017-09-01 10:30 | 2.77 | 2.73
2017-09-01 11:00 | 2.7 | 2.65
2017-09-01 11:30 | 2.35 | 2.29
2017-09-01 12:00 | 2.22 | 2.21
2017-09-01 12:30 | 2.4 | 2.37
2017-09-01 13:00 | 2.3 | 2.27
2017-09-01 13:30 | 2.45 | 2.42
2017-09-01 14:00 | 2.95 | 2.92
2017-09-01 14:30 | 3.17 | 3.15
2017-09-01 15:00 | 3.58 | 3.55
2017-09-01 15:30 | 4.36 | 4.32
2017-09-01 16:00 | 5.22 | 5.19
2017-09-01 16:30 | 6.29 | 6.28
2017-09-01 17:00 | 7.19 | 7.18
2017-09-01 17:30 | 8.12 | 8.11
2017-09-01 18:00 | 8.84 | 8.83
2017-09-01 18:30 | 9.91 | 9.9
2017-09-01 19:00 | 10.24 | 10.23
2017-09-01 19:30 | 10.15 | 10.14
2017-09-01 20:00 | 10.17 | 10.16
2017-09-01 20:30 | 10.28 | 10.27
2017-09-01 21:00 | 9.98 | 9.97
2017-09-01 21:30 | 9.36 | 9.35
2017-09-01 22:00 | 8.88 | 8.87
2017-09-01 22:30 | 8.53 | 8.52
2017-09-01 23:00 | 8.41 | 8.39
2017-09-01 23:30 | 7.62 | 7.6
2017-09-02 | 6.66 | 6.65
2017-09-02 00:30 | 6.01 | 6
2017-09-02 01:00 | 5.64 | 5.62
2017-09-02 01:30 | 5.24 | 5.22
2017-09-02 02:00 | 4.87 | 4.85
2017-09-02 02:30 | 4.71 | 4.69
2017-09-02 03:00 | 4.47 | 4.45
2017-09-02 03:30 | 4.38 | 4.36
2017-09-02 04:00 | 4.31 | 4.28
2017-09-02 04:30 | 4.47 | 4.45
2017-09-02 05:00 | 4.59 | 4.57
2017-09-02 05:30 | 4.85 | 4.83
2017-09-02 06:00 | 4.97 | 4.94
2017-09-02 06:30 | 5.17 | 5.13
2017-09-02 07:00 | 5.53 | 5.49
2017-09-02 07:30 | 5.84 | 5.8
2017-09-02 08:00 | 5.75 | 5.72
2017-09-02 08:30 | 5.88 | 5.86
2017-09-02 09:00 | 5.22 | 5.2
2017-09-02 09:30 | 5.17 | 5.14
2017-09-02 10:00 | 4.72 | 4.69
2017-09-02 10:30 | 4.07 | 4.04
2017-09-02 11:00 | 3.65 | 3.61
2017-09-02 11:30 | 3.57 | 3.52
2017-09-02 12:00 | 3.69 | 3.64
2017-09-02 12:30 | 3.51 | 3.46
2017-09-02 13:00 | 3.18 | 3.12
2017-09-02 13:30 | 3.3 | 3.24
2017-09-02 14:00 | 3.49 | 3.45
2017-09-02 14:30 | 3.77 | 3.73
2017-09-02 15:00 | 4.2 | 4.17
2017-09-02 15:30 | 4.87 | 4.84
2017-09-02 16:00 | 5.48 | 5.46
2017-09-02 16:30 | 6.3 | 6.28
2017-09-02 17:00 | 7.27 | 7.25
2017-09-02 17:30 | 8.01 | 8
2017-09-02 18:00 | 8.77 | 8.76
2017-09-02 18:30 | 9.6 | 9.59
2017-09-02 19:00 | 9.68 | 9.66
2017-09-02 19:30 | 9.51 | 9.49
2017-09-02 20:00 | 9.23 | 9.21
2017-09-02 20:30 | 9.34 | 9.33
2017-09-02 21:00 | 8.96 | 8.95
2017-09-02 21:30 | 8.48 | 8.46
2017-09-02 22:00 | 8.23 | 8.21
2017-09-02 22:30 | 8.1 | 8.09
2017-09-02 23:00 | 7.93 | 7.92
2017-09-02 23:30 | 7.11 | 7.1
2017-09-03 | 6.33 | 6.32
2017-09-03 00:30 | 5.62 | 5.6
2017-09-03 01:00 | 5.27 | 5.26
2017-09-03 01:30 | 4.94 | 4.92
2017-09-03 02:00 | 4.51 | 4.49
2017-09-03 02:30 | 4.31 | 4.29
2017-09-03 03:00 | 4.29 | 4.27
2017-09-03 03:30 | 4.23 | 4.21
2017-09-03 04:00 | 4.2 | 4.17
2017-09-03 04:30 | 4.24 | 4.22
2017-09-03 05:00 | 4.33 | 4.31
2017-09-03 05:30 | 4.39 | 4.37
2017-09-03 06:00 | 4.55 | 4.52
2017-09-03 06:30 | 4.87 | 4.81
2017-09-03 07:00 | 5.21 | 5.15
2017-09-03 07:30 | 5.41 | 5.37
2017-09-03 08:00 | 5.48 | 5.45
2017-09-03 08:30 | 5.41 | 5.38
2017-09-03 09:00 | 5.27 | 5.24
2017-09-03 09:30 | 5.01 | 4.98
2017-09-03 10:00 | 4.74 | 4.71
2017-09-03 10:30 | 4.31 | 4.28
2017-09-03 11:00 | 3.88 | 3.84
2017-09-03 11:30 | 3.76 | 3.72
2017-09-03 12:00 | 3.66 | 3.61
2017-09-03 12:30 | 3.48 | 3.43
2017-09-03 13:00 | 3.38 | 3.33
2017-09-03 13:30 | 3.4 | 3.35
2017-09-03 14:00 | 3.88 | 3.84
2017-09-03 14:30 | 4.26 | 4.22
2017-09-03 15:00 | 4.65 | 4.61
2017-09-03 15:30 | 5.45 | 5.42
2017-09-03 16:00 | 6.21 | 6.19
2017-09-03 16:30 | 6.97 | 6.95
2017-09-03 17:00 | 7.95 | 7.94
2017-09-03 17:30 | 8.71 | 8.69
2017-09-03 18:00 | 9.56 | 9.55
2017-09-03 18:30 | 10.26 | 10.24
2017-09-03 19:00 | 10.35 | 10.34
2017-09-03 19:30 | 10.09 | 10.08
2017-09-03 20:00 | 9.96 | 9.95
2017-09-03 20:30 | 9.85 | 9.84
2017-09-03 21:00 | 9.41 | 9.4
2017-09-03 21:30 | 8.58 | 8.57
2017-09-03 22:00 | 7.94 | 7.93
2017-09-03 22:30 | 7.67 | 7.65
2017-09-03 23:00 | 7.44 | 7.43
2017-09-03 23:30 | 6.53 | 6.52
2017-09-04 | 5.65 | 5.63
2017-09-04 00:30 | 5.08 | 5.07
2017-09-04 01:00 | 4.79 | 4.77
2017-09-04 01:30 | 4.39 | 4.37
2017-09-04 02:00 | 4.1 | 4.08
2017-09-04 02:30 | 3.97 | 3.94
2017-09-04 03:00 | 3.91 | 3.89
2017-09-04 03:30 | 3.95 | 3.92
2017-09-04 04:00 | 3.94 | 3.91
2017-09-04 04:30 | 4.22 | 4.2
2017-09-04 05:00 | 4.48 | 4.46
2017-09-04 05:30 | 5.09 | 5.08
2017-09-04 06:00 | 5.47 | 5.45
2017-09-04 06:30 | 6.01 | 5.99
2017-09-04 07:00 | 6.28 | 6.26
2017-09-04 07:30 | 6.31 | 6.29
2017-09-04 08:00 | 5.69 | 5.68
2017-09-04 08:30 | 4.79 | 4.77
2017-09-04 09:00 | 3.97 | 3.95
2017-09-04 09:30 | 3.59 | 3.57
2017-09-04 10:00 | 3.38 | 3.35
2017-09-04 10:30 | 3.06 | 3.02
2017-09-04 11:00 | 2.96 | 2.92
2017-09-04 11:30 | 2.87 | 2.83
2017-09-04 12:00 | 2.73 | 2.69
2017-09-04 12:30 | 3.01 | 2.96
2017-09-04 13:00 | 3.69 | 3.66
2017-09-04 13:30 | 3.39 | 3.34
2017-09-04 14:00 | 3.74 | 3.69
2017-09-04 14:30 | 4.29 | 4.26
2017-09-04 15:00 | 4.83 | 4.8
2017-09-04 15:30 | 5.48 | 5.45
2017-09-04 16:00 | 6.54 | 6.52
2017-09-04 16:30 | 7.5 | 7.48
2017-09-04 17:00 | 8.41 | 8.4
2017-09-04 17:30 | 9.42 | 9.4
2017-09-04 18:00 | 10.25 | 10.22
2017-09-04 18:30 | 11.14 | 11.12
2017-09-04 19:00 | 11.44 | 11.42
2017-09-04 19:30 | 10.98 | 10.96
2017-09-04 20:00 | 10.64 | 10.63
2017-09-04 20:30 | 10.63 | 10.61
2017-09-04 21:00 | 9.98 | 9.96
2017-09-04 21:30 | 9.11 | 9.1
2017-09-04 22:00 | 8.28 | 8.27
2017-09-04 22:30 | 7.73 | 7.72
2017-09-04 23:00 | 7.35 | 7.33
2017-09-04 23:30 | 6.52 | 6.51
2017-09-05 | 5.57 | 5.55
2017-09-05 00:30 | 4.95 | 4.93
2017-09-05 01:00 | 4.66 | 4.64
2017-09-05 01:30 | 4.37 | 4.35
2017-09-05 02:00 | 4.17 | 4.15
2017-09-05 02:30 | 3.95 | 3.92
2017-09-05 03:00 | 3.88 | 3.85
2017-09-05 03:30 | 3.95 | 3.92
2017-09-05 04:00 | 3.99 | 3.97
2017-09-05 04:30 | 4.23 | 4.21
2017-09-05 05:00 | 4.62 | 4.6
2017-09-05 05:30 | 5.12 | 5.11
2017-09-05 06:00 | 5.55 | 5.53
2017-09-05 06:30 | 6.07 | 6.04
2017-09-05 07:00 | 6.43 | 6.4
2017-09-05 07:30 | 6.26 | 6.24
2017-09-05 08:00 | 5.62 | 5.61
2017-09-05 08:30 | 5.54 | 5.51
2017-09-05 09:00 | 3.89 | 3.84
2017-09-05 09:30 | 3.34 | 3.28
2017-09-05 10:00 | 2.88 | 2.81
2017-09-05 10:30 | 3.56 | 3.53
2017-09-05 11:00 | 3.59 | 3.59
2017-09-05 11:30 | 2.24 | 2.23
2017-09-05 12:00 | 2.35 | 2.34
2017-09-05 12:30 | 2.96 | 2.94
2017-09-05 13:00 | 2.37 | 2.34
2017-09-05 13:30 | 2.52 | 2.49
2017-09-05 14:00 | 2.94 | 2.92
2017-09-05 14:30 | 3.25 | 3.22
2017-09-05 15:00 | 3.71 | 3.69
2017-09-05 15:30 | 4.37 | 4.36
2017-09-05 16:00 | 5.49 | 5.47
2017-09-05 16:30 | 6.47 | 6.46
2017-09-05 17:00 | 7.51 | 7.5
2017-09-05 17:30 | 8.39 | 8.38
2017-09-05 18:00 | 9.52 | 9.5
2017-09-05 18:30 | 10.94 | 10.92
2017-09-05 19:00 | 11.35 | 11.32
2017-09-05 19:30 | 10.8 | 10.79
2017-09-05 20:00 | 10.6 | 10.59
2017-09-05 20:30 | 10.58 | 10.57
2017-09-05 21:00 | 9.9 | 9.88
2017-09-05 21:30 | 9.07 | 9.05
2017-09-05 22:00 | 8.36 | 8.35
2017-09-05 22:30 | 7.87 | 7.86
2017-09-05 23:00 | 7.45 | 7.43
2017-09-05 23:30 | 6.58 | 6.57
2017-09-06 | 5.74 | 5.72
2017-09-06 00:30 | 5.06 | 5.04
2017-09-06 01:00 | 4.76 | 4.74
2017-09-06 01:30 | 4.49 | 4.47
2017-09-06 02:00 | 4.28 | 4.25
2017-09-06 02:30 | 4.08 | 4.06
2017-09-06 03:00 | 4.02 | 3.99
2017-09-06 03:30 | 4.12 | 4.09
2017-09-06 04:00 | 4.15 | 4.13
2017-09-06 04:30 | 4.48 | 4.46
2017-09-06 05:00 | 4.89 | 4.87
2017-09-06 05:30 | 5.51 | 5.5
2017-09-06 06:00 | 5.98 | 5.96
2017-09-06 06:30 | 6.4 | 6.38
2017-09-06 07:00 | 6.76 | 6.74
2017-09-06 07:30 | 6.53 | 6.52
2017-09-06 08:00 | 5.86 | 5.84
2017-09-06 08:30 | 4.78 | 4.76
2017-09-06 09:00 | 3.77 | 3.74
2017-09-06 09:30 | 3.23 | 3.19
2017-09-06 10:00 | 2.89 | 2.84
2017-09-06 10:30 | 2.6 | 2.55
2017-09-06 11:00 | 2.21 | 2.17
2017-09-06 11:30 | 2.01 | 1.95
2017-09-06 12:00 | 1.95 | 1.89
2017-09-06 12:30 | 1.99 | 1.95
2017-09-06 13:00 | 2.1 | 2.05
2017-09-06 13:30 | 2.17 | 2.13
2017-09-06 14:00 | 2.61 | 2.58
2017-09-06 14:30 | 3.04 | 3.01
2017-09-06 15:00 | 3.33 | 3.31
2017-09-06 15:30 | 4.21 | 4.19
2017-09-06 16:00 | 5.16 | 5.15
2017-09-06 16:30 | 6.16 | 6.15
2017-09-06 17:00 | 7.26 | 7.25
2017-09-06 17:30 | 8.12 | 8.1
2017-09-06 18:00 | 9.29 | 9.27
2017-09-06 18:30 | 10.48 | 10.47
2017-09-06 19:00 | 10.97 | 10.96
2017-09-06 19:30 | 10.8 | 10.78
2017-09-06 20:00 | 10.63 | 10.61
2017-09-06 20:30 | 10.83 | 10.82
2017-09-06 21:00 | 10.46 | 10.45
2017-09-06 21:30 | 9.73 | 9.72
2017-09-06 22:00 | 9.01 | 9
2017-09-06 22:30 | 8.34 | 8.33
2017-09-06 23:00 | 7.86 | 7.85
2017-09-06 23:30 | 6.83 | 6.82
2017-09-07 | 5.94 | 5.93
2017-09-07 00:30 | 5.26 | 5.25
2017-09-07 01:00 | 4.98 | 4.96
2017-09-07 01:30 | 4.61 | 4.59
2017-09-07 02:00 | 4.6 | 4.57
2017-09-07 02:30 | 4.65 | 4.62
2017-09-07 03:00 | 4.51 | 4.48
2017-09-07 03:30 | 4.54 | 4.51
2017-09-07 04:00 | 4.62 | 4.59
2017-09-07 04:30 | 4.52 | 4.5
2017-09-07 05:00 | 4.95 | 4.93
2017-09-07 05:30 | 5.55 | 5.54
2017-09-07 06:00 | 6.08 | 6.06
2017-09-07 06:30 | 6.64 | 6.61
2017-09-07 07:00 | 7.06 | 7.04
2017-09-07 07:30 | 6.89 | 6.88
2017-09-07 08:00 | 6.11 | 6.09
2017-09-07 08:30 | 4.92 | 4.91
2017-09-07 09:00 | 3.89 | 3.87
2017-09-07 09:30 | 3.55 | 3.52
2017-09-07 10:00 | 3.07 | 3.06
2017-09-07 10:30 | 2.85 | 2.84
2017-09-07 11:00 | 2.58 | 2.57
2017-09-07 11:30 | 2.17 | 2.16
2017-09-07 12:00 | 2.01 | 1.98
2017-09-07 12:30 | 1.92 | 1.89
2017-09-07 13:00 | 2.04 | 2
2017-09-07 13:30 | 2.45 | 2.42
2017-09-07 14:00 | 2.8 | 2.77
2017-09-07 14:30 | 3.32 | 3.3
2017-09-07 15:00 | 3.87 | 3.86
2017-09-07 15:30 | 4.58 | 4.56
2017-09-07 16:00 | 5.56 | 5.55
2017-09-07 16:30 | 6.28 | 6.27
2017-09-07 17:00 | 7.3 | 7.29
2017-09-07 17:30 | 8.07 | 8.06
2017-09-07 18:00 | 9.07 | 9.06
2017-09-07 18:30 | 10.18 | 10.16
2017-09-07 19:00 | 10.59 | 10.58
2017-09-07 19:30 | 10.34 | 10.33
2017-09-07 20:00 | 10.38 | 10.37
2017-09-07 20:30 | 10.49 | 10.48
2017-09-07 21:00 | 10.09 | 10.08
2017-09-07 21:30 | 9.38 | 9.37
2017-09-07 22:00 | 8.72 | 8.71
2017-09-07 22:30 | 8.28 | 8.27
2017-09-07 23:00 | 7.82 | 7.81
2017-09-07 23:30 | 6.94 | 6.93
2017-09-08 | 6.06 | 6.04
2017-09-08 00:30 | 5.31 | 5.29
2017-09-08 01:00 | 5.02 | 5
2017-09-08 01:30 | 4.64 | 4.62
2017-09-08 02:00 | 4.35 | 4.33
2017-09-08 02:30 | 4.2 | 4.17
2017-09-08 03:00 | 4.13 | 4.11
2017-09-08 03:30 | 4.21 | 4.19
2017-09-08 04:00 | 4.25 | 4.22
2017-09-08 04:30 | 4.51 | 4.49
2017-09-08 05:00 | 4.88 | 4.87
2017-09-08 05:30 | 5.58 | 5.57
2017-09-08 06:00 | 6.86 | 6.84
2017-09-08 06:30 | 8.36 | 8.32
2017-09-08 07:00 | 8.6 | 8.56
2017-09-08 07:30 | 8.52 | 8.49
2017-09-08 08:00 | 7.82 | 7.79
2017-09-08 08:30 | 6.59 | 6.56
2017-09-08 09:00 | 5.54 | 5.5
2017-09-08 09:30 | 4.99 | 4.94
2017-09-08 10:00 | 4.64 | 4.59
2017-09-08 10:30 | 4.13 | 4.08
2017-09-08 11:00 | 3.83 | 3.77
2017-09-08 11:30 | 3.72 | 3.66
2017-09-08 12:00 | 3.58 | 3.5
2017-09-08 12:30 | 3.56 | 3.46
2017-09-08 13:00 | 3.68 | 3.58
2017-09-08 13:30 | 3.86 | 3.77
2017-09-08 14:00 | 4.11 | 4.02
2017-09-08 14:30 | 4.49 | 4.43
2017-09-08 15:00 | 5.1 | 5.05
2017-09-08 15:30 | 5.74 | 5.7
2017-09-08 16:00 | 6.67 | 6.63
2017-09-08 16:30 | 7.59 | 7.55
2017-09-08 17:00 | 8.51 | 8.51
2017-09-08 17:30 | 9.17 | 9.16
2017-09-08 18:00 | 9.84 | 9.83
2017-09-08 18:30 | 9.74 | 9.72
2017-09-08 19:00 | 10.2 | 10.18
2017-09-08 19:30 | 9.93 | 9.92
2017-09-08 20:00 | 9.92 | 9.91
2017-09-08 20:30 | 9.98 | 9.97
2017-09-08 21:00 | 9.59 | 9.58
2017-09-08 21:30 | 9.05 | 9.04
2017-09-08 22:00 | 8.6 | 8.59
2017-09-08 22:30 | 8.51 | 8.5
2017-09-08 23:00 | 8.21 | 8.2
2017-09-08 23:30 | 7.29 | 7.29
2017-09-09 | 6.47 | 6.46
2017-09-09 00:30 | 5.83 | 5.82
2017-09-09 01:00 | 5.52 | 5.5
2017-09-09 01:30 | 5.09 | 5.07
2017-09-09 02:00 | 4.78 | 4.77
2017-09-09 02:30 | 4.55 | 4.54
2017-09-09 03:00 | 4.53 | 4.5
2017-09-09 03:30 | 4.52 | 4.5
2017-09-09 04:00 | 4.47 | 4.45
2017-09-09 04:30 | 4.54 | 4.52
2017-09-09 05:00 | 4.66 | 4.64
2017-09-09 05:30 | 4.92 | 4.91
2017-09-09 06:00 | 5 | 4.97
2017-09-09 06:30 | 5.37 | 5.33
2017-09-09 07:00 | 5.39 | 5.34
2017-09-09 07:30 | 5.4 | 5.37
2017-09-09 08:00 | 5.25 | 5.22
2017-09-09 08:30 | 5.18 | 5.15
2017-09-09 09:00 | 5.14 | 5.13
2017-09-09 09:30 | 4.84 | 4.82
2017-09-09 10:00 | 4.38 | 4.37
2017-09-09 10:30 | 3.71 | 3.69
2017-09-09 11:00 | 3.29 | 3.26
2017-09-09 11:30 | 3.13 | 3.08
2017-09-09 12:00 | 2.99 | 2.95
2017-09-09 12:30 | 3.06 | 3.01
2017-09-09 13:00 | 2.99 | 2.95
2017-09-09 13:30 | 3.13 | 3.08
2017-09-09 14:00 | 3.43 | 3.38
2017-09-09 14:30 | 3.77 | 3.74
2017-09-09 15:00 | 4.33 | 4.31
2017-09-09 15:30 | 5.01 | 4.99
2017-09-09 16:00 | 6 | 5.98
2017-09-09 16:30 | 6.51 | 6.49
2017-09-09 17:00 | 7.2 | 7.18
2017-09-09 17:30 | 8.12 | 8.11
2017-09-09 18:00 | 9.03 | 9.03
2017-09-09 18:30 | 9.6 | 9.59
2017-09-09 19:00 | 9.85 | 9.84
2017-09-09 19:30 | 9.69 | 9.68
2017-09-09 20:00 | 9.67 | 9.66
2017-09-09 20:30 | 9.69 | 9.68
2017-09-09 21:00 | 9.27 | 9.26
2017-09-09 21:30 | 8.77 | 8.76
2017-09-09 22:00 | 8.27 | 8.26
2017-09-09 22:30 | 8.15 | 8.14
2017-09-09 23:00 | 8.13 | 8.12
2017-09-09 23:30 | 7.21 | 7.2
2017-09-10 | 6.35 | 6.34
2017-09-10 00:30 | 5.67 | 5.65
2017-09-10 01:00 | 5.32 | 5.31
2017-09-10 01:30 | 4.86 | 4.85
2017-09-10 02:00 | 4.57 | 4.55
2017-09-10 02:30 | 4.38 | 4.36
2017-09-10 03:00 | 4.36 | 4.34
2017-09-10 03:30 | 4.29 | 4.27
2017-09-10 04:00 | 4.18 | 4.16
2017-09-10 04:30 | 4.29 | 4.27
2017-09-10 05:00 | 4.33 | 4.31
2017-09-10 05:30 | 4.5 | 4.47
2017-09-10 06:00 | 4.52 | 4.47
2017-09-10 06:30 | 4.66 | 4.59
2017-09-10 07:00 | 4.84 | 4.78
2017-09-10 07:30 | 4.93 | 4.88
2017-09-10 08:00 | 4.89 | 4.85
2017-09-10 08:30 | 4.76 | 4.72
2017-09-10 09:00 | 4.58 | 4.55
2017-09-10 09:30 | 4.35 | 4.32
2017-09-10 10:00 | 4.1 | 4.07
2017-09-10 10:30 | 3.85 | 3.82
2017-09-10 11:00 | 3.7 | 3.67
2017-09-10 11:30 | 3.55 | 3.51
2017-09-10 12:00 | 3.31 | 3.26
2017-09-10 12:30 | 3.27 | 3.22
2017-09-10 13:00 | 3.37 | 3.32
2017-09-10 13:30 | 3.5 | 3.45
2017-09-10 14:00 | 3.93 | 3.88
2017-09-10 14:30 | 4.42 | 4.39
2017-09-10 15:00 | 4.82 | 4.79
2017-09-10 15:30 | 5.34 | 5.31
2017-09-10 16:00 | 6.11 | 6.09
2017-09-10 16:30 | 6.95 | 6.93
2017-09-10 17:00 | 7.83 | 7.81
2017-09-10 17:30 | 8.9 | 8.89
2017-09-10 18:00 | 9.8 | 9.79
2017-09-10 18:30 | 10.74 | 10.72
2017-09-10 19:00 | 10.89 | 10.88
2017-09-10 19:30 | 10.43 | 10.42
2017-09-10 20:00 | 10.07 | 10.06
2017-09-10 20:30 | 10.23 | 10.22
2017-09-10 21:00 | 9.54 | 9.53
2017-09-10 21:30 | 8.8 | 8.79
2017-09-10 22:00 | 8.18 | 8.17
2017-09-10 22:30 | 7.91 | 7.89
2017-09-10 23:00 | 7.64 | 7.63
2017-09-10 23:30 | 6.72 | 6.71
2017-09-11 | 5.85 | 5.84
2017-09-11 00:30 | 5.25 | 5.24
2017-09-11 01:00 | 4.87 | 4.86
2017-09-11 01:30 | 4.55 | 4.53
2017-09-11 02:00 | 4.24 | 4.22
2017-09-11 02:30 | 4.03 | 4.01
2017-09-11 03:00 | 4 | 3.97
2017-09-11 03:30 | 4.05 | 4.02
2017-09-11 04:00 | 4.01 | 3.98
2017-09-11 04:30 | 4.33 | 4.31
2017-09-11 05:00 | 4.68 | 4.66
2017-09-11 05:30 | 5.31 | 5.3
2017-09-11 06:00 | 5.73 | 5.7
2017-09-11 06:30 | 6.3 | 6.27
2017-09-11 07:00 | 6.64 | 6.62
2017-09-11 07:30 | 6.7 | 6.68
2017-09-11 08:00 | 7.09 | 7.08
2017-09-11 08:30 | 6.13 | 6.12
2017-09-11 09:00 | 4.92 | 4.9
2017-09-11 09:30 | 3.65 | 3.63
2017-09-11 10:00 | 3.34 | 3.3
2017-09-11 10:30 | 2.97 | 2.95
2017-09-11 11:00 | 2.6 | 2.57
2017-09-11 11:30 | 2.56 | 2.53
2017-09-11 12:00 | 2.59 | 2.55
2017-09-11 12:30 | 2.6 | 2.57
2017-09-11 13:00 | 2.84 | 2.81
2017-09-11 13:30 | 3.02 | 3
2017-09-11 14:00 | 3.46 | 3.45
2017-09-11 14:30 | 3.8 | 3.79
2017-09-11 15:00 | 4.27 | 4.26
2017-09-11 15:30 | 4.87 | 4.86
2017-09-11 16:00 | 5.79 | 5.78
2017-09-11 16:30 | 6.79 | 6.78
2017-09-11 17:00 | 7.79 | 7.77
2017-09-11 17:30 | 8.72 | 8.7
2017-09-11 18:00 | 9.72 | 9.71
2017-09-11 18:30 | 10.94 | 10.93
2017-09-11 19:00 | 11.15 | 11.13
2017-09-11 19:30 | 10.75 | 10.73
2017-09-11 20:00 | 10.65 | 10.64
2017-09-11 20:30 | 10.56 | 10.55
2017-09-11 21:00 | 9.87 | 9.86
2017-09-11 21:30 | 9.07 | 9.06
2017-09-11 22:00 | 8.16 | 8.15
2017-09-11 22:30 | 7.69 | 7.68
2017-09-11 23:00 | 7.38 | 7.37
2017-09-11 23:30 | 6.45 | 6.44
2017-09-12 | 5.63 | 5.61
2017-09-12 00:30 | 5.01 | 5
2017-09-12 01:00 | 4.71 | 4.7
2017-09-12 01:30 | 4.43 | 4.42
2017-09-12 02:00 | 4.17 | 4.15
2017-09-12 02:30 | 4 | 3.98
2017-09-12 03:00 | 3.98 | 3.95
2017-09-12 03:30 | 4.02 | 4
2017-09-12 04:00 | 5.01 | 4.98
2017-09-12 04:30 | 5.35 | 5.33
2017-09-12 05:00 | 5.64 | 5.62
2017-09-12 05:30 | 5.92 | 5.91
2017-09-12 06:00 | 6.4 | 6.37
2017-09-12 06:30 | 6.71 | 6.67
2017-09-12 07:00 | 6.93 | 6.9
2017-09-12 07:30 | 6.26 | 6.24
2017-09-12 08:00 | 5.5 | 5.48
2017-09-12 08:30 | 4.51 | 4.49
2017-09-12 09:00 | 3.62 | 3.6
2017-09-12 09:30 | 3.3 | 3.28
2017-09-12 10:00 | 2.9 | 2.87
2017-09-12 10:30 | 2.65 | 2.62
2017-09-12 11:00 | 2.42 | 2.39
2017-09-12 11:30 | 2.37 | 2.32
2017-09-12 12:00 | 2.53 | 2.5
2017-09-12 12:30 | 2.81 | 2.78
2017-09-12 13:00 | 3.22 | 3.2
2017-09-12 13:30 | 3.5 | 3.48
2017-09-12 14:00 | 3.93 | 3.9
2017-09-12 14:30 | 4.39 | 4.37
2017-09-12 15:00 | 4.74 | 4.72
2017-09-12 15:30 | 5.52 | 5.5
2017-09-12 16:00 | 7.47 | 7.47
2017-09-12 16:30 | 7.45 | 7.44
2017-09-12 17:00 | 8.31 | 8.3
2017-09-12 17:30 | 9.1 | 9.09
2017-09-12 18:00 | 9.92 | 9.9
2017-09-12 18:30 | 11.06 | 11.03
2017-09-12 19:00 | 11.47 | 11.44
2017-09-12 19:30 | 10.99 | 10.97
2017-09-12 20:00 | 10.77 | 10.76
2017-09-12 20:30 | 10.79 | 10.78
2017-09-12 21:00 | 10.16 | 10.15
2017-09-12 21:30 | 9.36 | 9.36
2017-09-12 22:00 | 8.48 | 8.48
2017-09-12 22:30 | 7.93 | 7.92
2017-09-12 23:00 | 7.48 | 7.46
2017-09-12 23:30 | 6.48 | 6.47
2017-09-13 | 5.71 | 5.69
2017-09-13 00:30 | 5.03 | 5.01
2017-09-13 01:00 | 4.78 | 4.76
2017-09-13 01:30 | 4.41 | 4.39
2017-09-13 02:00 | 4.14 | 4.12
2017-09-13 02:30 | 3.99 | 3.97
2017-09-13 03:00 | 3.91 | 3.89
2017-09-13 03:30 | 3.99 | 3.97
2017-09-13 04:00 | 3.97 | 3.95
2017-09-13 04:30 | 4.17 | 4.15
2017-09-13 05:00 | 4.44 | 4.41
2017-09-13 05:30 | 4.99 | 4.98
2017-09-13 06:00 | 5.57 | 5.56
2017-09-13 06:30 | 6.22 | 6.21
2017-09-13 07:00 | 6.56 | 6.54
2017-09-13 07:30 | 6.69 | 6.68
2017-09-13 08:00 | 5.68 | 5.67
2017-09-13 08:30 | 4.64 | 4.63
2017-09-13 09:00 | 3.88 | 3.86
2017-09-13 09:30 | 3.59 | 3.57
2017-09-13 10:00 | 3.37 | 3.34
2017-09-13 10:30 | 3.18 | 3.15
2017-09-13 11:00 | 3.12 | 3.08
2017-09-13 11:30 | 3.05 | 3.01
2017-09-13 12:00 | 3.08 | 3.04
2017-09-13 12:30 | 4.21 | 4.19
2017-09-13 13:00 | 5.49 | 5.47
2017-09-13 13:30 | 5.51 | 5.49
2017-09-13 14:00 | 5.74 | 5.72
2017-09-13 14:30 | 4.95 | 4.92
2017-09-13 15:00 | 5.51 | 5.48
2017-09-13 15:30 | 6.28 | 6.26
2017-09-13 16:00 | 7.18 | 7.17
2017-09-13 16:30 | 8.12 | 8.1
2017-09-13 17:00 | 9.2 | 9.19
2017-09-13 17:30 | 9.94 | 9.93
2017-09-13 18:00 | 10.55 | 10.53
2017-09-13 18:30 | 11.44 | 11.41
2017-09-13 19:00 | 11.75 | 11.71
2017-09-13 19:30 | 11.51 | 11.48
2017-09-13 20:00 | 11.32 | 11.3
2017-09-13 20:30 | 11.29 | 11.27
2017-09-13 21:00 | 10.5 | 10.49
2017-09-13 21:30 | 9.8 | 9.79
2017-09-13 22:00 | 8.74 | 8.74
2017-09-13 22:30 | 7.99 | 7.98
2017-09-13 23:00 | 7.44 | 7.43
2017-09-13 23:30 | 6.47 | 6.46
2017-09-14 | 5.69 | 5.68
2017-09-14 00:30 | 5.08 | 5.07
2017-09-14 01:00 | 4.8 | 4.79
2017-09-14 01:30 | 4.46 | 4.44
2017-09-14 02:00 | 4.3 | 4.28
2017-09-14 02:30 | 4.11 | 4.09
2017-09-14 03:00 | 4.03 | 4.01
2017-09-14 03:30 | 4 | 3.98
2017-09-14 04:00 | 3.98 | 3.96
2017-09-14 04:30 | 4.12 | 4.1
2017-09-14 05:00 | 4.48 | 4.46
2017-09-14 05:30 | 4.93 | 4.91
2017-09-14 06:00 | 5.34 | 5.32
2017-09-14 06:30 | 5.69 | 5.67
2017-09-14 07:00 | 6.08 | 6.06
2017-09-14 07:30 | 7 | 6.99
2017-09-14 08:00 | 7.23 | 7.22
2017-09-14 08:30 | 6.86 | 6.86
2017-09-14 09:00 | 5.9 | 5.9
2017-09-14 09:30 | 4.28 | 4.28
2017-09-14 10:00 | 3.27 | 3.26
2017-09-14 10:30 | 2.99 | 2.98
2017-09-14 11:00 | 2.55 | 2.52
2017-09-14 11:30 | 2.54 | 2.51
2017-09-14 12:00 | 2.6 | 2.58
2017-09-14 12:30 | 2.67 | 2.65
2017-09-14 13:00 | 2.44 | 2.41
2017-09-14 13:30 | 2.51 | 2.48
2017-09-14 14:00 | 2.83 | 2.81
2017-09-14 14:30 | 3.26 | 3.23
2017-09-14 15:00 | 3.82 | 3.8
2017-09-14 15:30 | 4.41 | 4.4
2017-09-14 16:00 | 5.52 | 5.51
2017-09-14 16:30 | 6.38 | 6.37
2017-09-14 17:00 | 7.25 | 7.24
2017-09-14 17:30 | 8.17 | 8.16
2017-09-14 18:00 | 9.28 | 9.27
2017-09-14 18:30 | 10.41 | 10.4
2017-09-14 19:00 | 10.8 | 10.79
2017-09-14 19:30 | 10.29 | 10.29
2017-09-14 20:00 | 10.07 | 10.06
2017-09-14 20:30 | 10.3 | 10.29
2017-09-14 21:00 | 9.85 | 9.84
2017-09-14 21:30 | 9.01 | 9
2017-09-14 22:00 | 8.48 | 8.47
2017-09-14 22:30 | 8.08 | 8.07
2017-09-14 23:00 | 7.77 | 7.76
2017-09-14 23:30 | 6.76 | 6.75
2017-09-15 | 5.82 | 5.81
2017-09-15 00:30 | 5.19 | 5.18
2017-09-15 01:00 | 4.88 | 4.87
2017-09-15 01:30 | 4.64 | 4.62
2017-09-15 02:00 | 4.37 | 4.35
2017-09-15 02:30 | 4.25 | 4.22
2017-09-15 03:00 | 4.19 | 4.16
2017-09-15 03:30 | 4.24 | 4.22
2017-09-15 04:00 | 4.28 | 4.25
2017-09-15 04:30 | 4.53 | 4.51
2017-09-15 05:00 | 4.87 | 4.85
2017-09-15 05:30 | 5.58 | 5.57
2017-09-15 06:00 | 5.96 | 5.92
2017-09-15 06:30 | 6.55 | 6.52
2017-09-15 07:00 | 6.92 | 6.9
2017-09-15 07:30 | 6.74 | 6.73
2017-09-15 08:00 | 6.03 | 6.02
2017-09-15 08:30 | 4.88 | 4.86
2017-09-15 09:00 | 4 | 3.98
2017-09-15 09:30 | 3.58 | 3.54
2017-09-15 10:00 | 3.09 | 3.05
2017-09-15 10:30 | 2.63 | 2.59
2017-09-15 11:00 | 2.33 | 2.27
2017-09-15 11:30 | 2.17 | 2.1
2017-09-15 12:00 | 1.98 | 1.91
2017-09-15 12:30 | 1.86 | 1.81
2017-09-15 13:00 | 1.92 | 1.87
2017-09-15 13:30 | 2.21 | 2.15
2017-09-15 14:00 | 2.56 | 2.51
2017-09-15 14:30 | 2.95 | 2.91
2017-09-15 15:00 | 3.34 | 3.31
2017-09-15 15:30 | 4.11 | 4.08
2017-09-15 16:00 | 5 | 4.98
2017-09-15 16:30 | 5.87 | 5.84
2017-09-15 17:00 | 6.76 | 6.75
2017-09-15 17:30 | 7.68 | 7.67
2017-09-15 18:00 | 8.5 | 8.49
2017-09-15 18:30 | 9.37 | 9.36
2017-09-15 19:00 | 9.83 | 9.82
2017-09-15 19:30 | 9.78 | 9.77
2017-09-15 20:00 | 9.89 | 9.88
2017-09-15 20:30 | 9.91 | 9.9
2017-09-15 21:00 | 9.47 | 9.45
2017-09-15 21:30 | 8.92 | 8.91
2017-09-15 22:00 | 8.45 | 8.43
2017-09-15 22:30 | 8.06 | 8.05
2017-09-15 23:00 | 7.93 | 7.92
2017-09-15 23:30 | 7.15 | 7.14
2017-09-16 | 6.3 | 6.29
2017-09-16 00:30 | 5.62 | 5.6
2017-09-16 01:00 | 5.29 | 5.27
2017-09-16 01:30 | 4.94 | 4.92
2017-09-16 02:00 | 4.6 | 4.58
2017-09-16 02:30 | 4.41 | 4.39
2017-09-16 03:00 | 4.31 | 4.28
2017-09-16 03:30 | 4.37 | 4.35
2017-09-16 04:00 | 4.3 | 4.28
2017-09-16 04:30 | 4.37 | 4.34
2017-09-16 05:00 | 4.66 | 4.64
2017-09-16 05:30 | 4.85 | 4.82
2017-09-16 06:00 | 4.84 | 4.79
2017-09-16 06:30 | 5.03 | 4.96
2017-09-16 07:00 | 4.99 | 4.93
2017-09-16 07:30 | 5.08 | 5.03
2017-09-16 08:00 | 4.82 | 4.77
2017-09-16 08:30 | 4.67 | 4.64
2017-09-16 09:00 | 4.43 | 4.4
2017-09-16 09:30 | 4.03 | 4
2017-09-16 10:00 | 3.85 | 3.81
2017-09-16 10:30 | 3.45 | 3.41
2017-09-16 11:00 | 3.19 | 3.14
2017-09-16 11:30 | 2.96 | 2.91
2017-09-16 12:00 | 2.8 | 2.74
2017-09-16 12:30 | 2.71 | 2.65
2017-09-16 13:00 | 2.69 | 2.63
2017-09-16 13:30 | 2.81 | 2.75
2017-09-16 14:00 | 3.2 | 3.15
2017-09-16 14:30 | 3.59 | 3.54
2017-09-16 15:00 | 4 | 3.96
2017-09-16 15:30 | 4.58 | 4.56
2017-09-16 16:00 | 5.23 | 5.21
2017-09-16 16:30 | 6.34 | 6.32
2017-09-16 17:00 | 6.97 | 6.95
2017-09-16 17:30 | 7.44 | 7.43
2017-09-16 18:00 | 8.14 | 8.12
2017-09-16 18:30 | 9.08 | 9.06
2017-09-16 19:00 | 9.45 | 9.44
2017-09-16 19:30 | 9.2 | 9.19
2017-09-16 20:00 | 9.16 | 9.15
2017-09-16 20:30 | 9.11 | 9.1
2017-09-16 21:00 | 8.79 | 8.78
2017-09-16 21:30 | 8.09 | 8.07
2017-09-16 22:00 | 7.72 | 7.71
2017-09-16 22:30 | 7.73 | 7.72
2017-09-16 23:00 | 7.56 | 7.55
2017-09-16 23:30 | 6.72 | 6.71
2017-09-17 | 5.94 | 5.93
2017-09-17 00:30 | 5.37 | 5.35
2017-09-17 01:00 | 4.95 | 4.94
2017-09-17 01:30 | 4.61 | 4.59
2017-09-17 02:00 | 4.39 | 4.36
2017-09-17 02:30 | 4.1 | 4.08
2017-09-17 03:00 | 3.98 | 3.95
2017-09-17 03:30 | 3.87 | 3.84
2017-09-17 04:00 | 3.82 | 3.79
2017-09-17 04:30 | 3.92 | 3.89
2017-09-17 05:00 | 4.05 | 4.03
2017-09-17 05:30 | 4.11 | 4.08
2017-09-17 06:00 | 4.24 | 4.18
2017-09-17 06:30 | 4.28 | 4.19
2017-09-17 07:00 | 4.42 | 4.33
2017-09-17 07:30 | 4.68 | 4.61
2017-09-17 08:00 | 4.71 | 4.66
2017-09-17 08:30 | 5.24 | 5.2
2017-09-17 09:00 | 5.5 | 5.47
2017-09-17 09:30 | 5.15 | 5.13
2017-09-17 10:00 | 3.88 | 3.85
2017-09-17 10:30 | 4.32 | 4.3
2017-09-17 11:00 | 3.64 | 3.6
2017-09-17 11:30 | 4.31 | 4.27
2017-09-17 12:00 | 4.27 | 4.23
2017-09-17 12:30 | 3.58 | 3.53
2017-09-17 13:00 | 4.59 | 4.55
2017-09-17 13:30 | 3.88 | 3.85
2017-09-17 14:00 | 4.47 | 4.43
2017-09-17 14:30 | 4.58 | 4.56
2017-09-17 15:00 | 5.75 | 5.73
2017-09-17 15:30 | 5.31 | 5.29
2017-09-17 16:00 | 5.75 | 5.73
2017-09-17 16:30 | 6.53 | 6.51
2017-09-17 17:00 | 7.52 | 7.5
2017-09-17 17:30 | 8.38 | 8.37
2017-09-17 18:00 | 9.4 | 9.39
2017-09-17 18:30 | 10.27 | 10.25
2017-09-17 19:00 | 10.28 | 10.27
2017-09-17 19:30 | 9.9 | 9.89
2017-09-17 20:00 | 9.64 | 9.63
2017-09-17 20:30 | 9.56 | 9.55
2017-09-17 21:00 | 9.09 | 9.08
2017-09-17 21:30 | 8.37 | 8.36
2017-09-17 22:00 | 7.91 | 7.9
2017-09-17 22:30 | 7.55 | 7.54
2017-09-17 23:00 | 7.38 | 7.37
2017-09-17 23:30 | 6.48 | 6.46
2017-09-18 | 5.59 | 5.58
2017-09-18 00:30 | 4.94 | 4.92
2017-09-18 01:00 | 4.61 | 4.59
2017-09-18 01:30 | 4.35 | 4.33
2017-09-18 02:00 | 4.07 | 4.04
2017-09-18 02:30 | 3.95 | 3.93
2017-09-18 03:00 | 3.89 | 3.86
2017-09-18 03:30 | 3.89 | 3.86
2017-09-18 04:00 | 3.89 | 3.86
2017-09-18 04:30 | 4.11 | 4.08
2017-09-18 05:00 | 4.4 | 4.38
2017-09-18 05:30 | 4.84 | 4.83
2017-09-18 06:00 | 5.49 | 5.46
2017-09-18 06:30 | 5.88 | 5.85
2017-09-18 07:00 | 5.67 | 5.64
2017-09-18 07:30 | 5.43 | 5.41
2017-09-18 08:00 | 5.34 | 5.32
2017-09-18 08:30 | 4.53 | 4.52
2017-09-18 09:00 | 4.65 | 4.64
2017-09-18 09:30 | 5.02 | 5.01
2017-09-18 10:00 | 4.99 | 4.98
2017-09-18 10:30 | 4.39 | 4.37
2017-09-18 11:00 | 4.18 | 4.17
2017-09-18 11:30 | 4.67 | 4.67
2017-09-18 12:00 | 4.93 | 4.92
2017-09-18 12:30 | 4.84 | 4.83
2017-09-18 13:00 | 4.82 | 4.81
2017-09-18 13:30 | 4.76 | 4.75
2017-09-18 14:00 | 4.18 | 4.17
2017-09-18 14:30 | 3.99 | 3.95
2017-09-18 15:00 | 4.57 | 4.54
2017-09-18 15:30 | 5.19 | 5.17
2017-09-18 16:00 | 5.92 | 5.91
2017-09-18 16:30 | 6.98 | 6.97
2017-09-18 17:00 | 7.93 | 7.93
2017-09-18 17:30 | 8.65 | 8.64
2017-09-18 18:00 | 9.71 | 9.7
2017-09-18 18:30 | 10.99 | 10.97
2017-09-18 19:00 | 11.41 | 11.4
2017-09-18 19:30 | 10.96 | 10.94
2017-09-18 20:00 | 10.71 | 10.7
2017-09-18 20:30 | 10.6 | 10.59
2017-09-18 21:00 | 9.99 | 9.99
2017-09-18 21:30 | 9.32 | 9.32
2017-09-18 22:00 | 8.58 | 8.58
2017-09-18 22:30 | 7.84 | 7.84
2017-09-18 23:00 | 7.48 | 7.47
2017-09-18 23:30 | 6.53 | 6.52
2017-09-19 | 5.66 | 5.65
2017-09-19 00:30 | 4.97 | 4.96
2017-09-19 01:00 | 4.67 | 4.65
2017-09-19 01:30 | 4.4 | 4.37
2017-09-19 02:00 | 4.13 | 4.1
2017-09-19 02:30 | 3.92 | 3.89
2017-09-19 03:00 | 3.96 | 3.93
2017-09-19 03:30 | 3.91 | 3.88
2017-09-19 04:00 | 3.99 | 3.96
2017-09-19 04:30 | 4.22 | 4.19
2017-09-19 05:00 | 4.57 | 4.54
2017-09-19 05:30 | 4.96 | 4.94
2017-09-19 06:00 | 5.52 | 5.49
2017-09-19 06:30 | 5.81 | 5.78
2017-09-19 07:00 | 5.67 | 5.64
2017-09-19 07:30 | 5.38 | 5.35
2017-09-19 08:00 | 4.93 | 4.91
2017-09-19 08:30 | 4.59 | 4.57
2017-09-19 09:00 | 4.03 | 4.02
2017-09-19 09:30 | 3.76 | 3.76
2017-09-19 10:00 | 3.55 | 3.55
2017-09-19 10:30 | 3.19 | 3.19
2017-09-19 11:00 | 3.13 | 3.13
2017-09-19 11:30 | 3.1 | 3.1
2017-09-19 12:00 | 3.13 | 3.12
2017-09-19 12:30 | 3.22 | 3.22
2017-09-19 13:00 | 3.33 | 3.32
2017-09-19 13:30 | 3.65 | 3.63
2017-09-19 14:00 | 3.97 | 3.95
2017-09-19 14:30 | 4.59 | 4.57
2017-09-19 15:00 | 5.1 | 5.09
2017-09-19 15:30 | 5.93 | 5.91
2017-09-19 16:00 | 6.81 | 6.79
2017-09-19 16:30 | 7.48 | 7.47
2017-09-19 17:00 | 8.26 | 8.26
2017-09-19 17:30 | 9.3 | 9.3
2017-09-19 18:00 | 10.07 | 10.06
2017-09-19 18:30 | 11.05 | 11.03
2017-09-19 19:00 | 11.38 | 11.35
2017-09-19 19:30 | 10.91 | 10.89
2017-09-19 20:00 | 10.85 | 10.83
2017-09-19 20:30 | 10.63 | 10.62
2017-09-19 21:00 | 10.05 | 10.04
2017-09-19 21:30 | 9.29 | 9.28
2017-09-19 22:00 | 8.45 | 8.45
2017-09-19 22:30 | 7.76 | 7.76
2017-09-19 23:00 | 7.26 | 7.24
2017-09-19 23:30 | 6.38 | 6.37
2017-09-20 | 5.52 | 5.51
2017-09-20 00:30 | 4.89 | 4.88
2017-09-20 01:00 | 4.71 | 4.7
2017-09-20 01:30 | 4.48 | 4.47
2017-09-20 02:00 | 4.18 | 4.16
2017-09-20 02:30 | 4.01 | 3.99
2017-09-20 03:00 | 3.96 | 3.94
2017-09-20 03:30 | 3.91 | 3.89
2017-09-20 04:00 | 3.97 | 3.95
2017-09-20 04:30 | 4.16 | 4.15
2017-09-20 05:00 | 4.37 | 4.35
2017-09-20 05:30 | 4.75 | 4.73
2017-09-20 06:00 | 5.04 | 5
2017-09-20 06:30 | 5.49 | 5.46
2017-09-20 07:00 | 5.51 | 5.49
2017-09-20 07:30 | 5.2 | 5.18
2017-09-20 08:00 | 4.92 | 4.91
2017-09-20 08:30 | 4.55 | 4.54
2017-09-20 09:00 | 4.25 | 4.23
2017-09-20 09:30 | 3.85 | 3.83
2017-09-20 10:00 | 3.66 | 3.63
2017-09-20 10:30 | 3.35 | 3.32
2017-09-20 11:00 | 3.24 | 3.21
2017-09-20 11:30 | 3.3 | 3.27
2017-09-20 12:00 | 3.16 | 3.13
2017-09-20 12:30 | 3.39 | 3.37
2017-09-20 13:00 | 3.54 | 3.52
2017-09-20 13:30 | 3.7 | 3.67
2017-09-20 14:00 | 4.29 | 4.26
2017-09-20 14:30 | 4.6 | 4.58
2017-09-20 15:00 | 5.01 | 5
2017-09-20 15:30 | 5.74 | 5.73
2017-09-20 16:00 | 6.37 | 6.36
2017-09-20 16:30 | 7.16 | 7.15
2017-09-20 17:00 | 8.07 | 8.06
2017-09-20 17:30 | 8.86 | 8.85
2017-09-20 18:00 | 9.74 | 9.73
2017-09-20 18:30 | 10.9 | 10.88
2017-09-20 19:00 | 11.24 | 11.22
2017-09-20 19:30 | 10.87 | 10.85
2017-09-20 20:00 | 10.76 | 10.74
2017-09-20 20:30 | 10.74 | 10.73
2017-09-20 21:00 | 10.14 | 10.13
2017-09-20 21:30 | 9.33 | 9.33
2017-09-20 22:00 | 8.61 | 8.61
2017-09-20 22:30 | 7.83 | 7.83
2017-09-20 23:00 | 7.4 | 7.39
2017-09-20 23:30 | 6.4 | 6.39
2017-09-21 | 5.6 | 5.59
2017-09-21 00:30 | 4.93 | 4.91
2017-09-21 01:00 | 4.63 | 4.62
2017-09-21 01:30 | 4.34 | 4.33
2017-09-21 02:00 | 4.16 | 4.15
2017-09-21 02:30 | 3.94 | 3.92
2017-09-21 03:00 | 3.8 | 3.78
2017-09-21 03:30 | 3.94 | 3.92
2017-09-21 04:00 | 4.01 | 3.99
2017-09-21 04:30 | 4.19 | 4.17
2017-09-21 05:00 | 4.46 | 4.44
2017-09-21 05:30 | 4.85 | 4.84
2017-09-21 06:00 | 4.94 | 4.9
2017-09-21 06:30 | 5.42 | 5.39
2017-09-21 07:00 | 5.28 | 5.25
2017-09-21 07:30 | 5.36 | 5.35
2017-09-21 08:00 | 4.93 | 4.93
2017-09-21 08:30 | 4.53 | 4.52
2017-09-21 09:00 | 4.57 | 4.56
2017-09-21 09:30 | 4.68 | 4.67
2017-09-21 10:00 | 4.24 | 4.22
2017-09-21 10:30 | 4.59 | 4.58
2017-09-21 11:00 | 4.32 | 4.3
2017-09-21 11:30 | 3.95 | 3.92
2017-09-21 12:00 | 3.63 | 3.59
2017-09-21 12:30 | 3.84 | 3.81
2017-09-21 13:00 | 3.65 | 3.62
2017-09-21 13:30 | 4.04 | 4.02
2017-09-21 14:00 | 4.05 | 4.03
2017-09-21 14:30 | 4.57 | 4.56
2017-09-21 15:00 | 5.03 | 5.02
2017-09-21 15:30 | 5.69 | 5.68
2017-09-21 16:00 | 6.55 | 6.54
2017-09-21 16:30 | 7.28 | 7.27
2017-09-21 17:00 | 8.28 | 8.27
2017-09-21 17:30 | 9 | 8.99
2017-09-21 18:00 | 9.51 | 9.5
2017-09-21 18:30 | 10.26 | 10.24
2017-09-21 19:00 | 10.62 | 10.6
2017-09-21 19:30 | 10.2 | 10.18
2017-09-21 20:00 | 10.08 | 10.06
2017-09-21 20:30 | 10.07 | 10.05
2017-09-21 21:00 | 9.46 | 9.45
2017-09-21 21:30 | 8.66 | 8.65
2017-09-21 22:00 | 7.99 | 7.98
2017-09-21 22:30 | 7.71 | 7.7
2017-09-21 23:00 | 7.52 | 7.51
2017-09-21 23:30 | 6.39 | 6.38
2017-09-22 | 5.59 | 5.57
2017-09-22 00:30 | 4.94 | 4.93
2017-09-22 01:00 | 4.67 | 4.65
2017-09-22 01:30 | 4.39 | 4.38
2017-09-22 02:00 | 4.17 | 4.15
2017-09-22 02:30 | 4.1 | 4.09
2017-09-22 03:00 | 4.19 | 4.17
2017-09-22 03:30 | 4.02 | 4
2017-09-22 04:00 | 4.09 | 4.07
2017-09-22 04:30 | 4.22 | 4.2
2017-09-22 05:00 | 4.37 | 4.35
2017-09-22 05:30 | 4.73 | 4.71
2017-09-22 06:00 | 4.92 | 4.89
2017-09-22 06:30 | 5.05 | 5.01
2017-09-22 07:00 | 4.95 | 4.91
2017-09-22 07:30 | 4.77 | 4.74
2017-09-22 08:00 | 4.49 | 4.47
2017-09-22 08:30 | 4.76 | 4.74
2017-09-22 09:00 | 5.74 | 5.73
2017-09-22 09:30 | 5.57 | 5.56
2017-09-22 10:00 | 4.87 | 4.85
2017-09-22 10:30 | 4.64 | 4.61
2017-09-22 11:00 | 4.69 | 4.66
2017-09-22 11:30 | 3.64 | 3.58
2017-09-22 12:00 | 3.49 | 3.42
2017-09-22 12:30 | 3.78 | 3.72
2017-09-22 13:00 | 4.02 | 3.97
2017-09-22 13:30 | 5.15 | 5.09
2017-09-22 14:00 | 5.3 | 5.24
2017-09-22 14:30 | 5.48 | 5.42
2017-09-22 15:00 | 7.81 | 7.77
2017-09-22 15:30 | 7.9 | 7.86
2017-09-22 16:00 | 7.68 | 7.65
2017-09-22 16:30 | 7.68 | 7.65
2017-09-22 17:00 | 7.65 | 7.63
2017-09-22 17:30 | 8.62 | 8.6
2017-09-22 18:00 | 9 | 8.98
2017-09-22 18:30 | 9.84 | 9.83
2017-09-22 19:00 | 10.22 | 10.2
2017-09-22 19:30 | 9.97 | 9.95
2017-09-22 20:00 | 9.81 | 9.79
2017-09-22 20:30 | 9.78 | 9.76
2017-09-22 21:00 | 9.21 | 9.2
2017-09-22 21:30 | 8.54 | 8.53
2017-09-22 22:00 | 7.99 | 7.97
2017-09-22 22:30 | 7.72 | 7.71
2017-09-22 23:00 | 7.64 | 7.63
2017-09-22 23:30 | 6.8 | 6.79
2017-09-23 | 6.05 | 6.04
2017-09-23 00:30 | 5.43 | 5.42
2017-09-23 01:00 | 5.2 | 5.19
2017-09-23 01:30 | 4.87 | 4.86
2017-09-23 02:00 | 4.64 | 4.63
2017-09-23 02:30 | 4.37 | 4.36
2017-09-23 03:00 | 4.27 | 4.25
2017-09-23 03:30 | 4.18 | 4.17
2017-09-23 04:00 | 4.15 | 4.13
2017-09-23 04:30 | 4.21 | 4.19
2017-09-23 05:00 | 4.17 | 4.15
2017-09-23 05:30 | 4.36 | 4.34
2017-09-23 06:00 | 4.17 | 4.11
2017-09-23 06:30 | 4.3 | 4.24
2017-09-23 07:00 | 4.33 | 4.27
2017-09-23 07:30 | 4.48 | 4.44
2017-09-23 08:00 | 4.45 | 4.43
2017-09-23 08:30 | 4.39 | 4.37
2017-09-23 09:00 | 4.24 | 4.22
2017-09-23 09:30 | 4.29 | 4.26
2017-09-23 10:00 | 4.12 | 4.08
2017-09-23 10:30 | 3.96 | 3.91
2017-09-23 11:00 | 3.92 | 3.86
2017-09-23 11:30 | 4.08 | 4.01
2017-09-23 12:00 | 4.3 | 4.24
2017-09-23 12:30 | 4.48 | 4.41
2017-09-23 13:00 | 4.87 | 4.81
2017-09-23 13:30 | 5.34 | 5.28
2017-09-23 14:00 | 6.05 | 5.99
2017-09-23 14:30 | 6.62 | 6.56
2017-09-23 15:00 | 7.1 | 7.04
2017-09-23 15:30 | 7.72 | 7.67
2017-09-23 16:00 | 8.3 | 8.26
2017-09-23 16:30 | 8.82 | 8.79
2017-09-23 17:00 | 9.36 | 9.33
2017-09-23 17:30 | 9.39 | 9.36
2017-09-23 18:00 | 9.55 | 9.52
2017-09-23 18:30 | 10.31 | 10.28
2017-09-23 19:00 | 10.47 | 10.44
2017-09-23 19:30 | 10.18 | 10.16
2017-09-23 20:00 | 9.92 | 9.9
2017-09-23 20:30 | 9.74 | 9.72
2017-09-23 21:00 | 9.21 | 9.19
2017-09-23 21:30 | 8.57 | 8.56
2017-09-23 22:00 | 8.12 | 8.1
2017-09-23 22:30 | 7.89 | 7.87
2017-09-23 23:00 | 7.77 | 7.76
2017-09-23 23:30 | 6.95 | 6.93
2017-09-24 | 6.08 | 6.07
2017-09-24 00:30 | 5.44 | 5.43
2017-09-24 01:00 | 5.18 | 5.17
2017-09-24 01:30 | 4.85 | 4.84
2017-09-24 02:00 | 4.52 | 4.51
2017-09-24 02:30 | 4.41 | 4.39
2017-09-24 03:00 | 4.22 | 4.2
2017-09-24 03:30 | 4.16 | 4.15
2017-09-24 04:00 | 4.09 | 4.07
2017-09-24 04:30 | 4.13 | 4.11
2017-09-24 05:00 | 4.11 | 4.09
2017-09-24 05:30 | 4.16 | 4.13
2017-09-24 06:00 | 4.18 | 4.11
2017-09-24 06:30 | 4.07 | 3.99
2017-09-24 07:00 | 4.13 | 4.06
2017-09-24 07:30 | 4.21 | 4.16
2017-09-24 08:00 | 4.23 | 4.2
2017-09-24 08:30 | 4.26 | 4.23
2017-09-24 09:00 | 4.36 | 4.33
2017-09-24 09:30 | 4.42 | 4.38
2017-09-24 10:00 | 4.33 | 4.28
2017-09-24 10:30 | 4.31 | 4.26
2017-09-24 11:00 | 4.57 | 4.52
2017-09-24 11:30 | 4.94 | 4.88
2017-09-24 12:00 | 5.42 | 5.36
2017-09-24 12:30 | 6.01 | 5.95
2017-09-24 13:00 | 6.57 | 6.5
2017-09-24 13:30 | 7.22 | 7.15
2017-09-24 14:00 | 8.07 | 7.98
2017-09-24 14:30 | 8.54 | 8.47
2017-09-24 15:00 | 9.17 | 9.1
2017-09-24 15:30 | 9.99 | 9.91
2017-09-24 16:00 | 10.46 | 10.39
2017-09-24 16:30 | 11.02 | 10.96
2017-09-24 17:00 | 11.49 | 11.44
2017-09-24 17:30 | 11.57 | 11.52
2017-09-24 18:00 | 11.67 | 11.63
2017-09-24 18:30 | 12.22 | 12.15
2017-09-24 19:00 | 12.3 | 12.25
2017-09-24 19:30 | 11.75 | 11.7
2017-09-24 20:00 | 11.31 | 11.28
2017-09-24 20:30 | 10.82 | 10.8
2017-09-24 21:00 | 10.18 | 10.16
2017-09-24 21:30 | 9.35 | 9.33
2017-09-24 22:00 | 8.54 | 8.53
2017-09-24 22:30 | 8.02 | 8.01
2017-09-24 23:00 | 7.79 | 7.77
2017-09-24 23:30 | 6.75 | 6.74
2017-09-25 | 5.85 | 5.84
2017-09-25 00:30 | 5.32 | 5.31
2017-09-25 01:00 | 5.03 | 5.02
2017-09-25 01:30 | 4.65 | 4.63
2017-09-25 02:00 | 4.42 | 4.41
2017-09-25 02:30 | 4.79 | 4.78
2017-09-25 03:00 | 4.86 | 4.85
2017-09-25 03:30 | 4.91 | 4.9
2017-09-25 04:00 | 4.24 | 4.22
2017-09-25 04:30 | 4.35 | 4.33
2017-09-25 05:00 | 4.56 | 4.54
2017-09-25 05:30 | 4.92 | 4.9
2017-09-25 06:00 | 5.45 | 5.43
2017-09-25 06:30 | 5.61 | 5.59
2017-09-25 07:00 | 5.52 | 5.5
2017-09-25 07:30 | 5.58 | 5.57
2017-09-25 08:00 | 5.21 | 5.2
2017-09-25 08:30 | 4.95 | 4.94
2017-09-25 09:00 | 4.64 | 4.63
2017-09-25 09:30 | 4.47 | 4.46
2017-09-25 10:00 | 4.57 | 4.55
2017-09-25 10:30 | 4.49 | 4.46
2017-09-25 11:00 | 4.63 | 4.6
2017-09-25 11:30 | 4.98 | 4.95
2017-09-25 12:00 | 5.56 | 5.51
2017-09-25 12:30 | 6.07 | 6.01
2017-09-25 13:00 | 6.8 | 6.72
2017-09-25 13:30 | 9.09 | 9.01
2017-09-25 14:00 | 8.63 | 8.54
2017-09-25 14:30 | 9.32 | 9.22
2017-09-25 15:00 | 9.99 | 9.9
2017-09-25 15:30 | 10.88 | 10.78
2017-09-25 16:00 | 11.87 | 11.76
2017-09-25 16:30 | 12.98 | 12.87
2017-09-25 17:00 | 13.35 | 13.25
2017-09-25 17:30 | 13.5 | 13.4
2017-09-25 18:00 | 13.59 | 13.5
2017-09-25 18:30 | 14.19 | 14.08
2017-09-25 19:00 | 14.53 | 14.43
2017-09-25 19:30 | 13.77 | 13.68
2017-09-25 20:00 | 13.39 | 13.32
2017-09-25 20:30 | 12.8 | 12.74
2017-09-25 21:00 | 11.87 | 11.83
2017-09-25 21:30 | 10.81 | 10.79
2017-09-25 22:00 | 9.95 | 9.93
2017-09-25 22:30 | 9.01 | 9
2017-09-25 23:00 | 8.29 | 8.27
2017-09-25 23:30 | 7.06 | 7.04
2017-09-26 | 6.24 | 6.23
2017-09-26 00:30 | 5.64 | 5.63
2017-09-26 01:00 | 5.32 | 5.31
2017-09-26 01:30 | 5 | 4.98
2017-09-26 02:00 | 4.75 | 4.73
2017-09-26 02:30 | 4.53 | 4.51
2017-09-26 03:00 | 4.33 | 4.31
2017-09-26 03:30 | 4.4 | 4.39
2017-09-26 04:00 | 4.42 | 4.4
2017-09-26 04:30 | 4.5 | 4.49
2017-09-26 05:00 | 4.56 | 4.55
2017-09-26 05:30 | 4.97 | 4.95
2017-09-26 06:00 | 5.36 | 5.34
2017-09-26 06:30 | 5.68 | 5.66
2017-09-26 07:00 | 5.54 | 5.53
2017-09-26 07:30 | 5.23 | 5.22
2017-09-26 08:00 | 5.02 | 5.01
2017-09-26 08:30 | 5.01 | 4.99
2017-09-26 09:00 | 4.95 | 4.92
2017-09-26 09:30 | 6.41 | 6.39
2017-09-26 10:00 | 7.75 | 7.73
2017-09-26 10:30 | 7.8 | 7.77
2017-09-26 11:00 | 6.76 | 6.74
2017-09-26 11:30 | 5.85 | 5.82
2017-09-26 12:00 | 6.05 | 6.03
2017-09-26 12:30 | 4.63 | 4.6
2017-09-26 13:00 | 5.01 | 4.98
2017-09-26 13:30 | 5.47 | 5.43
2017-09-26 14:00 | 6.13 | 6.09
2017-09-26 14:30 | 7.29 | 7.26
2017-09-26 15:00 | 8.07 | 8.05
2017-09-26 15:30 | 9.11 | 9.1
2017-09-26 16:00 | 8.65 | 8.64
2017-09-26 16:30 | 8.3 | 8.28
2017-09-26 17:00 | 9.91 | 9.9
2017-09-26 17:30 | 11.14 | 11.14
2017-09-26 18:00 | 10.43 | 10.42
2017-09-26 18:30 | 11.22 | 11.18
2017-09-26 19:00 | 11.76 | 11.73
2017-09-26 19:30 | 11.33 | 11.3
2017-09-26 20:00 | 11.19 | 11.17
2017-09-26 20:30 | 10.8 | 10.79
2017-09-26 21:00 | 10.21 | 10.2
2017-09-26 21:30 | 9.39 | 9.38
2017-09-26 22:00 | 8.54 | 8.53
2017-09-26 22:30 | 7.91 | 7.9
2017-09-26 23:00 | 7.43 | 7.42
2017-09-26 23:30 | 6.46 | 6.45
2017-09-27 | 5.68 | 5.67
2017-09-27 00:30 | 5.02 | 5.01
2017-09-27 01:00 | 4.78 | 4.77
2017-09-27 01:30 | 4.51 | 4.5
2017-09-27 02:00 | 4.35 | 4.34
2017-09-27 02:30 | 4.16 | 4.15
2017-09-27 03:00 | 4.07 | 4.05
2017-09-27 03:30 | 4.1 | 4.08
2017-09-27 04:00 | 4.08 | 4.06
2017-09-27 04:30 | 4.26 | 4.24
2017-09-27 05:00 | 4.39 | 4.38
2017-09-27 05:30 | 4.77 | 4.75
2017-09-27 06:00 | 5.01 | 4.98
2017-09-27 06:30 | 5.13 | 5.09
2017-09-27 07:00 | 5.65 | 5.62
2017-09-27 07:30 | 5.36 | 5.34
2017-09-27 08:00 | 5.25 | 5.24
2017-09-27 08:30 | 5.59 | 5.58
2017-09-27 09:00 | 5.84 | 5.83
2017-09-27 09:30 | 6.28 | 6.27
2017-09-27 10:00 | 6.4 | 6.39
2017-09-27 10:30 | 5.72 | 5.7
2017-09-27 11:00 | 5.78 | 5.77
2017-09-27 11:30 | 5.9 | 5.88
2017-09-27 12:00 | 5.82 | 5.81
2017-09-27 12:30 | 5.35 | 5.34
2017-09-27 13:00 | 4.53 | 4.51
2017-09-27 13:30 | 5.49 | 5.47
2017-09-27 14:00 | 6.16 | 6.15
2017-09-27 14:30 | 7.51 | 7.5
2017-09-27 15:00 | 6.72 | 6.71
2017-09-27 15:30 | 5.64 | 5.61
2017-09-27 16:00 | 6.82 | 6.81
2017-09-27 16:30 | 7.74 | 7.73
2017-09-27 17:00 | 8.64 | 8.64
2017-09-27 17:30 | 9.33 | 9.32
2017-09-27 18:00 | 10.36 | 10.35
2017-09-27 18:30 | 11.08 | 11.05
2017-09-27 19:00 | 11.29 | 11.26
2017-09-27 19:30 | 11.09 | 11.06
2017-09-27 20:00 | 11.12 | 11.1
2017-09-27 20:30 | 11.04 | 11.02
2017-09-27 21:00 | 10.4 | 10.39
2017-09-27 21:30 | 9.66 | 9.66
2017-09-27 22:00 | 8.76 | 8.75
2017-09-27 22:30 | 8.23 | 8.22
2017-09-27 23:00 | 7.77 | 7.76
2017-09-27 23:30 | 6.72 | 6.71
2017-09-28 | 5.94 | 5.93
2017-09-28 00:30 | 5.29 | 5.28
2017-09-28 01:00 | 5.03 | 5.02
2017-09-28 01:30 | 4.65 | 4.64
2017-09-28 02:00 | 4.42 | 4.4
2017-09-28 02:30 | 4.23 | 4.21
2017-09-28 03:00 | 4.13 | 4.11
2017-09-28 03:30 | 4.18 | 4.16
2017-09-28 04:00 | 4.15 | 4.13
2017-09-28 04:30 | 4.37 | 4.35
2017-09-28 05:00 | 4.6 | 4.58
2017-09-28 05:30 | 4.86 | 4.84
2017-09-28 06:00 | 5.35 | 5.33
2017-09-28 06:30 | 5.76 | 5.73
2017-09-28 07:00 | 5.73 | 5.72
2017-09-28 07:30 | 5.57 | 5.56
2017-09-28 08:00 | 5.26 | 5.25
2017-09-28 08:30 | 4.77 | 4.75
2017-09-28 09:00 | 4.67 | 4.65
2017-09-28 09:30 | 4.82 | 4.79
2017-09-28 10:00 | 4.73 | 4.7
2017-09-28 10:30 | 4.77 | 4.73
2017-09-28 11:00 | 5.06 | 5
2017-09-28 11:30 | 5.43 | 5.35
2017-09-28 12:00 | 5.8 | 5.72
2017-09-28 12:30 | 6.68 | 6.58
2017-09-28 13:00 | 7.6 | 7.5
2017-09-28 13:30 | 8.74 | 8.59
2017-09-28 14:00 | 9.87 | 9.73
2017-09-28 14:30 | 11.27 | 11.09
2017-09-28 15:00 | 12.52 | 12.32
2017-09-28 15:30 | 13.7 | 13.51
2017-09-28 16:00 | 14.63 | 14.41
2017-09-28 16:30 | 15.46 | 15.22
2017-09-28 17:00 | 16.01 | 15.83
2017-09-28 17:30 | 16.5 | 16.3
2017-09-28 18:00 | 16.34 | 16.15
2017-09-28 18:30 | 16.68 | 16.45
2017-09-28 19:00 | 16.8 | 16.59
2017-09-28 19:30 | 16.04 | 15.84
2017-09-28 20:00 | 15.18 | 15.02
2017-09-28 20:30 | 14.4 | 14.27
2017-09-28 21:00 | 13.19 | 13.08
2017-09-28 21:30 | 11.89 | 11.83
2017-09-28 22:00 | 10.83 | 10.78
2017-09-28 22:30 | 10.06 | 10.04
2017-09-28 23:00 | 9.44 | 9.42
2017-09-28 23:30 | 8.14 | 8.12
2017-09-29 | 7.11 | 7.1
2017-09-29 00:30 | 6.3 | 6.29
2017-09-29 01:00 | 6 | 5.99
2017-09-29 01:30 | 5.53 | 5.52
2017-09-29 02:00 | 5.22 | 5.2
2017-09-29 02:30 | 4.98 | 4.96
2017-09-29 03:00 | 4.82 | 4.8
2017-09-29 03:30 | 4.82 | 4.8
2017-09-29 04:00 | 4.76 | 4.74
2017-09-29 04:30 | 4.92 | 4.9
2017-09-29 05:00 | 4.93 | 4.91
2017-09-29 05:30 | 5.15 | 5.14
2017-09-29 06:00 | 5.2 | 5.17
2017-09-29 06:30 | 5.27 | 5.25
2017-09-29 07:00 | 5.16 | 5.14
2017-09-29 07:30 | 5.05 | 5.04
2017-09-29 08:00 | 4.89 | 4.87
2017-09-29 08:30 | 4.82 | 4.81
2017-09-29 09:00 | 4.89 | 4.87
2017-09-29 09:30 | 5.01 | 4.98
2017-09-29 10:00 | 5.13 | 5.1
2017-09-29 10:30 | 5.3 | 5.24
2017-09-29 11:00 | 5.68 | 5.61
2017-09-29 11:30 | 6.23 | 6.14
2017-09-29 12:00 | 6.89 | 6.79
2017-09-29 12:30 | 7.63 | 7.51
2017-09-29 13:00 | 8.33 | 8.2
2017-09-29 13:30 | 9.24 | 9.09
2017-09-29 14:00 | 10.27 | 10.1
2017-09-29 14:30 | 11.05 | 10.87
2017-09-29 15:00 | 12.29 | 12.12
2017-09-29 15:30 | 13.01 | 12.83
2017-09-29 16:00 | 13.87 | 13.68
2017-09-29 16:30 | 14.32 | 14.14
2017-09-29 17:00 | 15.07 | 14.9
2017-09-29 17:30 | 15.09 | 14.92
2017-09-29 18:00 | 14.5 | 14.34
2017-09-29 18:30 | 14.43 | 14.25
2017-09-29 19:00 | 14.5 | 14.34
2017-09-29 19:30 | 13.84 | 13.71
2017-09-29 20:00 | 13.26 | 13.15
2017-09-29 20:30 | 12.64 | 12.55
2017-09-29 21:00 | 11.8 | 11.74
2017-09-29 21:30 | 10.86 | 10.82
2017-09-29 22:00 | 9.93 | 9.9
2017-09-29 22:30 | 9.53 | 9.51
2017-09-29 23:00 | 9.14 | 9.12
2017-09-29 23:30 | 7.97 | 7.95
2017-09-30 | 7.01 | 6.99
2017-09-30 00:30 | 6.31 | 6.29
2017-09-30 01:00 | 5.89 | 5.87
2017-09-30 01:30 | 5.44 | 5.43
2017-09-30 02:00 | 5.22 | 5.21
2017-09-30 02:30 | 4.98 | 4.97
2017-09-30 03:00 | 4.83 | 4.81
2017-09-30 03:30 | 4.79 | 4.78
2017-09-30 04:00 | 4.62 | 4.61
2017-09-30 04:30 | 4.74 | 4.73
2017-09-30 05:00 | 4.74 | 4.72
2017-09-30 05:30 | 4.68 | 4.65
2017-09-30 06:00 | 4.63 | 4.58
2017-09-30 06:30 | 4.58 | 4.53
2017-09-30 07:00 | 4.5 | 4.45
2017-09-30 07:30 | 4.67 | 4.64
2017-09-30 08:00 | 4.58 | 4.56
2017-09-30 08:30 | 4.74 | 4.7
2017-09-30 09:00 | 5.22 | 5.18
2017-09-30 09:30 | 5.84 | 5.81
2017-09-30 10:00 | 5.23 | 5.18
2017-09-30 10:30 | 5.72 | 5.68
2017-09-30 11:00 | 5.97 | 5.93
2017-09-30 11:30 | 5.33 | 5.27
2017-09-30 12:00 | 5.99 | 5.93
2017-09-30 12:30 | 6.3 | 6.23
2017-09-30 13:00 | 6.97 | 6.89
2017-09-30 13:30 | 7.63 | 7.54
2017-09-30 14:00 | 8.59 | 8.5
2017-09-30 14:30 | 9.28 | 9.18
2017-09-30 15:00 | 10.15 | 10.05
2017-09-30 15:30 | 11.08 | 10.97
2017-09-30 16:00 | 11.75 | 11.65
2017-09-30 16:30 | 12.27 | 12.18
2017-09-30 17:00 | 11.47 | 11.42
2017-09-30 17:30 | 10.73 | 10.69
2017-09-30 18:00 | 10.29 | 10.26
2017-09-30 18:30 | 10.79 | 10.74
2017-09-30 19:00 | 10.83 | 10.79
2017-09-30 19:30 | 10.39 | 10.36
2017-09-30 20:00 | 10.11 | 10.08
2017-09-30 20:30 | 9.73 | 9.71
2017-09-30 21:00 | 9.27 | 9.25
2017-09-30 21:30 | 8.81 | 8.79
2017-09-30 22:00 | 8.29 | 8.27
2017-09-30 22:30 | 8.06 | 8.05
2017-09-30 23:00 | 7.84 | 7.82
2017-09-30 23:30 | 6.9 | 6.89
2017-10-01 | 6.1 | 6.09
2017-10-01 00:30 | 5.49 | 5.48
2017-10-01 01:00 | 5.07 | 5.06
2017-10-01 01:30 | 4.73 | 4.71
2017-10-01 02:00 | 4.51 | 4.49
2017-10-01 02:30 | 4.4 | 4.39
2017-10-01 03:00 | 4.28 | 4.26
2017-10-01 03:30 | 4.15 | 4.13
2017-10-01 04:00 | 4.06 | 4.04
2017-10-01 04:30 | 4.14 | 4.12
2017-10-01 05:00 | 4.24 | 4.22
2017-10-01 05:30 | 4.24 | 4.22
2017-10-01 06:00 | 4.13 | 4.07
2017-10-01 06:30 | 4.34 | 4.27
2017-10-01 07:00 | 4.54 | 4.48
2017-10-01 07:30 | 4.78 | 4.74
2017-10-01 08:00 | 5.35 | 5.32
2017-10-01 08:30 | 5.6 | 5.57
2017-10-01 09:00 | 5.73 | 5.71
2017-10-01 09:30 | 4.84 | 4.81
2017-10-01 10:00 | 4.75 | 4.73
2017-10-01 10:30 | 5.49 | 5.47
2017-10-01 11:00 | 4.97 | 4.94
2017-10-01 11:30 | 4.76 | 4.72
2017-10-01 12:00 | 6.76 | 6.73
2017-10-01 12:30 | 7.26 | 7.24
2017-10-01 13:00 | 6.8 | 6.78
2017-10-01 13:30 | 6.2 | 6.18
2017-10-01 14:00 | 6.14 | 6.12
2017-10-01 14:30 | 6.33 | 6.31
2017-10-01 15:00 | 6.54 | 6.52
2017-10-01 15:30 | 7.17 | 7.16
2017-10-01 16:00 | 7.6 | 7.59
2017-10-01 16:30 | 7.99 | 7.98
2017-10-01 17:00 | 8.53 | 8.52
2017-10-01 17:30 | 8.95 | 8.94
2017-10-01 18:00 | 9.2 | 9.19
2017-10-01 18:30 | 9.35 | 9.34
2017-10-01 19:00 | 9.27 | 9.26
2017-10-01 19:30 | 8.82 | 8.81
2017-10-01 20:00 | 8.91 | 8.9
2017-10-01 20:30 | 8.73 | 8.72
2017-10-01 21:00 | 8.25 | 8.24
2017-10-01 21:30 | 7.8 | 7.79
2017-10-01 22:00 | 7.42 | 7.41
2017-10-01 22:30 | 7.22 | 7.21
2017-10-01 23:00 | 7.06 | 7.05
2017-10-01 23:30 | 6.33 | 6.32
2017-10-02 | 5.56 | 5.55
2017-10-02 00:30 | 5.06 | 5.05
2017-10-02 01:00 | 4.84 | 4.82
2017-10-02 01:30 | 4.47 | 4.45
2017-10-02 02:00 | 4.16 | 4.14
2017-10-02 02:30 | 4.05 | 4.02
2017-10-02 03:00 | 3.89 | 3.86
2017-10-02 03:30 | 3.96 | 3.94
2017-10-02 04:00 | 3.82 | 3.78
2017-10-02 04:30 | 3.88 | 3.85
2017-10-02 05:00 | 3.89 | 3.86
2017-10-02 05:30 | 4.04 | 4.01
2017-10-02 06:00 | 3.93 | 3.85
2017-10-02 06:30 | 4.12 | 4.03
2017-10-02 07:00 | 4.17 | 4.08
2017-10-02 07:30 | 4.63 | 4.56
2017-10-02 08:00 | 5.38 | 5.33
2017-10-02 08:30 | 5.66 | 5.61
2017-10-02 09:00 | 5.82 | 5.78
2017-10-02 09:30 | 6.51 | 6.49
2017-10-02 10:00 | 7.24 | 7.23
2017-10-02 10:30 | 6.78 | 6.77
2017-10-02 11:00 | 6.42 | 6.41
2017-10-02 11:30 | 7.28 | 7.26
2017-10-02 12:00 | 7.59 | 7.58
2017-10-02 12:30 | 7.81 | 7.8
2017-10-02 13:00 | 7.62 | 7.6
2017-10-02 13:30 | 7.27 | 7.25
2017-10-02 14:00 | 7.91 | 7.89
2017-10-02 14:30 | 8.3 | 8.29
2017-10-02 15:00 | 7.9 | 7.89
2017-10-02 15:30 | 7.87 | 7.85
2017-10-02 16:00 | 8.31 | 8.3
2017-10-02 16:30 | 9.16 | 9.15
2017-10-02 17:00 | 9.74 | 9.73
2017-10-02 17:30 | 10.32 | 10.31
2017-10-02 18:00 | 10.65 | 10.64
2017-10-02 18:30 | 11.03 | 11.01
2017-10-02 19:00 | 10.85 | 10.84
2017-10-02 19:30 | 10.38 | 10.37
2017-10-02 20:00 | 10.13 | 10.12
2017-10-02 20:30 | 10.11 | 10.1
2017-10-02 21:00 | 9.41 | 9.39
2017-10-02 21:30 | 8.67 | 8.66
2017-10-02 22:00 | 8.03 | 8.01
2017-10-02 22:30 | 7.57 | 7.56
2017-10-02 23:00 | 7.27 | 7.26
2017-10-02 23:30 | 6.4 | 6.39
2017-10-03 | 5.58 | 5.56
2017-10-03 00:30 | 4.92 | 4.91
2017-10-03 01:00 | 4.67 | 4.65
2017-10-03 01:30 | 4.39 | 4.37
2017-10-03 02:00 | 4.15 | 4.12
2017-10-03 02:30 | 3.94 | 3.91
2017-10-03 03:00 | 3.94 | 3.92
2017-10-03 03:30 | 3.96 | 3.94
2017-10-03 04:00 | 3.93 | 3.91
2017-10-03 04:30 | 4.32 | 4.3
2017-10-03 05:00 | 4.52 | 4.5
2017-10-03 05:30 | 4.84 | 4.83
2017-10-03 06:00 | 5.23 | 5.2
2017-10-03 06:30 | 5.82 | 5.79
2017-10-03 07:00 | 6.26 | 6.23
2017-10-03 07:30 | 6.71 | 6.7
2017-10-03 08:00 | 6.65 | 6.63
2017-10-03 08:30 | 6.41 | 6.39
2017-10-03 09:00 | 5.85 | 5.84
2017-10-03 09:30 | 6.15 | 6.14
2017-10-03 10:00 | 6 | 5.99
2017-10-03 10:30 | 5.46 | 5.44
2017-10-03 11:00 | 4.86 | 4.85
2017-10-03 11:30 | 5.04 | 5.03
2017-10-03 12:00 | 4.46 | 4.44
2017-10-03 12:30 | 3.58 | 3.57
2017-10-03 13:00 | 4.2 | 4.19
2017-10-03 13:30 | 3.45 | 3.43
2017-10-03 14:00 | 3.3 | 3.27
2017-10-03 14:30 | 3.78 | 3.76
2017-10-03 15:00 | 4.24 | 4.23
2017-10-03 15:30 | 6.12 | 6.1
2017-10-03 16:00 | 6.84 | 6.82
2017-10-03 16:30 | 7.56 | 7.54
2017-10-03 17:00 | 8.74 | 8.72
2017-10-03 17:30 | 9.42 | 9.41
2017-10-03 18:00 | 10.01 | 10
2017-10-03 18:30 | 10.79 | 10.78
2017-10-03 19:00 | 11.33 | 11.31
2017-10-03 19:30 | 10.79 | 10.77
2017-10-03 20:00 | 10.59 | 10.57
2017-10-03 20:30 | 10.35 | 10.34
2017-10-03 21:00 | 9.89 | 9.88
2017-10-03 21:30 | 9.25 | 9.23
2017-10-03 22:00 | 8.32 | 8.31
2017-10-03 22:30 | 7.82 | 7.81
2017-10-03 23:00 | 7.53 | 7.51
2017-10-03 23:30 | 6.49 | 6.48
2017-10-04 | 5.63 | 5.62
2017-10-04 00:30 | 4.94 | 4.93
2017-10-04 01:00 | 4.76 | 4.75
2017-10-04 01:30 | 4.48 | 4.46
2017-10-04 02:00 | 4.23 | 4.21
2017-10-04 02:30 | 4.11 | 4.09
2017-10-04 03:00 | 4.03 | 4.01
2017-10-04 03:30 | 4.1 | 4.07
2017-10-04 04:00 | 4.04 | 4.02
2017-10-04 04:30 | 4.22 | 4.19
2017-10-04 05:00 | 4.56 | 4.55
2017-10-04 05:30 | 4.9 | 4.88
2017-10-04 06:00 | 5.19 | 5.15
2017-10-04 06:30 | 5.54 | 5.5
2017-10-04 07:00 | 6.11 | 6.09
2017-10-04 07:30 | 6.62 | 6.6
2017-10-04 08:00 | 6 | 5.99
2017-10-04 08:30 | 4.72 | 4.7
2017-10-04 09:00 | 4.55 | 4.53
2017-10-04 09:30 | 4.44 | 4.41
2017-10-04 10:00 | 4.55 | 4.52
2017-10-04 10:30 | 4.48 | 4.44
2017-10-04 11:00 | 4.95 | 4.92
2017-10-04 11:30 | 5.72 | 5.69
2017-10-04 12:00 | 5.66 | 5.64
2017-10-04 12:30 | 4.66 | 4.64
2017-10-04 13:00 | 3.34 | 3.31
2017-10-04 13:30 | 3.79 | 3.76
2017-10-04 14:00 | 4.5 | 4.47
2017-10-04 14:30 | 5.46 | 5.44
2017-10-04 15:00 | 5.68 | 5.66
2017-10-04 15:30 | 6.07 | 6.05
2017-10-04 16:00 | 7.22 | 7.19
2017-10-04 16:30 | 8.07 | 8.04
2017-10-04 17:00 | 8.93 | 8.91
2017-10-04 17:30 | 9.47 | 9.45
2017-10-04 18:00 | 10.13 | 10.11
2017-10-04 18:30 | 11.03 | 11.01
2017-10-04 19:00 | 11.92 | 11.88
2017-10-04 19:30 | 11.43 | 11.4
2017-10-04 20:00 | 11.13 | 11.11
2017-10-04 20:30 | 10.83 | 10.82
2017-10-04 21:00 | 10.25 | 10.24
2017-10-04 21:30 | 9.51 | 9.5
2017-10-04 22:00 | 8.67 | 8.66
2017-10-04 22:30 | 8.1 | 8.09
2017-10-04 23:00 | 7.79 | 7.78
2017-10-04 23:30 | 6.72 | 6.71
2017-10-05 | 5.73 | 5.72
2017-10-05 00:30 | 5.09 | 5.08
2017-10-05 01:00 | 4.81 | 4.79
2017-10-05 01:30 | 4.52 | 4.5
2017-10-05 02:00 | 4.29 | 4.26
2017-10-05 02:30 | 4.17 | 4.15
2017-10-05 03:00 | 3.99 | 3.97
2017-10-05 03:30 | 4.08 | 4.06
2017-10-05 04:00 | 4.05 | 4.02
2017-10-05 04:30 | 4.29 | 4.27
2017-10-05 05:00 | 4.55 | 4.53
2017-10-05 05:30 | 4.98 | 4.95
2017-10-05 06:00 | 5.7 | 5.68
2017-10-05 06:30 | 5.84 | 5.82
2017-10-05 07:00 | 6.08 | 6.07
2017-10-05 07:30 | 6.09 | 6.08
2017-10-05 08:00 | 5.76 | 5.76
2017-10-05 08:30 | 4.86 | 4.85
2017-10-05 09:00 | 4.49 | 4.48
2017-10-05 09:30 | 4.2 | 4.17
2017-10-05 10:00 | 3.81 | 3.79
2017-10-05 10:30 | 4.25 | 4.24
2017-10-05 11:00 | 4.78 | 4.77
2017-10-05 11:30 | 5.11 | 5.08
2017-10-05 12:00 | 4.57 | 4.52
2017-10-05 12:30 | 4.66 | 4.59
2017-10-05 13:00 | 5.08 | 5.01
2017-10-05 13:30 | 5.35 | 5.29
2017-10-05 14:00 | 5.69 | 5.63
2017-10-05 14:30 | 6.23 | 6.17
2017-10-05 15:00 | 6.77 | 6.71
2017-10-05 15:30 | 7.81 | 7.75
2017-10-05 16:00 | 9.07 | 9.01
2017-10-05 16:30 | 9.85 | 9.79
2017-10-05 17:00 | 10.42 | 10.37
2017-10-05 17:30 | 10.75 | 10.72
2017-10-05 18:00 | 10.99 | 10.96
2017-10-05 18:30 | 11.61 | 11.56
2017-10-05 19:00 | 12.04 | 12
2017-10-05 19:30 | 11.79 | 11.75
2017-10-05 20:00 | 11.39 | 11.36
2017-10-05 20:30 | 11.14 | 11.12
2017-10-05 21:00 | 10.41 | 10.39
2017-10-05 21:30 | 9.52 | 9.51
2017-10-05 22:00 | 8.82 | 8.81
2017-10-05 22:30 | 8.31 | 8.3
2017-10-05 23:00 | 7.97 | 7.96
2017-10-05 23:30 | 7.03 | 7.02
2017-10-06 | 6.01 | 6
2017-10-06 00:30 | 5.41 | 5.4
2017-10-06 01:00 | 5.1 | 5.09
2017-10-06 01:30 | 4.74 | 4.72
2017-10-06 02:00 | 4.57 | 4.56
2017-10-06 02:30 | 4.32 | 4.31
2017-10-06 03:00 | 4.26 | 4.24
2017-10-06 03:30 | 4.33 | 4.32
2017-10-06 04:00 | 4.35 | 4.34
2017-10-06 04:30 | 4.52 | 4.5
2017-10-06 05:00 | 4.68 | 4.66
2017-10-06 05:30 | 4.93 | 4.91
2017-10-06 06:00 | 5.57 | 5.55
2017-10-06 06:30 | 5.65 | 5.63
2017-10-06 07:00 | 5.83 | 5.82
2017-10-06 07:30 | 6.01 | 6.01
2017-10-06 08:00 | 5.62 | 5.61
2017-10-06 08:30 | 4.81 | 4.8
2017-10-06 09:00 | 4.73 | 4.71
2017-10-06 09:30 | 4.5 | 4.47
2017-10-06 10:00 | 4.46 | 4.43
2017-10-06 10:30 | 4.22 | 4.17
2017-10-06 11:00 | 4.25 | 4.19
2017-10-06 11:30 | 4.64 | 4.57
2017-10-06 12:00 | 5.15 | 5.08
2017-10-06 12:30 | 5.71 | 5.62
2017-10-06 13:00 | 6.31 | 6.2
2017-10-06 13:30 | 7.24 | 7.13
2017-10-06 14:00 | 8.09 | 7.96
2017-10-06 14:30 | 10.82 | 10.73
2017-10-06 15:00 | 11.1 | 11.02
2017-10-06 15:30 | 9.62 | 9.57
2017-10-06 16:00 | 8.54 | 8.5
2017-10-06 16:30 | 9.53 | 9.5
2017-10-06 17:00 | 9.85 | 9.82
2017-10-06 17:30 | 10.04 | 10.01
2017-10-06 18:00 | 10.65 | 10.61
2017-10-06 18:30 | 11.53 | 11.47
2017-10-06 19:00 | 11.82 | 11.76
2017-10-06 19:30 | 11.48 | 11.44
2017-10-06 20:00 | 11.22 | 11.18
2017-10-06 20:30 | 11.04 | 11.01
2017-10-06 21:00 | 10.45 | 10.43
2017-10-06 21:30 | 9.8 | 9.78
2017-10-06 22:00 | 8.99 | 8.97
2017-10-06 22:30 | 8.74 | 8.73
2017-10-06 23:00 | 8.51 | 8.5
2017-10-06 23:30 | 7.59 | 7.57
2017-10-07 | 6.62 | 6.6
2017-10-07 00:30 | 5.95 | 5.94
2017-10-07 01:00 | 5.62 | 5.61
2017-10-07 01:30 | 5.31 | 5.3
2017-10-07 02:00 | 5.14 | 5.13
2017-10-07 02:30 | 4.81 | 4.8
2017-10-07 03:00 | 4.75 | 4.73
2017-10-07 03:30 | 4.71 | 4.7
2017-10-07 04:00 | 4.59 | 4.58
2017-10-07 04:30 | 4.57 | 4.55
2017-10-07 05:00 | 4.53 | 4.52
2017-10-07 05:30 | 4.76 | 4.74
2017-10-07 06:00 | 4.64 | 4.6
2017-10-07 06:30 | 4.82 | 4.77
2017-10-07 07:00 | 5.2 | 5.16
2017-10-07 07:30 | 5.77 | 5.75
2017-10-07 08:00 | 6.08 | 6.06
2017-10-07 08:30 | 6.47 | 6.45
2017-10-07 09:00 | 6.87 | 6.85
2017-10-07 09:30 | 6.7 | 6.68
2017-10-07 10:00 | 6.66 | 6.64
2017-10-07 10:30 | 6.89 | 6.87
2017-10-07 11:00 | 6.7 | 6.67
2017-10-07 11:30 | 6.82 | 6.8
2017-10-07 12:00 | 7.01 | 6.99
2017-10-07 12:30 | 6.32 | 6.3
2017-10-07 13:00 | 5.51 | 5.48
2017-10-07 13:30 | 6.57 | 6.55
2017-10-07 14:00 | 7.54 | 7.52
2017-10-07 14:30 | 7.47 | 7.45
2017-10-07 15:00 | 6.87 | 6.85
2017-10-07 15:30 | 7.38 | 7.37
2017-10-07 16:00 | 7.61 | 7.59
2017-10-07 16:30 | 7.62 | 7.6
2017-10-07 17:00 | 8.23 | 8.22
2017-10-07 17:30 | 8.53 | 8.52
2017-10-07 18:00 | 8.65 | 8.64
2017-10-07 18:30 | 9.22 | 9.21
2017-10-07 19:00 | 9.71 | 9.7
2017-10-07 19:30 | 9.39 | 9.37
2017-10-07 20:00 | 9.24 | 9.22
2017-10-07 20:30 | 9.09 | 9.08
2017-10-07 21:00 | 8.62 | 8.61
2017-10-07 21:30 | 8.02 | 8.01
2017-10-07 22:00 | 7.73 | 7.73
2017-10-07 22:30 | 7.79 | 7.79
2017-10-07 23:00 | 8.64 | 8.63
2017-10-07 23:30 | 7.85 | 7.84
2017-10-08 | 6.81 | 6.8
2017-10-08 00:30 | 5.49 | 5.48
2017-10-08 01:00 | 5.14 | 5.13
2017-10-08 01:30 | 4.88 | 4.87
2017-10-08 02:00 | 4.55 | 4.54
2017-10-08 02:30 | 4.4 | 4.39
2017-10-08 03:00 | 4.24 | 4.22
2017-10-08 03:30 | 4.21 | 4.2
2017-10-08 04:00 | 4.12 | 4.1
2017-10-08 04:30 | 4.2 | 4.18
2017-10-08 05:00 | 4.16 | 4.14
2017-10-08 05:30 | 4.16 | 4.12
2017-10-08 06:00 | 4.1 | 4.01
2017-10-08 06:30 | 4.19 | 4.11
2017-10-08 07:00 | 4.38 | 4.31
2017-10-08 07:30 | 4.3 | 4.25
2017-10-08 08:00 | 4.23 | 4.2
2017-10-08 08:30 | 4.69 | 4.67
2017-10-08 09:00 | 4.89 | 4.87
2017-10-08 09:30 | 4.97 | 4.94
2017-10-08 10:00 | 5.58 | 5.55
2017-10-08 10:30 | 6.12 | 6.09
2017-10-08 11:00 | 6.46 | 6.44
2017-10-08 11:30 | 5.97 | 5.94
2017-10-08 12:00 | 5.9 | 5.87
2017-10-08 12:30 | 6.54 | 6.51
2017-10-08 13:00 | 7.4 | 7.37
2017-10-08 13:30 | 7.75 | 7.72
2017-10-08 14:00 | 7.57 | 7.55
2017-10-08 14:30 | 7.95 | 7.93
2017-10-08 15:00 | 8.1 | 8.08
2017-10-08 15:30 | 8.22 | 8.2
2017-10-08 16:00 | 7.54 | 7.52
2017-10-08 16:30 | 8.1 | 8.08
2017-10-08 17:00 | 8.84 | 8.83
2017-10-08 17:30 | 10.03 | 10.02
2017-10-08 18:00 | 11.14 | 11.13
2017-10-08 18:30 | 11.94 | 11.92
2017-10-08 19:00 | 11.49 | 11.47
2017-10-08 19:30 | 11 | 10.98
2017-10-08 20:00 | 10.63 | 10.62
2017-10-08 20:30 | 10.31 | 10.29
2017-10-08 21:00 | 9.75 | 9.74
2017-10-08 21:30 | 9.13 | 9.12
2017-10-08 22:00 | 8.34 | 8.33
2017-10-08 22:30 | 7.97 | 7.96
2017-10-08 23:00 | 7.6 | 7.59
2017-10-08 23:30 | 6.65 | 6.64
2017-10-09 | 5.81 | 5.8
2017-10-09 00:30 | 5.14 | 5.13
2017-10-09 01:00 | 4.82 | 4.81
2017-10-09 01:30 | 4.56 | 4.54
2017-10-09 02:00 | 4.32 | 4.3
2017-10-09 02:30 | 4.26 | 4.24
2017-10-09 03:00 | 4.12 | 4.1
2017-10-09 03:30 | 4.23 | 4.21
2017-10-09 04:00 | 4.29 | 4.28
2017-10-09 04:30 | 4.37 | 4.35
2017-10-09 05:00 | 4.59 | 4.57
2017-10-09 05:30 | 5.13 | 5.12
2017-10-09 06:00 | 5.76 | 5.75
2017-10-09 06:30 | 6.1 | 6.09
2017-10-09 07:00 | 6.59 | 6.58
2017-10-09 07:30 | 7.04 | 7.04
2017-10-09 08:00 | 7.24 | 7.23
2017-10-09 08:30 | 6.61 | 6.6
2017-10-09 09:00 | 5.89 | 5.88
2017-10-09 09:30 | 5.72 | 5.71
2017-10-09 10:00 | 5.85 | 5.84
2017-10-09 10:30 | 6 | 5.99
2017-10-09 11:00 | 4.32 | 4.3
2017-10-09 11:30 | 3.98 | 3.95
2017-10-09 12:00 | 4.77 | 4.74
2017-10-09 12:30 | 5.7 | 5.67
2017-10-09 13:00 | 6.52 | 6.49
2017-10-09 13:30 | 4.98 | 4.92
2017-10-09 14:00 | 5.99 | 5.94
2017-10-09 14:30 | 6.89 | 6.83
2017-10-09 15:00 | 7.3 | 7.23
2017-10-09 15:30 | 9.18 | 9.13
2017-10-09 16:00 | 10.39 | 10.36
2017-10-09 16:30 | 10.06 | 10.03
2017-10-09 17:00 | 10.25 | 10.22
2017-10-09 17:30 | 11.13 | 11.1
2017-10-09 18:00 | 11.53 | 11.5
2017-10-09 18:30 | 12.43 | 12.38
2017-10-09 19:00 | 13.12 | 13.06
2017-10-09 19:30 | 12.55 | 12.5
2017-10-09 20:00 | 12.36 | 12.32
2017-10-09 20:30 | 11.93 | 11.9
2017-10-09 21:00 | 11.11 | 11.09
2017-10-09 21:30 | 10.1 | 10.09
2017-10-09 22:00 | 9.14 | 9.13
2017-10-09 22:30 | 8.36 | 8.35
2017-10-09 23:00 | 8.11 | 8.1
2017-10-09 23:30 | 7.13 | 7.12
2017-10-10 | 6.31 | 6.3
2017-10-10 00:30 | 5.66 | 5.65
2017-10-10 01:00 | 5.39 | 5.37
2017-10-10 01:30 | 5.03 | 5.02
2017-10-10 02:00 | 4.82 | 4.81
2017-10-10 02:30 | 4.6 | 4.59
2017-10-10 03:00 | 4.59 | 4.58
2017-10-10 03:30 | 4.62 | 4.6
2017-10-10 04:00 | 4.66 | 4.64
2017-10-10 04:30 | 4.69 | 4.67
2017-10-10 05:00 | 4.96 | 4.94
2017-10-10 05:30 | 5.36 | 5.34
2017-10-10 06:00 | 5.87 | 5.85
2017-10-10 06:30 | 6.01 | 6
2017-10-10 07:00 | 6.1 | 6.09
2017-10-10 07:30 | 6.35 | 6.34
2017-10-10 08:00 | 6.03 | 6.01
2017-10-10 08:30 | 5.18 | 5.16
2017-10-10 09:00 | 4.99 | 4.96
2017-10-10 09:30 | 5.13 | 5.1
2017-10-10 10:00 | 5.5 | 5.45
2017-10-10 10:30 | 5.95 | 5.87
2017-10-10 11:00 | 6.68 | 6.58
2017-10-10 11:30 | 7.85 | 7.74
2017-10-10 12:00 | 8.1 | 7.97
2017-10-10 12:30 | 8.7 | 8.58
2017-10-10 13:00 | 9.87 | 9.76
2017-10-10 13:30 | 10.74 | 10.65
2017-10-10 14:00 | 8.29 | 8.16
2017-10-10 14:30 | 8.85 | 8.72
2017-10-10 15:00 | 9.29 | 9.17
2017-10-10 15:30 | 10.05 | 9.94
2017-10-10 16:00 | 11.16 | 11.05
2017-10-10 16:30 | 11.88 | 11.77
2017-10-10 17:00 | 12.48 | 12.39
2017-10-10 17:30 | 12.3 | 12.23
2017-10-10 18:00 | 12.43 | 12.37
2017-10-10 18:30 | 13.29 | 13.19
2017-10-10 19:00 | 13.87 | 13.78
2017-10-10 19:30 | 13.32 | 13.23
2017-10-10 20:00 | 12.95 | 12.89
2017-10-10 20:30 | 12.46 | 12.42
2017-10-10 21:00 | 11.56 | 11.53
2017-10-10 21:30 | 10.53 | 10.51
2017-10-10 22:00 | 9.54 | 9.52
2017-10-10 22:30 | 9 | 8.99
2017-10-10 23:00 | 8.46 | 8.45
2017-10-10 23:30 | 7.43 | 7.41
2017-10-11 | 6.48 | 6.47
2017-10-11 00:30 | 5.84 | 5.83
2017-10-11 01:00 | 5.57 | 5.56
2017-10-11 01:30 | 5.23 | 5.22
2017-10-11 02:00 | 5.03 | 5.01
2017-10-11 02:30 | 4.86 | 4.84
2017-10-11 03:00 | 4.71 | 4.7
2017-10-11 03:30 | 4.72 | 4.71
2017-10-11 04:00 | 4.7 | 4.68
2017-10-11 04:30 | 4.81 | 4.8
2017-10-11 05:00 | 5.05 | 5.03
2017-10-11 05:30 | 5.4 | 5.38
2017-10-11 06:00 | 6.07 | 6.06
2017-10-11 06:30 | 6.55 | 6.54
2017-10-11 07:00 | 7.17 | 7.16
2017-10-11 07:30 | 7.39 | 7.38
2017-10-11 08:00 | 6.79 | 6.78
2017-10-11 08:30 | 6.01 | 6
2017-10-11 09:00 | 6.24 | 6.22
2017-10-11 09:30 | 6.5 | 6.49
2017-10-11 10:00 | 7.12 | 7.11
2017-10-11 10:30 | 6.99 | 6.98
2017-10-11 11:00 | 6.75 | 6.73
2017-10-11 11:30 | 6.31 | 6.29
2017-10-11 12:00 | 6.28 | 6.25
2017-10-11 12:30 | 6.79 | 6.76
2017-10-11 13:00 | 6.2 | 6.16
2017-10-11 13:30 | 7.32 | 7.28
2017-10-11 14:00 | 7.66 | 7.62
2017-10-11 14:30 | 7.47 | 7.42
2017-10-11 15:00 | 7.11 | 7.06
2017-10-11 15:30 | 7.89 | 7.83
2017-10-11 16:00 | 8.72 | 8.66
2017-10-11 16:30 | 10.17 | 10.11
2017-10-11 17:00 | 10.8 | 10.76
2017-10-11 17:30 | 11.03 | 11
2017-10-11 18:00 | 11.27 | 11.24
2017-10-11 18:30 | 12.4 | 12.34
2017-10-11 19:00 | 12.9 | 12.84
2017-10-11 19:30 | 12.54 | 12.48
2017-10-11 20:00 | 12.38 | 12.33
2017-10-11 20:30 | 12.17 | 12.13
2017-10-11 21:00 | 11.38 | 11.35
2017-10-11 21:30 | 10.45 | 10.43
2017-10-11 22:00 | 9.49 | 9.48
2017-10-11 22:30 | 8.81 | 8.8
2017-10-11 23:00 | 8.45 | 8.44
2017-10-11 23:30 | 7.29 | 7.27
2017-10-12 | 6.47 | 6.46
2017-10-12 00:30 | 5.78 | 5.77
2017-10-12 01:00 | 5.51 | 5.5
2017-10-12 01:30 | 5.23 | 5.21
2017-10-12 02:00 | 4.95 | 4.93
2017-10-12 02:30 | 4.83 | 4.82
2017-10-12 03:00 | 4.77 | 4.75
2017-10-12 03:30 | 4.72 | 4.71
2017-10-12 04:00 | 4.78 | 4.76
2017-10-12 04:30 | 4.85 | 4.84
2017-10-12 05:00 | 5.12 | 5.1
2017-10-12 05:30 | 5.49 | 5.47
2017-10-12 06:00 | 6.11 | 6.1
2017-10-12 06:30 | 6.49 | 6.48
2017-10-12 07:00 | 6.83 | 6.82
2017-10-12 07:30 | 7.79 | 7.79
2017-10-12 08:00 | 7.72 | 7.72
2017-10-12 08:30 | 7.48 | 7.48
2017-10-12 09:00 | 7.25 | 7.24
2017-10-12 09:30 | 7.12 | 7.11
2017-10-12 10:00 | 7 | 6.99
2017-10-12 10:30 | 7.54 | 7.53
2017-10-12 11:00 | 6.97 | 6.96
2017-10-12 11:30 | 7.04 | 7.03
2017-10-12 12:00 | 7.3 | 7.29
2017-10-12 12:30 | 7.47 | 7.46
2017-10-12 13:00 | 7.05 | 7.04
2017-10-12 13:30 | 6.7 | 6.68
2017-10-12 14:00 | 6.61 | 6.6
2017-10-12 14:30 | 6.59 | 6.58
2017-10-12 15:00 | 6.71 | 6.7
2017-10-12 15:30 | 7.16 | 7.15
2017-10-12 16:00 | 7.7 | 7.69
2017-10-12 16:30 | 8.32 | 8.31
2017-10-12 17:00 | 8.57 | 8.55
2017-10-12 17:30 | 9.23 | 9.21
2017-10-12 18:00 | 9.93 | 9.92
2017-10-12 18:30 | 10.86 | 10.83
2017-10-12 19:00 | 11.59 | 11.56
2017-10-12 19:30 | 11.41 | 11.39
2017-10-12 20:00 | 11.12 | 11.1
2017-10-12 20:30 | 11.11 | 11.09
2017-10-12 21:00 | 10.56 | 10.54
2017-10-12 21:30 | 9.9 | 9.89
2017-10-12 22:00 | 9.07 | 9.06
2017-10-12 22:30 | 8.46 | 8.45
2017-10-12 23:00 | 8.08 | 8.06
2017-10-12 23:30 | 7.06 | 7.04
2017-10-13 | 6.15 | 6.14
2017-10-13 00:30 | 5.5 | 5.49
2017-10-13 01:00 | 5.15 | 5.14
2017-10-13 01:30 | 4.93 | 4.92
2017-10-13 02:00 | 4.57 | 4.55
2017-10-13 02:30 | 4.4 | 4.38
2017-10-13 03:00 | 4.35 | 4.33
2017-10-13 03:30 | 4.49 | 4.47
2017-10-13 04:00 | 4.5 | 4.48
2017-10-13 04:30 | 4.66 | 4.64
2017-10-13 05:00 | 4.82 | 4.8
2017-10-13 05:30 | 5.19 | 5.17
2017-10-13 06:00 | 5.55 | 5.53
2017-10-13 06:30 | 6.03 | 6.01
2017-10-13 07:00 | 6.19 | 6.18
2017-10-13 07:30 | 6.61 | 6.6
2017-10-13 08:00 | 6.34 | 6.33
2017-10-13 08:30 | 4.84 | 4.82
2017-10-13 09:00 | 4.24 | 4.22
2017-10-13 09:30 | 4.17 | 4.14
2017-10-13 10:00 | 3.92 | 3.88
2017-10-13 10:30 | 4.01 | 3.96
2017-10-13 11:00 | 4.68 | 4.64
2017-10-13 11:30 | 5.01 | 4.96
2017-10-13 12:00 | 5.67 | 5.62
2017-10-13 12:30 | 6.47 | 6.41
2017-10-13 13:00 | 6.66 | 6.58
2017-10-13 13:30 | 7.47 | 7.39
2017-10-13 14:00 | 7.91 | 7.84
2017-10-13 14:30 | 7.69 | 7.6
2017-10-13 15:00 | 9.12 | 9.04
2017-10-13 15:30 | 8.9 | 8.82
2017-10-13 16:00 | 9.76 | 9.69
2017-10-13 16:30 | 9.77 | 9.72
2017-10-13 17:00 | 10.18 | 10.14
2017-10-13 17:30 | 10.35 | 10.32
2017-10-13 18:00 | 10.59 | 10.56
2017-10-13 18:30 | 11.25 | 11.2
2017-10-13 19:00 | 11.81 | 11.76
2017-10-13 19:30 | 11.46 | 11.42
2017-10-13 20:00 | 11.17 | 11.14
2017-10-13 20:30 | 10.88 | 10.85
2017-10-13 21:00 | 10.45 | 10.43
2017-10-13 21:30 | 9.85 | 9.83
2017-10-13 22:00 | 9.3 | 9.28
2017-10-13 22:30 | 8.94 | 8.93
2017-10-13 23:00 | 8.58 | 8.57
2017-10-13 23:30 | 7.58 | 7.56
2017-10-14 | 6.61 | 6.6
2017-10-14 00:30 | 5.96 | 5.95
2017-10-14 01:00 | 5.76 | 5.74
2017-10-14 01:30 | 5.44 | 5.43
2017-10-14 02:00 | 5.13 | 5.11
2017-10-14 02:30 | 4.9 | 4.89
2017-10-14 03:00 | 4.75 | 4.73
2017-10-14 03:30 | 4.79 | 4.77
2017-10-14 04:00 | 4.59 | 4.57
2017-10-14 04:30 | 4.65 | 4.63
2017-10-14 05:00 | 4.72 | 4.7
2017-10-14 05:30 | 4.61 | 4.58
2017-10-14 06:00 | 4.61 | 4.56
2017-10-14 06:30 | 4.73 | 4.68
2017-10-14 07:00 | 5.15 | 5.11
2017-10-14 07:30 | 5.68 | 5.66
2017-10-14 08:00 | 5.7 | 5.68
2017-10-14 08:30 | 5.84 | 5.82
2017-10-14 09:00 | 6.14 | 6.11
2017-10-14 09:30 | 5.79 | 5.76
2017-10-14 10:00 | 5.37 | 5.33
2017-10-14 10:30 | 6.28 | 6.25
2017-10-14 11:00 | 6.25 | 6.21
2017-10-14 11:30 | 6.86 | 6.82
2017-10-14 12:00 | 6.71 | 6.67
2017-10-14 12:30 | 7.03 | 6.99
2017-10-14 13:00 | 7.15 | 7.1
2017-10-14 13:30 | 7.08 | 7.03
2017-10-14 14:00 | 7.95 | 7.92
2017-10-14 14:30 | 8.11 | 8.08
2017-10-14 15:00 | 7.52 | 7.49
2017-10-14 15:30 | 7.18 | 7.16
2017-10-14 16:00 | 7.58 | 7.55
2017-10-14 16:30 | 8.03 | 8.01
2017-10-14 17:00 | 8.53 | 8.51
2017-10-14 17:30 | 8.92 | 8.9
2017-10-14 18:00 | 9.23 | 9.22
2017-10-14 18:30 | 10.16 | 10.14
2017-10-14 19:00 | 10.27 | 10.26
2017-10-14 19:30 | 9.84 | 9.82
2017-10-14 20:00 | 9.59 | 9.57
2017-10-14 20:30 | 9.51 | 9.5
2017-10-14 21:00 | 9.06 | 9.05
2017-10-14 21:30 | 8.53 | 8.52
2017-10-14 22:00 | 7.94 | 7.93
2017-10-14 22:30 | 7.69 | 7.68
2017-10-14 23:00 | 7.62 | 7.61
2017-10-14 23:30 | 6.91 | 6.91
2017-10-15 | 6.02 | 6.01
2017-10-15 00:30 | 5.41 | 5.4
2017-10-15 01:00 | 5.04 | 5.03
2017-10-15 01:30 | 4.79 | 4.77
2017-10-15 02:00 | 4.56 | 4.55
2017-10-15 02:30 | 4.4 | 4.38
2017-10-15 03:00 | 4.24 | 4.21
2017-10-15 03:30 | 4.15 | 4.12
2017-10-15 04:00 | 4 | 3.97
2017-10-15 04:30 | 4.1 | 4.08
2017-10-15 05:00 | 4.2 | 4.17
2017-10-15 05:30 | 4.11 | 4.05
2017-10-15 06:00 | 4.12 | 4.03
2017-10-15 06:30 | 4.13 | 4.04
2017-10-15 07:00 | 4.81 | 4.74
2017-10-15 07:30 | 4.84 | 4.78
2017-10-15 08:00 | 5.75 | 5.71
2017-10-15 08:30 | 6.89 | 6.87
2017-10-15 09:00 | 7.53 | 7.52
2017-10-15 09:30 | 7.35 | 7.33
2017-10-15 10:00 | 8.39 | 8.38
2017-10-15 10:30 | 8.23 | 8.22
2017-10-15 11:00 | 8.35 | 8.34
2017-10-15 11:30 | 6.44 | 6.42
2017-10-15 12:00 | 7.93 | 7.92
2017-10-15 12:30 | 8.09 | 8.08
2017-10-15 13:00 | 8.2 | 8.19
2017-10-15 13:30 | 6.45 | 6.43
2017-10-15 14:00 | 6.82 | 6.8
2017-10-15 14:30 | 8.34 | 8.33
2017-10-15 15:00 | 7.55 | 7.54
2017-10-15 15:30 | 8.13 | 8.12
2017-10-15 16:00 | 8.49 | 8.48
2017-10-15 16:30 | 8.78 | 8.77
2017-10-15 17:00 | 9.78 | 9.77
2017-10-15 17:30 | 10.33 | 10.32
2017-10-15 18:00 | 10.49 | 10.48
2017-10-15 18:30 | 10.88 | 10.87
2017-10-15 19:00 | 10.95 | 10.93
2017-10-15 19:30 | 10.3 | 10.29
2017-10-15 20:00 | 10.03 | 10.02
2017-10-15 20:30 | 9.87 | 9.86
2017-10-15 21:00 | 9.3 | 9.3
2017-10-15 21:30 | 8.72 | 8.71
2017-10-15 22:00 | 8.09 | 8.08
2017-10-15 22:30 | 7.56 | 7.55
2017-10-15 23:00 | 7.29 | 7.28
2017-10-15 23:30 | 6.4 | 6.39
2017-10-16 | 5.58 | 5.56
2017-10-16 00:30 | 4.92 | 4.9
2017-10-16 01:00 | 4.67 | 4.64
2017-10-16 01:30 | 4.28 | 4.25
2017-10-16 02:00 | 4.07 | 4.03
2017-10-16 02:30 | 3.97 | 3.94
2017-10-16 03:00 | 3.94 | 3.9
2017-10-16 03:30 | 3.96 | 3.93
2017-10-16 04:00 | 3.85 | 3.82
2017-10-16 04:30 | 4.37 | 4.34
2017-10-16 05:00 | 4.41 | 4.39
2017-10-16 05:30 | 4.65 | 4.61
2017-10-16 06:00 | 4.99 | 4.94
2017-10-16 06:30 | 5.7 | 5.67
2017-10-16 07:00 | 5.81 | 5.78
2017-10-16 07:30 | 5.94 | 5.92
2017-10-16 08:00 | 5.8 | 5.78
2017-10-16 08:30 | 5.72 | 5.7
2017-10-16 09:00 | 6.21 | 6.2
2017-10-16 09:30 | 5.8 | 5.79
2017-10-16 10:00 | 5.42 | 5.41
2017-10-16 10:30 | 6.02 | 6.01
2017-10-16 11:00 | 6.38 | 6.37
2017-10-16 11:30 | 5.73 | 5.72
2017-10-16 12:00 | 5.61 | 5.6
2017-10-16 12:30 | 5.91 | 5.9
2017-10-16 13:00 | 6.56 | 6.55
2017-10-16 13:30 | 6.49 | 6.48
2017-10-16 14:00 | 6.74 | 6.73
2017-10-16 14:30 | 6.86 | 6.85
2017-10-16 15:00 | 7.23 | 7.23
2017-10-16 15:30 | 7.53 | 7.52
2017-10-16 16:00 | 7.57 | 7.56
2017-10-16 16:30 | 8.35 | 8.34
2017-10-16 17:00 | 9.21 | 9.19
2017-10-16 17:30 | 9.71 | 9.7
2017-10-16 18:00 | 10.14 | 10.13
2017-10-16 18:30 | 11 | 10.98
2017-10-16 19:00 | 11.43 | 11.42
2017-10-16 19:30 | 11.04 | 11.03
2017-10-16 20:00 | 10.76 | 10.74
2017-10-16 20:30 | 10.63 | 10.62
2017-10-16 21:00 | 10.1 | 10.09
2017-10-16 21:30 | 9.36 | 9.34
2017-10-16 22:00 | 8.43 | 8.42
2017-10-16 22:30 | 7.74 | 7.73
2017-10-16 23:00 | 7.61 | 7.6
2017-10-16 23:30 | 6.7 | 6.69
2017-10-17 | 5.95 | 5.94
2017-10-17 00:30 | 5.3 | 5.28
2017-10-17 01:00 | 5.02 | 5.01
2017-10-17 01:30 | 4.65 | 4.63
2017-10-17 02:00 | 4.32 | 4.3
2017-10-17 02:30 | 4.21 | 4.18
2017-10-17 03:00 | 4.22 | 4.2
2017-10-17 03:30 | 4.23 | 4.2
2017-10-17 04:00 | 4.29 | 4.27
2017-10-17 04:30 | 4.48 | 4.46
2017-10-17 05:00 | 4.71 | 4.7
2017-10-17 05:30 | 5.04 | 5.01
2017-10-17 06:00 | 5.32 | 5.28
2017-10-17 06:30 | 5.74 | 5.71
2017-10-17 07:00 | 6.35 | 6.33
2017-10-17 07:30 | 7.11 | 7.1
2017-10-17 08:00 | 7.52 | 7.51
2017-10-17 08:30 | 6.85 | 6.85
2017-10-17 09:00 | 6.86 | 6.86
2017-10-17 09:30 | 6.2 | 6.2
2017-10-17 10:00 | 6.1 | 6.09
2017-10-17 10:30 | 5.74 | 5.74
2017-10-17 11:00 | 6.33 | 6.33
2017-10-17 11:30 | 6.36 | 6.36
2017-10-17 12:00 | 6.55 | 6.55
2017-10-17 12:30 | 6.67 | 6.67
2017-10-17 13:00 | 6.75 | 6.74
2017-10-17 13:30 | 6.33 | 6.32
2017-10-17 14:00 | 6.42 | 6.41
2017-10-17 14:30 | 6.33 | 6.32
2017-10-17 15:00 | 6.59 | 6.58
2017-10-17 15:30 | 7.27 | 7.26
2017-10-17 16:00 | 8.01 | 8
2017-10-17 16:30 | 8.83 | 8.82
2017-10-17 17:00 | 9.54 | 9.54
2017-10-17 17:30 | 10.14 | 10.13
2017-10-17 18:00 | 10.82 | 10.81
2017-10-17 18:30 | 11.58 | 11.57
2017-10-17 19:00 | 11.89 | 11.88
2017-10-17 19:30 | 11.48 | 11.47
2017-10-17 20:00 | 11.29 | 11.29
2017-10-17 20:30 | 11.05 | 11.04
2017-10-17 21:00 | 10.35 | 10.34
2017-10-17 21:30 | 9.5 | 9.5
2017-10-17 22:00 | 8.53 | 8.53
2017-10-17 22:30 | 8.07 | 8.06
2017-10-17 23:00 | 7.85 | 7.85
2017-10-17 23:30 | 6.92 | 6.91
2017-10-18 | 5.96 | 5.95
2017-10-18 00:30 | 5.44 | 5.42
2017-10-18 01:00 | 5.09 | 5.07
2017-10-18 01:30 | 4.76 | 4.74
2017-10-18 02:00 | 4.61 | 4.59
2017-10-18 02:30 | 4.41 | 4.38
2017-10-18 03:00 | 4.26 | 4.23
2017-10-18 03:30 | 4.41 | 4.39
2017-10-18 04:00 | 4.49 | 4.47
2017-10-18 04:30 | 4.71 | 4.69
2017-10-18 05:00 | 4.97 | 4.95
2017-10-18 05:30 | 5.25 | 5.22
2017-10-18 06:00 | 5.95 | 5.91
2017-10-18 06:30 | 6.49 | 6.47
2017-10-18 07:00 | 6.85 | 6.83
2017-10-18 07:30 | 7.4 | 7.39
2017-10-18 08:00 | 7.07 | 7.06
2017-10-18 08:30 | 6.61 | 6.6
2017-10-18 09:00 | 5.55 | 5.55
2017-10-18 09:30 | 4.85 | 4.84
2017-10-18 10:00 | 4.93 | 4.92
2017-10-18 10:30 | 4.36 | 4.35
2017-10-18 11:00 | 6.63 | 6.62
2017-10-18 11:30 | 6.1 | 6.09
2017-10-18 12:00 | 4.96 | 4.95
2017-10-18 12:30 | 4.81 | 4.8
2017-10-18 13:00 | 5.93 | 5.92
2017-10-18 13:30 | 5.02 | 5.01
2017-10-18 14:00 | 4.78 | 4.78
2017-10-18 14:30 | 5.44 | 5.43
2017-10-18 15:00 | 5.88 | 5.88
2017-10-18 15:30 | 6.21 | 6.21
2017-10-18 16:00 | 7.21 | 7.2
2017-10-18 16:30 | 7.9 | 7.9
2017-10-18 17:00 | 8.85 | 8.84
2017-10-18 17:30 | 9.63 | 9.63
2017-10-18 18:00 | 10.38 | 10.38
2017-10-18 18:30 | 11.04 | 11.03
2017-10-18 19:00 | 11.44 | 11.42
2017-10-18 19:30 | 11.52 | 11.51
2017-10-18 20:00 | 11.28 | 11.27
2017-10-18 20:30 | 11.22 | 11.21
2017-10-18 21:00 | 10.65 | 10.64
2017-10-18 21:30 | 9.59 | 9.59
2017-10-18 22:00 | 8.6 | 8.6
2017-10-18 22:30 | 8.1 | 8.09
2017-10-18 23:00 | 7.59 | 7.58
2017-10-18 23:30 | 6.57 | 6.57
2017-10-19 | 5.61 | 5.59
2017-10-19 00:30 | 4.99 | 4.97
2017-10-19 01:00 | 4.66 | 4.64
2017-10-19 01:30 | 4.43 | 4.41
2017-10-19 02:00 | 4.18 | 4.16
2017-10-19 02:30 | 4.08 | 4.06
2017-10-19 03:00 | 3.98 | 3.95
2017-10-19 03:30 | 3.96 | 3.94
2017-10-19 04:00 | 4.03 | 4.01
2017-10-19 04:30 | 4.23 | 4.21
2017-10-19 05:00 | 4.43 | 4.41
2017-10-19 05:30 | 4.87 | 4.83
2017-10-19 06:00 | 5.47 | 5.43
2017-10-19 06:30 | 6.06 | 6.04
2017-10-19 07:00 | 6.01 | 5.99
2017-10-19 07:30 | 5.95 | 5.94
2017-10-19 08:00 | 5.31 | 5.3
2017-10-19 08:30 | 5.19 | 5.18
2017-10-19 09:00 | 6.03 | 6.03
2017-10-19 09:30 | 5.88 | 5.87
2017-10-19 10:00 | 4.88 | 4.87
2017-10-19 10:30 | 5.48 | 5.48
2017-10-19 11:00 | 3.81 | 3.8
2017-10-19 11:30 | 5.82 | 5.81
2017-10-19 12:00 | 4.32 | 4.31
2017-10-19 12:30 | 5.74 | 5.74
2017-10-19 13:00 | 6.29 | 6.29
2017-10-19 13:30 | 7.69 | 7.68
2017-10-19 14:00 | 7.09 | 7.09
2017-10-19 14:30 | 7 | 7
2017-10-19 15:00 | 5.66 | 5.66
2017-10-19 15:30 | 6.08 | 6.07
2017-10-19 16:00 | 6.96 | 6.96
2017-10-19 16:30 | 7.55 | 7.55
2017-10-19 17:00 | 8.35 | 8.35
2017-10-19 17:30 | 8.7 | 8.7
2017-10-19 18:00 | 9.2 | 9.2
2017-10-19 18:30 | 10.25 | 10.23
2017-10-19 19:00 | 11.25 | 11.23
2017-10-19 19:30 | 11.02 | 11
2017-10-19 20:00 | 10.83 | 10.82
2017-10-19 20:30 | 10.78 | 10.77
2017-10-19 21:00 | 10.28 | 10.27
2017-10-19 21:30 | 9.62 | 9.62
2017-10-19 22:00 | 8.74 | 8.74
2017-10-19 22:30 | 7.9 | 7.89
2017-10-19 23:00 | 7.51 | 7.5
2017-10-19 23:30 | 6.49 | 6.48
2017-10-20 | 5.61 | 5.6
2017-10-20 00:30 | 5.01 | 4.99
2017-10-20 01:00 | 4.77 | 4.75
2017-10-20 01:30 | 4.43 | 4.41
2017-10-20 02:00 | 4.15 | 4.13
2017-10-20 02:30 | 3.98 | 3.95
2017-10-20 03:00 | 3.9 | 3.87
2017-10-20 03:30 | 3.96 | 3.94
2017-10-20 04:00 | 4.04 | 4.01
2017-10-20 04:30 | 4.29 | 4.27
2017-10-20 05:00 | 4.36 | 4.34
2017-10-20 05:30 | 4.69 | 4.65
2017-10-20 06:00 | 5.37 | 5.33
2017-10-20 06:30 | 5.75 | 5.72
2017-10-20 07:00 | 5.89 | 5.87
2017-10-20 07:30 | 6.36 | 6.35
2017-10-20 08:00 | 5.56 | 5.56
2017-10-20 08:30 | 4.32 | 4.31
2017-10-20 09:00 | 4.68 | 4.67
2017-10-20 09:30 | 5.22 | 5.22
2017-10-20 10:00 | 4.68 | 4.67
2017-10-20 10:30 | 4.2 | 4.18
2017-10-20 11:00 | 4.95 | 4.93
2017-10-20 11:30 | 5.49 | 5.48
2017-10-20 12:00 | 3.67 | 3.65
2017-10-20 12:30 | 4.99 | 4.97
2017-10-20 13:00 | 5.14 | 5.12
2017-10-20 13:30 | 4.54 | 4.52
2017-10-20 14:00 | 5.14 | 5.12
2017-10-20 14:30 | 4.12 | 4.09
2017-10-20 15:00 | 4.45 | 4.42
2017-10-20 15:30 | 5.33 | 5.31
2017-10-20 16:00 | 6.91 | 6.89
2017-10-20 16:30 | 7.37 | 7.35
2017-10-20 17:00 | 7.97 | 7.95
2017-10-20 17:30 | 8.47 | 8.46
2017-10-20 18:00 | 8.8 | 8.78
2017-10-20 18:30 | 9.62 | 9.61
2017-10-20 19:00 | 10.39 | 10.37
2017-10-20 19:30 | 10.35 | 10.33
2017-10-20 20:00 | 10.18 | 10.16
2017-10-20 20:30 | 10.05 | 10.03
2017-10-20 21:00 | 9.49 | 9.48
2017-10-20 21:30 | 8.77 | 8.76
2017-10-20 22:00 | 8.08 | 8.07
2017-10-20 22:30 | 7.7 | 7.7
2017-10-20 23:00 | 7.56 | 7.56
2017-10-20 23:30 | 6.69 | 6.68
2017-10-21 | 5.88 | 5.87
2017-10-21 00:30 | 5.29 | 5.28
2017-10-21 01:00 | 5.01 | 5
2017-10-21 01:30 | 4.69 | 4.68
2017-10-21 02:00 | 4.43 | 4.41
2017-10-21 02:30 | 4.25 | 4.22
2017-10-21 03:00 | 4.16 | 4.13
2017-10-21 03:30 | 4.25 | 4.23
2017-10-21 04:00 | 4.17 | 4.15
2017-10-21 04:30 | 4.12 | 4.09
2017-10-21 05:00 | 4.2 | 4.18
2017-10-21 05:30 | 4.23 | 4.18
2017-10-21 06:00 | 4.47 | 4.41
2017-10-21 06:30 | 4.77 | 4.72
2017-10-21 07:00 | 5.16 | 5.12
2017-10-21 07:30 | 5.74 | 5.71
2017-10-21 08:00 | 6.21 | 6.19
2017-10-21 08:30 | 6.93 | 6.92
2017-10-21 09:00 | 7.33 | 7.31
2017-10-21 09:30 | 7.68 | 7.66
2017-10-21 10:00 | 7.97 | 7.96
2017-10-21 10:30 | 7.96 | 7.94
2017-10-21 11:00 | 7.33 | 7.31
2017-10-21 11:30 | 7.41 | 7.4
2017-10-21 12:00 | 7.59 | 7.58
2017-10-21 12:30 | 7.44 | 7.43
2017-10-21 13:00 | 7.44 | 7.42
2017-10-21 13:30 | 7.57 | 7.55
2017-10-21 14:00 | 7.66 | 7.65
2017-10-21 14:30 | 7.52 | 7.51
2017-10-21 15:00 | 7.57 | 7.56
2017-10-21 15:30 | 7.63 | 7.62
2017-10-21 16:00 | 7.82 | 7.81
2017-10-21 16:30 | 8.12 | 8.11
2017-10-21 17:00 | 8.47 | 8.46
2017-10-21 17:30 | 8.73 | 8.72
2017-10-21 18:00 | 9.23 | 9.22
2017-10-21 18:30 | 9.69 | 9.69
2017-10-21 19:00 | 10.15 | 10.14
2017-10-21 19:30 | 9.83 | 9.82
2017-10-21 20:00 | 9.66 | 9.66
2017-10-21 20:30 | 9.61 | 9.6
2017-10-21 21:00 | 8.97 | 8.96
2017-10-21 21:30 | 8.34 | 8.33
2017-10-21 22:00 | 7.9 | 7.89
2017-10-21 22:30 | 7.66 | 7.66
2017-10-21 23:00 | 7.63 | 7.62
2017-10-21 23:30 | 6.89 | 6.88
2017-10-22 | 6.12 | 6.1
2017-10-22 00:30 | 5.42 | 5.4
2017-10-22 01:00 | 5.05 | 5.02
2017-10-22 01:30 | 4.73 | 4.7
2017-10-22 02:00 | 4.34 | 4.31
2017-10-22 02:30 | 4.08 | 4.04
2017-10-22 03:00 | 4.07 | 4.03
2017-10-22 03:30 | 4.03 | 3.99
2017-10-22 04:00 | 4.01 | 3.97
2017-10-22 04:30 | 4 | 3.97
2017-10-22 05:00 | 3.95 | 3.9
2017-10-22 05:30 | 3.89 | 3.78
2017-10-22 06:00 | 3.95 | 3.82
2017-10-22 06:30 | 3.76 | 3.63
2017-10-22 07:00 | 3.67 | 3.55
2017-10-22 07:30 | 3.85 | 3.77
2017-10-22 08:00 | 3.72 | 3.66
2017-10-22 08:30 | 3.8 | 3.77
2017-10-22 09:00 | 3.65 | 3.62
2017-10-22 09:30 | 3.66 | 3.63
2017-10-22 10:00 | 3.51 | 3.48
2017-10-22 10:30 | 3.66 | 3.62
2017-10-22 11:00 | 3.8 | 3.76
2017-10-22 11:30 | 4.05 | 4.02
2017-10-22 12:00 | 4.07 | 4.04
2017-10-22 12:30 | 3.93 | 3.9
2017-10-22 13:00 | 3.84 | 3.8
2017-10-22 13:30 | 4.27 | 4.23
2017-10-22 14:00 | 4.77 | 4.74
2017-10-22 14:30 | 4.93 | 4.9
2017-10-22 15:00 | 5.25 | 5.22
2017-10-22 15:30 | 5.95 | 5.93
2017-10-22 16:00 | 6.76 | 6.74
2017-10-22 16:30 | 7.62 | 7.61
2017-10-22 17:00 | 8.16 | 8.15
2017-10-22 17:30 | 8.79 | 8.78
2017-10-22 18:00 | 9.33 | 9.31
2017-10-22 18:30 | 10.07 | 10.05
2017-10-22 19:00 | 10.75 | 10.74
2017-10-22 19:30 | 10.29 | 10.28
2017-10-22 20:00 | 9.89 | 9.88
2017-10-22 20:30 | 9.78 | 9.77
2017-10-22 21:00 | 9.33 | 9.32
2017-10-22 21:30 | 8.63 | 8.62
2017-10-22 22:00 | 7.91 | 7.9
2017-10-22 22:30 | 7.5 | 7.49
2017-10-22 23:00 | 7.25 | 7.24
2017-10-22 23:30 | 6.29 | 6.28
2017-10-23 | 5.53 | 5.51
2017-10-23 00:30 | 4.83 | 4.81
2017-10-23 01:00 | 4.53 | 4.5
2017-10-23 01:30 | 4.95 | 4.92
2017-10-23 02:00 | 5.55 | 5.51
2017-10-23 02:30 | 5.38 | 5.34
2017-10-23 03:00 | 5.07 | 5.03
2017-10-23 03:30 | 4.22 | 4.18
2017-10-23 04:00 | 3.92 | 3.89
2017-10-23 04:30 | 4.21 | 4.18
2017-10-23 05:00 | 4.47 | 4.44
2017-10-23 05:30 | 4.56 | 4.51
2017-10-23 06:00 | 5.31 | 5.27
2017-10-23 06:30 | 5.94 | 5.92
2017-10-23 07:00 | 5.12 | 5.08
2017-10-23 07:30 | 5.12 | 5.09
2017-10-23 08:00 | 4.95 | 4.93
2017-10-23 08:30 | 6.24 | 6.23
2017-10-23 09:00 | 7.02 | 7.02
2017-10-23 09:30 | 6.24 | 6.23
2017-10-23 10:00 | 6.08 | 6.07
2017-10-23 10:30 | 5.79 | 5.79
2017-10-23 11:00 | 5.56 | 5.56
2017-10-23 11:30 | 6.56 | 6.55
2017-10-23 12:00 | 4.37 | 4.36
2017-10-23 12:30 | 2.92 | 2.91
2017-10-23 13:00 | 2.83 | 2.81
2017-10-23 13:30 | 4.65 | 4.64
2017-10-23 14:00 | 6.14 | 6.13
2017-10-23 14:30 | 5.45 | 5.45
2017-10-23 15:00 | 5.6 | 5.6
2017-10-23 15:30 | 6.16 | 6.16
2017-10-23 16:00 | 7.06 | 7.06
2017-10-23 16:30 | 7.76 | 7.75
2017-10-23 17:00 | 8.29 | 8.29
2017-10-23 17:30 | 9.16 | 9.15
2017-10-23 18:00 | 9.95 | 9.94
2017-10-23 18:30 | 11.17 | 11.16
2017-10-23 19:00 | 11.6 | 11.59
2017-10-23 19:30 | 11.26 | 11.25
2017-10-23 20:00 | 10.95 | 10.94
2017-10-23 20:30 | 10.89 | 10.88
2017-10-23 21:00 | 10.34 | 10.34
2017-10-23 21:30 | 9.29 | 9.29
2017-10-23 22:00 | 8.5 | 8.49
2017-10-23 22:30 | 7.59 | 7.59
2017-10-23 23:00 | 8.21 | 8.2
2017-10-23 23:30 | 7.44 | 7.43
2017-10-24 | 6.63 | 6.61
2017-10-24 00:30 | 5.88 | 5.85
2017-10-24 01:00 | 5.68 | 5.65
2017-10-24 01:30 | 5.35 | 5.31
2017-10-24 02:00 | 5.12 | 5.08
2017-10-24 02:30 | 5.05 | 5.01
2017-10-24 03:00 | 5.01 | 4.97
2017-10-24 03:30 | 4.99 | 4.94
2017-10-24 04:00 | 5.02 | 4.98
2017-10-24 04:30 | 5.21 | 5.16
2017-10-24 05:00 | 5.47 | 5.42
2017-10-24 05:30 | 5.79 | 5.72
2017-10-24 06:00 | 6.22 | 6.15
2017-10-24 06:30 | 6.45 | 6.4
2017-10-24 07:00 | 6.5 | 6.46
2017-10-24 07:30 | 6.43 | 6.39
2017-10-24 08:00 | 5.91 | 5.89
2017-10-24 08:30 | 4.93 | 4.91
2017-10-24 09:00 | 4.38 | 4.37
2017-10-24 09:30 | 3.98 | 3.96
2017-10-24 10:00 | 3.88 | 3.87
2017-10-24 10:30 | 3.82 | 3.81
2017-10-24 11:00 | 3.7 | 3.69
2017-10-24 11:30 | 3.71 | 3.71
2017-10-24 12:00 | 4.15 | 4.14
2017-10-24 12:30 | 4.09 | 4.08
2017-10-24 13:00 | 4.85 | 4.85
2017-10-24 13:30 | 5.61 | 5.61
2017-10-24 14:00 | 5.68 | 5.68
2017-10-24 14:30 | 6.07 | 6.07
2017-10-24 15:00 | 6.62 | 6.61
2017-10-24 15:30 | 6.87 | 6.86
2017-10-24 16:00 | 8.11 | 8.11
2017-10-24 16:30 | 7.39 | 7.39
2017-10-24 17:00 | 8.14 | 8.14
2017-10-24 17:30 | 9.02 | 9.01
2017-10-24 18:00 | 9.67 | 9.67
2017-10-24 18:30 | 10.59 | 10.58
2017-10-24 19:00 | 11.58 | 11.56
2017-10-24 19:30 | 11.33 | 11.32
2017-10-24 20:00 | 11.11 | 11.1
2017-10-24 20:30 | 11.15 | 11.14
2017-10-24 21:00 | 10.44 | 10.44
2017-10-24 21:30 | 9.51 | 9.5
2017-10-24 22:00 | 8.49 | 8.49
2017-10-24 22:30 | 7.58 | 7.57
2017-10-24 23:00 | 7.22 | 7.21
2017-10-24 23:30 | 6.34 | 6.33
2017-10-25 | 5.48 | 5.47
2017-10-25 00:30 | 4.91 | 4.89
2017-10-25 01:00 | 4.6 | 4.58
2017-10-25 01:30 | 4.33 | 4.3
2017-10-25 02:00 | 4.12 | 4.08
2017-10-25 02:30 | 4.02 | 3.99
2017-10-25 03:00 | 3.89 | 3.85
2017-10-25 03:30 | 3.91 | 3.87
2017-10-25 04:00 | 3.91 | 3.87
2017-10-25 04:30 | 4.13 | 4.1
2017-10-25 05:00 | 4.28 | 4.23
2017-10-25 05:30 | 4.64 | 4.57
2017-10-25 06:00 | 4.85 | 4.78
2017-10-25 06:30 | 5.48 | 5.44
2017-10-25 07:00 | 5.59 | 5.56
2017-10-25 07:30 | 5.48 | 5.47
2017-10-25 08:00 | 4.95 | 4.94
2017-10-25 08:30 | 4.1 | 4.1
2017-10-25 09:00 | 3.61 | 3.6
2017-10-25 09:30 | 3.3 | 3.3
2017-10-25 10:00 | 3.05 | 3.04
2017-10-25 10:30 | 2.97 | 2.96
2017-10-25 11:00 | 3.03 | 3.01
2017-10-25 11:30 | 3.32 | 3.3
2017-10-25 12:00 | 3.56 | 3.53
2017-10-25 12:30 | 4.03 | 4
2017-10-25 13:00 | 5.04 | 5.02
2017-10-25 13:30 | 4.94 | 4.92
2017-10-25 14:00 | 5.26 | 5.23
2017-10-25 14:30 | 5.62 | 5.59
2017-10-25 15:00 | 5.61 | 5.58
2017-10-25 15:30 | 6.56 | 6.53
2017-10-25 16:00 | 7.66 | 7.63
2017-10-25 16:30 | 8.67 | 8.65
2017-10-25 17:00 | 9.51 | 9.49
2017-10-25 17:30 | 10.1 | 10.09
2017-10-25 18:00 | 10.52 | 10.5
2017-10-25 18:30 | 11.39 | 11.36
2017-10-25 19:00 | 12.21 | 12.16
2017-10-25 19:30 | 12.1 | 12.06
2017-10-25 20:00 | 11.75 | 11.73
2017-10-25 20:30 | 11.52 | 11.5
2017-10-25 21:00 | 10.9 | 10.88
2017-10-25 21:30 | 9.61 | 9.6
2017-10-25 22:00 | 8.62 | 8.61
2017-10-25 22:30 | 7.9 | 7.89
2017-10-25 23:00 | 7.56 | 7.55
2017-10-25 23:30 | 6.62 | 6.61
2017-10-26 | 5.81 | 5.8
2017-10-26 00:30 | 5.18 | 5.17
2017-10-26 01:00 | 4.89 | 4.87
2017-10-26 01:30 | 4.56 | 4.54
2017-10-26 02:00 | 4.3 | 4.28
2017-10-26 02:30 | 4.04 | 4.01
2017-10-26 03:00 | 4.01 | 3.99
2017-10-26 03:30 | 4.06 | 4.03
2017-10-26 04:00 | 4.11 | 4.08
2017-10-26 04:30 | 4.26 | 4.24
2017-10-26 05:00 | 4.43 | 4.4
2017-10-26 05:30 | 4.7 | 4.65
2017-10-26 06:00 | 5.08 | 5.03
2017-10-26 06:30 | 5.17 | 5.13
2017-10-26 07:00 | 5.2 | 5.17
2017-10-26 07:30 | 5.21 | 5.19
2017-10-26 08:00 | 4.59 | 4.57
2017-10-26 08:30 | 3.91 | 3.89
2017-10-26 09:00 | 3.4 | 3.38
2017-10-26 09:30 | 3.35 | 3.31
2017-10-26 10:00 | 3.26 | 3.21
2017-10-26 10:30 | 3.26 | 3.21
2017-10-26 11:00 | 3.45 | 3.41
2017-10-26 11:30 | 3.66 | 3.6
2017-10-26 12:00 | 4.05 | 4
2017-10-26 12:30 | 4.55 | 4.49
2017-10-26 13:00 | 5.3 | 5.24
2017-10-26 13:30 | 6.16 | 6.09
2017-10-26 14:00 | 7.21 | 7.13
2017-10-26 14:30 | 9.53 | 9.46
2017-10-26 15:00 | 9.79 | 9.72
2017-10-26 15:30 | 9.33 | 9.24
2017-10-26 16:00 | 10.33 | 10.26
2017-10-26 16:30 | 11.75 | 11.69
2017-10-26 17:00 | 12.35 | 12.29
2017-10-26 17:30 | 12.99 | 12.92
2017-10-26 18:00 | 12.54 | 12.49
2017-10-26 18:30 | 12.3 | 12.24
2017-10-26 19:00 | 12.38 | 12.33
2017-10-26 19:30 | 12.36 | 12.31
2017-10-26 20:00 | 12.49 | 12.44
2017-10-26 20:30 | 12.22 | 12.19
2017-10-26 21:00 | 11.14 | 11.12
2017-10-26 21:30 | 10.51 | 10.5
2017-10-26 22:00 | 9.5 | 9.49
2017-10-26 22:30 | 8.72 | 8.72
2017-10-26 23:00 | 8.13 | 8.12
2017-10-26 23:30 | 7.19 | 7.18
2017-10-27 | 6.28 | 6.27
2017-10-27 00:30 | 5.66 | 5.65
2017-10-27 01:00 | 5.4 | 5.39
2017-10-27 01:30 | 5.01 | 5
2017-10-27 02:00 | 4.82 | 4.81
2017-10-27 02:30 | 4.68 | 4.67
2017-10-27 03:00 | 4.59 | 4.57
2017-10-27 03:30 | 4.52 | 4.5
2017-10-27 04:00 | 4.52 | 4.5
2017-10-27 04:30 | 4.57 | 4.56
2017-10-27 05:00 | 4.72 | 4.7
2017-10-27 05:30 | 4.97 | 4.92
2017-10-27 06:00 | 5.36 | 5.33
2017-10-27 06:30 | 6 | 5.99
2017-10-27 07:00 | 5.92 | 5.91
2017-10-27 07:30 | 5.89 | 5.89
2017-10-27 08:00 | 5.18 | 5.18
2017-10-27 08:30 | 4.25 | 4.24
2017-10-27 09:00 | 3.7 | 3.69
2017-10-27 09:30 | 3.42 | 3.41
2017-10-27 10:00 | 2.95 | 2.92
2017-10-27 10:30 | 3.03 | 2.99
2017-10-27 11:00 | 3.02 | 2.98
2017-10-27 11:30 | 3.45 | 3.42
2017-10-27 12:00 | 3.48 | 3.44
2017-10-27 12:30 | 3.91 | 3.88
2017-10-27 13:00 | 4.32 | 4.27
2017-10-27 13:30 | 4.55 | 4.5
2017-10-27 14:00 | 4.81 | 4.76
2017-10-27 14:30 | 5.3 | 5.25
2017-10-27 15:00 | 6.11 | 6.06
2017-10-27 15:30 | 7.51 | 7.45
2017-10-27 16:00 | 8.74 | 8.69
2017-10-27 16:30 | 9.38 | 9.34
2017-10-27 17:00 | 10.05 | 10.02
2017-10-27 17:30 | 10.5 | 10.47
2017-10-27 18:00 | 10.62 | 10.59
2017-10-27 18:30 | 10.61 | 10.58
2017-10-27 19:00 | 11 | 10.97
2017-10-27 19:30 | 10.8 | 10.77
2017-10-27 20:00 | 10.8 | 10.77
2017-10-27 20:30 | 10.63 | 10.6
2017-10-27 21:00 | 10.08 | 10.06
2017-10-27 21:30 | 9.4 | 9.39
2017-10-27 22:00 | 8.75 | 8.74
2017-10-27 22:30 | 8.36 | 8.35
2017-10-27 23:00 | 8.06 | 8.06
2017-10-27 23:30 | 7.04 | 7.03
2017-10-28 | 6.21 | 6.2
2017-10-28 00:30 | 5.63 | 5.62
2017-10-28 01:00 | 5.37 | 5.36
2017-10-28 01:30 | 4.98 | 4.97
2017-10-28 02:00 | 4.66 | 4.65
2017-10-28 02:30 | 4.47 | 4.45
2017-10-28 03:00 | 4.44 | 4.43
2017-10-28 03:30 | 4.4 | 4.38
2017-10-28 04:00 | 4.38 | 4.36
2017-10-28 04:30 | 4.41 | 4.39
2017-10-28 05:00 | 4.24 | 4.2
2017-10-28 05:30 | 4.51 | 4.45
2017-10-28 06:00 | 4.7 | 4.64
2017-10-28 06:30 | 4.64 | 4.6
2017-10-28 07:00 | 4.66 | 4.63
2017-10-28 07:30 | 4.73 | 4.71
2017-10-28 08:00 | 4.65 | 4.63
2017-10-28 08:30 | 4.69 | 4.68
2017-10-28 09:00 | 4.79 | 4.76
2017-10-28 09:30 | 4.84 | 4.81
2017-10-28 10:00 | 4.89 | 4.85
2017-10-28 10:30 | 5.26 | 5.22
2017-10-28 11:00 | 5.64 | 5.6
2017-10-28 11:30 | 5.53 | 5.48
2017-10-28 12:00 | 5.92 | 5.86
2017-10-28 12:30 | 6.6 | 6.55
2017-10-28 13:00 | 6.85 | 6.78
2017-10-28 13:30 | 7.05 | 6.98
2017-10-28 14:00 | 8.17 | 8.12
2017-10-28 14:30 | 8.5 | 8.45
2017-10-28 15:00 | 8.69 | 8.64
2017-10-28 15:30 | 9.65 | 9.6
2017-10-28 16:00 | 10.09 | 10.04
2017-10-28 16:30 | 10.28 | 10.24
2017-10-28 17:00 | 10.1 | 10.07
2017-10-28 17:30 | 10.14 | 10.12
2017-10-28 18:00 | 10.29 | 10.27
2017-10-28 18:30 | 10.72 | 10.69
2017-10-28 19:00 | 11.1 | 11.07
2017-10-28 19:30 | 10.71 | 10.68
2017-10-28 20:00 | 10.62 | 10.6
2017-10-28 20:30 | 10.39 | 10.36
2017-10-28 21:00 | 9.66 | 9.63
2017-10-28 21:30 | 9.23 | 9.21
2017-10-28 22:00 | 8.72 | 8.71
2017-10-28 22:30 | 8.46 | 8.44
2017-10-28 23:00 | 8.33 | 8.32
2017-10-28 23:30 | 7.37 | 7.36
2017-10-29 | 6.45 | 6.44
2017-10-29 00:30 | 5.9 | 5.88
2017-10-29 01:00 | 5.62 | 5.61
2017-10-29 01:30 | 5.31 | 5.3
2017-10-29 02:00 | 5.04 | 5.02
2017-10-29 02:30 | 4.79 | 4.78
2017-10-29 03:00 | 4.67 | 4.65
2017-10-29 03:30 | 4.66 | 4.65
2017-10-29 04:00 | 4.62 | 4.6
2017-10-29 04:30 | 4.65 | 4.63
2017-10-29 05:00 | 4.6 | 4.58
2017-10-29 05:30 | 4.47 | 4.42
2017-10-29 06:00 | 4.52 | 4.47
2017-10-29 06:30 | 4.66 | 4.61
2017-10-29 07:00 | 4.26 | 4.23
2017-10-29 07:30 | 4.35 | 4.33
2017-10-29 08:00 | 4.6 | 4.58
2017-10-29 08:30 | 4.98 | 4.95
2017-10-29 09:00 | 5.17 | 5.12
2017-10-29 09:30 | 5.45 | 5.4
2017-10-29 10:00 | 5.89 | 5.84
2017-10-29 10:30 | 6.26 | 6.2
2017-10-29 11:00 | 6.8 | 6.73
2017-10-29 11:30 | 7.56 | 7.47
2017-10-29 12:00 | 8.3 | 8.18
2017-10-29 12:30 | 9.2 | 9.08
2017-10-29 13:00 | 9.96 | 9.82
2017-10-29 13:30 | 10.9 | 10.74
2017-10-29 14:00 | 11.67 | 11.49
2017-10-29 14:30 | 12.77 | 12.59
2017-10-29 15:00 | 13.56 | 13.37
2017-10-29 15:30 | 14.23 | 14.04
2017-10-29 16:00 | 15.02 | 14.85
2017-10-29 16:30 | 16.03 | 15.85
2017-10-29 17:00 | 16.04 | 15.88
2017-10-29 17:30 | 15.66 | 15.52
2017-10-29 18:00 | 15.72 | 15.58
2017-10-29 18:30 | 15.85 | 15.69
2017-10-29 19:00 | 15.69 | 15.55
2017-10-29 19:30 | 14.01 | 13.91
2017-10-29 20:00 | 13.05 | 12.99
2017-10-29 20:30 | 12.53 | 12.48
2017-10-29 21:00 | 11.37 | 11.34
2017-10-29 21:30 | 10.27 | 10.25
2017-10-29 22:00 | 9.56 | 9.55
2017-10-29 22:30 | 8.86 | 8.84
2017-10-29 23:00 | 8.5 | 8.48
2017-10-29 23:30 | 7.34 | 7.32
2017-10-30 | 6.38 | 6.37
2017-10-30 00:30 | 5.74 | 5.73
2017-10-30 01:00 | 5.41 | 5.39
2017-10-30 01:30 | 5.15 | 5.14
2017-10-30 02:00 | 5.02 | 5
2017-10-30 02:30 | 4.84 | 4.82
2017-10-30 03:00 | 4.64 | 4.63
2017-10-30 03:30 | 4.68 | 4.66
2017-10-30 04:00 | 4.77 | 4.75
2017-10-30 04:30 | 4.89 | 4.87
2017-10-30 05:00 | 4.94 | 4.92
2017-10-30 05:30 | 5.19 | 5.16
2017-10-30 06:00 | 5.47 | 5.44
2017-10-30 06:30 | 5.88 | 5.86
2017-10-30 07:00 | 6.11 | 6.1
2017-10-30 07:30 | 6.36 | 6.35
2017-10-30 08:00 | 6.26 | 6.24
2017-10-30 08:30 | 5.99 | 5.96
2017-10-30 09:00 | 6.44 | 6.41
2017-10-30 09:30 | 6.23 | 6.18
2017-10-30 10:00 | 7.65 | 7.61
2017-10-30 10:30 | 5.94 | 5.86
2017-10-30 11:00 | 6.48 | 6.38
2017-10-30 11:30 | 7.95 | 7.86
2017-10-30 12:00 | 7.24 | 7.11
2017-10-30 12:30 | 8.01 | 7.89
2017-10-30 13:00 | 8.91 | 8.78
2017-10-30 13:30 | 9.78 | 9.63
2017-10-30 14:00 | 10.4 | 10.2
2017-10-30 14:30 | 11.62 | 11.37
2017-10-30 15:00 | 13.08 | 12.9
2017-10-30 15:30 | 13.71 | 13.55
2017-10-30 16:00 | 12.99 | 12.8
2017-10-30 16:30 | 14.33 | 14.14
2017-10-30 17:00 | 15.11 | 14.96
2017-10-30 17:30 | 15.55 | 15.41
2017-10-30 18:00 | 15.62 | 15.49
2017-10-30 18:30 | 16.06 | 15.92
2017-10-30 19:00 | 16.74 | 16.59
2017-10-30 19:30 | 16.08 | 15.95
2017-10-30 20:00 | 15.38 | 15.26
2017-10-30 20:30 | 14.78 | 14.68
2017-10-30 21:00 | 13.67 | 13.59
2017-10-30 21:30 | 12.15 | 12.1
2017-10-30 22:00 | 10.83 | 10.8
2017-10-30 22:30 | 9.79 | 9.77
2017-10-30 23:00 | 9.14 | 9.12
2017-10-30 23:30 | 7.91 | 7.89
2017-10-31 | 6.97 | 6.95
2017-10-31 00:30 | 6.35 | 6.33
2017-10-31 01:00 | 6.01 | 5.99
2017-10-31 01:30 | 5.69 | 5.68
2017-10-31 02:00 | 5.34 | 5.32
2017-10-31 02:30 | 5.13 | 5.11
2017-10-31 03:00 | 5.07 | 5.05
2017-10-31 03:30 | 4.87 | 4.85
2017-10-31 04:00 | 4.98 | 4.96
2017-10-31 04:30 | 5.01 | 5
2017-10-31 05:00 | 5.03 | 5.01
2017-10-31 05:30 | 5.19 | 5.16
2017-10-31 06:00 | 5.34 | 5.3
2017-10-31 06:30 | 5.58 | 5.55
2017-10-31 07:00 | 5.66 | 5.65
2017-10-31 07:30 | 6.25 | 6.25
2017-10-31 08:00 | 5.69 | 5.68
2017-10-31 08:30 | 5.81 | 5.79
2017-10-31 09:00 | 4.19 | 4.16
2017-10-31 09:30 | 4.07 | 4.03
2017-10-31 10:00 | 4.51 | 4.48
2017-10-31 10:30 | 3.88 | 3.85
2017-10-31 11:00 | 4.02 | 3.99
2017-10-31 11:30 | 4.06 | 4.01
2017-10-31 12:00 | 4.58 | 4.53
2017-10-31 12:30 | 5.36 | 5.33
2017-10-31 13:00 | 5.18 | 5.12
2017-10-31 13:30 | 5.36 | 5.3
2017-10-31 14:00 | 6.02 | 5.95
2017-10-31 14:30 | 6.69 | 6.62
2017-10-31 15:00 | 7.18 | 7.11
2017-10-31 15:30 | 8.16 | 8.09
2017-10-31 16:00 | 9.43 | 9.36
2017-10-31 16:30 | 10.5 | 10.44
2017-10-31 17:00 | 11.26 | 11.21
2017-10-31 17:30 | 11.58 | 11.53
2017-10-31 18:00 | 11.56 | 11.52
2017-10-31 18:30 | 11.96 | 11.91
2017-10-31 19:00 | 12.59 | 12.53
2017-10-31 19:30 | 12.22 | 12.17
2017-10-31 20:00 | 11.97 | 11.94
2017-10-31 20:30 | 11.82 | 11.8
2017-10-31 21:00 | 11 | 10.98
2017-10-31 21:30 | 10.29 | 10.28
2017-10-31 22:00 | 9.18 | 9.17
2017-10-31 22:30 | 8.18 | 8.17
2017-10-31 23:00 | 7.72 | 7.71
2017-10-31 23:30 | 6.63 | 6.62
2017-11-01 | 5.7 | 5.68
2017-11-01 00:30 | 5.1 | 5.09
2017-11-01 01:00 | 4.92 | 4.9
2017-11-01 01:30 | 4.68 | 4.67
2017-11-01 02:00 | 4.37 | 4.35
2017-11-01 02:30 | 4.34 | 4.31
2017-11-01 03:00 | 4.17 | 4.15
2017-11-01 03:30 | 4.22 | 4.2
2017-11-01 04:00 | 4.28 | 4.25
2017-11-01 04:30 | 4.42 | 4.39
2017-11-01 05:00 | 4.56 | 4.52
2017-11-01 05:30 | 4.86 | 4.8
2017-11-01 06:00 | 5.05 | 4.99
2017-11-01 06:30 | 5.32 | 5.29
2017-11-01 07:00 | 5.66 | 5.64
2017-11-01 07:30 | 5.99 | 5.98
2017-11-01 08:00 | 5.26 | 5.25
2017-11-01 08:30 | 4.14 | 4.13
2017-11-01 09:00 | 3.75 | 3.74
2017-11-01 09:30 | 4.12 | 4.1
2017-11-01 10:00 | 3.66 | 3.64
2017-11-01 10:30 | 3.61 | 3.59
2017-11-01 11:00 | 3.3 | 3.27
2017-11-01 11:30 | 3.9 | 3.86
2017-11-01 12:00 | 4.91 | 4.89
2017-11-01 12:30 | 4.96 | 4.94
2017-11-01 13:00 | 4.71 | 4.69
2017-11-01 13:30 | 4.49 | 4.46
2017-11-01 14:00 | 4.41 | 4.38
2017-11-01 14:30 | 4.82 | 4.79
2017-11-01 15:00 | 5.56 | 5.54
2017-11-01 15:30 | 6.35 | 6.33
2017-11-01 16:00 | 7.48 | 7.46
2017-11-01 16:30 | 8.46 | 8.45
2017-11-01 17:00 | 9.51 | 9.49
2017-11-01 17:30 | 10.1 | 10.09
2017-11-01 18:00 | 10.53 | 10.52
2017-11-01 18:30 | 11.37 | 11.35
2017-11-01 19:00 | 12.36 | 12.32
2017-11-01 19:30 | 12.29 | 12.25
2017-11-01 20:00 | 11.98 | 11.95
2017-11-01 20:30 | 11.68 | 11.66
2017-11-01 21:00 | 11.09 | 11.08
2017-11-01 21:30 | 10.15 | 10.14
2017-11-01 22:00 | 9.28 | 9.27
2017-11-01 22:30 | 8.21 | 8.2
2017-11-01 23:00 | 7.66 | 7.65
2017-11-01 23:30 | 6.61 | 6.6
2017-11-02 | 5.81 | 5.8
2017-11-02 00:30 | 5.16 | 5.15
2017-11-02 01:00 | 4.97 | 4.96
2017-11-02 01:30 | 4.57 | 4.55
2017-11-02 02:00 | 4.45 | 4.43
2017-11-02 02:30 | 4.3 | 4.27
2017-11-02 03:00 | 4.17 | 4.15
2017-11-02 03:30 | 4.26 | 4.23
2017-11-02 04:00 | 4.26 | 4.23
2017-11-02 04:30 | 4.45 | 4.42
2017-11-02 05:00 | 4.45 | 4.41
2017-11-02 05:30 | 4.89 | 4.83
2017-11-02 06:00 | 5.44 | 5.4
2017-11-02 06:30 | 5.64 | 5.6
2017-11-02 07:00 | 5.52 | 5.49
2017-11-02 07:30 | 5.37 | 5.36
2017-11-02 08:00 | 4.85 | 4.84
2017-11-02 08:30 | 4.19 | 4.17
2017-11-02 09:00 | 3.67 | 3.65
2017-11-02 09:30 | 3.59 | 3.56
2017-11-02 10:00 | 3.46 | 3.43
2017-11-02 10:30 | 3.37 | 3.34
2017-11-02 11:00 | 3.54 | 3.5
2017-11-02 11:30 | 3.6 | 3.57
2017-11-02 12:00 | 3.8 | 3.76
2017-11-02 12:30 | 4.1 | 4.06
2017-11-02 13:00 | 4.31 | 4.28
2017-11-02 13:30 | 4.74 | 4.7
2017-11-02 14:00 | 5.48 | 5.42
2017-11-02 14:30 | 6.06 | 5.99
2017-11-02 15:00 | 7 | 6.93
2017-11-02 15:30 | 7.77 | 7.72
2017-11-02 16:00 | 8.45 | 8.4
2017-11-02 16:30 | 9.39 | 9.35
2017-11-02 17:00 | 10.16 | 10.13
2017-11-02 17:30 | 10.68 | 10.66
2017-11-02 18:00 | 10.84 | 10.82
2017-11-02 18:30 | 11.25 | 11.23
2017-11-02 19:00 | 12.23 | 12.18
2017-11-02 19:30 | 12.05 | 12
2017-11-02 20:00 | 11.84 | 11.81
2017-11-02 20:30 | 11.72 | 11.69
2017-11-02 21:00 | 11.03 | 11.01
2017-11-02 21:30 | 10.03 | 10.02
2017-11-02 22:00 | 8.94 | 8.93
2017-11-02 22:30 | 8.14 | 8.13
2017-11-02 23:00 | 7.88 | 7.87
2017-11-02 23:30 | 6.91 | 6.9
2017-11-03 | 6.03 | 6.02
2017-11-03 00:30 | 5.34 | 5.32
2017-11-03 01:00 | 5.09 | 5.08
2017-11-03 01:30 | 4.77 | 4.76
2017-11-03 02:00 | 4.5 | 4.48
2017-11-03 02:30 | 4.39 | 4.38
2017-11-03 03:00 | 4.36 | 4.34
2017-11-03 03:30 | 4.34 | 4.32
2017-11-03 04:00 | 4.31 | 4.29
2017-11-03 04:30 | 4.55 | 4.53
2017-11-03 05:00 | 4.56 | 4.52
2017-11-03 05:30 | 4.91 | 4.86
2017-11-03 06:00 | 4.98 | 4.92
2017-11-03 06:30 | 5.11 | 5.07
2017-11-03 07:00 | 5.05 | 5.03
2017-11-03 07:30 | 5.09 | 5.07
2017-11-03 08:00 | 4.65 | 4.62
2017-11-03 08:30 | 4.39 | 4.35
2017-11-03 09:00 | 4.27 | 4.23
2017-11-03 09:30 | 4.22 | 4.18
2017-11-03 10:00 | 4.24 | 4.2
2017-11-03 10:30 | 3.99 | 3.95
2017-11-03 11:00 | 4.55 | 4.5
2017-11-03 11:30 | 4.68 | 4.63
2017-11-03 12:00 | 5.41 | 5.35
2017-11-03 12:30 | 5.16 | 5.1
2017-11-03 13:00 | 5.71 | 5.65
2017-11-03 13:30 | 6.23 | 6.16
2017-11-03 14:00 | 6.95 | 6.88
2017-11-03 14:30 | 7.71 | 7.64
2017-11-03 15:00 | 8.46 | 8.39
2017-11-03 15:30 | 8.58 | 8.53
2017-11-03 16:00 | 8.7 | 8.65
2017-11-03 16:30 | 9.43 | 9.38
2017-11-03 17:00 | 9.85 | 9.81
2017-11-03 17:30 | 10.24 | 10.21
2017-11-03 18:00 | 10.25 | 10.22
2017-11-03 18:30 | 10.57 | 10.54
2017-11-03 19:00 | 11.41 | 11.36
2017-11-03 19:30 | 11.25 | 11.22
2017-11-03 20:00 | 11.06 | 11.03
2017-11-03 20:30 | 10.89 | 10.86
2017-11-03 21:00 | 10.34 | 10.32
2017-11-03 21:30 | 9.65 | 9.63
2017-11-03 22:00 | 8.95 | 8.93
2017-11-03 22:30 | 8.51 | 8.49
2017-11-03 23:00 | 8.24 | 8.23
2017-11-03 23:30 | 7.31 | 7.3
2017-11-04 | 6.43 | 6.42
2017-11-04 00:30 | 5.87 | 5.86
2017-11-04 01:00 | 5.64 | 5.63
2017-11-04 01:30 | 5.26 | 5.24
2017-11-04 02:00 | 4.97 | 4.96
2017-11-04 02:30 | 4.84 | 4.83
2017-11-04 03:00 | 4.71 | 4.69
2017-11-04 03:30 | 4.62 | 4.61
2017-11-04 04:00 | 4.52 | 4.51
2017-11-04 04:30 | 4.52 | 4.5
2017-11-04 05:00 | 4.49 | 4.45
2017-11-04 05:30 | 4.47 | 4.4
2017-11-04 06:00 | 4.33 | 4.25
2017-11-04 06:30 | 4.23 | 4.17
2017-11-04 07:00 | 4.16 | 4.11
2017-11-04 07:30 | 4.28 | 4.25
2017-11-04 08:00 | 4.32 | 4.29
2017-11-04 08:30 | 4.48 | 4.45
2017-11-04 09:00 | 4.53 | 4.49
2017-11-04 09:30 | 4.56 | 4.52
2017-11-04 10:00 | 4.67 | 4.62
2017-11-04 10:30 | 4.7 | 4.64
2017-11-04 11:00 | 4.91 | 4.84
2017-11-04 11:30 | 5.33 | 5.27
2017-11-04 12:00 | 5.94 | 5.88
2017-11-04 12:30 | 6.51 | 6.44
2017-11-04 13:00 | 7.42 | 7.34
2017-11-04 13:30 | 8.28 | 8.19
2017-11-04 14:00 | 9.72 | 9.62
2017-11-04 14:30 | 9.55 | 9.45
2017-11-04 15:00 | 10.51 | 10.42
2017-11-04 15:30 | 10.55 | 10.46
2017-11-04 16:00 | 10.58 | 10.5
2017-11-04 16:30 | 10.95 | 10.87
2017-11-04 17:00 | 11.36 | 11.3
2017-11-04 17:30 | 11.37 | 11.31
2017-11-04 18:00 | 11.18 | 11.13
2017-11-04 18:30 | 11.11 | 11.07
2017-11-04 19:00 | 11.73 | 11.68
2017-11-04 19:30 | 11.44 | 11.4
2017-11-04 20:00 | 11.16 | 11.12
2017-11-04 20:30 | 10.77 | 10.74
2017-11-04 21:00 | 10.05 | 10.03
2017-11-04 21:30 | 9.37 | 9.35
2017-11-04 22:00 | 8.74 | 8.72
2017-11-04 22:30 | 8.67 | 8.66
2017-11-04 23:00 | 8.48 | 8.46
2017-11-04 23:30 | 7.43 | 7.41
2017-11-05 | 6.59 | 6.58
2017-11-05 00:30 | 5.97 | 5.96
2017-11-05 01:00 | 5.63 | 5.62
2017-11-05 01:30 | 5.46 | 5.44
2017-11-05 02:00 | 5.11 | 5.09
2017-11-05 02:30 | 4.99 | 4.97
2017-11-05 03:00 | 4.93 | 4.91
2017-11-05 03:30 | 4.87 | 4.85
2017-11-05 04:00 | 4.83 | 4.81
2017-11-05 04:30 | 4.81 | 4.79
2017-11-05 05:00 | 4.72 | 4.7
2017-11-05 05:30 | 4.53 | 4.48
2017-11-05 06:00 | 4.52 | 4.48
2017-11-05 06:30 | 4.38 | 4.33
2017-11-05 07:00 | 4.29 | 4.25
2017-11-05 07:30 | 4.41 | 4.38
2017-11-05 08:00 | 4.76 | 4.73
2017-11-05 08:30 | 5.61 | 5.59
2017-11-05 09:00 | 6.84 | 6.82
2017-11-05 09:30 | 6.69 | 6.66
2017-11-05 10:00 | 6.32 | 6.28
2017-11-05 10:30 | 5.38 | 5.32
2017-11-05 11:00 | 6.31 | 6.26
2017-11-05 11:30 | 6.81 | 6.75
2017-11-05 12:00 | 6.85 | 6.79
2017-11-05 12:30 | 7.24 | 7.18
2017-11-05 13:00 | 7.91 | 7.83
2017-11-05 13:30 | 8.38 | 8.3
2017-11-05 14:00 | 9.37 | 9.28
2017-11-05 14:30 | 10.29 | 10.19
2017-11-05 15:00 | 10.15 | 10.05
2017-11-05 15:30 | 10.81 | 10.7
2017-11-05 16:00 | 11.49 | 11.39
2017-11-05 16:30 | 12.03 | 11.95
2017-11-05 17:00 | 12.49 | 12.42
2017-11-05 17:30 | 12.89 | 12.82
2017-11-05 18:00 | 12.81 | 12.75
2017-11-05 18:30 | 13.04 | 12.97
2017-11-05 19:00 | 13.19 | 13.12
2017-11-05 19:30 | 12.57 | 12.52
2017-11-05 20:00 | 12.17 | 12.13
2017-11-05 20:30 | 11.41 | 11.39
2017-11-05 21:00 | 10.7 | 10.68
2017-11-05 21:30 | 9.71 | 9.7
2017-11-05 22:00 | 9.01 | 9
2017-11-05 22:30 | 8.36 | 8.35
2017-11-05 23:00 | 7.99 | 7.98
2017-11-05 23:30 | 6.97 | 6.97
2017-11-06 | 6.08 | 6.08
2017-11-06 00:30 | 5.46 | 5.45
2017-11-06 01:00 | 5.39 | 5.38
2017-11-06 01:30 | 4.95 | 4.94
2017-11-06 02:00 | 4.72 | 4.71
2017-11-06 02:30 | 4.64 | 4.63
2017-11-06 03:00 | 4.51 | 4.49
2017-11-06 03:30 | 4.57 | 4.55
2017-11-06 04:00 | 4.55 | 4.54
2017-11-06 04:30 | 4.74 | 4.73
2017-11-06 05:00 | 4.92 | 4.9
2017-11-06 05:30 | 5.09 | 5.06
2017-11-06 06:00 | 5.35 | 5.31
2017-11-06 06:30 | 5.92 | 5.9
2017-11-06 07:00 | 6.48 | 6.47
2017-11-06 07:30 | 6.63 | 6.63
2017-11-06 08:00 | 6.35 | 6.34
2017-11-06 08:30 | 6.16 | 6.15
2017-11-06 09:00 | 6.07 | 6.06
2017-11-06 09:30 | 6.71 | 6.7
2017-11-06 10:00 | 5.34 | 5.34
2017-11-06 10:30 | 4.94 | 4.93
2017-11-06 11:00 | 5.18 | 5.16
2017-11-06 11:30 | 6.19 | 6.17
2017-11-06 12:00 | 6.17 | 6.15
2017-11-06 12:30 | 6.49 | 6.46
2017-11-06 13:00 | 7.33 | 7.3
2017-11-06 13:30 | 6.37 | 6.32
2017-11-06 14:00 | 6.09 | 6.02
2017-11-06 14:30 | 7 | 6.94
2017-11-06 15:00 | 7.91 | 7.85
2017-11-06 15:30 | 8.55 | 8.49
2017-11-06 16:00 | 9.62 | 9.56
2017-11-06 16:30 | 10.44 | 10.38
2017-11-06 17:00 | 11.5 | 11.45
2017-11-06 17:30 | 12.05 | 12
2017-11-06 18:00 | 12.54 | 12.49
2017-11-06 18:30 | 13.08 | 13.03
2017-11-06 19:00 | 13.94 | 13.87
2017-11-06 19:30 | 13.51 | 13.44
2017-11-06 20:00 | 13.11 | 13.06
2017-11-06 20:30 | 12.74 | 12.7
2017-11-06 21:00 | 11.9 | 11.87
2017-11-06 21:30 | 10.85 | 10.83
2017-11-06 22:00 | 9.79 | 9.78
2017-11-06 22:30 | 8.32 | 8.31
2017-11-06 23:00 | 7.88 | 7.87
2017-11-06 23:30 | 6.75 | 6.73
2017-11-07 | 5.87 | 5.86
2017-11-07 00:30 | 5.34 | 5.33
2017-11-07 01:00 | 5.16 | 5.14
2017-11-07 01:30 | 4.9 | 4.88
2017-11-07 02:00 | 4.69 | 4.68
2017-11-07 02:30 | 4.55 | 4.53
2017-11-07 03:00 | 4.5 | 4.48
2017-11-07 03:30 | 4.49 | 4.47
2017-11-07 04:00 | 4.52 | 4.5
2017-11-07 04:30 | 4.62 | 4.6
2017-11-07 05:00 | 4.77 | 4.75
2017-11-07 05:30 | 5.11 | 5.08
2017-11-07 06:00 | 5.56 | 5.53
2017-11-07 06:30 | 5.76 | 5.75
2017-11-07 07:00 | 5.71 | 5.7
2017-11-07 07:30 | 5.74 | 5.72
2017-11-07 08:00 | 5.26 | 5.24
2017-11-07 08:30 | 4.93 | 4.91
2017-11-07 09:00 | 4.56 | 4.53
2017-11-07 09:30 | 4.73 | 4.7
2017-11-07 10:00 | 5.11 | 5.07
2017-11-07 10:30 | 6.18 | 6.14
2017-11-07 11:00 | 6.95 | 6.9
2017-11-07 11:30 | 6.37 | 6.3
2017-11-07 12:00 | 6.19 | 6.12
2017-11-07 12:30 | 7.56 | 7.52
2017-11-07 13:00 | 7.07 | 7.02
2017-11-07 13:30 | 5.97 | 5.91
2017-11-07 14:00 | 8.22 | 8.19
2017-11-07 14:30 | 7.07 | 7.03
2017-11-07 15:00 | 8.29 | 8.28
2017-11-07 15:30 | 5.94 | 5.92
2017-11-07 16:00 | 7.25 | 7.24
2017-11-07 16:30 | 8.3 | 8.29
2017-11-07 17:00 | 9.39 | 9.39
2017-11-07 17:30 | 9.5 | 9.5
2017-11-07 18:00 | 10.2 | 10.19
2017-11-07 18:30 | 10.95 | 10.94
2017-11-07 19:00 | 11.8 | 11.78
2017-11-07 19:30 | 11.54 | 11.52
2017-11-07 20:00 | 11.43 | 11.41
2017-11-07 20:30 | 11.1 | 11.09
2017-11-07 21:00 | 10.33 | 10.32
2017-11-07 21:30 | 9.45 | 9.44
2017-11-07 22:00 | 8.67 | 8.66
2017-11-07 22:30 | 8.04 | 8.03
2017-11-07 23:00 | 7.35 | 7.34
2017-11-07 23:30 | 6.31 | 6.3
2017-11-08 | 5.55 | 5.54
2017-11-08 00:30 | 5.08 | 5.07
2017-11-08 01:00 | 4.82 | 4.81
2017-11-08 01:30 | 4.45 | 4.43
2017-11-08 02:00 | 4.28 | 4.26
2017-11-08 02:30 | 4.25 | 4.23
2017-11-08 03:00 | 4.08 | 4.05
2017-11-08 03:30 | 4.19 | 4.17
2017-11-08 04:00 | 4.17 | 4.14
2017-11-08 04:30 | 4.38 | 4.35
2017-11-08 05:00 | 4.56 | 4.52
2017-11-08 05:30 | 5.18 | 5.13
2017-11-08 06:00 | 5.63 | 5.6
2017-11-08 06:30 | 5.89 | 5.87
2017-11-08 07:00 | 6.29 | 6.27
2017-11-08 07:30 | 6.09 | 6.08
2017-11-08 08:00 | 5.3 | 5.3
2017-11-08 08:30 | 4.66 | 4.66
2017-11-08 09:00 | 3.72 | 3.7
2017-11-08 09:30 | 4.14 | 4.13
2017-11-08 10:00 | 4.44 | 4.42
2017-11-08 10:30 | 5.22 | 5.21
2017-11-08 11:00 | 4.05 | 4.04
2017-11-08 11:30 | 5.24 | 5.22
2017-11-08 12:00 | 5.76 | 5.75
2017-11-08 12:30 | 5.93 | 5.92
2017-11-08 13:00 | 7.11 | 7.1
2017-11-08 13:30 | 6.57 | 6.57
2017-11-08 14:00 | 6.47 | 6.46
2017-11-08 14:30 | 6.33 | 6.33
2017-11-08 15:00 | 7.58 | 7.58
2017-11-08 15:30 | 7.22 | 7.21
2017-11-08 16:00 | 7.81 | 7.81
2017-11-08 16:30 | 7.95 | 7.95
2017-11-08 17:00 | 8.37 | 8.37
2017-11-08 17:30 | 9.11 | 9.11
2017-11-08 18:00 | 9.51 | 9.5
2017-11-08 18:30 | 10.19 | 10.18
2017-11-08 19:00 | 11.37 | 11.36
2017-11-08 19:30 | 11.06 | 11.06
2017-11-08 20:00 | 10.93 | 10.92
2017-11-08 20:30 | 10.81 | 10.8
2017-11-08 21:00 | 10.12 | 10.11
2017-11-08 21:30 | 9.37 | 9.36
2017-11-08 22:00 | 8.56 | 8.56
2017-11-08 22:30 | 7.68 | 7.67
2017-11-08 23:00 | 7.08 | 7.07
2017-11-08 23:30 | 6.2 | 6.19
2017-11-09 | 5.35 | 5.34
2017-11-09 00:30 | 4.75 | 4.72
2017-11-09 01:00 | 4.55 | 4.52
2017-11-09 01:30 | 4.29 | 4.26
2017-11-09 02:00 | 4.11 | 4.08
2017-11-09 02:30 | 3.97 | 3.92
2017-11-09 03:00 | 3.87 | 3.82
2017-11-09 03:30 | 3.92 | 3.87
2017-11-09 04:00 | 3.99 | 3.95
2017-11-09 04:30 | 4.12 | 4.08
2017-11-09 05:00 | 4.24 | 4.17
2017-11-09 05:30 | 4.62 | 4.54
2017-11-09 06:00 | 5.26 | 5.2
2017-11-09 06:30 | 5.42 | 5.39
2017-11-09 07:00 | 5.39 | 5.36
2017-11-09 07:30 | 5.35 | 5.33
2017-11-09 08:00 | 4.74 | 4.74
2017-11-09 08:30 | 4.12 | 4.11
2017-11-09 09:00 | 3.35 | 3.33
2017-11-09 09:30 | 2.96 | 2.95
2017-11-09 10:00 | 3.78 | 3.76
2017-11-09 10:30 | 3.9 | 3.89
2017-11-09 11:00 | 3.93 | 3.92
2017-11-09 11:30 | 3.7 | 3.68
2017-11-09 12:00 | 4.38 | 4.37
2017-11-09 12:30 | 4.29 | 4.28
2017-11-09 13:00 | 3.37 | 3.36
2017-11-09 13:30 | 4.26 | 4.25
2017-11-09 14:00 | 5.24 | 5.24
2017-11-09 14:30 | 6.17 | 6.17
2017-11-09 15:00 | 4.08 | 4.08
2017-11-09 15:30 | 6.04 | 6.03
2017-11-09 16:00 | 6.8 | 6.8
2017-11-09 16:30 | 7.42 | 7.42
2017-11-09 17:00 | 7.93 | 7.93
2017-11-09 17:30 | 8.42 | 8.41
2017-11-09 18:00 | 9 | 8.99
2017-11-09 18:30 | 9.82 | 9.82
2017-11-09 19:00 | 10.84 | 10.82
2017-11-09 19:30 | 10.93 | 10.91
2017-11-09 20:00 | 10.8 | 10.79
2017-11-09 20:30 | 10.72 | 10.71
2017-11-09 21:00 | 10.11 | 10.11
2017-11-09 21:30 | 9.01 | 9
2017-11-09 22:00 | 7.98 | 7.97
2017-11-09 22:30 | 7.46 | 7.45
2017-11-09 23:00 | 7.19 | 7.18
2017-11-09 23:30 | 6.25 | 6.24
2017-11-10 | 5.4 | 5.39
2017-11-10 00:30 | 4.83 | 4.81
2017-11-10 01:00 | 4.58 | 4.55
2017-11-10 01:30 | 4.28 | 4.26
2017-11-10 02:00 | 4.1 | 4.07
2017-11-10 02:30 | 3.9 | 3.87
2017-11-10 03:00 | 3.91 | 3.87
2017-11-10 03:30 | 3.84 | 3.81
2017-11-10 04:00 | 4.01 | 3.98
2017-11-10 04:30 | 4.09 | 4.06
2017-11-10 05:00 | 4.23 | 4.17
2017-11-10 05:30 | 4.54 | 4.47
2017-11-10 06:00 | 4.85 | 4.78
2017-11-10 06:30 | 4.85 | 4.79
2017-11-10 07:00 | 4.63 | 4.58
2017-11-10 07:30 | 4.79 | 4.76
2017-11-10 08:00 | 4.39 | 4.37
2017-11-10 08:30 | 4.33 | 4.32
2017-11-10 09:00 | 4.09 | 4.08
2017-11-10 09:30 | 3.86 | 3.84
2017-11-10 10:00 | 5.05 | 5.04
2017-11-10 10:30 | 5.69 | 5.68
2017-11-10 11:00 | 4.02 | 4.01
2017-11-10 11:30 | 2.09 | 2.05
2017-11-10 12:00 | 3.94 | 3.92
2017-11-10 12:30 | 3.63 | 3.62
2017-11-10 13:00 | 3.39 | 3.36
2017-11-10 13:30 | 4.71 | 4.69
2017-11-10 14:00 | 2.73 | 2.7
2017-11-10 14:30 | 3.41 | 3.39
2017-11-10 15:00 | 3.89 | 3.87
2017-11-10 15:30 | 5.88 | 5.87
2017-11-10 16:00 | 6.3 | 6.28
2017-11-10 16:30 | 6.52 | 6.51
2017-11-10 17:00 | 6.82 | 6.81
2017-11-10 17:30 | 7.66 | 7.65
2017-11-10 18:00 | 8.18 | 8.16
2017-11-10 18:30 | 8.98 | 8.97
2017-11-10 19:00 | 9.79 | 9.78
2017-11-10 19:30 | 9.76 | 9.75
2017-11-10 20:00 | 9.72 | 9.71
2017-11-10 20:30 | 9.58 | 9.57
2017-11-10 21:00 | 8.93 | 8.92
2017-11-10 21:30 | 8.24 | 8.23
2017-11-10 22:00 | 7.71 | 7.7
2017-11-10 22:30 | 7.34 | 7.34
2017-11-10 23:00 | 7.28 | 7.27
2017-11-10 23:30 | 6.45 | 6.44
2017-11-11 | 5.79 | 5.77
2017-11-11 00:30 | 5.13 | 5.11
2017-11-11 01:00 | 4.82 | 4.8
2017-11-11 01:30 | 4.59 | 4.56
2017-11-11 02:00 | 4.3 | 4.27
2017-11-11 02:30 | 4.13 | 4.1
2017-11-11 03:00 | 4.1 | 4.07
2017-11-11 03:30 | 3.95 | 3.91
2017-11-11 04:00 | 3.98 | 3.95
2017-11-11 04:30 | 3.99 | 3.95
2017-11-11 05:00 | 4.04 | 3.99
2017-11-11 05:30 | 4.08 | 3.98
2017-11-11 06:00 | 4.11 | 4
2017-11-11 06:30 | 4.3 | 4.2
2017-11-11 07:00 | 4.15 | 4.06
2017-11-11 07:30 | 4.84 | 4.78
2017-11-11 08:00 | 4.51 | 4.46
2017-11-11 08:30 | 5.05 | 5.02
2017-11-11 09:00 | 5.73 | 5.71
2017-11-11 09:30 | 4.32 | 4.3
2017-11-11 10:00 | 4.93 | 4.9
2017-11-11 10:30 | 6.3 | 6.28
2017-11-11 11:00 | 4.19 | 4.15
2017-11-11 11:30 | 3.87 | 3.83
2017-11-11 12:00 | 4.97 | 4.94
2017-11-11 12:30 | 4.63 | 4.6
2017-11-11 13:00 | 6.06 | 6.04
2017-11-11 13:30 | 4.96 | 4.92
2017-11-11 14:00 | 4.72 | 4.69
2017-11-11 14:30 | 6.28 | 6.25
2017-11-11 15:00 | 6.38 | 6.36
2017-11-11 15:30 | 6.5 | 6.48
2017-11-11 16:00 | 5.78 | 5.76
2017-11-11 16:30 | 7.18 | 7.16
2017-11-11 17:00 | 8.45 | 8.43
2017-11-11 17:30 | 8.33 | 8.31
2017-11-11 18:00 | 8.56 | 8.55
2017-11-11 18:30 | 8.93 | 8.92
2017-11-11 19:00 | 9.47 | 9.45
2017-11-11 19:30 | 9.27 | 9.25
2017-11-11 20:00 | 9.31 | 9.3
2017-11-11 20:30 | 9.1 | 9.09
2017-11-11 21:00 | 8.68 | 8.67
2017-11-11 21:30 | 8.09 | 8.08
2017-11-11 22:00 | 7.71 | 7.7
2017-11-11 22:30 | 7.32 | 7.31
2017-11-11 23:00 | 7.2 | 7.19
2017-11-11 23:30 | 6.49 | 6.48
2017-11-12 | 5.71 | 5.69
2017-11-12 00:30 | 5.29 | 5.27
2017-11-12 01:00 | 4.93 | 4.91
2017-11-12 01:30 | 4.58 | 4.55
2017-11-12 02:00 | 4.29 | 4.26
2017-11-12 02:30 | 4.17 | 4.14
2017-11-12 03:00 | 3.97 | 3.94
2017-11-12 03:30 | 3.96 | 3.92
2017-11-12 04:00 | 3.9 | 3.85
2017-11-12 04:30 | 3.97 | 3.93
2017-11-12 05:00 | 3.79 | 3.69
2017-11-12 05:30 | 3.82 | 3.7
2017-11-12 06:00 | 3.59 | 3.45
2017-11-12 06:30 | 3.41 | 3.28
2017-11-12 07:00 | 3.68 | 3.57
2017-11-12 07:30 | 3.66 | 3.58
2017-11-12 08:00 | 3.79 | 3.74
2017-11-12 08:30 | 3.66 | 3.63
2017-11-12 09:00 | 3.72 | 3.69
2017-11-12 09:30 | 4.85 | 4.82
2017-11-12 10:00 | 4.51 | 4.48
2017-11-12 10:30 | 3.69 | 3.65
2017-11-12 11:00 | 3.86 | 3.82
2017-11-12 11:30 | 3.01 | 2.95
2017-11-12 12:00 | 3.72 | 3.67
2017-11-12 12:30 | 3.95 | 3.9
2017-11-12 13:00 | 4.34 | 4.3
2017-11-12 13:30 | 3.85 | 3.8
2017-11-12 14:00 | 4.12 | 4.08
2017-11-12 14:30 | 4.2 | 4.15
2017-11-12 15:00 | 5.25 | 5.22
2017-11-12 15:30 | 5.78 | 5.76
2017-11-12 16:00 | 6.73 | 6.71
2017-11-12 16:30 | 7.44 | 7.42
2017-11-12 17:00 | 7.84 | 7.82
2017-11-12 17:30 | 8.51 | 8.5
2017-11-12 18:00 | 9.08 | 9.07
2017-11-12 18:30 | 9.66 | 9.65
2017-11-12 19:00 | 10.45 | 10.44
2017-11-12 19:30 | 10.27 | 10.25
2017-11-12 20:00 | 10.11 | 10.1
2017-11-12 20:30 | 9.72 | 9.71
2017-11-12 21:00 | 9.11 | 9.1
2017-11-12 21:30 | 8.45 | 8.44
2017-11-12 22:00 | 7.82 | 7.81
2017-11-12 22:30 | 7.35 | 7.34
2017-11-12 23:00 | 7.11 | 7.1
2017-11-12 23:30 | 6.21 | 6.2
2017-11-13 | 5.39 | 5.37
2017-11-13 00:30 | 4.78 | 4.76
2017-11-13 01:00 | 4.47 | 4.44
2017-11-13 01:30 | 4.27 | 4.24
2017-11-13 02:00 | 4.03 | 3.99
2017-11-13 02:30 | 3.96 | 3.92
2017-11-13 03:00 | 3.85 | 3.81
2017-11-13 03:30 | 3.81 | 3.77
2017-11-13 04:00 | 3.95 | 3.9
2017-11-13 04:30 | 4.14 | 4.1
2017-11-13 05:00 | 4.24 | 4.16
2017-11-13 05:30 | 4.71 | 4.63
2017-11-13 06:00 | 5.17 | 5.12
2017-11-13 06:30 | 5.3 | 5.26
2017-11-13 07:00 | 5.45 | 5.42
2017-11-13 07:30 | 5.19 | 5.18
2017-11-13 08:00 | 4.63 | 4.63
2017-11-13 08:30 | 4.06 | 4.05
2017-11-13 09:00 | 4.42 | 4.41
2017-11-13 09:30 | 4.45 | 4.44
2017-11-13 10:00 | 4.27 | 4.26
2017-11-13 10:30 | 2.92 | 2.91
2017-11-13 11:00 | 4.47 | 4.46
2017-11-13 11:30 | 4.43 | 4.43
2017-11-13 12:00 | 3.83 | 3.82
2017-11-13 12:30 | 5.18 | 5.18
2017-11-13 13:00 | 4.52 | 4.5
2017-11-13 13:30 | 4.35 | 4.32
2017-11-13 14:00 | 5.49 | 5.48
2017-11-13 14:30 | 5.61 | 5.6
2017-11-13 15:00 | 4.78 | 4.76
2017-11-13 15:30 | 5.43 | 5.42
2017-11-13 16:00 | 6.41 | 6.4
2017-11-13 16:30 | 7.21 | 7.2
2017-11-13 17:00 | 8.2 | 8.19
2017-11-13 17:30 | 9.02 | 9.01
2017-11-13 18:00 | 9.57 | 9.57
2017-11-13 18:30 | 10.37 | 10.36
2017-11-13 19:00 | 11.52 | 11.51
2017-11-13 19:30 | 11.36 | 11.34
2017-11-13 20:00 | 11.12 | 11.12
2017-11-13 20:30 | 10.85 | 10.84
2017-11-13 21:00 | 10.18 | 10.17
2017-11-13 21:30 | 9.5 | 9.49
2017-11-13 22:00 | 8.53 | 8.52
2017-11-13 22:30 | 7.71 | 7.71
2017-11-13 23:00 | 7.14 | 7.13
2017-11-13 23:30 | 6.15 | 6.14
2017-11-14 | 5.33 | 5.31
2017-11-14 00:30 | 4.74 | 4.71
2017-11-14 01:00 | 4.55 | 4.53
2017-11-14 01:30 | 4.37 | 4.35
2017-11-14 02:00 | 4.04 | 4
2017-11-14 02:30 | 3.85 | 3.81
2017-11-14 03:00 | 3.81 | 3.77
2017-11-14 03:30 | 3.92 | 3.88
2017-11-14 04:00 | 3.93 | 3.89
2017-11-14 04:30 | 4.17 | 4.14
2017-11-14 05:00 | 4.26 | 4.19
2017-11-14 05:30 | 4.82 | 4.76
2017-11-14 06:00 | 5.29 | 5.24
2017-11-14 06:30 | 5.4 | 5.36
2017-11-14 07:00 | 5.33 | 5.3
2017-11-14 07:30 | 5.14 | 5.13
2017-11-14 08:00 | 4.63 | 4.62
2017-11-14 08:30 | 3.82 | 3.8
2017-11-14 09:00 | 3.45 | 3.44
2017-11-14 09:30 | 3.24 | 3.23
2017-11-14 10:00 | 3.63 | 3.6
2017-11-14 10:30 | 3.41 | 3.38
2017-11-14 11:00 | 3.67 | 3.64
2017-11-14 11:30 | 3.69 | 3.67
2017-11-14 12:00 | 4.1 | 4.08
2017-11-14 12:30 | 4.18 | 4.16
2017-11-14 13:00 | 4.14 | 4.12
2017-11-14 13:30 | 4.34 | 4.33
2017-11-14 14:00 | 4.53 | 4.51
2017-11-14 14:30 | 5.81 | 5.8
2017-11-14 15:00 | 5.43 | 5.41
2017-11-14 15:30 | 5.77 | 5.75
2017-11-14 16:00 | 6.61 | 6.6
2017-11-14 16:30 | 7.17 | 7.14
2017-11-14 17:00 | 8.29 | 8.28
2017-11-14 17:30 | 9.05 | 9.04
2017-11-14 18:00 | 9.71 | 9.71
2017-11-14 18:30 | 10.22 | 10.21
2017-11-14 19:00 | 11.45 | 11.42
2017-11-14 19:30 | 11.41 | 11.39
2017-11-14 20:00 | 10.87 | 10.86
2017-11-14 20:30 | 10.79 | 10.78
2017-11-14 21:00 | 10.29 | 10.28
2017-11-14 21:30 | 9.4 | 9.4
2017-11-14 22:00 | 8.47 | 8.47
2017-11-14 22:30 | 7.65 | 7.64
2017-11-14 23:00 | 7.18 | 7.17
2017-11-14 23:30 | 6.21 | 6.2
2017-11-15 | 5.41 | 5.39
2017-11-15 00:30 | 4.77 | 4.74
2017-11-15 01:00 | 4.59 | 4.57
2017-11-15 01:30 | 4.31 | 4.29
2017-11-15 02:00 | 4.14 | 4.11
2017-11-15 02:30 | 3.97 | 3.93
2017-11-15 03:00 | 3.93 | 3.9
2017-11-15 03:30 | 3.98 | 3.94
2017-11-15 04:00 | 3.94 | 3.9
2017-11-15 04:30 | 4.16 | 4.11
2017-11-15 05:00 | 4.25 | 4.18
2017-11-15 05:30 | 4.59 | 4.51
2017-11-15 06:00 | 4.7 | 4.62
2017-11-15 06:30 | 4.96 | 4.9
2017-11-15 07:00 | 4.73 | 4.68
2017-11-15 07:30 | 4.49 | 4.46
2017-11-15 08:00 | 4.18 | 4.15
2017-11-15 08:30 | 3.79 | 3.77
2017-11-15 09:00 | 3.55 | 3.51
2017-11-15 09:30 | 4.05 | 4.02
2017-11-15 10:00 | 4.11 | 4.09
2017-11-15 10:30 | 4.09 | 4.07
2017-11-15 11:00 | 3.62 | 3.59
2017-11-15 11:30 | 4.17 | 4.15
2017-11-15 12:00 | 4.76 | 4.75
2017-11-15 12:30 | 5.66 | 5.65
2017-11-15 13:00 | 5.2 | 5.18
2017-11-15 13:30 | 4.66 | 4.63
2017-11-15 14:00 | 4.44 | 4.41
2017-11-15 14:30 | 6.26 | 6.24
2017-11-15 15:00 | 7.92 | 7.9
2017-11-15 15:30 | 5.84 | 5.82
2017-11-15 16:00 | 5.72 | 5.7
2017-11-15 16:30 | 6.86 | 6.85
2017-11-15 17:00 | 8 | 7.98
2017-11-15 17:30 | 9.01 | 9
2017-11-15 18:00 | 9.88 | 9.87
2017-11-15 18:30 | 10.38 | 10.38
2017-11-15 19:00 | 11.49 | 11.47
2017-11-15 19:30 | 11.13 | 11.12
2017-11-15 20:00 | 11.03 | 11.02
2017-11-15 20:30 | 11.28 | 11.26
2017-11-15 21:00 | 10.45 | 10.45
2017-11-15 21:30 | 9.63 | 9.62
2017-11-15 22:00 | 8.76 | 8.75
2017-11-15 22:30 | 7.89 | 7.88
2017-11-15 23:00 | 7.35 | 7.34
2017-11-15 23:30 | 6.41 | 6.4
2017-11-16 | 5.6 | 5.58
2017-11-16 00:30 | 5 | 4.98
2017-11-16 01:00 | 4.7 | 4.68
2017-11-16 01:30 | 4.42 | 4.39
2017-11-16 02:00 | 4.18 | 4.15
2017-11-16 02:30 | 4.01 | 3.98
2017-11-16 03:00 | 3.9 | 3.86
2017-11-16 03:30 | 4.04 | 4.01
2017-11-16 04:00 | 4.12 | 4.09
2017-11-16 04:30 | 4.27 | 4.24
2017-11-16 05:00 | 4.29 | 4.22
2017-11-16 05:30 | 4.8 | 4.74
2017-11-16 06:00 | 5.26 | 5.22
2017-11-16 06:30 | 5.6 | 5.58
2017-11-16 07:00 | 5.69 | 5.67
2017-11-16 07:30 | 5.39 | 5.38
2017-11-16 08:00 | 5.08 | 5.07
2017-11-16 08:30 | 4.76 | 4.74
2017-11-16 09:00 | 4.32 | 4.3
2017-11-16 09:30 | 4.35 | 4.34
2017-11-16 10:00 | 4.52 | 4.5
2017-11-16 10:30 | 4.48 | 4.46
2017-11-16 11:00 | 6.06 | 6.05
2017-11-16 11:30 | 4.48 | 4.46
2017-11-16 12:00 | 5.3 | 5.28
2017-11-16 12:30 | 5.1 | 5.08
2017-11-16 13:00 | 6.54 | 6.52
2017-11-16 13:30 | 5.84 | 5.81
2017-11-16 14:00 | 6.47 | 6.44
2017-11-16 14:30 | 7 | 6.98
2017-11-16 15:00 | 6.88 | 6.86
2017-11-16 15:30 | 7.41 | 7.39
2017-11-16 16:00 | 7.43 | 7.41
2017-11-16 16:30 | 7.78 | 7.76
2017-11-16 17:00 | 8.85 | 8.84
2017-11-16 17:30 | 9.21 | 9.19
2017-11-16 18:00 | 9.68 | 9.67
2017-11-16 18:30 | 10.25 | 10.24
2017-11-16 19:00 | 11.27 | 11.24
2017-11-16 19:30 | 10.87 | 10.85
2017-11-16 20:00 | 10.84 | 10.82
2017-11-16 20:30 | 11.17 | 11.15
2017-11-16 21:00 | 10.46 | 10.45
2017-11-16 21:30 | 9.49 | 9.47
2017-11-16 22:00 | 8.51 | 8.49
2017-11-16 22:30 | 7.85 | 7.84
2017-11-16 23:00 | 7.5 | 7.49
2017-11-16 23:30 | 6.53 | 6.52
2017-11-17 | 5.64 | 5.63
2017-11-17 00:30 | 5.12 | 5.11
2017-11-17 01:00 | 4.85 | 4.84
2017-11-17 01:30 | 4.59 | 4.57
2017-11-17 02:00 | 4.26 | 4.24
2017-11-17 02:30 | 4.2 | 4.17
2017-11-17 03:00 | 4.09 | 4.07
2017-11-17 03:30 | 4.24 | 4.22
2017-11-17 04:00 | 4.24 | 4.22
2017-11-17 04:30 | 4.37 | 4.34
2017-11-17 05:00 | 4.52 | 4.46
2017-11-17 05:30 | 5.7 | 5.63
2017-11-17 06:00 | 5.79 | 5.72
2017-11-17 06:30 | 5.01 | 4.96
2017-11-17 07:00 | 4.71 | 4.68
2017-11-17 07:30 | 4.83 | 4.81
2017-11-17 08:00 | 4.68 | 4.67
2017-11-17 08:30 | 3.8 | 3.77
2017-11-17 09:00 | 3.75 | 3.72
2017-11-17 09:30 | 4.24 | 4.2
2017-11-17 10:00 | 4.5 | 4.46
2017-11-17 10:30 | 4.31 | 4.26
2017-11-17 11:00 | 4.72 | 4.68
2017-11-17 11:30 | 4.19 | 4.15
2017-11-17 12:00 | 4.36 | 4.32
2017-11-17 12:30 | 4.75 | 4.72
2017-11-17 13:00 | 4.63 | 4.58
2017-11-17 13:30 | 5.44 | 5.4
2017-11-17 14:00 | 4.9 | 4.86
2017-11-17 14:30 | 6.28 | 6.25
2017-11-17 15:00 | 6.73 | 6.7
2017-11-17 15:30 | 6.88 | 6.86
2017-11-17 16:00 | 7.22 | 7.19
2017-11-17 16:30 | 8.14 | 8.11
2017-11-17 17:00 | 8.17 | 8.15
2017-11-17 17:30 | 8.31 | 8.28
2017-11-17 18:00 | 8.82 | 8.8
2017-11-17 18:30 | 9.24 | 9.22
2017-11-17 19:00 | 9.98 | 9.97
2017-11-17 19:30 | 10.01 | 10
2017-11-17 20:00 | 9.92 | 9.9
2017-11-17 20:30 | 9.79 | 9.77
2017-11-17 21:00 | 9.26 | 9.24
2017-11-17 21:30 | 8.6 | 8.59
2017-11-17 22:00 | 8.07 | 8.06
2017-11-17 22:30 | 7.73 | 7.72
2017-11-17 23:00 | 7.58 | 7.57
2017-11-17 23:30 | 6.7 | 6.69
2017-11-18 | 5.93 | 5.91
2017-11-18 00:30 | 5.31 | 5.3
2017-11-18 01:00 | 5.09 | 5.08
2017-11-18 01:30 | 4.88 | 4.86
2017-11-18 02:00 | 4.6 | 4.58
2017-11-18 02:30 | 4.41 | 4.39
2017-11-18 03:00 | 4.37 | 4.35
2017-11-18 03:30 | 4.22 | 4.2
2017-11-18 04:00 | 4.17 | 4.15
2017-11-18 04:30 | 4.24 | 4.22
2017-11-18 05:00 | 4.23 | 4.2
2017-11-18 05:30 | 4.24 | 4.16
2017-11-18 06:00 | 4.39 | 4.31
2017-11-18 06:30 | 4.46 | 4.39
2017-11-18 07:00 | 4.27 | 4.2
2017-11-18 07:30 | 4.51 | 4.47
2017-11-18 08:00 | 5.29 | 5.25
2017-11-18 08:30 | 5.99 | 5.97
2017-11-18 09:00 | 6.48 | 6.46
2017-11-18 09:30 | 7.65 | 7.64
2017-11-18 10:00 | 7.99 | 7.97
2017-11-18 10:30 | 7.81 | 7.79
2017-11-18 11:00 | 7.53 | 7.51
2017-11-18 11:30 | 6.61 | 6.59
2017-11-18 12:00 | 6.15 | 6.13
2017-11-18 12:30 | 6.71 | 6.69
2017-11-18 13:00 | 7.93 | 7.92
2017-11-18 13:30 | 7.4 | 7.38
2017-11-18 14:00 | 7.32 | 7.31
2017-11-18 14:30 | 6.97 | 6.95
2017-11-18 15:00 | 6.97 | 6.95
2017-11-18 15:30 | 6.95 | 6.93
2017-11-18 16:00 | 7.69 | 7.68
2017-11-18 16:30 | 7.89 | 7.88
2017-11-18 17:00 | 8.36 | 8.35
2017-11-18 17:30 | 8.57 | 8.56
2017-11-18 18:00 | 8.68 | 8.66
2017-11-18 18:30 | 8.81 | 8.79
2017-11-18 19:00 | 9.65 | 9.64
2017-11-18 19:30 | 9.52 | 9.51
2017-11-18 20:00 | 9.38 | 9.37
2017-11-18 20:30 | 9.24 | 9.23
2017-11-18 21:00 | 8.65 | 8.63
2017-11-18 21:30 | 8.13 | 8.11
2017-11-18 22:00 | 7.64 | 7.62
2017-11-18 22:30 | 7.44 | 7.43
2017-11-18 23:00 | 7.4 | 7.39
2017-11-18 23:30 | 6.67 | 6.66
2017-11-19 | 5.85 | 5.84
2017-11-19 00:30 | 5.27 | 5.25
2017-11-19 01:00 | 4.91 | 4.89
2017-11-19 01:30 | 4.6 | 4.57
2017-11-19 02:00 | 4.31 | 4.28
2017-11-19 02:30 | 4.21 | 4.18
2017-11-19 03:00 | 4.16 | 4.13
2017-11-19 03:30 | 4.03 | 4
2017-11-19 04:00 | 3.96 | 3.92
2017-11-19 04:30 | 4.47 | 4.43
2017-11-19 05:00 | 5.36 | 5.27
2017-11-19 05:30 | 5.27 | 5.15
2017-11-19 06:00 | 3.96 | 3.84
2017-11-19 06:30 | 3.64 | 3.53
2017-11-19 07:00 | 3.33 | 3.23
2017-11-19 07:30 | 3.6 | 3.53
2017-11-19 08:00 | 3.97 | 3.92
2017-11-19 08:30 | 4.61 | 4.59
2017-11-19 09:00 | 7.09 | 7.08
2017-11-19 09:30 | 5.4 | 5.37
2017-11-19 10:00 | 4.91 | 4.88
2017-11-19 10:30 | 5.41 | 5.38
2017-11-19 11:00 | 4.92 | 4.88
2017-11-19 11:30 | 4.99 | 4.96
2017-11-19 12:00 | 5.75 | 5.72
2017-11-19 12:30 | 7.59 | 7.57
2017-11-19 13:00 | 7.49 | 7.47
2017-11-19 13:30 | 7.54 | 7.53
2017-11-19 14:00 | 6.85 | 6.83
2017-11-19 14:30 | 5.25 | 5.22
2017-11-19 15:00 | 5.66 | 5.64
2017-11-19 15:30 | 6.9 | 6.88
2017-11-19 16:00 | 7.21 | 7.19
2017-11-19 16:30 | 6.94 | 6.92
2017-11-19 17:00 | 7.82 | 7.8
2017-11-19 17:30 | 9 | 8.99
2017-11-19 18:00 | 9.33 | 9.32
2017-11-19 18:30 | 9.86 | 9.85
2017-11-19 19:00 | 10.54 | 10.53
2017-11-19 19:30 | 10.36 | 10.35
2017-11-19 20:00 | 10.09 | 10.08
2017-11-19 20:30 | 9.93 | 9.92
2017-11-19 21:00 | 9.36 | 9.35
2017-11-19 21:30 | 8.69 | 8.68
2017-11-19 22:00 | 7.91 | 7.9
2017-11-19 22:30 | 7.45 | 7.44
2017-11-19 23:00 | 7.22 | 7.21
2017-11-19 23:30 | 6.34 | 6.32
2017-11-20 | 5.51 | 5.49
2017-11-20 00:30 | 4.83 | 4.8
2017-11-20 01:00 | 4.53 | 4.5
2017-11-20 01:30 | 4.42 | 4.39
2017-11-20 02:00 | 4.09 | 4.05
2017-11-20 02:30 | 3.93 | 3.89
2017-11-20 03:00 | 3.91 | 3.87
2017-11-20 03:30 | 4.08 | 4.05
2017-11-20 04:00 | 3.85 | 3.81
2017-11-20 04:30 | 4.07 | 4.03
2017-11-20 05:00 | 4.15 | 4.07
2017-11-20 05:30 | 4.49 | 4.4
2017-11-20 06:00 | 5.01 | 4.94
2017-11-20 06:30 | 5.38 | 5.34
2017-11-20 07:00 | 5.43 | 5.4
2017-11-20 07:30 | 5.29 | 5.27
2017-11-20 08:00 | 4.8 | 4.79
2017-11-20 08:30 | 4.3 | 4.29
2017-11-20 09:00 | 4.03 | 4.03
2017-11-20 09:30 | 3.53 | 3.52
2017-11-20 10:00 | 3.82 | 3.8
2017-11-20 10:30 | 3.65 | 3.63
2017-11-20 11:00 | 3.25 | 3.23
2017-11-20 11:30 | 4.17 | 4.16
2017-11-20 12:00 | 3.94 | 3.92
2017-11-20 12:30 | 4.7 | 4.69
2017-11-20 13:00 | 5.06 | 5.05
2017-11-20 13:30 | 5.68 | 5.67
2017-11-20 14:00 | 4.42 | 4.4
2017-11-20 14:30 | 5.76 | 5.75
2017-11-20 15:00 | 6.89 | 6.88
2017-11-20 15:30 | 5.76 | 5.75
2017-11-20 16:00 | 7.17 | 7.16
2017-11-20 16:30 | 7.58 | 7.57
2017-11-20 17:00 | 8.92 | 8.91
2017-11-20 17:30 | 9.7 | 9.69
2017-11-20 18:00 | 10.2 | 10.19
2017-11-20 18:30 | 10.49 | 10.48
2017-11-20 19:00 | 11.43 | 11.42
2017-11-20 19:30 | 11.31 | 11.3
2017-11-20 20:00 | 11.14 | 11.13
2017-11-20 20:30 | 10.91 | 10.9
2017-11-20 21:00 | 10.14 | 10.13
2017-11-20 21:30 | 9.37 | 9.37
2017-11-20 22:00 | 8.38 | 8.38
2017-11-20 22:30 | 7.58 | 7.57
2017-11-20 23:00 | 7.17 | 7.16
2017-11-20 23:30 | 6.13 | 6.12
2017-11-21 | 5.3 | 5.28
2017-11-21 00:30 | 4.74 | 4.71
2017-11-21 01:00 | 4.47 | 4.44
2017-11-21 01:30 | 4.22 | 4.19
2017-11-21 02:00 | 4.02 | 3.98
2017-11-21 02:30 | 3.84 | 3.79
2017-11-21 03:00 | 3.87 | 3.83
2017-11-21 03:30 | 3.96 | 3.92
2017-11-21 04:00 | 3.95 | 3.91
2017-11-21 04:30 | 4.08 | 4.04
2017-11-21 05:00 | 4.13 | 4.05
2017-11-21 05:30 | 4.75 | 4.69
2017-11-21 06:00 | 4.86 | 4.8
2017-11-21 06:30 | 4.88 | 4.82
2017-11-21 07:00 | 5.11 | 5.08
2017-11-21 07:30 | 5.19 | 5.18
2017-11-21 08:00 | 4.75 | 4.73
2017-11-21 08:30 | 4.2 | 4.18
2017-11-21 09:00 | 3.96 | 3.94
2017-11-21 09:30 | 4.09 | 4.07
2017-11-21 10:00 | 4.02 | 4
2017-11-21 10:30 | 4.19 | 4.18
2017-11-21 11:00 | 3.64 | 3.61
2017-11-21 11:30 | 3.91 | 3.88
2017-11-21 12:00 | 3.94 | 3.92
2017-11-21 12:30 | 5.96 | 5.94
2017-11-21 13:00 | 7.37 | 7.36
2017-11-21 13:30 | 4.65 | 4.63
2017-11-21 14:00 | 3.48 | 3.46
2017-11-21 14:30 | 4.12 | 4.1
2017-11-21 15:00 | 5.15 | 5.13
2017-11-21 15:30 | 5.77 | 5.75
2017-11-21 16:00 | 7.01 | 7
2017-11-21 16:30 | 7.65 | 7.64
2017-11-21 17:00 | 8.32 | 8.31
2017-11-21 17:30 | 9.06 | 9.06
2017-11-21 18:00 | 9.51 | 9.5
2017-11-21 18:30 | 10.12 | 10.12
2017-11-21 19:00 | 11.27 | 11.25
2017-11-21 19:30 | 11.5 | 11.49
2017-11-21 20:00 | 11.25 | 11.24
2017-11-21 20:30 | 10.95 | 10.94
2017-11-21 21:00 | 10.19 | 10.19
2017-11-21 21:30 | 9.5 | 9.5
2017-11-21 22:00 | 8.63 | 8.63
2017-11-21 22:30 | 7.95 | 7.95
2017-11-21 23:00 | 7.38 | 7.37
2017-11-21 23:30 | 6.3 | 6.28
2017-11-22 | 5.43 | 5.41
2017-11-22 00:30 | 4.8 | 4.78
2017-11-22 01:00 | 4.62 | 4.59
2017-11-22 01:30 | 4.42 | 4.39
2017-11-22 02:00 | 4.15 | 4.12
2017-11-22 02:30 | 3.97 | 3.94
2017-11-22 03:00 | 3.86 | 3.81
2017-11-22 03:30 | 4.01 | 3.97
2017-11-22 04:00 | 4.08 | 4.04
2017-11-22 04:30 | 4.2 | 4.17
2017-11-22 05:00 | 4.25 | 4.18
2017-11-22 05:30 | 4.99 | 4.93
2017-11-22 06:00 | 5.6 | 5.56
2017-11-22 06:30 | 5.76 | 5.73
2017-11-22 07:00 | 5.39 | 5.36
2017-11-22 07:30 | 5.05 | 5.03
2017-11-22 08:00 | 4.61 | 4.6
2017-11-22 08:30 | 3.93 | 3.92
2017-11-22 09:00 | 4.69 | 4.68
2017-11-22 09:30 | 3.88 | 3.87
2017-11-22 10:00 | 3.85 | 3.84
2017-11-22 10:30 | 3.69 | 3.67
2017-11-22 11:00 | 3.65 | 3.63
2017-11-22 11:30 | 3.94 | 3.91
2017-11-22 12:00 | 3.8 | 3.78
2017-11-22 12:30 | 3.68 | 3.65
2017-11-22 13:00 | 4.35 | 4.33
2017-11-22 13:30 | 4.06 | 4.03
2017-11-22 14:00 | 3.82 | 3.8
2017-11-22 14:30 | 4.56 | 4.54
2017-11-22 15:00 | 5.57 | 5.55
2017-11-22 15:30 | 5.32 | 5.3
2017-11-22 16:00 | 6.13 | 6.11
2017-11-22 16:30 | 7.4 | 7.38
2017-11-22 17:00 | 8.3 | 8.29
2017-11-22 17:30 | 9.3 | 9.29
2017-11-22 18:00 | 9.78 | 9.78
2017-11-22 18:30 | 10.46 | 10.45
2017-11-22 19:00 | 11.46 | 11.44
2017-11-22 19:30 | 10.99 | 10.97
2017-11-22 20:00 | 10.7 | 10.69
2017-11-22 20:30 | 10.96 | 10.95
2017-11-22 21:00 | 10.41 | 10.4
2017-11-22 21:30 | 9.64 | 9.64
2017-11-22 22:00 | 8.63 | 8.63
2017-11-22 22:30 | 7.93 | 7.92
2017-11-22 23:00 | 7.41 | 7.4
2017-11-22 23:30 | 6.39 | 6.38
2017-11-23 | 5.57 | 5.56
2017-11-23 00:30 | 4.85 | 4.83
2017-11-23 01:00 | 4.72 | 4.7
2017-11-23 01:30 | 4.43 | 4.4
2017-11-23 02:00 | 4.18 | 4.15
2017-11-23 02:30 | 4.05 | 4.02
2017-11-23 03:00 | 3.97 | 3.93
2017-11-23 03:30 | 3.99 | 3.96
2017-11-23 04:00 | 4.03 | 3.99
2017-11-23 04:30 | 4.2 | 4.17
2017-11-23 05:00 | 4.25 | 4.17
2017-11-23 05:30 | 4.66 | 4.58
2017-11-23 06:00 | 5.39 | 5.34
2017-11-23 06:30 | 5.46 | 5.43
2017-11-23 07:00 | 5.44 | 5.41
2017-11-23 07:30 | 5.09 | 5.07
2017-11-23 08:00 | 4.77 | 4.75
2017-11-23 08:30 | 4.54 | 4.52
2017-11-23 09:00 | 4.14 | 4.12
2017-11-23 09:30 | 4.12 | 4.1
2017-11-23 10:00 | 4.81 | 4.78
2017-11-23 10:30 | 4.87 | 4.84
2017-11-23 11:00 | 4.52 | 4.49
2017-11-23 11:30 | 4.83 | 4.8
2017-11-23 12:00 | 5.24 | 5.23
2017-11-23 12:30 | 5.34 | 5.32
2017-11-23 13:00 | 5.54 | 5.52
2017-11-23 13:30 | 6.56 | 6.54
2017-11-23 14:00 | 5.81 | 5.78
2017-11-23 14:30 | 5.86 | 5.83
2017-11-23 15:00 | 6.42 | 6.4
2017-11-23 15:30 | 5.39 | 5.35
2017-11-23 16:00 | 6.51 | 6.47
2017-11-23 16:30 | 7.13 | 7.1
2017-11-23 17:00 | 8.31 | 8.29
2017-11-23 17:30 | 9.78 | 9.77
2017-11-23 18:00 | 10.09 | 10.08
2017-11-23 18:30 | 10.66 | 10.65
2017-11-23 19:00 | 10.83 | 10.81
2017-11-23 19:30 | 10.79 | 10.77
2017-11-23 20:00 | 10.73 | 10.72
2017-11-23 20:30 | 10.49 | 10.47
2017-11-23 21:00 | 9.85 | 9.84
2017-11-23 21:30 | 9.16 | 9.15
2017-11-23 22:00 | 8.48 | 8.47
2017-11-23 22:30 | 8.01 | 8
2017-11-23 23:00 | 7.68 | 7.66
2017-11-23 23:30 | 6.54 | 6.53
2017-11-24 | 5.66 | 5.65
2017-11-24 00:30 | 5.02 | 5
2017-11-24 01:00 | 4.79 | 4.76
2017-11-24 01:30 | 4.47 | 4.45
2017-11-24 02:00 | 4.19 | 4.16
2017-11-24 02:30 | 4.11 | 4.09
2017-11-24 03:00 | 4.04 | 4.01
2017-11-24 03:30 | 4.13 | 4.1
2017-11-24 04:00 | 4.16 | 4.13
2017-11-24 04:30 | 4.33 | 4.29
2017-11-24 05:00 | 4.25 | 4.18
2017-11-24 05:30 | 4.68 | 4.61
2017-11-24 06:00 | 4.99 | 4.93
2017-11-24 06:30 | 5.09 | 5.04
2017-11-24 07:00 | 4.74 | 4.69
2017-11-24 07:30 | 4.61 | 4.58
2017-11-24 08:00 | 4.31 | 4.28
2017-11-24 08:30 | 3.84 | 3.8
2017-11-24 09:00 | 3.46 | 3.41
2017-11-24 09:30 | 3.81 | 3.77
2017-11-24 10:00 | 3.86 | 3.82
2017-11-24 10:30 | 3.78 | 3.73
2017-11-24 11:00 | 5.25 | 5.22
2017-11-24 11:30 | 4.36 | 4.29
2017-11-24 12:00 | 4.64 | 4.59
2017-11-24 12:30 | 5.02 | 4.96
2017-11-24 13:00 | 4.96 | 4.9
2017-11-24 13:30 | 5.62 | 5.56
2017-11-24 14:00 | 5.98 | 5.94
2017-11-24 14:30 | 5.85 | 5.81
2017-11-24 15:00 | 6.16 | 6.11
2017-11-24 15:30 | 6.7 | 6.65
2017-11-24 16:00 | 7.7 | 7.65
2017-11-24 16:30 | 8.49 | 8.45
2017-11-24 17:00 | 9.15 | 9.11
2017-11-24 17:30 | 9.6 | 9.56
2017-11-24 18:00 | 9.85 | 9.82
2017-11-24 18:30 | 9.99 | 9.96
2017-11-24 19:00 | 10.59 | 10.56
2017-11-24 19:30 | 10.53 | 10.5
2017-11-24 20:00 | 10.55 | 10.53
2017-11-24 20:30 | 10.55 | 10.54
2017-11-24 21:00 | 9.89 | 9.87
2017-11-24 21:30 | 9.11 | 9.09
2017-11-24 22:00 | 8.46 | 8.44
2017-11-24 22:30 | 8.21 | 8.19
2017-11-24 23:00 | 8.03 | 8.02
2017-11-24 23:30 | 6.99 | 6.97
2017-11-25 | 6.02 | 6.01
2017-11-25 00:30 | 5.34 | 5.33
2017-11-25 01:00 | 5.21 | 5.19
2017-11-25 01:30 | 4.87 | 4.85
2017-11-25 02:00 | 4.6 | 4.58
2017-11-25 02:30 | 4.43 | 4.41
2017-11-25 03:00 | 4.29 | 4.27
2017-11-25 03:30 | 4.27 | 4.25
2017-11-25 04:00 | 4.16 | 4.14
2017-11-25 04:30 | 4.28 | 4.25
2017-11-25 05:00 | 4.06 | 3.97
2017-11-25 05:30 | 4.11 | 4.01
2017-11-25 06:00 | 4.06 | 3.96
2017-11-25 06:30 | 3.98 | 3.9
2017-11-25 07:00 | 4.07 | 4.01
2017-11-25 07:30 | 4.18 | 4.14
2017-11-25 08:00 | 4.2 | 4.18
2017-11-25 08:30 | 4.17 | 4.15
2017-11-25 09:00 | 4.32 | 4.28
2017-11-25 09:30 | 4.87 | 4.83
2017-11-25 10:00 | 5.63 | 5.59
2017-11-25 10:30 | 6.19 | 6.15
2017-11-25 11:00 | 5.6 | 5.55
2017-11-25 11:30 | 5.22 | 5.16
2017-11-25 12:00 | 6.35 | 6.3
2017-11-25 12:30 | 6.62 | 6.57
2017-11-25 13:00 | 6.78 | 6.73
2017-11-25 13:30 | 7.88 | 7.83
2017-11-25 14:00 | 8.35 | 8.3
2017-11-25 14:30 | 8.48 | 8.43
2017-11-25 15:00 | 7.39 | 7.33
2017-11-25 15:30 | 8.58 | 8.53
2017-11-25 16:00 | 9.98 | 9.93
2017-11-25 16:30 | 9.99 | 9.94
2017-11-25 17:00 | 9.76 | 9.72
2017-11-25 17:30 | 9.78 | 9.75
2017-11-25 18:00 | 9.85 | 9.82
2017-11-25 18:30 | 9.93 | 9.9
2017-11-25 19:00 | 10.33 | 10.3
2017-11-25 19:30 | 10.37 | 10.35
2017-11-25 20:00 | 10.42 | 10.4
2017-11-25 20:30 | 10.14 | 10.12
2017-11-25 21:00 | 9.4 | 9.38
2017-11-25 21:30 | 8.77 | 8.76
2017-11-25 22:00 | 8.42 | 8.4
2017-11-25 22:30 | 8.15 | 8.13
2017-11-25 23:00 | 7.93 | 7.92
2017-11-25 23:30 | 7 | 6.98
2017-11-26 | 6.22 | 6.21
2017-11-26 00:30 | 5.6 | 5.58
2017-11-26 01:00 | 5.34 | 5.32
2017-11-26 01:30 | 4.96 | 4.95
2017-11-26 02:00 | 4.73 | 4.71
2017-11-26 02:30 | 4.52 | 4.5
2017-11-26 03:00 | 4.41 | 4.39
2017-11-26 03:30 | 4.37 | 4.35
2017-11-26 04:00 | 4.34 | 4.31
2017-11-26 04:30 | 4.41 | 4.39
2017-11-26 05:00 | 4.1 | 4.02
2017-11-26 05:30 | 4.04 | 3.94
2017-11-26 06:00 | 4.02 | 3.93
2017-11-26 06:30 | 3.89 | 3.81
2017-11-26 07:00 | 3.91 | 3.84
2017-11-26 07:30 | 3.94 | 3.9
2017-11-26 08:00 | 4.44 | 4.41
2017-11-26 08:30 | 5.88 | 5.86
2017-11-26 09:00 | 5.99 | 5.96
2017-11-26 09:30 | 5.67 | 5.64
2017-11-26 10:00 | 4.99 | 4.94
2017-11-26 10:30 | 5.46 | 5.41
2017-11-26 11:00 | 5.64 | 5.59
2017-11-26 11:30 | 6.18 | 6.13
2017-11-26 12:00 | 7.04 | 6.98
2017-11-26 12:30 | 7.64 | 7.59
2017-11-26 13:00 | 7.38 | 7.31
2017-11-26 13:30 | 8.01 | 7.94
2017-11-26 14:00 | 9.48 | 9.42
2017-11-26 14:30 | 9.99 | 9.93
2017-11-26 15:00 | 9.35 | 9.29
2017-11-26 15:30 | 9.09 | 9.02
2017-11-26 16:00 | 9.72 | 9.66
2017-11-26 16:30 | 10.49 | 10.44
2017-11-26 17:00 | 11.2 | 11.16
2017-11-26 17:30 | 11.69 | 11.66
2017-11-26 18:00 | 11.96 | 11.92
2017-11-26 18:30 | 11.81 | 11.78
2017-11-26 19:00 | 12.19 | 12.14
2017-11-26 19:30 | 12.12 | 12.08
2017-11-26 20:00 | 11.82 | 11.79
2017-11-26 20:30 | 11.4 | 11.38
2017-11-26 21:00 | 10.74 | 10.73
2017-11-26 21:30 | 9.78 | 9.76
2017-11-26 22:00 | 9.06 | 9.05
2017-11-26 22:30 | 8.43 | 8.42
2017-11-26 23:00 | 8.22 | 8.22
2017-11-26 23:30 | 7.19 | 7.18
2017-11-27 | 6.3 | 6.29
2017-11-27 00:30 | 5.66 | 5.65
2017-11-27 01:00 | 5.4 | 5.39
2017-11-27 01:30 | 5.11 | 5.1
2017-11-27 02:00 | 4.77 | 4.75
2017-11-27 02:30 | 4.59 | 4.58
2017-11-27 03:00 | 4.6 | 4.58
2017-11-27 03:30 | 4.71 | 4.7
2017-11-27 04:00 | 4.67 | 4.66
2017-11-27 04:30 | 4.73 | 4.71
2017-11-27 05:00 | 4.81 | 4.76
2017-11-27 05:30 | 5.24 | 5.2
2017-11-27 06:00 | 5.72 | 5.69
2017-11-27 06:30 | 5.67 | 5.65
2017-11-27 07:00 | 5.53 | 5.51
2017-11-27 07:30 | 5.85 | 5.84
2017-11-27 08:00 | 6.3 | 6.29
2017-11-27 08:30 | 5.77 | 5.76
2017-11-27 09:00 | 5.73 | 5.72
2017-11-27 09:30 | 5.21 | 5.18
2017-11-27 10:00 | 5.27 | 5.23
2017-11-27 10:30 | 5.23 | 5.19
2017-11-27 11:00 | 5.28 | 5.23
2017-11-27 11:30 | 5.98 | 5.94
2017-11-27 12:00 | 6.87 | 6.83
2017-11-27 12:30 | 6.94 | 6.89
2017-11-27 13:00 | 7.02 | 6.96
2017-11-27 13:30 | 7.7 | 7.63
2017-11-27 14:00 | 8.59 | 8.53
2017-11-27 14:30 | 8.02 | 7.94
2017-11-27 15:00 | 9.14 | 9.07
2017-11-27 15:30 | 9.32 | 9.25
2017-11-27 16:00 | 9.99 | 9.93
2017-11-27 16:30 | 10.83 | 10.77
2017-11-27 17:00 | 11.89 | 11.84
2017-11-27 17:30 | 12.42 | 12.37
2017-11-27 18:00 | 12.76 | 12.71
2017-11-27 18:30 | 13.04 | 13
2017-11-27 19:00 | 13.62 | 13.56
2017-11-27 19:30 | 13.4 | 13.34
2017-11-27 20:00 | 13.22 | 13.16
2017-11-27 20:30 | 12.65 | 12.61
2017-11-27 21:00 | 11.52 | 11.49
2017-11-27 21:30 | 10.39 | 10.37
2017-11-27 22:00 | 9.37 | 9.35
2017-11-27 22:30 | 8.8 | 8.78
2017-11-27 23:00 | 8.5 | 8.49
2017-11-27 23:30 | 7.37 | 7.36
2017-11-28 | 6.54 | 6.53
2017-11-28 00:30 | 5.91 | 5.9
2017-11-28 01:00 | 5.58 | 5.56
2017-11-28 01:30 | 5.33 | 5.32
2017-11-28 02:00 | 5.08 | 5.06
2017-11-28 02:30 | 4.95 | 4.93
2017-11-28 03:00 | 4.93 | 4.91
2017-11-28 03:30 | 4.97 | 4.95
2017-11-28 04:00 | 4.8 | 4.78
2017-11-28 04:30 | 4.86 | 4.84
2017-11-28 05:00 | 4.89 | 4.86
2017-11-28 05:30 | 5.37 | 5.32
2017-11-28 06:00 | 5.62 | 5.59
2017-11-28 06:30 | 5.83 | 5.81
2017-11-28 07:00 | 5.98 | 5.97
2017-11-28 07:30 | 5.98 | 5.97
2017-11-28 08:00 | 5.93 | 5.92
2017-11-28 08:30 | 5.81 | 5.8
2017-11-28 09:00 | 5.42 | 5.4
2017-11-28 09:30 | 5.74 | 5.72
2017-11-28 10:00 | 6.28 | 6.25
2017-11-28 10:30 | 6.02 | 5.97
2017-11-28 11:00 | 6.66 | 6.6
2017-11-28 11:30 | 6.58 | 6.51
2017-11-28 12:00 | 8.26 | 8.19
2017-11-28 12:30 | 8.46 | 8.39
2017-11-28 13:00 | 8.55 | 8.48
2017-11-28 13:30 | 8.96 | 8.89
2017-11-28 14:00 | 8.85 | 8.78
2017-11-28 14:30 | 8.62 | 8.54
2017-11-28 15:00 | 8.66 | 8.59
2017-11-28 15:30 | 9.04 | 8.96
2017-11-28 16:00 | 10.77 | 10.7
2017-11-28 16:30 | 11.06 | 10.99
2017-11-28 17:00 | 11.44 | 11.39
2017-11-28 17:30 | 11.96 | 11.92
2017-11-28 18:00 | 12.3 | 12.26
2017-11-28 18:30 | 12.84 | 12.8
2017-11-28 19:00 | 13.83 | 13.74
2017-11-28 19:30 | 13.77 | 13.69
2017-11-28 20:00 | 13.57 | 13.51
2017-11-28 20:30 | 13.15 | 13.11
2017-11-28 21:00 | 12.24 | 12.2
2017-11-28 21:30 | 11.1 | 11.08
2017-11-28 22:00 | 9.77 | 9.76
2017-11-28 22:30 | 9.16 | 9.15
2017-11-28 23:00 | 8.74 | 8.73
2017-11-28 23:30 | 7.64 | 7.62
2017-11-29 | 6.66 | 6.64
2017-11-29 00:30 | 6.06 | 6.05
2017-11-29 01:00 | 5.88 | 5.87
2017-11-29 01:30 | 5.56 | 5.55
2017-11-29 02:00 | 5.28 | 5.27
2017-11-29 02:30 | 5.13 | 5.12
2017-11-29 03:00 | 5.14 | 5.12
2017-11-29 03:30 | 5.09 | 5.07
2017-11-29 04:00 | 5.1 | 5.08
2017-11-29 04:30 | 5.24 | 5.22
2017-11-29 05:00 | 5.3 | 5.27
2017-11-29 05:30 | 5.59 | 5.56
2017-11-29 06:00 | 5.73 | 5.71
2017-11-29 06:30 | 6.13 | 6.11
2017-11-29 07:00 | 6.91 | 6.9
2017-11-29 07:30 | 7.03 | 7.03
2017-11-29 08:00 | 8.05 | 8.04
2017-11-29 08:30 | 7.29 | 7.28
2017-11-29 09:00 | 7.6 | 7.6
2017-11-29 09:30 | 7.68 | 7.67
2017-11-29 10:00 | 8.17 | 8.17
2017-11-29 10:30 | 8.59 | 8.59
2017-11-29 11:00 | 8.63 | 8.62
2017-11-29 11:30 | 7.86 | 7.85
2017-11-29 12:00 | 8.08 | 8.07
2017-11-29 12:30 | 7.9 | 7.89
2017-11-29 13:00 | 7.81 | 7.8
2017-11-29 13:30 | 7.28 | 7.26
2017-11-29 14:00 | 7.16 | 7.15
2017-11-29 14:30 | 7.01 | 7
2017-11-29 15:00 | 6.98 | 6.97
2017-11-29 15:30 | 7.53 | 7.51
2017-11-29 16:00 | 8.78 | 8.77
2017-11-29 16:30 | 9.11 | 9.1
2017-11-29 17:00 | 9.01 | 8.99
2017-11-29 17:30 | 9.8 | 9.79
2017-11-29 18:00 | 10.32 | 10.31
2017-11-29 18:30 | 10.95 | 10.93
2017-11-29 19:00 | 11.92 | 11.9
2017-11-29 19:30 | 11.87 | 11.85
2017-11-29 20:00 | 11.83 | 11.81
2017-11-29 20:30 | 11.77 | 11.75
2017-11-29 21:00 | 11.23 | 11.22
2017-11-29 21:30 | 10.06 | 10.05
2017-11-29 22:00 | 8.99 | 8.98
2017-11-29 22:30 | 8.29 | 8.27
2017-11-29 23:00 | 8.02 | 8.01
2017-11-29 23:30 | 7.12 | 7.11
2017-11-30 | 6.38 | 6.37
2017-11-30 00:30 | 5.7 | 5.69
2017-11-30 01:00 | 5.42 | 5.41
2017-11-30 01:30 | 5.23 | 5.21
2017-11-30 02:00 | 4.97 | 4.96
2017-11-30 02:30 | 4.82 | 4.8
2017-11-30 03:00 | 4.78 | 4.77
2017-11-30 03:30 | 4.77 | 4.76
2017-11-30 04:00 | 4.71 | 4.7
2017-11-30 04:30 | 4.94 | 4.93
2017-11-30 05:00 | 4.92 | 4.88
2017-11-30 05:30 | 5.15 | 5.11
2017-11-30 06:00 | 5.87 | 5.84
2017-11-30 06:30 | 5.89 | 5.87
2017-11-30 07:00 | 5.95 | 5.94
2017-11-30 07:30 | 6.14 | 6.14
2017-11-30 08:00 | 5.99 | 5.98
2017-11-30 08:30 | 5.76 | 5.74
2017-11-30 09:00 | 6.47 | 6.45
2017-11-30 09:30 | 6.52 | 6.51
2017-11-30 10:00 | 5.17 | 5.14
2017-11-30 10:30 | 5.86 | 5.84
2017-11-30 11:00 | 6.31 | 6.29
2017-11-30 11:30 | 5.6 | 5.58
2017-11-30 12:00 | 5.97 | 5.95
2017-11-30 12:30 | 6.16 | 6.14
2017-11-30 13:00 | 5.95 | 5.93
2017-11-30 13:30 | 5.79 | 5.77
2017-11-30 14:00 | 7.75 | 7.73
2017-11-30 14:30 | 8.52 | 8.5
2017-11-30 15:00 | 7.74 | 7.73
2017-11-30 15:30 | 8.1 | 8.08
2017-11-30 16:00 | 8.59 | 8.57
2017-11-30 16:30 | 9.4 | 9.38
2017-11-30 17:00 | 10.01 | 10
2017-11-30 17:30 | 10.34 | 10.33
2017-11-30 18:00 | 10.62 | 10.61
2017-11-30 18:30 | 10.83 | 10.81
2017-11-30 19:00 | 11.78 | 11.75
2017-11-30 19:30 | 11.31 | 11.28
2017-11-30 20:00 | 11.34 | 11.32
2017-11-30 20:30 | 11.38 | 11.37
2017-11-30 21:00 | 10.52 | 10.5
2017-11-30 21:30 | 9.78 | 9.75
2017-11-30 22:00 | 9.02 | 8.99
2017-11-30 22:30 | 8.51 | 8.49
2017-11-30 23:00 | 8.29 | 8.28
2017-11-30 23:30 | 7.33 | 7.31
2017-12-01 | 6.43 | 6.42
2017-12-01 00:30 | 5.8 | 5.79
2017-12-01 01:00 | 5.59 | 5.57
2017-12-01 01:30 | 5.26 | 5.25
2017-12-01 02:00 | 4.99 | 4.97
2017-12-01 02:30 | 4.84 | 4.82
2017-12-01 03:00 | 4.8 | 4.78
2017-12-01 03:30 | 4.81 | 4.79
2017-12-01 04:00 | 4.8 | 4.79
2017-12-01 04:30 | 4.96 | 4.95
2017-12-01 05:00 | 4.91 | 4.88
2017-12-01 05:30 | 5.14 | 5.1
2017-12-01 06:00 | 5.6 | 5.57
2017-12-01 06:30 | 5.66 | 5.65
2017-12-01 07:00 | 5.9 | 5.89
2017-12-01 07:30 | 5.96 | 5.95
2017-12-01 08:00 | 6.04 | 6.03
2017-12-01 08:30 | 6.17 | 6.16
2017-12-01 09:00 | 5.74 | 5.72
2017-12-01 09:30 | 5.25 | 5.22
2017-12-01 10:00 | 5.47 | 5.44
2017-12-01 10:30 | 5.46 | 5.43
2017-12-01 11:00 | 5.47 | 5.42
2017-12-01 11:30 | 5.75 | 5.7
2017-12-01 12:00 | 6.57 | 6.52
2017-12-01 12:30 | 6.24 | 6.18
2017-12-01 13:00 | 6.37 | 6.3
2017-12-01 13:30 | 6.85 | 6.78
2017-12-01 14:00 | 6.96 | 6.89
2017-12-01 14:30 | 7.06 | 6.98
2017-12-01 15:00 | 8.02 | 7.94
2017-12-01 15:30 | 8.6 | 8.53
2017-12-01 16:00 | 9.17 | 9.1
2017-12-01 16:30 | 9.65 | 9.6
2017-12-01 17:00 | 10.3 | 10.26
2017-12-01 17:30 | 10.25 | 10.22
2017-12-01 18:00 | 10.35 | 10.32
2017-12-01 18:30 | 10.33 | 10.3
2017-12-01 19:00 | 11.03 | 10.99
2017-12-01 19:30 | 11.21 | 11.18
2017-12-01 20:00 | 11.22 | 11.19
2017-12-01 20:30 | 11.12 | 11.1
2017-12-01 21:00 | 10.52 | 10.49
2017-12-01 21:30 | 9.87 | 9.84
2017-12-01 22:00 | 9.21 | 9.19
2017-12-01 22:30 | 8.76 | 8.74
2017-12-01 23:00 | 8.56 | 8.54
2017-12-01 23:30 | 7.41 | 7.39
2017-12-02 | 6.6 | 6.59
2017-12-02 00:30 | 6.09 | 6.08
2017-12-02 01:00 | 5.83 | 5.82
2017-12-02 01:30 | 5.42 | 5.4
2017-12-02 02:00 | 5.16 | 5.15
2017-12-02 02:30 | 5.1 | 5.08
2017-12-02 03:00 | 4.98 | 4.96
2017-12-02 03:30 | 4.92 | 4.9
2017-12-02 04:00 | 4.9 | 4.88
2017-12-02 04:30 | 4.94 | 4.93
2017-12-02 05:00 | 4.66 | 4.62
2017-12-02 05:30 | 4.62 | 4.57
2017-12-02 06:00 | 4.67 | 4.63
2017-12-02 06:30 | 5.25 | 5.22
2017-12-02 07:00 | 5.35 | 5.32
2017-12-02 07:30 | 5.49 | 5.46
2017-12-02 08:00 | 5.92 | 5.9
2017-12-02 08:30 | 5.8 | 5.78
2017-12-02 09:00 | 5.36 | 5.32
2017-12-02 09:30 | 6.95 | 6.91
2017-12-02 10:00 | 7.55 | 7.51
2017-12-02 10:30 | 7.05 | 7.01
2017-12-02 11:00 | 6.04 | 5.98
2017-12-02 11:30 | 6.24 | 6.17
2017-12-02 12:00 | 5.38 | 5.29
2017-12-02 12:30 | 6.04 | 5.97
2017-12-02 13:00 | 7.35 | 7.28
2017-12-02 13:30 | 7.53 | 7.47
2017-12-02 14:00 | 9.42 | 9.36
2017-12-02 14:30 | 9.95 | 9.9
2017-12-02 15:00 | 9.14 | 9.08
2017-12-02 15:30 | 9.32 | 9.26
2017-12-02 16:00 | 10.15 | 10.1
2017-12-02 16:30 | 9.98 | 9.93
2017-12-02 17:00 | 10.45 | 10.41
2017-12-02 17:30 | 10.98 | 10.94
2017-12-02 18:00 | 10.73 | 10.69
2017-12-02 18:30 | 10.98 | 10.94
2017-12-02 19:00 | 11.69 | 11.64
2017-12-02 19:30 | 11.64 | 11.59
2017-12-02 20:00 | 11.48 | 11.43
2017-12-02 20:30 | 11.22 | 11.19
2017-12-02 21:00 | 10.59 | 10.56
2017-12-02 21:30 | 10.07 | 10.05
2017-12-02 22:00 | 9.52 | 9.5
2017-12-02 22:30 | 9.14 | 9.12
2017-12-02 23:00 | 9.04 | 9.02
2017-12-02 23:30 | 8.06 | 8.04
2017-12-03 | 7.3 | 7.29
2017-12-03 00:30 | 6.6 | 6.58
2017-12-03 01:00 | 6.31 | 6.29
2017-12-03 01:30 | 5.95 | 5.93
2017-12-03 02:00 | 5.6 | 5.58
2017-12-03 02:30 | 5.32 | 5.31
2017-12-03 03:00 | 5.24 | 5.22
2017-12-03 03:30 | 5.25 | 5.24
2017-12-03 04:00 | 5.12 | 5.1
2017-12-03 04:30 | 5.03 | 5.01
2017-12-03 05:00 | 4.79 | 4.77
2017-12-03 05:30 | 4.62 | 4.57
2017-12-03 06:00 | 4.51 | 4.47
2017-12-03 06:30 | 4.69 | 4.65
2017-12-03 07:00 | 4.45 | 4.42
2017-12-03 07:30 | 5.42 | 5.4
2017-12-03 08:00 | 5.14 | 5.12
2017-12-03 08:30 | 5.22 | 5.19
2017-12-03 09:00 | 5.66 | 5.62
2017-12-03 09:30 | 5.93 | 5.89
2017-12-03 10:00 | 7.11 | 7.07
2017-12-03 10:30 | 8.17 | 8.13
2017-12-03 11:00 | 8.32 | 8.27
2017-12-03 11:30 | 7.75 | 7.68
2017-12-03 12:00 | 9.65 | 9.57
2017-12-03 12:30 | 9.93 | 9.85
2017-12-03 13:00 | 10.67 | 10.58
2017-12-03 13:30 | 10.3 | 10.21
2017-12-03 14:00 | 10.22 | 10.12
2017-12-03 14:30 | 11.38 | 11.29
2017-12-03 15:00 | 10.96 | 10.85
2017-12-03 15:30 | 11.61 | 11.51
2017-12-03 16:00 | 13.14 | 13.04
2017-12-03 16:30 | 13.33 | 13.24
2017-12-03 17:00 | 13.42 | 13.33
2017-12-03 17:30 | 14.24 | 14.15
2017-12-03 18:00 | 14.36 | 14.27
2017-12-03 18:30 | 14.06 | 13.98
2017-12-03 19:00 | 14.17 | 14.08
2017-12-03 19:30 | 14.14 | 14.05
2017-12-03 20:00 | 13.76 | 13.68
2017-12-03 20:30 | 13.21 | 13.15
2017-12-03 21:00 | 12.16 | 12.11
2017-12-03 21:30 | 11.25 | 11.21
2017-12-03 22:00 | 10.3 | 10.28
2017-12-03 22:30 | 9.7 | 9.68
2017-12-03 23:00 | 9.32 | 9.3
2017-12-03 23:30 | 8.23 | 8.22
2017-12-04 | 7.32 | 7.3
2017-12-04 00:30 | 6.55 | 6.53
2017-12-04 01:00 | 6.26 | 6.24
2017-12-04 01:30 | 5.92 | 5.9
2017-12-04 02:00 | 5.63 | 5.61
2017-12-04 02:30 | 5.43 | 5.41
2017-12-04 03:00 | 5.32 | 5.3
2017-12-04 03:30 | 5.31 | 5.29
2017-12-04 04:00 | 5.26 | 5.25
2017-12-04 04:30 | 5.31 | 5.3
2017-12-04 05:00 | 5.24 | 5.21
2017-12-04 05:30 | 5.41 | 5.38
2017-12-04 06:00 | 5.19 | 5.16
2017-12-04 06:30 | 5.44 | 5.42
2017-12-04 07:00 | 5.5 | 5.49
2017-12-04 07:30 | 5.97 | 5.96
2017-12-04 08:00 | 6.1 | 6.07
2017-12-04 08:30 | 6.1 | 6.06
2017-12-04 09:00 | 6.48 | 6.45
2017-12-04 09:30 | 7.58 | 7.54
2017-12-04 10:00 | 7.21 | 7.17
2017-12-04 10:30 | 8.67 | 8.64
2017-12-04 11:00 | 9.41 | 9.38
2017-12-04 11:30 | 9.39 | 9.37
2017-12-04 12:00 | 9.27 | 9.25
2017-12-04 12:30 | 9.29 | 9.27
2017-12-04 13:00 | 8.88 | 8.87
2017-12-04 13:30 | 8.31 | 8.3
2017-12-04 14:00 | 8.18 | 8.17
2017-12-04 14:30 | 7.83 | 7.82
2017-12-04 15:00 | 7.26 | 7.25
2017-12-04 15:30 | 7.77 | 7.76
2017-12-04 16:00 | 8.31 | 8.3
2017-12-04 16:30 | 8.73 | 8.72
2017-12-04 17:00 | 8.96 | 8.95
2017-12-04 17:30 | 9.28 | 9.26
2017-12-04 18:00 | 10.19 | 10.18
2017-12-04 18:30 | 10.71 | 10.7
2017-12-04 19:00 | 11.39 | 11.38
2017-12-04 19:30 | 11.68 | 11.66
2017-12-04 20:00 | 11.51 | 11.5
2017-12-04 20:30 | 11.23 | 11.22
2017-12-04 21:00 | 10.62 | 10.61
2017-12-04 21:30 | 9.87 | 9.86
2017-12-04 22:00 | 8.86 | 8.85
2017-12-04 22:30 | 8.18 | 8.17
2017-12-04 23:00 | 7.94 | 7.92
2017-12-04 23:30 | 6.82 | 6.81
2017-12-05 | 6.04 | 6.03
2017-12-05 00:30 | 5.42 | 5.41
2017-12-05 01:00 | 5.33 | 5.32
2017-12-05 01:30 | 4.98 | 4.97
2017-12-05 02:00 | 4.72 | 4.7
2017-12-05 02:30 | 4.66 | 4.64
2017-12-05 03:00 | 4.63 | 4.61
2017-12-05 03:30 | 4.55 | 4.54
2017-12-05 04:00 | 4.53 | 4.52
2017-12-05 04:30 | 4.69 | 4.68
2017-12-05 05:00 | 4.78 | 4.76
2017-12-05 05:30 | 5.2 | 5.16
2017-12-05 06:00 | 5.67 | 5.63
2017-12-05 06:30 | 5.78 | 5.76
2017-12-05 07:00 | 6.26 | 6.25
2017-12-05 07:30 | 6.44 | 6.42
2017-12-05 08:00 | 6.32 | 6.31
2017-12-05 08:30 | 6.56 | 6.54
2017-12-05 09:00 | 5.86 | 5.83
2017-12-05 09:30 | 4.52 | 4.48
2017-12-05 10:00 | 3.72 | 3.66
2017-12-05 10:30 | 5.74 | 5.71
2017-12-05 11:00 | 5.02 | 4.99
2017-12-05 11:30 | 4.08 | 4.03
2017-12-05 12:00 | 4.67 | 4.62
2017-12-05 12:30 | 5.31 | 5.25
2017-12-05 13:00 | 6.06 | 6
2017-12-05 13:30 | 6.74 | 6.69
2017-12-05 14:00 | 7.47 | 7.41
2017-12-05 14:30 | 7.5 | 7.43
2017-12-05 15:00 | 7.35 | 7.29
2017-12-05 15:30 | 9.17 | 9.11
2017-12-05 16:00 | 9.78 | 9.73
2017-12-05 16:30 | 9.9 | 9.85
2017-12-05 17:00 | 11.25 | 11.2
2017-12-05 17:30 | 11.98 | 11.93
2017-12-05 18:00 | 12.55 | 12.49
2017-12-05 18:30 | 12.93 | 12.88
2017-12-05 19:00 | 13.7 | 13.63
2017-12-05 19:30 | 13.98 | 13.9
2017-12-05 20:00 | 13.53 | 13.47
2017-12-05 20:30 | 13.08 | 13.03
2017-12-05 21:00 | 12.16 | 12.13
2017-12-05 21:30 | 11.06 | 11.03
2017-12-05 22:00 | 9.91 | 9.9
2017-12-05 22:30 | 9.1 | 9.09
2017-12-05 23:00 | 8.58 | 8.56
2017-12-05 23:30 | 7.43 | 7.41
2017-12-06 | 6.45 | 6.44
2017-12-06 00:30 | 5.78 | 5.77
2017-12-06 01:00 | 5.55 | 5.54
2017-12-06 01:30 | 5.2 | 5.19
2017-12-06 02:00 | 4.88 | 4.87
2017-12-06 02:30 | 4.77 | 4.76
2017-12-06 03:00 | 4.73 | 4.72
2017-12-06 03:30 | 4.68 | 4.67
2017-12-06 04:00 | 4.74 | 4.73
2017-12-06 04:30 | 4.92 | 4.91
2017-12-06 05:00 | 4.71 | 4.67
2017-12-06 05:30 | 5.05 | 5
2017-12-06 06:00 | 5.09 | 5.04
2017-12-06 06:30 | 5.23 | 5.2
2017-12-06 07:00 | 5.42 | 5.4
2017-12-06 07:30 | 5.33 | 5.32
2017-12-06 08:00 | 4.84 | 4.82
2017-12-06 08:30 | 4.53 | 4.51
2017-12-06 09:00 | 4.14 | 4.12
2017-12-06 09:30 | 4.07 | 4.04
2017-12-06 10:00 | 4.9 | 4.87
2017-12-06 10:30 | 3.84 | 3.79
2017-12-06 11:00 | 4.02 | 3.98
2017-12-06 11:30 | 4 | 3.96
2017-12-06 12:00 | 4.15 | 4.11
2017-12-06 12:30 | 4.48 | 4.42
2017-12-06 13:00 | 4.83 | 4.78
2017-12-06 13:30 | 5.8 | 5.75
2017-12-06 14:00 | 5.93 | 5.86
2017-12-06 14:30 | 6.33 | 6.27
2017-12-06 15:00 | 7.16 | 7.08
2017-12-06 15:30 | 8.1 | 8.02
2017-12-06 16:00 | 9.3 | 9.18
2017-12-06 16:30 | 10.61 | 10.52
2017-12-06 17:00 | 11.59 | 11.53
2017-12-06 17:30 | 12.36 | 12.29
2017-12-06 18:00 | 12.45 | 12.39
2017-12-06 18:30 | 12.77 | 12.71
2017-12-06 19:00 | 13.3 | 13.24
2017-12-06 19:30 | 13.22 | 13.15
2017-12-06 20:00 | 13.16 | 13.09
2017-12-06 20:30 | 12.77 | 12.71
2017-12-06 21:00 | 12 | 11.96
2017-12-06 21:30 | 11.03 | 11.01
2017-12-06 22:00 | 9.71 | 9.7
2017-12-06 22:30 | 8.87 | 8.85
2017-12-06 23:00 | 8.36 | 8.35
2017-12-06 23:30 | 7.16 | 7.15
2017-12-07 | 6.14 | 6.13
2017-12-07 00:30 | 5.53 | 5.52
2017-12-07 01:00 | 5.35 | 5.34
2017-12-07 01:30 | 5.06 | 5.05
2017-12-07 02:00 | 4.8 | 4.79
2017-12-07 02:30 | 4.72 | 4.7
2017-12-07 03:00 | 4.58 | 4.56
2017-12-07 03:30 | 4.52 | 4.5
2017-12-07 04:00 | 4.46 | 4.43
2017-12-07 04:30 | 4.65 | 4.62
2017-12-07 05:00 | 4.58 | 4.52
2017-12-07 05:30 | 4.99 | 4.93
2017-12-07 06:00 | 5.18 | 5.13
2017-12-07 06:30 | 5.4 | 5.37
2017-12-07 07:00 | 5.14 | 5.11
2017-12-07 07:30 | 5.04 | 5.03
2017-12-07 08:00 | 4.61 | 4.6
2017-12-07 08:30 | 4.37 | 4.35
2017-12-07 09:00 | 3.99 | 3.96
2017-12-07 09:30 | 4.11 | 4.08
2017-12-07 10:00 | 4.36 | 4.32
2017-12-07 10:30 | 4.58 | 4.52
2017-12-07 11:00 | 4.75 | 4.69
2017-12-07 11:30 | 5.41 | 5.34
2017-12-07 12:00 | 5.66 | 5.58
2017-12-07 12:30 | 6.32 | 6.21
2017-12-07 13:00 | 6.62 | 6.51
2017-12-07 13:30 | 7.24 | 7.13
2017-12-07 14:00 | 8.13 | 7.95
2017-12-07 14:30 | 8.86 | 8.69
2017-12-07 15:00 | 9.81 | 9.66
2017-12-07 15:30 | 10.73 | 10.58
2017-12-07 16:00 | 12.07 | 11.87
2017-12-07 16:30 | 13.06 | 12.85
2017-12-07 17:00 | 13.59 | 13.46
2017-12-07 17:30 | 13.98 | 13.85
2017-12-07 18:00 | 13.93 | 13.81
2017-12-07 18:30 | 13.86 | 13.76
2017-12-07 19:00 | 14.27 | 14.15
2017-12-07 19:30 | 14.45 | 14.32
2017-12-07 20:00 | 14.1 | 14
2017-12-07 20:30 | 13.46 | 13.38
2017-12-07 21:00 | 12.7 | 12.64
2017-12-07 21:30 | 11.82 | 11.78
2017-12-07 22:00 | 10.52 | 10.49
2017-12-07 22:30 | 9.6 | 9.58
2017-12-07 23:00 | 9 | 8.99
2017-12-07 23:30 | 7.85 | 7.84
2017-12-08 | 6.94 | 6.93
2017-12-08 00:30 | 6.41 | 6.4
2017-12-08 01:00 | 6.22 | 6.2
2017-12-08 01:30 | 5.79 | 5.78
2017-12-08 02:00 | 5.5 | 5.48
2017-12-08 02:30 | 5.4 | 5.38
2017-12-08 03:00 | 5.22 | 5.21
2017-12-08 03:30 | 5.22 | 5.2
2017-12-08 04:00 | 5.2 | 5.19
2017-12-08 04:30 | 5.32 | 5.31
2017-12-08 05:00 | 5.1 | 5.08
2017-12-08 05:30 | 5.32 | 5.29
2017-12-08 06:00 | 5.86 | 5.83
2017-12-08 06:30 | 5.98 | 5.97
2017-12-08 07:00 | 5.88 | 5.87
2017-12-08 07:30 | 6.13 | 6.12
2017-12-08 08:00 | 5.78 | 5.77
2017-12-08 08:30 | 5.8 | 5.77
2017-12-08 09:00 | 5.98 | 5.94
2017-12-08 09:30 | 6.22 | 6.16
2017-12-08 10:00 | 7.05 | 6.97
2017-12-08 10:30 | 8.19 | 8.11
2017-12-08 11:00 | 10.27 | 10.18
2017-12-08 11:30 | 10.41 | 10.3
2017-12-08 12:00 | 10.54 | 10.45
2017-12-08 12:30 | 10.89 | 10.84
2017-12-08 13:00 | 9.59 | 9.57
2017-12-08 13:30 | 8.64 | 8.63
2017-12-08 14:00 | 7.83 | 7.82
2017-12-08 14:30 | 8.34 | 8.33
2017-12-08 15:00 | 7.98 | 7.97
2017-12-08 15:30 | 8.37 | 8.36
2017-12-08 16:00 | 8.47 | 8.46
2017-12-08 16:30 | 8.53 | 8.51
2017-12-08 17:00 | 8.85 | 8.83
2017-12-08 17:30 | 9.07 | 9.05
2017-12-08 18:00 | 9.36 | 9.34
2017-12-08 18:30 | 9.56 | 9.54
2017-12-08 19:00 | 10.21 | 10.2
2017-12-08 19:30 | 10.2 | 10.19
2017-12-08 20:00 | 10.37 | 10.36
2017-12-08 20:30 | 10.2 | 10.19
2017-12-08 21:00 | 9.67 | 9.66
2017-12-08 21:30 | 8.91 | 8.9
2017-12-08 22:00 | 8.2 | 8.19
2017-12-08 22:30 | 7.95 | 7.94
2017-12-08 23:00 | 7.81 | 7.8
2017-12-08 23:30 | 6.84 | 6.83
2017-12-09 | 6.03 | 6.02
2017-12-09 00:30 | 5.52 | 5.51
2017-12-09 01:00 | 5.25 | 5.24
2017-12-09 01:30 | 5.01 | 4.99
2017-12-09 02:00 | 4.71 | 4.7
2017-12-09 02:30 | 4.55 | 4.53
2017-12-09 03:00 | 4.44 | 4.43
2017-12-09 03:30 | 4.48 | 4.46
2017-12-09 04:00 | 4.37 | 4.35
2017-12-09 04:30 | 4.37 | 4.35
2017-12-09 05:00 | 4.24 | 4.17
2017-12-09 05:30 | 4.06 | 3.96
2017-12-09 06:00 | 4.03 | 3.94
2017-12-09 06:30 | 4.19 | 4.13
2017-12-09 07:00 | 4.18 | 4.13
2017-12-09 07:30 | 4.19 | 4.16
2017-12-09 08:00 | 4.32 | 4.3
2017-12-09 08:30 | 4.49 | 4.47
2017-12-09 09:00 | 4.62 | 4.58
2017-12-09 09:30 | 4.88 | 4.84
2017-12-09 10:00 | 5.28 | 5.23
2017-12-09 10:30 | 5.38 | 5.33
2017-12-09 11:00 | 5.73 | 5.66
2017-12-09 11:30 | 6.24 | 6.16
2017-12-09 12:00 | 6.93 | 6.83
2017-12-09 12:30 | 7.62 | 7.51
2017-12-09 13:00 | 8.76 | 8.64
2017-12-09 13:30 | 8.89 | 8.76
2017-12-09 14:00 | 10.06 | 9.93
2017-12-09 14:30 | 10.06 | 9.93
2017-12-09 15:00 | 10.43 | 10.31
2017-12-09 15:30 | 10.75 | 10.63
2017-12-09 16:00 | 11.33 | 11.23
2017-12-09 16:30 | 11.91 | 11.84
2017-12-09 17:00 | 11.62 | 11.57
2017-12-09 17:30 | 11.2 | 11.17
2017-12-09 18:00 | 10.52 | 10.5
2017-12-09 18:30 | 10.03 | 10
2017-12-09 19:00 | 10.4 | 10.38
2017-12-09 19:30 | 11.71 | 11.7
2017-12-09 20:00 | 11.51 | 11.5
2017-12-09 20:30 | 11.26 | 11.25
2017-12-09 21:00 | 9.62 | 9.61
2017-12-09 21:30 | 8.65 | 8.63
2017-12-09 22:00 | 8.17 | 8.15
2017-12-09 22:30 | 8.08 | 8.07
2017-12-09 23:00 | 7.85 | 7.83
2017-12-09 23:30 | 6.88 | 6.87
2017-12-10 | 6.09 | 6.08
2017-12-10 00:30 | 5.59 | 5.57
2017-12-10 01:00 | 5.38 | 5.36
2017-12-10 01:30 | 5.01 | 4.99
2017-12-10 02:00 | 4.72 | 4.71
2017-12-10 02:30 | 4.53 | 4.52
2017-12-10 03:00 | 4.43 | 4.41
2017-12-10 03:30 | 4.46 | 4.43
2017-12-10 04:00 | 4.33 | 4.3
2017-12-10 04:30 | 4.31 | 4.28
2017-12-10 05:00 | 4.13 | 4.06
2017-12-10 05:30 | 3.98 | 3.88
2017-12-10 06:00 | 4.07 | 3.97
2017-12-10 06:30 | 3.9 | 3.82
2017-12-10 07:00 | 3.91 | 3.85
2017-12-10 07:30 | 4.1 | 4.07
2017-12-10 08:00 | 4.17 | 4.14
2017-12-10 08:30 | 4.55 | 4.52
2017-12-10 09:00 | 4.52 | 4.49
2017-12-10 09:30 | 4.66 | 4.62
2017-12-10 10:00 | 4.91 | 4.86
2017-12-10 10:30 | 5.15 | 5.11
2017-12-10 11:00 | 5.35 | 5.3
2017-12-10 11:30 | 5.45 | 5.4
2017-12-10 12:00 | 6.1 | 6.05
2017-12-10 12:30 | 7.12 | 7.07
2017-12-10 13:00 | 7.04 | 6.98
2017-12-10 13:30 | 8.28 | 8.23
2017-12-10 14:00 | 9.24 | 9.2
2017-12-10 14:30 | 9.02 | 8.98
2017-12-10 15:00 | 9.43 | 9.39
2017-12-10 15:30 | 9.25 | 9.22
2017-12-10 16:00 | 8.74 | 8.71
2017-12-10 16:30 | 9.27 | 9.24
2017-12-10 17:00 | 10.34 | 10.31
2017-12-10 17:30 | 10.55 | 10.53
2017-12-10 18:00 | 10.8 | 10.77
2017-12-10 18:30 | 10.71 | 10.69
2017-12-10 19:00 | 10.77 | 10.76
2017-12-10 19:30 | 11 | 10.97
2017-12-10 20:00 | 10.75 | 10.73
2017-12-10 20:30 | 10.47 | 10.46
2017-12-10 21:00 | 9.85 | 9.84
2017-12-10 21:30 | 9.01 | 9
2017-12-10 22:00 | 8.35 | 8.35
2017-12-10 22:30 | 8 | 8
2017-12-10 23:00 | 7.87 | 7.87
2017-12-10 23:30 | 6.88 | 6.87
2017-12-11 | 5.95 | 5.94
2017-12-11 00:30 | 5.35 | 5.33
2017-12-11 01:00 | 5.09 | 5.07
2017-12-11 01:30 | 4.8 | 4.79
2017-12-11 02:00 | 4.62 | 4.6
2017-12-11 02:30 | 4.43 | 4.41
2017-12-11 03:00 | 4.39 | 4.37
2017-12-11 03:30 | 4.48 | 4.46
2017-12-11 04:00 | 4.44 | 4.42
2017-12-11 04:30 | 4.6 | 4.58
2017-12-11 05:00 | 4.56 | 4.5
2017-12-11 05:30 | 4.73 | 4.65
2017-12-11 06:00 | 4.79 | 4.73
2017-12-11 06:30 | 4.7 | 4.64
2017-12-11 07:00 | 4.55 | 4.51
2017-12-11 07:30 | 4.25 | 4.23
2017-12-11 08:00 | 4.01 | 3.99
2017-12-11 08:30 | 3.96 | 3.93
2017-12-11 09:00 | 3.82 | 3.79
2017-12-11 09:30 | 4.21 | 4.18
2017-12-11 10:00 | 4.8 | 4.77
2017-12-11 10:30 | 4.89 | 4.86
2017-12-11 11:00 | 4.98 | 4.94
2017-12-11 11:30 | 6 | 5.97
2017-12-11 12:00 | 5.87 | 5.84
2017-12-11 12:30 | 6.16 | 6.12
2017-12-11 13:00 | 6.06 | 6.01
2017-12-11 13:30 | 6.59 | 6.53
2017-12-11 14:00 | 6.63 | 6.55
2017-12-11 14:30 | 7.87 | 7.8
2017-12-11 15:00 | 8.49 | 8.42
2017-12-11 15:30 | 9.35 | 9.28
2017-12-11 16:00 | 9.29 | 9.22
2017-12-11 16:30 | 10.01 | 9.95
2017-12-11 17:00 | 10.92 | 10.88
2017-12-11 17:30 | 11.22 | 11.18
2017-12-11 18:00 | 11.63 | 11.6
2017-12-11 18:30 | 12.05 | 12.02
2017-12-11 19:00 | 12.57 | 12.54
2017-12-11 19:30 | 12.72 | 12.68
2017-12-11 20:00 | 12.62 | 12.59
2017-12-11 20:30 | 12.21 | 12.18
2017-12-11 21:00 | 11.3 | 11.28
2017-12-11 21:30 | 10.3 | 10.3
2017-12-11 22:00 | 9.04 | 9.04
2017-12-11 22:30 | 8.28 | 8.27
2017-12-11 23:00 | 7.89 | 7.88
2017-12-11 23:30 | 6.8 | 6.79
2017-12-12 | 6.07 | 6.06
2017-12-12 00:30 | 5.46 | 5.45
2017-12-12 01:00 | 5.29 | 5.28
2017-12-12 01:30 | 4.95 | 4.94
2017-12-12 02:00 | 4.65 | 4.63
2017-12-12 02:30 | 4.44 | 4.42
2017-12-12 03:00 | 4.44 | 4.41
2017-12-12 03:30 | 4.5 | 4.47
2017-12-12 04:00 | 4.46 | 4.44
2017-12-12 04:30 | 4.53 | 4.5
2017-12-12 05:00 | 4.56 | 4.5
2017-12-12 05:30 | 5.06 | 5
2017-12-12 06:00 | 5.19 | 5.13
2017-12-12 06:30 | 5.08 | 5.04
2017-12-12 07:00 | 4.93 | 4.9
2017-12-12 07:30 | 4.7 | 4.68
2017-12-12 08:00 | 4.31 | 4.29
2017-12-12 08:30 | 4.21 | 4.19
2017-12-12 09:00 | 4.02 | 3.99
2017-12-12 09:30 | 4 | 3.95
2017-12-12 10:00 | 4.31 | 4.26
2017-12-12 10:30 | 5.29 | 5.25
2017-12-12 11:00 | 5.3 | 5.26
2017-12-12 11:30 | 4.96 | 4.91
2017-12-12 12:00 | 6.03 | 5.99
2017-12-12 12:30 | 6.11 | 6.08
2017-12-12 13:00 | 5.59 | 5.53
2017-12-12 13:30 | 6.23 | 6.17
2017-12-12 14:00 | 6.79 | 6.72
2017-12-12 14:30 | 7.74 | 7.67
2017-12-12 15:00 | 8.3 | 8.24
2017-12-12 15:30 | 8.77 | 8.71
2017-12-12 16:00 | 9.12 | 9.06
2017-12-12 16:30 | 9.87 | 9.81
2017-12-12 17:00 | 10.7 | 10.65
2017-12-12 17:30 | 11.42 | 11.37
2017-12-12 18:00 | 11.67 | 11.62
2017-12-12 18:30 | 12.04 | 12.01
2017-12-12 19:00 | 12.55 | 12.51
2017-12-12 19:30 | 12.77 | 12.71
2017-12-12 20:00 | 12.58 | 12.54
2017-12-12 20:30 | 12.2 | 12.17
2017-12-12 21:00 | 11.08 | 11.06
2017-12-12 21:30 | 10.13 | 10.12
2017-12-12 22:00 | 9 | 8.99
2017-12-12 22:30 | 8.48 | 8.47
2017-12-12 23:00 | 8.16 | 8.15
2017-12-12 23:30 | 6.94 | 6.93
2017-12-13 | 6.1 | 6.08
2017-12-13 00:30 | 5.52 | 5.51
2017-12-13 01:00 | 5.29 | 5.27
2017-12-13 01:30 | 5.03 | 5.02
2017-12-13 02:00 | 4.8 | 4.79
2017-12-13 02:30 | 4.59 | 4.57
2017-12-13 03:00 | 4.46 | 4.44
2017-12-13 03:30 | 4.54 | 4.51
2017-12-13 04:00 | 4.43 | 4.41
2017-12-13 04:30 | 4.56 | 4.53
2017-12-13 05:00 | 4.46 | 4.4
2017-12-13 05:30 | 4.6 | 4.52
2017-12-13 06:00 | 4.55 | 4.48
2017-12-13 06:30 | 4.56 | 4.5
2017-12-13 07:00 | 4.3 | 4.25
2017-12-13 07:30 | 4.1 | 4.07
2017-12-13 08:00 | 3.99 | 3.96
2017-12-13 08:30 | 4.27 | 4.25
2017-12-13 09:00 | 4.78 | 4.75
2017-12-13 09:30 | 4.97 | 4.95
2017-12-13 10:00 | 5.04 | 5.01
2017-12-13 10:30 | 4.8 | 4.77
2017-12-13 11:00 | 5.18 | 5.14
2017-12-13 11:30 | 5.27 | 5.21
2017-12-13 12:00 | 6.49 | 6.44
2017-12-13 12:30 | 6.27 | 6.21
2017-12-13 13:00 | 7.24 | 7.17
2017-12-13 13:30 | 7.58 | 7.49
2017-12-13 14:00 | 8.07 | 7.97
2017-12-13 14:30 | 8.87 | 8.77
2017-12-13 15:00 | 9.53 | 9.44
2017-12-13 15:30 | 10.08 | 9.99
2017-12-13 16:00 | 10.51 | 10.42
2017-12-13 16:30 | 10.87 | 10.79
2017-12-13 17:00 | 11.4 | 11.34
2017-12-13 17:30 | 12.16 | 12.1
2017-12-13 18:00 | 12.43 | 12.38
2017-12-13 18:30 | 12.54 | 12.5
2017-12-13 19:00 | 13.04 | 12.99
2017-12-13 19:30 | 13.25 | 13.18
2017-12-13 20:00 | 13.04 | 12.98
2017-12-13 20:30 | 12.69 | 12.64
2017-12-13 21:00 | 11.9 | 11.87
2017-12-13 21:30 | 10.69 | 10.67
2017-12-13 22:00 | 9.69 | 9.67
2017-12-13 22:30 | 9.17 | 9.16
2017-12-13 23:00 | 8.6 | 8.59
2017-12-13 23:30 | 7.45 | 7.43
2017-12-14 | 6.58 | 6.57
2017-12-14 00:30 | 5.97 | 5.96
2017-12-14 01:00 | 5.73 | 5.72
2017-12-14 01:30 | 5.35 | 5.34
2017-12-14 02:00 | 5.05 | 5.04
2017-12-14 02:30 | 4.92 | 4.91
2017-12-14 03:00 | 4.8 | 4.79
2017-12-14 03:30 | 4.85 | 4.84
2017-12-14 04:00 | 4.76 | 4.74
2017-12-14 04:30 | 4.81 | 4.79
2017-12-14 05:00 | 4.74 | 4.69
2017-12-14 05:30 | 5.17 | 5.12
2017-12-14 06:00 | 5.32 | 5.28
2017-12-14 06:30 | 5.21 | 5.19
2017-12-14 07:00 | 5.07 | 5.05
2017-12-14 07:30 | 4.91 | 4.9
2017-12-14 08:00 | 4.8 | 4.79
2017-12-14 08:30 | 4.8 | 4.77
2017-12-14 09:00 | 4.84 | 4.8
2017-12-14 09:30 | 5.09 | 5.04
2017-12-14 10:00 | 5.3 | 5.25
2017-12-14 10:30 | 5.43 | 5.38
2017-12-14 11:00 | 5.92 | 5.87
2017-12-14 11:30 | 5.92 | 5.86
2017-12-14 12:00 | 5.98 | 5.91
2017-12-14 12:30 | 6.67 | 6.6
2017-12-14 13:00 | 7.2 | 7.08
2017-12-14 13:30 | 7.63 | 7.51
2017-12-14 14:00 | 8.53 | 8.39
2017-12-14 14:30 | 9.16 | 8.99
2017-12-14 15:00 | 9.91 | 9.74
2017-12-14 15:30 | 10.6 | 10.47
2017-12-14 16:00 | 11.28 | 11.14
2017-12-14 16:30 | 12.18 | 12.05
2017-12-14 17:00 | 12.73 | 12.62
2017-12-14 17:30 | 13.14 | 13.05
2017-12-14 18:00 | 14.05 | 13.98
2017-12-14 18:30 | 13.74 | 13.67
2017-12-14 19:00 | 13.76 | 13.68
2017-12-14 19:30 | 14 | 13.9
2017-12-14 20:00 | 13.59 | 13.49
2017-12-14 20:30 | 13.29 | 13.21
2017-12-14 21:00 | 12.34 | 12.28
2017-12-14 21:30 | 11.29 | 11.25
2017-12-14 22:00 | 10.06 | 10.04
2017-12-14 22:30 | 9.45 | 9.43
2017-12-14 23:00 | 8.84 | 8.83
2017-12-14 23:30 | 7.69 | 7.68
2017-12-15 | 6.83 | 6.82
2017-12-15 00:30 | 6.22 | 6.21
2017-12-15 01:00 | 6.04 | 6.03
2017-12-15 01:30 | 5.68 | 5.67
2017-12-15 02:00 | 5.36 | 5.34
2017-12-15 02:30 | 5.11 | 5.1
2017-12-15 03:00 | 5.16 | 5.14
2017-12-15 03:30 | 5.02 | 5
2017-12-15 04:00 | 4.95 | 4.93
2017-12-15 04:30 | 5.06 | 5.04
2017-12-15 05:00 | 4.99 | 4.95
2017-12-15 05:30 | 5.11 | 5.06
2017-12-15 06:00 | 5.17 | 5.13
2017-12-15 06:30 | 4.95 | 4.92
2017-12-15 07:00 | 4.91 | 4.89
2017-12-15 07:30 | 4.8 | 4.78
2017-12-15 08:00 | 4.81 | 4.78
2017-12-15 08:30 | 5.17 | 5.13
2017-12-15 09:00 | 5.02 | 4.97
2017-12-15 09:30 | 5.09 | 5.02
2017-12-15 10:00 | 5.17 | 5.09
2017-12-15 10:30 | 5.66 | 5.58
2017-12-15 11:00 | 6.05 | 5.97
2017-12-15 11:30 | 6.32 | 6.24
2017-12-15 12:00 | 6.64 | 6.54
2017-12-15 12:30 | 7.39 | 7.25
2017-12-15 13:00 | 8 | 7.86
2017-12-15 13:30 | 8.18 | 8.04
2017-12-15 14:00 | 9.21 | 9.07
2017-12-15 14:30 | 9.59 | 9.44
2017-12-15 15:00 | 10.15 | 10.01
2017-12-15 15:30 | 10.96 | 10.81
2017-12-15 16:00 | 11.56 | 11.42
2017-12-15 16:30 | 12.51 | 12.36
2017-12-15 17:00 | 13.14 | 13
2017-12-15 17:30 | 13.4 | 13.28
2017-12-15 18:00 | 13.26 | 13.15
2017-12-15 18:30 | 13.06 | 12.96
2017-12-15 19:00 | 13.27 | 13.18
2017-12-15 19:30 | 13.44 | 13.33
2017-12-15 20:00 | 13.33 | 13.24
2017-12-15 20:30 | 12.83 | 12.75
2017-12-15 21:00 | 12.1 | 12.03
2017-12-15 21:30 | 11.09 | 11.04
2017-12-15 22:00 | 10.37 | 10.33
2017-12-15 22:30 | 9.94 | 9.92
2017-12-15 23:00 | 9.55 | 9.53
2017-12-15 23:30 | 8.33 | 8.31
2017-12-16 | 7.37 | 7.35
2017-12-16 00:30 | 6.71 | 6.69
2017-12-16 01:00 | 6.47 | 6.45
2017-12-16 01:30 | 6.09 | 6.07
2017-12-16 02:00 | 5.71 | 5.69
2017-12-16 02:30 | 5.53 | 5.51
2017-12-16 03:00 | 5.42 | 5.4
2017-12-16 03:30 | 5.34 | 5.32
2017-12-16 04:00 | 5.22 | 5.2
2017-12-16 04:30 | 5.26 | 5.24
2017-12-16 05:00 | 5.02 | 5
2017-12-16 05:30 | 4.96 | 4.93
2017-12-16 06:00 | 4.98 | 4.95
2017-12-16 06:30 | 4.97 | 4.95
2017-12-16 07:00 | 5 | 4.98
2017-12-16 07:30 | 5.66 | 5.63
2017-12-16 08:00 | 5.68 | 5.65
2017-12-16 08:30 | 5.94 | 5.91
2017-12-16 09:00 | 6.71 | 6.67
2017-12-16 09:30 | 6.97 | 6.92
2017-12-16 10:00 | 7.86 | 7.8
2017-12-16 10:30 | 7.73 | 7.63
2017-12-16 11:00 | 7.88 | 7.77
2017-12-16 11:30 | 8.19 | 8.06
2017-12-16 12:00 | 8.61 | 8.47
2017-12-16 12:30 | 9.75 | 9.6
2017-12-16 13:00 | 10.78 | 10.63
2017-12-16 13:30 | 11.07 | 10.91
2017-12-16 14:00 | 11.09 | 10.92
2017-12-16 14:30 | 12.33 | 12.17
2017-12-16 15:00 | 11.82 | 11.65
2017-12-16 15:30 | 12.48 | 12.31
2017-12-16 16:00 | 13 | 12.85
2017-12-16 16:30 | 13.68 | 13.54
2017-12-16 17:00 | 13.96 | 13.84
2017-12-16 17:30 | 13.14 | 13.03
2017-12-16 18:00 | 12.54 | 12.44
2017-12-16 18:30 | 12.58 | 12.49
2017-12-16 19:00 | 12.56 | 12.47
2017-12-16 19:30 | 12.68 | 12.58
2017-12-16 20:00 | 12.61 | 12.53
2017-12-16 20:30 | 12.21 | 12.13
2017-12-16 21:00 | 11.41 | 11.35
2017-12-16 21:30 | 10.78 | 10.73
2017-12-16 22:00 | 10.32 | 10.28
2017-12-16 22:30 | 9.99 | 9.96
2017-12-16 23:00 | 9.69 | 9.67
2017-12-16 23:30 | 8.63 | 8.61
2017-12-17 | 7.6 | 7.58
2017-12-17 00:30 | 6.88 | 6.86
2017-12-17 01:00 | 6.55 | 6.53
2017-12-17 01:30 | 6.11 | 6.09
2017-12-17 02:00 | 5.86 | 5.85
2017-12-17 02:30 | 5.62 | 5.6
2017-12-17 03:00 | 5.38 | 5.36
2017-12-17 03:30 | 5.36 | 5.34
2017-12-17 04:00 | 5.21 | 5.19
2017-12-17 04:30 | 5.18 | 5.16
2017-12-17 05:00 | 4.83 | 4.8
2017-12-17 05:30 | 4.71 | 4.66
2017-12-17 06:00 | 4.73 | 4.69
2017-12-17 06:30 | 4.75 | 4.72
2017-12-17 07:00 | 4.78 | 4.76
2017-12-17 07:30 | 5.1 | 5.07
2017-12-17 08:00 | 5.26 | 5.23
2017-12-17 08:30 | 5.7 | 5.66
2017-12-17 09:00 | 6.09 | 6.04
2017-12-17 09:30 | 6.66 | 6.61
2017-12-17 10:00 | 7.29 | 7.24
2017-12-17 10:30 | 7.34 | 7.27
2017-12-17 11:00 | 8.19 | 8.1
2017-12-17 11:30 | 9.26 | 9.15
2017-12-17 12:00 | 9.76 | 9.64
2017-12-17 12:30 | 10.25 | 10.11
2017-12-17 13:00 | 10.23 | 10.08
2017-12-17 13:30 | 11.46 | 11.29
2017-12-17 14:00 | 12.02 | 11.85
2017-12-17 14:30 | 12.31 | 12.12
2017-12-17 15:00 | 12.56 | 12.36
2017-12-17 15:30 | 13.19 | 13
2017-12-17 16:00 | 13.48 | 13.3
2017-12-17 16:30 | 14.09 | 13.93
2017-12-17 17:00 | 14.56 | 14.42
2017-12-17 17:30 | 14.45 | 14.33
2017-12-17 18:00 | 13.93 | 13.83
2017-12-17 18:30 | 13.64 | 13.56
2017-12-17 19:00 | 13.65 | 13.56
2017-12-17 19:30 | 13.4 | 13.3
2017-12-17 20:00 | 13.26 | 13.17
2017-12-17 20:30 | 12.75 | 12.69
2017-12-17 21:00 | 12.02 | 11.97
2017-12-17 21:30 | 11.15 | 11.12
2017-12-17 22:00 | 10.47 | 10.44
2017-12-17 22:30 | 9.95 | 9.93
2017-12-17 23:00 | 9.56 | 9.55
2017-12-17 23:30 | 8.32 | 8.31
2017-12-18 | 7.3 | 7.29
2017-12-18 00:30 | 6.75 | 6.73
2017-12-18 01:00 | 6.49 | 6.47
2017-12-18 01:30 | 6.11 | 6.1
2017-12-18 02:00 | 5.77 | 5.75
2017-12-18 02:30 | 5.75 | 5.73
2017-12-18 03:00 | 5.48 | 5.46
2017-12-18 03:30 | 5.53 | 5.52
2017-12-18 04:00 | 5.52 | 5.5
2017-12-18 04:30 | 5.48 | 5.47
2017-12-18 05:00 | 5.4 | 5.38
2017-12-18 05:30 | 5.55 | 5.54
2017-12-18 06:00 | 5.88 | 5.87
2017-12-18 06:30 | 5.85 | 5.83
2017-12-18 07:00 | 5.85 | 5.84
2017-12-18 07:30 | 6.02 | 6.01
2017-12-18 08:00 | 5.82 | 5.8
2017-12-18 08:30 | 5.89 | 5.87
2017-12-18 09:00 | 6.25 | 6.22
2017-12-18 09:30 | 6.36 | 6.33
2017-12-18 10:00 | 7 | 6.96
2017-12-18 10:30 | 7.79 | 7.73
2017-12-18 11:00 | 8.07 | 8.01
2017-12-18 11:30 | 7.92 | 7.85
2017-12-18 12:00 | 8.66 | 8.57
2017-12-18 12:30 | 8.53 | 8.42
2017-12-18 13:00 | 8.76 | 8.64
2017-12-18 13:30 | 9.27 | 9.13
2017-12-18 14:00 | 9.79 | 9.66
2017-12-18 14:30 | 10.11 | 9.96
2017-12-18 15:00 | 10.71 | 10.54
2017-12-18 15:30 | 11.41 | 11.26
2017-12-18 16:00 | 12.29 | 12.14
2017-12-18 16:30 | 12.84 | 12.71
2017-12-18 17:00 | 13.77 | 13.64
2017-12-18 17:30 | 14.55 | 14.41
2017-12-18 18:00 | 14.25 | 14.13
2017-12-18 18:30 | 14.14 | 14.05
2017-12-18 19:00 | 14.19 | 14.1
2017-12-18 19:30 | 14.02 | 13.92
2017-12-18 20:00 | 13.79 | 13.71
2017-12-18 20:30 | 13.55 | 13.47
2017-12-18 21:00 | 12.5 | 12.45
2017-12-18 21:30 | 11.38 | 11.35
2017-12-18 22:00 | 10.34 | 10.32
2017-12-18 22:30 | 9.78 | 9.76
2017-12-18 23:00 | 9.46 | 9.44
2017-12-18 23:30 | 8.24 | 8.22
2017-12-19 | 7.35 | 7.33
2017-12-19 00:30 | 6.5 | 6.49
2017-12-19 01:00 | 6.15 | 6.13
2017-12-19 01:30 | 5.78 | 5.77
2017-12-19 02:00 | 5.54 | 5.52
2017-12-19 02:30 | 5.35 | 5.33
2017-12-19 03:00 | 5.29 | 5.28
2017-12-19 03:30 | 5.17 | 5.16
2017-12-19 04:00 | 5.14 | 5.12
2017-12-19 04:30 | 5.16 | 5.14
2017-12-19 05:00 | 5 | 4.97
2017-12-19 05:30 | 5.38 | 5.35
2017-12-19 06:00 | 5.49 | 5.46
2017-12-19 06:30 | 5.58 | 5.57
2017-12-19 07:00 | 5.62 | 5.61
2017-12-19 07:30 | 5.49 | 5.47
2017-12-19 08:00 | 5.45 | 5.43
2017-12-19 08:30 | 5.09 | 5.07
2017-12-19 09:00 | 5.31 | 5.28
2017-12-19 09:30 | 5.47 | 5.43
2017-12-19 10:00 | 5.92 | 5.86
2017-12-19 10:30 | 7.29 | 7.23
2017-12-19 11:00 | 7.87 | 7.79
2017-12-19 11:30 | 8.65 | 8.55
2017-12-19 12:00 | 8.85 | 8.72
2017-12-19 12:30 | 8.9 | 8.74
2017-12-19 13:00 | 9.74 | 9.56
2017-12-19 13:30 | 10.55 | 10.34
2017-12-19 14:00 | 11.72 | 11.44
2017-12-19 14:30 | 12.57 | 12.32
2017-12-19 15:00 | 13.48 | 13.24
2017-12-19 15:30 | 14.46 | 14.24
2017-12-19 16:00 | 14.3 | 14.09
2017-12-19 16:30 | 15.12 | 14.92
2017-12-19 17:00 | 16.08 | 15.9
2017-12-19 17:30 | 15.47 | 15.31
2017-12-19 18:00 | 15.28 | 15.12
2017-12-19 18:30 | 15.03 | 14.9
2017-12-19 19:00 | 15.12 | 15
2017-12-19 19:30 | 14.96 | 14.82
2017-12-19 20:00 | 14.88 | 14.76
2017-12-19 20:30 | 14.49 | 14.38
2017-12-19 21:00 | 13.51 | 13.43
2017-12-19 21:30 | 12.26 | 12.2
2017-12-19 22:00 | 11.22 | 11.18
2017-12-19 22:30 | 10.44 | 10.42
2017-12-19 23:00 | 9.9 | 9.88
2017-12-19 23:30 | 8.73 | 8.71
2017-12-20 | 7.77 | 7.76
2017-12-20 00:30 | 7.11 | 7.1
2017-12-20 01:00 | 6.77 | 6.76
2017-12-20 01:30 | 6.33 | 6.32
2017-12-20 02:00 | 6.05 | 6.03
2017-12-20 02:30 | 5.82 | 5.81
2017-12-20 03:00 | 5.76 | 5.74
2017-12-20 03:30 | 5.65 | 5.63
2017-12-20 04:00 | 5.7 | 5.69
2017-12-20 04:30 | 5.67 | 5.65
2017-12-20 05:00 | 5.49 | 5.48
2017-12-20 05:30 | 5.57 | 5.55
2017-12-20 06:00 | 5.56 | 5.54
2017-12-20 06:30 | 5.61 | 5.59
2017-12-20 07:00 | 5.73 | 5.71
2017-12-20 07:30 | 5.78 | 5.76
2017-12-20 08:00 | 6.43 | 6.41
2017-12-20 08:30 | 6.63 | 6.6
2017-12-20 09:00 | 7.19 | 7.15
2017-12-20 09:30 | 6.81 | 6.75
2017-12-20 10:00 | 6.78 | 6.68
2017-12-20 10:30 | 7.37 | 7.25
2017-12-20 11:00 | 8.04 | 7.91
2017-12-20 11:30 | 8.69 | 8.52
2017-12-20 12:00 | 10.03 | 9.84
2017-12-20 12:30 | 10.55 | 10.33
2017-12-20 13:00 | 11.51 | 11.21
2017-12-20 13:30 | 12.22 | 11.93
2017-12-20 14:00 | 13.15 | 12.88
2017-12-20 14:30 | 14.01 | 13.72
2017-12-20 15:00 | 14.8 | 14.47
2017-12-20 15:30 | 15.59 | 15.26
2017-12-20 16:00 | 16.32 | 16.03
2017-12-20 16:30 | 17.02 | 16.74
2017-12-20 17:00 | 17.92 | 17.63
2017-12-20 17:30 | 18.27 | 18
2017-12-20 18:00 | 17.92 | 17.67
2017-12-20 18:30 | 17.45 | 17.24
2017-12-20 19:00 | 17.25 | 17.04
2017-12-20 19:30 | 16.79 | 16.58
2017-12-20 20:00 | 16.61 | 16.41
2017-12-20 20:30 | 16.24 | 16.07
2017-12-20 21:00 | 15.08 | 14.94
2017-12-20 21:30 | 13.67 | 13.56
2017-12-20 22:00 | 12.62 | 12.53
2017-12-20 22:30 | 11.73 | 11.67
2017-12-20 23:00 | 11.19 | 11.14
2017-12-20 23:30 | 9.69 | 9.65
2017-12-21 | 8.63 | 8.6
2017-12-21 00:30 | 7.8 | 7.77
2017-12-21 01:00 | 7.39 | 7.37
2017-12-21 01:30 | 6.89 | 6.88
2017-12-21 02:00 | 6.59 | 6.57
2017-12-21 02:30 | 6.3 | 6.28
2017-12-21 03:00 | 6.17 | 6.15
2017-12-21 03:30 | 6.12 | 6.1
2017-12-21 04:00 | 6.05 | 6.03
2017-12-21 04:30 | 6.06 | 6.04
2017-12-21 05:00 | 5.99 | 5.97
2017-12-21 05:30 | 6.01 | 5.99
2017-12-21 06:00 | 6.46 | 6.44
2017-12-21 06:30 | 6.59 | 6.58
2017-12-21 07:00 | 6.8 | 6.79
2017-12-21 07:30 | 7 | 6.98
2017-12-21 08:00 | 6.66 | 6.63
2017-12-21 08:30 | 6.58 | 6.54
2017-12-21 09:00 | 7.16 | 7.1
2017-12-21 09:30 | 7.66 | 7.57
2017-12-21 10:00 | 8.16 | 8.05
2017-12-21 10:30 | 8.97 | 8.83
2017-12-21 11:00 | 10.27 | 10.12
2017-12-21 11:30 | 11.08 | 10.9
2017-12-21 12:00 | 12.01 | 11.81
2017-12-21 12:30 | 12.01 | 11.76
2017-12-21 13:00 | 13.28 | 13.02
2017-12-21 13:30 | 12.99 | 12.76
2017-12-21 14:00 | 14.22 | 13.99
2017-12-21 14:30 | 14.57 | 14.33
2017-12-21 15:00 | 14.41 | 14.15
2017-12-21 15:30 | 15.25 | 14.99
2017-12-21 16:00 | 15.18 | 14.9
2017-12-21 16:30 | 14.92 | 14.69
2017-12-21 17:00 | 15.22 | 15.01
2017-12-21 17:30 | 15.17 | 14.99
2017-12-21 18:00 | 15.21 | 15.04
2017-12-21 18:30 | 14.97 | 14.82
2017-12-21 19:00 | 15.17 | 15.02
2017-12-21 19:30 | 15.13 | 14.96
2017-12-21 20:00 | 15.05 | 14.89
2017-12-21 20:30 | 14.76 | 14.61
2017-12-21 21:00 | 14.15 | 14.02
2017-12-21 21:30 | 13.04 | 12.94
2017-12-21 22:00 | 11.66 | 11.59
2017-12-21 22:30 | 11.1 | 11.06
2017-12-21 23:00 | 10.48 | 10.45
2017-12-21 23:30 | 9.21 | 9.18
2017-12-22 | 8.26 | 8.23
2017-12-22 00:30 | 7.41 | 7.39
2017-12-22 01:00 | 7.09 | 7.08
2017-12-22 01:30 | 6.57 | 6.55
2017-12-22 02:00 | 6.25 | 6.23
2017-12-22 02:30 | 6.2 | 6.18
2017-12-22 03:00 | 5.95 | 5.93
2017-12-22 03:30 | 5.82 | 5.79
2017-12-22 04:00 | 5.71 | 5.68
2017-12-22 04:30 | 5.84 | 5.82
2017-12-22 05:00 | 5.79 | 5.76
2017-12-22 05:30 | 5.69 | 5.66
2017-12-22 06:00 | 5.76 | 5.74
2017-12-22 06:30 | 5.76 | 5.73
2017-12-22 07:00 | 6.14 | 6.12
2017-12-22 07:30 | 6.45 | 6.42
2017-12-22 08:00 | 6.25 | 6.22
2017-12-22 08:30 | 6.51 | 6.47
2017-12-22 09:00 | 6.74 | 6.7
2017-12-22 09:30 | 6.89 | 6.85
2017-12-22 10:00 | 6.2 | 6.14
2017-12-22 10:30 | 6.54 | 6.48
2017-12-22 11:00 | 6.41 | 6.35
2017-12-22 11:30 | 6.57 | 6.48
2017-12-22 12:00 | 8.48 | 8.4
2017-12-22 12:30 | 8.69 | 8.58
2017-12-22 13:00 | 7.63 | 7.48
2017-12-22 13:30 | 8.55 | 8.39
2017-12-22 14:00 | 9.97 | 9.82
2017-12-22 14:30 | 11.92 | 11.78
2017-12-22 15:00 | 11.94 | 11.8
2017-12-22 15:30 | 12.69 | 12.56
2017-12-22 16:00 | 12.94 | 12.82
2017-12-22 16:30 | 13.32 | 13.21
2017-12-22 17:00 | 13.26 | 13.16
2017-12-22 17:30 | 12.59 | 12.52
2017-12-22 18:00 | 12.03 | 11.97
2017-12-22 18:30 | 11.81 | 11.75
2017-12-22 19:00 | 12.25 | 12.17
2017-12-22 19:30 | 12.4 | 12.31
2017-12-22 20:00 | 12.36 | 12.28
2017-12-22 20:30 | 11.98 | 11.92
2017-12-22 21:00 | 11.49 | 11.43
2017-12-22 21:30 | 10.87 | 10.82
2017-12-22 22:00 | 10.4 | 10.36
2017-12-22 22:30 | 9.95 | 9.92
2017-12-22 23:00 | 9.77 | 9.74
2017-12-22 23:30 | 8.74 | 8.71
2017-12-23 | 7.83 | 7.81
2017-12-23 00:30 | 7.23 | 7.21
2017-12-23 01:00 | 6.94 | 6.92
2017-12-23 01:30 | 6.53 | 6.51
2017-12-23 02:00 | 6.17 | 6.14
2017-12-23 02:30 | 5.86 | 5.83
2017-12-23 03:00 | 5.69 | 5.67
2017-12-23 03:30 | 5.63 | 5.61
2017-12-23 04:00 | 5.5 | 5.48
2017-12-23 04:30 | 5.41 | 5.39
2017-12-23 05:00 | 5.26 | 5.23
2017-12-23 05:30 | 5.11 | 5.09
2017-12-23 06:00 | 5.1 | 5.07
2017-12-23 06:30 | 5.36 | 5.33
2017-12-23 07:00 | 5.33 | 5.3
2017-12-23 07:30 | 5.35 | 5.32
2017-12-23 08:00 | 5.72 | 5.69
2017-12-23 08:30 | 6.38 | 6.34
2017-12-23 09:00 | 6.74 | 6.69
2017-12-23 09:30 | 7.15 | 7.1
2017-12-23 10:00 | 8 | 7.93
2017-12-23 10:30 | 7.76 | 7.66
2017-12-23 11:00 | 8.51 | 8.39
2017-12-23 11:30 | 8.77 | 8.61
2017-12-23 12:00 | 9.6 | 9.42
2017-12-23 12:30 | 10.37 | 10.18
2017-12-23 13:00 | 11.01 | 10.79
2017-12-23 13:30 | 12.15 | 11.9
2017-12-23 14:00 | 14.06 | 13.84
2017-12-23 14:30 | 13.1 | 12.85
2017-12-23 15:00 | 13.93 | 13.71
2017-12-23 15:30 | 13.94 | 13.72
2017-12-23 16:00 | 14.37 | 14.16
2017-12-23 16:30 | 15.08 | 14.87
2017-12-23 17:00 | 15.65 | 15.43
2017-12-23 17:30 | 15.73 | 15.52
2017-12-23 18:00 | 15.59 | 15.39
2017-12-23 18:30 | 15.15 | 14.98
2017-12-23 19:00 | 14.9 | 14.75
2017-12-23 19:30 | 14.78 | 14.62
2017-12-23 20:00 | 14.64 | 14.5
2017-12-23 20:30 | 14.02 | 13.9
2017-12-23 21:00 | 13.26 | 13.14
2017-12-23 21:30 | 12.49 | 12.4
2017-12-23 22:00 | 11.63 | 11.56
2017-12-23 22:30 | 11.31 | 11.25
2017-12-23 23:00 | 10.79 | 10.76
2017-12-23 23:30 | 9.49 | 9.46
2017-12-24 | 8.38 | 8.36
2017-12-24 00:30 | 7.68 | 7.65
2017-12-24 01:00 | 7.28 | 7.26
2017-12-24 01:30 | 6.79 | 6.76
2017-12-24 02:00 | 6.42 | 6.39
2017-12-24 02:30 | 6.2 | 6.17
2017-12-24 03:00 | 6.04 | 6.02
2017-12-24 03:30 | 5.8 | 5.78
2017-12-24 04:00 | 5.76 | 5.74
2017-12-24 04:30 | 5.68 | 5.66
2017-12-24 05:00 | 5.3 | 5.27
2017-12-24 05:30 | 5.19 | 5.17
2017-12-24 06:00 | 5.16 | 5.13
2017-12-24 06:30 | 5.27 | 5.24
2017-12-24 07:00 | 5.43 | 5.4
2017-12-24 07:30 | 5.81 | 5.77
2017-12-24 08:00 | 6.19 | 6.15
2017-12-24 08:30 | 6.68 | 6.64
2017-12-24 09:00 | 7.2 | 7.15
2017-12-24 09:30 | 7.75 | 7.68
2017-12-24 10:00 | 8.4 | 8.29
2017-12-24 10:30 | 8.94 | 8.81
2017-12-24 11:00 | 9.65 | 9.5
2017-12-24 11:30 | 10.49 | 10.31
2017-12-24 12:00 | 11.32 | 11.1
2017-12-24 12:30 | 12.04 | 11.79
2017-12-24 13:00 | 12.81 | 12.55
2017-12-24 13:30 | 13.55 | 13.29
2017-12-24 14:00 | 14.3 | 14.04
2017-12-24 14:30 | 15.14 | 14.86
2017-12-24 15:00 | 16.27 | 15.94
2017-12-24 15:30 | 16.99 | 16.67
2017-12-24 16:00 | 17.47 | 17.16
2017-12-24 16:30 | 17.97 | 17.68
2017-12-24 17:00 | 18.41 | 18.14
2017-12-24 17:30 | 18.47 | 18.2
2017-12-24 18:00 | 18.05 | 17.8
2017-12-24 18:30 | 17.1 | 16.88
2017-12-24 19:00 | 16.49 | 16.29
2017-12-24 19:30 | 16.08 | 15.85
2017-12-24 20:00 | 15.68 | 15.49
2017-12-24 20:30 | 15.29 | 15.11
2017-12-24 21:00 | 14.49 | 14.33
2017-12-24 21:30 | 13.79 | 13.66
2017-12-24 22:00 | 13.1 | 12.98
2017-12-24 22:30 | 12.43 | 12.34
2017-12-24 23:00 | 11.93 | 11.86
2017-12-24 23:30 | 10.45 | 10.39
2017-12-25 | 9.28 | 9.24
2017-12-25 00:30 | 8.45 | 8.42
2017-12-25 01:00 | 7.81 | 7.78
2017-12-25 01:30 | 7.36 | 7.33
2017-12-25 02:00 | 6.93 | 6.9
2017-12-25 02:30 | 6.46 | 6.43
2017-12-25 03:00 | 6.26 | 6.23
2017-12-25 03:30 | 6.06 | 6.03
2017-12-25 04:00 | 5.96 | 5.94
2017-12-25 04:30 | 6.01 | 5.98
2017-12-25 05:00 | 5.88 | 5.86
2017-12-25 05:30 | 5.68 | 5.66
2017-12-25 06:00 | 5.76 | 5.73
2017-12-25 06:30 | 5.97 | 5.95
2017-12-25 07:00 | 6.51 | 6.49
2017-12-25 07:30 | 7.14 | 7.11
2017-12-25 08:00 | 7.8 | 7.77
2017-12-25 08:30 | 8.24 | 8.21
2017-12-25 09:00 | 8.42 | 8.36
2017-12-25 09:30 | 9.06 | 8.97
2017-12-25 10:00 | 9.47 | 9.36
2017-12-25 10:30 | 9.86 | 9.74
2017-12-25 11:00 | 10.3 | 10.18
2017-12-25 11:30 | 10.58 | 10.45
2017-12-25 12:00 | 10.87 | 10.73
2017-12-25 12:30 | 11.4 | 11.23
2017-12-25 13:00 | 11.72 | 11.54
2017-12-25 13:30 | 11.92 | 11.73
2017-12-25 14:00 | 12.31 | 12.12
2017-12-25 14:30 | 12.45 | 12.27
2017-12-25 15:00 | 13.16 | 12.97
2017-12-25 15:30 | 14.14 | 13.96
2017-12-25 16:00 | 15.35 | 15.18
2017-12-25 16:30 | 15.31 | 15.15
2017-12-25 17:00 | 14.76 | 14.61
2017-12-25 17:30 | 14.27 | 14.12
2017-12-25 18:00 | 14.02 | 13.87
2017-12-25 18:30 | 13.9 | 13.76
2017-12-25 19:00 | 13.07 | 12.95
2017-12-25 19:30 | 12.28 | 12.18
2017-12-25 20:00 | 11.74 | 11.66
2017-12-25 20:30 | 11.34 | 11.28
2017-12-25 21:00 | 10.62 | 10.57
2017-12-25 21:30 | 10.04 | 10
2017-12-25 22:00 | 9.64 | 9.61
2017-12-25 22:30 | 9.41 | 9.38
2017-12-25 23:00 | 8.74 | 8.72
2017-12-25 23:30 | 7.54 | 7.52
2017-12-26 | 6.84 | 6.83
2017-12-26 00:30 | 6.29 | 6.27
2017-12-26 01:00 | 6.07 | 6.05
2017-12-26 01:30 | 5.73 | 5.71
2017-12-26 02:00 | 5.33 | 5.31
2017-12-26 02:30 | 5.21 | 5.18
2017-12-26 03:00 | 5.08 | 5.06
2017-12-26 03:30 | 5.04 | 5.02
2017-12-26 04:00 | 5.02 | 5
2017-12-26 04:30 | 5.11 | 5.09
2017-12-26 05:00 | 4.88 | 4.86
2017-12-26 05:30 | 4.68 | 4.65
2017-12-26 06:00 | 4.77 | 4.74
2017-12-26 06:30 | 4.57 | 4.54
2017-12-26 07:00 | 4.36 | 4.34
2017-12-26 07:30 | 4.57 | 4.54
2017-12-26 08:00 | 4.69 | 4.66
2017-12-26 08:30 | 4.64 | 4.6
2017-12-26 09:00 | 6.23 | 6.2
2017-12-26 09:30 | 5.88 | 5.84
2017-12-26 10:00 | 5.04 | 4.99
2017-12-26 10:30 | 6.07 | 6.03
2017-12-26 11:00 | 7.23 | 7.19
2017-12-26 11:30 | 7.87 | 7.82
2017-12-26 12:00 | 7.48 | 7.43
2017-12-26 12:30 | 7.51 | 7.47
2017-12-26 13:00 | 7.69 | 7.64
2017-12-26 13:30 | 7.83 | 7.76
2017-12-26 14:00 | 8.33 | 8.25
2017-12-26 14:30 | 9.38 | 9.31
2017-12-26 15:00 | 10.7 | 10.63
2017-12-26 15:30 | 11.47 | 11.41
2017-12-26 16:00 | 10.6 | 10.54
2017-12-26 16:30 | 10.72 | 10.67
2017-12-26 17:00 | 11.29 | 11.25
2017-12-26 17:30 | 11.27 | 11.24
2017-12-26 18:00 | 11.16 | 11.13
2017-12-26 18:30 | 12.29 | 12.26
2017-12-26 19:00 | 12.83 | 12.79
2017-12-26 19:30 | 11.88 | 11.84
2017-12-26 20:00 | 11.31 | 11.27
2017-12-26 20:30 | 10.86 | 10.84
2017-12-26 21:00 | 10.1 | 10.08
2017-12-26 21:30 | 9.33 | 9.32
2017-12-26 22:00 | 8.92 | 8.9
2017-12-26 22:30 | 8.64 | 8.63
2017-12-26 23:00 | 8.35 | 8.34
2017-12-26 23:30 | 7.33 | 7.32
2017-12-27 | 6.59 | 6.57
2017-12-27 00:30 | 6.04 | 6.03
2017-12-27 01:00 | 5.85 | 5.84
2017-12-27 01:30 | 5.5 | 5.48
2017-12-27 02:00 | 5.26 | 5.25
2017-12-27 02:30 | 5.09 | 5.07
2017-12-27 03:00 | 5.1 | 5.08
2017-12-27 03:30 | 4.94 | 4.92
2017-12-27 04:00 | 4.98 | 4.96
2017-12-27 04:30 | 4.97 | 4.95
2017-12-27 05:00 | 4.78 | 4.76
2017-12-27 05:30 | 4.77 | 4.74
2017-12-27 06:00 | 4.75 | 4.71
2017-12-27 06:30 | 4.71 | 4.68
2017-12-27 07:00 | 4.66 | 4.64
2017-12-27 07:30 | 4.66 | 4.62
2017-12-27 08:00 | 4.67 | 4.63
2017-12-27 08:30 | 4.74 | 4.69
2017-12-27 09:00 | 5.41 | 5.36
2017-12-27 09:30 | 6.79 | 6.73
2017-12-27 10:00 | 7.13 | 7.07
2017-12-27 10:30 | 6.59 | 6.52
2017-12-27 11:00 | 6.49 | 6.41
2017-12-27 11:30 | 7.47 | 7.38
2017-12-27 12:00 | 7.73 | 7.63
2017-12-27 12:30 | 9.06 | 8.97
2017-12-27 13:00 | 9.67 | 9.58
2017-12-27 13:30 | 10.12 | 10.03
2017-12-27 14:00 | 10.4 | 10.3
2017-12-27 14:30 | 10.97 | 10.87
2017-12-27 15:00 | 11 | 10.93
2017-12-27 15:30 | 9.55 | 9.47
2017-12-27 16:00 | 9.83 | 9.75
2017-12-27 16:30 | 11.37 | 11.3
2017-12-27 17:00 | 11.72 | 11.67
2017-12-27 17:30 | 11.27 | 11.23
2017-12-27 18:00 | 11.2 | 11.16
2017-12-27 18:30 | 11.24 | 11.21
2017-12-27 19:00 | 11.6 | 11.57
2017-12-27 19:30 | 11.78 | 11.72
2017-12-27 20:00 | 11.84 | 11.79
2017-12-27 20:30 | 11.65 | 11.6
2017-12-27 21:00 | 10.97 | 10.94
2017-12-27 21:30 | 10.15 | 10.12
2017-12-27 22:00 | 9.37 | 9.35
2017-12-27 22:30 | 8.91 | 8.89
2017-12-27 23:00 | 8.65 | 8.63
2017-12-27 23:30 | 7.55 | 7.53
2017-12-28 | 6.64 | 6.62
2017-12-28 00:30 | 6.18 | 6.16
2017-12-28 01:00 | 5.83 | 5.81
2017-12-28 01:30 | 5.42 | 5.4
2017-12-28 02:00 | 5.15 | 5.14
2017-12-28 02:30 | 4.97 | 4.96
2017-12-28 03:00 | 4.82 | 4.8
2017-12-28 03:30 | 4.83 | 4.81
2017-12-28 04:00 | 4.74 | 4.72
2017-12-28 04:30 | 4.79 | 4.77
2017-12-28 05:00 | 4.62 | 4.59
2017-12-28 05:30 | 4.63 | 4.58
2017-12-28 06:00 | 4.59 | 4.53
2017-12-28 06:30 | 4.4 | 4.35
2017-12-28 07:00 | 4.49 | 4.46
2017-12-28 07:30 | 4.46 | 4.43
2017-12-28 08:00 | 4.57 | 4.53
2017-12-28 08:30 | 4.69 | 4.64
2017-12-28 09:00 | 5.36 | 5.31
2017-12-28 09:30 | 6.09 | 6.05
2017-12-28 10:00 | 6.06 | 6.01
2017-12-28 10:30 | 6.13 | 6.07
2017-12-28 11:00 | 5.82 | 5.74
2017-12-28 11:30 | 6.85 | 6.77
2017-12-28 12:00 | 8.03 | 7.96
2017-12-28 12:30 | 8.6 | 8.52
2017-12-28 13:00 | 9.96 | 9.89
2017-12-28 13:30 | 10.23 | 10.16
2017-12-28 14:00 | 10.13 | 10.07
2017-12-28 14:30 | 9.67 | 9.61
2017-12-28 15:00 | 9.7 | 9.63
2017-12-28 15:30 | 9.53 | 9.46
2017-12-28 16:00 | 9.94 | 9.88
2017-12-28 16:30 | 9.96 | 9.91
2017-12-28 17:00 | 10.5 | 10.45
2017-12-28 17:30 | 11.02 | 10.97
2017-12-28 18:00 | 11.38 | 11.33
2017-12-28 18:30 | 11.53 | 11.49
2017-12-28 19:00 | 11.77 | 11.72
2017-12-28 19:30 | 12.16 | 12.1
2017-12-28 20:00 | 12.37 | 12.32
2017-12-28 20:30 | 12.15 | 12.1
2017-12-28 21:00 | 11.4 | 11.36
2017-12-28 21:30 | 10.6 | 10.57
2017-12-28 22:00 | 9.95 | 9.93
2017-12-28 22:30 | 9.46 | 9.44
2017-12-28 23:00 | 9.11 | 9.1
2017-12-28 23:30 | 7.94 | 7.92
2017-12-29 | 7.13 | 7.11
2017-12-29 00:30 | 6.58 | 6.56
2017-12-29 01:00 | 6.25 | 6.23
2017-12-29 01:30 | 5.91 | 5.89
2017-12-29 02:00 | 5.7 | 5.68
2017-12-29 02:30 | 5.57 | 5.55
2017-12-29 03:00 | 5.3 | 5.28
2017-12-29 03:30 | 5.3 | 5.27
2017-12-29 04:00 | 5.23 | 5.21
2017-12-29 04:30 | 5.26 | 5.24
2017-12-29 05:00 | 5.15 | 5.13
2017-12-29 05:30 | 5.12 | 5.09
2017-12-29 06:00 | 5.22 | 5.19
2017-12-29 06:30 | 5.33 | 5.3
2017-12-29 07:00 | 4.97 | 4.94
2017-12-29 07:30 | 5.28 | 5.25
2017-12-29 08:00 | 4.79 | 4.76
2017-12-29 08:30 | 5.09 | 5.05
2017-12-29 09:00 | 5.64 | 5.59
2017-12-29 09:30 | 5.96 | 5.9
2017-12-29 10:00 | 6.31 | 6.24
2017-12-29 10:30 | 6.67 | 6.59
2017-12-29 11:00 | 7.63 | 7.54
2017-12-29 11:30 | 8.68 | 8.57
2017-12-29 12:00 | 7.88 | 7.75
2017-12-29 12:30 | 8.55 | 8.4
2017-12-29 13:00 | 9.69 | 9.54
2017-12-29 13:30 | 10.4 | 10.21
2017-12-29 14:00 | 12.62 | 12.46
2017-12-29 14:30 | 11.87 | 11.69
2017-12-29 15:00 | 12.02 | 11.84
2017-12-29 15:30 | 12.21 | 12.03
2017-12-29 16:00 | 12.69 | 12.51
2017-12-29 16:30 | 13.18 | 13.01
2017-12-29 17:00 | 14.53 | 14.38
2017-12-29 17:30 | 14.27 | 14.12
2017-12-29 18:00 | 14.28 | 14.14
2017-12-29 18:30 | 13.96 | 13.83
2017-12-29 19:00 | 13.79 | 13.68
2017-12-29 19:30 | 14.02 | 13.89
2017-12-29 20:00 | 13.96 | 13.84
2017-12-29 20:30 | 13.62 | 13.51
2017-12-29 21:00 | 12.78 | 12.7
2017-12-29 21:30 | 11.92 | 11.85
2017-12-29 22:00 | 11.15 | 11.09
2017-12-29 22:30 | 10.59 | 10.55
2017-12-29 23:00 | 10.15 | 10.13
2017-12-29 23:30 | 8.86 | 8.85
2017-12-30 | 8.03 | 8.01
2017-12-30 00:30 | 7.35 | 7.33
2017-12-30 01:00 | 7.06 | 7.05
2017-12-30 01:30 | 6.64 | 6.62
2017-12-30 02:00 | 6.23 | 6.21
2017-12-30 02:30 | 6.06 | 6.05
2017-12-30 03:00 | 5.92 | 5.9
2017-12-30 03:30 | 5.73 | 5.7
2017-12-30 04:00 | 5.63 | 5.61
2017-12-30 04:30 | 5.63 | 5.61
2017-12-30 05:00 | 5.32 | 5.3
2017-12-30 05:30 | 5.19 | 5.17
2017-12-30 06:00 | 5.16 | 5.13
2017-12-30 06:30 | 5.12 | 5.09
2017-12-30 07:00 | 5.03 | 5
2017-12-30 07:30 | 6.04 | 6.01
2017-12-30 08:00 | 5.63 | 5.59
2017-12-30 08:30 | 6.39 | 6.34
2017-12-30 09:00 | 6.66 | 6.61
2017-12-30 09:30 | 7.24 | 7.18
2017-12-30 10:00 | 8.67 | 8.59
2017-12-30 10:30 | 9.54 | 9.46
2017-12-30 11:00 | 9.5 | 9.4
2017-12-30 11:30 | 10.41 | 10.29
2017-12-30 12:00 | 11.11 | 10.98
2017-12-30 12:30 | 12.22 | 12.09
2017-12-30 13:00 | 11.66 | 11.53
2017-12-30 13:30 | 10.25 | 10.08
2017-12-30 14:00 | 11.95 | 11.77
2017-12-30 14:30 | 12.02 | 11.84
2017-12-30 15:00 | 12.57 | 12.38
2017-12-30 15:30 | 13.53 | 13.33
2017-12-30 16:00 | 14.82 | 14.61
2017-12-30 16:30 | 15.66 | 15.44
2017-12-30 17:00 | 16.52 | 16.32
2017-12-30 17:30 | 16.59 | 16.4
2017-12-30 18:00 | 16.49 | 16.3
2017-12-30 18:30 | 16.47 | 16.29
2017-12-30 19:00 | 16.63 | 16.44
2017-12-30 19:30 | 16.63 | 16.42
2017-12-30 20:00 | 16.43 | 16.23
2017-12-30 20:30 | 15.91 | 15.73
2017-12-30 21:00 | 14.88 | 14.73
2017-12-30 21:30 | 13.97 | 13.85
2017-12-30 22:00 | 13.08 | 12.97
2017-12-30 22:30 | 12.47 | 12.37
2017-12-30 23:00 | 11.69 | 11.62
2017-12-30 23:30 | 10.4 | 10.34
2017-12-31 | 9.3 | 9.25
2017-12-31 00:30 | 8.59 | 8.55
2017-12-31 01:00 | 8.06 | 8.04
2017-12-31 01:30 | 7.69 | 7.66
2017-12-31 02:00 | 7.31 | 7.28
2017-12-31 02:30 | 7.2 | 7.17
2017-12-31 03:00 | 6.97 | 6.94
2017-12-31 03:30 | 6.87 | 6.84
2017-12-31 04:00 | 6.81 | 6.79
2017-12-31 04:30 | 6.72 | 6.69
2017-12-31 05:00 | 6.44 | 6.41
2017-12-31 05:30 | 6.07 | 6.05
2017-12-31 06:00 | 6.09 | 6.06
2017-12-31 06:30 | 6.01 | 5.99
2017-12-31 07:00 | 5.86 | 5.83
2017-12-31 07:30 | 5.91 | 5.87
2017-12-31 08:00 | 6.38 | 6.34
2017-12-31 08:30 | 7.24 | 7.19
2017-12-31 09:00 | 7.99 | 7.92
2017-12-31 09:30 | 9.19 | 9.09
2017-12-31 10:00 | 10.85 | 10.71
2017-12-31 10:30 | 11.33 | 11.14
2017-12-31 11:00 | 12.58 | 12.37
2017-12-31 11:30 | 14.78 | 14.56
2017-12-31 12:00 | 15.15 | 14.9
2017-12-31 12:30 | 15.1 | 14.82
2017-12-31 13:00 | 16.22 | 15.94
2017-12-31 13:30 | 18.24 | 17.97
2017-12-31 14:00 | 17.31 | 17.07
2017-12-31 14:30 | 16.25 | 16.05
2017-12-31 15:00 | 16.34 | 16.19
2017-12-31 15:30 | 15.02 | 14.84
2017-12-31 16:00 | 13.74 | 13.59
2017-12-31 16:30 | 13.34 | 13.21
2017-12-31 17:00 | 13.63 | 13.51
2017-12-31 17:30 | 13.39 | 13.27
2017-12-31 18:00 | 12.9 | 12.78
2017-12-31 18:30 | 12.82 | 12.72
2017-12-31 19:00 | 12.41 | 12.33
2017-12-31 19:30 | 12.13 | 12.03
2017-12-31 20:00 | 11.93 | 11.84
2017-12-31 20:30 | 11.52 | 11.44
2017-12-31 21:00 | 10.8 | 10.73
2017-12-31 21:30 | 10.25 | 10.2
2017-12-31 22:00 | 9.93 | 9.88
2017-12-31 22:30 | 10.03 | 9.99
2017-12-31 23:00 | 9.89 | 9.86
2017-12-31 23:30 | 8.95 | 8.92
2018-01-01 | 8.26 | 8.24
2018-01-01 00:30 | 7.65 | 7.62
2018-01-01 01:00 | 7.4 | 7.37
2018-01-01 01:30 | 6.98 | 6.95
2018-01-01 02:00 | 6.64 | 6.61
2018-01-01 02:30 | 6.36 | 6.33
2018-01-01 03:00 | 6.21 | 6.19
2018-01-01 03:30 | 6.1 | 6.07
2018-01-01 04:00 | 5.91 | 5.89
2018-01-01 04:30 | 5.9 | 5.87
2018-01-01 05:00 | 5.71 | 5.69
2018-01-01 05:30 | 5.58 | 5.56
2018-01-01 06:00 | 5.5 | 5.48
2018-01-01 06:30 | 5.33 | 5.31
2018-01-01 07:00 | 5.52 | 5.5
2018-01-01 07:30 | 5.55 | 5.53
2018-01-01 08:00 | 5.85 | 5.82
2018-01-01 08:30 | 6.61 | 6.58
2018-01-01 09:00 | 6.93 | 6.89
2018-01-01 09:30 | 8.23 | 8.19
2018-01-01 10:00 | 8.9 | 8.84
2018-01-01 10:30 | 10.43 | 10.36
2018-01-01 11:00 | 11.02 | 10.94
2018-01-01 11:30 | 10.49 | 10.37
2018-01-01 12:00 | 10.97 | 10.83
2018-01-01 12:30 | 13.07 | 12.92
2018-01-01 13:00 | 13.64 | 13.47
2018-01-01 13:30 | 14.44 | 14.26
2018-01-01 14:00 | 14.62 | 14.43
2018-01-01 14:30 | 15.43 | 15.22
2018-01-01 15:00 | 15.3 | 15.06
2018-01-01 15:30 | 16.43 | 16.19
2018-01-01 16:00 | 17.26 | 17.01
2018-01-01 16:30 | 17.77 | 17.52
2018-01-01 17:00 | 18.43 | 18.2
2018-01-01 17:30 | 18.13 | 17.91
2018-01-01 18:00 | 16.85 | 16.65
2018-01-01 18:30 | 15.24 | 15.11
2018-01-01 19:00 | 15.21 | 15.09
2018-01-01 19:30 | 14.85 | 14.71
2018-01-01 20:00 | 14.33 | 14.21
2018-01-01 20:30 | 13.76 | 13.67
2018-01-01 21:00 | 12.66 | 12.58
2018-01-01 21:30 | 11.6 | 11.55
2018-01-01 22:00 | 10.68 | 10.64
2018-01-01 22:30 | 10.18 | 10.16
2018-01-01 23:00 | 9.7 | 9.68
2018-01-01 23:30 | 8.55 | 8.53
2018-01-02 | 7.64 | 7.62
2018-01-02 00:30 | 7.08 | 7.06
2018-01-02 01:00 | 6.83 | 6.82
2018-01-02 01:30 | 6.48 | 6.46
2018-01-02 02:00 | 6.12 | 6.1
2018-01-02 02:30 | 5.87 | 5.85
2018-01-02 03:00 | 5.79 | 5.77
2018-01-02 03:30 | 5.78 | 5.76
2018-01-02 04:00 | 5.65 | 5.63
2018-01-02 04:30 | 5.75 | 5.73
2018-01-02 05:00 | 5.62 | 5.6
2018-01-02 05:30 | 5.48 | 5.45
2018-01-02 06:00 | 5.56 | 5.54
2018-01-02 06:30 | 5.6 | 5.58
2018-01-02 07:00 | 5.67 | 5.65
2018-01-02 07:30 | 5.92 | 5.9
2018-01-02 08:00 | 6.29 | 6.27
2018-01-02 08:30 | 6.6 | 6.56
2018-01-02 09:00 | 6.85 | 6.81
2018-01-02 09:30 | 6.83 | 6.77
2018-01-02 10:00 | 7.27 | 7.22
2018-01-02 10:30 | 8.22 | 8.16
2018-01-02 11:00 | 8.83 | 8.76
2018-01-02 11:30 | 9.49 | 9.4
2018-01-02 12:00 | 9.31 | 9.2
2018-01-02 12:30 | 9.72 | 9.59
2018-01-02 13:00 | 10.16 | 10.01
2018-01-02 13:30 | 11.16 | 10.99
2018-01-02 14:00 | 11.31 | 11.11
2018-01-02 14:30 | 13.21 | 13.02
2018-01-02 15:00 | 13.2 | 12.98
2018-01-02 15:30 | 13.9 | 13.7
2018-01-02 16:00 | 12.85 | 12.65
2018-01-02 16:30 | 13.08 | 12.92
2018-01-02 17:00 | 13.25 | 13.12
2018-01-02 17:30 | 13.71 | 13.6
2018-01-02 18:00 | 13.91 | 13.8
2018-01-02 18:30 | 14.01 | 13.91
2018-01-02 19:00 | 13.92 | 13.83
2018-01-02 19:30 | 13.21 | 13.13
2018-01-02 20:00 | 12.85 | 12.79
2018-01-02 20:30 | 12.43 | 12.37
2018-01-02 21:00 | 11.59 | 11.55
2018-01-02 21:30 | 10.64 | 10.61
2018-01-02 22:00 | 9.92 | 9.9
2018-01-02 22:30 | 9.51 | 9.5
2018-01-02 23:00 | 9.12 | 9.1
2018-01-02 23:30 | 8 | 7.98
2018-01-03 | 7.13 | 7.12
2018-01-03 00:30 | 6.54 | 6.52
2018-01-03 01:00 | 6.26 | 6.24
2018-01-03 01:30 | 6.02 | 6.01
2018-01-03 02:00 | 5.66 | 5.65
2018-01-03 02:30 | 5.55 | 5.53
2018-01-03 03:00 | 5.35 | 5.33
2018-01-03 03:30 | 5.29 | 5.27
2018-01-03 04:00 | 5.28 | 5.26
2018-01-03 04:30 | 5.39 | 5.37
2018-01-03 05:00 | 5.28 | 5.26
2018-01-03 05:30 | 5.25 | 5.23
2018-01-03 06:00 | 5.25 | 5.23
2018-01-03 06:30 | 5.07 | 5.05
2018-01-03 07:00 | 5.04 | 5.02
2018-01-03 07:30 | 5.18 | 5.15
2018-01-03 08:00 | 5.23 | 5.19
2018-01-03 08:30 | 5.36 | 5.31
2018-01-03 09:00 | 5.59 | 5.54
2018-01-03 09:30 | 5.77 | 5.72
2018-01-03 10:00 | 6.02 | 5.95
2018-01-03 10:30 | 6.49 | 6.4
2018-01-03 11:00 | 7.24 | 7.11
2018-01-03 11:30 | 8.11 | 7.93
2018-01-03 12:00 | 9.02 | 8.84
2018-01-03 12:30 | 9.75 | 9.57
2018-01-03 13:00 | 10.7 | 10.5
2018-01-03 13:30 | 13.14 | 12.94
2018-01-03 14:00 | 14.67 | 14.5
2018-01-03 14:30 | 13.74 | 13.59
2018-01-03 15:00 | 11.84 | 11.72
2018-01-03 15:30 | 9.72 | 9.58
2018-01-03 16:00 | 10.55 | 10.42
2018-01-03 16:30 | 11.37 | 11.26
2018-01-03 17:00 | 11.77 | 11.67
2018-01-03 17:30 | 12.68 | 12.59
2018-01-03 18:00 | 13.13 | 13.04
2018-01-03 18:30 | 13.36 | 13.28
2018-01-03 19:00 | 13.65 | 13.58
2018-01-03 19:30 | 13.68 | 13.59
2018-01-03 20:00 | 13.72 | 13.63
2018-01-03 20:30 | 13.38 | 13.3
2018-01-03 21:00 | 12.42 | 12.35
2018-01-03 21:30 | 11.42 | 11.38
2018-01-03 22:00 | 10.42 | 10.4
2018-01-03 22:30 | 9.85 | 9.83
2018-01-03 23:00 | 9.35 | 9.33
2018-01-03 23:30 | 8.12 | 8.1
2018-01-04 | 7.18 | 7.17
2018-01-04 00:30 | 6.54 | 6.52
2018-01-04 01:00 | 6.24 | 6.22
2018-01-04 01:30 | 5.89 | 5.87
2018-01-04 02:00 | 5.57 | 5.56
2018-01-04 02:30 | 5.33 | 5.31
2018-01-04 03:00 | 5.15 | 5.13
2018-01-04 03:30 | 5.17 | 5.15
2018-01-04 04:00 | 5.05 | 5.03
2018-01-04 04:30 | 5.1 | 5.08
2018-01-04 05:00 | 5.02 | 4.99
2018-01-04 05:30 | 4.92 | 4.89
2018-01-04 06:00 | 5.06 | 5.02
2018-01-04 06:30 | 5.03 | 5
2018-01-04 07:00 | 5.11 | 5.09
2018-01-04 07:30 | 5.26 | 5.24
2018-01-04 08:00 | 5.27 | 5.24
2018-01-04 08:30 | 5.35 | 5.32
2018-01-04 09:00 | 5.7 | 5.67
2018-01-04 09:30 | 6.48 | 6.44
2018-01-04 10:00 | 6.97 | 6.93
2018-01-04 10:30 | 7.75 | 7.7
2018-01-04 11:00 | 7.45 | 7.39
2018-01-04 11:30 | 7.41 | 7.33
2018-01-04 12:00 | 7.69 | 7.59
2018-01-04 12:30 | 8.46 | 8.36
2018-01-04 13:00 | 9.69 | 9.59
2018-01-04 13:30 | 10.29 | 10.18
2018-01-04 14:00 | 10.94 | 10.83
2018-01-04 14:30 | 11.35 | 11.25
2018-01-04 15:00 | 10.91 | 10.78
2018-01-04 15:30 | 10.86 | 10.73
2018-01-04 16:00 | 11.08 | 10.96
2018-01-04 16:30 | 11.92 | 11.81
2018-01-04 17:00 | 12.38 | 12.29
2018-01-04 17:30 | 12.74 | 12.65
2018-01-04 18:00 | 13.27 | 13.19
2018-01-04 18:30 | 13.24 | 13.17
2018-01-04 19:00 | 13.29 | 13.23
2018-01-04 19:30 | 13.49 | 13.4
2018-01-04 20:00 | 13.59 | 13.51
2018-01-04 20:30 | 12.92 | 12.86
2018-01-04 21:00 | 12.4 | 12.35
2018-01-04 21:30 | 11.64 | 11.6
2018-01-04 22:00 | 10.72 | 10.68
2018-01-04 22:30 | 9.76 | 9.75
2018-01-04 23:00 | 9.16 | 9.15
2018-01-04 23:30 | 8 | 7.98
2018-01-05 | 7.1 | 7.08
2018-01-05 00:30 | 6.6 | 6.59
2018-01-05 01:00 | 6.36 | 6.35
2018-01-05 01:30 | 5.96 | 5.94
2018-01-05 02:00 | 5.67 | 5.65
2018-01-05 02:30 | 5.49 | 5.47
2018-01-05 03:00 | 5.36 | 5.35
2018-01-05 03:30 | 5.4 | 5.38
2018-01-05 04:00 | 5.4 | 5.38
2018-01-05 04:30 | 5.45 | 5.43
2018-01-05 05:00 | 5.28 | 5.26
2018-01-05 05:30 | 5.22 | 5.2
2018-01-05 06:00 | 5.47 | 5.45
2018-01-05 06:30 | 5.75 | 5.74
2018-01-05 07:00 | 5.97 | 5.96
2018-01-05 07:30 | 5.8 | 5.79
2018-01-05 08:00 | 5.67 | 5.65
2018-01-05 08:30 | 6.07 | 6.05
2018-01-05 09:00 | 6.98 | 6.96
2018-01-05 09:30 | 7.84 | 7.81
2018-01-05 10:00 | 7.4 | 7.35
2018-01-05 10:30 | 6.88 | 6.8
2018-01-05 11:00 | 8.55 | 8.46
2018-01-05 11:30 | 8.49 | 8.39
2018-01-05 12:00 | 8.96 | 8.84
2018-01-05 12:30 | 9.51 | 9.37
2018-01-05 13:00 | 11.29 | 11.17
2018-01-05 13:30 | 11.06 | 10.93
2018-01-05 14:00 | 10.83 | 10.68
2018-01-05 14:30 | 11.09 | 10.92
2018-01-05 15:00 | 11.54 | 11.32
2018-01-05 15:30 | 11.54 | 11.38
2018-01-05 16:00 | 12.46 | 12.32
2018-01-05 16:30 | 12.56 | 12.43
2018-01-05 17:00 | 12.92 | 12.83
2018-01-05 17:30 | 12.18 | 12.1
2018-01-05 18:00 | 12.04 | 11.97
2018-01-05 18:30 | 12.25 | 12.19
2018-01-05 19:00 | 12.44 | 12.39
2018-01-05 19:30 | 12.67 | 12.59
2018-01-05 20:00 | 12.66 | 12.59
2018-01-05 20:30 | 12.25 | 12.2
2018-01-05 21:00 | 11.58 | 11.53
2018-01-05 21:30 | 10.84 | 10.8
2018-01-05 22:00 | 10.14 | 10.11
2018-01-05 22:30 | 9.68 | 9.66
2018-01-05 23:00 | 9.44 | 9.43
2018-01-05 23:30 | 8.2 | 8.18
2018-01-06 | 7.37 | 7.36
2018-01-06 00:30 | 6.72 | 6.71
2018-01-06 01:00 | 6.44 | 6.42
2018-01-06 01:30 | 6.07 | 6.05
2018-01-06 02:00 | 5.64 | 5.62
2018-01-06 02:30 | 5.46 | 5.44
2018-01-06 03:00 | 5.32 | 5.3
2018-01-06 03:30 | 5.37 | 5.35
2018-01-06 04:00 | 5.17 | 5.15
2018-01-06 04:30 | 5.22 | 5.2
2018-01-06 05:00 | 5.16 | 5.14
2018-01-06 05:30 | 5.01 | 4.99
2018-01-06 06:00 | 4.65 | 4.62
2018-01-06 06:30 | 4.61 | 4.59
2018-01-06 07:00 | 4.68 | 4.65
2018-01-06 07:30 | 5.07 | 5.04
2018-01-06 08:00 | 5.23 | 5.2
2018-01-06 08:30 | 5.55 | 5.5
2018-01-06 09:00 | 5.74 | 5.69
2018-01-06 09:30 | 6.03 | 5.97
2018-01-06 10:00 | 6.25 | 6.19
2018-01-06 10:30 | 6.77 | 6.69
2018-01-06 11:00 | 7.11 | 7.01
2018-01-06 11:30 | 7.53 | 7.4
2018-01-06 12:00 | 8.16 | 8.03
2018-01-06 12:30 | 9.04 | 8.89
2018-01-06 13:00 | 9.9 | 9.73
2018-01-06 13:30 | 10.78 | 10.61
2018-01-06 14:00 | 11.54 | 11.35
2018-01-06 14:30 | 11.89 | 11.69
2018-01-06 15:00 | 12.81 | 12.61
2018-01-06 15:30 | 13.24 | 13.04
2018-01-06 16:00 | 13.8 | 13.61
2018-01-06 16:30 | 14.64 | 14.46
2018-01-06 17:00 | 15.04 | 14.88
2018-01-06 17:30 | 15.34 | 15.19
2018-01-06 18:00 | 15.27 | 15.13
2018-01-06 18:30 | 14.88 | 14.74
2018-01-06 19:00 | 14.35 | 14.24
2018-01-06 19:30 | 14.24 | 14.11
2018-01-06 20:00 | 14.09 | 13.97
2018-01-06 20:30 | 13.51 | 13.41
2018-01-06 21:00 | 12.43 | 12.35
2018-01-06 21:30 | 11.52 | 11.47
2018-01-06 22:00 | 10.71 | 10.68
2018-01-06 22:30 | 10.27 | 10.24
2018-01-06 23:00 | 9.78 | 9.76
2018-01-06 23:30 | 8.52 | 8.5
2018-01-07 | 7.51 | 7.49
2018-01-07 00:30 | 6.92 | 6.9
2018-01-07 01:00 | 6.56 | 6.54
2018-01-07 01:30 | 6.2 | 6.18
2018-01-07 02:00 | 5.82 | 5.81
2018-01-07 02:30 | 5.5 | 5.48
2018-01-07 03:00 | 5.38 | 5.36
2018-01-07 03:30 | 5.39 | 5.37
2018-01-07 04:00 | 5.2 | 5.18
2018-01-07 04:30 | 5.18 | 5.17
2018-01-07 05:00 | 4.92 | 4.9
2018-01-07 05:30 | 4.79 | 4.75
2018-01-07 06:00 | 4.62 | 4.58
2018-01-07 06:30 | 4.56 | 4.53
2018-01-07 07:00 | 4.47 | 4.45
2018-01-07 07:30 | 4.74 | 4.71
2018-01-07 08:00 | 4.84 | 4.81
2018-01-07 08:30 | 5.35 | 5.31
2018-01-07 09:00 | 5.79 | 5.75
2018-01-07 09:30 | 6.08 | 6.03
2018-01-07 10:00 | 6.66 | 6.6
2018-01-07 10:30 | 7.14 | 7.05
2018-01-07 11:00 | 7.62 | 7.51
2018-01-07 11:30 | 8.32 | 8.19
2018-01-07 12:00 | 9.2 | 9.03
2018-01-07 12:30 | 10.15 | 9.97
2018-01-07 13:00 | 10.98 | 10.77
2018-01-07 13:30 | 11.89 | 11.67
2018-01-07 14:00 | 12.95 | 12.71
2018-01-07 14:30 | 13.76 | 13.51
2018-01-07 15:00 | 14.62 | 14.37
2018-01-07 15:30 | 15.47 | 15.22
2018-01-07 16:00 | 16.15 | 15.91
2018-01-07 16:30 | 16.89 | 16.65
2018-01-07 17:00 | 17.44 | 17.22
2018-01-07 17:30 | 17.64 | 17.44
2018-01-07 18:00 | 17.63 | 17.43
2018-01-07 18:30 | 17.06 | 16.89
2018-01-07 19:00 | 16.43 | 16.27
2018-01-07 19:30 | 15.92 | 15.74
2018-01-07 20:00 | 15.57 | 15.42
2018-01-07 20:30 | 14.87 | 14.75
2018-01-07 21:00 | 13.82 | 13.72
2018-01-07 21:30 | 12.75 | 12.68
2018-01-07 22:00 | 11.61 | 11.55
2018-01-07 22:30 | 10.79 | 10.75
2018-01-07 23:00 | 10.22 | 10.19
2018-01-07 23:30 | 8.95 | 8.92
2018-01-08 | 7.86 | 7.84
2018-01-08 00:30 | 7.16 | 7.14
2018-01-08 01:00 | 6.85 | 6.84
2018-01-08 01:30 | 6.41 | 6.39
2018-01-08 02:00 | 6.12 | 6.11
2018-01-08 02:30 | 5.76 | 5.75
2018-01-08 03:00 | 5.63 | 5.62
2018-01-08 03:30 | 5.71 | 5.69
2018-01-08 04:00 | 5.53 | 5.52
2018-01-08 04:30 | 5.54 | 5.52
2018-01-08 05:00 | 5.5 | 5.48
2018-01-08 05:30 | 5.54 | 5.53
2018-01-08 06:00 | 6.03 | 6.02
2018-01-08 06:30 | 6.12 | 6.11
2018-01-08 07:00 | 6.07 | 6.06
2018-01-08 07:30 | 5.97 | 5.96
2018-01-08 08:00 | 5.84 | 5.82
2018-01-08 08:30 | 5.94 | 5.91
2018-01-08 09:00 | 6.17 | 6.13
2018-01-08 09:30 | 7.07 | 7.03
2018-01-08 10:00 | 7.8 | 7.74
2018-01-08 10:30 | 8.12 | 8.04
2018-01-08 11:00 | 8.53 | 8.43
2018-01-08 11:30 | 9.19 | 9.07
2018-01-08 12:00 | 9.9 | 9.75
2018-01-08 12:30 | 10.61 | 10.46
2018-01-08 13:00 | 11.41 | 11.24
2018-01-08 13:30 | 12 | 11.79
2018-01-08 14:00 | 12.77 | 12.55
2018-01-08 14:30 | 13.41 | 13.23
2018-01-08 15:00 | 14.29 | 14.07
2018-01-08 15:30 | 15.41 | 15.19
2018-01-08 16:00 | 16.42 | 16.19
2018-01-08 16:30 | 17.23 | 16.96
2018-01-08 17:00 | 17.27 | 17.01
2018-01-08 17:30 | 17.82 | 17.56
2018-01-08 18:00 | 17.98 | 17.77
2018-01-08 18:30 | 17.74 | 17.55
2018-01-08 19:00 | 17.38 | 17.21
2018-01-08 19:30 | 17.29 | 17.08
2018-01-08 20:00 | 16.97 | 16.77
2018-01-08 20:30 | 16.32 | 16.16
2018-01-08 21:00 | 14.95 | 14.83
2018-01-08 21:30 | 13.6 | 13.51
2018-01-08 22:00 | 12.16 | 12.09
2018-01-08 22:30 | 11.21 | 11.16
2018-01-08 23:00 | 10.47 | 10.44
2018-01-08 23:30 | 9.17 | 9.15
2018-01-09 | 8.27 | 8.26
2018-01-09 00:30 | 7.59 | 7.57
2018-01-09 01:00 | 7.15 | 7.13
2018-01-09 01:30 | 6.75 | 6.74
2018-01-09 02:00 | 6.36 | 6.35
2018-01-09 02:30 | 6.08 | 6.07
2018-01-09 03:00 | 5.99 | 5.97
2018-01-09 03:30 | 5.94 | 5.92
2018-01-09 04:00 | 5.81 | 5.79
2018-01-09 04:30 | 5.81 | 5.79
2018-01-09 05:00 | 5.71 | 5.7
2018-01-09 05:30 | 5.57 | 5.55
2018-01-09 06:00 | 5.46 | 5.44
2018-01-09 06:30 | 5.58 | 5.57
2018-01-09 07:00 | 5.59 | 5.57
2018-01-09 07:30 | 6.54 | 6.53
2018-01-09 08:00 | 7.31 | 7.3
2018-01-09 08:30 | 7.4 | 7.38
2018-01-09 09:00 | 7.82 | 7.78
2018-01-09 09:30 | 7.93 | 7.88
2018-01-09 10:00 | 8.29 | 8.21
2018-01-09 10:30 | 8.52 | 8.42
2018-01-09 11:00 | 9.03 | 8.91
2018-01-09 11:30 | 10.3 | 10.16
2018-01-09 12:00 | 10.9 | 10.73
2018-01-09 12:30 | 11.53 | 11.35
2018-01-09 13:00 | 11.78 | 11.55
2018-01-09 13:30 | 12.38 | 12.15
2018-01-09 14:00 | 13.27 | 13.06
2018-01-09 14:30 | 14.16 | 13.92
2018-01-09 15:00 | 14.96 | 14.72
2018-01-09 15:30 | 15.98 | 15.68
2018-01-09 16:00 | 16.04 | 15.71
2018-01-09 16:30 | 16.45 | 16.2
2018-01-09 17:00 | 17.34 | 17.1
2018-01-09 17:30 | 17.89 | 17.66
2018-01-09 18:00 | 17.83 | 17.6
2018-01-09 18:30 | 17.5 | 17.3
2018-01-09 19:00 | 17.32 | 17.13
2018-01-09 19:30 | 17.15 | 16.92
2018-01-09 20:00 | 16.86 | 16.67
2018-01-09 20:30 | 16.12 | 15.96
2018-01-09 21:00 | 14.77 | 14.66
2018-01-09 21:30 | 13.51 | 13.4
2018-01-09 22:00 | 12.05 | 11.96
2018-01-09 22:30 | 11.06 | 11.02
2018-01-09 23:00 | 10.44 | 10.41
2018-01-09 23:30 | 9.05 | 9.02
2018-01-10 | 8.11 | 8.09
2018-01-10 00:30 | 7.4 | 7.39
2018-01-10 01:00 | 7.07 | 7.05
2018-01-10 01:30 | 6.8 | 6.78
2018-01-10 02:00 | 6.42 | 6.4
2018-01-10 02:30 | 6.19 | 6.17
2018-01-10 03:00 | 5.96 | 5.94
2018-01-10 03:30 | 5.93 | 5.91
2018-01-10 04:00 | 5.87 | 5.85
2018-01-10 04:30 | 5.9 | 5.88
2018-01-10 05:00 | 5.81 | 5.79
2018-01-10 05:30 | 6 | 5.99
2018-01-10 06:00 | 6.25 | 6.24
2018-01-10 06:30 | 6.25 | 6.24
2018-01-10 07:00 | 6.34 | 6.33
2018-01-10 07:30 | 6.44 | 6.42
2018-01-10 08:00 | 6.54 | 6.52
2018-01-10 08:30 | 6.46 | 6.43
2018-01-10 09:00 | 6.64 | 6.59
2018-01-10 09:30 | 7.06 | 6.98
2018-01-10 10:00 | 7.7 | 7.58
2018-01-10 10:30 | 8.39 | 8.27
2018-01-10 11:00 | 9.15 | 9.02
2018-01-10 11:30 | 10.47 | 10.32
2018-01-10 12:00 | 10.47 | 10.31
2018-01-10 12:30 | 10.63 | 10.44
2018-01-10 13:00 | 11.71 | 11.47
2018-01-10 13:30 | 12.48 | 12.21
2018-01-10 14:00 | 13.04 | 12.8
2018-01-10 14:30 | 13.2 | 12.94
2018-01-10 15:00 | 13.96 | 13.67
2018-01-10 15:30 | 14.87 | 14.55
2018-01-10 16:00 | 15.83 | 15.53
2018-01-10 16:30 | 16.53 | 16.26
2018-01-10 17:00 | 17.3 | 17.02
2018-01-10 17:30 | 18.01 | 17.78
2018-01-10 18:00 | 18.14 | 17.89
2018-01-10 18:30 | 17.88 | 17.64
2018-01-10 19:00 | 17.37 | 17.18
2018-01-10 19:30 | 17.31 | 17.1
2018-01-10 20:00 | 17.03 | 16.84
2018-01-10 20:30 | 16.52 | 16.34
2018-01-10 21:00 | 15.31 | 15.16
2018-01-10 21:30 | 14.13 | 14.01
2018-01-10 22:00 | 12.74 | 12.64
2018-01-10 22:30 | 11.77 | 11.72
2018-01-10 23:00 | 11.01 | 10.97
2018-01-10 23:30 | 9.82 | 9.78
2018-01-11 | 8.77 | 8.73
2018-01-11 00:30 | 8.06 | 8.04
2018-01-11 01:00 | 7.76 | 7.74
2018-01-11 01:30 | 7.28 | 7.26
2018-01-11 02:00 | 6.9 | 6.88
2018-01-11 02:30 | 6.72 | 6.7
2018-01-11 03:00 | 6.52 | 6.5
2018-01-11 03:30 | 6.52 | 6.5
2018-01-11 04:00 | 6.48 | 6.46
2018-01-11 04:30 | 6.4 | 6.39
2018-01-11 05:00 | 6.28 | 6.26
2018-01-11 05:30 | 6.21 | 6.19
2018-01-11 06:00 | 6.64 | 6.63
2018-01-11 06:30 | 6.84 | 6.83
2018-01-11 07:00 | 6.94 | 6.93
2018-01-11 07:30 | 6.94 | 6.92
2018-01-11 08:00 | 7.83 | 7.81
2018-01-11 08:30 | 7.6 | 7.58
2018-01-11 09:00 | 8.33 | 8.3
2018-01-11 09:30 | 8.65 | 8.6
2018-01-11 10:00 | 8.9 | 8.82
2018-01-11 10:30 | 9.16 | 9.06
2018-01-11 11:00 | 9.5 | 9.39
2018-01-11 11:30 | 11.15 | 11
2018-01-11 12:00 | 11.44 | 11.27
2018-01-11 12:30 | 10.35 | 10.16
2018-01-11 13:00 | 10.92 | 10.65
2018-01-11 13:30 | 11.78 | 11.53
2018-01-11 14:00 | 12.79 | 12.54
2018-01-11 14:30 | 14.31 | 14.07
2018-01-11 15:00 | 14.37 | 14.13
2018-01-11 15:30 | 15.16 | 14.85
2018-01-11 16:00 | 16.18 | 15.92
2018-01-11 16:30 | 15.94 | 15.71
2018-01-11 17:00 | 15.57 | 15.33
2018-01-11 17:30 | 16.65 | 16.45
2018-01-11 18:00 | 17.05 | 16.85
2018-01-11 18:30 | 16.78 | 16.6
2018-01-11 19:00 | 16.96 | 16.78
2018-01-11 19:30 | 17.02 | 16.81
2018-01-11 20:00 | 16.74 | 16.54
2018-01-11 20:30 | 16.11 | 15.94
2018-01-11 21:00 | 14.8 | 14.66
2018-01-11 21:30 | 13.72 | 13.61
2018-01-11 22:00 | 12.43 | 12.36
2018-01-11 22:30 | 11.66 | 11.61
2018-01-11 23:00 | 10.92 | 10.88
2018-01-11 23:30 | 9.5 | 9.47
2018-01-12 | 8.53 | 8.51
2018-01-12 00:30 | 7.86 | 7.84
2018-01-12 01:00 | 7.56 | 7.54
2018-01-12 01:30 | 7.14 | 7.12
2018-01-12 02:00 | 6.75 | 6.74
2018-01-12 02:30 | 6.58 | 6.57
2018-01-12 03:00 | 6.51 | 6.49
2018-01-12 03:30 | 6.4 | 6.39
2018-01-12 04:00 | 6.35 | 6.33
2018-01-12 04:30 | 6.29 | 6.27
2018-01-12 05:00 | 6.23 | 6.21
2018-01-12 05:30 | 6.06 | 6.04
2018-01-12 06:00 | 6.07 | 6.05
2018-01-12 06:30 | 6.23 | 6.22
2018-01-12 07:00 | 6.25 | 6.23
2018-01-12 07:30 | 6.86 | 6.84
2018-01-12 08:00 | 7.88 | 7.86
2018-01-12 08:30 | 8.81 | 8.79
2018-01-12 09:00 | 9.23 | 9.2
2018-01-12 09:30 | 8.96 | 8.92
2018-01-12 10:00 | 9.15 | 9.09
2018-01-12 10:30 | 9.47 | 9.4
2018-01-12 11:00 | 9.89 | 9.79
2018-01-12 11:30 | 10.68 | 10.55
2018-01-12 12:00 | 11.88 | 11.73
2018-01-12 12:30 | 12.04 | 11.87
2018-01-12 13:00 | 12.96 | 12.76
2018-01-12 13:30 | 13.69 | 13.46
2018-01-12 14:00 | 14.6 | 14.37
2018-01-12 14:30 | 15.77 | 15.53
2018-01-12 15:00 | 16.35 | 16.03
2018-01-12 15:30 | 16.57 | 16.21
2018-01-12 16:00 | 17.23 | 16.9
2018-01-12 16:30 | 17.89 | 17.57
2018-01-12 17:00 | 18.43 | 18.14
2018-01-12 17:30 | 18.99 | 18.72
2018-01-12 18:00 | 18.43 | 18.17
2018-01-12 18:30 | 17.88 | 17.64
2018-01-12 19:00 | 17.77 | 17.54
2018-01-12 19:30 | 17.78 | 17.5
2018-01-12 20:00 | 17.84 | 17.58
2018-01-12 20:30 | 17.13 | 16.9
2018-01-12 21:00 | 15.95 | 15.76
2018-01-12 21:30 | 14.83 | 14.67
2018-01-12 22:00 | 13.61 | 13.49
2018-01-12 22:30 | 12.85 | 12.76
2018-01-12 23:00 | 12.12 | 12.05
2018-01-12 23:30 | 10.62 | 10.56
2018-01-13 | 9.6 | 9.55
2018-01-13 00:30 | 8.94 | 8.9
2018-01-13 01:00 | 8.53 | 8.5
2018-01-13 01:30 | 7.87 | 7.84
2018-01-13 02:00 | 7.4 | 7.38
2018-01-13 02:30 | 7.15 | 7.13
2018-01-13 03:00 | 6.95 | 6.93
2018-01-13 03:30 | 6.73 | 6.71
2018-01-13 04:00 | 6.5 | 6.48
2018-01-13 04:30 | 6.48 | 6.46
2018-01-13 05:00 | 6.33 | 6.31
2018-01-13 05:30 | 6.08 | 6.06
2018-01-13 06:00 | 6.02 | 6
2018-01-13 06:30 | 6.1 | 6.08
2018-01-13 07:00 | 6.34 | 6.31
2018-01-13 07:30 | 7.01 | 6.97
2018-01-13 08:00 | 7.39 | 7.34
2018-01-13 08:30 | 8.08 | 8.03
2018-01-13 09:00 | 8.9 | 8.81
2018-01-13 09:30 | 9.93 | 9.78
2018-01-13 10:00 | 10.85 | 10.67
2018-01-13 10:30 | 11.87 | 11.66
2018-01-13 11:00 | 12.56 | 12.29
2018-01-13 11:30 | 13.92 | 13.61
2018-01-13 12:00 | 15.15 | 14.8
2018-01-13 12:30 | 16.19 | 15.81
2018-01-13 13:00 | 17.5 | 17.1
2018-01-13 13:30 | 18.76 | 18.37
2018-01-13 14:00 | 19.46 | 19.06
2018-01-13 14:30 | 20.03 | 19.63
2018-01-13 15:00 | 20.7 | 20.26
2018-01-13 15:30 | 21.85 | 21.44
2018-01-13 16:00 | 22.54 | 22.16
2018-01-13 16:30 | 22.23 | 21.84
2018-01-13 17:00 | 22.25 | 21.87
2018-01-13 17:30 | 21.41 | 21.07
2018-01-13 18:00 | 20.25 | 19.97
2018-01-13 18:30 | 19.92 | 19.64
2018-01-13 19:00 | 19.84 | 19.54
2018-01-13 19:30 | 19.88 | 19.54
2018-01-13 20:00 | 19.55 | 19.23
2018-01-13 20:30 | 18.63 | 18.36
2018-01-13 21:00 | 17.58 | 17.33
2018-01-13 21:30 | 16.56 | 16.33
2018-01-13 22:00 | 15.43 | 15.23
2018-01-13 22:30 | 14.68 | 14.5
2018-01-13 23:00 | 13.71 | 13.57
2018-01-13 23:30 | 12.17 | 12.06
2018-01-14 | 10.98 | 10.9
2018-01-14 00:30 | 10.04 | 9.97
2018-01-14 01:00 | 9.91 | 9.86
2018-01-14 01:30 | 9.41 | 9.36
2018-01-14 02:00 | 8.94 | 8.9
2018-01-14 02:30 | 8.7 | 8.66
2018-01-14 03:00 | 8.14 | 8.1
2018-01-14 03:30 | 7.81 | 7.78
2018-01-14 04:00 | 7.58 | 7.55
2018-01-14 04:30 | 7.43 | 7.4
2018-01-14 05:00 | 7.27 | 7.23
2018-01-14 05:30 | 6.91 | 6.88
2018-01-14 06:00 | 6.85 | 6.82
2018-01-14 06:30 | 7.13 | 7.1
2018-01-14 07:00 | 7.35 | 7.32
2018-01-14 07:30 | 8.02 | 7.99
2018-01-14 08:00 | 9.01 | 8.95
2018-01-14 08:30 | 10.2 | 10.1
2018-01-14 09:00 | 11.48 | 11.33
2018-01-14 09:30 | 12.2 | 12.02
2018-01-14 10:00 | 13.55 | 13.34
2018-01-14 10:30 | 14.01 | 13.75
2018-01-14 11:00 | 14.13 | 13.85
2018-01-14 11:30 | 14.14 | 13.83
2018-01-14 12:00 | 14.96 | 14.64
2018-01-14 12:30 | 17.13 | 16.78
2018-01-14 13:00 | 17.12 | 16.75
2018-01-14 13:30 | 16.95 | 16.57
2018-01-14 14:00 | 17.45 | 17.07
2018-01-14 14:30 | 18.65 | 18.29
2018-01-14 15:00 | 18.52 | 18.15
2018-01-14 15:30 | 19.05 | 18.68
2018-01-14 16:00 | 19.71 | 19.36
2018-01-14 16:30 | 20.46 | 20.11
2018-01-14 17:00 | 21.23 | 20.9
2018-01-14 17:30 | 20.23 | 19.93
2018-01-14 18:00 | 19.07 | 18.79
2018-01-14 18:30 | 17.62 | 17.4
2018-01-14 19:00 | 16.24 | 16.08
2018-01-14 19:30 | 15.24 | 15.07
2018-01-14 20:00 | 14.77 | 14.64
2018-01-14 20:30 | 13.86 | 13.77
2018-01-14 21:00 | 12.71 | 12.64
2018-01-14 21:30 | 11.65 | 11.59
2018-01-14 22:00 | 10.66 | 10.62
2018-01-14 22:30 | 10.04 | 10.01
2018-01-14 23:00 | 9.46 | 9.45
2018-01-14 23:30 | 8.2 | 8.19
2018-01-15 | 7.28 | 7.27
2018-01-15 00:30 | 6.51 | 6.5
2018-01-15 01:00 | 6.19 | 6.18
2018-01-15 01:30 | 5.87 | 5.86
2018-01-15 02:00 | 5.44 | 5.43
2018-01-15 02:30 | 5.32 | 5.31
2018-01-15 03:00 | 5.14 | 5.13
2018-01-15 03:30 | 5.14 | 5.13
2018-01-15 04:00 | 5.04 | 5.03
2018-01-15 04:30 | 5.1 | 5.09
2018-01-15 05:00 | 5.14 | 5.12
2018-01-15 05:30 | 5.4 | 5.37
2018-01-15 06:00 | 5.53 | 5.5
2018-01-15 06:30 | 5.7 | 5.68
2018-01-15 07:00 | 5.54 | 5.53
2018-01-15 07:30 | 5.37 | 5.37
2018-01-15 08:00 | 4.99 | 4.98
2018-01-15 08:30 | 4.88 | 4.86
2018-01-15 09:00 | 4.6 | 4.58
2018-01-15 09:30 | 4.61 | 4.58
2018-01-15 10:00 | 4.57 | 4.54
2018-01-15 10:30 | 4.65 | 4.61
2018-01-15 11:00 | 4.85 | 4.78
2018-01-15 11:30 | 5.46 | 5.37
2018-01-15 12:00 | 6.11 | 6.05
2018-01-15 12:30 | 6.19 | 6.11
2018-01-15 13:00 | 6.78 | 6.7
2018-01-15 13:30 | 7.32 | 7.23
2018-01-15 14:00 | 7.82 | 7.72
2018-01-15 14:30 | 8.59 | 8.5
2018-01-15 15:00 | 9.03 | 8.93
2018-01-15 15:30 | 9.24 | 9.13
2018-01-15 16:00 | 9.94 | 9.84
2018-01-15 16:30 | 11.19 | 11.09
2018-01-15 17:00 | 12.04 | 11.96
2018-01-15 17:30 | 12.6 | 12.53
2018-01-15 18:00 | 12.91 | 12.85
2018-01-15 18:30 | 12.94 | 12.88
2018-01-15 19:00 | 12.83 | 12.78
2018-01-15 19:30 | 13.08 | 13.01
2018-01-15 20:00 | 13.18 | 13.12
2018-01-15 20:30 | 12.77 | 12.72
2018-01-15 21:00 | 11.71 | 11.68
2018-01-15 21:30 | 10.34 | 10.33
2018-01-15 22:00 | 9.26 | 9.25
2018-01-15 22:30 | 8.68 | 8.67
2018-01-15 23:00 | 8.42 | 8.41
2018-01-15 23:30 | 7.14 | 7.13
2018-01-16 | 6.31 | 6.3
2018-01-16 00:30 | 5.81 | 5.8
2018-01-16 01:00 | 5.56 | 5.55
2018-01-16 01:30 | 5.25 | 5.24
2018-01-16 02:00 | 4.99 | 4.98
2018-01-16 02:30 | 4.89 | 4.88
2018-01-16 03:00 | 4.85 | 4.84
2018-01-16 03:30 | 4.76 | 4.74
2018-01-16 04:00 | 4.75 | 4.73
2018-01-16 04:30 | 4.87 | 4.86
2018-01-16 05:00 | 4.92 | 4.9
2018-01-16 05:30 | 5.13 | 5.09
2018-01-16 06:00 | 5.37 | 5.32
2018-01-16 06:30 | 5.28 | 5.24
2018-01-16 07:00 | 5.15 | 5.11
2018-01-16 07:30 | 5.42 | 5.4
2018-01-16 08:00 | 5.47 | 5.45
2018-01-16 08:30 | 5.25 | 5.24
2018-01-16 09:00 | 5.02 | 5.01
2018-01-16 09:30 | 4.74 | 4.72
2018-01-16 10:00 | 4.6 | 4.58
2018-01-16 10:30 | 4.68 | 4.65
2018-01-16 11:00 | 4.87 | 4.84
2018-01-16 11:30 | 4.97 | 4.95
2018-01-16 12:00 | 5.62 | 5.59
2018-01-16 12:30 | 5.99 | 5.95
2018-01-16 13:00 | 6.24 | 6.2
2018-01-16 13:30 | 6.72 | 6.66
2018-01-16 14:00 | 7.45 | 7.39
2018-01-16 14:30 | 8.4 | 8.34
2018-01-16 15:00 | 8.85 | 8.79
2018-01-16 15:30 | 9.67 | 9.6
2018-01-16 16:00 | 9.3 | 9.22
2018-01-16 16:30 | 10.91 | 10.85
2018-01-16 17:00 | 12.19 | 12.13
2018-01-16 17:30 | 12.94 | 12.87
2018-01-16 18:00 | 13.17 | 13.11
2018-01-16 18:30 | 12.94 | 12.89
2018-01-16 19:00 | 12.78 | 12.73
2018-01-16 19:30 | 13.06 | 12.99
2018-01-16 20:00 | 13.23 | 13.17
2018-01-16 20:30 | 12.68 | 12.64
2018-01-16 21:00 | 11.82 | 11.79
2018-01-16 21:30 | 10.31 | 10.29
2018-01-16 22:00 | 9.21 | 9.2
2018-01-16 22:30 | 8.64 | 8.63
2018-01-16 23:00 | 8.25 | 8.24
2018-01-16 23:30 | 7.14 | 7.13
2018-01-17 | 6.29 | 6.28
2018-01-17 00:30 | 5.76 | 5.75
2018-01-17 01:00 | 5.63 | 5.62
2018-01-17 01:30 | 5.35 | 5.34
2018-01-17 02:00 | 4.99 | 4.97
2018-01-17 02:30 | 4.9 | 4.88
2018-01-17 03:00 | 4.76 | 4.75
2018-01-17 03:30 | 4.72 | 4.7
2018-01-17 04:00 | 4.63 | 4.61
2018-01-17 04:30 | 4.8 | 4.78
2018-01-17 05:00 | 4.88 | 4.86
2018-01-17 05:30 | 4.99 | 4.94
2018-01-17 06:00 | 5.37 | 5.33
2018-01-17 06:30 | 5.38 | 5.34
2018-01-17 07:00 | 5.25 | 5.23
2018-01-17 07:30 | 5.03 | 5.01
2018-01-17 08:00 | 4.71 | 4.7
2018-01-17 08:30 | 4.35 | 4.34
2018-01-17 09:00 | 4.09 | 4.08
2018-01-17 09:30 | 4.03 | 4.01
2018-01-17 10:00 | 4.03 | 4
2018-01-17 10:30 | 4.06 | 4.03
2018-01-17 11:00 | 4.28 | 4.24
2018-01-17 11:30 | 4.52 | 4.48
2018-01-17 12:00 | 4.88 | 4.83
2018-01-17 12:30 | 5.3 | 5.24
2018-01-17 13:00 | 5.72 | 5.66
2018-01-17 13:30 | 6.32 | 6.24
2018-01-17 14:00 | 7.08 | 6.98
2018-01-17 14:30 | 7.72 | 7.62
2018-01-17 15:00 | 8.4 | 8.3
2018-01-17 15:30 | 9.27 | 9.17
2018-01-17 16:00 | 9.57 | 9.46
2018-01-17 16:30 | 10.77 | 10.68
2018-01-17 17:00 | 11.58 | 11.51
2018-01-17 17:30 | 12.14 | 12.08
2018-01-17 18:00 | 12.45 | 12.39
2018-01-17 18:30 | 12.3 | 12.26
2018-01-17 19:00 | 12.5 | 12.47
2018-01-17 19:30 | 12.91 | 12.85
2018-01-17 20:00 | 13.02 | 12.97
2018-01-17 20:30 | 12.66 | 12.62
2018-01-17 21:00 | 11.77 | 11.74
2018-01-17 21:30 | 10.39 | 10.37
2018-01-17 22:00 | 9.37 | 9.35
2018-01-17 22:30 | 8.79 | 8.78
2018-01-17 23:00 | 8.43 | 8.42
2018-01-17 23:30 | 7.36 | 7.35
2018-01-18 | 6.41 | 6.4
2018-01-18 00:30 | 5.86 | 5.85
2018-01-18 01:00 | 5.61 | 5.6
2018-01-18 01:30 | 5.29 | 5.28
2018-01-18 02:00 | 4.94 | 4.93
2018-01-18 02:30 | 4.84 | 4.83
2018-01-18 03:00 | 4.75 | 4.73
2018-01-18 03:30 | 4.76 | 4.75
2018-01-18 04:00 | 4.75 | 4.74
2018-01-18 04:30 | 4.86 | 4.84
2018-01-18 05:00 | 4.93 | 4.91
2018-01-18 05:30 | 5.01 | 4.97
2018-01-18 06:00 | 5.66 | 5.62
2018-01-18 06:30 | 5.57 | 5.54
2018-01-18 07:00 | 5.45 | 5.43
2018-01-18 07:30 | 5.19 | 5.18
2018-01-18 08:00 | 4.98 | 4.97
2018-01-18 08:30 | 4.83 | 4.82
2018-01-18 09:00 | 4.56 | 4.54
2018-01-18 09:30 | 4.57 | 4.55
2018-01-18 10:00 | 4.65 | 4.62
2018-01-18 10:30 | 4.89 | 4.85
2018-01-18 11:00 | 5.51 | 5.47
2018-01-18 11:30 | 6.19 | 6.12
2018-01-18 12:00 | 6.22 | 6.14
2018-01-18 12:30 | 7.22 | 7.13
2018-01-18 13:00 | 7.4 | 7.3
2018-01-18 13:30 | 7.94 | 7.82
2018-01-18 14:00 | 9.01 | 8.87
2018-01-18 14:30 | 9.56 | 9.42
2018-01-18 15:00 | 10.17 | 9.99
2018-01-18 15:30 | 10.89 | 10.7
2018-01-18 16:00 | 11.36 | 11.21
2018-01-18 16:30 | 12.31 | 12.17
2018-01-18 17:00 | 13.03 | 12.9
2018-01-18 17:30 | 13.55 | 13.43
2018-01-18 18:00 | 13.7 | 13.59
2018-01-18 18:30 | 13.6 | 13.51
2018-01-18 19:00 | 13.86 | 13.78
2018-01-18 19:30 | 13.76 | 13.66
2018-01-18 20:00 | 13.74 | 13.65
2018-01-18 20:30 | 13.36 | 13.29
2018-01-18 21:00 | 12.27 | 12.22
2018-01-18 21:30 | 10.87 | 10.84
2018-01-18 22:00 | 9.8 | 9.78
2018-01-18 22:30 | 9.25 | 9.23
2018-01-18 23:00 | 8.77 | 8.76
2018-01-18 23:30 | 7.4 | 7.39
2018-01-19 | 6.64 | 6.62
2018-01-19 00:30 | 5.97 | 5.96
2018-01-19 01:00 | 5.78 | 5.77
2018-01-19 01:30 | 5.41 | 5.4
2018-01-19 02:00 | 5.09 | 5.08
2018-01-19 02:30 | 4.95 | 4.94
2018-01-19 03:00 | 4.84 | 4.82
2018-01-19 03:30 | 4.7 | 4.68
2018-01-19 04:00 | 4.77 | 4.76
2018-01-19 04:30 | 4.85 | 4.83
2018-01-19 05:00 | 4.93 | 4.91
2018-01-19 05:30 | 4.89 | 4.84
2018-01-19 06:00 | 4.91 | 4.86
2018-01-19 06:30 | 4.81 | 4.76
2018-01-19 07:00 | 4.55 | 4.5
2018-01-19 07:30 | 4.41 | 4.38
2018-01-19 08:00 | 4.17 | 4.15
2018-01-19 08:30 | 4 | 3.97
2018-01-19 09:00 | 3.86 | 3.83
2018-01-19 09:30 | 3.77 | 3.73
2018-01-19 10:00 | 4.03 | 3.98
2018-01-19 10:30 | 4.27 | 4.22
2018-01-19 11:00 | 4.65 | 4.59
2018-01-19 11:30 | 5.54 | 5.48
2018-01-19 12:00 | 6.5 | 6.41
2018-01-19 12:30 | 7.21 | 7.1
2018-01-19 13:00 | 7.9 | 7.77
2018-01-19 13:30 | 8.49 | 8.37
2018-01-19 14:00 | 9.46 | 9.32
2018-01-19 14:30 | 10.39 | 10.23
2018-01-19 15:00 | 11.1 | 10.94
2018-01-19 15:30 | 11.92 | 11.75
2018-01-19 16:00 | 12.57 | 12.38
2018-01-19 16:30 | 12.9 | 12.73
2018-01-19 17:00 | 13.47 | 13.34
2018-01-19 17:30 | 13.83 | 13.7
2018-01-19 18:00 | 13.87 | 13.75
2018-01-19 18:30 | 13.9 | 13.79
2018-01-19 19:00 | 13.59 | 13.5
2018-01-19 19:30 | 13.73 | 13.61
2018-01-19 20:00 | 13.67 | 13.57
2018-01-19 20:30 | 13.13 | 13.04
2018-01-19 21:00 | 12.04 | 11.98
2018-01-19 21:30 | 11.15 | 11.11
2018-01-19 22:00 | 10.16 | 10.14
2018-01-19 22:30 | 9.66 | 9.65
2018-01-19 23:00 | 9.24 | 9.23
2018-01-19 23:30 | 8.07 | 8.06
2018-01-20 | 7.18 | 7.16
2018-01-20 00:30 | 6.44 | 6.43
2018-01-20 01:00 | 6.11 | 6.1
2018-01-20 01:30 | 5.65 | 5.63
2018-01-20 02:00 | 5.39 | 5.38
2018-01-20 02:30 | 5.14 | 5.13
2018-01-20 03:00 | 4.95 | 4.94
2018-01-20 03:30 | 4.92 | 4.9
2018-01-20 04:00 | 4.86 | 4.84
2018-01-20 04:30 | 4.77 | 4.76
2018-01-20 05:00 | 4.73 | 4.71
2018-01-20 05:30 | 4.57 | 4.52
2018-01-20 06:00 | 4.58 | 4.51
2018-01-20 06:30 | 4.52 | 4.46
2018-01-20 07:00 | 4.45 | 4.4
2018-01-20 07:30 | 4.45 | 4.42
2018-01-20 08:00 | 4.44 | 4.41
2018-01-20 08:30 | 4.42 | 4.39
2018-01-20 09:00 | 4.58 | 4.54
2018-01-20 09:30 | 4.85 | 4.8
2018-01-20 10:00 | 5.03 | 4.97
2018-01-20 10:30 | 5.24 | 5.19
2018-01-20 11:00 | 5.6 | 5.54
2018-01-20 11:30 | 6.1 | 6.02
2018-01-20 12:00 | 6.58 | 6.49
2018-01-20 12:30 | 7.22 | 7.12
2018-01-20 13:00 | 7.92 | 7.8
2018-01-20 13:30 | 9.01 | 8.87
2018-01-20 14:00 | 10.16 | 10
2018-01-20 14:30 | 11.08 | 10.91
2018-01-20 15:00 | 11.8 | 11.62
2018-01-20 15:30 | 12.79 | 12.6
2018-01-20 16:00 | 13.53 | 13.34
2018-01-20 16:30 | 14.22 | 14.04
2018-01-20 17:00 | 14.61 | 14.44
2018-01-20 17:30 | 14.72 | 14.57
2018-01-20 18:00 | 14.5 | 14.37
2018-01-20 18:30 | 14.15 | 14.04
2018-01-20 19:00 | 13.78 | 13.69
2018-01-20 19:30 | 13.68 | 13.56
2018-01-20 20:00 | 13.55 | 13.45
2018-01-20 20:30 | 13.1 | 13.02
2018-01-20 21:00 | 12.22 | 12.14
2018-01-20 21:30 | 11.45 | 11.39
2018-01-20 22:00 | 10.52 | 10.48
2018-01-20 22:30 | 10.06 | 10.03
2018-01-20 23:00 | 9.7 | 9.68
2018-01-20 23:30 | 8.51 | 8.49
2018-01-21 | 7.49 | 7.47
2018-01-21 00:30 | 6.92 | 6.9
2018-01-21 01:00 | 6.51 | 6.49
2018-01-21 01:30 | 6.08 | 6.07
2018-01-21 02:00 | 5.85 | 5.83
2018-01-21 02:30 | 5.54 | 5.52
2018-01-21 03:00 | 5.39 | 5.37
2018-01-21 03:30 | 5.25 | 5.23
2018-01-21 04:00 | 5.13 | 5.12
2018-01-21 04:30 | 5.06 | 5.05
2018-01-21 05:00 | 5.05 | 5.04
2018-01-21 05:30 | 4.79 | 4.75
2018-01-21 06:00 | 4.63 | 4.57
2018-01-21 06:30 | 4.53 | 4.49
2018-01-21 07:00 | 4.48 | 4.45
2018-01-21 07:30 | 4.88 | 4.85
2018-01-21 08:00 | 5.25 | 5.22
2018-01-21 08:30 | 5.53 | 5.5
2018-01-21 09:00 | 6.84 | 6.81
2018-01-21 09:30 | 7.38 | 7.34
2018-01-21 10:00 | 6.57 | 6.52
2018-01-21 10:30 | 8.72 | 8.68
2018-01-21 11:00 | 8.3 | 8.23
2018-01-21 11:30 | 9.33 | 9.25
2018-01-21 12:00 | 9.78 | 9.68
2018-01-21 12:30 | 10.61 | 10.5
2018-01-21 13:00 | 11.18 | 11.07
2018-01-21 13:30 | 11.09 | 10.98
2018-01-21 14:00 | 12.05 | 11.93
2018-01-21 14:30 | 13 | 12.88
2018-01-21 15:00 | 12.5 | 12.37
2018-01-21 15:30 | 13.18 | 13.05
2018-01-21 16:00 | 13.22 | 13.1
2018-01-21 16:30 | 13.54 | 13.44
2018-01-21 17:00 | 13.61 | 13.52
2018-01-21 17:30 | 13.6 | 13.52
2018-01-21 18:00 | 13.72 | 13.64
2018-01-21 18:30 | 13.71 | 13.65
2018-01-21 19:00 | 13.86 | 13.8
2018-01-21 19:30 | 14.11 | 14.02
2018-01-21 20:00 | 14.08 | 13.99
2018-01-21 20:30 | 13.53 | 13.46
2018-01-21 21:00 | 12.67 | 12.62
2018-01-21 21:30 | 11.7 | 11.66
2018-01-21 22:00 | 10.79 | 10.76
2018-01-21 22:30 | 10.13 | 10.11
2018-01-21 23:00 | 9.72 | 9.7
2018-01-21 23:30 | 8.51 | 8.5
2018-01-22 | 7.56 | 7.55
2018-01-22 00:30 | 6.87 | 6.85
2018-01-22 01:00 | 6.54 | 6.52
2018-01-22 01:30 | 6.27 | 6.26
2018-01-22 02:00 | 5.95 | 5.93
2018-01-22 02:30 | 5.77 | 5.76
2018-01-22 03:00 | 5.66 | 5.65
2018-01-22 03:30 | 5.61 | 5.59
2018-01-22 04:00 | 5.56 | 5.54
2018-01-22 04:30 | 5.56 | 5.54
2018-01-22 05:00 | 5.69 | 5.67
2018-01-22 05:30 | 5.96 | 5.95
2018-01-22 06:00 | 6.23 | 6.21
2018-01-22 06:30 | 6.6 | 6.59
2018-01-22 07:00 | 6.93 | 6.92
2018-01-22 07:30 | 6.88 | 6.87
2018-01-22 08:00 | 6.8 | 6.78
2018-01-22 08:30 | 6.48 | 6.45
2018-01-22 09:00 | 6.24 | 6.21
2018-01-22 09:30 | 7.63 | 7.59
2018-01-22 10:00 | 7.23 | 7.17
2018-01-22 10:30 | 7.45 | 7.37
2018-01-22 11:00 | 8.44 | 8.37
2018-01-22 11:30 | 8.74 | 8.67
2018-01-22 12:00 | 9.9 | 9.82
2018-01-22 12:30 | 10.93 | 10.85
2018-01-22 13:00 | 10.83 | 10.73
2018-01-22 13:30 | 10.48 | 10.26
2018-01-22 14:00 | 10.86 | 10.66
2018-01-22 14:30 | 11.6 | 11.44
2018-01-22 15:00 | 11.69 | 11.52
2018-01-22 15:30 | 12.85 | 12.66
2018-01-22 16:00 | 13.86 | 13.64
2018-01-22 16:30 | 14.61 | 14.43
2018-01-22 17:00 | 15.27 | 15.1
2018-01-22 17:30 | 15.95 | 15.8
2018-01-22 18:00 | 16.32 | 16.17
2018-01-22 18:30 | 16.22 | 16.09
2018-01-22 19:00 | 15.95 | 15.83
2018-01-22 19:30 | 15.72 | 15.58
2018-01-22 20:00 | 15.84 | 15.7
2018-01-22 20:30 | 15.33 | 15.22
2018-01-22 21:00 | 13.86 | 13.78
2018-01-22 21:30 | 12.46 | 12.4
2018-01-22 22:00 | 11.24 | 11.2
2018-01-22 22:30 | 10.44 | 10.42
2018-01-22 23:00 | 9.76 | 9.74
2018-01-22 23:30 | 8.54 | 8.52
2018-01-23 | 7.65 | 7.63
2018-01-23 00:30 | 6.97 | 6.96
2018-01-23 01:00 | 6.62 | 6.61
2018-01-23 01:30 | 6.26 | 6.25
2018-01-23 02:00 | 5.98 | 5.97
2018-01-23 02:30 | 5.83 | 5.82
2018-01-23 03:00 | 5.61 | 5.6
2018-01-23 03:30 | 5.65 | 5.64
2018-01-23 04:00 | 5.6 | 5.58
2018-01-23 04:30 | 5.68 | 5.67
2018-01-23 05:00 | 5.71 | 5.7
2018-01-23 05:30 | 5.8 | 5.79
2018-01-23 06:00 | 6.29 | 6.27
2018-01-23 06:30 | 6.39 | 6.38
2018-01-23 07:00 | 6.48 | 6.47
2018-01-23 07:30 | 6.85 | 6.84
2018-01-23 08:00 | 7.23 | 7.21
2018-01-23 08:30 | 6.6 | 6.57
2018-01-23 09:00 | 6.16 | 6.11
2018-01-23 09:30 | 6.4 | 6.33
2018-01-23 10:00 | 7.22 | 7.13
2018-01-23 10:30 | 7.85 | 7.74
2018-01-23 11:00 | 8.46 | 8.34
2018-01-23 11:30 | 7.98 | 7.84
2018-01-23 12:00 | 8.91 | 8.76
2018-01-23 12:30 | 9.78 | 9.55
2018-01-23 13:00 | 10.65 | 10.44
2018-01-23 13:30 | 10.8 | 10.63
2018-01-23 14:00 | 11.55 | 11.36
2018-01-23 14:30 | 11.87 | 11.67
2018-01-23 15:00 | 13.08 | 12.87
2018-01-23 15:30 | 13.57 | 13.28
2018-01-23 16:00 | 14.44 | 14.13
2018-01-23 16:30 | 15.55 | 15.33
2018-01-23 17:00 | 16.49 | 16.28
2018-01-23 17:30 | 17.12 | 16.91
2018-01-23 18:00 | 17.21 | 17.02
2018-01-23 18:30 | 17.1 | 16.92
2018-01-23 19:00 | 16.84 | 16.67
2018-01-23 19:30 | 16.62 | 16.42
2018-01-23 20:00 | 16.5 | 16.33
2018-01-23 20:30 | 16.01 | 15.87
2018-01-23 21:00 | 14.63 | 14.52
2018-01-23 21:30 | 12.99 | 12.92
2018-01-23 22:00 | 11.77 | 11.72
2018-01-23 22:30 | 10.91 | 10.88
2018-01-23 23:00 | 10.32 | 10.29
2018-01-23 23:30 | 8.98 | 8.96
2018-01-24 | 7.85 | 7.83
2018-01-24 00:30 | 7.19 | 7.17
2018-01-24 01:00 | 6.92 | 6.9
2018-01-24 01:30 | 6.67 | 6.65
2018-01-24 02:00 | 6.43 | 6.42
2018-01-24 02:30 | 6.24 | 6.22
2018-01-24 03:00 | 6.01 | 6
2018-01-24 03:30 | 5.92 | 5.91
2018-01-24 04:00 | 5.81 | 5.8
2018-01-24 04:30 | 5.93 | 5.91
2018-01-24 05:00 | 6.05 | 6.04
2018-01-24 05:30 | 6.16 | 6.15
2018-01-24 06:00 | 6.73 | 6.72
2018-01-24 06:30 | 7.1 | 7.1
2018-01-24 07:00 | 7.56 | 7.56
2018-01-24 07:30 | 7.21 | 7.2
2018-01-24 08:00 | 7.73 | 7.72
2018-01-24 08:30 | 6.8 | 6.78
2018-01-24 09:00 | 6.85 | 6.83
2018-01-24 09:30 | 7.02 | 6.99
2018-01-24 10:00 | 6.97 | 6.92
2018-01-24 10:30 | 7.24 | 7.17
2018-01-24 11:00 | 7.83 | 7.76
2018-01-24 11:30 | 8.79 | 8.73
2018-01-24 12:00 | 7.87 | 7.78
2018-01-24 12:30 | 8.03 | 7.92
2018-01-24 13:00 | 8.98 | 8.85
2018-01-24 13:30 | 10.09 | 9.91
2018-01-24 14:00 | 10.73 | 10.58
2018-01-24 14:30 | 11.27 | 11.12
2018-01-24 15:00 | 11.29 | 11.12
2018-01-24 15:30 | 12.71 | 12.52
2018-01-24 16:00 | 14.44 | 14.19
2018-01-24 16:30 | 15.33 | 15.06
2018-01-24 17:00 | 16.1 | 15.89
2018-01-24 17:30 | 16.59 | 16.4
2018-01-24 18:00 | 16.83 | 16.65
2018-01-24 18:30 | 17 | 16.82
2018-01-24 19:00 | 16.76 | 16.59
2018-01-24 19:30 | 16.66 | 16.47
2018-01-24 20:00 | 16.93 | 16.75
2018-01-24 20:30 | 16.52 | 16.36
2018-01-24 21:00 | 15.23 | 15.1
2018-01-24 21:30 | 13.83 | 13.69
2018-01-24 22:00 | 12.55 | 12.46
2018-01-24 22:30 | 11.54 | 11.49
2018-01-24 23:00 | 10.85 | 10.81
2018-01-24 23:30 | 9.43 | 9.4
2018-01-25 | 8.52 | 8.49
2018-01-25 00:30 | 7.87 | 7.85
2018-01-25 01:00 | 7.49 | 7.47
2018-01-25 01:30 | 7.15 | 7.13
2018-01-25 02:00 | 6.8 | 6.78
2018-01-25 02:30 | 6.57 | 6.55
2018-01-25 03:00 | 6.39 | 6.37
2018-01-25 03:30 | 6.33 | 6.32
2018-01-25 04:00 | 6.28 | 6.27
2018-01-25 04:30 | 6.23 | 6.21
2018-01-25 05:00 | 6.41 | 6.4
2018-01-25 05:30 | 6.7 | 6.69
2018-01-25 06:00 | 6.91 | 6.9
2018-01-25 06:30 | 7.47 | 7.46
2018-01-25 07:00 | 7.93 | 7.92
2018-01-25 07:30 | 7.99 | 7.97
2018-01-25 08:00 | 8.15 | 8.12
2018-01-25 08:30 | 8.06 | 8.02
2018-01-25 09:00 | 7.94 | 7.86
2018-01-25 09:30 | 8.41 | 8.29
2018-01-25 10:00 | 8.9 | 8.76
2018-01-25 10:30 | 9.1 | 8.92
2018-01-25 11:00 | 9.77 | 9.58
2018-01-25 11:30 | 10.32 | 10.11
2018-01-25 12:00 | 10.68 | 10.45
2018-01-25 12:30 | 11.28 | 11.04
2018-01-25 13:00 | 11.71 | 11.46
2018-01-25 13:30 | 12.47 | 12.22
2018-01-25 14:00 | 13 | 12.7
2018-01-25 14:30 | 13.28 | 12.99
2018-01-25 15:00 | 13.61 | 13.33
2018-01-25 15:30 | 14.32 | 14.02
2018-01-25 16:00 | 15.04 | 14.77
2018-01-25 16:30 | 15.51 | 15.27
2018-01-25 17:00 | 16.02 | 15.8
2018-01-25 17:30 | 16.52 | 16.31
2018-01-25 18:00 | 16.46 | 16.27
2018-01-25 18:30 | 16.09 | 15.91
2018-01-25 19:00 | 16.29 | 16.1
2018-01-25 19:30 | 16.58 | 16.34
2018-01-25 20:00 | 16.48 | 16.25
2018-01-25 20:30 | 16.19 | 15.99
2018-01-25 21:00 | 15.16 | 15
2018-01-25 21:30 | 14.29 | 14.15
2018-01-25 22:00 | 13.4 | 13.28
2018-01-25 22:30 | 12.75 | 12.66
2018-01-25 23:00 | 12.01 | 11.94
2018-01-25 23:30 | 10.58 | 10.53
2018-01-26 | 9.38 | 9.34
2018-01-26 00:30 | 8.55 | 8.52
2018-01-26 01:00 | 8.31 | 8.28
2018-01-26 01:30 | 7.76 | 7.74
2018-01-26 02:00 | 7.24 | 7.22
2018-01-26 02:30 | 7.05 | 7.02
2018-01-26 03:00 | 6.78 | 6.75
2018-01-26 03:30 | 6.54 | 6.52
2018-01-26 04:00 | 6.35 | 6.32
2018-01-26 04:30 | 6.41 | 6.39
2018-01-26 05:00 | 6.28 | 6.26
2018-01-26 05:30 | 5.95 | 5.93
2018-01-26 06:00 | 5.69 | 5.67
2018-01-26 06:30 | 5.51 | 5.49
2018-01-26 07:00 | 5.5 | 5.48
2018-01-26 07:30 | 6.13 | 6.1
2018-01-26 08:00 | 6.97 | 6.93
2018-01-26 08:30 | 7.77 | 7.74
2018-01-26 09:00 | 8.59 | 8.55
2018-01-26 09:30 | 9.22 | 9.16
2018-01-26 10:00 | 9.42 | 9.33
2018-01-26 10:30 | 10.23 | 10.11
2018-01-26 11:00 | 10.51 | 10.38
2018-01-26 11:30 | 11.09 | 10.95
2018-01-26 12:00 | 11.77 | 11.61
2018-01-26 12:30 | 12.71 | 12.54
2018-01-26 13:00 | 12.03 | 11.84
2018-01-26 13:30 | 11.92 | 11.7
2018-01-26 14:00 | 12.5 | 12.28
2018-01-26 14:30 | 12.95 | 12.75
2018-01-26 15:00 | 13.54 | 13.33
2018-01-26 15:30 | 14.48 | 14.28
2018-01-26 16:00 | 15.18 | 14.98
2018-01-26 16:30 | 14.9 | 14.71
2018-01-26 17:00 | 15.57 | 15.39
2018-01-26 17:30 | 15.9 | 15.73
2018-01-26 18:00 | 15.87 | 15.7
2018-01-26 18:30 | 15.4 | 15.25
2018-01-26 19:00 | 15.13 | 14.98
2018-01-26 19:30 | 15.1 | 14.95
2018-01-26 20:00 | 15.21 | 15.07
2018-01-26 20:30 | 15.04 | 14.9
2018-01-26 21:00 | 14.44 | 14.3
2018-01-26 21:30 | 13.72 | 13.6
2018-01-26 22:00 | 12.87 | 12.77
2018-01-26 22:30 | 12.22 | 12.14
2018-01-26 23:00 | 11.7 | 11.63
2018-01-26 23:30 | 10.22 | 10.17
2018-01-27 | 9.34 | 9.29
2018-01-27 00:30 | 8.49 | 8.46
2018-01-27 01:00 | 8.12 | 8.1
2018-01-27 01:30 | 7.57 | 7.54
2018-01-27 02:00 | 7.18 | 7.16
2018-01-27 02:30 | 6.98 | 6.96
2018-01-27 03:00 | 6.85 | 6.82
2018-01-27 03:30 | 6.71 | 6.68
2018-01-27 04:00 | 6.55 | 6.53
2018-01-27 04:30 | 6.49 | 6.47
2018-01-27 05:00 | 6.41 | 6.39
2018-01-27 05:30 | 6.27 | 6.24
2018-01-27 06:00 | 6.15 | 6.13
2018-01-27 06:30 | 6.24 | 6.21
2018-01-27 07:00 | 6.3 | 6.27
2018-01-27 07:30 | 6.84 | 6.8
2018-01-27 08:00 | 7.18 | 7.13
2018-01-27 08:30 | 7.9 | 7.85
2018-01-27 09:00 | 8.66 | 8.59
2018-01-27 09:30 | 10.23 | 10.15
2018-01-27 10:00 | 10 | 9.89
2018-01-27 10:30 | 10.75 | 10.62
2018-01-27 11:00 | 11.66 | 11.49
2018-01-27 11:30 | 11.95 | 11.76
2018-01-27 12:00 | 12.03 | 11.82
2018-01-27 12:30 | 12.02 | 11.79
2018-01-27 13:00 | 13.05 | 12.8
2018-01-27 13:30 | 13.36 | 13.08
2018-01-27 14:00 | 14.09 | 13.79
2018-01-27 14:30 | 14.49 | 14.2
2018-01-27 15:00 | 15.12 | 14.84
2018-01-27 15:30 | 15.66 | 15.38
2018-01-27 16:00 | 15.89 | 15.63
2018-01-27 16:30 | 16.61 | 16.36
2018-01-27 17:00 | 16.84 | 16.61
2018-01-27 17:30 | 17.05 | 16.84
2018-01-27 18:00 | 16.53 | 16.34
2018-01-27 18:30 | 16.19 | 16.01
2018-01-27 19:00 | 15.62 | 15.47
2018-01-27 19:30 | 15.55 | 15.36
2018-01-27 20:00 | 15.48 | 15.31
2018-01-27 20:30 | 15.11 | 14.96
2018-01-27 21:00 | 14.19 | 14.06
2018-01-27 21:30 | 13.26 | 13.16
2018-01-27 22:00 | 12.42 | 12.33
2018-01-27 22:30 | 11.82 | 11.75
2018-01-27 23:00 | 11.38 | 11.33
2018-01-27 23:30 | 9.99 | 9.95
2018-01-28 | 8.99 | 8.97
2018-01-28 00:30 | 8.3 | 8.28
2018-01-28 01:00 | 7.94 | 7.92
2018-01-28 01:30 | 7.5 | 7.48
2018-01-28 02:00 | 7.09 | 7.07
2018-01-28 02:30 | 6.81 | 6.79
2018-01-28 03:00 | 6.61 | 6.59
2018-01-28 03:30 | 6.41 | 6.39
2018-01-28 04:00 | 6.27 | 6.25
2018-01-28 04:30 | 6.25 | 6.23
2018-01-28 05:00 | 6.17 | 6.15
2018-01-28 05:30 | 6.03 | 6.01
2018-01-28 06:00 | 5.99 | 5.97
2018-01-28 06:30 | 5.85 | 5.83
2018-01-28 07:00 | 6.04 | 6.02
2018-01-28 07:30 | 5.87 | 5.84
2018-01-28 08:00 | 6.24 | 6.2
2018-01-28 08:30 | 7.75 | 7.71
2018-01-28 09:00 | 7.79 | 7.75
2018-01-28 09:30 | 9.66 | 9.62
2018-01-28 10:00 | 7.84 | 7.78
2018-01-28 10:30 | 8.86 | 8.81
2018-01-28 11:00 | 8.88 | 8.82
2018-01-28 11:30 | 8.92 | 8.85
2018-01-28 12:00 | 8.51 | 8.41
2018-01-28 12:30 | 10.59 | 10.49
2018-01-28 13:00 | 10.83 | 10.72
2018-01-28 13:30 | 10.32 | 10.2
2018-01-28 14:00 | 11.12 | 11.04
2018-01-28 14:30 | 8.95 | 8.83
2018-01-28 15:00 | 10.75 | 10.64
2018-01-28 15:30 | 11.17 | 11.05
2018-01-28 16:00 | 12.01 | 11.88
2018-01-28 16:30 | 12.96 | 12.85
2018-01-28 17:00 | 13.76 | 13.66
2018-01-28 17:30 | 14.43 | 14.33
2018-01-28 18:00 | 14.72 | 14.63
2018-01-28 18:30 | 14.65 | 14.57
2018-01-28 19:00 | 14.54 | 14.46
2018-01-28 19:30 | 14.5 | 14.39
2018-01-28 20:00 | 14.35 | 14.26
2018-01-28 20:30 | 13.67 | 13.6
2018-01-28 21:00 | 12.69 | 12.63
2018-01-28 21:30 | 11.62 | 11.57
2018-01-28 22:00 | 11.07 | 11.04
2018-01-28 22:30 | 10.42 | 10.4
2018-01-28 23:00 | 9.91 | 9.9
2018-01-28 23:30 | 8.84 | 8.82
2018-01-29 | 7.78 | 7.76
2018-01-29 00:30 | 7.1 | 7.08
2018-01-29 01:00 | 6.9 | 6.88
2018-01-29 01:30 | 6.35 | 6.33
2018-01-29 02:00 | 6.05 | 6.03
2018-01-29 02:30 | 5.89 | 5.88
2018-01-29 03:00 | 5.89 | 5.88
2018-01-29 03:30 | 5.81 | 5.8
2018-01-29 04:00 | 5.71 | 5.7
2018-01-29 04:30 | 5.82 | 5.8
2018-01-29 05:00 | 5.91 | 5.89
2018-01-29 05:30 | 6.12 | 6.11
2018-01-29 06:00 | 6.61 | 6.6
2018-01-29 06:30 | 6.99 | 6.99
2018-01-29 07:00 | 7.08 | 7.07
2018-01-29 07:30 | 7.39 | 7.38
2018-01-29 08:00 | 7.22 | 7.2
2018-01-29 08:30 | 7.54 | 7.52
2018-01-29 09:00 | 8.04 | 8.01
2018-01-29 09:30 | 6.87 | 6.82
2018-01-29 10:00 | 7.02 | 6.95
2018-01-29 10:30 | 8.8 | 8.73
2018-01-29 11:00 | 8.61 | 8.54
2018-01-29 11:30 | 7.14 | 7.05
2018-01-29 12:00 | 7.46 | 7.34
2018-01-29 12:30 | 8.2 | 8.06
2018-01-29 13:00 | 8.53 | 8.39
2018-01-29 13:30 | 8.84 | 8.71
2018-01-29 14:00 | 9.49 | 9.36
2018-01-29 14:30 | 9.86 | 9.7
2018-01-29 15:00 | 10.29 | 10.12
2018-01-29 15:30 | 11.03 | 10.87
2018-01-29 16:00 | 12.54 | 12.38
2018-01-29 16:30 | 13.56 | 13.43
2018-01-29 17:00 | 14.07 | 13.95
2018-01-29 17:30 | 14.86 | 14.76
2018-01-29 18:00 | 14.59 | 14.49
2018-01-29 18:30 | 14.56 | 14.48
2018-01-29 19:00 | 14.91 | 14.82
2018-01-29 19:30 | 14.47 | 14.36
2018-01-29 20:00 | 14.42 | 14.32
2018-01-29 20:30 | 14.24 | 14.16
2018-01-29 21:00 | 12.94 | 12.88
2018-01-29 21:30 | 11.85 | 11.81
2018-01-29 22:00 | 10.73 | 10.71
2018-01-29 22:30 | 9.94 | 9.92
2018-01-29 23:00 | 9.48 | 9.46
2018-01-29 23:30 | 8.25 | 8.24
2018-01-30 | 7.28 | 7.27
2018-01-30 00:30 | 6.6 | 6.59
2018-01-30 01:00 | 6.37 | 6.36
2018-01-30 01:30 | 6.09 | 6.08
2018-01-30 02:00 | 5.84 | 5.83
2018-01-30 02:30 | 5.67 | 5.66
2018-01-30 03:00 | 5.54 | 5.53
2018-01-30 03:30 | 5.51 | 5.5
2018-01-30 04:00 | 5.54 | 5.53
2018-01-30 04:30 | 5.59 | 5.58
2018-01-30 05:00 | 5.75 | 5.74
2018-01-30 05:30 | 5.8 | 5.78
2018-01-30 06:00 | 5.7 | 5.68
2018-01-30 06:30 | 5.74 | 5.73
2018-01-30 07:00 | 6.34 | 6.33
2018-01-30 07:30 | 6.14 | 6.12
2018-01-30 08:00 | 6.23 | 6.2
2018-01-30 08:30 | 5.57 | 5.53
2018-01-30 09:00 | 5.85 | 5.8
2018-01-30 09:30 | 6.14 | 6.1
2018-01-30 10:00 | 6.83 | 6.78
2018-01-30 10:30 | 7.31 | 7.25
2018-01-30 11:00 | 7.42 | 7.35
2018-01-30 11:30 | 7.94 | 7.85
2018-01-30 12:00 | 7.65 | 7.56
2018-01-30 12:30 | 8.7 | 8.6
2018-01-30 13:00 | 8.28 | 8.14
2018-01-30 13:30 | 10.19 | 10.05
2018-01-30 14:00 | 11.14 | 10.99
2018-01-30 14:30 | 11.09 | 10.93
2018-01-30 15:00 | 11.24 | 11.06
2018-01-30 15:30 | 13.46 | 13.3
2018-01-30 16:00 | 12.73 | 12.53
2018-01-30 16:30 | 14.17 | 13.98
2018-01-30 17:00 | 16.06 | 15.9
2018-01-30 17:30 | 15.91 | 15.74
2018-01-30 18:00 | 16.65 | 16.49
2018-01-30 18:30 | 17.02 | 16.86
2018-01-30 19:00 | 17.17 | 17.01
2018-01-30 19:30 | 17.13 | 16.95
2018-01-30 20:00 | 17.07 | 16.91
2018-01-30 20:30 | 16.42 | 16.29
2018-01-30 21:00 | 15.08 | 14.97
2018-01-30 21:30 | 13.41 | 13.33
2018-01-30 22:00 | 12.07 | 12
2018-01-30 22:30 | 11.13 | 11.08
2018-01-30 23:00 | 10.51 | 10.47
2018-01-30 23:30 | 9.02 | 9
2018-01-31 | 8.06 | 8.04
2018-01-31 00:30 | 7.48 | 7.47
2018-01-31 01:00 | 7.19 | 7.18
2018-01-31 01:30 | 6.73 | 6.72
2018-01-31 02:00 | 6.34 | 6.32
2018-01-31 02:30 | 6.21 | 6.19
2018-01-31 03:00 | 6.07 | 6.06
2018-01-31 03:30 | 5.92 | 5.91
2018-01-31 04:00 | 5.86 | 5.84
2018-01-31 04:30 | 5.94 | 5.92
2018-01-31 05:00 | 6.08 | 6.06
2018-01-31 05:30 | 6.35 | 6.34
2018-01-31 06:00 | 6.74 | 6.74
2018-01-31 06:30 | 6.93 | 6.93
2018-01-31 07:00 | 7.08 | 7.07
2018-01-31 07:30 | 7.42 | 7.41
2018-01-31 08:00 | 7.47 | 7.45
2018-01-31 08:30 | 7.17 | 7.13
2018-01-31 09:00 | 7.01 | 6.94
2018-01-31 09:30 | 7.33 | 7.24
2018-01-31 10:00 | 7.76 | 7.63
2018-01-31 10:30 | 8.23 | 8.08
2018-01-31 11:00 | 9.05 | 8.89
2018-01-31 11:30 | 10.09 | 9.9
2018-01-31 12:00 | 11.72 | 11.52
2018-01-31 12:30 | 13 | 12.79
2018-01-31 13:00 | 12.93 | 12.68
2018-01-31 13:30 | 14.75 | 14.45
2018-01-31 14:00 | 14.73 | 14.44
2018-01-31 14:30 | 15.25 | 14.95
2018-01-31 15:00 | 15.79 | 15.45
2018-01-31 15:30 | 17.84 | 17.57
2018-01-31 16:00 | 17.63 | 17.31
2018-01-31 16:30 | 18.28 | 18.01
2018-01-31 17:00 | 18.41 | 18.16
2018-01-31 17:30 | 18.19 | 17.96
2018-01-31 18:00 | 17.75 | 17.54
2018-01-31 18:30 | 17.22 | 17.03
2018-01-31 19:00 | 16.61 | 16.43
2018-01-31 19:30 | 15.97 | 15.8
2018-01-31 20:00 | 15.33 | 15.21
2018-01-31 20:30 | 14.68 | 14.57
2018-01-31 21:00 | 13.56 | 13.47
2018-01-31 21:30 | 12.76 | 12.69
2018-01-31 22:00 | 11.75 | 11.69
2018-01-31 22:30 | 10.88 | 10.84
2018-01-31 23:00 | 10.22 | 10.19
2018-01-31 23:30 | 8.73 | 8.71
2018-02-01 | 7.9 | 7.88
2018-02-01 00:30 | 7.38 | 7.36
2018-02-01 01:00 | 7.01 | 6.99
2018-02-01 01:30 | 6.61 | 6.59
2018-02-01 02:00 | 6.23 | 6.21
2018-02-01 02:30 | 6.08 | 6.07
2018-02-01 03:00 | 6 | 5.99
2018-02-01 03:30 | 5.99 | 5.97
2018-02-01 04:00 | 5.88 | 5.87
2018-02-01 04:30 | 5.96 | 5.95
2018-02-01 05:00 | 6.11 | 6.1
2018-02-01 05:30 | 6.43 | 6.42
2018-02-01 06:00 | 7.03 | 7.02
2018-02-01 06:30 | 7.22 | 7.22
2018-02-01 07:00 | 7.12 | 7.11
2018-02-01 07:30 | 7.32 | 7.31
2018-02-01 08:00 | 7.51 | 7.51
2018-02-01 08:30 | 6.91 | 6.9
2018-02-01 09:00 | 7.02 | 7.01
2018-02-01 09:30 | 7.33 | 7.32
2018-02-01 10:00 | 7.16 | 7.15
2018-02-01 10:30 | 5.42 | 5.4
2018-02-01 11:00 | 6.83 | 6.82
2018-02-01 11:30 | 7.22 | 7.21
2018-02-01 12:00 | 7.43 | 7.42
2018-02-01 12:30 | 7.36 | 7.35
2018-02-01 13:00 | 6.32 | 6.3
2018-02-01 13:30 | 6.35 | 6.33
2018-02-01 14:00 | 7.01 | 6.99
2018-02-01 14:30 | 7.21 | 7.2
2018-02-01 15:00 | 7.1 | 7.09
2018-02-01 15:30 | 7.22 | 7.2
2018-02-01 16:00 | 8.28 | 8.27
2018-02-01 16:30 | 8.35 | 8.33
2018-02-01 17:00 | 9.24 | 9.23
2018-02-01 17:30 | 9.82 | 9.81
2018-02-01 18:00 | 10.28 | 10.27
2018-02-01 18:30 | 10.7 | 10.69
2018-02-01 19:00 | 11.15 | 11.13
2018-02-01 19:30 | 11.34 | 11.31
2018-02-01 20:00 | 11.42 | 11.4
2018-02-01 20:30 | 11.18 | 11.16
2018-02-01 21:00 | 10.48 | 10.46
2018-02-01 21:30 | 9.85 | 9.84
2018-02-01 22:00 | 8.94 | 8.93
2018-02-01 22:30 | 8.46 | 8.45
2018-02-01 23:00 | 8.19 | 8.18
2018-02-01 23:30 | 7.09 | 7.08
2018-02-02 | 6.19 | 6.18
2018-02-02 00:30 | 5.63 | 5.62
2018-02-02 01:00 | 5.44 | 5.42
2018-02-02 01:30 | 5.12 | 5.11
2018-02-02 02:00 | 4.99 | 4.98
2018-02-02 02:30 | 4.88 | 4.86
2018-02-02 03:00 | 4.72 | 4.71
2018-02-02 03:30 | 4.81 | 4.79
2018-02-02 04:00 | 4.89 | 4.88
2018-02-02 04:30 | 4.99 | 4.98
2018-02-02 05:00 | 5.1 | 5.09
2018-02-02 05:30 | 5.43 | 5.41
2018-02-02 06:00 | 5.79 | 5.77
2018-02-02 06:30 | 6.61 | 6.6
2018-02-02 07:00 | 6.97 | 6.96
2018-02-02 07:30 | 7.44 | 7.43
2018-02-02 08:00 | 7.27 | 7.26
2018-02-02 08:30 | 7.85 | 7.85
2018-02-02 09:00 | 7.79 | 7.78
2018-02-02 09:30 | 6.94 | 6.94
2018-02-02 10:00 | 6.76 | 6.75
2018-02-02 10:30 | 6.45 | 6.44
2018-02-02 11:00 | 6.14 | 6.13
2018-02-02 11:30 | 5.8 | 5.79
2018-02-02 12:00 | 5.94 | 5.93
2018-02-02 12:30 | 6.41 | 6.4
2018-02-02 13:00 | 6.37 | 6.36
2018-02-02 13:30 | 5.76 | 5.75
2018-02-02 14:00 | 5.44 | 5.42
2018-02-02 14:30 | 6.44 | 6.42
2018-02-02 15:00 | 6.35 | 6.33
2018-02-02 15:30 | 6.55 | 6.53
2018-02-02 16:00 | 7.23 | 7.21
2018-02-02 16:30 | 7.54 | 7.52
2018-02-02 17:00 | 8.27 | 8.25
2018-02-02 17:30 | 8.52 | 8.51
2018-02-02 18:00 | 8.81 | 8.79
2018-02-02 18:30 | 8.97 | 8.95
2018-02-02 19:00 | 9.75 | 9.73
2018-02-02 19:30 | 9.78 | 9.76
2018-02-02 20:00 | 9.95 | 9.93
2018-02-02 20:30 | 9.8 | 9.78
2018-02-02 21:00 | 9.35 | 9.33
2018-02-02 21:30 | 8.67 | 8.65
2018-02-02 22:00 | 7.97 | 7.96
2018-02-02 22:30 | 7.77 | 7.76
2018-02-02 23:00 | 7.63 | 7.62
2018-02-02 23:30 | 6.64 | 6.63
2018-02-03 | 5.86 | 5.84
2018-02-03 00:30 | 5.4 | 5.38
2018-02-03 01:00 | 5.14 | 5.13
2018-02-03 01:30 | 4.81 | 4.79
2018-02-03 02:00 | 4.54 | 4.52
2018-02-03 02:30 | 4.41 | 4.39
2018-02-03 03:00 | 4.41 | 4.38
2018-02-03 03:30 | 4.34 | 4.32
2018-02-03 04:00 | 4.32 | 4.29
2018-02-03 04:30 | 4.28 | 4.25
2018-02-03 05:00 | 4.4 | 4.38
2018-02-03 05:30 | 4.46 | 4.43
2018-02-03 06:00 | 4.4 | 4.33
2018-02-03 06:30 | 4.63 | 4.56
2018-02-03 07:00 | 4.91 | 4.84
2018-02-03 07:30 | 5.46 | 5.41
2018-02-03 08:00 | 5.59 | 5.54
2018-02-03 08:30 | 6.27 | 6.25
2018-02-03 09:00 | 6.8 | 6.78
2018-02-03 09:30 | 6.93 | 6.91
2018-02-03 10:00 | 7.26 | 7.24
2018-02-03 10:30 | 7.09 | 7.07
2018-02-03 11:00 | 7.15 | 7.13
2018-02-03 11:30 | 7.48 | 7.45
2018-02-03 12:00 | 7.1 | 7.08
2018-02-03 12:30 | 7.59 | 7.57
2018-02-03 13:00 | 7.41 | 7.39
2018-02-03 13:30 | 7.78 | 7.76
2018-02-03 14:00 | 7.62 | 7.6
2018-02-03 14:30 | 7.63 | 7.62
2018-02-03 15:00 | 7.64 | 7.62
2018-02-03 15:30 | 7.52 | 7.5
2018-02-03 16:00 | 7.56 | 7.55
2018-02-03 16:30 | 7.79 | 7.78
2018-02-03 17:00 | 7.95 | 7.94
2018-02-03 17:30 | 8.31 | 8.3
2018-02-03 18:00 | 8.78 | 8.77
2018-02-03 18:30 | 9.09 | 9.08
2018-02-03 19:00 | 9.37 | 9.36
2018-02-03 19:30 | 9.72 | 9.7
2018-02-03 20:00 | 9.73 | 9.71
2018-02-03 20:30 | 9.69 | 9.68
2018-02-03 21:00 | 9.04 | 9.02
2018-02-03 21:30 | 8.48 | 8.47
2018-02-03 22:00 | 8.03 | 8.02
2018-02-03 22:30 | 7.79 | 7.78
2018-02-03 23:00 | 7.7 | 7.69
2018-02-03 23:30 | 6.84 | 6.83
2018-02-04 | 6.03 | 6.02
2018-02-04 00:30 | 5.37 | 5.35
2018-02-04 01:00 | 5.02 | 5
2018-02-04 01:30 | 4.76 | 4.73
2018-02-04 02:00 | 4.47 | 4.45
2018-02-04 02:30 | 4.38 | 4.36
2018-02-04 03:00 | 4.2 | 4.17
2018-02-04 03:30 | 4.18 | 4.15
2018-02-04 04:00 | 4.13 | 4.09
2018-02-04 04:30 | 4.22 | 4.18
2018-02-04 05:00 | 4.16 | 4.12
2018-02-04 05:30 | 4.05 | 3.98
2018-02-04 06:00 | 4.16 | 4.05
2018-02-04 06:30 | 4.2 | 4.09
2018-02-04 07:00 | 4.54 | 4.46
2018-02-04 07:30 | 4.67 | 4.61
2018-02-04 08:00 | 4.75 | 4.7
2018-02-04 08:30 | 4.62 | 4.58
2018-02-04 09:00 | 4.34 | 4.32
2018-02-04 09:30 | 4.26 | 4.23
2018-02-04 10:00 | 4.8 | 4.76
2018-02-04 10:30 | 4.48 | 4.43
2018-02-04 11:00 | 4.75 | 4.71
2018-02-04 11:30 | 4.63 | 4.58
2018-02-04 12:00 | 5.45 | 5.4
2018-02-04 12:30 | 5.67 | 5.61
2018-02-04 13:00 | 5.83 | 5.78
2018-02-04 13:30 | 5.33 | 5.27
2018-02-04 14:00 | 5.91 | 5.86
2018-02-04 14:30 | 5.61 | 5.56
2018-02-04 15:00 | 6.24 | 6.19
2018-02-04 15:30 | 6.77 | 6.72
2018-02-04 16:00 | 7.29 | 7.26
2018-02-04 16:30 | 8.2 | 8.17
2018-02-04 17:00 | 9.28 | 9.25
2018-02-04 17:30 | 9.99 | 9.97
2018-02-04 18:00 | 10.63 | 10.61
2018-02-04 18:30 | 10.85 | 10.83
2018-02-04 19:00 | 11.26 | 11.24
2018-02-04 19:30 | 11.58 | 11.56
2018-02-04 20:00 | 11.52 | 11.5
2018-02-04 20:30 | 11.08 | 11.06
2018-02-04 21:00 | 10.38 | 10.36
2018-02-04 21:30 | 9.59 | 9.57
2018-02-04 22:00 | 8.76 | 8.75
2018-02-04 22:30 | 8.3 | 8.29
2018-02-04 23:00 | 8 | 7.99
2018-02-04 23:30 | 6.92 | 6.91
2018-02-05 | 6.11 | 6.1
2018-02-05 00:30 | 5.45 | 5.43
2018-02-05 01:00 | 5.22 | 5.21
2018-02-05 01:30 | 4.94 | 4.93
2018-02-05 02:00 | 4.65 | 4.64
2018-02-05 02:30 | 4.62 | 4.6
2018-02-05 03:00 | 4.53 | 4.51
2018-02-05 03:30 | 4.47 | 4.45
2018-02-05 04:00 | 4.43 | 4.4
2018-02-05 04:30 | 4.56 | 4.54
2018-02-05 05:00 | 4.83 | 4.81
2018-02-05 05:30 | 4.98 | 4.94
2018-02-05 06:00 | 5.26 | 5.2
2018-02-05 06:30 | 5.59 | 5.56
2018-02-05 07:00 | 5.58 | 5.55
2018-02-05 07:30 | 5.38 | 5.36
2018-02-05 08:00 | 5.13 | 5.12
2018-02-05 08:30 | 4.51 | 4.49
2018-02-05 09:00 | 4.04 | 4.02
2018-02-05 09:30 | 3.8 | 3.77
2018-02-05 10:00 | 3.7 | 3.67
2018-02-05 10:30 | 3.85 | 3.81
2018-02-05 11:00 | 3.81 | 3.77
2018-02-05 11:30 | 4.38 | 4.35
2018-02-05 12:00 | 4.88 | 4.84
2018-02-05 12:30 | 5.46 | 5.42
2018-02-05 13:00 | 5.99 | 5.95
2018-02-05 13:30 | 5.96 | 5.91
2018-02-05 14:00 | 6.94 | 6.89
2018-02-05 14:30 | 7.42 | 7.37
2018-02-05 15:00 | 7.23 | 7.19
2018-02-05 15:30 | 7.84 | 7.8
2018-02-05 16:00 | 8.9 | 8.86
2018-02-05 16:30 | 9.13 | 9.1
2018-02-05 17:00 | 10.62 | 10.6
2018-02-05 17:30 | 11.15 | 11.14
2018-02-05 18:00 | 11.49 | 11.48
2018-02-05 18:30 | 11.72 | 11.71
2018-02-05 19:00 | 12.24 | 12.22
2018-02-05 19:30 | 12.28 | 12.26
2018-02-05 20:00 | 12.2 | 12.18
2018-02-05 20:30 | 11.91 | 11.89
2018-02-05 21:00 | 11.26 | 11.25
2018-02-05 21:30 | 10.45 | 10.44
2018-02-05 22:00 | 9.64 | 9.63
2018-02-05 22:30 | 8.84 | 8.83
2018-02-05 23:00 | 8.1 | 8.09
2018-02-05 23:30 | 6.91 | 6.9
2018-02-06 | 5.92 | 5.91
2018-02-06 00:30 | 5.43 | 5.42
2018-02-06 01:00 | 5.15 | 5.14
2018-02-06 01:30 | 4.91 | 4.89
2018-02-06 02:00 | 4.64 | 4.62
2018-02-06 02:30 | 4.52 | 4.5
2018-02-06 03:00 | 4.43 | 4.4
2018-02-06 03:30 | 4.5 | 4.48
2018-02-06 04:00 | 4.49 | 4.47
2018-02-06 04:30 | 4.71 | 4.69
2018-02-06 05:00 | 4.89 | 4.87
2018-02-06 05:30 | 5.15 | 5.12
2018-02-06 06:00 | 5.48 | 5.44
2018-02-06 06:30 | 6.2 | 6.18
2018-02-06 07:00 | 6.22 | 6.21
2018-02-06 07:30 | 5.98 | 5.97
2018-02-06 08:00 | 6.2 | 6.2
2018-02-06 08:30 | 5.44 | 5.43
2018-02-06 09:00 | 4.37 | 4.35
2018-02-06 09:30 | 4.53 | 4.5
2018-02-06 10:00 | 4.4 | 4.38
2018-02-06 10:30 | 4.97 | 4.95
2018-02-06 11:00 | 4.59 | 4.56
2018-02-06 11:30 | 4.92 | 4.89
2018-02-06 12:00 | 4.28 | 4.24
2018-02-06 12:30 | 5.3 | 5.26
2018-02-06 13:00 | 6.76 | 6.72
2018-02-06 13:30 | 7.49 | 7.45
2018-02-06 14:00 | 7.88 | 7.84
2018-02-06 14:30 | 7.46 | 7.42
2018-02-06 15:00 | 7.6 | 7.55
2018-02-06 15:30 | 8.34 | 8.3
2018-02-06 16:00 | 8.71 | 8.68
2018-02-06 16:30 | 8.72 | 8.69
2018-02-06 17:00 | 10.02 | 9.99
2018-02-06 17:30 | 10.52 | 10.5
2018-02-06 18:00 | 11.28 | 11.26
2018-02-06 18:30 | 12.04 | 12.01
2018-02-06 19:00 | 12.56 | 12.53
2018-02-06 19:30 | 12.56 | 12.52
2018-02-06 20:00 | 12.73 | 12.69
2018-02-06 20:30 | 12.1 | 12.08
2018-02-06 21:00 | 11.24 | 11.23
2018-02-06 21:30 | 10.27 | 10.26
2018-02-06 22:00 | 9.17 | 9.16
2018-02-06 22:30 | 8.51 | 8.5
2018-02-06 23:00 | 8.14 | 8.13
2018-02-06 23:30 | 6.87 | 6.86
2018-02-07 | 5.95 | 5.94
2018-02-07 00:30 | 5.42 | 5.41
2018-02-07 01:00 | 5.24 | 5.23
2018-02-07 01:30 | 4.96 | 4.95
2018-02-07 02:00 | 4.77 | 4.75
2018-02-07 02:30 | 4.55 | 4.53
2018-02-07 03:00 | 4.47 | 4.45
2018-02-07 03:30 | 4.49 | 4.47
2018-02-07 04:00 | 4.54 | 4.51
2018-02-07 04:30 | 4.66 | 4.64
2018-02-07 05:00 | 4.88 | 4.86
2018-02-07 05:30 | 5.17 | 5.14
2018-02-07 06:00 | 5.42 | 5.37
2018-02-07 06:30 | 5.68 | 5.65
2018-02-07 07:00 | 5.67 | 5.65
2018-02-07 07:30 | 5.61 | 5.6
2018-02-07 08:00 | 5.06 | 5.05
2018-02-07 08:30 | 4.35 | 4.33
2018-02-07 09:00 | 3.79 | 3.77
2018-02-07 09:30 | 4.06 | 4.03
2018-02-07 10:00 | 4.32 | 4.3
2018-02-07 10:30 | 4.18 | 4.14
2018-02-07 11:00 | 3.9 | 3.87
2018-02-07 11:30 | 4.25 | 4.21
2018-02-07 12:00 | 3.74 | 3.7
2018-02-07 12:30 | 4.29 | 4.24
2018-02-07 13:00 | 5.1 | 5.05
2018-02-07 13:30 | 5.5 | 5.45
2018-02-07 14:00 | 5.23 | 5.17
2018-02-07 14:30 | 6.06 | 6
2018-02-07 15:00 | 6.12 | 6.06
2018-02-07 15:30 | 6.99 | 6.93
2018-02-07 16:00 | 8.29 | 8.24
2018-02-07 16:30 | 9.46 | 9.41
2018-02-07 17:00 | 10.29 | 10.24
2018-02-07 17:30 | 11.08 | 11.04
2018-02-07 18:00 | 11.44 | 11.41
2018-02-07 18:30 | 11.98 | 11.95
2018-02-07 19:00 | 12.62 | 12.58
2018-02-07 19:30 | 12.93 | 12.88
2018-02-07 20:00 | 12.84 | 12.79
2018-02-07 20:30 | 12.4 | 12.37
2018-02-07 21:00 | 11.65 | 11.63
2018-02-07 21:30 | 10.71 | 10.69
2018-02-07 22:00 | 9.6 | 9.59
2018-02-07 22:30 | 8.61 | 8.6
2018-02-07 23:00 | 8.2 | 8.19
2018-02-07 23:30 | 7.03 | 7.02
2018-02-08 | 6.15 | 6.14
2018-02-08 00:30 | 5.58 | 5.57
2018-02-08 01:00 | 5.37 | 5.36
2018-02-08 01:30 | 5.18 | 5.17
2018-02-08 02:00 | 4.8 | 4.79
2018-02-08 02:30 | 4.66 | 4.64
2018-02-08 03:00 | 4.54 | 4.52
2018-02-08 03:30 | 4.58 | 4.56
2018-02-08 04:00 | 4.56 | 4.54
2018-02-08 04:30 | 4.66 | 4.64
2018-02-08 05:00 | 4.88 | 4.87
2018-02-08 05:30 | 5.17 | 5.14
2018-02-08 06:00 | 5.76 | 5.72
2018-02-08 06:30 | 6.3 | 6.28
2018-02-08 07:00 | 6.34 | 6.32
2018-02-08 07:30 | 6.14 | 6.14
2018-02-08 08:00 | 5.69 | 5.69
2018-02-08 08:30 | 5.38 | 5.37
2018-02-08 09:00 | 4.23 | 4.21
2018-02-08 09:30 | 4.6 | 4.59
2018-02-08 10:00 | 5.01 | 4.99
2018-02-08 10:30 | 4.25 | 4.23
2018-02-08 11:00 | 4.9 | 4.88
2018-02-08 11:30 | 4.89 | 4.87
2018-02-08 12:00 | 5.65 | 5.63
2018-02-08 12:30 | 5.3 | 5.28
2018-02-08 13:00 | 4.59 | 4.55
2018-02-08 13:30 | 5.83 | 5.8
2018-02-08 14:00 | 6.29 | 6.26
2018-02-08 14:30 | 6.69 | 6.64
2018-02-08 15:00 | 7.68 | 7.64
2018-02-08 15:30 | 7.32 | 7.28
2018-02-08 16:00 | 9.01 | 8.96
2018-02-08 16:30 | 9.77 | 9.74
2018-02-08 17:00 | 10.34 | 10.31
2018-02-08 17:30 | 10.73 | 10.7
2018-02-08 18:00 | 11.14 | 11.11
2018-02-08 18:30 | 11.58 | 11.55
2018-02-08 19:00 | 12.15 | 12.11
2018-02-08 19:30 | 12.55 | 12.5
2018-02-08 20:00 | 12.54 | 12.5
2018-02-08 20:30 | 12.09 | 12.05
2018-02-08 21:00 | 11.4 | 11.37
2018-02-08 21:30 | 10.55 | 10.54
2018-02-08 22:00 | 9.76 | 9.75
2018-02-08 22:30 | 8.83 | 8.82
2018-02-08 23:00 | 8.14 | 8.12
2018-02-08 23:30 | 6.94 | 6.93
2018-02-09 | 6.1 | 6.09
2018-02-09 00:30 | 5.49 | 5.48
2018-02-09 01:00 | 5.22 | 5.21
2018-02-09 01:30 | 5.01 | 4.99
2018-02-09 02:00 | 4.7 | 4.68
2018-02-09 02:30 | 4.53 | 4.51
2018-02-09 03:00 | 4.53 | 4.51
2018-02-09 03:30 | 4.5 | 4.47
2018-02-09 04:00 | 4.51 | 4.48
2018-02-09 04:30 | 4.59 | 4.56
2018-02-09 05:00 | 4.8 | 4.78
2018-02-09 05:30 | 5.08 | 5.05
2018-02-09 06:00 | 5.83 | 5.79
2018-02-09 06:30 | 6.13 | 6.1
2018-02-09 07:00 | 6.13 | 6.1
2018-02-09 07:30 | 6.05 | 6.04
2018-02-09 08:00 | 5.58 | 5.57
2018-02-09 08:30 | 5.08 | 5.07
2018-02-09 09:00 | 4.5 | 4.48
2018-02-09 09:30 | 4.74 | 4.72
2018-02-09 10:00 | 5.91 | 5.89
2018-02-09 10:30 | 4.87 | 4.83
2018-02-09 11:00 | 4.25 | 4.19
2018-02-09 11:30 | 4.07 | 3.99
2018-02-09 12:00 | 4.5 | 4.43
2018-02-09 12:30 | 4.99 | 4.92
2018-02-09 13:00 | 5.44 | 5.35
2018-02-09 13:30 | 6.07 | 5.97
2018-02-09 14:00 | 6.94 | 6.84
2018-02-09 14:30 | 7.64 | 7.53
2018-02-09 15:00 | 8.23 | 8.13
2018-02-09 15:30 | 9.22 | 9.11
2018-02-09 16:00 | 10.58 | 10.46
2018-02-09 16:30 | 11.79 | 11.67
2018-02-09 17:00 | 12.68 | 12.57
2018-02-09 17:30 | 13.19 | 13.09
2018-02-09 18:00 | 13.17 | 13.08
2018-02-09 18:30 | 13.09 | 13.01
2018-02-09 19:00 | 13.06 | 12.99
2018-02-09 19:30 | 13.17 | 13.08
2018-02-09 20:00 | 12.96 | 12.88
2018-02-09 20:30 | 12.45 | 12.39
2018-02-09 21:00 | 11.55 | 11.51
2018-02-09 21:30 | 10.64 | 10.62
2018-02-09 22:00 | 9.84 | 9.82
2018-02-09 22:30 | 9.32 | 9.31
2018-02-09 23:00 | 8.95 | 8.94
2018-02-09 23:30 | 7.77 | 7.76
2018-02-10 | 6.84 | 6.82
2018-02-10 00:30 | 6.2 | 6.19
2018-02-10 01:00 | 5.95 | 5.94
2018-02-10 01:30 | 5.66 | 5.65
2018-02-10 02:00 | 5.32 | 5.31
2018-02-10 02:30 | 5 | 4.99
2018-02-10 03:00 | 4.88 | 4.87
2018-02-10 03:30 | 4.91 | 4.9
2018-02-10 04:00 | 4.73 | 4.72
2018-02-10 04:30 | 4.84 | 4.83
2018-02-10 05:00 | 4.82 | 4.8
2018-02-10 05:30 | 4.76 | 4.73
2018-02-10 06:00 | 4.67 | 4.61
2018-02-10 06:30 | 4.75 | 4.69
2018-02-10 07:00 | 4.82 | 4.77
2018-02-10 07:30 | 4.91 | 4.88
2018-02-10 08:00 | 4.98 | 4.96
2018-02-10 08:30 | 5.36 | 5.34
2018-02-10 09:00 | 5.54 | 5.5
2018-02-10 09:30 | 5.5 | 5.46
2018-02-10 10:00 | 5.71 | 5.65
2018-02-10 10:30 | 6.02 | 5.95
2018-02-10 11:00 | 6.17 | 6.1
2018-02-10 11:30 | 6.72 | 6.63
2018-02-10 12:00 | 7.54 | 7.44
2018-02-10 12:30 | 8.55 | 8.41
2018-02-10 13:00 | 9.51 | 9.35
2018-02-10 13:30 | 10.56 | 10.38
2018-02-10 14:00 | 11.57 | 11.38
2018-02-10 14:30 | 12.64 | 12.43
2018-02-10 15:00 | 13.8 | 13.59
2018-02-10 15:30 | 15.05 | 14.81
2018-02-10 16:00 | 16.11 | 15.88
2018-02-10 16:30 | 17.08 | 16.85
2018-02-10 17:00 | 17.55 | 17.32
2018-02-10 17:30 | 17.51 | 17.3
2018-02-10 18:00 | 17.08 | 16.9
2018-02-10 18:30 | 15.47 | 15.31
2018-02-10 19:00 | 15.21 | 15.06
2018-02-10 19:30 | 14.9 | 14.74
2018-02-10 20:00 | 14.78 | 14.63
2018-02-10 20:30 | 13.88 | 13.78
2018-02-10 21:00 | 12.97 | 12.88
2018-02-10 21:30 | 12.19 | 12.13
2018-02-10 22:00 | 11.23 | 11.19
2018-02-10 22:30 | 10.8 | 10.77
2018-02-10 23:00 | 10.32 | 10.3
2018-02-10 23:30 | 9.13 | 9.11
2018-02-11 | 8.14 | 8.12
2018-02-11 00:30 | 7.51 | 7.49
2018-02-11 01:00 | 7.14 | 7.12
2018-02-11 01:30 | 6.64 | 6.63
2018-02-11 02:00 | 6.2 | 6.18
2018-02-11 02:30 | 6.01 | 5.99
2018-02-11 03:00 | 5.82 | 5.8
2018-02-11 03:30 | 5.73 | 5.72
2018-02-11 04:00 | 5.54 | 5.52
2018-02-11 04:30 | 5.5 | 5.48
2018-02-11 05:00 | 5.46 | 5.44
2018-02-11 05:30 | 5.32 | 5.3
2018-02-11 06:00 | 5.26 | 5.24
2018-02-11 06:30 | 5.32 | 5.29
2018-02-11 07:00 | 5.32 | 5.3
2018-02-11 07:30 | 5.59 | 5.57
2018-02-11 08:00 | 5.91 | 5.89
2018-02-11 08:30 | 6.57 | 6.54
2018-02-11 09:00 | 7.03 | 7
2018-02-11 09:30 | 7.67 | 7.62
2018-02-11 10:00 | 8.63 | 8.55
2018-02-11 10:30 | 9.32 | 9.21
2018-02-11 11:00 | 10.16 | 10.02
2018-02-11 11:30 | 11.32 | 11.13
2018-02-11 12:00 | 12.49 | 12.26
2018-02-11 12:30 | 14.03 | 13.78
2018-02-11 13:00 | 15.07 | 14.78
2018-02-11 13:30 | 16.28 | 15.95
2018-02-11 14:00 | 17.43 | 17.09
2018-02-11 14:30 | 18.52 | 18.16
2018-02-11 15:00 | 19.65 | 19.27
2018-02-11 15:30 | 20.82 | 20.44
2018-02-11 16:00 | 21.37 | 21
2018-02-11 16:30 | 22.02 | 21.66
2018-02-11 17:00 | 22.66 | 22.33
2018-02-11 17:30 | 22.15 | 21.85
2018-02-11 18:00 | 22.1 | 21.8
2018-02-11 18:30 | 18.71 | 18.47
2018-02-11 19:00 | 16.94 | 16.74
2018-02-11 19:30 | 15.69 | 15.54
2018-02-11 20:00 | 15.02 | 14.9
2018-02-11 20:30 | 14.11 | 14.03
2018-02-11 21:00 | 12.86 | 12.8
2018-02-11 21:30 | 11.74 | 11.69
2018-02-11 22:00 | 10.77 | 10.74
2018-02-11 22:30 | 10.16 | 10.13
2018-02-11 23:00 | 9.7 | 9.68
2018-02-11 23:30 | 8.39 | 8.38
2018-02-12 | 7.49 | 7.48
2018-02-12 00:30 | 6.86 | 6.84
2018-02-12 01:00 | 6.49 | 6.48
2018-02-12 01:30 | 6.17 | 6.16
2018-02-12 02:00 | 5.86 | 5.85
2018-02-12 02:30 | 5.69 | 5.67
2018-02-12 03:00 | 5.58 | 5.56
2018-02-12 03:30 | 5.58 | 5.57
2018-02-12 04:00 | 5.56 | 5.54
2018-02-12 04:30 | 5.63 | 5.62
2018-02-12 05:00 | 5.83 | 5.81
2018-02-12 05:30 | 6.09 | 6.07
2018-02-12 06:00 | 6.06 | 6.05
2018-02-12 06:30 | 6.25 | 6.24
2018-02-12 07:00 | 6.55 | 6.54
2018-02-12 07:30 | 6.75 | 6.74
2018-02-12 08:00 | 6.76 | 6.74
2018-02-12 08:30 | 6.38 | 6.35
2018-02-12 09:00 | 6.82 | 6.77
2018-02-12 09:30 | 7.29 | 7.21
2018-02-12 10:00 | 7.76 | 7.66
2018-02-12 10:30 | 8.41 | 8.29
2018-02-12 11:00 | 9.01 | 8.85
2018-02-12 11:30 | 9.88 | 9.69
2018-02-12 12:00 | 10.91 | 10.69
2018-02-12 12:30 | 11.87 | 11.62
2018-02-12 13:00 | 12.96 | 12.7
2018-02-12 13:30 | 14.15 | 13.81
2018-02-12 14:00 | 15.24 | 14.84
2018-02-12 14:30 | 15.88 | 15.48
2018-02-12 15:00 | 16.56 | 16.19
2018-02-12 15:30 | 18.04 | 17.73
2018-02-12 16:00 | 19.14 | 18.81
2018-02-12 16:30 | 20.06 | 19.69
2018-02-12 17:00 | 20.94 | 20.55
2018-02-12 17:30 | 21.55 | 21.23
2018-02-12 18:00 | 21.92 | 21.61
2018-02-12 18:30 | 21.64 | 21.38
2018-02-12 19:00 | 21.93 | 21.64
2018-02-12 19:30 | 21.84 | 21.54
2018-02-12 20:00 | 21.21 | 20.92
2018-02-12 20:30 | 20.38 | 20.11
2018-02-12 21:00 | 18.74 | 18.49
2018-02-12 21:30 | 16.81 | 16.6
2018-02-12 22:00 | 15.1 | 14.95
2018-02-12 22:30 | 13.85 | 13.73
2018-02-12 23:00 | 12.95 | 12.85
2018-02-12 23:30 | 11.33 | 11.26
2018-02-13 | 10.17 | 10.11
2018-02-13 00:30 | 9.44 | 9.38
2018-02-13 01:00 | 9.22 | 9.17
2018-02-13 01:30 | 8.78 | 8.73
2018-02-13 02:00 | 8.49 | 8.45
2018-02-13 02:30 | 8.25 | 8.21
2018-02-13 03:00 | 8.21 | 8.17
2018-02-13 03:30 | 8.24 | 8.2
2018-02-13 04:00 | 8.15 | 8.11
2018-02-13 04:30 | 8.21 | 8.18
2018-02-13 05:00 | 8.38 | 8.35
2018-02-13 05:30 | 8.64 | 8.6
2018-02-13 06:00 | 9.06 | 9.04
2018-02-13 06:30 | 9.43 | 9.41
2018-02-13 07:00 | 9.94 | 9.9
2018-02-13 07:30 | 10.41 | 10.35
2018-02-13 08:00 | 11.21 | 11.14
2018-02-13 08:30 | 11.75 | 11.66
2018-02-13 09:00 | 10.74 | 10.63
2018-02-13 09:30 | 9.73 | 9.58
2018-02-13 10:00 | 10.66 | 10.48
2018-02-13 10:30 | 11.27 | 11.07
2018-02-13 11:00 | 12.09 | 11.87
2018-02-13 11:30 | 12.01 | 11.76
2018-02-13 12:00 | 12.52 | 12.26
2018-02-13 12:30 | 13.66 | 13.33
2018-02-13 13:00 | 14.61 | 14.23
2018-02-13 13:30 | 15.03 | 14.67
2018-02-13 14:00 | 15.84 | 15.47
2018-02-13 14:30 | 16.59 | 16.15
2018-02-13 15:00 | 17.3 | 16.88
2018-02-13 15:30 | 18.4 | 18.01
2018-02-13 16:00 | 19.85 | 19.45
2018-02-13 16:30 | 21.68 | 21.34
2018-02-13 17:00 | 21.24 | 20.9
2018-02-13 17:30 | 21.32 | 21.01
2018-02-13 18:00 | 21.45 | 21.16
2018-02-13 18:30 | 21.24 | 20.95
2018-02-13 19:00 | 22.01 | 21.67
2018-02-13 19:30 | 21.12 | 20.79
2018-02-13 20:00 | 19.4 | 19.2
2018-02-13 20:30 | 17.34 | 17.17
2018-02-13 21:00 | 15.41 | 15.28
2018-02-13 21:30 | 13.39 | 13.3
2018-02-13 22:00 | 12.02 | 11.95
2018-02-13 22:30 | 11 | 10.96
2018-02-13 23:00 | 10.36 | 10.33
2018-02-13 23:30 | 9.1 | 9.08
2018-02-14 | 8.03 | 8.02
2018-02-14 00:30 | 7.37 | 7.35
2018-02-14 01:00 | 7.06 | 7.05
2018-02-14 01:30 | 6.76 | 6.75
2018-02-14 02:00 | 6.42 | 6.4
2018-02-14 02:30 | 6.24 | 6.22
2018-02-14 03:00 | 6.12 | 6.1
2018-02-14 03:30 | 6.07 | 6.05
2018-02-14 04:00 | 5.92 | 5.9
2018-02-14 04:30 | 6.07 | 6.05
2018-02-14 05:00 | 6.23 | 6.22
2018-02-14 05:30 | 6.49 | 6.48
2018-02-14 06:00 | 6.95 | 6.94
2018-02-14 06:30 | 7.39 | 7.38
2018-02-14 07:00 | 7.64 | 7.63
2018-02-14 07:30 | 7.79 | 7.78
2018-02-14 08:00 | 7.84 | 7.82
2018-02-14 08:30 | 7.6 | 7.56
2018-02-14 09:00 | 7.78 | 7.71
2018-02-14 09:30 | 8.45 | 8.34
2018-02-14 10:00 | 9 | 8.86
2018-02-14 10:30 | 9.58 | 9.4
2018-02-14 11:00 | 10.46 | 10.26
2018-02-14 11:30 | 11.37 | 11.13
2018-02-14 12:00 | 12.42 | 12.13
2018-02-14 12:30 | 13.59 | 13.25
2018-02-14 13:00 | 14.55 | 14.17
2018-02-14 13:30 | 15.66 | 15.3
2018-02-14 14:00 | 16.53 | 16.16
2018-02-14 14:30 | 17.52 | 17.04
2018-02-14 15:00 | 18.31 | 17.86
2018-02-14 15:30 | 19.38 | 19
2018-02-14 16:00 | 21.23 | 20.8
2018-02-14 16:30 | 22.87 | 22.45
2018-02-14 17:00 | 22.8 | 22.35
2018-02-14 17:30 | 23.19 | 22.79
2018-02-14 18:00 | 23.46 | 23.07
2018-02-14 18:30 | 23.04 | 22.69
2018-02-14 19:00 | 23.17 | 22.76
2018-02-14 19:30 | 22.93 | 22.52
2018-02-14 20:00 | 21.96 | 21.54
2018-02-14 20:30 | 21.28 | 20.92
2018-02-14 21:00 | 19.99 | 19.69
2018-02-14 21:30 | 18.54 | 18.29
2018-02-14 22:00 | 16.85 | 16.63
2018-02-14 22:30 | 14.89 | 14.72
2018-02-14 23:00 | 13.66 | 13.54
2018-02-14 23:30 | 12.41 | 12.3
2018-02-15 | 11.04 | 10.95
2018-02-15 00:30 | 10.16 | 10.1
2018-02-15 01:00 | 9.51 | 9.46
2018-02-15 01:30 | 9.08 | 9.03
2018-02-15 02:00 | 9.32 | 9.28
2018-02-15 02:30 | 8.92 | 8.88
2018-02-15 03:00 | 8.46 | 8.42
2018-02-15 03:30 | 8.19 | 8.15
2018-02-15 04:00 | 7.96 | 7.93
2018-02-15 04:30 | 7.78 | 7.75
2018-02-15 05:00 | 7.83 | 7.81
2018-02-15 05:30 | 7.81 | 7.79
2018-02-15 06:00 | 7.81 | 7.8
2018-02-15 06:30 | 8.29 | 8.27
2018-02-15 07:00 | 8.62 | 8.6
2018-02-15 07:30 | 8.99 | 8.96
2018-02-15 08:00 | 9.21 | 9.16
2018-02-15 08:30 | 9.16 | 9.08
2018-02-15 09:00 | 9.53 | 9.4
2018-02-15 09:30 | 10.39 | 10.22
2018-02-15 10:00 | 11.14 | 10.93
2018-02-15 10:30 | 11.85 | 11.61
2018-02-15 11:00 | 12.41 | 12.14
2018-02-15 11:30 | 13.66 | 13.36
2018-02-15 12:00 | 14.42 | 14.07
2018-02-15 12:30 | 15.5 | 15.15
2018-02-15 13:00 | 16.27 | 15.89
2018-02-15 13:30 | 16.58 | 16.18
2018-02-15 14:00 | 17.62 | 17.22
2018-02-15 14:30 | 19.84 | 19.46
2018-02-15 15:00 | 20.2 | 19.84
2018-02-15 15:30 | 20.9 | 20.54
2018-02-15 16:00 | 20.01 | 19.68
2018-02-15 16:30 | 18.26 | 17.98
2018-02-15 17:00 | 17.82 | 17.56
2018-02-15 17:30 | 17.37 | 17.14
2018-02-15 18:00 | 17.27 | 17.05
2018-02-15 18:30 | 17.6 | 17.37
2018-02-15 19:00 | 18.27 | 18
2018-02-15 19:30 | 18.44 | 18.16
2018-02-15 20:00 | 18 | 17.73
2018-02-15 20:30 | 18.13 | 17.9
2018-02-15 21:00 | 17.29 | 17.09
2018-02-15 21:30 | 16.08 | 15.89
2018-02-15 22:00 | 14.73 | 14.59
2018-02-15 22:30 | 13.2 | 13.08
2018-02-15 23:00 | 12.37 | 12.29
2018-02-15 23:30 | 11.17 | 11.1
2018-02-16 | 10.14 | 10.09
2018-02-16 00:30 | 9.4 | 9.36
2018-02-16 01:00 | 8.95 | 8.91
2018-02-16 01:30 | 8.58 | 8.54
2018-02-16 02:00 | 8.88 | 8.84
2018-02-16 02:30 | 8.56 | 8.53
2018-02-16 03:00 | 8.17 | 8.14
2018-02-16 03:30 | 7.98 | 7.94
2018-02-16 04:00 | 7.87 | 7.84
2018-02-16 04:30 | 7.77 | 7.74
2018-02-16 05:00 | 7.73 | 7.71
2018-02-16 05:30 | 8.05 | 8.02
2018-02-16 06:00 | 8.5 | 8.48
2018-02-16 06:30 | 9.74 | 9.73
2018-02-16 07:00 | 10.74 | 10.73
2018-02-16 07:30 | 11.04 | 11.02
2018-02-16 08:00 | 11.33 | 11.29
2018-02-16 08:30 | 11.45 | 11.39
2018-02-16 09:00 | 10.2 | 10.08
2018-02-16 09:30 | 10.45 | 10.29
2018-02-16 10:00 | 10.97 | 10.78
2018-02-16 10:30 | 11.48 | 11.28
2018-02-16 11:00 | 11.8 | 11.55
2018-02-16 11:30 | 12.69 | 12.4
2018-02-16 12:00 | 13.35 | 13.05
2018-02-16 12:30 | 14.31 | 14
2018-02-16 13:00 | 15.32 | 14.98
2018-02-16 13:30 | 16.29 | 15.88
2018-02-16 14:00 | 17.3 | 16.89
2018-02-16 14:30 | 18.46 | 18.1
2018-02-16 15:00 | 19.52 | 19.14
2018-02-16 15:30 | 20 | 19.66
2018-02-16 16:00 | 19.59 | 19.29
2018-02-16 16:30 | 18.96 | 18.66
2018-02-16 17:00 | 18.79 | 18.5
2018-02-16 17:30 | 17.37 | 17.19
2018-02-16 18:00 | 16.04 | 15.89
2018-02-16 18:30 | 14.57 | 14.43
2018-02-16 19:00 | 14.68 | 14.54
2018-02-16 19:30 | 15.08 | 14.95
2018-02-16 20:00 | 15.26 | 15.15
2018-02-16 20:30 | 14.11 | 13.99
2018-02-16 21:00 | 12.99 | 12.9
2018-02-16 21:30 | 11.94 | 11.88
2018-02-16 22:00 | 11.14 | 11.09
2018-02-16 22:30 | 10.63 | 10.59
2018-02-16 23:00 | 9.88 | 9.86
2018-02-16 23:30 | 9.24 | 9.22
2018-02-17 | 8.49 | 8.46
2018-02-17 00:30 | 7.82 | 7.8
2018-02-17 01:00 | 7.31 | 7.3
2018-02-17 01:30 | 7 | 6.98
2018-02-17 02:00 | 6.71 | 6.69
2018-02-17 02:30 | 6.52 | 6.5
2018-02-17 03:00 | 6.42 | 6.4
2018-02-17 03:30 | 6.41 | 6.38
2018-02-17 04:00 | 6.31 | 6.29
2018-02-17 04:30 | 6.4 | 6.38
2018-02-17 05:00 | 6.31 | 6.29
2018-02-17 05:30 | 6.32 | 6.3
2018-02-17 06:00 | 6.25 | 6.22
2018-02-17 06:30 | 6.34 | 6.32
2018-02-17 07:00 | 6.38 | 6.36
2018-02-17 07:30 | 7.29 | 7.27
2018-02-17 08:00 | 7.35 | 7.32
2018-02-17 08:30 | 8.39 | 8.35
2018-02-17 09:00 | 8.77 | 8.73
2018-02-17 09:30 | 9.15 | 9.07
2018-02-17 10:00 | 9.32 | 9.22
2018-02-17 10:30 | 10.15 | 10.04
2018-02-17 11:00 | 11.19 | 11.06
2018-02-17 11:30 | 11.78 | 11.64
2018-02-17 12:00 | 11.6 | 11.45
2018-02-17 12:30 | 11.83 | 11.66
2018-02-17 13:00 | 11.81 | 11.61
2018-02-17 13:30 | 12.67 | 12.46
2018-02-17 14:00 | 13.34 | 13.13
2018-02-17 14:30 | 13.26 | 13.04
2018-02-17 15:00 | 14.04 | 13.84
2018-02-17 15:30 | 14.39 | 14.18
2018-02-17 16:00 | 15.02 | 14.83
2018-02-17 16:30 | 15.29 | 15.08
2018-02-17 17:00 | 15.36 | 15.17
2018-02-17 17:30 | 15.7 | 15.53
2018-02-17 18:00 | 15.06 | 14.92
2018-02-17 18:30 | 14.62 | 14.5
2018-02-17 19:00 | 14.99 | 14.85
2018-02-17 19:30 | 14.93 | 14.78
2018-02-17 20:00 | 14.85 | 14.71
2018-02-17 20:30 | 14.05 | 13.93
2018-02-17 21:00 | 13.24 | 13.15
2018-02-17 21:30 | 12.46 | 12.38
2018-02-17 22:00 | 11.7 | 11.64
2018-02-17 22:30 | 11.06 | 11.01
2018-02-17 23:00 | 10.44 | 10.4
2018-02-17 23:30 | 9.77 | 9.74
2018-02-18 | 8.73 | 8.71
2018-02-18 00:30 | 7.99 | 7.97
2018-02-18 01:00 | 7.48 | 7.46
2018-02-18 01:30 | 7.09 | 7.08
2018-02-18 02:00 | 6.72 | 6.71
2018-02-18 02:30 | 6.49 | 6.47
2018-02-18 03:00 | 6.17 | 6.15
2018-02-18 03:30 | 6.05 | 6.03
2018-02-18 04:00 | 5.94 | 5.92
2018-02-18 04:30 | 5.95 | 5.93
2018-02-18 05:00 | 5.89 | 5.87
2018-02-18 05:30 | 5.71 | 5.69
2018-02-18 06:00 | 5.58 | 5.56
2018-02-18 06:30 | 5.55 | 5.53
2018-02-18 07:00 | 5.67 | 5.65
2018-02-18 07:30 | 5.95 | 5.93
2018-02-18 08:00 | 6.36 | 6.34
2018-02-18 08:30 | 7.27 | 7.25
2018-02-18 09:00 | 7.16 | 7.11
2018-02-18 09:30 | 7.71 | 7.65
2018-02-18 10:00 | 8.7 | 8.62
2018-02-18 10:30 | 8.58 | 8.48
2018-02-18 11:00 | 9.14 | 9
2018-02-18 11:30 | 9.72 | 9.56
2018-02-18 12:00 | 11.01 | 10.84
2018-02-18 12:30 | 12.28 | 12.09
2018-02-18 13:00 | 12.67 | 12.45
2018-02-18 13:30 | 12.53 | 12.29
2018-02-18 14:00 | 13.51 | 13.27
2018-02-18 14:30 | 14.25 | 14.02
2018-02-18 15:00 | 15.21 | 14.97
2018-02-18 15:30 | 16.21 | 15.96
2018-02-18 16:00 | 16.98 | 16.74
2018-02-18 16:30 | 17.55 | 17.33
2018-02-18 17:00 | 18.25 | 18.02
2018-02-18 17:30 | 18.17 | 17.96
2018-02-18 18:00 | 17.86 | 17.67
2018-02-18 18:30 | 17.37 | 17.2
2018-02-18 19:00 | 17.23 | 17.06
2018-02-18 19:30 | 16.84 | 16.67
2018-02-18 20:00 | 16.15 | 16.01
2018-02-18 20:30 | 15.26 | 15.14
2018-02-18 21:00 | 14.28 | 14.18
2018-02-18 21:30 | 13.03 | 12.95
2018-02-18 22:00 | 11.71 | 11.66
2018-02-18 22:30 | 10.83 | 10.79
2018-02-18 23:00 | 9.87 | 9.84
2018-02-18 23:30 | 9.1 | 9.08
2018-02-19 | 8.01 | 8
2018-02-19 00:30 | 7.22 | 7.2
2018-02-19 01:00 | 6.72 | 6.7
2018-02-19 01:30 | 6.43 | 6.42
2018-02-19 02:00 | 6.21 | 6.2
2018-02-19 02:30 | 6.17 | 6.16
2018-02-19 03:00 | 6.08 | 6.06
2018-02-19 03:30 | 5.99 | 5.97
2018-02-19 04:00 | 5.82 | 5.81
2018-02-19 04:30 | 5.89 | 5.88
2018-02-19 05:00 | 5.96 | 5.95
2018-02-19 05:30 | 6.11 | 6.1
2018-02-19 06:00 | 6.56 | 6.55
2018-02-19 06:30 | 6.85 | 6.85
2018-02-19 07:00 | 7 | 6.99
2018-02-19 07:30 | 7.26 | 7.26
2018-02-19 08:00 | 7.02 | 7.01
2018-02-19 08:30 | 6.58 | 6.56
2018-02-19 09:00 | 6.44 | 6.4
2018-02-19 09:30 | 6.68 | 6.61
2018-02-19 10:00 | 6.81 | 6.72
2018-02-19 10:30 | 6.94 | 6.83
2018-02-19 11:00 | 7.3 | 7.16
2018-02-19 11:30 | 7.6 | 7.46
2018-02-19 12:00 | 8.02 | 7.88
2018-02-19 12:30 | 8.75 | 8.61
2018-02-19 13:00 | 9.44 | 9.27
2018-02-19 13:30 | 10.06 | 9.88
2018-02-19 14:00 | 11.11 | 10.92
2018-02-19 14:30 | 12.07 | 11.79
2018-02-19 15:00 | 12.83 | 12.57
2018-02-19 15:30 | 14.18 | 13.96
2018-02-19 16:00 | 15.88 | 15.64
2018-02-19 16:30 | 17.01 | 16.77
2018-02-19 17:00 | 18.14 | 17.92
2018-02-19 17:30 | 17.88 | 17.68
2018-02-19 18:00 | 17.45 | 17.28
2018-02-19 18:30 | 17.4 | 17.25
2018-02-19 19:00 | 17.62 | 17.43
2018-02-19 19:30 | 17.01 | 16.84
2018-02-19 20:00 | 16.54 | 16.41
2018-02-19 20:30 | 16.16 | 16.04
2018-02-19 21:00 | 14.9 | 14.8
2018-02-19 21:30 | 13.39 | 13.31
2018-02-19 22:00 | 12.03 | 11.98
2018-02-19 22:30 | 11.29 | 11.25
2018-02-19 23:00 | 10.66 | 10.62
2018-02-19 23:30 | 9.35 | 9.32
2018-02-20 | 8.32 | 8.3
2018-02-20 00:30 | 7.64 | 7.62
2018-02-20 01:00 | 7.39 | 7.37
2018-02-20 01:30 | 6.88 | 6.86
2018-02-20 02:00 | 6.5 | 6.48
2018-02-20 02:30 | 6.32 | 6.3
2018-02-20 03:00 | 6.24 | 6.22
2018-02-20 03:30 | 6.22 | 6.19
2018-02-20 04:00 | 6.19 | 6.17
2018-02-20 04:30 | 6.15 | 6.13
2018-02-20 05:00 | 6.25 | 6.23
2018-02-20 05:30 | 6.71 | 6.7
2018-02-20 06:00 | 7.05 | 7.04
2018-02-20 06:30 | 7.43 | 7.41
2018-02-20 07:00 | 7.37 | 7.36
2018-02-20 07:30 | 7.27 | 7.26
2018-02-20 08:00 | 7.63 | 7.62
2018-02-20 08:30 | 6.75 | 6.73
2018-02-20 09:00 | 6.61 | 6.57
2018-02-20 09:30 | 6.13 | 6.07
2018-02-20 10:00 | 7.33 | 7.27
2018-02-20 10:30 | 8.13 | 8.08
2018-02-20 11:00 | 8.22 | 8.16
2018-02-20 11:30 | 6.68 | 6.59
2018-02-20 12:00 | 8.47 | 8.4
2018-02-20 12:30 | 8.37 | 8.29
2018-02-20 13:00 | 9.23 | 9.16
2018-02-20 13:30 | 9.67 | 9.6
2018-02-20 14:00 | 9.9 | 9.82
2018-02-20 14:30 | 9.45 | 9.37
2018-02-20 15:00 | 8.76 | 8.68
2018-02-20 15:30 | 10.31 | 10.25
2018-02-20 16:00 | 10.87 | 10.8
2018-02-20 16:30 | 11.16 | 11.1
2018-02-20 17:00 | 11.9 | 11.84
2018-02-20 17:30 | 12.25 | 12.19
2018-02-20 18:00 | 12.71 | 12.65
2018-02-20 18:30 | 13.29 | 13.23
2018-02-20 19:00 | 13.82 | 13.74
2018-02-20 19:30 | 13.66 | 13.58
2018-02-20 20:00 | 13.63 | 13.56
2018-02-20 20:30 | 13.38 | 13.32
2018-02-20 21:00 | 12.25 | 12.21
2018-02-20 21:30 | 11.06 | 11.03
2018-02-20 22:00 | 10.27 | 10.25
2018-02-20 22:30 | 9.65 | 9.63
2018-02-20 23:00 | 9.16 | 9.15
2018-02-20 23:30 | 7.96 | 7.95
2018-02-21 | 7.13 | 7.11
2018-02-21 00:30 | 6.46 | 6.45
2018-02-21 01:00 | 6.36 | 6.35
2018-02-21 01:30 | 6.12 | 6.11
2018-02-21 02:00 | 5.88 | 5.86
2018-02-21 02:30 | 5.72 | 5.71
2018-02-21 03:00 | 5.62 | 5.61
2018-02-21 03:30 | 5.67 | 5.66
2018-02-21 04:00 | 5.72 | 5.71
2018-02-21 04:30 | 5.87 | 5.85
2018-02-21 05:00 | 5.98 | 5.97
2018-02-21 05:30 | 6.3 | 6.28
2018-02-21 06:00 | 6.4 | 6.39
2018-02-21 06:30 | 6.88 | 6.87
2018-02-21 07:00 | 7.7 | 7.69
2018-02-21 07:30 | 7.9 | 7.89
2018-02-21 08:00 | 6.83 | 6.83
2018-02-21 08:30 | 7.54 | 7.53
2018-02-21 09:00 | 7.34 | 7.33
2018-02-21 09:30 | 6.99 | 6.97
2018-02-21 10:00 | 7.77 | 7.75
2018-02-21 10:30 | 6.57 | 6.54
2018-02-21 11:00 | 7.17 | 7.14
2018-02-21 11:30 | 6.77 | 6.74
2018-02-21 12:00 | 7.87 | 7.84
2018-02-21 12:30 | 7.16 | 7.13
2018-02-21 13:00 | 7.04 | 7.01
2018-02-21 13:30 | 5.81 | 5.78
2018-02-21 14:00 | 6.92 | 6.89
2018-02-21 14:30 | 7.08 | 7.05
2018-02-21 15:00 | 7.64 | 7.62
2018-02-21 15:30 | 7.9 | 7.88
2018-02-21 16:00 | 8.38 | 8.36
2018-02-21 16:30 | 9.22 | 9.2
2018-02-21 17:00 | 10.3 | 10.29
2018-02-21 17:30 | 10.88 | 10.87
2018-02-21 18:00 | 11.07 | 11.06
2018-02-21 18:30 | 11.59 | 11.58
2018-02-21 19:00 | 12.53 | 12.48
2018-02-21 19:30 | 12.16 | 12.12
2018-02-21 20:00 | 12.12 | 12.09
2018-02-21 20:30 | 11.9 | 11.88
2018-02-21 21:00 | 10.99 | 10.97
2018-02-21 21:30 | 10.06 | 10.05
2018-02-21 22:00 | 9.21 | 9.2
2018-02-21 22:30 | 8.66 | 8.65
2018-02-21 23:00 | 8.3 | 8.29
2018-02-21 23:30 | 7.29 | 7.28
2018-02-22 | 6.43 | 6.42
2018-02-22 00:30 | 5.89 | 5.88
2018-02-22 01:00 | 5.82 | 5.81
2018-02-22 01:30 | 5.62 | 5.61
2018-02-22 02:00 | 5.26 | 5.25
2018-02-22 02:30 | 5.28 | 5.27
2018-02-22 03:00 | 5.13 | 5.12
2018-02-22 03:30 | 5.11 | 5.09
2018-02-22 04:00 | 5.09 | 5.08
2018-02-22 04:30 | 5.17 | 5.16
2018-02-22 05:00 | 5.35 | 5.34
2018-02-22 05:30 | 6.11 | 6.1
2018-02-22 06:00 | 6.58 | 6.57
2018-02-22 06:30 | 7 | 7
2018-02-22 07:00 | 7.69 | 7.69
2018-02-22 07:30 | 7.81 | 7.81
2018-02-22 08:00 | 7.71 | 7.71
2018-02-22 08:30 | 7.67 | 7.66
2018-02-22 09:00 | 7.7 | 7.7
2018-02-22 09:30 | 7.97 | 7.97
2018-02-22 10:00 | 7.07 | 7.06
2018-02-22 10:30 | 7.2 | 7.18
2018-02-22 11:00 | 8.38 | 8.37
2018-02-22 11:30 | 8.85 | 8.83
2018-02-22 12:00 | 7.75 | 7.74
2018-02-22 12:30 | 7.27 | 7.26
2018-02-22 13:00 | 6.84 | 6.83
2018-02-22 13:30 | 7.04 | 7.03
2018-02-22 14:00 | 8.09 | 8.08
2018-02-22 14:30 | 8.36 | 8.35
2018-02-22 15:00 | 8.22 | 8.21
2018-02-22 15:30 | 8.07 | 8.05
2018-02-22 16:00 | 9.61 | 9.6
2018-02-22 16:30 | 9.46 | 9.44
2018-02-22 17:00 | 9.57 | 9.55
2018-02-22 17:30 | 9.77 | 9.75
2018-02-22 18:00 | 10.13 | 10.12
2018-02-22 18:30 | 10.48 | 10.46
2018-02-22 19:00 | 11.64 | 11.6
2018-02-22 19:30 | 11.67 | 11.63
2018-02-22 20:00 | 11.67 | 11.63
2018-02-22 20:30 | 11.41 | 11.39
2018-02-22 21:00 | 10.68 | 10.66
2018-02-22 21:30 | 10 | 9.98
2018-02-22 22:00 | 9.31 | 9.3
2018-02-22 22:30 | 8.81 | 8.8
2018-02-22 23:00 | 8.6 | 8.59
2018-02-22 23:30 | 7.5 | 7.49
2018-02-23 | 6.77 | 6.76
2018-02-23 00:30 | 6.12 | 6.11
2018-02-23 01:00 | 5.88 | 5.87
2018-02-23 01:30 | 5.68 | 5.67
2018-02-23 02:00 | 5.35 | 5.34
2018-02-23 02:30 | 5.28 | 5.27
2018-02-23 03:00 | 5.38 | 5.37
2018-02-23 03:30 | 5.33 | 5.32
2018-02-23 04:00 | 5.24 | 5.23
2018-02-23 04:30 | 5.32 | 5.31
2018-02-23 05:00 | 5.4 | 5.39
2018-02-23 05:30 | 5.68 | 5.67
2018-02-23 06:00 | 6.06 | 6.04
2018-02-23 06:30 | 6.55 | 6.53
2018-02-23 07:00 | 7.11 | 7.1
2018-02-23 07:30 | 7.5 | 7.49
2018-02-23 08:00 | 7.84 | 7.83
2018-02-23 08:30 | 7.54 | 7.53
2018-02-23 09:00 | 6.86 | 6.84
2018-02-23 09:30 | 6.72 | 6.7
2018-02-23 10:00 | 7.33 | 7.31
2018-02-23 10:30 | 7.61 | 7.6
2018-02-23 11:00 | 7.92 | 7.9
2018-02-23 11:30 | 7.46 | 7.44
2018-02-23 12:00 | 7.31 | 7.29
2018-02-23 12:30 | 8.49 | 8.47
2018-02-23 13:00 | 8.78 | 8.77
2018-02-23 13:30 | 8.71 | 8.7
2018-02-23 14:00 | 8.5 | 8.48
2018-02-23 14:30 | 8.13 | 8.12
2018-02-23 15:00 | 8.03 | 8.02
2018-02-23 15:30 | 8.51 | 8.5
2018-02-23 16:00 | 9.09 | 9.08
2018-02-23 16:30 | 9.1 | 9.09
2018-02-23 17:00 | 9.23 | 9.21
2018-02-23 17:30 | 9.73 | 9.71
2018-02-23 18:00 | 10.19 | 10.18
2018-02-23 18:30 | 10.35 | 10.34
2018-02-23 19:00 | 11.04 | 11.02
2018-02-23 19:30 | 11.1 | 11.08
2018-02-23 20:00 | 11.18 | 11.16
2018-02-23 20:30 | 11 | 10.98
2018-02-23 21:00 | 10.33 | 10.31
2018-02-23 21:30 | 9.8 | 9.79
2018-02-23 22:00 | 9.16 | 9.15
2018-02-23 22:30 | 8.85 | 8.84
2018-02-23 23:00 | 8.67 | 8.66
2018-02-23 23:30 | 7.69 | 7.68
2018-02-24 | 6.84 | 6.83
2018-02-24 00:30 | 6.27 | 6.26
2018-02-24 01:00 | 6.09 | 6.08
2018-02-24 01:30 | 5.82 | 5.81
2018-02-24 02:00 | 5.59 | 5.58
2018-02-24 02:30 | 5.47 | 5.45
2018-02-24 03:00 | 5.33 | 5.32
2018-02-24 03:30 | 5.2 | 5.18
2018-02-24 04:00 | 5.11 | 5.09
2018-02-24 04:30 | 5.16 | 5.15
2018-02-24 05:00 | 5.17 | 5.16
2018-02-24 05:30 | 5.26 | 5.24
2018-02-24 06:00 | 5.24 | 5.22
2018-02-24 06:30 | 5.4 | 5.37
2018-02-24 07:00 | 5.87 | 5.85
2018-02-24 07:30 | 6.24 | 6.22
2018-02-24 08:00 | 5.85 | 5.82
2018-02-24 08:30 | 6.1 | 6.07
2018-02-24 09:00 | 7.41 | 7.38
2018-02-24 09:30 | 7.46 | 7.43
2018-02-24 10:00 | 6.96 | 6.91
2018-02-24 10:30 | 6.96 | 6.9
2018-02-24 11:00 | 8.26 | 8.2
2018-02-24 11:30 | 9.26 | 9.22
2018-02-24 12:00 | 9.63 | 9.59
2018-02-24 12:30 | 9.3 | 9.26
2018-02-24 13:00 | 7.22 | 7.16
2018-02-24 13:30 | 8.51 | 8.45
2018-02-24 14:00 | 9.88 | 9.83
2018-02-24 14:30 | 10.28 | 10.23
2018-02-24 15:00 | 9.68 | 9.63
2018-02-24 15:30 | 10.29 | 10.25
2018-02-24 16:00 | 10.68 | 10.64
2018-02-24 16:30 | 11.37 | 11.32
2018-02-24 17:00 | 12.22 | 12.18
2018-02-24 17:30 | 12.25 | 12.21
2018-02-24 18:00 | 12.28 | 12.25
2018-02-24 18:30 | 12.4 | 12.37
2018-02-24 19:00 | 12.78 | 12.72
2018-02-24 19:30 | 12.71 | 12.65
2018-02-24 20:00 | 12.58 | 12.52
2018-02-24 20:30 | 12.15 | 12.11
2018-02-24 21:00 | 11.52 | 11.49
2018-02-24 21:30 | 10.93 | 10.9
2018-02-24 22:00 | 10.32 | 10.3
2018-02-24 22:30 | 10.06 | 10.04
2018-02-24 23:00 | 9.89 | 9.87
2018-02-24 23:30 | 8.74 | 8.73
2018-02-25 | 7.79 | 7.77
2018-02-25 00:30 | 7.21 | 7.19
2018-02-25 01:00 | 6.85 | 6.83
2018-02-25 01:30 | 6.39 | 6.38
2018-02-25 02:00 | 6.05 | 6.03
2018-02-25 02:30 | 5.85 | 5.83
2018-02-25 03:00 | 5.76 | 5.74
2018-02-25 03:30 | 5.57 | 5.55
2018-02-25 04:00 | 5.61 | 5.59
2018-02-25 04:30 | 5.62 | 5.6
2018-02-25 05:00 | 5.66 | 5.64
2018-02-25 05:30 | 5.57 | 5.55
2018-02-25 06:00 | 5.41 | 5.39
2018-02-25 06:30 | 5.37 | 5.35
2018-02-25 07:00 | 5.51 | 5.49
2018-02-25 07:30 | 5.85 | 5.83
2018-02-25 08:00 | 6.34 | 6.31
2018-02-25 08:30 | 6.38 | 6.35
2018-02-25 09:00 | 7.33 | 7.3
2018-02-25 09:30 | 8.14 | 8.11
2018-02-25 10:00 | 8.1 | 8.04
2018-02-25 10:30 | 9.33 | 9.27
2018-02-25 11:00 | 10.17 | 10.09
2018-02-25 11:30 | 10.08 | 9.97
2018-02-25 12:00 | 10.29 | 10.16
2018-02-25 12:30 | 10.84 | 10.69
2018-02-25 13:00 | 11.77 | 11.59
2018-02-25 13:30 | 12.82 | 12.63
2018-02-25 14:00 | 14.75 | 14.55
2018-02-25 14:30 | 16.33 | 16.13
2018-02-25 15:00 | 15.06 | 14.85
2018-02-25 15:30 | 16.6 | 16.41
2018-02-25 16:00 | 16.44 | 16.3
2018-02-25 16:30 | 15.23 | 15.12
2018-02-25 17:00 | 14.77 | 14.69
2018-02-25 17:30 | 14.6 | 14.52
2018-02-25 18:00 | 14.58 | 14.49
2018-02-25 18:30 | 14.43 | 14.36
2018-02-25 19:00 | 15.11 | 15
2018-02-25 19:30 | 14.88 | 14.77
2018-02-25 20:00 | 14.63 | 14.52
2018-02-25 20:30 | 14.2 | 14.12
2018-02-25 21:00 | 13.27 | 13.21
2018-02-25 21:30 | 12.28 | 12.23
2018-02-25 22:00 | 11.31 | 11.27
2018-02-25 22:30 | 10.69 | 10.66
2018-02-25 23:00 | 10.19 | 10.17
2018-02-25 23:30 | 8.92 | 8.91
2018-02-26 | 7.97 | 7.95
2018-02-26 00:30 | 7.24 | 7.23
2018-02-26 01:00 | 6.96 | 6.95
2018-02-26 01:30 | 6.63 | 6.62
2018-02-26 02:00 | 6.28 | 6.26
2018-02-26 02:30 | 6.1 | 6.08
2018-02-26 03:00 | 6.01 | 5.99
2018-02-26 03:30 | 6.02 | 6
2018-02-26 04:00 | 6.02 | 6
2018-02-26 04:30 | 6.03 | 6.01
2018-02-26 05:00 | 6.17 | 6.15
2018-02-26 05:30 | 6.53 | 6.52
2018-02-26 06:00 | 6.65 | 6.63
2018-02-26 06:30 | 7.1 | 7.09
2018-02-26 07:00 | 7.49 | 7.48
2018-02-26 07:30 | 7.57 | 7.56
2018-02-26 08:00 | 7.19 | 7.17
2018-02-26 08:30 | 6.83 | 6.81
2018-02-26 09:00 | 6.88 | 6.84
2018-02-26 09:30 | 7.68 | 7.61
2018-02-26 10:00 | 8.03 | 7.94
2018-02-26 10:30 | 8.64 | 8.54
2018-02-26 11:00 | 8.86 | 8.73
2018-02-26 11:30 | 9.21 | 9.07
2018-02-26 12:00 | 9.33 | 9.17
2018-02-26 12:30 | 10.14 | 9.96
2018-02-26 13:00 | 10.83 | 10.64
2018-02-26 13:30 | 11.66 | 11.44
2018-02-26 14:00 | 12.65 | 12.42
2018-02-26 14:30 | 13.15 | 12.91
2018-02-26 15:00 | 13.92 | 13.68
2018-02-26 15:30 | 15.59 | 15.32
2018-02-26 16:00 | 17.62 | 17.33
2018-02-26 16:30 | 19.28 | 18.98
2018-02-26 17:00 | 20.49 | 20.19
2018-02-26 17:30 | 21.4 | 21.1
2018-02-26 18:00 | 21.84 | 21.56
2018-02-26 18:30 | 21.79 | 21.51
2018-02-26 19:00 | 20.87 | 20.59
2018-02-26 19:30 | 17.73 | 17.54
2018-02-26 20:00 | 17.05 | 16.89
2018-02-26 20:30 | 16.21 | 16.07
2018-02-26 21:00 | 14.69 | 14.59
2018-02-26 21:30 | 12.94 | 12.87
2018-02-26 22:00 | 11.59 | 11.55
2018-02-26 22:30 | 10.69 | 10.66
2018-02-26 23:00 | 9.96 | 9.94
2018-02-26 23:30 | 8.62 | 8.6
2018-02-27 | 7.66 | 7.65
2018-02-27 00:30 | 6.98 | 6.97
2018-02-27 01:00 | 6.68 | 6.66
2018-02-27 01:30 | 6.33 | 6.32
2018-02-27 02:00 | 6.06 | 6.05
2018-02-27 02:30 | 5.8 | 5.79
2018-02-27 03:00 | 5.73 | 5.71
2018-02-27 03:30 | 5.74 | 5.73
2018-02-27 04:00 | 5.8 | 5.78
2018-02-27 04:30 | 5.86 | 5.85
2018-02-27 05:00 | 5.98 | 5.96
2018-02-27 05:30 | 6.35 | 6.33
2018-02-27 06:00 | 6.52 | 6.51
2018-02-27 06:30 | 7.29 | 7.28
2018-02-27 07:00 | 7.81 | 7.8
2018-02-27 07:30 | 7.78 | 7.77
2018-02-27 08:00 | 7.9 | 7.89
2018-02-27 08:30 | 7.76 | 7.75
2018-02-27 09:00 | 7.35 | 7.34
2018-02-27 09:30 | 7.09 | 7.08
2018-02-27 10:00 | 6.88 | 6.87
2018-02-27 10:30 | 6.87 | 6.85
2018-02-27 11:00 | 6.95 | 6.93
2018-02-27 11:30 | 6.43 | 6.4
2018-02-27 12:00 | 5.81 | 5.77
2018-02-27 12:30 | 6.4 | 6.36
2018-02-27 13:00 | 7.61 | 7.57
2018-02-27 13:30 | 7.31 | 7.26
2018-02-27 14:00 | 7.53 | 7.48
2018-02-27 14:30 | 8.56 | 8.51
2018-02-27 15:00 | 9.15 | 9.11
2018-02-27 15:30 | 9.69 | 9.65
2018-02-27 16:00 | 11.1 | 11.05
2018-02-27 16:30 | 11.59 | 11.54
2018-02-27 17:00 | 11.97 | 11.94
2018-02-27 17:30 | 12.37 | 12.34
2018-02-27 18:00 | 12.45 | 12.42
2018-02-27 18:30 | 12.89 | 12.85
2018-02-27 19:00 | 13.4 | 13.34
2018-02-27 19:30 | 13.14 | 13.09
2018-02-27 20:00 | 13.24 | 13.19
2018-02-27 20:30 | 12.86 | 12.82
2018-02-27 21:00 | 11.91 | 11.89
2018-02-27 21:30 | 10.86 | 10.84
2018-02-27 22:00 | 9.71 | 9.7
2018-02-27 22:30 | 9.17 | 9.16
2018-02-27 23:00 | 8.9 | 8.88
2018-02-27 23:30 | 7.81 | 7.8
2018-02-28 | 6.94 | 6.93
2018-02-28 00:30 | 6.25 | 6.24
2018-02-28 01:00 | 6.1 | 6.1
2018-02-28 01:30 | 5.8 | 5.79
2018-02-28 02:00 | 5.4 | 5.4
2018-02-28 02:30 | 5.3 | 5.29
2018-02-28 03:00 | 5.18 | 5.17
2018-02-28 03:30 | 5.15 | 5.14
2018-02-28 04:00 | 5.18 | 5.16
2018-02-28 04:30 | 5.27 | 5.26
2018-02-28 05:00 | 5.54 | 5.53
2018-02-28 05:30 | 6.05 | 6.04
2018-02-28 06:00 | 6.47 | 6.45
2018-02-28 06:30 | 6.73 | 6.72
2018-02-28 07:00 | 7 | 6.99
2018-02-28 07:30 | 6.69 | 6.68
2018-02-28 08:00 | 6.08 | 6.06
2018-02-28 08:30 | 5.66 | 5.65
2018-02-28 09:00 | 5.24 | 5.22
2018-02-28 09:30 | 5.13 | 5.1
2018-02-28 10:00 | 5.21 | 5.18
2018-02-28 10:30 | 5.36 | 5.31
2018-02-28 11:00 | 5.66 | 5.61
2018-02-28 11:30 | 5.69 | 5.61
2018-02-28 12:00 | 6.14 | 6.06
2018-02-28 12:30 | 6.58 | 6.49
2018-02-28 13:00 | 7.41 | 7.33
2018-02-28 13:30 | 7.78 | 7.7
2018-02-28 14:00 | 7.75 | 7.65
2018-02-28 14:30 | 8.33 | 8.23
2018-02-28 15:00 | 8.87 | 8.76
2018-02-28 15:30 | 9.99 | 9.85
2018-02-28 16:00 | 11.29 | 11.15
2018-02-28 16:30 | 12.45 | 12.34
2018-02-28 17:00 | 13.37 | 13.27
2018-02-28 17:30 | 14.12 | 14.03
2018-02-28 18:00 | 14.6 | 14.51
2018-02-28 18:30 | 14.6 | 14.52
2018-02-28 19:00 | 15.38 | 15.26
2018-02-28 19:30 | 15.02 | 14.9
2018-02-28 20:00 | 14.94 | 14.84
2018-02-28 20:30 | 14.22 | 14.15
2018-02-28 21:00 | 13.1 | 13.04
2018-02-28 21:30 | 11.71 | 11.68
2018-02-28 22:00 | 10.68 | 10.66
2018-02-28 22:30 | 9.92 | 9.9
2018-02-28 23:00 | 9.36 | 9.35
2018-02-28 23:30 | 8.18 | 8.16
2018-03-01 | 7.17 | 7.16
2018-03-01 00:30 | 6.65 | 6.64
2018-03-01 01:00 | 6.39 | 6.37
2018-03-01 01:30 | 6.02 | 6.01
2018-03-01 02:00 | 5.75 | 5.74
2018-03-01 02:30 | 5.57 | 5.56
2018-03-01 03:00 | 5.46 | 5.45
2018-03-01 03:30 | 5.46 | 5.44
2018-03-01 04:00 | 5.4 | 5.38
2018-03-01 04:30 | 5.47 | 5.45
2018-03-01 05:00 | 5.71 | 5.7
2018-03-01 05:30 | 6.26 | 6.25
2018-03-01 06:00 | 6.53 | 6.52
2018-03-01 06:30 | 6.89 | 6.88
2018-03-01 07:00 | 6.86 | 6.85
2018-03-01 07:30 | 7 | 6.99
2018-03-01 08:00 | 6.69 | 6.68
2018-03-01 08:30 | 6.18 | 6.16
2018-03-01 09:00 | 5.74 | 5.71
2018-03-01 09:30 | 5.81 | 5.77
2018-03-01 10:00 | 6.1 | 6.04
2018-03-01 10:30 | 6.55 | 6.46
2018-03-01 11:00 | 7.05 | 6.93
2018-03-01 11:30 | 7.68 | 7.55
2018-03-01 12:00 | 8.57 | 8.42
2018-03-01 12:30 | 9.48 | 9.31
2018-03-01 13:00 | 10.28 | 10.1
2018-03-01 13:30 | 11.32 | 11.1
2018-03-01 14:00 | 12.5 | 12.27
2018-03-01 14:30 | 13.51 | 13.23
2018-03-01 15:00 | 14.39 | 14.13
2018-03-01 15:30 | 16.05 | 15.81
2018-03-01 16:00 | 16.99 | 16.73
2018-03-01 16:30 | 18.09 | 17.83
2018-03-01 17:00 | 19.69 | 19.39
2018-03-01 17:30 | 20.45 | 20.15
2018-03-01 18:00 | 21.09 | 20.83
2018-03-01 18:30 | 21.26 | 21
2018-03-01 19:00 | 21.62 | 21.32
2018-03-01 19:30 | 21.22 | 20.91
2018-03-01 20:00 | 20.95 | 20.63
2018-03-01 20:30 | 19.98 | 19.68
2018-03-01 21:00 | 18.23 | 18.01
2018-03-01 21:30 | 16.28 | 16.11
2018-03-01 22:00 | 14.5 | 14.37
2018-03-01 22:30 | 13.16 | 13.07
2018-03-01 23:00 | 12.28 | 12.21
2018-03-01 23:30 | 10.66 | 10.61
2018-03-02 | 9.52 | 9.48
2018-03-02 00:30 | 8.82 | 8.79
2018-03-02 01:00 | 8.44 | 8.42
2018-03-02 01:30 | 7.93 | 7.91
2018-03-02 02:00 | 7.52 | 7.51
2018-03-02 02:30 | 7.2 | 7.18
2018-03-02 03:00 | 7.06 | 7.04
2018-03-02 03:30 | 7.02 | 7
2018-03-02 04:00 | 6.92 | 6.91
2018-03-02 04:30 | 6.91 | 6.9
2018-03-02 05:00 | 6.92 | 6.91
2018-03-02 05:30 | 7.06 | 7.05
2018-03-02 06:00 | 7.06 | 7.04
2018-03-02 06:30 | 7.3 | 7.28
2018-03-02 07:00 | 7.3 | 7.28
2018-03-02 07:30 | 7.34 | 7.32
2018-03-02 08:00 | 7.34 | 7.33
2018-03-02 08:30 | 8.24 | 8.22
2018-03-02 09:00 | 7.46 | 7.42
2018-03-02 09:30 | 7.63 | 7.58
2018-03-02 10:00 | 8.36 | 8.29
2018-03-02 10:30 | 8.9 | 8.83
2018-03-02 11:00 | 9.36 | 9.27
2018-03-02 11:30 | 11 | 10.9
2018-03-02 12:00 | 10.74 | 10.65
2018-03-02 12:30 | 9.47 | 9.37
2018-03-02 13:00 | 9.21 | 9.09
2018-03-02 13:30 | 10.56 | 10.44
2018-03-02 14:00 | 12.92 | 12.8
2018-03-02 14:30 | 12.49 | 12.37
2018-03-02 15:00 | 9.71 | 9.58
2018-03-02 15:30 | 10.44 | 10.3
2018-03-02 16:00 | 12.71 | 12.57
2018-03-02 16:30 | 13.61 | 13.5
2018-03-02 17:00 | 14.17 | 14.06
2018-03-02 17:30 | 14.09 | 14
2018-03-02 18:00 | 13.71 | 13.63
2018-03-02 18:30 | 13.64 | 13.56
2018-03-02 19:00 | 13.77 | 13.67
2018-03-02 19:30 | 13.63 | 13.54
2018-03-02 20:00 | 13.54 | 13.45
2018-03-02 20:30 | 13.28 | 13.22
2018-03-02 21:00 | 12.46 | 12.4
2018-03-02 21:30 | 11.61 | 11.57
2018-03-02 22:00 | 10.92 | 10.89
2018-03-02 22:30 | 10.63 | 10.61
2018-03-02 23:00 | 10.31 | 10.29
2018-03-02 23:30 | 9.21 | 9.19
2018-03-03 | 8.25 | 8.23
2018-03-03 00:30 | 7.67 | 7.65
2018-03-03 01:00 | 7.36 | 7.34
2018-03-03 01:30 | 7.03 | 7.02
2018-03-03 02:00 | 6.68 | 6.67
2018-03-03 02:30 | 6.51 | 6.49
2018-03-03 03:00 | 6.32 | 6.3
2018-03-03 03:30 | 6.26 | 6.24
2018-03-03 04:00 | 6.2 | 6.18
2018-03-03 04:30 | 6.49 | 6.48
2018-03-03 05:00 | 6.8 | 6.79
2018-03-03 05:30 | 6.79 | 6.78
2018-03-03 06:00 | 6.65 | 6.64
2018-03-03 06:30 | 6.64 | 6.63
2018-03-03 07:00 | 6.75 | 6.74
2018-03-03 07:30 | 7.41 | 7.4
2018-03-03 08:00 | 7.87 | 7.85
2018-03-03 08:30 | 8.09 | 8.07
2018-03-03 09:00 | 8.51 | 8.48
2018-03-03 09:30 | 8.85 | 8.82
2018-03-03 10:00 | 9.09 | 9.02
2018-03-03 10:30 | 9.78 | 9.71
2018-03-03 11:00 | 10.15 | 10.07
2018-03-03 11:30 | 10.19 | 10.08
2018-03-03 12:00 | 11.22 | 11.08
2018-03-03 12:30 | 12.27 | 12.12
2018-03-03 13:00 | 13.42 | 13.27
2018-03-03 13:30 | 14.12 | 13.97
2018-03-03 14:00 | 13.91 | 13.73
2018-03-03 14:30 | 14.65 | 14.46
2018-03-03 15:00 | 14.88 | 14.69
2018-03-03 15:30 | 15.63 | 15.44
2018-03-03 16:00 | 15.62 | 15.4
2018-03-03 16:30 | 16.27 | 16.06
2018-03-03 17:00 | 17.11 | 16.91
2018-03-03 17:30 | 17.26 | 17.07
2018-03-03 18:00 | 16.7 | 16.53
2018-03-03 18:30 | 16.74 | 16.57
2018-03-03 19:00 | 16.45 | 16.26
2018-03-03 19:30 | 16.1 | 15.91
2018-03-03 20:00 | 15.77 | 15.61
2018-03-03 20:30 | 15.18 | 15.04
2018-03-03 21:00 | 14.12 | 14
2018-03-03 21:30 | 13.23 | 13.15
2018-03-03 22:00 | 12.52 | 12.44
2018-03-03 22:30 | 12.1 | 12.04
2018-03-03 23:00 | 11.55 | 11.5
2018-03-03 23:30 | 10.34 | 10.3
2018-03-04 | 9.31 | 9.28
2018-03-04 00:30 | 8.53 | 8.51
2018-03-04 01:00 | 8.07 | 8.05
2018-03-04 01:30 | 7.59 | 7.56
2018-03-04 02:00 | 7.21 | 7.19
2018-03-04 02:30 | 7.01 | 6.99
2018-03-04 03:00 | 6.73 | 6.71
2018-03-04 03:30 | 6.53 | 6.51
2018-03-04 04:00 | 6.41 | 6.39
2018-03-04 04:30 | 6.41 | 6.39
2018-03-04 05:00 | 6.39 | 6.36
2018-03-04 05:30 | 6.25 | 6.23
2018-03-04 06:00 | 6.09 | 6.07
2018-03-04 06:30 | 6.19 | 6.17
2018-03-04 07:00 | 6.19 | 6.16
2018-03-04 07:30 | 6.34 | 6.31
2018-03-04 08:00 | 6.91 | 6.88
2018-03-04 08:30 | 7.82 | 7.78
2018-03-04 09:00 | 8.27 | 8.23
2018-03-04 09:30 | 8.25 | 8.18
2018-03-04 10:00 | 10.07 | 9.98
2018-03-04 10:30 | 10.08 | 9.96
2018-03-04 11:00 | 10.65 | 10.51
2018-03-04 11:30 | 11.53 | 11.35
2018-03-04 12:00 | 12.66 | 12.44
2018-03-04 12:30 | 13.68 | 13.43
2018-03-04 13:00 | 14.61 | 14.36
2018-03-04 13:30 | 15.87 | 15.61
2018-03-04 14:00 | 17.69 | 17.43
2018-03-04 14:30 | 18.37 | 18.1
2018-03-04 15:00 | 17.22 | 16.95
2018-03-04 15:30 | 17.63 | 17.35
2018-03-04 16:00 | 19.31 | 19.05
2018-03-04 16:30 | 19.46 | 19.22
2018-03-04 17:00 | 19.85 | 19.62
2018-03-04 17:30 | 19.86 | 19.65
2018-03-04 18:00 | 19.64 | 19.43
2018-03-04 18:30 | 19.68 | 19.44
2018-03-04 19:00 | 19.59 | 19.34
2018-03-04 19:30 | 18.86 | 18.62
2018-03-04 20:00 | 18.24 | 18.02
2018-03-04 20:30 | 17.09 | 16.91
2018-03-04 21:00 | 15.87 | 15.72
2018-03-04 21:30 | 14.58 | 14.47
2018-03-04 22:00 | 13.41 | 13.31
2018-03-04 22:30 | 12.6 | 12.53
2018-03-04 23:00 | 11.75 | 11.69
2018-03-04 23:30 | 10.39 | 10.35
2018-03-05 | 9.22 | 9.19
2018-03-05 00:30 | 8.51 | 8.48
2018-03-05 01:00 | 8.29 | 8.27
2018-03-05 01:30 | 7.86 | 7.85
2018-03-05 02:00 | 7.53 | 7.52
2018-03-05 02:30 | 7.31 | 7.29
2018-03-05 03:00 | 7.06 | 7.04
2018-03-05 03:30 | 6.95 | 6.93
2018-03-05 04:00 | 6.95 | 6.93
2018-03-05 04:30 | 6.96 | 6.94
2018-03-05 05:00 | 7.08 | 7.07
2018-03-05 05:30 | 7.47 | 7.46
2018-03-05 06:00 | 8.16 | 8.15
2018-03-05 06:30 | 8.45 | 8.44
2018-03-05 07:00 | 8.8 | 8.79
2018-03-05 07:30 | 9 | 9
2018-03-05 08:00 | 9.02 | 9.01
2018-03-05 08:30 | 8.86 | 8.85
2018-03-05 09:00 | 8.84 | 8.82
2018-03-05 09:30 | 8.79 | 8.76
2018-03-05 10:00 | 8.81 | 8.77
2018-03-05 10:30 | 8.85 | 8.81
2018-03-05 11:00 | 8.05 | 7.99
2018-03-05 11:30 | 8.53 | 8.45
2018-03-05 12:00 | 8.34 | 8.25
2018-03-05 12:30 | 9.2 | 9.13
2018-03-05 13:00 | 8.71 | 8.61
2018-03-05 13:30 | 10.47 | 10.37
2018-03-05 14:00 | 10.82 | 10.7
2018-03-05 14:30 | 11.1 | 10.98
2018-03-05 15:00 | 11.27 | 11.14
2018-03-05 15:30 | 12.18 | 12.06
2018-03-05 16:00 | 13.53 | 13.42
2018-03-05 16:30 | 14.06 | 13.95
2018-03-05 17:00 | 14.57 | 14.47
2018-03-05 17:30 | 15.49 | 15.39
2018-03-05 18:00 | 15.93 | 15.82
2018-03-05 18:30 | 16.46 | 16.33
2018-03-05 19:00 | 16.95 | 16.8
2018-03-05 19:30 | 16.55 | 16.4
2018-03-05 20:00 | 16.15 | 16.03
2018-03-05 20:30 | 15.64 | 15.54
2018-03-05 21:00 | 14.26 | 14.18
2018-03-05 21:30 | 12.88 | 12.81
2018-03-05 22:00 | 11.71 | 11.67
2018-03-05 22:30 | 11.16 | 11.13
2018-03-05 23:00 | 10.6 | 10.58
2018-03-05 23:30 | 9.27 | 9.26
2018-03-06 | 8.4 | 8.39
2018-03-06 00:30 | 7.77 | 7.75
2018-03-06 01:00 | 7.47 | 7.45
2018-03-06 01:30 | 6.8 | 6.79
2018-03-06 02:00 | 6.41 | 6.4
2018-03-06 02:30 | 6.19 | 6.17
2018-03-06 03:00 | 6.08 | 6.06
2018-03-06 03:30 | 6 | 5.99
2018-03-06 04:00 | 6.05 | 6.03
2018-03-06 04:30 | 6.04 | 6.03
2018-03-06 05:00 | 6.1 | 6.08
2018-03-06 05:30 | 6.38 | 6.37
2018-03-06 06:00 | 6.55 | 6.53
2018-03-06 06:30 | 6.97 | 6.96
2018-03-06 07:00 | 7.23 | 7.21
2018-03-06 07:30 | 7.51 | 7.49
2018-03-06 08:00 | 7.47 | 7.45
2018-03-06 08:30 | 7.02 | 7
2018-03-06 09:00 | 7.02 | 7
2018-03-06 09:30 | 7.5 | 7.48
2018-03-06 10:00 | 7.2 | 7.17
2018-03-06 10:30 | 7.35 | 7.32
2018-03-06 11:00 | 7.28 | 7.26
2018-03-06 11:30 | 7.48 | 7.46
2018-03-06 12:00 | 6.96 | 6.94
2018-03-06 12:30 | 6.67 | 6.65
2018-03-06 13:00 | 6.37 | 6.36
2018-03-06 13:30 | 6.65 | 6.63
2018-03-06 14:00 | 7.24 | 7.23
2018-03-06 14:30 | 7.12 | 7.11
2018-03-06 15:00 | 7 | 6.99
2018-03-06 15:30 | 7.23 | 7.22
2018-03-06 16:00 | 7.93 | 7.92
2018-03-06 16:30 | 8.46 | 8.44
2018-03-06 17:00 | 9.2 | 9.19
2018-03-06 17:30 | 9.91 | 9.9
2018-03-06 18:00 | 10.62 | 10.61
2018-03-06 18:30 | 11.14 | 11.13
2018-03-06 19:00 | 11.57 | 11.56
2018-03-06 19:30 | 11.29 | 11.28
2018-03-06 20:00 | 11.05 | 11.04
2018-03-06 20:30 | 10.75 | 10.74
2018-03-06 21:00 | 10.07 | 10.06
2018-03-06 21:30 | 9.34 | 9.33
2018-03-06 22:00 | 8.67 | 8.66
2018-03-06 22:30 | 8.09 | 8.09
2018-03-06 23:00 | 7.96 | 7.95
2018-03-06 23:30 | 7.04 | 7.03
2018-03-07 | 6.15 | 6.14
2018-03-07 00:30 | 5.62 | 5.6
2018-03-07 01:00 | 5.38 | 5.36
2018-03-07 01:30 | 5.19 | 5.17
2018-03-07 02:00 | 5.02 | 4.99
2018-03-07 02:30 | 4.94 | 4.92
2018-03-07 03:00 | 4.84 | 4.81
2018-03-07 03:30 | 4.9 | 4.88
2018-03-07 04:00 | 4.93 | 4.9
2018-03-07 04:30 | 5.1 | 5.07
2018-03-07 05:00 | 5.26 | 5.23
2018-03-07 05:30 | 5.85 | 5.84
2018-03-07 06:00 | 6.43 | 6.41
2018-03-07 06:30 | 6.79 | 6.77
2018-03-07 07:00 | 7.37 | 7.36
2018-03-07 07:30 | 7.53 | 7.52
2018-03-07 08:00 | 7.51 | 7.5
2018-03-07 08:30 | 7.07 | 7.06
2018-03-07 09:00 | 6.44 | 6.43
2018-03-07 09:30 | 6.71 | 6.7
2018-03-07 10:00 | 7.69 | 7.68
2018-03-07 10:30 | 7.51 | 7.5
2018-03-07 11:00 | 6.09 | 6.08
2018-03-07 11:30 | 6.54 | 6.53
2018-03-07 12:00 | 7.42 | 7.41
2018-03-07 12:30 | 6.32 | 6.31
2018-03-07 13:00 | 5.84 | 5.82
2018-03-07 13:30 | 5.71 | 5.7
2018-03-07 14:00 | 5.27 | 5.25
2018-03-07 14:30 | 5.95 | 5.94
2018-03-07 15:00 | 6.02 | 6
2018-03-07 15:30 | 6.85 | 6.83
2018-03-07 16:00 | 7.97 | 7.96
2018-03-07 16:30 | 8.61 | 8.6
2018-03-07 17:00 | 9.45 | 9.44
2018-03-07 17:30 | 10.15 | 10.15
2018-03-07 18:00 | 10.8 | 10.79
2018-03-07 18:30 | 11.64 | 11.62
2018-03-07 19:00 | 12.62 | 12.6
2018-03-07 19:30 | 12.45 | 12.43
2018-03-07 20:00 | 12.14 | 12.13
2018-03-07 20:30 | 11.87 | 11.86
2018-03-07 21:00 | 10.91 | 10.9
2018-03-07 21:30 | 10.01 | 10
2018-03-07 22:00 | 9.08 | 9.07
2018-03-07 22:30 | 8.45 | 8.44
2018-03-07 23:00 | 8.1 | 8.1
2018-03-07 23:30 | 7.11 | 7.1
2018-03-08 | 6.33 | 6.32
2018-03-08 00:30 | 5.77 | 5.75
2018-03-08 01:00 | 5.5 | 5.48
2018-03-08 01:30 | 5.26 | 5.24
2018-03-08 02:00 | 4.96 | 4.94
2018-03-08 02:30 | 4.86 | 4.83
2018-03-08 03:00 | 4.75 | 4.72
2018-03-08 03:30 | 4.79 | 4.77
2018-03-08 04:00 | 4.88 | 4.85
2018-03-08 04:30 | 5.06 | 5.03
2018-03-08 05:00 | 5.35 | 5.33
2018-03-08 05:30 | 5.64 | 5.63
2018-03-08 06:00 | 6.29 | 6.26
2018-03-08 06:30 | 6.68 | 6.65
2018-03-08 07:00 | 7.03 | 7.02
2018-03-08 07:30 | 6.99 | 6.98
2018-03-08 08:00 | 6.98 | 6.97
2018-03-08 08:30 | 6.29 | 6.29
2018-03-08 09:00 | 5.39 | 5.39
2018-03-08 09:30 | 5.7 | 5.69
2018-03-08 10:00 | 7.23 | 7.22
2018-03-08 10:30 | 4.72 | 4.69
2018-03-08 11:00 | 4.82 | 4.8
2018-03-08 11:30 | 6.09 | 6.07
2018-03-08 12:00 | 5.64 | 5.62
2018-03-08 12:30 | 5.37 | 5.35
2018-03-08 13:00 | 6.67 | 6.65
2018-03-08 13:30 | 6.31 | 6.29
2018-03-08 14:00 | 5.77 | 5.75
2018-03-08 14:30 | 5.84 | 5.82
2018-03-08 15:00 | 5.58 | 5.56
2018-03-08 15:30 | 6.45 | 6.43
2018-03-08 16:00 | 6.88 | 6.86
2018-03-08 16:30 | 7.61 | 7.59
2018-03-08 17:00 | 8.96 | 8.94
2018-03-08 17:30 | 9.92 | 9.9
2018-03-08 18:00 | 10.53 | 10.52
2018-03-08 18:30 | 11.22 | 11.2
2018-03-08 19:00 | 12.22 | 12.17
2018-03-08 19:30 | 11.87 | 11.84
2018-03-08 20:00 | 11.76 | 11.74
2018-03-08 20:30 | 11.45 | 11.44
2018-03-08 21:00 | 10.26 | 10.24
2018-03-08 21:30 | 9.44 | 9.43
2018-03-08 22:00 | 8.73 | 8.72
2018-03-08 22:30 | 8.31 | 8.29
2018-03-08 23:00 | 8.09 | 8.07
2018-03-08 23:30 | 6.84 | 6.83
2018-03-09 | 5.97 | 5.95
2018-03-09 00:30 | 5.43 | 5.42
2018-03-09 01:00 | 5.28 | 5.27
2018-03-09 01:30 | 5.04 | 5.02
2018-03-09 02:00 | 4.73 | 4.72
2018-03-09 02:30 | 4.61 | 4.6
2018-03-09 03:00 | 4.51 | 4.49
2018-03-09 03:30 | 4.6 | 4.58
2018-03-09 04:00 | 4.62 | 4.6
2018-03-09 04:30 | 4.74 | 4.72
2018-03-09 05:00 | 4.96 | 4.94
2018-03-09 05:30 | 5.41 | 5.39
2018-03-09 06:00 | 5.65 | 5.62
2018-03-09 06:30 | 6.01 | 5.98
2018-03-09 07:00 | 6.29 | 6.27
2018-03-09 07:30 | 6.49 | 6.47
2018-03-09 08:00 | 5.96 | 5.95
2018-03-09 08:30 | 5.3 | 5.29
2018-03-09 09:00 | 4.92 | 4.9
2018-03-09 09:30 | 5.4 | 5.38
2018-03-09 10:00 | 4.11 | 4.08
2018-03-09 10:30 | 4.65 | 4.62
2018-03-09 11:00 | 4.6 | 4.57
2018-03-09 11:30 | 3.73 | 3.68
2018-03-09 12:00 | 5.05 | 5.02
2018-03-09 12:30 | 6.63 | 6.61
2018-03-09 13:00 | 6.63 | 6.61
2018-03-09 13:30 | 6.34 | 6.33
2018-03-09 14:00 | 6.1 | 6.09
2018-03-09 14:30 | 4.85 | 4.82
2018-03-09 15:00 | 5.87 | 5.84
2018-03-09 15:30 | 6.65 | 6.63
2018-03-09 16:00 | 7.33 | 7.31
2018-03-09 16:30 | 7.66 | 7.63
2018-03-09 17:00 | 8.82 | 8.81
2018-03-09 17:30 | 9.27 | 9.26
2018-03-09 18:00 | 9.48 | 9.47
2018-03-09 18:30 | 10.03 | 10.02
2018-03-09 19:00 | 11.13 | 11.1
2018-03-09 19:30 | 10.89 | 10.86
2018-03-09 20:00 | 10.86 | 10.85
2018-03-09 20:30 | 10.74 | 10.73
2018-03-09 21:00 | 9.98 | 9.97
2018-03-09 21:30 | 9.31 | 9.29
2018-03-09 22:00 | 8.68 | 8.66
2018-03-09 22:30 | 8.45 | 8.44
2018-03-09 23:00 | 8.12 | 8.11
2018-03-09 23:30 | 7.15 | 7.14
2018-03-10 | 6.35 | 6.34
2018-03-10 00:30 | 5.88 | 5.87
2018-03-10 01:00 | 5.6 | 5.59
2018-03-10 01:30 | 5.33 | 5.31
2018-03-10 02:00 | 4.93 | 4.92
2018-03-10 02:30 | 4.77 | 4.76
2018-03-10 03:00 | 4.74 | 4.72
2018-03-10 03:30 | 4.77 | 4.75
2018-03-10 04:00 | 4.65 | 4.63
2018-03-10 04:30 | 4.77 | 4.76
2018-03-10 05:00 | 5.1 | 5.09
2018-03-10 05:30 | 5.39 | 5.38
2018-03-10 06:00 | 5.32 | 5.29
2018-03-10 06:30 | 5.46 | 5.43
2018-03-10 07:00 | 5.68 | 5.65
2018-03-10 07:30 | 6.1 | 6.08
2018-03-10 08:00 | 5.89 | 5.87
2018-03-10 08:30 | 5.12 | 5.09
2018-03-10 09:00 | 5.45 | 5.42
2018-03-10 09:30 | 6.5 | 6.46
2018-03-10 10:00 | 7.06 | 7.02
2018-03-10 10:30 | 7.68 | 7.65
2018-03-10 11:00 | 5.6 | 5.56
2018-03-10 11:30 | 4.38 | 4.32
2018-03-10 12:00 | 5.99 | 5.94
2018-03-10 12:30 | 7.05 | 7.01
2018-03-10 13:00 | 7.26 | 7.22
2018-03-10 13:30 | 5.86 | 5.81
2018-03-10 14:00 | 5.83 | 5.77
2018-03-10 14:30 | 8.02 | 7.99
2018-03-10 15:00 | 6.94 | 6.92
2018-03-10 15:30 | 7.23 | 7.2
2018-03-10 16:00 | 7 | 6.97
2018-03-10 16:30 | 8.5 | 8.48
2018-03-10 17:00 | 8.89 | 8.88
2018-03-10 17:30 | 9.34 | 9.33
2018-03-10 18:00 | 9.67 | 9.66
2018-03-10 18:30 | 10.05 | 10.03
2018-03-10 19:00 | 10.59 | 10.57
2018-03-10 19:30 | 10.29 | 10.28
2018-03-10 20:00 | 10.21 | 10.2
2018-03-10 20:30 | 9.9 | 9.89
2018-03-10 21:00 | 9.24 | 9.22
2018-03-10 21:30 | 8.72 | 8.71
2018-03-10 22:00 | 8.23 | 8.22
2018-03-10 22:30 | 8.12 | 8.11
2018-03-10 23:00 | 7.98 | 7.98
2018-03-10 23:30 | 6.89 | 6.88
2018-03-11 | 6.19 | 6.18
2018-03-11 00:30 | 5.58 | 5.56
2018-03-11 01:00 | 5.34 | 5.33
2018-03-11 01:30 | 5.02 | 5
2018-03-11 02:00 | 4.77 | 4.75
2018-03-11 02:30 | 4.58 | 4.55
2018-03-11 03:00 | 4.56 | 4.54
2018-03-11 03:30 | 4.55 | 4.53
2018-03-11 04:00 | 4.47 | 4.45
2018-03-11 04:30 | 4.4 | 4.37
2018-03-11 05:00 | 4.42 | 4.4
2018-03-11 05:30 | 4.66 | 4.65
2018-03-11 06:00 | 4.53 | 4.47
2018-03-11 06:30 | 4.62 | 4.54
2018-03-11 07:00 | 4.54 | 4.47
2018-03-11 07:30 | 4.43 | 4.38
2018-03-11 08:00 | 4.78 | 4.75
2018-03-11 08:30 | 5.49 | 5.47
2018-03-11 09:00 | 5.8 | 5.78
2018-03-11 09:30 | 5.18 | 5.15
2018-03-11 10:00 | 6.18 | 6.15
2018-03-11 10:30 | 6.56 | 6.53
2018-03-11 11:00 | 6.3 | 6.27
2018-03-11 11:30 | 7.34 | 7.32
2018-03-11 12:00 | 6.67 | 6.65
2018-03-11 12:30 | 5.35 | 5.32
2018-03-11 13:00 | 7.12 | 7.1
2018-03-11 13:30 | 7.68 | 7.65
2018-03-11 14:00 | 6.9 | 6.87
2018-03-11 14:30 | 6.67 | 6.65
2018-03-11 15:00 | 8.54 | 8.52
2018-03-11 15:30 | 8.41 | 8.4
2018-03-11 16:00 | 8.24 | 8.22
2018-03-11 16:30 | 8.64 | 8.63
2018-03-11 17:00 | 9.23 | 9.21
2018-03-11 17:30 | 9.9 | 9.89
2018-03-11 18:00 | 10.46 | 10.45
2018-03-11 18:30 | 10.91 | 10.89
2018-03-11 19:00 | 11.6 | 11.59
2018-03-11 19:30 | 11.3 | 11.29
2018-03-11 20:00 | 11 | 10.99
2018-03-11 20:30 | 10.7 | 10.69
2018-03-11 21:00 | 10.07 | 10.06
2018-03-11 21:30 | 9.34 | 9.32
2018-03-11 22:00 | 8.52 | 8.51
2018-03-11 22:30 | 8.08 | 8.07
2018-03-11 23:00 | 7.74 | 7.73
2018-03-11 23:30 | 6.84 | 6.83
2018-03-12 | 5.98 | 5.97
2018-03-12 00:30 | 5.41 | 5.4
2018-03-12 01:00 | 5.21 | 5.2
2018-03-12 01:30 | 4.89 | 4.87
2018-03-12 02:00 | 4.61 | 4.58
2018-03-12 02:30 | 4.57 | 4.55
2018-03-12 03:00 | 4.43 | 4.41
2018-03-12 03:30 | 4.43 | 4.41
2018-03-12 04:00 | 4.39 | 4.37
2018-03-12 04:30 | 4.62 | 4.59
2018-03-12 05:00 | 4.91 | 4.89
2018-03-12 05:30 | 5.29 | 5.26
2018-03-12 06:00 | 5.61 | 5.57
2018-03-12 06:30 | 6.06 | 6.02
2018-03-12 07:00 | 6.52 | 6.49
2018-03-12 07:30 | 6.63 | 6.61
2018-03-12 08:00 | 6.34 | 6.33
2018-03-12 08:30 | 5.78 | 5.77
2018-03-12 09:00 | 5.27 | 5.26
2018-03-12 09:30 | 4.4 | 4.39
2018-03-12 10:00 | 4.04 | 4.02
2018-03-12 10:30 | 4.34 | 4.32
2018-03-12 11:00 | 4.47 | 4.45
2018-03-12 11:30 | 5.37 | 5.36
2018-03-12 12:00 | 5.74 | 5.72
2018-03-12 12:30 | 6.15 | 6.14
2018-03-12 13:00 | 4.87 | 4.86
2018-03-12 13:30 | 4.24 | 4.21
2018-03-12 14:00 | 4.8 | 4.77
2018-03-12 14:30 | 5.05 | 5.02
2018-03-12 15:00 | 6.13 | 6.1
2018-03-12 15:30 | 7.6 | 7.58
2018-03-12 16:00 | 7.69 | 7.67
2018-03-12 16:30 | 8.92 | 8.89
2018-03-12 17:00 | 10.47 | 10.45
2018-03-12 17:30 | 11.51 | 11.49
2018-03-12 18:00 | 11.99 | 11.97
2018-03-12 18:30 | 12.42 | 12.39
2018-03-12 19:00 | 13.31 | 13.27
2018-03-12 19:30 | 12.95 | 12.91
2018-03-12 20:00 | 12.48 | 12.45
2018-03-12 20:30 | 12.11 | 12.09
2018-03-12 21:00 | 11 | 10.98
2018-03-12 21:30 | 10.03 | 10.01
2018-03-12 22:00 | 9.14 | 9.13
2018-03-12 22:30 | 8.46 | 8.45
2018-03-12 23:00 | 8.09 | 8.08
2018-03-12 23:30 | 7.06 | 7.05
2018-03-13 | 6.26 | 6.25
2018-03-13 00:30 | 5.7 | 5.69
2018-03-13 01:00 | 5.44 | 5.43
2018-03-13 01:30 | 5.17 | 5.16
2018-03-13 02:00 | 4.9 | 4.89
2018-03-13 02:30 | 4.79 | 4.77
2018-03-13 03:00 | 4.64 | 4.62
2018-03-13 03:30 | 4.64 | 4.62
2018-03-13 04:00 | 4.75 | 4.73
2018-03-13 04:30 | 4.94 | 4.93
2018-03-13 05:00 | 5.14 | 5.12
2018-03-13 05:30 | 5.5 | 5.49
2018-03-13 06:00 | 5.62 | 5.59
2018-03-13 06:30 | 5.94 | 5.91
2018-03-13 07:00 | 6.34 | 6.32
2018-03-13 07:30 | 6.3 | 6.28
2018-03-13 08:00 | 5.88 | 5.87
2018-03-13 08:30 | 5.32 | 5.31
2018-03-13 09:00 | 4.84 | 4.83
2018-03-13 09:30 | 4.71 | 4.68
2018-03-13 10:00 | 5.09 | 5.06
2018-03-13 10:30 | 6.1 | 6.08
2018-03-13 11:00 | 6.94 | 6.92
2018-03-13 11:30 | 6.64 | 6.62
2018-03-13 12:00 | 6.77 | 6.75
2018-03-13 12:30 | 6.55 | 6.54
2018-03-13 13:00 | 6.42 | 6.4
2018-03-13 13:30 | 6.89 | 6.87
2018-03-13 14:00 | 7.4 | 7.38
2018-03-13 14:30 | 7.25 | 7.23
2018-03-13 15:00 | 7.13 | 7.12
2018-03-13 15:30 | 7.62 | 7.61
2018-03-13 16:00 | 8.59 | 8.57
2018-03-13 16:30 | 9.15 | 9.14
2018-03-13 17:00 | 10.01 | 9.99
2018-03-13 17:30 | 10.92 | 10.91
2018-03-13 18:00 | 11.42 | 11.41
2018-03-13 18:30 | 12.18 | 12.15
2018-03-13 19:00 | 12.94 | 12.9
2018-03-13 19:30 | 12.6 | 12.56
2018-03-13 20:00 | 12.52 | 12.49
2018-03-13 20:30 | 12.23 | 12.21
2018-03-13 21:00 | 11.29 | 11.28
2018-03-13 21:30 | 10.44 | 10.43
2018-03-13 22:00 | 9.51 | 9.5
2018-03-13 22:30 | 8.79 | 8.78
2018-03-13 23:00 | 8.39 | 8.37
2018-03-13 23:30 | 7.35 | 7.33
2018-03-14 | 6.48 | 6.47
2018-03-14 00:30 | 5.82 | 5.81
2018-03-14 01:00 | 5.7 | 5.69
2018-03-14 01:30 | 5.36 | 5.35
2018-03-14 02:00 | 5.09 | 5.08
2018-03-14 02:30 | 5.01 | 4.99
2018-03-14 03:00 | 4.97 | 4.95
2018-03-14 03:30 | 4.95 | 4.93
2018-03-14 04:00 | 4.92 | 4.9
2018-03-14 04:30 | 5.39 | 5.37
2018-03-14 05:00 | 5.98 | 5.98
2018-03-14 05:30 | 6.26 | 6.26
2018-03-14 06:00 | 6.46 | 6.45
2018-03-14 06:30 | 7 | 6.99
2018-03-14 07:00 | 7.39 | 7.38
2018-03-14 07:30 | 6.66 | 6.65
2018-03-14 08:00 | 6.79 | 6.78
2018-03-14 08:30 | 5.68 | 5.66
2018-03-14 09:00 | 5.46 | 5.45
2018-03-14 09:30 | 5.43 | 5.42
2018-03-14 10:00 | 5.15 | 5.13
2018-03-14 10:30 | 5.24 | 5.21
2018-03-14 11:00 | 4.76 | 4.73
2018-03-14 11:30 | 4.92 | 4.88
2018-03-14 12:00 | 5.21 | 5.18
2018-03-14 12:30 | 5.56 | 5.53
2018-03-14 13:00 | 5.63 | 5.59
2018-03-14 13:30 | 5.81 | 5.76
2018-03-14 14:00 | 6.23 | 6.18
2018-03-14 14:30 | 6.07 | 6.02
2018-03-14 15:00 | 6.56 | 6.51
2018-03-14 15:30 | 7.17 | 7.14
2018-03-14 16:00 | 8.13 | 8.1
2018-03-14 16:30 | 9.12 | 9.1
2018-03-14 17:00 | 10.12 | 10.09
2018-03-14 17:30 | 10.97 | 10.95
2018-03-14 18:00 | 11.36 | 11.34
2018-03-14 18:30 | 11.99 | 11.96
2018-03-14 19:00 | 13.08 | 13.03
2018-03-14 19:30 | 12.85 | 12.81
2018-03-14 20:00 | 12.73 | 12.7
2018-03-14 20:30 | 12.34 | 12.32
2018-03-14 21:00 | 11.56 | 11.54
2018-03-14 21:30 | 10.63 | 10.61
2018-03-14 22:00 | 9.86 | 9.85
2018-03-14 22:30 | 9.03 | 9.03
2018-03-14 23:00 | 8.41 | 8.4
2018-03-14 23:30 | 7.2 | 7.19
2018-03-15 | 6.33 | 6.32
2018-03-15 00:30 | 5.71 | 5.7
2018-03-15 01:00 | 5.56 | 5.55
2018-03-15 01:30 | 5.29 | 5.28
2018-03-15 02:00 | 5.03 | 5.01
2018-03-15 02:30 | 4.79 | 4.77
2018-03-15 03:00 | 4.78 | 4.76
2018-03-15 03:30 | 4.79 | 4.78
2018-03-15 04:00 | 4.79 | 4.77
2018-03-15 04:30 | 4.94 | 4.92
2018-03-15 05:00 | 5.13 | 5.12
2018-03-15 05:30 | 5.56 | 5.55
2018-03-15 06:00 | 5.81 | 5.8
2018-03-15 06:30 | 6.14 | 6.12
2018-03-15 07:00 | 6.25 | 6.23
2018-03-15 07:30 | 6.12 | 6.11
2018-03-15 08:00 | 5.96 | 5.94
2018-03-15 08:30 | 5.22 | 5.19
2018-03-15 09:00 | 5.64 | 5.61
2018-03-15 09:30 | 4.91 | 4.88
2018-03-15 10:00 | 4.29 | 4.23
2018-03-15 10:30 | 4.34 | 4.28
2018-03-15 11:00 | 4.28 | 4.21
2018-03-15 11:30 | 4.71 | 4.65
2018-03-15 12:00 | 6.1 | 6.05
2018-03-15 12:30 | 5.62 | 5.56
2018-03-15 13:00 | 5.86 | 5.78
2018-03-15 13:30 | 6.19 | 6.12
2018-03-15 14:00 | 7.02 | 6.95
2018-03-15 14:30 | 7.64 | 7.57
2018-03-15 15:00 | 7.94 | 7.85
2018-03-15 15:30 | 8.62 | 8.55
2018-03-15 16:00 | 10.11 | 10.04
2018-03-15 16:30 | 11.09 | 11.02
2018-03-15 17:00 | 11.58 | 11.53
2018-03-15 17:30 | 12.21 | 12.16
2018-03-15 18:00 | 12.54 | 12.51
2018-03-15 18:30 | 13.07 | 13.01
2018-03-15 19:00 | 14.12 | 14.03
2018-03-15 19:30 | 13.86 | 13.77
2018-03-15 20:00 | 13.48 | 13.42
2018-03-15 20:30 | 13.02 | 12.97
2018-03-15 21:00 | 12.22 | 12.18
2018-03-15 21:30 | 10.9 | 10.88
2018-03-15 22:00 | 9.79 | 9.78
2018-03-15 22:30 | 9.09 | 9.07
2018-03-15 23:00 | 8.66 | 8.65
2018-03-15 23:30 | 7.39 | 7.38
2018-03-16 | 6.28 | 6.26
2018-03-16 00:30 | 5.75 | 5.74
2018-03-16 01:00 | 5.63 | 5.62
2018-03-16 01:30 | 5.32 | 5.31
2018-03-16 02:00 | 5.1 | 5.08
2018-03-16 02:30 | 4.9 | 4.89
2018-03-16 03:00 | 4.85 | 4.84
2018-03-16 03:30 | 4.88 | 4.86
2018-03-16 04:00 | 4.87 | 4.85
2018-03-16 04:30 | 4.92 | 4.9
2018-03-16 05:00 | 5.12 | 5.11
2018-03-16 05:30 | 5.52 | 5.51
2018-03-16 06:00 | 5.7 | 5.67
2018-03-16 06:30 | 6.08 | 6.05
2018-03-16 07:00 | 6.41 | 6.37
2018-03-16 07:30 | 6.74 | 6.71
2018-03-16 08:00 | 6.05 | 6.03
2018-03-16 08:30 | 5.48 | 5.45
2018-03-16 09:00 | 4.81 | 4.78
2018-03-16 09:30 | 4.6 | 4.57
2018-03-16 10:00 | 4.49 | 4.46
2018-03-16 10:30 | 4.77 | 4.74
2018-03-16 11:00 | 5.19 | 5.16
2018-03-16 11:30 | 5.52 | 5.48
2018-03-16 12:00 | 5.74 | 5.69
2018-03-16 12:30 | 6.08 | 6.04
2018-03-16 13:00 | 6.49 | 6.44
2018-03-16 13:30 | 7.16 | 7.1
2018-03-16 14:00 | 7.94 | 7.87
2018-03-16 14:30 | 8.6 | 8.52
2018-03-16 15:00 | 9.1 | 9.02
2018-03-16 15:30 | 9.67 | 9.58
2018-03-16 16:00 | 10.96 | 10.87
2018-03-16 16:30 | 12.01 | 11.9
2018-03-16 17:00 | 12.6 | 12.52
2018-03-16 17:30 | 12.73 | 12.66
2018-03-16 18:00 | 12.52 | 12.45
2018-03-16 18:30 | 12.86 | 12.77
2018-03-16 19:00 | 13.39 | 13.3
2018-03-16 19:30 | 12.98 | 12.91
2018-03-16 20:00 | 12.69 | 12.63
2018-03-16 20:30 | 12.44 | 12.39
2018-03-16 21:00 | 11.53 | 11.5
2018-03-16 21:30 | 10.69 | 10.67
2018-03-16 22:00 | 9.82 | 9.81
2018-03-16 22:30 | 9.36 | 9.35
2018-03-16 23:00 | 8.95 | 8.93
2018-03-16 23:30 | 7.87 | 7.86
2018-03-17 | 7.03 | 7.02
2018-03-17 00:30 | 6.47 | 6.46
2018-03-17 01:00 | 6.15 | 6.14
2018-03-17 01:30 | 5.73 | 5.72
2018-03-17 02:00 | 5.47 | 5.45
2018-03-17 02:30 | 5.29 | 5.28
2018-03-17 03:00 | 5.16 | 5.15
2018-03-17 03:30 | 5.16 | 5.14
2018-03-17 04:00 | 5.09 | 5.07
2018-03-17 04:30 | 4.96 | 4.95
2018-03-17 05:00 | 5.05 | 5.03
2018-03-17 05:30 | 5.2 | 5.19
2018-03-17 06:00 | 5.08 | 5.05
2018-03-17 06:30 | 5.12 | 5.07
2018-03-17 07:00 | 5.22 | 5.17
2018-03-17 07:30 | 5.31 | 5.28
2018-03-17 08:00 | 5.23 | 5.21
2018-03-17 08:30 | 5.36 | 5.33
2018-03-17 09:00 | 5.24 | 5.21
2018-03-17 09:30 | 5.35 | 5.31
2018-03-17 10:00 | 5.5 | 5.45
2018-03-17 10:30 | 5.54 | 5.49
2018-03-17 11:00 | 5.6 | 5.54
2018-03-17 11:30 | 6.1 | 6.04
2018-03-17 12:00 | 6.59 | 6.52
2018-03-17 12:30 | 7.18 | 7.1
2018-03-17 13:00 | 8.01 | 7.9
2018-03-17 13:30 | 8.78 | 8.67
2018-03-17 14:00 | 9.67 | 9.56
2018-03-17 14:30 | 10.49 | 10.37
2018-03-17 15:00 | 11.24 | 11.12
2018-03-17 15:30 | 12.11 | 11.98
2018-03-17 16:00 | 12.89 | 12.77
2018-03-17 16:30 | 13.69 | 13.57
2018-03-17 17:00 | 14.24 | 14.13
2018-03-17 17:30 | 14.25 | 14.15
2018-03-17 18:00 | 13.97 | 13.88
2018-03-17 18:30 | 13.69 | 13.61
2018-03-17 19:00 | 13.94 | 13.85
2018-03-17 19:30 | 13.34 | 13.26
2018-03-17 20:00 | 13.15 | 13.08
2018-03-17 20:30 | 12.43 | 12.38
2018-03-17 21:00 | 11.48 | 11.44
2018-03-17 21:30 | 10.8 | 10.78
2018-03-17 22:00 | 10 | 9.98
2018-03-17 22:30 | 9.68 | 9.66
2018-03-17 23:00 | 9.42 | 9.4
2018-03-17 23:30 | 8.35 | 8.33
2018-03-18 | 7.37 | 7.36
2018-03-18 00:30 | 6.7 | 6.69
2018-03-18 01:00 | 6.4 | 6.38
2018-03-18 01:30 | 6.07 | 6.06
2018-03-18 02:00 | 5.74 | 5.73
2018-03-18 02:30 | 5.58 | 5.56
2018-03-18 03:00 | 5.46 | 5.44
2018-03-18 03:30 | 5.3 | 5.28
2018-03-18 04:00 | 5.32 | 5.3
2018-03-18 04:30 | 5.32 | 5.31
2018-03-18 05:00 | 5.38 | 5.36
2018-03-18 05:30 | 5.37 | 5.36
2018-03-18 06:00 | 5.18 | 5.16
2018-03-18 06:30 | 5.19 | 5.15
2018-03-18 07:00 | 5.19 | 5.16
2018-03-18 07:30 | 5.64 | 5.62
2018-03-18 08:00 | 6 | 5.98
2018-03-18 08:30 | 6.39 | 6.37
2018-03-18 09:00 | 6.37 | 6.35
2018-03-18 09:30 | 6.1 | 6.06
2018-03-18 10:00 | 7.1 | 7.06
2018-03-18 10:30 | 8.08 | 8.03
2018-03-18 11:00 | 7.65 | 7.59
2018-03-18 11:30 | 7.86 | 7.79
2018-03-18 12:00 | 8.43 | 8.36
2018-03-18 12:30 | 8.83 | 8.73
2018-03-18 13:00 | 9.72 | 9.61
2018-03-18 13:30 | 10.45 | 10.34
2018-03-18 14:00 | 11.47 | 11.34
2018-03-18 14:30 | 12.03 | 11.89
2018-03-18 15:00 | 13.31 | 13.16
2018-03-18 15:30 | 14.47 | 14.3
2018-03-18 16:00 | 15.17 | 15.01
2018-03-18 16:30 | 15.74 | 15.6
2018-03-18 17:00 | 16.28 | 16.15
2018-03-18 17:30 | 16.46 | 16.34
2018-03-18 18:00 | 16.31 | 16.19
2018-03-18 18:30 | 16.48 | 16.35
2018-03-18 19:00 | 16.77 | 16.62
2018-03-18 19:30 | 15.86 | 15.73
2018-03-18 20:00 | 15.34 | 15.23
2018-03-18 20:30 | 14.49 | 14.4
2018-03-18 21:00 | 13.22 | 13.17
2018-03-18 21:30 | 12.2 | 12.16
2018-03-18 22:00 | 11.14 | 11.11
2018-03-18 22:30 | 10.27 | 10.26
2018-03-18 23:00 | 9.77 | 9.75
2018-03-18 23:30 | 8.66 | 8.65
2018-03-19 | 7.66 | 7.65
2018-03-19 00:30 | 6.88 | 6.87
2018-03-19 01:00 | 6.65 | 6.63
2018-03-19 01:30 | 6.22 | 6.2
2018-03-19 02:00 | 5.89 | 5.87
2018-03-19 02:30 | 5.77 | 5.75
2018-03-19 03:00 | 5.62 | 5.6
2018-03-19 03:30 | 5.53 | 5.51
2018-03-19 04:00 | 5.46 | 5.44
2018-03-19 04:30 | 5.51 | 5.5
2018-03-19 05:00 | 5.8 | 5.79
2018-03-19 05:30 | 6.7 | 6.69
2018-03-19 06:00 | 6.64 | 6.64
2018-03-19 06:30 | 7.13 | 7.12
2018-03-19 07:00 | 6.99 | 6.98
2018-03-19 07:30 | 7.01 | 7
2018-03-19 08:00 | 6.99 | 6.98
2018-03-19 08:30 | 7.11 | 7.1
2018-03-19 09:00 | 6.63 | 6.61
2018-03-19 09:30 | 6.85 | 6.82
2018-03-19 10:00 | 7.11 | 7.06
2018-03-19 10:30 | 7.08 | 7
2018-03-19 11:00 | 7.42 | 7.33
2018-03-19 11:30 | 8.3 | 8.19
2018-03-19 12:00 | 8.76 | 8.64
2018-03-19 12:30 | 9.09 | 8.98
2018-03-19 13:00 | 9.3 | 9.18
2018-03-19 13:30 | 9.9 | 9.74
2018-03-19 14:00 | 11.09 | 10.93
2018-03-19 14:30 | 11.87 | 11.7
2018-03-19 15:00 | 12.37 | 12.2
2018-03-19 15:30 | 12.89 | 12.71
2018-03-19 16:00 | 14.73 | 14.54
2018-03-19 16:30 | 15.86 | 15.66
2018-03-19 17:00 | 16.59 | 16.42
2018-03-19 17:30 | 16.91 | 16.75
2018-03-19 18:00 | 16.6 | 16.45
2018-03-19 18:30 | 17.1 | 16.94
2018-03-19 19:00 | 17.83 | 17.67
2018-03-19 19:30 | 17.34 | 17.18
2018-03-19 20:00 | 16.61 | 16.49
2018-03-19 20:30 | 15.97 | 15.87
2018-03-19 21:00 | 14.77 | 14.69
2018-03-19 21:30 | 13.74 | 13.67
2018-03-19 22:00 | 12.5 | 12.46
2018-03-19 22:30 | 11.75 | 11.72
2018-03-19 23:00 | 11.01 | 10.99
2018-03-19 23:30 | 9.31 | 9.29
2018-03-20 | 7.97 | 7.96
2018-03-20 00:30 | 7.25 | 7.23
2018-03-20 01:00 | 6.88 | 6.87
2018-03-20 01:30 | 6.53 | 6.51
2018-03-20 02:00 | 6.23 | 6.22
2018-03-20 02:30 | 6.03 | 6.01
2018-03-20 03:00 | 5.85 | 5.84
2018-03-20 03:30 | 5.83 | 5.81
2018-03-20 04:00 | 5.72 | 5.7
2018-03-20 04:30 | 5.78 | 5.77
2018-03-20 05:00 | 6.06 | 6.05
2018-03-20 05:30 | 6.44 | 6.43
2018-03-20 06:00 | 6.54 | 6.53
2018-03-20 06:30 | 6.89 | 6.88
2018-03-20 07:00 | 7.23 | 7.22
2018-03-20 07:30 | 7.26 | 7.25
2018-03-20 08:00 | 6.94 | 6.93
2018-03-20 08:30 | 6.43 | 6.41
2018-03-20 09:00 | 7.47 | 7.46
2018-03-20 09:30 | 8.45 | 8.43
2018-03-20 10:00 | 8.55 | 8.51
2018-03-20 10:30 | 8.92 | 8.82
2018-03-20 11:00 | 8.77 | 8.72
2018-03-20 11:30 | 8.94 | 8.87
2018-03-20 12:00 | 9.48 | 9.4
2018-03-20 12:30 | 9.65 | 9.59
2018-03-20 13:00 | 10.14 | 10.06
2018-03-20 13:30 | 9.81 | 9.71
2018-03-20 14:00 | 9.35 | 9.22
2018-03-20 14:30 | 9.79 | 9.65
2018-03-20 15:00 | 10.51 | 10.39
2018-03-20 15:30 | 10.53 | 10.41
2018-03-20 16:00 | 11.63 | 11.51
2018-03-20 16:30 | 12.45 | 12.36
2018-03-20 17:00 | 13.37 | 13.28
2018-03-20 17:30 | 13.88 | 13.8
2018-03-20 18:00 | 13.98 | 13.9
2018-03-20 18:30 | 14.62 | 14.53
2018-03-20 19:00 | 15.31 | 15.21
2018-03-20 19:30 | 14.82 | 14.72
2018-03-20 20:00 | 14.26 | 14.19
2018-03-20 20:30 | 13.07 | 13.03
2018-03-20 21:00 | 12.41 | 12.38
2018-03-20 21:30 | 11.54 | 11.52
2018-03-20 22:00 | 10.76 | 10.74
2018-03-20 22:30 | 10.12 | 10.11
2018-03-20 23:00 | 9.79 | 9.78
2018-03-20 23:30 | 8.2 | 8.19
2018-03-21 | 6.96 | 6.94
2018-03-21 00:30 | 6.28 | 6.26
2018-03-21 01:00 | 6.08 | 6.07
2018-03-21 01:30 | 5.84 | 5.83
2018-03-21 02:00 | 5.47 | 5.46
2018-03-21 02:30 | 5.36 | 5.35
2018-03-21 03:00 | 5.21 | 5.19
2018-03-21 03:30 | 5.22 | 5.2
2018-03-21 04:00 | 5.42 | 5.41
2018-03-21 04:30 | 5.54 | 5.53
2018-03-21 05:00 | 6.09 | 6.08
2018-03-21 05:30 | 6.55 | 6.54
2018-03-21 06:00 | 6.73 | 6.73
2018-03-21 06:30 | 7.09 | 7.08
2018-03-21 07:00 | 7.17 | 7.17
2018-03-21 07:30 | 7.44 | 7.44
2018-03-21 08:00 | 6.71 | 6.7
2018-03-21 08:30 | 6.13 | 6.11
2018-03-21 09:00 | 5.77 | 5.76
2018-03-21 09:30 | 5.98 | 5.96
2018-03-21 10:00 | 6.11 | 6.08
2018-03-21 10:30 | 7.43 | 7.41
2018-03-21 11:00 | 7.05 | 7.02
2018-03-21 11:30 | 6.83 | 6.8
2018-03-21 12:00 | 7.73 | 7.71
2018-03-21 12:30 | 7.52 | 7.5
2018-03-21 13:00 | 7.05 | 7.04
2018-03-21 13:30 | 7.72 | 7.7
2018-03-21 14:00 | 7.67 | 7.66
2018-03-21 14:30 | 6.79 | 6.77
2018-03-21 15:00 | 8.05 | 8.04
2018-03-21 15:30 | 8.18 | 8.16
2018-03-21 16:00 | 8.98 | 8.97
2018-03-21 16:30 | 9.7 | 9.68
2018-03-21 17:00 | 10.03 | 10.02
2018-03-21 17:30 | 10.98 | 10.96
2018-03-21 18:00 | 11.59 | 11.57
2018-03-21 18:30 | 12.72 | 12.68
2018-03-21 19:00 | 13.5 | 13.45
2018-03-21 19:30 | 13.17 | 13.12
2018-03-21 20:00 | 12.62 | 12.59
2018-03-21 20:30 | 12.08 | 12.06
2018-03-21 21:00 | 11.59 | 11.57
2018-03-21 21:30 | 10.84 | 10.83
2018-03-21 22:00 | 10.21 | 10.2
2018-03-21 22:30 | 9.65 | 9.65
2018-03-21 23:00 | 9.21 | 9.2
2018-03-21 23:30 | 7.75 | 7.74
2018-03-22 | 6.65 | 6.63
2018-03-22 00:30 | 5.89 | 5.88
2018-03-22 01:00 | 5.75 | 5.74
2018-03-22 01:30 | 5.43 | 5.42
2018-03-22 02:00 | 5.2 | 5.19
2018-03-22 02:30 | 5.1 | 5.09
2018-03-22 03:00 | 4.99 | 4.98
2018-03-22 03:30 | 4.91 | 4.9
2018-03-22 04:00 | 4.99 | 4.97
2018-03-22 04:30 | 5.04 | 5.03
2018-03-22 05:00 | 5.38 | 5.37
2018-03-22 05:30 | 5.91 | 5.9
2018-03-22 06:00 | 6.12 | 6.1
2018-03-22 06:30 | 6.53 | 6.52
2018-03-22 07:00 | 7.06 | 7.05
2018-03-22 07:30 | 7.34 | 7.33
2018-03-22 08:00 | 6.81 | 6.8
2018-03-22 08:30 | 6.64 | 6.63
2018-03-22 09:00 | 5.49 | 5.47
2018-03-22 09:30 | 6 | 5.98
2018-03-22 10:00 | 4.58 | 4.55
2018-03-22 10:30 | 4.81 | 4.78
2018-03-22 11:00 | 6.17 | 6.15
2018-03-22 11:30 | 7.7 | 7.69
2018-03-22 12:00 | 6.69 | 6.68
2018-03-22 12:30 | 6.35 | 6.34
2018-03-22 13:00 | 5.18 | 5.16
2018-03-22 13:30 | 6.43 | 6.41
2018-03-22 14:00 | 5.71 | 5.68
2018-03-22 14:30 | 6.19 | 6.16
2018-03-22 15:00 | 6.15 | 6.12
2018-03-22 15:30 | 7.25 | 7.22
2018-03-22 16:00 | 8.4 | 8.38
2018-03-22 16:30 | 9.39 | 9.37
2018-03-22 17:00 | 10.43 | 10.41
2018-03-22 17:30 | 11.24 | 11.22
2018-03-22 18:00 | 11.42 | 11.4
2018-03-22 18:30 | 12.18 | 12.14
2018-03-22 19:00 | 12.88 | 12.82
2018-03-22 19:30 | 12.66 | 12.61
2018-03-22 20:00 | 12.02 | 11.99
2018-03-22 20:30 | 11.73 | 11.71
2018-03-22 21:00 | 11.23 | 11.22
2018-03-22 21:30 | 10.65 | 10.64
2018-03-22 22:00 | 9.72 | 9.72
2018-03-22 22:30 | 9.18 | 9.17
2018-03-22 23:00 | 8.63 | 8.63
2018-03-22 23:30 | 7.27 | 7.26
2018-03-23 | 6.31 | 6.29
2018-03-23 00:30 | 5.69 | 5.68
2018-03-23 01:00 | 5.46 | 5.45
2018-03-23 01:30 | 5.27 | 5.26
2018-03-23 02:00 | 4.95 | 4.94
2018-03-23 02:30 | 4.8 | 4.79
2018-03-23 03:00 | 4.69 | 4.67
2018-03-23 03:30 | 4.82 | 4.8
2018-03-23 04:00 | 4.77 | 4.75
2018-03-23 04:30 | 4.97 | 4.95
2018-03-23 05:00 | 5.39 | 5.37
2018-03-23 05:30 | 5.63 | 5.62
2018-03-23 06:00 | 5.93 | 5.91
2018-03-23 06:30 | 6.1 | 6.08
2018-03-23 07:00 | 6.31 | 6.29
2018-03-23 07:30 | 6.54 | 6.53
2018-03-23 08:00 | 6 | 5.99
2018-03-23 08:30 | 6.63 | 6.62
2018-03-23 09:00 | 6.16 | 6.12
2018-03-23 09:30 | 5.27 | 5.16
2018-03-23 10:00 | 5.84 | 5.72
2018-03-23 10:30 | 6.63 | 6.52
2018-03-23 11:00 | 4.78 | 4.61
2018-03-23 11:30 | 5.58 | 5.44
2018-03-23 12:00 | 4.25 | 4.05
2018-03-23 12:30 | 5.84 | 5.72
2018-03-23 13:00 | 6.56 | 6.53
2018-03-23 13:30 | 5.28 | 5.23
2018-03-23 14:00 | 6.2 | 6.17
2018-03-23 14:30 | 6.52 | 6.49
2018-03-23 15:00 | 6.15 | 6.12
2018-03-23 15:30 | 7.2 | 7.16
2018-03-23 16:00 | 7.95 | 7.91
2018-03-23 16:30 | 8.99 | 8.96
2018-03-23 17:00 | 9.55 | 9.52
2018-03-23 17:30 | 10.11 | 10.08
2018-03-23 18:00 | 10.53 | 10.5
2018-03-23 18:30 | 11.17 | 11.14
2018-03-23 19:00 | 11.65 | 11.62
2018-03-23 19:30 | 11.49 | 11.46
2018-03-23 20:00 | 11.38 | 11.35
2018-03-23 20:30 | 11.03 | 11.02
2018-03-23 21:00 | 10.41 | 10.39
2018-03-23 21:30 | 9.81 | 9.79
2018-03-23 22:00 | 9.21 | 9.2
2018-03-23 22:30 | 8.75 | 8.73
2018-03-23 23:00 | 8.48 | 8.47
2018-03-23 23:30 | 7.56 | 7.55
2018-03-24 | 6.84 | 6.82
2018-03-24 00:30 | 6.24 | 6.23
2018-03-24 01:00 | 6.02 | 6.01
2018-03-24 01:30 | 5.67 | 5.66
2018-03-24 02:00 | 5.35 | 5.34
2018-03-24 02:30 | 5.18 | 5.16
2018-03-24 03:00 | 5.17 | 5.15
2018-03-24 03:30 | 5.03 | 5.02
2018-03-24 04:00 | 4.98 | 4.97
2018-03-24 04:30 | 4.99 | 4.97
2018-03-24 05:00 | 5.01 | 4.99
2018-03-24 05:30 | 5.11 | 5.09
2018-03-24 06:00 | 5.12 | 5.09
2018-03-24 06:30 | 5.25 | 5.22
2018-03-24 07:00 | 5.34 | 5.3
2018-03-24 07:30 | 5.41 | 5.38
2018-03-24 08:00 | 5.62 | 5.59
2018-03-24 08:30 | 5.68 | 5.66
2018-03-24 09:00 | 5.79 | 5.75
2018-03-24 09:30 | 6.21 | 6.17
2018-03-24 10:00 | 6.75 | 6.71
2018-03-24 10:30 | 6.94 | 6.9
2018-03-24 11:00 | 6.82 | 6.78
2018-03-24 11:30 | 6.78 | 6.73
2018-03-24 12:00 | 6.8 | 6.74
2018-03-24 12:30 | 6.86 | 6.8
2018-03-24 13:00 | 7.39 | 7.34
2018-03-24 13:30 | 6.64 | 6.57
2018-03-24 14:00 | 6.87 | 6.8
2018-03-24 14:30 | 7.58 | 7.52
2018-03-24 15:00 | 8.07 | 8.02
2018-03-24 15:30 | 9.18 | 9.13
2018-03-24 16:00 | 9.67 | 9.63
2018-03-24 16:30 | 9.38 | 9.35
2018-03-24 17:00 | 9.92 | 9.89
2018-03-24 17:30 | 10.41 | 10.38
2018-03-24 18:00 | 10.94 | 10.92
2018-03-24 18:30 | 11.71 | 11.67
2018-03-24 19:00 | 12.04 | 12
2018-03-24 19:30 | 11.69 | 11.65
2018-03-24 20:00 | 11.42 | 11.39
2018-03-24 20:30 | 10.99 | 10.97
2018-03-24 21:00 | 10.27 | 10.25
2018-03-24 21:30 | 9.62 | 9.61
2018-03-24 22:00 | 9.06 | 9.04
2018-03-24 22:30 | 8.74 | 8.73
2018-03-24 23:00 | 8.53 | 8.51
2018-03-24 23:30 | 7.61 | 7.59
2018-03-25 | 6.76 | 6.75
2018-03-25 00:30 | 6.41 | 6.4
2018-03-25 01:00 | 5.94 | 5.93
2018-03-25 01:30 | 5.64 | 5.63
2018-03-25 02:00 | 5.28 | 5.26
2018-03-25 02:30 | 5.17 | 5.15
2018-03-25 03:00 | 5.09 | 5.07
2018-03-25 03:30 | 4.86 | 4.84
2018-03-25 04:00 | 4.78 | 4.76
2018-03-25 04:30 | 4.78 | 4.76
2018-03-25 05:00 | 4.82 | 4.8
2018-03-25 05:30 | 4.96 | 4.94
2018-03-25 06:00 | 5.07 | 5.02
2018-03-25 06:30 | 5.21 | 5.14
2018-03-25 07:00 | 5.3 | 5.23
2018-03-25 07:30 | 5.15 | 5.1
2018-03-25 08:00 | 5.18 | 5.15
2018-03-25 08:30 | 5.28 | 5.26
2018-03-25 09:00 | 5.8 | 5.77
2018-03-25 09:30 | 6.7 | 6.67
2018-03-25 10:00 | 6.88 | 6.84
2018-03-25 10:30 | 6.16 | 6.11
2018-03-25 11:00 | 7.04 | 7
2018-03-25 11:30 | 7.52 | 7.47
2018-03-25 12:00 | 7.88 | 7.83
2018-03-25 12:30 | 7.12 | 7.06
2018-03-25 13:00 | 6.82 | 6.76
2018-03-25 13:30 | 8.55 | 8.51
2018-03-25 14:00 | 8.95 | 8.91
2018-03-25 14:30 | 7.97 | 7.91
2018-03-25 15:00 | 9.09 | 9.04
2018-03-25 15:30 | 9.69 | 9.64
2018-03-25 16:00 | 9.87 | 9.83
2018-03-25 16:30 | 11.33 | 11.3
2018-03-25 17:00 | 11.87 | 11.84
2018-03-25 17:30 | 12.53 | 12.5
2018-03-25 18:00 | 12.63 | 12.6
2018-03-25 18:30 | 13.17 | 13.13
2018-03-25 19:00 | 13.4 | 13.35
2018-03-25 19:30 | 12.76 | 12.71
2018-03-25 20:00 | 12.21 | 12.18
2018-03-25 20:30 | 11.85 | 11.82
2018-03-25 21:00 | 10.96 | 10.94
2018-03-25 21:30 | 10.15 | 10.13
2018-03-25 22:00 | 9.4 | 9.39
2018-03-25 22:30 | 8.93 | 8.92
2018-03-25 23:00 | 8.71 | 8.7
2018-03-25 23:30 | 7.74 | 7.74
2018-03-26 | 6.91 | 6.9
2018-03-26 00:30 | 6.34 | 6.33
2018-03-26 01:00 | 6.11 | 6.1
2018-03-26 01:30 | 5.83 | 5.82
2018-03-26 02:00 | 5.56 | 5.54
2018-03-26 02:30 | 5.46 | 5.45
2018-03-26 03:00 | 5.38 | 5.37
2018-03-26 03:30 | 5.35 | 5.34
2018-03-26 04:00 | 5.38 | 5.37
2018-03-26 04:30 | 5.48 | 5.47
2018-03-26 05:00 | 5.68 | 5.67
2018-03-26 05:30 | 5.97 | 5.96
2018-03-26 06:00 | 6.43 | 6.42
2018-03-26 06:30 | 6.78 | 6.77
2018-03-26 07:00 | 7.04 | 7.03
2018-03-26 07:30 | 6.86 | 6.85
2018-03-26 08:00 | 7.12 | 7.11
2018-03-26 08:30 | 6.01 | 5.99
2018-03-26 09:00 | 6.55 | 6.54
2018-03-26 09:30 | 6.42 | 6.4
2018-03-26 10:00 | 7.01 | 6.99
2018-03-26 10:30 | 8.02 | 8
2018-03-26 11:00 | 6.85 | 6.81
2018-03-26 11:30 | 7.26 | 7.2
2018-03-26 12:00 | 7.88 | 7.82
2018-03-26 12:30 | 8.41 | 8.34
2018-03-26 13:00 | 8.03 | 7.93
2018-03-26 13:30 | 8.24 | 8.14
2018-03-26 14:00 | 9.12 | 9.02
2018-03-26 14:30 | 9.79 | 9.66
2018-03-26 15:00 | 11.07 | 10.95
2018-03-26 15:30 | 11.72 | 11.6
2018-03-26 16:00 | 13.49 | 13.36
2018-03-26 16:30 | 13.95 | 13.83
2018-03-26 17:00 | 14.31 | 14.22
2018-03-26 17:30 | 15.17 | 15.07
2018-03-26 18:00 | 15.56 | 15.46
2018-03-26 18:30 | 16.42 | 16.29
2018-03-26 19:00 | 16.68 | 16.55
2018-03-26 19:30 | 15.98 | 15.86
2018-03-26 20:00 | 15.28 | 15.18
2018-03-26 20:30 | 14.64 | 14.56
2018-03-26 21:00 | 14.06 | 13.99
2018-03-26 21:30 | 12.57 | 12.52
2018-03-26 22:00 | 11.17 | 11.14
2018-03-26 22:30 | 10.5 | 10.47
2018-03-26 23:00 | 10.06 | 10.04
2018-03-26 23:30 | 8.71 | 8.7
2018-03-27 | 7.82 | 7.81
2018-03-27 00:30 | 7.2 | 7.19
2018-03-27 01:00 | 6.92 | 6.91
2018-03-27 01:30 | 6.5 | 6.49
2018-03-27 02:00 | 6.28 | 6.27
2018-03-27 02:30 | 6.13 | 6.12
2018-03-27 03:00 | 5.99 | 5.98
2018-03-27 03:30 | 5.94 | 5.92
2018-03-27 04:00 | 5.95 | 5.94
2018-03-27 04:30 | 6.02 | 6
2018-03-27 05:00 | 6.32 | 6.3
2018-03-27 05:30 | 6.75 | 6.74
2018-03-27 06:00 | 7.49 | 7.48
2018-03-27 06:30 | 7.66 | 7.66
2018-03-27 07:00 | 7.86 | 7.85
2018-03-27 07:30 | 8.3 | 8.29
2018-03-27 08:00 | 8.4 | 8.39
2018-03-27 08:30 | 8.24 | 8.24
2018-03-27 09:00 | 8.32 | 8.31
2018-03-27 09:30 | 8.07 | 8.05
2018-03-27 10:00 | 8.2 | 8.17
2018-03-27 10:30 | 8.44 | 8.41
2018-03-27 11:00 | 6.88 | 6.83
2018-03-27 11:30 | 8.53 | 8.49
2018-03-27 12:00 | 9.03 | 8.99
2018-03-27 12:30 | 8.76 | 8.71
2018-03-27 13:00 | 9.06 | 9.01
2018-03-27 13:30 | 8.94 | 8.88
2018-03-27 14:00 | 7.91 | 7.82
2018-03-27 14:30 | 8.84 | 8.75
2018-03-27 15:00 | 8.95 | 8.86
2018-03-27 15:30 | 11.14 | 11.06
2018-03-27 16:00 | 11.38 | 11.3
2018-03-27 16:30 | 11.88 | 11.8
2018-03-27 17:00 | 12.36 | 12.29
2018-03-27 17:30 | 13.27 | 13.21
2018-03-27 18:00 | 13.6 | 13.53
2018-03-27 18:30 | 14.45 | 14.35
2018-03-27 19:00 | 14.96 | 14.85
2018-03-27 19:30 | 14.38 | 14.29
2018-03-27 20:00 | 13.8 | 13.72
2018-03-27 20:30 | 13.6 | 13.54
2018-03-27 21:00 | 12.51 | 12.47
2018-03-27 21:30 | 11.09 | 11.07
2018-03-27 22:00 | 10.08 | 10.07
2018-03-27 22:30 | 9.67 | 9.66
2018-03-27 23:00 | 9.19 | 9.18
2018-03-27 23:30 | 8.16 | 8.15
2018-03-28 | 7.11 | 7.1
2018-03-28 00:30 | 6.48 | 6.47
2018-03-28 01:00 | 6.22 | 6.21
2018-03-28 01:30 | 5.96 | 5.95
2018-03-28 02:00 | 5.76 | 5.75
2018-03-28 02:30 | 5.66 | 5.64
2018-03-28 03:00 | 5.61 | 5.6
2018-03-28 03:30 | 5.51 | 5.5
2018-03-28 04:00 | 5.49 | 5.48
2018-03-28 04:30 | 5.55 | 5.53
2018-03-28 05:00 | 5.87 | 5.86
2018-03-28 05:30 | 6.18 | 6.17
2018-03-28 06:00 | 6.34 | 6.32
2018-03-28 06:30 | 6.56 | 6.54
2018-03-28 07:00 | 7.18 | 7.17
2018-03-28 07:30 | 7.3 | 7.29
2018-03-28 08:00 | 6.88 | 6.88
2018-03-28 08:30 | 6.45 | 6.43
2018-03-28 09:00 | 5.93 | 5.91
2018-03-28 09:30 | 6.02 | 5.99
2018-03-28 10:00 | 6.48 | 6.44
2018-03-28 10:30 | 6.35 | 6.31
2018-03-28 11:00 | 6.41 | 6.35
2018-03-28 11:30 | 6.95 | 6.88
2018-03-28 12:00 | 7.33 | 7.26
2018-03-28 12:30 | 7.27 | 7.2
2018-03-28 13:00 | 7.04 | 6.95
2018-03-28 13:30 | 8.09 | 8
2018-03-28 14:00 | 8.7 | 8.6
2018-03-28 14:30 | 8.99 | 8.89
2018-03-28 15:00 | 9.34 | 9.24
2018-03-28 15:30 | 10.15 | 10.06
2018-03-28 16:00 | 11.91 | 11.83
2018-03-28 16:30 | 13 | 12.92
2018-03-28 17:00 | 13.3 | 13.23
2018-03-28 17:30 | 13.56 | 13.5
2018-03-28 18:00 | 13.66 | 13.6
2018-03-28 18:30 | 14.74 | 14.63
2018-03-28 19:00 | 14.93 | 14.83
2018-03-28 19:30 | 14.12 | 14.03
2018-03-28 20:00 | 13.89 | 13.82
2018-03-28 20:30 | 13.63 | 13.57
2018-03-28 21:00 | 12.73 | 12.68
2018-03-28 21:30 | 11.28 | 11.25
2018-03-28 22:00 | 9.98 | 9.97
2018-03-28 22:30 | 9.44 | 9.43
2018-03-28 23:00 | 9.05 | 9.04
2018-03-28 23:30 | 7.85 | 7.84
2018-03-29 | 6.92 | 6.91
2018-03-29 00:30 | 6.41 | 6.4
2018-03-29 01:00 | 6.17 | 6.16
2018-03-29 01:30 | 5.79 | 5.78
2018-03-29 02:00 | 5.54 | 5.53
2018-03-29 02:30 | 5.4 | 5.38
2018-03-29 03:00 | 5.29 | 5.27
2018-03-29 03:30 | 5.24 | 5.23
2018-03-29 04:00 | 5.29 | 5.27
2018-03-29 04:30 | 5.42 | 5.41
2018-03-29 05:00 | 5.57 | 5.56
2018-03-29 05:30 | 6.07 | 6.06
2018-03-29 06:00 | 6.88 | 6.87
2018-03-29 06:30 | 7.24 | 7.24
2018-03-29 07:00 | 7.44 | 7.44
2018-03-29 07:30 | 7.47 | 7.46
2018-03-29 08:00 | 7.59 | 7.58
2018-03-29 08:30 | 6.98 | 6.97
2018-03-29 09:00 | 7.04 | 7.03
2018-03-29 09:30 | 7.16 | 7.15
2018-03-29 10:00 | 7.05 | 7.03
2018-03-29 10:30 | 7.41 | 7.4
2018-03-29 11:00 | 7.72 | 7.71
2018-03-29 11:30 | 6.76 | 6.74
2018-03-29 12:00 | 6.86 | 6.83
2018-03-29 12:30 | 7.75 | 7.72
2018-03-29 13:00 | 7.98 | 7.95
2018-03-29 13:30 | 8 | 7.98
2018-03-29 14:00 | 7.05 | 7.02
2018-03-29 14:30 | 6.78 | 6.75
2018-03-29 15:00 | 8.2 | 8.17
2018-03-29 15:30 | 8.72 | 8.68
2018-03-29 16:00 | 8.78 | 8.75
2018-03-29 16:30 | 9.08 | 9.06
2018-03-29 17:00 | 9.7 | 9.68
2018-03-29 17:30 | 10.08 | 10.05
2018-03-29 18:00 | 10.7 | 10.67
2018-03-29 18:30 | 11.64 | 11.59
2018-03-29 19:00 | 12.26 | 12.2
2018-03-29 19:30 | 11.93 | 11.89
2018-03-29 20:00 | 11.72 | 11.68
2018-03-29 20:30 | 11.53 | 11.5
2018-03-29 21:00 | 10.9 | 10.88
2018-03-29 21:30 | 10.41 | 10.4
2018-03-29 22:00 | 9.73 | 9.71
2018-03-29 22:30 | 9.34 | 9.32
2018-03-29 23:00 | 9.09 | 9.07
2018-03-29 23:30 | 8.05 | 8.03
2018-03-30 | 7.22 | 7.21
2018-03-30 00:30 | 6.73 | 6.72
2018-03-30 01:00 | 6.34 | 6.33
2018-03-30 01:30 | 5.98 | 5.97
2018-03-30 02:00 | 5.6 | 5.58
2018-03-30 02:30 | 5.35 | 5.34
2018-03-30 03:00 | 5.19 | 5.18
2018-03-30 03:30 | 5.07 | 5.05
2018-03-30 04:00 | 5.01 | 5
2018-03-30 04:30 | 4.97 | 4.96
2018-03-30 05:00 | 5.02 | 5
2018-03-30 05:30 | 5.09 | 5.07
2018-03-30 06:00 | 5.05 | 5.02
2018-03-30 06:30 | 5.02 | 4.97
2018-03-30 07:00 | 5.16 | 5.1
2018-03-30 07:30 | 5.58 | 5.54
2018-03-30 08:00 | 5.72 | 5.68
2018-03-30 08:30 | 5.95 | 5.92
2018-03-30 09:00 | 5.03 | 5.02
2018-03-30 09:30 | 5.64 | 5.63
2018-03-30 10:00 | 5.37 | 5.36
2018-03-30 10:30 | 5.61 | 5.59
2018-03-30 11:00 | 6.29 | 6.28
2018-03-30 11:30 | 8.13 | 8.12
2018-03-30 12:00 | 7.8 | 7.79
2018-03-30 12:30 | 7.22 | 7.21
2018-03-30 13:00 | 7.47 | 7.45
2018-03-30 13:30 | 6.5 | 6.47
2018-03-30 14:00 | 7 | 6.97
2018-03-30 14:30 | 8.08 | 8.06
2018-03-30 15:00 | 8.11 | 8.09
2018-03-30 15:30 | 9.65 | 9.63
2018-03-30 16:00 | 9.7 | 9.68
2018-03-30 16:30 | 10.11 | 10.09
2018-03-30 17:00 | 10.29 | 10.27
2018-03-30 17:30 | 10.49 | 10.47
2018-03-30 18:00 | 10.83 | 10.81
2018-03-30 18:30 | 11.46 | 11.43
2018-03-30 19:00 | 11.69 | 11.66
2018-03-30 19:30 | 11.39 | 11.37
2018-03-30 20:00 | 11.24 | 11.22
2018-03-30 20:30 | 10.83 | 10.81
2018-03-30 21:00 | 10.37 | 10.35
2018-03-30 21:30 | 9.79 | 9.78
2018-03-30 22:00 | 9.3 | 9.29
2018-03-30 22:30 | 9.02 | 9.01
2018-03-30 23:00 | 8.71 | 8.69
2018-03-30 23:30 | 7.79 | 7.78
2018-03-31 | 6.98 | 6.97
2018-03-31 00:30 | 6.54 | 6.52
2018-03-31 01:00 | 6.2 | 6.19
2018-03-31 01:30 | 5.83 | 5.82
2018-03-31 02:00 | 5.53 | 5.52
2018-03-31 02:30 | 5.29 | 5.27
2018-03-31 03:00 | 5.08 | 5.06
2018-03-31 03:30 | 5.07 | 5.06
2018-03-31 04:00 | 5.05 | 5.03
2018-03-31 04:30 | 5 | 4.98
2018-03-31 05:00 | 4.95 | 4.93
2018-03-31 05:30 | 5.01 | 4.99
2018-03-31 06:00 | 5.01 | 4.98
2018-03-31 06:30 | 5.05 | 5.02
2018-03-31 07:00 | 5.23 | 5.2
2018-03-31 07:30 | 5.24 | 5.21
2018-03-31 08:00 | 5.46 | 5.44
2018-03-31 08:30 | 5.89 | 5.86
2018-03-31 09:00 | 6.2 | 6.17
2018-03-31 09:30 | 5.85 | 5.8
2018-03-31 10:00 | 6.71 | 6.66
2018-03-31 10:30 | 5.94 | 5.88
2018-03-31 11:00 | 6.19 | 6.13
2018-03-31 11:30 | 6.21 | 6.14
2018-03-31 12:00 | 6.69 | 6.62
2018-03-31 12:30 | 6.69 | 6.61
2018-03-31 13:00 | 7.15 | 7.06
2018-03-31 13:30 | 7.02 | 6.93
2018-03-31 14:00 | 7.62 | 7.54
2018-03-31 14:30 | 8.36 | 8.29
2018-03-31 15:00 | 8.71 | 8.65
2018-03-31 15:30 | 9.37 | 9.31
2018-03-31 16:00 | 9.86 | 9.81
2018-03-31 16:30 | 10.65 | 10.6
2018-03-31 17:00 | 11 | 10.95
2018-03-31 17:30 | 11.42 | 11.38
2018-03-31 18:00 | 11.34 | 11.31
2018-03-31 18:30 | 11.85 | 11.81
2018-03-31 19:00 | 12.11 | 12.07
2018-03-31 19:30 | 11.74 | 11.7
2018-03-31 20:00 | 11.36 | 11.34
2018-03-31 20:30 | 11.05 | 11.02
2018-03-31 21:00 | 10.28 | 10.26
2018-03-31 21:30 | 9.74 | 9.73
2018-03-31 22:00 | 9.17 | 9.16
2018-03-31 22:30 | 9 | 8.99
2018-03-31 23:00 | 8.6 | 8.58
2018-03-31 23:30 | 7.72 | 7.7
2018-04-01 | 6.87 | 6.86
2018-04-01 00:30 | 6.29 | 6.28
2018-04-01 01:00 | 5.99 | 5.98
2018-04-01 01:30 | 5.65 | 5.64
2018-04-01 02:00 | 5.4 | 5.39
2018-04-01 02:30 | 5.34 | 5.32
2018-04-01 03:00 | 5.18 | 5.16
2018-04-01 03:30 | 5.13 | 5.12
2018-04-01 04:00 | 4.97 | 4.95
2018-04-01 04:30 | 4.92 | 4.9
2018-04-01 05:00 | 4.99 | 4.97
2018-04-01 05:30 | 5.09 | 5.07
2018-04-01 06:00 | 4.97 | 4.94
2018-04-01 06:30 | 5.04 | 4.99
2018-04-01 07:00 | 5.04 | 4.99
2018-04-01 07:30 | 5.1 | 5.07
2018-04-01 08:00 | 5.22 | 5.2
2018-04-01 08:30 | 5.36 | 5.33
2018-04-01 09:00 | 5.33 | 5.3
2018-04-01 09:30 | 5.67 | 5.64
2018-04-01 10:00 | 6.15 | 6.11
2018-04-01 10:30 | 6.33 | 6.29
2018-04-01 11:00 | 6.76 | 6.72
2018-04-01 11:30 | 6.82 | 6.77
2018-04-01 12:00 | 7.46 | 7.41
2018-04-01 12:30 | 6.76 | 6.68
2018-04-01 13:00 | 8.74 | 8.69
2018-04-01 13:30 | 9.37 | 9.33
2018-04-01 14:00 | 9.09 | 9.04
2018-04-01 14:30 | 8.74 | 8.7
2018-04-01 15:00 | 8.06 | 8.02
2018-04-01 15:30 | 9.49 | 9.45
2018-04-01 16:00 | 9.93 | 9.9
2018-04-01 16:30 | 10.82 | 10.79
2018-04-01 17:00 | 11.34 | 11.31
2018-04-01 17:30 | 11.36 | 11.34
2018-04-01 18:00 | 11.23 | 11.21
2018-04-01 18:30 | 11.73 | 11.69
2018-04-01 19:00 | 11.78 | 11.75
2018-04-01 19:30 | 11.33 | 11.3
2018-04-01 20:00 | 11.25 | 11.23
2018-04-01 20:30 | 10.93 | 10.91
2018-04-01 21:00 | 10.31 | 10.3
2018-04-01 21:30 | 9.67 | 9.66
2018-04-01 22:00 | 8.97 | 8.96
2018-04-01 22:30 | 8.83 | 8.82
2018-04-01 23:00 | 8.7 | 8.69
2018-04-01 23:30 | 7.81 | 7.8
2018-04-02 | 6.88 | 6.87
2018-04-02 00:30 | 6.35 | 6.34
2018-04-02 01:00 | 6.14 | 6.13
2018-04-02 01:30 | 5.75 | 5.73
2018-04-02 02:00 | 5.44 | 5.42
2018-04-02 02:30 | 5.29 | 5.27
2018-04-02 03:00 | 5.14 | 5.12
2018-04-02 03:30 | 5.14 | 5.12
2018-04-02 04:00 | 4.95 | 4.94
2018-04-02 04:30 | 4.95 | 4.93
2018-04-02 05:00 | 4.99 | 4.98
2018-04-02 05:30 | 5.05 | 5.03
2018-04-02 06:00 | 4.99 | 4.96
2018-04-02 06:30 | 4.95 | 4.9
2018-04-02 07:00 | 4.79 | 4.74
2018-04-02 07:30 | 4.79 | 4.76
2018-04-02 08:00 | 4.84 | 4.81
2018-04-02 08:30 | 5.3 | 5.28
2018-04-02 09:00 | 5.89 | 5.86
2018-04-02 09:30 | 6.14 | 6.1
2018-04-02 10:00 | 6.26 | 6.22
2018-04-02 10:30 | 7.29 | 7.24
2018-04-02 11:00 | 8.04 | 8
2018-04-02 11:30 | 8.31 | 8.27
2018-04-02 12:00 | 8.93 | 8.89
2018-04-02 12:30 | 9.95 | 9.92
2018-04-02 13:00 | 8.55 | 8.51
2018-04-02 13:30 | 7.57 | 7.53
2018-04-02 14:00 | 7.79 | 7.74
2018-04-02 14:30 | 8.75 | 8.71
2018-04-02 15:00 | 9.65 | 9.61
2018-04-02 15:30 | 9.87 | 9.83
2018-04-02 16:00 | 10.49 | 10.44
2018-04-02 16:30 | 11.08 | 11.04
2018-04-02 17:00 | 11.51 | 11.48
2018-04-02 17:30 | 12 | 11.97
2018-04-02 18:00 | 12.48 | 12.45
2018-04-02 18:30 | 13.1 | 13.05
2018-04-02 19:00 | 13.09 | 13.05
2018-04-02 19:30 | 12.37 | 12.35
2018-04-02 20:00 | 11.89 | 11.87
2018-04-02 20:30 | 11.55 | 11.53
2018-04-02 21:00 | 10.71 | 10.69
2018-04-02 21:30 | 10.01 | 10
2018-04-02 22:00 | 9.19 | 9.18
2018-04-02 22:30 | 8.79 | 8.77
2018-04-02 23:00 | 8.44 | 8.43
2018-04-02 23:30 | 7.57 | 7.56
2018-04-03 | 6.64 | 6.63
2018-04-03 00:30 | 6 | 5.99
2018-04-03 01:00 | 5.74 | 5.73
2018-04-03 01:30 | 5.5 | 5.49
2018-04-03 02:00 | 5.23 | 5.22
2018-04-03 02:30 | 5.07 | 5.05
2018-04-03 03:00 | 4.96 | 4.94
2018-04-03 03:30 | 4.87 | 4.85
2018-04-03 04:00 | 4.86 | 4.84
2018-04-03 04:30 | 5.05 | 5.03
2018-04-03 05:00 | 5.24 | 5.22
2018-04-03 05:30 | 5.51 | 5.49
2018-04-03 06:00 | 5.54 | 5.52
2018-04-03 06:30 | 5.77 | 5.73
2018-04-03 07:00 | 5.71 | 5.68
2018-04-03 07:30 | 5.6 | 5.58
2018-04-03 08:00 | 5.66 | 5.64
2018-04-03 08:30 | 5.36 | 5.34
2018-04-03 09:00 | 5.8 | 5.78
2018-04-03 09:30 | 7.1 | 7.08
2018-04-03 10:00 | 6.4 | 6.37
2018-04-03 10:30 | 5.64 | 5.61
2018-04-03 11:00 | 4.84 | 4.79
2018-04-03 11:30 | 4.68 | 4.63
2018-04-03 12:00 | 6.1 | 6.06
2018-04-03 12:30 | 4.84 | 4.79
2018-04-03 13:00 | 5.43 | 5.39
2018-04-03 13:30 | 5.71 | 5.67
2018-04-03 14:00 | 6.35 | 6.31
2018-04-03 14:30 | 6.77 | 6.74
2018-04-03 15:00 | 7.48 | 7.46
2018-04-03 15:30 | 8.02 | 8
2018-04-03 16:00 | 9.11 | 9.09
2018-04-03 16:30 | 10.08 | 10.06
2018-04-03 17:00 | 10.56 | 10.54
2018-04-03 17:30 | 11.33 | 11.31
2018-04-03 18:00 | 11.93 | 11.91
2018-04-03 18:30 | 12.96 | 12.91
2018-04-03 19:00 | 13.38 | 13.34
2018-04-03 19:30 | 12.79 | 12.75
2018-04-03 20:00 | 12.36 | 12.33
2018-04-03 20:30 | 11.78 | 11.77
2018-04-03 21:00 | 10.74 | 10.73
2018-04-03 21:30 | 9.84 | 9.83
2018-04-03 22:00 | 9.06 | 9.05
2018-04-03 22:30 | 8.65 | 8.64
2018-04-03 23:00 | 8.31 | 8.3
2018-04-03 23:30 | 7.25 | 7.24
2018-04-04 | 6.42 | 6.41
2018-04-04 00:30 | 5.83 | 5.82
2018-04-04 01:00 | 5.73 | 5.72
2018-04-04 01:30 | 5.41 | 5.4
2018-04-04 02:00 | 5.2 | 5.19
2018-04-04 02:30 | 5.03 | 5.01
2018-04-04 03:00 | 4.93 | 4.91
2018-04-04 03:30 | 4.84 | 4.83
2018-04-04 04:00 | 4.94 | 4.93
2018-04-04 04:30 | 5.03 | 5.02
2018-04-04 05:00 | 5.16 | 5.14
2018-04-04 05:30 | 5.67 | 5.66
2018-04-04 06:00 | 6.21 | 6.2
2018-04-04 06:30 | 6.34 | 6.32
2018-04-04 07:00 | 6.49 | 6.47
2018-04-04 07:30 | 6.64 | 6.62
2018-04-04 08:00 | 6.83 | 6.82
2018-04-04 08:30 | 7.17 | 7.16
2018-04-04 09:00 | 7.18 | 7.18
2018-04-04 09:30 | 7.3 | 7.29
2018-04-04 10:00 | 6.99 | 6.98
2018-04-04 10:30 | 5.77 | 5.76
2018-04-04 11:00 | 4.97 | 4.95
2018-04-04 11:30 | 5.27 | 5.24
2018-04-04 12:00 | 5.73 | 5.71
2018-04-04 12:30 | 7.71 | 7.69
2018-04-04 13:00 | 6.64 | 6.63
2018-04-04 13:30 | 6.27 | 6.26
2018-04-04 14:00 | 6.39 | 6.38
2018-04-04 14:30 | 6.46 | 6.44
2018-04-04 15:00 | 7.03 | 7.02
2018-04-04 15:30 | 7.33 | 7.32
2018-04-04 16:00 | 7.94 | 7.93
2018-04-04 16:30 | 8.98 | 8.97
2018-04-04 17:00 | 9.16 | 9.15
2018-04-04 17:30 | 10.21 | 10.19
2018-04-04 18:00 | 11.23 | 11.22
2018-04-04 18:30 | 12.19 | 12.16
2018-04-04 19:00 | 12.29 | 12.27
2018-04-04 19:30 | 12.11 | 12.08
2018-04-04 20:00 | 12.09 | 12.07
2018-04-04 20:30 | 11.32 | 11.31
2018-04-04 21:00 | 10.41 | 10.4
2018-04-04 21:30 | 9.5 | 9.48
2018-04-04 22:00 | 8.82 | 8.81
2018-04-04 22:30 | 8.42 | 8.41
2018-04-04 23:00 | 8.25 | 8.24
2018-04-04 23:30 | 7.28 | 7.28
2018-04-05 | 6.44 | 6.43
2018-04-05 00:30 | 5.84 | 5.83
2018-04-05 01:00 | 5.6 | 5.58
2018-04-05 01:30 | 5.29 | 5.27
2018-04-05 02:00 | 5.02 | 5
2018-04-05 02:30 | 4.92 | 4.9
2018-04-05 03:00 | 4.72 | 4.69
2018-04-05 03:30 | 4.79 | 4.76
2018-04-05 04:00 | 4.75 | 4.72
2018-04-05 04:30 | 4.86 | 4.84
2018-04-05 05:00 | 5.09 | 5.08
2018-04-05 05:30 | 5.39 | 5.38
2018-04-05 06:00 | 5.55 | 5.52
2018-04-05 06:30 | 5.64 | 5.6
2018-04-05 07:00 | 5.67 | 5.63
2018-04-05 07:30 | 5.77 | 5.74
2018-04-05 08:00 | 5.85 | 5.84
2018-04-05 08:30 | 6.28 | 6.28
2018-04-05 09:00 | 5 | 4.99
2018-04-05 09:30 | 4.6 | 4.59
2018-04-05 10:00 | 4.73 | 4.71
2018-04-05 10:30 | 4.6 | 4.58
2018-04-05 11:00 | 4.68 | 4.66
2018-04-05 11:30 | 4.97 | 4.95
2018-04-05 12:00 | 4.87 | 4.85
2018-04-05 12:30 | 5.74 | 5.71
2018-04-05 13:00 | 4.67 | 4.64
2018-04-05 13:30 | 6.29 | 6.27
2018-04-05 14:00 | 7.78 | 7.76
2018-04-05 14:30 | 6.78 | 6.76
2018-04-05 15:00 | 7.61 | 7.59
2018-04-05 15:30 | 7.41 | 7.39
2018-04-05 16:00 | 7.77 | 7.76
2018-04-05 16:30 | 8.41 | 8.39
2018-04-05 17:00 | 9.91 | 9.9
2018-04-05 17:30 | 10.52 | 10.51
2018-04-05 18:00 | 11.34 | 11.33
2018-04-05 18:30 | 12.13 | 12.09
2018-04-05 19:00 | 12.47 | 12.43
2018-04-05 19:30 | 11.88 | 11.85
2018-04-05 20:00 | 11.76 | 11.74
2018-04-05 20:30 | 11.45 | 11.44
2018-04-05 21:00 | 10.27 | 10.26
2018-04-05 21:30 | 9.48 | 9.47
2018-04-05 22:00 | 8.7 | 8.69
2018-04-05 22:30 | 8.4 | 8.39
2018-04-05 23:00 | 8.12 | 8.12
2018-04-05 23:30 | 7.17 | 7.16
2018-04-06 | 6.32 | 6.3
2018-04-06 00:30 | 5.72 | 5.7
2018-04-06 01:00 | 5.52 | 5.5
2018-04-06 01:30 | 5.18 | 5.16
2018-04-06 02:00 | 4.98 | 4.96
2018-04-06 02:30 | 4.8 | 4.78
2018-04-06 03:00 | 4.56 | 4.53
2018-04-06 03:30 | 4.73 | 4.7
2018-04-06 04:00 | 4.62 | 4.59
2018-04-06 04:30 | 4.77 | 4.74
2018-04-06 05:00 | 4.87 | 4.84
2018-04-06 05:30 | 5.31 | 5.3
2018-04-06 06:00 | 5.93 | 5.92
2018-04-06 06:30 | 6.04 | 6.02
2018-04-06 07:00 | 6.12 | 6.09
2018-04-06 07:30 | 5.86 | 5.84
2018-04-06 08:00 | 6.06 | 6.04
2018-04-06 08:30 | 6.68 | 6.67
2018-04-06 09:00 | 5.95 | 5.94
2018-04-06 09:30 | 5.68 | 5.68
2018-04-06 10:00 | 5.66 | 5.65
2018-04-06 10:30 | 5.76 | 5.75
2018-04-06 11:00 | 5.01 | 4.99
2018-04-06 11:30 | 4.85 | 4.82
2018-04-06 12:00 | 5.52 | 5.49
2018-04-06 12:30 | 5.57 | 5.55
2018-04-06 13:00 | 5.01 | 4.98
2018-04-06 13:30 | 5.13 | 5.1
2018-04-06 14:00 | 5.58 | 5.55
2018-04-06 14:30 | 5.9 | 5.87
2018-04-06 15:00 | 6.56 | 6.53
2018-04-06 15:30 | 7.38 | 7.36
2018-04-06 16:00 | 8.07 | 8.06
2018-04-06 16:30 | 8.81 | 8.79
2018-04-06 17:00 | 9.26 | 9.24
2018-04-06 17:30 | 9.86 | 9.84
2018-04-06 18:00 | 10.41 | 10.39
2018-04-06 18:30 | 11.33 | 11.3
2018-04-06 19:00 | 11.61 | 11.59
2018-04-06 19:30 | 11.11 | 11.09
2018-04-06 20:00 | 10.93 | 10.91
2018-04-06 20:30 | 10.71 | 10.7
2018-04-06 21:00 | 9.95 | 9.94
2018-04-06 21:30 | 9.44 | 9.43
2018-04-06 22:00 | 8.8 | 8.79
2018-04-06 22:30 | 8.58 | 8.57
2018-04-06 23:00 | 8.19 | 8.18
2018-04-06 23:30 | 7.42 | 7.41
2018-04-07 | 6.57 | 6.56
2018-04-07 00:30 | 5.89 | 5.88
2018-04-07 01:00 | 5.7 | 5.69
2018-04-07 01:30 | 5.37 | 5.35
2018-04-07 02:00 | 5.06 | 5.04
2018-04-07 02:30 | 4.85 | 4.83
2018-04-07 03:00 | 4.67 | 4.64
2018-04-07 03:30 | 4.69 | 4.67
2018-04-07 04:00 | 4.65 | 4.63
2018-04-07 04:30 | 4.75 | 4.73
2018-04-07 05:00 | 4.78 | 4.76
2018-04-07 05:30 | 4.82 | 4.8
2018-04-07 06:00 | 4.77 | 4.73
2018-04-07 06:30 | 4.93 | 4.87
2018-04-07 07:00 | 4.99 | 4.93
2018-04-07 07:30 | 4.84 | 4.8
2018-04-07 08:00 | 4.91 | 4.88
2018-04-07 08:30 | 4.94 | 4.92
2018-04-07 09:00 | 4.88 | 4.85
2018-04-07 09:30 | 4.9 | 4.86
2018-04-07 10:00 | 5.64 | 5.6
2018-04-07 10:30 | 5.15 | 5.1
2018-04-07 11:00 | 4.93 | 4.89
2018-04-07 11:30 | 4.8 | 4.74
2018-04-07 12:00 | 5.87 | 5.83
2018-04-07 12:30 | 5.75 | 5.71
2018-04-07 13:00 | 5.96 | 5.91
2018-04-07 13:30 | 5.52 | 5.46
2018-04-07 14:00 | 6.34 | 6.29
2018-04-07 14:30 | 7.12 | 7.08
2018-04-07 15:00 | 7.35 | 7.31
2018-04-07 15:30 | 7.81 | 7.77
2018-04-07 16:00 | 8.69 | 8.66
2018-04-07 16:30 | 9.29 | 9.26
2018-04-07 17:00 | 9.65 | 9.63
2018-04-07 17:30 | 10.04 | 10.03
2018-04-07 18:00 | 10.24 | 10.22
2018-04-07 18:30 | 10.78 | 10.76
2018-04-07 19:00 | 10.95 | 10.94
2018-04-07 19:30 | 10.48 | 10.46
2018-04-07 20:00 | 10.33 | 10.32
2018-04-07 20:30 | 9.99 | 9.98
2018-04-07 21:00 | 9.29 | 9.28
2018-04-07 21:30 | 8.8 | 8.79
2018-04-07 22:00 | 8.38 | 8.37
2018-04-07 22:30 | 8.03 | 8.03
2018-04-07 23:00 | 7.93 | 7.92
2018-04-07 23:30 | 7.22 | 7.21
2018-04-08 | 6.37 | 6.35
2018-04-08 00:30 | 5.86 | 5.85
2018-04-08 01:00 | 5.57 | 5.56
2018-04-08 01:30 | 5.15 | 5.13
2018-04-08 02:00 | 4.97 | 4.95
2018-04-08 02:30 | 4.71 | 4.68
2018-04-08 03:00 | 4.61 | 4.59
2018-04-08 03:30 | 4.58 | 4.55
2018-04-08 04:00 | 4.46 | 4.43
2018-04-08 04:30 | 4.45 | 4.42
2018-04-08 05:00 | 4.46 | 4.42
2018-04-08 05:30 | 4.55 | 4.52
2018-04-08 06:00 | 4.59 | 4.55
2018-04-08 06:30 | 4.75 | 4.69
2018-04-08 07:00 | 4.73 | 4.64
2018-04-08 07:30 | 5.09 | 5.02
2018-04-08 08:00 | 5.63 | 5.58
2018-04-08 08:30 | 5.77 | 5.72
2018-04-08 09:00 | 6.09 | 6.07
2018-04-08 09:30 | 6.25 | 6.24
2018-04-08 10:00 | 4.74 | 4.72
2018-04-08 10:30 | 4.71 | 4.68
2018-04-08 11:00 | 5.01 | 4.98
2018-04-08 11:30 | 4.96 | 4.93
2018-04-08 12:00 | 4.97 | 4.93
2018-04-08 12:30 | 5.84 | 5.8
2018-04-08 13:00 | 6.09 | 6.05
2018-04-08 13:30 | 6.58 | 6.54
2018-04-08 14:00 | 6.09 | 6.05
2018-04-08 14:30 | 6.63 | 6.6
2018-04-08 15:00 | 7.23 | 7.2
2018-04-08 15:30 | 7.97 | 7.94
2018-04-08 16:00 | 8.38 | 8.36
2018-04-08 16:30 | 9.22 | 9.2
2018-04-08 17:00 | 10.04 | 10.02
2018-04-08 17:30 | 10.76 | 10.74
2018-04-08 18:00 | 11.37 | 11.35
2018-04-08 18:30 | 12.06 | 12.04
2018-04-08 19:00 | 11.84 | 11.82
2018-04-08 19:30 | 11.09 | 11.08
2018-04-08 20:00 | 10.85 | 10.84
2018-04-08 20:30 | 10.44 | 10.43
2018-04-08 21:00 | 9.75 | 9.74
2018-04-08 21:30 | 9.05 | 9.04
2018-04-08 22:00 | 8.39 | 8.39
2018-04-08 22:30 | 8.02 | 8.01
2018-04-08 23:00 | 7.76 | 7.75
2018-04-08 23:30 | 6.92 | 6.9
2018-04-09 | 6.04 | 6.02
2018-04-09 00:30 | 5.43 | 5.41
2018-04-09 01:00 | 5.21 | 5.19
2018-04-09 01:30 | 4.91 | 4.88
2018-04-09 02:00 | 4.58 | 4.55
2018-04-09 02:30 | 4.53 | 4.49
2018-04-09 03:00 | 4.46 | 4.42
2018-04-09 03:30 | 4.42 | 4.39
2018-04-09 04:00 | 4.41 | 4.37
2018-04-09 04:30 | 4.52 | 4.48
2018-04-09 05:00 | 4.73 | 4.7
2018-04-09 05:30 | 5.17 | 5.14
2018-04-09 06:00 | 5.87 | 5.85
2018-04-09 06:30 | 6.04 | 6.01
2018-04-09 07:00 | 6.01 | 5.98
2018-04-09 07:30 | 5.66 | 5.64
2018-04-09 08:00 | 5.44 | 5.43
2018-04-09 08:30 | 5.07 | 5.06
2018-04-09 09:00 | 4.65 | 4.64
2018-04-09 09:30 | 4.41 | 4.39
2018-04-09 10:00 | 4.37 | 4.34
2018-04-09 10:30 | 4.45 | 4.42
2018-04-09 11:00 | 4.57 | 4.54
2018-04-09 11:30 | 4.26 | 4.21
2018-04-09 12:00 | 4.4 | 4.35
2018-04-09 12:30 | 4.53 | 4.48
2018-04-09 13:00 | 4.98 | 4.93
2018-04-09 13:30 | 5.38 | 5.34
2018-04-09 14:00 | 6.01 | 5.95
2018-04-09 14:30 | 6.57 | 6.51
2018-04-09 15:00 | 7.19 | 7.14
2018-04-09 15:30 | 8.12 | 8.07
2018-04-09 16:00 | 9.01 | 8.97
2018-04-09 16:30 | 9.95 | 9.92
2018-04-09 17:00 | 10.79 | 10.76
2018-04-09 17:30 | 11.42 | 11.39
2018-04-09 18:00 | 12.11 | 12.07
2018-04-09 18:30 | 12.85 | 12.8
2018-04-09 19:00 | 12.98 | 12.94
2018-04-09 19:30 | 12.36 | 12.33
2018-04-09 20:00 | 12.04 | 12.02
2018-04-09 20:30 | 11.52 | 11.5
2018-04-09 21:00 | 10.69 | 10.67
2018-04-09 21:30 | 9.78 | 9.76
2018-04-09 22:00 | 9.01 | 8.99
2018-04-09 22:30 | 8.43 | 8.42
2018-04-09 23:00 | 8.06 | 8.05
2018-04-09 23:30 | 7.04 | 7.03
2018-04-10 | 6.18 | 6.17
2018-04-10 00:30 | 5.56 | 5.54
2018-04-10 01:00 | 5.26 | 5.24
2018-04-10 01:30 | 4.92 | 4.89
2018-04-10 02:00 | 4.64 | 4.61
2018-04-10 02:30 | 4.56 | 4.53
2018-04-10 03:00 | 4.48 | 4.45
2018-04-10 03:30 | 4.48 | 4.45
2018-04-10 04:00 | 4.49 | 4.46
2018-04-10 04:30 | 4.58 | 4.55
2018-04-10 05:00 | 4.82 | 4.79
2018-04-10 05:30 | 5.15 | 5.12
2018-04-10 06:00 | 5.32 | 5.29
2018-04-10 06:30 | 5.44 | 5.38
2018-04-10 07:00 | 5.37 | 5.31
2018-04-10 07:30 | 5.1 | 5.06
2018-04-10 08:00 | 4.73 | 4.69
2018-04-10 08:30 | 4.29 | 4.25
2018-04-10 09:00 | 3.88 | 3.85
2018-04-10 09:30 | 3.67 | 3.64
2018-04-10 10:00 | 3.59 | 3.56
2018-04-10 10:30 | 3.68 | 3.64
2018-04-10 11:00 | 3.67 | 3.63
2018-04-10 11:30 | 3.9 | 3.85
2018-04-10 12:00 | 4.81 | 4.76
2018-04-10 12:30 | 4.96 | 4.92
2018-04-10 13:00 | 5.53 | 5.49
2018-04-10 13:30 | 6.09 | 6.04
2018-04-10 14:00 | 6.71 | 6.66
2018-04-10 14:30 | 7.43 | 7.39
2018-04-10 15:00 | 8.59 | 8.56
2018-04-10 15:30 | 9.97 | 9.94
2018-04-10 16:00 | 9.64 | 9.62
2018-04-10 16:30 | 9.27 | 9.25
2018-04-10 17:00 | 10.29 | 10.26
2018-04-10 17:30 | 11.41 | 11.39
2018-04-10 18:00 | 11.97 | 11.94
2018-04-10 18:30 | 12.91 | 12.86
2018-04-10 19:00 | 13.1 | 13.05
2018-04-10 19:30 | 12.67 | 12.62
2018-04-10 20:00 | 12.24 | 12.21
2018-04-10 20:30 | 11.46 | 11.44
2018-04-10 21:00 | 10.96 | 10.95
2018-04-10 21:30 | 10.39 | 10.38
2018-04-10 22:00 | 9.52 | 9.52
2018-04-10 22:30 | 8.65 | 8.64
2018-04-10 23:00 | 8.23 | 8.22
2018-04-10 23:30 | 7.07 | 7.06
2018-04-11 | 6.19 | 6.18
2018-04-11 00:30 | 5.64 | 5.62
2018-04-11 01:00 | 5.42 | 5.4
2018-04-11 01:30 | 5.11 | 5.09
2018-04-11 02:00 | 4.84 | 4.82
2018-04-11 02:30 | 4.69 | 4.67
2018-04-11 03:00 | 4.65 | 4.63
2018-04-11 03:30 | 4.67 | 4.64
2018-04-11 04:00 | 4.59 | 4.57
2018-04-11 04:30 | 4.8 | 4.78
2018-04-11 05:00 | 5 | 4.98
2018-04-11 05:30 | 5.47 | 5.46
2018-04-11 06:00 | 6.15 | 6.14
2018-04-11 06:30 | 6.22 | 6.2
2018-04-11 07:00 | 6.38 | 6.36
2018-04-11 07:30 | 5.83 | 5.82
2018-04-11 08:00 | 5.13 | 5.11
2018-04-11 08:30 | 5.06 | 5.05
2018-04-11 09:00 | 4.98 | 4.97
2018-04-11 09:30 | 4.77 | 4.75
2018-04-11 10:00 | 5.37 | 5.35
2018-04-11 10:30 | 4.53 | 4.51
2018-04-11 11:00 | 4.78 | 4.76
2018-04-11 11:30 | 4.45 | 4.43
2018-04-11 12:00 | 5.26 | 5.24
2018-04-11 12:30 | 5.22 | 5.2
2018-04-11 13:00 | 5.19 | 5.17
2018-04-11 13:30 | 5.09 | 5.06
2018-04-11 14:00 | 5.67 | 5.64
2018-04-11 14:30 | 6.1 | 6.08
2018-04-11 15:00 | 6.69 | 6.68
2018-04-11 15:30 | 7.39 | 7.37
2018-04-11 16:00 | 7.94 | 7.93
2018-04-11 16:30 | 8.87 | 8.86
2018-04-11 17:00 | 9.93 | 9.92
2018-04-11 17:30 | 10.59 | 10.58
2018-04-11 18:00 | 11.31 | 11.3
2018-04-11 18:30 | 12.17 | 12.14
2018-04-11 19:00 | 12.5 | 12.47
2018-04-11 19:30 | 12.09 | 12.07
2018-04-11 20:00 | 11.79 | 11.77
2018-04-11 20:30 | 11.54 | 11.53
2018-04-11 21:00 | 10.87 | 10.86
2018-04-11 21:30 | 10.04 | 10.03
2018-04-11 22:00 | 9.25 | 9.25
2018-04-11 22:30 | 8.45 | 8.45
2018-04-11 23:00 | 7.92 | 7.91
2018-04-11 23:30 | 6.89 | 6.88
2018-04-12 | 5.99 | 5.97
2018-04-12 00:30 | 5.43 | 5.41
2018-04-12 01:00 | 5.18 | 5.16
2018-04-12 01:30 | 4.91 | 4.89
2018-04-12 02:00 | 4.64 | 4.61
2018-04-12 02:30 | 4.5 | 4.47
2018-04-12 03:00 | 4.56 | 4.53
2018-04-12 03:30 | 4.49 | 4.46
2018-04-12 04:00 | 4.37 | 4.34
2018-04-12 04:30 | 4.6 | 4.57
2018-04-12 05:00 | 4.75 | 4.72
2018-04-12 05:30 | 5.11 | 5.08
2018-04-12 06:00 | 5.49 | 5.47
2018-04-12 06:30 | 6.08 | 6.05
2018-04-12 07:00 | 6.16 | 6.13
2018-04-12 07:30 | 6.03 | 6.01
2018-04-12 08:00 | 5.93 | 5.91
2018-04-12 08:30 | 6.04 | 6.03
2018-04-12 09:00 | 5.45 | 5.45
2018-04-12 09:30 | 5.13 | 5.13
2018-04-12 10:00 | 4.83 | 4.82
2018-04-12 10:30 | 5.49 | 5.48
2018-04-12 11:00 | 6.61 | 6.6
2018-04-12 11:30 | 6.89 | 6.87
2018-04-12 12:00 | 7.37 | 7.36
2018-04-12 12:30 | 5.38 | 5.37
2018-04-12 13:00 | 5.11 | 5.09
2018-04-12 13:30 | 6.66 | 6.65
2018-04-12 14:00 | 7.19 | 7.18
2018-04-12 14:30 | 7.25 | 7.24
2018-04-12 15:00 | 5.75 | 5.74
2018-04-12 15:30 | 6.43 | 6.41
2018-04-12 16:00 | 7.61 | 7.59
2018-04-12 16:30 | 8.68 | 8.67
2018-04-12 17:00 | 9.12 | 9.11
2018-04-12 17:30 | 10.26 | 10.25
2018-04-12 18:00 | 11.21 | 11.19
2018-04-12 18:30 | 11.96 | 11.92
2018-04-12 19:00 | 11.91 | 11.88
2018-04-12 19:30 | 11.81 | 11.78
2018-04-12 20:00 | 11.72 | 11.7
2018-04-12 20:30 | 11.43 | 11.42
2018-04-12 21:00 | 10.73 | 10.72
2018-04-12 21:30 | 9.86 | 9.85
2018-04-12 22:00 | 8.95 | 8.94
2018-04-12 22:30 | 8.27 | 8.26
2018-04-12 23:00 | 7.9 | 7.88
2018-04-12 23:30 | 6.77 | 6.75
2018-04-13 | 6.05 | 6.03
2018-04-13 00:30 | 5.4 | 5.38
2018-04-13 01:00 | 5.09 | 5.06
2018-04-13 01:30 | 4.78 | 4.75
2018-04-13 02:00 | 4.63 | 4.59
2018-04-13 02:30 | 4.48 | 4.44
2018-04-13 03:00 | 4.3 | 4.26
2018-04-13 03:30 | 4.37 | 4.33
2018-04-13 04:00 | 4.35 | 4.3
2018-04-13 04:30 | 4.57 | 4.54
2018-04-13 05:00 | 4.72 | 4.69
2018-04-13 05:30 | 5.11 | 5.08
2018-04-13 06:00 | 5.15 | 5.12
2018-04-13 06:30 | 5.32 | 5.27
2018-04-13 07:00 | 5.4 | 5.34
2018-04-13 07:30 | 5.14 | 5.08
2018-04-13 08:00 | 4.64 | 4.6
2018-04-13 08:30 | 4.35 | 4.33
2018-04-13 09:00 | 4.08 | 4.05
2018-04-13 09:30 | 3.89 | 3.86
2018-04-13 10:00 | 3.89 | 3.85
2018-04-13 10:30 | 3.78 | 3.74
2018-04-13 11:00 | 3.82 | 3.77
2018-04-13 11:30 | 4.86 | 4.81
2018-04-13 12:00 | 6.29 | 6.26
2018-04-13 12:30 | 4.75 | 4.71
2018-04-13 13:00 | 5.5 | 5.47
2018-04-13 13:30 | 5.68 | 5.64
2018-04-13 14:00 | 5.9 | 5.86
2018-04-13 14:30 | 6.25 | 6.2
2018-04-13 15:00 | 6.96 | 6.92
2018-04-13 15:30 | 7.19 | 7.15
2018-04-13 16:00 | 7.86 | 7.83
2018-04-13 16:30 | 9.45 | 9.43
2018-04-13 17:00 | 9.82 | 9.79
2018-04-13 17:30 | 9.98 | 9.95
2018-04-13 18:00 | 10.39 | 10.37
2018-04-13 18:30 | 11.17 | 11.15
2018-04-13 19:00 | 11.31 | 11.29
2018-04-13 19:30 | 10.96 | 10.94
2018-04-13 20:00 | 10.78 | 10.76
2018-04-13 20:30 | 10.62 | 10.61
2018-04-13 21:00 | 10.02 | 10.01
2018-04-13 21:30 | 9.4 | 9.39
2018-04-13 22:00 | 8.9 | 8.88
2018-04-13 22:30 | 8.56 | 8.54
2018-04-13 23:00 | 8.33 | 8.33
2018-04-13 23:30 | 7.39 | 7.38
2018-04-14 | 6.55 | 6.54
2018-04-14 00:30 | 5.95 | 5.93
2018-04-14 01:00 | 5.59 | 5.57
2018-04-14 01:30 | 5.26 | 5.24
2018-04-14 02:00 | 4.96 | 4.94
2018-04-14 02:30 | 4.84 | 4.82
2018-04-14 03:00 | 4.65 | 4.62
2018-04-14 03:30 | 4.63 | 4.6
2018-04-14 04:00 | 4.57 | 4.54
2018-04-14 04:30 | 4.57 | 4.54
2018-04-14 05:00 | 4.53 | 4.5
2018-04-14 05:30 | 4.77 | 4.74
2018-04-14 06:00 | 4.77 | 4.74
2018-04-14 06:30 | 4.81 | 4.75
2018-04-14 07:00 | 4.95 | 4.88
2018-04-14 07:30 | 5.05 | 4.99
2018-04-14 08:00 | 4.93 | 4.89
2018-04-14 08:30 | 5.68 | 5.66
2018-04-14 09:00 | 6.31 | 6.29
2018-04-14 09:30 | 6.73 | 6.71
2018-04-14 10:00 | 7.21 | 7.19
2018-04-14 10:30 | 7.48 | 7.46
2018-04-14 11:00 | 7.62 | 7.6
2018-04-14 11:30 | 7.14 | 7.11
2018-04-14 12:00 | 6.87 | 6.84
2018-04-14 12:30 | 7.02 | 6.99
2018-04-14 13:00 | 7.8 | 7.77
2018-04-14 13:30 | 7.31 | 7.27
2018-04-14 14:00 | 5.86 | 5.81
2018-04-14 14:30 | 5.53 | 5.48
2018-04-14 15:00 | 6.53 | 6.49
2018-04-14 15:30 | 7.23 | 7.19
2018-04-14 16:00 | 7.76 | 7.72
2018-04-14 16:30 | 8.59 | 8.56
2018-04-14 17:00 | 9.51 | 9.48
2018-04-14 17:30 | 10.08 | 10.05
2018-04-14 18:00 | 10.59 | 10.57
2018-04-14 18:30 | 11.17 | 11.15
2018-04-14 19:00 | 11.18 | 11.16
2018-04-14 19:30 | 10.7 | 10.68
2018-04-14 20:00 | 10.45 | 10.43
2018-04-14 20:30 | 10.31 | 10.29
2018-04-14 21:00 | 9.63 | 9.62
2018-04-14 21:30 | 9.17 | 9.16
2018-04-14 22:00 | 8.61 | 8.6
2018-04-14 22:30 | 8.46 | 8.45
2018-04-14 23:00 | 8.45 | 8.44
2018-04-14 23:30 | 7.55 | 7.54
2018-04-15 | 6.67 | 6.66
2018-04-15 00:30 | 6.04 | 6.03
2018-04-15 01:00 | 5.74 | 5.72
2018-04-15 01:30 | 5.44 | 5.42
2018-04-15 02:00 | 5.04 | 5.02
2018-04-15 02:30 | 4.86 | 4.84
2018-04-15 03:00 | 4.73 | 4.71
2018-04-15 03:30 | 4.65 | 4.63
2018-04-15 04:00 | 4.64 | 4.61
2018-04-15 04:30 | 4.61 | 4.57
2018-04-15 05:00 | 4.6 | 4.57
2018-04-15 05:30 | 4.61 | 4.58
2018-04-15 06:00 | 4.63 | 4.59
2018-04-15 06:30 | 4.65 | 4.56
2018-04-15 07:00 | 4.72 | 4.64
2018-04-15 07:30 | 4.79 | 4.73
2018-04-15 08:00 | 4.97 | 4.94
2018-04-15 08:30 | 5.18 | 5.16
2018-04-15 09:00 | 5.14 | 5.11
2018-04-15 09:30 | 5.23 | 5.2
2018-04-15 10:00 | 5.43 | 5.39
2018-04-15 10:30 | 5.31 | 5.27
2018-04-15 11:00 | 5.39 | 5.35
2018-04-15 11:30 | 5.75 | 5.7
2018-04-15 12:00 | 6.38 | 6.32
2018-04-15 12:30 | 7.12 | 7.06
2018-04-15 13:00 | 7.9 | 7.83
2018-04-15 13:30 | 8.83 | 8.76
2018-04-15 14:00 | 9.86 | 9.78
2018-04-15 14:30 | 10.88 | 10.8
2018-04-15 15:00 | 11.28 | 11.2
2018-04-15 15:30 | 11.92 | 11.84
2018-04-15 16:00 | 12.77 | 12.69
2018-04-15 16:30 | 13.53 | 13.46
2018-04-15 17:00 | 14.1 | 14.04
2018-04-15 17:30 | 14.27 | 14.21
2018-04-15 18:00 | 14.56 | 14.49
2018-04-15 18:30 | 14.95 | 14.87
2018-04-15 19:00 | 14.74 | 14.66
2018-04-15 19:30 | 13.76 | 13.69
2018-04-15 20:00 | 13.24 | 13.18
2018-04-15 20:30 | 12.47 | 12.43
2018-04-15 21:00 | 11.45 | 11.43
2018-04-15 21:30 | 10.44 | 10.43
2018-04-15 22:00 | 9.52 | 9.51
2018-04-15 22:30 | 8.98 | 8.97
2018-04-15 23:00 | 8.49 | 8.48
2018-04-15 23:30 | 7.41 | 7.4
2018-04-16 | 6.5 | 6.49
2018-04-16 00:30 | 5.82 | 5.81
2018-04-16 01:00 | 5.54 | 5.52
2018-04-16 01:30 | 5.15 | 5.13
2018-04-16 02:00 | 4.84 | 4.81
2018-04-16 02:30 | 4.71 | 4.68
2018-04-16 03:00 | 4.59 | 4.55
2018-04-16 03:30 | 4.51 | 4.48
2018-04-16 04:00 | 4.52 | 4.48
2018-04-16 04:30 | 4.65 | 4.61
2018-04-16 05:00 | 4.85 | 4.81
2018-04-16 05:30 | 5.25 | 5.22
2018-04-16 06:00 | 5.83 | 5.81
2018-04-16 06:30 | 6.15 | 6.13
2018-04-16 07:00 | 6.17 | 6.14
2018-04-16 07:30 | 5.8 | 5.78
2018-04-16 08:00 | 5.38 | 5.36
2018-04-16 08:30 | 4.96 | 4.94
2018-04-16 09:00 | 4.6 | 4.59
2018-04-16 09:30 | 4.22 | 4.2
2018-04-16 10:00 | 4 | 3.98
2018-04-16 10:30 | 4.03 | 4.01
2018-04-16 11:00 | 4.35 | 4.34
2018-04-16 11:30 | 4.47 | 4.46
2018-04-16 12:00 | 4.72 | 4.7
2018-04-16 12:30 | 5.19 | 5.17
2018-04-16 13:00 | 5.8 | 5.78
2018-04-16 13:30 | 6.37 | 6.34
2018-04-16 14:00 | 7.1 | 7.06
2018-04-16 14:30 | 7.87 | 7.83
2018-04-16 15:00 | 8.63 | 8.59
2018-04-16 15:30 | 9.67 | 9.62
2018-04-16 16:00 | 10.83 | 10.77
2018-04-16 16:30 | 11.78 | 11.73
2018-04-16 17:00 | 12.61 | 12.57
2018-04-16 17:30 | 13.02 | 12.97
2018-04-16 18:00 | 13.61 | 13.54
2018-04-16 18:30 | 14.24 | 14.16
2018-04-16 19:00 | 14.22 | 14.16
2018-04-16 19:30 | 13.35 | 13.3
2018-04-16 20:00 | 12.75 | 12.71
2018-04-16 20:30 | 12.4 | 12.38
2018-04-16 21:00 | 11.65 | 11.64
2018-04-16 21:30 | 10.66 | 10.66
2018-04-16 22:00 | 9.54 | 9.54
2018-04-16 22:30 | 8.84 | 8.83
2018-04-16 23:00 | 8.18 | 8.17
2018-04-16 23:30 | 7 | 6.99
2018-04-17 | 6.07 | 6.05
2018-04-17 00:30 | 5.43 | 5.41
2018-04-17 01:00 | 5.26 | 5.24
2018-04-17 01:30 | 5.01 | 4.99
2018-04-17 02:00 | 4.77 | 4.75
2018-04-17 02:30 | 4.56 | 4.53
2018-04-17 03:00 | 4.56 | 4.52
2018-04-17 03:30 | 4.49 | 4.45
2018-04-17 04:00 | 4.46 | 4.42
2018-04-17 04:30 | 4.7 | 4.66
2018-04-17 05:00 | 4.89 | 4.86
2018-04-17 05:30 | 5.61 | 5.59
2018-04-17 06:00 | 6.18 | 6.16
2018-04-17 06:30 | 6.61 | 6.59
2018-04-17 07:00 | 6.94 | 6.92
2018-04-17 07:30 | 6.53 | 6.52
2018-04-17 08:00 | 6.06 | 6.05
2018-04-17 08:30 | 5.18 | 5.17
2018-04-17 09:00 | 4.79 | 4.78
2018-04-17 09:30 | 5.49 | 5.49
2018-04-17 10:00 | 5.26 | 5.26
2018-04-17 10:30 | 5.16 | 5.16
2018-04-17 11:00 | 5.26 | 5.25
2018-04-17 11:30 | 5.3 | 5.29
2018-04-17 12:00 | 5.58 | 5.57
2018-04-17 12:30 | 6.1 | 6.08
2018-04-17 13:00 | 6.49 | 6.46
2018-04-17 13:30 | 6.98 | 6.96
2018-04-17 14:00 | 7.44 | 7.42
2018-04-17 14:30 | 8.16 | 8.13
2018-04-17 15:00 | 8.71 | 8.68
2018-04-17 15:30 | 9.25 | 9.23
2018-04-17 16:00 | 10.77 | 10.74
2018-04-17 16:30 | 11.25 | 11.21
2018-04-17 17:00 | 11.89 | 11.86
2018-04-17 17:30 | 12.26 | 12.23
2018-04-17 18:00 | 13.31 | 13.26
2018-04-17 18:30 | 14.38 | 14.3
2018-04-17 19:00 | 14.01 | 13.94
2018-04-17 19:30 | 13.1 | 13.04
2018-04-17 20:00 | 12.95 | 12.9
2018-04-17 20:30 | 12.63 | 12.59
2018-04-17 21:00 | 11.65 | 11.63
2018-04-17 21:30 | 10.67 | 10.66
2018-04-17 22:00 | 9.39 | 9.38
2018-04-17 22:30 | 8.5 | 8.49
2018-04-17 23:00 | 8 | 7.99
2018-04-17 23:30 | 6.94 | 6.93
2018-04-18 | 6.03 | 6.02
2018-04-18 00:30 | 5.46 | 5.44
2018-04-18 01:00 | 5.3 | 5.29
2018-04-18 01:30 | 5.1 | 5.08
2018-04-18 02:00 | 4.81 | 4.79
2018-04-18 02:30 | 4.66 | 4.63
2018-04-18 03:00 | 4.52 | 4.49
2018-04-18 03:30 | 4.61 | 4.59
2018-04-18 04:00 | 4.59 | 4.56
2018-04-18 04:30 | 4.85 | 4.83
2018-04-18 05:00 | 5.05 | 5.02
2018-04-18 05:30 | 5.46 | 5.44
2018-04-18 06:00 | 5.76 | 5.74
2018-04-18 06:30 | 6.12 | 6.1
2018-04-18 07:00 | 6.58 | 6.55
2018-04-18 07:30 | 6.88 | 6.87
2018-04-18 08:00 | 6.87 | 6.86
2018-04-18 08:30 | 6.7 | 6.69
2018-04-18 09:00 | 5.78 | 5.77
2018-04-18 09:30 | 5.65 | 5.64
2018-04-18 10:00 | 5.72 | 5.71
2018-04-18 10:30 | 6.53 | 6.52
2018-04-18 11:00 | 6.13 | 6.12
2018-04-18 11:30 | 5.19 | 5.17
2018-04-18 12:00 | 5.48 | 5.47
2018-04-18 12:30 | 5.88 | 5.86
2018-04-18 13:00 | 6.66 | 6.65
2018-04-18 13:30 | 6.74 | 6.73
2018-04-18 14:00 | 6.52 | 6.51
2018-04-18 14:30 | 6.22 | 6.2
2018-04-18 15:00 | 5.47 | 5.45
2018-04-18 15:30 | 6.95 | 6.95
2018-04-18 16:00 | 7.83 | 7.83
2018-04-18 16:30 | 8.68 | 8.67
2018-04-18 17:00 | 9.74 | 9.74
2018-04-18 17:30 | 10.45 | 10.45
2018-04-18 18:00 | 11.34 | 11.33
2018-04-18 18:30 | 12.13 | 12.11
2018-04-18 19:00 | 12.25 | 12.24
2018-04-18 19:30 | 11.34 | 11.33
2018-04-18 20:00 | 11.41 | 11.4
2018-04-18 20:30 | 11.43 | 11.43
2018-04-18 21:00 | 10.85 | 10.85
2018-04-18 21:30 | 9.94 | 9.93
2018-04-18 22:00 | 8.98 | 8.98
2018-04-18 22:30 | 8.22 | 8.22
2018-04-18 23:00 | 7.67 | 7.66
2018-04-18 23:30 | 6.6 | 6.59
2018-04-19 | 5.79 | 5.77
2018-04-19 00:30 | 5.18 | 5.16
2018-04-19 01:00 | 4.94 | 4.91
2018-04-19 01:30 | 4.65 | 4.62
2018-04-19 02:00 | 4.48 | 4.44
2018-04-19 02:30 | 4.33 | 4.29
2018-04-19 03:00 | 4.17 | 4.12
2018-04-19 03:30 | 4.22 | 4.18
2018-04-19 04:00 | 4.26 | 4.22
2018-04-19 04:30 | 4.48 | 4.45
2018-04-19 05:00 | 4.77 | 4.73
2018-04-19 05:30 | 5.33 | 5.31
2018-04-19 06:00 | 5.66 | 5.65
2018-04-19 06:30 | 5.93 | 5.89
2018-04-19 07:00 | 6.24 | 6.2
2018-04-19 07:30 | 6.15 | 6.12
2018-04-19 08:00 | 5.51 | 5.48
2018-04-19 08:30 | 4.85 | 4.84
2018-04-19 09:00 | 4.61 | 4.6
2018-04-19 09:30 | 4.62 | 4.61
2018-04-19 10:00 | 4.42 | 4.41
2018-04-19 10:30 | 4.59 | 4.58
2018-04-19 11:00 | 5.68 | 5.67
2018-04-19 11:30 | 5.86 | 5.85
2018-04-19 12:00 | 5.71 | 5.7
2018-04-19 12:30 | 6.49 | 6.48
2018-04-19 13:00 | 6.93 | 6.93
2018-04-19 13:30 | 7.04 | 7.03
2018-04-19 14:00 | 6.87 | 6.87
2018-04-19 14:30 | 6.55 | 6.54
2018-04-19 15:00 | 7.28 | 7.27
2018-04-19 15:30 | 7.38 | 7.37
2018-04-19 16:00 | 7.65 | 7.64
2018-04-19 16:30 | 9.17 | 9.16
2018-04-19 17:00 | 9.55 | 9.54
2018-04-19 17:30 | 10.44 | 10.43
2018-04-19 18:00 | 11.53 | 11.5
2018-04-19 18:30 | 12.25 | 12.21
2018-04-19 19:00 | 12.38 | 12.34
2018-04-19 19:30 | 11.63 | 11.6
2018-04-19 20:00 | 11.31 | 11.29
2018-04-19 20:30 | 11.65 | 11.63
2018-04-19 21:00 | 11.02 | 11.02
2018-04-19 21:30 | 10.03 | 10.02
2018-04-19 22:00 | 9.02 | 9.01
2018-04-19 22:30 | 8.25 | 8.24
2018-04-19 23:00 | 7.93 | 7.92
2018-04-19 23:30 | 6.92 | 6.91
2018-04-20 | 6.02 | 6.01
2018-04-20 00:30 | 5.4 | 5.38
2018-04-20 01:00 | 5.2 | 5.18
2018-04-20 01:30 | 4.96 | 4.94
2018-04-20 02:00 | 4.67 | 4.64
2018-04-20 02:30 | 4.48 | 4.45
2018-04-20 03:00 | 4.48 | 4.45
2018-04-20 03:30 | 4.51 | 4.47
2018-04-20 04:00 | 4.45 | 4.41
2018-04-20 04:30 | 4.65 | 4.61
2018-04-20 05:00 | 4.89 | 4.86
2018-04-20 05:30 | 5.27 | 5.25
2018-04-20 06:00 | 5.99 | 5.98
2018-04-20 06:30 | 6.47 | 6.46
2018-04-20 07:00 | 6.88 | 6.86
2018-04-20 07:30 | 6.99 | 6.98
2018-04-20 08:00 | 6.5 | 6.49
2018-04-20 08:30 | 6.5 | 6.49
2018-04-20 09:00 | 4.92 | 4.91
2018-04-20 09:30 | 4.64 | 4.63
2018-04-20 10:00 | 4.56 | 4.54
2018-04-20 10:30 | 4.1 | 4.07
2018-04-20 11:00 | 5.44 | 5.41
2018-04-20 11:30 | 6.43 | 6.41
2018-04-20 12:00 | 5.42 | 5.39
2018-04-20 12:30 | 5.63 | 5.61
2018-04-20 13:00 | 6.64 | 6.62
2018-04-20 13:30 | 8.77 | 8.76
2018-04-20 14:00 | 8.79 | 8.78
2018-04-20 14:30 | 9.05 | 9.04
2018-04-20 15:00 | 9.17 | 9.16
2018-04-20 15:30 | 9.02 | 9.01
2018-04-20 16:00 | 9.39 | 9.38
2018-04-20 16:30 | 9.73 | 9.73
2018-04-20 17:00 | 9.46 | 9.45
2018-04-20 17:30 | 9.77 | 9.76
2018-04-20 18:00 | 9.99 | 9.97
2018-04-20 18:30 | 10.4 | 10.38
2018-04-20 19:00 | 10.6 | 10.58
2018-04-20 19:30 | 10.21 | 10.19
2018-04-20 20:00 | 10.1 | 10.08
2018-04-20 20:30 | 9.97 | 9.95
2018-04-20 21:00 | 9.39 | 9.38
2018-04-20 21:30 | 8.83 | 8.81
2018-04-20 22:00 | 8.3 | 8.29
2018-04-20 22:30 | 8.05 | 8.04
2018-04-20 23:00 | 7.96 | 7.95
2018-04-20 23:30 | 6.93 | 6.92
2018-04-21 | 6.15 | 6.13
2018-04-21 00:30 | 5.51 | 5.48
2018-04-21 01:00 | 5.29 | 5.27
2018-04-21 01:30 | 5.03 | 5.01
2018-04-21 02:00 | 4.64 | 4.6
2018-04-21 02:30 | 4.46 | 4.41
2018-04-21 03:00 | 4.33 | 4.29
2018-04-21 03:30 | 4.27 | 4.23
2018-04-21 04:00 | 4.27 | 4.22
2018-04-21 04:30 | 4.31 | 4.27
2018-04-21 05:00 | 4.38 | 4.34
2018-04-21 05:30 | 4.53 | 4.49
2018-04-21 06:00 | 4.71 | 4.68
2018-04-21 06:30 | 4.87 | 4.81
2018-04-21 07:00 | 5.16 | 5.09
2018-04-21 07:30 | 5.21 | 5.13
2018-04-21 08:00 | 5.33 | 5.27
2018-04-21 08:30 | 5.2 | 5.16
2018-04-21 09:00 | 4.77 | 4.75
2018-04-21 09:30 | 4.76 | 4.73
2018-04-21 10:00 | 4.84 | 4.81
2018-04-21 10:30 | 4.87 | 4.83
2018-04-21 11:00 | 5.64 | 5.6
2018-04-21 11:30 | 5.75 | 5.73
2018-04-21 12:00 | 6.22 | 6.19
2018-04-21 12:30 | 5.69 | 5.66
2018-04-21 13:00 | 6.22 | 6.19
2018-04-21 13:30 | 7.75 | 7.72
2018-04-21 14:00 | 8.53 | 8.5
2018-04-21 14:30 | 6.82 | 6.79
2018-04-21 15:00 | 6.05 | 6.02
2018-04-21 15:30 | 6.49 | 6.46
2018-04-21 16:00 | 8.04 | 8.02
2018-04-21 16:30 | 8.82 | 8.8
2018-04-21 17:00 | 9.17 | 9.16
2018-04-21 17:30 | 9.73 | 9.72
2018-04-21 18:00 | 10.31 | 10.3
2018-04-21 18:30 | 10.78 | 10.77
2018-04-21 19:00 | 10.53 | 10.52
2018-04-21 19:30 | 10.12 | 10.11
2018-04-21 20:00 | 10.08 | 10.07
2018-04-21 20:30 | 9.79 | 9.78
2018-04-21 21:00 | 9.16 | 9.15
2018-04-21 21:30 | 8.42 | 8.42
2018-04-21 22:00 | 7.97 | 7.96
2018-04-21 22:30 | 7.87 | 7.86
2018-04-21 23:00 | 7.78 | 7.77
2018-04-21 23:30 | 6.93 | 6.92
2018-04-22 | 6.18 | 6.16
2018-04-22 00:30 | 5.57 | 5.54
2018-04-22 01:00 | 5.18 | 5.15
2018-04-22 01:30 | 4.96 | 4.92
2018-04-22 02:00 | 4.59 | 4.54
2018-04-22 02:30 | 4.43 | 4.38
2018-04-22 03:00 | 4.31 | 4.26
2018-04-22 03:30 | 4.19 | 4.14
2018-04-22 04:00 | 4.19 | 4.14
2018-04-22 04:30 | 4.21 | 4.16
2018-04-22 05:00 | 4.27 | 4.22
2018-04-22 05:30 | 4.34 | 4.29
2018-04-22 06:00 | 4.43 | 4.38
2018-04-22 06:30 | 4.53 | 4.43
2018-04-22 07:00 | 4.62 | 4.52
2018-04-22 07:30 | 4.73 | 4.65
2018-04-22 08:00 | 4.78 | 4.71
2018-04-22 08:30 | 5.02 | 4.97
2018-04-22 09:00 | 5.15 | 5.12
2018-04-22 09:30 | 4.99 | 4.97
2018-04-22 10:00 | 5.65 | 5.63
2018-04-22 10:30 | 5.33 | 5.3
2018-04-22 11:00 | 5.68 | 5.65
2018-04-22 11:30 | 4.99 | 4.96
2018-04-22 12:00 | 7.14 | 7.12
2018-04-22 12:30 | 7.54 | 7.53
2018-04-22 13:00 | 5.43 | 5.41
2018-04-22 13:30 | 6.93 | 6.91
2018-04-22 14:00 | 5.86 | 5.83
2018-04-22 14:30 | 7.43 | 7.41
2018-04-22 15:00 | 6.65 | 6.63
2018-04-22 15:30 | 7.21 | 7.2
2018-04-22 16:00 | 7.53 | 7.52
2018-04-22 16:30 | 8.23 | 8.21
2018-04-22 17:00 | 9.59 | 9.57
2018-04-22 17:30 | 10.52 | 10.5
2018-04-22 18:00 | 11.38 | 11.36
2018-04-22 18:30 | 11.64 | 11.63
2018-04-22 19:00 | 11.44 | 11.43
2018-04-22 19:30 | 10.86 | 10.85
2018-04-22 20:00 | 10.56 | 10.55
2018-04-22 20:30 | 10.33 | 10.32
2018-04-22 21:00 | 9.64 | 9.63
2018-04-22 21:30 | 8.87 | 8.87
2018-04-22 22:00 | 8.21 | 8.2
2018-04-22 22:30 | 7.68 | 7.67
2018-04-22 23:00 | 7.49 | 7.48
2018-04-22 23:30 | 6.53 | 6.51
2018-04-23 | 5.7 | 5.67
2018-04-23 00:30 | 5.13 | 5.09
2018-04-23 01:00 | 4.95 | 4.91
2018-04-23 01:30 | 4.59 | 4.55
2018-04-23 02:00 | 4.32 | 4.26
2018-04-23 02:30 | 4.18 | 4.13
2018-04-23 03:00 | 4.6 | 4.54
2018-04-23 03:30 | 4.68 | 4.62
2018-04-23 04:00 | 5.24 | 5.18
2018-04-23 04:30 | 5.52 | 5.46
2018-04-23 05:00 | 5.45 | 5.41
2018-04-23 05:30 | 5.12 | 5.09
2018-04-23 06:00 | 5.36 | 5.33
2018-04-23 06:30 | 5.84 | 5.79
2018-04-23 07:00 | 6.54 | 6.5
2018-04-23 07:30 | 6.94 | 6.92
2018-04-23 08:00 | 5.99 | 5.97
2018-04-23 08:30 | 5.38 | 5.37
2018-04-23 09:00 | 4.68 | 4.68
2018-04-23 09:30 | 4.48 | 4.47
2018-04-23 10:00 | 3.96 | 3.95
2018-04-23 10:30 | 3.95 | 3.93
2018-04-23 11:00 | 4.07 | 4.06
2018-04-23 11:30 | 4.49 | 4.48
2018-04-23 12:00 | 5.23 | 5.22
2018-04-23 12:30 | 4.96 | 4.95
2018-04-23 13:00 | 5.12 | 5.11
2018-04-23 13:30 | 4.85 | 4.84
2018-04-23 14:00 | 4.97 | 4.96
2018-04-23 14:30 | 5.33 | 5.32
2018-04-23 15:00 | 5.61 | 5.6
2018-04-23 15:30 | 6.74 | 6.73
2018-04-23 16:00 | 7.66 | 7.65
2018-04-23 16:30 | 9.08 | 9.07
2018-04-23 17:00 | 9.75 | 9.75
2018-04-23 17:30 | 10.56 | 10.56
2018-04-23 18:00 | 11.76 | 11.74
2018-04-23 18:30 | 12.4 | 12.37
2018-04-23 19:00 | 12.43 | 12.41
2018-04-23 19:30 | 11.43 | 11.42
2018-04-23 20:00 | 11.24 | 11.23
2018-04-23 20:30 | 11.28 | 11.27
2018-04-23 21:00 | 10.5 | 10.5
2018-04-23 21:30 | 9.72 | 9.72
2018-04-23 22:00 | 8.78 | 8.77
2018-04-23 22:30 | 7.87 | 7.87
2018-04-23 23:00 | 7.46 | 7.45
2018-04-23 23:30 | 6.49 | 6.47
2018-04-24 | 5.66 | 5.63
2018-04-24 00:30 | 5.09 | 5.06
2018-04-24 01:00 | 4.82 | 4.78
2018-04-24 01:30 | 4.64 | 4.6
2018-04-24 02:00 | 4.37 | 4.32
2018-04-24 02:30 | 4.25 | 4.2
2018-04-24 03:00 | 4.1 | 4.05
2018-04-24 03:30 | 4.14 | 4.09
2018-04-24 04:00 | 4.16 | 4.1
2018-04-24 04:30 | 4.4 | 4.35
2018-04-24 05:00 | 4.69 | 4.65
2018-04-24 05:30 | 5.33 | 5.31
2018-04-24 06:00 | 6.13 | 6.12
2018-04-24 06:30 | 6.56 | 6.54
2018-04-24 07:00 | 6.96 | 6.94
2018-04-24 07:30 | 6.95 | 6.94
2018-04-24 08:00 | 6.08 | 6.06
2018-04-24 08:30 | 5.22 | 5.2
2018-04-24 09:00 | 4.51 | 4.5
2018-04-24 09:30 | 4.07 | 4.07
2018-04-24 10:00 | 3.89 | 3.89
2018-04-24 10:30 | 3.6 | 3.6
2018-04-24 11:00 | 3.15 | 3.14
2018-04-24 11:30 | 3.08 | 3.06
2018-04-24 12:00 | 3.54 | 3.53
2018-04-24 12:30 | 4.11 | 4.1
2018-04-24 13:00 | 4.81 | 4.8
2018-04-24 13:30 | 6.33 | 6.33
2018-04-24 14:00 | 6.29 | 6.29
2018-04-24 14:30 | 7.11 | 7.11
2018-04-24 15:00 | 7.35 | 7.35
2018-04-24 15:30 | 8.3 | 8.3
2018-04-24 16:00 | 9 | 9
2018-04-24 16:30 | 8.56 | 8.56
2018-04-24 17:00 | 9.33 | 9.33
2018-04-24 17:30 | 10.2 | 10.2
2018-04-24 18:00 | 11.08 | 11.07
2018-04-24 18:30 | 11.45 | 11.42
2018-04-24 19:00 | 11.58 | 11.56
2018-04-24 19:30 | 10.88 | 10.86
2018-04-24 20:00 | 10.78 | 10.77
2018-04-24 20:30 | 10.88 | 10.87
2018-04-24 21:00 | 10.31 | 10.31
2018-04-24 21:30 | 9.66 | 9.65
2018-04-24 22:00 | 8.57 | 8.56
2018-04-24 22:30 | 8 | 7.98
2018-04-24 23:00 | 7.68 | 7.67
2018-04-24 23:30 | 6.74 | 6.72
2018-04-25 | 6.03 | 6.01
2018-04-25 00:30 | 5.37 | 5.35
2018-04-25 01:00 | 5.1 | 5.08
2018-04-25 01:30 | 4.96 | 4.93
2018-04-25 02:00 | 4.62 | 4.59
2018-04-25 02:30 | 4.41 | 4.37
2018-04-25 03:00 | 4.24 | 4.2
2018-04-25 03:30 | 4.29 | 4.25
2018-04-25 04:00 | 4.2 | 4.16
2018-04-25 04:30 | 4.3 | 4.26
2018-04-25 05:00 | 4.32 | 4.28
2018-04-25 05:30 | 4.38 | 4.34
2018-04-25 06:00 | 4.56 | 4.52
2018-04-25 06:30 | 4.66 | 4.58
2018-04-25 07:00 | 4.66 | 4.56
2018-04-25 07:30 | 4.6 | 4.5
2018-04-25 08:00 | 4.39 | 4.3
2018-04-25 08:30 | 4.3 | 4.22
2018-04-25 09:00 | 4.24 | 4.19
2018-04-25 09:30 | 4.51 | 4.48
2018-04-25 10:00 | 4.22 | 4.19
2018-04-25 10:30 | 4.1 | 4.08
2018-04-25 11:00 | 4.46 | 4.45
2018-04-25 11:30 | 4.82 | 4.8
2018-04-25 12:00 | 5.7 | 5.68
2018-04-25 12:30 | 5.43 | 5.42
2018-04-25 13:00 | 5.37 | 5.35
2018-04-25 13:30 | 5.06 | 5.04
2018-04-25 14:00 | 5.87 | 5.86
2018-04-25 14:30 | 5.29 | 5.27
2018-04-25 15:00 | 6.1 | 6.09
2018-04-25 15:30 | 6.86 | 6.85
2018-04-25 16:00 | 7.46 | 7.45
2018-04-25 16:30 | 8.37 | 8.36
2018-04-25 17:00 | 9.21 | 9.2
2018-04-25 17:30 | 10.05 | 10.04
2018-04-25 18:00 | 11.1 | 11.09
2018-04-25 18:30 | 11.37 | 11.36
2018-04-25 19:00 | 11.12 | 11.11
2018-04-25 19:30 | 10.64 | 10.64
2018-04-25 20:00 | 10.48 | 10.48
2018-04-25 20:30 | 10.14 | 10.14
2018-04-25 21:00 | 9.54 | 9.53
2018-04-25 21:30 | 8.81 | 8.8
2018-04-25 22:00 | 8.06 | 8.05
2018-04-25 22:30 | 7.64 | 7.63
2018-04-25 23:00 | 7.41 | 7.4
2018-04-25 23:30 | 6.64 | 6.63
2018-04-26 | 5.82 | 5.8
2018-04-26 00:30 | 5.22 | 5.2
2018-04-26 01:00 | 5.06 | 5.04
2018-04-26 01:30 | 4.85 | 4.82
2018-04-26 02:00 | 4.55 | 4.52
2018-04-26 02:30 | 4.48 | 4.45
2018-04-26 03:00 | 4.23 | 4.19
2018-04-26 03:30 | 4.34 | 4.31
2018-04-26 04:00 | 4.4 | 4.37
2018-04-26 04:30 | 4.49 | 4.45
2018-04-26 05:00 | 4.78 | 4.75
2018-04-26 05:30 | 5.21 | 5.19
2018-04-26 06:00 | 5.45 | 5.43
2018-04-26 06:30 | 5.85 | 5.81
2018-04-26 07:00 | 6.19 | 6.16
2018-04-26 07:30 | 6.23 | 6.2
2018-04-26 08:00 | 5.75 | 5.72
2018-04-26 08:30 | 4.89 | 4.87
2018-04-26 09:00 | 4.36 | 4.34
2018-04-26 09:30 | 3.96 | 3.94
2018-04-26 10:00 | 3.67 | 3.64
2018-04-26 10:30 | 3.46 | 3.43
2018-04-26 11:00 | 3.48 | 3.45
2018-04-26 11:30 | 3.5 | 3.46
2018-04-26 12:00 | 3.55 | 3.51
2018-04-26 12:30 | 3.72 | 3.68
2018-04-26 13:00 | 4.33 | 4.29
2018-04-26 13:30 | 5.17 | 5.14
2018-04-26 14:00 | 5.32 | 5.28
2018-04-26 14:30 | 5.77 | 5.74
2018-04-26 15:00 | 6.45 | 6.42
2018-04-26 15:30 | 7.06 | 7.04
2018-04-26 16:00 | 8.09 | 8.06
2018-04-26 16:30 | 9.18 | 9.16
2018-04-26 17:00 | 9.65 | 9.63
2018-04-26 17:30 | 10.33 | 10.31
2018-04-26 18:00 | 11.39 | 11.36
2018-04-26 18:30 | 11.87 | 11.83
2018-04-26 19:00 | 12.15 | 12.12
2018-04-26 19:30 | 11.7 | 11.67
2018-04-26 20:00 | 11.51 | 11.48
2018-04-26 20:30 | 11.25 | 11.24
2018-04-26 21:00 | 10.59 | 10.57
2018-04-26 21:30 | 9.69 | 9.68
2018-04-26 22:00 | 8.84 | 8.83
2018-04-26 22:30 | 8.22 | 8.21
2018-04-26 23:00 | 8.01 | 8
2018-04-26 23:30 | 6.98 | 6.97
2018-04-27 | 6.14 | 6.12
2018-04-27 00:30 | 5.5 | 5.48
2018-04-27 01:00 | 5.12 | 5.1
2018-04-27 01:30 | 4.82 | 4.79
2018-04-27 02:00 | 4.59 | 4.55
2018-04-27 02:30 | 4.42 | 4.38
2018-04-27 03:00 | 4.43 | 4.39
2018-04-27 03:30 | 4.39 | 4.36
2018-04-27 04:00 | 4.4 | 4.36
2018-04-27 04:30 | 4.55 | 4.51
2018-04-27 05:00 | 4.84 | 4.8
2018-04-27 05:30 | 5.23 | 5.21
2018-04-27 06:00 | 5.47 | 5.45
2018-04-27 06:30 | 5.81 | 5.77
2018-04-27 07:00 | 6.18 | 6.14
2018-04-27 07:30 | 6.2 | 6.18
2018-04-27 08:00 | 5.75 | 5.73
2018-04-27 08:30 | 4.97 | 4.96
2018-04-27 09:00 | 4.27 | 4.26
2018-04-27 09:30 | 3.93 | 3.91
2018-04-27 10:00 | 3.52 | 3.49
2018-04-27 10:30 | 3.31 | 3.28
2018-04-27 11:00 | 3.24 | 3.21
2018-04-27 11:30 | 3.12 | 3.08
2018-04-27 12:00 | 3.26 | 3.23
2018-04-27 12:30 | 3.58 | 3.55
2018-04-27 13:00 | 3.59 | 3.56
2018-04-27 13:30 | 3.98 | 3.94
2018-04-27 14:00 | 4.26 | 4.23
2018-04-27 14:30 | 4.62 | 4.59
2018-04-27 15:00 | 5.09 | 5.07
2018-04-27 15:30 | 6.17 | 6.14
2018-04-27 16:00 | 7.02 | 7
2018-04-27 16:30 | 7.7 | 7.68
2018-04-27 17:00 | 8.59 | 8.57
2018-04-27 17:30 | 9.21 | 9.19
2018-04-27 18:00 | 10.12 | 10.11
2018-04-27 18:30 | 10.47 | 10.46
2018-04-27 19:00 | 10.62 | 10.61
2018-04-27 19:30 | 10.2 | 10.19
2018-04-27 20:00 | 10.18 | 10.17
2018-04-27 20:30 | 10 | 9.99
2018-04-27 21:00 | 9.39 | 9.38
2018-04-27 21:30 | 8.9 | 8.89
2018-04-27 22:00 | 8.15 | 8.14
2018-04-27 22:30 | 7.94 | 7.93
2018-04-27 23:00 | 7.82 | 7.81
2018-04-27 23:30 | 6.97 | 6.96
2018-04-28 | 6.11 | 6.1
2018-04-28 00:30 | 5.54 | 5.52
2018-04-28 01:00 | 5.28 | 5.25
2018-04-28 01:30 | 4.87 | 4.83
2018-04-28 02:00 | 4.61 | 4.57
2018-04-28 02:30 | 4.39 | 4.35
2018-04-28 03:00 | 4.29 | 4.25
2018-04-28 03:30 | 4.29 | 4.25
2018-04-28 04:00 | 4.17 | 4.12
2018-04-28 04:30 | 4.19 | 4.14
2018-04-28 05:00 | 4.36 | 4.31
2018-04-28 05:30 | 4.45 | 4.41
2018-04-28 06:00 | 4.59 | 4.54
2018-04-28 06:30 | 4.64 | 4.55
2018-04-28 07:00 | 4.98 | 4.89
2018-04-28 07:30 | 5.41 | 5.34
2018-04-28 08:00 | 5.13 | 5.06
2018-04-28 08:30 | 5.63 | 5.59
2018-04-28 09:00 | 5.72 | 5.7
2018-04-28 09:30 | 5.9 | 5.88
2018-04-28 10:00 | 4.47 | 4.44
2018-04-28 10:30 | 4.34 | 4.31
2018-04-28 11:00 | 5.19 | 5.16
2018-04-28 11:30 | 4.12 | 4.08
2018-04-28 12:00 | 3.65 | 3.6
2018-04-28 12:30 | 4.27 | 4.23
2018-04-28 13:00 | 4.76 | 4.73
2018-04-28 13:30 | 4.4 | 4.37
2018-04-28 14:00 | 5.23 | 5.2
2018-04-28 14:30 | 6.19 | 6.16
2018-04-28 15:00 | 5.27 | 5.24
2018-04-28 15:30 | 6.22 | 6.19
2018-04-28 16:00 | 7.33 | 7.31
2018-04-28 16:30 | 7.77 | 7.75
2018-04-28 17:00 | 8.37 | 8.36
2018-04-28 17:30 | 9.01 | 9
2018-04-28 18:00 | 9.89 | 9.88
2018-04-28 18:30 | 10.08 | 10.07
2018-04-28 19:00 | 9.9 | 9.89
2018-04-28 19:30 | 9.56 | 9.55
2018-04-28 20:00 | 9.43 | 9.42
2018-04-28 20:30 | 9.28 | 9.27
2018-04-28 21:00 | 8.71 | 8.7
2018-04-28 21:30 | 8.05 | 8.04
2018-04-28 22:00 | 7.65 | 7.64
2018-04-28 22:30 | 7.49 | 7.48
2018-04-28 23:00 | 7.46 | 7.45
2018-04-28 23:30 | 6.82 | 6.8
2018-04-29 | 5.99 | 5.96
2018-04-29 00:30 | 5.34 | 5.31
2018-04-29 01:00 | 5.09 | 5.05
2018-04-29 01:30 | 4.74 | 4.7
2018-04-29 02:00 | 4.48 | 4.44
2018-04-29 02:30 | 4.32 | 4.27
2018-04-29 03:00 | 4.24 | 4.18
2018-04-29 03:30 | 4.1 | 4.04
2018-04-29 04:00 | 4.07 | 4
2018-04-29 04:30 | 4.13 | 4.07
2018-04-29 05:00 | 4.12 | 4.06
2018-04-29 05:30 | 4.24 | 4.19
2018-04-29 06:00 | 4.27 | 4.22
2018-04-29 06:30 | 4.41 | 4.3
2018-04-29 07:00 | 4.46 | 4.33
2018-04-29 07:30 | 4.69 | 4.59
2018-04-29 08:00 | 4.81 | 4.72
2018-04-29 08:30 | 4.84 | 4.78
2018-04-29 09:00 | 4.84 | 4.8
2018-04-29 09:30 | 4.59 | 4.56
2018-04-29 10:00 | 4.46 | 4.43
2018-04-29 10:30 | 4.17 | 4.14
2018-04-29 11:00 | 4.06 | 4.02
2018-04-29 11:30 | 5.24 | 5.22
2018-04-29 12:00 | 4.64 | 4.61
2018-04-29 12:30 | 4.4 | 4.37
2018-04-29 13:00 | 4.28 | 4.25
2018-04-29 13:30 | 4.5 | 4.46
2018-04-29 14:00 | 5.26 | 5.23
2018-04-29 14:30 | 5.72 | 5.69
2018-04-29 15:00 | 5.71 | 5.69
2018-04-29 15:30 | 6.37 | 6.35
2018-04-29 16:00 | 7.24 | 7.22
2018-04-29 16:30 | 8.12 | 8.1
2018-04-29 17:00 | 9.26 | 9.25
2018-04-29 17:30 | 10.2 | 10.19
2018-04-29 18:00 | 11.28 | 11.27
2018-04-29 18:30 | 11.2 | 11.19
2018-04-29 19:00 | 10.91 | 10.9
2018-04-29 19:30 | 10.46 | 10.46
2018-04-29 20:00 | 10.18 | 10.18
2018-04-29 20:30 | 10.03 | 10.02
2018-04-29 21:00 | 9.24 | 9.23
2018-04-29 21:30 | 8.59 | 8.58
2018-04-29 22:00 | 7.94 | 7.93
2018-04-29 22:30 | 7.45 | 7.44
2018-04-29 23:00 | 7.27 | 7.25
2018-04-29 23:30 | 6.42 | 6.4
2018-04-30 | 5.6 | 5.56
2018-04-30 00:30 | 5 | 4.95
2018-04-30 01:00 | 4.72 | 4.66
2018-04-30 01:30 | 4.46 | 4.4
2018-04-30 02:00 | 4.18 | 4.11
2018-04-30 02:30 | 4.17 | 4.11
2018-04-30 03:00 | 4.02 | 3.95
2018-04-30 03:30 | 4.01 | 3.94
2018-04-30 04:00 | 4 | 3.92
2018-04-30 04:30 | 4.22 | 4.15
2018-04-30 05:00 | 4.64 | 4.59
2018-04-30 05:30 | 5.06 | 5.02
2018-04-30 06:00 | 5.55 | 5.52
2018-04-30 06:30 | 5.94 | 5.89
2018-04-30 07:00 | 6.5 | 6.45
2018-04-30 07:30 | 6.9 | 6.87
2018-04-30 08:00 | 6.33 | 6.31
2018-04-30 08:30 | 5.47 | 5.45
2018-04-30 09:00 | 4.62 | 4.61
2018-04-30 09:30 | 4.06 | 4.05
2018-04-30 10:00 | 3.87 | 3.86
2018-04-30 10:30 | 3.6 | 3.59
2018-04-30 11:00 | 3.48 | 3.47
2018-04-30 11:30 | 3.46 | 3.44
2018-04-30 12:00 | 3.27 | 3.26
2018-04-30 12:30 | 3.46 | 3.45
2018-04-30 13:00 | 3.6 | 3.59
2018-04-30 13:30 | 3.82 | 3.81
2018-04-30 14:00 | 4.14 | 4.13
2018-04-30 14:30 | 4.54 | 4.53
2018-04-30 15:00 | 4.98 | 4.97
2018-04-30 15:30 | 5.56 | 5.55
2018-04-30 16:00 | 6.88 | 6.88
2018-04-30 16:30 | 7.9 | 7.89
2018-04-30 17:00 | 9.14 | 9.13
2018-04-30 17:30 | 10.32 | 10.31
2018-04-30 18:00 | 11.58 | 11.57
2018-04-30 18:30 | 12.06 | 12.05
2018-04-30 19:00 | 11.95 | 11.94
2018-04-30 19:30 | 11.46 | 11.46
2018-04-30 20:00 | 11.01 | 11
2018-04-30 20:30 | 10.48 | 10.47
2018-04-30 21:00 | 9.74 | 9.73
2018-04-30 21:30 | 8.9 | 8.9
2018-04-30 22:00 | 8.17 | 8.16
2018-04-30 22:30 | 7.55 | 7.54
2018-04-30 23:00 | 7.29 | 7.28
2018-04-30 23:30 | 6.4 | 6.38
2018-05-01 | 5.6 | 5.57
2018-05-01 00:30 | 4.92 | 4.88
2018-05-01 01:00 | 4.71 | 4.67
2018-05-01 01:30 | 4.49 | 4.44
2018-05-01 02:00 | 4.24 | 4.19
2018-05-01 02:30 | 4.19 | 4.14
2018-05-01 03:00 | 4 | 3.93
2018-05-01 03:30 | 4.01 | 3.95
2018-05-01 04:00 | 4 | 3.94
2018-05-01 04:30 | 4.24 | 4.17
2018-05-01 05:00 | 4.63 | 4.58
2018-05-01 05:30 | 5.1 | 5.07
2018-05-01 06:00 | 5.62 | 5.59
2018-05-01 06:30 | 6.05 | 6
2018-05-01 07:00 | 6.55 | 6.5
2018-05-01 07:30 | 6.58 | 6.55
2018-05-01 08:00 | 5.93 | 5.9
2018-05-01 08:30 | 4.85 | 4.81
2018-05-01 09:00 | 4.26 | 4.22
2018-05-01 09:30 | 3.79 | 3.76
2018-05-01 10:00 | 4.06 | 4.03
2018-05-01 10:30 | 3.05 | 3.03
2018-05-01 11:00 | 3.66 | 3.64
2018-05-01 11:30 | 4.47 | 4.46
2018-05-01 12:00 | 5.82 | 5.81
2018-05-01 12:30 | 5.48 | 5.46
2018-05-01 13:00 | 3.6 | 3.58
2018-05-01 13:30 | 3.45 | 3.44
2018-05-01 14:00 | 4.01 | 4
2018-05-01 14:30 | 5.89 | 5.88
2018-05-01 15:00 | 6.33 | 6.33
2018-05-01 15:30 | 5.87 | 5.87
2018-05-01 16:00 | 7.25 | 7.25
2018-05-01 16:30 | 8.07 | 8.07
2018-05-01 17:00 | 9.36 | 9.35
2018-05-01 17:30 | 10.48 | 10.48
2018-05-01 18:00 | 11.61 | 11.6
2018-05-01 18:30 | 12.03 | 12.01
2018-05-01 19:00 | 12.05 | 12.03
2018-05-01 19:30 | 11.7 | 11.68
2018-05-01 20:00 | 11.42 | 11.41
2018-05-01 20:30 | 11.18 | 11.17
2018-05-01 21:00 | 10.44 | 10.44
2018-05-01 21:30 | 9.57 | 9.57
2018-05-01 22:00 | 8.85 | 8.85
2018-05-01 22:30 | 7.87 | 7.86
2018-05-01 23:00 | 7.47 | 7.46
2018-05-01 23:30 | 6.52 | 6.51
2018-05-02 | 5.62 | 5.6
2018-05-02 00:30 | 4.99 | 4.96
2018-05-02 01:00 | 4.67 | 4.63
2018-05-02 01:30 | 4.47 | 4.43
2018-05-02 02:00 | 4.3 | 4.25
2018-05-02 02:30 | 4.17 | 4.13
2018-05-02 03:00 | 4.13 | 4.08
2018-05-02 03:30 | 4.19 | 4.15
2018-05-02 04:00 | 4.13 | 4.09
2018-05-02 04:30 | 4.37 | 4.33
2018-05-02 05:00 | 4.63 | 4.59
2018-05-02 05:30 | 5.13 | 5.1
2018-05-02 06:00 | 5.5 | 5.48
2018-05-02 06:30 | 5.97 | 5.93
2018-05-02 07:00 | 6.47 | 6.43
2018-05-02 07:30 | 6.91 | 6.88
2018-05-02 08:00 | 7.2 | 7.18
2018-05-02 08:30 | 6.51 | 6.49
2018-05-02 09:00 | 5.54 | 5.53
2018-05-02 09:30 | 4.12 | 4.11
2018-05-02 10:00 | 5.29 | 5.28
2018-05-02 10:30 | 5.01 | 5.01
2018-05-02 11:00 | 3.73 | 3.72
2018-05-02 11:30 | 5.13 | 5.12
2018-05-02 12:00 | 4.87 | 4.86
2018-05-02 12:30 | 4.74 | 4.73
2018-05-02 13:00 | 5.68 | 5.67
2018-05-02 13:30 | 4.32 | 4.31
2018-05-02 14:00 | 5.47 | 5.46
2018-05-02 14:30 | 6.06 | 6.05
2018-05-02 15:00 | 6.73 | 6.72
2018-05-02 15:30 | 6.74 | 6.74
2018-05-02 16:00 | 8.16 | 8.16
2018-05-02 16:30 | 8.95 | 8.95
2018-05-02 17:00 | 9.22 | 9.22
2018-05-02 17:30 | 10.14 | 10.14
2018-05-02 18:00 | 11.53 | 11.52
2018-05-02 18:30 | 11.98 | 11.96
2018-05-02 19:00 | 11.97 | 11.95
2018-05-02 19:30 | 11.52 | 11.51
2018-05-02 20:00 | 11.4 | 11.39
2018-05-02 20:30 | 11.34 | 11.33
2018-05-02 21:00 | 10.67 | 10.66
2018-05-02 21:30 | 9.86 | 9.85
2018-05-02 22:00 | 9.09 | 9.08
2018-05-02 22:30 | 8.1 | 8.09
2018-05-02 23:00 | 7.53 | 7.52
2018-05-02 23:30 | 6.54 | 6.53
2018-05-03 | 5.72 | 5.69
2018-05-03 00:30 | 5.12 | 5.09
2018-05-03 01:00 | 4.8 | 4.76
2018-05-03 01:30 | 4.54 | 4.49
2018-05-03 02:00 | 4.33 | 4.28
2018-05-03 02:30 | 4.22 | 4.18
2018-05-03 03:00 | 4.18 | 4.14
2018-05-03 03:30 | 4.13 | 4.08
2018-05-03 04:00 | 4.17 | 4.13
2018-05-03 04:30 | 4.4 | 4.36
2018-05-03 05:00 | 4.73 | 4.69
2018-05-03 05:30 | 5.21 | 5.18
2018-05-03 06:00 | 5.9 | 5.89
2018-05-03 06:30 | 6.6 | 6.58
2018-05-03 07:00 | 7.15 | 7.12
2018-05-03 07:30 | 7.11 | 7.09
2018-05-03 08:00 | 6.4 | 6.38
2018-05-03 08:30 | 5.63 | 5.62
2018-05-03 09:00 | 4.68 | 4.67
2018-05-03 09:30 | 4.29 | 4.28
2018-05-03 10:00 | 4.16 | 4.15
2018-05-03 10:30 | 3.66 | 3.66
2018-05-03 11:00 | 3.48 | 3.47
2018-05-03 11:30 | 3.69 | 3.68
2018-05-03 12:00 | 3.64 | 3.63
2018-05-03 12:30 | 3.85 | 3.84
2018-05-03 13:00 | 3.89 | 3.87
2018-05-03 13:30 | 4.95 | 4.93
2018-05-03 14:00 | 5.2 | 5.19
2018-05-03 14:30 | 4.88 | 4.86
2018-05-03 15:00 | 5.55 | 5.53
2018-05-03 15:30 | 6.01 | 5.99
2018-05-03 16:00 | 6.47 | 6.46
2018-05-03 16:30 | 7.85 | 7.84
2018-05-03 17:00 | 8.78 | 8.77
2018-05-03 17:30 | 9.84 | 9.83
2018-05-03 18:00 | 10.84 | 10.82
2018-05-03 18:30 | 10.95 | 10.93
2018-05-03 19:00 | 11.04 | 11.03
2018-05-03 19:30 | 10.73 | 10.72
2018-05-03 20:00 | 10.88 | 10.87
2018-05-03 20:30 | 10.65 | 10.64
2018-05-03 21:00 | 9.95 | 9.94
2018-05-03 21:30 | 9.19 | 9.18
2018-05-03 22:00 | 8.47 | 8.46
2018-05-03 22:30 | 8 | 7.99
2018-05-03 23:00 | 7.62 | 7.61
2018-05-03 23:30 | 6.68 | 6.66
2018-05-04 | 5.74 | 5.71
2018-05-04 00:30 | 5.13 | 5.1
2018-05-04 01:00 | 4.82 | 4.78
2018-05-04 01:30 | 4.61 | 4.58
2018-05-04 02:00 | 4.33 | 4.29
2018-05-04 02:30 | 4.19 | 4.14
2018-05-04 03:00 | 4.1 | 4.05
2018-05-04 03:30 | 4.22 | 4.18
2018-05-04 04:00 | 4.22 | 4.18
2018-05-04 04:30 | 4.33 | 4.28
2018-05-04 05:00 | 4.58 | 4.53
2018-05-04 05:30 | 4.98 | 4.95
2018-05-04 06:00 | 5.43 | 5.41
2018-05-04 06:30 | 5.8 | 5.76
2018-05-04 07:00 | 6.31 | 6.27
2018-05-04 07:30 | 6.43 | 6.4
2018-05-04 08:00 | 5.75 | 5.72
2018-05-04 08:30 | 4.87 | 4.84
2018-05-04 09:00 | 4.14 | 4.12
2018-05-04 09:30 | 3.76 | 3.74
2018-05-04 10:00 | 3.53 | 3.51
2018-05-04 10:30 | 3.43 | 3.41
2018-05-04 11:00 | 3.54 | 3.52
2018-05-04 11:30 | 3.46 | 3.43
2018-05-04 12:00 | 3.51 | 3.48
2018-05-04 12:30 | 4.07 | 4.04
2018-05-04 13:00 | 3.58 | 3.55
2018-05-04 13:30 | 3.86 | 3.84
2018-05-04 14:00 | 4.47 | 4.45
2018-05-04 14:30 | 5.29 | 5.26
2018-05-04 15:00 | 6.24 | 6.21
2018-05-04 15:30 | 6.24 | 6.21
2018-05-04 16:00 | 7.52 | 7.5
2018-05-04 16:30 | 8.35 | 8.33
2018-05-04 17:00 | 8.96 | 8.95
2018-05-04 17:30 | 9.74 | 9.73
2018-05-04 18:00 | 10.73 | 10.71
2018-05-04 18:30 | 10.83 | 10.8
2018-05-04 19:00 | 10.78 | 10.76
2018-05-04 19:30 | 10.43 | 10.42
2018-05-04 20:00 | 10.53 | 10.52
2018-05-04 20:30 | 10.45 | 10.44
2018-05-04 21:00 | 9.97 | 9.96
2018-05-04 21:30 | 9.26 | 9.26
2018-05-04 22:00 | 8.41 | 8.41
2018-05-04 22:30 | 8.07 | 8.06
2018-05-04 23:00 | 7.93 | 7.92
2018-05-04 23:30 | 7.06 | 7.05
2018-05-05 | 6.2 | 6.18
2018-05-05 00:30 | 5.57 | 5.55
2018-05-05 01:00 | 5.3 | 5.28
2018-05-05 01:30 | 4.91 | 4.88
2018-05-05 02:00 | 4.55 | 4.51
2018-05-05 02:30 | 4.41 | 4.37
2018-05-05 03:00 | 4.34 | 4.3
2018-05-05 03:30 | 4.35 | 4.31
2018-05-05 04:00 | 4.29 | 4.25
2018-05-05 04:30 | 4.33 | 4.29
2018-05-05 05:00 | 4.42 | 4.38
2018-05-05 05:30 | 4.49 | 4.45
2018-05-05 06:00 | 4.61 | 4.57
2018-05-05 06:30 | 4.72 | 4.65
2018-05-05 07:00 | 5.08 | 5
2018-05-05 07:30 | 5.23 | 5.17
2018-05-05 08:00 | 5.18 | 5.12
2018-05-05 08:30 | 5.19 | 5.15
2018-05-05 09:00 | 5.22 | 5.2
2018-05-05 09:30 | 4.87 | 4.84
2018-05-05 10:00 | 4.77 | 4.73
2018-05-05 10:30 | 4.84 | 4.8
2018-05-05 11:00 | 4.92 | 4.88
2018-05-05 11:30 | 4.86 | 4.82
2018-05-05 12:00 | 4.88 | 4.83
2018-05-05 12:30 | 6.37 | 6.33
2018-05-05 13:00 | 5.82 | 5.77
2018-05-05 13:30 | 5.81 | 5.76
2018-05-05 14:00 | 6.48 | 6.44
2018-05-05 14:30 | 6.82 | 6.79
2018-05-05 15:00 | 7.19 | 7.17
2018-05-05 15:30 | 7.72 | 7.69
2018-05-05 16:00 | 7.79 | 7.76
2018-05-05 16:30 | 8.42 | 8.4
2018-05-05 17:00 | 8.96 | 8.94
2018-05-05 17:30 | 9.49 | 9.48
2018-05-05 18:00 | 10.24 | 10.23
2018-05-05 18:30 | 10.16 | 10.14
2018-05-05 19:00 | 10.02 | 10.01
2018-05-05 19:30 | 9.66 | 9.65
2018-05-05 20:00 | 9.52 | 9.51
2018-05-05 20:30 | 9.32 | 9.31
2018-05-05 21:00 | 8.85 | 8.84
2018-05-05 21:30 | 8.19 | 8.18
2018-05-05 22:00 | 7.7 | 7.69
2018-05-05 22:30 | 7.55 | 7.54
2018-05-05 23:00 | 7.48 | 7.47
2018-05-05 23:30 | 6.67 | 6.65
2018-05-06 | 6.01 | 5.99
2018-05-06 00:30 | 5.36 | 5.33
2018-05-06 01:00 | 5.11 | 5.08
2018-05-06 01:30 | 4.86 | 4.82
2018-05-06 02:00 | 4.53 | 4.48
2018-05-06 02:30 | 4.43 | 4.38
2018-05-06 03:00 | 4.2 | 4.14
2018-05-06 03:30 | 4.14 | 4.09
2018-05-06 04:00 | 4.05 | 3.99
2018-05-06 04:30 | 4.06 | 4
2018-05-06 05:00 | 4.13 | 4.07
2018-05-06 05:30 | 4.24 | 4.18
2018-05-06 06:00 | 4.38 | 4.33
2018-05-06 06:30 | 4.4 | 4.3
2018-05-06 07:00 | 4.64 | 4.53
2018-05-06 07:30 | 4.74 | 4.65
2018-05-06 08:00 | 4.77 | 4.68
2018-05-06 08:30 | 4.73 | 4.66
2018-05-06 09:00 | 4.81 | 4.77
2018-05-06 09:30 | 4.69 | 4.67
2018-05-06 10:00 | 4.26 | 4.23
2018-05-06 10:30 | 4.03 | 4
2018-05-06 11:00 | 3.8 | 3.76
2018-05-06 11:30 | 3.9 | 3.87
2018-05-06 12:00 | 3.74 | 3.71
2018-05-06 12:30 | 3.95 | 3.93
2018-05-06 13:00 | 3.97 | 3.95
2018-05-06 13:30 | 4.58 | 4.55
2018-05-06 14:00 | 4.72 | 4.69
2018-05-06 14:30 | 5.79 | 5.77
2018-05-06 15:00 | 6.35 | 6.33
2018-05-06 15:30 | 6.02 | 6
2018-05-06 16:00 | 7.49 | 7.48
2018-05-06 16:30 | 7.62 | 7.61
2018-05-06 17:00 | 8.38 | 8.37
2018-05-06 17:30 | 9.21 | 9.2
2018-05-06 18:00 | 10.08 | 10.06
2018-05-06 18:30 | 10.04 | 10.03
2018-05-06 19:00 | 9.74 | 9.73
2018-05-06 19:30 | 9.23 | 9.22
2018-05-06 20:00 | 9.12 | 9.12
2018-05-06 20:30 | 8.91 | 8.9
2018-05-06 21:00 | 8.55 | 8.54
2018-05-06 21:30 | 7.98 | 7.97
2018-05-06 22:00 | 7.47 | 7.46
2018-05-06 22:30 | 7.35 | 7.33
2018-05-06 23:00 | 7.31 | 7.3
2018-05-06 23:30 | 6.59 | 6.57
2018-05-07 | 5.85 | 5.83
2018-05-07 00:30 | 5.18 | 5.15
2018-05-07 01:00 | 4.89 | 4.86
2018-05-07 01:30 | 4.55 | 4.51
2018-05-07 02:00 | 4.35 | 4.3
2018-05-07 02:30 | 4.21 | 4.16
2018-05-07 03:00 | 3.98 | 3.92
2018-05-07 03:30 | 3.96 | 3.9
2018-05-07 04:00 | 3.88 | 3.82
2018-05-07 04:30 | 3.92 | 3.85
2018-05-07 05:00 | 3.97 | 3.91
2018-05-07 05:30 | 4.03 | 3.97
2018-05-07 06:00 | 4.22 | 4.17
2018-05-07 06:30 | 4.27 | 4.19
2018-05-07 07:00 | 4.32 | 4.18
2018-05-07 07:30 | 4.59 | 4.47
2018-05-07 08:00 | 4.79 | 4.67
2018-05-07 08:30 | 5.28 | 5.2
2018-05-07 09:00 | 4.54 | 4.47
2018-05-07 09:30 | 5.26 | 5.21
2018-05-07 10:00 | 5.74 | 5.71
2018-05-07 10:30 | 5.55 | 5.53
2018-05-07 11:00 | 5.1 | 5.09
2018-05-07 11:30 | 6.25 | 6.24
2018-05-07 12:00 | 6.29 | 6.28
2018-05-07 12:30 | 7.66 | 7.65
2018-05-07 13:00 | 7.24 | 7.23
2018-05-07 13:30 | 6.88 | 6.87
2018-05-07 14:00 | 7.25 | 7.24
2018-05-07 14:30 | 7.61 | 7.59
2018-05-07 15:00 | 7.54 | 7.52
2018-05-07 15:30 | 7.95 | 7.94
2018-05-07 16:00 | 8.44 | 8.43
2018-05-07 16:30 | 9.09 | 9.08
2018-05-07 17:00 | 10.07 | 10.07
2018-05-07 17:30 | 10.97 | 10.96
2018-05-07 18:00 | 11.18 | 11.17
2018-05-07 18:30 | 11.01 | 11
2018-05-07 19:00 | 10.85 | 10.85
2018-05-07 19:30 | 10.51 | 10.5
2018-05-07 20:00 | 10.27 | 10.27
2018-05-07 20:30 | 10.11 | 10.11
2018-05-07 21:00 | 9.42 | 9.42
2018-05-07 21:30 | 8.62 | 8.62
2018-05-07 22:00 | 8.12 | 8.12
2018-05-07 22:30 | 7.62 | 7.61
2018-05-07 23:00 | 7.35 | 7.33
2018-05-07 23:30 | 6.4 | 6.37
2018-05-08 | 5.6 | 5.57
2018-05-08 00:30 | 4.99 | 4.96
2018-05-08 01:00 | 4.72 | 4.68
2018-05-08 01:30 | 4.51 | 4.47
2018-05-08 02:00 | 4.21 | 4.17
2018-05-08 02:30 | 4.09 | 4.05
2018-05-08 03:00 | 3.89 | 3.84
2018-05-08 03:30 | 3.97 | 3.92
2018-05-08 04:00 | 4.06 | 4.01
2018-05-08 04:30 | 4.22 | 4.17
2018-05-08 05:00 | 4.56 | 4.52
2018-05-08 05:30 | 5.06 | 5.03
2018-05-08 06:00 | 5.51 | 5.49
2018-05-08 06:30 | 5.99 | 5.97
2018-05-08 07:00 | 6.44 | 6.42
2018-05-08 07:30 | 6.88 | 6.85
2018-05-08 08:00 | 7.67 | 7.66
2018-05-08 08:30 | 7.11 | 7.1
2018-05-08 09:00 | 6.51 | 6.51
2018-05-08 09:30 | 6.1 | 6.1
2018-05-08 10:00 | 6.24 | 6.23
2018-05-08 10:30 | 6.12 | 6.12
2018-05-08 11:00 | 6.08 | 6.08
2018-05-08 11:30 | 6.37 | 6.36
2018-05-08 12:00 | 6.39 | 6.38
2018-05-08 12:30 | 6.27 | 6.26
2018-05-08 13:00 | 6.39 | 6.38
2018-05-08 13:30 | 6.4 | 6.4
2018-05-08 14:00 | 7.38 | 7.38
2018-05-08 14:30 | 7.45 | 7.45
2018-05-08 15:00 | 7.49 | 7.49
2018-05-08 15:30 | 8.13 | 8.12
2018-05-08 16:00 | 8.87 | 8.87
2018-05-08 16:30 | 8.72 | 8.71
2018-05-08 17:00 | 10.17 | 10.16
2018-05-08 17:30 | 11.31 | 11.3
2018-05-08 18:00 | 12.26 | 12.25
2018-05-08 18:30 | 12.39 | 12.37
2018-05-08 19:00 | 12.53 | 12.51
2018-05-08 19:30 | 12.1 | 12.09
2018-05-08 20:00 | 11.8 | 11.79
2018-05-08 20:30 | 11.5 | 11.5
2018-05-08 21:00 | 10.73 | 10.72
2018-05-08 21:30 | 10.07 | 10.07
2018-05-08 22:00 | 9.31 | 9.31
2018-05-08 22:30 | 8.66 | 8.66
2018-05-08 23:00 | 7.97 | 7.97
2018-05-08 23:30 | 6.59 | 6.57
2018-05-09 | 5.75 | 5.72
2018-05-09 00:30 | 5.1 | 5.07
2018-05-09 01:00 | 4.8 | 4.77
2018-05-09 01:30 | 4.5 | 4.46
2018-05-09 02:00 | 4.29 | 4.24
2018-05-09 02:30 | 4.15 | 4.11
2018-05-09 03:00 | 4.02 | 3.96
2018-05-09 03:30 | 4.11 | 4.06
2018-05-09 04:00 | 4.13 | 4.07
2018-05-09 04:30 | 4.3 | 4.25
2018-05-09 05:00 | 4.58 | 4.54
2018-05-09 05:30 | 5.2 | 5.18
2018-05-09 06:00 | 6.03 | 6.02
2018-05-09 06:30 | 6.21 | 6.19
2018-05-09 07:00 | 6.63 | 6.6
2018-05-09 07:30 | 7.01 | 6.98
2018-05-09 08:00 | 6.04 | 6.01
2018-05-09 08:30 | 5.69 | 5.67
2018-05-09 09:00 | 5.95 | 5.93
2018-05-09 09:30 | 5.31 | 5.29
2018-05-09 10:00 | 3.67 | 3.65
2018-05-09 10:30 | 3.32 | 3.3
2018-05-09 11:00 | 3.14 | 3.12
2018-05-09 11:30 | 3.13 | 3.1
2018-05-09 12:00 | 3.1 | 3.07
2018-05-09 12:30 | 3.26 | 3.24
2018-05-09 13:00 | 3.52 | 3.5
2018-05-09 13:30 | 3.74 | 3.72
2018-05-09 14:00 | 4.27 | 4.25
2018-05-09 14:30 | 4.68 | 4.66
2018-05-09 15:00 | 5.07 | 5.05
2018-05-09 15:30 | 6.01 | 6
2018-05-09 16:00 | 7.03 | 7.01
2018-05-09 16:30 | 7.98 | 7.97
2018-05-09 17:00 | 9.13 | 9.12
2018-05-09 17:30 | 10 | 9.99
2018-05-09 18:00 | 11.08 | 11.07
2018-05-09 18:30 | 11.47 | 11.46
2018-05-09 19:00 | 11.53 | 11.52
2018-05-09 19:30 | 11.06 | 11.05
2018-05-09 20:00 | 11 | 10.99
2018-05-09 20:30 | 10.95 | 10.94
2018-05-09 21:00 | 10.18 | 10.17
2018-05-09 21:30 | 9.18 | 9.17
2018-05-09 22:00 | 8.57 | 8.56
2018-05-09 22:30 | 7.94 | 7.93
2018-05-09 23:00 | 7.64 | 7.63
2018-05-09 23:30 | 6.52 | 6.5
2018-05-10 | 5.62 | 5.59
2018-05-10 00:30 | 5.08 | 5.05
2018-05-10 01:00 | 4.78 | 4.74
2018-05-10 01:30 | 4.5 | 4.45
2018-05-10 02:00 | 4.31 | 4.26
2018-05-10 02:30 | 4.1 | 4.05
2018-05-10 03:00 | 4.07 | 4.01
2018-05-10 03:30 | 4.05 | 3.99
2018-05-10 04:00 | 4.14 | 4.08
2018-05-10 04:30 | 4.33 | 4.28
2018-05-10 05:00 | 4.64 | 4.6
2018-05-10 05:30 | 5.11 | 5.08
2018-05-10 06:00 | 5.61 | 5.58
2018-05-10 06:30 | 6.04 | 6.01
2018-05-10 07:00 | 6.47 | 6.43
2018-05-10 07:30 | 6.6 | 6.57
2018-05-10 08:00 | 5.95 | 5.92
2018-05-10 08:30 | 5.11 | 5.08
2018-05-10 09:00 | 4.16 | 4.13
2018-05-10 09:30 | 3.78 | 3.76
2018-05-10 10:00 | 3.3 | 3.28
2018-05-10 10:30 | 2.95 | 2.93
2018-05-10 11:00 | 2.82 | 2.8
2018-05-10 11:30 | 2.76 | 2.74
2018-05-10 12:00 | 2.74 | 2.71
2018-05-10 12:30 | 2.89 | 2.86
2018-05-10 13:00 | 3.41 | 3.4
2018-05-10 13:30 | 4 | 3.99
2018-05-10 14:00 | 4.75 | 4.74
2018-05-10 14:30 | 5.99 | 5.98
2018-05-10 15:00 | 5.97 | 5.97
2018-05-10 15:30 | 5.98 | 5.97
2018-05-10 16:00 | 7.15 | 7.14
2018-05-10 16:30 | 8.23 | 8.22
2018-05-10 17:00 | 9.14 | 9.13
2018-05-10 17:30 | 10.02 | 10.01
2018-05-10 18:00 | 11.38 | 11.36
2018-05-10 18:30 | 11.4 | 11.38
2018-05-10 19:00 | 11.69 | 11.66
2018-05-10 19:30 | 11.38 | 11.37
2018-05-10 20:00 | 11.45 | 11.44
2018-05-10 20:30 | 11.38 | 11.38
2018-05-10 21:00 | 10.6 | 10.59
2018-05-10 21:30 | 9.87 | 9.86
2018-05-10 22:00 | 9.14 | 9.14
2018-05-10 22:30 | 8.55 | 8.55
2018-05-10 23:00 | 7.78 | 7.77
2018-05-10 23:30 | 6.68 | 6.67
2018-05-11 | 5.73 | 5.7
2018-05-11 00:30 | 5.08 | 5.05
2018-05-11 01:00 | 4.76 | 4.72
2018-05-11 01:30 | 4.53 | 4.49
2018-05-11 02:00 | 4.25 | 4.19
2018-05-11 02:30 | 4.12 | 4.06
2018-05-11 03:00 | 4.04 | 3.98
2018-05-11 03:30 | 4.09 | 4.03
2018-05-11 04:00 | 4.09 | 4.03
2018-05-11 04:30 | 4.28 | 4.22
2018-05-11 05:00 | 4.66 | 4.61
2018-05-11 05:30 | 5.22 | 5.19
2018-05-11 06:00 | 6.06 | 6.05
2018-05-11 06:30 | 6.55 | 6.53
2018-05-11 07:00 | 7.24 | 7.22
2018-05-11 07:30 | 7.15 | 7.13
2018-05-11 08:00 | 6.63 | 6.61
2018-05-11 08:30 | 5.65 | 5.64
2018-05-11 09:00 | 4.61 | 4.58
2018-05-11 09:30 | 4.31 | 4.29
2018-05-11 10:00 | 4.26 | 4.25
2018-05-11 10:30 | 3.43 | 3.4
2018-05-11 11:00 | 2.87 | 2.83
2018-05-11 11:30 | 2.62 | 2.58
2018-05-11 12:00 | 2.47 | 2.43
2018-05-11 12:30 | 2.59 | 2.55
2018-05-11 13:00 | 2.82 | 2.79
2018-05-11 13:30 | 2.97 | 2.94
2018-05-11 14:00 | 3.5 | 3.47
2018-05-11 14:30 | 3.84 | 3.82
2018-05-11 15:00 | 4.35 | 4.32
2018-05-11 15:30 | 6.01 | 5.99
2018-05-11 16:00 | 7.33 | 7.3
2018-05-11 16:30 | 7.9 | 7.88
2018-05-11 17:00 | 8.46 | 8.45
2018-05-11 17:30 | 9.5 | 9.49
2018-05-11 18:00 | 10.44 | 10.43
2018-05-11 18:30 | 10.87 | 10.87
2018-05-11 19:00 | 11.02 | 11.02
2018-05-11 19:30 | 10.78 | 10.77
2018-05-11 20:00 | 10.78 | 10.77
2018-05-11 20:30 | 10.97 | 10.97
2018-05-11 21:00 | 10.59 | 10.58
2018-05-11 21:30 | 9.88 | 9.87
2018-05-11 22:00 | 9.13 | 9.12
2018-05-11 22:30 | 8.5 | 8.5
2018-05-11 23:00 | 8.41 | 8.4
2018-05-11 23:30 | 7.51 | 7.49
2018-05-12 | 6.69 | 6.66
2018-05-12 00:30 | 5.96 | 5.93
2018-05-12 01:00 | 5.61 | 5.58
2018-05-12 01:30 | 5.24 | 5.21
2018-05-12 02:00 | 4.92 | 4.87
2018-05-12 02:30 | 4.67 | 4.62
2018-05-12 03:00 | 4.62 | 4.56
2018-05-12 03:30 | 4.62 | 4.57
2018-05-12 04:00 | 4.62 | 4.57
2018-05-12 04:30 | 4.61 | 4.56
2018-05-12 05:00 | 4.79 | 4.74
2018-05-12 05:30 | 5.04 | 5
2018-05-12 06:00 | 5.27 | 5.23
2018-05-12 06:30 | 5.4 | 5.33
2018-05-12 07:00 | 5.93 | 5.86
2018-05-12 07:30 | 6.33 | 6.27
2018-05-12 08:00 | 6.5 | 6.46
2018-05-12 08:30 | 6.39 | 6.35
2018-05-12 09:00 | 6.1 | 6.08
2018-05-12 09:30 | 5.49 | 5.47
2018-05-12 10:00 | 4.98 | 4.96
2018-05-12 10:30 | 4.47 | 4.44
2018-05-12 11:00 | 4.01 | 3.98
2018-05-12 11:30 | 3.74 | 3.71
2018-05-12 12:00 | 3.61 | 3.59
2018-05-12 12:30 | 3.57 | 3.54
2018-05-12 13:00 | 3.65 | 3.62
2018-05-12 13:30 | 3.79 | 3.76
2018-05-12 14:00 | 4.16 | 4.13
2018-05-12 14:30 | 4.49 | 4.47
2018-05-12 15:00 | 4.97 | 4.95
2018-05-12 15:30 | 5.63 | 5.61
2018-05-12 16:00 | 6.43 | 6.41
2018-05-12 16:30 | 7.31 | 7.3
2018-05-12 17:00 | 8.24 | 8.23
2018-05-12 17:30 | 9.24 | 9.23
2018-05-12 18:00 | 10.31 | 10.3
2018-05-12 18:30 | 10.62 | 10.62
2018-05-12 19:00 | 10.7 | 10.7
2018-05-12 19:30 | 10.47 | 10.46
2018-05-12 20:00 | 10.33 | 10.32
2018-05-12 20:30 | 10.14 | 10.13
2018-05-12 21:00 | 9.55 | 9.55
2018-05-12 21:30 | 8.95 | 8.94
2018-05-12 22:00 | 8.47 | 8.46
2018-05-12 22:30 | 8.19 | 8.18
2018-05-12 23:00 | 8.26 | 8.25
2018-05-12 23:30 | 7.45 | 7.43
2018-05-13 | 6.67 | 6.64
2018-05-13 00:30 | 5.95 | 5.92
2018-05-13 01:00 | 5.52 | 5.48
2018-05-13 01:30 | 5.08 | 5.04
2018-05-13 02:00 | 4.86 | 4.81
2018-05-13 02:30 | 4.72 | 4.67
2018-05-13 03:00 | 4.56 | 4.5
2018-05-13 03:30 | 4.47 | 4.41
2018-05-13 04:00 | 4.36 | 4.3
2018-05-13 04:30 | 4.5 | 4.44
2018-05-13 05:00 | 4.56 | 4.51
2018-05-13 05:30 | 4.85 | 4.8
2018-05-13 06:00 | 5.02 | 4.97
2018-05-13 06:30 | 5.3 | 5.23
2018-05-13 07:00 | 5.94 | 5.86
2018-05-13 07:30 | 6.39 | 6.33
2018-05-13 08:00 | 6.61 | 6.56
2018-05-13 08:30 | 6.53 | 6.49
2018-05-13 09:00 | 6.32 | 6.28
2018-05-13 09:30 | 5.89 | 5.86
2018-05-13 10:00 | 5.34 | 5.31
2018-05-13 10:30 | 4.65 | 4.62
2018-05-13 11:00 | 4.28 | 4.25
2018-05-13 11:30 | 3.98 | 3.95
2018-05-13 12:00 | 3.78 | 3.75
2018-05-13 12:30 | 3.77 | 3.74
2018-05-13 13:00 | 3.8 | 3.77
2018-05-13 13:30 | 3.87 | 3.85
2018-05-13 14:00 | 4.18 | 4.15
2018-05-13 14:30 | 4.46 | 4.44
2018-05-13 15:00 | 4.9 | 4.88
2018-05-13 15:30 | 5.74 | 5.73
2018-05-13 16:00 | 6.51 | 6.5
2018-05-13 16:30 | 7.43 | 7.42
2018-05-13 17:00 | 8.58 | 8.56
2018-05-13 17:30 | 9.84 | 9.83
2018-05-13 18:00 | 10.79 | 10.78
2018-05-13 18:30 | 10.71 | 10.7
2018-05-13 19:00 | 10.61 | 10.6
2018-05-13 19:30 | 10.24 | 10.24
2018-05-13 20:00 | 10.14 | 10.14
2018-05-13 20:30 | 10.46 | 10.45
2018-05-13 21:00 | 10.13 | 10.12
2018-05-13 21:30 | 9.55 | 9.54
2018-05-13 22:00 | 8.33 | 8.32
2018-05-13 22:30 | 7.92 | 7.9
2018-05-13 23:00 | 7.7 | 7.68
2018-05-13 23:30 | 6.85 | 6.82
2018-05-14 | 5.96 | 5.92
2018-05-14 00:30 | 5.3 | 5.25
2018-05-14 01:00 | 4.94 | 4.89
2018-05-14 01:30 | 4.71 | 4.66
2018-05-14 02:00 | 4.56 | 4.51
2018-05-14 02:30 | 4.36 | 4.3
2018-05-14 03:00 | 4.22 | 4.15
2018-05-14 03:30 | 4.32 | 4.25
2018-05-14 04:00 | 4.34 | 4.28
2018-05-14 04:30 | 4.59 | 4.53
2018-05-14 05:00 | 5.05 | 5.01
2018-05-14 05:30 | 5.67 | 5.64
2018-05-14 06:00 | 6.57 | 6.56
2018-05-14 06:30 | 7.22 | 7.2
2018-05-14 07:00 | 7.83 | 7.8
2018-05-14 07:30 | 8.39 | 8.38
2018-05-14 08:00 | 7.82 | 7.81
2018-05-14 08:30 | 6.55 | 6.54
2018-05-14 09:00 | 5.73 | 5.72
2018-05-14 09:30 | 5.23 | 5.21
2018-05-14 10:00 | 5.66 | 5.65
2018-05-14 10:30 | 5.18 | 5.16
2018-05-14 11:00 | 5.09 | 5.08
2018-05-14 11:30 | 3.89 | 3.88
2018-05-14 12:00 | 3.84 | 3.83
2018-05-14 12:30 | 4.25 | 4.25
2018-05-14 13:00 | 5.84 | 5.83
2018-05-14 13:30 | 6.08 | 6.07
2018-05-14 14:00 | 6.05 | 6.04
2018-05-14 14:30 | 6.09 | 6.08
2018-05-14 15:00 | 6.35 | 6.35
2018-05-14 15:30 | 6.45 | 6.45
2018-05-14 16:00 | 7.45 | 7.45
2018-05-14 16:30 | 8.54 | 8.54
2018-05-14 17:00 | 9.66 | 9.66
2018-05-14 17:30 | 10.72 | 10.72
2018-05-14 18:00 | 11.99 | 11.98
2018-05-14 18:30 | 12.31 | 12.3
2018-05-14 19:00 | 12.33 | 12.32
2018-05-14 19:30 | 11.74 | 11.74
2018-05-14 20:00 | 11.32 | 11.32
2018-05-14 20:30 | 11.58 | 11.58
2018-05-14 21:00 | 10.89 | 10.89
2018-05-14 21:30 | 10.14 | 10.14
2018-05-14 22:00 | 9.41 | 9.41
2018-05-14 22:30 | 8.37 | 8.37
2018-05-14 23:00 | 7.78 | 7.77
2018-05-14 23:30 | 6.67 | 6.65
2018-05-15 | 5.65 | 5.62
2018-05-15 00:30 | 5.09 | 5.05
2018-05-15 01:00 | 4.78 | 4.73
2018-05-15 01:30 | 4.52 | 4.47
2018-05-15 02:00 | 4.38 | 4.33
2018-05-15 02:30 | 4.24 | 4.19
2018-05-15 03:00 | 4.18 | 4.13
2018-05-15 03:30 | 4.21 | 4.16
2018-05-15 04:00 | 4.27 | 4.21
2018-05-15 04:30 | 4.47 | 4.42
2018-05-15 05:00 | 4.87 | 4.83
2018-05-15 05:30 | 5.49 | 5.46
2018-05-15 06:00 | 6.16 | 6.14
2018-05-15 06:30 | 6.82 | 6.79
2018-05-15 07:00 | 7.22 | 7.18
2018-05-15 07:30 | 7.4 | 7.38
2018-05-15 08:00 | 6.78 | 6.76
2018-05-15 08:30 | 5.53 | 5.5
2018-05-15 09:00 | 4.72 | 4.69
2018-05-15 09:30 | 4.59 | 4.57
2018-05-15 10:00 | 4.14 | 4.13
2018-05-15 10:30 | 3.65 | 3.63
2018-05-15 11:00 | 4.28 | 4.26
2018-05-15 11:30 | 4.23 | 4.22
2018-05-15 12:00 | 4.01 | 4
2018-05-15 12:30 | 4.62 | 4.61
2018-05-15 13:00 | 5.41 | 5.4
2018-05-15 13:30 | 5.95 | 5.94
2018-05-15 14:00 | 5.94 | 5.93
2018-05-15 14:30 | 5.95 | 5.95
2018-05-15 15:00 | 6.49 | 6.48
2018-05-15 15:30 | 7.13 | 7.13
2018-05-15 16:00 | 8.29 | 8.28
2018-05-15 16:30 | 9.38 | 9.37
2018-05-15 17:00 | 9.41 | 9.41
2018-05-15 17:30 | 10.33 | 10.32
2018-05-15 18:00 | 11.78 | 11.76
2018-05-15 18:30 | 12 | 11.99
2018-05-15 19:00 | 12.29 | 12.28
2018-05-15 19:30 | 11.74 | 11.73
2018-05-15 20:00 | 11.55 | 11.55
2018-05-15 20:30 | 11.44 | 11.44
2018-05-15 21:00 | 10.77 | 10.77
2018-05-15 21:30 | 9.69 | 9.69
2018-05-15 22:00 | 8.96 | 8.95
2018-05-15 22:30 | 8.35 | 8.35
2018-05-15 23:00 | 7.93 | 7.92
2018-05-15 23:30 | 6.85 | 6.83
2018-05-16 | 5.91 | 5.87
2018-05-16 00:30 | 5.35 | 5.31
2018-05-16 01:00 | 5.08 | 5.04
2018-05-16 01:30 | 4.82 | 4.78
2018-05-16 02:00 | 4.44 | 4.39
2018-05-16 02:30 | 4.37 | 4.32
2018-05-16 03:00 | 4.32 | 4.27
2018-05-16 03:30 | 4.38 | 4.33
2018-05-16 04:00 | 4.5 | 4.44
2018-05-16 04:30 | 4.74 | 4.69
2018-05-16 05:00 | 5.19 | 5.16
2018-05-16 05:30 | 5.96 | 5.93
2018-05-16 06:00 | 6.5 | 6.48
2018-05-16 06:30 | 7.1 | 7.08
2018-05-16 07:00 | 7.82 | 7.79
2018-05-16 07:30 | 8.04 | 8.02
2018-05-16 08:00 | 7.23 | 7.2
2018-05-16 08:30 | 6.04 | 6.01
2018-05-16 09:00 | 4.78 | 4.74
2018-05-16 09:30 | 4.17 | 4.14
2018-05-16 10:00 | 3.63 | 3.59
2018-05-16 10:30 | 3.22 | 3.19
2018-05-16 11:00 | 2.83 | 2.8
2018-05-16 11:30 | 2.54 | 2.51
2018-05-16 12:00 | 2.85 | 2.82
2018-05-16 12:30 | 2.39 | 2.36
2018-05-16 13:00 | 3.3 | 3.27
2018-05-16 13:30 | 4.98 | 4.96
2018-05-16 14:00 | 5.04 | 5.02
2018-05-16 14:30 | 4.13 | 4.11
2018-05-16 15:00 | 4.7 | 4.69
2018-05-16 15:30 | 5.76 | 5.76
2018-05-16 16:00 | 6.6 | 6.59
2018-05-16 16:30 | 7.61 | 7.61
2018-05-16 17:00 | 8.85 | 8.84
2018-05-16 17:30 | 10.39 | 10.38
2018-05-16 18:00 | 11.61 | 11.6
2018-05-16 18:30 | 11.81 | 11.8
2018-05-16 19:00 | 12.15 | 12.15
2018-05-16 19:30 | 12.03 | 12.03
2018-05-16 20:00 | 11.8 | 11.8
2018-05-16 20:30 | 11.89 | 11.89
2018-05-16 21:00 | 11.23 | 11.23
2018-05-16 21:30 | 10.29 | 10.29
2018-05-16 22:00 | 9.49 | 9.49
2018-05-16 22:30 | 8.51 | 8.51
2018-05-16 23:00 | 7.93 | 7.92
2018-05-16 23:30 | 7.05 | 7.04
2018-05-17 | 6.19 | 6.16
2018-05-17 00:30 | 5.43 | 5.4
2018-05-17 01:00 | 5.04 | 5
2018-05-17 01:30 | 4.77 | 4.73
2018-05-17 02:00 | 4.52 | 4.47
2018-05-17 02:30 | 4.34 | 4.29
2018-05-17 03:00 | 4.3 | 4.25
2018-05-17 03:30 | 4.32 | 4.26
2018-05-17 04:00 | 4.41 | 4.36
2018-05-17 04:30 | 4.71 | 4.67
2018-05-17 05:00 | 5.15 | 5.11
2018-05-17 05:30 | 6.04 | 6.01
2018-05-17 06:00 | 6.98 | 6.97
2018-05-17 06:30 | 7.9 | 7.89
2018-05-17 07:00 | 8.59 | 8.59
2018-05-17 07:30 | 8.87 | 8.87
2018-05-17 08:00 | 8.17 | 8.16
2018-05-17 08:30 | 6.74 | 6.74
2018-05-17 09:00 | 5.58 | 5.57
2018-05-17 09:30 | 4.91 | 4.9
2018-05-17 10:00 | 4.39 | 4.38
2018-05-17 10:30 | 4 | 3.99
2018-05-17 11:00 | 3.67 | 3.66
2018-05-17 11:30 | 3.54 | 3.53
2018-05-17 12:00 | 3.94 | 3.94
2018-05-17 12:30 | 5.05 | 5.05
2018-05-17 13:00 | 5.23 | 5.22
2018-05-17 13:30 | 4.71 | 4.7
2018-05-17 14:00 | 5.36 | 5.35
2018-05-17 14:30 | 5.52 | 5.52
2018-05-17 15:00 | 5.19 | 5.18
2018-05-17 15:30 | 6 | 5.99
2018-05-17 16:00 | 7.01 | 7.01
2018-05-17 16:30 | 7.87 | 7.87
2018-05-17 17:00 | 9.11 | 9.1
2018-05-17 17:30 | 10.52 | 10.52
2018-05-17 18:00 | 11.49 | 11.48
2018-05-17 18:30 | 11.61 | 11.59
2018-05-17 19:00 | 11.95 | 11.93
2018-05-17 19:30 | 11.41 | 11.41
2018-05-17 20:00 | 11.71 | 11.71
2018-05-17 20:30 | 11.76 | 11.76
2018-05-17 21:00 | 11.24 | 11.24
2018-05-17 21:30 | 10.56 | 10.55
2018-05-17 22:00 | 9.74 | 9.73
2018-05-17 22:30 | 8.87 | 8.86
2018-05-17 23:00 | 8.16 | 8.15
2018-05-17 23:30 | 7.16 | 7.14
2018-05-18 | 6.34 | 6.31
2018-05-18 00:30 | 5.56 | 5.53
2018-05-18 01:00 | 5.18 | 5.15
2018-05-18 01:30 | 4.93 | 4.89
2018-05-18 02:00 | 4.63 | 4.59
2018-05-18 02:30 | 4.51 | 4.47
2018-05-18 03:00 | 4.42 | 4.37
2018-05-18 03:30 | 4.4 | 4.35
2018-05-18 04:00 | 4.52 | 4.47
2018-05-18 04:30 | 4.68 | 4.63
2018-05-18 05:00 | 4.97 | 4.93
2018-05-18 05:30 | 5.64 | 5.61
2018-05-18 06:00 | 6.28 | 6.26
2018-05-18 06:30 | 6.85 | 6.83
2018-05-18 07:00 | 7.22 | 7.19
2018-05-18 07:30 | 7.28 | 7.26
2018-05-18 08:00 | 6.98 | 6.95
2018-05-18 08:30 | 6.24 | 6.22
2018-05-18 09:00 | 5.69 | 5.66
2018-05-18 09:30 | 5.19 | 5.16
2018-05-18 10:00 | 4.72 | 4.7
2018-05-18 10:30 | 3.92 | 3.88
2018-05-18 11:00 | 4.12 | 4.07
2018-05-18 11:30 | 4.72 | 4.67
2018-05-18 12:00 | 4.64 | 4.6
2018-05-18 12:30 | 4.62 | 4.58
2018-05-18 13:00 | 4.75 | 4.71
2018-05-18 13:30 | 5.12 | 5.09
2018-05-18 14:00 | 4.36 | 4.34
2018-05-18 14:30 | 4.18 | 4.15
2018-05-18 15:00 | 4.71 | 4.69
2018-05-18 15:30 | 5.61 | 5.59
2018-05-18 16:00 | 7.52 | 7.5
2018-05-18 16:30 | 8.59 | 8.57
2018-05-18 17:00 | 8.69 | 8.67
2018-05-18 17:30 | 9.2 | 9.19
2018-05-18 18:00 | 9.98 | 9.97
2018-05-18 18:30 | 10.22 | 10.21
2018-05-18 19:00 | 10.23 | 10.23
2018-05-18 19:30 | 10.16 | 10.15
2018-05-18 20:00 | 10.04 | 10.03
2018-05-18 20:30 | 10.12 | 10.11
2018-05-18 21:00 | 9.61 | 9.6
2018-05-18 21:30 | 9.18 | 9.17
2018-05-18 22:00 | 8.65 | 8.64
2018-05-18 22:30 | 8.44 | 8.43
2018-05-18 23:00 | 8.33 | 8.32
2018-05-18 23:30 | 7.39 | 7.37
2018-05-19 | 6.54 | 6.52
2018-05-19 00:30 | 5.87 | 5.84
2018-05-19 01:00 | 5.59 | 5.55
2018-05-19 01:30 | 5.2 | 5.16
2018-05-19 02:00 | 4.75 | 4.71
2018-05-19 02:30 | 4.63 | 4.58
2018-05-19 03:00 | 4.54 | 4.49
2018-05-19 03:30 | 4.53 | 4.48
2018-05-19 04:00 | 4.51 | 4.47
2018-05-19 04:30 | 4.56 | 4.51
2018-05-19 05:00 | 4.68 | 4.63
2018-05-19 05:30 | 4.95 | 4.9
2018-05-19 06:00 | 5.17 | 5.13
2018-05-19 06:30 | 5.41 | 5.36
2018-05-19 07:00 | 5.86 | 5.78
2018-05-19 07:30 | 6.33 | 6.28
2018-05-19 08:00 | 6.42 | 6.38
2018-05-19 08:30 | 6.25 | 6.21
2018-05-19 09:00 | 5.85 | 5.81
2018-05-19 09:30 | 5.4 | 5.37
2018-05-19 10:00 | 4.88 | 4.86
2018-05-19 10:30 | 4.47 | 4.44
2018-05-19 11:00 | 4.21 | 4.18
2018-05-19 11:30 | 3.88 | 3.85
2018-05-19 12:00 | 3.79 | 3.76
2018-05-19 12:30 | 3.64 | 3.6
2018-05-19 13:00 | 3.75 | 3.72
2018-05-19 13:30 | 3.89 | 3.86
2018-05-19 14:00 | 4.32 | 4.29
2018-05-19 14:30 | 4.69 | 4.66
2018-05-19 15:00 | 5.07 | 5.05
2018-05-19 15:30 | 5.79 | 5.77
2018-05-19 16:00 | 6.45 | 6.43
2018-05-19 16:30 | 7.47 | 7.45
2018-05-19 17:00 | 8.51 | 8.5
2018-05-19 17:30 | 9.65 | 9.64
2018-05-19 18:00 | 10.47 | 10.46
2018-05-19 18:30 | 10.41 | 10.41
2018-05-19 19:00 | 10.23 | 10.22
2018-05-19 19:30 | 9.88 | 9.87
2018-05-19 20:00 | 9.89 | 9.88
2018-05-19 20:30 | 9.94 | 9.94
2018-05-19 21:00 | 9.42 | 9.41
2018-05-19 21:30 | 8.58 | 8.58
2018-05-19 22:00 | 8.4 | 8.39
2018-05-19 22:30 | 8.31 | 8.3
2018-05-19 23:00 | 8.35 | 8.34
2018-05-19 23:30 | 7.44 | 7.42
2018-05-20 | 6.65 | 6.63
2018-05-20 00:30 | 5.9 | 5.87
2018-05-20 01:00 | 5.51 | 5.48
2018-05-20 01:30 | 5.15 | 5.11
2018-05-20 02:00 | 4.79 | 4.75
2018-05-20 02:30 | 4.61 | 4.56
2018-05-20 03:00 | 4.46 | 4.4
2018-05-20 03:30 | 4.39 | 4.33
2018-05-20 04:00 | 4.39 | 4.33
2018-05-20 04:30 | 4.45 | 4.4
2018-05-20 05:00 | 4.55 | 4.5
2018-05-20 05:30 | 4.71 | 4.66
2018-05-20 06:00 | 4.78 | 4.74
2018-05-20 06:30 | 5.03 | 4.96
2018-05-20 07:00 | 5.33 | 5.24
2018-05-20 07:30 | 5.81 | 5.74
2018-05-20 08:00 | 5.93 | 5.87
2018-05-20 08:30 | 6.01 | 5.96
2018-05-20 09:00 | 5.82 | 5.78
2018-05-20 09:30 | 5.57 | 5.54
2018-05-20 10:00 | 5.22 | 5.19
2018-05-20 10:30 | 4.8 | 4.77
2018-05-20 11:00 | 4.4 | 4.38
2018-05-20 11:30 | 4.27 | 4.25
2018-05-20 12:00 | 4.16 | 4.13
2018-05-20 12:30 | 4.16 | 4.14
2018-05-20 13:00 | 4.28 | 4.26
2018-05-20 13:30 | 4.36 | 4.33
2018-05-20 14:00 | 4.68 | 4.65
2018-05-20 14:30 | 5.06 | 5.03
2018-05-20 15:00 | 5.59 | 5.57
2018-05-20 15:30 | 6.26 | 6.25
2018-05-20 16:00 | 6.96 | 6.94
2018-05-20 16:30 | 8.04 | 8.02
2018-05-20 17:00 | 9.44 | 9.43
2018-05-20 17:30 | 10.6 | 10.59
2018-05-20 18:00 | 11.38 | 11.37
2018-05-20 18:30 | 11.22 | 11.21
2018-05-20 19:00 | 11.26 | 11.26
2018-05-20 19:30 | 10.87 | 10.86
2018-05-20 20:00 | 10.6 | 10.6
2018-05-20 20:30 | 10.55 | 10.54
2018-05-20 21:00 | 10.04 | 10.04
2018-05-20 21:30 | 9.3 | 9.3
2018-05-20 22:00 | 8.69 | 8.69
2018-05-20 22:30 | 8.23 | 8.22
2018-05-20 23:00 | 8.01 | 8
2018-05-20 23:30 | 7.07 | 7.05
2018-05-21 | 6.3 | 6.27
2018-05-21 00:30 | 5.59 | 5.56
2018-05-21 01:00 | 5.12 | 5.07
2018-05-21 01:30 | 4.89 | 4.84
2018-05-21 02:00 | 4.65 | 4.6
2018-05-21 02:30 | 4.52 | 4.46
2018-05-21 03:00 | 4.36 | 4.29
2018-05-21 03:30 | 4.48 | 4.42
2018-05-21 04:00 | 4.66 | 4.6
2018-05-21 04:30 | 4.9 | 4.85
2018-05-21 05:00 | 5.33 | 5.29
2018-05-21 05:30 | 6.13 | 6.1
2018-05-21 06:00 | 6.76 | 6.74
2018-05-21 06:30 | 7.42 | 7.41
2018-05-21 07:00 | 8.28 | 8.26
2018-05-21 07:30 | 9.05 | 9.04
2018-05-21 08:00 | 8.75 | 8.74
2018-05-21 08:30 | 7.22 | 7.21
2018-05-21 09:00 | 6.03 | 6.01
2018-05-21 09:30 | 5.45 | 5.44
2018-05-21 10:00 | 4.77 | 4.76
2018-05-21 10:30 | 4.21 | 4.19
2018-05-21 11:00 | 3.92 | 3.91
2018-05-21 11:30 | 3.72 | 3.7
2018-05-21 12:00 | 3.56 | 3.55
2018-05-21 12:30 | 3.71 | 3.71
2018-05-21 13:00 | 4.24 | 4.23
2018-05-21 13:30 | 5.53 | 5.51
2018-05-21 14:00 | 5.91 | 5.9
2018-05-21 14:30 | 6.33 | 6.32
2018-05-21 15:00 | 6.51 | 6.49
2018-05-21 15:30 | 5.95 | 5.95
2018-05-21 16:00 | 7 | 7
2018-05-21 16:30 | 8.19 | 8.19
2018-05-21 17:00 | 9.57 | 9.57
2018-05-21 17:30 | 10.93 | 10.93
2018-05-21 18:00 | 12.15 | 12.14
2018-05-21 18:30 | 12.47 | 12.46
2018-05-21 19:00 | 12.65 | 12.64
2018-05-21 19:30 | 12.35 | 12.35
2018-05-21 20:00 | 11.99 | 11.98
2018-05-21 20:30 | 11.88 | 11.87
2018-05-21 21:00 | 11.09 | 11.08
2018-05-21 21:30 | 10.24 | 10.23
2018-05-21 22:00 | 9.35 | 9.35
2018-05-21 22:30 | 8.62 | 8.61
2018-05-21 23:00 | 8.25 | 8.24
2018-05-21 23:30 | 7.33 | 7.31
2018-05-22 | 6.5 | 6.47
2018-05-22 00:30 | 5.76 | 5.73
2018-05-22 01:00 | 5.32 | 5.28
2018-05-22 01:30 | 5.01 | 4.97
2018-05-22 02:00 | 4.77 | 4.72
2018-05-22 02:30 | 4.69 | 4.65
2018-05-22 03:00 | 4.64 | 4.58
2018-05-22 03:30 | 4.71 | 4.67
2018-05-22 04:00 | 4.84 | 4.79
2018-05-22 04:30 | 5.09 | 5.05
2018-05-22 05:00 | 5.67 | 5.64
2018-05-22 05:30 | 6.42 | 6.41
2018-05-22 06:00 | 7.5 | 7.49
2018-05-22 06:30 | 8.58 | 8.57
2018-05-22 07:00 | 9.39 | 9.38
2018-05-22 07:30 | 9.57 | 9.57
2018-05-22 08:00 | 8.9 | 8.89
2018-05-22 08:30 | 7.22 | 7.21
2018-05-22 09:00 | 6.03 | 6.01
2018-05-22 09:30 | 5.2 | 5.19
2018-05-22 10:00 | 4.53 | 4.51
2018-05-22 10:30 | 3.91 | 3.9
2018-05-22 11:00 | 3.68 | 3.67
2018-05-22 11:30 | 3.19 | 3.17
2018-05-22 12:00 | 3 | 2.98
2018-05-22 12:30 | 3.33 | 3.32
2018-05-22 13:00 | 3.75 | 3.75
2018-05-22 13:30 | 3.85 | 3.84
2018-05-22 14:00 | 4.21 | 4.2
2018-05-22 14:30 | 4.6 | 4.6
2018-05-22 15:00 | 5.03 | 5.03
2018-05-22 15:30 | 5.63 | 5.62
2018-05-22 16:00 | 6.83 | 6.82
2018-05-22 16:30 | 7.82 | 7.82
2018-05-22 17:00 | 9.32 | 9.32
2018-05-22 17:30 | 10.88 | 10.88
2018-05-22 18:00 | 12.33 | 12.32
2018-05-22 18:30 | 12.67 | 12.65
2018-05-22 19:00 | 12.76 | 12.75
2018-05-22 19:30 | 12.12 | 12.12
2018-05-22 20:00 | 12.48 | 12.48
2018-05-22 20:30 | 12.62 | 12.61
2018-05-22 21:00 | 11.81 | 11.81
2018-05-22 21:30 | 10.96 | 10.96
2018-05-22 22:00 | 10.07 | 10.07
2018-05-22 22:30 | 9.01 | 9.01
2018-05-22 23:00 | 8.27 | 8.26
2018-05-22 23:30 | 7.44 | 7.43
2018-05-23 | 6.64 | 6.62
2018-05-23 00:30 | 5.85 | 5.82
2018-05-23 01:00 | 5.45 | 5.42
2018-05-23 01:30 | 5.07 | 5.03
2018-05-23 02:00 | 4.8 | 4.76
2018-05-23 02:30 | 4.75 | 4.71
2018-05-23 03:00 | 4.56 | 4.52
2018-05-23 03:30 | 4.69 | 4.64
2018-05-23 04:00 | 4.84 | 4.8
2018-05-23 04:30 | 5.09 | 5.06
2018-05-23 05:00 | 5.66 | 5.63
2018-05-23 05:30 | 6.45 | 6.43
2018-05-23 06:00 | 7.22 | 7.21
2018-05-23 06:30 | 7.9 | 7.89
2018-05-23 07:00 | 8.79 | 8.78
2018-05-23 07:30 | 9.08 | 9.07
2018-05-23 08:00 | 8.39 | 8.38
2018-05-23 08:30 | 6.9 | 6.89
2018-05-23 09:00 | 6.33 | 6.31
2018-05-23 09:30 | 6.31 | 6.28
2018-05-23 10:00 | 5.62 | 5.59
2018-05-23 10:30 | 3.61 | 3.59
2018-05-23 11:00 | 3.35 | 3.32
2018-05-23 11:30 | 3.18 | 3.16
2018-05-23 12:00 | 3.43 | 3.41
2018-05-23 12:30 | 4.01 | 4
2018-05-23 13:00 | 3.54 | 3.52
2018-05-23 13:30 | 3.65 | 3.64
2018-05-23 14:00 | 4.59 | 4.58
2018-05-23 14:30 | 5.17 | 5.16
2018-05-23 15:00 | 5.91 | 5.91
2018-05-23 15:30 | 6.26 | 6.26
2018-05-23 16:00 | 7.14 | 7.14
2018-05-23 16:30 | 8.03 | 8.03
2018-05-23 17:00 | 9.38 | 9.37
2018-05-23 17:30 | 10.82 | 10.82
2018-05-23 18:00 | 11.86 | 11.85
2018-05-23 18:30 | 12.06 | 12.05
2018-05-23 19:00 | 12.54 | 12.53
2018-05-23 19:30 | 12.8 | 12.8
2018-05-23 20:00 | 13.03 | 13.03
2018-05-23 20:30 | 13.22 | 13.22
2018-05-23 21:00 | 12.06 | 12.05
2018-05-23 21:30 | 10.32 | 10.32
2018-05-23 22:00 | 9.36 | 9.35
2018-05-23 22:30 | 8.65 | 8.64
2018-05-23 23:00 | 8.25 | 8.24
2018-05-23 23:30 | 7.2 | 7.18
2018-05-24 | 6.39 | 6.37
2018-05-24 00:30 | 5.62 | 5.6
2018-05-24 01:00 | 5.27 | 5.24
2018-05-24 01:30 | 4.9 | 4.87
2018-05-24 02:00 | 4.67 | 4.63
2018-05-24 02:30 | 4.53 | 4.49
2018-05-24 03:00 | 4.46 | 4.42
2018-05-24 03:30 | 4.53 | 4.48
2018-05-24 04:00 | 4.54 | 4.49
2018-05-24 04:30 | 4.82 | 4.78
2018-05-24 05:00 | 5.38 | 5.35
2018-05-24 05:30 | 6.09 | 6.06
2018-05-24 06:00 | 6.76 | 6.75
2018-05-24 06:30 | 7.86 | 7.86
2018-05-24 07:00 | 8.8 | 8.79
2018-05-24 07:30 | 9.1 | 9.09
2018-05-24 08:00 | 8.32 | 8.31
2018-05-24 08:30 | 6.81 | 6.8
2018-05-24 09:00 | 5.86 | 5.85
2018-05-24 09:30 | 5.59 | 5.56
2018-05-24 10:00 | 5.09 | 5.06
2018-05-24 10:30 | 4.9 | 4.87
2018-05-24 11:00 | 4.74 | 4.71
2018-05-24 11:30 | 5.05 | 5.03
2018-05-24 12:00 | 5.71 | 5.69
2018-05-24 12:30 | 4.18 | 4.16
2018-05-24 13:00 | 5.48 | 5.46
2018-05-24 13:30 | 4.84 | 4.81
2018-05-24 14:00 | 5.81 | 5.79
2018-05-24 14:30 | 5.8 | 5.78
2018-05-24 15:00 | 4.77 | 4.75
2018-05-24 15:30 | 5.05 | 5.04
2018-05-24 16:00 | 6.21 | 6.19
2018-05-24 16:30 | 7.45 | 7.44
2018-05-24 17:00 | 8.79 | 8.78
2018-05-24 17:30 | 10.53 | 10.53
2018-05-24 18:00 | 11.24 | 11.23
2018-05-24 18:30 | 11.29 | 11.28
2018-05-24 19:00 | 11.52 | 11.51
2018-05-24 19:30 | 11.39 | 11.38
2018-05-24 20:00 | 11.4 | 11.39
2018-05-24 20:30 | 11.33 | 11.33
2018-05-24 21:00 | 10.94 | 10.94
2018-05-24 21:30 | 10.17 | 10.17
2018-05-24 22:00 | 9.28 | 9.27
2018-05-24 22:30 | 8.76 | 8.75
2018-05-24 23:00 | 8.17 | 8.16
2018-05-24 23:30 | 7.35 | 7.34
2018-05-25 | 6.43 | 6.4
2018-05-25 00:30 | 5.67 | 5.64
2018-05-25 01:00 | 5.23 | 5.19
2018-05-25 01:30 | 4.92 | 4.89
2018-05-25 02:00 | 4.72 | 4.68
2018-05-25 02:30 | 4.54 | 4.49
2018-05-25 03:00 | 4.39 | 4.34
2018-05-25 03:30 | 4.51 | 4.46
2018-05-25 04:00 | 4.49 | 4.45
2018-05-25 04:30 | 4.78 | 4.74
2018-05-25 05:00 | 5.14 | 5.11
2018-05-25 05:30 | 5.85 | 5.83
2018-05-25 06:00 | 6.47 | 6.46
2018-05-25 06:30 | 7.13 | 7.12
2018-05-25 07:00 | 7.8 | 7.78
2018-05-25 07:30 | 8.54 | 8.53
2018-05-25 08:00 | 8.27 | 8.25
2018-05-25 08:30 | 7.16 | 7.14
2018-05-25 09:00 | 6.21 | 6.18
2018-05-25 09:30 | 6.18 | 6.15
2018-05-25 10:00 | 5.19 | 5.17
2018-05-25 10:30 | 5.5 | 5.47
2018-05-25 11:00 | 6.09 | 6.06
2018-05-25 11:30 | 4.44 | 4.41
2018-05-25 12:00 | 3.67 | 3.65
2018-05-25 12:30 | 4.98 | 4.96
2018-05-25 13:00 | 4.77 | 4.76
2018-05-25 13:30 | 4.87 | 4.85
2018-05-25 14:00 | 4.44 | 4.43
2018-05-25 14:30 | 4.72 | 4.7
2018-05-25 15:00 | 5.79 | 5.78
2018-05-25 15:30 | 6.5 | 6.49
2018-05-25 16:00 | 7.27 | 7.25
2018-05-25 16:30 | 7.85 | 7.83
2018-05-25 17:00 | 8.77 | 8.76
2018-05-25 17:30 | 10.01 | 10
2018-05-25 18:00 | 10.66 | 10.65
2018-05-25 18:30 | 10.78 | 10.77
2018-05-25 19:00 | 10.79 | 10.78
2018-05-25 19:30 | 10.59 | 10.58
2018-05-25 20:00 | 10.64 | 10.64
2018-05-25 20:30 | 10.5 | 10.5
2018-05-25 21:00 | 10.03 | 10.03
2018-05-25 21:30 | 9.41 | 9.4
2018-05-25 22:00 | 8.76 | 8.75
2018-05-25 22:30 | 8.44 | 8.43
2018-05-25 23:00 | 8.23 | 8.22
2018-05-25 23:30 | 7.36 | 7.35
2018-05-26 | 6.5 | 6.48
2018-05-26 00:30 | 5.82 | 5.8
2018-05-26 01:00 | 5.36 | 5.33
2018-05-26 01:30 | 5.01 | 4.97
2018-05-26 02:00 | 4.69 | 4.65
2018-05-26 02:30 | 4.56 | 4.52
2018-05-26 03:00 | 4.38 | 4.34
2018-05-26 03:30 | 4.46 | 4.41
2018-05-26 04:00 | 4.31 | 4.25
2018-05-26 04:30 | 4.47 | 4.43
2018-05-26 05:00 | 4.68 | 4.64
2018-05-26 05:30 | 4.95 | 4.91
2018-05-26 06:00 | 5.07 | 5.03
2018-05-26 06:30 | 5.41 | 5.37
2018-05-26 07:00 | 5.81 | 5.75
2018-05-26 07:30 | 6.24 | 6.18
2018-05-26 08:00 | 6.19 | 6.14
2018-05-26 08:30 | 6.16 | 6.12
2018-05-26 09:00 | 5.84 | 5.81
2018-05-26 09:30 | 5.46 | 5.44
2018-05-26 10:00 | 6.17 | 6.15
2018-05-26 10:30 | 6.31 | 6.29
2018-05-26 11:00 | 6.2 | 6.18
2018-05-26 11:30 | 5.76 | 5.75
2018-05-26 12:00 | 5.7 | 5.68
2018-05-26 12:30 | 5.61 | 5.59
2018-05-26 13:00 | 5.05 | 5.03
2018-05-26 13:30 | 4.56 | 4.53
2018-05-26 14:00 | 5.23 | 5.21
2018-05-26 14:30 | 6.06 | 6.04
2018-05-26 15:00 | 6.63 | 6.61
2018-05-26 15:30 | 7.53 | 7.51
2018-05-26 16:00 | 7.72 | 7.71
2018-05-26 16:30 | 8.37 | 8.35
2018-05-26 17:00 | 9.5 | 9.49
2018-05-26 17:30 | 10.39 | 10.38
2018-05-26 18:00 | 10.8 | 10.79
2018-05-26 18:30 | 10.66 | 10.66
2018-05-26 19:00 | 10.66 | 10.65
2018-05-26 19:30 | 10.33 | 10.32
2018-05-26 20:00 | 10.2 | 10.2
2018-05-26 20:30 | 10.31 | 10.3
2018-05-26 21:00 | 9.74 | 9.74
2018-05-26 21:30 | 9.24 | 9.23
2018-05-26 22:00 | 8.59 | 8.59
2018-05-26 22:30 | 8.41 | 8.4
2018-05-26 23:00 | 8.26 | 8.25
2018-05-26 23:30 | 7.43 | 7.42
2018-05-27 | 6.51 | 6.48
2018-05-27 00:30 | 5.82 | 5.79
2018-05-27 01:00 | 5.37 | 5.34
2018-05-27 01:30 | 5.01 | 4.97
2018-05-27 02:00 | 4.62 | 4.58
2018-05-27 02:30 | 4.63 | 4.59
2018-05-27 03:00 | 4.39 | 4.34
2018-05-27 03:30 | 4.26 | 4.21
2018-05-27 04:00 | 4.29 | 4.24
2018-05-27 04:30 | 4.33 | 4.27
2018-05-27 05:00 | 4.44 | 4.39
2018-05-27 05:30 | 4.64 | 4.6
2018-05-27 06:00 | 4.71 | 4.67
2018-05-27 06:30 | 4.84 | 4.79
2018-05-27 07:00 | 5.11 | 5.03
2018-05-27 07:30 | 5.73 | 5.66
2018-05-27 08:00 | 5.5 | 5.44
2018-05-27 08:30 | 5.86 | 5.81
2018-05-27 09:00 | 6.49 | 6.45
2018-05-27 09:30 | 6.48 | 6.45
2018-05-27 10:00 | 5.9 | 5.88
2018-05-27 10:30 | 6.1 | 6.08
2018-05-27 11:00 | 5.22 | 5.2
2018-05-27 11:30 | 6.01 | 6
2018-05-27 12:00 | 7.12 | 7.1
2018-05-27 12:30 | 6.36 | 6.35
2018-05-27 13:00 | 5.63 | 5.62
2018-05-27 13:30 | 6.13 | 6.11
2018-05-27 14:00 | 5.49 | 5.47
2018-05-27 14:30 | 6.61 | 6.59
2018-05-27 15:00 | 6.81 | 6.79
2018-05-27 15:30 | 7.16 | 7.14
2018-05-27 16:00 | 7.83 | 7.81
2018-05-27 16:30 | 8.83 | 8.82
2018-05-27 17:00 | 9.72 | 9.71
2018-05-27 17:30 | 11.1 | 11.09
2018-05-27 18:00 | 11.8 | 11.79
2018-05-27 18:30 | 11.72 | 11.71
2018-05-27 19:00 | 11.55 | 11.54
2018-05-27 19:30 | 11.15 | 11.14
2018-05-27 20:00 | 11.02 | 11.01
2018-05-27 20:30 | 10.9 | 10.89
2018-05-27 21:00 | 10.37 | 10.36
2018-05-27 21:30 | 9.47 | 9.47
2018-05-27 22:00 | 8.78 | 8.77
2018-05-27 22:30 | 8.22 | 8.21
2018-05-27 23:00 | 7.94 | 7.93
2018-05-27 23:30 | 7.06 | 7.04
2018-05-28 | 6.14 | 6.11
2018-05-28 00:30 | 5.55 | 5.52
2018-05-28 01:00 | 5.05 | 5.01
2018-05-28 01:30 | 4.72 | 4.68
2018-05-28 02:00 | 4.45 | 4.4
2018-05-28 02:30 | 4.36 | 4.31
2018-05-28 03:00 | 4.22 | 4.16
2018-05-28 03:30 | 4.25 | 4.2
2018-05-28 04:00 | 4.39 | 4.34
2018-05-28 04:30 | 4.56 | 4.52
2018-05-28 05:00 | 4.79 | 4.75
2018-05-28 05:30 | 5.54 | 5.52
2018-05-28 06:00 | 6.18 | 6.16
2018-05-28 06:30 | 7.16 | 7.15
2018-05-28 07:00 | 7.94 | 7.92
2018-05-28 07:30 | 8.36 | 8.35
2018-05-28 08:00 | 7.86 | 7.85
2018-05-28 08:30 | 6.99 | 6.97
2018-05-28 09:00 | 5.97 | 5.96
2018-05-28 09:30 | 5.85 | 5.84
2018-05-28 10:00 | 4.61 | 4.61
2018-05-28 10:30 | 4.52 | 4.52
2018-05-28 11:00 | 5.76 | 5.75
2018-05-28 11:30 | 5.23 | 5.23
2018-05-28 12:00 | 5.67 | 5.67
2018-05-28 12:30 | 6.9 | 6.89
2018-05-28 13:00 | 6.4 | 6.39
2018-05-28 13:30 | 6.64 | 6.64
2018-05-28 14:00 | 7.17 | 7.16
2018-05-28 14:30 | 7.32 | 7.3
2018-05-28 15:00 | 7.79 | 7.78
2018-05-28 15:30 | 8.31 | 8.3
2018-05-28 16:00 | 8.71 | 8.7
2018-05-28 16:30 | 9.11 | 9.1
2018-05-28 17:00 | 10.52 | 10.52
2018-05-28 17:30 | 11.95 | 11.94
2018-05-28 18:00 | 12.57 | 12.56
2018-05-28 18:30 | 12.05 | 12.04
2018-05-28 19:00 | 12.27 | 12.27
2018-05-28 19:30 | 11.93 | 11.93
2018-05-28 20:00 | 11.6 | 11.59
2018-05-28 20:30 | 11.3 | 11.3
2018-05-28 21:00 | 10.47 | 10.46
2018-05-28 21:30 | 9.68 | 9.67
2018-05-28 22:00 | 8.81 | 8.81
2018-05-28 22:30 | 8.19 | 8.18
2018-05-28 23:00 | 7.8 | 7.79
2018-05-28 23:30 | 6.77 | 6.74
2018-05-29 | 5.97 | 5.95
2018-05-29 00:30 | 5.34 | 5.31
2018-05-29 01:00 | 4.98 | 4.94
2018-05-29 01:30 | 4.66 | 4.62
2018-05-29 02:00 | 4.41 | 4.37
2018-05-29 02:30 | 4.28 | 4.24
2018-05-29 03:00 | 4.17 | 4.12
2018-05-29 03:30 | 4.26 | 4.21
2018-05-29 04:00 | 4.25 | 4.19
2018-05-29 04:30 | 4.53 | 4.48
2018-05-29 05:00 | 4.85 | 4.81
2018-05-29 05:30 | 5.38 | 5.35
2018-05-29 06:00 | 5.95 | 5.94
2018-05-29 06:30 | 6.52 | 6.51
2018-05-29 07:00 | 6.98 | 6.95
2018-05-29 07:30 | 7.54 | 7.52
2018-05-29 08:00 | 7.33 | 7.3
2018-05-29 08:30 | 6.66 | 6.64
2018-05-29 09:00 | 5.6 | 5.58
2018-05-29 09:30 | 4.78 | 4.76
2018-05-29 10:00 | 4.56 | 4.55
2018-05-29 10:30 | 4.37 | 4.37
2018-05-29 11:00 | 5.28 | 5.28
2018-05-29 11:30 | 4.72 | 4.71
2018-05-29 12:00 | 4.99 | 4.98
2018-05-29 12:30 | 6.11 | 6.11
2018-05-29 13:00 | 6.7 | 6.7
2018-05-29 13:30 | 5.88 | 5.88
2018-05-29 14:00 | 5.06 | 5.05
2018-05-29 14:30 | 5.53 | 5.52
2018-05-29 15:00 | 6.31 | 6.3
2018-05-29 15:30 | 6.24 | 6.23
2018-05-29 16:00 | 7.8 | 7.79
2018-05-29 16:30 | 8.28 | 8.28
2018-05-29 17:00 | 9.71 | 9.7
2018-05-29 17:30 | 11.26 | 11.26
2018-05-29 18:00 | 11.89 | 11.88
2018-05-29 18:30 | 12.31 | 12.3
2018-05-29 19:00 | 12.49 | 12.48
2018-05-29 19:30 | 12.01 | 12
2018-05-29 20:00 | 12.05 | 12.04
2018-05-29 20:30 | 11.99 | 11.99
2018-05-29 21:00 | 11.17 | 11.17
2018-05-29 21:30 | 10.43 | 10.43
2018-05-29 22:00 | 9.52 | 9.52
2018-05-29 22:30 | 8.53 | 8.52
2018-05-29 23:00 | 8.02 | 8.01
2018-05-29 23:30 | 7.02 | 7
2018-05-30 | 6.13 | 6.1
2018-05-30 00:30 | 5.52 | 5.49
2018-05-30 01:00 | 5.07 | 5.03
2018-05-30 01:30 | 4.72 | 4.67
2018-05-30 02:00 | 4.52 | 4.47
2018-05-30 02:30 | 4.34 | 4.29
2018-05-30 03:00 | 4.27 | 4.21
2018-05-30 03:30 | 4.39 | 4.34
2018-05-30 04:00 | 4.39 | 4.34
2018-05-30 04:30 | 4.6 | 4.55
2018-05-30 05:00 | 5.06 | 5.03
2018-05-30 05:30 | 5.72 | 5.7
2018-05-30 06:00 | 6.18 | 6.16
2018-05-30 06:30 | 6.83 | 6.82
2018-05-30 07:00 | 7.47 | 7.45
2018-05-30 07:30 | 8.58 | 8.57
2018-05-30 08:00 | 8.51 | 8.5
2018-05-30 08:30 | 7.84 | 7.83
2018-05-30 09:00 | 7.1 | 7.09
2018-05-30 09:30 | 6.32 | 6.3
2018-05-30 10:00 | 5.54 | 5.51
2018-05-30 10:30 | 3.9 | 3.86
2018-05-30 11:00 | 3.42 | 3.39
2018-05-30 11:30 | 3.18 | 3.15
2018-05-30 12:00 | 3.13 | 3.11
2018-05-30 12:30 | 3.13 | 3.11
2018-05-30 13:00 | 3.21 | 3.19
2018-05-30 13:30 | 3.52 | 3.5
2018-05-30 14:00 | 4.41 | 4.4
2018-05-30 14:30 | 5.57 | 5.57
2018-05-30 15:00 | 5.15 | 5.15
2018-05-30 15:30 | 5.9 | 5.9
2018-05-30 16:00 | 7.04 | 7.03
2018-05-30 16:30 | 8.47 | 8.47
2018-05-30 17:00 | 9.31 | 9.3
2018-05-30 17:30 | 10.66 | 10.66
2018-05-30 18:00 | 11.7 | 11.68
2018-05-30 18:30 | 11.95 | 11.93
2018-05-30 19:00 | 12.05 | 12.04
2018-05-30 19:30 | 12.02 | 12.01
2018-05-30 20:00 | 11.89 | 11.89
2018-05-30 20:30 | 11.74 | 11.74
2018-05-30 21:00 | 11.21 | 11.21
2018-05-30 21:30 | 10.27 | 10.27
2018-05-30 22:00 | 9.35 | 9.34
2018-05-30 22:30 | 8.46 | 8.45
2018-05-30 23:00 | 7.96 | 7.95
2018-05-30 23:30 | 7.05 | 7.03
2018-05-31 | 6.2 | 6.18
2018-05-31 00:30 | 5.61 | 5.58
2018-05-31 01:00 | 5.26 | 5.22
2018-05-31 01:30 | 4.91 | 4.87
2018-05-31 02:00 | 4.71 | 4.67
2018-05-31 02:30 | 4.66 | 4.61
2018-05-31 03:00 | 4.6 | 4.55
2018-05-31 03:30 | 4.72 | 4.67
2018-05-31 04:00 | 4.85 | 4.8
2018-05-31 04:30 | 5.15 | 5.11
2018-05-31 05:00 | 5.72 | 5.69
2018-05-31 05:30 | 6.61 | 6.6
2018-05-31 06:00 | 7.3 | 7.29
2018-05-31 06:30 | 8.32 | 8.31
2018-05-31 07:00 | 9.53 | 9.52
2018-05-31 07:30 | 10.18 | 10.18
2018-05-31 08:00 | 9.44 | 9.43
2018-05-31 08:30 | 7.68 | 7.68
2018-05-31 09:00 | 6.53 | 6.52
2018-05-31 09:30 | 5.74 | 5.73
2018-05-31 10:00 | 5.14 | 5.13
2018-05-31 10:30 | 4.4 | 4.38
2018-05-31 11:00 | 3.97 | 3.95
2018-05-31 11:30 | 3.69 | 3.67
2018-05-31 12:00 | 3.44 | 3.41
2018-05-31 12:30 | 3.33 | 3.31
2018-05-31 13:00 | 3.56 | 3.54
2018-05-31 13:30 | 3.65 | 3.63
2018-05-31 14:00 | 4.07 | 4.06
2018-05-31 14:30 | 4.45 | 4.44
2018-05-31 15:00 | 4.74 | 4.73
2018-05-31 15:30 | 5.65 | 5.64
2018-05-31 16:00 | 6.58 | 6.57
2018-05-31 16:30 | 7.86 | 7.86
2018-05-31 17:00 | 9.54 | 9.54
2018-05-31 17:30 | 11.35 | 11.35
2018-05-31 18:00 | 12.41 | 12.4
2018-05-31 18:30 | 12.74 | 12.73
2018-05-31 19:00 | 13.11 | 13.1
2018-05-31 19:30 | 13 | 12.99
2018-05-31 20:00 | 12.97 | 12.97
2018-05-31 20:30 | 12.98 | 12.97
2018-05-31 21:00 | 12.39 | 12.39
2018-05-31 21:30 | 11.46 | 11.46
2018-05-31 22:00 | 10.37 | 10.36
2018-05-31 22:30 | 9.67 | 9.66
2018-05-31 23:00 | 9.22 | 9.22
2018-05-31 23:30 | 7.97 | 7.96
2018-06-01 | 7.04 | 7.02
2018-06-01 00:30 | 6.29 | 6.27
2018-06-01 01:00 | 5.82 | 5.79
2018-06-01 01:30 | 5.49 | 5.46
2018-06-01 02:00 | 5.23 | 5.2
2018-06-01 02:30 | 5.05 | 5.01
2018-06-01 03:00 | 5.02 | 4.98
2018-06-01 03:30 | 5.17 | 5.12
2018-06-01 04:00 | 5.14 | 5.1
2018-06-01 04:30 | 5.49 | 5.46
2018-06-01 05:00 | 6.2 | 6.18
2018-06-01 05:30 | 7.01 | 6.99
2018-06-01 06:00 | 7.84 | 7.83
2018-06-01 06:30 | 8.7 | 8.69
2018-06-01 07:00 | 9.7 | 9.7
2018-06-01 07:30 | 10.02 | 10.01
2018-06-01 08:00 | 9.37 | 9.37
2018-06-01 08:30 | 7.89 | 7.88
2018-06-01 09:00 | 6.44 | 6.43
2018-06-01 09:30 | 5.35 | 5.33
2018-06-01 10:00 | 4.68 | 4.66
2018-06-01 10:30 | 4.08 | 4.06
2018-06-01 11:00 | 3.7 | 3.68
2018-06-01 11:30 | 3.45 | 3.43
2018-06-01 12:00 | 3.54 | 3.51
2018-06-01 12:30 | 3.48 | 3.46
2018-06-01 13:00 | 3.6 | 3.58
2018-06-01 13:30 | 3.6 | 3.57
2018-06-01 14:00 | 3.89 | 3.87
2018-06-01 14:30 | 4.25 | 4.23
2018-06-01 15:00 | 4.43 | 4.41
2018-06-01 15:30 | 5.01 | 4.99
2018-06-01 16:00 | 6.27 | 6.26
2018-06-01 16:30 | 7.39 | 7.38
2018-06-01 17:00 | 8.71 | 8.7
2018-06-01 17:30 | 10.21 | 10.2
2018-06-01 18:00 | 11.15 | 11.14
2018-06-01 18:30 | 11.48 | 11.47
2018-06-01 19:00 | 11.76 | 11.75
2018-06-01 19:30 | 11.8 | 11.79
2018-06-01 20:00 | 12.03 | 12.03
2018-06-01 20:30 | 12.09 | 12.09
2018-06-01 21:00 | 11.7 | 11.7
2018-06-01 21:30 | 11.12 | 11.12
2018-06-01 22:00 | 10.33 | 10.32
2018-06-01 22:30 | 9.97 | 9.96
2018-06-01 23:00 | 9.79 | 9.78
2018-06-01 23:30 | 8.69 | 8.68
2018-06-02 | 7.64 | 7.63
2018-06-02 00:30 | 6.8 | 6.78
2018-06-02 01:00 | 6.46 | 6.44
2018-06-02 01:30 | 6.01 | 5.98
2018-06-02 02:00 | 5.56 | 5.53
2018-06-02 02:30 | 5.34 | 5.31
2018-06-02 03:00 | 5.21 | 5.18
2018-06-02 03:30 | 5.21 | 5.17
2018-06-02 04:00 | 5.24 | 5.2
2018-06-02 04:30 | 5.35 | 5.32
2018-06-02 05:00 | 5.61 | 5.58
2018-06-02 05:30 | 5.8 | 5.77
2018-06-02 06:00 | 6.14 | 6.12
2018-06-02 06:30 | 6.61 | 6.59
2018-06-02 07:00 | 7.45 | 7.42
2018-06-02 07:30 | 8.13 | 8.11
2018-06-02 08:00 | 8.27 | 8.25
2018-06-02 08:30 | 8.22 | 8.2
2018-06-02 09:00 | 7.96 | 7.94
2018-06-02 09:30 | 7.21 | 7.2
2018-06-02 10:00 | 6.36 | 6.34
2018-06-02 10:30 | 5.58 | 5.56
2018-06-02 11:00 | 4.89 | 4.87
2018-06-02 11:30 | 4.58 | 4.56
2018-06-02 12:00 | 4.38 | 4.36
2018-06-02 12:30 | 4.14 | 4.11
2018-06-02 13:00 | 4.17 | 4.15
2018-06-02 13:30 | 4.24 | 4.21
2018-06-02 14:00 | 4.55 | 4.52
2018-06-02 14:30 | 4.84 | 4.81
2018-06-02 15:00 | 5.35 | 5.33
2018-06-02 15:30 | 5.8 | 5.78
2018-06-02 16:00 | 6.57 | 6.55
2018-06-02 16:30 | 7.65 | 7.63
2018-06-02 17:00 | 8.91 | 8.9
2018-06-02 17:30 | 10.2 | 10.19
2018-06-02 18:00 | 11.13 | 11.12
2018-06-02 18:30 | 11.3 | 11.29
2018-06-02 19:00 | 11.4 | 11.4
2018-06-02 19:30 | 11.3 | 11.3
2018-06-02 20:00 | 11.36 | 11.35
2018-06-02 20:30 | 11.36 | 11.36
2018-06-02 21:00 | 10.87 | 10.86
2018-06-02 21:30 | 10.15 | 10.14
2018-06-02 22:00 | 9.77 | 9.76
2018-06-02 22:30 | 9.48 | 9.48
2018-06-02 23:00 | 9.39 | 9.39
2018-06-02 23:30 | 8.49 | 8.48
2018-06-03 | 7.43 | 7.42
2018-06-03 00:30 | 6.75 | 6.73
2018-06-03 01:00 | 6.33 | 6.3
2018-06-03 01:30 | 5.95 | 5.92
2018-06-03 02:00 | 5.52 | 5.49
2018-06-03 02:30 | 5.34 | 5.3
2018-06-03 03:00 | 5.21 | 5.17
2018-06-03 03:30 | 5.21 | 5.17
2018-06-03 04:00 | 5.04 | 5.01
2018-06-03 04:30 | 5.15 | 5.11
2018-06-03 05:00 | 5.23 | 5.19
2018-06-03 05:30 | 5.37 | 5.34
2018-06-03 06:00 | 5.6 | 5.58
2018-06-03 06:30 | 5.96 | 5.93
2018-06-03 07:00 | 6.4 | 6.35
2018-06-03 07:30 | 6.89 | 6.85
2018-06-03 08:00 | 7.23 | 7.2
2018-06-03 08:30 | 7.43 | 7.4
2018-06-03 09:00 | 7.35 | 7.33
2018-06-03 09:30 | 6.8 | 6.78
2018-06-03 10:00 | 6.1 | 6.08
2018-06-03 10:30 | 5.46 | 5.44
2018-06-03 11:00 | 5.2 | 5.18
2018-06-03 11:30 | 4.91 | 4.89
2018-06-03 12:00 | 4.95 | 4.94
2018-06-03 12:30 | 4.79 | 4.77
2018-06-03 13:00 | 4.7 | 4.68
2018-06-03 13:30 | 4.78 | 4.76
2018-06-03 14:00 | 4.95 | 4.92
2018-06-03 14:30 | 5.47 | 5.45
2018-06-03 15:00 | 5.96 | 5.94
2018-06-03 15:30 | 6.84 | 6.82
2018-06-03 16:00 | 7.62 | 7.61
2018-06-03 16:30 | 8.73 | 8.71
2018-06-03 17:00 | 9.84 | 9.82
2018-06-03 17:30 | 11.25 | 11.24
2018-06-03 18:00 | 11.93 | 11.92
2018-06-03 18:30 | 11.66 | 11.65
2018-06-03 19:00 | 11.58 | 11.57
2018-06-03 19:30 | 11.17 | 11.16
2018-06-03 20:00 | 10.97 | 10.96
2018-06-03 20:30 | 10.93 | 10.93
2018-06-03 21:00 | 10.16 | 10.15
2018-06-03 21:30 | 9.53 | 9.53
2018-06-03 22:00 | 8.98 | 8.97
2018-06-03 22:30 | 8.48 | 8.47
2018-06-03 23:00 | 8.17 | 8.16
2018-06-03 23:30 | 7.18 | 7.16
2018-06-04 | 6.36 | 6.34
2018-06-04 00:30 | 5.71 | 5.68
2018-06-04 01:00 | 5.39 | 5.36
2018-06-04 01:30 | 5.06 | 5.02
2018-06-04 02:00 | 4.83 | 4.79
2018-06-04 02:30 | 4.68 | 4.63
2018-06-04 03:00 | 4.62 | 4.57
2018-06-04 03:30 | 4.65 | 4.6
2018-06-04 04:00 | 4.82 | 4.77
2018-06-04 04:30 | 5.07 | 5.03
2018-06-04 05:00 | 5.57 | 5.53
2018-06-04 05:30 | 6.39 | 6.37
2018-06-04 06:00 | 7.27 | 7.26
2018-06-04 06:30 | 8.24 | 8.23
2018-06-04 07:00 | 9.51 | 9.51
2018-06-04 07:30 | 10.08 | 10.08
2018-06-04 08:00 | 9.28 | 9.28
2018-06-04 08:30 | 7.92 | 7.92
2018-06-04 09:00 | 6.56 | 6.56
2018-06-04 09:30 | 5.78 | 5.77
2018-06-04 10:00 | 5.35 | 5.34
2018-06-04 10:30 | 4.78 | 4.77
2018-06-04 11:00 | 4.27 | 4.26
2018-06-04 11:30 | 4.33 | 4.32
2018-06-04 12:00 | 4.8 | 4.79
2018-06-04 12:30 | 4.9 | 4.9
2018-06-04 13:00 | 4.62 | 4.62
2018-06-04 13:30 | 4.66 | 4.65
2018-06-04 14:00 | 4.87 | 4.86
2018-06-04 14:30 | 5.44 | 5.44
2018-06-04 15:00 | 5.22 | 5.22
2018-06-04 15:30 | 6.02 | 6.01
2018-06-04 16:00 | 7.19 | 7.18
2018-06-04 16:30 | 8.53 | 8.53
2018-06-04 17:00 | 10.04 | 10.04
2018-06-04 17:30 | 11.8 | 11.79
2018-06-04 18:00 | 12.98 | 12.97
2018-06-04 18:30 | 13.06 | 13.05
2018-06-04 19:00 | 12.94 | 12.93
2018-06-04 19:30 | 12.85 | 12.84
2018-06-04 20:00 | 12.75 | 12.75
2018-06-04 20:30 | 12.29 | 12.29
2018-06-04 21:00 | 11.68 | 11.67
2018-06-04 21:30 | 11.16 | 11.16
2018-06-04 22:00 | 9.91 | 9.91
2018-06-04 22:30 | 8.9 | 8.9
2018-06-04 23:00 | 8.55 | 8.54
2018-06-04 23:30 | 7.52 | 7.51
2018-06-05 | 6.61 | 6.58
2018-06-05 00:30 | 5.78 | 5.75
2018-06-05 01:00 | 5.42 | 5.38
2018-06-05 01:30 | 5.07 | 5.02
2018-06-05 02:00 | 4.87 | 4.83
2018-06-05 02:30 | 4.69 | 4.64
2018-06-05 03:00 | 4.64 | 4.59
2018-06-05 03:30 | 4.81 | 4.77
2018-06-05 04:00 | 4.91 | 4.86
2018-06-05 04:30 | 5.14 | 5.1
2018-06-05 05:00 | 5.75 | 5.72
2018-06-05 05:30 | 6.56 | 6.55
2018-06-05 06:00 | 7.78 | 7.78
2018-06-05 06:30 | 8.86 | 8.86
2018-06-05 07:00 | 9.8 | 9.8
2018-06-05 07:30 | 10.12 | 10.12
2018-06-05 08:00 | 9.03 | 9.02
2018-06-05 08:30 | 7.69 | 7.69
2018-06-05 09:00 | 6.1 | 6.08
2018-06-05 09:30 | 5.57 | 5.56
2018-06-05 10:00 | 5 | 4.99
2018-06-05 10:30 | 4.5 | 4.49
2018-06-05 11:00 | 4.1 | 4.09
2018-06-05 11:30 | 3.94 | 3.92
2018-06-05 12:00 | 3.88 | 3.87
2018-06-05 12:30 | 4.35 | 4.34
2018-06-05 13:00 | 4.49 | 4.48
2018-06-05 13:30 | 5.82 | 5.81
2018-06-05 14:00 | 5.29 | 5.29
2018-06-05 14:30 | 6.18 | 6.17
2018-06-05 15:00 | 6.92 | 6.92
2018-06-05 15:30 | 7.17 | 7.16
2018-06-05 16:00 | 7.3 | 7.29
2018-06-05 16:30 | 8.79 | 8.78
2018-06-05 17:00 | 10.47 | 10.47
2018-06-05 17:30 | 12.13 | 12.12
2018-06-05 18:00 | 13.09 | 13.07
2018-06-05 18:30 | 13.14 | 13.13
2018-06-05 19:00 | 13.45 | 13.43
2018-06-05 19:30 | 13.3 | 13.28
2018-06-05 20:00 | 13.11 | 13.1
2018-06-05 20:30 | 12.94 | 12.94
2018-06-05 21:00 | 12.39 | 12.39
2018-06-05 21:30 | 11.62 | 11.62
2018-06-05 22:00 | 10.61 | 10.61
2018-06-05 22:30 | 9.57 | 9.56
2018-06-05 23:00 | 8.84 | 8.83
2018-06-05 23:30 | 7.74 | 7.72
2018-06-06 | 6.83 | 6.81
2018-06-06 00:30 | 6.16 | 6.14
2018-06-06 01:00 | 5.7 | 5.67
2018-06-06 01:30 | 5.38 | 5.35
2018-06-06 02:00 | 5.07 | 5.03
2018-06-06 02:30 | 4.94 | 4.9
2018-06-06 03:00 | 4.88 | 4.84
2018-06-06 03:30 | 4.96 | 4.92
2018-06-06 04:00 | 5.08 | 5.04
2018-06-06 04:30 | 5.42 | 5.39
2018-06-06 05:00 | 5.9 | 5.87
2018-06-06 05:30 | 6.78 | 6.77
2018-06-06 06:00 | 7.61 | 7.6
2018-06-06 06:30 | 8.52 | 8.51
2018-06-06 07:00 | 9.51 | 9.5
2018-06-06 07:30 | 10.03 | 10.02
2018-06-06 08:00 | 9.43 | 9.42
2018-06-06 08:30 | 8.58 | 8.56
2018-06-06 09:00 | 7.2 | 7.18
2018-06-06 09:30 | 5.84 | 5.83
2018-06-06 10:00 | 5.21 | 5.2
2018-06-06 10:30 | 4.6 | 4.59
2018-06-06 11:00 | 4.19 | 4.18
2018-06-06 11:30 | 3.91 | 3.9
2018-06-06 12:00 | 3.84 | 3.83
2018-06-06 12:30 | 4.12 | 4.11
2018-06-06 13:00 | 3.99 | 3.97
2018-06-06 13:30 | 5.11 | 5.09
2018-06-06 14:00 | 6.52 | 6.5
2018-06-06 14:30 | 4.95 | 4.92
2018-06-06 15:00 | 5.29 | 5.27
2018-06-06 15:30 | 6.84 | 6.83
2018-06-06 16:00 | 7.23 | 7.21
2018-06-06 16:30 | 7.83 | 7.82
2018-06-06 17:00 | 9.23 | 9.22
2018-06-06 17:30 | 10.98 | 10.97
2018-06-06 18:00 | 12.03 | 12.03
2018-06-06 18:30 | 12.22 | 12.22
2018-06-06 19:00 | 12.41 | 12.41
2018-06-06 19:30 | 12.2 | 12.19
2018-06-06 20:00 | 12.02 | 12.01
2018-06-06 20:30 | 11.99 | 11.99
2018-06-06 21:00 | 11.26 | 11.25
2018-06-06 21:30 | 10.44 | 10.43
2018-06-06 22:00 | 9.63 | 9.62
2018-06-06 22:30 | 9.1 | 9.09
2018-06-06 23:00 | 8.87 | 8.87
2018-06-06 23:30 | 7.85 | 7.83
2018-06-07 | 6.87 | 6.85
2018-06-07 00:30 | 6.09 | 6.06
2018-06-07 01:00 | 5.56 | 5.52
2018-06-07 01:30 | 5.11 | 5.07
2018-06-07 02:00 | 4.73 | 4.69
2018-06-07 02:30 | 4.58 | 4.53
2018-06-07 03:00 | 4.58 | 4.53
2018-06-07 03:30 | 4.64 | 4.6
2018-06-07 04:00 | 4.62 | 4.58
2018-06-07 04:30 | 4.85 | 4.8
2018-06-07 05:00 | 5.36 | 5.33
2018-06-07 05:30 | 6.01 | 5.99
2018-06-07 06:00 | 6.56 | 6.55
2018-06-07 06:30 | 7.61 | 7.61
2018-06-07 07:00 | 8.51 | 8.51
2018-06-07 07:30 | 9.3 | 9.29
2018-06-07 08:00 | 9.19 | 9.19
2018-06-07 08:30 | 8.74 | 8.74
2018-06-07 09:00 | 8.21 | 8.2
2018-06-07 09:30 | 8.04 | 8.03
2018-06-07 10:00 | 7.63 | 7.62
2018-06-07 10:30 | 6.34 | 6.33
2018-06-07 11:00 | 6.38 | 6.36
2018-06-07 11:30 | 4.89 | 4.88
2018-06-07 12:00 | 4.5 | 4.49
2018-06-07 12:30 | 5.03 | 5.02
2018-06-07 13:00 | 5.95 | 5.94
2018-06-07 13:30 | 7.57 | 7.56
2018-06-07 14:00 | 6.38 | 6.37
2018-06-07 14:30 | 6.33 | 6.32
2018-06-07 15:00 | 6.15 | 6.13
2018-06-07 15:30 | 6.51 | 6.5
2018-06-07 16:00 | 7.8 | 7.79
2018-06-07 16:30 | 8.76 | 8.75
2018-06-07 17:00 | 10.11 | 10.11
2018-06-07 17:30 | 11.69 | 11.69
2018-06-07 18:00 | 13.05 | 13.04
2018-06-07 18:30 | 13.16 | 13.15
2018-06-07 19:00 | 13.59 | 13.58
2018-06-07 19:30 | 13.31 | 13.3
2018-06-07 20:00 | 13.3 | 13.29
2018-06-07 20:30 | 13.33 | 13.32
2018-06-07 21:00 | 12.32 | 12.32
2018-06-07 21:30 | 11.22 | 11.22
2018-06-07 22:00 | 10.04 | 10.03
2018-06-07 22:30 | 9.29 | 9.29
2018-06-07 23:00 | 8.88 | 8.87
2018-06-07 23:30 | 7.84 | 7.83
2018-06-08 | 6.77 | 6.75
2018-06-08 00:30 | 5.89 | 5.86
2018-06-08 01:00 | 5.47 | 5.44
2018-06-08 01:30 | 5.16 | 5.12
2018-06-08 02:00 | 4.85 | 4.81
2018-06-08 02:30 | 4.62 | 4.58
2018-06-08 03:00 | 4.63 | 4.58
2018-06-08 03:30 | 4.71 | 4.67
2018-06-08 04:00 | 4.76 | 4.72
2018-06-08 04:30 | 4.95 | 4.91
2018-06-08 05:00 | 5.36 | 5.33
2018-06-08 05:30 | 6.12 | 6.11
2018-06-08 06:00 | 6.61 | 6.6
2018-06-08 06:30 | 7.33 | 7.32
2018-06-08 07:00 | 8.17 | 8.16
2018-06-08 07:30 | 8.47 | 8.46
2018-06-08 08:00 | 8.11 | 8.09
2018-06-08 08:30 | 7.1 | 7.08
2018-06-08 09:00 | 6.58 | 6.56
2018-06-08 09:30 | 6.67 | 6.65
2018-06-08 10:00 | 5.94 | 5.92
2018-06-08 10:30 | 5.27 | 5.24
2018-06-08 11:00 | 6.21 | 6.19
2018-06-08 11:30 | 6.48 | 6.46
2018-06-08 12:00 | 5.78 | 5.76
2018-06-08 12:30 | 6.13 | 6.11
2018-06-08 13:00 | 5.26 | 5.24
2018-06-08 13:30 | 5.06 | 5.03
2018-06-08 14:00 | 5.01 | 4.99
2018-06-08 14:30 | 4.21 | 4.19
2018-06-08 15:00 | 6.23 | 6.21
2018-06-08 15:30 | 7.03 | 7.02
2018-06-08 16:00 | 7.55 | 7.53
2018-06-08 16:30 | 9.02 | 9.01
2018-06-08 17:00 | 10.16 | 10.15
2018-06-08 17:30 | 11.08 | 11.07
2018-06-08 18:00 | 11.57 | 11.56
2018-06-08 18:30 | 11.62 | 11.61
2018-06-08 19:00 | 11.72 | 11.71
2018-06-08 19:30 | 11.46 | 11.44
2018-06-08 20:00 | 11.62 | 11.61
2018-06-08 20:30 | 11.52 | 11.51
2018-06-08 21:00 | 10.97 | 10.96
2018-06-08 21:30 | 10.21 | 10.2
2018-06-08 22:00 | 9.57 | 9.56
2018-06-08 22:30 | 9.11 | 9.1
2018-06-08 23:00 | 8.8 | 8.79
2018-06-08 23:30 | 7.92 | 7.91
2018-06-09 | 6.97 | 6.95
2018-06-09 00:30 | 6.2 | 6.18
2018-06-09 01:00 | 5.72 | 5.69
2018-06-09 01:30 | 5.32 | 5.29
2018-06-09 02:00 | 4.96 | 4.92
2018-06-09 02:30 | 4.69 | 4.64
2018-06-09 03:00 | 4.58 | 4.53
2018-06-09 03:30 | 4.53 | 4.48
2018-06-09 04:00 | 4.66 | 4.62
2018-06-09 04:30 | 4.62 | 4.57
2018-06-09 05:00 | 4.75 | 4.71
2018-06-09 05:30 | 4.89 | 4.85
2018-06-09 06:00 | 5.07 | 5.04
2018-06-09 06:30 | 5.45 | 5.42
2018-06-09 07:00 | 5.81 | 5.76
2018-06-09 07:30 | 6.39 | 6.34
2018-06-09 08:00 | 6.85 | 6.81
2018-06-09 08:30 | 7.08 | 7.05
2018-06-09 09:00 | 7.4 | 7.38
2018-06-09 09:30 | 6.33 | 6.3
2018-06-09 10:00 | 6.78 | 6.76
2018-06-09 10:30 | 7.14 | 7.13
2018-06-09 11:00 | 6.46 | 6.44
2018-06-09 11:30 | 6.43 | 6.41
2018-06-09 12:00 | 6.47 | 6.45
2018-06-09 12:30 | 4.66 | 4.64
2018-06-09 13:00 | 5 | 4.98
2018-06-09 13:30 | 5.53 | 5.51
2018-06-09 14:00 | 5.79 | 5.77
2018-06-09 14:30 | 5.71 | 5.69
2018-06-09 15:00 | 5.88 | 5.86
2018-06-09 15:30 | 6.22 | 6.2
2018-06-09 16:00 | 6.85 | 6.83
2018-06-09 16:30 | 7.8 | 7.78
2018-06-09 17:00 | 8.91 | 8.9
2018-06-09 17:30 | 10.18 | 10.17
2018-06-09 18:00 | 10.93 | 10.92
2018-06-09 18:30 | 10.79 | 10.79
2018-06-09 19:00 | 10.64 | 10.63
2018-06-09 19:30 | 10.4 | 10.39
2018-06-09 20:00 | 10.38 | 10.37
2018-06-09 20:30 | 10.35 | 10.34
2018-06-09 21:00 | 9.77 | 9.76
2018-06-09 21:30 | 9.2 | 9.2
2018-06-09 22:00 | 8.73 | 8.72
2018-06-09 22:30 | 8.51 | 8.51
2018-06-09 23:00 | 8.35 | 8.34
2018-06-09 23:30 | 7.54 | 7.52
2018-06-10 | 6.76 | 6.74
2018-06-10 00:30 | 5.96 | 5.93
2018-06-10 01:00 | 5.61 | 5.58
2018-06-10 01:30 | 5.27 | 5.24
2018-06-10 02:00 | 4.78 | 4.74
2018-06-10 02:30 | 4.59 | 4.55
2018-06-10 03:00 | 4.49 | 4.44
2018-06-10 03:30 | 4.33 | 4.28
2018-06-10 04:00 | 4.3 | 4.25
2018-06-10 04:30 | 4.41 | 4.36
2018-06-10 05:00 | 4.39 | 4.35
2018-06-10 05:30 | 4.54 | 4.5
2018-06-10 06:00 | 4.67 | 4.63
2018-06-10 06:30 | 4.9 | 4.86
2018-06-10 07:00 | 5.17 | 5.09
2018-06-10 07:30 | 5.67 | 5.6
2018-06-10 08:00 | 6.29 | 6.24
2018-06-10 08:30 | 6.07 | 6.03
2018-06-10 09:00 | 6.13 | 6.1
2018-06-10 09:30 | 6 | 5.97
2018-06-10 10:00 | 5.71 | 5.68
2018-06-10 10:30 | 5.35 | 5.33
2018-06-10 11:00 | 6.08 | 6.06
2018-06-10 11:30 | 5.12 | 5.1
2018-06-10 12:00 | 5.07 | 5.05
2018-06-10 12:30 | 5.36 | 5.34
2018-06-10 13:00 | 4.63 | 4.6
2018-06-10 13:30 | 4.98 | 4.95
2018-06-10 14:00 | 6.85 | 6.84
2018-06-10 14:30 | 7.24 | 7.22
2018-06-10 15:00 | 7.06 | 7.04
2018-06-10 15:30 | 6.65 | 6.63
2018-06-10 16:00 | 7.87 | 7.85
2018-06-10 16:30 | 8.82 | 8.81
2018-06-10 17:00 | 10.36 | 10.35
2018-06-10 17:30 | 11.5 | 11.49
2018-06-10 18:00 | 11.8 | 11.79
2018-06-10 18:30 | 11.76 | 11.75
2018-06-10 19:00 | 11.54 | 11.53
2018-06-10 19:30 | 11.24 | 11.23
2018-06-10 20:00 | 11.08 | 11.07
2018-06-10 20:30 | 11.08 | 11.08
2018-06-10 21:00 | 10.44 | 10.44
2018-06-10 21:30 | 9.67 | 9.66
2018-06-10 22:00 | 8.98 | 8.97
2018-06-10 22:30 | 8.38 | 8.37
2018-06-10 23:00 | 8.17 | 8.16
2018-06-10 23:30 | 7.34 | 7.32
2018-06-11 | 6.44 | 6.41
2018-06-11 00:30 | 5.67 | 5.63
2018-06-11 01:00 | 5.45 | 5.41
2018-06-11 01:30 | 5.01 | 4.97
2018-06-11 02:00 | 4.62 | 4.57
2018-06-11 02:30 | 4.52 | 4.47
2018-06-11 03:00 | 4.46 | 4.41
2018-06-11 03:30 | 4.54 | 4.49
2018-06-11 04:00 | 4.64 | 4.59
2018-06-11 04:30 | 4.93 | 4.89
2018-06-11 05:00 | 6.74 | 6.7
2018-06-11 05:30 | 7.84 | 7.81
2018-06-11 06:00 | 8.83 | 8.81
2018-06-11 06:30 | 9.59 | 9.58
2018-06-11 07:00 | 9.22 | 9.21
2018-06-11 07:30 | 9.69 | 9.69
2018-06-11 08:00 | 8.84 | 8.83
2018-06-11 08:30 | 7.66 | 7.65
2018-06-11 09:00 | 6.38 | 6.37
2018-06-11 09:30 | 5.83 | 5.82
2018-06-11 10:00 | 5.18 | 5.16
2018-06-11 10:30 | 4.64 | 4.62
2018-06-11 11:00 | 4.39 | 4.38
2018-06-11 11:30 | 4.12 | 4.11
2018-06-11 12:00 | 3.98 | 3.97
2018-06-11 12:30 | 4.06 | 4.05
2018-06-11 13:00 | 4 | 3.99
2018-06-11 13:30 | 3.81 | 3.79
2018-06-11 14:00 | 3.94 | 3.91
2018-06-11 14:30 | 4.57 | 4.54
2018-06-11 15:00 | 4.4 | 4.36
2018-06-11 15:30 | 5.58 | 5.55
2018-06-11 16:00 | 6.91 | 6.89
2018-06-11 16:30 | 8.32 | 8.31
2018-06-11 17:00 | 9.69 | 9.68
2018-06-11 17:30 | 11.39 | 11.39
2018-06-11 18:00 | 12.35 | 12.34
2018-06-11 18:30 | 12.41 | 12.4
2018-06-11 19:00 | 12.57 | 12.56
2018-06-11 19:30 | 12.51 | 12.51
2018-06-11 20:00 | 12.42 | 12.41
2018-06-11 20:30 | 12.33 | 12.32
2018-06-11 21:00 | 11.65 | 11.64
2018-06-11 21:30 | 10.74 | 10.73
2018-06-11 22:00 | 9.87 | 9.86
2018-06-11 22:30 | 9.31 | 9.31
2018-06-11 23:00 | 8.87 | 8.86
2018-06-11 23:30 | 7.76 | 7.75
2018-06-12 | 6.9 | 6.88
2018-06-12 00:30 | 6.05 | 6.03
2018-06-12 01:00 | 5.73 | 5.7
2018-06-12 01:30 | 5.41 | 5.37
2018-06-12 02:00 | 5.08 | 5.04
2018-06-12 02:30 | 4.91 | 4.87
2018-06-12 03:00 | 4.88 | 4.84
2018-06-12 03:30 | 5.01 | 4.97
2018-06-12 04:00 | 5.11 | 5.06
2018-06-12 04:30 | 5.34 | 5.3
2018-06-12 05:00 | 5.93 | 5.9
2018-06-12 05:30 | 6.72 | 6.71
2018-06-12 06:00 | 8.02 | 8.02
2018-06-12 06:30 | 9.14 | 9.14
2018-06-12 07:00 | 10.11 | 10.11
2018-06-12 07:30 | 10.64 | 10.64
2018-06-12 08:00 | 10.05 | 10.05
2018-06-12 08:30 | 8.42 | 8.42
2018-06-12 09:00 | 7.29 | 7.28
2018-06-12 09:30 | 6.87 | 6.87
2018-06-12 10:00 | 6 | 5.99
2018-06-12 10:30 | 5.01 | 5
2018-06-12 11:00 | 4.65 | 4.64
2018-06-12 11:30 | 4.43 | 4.42
2018-06-12 12:00 | 4.2 | 4.19
2018-06-12 12:30 | 4.18 | 4.17
2018-06-12 13:00 | 3.87 | 3.85
2018-06-12 13:30 | 4.53 | 4.51
2018-06-12 14:00 | 6.89 | 6.86
2018-06-12 14:30 | 7.05 | 7.02
2018-06-12 15:00 | 6.23 | 6.19
2018-06-12 15:30 | 7.21 | 7.18
2018-06-12 16:00 | 8.18 | 8.16
2018-06-12 16:30 | 9.49 | 9.47
2018-06-12 17:00 | 11.07 | 11.06
2018-06-12 17:30 | 12.64 | 12.63
2018-06-12 18:00 | 13.62 | 13.62
2018-06-12 18:30 | 13.84 | 13.84
2018-06-12 19:00 | 14.14 | 14.14
2018-06-12 19:30 | 13.77 | 13.77
2018-06-12 20:00 | 12.88 | 12.88
2018-06-12 20:30 | 12.79 | 12.78
2018-06-12 21:00 | 13.3 | 13.3
2018-06-12 21:30 | 12.56 | 12.56
2018-06-12 22:00 | 11.6 | 11.6
2018-06-12 22:30 | 10.81 | 10.8
2018-06-12 23:00 | 10.07 | 10.06
2018-06-12 23:30 | 8.94 | 8.93
2018-06-13 | 7.95 | 7.92
2018-06-13 00:30 | 7.2 | 7.17
2018-06-13 01:00 | 6.78 | 6.75
2018-06-13 01:30 | 6.52 | 6.48
2018-06-13 02:00 | 6.26 | 6.22
2018-06-13 02:30 | 6.07 | 6.02
2018-06-13 03:00 | 6.07 | 6.02
2018-06-13 03:30 | 6.14 | 6.1
2018-06-13 04:00 | 6.21 | 6.17
2018-06-13 04:30 | 6.47 | 6.43
2018-06-13 05:00 | 7.05 | 7.03
2018-06-13 05:30 | 7.92 | 7.9
2018-06-13 06:00 | 9.39 | 9.38
2018-06-13 06:30 | 10.38 | 10.38
2018-06-13 07:00 | 11.33 | 11.33
2018-06-13 07:30 | 11.93 | 11.93
2018-06-13 08:00 | 11.32 | 11.32
2018-06-13 08:30 | 9.76 | 9.76
2018-06-13 09:00 | 8.56 | 8.56
2018-06-13 09:30 | 7 | 6.98
2018-06-13 10:00 | 6.76 | 6.75
2018-06-13 10:30 | 7.76 | 7.74
2018-06-13 11:00 | 6.5 | 6.48
2018-06-13 11:30 | 6.39 | 6.37
2018-06-13 12:00 | 6.31 | 6.28
2018-06-13 12:30 | 6.31 | 6.28
2018-06-13 13:00 | 5.9 | 5.87
2018-06-13 13:30 | 6.38 | 6.35
2018-06-13 14:00 | 6.17 | 6.15
2018-06-13 14:30 | 5.71 | 5.7
2018-06-13 15:00 | 5.6 | 5.58
2018-06-13 15:30 | 6.82 | 6.81
2018-06-13 16:00 | 7.54 | 7.53
2018-06-13 16:30 | 8.51 | 8.5
2018-06-13 17:00 | 9.84 | 9.83
2018-06-13 17:30 | 11.43 | 11.42
2018-06-13 18:00 | 12.09 | 12.09
2018-06-13 18:30 | 12.18 | 12.17
2018-06-13 19:00 | 12.29 | 12.28
2018-06-13 19:30 | 12.09 | 12.08
2018-06-13 20:00 | 12.07 | 12.06
2018-06-13 20:30 | 11.87 | 11.86
2018-06-13 21:00 | 11.32 | 11.31
2018-06-13 21:30 | 10.4 | 10.39
2018-06-13 22:00 | 9.61 | 9.6
2018-06-13 22:30 | 8.9 | 8.89
2018-06-13 23:00 | 8.4 | 8.39
2018-06-13 23:30 | 7.3 | 7.29
2018-06-14 | 6.45 | 6.43
2018-06-14 00:30 | 5.8 | 5.78
2018-06-14 01:00 | 5.29 | 5.26
2018-06-14 01:30 | 4.9 | 4.87
2018-06-14 02:00 | 4.58 | 4.54
2018-06-14 02:30 | 4.46 | 4.42
2018-06-14 03:00 | 4.39 | 4.35
2018-06-14 03:30 | 4.53 | 4.49
2018-06-14 04:00 | 4.56 | 4.52
2018-06-14 04:30 | 4.72 | 4.68
2018-06-14 05:00 | 5.22 | 5.19
2018-06-14 05:30 | 5.9 | 5.89
2018-06-14 06:00 | 7.12 | 7.11
2018-06-14 06:30 | 7.81 | 7.81
2018-06-14 07:00 | 8.56 | 8.55
2018-06-14 07:30 | 8.95 | 8.94
2018-06-14 08:00 | 8.37 | 8.37
2018-06-14 08:30 | 7.15 | 7.14
2018-06-14 09:00 | 6.91 | 6.91
2018-06-14 09:30 | 5.84 | 5.83
2018-06-14 10:00 | 5.65 | 5.64
2018-06-14 10:30 | 5.91 | 5.9
2018-06-14 11:00 | 6.44 | 6.44
2018-06-14 11:30 | 5.84 | 5.83
2018-06-14 12:00 | 4.75 | 4.75
2018-06-14 12:30 | 4.58 | 4.58
2018-06-14 13:00 | 3.38 | 3.36
2018-06-14 13:30 | 4.11 | 4.09
2018-06-14 14:00 | 4.46 | 4.45
2018-06-14 14:30 | 4.74 | 4.72
2018-06-14 15:00 | 4.67 | 4.65
2018-06-14 15:30 | 6.15 | 6.14
2018-06-14 16:00 | 7.29 | 7.28
2018-06-14 16:30 | 8.04 | 8.03
2018-06-14 17:00 | 9.15 | 9.15
2018-06-14 17:30 | 10.6 | 10.59
2018-06-14 18:00 | 11.39 | 11.38
2018-06-14 18:30 | 11.68 | 11.68
2018-06-14 19:00 | 11.69 | 11.69
2018-06-14 19:30 | 11.5 | 11.49
2018-06-14 20:00 | 11.62 | 11.62
2018-06-14 20:30 | 11.82 | 11.82
2018-06-14 21:00 | 11.24 | 11.23
2018-06-14 21:30 | 10.58 | 10.57
2018-06-14 22:00 | 9.67 | 9.66
2018-06-14 22:30 | 9.01 | 9
2018-06-14 23:00 | 8.63 | 8.62
2018-06-14 23:30 | 7.59 | 7.58
2018-06-15 | 6.65 | 6.63
2018-06-15 00:30 | 5.94 | 5.91
2018-06-15 01:00 | 5.62 | 5.59
2018-06-15 01:30 | 5.31 | 5.29
2018-06-15 02:00 | 4.92 | 4.88
2018-06-15 02:30 | 4.78 | 4.74
2018-06-15 03:00 | 4.68 | 4.64
2018-06-15 03:30 | 4.86 | 4.82
2018-06-15 04:00 | 4.91 | 4.87
2018-06-15 04:30 | 5.07 | 5.03
2018-06-15 05:00 | 5.64 | 5.61
2018-06-15 05:30 | 6.37 | 6.35
2018-06-15 06:00 | 7.61 | 7.6
2018-06-15 06:30 | 8.66 | 8.66
2018-06-15 07:00 | 9.53 | 9.53
2018-06-15 07:30 | 10.29 | 10.29
2018-06-15 08:00 | 9.75 | 9.74
2018-06-15 08:30 | 8.1 | 8.09
2018-06-15 09:00 | 6.66 | 6.66
2018-06-15 09:30 | 6.08 | 6.07
2018-06-15 10:00 | 5.18 | 5.17
2018-06-15 10:30 | 4.39 | 4.38
2018-06-15 11:00 | 3.71 | 3.68
2018-06-15 11:30 | 3.48 | 3.45
2018-06-15 12:00 | 3.16 | 3.13
2018-06-15 12:30 | 3.28 | 3.26
2018-06-15 13:00 | 3.38 | 3.36
2018-06-15 13:30 | 3.46 | 3.44
2018-06-15 14:00 | 3.71 | 3.69
2018-06-15 14:30 | 4.1 | 4.08
2018-06-15 15:00 | 4.51 | 4.49
2018-06-15 15:30 | 5.46 | 5.45
2018-06-15 16:00 | 6.52 | 6.51
2018-06-15 16:30 | 7.6 | 7.59
2018-06-15 17:00 | 8.76 | 8.75
2018-06-15 17:30 | 9.72 | 9.71
2018-06-15 18:00 | 10.86 | 10.84
2018-06-15 18:30 | 11.23 | 11.22
2018-06-15 19:00 | 11.64 | 11.63
2018-06-15 19:30 | 11.63 | 11.62
2018-06-15 20:00 | 11.75 | 11.75
2018-06-15 20:30 | 11.89 | 11.88
2018-06-15 21:00 | 11.52 | 11.51
2018-06-15 21:30 | 11.18 | 11.17
2018-06-15 22:00 | 10.65 | 10.64
2018-06-15 22:30 | 10.24 | 10.23
2018-06-15 23:00 | 9.98 | 9.98
2018-06-15 23:30 | 9.01 | 9
2018-06-16 | 7.93 | 7.92
2018-06-16 00:30 | 7.17 | 7.16
2018-06-16 01:00 | 6.79 | 6.77
2018-06-16 01:30 | 6.35 | 6.33
2018-06-16 02:00 | 5.91 | 5.88
2018-06-16 02:30 | 5.65 | 5.62
2018-06-16 03:00 | 5.46 | 5.42
2018-06-16 03:30 | 5.49 | 5.46
2018-06-16 04:00 | 5.4 | 5.37
2018-06-16 04:30 | 5.56 | 5.53
2018-06-16 05:00 | 5.84 | 5.81
2018-06-16 05:30 | 6.24 | 6.21
2018-06-16 06:00 | 6.51 | 6.5
2018-06-16 06:30 | 7.07 | 7.05
2018-06-16 07:00 | 7.9 | 7.87
2018-06-16 07:30 | 8.73 | 8.71
2018-06-16 08:00 | 8.92 | 8.91
2018-06-16 08:30 | 8.75 | 8.74
2018-06-16 09:00 | 8.16 | 8.15
2018-06-16 09:30 | 7.6 | 7.59
2018-06-16 10:00 | 6.77 | 6.76
2018-06-16 10:30 | 6.02 | 6
2018-06-16 11:00 | 5.24 | 5.22
2018-06-16 11:30 | 4.78 | 4.76
2018-06-16 12:00 | 4.48 | 4.46
2018-06-16 12:30 | 4.39 | 4.36
2018-06-16 13:00 | 4.38 | 4.35
2018-06-16 13:30 | 4.46 | 4.43
2018-06-16 14:00 | 4.89 | 4.86
2018-06-16 14:30 | 5.21 | 5.19
2018-06-16 15:00 | 5.52 | 5.5
2018-06-16 15:30 | 6.01 | 5.99
2018-06-16 16:00 | 6.62 | 6.6
2018-06-16 16:30 | 7.78 | 7.76
2018-06-16 17:00 | 8.98 | 8.96
2018-06-16 17:30 | 10.24 | 10.23
2018-06-16 18:00 | 11.23 | 11.22
2018-06-16 18:30 | 11.39 | 11.38
2018-06-16 19:00 | 11.6 | 11.59
2018-06-16 19:30 | 11.52 | 11.51
2018-06-16 20:00 | 11.69 | 11.68
2018-06-16 20:30 | 11.8 | 11.79
2018-06-16 21:00 | 11.24 | 11.23
2018-06-16 21:30 | 10.78 | 10.78
2018-06-16 22:00 | 10.51 | 10.51
2018-06-16 22:30 | 10.29 | 10.28
2018-06-16 23:00 | 10.01 | 10.01
2018-06-16 23:30 | 9.16 | 9.15
2018-06-17 | 8.19 | 8.18
2018-06-17 00:30 | 7.39 | 7.38
2018-06-17 01:00 | 6.91 | 6.89
2018-06-17 01:30 | 6.43 | 6.41
2018-06-17 02:00 | 6.01 | 5.99
2018-06-17 02:30 | 5.84 | 5.81
2018-06-17 03:00 | 5.68 | 5.65
2018-06-17 03:30 | 5.45 | 5.42
2018-06-17 04:00 | 5.41 | 5.38
2018-06-17 04:30 | 5.59 | 5.56
2018-06-17 05:00 | 5.78 | 5.75
2018-06-17 05:30 | 6.06 | 6.03
2018-06-17 06:00 | 6.33 | 6.31
2018-06-17 06:30 | 6.79 | 6.78
2018-06-17 07:00 | 7.34 | 7.31
2018-06-17 07:30 | 8.18 | 8.16
2018-06-17 08:00 | 8.59 | 8.58
2018-06-17 08:30 | 8.73 | 8.72
2018-06-17 09:00 | 8.38 | 8.37
2018-06-17 09:30 | 7.88 | 7.87
2018-06-17 10:00 | 7.32 | 7.3
2018-06-17 10:30 | 6.78 | 6.77
2018-06-17 11:00 | 6.33 | 6.31
2018-06-17 11:30 | 5.85 | 5.83
2018-06-17 12:00 | 5.52 | 5.5
2018-06-17 12:30 | 5.34 | 5.32
2018-06-17 13:00 | 5.32 | 5.29
2018-06-17 13:30 | 5.41 | 5.39
2018-06-17 14:00 | 5.76 | 5.73
2018-06-17 14:30 | 5.93 | 5.91
2018-06-17 15:00 | 6.25 | 6.22
2018-06-17 15:30 | 6.95 | 6.93
2018-06-17 16:00 | 7.91 | 7.89
2018-06-17 16:30 | 9.27 | 9.26
2018-06-17 17:00 | 11.01 | 11
2018-06-17 17:30 | 12.87 | 12.86
2018-06-17 18:00 | 14.33 | 14.32
2018-06-17 18:30 | 14.57 | 14.56
2018-06-17 19:00 | 14.73 | 14.72
2018-06-17 19:30 | 14.63 | 14.62
2018-06-17 20:00 | 14.39 | 14.39
2018-06-17 20:30 | 14.47 | 14.47
2018-06-17 21:00 | 13.88 | 13.87
2018-06-17 21:30 | 12.89 | 12.88
2018-06-17 22:00 | 11.93 | 11.93
2018-06-17 22:30 | 11.14 | 11.13
2018-06-17 23:00 | 10.46 | 10.45
2018-06-17 23:30 | 9.29 | 9.29
2018-06-18 | 8.23 | 8.22
2018-06-18 00:30 | 7.29 | 7.27
2018-06-18 01:00 | 6.68 | 6.66
2018-06-18 01:30 | 6.36 | 6.34
2018-06-18 02:00 | 5.98 | 5.96
2018-06-18 02:30 | 5.83 | 5.8
2018-06-18 03:00 | 5.77 | 5.75
2018-06-18 03:30 | 5.82 | 5.79
2018-06-18 04:00 | 5.95 | 5.92
2018-06-18 04:30 | 6.37 | 6.35
2018-06-18 05:00 | 7.05 | 7.04
2018-06-18 05:30 | 7.97 | 7.96
2018-06-18 06:00 | 9.16 | 9.16
2018-06-18 06:30 | 10.4 | 10.4
2018-06-18 07:00 | 11.57 | 11.57
2018-06-18 07:30 | 12.27 | 12.27
2018-06-18 08:00 | 11.68 | 11.67
2018-06-18 08:30 | 9.97 | 9.96
2018-06-18 09:00 | 8.33 | 8.32
2018-06-18 09:30 | 7.23 | 7.22
2018-06-18 10:00 | 6.5 | 6.49
2018-06-18 10:30 | 5.9 | 5.89
2018-06-18 11:00 | 5.58 | 5.57
2018-06-18 11:30 | 5.08 | 5.07
2018-06-18 12:00 | 4.81 | 4.8
2018-06-18 12:30 | 4.58 | 4.57
2018-06-18 13:00 | 4.48 | 4.46
2018-06-18 13:30 | 4.44 | 4.42
2018-06-18 14:00 | 4.69 | 4.66
2018-06-18 14:30 | 5.05 | 5.02
2018-06-18 15:00 | 5.38 | 5.36
2018-06-18 15:30 | 6.18 | 6.15
2018-06-18 16:00 | 7.53 | 7.51
2018-06-18 16:30 | 9.3 | 9.29
2018-06-18 17:00 | 11.45 | 11.45
2018-06-18 17:30 | 13.81 | 13.8
2018-06-18 18:00 | 15.3 | 15.28
2018-06-18 18:30 | 15.77 | 15.75
2018-06-18 19:00 | 16.24 | 16.22
2018-06-18 19:30 | 16.3 | 16.28
2018-06-18 20:00 | 16.25 | 16.23
2018-06-18 20:30 | 16.02 | 16
2018-06-18 21:00 | 15.23 | 15.22
2018-06-18 21:30 | 13.92 | 13.91
2018-06-18 22:00 | 12.48 | 12.48
2018-06-18 22:30 | 11.56 | 11.55
2018-06-18 23:00 | 10.83 | 10.82
2018-06-18 23:30 | 9.52 | 9.51
2018-06-19 | 8.29 | 8.29
2018-06-19 00:30 | 7.41 | 7.4
2018-06-19 01:00 | 6.87 | 6.86
2018-06-19 01:30 | 6.46 | 6.44
2018-06-19 02:00 | 6.15 | 6.13
2018-06-19 02:30 | 5.96 | 5.94
2018-06-19 03:00 | 6.03 | 6.01
2018-06-19 03:30 | 5.98 | 5.96
2018-06-19 04:00 | 6.15 | 6.13
2018-06-19 04:30 | 6.46 | 6.44
2018-06-19 05:00 | 7.17 | 7.16
2018-06-19 05:30 | 8.34 | 8.33
2018-06-19 06:00 | 9.78 | 9.78
2018-06-19 06:30 | 11 | 11
2018-06-19 07:00 | 12.14 | 12.14
2018-06-19 07:30 | 12.68 | 12.68
2018-06-19 08:00 | 11.95 | 11.95
2018-06-19 08:30 | 10.07 | 10.07
2018-06-19 09:00 | 8.39 | 8.39
2018-06-19 09:30 | 7.47 | 7.46
2018-06-19 10:00 | 6.77 | 6.76
2018-06-19 10:30 | 5.85 | 5.84
2018-06-19 11:00 | 5.3 | 5.29
2018-06-19 11:30 | 4.99 | 4.98
2018-06-19 12:00 | 4.59 | 4.58
2018-06-19 12:30 | 4.5 | 4.49
2018-06-19 13:00 | 4.05 | 4.02
2018-06-19 13:30 | 4.11 | 4.09
2018-06-19 14:00 | 4.44 | 4.41
2018-06-19 14:30 | 4.76 | 4.73
2018-06-19 15:00 | 5.04 | 5.01
2018-06-19 15:30 | 5.75 | 5.73
2018-06-19 16:00 | 7.07 | 7.05
2018-06-19 16:30 | 8.63 | 8.62
2018-06-19 17:00 | 10.46 | 10.45
2018-06-19 17:30 | 12.67 | 12.66
2018-06-19 18:00 | 14.28 | 14.27
2018-06-19 18:30 | 14.99 | 14.98
2018-06-19 19:00 | 15.32 | 15.31
2018-06-19 19:30 | 15.24 | 15.22
2018-06-19 20:00 | 15.17 | 15.15
2018-06-19 20:30 | 15.19 | 15.18
2018-06-19 21:00 | 14.47 | 14.46
2018-06-19 21:30 | 13.35 | 13.35
2018-06-19 22:00 | 12.17 | 12.17
2018-06-19 22:30 | 11.2 | 11.2
2018-06-19 23:00 | 10.57 | 10.57
2018-06-19 23:30 | 9.33 | 9.33
2018-06-20 | 8.3 | 8.29
2018-06-20 00:30 | 7.4 | 7.39
2018-06-20 01:00 | 6.86 | 6.84
2018-06-20 01:30 | 6.46 | 6.44
2018-06-20 02:00 | 6.08 | 6.05
2018-06-20 02:30 | 5.9 | 5.87
2018-06-20 03:00 | 5.78 | 5.75
2018-06-20 03:30 | 5.88 | 5.85
2018-06-20 04:00 | 5.97 | 5.94
2018-06-20 04:30 | 6.44 | 6.42
2018-06-20 05:00 | 7.16 | 7.15
2018-06-20 05:30 | 8.16 | 8.15
2018-06-20 06:00 | 9.2 | 9.19
2018-06-20 06:30 | 10.27 | 10.27
2018-06-20 07:00 | 11.22 | 11.22
2018-06-20 07:30 | 12.27 | 12.27
2018-06-20 08:00 | 11.56 | 11.56
2018-06-20 08:30 | 9.83 | 9.82
2018-06-20 09:00 | 8.47 | 8.47
2018-06-20 09:30 | 7.52 | 7.51
2018-06-20 10:00 | 6.51 | 6.51
2018-06-20 10:30 | 5.73 | 5.72
2018-06-20 11:00 | 5.12 | 5.11
2018-06-20 11:30 | 5.01 | 5
2018-06-20 12:00 | 4.77 | 4.76
2018-06-20 12:30 | 4.64 | 4.63
2018-06-20 13:00 | 4.66 | 4.63
2018-06-20 13:30 | 6 | 5.97
2018-06-20 14:00 | 4.69 | 4.66
2018-06-20 14:30 | 5.55 | 5.52
2018-06-20 15:00 | 5.66 | 5.63
2018-06-20 15:30 | 6.13 | 6.1
2018-06-20 16:00 | 7.72 | 7.7
2018-06-20 16:30 | 8.67 | 8.66
2018-06-20 17:00 | 10.25 | 10.24
2018-06-20 17:30 | 12.09 | 12.08
2018-06-20 18:00 | 13.34 | 13.33
2018-06-20 18:30 | 13.84 | 13.83
2018-06-20 19:00 | 14.17 | 14.16
2018-06-20 19:30 | 14.27 | 14.26
2018-06-20 20:00 | 14.32 | 14.31
2018-06-20 20:30 | 14.42 | 14.41
2018-06-20 21:00 | 13.85 | 13.84
2018-06-20 21:30 | 12.83 | 12.82
2018-06-20 22:00 | 11.85 | 11.84
2018-06-20 22:30 | 10.96 | 10.95
2018-06-20 23:00 | 10.43 | 10.42
2018-06-20 23:30 | 9.25 | 9.24
2018-06-21 | 8.11 | 8.1
2018-06-21 00:30 | 7.22 | 7.2
2018-06-21 01:00 | 6.73 | 6.71
2018-06-21 01:30 | 6.34 | 6.32
2018-06-21 02:00 | 6.01 | 5.98
2018-06-21 02:30 | 5.88 | 5.85
2018-06-21 03:00 | 5.9 | 5.87
2018-06-21 03:30 | 5.91 | 5.88
2018-06-21 04:00 | 5.88 | 5.85
2018-06-21 04:30 | 6.2 | 6.18
2018-06-21 05:00 | 6.92 | 6.9
2018-06-21 05:30 | 7.97 | 7.96
2018-06-21 06:00 | 9.41 | 9.41
2018-06-21 06:30 | 10.69 | 10.69
2018-06-21 07:00 | 11.84 | 11.83
2018-06-21 07:30 | 12.46 | 12.45
2018-06-21 08:00 | 11.64 | 11.64
2018-06-21 08:30 | 9.75 | 9.75
2018-06-21 09:00 | 8.12 | 8.12
2018-06-21 09:30 | 7.26 | 7.25
2018-06-21 10:00 | 6.26 | 6.25
2018-06-21 10:30 | 5.36 | 5.35
2018-06-21 11:00 | 4.8 | 4.79
2018-06-21 11:30 | 4.37 | 4.35
2018-06-21 12:00 | 4.23 | 4.22
2018-06-21 12:30 | 4.23 | 4.22
2018-06-21 13:00 | 4.32 | 4.3
2018-06-21 13:30 | 3.93 | 3.9
2018-06-21 14:00 | 4.4 | 4.37
2018-06-21 14:30 | 4.92 | 4.89
2018-06-21 15:00 | 5.77 | 5.75
2018-06-21 15:30 | 6 | 5.98
2018-06-21 16:00 | 7.05 | 7.03
2018-06-21 16:30 | 7.96 | 7.95
2018-06-21 17:00 | 9.64 | 9.64
2018-06-21 17:30 | 11.2 | 11.2
2018-06-21 18:00 | 12.37 | 12.36
2018-06-21 18:30 | 12.85 | 12.84
2018-06-21 19:00 | 13.24 | 13.23
2018-06-21 19:30 | 13.29 | 13.28
2018-06-21 20:00 | 13.55 | 13.54
2018-06-21 20:30 | 13.77 | 13.77
2018-06-21 21:00 | 13.26 | 13.26
2018-06-21 21:30 | 12.46 | 12.46
2018-06-21 22:00 | 11.61 | 11.6
2018-06-21 22:30 | 10.79 | 10.78
2018-06-21 23:00 | 10.28 | 10.27
2018-06-21 23:30 | 9.31 | 9.3
2018-06-22 | 8.19 | 8.18
2018-06-22 00:30 | 7.21 | 7.2
2018-06-22 01:00 | 6.7 | 6.68
2018-06-22 01:30 | 6.31 | 6.29
2018-06-22 02:00 | 5.95 | 5.92
2018-06-22 02:30 | 5.72 | 5.68
2018-06-22 03:00 | 5.62 | 5.58
2018-06-22 03:30 | 5.73 | 5.7
2018-06-22 04:00 | 5.82 | 5.79
2018-06-22 04:30 | 6.2 | 6.17
2018-06-22 05:00 | 6.81 | 6.8
2018-06-22 05:30 | 7.63 | 7.62
2018-06-22 06:00 | 8.58 | 8.58
2018-06-22 06:30 | 9.59 | 9.58
2018-06-22 07:00 | 10.79 | 10.78
2018-06-22 07:30 | 11.7 | 11.7
2018-06-22 08:00 | 10.97 | 10.97
2018-06-22 08:30 | 9.18 | 9.17
2018-06-22 09:00 | 7.48 | 7.47
2018-06-22 09:30 | 6.43 | 6.42
2018-06-22 10:00 | 5.62 | 5.61
2018-06-22 10:30 | 4.8 | 4.78
2018-06-22 11:00 | 4.33 | 4.31
2018-06-22 11:30 | 3.79 | 3.76
2018-06-22 12:00 | 3.61 | 3.59
2018-06-22 12:30 | 3.55 | 3.52
2018-06-22 13:00 | 3.67 | 3.64
2018-06-22 13:30 | 3.56 | 3.53
2018-06-22 14:00 | 4.05 | 4.03
2018-06-22 14:30 | 4.9 | 4.88
2018-06-22 15:00 | 5.59 | 5.57
2018-06-22 15:30 | 6.33 | 6.31
2018-06-22 16:00 | 6.81 | 6.79
2018-06-22 16:30 | 7.95 | 7.94
2018-06-22 17:00 | 9.52 | 9.52
2018-06-22 17:30 | 10.85 | 10.85
2018-06-22 18:00 | 11.55 | 11.54
2018-06-22 18:30 | 11.96 | 11.95
2018-06-22 19:00 | 12.12 | 12.12
2018-06-22 19:30 | 12.24 | 12.23
2018-06-22 20:00 | 12.44 | 12.43
2018-06-22 20:30 | 12.71 | 12.7
2018-06-22 21:00 | 12.23 | 12.22
2018-06-22 21:30 | 11.52 | 11.52
2018-06-22 22:00 | 10.99 | 10.99
2018-06-22 22:30 | 10.7 | 10.69
2018-06-22 23:00 | 10.3 | 10.3
2018-06-22 23:30 | 9.33 | 9.32
2018-06-23 | 8.34 | 8.33
2018-06-23 00:30 | 7.48 | 7.46
2018-06-23 01:00 | 6.98 | 6.96
2018-06-23 01:30 | 6.54 | 6.52
2018-06-23 02:00 | 6.06 | 6.03
2018-06-23 02:30 | 5.84 | 5.81
2018-06-23 03:00 | 5.63 | 5.6
2018-06-23 03:30 | 5.73 | 5.69
2018-06-23 04:00 | 5.68 | 5.65
2018-06-23 04:30 | 5.67 | 5.64
2018-06-23 05:00 | 6.05 | 6.03
2018-06-23 05:30 | 6.44 | 6.42
2018-06-23 06:00 | 6.79 | 6.77
2018-06-23 06:30 | 7.27 | 7.26
2018-06-23 07:00 | 8.01 | 7.99
2018-06-23 07:30 | 8.93 | 8.92
2018-06-23 08:00 | 9.19 | 9.18
2018-06-23 08:30 | 9.13 | 9.12
2018-06-23 09:00 | 8.58 | 8.57
2018-06-23 09:30 | 7.96 | 7.95
2018-06-23 10:00 | 7.4 | 7.38
2018-06-23 10:30 | 6.53 | 6.51
2018-06-23 11:00 | 5.76 | 5.74
2018-06-23 11:30 | 5.48 | 5.47
2018-06-23 12:00 | 5.03 | 5.01
2018-06-23 12:30 | 4.71 | 4.69
2018-06-23 13:00 | 4.68 | 4.65
2018-06-23 13:30 | 4.82 | 4.8
2018-06-23 14:00 | 5.15 | 5.13
2018-06-23 14:30 | 5.42 | 5.4
2018-06-23 15:00 | 5.85 | 5.83
2018-06-23 15:30 | 6.32 | 6.3
2018-06-23 16:00 | 7.12 | 7.1
2018-06-23 16:30 | 8 | 7.99
2018-06-23 17:00 | 9.37 | 9.35
2018-06-23 17:30 | 10.71 | 10.7
2018-06-23 18:00 | 11.85 | 11.84
2018-06-23 18:30 | 12 | 11.99
2018-06-23 19:00 | 12.04 | 12.04
2018-06-23 19:30 | 11.88 | 11.87
2018-06-23 20:00 | 11.87 | 11.87
2018-06-23 20:30 | 12.14 | 12.13
2018-06-23 21:00 | 11.76 | 11.76
2018-06-23 21:30 | 11.16 | 11.15
2018-06-23 22:00 | 10.8 | 10.8
2018-06-23 22:30 | 10.49 | 10.48
2018-06-23 23:00 | 10.28 | 10.28
2018-06-23 23:30 | 9.37 | 9.36
2018-06-24 | 8.42 | 8.41
2018-06-24 00:30 | 7.61 | 7.6
2018-06-24 01:00 | 7.14 | 7.12
2018-06-24 01:30 | 6.66 | 6.63
2018-06-24 02:00 | 6.26 | 6.23
2018-06-24 02:30 | 6.06 | 6.04
2018-06-24 03:00 | 5.9 | 5.87
2018-06-24 03:30 | 5.78 | 5.75
2018-06-24 04:00 | 5.75 | 5.72
2018-06-24 04:30 | 5.87 | 5.84
2018-06-24 05:00 | 6.06 | 6.04
2018-06-24 05:30 | 6.39 | 6.38
2018-06-24 06:00 | 6.59 | 6.58
2018-06-24 06:30 | 6.93 | 6.91
2018-06-24 07:00 | 7.56 | 7.53
2018-06-24 07:30 | 8.38 | 8.36
2018-06-24 08:00 | 8.72 | 8.71
2018-06-24 08:30 | 8.93 | 8.92
2018-06-24 09:00 | 8.72 | 8.71
2018-06-24 09:30 | 8.15 | 8.14
2018-06-24 10:00 | 7.61 | 7.6
2018-06-24 10:30 | 6.86 | 6.85
2018-06-24 11:00 | 6.13 | 6.12
2018-06-24 11:30 | 5.73 | 5.71
2018-06-24 12:00 | 5.38 | 5.36
2018-06-24 12:30 | 5.22 | 5.19
2018-06-24 13:00 | 5.17 | 5.15
2018-06-24 13:30 | 5.14 | 5.11
2018-06-24 14:00 | 5.56 | 5.54
2018-06-24 14:30 | 5.89 | 5.86
2018-06-24 15:00 | 6.27 | 6.24
2018-06-24 15:30 | 6.82 | 6.8
2018-06-24 16:00 | 7.68 | 7.66
2018-06-24 16:30 | 8.93 | 8.92
2018-06-24 17:00 | 10.53 | 10.52
2018-06-24 17:30 | 12.04 | 12.03
2018-06-24 18:00 | 13.15 | 13.14
2018-06-24 18:30 | 13.31 | 13.3
2018-06-24 19:00 | 13.46 | 13.45
2018-06-24 19:30 | 13.39 | 13.38
2018-06-24 20:00 | 13.31 | 13.3
2018-06-24 20:30 | 13.2 | 13.2
2018-06-24 21:00 | 12.76 | 12.76
2018-06-24 21:30 | 12.09 | 12.09
2018-06-24 22:00 | 11.31 | 11.3
2018-06-24 22:30 | 10.84 | 10.83
2018-06-24 23:00 | 10.34 | 10.33
2018-06-24 23:30 | 9.23 | 9.22
2018-06-25 | 7.97 | 7.96
2018-06-25 00:30 | 7.17 | 7.15
2018-06-25 01:00 | 6.73 | 6.71
2018-06-25 01:30 | 6.21 | 6.19
2018-06-25 02:00 | 5.89 | 5.86
2018-06-25 02:30 | 5.74 | 5.71
2018-06-25 03:00 | 5.62 | 5.58
2018-06-25 03:30 | 5.65 | 5.61
2018-06-25 04:00 | 5.77 | 5.74
2018-06-25 04:30 | 6.08 | 6.05
2018-06-25 05:00 | 6.69 | 6.67
2018-06-25 05:30 | 7.59 | 7.58
2018-06-25 06:00 | 8.74 | 8.73
2018-06-25 06:30 | 9.88 | 9.88
2018-06-25 07:00 | 10.85 | 10.85
2018-06-25 07:30 | 11.89 | 11.89
2018-06-25 08:00 | 12.18 | 12.17
2018-06-25 08:30 | 11.36 | 11.36
2018-06-25 09:00 | 9.98 | 9.97
2018-06-25 09:30 | 8.22 | 8.22
2018-06-25 10:00 | 8.72 | 8.71
2018-06-25 10:30 | 7.19 | 7.19
2018-06-25 11:00 | 6.21 | 6.2
2018-06-25 11:30 | 5.62 | 5.61
2018-06-25 12:00 | 5.19 | 5.18
2018-06-25 12:30 | 5.11 | 5.1
2018-06-25 13:00 | 6.78 | 6.75
2018-06-25 13:30 | 5.38 | 5.37
2018-06-25 14:00 | 6.05 | 6.03
2018-06-25 14:30 | 6.95 | 6.93
2018-06-25 15:00 | 5.61 | 5.58
2018-06-25 15:30 | 7.27 | 7.26
2018-06-25 16:00 | 8.39 | 8.38
2018-06-25 16:30 | 9.47 | 9.46
2018-06-25 17:00 | 11 | 10.99
2018-06-25 17:30 | 12.77 | 12.77
2018-06-25 18:00 | 14.08 | 14.07
2018-06-25 18:30 | 14.36 | 14.35
2018-06-25 19:00 | 14.4 | 14.39
2018-06-25 19:30 | 14.06 | 14.05
2018-06-25 20:00 | 13.98 | 13.98
2018-06-25 20:30 | 13.9 | 13.89
2018-06-25 21:00 | 13.13 | 13.12
2018-06-25 21:30 | 12.15 | 12.14
2018-06-25 22:00 | 11.24 | 11.23
2018-06-25 22:30 | 10.28 | 10.27
2018-06-25 23:00 | 9.71 | 9.7
2018-06-25 23:30 | 8.58 | 8.57
2018-06-26 | 7.5 | 7.49
2018-06-26 00:30 | 6.66 | 6.64
2018-06-26 01:00 | 6.18 | 6.15
2018-06-26 01:30 | 5.76 | 5.72
2018-06-26 02:00 | 5.56 | 5.53
2018-06-26 02:30 | 5.34 | 5.3
2018-06-26 03:00 | 5.2 | 5.16
2018-06-26 03:30 | 5.23 | 5.19
2018-06-26 04:00 | 5.45 | 5.42
2018-06-26 04:30 | 5.57 | 5.54
2018-06-26 05:00 | 6.14 | 6.11
2018-06-26 05:30 | 7.12 | 7.11
2018-06-26 06:00 | 8.17 | 8.16
2018-06-26 06:30 | 8.91 | 8.91
2018-06-26 07:00 | 9.7 | 9.7
2018-06-26 07:30 | 10.19 | 10.18
2018-06-26 08:00 | 9.72 | 9.71
2018-06-26 08:30 | 8.64 | 8.63
2018-06-26 09:00 | 7.56 | 7.55
2018-06-26 09:30 | 6.89 | 6.87
2018-06-26 10:00 | 5.84 | 5.82
2018-06-26 10:30 | 5.84 | 5.82
2018-06-26 11:00 | 5.37 | 5.35
2018-06-26 11:30 | 5.68 | 5.66
2018-06-26 12:00 | 5.72 | 5.7
2018-06-26 12:30 | 4.52 | 4.5
2018-06-26 13:00 | 5.24 | 5.22
2018-06-26 13:30 | 5.96 | 5.93
2018-06-26 14:00 | 5.63 | 5.6
2018-06-26 14:30 | 5.95 | 5.92
2018-06-26 15:00 | 6.57 | 6.54
2018-06-26 15:30 | 7.15 | 7.13
2018-06-26 16:00 | 8.13 | 8.12
2018-06-26 16:30 | 9.33 | 9.32
2018-06-26 17:00 | 10.67 | 10.66
2018-06-26 17:30 | 12.11 | 12.11
2018-06-26 18:00 | 13.07 | 13.06
2018-06-26 18:30 | 13.53 | 13.52
2018-06-26 19:00 | 13.7 | 13.69
2018-06-26 19:30 | 13.44 | 13.44
2018-06-26 20:00 | 13.11 | 13.11
2018-06-26 20:30 | 13.2 | 13.19
2018-06-26 21:00 | 12.6 | 12.6
2018-06-26 21:30 | 11.56 | 11.55
2018-06-26 22:00 | 10.47 | 10.46
2018-06-26 22:30 | 9.7 | 9.7
2018-06-26 23:00 | 9.41 | 9.4
2018-06-26 23:30 | 8.2 | 8.19
2018-06-27 | 7.14 | 7.12
2018-06-27 00:30 | 6.32 | 6.29
2018-06-27 01:00 | 5.95 | 5.92
2018-06-27 01:30 | 5.59 | 5.56
2018-06-27 02:00 | 5.11 | 5.07
2018-06-27 02:30 | 4.9 | 4.86
2018-06-27 03:00 | 4.98 | 4.93
2018-06-27 03:30 | 4.91 | 4.86
2018-06-27 04:00 | 4.97 | 4.92
2018-06-27 04:30 | 5.32 | 5.28
2018-06-27 05:00 | 5.65 | 5.62
2018-06-27 05:30 | 6.48 | 6.46
2018-06-27 06:00 | 7.26 | 7.25
2018-06-27 06:30 | 8.23 | 8.22
2018-06-27 07:00 | 8.91 | 8.91
2018-06-27 07:30 | 9.65 | 9.65
2018-06-27 08:00 | 9.77 | 9.76
2018-06-27 08:30 | 9.17 | 9.16
2018-06-27 09:00 | 8.29 | 8.28
2018-06-27 09:30 | 8.57 | 8.56
2018-06-27 10:00 | 8.62 | 8.61
2018-06-27 10:30 | 8.83 | 8.81
2018-06-27 11:00 | 8.93 | 8.92
2018-06-27 11:30 | 8.82 | 8.81
2018-06-27 12:00 | 8.83 | 8.82
2018-06-27 12:30 | 9.1 | 9.1
2018-06-27 13:00 | 8.66 | 8.64
2018-06-27 13:30 | 8.5 | 8.49
2018-06-27 14:00 | 8.6 | 8.58
2018-06-27 14:30 | 8.42 | 8.41
2018-06-27 15:00 | 8.52 | 8.51
2018-06-27 15:30 | 9.36 | 9.35
2018-06-27 16:00 | 9.96 | 9.96
2018-06-27 16:30 | 11.03 | 11.02
2018-06-27 17:00 | 11.86 | 11.85
2018-06-27 17:30 | 13.29 | 13.28
2018-06-27 18:00 | 14.37 | 14.35
2018-06-27 18:30 | 14.77 | 14.75
2018-06-27 19:00 | 14.95 | 14.94
2018-06-27 19:30 | 14.68 | 14.67
2018-06-27 20:00 | 14.68 | 14.67
2018-06-27 20:30 | 14.39 | 14.38
2018-06-27 21:00 | 13.51 | 13.5
2018-06-27 21:30 | 12.29 | 12.29
2018-06-27 22:00 | 11.33 | 11.32
2018-06-27 22:30 | 10.37 | 10.36
2018-06-27 23:00 | 9.93 | 9.92
2018-06-27 23:30 | 8.6 | 8.59
2018-06-28 | 7.57 | 7.55
2018-06-28 00:30 | 6.68 | 6.66
2018-06-28 01:00 | 6.15 | 6.13
2018-06-28 01:30 | 5.71 | 5.68
2018-06-28 02:00 | 5.39 | 5.35
2018-06-28 02:30 | 5.24 | 5.21
2018-06-28 03:00 | 5.2 | 5.17
2018-06-28 03:30 | 5.16 | 5.12
2018-06-28 04:00 | 5.2 | 5.16
2018-06-28 04:30 | 5.43 | 5.39
2018-06-28 05:00 | 5.89 | 5.86
2018-06-28 05:30 | 6.71 | 6.69
2018-06-28 06:00 | 7.64 | 7.64
2018-06-28 06:30 | 8.38 | 8.38
2018-06-28 07:00 | 8.95 | 8.94
2018-06-28 07:30 | 9.67 | 9.66
2018-06-28 08:00 | 10.39 | 10.39
2018-06-28 08:30 | 10.26 | 10.25
2018-06-28 09:00 | 9.55 | 9.54
2018-06-28 09:30 | 9.32 | 9.31
2018-06-28 10:00 | 7.97 | 7.95
2018-06-28 10:30 | 7.42 | 7.4
2018-06-28 11:00 | 6.86 | 6.84
2018-06-28 11:30 | 7.16 | 7.14
2018-06-28 12:00 | 7.43 | 7.41
2018-06-28 12:30 | 7.8 | 7.79
2018-06-28 13:00 | 8.11 | 8.09
2018-06-28 13:30 | 7.75 | 7.74
2018-06-28 14:00 | 7.34 | 7.32
2018-06-28 14:30 | 6.73 | 6.72
2018-06-28 15:00 | 6.57 | 6.56
2018-06-28 15:30 | 7.7 | 7.68
2018-06-28 16:00 | 8.98 | 8.97
2018-06-28 16:30 | 9 | 9
2018-06-28 17:00 | 9.71 | 9.7
2018-06-28 17:30 | 11.18 | 11.18
2018-06-28 18:00 | 12.65 | 12.65
2018-06-28 18:30 | 13.19 | 13.17
2018-06-28 19:00 | 13.4 | 13.39
2018-06-28 19:30 | 13.3 | 13.29
2018-06-28 20:00 | 13.47 | 13.46
2018-06-28 20:30 | 13.63 | 13.63
2018-06-28 21:00 | 13.2 | 13.2
2018-06-28 21:30 | 12.37 | 12.37
2018-06-28 22:00 | 11.28 | 11.28
2018-06-28 22:30 | 10.31 | 10.3
2018-06-28 23:00 | 9.81 | 9.8
2018-06-28 23:30 | 8.6 | 8.6
2018-06-29 | 7.62 | 7.61
2018-06-29 00:30 | 6.69 | 6.67
2018-06-29 01:00 | 6.21 | 6.19
2018-06-29 01:30 | 5.84 | 5.82
2018-06-29 02:00 | 5.4 | 5.36
2018-06-29 02:30 | 5.2 | 5.17
2018-06-29 03:00 | 5.07 | 5.03
2018-06-29 03:30 | 5.17 | 5.14
2018-06-29 04:00 | 5.25 | 5.22
2018-06-29 04:30 | 5.42 | 5.39
2018-06-29 05:00 | 5.88 | 5.85
2018-06-29 05:30 | 6.45 | 6.43
2018-06-29 06:00 | 7.08 | 7.07
2018-06-29 06:30 | 7.65 | 7.64
2018-06-29 07:00 | 8.3 | 8.29
2018-06-29 07:30 | 9.17 | 9.16
2018-06-29 08:00 | 9.16 | 9.15
2018-06-29 08:30 | 8.56 | 8.55
2018-06-29 09:00 | 8.12 | 8.11
2018-06-29 09:30 | 7.94 | 7.92
2018-06-29 10:00 | 7.8 | 7.78
2018-06-29 10:30 | 7.47 | 7.45
2018-06-29 11:00 | 7.3 | 7.28
2018-06-29 11:30 | 6.44 | 6.42
2018-06-29 12:00 | 4.45 | 4.42
2018-06-29 12:30 | 4.02 | 3.99
2018-06-29 13:00 | 3.93 | 3.9
2018-06-29 13:30 | 4.03 | 4.01
2018-06-29 14:00 | 4.39 | 4.38
2018-06-29 14:30 | 4.69 | 4.67
2018-06-29 15:00 | 5.25 | 5.23
2018-06-29 15:30 | 7.17 | 7.14
2018-06-29 16:00 | 7.9 | 7.88
2018-06-29 16:30 | 8.8 | 8.79
2018-06-29 17:00 | 8.88 | 8.87
2018-06-29 17:30 | 10.18 | 10.16
2018-06-29 18:00 | 11.16 | 11.15
2018-06-29 18:30 | 11.68 | 11.68
2018-06-29 19:00 | 11.82 | 11.81
2018-06-29 19:30 | 11.72 | 11.71
2018-06-29 20:00 | 11.86 | 11.85
2018-06-29 20:30 | 11.9 | 11.9
2018-06-29 21:00 | 11.54 | 11.53
2018-06-29 21:30 | 10.86 | 10.85
2018-06-29 22:00 | 10.26 | 10.25
2018-06-29 22:30 | 9.98 | 9.97
2018-06-29 23:00 | 9.54 | 9.53
2018-06-29 23:30 | 8.57 | 8.56
2018-06-30 | 7.66 | 7.65
2018-06-30 00:30 | 6.85 | 6.83
2018-06-30 01:00 | 6.33 | 6.31
2018-06-30 01:30 | 5.88 | 5.86
2018-06-30 02:00 | 5.39 | 5.36
2018-06-30 02:30 | 5.18 | 5.15
2018-06-30 03:00 | 5.02 | 4.98
2018-06-30 03:30 | 5.02 | 4.98
2018-06-30 04:00 | 4.92 | 4.88
2018-06-30 04:30 | 4.99 | 4.95
2018-06-30 05:00 | 5.16 | 5.13
2018-06-30 05:30 | 5.37 | 5.34
2018-06-30 06:00 | 5.56 | 5.52
2018-06-30 06:30 | 5.85 | 5.82
2018-06-30 07:00 | 6.39 | 6.34
2018-06-30 07:30 | 6.98 | 6.93
2018-06-30 08:00 | 7.43 | 7.4
2018-06-30 08:30 | 7.74 | 7.72
2018-06-30 09:00 | 8.08 | 8.07
2018-06-30 09:30 | 7.12 | 7.11
2018-06-30 10:00 | 7.59 | 7.58
2018-06-30 10:30 | 7.02 | 7
2018-06-30 11:00 | 6.61 | 6.6
2018-06-30 11:30 | 6.47 | 6.45
2018-06-30 12:00 | 6.34 | 6.32
2018-06-30 12:30 | 5.6 | 5.58
2018-06-30 13:00 | 5.09 | 5.07
2018-06-30 13:30 | 5.41 | 5.39
2018-06-30 14:00 | 5.95 | 5.94
2018-06-30 14:30 | 6.6 | 6.58
2018-06-30 15:00 | 6.66 | 6.64
2018-06-30 15:30 | 6.81 | 6.79
2018-06-30 16:00 | 7.09 | 7.08
2018-06-30 16:30 | 8.07 | 8.06
2018-06-30 17:00 | 9.18 | 9.17
2018-06-30 17:30 | 10.3 | 10.28
2018-06-30 18:00 | 10.9 | 10.89
2018-06-30 18:30 | 10.99 | 10.98
2018-06-30 19:00 | 10.92 | 10.91
2018-06-30 19:30 | 10.75 | 10.74
2018-06-30 20:00 | 10.76 | 10.75
2018-06-30 20:30 | 10.91 | 10.9
2018-06-30 21:00 | 10.46 | 10.45
2018-06-30 21:30 | 9.88 | 9.87
2018-06-30 22:00 | 9.42 | 9.41
2018-06-30 22:30 | 9.07 | 9.06
2018-06-30 23:00 | 8.76 | 8.75
2018-06-30 23:30 | 8.09 | 8.08
2018-07-01 | 7.36 | 7.34
2018-07-01 00:30 | 6.71 | 6.69
2018-07-01 01:00 | 6.45 | 6.42
2018-07-01 01:30 | 6.01 | 5.98
2018-07-01 02:00 | 5.56 | 5.53
2018-07-01 02:30 | 5.25 | 5.21
2018-07-01 03:00 | 4.82 | 4.78
2018-07-01 03:30 | 4.74 | 4.7
2018-07-01 04:00 | 4.63 | 4.59
2018-07-01 04:30 | 4.63 | 4.59
2018-07-01 05:00 | 4.89 | 4.85
2018-07-01 05:30 | 5.14 | 5.09
2018-07-01 06:00 | 5.38 | 5.34
2018-07-01 06:30 | 5.58 | 5.55
2018-07-01 07:00 | 5.7 | 5.64
2018-07-01 07:30 | 6.2 | 6.14
2018-07-01 08:00 | 6.5 | 6.44
2018-07-01 08:30 | 7.34 | 7.3
2018-07-01 09:00 | 7.71 | 7.68
2018-07-01 09:30 | 7.72 | 7.69
2018-07-01 10:00 | 7.2 | 7.18
2018-07-01 10:30 | 7.33 | 7.31
2018-07-01 11:00 | 7.69 | 7.68
2018-07-01 11:30 | 7.99 | 7.98
2018-07-01 12:00 | 7.98 | 7.97
2018-07-01 12:30 | 7.2 | 7.18
2018-07-01 13:00 | 7.18 | 7.17
2018-07-01 13:30 | 7.35 | 7.33
2018-07-01 14:00 | 7.77 | 7.75
2018-07-01 14:30 | 7.66 | 7.64
2018-07-01 15:00 | 7.82 | 7.8
2018-07-01 15:30 | 8.29 | 8.28
2018-07-01 16:00 | 8.47 | 8.45
2018-07-01 16:30 | 9.16 | 9.14
2018-07-01 17:00 | 10.05 | 10.04
2018-07-01 17:30 | 11.26 | 11.25
2018-07-01 18:00 | 12.21 | 12.19
2018-07-01 18:30 | 12.25 | 12.25
2018-07-01 19:00 | 11.92 | 11.91
2018-07-01 19:30 | 11.5 | 11.49
2018-07-01 20:00 | 11.43 | 11.43
2018-07-01 20:30 | 11.35 | 11.34
2018-07-01 21:00 | 10.71 | 10.7
2018-07-01 21:30 | 10.28 | 10.27
2018-07-01 22:00 | 9.53 | 9.52
2018-07-01 22:30 | 8.85 | 8.84
2018-07-01 23:00 | 8.56 | 8.55
2018-07-01 23:30 | 7.6 | 7.59
2018-07-02 | 6.68 | 6.66
2018-07-02 00:30 | 5.96 | 5.93
2018-07-02 01:00 | 5.6 | 5.57
2018-07-02 01:30 | 5.19 | 5.16
2018-07-02 02:00 | 4.79 | 4.75
2018-07-02 02:30 | 4.68 | 4.64
2018-07-02 03:00 | 4.62 | 4.57
2018-07-02 03:30 | 4.54 | 4.5
2018-07-02 04:00 | 4.58 | 4.54
2018-07-02 04:30 | 4.67 | 4.62
2018-07-02 05:00 | 5.12 | 5.09
2018-07-02 05:30 | 5.65 | 5.63
2018-07-02 06:00 | 6.51 | 6.5
2018-07-02 06:30 | 7.11 | 7.1
2018-07-02 07:00 | 7.13 | 7.11
2018-07-02 07:30 | 7.37 | 7.35
2018-07-02 08:00 | 6.95 | 6.92
2018-07-02 08:30 | 6.92 | 6.89
2018-07-02 09:00 | 6.9 | 6.88
2018-07-02 09:30 | 6.12 | 6.1
2018-07-02 10:00 | 5.69 | 5.67
2018-07-02 10:30 | 5.08 | 5.06
2018-07-02 11:00 | 4.76 | 4.75
2018-07-02 11:30 | 5.42 | 5.41
2018-07-02 12:00 | 5.77 | 5.76
2018-07-02 12:30 | 5.24 | 5.23
2018-07-02 13:00 | 6.52 | 6.51
2018-07-02 13:30 | 6.72 | 6.71
2018-07-02 14:00 | 5.97 | 5.95
2018-07-02 14:30 | 6.39 | 6.38
2018-07-02 15:00 | 5.63 | 5.62
2018-07-02 15:30 | 7.12 | 7.11
2018-07-02 16:00 | 7.77 | 7.76
2018-07-02 16:30 | 8.58 | 8.57
2018-07-02 17:00 | 10.14 | 10.14
2018-07-02 17:30 | 11.7 | 11.7
2018-07-02 18:00 | 12.44 | 12.44
2018-07-02 18:30 | 12.84 | 12.84
2018-07-02 19:00 | 12.89 | 12.89
2018-07-02 19:30 | 12.56 | 12.56
2018-07-02 20:00 | 12.23 | 12.23
2018-07-02 20:30 | 12.16 | 12.16
2018-07-02 21:00 | 11.64 | 11.63
2018-07-02 21:30 | 10.94 | 10.94
2018-07-02 22:00 | 10.11 | 10.11
2018-07-02 22:30 | 9.29 | 9.29
2018-07-02 23:00 | 8.89 | 8.88
2018-07-02 23:30 | 7.51 | 7.49
2018-07-03 | 7.06 | 7.03
2018-07-03 00:30 | 6.37 | 6.34
2018-07-03 01:00 | 5.94 | 5.9
2018-07-03 01:30 | 5.66 | 5.62
2018-07-03 02:00 | 5.28 | 5.24
2018-07-03 02:30 | 5.15 | 5.1
2018-07-03 03:00 | 5.02 | 4.97
2018-07-03 03:30 | 5.06 | 5.01
2018-07-03 04:00 | 5.18 | 5.13
2018-07-03 04:30 | 5.3 | 5.25
2018-07-03 05:00 | 5.72 | 5.68
2018-07-03 05:30 | 6.53 | 6.51
2018-07-03 06:00 | 7.28 | 7.27
2018-07-03 06:30 | 8.06 | 8.05
2018-07-03 07:00 | 8.56 | 8.55
2018-07-03 07:30 | 8.81 | 8.79
2018-07-03 08:00 | 8.23 | 8.21
2018-07-03 08:30 | 7.62 | 7.6
2018-07-03 09:00 | 6.94 | 6.91
2018-07-03 09:30 | 6.26 | 6.24
2018-07-03 10:00 | 5.64 | 5.62
2018-07-03 10:30 | 4.8 | 4.78
2018-07-03 11:00 | 4.46 | 4.44
2018-07-03 11:30 | 4.08 | 4.06
2018-07-03 12:00 | 4.33 | 4.31
2018-07-03 12:30 | 4.22 | 4.2
2018-07-03 13:00 | 4.11 | 4.1
2018-07-03 13:30 | 4.5 | 4.48
2018-07-03 14:00 | 4.95 | 4.93
2018-07-03 14:30 | 5.19 | 5.18
2018-07-03 15:00 | 5.81 | 5.8
2018-07-03 15:30 | 6.44 | 6.42
2018-07-03 16:00 | 7.35 | 7.33
2018-07-03 16:30 | 8.62 | 8.61
2018-07-03 17:00 | 9.86 | 9.86
2018-07-03 17:30 | 11.23 | 11.23
2018-07-03 18:00 | 12.76 | 12.76
2018-07-03 18:30 | 12.79 | 12.78
2018-07-03 19:00 | 13 | 12.99
2018-07-03 19:30 | 12.9 | 12.89
2018-07-03 20:00 | 12.67 | 12.66
2018-07-03 20:30 | 12.68 | 12.67
2018-07-03 21:00 | 12.08 | 12.07
2018-07-03 21:30 | 11.3 | 11.29
2018-07-03 22:00 | 10.4 | 10.39
2018-07-03 22:30 | 9.34 | 9.34
2018-07-03 23:00 | 8.79 | 8.78
2018-07-03 23:30 | 7.88 | 7.86
2018-07-04 | 6.87 | 6.84
2018-07-04 00:30 | 6.2 | 6.17
2018-07-04 01:00 | 5.62 | 5.59
2018-07-04 01:30 | 5.23 | 5.19
2018-07-04 02:00 | 4.94 | 4.9
2018-07-04 02:30 | 4.87 | 4.82
2018-07-04 03:00 | 4.75 | 4.7
2018-07-04 03:30 | 4.77 | 4.73
2018-07-04 04:00 | 4.8 | 4.76
2018-07-04 04:30 | 4.97 | 4.92
2018-07-04 05:00 | 5.34 | 5.3
2018-07-04 05:30 | 5.98 | 5.95
2018-07-04 06:00 | 6.49 | 6.48
2018-07-04 06:30 | 6.96 | 6.95
2018-07-04 07:00 | 7.49 | 7.46
2018-07-04 07:30 | 7.81 | 7.79
2018-07-04 08:00 | 8.06 | 8.04
2018-07-04 08:30 | 8.3 | 8.28
2018-07-04 09:00 | 7.96 | 7.93
2018-07-04 09:30 | 6.67 | 6.65
2018-07-04 10:00 | 5.9 | 5.87
2018-07-04 10:30 | 5.11 | 5.1
2018-07-04 11:00 | 5.07 | 5.05
2018-07-04 11:30 | 6.6 | 6.58
2018-07-04 12:00 | 5.66 | 5.64
2018-07-04 12:30 | 5.23 | 5.21
2018-07-04 13:00 | 4.76 | 4.75
2018-07-04 13:30 | 4.8 | 4.79
2018-07-04 14:00 | 4.7 | 4.69
2018-07-04 14:30 | 4.98 | 4.96
2018-07-04 15:00 | 5.73 | 5.71
2018-07-04 15:30 | 6.12 | 6.1
2018-07-04 16:00 | 6.94 | 6.93
2018-07-04 16:30 | 7.9 | 7.89
2018-07-04 17:00 | 9.16 | 9.16
2018-07-04 17:30 | 10.43 | 10.42
2018-07-04 18:00 | 11.67 | 11.66
2018-07-04 18:30 | 12.26 | 12.26
2018-07-04 19:00 | 12.46 | 12.45
2018-07-04 19:30 | 12.07 | 12.07
2018-07-04 20:00 | 11.98 | 11.98
2018-07-04 20:30 | 12.21 | 12.21
2018-07-04 21:00 | 11.75 | 11.74
2018-07-04 21:30 | 11.01 | 11.01
2018-07-04 22:00 | 10.24 | 10.23
2018-07-04 22:30 | 9.36 | 9.35
2018-07-04 23:00 | 8.75 | 8.74
2018-07-04 23:30 | 7.7 | 7.68
2018-07-05 | 6.75 | 6.73
2018-07-05 00:30 | 6.02 | 5.99
2018-07-05 01:00 | 5.58 | 5.55
2018-07-05 01:30 | 5.12 | 5.09
2018-07-05 02:00 | 4.83 | 4.79
2018-07-05 02:30 | 4.71 | 4.66
2018-07-05 03:00 | 4.46 | 4.41
2018-07-05 03:30 | 4.42 | 4.37
2018-07-05 04:00 | 4.55 | 4.5
2018-07-05 04:30 | 4.68 | 4.64
2018-07-05 05:00 | 4.97 | 4.93
2018-07-05 05:30 | 5.59 | 5.56
2018-07-05 06:00 | 6.32 | 6.3
2018-07-05 06:30 | 6.7 | 6.69
2018-07-05 07:00 | 7.04 | 7.01
2018-07-05 07:30 | 7.17 | 7.14
2018-07-05 08:00 | 7.2 | 7.17
2018-07-05 08:30 | 6.58 | 6.56
2018-07-05 09:00 | 5.86 | 5.83
2018-07-05 09:30 | 5.83 | 5.81
2018-07-05 10:00 | 5.24 | 5.22
2018-07-05 10:30 | 6.77 | 6.75
2018-07-05 11:00 | 7.24 | 7.23
2018-07-05 11:30 | 5.99 | 5.97
2018-07-05 12:00 | 7.46 | 7.45
2018-07-05 12:30 | 5.85 | 5.84
2018-07-05 13:00 | 6.11 | 6.09
2018-07-05 13:30 | 6.91 | 6.9
2018-07-05 14:00 | 6.82 | 6.8
2018-07-05 14:30 | 6.99 | 6.98
2018-07-05 15:00 | 7.73 | 7.72
2018-07-05 15:30 | 7.58 | 7.57
2018-07-05 16:00 | 7.88 | 7.87
2018-07-05 16:30 | 8.51 | 8.5
2018-07-05 17:00 | 9.69 | 9.68
2018-07-05 17:30 | 11.29 | 11.29
2018-07-05 18:00 | 11.96 | 11.95
2018-07-05 18:30 | 11.86 | 11.85
2018-07-05 19:00 | 11.71 | 11.7
2018-07-05 19:30 | 11.39 | 11.39
2018-07-05 20:00 | 11.4 | 11.39
2018-07-05 20:30 | 11.41 | 11.4
2018-07-05 21:00 | 10.88 | 10.87
2018-07-05 21:30 | 10.14 | 10.13
2018-07-05 22:00 | 9.42 | 9.41
2018-07-05 22:30 | 8.97 | 8.96
2018-07-05 23:00 | 8.52 | 8.51
2018-07-05 23:30 | 7.64 | 7.63
2018-07-06 | 6.6 | 6.58
2018-07-06 00:30 | 5.85 | 5.82
2018-07-06 01:00 | 5.47 | 5.44
2018-07-06 01:30 | 5.07 | 5.04
2018-07-06 02:00 | 4.8 | 4.76
2018-07-06 02:30 | 4.58 | 4.54
2018-07-06 03:00 | 4.41 | 4.36
2018-07-06 03:30 | 4.47 | 4.43
2018-07-06 04:00 | 4.44 | 4.4
2018-07-06 04:30 | 4.66 | 4.62
2018-07-06 05:00 | 4.93 | 4.89
2018-07-06 05:30 | 5.35 | 5.32
2018-07-06 06:00 | 5.7 | 5.68
2018-07-06 06:30 | 6.01 | 5.99
2018-07-06 07:00 | 6.21 | 6.18
2018-07-06 07:30 | 6.47 | 6.44
2018-07-06 08:00 | 6.21 | 6.17
2018-07-06 08:30 | 5.78 | 5.74
2018-07-06 09:00 | 5.9 | 5.87
2018-07-06 09:30 | 6.34 | 6.32
2018-07-06 10:00 | 6.89 | 6.87
2018-07-06 10:30 | 6.72 | 6.7
2018-07-06 11:00 | 6.71 | 6.7
2018-07-06 11:30 | 5.1 | 5.08
2018-07-06 12:00 | 4.28 | 4.25
2018-07-06 12:30 | 4.67 | 4.64
2018-07-06 13:00 | 5.43 | 5.41
2018-07-06 13:30 | 6.99 | 6.97
2018-07-06 14:00 | 6.67 | 6.65
2018-07-06 14:30 | 6.32 | 6.29
2018-07-06 15:00 | 7.45 | 7.43
2018-07-06 15:30 | 7.28 | 7.25
2018-07-06 16:00 | 8.03 | 8.01
2018-07-06 16:30 | 8.29 | 8.27
2018-07-06 17:00 | 9.41 | 9.39
2018-07-06 17:30 | 10.44 | 10.42
2018-07-06 18:00 | 10.96 | 10.94
2018-07-06 18:30 | 11.06 | 11.04
2018-07-06 19:00 | 11.07 | 11.06
2018-07-06 19:30 | 10.73 | 10.72
2018-07-06 20:00 | 10.83 | 10.82
2018-07-06 20:30 | 10.77 | 10.76
2018-07-06 21:00 | 10.31 | 10.3
2018-07-06 21:30 | 9.77 | 9.76
2018-07-06 22:00 | 9.01 | 9
2018-07-06 22:30 | 8.57 | 8.57
2018-07-06 23:00 | 8.73 | 8.72
2018-07-06 23:30 | 7.73 | 7.72
2018-07-07 | 6.8 | 6.78
2018-07-07 00:30 | 6.1 | 6.08
2018-07-07 01:00 | 5.65 | 5.62
2018-07-07 01:30 | 5.3 | 5.27
2018-07-07 02:00 | 4.84 | 4.81
2018-07-07 02:30 | 4.57 | 4.53
2018-07-07 03:00 | 4.41 | 4.37
2018-07-07 03:30 | 4.47 | 4.43
2018-07-07 04:00 | 4.44 | 4.4
2018-07-07 04:30 | 4.37 | 4.33
2018-07-07 05:00 | 4.45 | 4.4
2018-07-07 05:30 | 4.71 | 4.68
2018-07-07 06:00 | 4.82 | 4.79
2018-07-07 06:30 | 5.05 | 5.02
2018-07-07 07:00 | 5.19 | 5.14
2018-07-07 07:30 | 5.87 | 5.82
2018-07-07 08:00 | 6.25 | 6.19
2018-07-07 08:30 | 6.94 | 6.91
2018-07-07 09:00 | 6.82 | 6.79
2018-07-07 09:30 | 6.69 | 6.67
2018-07-07 10:00 | 6.14 | 6.13
2018-07-07 10:30 | 7.2 | 7.18
2018-07-07 11:00 | 6.36 | 6.33
2018-07-07 11:30 | 7.18 | 7.16
2018-07-07 12:00 | 7.8 | 7.79
2018-07-07 12:30 | 8.47 | 8.46
2018-07-07 13:00 | 7.8 | 7.78
2018-07-07 13:30 | 7.41 | 7.39
2018-07-07 14:00 | 6.69 | 6.67
2018-07-07 14:30 | 5.82 | 5.79
2018-07-07 15:00 | 7.07 | 7.05
2018-07-07 15:30 | 7.87 | 7.85
2018-07-07 16:00 | 7.21 | 7.19
2018-07-07 16:30 | 8.01 | 8
2018-07-07 17:00 | 8.82 | 8.81
2018-07-07 17:30 | 9.83 | 9.82
2018-07-07 18:00 | 10.87 | 10.86
2018-07-07 18:30 | 11 | 11
2018-07-07 19:00 | 10.97 | 10.96
2018-07-07 19:30 | 10.81 | 10.81
2018-07-07 20:00 | 10.8 | 10.79
2018-07-07 20:30 | 10.83 | 10.83
2018-07-07 21:00 | 10.31 | 10.3
2018-07-07 21:30 | 9.64 | 9.63
2018-07-07 22:00 | 9.26 | 9.25
2018-07-07 22:30 | 8.98 | 8.97
2018-07-07 23:00 | 8.95 | 8.94
2018-07-07 23:30 | 8.2 | 8.19
2018-07-08 | 7.36 | 7.35
2018-07-08 00:30 | 6.73 | 6.71
2018-07-08 01:00 | 6.21 | 6.19
2018-07-08 01:30 | 5.86 | 5.83
2018-07-08 02:00 | 5.41 | 5.37
2018-07-08 02:30 | 5.27 | 5.23
2018-07-08 03:00 | 5 | 4.96
2018-07-08 03:30 | 4.94 | 4.89
2018-07-08 04:00 | 4.93 | 4.88
2018-07-08 04:30 | 4.89 | 4.85
2018-07-08 05:00 | 5.12 | 5.08
2018-07-08 05:30 | 5.22 | 5.18
2018-07-08 06:00 | 5.53 | 5.5
2018-07-08 06:30 | 5.76 | 5.72
2018-07-08 07:00 | 6.12 | 6.07
2018-07-08 07:30 | 6.7 | 6.65
2018-07-08 08:00 | 6.87 | 6.84
2018-07-08 08:30 | 7.08 | 7.05
2018-07-08 09:00 | 7.13 | 7.11
2018-07-08 09:30 | 6.95 | 6.93
2018-07-08 10:00 | 6.53 | 6.51
2018-07-08 10:30 | 5.84 | 5.82
2018-07-08 11:00 | 5.39 | 5.37
2018-07-08 11:30 | 4.95 | 4.93
2018-07-08 12:00 | 4.81 | 4.79
2018-07-08 12:30 | 4.72 | 4.7
2018-07-08 13:00 | 4.63 | 4.6
2018-07-08 13:30 | 4.79 | 4.76
2018-07-08 14:00 | 5.06 | 5.03
2018-07-08 14:30 | 5.31 | 5.28
2018-07-08 15:00 | 5.62 | 5.59
2018-07-08 15:30 | 6.33 | 6.3
2018-07-08 16:00 | 7.28 | 7.25
2018-07-08 16:30 | 8.44 | 8.42
2018-07-08 17:00 | 10 | 9.99
2018-07-08 17:30 | 11.52 | 11.51
2018-07-08 18:00 | 12.82 | 12.81
2018-07-08 18:30 | 13.04 | 13.03
2018-07-08 19:00 | 13.08 | 13.07
2018-07-08 19:30 | 12.93 | 12.92
2018-07-08 20:00 | 12.9 | 12.89
2018-07-08 20:30 | 12.95 | 12.94
2018-07-08 21:00 | 12.35 | 12.35
2018-07-08 21:30 | 11.61 | 11.6
2018-07-08 22:00 | 10.95 | 10.94
2018-07-08 22:30 | 10.53 | 10.52
2018-07-08 23:00 | 10.03 | 10.02
2018-07-08 23:30 | 8.91 | 8.9
2018-07-09 | 7.87 | 7.85
2018-07-09 00:30 | 7.07 | 7.05
2018-07-09 01:00 | 6.6 | 6.58
2018-07-09 01:30 | 6.08 | 6.05
2018-07-09 02:00 | 5.7 | 5.66
2018-07-09 02:30 | 5.54 | 5.5
2018-07-09 03:00 | 5.46 | 5.42
2018-07-09 03:30 | 5.53 | 5.49
2018-07-09 04:00 | 5.69 | 5.66
2018-07-09 04:30 | 5.94 | 5.9
2018-07-09 05:00 | 6.48 | 6.46
2018-07-09 05:30 | 7.34 | 7.33
2018-07-09 06:00 | 8.39 | 8.39
2018-07-09 06:30 | 9.12 | 9.12
2018-07-09 07:00 | 9.62 | 9.61
2018-07-09 07:30 | 9.94 | 9.94
2018-07-09 08:00 | 9.54 | 9.54
2018-07-09 08:30 | 8.87 | 8.86
2018-07-09 09:00 | 8.02 | 8.02
2018-07-09 09:30 | 7.28 | 7.27
2018-07-09 10:00 | 6.29 | 6.28
2018-07-09 10:30 | 5.39 | 5.37
2018-07-09 11:00 | 4.82 | 4.79
2018-07-09 11:30 | 4.57 | 4.54
2018-07-09 12:00 | 4.23 | 4.2
2018-07-09 12:30 | 3.94 | 3.9
2018-07-09 13:00 | 4.25 | 4.22
2018-07-09 13:30 | 4.78 | 4.75
2018-07-09 14:00 | 5.11 | 5.08
2018-07-09 14:30 | 5.68 | 5.66
2018-07-09 15:00 | 5.52 | 5.49
2018-07-09 15:30 | 6.84 | 6.82
2018-07-09 16:00 | 7.36 | 7.35
2018-07-09 16:30 | 8.08 | 8.07
2018-07-09 17:00 | 9.6 | 9.59
2018-07-09 17:30 | 11.85 | 11.85
2018-07-09 18:00 | 13.92 | 13.91
2018-07-09 18:30 | 14.56 | 14.54
2018-07-09 19:00 | 14.76 | 14.75
2018-07-09 19:30 | 14.89 | 14.88
2018-07-09 20:00 | 14.83 | 14.82
2018-07-09 20:30 | 14.85 | 14.84
2018-07-09 21:00 | 14.32 | 14.32
2018-07-09 21:30 | 13.39 | 13.39
2018-07-09 22:00 | 12.41 | 12.41
2018-07-09 22:30 | 11.28 | 11.27
2018-07-09 23:00 | 10.46 | 10.45
2018-07-09 23:30 | 9.21 | 9.2
2018-07-10 | 8.15 | 8.14
2018-07-10 00:30 | 7.45 | 7.43
2018-07-10 01:00 | 7.02 | 7
2018-07-10 01:30 | 6.71 | 6.68
2018-07-10 02:00 | 6.17 | 6.14
2018-07-10 02:30 | 5.93 | 5.9
2018-07-10 03:00 | 5.79 | 5.75
2018-07-10 03:30 | 5.82 | 5.79
2018-07-10 04:00 | 5.9 | 5.87
2018-07-10 04:30 | 6.19 | 6.16
2018-07-10 05:00 | 6.84 | 6.82
2018-07-10 05:30 | 7.74 | 7.73
2018-07-10 06:00 | 8.76 | 8.76
2018-07-10 06:30 | 9.35 | 9.35
2018-07-10 07:00 | 10.11 | 10.1
2018-07-10 07:30 | 10.34 | 10.34
2018-07-10 08:00 | 10.23 | 10.22
2018-07-10 08:30 | 9.67 | 9.66
2018-07-10 09:00 | 9.55 | 9.55
2018-07-10 09:30 | 7.99 | 7.98
2018-07-10 10:00 | 7.38 | 7.37
2018-07-10 10:30 | 6.86 | 6.85
2018-07-10 11:00 | 5.55 | 5.54
2018-07-10 11:30 | 5.1 | 5.08
2018-07-10 12:00 | 4.59 | 4.57
2018-07-10 12:30 | 4.35 | 4.32
2018-07-10 13:00 | 4.37 | 4.35
2018-07-10 13:30 | 4.45 | 4.42
2018-07-10 14:00 | 4.69 | 4.66
2018-07-10 14:30 | 4.94 | 4.91
2018-07-10 15:00 | 5.5 | 5.48
2018-07-10 15:30 | 6.77 | 6.74
2018-07-10 16:00 | 8.34 | 8.33
2018-07-10 16:30 | 9.14 | 9.13
2018-07-10 17:00 | 10.53 | 10.52
2018-07-10 17:30 | 12.25 | 12.25
2018-07-10 18:00 | 13.62 | 13.61
2018-07-10 18:30 | 14.24 | 14.23
2018-07-10 19:00 | 14.31 | 14.3
2018-07-10 19:30 | 14.29 | 14.28
2018-07-10 20:00 | 14.22 | 14.22
2018-07-10 20:30 | 14.12 | 14.12
2018-07-10 21:00 | 13.7 | 13.7
2018-07-10 21:30 | 12.96 | 12.95
2018-07-10 22:00 | 12.21 | 12.21
2018-07-10 22:30 | 11.15 | 11.15
2018-07-10 23:00 | 10.32 | 10.32
2018-07-10 23:30 | 9.18 | 9.17
2018-07-11 | 8.03 | 8.02
2018-07-11 00:30 | 7.18 | 7.16
2018-07-11 01:00 | 6.7 | 6.68
2018-07-11 01:30 | 6.31 | 6.28
2018-07-11 02:00 | 5.94 | 5.9
2018-07-11 02:30 | 5.74 | 5.7
2018-07-11 03:00 | 5.69 | 5.65
2018-07-11 03:30 | 5.68 | 5.64
2018-07-11 04:00 | 5.83 | 5.79
2018-07-11 04:30 | 6.14 | 6.11
2018-07-11 05:00 | 6.75 | 6.73
2018-07-11 05:30 | 7.53 | 7.52
2018-07-11 06:00 | 8.61 | 8.61
2018-07-11 06:30 | 9.4 | 9.39
2018-07-11 07:00 | 10.15 | 10.14
2018-07-11 07:30 | 10.44 | 10.44
2018-07-11 08:00 | 9.57 | 9.57
2018-07-11 08:30 | 8.69 | 8.68
2018-07-11 09:00 | 7.87 | 7.86
2018-07-11 09:30 | 7.18 | 7.17
2018-07-11 10:00 | 7.1 | 7.09
2018-07-11 10:30 | 5.65 | 5.64
2018-07-11 11:00 | 5.22 | 5.21
2018-07-11 11:30 | 6.58 | 6.56
2018-07-11 12:00 | 5.23 | 5.21
2018-07-11 12:30 | 5.49 | 5.47
2018-07-11 13:00 | 5.8 | 5.77
2018-07-11 13:30 | 6.85 | 6.83
2018-07-11 14:00 | 8.12 | 8.1
2018-07-11 14:30 | 8.1 | 8.09
2018-07-11 15:00 | 7.97 | 7.95
2018-07-11 15:30 | 8.12 | 8.1
2018-07-11 16:00 | 9.12 | 9.11
2018-07-11 16:30 | 10 | 9.99
2018-07-11 17:00 | 11.45 | 11.45
2018-07-11 17:30 | 13.1 | 13.1
2018-07-11 18:00 | 13.78 | 13.77
2018-07-11 18:30 | 13.96 | 13.96
2018-07-11 19:00 | 14.22 | 14.22
2018-07-11 19:30 | 14.11 | 14.11
2018-07-11 20:00 | 14.16 | 14.15
2018-07-11 20:30 | 13.99 | 13.99
2018-07-11 21:00 | 13.14 | 13.13
2018-07-11 21:30 | 12.37 | 12.36
2018-07-11 22:00 | 11.47 | 11.47
2018-07-11 22:30 | 10.5 | 10.5
2018-07-11 23:00 | 9.85 | 9.84
2018-07-11 23:30 | 8.66 | 8.64
2018-07-12 | 7.49 | 7.47
2018-07-12 00:30 | 6.72 | 6.69
2018-07-12 01:00 | 6.3 | 6.27
2018-07-12 01:30 | 5.72 | 5.69
2018-07-12 02:00 | 5.32 | 5.28
2018-07-12 02:30 | 5.16 | 5.12
2018-07-12 03:00 | 4.98 | 4.94
2018-07-12 03:30 | 4.99 | 4.95
2018-07-12 04:00 | 5.11 | 5.07
2018-07-12 04:30 | 5.39 | 5.35
2018-07-12 05:00 | 5.77 | 5.74
2018-07-12 05:30 | 6.46 | 6.44
2018-07-12 06:00 | 7.21 | 7.19
2018-07-12 06:30 | 7.7 | 7.69
2018-07-12 07:00 | 8.07 | 8.05
2018-07-12 07:30 | 8.24 | 8.22
2018-07-12 08:00 | 8.1 | 8.08
2018-07-12 08:30 | 7.39 | 7.37
2018-07-12 09:00 | 7.13 | 7.11
2018-07-12 09:30 | 6.97 | 6.95
2018-07-12 10:00 | 6.9 | 6.89
2018-07-12 10:30 | 6.22 | 6.2
2018-07-12 11:00 | 5.03 | 5.01
2018-07-12 11:30 | 4.91 | 4.89
2018-07-12 12:00 | 4.32 | 4.3
2018-07-12 12:30 | 4.44 | 4.42
2018-07-12 13:00 | 4.63 | 4.6
2018-07-12 13:30 | 4.36 | 4.33
2018-07-12 14:00 | 5.13 | 5.11
2018-07-12 14:30 | 4.66 | 4.63
2018-07-12 15:00 | 5.46 | 5.43
2018-07-12 15:30 | 5.5 | 5.48
2018-07-12 16:00 | 6.4 | 6.38
2018-07-12 16:30 | 7.5 | 7.49
2018-07-12 17:00 | 8.96 | 8.96
2018-07-12 17:30 | 10.25 | 10.25
2018-07-12 18:00 | 11.51 | 11.51
2018-07-12 18:30 | 12.11 | 12.1
2018-07-12 19:00 | 12.36 | 12.36
2018-07-12 19:30 | 12.51 | 12.51
2018-07-12 20:00 | 12.73 | 12.72
2018-07-12 20:30 | 12.86 | 12.85
2018-07-12 21:00 | 12.33 | 12.32
2018-07-12 21:30 | 11.71 | 11.7
2018-07-12 22:00 | 11.07 | 11.07
2018-07-12 22:30 | 10.48 | 10.47
2018-07-12 23:00 | 10.04 | 10.03
2018-07-12 23:30 | 8.81 | 8.8
2018-07-13 | 7.69 | 7.67
2018-07-13 00:30 | 6.79 | 6.77
2018-07-13 01:00 | 6.38 | 6.35
2018-07-13 01:30 | 6.03 | 6
2018-07-13 02:00 | 5.68 | 5.65
2018-07-13 02:30 | 5.47 | 5.44
2018-07-13 03:00 | 5.31 | 5.27
2018-07-13 03:30 | 5.32 | 5.28
2018-07-13 04:00 | 5.37 | 5.33
2018-07-13 04:30 | 5.58 | 5.55
2018-07-13 05:00 | 5.98 | 5.96
2018-07-13 05:30 | 6.69 | 6.67
2018-07-13 06:00 | 7.35 | 7.34
2018-07-13 06:30 | 7.78 | 7.77
2018-07-13 07:00 | 8.22 | 8.2
2018-07-13 07:30 | 8.53 | 8.51
2018-07-13 08:00 | 8.01 | 7.99
2018-07-13 08:30 | 7.33 | 7.31
2018-07-13 09:00 | 6.7 | 6.68
2018-07-13 09:30 | 6.08 | 6.06
2018-07-13 10:00 | 5.36 | 5.33
2018-07-13 10:30 | 4.68 | 4.65
2018-07-13 11:00 | 4.26 | 4.23
2018-07-13 11:30 | 3.88 | 3.85
2018-07-13 12:00 | 3.55 | 3.52
2018-07-13 12:30 | 3.49 | 3.45
2018-07-13 13:00 | 3.47 | 3.43
2018-07-13 13:30 | 3.49 | 3.45
2018-07-13 14:00 | 3.77 | 3.74
2018-07-13 14:30 | 4.17 | 4.14
2018-07-13 15:00 | 4.57 | 4.53
2018-07-13 15:30 | 6.29 | 6.26
2018-07-13 16:00 | 6.61 | 6.59
2018-07-13 16:30 | 7.22 | 7.2
2018-07-13 17:00 | 8.78 | 8.76
2018-07-13 17:30 | 10.48 | 10.47
2018-07-13 18:00 | 11.89 | 11.88
2018-07-13 18:30 | 12.74 | 12.74
2018-07-13 19:00 | 13.19 | 13.19
2018-07-13 19:30 | 13.28 | 13.27
2018-07-13 20:00 | 13.63 | 13.62
2018-07-13 20:30 | 13.95 | 13.95
2018-07-13 21:00 | 13.71 | 13.7
2018-07-13 21:30 | 13.32 | 13.31
2018-07-13 22:00 | 12.66 | 12.65
2018-07-13 22:30 | 12.19 | 12.18
2018-07-13 23:00 | 11.96 | 11.96
2018-07-13 23:30 | 10.94 | 10.94
2018-07-14 | 9.69 | 9.68
2018-07-14 00:30 | 8.8 | 8.79
2018-07-14 01:00 | 8.25 | 8.24
2018-07-14 01:30 | 7.61 | 7.59
2018-07-14 02:00 | 7.18 | 7.17
2018-07-14 02:30 | 6.91 | 6.89
2018-07-14 03:00 | 6.62 | 6.6
2018-07-14 03:30 | 6.67 | 6.65
2018-07-14 04:00 | 6.55 | 6.53
2018-07-14 04:30 | 6.67 | 6.65
2018-07-14 05:00 | 6.93 | 6.92
2018-07-14 05:30 | 7.31 | 7.3
2018-07-14 06:00 | 7.66 | 7.65
2018-07-14 06:30 | 8.29 | 8.28
2018-07-14 07:00 | 9.19 | 9.18
2018-07-14 07:30 | 10.13 | 10.13
2018-07-14 08:00 | 10.45 | 10.44
2018-07-14 08:30 | 10.44 | 10.44
2018-07-14 09:00 | 10.19 | 10.18
2018-07-14 09:30 | 9.5 | 9.48
2018-07-14 10:00 | 8.4 | 8.38
2018-07-14 10:30 | 7.44 | 7.42
2018-07-14 11:00 | 6.61 | 6.59
2018-07-14 11:30 | 5.9 | 5.88
2018-07-14 12:00 | 5.23 | 5.21
2018-07-14 12:30 | 4.96 | 4.93
2018-07-14 13:00 | 4.69 | 4.67
2018-07-14 13:30 | 4.7 | 4.67
2018-07-14 14:00 | 4.99 | 4.96
2018-07-14 14:30 | 5.12 | 5.09
2018-07-14 15:00 | 5.55 | 5.51
2018-07-14 15:30 | 6.18 | 6.15
2018-07-14 16:00 | 7 | 6.97
2018-07-14 16:30 | 8.1 | 8.08
2018-07-14 17:00 | 9.65 | 9.63
2018-07-14 17:30 | 11.25 | 11.25
2018-07-14 18:00 | 12.74 | 12.73
2018-07-14 18:30 | 13.52 | 13.51
2018-07-14 19:00 | 14.02 | 14.01
2018-07-14 19:30 | 13.99 | 13.98
2018-07-14 20:00 | 14.28 | 14.27
2018-07-14 20:30 | 14.49 | 14.48
2018-07-14 21:00 | 14.2 | 14.19
2018-07-14 21:30 | 13.85 | 13.84
2018-07-14 22:00 | 13.3 | 13.29
2018-07-14 22:30 | 12.74 | 12.73
2018-07-14 23:00 | 12.25 | 12.25
2018-07-14 23:30 | 11.29 | 11.29
2018-07-15 | 10.19 | 10.19
2018-07-15 00:30 | 9.41 | 9.41
2018-07-15 01:00 | 8.72 | 8.71
2018-07-15 01:30 | 8.09 | 8.08
2018-07-15 02:00 | 7.63 | 7.62
2018-07-15 02:30 | 7.34 | 7.33
2018-07-15 03:00 | 7.11 | 7.09
2018-07-15 03:30 | 6.94 | 6.93
2018-07-15 04:00 | 6.85 | 6.83
2018-07-15 04:30 | 6.91 | 6.89
2018-07-15 05:00 | 7.01 | 6.99
2018-07-15 05:30 | 7.31 | 7.29
2018-07-15 06:00 | 7.81 | 7.8
2018-07-15 06:30 | 8.19 | 8.18
2018-07-15 07:00 | 8.73 | 8.71
2018-07-15 07:30 | 9.62 | 9.61
2018-07-15 08:00 | 10.34 | 10.34
2018-07-15 08:30 | 10.67 | 10.66
2018-07-15 09:00 | 10.52 | 10.51
2018-07-15 09:30 | 10.01 | 10
2018-07-15 10:00 | 8.94 | 8.92
2018-07-15 10:30 | 8 | 7.98
2018-07-15 11:00 | 7.11 | 7.1
2018-07-15 11:30 | 6.44 | 6.43
2018-07-15 12:00 | 5.95 | 5.93
2018-07-15 12:30 | 5.39 | 5.37
2018-07-15 13:00 | 5.08 | 5.05
2018-07-15 13:30 | 5.07 | 5.04
2018-07-15 14:00 | 5.29 | 5.26
2018-07-15 14:30 | 5.7 | 5.67
2018-07-15 15:00 | 6.17 | 6.14
2018-07-15 15:30 | 6.83 | 6.8
2018-07-15 16:00 | 7.67 | 7.65
2018-07-15 16:30 | 8.86 | 8.84
2018-07-15 17:00 | 10.54 | 10.53
2018-07-15 17:30 | 12.48 | 12.47
2018-07-15 18:00 | 14.2 | 14.19
2018-07-15 18:30 | 14.73 | 14.72
2018-07-15 19:00 | 15.04 | 15.03
2018-07-15 19:30 | 14.96 | 14.95
2018-07-15 20:00 | 14.85 | 14.84
2018-07-15 20:30 | 14.94 | 14.93
2018-07-15 21:00 | 14.14 | 14.13
2018-07-15 21:30 | 13.25 | 13.24
2018-07-15 22:00 | 12.22 | 12.21
2018-07-15 22:30 | 11.28 | 11.27
2018-07-15 23:00 | 10.78 | 10.77
2018-07-15 23:30 | 9.72 | 9.71
2018-07-16 | 8.59 | 8.58
2018-07-16 00:30 | 7.77 | 7.76
2018-07-16 01:00 | 7.29 | 7.27
2018-07-16 01:30 | 6.88 | 6.86
2018-07-16 02:00 | 6.46 | 6.44
2018-07-16 02:30 | 6.29 | 6.27
2018-07-16 03:00 | 6.17 | 6.14
2018-07-16 03:30 | 6.18 | 6.15
2018-07-16 04:00 | 6.28 | 6.26
2018-07-16 04:30 | 6.57 | 6.55
2018-07-16 05:00 | 7.13 | 7.11
2018-07-16 05:30 | 7.92 | 7.91
2018-07-16 06:00 | 8.99 | 8.99
2018-07-16 06:30 | 10.04 | 10.03
2018-07-16 07:00 | 11.14 | 11.13
2018-07-16 07:30 | 12 | 11.99
2018-07-16 08:00 | 11.25 | 11.24
2018-07-16 08:30 | 9.41 | 9.4
2018-07-16 09:00 | 8.33 | 8.32
2018-07-16 09:30 | 7.52 | 7.52
2018-07-16 10:00 | 6.51 | 6.5
2018-07-16 10:30 | 5.83 | 5.82
2018-07-16 11:00 | 4.7 | 4.68
2018-07-16 11:30 | 4.65 | 4.64
2018-07-16 12:00 | 4.44 | 4.43
2018-07-16 12:30 | 4.15 | 4.13
2018-07-16 13:00 | 4.09 | 4.07
2018-07-16 13:30 | 4.2 | 4.18
2018-07-16 14:00 | 4.48 | 4.46
2018-07-16 14:30 | 4.98 | 4.96
2018-07-16 15:00 | 4.77 | 4.75
2018-07-16 15:30 | 5.7 | 5.69
2018-07-16 16:00 | 7.22 | 7.2
2018-07-16 16:30 | 8.92 | 8.91
2018-07-16 17:00 | 10.26 | 10.25
2018-07-16 17:30 | 11.87 | 11.86
2018-07-16 18:00 | 13.61 | 13.6
2018-07-16 18:30 | 14.37 | 14.36
2018-07-16 19:00 | 14.78 | 14.77
2018-07-16 19:30 | 14.64 | 14.63
2018-07-16 20:00 | 15.09 | 15.08
2018-07-16 20:30 | 15.22 | 15.21
2018-07-16 21:00 | 14.71 | 14.7
2018-07-16 21:30 | 13.74 | 13.73
2018-07-16 22:00 | 12.63 | 12.62
2018-07-16 22:30 | 11.31 | 11.3
2018-07-16 23:00 | 10.66 | 10.66
2018-07-16 23:30 | 9.6 | 9.59
2018-07-17 | 8.59 | 8.58
2018-07-17 00:30 | 7.61 | 7.6
2018-07-17 01:00 | 7.17 | 7.16
2018-07-17 01:30 | 6.68 | 6.66
2018-07-17 02:00 | 6.26 | 6.24
2018-07-17 02:30 | 6.14 | 6.11
2018-07-17 03:00 | 6.16 | 6.13
2018-07-17 03:30 | 6.28 | 6.25
2018-07-17 04:00 | 6.38 | 6.36
2018-07-17 04:30 | 6.64 | 6.62
2018-07-17 05:00 | 7.45 | 7.43
2018-07-17 05:30 | 8.58 | 8.57
2018-07-17 06:00 | 9.84 | 9.83
2018-07-17 06:30 | 11.06 | 11.05
2018-07-17 07:00 | 12.01 | 12
2018-07-17 07:30 | 12.83 | 12.82
2018-07-17 08:00 | 11.93 | 11.93
2018-07-17 08:30 | 10.05 | 10.04
2018-07-17 09:00 | 8.28 | 8.27
2018-07-17 09:30 | 7.09 | 7.08
2018-07-17 10:00 | 6.12 | 6.1
2018-07-17 10:30 | 5.19 | 5.17
2018-07-17 11:00 | 4.65 | 4.63
2018-07-17 11:30 | 4.18 | 4.16
2018-07-17 12:00 | 3.72 | 3.69
2018-07-17 12:30 | 3.54 | 3.5
2018-07-17 13:00 | 3.61 | 3.58
2018-07-17 13:30 | 3.98 | 3.95
2018-07-17 14:00 | 4.35 | 4.32
2018-07-17 14:30 | 4.5 | 4.48
2018-07-17 15:00 | 5.75 | 5.72
2018-07-17 15:30 | 6.41 | 6.39
2018-07-17 16:00 | 8.3 | 8.28
2018-07-17 16:30 | 9.55 | 9.53
2018-07-17 17:00 | 10.97 | 10.96
2018-07-17 17:30 | 11.7 | 11.7
2018-07-17 18:00 | 13.71 | 13.69
2018-07-17 18:30 | 14.44 | 14.42
2018-07-17 19:00 | 15.21 | 15.2
2018-07-17 19:30 | 15.36 | 15.34
2018-07-17 20:00 | 15.55 | 15.53
2018-07-17 20:30 | 15.5 | 15.49
2018-07-17 21:00 | 14.93 | 14.92
2018-07-17 21:30 | 14.2 | 14.19
2018-07-17 22:00 | 13.03 | 13.03
2018-07-17 22:30 | 11.79 | 11.79
2018-07-17 23:00 | 10.97 | 10.97
2018-07-17 23:30 | 9.81 | 9.81
2018-07-18 | 8.61 | 8.6
2018-07-18 00:30 | 7.58 | 7.57
2018-07-18 01:00 | 7.14 | 7.12
2018-07-18 01:30 | 6.78 | 6.76
2018-07-18 02:00 | 6.41 | 6.39
2018-07-18 02:30 | 6.33 | 6.31
2018-07-18 03:00 | 6.25 | 6.23
2018-07-18 03:30 | 6.33 | 6.31
2018-07-18 04:00 | 6.48 | 6.46
2018-07-18 04:30 | 6.74 | 6.72
2018-07-18 05:00 | 7.42 | 7.4
2018-07-18 05:30 | 8.54 | 8.54
2018-07-18 06:00 | 9.97 | 9.97
2018-07-18 06:30 | 11.48 | 11.48
2018-07-18 07:00 | 12.83 | 12.83
2018-07-18 07:30 | 13.57 | 13.57
2018-07-18 08:00 | 12.72 | 12.72
2018-07-18 08:30 | 10.73 | 10.72
2018-07-18 09:00 | 8.84 | 8.84
2018-07-18 09:30 | 7.69 | 7.69
2018-07-18 10:00 | 6.66 | 6.65
2018-07-18 10:30 | 5.63 | 5.62
2018-07-18 11:00 | 5.16 | 5.15
2018-07-18 11:30 | 4.66 | 4.64
2018-07-18 12:00 | 4.67 | 4.66
2018-07-18 12:30 | 4.39 | 4.37
2018-07-18 13:00 | 3.96 | 3.93
2018-07-18 13:30 | 3.85 | 3.82
2018-07-18 14:00 | 4.02 | 4
2018-07-18 14:30 | 4.44 | 4.42
2018-07-18 15:00 | 4.8 | 4.78
2018-07-18 15:30 | 5.6 | 5.59
2018-07-18 16:00 | 6.7 | 6.69
2018-07-18 16:30 | 7.95 | 7.94
2018-07-18 17:00 | 9.5 | 9.49
2018-07-18 17:30 | 10.96 | 10.96
2018-07-18 18:00 | 12.87 | 12.86
2018-07-18 18:30 | 13.68 | 13.67
2018-07-18 19:00 | 14.34 | 14.33
2018-07-18 19:30 | 14.57 | 14.56
2018-07-18 20:00 | 14.92 | 14.91
2018-07-18 20:30 | 15.09 | 15.08
2018-07-18 21:00 | 14.54 | 14.53
2018-07-18 21:30 | 13.65 | 13.64
2018-07-18 22:00 | 12.7 | 12.7
2018-07-18 22:30 | 11.58 | 11.58
2018-07-18 23:00 | 10.75 | 10.74
2018-07-18 23:30 | 9.64 | 9.63
2018-07-19 | 8.53 | 8.52
2018-07-19 00:30 | 7.6 | 7.59
2018-07-19 01:00 | 7.16 | 7.14
2018-07-19 01:30 | 6.78 | 6.76
2018-07-19 02:00 | 6.43 | 6.41
2018-07-19 02:30 | 6.3 | 6.27
2018-07-19 03:00 | 6.17 | 6.14
2018-07-19 03:30 | 6.27 | 6.24
2018-07-19 04:00 | 6.47 | 6.44
2018-07-19 04:30 | 6.81 | 6.78
2018-07-19 05:00 | 7.43 | 7.42
2018-07-19 05:30 | 8.6 | 8.59
2018-07-19 06:00 | 9.71 | 9.7
2018-07-19 06:30 | 10.9 | 10.89
2018-07-19 07:00 | 12.26 | 12.25
2018-07-19 07:30 | 13.58 | 13.58
2018-07-19 08:00 | 12.96 | 12.95
2018-07-19 08:30 | 10.99 | 10.98
2018-07-19 09:00 | 8.98 | 8.97
2018-07-19 09:30 | 7.55 | 7.55
2018-07-19 10:00 | 6.61 | 6.6
2018-07-19 10:30 | 5.82 | 5.81
2018-07-19 11:00 | 5.09 | 5.08
2018-07-19 11:30 | 4.54 | 4.53
2018-07-19 12:00 | 4.15 | 4.13
2018-07-19 12:30 | 4.02 | 3.99
2018-07-19 13:00 | 5.16 | 5.12
2018-07-19 13:30 | 5.24 | 5.21
2018-07-19 14:00 | 5.48 | 5.45
2018-07-19 14:30 | 5.82 | 5.79
2018-07-19 15:00 | 6.15 | 6.12
2018-07-19 15:30 | 5.78 | 5.76
2018-07-19 16:00 | 6.73 | 6.72
2018-07-19 16:30 | 8.06 | 8.06
2018-07-19 17:00 | 9.52 | 9.52
2018-07-19 17:30 | 10.92 | 10.92
2018-07-19 18:00 | 12.55 | 12.55
2018-07-19 18:30 | 13.37 | 13.35
2018-07-19 19:00 | 14 | 13.99
2018-07-19 19:30 | 13.86 | 13.85
2018-07-19 20:00 | 13.89 | 13.88
2018-07-19 20:30 | 14.06 | 14.06
2018-07-19 21:00 | 13.61 | 13.61
2018-07-19 21:30 | 12.75 | 12.74
2018-07-19 22:00 | 11.73 | 11.72
2018-07-19 22:30 | 10.66 | 10.66
2018-07-19 23:00 | 9.99 | 9.98
2018-07-19 23:30 | 8.87 | 8.87
2018-07-20 | 7.99 | 7.97
2018-07-20 00:30 | 7.08 | 7.06
2018-07-20 01:00 | 6.56 | 6.54
2018-07-20 01:30 | 6.18 | 6.16
2018-07-20 02:00 | 5.81 | 5.78
2018-07-20 02:30 | 5.63 | 5.59
2018-07-20 03:00 | 5.56 | 5.52
2018-07-20 03:30 | 5.72 | 5.68
2018-07-20 04:00 | 5.8 | 5.76
2018-07-20 04:30 | 6.04 | 6.01
2018-07-20 05:00 | 6.62 | 6.6
2018-07-20 05:30 | 7.45 | 7.44
2018-07-20 06:00 | 8.73 | 8.73
2018-07-20 06:30 | 10.02 | 10.01
2018-07-20 07:00 | 11.24 | 11.24
2018-07-20 07:30 | 12.31 | 12.31
2018-07-20 08:00 | 12.1 | 12.1
2018-07-20 08:30 | 9.89 | 9.88
2018-07-20 09:00 | 8.06 | 8.06
2018-07-20 09:30 | 7.09 | 7.09
2018-07-20 10:00 | 6.31 | 6.3
2018-07-20 10:30 | 5 | 4.99
2018-07-20 11:00 | 4.46 | 4.43
2018-07-20 11:30 | 5.59 | 5.56
2018-07-20 12:00 | 5.76 | 5.72
2018-07-20 12:30 | 6.84 | 6.81
2018-07-20 13:00 | 6.68 | 6.65
2018-07-20 13:30 | 6.7 | 6.67
2018-07-20 14:00 | 8.2 | 8.18
2018-07-20 14:30 | 7.51 | 7.49
2018-07-20 15:00 | 6.14 | 6.12
2018-07-20 15:30 | 5.87 | 5.84
2018-07-20 16:00 | 7.17 | 7.15
2018-07-20 16:30 | 7.64 | 7.62
2018-07-20 17:00 | 8.73 | 8.72
2018-07-20 17:30 | 9.89 | 9.88
2018-07-20 18:00 | 11.18 | 11.17
2018-07-20 18:30 | 11.71 | 11.7
2018-07-20 19:00 | 12.04 | 12.03
2018-07-20 19:30 | 12.02 | 12.01
2018-07-20 20:00 | 12.24 | 12.23
2018-07-20 20:30 | 12.2 | 12.19
2018-07-20 21:00 | 11.8 | 11.79
2018-07-20 21:30 | 11.16 | 11.15
2018-07-20 22:00 | 10.76 | 10.75
2018-07-20 22:30 | 10.2 | 10.19
2018-07-20 23:00 | 9.96 | 9.95
2018-07-20 23:30 | 8.93 | 8.92
2018-07-21 | 8 | 7.98
2018-07-21 00:30 | 7.16 | 7.14
2018-07-21 01:00 | 6.72 | 6.69
2018-07-21 01:30 | 6.28 | 6.25
2018-07-21 02:00 | 5.87 | 5.84
2018-07-21 02:30 | 5.56 | 5.52
2018-07-21 03:00 | 5.43 | 5.39
2018-07-21 03:30 | 5.55 | 5.51
2018-07-21 04:00 | 5.5 | 5.46
2018-07-21 04:30 | 5.59 | 5.56
2018-07-21 05:00 | 5.73 | 5.69
2018-07-21 05:30 | 6.06 | 6.03
2018-07-21 06:00 | 6.38 | 6.35
2018-07-21 06:30 | 7.09 | 7.06
2018-07-21 07:00 | 7.9 | 7.87
2018-07-21 07:30 | 8.81 | 8.79
2018-07-21 08:00 | 8.99 | 8.97
2018-07-21 08:30 | 8.85 | 8.84
2018-07-21 09:00 | 8.17 | 8.15
2018-07-21 09:30 | 7.59 | 7.57
2018-07-21 10:00 | 6.96 | 6.94
2018-07-21 10:30 | 6.13 | 6.11
2018-07-21 11:00 | 5.44 | 5.41
2018-07-21 11:30 | 4.92 | 4.89
2018-07-21 12:00 | 4.66 | 4.63
2018-07-21 12:30 | 4.35 | 4.32
2018-07-21 13:00 | 4.09 | 4.05
2018-07-21 13:30 | 4.14 | 4.1
2018-07-21 14:00 | 4.44 | 4.4
2018-07-21 14:30 | 4.8 | 4.77
2018-07-21 15:00 | 5.22 | 5.19
2018-07-21 15:30 | 5.88 | 5.85
2018-07-21 16:00 | 6.56 | 6.53
2018-07-21 16:30 | 7.85 | 7.83
2018-07-21 17:00 | 9.38 | 9.37
2018-07-21 17:30 | 10.96 | 10.96
2018-07-21 18:00 | 12.42 | 12.41
2018-07-21 18:30 | 12.98 | 12.97
2018-07-21 19:00 | 13.33 | 13.32
2018-07-21 19:30 | 13.26 | 13.25
2018-07-21 20:00 | 13.4 | 13.4
2018-07-21 20:30 | 13.59 | 13.59
2018-07-21 21:00 | 13.35 | 13.34
2018-07-21 21:30 | 12.82 | 12.81
2018-07-21 22:00 | 12.4 | 12.4
2018-07-21 22:30 | 11.96 | 11.96
2018-07-21 23:00 | 11.59 | 11.59
2018-07-21 23:30 | 10.62 | 10.62
2018-07-22 | 9.51 | 9.5
2018-07-22 00:30 | 8.53 | 8.52
2018-07-22 01:00 | 8.04 | 8.02
2018-07-22 01:30 | 7.57 | 7.55
2018-07-22 02:00 | 7.09 | 7.07
2018-07-22 02:30 | 6.7 | 6.67
2018-07-22 03:00 | 6.51 | 6.49
2018-07-22 03:30 | 6.44 | 6.42
2018-07-22 04:00 | 6.41 | 6.38
2018-07-22 04:30 | 6.58 | 6.55
2018-07-22 05:00 | 6.63 | 6.61
2018-07-22 05:30 | 6.87 | 6.85
2018-07-22 06:00 | 7.23 | 7.21
2018-07-22 06:30 | 7.74 | 7.72
2018-07-22 07:00 | 8.23 | 8.21
2018-07-22 07:30 | 9.16 | 9.15
2018-07-22 08:00 | 9.89 | 9.88
2018-07-22 08:30 | 10.05 | 10.05
2018-07-22 09:00 | 10.15 | 10.14
2018-07-22 09:30 | 9.45 | 9.43
2018-07-22 10:00 | 8.35 | 8.34
2018-07-22 10:30 | 7.36 | 7.35
2018-07-22 11:00 | 6.61 | 6.59
2018-07-22 11:30 | 5.92 | 5.9
2018-07-22 12:00 | 5.62 | 5.61
2018-07-22 12:30 | 5.36 | 5.34
2018-07-22 13:00 | 5.77 | 5.75
2018-07-22 13:30 | 5.34 | 5.31
2018-07-22 14:00 | 5.25 | 5.23
2018-07-22 14:30 | 5.41 | 5.38
2018-07-22 15:00 | 6.06 | 6.03
2018-07-22 15:30 | 6.46 | 6.43
2018-07-22 16:00 | 7.44 | 7.42
2018-07-22 16:30 | 8.53 | 8.51
2018-07-22 17:00 | 10.31 | 10.3
2018-07-22 17:30 | 12.13 | 12.12
2018-07-22 18:00 | 13.62 | 13.61
2018-07-22 18:30 | 14.2 | 14.19
2018-07-22 19:00 | 14.41 | 14.41
2018-07-22 19:30 | 14.53 | 14.53
2018-07-22 20:00 | 14.46 | 14.45
2018-07-22 20:30 | 14.36 | 14.36
2018-07-22 21:00 | 13.89 | 13.88
2018-07-22 21:30 | 13.09 | 13.08
2018-07-22 22:00 | 12.06 | 12.06
2018-07-22 22:30 | 11.28 | 11.28
2018-07-22 23:00 | 10.73 | 10.72
2018-07-22 23:30 | 9.44 | 9.43
2018-07-23 | 8.46 | 8.44
2018-07-23 00:30 | 7.56 | 7.55
2018-07-23 01:00 | 7.1 | 7.08
2018-07-23 01:30 | 6.65 | 6.62
2018-07-23 02:00 | 6.32 | 6.29
2018-07-23 02:30 | 6.15 | 6.13
2018-07-23 03:00 | 6 | 5.97
2018-07-23 03:30 | 6.05 | 6.02
2018-07-23 04:00 | 6.23 | 6.2
2018-07-23 04:30 | 6.48 | 6.46
2018-07-23 05:00 | 7.12 | 7.11
2018-07-23 05:30 | 8.12 | 8.11
2018-07-23 06:00 | 9.21 | 9.2
2018-07-23 06:30 | 10.4 | 10.4
2018-07-23 07:00 | 11.77 | 11.76
2018-07-23 07:30 | 12.86 | 12.85
2018-07-23 08:00 | 11.93 | 11.93
2018-07-23 08:30 | 9.93 | 9.92
2018-07-23 09:00 | 8.22 | 8.22
2018-07-23 09:30 | 7.28 | 7.27
2018-07-23 10:00 | 6.39 | 6.38
2018-07-23 10:30 | 5.52 | 5.51
2018-07-23 11:00 | 4.84 | 4.82
2018-07-23 11:30 | 4.45 | 4.43
2018-07-23 12:00 | 4.35 | 4.34
2018-07-23 12:30 | 4.64 | 4.63
2018-07-23 13:00 | 4.81 | 4.8
2018-07-23 13:30 | 5.01 | 4.99
2018-07-23 14:00 | 4.45 | 4.42
2018-07-23 14:30 | 4.97 | 4.94
2018-07-23 15:00 | 5.81 | 5.79
2018-07-23 15:30 | 6.29 | 6.26
2018-07-23 16:00 | 6.56 | 6.53
2018-07-23 16:30 | 7.89 | 7.88
2018-07-23 17:00 | 9.5 | 9.49
2018-07-23 17:30 | 11.36 | 11.36
2018-07-23 18:00 | 13.48 | 13.47
2018-07-23 18:30 | 14.23 | 14.22
2018-07-23 19:00 | 14.68 | 14.67
2018-07-23 19:30 | 14.49 | 14.49
2018-07-23 20:00 | 14.51 | 14.51
2018-07-23 20:30 | 14.48 | 14.47
2018-07-23 21:00 | 13.79 | 13.78
2018-07-23 21:30 | 12.83 | 12.82
2018-07-23 22:00 | 11.89 | 11.89
2018-07-23 22:30 | 11.12 | 11.11
2018-07-23 23:00 | 10.54 | 10.53
2018-07-23 23:30 | 9.26 | 9.26
2018-07-24 | 8.07 | 8.05
2018-07-24 00:30 | 7.22 | 7.2
2018-07-24 01:00 | 6.8 | 6.78
2018-07-24 01:30 | 6.45 | 6.42
2018-07-24 02:00 | 6.16 | 6.13
2018-07-24 02:30 | 5.87 | 5.84
2018-07-24 03:00 | 5.81 | 5.78
2018-07-24 03:30 | 5.9 | 5.87
2018-07-24 04:00 | 6.02 | 5.99
2018-07-24 04:30 | 6.47 | 6.45
2018-07-24 05:00 | 7.11 | 7.1
2018-07-24 05:30 | 8.02 | 8.01
2018-07-24 06:00 | 9.04 | 9.03
2018-07-24 06:30 | 10.19 | 10.18
2018-07-24 07:00 | 11.29 | 11.29
2018-07-24 07:30 | 11.95 | 11.94
2018-07-24 08:00 | 11.15 | 11.15
2018-07-24 08:30 | 9.13 | 9.12
2018-07-24 09:00 | 7.36 | 7.35
2018-07-24 09:30 | 6.46 | 6.44
2018-07-24 10:00 | 5.59 | 5.57
2018-07-24 10:30 | 4.79 | 4.77
2018-07-24 11:00 | 4.22 | 4.19
2018-07-24 11:30 | 3.79 | 3.76
2018-07-24 12:00 | 3.47 | 3.44
2018-07-24 12:30 | 3.36 | 3.33
2018-07-24 13:00 | 3.32 | 3.29
2018-07-24 13:30 | 3.41 | 3.37
2018-07-24 14:00 | 3.62 | 3.6
2018-07-24 14:30 | 4.02 | 4
2018-07-24 15:00 | 4.43 | 4.4
2018-07-24 15:30 | 5.26 | 5.24
2018-07-24 16:00 | 6.33 | 6.32
2018-07-24 16:30 | 7.49 | 7.48
2018-07-24 17:00 | 8.97 | 8.96
2018-07-24 17:30 | 10.39 | 10.38
2018-07-24 18:00 | 11.92 | 11.92
2018-07-24 18:30 | 12.65 | 12.64
2018-07-24 19:00 | 13.1 | 13.1
2018-07-24 19:30 | 12.95 | 12.94
2018-07-24 20:00 | 12.89 | 12.89
2018-07-24 20:30 | 12.96 | 12.96
2018-07-24 21:00 | 12.46 | 12.46
2018-07-24 21:30 | 11.5 | 11.49
2018-07-24 22:00 | 10.66 | 10.66
2018-07-24 22:30 | 9.9 | 9.9
2018-07-24 23:00 | 9.45 | 9.44
2018-07-24 23:30 | 8.29 | 8.28
2018-07-25 | 7.51 | 7.49
2018-07-25 00:30 | 6.81 | 6.79
2018-07-25 01:00 | 6.29 | 6.26
2018-07-25 01:30 | 5.86 | 5.83
2018-07-25 02:00 | 5.67 | 5.64
2018-07-25 02:30 | 5.46 | 5.42
2018-07-25 03:00 | 5.3 | 5.26
2018-07-25 03:30 | 5.35 | 5.31
2018-07-25 04:00 | 5.51 | 5.47
2018-07-25 04:30 | 5.85 | 5.82
2018-07-25 05:00 | 6.4 | 6.38
2018-07-25 05:30 | 7.28 | 7.27
2018-07-25 06:00 | 8.24 | 8.24
2018-07-25 06:30 | 9.27 | 9.27
2018-07-25 07:00 | 10.26 | 10.25
2018-07-25 07:30 | 11.21 | 11.21
2018-07-25 08:00 | 11.15 | 11.14
2018-07-25 08:30 | 10.96 | 10.95
2018-07-25 09:00 | 11.11 | 11.1
2018-07-25 09:30 | 10.55 | 10.54
2018-07-25 10:00 | 9.96 | 9.95
2018-07-25 10:30 | 8.42 | 8.4
2018-07-25 11:00 | 7.21 | 7.19
2018-07-25 11:30 | 7.64 | 7.62
2018-07-25 12:00 | 4.84 | 4.8
2018-07-25 12:30 | 3.86 | 3.83
2018-07-25 13:00 | 4.77 | 4.75
2018-07-25 13:30 | 5.83 | 5.81
2018-07-25 14:00 | 7.19 | 7.18
2018-07-25 14:30 | 6.18 | 6.16
2018-07-25 15:00 | 6.76 | 6.75
2018-07-25 15:30 | 7.14 | 7.13
2018-07-25 16:00 | 7.98 | 7.97
2018-07-25 16:30 | 8.78 | 8.78
2018-07-25 17:00 | 9.88 | 9.88
2018-07-25 17:30 | 11.32 | 11.32
2018-07-25 18:00 | 12.79 | 12.79
2018-07-25 18:30 | 13.62 | 13.61
2018-07-25 19:00 | 14.16 | 14.15
2018-07-25 19:30 | 13.87 | 13.86
2018-07-25 20:00 | 13.76 | 13.76
2018-07-25 20:30 | 13.86 | 13.86
2018-07-25 21:00 | 13.38 | 13.38
2018-07-25 21:30 | 13.54 | 13.54
2018-07-25 22:00 | 12.9 | 12.9
2018-07-25 22:30 | 11.65 | 11.64
2018-07-25 23:00 | 11 | 10.99
2018-07-25 23:30 | 9.82 | 9.81
2018-07-26 | 8.89 | 8.87
2018-07-26 00:30 | 7.74 | 7.71
2018-07-26 01:00 | 7.21 | 7.18
2018-07-26 01:30 | 6.71 | 6.67
2018-07-26 02:00 | 6.46 | 6.42
2018-07-26 02:30 | 6.26 | 6.22
2018-07-26 03:00 | 6.07 | 6.02
2018-07-26 03:30 | 5.14 | 5.1
2018-07-26 04:00 | 5.07 | 5.03
2018-07-26 04:30 | 5.31 | 5.28
2018-07-26 05:00 | 5.84 | 5.82
2018-07-26 05:30 | 6.69 | 6.68
2018-07-26 06:00 | 7.8 | 7.8
2018-07-26 06:30 | 8.7 | 8.69
2018-07-26 07:00 | 9.52 | 9.51
2018-07-26 07:30 | 10.13 | 10.13
2018-07-26 08:00 | 9.2 | 9.19
2018-07-26 08:30 | 7.75 | 7.74
2018-07-26 09:00 | 6.57 | 6.55
2018-07-26 09:30 | 5.82 | 5.81
2018-07-26 10:00 | 5.08 | 5.06
2018-07-26 10:30 | 4.33 | 4.31
2018-07-26 11:00 | 4.01 | 3.99
2018-07-26 11:30 | 3.78 | 3.77
2018-07-26 12:00 | 3.64 | 3.62
2018-07-26 12:30 | 3.69 | 3.67
2018-07-26 13:00 | 3.76 | 3.74
2018-07-26 13:30 | 3.96 | 3.95
2018-07-26 14:00 | 4.29 | 4.27
2018-07-26 14:30 | 4.68 | 4.67
2018-07-26 15:00 | 5.07 | 5.06
2018-07-26 15:30 | 5.81 | 5.8
2018-07-26 16:00 | 7.14 | 7.14
2018-07-26 16:30 | 7.76 | 7.75
2018-07-26 17:00 | 8.95 | 8.94
2018-07-26 17:30 | 10.15 | 10.15
2018-07-26 18:00 | 11.57 | 11.56
2018-07-26 18:30 | 12.23 | 12.22
2018-07-26 19:00 | 12.6 | 12.59
2018-07-26 19:30 | 12.26 | 12.25
2018-07-26 20:00 | 12.44 | 12.44
2018-07-26 20:30 | 12.38 | 12.37
2018-07-26 21:00 | 11.97 | 11.97
2018-07-26 21:30 | 11.35 | 11.34
2018-07-26 22:00 | 10.37 | 10.36
2018-07-26 22:30 | 9.55 | 9.55
2018-07-26 23:00 | 8.99 | 8.98
2018-07-26 23:30 | 7.9 | 7.89
2018-07-27 | 6.92 | 6.9
2018-07-27 00:30 | 6.14 | 6.12
2018-07-27 01:00 | 5.67 | 5.64
2018-07-27 01:30 | 5.32 | 5.28
2018-07-27 02:00 | 5.04 | 5.01
2018-07-27 02:30 | 4.87 | 4.83
2018-07-27 03:00 | 4.74 | 4.69
2018-07-27 03:30 | 4.86 | 4.81
2018-07-27 04:00 | 4.94 | 4.9
2018-07-27 04:30 | 5.05 | 5.01
2018-07-27 05:00 | 5.52 | 5.48
2018-07-27 05:30 | 6.23 | 6.21
2018-07-27 06:00 | 7.5 | 7.49
2018-07-27 06:30 | 8.37 | 8.37
2018-07-27 07:00 | 9.47 | 9.46
2018-07-27 07:30 | 10.09 | 10.09
2018-07-27 08:00 | 9.27 | 9.26
2018-07-27 08:30 | 7.9 | 7.89
2018-07-27 09:00 | 6.8 | 6.79
2018-07-27 09:30 | 6.07 | 6.07
2018-07-27 10:00 | 5.22 | 5.21
2018-07-27 10:30 | 4.35 | 4.33
2018-07-27 11:00 | 3.72 | 3.7
2018-07-27 11:30 | 3.44 | 3.42
2018-07-27 12:00 | 3.23 | 3.21
2018-07-27 12:30 | 3.16 | 3.14
2018-07-27 13:00 | 3.21 | 3.18
2018-07-27 13:30 | 3.64 | 3.62
2018-07-27 14:00 | 4.06 | 4.04
2018-07-27 14:30 | 4.12 | 4.1
2018-07-27 15:00 | 4.54 | 4.52
2018-07-27 15:30 | 5.37 | 5.35
2018-07-27 16:00 | 6.29 | 6.28
2018-07-27 16:30 | 7.15 | 7.13
2018-07-27 17:00 | 8.27 | 8.26
2018-07-27 17:30 | 9.19 | 9.17
2018-07-27 18:00 | 10.37 | 10.36
2018-07-27 18:30 | 10.91 | 10.9
2018-07-27 19:00 | 11.15 | 11.14
2018-07-27 19:30 | 11.03 | 11.02
2018-07-27 20:00 | 11.05 | 11.04
2018-07-27 20:30 | 11.01 | 11
2018-07-27 21:00 | 10.49 | 10.48
2018-07-27 21:30 | 9.83 | 9.82
2018-07-27 22:00 | 9.34 | 9.33
2018-07-27 22:30 | 8.83 | 8.82
2018-07-27 23:00 | 8.59 | 8.58
2018-07-27 23:30 | 7.77 | 7.76
2018-07-28 | 6.86 | 6.84
2018-07-28 00:30 | 6.31 | 6.29
2018-07-28 01:00 | 5.89 | 5.87
2018-07-28 01:30 | 5.49 | 5.46
2018-07-28 02:00 | 5.01 | 4.98
2018-07-28 02:30 | 4.82 | 4.78
2018-07-28 03:00 | 4.67 | 4.63
2018-07-28 03:30 | 4.74 | 4.7
2018-07-28 04:00 | 4.67 | 4.62
2018-07-28 04:30 | 4.79 | 4.76
2018-07-28 05:00 | 4.96 | 4.92
2018-07-28 05:30 | 5.21 | 5.18
2018-07-28 06:00 | 5.4 | 5.37
2018-07-28 06:30 | 5.79 | 5.75
2018-07-28 07:00 | 6.22 | 6.16
2018-07-28 07:30 | 6.69 | 6.64
2018-07-28 08:00 | 6.78 | 6.74
2018-07-28 08:30 | 6.68 | 6.65
2018-07-28 09:00 | 6.54 | 6.51
2018-07-28 09:30 | 6.15 | 6.13
2018-07-28 10:00 | 5.6 | 5.58
2018-07-28 10:30 | 5.08 | 5.05
2018-07-28 11:00 | 4.55 | 4.53
2018-07-28 11:30 | 4.37 | 4.34
2018-07-28 12:00 | 4.26 | 4.23
2018-07-28 12:30 | 4.15 | 4.11
2018-07-28 13:00 | 4.06 | 4.02
2018-07-28 13:30 | 4.08 | 4.04
2018-07-28 14:00 | 4.38 | 4.34
2018-07-28 14:30 | 4.72 | 4.68
2018-07-28 15:00 | 5.17 | 5.14
2018-07-28 15:30 | 5.86 | 5.83
2018-07-28 16:00 | 6.33 | 6.31
2018-07-28 16:30 | 7.42 | 7.4
2018-07-28 17:00 | 8.41 | 8.39
2018-07-28 17:30 | 9.16 | 9.15
2018-07-28 18:00 | 10.02 | 10.01
2018-07-28 18:30 | 10.24 | 10.23
2018-07-28 19:00 | 10.27 | 10.26
2018-07-28 19:30 | 10.11 | 10.1
2018-07-28 20:00 | 10.15 | 10.14
2018-07-28 20:30 | 10.05 | 10.04
2018-07-28 21:00 | 9.66 | 9.65
2018-07-28 21:30 | 9.05 | 9.04
2018-07-28 22:00 | 8.75 | 8.74
2018-07-28 22:30 | 8.54 | 8.54
2018-07-28 23:00 | 8.33 | 8.32
2018-07-28 23:30 | 7.6 | 7.58
2018-07-29 | 6.87 | 6.85
2018-07-29 00:30 | 6.17 | 6.14
2018-07-29 01:00 | 5.82 | 5.79
2018-07-29 01:30 | 5.49 | 5.45
2018-07-29 02:00 | 5.05 | 5
2018-07-29 02:30 | 4.87 | 4.83
2018-07-29 03:00 | 4.66 | 4.62
2018-07-29 03:30 | 4.59 | 4.54
2018-07-29 04:00 | 4.53 | 4.47
2018-07-29 04:30 | 4.56 | 4.51
2018-07-29 05:00 | 4.65 | 4.59
2018-07-29 05:30 | 4.8 | 4.75
2018-07-29 06:00 | 5.03 | 4.99
2018-07-29 06:30 | 5.19 | 5.14
2018-07-29 07:00 | 5.57 | 5.49
2018-07-29 07:30 | 5.98 | 5.91
2018-07-29 08:00 | 6.28 | 6.23
2018-07-29 08:30 | 6.27 | 6.22
2018-07-29 09:00 | 6.19 | 6.14
2018-07-29 09:30 | 6.08 | 6.05
2018-07-29 10:00 | 5.56 | 5.53
2018-07-29 10:30 | 5.14 | 5.11
2018-07-29 11:00 | 4.51 | 4.48
2018-07-29 11:30 | 4.35 | 4.32
2018-07-29 12:00 | 4.37 | 4.34
2018-07-29 12:30 | 4.2 | 4.17
2018-07-29 13:00 | 4.13 | 4.1
2018-07-29 13:30 | 4.26 | 4.23
2018-07-29 14:00 | 4.62 | 4.59
2018-07-29 14:30 | 4.88 | 4.85
2018-07-29 15:00 | 5.59 | 5.57
2018-07-29 15:30 | 6.41 | 6.39
2018-07-29 16:00 | 7.33 | 7.32
2018-07-29 16:30 | 8.18 | 8.17
2018-07-29 17:00 | 9.3 | 9.29
2018-07-29 17:30 | 10.38 | 10.37
2018-07-29 18:00 | 11.59 | 11.58
2018-07-29 18:30 | 11.65 | 11.64
2018-07-29 19:00 | 11.55 | 11.54
2018-07-29 19:30 | 11.13 | 11.12
2018-07-29 20:00 | 10.91 | 10.91
2018-07-29 20:30 | 10.87 | 10.87
2018-07-29 21:00 | 10.24 | 10.23
2018-07-29 21:30 | 9.46 | 9.46
2018-07-29 22:00 | 8.92 | 8.91
2018-07-29 22:30 | 8.49 | 8.48
2018-07-29 23:00 | 8.23 | 8.22
2018-07-29 23:30 | 7.42 | 7.4
2018-07-30 | 6.45 | 6.42
2018-07-30 00:30 | 5.58 | 5.55
2018-07-30 01:00 | 5.1 | 5.06
2018-07-30 01:30 | 4.88 | 4.83
2018-07-30 02:00 | 4.66 | 4.61
2018-07-30 02:30 | 4.47 | 4.42
2018-07-30 03:00 | 4.37 | 4.31
2018-07-30 03:30 | 4.46 | 4.4
2018-07-30 04:00 | 4.42 | 4.37
2018-07-30 04:30 | 4.68 | 4.62
2018-07-30 05:00 | 5.04 | 5
2018-07-30 05:30 | 5.65 | 5.62
2018-07-30 06:00 | 6.43 | 6.41
2018-07-30 06:30 | 7.44 | 7.43
2018-07-30 07:00 | 8.23 | 8.21
2018-07-30 07:30 | 8.72 | 8.7
2018-07-30 08:00 | 8.05 | 8.03
2018-07-30 08:30 | 6.9 | 6.88
2018-07-30 09:00 | 5.83 | 5.81
2018-07-30 09:30 | 5.21 | 5.2
2018-07-30 10:00 | 4.7 | 4.69
2018-07-30 10:30 | 4.19 | 4.17
2018-07-30 11:00 | 3.73 | 3.71
2018-07-30 11:30 | 3.45 | 3.43
2018-07-30 12:00 | 3.22 | 3.2
2018-07-30 12:30 | 3.36 | 3.34
2018-07-30 13:00 | 3.48 | 3.46
2018-07-30 13:30 | 3.52 | 3.5
2018-07-30 14:00 | 3.94 | 3.93
2018-07-30 14:30 | 4.28 | 4.27
2018-07-30 15:00 | 4.6 | 4.58
2018-07-30 15:30 | 5.46 | 5.45
2018-07-30 16:00 | 6.65 | 6.64
2018-07-30 16:30 | 7.7 | 7.69
2018-07-30 17:00 | 9.24 | 9.24
2018-07-30 17:30 | 10.88 | 10.88
2018-07-30 18:00 | 12.24 | 12.23
2018-07-30 18:30 | 13.05 | 13.05
2018-07-30 19:00 | 13.3 | 13.3
2018-07-30 19:30 | 13.01 | 13.01
2018-07-30 20:00 | 12.89 | 12.89
2018-07-30 20:30 | 12.91 | 12.91
2018-07-30 21:00 | 12.34 | 12.34
2018-07-30 21:30 | 11.52 | 11.51
2018-07-30 22:00 | 10.93 | 10.93
2018-07-30 22:30 | 9.84 | 9.83
2018-07-30 23:00 | 9.34 | 9.34
2018-07-30 23:30 | 8.18 | 8.16
2018-07-31 | 7.18 | 7.16
2018-07-31 00:30 | 6.5 | 6.48
2018-07-31 01:00 | 6.73 | 6.7
2018-07-31 01:30 | 6.93 | 6.89
2018-07-31 02:00 | 6.58 | 6.54
2018-07-31 02:30 | 6.4 | 6.35
2018-07-31 03:00 | 6.32 | 6.27
2018-07-31 03:30 | 5.73 | 5.68
2018-07-31 04:00 | 5.46 | 5.41
2018-07-31 04:30 | 5.72 | 5.68
2018-07-31 05:00 | 6.39 | 6.37
2018-07-31 05:30 | 7.29 | 7.27
2018-07-31 06:00 | 8.26 | 8.25
2018-07-31 06:30 | 9.12 | 9.11
2018-07-31 07:00 | 10.37 | 10.36
2018-07-31 07:30 | 11.31 | 11.3
2018-07-31 08:00 | 10.6 | 10.6
2018-07-31 08:30 | 8.87 | 8.86
2018-07-31 09:00 | 7.16 | 7.15
2018-07-31 09:30 | 6.16 | 6.15
2018-07-31 10:00 | 5.38 | 5.37
2018-07-31 10:30 | 4.59 | 4.57
2018-07-31 11:00 | 4.09 | 4.07
2018-07-31 11:30 | 3.76 | 3.74
2018-07-31 12:00 | 3.6 | 3.58
2018-07-31 12:30 | 3.53 | 3.51
2018-07-31 13:00 | 3.47 | 3.45
2018-07-31 13:30 | 3.53 | 3.51
2018-07-31 14:00 | 3.84 | 3.82
2018-07-31 14:30 | 4.04 | 4.02
2018-07-31 15:00 | 4.36 | 4.34
2018-07-31 15:30 | 5.27 | 5.25
2018-07-31 16:00 | 6.32 | 6.31
2018-07-31 16:30 | 7.73 | 7.72
2018-07-31 17:00 | 9.18 | 9.18
2018-07-31 17:30 | 10.64 | 10.64
2018-07-31 18:00 | 12.38 | 12.38
2018-07-31 18:30 | 13.54 | 13.53
2018-07-31 19:00 | 13.71 | 13.7
2018-07-31 19:30 | 13.77 | 13.76
2018-07-31 20:00 | 13.91 | 13.9
2018-07-31 20:30 | 14.13 | 14.12
2018-07-31 21:00 | 13.72 | 13.71
2018-07-31 21:30 | 12.86 | 12.86
2018-07-31 22:00 | 12.01 | 12.01
2018-07-31 22:30 | 10.85 | 10.84
2018-07-31 23:00 | 10.03 | 10.03
2018-07-31 23:30 | 8.86 | 8.85
2018-08-01 | 7.88 | 7.87
2018-08-01 00:30 | 7.04 | 7.02
2018-08-01 01:00 | 6.58 | 6.55
2018-08-01 01:30 | 6.23 | 6.2
2018-08-01 02:00 | 5.92 | 5.89
2018-08-01 02:30 | 5.85 | 5.82
2018-08-01 03:00 | 5.79 | 5.76
2018-08-01 03:30 | 5.85 | 5.82
2018-08-01 04:00 | 6 | 5.97
2018-08-01 04:30 | 6.39 | 6.37
2018-08-01 05:00 | 6.91 | 6.9
2018-08-01 05:30 | 7.86 | 7.85
2018-08-01 06:00 | 9.1 | 9.09
2018-08-01 06:30 | 10.52 | 10.52
2018-08-01 07:00 | 11.82 | 11.82
2018-08-01 07:30 | 12.41 | 12.41
2018-08-01 08:00 | 11.31 | 11.31
2018-08-01 08:30 | 9.41 | 9.41
2018-08-01 09:00 | 8.04 | 8.04
2018-08-01 09:30 | 6.91 | 6.9
2018-08-01 10:00 | 5.98 | 5.97
2018-08-01 10:30 | 5.03 | 5.01
2018-08-01 11:00 | 4.32 | 4.31
2018-08-01 11:30 | 3.91 | 3.89
2018-08-01 12:00 | 3.68 | 3.66
2018-08-01 12:30 | 3.52 | 3.5
2018-08-01 13:00 | 3.52 | 3.49
2018-08-01 13:30 | 3.64 | 3.62
2018-08-01 14:00 | 3.99 | 3.98
2018-08-01 14:30 | 4.22 | 4.2
2018-08-01 15:00 | 4.48 | 4.46
2018-08-01 15:30 | 5.22 | 5.2
2018-08-01 16:00 | 6.39 | 6.38
2018-08-01 16:30 | 7.68 | 7.67
2018-08-01 17:00 | 9.05 | 9.04
2018-08-01 17:30 | 10.52 | 10.52
2018-08-01 18:00 | 12.16 | 12.16
2018-08-01 18:30 | 13.31 | 13.31
2018-08-01 19:00 | 13.75 | 13.75
2018-08-01 19:30 | 13.74 | 13.73
2018-08-01 20:00 | 13.81 | 13.8
2018-08-01 20:30 | 13.83 | 13.83
2018-08-01 21:00 | 12.97 | 12.96
2018-08-01 21:30 | 12.02 | 12.01
2018-08-01 22:00 | 11.08 | 11.08
2018-08-01 22:30 | 10.42 | 10.41
2018-08-01 23:00 | 9.88 | 9.87
2018-08-01 23:30 | 8.71 | 8.7
2018-08-02 | 7.66 | 7.65
2018-08-02 00:30 | 6.88 | 6.86
2018-08-02 01:00 | 6.4 | 6.37
2018-08-02 01:30 | 6.09 | 6.06
2018-08-02 02:00 | 5.8 | 5.77
2018-08-02 02:30 | 5.58 | 5.54
2018-08-02 03:00 | 5.48 | 5.45
2018-08-02 03:30 | 5.6 | 5.56
2018-08-02 04:00 | 5.78 | 5.75
2018-08-02 04:30 | 6.05 | 6.02
2018-08-02 05:00 | 6.66 | 6.64
2018-08-02 05:30 | 7.52 | 7.51
2018-08-02 06:00 | 8.59 | 8.58
2018-08-02 06:30 | 9.62 | 9.61
2018-08-02 07:00 | 10.81 | 10.8
2018-08-02 07:30 | 11.67 | 11.66
2018-08-02 08:00 | 11.47 | 11.46
2018-08-02 08:30 | 9.8 | 9.79
2018-08-02 09:00 | 8.16 | 8.14
2018-08-02 09:30 | 6.93 | 6.91
2018-08-02 10:00 | 6.18 | 6.15
2018-08-02 10:30 | 5.29 | 5.25
2018-08-02 11:00 | 4.75 | 4.71
2018-08-02 11:30 | 4.38 | 4.34
2018-08-02 12:00 | 4.23 | 4.19
2018-08-02 12:30 | 4.11 | 4.06
2018-08-02 13:00 | 4.22 | 4.17
2018-08-02 13:30 | 4.41 | 4.37
2018-08-02 14:00 | 4.74 | 4.7
2018-08-02 14:30 | 4.99 | 4.95
2018-08-02 15:00 | 5.45 | 5.42
2018-08-02 15:30 | 6.27 | 6.24
2018-08-02 16:00 | 7.1 | 7.07
2018-08-02 16:30 | 8.15 | 8.12
2018-08-02 17:00 | 9.32 | 9.3
2018-08-02 17:30 | 9.92 | 9.92
2018-08-02 18:00 | 11.46 | 11.45
2018-08-02 18:30 | 12.22 | 12.22
2018-08-02 19:00 | 12.69 | 12.69
2018-08-02 19:30 | 12.78 | 12.78
2018-08-02 20:00 | 12.86 | 12.86
2018-08-02 20:30 | 12.91 | 12.9
2018-08-02 21:00 | 12.75 | 12.75
2018-08-02 21:30 | 11.76 | 11.76
2018-08-02 22:00 | 10.9 | 10.9
2018-08-02 22:30 | 10.26 | 10.25
2018-08-02 23:00 | 9.66 | 9.65
2018-08-02 23:30 | 8.59 | 8.58
2018-08-03 | 7.51 | 7.5
2018-08-03 00:30 | 6.67 | 6.65
2018-08-03 01:00 | 6.35 | 6.33
2018-08-03 01:30 | 5.9 | 5.87
2018-08-03 02:00 | 5.6 | 5.57
2018-08-03 02:30 | 5.4 | 5.36
2018-08-03 03:00 | 5.26 | 5.21
2018-08-03 03:30 | 5.38 | 5.34
2018-08-03 04:00 | 5.56 | 5.52
2018-08-03 04:30 | 5.76 | 5.73
2018-08-03 05:00 | 6.28 | 6.25
2018-08-03 05:30 | 6.97 | 6.95
2018-08-03 06:00 | 7.88 | 7.87
2018-08-03 06:30 | 8.71 | 8.7
2018-08-03 07:00 | 9.74 | 9.73
2018-08-03 07:30 | 10.23 | 10.22
2018-08-03 08:00 | 9.36 | 9.35
2018-08-03 08:30 | 7.71 | 7.7
2018-08-03 09:00 | 6.25 | 6.23
2018-08-03 09:30 | 5.32 | 5.29
2018-08-03 10:00 | 4.53 | 4.5
2018-08-03 10:30 | 3.87 | 3.84
2018-08-03 11:00 | 3.48 | 3.45
2018-08-03 11:30 | 3.13 | 3.1
2018-08-03 12:00 | 3.26 | 3.23
2018-08-03 12:30 | 3.45 | 3.42
2018-08-03 13:00 | 4.63 | 4.6
2018-08-03 13:30 | 4.12 | 4.09
2018-08-03 14:00 | 3.92 | 3.89
2018-08-03 14:30 | 4.42 | 4.39
2018-08-03 15:00 | 4.34 | 4.31
2018-08-03 15:30 | 5.41 | 5.39
2018-08-03 16:00 | 6.4 | 6.37
2018-08-03 16:30 | 7.14 | 7.13
2018-08-03 17:00 | 8.23 | 8.21
2018-08-03 17:30 | 9.47 | 9.46
2018-08-03 18:00 | 10.71 | 10.7
2018-08-03 18:30 | 11.37 | 11.37
2018-08-03 19:00 | 11.78 | 11.78
2018-08-03 19:30 | 11.69 | 11.69
2018-08-03 20:00 | 11.79 | 11.78
2018-08-03 20:30 | 11.72 | 11.71
2018-08-03 21:00 | 11.3 | 11.29
2018-08-03 21:30 | 10.69 | 10.68
2018-08-03 22:00 | 9.89 | 9.88
2018-08-03 22:30 | 9.48 | 9.47
2018-08-03 23:00 | 9.33 | 9.32
2018-08-03 23:30 | 8.43 | 8.42
2018-08-04 | 7.6 | 7.58
2018-08-04 00:30 | 6.74 | 6.71
2018-08-04 01:00 | 6.37 | 6.34
2018-08-04 01:30 | 5.85 | 5.81
2018-08-04 02:00 | 5.51 | 5.47
2018-08-04 02:30 | 5.34 | 5.29
2018-08-04 03:00 | 5.1 | 5.06
2018-08-04 03:30 | 5.14 | 5.09
2018-08-04 04:00 | 5.09 | 5.04
2018-08-04 04:30 | 4.99 | 4.94
2018-08-04 05:00 | 5.18 | 5.13
2018-08-04 05:30 | 5.44 | 5.4
2018-08-04 06:00 | 5.81 | 5.78
2018-08-04 06:30 | 6.11 | 6.07
2018-08-04 07:00 | 6.79 | 6.74
2018-08-04 07:30 | 7.34 | 7.29
2018-08-04 08:00 | 7.3 | 7.26
2018-08-04 08:30 | 7.08 | 7.05
2018-08-04 09:00 | 6.63 | 6.61
2018-08-04 09:30 | 6.14 | 6.12
2018-08-04 10:00 | 5.65 | 5.63
2018-08-04 10:30 | 5.01 | 4.99
2018-08-04 11:00 | 4.47 | 4.45
2018-08-04 11:30 | 4.08 | 4.05
2018-08-04 12:00 | 3.94 | 3.91
2018-08-04 12:30 | 3.78 | 3.75
2018-08-04 13:00 | 3.85 | 3.81
2018-08-04 13:30 | 3.82 | 3.79
2018-08-04 14:00 | 4.11 | 4.08
2018-08-04 14:30 | 4.37 | 4.34
2018-08-04 15:00 | 4.88 | 4.85
2018-08-04 15:30 | 5.52 | 5.5
2018-08-04 16:00 | 6.28 | 6.26
2018-08-04 16:30 | 7.17 | 7.15
2018-08-04 17:00 | 8.14 | 8.13
2018-08-04 17:30 | 8.98 | 8.97
2018-08-04 18:00 | 10.03 | 10.02
2018-08-04 18:30 | 10.5 | 10.49
2018-08-04 19:00 | 10.71 | 10.7
2018-08-04 19:30 | 10.5 | 10.49
2018-08-04 20:00 | 10.63 | 10.63
2018-08-04 20:30 | 10.6 | 10.6
2018-08-04 21:00 | 10.16 | 10.16
2018-08-04 21:30 | 9.66 | 9.66
2018-08-04 22:00 | 9.37 | 9.37
2018-08-04 22:30 | 9.3 | 9.29
2018-08-04 23:00 | 9.1 | 9.09
2018-08-04 23:30 | 8.3 | 8.29
2018-08-05 | 7.61 | 7.59
2018-08-05 00:30 | 6.79 | 6.77
2018-08-05 01:00 | 6.32 | 6.29
2018-08-05 01:30 | 6 | 5.97
2018-08-05 02:00 | 5.51 | 5.48
2018-08-05 02:30 | 5.39 | 5.35
2018-08-05 03:00 | 5.15 | 5.1
2018-08-05 03:30 | 5.2 | 5.16
2018-08-05 04:00 | 5.22 | 5.17
2018-08-05 04:30 | 5.18 | 5.13
2018-08-05 05:00 | 5.3 | 5.26
2018-08-05 05:30 | 5.49 | 5.45
2018-08-05 06:00 | 5.72 | 5.68
2018-08-05 06:30 | 6 | 5.95
2018-08-05 07:00 | 6.64 | 6.59
2018-08-05 07:30 | 7.08 | 7.03
2018-08-05 08:00 | 7.22 | 7.19
2018-08-05 08:30 | 7.33 | 7.3
2018-08-05 09:00 | 7.08 | 7.05
2018-08-05 09:30 | 6.68 | 6.66
2018-08-05 10:00 | 5.95 | 5.92
2018-08-05 10:30 | 5.25 | 5.22
2018-08-05 11:00 | 4.77 | 4.73
2018-08-05 11:30 | 4.47 | 4.43
2018-08-05 12:00 | 4.41 | 4.38
2018-08-05 12:30 | 4.02 | 3.99
2018-08-05 13:00 | 4.02 | 4
2018-08-05 13:30 | 4.18 | 4.15
2018-08-05 14:00 | 4.52 | 4.5
2018-08-05 14:30 | 4.8 | 4.77
2018-08-05 15:00 | 5.36 | 5.33
2018-08-05 15:30 | 6.01 | 5.99
2018-08-05 16:00 | 6.76 | 6.74
2018-08-05 16:30 | 7.83 | 7.81
2018-08-05 17:00 | 9.24 | 9.23
2018-08-05 17:30 | 10.3 | 10.29
2018-08-05 18:00 | 11.45 | 11.44
2018-08-05 18:30 | 11.79 | 11.79
2018-08-05 19:00 | 11.8 | 11.79
2018-08-05 19:30 | 11.25 | 11.24
2018-08-05 20:00 | 11.14 | 11.14
2018-08-05 20:30 | 10.9 | 10.89
2018-08-05 21:00 | 10.53 | 10.53
2018-08-05 21:30 | 9.9 | 9.89
2018-08-05 22:00 | 9.06 | 9.05
2018-08-05 22:30 | 8.54 | 8.53
2018-08-05 23:00 | 8.19 | 8.18
2018-08-05 23:30 | 7.3 | 7.28
2018-08-06 | 6.46 | 6.43
2018-08-06 00:30 | 5.82 | 5.78
2018-08-06 01:00 | 5.36 | 5.32
2018-08-06 01:30 | 4.96 | 4.91
2018-08-06 02:00 | 4.67 | 4.62
2018-08-06 02:30 | 4.59 | 4.54
2018-08-06 03:00 | 4.48 | 4.42
2018-08-06 03:30 | 4.44 | 4.38
2018-08-06 04:00 | 4.53 | 4.47
2018-08-06 04:30 | 4.66 | 4.61
2018-08-06 05:00 | 5.14 | 5.1
2018-08-06 05:30 | 5.81 | 5.78
2018-08-06 06:00 | 6.49 | 6.46
2018-08-06 06:30 | 7.04 | 7.02
2018-08-06 07:00 | 7.83 | 7.8
2018-08-06 07:30 | 8.12 | 8.09
2018-08-06 08:00 | 7.54 | 7.51
2018-08-06 08:30 | 6.43 | 6.39
2018-08-06 09:00 | 5.17 | 5.12
2018-08-06 09:30 | 4.44 | 4.4
2018-08-06 10:00 | 4.03 | 4
2018-08-06 10:30 | 3.52 | 3.48
2018-08-06 11:00 | 3.03 | 3
2018-08-06 11:30 | 2.93 | 2.9
2018-08-06 12:00 | 2.7 | 2.67
2018-08-06 12:30 | 2.72 | 2.69
2018-08-06 13:00 | 2.87 | 2.85
2018-08-06 13:30 | 3.74 | 3.71
2018-08-06 14:00 | 4.28 | 4.26
2018-08-06 14:30 | 4 | 3.98
2018-08-06 15:00 | 4.53 | 4.51
2018-08-06 15:30 | 5.54 | 5.53
2018-08-06 16:00 | 7.14 | 7.13
2018-08-06 16:30 | 7.97 | 7.96
2018-08-06 17:00 | 9.43 | 9.41
2018-08-06 17:30 | 10.62 | 10.61
2018-08-06 18:00 | 11.41 | 11.4
2018-08-06 18:30 | 11.8 | 11.79
2018-08-06 19:00 | 11.97 | 11.97
2018-08-06 19:30 | 11.66 | 11.65
2018-08-06 20:00 | 11.31 | 11.3
2018-08-06 20:30 | 11.39 | 11.39
2018-08-06 21:00 | 10.76 | 10.75
2018-08-06 21:30 | 9.91 | 9.91
2018-08-06 22:00 | 9.02 | 9.01
2018-08-06 22:30 | 8.31 | 8.3
2018-08-06 23:00 | 7.94 | 7.93
2018-08-06 23:30 | 7.06 | 7.04
2018-08-07 | 6.14 | 6.12
2018-08-07 00:30 | 5.49 | 5.46
2018-08-07 01:00 | 5.11 | 5.07
2018-08-07 01:30 | 4.82 | 4.78
2018-08-07 02:00 | 4.56 | 4.51
2018-08-07 02:30 | 4.37 | 4.31
2018-08-07 03:00 | 4.24 | 4.18
2018-08-07 03:30 | 4.35 | 4.29
2018-08-07 04:00 | 4.51 | 4.45
2018-08-07 04:30 | 4.66 | 4.61
2018-08-07 05:00 | 5.07 | 5.03
2018-08-07 05:30 | 5.59 | 5.56
2018-08-07 06:00 | 6.28 | 6.25
2018-08-07 06:30 | 6.98 | 6.96
2018-08-07 07:00 | 7.51 | 7.47
2018-08-07 07:30 | 8.35 | 8.32
2018-08-07 08:00 | 7.93 | 7.9
2018-08-07 08:30 | 6.59 | 6.55
2018-08-07 09:00 | 6.47 | 6.44
2018-08-07 09:30 | 7.51 | 7.48
2018-08-07 10:00 | 6.77 | 6.74
2018-08-07 10:30 | 6.96 | 6.93
2018-08-07 11:00 | 6.27 | 6.23
2018-08-07 11:30 | 4.45 | 4.41
2018-08-07 12:00 | 5.37 | 5.33
2018-08-07 12:30 | 5.28 | 5.23
2018-08-07 13:00 | 5.45 | 5.4
2018-08-07 13:30 | 4.37 | 4.31
2018-08-07 14:00 | 4.51 | 4.46
2018-08-07 14:30 | 3.95 | 3.89
2018-08-07 15:00 | 3.99 | 3.94
2018-08-07 15:30 | 5.69 | 5.65
2018-08-07 16:00 | 6.18 | 6.15
2018-08-07 16:30 | 7.03 | 7.01
2018-08-07 17:00 | 8.64 | 8.62
2018-08-07 17:30 | 10.12 | 10.12
2018-08-07 18:00 | 11.78 | 11.77
2018-08-07 18:30 | 12.78 | 12.78
2018-08-07 19:00 | 13.29 | 13.29
2018-08-07 19:30 | 13.1 | 13.1
2018-08-07 20:00 | 12.88 | 12.88
2018-08-07 20:30 | 13.09 | 13.09
2018-08-07 21:00 | 12.69 | 12.69
2018-08-07 21:30 | 11.77 | 11.77
2018-08-07 22:00 | 10.93 | 10.92
2018-08-07 22:30 | 10.2 | 10.19
2018-08-07 23:00 | 9.68 | 9.67
2018-08-07 23:30 | 8.67 | 8.66
2018-08-08 | 7.6 | 7.58
2018-08-08 00:30 | 6.82 | 6.79
2018-08-08 01:00 | 6.45 | 6.43
2018-08-08 01:30 | 6.08 | 6.04
2018-08-08 02:00 | 5.75 | 5.71
2018-08-08 02:30 | 5.57 | 5.53
2018-08-08 03:00 | 5.45 | 5.4
2018-08-08 03:30 | 5.57 | 5.53
2018-08-08 04:00 | 5.75 | 5.71
2018-08-08 04:30 | 6.09 | 6.06
2018-08-08 05:00 | 6.66 | 6.63
2018-08-08 05:30 | 7.58 | 7.57
2018-08-08 06:00 | 8.64 | 8.63
2018-08-08 06:30 | 9.74 | 9.74
2018-08-08 07:00 | 10.82 | 10.81
2018-08-08 07:30 | 11.25 | 11.25
2018-08-08 08:00 | 10.31 | 10.31
2018-08-08 08:30 | 8.69 | 8.68
2018-08-08 09:00 | 6.99 | 6.97
2018-08-08 09:30 | 6.01 | 5.99
2018-08-08 10:00 | 5.2 | 5.17
2018-08-08 10:30 | 4.37 | 4.34
2018-08-08 11:00 | 3.78 | 3.74
2018-08-08 11:30 | 3.41 | 3.36
2018-08-08 12:00 | 3.2 | 3.14
2018-08-08 12:30 | 3.06 | 3
2018-08-08 13:00 | 3.05 | 3
2018-08-08 13:30 | 3.03 | 2.97
2018-08-08 14:00 | 3.41 | 3.36
2018-08-08 14:30 | 3.77 | 3.72
2018-08-08 15:00 | 4.05 | 4
2018-08-08 15:30 | 4.92 | 4.88
2018-08-08 16:00 | 6.16 | 6.13
2018-08-08 16:30 | 7.32 | 7.3
2018-08-08 17:00 | 8.43 | 8.41
2018-08-08 17:30 | 9.56 | 9.55
2018-08-08 18:00 | 11.53 | 11.53
2018-08-08 18:30 | 12.66 | 12.65
2018-08-08 19:00 | 13.33 | 13.33
2018-08-08 19:30 | 13.33 | 13.33
2018-08-08 20:00 | 13.19 | 13.19
2018-08-08 20:30 | 13.46 | 13.45
2018-08-08 21:00 | 12.95 | 12.95
2018-08-08 21:30 | 12.21 | 12.21
2018-08-08 22:00 | 11.34 | 11.33
2018-08-08 22:30 | 10.57 | 10.56
2018-08-08 23:00 | 10.09 | 10.09
2018-08-08 23:30 | 9.04 | 9.03
2018-08-09 | 8.09 | 8.07
2018-08-09 00:30 | 7.21 | 7.19
2018-08-09 01:00 | 6.78 | 6.76
2018-08-09 01:30 | 6.45 | 6.42
2018-08-09 02:00 | 6.09 | 6.06
2018-08-09 02:30 | 5.93 | 5.9
2018-08-09 03:00 | 5.8 | 5.76
2018-08-09 03:30 | 5.89 | 5.86
2018-08-09 04:00 | 6.01 | 5.98
2018-08-09 04:30 | 6.35 | 6.32
2018-08-09 05:00 | 6.89 | 6.87
2018-08-09 05:30 | 7.92 | 7.91
2018-08-09 06:00 | 8.9 | 8.89
2018-08-09 06:30 | 10.01 | 10
2018-08-09 07:00 | 11.33 | 11.33
2018-08-09 07:30 | 11.78 | 11.78
2018-08-09 08:00 | 11.44 | 11.44
2018-08-09 08:30 | 9.76 | 9.75
2018-08-09 09:00 | 8.13 | 8.11
2018-08-09 09:30 | 7.02 | 7
2018-08-09 10:00 | 6.11 | 6.08
2018-08-09 10:30 | 5.22 | 5.19
2018-08-09 11:00 | 4.63 | 4.59
2018-08-09 11:30 | 4.27 | 4.23
2018-08-09 12:00 | 4.09 | 4.04
2018-08-09 12:30 | 3.97 | 3.93
2018-08-09 13:00 | 3.95 | 3.9
2018-08-09 13:30 | 4.02 | 3.97
2018-08-09 14:00 | 4.25 | 4.2
2018-08-09 14:30 | 4.59 | 4.54
2018-08-09 15:00 | 4.88 | 4.84
2018-08-09 15:30 | 5.7 | 5.66
2018-08-09 16:00 | 6.82 | 6.79
2018-08-09 16:30 | 7.39 | 7.37
2018-08-09 17:00 | 8.48 | 8.47
2018-08-09 17:30 | 9.95 | 9.94
2018-08-09 18:00 | 11.4 | 11.4
2018-08-09 18:30 | 12.32 | 12.31
2018-08-09 19:00 | 12.99 | 12.99
2018-08-09 19:30 | 12.89 | 12.89
2018-08-09 20:00 | 13.29 | 13.29
2018-08-09 20:30 | 13.44 | 13.43
2018-08-09 21:00 | 13.12 | 13.11
2018-08-09 21:30 | 12.31 | 12.3
2018-08-09 22:00 | 11.21 | 11.2
2018-08-09 22:30 | 10.52 | 10.51
2018-08-09 23:00 | 10.04 | 10.03
2018-08-09 23:30 | 9.04 | 9.04
2018-08-10 | 7.99 | 7.97
2018-08-10 00:30 | 7.09 | 7.07
2018-08-10 01:00 | 6.71 | 6.68
2018-08-10 01:30 | 6.31 | 6.28
2018-08-10 02:00 | 5.96 | 5.92
2018-08-10 02:30 | 5.75 | 5.71
2018-08-10 03:00 | 5.79 | 5.75
2018-08-10 03:30 | 5.86 | 5.83
2018-08-10 04:00 | 5.96 | 5.93
2018-08-10 04:30 | 6.19 | 6.17
2018-08-10 05:00 | 6.83 | 6.81
2018-08-10 05:30 | 7.75 | 7.75
2018-08-10 06:00 | 8.65 | 8.64
2018-08-10 06:30 | 9.65 | 9.65
2018-08-10 07:00 | 10.6 | 10.59
2018-08-10 07:30 | 11.1 | 11.09
2018-08-10 08:00 | 10.38 | 10.38
2018-08-10 08:30 | 10.01 | 10
2018-08-10 09:00 | 8.76 | 8.74
2018-08-10 09:30 | 7.6 | 7.58
2018-08-10 10:00 | 6.77 | 6.75
2018-08-10 10:30 | 5.73 | 5.69
2018-08-10 11:00 | 5.05 | 5
2018-08-10 11:30 | 4.7 | 4.66
2018-08-10 12:00 | 4.67 | 4.62
2018-08-10 12:30 | 5.06 | 5.02
2018-08-10 13:00 | 4.21 | 4.18
2018-08-10 13:30 | 3.48 | 3.44
2018-08-10 14:00 | 3.35 | 3.31
2018-08-10 14:30 | 3.42 | 3.38
2018-08-10 15:00 | 3.83 | 3.79
2018-08-10 15:30 | 4.62 | 4.59
2018-08-10 16:00 | 5.75 | 5.73
2018-08-10 16:30 | 6.94 | 6.92
2018-08-10 17:00 | 8.19 | 8.17
2018-08-10 17:30 | 9.22 | 9.21
2018-08-10 18:00 | 10.51 | 10.5
2018-08-10 18:30 | 11.6 | 11.59
2018-08-10 19:00 | 11.96 | 11.96
2018-08-10 19:30 | 11.99 | 11.99
2018-08-10 20:00 | 12.02 | 12.02
2018-08-10 20:30 | 12.29 | 12.29
2018-08-10 21:00 | 11.89 | 11.89
2018-08-10 21:30 | 11.42 | 11.42
2018-08-10 22:00 | 10.73 | 10.72
2018-08-10 22:30 | 10.41 | 10.4
2018-08-10 23:00 | 9.98 | 9.97
2018-08-10 23:30 | 8.92 | 8.91
2018-08-11 | 7.89 | 7.88
2018-08-11 00:30 | 7.07 | 7.05
2018-08-11 01:00 | 6.62 | 6.6
2018-08-11 01:30 | 6.13 | 6.1
2018-08-11 02:00 | 5.61 | 5.58
2018-08-11 02:30 | 5.41 | 5.38
2018-08-11 03:00 | 5.26 | 5.22
2018-08-11 03:30 | 5.18 | 5.14
2018-08-11 04:00 | 5.1 | 5.07
2018-08-11 04:30 | 5.27 | 5.23
2018-08-11 05:00 | 5.36 | 5.33
2018-08-11 05:30 | 5.61 | 5.58
2018-08-11 06:00 | 6 | 5.97
2018-08-11 06:30 | 6.26 | 6.22
2018-08-11 07:00 | 6.86 | 6.82
2018-08-11 07:30 | 7.33 | 7.29
2018-08-11 08:00 | 7.35 | 7.31
2018-08-11 08:30 | 6.95 | 6.92
2018-08-11 09:00 | 6.66 | 6.64
2018-08-11 09:30 | 6.28 | 6.26
2018-08-11 10:00 | 5.54 | 5.52
2018-08-11 10:30 | 4.85 | 4.82
2018-08-11 11:00 | 4.26 | 4.23
2018-08-11 11:30 | 4.1 | 4.07
2018-08-11 12:00 | 3.87 | 3.84
2018-08-11 12:30 | 3.73 | 3.7
2018-08-11 13:00 | 3.52 | 3.48
2018-08-11 13:30 | 3.64 | 3.6
2018-08-11 14:00 | 3.99 | 3.96
2018-08-11 14:30 | 4.18 | 4.15
2018-08-11 15:00 | 4.45 | 4.42
2018-08-11 15:30 | 5.2 | 5.18
2018-08-11 16:00 | 6.05 | 6.03
2018-08-11 16:30 | 6.97 | 6.95
2018-08-11 17:00 | 7.91 | 7.89
2018-08-11 17:30 | 8.97 | 8.96
2018-08-11 18:00 | 9.95 | 9.95
2018-08-11 18:30 | 10.45 | 10.44
2018-08-11 19:00 | 10.75 | 10.74
2018-08-11 19:30 | 10.51 | 10.51
2018-08-11 20:00 | 10.49 | 10.48
2018-08-11 20:30 | 10.39 | 10.38
2018-08-11 21:00 | 10.02 | 10.02
2018-08-11 21:30 | 9.51 | 9.5
2018-08-11 22:00 | 9.08 | 9.08
2018-08-11 22:30 | 8.89 | 8.89
2018-08-11 23:00 | 8.69 | 8.68
2018-08-11 23:30 | 7.86 | 7.85
2018-08-12 | 7.06 | 7.04
2018-08-12 00:30 | 6.38 | 6.35
2018-08-12 01:00 | 5.83 | 5.8
2018-08-12 01:30 | 5.5 | 5.47
2018-08-12 02:00 | 5.16 | 5.12
2018-08-12 02:30 | 4.94 | 4.89
2018-08-12 03:00 | 4.82 | 4.77
2018-08-12 03:30 | 4.77 | 4.72
2018-08-12 04:00 | 4.71 | 4.66
2018-08-12 04:30 | 4.67 | 4.62
2018-08-12 05:00 | 4.83 | 4.78
2018-08-12 05:30 | 4.98 | 4.93
2018-08-12 06:00 | 5.16 | 5.12
2018-08-12 06:30 | 5.43 | 5.36
2018-08-12 07:00 | 5.77 | 5.69
2018-08-12 07:30 | 6.02 | 5.95
2018-08-12 08:00 | 6.24 | 6.19
2018-08-12 08:30 | 6.44 | 6.39
2018-08-12 09:00 | 6.11 | 6.07
2018-08-12 09:30 | 5.96 | 5.93
2018-08-12 10:00 | 5.43 | 5.4
2018-08-12 10:30 | 4.9 | 4.87
2018-08-12 11:00 | 4.49 | 4.46
2018-08-12 11:30 | 4.21 | 4.19
2018-08-12 12:00 | 4.01 | 3.98
2018-08-12 12:30 | 3.85 | 3.82
2018-08-12 13:00 | 3.76 | 3.73
2018-08-12 13:30 | 3.9 | 3.87
2018-08-12 14:00 | 4.17 | 4.14
2018-08-12 14:30 | 4.51 | 4.48
2018-08-12 15:00 | 4.8 | 4.76
2018-08-12 15:30 | 5.51 | 5.48
2018-08-12 16:00 | 6.45 | 6.42
2018-08-12 16:30 | 7.4 | 7.38
2018-08-12 17:00 | 9 | 8.98
2018-08-12 17:30 | 10.31 | 10.3
2018-08-12 18:00 | 11.66 | 11.65
2018-08-12 18:30 | 12.38 | 12.37
2018-08-12 19:00 | 12.72 | 12.71
2018-08-12 19:30 | 12.39 | 12.39
2018-08-12 20:00 | 12.33 | 12.32
2018-08-12 20:30 | 12.46 | 12.45
2018-08-12 21:00 | 12 | 12
2018-08-12 21:30 | 11.23 | 11.23
2018-08-12 22:00 | 10.46 | 10.45
2018-08-12 22:30 | 9.94 | 9.93
2018-08-12 23:00 | 9.56 | 9.55
2018-08-12 23:30 | 8.52 | 8.51
2018-08-13 | 7.64 | 7.62
2018-08-13 00:30 | 6.95 | 6.92
2018-08-13 01:00 | 6.49 | 6.46
2018-08-13 01:30 | 6.12 | 6.09
2018-08-13 02:00 | 5.79 | 5.75
2018-08-13 02:30 | 5.68 | 5.64
2018-08-13 03:00 | 5.63 | 5.59
2018-08-13 03:30 | 5.58 | 5.54
2018-08-13 04:00 | 5.71 | 5.67
2018-08-13 04:30 | 6.04 | 6.01
2018-08-13 05:00 | 6.67 | 6.65
2018-08-13 05:30 | 7.66 | 7.64
2018-08-13 06:00 | 8.99 | 8.98
2018-08-13 06:30 | 9.83 | 9.82
2018-08-13 07:00 | 11.19 | 11.19
2018-08-13 07:30 | 11.79 | 11.79
2018-08-13 08:00 | 10.92 | 10.92
2018-08-13 08:30 | 9.18 | 9.17
2018-08-13 09:00 | 7.56 | 7.56
2018-08-13 09:30 | 6.52 | 6.51
2018-08-13 10:00 | 5.57 | 5.55
2018-08-13 10:30 | 5.11 | 5.1
2018-08-13 11:00 | 4.47 | 4.46
2018-08-13 11:30 | 3.93 | 3.91
2018-08-13 12:00 | 3.71 | 3.68
2018-08-13 12:30 | 3.68 | 3.66
2018-08-13 13:00 | 3.5 | 3.47
2018-08-13 13:30 | 3.43 | 3.39
2018-08-13 14:00 | 3.84 | 3.81
2018-08-13 14:30 | 4.12 | 4.09
2018-08-13 15:00 | 4.49 | 4.46
2018-08-13 15:30 | 5.33 | 5.3
2018-08-13 16:00 | 6.47 | 6.45
2018-08-13 16:30 | 7.63 | 7.61
2018-08-13 17:00 | 9.38 | 9.37
2018-08-13 17:30 | 11.07 | 11.07
2018-08-13 18:00 | 12.89 | 12.89
2018-08-13 18:30 | 13.91 | 13.9
2018-08-13 19:00 | 14.35 | 14.35
2018-08-13 19:30 | 14.45 | 14.45
2018-08-13 20:00 | 14.61 | 14.6
2018-08-13 20:30 | 14.52 | 14.51
2018-08-13 21:00 | 13.68 | 13.67
2018-08-13 21:30 | 12.72 | 12.71
2018-08-13 22:00 | 11.56 | 11.55
2018-08-13 22:30 | 10.78 | 10.77
2018-08-13 23:00 | 10.11 | 10.11
2018-08-13 23:30 | 9.01 | 9
2018-08-14 | 8.06 | 8.05
2018-08-14 00:30 | 7.27 | 7.25
2018-08-14 01:00 | 6.82 | 6.8
2018-08-14 01:30 | 6.37 | 6.34
2018-08-14 02:00 | 6.14 | 6.11
2018-08-14 02:30 | 5.94 | 5.9
2018-08-14 03:00 | 5.92 | 5.88
2018-08-14 03:30 | 6.02 | 5.98
2018-08-14 04:00 | 6.21 | 6.18
2018-08-14 04:30 | 6.46 | 6.44
2018-08-14 05:00 | 7.01 | 6.99
2018-08-14 05:30 | 8.12 | 8.11
2018-08-14 06:00 | 9.09 | 9.08
2018-08-14 06:30 | 10.23 | 10.22
2018-08-14 07:00 | 11.59 | 11.58
2018-08-14 07:30 | 12.5 | 12.5
2018-08-14 08:00 | 11.58 | 11.58
2018-08-14 08:30 | 9.64 | 9.64
2018-08-14 09:00 | 7.95 | 7.94
2018-08-14 09:30 | 6.82 | 6.82
2018-08-14 10:00 | 5.92 | 5.91
2018-08-14 10:30 | 5.27 | 5.26
2018-08-14 11:00 | 4.51 | 4.5
2018-08-14 11:30 | 3.91 | 3.89
2018-08-14 12:00 | 3.64 | 3.62
2018-08-14 12:30 | 3.51 | 3.47
2018-08-14 13:00 | 3.58 | 3.55
2018-08-14 13:30 | 3.45 | 3.42
2018-08-14 14:00 | 3.74 | 3.71
2018-08-14 14:30 | 4.02 | 4
2018-08-14 15:00 | 4.33 | 4.31
2018-08-14 15:30 | 5.16 | 5.14
2018-08-14 16:00 | 6.26 | 6.25
2018-08-14 16:30 | 7.41 | 7.4
2018-08-14 17:00 | 8.91 | 8.91
2018-08-14 17:30 | 10.23 | 10.23
2018-08-14 18:00 | 11.9 | 11.9
2018-08-14 18:30 | 13.01 | 13.01
2018-08-14 19:00 | 13.28 | 13.28
2018-08-14 19:30 | 13.13 | 13.13
2018-08-14 20:00 | 13.22 | 13.22
2018-08-14 20:30 | 13.36 | 13.36
2018-08-14 21:00 | 12.87 | 12.87
2018-08-14 21:30 | 12.08 | 12.08
2018-08-14 22:00 | 11.24 | 11.23
2018-08-14 22:30 | 10.61 | 10.61
2018-08-14 23:00 | 10.19 | 10.19
2018-08-14 23:30 | 9.16 | 9.15
2018-08-15 | 7.96 | 7.94
2018-08-15 00:30 | 6.96 | 6.93
2018-08-15 01:00 | 6.58 | 6.55
2018-08-15 01:30 | 6.19 | 6.16
2018-08-15 02:00 | 5.83 | 5.79
2018-08-15 02:30 | 5.66 | 5.63
2018-08-15 03:00 | 5.52 | 5.48
2018-08-15 03:30 | 5.64 | 5.6
2018-08-15 04:00 | 5.71 | 5.67
2018-08-15 04:30 | 5.86 | 5.83
2018-08-15 05:00 | 6.44 | 6.42
2018-08-15 05:30 | 7 | 6.98
2018-08-15 06:00 | 7.66 | 7.65
2018-08-15 06:30 | 8.49 | 8.47
2018-08-15 07:00 | 9.7 | 9.69
2018-08-15 07:30 | 10.53 | 10.52
2018-08-15 08:00 | 10.45 | 10.44
2018-08-15 08:30 | 10.8 | 10.79
2018-08-15 09:00 | 9.47 | 9.46
2018-08-15 09:30 | 7.91 | 7.9
2018-08-15 10:00 | 6.24 | 6.23
2018-08-15 10:30 | 5.24 | 5.23
2018-08-15 11:00 | 4.62 | 4.6
2018-08-15 11:30 | 4.26 | 4.24
2018-08-15 12:00 | 4.01 | 3.99
2018-08-15 12:30 | 3.86 | 3.85
2018-08-15 13:00 | 3.91 | 3.9
2018-08-15 13:30 | 3.84 | 3.83
2018-08-15 14:00 | 4.26 | 4.25
2018-08-15 14:30 | 4.65 | 4.65
2018-08-15 15:00 | 4.94 | 4.93
2018-08-15 15:30 | 5.76 | 5.75
2018-08-15 16:00 | 6.83 | 6.83
2018-08-15 16:30 | 7.89 | 7.88
2018-08-15 17:00 | 9.15 | 9.15
2018-08-15 17:30 | 10.22 | 10.22
2018-08-15 18:00 | 11.65 | 11.65
2018-08-15 18:30 | 12.43 | 12.43
2018-08-15 19:00 | 12.58 | 12.58
2018-08-15 19:30 | 12.48 | 12.48
2018-08-15 20:00 | 12.6 | 12.6
2018-08-15 20:30 | 12.78 | 12.78
2018-08-15 21:00 | 12.21 | 12.21
2018-08-15 21:30 | 11.29 | 11.29
2018-08-15 22:00 | 10.66 | 10.66
2018-08-15 22:30 | 9.84 | 9.83
2018-08-15 23:00 | 9.1 | 9.09
2018-08-15 23:30 | 8.13 | 8.12
2018-08-16 | 8.12 | 8.09
2018-08-16 00:30 | 7.94 | 7.9
2018-08-16 01:00 | 7.52 | 7.48
2018-08-16 01:30 | 7.13 | 7.09
2018-08-16 02:00 | 6.77 | 6.72
2018-08-16 02:30 | 5.59 | 5.55
2018-08-16 03:00 | 5.2 | 5.16
2018-08-16 03:30 | 5.19 | 5.15
2018-08-16 04:00 | 5.38 | 5.34
2018-08-16 04:30 | 5.59 | 5.55
2018-08-16 05:00 | 6.15 | 6.12
2018-08-16 05:30 | 7.16 | 7.15
2018-08-16 06:00 | 8.42 | 8.41
2018-08-16 06:30 | 9.37 | 9.37
2018-08-16 07:00 | 10.5 | 10.49
2018-08-16 07:30 | 10.58 | 10.58
2018-08-16 08:00 | 9.5 | 9.5
2018-08-16 08:30 | 7.69 | 7.68
2018-08-16 09:00 | 6.17 | 6.15
2018-08-16 09:30 | 5.31 | 5.3
2018-08-16 10:00 | 4.5 | 4.48
2018-08-16 10:30 | 3.59 | 3.57
2018-08-16 11:00 | 2.88 | 2.84
2018-08-16 11:30 | 2.5 | 2.45
2018-08-16 12:00 | 2.42 | 2.38
2018-08-16 12:30 | 3.13 | 3.1
2018-08-16 13:00 | 3.05 | 3.02
2018-08-16 13:30 | 2.67 | 2.64
2018-08-16 14:00 | 3.04 | 3.02
2018-08-16 14:30 | 3.41 | 3.39
2018-08-16 15:00 | 3.72 | 3.7
2018-08-16 15:30 | 4.55 | 4.53
2018-08-16 16:00 | 5.64 | 5.63
2018-08-16 16:30 | 6.64 | 6.63
2018-08-16 17:00 | 7.94 | 7.93
2018-08-16 17:30 | 8.88 | 8.87
2018-08-16 18:00 | 10.13 | 10.12
2018-08-16 18:30 | 11.08 | 11.08
2018-08-16 19:00 | 11.46 | 11.45
2018-08-16 19:30 | 11.29 | 11.28
2018-08-16 20:00 | 11.32 | 11.31
2018-08-16 20:30 | 11.35 | 11.35
2018-08-16 21:00 | 11.11 | 11.1
2018-08-16 21:30 | 10.32 | 10.31
2018-08-16 22:00 | 9.69 | 9.68
2018-08-16 22:30 | 9.25 | 9.24
2018-08-16 23:00 | 8.85 | 8.84
2018-08-16 23:30 | 8 | 7.98
2018-08-17 | 7.07 | 7.05
2018-08-17 00:30 | 6.29 | 6.26
2018-08-17 01:00 | 5.92 | 5.89
2018-08-17 01:30 | 5.6 | 5.56
2018-08-17 02:00 | 5.34 | 5.3
2018-08-17 02:30 | 5.11 | 5.06
2018-08-17 03:00 | 5.07 | 5.02
2018-08-17 03:30 | 5.13 | 5.08
2018-08-17 04:00 | 5.22 | 5.17
2018-08-17 04:30 | 5.46 | 5.42
2018-08-17 05:00 | 5.94 | 5.91
2018-08-17 05:30 | 6.66 | 6.63
2018-08-17 06:00 | 7.38 | 7.36
2018-08-17 06:30 | 8.28 | 8.26
2018-08-17 07:00 | 9.29 | 9.28
2018-08-17 07:30 | 9.67 | 9.66
2018-08-17 08:00 | 9.12 | 9.11
2018-08-17 08:30 | 8.09 | 8.06
2018-08-17 09:00 | 6.64 | 6.61
2018-08-17 09:30 | 5.62 | 5.58
2018-08-17 10:00 | 3.92 | 3.89
2018-08-17 10:30 | 3.27 | 3.23
2018-08-17 11:00 | 3 | 2.97
2018-08-17 11:30 | 2.83 | 2.8
2018-08-17 12:00 | 2.55 | 2.52
2018-08-17 12:30 | 2.41 | 2.38
2018-08-17 13:00 | 2.5 | 2.48
2018-08-17 13:30 | 2.7 | 2.67
2018-08-17 14:00 | 3.05 | 3.02
2018-08-17 14:30 | 3.54 | 3.52
2018-08-17 15:00 | 4.01 | 4
2018-08-17 15:30 | 4.75 | 4.74
2018-08-17 16:00 | 5.81 | 5.79
2018-08-17 16:30 | 6.7 | 6.69
2018-08-17 17:00 | 7.84 | 7.83
2018-08-17 17:30 | 8.68 | 8.67
2018-08-17 18:00 | 9.6 | 9.59
2018-08-17 18:30 | 10.5 | 10.49
2018-08-17 19:00 | 10.7 | 10.69
2018-08-17 19:30 | 10.55 | 10.54
2018-08-17 20:00 | 10.65 | 10.65
2018-08-17 20:30 | 10.71 | 10.7
2018-08-17 21:00 | 10.22 | 10.21
2018-08-17 21:30 | 9.69 | 9.68
2018-08-17 22:00 | 9.25 | 9.25
2018-08-17 22:30 | 8.93 | 8.92
2018-08-17 23:00 | 8.73 | 8.71
2018-08-17 23:30 | 7.91 | 7.9
2018-08-18 | 7.14 | 7.12
2018-08-18 00:30 | 6.39 | 6.36
2018-08-18 01:00 | 6 | 5.96
2018-08-18 01:30 | 5.62 | 5.58
2018-08-18 02:00 | 5.24 | 5.2
2018-08-18 02:30 | 4.97 | 4.92
2018-08-18 03:00 | 4.9 | 4.84
2018-08-18 03:30 | 5.03 | 4.97
2018-08-18 04:00 | 4.92 | 4.87
2018-08-18 04:30 | 4.95 | 4.89
2018-08-18 05:00 | 5.14 | 5.1
2018-08-18 05:30 | 5.51 | 5.46
2018-08-18 06:00 | 5.89 | 5.85
2018-08-18 06:30 | 6.2 | 6.13
2018-08-18 07:00 | 6.85 | 6.8
2018-08-18 07:30 | 7.07 | 7.03
2018-08-18 08:00 | 6.98 | 6.94
2018-08-18 08:30 | 6.51 | 6.47
2018-08-18 09:00 | 6.02 | 5.99
2018-08-18 09:30 | 5.69 | 5.67
2018-08-18 10:00 | 5.12 | 5.1
2018-08-18 10:30 | 4.54 | 4.51
2018-08-18 11:00 | 4.05 | 4.03
2018-08-18 11:30 | 3.71 | 3.69
2018-08-18 12:00 | 3.43 | 3.4
2018-08-18 12:30 | 3.35 | 3.32
2018-08-18 13:00 | 3.27 | 3.22
2018-08-18 13:30 | 3.51 | 3.47
2018-08-18 14:00 | 3.78 | 3.75
2018-08-18 14:30 | 3.99 | 3.96
2018-08-18 15:00 | 4.5 | 4.47
2018-08-18 15:30 | 5.14 | 5.12
2018-08-18 16:00 | 5.91 | 5.89
2018-08-18 16:30 | 6.8 | 6.78
2018-08-18 17:00 | 7.85 | 7.83
2018-08-18 17:30 | 8.57 | 8.56
2018-08-18 18:00 | 9.47 | 9.45
2018-08-18 18:30 | 10.27 | 10.26
2018-08-18 19:00 | 10.52 | 10.51
2018-08-18 19:30 | 10.15 | 10.14
2018-08-18 20:00 | 10.17 | 10.17
2018-08-18 20:30 | 10.19 | 10.18
2018-08-18 21:00 | 9.87 | 9.86
2018-08-18 21:30 | 9.35 | 9.35
2018-08-18 22:00 | 9.03 | 9.02
2018-08-18 22:30 | 8.82 | 8.81
2018-08-18 23:00 | 8.72 | 8.7
2018-08-18 23:30 | 8.07 | 8.05
2018-08-19 | 7.3 | 7.28
2018-08-19 00:30 | 6.65 | 6.63
2018-08-19 01:00 | 6.29 | 6.27
2018-08-19 01:30 | 5.86 | 5.82
2018-08-19 02:00 | 5.47 | 5.43
2018-08-19 02:30 | 5.19 | 5.14
2018-08-19 03:00 | 5.03 | 4.98
2018-08-19 03:30 | 5.04 | 4.99
2018-08-19 04:00 | 4.99 | 4.94
2018-08-19 04:30 | 5.03 | 4.98
2018-08-19 05:00 | 5.17 | 5.12
2018-08-19 05:30 | 5.26 | 5.22
2018-08-19 06:00 | 5.55 | 5.5
2018-08-19 06:30 | 5.77 | 5.69
2018-08-19 07:00 | 6.18 | 6.11
2018-08-19 07:30 | 6.38 | 6.32
2018-08-19 08:00 | 6.31 | 6.25
2018-08-19 08:30 | 6.24 | 6.2
2018-08-19 09:00 | 6.13 | 6.09
2018-08-19 09:30 | 5.7 | 5.66
2018-08-19 10:00 | 5.1 | 5.07
2018-08-19 10:30 | 4.71 | 4.69
2018-08-19 11:00 | 4.2 | 4.18
2018-08-19 11:30 | 3.88 | 3.85
2018-08-19 12:00 | 3.89 | 3.86
2018-08-19 12:30 | 3.64 | 3.61
2018-08-19 13:00 | 3.5 | 3.46
2018-08-19 13:30 | 3.67 | 3.63
2018-08-19 14:00 | 3.91 | 3.88
2018-08-19 14:30 | 4.26 | 4.23
2018-08-19 15:00 | 4.74 | 4.7
2018-08-19 15:30 | 5.35 | 5.31
2018-08-19 16:00 | 6.34 | 6.3
2018-08-19 16:30 | 7.54 | 7.51
2018-08-19 17:00 | 8.96 | 8.94
2018-08-19 17:30 | 10.35 | 10.34
2018-08-19 18:00 | 11.67 | 11.66
2018-08-19 18:30 | 12.65 | 12.64
2018-08-19 19:00 | 12.98 | 12.98
2018-08-19 19:30 | 12.72 | 12.71
2018-08-19 20:00 | 12.47 | 12.46
2018-08-19 20:30 | 12.58 | 12.57
2018-08-19 21:00 | 12.15 | 12.15
2018-08-19 21:30 | 11.44 | 11.43
2018-08-19 22:00 | 10.61 | 10.61
2018-08-19 22:30 | 9.73 | 9.72
2018-08-19 23:00 | 9.2 | 9.19
2018-08-19 23:30 | 8.26 | 8.24
2018-08-20 | 7.26 | 7.24
2018-08-20 00:30 | 6.55 | 6.51
2018-08-20 01:00 | 6.09 | 6.06
2018-08-20 01:30 | 5.71 | 5.67
2018-08-20 02:00 | 5.37 | 5.32
2018-08-20 02:30 | 5.22 | 5.17
2018-08-20 03:00 | 5.17 | 5.11
2018-08-20 03:30 | 5.24 | 5.19
2018-08-20 04:00 | 5.24 | 5.19
2018-08-20 04:30 | 5.58 | 5.54
2018-08-20 05:00 | 6.09 | 6.06
2018-08-20 05:30 | 6.82 | 6.8
2018-08-20 06:00 | 7.65 | 7.63
2018-08-20 06:30 | 8.54 | 8.52
2018-08-20 07:00 | 9.45 | 9.44
2018-08-20 07:30 | 9.5 | 9.49
2018-08-20 08:00 | 9.05 | 9.04
2018-08-20 08:30 | 7.55 | 7.54
2018-08-20 09:00 | 6.28 | 6.27
2018-08-20 09:30 | 5.33 | 5.31
2018-08-20 10:00 | 4.69 | 4.68
2018-08-20 10:30 | 4.21 | 4.19
2018-08-20 11:00 | 3.67 | 3.65
2018-08-20 11:30 | 3.38 | 3.36
2018-08-20 12:00 | 3.19 | 3.16
2018-08-20 12:30 | 3.05 | 3.01
2018-08-20 13:00 | 3 | 2.96
2018-08-20 13:30 | 2.98 | 2.94
2018-08-20 14:00 | 3.15 | 3.11
2018-08-20 14:30 | 3.52 | 3.48
2018-08-20 15:00 | 3.91 | 3.87
2018-08-20 15:30 | 4.69 | 4.66
2018-08-20 16:00 | 5.89 | 5.86
2018-08-20 16:30 | 7.46 | 7.44
2018-08-20 17:00 | 8.92 | 8.91
2018-08-20 17:30 | 10.32 | 10.31
2018-08-20 18:00 | 12.28 | 12.28
2018-08-20 18:30 | 13.79 | 13.78
2018-08-20 19:00 | 14.3 | 14.3
2018-08-20 19:30 | 14.05 | 14.05
2018-08-20 20:00 | 14.19 | 14.19
2018-08-20 20:30 | 14.41 | 14.4
2018-08-20 21:00 | 14.01 | 14.01
2018-08-20 21:30 | 13.07 | 13.07
2018-08-20 22:00 | 12.14 | 12.14
2018-08-20 22:30 | 11.01 | 11.01
2018-08-20 23:00 | 10.25 | 10.24
2018-08-20 23:30 | 9.11 | 9.1
2018-08-21 | 8.08 | 8.06
2018-08-21 00:30 | 7.35 | 7.33
2018-08-21 01:00 | 6.89 | 6.86
2018-08-21 01:30 | 6.45 | 6.42
2018-08-21 02:00 | 6.12 | 6.09
2018-08-21 02:30 | 6.09 | 6.06
2018-08-21 03:00 | 5.98 | 5.95
2018-08-21 03:30 | 6.14 | 6.11
2018-08-21 04:00 | 6.33 | 6.31
2018-08-21 04:30 | 6.65 | 6.62
2018-08-21 05:00 | 7.34 | 7.33
2018-08-21 05:30 | 8.57 | 8.56
2018-08-21 06:00 | 9.95 | 9.95
2018-08-21 06:30 | 11.25 | 11.25
2018-08-21 07:00 | 11.99 | 11.99
2018-08-21 07:30 | 12.44 | 12.44
2018-08-21 08:00 | 11.33 | 11.33
2018-08-21 08:30 | 9.13 | 9.12
2018-08-21 09:00 | 7.49 | 7.48
2018-08-21 09:30 | 6.14 | 6.13
2018-08-21 10:00 | 5.14 | 5.12
2018-08-21 10:30 | 4.23 | 4.2
2018-08-21 11:00 | 3.47 | 3.44
2018-08-21 11:30 | 3.2 | 3.17
2018-08-21 12:00 | 2.87 | 2.82
2018-08-21 12:30 | 3.16 | 3.13
2018-08-21 13:00 | 3.23 | 3.2
2018-08-21 13:30 | 3.28 | 3.24
2018-08-21 14:00 | 3.53 | 3.5
2018-08-21 14:30 | 3.88 | 3.85
2018-08-21 15:00 | 4.42 | 4.39
2018-08-21 15:30 | 5.19 | 5.17
2018-08-21 16:00 | 6.47 | 6.45
2018-08-21 16:30 | 7.51 | 7.5
2018-08-21 17:00 | 8.91 | 8.91
2018-08-21 17:30 | 10.35 | 10.35
2018-08-21 18:00 | 12.14 | 12.14
2018-08-21 18:30 | 13.53 | 13.53
2018-08-21 19:00 | 14.07 | 14.07
2018-08-21 19:30 | 13.96 | 13.96
2018-08-21 20:00 | 13.96 | 13.96
2018-08-21 20:30 | 14.16 | 14.16
2018-08-21 21:00 | 13.86 | 13.86
2018-08-21 21:30 | 13.02 | 13.01
2018-08-21 22:00 | 12.06 | 12.06
2018-08-21 22:30 | 10.63 | 10.63
2018-08-21 23:00 | 10.04 | 10.04
2018-08-21 23:30 | 8.95 | 8.94
2018-08-22 | 7.96 | 7.95
2018-08-22 00:30 | 7.22 | 7.2
2018-08-22 01:00 | 6.93 | 6.91
2018-08-22 01:30 | 6.52 | 6.49
2018-08-22 02:00 | 6.16 | 6.13
2018-08-22 02:30 | 6.03 | 6
2018-08-22 03:00 | 5.86 | 5.82
2018-08-22 03:30 | 5.9 | 5.87
2018-08-22 04:00 | 6.12 | 6.09
2018-08-22 04:30 | 6.42 | 6.39
2018-08-22 05:00 | 7.12 | 7.1
2018-08-22 05:30 | 8.11 | 8.1
2018-08-22 06:00 | 9.06 | 9.06
2018-08-22 06:30 | 10.14 | 10.14
2018-08-22 07:00 | 11.25 | 11.25
2018-08-22 07:30 | 11.18 | 11.18
2018-08-22 08:00 | 10.11 | 10.1
2018-08-22 08:30 | 8.14 | 8.13
2018-08-22 09:00 | 6.74 | 6.73
2018-08-22 09:30 | 5.64 | 5.63
2018-08-22 10:00 | 4.54 | 4.53
2018-08-22 10:30 | 3.93 | 3.91
2018-08-22 11:00 | 3.49 | 3.47
2018-08-22 11:30 | 3.27 | 3.24
2018-08-22 12:00 | 3.08 | 3.06
2018-08-22 12:30 | 2.69 | 2.65
2018-08-22 13:00 | 2.95 | 2.92
2018-08-22 13:30 | 3.04 | 3.01
2018-08-22 14:00 | 3.3 | 3.28
2018-08-22 14:30 | 3.61 | 3.58
2018-08-22 15:00 | 3.98 | 3.95
2018-08-22 15:30 | 4.78 | 4.76
2018-08-22 16:00 | 6.06 | 6.04
2018-08-22 16:30 | 7.39 | 7.38
2018-08-22 17:00 | 8.66 | 8.65
2018-08-22 17:30 | 9.96 | 9.95
2018-08-22 18:00 | 11.47 | 11.47
2018-08-22 18:30 | 12.78 | 12.78
2018-08-22 19:00 | 13.46 | 13.46
2018-08-22 19:30 | 13.51 | 13.51
2018-08-22 20:00 | 13.74 | 13.74
2018-08-22 20:30 | 13.91 | 13.9
2018-08-22 21:00 | 13.46 | 13.45
2018-08-22 21:30 | 12.44 | 12.43
2018-08-22 22:00 | 11.59 | 11.59
2018-08-22 22:30 | 10.65 | 10.65
2018-08-22 23:00 | 9.85 | 9.84
2018-08-22 23:30 | 8.76 | 8.75
2018-08-23 | 7.71 | 7.7
2018-08-23 00:30 | 6.86 | 6.83
2018-08-23 01:00 | 6.47 | 6.44
2018-08-23 01:30 | 6.16 | 6.13
2018-08-23 02:00 | 5.89 | 5.85
2018-08-23 02:30 | 5.74 | 5.7
2018-08-23 03:00 | 5.69 | 5.65
2018-08-23 03:30 | 5.71 | 5.67
2018-08-23 04:00 | 5.87 | 5.84
2018-08-23 04:30 | 6.22 | 6.19
2018-08-23 05:00 | 6.89 | 6.87
2018-08-23 05:30 | 7.87 | 7.85
2018-08-23 06:00 | 8.92 | 8.91
2018-08-23 06:30 | 10.51 | 10.51
2018-08-23 07:00 | 11.37 | 11.36
2018-08-23 07:30 | 11.67 | 11.66
2018-08-23 08:00 | 10.64 | 10.64
2018-08-23 08:30 | 8.75 | 8.75
2018-08-23 09:00 | 7.07 | 7.06
2018-08-23 09:30 | 5.85 | 5.84
2018-08-23 10:00 | 5.12 | 5.11
2018-08-23 10:30 | 4.15 | 4.13
2018-08-23 11:00 | 3.66 | 3.65
2018-08-23 11:30 | 3.31 | 3.28
2018-08-23 12:00 | 3.27 | 3.25
2018-08-23 12:30 | 3.28 | 3.26
2018-08-23 13:00 | 3.3 | 3.29
2018-08-23 13:30 | 3.92 | 3.91
2018-08-23 14:00 | 4.26 | 4.25
2018-08-23 14:30 | 4.32 | 4.3
2018-08-23 15:00 | 5.77 | 5.75
2018-08-23 15:30 | 5.98 | 5.96
2018-08-23 16:00 | 6.22 | 6.21
2018-08-23 16:30 | 7.44 | 7.43
2018-08-23 17:00 | 8.88 | 8.88
2018-08-23 17:30 | 10.15 | 10.15
2018-08-23 18:00 | 11.52 | 11.51
2018-08-23 18:30 | 12.62 | 12.62
2018-08-23 19:00 | 12.79 | 12.79
2018-08-23 19:30 | 12.79 | 12.78
2018-08-23 20:00 | 12.85 | 12.85
2018-08-23 20:30 | 13.09 | 13.09
2018-08-23 21:00 | 12.45 | 12.45
2018-08-23 21:30 | 11.46 | 11.46
2018-08-23 22:00 | 10.68 | 10.68
2018-08-23 22:30 | 9.94 | 9.93
2018-08-23 23:00 | 9.27 | 9.27
2018-08-23 23:30 | 8.21 | 8.2
2018-08-24 | 7.26 | 7.24
2018-08-24 00:30 | 6.51 | 6.49
2018-08-24 01:00 | 6.12 | 6.09
2018-08-24 01:30 | 5.72 | 5.69
2018-08-24 02:00 | 5.35 | 5.31
2018-08-24 02:30 | 5.16 | 5.12
2018-08-24 03:00 | 5 | 4.96
2018-08-24 03:30 | 5.09 | 5.04
2018-08-24 04:00 | 5.28 | 5.23
2018-08-24 04:30 | 5.55 | 5.52
2018-08-24 05:00 | 5.91 | 5.89
2018-08-24 05:30 | 6.68 | 6.66
2018-08-24 06:00 | 7.62 | 7.61
2018-08-24 06:30 | 8.59 | 8.58
2018-08-24 07:00 | 9.22 | 9.21
2018-08-24 07:30 | 9.29 | 9.28
2018-08-24 08:00 | 8.15 | 8.14
2018-08-24 08:30 | 6.8 | 6.78
2018-08-24 09:00 | 5.58 | 5.55
2018-08-24 09:30 | 4.76 | 4.74
2018-08-24 10:00 | 3.84 | 3.81
2018-08-24 10:30 | 3.37 | 3.33
2018-08-24 11:00 | 3.95 | 3.91
2018-08-24 11:30 | 2.83 | 2.79
2018-08-24 12:00 | 2.88 | 2.83
2018-08-24 12:30 | 2.85 | 2.82
2018-08-24 13:00 | 3.91 | 3.88
2018-08-24 13:30 | 3.02 | 3
2018-08-24 14:00 | 3.57 | 3.55
2018-08-24 14:30 | 3.29 | 3.27
2018-08-24 15:00 | 3.81 | 3.78
2018-08-24 15:30 | 4.65 | 4.62
2018-08-24 16:00 | 5.65 | 5.63
2018-08-24 16:30 | 6.71 | 6.69
2018-08-24 17:00 | 8.28 | 8.27
2018-08-24 17:30 | 9.48 | 9.47
2018-08-24 18:00 | 10.47 | 10.47
2018-08-24 18:30 | 11.4 | 11.4
2018-08-24 19:00 | 11.58 | 11.58
2018-08-24 19:30 | 11.51 | 11.5
2018-08-24 20:00 | 11.6 | 11.6
2018-08-24 20:30 | 11.62 | 11.61
2018-08-24 21:00 | 11.09 | 11.08
2018-08-24 21:30 | 10.56 | 10.55
2018-08-24 22:00 | 9.99 | 9.98
2018-08-24 22:30 | 9.54 | 9.53
2018-08-24 23:00 | 9.3 | 9.28
2018-08-24 23:30 | 8.41 | 8.39
2018-08-25 | 7.5 | 7.48
2018-08-25 00:30 | 6.63 | 6.6
2018-08-25 01:00 | 6.13 | 6.09
2018-08-25 01:30 | 5.65 | 5.61
2018-08-25 02:00 | 5.29 | 5.24
2018-08-25 02:30 | 5.05 | 5
2018-08-25 03:00 | 4.95 | 4.89
2018-08-25 03:30 | 4.94 | 4.88
2018-08-25 04:00 | 4.92 | 4.86
2018-08-25 04:30 | 4.99 | 4.94
2018-08-25 05:00 | 5.11 | 5.06
2018-08-25 05:30 | 5.27 | 5.22
2018-08-25 06:00 | 5.5 | 5.45
2018-08-25 06:30 | 5.91 | 5.84
2018-08-25 07:00 | 6.52 | 6.46
2018-08-25 07:30 | 7.37 | 7.32
2018-08-25 08:00 | 7.42 | 7.38
2018-08-25 08:30 | 6.67 | 6.63
2018-08-25 09:00 | 6.04 | 6.01
2018-08-25 09:30 | 5.73 | 5.71
2018-08-25 10:00 | 5.13 | 5.1
2018-08-25 10:30 | 4.82 | 4.8
2018-08-25 11:00 | 5.26 | 5.24
2018-08-25 11:30 | 5.12 | 5.09
2018-08-25 12:00 | 5.9 | 5.88
2018-08-25 12:30 | 6.79 | 6.77
2018-08-25 13:00 | 6.12 | 6.09
2018-08-25 13:30 | 7.18 | 7.15
2018-08-25 14:00 | 6.47 | 6.44
2018-08-25 14:30 | 6.89 | 6.87
2018-08-25 15:00 | 5.27 | 5.23
2018-08-25 15:30 | 5.46 | 5.42
2018-08-25 16:00 | 6.58 | 6.55
2018-08-25 16:30 | 7.41 | 7.38
2018-08-25 17:00 | 8.65 | 8.63
2018-08-25 17:30 | 9.59 | 9.58
2018-08-25 18:00 | 10.7 | 10.7
2018-08-25 18:30 | 11.14 | 11.13
2018-08-25 19:00 | 11.38 | 11.37
2018-08-25 19:30 | 11.15 | 11.14
2018-08-25 20:00 | 11.38 | 11.37
2018-08-25 20:30 | 11.32 | 11.32
2018-08-25 21:00 | 10.95 | 10.94
2018-08-25 21:30 | 10.36 | 10.36
2018-08-25 22:00 | 9.84 | 9.83
2018-08-25 22:30 | 9.52 | 9.51
2018-08-25 23:00 | 9.19 | 9.18
2018-08-25 23:30 | 8.34 | 8.33
2018-08-26 | 7.52 | 7.5
2018-08-26 00:30 | 6.71 | 6.68
2018-08-26 01:00 | 6.31 | 6.28
2018-08-26 01:30 | 5.7 | 5.67
2018-08-26 02:00 | 5.3 | 5.26
2018-08-26 02:30 | 5.08 | 5.03
2018-08-26 03:00 | 4.96 | 4.92
2018-08-26 03:30 | 4.84 | 4.78
2018-08-26 04:00 | 4.8 | 4.75
2018-08-26 04:30 | 4.8 | 4.75
2018-08-26 05:00 | 4.96 | 4.91
2018-08-26 05:30 | 4.93 | 4.89
2018-08-26 06:00 | 5.03 | 4.99
2018-08-26 06:30 | 5.23 | 5.17
2018-08-26 07:00 | 5.42 | 5.32
2018-08-26 07:30 | 5.76 | 5.68
2018-08-26 08:00 | 6.72 | 6.66
2018-08-26 08:30 | 7.46 | 7.42
2018-08-26 09:00 | 8.47 | 8.44
2018-08-26 09:30 | 8.75 | 8.72
2018-08-26 10:00 | 8.47 | 8.45
2018-08-26 10:30 | 8.47 | 8.45
2018-08-26 11:00 | 9.84 | 9.83
2018-08-26 11:30 | 9.37 | 9.35
2018-08-26 12:00 | 8.81 | 8.79
2018-08-26 12:30 | 9.15 | 9.13
2018-08-26 13:00 | 8.9 | 8.88
2018-08-26 13:30 | 9.14 | 9.13
2018-08-26 14:00 | 7.89 | 7.87
2018-08-26 14:30 | 6.26 | 6.23
2018-08-26 15:00 | 6.64 | 6.61
2018-08-26 15:30 | 7.75 | 7.72
2018-08-26 16:00 | 7.78 | 7.75
2018-08-26 16:30 | 8.31 | 8.29
2018-08-26 17:00 | 9.82 | 9.8
2018-08-26 17:30 | 10.75 | 10.74
2018-08-26 18:00 | 12.09 | 12.09
2018-08-26 18:30 | 13.06 | 13.05
2018-08-26 19:00 | 13.09 | 13.09
2018-08-26 19:30 | 12.85 | 12.84
2018-08-26 20:00 | 12.57 | 12.56
2018-08-26 20:30 | 12.51 | 12.51
2018-08-26 21:00 | 12.11 | 12.1
2018-08-26 21:30 | 11.18 | 11.18
2018-08-26 22:00 | 10.5 | 10.5
2018-08-26 22:30 | 9.79 | 9.79
2018-08-26 23:00 | 9.21 | 9.2
2018-08-26 23:30 | 8.18 | 8.17
2018-08-27 | 7.31 | 7.29
2018-08-27 00:30 | 6.48 | 6.45
2018-08-27 01:00 | 5.98 | 5.95
2018-08-27 01:30 | 5.52 | 5.48
2018-08-27 02:00 | 5.19 | 5.14
2018-08-27 02:30 | 5.11 | 5.06
2018-08-27 03:00 | 5.05 | 5
2018-08-27 03:30 | 5.13 | 5.08
2018-08-27 04:00 | 5.17 | 5.12
2018-08-27 04:30 | 5.39 | 5.35
2018-08-27 05:00 | 5.86 | 5.83
2018-08-27 05:30 | 6.6 | 6.58
2018-08-27 06:00 | 7.33 | 7.31
2018-08-27 06:30 | 8.19 | 8.16
2018-08-27 07:00 | 8.87 | 8.85
2018-08-27 07:30 | 8.9 | 8.89
2018-08-27 08:00 | 8.4 | 8.39
2018-08-27 08:30 | 7.06 | 7.05
2018-08-27 09:00 | 5.95 | 5.94
2018-08-27 09:30 | 5.01 | 4.99
2018-08-27 10:00 | 4.51 | 4.49
2018-08-27 10:30 | 3.91 | 3.89
2018-08-27 11:00 | 3.54 | 3.53
2018-08-27 11:30 | 3.23 | 3.21
2018-08-27 12:00 | 2.95 | 2.93
2018-08-27 12:30 | 2.81 | 2.79
2018-08-27 13:00 | 2.93 | 2.92
2018-08-27 13:30 | 3 | 2.98
2018-08-27 14:00 | 3.38 | 3.36
2018-08-27 14:30 | 3.9 | 3.89
2018-08-27 15:00 | 4.02 | 4
2018-08-27 15:30 | 5.74 | 5.73
2018-08-27 16:00 | 6.52 | 6.5
2018-08-27 16:30 | 7.55 | 7.54
2018-08-27 17:00 | 9.27 | 9.27
2018-08-27 17:30 | 10.51 | 10.51
2018-08-27 18:00 | 11.54 | 11.54
2018-08-27 18:30 | 12.95 | 12.95
2018-08-27 19:00 | 13.18 | 13.17
2018-08-27 19:30 | 12.89 | 12.89
2018-08-27 20:00 | 12.82 | 12.82
2018-08-27 20:30 | 12.79 | 12.79
2018-08-27 21:00 | 12.22 | 12.22
2018-08-27 21:30 | 11.29 | 11.29
2018-08-27 22:00 | 10.53 | 10.53
2018-08-27 22:30 | 9.34 | 9.34
2018-08-27 23:00 | 8.79 | 8.78
2018-08-27 23:30 | 7.7 | 7.68
2018-08-28 | 6.74 | 6.71
2018-08-28 00:30 | 6.04 | 6.01
2018-08-28 01:00 | 5.63 | 5.59
2018-08-28 01:30 | 5.26 | 5.22
2018-08-28 02:00 | 4.96 | 4.92
2018-08-28 02:30 | 4.96 | 4.91
2018-08-28 03:00 | 4.85 | 4.8
2018-08-28 03:30 | 4.83 | 4.78
2018-08-28 04:00 | 4.98 | 4.93
2018-08-28 04:30 | 5.25 | 5.21
2018-08-28 05:00 | 5.72 | 5.69
2018-08-28 05:30 | 6.53 | 6.51
2018-08-28 06:00 | 7.15 | 7.13
2018-08-28 06:30 | 8.39 | 8.37
2018-08-28 07:00 | 9.37 | 9.35
2018-08-28 07:30 | 9.31 | 9.3
2018-08-28 08:00 | 8.34 | 8.32
2018-08-28 08:30 | 6.82 | 6.81
2018-08-28 09:00 | 5.58 | 5.56
2018-08-28 09:30 | 4.8 | 4.79
2018-08-28 10:00 | 4.23 | 4.22
2018-08-28 10:30 | 3.88 | 3.87
2018-08-28 11:00 | 3.56 | 3.54
2018-08-28 11:30 | 3.48 | 3.46
2018-08-28 12:00 | 3.56 | 3.55
2018-08-28 12:30 | 3.13 | 3.11
2018-08-28 13:00 | 3.19 | 3.17
2018-08-28 13:30 | 3.24 | 3.22
2018-08-28 14:00 | 3.33 | 3.32
2018-08-28 14:30 | 3.53 | 3.51
2018-08-28 15:00 | 4.03 | 4.01
2018-08-28 15:30 | 4.86 | 4.84
2018-08-28 16:00 | 6.08 | 6.07
2018-08-28 16:30 | 7.49 | 7.48
2018-08-28 17:00 | 8.35 | 8.34
2018-08-28 17:30 | 9.67 | 9.66
2018-08-28 18:00 | 11.2 | 11.2
2018-08-28 18:30 | 12.69 | 12.69
2018-08-28 19:00 | 13.03 | 13.03
2018-08-28 19:30 | 12.84 | 12.84
2018-08-28 20:00 | 12.87 | 12.87
2018-08-28 20:30 | 12.84 | 12.84
2018-08-28 21:00 | 12.21 | 12.21
2018-08-28 21:30 | 11.23 | 11.23
2018-08-28 22:00 | 10.16 | 10.15
2018-08-28 22:30 | 9.41 | 9.41
2018-08-28 23:00 | 8.94 | 8.93
2018-08-28 23:30 | 7.95 | 7.93
2018-08-29 | 6.96 | 6.94
2018-08-29 00:30 | 6.16 | 6.13
2018-08-29 01:00 | 5.68 | 5.64
2018-08-29 01:30 | 5.34 | 5.3
2018-08-29 02:00 | 5.11 | 5.06
2018-08-29 02:30 | 4.95 | 4.9
2018-08-29 03:00 | 4.85 | 4.8
2018-08-29 03:30 | 4.98 | 4.94
2018-08-29 04:00 | 5.07 | 5.01
2018-08-29 04:30 | 5.32 | 5.27
2018-08-29 05:00 | 5.9 | 5.87
2018-08-29 05:30 | 6.81 | 6.79
2018-08-29 06:00 | 7.66 | 7.65
2018-08-29 06:30 | 8.33 | 8.3
2018-08-29 07:00 | 9.12 | 9.1
2018-08-29 07:30 | 9.35 | 9.34
2018-08-29 08:00 | 8.49 | 8.48
2018-08-29 08:30 | 6.93 | 6.91
2018-08-29 09:00 | 5.54 | 5.52
2018-08-29 09:30 | 4.76 | 4.75
2018-08-29 10:00 | 4.14 | 4.12
2018-08-29 10:30 | 3.54 | 3.52
2018-08-29 11:00 | 3.07 | 3.04
2018-08-29 11:30 | 2.94 | 2.91
2018-08-29 12:00 | 2.73 | 2.7
2018-08-29 12:30 | 2.57 | 2.54
2018-08-29 13:00 | 2.7 | 2.67
2018-08-29 13:30 | 2.54 | 2.51
2018-08-29 14:00 | 2.85 | 2.82
2018-08-29 14:30 | 3.37 | 3.35
2018-08-29 15:00 | 3.75 | 3.73
2018-08-29 15:30 | 4.64 | 4.62
2018-08-29 16:00 | 5.84 | 5.83
2018-08-29 16:30 | 7.1 | 7.09
2018-08-29 17:00 | 8.51 | 8.51
2018-08-29 17:30 | 9.67 | 9.67
2018-08-29 18:00 | 11.04 | 11.04
2018-08-29 18:30 | 12.45 | 12.44
2018-08-29 19:00 | 13.01 | 13
2018-08-29 19:30 | 12.82 | 12.81
2018-08-29 20:00 | 13.07 | 13.07
2018-08-29 20:30 | 13.28 | 13.28
2018-08-29 21:00 | 12.68 | 12.67
2018-08-29 21:30 | 11.51 | 11.5
2018-08-29 22:00 | 10.57 | 10.57
2018-08-29 22:30 | 9.89 | 9.88
2018-08-29 23:00 | 9.36 | 9.35
2018-08-29 23:30 | 8.3 | 8.29
2018-08-30 | 7.4 | 7.38
2018-08-30 00:30 | 6.62 | 6.59
2018-08-30 01:00 | 6.18 | 6.15
2018-08-30 01:30 | 5.89 | 5.86
2018-08-30 02:00 | 5.53 | 5.49
2018-08-30 02:30 | 5.41 | 5.37
2018-08-30 03:00 | 5.28 | 5.23
2018-08-30 03:30 | 5.44 | 5.4
2018-08-30 04:00 | 5.62 | 5.58
2018-08-30 04:30 | 5.92 | 5.89
2018-08-30 05:00 | 6.47 | 6.45
2018-08-30 05:30 | 7.38 | 7.37
2018-08-30 06:00 | 8.39 | 8.38
2018-08-30 06:30 | 9.82 | 9.82
2018-08-30 07:00 | 10.92 | 10.91
2018-08-30 07:30 | 10.75 | 10.75
2018-08-30 08:00 | 9.58 | 9.58
2018-08-30 08:30 | 7.71 | 7.7
2018-08-30 09:00 | 6.14 | 6.13
2018-08-30 09:30 | 5.29 | 5.28
2018-08-30 10:00 | 4.4 | 4.39
2018-08-30 10:30 | 3.61 | 3.59
2018-08-30 11:00 | 3.21 | 3.19
2018-08-30 11:30 | 2.92 | 2.9
2018-08-30 12:00 | 2.78 | 2.76
2018-08-30 12:30 | 2.73 | 2.71
2018-08-30 13:00 | 2.8 | 2.78
2018-08-30 13:30 | 2.97 | 2.95
2018-08-30 14:00 | 3.3 | 3.28
2018-08-30 14:30 | 3.54 | 3.52
2018-08-30 15:00 | 4.03 | 4.02
2018-08-30 15:30 | 4.83 | 4.82
2018-08-30 16:00 | 6.12 | 6.12
2018-08-30 16:30 | 7.26 | 7.25
2018-08-30 17:00 | 8.55 | 8.54
2018-08-30 17:30 | 9.56 | 9.55
2018-08-30 18:00 | 10.97 | 10.97
2018-08-30 18:30 | 12.16 | 12.15
2018-08-30 19:00 | 12.5 | 12.5
2018-08-30 19:30 | 12.29 | 12.28
2018-08-30 20:00 | 12.05 | 12.05
2018-08-30 20:30 | 12.3 | 12.3
2018-08-30 21:00 | 11.54 | 11.54
2018-08-30 21:30 | 10.76 | 10.76
2018-08-30 22:00 | 9.91 | 9.91
2018-08-30 22:30 | 9.27 | 9.26
2018-08-30 23:00 | 8.82 | 8.81
2018-08-30 23:30 | 7.82 | 7.81
2018-08-31 | 6.91 | 6.89
2018-08-31 00:30 | 6.22 | 6.19
2018-08-31 01:00 | 5.85 | 5.81
2018-08-31 01:30 | 5.42 | 5.37
2018-08-31 02:00 | 5.04 | 4.99
2018-08-31 02:30 | 4.84 | 4.79
2018-08-31 03:00 | 4.82 | 4.77
2018-08-31 03:30 | 4.96 | 4.91
2018-08-31 04:00 | 5.04 | 4.99
2018-08-31 04:30 | 5.28 | 5.23
2018-08-31 05:00 | 5.82 | 5.79
2018-08-31 05:30 | 6.52 | 6.5
2018-08-31 06:00 | 7.22 | 7.2
2018-08-31 06:30 | 8.1 | 8.07
2018-08-31 07:00 | 8.79 | 8.77
2018-08-31 07:30 | 8.65 | 8.63
2018-08-31 08:00 | 7.6 | 7.59
2018-08-31 08:30 | 6.11 | 6.08
2018-08-31 09:00 | 4.81 | 4.78
2018-08-31 09:30 | 4.03 | 4
2018-08-31 10:00 | 3.36 | 3.32
2018-08-31 10:30 | 2.94 | 2.89
2018-08-31 11:00 | 2.52 | 2.47
2018-08-31 11:30 | 2.36 | 2.31
2018-08-31 12:00 | 2.2 | 2.15
2018-08-31 12:30 | 2.11 | 2.07
2018-08-31 13:00 | 2.24 | 2.2
2018-08-31 13:30 | 2.64 | 2.61
2018-08-31 14:00 | 3.07 | 3.05
2018-08-31 14:30 | 3.24 | 3.22
2018-08-31 15:00 | 3.74 | 3.72
2018-08-31 15:30 | 4.51 | 4.49
2018-08-31 16:00 | 5.87 | 5.85
2018-08-31 16:30 | 6.74 | 6.72
2018-08-31 17:00 | 7.81 | 7.8
2018-08-31 17:30 | 8.77 | 8.75
2018-08-31 18:00 | 9.81 | 9.8
2018-08-31 18:30 | 10.72 | 10.72
2018-08-31 19:00 | 11.09 | 11.08
2018-08-31 19:30 | 10.9 | 10.89
2018-08-31 20:00 | 10.74 | 10.73
2018-08-31 20:30 | 10.65 | 10.64
2018-08-31 21:00 | 10.18 | 10.17
2018-08-31 21:30 | 9.57 | 9.57
2018-08-31 22:00 | 9.04 | 9.03
2018-08-31 22:30 | 8.44 | 8.43
2018-08-31 23:00 | 8.27 | 8.26
2018-08-31 23:30 | 7.41 | 7.39
2018-09-01 | 6.55 | 6.53
2018-09-01 00:30 | 5.9 | 5.87
2018-09-01 01:00 | 5.53 | 5.49
2018-09-01 01:30 | 5.08 | 5.03
2018-09-01 02:00 | 4.81 | 4.77
2018-09-01 02:30 | 4.56 | 4.5
2018-09-01 03:00 | 4.5 | 4.44
2018-09-01 03:30 | 4.49 | 4.43
2018-09-01 04:00 | 4.37 | 4.31
2018-09-01 04:30 | 4.43 | 4.37
2018-09-01 05:00 | 4.49 | 4.43
2018-09-01 05:30 | 4.7 | 4.65
2018-09-01 06:00 | 4.89 | 4.82
2018-09-01 06:30 | 5.1 | 4.99
2018-09-01 07:00 | 5.29 | 5.19
2018-09-01 07:30 | 5.48 | 5.4
2018-09-01 08:00 | 5.39 | 5.32
2018-09-01 08:30 | 5.94 | 5.89
2018-09-01 09:00 | 5.17 | 5.12
2018-09-01 09:30 | 4.82 | 4.78
2018-09-01 10:00 | 4.42 | 4.39
2018-09-01 10:30 | 4.23 | 4.21
2018-09-01 11:00 | 5.01 | 4.98
2018-09-01 11:30 | 3.45 | 3.42
2018-09-01 12:00 | 3.27 | 3.24
2018-09-01 12:30 | 3.18 | 3.14
2018-09-01 13:00 | 3.21 | 3.17
2018-09-01 13:30 | 3.3 | 3.26
2018-09-01 14:00 | 3.71 | 3.67
2018-09-01 14:30 | 4.05 | 4.02
2018-09-01 15:00 | 4.59 | 4.56
2018-09-01 15:30 | 5.29 | 5.27
2018-09-01 16:00 | 5.94 | 5.92
2018-09-01 16:30 | 6.82 | 6.8
2018-09-01 17:00 | 7.8 | 7.79
2018-09-01 17:30 | 8.59 | 8.57
2018-09-01 18:00 | 9.49 | 9.48
2018-09-01 18:30 | 10.32 | 10.31
2018-09-01 19:00 | 10.48 | 10.47
2018-09-01 19:30 | 10.15 | 10.14
2018-09-01 20:00 | 10.16 | 10.15
2018-09-01 20:30 | 10.07 | 10.06
2018-09-01 21:00 | 9.8 | 9.8
2018-09-01 21:30 | 9.16 | 9.16
2018-09-01 22:00 | 8.57 | 8.56
2018-09-01 22:30 | 8.5 | 8.48
2018-09-01 23:00 | 8.26 | 8.24
2018-09-01 23:30 | 7.52 | 7.5
2018-09-02 | 6.72 | 6.69
2018-09-02 00:30 | 6.1 | 6.07
2018-09-02 01:00 | 5.7 | 5.66
2018-09-02 01:30 | 5.28 | 5.23
2018-09-02 02:00 | 4.92 | 4.86
2018-09-02 02:30 | 4.68 | 4.63
2018-09-02 03:00 | 4.51 | 4.45
2018-09-02 03:30 | 4.42 | 4.35
2018-09-02 04:00 | 4.52 | 4.46
2018-09-02 04:30 | 4.66 | 4.6
2018-09-02 05:00 | 4.75 | 4.7
2018-09-02 05:30 | 4.87 | 4.81
2018-09-02 06:00 | 5.02 | 4.95
2018-09-02 06:30 | 5.34 | 5.23
2018-09-02 07:00 | 5.53 | 5.42
2018-09-02 07:30 | 5.67 | 5.59
2018-09-02 08:00 | 5.63 | 5.56
2018-09-02 08:30 | 5.6 | 5.54
2018-09-02 09:00 | 5.28 | 5.23
2018-09-02 09:30 | 5.12 | 5.08
2018-09-02 10:00 | 4.57 | 4.54
2018-09-02 10:30 | 4.01 | 3.98
2018-09-02 11:00 | 3.85 | 3.82
2018-09-02 11:30 | 3.55 | 3.52
2018-09-02 12:00 | 3.39 | 3.36
2018-09-02 12:30 | 3.26 | 3.22
2018-09-02 13:00 | 3.25 | 3.22
2018-09-02 13:30 | 3.19 | 3.16
2018-09-02 14:00 | 3.5 | 3.46
2018-09-02 14:30 | 3.92 | 3.89
2018-09-02 15:00 | 4.51 | 4.49
2018-09-02 15:30 | 5.17 | 5.15
2018-09-02 16:00 | 6.15 | 6.13
2018-09-02 16:30 | 7.6 | 7.59
2018-09-02 17:00 | 8.74 | 8.73
2018-09-02 17:30 | 9.33 | 9.32
2018-09-02 18:00 | 10.15 | 10.14
2018-09-02 18:30 | 10.94 | 10.93
2018-09-02 19:00 | 11.1 | 11.1
2018-09-02 19:30 | 10.87 | 10.87
2018-09-02 20:00 | 10.71 | 10.7
2018-09-02 20:30 | 10.65 | 10.65
2018-09-02 21:00 | 10.24 | 10.23
2018-09-02 21:30 | 9.64 | 9.64
2018-09-02 22:00 | 9.04 | 9.03
2018-09-02 22:30 | 8.49 | 8.48
2018-09-02 23:00 | 8.14 | 8.12
2018-09-02 23:30 | 7.29 | 7.27
2018-09-03 | 6.42 | 6.39
2018-09-03 00:30 | 5.65 | 5.61
2018-09-03 01:00 | 5.33 | 5.28
2018-09-03 01:30 | 5.02 | 4.97
2018-09-03 02:00 | 4.71 | 4.65
2018-09-03 02:30 | 4.65 | 4.59
2018-09-03 03:00 | 4.44 | 4.37
2018-09-03 03:30 | 4.47 | 4.4
2018-09-03 04:00 | 4.61 | 4.54
2018-09-03 04:30 | 4.81 | 4.75
2018-09-03 05:00 | 5.31 | 5.26
2018-09-03 05:30 | 6.01 | 5.98
2018-09-03 06:00 | 6.88 | 6.86
2018-09-03 06:30 | 7.53 | 7.5
2018-09-03 07:00 | 8.17 | 8.15
2018-09-03 07:30 | 8.1 | 8.09
2018-09-03 08:00 | 7.21 | 7.19
2018-09-03 08:30 | 5.68 | 5.66
2018-09-03 09:00 | 5.37 | 5.35
2018-09-03 09:30 | 5.34 | 5.32
2018-09-03 10:00 | 5.47 | 5.44
2018-09-03 10:30 | 5.66 | 5.65
2018-09-03 11:00 | 6.09 | 6.08
2018-09-03 11:30 | 6.03 | 6
2018-09-03 12:00 | 7.19 | 7.17
2018-09-03 12:30 | 7 | 6.99
2018-09-03 13:00 | 6.59 | 6.58
2018-09-03 13:30 | 6.43 | 6.41
2018-09-03 14:00 | 5.86 | 5.84
2018-09-03 14:30 | 6.82 | 6.8
2018-09-03 15:00 | 6.58 | 6.56
2018-09-03 15:30 | 8.35 | 8.34
2018-09-03 16:00 | 8.63 | 8.62
2018-09-03 16:30 | 9.27 | 9.26
2018-09-03 17:00 | 10.33 | 10.32
2018-09-03 17:30 | 11.29 | 11.28
2018-09-03 18:00 | 12.33 | 12.32
2018-09-03 18:30 | 13.3 | 13.29
2018-09-03 19:00 | 13.94 | 13.94
2018-09-03 19:30 | 13.7 | 13.7
2018-09-03 20:00 | 13.43 | 13.43
2018-09-03 20:30 | 13.34 | 13.34
2018-09-03 21:00 | 12.82 | 12.81
2018-09-03 21:30 | 11.57 | 11.57
2018-09-03 22:00 | 10.94 | 10.94
2018-09-03 22:30 | 9.55 | 9.55
2018-09-03 23:00 | 8.84 | 8.82
2018-09-03 23:30 | 7.81 | 7.79
2018-09-04 | 6.85 | 6.82
2018-09-04 00:30 | 6.03 | 6
2018-09-04 01:00 | 5.72 | 5.68
2018-09-04 01:30 | 5.36 | 5.31
2018-09-04 02:00 | 4.98 | 4.93
2018-09-04 02:30 | 4.96 | 4.9
2018-09-04 03:00 | 4.87 | 4.81
2018-09-04 03:30 | 4.86 | 4.8
2018-09-04 04:00 | 4.97 | 4.9
2018-09-04 04:30 | 5.16 | 5.11
2018-09-04 05:00 | 5.69 | 5.65
2018-09-04 05:30 | 6.42 | 6.4
2018-09-04 06:00 | 6.95 | 6.93
2018-09-04 06:30 | 7.84 | 7.81
2018-09-04 07:00 | 8.9 | 8.88
2018-09-04 07:30 | 8.2 | 8.18
2018-09-04 08:00 | 7.4 | 7.38
2018-09-04 08:30 | 7.18 | 7.16
2018-09-04 09:00 | 6.32 | 6.3
2018-09-04 09:30 | 6.13 | 6.11
2018-09-04 10:00 | 4.05 | 4.02
2018-09-04 10:30 | 3.14 | 3.11
2018-09-04 11:00 | 3.29 | 3.26
2018-09-04 11:30 | 3.49 | 3.46
2018-09-04 12:00 | 3.93 | 3.91
2018-09-04 12:30 | 4.84 | 4.82
2018-09-04 13:00 | 4.33 | 4.32
2018-09-04 13:30 | 4.62 | 4.6
2018-09-04 14:00 | 5.13 | 5.11
2018-09-04 14:30 | 3.95 | 3.93
2018-09-04 15:00 | 3.91 | 3.89
2018-09-04 15:30 | 4.89 | 4.87
2018-09-04 16:00 | 6.34 | 6.32
2018-09-04 16:30 | 7.05 | 7.03
2018-09-04 17:00 | 8.81 | 8.8
2018-09-04 17:30 | 10.1 | 10.09
2018-09-04 18:00 | 11.4 | 11.39
2018-09-04 18:30 | 12.43 | 12.43
2018-09-04 19:00 | 12.73 | 12.73
2018-09-04 19:30 | 12.54 | 12.53
2018-09-04 20:00 | 12.45 | 12.44
2018-09-04 20:30 | 12.45 | 12.44
2018-09-04 21:00 | 11.87 | 11.87
2018-09-04 21:30 | 10.78 | 10.78
2018-09-04 22:00 | 9.89 | 9.88
2018-09-04 22:30 | 9.06 | 9.06
2018-09-04 23:00 | 8.57 | 8.55
2018-09-04 23:30 | 7.58 | 7.56
2018-09-05 | 6.57 | 6.54
2018-09-05 00:30 | 5.89 | 5.86
2018-09-05 01:00 | 5.52 | 5.47
2018-09-05 01:30 | 5.17 | 5.12
2018-09-05 02:00 | 4.78 | 4.72
2018-09-05 02:30 | 4.63 | 4.57
2018-09-05 03:00 | 4.6 | 4.54
2018-09-05 03:30 | 4.6 | 4.54
2018-09-05 04:00 | 4.74 | 4.68
2018-09-05 04:30 | 4.97 | 4.92
2018-09-05 05:00 | 5.46 | 5.42
2018-09-05 05:30 | 6.21 | 6.18
2018-09-05 06:00 | 7.3 | 7.29
2018-09-05 06:30 | 8.07 | 8.04
2018-09-05 07:00 | 8.77 | 8.75
2018-09-05 07:30 | 8.59 | 8.57
2018-09-05 08:00 | 7.56 | 7.55
2018-09-05 08:30 | 6.16 | 6.13
2018-09-05 09:00 | 4.86 | 4.82
2018-09-05 09:30 | 4.42 | 4.39
2018-09-05 10:00 | 3.68 | 3.66
2018-09-05 10:30 | 5.2 | 5.17
2018-09-05 11:00 | 6.88 | 6.85
2018-09-05 11:30 | 5.58 | 5.56
2018-09-05 12:00 | 5.75 | 5.73
2018-09-05 12:30 | 5.18 | 5.16
2018-09-05 13:00 | 3.52 | 3.49
2018-09-05 13:30 | 3.75 | 3.73
2018-09-05 14:00 | 5.51 | 5.49
2018-09-05 14:30 | 6.17 | 6.15
2018-09-05 15:00 | 6.37 | 6.34
2018-09-05 15:30 | 6.42 | 6.4
2018-09-05 16:00 | 6.24 | 6.22
2018-09-05 16:30 | 7.67 | 7.66
2018-09-05 17:00 | 8.95 | 8.94
2018-09-05 17:30 | 10.17 | 10.16
2018-09-05 18:00 | 11.23 | 11.22
2018-09-05 18:30 | 12.47 | 12.46
2018-09-05 19:00 | 13.35 | 13.35
2018-09-05 19:30 | 12.85 | 12.85
2018-09-05 20:00 | 12.75 | 12.75
2018-09-05 20:30 | 12.8 | 12.79
2018-09-05 21:00 | 12.47 | 12.47
2018-09-05 21:30 | 11.68 | 11.68
2018-09-05 22:00 | 10.65 | 10.65
2018-09-05 22:30 | 9.45 | 9.44
2018-09-05 23:00 | 8.89 | 8.88
2018-09-05 23:30 | 7.88 | 7.86
2018-09-06 | 6.89 | 6.86
2018-09-06 00:30 | 6.16 | 6.13
2018-09-06 01:00 | 5.72 | 5.69
2018-09-06 01:30 | 5.24 | 5.19
2018-09-06 02:00 | 5.06 | 5.01
2018-09-06 02:30 | 4.79 | 4.74
2018-09-06 03:00 | 4.77 | 4.71
2018-09-06 03:30 | 4.85 | 4.79
2018-09-06 04:00 | 4.93 | 4.87
2018-09-06 04:30 | 5.19 | 5.14
2018-09-06 05:00 | 5.64 | 5.6
2018-09-06 05:30 | 6.25 | 6.22
2018-09-06 06:00 | 6.85 | 6.82
2018-09-06 06:30 | 7.75 | 7.71
2018-09-06 07:00 | 8.83 | 8.81
2018-09-06 07:30 | 8.88 | 8.86
2018-09-06 08:00 | 8.02 | 8
2018-09-06 08:30 | 6.22 | 6.2
2018-09-06 09:00 | 5.25 | 5.23
2018-09-06 09:30 | 5.17 | 5.14
2018-09-06 10:00 | 5.24 | 5.22
2018-09-06 10:30 | 5.68 | 5.66
2018-09-06 11:00 | 6.54 | 6.53
2018-09-06 11:30 | 6.13 | 6.12
2018-09-06 12:00 | 4.26 | 4.24
2018-09-06 12:30 | 2.65 | 2.62
2018-09-06 13:00 | 3.38 | 3.36
2018-09-06 13:30 | 3.32 | 3.3
2018-09-06 14:00 | 2.72 | 2.7
2018-09-06 14:30 | 3.11 | 3.09
2018-09-06 15:00 | 3.56 | 3.55
2018-09-06 15:30 | 4.81 | 4.8
2018-09-06 16:00 | 6.07 | 6.06
2018-09-06 16:30 | 7.2 | 7.19
2018-09-06 17:00 | 8.57 | 8.57
2018-09-06 17:30 | 9.6 | 9.6
2018-09-06 18:00 | 10.78 | 10.78
2018-09-06 18:30 | 12.04 | 12.03
2018-09-06 19:00 | 12.45 | 12.45
2018-09-06 19:30 | 11.79 | 11.78
2018-09-06 20:00 | 11.78 | 11.78
2018-09-06 20:30 | 12.05 | 12.05
2018-09-06 21:00 | 11.56 | 11.56
2018-09-06 21:30 | 10.68 | 10.67
2018-09-06 22:00 | 9.83 | 9.82
2018-09-06 22:30 | 9.03 | 9.02
2018-09-06 23:00 | 8.51 | 8.5
2018-09-06 23:30 | 7.52 | 7.49
2018-09-07 | 6.53 | 6.5
2018-09-07 00:30 | 5.82 | 5.78
2018-09-07 01:00 | 5.44 | 5.4
2018-09-07 01:30 | 5.07 | 5.02
2018-09-07 02:00 | 4.74 | 4.68
2018-09-07 02:30 | 4.59 | 4.54
2018-09-07 03:00 | 4.51 | 4.45
2018-09-07 03:30 | 4.57 | 4.51
2018-09-07 04:00 | 4.55 | 4.48
2018-09-07 04:30 | 4.79 | 4.74
2018-09-07 05:00 | 5.23 | 5.19
2018-09-07 05:30 | 5.8 | 5.77
2018-09-07 06:00 | 6.3 | 6.27
2018-09-07 06:30 | 7.02 | 6.97
2018-09-07 07:00 | 7.16 | 7.11
2018-09-07 07:30 | 7.86 | 7.83
2018-09-07 08:00 | 7.75 | 7.72
2018-09-07 08:30 | 6.07 | 6.03
2018-09-07 09:00 | 4.62 | 4.57
2018-09-07 09:30 | 3.91 | 3.88
2018-09-07 10:00 | 4.46 | 4.43
2018-09-07 10:30 | 4.57 | 4.54
2018-09-07 11:00 | 3.2 | 3.18
2018-09-07 11:30 | 4.63 | 4.61
2018-09-07 12:00 | 5.11 | 5.09
2018-09-07 12:30 | 4.65 | 4.63
2018-09-07 13:00 | 3.6 | 3.57
2018-09-07 13:30 | 4.29 | 4.27
2018-09-07 14:00 | 3.81 | 3.79
2018-09-07 14:30 | 4.12 | 4.1
2018-09-07 15:00 | 4.05 | 4.03
2018-09-07 15:30 | 5.14 | 5.12
2018-09-07 16:00 | 5.84 | 5.83
2018-09-07 16:30 | 6.7 | 6.69
2018-09-07 17:00 | 8.12 | 8.11
2018-09-07 17:30 | 8.91 | 8.9
2018-09-07 18:00 | 9.76 | 9.75
2018-09-07 18:30 | 10.62 | 10.61
2018-09-07 19:00 | 11.07 | 11.07
2018-09-07 19:30 | 10.68 | 10.67
2018-09-07 20:00 | 10.5 | 10.49
2018-09-07 20:30 | 10.51 | 10.5
2018-09-07 21:00 | 10.2 | 10.19
2018-09-07 21:30 | 9.49 | 9.48
2018-09-07 22:00 | 8.8 | 8.8
2018-09-07 22:30 | 8.45 | 8.43
2018-09-07 23:00 | 8.33 | 8.32
2018-09-07 23:30 | 7.51 | 7.49
2018-09-08 | 6.64 | 6.62
2018-09-08 00:30 | 5.86 | 5.83
2018-09-08 01:00 | 5.52 | 5.48
2018-09-08 01:30 | 4.98 | 4.94
2018-09-08 02:00 | 4.74 | 4.7
2018-09-08 02:30 | 4.56 | 4.51
2018-09-08 03:00 | 4.4 | 4.35
2018-09-08 03:30 | 4.42 | 4.37
2018-09-08 04:00 | 4.35 | 4.29
2018-09-08 04:30 | 4.36 | 4.31
2018-09-08 05:00 | 4.48 | 4.43
2018-09-08 05:30 | 4.61 | 4.56
2018-09-08 06:00 | 4.73 | 4.66
2018-09-08 06:30 | 5 | 4.91
2018-09-08 07:00 | 5.5 | 5.42
2018-09-08 07:30 | 6.16 | 6.09
2018-09-08 08:00 | 6.97 | 6.92
2018-09-08 08:30 | 7.44 | 7.39
2018-09-08 09:00 | 7.91 | 7.88
2018-09-08 09:30 | 7.27 | 7.24
2018-09-08 10:00 | 7.3 | 7.27
2018-09-08 10:30 | 7.35 | 7.33
2018-09-08 11:00 | 6.78 | 6.76
2018-09-08 11:30 | 4.6 | 4.58
2018-09-08 12:00 | 5.35 | 5.33
2018-09-08 12:30 | 5.12 | 5.09
2018-09-08 13:00 | 6.81 | 6.79
2018-09-08 13:30 | 7.66 | 7.64
2018-09-08 14:00 | 7.92 | 7.91
2018-09-08 14:30 | 7.92 | 7.91
2018-09-08 15:00 | 6.33 | 6.32
2018-09-08 15:30 | 7.43 | 7.42
2018-09-08 16:00 | 7.7 | 7.68
2018-09-08 16:30 | 7.3 | 7.28
2018-09-08 17:00 | 8.46 | 8.45
2018-09-08 17:30 | 9.03 | 9.01
2018-09-08 18:00 | 9.87 | 9.85
2018-09-08 18:30 | 10.52 | 10.51
2018-09-08 19:00 | 10.77 | 10.76
2018-09-08 19:30 | 10.29 | 10.28
2018-09-08 20:00 | 10.28 | 10.27
2018-09-08 20:30 | 10.39 | 10.38
2018-09-08 21:00 | 9.99 | 9.98
2018-09-08 21:30 | 9.21 | 9.2
2018-09-08 22:00 | 8.84 | 8.83
2018-09-08 22:30 | 8.52 | 8.5
2018-09-08 23:00 | 8.31 | 8.3
2018-09-08 23:30 | 7.59 | 7.57
2018-09-09 | 6.64 | 6.61
2018-09-09 00:30 | 5.97 | 5.94
2018-09-09 01:00 | 5.62 | 5.58
2018-09-09 01:30 | 5.2 | 5.16
2018-09-09 02:00 | 4.74 | 4.69
2018-09-09 02:30 | 4.61 | 4.56
2018-09-09 03:00 | 4.53 | 4.48
2018-09-09 03:30 | 4.39 | 4.33
2018-09-09 04:00 | 4.28 | 4.22
2018-09-09 04:30 | 4.39 | 4.33
2018-09-09 05:00 | 4.46 | 4.41
2018-09-09 05:30 | 4.5 | 4.45
2018-09-09 06:00 | 4.59 | 4.51
2018-09-09 06:30 | 4.82 | 4.7
2018-09-09 07:00 | 5.02 | 4.9
2018-09-09 07:30 | 5.19 | 5.1
2018-09-09 08:00 | 5 | 4.92
2018-09-09 08:30 | 4.93 | 4.86
2018-09-09 09:00 | 4.74 | 4.69
2018-09-09 09:30 | 4.66 | 4.63
2018-09-09 10:00 | 4.32 | 4.29
2018-09-09 10:30 | 3.9 | 3.87
2018-09-09 11:00 | 3.84 | 3.81
2018-09-09 11:30 | 3.74 | 3.71
2018-09-09 12:00 | 3.61 | 3.57
2018-09-09 12:30 | 3.57 | 3.54
2018-09-09 13:00 | 3.56 | 3.53
2018-09-09 13:30 | 3.72 | 3.69
2018-09-09 14:00 | 3.87 | 3.84
2018-09-09 14:30 | 4.18 | 4.15
2018-09-09 15:00 | 4.69 | 4.67
2018-09-09 15:30 | 5.37 | 5.35
2018-09-09 16:00 | 6.12 | 6.1
2018-09-09 16:30 | 7.22 | 7.2
2018-09-09 17:00 | 8.45 | 8.44
2018-09-09 17:30 | 9.37 | 9.36
2018-09-09 18:00 | 10.31 | 10.3
2018-09-09 18:30 | 11.22 | 11.22
2018-09-09 19:00 | 11.52 | 11.51
2018-09-09 19:30 | 11.19 | 11.18
2018-09-09 20:00 | 10.94 | 10.94
2018-09-09 20:30 | 10.69 | 10.69
2018-09-09 21:00 | 10.25 | 10.25
2018-09-09 21:30 | 9.5 | 9.5
2018-09-09 22:00 | 8.77 | 8.76
2018-09-09 22:30 | 8.21 | 8.19
2018-09-09 23:00 | 7.86 | 7.84
2018-09-09 23:30 | 7.09 | 7.06
2018-09-10 | 6.26 | 6.22
2018-09-10 00:30 | 5.56 | 5.51
2018-09-10 01:00 | 5.19 | 5.14
2018-09-10 01:30 | 4.78 | 4.72
2018-09-10 02:00 | 4.49 | 4.42
2018-09-10 02:30 | 4.44 | 4.37
2018-09-10 03:00 | 4.32 | 4.24
2018-09-10 03:30 | 4.36 | 4.29
2018-09-10 04:00 | 4.48 | 4.41
2018-09-10 04:30 | 4.61 | 4.54
2018-09-10 05:00 | 5.05 | 5
2018-09-10 05:30 | 5.66 | 5.62
2018-09-10 06:00 | 6.29 | 6.25
2018-09-10 06:30 | 7.29 | 7.26
2018-09-10 07:00 | 7.77 | 7.75
2018-09-10 07:30 | 7.62 | 7.6
2018-09-10 08:00 | 6.79 | 6.77
2018-09-10 08:30 | 5.53 | 5.5
2018-09-10 09:00 | 3.95 | 3.9
2018-09-10 09:30 | 3.48 | 3.44
2018-09-10 10:00 | 3.31 | 3.28
2018-09-10 10:30 | 3.04 | 3.02
2018-09-10 11:00 | 2.75 | 2.74
2018-09-10 11:30 | 2.48 | 2.44
2018-09-10 12:00 | 2.46 | 2.44
2018-09-10 12:30 | 2.65 | 2.64
2018-09-10 13:00 | 2.82 | 2.81
2018-09-10 13:30 | 2.99 | 2.98
2018-09-10 14:00 | 3.15 | 3.14
2018-09-10 14:30 | 3.51 | 3.5
2018-09-10 15:00 | 4.03 | 4.02
2018-09-10 15:30 | 4.87 | 4.87
2018-09-10 16:00 | 6.12 | 6.11
2018-09-10 16:30 | 7.35 | 7.34
2018-09-10 17:00 | 8.62 | 8.61
2018-09-10 17:30 | 9.87 | 9.86
2018-09-10 18:00 | 11.13 | 11.13
2018-09-10 18:30 | 12.1 | 12.1
2018-09-10 19:00 | 12.48 | 12.48
2018-09-10 19:30 | 12.1 | 12.1
2018-09-10 20:00 | 11.84 | 11.84
2018-09-10 20:30 | 11.71 | 11.7
2018-09-10 21:00 | 11.37 | 11.36
2018-09-10 21:30 | 10.38 | 10.37
2018-09-10 22:00 | 9.66 | 9.65
2018-09-10 22:30 | 8.73 | 8.72
2018-09-10 23:00 | 8.16 | 8.14
2018-09-10 23:30 | 7.17 | 7.14
2018-09-11 | 6.3 | 6.26
2018-09-11 00:30 | 5.54 | 5.5
2018-09-11 01:00 | 5.23 | 5.17
2018-09-11 01:30 | 4.91 | 4.85
2018-09-11 02:00 | 4.5 | 4.43
2018-09-11 02:30 | 4.47 | 4.4
2018-09-11 03:00 | 4.4 | 4.33
2018-09-11 03:30 | 4.45 | 4.38
2018-09-11 04:00 | 4.65 | 4.58
2018-09-11 04:30 | 4.91 | 4.85
2018-09-11 05:00 | 5.35 | 5.31
2018-09-11 05:30 | 5.99 | 5.96
2018-09-11 06:00 | 6.81 | 6.78
2018-09-11 06:30 | 7.82 | 7.79
2018-09-11 07:00 | 8.09 | 8.06
2018-09-11 07:30 | 8.04 | 8.02
2018-09-11 08:00 | 7.12 | 7.1
2018-09-11 08:30 | 5.78 | 5.75
2018-09-11 09:00 | 4.92 | 4.89
2018-09-11 09:30 | 4.18 | 4.15
2018-09-11 10:00 | 3.58 | 3.56
2018-09-11 10:30 | 3.23 | 3.21
2018-09-11 11:00 | 3 | 2.98
2018-09-11 11:30 | 3.51 | 3.5
2018-09-11 12:00 | 3.6 | 3.59
2018-09-11 12:30 | 3.62 | 3.61
2018-09-11 13:00 | 3.84 | 3.83
2018-09-11 13:30 | 3.74 | 3.73
2018-09-11 14:00 | 4.79 | 4.78
2018-09-11 14:30 | 4.22 | 4.21
2018-09-11 15:00 | 4.81 | 4.79
2018-09-11 15:30 | 5.09 | 5.07
2018-09-11 16:00 | 6.56 | 6.56
2018-09-11 16:30 | 7.47 | 7.46
2018-09-11 17:00 | 8.64 | 8.63
2018-09-11 17:30 | 10 | 10
2018-09-11 18:00 | 11.11 | 11.11
2018-09-11 18:30 | 12.24 | 12.23
2018-09-11 19:00 | 12.45 | 12.44
2018-09-11 19:30 | 12.17 | 12.16
2018-09-11 20:00 | 12.25 | 12.25
2018-09-11 20:30 | 11.97 | 11.97
2018-09-11 21:00 | 11.41 | 11.41
2018-09-11 21:30 | 10.4 | 10.4
2018-09-11 22:00 | 9.36 | 9.36
2018-09-11 22:30 | 8.56 | 8.55
2018-09-11 23:00 | 8.17 | 8.16
2018-09-11 23:30 | 7.24 | 7.22
2018-09-12 | 6.31 | 6.28
2018-09-12 00:30 | 5.47 | 5.43
2018-09-12 01:00 | 5.13 | 5.09
2018-09-12 01:30 | 4.77 | 4.71
2018-09-12 02:00 | 4.53 | 4.47
2018-09-12 02:30 | 4.44 | 4.38
2018-09-12 03:00 | 4.31 | 4.24
2018-09-12 03:30 | 4.35 | 4.28
2018-09-12 04:00 | 4.42 | 4.35
2018-09-12 04:30 | 4.71 | 4.65
2018-09-12 05:00 | 5.03 | 4.98
2018-09-12 05:30 | 5.76 | 5.73
2018-09-12 06:00 | 6.36 | 6.32
2018-09-12 06:30 | 7 | 6.95
2018-09-12 07:00 | 7.18 | 7.13
2018-09-12 07:30 | 7.2 | 7.17
2018-09-12 08:00 | 6.73 | 6.71
2018-09-12 08:30 | 5.51 | 5.48
2018-09-12 09:00 | 4.87 | 4.84
2018-09-12 09:30 | 4.41 | 4.39
2018-09-12 10:00 | 3.71 | 3.69
2018-09-12 10:30 | 4.6 | 4.58
2018-09-12 11:00 | 4.3 | 4.29
2018-09-12 11:30 | 3.46 | 3.45
2018-09-12 12:00 | 3.72 | 3.71
2018-09-12 12:30 | 3.17 | 3.15
2018-09-12 13:00 | 4.32 | 4.3
2018-09-12 13:30 | 3.69 | 3.67
2018-09-12 14:00 | 3.71 | 3.7
2018-09-12 14:30 | 3.68 | 3.67
2018-09-12 15:00 | 4.52 | 4.51
2018-09-12 15:30 | 5.04 | 5.03
2018-09-12 16:00 | 5.93 | 5.92
2018-09-12 16:30 | 7.07 | 7.06
2018-09-12 17:00 | 8.42 | 8.42
2018-09-12 17:30 | 9.56 | 9.55
2018-09-12 18:00 | 10.63 | 10.62
2018-09-12 18:30 | 11.91 | 11.91
2018-09-12 19:00 | 12.29 | 12.29
2018-09-12 19:30 | 11.96 | 11.96
2018-09-12 20:00 | 11.53 | 11.53
2018-09-12 20:30 | 11.35 | 11.34
2018-09-12 21:00 | 11.25 | 11.24
2018-09-12 21:30 | 10.34 | 10.34
2018-09-12 22:00 | 9.46 | 9.46
2018-09-12 22:30 | 8.48 | 8.47
2018-09-12 23:00 | 8.09 | 8.07
2018-09-12 23:30 | 7.13 | 7.1
2018-09-13 | 6.19 | 6.16
2018-09-13 00:30 | 5.48 | 5.44
2018-09-13 01:00 | 5.17 | 5.13
2018-09-13 01:30 | 4.83 | 4.78
2018-09-13 02:00 | 4.51 | 4.45
2018-09-13 02:30 | 4.42 | 4.35
2018-09-13 03:00 | 4.3 | 4.23
2018-09-13 03:30 | 4.35 | 4.28
2018-09-13 04:00 | 4.45 | 4.39
2018-09-13 04:30 | 4.67 | 4.6
2018-09-13 05:00 | 5.09 | 5.03
2018-09-13 05:30 | 5.65 | 5.61
2018-09-13 06:00 | 6.46 | 6.42
2018-09-13 06:30 | 7.41 | 7.38
2018-09-13 07:00 | 7.57 | 7.54
2018-09-13 07:30 | 7.39 | 7.37
2018-09-13 08:00 | 6.52 | 6.49
2018-09-13 08:30 | 5.43 | 5.4
2018-09-13 09:00 | 4.39 | 4.36
2018-09-13 09:30 | 3.59 | 3.57
2018-09-13 10:00 | 3.11 | 3.09
2018-09-13 10:30 | 2.93 | 2.91
2018-09-13 11:00 | 2.75 | 2.74
2018-09-13 11:30 | 2.71 | 2.71
2018-09-13 12:00 | 2.73 | 2.73
2018-09-13 12:30 | 2.7 | 2.69
2018-09-13 13:00 | 2.94 | 2.93
2018-09-13 13:30 | 2.97 | 2.96
2018-09-13 14:00 | 3.47 | 3.46
2018-09-13 14:30 | 3.87 | 3.85
2018-09-13 15:00 | 4.13 | 4.11
2018-09-13 15:30 | 4.97 | 4.95
2018-09-13 16:00 | 6.14 | 6.13
2018-09-13 16:30 | 7.4 | 7.4
2018-09-13 17:00 | 8.47 | 8.47
2018-09-13 17:30 | 9.5 | 9.49
2018-09-13 18:00 | 10.32 | 10.31
2018-09-13 18:30 | 11.42 | 11.42
2018-09-13 19:00 | 11.85 | 11.84
2018-09-13 19:30 | 11.46 | 11.46
2018-09-13 20:00 | 11.22 | 11.22
2018-09-13 20:30 | 11.25 | 11.25
2018-09-13 21:00 | 10.75 | 10.74
2018-09-13 21:30 | 9.9 | 9.9
2018-09-13 22:00 | 8.99 | 8.98
2018-09-13 22:30 | 8.38 | 8.37
2018-09-13 23:00 | 8.01 | 8
2018-09-13 23:30 | 7.13 | 7.11
2018-09-14 | 6.09 | 6.06
2018-09-14 00:30 | 5.35 | 5.32
2018-09-14 01:00 | 5.04 | 5
2018-09-14 01:30 | 4.73 | 4.68
2018-09-14 02:00 | 4.55 | 4.5
2018-09-14 02:30 | 4.36 | 4.3
2018-09-14 03:00 | 4.26 | 4.2
2018-09-14 03:30 | 4.27 | 4.21
2018-09-14 04:00 | 4.27 | 4.21
2018-09-14 04:30 | 4.48 | 4.43
2018-09-14 05:00 | 4.85 | 4.8
2018-09-14 05:30 | 5.39 | 5.35
2018-09-14 06:00 | 5.69 | 5.63
2018-09-14 06:30 | 6.16 | 6.09
2018-09-14 07:00 | 6.38 | 6.32
2018-09-14 07:30 | 6.34 | 6.29
2018-09-14 08:00 | 5.51 | 5.47
2018-09-14 08:30 | 4.52 | 4.47
2018-09-14 09:00 | 3.68 | 3.64
2018-09-14 09:30 | 3.41 | 3.38
2018-09-14 10:00 | 3.62 | 3.6
2018-09-14 10:30 | 2.97 | 2.95
2018-09-14 11:00 | 2.61 | 2.58
2018-09-14 11:30 | 2.85 | 2.82
2018-09-14 12:00 | 2.6 | 2.57
2018-09-14 12:30 | 2.41 | 2.37
2018-09-14 13:00 | 2.5 | 2.45
2018-09-14 13:30 | 2.78 | 2.74
2018-09-14 14:00 | 3.3 | 3.26
2018-09-14 14:30 | 3.86 | 3.83
2018-09-14 15:00 | 4.31 | 4.29
2018-09-14 15:30 | 5.03 | 5.01
2018-09-14 16:00 | 5.98 | 5.97
2018-09-14 16:30 | 7.08 | 7.06
2018-09-14 17:00 | 8 | 7.99
2018-09-14 17:30 | 8.68 | 8.66
2018-09-14 18:00 | 9.44 | 9.43
2018-09-14 18:30 | 10.39 | 10.38
2018-09-14 19:00 | 10.69 | 10.68
2018-09-14 19:30 | 10.54 | 10.53
2018-09-14 20:00 | 10.5 | 10.5
2018-09-14 20:30 | 10.48 | 10.47
2018-09-14 21:00 | 10.06 | 10.06
2018-09-14 21:30 | 9.28 | 9.27
2018-09-14 22:00 | 8.62 | 8.62
2018-09-14 22:30 | 8.26 | 8.24
2018-09-14 23:00 | 8.19 | 8.18
2018-09-14 23:30 | 7.29 | 7.27
2018-09-15 | 6.38 | 6.35
2018-09-15 00:30 | 5.73 | 5.7
2018-09-15 01:00 | 5.24 | 5.2
2018-09-15 01:30 | 5.03 | 4.98
2018-09-15 02:00 | 4.71 | 4.66
2018-09-15 02:30 | 4.45 | 4.39
2018-09-15 03:00 | 4.35 | 4.27
2018-09-15 03:30 | 4.31 | 4.25
2018-09-15 04:00 | 4.26 | 4.19
2018-09-15 04:30 | 4.28 | 4.21
2018-09-15 05:00 | 4.45 | 4.38
2018-09-15 05:30 | 4.66 | 4.59
2018-09-15 06:00 | 4.67 | 4.55
2018-09-15 06:30 | 4.86 | 4.74
2018-09-15 07:00 | 4.9 | 4.78
2018-09-15 07:30 | 4.95 | 4.85
2018-09-15 08:00 | 4.85 | 4.77
2018-09-15 08:30 | 4.74 | 4.68
2018-09-15 09:00 | 4.5 | 4.45
2018-09-15 09:30 | 4.12 | 4.08
2018-09-15 10:00 | 3.86 | 3.83
2018-09-15 10:30 | 3.52 | 3.48
2018-09-15 11:00 | 3.33 | 3.29
2018-09-15 11:30 | 3.14 | 3.09
2018-09-15 12:00 | 3.25 | 3.21
2018-09-15 12:30 | 3.21 | 3.15
2018-09-15 13:00 | 3.27 | 3.22
2018-09-15 13:30 | 3.69 | 3.63
2018-09-15 14:00 | 4.16 | 4.11
2018-09-15 14:30 | 4.6 | 4.56
2018-09-15 15:00 | 5.18 | 5.14
2018-09-15 15:30 | 5.77 | 5.74
2018-09-15 16:00 | 6.57 | 6.55
2018-09-15 16:30 | 7.33 | 7.31
2018-09-15 17:00 | 8.29 | 8.28
2018-09-15 17:30 | 9.09 | 9.08
2018-09-15 18:00 | 9.69 | 9.68
2018-09-15 18:30 | 10.54 | 10.53
2018-09-15 19:00 | 10.73 | 10.72
2018-09-15 19:30 | 10.47 | 10.46
2018-09-15 20:00 | 10.22 | 10.22
2018-09-15 20:30 | 10.18 | 10.18
2018-09-15 21:00 | 9.53 | 9.53
2018-09-15 21:30 | 9.1 | 9.09
2018-09-15 22:00 | 8.54 | 8.53
2018-09-15 22:30 | 8.29 | 8.29
2018-09-15 23:00 | 8.19 | 8.18
2018-09-15 23:30 | 7.4 | 7.38
2018-09-16 | 6.47 | 6.44
2018-09-16 00:30 | 5.67 | 5.64
2018-09-16 01:00 | 5.38 | 5.34
2018-09-16 01:30 | 5.06 | 5.02
2018-09-16 02:00 | 4.66 | 4.61
2018-09-16 02:30 | 4.43 | 4.37
2018-09-16 03:00 | 4.27 | 4.2
2018-09-16 03:30 | 4.21 | 4.14
2018-09-16 04:00 | 4.16 | 4.09
2018-09-16 04:30 | 4.2 | 4.13
2018-09-16 05:00 | 4.24 | 4.18
2018-09-16 05:30 | 4.33 | 4.26
2018-09-16 06:00 | 4.34 | 4.23
2018-09-16 06:30 | 4.48 | 4.33
2018-09-16 07:00 | 4.4 | 4.25
2018-09-16 07:30 | 4.45 | 4.33
2018-09-16 08:00 | 4.45 | 4.35
2018-09-16 08:30 | 4.66 | 4.59
2018-09-16 09:00 | 4.54 | 4.49
2018-09-16 09:30 | 4.43 | 4.4
2018-09-16 10:00 | 5.04 | 5.01
2018-09-16 10:30 | 4.84 | 4.81
2018-09-16 11:00 | 3.59 | 3.55
2018-09-16 11:30 | 3.68 | 3.64
2018-09-16 12:00 | 3.63 | 3.59
2018-09-16 12:30 | 3.97 | 3.93
2018-09-16 13:00 | 4.81 | 4.77
2018-09-16 13:30 | 5.32 | 5.29
2018-09-16 14:00 | 4.73 | 4.69
2018-09-16 14:30 | 4.6 | 4.56
2018-09-16 15:00 | 5.27 | 5.24
2018-09-16 15:30 | 5.93 | 5.91
2018-09-16 16:00 | 6.61 | 6.6
2018-09-16 16:30 | 7.54 | 7.52
2018-09-16 17:00 | 8.6 | 8.58
2018-09-16 17:30 | 9.48 | 9.47
2018-09-16 18:00 | 10.36 | 10.35
2018-09-16 18:30 | 11.26 | 11.26
2018-09-16 19:00 | 11.52 | 11.51
2018-09-16 19:30 | 11.01 | 11.01
2018-09-16 20:00 | 10.64 | 10.64
2018-09-16 20:30 | 10.59 | 10.58
2018-09-16 21:00 | 10.03 | 10.03
2018-09-16 21:30 | 9.3 | 9.29
2018-09-16 22:00 | 8.49 | 8.48
2018-09-16 22:30 | 7.88 | 7.86
2018-09-16 23:00 | 7.66 | 7.63
2018-09-16 23:30 | 6.8 | 6.77
2018-09-17 | 5.96 | 5.92
2018-09-17 00:30 | 5.28 | 5.23
2018-09-17 01:00 | 4.83 | 4.77
2018-09-17 01:30 | 4.53 | 4.46
2018-09-17 02:00 | 4.27 | 4.19
2018-09-17 02:30 | 4.24 | 4.16
2018-09-17 03:00 | 4.24 | 4.16
2018-09-17 03:30 | 4.23 | 4.14
2018-09-17 04:00 | 4.24 | 4.16
2018-09-17 04:30 | 4.47 | 4.39
2018-09-17 05:00 | 4.84 | 4.78
2018-09-17 05:30 | 5.32 | 5.27
2018-09-17 06:00 | 5.84 | 5.77
2018-09-17 06:30 | 6.79 | 6.74
2018-09-17 07:00 | 6.97 | 6.92
2018-09-17 07:30 | 6.79 | 6.76
2018-09-17 08:00 | 6.09 | 6.07
2018-09-17 08:30 | 4.95 | 4.92
2018-09-17 09:00 | 4.04 | 4
2018-09-17 09:30 | 3.41 | 3.38
2018-09-17 10:00 | 2.91 | 2.87
2018-09-17 10:30 | 2.4 | 2.36
2018-09-17 11:00 | 2.58 | 2.56
2018-09-17 11:30 | 3.35 | 3.34
2018-09-17 12:00 | 3.84 | 3.83
2018-09-17 12:30 | 3.09 | 3.08
2018-09-17 13:00 | 4.18 | 4.18
2018-09-17 13:30 | 4.95 | 4.95
2018-09-17 14:00 | 3.63 | 3.62
2018-09-17 14:30 | 5.69 | 5.68
2018-09-17 15:00 | 4.43 | 4.42
2018-09-17 15:30 | 4.8 | 4.79
2018-09-17 16:00 | 6.02 | 6.01
2018-09-17 16:30 | 7.4 | 7.4
2018-09-17 17:00 | 8.73 | 8.72
2018-09-17 17:30 | 9.92 | 9.92
2018-09-17 18:00 | 10.93 | 10.93
2018-09-17 18:30 | 12.03 | 12.03
2018-09-17 19:00 | 12.43 | 12.42
2018-09-17 19:30 | 12.14 | 12.14
2018-09-17 20:00 | 11.89 | 11.89
2018-09-17 20:30 | 11.85 | 11.85
2018-09-17 21:00 | 11.23 | 11.23
2018-09-17 21:30 | 10.34 | 10.34
2018-09-17 22:00 | 9.53 | 9.53
2018-09-17 22:30 | 8.46 | 8.45
2018-09-17 23:00 | 7.95 | 7.93
2018-09-17 23:30 | 7.02 | 6.98
2018-09-18 | 6.1 | 6.06
2018-09-18 00:30 | 5.39 | 5.34
2018-09-18 01:00 | 5.01 | 4.96
2018-09-18 01:30 | 4.69 | 4.63
2018-09-18 02:00 | 4.35 | 4.27
2018-09-18 02:30 | 4.25 | 4.17
2018-09-18 03:00 | 4.25 | 4.17
2018-09-18 03:30 | 4.28 | 4.19
2018-09-18 04:00 | 4.4 | 4.31
2018-09-18 04:30 | 4.61 | 4.53
2018-09-18 05:00 | 5.01 | 4.95
2018-09-18 05:30 | 5.59 | 5.55
2018-09-18 06:00 | 6.39 | 6.34
2018-09-18 06:30 | 7.06 | 7.01
2018-09-18 07:00 | 7.17 | 7.13
2018-09-18 07:30 | 6.9 | 6.86
2018-09-18 08:00 | 6.18 | 6.16
2018-09-18 08:30 | 5.04 | 5.01
2018-09-18 09:00 | 4.74 | 4.71
2018-09-18 09:30 | 4.38 | 4.35
2018-09-18 10:00 | 4.34 | 4.32
2018-09-18 10:30 | 5.15 | 5.13
2018-09-18 11:00 | 3.95 | 3.93
2018-09-18 11:30 | 3.49 | 3.47
2018-09-18 12:00 | 2.99 | 2.97
2018-09-18 12:30 | 3.08 | 3.06
2018-09-18 13:00 | 3.75 | 3.74
2018-09-18 13:30 | 4.19 | 4.18
2018-09-18 14:00 | 4.68 | 4.66
2018-09-18 14:30 | 4.41 | 4.39
2018-09-18 15:00 | 3.97 | 3.96
2018-09-18 15:30 | 4.8 | 4.79
2018-09-18 16:00 | 5.76 | 5.75
2018-09-18 16:30 | 6.73 | 6.72
2018-09-18 17:00 | 7.85 | 7.83
2018-09-18 17:30 | 9.06 | 9.05
2018-09-18 18:00 | 10.12 | 10.12
2018-09-18 18:30 | 11.46 | 11.45
2018-09-18 19:00 | 11.85 | 11.84
2018-09-18 19:30 | 11.6 | 11.6
2018-09-18 20:00 | 11.59 | 11.59
2018-09-18 20:30 | 11.69 | 11.68
2018-09-18 21:00 | 11.11 | 11.11
2018-09-18 21:30 | 10.28 | 10.28
2018-09-18 22:00 | 9.11 | 9.1
2018-09-18 22:30 | 8.32 | 8.3
2018-09-18 23:00 | 7.99 | 7.97
2018-09-18 23:30 | 7 | 6.97
2018-09-19 | 6.1 | 6.06
2018-09-19 00:30 | 5.43 | 5.39
2018-09-19 01:00 | 5.04 | 5
2018-09-19 01:30 | 4.78 | 4.73
2018-09-19 02:00 | 4.52 | 4.45
2018-09-19 02:30 | 4.34 | 4.27
2018-09-19 03:00 | 4.24 | 4.16
2018-09-19 03:30 | 4.26 | 4.18
2018-09-19 04:00 | 4.39 | 4.31
2018-09-19 04:30 | 4.72 | 4.66
2018-09-19 05:00 | 5 | 4.95
2018-09-19 05:30 | 5.65 | 5.61
2018-09-19 06:00 | 6.06 | 5.99
2018-09-19 06:30 | 6.65 | 6.58
2018-09-19 07:00 | 6.86 | 6.81
2018-09-19 07:30 | 6.93 | 6.9
2018-09-19 08:00 | 6.04 | 6.01
2018-09-19 08:30 | 5.14 | 5.11
2018-09-19 09:00 | 4.47 | 4.45
2018-09-19 09:30 | 4.01 | 3.99
2018-09-19 10:00 | 3.57 | 3.56
2018-09-19 10:30 | 3.18 | 3.16
2018-09-19 11:00 | 2.92 | 2.91
2018-09-19 11:30 | 2.75 | 2.74
2018-09-19 12:00 | 2.92 | 2.91
2018-09-19 12:30 | 2.97 | 2.96
2018-09-19 13:00 | 3.11 | 3.11
2018-09-19 13:30 | 3.19 | 3.18
2018-09-19 14:00 | 3.38 | 3.37
2018-09-19 14:30 | 3.82 | 3.82
2018-09-19 15:00 | 4.26 | 4.25
2018-09-19 15:30 | 5.11 | 5.11
2018-09-19 16:00 | 6.17 | 6.16
2018-09-19 16:30 | 7.36 | 7.36
2018-09-19 17:00 | 8.62 | 8.61
2018-09-19 17:30 | 9.58 | 9.57
2018-09-19 18:00 | 10.56 | 10.56
2018-09-19 18:30 | 11.86 | 11.86
2018-09-19 19:00 | 12.35 | 12.35
2018-09-19 19:30 | 11.83 | 11.83
2018-09-19 20:00 | 11.78 | 11.77
2018-09-19 20:30 | 11.68 | 11.68
2018-09-19 21:00 | 11.07 | 11.07
2018-09-19 21:30 | 10.19 | 10.19
2018-09-19 22:00 | 9.43 | 9.43
2018-09-19 22:30 | 8.36 | 8.35
2018-09-19 23:00 | 7.71 | 7.69
2018-09-19 23:30 | 6.8 | 6.78
2018-09-20 | 5.9 | 5.87
2018-09-20 00:30 | 5.21 | 5.16
2018-09-20 01:00 | 4.85 | 4.79
2018-09-20 01:30 | 4.59 | 4.53
2018-09-20 02:00 | 4.37 | 4.31
2018-09-20 02:30 | 4.25 | 4.19
2018-09-20 03:00 | 4.15 | 4.08
2018-09-20 03:30 | 4.23 | 4.16
2018-09-20 04:00 | 4.3 | 4.23
2018-09-20 04:30 | 4.48 | 4.42
2018-09-20 05:00 | 4.88 | 4.83
2018-09-20 05:30 | 5.47 | 5.43
2018-09-20 06:00 | 5.85 | 5.78
2018-09-20 06:30 | 6.54 | 6.49
2018-09-20 07:00 | 6.42 | 6.37
2018-09-20 07:30 | 6.62 | 6.59
2018-09-20 08:00 | 5.95 | 5.93
2018-09-20 08:30 | 4.65 | 4.63
2018-09-20 09:00 | 3.95 | 3.93
2018-09-20 09:30 | 3.52 | 3.51
2018-09-20 10:00 | 4.64 | 4.63
2018-09-20 10:30 | 4.33 | 4.32
2018-09-20 11:00 | 3.86 | 3.85
2018-09-20 11:30 | 2.66 | 2.64
2018-09-20 12:00 | 2.22 | 2.19
2018-09-20 12:30 | 4.01 | 3.99
2018-09-20 13:00 | 4.65 | 4.64
2018-09-20 13:30 | 5.31 | 5.3
2018-09-20 14:00 | 5.41 | 5.4
2018-09-20 14:30 | 5.09 | 5.08
2018-09-20 15:00 | 3.97 | 3.96
2018-09-20 15:30 | 4.68 | 4.66
2018-09-20 16:00 | 6.12 | 6.11
2018-09-20 16:30 | 7.28 | 7.28
2018-09-20 17:00 | 8.44 | 8.43
2018-09-20 17:30 | 9.23 | 9.22
2018-09-20 18:00 | 10.08 | 10.08
2018-09-20 18:30 | 11.34 | 11.33
2018-09-20 19:00 | 11.97 | 11.97
2018-09-20 19:30 | 11.67 | 11.67
2018-09-20 20:00 | 11.54 | 11.53
2018-09-20 20:30 | 11.46 | 11.46
2018-09-20 21:00 | 10.98 | 10.98
2018-09-20 21:30 | 9.84 | 9.83
2018-09-20 22:00 | 8.84 | 8.83
2018-09-20 22:30 | 8.18 | 8.17
2018-09-20 23:00 | 7.81 | 7.8
2018-09-20 23:30 | 6.89 | 6.87
2018-09-21 | 6.01 | 5.97
2018-09-21 00:30 | 5.36 | 5.32
2018-09-21 01:00 | 5.05 | 5
2018-09-21 01:30 | 4.68 | 4.62
2018-09-21 02:00 | 4.42 | 4.36
2018-09-21 02:30 | 4.17 | 4.11
2018-09-21 03:00 | 4.17 | 4.11
2018-09-21 03:30 | 4.33 | 4.27
2018-09-21 04:00 | 4.36 | 4.3
2018-09-21 04:30 | 4.49 | 4.43
2018-09-21 05:00 | 4.84 | 4.79
2018-09-21 05:30 | 5.38 | 5.33
2018-09-21 06:00 | 5.62 | 5.54
2018-09-21 06:30 | 5.89 | 5.81
2018-09-21 07:00 | 5.92 | 5.85
2018-09-21 07:30 | 5.7 | 5.65
2018-09-21 08:00 | 5.07 | 5.02
2018-09-21 08:30 | 4.15 | 4.1
2018-09-21 09:00 | 3.42 | 3.38
2018-09-21 09:30 | 2.86 | 2.82
2018-09-21 10:00 | 2.46 | 2.41
2018-09-21 10:30 | 1.98 | 1.93
2018-09-21 11:00 | 2.1 | 2.06
2018-09-21 11:30 | 3 | 2.96
2018-09-21 12:00 | 2.3 | 2.26
2018-09-21 12:30 | 2.58 | 2.54
2018-09-21 13:00 | 2.79 | 2.76
2018-09-21 13:30 | 2.78 | 2.74
2018-09-21 14:00 | 3.37 | 3.34
2018-09-21 14:30 | 3.37 | 3.35
2018-09-21 15:00 | 4.48 | 4.46
2018-09-21 15:30 | 4.77 | 4.76
2018-09-21 16:00 | 5.15 | 5.13
2018-09-21 16:30 | 6.35 | 6.34
2018-09-21 17:00 | 7.57 | 7.56
2018-09-21 17:30 | 8.32 | 8.31
2018-09-21 18:00 | 8.99 | 8.98
2018-09-21 18:30 | 10.19 | 10.18
2018-09-21 19:00 | 10.63 | 10.62
2018-09-21 19:30 | 10.31 | 10.3
2018-09-21 20:00 | 10.29 | 10.29
2018-09-21 20:30 | 10.3 | 10.3
2018-09-21 21:00 | 9.8 | 9.79
2018-09-21 21:30 | 9.18 | 9.17
2018-09-21 22:00 | 8.59 | 8.57
2018-09-21 22:30 | 8.19 | 8.17
2018-09-21 23:00 | 8.21 | 8.2
2018-09-21 23:30 | 7.34 | 7.32
2018-09-22 | 6.42 | 6.39
2018-09-22 00:30 | 5.72 | 5.68
2018-09-22 01:00 | 5.43 | 5.38
2018-09-22 01:30 | 5.06 | 5.01
2018-09-22 02:00 | 4.76 | 4.69
2018-09-22 02:30 | 4.56 | 4.49
2018-09-22 03:00 | 4.32 | 4.25
2018-09-22 03:30 | 4.36 | 4.29
2018-09-22 04:00 | 4.33 | 4.26
2018-09-22 04:30 | 4.45 | 4.37
2018-09-22 05:00 | 4.5 | 4.43
2018-09-22 05:30 | 4.69 | 4.61
2018-09-22 06:00 | 4.74 | 4.6
2018-09-22 06:30 | 4.79 | 4.65
2018-09-22 07:00 | 4.71 | 4.58
2018-09-22 07:30 | 4.78 | 4.67
2018-09-22 08:00 | 4.74 | 4.66
2018-09-22 08:30 | 4.54 | 4.47
2018-09-22 09:00 | 4.24 | 4.18
2018-09-22 09:30 | 4.01 | 3.98
2018-09-22 10:00 | 4.26 | 4.23
2018-09-22 10:30 | 4.59 | 4.56
2018-09-22 11:00 | 3.87 | 3.84
2018-09-22 11:30 | 3.69 | 3.65
2018-09-22 12:00 | 3.97 | 3.94
2018-09-22 12:30 | 3.74 | 3.71
2018-09-22 13:00 | 3.66 | 3.63
2018-09-22 13:30 | 3.52 | 3.48
2018-09-22 14:00 | 4.58 | 4.54
2018-09-22 14:30 | 3.88 | 3.84
2018-09-22 15:00 | 4.67 | 4.65
2018-09-22 15:30 | 5.47 | 5.45
2018-09-22 16:00 | 5.7 | 5.68
2018-09-22 16:30 | 6.62 | 6.6
2018-09-22 17:00 | 7.66 | 7.64
2018-09-22 17:30 | 8.31 | 8.3
2018-09-22 18:00 | 9.03 | 9.03
2018-09-22 18:30 | 9.95 | 9.94
2018-09-22 19:00 | 10.14 | 10.14
2018-09-22 19:30 | 9.93 | 9.92
2018-09-22 20:00 | 9.85 | 9.85
2018-09-22 20:30 | 9.61 | 9.6
2018-09-22 21:00 | 9.18 | 9.17
2018-09-22 21:30 | 8.7 | 8.69
2018-09-22 22:00 | 8.23 | 8.22
2018-09-22 22:30 | 7.89 | 7.87
2018-09-22 23:00 | 7.71 | 7.68
2018-09-22 23:30 | 7.1 | 7.07
2018-09-23 | 6.28 | 6.25
2018-09-23 00:30 | 5.6 | 5.55
2018-09-23 01:00 | 5.3 | 5.25
2018-09-23 01:30 | 4.95 | 4.89
2018-09-23 02:00 | 4.71 | 4.65
2018-09-23 02:30 | 4.42 | 4.35
2018-09-23 03:00 | 4.33 | 4.26
2018-09-23 03:30 | 4.25 | 4.17
2018-09-23 04:00 | 4.18 | 4.1
2018-09-23 04:30 | 4.3 | 4.22
2018-09-23 05:00 | 4.29 | 4.21
2018-09-23 05:30 | 4.34 | 4.25
2018-09-23 06:00 | 4.3 | 4.13
2018-09-23 06:30 | 4.41 | 4.25
2018-09-23 07:00 | 4.26 | 4.09
2018-09-23 07:30 | 4.28 | 4.15
2018-09-23 08:00 | 4.1 | 3.98
2018-09-23 08:30 | 4.24 | 4.15
2018-09-23 09:00 | 4.16 | 4.08
2018-09-23 09:30 | 3.91 | 3.86
2018-09-23 10:00 | 3.52 | 3.48
2018-09-23 10:30 | 3.29 | 3.25
2018-09-23 11:00 | 3.18 | 3.14
2018-09-23 11:30 | 3.21 | 3.17
2018-09-23 12:00 | 3.12 | 3.07
2018-09-23 12:30 | 3.07 | 3.01
2018-09-23 13:00 | 3.29 | 3.25
2018-09-23 13:30 | 3.61 | 3.57
2018-09-23 14:00 | 3.88 | 3.83
2018-09-23 14:30 | 4.39 | 4.35
2018-09-23 15:00 | 5.15 | 5.12
2018-09-23 15:30 | 5.84 | 5.82
2018-09-23 16:00 | 6.45 | 6.44
2018-09-23 16:30 | 7.35 | 7.33
2018-09-23 17:00 | 8.42 | 8.41
2018-09-23 17:30 | 9.5 | 9.49
2018-09-23 18:00 | 10.06 | 10.05
2018-09-23 18:30 | 10.92 | 10.91
2018-09-23 19:00 | 10.99 | 10.98
2018-09-23 19:30 | 10.63 | 10.63
2018-09-23 20:00 | 10.21 | 10.2
2018-09-23 20:30 | 10 | 9.99
2018-09-23 21:00 | 9.57 | 9.56
2018-09-23 21:30 | 8.92 | 8.91
2018-09-23 22:00 | 8.28 | 8.26
2018-09-23 22:30 | 7.78 | 7.75
2018-09-23 23:00 | 7.6 | 7.58
2018-09-23 23:30 | 6.6 | 6.57
2018-09-24 | 5.86 | 5.82
2018-09-24 00:30 | 5.19 | 5.14
2018-09-24 01:00 | 4.81 | 4.75
2018-09-24 01:30 | 4.51 | 4.45
2018-09-24 02:00 | 4.37 | 4.3
2018-09-24 02:30 | 4.24 | 4.16
2018-09-24 03:00 | 4.05 | 3.98
2018-09-24 03:30 | 4.17 | 4.09
2018-09-24 04:00 | 4.23 | 4.16
2018-09-24 04:30 | 4.38 | 4.3
2018-09-24 05:00 | 4.62 | 4.56
2018-09-24 05:30 | 5.07 | 5.01
2018-09-24 06:00 | 5.47 | 5.39
2018-09-24 06:30 | 5.97 | 5.91
2018-09-24 07:00 | 5.65 | 5.59
2018-09-24 07:30 | 5.21 | 5.16
2018-09-24 08:00 | 4.8 | 4.75
2018-09-24 08:30 | 4.22 | 4.18
2018-09-24 09:00 | 3.95 | 3.93
2018-09-24 09:30 | 3.66 | 3.64
2018-09-24 10:00 | 3.67 | 3.66
2018-09-24 10:30 | 3.7 | 3.69
2018-09-24 11:00 | 4.01 | 4
2018-09-24 11:30 | 3.87 | 3.86
2018-09-24 12:00 | 4.64 | 4.63
2018-09-24 12:30 | 4.8 | 4.79
2018-09-24 13:00 | 5.38 | 5.37
2018-09-24 13:30 | 5.69 | 5.69
2018-09-24 14:00 | 6.9 | 6.9
2018-09-24 14:30 | 6.49 | 6.48
2018-09-24 15:00 | 6.32 | 6.31
2018-09-24 15:30 | 6.58 | 6.57
2018-09-24 16:00 | 7.68 | 7.67
2018-09-24 16:30 | 8.64 | 8.63
2018-09-24 17:00 | 9.43 | 9.42
2018-09-24 17:30 | 10.23 | 10.23
2018-09-24 18:00 | 10.97 | 10.97
2018-09-24 18:30 | 11.87 | 11.86
2018-09-24 19:00 | 12 | 11.99
2018-09-24 19:30 | 11.54 | 11.54
2018-09-24 20:00 | 11.39 | 11.39
2018-09-24 20:30 | 11.22 | 11.22
2018-09-24 21:00 | 10.69 | 10.69
2018-09-24 21:30 | 9.8 | 9.8
2018-09-24 22:00 | 8.74 | 8.73
2018-09-24 22:30 | 8.1 | 8.08
2018-09-24 23:00 | 7.62 | 7.59
2018-09-24 23:30 | 6.74 | 6.71
2018-09-25 | 5.97 | 5.93
2018-09-25 00:30 | 5.19 | 5.15
2018-09-25 01:00 | 4.81 | 4.76
2018-09-25 01:30 | 4.51 | 4.46
2018-09-25 02:00 | 4.38 | 4.31
2018-09-25 02:30 | 4.23 | 4.16
2018-09-25 03:00 | 4.13 | 4.06
2018-09-25 03:30 | 4.27 | 4.2
2018-09-25 04:00 | 4.25 | 4.18
2018-09-25 04:30 | 4.35 | 4.28
2018-09-25 05:00 | 4.63 | 4.57
2018-09-25 05:30 | 5.08 | 5.04
2018-09-25 06:00 | 5.69 | 5.64
2018-09-25 06:30 | 6.31 | 6.26
2018-09-25 07:00 | 6.5 | 6.45
2018-09-25 07:30 | 7.09 | 7.05
2018-09-25 08:00 | 7.24 | 7.2
2018-09-25 08:30 | 6.62 | 6.58
2018-09-25 09:00 | 5.97 | 5.93
2018-09-25 09:30 | 6.79 | 6.75
2018-09-25 10:00 | 5.25 | 5.2
2018-09-25 10:30 | 5.53 | 5.49
2018-09-25 11:00 | 7.18 | 7.16
2018-09-25 11:30 | 7.95 | 7.93
2018-09-25 12:00 | 8.41 | 8.39
2018-09-25 12:30 | 7.25 | 7.23
2018-09-25 13:00 | 7.17 | 7.15
2018-09-25 13:30 | 7.12 | 7.09
2018-09-25 14:00 | 7.12 | 7.09
2018-09-25 14:30 | 7.31 | 7.3
2018-09-25 15:00 | 7.27 | 7.25
2018-09-25 15:30 | 7.54 | 7.52
2018-09-25 16:00 | 7.97 | 7.95
2018-09-25 16:30 | 8.94 | 8.93
2018-09-25 17:00 | 9.93 | 9.93
2018-09-25 17:30 | 10.61 | 10.6
2018-09-25 18:00 | 11.37 | 11.37
2018-09-25 18:30 | 12.02 | 12.02
2018-09-25 19:00 | 12.29 | 12.29
2018-09-25 19:30 | 11.84 | 11.84
2018-09-25 20:00 | 11.63 | 11.62
2018-09-25 20:30 | 11.18 | 11.17
2018-09-25 21:00 | 10.72 | 10.72
2018-09-25 21:30 | 9.68 | 9.68
2018-09-25 22:00 | 8.91 | 8.9
2018-09-25 22:30 | 8.28 | 8.26
2018-09-25 23:00 | 7.93 | 7.9
2018-09-25 23:30 | 6.98 | 6.96
2018-09-26 | 6.11 | 6.07
2018-09-26 00:30 | 5.42 | 5.38
2018-09-26 01:00 | 5.04 | 4.99
2018-09-26 01:30 | 4.71 | 4.65
2018-09-26 02:00 | 4.52 | 4.45
2018-09-26 02:30 | 4.28 | 4.21
2018-09-26 03:00 | 4.21 | 4.15
2018-09-26 03:30 | 4.27 | 4.2
2018-09-26 04:00 | 4.29 | 4.22
2018-09-26 04:30 | 4.58 | 4.52
2018-09-26 05:00 | 4.92 | 4.86
2018-09-26 05:30 | 5.23 | 5.18
2018-09-26 06:00 | 5.46 | 5.38
2018-09-26 06:30 | 5.8 | 5.72
2018-09-26 07:00 | 6.19 | 6.13
2018-09-26 07:30 | 5.75 | 5.69
2018-09-26 08:00 | 4.83 | 4.78
2018-09-26 08:30 | 4.22 | 4.18
2018-09-26 09:00 | 4.53 | 4.5
2018-09-26 09:30 | 4.68 | 4.65
2018-09-26 10:00 | 4.44 | 4.42
2018-09-26 10:30 | 3.89 | 3.87
2018-09-26 11:00 | 3.75 | 3.73
2018-09-26 11:30 | 4.44 | 4.43
2018-09-26 12:00 | 4.05 | 4.04
2018-09-26 12:30 | 4.85 | 4.83
2018-09-26 13:00 | 5.79 | 5.78
2018-09-26 13:30 | 5.74 | 5.73
2018-09-26 14:00 | 5.79 | 5.77
2018-09-26 14:30 | 6.91 | 6.9
2018-09-26 15:00 | 5.47 | 5.45
2018-09-26 15:30 | 4.89 | 4.87
2018-09-26 16:00 | 5.81 | 5.8
2018-09-26 16:30 | 6.98 | 6.97
2018-09-26 17:00 | 8.21 | 8.2
2018-09-26 17:30 | 9.29 | 9.28
2018-09-26 18:00 | 10.53 | 10.53
2018-09-26 18:30 | 11.75 | 11.75
2018-09-26 19:00 | 12.19 | 12.18
2018-09-26 19:30 | 11.86 | 11.86
2018-09-26 20:00 | 11.7 | 11.7
2018-09-26 20:30 | 11.62 | 11.62
2018-09-26 21:00 | 11.05 | 11.05
2018-09-26 21:30 | 9.99 | 9.99
2018-09-26 22:00 | 9.25 | 9.25
2018-09-26 22:30 | 8.4 | 8.38
2018-09-26 23:00 | 7.85 | 7.82
2018-09-26 23:30 | 6.89 | 6.86
2018-09-27 | 6.05 | 6.01
2018-09-27 00:30 | 5.45 | 5.4
2018-09-27 01:00 | 5 | 4.95
2018-09-27 01:30 | 4.82 | 4.77
2018-09-27 02:00 | 4.59 | 4.54
2018-09-27 02:30 | 4.38 | 4.32
2018-09-27 03:00 | 4.22 | 4.16
2018-09-27 03:30 | 4.24 | 4.17
2018-09-27 04:00 | 4.32 | 4.25
2018-09-27 04:30 | 4.39 | 4.31
2018-09-27 05:00 | 4.69 | 4.63
2018-09-27 05:30 | 5.12 | 5.07
2018-09-27 06:00 | 5.81 | 5.75
2018-09-27 06:30 | 6.08 | 6.03
2018-09-27 07:00 | 6.26 | 6.21
2018-09-27 07:30 | 6.22 | 6.18
2018-09-27 08:00 | 6.11 | 6.07
2018-09-27 08:30 | 6.08 | 6.05
2018-09-27 09:00 | 6.02 | 5.99
2018-09-27 09:30 | 6.68 | 6.66
2018-09-27 10:00 | 6.36 | 6.33
2018-09-27 10:30 | 5.79 | 5.77
2018-09-27 11:00 | 5.76 | 5.74
2018-09-27 11:30 | 5.97 | 5.95
2018-09-27 12:00 | 6.2 | 6.19
2018-09-27 12:30 | 5.44 | 5.42
2018-09-27 13:00 | 5.7 | 5.68
2018-09-27 13:30 | 4.83 | 4.81
2018-09-27 14:00 | 3.91 | 3.89
2018-09-27 14:30 | 4.25 | 4.24
2018-09-27 15:00 | 4.39 | 4.38
2018-09-27 15:30 | 4.91 | 4.9
2018-09-27 16:00 | 6.32 | 6.31
2018-09-27 16:30 | 6.99 | 6.98
2018-09-27 17:00 | 8.27 | 8.27
2018-09-27 17:30 | 9.08 | 9.07
2018-09-27 18:00 | 10.04 | 10.03
2018-09-27 18:30 | 11.18 | 11.17
2018-09-27 19:00 | 11.75 | 11.75
2018-09-27 19:30 | 11.57 | 11.56
2018-09-27 20:00 | 11.4 | 11.4
2018-09-27 20:30 | 11.49 | 11.49
2018-09-27 21:00 | 10.84 | 10.84
2018-09-27 21:30 | 9.77 | 9.77
2018-09-27 22:00 | 9.03 | 9.02
2018-09-27 22:30 | 8.55 | 8.54
2018-09-27 23:00 | 8.03 | 8.02
2018-09-27 23:30 | 7.13 | 7.11
2018-09-28 | 6.22 | 6.19
2018-09-28 00:30 | 5.47 | 5.44
2018-09-28 01:00 | 5.12 | 5.08
2018-09-28 01:30 | 4.72 | 4.67
2018-09-28 02:00 | 4.47 | 4.42
2018-09-28 02:30 | 4.3 | 4.24
2018-09-28 03:00 | 4.24 | 4.18
2018-09-28 03:30 | 4.27 | 4.21
2018-09-28 04:00 | 4.28 | 4.22
2018-09-28 04:30 | 4.46 | 4.41
2018-09-28 05:00 | 4.66 | 4.61
2018-09-28 05:30 | 4.98 | 4.93
2018-09-28 06:00 | 5.17 | 5.08
2018-09-28 06:30 | 5.44 | 5.37
2018-09-28 07:00 | 4.96 | 4.88
2018-09-28 07:30 | 5.3 | 5.23
2018-09-28 08:00 | 5.57 | 5.51
2018-09-28 08:30 | 5.32 | 5.28
2018-09-28 09:00 | 5.53 | 5.49
2018-09-28 09:30 | 5.12 | 5.09
2018-09-28 10:00 | 4.38 | 4.35
2018-09-28 10:30 | 4.66 | 4.64
2018-09-28 11:00 | 3.7 | 3.67
2018-09-28 11:30 | 3.42 | 3.38
2018-09-28 12:00 | 3.73 | 3.7
2018-09-28 12:30 | 3.48 | 3.43
2018-09-28 13:00 | 3.39 | 3.35
2018-09-28 13:30 | 4.27 | 4.24
2018-09-28 14:00 | 4.23 | 4.2
2018-09-28 14:30 | 3.94 | 3.9
2018-09-28 15:00 | 4.69 | 4.66
2018-09-28 15:30 | 5.5 | 5.47
2018-09-28 16:00 | 6.27 | 6.25
2018-09-28 16:30 | 7.05 | 7.03
2018-09-28 17:00 | 8.04 | 8.02
2018-09-28 17:30 | 8.82 | 8.8
2018-09-28 18:00 | 9.35 | 9.33
2018-09-28 18:30 | 10.21 | 10.2
2018-09-28 19:00 | 10.63 | 10.62
2018-09-28 19:30 | 10.47 | 10.46
2018-09-28 20:00 | 10.42 | 10.41
2018-09-28 20:30 | 10.27 | 10.26
2018-09-28 21:00 | 9.77 | 9.76
2018-09-28 21:30 | 9.04 | 9.03
2018-09-28 22:00 | 8.58 | 8.57
2018-09-28 22:30 | 8.27 | 8.26
2018-09-28 23:00 | 8.14 | 8.12
2018-09-28 23:30 | 7.28 | 7.27
2018-09-29 | 6.44 | 6.41
2018-09-29 00:30 | 5.68 | 5.65
2018-09-29 01:00 | 5.41 | 5.38
2018-09-29 01:30 | 5.06 | 5.01
2018-09-29 02:00 | 4.72 | 4.68
2018-09-29 02:30 | 4.61 | 4.56
2018-09-29 03:00 | 4.31 | 4.25
2018-09-29 03:30 | 4.33 | 4.27
2018-09-29 04:00 | 4.23 | 4.16
2018-09-29 04:30 | 4.23 | 4.17
2018-09-29 05:00 | 4.26 | 4.2
2018-09-29 05:30 | 4.43 | 4.35
2018-09-29 06:00 | 4.46 | 4.32
2018-09-29 06:30 | 4.51 | 4.39
2018-09-29 07:00 | 4.4 | 4.3
2018-09-29 07:30 | 4.33 | 4.24
2018-09-29 08:00 | 4.28 | 4.21
2018-09-29 08:30 | 4.23 | 4.18
2018-09-29 09:00 | 4.41 | 4.39
2018-09-29 09:30 | 4.09 | 4.05
2018-09-29 10:00 | 3.69 | 3.65
2018-09-29 10:30 | 3.43 | 3.37
2018-09-29 11:00 | 3.2 | 3.14
2018-09-29 11:30 | 3.38 | 3.3
2018-09-29 12:00 | 3.72 | 3.66
2018-09-29 12:30 | 3.64 | 3.58
2018-09-29 13:00 | 4.36 | 4.31
2018-09-29 13:30 | 4.33 | 4.26
2018-09-29 14:00 | 5.44 | 5.39
2018-09-29 14:30 | 5.77 | 5.73
2018-09-29 15:00 | 7.88 | 7.85
2018-09-29 15:30 | 8.09 | 8.07
2018-09-29 16:00 | 8.32 | 8.3
2018-09-29 16:30 | 8.12 | 8.1
2018-09-29 17:00 | 8.42 | 8.4
2018-09-29 17:30 | 8.7 | 8.68
2018-09-29 18:00 | 9.22 | 9.2
2018-09-29 18:30 | 9.89 | 9.88
2018-09-29 19:00 | 10.08 | 10.06
2018-09-29 19:30 | 9.71 | 9.7
2018-09-29 20:00 | 9.71 | 9.7
2018-09-29 20:30 | 9.54 | 9.53
2018-09-29 21:00 | 9.03 | 9.02
2018-09-29 21:30 | 8.5 | 8.49
2018-09-29 22:00 | 8.08 | 8.07
2018-09-29 22:30 | 7.88 | 7.87
2018-09-29 23:00 | 7.85 | 7.84
2018-09-29 23:30 | 7.2 | 7.18
2018-09-30 | 6.24 | 6.22
2018-09-30 00:30 | 5.69 | 5.66
2018-09-30 01:00 | 5.32 | 5.29
2018-09-30 01:30 | 4.93 | 4.89
2018-09-30 02:00 | 4.59 | 4.55
2018-09-30 02:30 | 4.52 | 4.47
2018-09-30 03:00 | 4.37 | 4.32
2018-09-30 03:30 | 4.3 | 4.24
2018-09-30 04:00 | 4.28 | 4.22
2018-09-30 04:30 | 4.28 | 4.22
2018-09-30 05:00 | 4.27 | 4.22
2018-09-30 05:30 | 4.32 | 4.26
2018-09-30 06:00 | 4.39 | 4.28
2018-09-30 06:30 | 4.57 | 4.46
2018-09-30 07:00 | 4.97 | 4.86
2018-09-30 07:30 | 5.19 | 5.09
2018-09-30 08:00 | 5.76 | 5.68
2018-09-30 08:30 | 6.91 | 6.85
2018-09-30 09:00 | 7.57 | 7.53
2018-09-30 09:30 | 7.68 | 7.65
2018-09-30 10:00 | 7.55 | 7.52
2018-09-30 10:30 | 7.67 | 7.63
2018-09-30 11:00 | 8.27 | 8.24
2018-09-30 11:30 | 8.84 | 8.82
2018-09-30 12:00 | 8.71 | 8.68
2018-09-30 12:30 | 8.23 | 8.21
2018-09-30 13:00 | 6.33 | 6.29
2018-09-30 13:30 | 4.35 | 4.3
2018-09-30 14:00 | 5.42 | 5.38
2018-09-30 14:30 | 5.8 | 5.76
2018-09-30 15:00 | 6.31 | 6.28
2018-09-30 15:30 | 5.1 | 5.06
2018-09-30 16:00 | 6.18 | 6.15
2018-09-30 16:30 | 7.33 | 7.3
2018-09-30 17:00 | 8.04 | 8.01
2018-09-30 17:30 | 8.72 | 8.7
2018-09-30 18:00 | 9.48 | 9.46
2018-09-30 18:30 | 10.37 | 10.37
2018-09-30 19:00 | 10.47 | 10.47
2018-09-30 19:30 | 9.97 | 9.97
2018-09-30 20:00 | 9.86 | 9.85
2018-09-30 20:30 | 9.82 | 9.82
2018-09-30 21:00 | 9.34 | 9.33
2018-09-30 21:30 | 8.76 | 8.74
2018-09-30 22:00 | 8.45 | 8.43
2018-09-30 22:30 | 8.27 | 8.25
2018-09-30 23:00 | 8.02 | 8
2018-09-30 23:30 | 7.29 | 7.26
2018-10-01 | 6.38 | 6.34
2018-10-01 00:30 | 5.72 | 5.67
2018-10-01 01:00 | 5.26 | 5.21
2018-10-01 01:30 | 4.89 | 4.84
2018-10-01 02:00 | 4.53 | 4.46
2018-10-01 02:30 | 4.49 | 4.41
2018-10-01 03:00 | 4.31 | 4.23
2018-10-01 03:30 | 4.33 | 4.25
2018-10-01 04:00 | 4.4 | 4.32
2018-10-01 04:30 | 4.35 | 4.27
2018-10-01 05:00 | 4.31 | 4.23
2018-10-01 05:30 | 4.39 | 4.28
2018-10-01 06:00 | 4.39 | 4.22
2018-10-01 06:30 | 4.17 | 3.98
2018-10-01 07:00 | 3.94 | 3.76
2018-10-01 07:30 | 3.81 | 3.65
2018-10-01 08:00 | 3.65 | 3.52
2018-10-01 08:30 | 3.6 | 3.5
2018-10-01 09:00 | 3.53 | 3.45
2018-10-01 09:30 | 3.46 | 3.39
2018-10-01 10:00 | 3.43 | 3.38
2018-10-01 10:30 | 3.17 | 3.12
2018-10-01 11:00 | 3.13 | 3.09
2018-10-01 11:30 | 3.34 | 3.31
2018-10-01 12:00 | 3.77 | 3.74
2018-10-01 12:30 | 3 | 2.96
2018-10-01 13:00 | 3.55 | 3.53
2018-10-01 13:30 | 3.65 | 3.62
2018-10-01 14:00 | 4.26 | 4.23
2018-10-01 14:30 | 4.35 | 4.33
2018-10-01 15:00 | 4.7 | 4.67
2018-10-01 15:30 | 5.01 | 4.99
2018-10-01 16:00 | 6.75 | 6.73
2018-10-01 16:30 | 6.76 | 6.74
2018-10-01 17:00 | 7.92 | 7.9
2018-10-01 17:30 | 8.92 | 8.91
2018-10-01 18:00 | 9.75 | 9.74
2018-10-01 18:30 | 10.96 | 10.95
2018-10-01 19:00 | 11.48 | 11.48
2018-10-01 19:30 | 10.91 | 10.9
2018-10-01 20:00 | 10.76 | 10.75
2018-10-01 20:30 | 10.54 | 10.53
2018-10-01 21:00 | 9.97 | 9.97
2018-10-01 21:30 | 9.17 | 9.16
2018-10-01 22:00 | 8.55 | 8.54
2018-10-01 22:30 | 8.01 | 7.99
2018-10-01 23:00 | 7.74 | 7.71
2018-10-01 23:30 | 7 | 6.97
2018-10-02 | 6.08 | 6.04
2018-10-02 00:30 | 5.48 | 5.42
2018-10-02 01:00 | 5.07 | 5.01
2018-10-02 01:30 | 4.72 | 4.65
2018-10-02 02:00 | 4.46 | 4.38
2018-10-02 02:30 | 4.32 | 4.25
2018-10-02 03:00 | 4.16 | 4.07
2018-10-02 03:30 | 4.22 | 4.14
2018-10-02 04:00 | 4.26 | 4.17
2018-10-02 04:30 | 4.42 | 4.34
2018-10-02 05:00 | 4.8 | 4.73
2018-10-02 05:30 | 5.13 | 5.04
2018-10-02 06:00 | 5.29 | 5.17
2018-10-02 06:30 | 5.31 | 5.19
2018-10-02 07:00 | 4.95 | 4.83
2018-10-02 07:30 | 4.6 | 4.49
2018-10-02 08:00 | 3.97 | 3.86
2018-10-02 08:30 | 3.39 | 3.29
2018-10-02 09:00 | 2.89 | 2.8
2018-10-02 09:30 | 2.54 | 2.46
2018-10-02 10:00 | 2.54 | 2.48
2018-10-02 10:30 | 2.41 | 2.36
2018-10-02 11:00 | 3.08 | 3.04
2018-10-02 11:30 | 2.79 | 2.75
2018-10-02 12:00 | 2.44 | 2.4
2018-10-02 12:30 | 2.85 | 2.82
2018-10-02 13:00 | 2.85 | 2.81
2018-10-02 13:30 | 2.81 | 2.77
2018-10-02 14:00 | 2.95 | 2.92
2018-10-02 14:30 | 2.99 | 2.95
2018-10-02 15:00 | 3.25 | 3.22
2018-10-02 15:30 | 4.13 | 4.1
2018-10-02 16:00 | 5.1 | 5.07
2018-10-02 16:30 | 6.37 | 6.35
2018-10-02 17:00 | 7.51 | 7.5
2018-10-02 17:30 | 8.64 | 8.63
2018-10-02 18:00 | 9.49 | 9.48
2018-10-02 18:30 | 10.99 | 10.99
2018-10-02 19:00 | 11.41 | 11.41
2018-10-02 19:30 | 10.96 | 10.96
2018-10-02 20:00 | 10.84 | 10.83
2018-10-02 20:30 | 10.76 | 10.76
2018-10-02 21:00 | 11.55 | 11.55
2018-10-02 21:30 | 10.89 | 10.87
2018-10-02 22:00 | 9.99 | 9.97
2018-10-02 22:30 | 9.26 | 9.23
2018-10-02 23:00 | 7.77 | 7.75
2018-10-02 23:30 | 7 | 6.97
2018-10-03 | 6.14 | 6.1
2018-10-03 00:30 | 5.39 | 5.34
2018-10-03 01:00 | 5.03 | 4.97
2018-10-03 01:30 | 4.74 | 4.68
2018-10-03 02:00 | 4.42 | 4.35
2018-10-03 02:30 | 4.34 | 4.26
2018-10-03 03:00 | 4.25 | 4.18
2018-10-03 03:30 | 4.24 | 4.16
2018-10-03 04:00 | 4.43 | 4.35
2018-10-03 04:30 | 4.47 | 4.4
2018-10-03 05:00 | 4.88 | 4.82
2018-10-03 05:30 | 5.2 | 5.11
2018-10-03 06:00 | 5.47 | 5.37
2018-10-03 06:30 | 5.27 | 5.16
2018-10-03 07:00 | 4.97 | 4.86
2018-10-03 07:30 | 4.49 | 4.38
2018-10-03 08:00 | 3.81 | 3.7
2018-10-03 08:30 | 3.3 | 3.2
2018-10-03 09:00 | 2.81 | 2.74
2018-10-03 09:30 | 2.44 | 2.38
2018-10-03 10:00 | 2.21 | 2.15
2018-10-03 10:30 | 1.81 | 1.74
2018-10-03 11:00 | 1.71 | 1.64
2018-10-03 11:30 | 1.72 | 1.66
2018-10-03 12:00 | 1.78 | 1.71
2018-10-03 12:30 | 1.85 | 1.77
2018-10-03 13:00 | 2.03 | 1.96
2018-10-03 13:30 | 2.32 | 2.25
2018-10-03 14:00 | 2.77 | 2.71
2018-10-03 14:30 | 3.14 | 3.09
2018-10-03 15:00 | 3.71 | 3.67
2018-10-03 15:30 | 4.52 | 4.49
2018-10-03 16:00 | 5.33 | 5.31
2018-10-03 16:30 | 6.41 | 6.39
2018-10-03 17:00 | 7.55 | 7.53
2018-10-03 17:30 | 8.52 | 8.5
2018-10-03 18:00 | 9.51 | 9.5
2018-10-03 18:30 | 10.79 | 10.78
2018-10-03 19:00 | 11.31 | 11.3
2018-10-03 19:30 | 10.93 | 10.92
2018-10-03 20:00 | 10.87 | 10.87
2018-10-03 20:30 | 10.57 | 10.57
2018-10-03 21:00 | 10.02 | 10.01
2018-10-03 21:30 | 9.31 | 9.3
2018-10-03 22:00 | 8.6 | 8.59
2018-10-03 22:30 | 8.06 | 8.05
2018-10-03 23:00 | 7.73 | 7.71
2018-10-03 23:30 | 6.8 | 6.77
2018-10-04 | 6.01 | 5.97
2018-10-04 00:30 | 5.38 | 5.34
2018-10-04 01:00 | 5.05 | 5
2018-10-04 01:30 | 4.7 | 4.65
2018-10-04 02:00 | 4.4 | 4.33
2018-10-04 02:30 | 4.31 | 4.24
2018-10-04 03:00 | 4.29 | 4.22
2018-10-04 03:30 | 4.31 | 4.24
2018-10-04 04:00 | 4.33 | 4.26
2018-10-04 04:30 | 4.49 | 4.43
2018-10-04 05:00 | 4.79 | 4.73
2018-10-04 05:30 | 5.03 | 4.95
2018-10-04 06:00 | 5.14 | 5.03
2018-10-04 06:30 | 4.98 | 4.87
2018-10-04 07:00 | 4.52 | 4.41
2018-10-04 07:30 | 4.87 | 4.78
2018-10-04 08:00 | 3.68 | 3.58
2018-10-04 08:30 | 3.13 | 3.04
2018-10-04 09:00 | 2.62 | 2.53
2018-10-04 09:30 | 2.49 | 2.43
2018-10-04 10:00 | 2.22 | 2.16
2018-10-04 10:30 | 2.02 | 1.95
2018-10-04 11:00 | 1.86 | 1.78
2018-10-04 11:30 | 1.82 | 1.75
2018-10-04 12:00 | 2.25 | 2.19
2018-10-04 12:30 | 2.3 | 2.24
2018-10-04 13:00 | 2.38 | 2.31
2018-10-04 13:30 | 2.81 | 2.76
2018-10-04 14:00 | 3.79 | 3.75
2018-10-04 14:30 | 4.3 | 4.27
2018-10-04 15:00 | 4.2 | 4.16
2018-10-04 15:30 | 5.18 | 5.16
2018-10-04 16:00 | 6.85 | 6.84
2018-10-04 16:30 | 6.48 | 6.47
2018-10-04 17:00 | 8.3 | 8.29
2018-10-04 17:30 | 9.05 | 9.03
2018-10-04 18:00 | 9.57 | 9.56
2018-10-04 18:30 | 10.5 | 10.49
2018-10-04 19:00 | 11.07 | 11.06
2018-10-04 19:30 | 10.75 | 10.74
2018-10-04 20:00 | 10.69 | 10.68
2018-10-04 20:30 | 10.49 | 10.49
2018-10-04 21:00 | 9.96 | 9.96
2018-10-04 21:30 | 9.28 | 9.27
2018-10-04 22:00 | 8.53 | 8.52
2018-10-04 22:30 | 7.92 | 7.91
2018-10-04 23:00 | 7.69 | 7.67
2018-10-04 23:30 | 6.89 | 6.86
2018-10-05 | 6.03 | 6
2018-10-05 00:30 | 5.42 | 5.39
2018-10-05 01:00 | 5.08 | 5.04
2018-10-05 01:30 | 4.74 | 4.69
2018-10-05 02:00 | 4.48 | 4.42
2018-10-05 02:30 | 4.34 | 4.28
2018-10-05 03:00 | 4.24 | 4.18
2018-10-05 03:30 | 4.33 | 4.27
2018-10-05 04:00 | 4.29 | 4.23
2018-10-05 04:30 | 4.33 | 4.27
2018-10-05 05:00 | 4.6 | 4.54
2018-10-05 05:30 | 4.84 | 4.77
2018-10-05 06:00 | 5.03 | 4.93
2018-10-05 06:30 | 5.27 | 5.18
2018-10-05 07:00 | 5.06 | 4.97
2018-10-05 07:30 | 4.93 | 4.86
2018-10-05 08:00 | 5.14 | 5.08
2018-10-05 08:30 | 4.85 | 4.81
2018-10-05 09:00 | 5.2 | 5.16
2018-10-05 09:30 | 5.54 | 5.51
2018-10-05 10:00 | 5.37 | 5.35
2018-10-05 10:30 | 6.26 | 6.24
2018-10-05 11:00 | 5.95 | 5.93
2018-10-05 11:30 | 4.66 | 4.63
2018-10-05 12:00 | 4.68 | 4.66
2018-10-05 12:30 | 4.87 | 4.85
2018-10-05 13:00 | 3.91 | 3.88
2018-10-05 13:30 | 5.34 | 5.33
2018-10-05 14:00 | 6.91 | 6.9
2018-10-05 14:30 | 6.86 | 6.84
2018-10-05 15:00 | 7.14 | 7.13
2018-10-05 15:30 | 7.33 | 7.32
2018-10-05 16:00 | 7.53 | 7.51
2018-10-05 16:30 | 7.52 | 7.5
2018-10-05 17:00 | 7.61 | 7.59
2018-10-05 17:30 | 8.24 | 8.23
2018-10-05 18:00 | 8.97 | 8.96
2018-10-05 18:30 | 10.07 | 10.06
2018-10-05 19:00 | 10.63 | 10.62
2018-10-05 19:30 | 10.28 | 10.27
2018-10-05 20:00 | 10.22 | 10.22
2018-10-05 20:30 | 10.17 | 10.16
2018-10-05 21:00 | 9.6 | 9.59
2018-10-05 21:30 | 9.07 | 9.06
2018-10-05 22:00 | 8.52 | 8.51
2018-10-05 22:30 | 8.17 | 8.16
2018-10-05 23:00 | 7.96 | 7.94
2018-10-05 23:30 | 7.11 | 7.09
2018-10-06 | 6.29 | 6.26
2018-10-06 00:30 | 5.88 | 5.84
2018-10-06 01:00 | 5.25 | 5.2
2018-10-06 01:30 | 4.89 | 4.84
2018-10-06 02:00 | 4.7 | 4.64
2018-10-06 02:30 | 4.48 | 4.43
2018-10-06 03:00 | 4.33 | 4.26
2018-10-06 03:30 | 4.3 | 4.24
2018-10-06 04:00 | 4.21 | 4.15
2018-10-06 04:30 | 4.32 | 4.26
2018-10-06 05:00 | 4.45 | 4.4
2018-10-06 05:30 | 4.5 | 4.43
2018-10-06 06:00 | 4.58 | 4.47
2018-10-06 06:30 | 4.68 | 4.56
2018-10-06 07:00 | 4.88 | 4.77
2018-10-06 07:30 | 5.5 | 5.42
2018-10-06 08:00 | 5.23 | 5.14
2018-10-06 08:30 | 5.8 | 5.73
2018-10-06 09:00 | 6.75 | 6.71
2018-10-06 09:30 | 6.87 | 6.84
2018-10-06 10:00 | 6.56 | 6.53
2018-10-06 10:30 | 6.29 | 6.26
2018-10-06 11:00 | 7.63 | 7.61
2018-10-06 11:30 | 5.87 | 5.84
2018-10-06 12:00 | 5.32 | 5.29
2018-10-06 12:30 | 6.06 | 6.03
2018-10-06 13:00 | 4.32 | 4.28
2018-10-06 13:30 | 5.07 | 5.04
2018-10-06 14:00 | 5.96 | 5.94
2018-10-06 14:30 | 7.28 | 7.26
2018-10-06 15:00 | 6.04 | 6.02
2018-10-06 15:30 | 7.51 | 7.48
2018-10-06 16:00 | 8.04 | 8.02
2018-10-06 16:30 | 8.72 | 8.7
2018-10-06 17:00 | 9.43 | 9.41
2018-10-06 17:30 | 9.72 | 9.71
2018-10-06 18:00 | 9.84 | 9.84
2018-10-06 18:30 | 10.32 | 10.31
2018-10-06 19:00 | 10.5 | 10.49
2018-10-06 19:30 | 10.03 | 10.03
2018-10-06 20:00 | 10.05 | 10.05
2018-10-06 20:30 | 10.09 | 10.09
2018-10-06 21:00 | 9.41 | 9.4
2018-10-06 21:30 | 8.76 | 8.75
2018-10-06 22:00 | 8.33 | 8.32
2018-10-06 22:30 | 7.94 | 7.92
2018-10-06 23:00 | 7.96 | 7.94
2018-10-06 23:30 | 7.31 | 7.28
2018-10-07 | 6.52 | 6.49
2018-10-07 00:30 | 5.72 | 5.68
2018-10-07 01:00 | 5.36 | 5.32
2018-10-07 01:30 | 4.94 | 4.89
2018-10-07 02:00 | 4.62 | 4.56
2018-10-07 02:30 | 4.47 | 4.41
2018-10-07 03:00 | 4.32 | 4.25
2018-10-07 03:30 | 4.29 | 4.22
2018-10-07 04:00 | 4.26 | 4.19
2018-10-07 04:30 | 4.29 | 4.22
2018-10-07 05:00 | 4.28 | 4.22
2018-10-07 05:30 | 4.29 | 4.2
2018-10-07 06:00 | 4.34 | 4.19
2018-10-07 06:30 | 4.25 | 4.1
2018-10-07 07:00 | 4.03 | 3.88
2018-10-07 07:30 | 3.97 | 3.85
2018-10-07 08:00 | 4.05 | 3.97
2018-10-07 08:30 | 4.1 | 4.05
2018-10-07 09:00 | 4.25 | 4.22
2018-10-07 09:30 | 5.08 | 5.05
2018-10-07 10:00 | 4.65 | 4.62
2018-10-07 10:30 | 5.02 | 5
2018-10-07 11:00 | 5.9 | 5.88
2018-10-07 11:30 | 6.26 | 6.24
2018-10-07 12:00 | 6.7 | 6.68
2018-10-07 12:30 | 7.11 | 7.09
2018-10-07 13:00 | 5.9 | 5.88
2018-10-07 13:30 | 5.9 | 5.88
2018-10-07 14:00 | 5.92 | 5.91
2018-10-07 14:30 | 5.96 | 5.94
2018-10-07 15:00 | 5.65 | 5.63
2018-10-07 15:30 | 6.08 | 6.06
2018-10-07 16:00 | 6.31 | 6.29
2018-10-07 16:30 | 7.69 | 7.68
2018-10-07 17:00 | 8.47 | 8.46
2018-10-07 17:30 | 9.45 | 9.43
2018-10-07 18:00 | 10.16 | 10.15
2018-10-07 18:30 | 11.27 | 11.27
2018-10-07 19:00 | 11.47 | 11.46
2018-10-07 19:30 | 10.95 | 10.94
2018-10-07 20:00 | 10.79 | 10.78
2018-10-07 20:30 | 10.6 | 10.6
2018-10-07 21:00 | 10.03 | 10.02
2018-10-07 21:30 | 9.25 | 9.24
2018-10-07 22:00 | 8.54 | 8.53
2018-10-07 22:30 | 7.99 | 7.97
2018-10-07 23:00 | 7.69 | 7.67
2018-10-07 23:30 | 6.88 | 6.85
2018-10-08 | 5.88 | 5.84
2018-10-08 00:30 | 5.25 | 5.2
2018-10-08 01:00 | 4.86 | 4.8
2018-10-08 01:30 | 4.58 | 4.51
2018-10-08 02:00 | 4.29 | 4.22
2018-10-08 02:30 | 4.25 | 4.18
2018-10-08 03:00 | 4.19 | 4.11
2018-10-08 03:30 | 4.16 | 4.08
2018-10-08 04:00 | 4.23 | 4.16
2018-10-08 04:30 | 4.36 | 4.29
2018-10-08 05:00 | 4.63 | 4.56
2018-10-08 05:30 | 5.07 | 4.99
2018-10-08 06:00 | 5.59 | 5.49
2018-10-08 06:30 | 5.89 | 5.82
2018-10-08 07:00 | 6.06 | 6
2018-10-08 07:30 | 5.42 | 5.37
2018-10-08 08:00 | 4.8 | 4.75
2018-10-08 08:30 | 3.86 | 3.82
2018-10-08 09:00 | 3.81 | 3.78
2018-10-08 09:30 | 3.4 | 3.38
2018-10-08 10:00 | 2.69 | 2.66
2018-10-08 10:30 | 2.71 | 2.68
2018-10-08 11:00 | 3.93 | 3.91
2018-10-08 11:30 | 3.4 | 3.39
2018-10-08 12:00 | 2.95 | 2.93
2018-10-08 12:30 | 3.51 | 3.49
2018-10-08 13:00 | 5.18 | 5.17
2018-10-08 13:30 | 7.34 | 7.34
2018-10-08 14:00 | 6.01 | 6
2018-10-08 14:30 | 3.78 | 3.76
2018-10-08 15:00 | 5.04 | 5.03
2018-10-08 15:30 | 5.18 | 5.17
2018-10-08 16:00 | 6.53 | 6.53
2018-10-08 16:30 | 7.67 | 7.66
2018-10-08 17:00 | 9.82 | 9.82
2018-10-08 17:30 | 10.86 | 10.85
2018-10-08 18:00 | 11.32 | 11.31
2018-10-08 18:30 | 11.9 | 11.89
2018-10-08 19:00 | 12.16 | 12.15
2018-10-08 19:30 | 11.57 | 11.57
2018-10-08 20:00 | 11.36 | 11.35
2018-10-08 20:30 | 11.32 | 11.32
2018-10-08 21:00 | 10.62 | 10.61
2018-10-08 21:30 | 9.67 | 9.66
2018-10-08 22:00 | 8.73 | 8.72
2018-10-08 22:30 | 7.93 | 7.91
2018-10-08 23:00 | 7.57 | 7.55
2018-10-08 23:30 | 6.62 | 6.59
2018-10-09 | 5.83 | 5.78
2018-10-09 00:30 | 5.09 | 5.04
2018-10-09 01:00 | 4.8 | 4.74
2018-10-09 01:30 | 4.48 | 4.42
2018-10-09 02:00 | 4.27 | 4.19
2018-10-09 02:30 | 4.21 | 4.14
2018-10-09 03:00 | 4.11 | 4.03
2018-10-09 03:30 | 4.18 | 4.1
2018-10-09 04:00 | 4.22 | 4.14
2018-10-09 04:30 | 4.44 | 4.36
2018-10-09 05:00 | 4.71 | 4.65
2018-10-09 05:30 | 5.07 | 4.99
2018-10-09 06:00 | 5.78 | 5.7
2018-10-09 06:30 | 6.18 | 6.13
2018-10-09 07:00 | 6.85 | 6.8
2018-10-09 07:30 | 7.06 | 7.03
2018-10-09 08:00 | 7.17 | 7.14
2018-10-09 08:30 | 6 | 5.97
2018-10-09 09:00 | 5.19 | 5.16
2018-10-09 09:30 | 5.38 | 5.36
2018-10-09 10:00 | 5.72 | 5.71
2018-10-09 10:30 | 4.42 | 4.41
2018-10-09 11:00 | 4.94 | 4.92
2018-10-09 11:30 | 3.7 | 3.69
2018-10-09 12:00 | 4.11 | 4.09
2018-10-09 12:30 | 4.12 | 4.11
2018-10-09 13:00 | 3.36 | 3.34
2018-10-09 13:30 | 3.94 | 3.92
2018-10-09 14:00 | 4.8 | 4.78
2018-10-09 14:30 | 5.53 | 5.52
2018-10-09 15:00 | 6.01 | 5.99
2018-10-09 15:30 | 7.99 | 7.98
2018-10-09 16:00 | 9.23 | 9.23
2018-10-09 16:30 | 10.02 | 10.02
2018-10-09 17:00 | 10.71 | 10.71
2018-10-09 17:30 | 11.87 | 11.87
2018-10-09 18:00 | 11.39 | 11.39
2018-10-09 18:30 | 11.98 | 11.98
2018-10-09 19:00 | 12.47 | 12.46
2018-10-09 19:30 | 11.92 | 11.91
2018-10-09 20:00 | 11.7 | 11.69
2018-10-09 20:30 | 11.57 | 11.57
2018-10-09 21:00 | 10.89 | 10.88
2018-10-09 21:30 | 9.67 | 9.67
2018-10-09 22:00 | 8.87 | 8.87
2018-10-09 22:30 | 8.15 | 8.14
2018-10-09 23:00 | 7.76 | 7.74
2018-10-09 23:30 | 6.87 | 6.85
2018-10-10 | 5.98 | 5.95
2018-10-10 00:30 | 5.27 | 5.23
2018-10-10 01:00 | 4.96 | 4.91
2018-10-10 01:30 | 4.69 | 4.64
2018-10-10 02:00 | 4.51 | 4.45
2018-10-10 02:30 | 4.37 | 4.31
2018-10-10 03:00 | 4.26 | 4.2
2018-10-10 03:30 | 4.3 | 4.23
2018-10-10 04:00 | 4.32 | 4.26
2018-10-10 04:30 | 4.5 | 4.44
2018-10-10 05:00 | 4.81 | 4.75
2018-10-10 05:30 | 5.21 | 5.12
2018-10-10 06:00 | 5.51 | 5.4
2018-10-10 06:30 | 5.85 | 5.78
2018-10-10 07:00 | 6.05 | 6
2018-10-10 07:30 | 5.93 | 5.9
2018-10-10 08:00 | 5.29 | 5.26
2018-10-10 08:30 | 4.34 | 4.33
2018-10-10 09:00 | 3.51 | 3.5
2018-10-10 09:30 | 2.98 | 2.95
2018-10-10 10:00 | 2.75 | 2.73
2018-10-10 10:30 | 2.68 | 2.65
2018-10-10 11:00 | 2.71 | 2.68
2018-10-10 11:30 | 3.02 | 2.99
2018-10-10 12:00 | 3.27 | 3.24
2018-10-10 12:30 | 3.75 | 3.72
2018-10-10 13:00 | 3.97 | 3.94
2018-10-10 13:30 | 4.32 | 4.29
2018-10-10 14:00 | 4.86 | 4.84
2018-10-10 14:30 | 5.61 | 5.59
2018-10-10 15:00 | 6.45 | 6.43
2018-10-10 15:30 | 7.41 | 7.38
2018-10-10 16:00 | 9.86 | 9.84
2018-10-10 16:30 | 10.24 | 10.23
2018-10-10 17:00 | 10.98 | 10.97
2018-10-10 17:30 | 11.71 | 11.7
2018-10-10 18:00 | 12.31 | 12.29
2018-10-10 18:30 | 13.26 | 13.23
2018-10-10 19:00 | 13.78 | 13.75
2018-10-10 19:30 | 13.08 | 13.07
2018-10-10 20:00 | 12.56 | 12.55
2018-10-10 20:30 | 12.28 | 12.27
2018-10-10 21:00 | 11.41 | 11.4
2018-10-10 21:30 | 10.52 | 10.52
2018-10-10 22:00 | 9.42 | 9.42
2018-10-10 22:30 | 8.47 | 8.46
2018-10-10 23:00 | 7.87 | 7.86
2018-10-10 23:30 | 6.86 | 6.85
2018-10-11 | 6.06 | 6.04
2018-10-11 00:30 | 5.37 | 5.34
2018-10-11 01:00 | 5.12 | 5.09
2018-10-11 01:30 | 4.93 | 4.89
2018-10-11 02:00 | 4.65 | 4.6
2018-10-11 02:30 | 4.5 | 4.45
2018-10-11 03:00 | 4.35 | 4.3
2018-10-11 03:30 | 4.36 | 4.31
2018-10-11 04:00 | 4.38 | 4.33
2018-10-11 04:30 | 4.55 | 4.51
2018-10-11 05:00 | 4.92 | 4.88
2018-10-11 05:30 | 5.16 | 5.09
2018-10-11 06:00 | 5.59 | 5.51
2018-10-11 06:30 | 6.09 | 6.04
2018-10-11 07:00 | 5.99 | 5.95
2018-10-11 07:30 | 5.87 | 5.84
2018-10-11 08:00 | 5.58 | 5.56
2018-10-11 08:30 | 4.55 | 4.54
2018-10-11 09:00 | 4.11 | 4.11
2018-10-11 09:30 | 3.94 | 3.93
2018-10-11 10:00 | 4.57 | 4.56
2018-10-11 10:30 | 5.35 | 5.35
2018-10-11 11:00 | 6.26 | 6.25
2018-10-11 11:30 | 6.49 | 6.49
2018-10-11 12:00 | 6.83 | 6.82
2018-10-11 12:30 | 8.07 | 8.06
2018-10-11 13:00 | 8.39 | 8.39
2018-10-11 13:30 | 7.18 | 7.17
2018-10-11 14:00 | 4.8 | 4.79
2018-10-11 14:30 | 6.14 | 6.13
2018-10-11 15:00 | 7.05 | 7.04
2018-10-11 15:30 | 7.31 | 7.3
2018-10-11 16:00 | 8.19 | 8.18
2018-10-11 16:30 | 9.19 | 9.18
2018-10-11 17:00 | 9.31 | 9.3
2018-10-11 17:30 | 9.7 | 9.69
2018-10-11 18:00 | 10.38 | 10.38
2018-10-11 18:30 | 11.26 | 11.25
2018-10-11 19:00 | 12.03 | 12.02
2018-10-11 19:30 | 11.66 | 11.66
2018-10-11 20:00 | 11.72 | 11.72
2018-10-11 20:30 | 11.68 | 11.68
2018-10-11 21:00 | 10.93 | 10.93
2018-10-11 21:30 | 10.22 | 10.22
2018-10-11 22:00 | 9.4 | 9.4
2018-10-11 22:30 | 8.52 | 8.51
2018-10-11 23:00 | 7.92 | 7.9
2018-10-11 23:30 | 6.92 | 6.89
2018-10-12 | 6.1 | 6.06
2018-10-12 00:30 | 5.32 | 5.27
2018-10-12 01:00 | 5.02 | 4.98
2018-10-12 01:30 | 4.72 | 4.66
2018-10-12 02:00 | 4.33 | 4.27
2018-10-12 02:30 | 4.24 | 4.17
2018-10-12 03:00 | 4.21 | 4.14
2018-10-12 03:30 | 4.29 | 4.22
2018-10-12 04:00 | 4.29 | 4.23
2018-10-12 04:30 | 4.48 | 4.43
2018-10-12 05:00 | 4.77 | 4.72
2018-10-12 05:30 | 5.18 | 5.11
2018-10-12 06:00 | 5.94 | 5.87
2018-10-12 06:30 | 6.14 | 6.09
2018-10-12 07:00 | 6.09 | 6.05
2018-10-12 07:30 | 7.08 | 7.06
2018-10-12 08:00 | 6.93 | 6.91
2018-10-12 08:30 | 7.11 | 7.1
2018-10-12 09:00 | 6.2 | 6.18
2018-10-12 09:30 | 6.23 | 6.22
2018-10-12 10:00 | 6.62 | 6.6
2018-10-12 10:30 | 5.2 | 5.18
2018-10-12 11:00 | 5.12 | 5.09
2018-10-12 11:30 | 5.35 | 5.31
2018-10-12 12:00 | 6.5 | 6.47
2018-10-12 12:30 | 6.16 | 6.13
2018-10-12 13:00 | 5.5 | 5.47
2018-10-12 13:30 | 5.98 | 5.94
2018-10-12 14:00 | 7.17 | 7.14
2018-10-12 14:30 | 7.09 | 7.06
2018-10-12 15:00 | 7.08 | 7.05
2018-10-12 15:30 | 7.09 | 7.06
2018-10-12 16:00 | 7.73 | 7.71
2018-10-12 16:30 | 8.66 | 8.64
2018-10-12 17:00 | 9.22 | 9.21
2018-10-12 17:30 | 9.77 | 9.76
2018-10-12 18:00 | 10.26 | 10.25
2018-10-12 18:30 | 10.85 | 10.84
2018-10-12 19:00 | 11.21 | 11.2
2018-10-12 19:30 | 10.95 | 10.94
2018-10-12 20:00 | 10.93 | 10.93
2018-10-12 20:30 | 10.87 | 10.86
2018-10-12 21:00 | 10.3 | 10.29
2018-10-12 21:30 | 9.56 | 9.55
2018-10-12 22:00 | 9.02 | 9.01
2018-10-12 22:30 | 8.49 | 8.47
2018-10-12 23:00 | 8.21 | 8.19
2018-10-12 23:30 | 7.5 | 7.48
2018-10-13 | 6.63 | 6.6
2018-10-13 00:30 | 5.87 | 5.83
2018-10-13 01:00 | 5.55 | 5.5
2018-10-13 01:30 | 5.11 | 5.06
2018-10-13 02:00 | 4.77 | 4.71
2018-10-13 02:30 | 4.45 | 4.38
2018-10-13 03:00 | 4.33 | 4.26
2018-10-13 03:30 | 4.21 | 4.14
2018-10-13 04:00 | 4.22 | 4.15
2018-10-13 04:30 | 4.35 | 4.28
2018-10-13 05:00 | 4.43 | 4.36
2018-10-13 05:30 | 4.43 | 4.32
2018-10-13 06:00 | 4.61 | 4.48
2018-10-13 06:30 | 4.69 | 4.56
2018-10-13 07:00 | 5.18 | 5.08
2018-10-13 07:30 | 5.38 | 5.29
2018-10-13 08:00 | 5.76 | 5.68
2018-10-13 08:30 | 6.4 | 6.33
2018-10-13 09:00 | 7.48 | 7.43
2018-10-13 09:30 | 8.19 | 8.16
2018-10-13 10:00 | 8.84 | 8.81
2018-10-13 10:30 | 7.89 | 7.86
2018-10-13 11:00 | 7.73 | 7.7
2018-10-13 11:30 | 7.7 | 7.67
2018-10-13 12:00 | 7.54 | 7.51
2018-10-13 12:30 | 6.93 | 6.9
2018-10-13 13:00 | 7.11 | 7.08
2018-10-13 13:30 | 7.42 | 7.39
2018-10-13 14:00 | 7.6 | 7.58
2018-10-13 14:30 | 7.34 | 7.31
2018-10-13 15:00 | 7.43 | 7.4
2018-10-13 15:30 | 7.6 | 7.57
2018-10-13 16:00 | 8.11 | 8.08
2018-10-13 16:30 | 9.15 | 9.13
2018-10-13 17:00 | 9.17 | 9.15
2018-10-13 17:30 | 9.72 | 9.7
2018-10-13 18:00 | 10.26 | 10.25
2018-10-13 18:30 | 10.78 | 10.77
2018-10-13 19:00 | 11.06 | 11.05
2018-10-13 19:30 | 10.86 | 10.85
2018-10-13 20:00 | 10.68 | 10.67
2018-10-13 20:30 | 10.5 | 10.49
2018-10-13 21:00 | 9.93 | 9.92
2018-10-13 21:30 | 9.36 | 9.35
2018-10-13 22:00 | 8.84 | 8.82
2018-10-13 22:30 | 8.31 | 8.3
2018-10-13 23:00 | 8.24 | 8.22
2018-10-13 23:30 | 7.45 | 7.42
2018-10-14 | 6.67 | 6.64
2018-10-14 00:30 | 5.91 | 5.87
2018-10-14 01:00 | 5.45 | 5.4
2018-10-14 01:30 | 5.01 | 4.96
2018-10-14 02:00 | 4.68 | 4.61
2018-10-14 02:30 | 4.52 | 4.46
2018-10-14 03:00 | 4.39 | 4.33
2018-10-14 03:30 | 4.35 | 4.28
2018-10-14 04:00 | 4.29 | 4.22
2018-10-14 04:30 | 4.36 | 4.29
2018-10-14 05:00 | 4.44 | 4.37
2018-10-14 05:30 | 4.42 | 4.32
2018-10-14 06:00 | 4.37 | 4.22
2018-10-14 06:30 | 4.43 | 4.28
2018-10-14 07:00 | 4.56 | 4.42
2018-10-14 07:30 | 4.81 | 4.71
2018-10-14 08:00 | 5.28 | 5.19
2018-10-14 08:30 | 6.25 | 6.18
2018-10-14 09:00 | 6.49 | 6.45
2018-10-14 09:30 | 6.9 | 6.86
2018-10-14 10:00 | 7.8 | 7.77
2018-10-14 10:30 | 8.05 | 8.02
2018-10-14 11:00 | 7.05 | 7.03
2018-10-14 11:30 | 7.91 | 7.89
2018-10-14 12:00 | 8.98 | 8.97
2018-10-14 12:30 | 9.07 | 9.05
2018-10-14 13:00 | 9.08 | 9.06
2018-10-14 13:30 | 8.49 | 8.47
2018-10-14 14:00 | 8.53 | 8.51
2018-10-14 14:30 | 8.65 | 8.63
2018-10-14 15:00 | 7.97 | 7.95
2018-10-14 15:30 | 8.06 | 8.03
2018-10-14 16:00 | 8.74 | 8.71
2018-10-14 16:30 | 9.43 | 9.41
2018-10-14 17:00 | 10.17 | 10.15
2018-10-14 17:30 | 10.83 | 10.82
2018-10-14 18:00 | 11.47 | 11.46
2018-10-14 18:30 | 12.18 | 12.17
2018-10-14 19:00 | 12.39 | 12.38
2018-10-14 19:30 | 11.9 | 11.9
2018-10-14 20:00 | 11.6 | 11.59
2018-10-14 20:30 | 11.3 | 11.3
2018-10-14 21:00 | 10.76 | 10.76
2018-10-14 21:30 | 9.88 | 9.87
2018-10-14 22:00 | 9.12 | 9.11
2018-10-14 22:30 | 8.46 | 8.44
2018-10-14 23:00 | 8 | 7.98
2018-10-14 23:30 | 7.12 | 7.09
2018-10-15 | 6.15 | 6.11
2018-10-15 00:30 | 5.35 | 5.31
2018-10-15 01:00 | 5.1 | 5.05
2018-10-15 01:30 | 4.74 | 4.68
2018-10-15 02:00 | 4.56 | 4.5
2018-10-15 02:30 | 4.36 | 4.29
2018-10-15 03:00 | 4.18 | 4.11
2018-10-15 03:30 | 4.23 | 4.16
2018-10-15 04:00 | 4.35 | 4.28
2018-10-15 04:30 | 4.43 | 4.37
2018-10-15 05:00 | 4.7 | 4.65
2018-10-15 05:30 | 5.16 | 5.1
2018-10-15 06:00 | 5.51 | 5.41
2018-10-15 06:30 | 6.17 | 6.1
2018-10-15 07:00 | 6.51 | 6.45
2018-10-15 07:30 | 7.38 | 7.35
2018-10-15 08:00 | 7.32 | 7.3
2018-10-15 08:30 | 6.63 | 6.6
2018-10-15 09:00 | 7.14 | 7.12
2018-10-15 09:30 | 5.97 | 5.94
2018-10-15 10:00 | 6.41 | 6.38
2018-10-15 10:30 | 6.3 | 6.28
2018-10-15 11:00 | 5.76 | 5.73
2018-10-15 11:30 | 6.43 | 6.4
2018-10-15 12:00 | 7.36 | 7.34
2018-10-15 12:30 | 7.29 | 7.27
2018-10-15 13:00 | 6.53 | 6.51
2018-10-15 13:30 | 5.74 | 5.72
2018-10-15 14:00 | 6.45 | 6.43
2018-10-15 14:30 | 6.04 | 6.02
2018-10-15 15:00 | 7.06 | 7.04
2018-10-15 15:30 | 6.39 | 6.37
2018-10-15 16:00 | 6.84 | 6.82
2018-10-15 16:30 | 7.96 | 7.95
2018-10-15 17:00 | 8.94 | 8.93
2018-10-15 17:30 | 9.68 | 9.67
2018-10-15 18:00 | 10.94 | 10.93
2018-10-15 18:30 | 12.22 | 12.21
2018-10-15 19:00 | 12.72 | 12.72
2018-10-15 19:30 | 12.11 | 12.11
2018-10-15 20:00 | 11.9 | 11.89
2018-10-15 20:30 | 11.79 | 11.78
2018-10-15 21:00 | 11.12 | 11.11
2018-10-15 21:30 | 10.27 | 10.26
2018-10-15 22:00 | 9.11 | 9.1
2018-10-15 22:30 | 8.42 | 8.4
2018-10-15 23:00 | 8.11 | 8.09
2018-10-15 23:30 | 7.11 | 7.09
2018-10-16 | 6.2 | 6.16
2018-10-16 00:30 | 5.45 | 5.4
2018-10-16 01:00 | 5.01 | 4.96
2018-10-16 01:30 | 4.71 | 4.65
2018-10-16 02:00 | 4.47 | 4.41
2018-10-16 02:30 | 4.53 | 4.47
2018-10-16 03:00 | 4.24 | 4.17
2018-10-16 03:30 | 4.35 | 4.28
2018-10-16 04:00 | 4.25 | 4.18
2018-10-16 04:30 | 4.52 | 4.46
2018-10-16 05:00 | 4.88 | 4.83
2018-10-16 05:30 | 5.31 | 5.25
2018-10-16 06:00 | 5.54 | 5.45
2018-10-16 06:30 | 6.21 | 6.15
2018-10-16 07:00 | 6.62 | 6.58
2018-10-16 07:30 | 6.68 | 6.65
2018-10-16 08:00 | 6.4 | 6.38
2018-10-16 08:30 | 6.4 | 6.38
2018-10-16 09:00 | 5.83 | 5.81
2018-10-16 09:30 | 4.74 | 4.73
2018-10-16 10:00 | 5.77 | 5.76
2018-10-16 10:30 | 5.05 | 5.04
2018-10-16 11:00 | 6.21 | 6.21
2018-10-16 11:30 | 5.93 | 5.92
2018-10-16 12:00 | 5.31 | 5.3
2018-10-16 12:30 | 5.69 | 5.69
2018-10-16 13:00 | 4.79 | 4.78
2018-10-16 13:30 | 4.12 | 4.11
2018-10-16 14:00 | 5 | 4.99
2018-10-16 14:30 | 5.08 | 5.07
2018-10-16 15:00 | 5.65 | 5.65
2018-10-16 15:30 | 6.41 | 6.4
2018-10-16 16:00 | 8.49 | 8.48
2018-10-16 16:30 | 8.67 | 8.67
2018-10-16 17:00 | 9.85 | 9.85
2018-10-16 17:30 | 11.12 | 11.11
2018-10-16 18:00 | 11.07 | 11.07
2018-10-16 18:30 | 12.3 | 12.29
2018-10-16 19:00 | 12.9 | 12.89
2018-10-16 19:30 | 12.47 | 12.47
2018-10-16 20:00 | 12.17 | 12.17
2018-10-16 20:30 | 12.18 | 12.17
2018-10-16 21:00 | 11.51 | 11.51
2018-10-16 21:30 | 10.55 | 10.55
2018-10-16 22:00 | 9.75 | 9.74
2018-10-16 22:30 | 8.59 | 8.58
2018-10-16 23:00 | 8.1 | 8.09
2018-10-16 23:30 | 7.12 | 7.1
2018-10-17 | 6.18 | 6.15
2018-10-17 00:30 | 5.44 | 5.4
2018-10-17 01:00 | 5.11 | 5.07
2018-10-17 01:30 | 4.78 | 4.73
2018-10-17 02:00 | 4.48 | 4.41
2018-10-17 02:30 | 4.35 | 4.29
2018-10-17 03:00 | 4.27 | 4.21
2018-10-17 03:30 | 4.27 | 4.2
2018-10-17 04:00 | 4.32 | 4.26
2018-10-17 04:30 | 4.49 | 4.43
2018-10-17 05:00 | 4.78 | 4.73
2018-10-17 05:30 | 5.16 | 5.08
2018-10-17 06:00 | 5.63 | 5.55
2018-10-17 06:30 | 5.79 | 5.74
2018-10-17 07:00 | 6.41 | 6.38
2018-10-17 07:30 | 6.42 | 6.4
2018-10-17 08:00 | 6.45 | 6.44
2018-10-17 08:30 | 6.52 | 6.51
2018-10-17 09:00 | 5.68 | 5.67
2018-10-17 09:30 | 5.69 | 5.69
2018-10-17 10:00 | 5.31 | 5.3
2018-10-17 10:30 | 5.51 | 5.5
2018-10-17 11:00 | 5.19 | 5.18
2018-10-17 11:30 | 4.62 | 4.61
2018-10-17 12:00 | 4.9 | 4.88
2018-10-17 12:30 | 4.79 | 4.78
2018-10-17 13:00 | 5.64 | 5.62
2018-10-17 13:30 | 4.61 | 4.59
2018-10-17 14:00 | 4.44 | 4.42
2018-10-17 14:30 | 4.78 | 4.76
2018-10-17 15:00 | 5.41 | 5.39
2018-10-17 15:30 | 6.42 | 6.4
2018-10-17 16:00 | 7.47 | 7.45
2018-10-17 16:30 | 8.22 | 8.2
2018-10-17 17:00 | 9.18 | 9.16
2018-10-17 17:30 | 9.8 | 9.78
2018-10-17 18:00 | 10.34 | 10.32
2018-10-17 18:30 | 11.46 | 11.44
2018-10-17 19:00 | 12.32 | 12.3
2018-10-17 19:30 | 12.05 | 12.03
2018-10-17 20:00 | 11.74 | 11.72
2018-10-17 20:30 | 11.61 | 11.6
2018-10-17 21:00 | 10.98 | 10.97
2018-10-17 21:30 | 9.97 | 9.96
2018-10-17 22:00 | 9.11 | 9.1
2018-10-17 22:30 | 8.45 | 8.44
2018-10-17 23:00 | 8.04 | 8.02
2018-10-17 23:30 | 6.98 | 6.95
2018-10-18 | 6.04 | 6.01
2018-10-18 00:30 | 5.34 | 5.3
2018-10-18 01:00 | 5.08 | 5.03
2018-10-18 01:30 | 4.77 | 4.72
2018-10-18 02:00 | 4.43 | 4.37
2018-10-18 02:30 | 4.36 | 4.3
2018-10-18 03:00 | 4.31 | 4.25
2018-10-18 03:30 | 4.33 | 4.27
2018-10-18 04:00 | 4.27 | 4.2
2018-10-18 04:30 | 4.51 | 4.45
2018-10-18 05:00 | 4.82 | 4.78
2018-10-18 05:30 | 5.1 | 5.03
2018-10-18 06:00 | 5.91 | 5.85
2018-10-18 06:30 | 6.32 | 6.28
2018-10-18 07:00 | 7.07 | 7.05
2018-10-18 07:30 | 7.78 | 7.76
2018-10-18 08:00 | 7.11 | 7.1
2018-10-18 08:30 | 5.89 | 5.87
2018-10-18 09:00 | 6.27 | 6.26
2018-10-18 09:30 | 5.45 | 5.44
2018-10-18 10:00 | 5.53 | 5.52
2018-10-18 10:30 | 6.3 | 6.3
2018-10-18 11:00 | 5.58 | 5.57
2018-10-18 11:30 | 6.56 | 6.55
2018-10-18 12:00 | 6.71 | 6.71
2018-10-18 12:30 | 4.53 | 4.52
2018-10-18 13:00 | 3.13 | 3.12
2018-10-18 13:30 | 5.11 | 5.1
2018-10-18 14:00 | 5.55 | 5.54
2018-10-18 14:30 | 6.72 | 6.71
2018-10-18 15:00 | 5.36 | 5.36
2018-10-18 15:30 | 6.29 | 6.28
2018-10-18 16:00 | 6.45 | 6.45
2018-10-18 16:30 | 7.7 | 7.69
2018-10-18 17:00 | 8.97 | 8.97
2018-10-18 17:30 | 9.92 | 9.91
2018-10-18 18:00 | 10.65 | 10.65
2018-10-18 18:30 | 11.6 | 11.6
2018-10-18 19:00 | 12.23 | 12.22
2018-10-18 19:30 | 11.88 | 11.87
2018-10-18 20:00 | 11.89 | 11.89
2018-10-18 20:30 | 11.84 | 11.84
2018-10-18 21:00 | 11.06 | 11.05
2018-10-18 21:30 | 10.23 | 10.23
2018-10-18 22:00 | 9.19 | 9.19
2018-10-18 22:30 | 8.39 | 8.38
2018-10-18 23:00 | 7.95 | 7.93
2018-10-18 23:30 | 7.07 | 7.05
2018-10-19 | 6.11 | 6.08
2018-10-19 00:30 | 5.38 | 5.34
2018-10-19 01:00 | 5.14 | 5.09
2018-10-19 01:30 | 4.84 | 4.79
2018-10-19 02:00 | 4.67 | 4.61
2018-10-19 02:30 | 4.72 | 4.65
2018-10-19 03:00 | 4.64 | 4.56
2018-10-19 03:30 | 4.7 | 4.63
2018-10-19 04:00 | 4.42 | 4.36
2018-10-19 04:30 | 4.49 | 4.42
2018-10-19 05:00 | 4.75 | 4.69
2018-10-19 05:30 | 4.99 | 4.88
2018-10-19 06:00 | 5.08 | 4.96
2018-10-19 06:30 | 5.13 | 5.04
2018-10-19 07:00 | 5.57 | 5.51
2018-10-19 07:30 | 6.14 | 6.1
2018-10-19 08:00 | 5.08 | 5.05
2018-10-19 08:30 | 4.53 | 4.51
2018-10-19 09:00 | 3.64 | 3.62
2018-10-19 09:30 | 3.22 | 3.2
2018-10-19 10:00 | 3.33 | 3.29
2018-10-19 10:30 | 3.1 | 3.06
2018-10-19 11:00 | 3.7 | 3.67
2018-10-19 11:30 | 5.5 | 5.49
2018-10-19 12:00 | 4.42 | 4.4
2018-10-19 12:30 | 5.53 | 5.51
2018-10-19 13:00 | 6 | 5.98
2018-10-19 13:30 | 6.18 | 6.17
2018-10-19 14:00 | 5.61 | 5.6
2018-10-19 14:30 | 4.16 | 4.14
2018-10-19 15:00 | 4.73 | 4.71
2018-10-19 15:30 | 5.28 | 5.26
2018-10-19 16:00 | 6.53 | 6.51
2018-10-19 16:30 | 7.18 | 7.17
2018-10-19 17:00 | 8.21 | 8.2
2018-10-19 17:30 | 8.94 | 8.92
2018-10-19 18:00 | 9.37 | 9.35
2018-10-19 18:30 | 10.13 | 10.12
2018-10-19 19:00 | 10.85 | 10.84
2018-10-19 19:30 | 10.77 | 10.76
2018-10-19 20:00 | 10.74 | 10.73
2018-10-19 20:30 | 10.54 | 10.53
2018-10-19 21:00 | 9.93 | 9.92
2018-10-19 21:30 | 9.14 | 9.14
2018-10-19 22:00 | 8.53 | 8.52
2018-10-19 22:30 | 8.22 | 8.2
2018-10-19 23:00 | 8.1 | 8.08
2018-10-19 23:30 | 7.19 | 7.17
2018-10-20 | 6.36 | 6.33
2018-10-20 00:30 | 5.66 | 5.63
2018-10-20 01:00 | 5.34 | 5.3
2018-10-20 01:30 | 4.87 | 4.82
2018-10-20 02:00 | 4.6 | 4.54
2018-10-20 02:30 | 4.5 | 4.44
2018-10-20 03:00 | 4.42 | 4.36
2018-10-20 03:30 | 4.36 | 4.29
2018-10-20 04:00 | 4.26 | 4.19
2018-10-20 04:30 | 4.28 | 4.22
2018-10-20 05:00 | 4.41 | 4.33
2018-10-20 05:30 | 4.45 | 4.32
2018-10-20 06:00 | 4.35 | 4.21
2018-10-20 06:30 | 4.35 | 4.22
2018-10-20 07:00 | 4.1 | 3.99
2018-10-20 07:30 | 4.09 | 4.01
2018-10-20 08:00 | 4.58 | 4.53
2018-10-20 08:30 | 5.09 | 5.06
2018-10-20 09:00 | 5.43 | 5.41
2018-10-20 09:30 | 6.3 | 6.27
2018-10-20 10:00 | 6 | 5.98
2018-10-20 10:30 | 5.27 | 5.24
2018-10-20 11:00 | 4.41 | 4.37
2018-10-20 11:30 | 4.12 | 4.06
2018-10-20 12:00 | 4.2 | 4.14
2018-10-20 12:30 | 3.79 | 3.71
2018-10-20 13:00 | 4.58 | 4.51
2018-10-20 13:30 | 4.54 | 4.47
2018-10-20 14:00 | 4.99 | 4.93
2018-10-20 14:30 | 5.51 | 5.46
2018-10-20 15:00 | 6.05 | 6.01
2018-10-20 15:30 | 6.83 | 6.8
2018-10-20 16:00 | 7.58 | 7.56
2018-10-20 16:30 | 8.42 | 8.4
2018-10-20 17:00 | 9.1 | 9.08
2018-10-20 17:30 | 9.54 | 9.52
2018-10-20 18:00 | 9.93 | 9.91
2018-10-20 18:30 | 10.42 | 10.41
2018-10-20 19:00 | 10.88 | 10.87
2018-10-20 19:30 | 10.51 | 10.5
2018-10-20 20:00 | 10.38 | 10.37
2018-10-20 20:30 | 10.25 | 10.24
2018-10-20 21:00 | 9.58 | 9.57
2018-10-20 21:30 | 8.99 | 8.99
2018-10-20 22:00 | 8.42 | 8.41
2018-10-20 22:30 | 8.09 | 8.08
2018-10-20 23:00 | 7.99 | 7.97
2018-10-20 23:30 | 7.05 | 7.03
2018-10-21 | 6.17 | 6.15
2018-10-21 00:30 | 5.57 | 5.53
2018-10-21 01:00 | 5.3 | 5.26
2018-10-21 01:30 | 4.97 | 4.92
2018-10-21 02:00 | 4.65 | 4.6
2018-10-21 02:30 | 4.59 | 4.53
2018-10-21 03:00 | 4.47 | 4.42
2018-10-21 03:30 | 4.39 | 4.33
2018-10-21 04:00 | 4.52 | 4.45
2018-10-21 04:30 | 4.24 | 4.17
2018-10-21 05:00 | 4.36 | 4.3
2018-10-21 05:30 | 4.33 | 4.24
2018-10-21 06:00 | 4.32 | 4.17
2018-10-21 06:30 | 4.25 | 4.1
2018-10-21 07:00 | 3.9 | 3.75
2018-10-21 07:30 | 4.78 | 4.69
2018-10-21 08:00 | 5.04 | 4.98
2018-10-21 08:30 | 4.35 | 4.3
2018-10-21 09:00 | 4.19 | 4.16
2018-10-21 09:30 | 4.03 | 3.99
2018-10-21 10:00 | 3.91 | 3.87
2018-10-21 10:30 | 4.79 | 4.76
2018-10-21 11:00 | 5.4 | 5.36
2018-10-21 11:30 | 4.79 | 4.73
2018-10-21 12:00 | 6.18 | 6.14
2018-10-21 12:30 | 6.93 | 6.9
2018-10-21 13:00 | 6.52 | 6.48
2018-10-21 13:30 | 7.35 | 7.32
2018-10-21 14:00 | 9.58 | 9.55
2018-10-21 14:30 | 10.38 | 10.36
2018-10-21 15:00 | 10.74 | 10.73
2018-10-21 15:30 | 10.28 | 10.27
2018-10-21 16:00 | 9.99 | 9.98
2018-10-21 16:30 | 9.58 | 9.57
2018-10-21 17:00 | 8.88 | 8.87
2018-10-21 17:30 | 9.19 | 9.17
2018-10-21 18:00 | 10.17 | 10.16
2018-10-21 18:30 | 10.95 | 10.94
2018-10-21 19:00 | 11.55 | 11.54
2018-10-21 19:30 | 11.06 | 11.06
2018-10-21 20:00 | 10.8 | 10.79
2018-10-21 20:30 | 10.56 | 10.55
2018-10-21 21:00 | 9.87 | 9.86
2018-10-21 21:30 | 9.18 | 9.17
2018-10-21 22:00 | 8.64 | 8.62
2018-10-21 22:30 | 8.01 | 7.99
2018-10-21 23:00 | 7.77 | 7.75
2018-10-21 23:30 | 6.84 | 6.81
2018-10-22 | 6.03 | 5.99
2018-10-22 00:30 | 5.32 | 5.27
2018-10-22 01:00 | 4.96 | 4.91
2018-10-22 01:30 | 4.61 | 4.53
2018-10-22 02:00 | 4.38 | 4.3
2018-10-22 02:30 | 4.28 | 4.2
2018-10-22 03:00 | 4.27 | 4.19
2018-10-22 03:30 | 4.33 | 4.26
2018-10-22 04:00 | 4.29 | 4.22
2018-10-22 04:30 | 4.48 | 4.41
2018-10-22 05:00 | 4.79 | 4.72
2018-10-22 05:30 | 4.99 | 4.88
2018-10-22 06:00 | 5.28 | 5.17
2018-10-22 06:30 | 5.63 | 5.55
2018-10-22 07:00 | 5.84 | 5.78
2018-10-22 07:30 | 5.74 | 5.69
2018-10-22 08:00 | 4.99 | 4.94
2018-10-22 08:30 | 4.15 | 4.12
2018-10-22 09:00 | 3.56 | 3.53
2018-10-22 09:30 | 3.24 | 3.23
2018-10-22 10:00 | 3.18 | 3.17
2018-10-22 10:30 | 3.44 | 3.43
2018-10-22 11:00 | 4.11 | 4.1
2018-10-22 11:30 | 3.8 | 3.78
2018-10-22 12:00 | 4.17 | 4.15
2018-10-22 12:30 | 4.72 | 4.7
2018-10-22 13:00 | 4.77 | 4.75
2018-10-22 13:30 | 5.2 | 5.18
2018-10-22 14:00 | 5.17 | 5.15
2018-10-22 14:30 | 6.97 | 6.96
2018-10-22 15:00 | 6.35 | 6.34
2018-10-22 15:30 | 8.26 | 8.24
2018-10-22 16:00 | 7.76 | 7.75
2018-10-22 16:30 | 8.43 | 8.42
2018-10-22 17:00 | 9.54 | 9.53
2018-10-22 17:30 | 10.44 | 10.44
2018-10-22 18:00 | 11.05 | 11.04
2018-10-22 18:30 | 12.13 | 12.12
2018-10-22 19:00 | 13.06 | 13.06
2018-10-22 19:30 | 12.66 | 12.65
2018-10-22 20:00 | 12.28 | 12.28
2018-10-22 20:30 | 12.17 | 12.17
2018-10-22 21:00 | 11.37 | 11.36
2018-10-22 21:30 | 10.36 | 10.35
2018-10-22 22:00 | 9.33 | 9.33
2018-10-22 22:30 | 8.37 | 8.36
2018-10-22 23:00 | 7.91 | 7.9
2018-10-22 23:30 | 6.8 | 6.77
2018-10-23 | 5.91 | 5.88
2018-10-23 00:30 | 5.34 | 5.29
2018-10-23 01:00 | 5.01 | 4.96
2018-10-23 01:30 | 4.77 | 4.72
2018-10-23 02:00 | 4.49 | 4.42
2018-10-23 02:30 | 4.39 | 4.33
2018-10-23 03:00 | 4.27 | 4.2
2018-10-23 03:30 | 4.35 | 4.28
2018-10-23 04:00 | 4.38 | 4.3
2018-10-23 04:30 | 4.51 | 4.44
2018-10-23 05:00 | 4.68 | 4.61
2018-10-23 05:30 | 4.98 | 4.87
2018-10-23 06:00 | 5.29 | 5.18
2018-10-23 06:30 | 5.57 | 5.49
2018-10-23 07:00 | 5.69 | 5.64
2018-10-23 07:30 | 5.48 | 5.44
2018-10-23 08:00 | 4.95 | 4.92
2018-10-23 08:30 | 4.22 | 4.2
2018-10-23 09:00 | 3.73 | 3.72
2018-10-23 09:30 | 3.36 | 3.35
2018-10-23 10:00 | 3.01 | 2.99
2018-10-23 10:30 | 2.95 | 2.93
2018-10-23 11:00 | 3.1 | 3.06
2018-10-23 11:30 | 3.29 | 3.26
2018-10-23 12:00 | 3.69 | 3.66
2018-10-23 12:30 | 4.12 | 4.09
2018-10-23 13:00 | 4.48 | 4.46
2018-10-23 13:30 | 5.08 | 5.05
2018-10-23 14:00 | 6.02 | 6
2018-10-23 14:30 | 7.08 | 7.06
2018-10-23 15:00 | 6.89 | 6.87
2018-10-23 15:30 | 7.66 | 7.64
2018-10-23 16:00 | 8.88 | 8.87
2018-10-23 16:30 | 9.72 | 9.7
2018-10-23 17:00 | 10.99 | 10.98
2018-10-23 17:30 | 11.57 | 11.56
2018-10-23 18:00 | 12.23 | 12.22
2018-10-23 18:30 | 12.97 | 12.95
2018-10-23 19:00 | 13.7 | 13.67
2018-10-23 19:30 | 13.36 | 13.34
2018-10-23 20:00 | 13.13 | 13.12
2018-10-23 20:30 | 12.73 | 12.72
2018-10-23 21:00 | 11.94 | 11.93
2018-10-23 21:30 | 10.9 | 10.89
2018-10-23 22:00 | 9.86 | 9.85
2018-10-23 22:30 | 8.81 | 8.81
2018-10-23 23:00 | 8.21 | 8.2
2018-10-23 23:30 | 7.16 | 7.14
2018-10-24 | 6.26 | 6.23
2018-10-24 00:30 | 5.63 | 5.61
2018-10-24 01:00 | 5.39 | 5.36
2018-10-24 01:30 | 5.02 | 4.98
2018-10-24 02:00 | 4.7 | 4.66
2018-10-24 02:30 | 4.67 | 4.62
2018-10-24 03:00 | 4.58 | 4.53
2018-10-24 03:30 | 4.51 | 4.46
2018-10-24 04:00 | 4.49 | 4.43
2018-10-24 04:30 | 4.67 | 4.62
2018-10-24 05:00 | 4.85 | 4.78
2018-10-24 05:30 | 5.23 | 5.14
2018-10-24 06:00 | 5.59 | 5.51
2018-10-24 06:30 | 6.1 | 6.05
2018-10-24 07:00 | 6.22 | 6.18
2018-10-24 07:30 | 6.16 | 6.13
2018-10-24 08:00 | 5.37 | 5.35
2018-10-24 08:30 | 5.38 | 5.37
2018-10-24 09:00 | 4.44 | 4.42
2018-10-24 09:30 | 3.78 | 3.76
2018-10-24 10:00 | 3.33 | 3.3
2018-10-24 10:30 | 3.26 | 3.23
2018-10-24 11:00 | 3.5 | 3.46
2018-10-24 11:30 | 4 | 3.97
2018-10-24 12:00 | 4.37 | 4.34
2018-10-24 12:30 | 4.98 | 4.94
2018-10-24 13:00 | 5.62 | 5.57
2018-10-24 13:30 | 6.12 | 6.07
2018-10-24 14:00 | 7.69 | 7.64
2018-10-24 14:30 | 8.35 | 8.31
2018-10-24 15:00 | 9.27 | 9.23
2018-10-24 15:30 | 10.15 | 10.11
2018-10-24 16:00 | 11.45 | 11.42
2018-10-24 16:30 | 12.13 | 12.1
2018-10-24 17:00 | 12.48 | 12.45
2018-10-24 17:30 | 12.8 | 12.78
2018-10-24 18:00 | 13.29 | 13.27
2018-10-24 18:30 | 13.93 | 13.89
2018-10-24 19:00 | 14.54 | 14.5
2018-10-24 19:30 | 14.12 | 14.09
2018-10-24 20:00 | 13.73 | 13.7
2018-10-24 20:30 | 13.36 | 13.34
2018-10-24 21:00 | 12.36 | 12.35
2018-10-24 21:30 | 11.35 | 11.34
2018-10-24 22:00 | 9.97 | 9.96
2018-10-24 22:30 | 9.07 | 9.06
2018-10-24 23:00 | 8.59 | 8.58
2018-10-24 23:30 | 7.51 | 7.5
2018-10-25 | 6.6 | 6.59
2018-10-25 00:30 | 5.97 | 5.94
2018-10-25 01:00 | 5.72 | 5.69
2018-10-25 01:30 | 5.35 | 5.32
2018-10-25 02:00 | 5.1 | 5.06
2018-10-25 02:30 | 4.92 | 4.89
2018-10-25 03:00 | 4.81 | 4.77
2018-10-25 03:30 | 4.77 | 4.72
2018-10-25 04:00 | 4.69 | 4.65
2018-10-25 04:30 | 4.81 | 4.76
2018-10-25 05:00 | 5.04 | 4.98
2018-10-25 05:30 | 5.31 | 5.23
2018-10-25 06:00 | 5.65 | 5.56
2018-10-25 06:30 | 5.77 | 5.71
2018-10-25 07:00 | 5.66 | 5.61
2018-10-25 07:30 | 6.19 | 6.17
2018-10-25 08:00 | 5.51 | 5.49
2018-10-25 08:30 | 5.37 | 5.35
2018-10-25 09:00 | 5.26 | 5.25
2018-10-25 09:30 | 4.51 | 4.48
2018-10-25 10:00 | 4.98 | 4.96
2018-10-25 10:30 | 5.95 | 5.93
2018-10-25 11:00 | 5.22 | 5.2
2018-10-25 11:30 | 4.68 | 4.64
2018-10-25 12:00 | 4.58 | 4.54
2018-10-25 12:30 | 4.65 | 4.62
2018-10-25 13:00 | 5.32 | 5.27
2018-10-25 13:30 | 5.53 | 5.49
2018-10-25 14:00 | 6.57 | 6.53
2018-10-25 14:30 | 6.62 | 6.59
2018-10-25 15:00 | 7.31 | 7.28
2018-10-25 15:30 | 8.11 | 8.09
2018-10-25 16:00 | 9.08 | 9.05
2018-10-25 16:30 | 10.22 | 10.19
2018-10-25 17:00 | 11.2 | 11.18
2018-10-25 17:30 | 11.81 | 11.79
2018-10-25 18:00 | 11.94 | 11.92
2018-10-25 18:30 | 12.77 | 12.75
2018-10-25 19:00 | 13.39 | 13.36
2018-10-25 19:30 | 12.92 | 12.91
2018-10-25 20:00 | 12.5 | 12.49
2018-10-25 20:30 | 12.25 | 12.24
2018-10-25 21:00 | 11.48 | 11.47
2018-10-25 21:30 | 10.56 | 10.55
2018-10-25 22:00 | 9.48 | 9.48
2018-10-25 22:30 | 8.77 | 8.76
2018-10-25 23:00 | 8.36 | 8.35
2018-10-25 23:30 | 7.36 | 7.34
2018-10-26 | 6.4 | 6.38
2018-10-26 00:30 | 5.84 | 5.82
2018-10-26 01:00 | 5.52 | 5.49
2018-10-26 01:30 | 5.27 | 5.24
2018-10-26 02:00 | 4.97 | 4.92
2018-10-26 02:30 | 4.8 | 4.75
2018-10-26 03:00 | 4.69 | 4.64
2018-10-26 03:30 | 4.71 | 4.66
2018-10-26 04:00 | 4.69 | 4.63
2018-10-26 04:30 | 4.77 | 4.71
2018-10-26 05:00 | 5.02 | 4.96
2018-10-26 05:30 | 5.33 | 5.24
2018-10-26 06:00 | 5.52 | 5.43
2018-10-26 06:30 | 5.71 | 5.64
2018-10-26 07:00 | 5.99 | 5.95
2018-10-26 07:30 | 6.13 | 6.12
2018-10-26 08:00 | 5.73 | 5.72
2018-10-26 08:30 | 5.03 | 5.03
2018-10-26 09:00 | 4.69 | 4.68
2018-10-26 09:30 | 4.85 | 4.84
2018-10-26 10:00 | 4.6 | 4.58
2018-10-26 10:30 | 4.55 | 4.52
2018-10-26 11:00 | 4.86 | 4.81
2018-10-26 11:30 | 5.13 | 5.06
2018-10-26 12:00 | 5.52 | 5.46
2018-10-26 12:30 | 6.29 | 6.22
2018-10-26 13:00 | 7 | 6.92
2018-10-26 13:30 | 7.78 | 7.71
2018-10-26 14:00 | 8.78 | 8.71
2018-10-26 14:30 | 9.51 | 9.43
2018-10-26 15:00 | 10.5 | 10.42
2018-10-26 15:30 | 11.67 | 11.59
2018-10-26 16:00 | 13 | 12.92
2018-10-26 16:30 | 14.06 | 13.98
2018-10-26 17:00 | 14.78 | 14.71
2018-10-26 17:30 | 14.92 | 14.85
2018-10-26 18:00 | 14.02 | 13.98
2018-10-26 18:30 | 13.66 | 13.62
2018-10-26 19:00 | 13.98 | 13.93
2018-10-26 19:30 | 13.39 | 13.36
2018-10-26 20:00 | 12.87 | 12.84
2018-10-26 20:30 | 12.39 | 12.37
2018-10-26 21:00 | 11.59 | 11.57
2018-10-26 21:30 | 10.56 | 10.54
2018-10-26 22:00 | 9.77 | 9.76
2018-10-26 22:30 | 9.39 | 9.38
2018-10-26 23:00 | 9.01 | 9
2018-10-26 23:30 | 7.85 | 7.84
2018-10-27 | 6.9 | 6.89
2018-10-27 00:30 | 6.24 | 6.22
2018-10-27 01:00 | 6.01 | 5.99
2018-10-27 01:30 | 5.54 | 5.51
2018-10-27 02:00 | 5.15 | 5.11
2018-10-27 02:30 | 5 | 4.96
2018-10-27 03:00 | 4.92 | 4.88
2018-10-27 03:30 | 4.83 | 4.79
2018-10-27 04:00 | 4.7 | 4.65
2018-10-27 04:30 | 4.68 | 4.62
2018-10-27 05:00 | 4.66 | 4.58
2018-10-27 05:30 | 4.76 | 4.64
2018-10-27 06:00 | 4.61 | 4.47
2018-10-27 06:30 | 4.54 | 4.43
2018-10-27 07:00 | 4.35 | 4.25
2018-10-27 07:30 | 4.56 | 4.51
2018-10-27 08:00 | 4.54 | 4.51
2018-10-27 08:30 | 4.48 | 4.45
2018-10-27 09:00 | 4.62 | 4.58
2018-10-27 09:30 | 5.09 | 5.05
2018-10-27 10:00 | 5.16 | 5.12
2018-10-27 10:30 | 5 | 4.95
2018-10-27 11:00 | 5.14 | 5.08
2018-10-27 11:30 | 5.36 | 5.3
2018-10-27 12:00 | 5.62 | 5.57
2018-10-27 12:30 | 5.99 | 5.94
2018-10-27 13:00 | 6.7 | 6.64
2018-10-27 13:30 | 7.43 | 7.38
2018-10-27 14:00 | 7.84 | 7.79
2018-10-27 14:30 | 8.19 | 8.14
2018-10-27 15:00 | 8.47 | 8.43
2018-10-27 15:30 | 9.15 | 9.11
2018-10-27 16:00 | 9.77 | 9.74
2018-10-27 16:30 | 10.57 | 10.54
2018-10-27 17:00 | 10.96 | 10.94
2018-10-27 17:30 | 10.91 | 10.89
2018-10-27 18:00 | 10.79 | 10.77
2018-10-27 18:30 | 11 | 10.99
2018-10-27 19:00 | 11.44 | 11.43
2018-10-27 19:30 | 11.16 | 11.15
2018-10-27 20:00 | 11.02 | 11
2018-10-27 20:30 | 10.71 | 10.7
2018-10-27 21:00 | 9.89 | 9.88
2018-10-27 21:30 | 9.25 | 9.24
2018-10-27 22:00 | 8.76 | 8.75
2018-10-27 22:30 | 8.57 | 8.57
2018-10-27 23:00 | 8.4 | 8.39
2018-10-27 23:30 | 7.54 | 7.53
2018-10-28 | 6.7 | 6.68
2018-10-28 00:30 | 6.07 | 6.05
2018-10-28 01:00 | 5.72 | 5.69
2018-10-28 01:30 | 5.37 | 5.34
2018-10-28 02:00 | 5.01 | 4.97
2018-10-28 02:30 | 4.86 | 4.82
2018-10-28 03:00 | 4.84 | 4.8
2018-10-28 03:30 | 4.72 | 4.66
2018-10-28 04:00 | 4.63 | 4.57
2018-10-28 04:30 | 4.56 | 4.5
2018-10-28 05:00 | 4.51 | 4.44
2018-10-28 05:30 | 4.44 | 4.31
2018-10-28 06:00 | 4.38 | 4.24
2018-10-28 06:30 | 4.18 | 4.05
2018-10-28 07:00 | 4.43 | 4.31
2018-10-28 07:30 | 4.95 | 4.87
2018-10-28 08:00 | 5.35 | 5.29
2018-10-28 08:30 | 6.2 | 6.16
2018-10-28 09:00 | 6.47 | 6.44
2018-10-28 09:30 | 6.76 | 6.74
2018-10-28 10:00 | 7.42 | 7.4
2018-10-28 10:30 | 3.92 | 3.87
2018-10-28 11:00 | 3.91 | 3.86
2018-10-28 11:30 | 4.4 | 4.34
2018-10-28 12:00 | 4.74 | 4.68
2018-10-28 12:30 | 5.27 | 5.21
2018-10-28 13:00 | 6.05 | 5.99
2018-10-28 13:30 | 6.69 | 6.64
2018-10-28 14:00 | 7.48 | 7.44
2018-10-28 14:30 | 7.92 | 7.88
2018-10-28 15:00 | 8.65 | 8.6
2018-10-28 15:30 | 10.1 | 10.06
2018-10-28 16:00 | 10.67 | 10.64
2018-10-28 16:30 | 11.18 | 11.15
2018-10-28 17:00 | 11.64 | 11.62
2018-10-28 17:30 | 12.07 | 12.05
2018-10-28 18:00 | 12.15 | 12.13
2018-10-28 18:30 | 12.47 | 12.46
2018-10-28 19:00 | 12.74 | 12.73
2018-10-28 19:30 | 12.01 | 12
2018-10-28 20:00 | 11.71 | 11.71
2018-10-28 20:30 | 11.41 | 11.41
2018-10-28 21:00 | 10.63 | 10.62
2018-10-28 21:30 | 9.86 | 9.85
2018-10-28 22:00 | 9.04 | 9.03
2018-10-28 22:30 | 8.37 | 8.36
2018-10-28 23:00 | 8.04 | 8.03
2018-10-28 23:30 | 7.1 | 7.08
2018-10-29 | 6.22 | 6.19
2018-10-29 00:30 | 5.54 | 5.51
2018-10-29 01:00 | 5.36 | 5.32
2018-10-29 01:30 | 5 | 4.96
2018-10-29 02:00 | 4.79 | 4.74
2018-10-29 02:30 | 4.71 | 4.67
2018-10-29 03:00 | 4.64 | 4.59
2018-10-29 03:30 | 4.63 | 4.57
2018-10-29 04:00 | 4.59 | 4.54
2018-10-29 04:30 | 4.79 | 4.74
2018-10-29 05:00 | 5 | 4.96
2018-10-29 05:30 | 5.29 | 5.21
2018-10-29 06:00 | 5.63 | 5.56
2018-10-29 06:30 | 6.11 | 6.05
2018-10-29 07:00 | 6.28 | 6.24
2018-10-29 07:30 | 6.73 | 6.7
2018-10-29 08:00 | 6.83 | 6.81
2018-10-29 08:30 | 5.74 | 5.71
2018-10-29 09:00 | 6.09 | 6.07
2018-10-29 09:30 | 5.65 | 5.63
2018-10-29 10:00 | 6.12 | 6.11
2018-10-29 10:30 | 6.12 | 6.1
2018-10-29 11:00 | 6.37 | 6.35
2018-10-29 11:30 | 6.99 | 6.98
2018-10-29 12:00 | 6.94 | 6.93
2018-10-29 12:30 | 7.3 | 7.28
2018-10-29 13:00 | 7.55 | 7.53
2018-10-29 13:30 | 7.53 | 7.52
2018-10-29 14:00 | 7.1 | 7.09
2018-10-29 14:30 | 7.17 | 7.15
2018-10-29 15:00 | 7.64 | 7.63
2018-10-29 15:30 | 8.04 | 8.03
2018-10-29 16:00 | 9.14 | 9.13
2018-10-29 16:30 | 9.7 | 9.69
2018-10-29 17:00 | 10.26 | 10.25
2018-10-29 17:30 | 10.91 | 10.91
2018-10-29 18:00 | 11.43 | 11.43
2018-10-29 18:30 | 11.82 | 11.81
2018-10-29 19:00 | 12.27 | 12.27
2018-10-29 19:30 | 11.96 | 11.96
2018-10-29 20:00 | 11.81 | 11.8
2018-10-29 20:30 | 11.61 | 11.6
2018-10-29 21:00 | 10.77 | 10.77
2018-10-29 21:30 | 9.54 | 9.53
2018-10-29 22:00 | 8.49 | 8.47
2018-10-29 22:30 | 7.98 | 7.97
2018-10-29 23:00 | 7.87 | 7.85
2018-10-29 23:30 | 6.97 | 6.94
2018-10-30 | 6.06 | 6.02
2018-10-30 00:30 | 5.34 | 5.29
2018-10-30 01:00 | 5.06 | 5.01
2018-10-30 01:30 | 4.76 | 4.7
2018-10-30 02:00 | 4.56 | 4.49
2018-10-30 02:30 | 4.49 | 4.42
2018-10-30 03:00 | 4.36 | 4.28
2018-10-30 03:30 | 4.42 | 4.35
2018-10-30 04:00 | 4.48 | 4.41
2018-10-30 04:30 | 4.69 | 4.63
2018-10-30 05:00 | 4.97 | 4.89
2018-10-30 05:30 | 5.13 | 5.01
2018-10-30 06:00 | 5.53 | 5.41
2018-10-30 06:30 | 5.65 | 5.56
2018-10-30 07:00 | 5.33 | 5.25
2018-10-30 07:30 | 5.19 | 5.13
2018-10-30 08:00 | 4.35 | 4.3
2018-10-30 08:30 | 3.74 | 3.7
2018-10-30 09:00 | 4.33 | 4.31
2018-10-30 09:30 | 4.29 | 4.27
2018-10-30 10:00 | 4.44 | 4.42
2018-10-30 10:30 | 4.14 | 4.12
2018-10-30 11:00 | 3.92 | 3.9
2018-10-30 11:30 | 3.97 | 3.95
2018-10-30 12:00 | 4.5 | 4.47
2018-10-30 12:30 | 4.9 | 4.87
2018-10-30 13:00 | 4.52 | 4.5
2018-10-30 13:30 | 4.88 | 4.86
2018-10-30 14:00 | 5.16 | 5.15
2018-10-30 14:30 | 4.63 | 4.62
2018-10-30 15:00 | 5.27 | 5.26
2018-10-30 15:30 | 5.55 | 5.54
2018-10-30 16:00 | 6.08 | 6.07
2018-10-30 16:30 | 7.3 | 7.29
2018-10-30 17:00 | 8.66 | 8.65
2018-10-30 17:30 | 9.34 | 9.33
2018-10-30 18:00 | 10.4 | 10.4
2018-10-30 18:30 | 11.24 | 11.24
2018-10-30 19:00 | 12.26 | 12.26
2018-10-30 19:30 | 11.96 | 11.95
2018-10-30 20:00 | 11.93 | 11.93
2018-10-30 20:30 | 11.76 | 11.76
2018-10-30 21:00 | 10.98 | 10.98
2018-10-30 21:30 | 9.73 | 9.72
2018-10-30 22:00 | 8.77 | 8.76
2018-10-30 22:30 | 8.2 | 8.18
2018-10-30 23:00 | 7.78 | 7.76
2018-10-30 23:30 | 6.98 | 6.95
2018-10-31 | 6.16 | 6.12
2018-10-31 00:30 | 5.5 | 5.45
2018-10-31 01:00 | 5.13 | 5.07
2018-10-31 01:30 | 4.78 | 4.72
2018-10-31 02:00 | 4.61 | 4.55
2018-10-31 02:30 | 4.51 | 4.44
2018-10-31 03:00 | 4.41 | 4.33
2018-10-31 03:30 | 4.43 | 4.36
2018-10-31 04:00 | 4.52 | 4.44
2018-10-31 04:30 | 4.71 | 4.64
2018-10-31 05:00 | 4.83 | 4.73
2018-10-31 05:30 | 5.22 | 5.1
2018-10-31 06:00 | 5.42 | 5.3
2018-10-31 06:30 | 5.37 | 5.28
2018-10-31 07:00 | 5.01 | 4.93
2018-10-31 07:30 | 4.89 | 4.83
2018-10-31 08:00 | 4.14 | 4.1
2018-10-31 08:30 | 3.26 | 3.23
2018-10-31 09:00 | 2.71 | 2.67
2018-10-31 09:30 | 2.91 | 2.88
2018-10-31 10:00 | 2.61 | 2.58
2018-10-31 10:30 | 2.46 | 2.43
2018-10-31 11:00 | 2.52 | 2.46
2018-10-31 11:30 | 2.57 | 2.51
2018-10-31 12:00 | 2.62 | 2.57
2018-10-31 12:30 | 2.89 | 2.84
2018-10-31 13:00 | 3.35 | 3.3
2018-10-31 13:30 | 3.76 | 3.72
2018-10-31 14:00 | 4.6 | 4.56
2018-10-31 14:30 | 5.48 | 5.45
2018-10-31 15:00 | 6.33 | 6.31
2018-10-31 15:30 | 7.57 | 7.54
2018-10-31 16:00 | 8.52 | 8.5
2018-10-31 16:30 | 9.98 | 9.96
2018-10-31 17:00 | 10.82 | 10.81
2018-10-31 17:30 | 11.1 | 11.09
2018-10-31 18:00 | 11.06 | 11.04
2018-10-31 18:30 | 11.65 | 11.64
2018-10-31 19:00 | 12.45 | 12.43
2018-10-31 19:30 | 12.33 | 12.31
2018-10-31 20:00 | 12.3 | 12.29
2018-10-31 20:30 | 11.97 | 11.97
2018-10-31 21:00 | 10.87 | 10.86
2018-10-31 21:30 | 9.93 | 9.92
2018-10-31 22:00 | 9.03 | 9.02
2018-10-31 22:30 | 8.39 | 8.38
2018-10-31 23:00 | 8 | 7.99
2018-10-31 23:30 | 7.04 | 7.02
2018-11-01 | 6.1 | 6.08
2018-11-01 00:30 | 5.46 | 5.42
2018-11-01 01:00 | 5.22 | 5.18
2018-11-01 01:30 | 4.94 | 4.89
2018-11-01 02:00 | 4.65 | 4.59
2018-11-01 02:30 | 4.64 | 4.58
2018-11-01 03:00 | 4.49 | 4.43
2018-11-01 03:30 | 4.47 | 4.41
2018-11-01 04:00 | 4.47 | 4.39
2018-11-01 04:30 | 4.63 | 4.56
2018-11-01 05:00 | 4.71 | 4.62
2018-11-01 05:30 | 5.08 | 4.96
2018-11-01 06:00 | 5.14 | 5.02
2018-11-01 06:30 | 5.08 | 4.99
2018-11-01 07:00 | 5.16 | 5.09
2018-11-01 07:30 | 4.96 | 4.92
2018-11-01 08:00 | 4.87 | 4.86
2018-11-01 08:30 | 4.23 | 4.22
2018-11-01 09:00 | 4.16 | 4.15
2018-11-01 09:30 | 3.68 | 3.66
2018-11-01 10:00 | 3.67 | 3.66
2018-11-01 10:30 | 3.52 | 3.5
2018-11-01 11:00 | 3.6 | 3.58
2018-11-01 11:30 | 3.53 | 3.51
2018-11-01 12:00 | 3.91 | 3.88
2018-11-01 12:30 | 4.29 | 4.26
2018-11-01 13:00 | 4.6 | 4.57
2018-11-01 13:30 | 5.01 | 4.97
2018-11-01 14:00 | 5.38 | 5.35
2018-11-01 14:30 | 5.97 | 5.94
2018-11-01 15:00 | 6.65 | 6.62
2018-11-01 15:30 | 7.46 | 7.43
2018-11-01 16:00 | 8.31 | 8.29
2018-11-01 16:30 | 9.37 | 9.35
2018-11-01 17:00 | 10.46 | 10.45
2018-11-01 17:30 | 11.09 | 11.08
2018-11-01 18:00 | 11.53 | 11.52
2018-11-01 18:30 | 11.89 | 11.87
2018-11-01 19:00 | 12.92 | 12.9
2018-11-01 19:30 | 12.39 | 12.38
2018-11-01 20:00 | 12.35 | 12.35
2018-11-01 20:30 | 11.95 | 11.95
2018-11-01 21:00 | 10.99 | 10.99
2018-11-01 21:30 | 9.7 | 9.69
2018-11-01 22:00 | 8.73 | 8.72
2018-11-01 22:30 | 8.3 | 8.29
2018-11-01 23:00 | 8.07 | 8.06
2018-11-01 23:30 | 6.95 | 6.92
2018-11-02 | 6.05 | 6.01
2018-11-02 00:30 | 5.47 | 5.43
2018-11-02 01:00 | 5.25 | 5.21
2018-11-02 01:30 | 4.93 | 4.88
2018-11-02 02:00 | 4.66 | 4.6
2018-11-02 02:30 | 4.44 | 4.37
2018-11-02 03:00 | 4.46 | 4.39
2018-11-02 03:30 | 4.45 | 4.37
2018-11-02 04:00 | 4.49 | 4.42
2018-11-02 04:30 | 4.59 | 4.52
2018-11-02 05:00 | 4.78 | 4.69
2018-11-02 05:30 | 5.16 | 5.05
2018-11-02 06:00 | 5.2 | 5.09
2018-11-02 06:30 | 5.61 | 5.54
2018-11-02 07:00 | 5.97 | 5.94
2018-11-02 07:30 | 6.29 | 6.27
2018-11-02 08:00 | 5.18 | 5.17
2018-11-02 08:30 | 4.75 | 4.74
2018-11-02 09:00 | 4.21 | 4.2
2018-11-02 09:30 | 4.23 | 4.22
2018-11-02 10:00 | 3.89 | 3.86
2018-11-02 10:30 | 3.62 | 3.57
2018-11-02 11:00 | 3.11 | 3.06
2018-11-02 11:30 | 3.22 | 3.17
2018-11-02 12:00 | 3.23 | 3.18
2018-11-02 12:30 | 3.58 | 3.54
2018-11-02 13:00 | 3.89 | 3.85
2018-11-02 13:30 | 4.42 | 4.38
2018-11-02 14:00 | 5.04 | 5
2018-11-02 14:30 | 5.51 | 5.48
2018-11-02 15:00 | 6.24 | 6.22
2018-11-02 15:30 | 7.08 | 7.05
2018-11-02 16:00 | 8.29 | 8.27
2018-11-02 16:30 | 9.38 | 9.36
2018-11-02 17:00 | 9.62 | 9.6
2018-11-02 17:30 | 10.21 | 10.19
2018-11-02 18:00 | 10.09 | 10.07
2018-11-02 18:30 | 10.56 | 10.55
2018-11-02 19:00 | 11.46 | 11.44
2018-11-02 19:30 | 11.28 | 11.26
2018-11-02 20:00 | 11.11 | 11.1
2018-11-02 20:30 | 10.99 | 10.98
2018-11-02 21:00 | 10.25 | 10.24
2018-11-02 21:30 | 9.5 | 9.49
2018-11-02 22:00 | 8.82 | 8.81
2018-11-02 22:30 | 8.33 | 8.32
2018-11-02 23:00 | 8.16 | 8.15
2018-11-02 23:30 | 7.24 | 7.22
2018-11-03 | 6.36 | 6.33
2018-11-03 00:30 | 5.76 | 5.72
2018-11-03 01:00 | 5.49 | 5.45
2018-11-03 01:30 | 5.18 | 5.14
2018-11-03 02:00 | 4.83 | 4.78
2018-11-03 02:30 | 4.7 | 4.65
2018-11-03 03:00 | 4.55 | 4.49
2018-11-03 03:30 | 4.45 | 4.38
2018-11-03 04:00 | 4.46 | 4.4
2018-11-03 04:30 | 4.49 | 4.43
2018-11-03 05:00 | 4.39 | 4.28
2018-11-03 05:30 | 4.43 | 4.26
2018-11-03 06:00 | 4.34 | 4.17
2018-11-03 06:30 | 4.03 | 3.88
2018-11-03 07:00 | 4.01 | 3.89
2018-11-03 07:30 | 4.24 | 4.15
2018-11-03 08:00 | 4.5 | 4.45
2018-11-03 08:30 | 4.39 | 4.35
2018-11-03 09:00 | 4.29 | 4.26
2018-11-03 09:30 | 4.35 | 4.32
2018-11-03 10:00 | 4.07 | 4.01
2018-11-03 10:30 | 3.76 | 3.69
2018-11-03 11:00 | 4.05 | 3.99
2018-11-03 11:30 | 4.26 | 4.2
2018-11-03 12:00 | 4.98 | 4.92
2018-11-03 12:30 | 5.07 | 5
2018-11-03 13:00 | 5.76 | 5.68
2018-11-03 13:30 | 6.66 | 6.59
2018-11-03 14:00 | 7.4 | 7.35
2018-11-03 14:30 | 8.39 | 8.34
2018-11-03 15:00 | 9.63 | 9.58
2018-11-03 15:30 | 10.71 | 10.66
2018-11-03 16:00 | 11.87 | 11.82
2018-11-03 16:30 | 12.71 | 12.66
2018-11-03 17:00 | 13.27 | 13.22
2018-11-03 17:30 | 13.19 | 13.15
2018-11-03 18:00 | 12.89 | 12.86
2018-11-03 18:30 | 12.83 | 12.8
2018-11-03 19:00 | 13.3 | 13.26
2018-11-03 19:30 | 12.86 | 12.83
2018-11-03 20:00 | 12.61 | 12.59
2018-11-03 20:30 | 12.06 | 12.04
2018-11-03 21:00 | 11.17 | 11.15
2018-11-03 21:30 | 10.38 | 10.37
2018-11-03 22:00 | 9.61 | 9.6
2018-11-03 22:30 | 9.24 | 9.23
2018-11-03 23:00 | 9.02 | 9.01
2018-11-03 23:30 | 8.04 | 8.03
2018-11-04 | 7.05 | 7.04
2018-11-04 00:30 | 6.29 | 6.27
2018-11-04 01:00 | 6.04 | 6.02
2018-11-04 01:30 | 5.63 | 5.61
2018-11-04 02:00 | 5.34 | 5.32
2018-11-04 02:30 | 5.12 | 5.09
2018-11-04 03:00 | 5.03 | 4.99
2018-11-04 03:30 | 4.94 | 4.9
2018-11-04 04:00 | 4.85 | 4.8
2018-11-04 04:30 | 4.84 | 4.8
2018-11-04 05:00 | 4.73 | 4.66
2018-11-04 05:30 | 4.64 | 4.5
2018-11-04 06:00 | 4.47 | 4.32
2018-11-04 06:30 | 4.34 | 4.21
2018-11-04 07:00 | 4.28 | 4.19
2018-11-04 07:30 | 4.36 | 4.31
2018-11-04 08:00 | 4.39 | 4.36
2018-11-04 08:30 | 4.75 | 4.73
2018-11-04 09:00 | 5.26 | 5.23
2018-11-04 09:30 | 5.67 | 5.64
2018-11-04 10:00 | 6.38 | 6.34
2018-11-04 10:30 | 7.18 | 7.13
2018-11-04 11:00 | 8.1 | 8.05
2018-11-04 11:30 | 9.04 | 8.98
2018-11-04 12:00 | 10.18 | 10.1
2018-11-04 12:30 | 11.32 | 11.21
2018-11-04 13:00 | 12.32 | 12.2
2018-11-04 13:30 | 13.39 | 13.25
2018-11-04 14:00 | 14.3 | 14.15
2018-11-04 14:30 | 15.07 | 14.92
2018-11-04 15:00 | 15.56 | 15.43
2018-11-04 15:30 | 16.13 | 16
2018-11-04 16:00 | 16.73 | 16.61
2018-11-04 16:30 | 17.13 | 17.03
2018-11-04 17:00 | 16.69 | 16.6
2018-11-04 17:30 | 16.41 | 16.33
2018-11-04 18:00 | 16.12 | 16.05
2018-11-04 18:30 | 15.77 | 15.72
2018-11-04 19:00 | 16.11 | 16.05
2018-11-04 19:30 | 15.4 | 15.35
2018-11-04 20:00 | 14.93 | 14.88
2018-11-04 20:30 | 14.11 | 14.08
2018-11-04 21:00 | 13.22 | 13.2
2018-11-04 21:30 | 11.95 | 11.93
2018-11-04 22:00 | 10.9 | 10.88
2018-11-04 22:30 | 10.19 | 10.17
2018-11-04 23:00 | 9.56 | 9.55
2018-11-04 23:30 | 8.42 | 8.41
2018-11-05 | 7.47 | 7.47
2018-11-05 00:30 | 6.7 | 6.69
2018-11-05 01:00 | 6.46 | 6.45
2018-11-05 01:30 | 6.09 | 6.07
2018-11-05 02:00 | 5.79 | 5.78
2018-11-05 02:30 | 5.6 | 5.59
2018-11-05 03:00 | 5.51 | 5.5
2018-11-05 03:30 | 5.52 | 5.5
2018-11-05 04:00 | 5.34 | 5.32
2018-11-05 04:30 | 5.56 | 5.54
2018-11-05 05:00 | 5.6 | 5.57
2018-11-05 05:30 | 5.83 | 5.78
2018-11-05 06:00 | 6.19 | 6.15
2018-11-05 06:30 | 6.51 | 6.48
2018-11-05 07:00 | 6.55 | 6.53
2018-11-05 07:30 | 6.7 | 6.69
2018-11-05 08:00 | 6.94 | 6.93
2018-11-05 08:30 | 7.74 | 7.74
2018-11-05 09:00 | 6.45 | 6.43
2018-11-05 09:30 | 6.63 | 6.59
2018-11-05 10:00 | 7.09 | 7.04
2018-11-05 10:30 | 7.41 | 7.35
2018-11-05 11:00 | 8.12 | 8.05
2018-11-05 11:30 | 8.66 | 8.57
2018-11-05 12:00 | 10.35 | 10.3
2018-11-05 12:30 | 11.21 | 11.11
2018-11-05 13:00 | 12.39 | 12.28
2018-11-05 13:30 | 13.46 | 13.33
2018-11-05 14:00 | 14.38 | 14.25
2018-11-05 14:30 | 15.17 | 15.02
2018-11-05 15:00 | 15.59 | 15.45
2018-11-05 15:30 | 16.38 | 16.24
2018-11-05 16:00 | 17.64 | 17.51
2018-11-05 16:30 | 18.61 | 18.48
2018-11-05 17:00 | 19.5 | 19.38
2018-11-05 17:30 | 19.69 | 19.58
2018-11-05 18:00 | 18.71 | 18.61
2018-11-05 18:30 | 17.93 | 17.83
2018-11-05 19:00 | 18.24 | 18.13
2018-11-05 19:30 | 17.28 | 17.18
2018-11-05 20:00 | 16.68 | 16.61
2018-11-05 20:30 | 15.87 | 15.81
2018-11-05 21:00 | 14.63 | 14.59
2018-11-05 21:30 | 13.28 | 13.25
2018-11-05 22:00 | 11.94 | 11.92
2018-11-05 22:30 | 11.04 | 11.03
2018-11-05 23:00 | 10.27 | 10.26
2018-11-05 23:30 | 9.02 | 9
2018-11-06 | 8.15 | 8.14
2018-11-06 00:30 | 7.36 | 7.35
2018-11-06 01:00 | 7.16 | 7.15
2018-11-06 01:30 | 6.68 | 6.66
2018-11-06 02:00 | 6.43 | 6.42
2018-11-06 02:30 | 6.29 | 6.28
2018-11-06 03:00 | 6.18 | 6.17
2018-11-06 03:30 | 6.07 | 6.06
2018-11-06 04:00 | 6.02 | 6.01
2018-11-06 04:30 | 6.24 | 6.23
2018-11-06 05:00 | 6.35 | 6.34
2018-11-06 05:30 | 6.51 | 6.5
2018-11-06 06:00 | 6.81 | 6.79
2018-11-06 06:30 | 7.08 | 7.07
2018-11-06 07:00 | 7.49 | 7.48
2018-11-06 07:30 | 7.7 | 7.69
2018-11-06 08:00 | 7.76 | 7.75
2018-11-06 08:30 | 6.98 | 6.96
2018-11-06 09:00 | 6.91 | 6.87
2018-11-06 09:30 | 7.2 | 7.14
2018-11-06 10:00 | 8.25 | 8.18
2018-11-06 10:30 | 8.72 | 8.63
2018-11-06 11:00 | 9.6 | 9.49
2018-11-06 11:30 | 10.88 | 10.73
2018-11-06 12:00 | 12.26 | 12.11
2018-11-06 12:30 | 12.37 | 12.22
2018-11-06 13:00 | 13.08 | 12.9
2018-11-06 13:30 | 14.38 | 14.2
2018-11-06 14:00 | 15.57 | 15.38
2018-11-06 14:30 | 15.68 | 15.46
2018-11-06 15:00 | 17.37 | 17.15
2018-11-06 15:30 | 17.76 | 17.55
2018-11-06 16:00 | 19.09 | 18.9
2018-11-06 16:30 | 19.18 | 19
2018-11-06 17:00 | 19.96 | 19.78
2018-11-06 17:30 | 19.88 | 19.71
2018-11-06 18:00 | 19.77 | 19.59
2018-11-06 18:30 | 19.85 | 19.68
2018-11-06 19:00 | 20.1 | 19.91
2018-11-06 19:30 | 19.36 | 19.2
2018-11-06 20:00 | 18.3 | 18.17
2018-11-06 20:30 | 18.19 | 18.08
2018-11-06 21:00 | 17.21 | 17.13
2018-11-06 21:30 | 15.59 | 15.53
2018-11-06 22:00 | 14.38 | 14.34
2018-11-06 22:30 | 12.06 | 12.04
2018-11-06 23:00 | 10.99 | 10.97
2018-11-06 23:30 | 9.94 | 9.93
2018-11-07 | 8.84 | 8.82
2018-11-07 00:30 | 8.24 | 8.22
2018-11-07 01:00 | 8.09 | 8.07
2018-11-07 01:30 | 7.52 | 7.51
2018-11-07 02:00 | 6.91 | 6.89
2018-11-07 02:30 | 6.8 | 6.78
2018-11-07 03:00 | 6.6 | 6.58
2018-11-07 03:30 | 6.5 | 6.48
2018-11-07 04:00 | 6.36 | 6.34
2018-11-07 04:30 | 6.28 | 6.26
2018-11-07 05:00 | 6.28 | 6.26
2018-11-07 05:30 | 6.57 | 6.55
2018-11-07 06:00 | 6.98 | 6.96
2018-11-07 06:30 | 7.33 | 7.32
2018-11-07 07:00 | 7.49 | 7.48
2018-11-07 07:30 | 8.12 | 8.11
2018-11-07 08:00 | 8.4 | 8.38
2018-11-07 08:30 | 8.45 | 8.41
2018-11-07 09:00 | 8.61 | 8.55
2018-11-07 09:30 | 9.04 | 8.95
2018-11-07 10:00 | 9.95 | 9.84
2018-11-07 10:30 | 10.42 | 10.28
2018-11-07 11:00 | 11.01 | 10.84
2018-11-07 11:30 | 11.64 | 11.47
2018-11-07 12:00 | 12.53 | 12.34
2018-11-07 12:30 | 13.66 | 13.42
2018-11-07 13:00 | 14.26 | 14.03
2018-11-07 13:30 | 15 | 14.79
2018-11-07 14:00 | 16.42 | 16.2
2018-11-07 14:30 | 15.34 | 15.12
2018-11-07 15:00 | 16.23 | 16.02
2018-11-07 15:30 | 17.63 | 17.41
2018-11-07 16:00 | 18.92 | 18.68
2018-11-07 16:30 | 19.67 | 19.45
2018-11-07 17:00 | 20.28 | 20.08
2018-11-07 17:30 | 20.35 | 20.16
2018-11-07 18:00 | 20.15 | 19.98
2018-11-07 18:30 | 20.16 | 19.99
2018-11-07 19:00 | 20.59 | 20.4
2018-11-07 19:30 | 19.55 | 19.39
2018-11-07 20:00 | 18.51 | 18.38
2018-11-07 20:30 | 17.46 | 17.36
2018-11-07 21:00 | 16.19 | 16.1
2018-11-07 21:30 | 14.74 | 14.68
2018-11-07 22:00 | 13.14 | 13.1
2018-11-07 22:30 | 11.76 | 11.74
2018-11-07 23:00 | 10.85 | 10.83
2018-11-07 23:30 | 9.38 | 9.37
2018-11-08 | 8.35 | 8.33
2018-11-08 00:30 | 7.69 | 7.67
2018-11-08 01:00 | 7.3 | 7.29
2018-11-08 01:30 | 6.92 | 6.91
2018-11-08 02:00 | 6.66 | 6.65
2018-11-08 02:30 | 6.48 | 6.47
2018-11-08 03:00 | 6.29 | 6.28
2018-11-08 03:30 | 6.31 | 6.29
2018-11-08 04:00 | 6.26 | 6.25
2018-11-08 04:30 | 6.33 | 6.32
2018-11-08 05:00 | 6.38 | 6.37
2018-11-08 05:30 | 6.35 | 6.33
2018-11-08 06:00 | 6.67 | 6.64
2018-11-08 06:30 | 6.67 | 6.65
2018-11-08 07:00 | 7.46 | 7.45
2018-11-08 07:30 | 7.89 | 7.88
2018-11-08 08:00 | 8.43 | 8.43
2018-11-08 08:30 | 8.21 | 8.21
2018-11-08 09:00 | 8 | 7.99
2018-11-08 09:30 | 8.1 | 8.1
2018-11-08 10:00 | 7.76 | 7.76
2018-11-08 10:30 | 7.56 | 7.56
2018-11-08 11:00 | 7.47 | 7.46
2018-11-08 11:30 | 5.92 | 5.91
2018-11-08 12:00 | 5.95 | 5.94
2018-11-08 12:30 | 5.04 | 5.04
2018-11-08 13:00 | 4.53 | 4.53
2018-11-08 13:30 | 5.66 | 5.65
2018-11-08 14:00 | 5.24 | 5.24
2018-11-08 14:30 | 3.7 | 3.69
2018-11-08 15:00 | 4.3 | 4.29
2018-11-08 15:30 | 4.95 | 4.95
2018-11-08 16:00 | 6.36 | 6.35
2018-11-08 16:30 | 7.57 | 7.57
2018-11-08 17:00 | 8.83 | 8.83
2018-11-08 17:30 | 9.72 | 9.72
2018-11-08 18:00 | 10.1 | 10.09
2018-11-08 18:30 | 11 | 11
2018-11-08 19:00 | 12.23 | 12.22
2018-11-08 19:30 | 11.94 | 11.93
2018-11-08 20:00 | 11.84 | 11.84
2018-11-08 20:30 | 11.61 | 11.61
2018-11-08 21:00 | 10.98 | 10.98
2018-11-08 21:30 | 10.12 | 10.11
2018-11-08 22:00 | 9 | 8.99
2018-11-08 22:30 | 8.32 | 8.3
2018-11-08 23:00 | 7.71 | 7.68
2018-11-08 23:30 | 6.71 | 6.68
2018-11-09 | 5.89 | 5.85
2018-11-09 00:30 | 5.24 | 5.2
2018-11-09 01:00 | 5.01 | 4.96
2018-11-09 01:30 | 4.72 | 4.66
2018-11-09 02:00 | 4.58 | 4.52
2018-11-09 02:30 | 4.48 | 4.41
2018-11-09 03:00 | 4.38 | 4.31
2018-11-09 03:30 | 4.38 | 4.31
2018-11-09 04:00 | 4.39 | 4.32
2018-11-09 04:30 | 4.46 | 4.39
2018-11-09 05:00 | 4.66 | 4.54
2018-11-09 05:30 | 4.99 | 4.87
2018-11-09 06:00 | 5.56 | 5.47
2018-11-09 06:30 | 5.59 | 5.53
2018-11-09 07:00 | 5.77 | 5.73
2018-11-09 07:30 | 5.25 | 5.23
2018-11-09 08:00 | 4.73 | 4.71
2018-11-09 08:30 | 3.98 | 3.97
2018-11-09 09:00 | 3.97 | 3.97
2018-11-09 09:30 | 3.58 | 3.57
2018-11-09 10:00 | 3.76 | 3.75
2018-11-09 10:30 | 4.62 | 4.61
2018-11-09 11:00 | 4.18 | 4.16
2018-11-09 11:30 | 3.89 | 3.86
2018-11-09 12:00 | 5.91 | 5.89
2018-11-09 12:30 | 4.08 | 4.06
2018-11-09 13:00 | 2.53 | 2.49
2018-11-09 13:30 | 5.34 | 5.32
2018-11-09 14:00 | 5.27 | 5.26
2018-11-09 14:30 | 4.1 | 4.08
2018-11-09 15:00 | 4.16 | 4.14
2018-11-09 15:30 | 5.28 | 5.26
2018-11-09 16:00 | 5.91 | 5.9
2018-11-09 16:30 | 6.15 | 6.13
2018-11-09 17:00 | 7.65 | 7.63
2018-11-09 17:30 | 8.6 | 8.59
2018-11-09 18:00 | 9.07 | 9.06
2018-11-09 18:30 | 9.44 | 9.43
2018-11-09 19:00 | 10.29 | 10.28
2018-11-09 19:30 | 10.37 | 10.37
2018-11-09 20:00 | 10.2 | 10.19
2018-11-09 20:30 | 10.04 | 10.04
2018-11-09 21:00 | 9.45 | 9.44
2018-11-09 21:30 | 8.78 | 8.77
2018-11-09 22:00 | 8.24 | 8.23
2018-11-09 22:30 | 7.87 | 7.85
2018-11-09 23:00 | 7.7 | 7.68
2018-11-09 23:30 | 6.79 | 6.76
2018-11-10 | 5.98 | 5.94
2018-11-10 00:30 | 5.37 | 5.33
2018-11-10 01:00 | 5.16 | 5.11
2018-11-10 01:30 | 4.88 | 4.82
2018-11-10 02:00 | 4.57 | 4.51
2018-11-10 02:30 | 4.39 | 4.32
2018-11-10 03:00 | 4.37 | 4.29
2018-11-10 03:30 | 4.35 | 4.27
2018-11-10 04:00 | 4.31 | 4.22
2018-11-10 04:30 | 4.28 | 4.19
2018-11-10 05:00 | 4.2 | 4.06
2018-11-10 05:30 | 4.29 | 4.1
2018-11-10 06:00 | 4.2 | 4
2018-11-10 06:30 | 3.93 | 3.76
2018-11-10 07:00 | 3.88 | 3.73
2018-11-10 07:30 | 3.75 | 3.64
2018-11-10 08:00 | 3.6 | 3.51
2018-11-10 08:30 | 3.52 | 3.46
2018-11-10 09:00 | 3.86 | 3.83
2018-11-10 09:30 | 4.06 | 4.02
2018-11-10 10:00 | 4.5 | 4.46
2018-11-10 10:30 | 4.98 | 4.95
2018-11-10 11:00 | 3.45 | 3.4
2018-11-10 11:30 | 4.94 | 4.9
2018-11-10 12:00 | 3.75 | 3.7
2018-11-10 12:30 | 5.07 | 5.04
2018-11-10 13:00 | 5.38 | 5.35
2018-11-10 13:30 | 5.27 | 5.23
2018-11-10 14:00 | 5.19 | 5.14
2018-11-10 14:30 | 5.48 | 5.44
2018-11-10 15:00 | 5.55 | 5.52
2018-11-10 15:30 | 6.18 | 6.15
2018-11-10 16:00 | 7.13 | 7.11
2018-11-10 16:30 | 7.59 | 7.56
2018-11-10 17:00 | 8.65 | 8.64
2018-11-10 17:30 | 8.81 | 8.79
2018-11-10 18:00 | 9.27 | 9.25
2018-11-10 18:30 | 9.54 | 9.53
2018-11-10 19:00 | 10.49 | 10.48
2018-11-10 19:30 | 10.38 | 10.37
2018-11-10 20:00 | 10.23 | 10.22
2018-11-10 20:30 | 9.96 | 9.95
2018-11-10 21:00 | 9.32 | 9.31
2018-11-10 21:30 | 8.81 | 8.81
2018-11-10 22:00 | 8.31 | 8.3
2018-11-10 22:30 | 8.03 | 8.01
2018-11-10 23:00 | 7.88 | 7.86
2018-11-10 23:30 | 6.91 | 6.89
2018-11-11 | 6.11 | 6.08
2018-11-11 00:30 | 5.58 | 5.55
2018-11-11 01:00 | 5.3 | 5.26
2018-11-11 01:30 | 5 | 4.96
2018-11-11 02:00 | 4.81 | 4.76
2018-11-11 02:30 | 4.6 | 4.54
2018-11-11 03:00 | 4.51 | 4.44
2018-11-11 03:30 | 4.46 | 4.4
2018-11-11 04:00 | 4.34 | 4.27
2018-11-11 04:30 | 4.4 | 4.33
2018-11-11 05:00 | 4.25 | 4.12
2018-11-11 05:30 | 4.32 | 4.14
2018-11-11 06:00 | 4.16 | 3.98
2018-11-11 06:30 | 3.86 | 3.69
2018-11-11 07:00 | 3.67 | 3.53
2018-11-11 07:30 | 3.77 | 3.67
2018-11-11 08:00 | 3.88 | 3.81
2018-11-11 08:30 | 3.81 | 3.77
2018-11-11 09:00 | 3.82 | 3.79
2018-11-11 09:30 | 3.86 | 3.83
2018-11-11 10:00 | 4.62 | 4.59
2018-11-11 10:30 | 4.75 | 4.71
2018-11-11 11:00 | 4.47 | 4.43
2018-11-11 11:30 | 4.96 | 4.93
2018-11-11 12:00 | 5.5 | 5.46
2018-11-11 12:30 | 5.76 | 5.72
2018-11-11 13:00 | 5.92 | 5.89
2018-11-11 13:30 | 5.1 | 5.06
2018-11-11 14:00 | 7.76 | 7.74
2018-11-11 14:30 | 6.27 | 6.24
2018-11-11 15:00 | 6.8 | 6.78
2018-11-11 15:30 | 7.02 | 7
2018-11-11 16:00 | 8.05 | 8.03
2018-11-11 16:30 | 8.98 | 8.96
2018-11-11 17:00 | 9.9 | 9.88
2018-11-11 17:30 | 10.51 | 10.49
2018-11-11 18:00 | 10.87 | 10.86
2018-11-11 18:30 | 11.28 | 11.27
2018-11-11 19:00 | 12.07 | 12.06
2018-11-11 19:30 | 11.69 | 11.68
2018-11-11 20:00 | 11.33 | 11.32
2018-11-11 20:30 | 10.97 | 10.96
2018-11-11 21:00 | 10.18 | 10.17
2018-11-11 21:30 | 9.32 | 9.32
2018-11-11 22:00 | 8.59 | 8.58
2018-11-11 22:30 | 8.03 | 8.01
2018-11-11 23:00 | 7.76 | 7.74
2018-11-11 23:30 | 6.87 | 6.84
2018-11-12 | 5.89 | 5.85
2018-11-12 00:30 | 5.3 | 5.24
2018-11-12 01:00 | 5.08 | 5.03
2018-11-12 01:30 | 4.71 | 4.65
2018-11-12 02:00 | 4.61 | 4.55
2018-11-12 02:30 | 4.59 | 4.52
2018-11-12 03:00 | 4.42 | 4.35
2018-11-12 03:30 | 4.49 | 4.41
2018-11-12 04:00 | 4.44 | 4.36
2018-11-12 04:30 | 4.57 | 4.5
2018-11-12 05:00 | 4.7 | 4.58
2018-11-12 05:30 | 5.02 | 4.9
2018-11-12 06:00 | 5.39 | 5.3
2018-11-12 06:30 | 5.69 | 5.63
2018-11-12 07:00 | 5.61 | 5.57
2018-11-12 07:30 | 5.31 | 5.28
2018-11-12 08:00 | 4.85 | 4.84
2018-11-12 08:30 | 3.96 | 3.95
2018-11-12 09:00 | 4.48 | 4.47
2018-11-12 09:30 | 4.39 | 4.39
2018-11-12 10:00 | 4.37 | 4.37
2018-11-12 10:30 | 3.82 | 3.81
2018-11-12 11:00 | 2.81 | 2.79
2018-11-12 11:30 | 3.08 | 3.07
2018-11-12 12:00 | 4.08 | 4.07
2018-11-12 12:30 | 4.24 | 4.23
2018-11-12 13:00 | 4.54 | 4.52
2018-11-12 13:30 | 4.02 | 4
2018-11-12 14:00 | 4.89 | 4.87
2018-11-12 14:30 | 5.7 | 5.68
2018-11-12 15:00 | 7.14 | 7.13
2018-11-12 15:30 | 6.6 | 6.59
2018-11-12 16:00 | 7.65 | 7.64
2018-11-12 16:30 | 8.87 | 8.86
2018-11-12 17:00 | 10.08 | 10.07
2018-11-12 17:30 | 10.75 | 10.75
2018-11-12 18:00 | 11.34 | 11.33
2018-11-12 18:30 | 11.84 | 11.83
2018-11-12 19:00 | 12.83 | 12.82
2018-11-12 19:30 | 12.53 | 12.52
2018-11-12 20:00 | 12.12 | 12.12
2018-11-12 20:30 | 11.86 | 11.86
2018-11-12 21:00 | 10.99 | 10.99
2018-11-12 21:30 | 9.9 | 9.89
2018-11-12 22:00 | 8.69 | 8.68
2018-11-12 22:30 | 7.98 | 7.97
2018-11-12 23:00 | 7.6 | 7.58
2018-11-12 23:30 | 6.67 | 6.65
2018-11-13 | 5.81 | 5.77
2018-11-13 00:30 | 5.2 | 5.15
2018-11-13 01:00 | 5.05 | 4.99
2018-11-13 01:30 | 4.77 | 4.71
2018-11-13 02:00 | 4.53 | 4.46
2018-11-13 02:30 | 4.41 | 4.33
2018-11-13 03:00 | 4.35 | 4.27
2018-11-13 03:30 | 4.43 | 4.34
2018-11-13 04:00 | 4.41 | 4.33
2018-11-13 04:30 | 4.56 | 4.49
2018-11-13 05:00 | 4.73 | 4.6
2018-11-13 05:30 | 5.07 | 4.95
2018-11-13 06:00 | 4.92 | 4.8
2018-11-13 06:30 | 4.83 | 4.72
2018-11-13 07:00 | 5.83 | 5.75
2018-11-13 07:30 | 4.92 | 4.85
2018-11-13 08:00 | 4.16 | 4.1
2018-11-13 08:30 | 3.59 | 3.56
2018-11-13 09:00 | 4.85 | 4.83
2018-11-13 09:30 | 4.87 | 4.85
2018-11-13 10:00 | 4.67 | 4.66
2018-11-13 10:30 | 3.81 | 3.79
2018-11-13 11:00 | 3.3 | 3.27
2018-11-13 11:30 | 4.32 | 4.3
2018-11-13 12:00 | 4.44 | 4.42
2018-11-13 12:30 | 4.46 | 4.45
2018-11-13 13:00 | 4.69 | 4.68
2018-11-13 13:30 | 5.11 | 5.1
2018-11-13 14:00 | 5.16 | 5.15
2018-11-13 14:30 | 5.67 | 5.66
2018-11-13 15:00 | 6.03 | 6.02
2018-11-13 15:30 | 7.2 | 7.19
2018-11-13 16:00 | 8.35 | 8.34
2018-11-13 16:30 | 8.63 | 8.62
2018-11-13 17:00 | 9.39 | 9.39
2018-11-13 17:30 | 10.31 | 10.3
2018-11-13 18:00 | 10.85 | 10.84
2018-11-13 18:30 | 11.7 | 11.7
2018-11-13 19:00 | 12.8 | 12.78
2018-11-13 19:30 | 12.38 | 12.37
2018-11-13 20:00 | 12.23 | 12.22
2018-11-13 20:30 | 11.78 | 11.78
2018-11-13 21:00 | 10.98 | 10.97
2018-11-13 21:30 | 10.14 | 10.14
2018-11-13 22:00 | 9.19 | 9.18
2018-11-13 22:30 | 8.19 | 8.18
2018-11-13 23:00 | 7.69 | 7.67
2018-11-13 23:30 | 6.73 | 6.7
2018-11-14 | 5.9 | 5.86
2018-11-14 00:30 | 5.33 | 5.28
2018-11-14 01:00 | 5.16 | 5.1
2018-11-14 01:30 | 4.82 | 4.76
2018-11-14 02:00 | 4.51 | 4.45
2018-11-14 02:30 | 4.47 | 4.4
2018-11-14 03:00 | 4.37 | 4.29
2018-11-14 03:30 | 4.39 | 4.32
2018-11-14 04:00 | 4.43 | 4.35
2018-11-14 04:30 | 4.61 | 4.54
2018-11-14 05:00 | 4.64 | 4.5
2018-11-14 05:30 | 4.85 | 4.7
2018-11-14 06:00 | 5.22 | 5.11
2018-11-14 06:30 | 5.38 | 5.31
2018-11-14 07:00 | 5.44 | 5.4
2018-11-14 07:30 | 5.61 | 5.59
2018-11-14 08:00 | 4.91 | 4.89
2018-11-14 08:30 | 4.66 | 4.65
2018-11-14 09:00 | 4.79 | 4.79
2018-11-14 09:30 | 5.01 | 5
2018-11-14 10:00 | 4.11 | 4.09
2018-11-14 10:30 | 3.94 | 3.92
2018-11-14 11:00 | 4.63 | 4.62
2018-11-14 11:30 | 5.19 | 5.17
2018-11-14 12:00 | 6.45 | 6.44
2018-11-14 12:30 | 6.61 | 6.6
2018-11-14 13:00 | 6.09 | 6.08
2018-11-14 13:30 | 7.62 | 7.61
2018-11-14 14:00 | 7.72 | 7.71
2018-11-14 14:30 | 6.57 | 6.56
2018-11-14 15:00 | 6.28 | 6.27
2018-11-14 15:30 | 7.37 | 7.36
2018-11-14 16:00 | 8.36 | 8.35
2018-11-14 16:30 | 9.47 | 9.46
2018-11-14 17:00 | 10.39 | 10.38
2018-11-14 17:30 | 11.05 | 11.05
2018-11-14 18:00 | 12.15 | 12.15
2018-11-14 18:30 | 12.85 | 12.84
2018-11-14 19:00 | 13.86 | 13.84
2018-11-14 19:30 | 13.42 | 13.4
2018-11-14 20:00 | 13.21 | 13.19
2018-11-14 20:30 | 12.92 | 12.91
2018-11-14 21:00 | 12.03 | 12.02
2018-11-14 21:30 | 11.05 | 11.04
2018-11-14 22:00 | 9.96 | 9.95
2018-11-14 22:30 | 9.15 | 9.15
2018-11-14 23:00 | 8.74 | 8.73
2018-11-14 23:30 | 7.67 | 7.66
2018-11-15 | 6.87 | 6.86
2018-11-15 00:30 | 6.19 | 6.16
2018-11-15 01:00 | 5.93 | 5.9
2018-11-15 01:30 | 5.65 | 5.61
2018-11-15 02:00 | 5.32 | 5.28
2018-11-15 02:30 | 5.17 | 5.12
2018-11-15 03:00 | 5.01 | 4.95
2018-11-15 03:30 | 5.13 | 5.08
2018-11-15 04:00 | 5.12 | 5.07
2018-11-15 04:30 | 5.24 | 5.19
2018-11-15 05:00 | 5.31 | 5.23
2018-11-15 05:30 | 5.66 | 5.56
2018-11-15 06:00 | 5.96 | 5.87
2018-11-15 06:30 | 6.14 | 6.08
2018-11-15 07:00 | 6.14 | 6.08
2018-11-15 07:30 | 5.62 | 5.58
2018-11-15 08:00 | 5.89 | 5.87
2018-11-15 08:30 | 5.48 | 5.47
2018-11-15 09:00 | 4.82 | 4.81
2018-11-15 09:30 | 4.93 | 4.92
2018-11-15 10:00 | 5.25 | 5.24
2018-11-15 10:30 | 5.18 | 5.17
2018-11-15 11:00 | 5.68 | 5.66
2018-11-15 11:30 | 5.37 | 5.35
2018-11-15 12:00 | 6.06 | 6.02
2018-11-15 12:30 | 6.27 | 6.23
2018-11-15 13:00 | 7.27 | 7.22
2018-11-15 13:30 | 9.37 | 9.34
2018-11-15 14:00 | 8.01 | 7.97
2018-11-15 14:30 | 8.57 | 8.52
2018-11-15 15:00 | 9.48 | 9.44
2018-11-15 15:30 | 10.39 | 10.35
2018-11-15 16:00 | 11.03 | 10.98
2018-11-15 16:30 | 12.11 | 12.06
2018-11-15 17:00 | 12.92 | 12.88
2018-11-15 17:30 | 12.74 | 12.71
2018-11-15 18:00 | 12.82 | 12.8
2018-11-15 18:30 | 13.28 | 13.26
2018-11-15 19:00 | 14.24 | 14.2
2018-11-15 19:30 | 13.96 | 13.93
2018-11-15 20:00 | 13.65 | 13.62
2018-11-15 20:30 | 13.07 | 13.05
2018-11-15 21:00 | 12.25 | 12.24
2018-11-15 21:30 | 11.52 | 11.52
2018-11-15 22:00 | 10.56 | 10.56
2018-11-15 22:30 | 9.47 | 9.46
2018-11-15 23:00 | 8.89 | 8.88
2018-11-15 23:30 | 7.86 | 7.85
2018-11-16 | 7 | 6.99
2018-11-16 00:30 | 6.32 | 6.3
2018-11-16 01:00 | 5.93 | 5.91
2018-11-16 01:30 | 5.69 | 5.66
2018-11-16 02:00 | 5.31 | 5.27
2018-11-16 02:30 | 5.18 | 5.14
2018-11-16 03:00 | 5.03 | 4.98
2018-11-16 03:30 | 5.02 | 4.97
2018-11-16 04:00 | 4.93 | 4.88
2018-11-16 04:30 | 5.1 | 5.05
2018-11-16 05:00 | 5.13 | 5.04
2018-11-16 05:30 | 5.44 | 5.36
2018-11-16 06:00 | 5.8 | 5.74
2018-11-16 06:30 | 6.01 | 5.98
2018-11-16 07:00 | 6.36 | 6.34
2018-11-16 07:30 | 6.58 | 6.57
2018-11-16 08:00 | 6.98 | 6.97
2018-11-16 08:30 | 6.26 | 6.26
2018-11-16 09:00 | 5.36 | 5.35
2018-11-16 09:30 | 5.47 | 5.46
2018-11-16 10:00 | 5.76 | 5.75
2018-11-16 10:30 | 5.17 | 5.15
2018-11-16 11:00 | 5.72 | 5.69
2018-11-16 11:30 | 5.69 | 5.66
2018-11-16 12:00 | 5.93 | 5.9
2018-11-16 12:30 | 6.5 | 6.47
2018-11-16 13:00 | 6.93 | 6.89
2018-11-16 13:30 | 8.28 | 8.23
2018-11-16 14:00 | 8.2 | 8.14
2018-11-16 14:30 | 8.67 | 8.62
2018-11-16 15:00 | 9.13 | 9.08
2018-11-16 15:30 | 9.98 | 9.93
2018-11-16 16:00 | 11.05 | 11
2018-11-16 16:30 | 11.74 | 11.7
2018-11-16 17:00 | 12.52 | 12.47
2018-11-16 17:30 | 12.68 | 12.65
2018-11-16 18:00 | 12.52 | 12.49
2018-11-16 18:30 | 12.43 | 12.41
2018-11-16 19:00 | 12.92 | 12.89
2018-11-16 19:30 | 12.74 | 12.72
2018-11-16 20:00 | 12.57 | 12.56
2018-11-16 20:30 | 11.96 | 11.95
2018-11-16 21:00 | 11.24 | 11.22
2018-11-16 21:30 | 10.39 | 10.39
2018-11-16 22:00 | 9.84 | 9.84
2018-11-16 22:30 | 9.36 | 9.35
2018-11-16 23:00 | 9.01 | 9
2018-11-16 23:30 | 7.99 | 7.98
2018-11-17 | 7.16 | 7.15
2018-11-17 00:30 | 6.47 | 6.46
2018-11-17 01:00 | 6.17 | 6.15
2018-11-17 01:30 | 5.81 | 5.8
2018-11-17 02:00 | 5.42 | 5.4
2018-11-17 02:30 | 5.4 | 5.38
2018-11-17 03:00 | 5.15 | 5.12
2018-11-17 03:30 | 5.09 | 5.06
2018-11-17 04:00 | 4.95 | 4.91
2018-11-17 04:30 | 4.96 | 4.92
2018-11-17 05:00 | 4.78 | 4.7
2018-11-17 05:30 | 4.83 | 4.73
2018-11-17 06:00 | 4.7 | 4.59
2018-11-17 06:30 | 4.45 | 4.37
2018-11-17 07:00 | 4.81 | 4.75
2018-11-17 07:30 | 5.52 | 5.47
2018-11-17 08:00 | 5.61 | 5.58
2018-11-17 08:30 | 6.77 | 6.75
2018-11-17 09:00 | 5.23 | 5.2
2018-11-17 09:30 | 4.77 | 4.72
2018-11-17 10:00 | 5.41 | 5.37
2018-11-17 10:30 | 6.65 | 6.62
2018-11-17 11:00 | 6.38 | 6.33
2018-11-17 11:30 | 6.54 | 6.49
2018-11-17 12:00 | 7.48 | 7.44
2018-11-17 12:30 | 9.03 | 8.99
2018-11-17 13:00 | 8.2 | 8.15
2018-11-17 13:30 | 9.06 | 9.01
2018-11-17 14:00 | 9.82 | 9.76
2018-11-17 14:30 | 11.45 | 11.41
2018-11-17 15:00 | 12.57 | 12.54
2018-11-17 15:30 | 12.22 | 12.19
2018-11-17 16:00 | 12.48 | 12.46
2018-11-17 16:30 | 12.96 | 12.95
2018-11-17 17:00 | 12.76 | 12.75
2018-11-17 17:30 | 12.82 | 12.81
2018-11-17 18:00 | 12.67 | 12.66
2018-11-17 18:30 | 11.77 | 11.76
2018-11-17 19:00 | 11.85 | 11.84
2018-11-17 19:30 | 10.98 | 10.96
2018-11-17 20:00 | 10.68 | 10.67
2018-11-17 20:30 | 10.27 | 10.26
2018-11-17 21:00 | 9.57 | 9.56
2018-11-17 21:30 | 9.03 | 9.02
2018-11-17 22:00 | 8.61 | 8.6
2018-11-17 22:30 | 8.22 | 8.21
2018-11-17 23:00 | 8.08 | 8.07
2018-11-17 23:30 | 7.17 | 7.15
2018-11-18 | 6.41 | 6.39
2018-11-18 00:30 | 5.79 | 5.76
2018-11-18 01:00 | 5.49 | 5.45
2018-11-18 01:30 | 5.2 | 5.16
2018-11-18 02:00 | 5 | 4.95
2018-11-18 02:30 | 4.86 | 4.81
2018-11-18 03:00 | 4.72 | 4.67
2018-11-18 03:30 | 4.59 | 4.53
2018-11-18 04:00 | 4.54 | 4.48
2018-11-18 04:30 | 4.54 | 4.47
2018-11-18 05:00 | 4.43 | 4.32
2018-11-18 05:30 | 4.51 | 4.36
2018-11-18 06:00 | 4.24 | 4.06
2018-11-18 06:30 | 4.32 | 4.17
2018-11-18 07:00 | 4.02 | 3.89
2018-11-18 07:30 | 4.05 | 3.98
2018-11-18 08:00 | 4.17 | 4.12
2018-11-18 08:30 | 5.05 | 5.02
2018-11-18 09:00 | 6.63 | 6.61
2018-11-18 09:30 | 5.54 | 5.52
2018-11-18 10:00 | 5.83 | 5.81
2018-11-18 10:30 | 8.23 | 8.21
2018-11-18 11:00 | 7.24 | 7.22
2018-11-18 11:30 | 6.68 | 6.66
2018-11-18 12:00 | 7.24 | 7.22
2018-11-18 12:30 | 6.67 | 6.65
2018-11-18 13:00 | 8.17 | 8.16
2018-11-18 13:30 | 7.12 | 7.1
2018-11-18 14:00 | 7.31 | 7.29
2018-11-18 14:30 | 6.91 | 6.89
2018-11-18 15:00 | 6.96 | 6.95
2018-11-18 15:30 | 7.76 | 7.74
2018-11-18 16:00 | 7.62 | 7.6
2018-11-18 16:30 | 7.12 | 7.1
2018-11-18 17:00 | 8.44 | 8.43
2018-11-18 17:30 | 9.75 | 9.74
2018-11-18 18:00 | 10.22 | 10.21
2018-11-18 18:30 | 10.72 | 10.72
2018-11-18 19:00 | 11.37 | 11.36
2018-11-18 19:30 | 11.14 | 11.14
2018-11-18 20:00 | 10.97 | 10.96
2018-11-18 20:30 | 10.8 | 10.79
2018-11-18 21:00 | 10.03 | 10.03
2018-11-18 21:30 | 9.23 | 9.22
2018-11-18 22:00 | 8.49 | 8.48
2018-11-18 22:30 | 8.08 | 8.07
2018-11-18 23:00 | 7.65 | 7.63
2018-11-18 23:30 | 6.72 | 6.69
2018-11-19 | 5.9 | 5.86
2018-11-19 00:30 | 5.31 | 5.26
2018-11-19 01:00 | 5.08 | 5.03
2018-11-19 01:30 | 4.81 | 4.75
2018-11-19 02:00 | 4.65 | 4.59
2018-11-19 02:30 | 4.56 | 4.49
2018-11-19 03:00 | 4.48 | 4.41
2018-11-19 03:30 | 4.45 | 4.38
2018-11-19 04:00 | 4.51 | 4.44
2018-11-19 04:30 | 4.64 | 4.58
2018-11-19 05:00 | 4.74 | 4.62
2018-11-19 05:30 | 5.01 | 4.88
2018-11-19 06:00 | 5.15 | 5.03
2018-11-19 06:30 | 5.2 | 5.11
2018-11-19 07:00 | 5.11 | 5.05
2018-11-19 07:30 | 4.86 | 4.82
2018-11-19 08:00 | 4.38 | 4.34
2018-11-19 08:30 | 4.1 | 4.08
2018-11-19 09:00 | 4.74 | 4.74
2018-11-19 09:30 | 3.77 | 3.76
2018-11-19 10:00 | 4.15 | 4.15
2018-11-19 10:30 | 5.1 | 5.1
2018-11-19 11:00 | 4.72 | 4.71
2018-11-19 11:30 | 5.07 | 5.06
2018-11-19 12:00 | 4.33 | 4.32
2018-11-19 12:30 | 4.75 | 4.74
2018-11-19 13:00 | 5.43 | 5.42
2018-11-19 13:30 | 4.79 | 4.78
2018-11-19 14:00 | 5.71 | 5.7
2018-11-19 14:30 | 6.19 | 6.17
2018-11-19 15:00 | 6.32 | 6.31
2018-11-19 15:30 | 6.34 | 6.33
2018-11-19 16:00 | 7.32 | 7.31
2018-11-19 16:30 | 8.19 | 8.18
2018-11-19 17:00 | 9.34 | 9.33
2018-11-19 17:30 | 10.23 | 10.22
2018-11-19 18:00 | 10.89 | 10.89
2018-11-19 18:30 | 11.37 | 11.37
2018-11-19 19:00 | 12.3 | 12.3
2018-11-19 19:30 | 12.43 | 12.42
2018-11-19 20:00 | 12.16 | 12.16
2018-11-19 20:30 | 11.63 | 11.63
2018-11-19 21:00 | 10.84 | 10.84
2018-11-19 21:30 | 9.79 | 9.78
2018-11-19 22:00 | 8.79 | 8.78
2018-11-19 22:30 | 8.04 | 8.02
2018-11-19 23:00 | 7.67 | 7.65
2018-11-19 23:30 | 6.72 | 6.69
2018-11-20 | 5.76 | 5.71
2018-11-20 00:30 | 5.25 | 5.2
2018-11-20 01:00 | 5.02 | 4.97
2018-11-20 01:30 | 4.79 | 4.73
2018-11-20 02:00 | 4.6 | 4.54
2018-11-20 02:30 | 4.51 | 4.45
2018-11-20 03:00 | 4.45 | 4.37
2018-11-20 03:30 | 4.45 | 4.38
2018-11-20 04:00 | 4.48 | 4.4
2018-11-20 04:30 | 4.66 | 4.59
2018-11-20 05:00 | 4.7 | 4.58
2018-11-20 05:30 | 5.02 | 4.9
2018-11-20 06:00 | 5.07 | 4.94
2018-11-20 06:30 | 5.04 | 4.95
2018-11-20 07:00 | 4.84 | 4.75
2018-11-20 07:30 | 5.05 | 5
2018-11-20 08:00 | 4.55 | 4.53
2018-11-20 08:30 | 3.86 | 3.85
2018-11-20 09:00 | 3.71 | 3.7
2018-11-20 09:30 | 3.28 | 3.27
2018-11-20 10:00 | 3.15 | 3.13
2018-11-20 10:30 | 3.32 | 3.31
2018-11-20 11:00 | 3.37 | 3.35
2018-11-20 11:30 | 3.96 | 3.94
2018-11-20 12:00 | 3.78 | 3.76
2018-11-20 12:30 | 4.43 | 4.4
2018-11-20 13:00 | 5.21 | 5.19
2018-11-20 13:30 | 5.52 | 5.49
2018-11-20 14:00 | 5.67 | 5.64
2018-11-20 14:30 | 6.36 | 6.34
2018-11-20 15:00 | 6.81 | 6.78
2018-11-20 15:30 | 7.56 | 7.54
2018-11-20 16:00 | 8.95 | 8.94
2018-11-20 16:30 | 9.58 | 9.57
2018-11-20 17:00 | 10.6 | 10.59
2018-11-20 17:30 | 11.29 | 11.28
2018-11-20 18:00 | 11.76 | 11.76
2018-11-20 18:30 | 12.3 | 12.3
2018-11-20 19:00 | 13.32 | 13.3
2018-11-20 19:30 | 13.24 | 13.23
2018-11-20 20:00 | 12.9 | 12.89
2018-11-20 20:30 | 12.33 | 12.32
2018-11-20 21:00 | 11.53 | 11.53
2018-11-20 21:30 | 10.49 | 10.49
2018-11-20 22:00 | 9.22 | 9.22
2018-11-20 22:30 | 8.46 | 8.46
2018-11-20 23:00 | 8.16 | 8.15
2018-11-20 23:30 | 7.11 | 7.09
2018-11-21 | 6.22 | 6.2
2018-11-21 00:30 | 5.54 | 5.51
2018-11-21 01:00 | 5.32 | 5.28
2018-11-21 01:30 | 5.06 | 5.02
2018-11-21 02:00 | 4.75 | 4.7
2018-11-21 02:30 | 4.61 | 4.55
2018-11-21 03:00 | 4.51 | 4.45
2018-11-21 03:30 | 4.53 | 4.47
2018-11-21 04:00 | 4.58 | 4.53
2018-11-21 04:30 | 4.77 | 4.72
2018-11-21 05:00 | 4.92 | 4.83
2018-11-21 05:30 | 5.17 | 5.08
2018-11-21 06:00 | 5.21 | 5.12
2018-11-21 06:30 | 5.26 | 5.2
2018-11-21 07:00 | 5.35 | 5.31
2018-11-21 07:30 | 5.19 | 5.16
2018-11-21 08:00 | 4.55 | 4.53
2018-11-21 08:30 | 3.77 | 3.75
2018-11-21 09:00 | 3.5 | 3.47
2018-11-21 09:30 | 3.66 | 3.63
2018-11-21 10:00 | 3.58 | 3.54
2018-11-21 10:30 | 3.81 | 3.77
2018-11-21 11:00 | 4.14 | 4.09
2018-11-21 11:30 | 4.69 | 4.64
2018-11-21 12:00 | 5.26 | 5.21
2018-11-21 12:30 | 6.27 | 6.22
2018-11-21 13:00 | 7.9 | 7.83
2018-11-21 13:30 | 8.62 | 8.52
2018-11-21 14:00 | 10.64 | 10.56
2018-11-21 14:30 | 12.14 | 12.07
2018-11-21 15:00 | 11.92 | 11.84
2018-11-21 15:30 | 13.04 | 12.97
2018-11-21 16:00 | 13.77 | 13.7
2018-11-21 16:30 | 14.8 | 14.73
2018-11-21 17:00 | 15.22 | 15.16
2018-11-21 17:30 | 14.67 | 14.62
2018-11-21 18:00 | 15.08 | 15.03
2018-11-21 18:30 | 15.78 | 15.72
2018-11-21 19:00 | 16.49 | 16.41
2018-11-21 19:30 | 16.21 | 16.14
2018-11-21 20:00 | 15.74 | 15.68
2018-11-21 20:30 | 15.19 | 15.14
2018-11-21 21:00 | 14.19 | 14.15
2018-11-21 21:30 | 12.62 | 12.59
2018-11-21 22:00 | 11.29 | 11.28
2018-11-21 22:30 | 10.36 | 10.35
2018-11-21 23:00 | 9.7 | 9.69
2018-11-21 23:30 | 8.46 | 8.45
2018-11-22 | 7.48 | 7.48
2018-11-22 00:30 | 6.84 | 6.83
2018-11-22 01:00 | 6.57 | 6.56
2018-11-22 01:30 | 6.23 | 6.21
2018-11-22 02:00 | 5.88 | 5.86
2018-11-22 02:30 | 5.79 | 5.77
2018-11-22 03:00 | 5.78 | 5.77
2018-11-22 03:30 | 5.58 | 5.57
2018-11-22 04:00 | 5.58 | 5.56
2018-11-22 04:30 | 5.67 | 5.65
2018-11-22 05:00 | 5.81 | 5.78
2018-11-22 05:30 | 6.11 | 6.08
2018-11-22 06:00 | 6.35 | 6.32
2018-11-22 06:30 | 6.79 | 6.77
2018-11-22 07:00 | 7.26 | 7.26
2018-11-22 07:30 | 8.32 | 8.32
2018-11-22 08:00 | 7.09 | 7.09
2018-11-22 08:30 | 7.27 | 7.26
2018-11-22 09:00 | 7.36 | 7.35
2018-11-22 09:30 | 6.52 | 6.5
2018-11-22 10:00 | 6.14 | 6.13
2018-11-22 10:30 | 7.55 | 7.53
2018-11-22 11:00 | 9.83 | 9.82
2018-11-22 11:30 | 9.06 | 9.05
2018-11-22 12:00 | 7.72 | 7.71
2018-11-22 12:30 | 5.61 | 5.6
2018-11-22 13:00 | 4.24 | 4.22
2018-11-22 13:30 | 4.66 | 4.64
2018-11-22 14:00 | 4.64 | 4.61
2018-11-22 14:30 | 5.5 | 5.48
2018-11-22 15:00 | 6.22 | 6.19
2018-11-22 15:30 | 7.53 | 7.51
2018-11-22 16:00 | 9.23 | 9.21
2018-11-22 16:30 | 10.06 | 10.04
2018-11-22 17:00 | 11.2 | 11.19
2018-11-22 17:30 | 12.14 | 12.12
2018-11-22 18:00 | 12.25 | 12.23
2018-11-22 18:30 | 12.75 | 12.73
2018-11-22 19:00 | 13.75 | 13.72
2018-11-22 19:30 | 13.76 | 13.72
2018-11-22 20:00 | 13.45 | 13.43
2018-11-22 20:30 | 12.97 | 12.96
2018-11-22 21:00 | 12.32 | 12.31
2018-11-22 21:30 | 11.39 | 11.39
2018-11-22 22:00 | 10.16 | 10.16
2018-11-22 22:30 | 9.09 | 9.08
2018-11-22 23:00 | 8.56 | 8.55
2018-11-22 23:30 | 7.53 | 7.52
2018-11-23 | 6.61 | 6.58
2018-11-23 00:30 | 5.97 | 5.94
2018-11-23 01:00 | 5.62 | 5.58
2018-11-23 01:30 | 5.23 | 5.18
2018-11-23 02:00 | 4.88 | 4.82
2018-11-23 02:30 | 4.79 | 4.73
2018-11-23 03:00 | 4.75 | 4.68
2018-11-23 03:30 | 4.78 | 4.71
2018-11-23 04:00 | 4.78 | 4.71
2018-11-23 04:30 | 4.8 | 4.73
2018-11-23 05:00 | 4.91 | 4.78
2018-11-23 05:30 | 5.13 | 5
2018-11-23 06:00 | 5.49 | 5.4
2018-11-23 06:30 | 5.54 | 5.48
2018-11-23 07:00 | 5.45 | 5.39
2018-11-23 07:30 | 5.17 | 5.13
2018-11-23 08:00 | 4.68 | 4.65
2018-11-23 08:30 | 3.74 | 3.72
2018-11-23 09:00 | 3.1 | 3.09
2018-11-23 09:30 | 2.58 | 2.56
2018-11-23 10:00 | 3.24 | 3.22
2018-11-23 10:30 | 3.01 | 2.99
2018-11-23 11:00 | 2.61 | 2.57
2018-11-23 11:30 | 2.01 | 1.95
2018-11-23 12:00 | 2.27 | 2.21
2018-11-23 12:30 | 2.4 | 2.34
2018-11-23 13:00 | 2.68 | 2.62
2018-11-23 13:30 | 2.98 | 2.92
2018-11-23 14:00 | 3.62 | 3.58
2018-11-23 14:30 | 4.21 | 4.17
2018-11-23 15:00 | 4.96 | 4.92
2018-11-23 15:30 | 5.82 | 5.8
2018-11-23 16:00 | 7.22 | 7.19
2018-11-23 16:30 | 8.17 | 8.14
2018-11-23 17:00 | 9.05 | 9.03
2018-11-23 17:30 | 9.51 | 9.49
2018-11-23 18:00 | 9.9 | 9.88
2018-11-23 18:30 | 10.14 | 10.12
2018-11-23 19:00 | 10.93 | 10.92
2018-11-23 19:30 | 11.04 | 11.03
2018-11-23 20:00 | 11.09 | 11.09
2018-11-23 20:30 | 10.81 | 10.8
2018-11-23 21:00 | 10.05 | 10.05
2018-11-23 21:30 | 9.37 | 9.36
2018-11-23 22:00 | 8.66 | 8.66
2018-11-23 22:30 | 8.36 | 8.35
2018-11-23 23:00 | 8.16 | 8.15
2018-11-23 23:30 | 7.18 | 7.16
2018-11-24 | 6.41 | 6.38
2018-11-24 00:30 | 5.67 | 5.63
2018-11-24 01:00 | 5.41 | 5.37
2018-11-24 01:30 | 5.11 | 5.06
2018-11-24 02:00 | 4.84 | 4.78
2018-11-24 02:30 | 4.63 | 4.57
2018-11-24 03:00 | 4.52 | 4.45
2018-11-24 03:30 | 4.56 | 4.49
2018-11-24 04:00 | 4.51 | 4.43
2018-11-24 04:30 | 4.55 | 4.48
2018-11-24 05:00 | 4.38 | 4.24
2018-11-24 05:30 | 4.34 | 4.16
2018-11-24 06:00 | 4.28 | 4.12
2018-11-24 06:30 | 3.93 | 3.77
2018-11-24 07:00 | 3.8 | 3.66
2018-11-24 07:30 | 3.76 | 3.66
2018-11-24 08:00 | 3.69 | 3.62
2018-11-24 08:30 | 3.51 | 3.46
2018-11-24 09:00 | 3.24 | 3.2
2018-11-24 09:30 | 3.11 | 3.06
2018-11-24 10:00 | 2.93 | 2.87
2018-11-24 10:30 | 2.66 | 2.59
2018-11-24 11:00 | 2.66 | 2.58
2018-11-24 11:30 | 2.61 | 2.54
2018-11-24 12:00 | 2.72 | 2.63
2018-11-24 12:30 | 2.91 | 2.82
2018-11-24 13:00 | 3.19 | 3.12
2018-11-24 13:30 | 3.67 | 3.6
2018-11-24 14:00 | 4.14 | 4.08
2018-11-24 14:30 | 4.8 | 4.76
2018-11-24 15:00 | 5.57 | 5.53
2018-11-24 15:30 | 6.43 | 6.4
2018-11-24 16:00 | 7.51 | 7.48
2018-11-24 16:30 | 8.49 | 8.47
2018-11-24 17:00 | 9.4 | 9.38
2018-11-24 17:30 | 9.85 | 9.83
2018-11-24 18:00 | 9.96 | 9.95
2018-11-24 18:30 | 10.33 | 10.32
2018-11-24 19:00 | 10.93 | 10.92
2018-11-24 19:30 | 10.91 | 10.9
2018-11-24 20:00 | 10.79 | 10.78
2018-11-24 20:30 | 10.43 | 10.42
2018-11-24 21:00 | 9.7 | 9.69
2018-11-24 21:30 | 9.07 | 9.06
2018-11-24 22:00 | 8.5 | 8.49
2018-11-24 22:30 | 8.22 | 8.2
2018-11-24 23:00 | 7.98 | 7.96
2018-11-24 23:30 | 7.15 | 7.13
2018-11-25 | 6.36 | 6.33
2018-11-25 00:30 | 5.68 | 5.65
2018-11-25 01:00 | 5.31 | 5.27
2018-11-25 01:30 | 5.15 | 5.1
2018-11-25 02:00 | 4.91 | 4.86
2018-11-25 02:30 | 4.77 | 4.72
2018-11-25 03:00 | 4.59 | 4.52
2018-11-25 03:30 | 4.49 | 4.42
2018-11-25 04:00 | 4.39 | 4.31
2018-11-25 04:30 | 4.42 | 4.33
2018-11-25 05:00 | 4.29 | 4.14
2018-11-25 05:30 | 4.25 | 4.06
2018-11-25 06:00 | 4.07 | 3.87
2018-11-25 06:30 | 3.8 | 3.61
2018-11-25 07:00 | 3.8 | 3.66
2018-11-25 07:30 | 3.67 | 3.57
2018-11-25 08:00 | 3.67 | 3.61
2018-11-25 08:30 | 3.75 | 3.71
2018-11-25 09:00 | 4.67 | 4.64
2018-11-25 09:30 | 4.71 | 4.68
2018-11-25 10:00 | 4.1 | 4.05
2018-11-25 10:30 | 4.83 | 4.78
2018-11-25 11:00 | 7.34 | 7.31
2018-11-25 11:30 | 5.36 | 5.32
2018-11-25 12:00 | 5.29 | 5.22
2018-11-25 12:30 | 7.07 | 7.02
2018-11-25 13:00 | 9.54 | 9.5
2018-11-25 13:30 | 9.52 | 9.49
2018-11-25 14:00 | 8.66 | 8.61
2018-11-25 14:30 | 10.02 | 9.98
2018-11-25 15:00 | 10.48 | 10.44
2018-11-25 15:30 | 12.16 | 12.13
2018-11-25 16:00 | 11.09 | 11.06
2018-11-25 16:30 | 12.2 | 12.18
2018-11-25 17:00 | 13.28 | 13.25
2018-11-25 17:30 | 13.81 | 13.79
2018-11-25 18:00 | 13.78 | 13.76
2018-11-25 18:30 | 13.16 | 13.15
2018-11-25 19:00 | 13.46 | 13.44
2018-11-25 19:30 | 13.52 | 13.5
2018-11-25 20:00 | 13.28 | 13.26
2018-11-25 20:30 | 12.73 | 12.72
2018-11-25 21:00 | 11.8 | 11.79
2018-11-25 21:30 | 10.86 | 10.85
2018-11-25 22:00 | 9.99 | 9.98
2018-11-25 22:30 | 9.11 | 9.1
2018-11-25 23:00 | 8.59 | 8.58
2018-11-25 23:30 | 7.58 | 7.57
2018-11-26 | 6.61 | 6.6
2018-11-26 00:30 | 5.89 | 5.86
2018-11-26 01:00 | 5.61 | 5.58
2018-11-26 01:30 | 5.27 | 5.23
2018-11-26 02:00 | 4.97 | 4.92
2018-11-26 02:30 | 4.83 | 4.78
2018-11-26 03:00 | 4.75 | 4.7
2018-11-26 03:30 | 4.8 | 4.74
2018-11-26 04:00 | 4.75 | 4.69
2018-11-26 04:30 | 4.9 | 4.84
2018-11-26 05:00 | 4.99 | 4.88
2018-11-26 05:30 | 5.1 | 4.98
2018-11-26 06:00 | 5.29 | 5.19
2018-11-26 06:30 | 5.29 | 5.21
2018-11-26 07:00 | 5.15 | 5.08
2018-11-26 07:30 | 5.12 | 5.08
2018-11-26 08:00 | 4.92 | 4.9
2018-11-26 08:30 | 4.38 | 4.37
2018-11-26 09:00 | 3.93 | 3.91
2018-11-26 09:30 | 4.08 | 4.07
2018-11-26 10:00 | 4.21 | 4.19
2018-11-26 10:30 | 4.76 | 4.73
2018-11-26 11:00 | 4.68 | 4.65
2018-11-26 11:30 | 4.98 | 4.93
2018-11-26 12:00 | 5.48 | 5.43
2018-11-26 12:30 | 6.1 | 6.05
2018-11-26 13:00 | 6.75 | 6.69
2018-11-26 13:30 | 7.55 | 7.49
2018-11-26 14:00 | 8.4 | 8.33
2018-11-26 14:30 | 9.25 | 9.17
2018-11-26 15:00 | 10.15 | 10.08
2018-11-26 15:30 | 11.45 | 11.37
2018-11-26 16:00 | 13.03 | 12.95
2018-11-26 16:30 | 13.92 | 13.85
2018-11-26 17:00 | 14.7 | 14.62
2018-11-26 17:30 | 14.83 | 14.77
2018-11-26 18:00 | 14.71 | 14.66
2018-11-26 18:30 | 14.54 | 14.51
2018-11-26 19:00 | 14.8 | 14.76
2018-11-26 19:30 | 14.31 | 14.28
2018-11-26 20:00 | 13.83 | 13.81
2018-11-26 20:30 | 13.2 | 13.19
2018-11-26 21:00 | 11.95 | 11.94
2018-11-26 21:30 | 10.81 | 10.8
2018-11-26 22:00 | 9.77 | 9.76
2018-11-26 22:30 | 9.04 | 9.04
2018-11-26 23:00 | 8.43 | 8.42
2018-11-26 23:30 | 7.37 | 7.35
2018-11-27 | 6.4 | 6.37
2018-11-27 00:30 | 5.88 | 5.85
2018-11-27 01:00 | 5.62 | 5.59
2018-11-27 01:30 | 5.26 | 5.22
2018-11-27 02:00 | 5.01 | 4.96
2018-11-27 02:30 | 4.78 | 4.73
2018-11-27 03:00 | 4.79 | 4.73
2018-11-27 03:30 | 4.75 | 4.68
2018-11-27 04:00 | 4.76 | 4.7
2018-11-27 04:30 | 4.88 | 4.82
2018-11-27 05:00 | 4.97 | 4.87
2018-11-27 05:30 | 5.22 | 5.11
2018-11-27 06:00 | 5.18 | 5.08
2018-11-27 06:30 | 5.11 | 5.03
2018-11-27 07:00 | 6.73 | 6.67
2018-11-27 07:30 | 7.16 | 7.12
2018-11-27 08:00 | 7.5 | 7.48
2018-11-27 08:30 | 7.34 | 7.33
2018-11-27 09:00 | 8.13 | 8.13
2018-11-27 09:30 | 7.55 | 7.55
2018-11-27 10:00 | 7.1 | 7.1
2018-11-27 10:30 | 6.73 | 6.73
2018-11-27 11:00 | 7.73 | 7.73
2018-11-27 11:30 | 8.87 | 8.87
2018-11-27 12:00 | 8.36 | 8.36
2018-11-27 12:30 | 8.59 | 8.59
2018-11-27 13:00 | 6.57 | 6.56
2018-11-27 13:30 | 6.75 | 6.75
2018-11-27 14:00 | 7.57 | 7.56
2018-11-27 14:30 | 7.53 | 7.52
2018-11-27 15:00 | 7.58 | 7.57
2018-11-27 15:30 | 8.95 | 8.94
2018-11-27 16:00 | 10.56 | 10.55
2018-11-27 16:30 | 12.33 | 12.32
2018-11-27 17:00 | 13.66 | 13.65
2018-11-27 17:30 | 14.32 | 14.3
2018-11-27 18:00 | 14.62 | 14.6
2018-11-27 18:30 | 14.85 | 14.83
2018-11-27 19:00 | 14.85 | 14.81
2018-11-27 19:30 | 14.74 | 14.7
2018-11-27 20:00 | 14.47 | 14.44
2018-11-27 20:30 | 13.79 | 13.77
2018-11-27 21:00 | 12.97 | 12.95
2018-11-27 21:30 | 11.85 | 11.85
2018-11-27 22:00 | 10.81 | 10.81
2018-11-27 22:30 | 9.87 | 9.86
2018-11-27 23:00 | 9.23 | 9.22
2018-11-27 23:30 | 8.26 | 8.25
2018-11-28 | 7.29 | 7.29
2018-11-28 00:30 | 6.65 | 6.64
2018-11-28 01:00 | 6.37 | 6.36
2018-11-28 01:30 | 5.99 | 5.98
2018-11-28 02:00 | 5.64 | 5.63
2018-11-28 02:30 | 5.49 | 5.47
2018-11-28 03:00 | 5.45 | 5.43
2018-11-28 03:30 | 5.44 | 5.42
2018-11-28 04:00 | 5.49 | 5.47
2018-11-28 04:30 | 5.44 | 5.41
2018-11-28 05:00 | 5.54 | 5.49
2018-11-28 05:30 | 5.94 | 5.89
2018-11-28 06:00 | 6.07 | 6.03
2018-11-28 06:30 | 6.09 | 6.06
2018-11-28 07:00 | 6.21 | 6.19
2018-11-28 07:30 | 6.55 | 6.53
2018-11-28 08:00 | 6.24 | 6.23
2018-11-28 08:30 | 5.9 | 5.87
2018-11-28 09:00 | 5.86 | 5.82
2018-11-28 09:30 | 6.34 | 6.29
2018-11-28 10:00 | 6.88 | 6.82
2018-11-28 10:30 | 7.89 | 7.82
2018-11-28 11:00 | 9.11 | 9.03
2018-11-28 11:30 | 9.32 | 9.2
2018-11-28 12:00 | 10.53 | 10.4
2018-11-28 12:30 | 13.56 | 13.44
2018-11-28 13:00 | 11.18 | 11.03
2018-11-28 13:30 | 11.89 | 11.76
2018-11-28 14:00 | 12.86 | 12.74
2018-11-28 14:30 | 12.7 | 12.56
2018-11-28 15:00 | 14.27 | 14.15
2018-11-28 15:30 | 14.84 | 14.69
2018-11-28 16:00 | 15.74 | 15.58
2018-11-28 16:30 | 16.84 | 16.69
2018-11-28 17:00 | 17.75 | 17.62
2018-11-28 17:30 | 18.16 | 18.04
2018-11-28 18:00 | 18.2 | 18.09
2018-11-28 18:30 | 18.01 | 17.9
2018-11-28 19:00 | 18.33 | 18.21
2018-11-28 19:30 | 17.58 | 17.47
2018-11-28 20:00 | 16.54 | 16.45
2018-11-28 20:30 | 15.7 | 15.62
2018-11-28 21:00 | 14.73 | 14.68
2018-11-28 21:30 | 13.35 | 13.33
2018-11-28 22:00 | 11.68 | 11.67
2018-11-28 22:30 | 10.23 | 10.22
2018-11-28 23:00 | 9.53 | 9.52
2018-11-28 23:30 | 8.22 | 8.21
2018-11-29 | 7.37 | 7.36
2018-11-29 00:30 | 6.73 | 6.72
2018-11-29 01:00 | 6.38 | 6.37
2018-11-29 01:30 | 5.87 | 5.86
2018-11-29 02:00 | 5.71 | 5.7
2018-11-29 02:30 | 5.56 | 5.55
2018-11-29 03:00 | 5.38 | 5.36
2018-11-29 03:30 | 5.33 | 5.3
2018-11-29 04:00 | 5.25 | 5.23
2018-11-29 04:30 | 5.31 | 5.27
2018-11-29 05:00 | 5.23 | 5.16
2018-11-29 05:30 | 5.48 | 5.4
2018-11-29 06:00 | 5.88 | 5.83
2018-11-29 06:30 | 6.03 | 6
2018-11-29 07:00 | 6.16 | 6.14
2018-11-29 07:30 | 6.17 | 6.16
2018-11-29 08:00 | 5.87 | 5.87
2018-11-29 08:30 | 5.28 | 5.27
2018-11-29 09:00 | 4.86 | 4.84
2018-11-29 09:30 | 4.85 | 4.82
2018-11-29 10:00 | 4.88 | 4.85
2018-11-29 10:30 | 5.13 | 5.09
2018-11-29 11:00 | 5.62 | 5.55
2018-11-29 11:30 | 6.12 | 6.05
2018-11-29 12:00 | 7.27 | 7.18
2018-11-29 12:30 | 7.69 | 7.6
2018-11-29 13:00 | 8.76 | 8.67
2018-11-29 13:30 | 9.4 | 9.31
2018-11-29 14:00 | 10.41 | 10.32
2018-11-29 14:30 | 10.29 | 10.18
2018-11-29 15:00 | 11.12 | 11.02
2018-11-29 15:30 | 12.31 | 12.21
2018-11-29 16:00 | 13.12 | 13.02
2018-11-29 16:30 | 14.46 | 14.35
2018-11-29 17:00 | 15.69 | 15.59
2018-11-29 17:30 | 15.67 | 15.59
2018-11-29 18:00 | 15.27 | 15.2
2018-11-29 18:30 | 15.06 | 15
2018-11-29 19:00 | 15.43 | 15.37
2018-11-29 19:30 | 15.19 | 15.13
2018-11-29 20:00 | 14.49 | 14.44
2018-11-29 20:30 | 13.63 | 13.6
2018-11-29 21:00 | 12.6 | 12.58
2018-11-29 21:30 | 11.27 | 11.26
2018-11-29 22:00 | 10.34 | 10.34
2018-11-29 22:30 | 9.66 | 9.65
2018-11-29 23:00 | 9.08 | 9.07
2018-11-29 23:30 | 7.95 | 7.94
2018-11-30 | 6.98 | 6.97
2018-11-30 00:30 | 6.3 | 6.28
2018-11-30 01:00 | 6.02 | 6.01
2018-11-30 01:30 | 5.74 | 5.72
2018-11-30 02:00 | 5.43 | 5.4
2018-11-30 02:30 | 5.34 | 5.31
2018-11-30 03:00 | 5.23 | 5.2
2018-11-30 03:30 | 5.22 | 5.19
2018-11-30 04:00 | 5.19 | 5.16
2018-11-30 04:30 | 5.11 | 5.07
2018-11-30 05:00 | 5.2 | 5.13
2018-11-30 05:30 | 5.43 | 5.35
2018-11-30 06:00 | 5.42 | 5.34
2018-11-30 06:30 | 5.21 | 5.15
2018-11-30 07:00 | 5.32 | 5.28
2018-11-30 07:30 | 5.15 | 5.13
2018-11-30 08:00 | 4.81 | 4.79
2018-11-30 08:30 | 4.5 | 4.47
2018-11-30 09:00 | 4.21 | 4.18
2018-11-30 09:30 | 4.24 | 4.2
2018-11-30 10:00 | 4.36 | 4.32
2018-11-30 10:30 | 4.7 | 4.66
2018-11-30 11:00 | 5.98 | 5.94
2018-11-30 11:30 | 7.55 | 7.51
2018-11-30 12:00 | 8.14 | 8.1
2018-11-30 12:30 | 7.05 | 6.99
2018-11-30 13:00 | 9.09 | 9.03
2018-11-30 13:30 | 8.77 | 8.71
2018-11-30 14:00 | 11.5 | 11.44
2018-11-30 14:30 | 10.85 | 10.78
2018-11-30 15:00 | 11.48 | 11.41
2018-11-30 15:30 | 11.37 | 11.31
2018-11-30 16:00 | 11.32 | 11.26
2018-11-30 16:30 | 12.44 | 12.38
2018-11-30 17:00 | 12.78 | 12.73
2018-11-30 17:30 | 13.2 | 13.15
2018-11-30 18:00 | 13.25 | 13.21
2018-11-30 18:30 | 13.21 | 13.18
2018-11-30 19:00 | 13.36 | 13.33
2018-11-30 19:30 | 13.46 | 13.43
2018-11-30 20:00 | 13.3 | 13.27
2018-11-30 20:30 | 12.88 | 12.86
2018-11-30 21:00 | 12.06 | 12.04
2018-11-30 21:30 | 11.25 | 11.24
2018-11-30 22:00 | 10.51 | 10.5
2018-11-30 22:30 | 9.93 | 9.93
2018-11-30 23:00 | 9.55 | 9.54
2018-11-30 23:30 | 8.42 | 8.41
2018-12-01 | 7.71 | 7.7
2018-12-01 00:30 | 7.06 | 7.05
2018-12-01 01:00 | 6.67 | 6.66
2018-12-01 01:30 | 6.25 | 6.24
2018-12-01 02:00 | 5.89 | 5.88
2018-12-01 02:30 | 5.75 | 5.74
2018-12-01 03:00 | 5.58 | 5.56
2018-12-01 03:30 | 5.53 | 5.51
2018-12-01 04:00 | 5.4 | 5.38
2018-12-01 04:30 | 5.61 | 5.59
2018-12-01 05:00 | 5.82 | 5.79
2018-12-01 05:30 | 5.79 | 5.74
2018-12-01 06:00 | 5.74 | 5.69
2018-12-01 06:30 | 5.57 | 5.54
2018-12-01 07:00 | 5.4 | 5.38
2018-12-01 07:30 | 5.79 | 5.78
2018-12-01 08:00 | 6.1 | 6.09
2018-12-01 08:30 | 6.39 | 6.38
2018-12-01 09:00 | 6.79 | 6.76
2018-12-01 09:30 | 7.38 | 7.35
2018-12-01 10:00 | 7.78 | 7.73
2018-12-01 10:30 | 8.31 | 8.24
2018-12-01 11:00 | 9.02 | 8.93
2018-12-01 11:30 | 9.84 | 9.73
2018-12-01 12:00 | 10.55 | 10.43
2018-12-01 12:30 | 11.47 | 11.34
2018-12-01 13:00 | 12.56 | 12.37
2018-12-01 13:30 | 13.54 | 13.35
2018-12-01 14:00 | 14.32 | 14.16
2018-12-01 14:30 | 15.23 | 15.05
2018-12-01 15:00 | 16.33 | 16.13
2018-12-01 15:30 | 17.44 | 17.28
2018-12-01 16:00 | 17.8 | 17.64
2018-12-01 16:30 | 18.56 | 18.39
2018-12-01 17:00 | 19.06 | 18.9
2018-12-01 17:30 | 19.07 | 18.94
2018-12-01 18:00 | 18.43 | 18.32
2018-12-01 18:30 | 17.54 | 17.44
2018-12-01 19:00 | 17 | 16.9
2018-12-01 19:30 | 16.25 | 16.16
2018-12-01 20:00 | 15.82 | 15.74
2018-12-01 20:30 | 15.15 | 15.09
2018-12-01 21:00 | 14.26 | 14.22
2018-12-01 21:30 | 13.28 | 13.25
2018-12-01 22:00 | 12.46 | 12.43
2018-12-01 22:30 | 11.86 | 11.84
2018-12-01 23:00 | 11.26 | 11.25
2018-12-01 23:30 | 10.11 | 10.09
2018-12-02 | 9.03 | 9.02
2018-12-02 00:30 | 8.25 | 8.23
2018-12-02 01:00 | 7.83 | 7.82
2018-12-02 01:30 | 7.43 | 7.41
2018-12-02 02:00 | 6.97 | 6.96
2018-12-02 02:30 | 6.77 | 6.76
2018-12-02 03:00 | 6.58 | 6.56
2018-12-02 03:30 | 6.42 | 6.41
2018-12-02 04:00 | 6.29 | 6.28
2018-12-02 04:30 | 6.31 | 6.3
2018-12-02 05:00 | 6.03 | 6
2018-12-02 05:30 | 5.94 | 5.9
2018-12-02 06:00 | 5.8 | 5.77
2018-12-02 06:30 | 5.67 | 5.64
2018-12-02 07:00 | 5.64 | 5.62
2018-12-02 07:30 | 6.08 | 6.06
2018-12-02 08:00 | 6.63 | 6.6
2018-12-02 08:30 | 7.17 | 7.13
2018-12-02 09:00 | 8.05 | 8.02
2018-12-02 09:30 | 8.45 | 8.41
2018-12-02 10:00 | 9.29 | 9.22
2018-12-02 10:30 | 10.51 | 10.41
2018-12-02 11:00 | 11.63 | 11.51
2018-12-02 11:30 | 12.93 | 12.79
2018-12-02 12:00 | 15.53 | 15.37
2018-12-02 12:30 | 15.39 | 15.21
2018-12-02 13:00 | 17.06 | 16.87
2018-12-02 13:30 | 17.98 | 17.77
2018-12-02 14:00 | 18.78 | 18.55
2018-12-02 14:30 | 21.1 | 20.88
2018-12-02 15:00 | 21.08 | 20.87
2018-12-02 15:30 | 21.48 | 21.29
2018-12-02 16:00 | 21.76 | 21.56
2018-12-02 16:30 | 21.88 | 21.69
2018-12-02 17:00 | 22.16 | 21.98
2018-12-02 17:30 | 22.31 | 22.13
2018-12-02 18:00 | 22.45 | 22.27
2018-12-02 18:30 | 22.23 | 22.06
2018-12-02 19:00 | 21.9 | 21.73
2018-12-02 19:30 | 21.61 | 21.42
2018-12-02 20:00 | 21.07 | 20.89
2018-12-02 20:30 | 19.95 | 19.79
2018-12-02 21:00 | 18.11 | 18
2018-12-02 21:30 | 16.48 | 16.38
2018-12-02 22:00 | 14.66 | 14.59
2018-12-02 22:30 | 13.31 | 13.28
2018-12-02 23:00 | 12.34 | 12.31
2018-12-02 23:30 | 10.75 | 10.73
2018-12-03 | 9.44 | 9.43
2018-12-03 00:30 | 8.66 | 8.64
2018-12-03 01:00 | 8.27 | 8.25
2018-12-03 01:30 | 9.15 | 9.14
2018-12-03 02:00 | 8.86 | 8.85
2018-12-03 02:30 | 8.5 | 8.49
2018-12-03 03:00 | 7.08 | 7.07
2018-12-03 03:30 | 6.94 | 6.93
2018-12-03 04:00 | 6.89 | 6.88
2018-12-03 04:30 | 6.9 | 6.89
2018-12-03 05:00 | 6.86 | 6.85
2018-12-03 05:30 | 6.93 | 6.92
2018-12-03 06:00 | 6.9 | 6.88
2018-12-03 06:30 | 7.36 | 7.35
2018-12-03 07:00 | 7.83 | 7.82
2018-12-03 07:30 | 7.96 | 7.95
2018-12-03 08:00 | 7.84 | 7.83
2018-12-03 08:30 | 7.57 | 7.54
2018-12-03 09:00 | 7.48 | 7.43
2018-12-03 09:30 | 7.89 | 7.83
2018-12-03 10:00 | 8.24 | 8.17
2018-12-03 10:30 | 8.81 | 8.71
2018-12-03 11:00 | 9.2 | 9.09
2018-12-03 11:30 | 10.28 | 10.16
2018-12-03 12:00 | 11.32 | 11.19
2018-12-03 12:30 | 12.47 | 12.35
2018-12-03 13:00 | 10.9 | 10.76
2018-12-03 13:30 | 11.58 | 11.44
2018-12-03 14:00 | 11.75 | 11.6
2018-12-03 14:30 | 12.29 | 12.14
2018-12-03 15:00 | 12.57 | 12.41
2018-12-03 15:30 | 13.53 | 13.37
2018-12-03 16:00 | 14.61 | 14.49
2018-12-03 16:30 | 15.57 | 15.44
2018-12-03 17:00 | 16.03 | 15.92
2018-12-03 17:30 | 16.27 | 16.18
2018-12-03 18:00 | 16.37 | 16.29
2018-12-03 18:30 | 16.06 | 16
2018-12-03 19:00 | 16.45 | 16.38
2018-12-03 19:30 | 16.12 | 16.05
2018-12-03 20:00 | 15.81 | 15.76
2018-12-03 20:30 | 15.15 | 15.11
2018-12-03 21:00 | 13.77 | 13.74
2018-12-03 21:30 | 12.72 | 12.7
2018-12-03 22:00 | 11.4 | 11.39
2018-12-03 22:30 | 10.21 | 10.2
2018-12-03 23:00 | 9.53 | 9.52
2018-12-03 23:30 | 8.38 | 8.37
2018-12-04 | 7.44 | 7.43
2018-12-04 00:30 | 6.8 | 6.79
2018-12-04 01:00 | 6.5 | 6.49
2018-12-04 01:30 | 6.16 | 6.15
2018-12-04 02:00 | 5.88 | 5.86
2018-12-04 02:30 | 5.72 | 5.7
2018-12-04 03:00 | 5.64 | 5.62
2018-12-04 03:30 | 5.56 | 5.54
2018-12-04 04:00 | 5.52 | 5.5
2018-12-04 04:30 | 5.59 | 5.56
2018-12-04 05:00 | 5.57 | 5.52
2018-12-04 05:30 | 5.67 | 5.63
2018-12-04 06:00 | 6.37 | 6.35
2018-12-04 06:30 | 6.06 | 6.05
2018-12-04 07:00 | 6.73 | 6.72
2018-12-04 07:30 | 6.08 | 6.08
2018-12-04 08:00 | 6.21 | 6.2
2018-12-04 08:30 | 6.38 | 6.38
2018-12-04 09:00 | 6.69 | 6.68
2018-12-04 09:30 | 5.93 | 5.9
2018-12-04 10:00 | 7.48 | 7.46
2018-12-04 10:30 | 6.05 | 6.01
2018-12-04 11:00 | 7.62 | 7.58
2018-12-04 11:30 | 8.55 | 8.51
2018-12-04 12:00 | 8.36 | 8.31
2018-12-04 12:30 | 8.68 | 8.62
2018-12-04 13:00 | 10.08 | 10.03
2018-12-04 13:30 | 10.23 | 10.16
2018-12-04 14:00 | 11.17 | 11.12
2018-12-04 14:30 | 11.75 | 11.7
2018-12-04 15:00 | 11.65 | 11.61
2018-12-04 15:30 | 11.77 | 11.74
2018-12-04 16:00 | 11.79 | 11.77
2018-12-04 16:30 | 12.03 | 12.01
2018-12-04 17:00 | 12.53 | 12.51
2018-12-04 17:30 | 12.88 | 12.86
2018-12-04 18:00 | 12.99 | 12.98
2018-12-04 18:30 | 13.26 | 13.24
2018-12-04 19:00 | 14 | 13.96
2018-12-04 19:30 | 13.93 | 13.9
2018-12-04 20:00 | 13.65 | 13.63
2018-12-04 20:30 | 13.08 | 13.07
2018-12-04 21:00 | 12.4 | 12.39
2018-12-04 21:30 | 11.39 | 11.38
2018-12-04 22:00 | 10.17 | 10.17
2018-12-04 22:30 | 9.49 | 9.48
2018-12-04 23:00 | 9.03 | 9.02
2018-12-04 23:30 | 7.59 | 7.58
2018-12-05 | 6.63 | 6.62
2018-12-05 00:30 | 6.07 | 6.06
2018-12-05 01:00 | 5.91 | 5.89
2018-12-05 01:30 | 5.52 | 5.49
2018-12-05 02:00 | 5.32 | 5.29
2018-12-05 02:30 | 5.37 | 5.34
2018-12-05 03:00 | 5.18 | 5.15
2018-12-05 03:30 | 5.16 | 5.12
2018-12-05 04:00 | 5.12 | 5.08
2018-12-05 04:30 | 5.25 | 5.22
2018-12-05 05:00 | 5.3 | 5.23
2018-12-05 05:30 | 5.65 | 5.58
2018-12-05 06:00 | 5.83 | 5.76
2018-12-05 06:30 | 5.69 | 5.64
2018-12-05 07:00 | 5.55 | 5.52
2018-12-05 07:30 | 5.42 | 5.4
2018-12-05 08:00 | 4.93 | 4.91
2018-12-05 08:30 | 5.37 | 5.36
2018-12-05 09:00 | 5.43 | 5.4
2018-12-05 09:30 | 4.37 | 4.33
2018-12-05 10:00 | 4.4 | 4.36
2018-12-05 10:30 | 5.01 | 4.98
2018-12-05 11:00 | 4.79 | 4.75
2018-12-05 11:30 | 5.89 | 5.87
2018-12-05 12:00 | 7.58 | 7.57
2018-12-05 12:30 | 6.6 | 6.58
2018-12-05 13:00 | 5.95 | 5.92
2018-12-05 13:30 | 5.73 | 5.7
2018-12-05 14:00 | 7.98 | 7.97
2018-12-05 14:30 | 8.08 | 8.06
2018-12-05 15:00 | 7.89 | 7.87
2018-12-05 15:30 | 8.36 | 8.34
2018-12-05 16:00 | 8.64 | 8.63
2018-12-05 16:30 | 9.56 | 9.55
2018-12-05 17:00 | 10.09 | 10.08
2018-12-05 17:30 | 10.84 | 10.83
2018-12-05 18:00 | 10.97 | 10.96
2018-12-05 18:30 | 11.65 | 11.65
2018-12-05 19:00 | 12.16 | 12.15
2018-12-05 19:30 | 12.44 | 12.43
2018-12-05 20:00 | 12.32 | 12.31
2018-12-05 20:30 | 11.81 | 11.81
2018-12-05 21:00 | 11.18 | 11.17
2018-12-05 21:30 | 10.72 | 10.71
2018-12-05 22:00 | 9.76 | 9.76
2018-12-05 22:30 | 8.7 | 8.69
2018-12-05 23:00 | 8.14 | 8.12
2018-12-05 23:30 | 7.04 | 7.02
2018-12-06 | 6.15 | 6.12
2018-12-06 00:30 | 5.53 | 5.5
2018-12-06 01:00 | 5.31 | 5.27
2018-12-06 01:30 | 5.15 | 5.1
2018-12-06 02:00 | 4.91 | 4.86
2018-12-06 02:30 | 4.82 | 4.77
2018-12-06 03:00 | 4.69 | 4.63
2018-12-06 03:30 | 4.75 | 4.7
2018-12-06 04:00 | 4.76 | 4.71
2018-12-06 04:30 | 4.93 | 4.87
2018-12-06 05:00 | 4.99 | 4.89
2018-12-06 05:30 | 5.25 | 5.15
2018-12-06 06:00 | 5.66 | 5.6
2018-12-06 06:30 | 6.11 | 6.07
2018-12-06 07:00 | 5.84 | 5.81
2018-12-06 07:30 | 6.43 | 6.42
2018-12-06 08:00 | 6.33 | 6.32
2018-12-06 08:30 | 4.89 | 4.89
2018-12-06 09:00 | 4.58 | 4.57
2018-12-06 09:30 | 4.12 | 4.12
2018-12-06 10:00 | 5.7 | 5.7
2018-12-06 10:30 | 6.02 | 6.01
2018-12-06 11:00 | 5.49 | 5.48
2018-12-06 11:30 | 4.92 | 4.91
2018-12-06 12:00 | 4.28 | 4.27
2018-12-06 12:30 | 4.98 | 4.97
2018-12-06 13:00 | 5.46 | 5.45
2018-12-06 13:30 | 5.54 | 5.53
2018-12-06 14:00 | 4.9 | 4.89
2018-12-06 14:30 | 5.41 | 5.4
2018-12-06 15:00 | 5.25 | 5.22
2018-12-06 15:30 | 5.36 | 5.33
2018-12-06 16:00 | 6.6 | 6.58
2018-12-06 16:30 | 8.04 | 8.03
2018-12-06 17:00 | 9.26 | 9.25
2018-12-06 17:30 | 10.05 | 10.04
2018-12-06 18:00 | 10.44 | 10.43
2018-12-06 18:30 | 11.09 | 11.08
2018-12-06 19:00 | 12.03 | 12.02
2018-12-06 19:30 | 12.25 | 12.24
2018-12-06 20:00 | 12.28 | 12.27
2018-12-06 20:30 | 12.04 | 12.03
2018-12-06 21:00 | 11.37 | 11.37
2018-12-06 21:30 | 10.51 | 10.51
2018-12-06 22:00 | 9.31 | 9.31
2018-12-06 22:30 | 8.65 | 8.64
2018-12-06 23:00 | 8.19 | 8.18
2018-12-06 23:30 | 7.09 | 7.07
2018-12-07 | 6.22 | 6.19
2018-12-07 00:30 | 5.69 | 5.66
2018-12-07 01:00 | 5.39 | 5.35
2018-12-07 01:30 | 5.11 | 5.06
2018-12-07 02:00 | 4.9 | 4.85
2018-12-07 02:30 | 4.8 | 4.75
2018-12-07 03:00 | 4.7 | 4.64
2018-12-07 03:30 | 4.78 | 4.73
2018-12-07 04:00 | 4.69 | 4.64
2018-12-07 04:30 | 4.76 | 4.7
2018-12-07 05:00 | 4.79 | 4.68
2018-12-07 05:30 | 4.98 | 4.86
2018-12-07 06:00 | 5.09 | 4.99
2018-12-07 06:30 | 5.14 | 5.07
2018-12-07 07:00 | 5.39 | 5.36
2018-12-07 07:30 | 5.46 | 5.43
2018-12-07 08:00 | 5.21 | 5.19
2018-12-07 08:30 | 5.73 | 5.73
2018-12-07 09:00 | 6.11 | 6.1
2018-12-07 09:30 | 5.12 | 5.11
2018-12-07 10:00 | 6.19 | 6.18
2018-12-07 10:30 | 5.59 | 5.58
2018-12-07 11:00 | 6.81 | 6.81
2018-12-07 11:30 | 6.53 | 6.52
2018-12-07 12:00 | 6.62 | 6.62
2018-12-07 12:30 | 4.93 | 4.93
2018-12-07 13:00 | 5.5 | 5.5
2018-12-07 13:30 | 4.62 | 4.61
2018-12-07 14:00 | 5.49 | 5.47
2018-12-07 14:30 | 5.62 | 5.61
2018-12-07 15:00 | 5.35 | 5.34
2018-12-07 15:30 | 6.69 | 6.69
2018-12-07 16:00 | 8.13 | 8.13
2018-12-07 16:30 | 8.75 | 8.75
2018-12-07 17:00 | 9.25 | 9.25
2018-12-07 17:30 | 9.62 | 9.61
2018-12-07 18:00 | 9.43 | 9.42
2018-12-07 18:30 | 9.44 | 9.43
2018-12-07 19:00 | 10.06 | 10.05
2018-12-07 19:30 | 10.4 | 10.39
2018-12-07 20:00 | 10.48 | 10.47
2018-12-07 20:30 | 10.33 | 10.32
2018-12-07 21:00 | 9.89 | 9.88
2018-12-07 21:30 | 9.2 | 9.19
2018-12-07 22:00 | 8.62 | 8.61
2018-12-07 22:30 | 8.3 | 8.29
2018-12-07 23:00 | 8.2 | 8.19
2018-12-07 23:30 | 7.29 | 7.27
2018-12-08 | 6.5 | 6.48
2018-12-08 00:30 | 5.87 | 5.83
2018-12-08 01:00 | 5.59 | 5.55
2018-12-08 01:30 | 5.25 | 5.2
2018-12-08 02:00 | 4.94 | 4.89
2018-12-08 02:30 | 4.87 | 4.82
2018-12-08 03:00 | 4.8 | 4.75
2018-12-08 03:30 | 4.83 | 4.78
2018-12-08 04:00 | 4.71 | 4.65
2018-12-08 04:30 | 4.75 | 4.7
2018-12-08 05:00 | 5.29 | 5.25
2018-12-08 05:30 | 5.4 | 5.33
2018-12-08 06:00 | 5.61 | 5.54
2018-12-08 06:30 | 5.59 | 5.53
2018-12-08 07:00 | 5.22 | 5.17
2018-12-08 07:30 | 5.23 | 5.19
2018-12-08 08:00 | 5.75 | 5.73
2018-12-08 08:30 | 7.07 | 7.06
2018-12-08 09:00 | 7.69 | 7.68
2018-12-08 09:30 | 7.08 | 7.08
2018-12-08 10:00 | 6.22 | 6.22
2018-12-08 10:30 | 5.58 | 5.56
2018-12-08 11:00 | 6.11 | 6.09
2018-12-08 11:30 | 6.35 | 6.34
2018-12-08 12:00 | 5.37 | 5.35
2018-12-08 12:30 | 4.43 | 4.39
2018-12-08 13:00 | 6.39 | 6.37
2018-12-08 13:30 | 7.04 | 7.02
2018-12-08 14:00 | 6.59 | 6.56
2018-12-08 14:30 | 6.3 | 6.28
2018-12-08 15:00 | 6.78 | 6.76
2018-12-08 15:30 | 7.59 | 7.57
2018-12-08 16:00 | 7.2 | 7.18
2018-12-08 16:30 | 7.37 | 7.36
2018-12-08 17:00 | 8.26 | 8.24
2018-12-08 17:30 | 8.69 | 8.68
2018-12-08 18:00 | 8.79 | 8.78
2018-12-08 18:30 | 9.23 | 9.22
2018-12-08 19:00 | 9.69 | 9.68
2018-12-08 19:30 | 10.06 | 10.04
2018-12-08 20:00 | 10.21 | 10.2
2018-12-08 20:30 | 9.98 | 9.97
2018-12-08 21:00 | 9.3 | 9.29
2018-12-08 21:30 | 8.83 | 8.82
2018-12-08 22:00 | 8.53 | 8.52
2018-12-08 22:30 | 8.3 | 8.29
2018-12-08 23:00 | 8.17 | 8.16
2018-12-08 23:30 | 7.48 | 7.47
2018-12-09 | 6.57 | 6.55
2018-12-09 00:30 | 6.02 | 5.99
2018-12-09 01:00 | 5.61 | 5.57
2018-12-09 01:30 | 5.4 | 5.36
2018-12-09 02:00 | 5.19 | 5.15
2018-12-09 02:30 | 5 | 4.97
2018-12-09 03:00 | 4.88 | 4.83
2018-12-09 03:30 | 4.88 | 4.83
2018-12-09 04:00 | 4.71 | 4.66
2018-12-09 04:30 | 4.74 | 4.69
2018-12-09 05:00 | 4.6 | 4.5
2018-12-09 05:30 | 4.53 | 4.39
2018-12-09 06:00 | 4.34 | 4.2
2018-12-09 06:30 | 4.25 | 4.13
2018-12-09 07:00 | 4.37 | 4.28
2018-12-09 07:30 | 4.34 | 4.28
2018-12-09 08:00 | 4.48 | 4.44
2018-12-09 08:30 | 4.7 | 4.68
2018-12-09 09:00 | 4.44 | 4.41
2018-12-09 09:30 | 5.83 | 5.81
2018-12-09 10:00 | 6.15 | 6.12
2018-12-09 10:30 | 6.66 | 6.63
2018-12-09 11:00 | 5.88 | 5.84
2018-12-09 11:30 | 6.31 | 6.28
2018-12-09 12:00 | 7.13 | 7.11
2018-12-09 12:30 | 7.87 | 7.85
2018-12-09 13:00 | 9.1 | 9.08
2018-12-09 13:30 | 7.64 | 7.6
2018-12-09 14:00 | 7.82 | 7.78
2018-12-09 14:30 | 8.26 | 8.22
2018-12-09 15:00 | 8.43 | 8.39
2018-12-09 15:30 | 9.02 | 8.99
2018-12-09 16:00 | 9.57 | 9.54
2018-12-09 16:30 | 10.26 | 10.23
2018-12-09 17:00 | 11.09 | 11.07
2018-12-09 17:30 | 11.82 | 11.8
2018-12-09 18:00 | 11.9 | 11.88
2018-12-09 18:30 | 11.86 | 11.84
2018-12-09 19:00 | 12.1 | 12.09
2018-12-09 19:30 | 12.34 | 12.32
2018-12-09 20:00 | 12.09 | 12.08
2018-12-09 20:30 | 11.88 | 11.87
2018-12-09 21:00 | 11.17 | 11.16
2018-12-09 21:30 | 10.43 | 10.42
2018-12-09 22:00 | 9.56 | 9.55
2018-12-09 22:30 | 9.04 | 9.03
2018-12-09 23:00 | 8.65 | 8.64
2018-12-09 23:30 | 7.61 | 7.6
2018-12-10 | 6.79 | 6.77
2018-12-10 00:30 | 6.2 | 6.18
2018-12-10 01:00 | 5.85 | 5.82
2018-12-10 01:30 | 5.52 | 5.48
2018-12-10 02:00 | 5.32 | 5.29
2018-12-10 02:30 | 5.19 | 5.16
2018-12-10 03:00 | 5.07 | 5.04
2018-12-10 03:30 | 5.05 | 5.01
2018-12-10 04:00 | 5.13 | 5.09
2018-12-10 04:30 | 5.12 | 5.07
2018-12-10 05:00 | 5.02 | 4.93
2018-12-10 05:30 | 5.23 | 5.13
2018-12-10 06:00 | 5.3 | 5.21
2018-12-10 06:30 | 5.28 | 5.22
2018-12-10 07:00 | 5.73 | 5.71
2018-12-10 07:30 | 6.16 | 6.15
2018-12-10 08:00 | 6.05 | 6.04
2018-12-10 08:30 | 5.56 | 5.56
2018-12-10 09:00 | 5.37 | 5.36
2018-12-10 09:30 | 6.12 | 6.1
2018-12-10 10:00 | 6.13 | 6.11
2018-12-10 10:30 | 6.57 | 6.55
2018-12-10 11:00 | 7.25 | 7.23
2018-12-10 11:30 | 8.19 | 8.17
2018-12-10 12:00 | 7.24 | 7.21
2018-12-10 12:30 | 6.98 | 6.94
2018-12-10 13:00 | 7.68 | 7.64
2018-12-10 13:30 | 8.97 | 8.93
2018-12-10 14:00 | 8.62 | 8.56
2018-12-10 14:30 | 8.43 | 8.36
2018-12-10 15:00 | 9.31 | 9.2
2018-12-10 15:30 | 11.82 | 11.75
2018-12-10 16:00 | 11.13 | 11.07
2018-12-10 16:30 | 12.36 | 12.31
2018-12-10 17:00 | 13 | 12.95
2018-12-10 17:30 | 13.92 | 13.87
2018-12-10 18:00 | 14.03 | 13.99
2018-12-10 18:30 | 13.9 | 13.88
2018-12-10 19:00 | 14.08 | 14.06
2018-12-10 19:30 | 14.29 | 14.27
2018-12-10 20:00 | 14.01 | 13.99
2018-12-10 20:30 | 13.52 | 13.51
2018-12-10 21:00 | 12.55 | 12.53
2018-12-10 21:30 | 11.34 | 11.33
2018-12-10 22:00 | 10.24 | 10.23
2018-12-10 22:30 | 9.38 | 9.38
2018-12-10 23:00 | 8.9 | 8.9
2018-12-10 23:30 | 7.75 | 7.74
2018-12-11 | 6.92 | 6.91
2018-12-11 00:30 | 6.25 | 6.24
2018-12-11 01:00 | 5.98 | 5.96
2018-12-11 01:30 | 5.67 | 5.65
2018-12-11 02:00 | 5.33 | 5.3
2018-12-11 02:30 | 5.13 | 5.1
2018-12-11 03:00 | 5.07 | 5.03
2018-12-11 03:30 | 5.04 | 5
2018-12-11 04:00 | 5.05 | 5.01
2018-12-11 04:30 | 5.17 | 5.13
2018-12-11 05:00 | 5.15 | 5.08
2018-12-11 05:30 | 5.23 | 5.14
2018-12-11 06:00 | 5.35 | 5.28
2018-12-11 06:30 | 5.43 | 5.38
2018-12-11 07:00 | 5.31 | 5.28
2018-12-11 07:30 | 5.35 | 5.33
2018-12-11 08:00 | 5.36 | 5.35
2018-12-11 08:30 | 4.97 | 4.95
2018-12-11 09:00 | 5.63 | 5.61
2018-12-11 09:30 | 5.42 | 5.39
2018-12-11 10:00 | 5.14 | 5.11
2018-12-11 10:30 | 5.72 | 5.7
2018-12-11 11:00 | 6.17 | 6.14
2018-12-11 11:30 | 6.42 | 6.39
2018-12-11 12:00 | 7.27 | 7.25
2018-12-11 12:30 | 8.7 | 8.67
2018-12-11 13:00 | 8.12 | 8.09
2018-12-11 13:30 | 8.89 | 8.85
2018-12-11 14:00 | 8.7 | 8.66
2018-12-11 14:30 | 8.75 | 8.7
2018-12-11 15:00 | 8.79 | 8.74
2018-12-11 15:30 | 9.68 | 9.61
2018-12-11 16:00 | 10.81 | 10.77
2018-12-11 16:30 | 11.82 | 11.78
2018-12-11 17:00 | 12.75 | 12.67
2018-12-11 17:30 | 13.37 | 13.29
2018-12-11 18:00 | 13.9 | 13.84
2018-12-11 18:30 | 14.09 | 14.04
2018-12-11 19:00 | 14.74 | 14.66
2018-12-11 19:30 | 14.45 | 14.37
2018-12-11 20:00 | 14.01 | 13.96
2018-12-11 20:30 | 13.7 | 13.65
2018-12-11 21:00 | 13.09 | 13.05
2018-12-11 21:30 | 12.03 | 12
2018-12-11 22:00 | 10.63 | 10.62
2018-12-11 22:30 | 9.65 | 9.65
2018-12-11 23:00 | 9.1 | 9.09
2018-12-11 23:30 | 8.05 | 8.04
2018-12-12 | 7.09 | 7.08
2018-12-12 00:30 | 6.37 | 6.35
2018-12-12 01:00 | 6.12 | 6.11
2018-12-12 01:30 | 5.76 | 5.74
2018-12-12 02:00 | 5.51 | 5.49
2018-12-12 02:30 | 5.36 | 5.34
2018-12-12 03:00 | 5.17 | 5.14
2018-12-12 03:30 | 5.23 | 5.2
2018-12-12 04:00 | 5.28 | 5.24
2018-12-12 04:30 | 5.31 | 5.27
2018-12-12 05:00 | 5.26 | 5.19
2018-12-12 05:30 | 5.55 | 5.47
2018-12-12 06:00 | 5.48 | 5.41
2018-12-12 06:30 | 5.87 | 5.87
2018-12-12 07:00 | 6.23 | 6.22
2018-12-12 07:30 | 6.17 | 6.17
2018-12-12 08:00 | 6.38 | 6.38
2018-12-12 08:30 | 6.06 | 6.05
2018-12-12 09:00 | 6.02 | 5.99
2018-12-12 09:30 | 5.76 | 5.71
2018-12-12 10:00 | 6.21 | 6.15
2018-12-12 10:30 | 6.12 | 6.06
2018-12-12 11:00 | 7.02 | 6.96
2018-12-12 11:30 | 6.43 | 6.34
2018-12-12 12:00 | 7.07 | 6.97
2018-12-12 12:30 | 7.47 | 7.37
2018-12-12 13:00 | 7.68 | 7.56
2018-12-12 13:30 | 8.73 | 8.62
2018-12-12 14:00 | 9.17 | 9.05
2018-12-12 14:30 | 9.16 | 9.05
2018-12-12 15:00 | 9.55 | 9.43
2018-12-12 15:30 | 10.26 | 10.15
2018-12-12 16:00 | 11.42 | 11.31
2018-12-12 16:30 | 12.41 | 12.32
2018-12-12 17:00 | 13.13 | 13.05
2018-12-12 17:30 | 13.95 | 13.87
2018-12-12 18:00 | 14.1 | 14.04
2018-12-12 18:30 | 14.07 | 14.01
2018-12-12 19:00 | 14.38 | 14.32
2018-12-12 19:30 | 14.3 | 14.23
2018-12-12 20:00 | 14.3 | 14.24
2018-12-12 20:30 | 14.05 | 14.01
2018-12-12 21:00 | 13.37 | 13.34
2018-12-12 21:30 | 11.94 | 11.92
2018-12-12 22:00 | 10.69 | 10.68
2018-12-12 22:30 | 10.09 | 10.08
2018-12-12 23:00 | 9.45 | 9.45
2018-12-12 23:30 | 8.18 | 8.17
2018-12-13 | 7.29 | 7.28
2018-12-13 00:30 | 6.59 | 6.58
2018-12-13 01:00 | 6.28 | 6.27
2018-12-13 01:30 | 5.91 | 5.89
2018-12-13 02:00 | 5.63 | 5.6
2018-12-13 02:30 | 5.53 | 5.51
2018-12-13 03:00 | 5.46 | 5.44
2018-12-13 03:30 | 5.38 | 5.36
2018-12-13 04:00 | 5.38 | 5.35
2018-12-13 04:30 | 5.43 | 5.4
2018-12-13 05:00 | 5.38 | 5.33
2018-12-13 05:30 | 5.57 | 5.5
2018-12-13 06:00 | 5.7 | 5.65
2018-12-13 06:30 | 5.75 | 5.71
2018-12-13 07:00 | 5.72 | 5.7
2018-12-13 07:30 | 5.47 | 5.45
2018-12-13 08:00 | 5.63 | 5.62
2018-12-13 08:30 | 5.49 | 5.47
2018-12-13 09:00 | 6.23 | 6.2
2018-12-13 09:30 | 6.29 | 6.23
2018-12-13 10:00 | 6.69 | 6.62
2018-12-13 10:30 | 6.34 | 6.25
2018-12-13 11:00 | 6.65 | 6.56
2018-12-13 11:30 | 6.63 | 6.52
2018-12-13 12:00 | 7.39 | 7.25
2018-12-13 12:30 | 8.45 | 8.31
2018-12-13 13:00 | 9.65 | 9.53
2018-12-13 13:30 | 10.5 | 10.4
2018-12-13 14:00 | 10.55 | 10.42
2018-12-13 14:30 | 9.56 | 9.38
2018-12-13 15:00 | 11.21 | 11.06
2018-12-13 15:30 | 11.26 | 11.11
2018-12-13 16:00 | 11.78 | 11.63
2018-12-13 16:30 | 13.7 | 13.57
2018-12-13 17:00 | 14.27 | 14.18
2018-12-13 17:30 | 14.29 | 14.2
2018-12-13 18:00 | 14.54 | 14.46
2018-12-13 18:30 | 14.55 | 14.48
2018-12-13 19:00 | 14.91 | 14.82
2018-12-13 19:30 | 14.9 | 14.81
2018-12-13 20:00 | 14.85 | 14.77
2018-12-13 20:30 | 14.4 | 14.34
2018-12-13 21:00 | 13.72 | 13.67
2018-12-13 21:30 | 12.93 | 12.88
2018-12-13 22:00 | 11.95 | 11.91
2018-12-13 22:30 | 10.76 | 10.75
2018-12-13 23:00 | 10.12 | 10.11
2018-12-13 23:30 | 8.94 | 8.93
2018-12-14 | 7.94 | 7.94
2018-12-14 00:30 | 7.3 | 7.29
2018-12-14 01:00 | 6.92 | 6.91
2018-12-14 01:30 | 6.49 | 6.48
2018-12-14 02:00 | 6.23 | 6.22
2018-12-14 02:30 | 6.08 | 6.07
2018-12-14 03:00 | 5.96 | 5.95
2018-12-14 03:30 | 5.9 | 5.89
2018-12-14 04:00 | 5.82 | 5.81
2018-12-14 04:30 | 5.93 | 5.92
2018-12-14 05:00 | 5.96 | 5.94
2018-12-14 05:30 | 5.99 | 5.96
2018-12-14 06:00 | 6.58 | 6.57
2018-12-14 06:30 | 7.23 | 7.22
2018-12-14 07:00 | 7.77 | 7.77
2018-12-14 07:30 | 8.21 | 8.21
2018-12-14 08:00 | 8.19 | 8.19
2018-12-14 08:30 | 8.3 | 8.29
2018-12-14 09:00 | 7.6 | 7.58
2018-12-14 09:30 | 7.62 | 7.61
2018-12-14 10:00 | 6.91 | 6.89
2018-12-14 10:30 | 7.82 | 7.8
2018-12-14 11:00 | 6.26 | 6.24
2018-12-14 11:30 | 6.26 | 6.22
2018-12-14 12:00 | 6.86 | 6.8
2018-12-14 12:30 | 7.41 | 7.33
2018-12-14 13:00 | 8.17 | 8.07
2018-12-14 13:30 | 9.25 | 9.15
2018-12-14 14:00 | 10.8 | 10.69
2018-12-14 14:30 | 12 | 11.89
2018-12-14 15:00 | 12.76 | 12.64
2018-12-14 15:30 | 13.72 | 13.61
2018-12-14 16:00 | 15.79 | 15.69
2018-12-14 16:30 | 15.33 | 15.23
2018-12-14 17:00 | 15.17 | 15.1
2018-12-14 17:30 | 14.88 | 14.82
2018-12-14 18:00 | 14.65 | 14.61
2018-12-14 18:30 | 14.48 | 14.43
2018-12-14 19:00 | 14.68 | 14.62
2018-12-14 19:30 | 14.73 | 14.67
2018-12-14 20:00 | 14.8 | 14.74
2018-12-14 20:30 | 14.56 | 14.51
2018-12-14 21:00 | 13.78 | 13.74
2018-12-14 21:30 | 12.72 | 12.69
2018-12-14 22:00 | 11.84 | 11.82
2018-12-14 22:30 | 11.42 | 11.4
2018-12-14 23:00 | 11.02 | 11.01
2018-12-14 23:30 | 9.81 | 9.79
2018-12-15 | 8.74 | 8.73
2018-12-15 00:30 | 8.04 | 8.02
2018-12-15 01:00 | 7.64 | 7.63
2018-12-15 01:30 | 6.99 | 6.98
2018-12-15 02:00 | 6.65 | 6.63
2018-12-15 02:30 | 6.49 | 6.48
2018-12-15 03:00 | 6.15 | 6.14
2018-12-15 03:30 | 6.03 | 6.01
2018-12-15 04:00 | 6.1 | 6.08
2018-12-15 04:30 | 6.21 | 6.2
2018-12-15 05:00 | 6.1 | 6.08
2018-12-15 05:30 | 6.05 | 6.02
2018-12-15 06:00 | 5.9 | 5.87
2018-12-15 06:30 | 5.78 | 5.75
2018-12-15 07:00 | 6.8 | 6.79
2018-12-15 07:30 | 6.76 | 6.74
2018-12-15 08:00 | 6.84 | 6.82
2018-12-15 08:30 | 7.11 | 7.09
2018-12-15 09:00 | 7 | 6.97
2018-12-15 09:30 | 7.25 | 7.22
2018-12-15 10:00 | 7.3 | 7.25
2018-12-15 10:30 | 8.46 | 8.41
2018-12-15 11:00 | 8.82 | 8.76
2018-12-15 11:30 | 11.29 | 11.22
2018-12-15 12:00 | 12.12 | 12.05
2018-12-15 12:30 | 12.18 | 12.11
2018-12-15 13:00 | 12.29 | 12.21
2018-12-15 13:30 | 12.08 | 11.98
2018-12-15 14:00 | 11.42 | 11.3
2018-12-15 14:30 | 12.4 | 12.28
2018-12-15 15:00 | 13.81 | 13.7
2018-12-15 15:30 | 14 | 13.88
2018-12-15 16:00 | 14.51 | 14.39
2018-12-15 16:30 | 15.11 | 15.01
2018-12-15 17:00 | 15.68 | 15.59
2018-12-15 17:30 | 15.46 | 15.39
2018-12-15 18:00 | 15.62 | 15.57
2018-12-15 18:30 | 16.26 | 16.23
2018-12-15 19:00 | 16.43 | 16.38
2018-12-15 19:30 | 16.13 | 16.09
2018-12-15 20:00 | 15.83 | 15.79
2018-12-15 20:30 | 15.29 | 15.26
2018-12-15 21:00 | 14.02 | 13.99
2018-12-15 21:30 | 12.4 | 12.38
2018-12-15 22:00 | 11.79 | 11.77
2018-12-15 22:30 | 11.22 | 11.21
2018-12-15 23:00 | 10.89 | 10.88
2018-12-15 23:30 | 9.93 | 9.92
2018-12-16 | 8.99 | 8.98
2018-12-16 00:30 | 8.32 | 8.3
2018-12-16 01:00 | 7.92 | 7.91
2018-12-16 01:30 | 7.46 | 7.44
2018-12-16 02:00 | 7.11 | 7.1
2018-12-16 02:30 | 6.91 | 6.9
2018-12-16 03:00 | 6.72 | 6.7
2018-12-16 03:30 | 6.67 | 6.65
2018-12-16 04:00 | 6.46 | 6.45
2018-12-16 04:30 | 6.37 | 6.35
2018-12-16 05:00 | 6.31 | 6.29
2018-12-16 05:30 | 6.26 | 6.24
2018-12-16 06:00 | 6.46 | 6.44
2018-12-16 06:30 | 6.33 | 6.31
2018-12-16 07:00 | 6.61 | 6.59
2018-12-16 07:30 | 7.41 | 7.39
2018-12-16 08:00 | 7.89 | 7.88
2018-12-16 08:30 | 8.33 | 8.32
2018-12-16 09:00 | 8.89 | 8.88
2018-12-16 09:30 | 9.77 | 9.75
2018-12-16 10:00 | 10.12 | 10.1
2018-12-16 10:30 | 9.5 | 9.49
2018-12-16 11:00 | 9.85 | 9.83
2018-12-16 11:30 | 9.58 | 9.56
2018-12-16 12:00 | 9.81 | 9.79
2018-12-16 12:30 | 9.14 | 9.12
2018-12-16 13:00 | 9.63 | 9.6
2018-12-16 13:30 | 9.08 | 9.05
2018-12-16 14:00 | 9.29 | 9.27
2018-12-16 14:30 | 9.89 | 9.87
2018-12-16 15:00 | 9.85 | 9.84
2018-12-16 15:30 | 9.85 | 9.84
2018-12-16 16:00 | 9.98 | 9.97
2018-12-16 16:30 | 10.06 | 10.04
2018-12-16 17:00 | 10.8 | 10.78
2018-12-16 17:30 | 11.25 | 11.24
2018-12-16 18:00 | 11.4 | 11.39
2018-12-16 18:30 | 11.75 | 11.74
2018-12-16 19:00 | 12.3 | 12.29
2018-12-16 19:30 | 12.17 | 12.16
2018-12-16 20:00 | 12.15 | 12.14
2018-12-16 20:30 | 11.83 | 11.82
2018-12-16 21:00 | 11.2 | 11.2
2018-12-16 21:30 | 10.43 | 10.42
2018-12-16 22:00 | 9.75 | 9.74
2018-12-16 22:30 | 9.23 | 9.23
2018-12-16 23:00 | 8.86 | 8.85
2018-12-16 23:30 | 7.82 | 7.81
2018-12-17 | 6.99 | 6.97
2018-12-17 00:30 | 6.29 | 6.27
2018-12-17 01:00 | 6.04 | 6.02
2018-12-17 01:30 | 5.75 | 5.73
2018-12-17 02:00 | 5.45 | 5.42
2018-12-17 02:30 | 5.4 | 5.37
2018-12-17 03:00 | 5.45 | 5.42
2018-12-17 03:30 | 5.28 | 5.25
2018-12-17 04:00 | 5.26 | 5.23
2018-12-17 04:30 | 5.33 | 5.3
2018-12-17 05:00 | 5.4 | 5.35
2018-12-17 05:30 | 5.5 | 5.43
2018-12-17 06:00 | 5.58 | 5.53
2018-12-17 06:30 | 5.67 | 5.63
2018-12-17 07:00 | 5.24 | 5.22
2018-12-17 07:30 | 5 | 4.99
2018-12-17 08:00 | 6.72 | 6.72
2018-12-17 08:30 | 6.88 | 6.87
2018-12-17 09:00 | 7.54 | 7.53
2018-12-17 09:30 | 7.92 | 7.91
2018-12-17 10:00 | 7.31 | 7.3
2018-12-17 10:30 | 7.05 | 7.04
2018-12-17 11:00 | 6.62 | 6.61
2018-12-17 11:30 | 6.49 | 6.47
2018-12-17 12:00 | 8.09 | 8.08
2018-12-17 12:30 | 9.4 | 9.39
2018-12-17 13:00 | 7.3 | 7.28
2018-12-17 13:30 | 7.1 | 7.08
2018-12-17 14:00 | 7.65 | 7.62
2018-12-17 14:30 | 9.17 | 9.14
2018-12-17 15:00 | 9.43 | 9.41
2018-12-17 15:30 | 9.98 | 9.97
2018-12-17 16:00 | 9.53 | 9.51
2018-12-17 16:30 | 10.17 | 10.16
2018-12-17 17:00 | 11.46 | 11.45
2018-12-17 17:30 | 11.93 | 11.93
2018-12-17 18:00 | 11.94 | 11.93
2018-12-17 18:30 | 12.86 | 12.86
2018-12-17 19:00 | 13.49 | 13.48
2018-12-17 19:30 | 13.63 | 13.62
2018-12-17 20:00 | 13.59 | 13.57
2018-12-17 20:30 | 13.43 | 13.42
2018-12-17 21:00 | 12.76 | 12.75
2018-12-17 21:30 | 11.72 | 11.72
2018-12-17 22:00 | 10.74 | 10.74
2018-12-17 22:30 | 9.74 | 9.74
2018-12-17 23:00 | 9.17 | 9.16
2018-12-17 23:30 | 8.03 | 8.02
2018-12-18 | 7.05 | 7.04
2018-12-18 00:30 | 6.46 | 6.45
2018-12-18 01:00 | 6.14 | 6.12
2018-12-18 01:30 | 5.76 | 5.73
2018-12-18 02:00 | 5.54 | 5.51
2018-12-18 02:30 | 5.38 | 5.35
2018-12-18 03:00 | 5.25 | 5.22
2018-12-18 03:30 | 5.33 | 5.3
2018-12-18 04:00 | 5.36 | 5.33
2018-12-18 04:30 | 5.43 | 5.4
2018-12-18 05:00 | 5.35 | 5.29
2018-12-18 05:30 | 5.58 | 5.52
2018-12-18 06:00 | 5.64 | 5.58
2018-12-18 06:30 | 5.51 | 5.46
2018-12-18 07:00 | 5.43 | 5.39
2018-12-18 07:30 | 5.79 | 5.77
2018-12-18 08:00 | 5.84 | 5.81
2018-12-18 08:30 | 6.49 | 6.47
2018-12-18 09:00 | 7.13 | 7.12
2018-12-18 09:30 | 6.88 | 6.86
2018-12-18 10:00 | 7.17 | 7.15
2018-12-18 10:30 | 8.26 | 8.25
2018-12-18 11:00 | 6.77 | 6.74
2018-12-18 11:30 | 8.11 | 8.09
2018-12-18 12:00 | 8.44 | 8.42
2018-12-18 12:30 | 9.19 | 9.17
2018-12-18 13:00 | 9.41 | 9.38
2018-12-18 13:30 | 9.57 | 9.54
2018-12-18 14:00 | 8.67 | 8.64
2018-12-18 14:30 | 8.5 | 8.46
2018-12-18 15:00 | 7.89 | 7.85
2018-12-18 15:30 | 9.18 | 9.14
2018-12-18 16:00 | 10.52 | 10.48
2018-12-18 16:30 | 11.99 | 11.93
2018-12-18 17:00 | 13.25 | 13.2
2018-12-18 17:30 | 14.05 | 14
2018-12-18 18:00 | 14.5 | 14.45
2018-12-18 18:30 | 14.71 | 14.67
2018-12-18 19:00 | 15.12 | 15.08
2018-12-18 19:30 | 15.41 | 15.36
2018-12-18 20:00 | 15.35 | 15.31
2018-12-18 20:30 | 14.84 | 14.8
2018-12-18 21:00 | 13.65 | 13.62
2018-12-18 21:30 | 12.25 | 12.24
2018-12-18 22:00 | 11.34 | 11.33
2018-12-18 22:30 | 10.51 | 10.5
2018-12-18 23:00 | 10.05 | 10.05
2018-12-18 23:30 | 8.79 | 8.79
2018-12-19 | 7.74 | 7.73
2018-12-19 00:30 | 7.04 | 7.03
2018-12-19 01:00 | 6.67 | 6.66
2018-12-19 01:30 | 6.37 | 6.36
2018-12-19 02:00 | 6.01 | 6
2018-12-19 02:30 | 5.88 | 5.87
2018-12-19 03:00 | 5.68 | 5.67
2018-12-19 03:30 | 5.59 | 5.57
2018-12-19 04:00 | 5.54 | 5.52
2018-12-19 04:30 | 5.58 | 5.56
2018-12-19 05:00 | 5.51 | 5.46
2018-12-19 05:30 | 5.6 | 5.53
2018-12-19 06:00 | 5.43 | 5.36
2018-12-19 06:30 | 5.6 | 5.57
2018-12-19 07:00 | 5.7 | 5.68
2018-12-19 07:30 | 5.93 | 5.92
2018-12-19 08:00 | 6.15 | 6.15
2018-12-19 08:30 | 6.63 | 6.62
2018-12-19 09:00 | 6.61 | 6.6
2018-12-19 09:30 | 7.44 | 7.43
2018-12-19 10:00 | 7.56 | 7.54
2018-12-19 10:30 | 7.93 | 7.9
2018-12-19 11:00 | 8.92 | 8.89
2018-12-19 11:30 | 8.91 | 8.86
2018-12-19 12:00 | 8.97 | 8.91
2018-12-19 12:30 | 10.99 | 10.93
2018-12-19 13:00 | 9.84 | 9.76
2018-12-19 13:30 | 9.82 | 9.73
2018-12-19 14:00 | 10.9 | 10.8
2018-12-19 14:30 | 11.39 | 11.29
2018-12-19 15:00 | 12.37 | 12.27
2018-12-19 15:30 | 13.44 | 13.34
2018-12-19 16:00 | 13.7 | 13.58
2018-12-19 16:30 | 14.92 | 14.8
2018-12-19 17:00 | 15.68 | 15.58
2018-12-19 17:30 | 16.46 | 16.36
2018-12-19 18:00 | 16.6 | 16.51
2018-12-19 18:30 | 16.57 | 16.49
2018-12-19 19:00 | 16.51 | 16.44
2018-12-19 19:30 | 16.52 | 16.43
2018-12-19 20:00 | 16.53 | 16.45
2018-12-19 20:30 | 16.06 | 15.99
2018-12-19 21:00 | 15.16 | 15.1
2018-12-19 21:30 | 14.06 | 14.01
2018-12-19 22:00 | 12.78 | 12.75
2018-12-19 22:30 | 11.75 | 11.74
2018-12-19 23:00 | 11.04 | 11.02
2018-12-19 23:30 | 9.63 | 9.62
2018-12-20 | 8.59 | 8.58
2018-12-20 00:30 | 7.81 | 7.8
2018-12-20 01:00 | 7.44 | 7.43
2018-12-20 01:30 | 7.07 | 7.06
2018-12-20 02:00 | 6.75 | 6.74
2018-12-20 02:30 | 6.64 | 6.63
2018-12-20 03:00 | 6.48 | 6.47
2018-12-20 03:30 | 6.31 | 6.3
2018-12-20 04:00 | 6.23 | 6.22
2018-12-20 04:30 | 6.3 | 6.29
2018-12-20 05:00 | 6.19 | 6.17
2018-12-20 05:30 | 6.26 | 6.22
2018-12-20 06:00 | 6.27 | 6.24
2018-12-20 06:30 | 6.29 | 6.27
2018-12-20 07:00 | 6.39 | 6.38
2018-12-20 07:30 | 7.12 | 7.11
2018-12-20 08:00 | 7.54 | 7.53
2018-12-20 08:30 | 6.53 | 6.51
2018-12-20 09:00 | 7.41 | 7.38
2018-12-20 09:30 | 7.43 | 7.37
2018-12-20 10:00 | 7.81 | 7.73
2018-12-20 10:30 | 8.43 | 8.32
2018-12-20 11:00 | 9.1 | 8.97
2018-12-20 11:30 | 10.14 | 9.99
2018-12-20 12:00 | 10.84 | 10.69
2018-12-20 12:30 | 11.72 | 11.56
2018-12-20 13:00 | 12.78 | 12.61
2018-12-20 13:30 | 14.01 | 13.82
2018-12-20 14:00 | 12.63 | 12.46
2018-12-20 14:30 | 13.83 | 13.59
2018-12-20 15:00 | 14.79 | 14.58
2018-12-20 15:30 | 16.17 | 15.97
2018-12-20 16:00 | 19.3 | 19.06
2018-12-20 16:30 | 20.46 | 20.2
2018-12-20 17:00 | 20.95 | 20.73
2018-12-20 17:30 | 21.63 | 21.42
2018-12-20 18:00 | 23.17 | 22.99
2018-12-20 18:30 | 21.51 | 21.31
2018-12-20 19:00 | 20.83 | 20.65
2018-12-20 19:30 | 20.14 | 19.95
2018-12-20 20:00 | 19.13 | 18.96
2018-12-20 20:30 | 21.75 | 21.59
2018-12-20 21:00 | 19.63 | 19.49
2018-12-20 21:30 | 17.25 | 17.14
2018-12-20 22:00 | 15.51 | 15.42
2018-12-20 22:30 | 13.63 | 13.57
2018-12-20 23:00 | 12.31 | 12.27
2018-12-20 23:30 | 11.19 | 11.16
2018-12-21 | 10.21 | 10.19
2018-12-21 00:30 | 9.34 | 9.32
2018-12-21 01:00 | 8.82 | 8.8
2018-12-21 01:30 | 8.38 | 8.36
2018-12-21 02:00 | 7.93 | 7.91
2018-12-21 02:30 | 7.72 | 7.7
2018-12-21 03:00 | 7.47 | 7.45
2018-12-21 03:30 | 7.28 | 7.26
2018-12-21 04:00 | 7.22 | 7.19
2018-12-21 04:30 | 7.14 | 7.12
2018-12-21 05:00 | 6.96 | 6.93
2018-12-21 05:30 | 6.87 | 6.85
2018-12-21 06:00 | 7.06 | 7.04
2018-12-21 06:30 | 7.36 | 7.34
2018-12-21 07:00 | 7.36 | 7.33
2018-12-21 07:30 | 8.16 | 8.13
2018-12-21 08:00 | 8.19 | 8.16
2018-12-21 08:30 | 8.09 | 8.05
2018-12-21 09:00 | 9.32 | 9.26
2018-12-21 09:30 | 10.08 | 9.98
2018-12-21 10:00 | 11.01 | 10.89
2018-12-21 10:30 | 12.09 | 11.91
2018-12-21 11:00 | 13 | 12.81
2018-12-21 11:30 | 13.93 | 13.73
2018-12-21 12:00 | 14.81 | 14.6
2018-12-21 12:30 | 15.8 | 15.57
2018-12-21 13:00 | 16.88 | 16.64
2018-12-21 13:30 | 17.55 | 17.3
2018-12-21 14:00 | 18.38 | 18.12
2018-12-21 14:30 | 19.25 | 19
2018-12-21 15:00 | 20.34 | 20.09
2018-12-21 15:30 | 21.36 | 21.11
2018-12-21 16:00 | 22.77 | 22.51
2018-12-21 16:30 | 24.08 | 23.82
2018-12-21 17:00 | 24.16 | 23.91
2018-12-21 17:30 | 22.78 | 22.56
2018-12-21 18:00 | 19.15 | 19
2018-12-21 18:30 | 17.94 | 17.84
2018-12-21 19:00 | 17.34 | 17.21
2018-12-21 19:30 | 16.5 | 16.4
2018-12-21 20:00 | 15.22 | 15.14
2018-12-21 20:30 | 15.49 | 15.42
2018-12-21 21:00 | 15.08 | 15.02
2018-12-21 21:30 | 14.12 | 14.08
2018-12-21 22:00 | 13.32 | 13.29
2018-12-21 22:30 | 11.9 | 11.87
2018-12-21 23:00 | 11.33 | 11.31
2018-12-21 23:30 | 10.28 | 10.26
2018-12-22 | 9.21 | 9.2
2018-12-22 00:30 | 8.7 | 8.68
2018-12-22 01:00 | 8.36 | 8.35
2018-12-22 01:30 | 7.9 | 7.88
2018-12-22 02:00 | 7.49 | 7.48
2018-12-22 02:30 | 7.3 | 7.28
2018-12-22 03:00 | 6.99 | 6.97
2018-12-22 03:30 | 6.79 | 6.77
2018-12-22 04:00 | 6.6 | 6.58
2018-12-22 04:30 | 6.65 | 6.63
2018-12-22 05:00 | 6.52 | 6.5
2018-12-22 05:30 | 6.41 | 6.38
2018-12-22 06:00 | 6.39 | 6.37
2018-12-22 06:30 | 6.31 | 6.29
2018-12-22 07:00 | 6.82 | 6.81
2018-12-22 07:30 | 6.6 | 6.58
2018-12-22 08:00 | 6.77 | 6.74
2018-12-22 08:30 | 6.84 | 6.81
2018-12-22 09:00 | 8.23 | 8.19
2018-12-22 09:30 | 9.4 | 9.37
2018-12-22 10:00 | 9.14 | 9.09
2018-12-22 10:30 | 9.2 | 9.14
2018-12-22 11:00 | 8.95 | 8.86
2018-12-22 11:30 | 10.58 | 10.48
2018-12-22 12:00 | 12.11 | 11.98
2018-12-22 12:30 | 13.11 | 12.95
2018-12-22 13:00 | 14.87 | 14.7
2018-12-22 13:30 | 16.46 | 16.28
2018-12-22 14:00 | 18.13 | 17.96
2018-12-22 14:30 | 18.18 | 18
2018-12-22 15:00 | 18.34 | 18.15
2018-12-22 15:30 | 19.72 | 19.52
2018-12-22 16:00 | 19.65 | 19.45
2018-12-22 16:30 | 20.25 | 20.04
2018-12-22 17:00 | 21.59 | 21.39
2018-12-22 17:30 | 20.35 | 20.18
2018-12-22 18:00 | 17.77 | 17.65
2018-12-22 18:30 | 16.45 | 16.36
2018-12-22 19:00 | 15.66 | 15.59
2018-12-22 19:30 | 15.18 | 15.1
2018-12-22 20:00 | 14.74 | 14.68
2018-12-22 20:30 | 14 | 13.96
2018-12-22 21:00 | 13.01 | 12.98
2018-12-22 21:30 | 12.2 | 12.18
2018-12-22 22:00 | 11.42 | 11.41
2018-12-22 22:30 | 10.76 | 10.75
2018-12-22 23:00 | 10.21 | 10.2
2018-12-22 23:30 | 9.07 | 9.06
2018-12-23 | 8.2 | 8.19
2018-12-23 00:30 | 7.57 | 7.56
2018-12-23 01:00 | 7.27 | 7.26
2018-12-23 01:30 | 6.82 | 6.81
2018-12-23 02:00 | 6.42 | 6.41
2018-12-23 02:30 | 6.23 | 6.22
2018-12-23 03:00 | 5.97 | 5.95
2018-12-23 03:30 | 5.79 | 5.77
2018-12-23 04:00 | 5.72 | 5.71
2018-12-23 04:30 | 5.6 | 5.59
2018-12-23 05:00 | 5.36 | 5.32
2018-12-23 05:30 | 5.28 | 5.21
2018-12-23 06:00 | 5.13 | 5.06
2018-12-23 06:30 | 5.04 | 4.98
2018-12-23 07:00 | 4.73 | 4.69
2018-12-23 07:30 | 4.72 | 4.7
2018-12-23 08:00 | 4.75 | 4.73
2018-12-23 08:30 | 4.56 | 4.54
2018-12-23 09:00 | 4.67 | 4.64
2018-12-23 09:30 | 4.91 | 4.87
2018-12-23 10:00 | 5.81 | 5.77
2018-12-23 10:30 | 5.44 | 5.39
2018-12-23 11:00 | 5.85 | 5.81
2018-12-23 11:30 | 5.96 | 5.91
2018-12-23 12:00 | 7.23 | 7.19
2018-12-23 12:30 | 8.64 | 8.61
2018-12-23 13:00 | 8.79 | 8.75
2018-12-23 13:30 | 8.59 | 8.55
2018-12-23 14:00 | 9 | 8.97
2018-12-23 14:30 | 8.74 | 8.71
2018-12-23 15:00 | 8.68 | 8.65
2018-12-23 15:30 | 8.89 | 8.86
2018-12-23 16:00 | 9.85 | 9.82
2018-12-23 16:30 | 10.11 | 10.09
2018-12-23 17:00 | 10.62 | 10.61
2018-12-23 17:30 | 10.93 | 10.91
2018-12-23 18:00 | 11.1 | 11.09
2018-12-23 18:30 | 11.18 | 11.16
2018-12-23 19:00 | 11.4 | 11.39
2018-12-23 19:30 | 11.52 | 11.5
2018-12-23 20:00 | 11.59 | 11.57
2018-12-23 20:30 | 11.54 | 11.53
2018-12-23 21:00 | 10.72 | 10.71
2018-12-23 21:30 | 10.11 | 10.1
2018-12-23 22:00 | 9.49 | 9.48
2018-12-23 22:30 | 9.15 | 9.14
2018-12-23 23:00 | 8.92 | 8.92
2018-12-23 23:30 | 7.84 | 7.83
2018-12-24 | 7.05 | 7.03
2018-12-24 00:30 | 6.42 | 6.4
2018-12-24 01:00 | 6.17 | 6.15
2018-12-24 01:30 | 5.69 | 5.66
2018-12-24 02:00 | 5.42 | 5.38
2018-12-24 02:30 | 5.2 | 5.16
2018-12-24 03:00 | 5.1 | 5.06
2018-12-24 03:30 | 5 | 4.96
2018-12-24 04:00 | 4.94 | 4.89
2018-12-24 04:30 | 5.15 | 5.11
2018-12-24 05:00 | 4.86 | 4.77
2018-12-24 05:30 | 4.87 | 4.76
2018-12-24 06:00 | 5.02 | 4.92
2018-12-24 06:30 | 4.92 | 4.83
2018-12-24 07:00 | 4.37 | 4.28
2018-12-24 07:30 | 4.44 | 4.39
2018-12-24 08:00 | 4.2 | 4.17
2018-12-24 08:30 | 4.59 | 4.57
2018-12-24 09:00 | 4.71 | 4.68
2018-12-24 09:30 | 4.55 | 4.5
2018-12-24 10:00 | 6.28 | 6.25
2018-12-24 10:30 | 6.11 | 6.07
2018-12-24 11:00 | 6.73 | 6.7
2018-12-24 11:30 | 5.07 | 5.02
2018-12-24 12:00 | 7.59 | 7.56
2018-12-24 12:30 | 5.91 | 5.87
2018-12-24 13:00 | 6.29 | 6.25
2018-12-24 13:30 | 6.05 | 6
2018-12-24 14:00 | 6.88 | 6.84
2018-12-24 14:30 | 7.12 | 7.07
2018-12-24 15:00 | 7.64 | 7.6
2018-12-24 15:30 | 7.31 | 7.27
2018-12-24 16:00 | 8.4 | 8.37
2018-12-24 16:30 | 9.35 | 9.32
2018-12-24 17:00 | 10.22 | 10.2
2018-12-24 17:30 | 10.78 | 10.76
2018-12-24 18:00 | 10.9 | 10.88
2018-12-24 18:30 | 11.09 | 11.08
2018-12-24 19:00 | 11.2 | 11.19
2018-12-24 19:30 | 11.33 | 11.31
2018-12-24 20:00 | 11.37 | 11.36
2018-12-24 20:30 | 11.02 | 11.01
2018-12-24 21:00 | 10.48 | 10.47
2018-12-24 21:30 | 9.98 | 9.97
2018-12-24 22:00 | 9.46 | 9.46
2018-12-24 22:30 | 9.17 | 9.16
2018-12-24 23:00 | 8.98 | 8.97
2018-12-24 23:30 | 8.07 | 8.06
2018-12-25 | 7.05 | 7.03
2018-12-25 00:30 | 6.4 | 6.38
2018-12-25 01:00 | 6.07 | 6.04
2018-12-25 01:30 | 5.62 | 5.59
2018-12-25 02:00 | 5.2 | 5.16
2018-12-25 02:30 | 4.97 | 4.92
2018-12-25 03:00 | 4.72 | 4.66
2018-12-25 03:30 | 4.65 | 4.59
2018-12-25 04:00 | 4.55 | 4.49
2018-12-25 04:30 | 4.5 | 4.43
2018-12-25 05:00 | 4.42 | 4.29
2018-12-25 05:30 | 4.35 | 4.18
2018-12-25 06:00 | 4.4 | 4.23
2018-12-25 06:30 | 4.33 | 4.17
2018-12-25 07:00 | 4.3 | 4.17
2018-12-25 07:30 | 4.29 | 4.18
2018-12-25 08:00 | 4.11 | 4.04
2018-12-25 08:30 | 4.14 | 4.1
2018-12-25 09:00 | 4.04 | 4.01
2018-12-25 09:30 | 3.97 | 3.95
2018-12-25 10:00 | 4.69 | 4.67
2018-12-25 10:30 | 5.28 | 5.27
2018-12-25 11:00 | 4.93 | 4.91
2018-12-25 11:30 | 5.08 | 5.06
2018-12-25 12:00 | 5.33 | 5.31
2018-12-25 12:30 | 5.58 | 5.56
2018-12-25 13:00 | 5.02 | 5
2018-12-25 13:30 | 5.7 | 5.67
2018-12-25 14:00 | 6.58 | 6.57
2018-12-25 14:30 | 6.88 | 6.87
2018-12-25 15:00 | 6.53 | 6.5
2018-12-25 15:30 | 6.98 | 6.96
2018-12-25 16:00 | 7.43 | 7.41
2018-12-25 16:30 | 8.3 | 8.29
2018-12-25 17:00 | 9.07 | 9.06
2018-12-25 17:30 | 9.62 | 9.61
2018-12-25 18:00 | 9.63 | 9.62
2018-12-25 18:30 | 9.59 | 9.58
2018-12-25 19:00 | 9.59 | 9.58
2018-12-25 19:30 | 9.7 | 9.69
2018-12-25 20:00 | 9.84 | 9.82
2018-12-25 20:30 | 9.73 | 9.72
2018-12-25 21:00 | 9.31 | 9.31
2018-12-25 21:30 | 8.92 | 8.91
2018-12-25 22:00 | 8.42 | 8.41
2018-12-25 22:30 | 8.17 | 8.17
2018-12-25 23:00 | 8.05 | 8.04
2018-12-25 23:30 | 7.15 | 7.13
2018-12-26 | 6.4 | 6.38
2018-12-26 00:30 | 5.88 | 5.86
2018-12-26 01:00 | 5.69 | 5.66
2018-12-26 01:30 | 5.3 | 5.27
2018-12-26 02:00 | 5.04 | 5
2018-12-26 02:30 | 4.9 | 4.86
2018-12-26 03:00 | 4.75 | 4.69
2018-12-26 03:30 | 4.66 | 4.61
2018-12-26 04:00 | 4.64 | 4.58
2018-12-26 04:30 | 4.62 | 4.56
2018-12-26 05:00 | 4.42 | 4.3
2018-12-26 05:30 | 4.36 | 4.21
2018-12-26 06:00 | 4.22 | 4.05
2018-12-26 06:30 | 3.89 | 3.72
2018-12-26 07:00 | 3.87 | 3.72
2018-12-26 07:30 | 3.93 | 3.82
2018-12-26 08:00 | 3.33 | 3.25
2018-12-26 08:30 | 3.13 | 3.07
2018-12-26 09:00 | 3.84 | 3.81
2018-12-26 09:30 | 4.06 | 4.02
2018-12-26 10:00 | 3.77 | 3.73
2018-12-26 10:30 | 4.19 | 4.15
2018-12-26 11:00 | 4.38 | 4.34
2018-12-26 11:30 | 4.52 | 4.48
2018-12-26 12:00 | 4.65 | 4.6
2018-12-26 12:30 | 4.83 | 4.78
2018-12-26 13:00 | 4.89 | 4.83
2018-12-26 13:30 | 5.53 | 5.47
2018-12-26 14:00 | 6 | 5.95
2018-12-26 14:30 | 6.54 | 6.49
2018-12-26 15:00 | 7.21 | 7.17
2018-12-26 15:30 | 8.06 | 8.02
2018-12-26 16:00 | 9.07 | 9.04
2018-12-26 16:30 | 9.91 | 9.89
2018-12-26 17:00 | 10.76 | 10.74
2018-12-26 17:30 | 11.4 | 11.37
2018-12-26 18:00 | 11.52 | 11.5
2018-12-26 18:30 | 11.33 | 11.32
2018-12-26 19:00 | 11.39 | 11.37
2018-12-26 19:30 | 11.63 | 11.61
2018-12-26 20:00 | 11.77 | 11.76
2018-12-26 20:30 | 11.53 | 11.52
2018-12-26 21:00 | 10.73 | 10.72
2018-12-26 21:30 | 10.07 | 10.06
2018-12-26 22:00 | 9.45 | 9.44
2018-12-26 22:30 | 8.98 | 8.97
2018-12-26 23:00 | 8.56 | 8.55
2018-12-26 23:30 | 7.57 | 7.56
2018-12-27 | 6.72 | 6.7
2018-12-27 00:30 | 6.06 | 6.04
2018-12-27 01:00 | 5.92 | 5.89
2018-12-27 01:30 | 5.55 | 5.51
2018-12-27 02:00 | 5.2 | 5.17
2018-12-27 02:30 | 5.03 | 4.98
2018-12-27 03:00 | 4.92 | 4.87
2018-12-27 03:30 | 4.9 | 4.85
2018-12-27 04:00 | 4.8 | 4.74
2018-12-27 04:30 | 4.8 | 4.74
2018-12-27 05:00 | 4.66 | 4.55
2018-12-27 05:30 | 4.7 | 4.56
2018-12-27 06:00 | 4.53 | 4.4
2018-12-27 06:30 | 4.3 | 4.19
2018-12-27 07:00 | 4.08 | 3.97
2018-12-27 07:30 | 3.88 | 3.81
2018-12-27 08:00 | 3.53 | 3.46
2018-12-27 08:30 | 3.45 | 3.41
2018-12-27 09:00 | 3.62 | 3.59
2018-12-27 09:30 | 4.08 | 4.03
2018-12-27 10:00 | 4.33 | 4.28
2018-12-27 10:30 | 4.78 | 4.73
2018-12-27 11:00 | 5.48 | 5.43
2018-12-27 11:30 | 5.45 | 5.41
2018-12-27 12:00 | 5.57 | 5.53
2018-12-27 12:30 | 5.92 | 5.88
2018-12-27 13:00 | 6.81 | 6.76
2018-12-27 13:30 | 6.95 | 6.9
2018-12-27 14:00 | 7.34 | 7.3
2018-12-27 14:30 | 7.91 | 7.86
2018-12-27 15:00 | 8.82 | 8.76
2018-12-27 15:30 | 9.7 | 9.65
2018-12-27 16:00 | 10.48 | 10.44
2018-12-27 16:30 | 11.51 | 11.46
2018-12-27 17:00 | 12.34 | 12.3
2018-12-27 17:30 | 12.71 | 12.67
2018-12-27 18:00 | 12.68 | 12.65
2018-12-27 18:30 | 12.67 | 12.64
2018-12-27 19:00 | 12.6 | 12.58
2018-12-27 19:30 | 12.46 | 12.45
2018-12-27 20:00 | 12.41 | 12.4
2018-12-27 20:30 | 12.09 | 12.08
2018-12-27 21:00 | 11.31 | 11.3
2018-12-27 21:30 | 10.34 | 10.33
2018-12-27 22:00 | 9.64 | 9.63
2018-12-27 22:30 | 9.08 | 9.07
2018-12-27 23:00 | 8.67 | 8.67
2018-12-27 23:30 | 7.77 | 7.76
2018-12-28 | 6.96 | 6.95
2018-12-28 00:30 | 6.28 | 6.26
2018-12-28 01:00 | 6 | 5.98
2018-12-28 01:30 | 5.6 | 5.57
2018-12-28 02:00 | 5.33 | 5.3
2018-12-28 02:30 | 5.13 | 5.09
2018-12-28 03:00 | 5 | 4.95
2018-12-28 03:30 | 4.93 | 4.89
2018-12-28 04:00 | 4.83 | 4.78
2018-12-28 04:30 | 4.84 | 4.79
2018-12-28 05:00 | 4.75 | 4.66
2018-12-28 05:30 | 4.83 | 4.7
2018-12-28 06:00 | 4.66 | 4.54
2018-12-28 06:30 | 4.47 | 4.36
2018-12-28 07:00 | 4.4 | 4.33
2018-12-28 07:30 | 4.43 | 4.38
2018-12-28 08:00 | 4.28 | 4.25
2018-12-28 08:30 | 4.61 | 4.58
2018-12-28 09:00 | 4.83 | 4.8
2018-12-28 09:30 | 5.14 | 5.11
2018-12-28 10:00 | 5.6 | 5.56
2018-12-28 10:30 | 5.81 | 5.77
2018-12-28 11:00 | 5.99 | 5.95
2018-12-28 11:30 | 6.23 | 6.19
2018-12-28 12:00 | 7.1 | 7.07
2018-12-28 12:30 | 6.77 | 6.73
2018-12-28 13:00 | 6.57 | 6.52
2018-12-28 13:30 | 7.55 | 7.5
2018-12-28 14:00 | 8.06 | 8.02
2018-12-28 14:30 | 8.35 | 8.31
2018-12-28 15:00 | 9.12 | 9.07
2018-12-28 15:30 | 9.7 | 9.66
2018-12-28 16:00 | 10.5 | 10.47
2018-12-28 16:30 | 11.15 | 11.11
2018-12-28 17:00 | 11.81 | 11.78
2018-12-28 17:30 | 12.03 | 12
2018-12-28 18:00 | 12.33 | 12.31
2018-12-28 18:30 | 12.25 | 12.23
2018-12-28 19:00 | 12.3 | 12.28
2018-12-28 19:30 | 12.35 | 12.33
2018-12-28 20:00 | 12.46 | 12.44
2018-12-28 20:30 | 12.01 | 12
2018-12-28 21:00 | 11.27 | 11.25
2018-12-28 21:30 | 10.41 | 10.4
2018-12-28 22:00 | 9.67 | 9.66
2018-12-28 22:30 | 9.24 | 9.23
2018-12-28 23:00 | 8.85 | 8.85
2018-12-28 23:30 | 7.86 | 7.85
2018-12-29 | 6.96 | 6.95
2018-12-29 00:30 | 6.32 | 6.3
2018-12-29 01:00 | 6.05 | 6.03
2018-12-29 01:30 | 5.75 | 5.72
2018-12-29 02:00 | 5.37 | 5.34
2018-12-29 02:30 | 5.2 | 5.17
2018-12-29 03:00 | 5.13 | 5.09
2018-12-29 03:30 | 5.08 | 5.04
2018-12-29 04:00 | 4.96 | 4.92
2018-12-29 04:30 | 4.85 | 4.8
2018-12-29 05:00 | 4.75 | 4.66
2018-12-29 05:30 | 4.67 | 4.54
2018-12-29 06:00 | 4.51 | 4.38
2018-12-29 06:30 | 4.25 | 4.14
2018-12-29 07:00 | 4.27 | 4.2
2018-12-29 07:30 | 4.59 | 4.54
2018-12-29 08:00 | 4.7 | 4.67
2018-12-29 08:30 | 4.14 | 4.11
2018-12-29 09:00 | 4.35 | 4.32
2018-12-29 09:30 | 5.46 | 5.42
2018-12-29 10:00 | 6.42 | 6.37
2018-12-29 10:30 | 5.62 | 5.57
2018-12-29 11:00 | 5.84 | 5.78
2018-12-29 11:30 | 6.51 | 6.46
2018-12-29 12:00 | 6.41 | 6.35
2018-12-29 12:30 | 6.31 | 6.24
2018-12-29 13:00 | 6.81 | 6.75
2018-12-29 13:30 | 7.5 | 7.44
2018-12-29 14:00 | 8.21 | 8.16
2018-12-29 14:30 | 8.78 | 8.73
2018-12-29 15:00 | 9.53 | 9.48
2018-12-29 15:30 | 10.44 | 10.39
2018-12-29 16:00 | 11.25 | 11.2
2018-12-29 16:30 | 12.68 | 12.64
2018-12-29 17:00 | 12.96 | 12.92
2018-12-29 17:30 | 13.41 | 13.38
2018-12-29 18:00 | 13.31 | 13.28
2018-12-29 18:30 | 13 | 12.97
2018-12-29 19:00 | 13.03 | 13.01
2018-12-29 19:30 | 13.25 | 13.22
2018-12-29 20:00 | 13.22 | 13.2
2018-12-29 20:30 | 12.9 | 12.88
2018-12-29 21:00 | 12.08 | 12.07
2018-12-29 21:30 | 11.33 | 11.31
2018-12-29 22:00 | 10.68 | 10.67
2018-12-29 22:30 | 10.23 | 10.22
2018-12-29 23:00 | 9.88 | 9.87
2018-12-29 23:30 | 8.94 | 8.93
2018-12-30 | 8.04 | 8.03
2018-12-30 00:30 | 7.31 | 7.3
2018-12-30 01:00 | 6.91 | 6.9
2018-12-30 01:30 | 6.48 | 6.47
2018-12-30 02:00 | 6.17 | 6.16
2018-12-30 02:30 | 5.96 | 5.95
2018-12-30 03:00 | 5.75 | 5.74
2018-12-30 03:30 | 5.69 | 5.67
2018-12-30 04:00 | 5.57 | 5.55
2018-12-30 04:30 | 5.39 | 5.37
2018-12-30 05:00 | 5.25 | 5.2
2018-12-30 05:30 | 5.1 | 5.02
2018-12-30 06:00 | 4.88 | 4.81
2018-12-30 06:30 | 5.23 | 5.18
2018-12-30 07:00 | 4.74 | 4.7
2018-12-30 07:30 | 4.74 | 4.71
2018-12-30 08:00 | 6.38 | 6.36
2018-12-30 08:30 | 5.97 | 5.94
2018-12-30 09:00 | 5.32 | 5.29
2018-12-30 09:30 | 5.9 | 5.86
2018-12-30 10:00 | 6.63 | 6.58
2018-12-30 10:30 | 7.09 | 7.03
2018-12-30 11:00 | 7.73 | 7.67
2018-12-30 11:30 | 8.25 | 8.2
2018-12-30 12:00 | 8.08 | 8.02
2018-12-30 12:30 | 8.69 | 8.62
2018-12-30 13:00 | 9.45 | 9.37
2018-12-30 13:30 | 10.02 | 9.93
2018-12-30 14:00 | 10.73 | 10.64
2018-12-30 14:30 | 11.06 | 10.98
2018-12-30 15:00 | 11.84 | 11.76
2018-12-30 15:30 | 12.79 | 12.7
2018-12-30 16:00 | 13.81 | 13.72
2018-12-30 16:30 | 14.46 | 14.39
2018-12-30 17:00 | 15.33 | 15.25
2018-12-30 17:30 | 15.54 | 15.48
2018-12-30 18:00 | 15.68 | 15.63
2018-12-30 18:30 | 15.48 | 15.43
2018-12-30 19:00 | 15.12 | 15.07
2018-12-30 19:30 | 14.9 | 14.84
2018-12-30 20:00 | 14.79 | 14.75
2018-12-30 20:30 | 14.14 | 14.11
2018-12-30 21:00 | 12.89 | 12.87
2018-12-30 21:30 | 11.89 | 11.87
2018-12-30 22:00 | 11.12 | 11.11
2018-12-30 22:30 | 10.49 | 10.48
2018-12-30 23:00 | 9.97 | 9.96
2018-12-30 23:30 | 8.89 | 8.88
2018-12-31 | 7.91 | 7.9
2018-12-31 00:30 | 7.21 | 7.2
2018-12-31 01:00 | 6.87 | 6.86
2018-12-31 01:30 | 6.42 | 6.41
2018-12-31 02:00 | 6.05 | 6.03
2018-12-31 02:30 | 5.72 | 5.71
2018-12-31 03:00 | 5.61 | 5.59
2018-12-31 03:30 | 5.5 | 5.48
2018-12-31 04:00 | 5.38 | 5.36
2018-12-31 04:30 | 5.39 | 5.37
2018-12-31 05:00 | 5.25 | 5.2
2018-12-31 05:30 | 5.11 | 5.02
2018-12-31 06:00 | 5.01 | 4.92
2018-12-31 06:30 | 4.86 | 4.8
2018-12-31 07:00 | 4.98 | 4.94
2018-12-31 07:30 | 4.89 | 4.87
2018-12-31 08:00 | 4.97 | 4.94
2018-12-31 08:30 | 6.11 | 6.1
2018-12-31 09:00 | 6.71 | 6.69
2018-12-31 09:30 | 5.92 | 5.88
2018-12-31 10:00 | 6.71 | 6.67
2018-12-31 10:30 | 7.4 | 7.35
2018-12-31 11:00 | 7.54 | 7.5
2018-12-31 11:30 | 8.16 | 8.12
2018-12-31 12:00 | 8.31 | 8.26
2018-12-31 12:30 | 8.14 | 8.08
2018-12-31 13:00 | 8.85 | 8.78
2018-12-31 13:30 | 9.31 | 9.23
2018-12-31 14:00 | 10.4 | 10.34
2018-12-31 14:30 | 10.64 | 10.56
2018-12-31 15:00 | 11.33 | 11.25
2018-12-31 15:30 | 12.1 | 12.03
2018-12-31 16:00 | 12.87 | 12.8
2018-12-31 16:30 | 13.64 | 13.58
2018-12-31 17:00 | 14.37 | 14.31
2018-12-31 17:30 | 14.64 | 14.59
2018-12-31 18:00 | 14.47 | 14.43
2018-12-31 18:30 | 13.94 | 13.91
2018-12-31 19:00 | 13.59 | 13.57
2018-12-31 19:30 | 13.21 | 13.17
2018-12-31 20:00 | 13.03 | 12.99
2018-12-31 20:30 | 12.45 | 12.42
2018-12-31 21:00 | 11.62 | 11.6
2018-12-31 21:30 | 10.79 | 10.78
2018-12-31 22:00 | 10.34 | 10.32
2018-12-31 22:30 | 10.17 | 10.16
2018-12-31 23:00 | 9.9 | 9.89
2018-12-31 23:30 | 8.98 | 8.97
2019-01-01 | 8.21 | 8.2
2019-01-01 00:30 | 7.51 | 7.49
2019-01-01 01:00 | 7.29 | 7.28
2019-01-01 01:30 | 6.91 | 6.9
2019-01-01 02:00 | 6.5 | 6.49
2019-01-01 02:30 | 6.27 | 6.25
2019-01-01 03:00 | 6.05 | 6.04
2019-01-01 03:30 | 5.89 | 5.88
2019-01-01 04:00 | 5.7 | 5.68
2019-01-01 04:30 | 5.63 | 5.62
2019-01-01 05:00 | 5.34 | 5.3
2019-01-01 05:30 | 5.13 | 5.05
2019-01-01 06:00 | 4.87 | 4.78
2019-01-01 06:30 | 4.65 | 4.56
2019-01-01 07:00 | 4.53 | 4.48
2019-01-01 07:30 | 4.46 | 4.43
2019-01-01 08:00 | 4.69 | 4.67
2019-01-01 08:30 | 5.53 | 5.51
2019-01-01 09:00 | 4.96 | 4.93
2019-01-01 09:30 | 5.36 | 5.33
2019-01-01 10:00 | 6.28 | 6.23
2019-01-01 10:30 | 7.02 | 6.97
2019-01-01 11:00 | 7.72 | 7.68
2019-01-01 11:30 | 8.24 | 8.2
2019-01-01 12:00 | 8.86 | 8.8
2019-01-01 12:30 | 9.43 | 9.37
2019-01-01 13:00 | 10.07 | 10
2019-01-01 13:30 | 10.51 | 10.44
2019-01-01 14:00 | 11.35 | 11.28
2019-01-01 14:30 | 12.07 | 11.98
2019-01-01 15:00 | 12.77 | 12.68
2019-01-01 15:30 | 13.52 | 13.43
2019-01-01 16:00 | 15.2 | 15.13
2019-01-01 16:30 | 14.34 | 14.26
2019-01-01 17:00 | 15.41 | 15.34
2019-01-01 17:30 | 15.95 | 15.89
2019-01-01 18:00 | 15.19 | 15.15
2019-01-01 18:30 | 14.78 | 14.75
2019-01-01 19:00 | 14.6 | 14.58
2019-01-01 19:30 | 14.44 | 14.41
2019-01-01 20:00 | 14.28 | 14.25
2019-01-01 20:30 | 13.78 | 13.75
2019-01-01 21:00 | 12.7 | 12.69
2019-01-01 21:30 | 11.8 | 11.79
2019-01-01 22:00 | 11.05 | 11.04
2019-01-01 22:30 | 10.48 | 10.47
2019-01-01 23:00 | 9.97 | 9.96
2019-01-01 23:30 | 8.8 | 8.79
2019-01-02 | 7.81 | 7.8
2019-01-02 00:30 | 7.14 | 7.13
2019-01-02 01:00 | 6.86 | 6.85
2019-01-02 01:30 | 6.38 | 6.37
2019-01-02 02:00 | 6.07 | 6.05
2019-01-02 02:30 | 5.79 | 5.78
2019-01-02 03:00 | 5.71 | 5.7
2019-01-02 03:30 | 5.63 | 5.61
2019-01-02 04:00 | 5.59 | 5.57
2019-01-02 04:30 | 5.56 | 5.55
2019-01-02 05:00 | 5.48 | 5.44
2019-01-02 05:30 | 5.41 | 5.34
2019-01-02 06:00 | 5.49 | 5.43
2019-01-02 06:30 | 5.8 | 5.78
2019-01-02 07:00 | 5.87 | 5.86
2019-01-02 07:30 | 5.72 | 5.72
2019-01-02 08:00 | 5.95 | 5.95
2019-01-02 08:30 | 6.38 | 6.37
2019-01-02 09:00 | 5.33 | 5.31
2019-01-02 09:30 | 5.96 | 5.93
2019-01-02 10:00 | 6.11 | 6.07
2019-01-02 10:30 | 6.84 | 6.81
2019-01-02 11:00 | 7.45 | 7.4
2019-01-02 11:30 | 8.63 | 8.58
2019-01-02 12:00 | 9.67 | 9.61
2019-01-02 12:30 | 10.53 | 10.47
2019-01-02 13:00 | 10.35 | 10.26
2019-01-02 13:30 | 11.13 | 11.03
2019-01-02 14:00 | 12.19 | 12.08
2019-01-02 14:30 | 12.15 | 12.05
2019-01-02 15:00 | 11.94 | 11.85
2019-01-02 15:30 | 12.9 | 12.79
2019-01-02 16:00 | 13.6 | 13.49
2019-01-02 16:30 | 14.3 | 14.2
2019-01-02 17:00 | 15.25 | 15.16
2019-01-02 17:30 | 15.86 | 15.78
2019-01-02 18:00 | 15.87 | 15.8
2019-01-02 18:30 | 15.69 | 15.64
2019-01-02 19:00 | 15.37 | 15.32
2019-01-02 19:30 | 15.03 | 14.98
2019-01-02 20:00 | 14.88 | 14.84
2019-01-02 20:30 | 14.33 | 14.3
2019-01-02 21:00 | 13.29 | 13.27
2019-01-02 21:30 | 12.17 | 12.15
2019-01-02 22:00 | 11.3 | 11.29
2019-01-02 22:30 | 10.71 | 10.7
2019-01-02 23:00 | 10.23 | 10.22
2019-01-02 23:30 | 9 | 8.98
2019-01-03 | 7.92 | 7.91
2019-01-03 00:30 | 7.24 | 7.23
2019-01-03 01:00 | 6.85 | 6.84
2019-01-03 01:30 | 6.42 | 6.41
2019-01-03 02:00 | 6.13 | 6.12
2019-01-03 02:30 | 5.96 | 5.95
2019-01-03 03:00 | 5.76 | 5.75
2019-01-03 03:30 | 5.66 | 5.64
2019-01-03 04:00 | 5.56 | 5.54
2019-01-03 04:30 | 5.59 | 5.57
2019-01-03 05:00 | 5.41 | 5.38
2019-01-03 05:30 | 5.71 | 5.66
2019-01-03 06:00 | 6.25 | 6.21
2019-01-03 06:30 | 6.28 | 6.26
2019-01-03 07:00 | 5.5 | 5.48
2019-01-03 07:30 | 5.59 | 5.58
2019-01-03 08:00 | 6.01 | 6.01
2019-01-03 08:30 | 5.51 | 5.51
2019-01-03 09:00 | 5.72 | 5.71
2019-01-03 09:30 | 5.9 | 5.88
2019-01-03 10:00 | 7.17 | 7.15
2019-01-03 10:30 | 6.94 | 6.89
2019-01-03 11:00 | 8.84 | 8.8
2019-01-03 11:30 | 10.18 | 10.13
2019-01-03 12:00 | 10.42 | 10.37
2019-01-03 12:30 | 9.14 | 9.07
2019-01-03 13:00 | 8.71 | 8.61
2019-01-03 13:30 | 10.19 | 10.1
2019-01-03 14:00 | 10.4 | 10.31
2019-01-03 14:30 | 11.37 | 11.28
2019-01-03 15:00 | 11.34 | 11.25
2019-01-03 15:30 | 12.72 | 12.63
2019-01-03 16:00 | 13.43 | 13.34
2019-01-03 16:30 | 14.23 | 14.14
2019-01-03 17:00 | 15.04 | 14.96
2019-01-03 17:30 | 15.85 | 15.78
2019-01-03 18:00 | 15.7 | 15.63
2019-01-03 18:30 | 15.69 | 15.64
2019-01-03 19:00 | 15.73 | 15.68
2019-01-03 19:30 | 15.77 | 15.7
2019-01-03 20:00 | 15.85 | 15.79
2019-01-03 20:30 | 15.32 | 15.27
2019-01-03 21:00 | 14.37 | 14.33
2019-01-03 21:30 | 13.44 | 13.41
2019-01-03 22:00 | 12.42 | 12.41
2019-01-03 22:30 | 11.57 | 11.56
2019-01-03 23:00 | 11.07 | 11.06
2019-01-03 23:30 | 9.87 | 9.85
2019-01-04 | 8.76 | 8.75
2019-01-04 00:30 | 8.09 | 8.08
2019-01-04 01:00 | 7.85 | 7.84
2019-01-04 01:30 | 7.24 | 7.23
2019-01-04 02:00 | 6.75 | 6.74
2019-01-04 02:30 | 6.38 | 6.36
2019-01-04 03:00 | 6.23 | 6.21
2019-01-04 03:30 | 6.41 | 6.4
2019-01-04 04:00 | 6.12 | 6.11
2019-01-04 04:30 | 6.09 | 6.08
2019-01-04 05:00 | 6.06 | 6.05
2019-01-04 05:30 | 5.99 | 5.96
2019-01-04 06:00 | 5.83 | 5.79
2019-01-04 06:30 | 6.1 | 6.07
2019-01-04 07:00 | 5.9 | 5.88
2019-01-04 07:30 | 6.06 | 6.05
2019-01-04 08:00 | 6.21 | 6.2
2019-01-04 08:30 | 6.41 | 6.39
2019-01-04 09:00 | 6.97 | 6.95
2019-01-04 09:30 | 7.6 | 7.57
2019-01-04 10:00 | 8.67 | 8.64
2019-01-04 10:30 | 8.08 | 8.06
2019-01-04 11:00 | 7.67 | 7.64
2019-01-04 11:30 | 8.08 | 8.03
2019-01-04 12:00 | 7.44 | 7.38
2019-01-04 12:30 | 8.17 | 8.1
2019-01-04 13:00 | 9.77 | 9.7
2019-01-04 13:30 | 10.6 | 10.52
2019-01-04 14:00 | 10.67 | 10.58
2019-01-04 14:30 | 10.9 | 10.82
2019-01-04 15:00 | 11.53 | 11.46
2019-01-04 15:30 | 11.76 | 11.69
2019-01-04 16:00 | 11.98 | 11.91
2019-01-04 16:30 | 13.08 | 13.02
2019-01-04 17:00 | 14.02 | 13.96
2019-01-04 17:30 | 14.07 | 14.02
2019-01-04 18:00 | 14.29 | 14.24
2019-01-04 18:30 | 14.22 | 14.18
2019-01-04 19:00 | 14.38 | 14.35
2019-01-04 19:30 | 14.52 | 14.47
2019-01-04 20:00 | 14.65 | 14.61
2019-01-04 20:30 | 14.1 | 14.06
2019-01-04 21:00 | 13.32 | 13.29
2019-01-04 21:30 | 12.32 | 12.3
2019-01-04 22:00 | 11.53 | 11.52
2019-01-04 22:30 | 10.92 | 10.91
2019-01-04 23:00 | 10.56 | 10.55
2019-01-04 23:30 | 9.31 | 9.3
2019-01-05 | 8.33 | 8.32
2019-01-05 00:30 | 7.69 | 7.68
2019-01-05 01:00 | 7.22 | 7.21
2019-01-05 01:30 | 6.77 | 6.76
2019-01-05 02:00 | 6.4 | 6.39
2019-01-05 02:30 | 6.27 | 6.25
2019-01-05 03:00 | 6.02 | 6.01
2019-01-05 03:30 | 5.95 | 5.94
2019-01-05 04:00 | 5.78 | 5.76
2019-01-05 04:30 | 5.68 | 5.67
2019-01-05 05:00 | 5.47 | 5.44
2019-01-05 05:30 | 5.36 | 5.29
2019-01-05 06:00 | 5.14 | 5.08
2019-01-05 06:30 | 5.11 | 5.06
2019-01-05 07:00 | 5.17 | 5.13
2019-01-05 07:30 | 5.46 | 5.43
2019-01-05 08:00 | 5.29 | 5.26
2019-01-05 08:30 | 6.02 | 5.99
2019-01-05 09:00 | 5.83 | 5.79
2019-01-05 09:30 | 7.04 | 6.99
2019-01-05 10:00 | 7.79 | 7.74
2019-01-05 10:30 | 7.95 | 7.91
2019-01-05 11:00 | 7.98 | 7.93
2019-01-05 11:30 | 7.81 | 7.75
2019-01-05 12:00 | 10.08 | 10.03
2019-01-05 12:30 | 9.69 | 9.63
2019-01-05 13:00 | 9.43 | 9.35
2019-01-05 13:30 | 10.14 | 10.05
2019-01-05 14:00 | 11.24 | 11.14
2019-01-05 14:30 | 14.26 | 14.19
2019-01-05 15:00 | 13.51 | 13.43
2019-01-05 15:30 | 13.01 | 12.94
2019-01-05 16:00 | 13.97 | 13.9
2019-01-05 16:30 | 14.19 | 14.12
2019-01-05 17:00 | 13.86 | 13.81
2019-01-05 17:30 | 13.83 | 13.79
2019-01-05 18:00 | 14.05 | 14.01
2019-01-05 18:30 | 14 | 13.97
2019-01-05 19:00 | 13.96 | 13.93
2019-01-05 19:30 | 14.08 | 14.04
2019-01-05 20:00 | 14.24 | 14.19
2019-01-05 20:30 | 13.86 | 13.82
2019-01-05 21:00 | 13.03 | 13
2019-01-05 21:30 | 12.34 | 12.32
2019-01-05 22:00 | 11.7 | 11.68
2019-01-05 22:30 | 11 | 10.99
2019-01-05 23:00 | 10.54 | 10.52
2019-01-05 23:30 | 9.54 | 9.53
2019-01-06 | 8.61 | 8.6
2019-01-06 00:30 | 7.89 | 7.88
2019-01-06 01:00 | 7.5 | 7.49
2019-01-06 01:30 | 7.07 | 7.06
2019-01-06 02:00 | 6.68 | 6.67
2019-01-06 02:30 | 6.48 | 6.47
2019-01-06 03:00 | 6.33 | 6.32
2019-01-06 03:30 | 6.36 | 6.35
2019-01-06 04:00 | 6.15 | 6.14
2019-01-06 04:30 | 6.03 | 6.01
2019-01-06 05:00 | 5.89 | 5.88
2019-01-06 05:30 | 5.69 | 5.64
2019-01-06 06:00 | 5.48 | 5.42
2019-01-06 06:30 | 5.42 | 5.37
2019-01-06 07:00 | 5.49 | 5.46
2019-01-06 07:30 | 5.3 | 5.28
2019-01-06 08:00 | 5.8 | 5.78
2019-01-06 08:30 | 6.69 | 6.67
2019-01-06 09:00 | 7.29 | 7.27
2019-01-06 09:30 | 7.35 | 7.31
2019-01-06 10:00 | 8.68 | 8.64
2019-01-06 10:30 | 9.02 | 8.97
2019-01-06 11:00 | 10.04 | 10
2019-01-06 11:30 | 10.47 | 10.42
2019-01-06 12:00 | 10.02 | 9.95
2019-01-06 12:30 | 11.07 | 11
2019-01-06 13:00 | 11.74 | 11.65
2019-01-06 13:30 | 12.39 | 12.29
2019-01-06 14:00 | 12.95 | 12.84
2019-01-06 14:30 | 13.86 | 13.76
2019-01-06 15:00 | 14.88 | 14.79
2019-01-06 15:30 | 14.98 | 14.9
2019-01-06 16:00 | 14.82 | 14.75
2019-01-06 16:30 | 15.6 | 15.53
2019-01-06 17:00 | 14.88 | 14.82
2019-01-06 17:30 | 15.76 | 15.71
2019-01-06 18:00 | 15.77 | 15.72
2019-01-06 18:30 | 15.59 | 15.55
2019-01-06 19:00 | 15.39 | 15.35
2019-01-06 19:30 | 15.24 | 15.2
2019-01-06 20:00 | 15.3 | 15.26
2019-01-06 20:30 | 14.91 | 14.87
2019-01-06 21:00 | 13.95 | 13.92
2019-01-06 21:30 | 12.76 | 12.74
2019-01-06 22:00 | 11.88 | 11.87
2019-01-06 22:30 | 10.97 | 10.96
2019-01-06 23:00 | 10.44 | 10.43
2019-01-06 23:30 | 9.26 | 9.25
2019-01-07 | 8.31 | 8.3
2019-01-07 00:30 | 7.64 | 7.63
2019-01-07 01:00 | 7.31 | 7.3
2019-01-07 01:30 | 7.01 | 7
2019-01-07 02:00 | 6.66 | 6.65
2019-01-07 02:30 | 6.39 | 6.38
2019-01-07 03:00 | 6.26 | 6.25
2019-01-07 03:30 | 6.25 | 6.23
2019-01-07 04:00 | 6.13 | 6.12
2019-01-07 04:30 | 6.15 | 6.13
2019-01-07 05:00 | 6.05 | 6.03
2019-01-07 05:30 | 6.05 | 6.02
2019-01-07 06:00 | 6.35 | 6.32
2019-01-07 06:30 | 6.7 | 6.68
2019-01-07 07:00 | 7.05 | 7.04
2019-01-07 07:30 | 7.36 | 7.35
2019-01-07 08:00 | 7.5 | 7.49
2019-01-07 08:30 | 7.04 | 7.03
2019-01-07 09:00 | 7.57 | 7.56
2019-01-07 09:30 | 6.86 | 6.85
2019-01-07 10:00 | 7.48 | 7.47
2019-01-07 10:30 | 7.97 | 7.94
2019-01-07 11:00 | 6.61 | 6.58
2019-01-07 11:30 | 7.07 | 7.04
2019-01-07 12:00 | 8.26 | 8.23
2019-01-07 12:30 | 8.89 | 8.86
2019-01-07 13:00 | 9.44 | 9.41
2019-01-07 13:30 | 10.27 | 10.24
2019-01-07 14:00 | 11.19 | 11.17
2019-01-07 14:30 | 11.18 | 11.16
2019-01-07 15:00 | 10.51 | 10.49
2019-01-07 15:30 | 10.83 | 10.81
2019-01-07 16:00 | 11.36 | 11.34
2019-01-07 16:30 | 11.63 | 11.61
2019-01-07 17:00 | 12.13 | 12.11
2019-01-07 17:30 | 12.54 | 12.53
2019-01-07 18:00 | 12.86 | 12.85
2019-01-07 18:30 | 13.35 | 13.34
2019-01-07 19:00 | 13.97 | 13.96
2019-01-07 19:30 | 14.24 | 14.22
2019-01-07 20:00 | 14.18 | 14.16
2019-01-07 20:30 | 14.02 | 14
2019-01-07 21:00 | 12.87 | 12.86
2019-01-07 21:30 | 11.82 | 11.81
2019-01-07 22:00 | 10.74 | 10.73
2019-01-07 22:30 | 10.2 | 10.19
2019-01-07 23:00 | 9.85 | 9.84
2019-01-07 23:30 | 8.95 | 8.94
2019-01-08 | 7.96 | 7.95
2019-01-08 00:30 | 7.32 | 7.31
2019-01-08 01:00 | 7 | 6.99
2019-01-08 01:30 | 6.55 | 6.54
2019-01-08 02:00 | 6.22 | 6.21
2019-01-08 02:30 | 6.06 | 6.05
2019-01-08 03:00 | 5.95 | 5.94
2019-01-08 03:30 | 5.86 | 5.85
2019-01-08 04:00 | 5.87 | 5.86
2019-01-08 04:30 | 5.83 | 5.81
2019-01-08 05:00 | 5.89 | 5.87
2019-01-08 05:30 | 5.89 | 5.86
2019-01-08 06:00 | 6.04 | 6
2019-01-08 06:30 | 6.33 | 6.3
2019-01-08 07:00 | 6.53 | 6.5
2019-01-08 07:30 | 6.91 | 6.89
2019-01-08 08:00 | 7.09 | 7.07
2019-01-08 08:30 | 6.65 | 6.63
2019-01-08 09:00 | 6.6 | 6.58
2019-01-08 09:30 | 6.53 | 6.51
2019-01-08 10:00 | 7.11 | 7.08
2019-01-08 10:30 | 7.66 | 7.64
2019-01-08 11:00 | 7.03 | 7.01
2019-01-08 11:30 | 7.01 | 6.98
2019-01-08 12:00 | 7.15 | 7.13
2019-01-08 12:30 | 7.33 | 7.3
2019-01-08 13:00 | 8.48 | 8.45
2019-01-08 13:30 | 8.13 | 8.11
2019-01-08 14:00 | 8.58 | 8.56
2019-01-08 14:30 | 8.47 | 8.45
2019-01-08 15:00 | 9.25 | 9.23
2019-01-08 15:30 | 9.19 | 9.17
2019-01-08 16:00 | 10.39 | 10.36
2019-01-08 16:30 | 11.54 | 11.52
2019-01-08 17:00 | 12.03 | 12.02
2019-01-08 17:30 | 12.6 | 12.58
2019-01-08 18:00 | 13.35 | 13.33
2019-01-08 18:30 | 13.9 | 13.89
2019-01-08 19:00 | 14.28 | 14.26
2019-01-08 19:30 | 14.53 | 14.5
2019-01-08 20:00 | 14.74 | 14.7
2019-01-08 20:30 | 14.36 | 14.33
2019-01-08 21:00 | 13.39 | 13.37
2019-01-08 21:30 | 12.44 | 12.43
2019-01-08 22:00 | 11.35 | 11.34
2019-01-08 22:30 | 10.48 | 10.47
2019-01-08 23:00 | 9.97 | 9.96
2019-01-08 23:30 | 8.95 | 8.94
2019-01-09 | 7.88 | 7.87
2019-01-09 00:30 | 7.26 | 7.25
2019-01-09 01:00 | 6.88 | 6.87
2019-01-09 01:30 | 6.5 | 6.49
2019-01-09 02:00 | 6.15 | 6.14
2019-01-09 02:30 | 6.05 | 6.04
2019-01-09 03:00 | 5.96 | 5.94
2019-01-09 03:30 | 5.85 | 5.84
2019-01-09 04:00 | 5.89 | 5.88
2019-01-09 04:30 | 5.9 | 5.89
2019-01-09 05:00 | 5.9 | 5.88
2019-01-09 05:30 | 5.84 | 5.79
2019-01-09 06:00 | 5.9 | 5.86
2019-01-09 06:30 | 6.17 | 6.15
2019-01-09 07:00 | 6.98 | 6.97
2019-01-09 07:30 | 7.62 | 7.62
2019-01-09 08:00 | 7.37 | 7.37
2019-01-09 08:30 | 7.22 | 7.21
2019-01-09 09:00 | 7.24 | 7.22
2019-01-09 09:30 | 8.55 | 8.54
2019-01-09 10:00 | 7.78 | 7.77
2019-01-09 10:30 | 7.85 | 7.83
2019-01-09 11:00 | 8.69 | 8.68
2019-01-09 11:30 | 6.68 | 6.65
2019-01-09 12:00 | 8.77 | 8.75
2019-01-09 12:30 | 10.47 | 10.45
2019-01-09 13:00 | 10.6 | 10.58
2019-01-09 13:30 | 10.29 | 10.28
2019-01-09 14:00 | 8.92 | 8.89
2019-01-09 14:30 | 9.58 | 9.56
2019-01-09 15:00 | 8.94 | 8.91
2019-01-09 15:30 | 9.68 | 9.65
2019-01-09 16:00 | 9.78 | 9.74
2019-01-09 16:30 | 11.14 | 11.1
2019-01-09 17:00 | 12.76 | 12.73
2019-01-09 17:30 | 13.29 | 13.27
2019-01-09 18:00 | 14.06 | 14.02
2019-01-09 18:30 | 14.33 | 14.3
2019-01-09 19:00 | 14.66 | 14.63
2019-01-09 19:30 | 14.91 | 14.86
2019-01-09 20:00 | 15.07 | 15.02
2019-01-09 20:30 | 14.77 | 14.73
2019-01-09 21:00 | 13.73 | 13.71
2019-01-09 21:30 | 12.77 | 12.76
2019-01-09 22:00 | 11.72 | 11.71
2019-01-09 22:30 | 10.93 | 10.93
2019-01-09 23:00 | 10.49 | 10.47
2019-01-09 23:30 | 9.41 | 9.4
2019-01-10 | 8.39 | 8.38
2019-01-10 00:30 | 7.53 | 7.52
2019-01-10 01:00 | 7.28 | 7.27
2019-01-10 01:30 | 6.89 | 6.87
2019-01-10 02:00 | 6.56 | 6.55
2019-01-10 02:30 | 6.43 | 6.42
2019-01-10 03:00 | 6.27 | 6.26
2019-01-10 03:30 | 6.26 | 6.25
2019-01-10 04:00 | 6.2 | 6.19
2019-01-10 04:30 | 6.19 | 6.18
2019-01-10 05:00 | 6.25 | 6.23
2019-01-10 05:30 | 6.29 | 6.27
2019-01-10 06:00 | 6.67 | 6.65
2019-01-10 06:30 | 7.05 | 7.04
2019-01-10 07:00 | 6.8 | 6.78
2019-01-10 07:30 | 6.66 | 6.65
2019-01-10 08:00 | 5.78 | 5.77
2019-01-10 08:30 | 7.01 | 7
2019-01-10 09:00 | 6.15 | 6.13
2019-01-10 09:30 | 6.08 | 6.05
2019-01-10 10:00 | 8.11 | 8.08
2019-01-10 10:30 | 8.64 | 8.62
2019-01-10 11:00 | 7.38 | 7.35
2019-01-10 11:30 | 8.5 | 8.47
2019-01-10 12:00 | 8.92 | 8.89
2019-01-10 12:30 | 10.29 | 10.26
2019-01-10 13:00 | 11.23 | 11.2
2019-01-10 13:30 | 9.04 | 9
2019-01-10 14:00 | 9.69 | 9.64
2019-01-10 14:30 | 10.38 | 10.33
2019-01-10 15:00 | 9.7 | 9.64
2019-01-10 15:30 | 10.7 | 10.64
2019-01-10 16:00 | 11.24 | 11.17
2019-01-10 16:30 | 12.83 | 12.76
2019-01-10 17:00 | 14.13 | 14.07
2019-01-10 17:30 | 14.66 | 14.6
2019-01-10 18:00 | 15.34 | 15.28
2019-01-10 18:30 | 15.28 | 15.24
2019-01-10 19:00 | 15.53 | 15.49
2019-01-10 19:30 | 15.6 | 15.54
2019-01-10 20:00 | 15.44 | 15.39
2019-01-10 20:30 | 14.87 | 14.83
2019-01-10 21:00 | 13.86 | 13.83
2019-01-10 21:30 | 12.82 | 12.8
2019-01-10 22:00 | 11.85 | 11.83
2019-01-10 22:30 | 11.08 | 11.07
2019-01-10 23:00 | 10.47 | 10.46
2019-01-10 23:30 | 9.22 | 9.21
2019-01-11 | 8.25 | 8.24
2019-01-11 00:30 | 7.55 | 7.54
2019-01-11 01:00 | 7.14 | 7.12
2019-01-11 01:30 | 6.67 | 6.66
2019-01-11 02:00 | 6.33 | 6.32
2019-01-11 02:30 | 6.15 | 6.14
2019-01-11 03:00 | 5.96 | 5.95
2019-01-11 03:30 | 5.89 | 5.88
2019-01-11 04:00 | 5.81 | 5.79
2019-01-11 04:30 | 5.8 | 5.78
2019-01-11 05:00 | 5.82 | 5.81
2019-01-11 05:30 | 5.89 | 5.85
2019-01-11 06:00 | 5.95 | 5.9
2019-01-11 06:30 | 5.59 | 5.55
2019-01-11 07:00 | 6.08 | 6.06
2019-01-11 07:30 | 6.48 | 6.46
2019-01-11 08:00 | 5.21 | 5.2
2019-01-11 08:30 | 5.47 | 5.45
2019-01-11 09:00 | 5.56 | 5.53
2019-01-11 09:30 | 6.96 | 6.93
2019-01-11 10:00 | 6.2 | 6.16
2019-01-11 10:30 | 5.96 | 5.91
2019-01-11 11:00 | 6.59 | 6.55
2019-01-11 11:30 | 6.89 | 6.85
2019-01-11 12:00 | 7.38 | 7.33
2019-01-11 12:30 | 8.3 | 8.25
2019-01-11 13:00 | 8 | 7.94
2019-01-11 13:30 | 8.93 | 8.86
2019-01-11 14:00 | 9.39 | 9.32
2019-01-11 14:30 | 9.73 | 9.66
2019-01-11 15:00 | 10.47 | 10.39
2019-01-11 15:30 | 11.32 | 11.23
2019-01-11 16:00 | 12.03 | 11.95
2019-01-11 16:30 | 12.88 | 12.81
2019-01-11 17:00 | 13.86 | 13.79
2019-01-11 17:30 | 14.53 | 14.47
2019-01-11 18:00 | 14.46 | 14.41
2019-01-11 18:30 | 14.45 | 14.41
2019-01-11 19:00 | 14.36 | 14.33
2019-01-11 19:30 | 14.47 | 14.43
2019-01-11 20:00 | 14.29 | 14.25
2019-01-11 20:30 | 13.98 | 13.95
2019-01-11 21:00 | 13.01 | 12.98
2019-01-11 21:30 | 12 | 11.99
2019-01-11 22:00 | 11.12 | 11.11
2019-01-11 22:30 | 10.7 | 10.69
2019-01-11 23:00 | 10.22 | 10.21
2019-01-11 23:30 | 9.12 | 9.11
2019-01-12 | 8.08 | 8.08
2019-01-12 00:30 | 7.38 | 7.37
2019-01-12 01:00 | 6.98 | 6.97
2019-01-12 01:30 | 6.51 | 6.5
2019-01-12 02:00 | 6.15 | 6.14
2019-01-12 02:30 | 6.03 | 6.02
2019-01-12 03:00 | 5.73 | 5.71
2019-01-12 03:30 | 5.59 | 5.57
2019-01-12 04:00 | 5.5 | 5.47
2019-01-12 04:30 | 5.39 | 5.36
2019-01-12 05:00 | 5.25 | 5.2
2019-01-12 05:30 | 5.16 | 5.07
2019-01-12 06:00 | 5.08 | 4.98
2019-01-12 06:30 | 4.74 | 4.66
2019-01-12 07:00 | 4.79 | 4.73
2019-01-12 07:30 | 4.8 | 4.77
2019-01-12 08:00 | 4.61 | 4.58
2019-01-12 08:30 | 4.73 | 4.71
2019-01-12 09:00 | 5.33 | 5.3
2019-01-12 09:30 | 6.16 | 6.12
2019-01-12 10:00 | 6.09 | 6.05
2019-01-12 10:30 | 6.34 | 6.3
2019-01-12 11:00 | 6.75 | 6.7
2019-01-12 11:30 | 6.6 | 6.54
2019-01-12 12:00 | 7.09 | 7.03
2019-01-12 12:30 | 7.86 | 7.79
2019-01-12 13:00 | 8.78 | 8.7
2019-01-12 13:30 | 9.55 | 9.46
2019-01-12 14:00 | 10.36 | 10.27
2019-01-12 14:30 | 11.1 | 11
2019-01-12 15:00 | 11.78 | 11.69
2019-01-12 15:30 | 12.66 | 12.57
2019-01-12 16:00 | 13.41 | 13.32
2019-01-12 16:30 | 14.28 | 14.2
2019-01-12 17:00 | 14.82 | 14.75
2019-01-12 17:30 | 15.11 | 15.04
2019-01-12 18:00 | 15.11 | 15.05
2019-01-12 18:30 | 14.94 | 14.89
2019-01-12 19:00 | 14.55 | 14.52
2019-01-12 19:30 | 14.31 | 14.26
2019-01-12 20:00 | 14.2 | 14.16
2019-01-12 20:30 | 13.71 | 13.68
2019-01-12 21:00 | 12.82 | 12.79
2019-01-12 21:30 | 11.95 | 11.94
2019-01-12 22:00 | 11.18 | 11.18
2019-01-12 22:30 | 10.64 | 10.64
2019-01-12 23:00 | 10.22 | 10.22
2019-01-12 23:30 | 9.1 | 9.09
2019-01-13 | 8.15 | 8.14
2019-01-13 00:30 | 8.46 | 8.45
2019-01-13 01:00 | 8.16 | 8.15
2019-01-13 01:30 | 7.55 | 7.54
2019-01-13 02:00 | 6.2 | 6.19
2019-01-13 02:30 | 5.93 | 5.91
2019-01-13 03:00 | 5.74 | 5.72
2019-01-13 03:30 | 5.66 | 5.64
2019-01-13 04:00 | 5.52 | 5.5
2019-01-13 04:30 | 5.42 | 5.4
2019-01-13 05:00 | 5.31 | 5.27
2019-01-13 05:30 | 5.08 | 4.99
2019-01-13 06:00 | 4.97 | 4.87
2019-01-13 06:30 | 4.88 | 4.79
2019-01-13 07:00 | 4.72 | 4.66
2019-01-13 07:30 | 4.74 | 4.71
2019-01-13 08:00 | 5.18 | 5.16
2019-01-13 08:30 | 5.37 | 5.35
2019-01-13 09:00 | 5.59 | 5.56
2019-01-13 09:30 | 6.66 | 6.62
2019-01-13 10:00 | 7.45 | 7.4
2019-01-13 10:30 | 7.55 | 7.5
2019-01-13 11:00 | 8.35 | 8.3
2019-01-13 11:30 | 9 | 8.96
2019-01-13 12:00 | 9.28 | 9.23
2019-01-13 12:30 | 9.71 | 9.65
2019-01-13 13:00 | 10.4 | 10.32
2019-01-13 13:30 | 11.14 | 11.05
2019-01-13 14:00 | 11.6 | 11.5
2019-01-13 14:30 | 12.19 | 12.08
2019-01-13 15:00 | 12.8 | 12.7
2019-01-13 15:30 | 13.63 | 13.54
2019-01-13 16:00 | 14.65 | 14.56
2019-01-13 16:30 | 15.46 | 15.38
2019-01-13 17:00 | 16.42 | 16.33
2019-01-13 17:30 | 16.76 | 16.68
2019-01-13 18:00 | 16.51 | 16.45
2019-01-13 18:30 | 16.1 | 16.05
2019-01-13 19:00 | 15.61 | 15.58
2019-01-13 19:30 | 15.28 | 15.24
2019-01-13 20:00 | 14.97 | 14.94
2019-01-13 20:30 | 14.37 | 14.34
2019-01-13 21:00 | 13.21 | 13.2
2019-01-13 21:30 | 11.94 | 11.93
2019-01-13 22:00 | 11.13 | 11.12
2019-01-13 22:30 | 10.53 | 10.52
2019-01-13 23:00 | 9.95 | 9.94
2019-01-13 23:30 | 8.73 | 8.73
2019-01-14 | 7.73 | 7.72
2019-01-14 00:30 | 7.06 | 7.05
2019-01-14 01:00 | 6.62 | 6.61
2019-01-14 01:30 | 6.29 | 6.28
2019-01-14 02:00 | 6.08 | 6.06
2019-01-14 02:30 | 5.9 | 5.88
2019-01-14 03:00 | 5.72 | 5.7
2019-01-14 03:30 | 5.61 | 5.59
2019-01-14 04:00 | 5.64 | 5.62
2019-01-14 04:30 | 5.73 | 5.71
2019-01-14 05:00 | 5.65 | 5.62
2019-01-14 05:30 | 5.68 | 5.63
2019-01-14 06:00 | 6.17 | 6.13
2019-01-14 06:30 | 6.23 | 6.2
2019-01-14 07:00 | 6.03 | 6.02
2019-01-14 07:30 | 6 | 5.99
2019-01-14 08:00 | 5.66 | 5.65
2019-01-14 08:30 | 5.94 | 5.92
2019-01-14 09:00 | 5.75 | 5.73
2019-01-14 09:30 | 5.93 | 5.9
2019-01-14 10:00 | 6.46 | 6.43
2019-01-14 10:30 | 6.26 | 6.23
2019-01-14 11:00 | 6.27 | 6.23
2019-01-14 11:30 | 6.66 | 6.61
2019-01-14 12:00 | 7.18 | 7.12
2019-01-14 12:30 | 7.96 | 7.89
2019-01-14 13:00 | 8.92 | 8.84
2019-01-14 13:30 | 9.76 | 9.65
2019-01-14 14:00 | 10.58 | 10.46
2019-01-14 14:30 | 11.05 | 10.94
2019-01-14 15:00 | 11.93 | 11.82
2019-01-14 15:30 | 12.83 | 12.71
2019-01-14 16:00 | 13.78 | 13.68
2019-01-14 16:30 | 15.04 | 14.93
2019-01-14 17:00 | 15.98 | 15.89
2019-01-14 17:30 | 16.85 | 16.75
2019-01-14 18:00 | 17.21 | 17.12
2019-01-14 18:30 | 17.15 | 17.08
2019-01-14 19:00 | 16.81 | 16.76
2019-01-14 19:30 | 16.84 | 16.77
2019-01-14 20:00 | 16.64 | 16.58
2019-01-14 20:30 | 16.21 | 16.15
2019-01-14 21:00 | 15.05 | 15.01
2019-01-14 21:30 | 13.72 | 13.69
2019-01-14 22:00 | 12.27 | 12.26
2019-01-14 22:30 | 11.06 | 11.05
2019-01-14 23:00 | 10.34 | 10.33
2019-01-14 23:30 | 9.16 | 9.15
2019-01-15 | 8.05 | 8.04
2019-01-15 00:30 | 7.37 | 7.36
2019-01-15 01:00 | 7.05 | 7.04
2019-01-15 01:30 | 6.5 | 6.49
2019-01-15 02:00 | 6.14 | 6.13
2019-01-15 02:30 | 6.02 | 6.01
2019-01-15 03:00 | 5.88 | 5.87
2019-01-15 03:30 | 5.83 | 5.82
2019-01-15 04:00 | 5.81 | 5.79
2019-01-15 04:30 | 5.76 | 5.74
2019-01-15 05:00 | 5.79 | 5.76
2019-01-15 05:30 | 5.9 | 5.86
2019-01-15 06:00 | 5.94 | 5.9
2019-01-15 06:30 | 6.34 | 6.32
2019-01-15 07:00 | 6.25 | 6.23
2019-01-15 07:30 | 6.42 | 6.42
2019-01-15 08:00 | 6.28 | 6.27
2019-01-15 08:30 | 6.81 | 6.8
2019-01-15 09:00 | 6.65 | 6.64
2019-01-15 09:30 | 6.93 | 6.91
2019-01-15 10:00 | 7.1 | 7.08
2019-01-15 10:30 | 7.39 | 7.35
2019-01-15 11:00 | 7.3 | 7.25
2019-01-15 11:30 | 8.07 | 8.01
2019-01-15 12:00 | 8.81 | 8.73
2019-01-15 12:30 | 10 | 9.91
2019-01-15 13:00 | 10.8 | 10.68
2019-01-15 13:30 | 11.65 | 11.52
2019-01-15 14:00 | 12.59 | 12.46
2019-01-15 14:30 | 13.31 | 13.16
2019-01-15 15:00 | 14.13 | 13.99
2019-01-15 15:30 | 14.96 | 14.81
2019-01-15 16:00 | 15.83 | 15.69
2019-01-15 16:30 | 16.85 | 16.72
2019-01-15 17:00 | 17.92 | 17.78
2019-01-15 17:30 | 18.4 | 18.28
2019-01-15 18:00 | 18.45 | 18.33
2019-01-15 18:30 | 18.18 | 18.08
2019-01-15 19:00 | 17.91 | 17.84
2019-01-15 19:30 | 17.56 | 17.47
2019-01-15 20:00 | 17.16 | 17.09
2019-01-15 20:30 | 16.34 | 16.28
2019-01-15 21:00 | 14.95 | 14.91
2019-01-15 21:30 | 13.6 | 13.57
2019-01-15 22:00 | 12.51 | 12.49
2019-01-15 22:30 | 11.39 | 11.38
2019-01-15 23:00 | 10.64 | 10.63
2019-01-15 23:30 | 9.42 | 9.41
2019-01-16 | 8.4 | 8.39
2019-01-16 00:30 | 7.53 | 7.52
2019-01-16 01:00 | 7.18 | 7.17
2019-01-16 01:30 | 6.8 | 6.79
2019-01-16 02:00 | 6.51 | 6.51
2019-01-16 02:30 | 6.44 | 6.43
2019-01-16 03:00 | 6.32 | 6.31
2019-01-16 03:30 | 6.26 | 6.25
2019-01-16 04:00 | 6.23 | 6.22
2019-01-16 04:30 | 6.21 | 6.2
2019-01-16 05:00 | 6.28 | 6.27
2019-01-16 05:30 | 6.21 | 6.17
2019-01-16 06:00 | 6.13 | 6.09
2019-01-16 06:30 | 6.33 | 6.31
2019-01-16 07:00 | 6.41 | 6.39
2019-01-16 07:30 | 6.16 | 6.14
2019-01-16 08:00 | 6.01 | 5.99
2019-01-16 08:30 | 6.03 | 6.01
2019-01-16 09:00 | 6.28 | 6.25
2019-01-16 09:30 | 6.44 | 6.4
2019-01-16 10:00 | 6.74 | 6.69
2019-01-16 10:30 | 7.1 | 7.04
2019-01-16 11:00 | 7.73 | 7.64
2019-01-16 11:30 | 8.59 | 8.5
2019-01-16 12:00 | 9.49 | 9.38
2019-01-16 12:30 | 10.58 | 10.45
2019-01-16 13:00 | 11.53 | 11.38
2019-01-16 13:30 | 12.64 | 12.47
2019-01-16 14:00 | 13.52 | 13.34
2019-01-16 14:30 | 14.28 | 14.09
2019-01-16 15:00 | 14.94 | 14.76
2019-01-16 15:30 | 15.83 | 15.66
2019-01-16 16:00 | 16.61 | 16.44
2019-01-16 16:30 | 17.43 | 17.28
2019-01-16 17:00 | 18.33 | 18.19
2019-01-16 17:30 | 19.16 | 19.02
2019-01-16 18:00 | 19.33 | 19.21
2019-01-16 18:30 | 19.12 | 19.01
2019-01-16 19:00 | 19.14 | 19.04
2019-01-16 19:30 | 19.13 | 19
2019-01-16 20:00 | 18.8 | 18.68
2019-01-16 20:30 | 17.91 | 17.8
2019-01-16 21:00 | 16.6 | 16.52
2019-01-16 21:30 | 15.19 | 15.13
2019-01-16 22:00 | 13.8 | 13.76
2019-01-16 22:30 | 12.45 | 12.43
2019-01-16 23:00 | 11.49 | 11.48
2019-01-16 23:30 | 10.13 | 10.12
2019-01-17 | 9.02 | 9.01
2019-01-17 00:30 | 8.26 | 8.25
2019-01-17 01:00 | 7.83 | 7.82
2019-01-17 01:30 | 7.51 | 7.5
2019-01-17 02:00 | 7.18 | 7.16
2019-01-17 02:30 | 7.01 | 7
2019-01-17 03:00 | 6.8 | 6.79
2019-01-17 03:30 | 6.75 | 6.74
2019-01-17 04:00 | 6.63 | 6.62
2019-01-17 04:30 | 6.53 | 6.52
2019-01-17 05:00 | 6.44 | 6.43
2019-01-17 05:30 | 6.47 | 6.45
2019-01-17 06:00 | 6.84 | 6.83
2019-01-17 06:30 | 7.11 | 7.1
2019-01-17 07:00 | 7.1 | 7.1
2019-01-17 07:30 | 7.6 | 7.6
2019-01-17 08:00 | 7.76 | 7.75
2019-01-17 08:30 | 7.92 | 7.91
2019-01-17 09:00 | 6.68 | 6.67
2019-01-17 09:30 | 7.57 | 7.54
2019-01-17 10:00 | 7.96 | 7.93
2019-01-17 10:30 | 7.53 | 7.48
2019-01-17 11:00 | 8.17 | 8.11
2019-01-17 11:30 | 7.87 | 7.81
2019-01-17 12:00 | 8.87 | 8.8
2019-01-17 12:30 | 9.26 | 9.17
2019-01-17 13:00 | 9.77 | 9.66
2019-01-17 13:30 | 10.56 | 10.45
2019-01-17 14:00 | 11.26 | 11.16
2019-01-17 14:30 | 11.88 | 11.77
2019-01-17 15:00 | 12.85 | 12.73
2019-01-17 15:30 | 13.78 | 13.65
2019-01-17 16:00 | 15.07 | 14.94
2019-01-17 16:30 | 16.14 | 16.01
2019-01-17 17:00 | 17.27 | 17.14
2019-01-17 17:30 | 17.82 | 17.7
2019-01-17 18:00 | 18.03 | 17.92
2019-01-17 18:30 | 17.79 | 17.7
2019-01-17 19:00 | 17.45 | 17.37
2019-01-17 19:30 | 17.29 | 17.2
2019-01-17 20:00 | 17.03 | 16.94
2019-01-17 20:30 | 16.27 | 16.2
2019-01-17 21:00 | 14.92 | 14.87
2019-01-17 21:30 | 13.69 | 13.66
2019-01-17 22:00 | 12.34 | 12.33
2019-01-17 22:30 | 11.4 | 11.39
2019-01-17 23:00 | 10.59 | 10.58
2019-01-17 23:30 | 9.27 | 9.26
2019-01-18 | 8.21 | 8.2
2019-01-18 00:30 | 7.57 | 7.55
2019-01-18 01:00 | 7.17 | 7.16
2019-01-18 01:30 | 6.72 | 6.71
2019-01-18 02:00 | 6.34 | 6.33
2019-01-18 02:30 | 6.17 | 6.16
2019-01-18 03:00 | 5.93 | 5.91
2019-01-18 03:30 | 5.95 | 5.93
2019-01-18 04:00 | 5.8 | 5.79
2019-01-18 04:30 | 5.84 | 5.82
2019-01-18 05:00 | 5.82 | 5.8
2019-01-18 05:30 | 5.86 | 5.82
2019-01-18 06:00 | 6.15 | 6.11
2019-01-18 06:30 | 6.43 | 6.41
2019-01-18 07:00 | 6.72 | 6.71
2019-01-18 07:30 | 5.94 | 5.93
2019-01-18 08:00 | 6 | 5.99
2019-01-18 08:30 | 6.6 | 6.59
2019-01-18 09:00 | 6.54 | 6.53
2019-01-18 09:30 | 7.4 | 7.39
2019-01-18 10:00 | 7.37 | 7.35
2019-01-18 10:30 | 7.13 | 7.11
2019-01-18 11:00 | 7.4 | 7.35
2019-01-18 11:30 | 8.63 | 8.57
2019-01-18 12:00 | 8.47 | 8.4
2019-01-18 12:30 | 8.86 | 8.77
2019-01-18 13:00 | 8.98 | 8.87
2019-01-18 13:30 | 9.66 | 9.55
2019-01-18 14:00 | 10.57 | 10.45
2019-01-18 14:30 | 11.43 | 11.32
2019-01-18 15:00 | 12.41 | 12.3
2019-01-18 15:30 | 13.48 | 13.36
2019-01-18 16:00 | 14.61 | 14.49
2019-01-18 16:30 | 15.64 | 15.52
2019-01-18 17:00 | 16.62 | 16.5
2019-01-18 17:30 | 17.26 | 17.15
2019-01-18 18:00 | 17.36 | 17.25
2019-01-18 18:30 | 17.11 | 17.02
2019-01-18 19:00 | 16.67 | 16.59
2019-01-18 19:30 | 16.53 | 16.44
2019-01-18 20:00 | 16.41 | 16.33
2019-01-18 20:30 | 15.62 | 15.56
2019-01-18 21:00 | 14.54 | 14.49
2019-01-18 21:30 | 13.45 | 13.41
2019-01-18 22:00 | 12.4 | 12.38
2019-01-18 22:30 | 11.66 | 11.65
2019-01-18 23:00 | 10.93 | 10.92
2019-01-18 23:30 | 9.81 | 9.8
2019-01-19 | 8.76 | 8.75
2019-01-19 00:30 | 7.99 | 7.99
2019-01-19 01:00 | 7.51 | 7.5
2019-01-19 01:30 | 7.07 | 7.06
2019-01-19 02:00 | 6.6 | 6.59
2019-01-19 02:30 | 6.32 | 6.31
2019-01-19 03:00 | 6.08 | 6.07
2019-01-19 03:30 | 5.97 | 5.95
2019-01-19 04:00 | 5.8 | 5.78
2019-01-19 04:30 | 5.71 | 5.7
2019-01-19 05:00 | 5.56 | 5.54
2019-01-19 05:30 | 5.39 | 5.32
2019-01-19 06:00 | 5.28 | 5.2
2019-01-19 06:30 | 4.96 | 4.9
2019-01-19 07:00 | 4.97 | 4.93
2019-01-19 07:30 | 5.48 | 5.45
2019-01-19 08:00 | 4.99 | 4.96
2019-01-19 08:30 | 5.5 | 5.47
2019-01-19 09:00 | 5.94 | 5.89
2019-01-19 09:30 | 6.55 | 6.5
2019-01-19 10:00 | 6.62 | 6.56
2019-01-19 10:30 | 7.19 | 7.13
2019-01-19 11:00 | 8.68 | 8.61
2019-01-19 11:30 | 11.15 | 11.08
2019-01-19 12:00 | 10.19 | 10.09
2019-01-19 12:30 | 10.91 | 10.8
2019-01-19 13:00 | 11.59 | 11.45
2019-01-19 13:30 | 12.51 | 12.36
2019-01-19 14:00 | 13.78 | 13.61
2019-01-19 14:30 | 14.89 | 14.71
2019-01-19 15:00 | 16.16 | 15.98
2019-01-19 15:30 | 17.36 | 17.19
2019-01-19 16:00 | 18.66 | 18.47
2019-01-19 16:30 | 19.31 | 19.11
2019-01-19 17:00 | 19.83 | 19.65
2019-01-19 17:30 | 19.7 | 19.54
2019-01-19 18:00 | 19.42 | 19.27
2019-01-19 18:30 | 18.71 | 18.58
2019-01-19 19:00 | 17.83 | 17.72
2019-01-19 19:30 | 17.27 | 17.16
2019-01-19 20:00 | 17.01 | 16.91
2019-01-19 20:30 | 16.06 | 15.98
2019-01-19 21:00 | 15.05 | 14.99
2019-01-19 21:30 | 14.03 | 13.98
2019-01-19 22:00 | 12.92 | 12.89
2019-01-19 22:30 | 12.23 | 12.21
2019-01-19 23:00 | 11.6 | 11.59
2019-01-19 23:30 | 10.36 | 10.35
2019-01-20 | 9.27 | 9.26
2019-01-20 00:30 | 8.48 | 8.47
2019-01-20 01:00 | 8.03 | 8.02
2019-01-20 01:30 | 7.41 | 7.4
2019-01-20 02:00 | 7.04 | 7.03
2019-01-20 02:30 | 6.81 | 6.8
2019-01-20 03:00 | 6.51 | 6.5
2019-01-20 03:30 | 6.44 | 6.43
2019-01-20 04:00 | 6.24 | 6.22
2019-01-20 04:30 | 6.12 | 6.11
2019-01-20 05:00 | 6.2 | 6.19
2019-01-20 05:30 | 5.98 | 5.96
2019-01-20 06:00 | 6.04 | 6.01
2019-01-20 06:30 | 6.22 | 6.19
2019-01-20 07:00 | 6.29 | 6.26
2019-01-20 07:30 | 5.69 | 5.67
2019-01-20 08:00 | 6.02 | 6
2019-01-20 08:30 | 7.16 | 7.14
2019-01-20 09:00 | 7 | 6.97
2019-01-20 09:30 | 7.67 | 7.64
2019-01-20 10:00 | 8.46 | 8.42
2019-01-20 10:30 | 9.24 | 9.19
2019-01-20 11:00 | 9.82 | 9.75
2019-01-20 11:30 | 10.28 | 10.18
2019-01-20 12:00 | 11.27 | 11.15
2019-01-20 12:30 | 12.58 | 12.44
2019-01-20 13:00 | 13.59 | 13.43
2019-01-20 13:30 | 14.42 | 14.26
2019-01-20 14:00 | 15.27 | 15.1
2019-01-20 14:30 | 16.26 | 16.07
2019-01-20 15:00 | 17.1 | 16.91
2019-01-20 15:30 | 18.01 | 17.82
2019-01-20 16:00 | 18.95 | 18.76
2019-01-20 16:30 | 19.58 | 19.41
2019-01-20 17:00 | 20.29 | 20.13
2019-01-20 17:30 | 20.66 | 20.5
2019-01-20 18:00 | 20.73 | 20.59
2019-01-20 18:30 | 19.82 | 19.7
2019-01-20 19:00 | 18.75 | 18.66
2019-01-20 19:30 | 18.34 | 18.24
2019-01-20 20:00 | 17.9 | 17.81
2019-01-20 20:30 | 17.05 | 16.98
2019-01-20 21:00 | 15.8 | 15.74
2019-01-20 21:30 | 14.52 | 14.48
2019-01-20 22:00 | 13.15 | 13.12
2019-01-20 22:30 | 12.16 | 12.14
2019-01-20 23:00 | 11.42 | 11.41
2019-01-20 23:30 | 10.15 | 10.14
2019-01-21 | 9.11 | 9.1
2019-01-21 00:30 | 8.44 | 8.43
2019-01-21 01:00 | 8.2 | 8.19
2019-01-21 01:30 | 7.74 | 7.73
2019-01-21 02:00 | 7.32 | 7.31
2019-01-21 02:30 | 7.15 | 7.14
2019-01-21 03:00 | 7.06 | 7.04
2019-01-21 03:30 | 6.94 | 6.93
2019-01-21 04:00 | 6.87 | 6.86
2019-01-21 04:30 | 6.85 | 6.84
2019-01-21 05:00 | 6.88 | 6.87
2019-01-21 05:30 | 6.78 | 6.77
2019-01-21 06:00 | 6.9 | 6.88
2019-01-21 06:30 | 7.1 | 7.09
2019-01-21 07:00 | 7.07 | 7.06
2019-01-21 07:30 | 6.72 | 6.7
2019-01-21 08:00 | 7.14 | 7.13
2019-01-21 08:30 | 7.25 | 7.24
2019-01-21 09:00 | 7.69 | 7.66
2019-01-21 09:30 | 7.87 | 7.84
2019-01-21 10:00 | 8.41 | 8.37
2019-01-21 10:30 | 8.68 | 8.62
2019-01-21 11:00 | 9.1 | 9.02
2019-01-21 11:30 | 9.55 | 9.45
2019-01-21 12:00 | 11.9 | 11.82
2019-01-21 12:30 | 12.24 | 12.15
2019-01-21 13:00 | 11.73 | 11.59
2019-01-21 13:30 | 12.56 | 12.41
2019-01-21 14:00 | 13.26 | 13.1
2019-01-21 14:30 | 13.91 | 13.74
2019-01-21 15:00 | 14.58 | 14.42
2019-01-21 15:30 | 15.39 | 15.23
2019-01-21 16:00 | 16.41 | 16.26
2019-01-21 16:30 | 17.41 | 17.27
2019-01-21 17:00 | 18.34 | 18.2
2019-01-21 17:30 | 18.86 | 18.73
2019-01-21 18:00 | 19 | 18.89
2019-01-21 18:30 | 18.6 | 18.5
2019-01-21 19:00 | 18.37 | 18.28
2019-01-21 19:30 | 18.14 | 18.04
2019-01-21 20:00 | 17.78 | 17.69
2019-01-21 20:30 | 17.14 | 17.06
2019-01-21 21:00 | 15.91 | 15.85
2019-01-21 21:30 | 14.53 | 14.49
2019-01-21 22:00 | 13.22 | 13.19
2019-01-21 22:30 | 12.16 | 12.15
2019-01-21 23:00 | 11.28 | 11.27
2019-01-21 23:30 | 9.92 | 9.91
2019-01-22 | 8.79 | 8.78
2019-01-22 00:30 | 7.97 | 7.96
2019-01-22 01:00 | 7.61 | 7.6
2019-01-22 01:30 | 7.22 | 7.21
2019-01-22 02:00 | 6.96 | 6.95
2019-01-22 02:30 | 6.73 | 6.71
2019-01-22 03:00 | 6.45 | 6.44
2019-01-22 03:30 | 6.37 | 6.36
2019-01-22 04:00 | 6.34 | 6.33
2019-01-22 04:30 | 6.29 | 6.28
2019-01-22 05:00 | 6.29 | 6.28
2019-01-22 05:30 | 6.29 | 6.26
2019-01-22 06:00 | 6.59 | 6.56
2019-01-22 06:30 | 6.78 | 6.77
2019-01-22 07:00 | 6.76 | 6.75
2019-01-22 07:30 | 6.99 | 6.99
2019-01-22 08:00 | 7.22 | 7.21
2019-01-22 08:30 | 7.06 | 7.05
2019-01-22 09:00 | 7.19 | 7.18
2019-01-22 09:30 | 7.86 | 7.83
2019-01-22 10:00 | 9.49 | 9.45
2019-01-22 10:30 | 8.95 | 8.9
2019-01-22 11:00 | 9.68 | 9.62
2019-01-22 11:30 | 9.77 | 9.69
2019-01-22 12:00 | 10.27 | 10.18
2019-01-22 12:30 | 12.11 | 12.02
2019-01-22 13:00 | 12.81 | 12.71
2019-01-22 13:30 | 13.22 | 13.1
2019-01-22 14:00 | 13.7 | 13.57
2019-01-22 14:30 | 14.22 | 14.08
2019-01-22 15:00 | 14.37 | 14.21
2019-01-22 15:30 | 15.51 | 15.35
2019-01-22 16:00 | 16.35 | 16.2
2019-01-22 16:30 | 17.52 | 17.36
2019-01-22 17:00 | 18.3 | 18.15
2019-01-22 17:30 | 18.89 | 18.75
2019-01-22 18:00 | 19.27 | 19.14
2019-01-22 18:30 | 19.58 | 19.47
2019-01-22 19:00 | 19.36 | 19.25
2019-01-22 19:30 | 19.18 | 19.06
2019-01-22 20:00 | 18.76 | 18.64
2019-01-22 20:30 | 17.87 | 17.77
2019-01-22 21:00 | 16.75 | 16.68
2019-01-22 21:30 | 15.6 | 15.54
2019-01-22 22:00 | 14.03 | 13.99
2019-01-22 22:30 | 12.67 | 12.65
2019-01-22 23:00 | 11.61 | 11.59
2019-01-22 23:30 | 10.23 | 10.22
2019-01-23 | 9.15 | 9.14
2019-01-23 00:30 | 8.44 | 8.43
2019-01-23 01:00 | 8.01 | 8
2019-01-23 01:30 | 7.54 | 7.53
2019-01-23 02:00 | 7.26 | 7.25
2019-01-23 02:30 | 7.04 | 7.03
2019-01-23 03:00 | 6.82 | 6.81
2019-01-23 03:30 | 6.72 | 6.71
2019-01-23 04:00 | 6.53 | 6.52
2019-01-23 04:30 | 6.51 | 6.5
2019-01-23 05:00 | 6.39 | 6.38
2019-01-23 05:30 | 6.4 | 6.38
2019-01-23 06:00 | 6.76 | 6.74
2019-01-23 06:30 | 6.99 | 6.98
2019-01-23 07:00 | 7.21 | 7.21
2019-01-23 07:30 | 7.26 | 7.25
2019-01-23 08:00 | 6.93 | 6.91
2019-01-23 08:30 | 7.27 | 7.25
2019-01-23 09:00 | 7.31 | 7.27
2019-01-23 09:30 | 7.71 | 7.65
2019-01-23 10:00 | 7.72 | 7.65
2019-01-23 10:30 | 8.59 | 8.5
2019-01-23 11:00 | 9.41 | 9.3
2019-01-23 11:30 | 9.3 | 9.15
2019-01-23 12:00 | 10.42 | 10.28
2019-01-23 12:30 | 11.47 | 11.32
2019-01-23 13:00 | 12.36 | 12.19
2019-01-23 13:30 | 13.17 | 12.98
2019-01-23 14:00 | 14.38 | 14.18
2019-01-23 14:30 | 15.21 | 15
2019-01-23 15:00 | 16.29 | 16.08
2019-01-23 15:30 | 17.01 | 16.81
2019-01-23 16:00 | 17.07 | 16.88
2019-01-23 16:30 | 20.43 | 20.25
2019-01-23 17:00 | 21.25 | 21.07
2019-01-23 17:30 | 20.89 | 20.72
2019-01-23 18:00 | 20.61 | 20.45
2019-01-23 18:30 | 20.44 | 20.29
2019-01-23 19:00 | 20.16 | 20.02
2019-01-23 19:30 | 20.03 | 19.87
2019-01-23 20:00 | 19.65 | 19.51
2019-01-23 20:30 | 19.06 | 18.93
2019-01-23 21:00 | 17.51 | 17.42
2019-01-23 21:30 | 16.08 | 16.01
2019-01-23 22:00 | 14.54 | 14.49
2019-01-23 22:30 | 13.06 | 13.03
2019-01-23 23:00 | 12.33 | 12.31
2019-01-23 23:30 | 10.74 | 10.73
2019-01-24 | 9.66 | 9.65
2019-01-24 00:30 | 8.91 | 8.9
2019-01-24 01:00 | 8.53 | 8.52
2019-01-24 01:30 | 8.08 | 8.07
2019-01-24 02:00 | 7.73 | 7.72
2019-01-24 02:30 | 7.52 | 7.5
2019-01-24 03:00 | 7.23 | 7.22
2019-01-24 03:30 | 7.05 | 7.03
2019-01-24 04:00 | 6.99 | 6.97
2019-01-24 04:30 | 6.94 | 6.93
2019-01-24 05:00 | 6.89 | 6.87
2019-01-24 05:30 | 7 | 6.99
2019-01-24 06:00 | 7.35 | 7.34
2019-01-24 06:30 | 7.87 | 7.86
2019-01-24 07:00 | 7.94 | 7.93
2019-01-24 07:30 | 8.04 | 8.04
2019-01-24 08:00 | 7.58 | 7.57
2019-01-24 08:30 | 7.49 | 7.47
2019-01-24 09:00 | 7.64 | 7.61
2019-01-24 09:30 | 8.13 | 8.09
2019-01-24 10:00 | 9.26 | 9.18
2019-01-24 10:30 | 10.45 | 10.35
2019-01-24 11:00 | 11.79 | 11.68
2019-01-24 11:30 | 12.88 | 12.75
2019-01-24 12:00 | 12.9 | 12.77
2019-01-24 12:30 | 14.4 | 14.27
2019-01-24 13:00 | 15.2 | 15.07
2019-01-24 13:30 | 14.75 | 14.59
2019-01-24 14:00 | 14.92 | 14.75
2019-01-24 14:30 | 14.86 | 14.67
2019-01-24 15:00 | 15.98 | 15.8
2019-01-24 15:30 | 17.02 | 16.85
2019-01-24 16:00 | 17.81 | 17.63
2019-01-24 16:30 | 18.84 | 18.66
2019-01-24 17:00 | 19.79 | 19.6
2019-01-24 17:30 | 20.53 | 20.35
2019-01-24 18:00 | 20.62 | 20.46
2019-01-24 18:30 | 19.91 | 19.76
2019-01-24 19:00 | 19.71 | 19.56
2019-01-24 19:30 | 19.53 | 19.36
2019-01-24 20:00 | 19.02 | 18.88
2019-01-24 20:30 | 18.14 | 18.03
2019-01-24 21:00 | 17 | 16.9
2019-01-24 21:30 | 15.88 | 15.8
2019-01-24 22:00 | 14.22 | 14.17
2019-01-24 22:30 | 13.26 | 13.23
2019-01-24 23:00 | 12.42 | 12.4
2019-01-24 23:30 | 10.88 | 10.87
2019-01-25 | 9.79 | 9.77
2019-01-25 00:30 | 9.11 | 9.1
2019-01-25 01:00 | 8.77 | 8.76
2019-01-25 01:30 | 8.28 | 8.27
2019-01-25 02:00 | 7.93 | 7.92
2019-01-25 02:30 | 7.79 | 7.78
2019-01-25 03:00 | 7.52 | 7.51
2019-01-25 03:30 | 7.49 | 7.48
2019-01-25 04:00 | 7.35 | 7.33
2019-01-25 04:30 | 7.36 | 7.35
2019-01-25 05:00 | 7.39 | 7.37
2019-01-25 05:30 | 7.29 | 7.28
2019-01-25 06:00 | 7.22 | 7.21
2019-01-25 06:30 | 7.37 | 7.36
2019-01-25 07:00 | 7.8 | 7.78
2019-01-25 07:30 | 7.75 | 7.73
2019-01-25 08:00 | 8.47 | 8.45
2019-01-25 08:30 | 8.74 | 8.72
2019-01-25 09:00 | 8.32 | 8.3
2019-01-25 09:30 | 7.82 | 7.78
2019-01-25 10:00 | 8.68 | 8.64
2019-01-25 10:30 | 8.94 | 8.89
2019-01-25 11:00 | 9.47 | 9.4
2019-01-25 11:30 | 10.17 | 10.08
2019-01-25 12:00 | 10.42 | 10.32
2019-01-25 12:30 | 11.49 | 11.36
2019-01-25 13:00 | 12.55 | 12.4
2019-01-25 13:30 | 14.1 | 13.97
2019-01-25 14:00 | 14.82 | 14.68
2019-01-25 14:30 | 14.65 | 14.47
2019-01-25 15:00 | 15.36 | 15.19
2019-01-25 15:30 | 16.15 | 15.98
2019-01-25 16:00 | 17.15 | 16.99
2019-01-25 16:30 | 18.01 | 17.85
2019-01-25 17:00 | 18.89 | 18.71
2019-01-25 17:30 | 19.56 | 19.39
2019-01-25 18:00 | 19.46 | 19.31
2019-01-25 18:30 | 18.99 | 18.87
2019-01-25 19:00 | 18.45 | 18.34
2019-01-25 19:30 | 18.37 | 18.24
2019-01-25 20:00 | 18.3 | 18.17
2019-01-25 20:30 | 17.64 | 17.53
2019-01-25 21:00 | 16.42 | 16.33
2019-01-25 21:30 | 15.41 | 15.34
2019-01-25 22:00 | 14.2 | 14.15
2019-01-25 22:30 | 13.51 | 13.47
2019-01-25 23:00 | 12.82 | 12.79
2019-01-25 23:30 | 11.41 | 11.4
2019-01-26 | 10.25 | 10.24
2019-01-26 00:30 | 9.44 | 9.43
2019-01-26 01:00 | 8.77 | 8.75
2019-01-26 01:30 | 8.32 | 8.3
2019-01-26 02:00 | 7.91 | 7.9
2019-01-26 02:30 | 7.57 | 7.56
2019-01-26 03:00 | 7.25 | 7.24
2019-01-26 03:30 | 7.12 | 7.1
2019-01-26 04:00 | 6.84 | 6.82
2019-01-26 04:30 | 6.72 | 6.7
2019-01-26 05:00 | 6.73 | 6.71
2019-01-26 05:30 | 6.6 | 6.59
2019-01-26 06:00 | 6.53 | 6.51
2019-01-26 06:30 | 6.49 | 6.47
2019-01-26 07:00 | 6.56 | 6.54
2019-01-26 07:30 | 7.06 | 7.03
2019-01-26 08:00 | 7.05 | 7.03
2019-01-26 08:30 | 7.47 | 7.44
2019-01-26 09:00 | 8.24 | 8.2
2019-01-26 09:30 | 8.92 | 8.87
2019-01-26 10:00 | 9.64 | 9.57
2019-01-26 10:30 | 10.56 | 10.48
2019-01-26 11:00 | 11.73 | 11.63
2019-01-26 11:30 | 11.24 | 11.13
2019-01-26 12:00 | 12.87 | 12.75
2019-01-26 12:30 | 12.45 | 12.33
2019-01-26 13:00 | 12.57 | 12.42
2019-01-26 13:30 | 13.05 | 12.9
2019-01-26 14:00 | 13.78 | 13.62
2019-01-26 14:30 | 14.26 | 14.09
2019-01-26 15:00 | 14.87 | 14.7
2019-01-26 15:30 | 15.68 | 15.51
2019-01-26 16:00 | 16.31 | 16.15
2019-01-26 16:30 | 16.86 | 16.71
2019-01-26 17:00 | 17.33 | 17.19
2019-01-26 17:30 | 17.58 | 17.46
2019-01-26 18:00 | 17.22 | 17.11
2019-01-26 18:30 | 16.61 | 16.53
2019-01-26 19:00 | 16.06 | 16
2019-01-26 19:30 | 15.92 | 15.83
2019-01-26 20:00 | 15.74 | 15.67
2019-01-26 20:30 | 15.2 | 15.13
2019-01-26 21:00 | 14.29 | 14.24
2019-01-26 21:30 | 13.36 | 13.32
2019-01-26 22:00 | 12.52 | 12.5
2019-01-26 22:30 | 11.93 | 11.92
2019-01-26 23:00 | 11.41 | 11.4
2019-01-26 23:30 | 10.31 | 10.29
2019-01-27 | 9.13 | 9.12
2019-01-27 00:30 | 8.33 | 8.32
2019-01-27 01:00 | 7.92 | 7.91
2019-01-27 01:30 | 7.51 | 7.51
2019-01-27 02:00 | 7.1 | 7.09
2019-01-27 02:30 | 6.76 | 6.75
2019-01-27 03:00 | 6.62 | 6.61
2019-01-27 03:30 | 6.43 | 6.42
2019-01-27 04:00 | 6.29 | 6.28
2019-01-27 04:30 | 6.15 | 6.13
2019-01-27 05:00 | 6.02 | 6
2019-01-27 05:30 | 5.69 | 5.64
2019-01-27 06:00 | 5.54 | 5.48
2019-01-27 06:30 | 5.53 | 5.48
2019-01-27 07:00 | 5.41 | 5.38
2019-01-27 07:30 | 5.61 | 5.6
2019-01-27 08:00 | 5.93 | 5.91
2019-01-27 08:30 | 6.6 | 6.58
2019-01-27 09:00 | 6.78 | 6.74
2019-01-27 09:30 | 7.28 | 7.24
2019-01-27 10:00 | 7.8 | 7.75
2019-01-27 10:30 | 8.24 | 8.18
2019-01-27 11:00 | 8.93 | 8.86
2019-01-27 11:30 | 9.86 | 9.77
2019-01-27 12:00 | 10.67 | 10.56
2019-01-27 12:30 | 11.67 | 11.54
2019-01-27 13:00 | 12.6 | 12.45
2019-01-27 13:30 | 13.55 | 13.39
2019-01-27 14:00 | 14.25 | 14.08
2019-01-27 14:30 | 14.93 | 14.76
2019-01-27 15:00 | 15.65 | 15.48
2019-01-27 15:30 | 16.44 | 16.28
2019-01-27 16:00 | 17.03 | 16.88
2019-01-27 16:30 | 17.68 | 17.55
2019-01-27 17:00 | 18.34 | 18.21
2019-01-27 17:30 | 18.74 | 18.61
2019-01-27 18:00 | 18.6 | 18.47
2019-01-27 18:30 | 18.04 | 17.92
2019-01-27 19:00 | 17.38 | 17.28
2019-01-27 19:30 | 16.97 | 16.86
2019-01-27 20:00 | 16.52 | 16.42
2019-01-27 20:30 | 15.8 | 15.73
2019-01-27 21:00 | 14.55 | 14.51
2019-01-27 21:30 | 13.78 | 13.74
2019-01-27 22:00 | 12.79 | 12.77
2019-01-27 22:30 | 12.17 | 12.15
2019-01-27 23:00 | 11.54 | 11.53
2019-01-27 23:30 | 10.28 | 10.27
2019-01-28 | 9.18 | 9.17
2019-01-28 00:30 | 8.4 | 8.39
2019-01-28 01:00 | 7.93 | 7.92
2019-01-28 01:30 | 7.44 | 7.43
2019-01-28 02:00 | 7.06 | 7.05
2019-01-28 02:30 | 6.8 | 6.79
2019-01-28 03:00 | 6.65 | 6.64
2019-01-28 03:30 | 6.42 | 6.4
2019-01-28 04:00 | 6.29 | 6.28
2019-01-28 04:30 | 6.24 | 6.23
2019-01-28 05:00 | 6.05 | 6.03
2019-01-28 05:30 | 5.8 | 5.77
2019-01-28 06:00 | 5.85 | 5.8
2019-01-28 06:30 | 5.74 | 5.7
2019-01-28 07:00 | 5.9 | 5.87
2019-01-28 07:30 | 5.73 | 5.71
2019-01-28 08:00 | 5.96 | 5.94
2019-01-28 08:30 | 6.95 | 6.93
2019-01-28 09:00 | 7.01 | 6.98
2019-01-28 09:30 | 7.66 | 7.62
2019-01-28 10:00 | 8.44 | 8.4
2019-01-28 10:30 | 9.49 | 9.44
2019-01-28 11:00 | 10.71 | 10.65
2019-01-28 11:30 | 10.96 | 10.87
2019-01-28 12:00 | 11.38 | 11.27
2019-01-28 12:30 | 11.97 | 11.86
2019-01-28 13:00 | 12.6 | 12.48
2019-01-28 13:30 | 13.04 | 12.91
2019-01-28 14:00 | 13.82 | 13.69
2019-01-28 14:30 | 14.54 | 14.4
2019-01-28 15:00 | 15.41 | 15.27
2019-01-28 15:30 | 16.36 | 16.21
2019-01-28 16:00 | 17.12 | 16.97
2019-01-28 16:30 | 17.96 | 17.82
2019-01-28 17:00 | 18.87 | 18.74
2019-01-28 17:30 | 19.36 | 19.24
2019-01-28 18:00 | 19.46 | 19.34
2019-01-28 18:30 | 18.92 | 18.81
2019-01-28 19:00 | 18.42 | 18.34
2019-01-28 19:30 | 18.22 | 18.13
2019-01-28 20:00 | 17.8 | 17.72
2019-01-28 20:30 | 17.01 | 16.94
2019-01-28 21:00 | 15.93 | 15.87
2019-01-28 21:30 | 14.58 | 14.53
2019-01-28 22:00 | 13.35 | 13.32
2019-01-28 22:30 | 12.45 | 12.43
2019-01-28 23:00 | 11.72 | 11.7
2019-01-28 23:30 | 10.34 | 10.33
2019-01-29 | 9.1 | 9.08
2019-01-29 00:30 | 8.39 | 8.37
2019-01-29 01:00 | 8.1 | 8.08
2019-01-29 01:30 | 7.65 | 7.64
2019-01-29 02:00 | 7.29 | 7.28
2019-01-29 02:30 | 7.16 | 7.14
2019-01-29 03:00 | 7.01 | 7
2019-01-29 03:30 | 6.99 | 6.97
2019-01-29 04:00 | 6.76 | 6.74
2019-01-29 04:30 | 6.74 | 6.73
2019-01-29 05:00 | 6.83 | 6.81
2019-01-29 05:30 | 6.76 | 6.75
2019-01-29 06:00 | 6.99 | 6.98
2019-01-29 06:30 | 7.8 | 7.79
2019-01-29 07:00 | 8.16 | 8.15
2019-01-29 07:30 | 8.17 | 8.16
2019-01-29 08:00 | 8.37 | 8.37
2019-01-29 08:30 | 8.27 | 8.26
2019-01-29 09:00 | 8.88 | 8.86
2019-01-29 09:30 | 8.7 | 8.68
2019-01-29 10:00 | 9.44 | 9.41
2019-01-29 10:30 | 10.76 | 10.74
2019-01-29 11:00 | 11.24 | 11.21
2019-01-29 11:30 | 11.28 | 11.25
2019-01-29 12:00 | 9.6 | 9.54
2019-01-29 12:30 | 10.03 | 9.95
2019-01-29 13:00 | 10.87 | 10.78
2019-01-29 13:30 | 11.37 | 11.27
2019-01-29 14:00 | 12.25 | 12.15
2019-01-29 14:30 | 12.7 | 12.59
2019-01-29 15:00 | 13.36 | 13.26
2019-01-29 15:30 | 14.61 | 14.51
2019-01-29 16:00 | 15.72 | 15.62
2019-01-29 16:30 | 16.38 | 16.27
2019-01-29 17:00 | 17.39 | 17.28
2019-01-29 17:30 | 18.06 | 17.94
2019-01-29 18:00 | 17.92 | 17.83
2019-01-29 18:30 | 17.87 | 17.79
2019-01-29 19:00 | 18.1 | 18.01
2019-01-29 19:30 | 18.23 | 18.12
2019-01-29 20:00 | 17.78 | 17.69
2019-01-29 20:30 | 17.22 | 17.14
2019-01-29 21:00 | 16.03 | 15.97
2019-01-29 21:30 | 14.6 | 14.56
2019-01-29 22:00 | 13.19 | 13.16
2019-01-29 22:30 | 12 | 11.98
2019-01-29 23:00 | 11.05 | 11.04
2019-01-29 23:30 | 9.57 | 9.55
2019-01-30 | 8.47 | 8.46
2019-01-30 00:30 | 7.8 | 7.79
2019-01-30 01:00 | 7.51 | 7.49
2019-01-30 01:30 | 7.14 | 7.13
2019-01-30 02:00 | 6.91 | 6.89
2019-01-30 02:30 | 6.71 | 6.69
2019-01-30 03:00 | 6.57 | 6.56
2019-01-30 03:30 | 6.49 | 6.48
2019-01-30 04:00 | 6.36 | 6.34
2019-01-30 04:30 | 6.46 | 6.44
2019-01-30 05:00 | 6.65 | 6.64
2019-01-30 05:30 | 6.76 | 6.74
2019-01-30 06:00 | 6.74 | 6.72
2019-01-30 06:30 | 7.19 | 7.18
2019-01-30 07:00 | 7.58 | 7.57
2019-01-30 07:30 | 7.4 | 7.39
2019-01-30 08:00 | 8.24 | 8.23
2019-01-30 08:30 | 7.85 | 7.83
2019-01-30 09:00 | 8.26 | 8.24
2019-01-30 09:30 | 9.32 | 9.3
2019-01-30 10:00 | 7.9 | 7.88
2019-01-30 10:30 | 7.49 | 7.45
2019-01-30 11:00 | 7.7 | 7.62
2019-01-30 11:30 | 8.32 | 8.22
2019-01-30 12:00 | 8.92 | 8.81
2019-01-30 12:30 | 9.08 | 8.98
2019-01-30 13:00 | 9.95 | 9.83
2019-01-30 13:30 | 10.88 | 10.75
2019-01-30 14:00 | 11.9 | 11.76
2019-01-30 14:30 | 12.98 | 12.86
2019-01-30 15:00 | 13.12 | 13
2019-01-30 15:30 | 14.01 | 13.89
2019-01-30 16:00 | 15.16 | 15.05
2019-01-30 16:30 | 15.61 | 15.51
2019-01-30 17:00 | 16.16 | 16.06
2019-01-30 17:30 | 16.97 | 16.88
2019-01-30 18:00 | 17.02 | 16.93
2019-01-30 18:30 | 17.44 | 17.36
2019-01-30 19:00 | 17.77 | 17.69
2019-01-30 19:30 | 17.93 | 17.83
2019-01-30 20:00 | 17.71 | 17.62
2019-01-30 20:30 | 16.83 | 16.75
2019-01-30 21:00 | 15.8 | 15.74
2019-01-30 21:30 | 14.77 | 14.72
2019-01-30 22:00 | 13.71 | 13.67
2019-01-30 22:30 | 12.45 | 12.43
2019-01-30 23:00 | 11.43 | 11.42
2019-01-30 23:30 | 9.88 | 9.87
2019-01-31 | 8.69 | 8.68
2019-01-31 00:30 | 8.04 | 8.02
2019-01-31 01:00 | 7.69 | 7.68
2019-01-31 01:30 | 7.26 | 7.24
2019-01-31 02:00 | 6.95 | 6.94
2019-01-31 02:30 | 6.87 | 6.86
2019-01-31 03:00 | 6.77 | 6.76
2019-01-31 03:30 | 6.63 | 6.62
2019-01-31 04:00 | 6.52 | 6.51
2019-01-31 04:30 | 6.55 | 6.54
2019-01-31 05:00 | 6.66 | 6.65
2019-01-31 05:30 | 6.65 | 6.63
2019-01-31 06:00 | 7.22 | 7.2
2019-01-31 06:30 | 7.8 | 7.79
2019-01-31 07:00 | 7.66 | 7.65
2019-01-31 07:30 | 8.45 | 8.45
2019-01-31 08:00 | 8.67 | 8.67
2019-01-31 08:30 | 8.69 | 8.68
2019-01-31 09:00 | 7.99 | 7.97
2019-01-31 09:30 | 8.2 | 8.16
2019-01-31 10:00 | 8.68 | 8.62
2019-01-31 10:30 | 10.51 | 10.46
2019-01-31 11:00 | 11.03 | 10.96
2019-01-31 11:30 | 11.9 | 11.82
2019-01-31 12:00 | 12.52 | 12.43
2019-01-31 12:30 | 12.1 | 12.01
2019-01-31 13:00 | 11.83 | 11.71
2019-01-31 13:30 | 12.96 | 12.83
2019-01-31 14:00 | 14.22 | 14.08
2019-01-31 14:30 | 14.35 | 14.22
2019-01-31 15:00 | 15.26 | 15.13
2019-01-31 15:30 | 16.52 | 16.38
2019-01-31 16:00 | 17.58 | 17.44
2019-01-31 16:30 | 18.22 | 18.08
2019-01-31 17:00 | 17.86 | 17.71
2019-01-31 17:30 | 19.22 | 19.07
2019-01-31 18:00 | 19.49 | 19.36
2019-01-31 18:30 | 19.33 | 19.2
2019-01-31 19:00 | 19.49 | 19.36
2019-01-31 19:30 | 19.21 | 19.05
2019-01-31 20:00 | 18.8 | 18.66
2019-01-31 20:30 | 18.07 | 17.96
2019-01-31 21:00 | 16.94 | 16.85
2019-01-31 21:30 | 15.43 | 15.36
2019-01-31 22:00 | 14.03 | 13.99
2019-01-31 22:30 | 13.03 | 13
2019-01-31 23:00 | 11.98 | 11.96
2019-01-31 23:30 | 10.41 | 10.4
2019-02-01 | 9.33 | 9.32
2019-02-01 00:30 | 8.67 | 8.66
2019-02-01 01:00 | 8.18 | 8.17
2019-02-01 01:30 | 7.78 | 7.77
2019-02-01 02:00 | 7.4 | 7.39
2019-02-01 02:30 | 7.16 | 7.14
2019-02-01 03:00 | 6.94 | 6.93
2019-02-01 03:30 | 6.84 | 6.83
2019-02-01 04:00 | 6.66 | 6.65
2019-02-01 04:30 | 6.64 | 6.62
2019-02-01 05:00 | 6.78 | 6.77
2019-02-01 05:30 | 6.79 | 6.77
2019-02-01 06:00 | 6.9 | 6.88
2019-02-01 06:30 | 7.14 | 7.12
2019-02-01 07:00 | 7.26 | 7.25
2019-02-01 07:30 | 8.2 | 8.19
2019-02-01 08:00 | 6.92 | 6.91
2019-02-01 08:30 | 6.66 | 6.64
2019-02-01 09:00 | 7.05 | 7.02
2019-02-01 09:30 | 7.3 | 7.26
2019-02-01 10:00 | 7.9 | 7.86
2019-02-01 10:30 | 8.02 | 7.97
2019-02-01 11:00 | 9.31 | 9.26
2019-02-01 11:30 | 9.18 | 9.08
2019-02-01 12:00 | 8.94 | 8.83
2019-02-01 12:30 | 9.43 | 9.32
2019-02-01 13:00 | 10.54 | 10.42
2019-02-01 13:30 | 11.21 | 11.08
2019-02-01 14:00 | 11.67 | 11.52
2019-02-01 14:30 | 12.62 | 12.48
2019-02-01 15:00 | 12.65 | 12.5
2019-02-01 15:30 | 14.16 | 14.02
2019-02-01 16:00 | 14.91 | 14.77
2019-02-01 16:30 | 16.45 | 16.33
2019-02-01 17:00 | 16.31 | 16.2
2019-02-01 17:30 | 16.08 | 15.99
2019-02-01 18:00 | 15.55 | 15.47
2019-02-01 18:30 | 15.44 | 15.38
2019-02-01 19:00 | 15.73 | 15.66
2019-02-01 19:30 | 15.83 | 15.75
2019-02-01 20:00 | 15.79 | 15.72
2019-02-01 20:30 | 15.39 | 15.33
2019-02-01 21:00 | 14.54 | 14.49
2019-02-01 21:30 | 13.69 | 13.65
2019-02-01 22:00 | 12.68 | 12.65
2019-02-01 22:30 | 12.04 | 12.02
2019-02-01 23:00 | 11.48 | 11.46
2019-02-01 23:30 | 10.13 | 10.11
2019-02-02 | 9.03 | 9.02
2019-02-02 00:30 | 8.27 | 8.26
2019-02-02 01:00 | 8.01 | 8
2019-02-02 01:30 | 7.61 | 7.6
2019-02-02 02:00 | 7.21 | 7.21
2019-02-02 02:30 | 7.05 | 7.03
2019-02-02 03:00 | 6.8 | 6.79
2019-02-02 03:30 | 6.68 | 6.66
2019-02-02 04:00 | 6.52 | 6.51
2019-02-02 04:30 | 6.4 | 6.38
2019-02-02 05:00 | 6.41 | 6.4
2019-02-02 05:30 | 6.29 | 6.27
2019-02-02 06:00 | 6.08 | 6.04
2019-02-02 06:30 | 6.11 | 6.08
2019-02-02 07:00 | 6.37 | 6.35
2019-02-02 07:30 | 7.16 | 7.14
2019-02-02 08:00 | 7.8 | 7.79
2019-02-02 08:30 | 6.82 | 6.8
2019-02-02 09:00 | 6.04 | 6.01
2019-02-02 09:30 | 7.76 | 7.72
2019-02-02 10:00 | 7.32 | 7.28
2019-02-02 10:30 | 7.27 | 7.22
2019-02-02 11:00 | 7.34 | 7.29
2019-02-02 11:30 | 7.98 | 7.92
2019-02-02 12:00 | 9.58 | 9.52
2019-02-02 12:30 | 10.68 | 10.61
2019-02-02 13:00 | 9.74 | 9.65
2019-02-02 13:30 | 11.12 | 11.03
2019-02-02 14:00 | 12.72 | 12.64
2019-02-02 14:30 | 11.37 | 11.28
2019-02-02 15:00 | 11.83 | 11.74
2019-02-02 15:30 | 12.75 | 12.67
2019-02-02 16:00 | 13.2 | 13.13
2019-02-02 16:30 | 13.48 | 13.41
2019-02-02 17:00 | 14.6 | 14.54
2019-02-02 17:30 | 14.76 | 14.7
2019-02-02 18:00 | 15.14 | 15.09
2019-02-02 18:30 | 15.07 | 15.03
2019-02-02 19:00 | 14.89 | 14.85
2019-02-02 19:30 | 14.84 | 14.79
2019-02-02 20:00 | 14.73 | 14.68
2019-02-02 20:30 | 14.17 | 14.13
2019-02-02 21:00 | 13.59 | 13.55
2019-02-02 21:30 | 12.66 | 12.63
2019-02-02 22:00 | 11.86 | 11.84
2019-02-02 22:30 | 11.14 | 11.13
2019-02-02 23:00 | 10.62 | 10.61
2019-02-02 23:30 | 9.57 | 9.56
2019-02-03 | 8.63 | 8.62
2019-02-03 00:30 | 7.95 | 7.94
2019-02-03 01:00 | 7.64 | 7.62
2019-02-03 01:30 | 7.2 | 7.19
2019-02-03 02:00 | 6.94 | 6.93
2019-02-03 02:30 | 6.62 | 6.61
2019-02-03 03:00 | 6.35 | 6.34
2019-02-03 03:30 | 6.33 | 6.32
2019-02-03 04:00 | 6.17 | 6.15
2019-02-03 04:30 | 6.01 | 6
2019-02-03 05:00 | 5.98 | 5.96
2019-02-03 05:30 | 5.87 | 5.83
2019-02-03 06:00 | 5.84 | 5.78
2019-02-03 06:30 | 5.9 | 5.85
2019-02-03 07:00 | 5.95 | 5.91
2019-02-03 07:30 | 5.86 | 5.83
2019-02-03 08:00 | 5.96 | 5.95
2019-02-03 08:30 | 5.54 | 5.52
2019-02-03 09:00 | 6.51 | 6.49
2019-02-03 09:30 | 6.42 | 6.39
2019-02-03 10:00 | 7.75 | 7.73
2019-02-03 10:30 | 9.46 | 9.43
2019-02-03 11:00 | 9.96 | 9.94
2019-02-03 11:30 | 10.13 | 10.11
2019-02-03 12:00 | 8.92 | 8.89
2019-02-03 12:30 | 9.2 | 9.18
2019-02-03 13:00 | 9.03 | 9
2019-02-03 13:30 | 7.32 | 7.28
2019-02-03 14:00 | 7.81 | 7.77
2019-02-03 14:30 | 8.9 | 8.87
2019-02-03 15:00 | 9.44 | 9.4
2019-02-03 15:30 | 11.12 | 11.08
2019-02-03 16:00 | 12.14 | 12.11
2019-02-03 16:30 | 13.15 | 13.12
2019-02-03 17:00 | 13.5 | 13.48
2019-02-03 17:30 | 14.43 | 14.4
2019-02-03 18:00 | 15.02 | 15
2019-02-03 18:30 | 14.75 | 14.72
2019-02-03 19:00 | 14.68 | 14.66
2019-02-03 19:30 | 14.62 | 14.59
2019-02-03 20:00 | 14.47 | 14.44
2019-02-03 20:30 | 13.78 | 13.76
2019-02-03 21:00 | 13.04 | 13.03
2019-02-03 21:30 | 12.05 | 12.04
2019-02-03 22:00 | 11.02 | 11.01
2019-02-03 22:30 | 10.35 | 10.34
2019-02-03 23:00 | 9.72 | 9.71
2019-02-03 23:30 | 8.6 | 8.59
2019-02-04 | 7.53 | 7.52
2019-02-04 00:30 | 6.98 | 6.98
2019-02-04 01:00 | 6.63 | 6.62
2019-02-04 01:30 | 6.25 | 6.24
2019-02-04 02:00 | 6.1 | 6.09
2019-02-04 02:30 | 5.86 | 5.85
2019-02-04 03:00 | 5.8 | 5.78
2019-02-04 03:30 | 5.79 | 5.77
2019-02-04 04:00 | 5.85 | 5.83
2019-02-04 04:30 | 5.89 | 5.87
2019-02-04 05:00 | 6.06 | 6.04
2019-02-04 05:30 | 6.17 | 6.14
2019-02-04 06:00 | 6.41 | 6.36
2019-02-04 06:30 | 7.23 | 7.2
2019-02-04 07:00 | 7.52 | 7.5
2019-02-04 07:30 | 7.97 | 7.96
2019-02-04 08:00 | 8.2 | 8.2
2019-02-04 08:30 | 8.09 | 8.08
2019-02-04 09:00 | 7.18 | 7.18
2019-02-04 09:30 | 7.77 | 7.76
2019-02-04 10:00 | 7.85 | 7.84
2019-02-04 10:30 | 7.46 | 7.45
2019-02-04 11:00 | 6.42 | 6.41
2019-02-04 11:30 | 7.52 | 7.51
2019-02-04 12:00 | 5.93 | 5.92
2019-02-04 12:30 | 5.92 | 5.9
2019-02-04 13:00 | 6.72 | 6.69
2019-02-04 13:30 | 6.98 | 6.94
2019-02-04 14:00 | 7.69 | 7.64
2019-02-04 14:30 | 8.51 | 8.46
2019-02-04 15:00 | 8.97 | 8.93
2019-02-04 15:30 | 9.86 | 9.81
2019-02-04 16:00 | 11.59 | 11.53
2019-02-04 16:30 | 12.88 | 12.83
2019-02-04 17:00 | 14.4 | 14.35
2019-02-04 17:30 | 15.56 | 15.51
2019-02-04 18:00 | 15.9 | 15.86
2019-02-04 18:30 | 16.13 | 16.09
2019-02-04 19:00 | 16.46 | 16.42
2019-02-04 19:30 | 16.49 | 16.44
2019-02-04 20:00 | 16.04 | 16
2019-02-04 20:30 | 15.62 | 15.59
2019-02-04 21:00 | 14.59 | 14.57
2019-02-04 21:30 | 13.35 | 13.33
2019-02-04 22:00 | 12.25 | 12.24
2019-02-04 22:30 | 11.19 | 11.19
2019-02-04 23:00 | 10.34 | 10.33
2019-02-04 23:30 | 9.09 | 9.09
2019-02-05 | 8.14 | 8.14
2019-02-05 00:30 | 7.48 | 7.47
2019-02-05 01:00 | 7.18 | 7.17
2019-02-05 01:30 | 6.88 | 6.87
2019-02-05 02:00 | 6.61 | 6.6
2019-02-05 02:30 | 6.47 | 6.46
2019-02-05 03:00 | 6.29 | 6.27
2019-02-05 03:30 | 6.2 | 6.18
2019-02-05 04:00 | 6.3 | 6.29
2019-02-05 04:30 | 6.46 | 6.44
2019-02-05 05:00 | 6.57 | 6.55
2019-02-05 05:30 | 6.8 | 6.78
2019-02-05 06:00 | 6.93 | 6.89
2019-02-05 06:30 | 7.54 | 7.52
2019-02-05 07:00 | 7.74 | 7.73
2019-02-05 07:30 | 8.05 | 8.04
2019-02-05 08:00 | 6.89 | 6.88
2019-02-05 08:30 | 6.45 | 6.44
2019-02-05 09:00 | 6.53 | 6.51
2019-02-05 09:30 | 7.96 | 7.95
2019-02-05 10:00 | 8.44 | 8.43
2019-02-05 10:30 | 6.96 | 6.94
2019-02-05 11:00 | 7.11 | 7.09
2019-02-05 11:30 | 7.73 | 7.69
2019-02-05 12:00 | 7.72 | 7.68
2019-02-05 12:30 | 7.89 | 7.84
2019-02-05 13:00 | 8.16 | 8.1
2019-02-05 13:30 | 9.11 | 9.04
2019-02-05 14:00 | 10.64 | 10.57
2019-02-05 14:30 | 11.02 | 10.96
2019-02-05 15:00 | 12.32 | 12.27
2019-02-05 15:30 | 12.71 | 12.66
2019-02-05 16:00 | 13.15 | 13.11
2019-02-05 16:30 | 13.7 | 13.66
2019-02-05 17:00 | 13.45 | 13.41
2019-02-05 17:30 | 14.25 | 14.21
2019-02-05 18:00 | 15.06 | 15.03
2019-02-05 18:30 | 15.46 | 15.42
2019-02-05 19:00 | 16.04 | 15.98
2019-02-05 19:30 | 16.07 | 16
2019-02-05 20:00 | 16.27 | 16.21
2019-02-05 20:30 | 15.59 | 15.55
2019-02-05 21:00 | 14.44 | 14.41
2019-02-05 21:30 | 13.27 | 13.25
2019-02-05 22:00 | 12.35 | 12.34
2019-02-05 22:30 | 11.24 | 11.24
2019-02-05 23:00 | 10.61 | 10.6
2019-02-05 23:30 | 9.44 | 9.43
2019-02-06 | 8.47 | 8.46
2019-02-06 00:30 | 7.72 | 7.72
2019-02-06 01:00 | 7.48 | 7.47
2019-02-06 01:30 | 7.18 | 7.17
2019-02-06 02:00 | 7.04 | 7.03
2019-02-06 02:30 | 6.7 | 6.69
2019-02-06 03:00 | 6.64 | 6.63
2019-02-06 03:30 | 6.52 | 6.51
2019-02-06 04:00 | 6.44 | 6.43
2019-02-06 04:30 | 6.56 | 6.55
2019-02-06 05:00 | 6.75 | 6.74
2019-02-06 05:30 | 6.99 | 6.98
2019-02-06 06:00 | 7.24 | 7.21
2019-02-06 06:30 | 7.69 | 7.67
2019-02-06 07:00 | 7.83 | 7.81
2019-02-06 07:30 | 8.14 | 8.12
2019-02-06 08:00 | 8.82 | 8.81
2019-02-06 08:30 | 8.31 | 8.31
2019-02-06 09:00 | 7.8 | 7.8
2019-02-06 09:30 | 6.87 | 6.86
2019-02-06 10:00 | 7.75 | 7.74
2019-02-06 10:30 | 6.96 | 6.95
2019-02-06 11:00 | 7.57 | 7.56
2019-02-06 11:30 | 8.41 | 8.4
2019-02-06 12:00 | 9.23 | 9.22
2019-02-06 12:30 | 8.9 | 8.89
2019-02-06 13:00 | 7.77 | 7.75
2019-02-06 13:30 | 7.62 | 7.59
2019-02-06 14:00 | 9.57 | 9.55
2019-02-06 14:30 | 10.75 | 10.73
2019-02-06 15:00 | 10.36 | 10.34
2019-02-06 15:30 | 9.29 | 9.26
2019-02-06 16:00 | 10.91 | 10.87
2019-02-06 16:30 | 11.67 | 11.64
2019-02-06 17:00 | 13.37 | 13.33
2019-02-06 17:30 | 14.37 | 14.34
2019-02-06 18:00 | 14.83 | 14.8
2019-02-06 18:30 | 15.08 | 15.06
2019-02-06 19:00 | 15.75 | 15.71
2019-02-06 19:30 | 15.88 | 15.83
2019-02-06 20:00 | 15.72 | 15.68
2019-02-06 20:30 | 15.17 | 15.14
2019-02-06 21:00 | 14.25 | 14.22
2019-02-06 21:30 | 13.16 | 13.14
2019-02-06 22:00 | 12.21 | 12.2
2019-02-06 22:30 | 11.13 | 11.13
2019-02-06 23:00 | 10.35 | 10.34
2019-02-06 23:30 | 9.18 | 9.17
2019-02-07 | 8.28 | 8.28
2019-02-07 00:30 | 7.61 | 7.6
2019-02-07 01:00 | 7.15 | 7.14
2019-02-07 01:30 | 6.84 | 6.83
2019-02-07 02:00 | 6.68 | 6.67
2019-02-07 02:30 | 6.61 | 6.6
2019-02-07 03:00 | 6.34 | 6.33
2019-02-07 03:30 | 6.34 | 6.33
2019-02-07 04:00 | 6.31 | 6.3
2019-02-07 04:30 | 6.5 | 6.49
2019-02-07 05:00 | 6.51 | 6.5
2019-02-07 05:30 | 6.75 | 6.73
2019-02-07 06:00 | 7.11 | 7.08
2019-02-07 06:30 | 7.3 | 7.28
2019-02-07 07:00 | 7.82 | 7.81
2019-02-07 07:30 | 8.14 | 8.13
2019-02-07 08:00 | 8.1 | 8.1
2019-02-07 08:30 | 7.21 | 7.2
2019-02-07 09:00 | 5.71 | 5.69
2019-02-07 09:30 | 6.41 | 6.4
2019-02-07 10:00 | 7.34 | 7.32
2019-02-07 10:30 | 7.14 | 7.12
2019-02-07 11:00 | 7.5 | 7.48
2019-02-07 11:30 | 7.45 | 7.43
2019-02-07 12:00 | 7.01 | 6.98
2019-02-07 12:30 | 9.25 | 9.23
2019-02-07 13:00 | 7.82 | 7.79
2019-02-07 13:30 | 9.37 | 9.35
2019-02-07 14:00 | 9.85 | 9.83
2019-02-07 14:30 | 8.31 | 8.28
2019-02-07 15:00 | 10.16 | 10.15
2019-02-07 15:30 | 10.43 | 10.41
2019-02-07 16:00 | 10.59 | 10.57
2019-02-07 16:30 | 11.07 | 11.05
2019-02-07 17:00 | 11.33 | 11.32
2019-02-07 17:30 | 12.75 | 12.73
2019-02-07 18:00 | 13.17 | 13.15
2019-02-07 18:30 | 13.64 | 13.63
2019-02-07 19:00 | 14.38 | 14.35
2019-02-07 19:30 | 14.57 | 14.54
2019-02-07 20:00 | 14.62 | 14.59
2019-02-07 20:30 | 13.98 | 13.96
2019-02-07 21:00 | 13.45 | 13.44
2019-02-07 21:30 | 12.53 | 12.52
2019-02-07 22:00 | 11.58 | 11.58
2019-02-07 22:30 | 10.63 | 10.62
2019-02-07 23:00 | 10.26 | 10.25
2019-02-07 23:30 | 9.07 | 9.07
2019-02-08 | 8.15 | 8.15
2019-02-08 00:30 | 7.49 | 7.48
2019-02-08 01:00 | 7.2 | 7.2
2019-02-08 01:30 | 6.89 | 6.88
2019-02-08 02:00 | 6.63 | 6.61
2019-02-08 02:30 | 6.57 | 6.56
2019-02-08 03:00 | 6.43 | 6.42
2019-02-08 03:30 | 6.32 | 6.31
2019-02-08 04:00 | 6.31 | 6.3
2019-02-08 04:30 | 6.27 | 6.26
2019-02-08 05:00 | 6.42 | 6.41
2019-02-08 05:30 | 6.76 | 6.75
2019-02-08 06:00 | 7.36 | 7.33
2019-02-08 06:30 | 7.7 | 7.68
2019-02-08 07:00 | 8.12 | 8.1
2019-02-08 07:30 | 8.43 | 8.42
2019-02-08 08:00 | 8.16 | 8.16
2019-02-08 08:30 | 8.17 | 8.16
2019-02-08 09:00 | 7.79 | 7.78
2019-02-08 09:30 | 7.91 | 7.9
2019-02-08 10:00 | 8.35 | 8.34
2019-02-08 10:30 | 6.22 | 6.2
2019-02-08 11:00 | 6.1 | 6.07
2019-02-08 11:30 | 6.4 | 6.37
2019-02-08 12:00 | 7.46 | 7.43
2019-02-08 12:30 | 7.45 | 7.43
2019-02-08 13:00 | 7.03 | 7
2019-02-08 13:30 | 7.51 | 7.47
2019-02-08 14:00 | 8.02 | 7.98
2019-02-08 14:30 | 9.49 | 9.45
2019-02-08 15:00 | 10.77 | 10.74
2019-02-08 15:30 | 11.55 | 11.51
2019-02-08 16:00 | 12.15 | 12.11
2019-02-08 16:30 | 13.03 | 12.99
2019-02-08 17:00 | 13.66 | 13.62
2019-02-08 17:30 | 14.3 | 14.26
2019-02-08 18:00 | 14.63 | 14.6
2019-02-08 18:30 | 14.79 | 14.76
2019-02-08 19:00 | 15.13 | 15.1
2019-02-08 19:30 | 15.42 | 15.37
2019-02-08 20:00 | 15.5 | 15.46
2019-02-08 20:30 | 15.09 | 15.05
2019-02-08 21:00 | 14.17 | 14.14
2019-02-08 21:30 | 13.3 | 13.28
2019-02-08 22:00 | 12.41 | 12.4
2019-02-08 22:30 | 11.76 | 11.75
2019-02-08 23:00 | 11.28 | 11.27
2019-02-08 23:30 | 10.12 | 10.11
2019-02-09 | 9.12 | 9.11
2019-02-09 00:30 | 8.35 | 8.34
2019-02-09 01:00 | 7.99 | 7.99
2019-02-09 01:30 | 7.56 | 7.56
2019-02-09 02:00 | 7.23 | 7.22
2019-02-09 02:30 | 7.04 | 7.03
2019-02-09 03:00 | 6.73 | 6.72
2019-02-09 03:30 | 6.64 | 6.63
2019-02-09 04:00 | 6.49 | 6.48
2019-02-09 04:30 | 6.37 | 6.35
2019-02-09 05:00 | 6.33 | 6.32
2019-02-09 05:30 | 6.3 | 6.27
2019-02-09 06:00 | 6.21 | 6.16
2019-02-09 06:30 | 6.1 | 6.05
2019-02-09 07:00 | 6.2 | 6.16
2019-02-09 07:30 | 6.66 | 6.64
2019-02-09 08:00 | 6.31 | 6.3
2019-02-09 08:30 | 7.05 | 7.04
2019-02-09 09:00 | 7.28 | 7.26
2019-02-09 09:30 | 7.41 | 7.38
2019-02-09 10:00 | 7.9 | 7.87
2019-02-09 10:30 | 8.78 | 8.74
2019-02-09 11:00 | 9.16 | 9.11
2019-02-09 11:30 | 9.74 | 9.68
2019-02-09 12:00 | 10.46 | 10.39
2019-02-09 12:30 | 11.77 | 11.68
2019-02-09 13:00 | 12.65 | 12.53
2019-02-09 13:30 | 13.69 | 13.56
2019-02-09 14:00 | 14.25 | 14.12
2019-02-09 14:30 | 14.97 | 14.83
2019-02-09 15:00 | 15.82 | 15.68
2019-02-09 15:30 | 16.88 | 16.74
2019-02-09 16:00 | 17.76 | 17.62
2019-02-09 16:30 | 18.61 | 18.46
2019-02-09 17:00 | 19.39 | 19.26
2019-02-09 17:30 | 19.6 | 19.48
2019-02-09 18:00 | 19.63 | 19.52
2019-02-09 18:30 | 19.03 | 18.93
2019-02-09 19:00 | 18.34 | 18.24
2019-02-09 19:30 | 18.07 | 17.96
2019-02-09 20:00 | 17.59 | 17.5
2019-02-09 20:30 | 16.96 | 16.89
2019-02-09 21:00 | 16.12 | 16.06
2019-02-09 21:30 | 15.27 | 15.22
2019-02-09 22:00 | 14.47 | 14.42
2019-02-09 22:30 | 13.86 | 13.83
2019-02-09 23:00 | 13.13 | 13.12
2019-02-09 23:30 | 11.61 | 11.6
2019-02-10 | 10.4 | 10.39
2019-02-10 00:30 | 9.46 | 9.45
2019-02-10 01:00 | 9.06 | 9.05
2019-02-10 01:30 | 8.54 | 8.54
2019-02-10 02:00 | 8.1 | 8.09
2019-02-10 02:30 | 7.71 | 7.7
2019-02-10 03:00 | 7.41 | 7.4
2019-02-10 03:30 | 7.18 | 7.17
2019-02-10 04:00 | 7.01 | 7
2019-02-10 04:30 | 6.82 | 6.82
2019-02-10 05:00 | 6.72 | 6.71
2019-02-10 05:30 | 6.49 | 6.47
2019-02-10 06:00 | 6.41 | 6.36
2019-02-10 06:30 | 6.35 | 6.31
2019-02-10 07:00 | 6.45 | 6.43
2019-02-10 07:30 | 6.59 | 6.58
2019-02-10 08:00 | 6.86 | 6.84
2019-02-10 08:30 | 7.25 | 7.23
2019-02-10 09:00 | 7.75 | 7.73
2019-02-10 09:30 | 8.49 | 8.46
2019-02-10 10:00 | 10.21 | 10.17
2019-02-10 10:30 | 10.77 | 10.71
2019-02-10 11:00 | 11.5 | 11.42
2019-02-10 11:30 | 12.91 | 12.81
2019-02-10 12:00 | 14.14 | 14.04
2019-02-10 12:30 | 14.87 | 14.75
2019-02-10 13:00 | 15.37 | 15.24
2019-02-10 13:30 | 15.75 | 15.6
2019-02-10 14:00 | 17.6 | 17.43
2019-02-10 14:30 | 17.2 | 17.03
2019-02-10 15:00 | 17.72 | 17.56
2019-02-10 15:30 | 18.3 | 18.14
2019-02-10 16:00 | 18.95 | 18.8
2019-02-10 16:30 | 19.34 | 19.19
2019-02-10 17:00 | 19.8 | 19.66
2019-02-10 17:30 | 19.76 | 19.63
2019-02-10 18:00 | 19.68 | 19.57
2019-02-10 18:30 | 19.13 | 19.03
2019-02-10 19:00 | 18.63 | 18.54
2019-02-10 19:30 | 17.98 | 17.89
2019-02-10 20:00 | 17.37 | 17.3
2019-02-10 20:30 | 16.55 | 16.49
2019-02-10 21:00 | 15.41 | 15.36
2019-02-10 21:30 | 14.23 | 14.21
2019-02-10 22:00 | 13.14 | 13.12
2019-02-10 22:30 | 12.43 | 12.43
2019-02-10 23:00 | 11.79 | 11.78
2019-02-10 23:30 | 10.43 | 10.42
2019-02-11 | 9.27 | 9.26
2019-02-11 00:30 | 8.65 | 8.64
2019-02-11 01:00 | 8.27 | 8.26
2019-02-11 01:30 | 7.83 | 7.82
2019-02-11 02:00 | 7.55 | 7.54
2019-02-11 02:30 | 7.33 | 7.32
2019-02-11 03:00 | 7.18 | 7.17
2019-02-11 03:30 | 7.12 | 7.11
2019-02-11 04:00 | 6.95 | 6.94
2019-02-11 04:30 | 6.97 | 6.96
2019-02-11 05:00 | 7.11 | 7.1
2019-02-11 05:30 | 7.33 | 7.32
2019-02-11 06:00 | 7.34 | 7.33
2019-02-11 06:30 | 7.54 | 7.53
2019-02-11 07:00 | 8 | 7.99
2019-02-11 07:30 | 8.13 | 8.13
2019-02-11 08:00 | 7.67 | 7.66
2019-02-11 08:30 | 7.51 | 7.5
2019-02-11 09:00 | 8.59 | 8.57
2019-02-11 09:30 | 7.89 | 7.87
2019-02-11 10:00 | 6.99 | 6.96
2019-02-11 10:30 | 7.72 | 7.69
2019-02-11 11:00 | 8.08 | 8.04
2019-02-11 11:30 | 9.07 | 9.03
2019-02-11 12:00 | 9.39 | 9.33
2019-02-11 12:30 | 10.54 | 10.48
2019-02-11 13:00 | 11.07 | 10.99
2019-02-11 13:30 | 12.27 | 12.18
2019-02-11 14:00 | 12.46 | 12.35
2019-02-11 14:30 | 13.11 | 12.97
2019-02-11 15:00 | 13.84 | 13.7
2019-02-11 15:30 | 15.32 | 15.16
2019-02-11 16:00 | 17.2 | 17.03
2019-02-11 16:30 | 18.26 | 18.11
2019-02-11 17:00 | 19.08 | 18.93
2019-02-11 17:30 | 19.88 | 19.74
2019-02-11 18:00 | 20.1 | 19.97
2019-02-11 18:30 | 19.61 | 19.51
2019-02-11 19:00 | 19.57 | 19.47
2019-02-11 19:30 | 19.37 | 19.25
2019-02-11 20:00 | 18.53 | 18.44
2019-02-11 20:30 | 17.43 | 17.36
2019-02-11 21:00 | 16.4 | 16.34
2019-02-11 21:30 | 15.14 | 15.1
2019-02-11 22:00 | 13.86 | 13.83
2019-02-11 22:30 | 12.41 | 12.4
2019-02-11 23:00 | 11.42 | 11.41
2019-02-11 23:30 | 10.1 | 10.09
2019-02-12 | 8.98 | 8.98
2019-02-12 00:30 | 8.24 | 8.23
2019-02-12 01:00 | 7.98 | 7.97
2019-02-12 01:30 | 7.69 | 7.68
2019-02-12 02:00 | 7.46 | 7.45
2019-02-12 02:30 | 7.25 | 7.24
2019-02-12 03:00 | 7.02 | 7.02
2019-02-12 03:30 | 6.92 | 6.91
2019-02-12 04:00 | 6.83 | 6.82
2019-02-12 04:30 | 6.77 | 6.76
2019-02-12 05:00 | 6.92 | 6.91
2019-02-12 05:30 | 7.04 | 7.03
2019-02-12 06:00 | 7.22 | 7.2
2019-02-12 06:30 | 7.38 | 7.36
2019-02-12 07:00 | 7.69 | 7.68
2019-02-12 07:30 | 8.05 | 8.05
2019-02-12 08:00 | 8.11 | 8.1
2019-02-12 08:30 | 7.86 | 7.85
2019-02-12 09:00 | 8.09 | 8.07
2019-02-12 09:30 | 8.51 | 8.47
2019-02-12 10:00 | 8.92 | 8.86
2019-02-12 10:30 | 9.35 | 9.28
2019-02-12 11:00 | 10.05 | 9.94
2019-02-12 11:30 | 10.88 | 10.77
2019-02-12 12:00 | 11.6 | 11.46
2019-02-12 12:30 | 12.47 | 12.34
2019-02-12 13:00 | 13.62 | 13.47
2019-02-12 13:30 | 14.66 | 14.5
2019-02-12 14:00 | 17.11 | 16.95
2019-02-12 14:30 | 16.86 | 16.67
2019-02-12 15:00 | 17.2 | 17
2019-02-12 15:30 | 18.76 | 18.54
2019-02-12 16:00 | 20.77 | 20.55
2019-02-12 16:30 | 22.1 | 21.88
2019-02-12 17:00 | 23.41 | 23.18
2019-02-12 17:30 | 24.18 | 23.95
2019-02-12 18:00 | 24.85 | 24.63
2019-02-12 18:30 | 24.82 | 24.6
2019-02-12 19:00 | 24.55 | 24.33
2019-02-12 19:30 | 24.39 | 24.16
2019-02-12 20:00 | 23.73 | 23.51
2019-02-12 20:30 | 22.03 | 21.87
2019-02-12 21:00 | 20.81 | 20.67
2019-02-12 21:30 | 19.11 | 18.99
2019-02-12 22:00 | 17.23 | 17.14
2019-02-12 22:30 | 15.53 | 15.47
2019-02-12 23:00 | 14.25 | 14.21
2019-02-12 23:30 | 12.5 | 12.46
2019-02-13 | 11.18 | 11.16
2019-02-13 00:30 | 10.16 | 10.15
2019-02-13 01:00 | 9.65 | 9.64
2019-02-13 01:30 | 9.21 | 9.2
2019-02-13 02:00 | 8.74 | 8.73
2019-02-13 02:30 | 8.5 | 8.49
2019-02-13 03:00 | 8.22 | 8.21
2019-02-13 03:30 | 8.07 | 8.06
2019-02-13 04:00 | 7.89 | 7.88
2019-02-13 04:30 | 7.81 | 7.8
2019-02-13 05:00 | 7.91 | 7.9
2019-02-13 05:30 | 7.99 | 7.98
2019-02-13 06:00 | 8.27 | 8.26
2019-02-13 06:30 | 8.82 | 8.82
2019-02-13 07:00 | 9.33 | 9.32
2019-02-13 07:30 | 9.65 | 9.65
2019-02-13 08:00 | 9.91 | 9.9
2019-02-13 08:30 | 10.42 | 10.39
2019-02-13 09:00 | 10.97 | 10.92
2019-02-13 09:30 | 11.66 | 11.59
2019-02-13 10:00 | 11.65 | 11.54
2019-02-13 10:30 | 12.53 | 12.4
2019-02-13 11:00 | 13.33 | 13.18
2019-02-13 11:30 | 14.46 | 14.29
2019-02-13 12:00 | 15.67 | 15.46
2019-02-13 12:30 | 16.99 | 16.77
2019-02-13 13:00 | 17.72 | 17.5
2019-02-13 13:30 | 18.55 | 18.32
2019-02-13 14:00 | 19.28 | 19.04
2019-02-13 14:30 | 19.73 | 19.49
2019-02-13 15:00 | 20.75 | 20.48
2019-02-13 15:30 | 22.39 | 22.12
2019-02-13 16:00 | 23.26 | 22.98
2019-02-13 16:30 | 24.75 | 24.48
2019-02-13 17:00 | 25.66 | 25.39
2019-02-13 17:30 | 26.69 | 26.41
2019-02-13 18:00 | 26.81 | 26.54
2019-02-13 18:30 | 26.85 | 26.58
2019-02-13 19:00 | 26.37 | 26.07
2019-02-13 19:30 | 26.29 | 25.98
2019-02-13 20:00 | 25.46 | 25.16
2019-02-13 20:30 | 24.83 | 24.57
2019-02-13 21:00 | 23.52 | 23.31
2019-02-13 21:30 | 21.81 | 21.64
2019-02-13 22:00 | 19.76 | 19.63
2019-02-13 22:30 | 17.21 | 17.11
2019-02-13 23:00 | 15.84 | 15.77
2019-02-13 23:30 | 14.26 | 14.2
2019-02-14 | 12.9 | 12.85
2019-02-14 00:30 | 12.14 | 12.1
2019-02-14 01:00 | 11.71 | 11.68
2019-02-14 01:30 | 10.97 | 10.94
2019-02-14 02:00 | 10.34 | 10.32
2019-02-14 02:30 | 10.08 | 10.06
2019-02-14 03:00 | 9.59 | 9.58
2019-02-14 03:30 | 9.31 | 9.3
2019-02-14 04:00 | 9.04 | 9.03
2019-02-14 04:30 | 8.92 | 8.91
2019-02-14 05:00 | 8.95 | 8.94
2019-02-14 05:30 | 9.09 | 9.08
2019-02-14 06:00 | 9.05 | 9.04
2019-02-14 06:30 | 9.17 | 9.16
2019-02-14 07:00 | 9.35 | 9.35
2019-02-14 07:30 | 9.88 | 9.87
2019-02-14 08:00 | 10.07 | 10.06
2019-02-14 08:30 | 9.14 | 9.12
2019-02-14 09:00 | 9.36 | 9.33
2019-02-14 09:30 | 9.72 | 9.67
2019-02-14 10:00 | 10.97 | 10.91
2019-02-14 10:30 | 9.68 | 9.6
2019-02-14 11:00 | 10.09 | 9.99
2019-02-14 11:30 | 11.02 | 10.92
2019-02-14 12:00 | 11.25 | 11.14
2019-02-14 12:30 | 12.42 | 12.32
2019-02-14 13:00 | 12.17 | 12.06
2019-02-14 13:30 | 13.97 | 13.88
2019-02-14 14:00 | 15.19 | 15.09
2019-02-14 14:30 | 14.62 | 14.53
2019-02-14 15:00 | 14.54 | 14.46
2019-02-14 15:30 | 13.8 | 13.73
2019-02-14 16:00 | 13.89 | 13.81
2019-02-14 16:30 | 14.36 | 14.29
2019-02-14 17:00 | 15.41 | 15.34
2019-02-14 17:30 | 15.72 | 15.66
2019-02-14 18:00 | 16.3 | 16.24
2019-02-14 18:30 | 16.32 | 16.27
2019-02-14 19:00 | 16.57 | 16.5
2019-02-14 19:30 | 16.48 | 16.4
2019-02-14 20:00 | 16.1 | 16.03
2019-02-14 20:30 | 15.47 | 15.42
2019-02-14 21:00 | 14.56 | 14.52
2019-02-14 21:30 | 13.34 | 13.31
2019-02-14 22:00 | 12.01 | 12
2019-02-14 22:30 | 11.03 | 11.03
2019-02-14 23:00 | 10.27 | 10.26
2019-02-14 23:30 | 9.07 | 9.06
2019-02-15 | 8.01 | 8.01
2019-02-15 00:30 | 7.5 | 7.5
2019-02-15 01:00 | 7.28 | 7.27
2019-02-15 01:30 | 7.02 | 7.01
2019-02-15 02:00 | 6.73 | 6.73
2019-02-15 02:30 | 6.63 | 6.62
2019-02-15 03:00 | 6.48 | 6.47
2019-02-15 03:30 | 6.43 | 6.42
2019-02-15 04:00 | 6.29 | 6.28
2019-02-15 04:30 | 6.29 | 6.27
2019-02-15 05:00 | 6.38 | 6.36
2019-02-15 05:30 | 6.68 | 6.66
2019-02-15 06:00 | 7.12 | 7.09
2019-02-15 06:30 | 7.44 | 7.41
2019-02-15 07:00 | 7.66 | 7.64
2019-02-15 07:30 | 7.61 | 7.61
2019-02-15 08:00 | 7.43 | 7.43
2019-02-15 08:30 | 6.69 | 6.69
2019-02-15 09:00 | 6.2 | 6.19
2019-02-15 09:30 | 6.54 | 6.53
2019-02-15 10:00 | 6.25 | 6.23
2019-02-15 10:30 | 7.18 | 7.15
2019-02-15 11:00 | 7.02 | 6.99
2019-02-15 11:30 | 7.39 | 7.36
2019-02-15 12:00 | 8.11 | 8.07
2019-02-15 12:30 | 8.09 | 8.03
2019-02-15 13:00 | 9.9 | 9.85
2019-02-15 13:30 | 9.72 | 9.65
2019-02-15 14:00 | 10.69 | 10.61
2019-02-15 14:30 | 11.31 | 11.22
2019-02-15 15:00 | 11.6 | 11.52
2019-02-15 15:30 | 12.27 | 12.18
2019-02-15 16:00 | 13.4 | 13.31
2019-02-15 16:30 | 14.38 | 14.3
2019-02-15 17:00 | 15.36 | 15.28
2019-02-15 17:30 | 15.75 | 15.68
2019-02-15 18:00 | 15.58 | 15.52
2019-02-15 18:30 | 15.27 | 15.23
2019-02-15 19:00 | 15.25 | 15.21
2019-02-15 19:30 | 15.12 | 15.07
2019-02-15 20:00 | 14.56 | 14.52
2019-02-15 20:30 | 13.9 | 13.88
2019-02-15 21:00 | 13.03 | 13.01
2019-02-15 21:30 | 12.07 | 12.06
2019-02-15 22:00 | 11.23 | 11.22
2019-02-15 22:30 | 10.75 | 10.75
2019-02-15 23:00 | 10.38 | 10.38
2019-02-15 23:30 | 9.17 | 9.16
2019-02-16 | 8.22 | 8.21
2019-02-16 00:30 | 7.62 | 7.62
2019-02-16 01:00 | 7.33 | 7.32
2019-02-16 01:30 | 6.87 | 6.86
2019-02-16 02:00 | 6.62 | 6.61
2019-02-16 02:30 | 6.46 | 6.45
2019-02-16 03:00 | 6.37 | 6.35
2019-02-16 03:30 | 6.36 | 6.34
2019-02-16 04:00 | 6.22 | 6.2
2019-02-16 04:30 | 6.04 | 6.01
2019-02-16 05:00 | 6.08 | 6.05
2019-02-16 05:30 | 6.07 | 6.03
2019-02-16 06:00 | 5.93 | 5.87
2019-02-16 06:30 | 5.85 | 5.79
2019-02-16 07:00 | 6.04 | 5.99
2019-02-16 07:30 | 5.87 | 5.82
2019-02-16 08:00 | 5.66 | 5.63
2019-02-16 08:30 | 5.54 | 5.53
2019-02-16 09:00 | 6.46 | 6.44
2019-02-16 09:30 | 7.2 | 7.18
2019-02-16 10:00 | 6.77 | 6.74
2019-02-16 10:30 | 7.62 | 7.6
2019-02-16 11:00 | 8.61 | 8.59
2019-02-16 11:30 | 7.69 | 7.67
2019-02-16 12:00 | 9.16 | 9.14
2019-02-16 12:30 | 8.93 | 8.91
2019-02-16 13:00 | 9.07 | 9.04
2019-02-16 13:30 | 9.33 | 9.3
2019-02-16 14:00 | 9.63 | 9.6
2019-02-16 14:30 | 10.83 | 10.81
2019-02-16 15:00 | 9.92 | 9.89
2019-02-16 15:30 | 10.47 | 10.45
2019-02-16 16:00 | 11.04 | 11.01
2019-02-16 16:30 | 11.82 | 11.8
2019-02-16 17:00 | 12.03 | 12.01
2019-02-16 17:30 | 12.77 | 12.75
2019-02-16 18:00 | 12.93 | 12.91
2019-02-16 18:30 | 12.85 | 12.83
2019-02-16 19:00 | 13.08 | 13.07
2019-02-16 19:30 | 13.05 | 13.04
2019-02-16 20:00 | 12.75 | 12.73
2019-02-16 20:30 | 12.43 | 12.41
2019-02-16 21:00 | 11.69 | 11.68
2019-02-16 21:30 | 10.96 | 10.96
2019-02-16 22:00 | 10.33 | 10.32
2019-02-16 22:30 | 9.92 | 9.92
2019-02-16 23:00 | 9.62 | 9.62
2019-02-16 23:30 | 8.6 | 8.6
2019-02-17 | 7.78 | 7.77
2019-02-17 00:30 | 7.19 | 7.18
2019-02-17 01:00 | 6.8 | 6.79
2019-02-17 01:30 | 6.47 | 6.45
2019-02-17 02:00 | 6.13 | 6.1
2019-02-17 02:30 | 5.93 | 5.9
2019-02-17 03:00 | 5.78 | 5.75
2019-02-17 03:30 | 5.84 | 5.81
2019-02-17 04:00 | 5.71 | 5.68
2019-02-17 04:30 | 5.64 | 5.6
2019-02-17 05:00 | 5.68 | 5.64
2019-02-17 05:30 | 5.54 | 5.47
2019-02-17 06:00 | 5.44 | 5.34
2019-02-17 06:30 | 5.35 | 5.24
2019-02-17 07:00 | 5.16 | 5.06
2019-02-17 07:30 | 5.26 | 5.2
2019-02-17 08:00 | 5.31 | 5.27
2019-02-17 08:30 | 5.38 | 5.36
2019-02-17 09:00 | 5.4 | 5.38
2019-02-17 09:30 | 5.53 | 5.5
2019-02-17 10:00 | 5.84 | 5.81
2019-02-17 10:30 | 6.2 | 6.16
2019-02-17 11:00 | 6.92 | 6.89
2019-02-17 11:30 | 8.5 | 8.47
2019-02-17 12:00 | 8.37 | 8.34
2019-02-17 12:30 | 9.04 | 9
2019-02-17 13:00 | 9.37 | 9.31
2019-02-17 13:30 | 9.94 | 9.87
2019-02-17 14:00 | 10.84 | 10.77
2019-02-17 14:30 | 12.1 | 12.03
2019-02-17 15:00 | 13.24 | 13.17
2019-02-17 15:30 | 13.54 | 13.47
2019-02-17 16:00 | 14.28 | 14.21
2019-02-17 16:30 | 14.98 | 14.91
2019-02-17 17:00 | 15.75 | 15.69
2019-02-17 17:30 | 16.32 | 16.27
2019-02-17 18:00 | 16.19 | 16.15
2019-02-17 18:30 | 15.8 | 15.77
2019-02-17 19:00 | 15.62 | 15.58
2019-02-17 19:30 | 15.46 | 15.43
2019-02-17 20:00 | 14.97 | 14.94
2019-02-17 20:30 | 14.17 | 14.15
2019-02-17 21:00 | 13.13 | 13.12
2019-02-17 21:30 | 12.15 | 12.15
2019-02-17 22:00 | 11.25 | 11.24
2019-02-17 22:30 | 10.5 | 10.49
2019-02-17 23:00 | 9.87 | 9.86
2019-02-17 23:30 | 8.75 | 8.74
2019-02-18 | 7.78 | 7.78
2019-02-18 00:30 | 7.16 | 7.15
2019-02-18 01:00 | 6.78 | 6.77
2019-02-18 01:30 | 6.36 | 6.34
2019-02-18 02:00 | 6.21 | 6.18
2019-02-18 02:30 | 6.01 | 5.99
2019-02-18 03:00 | 5.91 | 5.88
2019-02-18 03:30 | 5.92 | 5.89
2019-02-18 04:00 | 5.86 | 5.83
2019-02-18 04:30 | 5.88 | 5.85
2019-02-18 05:00 | 5.99 | 5.96
2019-02-18 05:30 | 6.19 | 6.15
2019-02-18 06:00 | 6.51 | 6.44
2019-02-18 06:30 | 6.9 | 6.86
2019-02-18 07:00 | 7.25 | 7.23
2019-02-18 07:30 | 7.23 | 7.22
2019-02-18 08:00 | 6.72 | 6.71
2019-02-18 08:30 | 6.22 | 6.22
2019-02-18 09:00 | 5.91 | 5.9
2019-02-18 09:30 | 5.92 | 5.9
2019-02-18 10:00 | 7.47 | 7.45
2019-02-18 10:30 | 7 | 6.98
2019-02-18 11:00 | 8.09 | 8.07
2019-02-18 11:30 | 8.17 | 8.14
2019-02-18 12:00 | 8.38 | 8.35
2019-02-18 12:30 | 8.57 | 8.53
2019-02-18 13:00 | 8.63 | 8.57
2019-02-18 13:30 | 8.91 | 8.84
2019-02-18 14:00 | 10.22 | 10.14
2019-02-18 14:30 | 11.1 | 11.01
2019-02-18 15:00 | 11.79 | 11.7
2019-02-18 15:30 | 12.83 | 12.73
2019-02-18 16:00 | 14.39 | 14.3
2019-02-18 16:30 | 15.58 | 15.5
2019-02-18 17:00 | 16.92 | 16.83
2019-02-18 17:30 | 17.61 | 17.52
2019-02-18 18:00 | 17.62 | 17.55
2019-02-18 18:30 | 17.35 | 17.29
2019-02-18 19:00 | 17.58 | 17.51
2019-02-18 19:30 | 17.09 | 17.03
2019-02-18 20:00 | 16.65 | 16.6
2019-02-18 20:30 | 15.88 | 15.85
2019-02-18 21:00 | 14.62 | 14.6
2019-02-18 21:30 | 13.31 | 13.3
2019-02-18 22:00 | 11.85 | 11.84
2019-02-18 22:30 | 10.88 | 10.88
2019-02-18 23:00 | 10.05 | 10.05
2019-02-18 23:30 | 8.9 | 8.89
2019-02-19 | 7.85 | 7.84
2019-02-19 00:30 | 7.28 | 7.27
2019-02-19 01:00 | 6.97 | 6.96
2019-02-19 01:30 | 6.65 | 6.64
2019-02-19 02:00 | 6.35 | 6.33
2019-02-19 02:30 | 6.15 | 6.13
2019-02-19 03:00 | 5.95 | 5.93
2019-02-19 03:30 | 5.95 | 5.93
2019-02-19 04:00 | 5.87 | 5.84
2019-02-19 04:30 | 5.93 | 5.9
2019-02-19 05:00 | 6.15 | 6.12
2019-02-19 05:30 | 6.28 | 6.25
2019-02-19 06:00 | 6.33 | 6.26
2019-02-19 06:30 | 6.55 | 6.5
2019-02-19 07:00 | 6.56 | 6.52
2019-02-19 07:30 | 6.57 | 6.55
2019-02-19 08:00 | 6.08 | 6.07
2019-02-19 08:30 | 5.52 | 5.51
2019-02-19 09:00 | 5.25 | 5.24
2019-02-19 09:30 | 5.37 | 5.35
2019-02-19 10:00 | 5.58 | 5.55
2019-02-19 10:30 | 5.75 | 5.72
2019-02-19 11:00 | 6.11 | 6.07
2019-02-19 11:30 | 6.81 | 6.76
2019-02-19 12:00 | 7.61 | 7.55
2019-02-19 12:30 | 8.61 | 8.54
2019-02-19 13:00 | 9.83 | 9.73
2019-02-19 13:30 | 11.16 | 11.06
2019-02-19 14:00 | 12.53 | 12.42
2019-02-19 14:30 | 13.74 | 13.62
2019-02-19 15:00 | 15.12 | 14.96
2019-02-19 15:30 | 16.65 | 16.49
2019-02-19 16:00 | 18.62 | 18.45
2019-02-19 16:30 | 19.72 | 19.56
2019-02-19 17:00 | 20.73 | 20.57
2019-02-19 17:30 | 21.34 | 21.17
2019-02-19 18:00 | 21.17 | 21.02
2019-02-19 18:30 | 20.71 | 20.59
2019-02-19 19:00 | 20.52 | 20.37
2019-02-19 19:30 | 20.23 | 20.09
2019-02-19 20:00 | 19.48 | 19.36
2019-02-19 20:30 | 18.58 | 18.48
2019-02-19 21:00 | 16.85 | 16.78
2019-02-19 21:30 | 15.33 | 15.28
2019-02-19 22:00 | 13.93 | 13.91
2019-02-19 22:30 | 12.31 | 12.3
2019-02-19 23:00 | 11.45 | 11.44
2019-02-19 23:30 | 10.06 | 10.05
2019-02-20 | 8.96 | 8.96
2019-02-20 00:30 | 8.28 | 8.28
2019-02-20 01:00 | 8 | 7.99
2019-02-20 01:30 | 7.63 | 7.62
2019-02-20 02:00 | 7.26 | 7.25
2019-02-20 02:30 | 7.15 | 7.15
2019-02-20 03:00 | 6.93 | 6.93
2019-02-20 03:30 | 6.95 | 6.94
2019-02-20 04:00 | 6.85 | 6.84
2019-02-20 04:30 | 6.96 | 6.95
2019-02-20 05:00 | 7.09 | 7.08
2019-02-20 05:30 | 7.29 | 7.28
2019-02-20 06:00 | 7.78 | 7.77
2019-02-20 06:30 | 9.28 | 9.27
2019-02-20 07:00 | 9.56 | 9.55
2019-02-20 07:30 | 9.54 | 9.54
2019-02-20 08:00 | 9.44 | 9.44
2019-02-20 08:30 | 8.89 | 8.88
2019-02-20 09:00 | 8.8 | 8.79
2019-02-20 09:30 | 8.42 | 8.39
2019-02-20 10:00 | 8.19 | 8.14
2019-02-20 10:30 | 8.73 | 8.66
2019-02-20 11:00 | 9.37 | 9.28
2019-02-20 11:30 | 10.09 | 9.98
2019-02-20 12:00 | 11.02 | 10.9
2019-02-20 12:30 | 11.97 | 11.85
2019-02-20 13:00 | 12.74 | 12.6
2019-02-20 13:30 | 13.56 | 13.4
2019-02-20 14:00 | 15.05 | 14.89
2019-02-20 14:30 | 15.51 | 15.31
2019-02-20 15:00 | 16.35 | 16.16
2019-02-20 15:30 | 17.62 | 17.43
2019-02-20 16:00 | 19.32 | 19.12
2019-02-20 16:30 | 20.41 | 20.23
2019-02-20 17:00 | 21.2 | 21.02
2019-02-20 17:30 | 21.56 | 21.39
2019-02-20 18:00 | 21.33 | 21.17
2019-02-20 18:30 | 20.97 | 20.84
2019-02-20 19:00 | 20.87 | 20.71
2019-02-20 19:30 | 20.75 | 20.59
2019-02-20 20:00 | 20.17 | 20.03
2019-02-20 20:30 | 19.28 | 19.16
2019-02-20 21:00 | 17.79 | 17.7
2019-02-20 21:30 | 16.33 | 16.27
2019-02-20 22:00 | 14.91 | 14.87
2019-02-20 22:30 | 13.51 | 13.49
2019-02-20 23:00 | 12.45 | 12.43
2019-02-20 23:30 | 11.19 | 11.18
2019-02-21 | 10.03 | 10.02
2019-02-21 00:30 | 9.36 | 9.36
2019-02-21 01:00 | 9.01 | 9
2019-02-21 01:30 | 8.53 | 8.53
2019-02-21 02:00 | 8.22 | 8.21
2019-02-21 02:30 | 8.01 | 8
2019-02-21 03:00 | 7.78 | 7.78
2019-02-21 03:30 | 7.59 | 7.58
2019-02-21 04:00 | 7.36 | 7.35
2019-02-21 04:30 | 7.28 | 7.28
2019-02-21 05:00 | 7.39 | 7.38
2019-02-21 05:30 | 7.47 | 7.46
2019-02-21 06:00 | 7.59 | 7.57
2019-02-21 06:30 | 7.82 | 7.81
2019-02-21 07:00 | 8.19 | 8.18
2019-02-21 07:30 | 8.75 | 8.75
2019-02-21 08:00 | 9.52 | 9.52
2019-02-21 08:30 | 9.9 | 9.9
2019-02-21 09:00 | 10.64 | 10.64
2019-02-21 09:30 | 11.49 | 11.48
2019-02-21 10:00 | 10.34 | 10.32
2019-02-21 10:30 | 10.83 | 10.8
2019-02-21 11:00 | 10.88 | 10.83
2019-02-21 11:30 | 12.03 | 11.97
2019-02-21 12:00 | 12.66 | 12.58
2019-02-21 12:30 | 13.82 | 13.74
2019-02-21 13:00 | 12.92 | 12.81
2019-02-21 13:30 | 15.46 | 15.36
2019-02-21 14:00 | 14.22 | 14.09
2019-02-21 14:30 | 15.36 | 15.22
2019-02-21 15:00 | 16.04 | 15.9
2019-02-21 15:30 | 16.42 | 16.27
2019-02-21 16:00 | 17.85 | 17.69
2019-02-21 16:30 | 19.21 | 19.05
2019-02-21 17:00 | 20.43 | 20.27
2019-02-21 17:30 | 21.24 | 21.08
2019-02-21 18:00 | 21.43 | 21.29
2019-02-21 18:30 | 21.27 | 21.13
2019-02-21 19:00 | 21.28 | 21.11
2019-02-21 19:30 | 20.88 | 20.72
2019-02-21 20:00 | 20.01 | 19.86
2019-02-21 20:30 | 18.52 | 18.41
2019-02-21 21:00 | 17.28 | 17.2
2019-02-21 21:30 | 16.02 | 15.96
2019-02-21 22:00 | 14.58 | 14.54
2019-02-21 22:30 | 13.15 | 13.13
2019-02-21 23:00 | 12.21 | 12.19
2019-02-21 23:30 | 10.76 | 10.75
2019-02-22 | 9.56 | 9.55
2019-02-22 00:30 | 8.91 | 8.91
2019-02-22 01:00 | 8.56 | 8.55
2019-02-22 01:30 | 8.27 | 8.26
2019-02-22 02:00 | 7.84 | 7.83
2019-02-22 02:30 | 7.66 | 7.65
2019-02-22 03:00 | 7.49 | 7.49
2019-02-22 03:30 | 7.46 | 7.45
2019-02-22 04:00 | 7.26 | 7.25
2019-02-22 04:30 | 7.28 | 7.27
2019-02-22 05:00 | 7.32 | 7.32
2019-02-22 05:30 | 7.57 | 7.56
2019-02-22 06:00 | 7.95 | 7.94
2019-02-22 06:30 | 8.46 | 8.45
2019-02-22 07:00 | 8.52 | 8.52
2019-02-22 07:30 | 8.33 | 8.33
2019-02-22 08:00 | 8.73 | 8.72
2019-02-22 08:30 | 8.46 | 8.45
2019-02-22 09:00 | 7.24 | 7.23
2019-02-22 09:30 | 7.29 | 7.28
2019-02-22 10:00 | 7.84 | 7.83
2019-02-22 10:30 | 6.8 | 6.77
2019-02-22 11:00 | 7.52 | 7.48
2019-02-22 11:30 | 6.55 | 6.51
2019-02-22 12:00 | 7.47 | 7.44
2019-02-22 12:30 | 10.16 | 10.14
2019-02-22 13:00 | 9.61 | 9.59
2019-02-22 13:30 | 8.11 | 8.08
2019-02-22 14:00 | 8.27 | 8.25
2019-02-22 14:30 | 8.4 | 8.37
2019-02-22 15:00 | 8.09 | 8.05
2019-02-22 15:30 | 9.48 | 9.45
2019-02-22 16:00 | 11.22 | 11.19
2019-02-22 16:30 | 11.31 | 11.29
2019-02-22 17:00 | 12.02 | 12
2019-02-22 17:30 | 12.1 | 12.07
2019-02-22 18:00 | 12.9 | 12.88
2019-02-22 18:30 | 13.35 | 13.34
2019-02-22 19:00 | 13.77 | 13.75
2019-02-22 19:30 | 13.78 | 13.75
2019-02-22 20:00 | 13.31 | 13.29
2019-02-22 20:30 | 12.78 | 12.78
2019-02-22 21:00 | 12.04 | 12.03
2019-02-22 21:30 | 11.37 | 11.36
2019-02-22 22:00 | 10.55 | 10.54
2019-02-22 22:30 | 10.08 | 10.08
2019-02-22 23:00 | 9.83 | 9.83
2019-02-22 23:30 | 8.7 | 8.7
2019-02-23 | 7.94 | 7.94
2019-02-23 00:30 | 7.25 | 7.24
2019-02-23 01:00 | 6.84 | 6.83
2019-02-23 01:30 | 6.55 | 6.53
2019-02-23 02:00 | 6.4 | 6.38
2019-02-23 02:30 | 6.21 | 6.19
2019-02-23 03:00 | 6.07 | 6.05
2019-02-23 03:30 | 6.04 | 6.02
2019-02-23 04:00 | 5.94 | 5.91
2019-02-23 04:30 | 5.87 | 5.85
2019-02-23 05:00 | 5.93 | 5.9
2019-02-23 05:30 | 5.92 | 5.89
2019-02-23 06:00 | 5.84 | 5.77
2019-02-23 06:30 | 5.8 | 5.73
2019-02-23 07:00 | 5.92 | 5.86
2019-02-23 07:30 | 6.82 | 6.78
2019-02-23 08:00 | 5.74 | 5.71
2019-02-23 08:30 | 5.21 | 5.19
2019-02-23 09:00 | 5.24 | 5.21
2019-02-23 09:30 | 5.77 | 5.74
2019-02-23 10:00 | 5.34 | 5.31
2019-02-23 10:30 | 5.5 | 5.46
2019-02-23 11:00 | 5.43 | 5.39
2019-02-23 11:30 | 6.63 | 6.59
2019-02-23 12:00 | 6.55 | 6.51
2019-02-23 12:30 | 7.29 | 7.25
2019-02-23 13:00 | 7.81 | 7.77
2019-02-23 13:30 | 8.6 | 8.57
2019-02-23 14:00 | 9.2 | 9.17
2019-02-23 14:30 | 9.15 | 9.12
2019-02-23 15:00 | 9.35 | 9.32
2019-02-23 15:30 | 9.62 | 9.59
2019-02-23 16:00 | 10.97 | 10.94
2019-02-23 16:30 | 12.05 | 12.02
2019-02-23 17:00 | 12.11 | 12.08
2019-02-23 17:30 | 12.79 | 12.77
2019-02-23 18:00 | 12.93 | 12.91
2019-02-23 18:30 | 13.16 | 13.15
2019-02-23 19:00 | 13.5 | 13.48
2019-02-23 19:30 | 13.29 | 13.27
2019-02-23 20:00 | 12.83 | 12.82
2019-02-23 20:30 | 12.42 | 12.41
2019-02-23 21:00 | 11.76 | 11.75
2019-02-23 21:30 | 10.97 | 10.96
2019-02-23 22:00 | 10.27 | 10.26
2019-02-23 22:30 | 9.85 | 9.84
2019-02-23 23:00 | 9.73 | 9.72
2019-02-23 23:30 | 8.73 | 8.72
2019-02-24 | 7.84 | 7.84
2019-02-24 00:30 | 7.23 | 7.21
2019-02-24 01:00 | 6.97 | 6.96
2019-02-24 01:30 | 6.56 | 6.54
2019-02-24 02:00 | 6.27 | 6.25
2019-02-24 02:30 | 6.08 | 6.05
2019-02-24 03:00 | 5.97 | 5.94
2019-02-24 03:30 | 5.9 | 5.87
2019-02-24 04:00 | 5.72 | 5.68
2019-02-24 04:30 | 5.59 | 5.55
2019-02-24 05:00 | 5.58 | 5.54
2019-02-24 05:30 | 5.56 | 5.52
2019-02-24 06:00 | 5.53 | 5.44
2019-02-24 06:30 | 5.57 | 5.48
2019-02-24 07:00 | 5.44 | 5.35
2019-02-24 07:30 | 5.38 | 5.32
2019-02-24 08:00 | 5.44 | 5.4
2019-02-24 08:30 | 5.53 | 5.51
2019-02-24 09:00 | 6.8 | 6.79
2019-02-24 09:30 | 8.09 | 8.07
2019-02-24 10:00 | 8.18 | 8.16
2019-02-24 10:30 | 8.5 | 8.48
2019-02-24 11:00 | 8.52 | 8.51
2019-02-24 11:30 | 7.36 | 7.34
2019-02-24 12:00 | 5.89 | 5.86
2019-02-24 12:30 | 5.86 | 5.83
2019-02-24 13:00 | 7.43 | 7.4
2019-02-24 13:30 | 8.12 | 8.09
2019-02-24 14:00 | 8.06 | 8.03
2019-02-24 14:30 | 9.07 | 9.04
2019-02-24 15:00 | 10.61 | 10.58
2019-02-24 15:30 | 8.99 | 8.97
2019-02-24 16:00 | 10.56 | 10.54
2019-02-24 16:30 | 10.81 | 10.79
2019-02-24 17:00 | 12.12 | 12.1
2019-02-24 17:30 | 12.4 | 12.39
2019-02-24 18:00 | 13.14 | 13.13
2019-02-24 18:30 | 13.38 | 13.37
2019-02-24 19:00 | 13.76 | 13.75
2019-02-24 19:30 | 13.42 | 13.42
2019-02-24 20:00 | 12.96 | 12.96
2019-02-24 20:30 | 12.47 | 12.46
2019-02-24 21:00 | 11.62 | 11.61
2019-02-24 21:30 | 10.8 | 10.79
2019-02-24 22:00 | 10.07 | 10.06
2019-02-24 22:30 | 9.52 | 9.51
2019-02-24 23:00 | 9.2 | 9.2
2019-02-24 23:30 | 8.18 | 8.17
2019-02-25 | 7.34 | 7.33
2019-02-25 00:30 | 6.82 | 6.81
2019-02-25 01:00 | 6.52 | 6.5
2019-02-25 01:30 | 6.11 | 6.08
2019-02-25 02:00 | 5.91 | 5.88
2019-02-25 02:30 | 5.7 | 5.66
2019-02-25 03:00 | 5.63 | 5.59
2019-02-25 03:30 | 5.56 | 5.52
2019-02-25 04:00 | 5.53 | 5.48
2019-02-25 04:30 | 5.65 | 5.6
2019-02-25 05:00 | 5.91 | 5.87
2019-02-25 05:30 | 6.15 | 6.11
2019-02-25 06:00 | 6.27 | 6.2
2019-02-25 06:30 | 6.55 | 6.49
2019-02-25 07:00 | 6.9 | 6.87
2019-02-25 07:30 | 7.36 | 7.34
2019-02-25 08:00 | 6.42 | 6.41
2019-02-25 08:30 | 5.67 | 5.67
2019-02-25 09:00 | 5.72 | 5.72
2019-02-25 09:30 | 6.16 | 6.15
2019-02-25 10:00 | 5.43 | 5.42
2019-02-25 10:30 | 6.47 | 6.46
2019-02-25 11:00 | 6.17 | 6.16
2019-02-25 11:30 | 5.18 | 5.17
2019-02-25 12:00 | 6.91 | 6.9
2019-02-25 12:30 | 5.39 | 5.38
2019-02-25 13:00 | 7.05 | 7.04
2019-02-25 13:30 | 7.23 | 7.23
2019-02-25 14:00 | 5.97 | 5.96
2019-02-25 14:30 | 7.04 | 7.03
2019-02-25 15:00 | 7.81 | 7.81
2019-02-25 15:30 | 7.74 | 7.73
2019-02-25 16:00 | 8.22 | 8.21
2019-02-25 16:30 | 9.4 | 9.39
2019-02-25 17:00 | 10.14 | 10.13
2019-02-25 17:30 | 11.5 | 11.5
2019-02-25 18:00 | 12.57 | 12.57
2019-02-25 18:30 | 13.03 | 13.03
2019-02-25 19:00 | 13.87 | 13.86
2019-02-25 19:30 | 13.7 | 13.69
2019-02-25 20:00 | 13.53 | 13.53
2019-02-25 20:30 | 13.09 | 13.09
2019-02-25 21:00 | 12.02 | 12.02
2019-02-25 21:30 | 10.99 | 10.99
2019-02-25 22:00 | 10 | 10
2019-02-25 22:30 | 9.23 | 9.23
2019-02-25 23:00 | 8.71 | 8.7
2019-02-25 23:30 | 7.74 | 7.72
2019-02-26 | 7.01 | 7
2019-02-26 00:30 | 6.61 | 6.59
2019-02-26 01:00 | 6.1 | 6.07
2019-02-26 01:30 | 5.78 | 5.74
2019-02-26 02:00 | 5.64 | 5.6
2019-02-26 02:30 | 5.59 | 5.55
2019-02-26 03:00 | 5.54 | 5.49
2019-02-26 03:30 | 5.41 | 5.36
2019-02-26 04:00 | 5.39 | 5.34
2019-02-26 04:30 | 5.55 | 5.5
2019-02-26 05:00 | 5.75 | 5.7
2019-02-26 05:30 | 6.05 | 6.01
2019-02-26 06:00 | 6.25 | 6.17
2019-02-26 06:30 | 6.57 | 6.5
2019-02-26 07:00 | 6.79 | 6.73
2019-02-26 07:30 | 6.89 | 6.85
2019-02-26 08:00 | 6.54 | 6.51
2019-02-26 08:30 | 5.8 | 5.77
2019-02-26 09:00 | 4.78 | 4.76
2019-02-26 09:30 | 4.43 | 4.41
2019-02-26 10:00 | 4.49 | 4.47
2019-02-26 10:30 | 5.46 | 5.45
2019-02-26 11:00 | 5.28 | 5.27
2019-02-26 11:30 | 5.93 | 5.91
2019-02-26 12:00 | 5.76 | 5.75
2019-02-26 12:30 | 7.23 | 7.23
2019-02-26 13:00 | 6.29 | 6.28
2019-02-26 13:30 | 5.91 | 5.9
2019-02-26 14:00 | 7.25 | 7.24
2019-02-26 14:30 | 7.74 | 7.73
2019-02-26 15:00 | 6.79 | 6.78
2019-02-26 15:30 | 6.78 | 6.77
2019-02-26 16:00 | 8.24 | 8.23
2019-02-26 16:30 | 8.74 | 8.74
2019-02-26 17:00 | 10.49 | 10.49
2019-02-26 17:30 | 11.67 | 11.67
2019-02-26 18:00 | 11.84 | 11.84
2019-02-26 18:30 | 13.03 | 13.03
2019-02-26 19:00 | 13.67 | 13.66
2019-02-26 19:30 | 13.61 | 13.6
2019-02-26 20:00 | 13.48 | 13.47
2019-02-26 20:30 | 12.99 | 12.98
2019-02-26 21:00 | 12.17 | 12.17
2019-02-26 21:30 | 12.15 | 12.15
2019-02-26 22:00 | 11.2 | 11.2
2019-02-26 22:30 | 10.3 | 10.29
2019-02-26 23:00 | 9.71 | 9.7
2019-02-26 23:30 | 8.63 | 8.6
2019-02-27 | 7.06 | 7.03
2019-02-27 00:30 | 6.22 | 6.19
2019-02-27 01:00 | 5.95 | 5.91
2019-02-27 01:30 | 5.68 | 5.63
2019-02-27 02:00 | 5.45 | 5.4
2019-02-27 02:30 | 5.35 | 5.3
2019-02-27 03:00 | 5.27 | 5.22
2019-02-27 03:30 | 5.26 | 5.2
2019-02-27 04:00 | 5.26 | 5.21
2019-02-27 04:30 | 5.4 | 5.34
2019-02-27 05:00 | 5.66 | 5.61
2019-02-27 05:30 | 5.9 | 5.86
2019-02-27 06:00 | 6.2 | 6.12
2019-02-27 06:30 | 7.05 | 6.98
2019-02-27 07:00 | 6.79 | 6.75
2019-02-27 07:30 | 6.76 | 6.73
2019-02-27 08:00 | 6.44 | 6.42
2019-02-27 08:30 | 5.48 | 5.47
2019-02-27 09:00 | 5.4 | 5.4
2019-02-27 09:30 | 5.72 | 5.72
2019-02-27 10:00 | 5.2 | 5.2
2019-02-27 10:30 | 5.46 | 5.46
2019-02-27 11:00 | 6.42 | 6.41
2019-02-27 11:30 | 3.94 | 3.93
2019-02-27 12:00 | 6.63 | 6.62
2019-02-27 12:30 | 7.58 | 7.57
2019-02-27 13:00 | 6.17 | 6.17
2019-02-27 13:30 | 5.89 | 5.88
2019-02-27 14:00 | 6.94 | 6.93
2019-02-27 14:30 | 6.98 | 6.98
2019-02-27 15:00 | 6.51 | 6.5
2019-02-27 15:30 | 7.14 | 7.14
2019-02-27 16:00 | 8.57 | 8.56
2019-02-27 16:30 | 9.12 | 9.11
2019-02-27 17:00 | 10.04 | 10.03
2019-02-27 17:30 | 11.21 | 11.2
2019-02-27 18:00 | 12.16 | 12.15
2019-02-27 18:30 | 12.77 | 12.76
2019-02-27 19:00 | 13.64 | 13.62
2019-02-27 19:30 | 13.49 | 13.48
2019-02-27 20:00 | 13.46 | 13.45
2019-02-27 20:30 | 13.26 | 13.26
2019-02-27 21:00 | 12.22 | 12.21
2019-02-27 21:30 | 11.44 | 11.43
2019-02-27 22:00 | 10.44 | 10.43
2019-02-27 22:30 | 9.51 | 9.51
2019-02-27 23:00 | 8.9 | 8.89
2019-02-27 23:30 | 7.88 | 7.86
2019-02-28 | 6.99 | 6.97
2019-02-28 00:30 | 6.43 | 6.41
2019-02-28 01:00 | 6.2 | 6.17
2019-02-28 01:30 | 5.99 | 5.95
2019-02-28 02:00 | 5.61 | 5.57
2019-02-28 02:30 | 5.55 | 5.51
2019-02-28 03:00 | 5.34 | 5.29
2019-02-28 03:30 | 5.38 | 5.33
2019-02-28 04:00 | 5.45 | 5.4
2019-02-28 04:30 | 5.53 | 5.48
2019-02-28 05:00 | 5.79 | 5.75
2019-02-28 05:30 | 6.21 | 6.18
2019-02-28 06:00 | 6.75 | 6.7
2019-02-28 06:30 | 7.5 | 7.46
2019-02-28 07:00 | 7.44 | 7.4
2019-02-28 07:30 | 7.04 | 7
2019-02-28 08:00 | 7 | 6.98
2019-02-28 08:30 | 7.07 | 7.06
2019-02-28 09:00 | 7.52 | 7.51
2019-02-28 09:30 | 6.9 | 6.89
2019-02-28 10:00 | 5.15 | 5.13
2019-02-28 10:30 | 5.57 | 5.56
2019-02-28 11:00 | 8.45 | 8.44
2019-02-28 11:30 | 5.98 | 5.97
2019-02-28 12:00 | 5.29 | 5.28
2019-02-28 12:30 | 6.06 | 6.06
2019-02-28 13:00 | 5.64 | 5.63
2019-02-28 13:30 | 6.48 | 6.48
2019-02-28 14:00 | 5.99 | 5.98
2019-02-28 14:30 | 6.55 | 6.54
2019-02-28 15:00 | 7.51 | 7.51
2019-02-28 15:30 | 6.93 | 6.92
2019-02-28 16:00 | 7.23 | 7.23
2019-02-28 16:30 | 8.99 | 8.98
2019-02-28 17:00 | 9.63 | 9.63
2019-02-28 17:30 | 10.1 | 10.1
2019-02-28 18:00 | 11.01 | 11.01
2019-02-28 18:30 | 11.87 | 11.87
2019-02-28 19:00 | 12.93 | 12.92
2019-02-28 19:30 | 12.81 | 12.8
2019-02-28 20:00 | 12.85 | 12.85
2019-02-28 20:30 | 12.51 | 12.5
2019-02-28 21:00 | 11.81 | 11.81
2019-02-28 21:30 | 10.97 | 10.97
2019-02-28 22:00 | 10.35 | 10.35
2019-02-28 22:30 | 9.73 | 9.73
2019-02-28 23:00 | 9.22 | 9.21
2019-02-28 23:30 | 8.06 | 8.05
2019-03-01 | 7.1 | 7.08
2019-03-01 00:30 | 6.47 | 6.44
2019-03-01 01:00 | 6.22 | 6.2
2019-03-01 01:30 | 6.01 | 5.98
2019-03-01 02:00 | 5.76 | 5.73
2019-03-01 02:30 | 5.65 | 5.61
2019-03-01 03:00 | 5.47 | 5.42
2019-03-01 03:30 | 5.63 | 5.58
2019-03-01 04:00 | 5.63 | 5.59
2019-03-01 04:30 | 5.63 | 5.58
2019-03-01 05:00 | 5.9 | 5.86
2019-03-01 05:30 | 6.61 | 6.59
2019-03-01 06:00 | 6.99 | 6.96
2019-03-01 06:30 | 7.43 | 7.4
2019-03-01 07:00 | 7.6 | 7.56
2019-03-01 07:30 | 7.33 | 7.3
2019-03-01 08:00 | 6.48 | 6.46
2019-03-01 08:30 | 6.22 | 6.21
2019-03-01 09:00 | 5.89 | 5.88
2019-03-01 09:30 | 6.01 | 6.01
2019-03-01 10:00 | 5.71 | 5.7
2019-03-01 10:30 | 6.05 | 6.04
2019-03-01 11:00 | 6.46 | 6.46
2019-03-01 11:30 | 6.23 | 6.22
2019-03-01 12:00 | 6.98 | 6.98
2019-03-01 12:30 | 6.36 | 6.35
2019-03-01 13:00 | 8.13 | 8.12
2019-03-01 13:30 | 6.85 | 6.85
2019-03-01 14:00 | 6.11 | 6.1
2019-03-01 14:30 | 7.49 | 7.48
2019-03-01 15:00 | 8.71 | 8.7
2019-03-01 15:30 | 7.93 | 7.92
2019-03-01 16:00 | 7.99 | 7.98
2019-03-01 16:30 | 9.25 | 9.25
2019-03-01 17:00 | 10.16 | 10.15
2019-03-01 17:30 | 10.92 | 10.91
2019-03-01 18:00 | 11.62 | 11.61
2019-03-01 18:30 | 11.75 | 11.74
2019-03-01 19:00 | 12.2 | 12.19
2019-03-01 19:30 | 12.05 | 12.04
2019-03-01 20:00 | 12.04 | 12.03
2019-03-01 20:30 | 11.75 | 11.74
2019-03-01 21:00 | 11.11 | 11.11
2019-03-01 21:30 | 10.42 | 10.42
2019-03-01 22:00 | 9.66 | 9.66
2019-03-01 22:30 | 9.41 | 9.4
2019-03-01 23:00 | 9.15 | 9.15
2019-03-01 23:30 | 8.25 | 8.24
2019-03-02 | 7.46 | 7.44
2019-03-02 00:30 | 6.75 | 6.73
2019-03-02 01:00 | 6.45 | 6.42
2019-03-02 01:30 | 6.07 | 6.03
2019-03-02 02:00 | 5.8 | 5.76
2019-03-02 02:30 | 5.7 | 5.65
2019-03-02 03:00 | 5.52 | 5.47
2019-03-02 03:30 | 5.39 | 5.33
2019-03-02 04:00 | 5.38 | 5.33
2019-03-02 04:30 | 5.57 | 5.53
2019-03-02 05:00 | 5.98 | 5.95
2019-03-02 05:30 | 6.13 | 6.1
2019-03-02 06:00 | 6.21 | 6.16
2019-03-02 06:30 | 6.3 | 6.23
2019-03-02 07:00 | 6.57 | 6.5
2019-03-02 07:30 | 6.79 | 6.74
2019-03-02 08:00 | 7.17 | 7.13
2019-03-02 08:30 | 8.19 | 8.16
2019-03-02 09:00 | 8.6 | 8.59
2019-03-02 09:30 | 7.76 | 7.75
2019-03-02 10:00 | 6.36 | 6.35
2019-03-02 10:30 | 5.44 | 5.43
2019-03-02 11:00 | 5.33 | 5.31
2019-03-02 11:30 | 6 | 5.99
2019-03-02 12:00 | 6.79 | 6.77
2019-03-02 12:30 | 7 | 6.98
2019-03-02 13:00 | 6.88 | 6.85
2019-03-02 13:30 | 6.52 | 6.49
2019-03-02 14:00 | 6.03 | 6
2019-03-02 14:30 | 7.39 | 7.36
2019-03-02 15:00 | 6.62 | 6.59
2019-03-02 15:30 | 8.79 | 8.78
2019-03-02 16:00 | 8.31 | 8.29
2019-03-02 16:30 | 10.04 | 10.02
2019-03-02 17:00 | 9.77 | 9.76
2019-03-02 17:30 | 10.03 | 10.02
2019-03-02 18:00 | 10.68 | 10.67
2019-03-02 18:30 | 11.02 | 11.01
2019-03-02 19:00 | 11.77 | 11.76
2019-03-02 19:30 | 11.54 | 11.53
2019-03-02 20:00 | 11.21 | 11.2
2019-03-02 20:30 | 10.89 | 10.88
2019-03-02 21:00 | 10.4 | 10.39
2019-03-02 21:30 | 9.79 | 9.79
2019-03-02 22:00 | 9.2 | 9.19
2019-03-02 22:30 | 9 | 8.98
2019-03-02 23:00 | 8.78 | 8.76
2019-03-02 23:30 | 7.99 | 7.96
2019-03-03 | 7.21 | 7.18
2019-03-03 00:30 | 6.48 | 6.44
2019-03-03 01:00 | 6.44 | 6.4
2019-03-03 01:30 | 5.96 | 5.92
2019-03-03 02:00 | 5.88 | 5.81
2019-03-03 02:30 | 6.06 | 5.98
2019-03-03 03:00 | 5.89 | 5.82
2019-03-03 03:30 | 5.82 | 5.74
2019-03-03 04:00 | 6.42 | 6.37
2019-03-03 04:30 | 5.63 | 5.58
2019-03-03 05:00 | 5.35 | 5.29
2019-03-03 05:30 | 5.34 | 5.28
2019-03-03 06:00 | 5.21 | 5.1
2019-03-03 06:30 | 5.32 | 5.19
2019-03-03 07:00 | 5.37 | 5.26
2019-03-03 07:30 | 5.57 | 5.48
2019-03-03 08:00 | 5.29 | 5.21
2019-03-03 08:30 | 6.13 | 6.09
2019-03-03 09:00 | 6.57 | 6.54
2019-03-03 09:30 | 5.37 | 5.35
2019-03-03 10:00 | 7.55 | 7.54
2019-03-03 10:30 | 5.29 | 5.26
2019-03-03 11:00 | 6.09 | 6.06
2019-03-03 11:30 | 9.09 | 9.08
2019-03-03 12:00 | 7.83 | 7.81
2019-03-03 12:30 | 8.21 | 8.19
2019-03-03 13:00 | 6.39 | 6.37
2019-03-03 13:30 | 6.58 | 6.55
2019-03-03 14:00 | 7.68 | 7.65
2019-03-03 14:30 | 6.9 | 6.87
2019-03-03 15:00 | 7.79 | 7.76
2019-03-03 15:30 | 8.32 | 8.3
2019-03-03 16:00 | 8.99 | 8.97
2019-03-03 16:30 | 10.5 | 10.49
2019-03-03 17:00 | 10.97 | 10.95
2019-03-03 17:30 | 11.93 | 11.92
2019-03-03 18:00 | 12.43 | 12.42
2019-03-03 18:30 | 12.64 | 12.64
2019-03-03 19:00 | 13.25 | 13.24
2019-03-03 19:30 | 13.11 | 13.11
2019-03-03 20:00 | 12.57 | 12.57
2019-03-03 20:30 | 12.17 | 12.16
2019-03-03 21:00 | 11.41 | 11.41
2019-03-03 21:30 | 10.71 | 10.71
2019-03-03 22:00 | 9.86 | 9.86
2019-03-03 22:30 | 9.31 | 9.3
2019-03-03 23:00 | 8.96 | 8.95
2019-03-03 23:30 | 7.94 | 7.92
2019-03-04 | 7.17 | 7.15
2019-03-04 00:30 | 6.56 | 6.53
2019-03-04 01:00 | 6.21 | 6.18
2019-03-04 01:30 | 5.91 | 5.86
2019-03-04 02:00 | 5.73 | 5.69
2019-03-04 02:30 | 5.51 | 5.46
2019-03-04 03:00 | 5.44 | 5.38
2019-03-04 03:30 | 5.47 | 5.42
2019-03-04 04:00 | 5.41 | 5.35
2019-03-04 04:30 | 5.54 | 5.49
2019-03-04 05:00 | 5.71 | 5.66
2019-03-04 05:30 | 6.1 | 6.06
2019-03-04 06:00 | 6.83 | 6.78
2019-03-04 06:30 | 7.03 | 6.97
2019-03-04 07:00 | 7 | 6.96
2019-03-04 07:30 | 7.16 | 7.14
2019-03-04 08:00 | 6.58 | 6.57
2019-03-04 08:30 | 5.73 | 5.73
2019-03-04 09:00 | 5.37 | 5.36
2019-03-04 09:30 | 6.24 | 6.23
2019-03-04 10:00 | 6.76 | 6.75
2019-03-04 10:30 | 6.29 | 6.29
2019-03-04 11:00 | 7.15 | 7.14
2019-03-04 11:30 | 7.88 | 7.88
2019-03-04 12:00 | 7.65 | 7.65
2019-03-04 12:30 | 7.35 | 7.34
2019-03-04 13:00 | 7.89 | 7.89
2019-03-04 13:30 | 7.94 | 7.93
2019-03-04 14:00 | 6.62 | 6.6
2019-03-04 14:30 | 6.32 | 6.3
2019-03-04 15:00 | 6.81 | 6.79
2019-03-04 15:30 | 8.16 | 8.14
2019-03-04 16:00 | 9.31 | 9.29
2019-03-04 16:30 | 10.36 | 10.34
2019-03-04 17:00 | 11.64 | 11.63
2019-03-04 17:30 | 12.8 | 12.79
2019-03-04 18:00 | 13.27 | 13.27
2019-03-04 18:30 | 13.83 | 13.82
2019-03-04 19:00 | 14.68 | 14.66
2019-03-04 19:30 | 14.32 | 14.31
2019-03-04 20:00 | 14.05 | 14.04
2019-03-04 20:30 | 13.51 | 13.5
2019-03-04 21:00 | 12.64 | 12.63
2019-03-04 21:30 | 11.6 | 11.6
2019-03-04 22:00 | 10.53 | 10.52
2019-03-04 22:30 | 9.62 | 9.62
2019-03-04 23:00 | 9.13 | 9.12
2019-03-04 23:30 | 8.02 | 8.01
2019-03-05 | 7.18 | 7.16
2019-03-05 00:30 | 6.57 | 6.55
2019-03-05 01:00 | 6.33 | 6.3
2019-03-05 01:30 | 6.02 | 5.99
2019-03-05 02:00 | 5.88 | 5.85
2019-03-05 02:30 | 5.7 | 5.66
2019-03-05 03:00 | 5.57 | 5.52
2019-03-05 03:30 | 5.57 | 5.52
2019-03-05 04:00 | 5.55 | 5.51
2019-03-05 04:30 | 5.66 | 5.62
2019-03-05 05:00 | 5.88 | 5.84
2019-03-05 05:30 | 6.17 | 6.14
2019-03-05 06:00 | 6.25 | 6.18
2019-03-05 06:30 | 6.52 | 6.45
2019-03-05 07:00 | 6.61 | 6.56
2019-03-05 07:30 | 6.51 | 6.48
2019-03-05 08:00 | 6 | 5.98
2019-03-05 08:30 | 5.7 | 5.68
2019-03-05 09:00 | 5.56 | 5.55
2019-03-05 09:30 | 5.76 | 5.75
2019-03-05 10:00 | 5.24 | 5.22
2019-03-05 10:30 | 5.75 | 5.73
2019-03-05 11:00 | 6.25 | 6.23
2019-03-05 11:30 | 6.2 | 6.19
2019-03-05 12:00 | 7.06 | 7.05
2019-03-05 12:30 | 6.02 | 6
2019-03-05 13:00 | 5.39 | 5.37
2019-03-05 13:30 | 5.71 | 5.68
2019-03-05 14:00 | 7.15 | 7.13
2019-03-05 14:30 | 7.24 | 7.2
2019-03-05 15:00 | 8.37 | 8.33
2019-03-05 15:30 | 9.41 | 9.37
2019-03-05 16:00 | 10.95 | 10.92
2019-03-05 16:30 | 11.88 | 11.84
2019-03-05 17:00 | 13.14 | 13.11
2019-03-05 17:30 | 13.99 | 13.96
2019-03-05 18:00 | 14.69 | 14.66
2019-03-05 18:30 | 15.4 | 15.37
2019-03-05 19:00 | 16.32 | 16.26
2019-03-05 19:30 | 15.94 | 15.9
2019-03-05 20:00 | 15.64 | 15.6
2019-03-05 20:30 | 14.88 | 14.85
2019-03-05 21:00 | 13.95 | 13.93
2019-03-05 21:30 | 12.9 | 12.89
2019-03-05 22:00 | 11.69 | 11.69
2019-03-05 22:30 | 10.51 | 10.51
2019-03-05 23:00 | 9.88 | 9.88
2019-03-05 23:30 | 8.66 | 8.65
2019-03-06 | 7.79 | 7.78
2019-03-06 00:30 | 7.07 | 7.06
2019-03-06 01:00 | 6.84 | 6.83
2019-03-06 01:30 | 6.61 | 6.6
2019-03-06 02:00 | 6.31 | 6.29
2019-03-06 02:30 | 6.13 | 6.11
2019-03-06 03:00 | 6.01 | 5.99
2019-03-06 03:30 | 6.04 | 6.02
2019-03-06 04:00 | 6.04 | 6.01
2019-03-06 04:30 | 6.11 | 6.09
2019-03-06 05:00 | 6.26 | 6.23
2019-03-06 05:30 | 6.59 | 6.57
2019-03-06 06:00 | 7.03 | 7
2019-03-06 06:30 | 7.83 | 7.81
2019-03-06 07:00 | 7.97 | 7.95
2019-03-06 07:30 | 7.83 | 7.82
2019-03-06 08:00 | 7.06 | 7.06
2019-03-06 08:30 | 6.43 | 6.43
2019-03-06 09:00 | 6.83 | 6.82
2019-03-06 09:30 | 7.09 | 7.08
2019-03-06 10:00 | 6.44 | 6.43
2019-03-06 10:30 | 6.4 | 6.37
2019-03-06 11:00 | 6.81 | 6.78
2019-03-06 11:30 | 7.62 | 7.58
2019-03-06 12:00 | 8.14 | 8.1
2019-03-06 12:30 | 8.98 | 8.9
2019-03-06 13:00 | 9.5 | 9.42
2019-03-06 13:30 | 10.69 | 10.6
2019-03-06 14:00 | 11.52 | 11.42
2019-03-06 14:30 | 12.58 | 12.48
2019-03-06 15:00 | 12.64 | 12.53
2019-03-06 15:30 | 14 | 13.89
2019-03-06 16:00 | 15.63 | 15.52
2019-03-06 16:30 | 16.78 | 16.67
2019-03-06 17:00 | 17.58 | 17.48
2019-03-06 17:30 | 18.38 | 18.29
2019-03-06 18:00 | 18.43 | 18.34
2019-03-06 18:30 | 18.57 | 18.49
2019-03-06 19:00 | 19.25 | 19.13
2019-03-06 19:30 | 19.18 | 19.07
2019-03-06 20:00 | 18.8 | 18.7
2019-03-06 20:30 | 17.81 | 17.74
2019-03-06 21:00 | 16.5 | 16.45
2019-03-06 21:30 | 14.91 | 14.88
2019-03-06 22:00 | 13.73 | 13.71
2019-03-06 22:30 | 12.51 | 12.5
2019-03-06 23:00 | 11.52 | 11.51
2019-03-06 23:30 | 10.14 | 10.13
2019-03-07 | 9.22 | 9.21
2019-03-07 00:30 | 8.47 | 8.47
2019-03-07 01:00 | 8.05 | 8.04
2019-03-07 01:30 | 7.69 | 7.68
2019-03-07 02:00 | 7.38 | 7.37
2019-03-07 02:30 | 7.07 | 7.06
2019-03-07 03:00 | 6.82 | 6.82
2019-03-07 03:30 | 6.84 | 6.83
2019-03-07 04:00 | 6.66 | 6.65
2019-03-07 04:30 | 6.65 | 6.63
2019-03-07 05:00 | 6.73 | 6.72
2019-03-07 05:30 | 6.95 | 6.94
2019-03-07 06:00 | 7.24 | 7.22
2019-03-07 06:30 | 7.75 | 7.73
2019-03-07 07:00 | 8.13 | 8.12
2019-03-07 07:30 | 7.81 | 7.81
2019-03-07 08:00 | 7.45 | 7.44
2019-03-07 08:30 | 7 | 6.99
2019-03-07 09:00 | 7.6 | 7.59
2019-03-07 09:30 | 7.98 | 7.96
2019-03-07 10:00 | 7.49 | 7.47
2019-03-07 10:30 | 7.79 | 7.75
2019-03-07 11:00 | 9.22 | 9.18
2019-03-07 11:30 | 9.74 | 9.69
2019-03-07 12:00 | 10.12 | 10.06
2019-03-07 12:30 | 11 | 10.94
2019-03-07 13:00 | 10.5 | 10.42
2019-03-07 13:30 | 13.59 | 13.53
2019-03-07 14:00 | 12.06 | 11.99
2019-03-07 14:30 | 10.1 | 10.02
2019-03-07 15:00 | 11.54 | 11.45
2019-03-07 15:30 | 13.49 | 13.42
2019-03-07 16:00 | 15.74 | 15.67
2019-03-07 16:30 | 15.88 | 15.8
2019-03-07 17:00 | 16.41 | 16.34
2019-03-07 17:30 | 17.09 | 17.02
2019-03-07 18:00 | 17.66 | 17.59
2019-03-07 18:30 | 18.03 | 17.94
2019-03-07 19:00 | 18.22 | 18.11
2019-03-07 19:30 | 17.74 | 17.65
2019-03-07 20:00 | 17.22 | 17.15
2019-03-07 20:30 | 16.06 | 16.01
2019-03-07 21:00 | 15.04 | 15.01
2019-03-07 21:30 | 13.8 | 13.78
2019-03-07 22:00 | 12.63 | 12.61
2019-03-07 22:30 | 11.55 | 11.54
2019-03-07 23:00 | 10.87 | 10.86
2019-03-07 23:30 | 9.53 | 9.52
2019-03-08 | 8.41 | 8.4
2019-03-08 00:30 | 7.64 | 7.63
2019-03-08 01:00 | 7.38 | 7.38
2019-03-08 01:30 | 6.97 | 6.96
2019-03-08 02:00 | 6.7 | 6.69
2019-03-08 02:30 | 6.62 | 6.61
2019-03-08 03:00 | 6.54 | 6.53
2019-03-08 03:30 | 6.47 | 6.45
2019-03-08 04:00 | 6.36 | 6.35
2019-03-08 04:30 | 6.5 | 6.48
2019-03-08 05:00 | 6.62 | 6.6
2019-03-08 05:30 | 7.12 | 7.11
2019-03-08 06:00 | 7.6 | 7.59
2019-03-08 06:30 | 8.17 | 8.16
2019-03-08 07:00 | 8.44 | 8.43
2019-03-08 07:30 | 8.42 | 8.42
2019-03-08 08:00 | 8.29 | 8.29
2019-03-08 08:30 | 7.4 | 7.39
2019-03-08 09:00 | 7.06 | 7.06
2019-03-08 09:30 | 7.72 | 7.72
2019-03-08 10:00 | 7.25 | 7.24
2019-03-08 10:30 | 7.48 | 7.46
2019-03-08 11:00 | 7.8 | 7.79
2019-03-08 11:30 | 7.44 | 7.42
2019-03-08 12:00 | 8.17 | 8.15
2019-03-08 12:30 | 8.38 | 8.36
2019-03-08 13:00 | 7.28 | 7.24
2019-03-08 13:30 | 7.74 | 7.69
2019-03-08 14:00 | 9.33 | 9.29
2019-03-08 14:30 | 8.92 | 8.87
2019-03-08 15:00 | 9.69 | 9.64
2019-03-08 15:30 | 10.29 | 10.25
2019-03-08 16:00 | 11.67 | 11.62
2019-03-08 16:30 | 12.96 | 12.92
2019-03-08 17:00 | 13.49 | 13.46
2019-03-08 17:30 | 14.19 | 14.15
2019-03-08 18:00 | 14.29 | 14.26
2019-03-08 18:30 | 14.41 | 14.39
2019-03-08 19:00 | 14.96 | 14.93
2019-03-08 19:30 | 14.73 | 14.7
2019-03-08 20:00 | 14.54 | 14.51
2019-03-08 20:30 | 14.09 | 14.07
2019-03-08 21:00 | 13.38 | 13.36
2019-03-08 21:30 | 12.56 | 12.55
2019-03-08 22:00 | 11.69 | 11.69
2019-03-08 22:30 | 11.16 | 11.16
2019-03-08 23:00 | 10.76 | 10.75
2019-03-08 23:30 | 9.6 | 9.59
2019-03-09 | 8.69 | 8.69
2019-03-09 00:30 | 7.92 | 7.92
2019-03-09 01:00 | 7.5 | 7.49
2019-03-09 01:30 | 7.11 | 7.1
2019-03-09 02:00 | 6.75 | 6.74
2019-03-09 02:30 | 6.59 | 6.58
2019-03-09 03:00 | 6.37 | 6.35
2019-03-09 03:30 | 6.31 | 6.29
2019-03-09 04:00 | 6.35 | 6.33
2019-03-09 04:30 | 6.34 | 6.33
2019-03-09 05:00 | 6.27 | 6.25
2019-03-09 05:30 | 6.29 | 6.27
2019-03-09 06:00 | 6.01 | 5.95
2019-03-09 06:30 | 6.03 | 5.95
2019-03-09 07:00 | 5.97 | 5.92
2019-03-09 07:30 | 6.5 | 6.47
2019-03-09 08:00 | 6.4 | 6.38
2019-03-09 08:30 | 6.91 | 6.9
2019-03-09 09:00 | 6.32 | 6.3
2019-03-09 09:30 | 7.4 | 7.38
2019-03-09 10:00 | 7.23 | 7.2
2019-03-09 10:30 | 7.77 | 7.74
2019-03-09 11:00 | 8.23 | 8.2
2019-03-09 11:30 | 8.74 | 8.71
2019-03-09 12:00 | 9.33 | 9.28
2019-03-09 12:30 | 9.98 | 9.92
2019-03-09 13:00 | 10.91 | 10.84
2019-03-09 13:30 | 11.17 | 11.1
2019-03-09 14:00 | 11.72 | 11.63
2019-03-09 14:30 | 12.73 | 12.64
2019-03-09 15:00 | 13.41 | 13.32
2019-03-09 15:30 | 14.4 | 14.31
2019-03-09 16:00 | 15.45 | 15.36
2019-03-09 16:30 | 16.49 | 16.39
2019-03-09 17:00 | 17.05 | 16.96
2019-03-09 17:30 | 17 | 16.93
2019-03-09 18:00 | 16.77 | 16.7
2019-03-09 18:30 | 16.47 | 16.41
2019-03-09 19:00 | 16.62 | 16.55
2019-03-09 19:30 | 16.06 | 16
2019-03-09 20:00 | 15.61 | 15.56
2019-03-09 20:30 | 14.89 | 14.85
2019-03-09 21:00 | 13.98 | 13.95
2019-03-09 21:30 | 13.07 | 13.05
2019-03-09 22:00 | 12.32 | 12.3
2019-03-09 22:30 | 11.93 | 11.92
2019-03-09 23:00 | 11.25 | 11.24
2019-03-09 23:30 | 10.18 | 10.17
2019-03-10 | 9.23 | 9.22
2019-03-10 00:30 | 8.46 | 8.45
2019-03-10 01:00 | 8.01 | 8
2019-03-10 01:30 | 7.57 | 7.57
2019-03-10 02:00 | 7.13 | 7.12
2019-03-10 02:30 | 6.89 | 6.88
2019-03-10 03:00 | 6.73 | 6.72
2019-03-10 03:30 | 6.57 | 6.56
2019-03-10 04:00 | 6.42 | 6.4
2019-03-10 04:30 | 6.29 | 6.27
2019-03-10 05:00 | 6.26 | 6.24
2019-03-10 05:30 | 6.25 | 6.23
2019-03-10 06:00 | 6.05 | 6
2019-03-10 06:30 | 6.03 | 5.96
2019-03-10 07:00 | 5.68 | 5.62
2019-03-10 07:30 | 6.11 | 6.07
2019-03-10 08:00 | 6.52 | 6.51
2019-03-10 08:30 | 6.85 | 6.84
2019-03-10 09:00 | 7.9 | 7.89
2019-03-10 09:30 | 7.7 | 7.68
2019-03-10 10:00 | 8.64 | 8.61
2019-03-10 10:30 | 8.42 | 8.39
2019-03-10 11:00 | 8.82 | 8.78
2019-03-10 11:30 | 9.38 | 9.32
2019-03-10 12:00 | 10.37 | 10.29
2019-03-10 12:30 | 12.4 | 12.31
2019-03-10 13:00 | 12.82 | 12.72
2019-03-10 13:30 | 14.5 | 14.39
2019-03-10 14:00 | 15.25 | 15.12
2019-03-10 14:30 | 15.95 | 15.82
2019-03-10 15:00 | 16.82 | 16.68
2019-03-10 15:30 | 17.97 | 17.84
2019-03-10 16:00 | 18.79 | 18.65
2019-03-10 16:30 | 19.77 | 19.63
2019-03-10 17:00 | 20.65 | 20.53
2019-03-10 17:30 | 20.89 | 20.78
2019-03-10 18:00 | 20.52 | 20.41
2019-03-10 18:30 | 20.1 | 19.99
2019-03-10 19:00 | 19.98 | 19.86
2019-03-10 19:30 | 18.93 | 18.83
2019-03-10 20:00 | 18.28 | 18.2
2019-03-10 20:30 | 17.45 | 17.38
2019-03-10 21:00 | 16.13 | 16.09
2019-03-10 21:30 | 14.97 | 14.93
2019-03-10 22:00 | 13.68 | 13.66
2019-03-10 22:30 | 12.78 | 12.77
2019-03-10 23:00 | 11.96 | 11.95
2019-03-10 23:30 | 10.62 | 10.61
2019-03-11 | 9.52 | 9.52
2019-03-11 00:30 | 8.78 | 8.77
2019-03-11 01:00 | 8.39 | 8.38
2019-03-11 01:30 | 7.92 | 7.91
2019-03-11 02:00 | 7.56 | 7.55
2019-03-11 02:30 | 7.31 | 7.3
2019-03-11 03:00 | 7.18 | 7.18
2019-03-11 03:30 | 6.99 | 6.98
2019-03-11 04:00 | 6.93 | 6.92
2019-03-11 04:30 | 6.87 | 6.86
2019-03-11 05:00 | 6.97 | 6.96
2019-03-11 05:30 | 7.31 | 7.3
2019-03-11 06:00 | 7.76 | 7.75
2019-03-11 06:30 | 8.17 | 8.15
2019-03-11 07:00 | 8.23 | 8.22
2019-03-11 07:30 | 8.33 | 8.33
2019-03-11 08:00 | 8.56 | 8.56
2019-03-11 08:30 | 8.13 | 8.12
2019-03-11 09:00 | 8 | 7.98
2019-03-11 09:30 | 8.61 | 8.57
2019-03-11 10:00 | 9.09 | 9.04
2019-03-11 10:30 | 10.47 | 10.4
2019-03-11 11:00 | 11.75 | 11.67
2019-03-11 11:30 | 11.31 | 11.21
2019-03-11 12:00 | 12.37 | 12.25
2019-03-11 12:30 | 13.59 | 13.46
2019-03-11 13:00 | 16.21 | 16.05
2019-03-11 13:30 | 19.85 | 19.71
2019-03-11 14:00 | 19.37 | 19.22
2019-03-11 14:30 | 17.95 | 17.81
2019-03-11 15:00 | 18.3 | 18.16
2019-03-11 15:30 | 18.08 | 17.94
2019-03-11 16:00 | 18.7 | 18.57
2019-03-11 16:30 | 19.87 | 19.75
2019-03-11 17:00 | 20.04 | 19.91
2019-03-11 17:30 | 20.4 | 20.27
2019-03-11 18:00 | 20.66 | 20.54
2019-03-11 18:30 | 20.7 | 20.57
2019-03-11 19:00 | 21.19 | 21.05
2019-03-11 19:30 | 20.29 | 20.17
2019-03-11 20:00 | 19.18 | 19.08
2019-03-11 20:30 | 18.1 | 18.03
2019-03-11 21:00 | 16.75 | 16.69
2019-03-11 21:30 | 15.41 | 15.36
2019-03-11 22:00 | 13.85 | 13.82
2019-03-11 22:30 | 12.55 | 12.53
2019-03-11 23:00 | 11.55 | 11.54
2019-03-11 23:30 | 10.23 | 10.22
2019-03-12 | 9.16 | 9.16
2019-03-12 00:30 | 8.4 | 8.39
2019-03-12 01:00 | 7.96 | 7.95
2019-03-12 01:30 | 7.64 | 7.64
2019-03-12 02:00 | 7.33 | 7.32
2019-03-12 02:30 | 7.15 | 7.15
2019-03-12 03:00 | 6.99 | 6.98
2019-03-12 03:30 | 6.92 | 6.91
2019-03-12 04:00 | 6.87 | 6.86
2019-03-12 04:30 | 6.99 | 6.98
2019-03-12 05:00 | 7.16 | 7.16
2019-03-12 05:30 | 7.37 | 7.37
2019-03-12 06:00 | 7.9 | 7.89
2019-03-12 06:30 | 8.56 | 8.56
2019-03-12 07:00 | 9.11 | 9.11
2019-03-12 07:30 | 9.25 | 9.24
2019-03-12 08:00 | 8.71 | 8.71
2019-03-12 08:30 | 8.24 | 8.24
2019-03-12 09:00 | 8.19 | 8.19
2019-03-12 09:30 | 7.12 | 7.1
2019-03-12 10:00 | 7.31 | 7.28
2019-03-12 10:30 | 8.07 | 8.01
2019-03-12 11:00 | 9.29 | 9.22
2019-03-12 11:30 | 10.59 | 10.49
2019-03-12 12:00 | 11.93 | 11.82
2019-03-12 12:30 | 13.23 | 13.08
2019-03-12 13:00 | 14.82 | 14.67
2019-03-12 13:30 | 16.15 | 16
2019-03-12 14:00 | 16.1 | 15.94
2019-03-12 14:30 | 17.27 | 17.11
2019-03-12 15:00 | 18.62 | 18.45
2019-03-12 15:30 | 20.81 | 20.63
2019-03-12 16:00 | 21.41 | 21.2
2019-03-12 16:30 | 22.05 | 21.84
2019-03-12 17:00 | 23.84 | 23.62
2019-03-12 17:30 | 24.92 | 24.71
2019-03-12 18:00 | 25.46 | 25.25
2019-03-12 18:30 | 25.2 | 24.98
2019-03-12 19:00 | 25.48 | 25.23
2019-03-12 19:30 | 24.89 | 24.63
2019-03-12 20:00 | 23.68 | 23.45
2019-03-12 20:30 | 23.13 | 22.92
2019-03-12 21:00 | 21.42 | 21.28
2019-03-12 21:30 | 19.17 | 19.06
2019-03-12 22:00 | 17.15 | 17.07
2019-03-12 22:30 | 15.22 | 15.16
2019-03-12 23:00 | 14.06 | 14.02
2019-03-12 23:30 | 12.53 | 12.51
2019-03-13 | 11.13 | 11.12
2019-03-13 00:30 | 10.35 | 10.33
2019-03-13 01:00 | 9.82 | 9.81
2019-03-13 01:30 | 9.19 | 9.19
2019-03-13 02:00 | 8.64 | 8.63
2019-03-13 02:30 | 8.47 | 8.46
2019-03-13 03:00 | 8.08 | 8.07
2019-03-13 03:30 | 7.8 | 7.79
2019-03-13 04:00 | 7.55 | 7.54
2019-03-13 04:30 | 7.48 | 7.47
2019-03-13 05:00 | 7.48 | 7.48
2019-03-13 05:30 | 7.69 | 7.69
2019-03-13 06:00 | 7.81 | 7.8
2019-03-13 06:30 | 7.73 | 7.71
2019-03-13 07:00 | 7.99 | 7.98
2019-03-13 07:30 | 7.86 | 7.85
2019-03-13 08:00 | 7.58 | 7.57
2019-03-13 08:30 | 7.3 | 7.28
2019-03-13 09:00 | 7.25 | 7.23
2019-03-13 09:30 | 7.73 | 7.69
2019-03-13 10:00 | 8.25 | 8.2
2019-03-13 10:30 | 8.92 | 8.85
2019-03-13 11:00 | 9.85 | 9.76
2019-03-13 11:30 | 10.94 | 10.82
2019-03-13 12:00 | 12.84 | 12.72
2019-03-13 12:30 | 13.36 | 13.22
2019-03-13 13:00 | 14.75 | 14.61
2019-03-13 13:30 | 16.13 | 15.97
2019-03-13 14:00 | 17.23 | 17.07
2019-03-13 14:30 | 17.63 | 17.45
2019-03-13 15:00 | 18.18 | 18.01
2019-03-13 15:30 | 19.48 | 19.31
2019-03-13 16:00 | 20.72 | 20.55
2019-03-13 16:30 | 20.81 | 20.62
2019-03-13 17:00 | 21.34 | 21.17
2019-03-13 17:30 | 21.47 | 21.3
2019-03-13 18:00 | 21.32 | 21.18
2019-03-13 18:30 | 20.95 | 20.81
2019-03-13 19:00 | 21.31 | 21.14
2019-03-13 19:30 | 20.63 | 20.48
2019-03-13 20:00 | 19.82 | 19.69
2019-03-13 20:30 | 18.76 | 18.65
2019-03-13 21:00 | 17.37 | 17.29
2019-03-13 21:30 | 15.88 | 15.82
2019-03-13 22:00 | 14.29 | 14.25
2019-03-13 22:30 | 13.02 | 13
2019-03-13 23:00 | 11.93 | 11.92
2019-03-13 23:30 | 10.47 | 10.46
2019-03-14 | 9.44 | 9.43
2019-03-14 00:30 | 8.75 | 8.74
2019-03-14 01:00 | 8.39 | 8.38
2019-03-14 01:30 | 7.94 | 7.94
2019-03-14 02:00 | 7.58 | 7.58
2019-03-14 02:30 | 7.38 | 7.37
2019-03-14 03:00 | 7.17 | 7.16
2019-03-14 03:30 | 7.04 | 7.03
2019-03-14 04:00 | 6.92 | 6.91
2019-03-14 04:30 | 6.87 | 6.86
2019-03-14 05:00 | 6.97 | 6.96
2019-03-14 05:30 | 7.33 | 7.33
2019-03-14 06:00 | 7.73 | 7.72
2019-03-14 06:30 | 8.04 | 8.02
2019-03-14 07:00 | 8.25 | 8.24
2019-03-14 07:30 | 8.15 | 8.15
2019-03-14 08:00 | 7.88 | 7.87
2019-03-14 08:30 | 7.52 | 7.51
2019-03-14 09:00 | 7.68 | 7.67
2019-03-14 09:30 | 8.28 | 8.26
2019-03-14 10:00 | 8.87 | 8.84
2019-03-14 10:30 | 8.76 | 8.73
2019-03-14 11:00 | 8.84 | 8.79
2019-03-14 11:30 | 10.26 | 10.21
2019-03-14 12:00 | 10.75 | 10.69
2019-03-14 12:30 | 11.81 | 11.74
2019-03-14 13:00 | 12.22 | 12.15
2019-03-14 13:30 | 12.6 | 12.51
2019-03-14 14:00 | 13.97 | 13.88
2019-03-14 14:30 | 13.1 | 13.01
2019-03-14 15:00 | 14.12 | 14.03
2019-03-14 15:30 | 13.81 | 13.71
2019-03-14 16:00 | 15.9 | 15.81
2019-03-14 16:30 | 16.72 | 16.64
2019-03-14 17:00 | 16.22 | 16.14
2019-03-14 17:30 | 16.29 | 16.22
2019-03-14 18:00 | 16.89 | 16.82
2019-03-14 18:30 | 17.74 | 17.65
2019-03-14 19:00 | 18.52 | 18.41
2019-03-14 19:30 | 18.2 | 18.11
2019-03-14 20:00 | 17.94 | 17.85
2019-03-14 20:30 | 17.22 | 17.15
2019-03-14 21:00 | 15.53 | 15.48
2019-03-14 21:30 | 14.12 | 14.1
2019-03-14 22:00 | 12.61 | 12.6
2019-03-14 22:30 | 11.48 | 11.47
2019-03-14 23:00 | 10.55 | 10.54
2019-03-14 23:30 | 9.44 | 9.43
2019-03-15 | 8.41 | 8.4
2019-03-15 00:30 | 7.72 | 7.72
2019-03-15 01:00 | 7.4 | 7.4
2019-03-15 01:30 | 7.02 | 7.01
2019-03-15 02:00 | 6.74 | 6.73
2019-03-15 02:30 | 7.61 | 7.59
2019-03-15 03:00 | 7.39 | 7.37
2019-03-15 03:30 | 6.86 | 6.84
2019-03-15 04:00 | 6.2 | 6.18
2019-03-15 04:30 | 6.24 | 6.22
2019-03-15 05:00 | 6.34 | 6.32
2019-03-15 05:30 | 6.62 | 6.6
2019-03-15 06:00 | 6.9 | 6.87
2019-03-15 06:30 | 7.11 | 7.07
2019-03-15 07:00 | 7.16 | 7.13
2019-03-15 07:30 | 7.07 | 7.05
2019-03-15 08:00 | 6.59 | 6.58
2019-03-15 08:30 | 6.02 | 6.02
2019-03-15 09:00 | 5.85 | 5.84
2019-03-15 09:30 | 5.9 | 5.87
2019-03-15 10:00 | 6.01 | 5.98
2019-03-15 10:30 | 6.5 | 6.46
2019-03-15 11:00 | 7.07 | 7.02
2019-03-15 11:30 | 7.64 | 7.58
2019-03-15 12:00 | 8.7 | 8.62
2019-03-15 12:30 | 10.6 | 10.52
2019-03-15 13:00 | 13.51 | 13.43
2019-03-15 13:30 | 14.17 | 14.08
2019-03-15 14:00 | 15.52 | 15.44
2019-03-15 14:30 | 15.39 | 15.31
2019-03-15 15:00 | 15.11 | 15.05
2019-03-15 15:30 | 14.96 | 14.91
2019-03-15 16:00 | 15.78 | 15.74
2019-03-15 16:30 | 15.24 | 15.18
2019-03-15 17:00 | 14.66 | 14.64
2019-03-15 17:30 | 13.09 | 13.08
2019-03-15 18:00 | 12.72 | 12.71
2019-03-15 18:30 | 12.66 | 12.64
2019-03-15 19:00 | 12.65 | 12.64
2019-03-15 19:30 | 12.26 | 12.25
2019-03-15 20:00 | 12.14 | 12.13
2019-03-15 20:30 | 11.69 | 11.68
2019-03-15 21:00 | 11.01 | 11
2019-03-15 21:30 | 10.23 | 10.22
2019-03-15 22:00 | 9.77 | 9.76
2019-03-15 22:30 | 9.26 | 9.25
2019-03-15 23:00 | 8.76 | 8.75
2019-03-15 23:30 | 7.83 | 7.82
2019-03-16 | 7.26 | 7.25
2019-03-16 00:30 | 6.67 | 6.64
2019-03-16 01:00 | 6.36 | 6.34
2019-03-16 01:30 | 6.11 | 6.07
2019-03-16 02:00 | 5.85 | 5.81
2019-03-16 02:30 | 5.85 | 5.81
2019-03-16 03:00 | 5.75 | 5.71
2019-03-16 03:30 | 5.6 | 5.57
2019-03-16 04:00 | 5.63 | 5.59
2019-03-16 04:30 | 5.54 | 5.5
2019-03-16 05:00 | 5.65 | 5.61
2019-03-16 05:30 | 5.8 | 5.76
2019-03-16 06:00 | 5.75 | 5.7
2019-03-16 06:30 | 5.85 | 5.76
2019-03-16 07:00 | 6.28 | 6.21
2019-03-16 07:30 | 6.78 | 6.72
2019-03-16 08:00 | 7.23 | 7.19
2019-03-16 08:30 | 7.54 | 7.5
2019-03-16 09:00 | 7.49 | 7.47
2019-03-16 09:30 | 8.44 | 8.43
2019-03-16 10:00 | 9 | 8.99
2019-03-16 10:30 | 8.81 | 8.79
2019-03-16 11:00 | 7.84 | 7.82
2019-03-16 11:30 | 8.46 | 8.45
2019-03-16 12:00 | 8.74 | 8.72
2019-03-16 12:30 | 8.61 | 8.59
2019-03-16 13:00 | 8.65 | 8.63
2019-03-16 13:30 | 7.74 | 7.72
2019-03-16 14:00 | 6.03 | 6.01
2019-03-16 14:30 | 7.99 | 7.97
2019-03-16 15:00 | 8.37 | 8.35
2019-03-16 15:30 | 8.71 | 8.69
2019-03-16 16:00 | 9.28 | 9.27
2019-03-16 16:30 | 9.9 | 9.88
2019-03-16 17:00 | 10.05 | 10.04
2019-03-16 17:30 | 10.36 | 10.35
2019-03-16 18:00 | 10.57 | 10.56
2019-03-16 18:30 | 11.58 | 11.58
2019-03-16 19:00 | 12.11 | 12.1
2019-03-16 19:30 | 11.98 | 11.97
2019-03-16 20:00 | 11.59 | 11.58
2019-03-16 20:30 | 11.49 | 11.48
2019-03-16 21:00 | 10.84 | 10.83
2019-03-16 21:30 | 10.28 | 10.27
2019-03-16 22:00 | 9.71 | 9.71
2019-03-16 22:30 | 9.38 | 9.37
2019-03-16 23:00 | 9.29 | 9.27
2019-03-16 23:30 | 8.4 | 8.38
2019-03-17 | 7.58 | 7.55
2019-03-17 00:30 | 6.96 | 6.93
2019-03-17 01:00 | 6.49 | 6.46
2019-03-17 01:30 | 6.18 | 6.15
2019-03-17 02:00 | 5.95 | 5.91
2019-03-17 02:30 | 5.79 | 5.75
2019-03-17 03:00 | 5.65 | 5.6
2019-03-17 03:30 | 5.65 | 5.6
2019-03-17 04:00 | 5.59 | 5.55
2019-03-17 04:30 | 5.49 | 5.44
2019-03-17 05:00 | 5.48 | 5.43
2019-03-17 05:30 | 5.56 | 5.5
2019-03-17 06:00 | 5.52 | 5.44
2019-03-17 06:30 | 5.42 | 5.3
2019-03-17 07:00 | 5.83 | 5.74
2019-03-17 07:30 | 6.04 | 5.97
2019-03-17 08:00 | 6.38 | 6.33
2019-03-17 08:30 | 7.09 | 7.05
2019-03-17 09:00 | 7.5 | 7.48
2019-03-17 09:30 | 7.97 | 7.96
2019-03-17 10:00 | 6.83 | 6.81
2019-03-17 10:30 | 7.53 | 7.51
2019-03-17 11:00 | 6.66 | 6.63
2019-03-17 11:30 | 6.45 | 6.42
2019-03-17 12:00 | 7.99 | 7.96
2019-03-17 12:30 | 7.88 | 7.85
2019-03-17 13:00 | 8.15 | 8.12
2019-03-17 13:30 | 8.11 | 8.08
2019-03-17 14:00 | 9.62 | 9.59
2019-03-17 14:30 | 11.49 | 11.46
2019-03-17 15:00 | 11.87 | 11.85
2019-03-17 15:30 | 12.33 | 12.31
2019-03-17 16:00 | 13.24 | 13.22
2019-03-17 16:30 | 13.45 | 13.43
2019-03-17 17:00 | 13.42 | 13.41
2019-03-17 17:30 | 13.66 | 13.64
2019-03-17 18:00 | 13.68 | 13.67
2019-03-17 18:30 | 13.95 | 13.94
2019-03-17 19:00 | 13.74 | 13.73
2019-03-17 19:30 | 13.08 | 13.07
2019-03-17 20:00 | 12.6 | 12.59
2019-03-17 20:30 | 12.36 | 12.35
2019-03-17 21:00 | 11.62 | 11.62
2019-03-17 21:30 | 10.97 | 10.97
2019-03-17 22:00 | 10.08 | 10.08
2019-03-17 22:30 | 9.52 | 9.51
2019-03-17 23:00 | 9.12 | 9.11
2019-03-17 23:30 | 8.24 | 8.23
2019-03-18 | 7.37 | 7.35
2019-03-18 00:30 | 6.88 | 6.86
2019-03-18 01:00 | 6.49 | 6.47
2019-03-18 01:30 | 6.15 | 6.12
2019-03-18 02:00 | 5.89 | 5.85
2019-03-18 02:30 | 5.7 | 5.66
2019-03-18 03:00 | 5.6 | 5.56
2019-03-18 03:30 | 5.62 | 5.58
2019-03-18 04:00 | 5.69 | 5.65
2019-03-18 04:30 | 5.82 | 5.78
2019-03-18 05:00 | 5.99 | 5.95
2019-03-18 05:30 | 6.32 | 6.29
2019-03-18 06:00 | 6.61 | 6.57
2019-03-18 06:30 | 6.95 | 6.9
2019-03-18 07:00 | 7.03 | 6.99
2019-03-18 07:30 | 7.15 | 7.13
2019-03-18 08:00 | 6.98 | 6.97
2019-03-18 08:30 | 6.93 | 6.92
2019-03-18 09:00 | 5.61 | 5.6
2019-03-18 09:30 | 6.73 | 6.72
2019-03-18 10:00 | 5.83 | 5.82
2019-03-18 10:30 | 5.13 | 5.11
2019-03-18 11:00 | 5.87 | 5.85
2019-03-18 11:30 | 5.94 | 5.92
2019-03-18 12:00 | 6.25 | 6.22
2019-03-18 12:30 | 7.18 | 7.14
2019-03-18 13:00 | 8.66 | 8.62
2019-03-18 13:30 | 12.36 | 12.32
2019-03-18 14:00 | 11.74 | 11.72
2019-03-18 14:30 | 7.59 | 7.56
2019-03-18 15:00 | 7.63 | 7.6
2019-03-18 15:30 | 8.92 | 8.89
2019-03-18 16:00 | 11.02 | 10.99
2019-03-18 16:30 | 11.72 | 11.7
2019-03-18 17:00 | 12.99 | 12.97
2019-03-18 17:30 | 13.6 | 13.58
2019-03-18 18:00 | 14.05 | 14.04
2019-03-18 18:30 | 14.4 | 14.38
2019-03-18 19:00 | 15.01 | 14.99
2019-03-18 19:30 | 14.43 | 14.41
2019-03-18 20:00 | 14.13 | 14.12
2019-03-18 20:30 | 13.53 | 13.53
2019-03-18 21:00 | 12.58 | 12.57
2019-03-18 21:30 | 11.62 | 11.62
2019-03-18 22:00 | 10.56 | 10.56
2019-03-18 22:30 | 9.8 | 9.79
2019-03-18 23:00 | 8.98 | 8.97
2019-03-18 23:30 | 7.99 | 7.98
2019-03-19 | 7.05 | 7.02
2019-03-19 00:30 | 6.42 | 6.39
2019-03-19 01:00 | 6.17 | 6.14
2019-03-19 01:30 | 5.93 | 5.89
2019-03-19 02:00 | 5.7 | 5.65
2019-03-19 02:30 | 5.52 | 5.47
2019-03-19 03:00 | 5.5 | 5.45
2019-03-19 03:30 | 5.43 | 5.38
2019-03-19 04:00 | 5.47 | 5.42
2019-03-19 04:30 | 5.62 | 5.57
2019-03-19 05:00 | 5.81 | 5.76
2019-03-19 05:30 | 6.05 | 6.01
2019-03-19 06:00 | 6.37 | 6.31
2019-03-19 06:30 | 6.69 | 6.63
2019-03-19 07:00 | 6.7 | 6.65
2019-03-19 07:30 | 6.88 | 6.85
2019-03-19 08:00 | 6.61 | 6.6
2019-03-19 08:30 | 5.83 | 5.82
2019-03-19 09:00 | 5.07 | 5.06
2019-03-19 09:30 | 4.87 | 4.85
2019-03-19 10:00 | 4.92 | 4.9
2019-03-19 10:30 | 5.04 | 5.01
2019-03-19 11:00 | 5.32 | 5.29
2019-03-19 11:30 | 5.71 | 5.67
2019-03-19 12:00 | 6.23 | 6.19
2019-03-19 12:30 | 6.8 | 6.76
2019-03-19 13:00 | 7.6 | 7.55
2019-03-19 13:30 | 8.28 | 8.22
2019-03-19 14:00 | 9.02 | 8.96
2019-03-19 14:30 | 9.85 | 9.79
2019-03-19 15:00 | 10.97 | 10.9
2019-03-19 15:30 | 12.49 | 12.42
2019-03-19 16:00 | 14.1 | 14.04
2019-03-19 16:30 | 15.28 | 15.21
2019-03-19 17:00 | 16.48 | 16.41
2019-03-19 17:30 | 17.49 | 17.42
2019-03-19 18:00 | 17.88 | 17.82
2019-03-19 18:30 | 18.26 | 18.18
2019-03-19 19:00 | 18.81 | 18.73
2019-03-19 19:30 | 18.16 | 18.08
2019-03-19 20:00 | 17.64 | 17.58
2019-03-19 20:30 | 16.95 | 16.89
2019-03-19 21:00 | 15.61 | 15.57
2019-03-19 21:30 | 14.27 | 14.25
2019-03-19 22:00 | 12.96 | 12.95
2019-03-19 22:30 | 11.87 | 11.87
2019-03-19 23:00 | 10.74 | 10.74
2019-03-19 23:30 | 9.5 | 9.49
2019-03-20 | 8.42 | 8.42
2019-03-20 00:30 | 7.62 | 7.62
2019-03-20 01:00 | 7.3 | 7.29
2019-03-20 01:30 | 6.96 | 6.96
2019-03-20 02:00 | 6.57 | 6.56
2019-03-20 02:30 | 6.42 | 6.41
2019-03-20 03:00 | 6.17 | 6.16
2019-03-20 03:30 | 6.08 | 6.06
2019-03-20 04:00 | 6.09 | 6.06
2019-03-20 04:30 | 6.14 | 6.11
2019-03-20 05:00 | 6.24 | 6.21
2019-03-20 05:30 | 6.59 | 6.57
2019-03-20 06:00 | 6.77 | 6.73
2019-03-20 06:30 | 7.03 | 6.98
2019-03-20 07:00 | 7.12 | 7.08
2019-03-20 07:30 | 6.91 | 6.88
2019-03-20 08:00 | 6.33 | 6.32
2019-03-20 08:30 | 5.8 | 5.79
2019-03-20 09:00 | 5.4 | 5.39
2019-03-20 09:30 | 5.88 | 5.87
2019-03-20 10:00 | 6.68 | 6.66
2019-03-20 10:30 | 5.63 | 5.61
2019-03-20 11:00 | 6.04 | 6.01
2019-03-20 11:30 | 6.92 | 6.87
2019-03-20 12:00 | 7.98 | 7.92
2019-03-20 12:30 | 10.31 | 10.26
2019-03-20 13:00 | 10.16 | 10.07
2019-03-20 13:30 | 11.82 | 11.74
2019-03-20 14:00 | 11 | 10.9
2019-03-20 14:30 | 12.24 | 12.14
2019-03-20 15:00 | 15.33 | 15.25
2019-03-20 15:30 | 14.92 | 14.83
2019-03-20 16:00 | 15.29 | 15.21
2019-03-20 16:30 | 15.2 | 15.13
2019-03-20 17:00 | 15.89 | 15.82
2019-03-20 17:30 | 17.1 | 17.03
2019-03-20 18:00 | 17.12 | 17.06
2019-03-20 18:30 | 17.17 | 17.09
2019-03-20 19:00 | 17.61 | 17.53
2019-03-20 19:30 | 17.24 | 17.17
2019-03-20 20:00 | 17.18 | 17.12
2019-03-20 20:30 | 16.22 | 16.17
2019-03-20 21:00 | 15.24 | 15.21
2019-03-20 21:30 | 14.24 | 14.22
2019-03-20 22:00 | 12.92 | 12.91
2019-03-20 22:30 | 11.9 | 11.9
2019-03-20 23:00 | 11 | 10.99
2019-03-20 23:30 | 9.73 | 9.73
2019-03-21 | 8.68 | 8.67
2019-03-21 00:30 | 7.93 | 7.93
2019-03-21 01:00 | 7.6 | 7.59
2019-03-21 01:30 | 7.31 | 7.31
2019-03-21 02:00 | 6.97 | 6.96
2019-03-21 02:30 | 6.83 | 6.82
2019-03-21 03:00 | 6.67 | 6.66
2019-03-21 03:30 | 6.55 | 6.54
2019-03-21 04:00 | 6.49 | 6.48
2019-03-21 04:30 | 6.5 | 6.48
2019-03-21 05:00 | 6.56 | 6.55
2019-03-21 05:30 | 7.01 | 7.01
2019-03-21 06:00 | 7.58 | 7.57
2019-03-21 06:30 | 7.9 | 7.88
2019-03-21 07:00 | 7.8 | 7.78
2019-03-21 07:30 | 8.49 | 8.48
2019-03-21 08:00 | 8.54 | 8.54
2019-03-21 08:30 | 7.72 | 7.71
2019-03-21 09:00 | 7.09 | 7.08
2019-03-21 09:30 | 7.33 | 7.32
2019-03-21 10:00 | 7.48 | 7.46
2019-03-21 10:30 | 7.04 | 7.03
2019-03-21 11:00 | 7.87 | 7.85
2019-03-21 11:30 | 6.75 | 6.71
2019-03-21 12:00 | 7.51 | 7.45
2019-03-21 12:30 | 8.45 | 8.38
2019-03-21 13:00 | 9.23 | 9.15
2019-03-21 13:30 | 9.76 | 9.68
2019-03-21 14:00 | 11.29 | 11.2
2019-03-21 14:30 | 12.07 | 11.98
2019-03-21 15:00 | 12.88 | 12.78
2019-03-21 15:30 | 14.14 | 14.04
2019-03-21 16:00 | 14.58 | 14.48
2019-03-21 16:30 | 16.53 | 16.45
2019-03-21 17:00 | 16.65 | 16.59
2019-03-21 17:30 | 16.51 | 16.45
2019-03-21 18:00 | 16.58 | 16.53
2019-03-21 18:30 | 16.92 | 16.84
2019-03-21 19:00 | 17.18 | 17.1
2019-03-21 19:30 | 16.65 | 16.58
2019-03-21 20:00 | 16.28 | 16.22
2019-03-21 20:30 | 16.01 | 15.96
2019-03-21 21:00 | 14.88 | 14.85
2019-03-21 21:30 | 13.51 | 13.48
2019-03-21 22:00 | 12.36 | 12.35
2019-03-21 22:30 | 11.57 | 11.56
2019-03-21 23:00 | 10.89 | 10.88
2019-03-21 23:30 | 9.59 | 9.59
2019-03-22 | 8.75 | 8.74
2019-03-22 00:30 | 8.01 | 8
2019-03-22 01:00 | 7.64 | 7.63
2019-03-22 01:30 | 7.41 | 7.4
2019-03-22 02:00 | 7.07 | 7.06
2019-03-22 02:30 | 7 | 6.99
2019-03-22 03:00 | 6.81 | 6.8
2019-03-22 03:30 | 6.71 | 6.7
2019-03-22 04:00 | 6.64 | 6.63
2019-03-22 04:30 | 6.67 | 6.66
2019-03-22 05:00 | 6.85 | 6.84
2019-03-22 05:30 | 7.22 | 7.22
2019-03-22 06:00 | 7.88 | 7.87
2019-03-22 06:30 | 8.31 | 8.3
2019-03-22 07:00 | 8.53 | 8.52
2019-03-22 07:30 | 8.28 | 8.27
2019-03-22 08:00 | 8.25 | 8.25
2019-03-22 08:30 | 7.36 | 7.35
2019-03-22 09:00 | 7.86 | 7.85
2019-03-22 09:30 | 7.45 | 7.43
2019-03-22 10:00 | 7.38 | 7.36
2019-03-22 10:30 | 8.23 | 8.2
2019-03-22 11:00 | 7.52 | 7.48
2019-03-22 11:30 | 8.57 | 8.51
2019-03-22 12:00 | 8.84 | 8.78
2019-03-22 12:30 | 10.8 | 10.75
2019-03-22 13:00 | 11.59 | 11.54
2019-03-22 13:30 | 9.76 | 9.68
2019-03-22 14:00 | 9.97 | 9.86
2019-03-22 14:30 | 10.44 | 10.34
2019-03-22 15:00 | 13.45 | 13.37
2019-03-22 15:30 | 13.39 | 13.31
2019-03-22 16:00 | 15.64 | 15.57
2019-03-22 16:30 | 15.78 | 15.72
2019-03-22 17:00 | 15.19 | 15.14
2019-03-22 17:30 | 15.33 | 15.28
2019-03-22 18:00 | 15.58 | 15.52
2019-03-22 18:30 | 16.03 | 15.96
2019-03-22 19:00 | 16.23 | 16.15
2019-03-22 19:30 | 15.83 | 15.77
2019-03-22 20:00 | 15.53 | 15.48
2019-03-22 20:30 | 15.07 | 15.02
2019-03-22 21:00 | 14.15 | 14.11
2019-03-22 21:30 | 13.43 | 13.4
2019-03-22 22:00 | 12.68 | 12.67
2019-03-22 22:30 | 12 | 11.99
2019-03-22 23:00 | 11.5 | 11.49
2019-03-22 23:30 | 10.31 | 10.3
2019-03-23 | 9.39 | 9.38
2019-03-23 00:30 | 8.53 | 8.53
2019-03-23 01:00 | 8.18 | 8.18
2019-03-23 01:30 | 7.69 | 7.68
2019-03-23 02:00 | 7.3 | 7.29
2019-03-23 02:30 | 7.05 | 7.04
2019-03-23 03:00 | 6.81 | 6.8
2019-03-23 03:30 | 6.67 | 6.66
2019-03-23 04:00 | 6.54 | 6.53
2019-03-23 04:30 | 6.44 | 6.43
2019-03-23 05:00 | 6.45 | 6.44
2019-03-23 05:30 | 6.58 | 6.57
2019-03-23 06:00 | 6.44 | 6.41
2019-03-23 06:30 | 6.42 | 6.37
2019-03-23 07:00 | 6.46 | 6.43
2019-03-23 07:30 | 7.17 | 7.15
2019-03-23 08:00 | 7.27 | 7.26
2019-03-23 08:30 | 6.96 | 6.95
2019-03-23 09:00 | 7.11 | 7.09
2019-03-23 09:30 | 7.44 | 7.41
2019-03-23 10:00 | 8.61 | 8.58
2019-03-23 10:30 | 8.56 | 8.52
2019-03-23 11:00 | 8.75 | 8.7
2019-03-23 11:30 | 9.25 | 9.19
2019-03-23 12:00 | 9.81 | 9.74
2019-03-23 12:30 | 10.73 | 10.64
2019-03-23 13:00 | 11.69 | 11.58
2019-03-23 13:30 | 12.74 | 12.64
2019-03-23 14:00 | 13.89 | 13.77
2019-03-23 14:30 | 15.11 | 14.97
2019-03-23 15:00 | 16.36 | 16.22
2019-03-23 15:30 | 17.62 | 17.47
2019-03-23 16:00 | 18.8 | 18.65
2019-03-23 16:30 | 19.85 | 19.7
2019-03-23 17:00 | 20.7 | 20.56
2019-03-23 17:30 | 20.57 | 20.44
2019-03-23 18:00 | 20.2 | 20.08
2019-03-23 18:30 | 20.1 | 19.97
2019-03-23 19:00 | 19.96 | 19.83
2019-03-23 19:30 | 19.34 | 19.21
2019-03-23 20:00 | 18.54 | 18.44
2019-03-23 20:30 | 17.67 | 17.58
2019-03-23 21:00 | 16.42 | 16.34
2019-03-23 21:30 | 15.17 | 15.12
2019-03-23 22:00 | 13.92 | 13.88
2019-03-23 22:30 | 13.12 | 13.1
2019-03-23 23:00 | 12.38 | 12.37
2019-03-23 23:30 | 11.13 | 11.12
2019-03-24 | 10 | 9.99
2019-03-24 00:30 | 9.16 | 9.15
2019-03-24 01:00 | 8.74 | 8.73
2019-03-24 01:30 | 8.22 | 8.22
2019-03-24 02:00 | 7.78 | 7.77
2019-03-24 02:30 | 7.47 | 7.46
2019-03-24 03:00 | 7.28 | 7.27
2019-03-24 03:30 | 7.05 | 7.05
2019-03-24 04:00 | 6.89 | 6.88
2019-03-24 04:30 | 6.64 | 6.63
2019-03-24 05:00 | 6.62 | 6.61
2019-03-24 05:30 | 6.55 | 6.54
2019-03-24 06:00 | 6.47 | 6.44
2019-03-24 06:30 | 6.46 | 6.41
2019-03-24 07:00 | 6.37 | 6.33
2019-03-24 07:30 | 6.6 | 6.58
2019-03-24 08:00 | 6.87 | 6.86
2019-03-24 08:30 | 7.3 | 7.29
2019-03-24 09:00 | 7.62 | 7.6
2019-03-24 09:30 | 8.08 | 8.05
2019-03-24 10:00 | 8.98 | 8.94
2019-03-24 10:30 | 9.79 | 9.75
2019-03-24 11:00 | 10.94 | 10.87
2019-03-24 11:30 | 12.03 | 11.93
2019-03-24 12:00 | 13.18 | 13.07
2019-03-24 12:30 | 14.47 | 14.33
2019-03-24 13:00 | 15.34 | 15.18
2019-03-24 13:30 | 16.52 | 16.35
2019-03-24 14:00 | 17.74 | 17.56
2019-03-24 14:30 | 18.74 | 18.55
2019-03-24 15:00 | 19.78 | 19.59
2019-03-24 15:30 | 21.06 | 20.87
2019-03-24 16:00 | 22.35 | 22.15
2019-03-24 16:30 | 23.23 | 23.04
2019-03-24 17:00 | 23.88 | 23.69
2019-03-24 17:30 | 24.12 | 23.94
2019-03-24 18:00 | 23.56 | 23.39
2019-03-24 18:30 | 23.18 | 22.99
2019-03-24 19:00 | 23.02 | 22.83
2019-03-24 19:30 | 21.78 | 21.62
2019-03-24 20:00 | 20.73 | 20.6
2019-03-24 20:30 | 19.49 | 19.37
2019-03-24 21:00 | 17.8 | 17.72
2019-03-24 21:30 | 16.18 | 16.12
2019-03-24 22:00 | 14.61 | 14.57
2019-03-24 22:30 | 13.26 | 13.24
2019-03-24 23:00 | 12.26 | 12.25
2019-03-24 23:30 | 10.82 | 10.81
2019-03-25 | 9.62 | 9.61
2019-03-25 00:30 | 8.85 | 8.84
2019-03-25 01:00 | 8.36 | 8.35
2019-03-25 01:30 | 7.91 | 7.9
2019-03-25 02:00 | 7.55 | 7.54
2019-03-25 02:30 | 7.35 | 7.34
2019-03-25 03:00 | 7.21 | 7.2
2019-03-25 03:30 | 7.06 | 7.05
2019-03-25 04:00 | 6.93 | 6.92
2019-03-25 04:30 | 6.91 | 6.9
2019-03-25 05:00 | 6.99 | 6.98
2019-03-25 05:30 | 7.22 | 7.21
2019-03-25 06:00 | 7.29 | 7.27
2019-03-25 06:30 | 7.62 | 7.6
2019-03-25 07:00 | 8.09 | 8.08
2019-03-25 07:30 | 8.26 | 8.25
2019-03-25 08:00 | 8.49 | 8.49
2019-03-25 08:30 | 7.23 | 7.21
2019-03-25 09:00 | 7.25 | 7.23
2019-03-25 09:30 | 7.37 | 7.34
2019-03-25 10:00 | 7.5 | 7.46
2019-03-25 10:30 | 7.76 | 7.71
2019-03-25 11:00 | 8.59 | 8.53
2019-03-25 11:30 | 9.03 | 8.96
2019-03-25 12:00 | 10.12 | 10.04
2019-03-25 12:30 | 10.99 | 10.9
2019-03-25 13:00 | 11.74 | 11.62
2019-03-25 13:30 | 13.05 | 12.94
2019-03-25 14:00 | 14.73 | 14.61
2019-03-25 14:30 | 16.24 | 16.13
2019-03-25 15:00 | 16.65 | 16.55
2019-03-25 15:30 | 16.79 | 16.69
2019-03-25 16:00 | 16.94 | 16.85
2019-03-25 16:30 | 17.16 | 17.06
2019-03-25 17:00 | 18.71 | 18.62
2019-03-25 17:30 | 18.95 | 18.85
2019-03-25 18:00 | 19.43 | 19.34
2019-03-25 18:30 | 20.18 | 20.05
2019-03-25 19:00 | 20.5 | 20.38
2019-03-25 19:30 | 19.7 | 19.58
2019-03-25 20:00 | 18.97 | 18.87
2019-03-25 20:30 | 17.93 | 17.86
2019-03-25 21:00 | 16.47 | 16.42
2019-03-25 21:30 | 15 | 14.96
2019-03-25 22:00 | 13.6 | 13.58
2019-03-25 22:30 | 12.68 | 12.67
2019-03-25 23:00 | 11.83 | 11.83
2019-03-25 23:30 | 10.48 | 10.48
2019-03-26 | 9.4 | 9.4
2019-03-26 00:30 | 8.66 | 8.65
2019-03-26 01:00 | 8.32 | 8.31
2019-03-26 01:30 | 7.94 | 7.93
2019-03-26 02:00 | 7.71 | 7.71
2019-03-26 02:30 | 7.5 | 7.49
2019-03-26 03:00 | 7.34 | 7.34
2019-03-26 03:30 | 7.22 | 7.22
2019-03-26 04:00 | 7.15 | 7.15
2019-03-26 04:30 | 7.15 | 7.14
2019-03-26 05:00 | 7.29 | 7.28
2019-03-26 05:30 | 7.49 | 7.48
2019-03-26 06:00 | 7.87 | 7.86
2019-03-26 06:30 | 8.41 | 8.41
2019-03-26 07:00 | 9.03 | 9.02
2019-03-26 07:30 | 9.18 | 9.18
2019-03-26 08:00 | 9.01 | 9.01
2019-03-26 08:30 | 8.65 | 8.64
2019-03-26 09:00 | 8.4 | 8.39
2019-03-26 09:30 | 8.64 | 8.63
2019-03-26 10:00 | 8.1 | 8.08
2019-03-26 10:30 | 8.86 | 8.84
2019-03-26 11:00 | 9.71 | 9.69
2019-03-26 11:30 | 10.33 | 10.31
2019-03-26 12:00 | 10.09 | 10.06
2019-03-26 12:30 | 10.57 | 10.54
2019-03-26 13:00 | 11.34 | 11.31
2019-03-26 13:30 | 11.31 | 11.28
2019-03-26 14:00 | 9.58 | 9.53
2019-03-26 14:30 | 11.89 | 11.85
2019-03-26 15:00 | 12.94 | 12.9
2019-03-26 15:30 | 13.62 | 13.58
2019-03-26 16:00 | 14.1 | 14.06
2019-03-26 16:30 | 14.29 | 14.25
2019-03-26 17:00 | 15.41 | 15.37
2019-03-26 17:30 | 16.23 | 16.19
2019-03-26 18:00 | 16.61 | 16.56
2019-03-26 18:30 | 17.56 | 17.49
2019-03-26 19:00 | 17.76 | 17.68
2019-03-26 19:30 | 17.23 | 17.17
2019-03-26 20:00 | 16.73 | 16.67
2019-03-26 20:30 | 16.16 | 16.11
2019-03-26 21:00 | 15.09 | 15.06
2019-03-26 21:30 | 13.8 | 13.78
2019-03-26 22:00 | 12.42 | 12.41
2019-03-26 22:30 | 11.54 | 11.54
2019-03-26 23:00 | 10.76 | 10.75
2019-03-26 23:30 | 9.5 | 9.49
2019-03-27 | 8.53 | 8.52
2019-03-27 00:30 | 7.91 | 7.9
2019-03-27 01:00 | 7.62 | 7.62
2019-03-27 01:30 | 7.33 | 7.32
2019-03-27 02:00 | 7.05 | 7.05
2019-03-27 02:30 | 6.9 | 6.89
2019-03-27 03:00 | 6.8 | 6.79
2019-03-27 03:30 | 6.74 | 6.73
2019-03-27 04:00 | 6.65 | 6.64
2019-03-27 04:30 | 6.7 | 6.69
2019-03-27 05:00 | 6.83 | 6.82
2019-03-27 05:30 | 7.28 | 7.27
2019-03-27 06:00 | 7.62 | 7.62
2019-03-27 06:30 | 8.03 | 8.02
2019-03-27 07:00 | 8.27 | 8.26
2019-03-27 07:30 | 8.53 | 8.52
2019-03-27 08:00 | 8.32 | 8.31
2019-03-27 08:30 | 8.12 | 8.11
2019-03-27 09:00 | 8.13 | 8.12
2019-03-27 09:30 | 7.89 | 7.89
2019-03-27 10:00 | 8.38 | 8.37
2019-03-27 10:30 | 7.98 | 7.97
2019-03-27 11:00 | 8.89 | 8.88
2019-03-27 11:30 | 9.21 | 9.2
2019-03-27 12:00 | 9.76 | 9.75
2019-03-27 12:30 | 9.45 | 9.44
2019-03-27 13:00 | 8.21 | 8.2
2019-03-27 13:30 | 8.22 | 8.21
2019-03-27 14:00 | 7.96 | 7.95
2019-03-27 14:30 | 8.14 | 8.13
2019-03-27 15:00 | 8.26 | 8.24
2019-03-27 15:30 | 8.61 | 8.6
2019-03-27 16:00 | 9.19 | 9.18
2019-03-27 16:30 | 9.55 | 9.55
2019-03-27 17:00 | 10.27 | 10.26
2019-03-27 17:30 | 10.78 | 10.77
2019-03-27 18:00 | 11.33 | 11.33
2019-03-27 18:30 | 12.03 | 12.02
2019-03-27 19:00 | 12.29 | 12.29
2019-03-27 19:30 | 11.96 | 11.95
2019-03-27 20:00 | 11.59 | 11.59
2019-03-27 20:30 | 11.43 | 11.43
2019-03-27 21:00 | 10.79 | 10.79
2019-03-27 21:30 | 10.07 | 10.06
2019-03-27 22:00 | 9.07 | 9.06
2019-03-27 22:30 | 8.5 | 8.48
2019-03-27 23:00 | 7.94 | 7.92
2019-03-27 23:30 | 6.96 | 6.93
2019-03-28 | 6.12 | 6.08
2019-03-28 00:30 | 5.48 | 5.43
2019-03-28 01:00 | 5.28 | 5.22
2019-03-28 01:30 | 4.96 | 4.9
2019-03-28 02:00 | 4.82 | 4.76
2019-03-28 02:30 | 4.76 | 4.69
2019-03-28 03:00 | 4.75 | 4.69
2019-03-28 03:30 | 4.78 | 4.71
2019-03-28 04:00 | 4.8 | 4.73
2019-03-28 04:30 | 4.84 | 4.77
2019-03-28 05:00 | 5.07 | 5.01
2019-03-28 05:30 | 5.49 | 5.45
2019-03-28 06:00 | 6.07 | 6.03
2019-03-28 06:30 | 6.62 | 6.57
2019-03-28 07:00 | 7.01 | 6.97
2019-03-28 07:30 | 7.42 | 7.38
2019-03-28 08:00 | 7.14 | 7.11
2019-03-28 08:30 | 6.18 | 6.16
2019-03-28 09:00 | 5.82 | 5.8
2019-03-28 09:30 | 5.75 | 5.73
2019-03-28 10:00 | 5.75 | 5.74
2019-03-28 10:30 | 4.36 | 4.35
2019-03-28 11:00 | 4.6 | 4.59
2019-03-28 11:30 | 5.48 | 5.47
2019-03-28 12:00 | 7.57 | 7.56
2019-03-28 12:30 | 7.3 | 7.29
2019-03-28 13:00 | 7.18 | 7.17
2019-03-28 13:30 | 6.91 | 6.9
2019-03-28 14:00 | 7.59 | 7.58
2019-03-28 14:30 | 6.62 | 6.61
2019-03-28 15:00 | 7 | 6.99
2019-03-28 15:30 | 7.81 | 7.81
2019-03-28 16:00 | 8.3 | 8.3
2019-03-28 16:30 | 8.47 | 8.46
2019-03-28 17:00 | 9.4 | 9.39
2019-03-28 17:30 | 10.37 | 10.37
2019-03-28 18:00 | 11.24 | 11.24
2019-03-28 18:30 | 12.05 | 12.04
2019-03-28 19:00 | 12.75 | 12.74
2019-03-28 19:30 | 12.4 | 12.39
2019-03-28 20:00 | 12.15 | 12.15
2019-03-28 20:30 | 11.98 | 11.98
2019-03-28 21:00 | 11.15 | 11.15
2019-03-28 21:30 | 10.29 | 10.29
2019-03-28 22:00 | 9.37 | 9.36
2019-03-28 22:30 | 8.7 | 8.69
2019-03-28 23:00 | 8.23 | 8.21
2019-03-28 23:30 | 7.25 | 7.23
2019-03-29 | 6.4 | 6.37
2019-03-29 00:30 | 5.8 | 5.76
2019-03-29 01:00 | 5.43 | 5.38
2019-03-29 01:30 | 5.27 | 5.22
2019-03-29 02:00 | 5.01 | 4.96
2019-03-29 02:30 | 4.98 | 4.93
2019-03-29 03:00 | 4.95 | 4.9
2019-03-29 03:30 | 4.92 | 4.86
2019-03-29 04:00 | 4.88 | 4.83
2019-03-29 04:30 | 5.04 | 4.98
2019-03-29 05:00 | 5.26 | 5.21
2019-03-29 05:30 | 5.6 | 5.56
2019-03-29 06:00 | 5.82 | 5.76
2019-03-29 06:30 | 5.99 | 5.93
2019-03-29 07:00 | 5.9 | 5.83
2019-03-29 07:30 | 6.06 | 6.02
2019-03-29 08:00 | 5.82 | 5.79
2019-03-29 08:30 | 5.78 | 5.76
2019-03-29 09:00 | 4.5 | 4.48
2019-03-29 09:30 | 4.67 | 4.65
2019-03-29 10:00 | 4.93 | 4.91
2019-03-29 10:30 | 4.84 | 4.82
2019-03-29 11:00 | 4.83 | 4.8
2019-03-29 11:30 | 5.38 | 5.35
2019-03-29 12:00 | 5.37 | 5.34
2019-03-29 12:30 | 6.05 | 6.04
2019-03-29 13:00 | 6.56 | 6.54
2019-03-29 13:30 | 6.86 | 6.84
2019-03-29 14:00 | 7.06 | 7.04
2019-03-29 14:30 | 6.92 | 6.9
2019-03-29 15:00 | 6.34 | 6.32
2019-03-29 15:30 | 8.06 | 8.04
2019-03-29 16:00 | 8.92 | 8.9
2019-03-29 16:30 | 9.99 | 9.97
2019-03-29 17:00 | 10.86 | 10.84
2019-03-29 17:30 | 11.65 | 11.64
2019-03-29 18:00 | 11.92 | 11.91
2019-03-29 18:30 | 12.71 | 12.69
2019-03-29 19:00 | 13.09 | 13.07
2019-03-29 19:30 | 12.63 | 12.61
2019-03-29 20:00 | 12.53 | 12.52
2019-03-29 20:30 | 12.2 | 12.19
2019-03-29 21:00 | 11.58 | 11.57
2019-03-29 21:30 | 10.81 | 10.81
2019-03-29 22:00 | 10.24 | 10.24
2019-03-29 22:30 | 9.85 | 9.84
2019-03-29 23:00 | 9.61 | 9.6
2019-03-29 23:30 | 8.64 | 8.63
2019-03-30 | 7.75 | 7.74
2019-03-30 00:30 | 7.12 | 7.11
2019-03-30 01:00 | 6.71 | 6.7
2019-03-30 01:30 | 6.35 | 6.33
2019-03-30 02:00 | 6.25 | 6.24
2019-03-30 02:30 | 6 | 5.98
2019-03-30 03:00 | 5.78 | 5.76
2019-03-30 03:30 | 5.77 | 5.74
2019-03-30 04:00 | 5.75 | 5.73
2019-03-30 04:30 | 5.71 | 5.69
2019-03-30 05:00 | 5.51 | 5.49
2019-03-30 05:30 | 5.63 | 5.61
2019-03-30 06:00 | 5.72 | 5.69
2019-03-30 06:30 | 5.81 | 5.75
2019-03-30 07:00 | 6.32 | 6.27
2019-03-30 07:30 | 6.63 | 6.59
2019-03-30 08:00 | 6.38 | 6.35
2019-03-30 08:30 | 7.13 | 7.11
2019-03-30 09:00 | 7.91 | 7.9
2019-03-30 09:30 | 8.11 | 8.09
2019-03-30 10:00 | 9.39 | 9.37
2019-03-30 10:30 | 9.05 | 9.03
2019-03-30 11:00 | 7.67 | 7.64
2019-03-30 11:30 | 9.5 | 9.48
2019-03-30 12:00 | 9.73 | 9.71
2019-03-30 12:30 | 9.59 | 9.57
2019-03-30 13:00 | 10.05 | 10.04
2019-03-30 13:30 | 10.59 | 10.58
2019-03-30 14:00 | 9.99 | 9.98
2019-03-30 14:30 | 9.92 | 9.9
2019-03-30 15:00 | 10.12 | 10.11
2019-03-30 15:30 | 10.22 | 10.21
2019-03-30 16:00 | 9.76 | 9.75
2019-03-30 16:30 | 10.38 | 10.37
2019-03-30 17:00 | 10.89 | 10.89
2019-03-30 17:30 | 11.1 | 11.09
2019-03-30 18:00 | 10.98 | 10.97
2019-03-30 18:30 | 11.34 | 11.33
2019-03-30 19:00 | 11.78 | 11.78
2019-03-30 19:30 | 11.5 | 11.49
2019-03-30 20:00 | 11.28 | 11.27
2019-03-30 20:30 | 10.97 | 10.96
2019-03-30 21:00 | 10.27 | 10.26
2019-03-30 21:30 | 9.49 | 9.49
2019-03-30 22:00 | 8.89 | 8.89
2019-03-30 22:30 | 8.65 | 8.64
2019-03-30 23:00 | 8.55 | 8.53
2019-03-30 23:30 | 7.58 | 7.56
2019-03-31 | 6.73 | 6.7
2019-03-31 00:30 | 6.13 | 6.09
2019-03-31 01:00 | 5.77 | 5.72
2019-03-31 01:30 | 5.43 | 5.37
2019-03-31 02:00 | 5.16 | 5.1
2019-03-31 02:30 | 4.97 | 4.9
2019-03-31 03:00 | 4.87 | 4.8
2019-03-31 03:30 | 4.81 | 4.73
2019-03-31 04:00 | 4.74 | 4.66
2019-03-31 04:30 | 4.66 | 4.58
2019-03-31 05:00 | 4.74 | 4.65
2019-03-31 05:30 | 4.8 | 4.71
2019-03-31 06:00 | 4.8 | 4.67
2019-03-31 06:30 | 4.89 | 4.71
2019-03-31 07:00 | 4.68 | 4.51
2019-03-31 07:30 | 4.44 | 4.28
2019-03-31 08:00 | 4.38 | 4.25
2019-03-31 08:30 | 4.3 | 4.2
2019-03-31 09:00 | 4.04 | 3.96
2019-03-31 09:30 | 3.58 | 3.52
2019-03-31 10:00 | 3.35 | 3.31
2019-03-31 10:30 | 3.04 | 3
2019-03-31 11:00 | 2.95 | 2.91
2019-03-31 11:30 | 2.7 | 2.66
2019-03-31 12:00 | 2.76 | 2.73
2019-03-31 12:30 | 2.76 | 2.72
2019-03-31 13:00 | 2.96 | 2.92
2019-03-31 13:30 | 3.34 | 3.31
2019-03-31 14:00 | 3.87 | 3.84
2019-03-31 14:30 | 4.53 | 4.51
2019-03-31 15:00 | 5.17 | 5.15
2019-03-31 15:30 | 6.03 | 6.02
2019-03-31 16:00 | 7.03 | 7.02
2019-03-31 16:30 | 8.28 | 8.27
2019-03-31 17:00 | 9.4 | 9.39
2019-03-31 17:30 | 10.35 | 10.34
2019-03-31 18:00 | 11.1 | 11.09
2019-03-31 18:30 | 11.64 | 11.63
2019-03-31 19:00 | 11.75 | 11.74
2019-03-31 19:30 | 11.22 | 11.22
2019-03-31 20:00 | 10.86 | 10.85
2019-03-31 20:30 | 10.46 | 10.45
2019-03-31 21:00 | 9.78 | 9.77
2019-03-31 21:30 | 8.93 | 8.91
2019-03-31 22:00 | 8.2 | 8.17
2019-03-31 22:30 | 7.77 | 7.74
2019-03-31 23:00 | 7.53 | 7.5
2019-03-31 23:30 | 6.65 | 6.61
2019-04-01 | 5.81 | 5.75
2019-04-01 00:30 | 5.28 | 5.21
2019-04-01 01:00 | 5.02 | 4.94
2019-04-01 01:30 | 4.69 | 4.6
2019-04-01 02:00 | 4.52 | 4.42
2019-04-01 02:30 | 4.41 | 4.31
2019-04-01 03:00 | 4.35 | 4.24
2019-04-01 03:30 | 4.36 | 4.25
2019-04-01 04:00 | 4.41 | 4.3
2019-04-01 04:30 | 4.6 | 4.5
2019-04-01 05:00 | 4.8 | 4.71
2019-04-01 05:30 | 5.29 | 5.22
2019-04-01 06:00 | 6.08 | 6.02
2019-04-01 06:30 | 6.55 | 6.48
2019-04-01 07:00 | 6.61 | 6.53
2019-04-01 07:30 | 5.97 | 5.9
2019-04-01 08:00 | 5.35 | 5.3
2019-04-01 08:30 | 4.75 | 4.71
2019-04-01 09:00 | 3.62 | 3.58
2019-04-01 09:30 | 2.94 | 2.91
2019-04-01 10:00 | 2.48 | 2.46
2019-04-01 10:30 | 2.6 | 2.57
2019-04-01 11:00 | 2.22 | 2.19
2019-04-01 11:30 | 2.47 | 2.45
2019-04-01 12:00 | 2.26 | 2.25
2019-04-01 12:30 | 3.1 | 3.09
2019-04-01 13:00 | 4.35 | 4.34
2019-04-01 13:30 | 3.94 | 3.94
2019-04-01 14:00 | 5.68 | 5.67
2019-04-01 14:30 | 5.54 | 5.53
2019-04-01 15:00 | 5.33 | 5.32
2019-04-01 15:30 | 6.31 | 6.31
2019-04-01 16:00 | 7.74 | 7.74
2019-04-01 16:30 | 8.22 | 8.22
2019-04-01 17:00 | 9.6 | 9.6
2019-04-01 17:30 | 10.62 | 10.62
2019-04-01 18:00 | 11.45 | 11.45
2019-04-01 18:30 | 12.3 | 12.3
2019-04-01 19:00 | 12.34 | 12.33
2019-04-01 19:30 | 11.9 | 11.9
2019-04-01 20:00 | 11.47 | 11.47
2019-04-01 20:30 | 11.3 | 11.29
2019-04-01 21:00 | 10.6 | 10.59
2019-04-01 21:30 | 9.68 | 9.67
2019-04-01 22:00 | 8.8 | 8.79
2019-04-01 22:30 | 8.03 | 8
2019-04-01 23:00 | 7.41 | 7.37
2019-04-01 23:30 | 6.41 | 6.36
2019-04-02 | 5.65 | 5.59
2019-04-02 00:30 | 5.12 | 5.05
2019-04-02 01:00 | 4.88 | 4.8
2019-04-02 01:30 | 4.59 | 4.5
2019-04-02 02:00 | 4.47 | 4.37
2019-04-02 02:30 | 4.36 | 4.27
2019-04-02 03:00 | 4.35 | 4.25
2019-04-02 03:30 | 4.35 | 4.25
2019-04-02 04:00 | 4.39 | 4.29
2019-04-02 04:30 | 4.53 | 4.44
2019-04-02 05:00 | 4.83 | 4.75
2019-04-02 05:30 | 5.13 | 5.07
2019-04-02 06:00 | 5.91 | 5.87
2019-04-02 06:30 | 6.4 | 6.34
2019-04-02 07:00 | 6.95 | 6.9
2019-04-02 07:30 | 7.43 | 7.39
2019-04-02 08:00 | 6.65 | 6.6
2019-04-02 08:30 | 4.77 | 4.72
2019-04-02 09:00 | 5.03 | 5
2019-04-02 09:30 | 3.78 | 3.75
2019-04-02 10:00 | 2.73 | 2.71
2019-04-02 10:30 | 2.52 | 2.51
2019-04-02 11:00 | 3.39 | 3.39
2019-04-02 11:30 | 4.42 | 4.41
2019-04-02 12:00 | 3.58 | 3.57
2019-04-02 12:30 | 5.31 | 5.3
2019-04-02 13:00 | 7.45 | 7.45
2019-04-02 13:30 | 4.82 | 4.81
2019-04-02 14:00 | 3.54 | 3.52
2019-04-02 14:30 | 6.38 | 6.38
2019-04-02 15:00 | 5.35 | 5.35
2019-04-02 15:30 | 5.98 | 5.98
2019-04-02 16:00 | 7.2 | 7.19
2019-04-02 16:30 | 8.4 | 8.39
2019-04-02 17:00 | 9.82 | 9.81
2019-04-02 17:30 | 10.38 | 10.37
2019-04-02 18:00 | 11.38 | 11.38
2019-04-02 18:30 | 12.32 | 12.31
2019-04-02 19:00 | 12.61 | 12.61
2019-04-02 19:30 | 12.15 | 12.15
2019-04-02 20:00 | 12.1 | 12.09
2019-04-02 20:30 | 11.61 | 11.61
2019-04-02 21:00 | 10.88 | 10.88
2019-04-02 21:30 | 9.95 | 9.94
2019-04-02 22:00 | 9 | 8.99
2019-04-02 22:30 | 8.06 | 8.04
2019-04-02 23:00 | 7.65 | 7.62
2019-04-02 23:30 | 6.74 | 6.7
2019-04-03 | 5.83 | 5.78
2019-04-03 00:30 | 5.25 | 5.18
2019-04-03 01:00 | 5.08 | 5.01
2019-04-03 01:30 | 4.83 | 4.75
2019-04-03 02:00 | 4.7 | 4.62
2019-04-03 02:30 | 4.6 | 4.52
2019-04-03 03:00 | 4.52 | 4.43
2019-04-03 03:30 | 4.53 | 4.44
2019-04-03 04:00 | 4.59 | 4.51
2019-04-03 04:30 | 4.63 | 4.54
2019-04-03 05:00 | 4.88 | 4.81
2019-04-03 05:30 | 5.38 | 5.32
2019-04-03 06:00 | 5.57 | 5.5
2019-04-03 06:30 | 5.92 | 5.83
2019-04-03 07:00 | 6.64 | 6.58
2019-04-03 07:30 | 6.93 | 6.88
2019-04-03 08:00 | 6.46 | 6.42
2019-04-03 08:30 | 5.92 | 5.88
2019-04-03 09:00 | 5.09 | 5.06
2019-04-03 09:30 | 3.33 | 3.3
2019-04-03 10:00 | 3.07 | 3.05
2019-04-03 10:30 | 4.95 | 4.94
2019-04-03 11:00 | 6.23 | 6.22
2019-04-03 11:30 | 4.15 | 4.14
2019-04-03 12:00 | 3.86 | 3.85
2019-04-03 12:30 | 4.08 | 4.07
2019-04-03 13:00 | 4.4 | 4.4
2019-04-03 13:30 | 4.21 | 4.2
2019-04-03 14:00 | 5.88 | 5.88
2019-04-03 14:30 | 6.09 | 6.09
2019-04-03 15:00 | 5.77 | 5.77
2019-04-03 15:30 | 7.2 | 7.19
2019-04-03 16:00 | 7.72 | 7.72
2019-04-03 16:30 | 8.43 | 8.42
2019-04-03 17:00 | 9.3 | 9.29
2019-04-03 17:30 | 10.71 | 10.71
2019-04-03 18:00 | 11.15 | 11.15
2019-04-03 18:30 | 12.06 | 12.05
2019-04-03 19:00 | 12.33 | 12.33
2019-04-03 19:30 | 12.1 | 12.1
2019-04-03 20:00 | 11.93 | 11.93
2019-04-03 20:30 | 11.63 | 11.63
2019-04-03 21:00 | 10.93 | 10.92
2019-04-03 21:30 | 9.98 | 9.98
2019-04-03 22:00 | 9.27 | 9.26
2019-04-03 22:30 | 8.25 | 8.23
2019-04-03 23:00 | 7.64 | 7.61
2019-04-03 23:30 | 6.69 | 6.64
2019-04-04 | 5.92 | 5.86
2019-04-04 00:30 | 5.33 | 5.27
2019-04-04 01:00 | 5.1 | 5.04
2019-04-04 01:30 | 4.8 | 4.74
2019-04-04 02:00 | 4.58 | 4.51
2019-04-04 02:30 | 4.59 | 4.52
2019-04-04 03:00 | 4.57 | 4.49
2019-04-04 03:30 | 4.52 | 4.44
2019-04-04 04:00 | 4.53 | 4.44
2019-04-04 04:30 | 4.73 | 4.65
2019-04-04 05:00 | 4.9 | 4.84
2019-04-04 05:30 | 5.36 | 5.31
2019-04-04 06:00 | 6.18 | 6.14
2019-04-04 06:30 | 6.73 | 6.67
2019-04-04 07:00 | 6.73 | 6.68
2019-04-04 07:30 | 6.58 | 6.54
2019-04-04 08:00 | 5.62 | 5.58
2019-04-04 08:30 | 4.78 | 4.76
2019-04-04 09:00 | 3.87 | 3.85
2019-04-04 09:30 | 3.39 | 3.38
2019-04-04 10:00 | 2.88 | 2.86
2019-04-04 10:30 | 2.78 | 2.77
2019-04-04 11:00 | 2.69 | 2.67
2019-04-04 11:30 | 2.61 | 2.59
2019-04-04 12:00 | 2.74 | 2.72
2019-04-04 12:30 | 2.83 | 2.81
2019-04-04 13:00 | 2.9 | 2.87
2019-04-04 13:30 | 3.45 | 3.43
2019-04-04 14:00 | 4.43 | 4.42
2019-04-04 14:30 | 4.86 | 4.85
2019-04-04 15:00 | 5.61 | 5.6
2019-04-04 15:30 | 6.24 | 6.24
2019-04-04 16:00 | 8.04 | 8.04
2019-04-04 16:30 | 8.66 | 8.65
2019-04-04 17:00 | 10.3 | 10.29
2019-04-04 17:30 | 11 | 10.99
2019-04-04 18:00 | 11.79 | 11.78
2019-04-04 18:30 | 12.77 | 12.76
2019-04-04 19:00 | 12.86 | 12.85
2019-04-04 19:30 | 12.45 | 12.45
2019-04-04 20:00 | 12.25 | 12.25
2019-04-04 20:30 | 11.75 | 11.75
2019-04-04 21:00 | 11 | 10.99
2019-04-04 21:30 | 10.1 | 10.1
2019-04-04 22:00 | 8.95 | 8.94
2019-04-04 22:30 | 8.29 | 8.28
2019-04-04 23:00 | 7.81 | 7.78
2019-04-04 23:30 | 6.9 | 6.87
2019-04-05 | 6.02 | 5.97
2019-04-05 00:30 | 5.38 | 5.32
2019-04-05 01:00 | 5.13 | 5.07
2019-04-05 01:30 | 4.95 | 4.88
2019-04-05 02:00 | 4.77 | 4.69
2019-04-05 02:30 | 4.68 | 4.61
2019-04-05 03:00 | 4.55 | 4.47
2019-04-05 03:30 | 4.55 | 4.47
2019-04-05 04:00 | 4.59 | 4.51
2019-04-05 04:30 | 4.62 | 4.55
2019-04-05 05:00 | 4.85 | 4.78
2019-04-05 05:30 | 5.23 | 5.18
2019-04-05 06:00 | 5.6 | 5.55
2019-04-05 06:30 | 5.84 | 5.76
2019-04-05 07:00 | 5.82 | 5.74
2019-04-05 07:30 | 5.68 | 5.61
2019-04-05 08:00 | 5.08 | 5.03
2019-04-05 08:30 | 4.21 | 4.17
2019-04-05 09:00 | 3.65 | 3.62
2019-04-05 09:30 | 3.66 | 3.62
2019-04-05 10:00 | 2.65 | 2.62
2019-04-05 10:30 | 2.68 | 2.65
2019-04-05 11:00 | 3.21 | 3.19
2019-04-05 11:30 | 3.82 | 3.79
2019-04-05 12:00 | 3.23 | 3.2
2019-04-05 12:30 | 2.73 | 2.7
2019-04-05 13:00 | 3.2 | 3.17
2019-04-05 13:30 | 3.6 | 3.57
2019-04-05 14:00 | 3.75 | 3.71
2019-04-05 14:30 | 4.71 | 4.68
2019-04-05 15:00 | 4.8 | 4.77
2019-04-05 15:30 | 5.88 | 5.85
2019-04-05 16:00 | 7.67 | 7.66
2019-04-05 16:30 | 8.31 | 8.3
2019-04-05 17:00 | 9.48 | 9.47
2019-04-05 17:30 | 9.88 | 9.87
2019-04-05 18:00 | 10.2 | 10.19
2019-04-05 18:30 | 10.93 | 10.92
2019-04-05 19:00 | 11.19 | 11.18
2019-04-05 19:30 | 10.87 | 10.86
2019-04-05 20:00 | 10.9 | 10.89
2019-04-05 20:30 | 10.64 | 10.63
2019-04-05 21:00 | 9.91 | 9.9
2019-04-05 21:30 | 9.25 | 9.24
2019-04-05 22:00 | 8.5 | 8.49
2019-04-05 22:30 | 8.24 | 8.22
2019-04-05 23:00 | 8.02 | 7.99
2019-04-05 23:30 | 7.09 | 7.06
2019-04-06 | 6.27 | 6.22
2019-04-06 00:30 | 5.63 | 5.58
2019-04-06 01:00 | 5.34 | 5.29
2019-04-06 01:30 | 5.11 | 5.05
2019-04-06 02:00 | 4.91 | 4.84
2019-04-06 02:30 | 4.74 | 4.67
2019-04-06 03:00 | 4.67 | 4.59
2019-04-06 03:30 | 4.7 | 4.62
2019-04-06 04:00 | 4.61 | 4.53
2019-04-06 04:30 | 4.62 | 4.54
2019-04-06 05:00 | 4.69 | 4.61
2019-04-06 05:30 | 4.79 | 4.71
2019-04-06 06:00 | 4.77 | 4.67
2019-04-06 06:30 | 4.91 | 4.76
2019-04-06 07:00 | 5.21 | 5.07
2019-04-06 07:30 | 5.12 | 5
2019-04-06 08:00 | 5.33 | 5.24
2019-04-06 08:30 | 4.79 | 4.72
2019-04-06 09:00 | 4.12 | 4.07
2019-04-06 09:30 | 3.92 | 3.89
2019-04-06 10:00 | 3.7 | 3.66
2019-04-06 10:30 | 3.52 | 3.48
2019-04-06 11:00 | 4.5 | 4.47
2019-04-06 11:30 | 4.75 | 4.71
2019-04-06 12:00 | 4.67 | 4.63
2019-04-06 12:30 | 4.92 | 4.89
2019-04-06 13:00 | 4.77 | 4.73
2019-04-06 13:30 | 6.22 | 6.18
2019-04-06 14:00 | 6.07 | 6.04
2019-04-06 14:30 | 7.09 | 7.06
2019-04-06 15:00 | 6.86 | 6.83
2019-04-06 15:30 | 7.74 | 7.72
2019-04-06 16:00 | 8.26 | 8.24
2019-04-06 16:30 | 8.74 | 8.72
2019-04-06 17:00 | 9.79 | 9.78
2019-04-06 17:30 | 10.29 | 10.28
2019-04-06 18:00 | 10.71 | 10.7
2019-04-06 18:30 | 11.3 | 11.29
2019-04-06 19:00 | 11.41 | 11.41
2019-04-06 19:30 | 10.87 | 10.86
2019-04-06 20:00 | 10.6 | 10.59
2019-04-06 20:30 | 10.17 | 10.16
2019-04-06 21:00 | 9.63 | 9.62
2019-04-06 21:30 | 9.01 | 9
2019-04-06 22:00 | 8.5 | 8.49
2019-04-06 22:30 | 8.25 | 8.24
2019-04-06 23:00 | 8.01 | 7.99
2019-04-06 23:30 | 7.25 | 7.22
2019-04-07 | 6.47 | 6.44
2019-04-07 00:30 | 5.87 | 5.83
2019-04-07 01:00 | 5.57 | 5.51
2019-04-07 01:30 | 5.22 | 5.16
2019-04-07 02:00 | 4.95 | 4.88
2019-04-07 02:30 | 4.84 | 4.78
2019-04-07 03:00 | 4.78 | 4.71
2019-04-07 03:30 | 4.68 | 4.6
2019-04-07 04:00 | 4.64 | 4.56
2019-04-07 04:30 | 4.7 | 4.62
2019-04-07 05:00 | 4.6 | 4.52
2019-04-07 05:30 | 4.68 | 4.6
2019-04-07 06:00 | 4.73 | 4.62
2019-04-07 06:30 | 4.93 | 4.79
2019-04-07 07:00 | 4.78 | 4.63
2019-04-07 07:30 | 4.65 | 4.53
2019-04-07 08:00 | 4.7 | 4.61
2019-04-07 08:30 | 4.55 | 4.49
2019-04-07 09:00 | 4.4 | 4.36
2019-04-07 09:30 | 4.24 | 4.21
2019-04-07 10:00 | 4.1 | 4.07
2019-04-07 10:30 | 4.01 | 3.97
2019-04-07 11:00 | 4.06 | 4.01
2019-04-07 11:30 | 4.23 | 4.18
2019-04-07 12:00 | 4.44 | 4.4
2019-04-07 12:30 | 5.11 | 5.07
2019-04-07 13:00 | 5.84 | 5.81
2019-04-07 13:30 | 6.18 | 6.14
2019-04-07 14:00 | 7.3 | 7.27
2019-04-07 14:30 | 8.2 | 8.17
2019-04-07 15:00 | 8.3 | 8.27
2019-04-07 15:30 | 9.03 | 9.01
2019-04-07 16:00 | 9.84 | 9.82
2019-04-07 16:30 | 10.75 | 10.74
2019-04-07 17:00 | 11.5 | 11.49
2019-04-07 17:30 | 12.19 | 12.18
2019-04-07 18:00 | 12.53 | 12.52
2019-04-07 18:30 | 12.99 | 12.98
2019-04-07 19:00 | 12.81 | 12.8
2019-04-07 19:30 | 12.14 | 12.13
2019-04-07 20:00 | 11.7 | 11.69
2019-04-07 20:30 | 11.16 | 11.15
2019-04-07 21:00 | 10.45 | 10.45
2019-04-07 21:30 | 9.72 | 9.72
2019-04-07 22:00 | 8.96 | 8.95
2019-04-07 22:30 | 8.48 | 8.47
2019-04-07 23:00 | 8.18 | 8.16
2019-04-07 23:30 | 7.23 | 7.21
2019-04-08 | 6.3 | 6.27
2019-04-08 00:30 | 5.75 | 5.71
2019-04-08 01:00 | 5.49 | 5.44
2019-04-08 01:30 | 5.25 | 5.19
2019-04-08 02:00 | 4.96 | 4.9
2019-04-08 02:30 | 4.8 | 4.73
2019-04-08 03:00 | 4.76 | 4.68
2019-04-08 03:30 | 4.75 | 4.67
2019-04-08 04:00 | 4.78 | 4.71
2019-04-08 04:30 | 4.88 | 4.8
2019-04-08 05:00 | 5.01 | 4.95
2019-04-08 05:30 | 5.35 | 5.29
2019-04-08 06:00 | 5.49 | 5.41
2019-04-08 06:30 | 5.75 | 5.65
2019-04-08 07:00 | 5.74 | 5.65
2019-04-08 07:30 | 5.49 | 5.42
2019-04-08 08:00 | 5.01 | 4.94
2019-04-08 08:30 | 4.65 | 4.61
2019-04-08 09:00 | 4.25 | 4.23
2019-04-08 09:30 | 3.86 | 3.84
2019-04-08 10:00 | 3.68 | 3.67
2019-04-08 10:30 | 3.62 | 3.6
2019-04-08 11:00 | 3.6 | 3.58
2019-04-08 11:30 | 4.03 | 4.01
2019-04-08 12:00 | 3.87 | 3.85
2019-04-08 12:30 | 4.37 | 4.35
2019-04-08 13:00 | 4.77 | 4.75
2019-04-08 13:30 | 5.31 | 5.29
2019-04-08 14:00 | 6.1 | 6.08
2019-04-08 14:30 | 6.89 | 6.88
2019-04-08 15:00 | 7.96 | 7.95
2019-04-08 15:30 | 8.94 | 8.93
2019-04-08 16:00 | 9.99 | 9.97
2019-04-08 16:30 | 11.13 | 11.12
2019-04-08 17:00 | 11.9 | 11.89
2019-04-08 17:30 | 12.83 | 12.82
2019-04-08 18:00 | 13.33 | 13.32
2019-04-08 18:30 | 14.21 | 14.19
2019-04-08 19:00 | 14.22 | 14.21
2019-04-08 19:30 | 13.21 | 13.2
2019-04-08 20:00 | 12.75 | 12.74
2019-04-08 20:30 | 12.31 | 12.31
2019-04-08 21:00 | 11.25 | 11.24
2019-04-08 21:30 | 10.45 | 10.45
2019-04-08 22:00 | 9.72 | 9.71
2019-04-08 22:30 | 8.8 | 8.79
2019-04-08 23:00 | 8.39 | 8.37
2019-04-08 23:30 | 7.3 | 7.28
2019-04-09 | 6.5 | 6.47
2019-04-09 00:30 | 5.85 | 5.8
2019-04-09 01:00 | 5.53 | 5.49
2019-04-09 01:30 | 5.19 | 5.13
2019-04-09 02:00 | 4.98 | 4.92
2019-04-09 02:30 | 4.9 | 4.84
2019-04-09 03:00 | 4.77 | 4.7
2019-04-09 03:30 | 4.79 | 4.72
2019-04-09 04:00 | 4.78 | 4.7
2019-04-09 04:30 | 4.81 | 4.73
2019-04-09 05:00 | 5.02 | 4.95
2019-04-09 05:30 | 5.36 | 5.31
2019-04-09 06:00 | 5.94 | 5.89
2019-04-09 06:30 | 6.17 | 6.1
2019-04-09 07:00 | 6.01 | 5.92
2019-04-09 07:30 | 5.63 | 5.56
2019-04-09 08:00 | 4.98 | 4.91
2019-04-09 08:30 | 4.58 | 4.54
2019-04-09 09:00 | 4.32 | 4.3
2019-04-09 09:30 | 4.14 | 4.13
2019-04-09 10:00 | 4.05 | 4.04
2019-04-09 10:30 | 3.65 | 3.64
2019-04-09 11:00 | 3.82 | 3.8
2019-04-09 11:30 | 3.53 | 3.5
2019-04-09 12:00 | 4.44 | 4.42
2019-04-09 12:30 | 4.8 | 4.77
2019-04-09 13:00 | 4.96 | 4.93
2019-04-09 13:30 | 5.49 | 5.46
2019-04-09 14:00 | 7.11 | 7.09
2019-04-09 14:30 | 7.16 | 7.14
2019-04-09 15:00 | 8.37 | 8.35
2019-04-09 15:30 | 8.96 | 8.95
2019-04-09 16:00 | 10.56 | 10.55
2019-04-09 16:30 | 11.01 | 11
2019-04-09 17:00 | 12.13 | 12.12
2019-04-09 17:30 | 12.92 | 12.91
2019-04-09 18:00 | 13.79 | 13.77
2019-04-09 18:30 | 14.45 | 14.42
2019-04-09 19:00 | 14.45 | 14.42
2019-04-09 19:30 | 13.45 | 13.43
2019-04-09 20:00 | 13.27 | 13.26
2019-04-09 20:30 | 12.58 | 12.57
2019-04-09 21:00 | 11.78 | 11.78
2019-04-09 21:30 | 10.82 | 10.82
2019-04-09 22:00 | 9.81 | 9.81
2019-04-09 22:30 | 8.95 | 8.94
2019-04-09 23:00 | 8.52 | 8.51
2019-04-09 23:30 | 7.48 | 7.46
2019-04-10 | 6.59 | 6.56
2019-04-10 00:30 | 6 | 5.97
2019-04-10 01:00 | 5.66 | 5.63
2019-04-10 01:30 | 5.39 | 5.34
2019-04-10 02:00 | 5.11 | 5.05
2019-04-10 02:30 | 5.01 | 4.95
2019-04-10 03:00 | 4.82 | 4.76
2019-04-10 03:30 | 4.86 | 4.8
2019-04-10 04:00 | 4.9 | 4.83
2019-04-10 04:30 | 5.04 | 4.97
2019-04-10 05:00 | 5.21 | 5.16
2019-04-10 05:30 | 5.51 | 5.46
2019-04-10 06:00 | 5.73 | 5.68
2019-04-10 06:30 | 6.1 | 6.03
2019-04-10 07:00 | 6.07 | 6
2019-04-10 07:30 | 5.97 | 5.91
2019-04-10 08:00 | 5.55 | 5.49
2019-04-10 08:30 | 4.97 | 4.93
2019-04-10 09:00 | 5.62 | 5.61
2019-04-10 09:30 | 4.62 | 4.61
2019-04-10 10:00 | 4.91 | 4.9
2019-04-10 10:30 | 5.37 | 5.36
2019-04-10 11:00 | 4.9 | 4.88
2019-04-10 11:30 | 5.07 | 5.05
2019-04-10 12:00 | 6.19 | 6.17
2019-04-10 12:30 | 5.03 | 5.02
2019-04-10 13:00 | 7.95 | 7.94
2019-04-10 13:30 | 8.07 | 8.06
2019-04-10 14:00 | 6.77 | 6.76
2019-04-10 14:30 | 8.7 | 8.69
2019-04-10 15:00 | 7.23 | 7.22
2019-04-10 15:30 | 6.69 | 6.69
2019-04-10 16:00 | 7.96 | 7.95
2019-04-10 16:30 | 9.09 | 9.09
2019-04-10 17:00 | 9.74 | 9.73
2019-04-10 17:30 | 10.93 | 10.93
2019-04-10 18:00 | 11.75 | 11.74
2019-04-10 18:30 | 12.28 | 12.28
2019-04-10 19:00 | 12.38 | 12.37
2019-04-10 19:30 | 11.93 | 11.93
2019-04-10 20:00 | 11.8 | 11.79
2019-04-10 20:30 | 11.64 | 11.63
2019-04-10 21:00 | 10.93 | 10.93
2019-04-10 21:30 | 10.34 | 10.34
2019-04-10 22:00 | 9.33 | 9.32
2019-04-10 22:30 | 8.5 | 8.48
2019-04-10 23:00 | 8.05 | 8.03
2019-04-10 23:30 | 7.09 | 7.06
2019-04-11 | 6.24 | 6.2
2019-04-11 00:30 | 5.64 | 5.59
2019-04-11 01:00 | 5.39 | 5.34
2019-04-11 01:30 | 5.04 | 4.98
2019-04-11 02:00 | 4.84 | 4.77
2019-04-11 02:30 | 4.77 | 4.7
2019-04-11 03:00 | 4.74 | 4.66
2019-04-11 03:30 | 4.64 | 4.56
2019-04-11 04:00 | 4.66 | 4.58
2019-04-11 04:30 | 4.82 | 4.74
2019-04-11 05:00 | 4.98 | 4.91
2019-04-11 05:30 | 5.23 | 5.17
2019-04-11 06:00 | 5.84 | 5.79
2019-04-11 06:30 | 6.15 | 6.08
2019-04-11 07:00 | 6.1 | 6.03
2019-04-11 07:30 | 6.31 | 6.26
2019-04-11 08:00 | 5.44 | 5.38
2019-04-11 08:30 | 4.8 | 4.76
2019-04-11 09:00 | 4.14 | 4.12
2019-04-11 09:30 | 3.65 | 3.63
2019-04-11 10:00 | 3.27 | 3.25
2019-04-11 10:30 | 3.54 | 3.53
2019-04-11 11:00 | 6.24 | 6.23
2019-04-11 11:30 | 5.93 | 5.92
2019-04-11 12:00 | 3.66 | 3.65
2019-04-11 12:30 | 3.77 | 3.75
2019-04-11 13:00 | 5 | 4.98
2019-04-11 13:30 | 3.15 | 3.11
2019-04-11 14:00 | 4.76 | 4.74
2019-04-11 14:30 | 5.35 | 5.34
2019-04-11 15:00 | 5.08 | 5.06
2019-04-11 15:30 | 6.06 | 6.05
2019-04-11 16:00 | 7.12 | 7.11
2019-04-11 16:30 | 9.09 | 9.08
2019-04-11 17:00 | 9.13 | 9.13
2019-04-11 17:30 | 9.98 | 9.97
2019-04-11 18:00 | 11.12 | 11.12
2019-04-11 18:30 | 11.92 | 11.92
2019-04-11 19:00 | 12.18 | 12.18
2019-04-11 19:30 | 11.52 | 11.52
2019-04-11 20:00 | 11.38 | 11.38
2019-04-11 20:30 | 10.99 | 10.99
2019-04-11 21:00 | 10.3 | 10.3
2019-04-11 21:30 | 9.52 | 9.51
2019-04-11 22:00 | 8.94 | 8.92
2019-04-11 22:30 | 8.3 | 8.28
2019-04-11 23:00 | 7.79 | 7.76
2019-04-11 23:30 | 7.01 | 6.97
2019-04-12 | 6.11 | 6.06
2019-04-12 00:30 | 5.45 | 5.39
2019-04-12 01:00 | 5.15 | 5.08
2019-04-12 01:30 | 4.88 | 4.81
2019-04-12 02:00 | 4.63 | 4.55
2019-04-12 02:30 | 4.59 | 4.5
2019-04-12 03:00 | 4.43 | 4.34
2019-04-12 03:30 | 4.49 | 4.39
2019-04-12 04:00 | 4.49 | 4.39
2019-04-12 04:30 | 4.69 | 4.6
2019-04-12 05:00 | 5.18 | 5.11
2019-04-12 05:30 | 5.55 | 5.49
2019-04-12 06:00 | 5.76 | 5.69
2019-04-12 06:30 | 5.73 | 5.63
2019-04-12 07:00 | 5.6 | 5.49
2019-04-12 07:30 | 5.41 | 5.32
2019-04-12 08:00 | 4.75 | 4.66
2019-04-12 08:30 | 4.57 | 4.49
2019-04-12 09:00 | 4.82 | 4.77
2019-04-12 09:30 | 4.21 | 4.17
2019-04-12 10:00 | 2.85 | 2.81
2019-04-12 10:30 | 3.43 | 3.39
2019-04-12 11:00 | 3.1 | 3.06
2019-04-12 11:30 | 5.39 | 5.36
2019-04-12 12:00 | 4.11 | 4.08
2019-04-12 12:30 | 4.5 | 4.47
2019-04-12 13:00 | 4.8 | 4.76
2019-04-12 13:30 | 5.24 | 5.21
2019-04-12 14:00 | 4.33 | 4.3
2019-04-12 14:30 | 5.65 | 5.62
2019-04-12 15:00 | 5.98 | 5.95
2019-04-12 15:30 | 6.57 | 6.54
2019-04-12 16:00 | 6.87 | 6.83
2019-04-12 16:30 | 7.55 | 7.52
2019-04-12 17:00 | 8.16 | 8.13
2019-04-12 17:30 | 9.18 | 9.17
2019-04-12 18:00 | 9.97 | 9.96
2019-04-12 18:30 | 10.4 | 10.39
2019-04-12 19:00 | 10.47 | 10.47
2019-04-12 19:30 | 10.34 | 10.33
2019-04-12 20:00 | 10.29 | 10.29
2019-04-12 20:30 | 10.21 | 10.21
2019-04-12 21:00 | 9.46 | 9.45
2019-04-12 21:30 | 8.89 | 8.87
2019-04-12 22:00 | 8.32 | 8.3
2019-04-12 22:30 | 8.07 | 8.04
2019-04-12 23:00 | 7.85 | 7.82
2019-04-12 23:30 | 6.99 | 6.94
2019-04-13 | 6.13 | 6.08
2019-04-13 00:30 | 5.54 | 5.46
2019-04-13 01:00 | 5.19 | 5.11
2019-04-13 01:30 | 4.9 | 4.81
2019-04-13 02:00 | 4.61 | 4.51
2019-04-13 02:30 | 4.56 | 4.46
2019-04-13 03:00 | 4.48 | 4.38
2019-04-13 03:30 | 4.45 | 4.34
2019-04-13 04:00 | 4.44 | 4.33
2019-04-13 04:30 | 4.42 | 4.31
2019-04-13 05:00 | 4.49 | 4.38
2019-04-13 05:30 | 4.59 | 4.49
2019-04-13 06:00 | 4.71 | 4.59
2019-04-13 06:30 | 4.76 | 4.59
2019-04-13 07:00 | 4.77 | 4.6
2019-04-13 07:30 | 4.68 | 4.53
2019-04-13 08:00 | 4.46 | 4.34
2019-04-13 08:30 | 4.23 | 4.13
2019-04-13 09:00 | 3.96 | 3.89
2019-04-13 09:30 | 3.75 | 3.71
2019-04-13 10:00 | 3.36 | 3.32
2019-04-13 10:30 | 3.22 | 3.19
2019-04-13 11:00 | 3.44 | 3.4
2019-04-13 11:30 | 4.19 | 4.16
2019-04-13 12:00 | 4.08 | 4.04
2019-04-13 12:30 | 3.24 | 3.2
2019-04-13 13:00 | 4.2 | 4.16
2019-04-13 13:30 | 5.35 | 5.32
2019-04-13 14:00 | 5.69 | 5.66
2019-04-13 14:30 | 5.14 | 5.11
2019-04-13 15:00 | 5.78 | 5.76
2019-04-13 15:30 | 7.13 | 7.12
2019-04-13 16:00 | 6.97 | 6.95
2019-04-13 16:30 | 7.41 | 7.39
2019-04-13 17:00 | 8.41 | 8.39
2019-04-13 17:30 | 9.04 | 9.03
2019-04-13 18:00 | 9.79 | 9.78
2019-04-13 18:30 | 10.34 | 10.34
2019-04-13 19:00 | 10.42 | 10.42
2019-04-13 19:30 | 9.94 | 9.94
2019-04-13 20:00 | 9.86 | 9.85
2019-04-13 20:30 | 9.65 | 9.64
2019-04-13 21:00 | 9.08 | 9.07
2019-04-13 21:30 | 8.58 | 8.56
2019-04-13 22:00 | 8.11 | 8.09
2019-04-13 22:30 | 7.77 | 7.73
2019-04-13 23:00 | 7.64 | 7.6
2019-04-13 23:30 | 6.91 | 6.87
2019-04-14 | 6.19 | 6.13
2019-04-14 00:30 | 5.61 | 5.55
2019-04-14 01:00 | 5.28 | 5.21
2019-04-14 01:30 | 5 | 4.93
2019-04-14 02:00 | 4.67 | 4.58
2019-04-14 02:30 | 4.45 | 4.35
2019-04-14 03:00 | 4.38 | 4.27
2019-04-14 03:30 | 4.35 | 4.24
2019-04-14 04:00 | 4.34 | 4.24
2019-04-14 04:30 | 4.3 | 4.2
2019-04-14 05:00 | 4.37 | 4.27
2019-04-14 05:30 | 4.38 | 4.28
2019-04-14 06:00 | 4.41 | 4.28
2019-04-14 06:30 | 4.6 | 4.42
2019-04-14 07:00 | 4.41 | 4.21
2019-04-14 07:30 | 4.35 | 4.17
2019-04-14 08:00 | 4.22 | 4.07
2019-04-14 08:30 | 5.34 | 5.24
2019-04-14 09:00 | 5.12 | 5.04
2019-04-14 09:30 | 4.16 | 4.09
2019-04-14 10:00 | 5 | 4.95
2019-04-14 10:30 | 4.48 | 4.44
2019-04-14 11:00 | 4.02 | 3.98
2019-04-14 11:30 | 4.89 | 4.86
2019-04-14 12:00 | 4.15 | 4.12
2019-04-14 12:30 | 4.91 | 4.89
2019-04-14 13:00 | 4.65 | 4.63
2019-04-14 13:30 | 5.11 | 5.09
2019-04-14 14:00 | 5.95 | 5.93
2019-04-14 14:30 | 6.82 | 6.8
2019-04-14 15:00 | 5.85 | 5.84
2019-04-14 15:30 | 7.01 | 6.99
2019-04-14 16:00 | 7.37 | 7.35
2019-04-14 16:30 | 8.16 | 8.14
2019-04-14 17:00 | 9.25 | 9.23
2019-04-14 17:30 | 9.83 | 9.82
2019-04-14 18:00 | 10.78 | 10.77
2019-04-14 18:30 | 11.27 | 11.27
2019-04-14 19:00 | 11.06 | 11.05
2019-04-14 19:30 | 10.58 | 10.58
2019-04-14 20:00 | 10.33 | 10.32
2019-04-14 20:30 | 10.05 | 10.04
2019-04-14 21:00 | 9.35 | 9.34
2019-04-14 21:30 | 8.8 | 8.78
2019-04-14 22:00 | 8.08 | 8.06
2019-04-14 22:30 | 7.71 | 7.68
2019-04-14 23:00 | 7.49 | 7.46
2019-04-14 23:30 | 6.72 | 6.68
2019-04-15 | 5.85 | 5.79
2019-04-15 00:30 | 5.35 | 5.28
2019-04-15 01:00 | 5.07 | 5
2019-04-15 01:30 | 4.78 | 4.7
2019-04-15 02:00 | 4.59 | 4.5
2019-04-15 02:30 | 4.53 | 4.43
2019-04-15 03:00 | 4.42 | 4.32
2019-04-15 03:30 | 4.43 | 4.32
2019-04-15 04:00 | 4.4 | 4.29
2019-04-15 04:30 | 4.56 | 4.46
2019-04-15 05:00 | 4.88 | 4.8
2019-04-15 05:30 | 5.12 | 5.04
2019-04-15 06:00 | 5.22 | 5.13
2019-04-15 06:30 | 5.48 | 5.36
2019-04-15 07:00 | 5.41 | 5.29
2019-04-15 07:30 | 4.99 | 4.88
2019-04-15 08:00 | 4.77 | 4.66
2019-04-15 08:30 | 3.76 | 3.66
2019-04-15 09:00 | 3.68 | 3.62
2019-04-15 09:30 | 3.98 | 3.93
2019-04-15 10:00 | 3.78 | 3.75
2019-04-15 10:30 | 3.13 | 3.11
2019-04-15 11:00 | 3.02 | 3
2019-04-15 11:30 | 3.33 | 3.31
2019-04-15 12:00 | 3.76 | 3.74
2019-04-15 12:30 | 4.51 | 4.5
2019-04-15 13:00 | 5 | 4.99
2019-04-15 13:30 | 4.79 | 4.77
2019-04-15 14:00 | 5.83 | 5.81
2019-04-15 14:30 | 5.87 | 5.85
2019-04-15 15:00 | 6.81 | 6.8
2019-04-15 15:30 | 8.31 | 8.31
2019-04-15 16:00 | 8.22 | 8.21
2019-04-15 16:30 | 9 | 9
2019-04-15 17:00 | 9.8 | 9.8
2019-04-15 17:30 | 10.57 | 10.56
2019-04-15 18:00 | 11.58 | 11.57
2019-04-15 18:30 | 12.32 | 12.31
2019-04-15 19:00 | 12.26 | 12.26
2019-04-15 19:30 | 11.72 | 11.72
2019-04-15 20:00 | 11.61 | 11.6
2019-04-15 20:30 | 11.3 | 11.29
2019-04-15 21:00 | 10.69 | 10.69
2019-04-15 21:30 | 9.86 | 9.86
2019-04-15 22:00 | 8.99 | 8.97
2019-04-15 22:30 | 8.3 | 8.28
2019-04-15 23:00 | 8.04 | 8.01
2019-04-15 23:30 | 6.94 | 6.89
2019-04-16 | 6.03 | 5.98
2019-04-16 00:30 | 5.41 | 5.35
2019-04-16 01:00 | 5.11 | 5.04
2019-04-16 01:30 | 4.85 | 4.77
2019-04-16 02:00 | 4.67 | 4.59
2019-04-16 02:30 | 4.53 | 4.44
2019-04-16 03:00 | 4.43 | 4.34
2019-04-16 03:30 | 4.44 | 4.35
2019-04-16 04:00 | 4.47 | 4.38
2019-04-16 04:30 | 4.64 | 4.55
2019-04-16 05:00 | 4.82 | 4.73
2019-04-16 05:30 | 5.22 | 5.15
2019-04-16 06:00 | 5.67 | 5.6
2019-04-16 06:30 | 6.12 | 6.03
2019-04-16 07:00 | 6.19 | 6.1
2019-04-16 07:30 | 5.77 | 5.69
2019-04-16 08:00 | 5.54 | 5.45
2019-04-16 08:30 | 5.41 | 5.34
2019-04-16 09:00 | 5.18 | 5.12
2019-04-16 09:30 | 4 | 3.96
2019-04-16 10:00 | 3.37 | 3.34
2019-04-16 10:30 | 3.32 | 3.3
2019-04-16 11:00 | 3.57 | 3.56
2019-04-16 11:30 | 4.29 | 4.28
2019-04-16 12:00 | 6.78 | 6.77
2019-04-16 12:30 | 5.07 | 5.05
2019-04-16 13:00 | 7.34 | 7.32
2019-04-16 13:30 | 5.97 | 5.95
2019-04-16 14:00 | 5.58 | 5.55
2019-04-16 14:30 | 6.22 | 6.2
2019-04-16 15:00 | 7.84 | 7.82
2019-04-16 15:30 | 7.22 | 7.2
2019-04-16 16:00 | 7.04 | 7.02
2019-04-16 16:30 | 8.37 | 8.36
2019-04-16 17:00 | 9.28 | 9.27
2019-04-16 17:30 | 10.09 | 10.08
2019-04-16 18:00 | 11.37 | 11.36
2019-04-16 18:30 | 11.98 | 11.98
2019-04-16 19:00 | 12.12 | 12.12
2019-04-16 19:30 | 11.68 | 11.68
2019-04-16 20:00 | 11.56 | 11.56
2019-04-16 20:30 | 11.26 | 11.26
2019-04-16 21:00 | 10.56 | 10.56
2019-04-16 21:30 | 9.81 | 9.8
2019-04-16 22:00 | 9 | 8.99
2019-04-16 22:30 | 8.28 | 8.26
2019-04-16 23:00 | 7.82 | 7.79
2019-04-16 23:30 | 6.85 | 6.8
2019-04-17 | 5.99 | 5.93
2019-04-17 00:30 | 5.32 | 5.25
2019-04-17 01:00 | 5.01 | 4.93
2019-04-17 01:30 | 4.88 | 4.8
2019-04-17 02:00 | 4.6 | 4.51
2019-04-17 02:30 | 4.48 | 4.38
2019-04-17 03:00 | 4.3 | 4.19
2019-04-17 03:30 | 4.34 | 4.23
2019-04-17 04:00 | 4.37 | 4.26
2019-04-17 04:30 | 4.51 | 4.41
2019-04-17 05:00 | 4.72 | 4.63
2019-04-17 05:30 | 5.13 | 5.05
2019-04-17 06:00 | 5.39 | 5.31
2019-04-17 06:30 | 5.64 | 5.52
2019-04-17 07:00 | 5.72 | 5.6
2019-04-17 07:30 | 5.28 | 5.17
2019-04-17 08:00 | 5.45 | 5.34
2019-04-17 08:30 | 5.15 | 5.04
2019-04-17 09:00 | 4.13 | 4.04
2019-04-17 09:30 | 2.99 | 2.92
2019-04-17 10:00 | 2.93 | 2.9
2019-04-17 10:30 | 3.2 | 3.18
2019-04-17 11:00 | 2.97 | 2.95
2019-04-17 11:30 | 3.54 | 3.52
2019-04-17 12:00 | 4.57 | 4.55
2019-04-17 12:30 | 4.81 | 4.79
2019-04-17 13:00 | 2.88 | 2.85
2019-04-17 13:30 | 3.75 | 3.72
2019-04-17 14:00 | 3.92 | 3.9
2019-04-17 14:30 | 4.98 | 4.96
2019-04-17 15:00 | 6.33 | 6.32
2019-04-17 15:30 | 6.04 | 6.03
2019-04-17 16:00 | 7.35 | 7.34
2019-04-17 16:30 | 7.76 | 7.75
2019-04-17 17:00 | 9.05 | 9.05
2019-04-17 17:30 | 10.25 | 10.25
2019-04-17 18:00 | 11.12 | 11.12
2019-04-17 18:30 | 11.98 | 11.98
2019-04-17 19:00 | 11.98 | 11.97
2019-04-17 19:30 | 11.55 | 11.55
2019-04-17 20:00 | 11.82 | 11.82
2019-04-17 20:30 | 11.46 | 11.46
2019-04-17 21:00 | 10.82 | 10.81
2019-04-17 21:30 | 9.95 | 9.94
2019-04-17 22:00 | 9.28 | 9.27
2019-04-17 22:30 | 8.55 | 8.53
2019-04-17 23:00 | 8.26 | 8.24
2019-04-17 23:30 | 7.13 | 7.09
2019-04-18 | 6.22 | 6.16
2019-04-18 00:30 | 5.59 | 5.53
2019-04-18 01:00 | 5.25 | 5.19
2019-04-18 01:30 | 4.98 | 4.9
2019-04-18 02:00 | 4.74 | 4.66
2019-04-18 02:30 | 4.6 | 4.51
2019-04-18 03:00 | 4.51 | 4.42
2019-04-18 03:30 | 4.48 | 4.39
2019-04-18 04:00 | 4.56 | 4.47
2019-04-18 04:30 | 4.63 | 4.54
2019-04-18 05:00 | 4.82 | 4.74
2019-04-18 05:30 | 5.26 | 5.2
2019-04-18 06:00 | 5.94 | 5.88
2019-04-18 06:30 | 6.18 | 6.09
2019-04-18 07:00 | 6.1 | 6.01
2019-04-18 07:30 | 5.68 | 5.59
2019-04-18 08:00 | 5 | 4.92
2019-04-18 08:30 | 4.62 | 4.56
2019-04-18 09:00 | 3.8 | 3.74
2019-04-18 09:30 | 3.37 | 3.32
2019-04-18 10:00 | 2.87 | 2.82
2019-04-18 10:30 | 2.53 | 2.48
2019-04-18 11:00 | 2.56 | 2.51
2019-04-18 11:30 | 2.44 | 2.38
2019-04-18 12:00 | 2.41 | 2.34
2019-04-18 12:30 | 2.96 | 2.91
2019-04-18 13:00 | 4.52 | 4.49
2019-04-18 13:30 | 4.44 | 4.41
2019-04-18 14:00 | 3.37 | 3.32
2019-04-18 14:30 | 4.42 | 4.39
2019-04-18 15:00 | 5.46 | 5.43
2019-04-18 15:30 | 6.04 | 6.02
2019-04-18 16:00 | 8.42 | 8.41
2019-04-18 16:30 | 7.98 | 7.96
2019-04-18 17:00 | 9.23 | 9.22
2019-04-18 17:30 | 9.54 | 9.53
2019-04-18 18:00 | 10.06 | 10.05
2019-04-18 18:30 | 10.58 | 10.57
2019-04-18 19:00 | 10.71 | 10.7
2019-04-18 19:30 | 10.48 | 10.46
2019-04-18 20:00 | 10.45 | 10.44
2019-04-18 20:30 | 10.3 | 10.29
2019-04-18 21:00 | 9.81 | 9.8
2019-04-18 21:30 | 9.19 | 9.18
2019-04-18 22:00 | 8.62 | 8.61
2019-04-18 22:30 | 8.35 | 8.33
2019-04-18 23:00 | 8.21 | 8.19
2019-04-18 23:30 | 7.33 | 7.3
2019-04-19 | 6.54 | 6.5
2019-04-19 00:30 | 5.84 | 5.79
2019-04-19 01:00 | 5.44 | 5.38
2019-04-19 01:30 | 5.1 | 5.03
2019-04-19 02:00 | 4.78 | 4.7
2019-04-19 02:30 | 4.66 | 4.58
2019-04-19 03:00 | 4.56 | 4.48
2019-04-19 03:30 | 4.47 | 4.39
2019-04-19 04:00 | 4.36 | 4.26
2019-04-19 04:30 | 4.41 | 4.31
2019-04-19 05:00 | 4.41 | 4.32
2019-04-19 05:30 | 4.49 | 4.4
2019-04-19 06:00 | 4.53 | 4.43
2019-04-19 06:30 | 4.67 | 4.5
2019-04-19 07:00 | 4.6 | 4.41
2019-04-19 07:30 | 4.5 | 4.32
2019-04-19 08:00 | 4.28 | 4.12
2019-04-19 08:30 | 4.04 | 3.91
2019-04-19 09:00 | 3.84 | 3.73
2019-04-19 09:30 | 4.82 | 4.76
2019-04-19 10:00 | 5.06 | 5.01
2019-04-19 10:30 | 6.14 | 6.1
2019-04-19 11:00 | 4.32 | 4.28
2019-04-19 11:30 | 4.88 | 4.86
2019-04-19 12:00 | 4.74 | 4.71
2019-04-19 12:30 | 5.29 | 5.26
2019-04-19 13:00 | 5.71 | 5.69
2019-04-19 13:30 | 4.63 | 4.6
2019-04-19 14:00 | 6.44 | 6.41
2019-04-19 14:30 | 6.67 | 6.64
2019-04-19 15:00 | 5.26 | 5.22
2019-04-19 15:30 | 6.46 | 6.42
2019-04-19 16:00 | 6.57 | 6.53
2019-04-19 16:30 | 7.48 | 7.45
2019-04-19 17:00 | 8.21 | 8.18
2019-04-19 17:30 | 9.31 | 9.28
2019-04-19 18:00 | 10.06 | 10.06
2019-04-19 18:30 | 10.32 | 10.32
2019-04-19 19:00 | 10.49 | 10.48
2019-04-19 19:30 | 10.05 | 10.05
2019-04-19 20:00 | 9.8 | 9.79
2019-04-19 20:30 | 9.69 | 9.68
2019-04-19 21:00 | 9.06 | 9.04
2019-04-19 21:30 | 8.53 | 8.51
2019-04-19 22:00 | 8.13 | 8.11
2019-04-19 22:30 | 7.98 | 7.96
2019-04-19 23:00 | 7.88 | 7.85
2019-04-19 23:30 | 7.04 | 7.01
2019-04-20 | 6.41 | 6.36
2019-04-20 00:30 | 5.83 | 5.78
2019-04-20 01:00 | 5.51 | 5.46
2019-04-20 01:30 | 5.13 | 5.07
2019-04-20 02:00 | 4.84 | 4.78
2019-04-20 02:30 | 4.74 | 4.67
2019-04-20 03:00 | 4.64 | 4.56
2019-04-20 03:30 | 4.56 | 4.49
2019-04-20 04:00 | 4.5 | 4.42
2019-04-20 04:30 | 4.45 | 4.37
2019-04-20 05:00 | 4.57 | 4.5
2019-04-20 05:30 | 4.64 | 4.57
2019-04-20 06:00 | 4.74 | 4.67
2019-04-20 06:30 | 4.82 | 4.69
2019-04-20 07:00 | 4.85 | 4.71
2019-04-20 07:30 | 5.02 | 4.91
2019-04-20 08:00 | 4.92 | 4.82
2019-04-20 08:30 | 5.05 | 4.98
2019-04-20 09:00 | 4.7 | 4.65
2019-04-20 09:30 | 5.08 | 5.05
2019-04-20 10:00 | 5.39 | 5.36
2019-04-20 10:30 | 4.91 | 4.88
2019-04-20 11:00 | 5.93 | 5.91
2019-04-20 11:30 | 7.9 | 7.88
2019-04-20 12:00 | 5.81 | 5.78
2019-04-20 12:30 | 5.71 | 5.68
2019-04-20 13:00 | 6.71 | 6.68
2019-04-20 13:30 | 5.73 | 5.7
2019-04-20 14:00 | 4.15 | 4.12
2019-04-20 14:30 | 7.58 | 7.57
2019-04-20 15:00 | 7.03 | 7.01
2019-04-20 15:30 | 6.44 | 6.42
2019-04-20 16:00 | 7.25 | 7.23
2019-04-20 16:30 | 7.98 | 7.96
2019-04-20 17:00 | 8.68 | 8.66
2019-04-20 17:30 | 9.41 | 9.39
2019-04-20 18:00 | 10.41 | 10.4
2019-04-20 18:30 | 10.87 | 10.86
2019-04-20 19:00 | 10.82 | 10.81
2019-04-20 19:30 | 10.23 | 10.23
2019-04-20 20:00 | 9.92 | 9.91
2019-04-20 20:30 | 9.87 | 9.86
2019-04-20 21:00 | 9.18 | 9.17
2019-04-20 21:30 | 8.53 | 8.52
2019-04-20 22:00 | 8.2 | 8.17
2019-04-20 22:30 | 8.01 | 7.99
2019-04-20 23:00 | 7.91 | 7.89
2019-04-20 23:30 | 7.32 | 7.29
2019-04-21 | 6.4 | 6.36
2019-04-21 00:30 | 5.83 | 5.78
2019-04-21 01:00 | 5.54 | 5.49
2019-04-21 01:30 | 5.3 | 5.25
2019-04-21 02:00 | 4.95 | 4.89
2019-04-21 02:30 | 4.83 | 4.76
2019-04-21 03:00 | 4.73 | 4.65
2019-04-21 03:30 | 4.67 | 4.6
2019-04-21 04:00 | 4.54 | 4.47
2019-04-21 04:30 | 4.53 | 4.45
2019-04-21 05:00 | 4.6 | 4.52
2019-04-21 05:30 | 4.67 | 4.6
2019-04-21 06:00 | 4.75 | 4.67
2019-04-21 06:30 | 4.87 | 4.73
2019-04-21 07:00 | 4.9 | 4.75
2019-04-21 07:30 | 4.93 | 4.82
2019-04-21 08:00 | 4.99 | 4.9
2019-04-21 08:30 | 4.82 | 4.75
2019-04-21 09:00 | 4.65 | 4.61
2019-04-21 09:30 | 4.37 | 4.34
2019-04-21 10:00 | 4.52 | 4.49
2019-04-21 10:30 | 4.81 | 4.78
2019-04-21 11:00 | 5.08 | 5.05
2019-04-21 11:30 | 6.97 | 6.94
2019-04-21 12:00 | 5.62 | 5.59
2019-04-21 12:30 | 4.57 | 4.54
2019-04-21 13:00 | 5.54 | 5.52
2019-04-21 13:30 | 5.01 | 4.98
2019-04-21 14:00 | 5.42 | 5.4
2019-04-21 14:30 | 5.25 | 5.22
2019-04-21 15:00 | 5.49 | 5.46
2019-04-21 15:30 | 5.88 | 5.86
2019-04-21 16:00 | 6.9 | 6.88
2019-04-21 16:30 | 7.98 | 7.96
2019-04-21 17:00 | 8.77 | 8.76
2019-04-21 17:30 | 9.69 | 9.68
2019-04-21 18:00 | 10.57 | 10.56
2019-04-21 18:30 | 10.65 | 10.64
2019-04-21 19:00 | 10.23 | 10.22
2019-04-21 19:30 | 9.88 | 9.88
2019-04-21 20:00 | 9.71 | 9.71
2019-04-21 20:30 | 9.55 | 9.54
2019-04-21 21:00 | 8.9 | 8.88
2019-04-21 21:30 | 8.49 | 8.47
2019-04-21 22:00 | 8.12 | 8.1
2019-04-21 22:30 | 7.87 | 7.84
2019-04-21 23:00 | 7.74 | 7.7
2019-04-21 23:30 | 6.9 | 6.85
2019-04-22 | 6.16 | 6.11
2019-04-22 00:30 | 5.7 | 5.64
2019-04-22 01:00 | 5.39 | 5.33
2019-04-22 01:30 | 5.12 | 5.05
2019-04-22 02:00 | 4.77 | 4.69
2019-04-22 02:30 | 4.64 | 4.56
2019-04-22 03:00 | 4.55 | 4.46
2019-04-22 03:30 | 4.53 | 4.44
2019-04-22 04:00 | 4.49 | 4.4
2019-04-22 04:30 | 4.55 | 4.47
2019-04-22 05:00 | 4.53 | 4.45
2019-04-22 05:30 | 4.6 | 4.51
2019-04-22 06:00 | 4.67 | 4.58
2019-04-22 06:30 | 4.72 | 4.56
2019-04-22 07:00 | 4.71 | 4.53
2019-04-22 07:30 | 4.51 | 4.35
2019-04-22 08:00 | 4.45 | 4.33
2019-04-22 08:30 | 4.94 | 4.85
2019-04-22 09:00 | 5.07 | 5
2019-04-22 09:30 | 4.54 | 4.48
2019-04-22 10:00 | 5.27 | 5.23
2019-04-22 10:30 | 4.21 | 4.18
2019-04-22 11:00 | 5.02 | 5
2019-04-22 11:30 | 5.97 | 5.95
2019-04-22 12:00 | 5.13 | 5.11
2019-04-22 12:30 | 5.94 | 5.92
2019-04-22 13:00 | 6 | 5.98
2019-04-22 13:30 | 7.08 | 7.07
2019-04-22 14:00 | 7.16 | 7.15
2019-04-22 14:30 | 6.82 | 6.8
2019-04-22 15:00 | 7.62 | 7.6
2019-04-22 15:30 | 8.04 | 8.02
2019-04-22 16:00 | 8.29 | 8.27
2019-04-22 16:30 | 9 | 8.98
2019-04-22 17:00 | 9.75 | 9.73
2019-04-22 17:30 | 10.75 | 10.74
2019-04-22 18:00 | 11.78 | 11.78
2019-04-22 18:30 | 12.07 | 12.07
2019-04-22 19:00 | 11.75 | 11.74
2019-04-22 19:30 | 11.09 | 11.08
2019-04-22 20:00 | 10.96 | 10.96
2019-04-22 20:30 | 10.66 | 10.65
2019-04-22 21:00 | 9.96 | 9.95
2019-04-22 21:30 | 9.12 | 9.11
2019-04-22 22:00 | 8.47 | 8.44
2019-04-22 22:30 | 8.04 | 8.02
2019-04-22 23:00 | 7.87 | 7.84
2019-04-22 23:30 | 6.98 | 6.95
2019-04-23 | 6.11 | 6.07
2019-04-23 00:30 | 5.47 | 5.41
2019-04-23 01:00 | 5.14 | 5.07
2019-04-23 01:30 | 4.91 | 4.84
2019-04-23 02:00 | 4.78 | 4.7
2019-04-23 02:30 | 4.64 | 4.56
2019-04-23 03:00 | 4.45 | 4.36
2019-04-23 03:30 | 4.49 | 4.4
2019-04-23 04:00 | 4.56 | 4.47
2019-04-23 04:30 | 4.68 | 4.6
2019-04-23 05:00 | 4.87 | 4.79
2019-04-23 05:30 | 5.34 | 5.28
2019-04-23 06:00 | 5.9 | 5.85
2019-04-23 06:30 | 6.5 | 6.44
2019-04-23 07:00 | 7.19 | 7.14
2019-04-23 07:30 | 7.25 | 7.21
2019-04-23 08:00 | 6.96 | 6.93
2019-04-23 08:30 | 6.08 | 6.05
2019-04-23 09:00 | 6.33 | 6.31
2019-04-23 09:30 | 5.58 | 5.56
2019-04-23 10:00 | 6.23 | 6.22
2019-04-23 10:30 | 6.32 | 6.31
2019-04-23 11:00 | 5.74 | 5.73
2019-04-23 11:30 | 5.96 | 5.95
2019-04-23 12:00 | 6.29 | 6.28
2019-04-23 12:30 | 5.08 | 5.07
2019-04-23 13:00 | 5.9 | 5.89
2019-04-23 13:30 | 5.58 | 5.57
2019-04-23 14:00 | 6.55 | 6.55
2019-04-23 14:30 | 6.86 | 6.85
2019-04-23 15:00 | 6.96 | 6.95
2019-04-23 15:30 | 7.89 | 7.88
2019-04-23 16:00 | 8.75 | 8.74
2019-04-23 16:30 | 9.49 | 9.48
2019-04-23 17:00 | 10.36 | 10.36
2019-04-23 17:30 | 11.35 | 11.35
2019-04-23 18:00 | 12.52 | 12.52
2019-04-23 18:30 | 12.77 | 12.77
2019-04-23 19:00 | 12.68 | 12.68
2019-04-23 19:30 | 11.93 | 11.93
2019-04-23 20:00 | 11.44 | 11.44
2019-04-23 20:30 | 11.24 | 11.24
2019-04-23 21:00 | 10.74 | 10.73
2019-04-23 21:30 | 9.84 | 9.83
2019-04-23 22:00 | 9.23 | 9.22
2019-04-23 22:30 | 8.68 | 8.66
2019-04-23 23:00 | 8.53 | 8.51
2019-04-23 23:30 | 7.61 | 7.58
2019-04-24 | 6.39 | 6.35
2019-04-24 00:30 | 5.62 | 5.57
2019-04-24 01:00 | 5.07 | 5
2019-04-24 01:30 | 4.88 | 4.8
2019-04-24 02:00 | 4.69 | 4.61
2019-04-24 02:30 | 4.55 | 4.46
2019-04-24 03:00 | 4.46 | 4.37
2019-04-24 03:30 | 4.42 | 4.32
2019-04-24 04:00 | 4.47 | 4.37
2019-04-24 04:30 | 4.66 | 4.57
2019-04-24 05:00 | 4.84 | 4.76
2019-04-24 05:30 | 5.32 | 5.26
2019-04-24 06:00 | 6 | 5.97
2019-04-24 06:30 | 6.48 | 6.41
2019-04-24 07:00 | 6.51 | 6.45
2019-04-24 07:30 | 6.5 | 6.45
2019-04-24 08:00 | 7.89 | 7.84
2019-04-24 08:30 | 7.66 | 7.59
2019-04-24 09:00 | 5.68 | 5.61
2019-04-24 09:30 | 6.32 | 6.28
2019-04-24 10:00 | 6.46 | 6.43
2019-04-24 10:30 | 5.62 | 5.6
2019-04-24 11:00 | 5.42 | 5.41
2019-04-24 11:30 | 5.99 | 5.98
2019-04-24 12:00 | 4.91 | 4.9
2019-04-24 12:30 | 5.88 | 5.87
2019-04-24 13:00 | 6.13 | 6.13
2019-04-24 13:30 | 7.31 | 7.3
2019-04-24 14:00 | 5.73 | 5.73
2019-04-24 14:30 | 6.13 | 6.13
2019-04-24 15:00 | 7.75 | 7.74
2019-04-24 15:30 | 8.59 | 8.59
2019-04-24 16:00 | 9 | 8.99
2019-04-24 16:30 | 8.93 | 8.93
2019-04-24 17:00 | 9.28 | 9.28
2019-04-24 17:30 | 10.39 | 10.39
2019-04-24 18:00 | 11.33 | 11.33
2019-04-24 18:30 | 11.75 | 11.74
2019-04-24 19:00 | 11.66 | 11.66
2019-04-24 19:30 | 11.2 | 11.19
2019-04-24 20:00 | 11.38 | 11.38
2019-04-24 20:30 | 11.24 | 11.24
2019-04-24 21:00 | 10.84 | 10.84
2019-04-24 21:30 | 10.36 | 10.36
2019-04-24 22:00 | 9.77 | 9.76
2019-04-24 22:30 | 9.43 | 9.42
2019-04-24 23:00 | 9 | 8.99
2019-04-24 23:30 | 7.82 | 7.8
2019-04-25 | 6.76 | 6.73
2019-04-25 00:30 | 5.82 | 5.76
2019-04-25 01:00 | 5.53 | 5.48
2019-04-25 01:30 | 5.22 | 5.15
2019-04-25 02:00 | 4.87 | 4.8
2019-04-25 02:30 | 4.72 | 4.64
2019-04-25 03:00 | 4.6 | 4.52
2019-04-25 03:30 | 4.55 | 4.47
2019-04-25 04:00 | 4.55 | 4.47
2019-04-25 04:30 | 4.58 | 4.49
2019-04-25 05:00 | 4.55 | 4.46
2019-04-25 05:30 | 4.65 | 4.56
2019-04-25 06:00 | 4.82 | 4.74
2019-04-25 06:30 | 4.78 | 4.65
2019-04-25 07:00 | 4.9 | 4.74
2019-04-25 07:30 | 4.91 | 4.76
2019-04-25 08:00 | 4.69 | 4.53
2019-04-25 08:30 | 4.57 | 4.44
2019-04-25 09:00 | 5.22 | 5.13
2019-04-25 09:30 | 5.32 | 5.25
2019-04-25 10:00 | 4.56 | 4.5
2019-04-25 10:30 | 4.98 | 4.94
2019-04-25 11:00 | 5.27 | 5.23
2019-04-25 11:30 | 5.44 | 5.41
2019-04-25 12:00 | 5.02 | 4.99
2019-04-25 12:30 | 4.6 | 4.58
2019-04-25 13:00 | 4.76 | 4.73
2019-04-25 13:30 | 4.75 | 4.73
2019-04-25 14:00 | 7.23 | 7.21
2019-04-25 14:30 | 7.78 | 7.75
2019-04-25 15:00 | 7.7 | 7.68
2019-04-25 15:30 | 7.64 | 7.62
2019-04-25 16:00 | 7.97 | 7.95
2019-04-25 16:30 | 8.48 | 8.46
2019-04-25 17:00 | 9.14 | 9.12
2019-04-25 17:30 | 9.92 | 9.91
2019-04-25 18:00 | 10.86 | 10.86
2019-04-25 18:30 | 11.15 | 11.15
2019-04-25 19:00 | 10.98 | 10.98
2019-04-25 19:30 | 10.49 | 10.49
2019-04-25 20:00 | 10.43 | 10.42
2019-04-25 20:30 | 10.32 | 10.32
2019-04-25 21:00 | 9.58 | 9.57
2019-04-25 21:30 | 8.96 | 8.94
2019-04-25 22:00 | 8.3 | 8.28
2019-04-25 22:30 | 7.94 | 7.92
2019-04-25 23:00 | 7.82 | 7.79
2019-04-25 23:30 | 6.94 | 6.9
2019-04-26 | 6.14 | 6.09
2019-04-26 00:30 | 5.57 | 5.52
2019-04-26 01:00 | 5.26 | 5.19
2019-04-26 01:30 | 4.95 | 4.88
2019-04-26 02:00 | 4.78 | 4.7
2019-04-26 02:30 | 4.57 | 4.49
2019-04-26 03:00 | 4.51 | 4.42
2019-04-26 03:30 | 4.53 | 4.44
2019-04-26 04:00 | 4.54 | 4.45
2019-04-26 04:30 | 4.64 | 4.56
2019-04-26 05:00 | 4.84 | 4.76
2019-04-26 05:30 | 5.19 | 5.13
2019-04-26 06:00 | 5.57 | 5.52
2019-04-26 06:30 | 6.04 | 5.96
2019-04-26 07:00 | 6.33 | 6.25
2019-04-26 07:30 | 6.4 | 6.34
2019-04-26 08:00 | 5.9 | 5.85
2019-04-26 08:30 | 4.8 | 4.74
2019-04-26 09:00 | 5.09 | 5.05
2019-04-26 09:30 | 3.97 | 3.94
2019-04-26 10:00 | 4.85 | 4.83
2019-04-26 10:30 | 4.8 | 4.78
2019-04-26 11:00 | 4.21 | 4.19
2019-04-26 11:30 | 4.5 | 4.48
2019-04-26 12:00 | 4.57 | 4.55
2019-04-26 12:30 | 4.56 | 4.54
2019-04-26 13:00 | 5.06 | 5.04
2019-04-26 13:30 | 3.94 | 3.92
2019-04-26 14:00 | 5.71 | 5.7
2019-04-26 14:30 | 4.94 | 4.93
2019-04-26 15:00 | 5.88 | 5.86
2019-04-26 15:30 | 6.25 | 6.24
2019-04-26 16:00 | 7.87 | 7.86
2019-04-26 16:30 | 8.4 | 8.38
2019-04-26 17:00 | 8.98 | 8.97
2019-04-26 17:30 | 9.93 | 9.91
2019-04-26 18:00 | 10.7 | 10.69
2019-04-26 18:30 | 11.13 | 11.12
2019-04-26 19:00 | 11.36 | 11.36
2019-04-26 19:30 | 10.85 | 10.84
2019-04-26 20:00 | 10.84 | 10.83
2019-04-26 20:30 | 10.65 | 10.64
2019-04-26 21:00 | 10.08 | 10.08
2019-04-26 21:30 | 9.36 | 9.35
2019-04-26 22:00 | 8.64 | 8.62
2019-04-26 22:30 | 8.39 | 8.37
2019-04-26 23:00 | 8.22 | 8.19
2019-04-26 23:30 | 7.34 | 7.31
2019-04-27 | 6.49 | 6.44
2019-04-27 00:30 | 5.81 | 5.75
2019-04-27 01:00 | 5.44 | 5.38
2019-04-27 01:30 | 5.19 | 5.12
2019-04-27 02:00 | 4.84 | 4.77
2019-04-27 02:30 | 4.73 | 4.65
2019-04-27 03:00 | 4.65 | 4.57
2019-04-27 03:30 | 4.6 | 4.51
2019-04-27 04:00 | 4.52 | 4.43
2019-04-27 04:30 | 4.5 | 4.41
2019-04-27 05:00 | 4.51 | 4.42
2019-04-27 05:30 | 4.75 | 4.67
2019-04-27 06:00 | 4.8 | 4.72
2019-04-27 06:30 | 4.88 | 4.74
2019-04-27 07:00 | 5.06 | 4.91
2019-04-27 07:30 | 5.11 | 4.99
2019-04-27 08:00 | 5.06 | 4.96
2019-04-27 08:30 | 4.89 | 4.81
2019-04-27 09:00 | 4.59 | 4.53
2019-04-27 09:30 | 4.11 | 4.07
2019-04-27 10:00 | 3.82 | 3.78
2019-04-27 10:30 | 3.68 | 3.64
2019-04-27 11:00 | 3.68 | 3.63
2019-04-27 11:30 | 3.81 | 3.77
2019-04-27 12:00 | 3.87 | 3.82
2019-04-27 12:30 | 4.19 | 4.15
2019-04-27 13:00 | 4.79 | 4.74
2019-04-27 13:30 | 5.91 | 5.88
2019-04-27 14:00 | 7.62 | 7.59
2019-04-27 14:30 | 5.97 | 5.94
2019-04-27 15:00 | 6.88 | 6.85
2019-04-27 15:30 | 7.81 | 7.79
2019-04-27 16:00 | 7.79 | 7.76
2019-04-27 16:30 | 8.67 | 8.66
2019-04-27 17:00 | 9.68 | 9.66
2019-04-27 17:30 | 10.35 | 10.34
2019-04-27 18:00 | 11.11 | 11.1
2019-04-27 18:30 | 11.22 | 11.22
2019-04-27 19:00 | 11.08 | 11.07
2019-04-27 19:30 | 10.58 | 10.58
2019-04-27 20:00 | 10.43 | 10.43
2019-04-27 20:30 | 10.26 | 10.25
2019-04-27 21:00 | 9.72 | 9.71
2019-04-27 21:30 | 9.14 | 9.13
2019-04-27 22:00 | 8.61 | 8.6
2019-04-27 22:30 | 8.24 | 8.21
2019-04-27 23:00 | 8.09 | 8.06
2019-04-27 23:30 | 7.32 | 7.29
2019-04-28 | 6.5 | 6.46
2019-04-28 00:30 | 5.92 | 5.87
2019-04-28 01:00 | 5.61 | 5.56
2019-04-28 01:30 | 5.3 | 5.25
2019-04-28 02:00 | 4.99 | 4.92
2019-04-28 02:30 | 4.84 | 4.77
2019-04-28 03:00 | 4.7 | 4.64
2019-04-28 03:30 | 4.6 | 4.52
2019-04-28 04:00 | 4.53 | 4.45
2019-04-28 04:30 | 4.59 | 4.5
2019-04-28 05:00 | 4.55 | 4.46
2019-04-28 05:30 | 4.55 | 4.46
2019-04-28 06:00 | 4.69 | 4.6
2019-04-28 06:30 | 4.74 | 4.59
2019-04-28 07:00 | 4.85 | 4.69
2019-04-28 07:30 | 4.76 | 4.62
2019-04-28 08:00 | 4.73 | 4.61
2019-04-28 08:30 | 4.64 | 4.55
2019-04-28 09:00 | 4.52 | 4.47
2019-04-28 09:30 | 4.34 | 4.31
2019-04-28 10:00 | 4.11 | 4.08
2019-04-28 10:30 | 4.03 | 4
2019-04-28 11:00 | 3.98 | 3.95
2019-04-28 11:30 | 4.04 | 4
2019-04-28 12:00 | 4.19 | 4.15
2019-04-28 12:30 | 4.51 | 4.48
2019-04-28 13:00 | 4.83 | 4.8
2019-04-28 13:30 | 5.13 | 5.1
2019-04-28 14:00 | 5.7 | 5.68
2019-04-28 14:30 | 6.33 | 6.3
2019-04-28 15:00 | 6.95 | 6.93
2019-04-28 15:30 | 7.77 | 7.75
2019-04-28 16:00 | 8.45 | 8.44
2019-04-28 16:30 | 9.52 | 9.5
2019-04-28 17:00 | 10.59 | 10.58
2019-04-28 17:30 | 11.55 | 11.54
2019-04-28 18:00 | 12.39 | 12.38
2019-04-28 18:30 | 12.48 | 12.47
2019-04-28 19:00 | 12.18 | 12.17
2019-04-28 19:30 | 11.52 | 11.52
2019-04-28 20:00 | 11.17 | 11.17
2019-04-28 20:30 | 10.91 | 10.9
2019-04-28 21:00 | 10.07 | 10.06
2019-04-28 21:30 | 9.34 | 9.33
2019-04-28 22:00 | 8.64 | 8.63
2019-04-28 22:30 | 8.18 | 8.15
2019-04-28 23:00 | 8 | 7.97
2019-04-28 23:30 | 7.15 | 7.12
2019-04-29 | 6.22 | 6.17
2019-04-29 00:30 | 5.55 | 5.5
2019-04-29 01:00 | 5.27 | 5.21
2019-04-29 01:30 | 4.98 | 4.91
2019-04-29 02:00 | 4.75 | 4.68
2019-04-29 02:30 | 4.63 | 4.55
2019-04-29 03:00 | 4.55 | 4.45
2019-04-29 03:30 | 4.56 | 4.47
2019-04-29 04:00 | 4.53 | 4.43
2019-04-29 04:30 | 4.81 | 4.73
2019-04-29 05:00 | 5 | 4.93
2019-04-29 05:30 | 5.3 | 5.23
2019-04-29 06:00 | 5.79 | 5.74
2019-04-29 06:30 | 6.38 | 6.32
2019-04-29 07:00 | 6.94 | 6.87
2019-04-29 07:30 | 6.97 | 6.92
2019-04-29 08:00 | 6.23 | 6.18
2019-04-29 08:30 | 6.28 | 6.24
2019-04-29 09:00 | 5.24 | 5.21
2019-04-29 09:30 | 5.12 | 5.1
2019-04-29 10:00 | 5.78 | 5.76
2019-04-29 10:30 | 6.12 | 6.11
2019-04-29 11:00 | 4.95 | 4.94
2019-04-29 11:30 | 4.65 | 4.64
2019-04-29 12:00 | 6.2 | 6.19
2019-04-29 12:30 | 5.04 | 5.03
2019-04-29 13:00 | 4.44 | 4.43
2019-04-29 13:30 | 4.53 | 4.52
2019-04-29 14:00 | 4.32 | 4.32
2019-04-29 14:30 | 5.03 | 5.02
2019-04-29 15:00 | 6.34 | 6.33
2019-04-29 15:30 | 6.46 | 6.45
2019-04-29 16:00 | 8.44 | 8.44
2019-04-29 16:30 | 9.07 | 9.06
2019-04-29 17:00 | 10.07 | 10.06
2019-04-29 17:30 | 10.95 | 10.95
2019-04-29 18:00 | 12.17 | 12.16
2019-04-29 18:30 | 12.45 | 12.45
2019-04-29 19:00 | 12.47 | 12.47
2019-04-29 19:30 | 11.96 | 11.96
2019-04-29 20:00 | 11.79 | 11.78
2019-04-29 20:30 | 11.46 | 11.45
2019-04-29 21:00 | 10.9 | 10.9
2019-04-29 21:30 | 9.78 | 9.77
2019-04-29 22:00 | 8.8 | 8.78
2019-04-29 22:30 | 7.98 | 7.96
2019-04-29 23:00 | 7.68 | 7.65
2019-04-29 23:30 | 6.86 | 6.82
2019-04-30 | 6 | 5.95
2019-04-30 00:30 | 5.37 | 5.3
2019-04-30 01:00 | 5.07 | 5
2019-04-30 01:30 | 4.86 | 4.78
2019-04-30 02:00 | 4.57 | 4.48
2019-04-30 02:30 | 4.49 | 4.39
2019-04-30 03:00 | 4.4 | 4.3
2019-04-30 03:30 | 4.39 | 4.29
2019-04-30 04:00 | 4.38 | 4.27
2019-04-30 04:30 | 4.55 | 4.46
2019-04-30 05:00 | 4.75 | 4.65
2019-04-30 05:30 | 5.17 | 5.1
2019-04-30 06:00 | 5.59 | 5.53
2019-04-30 06:30 | 5.9 | 5.82
2019-04-30 07:00 | 6.77 | 6.69
2019-04-30 07:30 | 6.94 | 6.88
2019-04-30 08:00 | 6.63 | 6.57
2019-04-30 08:30 | 5.21 | 5.14
2019-04-30 09:00 | 4.13 | 4.08
2019-04-30 09:30 | 4.6 | 4.57
2019-04-30 10:00 | 4.9 | 4.87
2019-04-30 10:30 | 3.17 | 3.15
2019-04-30 11:00 | 5.9 | 5.88
2019-04-30 11:30 | 5.37 | 5.35
2019-04-30 12:00 | 5.38 | 5.36
2019-04-30 12:30 | 7.27 | 7.26
2019-04-30 13:00 | 7.17 | 7.15
2019-04-30 13:30 | 6.3 | 6.29
2019-04-30 14:00 | 6.12 | 6.1
2019-04-30 14:30 | 5.7 | 5.68
2019-04-30 15:00 | 7.36 | 7.34
2019-04-30 15:30 | 7.46 | 7.45
2019-04-30 16:00 | 7.84 | 7.83
2019-04-30 16:30 | 9.04 | 9.03
2019-04-30 17:00 | 10.29 | 10.29
2019-04-30 17:30 | 11.46 | 11.46
2019-04-30 18:00 | 12.32 | 12.32
2019-04-30 18:30 | 12.21 | 12.21
2019-04-30 19:00 | 12.33 | 12.32
2019-04-30 19:30 | 12.01 | 12.01
2019-04-30 20:00 | 11.82 | 11.81
2019-04-30 20:30 | 11.6 | 11.6
2019-04-30 21:00 | 11.12 | 11.12
2019-04-30 21:30 | 10.05 | 10.04
2019-04-30 22:00 | 8.98 | 8.97
2019-04-30 22:30 | 8.23 | 8.21
2019-04-30 23:00 | 7.82 | 7.79
2019-04-30 23:30 | 6.89 | 6.85
2019-05-01 | 6.02 | 5.98
2019-05-01 00:30 | 5.35 | 5.28
2019-05-01 01:00 | 5.07 | 4.99
2019-05-01 01:30 | 4.9 | 4.82
2019-05-01 02:00 | 4.61 | 4.53
2019-05-01 02:30 | 4.56 | 4.47
2019-05-01 03:00 | 4.44 | 4.36
2019-05-01 03:30 | 4.54 | 4.46
2019-05-01 04:00 | 4.54 | 4.45
2019-05-01 04:30 | 4.67 | 4.59
2019-05-01 05:00 | 4.95 | 4.89
2019-05-01 05:30 | 5.5 | 5.45
2019-05-01 06:00 | 6.07 | 6.04
2019-05-01 06:30 | 6.53 | 6.47
2019-05-01 07:00 | 7.22 | 7.18
2019-05-01 07:30 | 7.91 | 7.87
2019-05-01 08:00 | 8.38 | 8.33
2019-05-01 08:30 | 6.93 | 6.89
2019-05-01 09:00 | 6.88 | 6.85
2019-05-01 09:30 | 6.11 | 6.09
2019-05-01 10:00 | 6.07 | 6.04
2019-05-01 10:30 | 5.58 | 5.56
2019-05-01 11:00 | 6.07 | 6.06
2019-05-01 11:30 | 7.22 | 7.21
2019-05-01 12:00 | 6.24 | 6.23
2019-05-01 12:30 | 7.39 | 7.38
2019-05-01 13:00 | 7.19 | 7.17
2019-05-01 13:30 | 5.98 | 5.97
2019-05-01 14:00 | 5.12 | 5.12
2019-05-01 14:30 | 5.93 | 5.93
2019-05-01 15:00 | 6.43 | 6.42
2019-05-01 15:30 | 7.11 | 7.11
2019-05-01 16:00 | 7.62 | 7.61
2019-05-01 16:30 | 8.49 | 8.49
2019-05-01 17:00 | 9.62 | 9.61
2019-05-01 17:30 | 10.7 | 10.7
2019-05-01 18:00 | 11.8 | 11.8
2019-05-01 18:30 | 12.44 | 12.44
2019-05-01 19:00 | 12.49 | 12.49
2019-05-01 19:30 | 11.96 | 11.95
2019-05-01 20:00 | 11.95 | 11.95
2019-05-01 20:30 | 11.83 | 11.83
2019-05-01 21:00 | 11.19 | 11.18
2019-05-01 21:30 | 10.3 | 10.3
2019-05-01 22:00 | 9.08 | 9.07
2019-05-01 22:30 | 8.36 | 8.34
2019-05-01 23:00 | 7.92 | 7.89
2019-05-01 23:30 | 6.98 | 6.95
2019-05-02 | 6.07 | 6.03
2019-05-02 00:30 | 5.51 | 5.45
2019-05-02 01:00 | 5.15 | 5.09
2019-05-02 01:30 | 4.94 | 4.87
2019-05-02 02:00 | 4.7 | 4.63
2019-05-02 02:30 | 4.67 | 4.59
2019-05-02 03:00 | 4.44 | 4.36
2019-05-02 03:30 | 4.49 | 4.41
2019-05-02 04:00 | 4.53 | 4.45
2019-05-02 04:30 | 4.7 | 4.62
2019-05-02 05:00 | 4.93 | 4.86
2019-05-02 05:30 | 5.33 | 5.28
2019-05-02 06:00 | 5.7 | 5.65
2019-05-02 06:30 | 6.42 | 6.36
2019-05-02 07:00 | 6.95 | 6.88
2019-05-02 07:30 | 6.58 | 6.53
2019-05-02 08:00 | 6.27 | 6.23
2019-05-02 08:30 | 5.82 | 5.79
2019-05-02 09:00 | 4.65 | 4.63
2019-05-02 09:30 | 4.77 | 4.75
2019-05-02 10:00 | 3.56 | 3.54
2019-05-02 10:30 | 4.19 | 4.18
2019-05-02 11:00 | 5.77 | 5.76
2019-05-02 11:30 | 6.22 | 6.21
2019-05-02 12:00 | 6.09 | 6.08
2019-05-02 12:30 | 5.68 | 5.67
2019-05-02 13:00 | 5.02 | 5
2019-05-02 13:30 | 5.73 | 5.73
2019-05-02 14:00 | 5.78 | 5.77
2019-05-02 14:30 | 6.22 | 6.21
2019-05-02 15:00 | 6.8 | 6.8
2019-05-02 15:30 | 7.65 | 7.64
2019-05-02 16:00 | 7.26 | 7.26
2019-05-02 16:30 | 8.5 | 8.49
2019-05-02 17:00 | 9.38 | 9.37
2019-05-02 17:30 | 10.61 | 10.61
2019-05-02 18:00 | 11.61 | 11.61
2019-05-02 18:30 | 12.03 | 12.03
2019-05-02 19:00 | 12.35 | 12.35
2019-05-02 19:30 | 12.01 | 12.01
2019-05-02 20:00 | 11.77 | 11.77
2019-05-02 20:30 | 11.55 | 11.55
2019-05-02 21:00 | 10.95 | 10.94
2019-05-02 21:30 | 10.23 | 10.23
2019-05-02 22:00 | 9.29 | 9.28
2019-05-02 22:30 | 8.55 | 8.53
2019-05-02 23:00 | 8.15 | 8.13
2019-05-02 23:30 | 7.15 | 7.12
2019-05-03 | 6.25 | 6.2
2019-05-03 00:30 | 5.53 | 5.47
2019-05-03 01:00 | 5.28 | 5.21
2019-05-03 01:30 | 4.98 | 4.9
2019-05-03 02:00 | 4.61 | 4.53
2019-05-03 02:30 | 4.67 | 4.59
2019-05-03 03:00 | 4.5 | 4.42
2019-05-03 03:30 | 4.53 | 4.44
2019-05-03 04:00 | 4.58 | 4.49
2019-05-03 04:30 | 4.75 | 4.66
2019-05-03 05:00 | 5.01 | 4.93
2019-05-03 05:30 | 5.31 | 5.24
2019-05-03 06:00 | 5.97 | 5.92
2019-05-03 06:30 | 6.8 | 6.74
2019-05-03 07:00 | 7.01 | 6.94
2019-05-03 07:30 | 7.36 | 7.31
2019-05-03 08:00 | 6.82 | 6.77
2019-05-03 08:30 | 6.02 | 5.98
2019-05-03 09:00 | 5.71 | 5.67
2019-05-03 09:30 | 5.82 | 5.8
2019-05-03 10:00 | 4.86 | 4.85
2019-05-03 10:30 | 4.73 | 4.71
2019-05-03 11:00 | 4.16 | 4.14
2019-05-03 11:30 | 4.81 | 4.79
2019-05-03 12:00 | 4.86 | 4.84
2019-05-03 12:30 | 5.61 | 5.59
2019-05-03 13:00 | 6.83 | 6.81
2019-05-03 13:30 | 5.63 | 5.62
2019-05-03 14:00 | 5.7 | 5.69
2019-05-03 14:30 | 5.04 | 5.03
2019-05-03 15:00 | 6.16 | 6.15
2019-05-03 15:30 | 6.94 | 6.93
2019-05-03 16:00 | 8.01 | 8
2019-05-03 16:30 | 8.67 | 8.66
2019-05-03 17:00 | 9.49 | 9.48
2019-05-03 17:30 | 10.34 | 10.34
2019-05-03 18:00 | 11 | 10.99
2019-05-03 18:30 | 11 | 10.99
2019-05-03 19:00 | 11.15 | 11.14
2019-05-03 19:30 | 10.68 | 10.68
2019-05-03 20:00 | 10.68 | 10.68
2019-05-03 20:30 | 10.59 | 10.58
2019-05-03 21:00 | 10.26 | 10.25
2019-05-03 21:30 | 9.4 | 9.4
2019-05-03 22:00 | 8.84 | 8.83
2019-05-03 22:30 | 8.59 | 8.57
2019-05-03 23:00 | 8.32 | 8.3
2019-05-03 23:30 | 7.42 | 7.4
2019-05-04 | 6.63 | 6.6
2019-05-04 00:30 | 6.02 | 5.98
2019-05-04 01:00 | 5.69 | 5.65
2019-05-04 01:30 | 5.34 | 5.29
2019-05-04 02:00 | 5.05 | 5
2019-05-04 02:30 | 5 | 4.95
2019-05-04 03:00 | 4.81 | 4.76
2019-05-04 03:30 | 4.74 | 4.68
2019-05-04 04:00 | 4.68 | 4.62
2019-05-04 04:30 | 4.68 | 4.61
2019-05-04 05:00 | 4.7 | 4.64
2019-05-04 05:30 | 4.88 | 4.83
2019-05-04 06:00 | 5.09 | 5.03
2019-05-04 06:30 | 5.24 | 5.17
2019-05-04 07:00 | 5.45 | 5.34
2019-05-04 07:30 | 5.92 | 5.83
2019-05-04 08:00 | 6.16 | 6.09
2019-05-04 08:30 | 6.61 | 6.55
2019-05-04 09:00 | 6.75 | 6.71
2019-05-04 09:30 | 6.91 | 6.89
2019-05-04 10:00 | 7.26 | 7.24
2019-05-04 10:30 | 6.77 | 6.75
2019-05-04 11:00 | 6.78 | 6.76
2019-05-04 11:30 | 6.74 | 6.72
2019-05-04 12:00 | 7.42 | 7.41
2019-05-04 12:30 | 7.89 | 7.88
2019-05-04 13:00 | 7.32 | 7.3
2019-05-04 13:30 | 8.04 | 8.02
2019-05-04 14:00 | 9.05 | 9.04
2019-05-04 14:30 | 8.25 | 8.23
2019-05-04 15:00 | 7.91 | 7.89
2019-05-04 15:30 | 8 | 7.98
2019-05-04 16:00 | 8.11 | 8.08
2019-05-04 16:30 | 8.72 | 8.7
2019-05-04 17:00 | 9.37 | 9.35
2019-05-04 17:30 | 9.99 | 9.98
2019-05-04 18:00 | 10.68 | 10.68
2019-05-04 18:30 | 10.73 | 10.73
2019-05-04 19:00 | 10.71 | 10.7
2019-05-04 19:30 | 10.32 | 10.32
2019-05-04 20:00 | 10.1 | 10.09
2019-05-04 20:30 | 10.02 | 10.01
2019-05-04 21:00 | 9.43 | 9.42
2019-05-04 21:30 | 8.86 | 8.84
2019-05-04 22:00 | 8.39 | 8.36
2019-05-04 22:30 | 8.01 | 7.97
2019-05-04 23:00 | 7.92 | 7.88
2019-05-04 23:30 | 7.17 | 7.13
2019-05-05 | 6.36 | 6.3
2019-05-05 00:30 | 5.71 | 5.64
2019-05-05 01:00 | 5.35 | 5.27
2019-05-05 01:30 | 5.07 | 4.98
2019-05-05 02:00 | 4.75 | 4.66
2019-05-05 02:30 | 4.57 | 4.48
2019-05-05 03:00 | 4.41 | 4.31
2019-05-05 03:30 | 4.44 | 4.33
2019-05-05 04:00 | 4.43 | 4.32
2019-05-05 04:30 | 4.32 | 4.2
2019-05-05 05:00 | 4.37 | 4.25
2019-05-05 05:30 | 4.56 | 4.45
2019-05-05 06:00 | 4.64 | 4.54
2019-05-05 06:30 | 4.82 | 4.66
2019-05-05 07:00 | 4.95 | 4.77
2019-05-05 07:30 | 5.02 | 4.87
2019-05-05 08:00 | 4.94 | 4.8
2019-05-05 08:30 | 4.83 | 4.7
2019-05-05 09:00 | 4.38 | 4.27
2019-05-05 09:30 | 4.15 | 4.05
2019-05-05 10:00 | 3.81 | 3.71
2019-05-05 10:30 | 3.27 | 3.18
2019-05-05 11:00 | 3.01 | 2.92
2019-05-05 11:30 | 2.76 | 2.69
2019-05-05 12:00 | 2.78 | 2.72
2019-05-05 12:30 | 2.87 | 2.82
2019-05-05 13:00 | 2.96 | 2.9
2019-05-05 13:30 | 3.23 | 3.19
2019-05-05 14:00 | 3.62 | 3.57
2019-05-05 14:30 | 4 | 3.95
2019-05-05 15:00 | 4.64 | 4.59
2019-05-05 15:30 | 5.44 | 5.4
2019-05-05 16:00 | 6.17 | 6.13
2019-05-05 16:30 | 7.22 | 7.18
2019-05-05 17:00 | 8.47 | 8.44
2019-05-05 17:30 | 9.41 | 9.39
2019-05-05 18:00 | 10.5 | 10.5
2019-05-05 18:30 | 10.61 | 10.61
2019-05-05 19:00 | 10.43 | 10.42
2019-05-05 19:30 | 10.05 | 10.04
2019-05-05 20:00 | 9.76 | 9.75
2019-05-05 20:30 | 9.67 | 9.65
2019-05-05 21:00 | 9.03 | 9.01
2019-05-05 21:30 | 8.64 | 8.61
2019-05-05 22:00 | 8.17 | 8.13
2019-05-05 22:30 | 7.95 | 7.91
2019-05-05 23:00 | 7.72 | 7.67
2019-05-05 23:30 | 6.98 | 6.93
2019-05-06 | 6.06 | 5.99
2019-05-06 00:30 | 5.63 | 5.55
2019-05-06 01:00 | 5.29 | 5.21
2019-05-06 01:30 | 4.97 | 4.88
2019-05-06 02:00 | 4.65 | 4.54
2019-05-06 02:30 | 4.5 | 4.39
2019-05-06 03:00 | 4.43 | 4.31
2019-05-06 03:30 | 4.32 | 4.2
2019-05-06 04:00 | 4.23 | 4.11
2019-05-06 04:30 | 4.26 | 4.13
2019-05-06 05:00 | 4.27 | 4.14
2019-05-06 05:30 | 4.39 | 4.27
2019-05-06 06:00 | 4.56 | 4.44
2019-05-06 06:30 | 4.68 | 4.49
2019-05-06 07:00 | 4.8 | 4.6
2019-05-06 07:30 | 4.66 | 4.47
2019-05-06 08:00 | 4.52 | 4.33
2019-05-06 08:30 | 4.35 | 4.2
2019-05-06 09:00 | 4.03 | 3.88
2019-05-06 09:30 | 3.78 | 3.66
2019-05-06 10:00 | 3.63 | 3.52
2019-05-06 10:30 | 3.48 | 3.38
2019-05-06 11:00 | 3.19 | 3.09
2019-05-06 11:30 | 2.87 | 2.77
2019-05-06 12:00 | 2.8 | 2.71
2019-05-06 12:30 | 2.92 | 2.84
2019-05-06 13:00 | 3.13 | 3.07
2019-05-06 13:30 | 3.39 | 3.34
2019-05-06 14:00 | 3.76 | 3.69
2019-05-06 14:30 | 4.25 | 4.2
2019-05-06 15:00 | 4.68 | 4.62
2019-05-06 15:30 | 5.63 | 5.58
2019-05-06 16:00 | 6.45 | 6.4
2019-05-06 16:30 | 7.7 | 7.66
2019-05-06 17:00 | 9.22 | 9.19
2019-05-06 17:30 | 10.69 | 10.67
2019-05-06 18:00 | 11.83 | 11.83
2019-05-06 18:30 | 11.76 | 11.76
2019-05-06 19:00 | 11.53 | 11.53
2019-05-06 19:30 | 11.08 | 11.08
2019-05-06 20:00 | 10.84 | 10.83
2019-05-06 20:30 | 10.6 | 10.59
2019-05-06 21:00 | 9.67 | 9.65
2019-05-06 21:30 | 9.03 | 9.01
2019-05-06 22:00 | 8.39 | 8.36
2019-05-06 22:30 | 7.85 | 7.81
2019-05-06 23:00 | 7.49 | 7.45
2019-05-06 23:30 | 6.71 | 6.65
2019-05-07 | 6 | 5.94
2019-05-07 00:30 | 5.32 | 5.23
2019-05-07 01:00 | 5.02 | 4.93
2019-05-07 01:30 | 4.78 | 4.68
2019-05-07 02:00 | 4.48 | 4.37
2019-05-07 02:30 | 4.34 | 4.23
2019-05-07 03:00 | 4.3 | 4.18
2019-05-07 03:30 | 4.37 | 4.26
2019-05-07 04:00 | 4.41 | 4.3
2019-05-07 04:30 | 4.61 | 4.5
2019-05-07 05:00 | 4.85 | 4.76
2019-05-07 05:30 | 5.45 | 5.38
2019-05-07 06:00 | 6.37 | 6.33
2019-05-07 06:30 | 7.08 | 7.02
2019-05-07 07:00 | 7.74 | 7.69
2019-05-07 07:30 | 7.58 | 7.53
2019-05-07 08:00 | 6.89 | 6.84
2019-05-07 08:30 | 5.53 | 5.48
2019-05-07 09:00 | 4.4 | 4.34
2019-05-07 09:30 | 3.74 | 3.68
2019-05-07 10:00 | 3.1 | 3.04
2019-05-07 10:30 | 2.53 | 2.46
2019-05-07 11:00 | 2.23 | 2.16
2019-05-07 11:30 | 2.15 | 2.1
2019-05-07 12:00 | 2.23 | 2.19
2019-05-07 12:30 | 2.33 | 2.31
2019-05-07 13:00 | 2.53 | 2.51
2019-05-07 13:30 | 2.74 | 2.73
2019-05-07 14:00 | 3.23 | 3.22
2019-05-07 14:30 | 3.78 | 3.77
2019-05-07 15:00 | 4.52 | 4.51
2019-05-07 15:30 | 5.41 | 5.4
2019-05-07 16:00 | 6.6 | 6.59
2019-05-07 16:30 | 7.91 | 7.9
2019-05-07 17:00 | 9.3 | 9.29
2019-05-07 17:30 | 10.58 | 10.58
2019-05-07 18:00 | 11.74 | 11.74
2019-05-07 18:30 | 12.18 | 12.18
2019-05-07 19:00 | 12.45 | 12.45
2019-05-07 19:30 | 11.98 | 11.98
2019-05-07 20:00 | 11.72 | 11.72
2019-05-07 20:30 | 11.6 | 11.6
2019-05-07 21:00 | 10.89 | 10.89
2019-05-07 21:30 | 9.76 | 9.75
2019-05-07 22:00 | 8.8 | 8.79
2019-05-07 22:30 | 8.07 | 8.04
2019-05-07 23:00 | 7.69 | 7.66
2019-05-07 23:30 | 6.85 | 6.81
2019-05-08 | 6.06 | 6
2019-05-08 00:30 | 5.43 | 5.36
2019-05-08 01:00 | 5.07 | 4.99
2019-05-08 01:30 | 4.85 | 4.76
2019-05-08 02:00 | 4.59 | 4.49
2019-05-08 02:30 | 4.51 | 4.42
2019-05-08 03:00 | 4.4 | 4.29
2019-05-08 03:30 | 4.47 | 4.37
2019-05-08 04:00 | 4.51 | 4.4
2019-05-08 04:30 | 4.73 | 4.64
2019-05-08 05:00 | 4.99 | 4.91
2019-05-08 05:30 | 5.49 | 5.42
2019-05-08 06:00 | 6.14 | 6.09
2019-05-08 06:30 | 6.65 | 6.59
2019-05-08 07:00 | 7.21 | 7.14
2019-05-08 07:30 | 7.06 | 7
2019-05-08 08:00 | 6.27 | 6.21
2019-05-08 08:30 | 4.99 | 4.91
2019-05-08 09:00 | 3.94 | 3.86
2019-05-08 09:30 | 3.21 | 3.12
2019-05-08 10:00 | 2.63 | 2.54
2019-05-08 10:30 | 2.23 | 2.15
2019-05-08 11:00 | 1.93 | 1.85
2019-05-08 11:30 | 1.82 | 1.76
2019-05-08 12:00 | 1.81 | 1.76
2019-05-08 12:30 | 2.1 | 2.06
2019-05-08 13:00 | 2.08 | 2.05
2019-05-08 13:30 | 2.79 | 2.78
2019-05-08 14:00 | 3.32 | 3.31
2019-05-08 14:30 | 3.82 | 3.81
2019-05-08 15:00 | 4.57 | 4.57
2019-05-08 15:30 | 5.51 | 5.5
2019-05-08 16:00 | 6.75 | 6.74
2019-05-08 16:30 | 7.94 | 7.93
2019-05-08 17:00 | 9.28 | 9.27
2019-05-08 17:30 | 10.37 | 10.36
2019-05-08 18:00 | 11.54 | 11.53
2019-05-08 18:30 | 11.8 | 11.79
2019-05-08 19:00 | 12.15 | 12.15
2019-05-08 19:30 | 11.69 | 11.69
2019-05-08 20:00 | 11.53 | 11.53
2019-05-08 20:30 | 11.59 | 11.59
2019-05-08 21:00 | 10.91 | 10.91
2019-05-08 21:30 | 10.25 | 10.24
2019-05-08 22:00 | 9.32 | 9.3
2019-05-08 22:30 | 8.41 | 8.39
2019-05-08 23:00 | 7.86 | 7.83
2019-05-08 23:30 | 7.04 | 7
2019-05-09 | 6.15 | 6.1
2019-05-09 00:30 | 5.52 | 5.45
2019-05-09 01:00 | 5.19 | 5.12
2019-05-09 01:30 | 4.86 | 4.77
2019-05-09 02:00 | 4.62 | 4.53
2019-05-09 02:30 | 4.53 | 4.42
2019-05-09 03:00 | 4.44 | 4.34
2019-05-09 03:30 | 4.5 | 4.39
2019-05-09 04:00 | 4.56 | 4.46
2019-05-09 04:30 | 4.79 | 4.69
2019-05-09 05:00 | 5.14 | 5.06
2019-05-09 05:30 | 5.7 | 5.64
2019-05-09 06:00 | 6.45 | 6.4
2019-05-09 06:30 | 7.27 | 7.21
2019-05-09 07:00 | 8.14 | 8.08
2019-05-09 07:30 | 8.05 | 8
2019-05-09 08:00 | 7.25 | 7.21
2019-05-09 08:30 | 5.84 | 5.79
2019-05-09 09:00 | 4.99 | 4.93
2019-05-09 09:30 | 4.13 | 4.07
2019-05-09 10:00 | 3.47 | 3.41
2019-05-09 10:30 | 2.89 | 2.83
2019-05-09 11:00 | 2.6 | 2.53
2019-05-09 11:30 | 2.11 | 2.03
2019-05-09 12:00 | 1.84 | 1.79
2019-05-09 12:30 | 2.04 | 2
2019-05-09 13:00 | 2.35 | 2.33
2019-05-09 13:30 | 2.72 | 2.7
2019-05-09 14:00 | 3.31 | 3.29
2019-05-09 14:30 | 3.82 | 3.8
2019-05-09 15:00 | 4.52 | 4.51
2019-05-09 15:30 | 5.33 | 5.32
2019-05-09 16:00 | 6.43 | 6.42
2019-05-09 16:30 | 7.99 | 7.98
2019-05-09 17:00 | 9.15 | 9.14
2019-05-09 17:30 | 10.3 | 10.3
2019-05-09 18:00 | 11.45 | 11.44
2019-05-09 18:30 | 11.47 | 11.46
2019-05-09 19:00 | 11.74 | 11.74
2019-05-09 19:30 | 11.55 | 11.55
2019-05-09 20:00 | 11.55 | 11.55
2019-05-09 20:30 | 11.53 | 11.53
2019-05-09 21:00 | 10.85 | 10.85
2019-05-09 21:30 | 10.18 | 10.17
2019-05-09 22:00 | 9.18 | 9.17
2019-05-09 22:30 | 8.34 | 8.32
2019-05-09 23:00 | 7.9 | 7.87
2019-05-09 23:30 | 6.94 | 6.9
2019-05-10 | 6.01 | 5.95
2019-05-10 00:30 | 5.38 | 5.31
2019-05-10 01:00 | 5.13 | 5.05
2019-05-10 01:30 | 4.82 | 4.74
2019-05-10 02:00 | 4.57 | 4.48
2019-05-10 02:30 | 4.5 | 4.41
2019-05-10 03:00 | 4.4 | 4.3
2019-05-10 03:30 | 4.49 | 4.39
2019-05-10 04:00 | 4.52 | 4.41
2019-05-10 04:30 | 4.64 | 4.56
2019-05-10 05:00 | 5.03 | 4.95
2019-05-10 05:30 | 5.45 | 5.39
2019-05-10 06:00 | 6.23 | 6.2
2019-05-10 06:30 | 6.89 | 6.84
2019-05-10 07:00 | 7.53 | 7.48
2019-05-10 07:30 | 7.79 | 7.75
2019-05-10 08:00 | 6.73 | 6.68
2019-05-10 08:30 | 6.4 | 6.35
2019-05-10 09:00 | 5 | 4.94
2019-05-10 09:30 | 5.07 | 5.02
2019-05-10 10:00 | 4.33 | 4.29
2019-05-10 10:30 | 3.53 | 3.49
2019-05-10 11:00 | 3.61 | 3.57
2019-05-10 11:30 | 2.36 | 2.32
2019-05-10 12:00 | 2.11 | 2.08
2019-05-10 12:30 | 2.45 | 2.42
2019-05-10 13:00 | 3.11 | 3.08
2019-05-10 13:30 | 3.97 | 3.95
2019-05-10 14:00 | 4.55 | 4.53
2019-05-10 14:30 | 4.8 | 4.78
2019-05-10 15:00 | 5.39 | 5.38
2019-05-10 15:30 | 7.24 | 7.23
2019-05-10 16:00 | 7.3 | 7.28
2019-05-10 16:30 | 8.06 | 8.04
2019-05-10 17:00 | 8.98 | 8.97
2019-05-10 17:30 | 9.95 | 9.94
2019-05-10 18:00 | 10.93 | 10.91
2019-05-10 18:30 | 11.29 | 11.28
2019-05-10 19:00 | 11.09 | 11.08
2019-05-10 19:30 | 10.83 | 10.82
2019-05-10 20:00 | 10.73 | 10.72
2019-05-10 20:30 | 10.54 | 10.53
2019-05-10 21:00 | 9.84 | 9.83
2019-05-10 21:30 | 9.33 | 9.32
2019-05-10 22:00 | 8.58 | 8.56
2019-05-10 22:30 | 8.34 | 8.31
2019-05-10 23:00 | 8.17 | 8.14
2019-05-10 23:30 | 7.36 | 7.33
2019-05-11 | 6.49 | 6.44
2019-05-11 00:30 | 5.74 | 5.68
2019-05-11 01:00 | 5.35 | 5.28
2019-05-11 01:30 | 5.1 | 5.02
2019-05-11 02:00 | 4.74 | 4.64
2019-05-11 02:30 | 4.66 | 4.57
2019-05-11 03:00 | 4.6 | 4.5
2019-05-11 03:30 | 4.5 | 4.4
2019-05-11 04:00 | 4.58 | 4.48
2019-05-11 04:30 | 4.62 | 4.52
2019-05-11 05:00 | 4.61 | 4.51
2019-05-11 05:30 | 4.77 | 4.67
2019-05-11 06:00 | 4.89 | 4.8
2019-05-11 06:30 | 5.2 | 5.08
2019-05-11 07:00 | 5.59 | 5.45
2019-05-11 07:30 | 5.52 | 5.39
2019-05-11 08:00 | 5.48 | 5.37
2019-05-11 08:30 | 5.13 | 5.03
2019-05-11 09:00 | 4.87 | 4.79
2019-05-11 09:30 | 4.26 | 4.19
2019-05-11 10:00 | 3.8 | 3.72
2019-05-11 10:30 | 3.18 | 3.1
2019-05-11 11:00 | 2.8 | 2.71
2019-05-11 11:30 | 2.69 | 2.61
2019-05-11 12:00 | 2.59 | 2.53
2019-05-11 12:30 | 2.58 | 2.5
2019-05-11 13:00 | 2.77 | 2.7
2019-05-11 13:30 | 2.95 | 2.89
2019-05-11 14:00 | 3.37 | 3.31
2019-05-11 14:30 | 3.79 | 3.73
2019-05-11 15:00 | 4.41 | 4.35
2019-05-11 15:30 | 5.15 | 5.09
2019-05-11 16:00 | 6.08 | 6.03
2019-05-11 16:30 | 7.22 | 7.19
2019-05-11 17:00 | 8.54 | 8.52
2019-05-11 17:30 | 9.65 | 9.63
2019-05-11 18:00 | 10.64 | 10.64
2019-05-11 18:30 | 10.63 | 10.63
2019-05-11 19:00 | 10.67 | 10.67
2019-05-11 19:30 | 10.5 | 10.5
2019-05-11 20:00 | 10.5 | 10.49
2019-05-11 20:30 | 10.47 | 10.46
2019-05-11 21:00 | 10.07 | 10.05
2019-05-11 21:30 | 9.47 | 9.45
2019-05-11 22:00 | 9 | 8.98
2019-05-11 22:30 | 8.82 | 8.79
2019-05-11 23:00 | 8.54 | 8.51
2019-05-11 23:30 | 7.88 | 7.84
2019-05-12 | 6.95 | 6.9
2019-05-12 00:30 | 6.26 | 6.2
2019-05-12 01:00 | 5.87 | 5.8
2019-05-12 01:30 | 5.42 | 5.34
2019-05-12 02:00 | 5.12 | 5.03
2019-05-12 02:30 | 4.94 | 4.85
2019-05-12 03:00 | 4.82 | 4.72
2019-05-12 03:30 | 4.78 | 4.69
2019-05-12 04:00 | 4.75 | 4.65
2019-05-12 04:30 | 4.8 | 4.7
2019-05-12 05:00 | 5.01 | 4.92
2019-05-12 05:30 | 5.15 | 5.06
2019-05-12 06:00 | 5.32 | 5.23
2019-05-12 06:30 | 5.52 | 5.4
2019-05-12 07:00 | 6 | 5.86
2019-05-12 07:30 | 6.49 | 6.38
2019-05-12 08:00 | 7.33 | 7.25
2019-05-12 08:30 | 7.18 | 7.11
2019-05-12 09:00 | 7.07 | 7.01
2019-05-12 09:30 | 6.23 | 6.17
2019-05-12 10:00 | 5.69 | 5.63
2019-05-12 10:30 | 5.36 | 5.31
2019-05-12 11:00 | 4.21 | 4.15
2019-05-12 11:30 | 3.66 | 3.61
2019-05-12 12:00 | 3.82 | 3.76
2019-05-12 12:30 | 3.51 | 3.46
2019-05-12 13:00 | 3.82 | 3.77
2019-05-12 13:30 | 4.3 | 4.26
2019-05-12 14:00 | 5.36 | 5.32
2019-05-12 14:30 | 4.89 | 4.84
2019-05-12 15:00 | 4.93 | 4.88
2019-05-12 15:30 | 5.65 | 5.61
2019-05-12 16:00 | 6.5 | 6.46
2019-05-12 16:30 | 7.71 | 7.68
2019-05-12 17:00 | 8.95 | 8.92
2019-05-12 17:30 | 10.17 | 10.16
2019-05-12 18:00 | 11.33 | 11.32
2019-05-12 18:30 | 11.11 | 11.1
2019-05-12 19:00 | 11.11 | 11.11
2019-05-12 19:30 | 10.87 | 10.86
2019-05-12 20:00 | 10.57 | 10.56
2019-05-12 20:30 | 10.65 | 10.64
2019-05-12 21:00 | 10.17 | 10.15
2019-05-12 21:30 | 9.41 | 9.39
2019-05-12 22:00 | 8.63 | 8.6
2019-05-12 22:30 | 8.09 | 8.06
2019-05-12 23:00 | 7.77 | 7.74
2019-05-12 23:30 | 6.96 | 6.91
2019-05-13 | 6.16 | 6.1
2019-05-13 00:30 | 5.56 | 5.5
2019-05-13 01:00 | 5.17 | 5.09
2019-05-13 01:30 | 4.87 | 4.79
2019-05-13 02:00 | 4.6 | 4.51
2019-05-13 02:30 | 4.53 | 4.45
2019-05-13 03:00 | 4.52 | 4.43
2019-05-13 03:30 | 4.36 | 4.26
2019-05-13 04:00 | 4.45 | 4.36
2019-05-13 04:30 | 4.56 | 4.46
2019-05-13 05:00 | 4.9 | 4.83
2019-05-13 05:30 | 5.45 | 5.39
2019-05-13 06:00 | 6.27 | 6.23
2019-05-13 06:30 | 6.82 | 6.76
2019-05-13 07:00 | 7.47 | 7.41
2019-05-13 07:30 | 7.55 | 7.5
2019-05-13 08:00 | 7.47 | 7.42
2019-05-13 08:30 | 7.94 | 7.88
2019-05-13 09:00 | 8.07 | 8.02
2019-05-13 09:30 | 7.42 | 7.38
2019-05-13 10:00 | 6.37 | 6.32
2019-05-13 10:30 | 5.69 | 5.64
2019-05-13 11:00 | 4.33 | 4.29
2019-05-13 11:30 | 3.88 | 3.84
2019-05-13 12:00 | 3.82 | 3.78
2019-05-13 12:30 | 2.92 | 2.89
2019-05-13 13:00 | 4.74 | 4.71
2019-05-13 13:30 | 6.15 | 6.12
2019-05-13 14:00 | 6.27 | 6.25
2019-05-13 14:30 | 6.29 | 6.26
2019-05-13 15:00 | 6.73 | 6.7
2019-05-13 15:30 | 6.89 | 6.86
2019-05-13 16:00 | 7.74 | 7.72
2019-05-13 16:30 | 8.44 | 8.42
2019-05-13 17:00 | 9.47 | 9.45
2019-05-13 17:30 | 11.13 | 11.13
2019-05-13 18:00 | 12.2 | 12.2
2019-05-13 18:30 | 12.33 | 12.33
2019-05-13 19:00 | 12.28 | 12.28
2019-05-13 19:30 | 11.83 | 11.82
2019-05-13 20:00 | 11.56 | 11.56
2019-05-13 20:30 | 11.25 | 11.25
2019-05-13 21:00 | 10.64 | 10.63
2019-05-13 21:30 | 9.81 | 9.8
2019-05-13 22:00 | 8.97 | 8.95
2019-05-13 22:30 | 8.2 | 8.18
2019-05-13 23:00 | 7.76 | 7.73
2019-05-13 23:30 | 6.99 | 6.95
2019-05-14 | 6.1 | 6.04
2019-05-14 00:30 | 5.48 | 5.42
2019-05-14 01:00 | 5.17 | 5.09
2019-05-14 01:30 | 4.93 | 4.85
2019-05-14 02:00 | 4.64 | 4.55
2019-05-14 02:30 | 4.48 | 4.38
2019-05-14 03:00 | 4.41 | 4.31
2019-05-14 03:30 | 4.37 | 4.27
2019-05-14 04:00 | 4.42 | 4.32
2019-05-14 04:30 | 4.69 | 4.61
2019-05-14 05:00 | 4.9 | 4.83
2019-05-14 05:30 | 5.42 | 5.35
2019-05-14 06:00 | 5.9 | 5.84
2019-05-14 06:30 | 6.75 | 6.7
2019-05-14 07:00 | 7.69 | 7.64
2019-05-14 07:30 | 7.97 | 7.92
2019-05-14 08:00 | 7.39 | 7.34
2019-05-14 08:30 | 6.59 | 6.54
2019-05-14 09:00 | 5.36 | 5.31
2019-05-14 09:30 | 4.59 | 4.55
2019-05-14 10:00 | 3.44 | 3.4
2019-05-14 10:30 | 3.73 | 3.7
2019-05-14 11:00 | 3.21 | 3.18
2019-05-14 11:30 | 3.21 | 3.19
2019-05-14 12:00 | 3.34 | 3.32
2019-05-14 12:30 | 3.8 | 3.79
2019-05-14 13:00 | 4.24 | 4.22
2019-05-14 13:30 | 4.19 | 4.18
2019-05-14 14:00 | 5.5 | 5.48
2019-05-14 14:30 | 6.04 | 6.02
2019-05-14 15:00 | 6.51 | 6.48
2019-05-14 15:30 | 6.85 | 6.83
2019-05-14 16:00 | 7.64 | 7.62
2019-05-14 16:30 | 8.24 | 8.22
2019-05-14 17:00 | 9.73 | 9.72
2019-05-14 17:30 | 11.26 | 11.26
2019-05-14 18:00 | 12.22 | 12.21
2019-05-14 18:30 | 12.49 | 12.49
2019-05-14 19:00 | 12.38 | 12.38
2019-05-14 19:30 | 11.84 | 11.84
2019-05-14 20:00 | 11.55 | 11.55
2019-05-14 20:30 | 11.61 | 11.61
2019-05-14 21:00 | 11.06 | 11.05
2019-05-14 21:30 | 9.97 | 9.96
2019-05-14 22:00 | 9.09 | 9.07
2019-05-14 22:30 | 8.43 | 8.41
2019-05-14 23:00 | 7.83 | 7.8
2019-05-14 23:30 | 7.08 | 7.04
2019-05-15 | 6.16 | 6.11
2019-05-15 00:30 | 5.49 | 5.43
2019-05-15 01:00 | 5.11 | 5.04
2019-05-15 01:30 | 4.92 | 4.84
2019-05-15 02:00 | 4.69 | 4.61
2019-05-15 02:30 | 4.51 | 4.42
2019-05-15 03:00 | 4.42 | 4.33
2019-05-15 03:30 | 4.39 | 4.29
2019-05-15 04:00 | 4.44 | 4.34
2019-05-15 04:30 | 4.66 | 4.57
2019-05-15 05:00 | 4.95 | 4.87
2019-05-15 05:30 | 5.49 | 5.43
2019-05-15 06:00 | 6.13 | 6.08
2019-05-15 06:30 | 6.51 | 6.46
2019-05-15 07:00 | 7.07 | 7
2019-05-15 07:30 | 7.41 | 7.35
2019-05-15 08:00 | 6.91 | 6.85
2019-05-15 08:30 | 6.11 | 6.04
2019-05-15 09:00 | 4.35 | 4.26
2019-05-15 09:30 | 4.77 | 4.71
2019-05-15 10:00 | 3.42 | 3.38
2019-05-15 10:30 | 3.35 | 3.33
2019-05-15 11:00 | 3.65 | 3.64
2019-05-15 11:30 | 3.34 | 3.33
2019-05-15 12:00 | 3.67 | 3.65
2019-05-15 12:30 | 3.89 | 3.88
2019-05-15 13:00 | 5.93 | 5.92
2019-05-15 13:30 | 6.52 | 6.51
2019-05-15 14:00 | 5.76 | 5.74
2019-05-15 14:30 | 6.03 | 6.02
2019-05-15 15:00 | 6.29 | 6.28
2019-05-15 15:30 | 6.93 | 6.91
2019-05-15 16:00 | 7.48 | 7.46
2019-05-15 16:30 | 8.56 | 8.54
2019-05-15 17:00 | 9.53 | 9.52
2019-05-15 17:30 | 10.96 | 10.96
2019-05-15 18:00 | 11.93 | 11.93
2019-05-15 18:30 | 12.08 | 12.07
2019-05-15 19:00 | 12.04 | 12.04
2019-05-15 19:30 | 11.64 | 11.63
2019-05-15 20:00 | 11.48 | 11.47
2019-05-15 20:30 | 11.56 | 11.55
2019-05-15 21:00 | 11.01 | 11
2019-05-15 21:30 | 10.27 | 10.26
2019-05-15 22:00 | 9.13 | 9.12
2019-05-15 22:30 | 8.42 | 8.4
2019-05-15 23:00 | 7.76 | 7.73
2019-05-15 23:30 | 6.95 | 6.9
2019-05-16 | 6.04 | 5.98
2019-05-16 00:30 | 5.41 | 5.35
2019-05-16 01:00 | 5.02 | 4.95
2019-05-16 01:30 | 4.77 | 4.69
2019-05-16 02:00 | 4.58 | 4.49
2019-05-16 02:30 | 4.42 | 4.33
2019-05-16 03:00 | 4.47 | 4.37
2019-05-16 03:30 | 4.49 | 4.39
2019-05-16 04:00 | 4.45 | 4.36
2019-05-16 04:30 | 4.67 | 4.58
2019-05-16 05:00 | 4.94 | 4.86
2019-05-16 05:30 | 5.5 | 5.44
2019-05-16 06:00 | 6.32 | 6.28
2019-05-16 06:30 | 6.99 | 6.94
2019-05-16 07:00 | 7.5 | 7.44
2019-05-16 07:30 | 7.68 | 7.63
2019-05-16 08:00 | 7.22 | 7.17
2019-05-16 08:30 | 5.46 | 5.4
2019-05-16 09:00 | 4.38 | 4.32
2019-05-16 09:30 | 3.76 | 3.72
2019-05-16 10:00 | 3.41 | 3.38
2019-05-16 10:30 | 3.45 | 3.42
2019-05-16 11:00 | 3.44 | 3.42
2019-05-16 11:30 | 3.94 | 3.92
2019-05-16 12:00 | 4.34 | 4.32
2019-05-16 12:30 | 3.27 | 3.25
2019-05-16 13:00 | 3.31 | 3.29
2019-05-16 13:30 | 3.92 | 3.91
2019-05-16 14:00 | 4.63 | 4.62
2019-05-16 14:30 | 4.68 | 4.67
2019-05-16 15:00 | 5.27 | 5.26
2019-05-16 15:30 | 5.8 | 5.79
2019-05-16 16:00 | 7.04 | 7.03
2019-05-16 16:30 | 8.01 | 7.99
2019-05-16 17:00 | 9.27 | 9.26
2019-05-16 17:30 | 10.44 | 10.43
2019-05-16 18:00 | 11.42 | 11.42
2019-05-16 18:30 | 11.89 | 11.89
2019-05-16 19:00 | 11.96 | 11.96
2019-05-16 19:30 | 11.47 | 11.47
2019-05-16 20:00 | 11.52 | 11.51
2019-05-16 20:30 | 11.42 | 11.42
2019-05-16 21:00 | 10.77 | 10.76
2019-05-16 21:30 | 10.01 | 10
2019-05-16 22:00 | 9.29 | 9.28
2019-05-16 22:30 | 8.8 | 8.78
2019-05-16 23:00 | 8.21 | 8.19
2019-05-16 23:30 | 7.03 | 6.99
2019-05-17 | 6.29 | 6.24
2019-05-17 00:30 | 5.67 | 5.61
2019-05-17 01:00 | 5.31 | 5.24
2019-05-17 01:30 | 4.94 | 4.86
2019-05-17 02:00 | 4.63 | 4.55
2019-05-17 02:30 | 4.51 | 4.42
2019-05-17 03:00 | 4.49 | 4.4
2019-05-17 03:30 | 4.37 | 4.28
2019-05-17 04:00 | 4.51 | 4.42
2019-05-17 04:30 | 4.65 | 4.57
2019-05-17 05:00 | 4.86 | 4.79
2019-05-17 05:30 | 5.15 | 5.09
2019-05-17 06:00 | 5.53 | 5.48
2019-05-17 06:30 | 6.15 | 6.11
2019-05-17 07:00 | 6.53 | 6.46
2019-05-17 07:30 | 6.83 | 6.76
2019-05-17 08:00 | 6.77 | 6.7
2019-05-17 08:30 | 6.95 | 6.89
2019-05-17 09:00 | 6.77 | 6.72
2019-05-17 09:30 | 6.73 | 6.68
2019-05-17 10:00 | 6.78 | 6.73
2019-05-17 10:30 | 6.21 | 6.16
2019-05-17 11:00 | 5.77 | 5.72
2019-05-17 11:30 | 6.17 | 6.12
2019-05-17 12:00 | 5.88 | 5.84
2019-05-17 12:30 | 5.56 | 5.52
2019-05-17 13:00 | 3.97 | 3.92
2019-05-17 13:30 | 5.05 | 5.01
2019-05-17 14:00 | 7.3 | 7.27
2019-05-17 14:30 | 7.18 | 7.14
2019-05-17 15:00 | 6.68 | 6.63
2019-05-17 15:30 | 5.4 | 5.34
2019-05-17 16:00 | 7.1 | 7.06
2019-05-17 16:30 | 8.2 | 8.16
2019-05-17 17:00 | 9.06 | 9.03
2019-05-17 17:30 | 10.1 | 10.09
2019-05-17 18:00 | 10.75 | 10.74
2019-05-17 18:30 | 10.73 | 10.73
2019-05-17 19:00 | 10.6 | 10.59
2019-05-17 19:30 | 10.34 | 10.33
2019-05-17 20:00 | 10.37 | 10.37
2019-05-17 20:30 | 10.27 | 10.26
2019-05-17 21:00 | 9.76 | 9.75
2019-05-17 21:30 | 9.19 | 9.17
2019-05-17 22:00 | 8.56 | 8.53
2019-05-17 22:30 | 8.33 | 8.3
2019-05-17 23:00 | 8.19 | 8.15
2019-05-17 23:30 | 7.38 | 7.34
2019-05-18 | 6.58 | 6.53
2019-05-18 00:30 | 5.94 | 5.88
2019-05-18 01:00 | 5.53 | 5.46
2019-05-18 01:30 | 5.13 | 5.04
2019-05-18 02:00 | 4.83 | 4.74
2019-05-18 02:30 | 4.67 | 4.58
2019-05-18 03:00 | 4.63 | 4.53
2019-05-18 03:30 | 4.51 | 4.41
2019-05-18 04:00 | 4.5 | 4.4
2019-05-18 04:30 | 4.53 | 4.43
2019-05-18 05:00 | 4.67 | 4.57
2019-05-18 05:30 | 4.77 | 4.68
2019-05-18 06:00 | 5.03 | 4.94
2019-05-18 06:30 | 5.25 | 5.14
2019-05-18 07:00 | 5.65 | 5.52
2019-05-18 07:30 | 6.17 | 6.06
2019-05-18 08:00 | 5.81 | 5.71
2019-05-18 08:30 | 5.56 | 5.48
2019-05-18 09:00 | 5.37 | 5.3
2019-05-18 09:30 | 4.45 | 4.38
2019-05-18 10:00 | 4.33 | 4.28
2019-05-18 10:30 | 5.32 | 5.28
2019-05-18 11:00 | 4.98 | 4.94
2019-05-18 11:30 | 3.85 | 3.82
2019-05-18 12:00 | 3.75 | 3.72
2019-05-18 12:30 | 4.57 | 4.54
2019-05-18 13:00 | 4.66 | 4.63
2019-05-18 13:30 | 4.54 | 4.51
2019-05-18 14:00 | 4.86 | 4.84
2019-05-18 14:30 | 6.42 | 6.4
2019-05-18 15:00 | 7.56 | 7.53
2019-05-18 15:30 | 7.35 | 7.32
2019-05-18 16:00 | 7.46 | 7.43
2019-05-18 16:30 | 8.12 | 8.1
2019-05-18 17:00 | 8.95 | 8.93
2019-05-18 17:30 | 10.04 | 10.03
2019-05-18 18:00 | 10.53 | 10.53
2019-05-18 18:30 | 10.49 | 10.49
2019-05-18 19:00 | 10.49 | 10.48
2019-05-18 19:30 | 10.11 | 10.1
2019-05-18 20:00 | 10.12 | 10.12
2019-05-18 20:30 | 9.93 | 9.92
2019-05-18 21:00 | 9.55 | 9.53
2019-05-18 21:30 | 9 | 8.98
2019-05-18 22:00 | 8.66 | 8.63
2019-05-18 22:30 | 8.3 | 8.27
2019-05-18 23:00 | 8.3 | 8.27
2019-05-18 23:30 | 7.49 | 7.45
2019-05-19 | 6.64 | 6.59
2019-05-19 00:30 | 5.99 | 5.93
2019-05-19 01:00 | 5.67 | 5.6
2019-05-19 01:30 | 5.24 | 5.17
2019-05-19 02:00 | 4.91 | 4.82
2019-05-19 02:30 | 4.66 | 4.57
2019-05-19 03:00 | 4.55 | 4.45
2019-05-19 03:30 | 4.45 | 4.35
2019-05-19 04:00 | 4.45 | 4.34
2019-05-19 04:30 | 4.46 | 4.35
2019-05-19 05:00 | 4.56 | 4.47
2019-05-19 05:30 | 4.58 | 4.49
2019-05-19 06:00 | 4.82 | 4.72
2019-05-19 06:30 | 4.99 | 4.89
2019-05-19 07:00 | 5.22 | 5.08
2019-05-19 07:30 | 5.56 | 5.43
2019-05-19 08:00 | 5.94 | 5.83
2019-05-19 08:30 | 5.52 | 5.42
2019-05-19 09:00 | 5.09 | 5
2019-05-19 09:30 | 4.69 | 4.61
2019-05-19 10:00 | 4.48 | 4.42
2019-05-19 10:30 | 4.14 | 4.08
2019-05-19 11:00 | 4.17 | 4.13
2019-05-19 11:30 | 5.77 | 5.74
2019-05-19 12:00 | 5.94 | 5.92
2019-05-19 12:30 | 5.27 | 5.24
2019-05-19 13:00 | 4.63 | 4.6
2019-05-19 13:30 | 4.15 | 4.12
2019-05-19 14:00 | 5.56 | 5.54
2019-05-19 14:30 | 5.7 | 5.68
2019-05-19 15:00 | 5.6 | 5.57
2019-05-19 15:30 | 6.61 | 6.58
2019-05-19 16:00 | 7.28 | 7.25
2019-05-19 16:30 | 8.5 | 8.48
2019-05-19 17:00 | 10.02 | 10
2019-05-19 17:30 | 11.13 | 11.12
2019-05-19 18:00 | 12.02 | 12.01
2019-05-19 18:30 | 11.8 | 11.8
2019-05-19 19:00 | 11.51 | 11.5
2019-05-19 19:30 | 10.94 | 10.94
2019-05-19 20:00 | 10.79 | 10.78
2019-05-19 20:30 | 10.67 | 10.66
2019-05-19 21:00 | 10.17 | 10.15
2019-05-19 21:30 | 9.44 | 9.42
2019-05-19 22:00 | 8.76 | 8.73
2019-05-19 22:30 | 8.23 | 8.21
2019-05-19 23:00 | 7.83 | 7.79
2019-05-19 23:30 | 7.1 | 7.05
2019-05-20 | 6.19 | 6.13
2019-05-20 00:30 | 5.51 | 5.44
2019-05-20 01:00 | 5.21 | 5.13
2019-05-20 01:30 | 4.78 | 4.7
2019-05-20 02:00 | 4.65 | 4.56
2019-05-20 02:30 | 4.46 | 4.36
2019-05-20 03:00 | 4.33 | 4.23
2019-05-20 03:30 | 4.45 | 4.35
2019-05-20 04:00 | 4.45 | 4.35
2019-05-20 04:30 | 4.72 | 4.63
2019-05-20 05:00 | 5.07 | 4.99
2019-05-20 05:30 | 5.55 | 5.49
2019-05-20 06:00 | 6.35 | 6.31
2019-05-20 06:30 | 6.93 | 6.88
2019-05-20 07:00 | 7.62 | 7.57
2019-05-20 07:30 | 7.83 | 7.78
2019-05-20 08:00 | 7.75 | 7.71
2019-05-20 08:30 | 7.99 | 7.93
2019-05-20 09:00 | 7.29 | 7.23
2019-05-20 09:30 | 6.62 | 6.57
2019-05-20 10:00 | 6.62 | 6.57
2019-05-20 10:30 | 4.31 | 4.26
2019-05-20 11:00 | 3.39 | 3.35
2019-05-20 11:30 | 5.21 | 5.17
2019-05-20 12:00 | 5.66 | 5.62
2019-05-20 12:30 | 4.97 | 4.93
2019-05-20 13:00 | 4.82 | 4.78
2019-05-20 13:30 | 5.24 | 5.21
2019-05-20 14:00 | 6.3 | 6.27
2019-05-20 14:30 | 6.01 | 5.98
2019-05-20 15:00 | 6.5 | 6.48
2019-05-20 15:30 | 7.48 | 7.46
2019-05-20 16:00 | 8.01 | 7.99
2019-05-20 16:30 | 9.02 | 9
2019-05-20 17:00 | 10.36 | 10.35
2019-05-20 17:30 | 11.81 | 11.81
2019-05-20 18:00 | 12.79 | 12.79
2019-05-20 18:30 | 12.76 | 12.76
2019-05-20 19:00 | 12.53 | 12.53
2019-05-20 19:30 | 11.9 | 11.9
2019-05-20 20:00 | 11.69 | 11.69
2019-05-20 20:30 | 11.59 | 11.59
2019-05-20 21:00 | 11.01 | 11
2019-05-20 21:30 | 10.05 | 10.04
2019-05-20 22:00 | 9.21 | 9.2
2019-05-20 22:30 | 8.31 | 8.29
2019-05-20 23:00 | 7.83 | 7.79
2019-05-20 23:30 | 7.06 | 7.02
2019-05-21 | 6.13 | 6.08
2019-05-21 00:30 | 5.53 | 5.46
2019-05-21 01:00 | 5.14 | 5.07
2019-05-21 01:30 | 4.79 | 4.71
2019-05-21 02:00 | 4.55 | 4.46
2019-05-21 02:30 | 4.43 | 4.32
2019-05-21 03:00 | 4.34 | 4.24
2019-05-21 03:30 | 4.39 | 4.29
2019-05-21 04:00 | 4.51 | 4.41
2019-05-21 04:30 | 4.62 | 4.53
2019-05-21 05:00 | 4.97 | 4.88
2019-05-21 05:30 | 5.4 | 5.34
2019-05-21 06:00 | 5.89 | 5.84
2019-05-21 06:30 | 6.46 | 6.41
2019-05-21 07:00 | 7.13 | 7.06
2019-05-21 07:30 | 7.34 | 7.28
2019-05-21 08:00 | 6.89 | 6.83
2019-05-21 08:30 | 5.72 | 5.65
2019-05-21 09:00 | 4.48 | 4.42
2019-05-21 09:30 | 4.05 | 4
2019-05-21 10:00 | 3.52 | 3.48
2019-05-21 10:30 | 3.15 | 3.12
2019-05-21 11:00 | 3.12 | 3.09
2019-05-21 11:30 | 3.49 | 3.47
2019-05-21 12:00 | 3.91 | 3.89
2019-05-21 12:30 | 4.84 | 4.82
2019-05-21 13:00 | 5.1 | 5.08
2019-05-21 13:30 | 4.47 | 4.45
2019-05-21 14:00 | 3.79 | 3.77
2019-05-21 14:30 | 4.57 | 4.56
2019-05-21 15:00 | 5.2 | 5.19
2019-05-21 15:30 | 6.05 | 6.05
2019-05-21 16:00 | 7.03 | 7.02
2019-05-21 16:30 | 8.31 | 8.31
2019-05-21 17:00 | 9.67 | 9.66
2019-05-21 17:30 | 11.08 | 11.07
2019-05-21 18:00 | 12.19 | 12.19
2019-05-21 18:30 | 12.46 | 12.46
2019-05-21 19:00 | 12.6 | 12.6
2019-05-21 19:30 | 12 | 12
2019-05-21 20:00 | 11.79 | 11.79
2019-05-21 20:30 | 11.78 | 11.78
2019-05-21 21:00 | 11.18 | 11.18
2019-05-21 21:30 | 10.29 | 10.28
2019-05-21 22:00 | 9.32 | 9.31
2019-05-21 22:30 | 8.55 | 8.53
2019-05-21 23:00 | 7.96 | 7.93
2019-05-21 23:30 | 6.96 | 6.91
2019-05-22 | 6.15 | 6.08
2019-05-22 00:30 | 5.44 | 5.37
2019-05-22 01:00 | 5.13 | 5.05
2019-05-22 01:30 | 4.85 | 4.76
2019-05-22 02:00 | 4.64 | 4.54
2019-05-22 02:30 | 4.56 | 4.46
2019-05-22 03:00 | 4.44 | 4.33
2019-05-22 03:30 | 4.5 | 4.39
2019-05-22 04:00 | 4.55 | 4.44
2019-05-22 04:30 | 4.74 | 4.64
2019-05-22 05:00 | 5.09 | 5
2019-05-22 05:30 | 5.56 | 5.49
2019-05-22 06:00 | 6.18 | 6.13
2019-05-22 06:30 | 6.7 | 6.64
2019-05-22 07:00 | 7.4 | 7.34
2019-05-22 07:30 | 7.46 | 7.4
2019-05-22 08:00 | 6.67 | 6.62
2019-05-22 08:30 | 5.47 | 5.4
2019-05-22 09:00 | 4.47 | 4.4
2019-05-22 09:30 | 3.6 | 3.52
2019-05-22 10:00 | 3.01 | 2.93
2019-05-22 10:30 | 2.99 | 2.94
2019-05-22 11:00 | 2.96 | 2.92
2019-05-22 11:30 | 3.92 | 3.89
2019-05-22 12:00 | 4.93 | 4.9
2019-05-22 12:30 | 4.42 | 4.39
2019-05-22 13:00 | 5.4 | 5.36
2019-05-22 13:30 | 6.96 | 6.93
2019-05-22 14:00 | 7.31 | 7.27
2019-05-22 14:30 | 6.07 | 6.04
2019-05-22 15:00 | 6.23 | 6.21
2019-05-22 15:30 | 6.72 | 6.7
2019-05-22 16:00 | 7.75 | 7.73
2019-05-22 16:30 | 8.7 | 8.69
2019-05-22 17:00 | 9.78 | 9.77
2019-05-22 17:30 | 11.29 | 11.28
2019-05-22 18:00 | 12.05 | 12.05
2019-05-22 18:30 | 12.15 | 12.15
2019-05-22 19:00 | 12.4 | 12.4
2019-05-22 19:30 | 12.09 | 12.08
2019-05-22 20:00 | 11.96 | 11.96
2019-05-22 20:30 | 11.94 | 11.94
2019-05-22 21:00 | 11.27 | 11.27
2019-05-22 21:30 | 10.26 | 10.25
2019-05-22 22:00 | 9.25 | 9.23
2019-05-22 22:30 | 8.62 | 8.6
2019-05-22 23:00 | 8.09 | 8.06
2019-05-22 23:30 | 7.07 | 7.03
2019-05-23 | 6.25 | 6.19
2019-05-23 00:30 | 5.52 | 5.45
2019-05-23 01:00 | 5.19 | 5.11
2019-05-23 01:30 | 4.86 | 4.77
2019-05-23 02:00 | 4.7 | 4.6
2019-05-23 02:30 | 4.61 | 4.51
2019-05-23 03:00 | 4.51 | 4.41
2019-05-23 03:30 | 4.55 | 4.44
2019-05-23 04:00 | 4.64 | 4.54
2019-05-23 04:30 | 4.84 | 4.74
2019-05-23 05:00 | 5.17 | 5.09
2019-05-23 05:30 | 5.74 | 5.68
2019-05-23 06:00 | 6.35 | 6.31
2019-05-23 06:30 | 7.37 | 7.33
2019-05-23 07:00 | 8.04 | 7.99
2019-05-23 07:30 | 8.21 | 8.17
2019-05-23 08:00 | 7.36 | 7.32
2019-05-23 08:30 | 7.32 | 7.26
2019-05-23 09:00 | 6.27 | 6.2
2019-05-23 09:30 | 5.53 | 5.47
2019-05-23 10:00 | 5.01 | 4.94
2019-05-23 10:30 | 5.8 | 5.74
2019-05-23 11:00 | 4.68 | 4.62
2019-05-23 11:30 | 4.79 | 4.74
2019-05-23 12:00 | 4.42 | 4.37
2019-05-23 12:30 | 4.67 | 4.63
2019-05-23 13:00 | 3.5 | 3.48
2019-05-23 13:30 | 3.58 | 3.56
2019-05-23 14:00 | 3.4 | 3.38
2019-05-23 14:30 | 4.47 | 4.45
2019-05-23 15:00 | 6.58 | 6.56
2019-05-23 15:30 | 6.63 | 6.61
2019-05-23 16:00 | 7.24 | 7.22
2019-05-23 16:30 | 8.24 | 8.23
2019-05-23 17:00 | 9.39 | 9.38
2019-05-23 17:30 | 10.75 | 10.75
2019-05-23 18:00 | 11.72 | 11.72
2019-05-23 18:30 | 11.98 | 11.98
2019-05-23 19:00 | 12.25 | 12.25
2019-05-23 19:30 | 11.92 | 11.92
2019-05-23 20:00 | 11.98 | 11.98
2019-05-23 20:30 | 11.79 | 11.78
2019-05-23 21:00 | 11 | 11
2019-05-23 21:30 | 10.24 | 10.23
2019-05-23 22:00 | 9.21 | 9.19
2019-05-23 22:30 | 8.62 | 8.6
2019-05-23 23:00 | 8.14 | 8.11
2019-05-23 23:30 | 7.21 | 7.17
2019-05-24 | 6.3 | 6.23
2019-05-24 00:30 | 5.61 | 5.54
2019-05-24 01:00 | 5.26 | 5.17
2019-05-24 01:30 | 4.95 | 4.86
2019-05-24 02:00 | 4.68 | 4.58
2019-05-24 02:30 | 4.62 | 4.52
2019-05-24 03:00 | 4.57 | 4.46
2019-05-24 03:30 | 4.57 | 4.46
2019-05-24 04:00 | 4.62 | 4.52
2019-05-24 04:30 | 4.85 | 4.76
2019-05-24 05:00 | 5.11 | 5.03
2019-05-24 05:30 | 5.73 | 5.67
2019-05-24 06:00 | 6.72 | 6.69
2019-05-24 06:30 | 7.54 | 7.49
2019-05-24 07:00 | 8.18 | 8.13
2019-05-24 07:30 | 8.45 | 8.4
2019-05-24 08:00 | 7.67 | 7.63
2019-05-24 08:30 | 6.35 | 6.3
2019-05-24 09:00 | 5.27 | 5.22
2019-05-24 09:30 | 4.51 | 4.47
2019-05-24 10:00 | 3.94 | 3.9
2019-05-24 10:30 | 3.08 | 3.02
2019-05-24 11:00 | 2.56 | 2.49
2019-05-24 11:30 | 2.92 | 2.87
2019-05-24 12:00 | 3.18 | 3.13
2019-05-24 12:30 | 2.58 | 2.52
2019-05-24 13:00 | 3.26 | 3.23
2019-05-24 13:30 | 3.49 | 3.46
2019-05-24 14:00 | 4.98 | 4.95
2019-05-24 14:30 | 4.82 | 4.78
2019-05-24 15:00 | 4.75 | 4.72
2019-05-24 15:30 | 5.22 | 5.2
2019-05-24 16:00 | 6.39 | 6.37
2019-05-24 16:30 | 7.6 | 7.57
2019-05-24 17:00 | 8.94 | 8.92
2019-05-24 17:30 | 9.91 | 9.9
2019-05-24 18:00 | 10.6 | 10.59
2019-05-24 18:30 | 10.75 | 10.74
2019-05-24 19:00 | 10.81 | 10.81
2019-05-24 19:30 | 10.67 | 10.67
2019-05-24 20:00 | 10.71 | 10.71
2019-05-24 20:30 | 10.68 | 10.67
2019-05-24 21:00 | 10.23 | 10.22
2019-05-24 21:30 | 9.51 | 9.5
2019-05-24 22:00 | 8.98 | 8.96
2019-05-24 22:30 | 8.61 | 8.58
2019-05-24 23:00 | 8.3 | 8.27
2019-05-24 23:30 | 7.46 | 7.41
2019-05-25 | 6.55 | 6.49
2019-05-25 00:30 | 5.92 | 5.85
2019-05-25 01:00 | 5.58 | 5.51
2019-05-25 01:30 | 5.17 | 5.09
2019-05-25 02:00 | 4.82 | 4.72
2019-05-25 02:30 | 4.75 | 4.65
2019-05-25 03:00 | 4.67 | 4.56
2019-05-25 03:30 | 4.68 | 4.58
2019-05-25 04:00 | 4.62 | 4.52
2019-05-25 04:30 | 4.68 | 4.58
2019-05-25 05:00 | 4.83 | 4.74
2019-05-25 05:30 | 4.97 | 4.88
2019-05-25 06:00 | 5.3 | 5.21
2019-05-25 06:30 | 5.57 | 5.47
2019-05-25 07:00 | 5.94 | 5.82
2019-05-25 07:30 | 6.19 | 6.08
2019-05-25 08:00 | 6.2 | 6.11
2019-05-25 08:30 | 5.95 | 5.88
2019-05-25 09:00 | 5.44 | 5.38
2019-05-25 09:30 | 4.98 | 4.92
2019-05-25 10:00 | 4.33 | 4.27
2019-05-25 10:30 | 3.94 | 3.88
2019-05-25 11:00 | 4.41 | 4.36
2019-05-25 11:30 | 3.34 | 3.29
2019-05-25 12:00 | 3.44 | 3.41
2019-05-25 12:30 | 3.99 | 3.95
2019-05-25 13:00 | 4.7 | 4.67
2019-05-25 13:30 | 4.85 | 4.82
2019-05-25 14:00 | 4.01 | 3.98
2019-05-25 14:30 | 4.54 | 4.51
2019-05-25 15:00 | 5.86 | 5.83
2019-05-25 15:30 | 6.56 | 6.53
2019-05-25 16:00 | 6.9 | 6.87
2019-05-25 16:30 | 8.11 | 8.08
2019-05-25 17:00 | 9.11 | 9.09
2019-05-25 17:30 | 9.95 | 9.95
2019-05-25 18:00 | 10.57 | 10.57
2019-05-25 18:30 | 10.57 | 10.56
2019-05-25 19:00 | 10.43 | 10.42
2019-05-25 19:30 | 10.15 | 10.15
2019-05-25 20:00 | 10.08 | 10.07
2019-05-25 20:30 | 9.99 | 9.98
2019-05-25 21:00 | 9.41 | 9.4
2019-05-25 21:30 | 8.94 | 8.93
2019-05-25 22:00 | 8.52 | 8.5
2019-05-25 22:30 | 8.1 | 8.07
2019-05-25 23:00 | 8 | 7.97
2019-05-25 23:30 | 7.37 | 7.33
2019-05-26 | 6.74 | 6.69
2019-05-26 00:30 | 6.05 | 5.98
2019-05-26 01:00 | 5.47 | 5.4
2019-05-26 01:30 | 5.05 | 4.97
2019-05-26 02:00 | 4.71 | 4.62
2019-05-26 02:30 | 4.61 | 4.52
2019-05-26 03:00 | 4.54 | 4.44
2019-05-26 03:30 | 4.48 | 4.37
2019-05-26 04:00 | 4.46 | 4.35
2019-05-26 04:30 | 4.4 | 4.3
2019-05-26 05:00 | 4.53 | 4.43
2019-05-26 05:30 | 4.6 | 4.51
2019-05-26 06:00 | 4.79 | 4.69
2019-05-26 06:30 | 4.97 | 4.87
2019-05-26 07:00 | 5.17 | 5.02
2019-05-26 07:30 | 5.74 | 5.61
2019-05-26 08:00 | 6.21 | 6.11
2019-05-26 08:30 | 6.9 | 6.83
2019-05-26 09:00 | 6.97 | 6.91
2019-05-26 09:30 | 5.71 | 5.66
2019-05-26 10:00 | 4.82 | 4.78
2019-05-26 10:30 | 4.3 | 4.25
2019-05-26 11:00 | 4.07 | 4.03
2019-05-26 11:30 | 3.84 | 3.81
2019-05-26 12:00 | 3.82 | 3.79
2019-05-26 12:30 | 3.9 | 3.88
2019-05-26 13:00 | 4.87 | 4.85
2019-05-26 13:30 | 7.31 | 7.29
2019-05-26 14:00 | 6.14 | 6.12
2019-05-26 14:30 | 7.77 | 7.75
2019-05-26 15:00 | 7.49 | 7.46
2019-05-26 15:30 | 7.32 | 7.3
2019-05-26 16:00 | 7.64 | 7.62
2019-05-26 16:30 | 8.83 | 8.81
2019-05-26 17:00 | 9.93 | 9.91
2019-05-26 17:30 | 11.21 | 11.2
2019-05-26 18:00 | 12.15 | 12.14
2019-05-26 18:30 | 11.86 | 11.85
2019-05-26 19:00 | 11.63 | 11.62
2019-05-26 19:30 | 11.15 | 11.15
2019-05-26 20:00 | 10.89 | 10.88
2019-05-26 20:30 | 10.7 | 10.69
2019-05-26 21:00 | 10.14 | 10.13
2019-05-26 21:30 | 9.44 | 9.43
2019-05-26 22:00 | 8.77 | 8.74
2019-05-26 22:30 | 8.29 | 8.26
2019-05-26 23:00 | 7.96 | 7.93
2019-05-26 23:30 | 7.11 | 7.07
2019-05-27 | 6.16 | 6.1
2019-05-27 00:30 | 5.6 | 5.52
2019-05-27 01:00 | 5.29 | 5.21
2019-05-27 01:30 | 4.91 | 4.82
2019-05-27 02:00 | 4.67 | 4.57
2019-05-27 02:30 | 4.6 | 4.49
2019-05-27 03:00 | 4.5 | 4.39
2019-05-27 03:30 | 4.52 | 4.41
2019-05-27 04:00 | 4.58 | 4.47
2019-05-27 04:30 | 4.75 | 4.64
2019-05-27 05:00 | 5.24 | 5.15
2019-05-27 05:30 | 5.67 | 5.6
2019-05-27 06:00 | 6.22 | 6.17
2019-05-27 06:30 | 7.28 | 7.24
2019-05-27 07:00 | 8.18 | 8.14
2019-05-27 07:30 | 8.26 | 8.21
2019-05-27 08:00 | 7.76 | 7.73
2019-05-27 08:30 | 6.76 | 6.72
2019-05-27 09:00 | 5.23 | 5.18
2019-05-27 09:30 | 4.5 | 4.45
2019-05-27 10:00 | 4.15 | 4.11
2019-05-27 10:30 | 3.58 | 3.54
2019-05-27 11:00 | 3.08 | 3.04
2019-05-27 11:30 | 3.05 | 3.02
2019-05-27 12:00 | 3.04 | 3.01
2019-05-27 12:30 | 3.24 | 3.22
2019-05-27 13:00 | 3.56 | 3.54
2019-05-27 13:30 | 3.99 | 3.98
2019-05-27 14:00 | 4.17 | 4.15
2019-05-27 14:30 | 4.44 | 4.42
2019-05-27 15:00 | 5.11 | 5.09
2019-05-27 15:30 | 5.99 | 5.98
2019-05-27 16:00 | 7.27 | 7.26
2019-05-27 16:30 | 8.52 | 8.51
2019-05-27 17:00 | 10.05 | 10.04
2019-05-27 17:30 | 11.36 | 11.35
2019-05-27 18:00 | 12.58 | 12.58
2019-05-27 18:30 | 12.64 | 12.64
2019-05-27 19:00 | 12.33 | 12.33
2019-05-27 19:30 | 12.09 | 12.08
2019-05-27 20:00 | 12.08 | 12.08
2019-05-27 20:30 | 11.97 | 11.97
2019-05-27 21:00 | 11.29 | 11.28
2019-05-27 21:30 | 10.29 | 10.28
2019-05-27 22:00 | 9.13 | 9.11
2019-05-27 22:30 | 8.4 | 8.37
2019-05-27 23:00 | 7.85 | 7.81
2019-05-27 23:30 | 7.02 | 6.97
2019-05-28 | 6.1 | 6.04
2019-05-28 00:30 | 5.5 | 5.42
2019-05-28 01:00 | 5.21 | 5.12
2019-05-28 01:30 | 4.91 | 4.82
2019-05-28 02:00 | 4.74 | 4.64
2019-05-28 02:30 | 4.65 | 4.54
2019-05-28 03:00 | 4.66 | 4.55
2019-05-28 03:30 | 4.67 | 4.57
2019-05-28 04:00 | 4.64 | 4.53
2019-05-28 04:30 | 4.96 | 4.86
2019-05-28 05:00 | 5.38 | 5.29
2019-05-28 05:30 | 5.92 | 5.86
2019-05-28 06:00 | 6.57 | 6.52
2019-05-28 06:30 | 7.24 | 7.19
2019-05-28 07:00 | 8.6 | 8.56
2019-05-28 07:30 | 8.93 | 8.9
2019-05-28 08:00 | 8.18 | 8.15
2019-05-28 08:30 | 6.72 | 6.68
2019-05-28 09:00 | 5.39 | 5.34
2019-05-28 09:30 | 4.58 | 4.53
2019-05-28 10:00 | 3.86 | 3.8
2019-05-28 10:30 | 3.26 | 3.2
2019-05-28 11:00 | 2.72 | 2.65
2019-05-28 11:30 | 2.64 | 2.58
2019-05-28 12:00 | 2.45 | 2.39
2019-05-28 12:30 | 2.58 | 2.52
2019-05-28 13:00 | 2.59 | 2.54
2019-05-28 13:30 | 2.9 | 2.85
2019-05-28 14:00 | 3.35 | 3.31
2019-05-28 14:30 | 3.9 | 3.86
2019-05-28 15:00 | 4.36 | 4.31
2019-05-28 15:30 | 5.15 | 5.1
2019-05-28 16:00 | 6.48 | 6.45
2019-05-28 16:30 | 8.14 | 8.12
2019-05-28 17:00 | 9.68 | 9.66
2019-05-28 17:30 | 11.47 | 11.47
2019-05-28 18:00 | 12.68 | 12.68
2019-05-28 18:30 | 12.95 | 12.95
2019-05-28 19:00 | 13.33 | 13.33
2019-05-28 19:30 | 12.96 | 12.96
2019-05-28 20:00 | 12.95 | 12.95
2019-05-28 20:30 | 12.96 | 12.96
2019-05-28 21:00 | 12.25 | 12.25
2019-05-28 21:30 | 11.39 | 11.39
2019-05-28 22:00 | 10.2 | 10.18
2019-05-28 22:30 | 9.16 | 9.14
2019-05-28 23:00 | 8.64 | 8.61
2019-05-28 23:30 | 7.71 | 7.67
2019-05-29 | 6.81 | 6.75
2019-05-29 00:30 | 6.01 | 5.94
2019-05-29 01:00 | 5.83 | 5.75
2019-05-29 01:30 | 6.35 | 6.26
2019-05-29 02:00 | 6.17 | 6.07
2019-05-29 02:30 | 6.12 | 6.02
2019-05-29 03:00 | 6.05 | 5.94
2019-05-29 03:30 | 5.94 | 5.84
2019-05-29 04:00 | 5.44 | 5.35
2019-05-29 04:30 | 6.1 | 6.01
2019-05-29 05:00 | 6.14 | 6.06
2019-05-29 05:30 | 6.76 | 6.7
2019-05-29 06:00 | 7.6 | 7.56
2019-05-29 06:30 | 8.87 | 8.85
2019-05-29 07:00 | 9.93 | 9.9
2019-05-29 07:30 | 10.23 | 10.2
2019-05-29 08:00 | 9.26 | 9.24
2019-05-29 08:30 | 8.02 | 7.99
2019-05-29 09:00 | 7.1 | 7.05
2019-05-29 09:30 | 5.62 | 5.57
2019-05-29 10:00 | 4.69 | 4.65
2019-05-29 10:30 | 3.84 | 3.78
2019-05-29 11:00 | 3.35 | 3.28
2019-05-29 11:30 | 3.67 | 3.6
2019-05-29 12:00 | 4.02 | 3.94
2019-05-29 12:30 | 3.98 | 3.9
2019-05-29 13:00 | 2.94 | 2.88
2019-05-29 13:30 | 2.95 | 2.9
2019-05-29 14:00 | 3.42 | 3.37
2019-05-29 14:30 | 3.83 | 3.78
2019-05-29 15:00 | 4.47 | 4.42
2019-05-29 15:30 | 5.33 | 5.29
2019-05-29 16:00 | 6.63 | 6.6
2019-05-29 16:30 | 8.17 | 8.14
2019-05-29 17:00 | 9.88 | 9.87
2019-05-29 17:30 | 11.41 | 11.4
2019-05-29 18:00 | 12.67 | 12.67
2019-05-29 18:30 | 12.87 | 12.86
2019-05-29 19:00 | 13.22 | 13.22
2019-05-29 19:30 | 13.25 | 13.25
2019-05-29 20:00 | 13.24 | 13.24
2019-05-29 20:30 | 13.29 | 13.29
2019-05-29 21:00 | 12.82 | 12.82
2019-05-29 21:30 | 11.86 | 11.86
2019-05-29 22:00 | 10.79 | 10.78
2019-05-29 22:30 | 9.72 | 9.7
2019-05-29 23:00 | 9.08 | 9.06
2019-05-29 23:30 | 8.02 | 7.99
2019-05-30 | 7.02 | 6.97
2019-05-30 00:30 | 6.25 | 6.19
2019-05-30 01:00 | 5.84 | 5.78
2019-05-30 01:30 | 5.52 | 5.44
2019-05-30 02:00 | 5.31 | 5.23
2019-05-30 02:30 | 5.12 | 5.03
2019-05-30 03:00 | 5.15 | 5.07
2019-05-30 03:30 | 5.17 | 5.08
2019-05-30 04:00 | 5.37 | 5.29
2019-05-30 04:30 | 5.6 | 5.52
2019-05-30 05:00 | 6.07 | 6
2019-05-30 05:30 | 6.91 | 6.86
2019-05-30 06:00 | 8.01 | 7.99
2019-05-30 06:30 | 9.17 | 9.15
2019-05-30 07:00 | 10.02 | 10
2019-05-30 07:30 | 10.35 | 10.33
2019-05-30 08:00 | 9.56 | 9.55
2019-05-30 08:30 | 7.83 | 7.8
2019-05-30 09:00 | 6.22 | 6.18
2019-05-30 09:30 | 5.21 | 5.18
2019-05-30 10:00 | 4.44 | 4.4
2019-05-30 10:30 | 3.76 | 3.71
2019-05-30 11:00 | 3.2 | 3.14
2019-05-30 11:30 | 2.91 | 2.84
2019-05-30 12:00 | 2.7 | 2.64
2019-05-30 12:30 | 2.69 | 2.63
2019-05-30 13:00 | 2.84 | 2.8
2019-05-30 13:30 | 2.82 | 2.77
2019-05-30 14:00 | 3.32 | 3.26
2019-05-30 14:30 | 3.85 | 3.8
2019-05-30 15:00 | 4.44 | 4.4
2019-05-30 15:30 | 5.34 | 5.3
2019-05-30 16:00 | 6.69 | 6.66
2019-05-30 16:30 | 8.12 | 8.1
2019-05-30 17:00 | 9.86 | 9.85
2019-05-30 17:30 | 11.6 | 11.6
2019-05-30 18:00 | 12.87 | 12.87
2019-05-30 18:30 | 13.21 | 13.2
2019-05-30 19:00 | 13.46 | 13.46
2019-05-30 19:30 | 13.31 | 13.3
2019-05-30 20:00 | 13.3 | 13.3
2019-05-30 20:30 | 13.39 | 13.39
2019-05-30 21:00 | 13.1 | 13.1
2019-05-30 21:30 | 12.2 | 12.2
2019-05-30 22:00 | 10.99 | 10.98
2019-05-30 22:30 | 10.06 | 10.04
2019-05-30 23:00 | 9.48 | 9.46
2019-05-30 23:30 | 8.37 | 8.34
2019-05-31 | 7.45 | 7.4
2019-05-31 00:30 | 6.77 | 6.72
2019-05-31 01:00 | 6.35 | 6.29
2019-05-31 01:30 | 6 | 5.93
2019-05-31 02:00 | 5.77 | 5.7
2019-05-31 02:30 | 5.74 | 5.67
2019-05-31 03:00 | 5.78 | 5.71
2019-05-31 03:30 | 5.85 | 5.78
2019-05-31 04:00 | 6 | 5.94
2019-05-31 04:30 | 6.39 | 6.33
2019-05-31 05:00 | 6.96 | 6.91
2019-05-31 05:30 | 7.86 | 7.83
2019-05-31 06:00 | 8.74 | 8.72
2019-05-31 06:30 | 9.79 | 9.77
2019-05-31 07:00 | 11.28 | 11.27
2019-05-31 07:30 | 11.87 | 11.87
2019-05-31 08:00 | 10.67 | 10.66
2019-05-31 08:30 | 8.83 | 8.82
2019-05-31 09:00 | 7.23 | 7.21
2019-05-31 09:30 | 5.69 | 5.66
2019-05-31 10:00 | 5.38 | 5.35
2019-05-31 10:30 | 4.41 | 4.36
2019-05-31 11:00 | 3.51 | 3.44
2019-05-31 11:30 | 2.96 | 2.87
2019-05-31 12:00 | 2.81 | 2.72
2019-05-31 12:30 | 2.77 | 2.67
2019-05-31 13:00 | 2.74 | 2.64
2019-05-31 13:30 | 2.83 | 2.73
2019-05-31 14:00 | 3.31 | 3.22
2019-05-31 14:30 | 4.06 | 3.98
2019-05-31 15:00 | 4.5 | 4.42
2019-05-31 15:30 | 5.87 | 5.8
2019-05-31 16:00 | 7.37 | 7.32
2019-05-31 16:30 | 8.85 | 8.82
2019-05-31 17:00 | 10.46 | 10.44
2019-05-31 17:30 | 12.22 | 12.22
2019-05-31 18:00 | 13.24 | 13.24
2019-05-31 18:30 | 13.66 | 13.66
2019-05-31 19:00 | 14.3 | 14.29
2019-05-31 19:30 | 14.23 | 14.23
2019-05-31 20:00 | 14.34 | 14.34
2019-05-31 20:30 | 14.54 | 14.54
2019-05-31 21:00 | 14.16 | 14.16
2019-05-31 21:30 | 13.27 | 13.27
2019-05-31 22:00 | 12.54 | 12.53
2019-05-31 22:30 | 11.86 | 11.86
2019-05-31 23:00 | 11.45 | 11.45
2019-05-31 23:30 | 10.23 | 10.21
2019-06-01 | 9.07 | 9.05
2019-06-01 00:30 | 8.23 | 8.2
2019-06-01 01:00 | 7.75 | 7.71
2019-06-01 01:30 | 7.28 | 7.25
2019-06-01 02:00 | 6.97 | 6.93
2019-06-01 02:30 | 6.81 | 6.76
2019-06-01 03:00 | 6.63 | 6.58
2019-06-01 03:30 | 6.71 | 6.66
2019-06-01 04:00 | 6.66 | 6.61
2019-06-01 04:30 | 6.84 | 6.79
2019-06-01 05:00 | 7 | 6.96
2019-06-01 05:30 | 7.42 | 7.38
2019-06-01 06:00 | 7.73 | 7.7
2019-06-01 06:30 | 8.26 | 8.23
2019-06-01 07:00 | 9.07 | 9.03
2019-06-01 07:30 | 10.22 | 10.2
2019-06-01 08:00 | 9.94 | 9.92
2019-06-01 08:30 | 9.59 | 9.57
2019-06-01 09:00 | 9.05 | 9.04
2019-06-01 09:30 | 8.26 | 8.24
2019-06-01 10:00 | 7.34 | 7.32
2019-06-01 10:30 | 6.25 | 6.23
2019-06-01 11:00 | 5.37 | 5.34
2019-06-01 11:30 | 4.68 | 4.65
2019-06-01 12:00 | 4.26 | 4.21
2019-06-01 12:30 | 5.33 | 5.29
2019-06-01 13:00 | 6.44 | 6.4
2019-06-01 13:30 | 6.27 | 6.23
2019-06-01 14:00 | 6.25 | 6.21
2019-06-01 14:30 | 6.36 | 6.32
2019-06-01 15:00 | 7.45 | 7.41
2019-06-01 15:30 | 7.87 | 7.83
2019-06-01 16:00 | 8.49 | 8.46
2019-06-01 16:30 | 9.59 | 9.57
2019-06-01 17:00 | 10.7 | 10.69
2019-06-01 17:30 | 11.8 | 11.8
2019-06-01 18:00 | 12.21 | 12.2
2019-06-01 18:30 | 12.21 | 12.21
2019-06-01 19:00 | 12.15 | 12.15
2019-06-01 19:30 | 11.69 | 11.68
2019-06-01 20:00 | 11.7 | 11.69
2019-06-01 20:30 | 11.56 | 11.56
2019-06-01 21:00 | 11 | 11
2019-06-01 21:30 | 10.34 | 10.33
2019-06-01 22:00 | 9.83 | 9.82
2019-06-01 22:30 | 9.46 | 9.44
2019-06-01 23:00 | 9.14 | 9.12
2019-06-01 23:30 | 8.22 | 8.19
2019-06-02 | 7.31 | 7.27
2019-06-02 00:30 | 6.62 | 6.57
2019-06-02 01:00 | 6.11 | 6.05
2019-06-02 01:30 | 5.69 | 5.63
2019-06-02 02:00 | 5.33 | 5.25
2019-06-02 02:30 | 5.13 | 5.05
2019-06-02 03:00 | 4.92 | 4.84
2019-06-02 03:30 | 4.84 | 4.76
2019-06-02 04:00 | 4.87 | 4.79
2019-06-02 04:30 | 4.98 | 4.9
2019-06-02 05:00 | 4.89 | 4.81
2019-06-02 05:30 | 5.09 | 5.01
2019-06-02 06:00 | 5.31 | 5.24
2019-06-02 06:30 | 5.53 | 5.45
2019-06-02 07:00 | 5.77 | 5.65
2019-06-02 07:30 | 5.65 | 5.53
2019-06-02 08:00 | 6.21 | 6.12
2019-06-02 08:30 | 6.54 | 6.47
2019-06-02 09:00 | 5.54 | 5.48
2019-06-02 09:30 | 6.04 | 5.99
2019-06-02 10:00 | 7.71 | 7.67
2019-06-02 10:30 | 6.36 | 6.33
2019-06-02 11:00 | 5.86 | 5.83
2019-06-02 11:30 | 6.06 | 6.04
2019-06-02 12:00 | 7.48 | 7.46
2019-06-02 12:30 | 7.79 | 7.76
2019-06-02 13:00 | 8.57 | 8.53
2019-06-02 13:30 | 8.5 | 8.46
2019-06-02 14:00 | 6.82 | 6.78
2019-06-02 14:30 | 5.77 | 5.72
2019-06-02 15:00 | 6.77 | 6.73
2019-06-02 15:30 | 7.25 | 7.21
2019-06-02 16:00 | 8 | 7.96
2019-06-02 16:30 | 9.2 | 9.17
2019-06-02 17:00 | 10.86 | 10.84
2019-06-02 17:30 | 12.57 | 12.56
2019-06-02 18:00 | 13.15 | 13.14
2019-06-02 18:30 | 12.81 | 12.81
2019-06-02 19:00 | 12.57 | 12.56
2019-06-02 19:30 | 12.12 | 12.11
2019-06-02 20:00 | 11.79 | 11.79
2019-06-02 20:30 | 11.81 | 11.81
2019-06-02 21:00 | 11.12 | 11.1
2019-06-02 21:30 | 10.39 | 10.38
2019-06-02 22:00 | 9.71 | 9.69
2019-06-02 22:30 | 9.04 | 9.02
2019-06-02 23:00 | 8.55 | 8.52
2019-06-02 23:30 | 7.63 | 7.59
2019-06-03 | 6.72 | 6.67
2019-06-03 00:30 | 5.99 | 5.93
2019-06-03 01:00 | 5.62 | 5.55
2019-06-03 01:30 | 5.22 | 5.15
2019-06-03 02:00 | 4.99 | 4.91
2019-06-03 02:30 | 4.8 | 4.71
2019-06-03 03:00 | 4.77 | 4.7
2019-06-03 03:30 | 4.72 | 4.64
2019-06-03 04:00 | 4.8 | 4.71
2019-06-03 04:30 | 4.98 | 4.9
2019-06-03 05:00 | 5.46 | 5.39
2019-06-03 05:30 | 6.05 | 6
2019-06-03 06:00 | 6.46 | 6.41
2019-06-03 06:30 | 7.26 | 7.22
2019-06-03 07:00 | 8.26 | 8.22
2019-06-03 07:30 | 8.88 | 8.86
2019-06-03 08:00 | 8.32 | 8.3
2019-06-03 08:30 | 7.43 | 7.4
2019-06-03 09:00 | 5.94 | 5.91
2019-06-03 09:30 | 5.21 | 5.18
2019-06-03 10:00 | 4.71 | 4.68
2019-06-03 10:30 | 3.96 | 3.93
2019-06-03 11:00 | 4.93 | 4.9
2019-06-03 11:30 | 4 | 3.96
2019-06-03 12:00 | 3.08 | 3.04
2019-06-03 12:30 | 3.12 | 3.08
2019-06-03 13:00 | 3.26 | 3.22
2019-06-03 13:30 | 3.36 | 3.33
2019-06-03 14:00 | 3.66 | 3.62
2019-06-03 14:30 | 4.26 | 4.22
2019-06-03 15:00 | 5.04 | 5.01
2019-06-03 15:30 | 6 | 5.97
2019-06-03 16:00 | 7.39 | 7.36
2019-06-03 16:30 | 8.92 | 8.9
2019-06-03 17:00 | 10.67 | 10.66
2019-06-03 17:30 | 12.39 | 12.39
2019-06-03 18:00 | 13.65 | 13.65
2019-06-03 18:30 | 13.81 | 13.81
2019-06-03 19:00 | 13.97 | 13.97
2019-06-03 19:30 | 13.47 | 13.47
2019-06-03 20:00 | 13.15 | 13.15
2019-06-03 20:30 | 12.95 | 12.95
2019-06-03 21:00 | 12.63 | 12.63
2019-06-03 21:30 | 11.89 | 11.89
2019-06-03 22:00 | 10.99 | 10.98
2019-06-03 22:30 | 9.99 | 9.98
2019-06-03 23:00 | 9.1 | 9.07
2019-06-03 23:30 | 8.05 | 8.01
2019-06-04 | 7.25 | 7.21
2019-06-04 00:30 | 6.45 | 6.39
2019-06-04 01:00 | 5.99 | 5.93
2019-06-04 01:30 | 5.76 | 5.68
2019-06-04 02:00 | 5.46 | 5.38
2019-06-04 02:30 | 5.39 | 5.31
2019-06-04 03:00 | 5.36 | 5.28
2019-06-04 03:30 | 5.33 | 5.24
2019-06-04 04:00 | 5.49 | 5.41
2019-06-04 04:30 | 5.82 | 5.75
2019-06-04 05:00 | 6.26 | 6.2
2019-06-04 05:30 | 7.16 | 7.12
2019-06-04 06:00 | 8.03 | 8
2019-06-04 06:30 | 9.07 | 9.05
2019-06-04 07:00 | 10.27 | 10.25
2019-06-04 07:30 | 10.55 | 10.54
2019-06-04 08:00 | 10.1 | 10.09
2019-06-04 08:30 | 8.56 | 8.54
2019-06-04 09:00 | 7.18 | 7.16
2019-06-04 09:30 | 6.06 | 6.04
2019-06-04 10:00 | 5.57 | 5.54
2019-06-04 10:30 | 4.79 | 4.76
2019-06-04 11:00 | 4.33 | 4.3
2019-06-04 11:30 | 3.94 | 3.9
2019-06-04 12:00 | 3.85 | 3.82
2019-06-04 12:30 | 3.89 | 3.86
2019-06-04 13:00 | 3.99 | 3.96
2019-06-04 13:30 | 4.1 | 4.06
2019-06-04 14:00 | 4.54 | 4.5
2019-06-04 14:30 | 6.34 | 6.31
2019-06-04 15:00 | 6.69 | 6.67
2019-06-04 15:30 | 6.79 | 6.77
2019-06-04 16:00 | 8.55 | 8.53
2019-06-04 16:30 | 10.4 | 10.38
2019-06-04 17:00 | 12.63 | 12.62
2019-06-04 17:30 | 14.93 | 14.93
2019-06-04 18:00 | 16.94 | 16.93
2019-06-04 18:30 | 17.67 | 17.66
2019-06-04 19:00 | 17.78 | 17.77
2019-06-04 19:30 | 17.15 | 17.14
2019-06-04 20:00 | 17.05 | 17.05
2019-06-04 20:30 | 17.01 | 17
2019-06-04 21:00 | 16 | 15.99
2019-06-04 21:30 | 14.69 | 14.69
2019-06-04 22:00 | 13.26 | 13.26
2019-06-04 22:30 | 11.74 | 11.74
2019-06-04 23:00 | 10.76 | 10.75
2019-06-04 23:30 | 9.58 | 9.56
2019-06-05 | 8.44 | 8.41
2019-06-05 00:30 | 7.6 | 7.56
2019-06-05 01:00 | 7.07 | 7.02
2019-06-05 01:30 | 6.71 | 6.66
2019-06-05 02:00 | 6.48 | 6.42
2019-06-05 02:30 | 6.28 | 6.22
2019-06-05 03:00 | 6.27 | 6.22
2019-06-05 03:30 | 6.18 | 6.11
2019-06-05 04:00 | 6.19 | 6.13
2019-06-05 04:30 | 6.6 | 6.54
2019-06-05 05:00 | 7.15 | 7.1
2019-06-05 05:30 | 8.18 | 8.16
2019-06-05 06:00 | 9.34 | 9.33
2019-06-05 06:30 | 10.8 | 10.79
2019-06-05 07:00 | 12.08 | 12.07
2019-06-05 07:30 | 12.22 | 12.22
2019-06-05 08:00 | 11.32 | 11.32
2019-06-05 08:30 | 9.46 | 9.45
2019-06-05 09:00 | 7.72 | 7.71
2019-06-05 09:30 | 6.51 | 6.5
2019-06-05 10:00 | 5.51 | 5.49
2019-06-05 10:30 | 4.69 | 4.66
2019-06-05 11:00 | 4.13 | 4.08
2019-06-05 11:30 | 3.73 | 3.69
2019-06-05 12:00 | 3.65 | 3.61
2019-06-05 12:30 | 3.53 | 3.49
2019-06-05 13:00 | 3.31 | 3.26
2019-06-05 13:30 | 3.43 | 3.38
2019-06-05 14:00 | 4.45 | 4.4
2019-06-05 14:30 | 5.28 | 5.25
2019-06-05 15:00 | 6.23 | 6.2
2019-06-05 15:30 | 6.68 | 6.65
2019-06-05 16:00 | 7.42 | 7.39
2019-06-05 16:30 | 8.67 | 8.65
2019-06-05 17:00 | 10.28 | 10.27
2019-06-05 17:30 | 12.26 | 12.25
2019-06-05 18:00 | 13.43 | 13.43
2019-06-05 18:30 | 14.17 | 14.17
2019-06-05 19:00 | 14.42 | 14.42
2019-06-05 19:30 | 14.27 | 14.26
2019-06-05 20:00 | 14.25 | 14.25
2019-06-05 20:30 | 14.26 | 14.26
2019-06-05 21:00 | 13.49 | 13.49
2019-06-05 21:30 | 12.51 | 12.5
2019-06-05 22:00 | 11.33 | 11.32
2019-06-05 22:30 | 10.56 | 10.55
2019-06-05 23:00 | 10.12 | 10.1
2019-06-05 23:30 | 8.91 | 8.89
2019-06-06 | 7.98 | 7.95
2019-06-06 00:30 | 7.07 | 7.02
2019-06-06 01:00 | 6.51 | 6.45
2019-06-06 01:30 | 6.26 | 6.2
2019-06-06 02:00 | 5.95 | 5.88
2019-06-06 02:30 | 5.76 | 5.69
2019-06-06 03:00 | 5.73 | 5.65
2019-06-06 03:30 | 5.71 | 5.64
2019-06-06 04:00 | 5.86 | 5.8
2019-06-06 04:30 | 6.12 | 6.06
2019-06-06 05:00 | 6.71 | 6.66
2019-06-06 05:30 | 7.43 | 7.39
2019-06-06 06:00 | 8.47 | 8.45
2019-06-06 06:30 | 9.62 | 9.61
2019-06-06 07:00 | 10.52 | 10.51
2019-06-06 07:30 | 10.86 | 10.85
2019-06-06 08:00 | 10.06 | 10.05
2019-06-06 08:30 | 8.35 | 8.34
2019-06-06 09:00 | 6.65 | 6.62
2019-06-06 09:30 | 5.59 | 5.57
2019-06-06 10:00 | 4.76 | 4.72
2019-06-06 10:30 | 4.07 | 4.02
2019-06-06 11:00 | 3.57 | 3.51
2019-06-06 11:30 | 3.37 | 3.3
2019-06-06 12:00 | 3.07 | 3.02
2019-06-06 12:30 | 3.84 | 3.8
2019-06-06 13:00 | 4.61 | 4.57
2019-06-06 13:30 | 3.91 | 3.86
2019-06-06 14:00 | 3.94 | 3.89
2019-06-06 14:30 | 4.56 | 4.52
2019-06-06 15:00 | 5.98 | 5.96
2019-06-06 15:30 | 6.31 | 6.28
2019-06-06 16:00 | 7.65 | 7.62
2019-06-06 16:30 | 8.73 | 8.71
2019-06-06 17:00 | 10.11 | 10.1
2019-06-06 17:30 | 11.85 | 11.85
2019-06-06 18:00 | 12.97 | 12.97
2019-06-06 18:30 | 13.25 | 13.25
2019-06-06 19:00 | 13.63 | 13.63
2019-06-06 19:30 | 13.67 | 13.67
2019-06-06 20:00 | 13.76 | 13.76
2019-06-06 20:30 | 13.76 | 13.76
2019-06-06 21:00 | 13.18 | 13.18
2019-06-06 21:30 | 12.4 | 12.4
2019-06-06 22:00 | 11.53 | 11.53
2019-06-06 22:30 | 10.78 | 10.77
2019-06-06 23:00 | 10.27 | 10.25
2019-06-06 23:30 | 9.03 | 9.01
2019-06-07 | 7.95 | 7.91
2019-06-07 00:30 | 7.13 | 7.08
2019-06-07 01:00 | 6.66 | 6.6
2019-06-07 01:30 | 6.2 | 6.13
2019-06-07 02:00 | 5.94 | 5.88
2019-06-07 02:30 | 5.82 | 5.75
2019-06-07 03:00 | 5.72 | 5.65
2019-06-07 03:30 | 5.82 | 5.75
2019-06-07 04:00 | 5.85 | 5.78
2019-06-07 04:30 | 6.21 | 6.15
2019-06-07 05:00 | 6.74 | 6.69
2019-06-07 05:30 | 7.47 | 7.44
2019-06-07 06:00 | 8.54 | 8.52
2019-06-07 06:30 | 9.65 | 9.64
2019-06-07 07:00 | 10.8 | 10.78
2019-06-07 07:30 | 11.32 | 11.31
2019-06-07 08:00 | 10.94 | 10.93
2019-06-07 08:30 | 10.1 | 10.08
2019-06-07 09:00 | 8.06 | 8.04
2019-06-07 09:30 | 6.87 | 6.84
2019-06-07 10:00 | 5.86 | 5.82
2019-06-07 10:30 | 4.88 | 4.83
2019-06-07 11:00 | 4.36 | 4.29
2019-06-07 11:30 | 4.61 | 4.55
2019-06-07 12:00 | 5.46 | 5.42
2019-06-07 12:30 | 7.12 | 7.08
2019-06-07 13:00 | 7.3 | 7.26
2019-06-07 13:30 | 7.42 | 7.39
2019-06-07 14:00 | 6.84 | 6.8
2019-06-07 14:30 | 7.15 | 7.12
2019-06-07 15:00 | 7.5 | 7.46
2019-06-07 15:30 | 7.43 | 7.4
2019-06-07 16:00 | 8.43 | 8.4
2019-06-07 16:30 | 9.02 | 8.99
2019-06-07 17:00 | 10.15 | 10.13
2019-06-07 17:30 | 11.74 | 11.73
2019-06-07 18:00 | 12.7 | 12.7
2019-06-07 18:30 | 12.96 | 12.96
2019-06-07 19:00 | 13.23 | 13.22
2019-06-07 19:30 | 13.2 | 13.19
2019-06-07 20:00 | 13.23 | 13.23
2019-06-07 20:30 | 13.43 | 13.43
2019-06-07 21:00 | 12.83 | 12.82
2019-06-07 21:30 | 12.09 | 12.08
2019-06-07 22:00 | 11.29 | 11.28
2019-06-07 22:30 | 10.76 | 10.75
2019-06-07 23:00 | 10.12 | 10.1
2019-06-07 23:30 | 9.05 | 9.03
2019-06-08 | 8.07 | 8.03
2019-06-08 00:30 | 7.18 | 7.13
2019-06-08 01:00 | 6.76 | 6.71
2019-06-08 01:30 | 6.31 | 6.25
2019-06-08 02:00 | 5.8 | 5.72
2019-06-08 02:30 | 5.63 | 5.55
2019-06-08 03:00 | 5.55 | 5.47
2019-06-08 03:30 | 5.42 | 5.34
2019-06-08 04:00 | 5.32 | 5.24
2019-06-08 04:30 | 5.41 | 5.33
2019-06-08 05:00 | 5.49 | 5.41
2019-06-08 05:30 | 5.67 | 5.6
2019-06-08 06:00 | 6.01 | 5.95
2019-06-08 06:30 | 6.27 | 6.21
2019-06-08 07:00 | 6.92 | 6.83
2019-06-08 07:30 | 7.54 | 7.47
2019-06-08 08:00 | 7.77 | 7.71
2019-06-08 08:30 | 8.57 | 8.53
2019-06-08 09:00 | 8.85 | 8.82
2019-06-08 09:30 | 9.47 | 9.45
2019-06-08 10:00 | 9.48 | 9.46
2019-06-08 10:30 | 9.37 | 9.34
2019-06-08 11:00 | 9.37 | 9.34
2019-06-08 11:30 | 9.74 | 9.71
2019-06-08 12:00 | 9.91 | 9.88
2019-06-08 12:30 | 10.15 | 10.13
2019-06-08 13:00 | 9.18 | 9.15
2019-06-08 13:30 | 9.8 | 9.77
2019-06-08 14:00 | 10.11 | 10.08
2019-06-08 14:30 | 10.33 | 10.31
2019-06-08 15:00 | 10.63 | 10.62
2019-06-08 15:30 | 10.89 | 10.88
2019-06-08 16:00 | 11.13 | 11.11
2019-06-08 16:30 | 11.58 | 11.57
2019-06-08 17:00 | 12.49 | 12.48
2019-06-08 17:30 | 13.7 | 13.69
2019-06-08 18:00 | 14.03 | 14.02
2019-06-08 18:30 | 13.75 | 13.74
2019-06-08 19:00 | 13.76 | 13.75
2019-06-08 19:30 | 13.22 | 13.21
2019-06-08 20:00 | 12.95 | 12.95
2019-06-08 20:30 | 12.95 | 12.94
2019-06-08 21:00 | 12.27 | 12.27
2019-06-08 21:30 | 11.51 | 11.51
2019-06-08 22:00 | 10.73 | 10.72
2019-06-08 22:30 | 10.32 | 10.3
2019-06-08 23:00 | 9.96 | 9.94
2019-06-08 23:30 | 9.04 | 9.01
2019-06-09 | 7.96 | 7.92
2019-06-09 00:30 | 7.08 | 7.03
2019-06-09 01:00 | 6.62 | 6.56
2019-06-09 01:30 | 6.19 | 6.13
2019-06-09 02:00 | 5.73 | 5.66
2019-06-09 02:30 | 5.42 | 5.35
2019-06-09 03:00 | 5.34 | 5.26
2019-06-09 03:30 | 5.22 | 5.14
2019-06-09 04:00 | 5.22 | 5.14
2019-06-09 04:30 | 5.15 | 5.06
2019-06-09 05:00 | 5.16 | 5.07
2019-06-09 05:30 | 5.4 | 5.32
2019-06-09 06:00 | 5.55 | 5.48
2019-06-09 06:30 | 5.81 | 5.74
2019-06-09 07:00 | 6.09 | 5.99
2019-06-09 07:30 | 6.55 | 6.46
2019-06-09 08:00 | 7.21 | 7.14
2019-06-09 08:30 | 7.6 | 7.54
2019-06-09 09:00 | 7.55 | 7.51
2019-06-09 09:30 | 6.48 | 6.43
2019-06-09 10:00 | 6.01 | 5.97
2019-06-09 10:30 | 5.44 | 5.39
2019-06-09 11:00 | 4.93 | 4.89
2019-06-09 11:30 | 4.72 | 4.67
2019-06-09 12:00 | 4.46 | 4.41
2019-06-09 12:30 | 4.5 | 4.46
2019-06-09 13:00 | 4.26 | 4.22
2019-06-09 13:30 | 4.06 | 4.02
2019-06-09 14:00 | 4.14 | 4.1
2019-06-09 14:30 | 5.11 | 5.08
2019-06-09 15:00 | 7.59 | 7.56
2019-06-09 15:30 | 7.75 | 7.72
2019-06-09 16:00 | 8.17 | 8.13
2019-06-09 16:30 | 8.93 | 8.9
2019-06-09 17:00 | 10.19 | 10.16
2019-06-09 17:30 | 11.63 | 11.62
2019-06-09 18:00 | 12.55 | 12.55
2019-06-09 18:30 | 12.54 | 12.54
2019-06-09 19:00 | 12.3 | 12.3
2019-06-09 19:30 | 11.98 | 11.98
2019-06-09 20:00 | 11.94 | 11.94
2019-06-09 20:30 | 11.85 | 11.84
2019-06-09 21:00 | 11.25 | 11.24
2019-06-09 21:30 | 10.55 | 10.53
2019-06-09 22:00 | 9.72 | 9.7
2019-06-09 22:30 | 9.09 | 9.06
2019-06-09 23:00 | 8.78 | 8.75
2019-06-09 23:30 | 7.88 | 7.84
2019-06-10 | 7.03 | 6.98
2019-06-10 00:30 | 6.22 | 6.15
2019-06-10 01:00 | 5.79 | 5.72
2019-06-10 01:30 | 5.44 | 5.37
2019-06-10 02:00 | 5.06 | 4.97
2019-06-10 02:30 | 4.9 | 4.81
2019-06-10 03:00 | 4.81 | 4.72
2019-06-10 03:30 | 4.84 | 4.74
2019-06-10 04:00 | 4.94 | 4.85
2019-06-10 04:30 | 5.35 | 5.27
2019-06-10 05:00 | 5.64 | 5.57
2019-06-10 05:30 | 6.29 | 6.25
2019-06-10 06:00 | 6.83 | 6.79
2019-06-10 06:30 | 7.77 | 7.74
2019-06-10 07:00 | 8.55 | 8.51
2019-06-10 07:30 | 8.89 | 8.86
2019-06-10 08:00 | 8.16 | 8.12
2019-06-10 08:30 | 6.81 | 6.76
2019-06-10 09:00 | 5.51 | 5.45
2019-06-10 09:30 | 4.73 | 4.68
2019-06-10 10:00 | 4.11 | 4.06
2019-06-10 10:30 | 3.47 | 3.41
2019-06-10 11:00 | 3.04 | 2.96
2019-06-10 11:30 | 2.75 | 2.66
2019-06-10 12:00 | 2.62 | 2.53
2019-06-10 12:30 | 2.71 | 2.64
2019-06-10 13:00 | 3.06 | 3
2019-06-10 13:30 | 3.44 | 3.4
2019-06-10 14:00 | 3.66 | 3.61
2019-06-10 14:30 | 4.05 | 4
2019-06-10 15:00 | 4.67 | 4.63
2019-06-10 15:30 | 5.59 | 5.55
2019-06-10 16:00 | 6.84 | 6.82
2019-06-10 16:30 | 8.23 | 8.21
2019-06-10 17:00 | 9.77 | 9.76
2019-06-10 17:30 | 11.48 | 11.47
2019-06-10 18:00 | 12.5 | 12.5
2019-06-10 18:30 | 12.51 | 12.5
2019-06-10 19:00 | 12.56 | 12.56
2019-06-10 19:30 | 12.19 | 12.19
2019-06-10 20:00 | 11.98 | 11.97
2019-06-10 20:30 | 11.91 | 11.91
2019-06-10 21:00 | 11.45 | 11.45
2019-06-10 21:30 | 10.44 | 10.42
2019-06-10 22:00 | 9.6 | 9.59
2019-06-10 22:30 | 8.92 | 8.9
2019-06-10 23:00 | 8.46 | 8.44
2019-06-10 23:30 | 7.46 | 7.41
2019-06-11 | 6.6 | 6.55
2019-06-11 00:30 | 5.82 | 5.75
2019-06-11 01:00 | 5.44 | 5.36
2019-06-11 01:30 | 5.13 | 5.04
2019-06-11 02:00 | 4.96 | 4.87
2019-06-11 02:30 | 4.81 | 4.71
2019-06-11 03:00 | 4.78 | 4.68
2019-06-11 03:30 | 4.82 | 4.72
2019-06-11 04:00 | 4.87 | 4.77
2019-06-11 04:30 | 5.14 | 5.05
2019-06-11 05:00 | 5.57 | 5.5
2019-06-11 05:30 | 6.16 | 6.1
2019-06-11 06:00 | 6.87 | 6.82
2019-06-11 06:30 | 7.65 | 7.61
2019-06-11 07:00 | 8.69 | 8.64
2019-06-11 07:30 | 9.04 | 9
2019-06-11 08:00 | 8.14 | 8.1
2019-06-11 08:30 | 6.72 | 6.67
2019-06-11 09:00 | 5.53 | 5.47
2019-06-11 09:30 | 4.73 | 4.67
2019-06-11 10:00 | 4.37 | 4.32
2019-06-11 10:30 | 3.66 | 3.6
2019-06-11 11:00 | 3.19 | 3.13
2019-06-11 11:30 | 2.96 | 2.91
2019-06-11 12:00 | 2.92 | 2.87
2019-06-11 12:30 | 2.97 | 2.92
2019-06-11 13:00 | 3.04 | 2.99
2019-06-11 13:30 | 3.31 | 3.28
2019-06-11 14:00 | 3.65 | 3.62
2019-06-11 14:30 | 4.26 | 4.24
2019-06-11 15:00 | 4.9 | 4.88
2019-06-11 15:30 | 5.8 | 5.79
2019-06-11 16:00 | 7.19 | 7.18
2019-06-11 16:30 | 8.43 | 8.41
2019-06-11 17:00 | 9.8 | 9.79
2019-06-11 17:30 | 11.52 | 11.52
2019-06-11 18:00 | 12.72 | 12.72
2019-06-11 18:30 | 12.77 | 12.77
2019-06-11 19:00 | 12.96 | 12.96
2019-06-11 19:30 | 12.77 | 12.77
2019-06-11 20:00 | 12.54 | 12.54
2019-06-11 20:30 | 12.5 | 12.5
2019-06-11 21:00 | 12.09 | 12.09
2019-06-11 21:30 | 11.04 | 11.04
2019-06-11 22:00 | 10.2 | 10.19
2019-06-11 22:30 | 9.28 | 9.26
2019-06-11 23:00 | 8.63 | 8.61
2019-06-11 23:30 | 7.83 | 7.8
2019-06-12 | 6.95 | 6.91
2019-06-12 00:30 | 6.15 | 6.09
2019-06-12 01:00 | 5.82 | 5.75
2019-06-12 01:30 | 5.39 | 5.31
2019-06-12 02:00 | 5.02 | 4.93
2019-06-12 02:30 | 4.94 | 4.84
2019-06-12 03:00 | 4.85 | 4.75
2019-06-12 03:30 | 4.86 | 4.76
2019-06-12 04:00 | 5.01 | 4.92
2019-06-12 04:30 | 5.36 | 5.28
2019-06-12 05:00 | 5.79 | 5.73
2019-06-12 05:30 | 6.48 | 6.44
2019-06-12 06:00 | 7.22 | 7.18
2019-06-12 06:30 | 8.17 | 8.15
2019-06-12 07:00 | 9.54 | 9.51
2019-06-12 07:30 | 9.89 | 9.86
2019-06-12 08:00 | 9.1 | 9.08
2019-06-12 08:30 | 7.72 | 7.69
2019-06-12 09:00 | 6.09 | 6.05
2019-06-12 09:30 | 5.28 | 5.24
2019-06-12 10:00 | 4.48 | 4.43
2019-06-12 10:30 | 3.77 | 3.71
2019-06-12 11:00 | 4.8 | 4.76
2019-06-12 11:30 | 5.14 | 5.1
2019-06-12 12:00 | 4.29 | 4.24
2019-06-12 12:30 | 3.45 | 3.4
2019-06-12 13:00 | 4.07 | 4.03
2019-06-12 13:30 | 5.91 | 5.88
2019-06-12 14:00 | 5.33 | 5.3
2019-06-12 14:30 | 5.33 | 5.31
2019-06-12 15:00 | 6.08 | 6.05
2019-06-12 15:30 | 5.63 | 5.6
2019-06-12 16:00 | 7.22 | 7.19
2019-06-12 16:30 | 7.97 | 7.95
2019-06-12 17:00 | 9.75 | 9.73
2019-06-12 17:30 | 11.46 | 11.46
2019-06-12 18:00 | 12.57 | 12.57
2019-06-12 18:30 | 12.79 | 12.79
2019-06-12 19:00 | 12.87 | 12.87
2019-06-12 19:30 | 12.33 | 12.32
2019-06-12 20:00 | 12.82 | 12.82
2019-06-12 20:30 | 12.93 | 12.93
2019-06-12 21:00 | 12.42 | 12.42
2019-06-12 21:30 | 11.55 | 11.55
2019-06-12 22:00 | 10.37 | 10.35
2019-06-12 22:30 | 9.54 | 9.53
2019-06-12 23:00 | 8.89 | 8.86
2019-06-12 23:30 | 7.92 | 7.89
2019-06-13 | 7.06 | 7.02
2019-06-13 00:30 | 6.28 | 6.22
2019-06-13 01:00 | 5.82 | 5.75
2019-06-13 01:30 | 5.44 | 5.37
2019-06-13 02:00 | 5.11 | 5.03
2019-06-13 02:30 | 5.03 | 4.95
2019-06-13 03:00 | 4.88 | 4.78
2019-06-13 03:30 | 4.87 | 4.78
2019-06-13 04:00 | 4.93 | 4.84
2019-06-13 04:30 | 5.11 | 5.02
2019-06-13 05:00 | 5.51 | 5.44
2019-06-13 05:30 | 6.24 | 6.19
2019-06-13 06:00 | 7.28 | 7.25
2019-06-13 06:30 | 8.3 | 8.28
2019-06-13 07:00 | 8.99 | 8.96
2019-06-13 07:30 | 9.03 | 8.99
2019-06-13 08:00 | 8.38 | 8.35
2019-06-13 08:30 | 7.55 | 7.51
2019-06-13 09:00 | 6.04 | 6
2019-06-13 09:30 | 4.97 | 4.93
2019-06-13 10:00 | 5.35 | 5.32
2019-06-13 10:30 | 4.89 | 4.85
2019-06-13 11:00 | 4.1 | 4.07
2019-06-13 11:30 | 3.4 | 3.37
2019-06-13 12:00 | 3.53 | 3.49
2019-06-13 12:30 | 5.08 | 5.06
2019-06-13 13:00 | 5.62 | 5.6
2019-06-13 13:30 | 5.78 | 5.76
2019-06-13 14:00 | 4.61 | 4.58
2019-06-13 14:30 | 5.34 | 5.31
2019-06-13 15:00 | 5.01 | 4.98
2019-06-13 15:30 | 6.11 | 6.09
2019-06-13 16:00 | 6.97 | 6.95
2019-06-13 16:30 | 8 | 7.98
2019-06-13 17:00 | 9.23 | 9.22
2019-06-13 17:30 | 11.09 | 11.09
2019-06-13 18:00 | 12.14 | 12.14
2019-06-13 18:30 | 12.46 | 12.46
2019-06-13 19:00 | 12.52 | 12.52
2019-06-13 19:30 | 12.14 | 12.13
2019-06-13 20:00 | 12.23 | 12.22
2019-06-13 20:30 | 12.11 | 12.11
2019-06-13 21:00 | 11.51 | 11.5
2019-06-13 21:30 | 10.58 | 10.57
2019-06-13 22:00 | 9.82 | 9.81
2019-06-13 22:30 | 9.25 | 9.23
2019-06-13 23:00 | 8.87 | 8.84
2019-06-13 23:30 | 7.92 | 7.89
2019-06-14 | 7.04 | 6.99
2019-06-14 00:30 | 6.18 | 6.11
2019-06-14 01:00 | 5.77 | 5.7
2019-06-14 01:30 | 5.41 | 5.34
2019-06-14 02:00 | 5.07 | 4.98
2019-06-14 02:30 | 4.93 | 4.84
2019-06-14 03:00 | 4.81 | 4.72
2019-06-14 03:30 | 4.85 | 4.75
2019-06-14 04:00 | 4.98 | 4.88
2019-06-14 04:30 | 5.2 | 5.11
2019-06-14 05:00 | 5.47 | 5.39
2019-06-14 05:30 | 6.11 | 6.05
2019-06-14 06:00 | 7.13 | 7.1
2019-06-14 06:30 | 7.86 | 7.83
2019-06-14 07:00 | 8.72 | 8.68
2019-06-14 07:30 | 9.16 | 9.13
2019-06-14 08:00 | 8.73 | 8.7
2019-06-14 08:30 | 7.76 | 7.72
2019-06-14 09:00 | 6.48 | 6.44
2019-06-14 09:30 | 5.34 | 5.3
2019-06-14 10:00 | 4.56 | 4.52
2019-06-14 10:30 | 3.61 | 3.54
2019-06-14 11:00 | 2.88 | 2.81
2019-06-14 11:30 | 2.78 | 2.72
2019-06-14 12:00 | 2.85 | 2.8
2019-06-14 12:30 | 3.45 | 3.41
2019-06-14 13:00 | 4.14 | 4.11
2019-06-14 13:30 | 3.15 | 3.12
2019-06-14 14:00 | 3.87 | 3.84
2019-06-14 14:30 | 4.16 | 4.14
2019-06-14 15:00 | 4.79 | 4.77
2019-06-14 15:30 | 6.19 | 6.17
2019-06-14 16:00 | 7.13 | 7.11
2019-06-14 16:30 | 7.78 | 7.76
2019-06-14 17:00 | 8.98 | 8.97
2019-06-14 17:30 | 10.24 | 10.23
2019-06-14 18:00 | 10.87 | 10.86
2019-06-14 18:30 | 10.88 | 10.88
2019-06-14 19:00 | 11.13 | 11.13
2019-06-14 19:30 | 10.94 | 10.93
2019-06-14 20:00 | 10.7 | 10.69
2019-06-14 20:30 | 10.82 | 10.82
2019-06-14 21:00 | 10.36 | 10.35
2019-06-14 21:30 | 9.62 | 9.61
2019-06-14 22:00 | 9.01 | 8.99
2019-06-14 22:30 | 8.71 | 8.68
2019-06-14 23:00 | 8.54 | 8.51
2019-06-14 23:30 | 7.68 | 7.65
2019-06-15 | 6.75 | 6.7
2019-06-15 00:30 | 6.15 | 6.09
2019-06-15 01:00 | 5.77 | 5.7
2019-06-15 01:30 | 5.33 | 5.25
2019-06-15 02:00 | 5.02 | 4.92
2019-06-15 02:30 | 4.87 | 4.78
2019-06-15 03:00 | 4.72 | 4.62
2019-06-15 03:30 | 4.68 | 4.57
2019-06-15 04:00 | 4.65 | 4.55
2019-06-15 04:30 | 4.71 | 4.61
2019-06-15 05:00 | 4.79 | 4.69
2019-06-15 05:30 | 5.02 | 4.93
2019-06-15 06:00 | 5.31 | 5.24
2019-06-15 06:30 | 5.65 | 5.57
2019-06-15 07:00 | 6.02 | 5.91
2019-06-15 07:30 | 6.64 | 6.55
2019-06-15 08:00 | 6.5 | 6.41
2019-06-15 08:30 | 6.37 | 6.29
2019-06-15 09:00 | 6.18 | 6.12
2019-06-15 09:30 | 5.85 | 5.8
2019-06-15 10:00 | 5.39 | 5.35
2019-06-15 10:30 | 4.75 | 4.7
2019-06-15 11:00 | 4.69 | 4.66
2019-06-15 11:30 | 3.97 | 3.94
2019-06-15 12:00 | 3.82 | 3.79
2019-06-15 12:30 | 3.75 | 3.72
2019-06-15 13:00 | 4.12 | 4.08
2019-06-15 13:30 | 4.31 | 4.28
2019-06-15 14:00 | 4.93 | 4.91
2019-06-15 14:30 | 5.24 | 5.22
2019-06-15 15:00 | 5.8 | 5.78
2019-06-15 15:30 | 6.41 | 6.39
2019-06-15 16:00 | 8.1 | 8.09
2019-06-15 16:30 | 8.56 | 8.54
2019-06-15 17:00 | 9.44 | 9.43
2019-06-15 17:30 | 10.54 | 10.53
2019-06-15 18:00 | 11.04 | 11.03
2019-06-15 18:30 | 10.79 | 10.78
2019-06-15 19:00 | 10.5 | 10.49
2019-06-15 19:30 | 10.29 | 10.29
2019-06-15 20:00 | 10.21 | 10.2
2019-06-15 20:30 | 10.26 | 10.25
2019-06-15 21:00 | 9.8 | 9.79
2019-06-15 21:30 | 9.14 | 9.13
2019-06-15 22:00 | 8.75 | 8.72
2019-06-15 22:30 | 8.53 | 8.51
2019-06-15 23:00 | 8.42 | 8.39
2019-06-15 23:30 | 7.73 | 7.69
2019-06-16 | 6.86 | 6.81
2019-06-16 00:30 | 6.19 | 6.13
2019-06-16 01:00 | 5.68 | 5.6
2019-06-16 01:30 | 5.31 | 5.23
2019-06-16 02:00 | 5.02 | 4.93
2019-06-16 02:30 | 4.88 | 4.79
2019-06-16 03:00 | 4.77 | 4.67
2019-06-16 03:30 | 4.67 | 4.56
2019-06-16 04:00 | 4.59 | 4.47
2019-06-16 04:30 | 4.53 | 4.43
2019-06-16 05:00 | 4.59 | 4.49
2019-06-16 05:30 | 4.77 | 4.68
2019-06-16 06:00 | 4.9 | 4.82
2019-06-16 06:30 | 5.17 | 5.09
2019-06-16 07:00 | 5.38 | 5.25
2019-06-16 07:30 | 5.82 | 5.7
2019-06-16 08:00 | 6.27 | 6.16
2019-06-16 08:30 | 7.48 | 7.42
2019-06-16 09:00 | 8.15 | 8.1
2019-06-16 09:30 | 8.53 | 8.48
2019-06-16 10:00 | 9.03 | 8.99
2019-06-16 10:30 | 8.73 | 8.69
2019-06-16 11:00 | 9.12 | 9.09
2019-06-16 11:30 | 7.86 | 7.82
2019-06-16 12:00 | 8.88 | 8.85
2019-06-16 12:30 | 9.42 | 9.39
2019-06-16 13:00 | 8.1 | 8.06
2019-06-16 13:30 | 6.21 | 6.16
2019-06-16 14:00 | 8.31 | 8.27
2019-06-16 14:30 | 9.06 | 9.02
2019-06-16 15:00 | 9.66 | 9.63
2019-06-16 15:30 | 10.2 | 10.18
2019-06-16 16:00 | 10.43 | 10.41
2019-06-16 16:30 | 10.95 | 10.92
2019-06-16 17:00 | 11.39 | 11.37
2019-06-16 17:30 | 12.6 | 12.6
2019-06-16 18:00 | 13.29 | 13.28
2019-06-16 18:30 | 13.12 | 13.11
2019-06-16 19:00 | 12.73 | 12.73
2019-06-16 19:30 | 12.24 | 12.24
2019-06-16 20:00 | 12.04 | 12.04
2019-06-16 20:30 | 12.1 | 12.09
2019-06-16 21:00 | 11.33 | 11.32
2019-06-16 21:30 | 10.64 | 10.63
2019-06-16 22:00 | 9.8 | 9.77
2019-06-16 22:30 | 9.14 | 9.11
2019-06-16 23:00 | 8.7 | 8.67
2019-06-16 23:30 | 7.92 | 7.87
2019-06-17 | 6.83 | 6.76
2019-06-17 00:30 | 6.03 | 5.96
2019-06-17 01:00 | 5.66 | 5.57
2019-06-17 01:30 | 5.32 | 5.23
2019-06-17 02:00 | 5.04 | 4.95
2019-06-17 02:30 | 4.86 | 4.76
2019-06-17 03:00 | 4.75 | 4.65
2019-06-17 03:30 | 4.73 | 4.63
2019-06-17 04:00 | 4.8 | 4.71
2019-06-17 04:30 | 4.98 | 4.89
2019-06-17 05:00 | 5.39 | 5.31
2019-06-17 05:30 | 6.02 | 5.96
2019-06-17 06:00 | 6.54 | 6.49
2019-06-17 06:30 | 7.67 | 7.64
2019-06-17 07:00 | 8.56 | 8.52
2019-06-17 07:30 | 9.44 | 9.41
2019-06-17 08:00 | 8.4 | 8.36
2019-06-17 08:30 | 7.04 | 7
2019-06-17 09:00 | 5.94 | 5.9
2019-06-17 09:30 | 5.04 | 5
2019-06-17 10:00 | 4.47 | 4.43
2019-06-17 10:30 | 3.93 | 3.87
2019-06-17 11:00 | 3.3 | 3.24
2019-06-17 11:30 | 2.96 | 2.88
2019-06-17 12:00 | 2.73 | 2.63
2019-06-17 12:30 | 2.62 | 2.53
2019-06-17 13:00 | 2.71 | 2.61
2019-06-17 13:30 | 2.86 | 2.77
2019-06-17 14:00 | 3.16 | 3.08
2019-06-17 14:30 | 3.68 | 3.6
2019-06-17 15:00 | 4.32 | 4.25
2019-06-17 15:30 | 5.18 | 5.12
2019-06-17 16:00 | 6.48 | 6.42
2019-06-17 16:30 | 7.94 | 7.9
2019-06-17 17:00 | 9.6 | 9.57
2019-06-17 17:30 | 11.43 | 11.43
2019-06-17 18:00 | 12.74 | 12.74
2019-06-17 18:30 | 13.11 | 13.11
2019-06-17 19:00 | 13.34 | 13.34
2019-06-17 19:30 | 13.2 | 13.2
2019-06-17 20:00 | 13.36 | 13.36
2019-06-17 20:30 | 13.36 | 13.36
2019-06-17 21:00 | 12.83 | 12.83
2019-06-17 21:30 | 11.88 | 11.88
2019-06-17 22:00 | 10.93 | 10.92
2019-06-17 22:30 | 10.19 | 10.17
2019-06-17 23:00 | 9.61 | 9.58
2019-06-17 23:30 | 8.63 | 8.6
2019-06-18 | 7.74 | 7.7
2019-06-18 00:30 | 6.8 | 6.75
2019-06-18 01:00 | 6.47 | 6.41
2019-06-18 01:30 | 6.12 | 6.06
2019-06-18 02:00 | 5.75 | 5.68
2019-06-18 02:30 | 5.71 | 5.63
2019-06-18 03:00 | 5.64 | 5.55
2019-06-18 03:30 | 5.64 | 5.56
2019-06-18 04:00 | 5.72 | 5.64
2019-06-18 04:30 | 6.06 | 6
2019-06-18 05:00 | 6.57 | 6.51
2019-06-18 05:30 | 7.55 | 7.51
2019-06-18 06:00 | 8.32 | 8.3
2019-06-18 06:30 | 9.46 | 9.45
2019-06-18 07:00 | 10.63 | 10.61
2019-06-18 07:30 | 11.28 | 11.26
2019-06-18 08:00 | 11.37 | 11.35
2019-06-18 08:30 | 9.5 | 9.47
2019-06-18 09:00 | 7.94 | 7.9
2019-06-18 09:30 | 6.82 | 6.78
2019-06-18 10:00 | 5.84 | 5.78
2019-06-18 10:30 | 5.07 | 4.99
2019-06-18 11:00 | 4.57 | 4.49
2019-06-18 11:30 | 4.18 | 4.08
2019-06-18 12:00 | 3.9 | 3.8
2019-06-18 12:30 | 3.87 | 3.78
2019-06-18 13:00 | 3.93 | 3.83
2019-06-18 13:30 | 3.97 | 3.87
2019-06-18 14:00 | 4.5 | 4.42
2019-06-18 14:30 | 5.03 | 4.96
2019-06-18 15:00 | 5.55 | 5.48
2019-06-18 15:30 | 6.34 | 6.27
2019-06-18 16:00 | 6.7 | 6.65
2019-06-18 16:30 | 7.91 | 7.88
2019-06-18 17:00 | 9.57 | 9.55
2019-06-18 17:30 | 11.5 | 11.49
2019-06-18 18:00 | 13.17 | 13.17
2019-06-18 18:30 | 13.46 | 13.46
2019-06-18 19:00 | 13.82 | 13.82
2019-06-18 19:30 | 13.69 | 13.69
2019-06-18 20:00 | 13.72 | 13.72
2019-06-18 20:30 | 13.57 | 13.56
2019-06-18 21:00 | 13.19 | 13.18
2019-06-18 21:30 | 12.15 | 12.15
2019-06-18 22:00 | 11.08 | 11.07
2019-06-18 22:30 | 10.17 | 10.16
2019-06-18 23:00 | 9.62 | 9.6
2019-06-18 23:30 | 8.7 | 8.67
2019-06-19 | 7.67 | 7.63
2019-06-19 00:30 | 6.86 | 6.81
2019-06-19 01:00 | 6.45 | 6.39
2019-06-19 01:30 | 5.99 | 5.92
2019-06-19 02:00 | 5.86 | 5.79
2019-06-19 02:30 | 5.71 | 5.64
2019-06-19 03:00 | 5.61 | 5.53
2019-06-19 03:30 | 5.58 | 5.5
2019-06-19 04:00 | 5.63 | 5.55
2019-06-19 04:30 | 6.02 | 5.96
2019-06-19 05:00 | 6.65 | 6.6
2019-06-19 05:30 | 7.58 | 7.55
2019-06-19 06:00 | 8.38 | 8.36
2019-06-19 06:30 | 9.33 | 9.32
2019-06-19 07:00 | 10.52 | 10.5
2019-06-19 07:30 | 10.87 | 10.85
2019-06-19 08:00 | 10.01 | 10
2019-06-19 08:30 | 8.17 | 8.15
2019-06-19 09:00 | 6.64 | 6.61
2019-06-19 09:30 | 5.53 | 5.49
2019-06-19 10:00 | 4.67 | 4.63
2019-06-19 10:30 | 3.86 | 3.8
2019-06-19 11:00 | 3.3 | 3.22
2019-06-19 11:30 | 2.9 | 2.82
2019-06-19 12:00 | 2.69 | 2.61
2019-06-19 12:30 | 2.64 | 2.55
2019-06-19 13:00 | 2.69 | 2.61
2019-06-19 13:30 | 2.9 | 2.83
2019-06-19 14:00 | 3.33 | 3.26
2019-06-19 14:30 | 3.75 | 3.69
2019-06-19 15:00 | 4.4 | 4.34
2019-06-19 15:30 | 5.17 | 5.12
2019-06-19 16:00 | 6.41 | 6.37
2019-06-19 16:30 | 7.73 | 7.69
2019-06-19 17:00 | 9.42 | 9.4
2019-06-19 17:30 | 11.08 | 11.08
2019-06-19 18:00 | 12.42 | 12.42
2019-06-19 18:30 | 12.73 | 12.73
2019-06-19 19:00 | 12.99 | 12.98
2019-06-19 19:30 | 12.64 | 12.64
2019-06-19 20:00 | 12.81 | 12.81
2019-06-19 20:30 | 12.93 | 12.92
2019-06-19 21:00 | 12.31 | 12.3
2019-06-19 21:30 | 11.5 | 11.5
2019-06-19 22:00 | 10.55 | 10.54
2019-06-19 22:30 | 9.62 | 9.6
2019-06-19 23:00 | 9.34 | 9.32
2019-06-19 23:30 | 8.39 | 8.36
2019-06-20 | 7.45 | 7.41
2019-06-20 00:30 | 6.56 | 6.51
2019-06-20 01:00 | 6.2 | 6.13
2019-06-20 01:30 | 5.83 | 5.76
2019-06-20 02:00 | 5.53 | 5.45
2019-06-20 02:30 | 5.28 | 5.19
2019-06-20 03:00 | 5.29 | 5.2
2019-06-20 03:30 | 5.33 | 5.25
2019-06-20 04:00 | 5.54 | 5.46
2019-06-20 04:30 | 5.75 | 5.68
2019-06-20 05:00 | 6.2 | 6.14
2019-06-20 05:30 | 6.94 | 6.89
2019-06-20 06:00 | 7.64 | 7.6
2019-06-20 06:30 | 8.54 | 8.52
2019-06-20 07:00 | 9.47 | 9.45
2019-06-20 07:30 | 9.85 | 9.82
2019-06-20 08:00 | 9.27 | 9.25
2019-06-20 08:30 | 7.74 | 7.71
2019-06-20 09:00 | 7.03 | 7
2019-06-20 09:30 | 5.58 | 5.55
2019-06-20 10:00 | 5.44 | 5.41
2019-06-20 10:30 | 5.21 | 5.18
2019-06-20 11:00 | 4.41 | 4.37
2019-06-20 11:30 | 5.18 | 5.14
2019-06-20 12:00 | 5.4 | 5.37
2019-06-20 12:30 | 4.68 | 4.64
2019-06-20 13:00 | 5.29 | 5.25
2019-06-20 13:30 | 7.03 | 6.99
2019-06-20 14:00 | 7.07 | 7.03
2019-06-20 14:30 | 7.14 | 7.1
2019-06-20 15:00 | 7.29 | 7.25
2019-06-20 15:30 | 7.99 | 7.96
2019-06-20 16:00 | 8.81 | 8.79
2019-06-20 16:30 | 9.5 | 9.47
2019-06-20 17:00 | 10.59 | 10.57
2019-06-20 17:30 | 12.02 | 12.02
2019-06-20 18:00 | 13.17 | 13.17
2019-06-20 18:30 | 13.43 | 13.43
2019-06-20 19:00 | 13.66 | 13.66
2019-06-20 19:30 | 13.29 | 13.29
2019-06-20 20:00 | 13.41 | 13.41
2019-06-20 20:30 | 13.41 | 13.41
2019-06-20 21:00 | 12.85 | 12.85
2019-06-20 21:30 | 12.06 | 12.05
2019-06-20 22:00 | 10.86 | 10.86
2019-06-20 22:30 | 10.17 | 10.16
2019-06-20 23:00 | 9.32 | 9.3
2019-06-20 23:30 | 8.19 | 8.16
2019-06-21 | 7.2 | 7.16
2019-06-21 00:30 | 6.32 | 6.26
2019-06-21 01:00 | 6 | 5.93
2019-06-21 01:30 | 5.57 | 5.5
2019-06-21 02:00 | 5.1 | 5.02
2019-06-21 02:30 | 4.93 | 4.84
2019-06-21 03:00 | 4.94 | 4.85
2019-06-21 03:30 | 4.95 | 4.86
2019-06-21 04:00 | 5.07 | 4.99
2019-06-21 04:30 | 5.25 | 5.17
2019-06-21 05:00 | 5.54 | 5.47
2019-06-21 05:30 | 6.15 | 6.1
2019-06-21 06:00 | 6.83 | 6.79
2019-06-21 06:30 | 7.81 | 7.78
2019-06-21 07:00 | 8.98 | 8.95
2019-06-21 07:30 | 9.38 | 9.35
2019-06-21 08:00 | 9.02 | 8.99
2019-06-21 08:30 | 8.13 | 8.09
2019-06-21 09:00 | 8.11 | 8.07
2019-06-21 09:30 | 5.87 | 5.82
2019-06-21 10:00 | 4.99 | 4.92
2019-06-21 10:30 | 4.52 | 4.46
2019-06-21 11:00 | 3.33 | 3.25
2019-06-21 11:30 | 2.88 | 2.81
2019-06-21 12:00 | 2.75 | 2.68
2019-06-21 12:30 | 2.63 | 2.55
2019-06-21 13:00 | 2.76 | 2.68
2019-06-21 13:30 | 2.95 | 2.88
2019-06-21 14:00 | 3.2 | 3.13
2019-06-21 14:30 | 3.74 | 3.68
2019-06-21 15:00 | 4.33 | 4.26
2019-06-21 15:30 | 5.13 | 5.08
2019-06-21 16:00 | 6.42 | 6.37
2019-06-21 16:30 | 7.75 | 7.71
2019-06-21 17:00 | 9.08 | 9.05
2019-06-21 17:30 | 10.44 | 10.43
2019-06-21 18:00 | 11.69 | 11.68
2019-06-21 18:30 | 12.19 | 12.19
2019-06-21 19:00 | 12.67 | 12.66
2019-06-21 19:30 | 12.61 | 12.6
2019-06-21 20:00 | 12.72 | 12.71
2019-06-21 20:30 | 13.04 | 13.03
2019-06-21 21:00 | 12.67 | 12.66
2019-06-21 21:30 | 12.11 | 12.11
2019-06-21 22:00 | 11.44 | 11.43
2019-06-21 22:30 | 11.01 | 11
2019-06-21 23:00 | 10.7 | 10.69
2019-06-21 23:30 | 9.64 | 9.62
2019-06-22 | 8.51 | 8.48
2019-06-22 00:30 | 7.61 | 7.57
2019-06-22 01:00 | 7.17 | 7.12
2019-06-22 01:30 | 6.7 | 6.65
2019-06-22 02:00 | 6.34 | 6.27
2019-06-22 02:30 | 6.14 | 6.08
2019-06-22 03:00 | 5.98 | 5.91
2019-06-22 03:30 | 5.96 | 5.89
2019-06-22 04:00 | 5.87 | 5.8
2019-06-22 04:30 | 6.05 | 5.98
2019-06-22 05:00 | 6.38 | 6.32
2019-06-22 05:30 | 6.66 | 6.61
2019-06-22 06:00 | 7.07 | 7.03
2019-06-22 06:30 | 7.78 | 7.74
2019-06-22 07:00 | 8.6 | 8.55
2019-06-22 07:30 | 9.4 | 9.36
2019-06-22 08:00 | 9.56 | 9.53
2019-06-22 08:30 | 9.41 | 9.39
2019-06-22 09:00 | 8.78 | 8.76
2019-06-22 09:30 | 8.01 | 7.99
2019-06-22 10:00 | 6.87 | 6.84
2019-06-22 10:30 | 6.01 | 5.98
2019-06-22 11:00 | 5.24 | 5.21
2019-06-22 11:30 | 4.63 | 4.58
2019-06-22 12:00 | 4.35 | 4.3
2019-06-22 12:30 | 4.17 | 4.12
2019-06-22 13:00 | 4 | 3.94
2019-06-22 13:30 | 4.12 | 4.05
2019-06-22 14:00 | 4.47 | 4.41
2019-06-22 14:30 | 4.95 | 4.89
2019-06-22 15:00 | 5.4 | 5.34
2019-06-22 15:30 | 6.13 | 6.07
2019-06-22 16:00 | 6.99 | 6.93
2019-06-22 16:30 | 8.34 | 8.3
2019-06-22 17:00 | 9.93 | 9.91
2019-06-22 17:30 | 11.46 | 11.45
2019-06-22 18:00 | 12.87 | 12.87
2019-06-22 18:30 | 13 | 13
2019-06-22 19:00 | 13.14 | 13.14
2019-06-22 19:30 | 12.95 | 12.94
2019-06-22 20:00 | 13.07 | 13.06
2019-06-22 20:30 | 13.05 | 13.05
2019-06-22 21:00 | 12.73 | 12.72
2019-06-22 21:30 | 12.39 | 12.39
2019-06-22 22:00 | 11.88 | 11.88
2019-06-22 22:30 | 11.45 | 11.45
2019-06-22 23:00 | 11.08 | 11.07
2019-06-22 23:30 | 10.18 | 10.16
2019-06-23 | 9.12 | 9.1
2019-06-23 00:30 | 8.23 | 8.2
2019-06-23 01:00 | 7.69 | 7.65
2019-06-23 01:30 | 7.25 | 7.2
2019-06-23 02:00 | 6.71 | 6.66
2019-06-23 02:30 | 6.52 | 6.46
2019-06-23 03:00 | 6.41 | 6.35
2019-06-23 03:30 | 6.4 | 6.35
2019-06-23 04:00 | 6.25 | 6.18
2019-06-23 04:30 | 6.31 | 6.24
2019-06-23 05:00 | 6.49 | 6.43
2019-06-23 05:30 | 6.85 | 6.8
2019-06-23 06:00 | 7.24 | 7.2
2019-06-23 06:30 | 7.63 | 7.59
2019-06-23 07:00 | 8.39 | 8.33
2019-06-23 07:30 | 9.21 | 9.16
2019-06-23 08:00 | 9.86 | 9.83
2019-06-23 08:30 | 10.4 | 10.38
2019-06-23 09:00 | 9.88 | 9.87
2019-06-23 09:30 | 9.04 | 9.02
2019-06-23 10:00 | 8 | 7.98
2019-06-23 10:30 | 7.97 | 7.95
2019-06-23 11:00 | 6.54 | 6.51
2019-06-23 11:30 | 6 | 5.97
2019-06-23 12:00 | 5.32 | 5.28
2019-06-23 12:30 | 4.92 | 4.86
2019-06-23 13:00 | 4.84 | 4.79
2019-06-23 13:30 | 4.74 | 4.68
2019-06-23 14:00 | 4.79 | 4.72
2019-06-23 14:30 | 6.05 | 6
2019-06-23 15:00 | 7.38 | 7.33
2019-06-23 15:30 | 7.52 | 7.47
2019-06-23 16:00 | 7.88 | 7.83
2019-06-23 16:30 | 9.23 | 9.2
2019-06-23 17:00 | 11.36 | 11.34
2019-06-23 17:30 | 13.13 | 13.12
2019-06-23 18:00 | 14 | 14
2019-06-23 18:30 | 13.95 | 13.95
2019-06-23 19:00 | 13.99 | 13.98
2019-06-23 19:30 | 13.57 | 13.56
2019-06-23 20:00 | 13.52 | 13.52
2019-06-23 20:30 | 13.42 | 13.41
2019-06-23 21:00 | 12.96 | 12.95
2019-06-23 21:30 | 12.3 | 12.3
2019-06-23 22:00 | 11.27 | 11.26
2019-06-23 22:30 | 10.74 | 10.73
2019-06-23 23:00 | 10.06 | 10.04
2019-06-23 23:30 | 8.96 | 8.93
2019-06-24 | 7.94 | 7.9
2019-06-24 00:30 | 7.09 | 7.04
2019-06-24 01:00 | 6.57 | 6.51
2019-06-24 01:30 | 6.15 | 6.08
2019-06-24 02:00 | 5.91 | 5.84
2019-06-24 02:30 | 5.75 | 5.68
2019-06-24 03:00 | 5.75 | 5.67
2019-06-24 03:30 | 5.74 | 5.67
2019-06-24 04:00 | 5.88 | 5.81
2019-06-24 04:30 | 6.21 | 6.14
2019-06-24 05:00 | 6.76 | 6.71
2019-06-24 05:30 | 7.63 | 7.6
2019-06-24 06:00 | 8.85 | 8.84
2019-06-24 06:30 | 10.08 | 10.08
2019-06-24 07:00 | 11.2 | 11.2
2019-06-24 07:30 | 11.78 | 11.77
2019-06-24 08:00 | 11.24 | 11.23
2019-06-24 08:30 | 9.52 | 9.51
2019-06-24 09:00 | 7.95 | 7.94
2019-06-24 09:30 | 6.85 | 6.83
2019-06-24 10:00 | 5.98 | 5.96
2019-06-24 10:30 | 5.07 | 5.04
2019-06-24 11:00 | 4.37 | 4.33
2019-06-24 11:30 | 4.11 | 4.07
2019-06-24 12:00 | 4.32 | 4.28
2019-06-24 12:30 | 5.08 | 5.04
2019-06-24 13:00 | 4.3 | 4.26
2019-06-24 13:30 | 4.29 | 4.24
2019-06-24 14:00 | 4.47 | 4.42
2019-06-24 14:30 | 4.73 | 4.68
2019-06-24 15:00 | 5.81 | 5.76
2019-06-24 15:30 | 6.75 | 6.72
2019-06-24 16:00 | 7.85 | 7.82
2019-06-24 16:30 | 10 | 9.98
2019-06-24 17:00 | 12.37 | 12.36
2019-06-24 17:30 | 14.51 | 14.51
2019-06-24 18:00 | 15.97 | 15.97
2019-06-24 18:30 | 16.32 | 16.32
2019-06-24 19:00 | 16.47 | 16.46
2019-06-24 19:30 | 16.35 | 16.35
2019-06-24 20:00 | 16.05 | 16.05
2019-06-24 20:30 | 15.69 | 15.68
2019-06-24 21:00 | 15.24 | 15.23
2019-06-24 21:30 | 13.92 | 13.92
2019-06-24 22:00 | 12.33 | 12.32
2019-06-24 22:30 | 11.19 | 11.18
2019-06-24 23:00 | 10.5 | 10.48
2019-06-24 23:30 | 9.26 | 9.24
2019-06-25 | 8.11 | 8.07
2019-06-25 00:30 | 7.33 | 7.29
2019-06-25 01:00 | 6.81 | 6.76
2019-06-25 01:30 | 6.27 | 6.21
2019-06-25 02:00 | 6 | 5.93
2019-06-25 02:30 | 5.73 | 5.65
2019-06-25 03:00 | 5.64 | 5.57
2019-06-25 03:30 | 5.64 | 5.56
2019-06-25 04:00 | 5.77 | 5.69
2019-06-25 04:30 | 6.03 | 5.97
2019-06-25 05:00 | 6.69 | 6.64
2019-06-25 05:30 | 7.37 | 7.33
2019-06-25 06:00 | 7.95 | 7.92
2019-06-25 06:30 | 9.03 | 9.02
2019-06-25 07:00 | 10.15 | 10.14
2019-06-25 07:30 | 11.2 | 11.19
2019-06-25 08:00 | 10.81 | 10.8
2019-06-25 08:30 | 9.29 | 9.27
2019-06-25 09:00 | 7.88 | 7.85
2019-06-25 09:30 | 7.5 | 7.47
2019-06-25 10:00 | 6.19 | 6.16
2019-06-25 10:30 | 5.29 | 5.26
2019-06-25 11:00 | 5.98 | 5.94
2019-06-25 11:30 | 4.66 | 4.62
2019-06-25 12:00 | 6.39 | 6.35
2019-06-25 12:30 | 7.36 | 7.33
2019-06-25 13:00 | 6.27 | 6.22
2019-06-25 13:30 | 6.38 | 6.34
2019-06-25 14:00 | 7.68 | 7.64
2019-06-25 14:30 | 7.21 | 7.18
2019-06-25 15:00 | 7.71 | 7.68
2019-06-25 15:30 | 8.02 | 7.99
2019-06-25 16:00 | 8.97 | 8.94
2019-06-25 16:30 | 10.38 | 10.36
2019-06-25 17:00 | 11.89 | 11.88
2019-06-25 17:30 | 13.74 | 13.74
2019-06-25 18:00 | 14.98 | 14.97
2019-06-25 18:30 | 15.41 | 15.41
2019-06-25 19:00 | 15.84 | 15.84
2019-06-25 19:30 | 15.34 | 15.34
2019-06-25 20:00 | 15.11 | 15.11
2019-06-25 20:30 | 15.06 | 15.06
2019-06-25 21:00 | 14.23 | 14.22
2019-06-25 21:30 | 13.17 | 13.17
2019-06-25 22:00 | 11.81 | 11.8
2019-06-25 22:30 | 10.65 | 10.64
2019-06-25 23:00 | 9.9 | 9.88
2019-06-25 23:30 | 8.78 | 8.75
2019-06-26 | 7.59 | 7.55
2019-06-26 00:30 | 6.77 | 6.71
2019-06-26 01:00 | 6.25 | 6.18
2019-06-26 01:30 | 5.88 | 5.81
2019-06-26 02:00 | 5.54 | 5.45
2019-06-26 02:30 | 5.33 | 5.25
2019-06-26 03:00 | 5.31 | 5.22
2019-06-26 03:30 | 5.25 | 5.16
2019-06-26 04:00 | 5.29 | 5.2
2019-06-26 04:30 | 5.48 | 5.4
2019-06-26 05:00 | 6.06 | 5.99
2019-06-26 05:30 | 6.67 | 6.62
2019-06-26 06:00 | 7.55 | 7.52
2019-06-26 06:30 | 8.64 | 8.62
2019-06-26 07:00 | 9.52 | 9.49
2019-06-26 07:30 | 10.03 | 10.01
2019-06-26 08:00 | 10.07 | 10.05
2019-06-26 08:30 | 9.4 | 9.38
2019-06-26 09:00 | 9.07 | 9.05
2019-06-26 09:30 | 8.2 | 8.18
2019-06-26 10:00 | 7.03 | 7
2019-06-26 10:30 | 5.47 | 5.44
2019-06-26 11:00 | 6.83 | 6.81
2019-06-26 11:30 | 7.38 | 7.36
2019-06-26 12:00 | 7.65 | 7.63
2019-06-26 12:30 | 8.66 | 8.64
2019-06-26 13:00 | 8.4 | 8.37
2019-06-26 13:30 | 8.15 | 8.12
2019-06-26 14:00 | 8.37 | 8.34
2019-06-26 14:30 | 7.68 | 7.64
2019-06-26 15:00 | 8.18 | 8.15
2019-06-26 15:30 | 9.03 | 9
2019-06-26 16:00 | 9.99 | 9.97
2019-06-26 16:30 | 11.07 | 11.06
2019-06-26 17:00 | 12.43 | 12.43
2019-06-26 17:30 | 13.95 | 13.95
2019-06-26 18:00 | 14.9 | 14.9
2019-06-26 18:30 | 15.1 | 15.1
2019-06-26 19:00 | 15.21 | 15.21
2019-06-26 19:30 | 14.81 | 14.8
2019-06-26 20:00 | 14.59 | 14.59
2019-06-26 20:30 | 14.47 | 14.47
2019-06-26 21:00 | 13.64 | 13.64
2019-06-26 21:30 | 12.56 | 12.56
2019-06-26 22:00 | 11.22 | 11.21
2019-06-26 22:30 | 10.28 | 10.27
2019-06-26 23:00 | 9.8 | 9.77
2019-06-26 23:30 | 8.6 | 8.57
2019-06-27 | 7.5 | 7.46
2019-06-27 00:30 | 6.71 | 6.66
2019-06-27 01:00 | 6.14 | 6.08
2019-06-27 01:30 | 5.68 | 5.61
2019-06-27 02:00 | 5.41 | 5.33
2019-06-27 02:30 | 5.32 | 5.24
2019-06-27 03:00 | 5.17 | 5.08
2019-06-27 03:30 | 5.13 | 5.04
2019-06-27 04:00 | 5.26 | 5.17
2019-06-27 04:30 | 5.49 | 5.41
2019-06-27 05:00 | 5.97 | 5.91
2019-06-27 05:30 | 6.64 | 6.59
2019-06-27 06:00 | 7.38 | 7.34
2019-06-27 06:30 | 8.61 | 8.58
2019-06-27 07:00 | 9.42 | 9.39
2019-06-27 07:30 | 9.77 | 9.74
2019-06-27 08:00 | 9.06 | 9.03
2019-06-27 08:30 | 7.8 | 7.76
2019-06-27 09:00 | 6.51 | 6.46
2019-06-27 09:30 | 5.5 | 5.45
2019-06-27 10:00 | 5.15 | 5.11
2019-06-27 10:30 | 5.13 | 5.08
2019-06-27 11:00 | 5.03 | 4.97
2019-06-27 11:30 | 4.33 | 4.27
2019-06-27 12:00 | 4.78 | 4.73
2019-06-27 12:30 | 3.65 | 3.59
2019-06-27 13:00 | 5.06 | 5
2019-06-27 13:30 | 5.48 | 5.42
2019-06-27 14:00 | 4.07 | 4.01
2019-06-27 14:30 | 4.47 | 4.4
2019-06-27 15:00 | 5.6 | 5.55
2019-06-27 15:30 | 6.33 | 6.29
2019-06-27 16:00 | 6.7 | 6.66
2019-06-27 16:30 | 8.86 | 8.83
2019-06-27 17:00 | 10.11 | 10.08
2019-06-27 17:30 | 11.46 | 11.46
2019-06-27 18:00 | 12.44 | 12.44
2019-06-27 18:30 | 12.96 | 12.96
2019-06-27 19:00 | 13.36 | 13.36
2019-06-27 19:30 | 12.93 | 12.93
2019-06-27 20:00 | 12.98 | 12.98
2019-06-27 20:30 | 12.94 | 12.94
2019-06-27 21:00 | 12.36 | 12.36
2019-06-27 21:30 | 11.35 | 11.35
2019-06-27 22:00 | 10.58 | 10.57
2019-06-27 22:30 | 9.95 | 9.93
2019-06-27 23:00 | 9.49 | 9.47
2019-06-27 23:30 | 8.46 | 8.42
2019-06-28 | 7.43 | 7.39
2019-06-28 00:30 | 6.53 | 6.47
2019-06-28 01:00 | 6.07 | 6
2019-06-28 01:30 | 5.62 | 5.55
2019-06-28 02:00 | 5.35 | 5.27
2019-06-28 02:30 | 5.23 | 5.14
2019-06-28 03:00 | 5.13 | 5.03
2019-06-28 03:30 | 4.99 | 4.9
2019-06-28 04:00 | 5.07 | 4.98
2019-06-28 04:30 | 5.46 | 5.38
2019-06-28 05:00 | 5.63 | 5.55
2019-06-28 05:30 | 6.26 | 6.21
2019-06-28 06:00 | 6.84 | 6.8
2019-06-28 06:30 | 7.63 | 7.6
2019-06-28 07:00 | 8.31 | 8.27
2019-06-28 07:30 | 8.97 | 8.93
2019-06-28 08:00 | 8.8 | 8.76
2019-06-28 08:30 | 6.91 | 6.86
2019-06-28 09:00 | 5.92 | 5.87
2019-06-28 09:30 | 6.93 | 6.89
2019-06-28 10:00 | 6.41 | 6.37
2019-06-28 10:30 | 3.86 | 3.8
2019-06-28 11:00 | 3.36 | 3.3
2019-06-28 11:30 | 4.03 | 3.97
2019-06-28 12:00 | 3.98 | 3.93
2019-06-28 12:30 | 3.13 | 3.07
2019-06-28 13:00 | 2.95 | 2.88
2019-06-28 13:30 | 3.51 | 3.45
2019-06-28 14:00 | 4.08 | 4.03
2019-06-28 14:30 | 5.19 | 5.13
2019-06-28 15:00 | 4.5 | 4.45
2019-06-28 15:30 | 7.21 | 7.17
2019-06-28 16:00 | 7.75 | 7.71
2019-06-28 16:30 | 7.86 | 7.83
2019-06-28 17:00 | 9.13 | 9.11
2019-06-28 17:30 | 10.72 | 10.71
2019-06-28 18:00 | 11.95 | 11.94
2019-06-28 18:30 | 12.23 | 12.23
2019-06-28 19:00 | 12.48 | 12.48
2019-06-28 19:30 | 12.25 | 12.25
2019-06-28 20:00 | 12.01 | 12.01
2019-06-28 20:30 | 11.9 | 11.89
2019-06-28 21:00 | 11.61 | 11.61
2019-06-28 21:30 | 10.96 | 10.96
2019-06-28 22:00 | 10.29 | 10.27
2019-06-28 22:30 | 9.91 | 9.89
2019-06-28 23:00 | 9.49 | 9.47
2019-06-28 23:30 | 8.69 | 8.66
2019-06-29 | 7.63 | 7.58
2019-06-29 00:30 | 6.84 | 6.78
2019-06-29 01:00 | 6.32 | 6.26
2019-06-29 01:30 | 5.87 | 5.8
2019-06-29 02:00 | 5.5 | 5.42
2019-06-29 02:30 | 5.49 | 5.4
2019-06-29 03:00 | 5.26 | 5.17
2019-06-29 03:30 | 5.22 | 5.14
2019-06-29 04:00 | 5.2 | 5.1
2019-06-29 04:30 | 5.33 | 5.24
2019-06-29 05:00 | 5.23 | 5.14
2019-06-29 05:30 | 5.57 | 5.49
2019-06-29 06:00 | 5.72 | 5.64
2019-06-29 06:30 | 6.13 | 6.06
2019-06-29 07:00 | 6.62 | 6.53
2019-06-29 07:30 | 6.92 | 6.83
2019-06-29 08:00 | 7.66 | 7.59
2019-06-29 08:30 | 7.84 | 7.79
2019-06-29 09:00 | 6.81 | 6.77
2019-06-29 09:30 | 6.43 | 6.39
2019-06-29 10:00 | 6.5 | 6.46
2019-06-29 10:30 | 6.18 | 6.13
2019-06-29 11:00 | 5.47 | 5.43
2019-06-29 11:30 | 5.3 | 5.26
2019-06-29 12:00 | 5.18 | 5.14
2019-06-29 12:30 | 5.47 | 5.43
2019-06-29 13:00 | 5.13 | 5.09
2019-06-29 13:30 | 4.01 | 3.97
2019-06-29 14:00 | 4.52 | 4.48
2019-06-29 14:30 | 5.63 | 5.59
2019-06-29 15:00 | 7.08 | 7.04
2019-06-29 15:30 | 6.34 | 6.3
2019-06-29 16:00 | 7.14 | 7.1
2019-06-29 16:30 | 8.7 | 8.67
2019-06-29 17:00 | 9.53 | 9.5
2019-06-29 17:30 | 10.6 | 10.59
2019-06-29 18:00 | 11.29 | 11.29
2019-06-29 18:30 | 11.31 | 11.3
2019-06-29 19:00 | 11.34 | 11.33
2019-06-29 19:30 | 11.05 | 11.04
2019-06-29 20:00 | 11.08 | 11.07
2019-06-29 20:30 | 11.23 | 11.22
2019-06-29 21:00 | 10.93 | 10.92
2019-06-29 21:30 | 10.52 | 10.51
2019-06-29 22:00 | 9.9 | 9.88
2019-06-29 22:30 | 9.69 | 9.66
2019-06-29 23:00 | 9.46 | 9.43
2019-06-29 23:30 | 8.57 | 8.54
2019-06-30 | 7.66 | 7.62
2019-06-30 00:30 | 7.02 | 6.96
2019-06-30 01:00 | 6.58 | 6.52
2019-06-30 01:30 | 6.02 | 5.94
2019-06-30 02:00 | 5.69 | 5.61
2019-06-30 02:30 | 5.46 | 5.38
2019-06-30 03:00 | 5.17 | 5.08
2019-06-30 03:30 | 5.14 | 5.05
2019-06-30 04:00 | 5.05 | 4.95
2019-06-30 04:30 | 5.16 | 5.06
2019-06-30 05:00 | 5.11 | 5.01
2019-06-30 05:30 | 5.41 | 5.32
2019-06-30 06:00 | 5.66 | 5.58
2019-06-30 06:30 | 6.02 | 5.94
2019-06-30 07:00 | 6.26 | 6.15
2019-06-30 07:30 | 6.75 | 6.65
2019-06-30 08:00 | 7.21 | 7.13
2019-06-30 08:30 | 7.52 | 7.45
2019-06-30 09:00 | 7.59 | 7.54
2019-06-30 09:30 | 7.08 | 7.04
2019-06-30 10:00 | 6.04 | 5.99
2019-06-30 10:30 | 5.38 | 5.33
2019-06-30 11:00 | 4.99 | 4.94
2019-06-30 11:30 | 4.59 | 4.55
2019-06-30 12:00 | 4.37 | 4.32
2019-06-30 12:30 | 4.29 | 4.25
2019-06-30 13:00 | 4.11 | 4.06
2019-06-30 13:30 | 4.21 | 4.16
2019-06-30 14:00 | 4.69 | 4.65
2019-06-30 14:30 | 5.13 | 5.08
2019-06-30 15:00 | 5.72 | 5.68
2019-06-30 15:30 | 6.52 | 6.47
2019-06-30 16:00 | 7.32 | 7.28
2019-06-30 16:30 | 8.49 | 8.45
2019-06-30 17:00 | 9.77 | 9.75
2019-06-30 17:30 | 11.23 | 11.22
2019-06-30 18:00 | 12.34 | 12.33
2019-06-30 18:30 | 12.32 | 12.32
2019-06-30 19:00 | 12.22 | 12.22
2019-06-30 19:30 | 11.8 | 11.79
2019-06-30 20:00 | 11.62 | 11.62
2019-06-30 20:30 | 11.57 | 11.56
2019-06-30 21:00 | 10.91 | 10.89
2019-06-30 21:30 | 10.3 | 10.28
2019-06-30 22:00 | 9.77 | 9.74
2019-06-30 22:30 | 9.17 | 9.13
2019-06-30 23:00 | 8.76 | 8.73
2019-06-30 23:30 | 7.86 | 7.81
2019-07-01 | 7.02 | 6.96
2019-07-01 00:30 | 6.32 | 6.25
2019-07-01 01:00 | 5.8 | 5.73
2019-07-01 01:30 | 5.37 | 5.28
2019-07-01 02:00 | 4.94 | 4.85
2019-07-01 02:30 | 4.92 | 4.82
2019-07-01 03:00 | 4.8 | 4.7
2019-07-01 03:30 | 4.81 | 4.71
2019-07-01 04:00 | 4.79 | 4.69
2019-07-01 04:30 | 5.11 | 5.01
2019-07-01 05:00 | 5.42 | 5.34
2019-07-01 05:30 | 5.87 | 5.8
2019-07-01 06:00 | 6.68 | 6.63
2019-07-01 06:30 | 7.44 | 7.41
2019-07-01 07:00 | 7.9 | 7.85
2019-07-01 07:30 | 7.98 | 7.93
2019-07-01 08:00 | 7.45 | 7.4
2019-07-01 08:30 | 6.84 | 6.79
2019-07-01 09:00 | 6 | 5.95
2019-07-01 09:30 | 5.31 | 5.25
2019-07-01 10:00 | 4.9 | 4.85
2019-07-01 10:30 | 4.12 | 4.05
2019-07-01 11:00 | 3.73 | 3.67
2019-07-01 11:30 | 3.8 | 3.73
2019-07-01 12:00 | 4.49 | 4.43
2019-07-01 12:30 | 4.91 | 4.86
2019-07-01 13:00 | 6.66 | 6.63
2019-07-01 13:30 | 6.81 | 6.77
2019-07-01 14:00 | 7.29 | 7.25
2019-07-01 14:30 | 6.8 | 6.76
2019-07-01 15:00 | 5.68 | 5.63
2019-07-01 15:30 | 5.92 | 5.87
2019-07-01 16:00 | 7.99 | 7.96
2019-07-01 16:30 | 8.92 | 8.89
2019-07-01 17:00 | 10.95 | 10.94
2019-07-01 17:30 | 12.92 | 12.92
2019-07-01 18:00 | 13.96 | 13.96
2019-07-01 18:30 | 13.89 | 13.89
2019-07-01 19:00 | 13.49 | 13.49
2019-07-01 19:30 | 12.82 | 12.82
2019-07-01 20:00 | 12.2 | 12.2
2019-07-01 20:30 | 11.65 | 11.64
2019-07-01 21:00 | 11.29 | 11.29
2019-07-01 21:30 | 10.9 | 10.89
2019-07-01 22:00 | 9.82 | 9.8
2019-07-01 22:30 | 8.84 | 8.82
2019-07-01 23:00 | 7.84 | 7.8
2019-07-01 23:30 | 7.43 | 7.39
2019-07-02 | 7.1 | 7.05
2019-07-02 00:30 | 6.31 | 6.24
2019-07-02 01:00 | 5.75 | 5.68
2019-07-02 01:30 | 5.34 | 5.25
2019-07-02 02:00 | 5 | 4.9
2019-07-02 02:30 | 4.92 | 4.82
2019-07-02 03:00 | 4.78 | 4.68
2019-07-02 03:30 | 4.84 | 4.74
2019-07-02 04:00 | 4.89 | 4.79
2019-07-02 04:30 | 5.08 | 4.99
2019-07-02 05:00 | 5.41 | 5.33
2019-07-02 05:30 | 5.91 | 5.84
2019-07-02 06:00 | 6.58 | 6.52
2019-07-02 06:30 | 7.27 | 7.23
2019-07-02 07:00 | 7.94 | 7.9
2019-07-02 07:30 | 7.94 | 7.88
2019-07-02 08:00 | 7.64 | 7.59
2019-07-02 08:30 | 6.11 | 6.04
2019-07-02 09:00 | 5.63 | 5.57
2019-07-02 09:30 | 5.25 | 5.2
2019-07-02 10:00 | 4.5 | 4.44
2019-07-02 10:30 | 4.39 | 4.34
2019-07-02 11:00 | 3.89 | 3.84
2019-07-02 11:30 | 3.71 | 3.66
2019-07-02 12:00 | 3.5 | 3.44
2019-07-02 12:30 | 3.65 | 3.6
2019-07-02 13:00 | 3.97 | 3.93
2019-07-02 13:30 | 4.72 | 4.69
2019-07-02 14:00 | 4.5 | 4.46
2019-07-02 14:30 | 5.34 | 5.31
2019-07-02 15:00 | 6.01 | 5.98
2019-07-02 15:30 | 6.71 | 6.68
2019-07-02 16:00 | 7.41 | 7.38
2019-07-02 16:30 | 8.59 | 8.57
2019-07-02 17:00 | 9.73 | 9.71
2019-07-02 17:30 | 11.15 | 11.15
2019-07-02 18:00 | 12.56 | 12.56
2019-07-02 18:30 | 13.01 | 13.01
2019-07-02 19:00 | 12.94 | 12.94
2019-07-02 19:30 | 12.72 | 12.72
2019-07-02 20:00 | 12.46 | 12.46
2019-07-02 20:30 | 12.52 | 12.52
2019-07-02 21:00 | 12.18 | 12.18
2019-07-02 21:30 | 11.09 | 11.08
2019-07-02 22:00 | 10.08 | 10.07
2019-07-02 22:30 | 9.35 | 9.32
2019-07-02 23:00 | 8.99 | 8.96
2019-07-02 23:30 | 8 | 7.96
2019-07-03 | 7.14 | 7.08
2019-07-03 00:30 | 6.35 | 6.28
2019-07-03 01:00 | 5.95 | 5.87
2019-07-03 01:30 | 5.63 | 5.53
2019-07-03 02:00 | 5.36 | 5.27
2019-07-03 02:30 | 5.13 | 5.03
2019-07-03 03:00 | 5.05 | 4.95
2019-07-03 03:30 | 4.97 | 4.87
2019-07-03 04:00 | 5.06 | 4.95
2019-07-03 04:30 | 5.28 | 5.18
2019-07-03 05:00 | 5.78 | 5.7
2019-07-03 05:30 | 6.33 | 6.27
2019-07-03 06:00 | 6.85 | 6.8
2019-07-03 06:30 | 7.38 | 7.35
2019-07-03 07:00 | 8.2 | 8.15
2019-07-03 07:30 | 8.32 | 8.27
2019-07-03 08:00 | 7.88 | 7.83
2019-07-03 08:30 | 6.96 | 6.91
2019-07-03 09:00 | 6.18 | 6.13
2019-07-03 09:30 | 6.25 | 6.19
2019-07-03 10:00 | 5.54 | 5.49
2019-07-03 10:30 | 4.17 | 4.11
2019-07-03 11:00 | 4.06 | 4
2019-07-03 11:30 | 5.14 | 5.1
2019-07-03 12:00 | 5.39 | 5.34
2019-07-03 12:30 | 3.95 | 3.89
2019-07-03 13:00 | 4.01 | 3.96
2019-07-03 13:30 | 4.67 | 4.61
2019-07-03 14:00 | 4.96 | 4.91
2019-07-03 14:30 | 4.88 | 4.84
2019-07-03 15:00 | 5.63 | 5.59
2019-07-03 15:30 | 6.31 | 6.28
2019-07-03 16:00 | 7.06 | 7.02
2019-07-03 16:30 | 8.16 | 8.14
2019-07-03 17:00 | 9.69 | 9.67
2019-07-03 17:30 | 11.32 | 11.32
2019-07-03 18:00 | 12.47 | 12.47
2019-07-03 18:30 | 12.85 | 12.84
2019-07-03 19:00 | 12.98 | 12.98
2019-07-03 19:30 | 12.72 | 12.72
2019-07-03 20:00 | 12.71 | 12.71
2019-07-03 20:30 | 12.6 | 12.6
2019-07-03 21:00 | 12.22 | 12.22
2019-07-03 21:30 | 11.44 | 11.43
2019-07-03 22:00 | 10.49 | 10.48
2019-07-03 22:30 | 9.5 | 9.48
2019-07-03 23:00 | 8.96 | 8.92
2019-07-03 23:30 | 7.96 | 7.92
2019-07-04 | 7.06 | 7
2019-07-04 00:30 | 6.28 | 6.21
2019-07-04 01:00 | 5.85 | 5.78
2019-07-04 01:30 | 5.49 | 5.41
2019-07-04 02:00 | 5.17 | 5.08
2019-07-04 02:30 | 5.02 | 4.92
2019-07-04 03:00 | 4.88 | 4.78
2019-07-04 03:30 | 4.81 | 4.71
2019-07-04 04:00 | 4.96 | 4.86
2019-07-04 04:30 | 5.19 | 5.1
2019-07-04 05:00 | 5.5 | 5.42
2019-07-04 05:30 | 6.02 | 5.95
2019-07-04 06:00 | 6.58 | 6.53
2019-07-04 06:30 | 7.55 | 7.52
2019-07-04 07:00 | 7.85 | 7.8
2019-07-04 07:30 | 7.88 | 7.83
2019-07-04 08:00 | 7.25 | 7.19
2019-07-04 08:30 | 6.45 | 6.39
2019-07-04 09:00 | 6.39 | 6.34
2019-07-04 09:30 | 6.6 | 6.56
2019-07-04 10:00 | 6.78 | 6.74
2019-07-04 10:30 | 4.19 | 4.14
2019-07-04 11:00 | 3.98 | 3.94
2019-07-04 11:30 | 6.68 | 6.64
2019-07-04 12:00 | 4.5 | 4.45
2019-07-04 12:30 | 3.68 | 3.64
2019-07-04 13:00 | 5.82 | 5.79
2019-07-04 13:30 | 4.61 | 4.57
2019-07-04 14:00 | 6.59 | 6.54
2019-07-04 14:30 | 6.81 | 6.77
2019-07-04 15:00 | 7.64 | 7.6
2019-07-04 15:30 | 7.86 | 7.82
2019-07-04 16:00 | 8.56 | 8.52
2019-07-04 16:30 | 9.05 | 9.02
2019-07-04 17:00 | 9.93 | 9.91
2019-07-04 17:30 | 11.28 | 11.27
2019-07-04 18:00 | 12.72 | 12.72
2019-07-04 18:30 | 13.1 | 13.09
2019-07-04 19:00 | 13.46 | 13.46
2019-07-04 19:30 | 13.1 | 13.1
2019-07-04 20:00 | 13.18 | 13.18
2019-07-04 20:30 | 13.13 | 13.13
2019-07-04 21:00 | 12.71 | 12.71
2019-07-04 21:30 | 12.19 | 12.18
2019-07-04 22:00 | 11.1 | 11.09
2019-07-04 22:30 | 10.11 | 10.09
2019-07-04 23:00 | 9.6 | 9.57
2019-07-04 23:30 | 8.56 | 8.52
2019-07-05 | 7.43 | 7.37
2019-07-05 00:30 | 6.63 | 6.56
2019-07-05 01:00 | 6.16 | 6.09
2019-07-05 01:30 | 5.67 | 5.59
2019-07-05 02:00 | 5.47 | 5.38
2019-07-05 02:30 | 5.17 | 5.08
2019-07-05 03:00 | 5.07 | 4.98
2019-07-05 03:30 | 5.02 | 4.93
2019-07-05 04:00 | 5.06 | 4.97
2019-07-05 04:30 | 5.2 | 5.1
2019-07-05 05:00 | 5.64 | 5.56
2019-07-05 05:30 | 6.11 | 6.05
2019-07-05 06:00 | 7.01 | 6.97
2019-07-05 06:30 | 7.76 | 7.74
2019-07-05 07:00 | 7.83 | 7.79
2019-07-05 07:30 | 8.15 | 8.11
2019-07-05 08:00 | 7.42 | 7.37
2019-07-05 08:30 | 6.94 | 6.89
2019-07-05 09:00 | 6.23 | 6.18
2019-07-05 09:30 | 5.52 | 5.47
2019-07-05 10:00 | 4.63 | 4.59
2019-07-05 10:30 | 5.38 | 5.33
2019-07-05 11:00 | 4.84 | 4.78
2019-07-05 11:30 | 4.04 | 3.98
2019-07-05 12:00 | 5.9 | 5.85
2019-07-05 12:30 | 5.63 | 5.57
2019-07-05 13:00 | 5.19 | 5.13
2019-07-05 13:30 | 5.44 | 5.38
2019-07-05 14:00 | 6.56 | 6.5
2019-07-05 14:30 | 6.28 | 6.22
2019-07-05 15:00 | 6.5 | 6.45
2019-07-05 15:30 | 6.85 | 6.8
2019-07-05 16:00 | 7.26 | 7.22
2019-07-05 16:30 | 8.42 | 8.38
2019-07-05 17:00 | 9.9 | 9.87
2019-07-05 17:30 | 10.97 | 10.96
2019-07-05 18:00 | 12.06 | 12.06
2019-07-05 18:30 | 12.46 | 12.45
2019-07-05 19:00 | 12.6 | 12.6
2019-07-05 19:30 | 12.37 | 12.37
2019-07-05 20:00 | 12.3 | 12.3
2019-07-05 20:30 | 12.35 | 12.35
2019-07-05 21:00 | 11.84 | 11.83
2019-07-05 21:30 | 11.22 | 11.21
2019-07-05 22:00 | 10.43 | 10.41
2019-07-05 22:30 | 9.77 | 9.75
2019-07-05 23:00 | 9.65 | 9.62
2019-07-05 23:30 | 8.74 | 8.71
2019-07-06 | 7.75 | 7.71
2019-07-06 00:30 | 6.88 | 6.83
2019-07-06 01:00 | 6.31 | 6.25
2019-07-06 01:30 | 5.87 | 5.8
2019-07-06 02:00 | 5.58 | 5.51
2019-07-06 02:30 | 5.32 | 5.24
2019-07-06 03:00 | 5.08 | 4.99
2019-07-06 03:30 | 5.01 | 4.92
2019-07-06 04:00 | 4.98 | 4.88
2019-07-06 04:30 | 5 | 4.9
2019-07-06 05:00 | 5.05 | 4.96
2019-07-06 05:30 | 5.19 | 5.11
2019-07-06 06:00 | 5.44 | 5.36
2019-07-06 06:30 | 5.95 | 5.89
2019-07-06 07:00 | 6.17 | 6.09
2019-07-06 07:30 | 6.7 | 6.6
2019-07-06 08:00 | 7.3 | 7.22
2019-07-06 08:30 | 7.92 | 7.86
2019-07-06 09:00 | 8.11 | 8.06
2019-07-06 09:30 | 8.14 | 8.1
2019-07-06 10:00 | 8.44 | 8.41
2019-07-06 10:30 | 7.18 | 7.14
2019-07-06 11:00 | 6.46 | 6.42
2019-07-06 11:30 | 6.51 | 6.48
2019-07-06 12:00 | 6.07 | 6.03
2019-07-06 12:30 | 5.8 | 5.76
2019-07-06 13:00 | 6.8 | 6.76
2019-07-06 13:30 | 7.14 | 7.1
2019-07-06 14:00 | 7.23 | 7.19
2019-07-06 14:30 | 6.09 | 6.05
2019-07-06 15:00 | 6.6 | 6.55
2019-07-06 15:30 | 7.66 | 7.61
2019-07-06 16:00 | 8.83 | 8.79
2019-07-06 16:30 | 9.93 | 9.9
2019-07-06 17:00 | 10.71 | 10.68
2019-07-06 17:30 | 11.55 | 11.54
2019-07-06 18:00 | 12.21 | 12.2
2019-07-06 18:30 | 12.09 | 12.08
2019-07-06 19:00 | 12.17 | 12.16
2019-07-06 19:30 | 11.75 | 11.74
2019-07-06 20:00 | 11.68 | 11.68
2019-07-06 20:30 | 11.53 | 11.53
2019-07-06 21:00 | 11.08 | 11.07
2019-07-06 21:30 | 10.45 | 10.43
2019-07-06 22:00 | 9.94 | 9.91
2019-07-06 22:30 | 9.66 | 9.64
2019-07-06 23:00 | 9.55 | 9.52
2019-07-06 23:30 | 8.74 | 8.71
2019-07-07 | 7.77 | 7.73
2019-07-07 00:30 | 7 | 6.94
2019-07-07 01:00 | 6.39 | 6.33
2019-07-07 01:30 | 6 | 5.93
2019-07-07 02:00 | 5.53 | 5.45
2019-07-07 02:30 | 5.28 | 5.19
2019-07-07 03:00 | 5.21 | 5.12
2019-07-07 03:30 | 5.03 | 4.93
2019-07-07 04:00 | 4.9 | 4.8
2019-07-07 04:30 | 5.03 | 4.94
2019-07-07 05:00 | 4.9 | 4.8
2019-07-07 05:30 | 5.09 | 5
2019-07-07 06:00 | 5.22 | 5.13
2019-07-07 06:30 | 5.49 | 5.41
2019-07-07 07:00 | 5.67 | 5.55
2019-07-07 07:30 | 6.41 | 6.3
2019-07-07 08:00 | 6.93 | 6.84
2019-07-07 08:30 | 7.61 | 7.53
2019-07-07 09:00 | 8.18 | 8.13
2019-07-07 09:30 | 7.35 | 7.3
2019-07-07 10:00 | 6.97 | 6.93
2019-07-07 10:30 | 6.87 | 6.83
2019-07-07 11:00 | 5.26 | 5.22
2019-07-07 11:30 | 5 | 4.96
2019-07-07 12:00 | 5.52 | 5.48
2019-07-07 12:30 | 6.33 | 6.29
2019-07-07 13:00 | 6.11 | 6.07
2019-07-07 13:30 | 6.89 | 6.85
2019-07-07 14:00 | 7.8 | 7.75
2019-07-07 14:30 | 7.73 | 7.68
2019-07-07 15:00 | 8.18 | 8.13
2019-07-07 15:30 | 8.3 | 8.25
2019-07-07 16:00 | 8.79 | 8.74
2019-07-07 16:30 | 9.64 | 9.6
2019-07-07 17:00 | 10.64 | 10.61
2019-07-07 17:30 | 12.07 | 12.06
2019-07-07 18:00 | 13.14 | 13.13
2019-07-07 18:30 | 13.17 | 13.17
2019-07-07 19:00 | 12.98 | 12.97
2019-07-07 19:30 | 12.33 | 12.33
2019-07-07 20:00 | 11.93 | 11.92
2019-07-07 20:30 | 11.76 | 11.75
2019-07-07 21:00 | 11.4 | 11.39
2019-07-07 21:30 | 10.84 | 10.83
2019-07-07 22:00 | 10.09 | 10.07
2019-07-07 22:30 | 9.58 | 9.55
2019-07-07 23:00 | 9.17 | 9.14
2019-07-07 23:30 | 8.27 | 8.23
2019-07-08 | 7.24 | 7.19
2019-07-08 00:30 | 6.47 | 6.41
2019-07-08 01:00 | 5.97 | 5.9
2019-07-08 01:30 | 5.58 | 5.5
2019-07-08 02:00 | 5.27 | 5.17
2019-07-08 02:30 | 5.07 | 4.98
2019-07-08 03:00 | 4.91 | 4.8
2019-07-08 03:30 | 4.9 | 4.78
2019-07-08 04:00 | 5.01 | 4.91
2019-07-08 04:30 | 5.24 | 5.15
2019-07-08 05:00 | 5.57 | 5.49
2019-07-08 05:30 | 5.91 | 5.84
2019-07-08 06:00 | 6.48 | 6.41
2019-07-08 06:30 | 6.9 | 6.86
2019-07-08 07:00 | 7.04 | 6.96
2019-07-08 07:30 | 7.23 | 7.16
2019-07-08 08:00 | 6.98 | 6.9
2019-07-08 08:30 | 7 | 6.93
2019-07-08 09:00 | 7.05 | 6.99
2019-07-08 09:30 | 7.37 | 7.31
2019-07-08 10:00 | 7.06 | 7.02
2019-07-08 10:30 | 5.67 | 5.63
2019-07-08 11:00 | 6.96 | 6.92
2019-07-08 11:30 | 6.23 | 6.19
2019-07-08 12:00 | 6.05 | 6.01
2019-07-08 12:30 | 8.59 | 8.56
2019-07-08 13:00 | 8.22 | 8.18
2019-07-08 13:30 | 7.4 | 7.37
2019-07-08 14:00 | 6.75 | 6.71
2019-07-08 14:30 | 7.86 | 7.82
2019-07-08 15:00 | 7.38 | 7.34
2019-07-08 15:30 | 7.54 | 7.5
2019-07-08 16:00 | 7.45 | 7.42
2019-07-08 16:30 | 9.06 | 9.03
2019-07-08 17:00 | 10.49 | 10.48
2019-07-08 17:30 | 12.46 | 12.46
2019-07-08 18:00 | 13.94 | 13.94
2019-07-08 18:30 | 14.2 | 14.2
2019-07-08 19:00 | 14.05 | 14.05
2019-07-08 19:30 | 13.46 | 13.46
2019-07-08 20:00 | 12.95 | 12.95
2019-07-08 20:30 | 13.01 | 13.01
2019-07-08 21:00 | 12.41 | 12.41
2019-07-08 21:30 | 11.41 | 11.4
2019-07-08 22:00 | 10.58 | 10.56
2019-07-08 22:30 | 9.74 | 9.71
2019-07-08 23:00 | 9.18 | 9.14
2019-07-08 23:30 | 8.25 | 8.21
2019-07-09 | 7.31 | 7.26
2019-07-09 00:30 | 6.54 | 6.47
2019-07-09 01:00 | 6.14 | 6.07
2019-07-09 01:30 | 5.69 | 5.61
2019-07-09 02:00 | 5.41 | 5.33
2019-07-09 02:30 | 5.27 | 5.18
2019-07-09 03:00 | 5.13 | 5.04
2019-07-09 03:30 | 5.1 | 5
2019-07-09 04:00 | 5.1 | 5
2019-07-09 04:30 | 5.36 | 5.27
2019-07-09 05:00 | 5.76 | 5.68
2019-07-09 05:30 | 6.23 | 6.16
2019-07-09 06:00 | 7.1 | 7.06
2019-07-09 06:30 | 7.89 | 7.86
2019-07-09 07:00 | 8.3 | 8.26
2019-07-09 07:30 | 8.42 | 8.37
2019-07-09 08:00 | 7.6 | 7.55
2019-07-09 08:30 | 7.05 | 7.01
2019-07-09 09:00 | 6.51 | 6.47
2019-07-09 09:30 | 6.54 | 6.49
2019-07-09 10:00 | 5.97 | 5.93
2019-07-09 10:30 | 5.28 | 5.23
2019-07-09 11:00 | 4.77 | 4.72
2019-07-09 11:30 | 4.52 | 4.47
2019-07-09 12:00 | 4.37 | 4.31
2019-07-09 12:30 | 4.31 | 4.24
2019-07-09 13:00 | 4.22 | 4.15
2019-07-09 13:30 | 4.29 | 4.22
2019-07-09 14:00 | 4.9 | 4.84
2019-07-09 14:30 | 5.46 | 5.41
2019-07-09 15:00 | 5.6 | 5.56
2019-07-09 15:30 | 5.83 | 5.8
2019-07-09 16:00 | 6.79 | 6.76
2019-07-09 16:30 | 8.21 | 8.19
2019-07-09 17:00 | 9.6 | 9.58
2019-07-09 17:30 | 11.11 | 11.1
2019-07-09 18:00 | 12.41 | 12.41
2019-07-09 18:30 | 13.05 | 13.05
2019-07-09 19:00 | 13.44 | 13.44
2019-07-09 19:30 | 12.91 | 12.91
2019-07-09 20:00 | 12.92 | 12.92
2019-07-09 20:30 | 13.06 | 13.06
2019-07-09 21:00 | 12.51 | 12.51
2019-07-09 21:30 | 11.76 | 11.76
2019-07-09 22:00 | 10.74 | 10.73
2019-07-09 22:30 | 9.79 | 9.78
2019-07-09 23:00 | 9.13 | 9.1
2019-07-09 23:30 | 8.27 | 8.23
2019-07-10 | 7.45 | 7.4
2019-07-10 00:30 | 6.62 | 6.55
2019-07-10 01:00 | 6.2 | 6.13
2019-07-10 01:30 | 5.92 | 5.85
2019-07-10 02:00 | 5.6 | 5.51
2019-07-10 02:30 | 5.37 | 5.28
2019-07-10 03:00 | 5.19 | 5.1
2019-07-10 03:30 | 5.25 | 5.15
2019-07-10 04:00 | 5.28 | 5.19
2019-07-10 04:30 | 5.57 | 5.48
2019-07-10 05:00 | 5.92 | 5.84
2019-07-10 05:30 | 6.56 | 6.51
2019-07-10 06:00 | 7 | 6.95
2019-07-10 06:30 | 7.72 | 7.68
2019-07-10 07:00 | 8.61 | 8.57
2019-07-10 07:30 | 8.78 | 8.74
2019-07-10 08:00 | 8.5 | 8.46
2019-07-10 08:30 | 7.43 | 7.39
2019-07-10 09:00 | 6.47 | 6.43
2019-07-10 09:30 | 5.56 | 5.51
2019-07-10 10:00 | 5.35 | 5.3
2019-07-10 10:30 | 4.29 | 4.23
2019-07-10 11:00 | 3.72 | 3.66
2019-07-10 11:30 | 3.53 | 3.48
2019-07-10 12:00 | 3.31 | 3.26
2019-07-10 12:30 | 3.29 | 3.23
2019-07-10 13:00 | 3.35 | 3.3
2019-07-10 13:30 | 3.42 | 3.38
2019-07-10 14:00 | 3.67 | 3.62
2019-07-10 14:30 | 4.09 | 4.03
2019-07-10 15:00 | 4.69 | 4.64
2019-07-10 15:30 | 5.51 | 5.46
2019-07-10 16:00 | 6.58 | 6.54
2019-07-10 16:30 | 7.91 | 7.88
2019-07-10 17:00 | 9.41 | 9.38
2019-07-10 17:30 | 10.93 | 10.92
2019-07-10 18:00 | 12.35 | 12.34
2019-07-10 18:30 | 12.91 | 12.91
2019-07-10 19:00 | 13.02 | 13.02
2019-07-10 19:30 | 12.97 | 12.96
2019-07-10 20:00 | 13.1 | 13.09
2019-07-10 20:30 | 13.24 | 13.23
2019-07-10 21:00 | 12.79 | 12.78
2019-07-10 21:30 | 12.08 | 12.08
2019-07-10 22:00 | 11.38 | 11.37
2019-07-10 22:30 | 10.72 | 10.71
2019-07-10 23:00 | 10.42 | 10.4
2019-07-10 23:30 | 9.39 | 9.37
2019-07-11 | 8.41 | 8.37
2019-07-11 00:30 | 7.49 | 7.44
2019-07-11 01:00 | 6.96 | 6.91
2019-07-11 01:30 | 6.51 | 6.45
2019-07-11 02:00 | 6.14 | 6.07
2019-07-11 02:30 | 5.92 | 5.84
2019-07-11 03:00 | 5.81 | 5.74
2019-07-11 03:30 | 5.78 | 5.7
2019-07-11 04:00 | 5.78 | 5.7
2019-07-11 04:30 | 5.98 | 5.9
2019-07-11 05:00 | 6.44 | 6.37
2019-07-11 05:30 | 7.13 | 7.08
2019-07-11 06:00 | 8.16 | 8.13
2019-07-11 06:30 | 8.94 | 8.92
2019-07-11 07:00 | 9.54 | 9.51
2019-07-11 07:30 | 9.46 | 9.43
2019-07-11 08:00 | 8.81 | 8.78
2019-07-11 08:30 | 7.78 | 7.74
2019-07-11 09:00 | 7.26 | 7.22
2019-07-11 09:30 | 6.16 | 6.11
2019-07-11 10:00 | 5.17 | 5.13
2019-07-11 10:30 | 4.46 | 4.41
2019-07-11 11:00 | 3.93 | 3.88
2019-07-11 11:30 | 3.58 | 3.53
2019-07-11 12:00 | 3.41 | 3.35
2019-07-11 12:30 | 3.39 | 3.33
2019-07-11 13:00 | 3.4 | 3.34
2019-07-11 13:30 | 3.56 | 3.5
2019-07-11 14:00 | 3.81 | 3.76
2019-07-11 14:30 | 4.18 | 4.13
2019-07-11 15:00 | 4.92 | 4.88
2019-07-11 15:30 | 5.67 | 5.63
2019-07-11 16:00 | 6.54 | 6.5
2019-07-11 16:30 | 7.86 | 7.83
2019-07-11 17:00 | 9.16 | 9.14
2019-07-11 17:30 | 10.63 | 10.62
2019-07-11 18:00 | 12.2 | 12.2
2019-07-11 18:30 | 12.99 | 12.98
2019-07-11 19:00 | 13.2 | 13.2
2019-07-11 19:30 | 13.01 | 13.01
2019-07-11 20:00 | 13.1 | 13.1
2019-07-11 20:30 | 13.3 | 13.3
2019-07-11 21:00 | 13 | 13
2019-07-11 21:30 | 12.27 | 12.27
2019-07-11 22:00 | 11.41 | 11.4
2019-07-11 22:30 | 10.69 | 10.68
2019-07-11 23:00 | 10.07 | 10.05
2019-07-11 23:30 | 9.13 | 9.1
2019-07-12 | 8.04 | 8
2019-07-12 00:30 | 7.25 | 7.2
2019-07-12 01:00 | 6.68 | 6.62
2019-07-12 01:30 | 6.24 | 6.17
2019-07-12 02:00 | 5.87 | 5.79
2019-07-12 02:30 | 5.58 | 5.5
2019-07-12 03:00 | 5.46 | 5.37
2019-07-12 03:30 | 5.52 | 5.43
2019-07-12 04:00 | 5.49 | 5.4
2019-07-12 04:30 | 5.87 | 5.79
2019-07-12 05:00 | 6.24 | 6.17
2019-07-12 05:30 | 6.91 | 6.85
2019-07-12 06:00 | 7.52 | 7.47
2019-07-12 06:30 | 8.34 | 8.31
2019-07-12 07:00 | 8.8 | 8.75
2019-07-12 07:30 | 9.06 | 9.02
2019-07-12 08:00 | 8.5 | 8.47
2019-07-12 08:30 | 7.37 | 7.33
2019-07-12 09:00 | 6.51 | 6.46
2019-07-12 09:30 | 5.6 | 5.54
2019-07-12 10:00 | 4.73 | 4.67
2019-07-12 10:30 | 4.01 | 3.94
2019-07-12 11:00 | 3.39 | 3.31
2019-07-12 11:30 | 2.82 | 2.71
2019-07-12 12:00 | 2.81 | 2.72
2019-07-12 12:30 | 2.83 | 2.75
2019-07-12 13:00 | 2.71 | 2.61
2019-07-12 13:30 | 2.92 | 2.84
2019-07-12 14:00 | 3.29 | 3.22
2019-07-12 14:30 | 3.78 | 3.71
2019-07-12 15:00 | 4.35 | 4.29
2019-07-12 15:30 | 5.11 | 5.05
2019-07-12 16:00 | 6.03 | 5.99
2019-07-12 16:30 | 7.23 | 7.2
2019-07-12 17:00 | 8.43 | 8.4
2019-07-12 17:30 | 9.61 | 9.6
2019-07-12 18:00 | 10.78 | 10.78
2019-07-12 18:30 | 11.36 | 11.35
2019-07-12 19:00 | 11.74 | 11.74
2019-07-12 19:30 | 11.84 | 11.83
2019-07-12 20:00 | 12.1 | 12.1
2019-07-12 20:30 | 12.36 | 12.35
2019-07-12 21:00 | 11.94 | 11.94
2019-07-12 21:30 | 11.32 | 11.31
2019-07-12 22:00 | 10.76 | 10.75
2019-07-12 22:30 | 10.36 | 10.34
2019-07-12 23:00 | 10.05 | 10.03
2019-07-12 23:30 | 9.03 | 9
2019-07-13 | 8.27 | 8.23
2019-07-13 00:30 | 7.43 | 7.38
2019-07-13 01:00 | 6.95 | 6.89
2019-07-13 01:30 | 6.5 | 6.43
2019-07-13 02:00 | 5.98 | 5.9
2019-07-13 02:30 | 5.84 | 5.77
2019-07-13 03:00 | 5.65 | 5.57
2019-07-13 03:30 | 5.6 | 5.51
2019-07-13 04:00 | 5.67 | 5.59
2019-07-13 04:30 | 5.79 | 5.71
2019-07-13 05:00 | 5.81 | 5.73
2019-07-13 05:30 | 6.17 | 6.1
2019-07-13 06:00 | 6.39 | 6.33
2019-07-13 06:30 | 6.79 | 6.72
2019-07-13 07:00 | 7.24 | 7.16
2019-07-13 07:30 | 7.72 | 7.66
2019-07-13 08:00 | 7.76 | 7.7
2019-07-13 08:30 | 7.56 | 7.51
2019-07-13 09:00 | 7.13 | 7.09
2019-07-13 09:30 | 6.74 | 6.71
2019-07-13 10:00 | 6.25 | 6.21
2019-07-13 10:30 | 5.25 | 5.21
2019-07-13 11:00 | 4.4 | 4.34
2019-07-13 11:30 | 3.82 | 3.76
2019-07-13 12:00 | 3.79 | 3.73
2019-07-13 12:30 | 3.91 | 3.85
2019-07-13 13:00 | 3.56 | 3.5
2019-07-13 13:30 | 3.56 | 3.5
2019-07-13 14:00 | 3.94 | 3.88
2019-07-13 14:30 | 4.39 | 4.32
2019-07-13 15:00 | 4.81 | 4.75
2019-07-13 15:30 | 5.63 | 5.57
2019-07-13 16:00 | 6.48 | 6.42
2019-07-13 16:30 | 7.7 | 7.65
2019-07-13 17:00 | 8.96 | 8.92
2019-07-13 17:30 | 10.31 | 10.3
2019-07-13 18:00 | 11.34 | 11.33
2019-07-13 18:30 | 11.44 | 11.43
2019-07-13 19:00 | 11.53 | 11.52
2019-07-13 19:30 | 11.4 | 11.4
2019-07-13 20:00 | 11.61 | 11.61
2019-07-13 20:30 | 11.7 | 11.69
2019-07-13 21:00 | 11.42 | 11.41
2019-07-13 21:30 | 10.85 | 10.84
2019-07-13 22:00 | 10.31 | 10.29
2019-07-13 22:30 | 9.97 | 9.95
2019-07-13 23:00 | 9.79 | 9.76
2019-07-13 23:30 | 9 | 8.97
2019-07-14 | 8.33 | 8.29
2019-07-14 00:30 | 7.47 | 7.42
2019-07-14 01:00 | 7.08 | 7.02
2019-07-14 01:30 | 6.47 | 6.41
2019-07-14 02:00 | 6.16 | 6.09
2019-07-14 02:30 | 5.97 | 5.9
2019-07-14 03:00 | 5.9 | 5.82
2019-07-14 03:30 | 5.66 | 5.58
2019-07-14 04:00 | 5.72 | 5.63
2019-07-14 04:30 | 5.81 | 5.72
2019-07-14 05:00 | 5.81 | 5.72
2019-07-14 05:30 | 6.12 | 6.05
2019-07-14 06:00 | 6.55 | 6.48
2019-07-14 06:30 | 6.95 | 6.89
2019-07-14 07:00 | 7.45 | 7.37
2019-07-14 07:30 | 8.11 | 8.05
2019-07-14 08:00 | 8.23 | 8.18
2019-07-14 08:30 | 8.24 | 8.2
2019-07-14 09:00 | 8.01 | 7.98
2019-07-14 09:30 | 7.34 | 7.3
2019-07-14 10:00 | 6.62 | 6.59
2019-07-14 10:30 | 5.75 | 5.72
2019-07-14 11:00 | 5.16 | 5.13
2019-07-14 11:30 | 4.69 | 4.65
2019-07-14 12:00 | 4.35 | 4.3
2019-07-14 12:30 | 4.22 | 4.16
2019-07-14 13:00 | 4.13 | 4.07
2019-07-14 13:30 | 4.02 | 3.94
2019-07-14 14:00 | 4.42 | 4.35
2019-07-14 14:30 | 4.96 | 4.89
2019-07-14 15:00 | 5.44 | 5.37
2019-07-14 15:30 | 6.27 | 6.21
2019-07-14 16:00 | 7.33 | 7.27
2019-07-14 16:30 | 8.84 | 8.8
2019-07-14 17:00 | 10.86 | 10.84
2019-07-14 17:30 | 12.91 | 12.9
2019-07-14 18:00 | 14.58 | 14.58
2019-07-14 18:30 | 15.32 | 15.31
2019-07-14 19:00 | 15.67 | 15.67
2019-07-14 19:30 | 15.48 | 15.47
2019-07-14 20:00 | 15.69 | 15.69
2019-07-14 20:30 | 15.77 | 15.77
2019-07-14 21:00 | 15.26 | 15.26
2019-07-14 21:30 | 14.47 | 14.47
2019-07-14 22:00 | 13.45 | 13.45
2019-07-14 22:30 | 12.53 | 12.52
2019-07-14 23:00 | 11.72 | 11.71
2019-07-14 23:30 | 10.6 | 10.59
2019-07-15 | 9.44 | 9.41
2019-07-15 00:30 | 8.56 | 8.53
2019-07-15 01:00 | 7.97 | 7.93
2019-07-15 01:30 | 7.44 | 7.39
2019-07-15 02:00 | 7.04 | 6.98
2019-07-15 02:30 | 6.83 | 6.77
2019-07-15 03:00 | 6.71 | 6.65
2019-07-15 03:30 | 6.72 | 6.67
2019-07-15 04:00 | 6.78 | 6.72
2019-07-15 04:30 | 7.2 | 7.15
2019-07-15 05:00 | 7.79 | 7.75
2019-07-15 05:30 | 8.77 | 8.74
2019-07-15 06:00 | 10.08 | 10.07
2019-07-15 06:30 | 11.41 | 11.4
2019-07-15 07:00 | 13.1 | 13.09
2019-07-15 07:30 | 14.25 | 14.25
2019-07-15 08:00 | 13.11 | 13.11
2019-07-15 08:30 | 10.96 | 10.95
2019-07-15 09:00 | 9.16 | 9.15
2019-07-15 09:30 | 8 | 7.99
2019-07-15 10:00 | 6.93 | 6.92
2019-07-15 10:30 | 5.9 | 5.88
2019-07-15 11:00 | 5.17 | 5.15
2019-07-15 11:30 | 4.76 | 4.74
2019-07-15 12:00 | 4.28 | 4.25
2019-07-15 12:30 | 4.18 | 4.14
2019-07-15 13:00 | 4.07 | 4.03
2019-07-15 13:30 | 4.08 | 4.03
2019-07-15 14:00 | 4.31 | 4.26
2019-07-15 14:30 | 4.69 | 4.64
2019-07-15 15:00 | 5.17 | 5.12
2019-07-15 15:30 | 6.05 | 6
2019-07-15 16:00 | 7.46 | 7.42
2019-07-15 16:30 | 9.18 | 9.16
2019-07-15 17:00 | 11.09 | 11.07
2019-07-15 17:30 | 13.56 | 13.56
2019-07-15 18:00 | 15.82 | 15.82
2019-07-15 18:30 | 16.78 | 16.78
2019-07-15 19:00 | 17.25 | 17.24
2019-07-15 19:30 | 17.37 | 17.36
2019-07-15 20:00 | 17.28 | 17.28
2019-07-15 20:30 | 17.13 | 17.13
2019-07-15 21:00 | 16.63 | 16.63
2019-07-15 21:30 | 15.47 | 15.47
2019-07-15 22:00 | 13.98 | 13.98
2019-07-15 22:30 | 12.67 | 12.66
2019-07-15 23:00 | 11.76 | 11.75
2019-07-15 23:30 | 10.5 | 10.48
2019-07-16 | 9.25 | 9.23
2019-07-16 00:30 | 8.38 | 8.34
2019-07-16 01:00 | 7.93 | 7.89
2019-07-16 01:30 | 7.44 | 7.39
2019-07-16 02:00 | 7.13 | 7.08
2019-07-16 02:30 | 6.96 | 6.9
2019-07-16 03:00 | 6.78 | 6.72
2019-07-16 03:30 | 6.86 | 6.8
2019-07-16 04:00 | 6.9 | 6.84
2019-07-16 04:30 | 7.37 | 7.32
2019-07-16 05:00 | 8.08 | 8.04
2019-07-16 05:30 | 9.23 | 9.21
2019-07-16 06:00 | 10.87 | 10.86
2019-07-16 06:30 | 12.44 | 12.44
2019-07-16 07:00 | 13.5 | 13.5
2019-07-16 07:30 | 13.92 | 13.91
2019-07-16 08:00 | 12.57 | 12.56
2019-07-16 08:30 | 10.24 | 10.23
2019-07-16 09:00 | 8.48 | 8.47
2019-07-16 09:30 | 7.26 | 7.25
2019-07-16 10:00 | 6.1 | 6.09
2019-07-16 10:30 | 4.91 | 4.88
2019-07-16 11:00 | 4.11 | 4.07
2019-07-16 11:30 | 3.91 | 3.87
2019-07-16 12:00 | 3.49 | 3.44
2019-07-16 12:30 | 3.46 | 3.41
2019-07-16 13:00 | 3.47 | 3.42
2019-07-16 13:30 | 3.3 | 3.23
2019-07-16 14:00 | 3.7 | 3.64
2019-07-16 14:30 | 4.02 | 3.96
2019-07-16 15:00 | 4.63 | 4.58
2019-07-16 15:30 | 5.6 | 5.56
2019-07-16 16:00 | 7.05 | 7.02
2019-07-16 16:30 | 8.52 | 8.5
2019-07-16 17:00 | 10.36 | 10.35
2019-07-16 17:30 | 12.48 | 12.48
2019-07-16 18:00 | 14.58 | 14.58
2019-07-16 18:30 | 15.59 | 15.59
2019-07-16 19:00 | 16.21 | 16.21
2019-07-16 19:30 | 16.22 | 16.22
2019-07-16 20:00 | 16.57 | 16.56
2019-07-16 20:30 | 17.07 | 17.07
2019-07-16 21:00 | 16.37 | 16.36
2019-07-16 21:30 | 15.3 | 15.3
2019-07-16 22:00 | 13.94 | 13.94
2019-07-16 22:30 | 12.98 | 12.98
2019-07-16 23:00 | 11.88 | 11.87
2019-07-16 23:30 | 10.46 | 10.45
2019-07-17 | 9.24 | 9.21
2019-07-17 00:30 | 8.25 | 8.22
2019-07-17 01:00 | 7.85 | 7.81
2019-07-17 01:30 | 7.4 | 7.36
2019-07-17 02:00 | 7.07 | 7.03
2019-07-17 02:30 | 6.8 | 6.75
2019-07-17 03:00 | 6.65 | 6.59
2019-07-17 03:30 | 6.68 | 6.62
2019-07-17 04:00 | 6.82 | 6.76
2019-07-17 04:30 | 7.21 | 7.16
2019-07-17 05:00 | 7.83 | 7.79
2019-07-17 05:30 | 8.96 | 8.94
2019-07-17 06:00 | 10.56 | 10.55
2019-07-17 06:30 | 11.95 | 11.94
2019-07-17 07:00 | 13.16 | 13.15
2019-07-17 07:30 | 13.78 | 13.78
2019-07-17 08:00 | 13.08 | 13.08
2019-07-17 08:30 | 11.33 | 11.32
2019-07-17 09:00 | 9.82 | 9.8
2019-07-17 09:30 | 8.51 | 8.5
2019-07-17 10:00 | 7.38 | 7.36
2019-07-17 10:30 | 6.23 | 6.2
2019-07-17 11:00 | 5.55 | 5.5
2019-07-17 11:30 | 4.9 | 4.85
2019-07-17 12:00 | 4.69 | 4.63
2019-07-17 12:30 | 4.47 | 4.42
2019-07-17 13:00 | 4.54 | 4.5
2019-07-17 13:30 | 4.4 | 4.34
2019-07-17 14:00 | 4.69 | 4.63
2019-07-17 14:30 | 4.77 | 4.72
2019-07-17 15:00 | 4.49 | 4.44
2019-07-17 15:30 | 5.45 | 5.41
2019-07-17 16:00 | 6.73 | 6.7
2019-07-17 16:30 | 8.3 | 8.27
2019-07-17 17:00 | 10.06 | 10.04
2019-07-17 17:30 | 11.83 | 11.82
2019-07-17 18:00 | 13.3 | 13.3
2019-07-17 18:30 | 14.19 | 14.19
2019-07-17 19:00 | 14.56 | 14.56
2019-07-17 19:30 | 14.78 | 14.78
2019-07-17 20:00 | 14.76 | 14.76
2019-07-17 20:30 | 15.07 | 15.07
2019-07-17 21:00 | 14.8 | 14.8
2019-07-17 21:30 | 13.89 | 13.89
2019-07-17 22:00 | 12.81 | 12.8
2019-07-17 22:30 | 11.9 | 11.89
2019-07-17 23:00 | 10.97 | 10.95
2019-07-17 23:30 | 9.85 | 9.83
2019-07-18 | 8.76 | 8.73
2019-07-18 00:30 | 7.92 | 7.88
2019-07-18 01:00 | 7.4 | 7.35
2019-07-18 01:30 | 6.98 | 6.92
2019-07-18 02:00 | 6.71 | 6.65
2019-07-18 02:30 | 6.43 | 6.37
2019-07-18 03:00 | 6.42 | 6.36
2019-07-18 03:30 | 6.44 | 6.37
2019-07-18 04:00 | 6.46 | 6.4
2019-07-18 04:30 | 6.91 | 6.85
2019-07-18 05:00 | 7.6 | 7.56
2019-07-18 05:30 | 8.68 | 8.66
2019-07-18 06:00 | 9.94 | 9.92
2019-07-18 06:30 | 11.5 | 11.49
2019-07-18 07:00 | 12.88 | 12.87
2019-07-18 07:30 | 13.46 | 13.46
2019-07-18 08:00 | 12.35 | 12.35
2019-07-18 08:30 | 10.27 | 10.26
2019-07-18 09:00 | 8.24 | 8.23
2019-07-18 09:30 | 6.84 | 6.82
2019-07-18 10:00 | 5.68 | 5.66
2019-07-18 10:30 | 4.57 | 4.53
2019-07-18 11:00 | 3.74 | 3.68
2019-07-18 11:30 | 3.2 | 3.14
2019-07-18 12:00 | 2.99 | 2.93
2019-07-18 12:30 | 2.86 | 2.8
2019-07-18 13:00 | 2.88 | 2.83
2019-07-18 13:30 | 2.91 | 2.85
2019-07-18 14:00 | 3.13 | 3.06
2019-07-18 14:30 | 3.68 | 3.63
2019-07-18 15:00 | 4.32 | 4.28
2019-07-18 15:30 | 5.14 | 5.09
2019-07-18 16:00 | 6.32 | 6.28
2019-07-18 16:30 | 7.79 | 7.77
2019-07-18 17:00 | 9.42 | 9.4
2019-07-18 17:30 | 11.31 | 11.3
2019-07-18 18:00 | 13.05 | 13.05
2019-07-18 18:30 | 13.85 | 13.85
2019-07-18 19:00 | 14.57 | 14.57
2019-07-18 19:30 | 14.62 | 14.62
2019-07-18 20:00 | 14.78 | 14.78
2019-07-18 20:30 | 15.01 | 15.01
2019-07-18 21:00 | 14.66 | 14.66
2019-07-18 21:30 | 13.92 | 13.92
2019-07-18 22:00 | 13.11 | 13.11
2019-07-18 22:30 | 12.07 | 12.06
2019-07-18 23:00 | 11.36 | 11.35
2019-07-18 23:30 | 10.21 | 10.19
2019-07-19 | 9.05 | 9.02
2019-07-19 00:30 | 8.13 | 8.1
2019-07-19 01:00 | 7.66 | 7.62
2019-07-19 01:30 | 7.12 | 7.07
2019-07-19 02:00 | 6.7 | 6.64
2019-07-19 02:30 | 6.49 | 6.44
2019-07-19 03:00 | 6.37 | 6.32
2019-07-19 03:30 | 6.52 | 6.46
2019-07-19 04:00 | 6.64 | 6.58
2019-07-19 04:30 | 7.06 | 7.01
2019-07-19 05:00 | 7.67 | 7.64
2019-07-19 05:30 | 8.66 | 8.64
2019-07-19 06:00 | 9.66 | 9.65
2019-07-19 06:30 | 10.95 | 10.94
2019-07-19 07:00 | 12.17 | 12.16
2019-07-19 07:30 | 12.9 | 12.89
2019-07-19 08:00 | 12.4 | 12.39
2019-07-19 08:30 | 10.08 | 10.07
2019-07-19 09:00 | 7.97 | 7.95
2019-07-19 09:30 | 6.54 | 6.52
2019-07-19 10:00 | 5.41 | 5.38
2019-07-19 10:30 | 4.44 | 4.38
2019-07-19 11:00 | 3.76 | 3.7
2019-07-19 11:30 | 3.19 | 3.12
2019-07-19 12:00 | 2.91 | 2.83
2019-07-19 12:30 | 2.68 | 2.59
2019-07-19 13:00 | 2.66 | 2.57
2019-07-19 13:30 | 2.7 | 2.61
2019-07-19 14:00 | 3.07 | 2.97
2019-07-19 14:30 | 3.44 | 3.35
2019-07-19 15:00 | 4.08 | 4
2019-07-19 15:30 | 5.08 | 5.02
2019-07-19 16:00 | 6.32 | 6.26
2019-07-19 16:30 | 7.6 | 7.56
2019-07-19 17:00 | 9.21 | 9.18
2019-07-19 17:30 | 10.83 | 10.81
2019-07-19 18:00 | 12.22 | 12.21
2019-07-19 18:30 | 13 | 12.99
2019-07-19 19:00 | 13.4 | 13.39
2019-07-19 19:30 | 13.57 | 13.57
2019-07-19 20:00 | 13.66 | 13.66
2019-07-19 20:30 | 13.92 | 13.92
2019-07-19 21:00 | 13.61 | 13.6
2019-07-19 21:30 | 13.17 | 13.16
2019-07-19 22:00 | 12.49 | 12.48
2019-07-19 22:30 | 12.1 | 12.09
2019-07-19 23:00 | 11.67 | 11.66
2019-07-19 23:30 | 10.6 | 10.59
2019-07-20 | 9.59 | 9.57
2019-07-20 00:30 | 8.69 | 8.66
2019-07-20 01:00 | 8.13 | 8.09
2019-07-20 01:30 | 7.6 | 7.56
2019-07-20 02:00 | 7.08 | 7.03
2019-07-20 02:30 | 6.9 | 6.85
2019-07-20 03:00 | 6.73 | 6.67
2019-07-20 03:30 | 6.67 | 6.61
2019-07-20 04:00 | 6.66 | 6.61
2019-07-20 04:30 | 6.81 | 6.76
2019-07-20 05:00 | 7.05 | 7
2019-07-20 05:30 | 7.48 | 7.43
2019-07-20 06:00 | 7.85 | 7.81
2019-07-20 06:30 | 8.45 | 8.42
2019-07-20 07:00 | 9.35 | 9.32
2019-07-20 07:30 | 10.3 | 10.28
2019-07-20 08:00 | 10.46 | 10.44
2019-07-20 08:30 | 10.19 | 10.18
2019-07-20 09:00 | 9.54 | 9.53
2019-07-20 09:30 | 8.49 | 8.47
2019-07-20 10:00 | 7.3 | 7.28
2019-07-20 10:30 | 6.23 | 6.21
2019-07-20 11:00 | 5.33 | 5.3
2019-07-20 11:30 | 4.76 | 4.72
2019-07-20 12:00 | 4.31 | 4.26
2019-07-20 12:30 | 4.02 | 3.97
2019-07-20 13:00 | 3.96 | 3.91
2019-07-20 13:30 | 4.04 | 3.98
2019-07-20 14:00 | 4.28 | 4.23
2019-07-20 14:30 | 4.53 | 4.47
2019-07-20 15:00 | 4.98 | 4.93
2019-07-20 15:30 | 5.83 | 5.78
2019-07-20 16:00 | 7.15 | 7.11
2019-07-20 16:30 | 8.44 | 8.41
2019-07-20 17:00 | 9.51 | 9.48
2019-07-20 17:30 | 10.84 | 10.82
2019-07-20 18:00 | 11.94 | 11.93
2019-07-20 18:30 | 12.46 | 12.46
2019-07-20 19:00 | 12.62 | 12.61
2019-07-20 19:30 | 12.61 | 12.6
2019-07-20 20:00 | 12.84 | 12.83
2019-07-20 20:30 | 12.84 | 12.83
2019-07-20 21:00 | 12.56 | 12.56
2019-07-20 21:30 | 11.99 | 11.98
2019-07-20 22:00 | 11.5 | 11.49
2019-07-20 22:30 | 11.22 | 11.2
2019-07-20 23:00 | 10.87 | 10.86
2019-07-20 23:30 | 10.01 | 9.99
2019-07-21 | 9.08 | 9.05
2019-07-21 00:30 | 8.22 | 8.19
2019-07-21 01:00 | 7.69 | 7.65
2019-07-21 01:30 | 7.19 | 7.14
2019-07-21 02:00 | 6.75 | 6.69
2019-07-21 02:30 | 6.49 | 6.43
2019-07-21 03:00 | 6.25 | 6.18
2019-07-21 03:30 | 6.35 | 6.28
2019-07-21 04:00 | 6.24 | 6.16
2019-07-21 04:30 | 6.19 | 6.11
2019-07-21 05:00 | 6.3 | 6.23
2019-07-21 05:30 | 6.56 | 6.5
2019-07-21 06:00 | 6.91 | 6.85
2019-07-21 06:30 | 7.27 | 7.21
2019-07-21 07:00 | 7.79 | 7.7
2019-07-21 07:30 | 8.5 | 8.44
2019-07-21 08:00 | 8.77 | 8.73
2019-07-21 08:30 | 8.94 | 8.91
2019-07-21 09:00 | 8.51 | 8.48
2019-07-21 09:30 | 7.76 | 7.73
2019-07-21 10:00 | 6.8 | 6.77
2019-07-21 10:30 | 5.85 | 5.8
2019-07-21 11:00 | 5.33 | 5.29
2019-07-21 11:30 | 4.8 | 4.76
2019-07-21 12:00 | 4.42 | 4.37
2019-07-21 12:30 | 4.1 | 4.04
2019-07-21 13:00 | 4.3 | 4.24
2019-07-21 13:30 | 4.87 | 4.82
2019-07-21 14:00 | 5.39 | 5.34
2019-07-21 14:30 | 5.46 | 5.4
2019-07-21 15:00 | 5.67 | 5.62
2019-07-21 15:30 | 6.54 | 6.49
2019-07-21 16:00 | 7.56 | 7.51
2019-07-21 16:30 | 8.8 | 8.76
2019-07-21 17:00 | 10.22 | 10.19
2019-07-21 17:30 | 11.96 | 11.95
2019-07-21 18:00 | 13.39 | 13.38
2019-07-21 18:30 | 13.81 | 13.81
2019-07-21 19:00 | 13.77 | 13.76
2019-07-21 19:30 | 13.47 | 13.46
2019-07-21 20:00 | 13.42 | 13.41
2019-07-21 20:30 | 13.55 | 13.55
2019-07-21 21:00 | 13.01 | 13
2019-07-21 21:30 | 12.18 | 12.17
2019-07-21 22:00 | 11.34 | 11.33
2019-07-21 22:30 | 10.55 | 10.54
2019-07-21 23:00 | 10.06 | 10.03
2019-07-21 23:30 | 8.99 | 8.96
2019-07-22 | 7.94 | 7.9
2019-07-22 00:30 | 7.22 | 7.16
2019-07-22 01:00 | 6.77 | 6.7
2019-07-22 01:30 | 6.37 | 6.3
2019-07-22 02:00 | 5.95 | 5.87
2019-07-22 02:30 | 5.88 | 5.79
2019-07-22 03:00 | 5.82 | 5.73
2019-07-22 03:30 | 5.88 | 5.8
2019-07-22 04:00 | 5.94 | 5.86
2019-07-22 04:30 | 6.26 | 6.18
2019-07-22 05:00 | 6.89 | 6.83
2019-07-22 05:30 | 7.7 | 7.66
2019-07-22 06:00 | 8.81 | 8.78
2019-07-22 06:30 | 10.29 | 10.28
2019-07-22 07:00 | 11.75 | 11.74
2019-07-22 07:30 | 12.78 | 12.77
2019-07-22 08:00 | 12.1 | 12.09
2019-07-22 08:30 | 10.26 | 10.25
2019-07-22 09:00 | 7.84 | 7.82
2019-07-22 09:30 | 6.61 | 6.59
2019-07-22 10:00 | 5.61 | 5.58
2019-07-22 10:30 | 4.74 | 4.7
2019-07-22 11:00 | 4.08 | 4.04
2019-07-22 11:30 | 3.63 | 3.58
2019-07-22 12:00 | 3.33 | 3.28
2019-07-22 12:30 | 3.23 | 3.18
2019-07-22 13:00 | 3.45 | 3.42
2019-07-22 13:30 | 3.35 | 3.31
2019-07-22 14:00 | 3.73 | 3.68
2019-07-22 14:30 | 4.12 | 4.08
2019-07-22 15:00 | 4.77 | 4.74
2019-07-22 15:30 | 5.81 | 5.77
2019-07-22 16:00 | 7.23 | 7.2
2019-07-22 16:30 | 8.64 | 8.61
2019-07-22 17:00 | 10.5 | 10.48
2019-07-22 17:30 | 12.08 | 12.07
2019-07-22 18:00 | 13.4 | 13.39
2019-07-22 18:30 | 13.85 | 13.85
2019-07-22 19:00 | 13.98 | 13.98
2019-07-22 19:30 | 13.66 | 13.66
2019-07-22 20:00 | 13.29 | 13.29
2019-07-22 20:30 | 13.32 | 13.32
2019-07-22 21:00 | 12.71 | 12.71
2019-07-22 21:30 | 11.94 | 11.93
2019-07-22 22:00 | 10.94 | 10.93
2019-07-22 22:30 | 9.97 | 9.94
2019-07-22 23:00 | 9.27 | 9.24
2019-07-22 23:30 | 8.31 | 8.27
2019-07-23 | 7.39 | 7.34
2019-07-23 00:30 | 6.6 | 6.54
2019-07-23 01:00 | 6.14 | 6.07
2019-07-23 01:30 | 5.78 | 5.7
2019-07-23 02:00 | 5.51 | 5.43
2019-07-23 02:30 | 5.32 | 5.23
2019-07-23 03:00 | 5.27 | 5.18
2019-07-23 03:30 | 5.35 | 5.25
2019-07-23 04:00 | 5.44 | 5.35
2019-07-23 04:30 | 5.75 | 5.66
2019-07-23 05:00 | 6.26 | 6.19
2019-07-23 05:30 | 7.09 | 7.04
2019-07-23 06:00 | 7.85 | 7.81
2019-07-23 06:30 | 8.79 | 8.76
2019-07-23 07:00 | 10.2 | 10.18
2019-07-23 07:30 | 10.52 | 10.5
2019-07-23 08:00 | 9.81 | 9.79
2019-07-23 08:30 | 8.22 | 8.2
2019-07-23 09:00 | 6.65 | 6.62
2019-07-23 09:30 | 5.55 | 5.51
2019-07-23 10:00 | 4.69 | 4.64
2019-07-23 10:30 | 3.95 | 3.9
2019-07-23 11:00 | 3.32 | 3.26
2019-07-23 11:30 | 2.95 | 2.9
2019-07-23 12:00 | 2.84 | 2.78
2019-07-23 12:30 | 2.91 | 2.86
2019-07-23 13:00 | 2.86 | 2.81
2019-07-23 13:30 | 2.94 | 2.89
2019-07-23 14:00 | 3.33 | 3.28
2019-07-23 14:30 | 3.95 | 3.91
2019-07-23 15:00 | 4.47 | 4.44
2019-07-23 15:30 | 5.36 | 5.33
2019-07-23 16:00 | 6.75 | 6.73
2019-07-23 16:30 | 7.87 | 7.85
2019-07-23 17:00 | 9.38 | 9.36
2019-07-23 17:30 | 10.93 | 10.92
2019-07-23 18:00 | 12.29 | 12.29
2019-07-23 18:30 | 12.97 | 12.97
2019-07-23 19:00 | 13.29 | 13.29
2019-07-23 19:30 | 12.98 | 12.98
2019-07-23 20:00 | 12.83 | 12.83
2019-07-23 20:30 | 12.87 | 12.87
2019-07-23 21:00 | 12.22 | 12.21
2019-07-23 21:30 | 11.44 | 11.43
2019-07-23 22:00 | 10.64 | 10.62
2019-07-23 22:30 | 9.71 | 9.68
2019-07-23 23:00 | 9.15 | 9.12
2019-07-23 23:30 | 8.27 | 8.23
2019-07-24 | 7.24 | 7.19
2019-07-24 00:30 | 6.5 | 6.43
2019-07-24 01:00 | 6.18 | 6.09
2019-07-24 01:30 | 5.89 | 5.8
2019-07-24 02:00 | 5.56 | 5.47
2019-07-24 02:30 | 5.44 | 5.34
2019-07-24 03:00 | 5.32 | 5.22
2019-07-24 03:30 | 5.33 | 5.22
2019-07-24 04:00 | 5.46 | 5.36
2019-07-24 04:30 | 5.8 | 5.71
2019-07-24 05:00 | 6.32 | 6.24
2019-07-24 05:30 | 7.18 | 7.13
2019-07-24 06:00 | 8.1 | 8.06
2019-07-24 06:30 | 9.49 | 9.47
2019-07-24 07:00 | 10.73 | 10.71
2019-07-24 07:30 | 11.26 | 11.24
2019-07-24 08:00 | 10.31 | 10.29
2019-07-24 08:30 | 8.34 | 8.32
2019-07-24 09:00 | 6.65 | 6.61
2019-07-24 09:30 | 5.66 | 5.62
2019-07-24 10:00 | 4.61 | 4.57
2019-07-24 10:30 | 3.8 | 3.75
2019-07-24 11:00 | 3.21 | 3.15
2019-07-24 11:30 | 2.8 | 2.73
2019-07-24 12:00 | 2.61 | 2.55
2019-07-24 12:30 | 2.59 | 2.53
2019-07-24 13:00 | 2.52 | 2.47
2019-07-24 13:30 | 2.73 | 2.67
2019-07-24 14:00 | 3.06 | 3.02
2019-07-24 14:30 | 3.55 | 3.51
2019-07-24 15:00 | 4.18 | 4.15
2019-07-24 15:30 | 4.96 | 4.93
2019-07-24 16:00 | 6.21 | 6.18
2019-07-24 16:30 | 7.68 | 7.66
2019-07-24 17:00 | 9.22 | 9.2
2019-07-24 17:30 | 10.56 | 10.54
2019-07-24 18:00 | 12.05 | 12.05
2019-07-24 18:30 | 12.91 | 12.91
2019-07-24 19:00 | 13.19 | 13.19
2019-07-24 19:30 | 13.14 | 13.14
2019-07-24 20:00 | 12.97 | 12.97
2019-07-24 20:30 | 13.34 | 13.34
2019-07-24 21:00 | 12.77 | 12.77
2019-07-24 21:30 | 11.83 | 11.82
2019-07-24 22:00 | 10.93 | 10.91
2019-07-24 22:30 | 9.99 | 9.97
2019-07-24 23:00 | 9.48 | 9.44
2019-07-24 23:30 | 8.49 | 8.45
2019-07-25 | 7.52 | 7.47
2019-07-25 00:30 | 6.7 | 6.64
2019-07-25 01:00 | 6.31 | 6.24
2019-07-25 01:30 | 5.9 | 5.82
2019-07-25 02:00 | 5.68 | 5.59
2019-07-25 02:30 | 5.58 | 5.49
2019-07-25 03:00 | 5.49 | 5.41
2019-07-25 03:30 | 5.55 | 5.45
2019-07-25 04:00 | 5.71 | 5.63
2019-07-25 04:30 | 6.04 | 5.96
2019-07-25 05:00 | 6.55 | 6.49
2019-07-25 05:30 | 7.47 | 7.43
2019-07-25 06:00 | 8.34 | 8.31
2019-07-25 06:30 | 9.32 | 9.3
2019-07-25 07:00 | 10.74 | 10.72
2019-07-25 07:30 | 11.46 | 11.45
2019-07-25 08:00 | 10.48 | 10.47
2019-07-25 08:30 | 8.55 | 8.52
2019-07-25 09:00 | 6.84 | 6.8
2019-07-25 09:30 | 5.83 | 5.79
2019-07-25 10:00 | 4.88 | 4.83
2019-07-25 10:30 | 3.9 | 3.84
2019-07-25 11:00 | 3.54 | 3.48
2019-07-25 11:30 | 3.36 | 3.32
2019-07-25 12:00 | 3.99 | 3.96
2019-07-25 12:30 | 5.01 | 4.97
2019-07-25 13:00 | 4.13 | 4.1
2019-07-25 13:30 | 3.87 | 3.83
2019-07-25 14:00 | 6.18 | 6.15
2019-07-25 14:30 | 5.59 | 5.55
2019-07-25 15:00 | 4.7 | 4.66
2019-07-25 15:30 | 6.85 | 6.82
2019-07-25 16:00 | 6.73 | 6.69
2019-07-25 16:30 | 7.53 | 7.5
2019-07-25 17:00 | 9.36 | 9.34
2019-07-25 17:30 | 11.07 | 11.06
2019-07-25 18:00 | 12.58 | 12.58
2019-07-25 18:30 | 13.25 | 13.25
2019-07-25 19:00 | 13.6 | 13.6
2019-07-25 19:30 | 13.07 | 13.07
2019-07-25 20:00 | 13.09 | 13.09
2019-07-25 20:30 | 13.33 | 13.33
2019-07-25 21:00 | 12.57 | 12.56
2019-07-25 21:30 | 11.71 | 11.71
2019-07-25 22:00 | 10.7 | 10.68
2019-07-25 22:30 | 10.03 | 10.01
2019-07-25 23:00 | 9.61 | 9.59
2019-07-25 23:30 | 8.52 | 8.49
2019-07-26 | 7.49 | 7.44
2019-07-26 00:30 | 6.72 | 6.66
2019-07-26 01:00 | 6.32 | 6.25
2019-07-26 01:30 | 5.9 | 5.82
2019-07-26 02:00 | 5.58 | 5.49
2019-07-26 02:30 | 5.46 | 5.37
2019-07-26 03:00 | 5.26 | 5.16
2019-07-26 03:30 | 5.37 | 5.26
2019-07-26 04:00 | 5.43 | 5.33
2019-07-26 04:30 | 5.74 | 5.65
2019-07-26 05:00 | 6.19 | 6.12
2019-07-26 05:30 | 6.97 | 6.92
2019-07-26 06:00 | 7.84 | 7.8
2019-07-26 06:30 | 8.7 | 8.67
2019-07-26 07:00 | 9.78 | 9.75
2019-07-26 07:30 | 10.3 | 10.28
2019-07-26 08:00 | 9.24 | 9.22
2019-07-26 08:30 | 8.14 | 8.11
2019-07-26 09:00 | 6.87 | 6.83
2019-07-26 09:30 | 5.92 | 5.87
2019-07-26 10:00 | 4.53 | 4.48
2019-07-26 10:30 | 3.62 | 3.55
2019-07-26 11:00 | 3.78 | 3.71
2019-07-26 11:30 | 3.52 | 3.45
2019-07-26 12:00 | 3.78 | 3.71
2019-07-26 12:30 | 3.82 | 3.75
2019-07-26 13:00 | 3.35 | 3.27
2019-07-26 13:30 | 3.11 | 3.03
2019-07-26 14:00 | 3.22 | 3.14
2019-07-26 14:30 | 3.67 | 3.62
2019-07-26 15:00 | 5.69 | 5.64
2019-07-26 15:30 | 5.31 | 5.26
2019-07-26 16:00 | 5.88 | 5.83
2019-07-26 16:30 | 7.23 | 7.19
2019-07-26 17:00 | 8.74 | 8.71
2019-07-26 17:30 | 9.88 | 9.86
2019-07-26 18:00 | 11.04 | 11.03
2019-07-26 18:30 | 11.57 | 11.56
2019-07-26 19:00 | 11.93 | 11.93
2019-07-26 19:30 | 11.65 | 11.65
2019-07-26 20:00 | 11.74 | 11.74
2019-07-26 20:30 | 11.71 | 11.71
2019-07-26 21:00 | 11.37 | 11.36
2019-07-26 21:30 | 10.68 | 10.67
2019-07-26 22:00 | 10.13 | 10.12
2019-07-26 22:30 | 9.82 | 9.8
2019-07-26 23:00 | 9.54 | 9.52
2019-07-26 23:30 | 8.65 | 8.61
2019-07-27 | 7.75 | 7.7
2019-07-27 00:30 | 7.04 | 6.98
2019-07-27 01:00 | 6.48 | 6.41
2019-07-27 01:30 | 6.03 | 5.95
2019-07-27 02:00 | 5.72 | 5.63
2019-07-27 02:30 | 5.44 | 5.34
2019-07-27 03:00 | 5.25 | 5.14
2019-07-27 03:30 | 5.2 | 5.1
2019-07-27 04:00 | 5.14 | 5.03
2019-07-27 04:30 | 5.29 | 5.19
2019-07-27 05:00 | 5.4 | 5.3
2019-07-27 05:30 | 5.61 | 5.51
2019-07-27 06:00 | 5.91 | 5.82
2019-07-27 06:30 | 6.36 | 6.27
2019-07-27 07:00 | 6.93 | 6.83
2019-07-27 07:30 | 7.09 | 7
2019-07-27 08:00 | 7.06 | 6.98
2019-07-27 08:30 | 6.94 | 6.87
2019-07-27 09:00 | 6.59 | 6.53
2019-07-27 09:30 | 5.89 | 5.84
2019-07-27 10:00 | 5.17 | 5.11
2019-07-27 10:30 | 4.6 | 4.54
2019-07-27 11:00 | 4.09 | 4.03
2019-07-27 11:30 | 3.54 | 3.47
2019-07-27 12:00 | 3.43 | 3.36
2019-07-27 12:30 | 3.37 | 3.3
2019-07-27 13:00 | 3.77 | 3.73
2019-07-27 13:30 | 4.6 | 4.56
2019-07-27 14:00 | 4.46 | 4.42
2019-07-27 14:30 | 4.92 | 4.88
2019-07-27 15:00 | 5.85 | 5.81
2019-07-27 15:30 | 5.55 | 5.51
2019-07-27 16:00 | 6.42 | 6.38
2019-07-27 16:30 | 7.37 | 7.33
2019-07-27 17:00 | 8.49 | 8.45
2019-07-27 17:30 | 9.52 | 9.49
2019-07-27 18:00 | 10.55 | 10.55
2019-07-27 18:30 | 10.96 | 10.96
2019-07-27 19:00 | 11.08 | 11.07
2019-07-27 19:30 | 10.81 | 10.81
2019-07-27 20:00 | 10.8 | 10.79
2019-07-27 20:30 | 10.92 | 10.91
2019-07-27 21:00 | 10.44 | 10.43
2019-07-27 21:30 | 9.83 | 9.81
2019-07-27 22:00 | 9.34 | 9.31
2019-07-27 22:30 | 9.18 | 9.15
2019-07-27 23:00 | 9.01 | 8.97
2019-07-27 23:30 | 8.39 | 8.34
2019-07-28 | 7.43 | 7.37
2019-07-28 00:30 | 6.56 | 6.48
2019-07-28 01:00 | 6.17 | 6.09
2019-07-28 01:30 | 5.67 | 5.58
2019-07-28 02:00 | 5.38 | 5.28
2019-07-28 02:30 | 5.32 | 5.22
2019-07-28 03:00 | 5.14 | 5.03
2019-07-28 03:30 | 5.13 | 5.02
2019-07-28 04:00 | 5.03 | 4.91
2019-07-28 04:30 | 5.07 | 4.95
2019-07-28 05:00 | 5.02 | 4.91
2019-07-28 05:30 | 5.22 | 5.11
2019-07-28 06:00 | 5.56 | 5.47
2019-07-28 06:30 | 5.83 | 5.72
2019-07-28 07:00 | 6.21 | 6.07
2019-07-28 07:30 | 6.81 | 6.69
2019-07-28 08:00 | 7.36 | 7.26
2019-07-28 08:30 | 6.93 | 6.85
2019-07-28 09:00 | 6.91 | 6.84
2019-07-28 09:30 | 5.95 | 5.87
2019-07-28 10:00 | 5.55 | 5.49
2019-07-28 10:30 | 4.58 | 4.51
2019-07-28 11:00 | 4.25 | 4.18
2019-07-28 11:30 | 4.45 | 4.39
2019-07-28 12:00 | 5.35 | 5.3
2019-07-28 12:30 | 4.99 | 4.93
2019-07-28 13:00 | 5.61 | 5.56
2019-07-28 13:30 | 6.45 | 6.4
2019-07-28 14:00 | 6.1 | 6.05
2019-07-28 14:30 | 4.19 | 4.13
2019-07-28 15:00 | 5.06 | 5.01
2019-07-28 15:30 | 6.28 | 6.22
2019-07-28 16:00 | 7.55 | 7.5
2019-07-28 16:30 | 8.74 | 8.7
2019-07-28 17:00 | 9.72 | 9.68
2019-07-28 17:30 | 11.07 | 11.05
2019-07-28 18:00 | 12.41 | 12.41
2019-07-28 18:30 | 12.7 | 12.7
2019-07-28 19:00 | 12.54 | 12.53
2019-07-28 19:30 | 12.28 | 12.27
2019-07-28 20:00 | 12.14 | 12.13
2019-07-28 20:30 | 12.11 | 12.1
2019-07-28 21:00 | 11.47 | 11.46
2019-07-28 21:30 | 10.81 | 10.79
2019-07-28 22:00 | 10.18 | 10.16
2019-07-28 22:30 | 9.56 | 9.54
2019-07-28 23:00 | 8.99 | 8.95
2019-07-28 23:30 | 7.91 | 7.86
2019-07-29 | 7.36 | 7.29
2019-07-29 00:30 | 6.62 | 6.55
2019-07-29 01:00 | 5.98 | 5.9
2019-07-29 01:30 | 5.4 | 5.3
2019-07-29 02:00 | 5.11 | 5.01
2019-07-29 02:30 | 4.99 | 4.88
2019-07-29 03:00 | 4.94 | 4.83
2019-07-29 03:30 | 4.99 | 4.87
2019-07-29 04:00 | 5.04 | 4.93
2019-07-29 04:30 | 5.23 | 5.12
2019-07-29 05:00 | 5.62 | 5.52
2019-07-29 05:30 | 6.08 | 6
2019-07-29 06:00 | 6.78 | 6.72
2019-07-29 06:30 | 7.91 | 7.88
2019-07-29 07:00 | 8.93 | 8.89
2019-07-29 07:30 | 9.25 | 9.22
2019-07-29 08:00 | 8.33 | 8.28
2019-07-29 08:30 | 6.75 | 6.69
2019-07-29 09:00 | 5.63 | 5.56
2019-07-29 09:30 | 4.83 | 4.76
2019-07-29 10:00 | 4.19 | 4.12
2019-07-29 10:30 | 3.49 | 3.41
2019-07-29 11:00 | 3.35 | 3.28
2019-07-29 11:30 | 3.23 | 3.16
2019-07-29 12:00 | 2.94 | 2.86
2019-07-29 12:30 | 2.84 | 2.77
2019-07-29 13:00 | 3.1 | 3.06
2019-07-29 13:30 | 3.21 | 3.16
2019-07-29 14:00 | 3.4 | 3.35
2019-07-29 14:30 | 4.78 | 4.73
2019-07-29 15:00 | 6.15 | 6.11
2019-07-29 15:30 | 7.08 | 7.04
2019-07-29 16:00 | 7.22 | 7.17
2019-07-29 16:30 | 7.73 | 7.68
2019-07-29 17:00 | 9.26 | 9.23
2019-07-29 17:30 | 10.86 | 10.84
2019-07-29 18:00 | 12.29 | 12.28
2019-07-29 18:30 | 12.87 | 12.87
2019-07-29 19:00 | 13.23 | 13.23
2019-07-29 19:30 | 12.76 | 12.76
2019-07-29 20:00 | 12.52 | 12.52
2019-07-29 20:30 | 12.29 | 12.29
2019-07-29 21:00 | 11.9 | 11.9
2019-07-29 21:30 | 11.15 | 11.14
2019-07-29 22:00 | 10.09 | 10.07
2019-07-29 22:30 | 9.24 | 9.21
2019-07-29 23:00 | 8.67 | 8.63
2019-07-29 23:30 | 7.77 | 7.71
2019-07-30 | 6.96 | 6.9
2019-07-30 00:30 | 6.23 | 6.15
2019-07-30 01:00 | 5.73 | 5.63
2019-07-30 01:30 | 5.51 | 5.42
2019-07-30 02:00 | 5.17 | 5.06
2019-07-30 02:30 | 5.03 | 4.93
2019-07-30 03:00 | 4.92 | 4.8
2019-07-30 03:30 | 4.99 | 4.88
2019-07-30 04:00 | 5.16 | 5.05
2019-07-30 04:30 | 5.48 | 5.37
2019-07-30 05:00 | 5.86 | 5.77
2019-07-30 05:30 | 6.67 | 6.6
2019-07-30 06:00 | 7.3 | 7.24
2019-07-30 06:30 | 8.31 | 8.27
2019-07-30 07:00 | 9.4 | 9.36
2019-07-30 07:30 | 9.67 | 9.63
2019-07-30 08:00 | 8.83 | 8.79
2019-07-30 08:30 | 7.66 | 7.6
2019-07-30 09:00 | 6.35 | 6.29
2019-07-30 09:30 | 5.21 | 5.14
2019-07-30 10:00 | 4.21 | 4.12
2019-07-30 10:30 | 3.6 | 3.5
2019-07-30 11:00 | 2.92 | 2.81
2019-07-30 11:30 | 2.23 | 2.11
2019-07-30 12:00 | 2.13 | 2.01
2019-07-30 12:30 | 2.15 | 2.04
2019-07-30 13:00 | 2.32 | 2.24
2019-07-30 13:30 | 2.51 | 2.45
2019-07-30 14:00 | 3.21 | 3.16
2019-07-30 14:30 | 3.52 | 3.48
2019-07-30 15:00 | 4.23 | 4.2
2019-07-30 15:30 | 5.07 | 5.04
2019-07-30 16:00 | 7.36 | 7.34
2019-07-30 16:30 | 8.77 | 8.75
2019-07-30 17:00 | 10.2 | 10.19
2019-07-30 17:30 | 11.45 | 11.45
2019-07-30 18:00 | 12.69 | 12.69
2019-07-30 18:30 | 12.99 | 12.99
2019-07-30 19:00 | 13.22 | 13.22
2019-07-30 19:30 | 12.8 | 12.8
2019-07-30 20:00 | 12.85 | 12.85
2019-07-30 20:30 | 12.75 | 12.74
2019-07-30 21:00 | 12.12 | 12.12
2019-07-30 21:30 | 11.22 | 11.22
2019-07-30 22:00 | 10.2 | 10.18
2019-07-30 22:30 | 9.33 | 9.3
2019-07-30 23:00 | 8.74 | 8.7
2019-07-30 23:30 | 7.83 | 7.78
2019-07-31 | 6.91 | 6.84
2019-07-31 00:30 | 6.11 | 6.04
2019-07-31 01:00 | 5.76 | 5.67
2019-07-31 01:30 | 5.46 | 5.37
2019-07-31 02:00 | 5.26 | 5.16
2019-07-31 02:30 | 5.12 | 5.02
2019-07-31 03:00 | 5.02 | 4.91
2019-07-31 03:30 | 5.06 | 4.96
2019-07-31 04:00 | 5.15 | 5.04
2019-07-31 04:30 | 5.42 | 5.32
2019-07-31 05:00 | 5.93 | 5.84
2019-07-31 05:30 | 6.62 | 6.56
2019-07-31 06:00 | 7.39 | 7.34
2019-07-31 06:30 | 8.53 | 8.5
2019-07-31 07:00 | 9.51 | 9.48
2019-07-31 07:30 | 9.82 | 9.79
2019-07-31 08:00 | 8.76 | 8.72
2019-07-31 08:30 | 7.11 | 7.06
2019-07-31 09:00 | 5.59 | 5.52
2019-07-31 09:30 | 4.6 | 4.53
2019-07-31 10:00 | 3.73 | 3.65
2019-07-31 10:30 | 3.12 | 3.03
2019-07-31 11:00 | 2.66 | 2.57
2019-07-31 11:30 | 2.35 | 2.24
2019-07-31 12:00 | 2.23 | 2.14
2019-07-31 12:30 | 2.54 | 2.45
2019-07-31 13:00 | 3.61 | 3.55
2019-07-31 13:30 | 3.68 | 3.62
2019-07-31 14:00 | 4.1 | 4.03
2019-07-31 14:30 | 3.5 | 3.44
2019-07-31 15:00 | 5.37 | 5.31
2019-07-31 15:30 | 4.96 | 4.89
2019-07-31 16:00 | 6.56 | 6.5
2019-07-31 16:30 | 8.1 | 8.05
2019-07-31 17:00 | 9.54 | 9.5
2019-07-31 17:30 | 10.79 | 10.76
2019-07-31 18:00 | 12.13 | 12.13
2019-07-31 18:30 | 12.94 | 12.94
2019-07-31 19:00 | 13.37 | 13.37
2019-07-31 19:30 | 13.05 | 13.05
2019-07-31 20:00 | 13.14 | 13.14
2019-07-31 20:30 | 13.1 | 13.1
2019-07-31 21:00 | 12.59 | 12.59
2019-07-31 21:30 | 11.65 | 11.64
2019-07-31 22:00 | 10.62 | 10.6
2019-07-31 22:30 | 9.84 | 9.82
2019-07-31 23:00 | 9.34 | 9.32
2019-07-31 23:30 | 8.41 | 8.37
2019-08-01 | 7.37 | 7.32
2019-08-01 00:30 | 6.66 | 6.59
2019-08-01 01:00 | 6.28 | 6.21
2019-08-01 01:30 | 5.91 | 5.82
2019-08-01 02:00 | 5.54 | 5.45
2019-08-01 02:30 | 5.39 | 5.29
2019-08-01 03:00 | 5.32 | 5.22
2019-08-01 03:30 | 5.25 | 5.15
2019-08-01 04:00 | 5.35 | 5.25
2019-08-01 04:30 | 5.56 | 5.47
2019-08-01 05:00 | 6.06 | 5.98
2019-08-01 05:30 | 6.74 | 6.67
2019-08-01 06:00 | 7.9 | 7.86
2019-08-01 06:30 | 9.02 | 8.99
2019-08-01 07:00 | 9.8 | 9.77
2019-08-01 07:30 | 10.24 | 10.21
2019-08-01 08:00 | 9.59 | 9.56
2019-08-01 08:30 | 8 | 7.95
2019-08-01 09:00 | 6.45 | 6.41
2019-08-01 09:30 | 5.78 | 5.73
2019-08-01 10:00 | 5.51 | 5.46
2019-08-01 10:30 | 5.79 | 5.74
2019-08-01 11:00 | 4.03 | 3.97
2019-08-01 11:30 | 4.3 | 4.24
2019-08-01 12:00 | 5.99 | 5.94
2019-08-01 12:30 | 5.15 | 5.1
2019-08-01 13:00 | 4.67 | 4.61
2019-08-01 13:30 | 4.54 | 4.46
2019-08-01 14:00 | 4.55 | 4.46
2019-08-01 14:30 | 5.01 | 4.93
2019-08-01 15:00 | 4.09 | 4
2019-08-01 15:30 | 6.68 | 6.61
2019-08-01 16:00 | 7.37 | 7.31
2019-08-01 16:30 | 8.5 | 8.45
2019-08-01 17:00 | 9.79 | 9.76
2019-08-01 17:30 | 10.94 | 10.92
2019-08-01 18:00 | 12.11 | 12.11
2019-08-01 18:30 | 12.77 | 12.76
2019-08-01 19:00 | 13.28 | 13.28
2019-08-01 19:30 | 13.07 | 13.07
2019-08-01 20:00 | 13.07 | 13.07
2019-08-01 20:30 | 13.21 | 13.21
2019-08-01 21:00 | 12.76 | 12.75
2019-08-01 21:30 | 12.06 | 12.06
2019-08-01 22:00 | 11.03 | 11.01
2019-08-01 22:30 | 10.35 | 10.33
2019-08-01 23:00 | 9.75 | 9.72
2019-08-01 23:30 | 8.69 | 8.65
2019-08-02 | 7.64 | 7.59
2019-08-02 00:30 | 6.76 | 6.69
2019-08-02 01:00 | 6.4 | 6.33
2019-08-02 01:30 | 6.06 | 5.98
2019-08-02 02:00 | 5.74 | 5.66
2019-08-02 02:30 | 5.58 | 5.49
2019-08-02 03:00 | 5.57 | 5.48
2019-08-02 03:30 | 5.59 | 5.5
2019-08-02 04:00 | 5.65 | 5.56
2019-08-02 04:30 | 5.94 | 5.86
2019-08-02 05:00 | 6.54 | 6.47
2019-08-02 05:30 | 7.32 | 7.27
2019-08-02 06:00 | 8.23 | 8.2
2019-08-02 06:30 | 9.49 | 9.47
2019-08-02 07:00 | 10.37 | 10.35
2019-08-02 07:30 | 10.85 | 10.83
2019-08-02 08:00 | 9.75 | 9.73
2019-08-02 08:30 | 8.08 | 8.05
2019-08-02 09:00 | 6.48 | 6.44
2019-08-02 09:30 | 5.29 | 5.24
2019-08-02 10:00 | 4.41 | 4.35
2019-08-02 10:30 | 3.54 | 3.47
2019-08-02 11:00 | 2.72 | 2.6
2019-08-02 11:30 | 2.41 | 2.28
2019-08-02 12:00 | 3.17 | 3.09
2019-08-02 12:30 | 4.4 | 4.34
2019-08-02 13:00 | 5.82 | 5.76
2019-08-02 13:30 | 4.86 | 4.8
2019-08-02 14:00 | 3.09 | 3
2019-08-02 14:30 | 3.77 | 3.7
2019-08-02 15:00 | 4.37 | 4.3
2019-08-02 15:30 | 6.48 | 6.43
2019-08-02 16:00 | 5.95 | 5.89
2019-08-02 16:30 | 8.04 | 7.99
2019-08-02 17:00 | 9.4 | 9.37
2019-08-02 17:30 | 10.31 | 10.29
2019-08-02 18:00 | 11.48 | 11.48
2019-08-02 18:30 | 12.15 | 12.15
2019-08-02 19:00 | 12.5 | 12.5
2019-08-02 19:30 | 12.21 | 12.21
2019-08-02 20:00 | 12.33 | 12.33
2019-08-02 20:30 | 12.4 | 12.39
2019-08-02 21:00 | 11.93 | 11.93
2019-08-02 21:30 | 11.48 | 11.48
2019-08-02 22:00 | 10.87 | 10.86
2019-08-02 22:30 | 10.59 | 10.58
2019-08-02 23:00 | 10.4 | 10.38
2019-08-02 23:30 | 9.41 | 9.38
2019-08-03 | 8.37 | 8.32
2019-08-03 00:30 | 7.58 | 7.53
2019-08-03 01:00 | 7.09 | 7.03
2019-08-03 01:30 | 6.68 | 6.61
2019-08-03 02:00 | 6.22 | 6.14
2019-08-03 02:30 | 6.01 | 5.93
2019-08-03 03:00 | 5.78 | 5.69
2019-08-03 03:30 | 5.77 | 5.68
2019-08-03 04:00 | 5.71 | 5.62
2019-08-03 04:30 | 5.8 | 5.71
2019-08-03 05:00 | 5.97 | 5.88
2019-08-03 05:30 | 6.29 | 6.22
2019-08-03 06:00 | 6.67 | 6.61
2019-08-03 06:30 | 7.11 | 7.04
2019-08-03 07:00 | 7.74 | 7.66
2019-08-03 07:30 | 8.21 | 8.15
2019-08-03 08:00 | 8.27 | 8.22
2019-08-03 08:30 | 7.9 | 7.86
2019-08-03 09:00 | 7.28 | 7.24
2019-08-03 09:30 | 6.44 | 6.4
2019-08-03 10:00 | 5.56 | 5.51
2019-08-03 10:30 | 4.6 | 4.54
2019-08-03 11:00 | 4.09 | 4.02
2019-08-03 11:30 | 3.63 | 3.55
2019-08-03 12:00 | 3.57 | 3.51
2019-08-03 12:30 | 4.41 | 4.36
2019-08-03 13:00 | 5.26 | 5.21
2019-08-03 13:30 | 4 | 3.95
2019-08-03 14:00 | 4.25 | 4.2
2019-08-03 14:30 | 5.08 | 5.03
2019-08-03 15:00 | 5.6 | 5.54
2019-08-03 15:30 | 5.49 | 5.43
2019-08-03 16:00 | 6.72 | 6.67
2019-08-03 16:30 | 7.38 | 7.33
2019-08-03 17:00 | 8.52 | 8.47
2019-08-03 17:30 | 9.72 | 9.68
2019-08-03 18:00 | 10.94 | 10.93
2019-08-03 18:30 | 11.38 | 11.37
2019-08-03 19:00 | 11.57 | 11.56
2019-08-03 19:30 | 11.36 | 11.35
2019-08-03 20:00 | 11.41 | 11.4
2019-08-03 20:30 | 11.38 | 11.37
2019-08-03 21:00 | 10.93 | 10.92
2019-08-03 21:30 | 10.43 | 10.41
2019-08-03 22:00 | 10.01 | 9.99
2019-08-03 22:30 | 9.87 | 9.84
2019-08-03 23:00 | 9.74 | 9.71
2019-08-03 23:30 | 8.83 | 8.8
2019-08-04 | 7.94 | 7.89
2019-08-04 00:30 | 7.13 | 7.07
2019-08-04 01:00 | 6.72 | 6.66
2019-08-04 01:30 | 6.29 | 6.22
2019-08-04 02:00 | 5.93 | 5.84
2019-08-04 02:30 | 5.72 | 5.63
2019-08-04 03:00 | 5.59 | 5.5
2019-08-04 03:30 | 5.58 | 5.48
2019-08-04 04:00 | 5.49 | 5.39
2019-08-04 04:30 | 5.55 | 5.44
2019-08-04 05:00 | 5.69 | 5.59
2019-08-04 05:30 | 5.9 | 5.81
2019-08-04 06:00 | 6.22 | 6.14
2019-08-04 06:30 | 6.56 | 6.47
2019-08-04 07:00 | 7.08 | 6.97
2019-08-04 07:30 | 7.52 | 7.43
2019-08-04 08:00 | 7.58 | 7.51
2019-08-04 08:30 | 7.51 | 7.46
2019-08-04 09:00 | 7 | 6.94
2019-08-04 09:30 | 6.38 | 6.32
2019-08-04 10:00 | 5.57 | 5.52
2019-08-04 10:30 | 5.06 | 5
2019-08-04 11:00 | 4.36 | 4.29
2019-08-04 11:30 | 3.88 | 3.81
2019-08-04 12:00 | 3.53 | 3.45
2019-08-04 12:30 | 3.31 | 3.24
2019-08-04 13:00 | 3.31 | 3.24
2019-08-04 13:30 | 3.52 | 3.45
2019-08-04 14:00 | 3.86 | 3.78
2019-08-04 14:30 | 4.2 | 4.12
2019-08-04 15:00 | 4.85 | 4.78
2019-08-04 15:30 | 5.73 | 5.67
2019-08-04 16:00 | 6.56 | 6.51
2019-08-04 16:30 | 7.86 | 7.81
2019-08-04 17:00 | 9.44 | 9.4
2019-08-04 17:30 | 10.75 | 10.72
2019-08-04 18:00 | 12.08 | 12.07
2019-08-04 18:30 | 12.63 | 12.63
2019-08-04 19:00 | 12.57 | 12.57
2019-08-04 19:30 | 12.23 | 12.23
2019-08-04 20:00 | 12.11 | 12.1
2019-08-04 20:30 | 12.23 | 12.22
2019-08-04 21:00 | 11.68 | 11.67
2019-08-04 21:30 | 10.89 | 10.87
2019-08-04 22:00 | 10.08 | 10.06
2019-08-04 22:30 | 9.6 | 9.57
2019-08-04 23:00 | 9.17 | 9.14
2019-08-04 23:30 | 8.24 | 8.2
2019-08-05 | 7.28 | 7.22
2019-08-05 00:30 | 6.52 | 6.44
2019-08-05 01:00 | 6.02 | 5.93
2019-08-05 01:30 | 5.65 | 5.55
2019-08-05 02:00 | 5.43 | 5.34
2019-08-05 02:30 | 5.25 | 5.14
2019-08-05 03:00 | 5.14 | 5.03
2019-08-05 03:30 | 5.17 | 5.05
2019-08-05 04:00 | 5.34 | 5.23
2019-08-05 04:30 | 5.72 | 5.62
2019-08-05 05:00 | 6.14 | 6.06
2019-08-05 05:30 | 6.91 | 6.85
2019-08-05 06:00 | 7.73 | 7.69
2019-08-05 06:30 | 8.72 | 8.69
2019-08-05 07:00 | 10.21 | 10.18
2019-08-05 07:30 | 10.36 | 10.34
2019-08-05 08:00 | 9.7 | 9.68
2019-08-05 08:30 | 9.22 | 9.19
2019-08-05 09:00 | 7.31 | 7.25
2019-08-05 09:30 | 5.76 | 5.7
2019-08-05 10:00 | 4.61 | 4.56
2019-08-05 10:30 | 3.79 | 3.73
2019-08-05 11:00 | 3.43 | 3.37
2019-08-05 11:30 | 3.45 | 3.39
2019-08-05 12:00 | 3.23 | 3.17
2019-08-05 12:30 | 3.52 | 3.46
2019-08-05 13:00 | 3.13 | 3.07
2019-08-05 13:30 | 3.27 | 3.2
2019-08-05 14:00 | 3.57 | 3.5
2019-08-05 14:30 | 4.64 | 4.6
2019-08-05 15:00 | 4.28 | 4.24
2019-08-05 15:30 | 5.33 | 5.29
2019-08-05 16:00 | 6.35 | 6.31
2019-08-05 16:30 | 7.76 | 7.73
2019-08-05 17:00 | 9.58 | 9.56
2019-08-05 17:30 | 11.15 | 11.13
2019-08-05 18:00 | 12.99 | 12.98
2019-08-05 18:30 | 13.71 | 13.71
2019-08-05 19:00 | 13.97 | 13.97
2019-08-05 19:30 | 13.53 | 13.53
2019-08-05 20:00 | 13.42 | 13.42
2019-08-05 20:30 | 13.6 | 13.6
2019-08-05 21:00 | 13.15 | 13.15
2019-08-05 21:30 | 12.08 | 12.07
2019-08-05 22:00 | 11.01 | 11
2019-08-05 22:30 | 10.19 | 10.17
2019-08-05 23:00 | 9.45 | 9.42
2019-08-05 23:30 | 8.44 | 8.4
2019-08-06 | 7.52 | 7.46
2019-08-06 00:30 | 6.76 | 6.69
2019-08-06 01:00 | 6.33 | 6.25
2019-08-06 01:30 | 5.94 | 5.85
2019-08-06 02:00 | 5.69 | 5.6
2019-08-06 02:30 | 5.6 | 5.51
2019-08-06 03:00 | 5.45 | 5.34
2019-08-06 03:30 | 5.48 | 5.38
2019-08-06 04:00 | 5.59 | 5.5
2019-08-06 04:30 | 5.95 | 5.86
2019-08-06 05:00 | 6.54 | 6.46
2019-08-06 05:30 | 7.28 | 7.23
2019-08-06 06:00 | 8.26 | 8.23
2019-08-06 06:30 | 9.67 | 9.65
2019-08-06 07:00 | 10.72 | 10.7
2019-08-06 07:30 | 10.82 | 10.81
2019-08-06 08:00 | 9.77 | 9.75
2019-08-06 08:30 | 8.05 | 8.02
2019-08-06 09:00 | 6.25 | 6.2
2019-08-06 09:30 | 5.02 | 4.97
2019-08-06 10:00 | 4.14 | 4.08
2019-08-06 10:30 | 3.44 | 3.37
2019-08-06 11:00 | 2.97 | 2.89
2019-08-06 11:30 | 2.69 | 2.61
2019-08-06 12:00 | 2.6 | 2.52
2019-08-06 12:30 | 2.39 | 2.3
2019-08-06 13:00 | 2.55 | 2.47
2019-08-06 13:30 | 2.72 | 2.67
2019-08-06 14:00 | 3.13 | 3.09
2019-08-06 14:30 | 3.92 | 3.89
2019-08-06 15:00 | 4.26 | 4.22
2019-08-06 15:30 | 5.38 | 5.34
2019-08-06 16:00 | 6.57 | 6.54
2019-08-06 16:30 | 7.74 | 7.71
2019-08-06 17:00 | 9.39 | 9.37
2019-08-06 17:30 | 11.06 | 11.05
2019-08-06 18:00 | 12.51 | 12.51
2019-08-06 18:30 | 13.54 | 13.54
2019-08-06 19:00 | 13.81 | 13.81
2019-08-06 19:30 | 13.36 | 13.36
2019-08-06 20:00 | 13.51 | 13.51
2019-08-06 20:30 | 13.4 | 13.4
2019-08-06 21:00 | 12.63 | 12.63
2019-08-06 21:30 | 11.58 | 11.57
2019-08-06 22:00 | 10.42 | 10.4
2019-08-06 22:30 | 9.73 | 9.71
2019-08-06 23:00 | 9.49 | 9.47
2019-08-06 23:30 | 8.4 | 8.36
2019-08-07 | 7.38 | 7.32
2019-08-07 00:30 | 6.6 | 6.53
2019-08-07 01:00 | 6.13 | 6.05
2019-08-07 01:30 | 5.81 | 5.72
2019-08-07 02:00 | 5.42 | 5.33
2019-08-07 02:30 | 5.4 | 5.3
2019-08-07 03:00 | 5.19 | 5.1
2019-08-07 03:30 | 5.21 | 5.11
2019-08-07 04:00 | 5.29 | 5.19
2019-08-07 04:30 | 5.65 | 5.56
2019-08-07 05:00 | 5.97 | 5.89
2019-08-07 05:30 | 6.71 | 6.65
2019-08-07 06:00 | 7.38 | 7.34
2019-08-07 06:30 | 8.3 | 8.27
2019-08-07 07:00 | 9.24 | 9.21
2019-08-07 07:30 | 10 | 9.97
2019-08-07 08:00 | 9.91 | 9.89
2019-08-07 08:30 | 9.11 | 9.08
2019-08-07 09:00 | 8.41 | 8.38
2019-08-07 09:30 | 8.05 | 8.02
2019-08-07 10:00 | 7.41 | 7.37
2019-08-07 10:30 | 6.07 | 6.01
2019-08-07 11:00 | 5.01 | 4.95
2019-08-07 11:30 | 4.31 | 4.24
2019-08-07 12:00 | 4.03 | 3.96
2019-08-07 12:30 | 3.93 | 3.86
2019-08-07 13:00 | 4.14 | 4.07
2019-08-07 13:30 | 5.57 | 5.51
2019-08-07 14:00 | 6.36 | 6.31
2019-08-07 14:30 | 6.87 | 6.83
2019-08-07 15:00 | 7.17 | 7.13
2019-08-07 15:30 | 8.02 | 7.98
2019-08-07 16:00 | 8.58 | 8.54
2019-08-07 16:30 | 9.36 | 9.33
2019-08-07 17:00 | 10.61 | 10.59
2019-08-07 17:30 | 11.61 | 11.6
2019-08-07 18:00 | 12.6 | 12.6
2019-08-07 18:30 | 13.22 | 13.22
2019-08-07 19:00 | 13.49 | 13.49
2019-08-07 19:30 | 13.21 | 13.21
2019-08-07 20:00 | 13.09 | 13.08
2019-08-07 20:30 | 13.14 | 13.14
2019-08-07 21:00 | 12.69 | 12.69
2019-08-07 21:30 | 11.53 | 11.52
2019-08-07 22:00 | 10.45 | 10.43
2019-08-07 22:30 | 9.74 | 9.71
2019-08-07 23:00 | 9.16 | 9.13
2019-08-07 23:30 | 8.15 | 8.11
2019-08-08 | 7.25 | 7.19
2019-08-08 00:30 | 6.45 | 6.38
2019-08-08 01:00 | 6.06 | 5.98
2019-08-08 01:30 | 5.58 | 5.5
2019-08-08 02:00 | 5.32 | 5.23
2019-08-08 02:30 | 5.23 | 5.14
2019-08-08 03:00 | 5.02 | 4.92
2019-08-08 03:30 | 5 | 4.91
2019-08-08 04:00 | 5.11 | 5.01
2019-08-08 04:30 | 5.37 | 5.28
2019-08-08 05:00 | 5.74 | 5.65
2019-08-08 05:30 | 6.42 | 6.35
2019-08-08 06:00 | 7.14 | 7.1
2019-08-08 06:30 | 7.88 | 7.83
2019-08-08 07:00 | 8.83 | 8.78
2019-08-08 07:30 | 9.41 | 9.37
2019-08-08 08:00 | 8.75 | 8.71
2019-08-08 08:30 | 8.36 | 8.31
2019-08-08 09:00 | 8.17 | 8.13
2019-08-08 09:30 | 7.5 | 7.46
2019-08-08 10:00 | 5.87 | 5.82
2019-08-08 10:30 | 3.67 | 3.62
2019-08-08 11:00 | 2.99 | 2.93
2019-08-08 11:30 | 2.65 | 2.6
2019-08-08 12:00 | 2.41 | 2.35
2019-08-08 12:30 | 2.48 | 2.43
2019-08-08 13:00 | 2.85 | 2.82
2019-08-08 13:30 | 3.51 | 3.48
2019-08-08 14:00 | 2.94 | 2.9
2019-08-08 14:30 | 3.46 | 3.43
2019-08-08 15:00 | 4.16 | 4.13
2019-08-08 15:30 | 5.38 | 5.36
2019-08-08 16:00 | 6.89 | 6.87
2019-08-08 16:30 | 8.34 | 8.32
2019-08-08 17:00 | 9.4 | 9.38
2019-08-08 17:30 | 10.44 | 10.43
2019-08-08 18:00 | 11.77 | 11.77
2019-08-08 18:30 | 12.36 | 12.36
2019-08-08 19:00 | 12.59 | 12.59
2019-08-08 19:30 | 12.33 | 12.33
2019-08-08 20:00 | 12.44 | 12.44
2019-08-08 20:30 | 12.33 | 12.33
2019-08-08 21:00 | 11.68 | 11.68
2019-08-08 21:30 | 10.9 | 10.89
2019-08-08 22:00 | 9.95 | 9.94
2019-08-08 22:30 | 9.44 | 9.42
2019-08-08 23:00 | 8.61 | 8.58
2019-08-08 23:30 | 7.59 | 7.54
2019-08-09 | 6.74 | 6.68
2019-08-09 00:30 | 5.95 | 5.88
2019-08-09 01:00 | 5.65 | 5.57
2019-08-09 01:30 | 5.42 | 5.33
2019-08-09 02:00 | 5.11 | 5.01
2019-08-09 02:30 | 4.93 | 4.83
2019-08-09 03:00 | 4.87 | 4.76
2019-08-09 03:30 | 4.89 | 4.78
2019-08-09 04:00 | 4.91 | 4.8
2019-08-09 04:30 | 5.18 | 5.07
2019-08-09 05:00 | 5.55 | 5.46
2019-08-09 05:30 | 6.27 | 6.2
2019-08-09 06:00 | 7.29 | 7.24
2019-08-09 06:30 | 8.25 | 8.21
2019-08-09 07:00 | 8.97 | 8.92
2019-08-09 07:30 | 9.11 | 9.07
2019-08-09 08:00 | 8.17 | 8.13
2019-08-09 08:30 | 7.67 | 7.62
2019-08-09 09:00 | 6.29 | 6.22
2019-08-09 09:30 | 5.27 | 5.2
2019-08-09 10:00 | 3.68 | 3.62
2019-08-09 10:30 | 2.62 | 2.52
2019-08-09 11:00 | 2.01 | 1.89
2019-08-09 11:30 | 1.74 | 1.62
2019-08-09 12:00 | 1.65 | 1.53
2019-08-09 12:30 | 1.5 | 1.36
2019-08-09 13:00 | 1.57 | 1.44
2019-08-09 13:30 | 1.76 | 1.66
2019-08-09 14:00 | 2.2 | 2.11
2019-08-09 14:30 | 2.7 | 2.61
2019-08-09 15:00 | 3.22 | 3.14
2019-08-09 15:30 | 4.32 | 4.26
2019-08-09 16:00 | 5.48 | 5.43
2019-08-09 16:30 | 6.81 | 6.78
2019-08-09 17:00 | 8.29 | 8.25
2019-08-09 17:30 | 9.32 | 9.29
2019-08-09 18:00 | 10.59 | 10.58
2019-08-09 18:30 | 11.33 | 11.32
2019-08-09 19:00 | 11.52 | 11.51
2019-08-09 19:30 | 11.25 | 11.24
2019-08-09 20:00 | 11.34 | 11.33
2019-08-09 20:30 | 11.57 | 11.56
2019-08-09 21:00 | 11.35 | 11.34
2019-08-09 21:30 | 10.77 | 10.76
2019-08-09 22:00 | 10.18 | 10.16
2019-08-09 22:30 | 9.82 | 9.8
2019-08-09 23:00 | 9.52 | 9.49
2019-08-09 23:30 | 8.62 | 8.58
2019-08-10 | 7.71 | 7.67
2019-08-10 00:30 | 6.93 | 6.87
2019-08-10 01:00 | 6.47 | 6.4
2019-08-10 01:30 | 6.05 | 5.97
2019-08-10 02:00 | 5.66 | 5.57
2019-08-10 02:30 | 5.45 | 5.36
2019-08-10 03:00 | 5.24 | 5.14
2019-08-10 03:30 | 5.19 | 5.09
2019-08-10 04:00 | 5.13 | 5.02
2019-08-10 04:30 | 5.21 | 5.11
2019-08-10 05:00 | 5.41 | 5.32
2019-08-10 05:30 | 5.56 | 5.47
2019-08-10 06:00 | 5.88 | 5.8
2019-08-10 06:30 | 6.23 | 6.14
2019-08-10 07:00 | 6.64 | 6.53
2019-08-10 07:30 | 6.87 | 6.77
2019-08-10 08:00 | 6.81 | 6.73
2019-08-10 08:30 | 6.41 | 6.33
2019-08-10 09:00 | 5.98 | 5.92
2019-08-10 09:30 | 5.38 | 5.33
2019-08-10 10:00 | 4.64 | 4.59
2019-08-10 10:30 | 4.06 | 4
2019-08-10 11:00 | 3.65 | 3.59
2019-08-10 11:30 | 3.21 | 3.14
2019-08-10 12:00 | 3.06 | 2.99
2019-08-10 12:30 | 2.91 | 2.82
2019-08-10 13:00 | 2.87 | 2.79
2019-08-10 13:30 | 3.09 | 3.01
2019-08-10 14:00 | 3.56 | 3.48
2019-08-10 14:30 | 3.74 | 3.66
2019-08-10 15:00 | 4.26 | 4.19
2019-08-10 15:30 | 5.29 | 5.23
2019-08-10 16:00 | 6.31 | 6.26
2019-08-10 16:30 | 7.39 | 7.34
2019-08-10 17:00 | 8.67 | 8.63
2019-08-10 17:30 | 9.77 | 9.73
2019-08-10 18:00 | 10.77 | 10.76
2019-08-10 18:30 | 11.49 | 11.49
2019-08-10 19:00 | 11.78 | 11.78
2019-08-10 19:30 | 11.5 | 11.5
2019-08-10 20:00 | 11.54 | 11.53
2019-08-10 20:30 | 11.66 | 11.65
2019-08-10 21:00 | 11.13 | 11.12
2019-08-10 21:30 | 10.71 | 10.7
2019-08-10 22:00 | 10.14 | 10.12
2019-08-10 22:30 | 9.84 | 9.81
2019-08-10 23:00 | 9.57 | 9.54
2019-08-10 23:30 | 8.93 | 8.89
2019-08-11 | 8.11 | 8.06
2019-08-11 00:30 | 7.37 | 7.31
2019-08-11 01:00 | 6.83 | 6.76
2019-08-11 01:30 | 6.36 | 6.28
2019-08-11 02:00 | 6.08 | 5.99
2019-08-11 02:30 | 5.69 | 5.6
2019-08-11 03:00 | 5.53 | 5.43
2019-08-11 03:30 | 5.42 | 5.32
2019-08-11 04:00 | 5.5 | 5.4
2019-08-11 04:30 | 5.49 | 5.39
2019-08-11 05:00 | 5.55 | 5.46
2019-08-11 05:30 | 5.85 | 5.76
2019-08-11 06:00 | 6.08 | 6
2019-08-11 06:30 | 6.31 | 6.2
2019-08-11 07:00 | 6.93 | 6.81
2019-08-11 07:30 | 7.03 | 6.93
2019-08-11 08:00 | 7.04 | 6.96
2019-08-11 08:30 | 6.98 | 6.91
2019-08-11 09:00 | 6.54 | 6.49
2019-08-11 09:30 | 6.06 | 6.01
2019-08-11 10:00 | 5.46 | 5.41
2019-08-11 10:30 | 4.93 | 4.88
2019-08-11 11:00 | 4.35 | 4.28
2019-08-11 11:30 | 3.98 | 3.91
2019-08-11 12:00 | 3.74 | 3.67
2019-08-11 12:30 | 3.65 | 3.59
2019-08-11 13:00 | 3.46 | 3.37
2019-08-11 13:30 | 3.74 | 3.66
2019-08-11 14:00 | 4.03 | 3.95
2019-08-11 14:30 | 4.32 | 4.23
2019-08-11 15:00 | 4.88 | 4.79
2019-08-11 15:30 | 5.78 | 5.71
2019-08-11 16:00 | 6.94 | 6.89
2019-08-11 16:30 | 8.33 | 8.29
2019-08-11 17:00 | 10.01 | 9.97
2019-08-11 17:30 | 11.71 | 11.68
2019-08-11 18:00 | 13.08 | 13.08
2019-08-11 18:30 | 13.82 | 13.82
2019-08-11 19:00 | 14.06 | 14.06
2019-08-11 19:30 | 13.84 | 13.84
2019-08-11 20:00 | 13.71 | 13.71
2019-08-11 20:30 | 13.55 | 13.55
2019-08-11 21:00 | 13.09 | 13.09
2019-08-11 21:30 | 12.44 | 12.43
2019-08-11 22:00 | 11.52 | 11.51
2019-08-11 22:30 | 10.51 | 10.49
2019-08-11 23:00 | 9.96 | 9.94
2019-08-11 23:30 | 8.96 | 8.93
2019-08-12 | 7.9 | 7.85
2019-08-12 00:30 | 7.09 | 7.04
2019-08-12 01:00 | 6.63 | 6.56
2019-08-12 01:30 | 6.27 | 6.19
2019-08-12 02:00 | 5.91 | 5.83
2019-08-12 02:30 | 5.76 | 5.67
2019-08-12 03:00 | 5.62 | 5.53
2019-08-12 03:30 | 5.64 | 5.55
2019-08-12 04:00 | 5.64 | 5.55
2019-08-12 04:30 | 5.94 | 5.86
2019-08-12 05:00 | 6.41 | 6.35
2019-08-12 05:30 | 7.27 | 7.22
2019-08-12 06:00 | 8 | 7.97
2019-08-12 06:30 | 9.45 | 9.42
2019-08-12 07:00 | 10.66 | 10.64
2019-08-12 07:30 | 10.98 | 10.97
2019-08-12 08:00 | 9.81 | 9.8
2019-08-12 08:30 | 8.25 | 8.23
2019-08-12 09:00 | 6.68 | 6.66
2019-08-12 09:30 | 5.55 | 5.52
2019-08-12 10:00 | 4.78 | 4.75
2019-08-12 10:30 | 4.11 | 4.07
2019-08-12 11:00 | 3.4 | 3.35
2019-08-12 11:30 | 3.07 | 3.01
2019-08-12 12:00 | 2.74 | 2.68
2019-08-12 12:30 | 2.57 | 2.49
2019-08-12 13:00 | 2.41 | 2.3
2019-08-12 13:30 | 2.55 | 2.46
2019-08-12 14:00 | 2.93 | 2.84
2019-08-12 14:30 | 3.46 | 3.39
2019-08-12 15:00 | 3.92 | 3.86
2019-08-12 15:30 | 4.94 | 4.89
2019-08-12 16:00 | 6.07 | 6.02
2019-08-12 16:30 | 7.55 | 7.5
2019-08-12 17:00 | 9.2 | 9.17
2019-08-12 17:30 | 11.17 | 11.15
2019-08-12 18:00 | 13.05 | 13.04
2019-08-12 18:30 | 14.28 | 14.28
2019-08-12 19:00 | 14.54 | 14.54
2019-08-12 19:30 | 14.29 | 14.29
2019-08-12 20:00 | 14.16 | 14.16
2019-08-12 20:30 | 14.22 | 14.22
2019-08-12 21:00 | 13.86 | 13.85
2019-08-12 21:30 | 12.85 | 12.85
2019-08-12 22:00 | 11.79 | 11.79
2019-08-12 22:30 | 10.98 | 10.97
2019-08-12 23:00 | 10.2 | 10.17
2019-08-12 23:30 | 9.13 | 9.09
2019-08-13 | 7.98 | 7.94
2019-08-13 00:30 | 7.21 | 7.15
2019-08-13 01:00 | 6.73 | 6.66
2019-08-13 01:30 | 6.48 | 6.41
2019-08-13 02:00 | 6.17 | 6.1
2019-08-13 02:30 | 6.1 | 6.02
2019-08-13 03:00 | 5.93 | 5.84
2019-08-13 03:30 | 6.11 | 6.03
2019-08-13 04:00 | 6.18 | 6.11
2019-08-13 04:30 | 6.47 | 6.39
2019-08-13 05:00 | 7.02 | 6.97
2019-08-13 05:30 | 7.87 | 7.83
2019-08-13 06:00 | 8.7 | 8.67
2019-08-13 06:30 | 9.91 | 9.89
2019-08-13 07:00 | 11.38 | 11.36
2019-08-13 07:30 | 11.78 | 11.77
2019-08-13 08:00 | 10.79 | 10.78
2019-08-13 08:30 | 8.55 | 8.53
2019-08-13 09:00 | 6.94 | 6.91
2019-08-13 09:30 | 5.85 | 5.82
2019-08-13 10:00 | 4.59 | 4.54
2019-08-13 10:30 | 3.64 | 3.56
2019-08-13 11:00 | 3.05 | 2.96
2019-08-13 11:30 | 2.4 | 2.28
2019-08-13 12:00 | 2.76 | 2.67
2019-08-13 12:30 | 4.52 | 4.46
2019-08-13 13:00 | 3.67 | 3.59
2019-08-13 13:30 | 3.27 | 3.18
2019-08-13 14:00 | 3.73 | 3.65
2019-08-13 14:30 | 3.37 | 3.27
2019-08-13 15:00 | 4.28 | 4.19
2019-08-13 15:30 | 4.33 | 4.26
2019-08-13 16:00 | 5.42 | 5.35
2019-08-13 16:30 | 7.35 | 7.31
2019-08-13 17:00 | 8.93 | 8.9
2019-08-13 17:30 | 10.57 | 10.55
2019-08-13 18:00 | 12.15 | 12.14
2019-08-13 18:30 | 13.18 | 13.17
2019-08-13 19:00 | 13.43 | 13.43
2019-08-13 19:30 | 13.08 | 13.08
2019-08-13 20:00 | 13.08 | 13.08
2019-08-13 20:30 | 13.18 | 13.18
2019-08-13 21:00 | 12.63 | 12.63
2019-08-13 21:30 | 11.81 | 11.8
2019-08-13 22:00 | 10.75 | 10.73
2019-08-13 22:30 | 10.26 | 10.24
2019-08-13 23:00 | 9.94 | 9.91
2019-08-13 23:30 | 8.9 | 8.87
2019-08-14 | 7.72 | 7.67
2019-08-14 00:30 | 6.91 | 6.84
2019-08-14 01:00 | 6.5 | 6.44
2019-08-14 01:30 | 6.19 | 6.12
2019-08-14 02:00 | 5.8 | 5.72
2019-08-14 02:30 | 5.67 | 5.57
2019-08-14 03:00 | 5.55 | 5.46
2019-08-14 03:30 | 5.51 | 5.41
2019-08-14 04:00 | 5.53 | 5.44
2019-08-14 04:30 | 5.75 | 5.66
2019-08-14 05:00 | 6.18 | 6.11
2019-08-14 05:30 | 6.74 | 6.68
2019-08-14 06:00 | 7.54 | 7.5
2019-08-14 06:30 | 8.37 | 8.33
2019-08-14 07:00 | 9.35 | 9.31
2019-08-14 07:30 | 10 | 9.98
2019-08-14 08:00 | 10.42 | 10.41
2019-08-14 08:30 | 8.76 | 8.73
2019-08-14 09:00 | 7.49 | 7.46
2019-08-14 09:30 | 6.81 | 6.77
2019-08-14 10:00 | 6.08 | 6.04
2019-08-14 10:30 | 4.84 | 4.79
2019-08-14 11:00 | 4.21 | 4.17
2019-08-14 11:30 | 4.7 | 4.66
2019-08-14 12:00 | 4.2 | 4.16
2019-08-14 12:30 | 4.12 | 4.08
2019-08-14 13:00 | 4.49 | 4.45
2019-08-14 13:30 | 6.02 | 5.96
2019-08-14 14:00 | 7.69 | 7.65
2019-08-14 14:30 | 7.16 | 7.11
2019-08-14 15:00 | 6.39 | 6.33
2019-08-14 15:30 | 7.58 | 7.52
2019-08-14 16:00 | 8.77 | 8.72
2019-08-14 16:30 | 9.63 | 9.6
2019-08-14 17:00 | 10.07 | 10.04
2019-08-14 17:30 | 11.25 | 11.23
2019-08-14 18:00 | 12.91 | 12.91
2019-08-14 18:30 | 13.88 | 13.88
2019-08-14 19:00 | 13.94 | 13.94
2019-08-14 19:30 | 13.74 | 13.74
2019-08-14 20:00 | 13.88 | 13.87
2019-08-14 20:30 | 13.86 | 13.86
2019-08-14 21:00 | 13.42 | 13.42
2019-08-14 21:30 | 12.5 | 12.49
2019-08-14 22:00 | 11.6 | 11.59
2019-08-14 22:30 | 10.75 | 10.73
2019-08-14 23:00 | 10.25 | 10.23
2019-08-14 23:30 | 9.23 | 9.19
2019-08-15 | 8.1 | 8.06
2019-08-15 00:30 | 7.26 | 7.2
2019-08-15 01:00 | 6.84 | 6.78
2019-08-15 01:30 | 6.37 | 6.3
2019-08-15 02:00 | 6.06 | 5.98
2019-08-15 02:30 | 6.04 | 5.97
2019-08-15 03:00 | 5.84 | 5.75
2019-08-15 03:30 | 5.88 | 5.79
2019-08-15 04:00 | 6.02 | 5.94
2019-08-15 04:30 | 6.46 | 6.39
2019-08-15 05:00 | 6.94 | 6.88
2019-08-15 05:30 | 7.84 | 7.81
2019-08-15 06:00 | 8.72 | 8.7
2019-08-15 06:30 | 9.75 | 9.72
2019-08-15 07:00 | 10.87 | 10.85
2019-08-15 07:30 | 10.78 | 10.76
2019-08-15 08:00 | 9.6 | 9.58
2019-08-15 08:30 | 7.48 | 7.44
2019-08-15 09:00 | 5.88 | 5.84
2019-08-15 09:30 | 4.84 | 4.78
2019-08-15 10:00 | 3.82 | 3.74
2019-08-15 10:30 | 3.14 | 3.06
2019-08-15 11:00 | 2.53 | 2.43
2019-08-15 11:30 | 2.25 | 2.14
2019-08-15 12:00 | 2.07 | 1.96
2019-08-15 12:30 | 2.03 | 1.94
2019-08-15 13:00 | 2.43 | 2.35
2019-08-15 13:30 | 3.14 | 3.07
2019-08-15 14:00 | 3.35 | 3.27
2019-08-15 14:30 | 3.51 | 3.44
2019-08-15 15:00 | 3.73 | 3.65
2019-08-15 15:30 | 4.62 | 4.56
2019-08-15 16:00 | 5.47 | 5.41
2019-08-15 16:30 | 6.83 | 6.79
2019-08-15 17:00 | 8.38 | 8.34
2019-08-15 17:30 | 10.09 | 10.07
2019-08-15 18:00 | 11.51 | 11.51
2019-08-15 18:30 | 12.45 | 12.45
2019-08-15 19:00 | 12.73 | 12.73
2019-08-15 19:30 | 12.7 | 12.7
2019-08-15 20:00 | 12.61 | 12.6
2019-08-15 20:30 | 12.64 | 12.64
2019-08-15 21:00 | 12.15 | 12.15
2019-08-15 21:30 | 11.41 | 11.4
2019-08-15 22:00 | 10.68 | 10.66
2019-08-15 22:30 | 10.03 | 10.01
2019-08-15 23:00 | 9.61 | 9.58
2019-08-15 23:30 | 8.61 | 8.57
2019-08-16 | 7.71 | 7.65
2019-08-16 00:30 | 6.9 | 6.84
2019-08-16 01:00 | 6.46 | 6.38
2019-08-16 01:30 | 6.05 | 5.98
2019-08-16 02:00 | 5.82 | 5.73
2019-08-16 02:30 | 5.65 | 5.56
2019-08-16 03:00 | 5.4 | 5.3
2019-08-16 03:30 | 5.5 | 5.4
2019-08-16 04:00 | 5.57 | 5.48
2019-08-16 04:30 | 5.93 | 5.84
2019-08-16 05:00 | 6.37 | 6.3
2019-08-16 05:30 | 7.16 | 7.12
2019-08-16 06:00 | 7.99 | 7.96
2019-08-16 06:30 | 8.78 | 8.74
2019-08-16 07:00 | 9.73 | 9.7
2019-08-16 07:30 | 10.45 | 10.43
2019-08-16 08:00 | 9.08 | 9.06
2019-08-16 08:30 | 7.26 | 7.22
2019-08-16 09:00 | 5.75 | 5.69
2019-08-16 09:30 | 4.47 | 4.4
2019-08-16 10:00 | 3.49 | 3.41
2019-08-16 10:30 | 2.72 | 2.62
2019-08-16 11:00 | 2.17 | 2.05
2019-08-16 11:30 | 1.78 | 1.65
2019-08-16 12:00 | 1.72 | 1.59
2019-08-16 12:30 | 1.69 | 1.56
2019-08-16 13:00 | 1.68 | 1.57
2019-08-16 13:30 | 1.84 | 1.73
2019-08-16 14:00 | 2.26 | 2.18
2019-08-16 14:30 | 3.07 | 3
2019-08-16 15:00 | 5.15 | 5.09
2019-08-16 15:30 | 5.66 | 5.6
2019-08-16 16:00 | 5.66 | 5.6
2019-08-16 16:30 | 6.88 | 6.83
2019-08-16 17:00 | 8.52 | 8.49
2019-08-16 17:30 | 9.31 | 9.28
2019-08-16 18:00 | 10.5 | 10.49
2019-08-16 18:30 | 11.28 | 11.28
2019-08-16 19:00 | 11.65 | 11.65
2019-08-16 19:30 | 11.43 | 11.43
2019-08-16 20:00 | 11.44 | 11.43
2019-08-16 20:30 | 11.5 | 11.5
2019-08-16 21:00 | 11.07 | 11.06
2019-08-16 21:30 | 10.51 | 10.5
2019-08-16 22:00 | 9.98 | 9.96
2019-08-16 22:30 | 9.61 | 9.58
2019-08-16 23:00 | 9.42 | 9.39
2019-08-16 23:30 | 8.53 | 8.49
2019-08-17 | 7.62 | 7.56
2019-08-17 00:30 | 6.84 | 6.77
2019-08-17 01:00 | 6.36 | 6.28
2019-08-17 01:30 | 6.05 | 5.97
2019-08-17 02:00 | 5.63 | 5.54
2019-08-17 02:30 | 5.49 | 5.4
2019-08-17 03:00 | 5.36 | 5.27
2019-08-17 03:30 | 5.24 | 5.13
2019-08-17 04:00 | 5.27 | 5.16
2019-08-17 04:30 | 5.42 | 5.32
2019-08-17 05:00 | 5.62 | 5.53
2019-08-17 05:30 | 5.89 | 5.81
2019-08-17 06:00 | 6.17 | 6.09
2019-08-17 06:30 | 6.58 | 6.48
2019-08-17 07:00 | 6.96 | 6.86
2019-08-17 07:30 | 7.14 | 7.06
2019-08-17 08:00 | 6.79 | 6.71
2019-08-17 08:30 | 6.33 | 6.24
2019-08-17 09:00 | 5.93 | 5.86
2019-08-17 09:30 | 5.17 | 5.11
2019-08-17 10:00 | 4.34 | 4.27
2019-08-17 10:30 | 3.72 | 3.65
2019-08-17 11:00 | 3.21 | 3.14
2019-08-17 11:30 | 2.82 | 2.73
2019-08-17 12:00 | 2.56 | 2.47
2019-08-17 12:30 | 2.63 | 2.56
2019-08-17 13:00 | 2.64 | 2.58
2019-08-17 13:30 | 2.79 | 2.74
2019-08-17 14:00 | 3.2 | 3.15
2019-08-17 14:30 | 3.57 | 3.52
2019-08-17 15:00 | 4.23 | 4.19
2019-08-17 15:30 | 5.06 | 5.03
2019-08-17 16:00 | 5.87 | 5.83
2019-08-17 16:30 | 7.04 | 7.01
2019-08-17 17:00 | 8.12 | 8.1
2019-08-17 17:30 | 9.16 | 9.14
2019-08-17 18:00 | 10.09 | 10.08
2019-08-17 18:30 | 10.75 | 10.74
2019-08-17 19:00 | 10.98 | 10.98
2019-08-17 19:30 | 10.62 | 10.61
2019-08-17 20:00 | 10.52 | 10.51
2019-08-17 20:30 | 10.57 | 10.56
2019-08-17 21:00 | 10.07 | 10.06
2019-08-17 21:30 | 9.5 | 9.48
2019-08-17 22:00 | 9.09 | 9.06
2019-08-17 22:30 | 8.84 | 8.8
2019-08-17 23:00 | 8.68 | 8.64
2019-08-17 23:30 | 7.95 | 7.9
2019-08-18 | 7.02 | 6.96
2019-08-18 00:30 | 6.34 | 6.27
2019-08-18 01:00 | 6.05 | 5.98
2019-08-18 01:30 | 5.71 | 5.62
2019-08-18 02:00 | 5.32 | 5.22
2019-08-18 02:30 | 5.17 | 5.07
2019-08-18 03:00 | 4.96 | 4.85
2019-08-18 03:30 | 4.96 | 4.84
2019-08-18 04:00 | 4.97 | 4.85
2019-08-18 04:30 | 4.94 | 4.82
2019-08-18 05:00 | 5.03 | 4.91
2019-08-18 05:30 | 5.2 | 5.09
2019-08-18 06:00 | 5.49 | 5.39
2019-08-18 06:30 | 5.8 | 5.65
2019-08-18 07:00 | 6.13 | 5.98
2019-08-18 07:30 | 6.25 | 6.13
2019-08-18 08:00 | 6.19 | 6.09
2019-08-18 08:30 | 5.92 | 5.82
2019-08-18 09:00 | 5.55 | 5.46
2019-08-18 09:30 | 4.91 | 4.83
2019-08-18 10:00 | 4.77 | 4.7
2019-08-18 10:30 | 3.99 | 3.92
2019-08-18 11:00 | 3.78 | 3.72
2019-08-18 11:30 | 3.8 | 3.76
2019-08-18 12:00 | 3.86 | 3.82
2019-08-18 12:30 | 3.8 | 3.76
2019-08-18 13:00 | 3.61 | 3.56
2019-08-18 13:30 | 3.68 | 3.64
2019-08-18 14:00 | 3.63 | 3.58
2019-08-18 14:30 | 4.01 | 3.96
2019-08-18 15:00 | 4.58 | 4.53
2019-08-18 15:30 | 5.46 | 5.41
2019-08-18 16:00 | 6.41 | 6.37
2019-08-18 16:30 | 7.65 | 7.6
2019-08-18 17:00 | 8.98 | 8.94
2019-08-18 17:30 | 10.35 | 10.32
2019-08-18 18:00 | 11.49 | 11.48
2019-08-18 18:30 | 12.09 | 12.09
2019-08-18 19:00 | 11.97 | 11.96
2019-08-18 19:30 | 11.64 | 11.63
2019-08-18 20:00 | 11.49 | 11.48
2019-08-18 20:30 | 11.36 | 11.34
2019-08-18 21:00 | 10.83 | 10.82
2019-08-18 21:30 | 10.28 | 10.26
2019-08-18 22:00 | 9.53 | 9.51
2019-08-18 22:30 | 8.93 | 8.9
2019-08-18 23:00 | 8.45 | 8.41
2019-08-18 23:30 | 7.48 | 7.43
2019-08-19 | 6.62 | 6.55
2019-08-19 00:30 | 5.96 | 5.88
2019-08-19 01:00 | 5.6 | 5.5
2019-08-19 01:30 | 5.26 | 5.16
2019-08-19 02:00 | 4.91 | 4.8
2019-08-19 02:30 | 4.83 | 4.71
2019-08-19 03:00 | 4.77 | 4.66
2019-08-19 03:30 | 4.8 | 4.68
2019-08-19 04:00 | 4.78 | 4.65
2019-08-19 04:30 | 4.96 | 4.84
2019-08-19 05:00 | 5.33 | 5.23
2019-08-19 05:30 | 5.9 | 5.83
2019-08-19 06:00 | 6.6 | 6.54
2019-08-19 06:30 | 7.54 | 7.48
2019-08-19 07:00 | 8.64 | 8.59
2019-08-19 07:30 | 8.78 | 8.74
2019-08-19 08:00 | 7.83 | 7.78
2019-08-19 08:30 | 6.81 | 6.76
2019-08-19 09:00 | 5.02 | 4.96
2019-08-19 09:30 | 4.04 | 3.98
2019-08-19 10:00 | 3.28 | 3.22
2019-08-19 10:30 | 2.74 | 2.67
2019-08-19 11:00 | 2.35 | 2.28
2019-08-19 11:30 | 2.08 | 2.01
2019-08-19 12:00 | 1.97 | 1.9
2019-08-19 12:30 | 2.11 | 2.06
2019-08-19 13:00 | 2.24 | 2.2
2019-08-19 13:30 | 2.47 | 2.43
2019-08-19 14:00 | 2.84 | 2.8
2019-08-19 14:30 | 3.23 | 3.19
2019-08-19 15:00 | 3.76 | 3.73
2019-08-19 15:30 | 4.77 | 4.74
2019-08-19 16:00 | 5.88 | 5.85
2019-08-19 16:30 | 7.3 | 7.26
2019-08-19 17:00 | 9.02 | 8.99
2019-08-19 17:30 | 10.52 | 10.5
2019-08-19 18:00 | 11.91 | 11.91
2019-08-19 18:30 | 12.82 | 12.81
2019-08-19 19:00 | 13.05 | 13.05
2019-08-19 19:30 | 12.84 | 12.84
2019-08-19 20:00 | 12.47 | 12.47
2019-08-19 20:30 | 12.31 | 12.3
2019-08-19 21:00 | 12.05 | 12.04
2019-08-19 21:30 | 11.19 | 11.18
2019-08-19 22:00 | 10.1 | 10.09
2019-08-19 22:30 | 9.41 | 9.38
2019-08-19 23:00 | 8.92 | 8.88
2019-08-19 23:30 | 7.96 | 7.91
2019-08-20 | 7.1 | 7.04
2019-08-20 00:30 | 6.35 | 6.27
2019-08-20 01:00 | 5.99 | 5.91
2019-08-20 01:30 | 5.66 | 5.57
2019-08-20 02:00 | 5.33 | 5.23
2019-08-20 02:30 | 5.2 | 5.1
2019-08-20 03:00 | 5.14 | 5.03
2019-08-20 03:30 | 5.32 | 5.21
2019-08-20 04:00 | 5.52 | 5.43
2019-08-20 04:30 | 5.69 | 5.6
2019-08-20 05:00 | 6.27 | 6.2
2019-08-20 05:30 | 7.18 | 7.13
2019-08-20 06:00 | 8.12 | 8.07
2019-08-20 06:30 | 8.95 | 8.89
2019-08-20 07:00 | 9.83 | 9.79
2019-08-20 07:30 | 9.83 | 9.8
2019-08-20 08:00 | 8.5 | 8.47
2019-08-20 08:30 | 6.66 | 6.59
2019-08-20 09:00 | 5.06 | 4.98
2019-08-20 09:30 | 3.99 | 3.92
2019-08-20 10:00 | 2.94 | 2.83
2019-08-20 10:30 | 2.23 | 2.08
2019-08-20 11:00 | 1.85 | 1.66
2019-08-20 11:30 | 1.55 | 1.35
2019-08-20 12:00 | 1.38 | 1.16
2019-08-20 12:30 | 1.34 | 1.14
2019-08-20 13:00 | 1.35 | 1.12
2019-08-20 13:30 | 1.63 | 1.46
2019-08-20 14:00 | 2.25 | 2.15
2019-08-20 14:30 | 2.75 | 2.66
2019-08-20 15:00 | 3.25 | 3.16
2019-08-20 15:30 | 4.1 | 4.03
2019-08-20 16:00 | 5.48 | 5.42
2019-08-20 16:30 | 7.01 | 6.97
2019-08-20 17:00 | 8.86 | 8.84
2019-08-20 17:30 | 10.52 | 10.5
2019-08-20 18:00 | 12.28 | 12.27
2019-08-20 18:30 | 13.69 | 13.69
2019-08-20 19:00 | 13.9 | 13.9
2019-08-20 19:30 | 13.71 | 13.71
2019-08-20 20:00 | 13.53 | 13.52
2019-08-20 20:30 | 13.93 | 13.93
2019-08-20 21:00 | 13.53 | 13.53
2019-08-20 21:30 | 12.37 | 12.37
2019-08-20 22:00 | 11.34 | 11.33
2019-08-20 22:30 | 10.67 | 10.65
2019-08-20 23:00 | 10.21 | 10.19
2019-08-20 23:30 | 9.12 | 9.09
2019-08-21 | 8.06 | 8.01
2019-08-21 00:30 | 7.27 | 7.21
2019-08-21 01:00 | 6.88 | 6.81
2019-08-21 01:30 | 6.42 | 6.35
2019-08-21 02:00 | 6.05 | 5.97
2019-08-21 02:30 | 5.9 | 5.82
2019-08-21 03:00 | 5.76 | 5.68
2019-08-21 03:30 | 5.92 | 5.83
2019-08-21 04:00 | 5.98 | 5.91
2019-08-21 04:30 | 6.33 | 6.26
2019-08-21 05:00 | 6.72 | 6.65
2019-08-21 05:30 | 7.65 | 7.61
2019-08-21 06:00 | 8.61 | 8.58
2019-08-21 06:30 | 9.53 | 9.5
2019-08-21 07:00 | 10.39 | 10.37
2019-08-21 07:30 | 10.25 | 10.23
2019-08-21 08:00 | 8.95 | 8.92
2019-08-21 08:30 | 6.79 | 6.74
2019-08-21 09:00 | 5.16 | 5.1
2019-08-21 09:30 | 3.97 | 3.89
2019-08-21 10:00 | 2.99 | 2.86
2019-08-21 10:30 | 2.28 | 2.14
2019-08-21 11:00 | 1.87 | 1.73
2019-08-21 11:30 | 1.64 | 1.49
2019-08-21 12:00 | 1.52 | 1.36
2019-08-21 12:30 | 1.45 | 1.3
2019-08-21 13:00 | 1.53 | 1.38
2019-08-21 13:30 | 1.89 | 1.78
2019-08-21 14:00 | 1.99 | 1.88
2019-08-21 14:30 | 2.56 | 2.49
2019-08-21 15:00 | 3.35 | 3.3
2019-08-21 15:30 | 4.29 | 4.24
2019-08-21 16:00 | 5.61 | 5.57
2019-08-21 16:30 | 6.9 | 6.86
2019-08-21 17:00 | 8.7 | 8.68
2019-08-21 17:30 | 10.18 | 10.16
2019-08-21 18:00 | 11.54 | 11.53
2019-08-21 18:30 | 12.76 | 12.76
2019-08-21 19:00 | 12.92 | 12.92
2019-08-21 19:30 | 12.71 | 12.71
2019-08-21 20:00 | 12.51 | 12.5
2019-08-21 20:30 | 12.72 | 12.72
2019-08-21 21:00 | 12.33 | 12.33
2019-08-21 21:30 | 11.33 | 11.32
2019-08-21 22:00 | 10.43 | 10.42
2019-08-21 22:30 | 9.52 | 9.49
2019-08-21 23:00 | 9.17 | 9.14
2019-08-21 23:30 | 8.25 | 8.21
2019-08-22 | 7.1 | 7.04
2019-08-22 00:30 | 6.37 | 6.3
2019-08-22 01:00 | 5.89 | 5.81
2019-08-22 01:30 | 5.53 | 5.43
2019-08-22 02:00 | 5.24 | 5.13
2019-08-22 02:30 | 5.22 | 5.12
2019-08-22 03:00 | 4.97 | 4.86
2019-08-22 03:30 | 5.1 | 4.99
2019-08-22 04:00 | 5.19 | 5.09
2019-08-22 04:30 | 5.51 | 5.41
2019-08-22 05:00 | 5.96 | 5.88
2019-08-22 05:30 | 6.76 | 6.71
2019-08-22 06:00 | 7.43 | 7.38
2019-08-22 06:30 | 8.41 | 8.35
2019-08-22 07:00 | 8.97 | 8.93
2019-08-22 07:30 | 8.74 | 8.69
2019-08-22 08:00 | 7.56 | 7.5
2019-08-22 08:30 | 5.72 | 5.65
2019-08-22 09:00 | 4.17 | 4.08
2019-08-22 09:30 | 3.19 | 3.07
2019-08-22 10:00 | 2.45 | 2.31
2019-08-22 10:30 | 1.88 | 1.72
2019-08-22 11:00 | 1.4 | 1.23
2019-08-22 11:30 | 1.24 | 1.07
2019-08-22 12:00 | 1.14 | 0.95
2019-08-22 12:30 | 1.18 | 1.01
2019-08-22 13:00 | 1.18 | 1
2019-08-22 13:30 | 1.4 | 1.28
2019-08-22 14:00 | 2.03 | 1.94
2019-08-22 14:30 | 2.74 | 2.68
2019-08-22 15:00 | 3.22 | 3.16
2019-08-22 15:30 | 4.35 | 4.3
2019-08-22 16:00 | 5.62 | 5.58
2019-08-22 16:30 | 7 | 6.96
2019-08-22 17:00 | 8.57 | 8.55
2019-08-22 17:30 | 10.01 | 9.99
2019-08-22 18:00 | 11.34 | 11.34
2019-08-22 18:30 | 12.3 | 12.3
2019-08-22 19:00 | 12.53 | 12.53
2019-08-22 19:30 | 12.48 | 12.48
2019-08-22 20:00 | 12.26 | 12.26
2019-08-22 20:30 | 11.95 | 11.94
2019-08-22 21:00 | 11.63 | 11.62
2019-08-22 21:30 | 11.07 | 11.07
2019-08-22 22:00 | 10.06 | 10.04
2019-08-22 22:30 | 9.26 | 9.23
2019-08-22 23:00 | 8.81 | 8.77
2019-08-22 23:30 | 7.82 | 7.77
2019-08-23 | 7.02 | 6.96
2019-08-23 00:30 | 6.23 | 6.16
2019-08-23 01:00 | 5.87 | 5.79
2019-08-23 01:30 | 5.4 | 5.31
2019-08-23 02:00 | 5.13 | 5.03
2019-08-23 02:30 | 5.03 | 4.94
2019-08-23 03:00 | 4.89 | 4.78
2019-08-23 03:30 | 5.01 | 4.9
2019-08-23 04:00 | 5.13 | 5.02
2019-08-23 04:30 | 5.34 | 5.25
2019-08-23 05:00 | 5.72 | 5.64
2019-08-23 05:30 | 6.41 | 6.35
2019-08-23 06:00 | 7.2 | 7.16
2019-08-23 06:30 | 7.93 | 7.87
2019-08-23 07:00 | 8.54 | 8.48
2019-08-23 07:30 | 8.41 | 8.37
2019-08-23 08:00 | 7.34 | 7.28
2019-08-23 08:30 | 5.75 | 5.68
2019-08-23 09:00 | 4.41 | 4.34
2019-08-23 09:30 | 3.73 | 3.64
2019-08-23 10:00 | 2.59 | 2.47
2019-08-23 10:30 | 1.99 | 1.85
2019-08-23 11:00 | 1.59 | 1.43
2019-08-23 11:30 | 1.31 | 1.14
2019-08-23 12:00 | 1.29 | 1.13
2019-08-23 12:30 | 1.21 | 1.02
2019-08-23 13:00 | 1.34 | 1.19
2019-08-23 13:30 | 1.51 | 1.38
2019-08-23 14:00 | 1.92 | 1.8
2019-08-23 14:30 | 2.37 | 2.26
2019-08-23 15:00 | 2.93 | 2.83
2019-08-23 15:30 | 3.88 | 3.8
2019-08-23 16:00 | 5.07 | 5.02
2019-08-23 16:30 | 6.42 | 6.38
2019-08-23 17:00 | 7.94 | 7.9
2019-08-23 17:30 | 9.11 | 9.07
2019-08-23 18:00 | 10.17 | 10.16
2019-08-23 18:30 | 11.22 | 11.21
2019-08-23 19:00 | 11.47 | 11.47
2019-08-23 19:30 | 11.26 | 11.25
2019-08-23 20:00 | 11.25 | 11.24
2019-08-23 20:30 | 11.36 | 11.35
2019-08-23 21:00 | 11.02 | 11.01
2019-08-23 21:30 | 10.37 | 10.36
2019-08-23 22:00 | 9.9 | 9.88
2019-08-23 22:30 | 9.59 | 9.56
2019-08-23 23:00 | 9.37 | 9.34
2019-08-23 23:30 | 8.5 | 8.45
2019-08-24 | 7.63 | 7.57
2019-08-24 00:30 | 7 | 6.94
2019-08-24 01:00 | 6.53 | 6.46
2019-08-24 01:30 | 6.07 | 5.99
2019-08-24 02:00 | 5.73 | 5.63
2019-08-24 02:30 | 5.52 | 5.43
2019-08-24 03:00 | 5.36 | 5.27
2019-08-24 03:30 | 5.31 | 5.21
2019-08-24 04:00 | 5.4 | 5.3
2019-08-24 04:30 | 5.45 | 5.35
2019-08-24 05:00 | 5.67 | 5.57
2019-08-24 05:30 | 5.95 | 5.87
2019-08-24 06:00 | 6.31 | 6.23
2019-08-24 06:30 | 6.81 | 6.71
2019-08-24 07:00 | 7.2 | 7.09
2019-08-24 07:30 | 7.18 | 7.09
2019-08-24 08:00 | 6.98 | 6.91
2019-08-24 08:30 | 6.64 | 6.57
2019-08-24 09:00 | 5.97 | 5.91
2019-08-24 09:30 | 5.42 | 5.36
2019-08-24 10:00 | 4.69 | 4.63
2019-08-24 10:30 | 4.11 | 4.06
2019-08-24 11:00 | 4.54 | 4.49
2019-08-24 11:30 | 3.86 | 3.8
2019-08-24 12:00 | 3.16 | 3.09
2019-08-24 12:30 | 3.1 | 3.03
2019-08-24 13:00 | 3.31 | 3.26
2019-08-24 13:30 | 3.22 | 3.15
2019-08-24 14:00 | 3.36 | 3.29
2019-08-24 14:30 | 3.38 | 3.31
2019-08-24 15:00 | 3.75 | 3.68
2019-08-24 15:30 | 4.61 | 4.54
2019-08-24 16:00 | 5.57 | 5.51
2019-08-24 16:30 | 6.85 | 6.8
2019-08-24 17:00 | 8.06 | 8.01
2019-08-24 17:30 | 9.14 | 9.1
2019-08-24 18:00 | 10.19 | 10.18
2019-08-24 18:30 | 11.04 | 11.04
2019-08-24 19:00 | 11.39 | 11.38
2019-08-24 19:30 | 11.1 | 11.09
2019-08-24 20:00 | 11.1 | 11.09
2019-08-24 20:30 | 10.97 | 10.96
2019-08-24 21:00 | 10.6 | 10.59
2019-08-24 21:30 | 10.07 | 10.06
2019-08-24 22:00 | 9.56 | 9.54
2019-08-24 22:30 | 9.39 | 9.36
2019-08-24 23:00 | 9.24 | 9.2
2019-08-24 23:30 | 8.56 | 8.52
2019-08-25 | 7.64 | 7.59
2019-08-25 00:30 | 6.89 | 6.82
2019-08-25 01:00 | 6.54 | 6.46
2019-08-25 01:30 | 6.11 | 6.02
2019-08-25 02:00 | 5.78 | 5.69
2019-08-25 02:30 | 5.59 | 5.5
2019-08-25 03:00 | 5.38 | 5.28
2019-08-25 03:30 | 5.43 | 5.34
2019-08-25 04:00 | 5.39 | 5.29
2019-08-25 04:30 | 5.4 | 5.3
2019-08-25 05:00 | 5.46 | 5.36
2019-08-25 05:30 | 5.72 | 5.63
2019-08-25 06:00 | 5.91 | 5.81
2019-08-25 06:30 | 6.24 | 6.11
2019-08-25 07:00 | 6.46 | 6.34
2019-08-25 07:30 | 6.37 | 6.25
2019-08-25 08:00 | 6.29 | 6.19
2019-08-25 08:30 | 6.09 | 6
2019-08-25 09:00 | 5.62 | 5.54
2019-08-25 09:30 | 4.99 | 4.91
2019-08-25 10:00 | 4.43 | 4.35
2019-08-25 10:30 | 3.82 | 3.76
2019-08-25 11:00 | 3.28 | 3.21
2019-08-25 11:30 | 2.94 | 2.87
2019-08-25 12:00 | 2.75 | 2.67
2019-08-25 12:30 | 2.74 | 2.68
2019-08-25 13:00 | 2.75 | 2.68
2019-08-25 13:30 | 2.83 | 2.77
2019-08-25 14:00 | 3.33 | 3.28
2019-08-25 14:30 | 3.74 | 3.69
2019-08-25 15:00 | 4.33 | 4.27
2019-08-25 15:30 | 5.18 | 5.12
2019-08-25 16:00 | 6.72 | 6.67
2019-08-25 16:30 | 8.46 | 8.43
2019-08-25 17:00 | 9.25 | 9.21
2019-08-25 17:30 | 10.37 | 10.34
2019-08-25 18:00 | 11.43 | 11.42
2019-08-25 18:30 | 12.12 | 12.12
2019-08-25 19:00 | 12.16 | 12.16
2019-08-25 19:30 | 11.8 | 11.79
2019-08-25 20:00 | 11.68 | 11.67
2019-08-25 20:30 | 11.45 | 11.44
2019-08-25 21:00 | 10.97 | 10.95
2019-08-25 21:30 | 10.26 | 10.24
2019-08-25 22:00 | 9.5 | 9.47
2019-08-25 22:30 | 8.89 | 8.86
2019-08-25 23:00 | 8.54 | 8.49
2019-08-25 23:30 | 7.61 | 7.55
2019-08-26 | 6.74 | 6.67
2019-08-26 00:30 | 6.1 | 6.03
2019-08-26 01:00 | 5.6 | 5.52
2019-08-26 01:30 | 5.26 | 5.16
2019-08-26 02:00 | 5.03 | 4.93
2019-08-26 02:30 | 4.88 | 4.77
2019-08-26 03:00 | 4.75 | 4.64
2019-08-26 03:30 | 4.76 | 4.65
2019-08-26 04:00 | 4.95 | 4.85
2019-08-26 04:30 | 5.2 | 5.1
2019-08-26 05:00 | 5.67 | 5.58
2019-08-26 05:30 | 6.23 | 6.17
2019-08-26 06:00 | 6.82 | 6.76
2019-08-26 06:30 | 7.75 | 7.68
2019-08-26 07:00 | 8.27 | 8.21
2019-08-26 07:30 | 8.12 | 8.07
2019-08-26 08:00 | 7.01 | 6.95
2019-08-26 08:30 | 5.45 | 5.38
2019-08-26 09:00 | 4.12 | 4.04
2019-08-26 09:30 | 3.4 | 3.32
2019-08-26 10:00 | 2.74 | 2.67
2019-08-26 10:30 | 2.26 | 2.17
2019-08-26 11:00 | 1.86 | 1.75
2019-08-26 11:30 | 1.57 | 1.46
2019-08-26 12:00 | 1.44 | 1.32
2019-08-26 12:30 | 1.48 | 1.39
2019-08-26 13:00 | 1.53 | 1.45
2019-08-26 13:30 | 1.86 | 1.8
2019-08-26 14:00 | 3.93 | 3.9
2019-08-26 14:30 | 4.73 | 4.7
2019-08-26 15:00 | 3.29 | 3.26
2019-08-26 15:30 | 3.81 | 3.78
2019-08-26 16:00 | 5.94 | 5.92
2019-08-26 16:30 | 7.31 | 7.29
2019-08-26 17:00 | 8.47 | 8.45
2019-08-26 17:30 | 10.07 | 10.05
2019-08-26 18:00 | 11.23 | 11.22
2019-08-26 18:30 | 12.12 | 12.11
2019-08-26 19:00 | 12.28 | 12.27
2019-08-26 19:30 | 11.81 | 11.8
2019-08-26 20:00 | 11.45 | 11.45
2019-08-26 20:30 | 11.38 | 11.37
2019-08-26 21:00 | 10.86 | 10.85
2019-08-26 21:30 | 9.95 | 9.93
2019-08-26 22:00 | 9.05 | 9.02
2019-08-26 22:30 | 8.42 | 8.39
2019-08-26 23:00 | 8.27 | 8.23
2019-08-26 23:30 | 7.2 | 7.14
2019-08-27 | 6.24 | 6.17
2019-08-27 00:30 | 5.55 | 5.46
2019-08-27 01:00 | 5.28 | 5.19
2019-08-27 01:30 | 5 | 4.9
2019-08-27 02:00 | 4.74 | 4.63
2019-08-27 02:30 | 4.68 | 4.57
2019-08-27 03:00 | 4.51 | 4.38
2019-08-27 03:30 | 4.59 | 4.47
2019-08-27 04:00 | 4.63 | 4.51
2019-08-27 04:30 | 4.98 | 4.88
2019-08-27 05:00 | 5.33 | 5.24
2019-08-27 05:30 | 5.87 | 5.8
2019-08-27 06:00 | 6.87 | 6.82
2019-08-27 06:30 | 7.62 | 7.56
2019-08-27 07:00 | 8.06 | 8
2019-08-27 07:30 | 8.62 | 8.58
2019-08-27 08:00 | 8.49 | 8.45
2019-08-27 08:30 | 8.54 | 8.49
2019-08-27 09:00 | 7.92 | 7.87
2019-08-27 09:30 | 6.92 | 6.86
2019-08-27 10:00 | 6.39 | 6.33
2019-08-27 10:30 | 5.48 | 5.42
2019-08-27 11:00 | 3.92 | 3.86
2019-08-27 11:30 | 3.02 | 2.96
2019-08-27 12:00 | 3.38 | 3.32
2019-08-27 12:30 | 3.03 | 2.98
2019-08-27 13:00 | 3.42 | 3.38
2019-08-27 13:30 | 3.61 | 3.57
2019-08-27 14:00 | 3.52 | 3.49
2019-08-27 14:30 | 4.37 | 4.34
2019-08-27 15:00 | 3.92 | 3.89
2019-08-27 15:30 | 5.54 | 5.52
2019-08-27 16:00 | 5.56 | 5.54
2019-08-27 16:30 | 7.54 | 7.51
2019-08-27 17:00 | 9.12 | 9.09
2019-08-27 17:30 | 10.09 | 10.07
2019-08-27 18:00 | 11.48 | 11.47
2019-08-27 18:30 | 12.43 | 12.43
2019-08-27 19:00 | 12.68 | 12.68
2019-08-27 19:30 | 12.34 | 12.34
2019-08-27 20:00 | 12.11 | 12.11
2019-08-27 20:30 | 11.68 | 11.68
2019-08-27 21:00 | 11.29 | 11.28
2019-08-27 21:30 | 10.36 | 10.34
2019-08-27 22:00 | 9.4 | 9.38
2019-08-27 22:30 | 8.62 | 8.59
2019-08-27 23:00 | 8.13 | 8.09
2019-08-27 23:30 | 7.21 | 7.16
2019-08-28 | 6.36 | 6.3
2019-08-28 00:30 | 5.68 | 5.6
2019-08-28 01:00 | 5.27 | 5.18
2019-08-28 01:30 | 4.91 | 4.81
2019-08-28 02:00 | 4.71 | 4.6
2019-08-28 02:30 | 4.62 | 4.51
2019-08-28 03:00 | 4.45 | 4.34
2019-08-28 03:30 | 4.5 | 4.38
2019-08-28 04:00 | 4.55 | 4.44
2019-08-28 04:30 | 4.84 | 4.74
2019-08-28 05:00 | 5.16 | 5.06
2019-08-28 05:30 | 5.61 | 5.54
2019-08-28 06:00 | 6.23 | 6.17
2019-08-28 06:30 | 6.91 | 6.83
2019-08-28 07:00 | 7.32 | 7.26
2019-08-28 07:30 | 7.83 | 7.78
2019-08-28 08:00 | 7.06 | 7.02
2019-08-28 08:30 | 6.75 | 6.69
2019-08-28 09:00 | 6.78 | 6.72
2019-08-28 09:30 | 6.39 | 6.33
2019-08-28 10:00 | 6.14 | 6.09
2019-08-28 10:30 | 5.16 | 5.11
2019-08-28 11:00 | 6.55 | 6.5
2019-08-28 11:30 | 5.56 | 5.5
2019-08-28 12:00 | 4.14 | 4.08
2019-08-28 12:30 | 4.89 | 4.84
2019-08-28 13:00 | 6.22 | 6.18
2019-08-28 13:30 | 6.67 | 6.62
2019-08-28 14:00 | 7.08 | 7.04
2019-08-28 14:30 | 7.5 | 7.46
2019-08-28 15:00 | 7.39 | 7.35
2019-08-28 15:30 | 7.74 | 7.69
2019-08-28 16:00 | 8.28 | 8.24
2019-08-28 16:30 | 8.75 | 8.72
2019-08-28 17:00 | 9.56 | 9.53
2019-08-28 17:30 | 10.56 | 10.54
2019-08-28 18:00 | 11.62 | 11.61
2019-08-28 18:30 | 12.89 | 12.89
2019-08-28 19:00 | 13.48 | 13.48
2019-08-28 19:30 | 13.1 | 13.1
2019-08-28 20:00 | 12.9 | 12.89
2019-08-28 20:30 | 12.87 | 12.86
2019-08-28 21:00 | 12.33 | 12.32
2019-08-28 21:30 | 11.3 | 11.29
2019-08-28 22:00 | 10.21 | 10.19
2019-08-28 22:30 | 9.31 | 9.28
2019-08-28 23:00 | 8.96 | 8.93
2019-08-28 23:30 | 8.01 | 7.97
2019-08-29 | 6.93 | 6.87
2019-08-29 00:30 | 6.19 | 6.1
2019-08-29 01:00 | 6.15 | 6.07
2019-08-29 01:30 | 5.56 | 5.47
2019-08-29 02:00 | 5.06 | 4.96
2019-08-29 02:30 | 4.84 | 4.72
2019-08-29 03:00 | 4.91 | 4.8
2019-08-29 03:30 | 4.82 | 4.7
2019-08-29 04:00 | 4.93 | 4.81
2019-08-29 04:30 | 5.21 | 5.11
2019-08-29 05:00 | 5.48 | 5.38
2019-08-29 05:30 | 6.05 | 5.98
2019-08-29 06:00 | 6.61 | 6.56
2019-08-29 06:30 | 7.18 | 7.11
2019-08-29 07:00 | 8.11 | 8.05
2019-08-29 07:30 | 8.8 | 8.75
2019-08-29 08:00 | 8.62 | 8.57
2019-08-29 08:30 | 7.62 | 7.56
2019-08-29 09:00 | 7 | 6.95
2019-08-29 09:30 | 7.41 | 7.37
2019-08-29 10:00 | 7.95 | 7.9
2019-08-29 10:30 | 7.73 | 7.68
2019-08-29 11:00 | 7.61 | 7.57
2019-08-29 11:30 | 7.24 | 7.21
2019-08-29 12:00 | 7.21 | 7.16
2019-08-29 12:30 | 7.82 | 7.78
2019-08-29 13:00 | 8.06 | 8.02
2019-08-29 13:30 | 7.9 | 7.86
2019-08-29 14:00 | 7.88 | 7.84
2019-08-29 14:30 | 7.55 | 7.49
2019-08-29 15:00 | 7.43 | 7.38
2019-08-29 15:30 | 7.29 | 7.24
2019-08-29 16:00 | 8.46 | 8.43
2019-08-29 16:30 | 9.5 | 9.46
2019-08-29 17:00 | 10.66 | 10.64
2019-08-29 17:30 | 11.79 | 11.78
2019-08-29 18:00 | 12.52 | 12.52
2019-08-29 18:30 | 13.58 | 13.58
2019-08-29 19:00 | 13.94 | 13.94
2019-08-29 19:30 | 13.66 | 13.66
2019-08-29 20:00 | 13.57 | 13.56
2019-08-29 20:30 | 13.46 | 13.46
2019-08-29 21:00 | 13.29 | 13.29
2019-08-29 21:30 | 12.38 | 12.38
2019-08-29 22:00 | 11.21 | 11.2
2019-08-29 22:30 | 10.16 | 10.13
2019-08-29 23:00 | 9.78 | 9.75
2019-08-29 23:30 | 8.78 | 8.74
2019-08-30 | 7.75 | 7.69
2019-08-30 00:30 | 6.8 | 6.73
2019-08-30 01:00 | 6.36 | 6.28
2019-08-30 01:30 | 5.9 | 5.82
2019-08-30 02:00 | 5.56 | 5.48
2019-08-30 02:30 | 5.41 | 5.31
2019-08-30 03:00 | 5.16 | 5.06
2019-08-30 03:30 | 5.23 | 5.12
2019-08-30 04:00 | 5.43 | 5.33
2019-08-30 04:30 | 5.62 | 5.53
2019-08-30 05:00 | 6.01 | 5.94
2019-08-30 05:30 | 6.6 | 6.55
2019-08-30 06:00 | 7.24 | 7.19
2019-08-30 06:30 | 8.09 | 8.03
2019-08-30 07:00 | 8.66 | 8.61
2019-08-30 07:30 | 8.9 | 8.86
2019-08-30 08:00 | 7.57 | 7.53
2019-08-30 08:30 | 5.95 | 5.88
2019-08-30 09:00 | 4.3 | 4.22
2019-08-30 09:30 | 3.6 | 3.51
2019-08-30 10:00 | 2.75 | 2.64
2019-08-30 10:30 | 2.07 | 1.94
2019-08-30 11:00 | 1.72 | 1.6
2019-08-30 11:30 | 1.51 | 1.39
2019-08-30 12:00 | 1.39 | 1.26
2019-08-30 12:30 | 1.35 | 1.2
2019-08-30 13:00 | 1.42 | 1.29
2019-08-30 13:30 | 1.56 | 1.46
2019-08-30 14:00 | 2.1 | 2.01
2019-08-30 14:30 | 2.48 | 2.39
2019-08-30 15:00 | 3.23 | 3.15
2019-08-30 15:30 | 5.14 | 5.08
2019-08-30 16:00 | 5.86 | 5.81
2019-08-30 16:30 | 6.85 | 6.81
2019-08-30 17:00 | 8 | 7.97
2019-08-30 17:30 | 9.22 | 9.19
2019-08-30 18:00 | 10.32 | 10.31
2019-08-30 18:30 | 11.34 | 11.33
2019-08-30 19:00 | 11.5 | 11.5
2019-08-30 19:30 | 11.42 | 11.41
2019-08-30 20:00 | 11.34 | 11.33
2019-08-30 20:30 | 11.4 | 11.39
2019-08-30 21:00 | 11.01 | 11
2019-08-30 21:30 | 10.41 | 10.4
2019-08-30 22:00 | 9.84 | 9.82
2019-08-30 22:30 | 9.52 | 9.49
2019-08-30 23:00 | 9.3 | 9.26
2019-08-30 23:30 | 8.47 | 8.43
2019-08-31 | 7.52 | 7.47
2019-08-31 00:30 | 6.74 | 6.66
2019-08-31 01:00 | 6.25 | 6.17
2019-08-31 01:30 | 5.85 | 5.75
2019-08-31 02:00 | 5.47 | 5.38
2019-08-31 02:30 | 5.39 | 5.28
2019-08-31 03:00 | 5.29 | 5.18
2019-08-31 03:30 | 5.18 | 5.07
2019-08-31 04:00 | 5.17 | 5.05
2019-08-31 04:30 | 5.18 | 5.07
2019-08-31 05:00 | 5.44 | 5.33
2019-08-31 05:30 | 5.68 | 5.58
2019-08-31 06:00 | 5.82 | 5.71
2019-08-31 06:30 | 6.23 | 6.1
2019-08-31 07:00 | 6.36 | 6.24
2019-08-31 07:30 | 6.18 | 6.06
2019-08-31 08:00 | 6.04 | 5.94
2019-08-31 08:30 | 5.67 | 5.57
2019-08-31 09:00 | 5.1 | 5.01
2019-08-31 09:30 | 4.43 | 4.33
2019-08-31 10:00 | 3.89 | 3.81
2019-08-31 10:30 | 3.48 | 3.4
2019-08-31 11:00 | 2.93 | 2.84
2019-08-31 11:30 | 2.46 | 2.38
2019-08-31 12:00 | 3.98 | 3.92
2019-08-31 12:30 | 5.39 | 5.34
2019-08-31 13:00 | 2.85 | 2.78
2019-08-31 13:30 | 4.95 | 4.9
2019-08-31 14:00 | 4.64 | 4.59
2019-08-31 14:30 | 3.53 | 3.46
2019-08-31 15:00 | 4.16 | 4.1
2019-08-31 15:30 | 4.67 | 4.61
2019-08-31 16:00 | 6.58 | 6.53
2019-08-31 16:30 | 7.52 | 7.47
2019-08-31 17:00 | 8.14 | 8.1
2019-08-31 17:30 | 9.25 | 9.22
2019-08-31 18:00 | 10.17 | 10.15
2019-08-31 18:30 | 11 | 10.99
2019-08-31 19:00 | 11.28 | 11.27
2019-08-31 19:30 | 11.09 | 11.08
2019-08-31 20:00 | 11.04 | 11.03
2019-08-31 20:30 | 10.96 | 10.95
2019-08-31 21:00 | 10.56 | 10.54
2019-08-31 21:30 | 10.22 | 10.21
2019-08-31 22:00 | 9.7 | 9.67
2019-08-31 22:30 | 9.46 | 9.43
2019-08-31 23:00 | 9.08 | 9.04
2019-08-31 23:30 | 8.41 | 8.37
2019-09-01 | 7.64 | 7.58
2019-09-01 00:30 | 6.94 | 6.88
2019-09-01 01:00 | 6.45 | 6.37
2019-09-01 01:30 | 6.02 | 5.93
2019-09-01 02:00 | 5.66 | 5.57
2019-09-01 02:30 | 5.5 | 5.41
2019-09-01 03:00 | 5.42 | 5.31
2019-09-01 03:30 | 5.3 | 5.19
2019-09-01 04:00 | 5.22 | 5.1
2019-09-01 04:30 | 5.27 | 5.17
2019-09-01 05:00 | 5.4 | 5.29
2019-09-01 05:30 | 5.54 | 5.44
2019-09-01 06:00 | 5.83 | 5.72
2019-09-01 06:30 | 6.18 | 6.03
2019-09-01 07:00 | 6.32 | 6.18
2019-09-01 07:30 | 6.5 | 6.4
2019-09-01 08:00 | 6.47 | 6.38
2019-09-01 08:30 | 6.34 | 6.27
2019-09-01 09:00 | 6 | 5.93
2019-09-01 09:30 | 5.43 | 5.36
2019-09-01 10:00 | 4.99 | 4.92
2019-09-01 10:30 | 4.4 | 4.35
2019-09-01 11:00 | 4.05 | 3.99
2019-09-01 11:30 | 3.74 | 3.68
2019-09-01 12:00 | 3.51 | 3.46
2019-09-01 12:30 | 3.25 | 3.2
2019-09-01 13:00 | 3.27 | 3.22
2019-09-01 13:30 | 3.28 | 3.23
2019-09-01 14:00 | 3.51 | 3.45
2019-09-01 14:30 | 3.91 | 3.86
2019-09-01 15:00 | 4.46 | 4.41
2019-09-01 15:30 | 5.09 | 5.05
2019-09-01 16:00 | 5.92 | 5.88
2019-09-01 16:30 | 7.14 | 7.11
2019-09-01 17:00 | 8.46 | 8.43
2019-09-01 17:30 | 9.66 | 9.63
2019-09-01 18:00 | 10.6 | 10.58
2019-09-01 18:30 | 11.48 | 11.48
2019-09-01 19:00 | 11.72 | 11.72
2019-09-01 19:30 | 11.38 | 11.37
2019-09-01 20:00 | 11.22 | 11.21
2019-09-01 20:30 | 11.16 | 11.15
2019-09-01 21:00 | 10.78 | 10.77
2019-09-01 21:30 | 10.11 | 10.09
2019-09-01 22:00 | 9.4 | 9.38
2019-09-01 22:30 | 8.92 | 8.89
2019-09-01 23:00 | 8.59 | 8.55
2019-09-01 23:30 | 7.59 | 7.53
2019-09-02 | 6.78 | 6.71
2019-09-02 00:30 | 6.14 | 6.06
2019-09-02 01:00 | 5.77 | 5.68
2019-09-02 01:30 | 5.43 | 5.32
2019-09-02 02:00 | 5.1 | 4.99
2019-09-02 02:30 | 4.94 | 4.82
2019-09-02 03:00 | 5.9 | 5.78
2019-09-02 03:30 | 5.33 | 5.21
2019-09-02 04:00 | 5.35 | 5.23
2019-09-02 04:30 | 5.61 | 5.5
2019-09-02 05:00 | 5.91 | 5.81
2019-09-02 05:30 | 6.72 | 6.65
2019-09-02 06:00 | 7.62 | 7.57
2019-09-02 06:30 | 8.19 | 8.13
2019-09-02 07:00 | 8.53 | 8.47
2019-09-02 07:30 | 8.28 | 8.24
2019-09-02 08:00 | 7.11 | 7.06
2019-09-02 08:30 | 5.72 | 5.66
2019-09-02 09:00 | 4.6 | 4.54
2019-09-02 09:30 | 3.94 | 3.88
2019-09-02 10:00 | 3.25 | 3.19
2019-09-02 10:30 | 2.79 | 2.73
2019-09-02 11:00 | 2.55 | 2.49
2019-09-02 11:30 | 2.4 | 2.36
2019-09-02 12:00 | 2.15 | 2.11
2019-09-02 12:30 | 2.22 | 2.17
2019-09-02 13:00 | 2.32 | 2.29
2019-09-02 13:30 | 2.07 | 2.01
2019-09-02 14:00 | 2.43 | 2.39
2019-09-02 14:30 | 2.9 | 2.86
2019-09-02 15:00 | 3.58 | 3.55
2019-09-02 15:30 | 4.5 | 4.47
2019-09-02 16:00 | 5.74 | 5.72
2019-09-02 16:30 | 7.09 | 7.07
2019-09-02 17:00 | 8.43 | 8.41
2019-09-02 17:30 | 9.64 | 9.62
2019-09-02 18:00 | 10.77 | 10.76
2019-09-02 18:30 | 11.98 | 11.98
2019-09-02 19:00 | 12.24 | 12.24
2019-09-02 19:30 | 11.8 | 11.79
2019-09-02 20:00 | 11.53 | 11.52
2019-09-02 20:30 | 11.34 | 11.33
2019-09-02 21:00 | 10.75 | 10.74
2019-09-02 21:30 | 9.93 | 9.91
2019-09-02 22:00 | 9.21 | 9.19
2019-09-02 22:30 | 8.6 | 8.57
2019-09-02 23:00 | 8.22 | 8.18
2019-09-02 23:30 | 7.39 | 7.33
2019-09-03 | 6.55 | 6.48
2019-09-03 00:30 | 5.77 | 5.69
2019-09-03 01:00 | 5.44 | 5.35
2019-09-03 01:30 | 5.18 | 5.08
2019-09-03 02:00 | 4.89 | 4.79
2019-09-03 02:30 | 4.86 | 4.75
2019-09-03 03:00 | 4.72 | 4.6
2019-09-03 03:30 | 4.8 | 4.68
2019-09-03 04:00 | 4.92 | 4.81
2019-09-03 04:30 | 5.09 | 4.98
2019-09-03 05:00 | 5.6 | 5.5
2019-09-03 05:30 | 6.22 | 6.16
2019-09-03 06:00 | 7.22 | 7.15
2019-09-03 06:30 | 8.32 | 8.26
2019-09-03 07:00 | 8.5 | 8.44
2019-09-03 07:30 | 8.27 | 8.23
2019-09-03 08:00 | 7.25 | 7.21
2019-09-03 08:30 | 5.92 | 5.88
2019-09-03 09:00 | 4.9 | 4.86
2019-09-03 09:30 | 4.1 | 4.05
2019-09-03 10:00 | 3.34 | 3.29
2019-09-03 10:30 | 2.84 | 2.78
2019-09-03 11:00 | 2.51 | 2.45
2019-09-03 11:30 | 2.32 | 2.27
2019-09-03 12:00 | 2.46 | 2.41
2019-09-03 12:30 | 2.64 | 2.61
2019-09-03 13:00 | 2.56 | 2.52
2019-09-03 13:30 | 2.52 | 2.48
2019-09-03 14:00 | 2.61 | 2.56
2019-09-03 14:30 | 3.02 | 2.98
2019-09-03 15:00 | 3.46 | 3.43
2019-09-03 15:30 | 4.39 | 4.36
2019-09-03 16:00 | 5.78 | 5.76
2019-09-03 16:30 | 6.85 | 6.83
2019-09-03 17:00 | 8.26 | 8.24
2019-09-03 17:30 | 9.53 | 9.51
2019-09-03 18:00 | 10.82 | 10.82
2019-09-03 18:30 | 12.09 | 12.09
2019-09-03 19:00 | 12.26 | 12.26
2019-09-03 19:30 | 11.86 | 11.85
2019-09-03 20:00 | 11.75 | 11.75
2019-09-03 20:30 | 11.6 | 11.59
2019-09-03 21:00 | 10.98 | 10.97
2019-09-03 21:30 | 10.02 | 10.01
2019-09-03 22:00 | 9.13 | 9.1
2019-09-03 22:30 | 8.58 | 8.54
2019-09-03 23:00 | 8.15 | 8.11
2019-09-03 23:30 | 7.36 | 7.31
2019-09-04 | 6.39 | 6.31
2019-09-04 00:30 | 5.74 | 5.64
2019-09-04 01:00 | 5.47 | 5.37
2019-09-04 01:30 | 5.16 | 5.05
2019-09-04 02:00 | 4.92 | 4.82
2019-09-04 02:30 | 4.78 | 4.66
2019-09-04 03:00 | 4.71 | 4.58
2019-09-04 03:30 | 5.67 | 5.55
2019-09-04 04:00 | 5.36 | 5.24
2019-09-04 04:30 | 5.57 | 5.46
2019-09-04 05:00 | 5.9 | 5.8
2019-09-04 05:30 | 6.51 | 6.44
2019-09-04 06:00 | 7.2 | 7.13
2019-09-04 06:30 | 7.83 | 7.76
2019-09-04 07:00 | 8.15 | 8.1
2019-09-04 07:30 | 7.86 | 7.82
2019-09-04 08:00 | 6.72 | 6.66
2019-09-04 08:30 | 5.41 | 5.34
2019-09-04 09:00 | 4.24 | 4.17
2019-09-04 09:30 | 3.26 | 3.18
2019-09-04 10:00 | 2.71 | 2.63
2019-09-04 10:30 | 2.47 | 2.41
2019-09-04 11:00 | 2.25 | 2.21
2019-09-04 11:30 | 2.09 | 2.05
2019-09-04 12:00 | 2.21 | 2.18
2019-09-04 12:30 | 2.5 | 2.48
2019-09-04 13:00 | 2.67 | 2.66
2019-09-04 13:30 | 2.9 | 2.88
2019-09-04 14:00 | 3.36 | 3.34
2019-09-04 14:30 | 3.74 | 3.73
2019-09-04 15:00 | 4.52 | 4.51
2019-09-04 15:30 | 5.7 | 5.69
2019-09-04 16:00 | 6.98 | 6.97
2019-09-04 16:30 | 8.15 | 8.15
2019-09-04 17:00 | 9.5 | 9.5
2019-09-04 17:30 | 10.44 | 10.43
2019-09-04 18:00 | 11.27 | 11.27
2019-09-04 18:30 | 12.29 | 12.29
2019-09-04 19:00 | 12.46 | 12.46
2019-09-04 19:30 | 11.88 | 11.88
2019-09-04 20:00 | 11.94 | 11.93
2019-09-04 20:30 | 11.92 | 11.92
2019-09-04 21:00 | 11.41 | 11.4
2019-09-04 21:30 | 10.28 | 10.27
2019-09-04 22:00 | 9.34 | 9.32
2019-09-04 22:30 | 8.65 | 8.63
2019-09-04 23:00 | 8.2 | 8.16
2019-09-04 23:30 | 7.21 | 7.16
2019-09-05 | 6.37 | 6.3
2019-09-05 00:30 | 5.66 | 5.58
2019-09-05 01:00 | 5.36 | 5.27
2019-09-05 01:30 | 5.05 | 4.95
2019-09-05 02:00 | 4.88 | 4.77
2019-09-05 02:30 | 4.78 | 4.67
2019-09-05 03:00 | 4.56 | 4.43
2019-09-05 03:30 | 4.67 | 4.54
2019-09-05 04:00 | 4.71 | 4.59
2019-09-05 04:30 | 4.85 | 4.73
2019-09-05 05:00 | 5.23 | 5.13
2019-09-05 05:30 | 5.83 | 5.75
2019-09-05 06:00 | 6.3 | 6.21
2019-09-05 06:30 | 6.95 | 6.85
2019-09-05 07:00 | 7.36 | 7.28
2019-09-05 07:30 | 7.26 | 7.2
2019-09-05 08:00 | 6.32 | 6.26
2019-09-05 08:30 | 4.88 | 4.81
2019-09-05 09:00 | 3.91 | 3.84
2019-09-05 09:30 | 3.2 | 3.13
2019-09-05 10:00 | 2.73 | 2.67
2019-09-05 10:30 | 2.33 | 2.28
2019-09-05 11:00 | 2.16 | 2.12
2019-09-05 11:30 | 2.01 | 1.97
2019-09-05 12:00 | 2.04 | 2.02
2019-09-05 12:30 | 2.35 | 2.32
2019-09-05 13:00 | 2.71 | 2.69
2019-09-05 13:30 | 3.14 | 3.12
2019-09-05 14:00 | 3.7 | 3.68
2019-09-05 14:30 | 5.42 | 5.42
2019-09-05 15:00 | 6.34 | 6.33
2019-09-05 15:30 | 7.33 | 7.33
2019-09-05 16:00 | 8.31 | 8.3
2019-09-05 16:30 | 9.41 | 9.41
2019-09-05 17:00 | 9.57 | 9.57
2019-09-05 17:30 | 10.26 | 10.25
2019-09-05 18:00 | 11.07 | 11.07
2019-09-05 18:30 | 12.24 | 12.24
2019-09-05 19:00 | 12.63 | 12.62
2019-09-05 19:30 | 11.92 | 11.91
2019-09-05 20:00 | 11.49 | 11.49
2019-09-05 20:30 | 11.2 | 11.2
2019-09-05 21:00 | 10.66 | 10.65
2019-09-05 21:30 | 9.9 | 9.89
2019-09-05 22:00 | 9.09 | 9.07
2019-09-05 22:30 | 8.47 | 8.44
2019-09-05 23:00 | 8.19 | 8.15
2019-09-05 23:30 | 7.3 | 7.26
2019-09-06 | 6.36 | 6.3
2019-09-06 00:30 | 5.68 | 5.59
2019-09-06 01:00 | 5.31 | 5.22
2019-09-06 01:30 | 5.02 | 4.92
2019-09-06 02:00 | 4.76 | 4.65
2019-09-06 02:30 | 4.71 | 4.59
2019-09-06 03:00 | 4.59 | 4.46
2019-09-06 03:30 | 4.62 | 4.49
2019-09-06 04:00 | 4.66 | 4.53
2019-09-06 04:30 | 4.83 | 4.71
2019-09-06 05:00 | 5.12 | 5.01
2019-09-06 05:30 | 5.61 | 5.53
2019-09-06 06:00 | 6.06 | 5.96
2019-09-06 06:30 | 6.74 | 6.62
2019-09-06 07:00 | 6.89 | 6.79
2019-09-06 07:30 | 6.65 | 6.57
2019-09-06 08:00 | 5.6 | 5.51
2019-09-06 08:30 | 4.27 | 4.15
2019-09-06 09:00 | 3.2 | 3.1
2019-09-06 09:30 | 2.48 | 2.39
2019-09-06 10:00 | 2.05 | 1.99
2019-09-06 10:30 | 1.65 | 1.59
2019-09-06 11:00 | 1.42 | 1.36
2019-09-06 11:30 | 1.47 | 1.42
2019-09-06 12:00 | 1.76 | 1.71
2019-09-06 12:30 | 2.14 | 2.09
2019-09-06 13:00 | 2.78 | 2.74
2019-09-06 13:30 | 3.1 | 3.06
2019-09-06 14:00 | 3.98 | 3.95
2019-09-06 14:30 | 4.78 | 4.76
2019-09-06 15:00 | 5.4 | 5.38
2019-09-06 15:30 | 6.6 | 6.58
2019-09-06 16:00 | 8.07 | 8.06
2019-09-06 16:30 | 9.36 | 9.34
2019-09-06 17:00 | 10.31 | 10.3
2019-09-06 17:30 | 10.94 | 10.93
2019-09-06 18:00 | 11.36 | 11.35
2019-09-06 18:30 | 12.06 | 12.05
2019-09-06 19:00 | 12.34 | 12.34
2019-09-06 19:30 | 11.89 | 11.88
2019-09-06 20:00 | 11.69 | 11.68
2019-09-06 20:30 | 11.23 | 11.22
2019-09-06 21:00 | 10.68 | 10.67
2019-09-06 21:30 | 9.89 | 9.88
2019-09-06 22:00 | 9 | 8.99
2019-09-06 22:30 | 8.77 | 8.75
2019-09-06 23:00 | 8.54 | 8.51
2019-09-06 23:30 | 7.68 | 7.65
2019-09-07 | 6.87 | 6.83
2019-09-07 00:30 | 6.08 | 6.02
2019-09-07 01:00 | 5.85 | 5.79
2019-09-07 01:30 | 5.52 | 5.45
2019-09-07 02:00 | 5.18 | 5.11
2019-09-07 02:30 | 5.11 | 5.03
2019-09-07 03:00 | 4.78 | 4.69
2019-09-07 03:30 | 4.72 | 4.62
2019-09-07 04:00 | 4.78 | 4.68
2019-09-07 04:30 | 4.76 | 4.65
2019-09-07 05:00 | 4.69 | 4.58
2019-09-07 05:30 | 4.83 | 4.72
2019-09-07 06:00 | 4.9 | 4.74
2019-09-07 06:30 | 5.2 | 5.02
2019-09-07 07:00 | 4.97 | 4.78
2019-09-07 07:30 | 5.05 | 4.89
2019-09-07 08:00 | 4.74 | 4.59
2019-09-07 08:30 | 4.44 | 4.31
2019-09-07 09:00 | 4.11 | 4.01
2019-09-07 09:30 | 3.83 | 3.75
2019-09-07 10:00 | 3.36 | 3.29
2019-09-07 10:30 | 3.12 | 3.05
2019-09-07 11:00 | 2.93 | 2.87
2019-09-07 11:30 | 2.6 | 2.55
2019-09-07 12:00 | 2.46 | 2.41
2019-09-07 12:30 | 2.64 | 2.6
2019-09-07 13:00 | 2.5 | 2.45
2019-09-07 13:30 | 2.68 | 2.63
2019-09-07 14:00 | 3.09 | 3.05
2019-09-07 14:30 | 3.57 | 3.54
2019-09-07 15:00 | 4.21 | 4.18
2019-09-07 15:30 | 4.97 | 4.94
2019-09-07 16:00 | 6.01 | 5.99
2019-09-07 16:30 | 6.98 | 6.96
2019-09-07 17:00 | 8.05 | 8.02
2019-09-07 17:30 | 9.01 | 8.98
2019-09-07 18:00 | 9.82 | 9.81
2019-09-07 18:30 | 10.56 | 10.55
2019-09-07 19:00 | 10.66 | 10.66
2019-09-07 19:30 | 10.32 | 10.32
2019-09-07 20:00 | 10.2 | 10.19
2019-09-07 20:30 | 10.15 | 10.14
2019-09-07 21:00 | 9.66 | 9.64
2019-09-07 21:30 | 9.06 | 9.03
2019-09-07 22:00 | 8.59 | 8.55
2019-09-07 22:30 | 8.38 | 8.34
2019-09-07 23:00 | 8.28 | 8.23
2019-09-07 23:30 | 7.5 | 7.44
2019-09-08 | 6.66 | 6.58
2019-09-08 00:30 | 6.02 | 5.93
2019-09-08 01:00 | 5.7 | 5.61
2019-09-08 01:30 | 5.3 | 5.19
2019-09-08 02:00 | 4.94 | 4.82
2019-09-08 02:30 | 4.73 | 4.61
2019-09-08 03:00 | 4.58 | 4.44
2019-09-08 03:30 | 4.59 | 4.46
2019-09-08 04:00 | 4.56 | 4.42
2019-09-08 04:30 | 4.57 | 4.43
2019-09-08 05:00 | 4.73 | 4.6
2019-09-08 05:30 | 4.79 | 4.66
2019-09-08 06:00 | 4.91 | 4.72
2019-09-08 06:30 | 5.04 | 4.81
2019-09-08 07:00 | 4.84 | 4.61
2019-09-08 07:30 | 4.66 | 4.46
2019-09-08 08:00 | 4.53 | 4.35
2019-09-08 08:30 | 4.39 | 4.25
2019-09-08 09:00 | 4.24 | 4.12
2019-09-08 09:30 | 3.81 | 3.71
2019-09-08 10:00 | 3.46 | 3.37
2019-09-08 10:30 | 3.02 | 2.93
2019-09-08 11:00 | 2.8 | 2.71
2019-09-08 11:30 | 2.71 | 2.65
2019-09-08 12:00 | 2.5 | 2.45
2019-09-08 12:30 | 2.48 | 2.42
2019-09-08 13:00 | 2.57 | 2.51
2019-09-08 13:30 | 2.72 | 2.67
2019-09-08 14:00 | 2.99 | 2.93
2019-09-08 14:30 | 3.41 | 3.35
2019-09-08 15:00 | 3.99 | 3.93
2019-09-08 15:30 | 4.8 | 4.75
2019-09-08 16:00 | 5.66 | 5.6
2019-09-08 16:30 | 6.95 | 6.9
2019-09-08 17:00 | 8.46 | 8.42
2019-09-08 17:30 | 9.74 | 9.72
2019-09-08 18:00 | 10.8 | 10.78
2019-09-08 18:30 | 11.8 | 11.79
2019-09-08 19:00 | 11.84 | 11.83
2019-09-08 19:30 | 11.4 | 11.39
2019-09-08 20:00 | 11.21 | 11.19
2019-09-08 20:30 | 11.01 | 10.99
2019-09-08 21:00 | 10.48 | 10.46
2019-09-08 21:30 | 9.85 | 9.83
2019-09-08 22:00 | 9.12 | 9.1
2019-09-08 22:30 | 8.39 | 8.35
2019-09-08 23:00 | 8.1 | 8.06
2019-09-08 23:30 | 7.27 | 7.21
2019-09-09 | 6.35 | 6.28
2019-09-09 00:30 | 5.73 | 5.65
2019-09-09 01:00 | 5.37 | 5.28
2019-09-09 01:30 | 4.93 | 4.82
2019-09-09 02:00 | 4.73 | 4.62
2019-09-09 02:30 | 4.55 | 4.43
2019-09-09 03:00 | 4.45 | 4.33
2019-09-09 03:30 | 4.56 | 4.43
2019-09-09 04:00 | 4.61 | 4.49
2019-09-09 04:30 | 4.83 | 4.71
2019-09-09 05:00 | 5.13 | 5.02
2019-09-09 05:30 | 5.63 | 5.55
2019-09-09 06:00 | 6.46 | 6.36
2019-09-09 06:30 | 7.19 | 7.1
2019-09-09 07:00 | 7.31 | 7.23
2019-09-09 07:30 | 6.91 | 6.84
2019-09-09 08:00 | 6.21 | 6.14
2019-09-09 08:30 | 4.71 | 4.63
2019-09-09 09:00 | 3.66 | 3.57
2019-09-09 09:30 | 2.98 | 2.88
2019-09-09 10:00 | 2.48 | 2.37
2019-09-09 10:30 | 2.17 | 2.07
2019-09-09 11:00 | 1.88 | 1.79
2019-09-09 11:30 | 1.78 | 1.68
2019-09-09 12:00 | 1.66 | 1.54
2019-09-09 12:30 | 1.72 | 1.61
2019-09-09 13:00 | 1.67 | 1.58
2019-09-09 13:30 | 1.52 | 1.36
2019-09-09 14:00 | 1.75 | 1.62
2019-09-09 14:30 | 2.08 | 1.97
2019-09-09 15:00 | 2.63 | 2.55
2019-09-09 15:30 | 3.72 | 3.66
2019-09-09 16:00 | 5.07 | 5.01
2019-09-09 16:30 | 6.49 | 6.44
2019-09-09 17:00 | 8.22 | 8.18
2019-09-09 17:30 | 9.86 | 9.83
2019-09-09 18:00 | 10.9 | 10.88
2019-09-09 18:30 | 12.04 | 12.03
2019-09-09 19:00 | 12.56 | 12.56
2019-09-09 19:30 | 12.17 | 12.16
2019-09-09 20:00 | 11.89 | 11.88
2019-09-09 20:30 | 11.78 | 11.77
2019-09-09 21:00 | 11.3 | 11.29
2019-09-09 21:30 | 10.23 | 10.21
2019-09-09 22:00 | 9.27 | 9.23
2019-09-09 22:30 | 8.7 | 8.66
2019-09-09 23:00 | 8.29 | 8.24
2019-09-09 23:30 | 7.46 | 7.4
2019-09-10 | 6.61 | 6.54
2019-09-10 00:30 | 5.92 | 5.83
2019-09-10 01:00 | 5.53 | 5.43
2019-09-10 01:30 | 5.16 | 5.05
2019-09-10 02:00 | 4.87 | 4.75
2019-09-10 02:30 | 4.8 | 4.67
2019-09-10 03:00 | 4.75 | 4.62
2019-09-10 03:30 | 4.87 | 4.74
2019-09-10 04:00 | 4.89 | 4.77
2019-09-10 04:30 | 5.19 | 5.07
2019-09-10 05:00 | 5.59 | 5.49
2019-09-10 05:30 | 6.2 | 6.13
2019-09-10 06:00 | 6.76 | 6.67
2019-09-10 06:30 | 7.64 | 7.55
2019-09-10 07:00 | 8.15 | 8.08
2019-09-10 07:30 | 7.9 | 7.83
2019-09-10 08:00 | 6.83 | 6.75
2019-09-10 08:30 | 5.34 | 5.24
2019-09-10 09:00 | 4.2 | 4.09
2019-09-10 09:30 | 3.48 | 3.36
2019-09-10 10:00 | 3.19 | 3.08
2019-09-10 10:30 | 2.86 | 2.74
2019-09-10 11:00 | 2.46 | 2.36
2019-09-10 11:30 | 2.27 | 2.16
2019-09-10 12:00 | 2.35 | 2.26
2019-09-10 12:30 | 2.45 | 2.36
2019-09-10 13:00 | 2.58 | 2.5
2019-09-10 13:30 | 3.08 | 3.01
2019-09-10 14:00 | 2.45 | 2.35
2019-09-10 14:30 | 2.72 | 2.62
2019-09-10 15:00 | 4.89 | 4.83
2019-09-10 15:30 | 5.8 | 5.76
2019-09-10 16:00 | 6.49 | 6.45
2019-09-10 16:30 | 7.52 | 7.47
2019-09-10 17:00 | 9.2 | 9.16
2019-09-10 17:30 | 10.61 | 10.58
2019-09-10 18:00 | 11.92 | 11.91
2019-09-10 18:30 | 13.04 | 13.04
2019-09-10 19:00 | 13.3 | 13.3
2019-09-10 19:30 | 12.92 | 12.92
2019-09-10 20:00 | 12.52 | 12.51
2019-09-10 20:30 | 12.67 | 12.66
2019-09-10 21:00 | 12.28 | 12.27
2019-09-10 21:30 | 11.46 | 11.45
2019-09-10 22:00 | 10.36 | 10.34
2019-09-10 22:30 | 9.61 | 9.58
2019-09-10 23:00 | 9.07 | 9.03
2019-09-10 23:30 | 8.21 | 8.16
2019-09-11 | 7.28 | 7.21
2019-09-11 00:30 | 6.61 | 6.53
2019-09-11 01:00 | 6.21 | 6.13
2019-09-11 01:30 | 5.86 | 5.76
2019-09-11 02:00 | 5.55 | 5.44
2019-09-11 02:30 | 5.51 | 5.4
2019-09-11 03:00 | 5.27 | 5.15
2019-09-11 03:30 | 5.42 | 5.31
2019-09-11 04:00 | 5.55 | 5.44
2019-09-11 04:30 | 5.72 | 5.62
2019-09-11 05:00 | 6.05 | 5.95
2019-09-11 05:30 | 6.75 | 6.68
2019-09-11 06:00 | 7.77 | 7.69
2019-09-11 06:30 | 8.69 | 8.62
2019-09-11 07:00 | 8.77 | 8.72
2019-09-11 07:30 | 8.22 | 8.17
2019-09-11 08:00 | 7.14 | 7.08
2019-09-11 08:30 | 5.53 | 5.46
2019-09-11 09:00 | 4.33 | 4.26
2019-09-11 09:30 | 3.57 | 3.48
2019-09-11 10:00 | 3.04 | 2.95
2019-09-11 10:30 | 3.35 | 3.27
2019-09-11 11:00 | 4.65 | 4.59
2019-09-11 11:30 | 4.85 | 4.79
2019-09-11 12:00 | 2.43 | 2.32
2019-09-11 12:30 | 2.9 | 2.82
2019-09-11 13:00 | 3.47 | 3.42
2019-09-11 13:30 | 2.95 | 2.88
2019-09-11 14:00 | 3.29 | 3.22
2019-09-11 14:30 | 4 | 3.94
2019-09-11 15:00 | 5.26 | 5.21
2019-09-11 15:30 | 5.34 | 5.29
2019-09-11 16:00 | 5.11 | 5.06
2019-09-11 16:30 | 6.51 | 6.46
2019-09-11 17:00 | 8.24 | 8.21
2019-09-11 17:30 | 9.96 | 9.93
2019-09-11 18:00 | 11.09 | 11.08
2019-09-11 18:30 | 12.44 | 12.44
2019-09-11 19:00 | 12.87 | 12.87
2019-09-11 19:30 | 12.53 | 12.53
2019-09-11 20:00 | 12.32 | 12.32
2019-09-11 20:30 | 12.54 | 12.54
2019-09-11 21:00 | 11.9 | 11.9
2019-09-11 21:30 | 11.08 | 11.07
2019-09-11 22:00 | 10.24 | 10.22
2019-09-11 22:30 | 9.52 | 9.5
2019-09-11 23:00 | 8.79 | 8.76
2019-09-11 23:30 | 7.95 | 7.91
2019-09-12 | 6.96 | 6.9
2019-09-12 00:30 | 6.24 | 6.16
2019-09-12 01:00 | 5.89 | 5.81
2019-09-12 01:30 | 5.46 | 5.37
2019-09-12 02:00 | 5.25 | 5.14
2019-09-12 02:30 | 5.06 | 4.95
2019-09-12 03:00 | 5.01 | 4.9
2019-09-12 03:30 | 5.06 | 4.94
2019-09-12 04:00 | 5.2 | 5.1
2019-09-12 04:30 | 5.38 | 5.27
2019-09-12 05:00 | 5.82 | 5.73
2019-09-12 05:30 | 6.58 | 6.52
2019-09-12 06:00 | 7.07 | 6.99
2019-09-12 06:30 | 7.86 | 7.79
2019-09-12 07:00 | 8.16 | 8.1
2019-09-12 07:30 | 7.71 | 7.66
2019-09-12 08:00 | 6.58 | 6.52
2019-09-12 08:30 | 5.04 | 4.97
2019-09-12 09:00 | 3.74 | 3.64
2019-09-12 09:30 | 2.99 | 2.9
2019-09-12 10:00 | 2.39 | 2.28
2019-09-12 10:30 | 1.86 | 1.74
2019-09-12 11:00 | 1.31 | 1.09
2019-09-12 11:30 | 1.07 | 0.85
2019-09-12 12:00 | 1.07 | 0.86
2019-09-12 12:30 | 1.05 | 0.83
2019-09-12 13:00 | 1.13 | 0.93
2019-09-12 13:30 | 1.28 | 1.15
2019-09-12 14:00 | 1.61 | 1.5
2019-09-12 14:30 | 2.01 | 1.91
2019-09-12 15:00 | 2.61 | 2.52
2019-09-12 15:30 | 3.63 | 3.57
2019-09-12 16:00 | 4.98 | 4.93
2019-09-12 16:30 | 6.42 | 6.38
2019-09-12 17:00 | 7.81 | 7.77
2019-09-12 17:30 | 9.03 | 9
2019-09-12 18:00 | 10.21 | 10.2
2019-09-12 18:30 | 11.48 | 11.47
2019-09-12 19:00 | 11.91 | 11.91
2019-09-12 19:30 | 11.43 | 11.43
2019-09-12 20:00 | 11.38 | 11.38
2019-09-12 20:30 | 11.42 | 11.42
2019-09-12 21:00 | 10.9 | 10.89
2019-09-12 21:30 | 9.99 | 9.98
2019-09-12 22:00 | 9.2 | 9.18
2019-09-12 22:30 | 8.68 | 8.65
2019-09-12 23:00 | 8.4 | 8.36
2019-09-12 23:30 | 7.63 | 7.58
2019-09-13 | 6.6 | 6.54
2019-09-13 00:30 | 5.94 | 5.86
2019-09-13 01:00 | 5.6 | 5.52
2019-09-13 01:30 | 5.29 | 5.2
2019-09-13 02:00 | 5.05 | 4.94
2019-09-13 02:30 | 4.85 | 4.73
2019-09-13 03:00 | 4.71 | 4.58
2019-09-13 03:30 | 4.9 | 4.79
2019-09-13 04:00 | 4.92 | 4.8
2019-09-13 04:30 | 5.09 | 4.98
2019-09-13 05:00 | 5.51 | 5.41
2019-09-13 05:30 | 6.12 | 6.04
2019-09-13 06:00 | 6.5 | 6.41
2019-09-13 06:30 | 7.2 | 7.1
2019-09-13 07:00 | 7.24 | 7.16
2019-09-13 07:30 | 6.87 | 6.8
2019-09-13 08:00 | 5.84 | 5.76
2019-09-13 08:30 | 4.49 | 4.4
2019-09-13 09:00 | 3.27 | 3.15
2019-09-13 09:30 | 2.48 | 2.36
2019-09-13 10:00 | 1.97 | 1.84
2019-09-13 10:30 | 1.63 | 1.5
2019-09-13 11:00 | 1.63 | 1.52
2019-09-13 11:30 | 2.34 | 2.25
2019-09-13 12:00 | 2.11 | 2.01
2019-09-13 12:30 | 1.2 | 1.1
2019-09-13 13:00 | 1.41 | 1.35
2019-09-13 13:30 | 1.67 | 1.62
2019-09-13 14:00 | 2.12 | 2.08
2019-09-13 14:30 | 2.77 | 2.74
2019-09-13 15:00 | 3.5 | 3.48
2019-09-13 15:30 | 4.93 | 4.91
2019-09-13 16:00 | 6.2 | 6.18
2019-09-13 16:30 | 7.3 | 7.27
2019-09-13 17:00 | 8.42 | 8.4
2019-09-13 17:30 | 9.34 | 9.32
2019-09-13 18:00 | 9.78 | 9.76
2019-09-13 18:30 | 10.74 | 10.74
2019-09-13 19:00 | 11.32 | 11.31
2019-09-13 19:30 | 10.89 | 10.89
2019-09-13 20:00 | 10.7 | 10.69
2019-09-13 20:30 | 10.67 | 10.66
2019-09-13 21:00 | 10.32 | 10.31
2019-09-13 21:30 | 9.49 | 9.47
2019-09-13 22:00 | 9.02 | 8.99
2019-09-13 22:30 | 8.73 | 8.7
2019-09-13 23:00 | 8.61 | 8.57
2019-09-13 23:30 | 7.72 | 7.67
2019-09-14 | 6.95 | 6.89
2019-09-14 00:30 | 6.16 | 6.08
2019-09-14 01:00 | 5.92 | 5.84
2019-09-14 01:30 | 5.56 | 5.46
2019-09-14 02:00 | 5.2 | 5.1
2019-09-14 02:30 | 4.9 | 4.79
2019-09-14 03:00 | 4.83 | 4.71
2019-09-14 03:30 | 4.82 | 4.71
2019-09-14 04:00 | 4.9 | 4.78
2019-09-14 04:30 | 4.94 | 4.83
2019-09-14 05:00 | 5.04 | 4.92
2019-09-14 05:30 | 5.21 | 5.1
2019-09-14 06:00 | 5.37 | 5.21
2019-09-14 06:30 | 5.68 | 5.51
2019-09-14 07:00 | 5.59 | 5.44
2019-09-14 07:30 | 5.36 | 5.23
2019-09-14 08:00 | 4.9 | 4.77
2019-09-14 08:30 | 4.65 | 4.53
2019-09-14 09:00 | 4.15 | 4.06
2019-09-14 09:30 | 3.75 | 3.67
2019-09-14 10:00 | 3.22 | 3.14
2019-09-14 10:30 | 2.82 | 2.76
2019-09-14 11:00 | 2.53 | 2.46
2019-09-14 11:30 | 2.32 | 2.27
2019-09-14 12:00 | 2.26 | 2.2
2019-09-14 12:30 | 2.39 | 2.35
2019-09-14 13:00 | 2.42 | 2.37
2019-09-14 13:30 | 2.71 | 2.67
2019-09-14 14:00 | 3.21 | 3.18
2019-09-14 14:30 | 3.73 | 3.7
2019-09-14 15:00 | 4.43 | 4.4
2019-09-14 15:30 | 5.34 | 5.32
2019-09-14 16:00 | 6.33 | 6.32
2019-09-14 16:30 | 7.35 | 7.34
2019-09-14 17:00 | 8.46 | 8.45
2019-09-14 17:30 | 9.24 | 9.23
2019-09-14 18:00 | 9.87 | 9.86
2019-09-14 18:30 | 10.66 | 10.66
2019-09-14 19:00 | 10.97 | 10.97
2019-09-14 19:30 | 10.51 | 10.5
2019-09-14 20:00 | 10.38 | 10.37
2019-09-14 20:30 | 10.25 | 10.24
2019-09-14 21:00 | 9.63 | 9.62
2019-09-14 21:30 | 9.15 | 9.13
2019-09-14 22:00 | 8.64 | 8.61
2019-09-14 22:30 | 8.47 | 8.44
2019-09-14 23:00 | 8.27 | 8.23
2019-09-14 23:30 | 7.59 | 7.55
2019-09-15 | 6.71 | 6.65
2019-09-15 00:30 | 5.96 | 5.87
2019-09-15 01:00 | 5.62 | 5.52
2019-09-15 01:30 | 5.21 | 5.11
2019-09-15 02:00 | 4.98 | 4.87
2019-09-15 02:30 | 4.76 | 4.63
2019-09-15 03:00 | 4.63 | 4.5
2019-09-15 03:30 | 4.62 | 4.49
2019-09-15 04:00 | 4.64 | 4.51
2019-09-15 04:30 | 4.65 | 4.52
2019-09-15 05:00 | 4.68 | 4.54
2019-09-15 05:30 | 4.91 | 4.79
2019-09-15 06:00 | 4.9 | 4.71
2019-09-15 06:30 | 5.01 | 4.79
2019-09-15 07:00 | 4.76 | 4.53
2019-09-15 07:30 | 4.69 | 4.51
2019-09-15 08:00 | 4.64 | 4.48
2019-09-15 08:30 | 4.44 | 4.3
2019-09-15 09:00 | 4.23 | 4.11
2019-09-15 09:30 | 3.9 | 3.8
2019-09-15 10:00 | 3.4 | 3.31
2019-09-15 10:30 | 3.02 | 2.93
2019-09-15 11:00 | 2.69 | 2.62
2019-09-15 11:30 | 2.52 | 2.45
2019-09-15 12:00 | 2.42 | 2.36
2019-09-15 12:30 | 2.51 | 2.46
2019-09-15 13:00 | 2.64 | 2.6
2019-09-15 13:30 | 2.84 | 2.79
2019-09-15 14:00 | 3.27 | 3.23
2019-09-15 14:30 | 3.72 | 3.68
2019-09-15 15:00 | 4.28 | 4.24
2019-09-15 15:30 | 5.12 | 5.08
2019-09-15 16:00 | 6.03 | 5.99
2019-09-15 16:30 | 7.36 | 7.32
2019-09-15 17:00 | 8.58 | 8.55
2019-09-15 17:30 | 9.73 | 9.71
2019-09-15 18:00 | 10.63 | 10.61
2019-09-15 18:30 | 11.57 | 11.56
2019-09-15 19:00 | 11.82 | 11.81
2019-09-15 19:30 | 11.38 | 11.37
2019-09-15 20:00 | 11.19 | 11.18
2019-09-15 20:30 | 10.99 | 10.98
2019-09-15 21:00 | 10.35 | 10.33
2019-09-15 21:30 | 9.42 | 9.39
2019-09-15 22:00 | 8.79 | 8.75
2019-09-15 22:30 | 8.33 | 8.29
2019-09-15 23:00 | 8 | 7.95
2019-09-15 23:30 | 7.03 | 6.98
2019-09-16 | 6.18 | 6.1
2019-09-16 00:30 | 5.56 | 5.46
2019-09-16 01:00 | 5.26 | 5.16
2019-09-16 01:30 | 4.97 | 4.86
2019-09-16 02:00 | 4.69 | 4.57
2019-09-16 02:30 | 4.56 | 4.43
2019-09-16 03:00 | 4.53 | 4.39
2019-09-16 03:30 | 4.57 | 4.43
2019-09-16 04:00 | 4.66 | 4.53
2019-09-16 04:30 | 4.86 | 4.74
2019-09-16 05:00 | 5.25 | 5.14
2019-09-16 05:30 | 5.73 | 5.64
2019-09-16 06:00 | 6.13 | 6.01
2019-09-16 06:30 | 6.82 | 6.71
2019-09-16 07:00 | 6.69 | 6.59
2019-09-16 07:30 | 6.3 | 6.21
2019-09-16 08:00 | 5.24 | 5.14
2019-09-16 08:30 | 3.96 | 3.85
2019-09-16 09:00 | 2.98 | 2.86
2019-09-16 09:30 | 2.26 | 2.11
2019-09-16 10:00 | 1.68 | 1.52
2019-09-16 10:30 | 1.34 | 1.17
2019-09-16 11:00 | 1.11 | 0.95
2019-09-16 11:30 | 1.11 | 0.96
2019-09-16 12:00 | 1.11 | 0.99
2019-09-16 12:30 | 1.26 | 1.2
2019-09-16 13:00 | 1.53 | 1.5
2019-09-16 13:30 | 1.88 | 1.85
2019-09-16 14:00 | 2.37 | 2.34
2019-09-16 14:30 | 3.13 | 3.11
2019-09-16 15:00 | 4.01 | 4
2019-09-16 15:30 | 5.2 | 5.19
2019-09-16 16:00 | 6.46 | 6.45
2019-09-16 16:30 | 7.72 | 7.71
2019-09-16 17:00 | 9.18 | 9.16
2019-09-16 17:30 | 10.31 | 10.3
2019-09-16 18:00 | 11.34 | 11.33
2019-09-16 18:30 | 12.39 | 12.39
2019-09-16 19:00 | 12.87 | 12.87
2019-09-16 19:30 | 12.26 | 12.26
2019-09-16 20:00 | 11.73 | 11.73
2019-09-16 20:30 | 11.42 | 11.42
2019-09-16 21:00 | 11.05 | 11.04
2019-09-16 21:30 | 10.35 | 10.34
2019-09-16 22:00 | 9.1 | 9.08
2019-09-16 22:30 | 8.29 | 8.25
2019-09-16 23:00 | 7.92 | 7.87
2019-09-16 23:30 | 7 | 6.94
2019-09-17 | 6.14 | 6.06
2019-09-17 00:30 | 5.56 | 5.48
2019-09-17 01:00 | 5.2 | 5.1
2019-09-17 01:30 | 4.98 | 4.88
2019-09-17 02:00 | 4.74 | 4.63
2019-09-17 02:30 | 4.6 | 4.48
2019-09-17 03:00 | 4.46 | 4.34
2019-09-17 03:30 | 4.52 | 4.39
2019-09-17 04:00 | 4.59 | 4.45
2019-09-17 04:30 | 4.82 | 4.7
2019-09-17 05:00 | 5.11 | 5.01
2019-09-17 05:30 | 5.53 | 5.44
2019-09-17 06:00 | 6.14 | 6.03
2019-09-17 06:30 | 6.85 | 6.75
2019-09-17 07:00 | 6.89 | 6.8
2019-09-17 07:30 | 6.38 | 6.31
2019-09-17 08:00 | 5.51 | 5.42
2019-09-17 08:30 | 4.69 | 4.6
2019-09-17 09:00 | 3.75 | 3.67
2019-09-17 09:30 | 2.99 | 2.92
2019-09-17 10:00 | 2.71 | 2.66
2019-09-17 10:30 | 1.95 | 1.89
2019-09-17 11:00 | 1.78 | 1.75
2019-09-17 11:30 | 2.28 | 2.26
2019-09-17 12:00 | 1.95 | 1.92
2019-09-17 12:30 | 2.07 | 2.06
2019-09-17 13:00 | 2.41 | 2.4
2019-09-17 13:30 | 3.23 | 3.22
2019-09-17 14:00 | 3.41 | 3.4
2019-09-17 14:30 | 4.32 | 4.32
2019-09-17 15:00 | 6.4 | 6.4
2019-09-17 15:30 | 7.2 | 7.19
2019-09-17 16:00 | 8.11 | 8.1
2019-09-17 16:30 | 9.04 | 9.03
2019-09-17 17:00 | 10.74 | 10.74
2019-09-17 17:30 | 12.24 | 12.24
2019-09-17 18:00 | 12.79 | 12.78
2019-09-17 18:30 | 12.63 | 12.63
2019-09-17 19:00 | 12.77 | 12.77
2019-09-17 19:30 | 12.25 | 12.25
2019-09-17 20:00 | 11.66 | 11.65
2019-09-17 20:30 | 11.02 | 11.01
2019-09-17 21:00 | 10.28 | 10.27
2019-09-17 21:30 | 9.47 | 9.45
2019-09-17 22:00 | 8.66 | 8.62
2019-09-17 22:30 | 8.16 | 8.12
2019-09-17 23:00 | 7.85 | 7.8
2019-09-17 23:30 | 6.98 | 6.93
2019-09-18 | 6.16 | 6.08
2019-09-18 00:30 | 5.61 | 5.52
2019-09-18 01:00 | 5.29 | 5.2
2019-09-18 01:30 | 4.95 | 4.84
2019-09-18 02:00 | 4.65 | 4.53
2019-09-18 02:30 | 4.47 | 4.34
2019-09-18 03:00 | 4.41 | 4.26
2019-09-18 03:30 | 4.49 | 4.36
2019-09-18 04:00 | 4.62 | 4.48
2019-09-18 04:30 | 4.82 | 4.7
2019-09-18 05:00 | 5.12 | 5
2019-09-18 05:30 | 5.6 | 5.5
2019-09-18 06:00 | 6.2 | 6.08
2019-09-18 06:30 | 6.85 | 6.75
2019-09-18 07:00 | 6.74 | 6.65
2019-09-18 07:30 | 6.15 | 6.07
2019-09-18 08:00 | 5.27 | 5.19
2019-09-18 08:30 | 3.8 | 3.69
2019-09-18 09:00 | 2.71 | 2.6
2019-09-18 09:30 | 2.13 | 2.02
2019-09-18 10:00 | 1.75 | 1.64
2019-09-18 10:30 | 1.31 | 1.18
2019-09-18 11:00 | 1.23 | 1.12
2019-09-18 11:30 | 1.24 | 1.13
2019-09-18 12:00 | 1.25 | 1.12
2019-09-18 12:30 | 1.32 | 1.23
2019-09-18 13:00 | 1.37 | 1.3
2019-09-18 13:30 | 1.3 | 1.21
2019-09-18 14:00 | 1.74 | 1.7
2019-09-18 14:30 | 2.42 | 2.39
2019-09-18 15:00 | 3.11 | 3.09
2019-09-18 15:30 | 4.05 | 4.02
2019-09-18 16:00 | 5.47 | 5.44
2019-09-18 16:30 | 6.66 | 6.63
2019-09-18 17:00 | 8.07 | 8.05
2019-09-18 17:30 | 9.16 | 9.14
2019-09-18 18:00 | 10.15 | 10.14
2019-09-18 18:30 | 11.61 | 11.6
2019-09-18 19:00 | 11.98 | 11.97
2019-09-18 19:30 | 11.63 | 11.62
2019-09-18 20:00 | 11.3 | 11.29
2019-09-18 20:30 | 11.27 | 11.26
2019-09-18 21:00 | 10.64 | 10.62
2019-09-18 21:30 | 9.98 | 9.97
2019-09-18 22:00 | 9.1 | 9.08
2019-09-18 22:30 | 8.52 | 8.48
2019-09-18 23:00 | 8.06 | 8.01
2019-09-18 23:30 | 7.17 | 7.12
2019-09-19 | 6.22 | 6.14
2019-09-19 00:30 | 5.67 | 5.58
2019-09-19 01:00 | 5.37 | 5.27
2019-09-19 01:30 | 4.98 | 4.86
2019-09-19 02:00 | 4.71 | 4.58
2019-09-19 02:30 | 4.56 | 4.43
2019-09-19 03:00 | 4.5 | 4.36
2019-09-19 03:30 | 4.66 | 4.52
2019-09-19 04:00 | 4.61 | 4.47
2019-09-19 04:30 | 4.86 | 4.73
2019-09-19 05:00 | 5.25 | 5.14
2019-09-19 05:30 | 5.89 | 5.81
2019-09-19 06:00 | 6.53 | 6.41
2019-09-19 06:30 | 7.03 | 6.93
2019-09-19 07:00 | 6.9 | 6.81
2019-09-19 07:30 | 6.64 | 6.57
2019-09-19 08:00 | 5.57 | 5.49
2019-09-19 08:30 | 4.29 | 4.2
2019-09-19 09:00 | 3.12 | 3.04
2019-09-19 09:30 | 2.26 | 2.15
2019-09-19 10:00 | 1.88 | 1.78
2019-09-19 10:30 | 1.76 | 1.68
2019-09-19 11:00 | 1.54 | 1.47
2019-09-19 11:30 | 1.4 | 1.34
2019-09-19 12:00 | 1.56 | 1.52
2019-09-19 12:30 | 1.7 | 1.67
2019-09-19 13:00 | 1.95 | 1.93
2019-09-19 13:30 | 2.68 | 2.66
2019-09-19 14:00 | 4.42 | 4.4
2019-09-19 14:30 | 3.51 | 3.49
2019-09-19 15:00 | 3.47 | 3.45
2019-09-19 15:30 | 4.58 | 4.55
2019-09-19 16:00 | 5.83 | 5.81
2019-09-19 16:30 | 7.24 | 7.22
2019-09-19 17:00 | 8.65 | 8.63
2019-09-19 17:30 | 9.66 | 9.64
2019-09-19 18:00 | 10.55 | 10.54
2019-09-19 18:30 | 11.86 | 11.86
2019-09-19 19:00 | 12.06 | 12.05
2019-09-19 19:30 | 11.65 | 11.65
2019-09-19 20:00 | 11.22 | 11.21
2019-09-19 20:30 | 10.88 | 10.87
2019-09-19 21:00 | 10.46 | 10.45
2019-09-19 21:30 | 9.65 | 9.63
2019-09-19 22:00 | 8.97 | 8.95
2019-09-19 22:30 | 8.34 | 8.31
2019-09-19 23:00 | 7.99 | 7.95
2019-09-19 23:30 | 7.06 | 7
2019-09-20 | 6.17 | 6.1
2019-09-20 00:30 | 5.49 | 5.4
2019-09-20 01:00 | 5.23 | 5.14
2019-09-20 01:30 | 4.89 | 4.78
2019-09-20 02:00 | 4.64 | 4.53
2019-09-20 02:30 | 4.54 | 4.41
2019-09-20 03:00 | 4.36 | 4.23
2019-09-20 03:30 | 4.47 | 4.33
2019-09-20 04:00 | 4.5 | 4.37
2019-09-20 04:30 | 4.72 | 4.59
2019-09-20 05:00 | 5.08 | 4.98
2019-09-20 05:30 | 5.52 | 5.43
2019-09-20 06:00 | 5.78 | 5.64
2019-09-20 06:30 | 6.19 | 6.06
2019-09-20 07:00 | 6.01 | 5.89
2019-09-20 07:30 | 6.1 | 6
2019-09-20 08:00 | 5.33 | 5.22
2019-09-20 08:30 | 4.81 | 4.7
2019-09-20 09:00 | 3.23 | 3.12
2019-09-20 09:30 | 3.18 | 3.1
2019-09-20 10:00 | 3.76 | 3.69
2019-09-20 10:30 | 2.74 | 2.67
2019-09-20 11:00 | 2.47 | 2.39
2019-09-20 11:30 | 2.59 | 2.53
2019-09-20 12:00 | 2.76 | 2.7
2019-09-20 12:30 | 2.93 | 2.88
2019-09-20 13:00 | 2.5 | 2.44
2019-09-20 13:30 | 2.03 | 1.97
2019-09-20 14:00 | 2.39 | 2.35
2019-09-20 14:30 | 4.71 | 4.68
2019-09-20 15:00 | 4.39 | 4.35
2019-09-20 15:30 | 4.59 | 4.55
2019-09-20 16:00 | 5.76 | 5.73
2019-09-20 16:30 | 6.98 | 6.96
2019-09-20 17:00 | 8.09 | 8.07
2019-09-20 17:30 | 8.95 | 8.93
2019-09-20 18:00 | 9.6 | 9.58
2019-09-20 18:30 | 10.5 | 10.5
2019-09-20 19:00 | 10.96 | 10.96
2019-09-20 19:30 | 10.75 | 10.74
2019-09-20 20:00 | 10.65 | 10.65
2019-09-20 20:30 | 10.59 | 10.58
2019-09-20 21:00 | 10.12 | 10.1
2019-09-20 21:30 | 9.29 | 9.27
2019-09-20 22:00 | 8.67 | 8.64
2019-09-20 22:30 | 8.41 | 8.38
2019-09-20 23:00 | 8.2 | 8.17
2019-09-20 23:30 | 7.4 | 7.35
2019-09-21 | 6.53 | 6.47
2019-09-21 00:30 | 5.79 | 5.7
2019-09-21 01:00 | 5.49 | 5.4
2019-09-21 01:30 | 5.11 | 5.02
2019-09-21 02:00 | 4.73 | 4.63
2019-09-21 02:30 | 4.63 | 4.52
2019-09-21 03:00 | 4.6 | 4.49
2019-09-21 03:30 | 4.44 | 4.32
2019-09-21 04:00 | 4.43 | 4.3
2019-09-21 04:30 | 4.61 | 4.49
2019-09-21 05:00 | 4.6 | 4.49
2019-09-21 05:30 | 4.72 | 4.6
2019-09-21 06:00 | 4.79 | 4.58
2019-09-21 06:30 | 5.18 | 5.01
2019-09-21 07:00 | 5.41 | 5.24
2019-09-21 07:30 | 5.7 | 5.56
2019-09-21 08:00 | 5.53 | 5.4
2019-09-21 08:30 | 4.15 | 4
2019-09-21 09:00 | 3.62 | 3.52
2019-09-21 09:30 | 3.68 | 3.61
2019-09-21 10:00 | 4.52 | 4.49
2019-09-21 10:30 | 4.01 | 3.98
2019-09-21 11:00 | 3.04 | 3
2019-09-21 11:30 | 2.32 | 2.28
2019-09-21 12:00 | 2.07 | 2.02
2019-09-21 12:30 | 2.03 | 1.98
2019-09-21 13:00 | 2.3 | 2.25
2019-09-21 13:30 | 2.57 | 2.53
2019-09-21 14:00 | 2.79 | 2.76
2019-09-21 14:30 | 3.2 | 3.17
2019-09-21 15:00 | 3.94 | 3.91
2019-09-21 15:30 | 4.89 | 4.87
2019-09-21 16:00 | 5.88 | 5.85
2019-09-21 16:30 | 6.96 | 6.94
2019-09-21 17:00 | 7.87 | 7.85
2019-09-21 17:30 | 8.67 | 8.64
2019-09-21 18:00 | 9.32 | 9.3
2019-09-21 18:30 | 10.3 | 10.29
2019-09-21 19:00 | 10.66 | 10.66
2019-09-21 19:30 | 10.21 | 10.2
2019-09-21 20:00 | 10.06 | 10.05
2019-09-21 20:30 | 9.98 | 9.97
2019-09-21 21:00 | 9.49 | 9.48
2019-09-21 21:30 | 8.89 | 8.87
2019-09-21 22:00 | 8.32 | 8.29
2019-09-21 22:30 | 8.05 | 8
2019-09-21 23:00 | 7.94 | 7.9
2019-09-21 23:30 | 7.16 | 7.11
2019-09-22 | 6.29 | 6.22
2019-09-22 00:30 | 5.68 | 5.6
2019-09-22 01:00 | 5.42 | 5.33
2019-09-22 01:30 | 5.02 | 4.92
2019-09-22 02:00 | 4.63 | 4.52
2019-09-22 02:30 | 4.57 | 4.45
2019-09-22 03:00 | 4.48 | 4.36
2019-09-22 03:30 | 4.48 | 4.36
2019-09-22 04:00 | 4.4 | 4.26
2019-09-22 04:30 | 4.42 | 4.3
2019-09-22 05:00 | 4.41 | 4.29
2019-09-22 05:30 | 4.52 | 4.39
2019-09-22 06:00 | 4.57 | 4.36
2019-09-22 06:30 | 4.56 | 4.34
2019-09-22 07:00 | 4.62 | 4.4
2019-09-22 07:30 | 4.54 | 4.35
2019-09-22 08:00 | 4 | 3.83
2019-09-22 08:30 | 4.26 | 4.14
2019-09-22 09:00 | 4.05 | 3.98
2019-09-22 09:30 | 4.09 | 4.03
2019-09-22 10:00 | 4.43 | 4.39
2019-09-22 10:30 | 3.63 | 3.59
2019-09-22 11:00 | 3.69 | 3.66
2019-09-22 11:30 | 3.39 | 3.37
2019-09-22 12:00 | 4.65 | 4.63
2019-09-22 12:30 | 6.22 | 6.2
2019-09-22 13:00 | 4.37 | 4.34
2019-09-22 13:30 | 4.32 | 4.29
2019-09-22 14:00 | 4.26 | 4.24
2019-09-22 14:30 | 4.55 | 4.52
2019-09-22 15:00 | 5.25 | 5.22
2019-09-22 15:30 | 5.96 | 5.94
2019-09-22 16:00 | 6.86 | 6.85
2019-09-22 16:30 | 7.97 | 7.95
2019-09-22 17:00 | 9.14 | 9.13
2019-09-22 17:30 | 9.98 | 9.97
2019-09-22 18:00 | 10.78 | 10.77
2019-09-22 18:30 | 11.71 | 11.71
2019-09-22 19:00 | 11.63 | 11.62
2019-09-22 19:30 | 11.11 | 11.1
2019-09-22 20:00 | 10.8 | 10.79
2019-09-22 20:30 | 10.59 | 10.57
2019-09-22 21:00 | 10.12 | 10.1
2019-09-22 21:30 | 9.39 | 9.36
2019-09-22 22:00 | 8.7 | 8.67
2019-09-22 22:30 | 8.28 | 8.24
2019-09-22 23:00 | 7.95 | 7.9
2019-09-22 23:30 | 7.12 | 7.05
2019-09-23 | 6.33 | 6.26
2019-09-23 00:30 | 5.69 | 5.61
2019-09-23 01:00 | 5.45 | 5.36
2019-09-23 01:30 | 5.05 | 4.95
2019-09-23 02:00 | 4.8 | 4.68
2019-09-23 02:30 | 4.58 | 4.46
2019-09-23 03:00 | 4.64 | 4.53
2019-09-23 03:30 | 4.62 | 4.5
2019-09-23 04:00 | 4.61 | 4.48
2019-09-23 04:30 | 4.75 | 4.63
2019-09-23 05:00 | 5.05 | 4.95
2019-09-23 05:30 | 5.39 | 5.29
2019-09-23 06:00 | 5.63 | 5.5
2019-09-23 06:30 | 5.86 | 5.74
2019-09-23 07:00 | 5.41 | 5.27
2019-09-23 07:30 | 4.8 | 4.68
2019-09-23 08:00 | 4.01 | 3.89
2019-09-23 08:30 | 3.57 | 3.48
2019-09-23 09:00 | 3.25 | 3.18
2019-09-23 09:30 | 2.85 | 2.79
2019-09-23 10:00 | 2.34 | 2.29
2019-09-23 10:30 | 1.99 | 1.94
2019-09-23 11:00 | 1.93 | 1.89
2019-09-23 11:30 | 2.01 | 1.99
2019-09-23 12:00 | 2.07 | 2.06
2019-09-23 12:30 | 2.24 | 2.22
2019-09-23 13:00 | 2.44 | 2.4
2019-09-23 13:30 | 3.22 | 3.19
2019-09-23 14:00 | 5.54 | 5.52
2019-09-23 14:30 | 5.92 | 5.9
2019-09-23 15:00 | 5.22 | 5.2
2019-09-23 15:30 | 6.58 | 6.56
2019-09-23 16:00 | 7.47 | 7.46
2019-09-23 16:30 | 8.56 | 8.54
2019-09-23 17:00 | 9.82 | 9.81
2019-09-23 17:30 | 10.73 | 10.72
2019-09-23 18:00 | 11.54 | 11.53
2019-09-23 18:30 | 12.63 | 12.63
2019-09-23 19:00 | 12.81 | 12.8
2019-09-23 19:30 | 12.33 | 12.33
2019-09-23 20:00 | 11.98 | 11.98
2019-09-23 20:30 | 11.63 | 11.62
2019-09-23 21:00 | 10.85 | 10.84
2019-09-23 21:30 | 10.02 | 10.01
2019-09-23 22:00 | 9.17 | 9.15
2019-09-23 22:30 | 8.6 | 8.57
2019-09-23 23:00 | 8.18 | 8.15
2019-09-23 23:30 | 7.3 | 7.25
2019-09-24 | 6.32 | 6.26
2019-09-24 00:30 | 5.72 | 5.63
2019-09-24 01:00 | 5.46 | 5.37
2019-09-24 01:30 | 5.2 | 5.1
2019-09-24 02:00 | 4.94 | 4.84
2019-09-24 02:30 | 4.75 | 4.64
2019-09-24 03:00 | 4.66 | 4.54
2019-09-24 03:30 | 4.69 | 4.57
2019-09-24 04:00 | 4.66 | 4.53
2019-09-24 04:30 | 4.85 | 4.73
2019-09-24 05:00 | 5.04 | 4.93
2019-09-24 05:30 | 5.61 | 5.52
2019-09-24 06:00 | 5.88 | 5.75
2019-09-24 06:30 | 6.04 | 5.92
2019-09-24 07:00 | 5.59 | 5.47
2019-09-24 07:30 | 4.95 | 4.84
2019-09-24 08:00 | 4.22 | 4.12
2019-09-24 08:30 | 3.76 | 3.66
2019-09-24 09:00 | 3.59 | 3.5
2019-09-24 09:30 | 4.01 | 3.95
2019-09-24 10:00 | 3.51 | 3.46
2019-09-24 10:30 | 3.75 | 3.71
2019-09-24 11:00 | 2.81 | 2.76
2019-09-24 11:30 | 3.7 | 3.66
2019-09-24 12:00 | 3.62 | 3.58
2019-09-24 12:30 | 2.01 | 1.96
2019-09-24 13:00 | 3.02 | 2.97
2019-09-24 13:30 | 3.47 | 3.41
2019-09-24 14:00 | 2.49 | 2.43
2019-09-24 14:30 | 3.51 | 3.46
2019-09-24 15:00 | 3.46 | 3.42
2019-09-24 15:30 | 5.27 | 5.23
2019-09-24 16:00 | 6.51 | 6.47
2019-09-24 16:30 | 7.35 | 7.32
2019-09-24 17:00 | 8.54 | 8.51
2019-09-24 17:30 | 9.54 | 9.51
2019-09-24 18:00 | 10.58 | 10.56
2019-09-24 18:30 | 11.6 | 11.59
2019-09-24 19:00 | 11.77 | 11.76
2019-09-24 19:30 | 11.34 | 11.34
2019-09-24 20:00 | 11.18 | 11.17
2019-09-24 20:30 | 11.07 | 11.06
2019-09-24 21:00 | 10.14 | 10.13
2019-09-24 21:30 | 9.39 | 9.37
2019-09-24 22:00 | 8.55 | 8.52
2019-09-24 22:30 | 8.12 | 8.08
2019-09-24 23:00 | 7.91 | 7.86
2019-09-24 23:30 | 7.06 | 7
2019-09-25 | 6.18 | 6.11
2019-09-25 00:30 | 5.57 | 5.49
2019-09-25 01:00 | 5.31 | 5.22
2019-09-25 01:30 | 4.96 | 4.86
2019-09-25 02:00 | 4.65 | 4.55
2019-09-25 02:30 | 4.62 | 4.5
2019-09-25 03:00 | 4.5 | 4.39
2019-09-25 03:30 | 4.57 | 4.45
2019-09-25 04:00 | 4.62 | 4.5
2019-09-25 04:30 | 4.68 | 4.56
2019-09-25 05:00 | 4.87 | 4.76
2019-09-25 05:30 | 5.32 | 5.24
2019-09-25 06:00 | 5.75 | 5.63
2019-09-25 06:30 | 6.19 | 6.07
2019-09-25 07:00 | 5.74 | 5.62
2019-09-25 07:30 | 6.12 | 6.03
2019-09-25 08:00 | 5.75 | 5.67
2019-09-25 08:30 | 5.78 | 5.72
2019-09-25 09:00 | 5.87 | 5.82
2019-09-25 09:30 | 5.36 | 5.31
2019-09-25 10:00 | 5.05 | 5
2019-09-25 10:30 | 3.7 | 3.64
2019-09-25 11:00 | 2.35 | 2.28
2019-09-25 11:30 | 3.28 | 3.23
2019-09-25 12:00 | 3.4 | 3.36
2019-09-25 12:30 | 3.2 | 3.16
2019-09-25 13:00 | 3.38 | 3.34
2019-09-25 13:30 | 3.42 | 3.39
2019-09-25 14:00 | 5.07 | 5.04
2019-09-25 14:30 | 3.48 | 3.43
2019-09-25 15:00 | 3.65 | 3.61
2019-09-25 15:30 | 4.3 | 4.27
2019-09-25 16:00 | 5.69 | 5.66
2019-09-25 16:30 | 6.57 | 6.54
2019-09-25 17:00 | 8.08 | 8.05
2019-09-25 17:30 | 9.25 | 9.23
2019-09-25 18:00 | 10.18 | 10.16
2019-09-25 18:30 | 11.35 | 11.34
2019-09-25 19:00 | 11.84 | 11.83
2019-09-25 19:30 | 11.36 | 11.36
2019-09-25 20:00 | 11.15 | 11.15
2019-09-25 20:30 | 10.95 | 10.94
2019-09-25 21:00 | 10.22 | 10.21
2019-09-25 21:30 | 9.44 | 9.42
2019-09-25 22:00 | 8.86 | 8.83
2019-09-25 22:30 | 8.29 | 8.26
2019-09-25 23:00 | 7.98 | 7.94
2019-09-25 23:30 | 7.19 | 7.14
2019-09-26 | 6.34 | 6.28
2019-09-26 00:30 | 5.67 | 5.59
2019-09-26 01:00 | 5.42 | 5.33
2019-09-26 01:30 | 5.05 | 4.95
2019-09-26 02:00 | 4.73 | 4.62
2019-09-26 02:30 | 4.6 | 4.49
2019-09-26 03:00 | 4.53 | 4.42
2019-09-26 03:30 | 4.55 | 4.44
2019-09-26 04:00 | 4.56 | 4.45
2019-09-26 04:30 | 4.73 | 4.62
2019-09-26 05:00 | 4.93 | 4.83
2019-09-26 05:30 | 5.46 | 5.38
2019-09-26 06:00 | 5.87 | 5.77
2019-09-26 06:30 | 6.37 | 6.28
2019-09-26 07:00 | 6.55 | 6.46
2019-09-26 07:30 | 6.68 | 6.6
2019-09-26 08:00 | 6.31 | 6.22
2019-09-26 08:30 | 5.93 | 5.85
2019-09-26 09:00 | 5.52 | 5.44
2019-09-26 09:30 | 6.15 | 6.09
2019-09-26 10:00 | 5.75 | 5.7
2019-09-26 10:30 | 5 | 4.93
2019-09-26 11:00 | 4.56 | 4.5
2019-09-26 11:30 | 5.45 | 5.41
2019-09-26 12:00 | 3.92 | 3.87
2019-09-26 12:30 | 3.19 | 3.13
2019-09-26 13:00 | 4.15 | 4.09
2019-09-26 13:30 | 5.24 | 5.19
2019-09-26 14:00 | 2.91 | 2.83
2019-09-26 14:30 | 2.37 | 2.29
2019-09-26 15:00 | 3.07 | 3
2019-09-26 15:30 | 3.95 | 3.9
2019-09-26 16:00 | 5.01 | 4.97
2019-09-26 16:30 | 6.24 | 6.21
2019-09-26 17:00 | 7.66 | 7.63
2019-09-26 17:30 | 8.81 | 8.79
2019-09-26 18:00 | 9.7 | 9.69
2019-09-26 18:30 | 10.76 | 10.75
2019-09-26 19:00 | 11.27 | 11.27
2019-09-26 19:30 | 10.84 | 10.84
2019-09-26 20:00 | 10.64 | 10.64
2019-09-26 20:30 | 10.56 | 10.55
2019-09-26 21:00 | 10.07 | 10.06
2019-09-26 21:30 | 9.47 | 9.45
2019-09-26 22:00 | 8.82 | 8.79
2019-09-26 22:30 | 8.27 | 8.23
2019-09-26 23:00 | 7.96 | 7.92
2019-09-26 23:30 | 7.2 | 7.15
2019-09-27 | 6.32 | 6.26
2019-09-27 00:30 | 5.55 | 5.46
2019-09-27 01:00 | 5.31 | 5.22
2019-09-27 01:30 | 4.98 | 4.89
2019-09-27 02:00 | 4.74 | 4.64
2019-09-27 02:30 | 4.67 | 4.56
2019-09-27 03:00 | 4.57 | 4.45
2019-09-27 03:30 | 4.48 | 4.36
2019-09-27 04:00 | 4.45 | 4.34
2019-09-27 04:30 | 4.59 | 4.48
2019-09-27 05:00 | 4.85 | 4.74
2019-09-27 05:30 | 5.16 | 5.06
2019-09-27 06:00 | 5.51 | 5.37
2019-09-27 06:30 | 6.02 | 5.89
2019-09-27 07:00 | 5.83 | 5.71
2019-09-27 07:30 | 4.8 | 4.66
2019-09-27 08:00 | 4.24 | 4.12
2019-09-27 08:30 | 3.63 | 3.53
2019-09-27 09:00 | 3.13 | 3.05
2019-09-27 09:30 | 2.53 | 2.44
2019-09-27 10:00 | 2 | 1.91
2019-09-27 10:30 | 1.42 | 1.31
2019-09-27 11:00 | 1.44 | 1.36
2019-09-27 11:30 | 1.69 | 1.63
2019-09-27 12:00 | 2.08 | 2.04
2019-09-27 12:30 | 2.27 | 2.22
2019-09-27 13:00 | 2.92 | 2.88
2019-09-27 13:30 | 5.06 | 5.05
2019-09-27 14:00 | 3.36 | 3.34
2019-09-27 14:30 | 3.51 | 3.48
2019-09-27 15:00 | 5.15 | 5.13
2019-09-27 15:30 | 5.35 | 5.34
2019-09-27 16:00 | 6.3 | 6.28
2019-09-27 16:30 | 7.3 | 7.28
2019-09-27 17:00 | 8.76 | 8.74
2019-09-27 17:30 | 9.37 | 9.35
2019-09-27 18:00 | 9.94 | 9.93
2019-09-27 18:30 | 10.45 | 10.45
2019-09-27 19:00 | 10.82 | 10.82
2019-09-27 19:30 | 10.56 | 10.55
2019-09-27 20:00 | 10.51 | 10.5
2019-09-27 20:30 | 10.25 | 10.24
2019-09-27 21:00 | 9.67 | 9.66
2019-09-27 21:30 | 9.03 | 9
2019-09-27 22:00 | 8.42 | 8.38
2019-09-27 22:30 | 8.19 | 8.15
2019-09-27 23:00 | 8.07 | 8.04
2019-09-27 23:30 | 7.21 | 7.16
2019-09-28 | 6.28 | 6.21
2019-09-28 00:30 | 5.76 | 5.68
2019-09-28 01:00 | 5.33 | 5.24
2019-09-28 01:30 | 5.09 | 4.99
2019-09-28 02:00 | 4.86 | 4.76
2019-09-28 02:30 | 4.69 | 4.59
2019-09-28 03:00 | 4.56 | 4.45
2019-09-28 03:30 | 4.52 | 4.4
2019-09-28 04:00 | 4.45 | 4.32
2019-09-28 04:30 | 4.49 | 4.38
2019-09-28 05:00 | 4.53 | 4.42
2019-09-28 05:30 | 4.58 | 4.44
2019-09-28 06:00 | 4.63 | 4.42
2019-09-28 06:30 | 4.78 | 4.58
2019-09-28 07:00 | 4.28 | 4.07
2019-09-28 07:30 | 3.95 | 3.77
2019-09-28 08:00 | 3.65 | 3.5
2019-09-28 08:30 | 3.31 | 3.18
2019-09-28 09:00 | 3.08 | 2.99
2019-09-28 09:30 | 2.9 | 2.83
2019-09-28 10:00 | 2.91 | 2.86
2019-09-28 10:30 | 2.43 | 2.37
2019-09-28 11:00 | 2.33 | 2.27
2019-09-28 11:30 | 2.36 | 2.3
2019-09-28 12:00 | 2.81 | 2.76
2019-09-28 12:30 | 2.85 | 2.79
2019-09-28 13:00 | 3.68 | 3.63
2019-09-28 13:30 | 5.21 | 5.18
2019-09-28 14:00 | 5.29 | 5.25
2019-09-28 14:30 | 7.43 | 7.41
2019-09-28 15:00 | 6.84 | 6.82
2019-09-28 15:30 | 6.64 | 6.62
2019-09-28 16:00 | 7.73 | 7.71
2019-09-28 16:30 | 8.75 | 8.74
2019-09-28 17:00 | 10.04 | 10.03
2019-09-28 17:30 | 10.41 | 10.41
2019-09-28 18:00 | 10.52 | 10.52
2019-09-28 18:30 | 11.13 | 11.12
2019-09-28 19:00 | 11.39 | 11.39
2019-09-28 19:30 | 11.07 | 11.06
2019-09-28 20:00 | 10.97 | 10.96
2019-09-28 20:30 | 10.61 | 10.6
2019-09-28 21:00 | 9.96 | 9.95
2019-09-28 21:30 | 9.37 | 9.36
2019-09-28 22:00 | 8.91 | 8.89
2019-09-28 22:30 | 8.51 | 8.48
2019-09-28 23:00 | 8.27 | 8.23
2019-09-28 23:30 | 7.46 | 7.41
2019-09-29 | 6.64 | 6.58
2019-09-29 00:30 | 5.97 | 5.9
2019-09-29 01:00 | 5.57 | 5.49
2019-09-29 01:30 | 5.2 | 5.11
2019-09-29 02:00 | 4.87 | 4.76
2019-09-29 02:30 | 4.74 | 4.63
2019-09-29 03:00 | 4.61 | 4.48
2019-09-29 03:30 | 4.57 | 4.44
2019-09-29 04:00 | 4.52 | 4.39
2019-09-29 04:30 | 4.48 | 4.33
2019-09-29 05:00 | 4.5 | 4.37
2019-09-29 05:30 | 4.52 | 4.35
2019-09-29 06:00 | 4.58 | 4.33
2019-09-29 06:30 | 4.4 | 4.14
2019-09-29 07:00 | 3.87 | 3.6
2019-09-29 07:30 | 3.65 | 3.41
2019-09-29 08:00 | 3.45 | 3.25
2019-09-29 08:30 | 3.22 | 3.06
2019-09-29 09:00 | 3.02 | 2.91
2019-09-29 09:30 | 2.8 | 2.72
2019-09-29 10:00 | 2.48 | 2.42
2019-09-29 10:30 | 2.25 | 2.19
2019-09-29 11:00 | 2.23 | 2.18
2019-09-29 11:30 | 2.15 | 2.11
2019-09-29 12:00 | 2.25 | 2.22
2019-09-29 12:30 | 2.57 | 2.54
2019-09-29 13:00 | 2.8 | 2.77
2019-09-29 13:30 | 3.18 | 3.15
2019-09-29 14:00 | 3.98 | 3.95
2019-09-29 14:30 | 4.48 | 4.46
2019-09-29 15:00 | 5.22 | 5.2
2019-09-29 15:30 | 6.07 | 6.06
2019-09-29 16:00 | 6.95 | 6.94
2019-09-29 16:30 | 8.06 | 8.05
2019-09-29 17:00 | 9.18 | 9.17
2019-09-29 17:30 | 10.1 | 10.08
2019-09-29 18:00 | 10.64 | 10.63
2019-09-29 18:30 | 11.4 | 11.39
2019-09-29 19:00 | 11.61 | 11.61
2019-09-29 19:30 | 11.03 | 11.02
2019-09-29 20:00 | 10.57 | 10.56
2019-09-29 20:30 | 10.48 | 10.46
2019-09-29 21:00 | 9.88 | 9.86
2019-09-29 21:30 | 9.24 | 9.21
2019-09-29 22:00 | 8.65 | 8.62
2019-09-29 22:30 | 8.22 | 8.18
2019-09-29 23:00 | 7.84 | 7.78
2019-09-29 23:30 | 6.98 | 6.93
2019-09-30 | 6.1 | 6.03
2019-09-30 00:30 | 5.43 | 5.34
2019-09-30 01:00 | 5.16 | 5.06
2019-09-30 01:30 | 4.85 | 4.74
2019-09-30 02:00 | 4.75 | 4.64
2019-09-30 02:30 | 4.75 | 4.64
2019-09-30 03:00 | 4.68 | 4.56
2019-09-30 03:30 | 4.63 | 4.52
2019-09-30 04:00 | 4.55 | 4.42
2019-09-30 04:30 | 4.75 | 4.63
2019-09-30 05:00 | 4.96 | 4.86
2019-09-30 05:30 | 5.34 | 5.24
2019-09-30 06:00 | 5.78 | 5.65
2019-09-30 06:30 | 5.81 | 5.69
2019-09-30 07:00 | 5.37 | 5.26
2019-09-30 07:30 | 5.35 | 5.24
2019-09-30 08:00 | 4.69 | 4.59
2019-09-30 08:30 | 3.94 | 3.85
2019-09-30 09:00 | 3.53 | 3.46
2019-09-30 09:30 | 3.59 | 3.53
2019-09-30 10:00 | 2.99 | 2.93
2019-09-30 10:30 | 2.32 | 2.26
2019-09-30 11:00 | 2.46 | 2.42
2019-09-30 11:30 | 2.98 | 2.96
2019-09-30 12:00 | 2.58 | 2.55
2019-09-30 12:30 | 3.13 | 3.11
2019-09-30 13:00 | 4.38 | 4.36
2019-09-30 13:30 | 4.36 | 4.34
2019-09-30 14:00 | 3.04 | 3.01
2019-09-30 14:30 | 4.99 | 4.97
2019-09-30 15:00 | 4.57 | 4.55
2019-09-30 15:30 | 5.27 | 5.26
2019-09-30 16:00 | 6.4 | 6.39
2019-09-30 16:30 | 7.75 | 7.74
2019-09-30 17:00 | 8.81 | 8.8
2019-09-30 17:30 | 9.72 | 9.7
2019-09-30 18:00 | 10.73 | 10.72
2019-09-30 18:30 | 11.74 | 11.74
2019-09-30 19:00 | 12.01 | 12.01
2019-09-30 19:30 | 11.43 | 11.43
2019-09-30 20:00 | 11.36 | 11.35
2019-09-30 20:30 | 11.04 | 11.03
2019-09-30 21:00 | 10.25 | 10.23
2019-09-30 21:30 | 9.41 | 9.38
2019-09-30 22:00 | 8.76 | 8.74
2019-09-30 22:30 | 8.31 | 8.28
2019-09-30 23:00 | 8.02 | 7.98
2019-09-30 23:30 | 7.07 | 7.01
2019-10-01 | 6.3 | 6.22
2019-10-01 00:30 | 5.69 | 5.6
2019-10-01 01:00 | 5.32 | 5.23
2019-10-01 01:30 | 5.06 | 4.97
2019-10-01 02:00 | 4.82 | 4.71
2019-10-01 02:30 | 4.69 | 4.57
2019-10-01 03:00 | 4.63 | 4.51
2019-10-01 03:30 | 4.69 | 4.57
2019-10-01 04:00 | 4.59 | 4.48
2019-10-01 04:30 | 4.79 | 4.68
2019-10-01 05:00 | 4.89 | 4.78
2019-10-01 05:30 | 5.28 | 5.18
2019-10-01 06:00 | 5.81 | 5.68
2019-10-01 06:30 | 5.84 | 5.72
2019-10-01 07:00 | 5.28 | 5.16
2019-10-01 07:30 | 4.69 | 4.59
2019-10-01 08:00 | 4.48 | 4.39
2019-10-01 08:30 | 4.23 | 4.15
2019-10-01 09:00 | 3.86 | 3.79
2019-10-01 09:30 | 5.56 | 5.51
2019-10-01 10:00 | 5.54 | 5.49
2019-10-01 10:30 | 4.03 | 3.96
2019-10-01 11:00 | 4.28 | 4.22
2019-10-01 11:30 | 3.5 | 3.43
2019-10-01 12:00 | 3.97 | 3.91
2019-10-01 12:30 | 4.8 | 4.74
2019-10-01 13:00 | 2.81 | 2.72
2019-10-01 13:30 | 3.3 | 3.22
2019-10-01 14:00 | 2.65 | 2.57
2019-10-01 14:30 | 3.32 | 3.26
2019-10-01 15:00 | 3.28 | 3.21
2019-10-01 15:30 | 4.31 | 4.24
2019-10-01 16:00 | 5.22 | 5.16
2019-10-01 16:30 | 6.27 | 6.21
2019-10-01 17:00 | 7.71 | 7.67
2019-10-01 17:30 | 9.19 | 9.16
2019-10-01 18:00 | 10.14 | 10.12
2019-10-01 18:30 | 11.38 | 11.38
2019-10-01 19:00 | 11.73 | 11.72
2019-10-01 19:30 | 11.32 | 11.32
2019-10-01 20:00 | 11.06 | 11.06
2019-10-01 20:30 | 10.88 | 10.87
2019-10-01 21:00 | 10.05 | 10.03
2019-10-01 21:30 | 9.28 | 9.25
2019-10-01 22:00 | 8.68 | 8.65
2019-10-01 22:30 | 8.09 | 8.05
2019-10-01 23:00 | 7.84 | 7.79
2019-10-01 23:30 | 7.1 | 7.04
2019-10-02 | 6.32 | 6.24
2019-10-02 00:30 | 5.62 | 5.52
2019-10-02 01:00 | 5.27 | 5.16
2019-10-02 01:30 | 4.93 | 4.81
2019-10-02 02:00 | 4.6 | 4.48
2019-10-02 02:30 | 4.5 | 4.36
2019-10-02 03:00 | 4.46 | 4.32
2019-10-02 03:30 | 4.52 | 4.38
2019-10-02 04:00 | 4.55 | 4.41
2019-10-02 04:30 | 4.71 | 4.59
2019-10-02 05:00 | 4.95 | 4.83
2019-10-02 05:30 | 5.38 | 5.26
2019-10-02 06:00 | 5.75 | 5.61
2019-10-02 06:30 | 5.57 | 5.41
2019-10-02 07:00 | 5.12 | 4.97
2019-10-02 07:30 | 4.48 | 4.35
2019-10-02 08:00 | 3.81 | 3.69
2019-10-02 08:30 | 3.33 | 3.22
2019-10-02 09:00 | 4.42 | 4.34
2019-10-02 09:30 | 5.42 | 5.35
2019-10-02 10:00 | 4.69 | 4.62
2019-10-02 10:30 | 3.33 | 3.26
2019-10-02 11:00 | 3.24 | 3.17
2019-10-02 11:30 | 1.83 | 1.71
2019-10-02 12:00 | 3.14 | 3.05
2019-10-02 12:30 | 2.66 | 2.6
2019-10-02 13:00 | 1.11 | 1
2019-10-02 13:30 | 1.11 | 1
2019-10-02 14:00 | 1.79 | 1.71
2019-10-02 14:30 | 2.17 | 2.1
2019-10-02 15:00 | 3.23 | 3.19
2019-10-02 15:30 | 4.67 | 4.63
2019-10-02 16:00 | 5.4 | 5.36
2019-10-02 16:30 | 6.26 | 6.22
2019-10-02 17:00 | 7.64 | 7.61
2019-10-02 17:30 | 8.82 | 8.8
2019-10-02 18:00 | 9.8 | 9.78
2019-10-02 18:30 | 11.01 | 11.01
2019-10-02 19:00 | 11.54 | 11.53
2019-10-02 19:30 | 11.1 | 11.1
2019-10-02 20:00 | 11.07 | 11.06
2019-10-02 20:30 | 10.89 | 10.88
2019-10-02 21:00 | 10.25 | 10.23
2019-10-02 21:30 | 9.48 | 9.45
2019-10-02 22:00 | 8.68 | 8.64
2019-10-02 22:30 | 8.31 | 8.27
2019-10-02 23:00 | 8 | 7.95
2019-10-02 23:30 | 7.19 | 7.13
2019-10-03 | 6.32 | 6.23
2019-10-03 00:30 | 5.7 | 5.6
2019-10-03 01:00 | 5.32 | 5.21
2019-10-03 01:30 | 4.94 | 4.8
2019-10-03 02:00 | 4.67 | 4.51
2019-10-03 02:30 | 4.6 | 4.45
2019-10-03 03:00 | 4.56 | 4.41
2019-10-03 03:30 | 4.58 | 4.43
2019-10-03 04:00 | 4.55 | 4.4
2019-10-03 04:30 | 4.77 | 4.63
2019-10-03 05:00 | 4.99 | 4.86
2019-10-03 05:30 | 5.51 | 5.37
2019-10-03 06:00 | 5.87 | 5.7
2019-10-03 06:30 | 5.65 | 5.48
2019-10-03 07:00 | 5.1 | 4.92
2019-10-03 07:30 | 4.48 | 4.31
2019-10-03 08:00 | 3.42 | 3.21
2019-10-03 08:30 | 2.82 | 2.64
2019-10-03 09:00 | 2.16 | 1.96
2019-10-03 09:30 | 1.73 | 1.56
2019-10-03 10:00 | 1.38 | 1.2
2019-10-03 10:30 | 1.27 | 1.12
2019-10-03 11:00 | 1.32 | 1.19
2019-10-03 11:30 | 1.33 | 1.22
2019-10-03 12:00 | 1.2 | 1.1
2019-10-03 12:30 | 1.08 | 0.98
2019-10-03 13:00 | 1.18 | 1.09
2019-10-03 13:30 | 1.24 | 1.13
2019-10-03 14:00 | 1.82 | 1.76
2019-10-03 14:30 | 2.41 | 2.36
2019-10-03 15:00 | 3.1 | 3.05
2019-10-03 15:30 | 4.16 | 4.12
2019-10-03 16:00 | 5.16 | 5.12
2019-10-03 16:30 | 6.44 | 6.41
2019-10-03 17:00 | 7.69 | 7.66
2019-10-03 17:30 | 8.83 | 8.8
2019-10-03 18:00 | 9.73 | 9.71
2019-10-03 18:30 | 10.68 | 10.68
2019-10-03 19:00 | 11.3 | 11.3
2019-10-03 19:30 | 10.96 | 10.96
2019-10-03 20:00 | 10.82 | 10.81
2019-10-03 20:30 | 10.63 | 10.62
2019-10-03 21:00 | 10.05 | 10.04
2019-10-03 21:30 | 9.38 | 9.36
2019-10-03 22:00 | 8.61 | 8.57
2019-10-03 22:30 | 8.2 | 8.15
2019-10-03 23:00 | 7.95 | 7.89
2019-10-03 23:30 | 7.13 | 7.06
2019-10-04 | 6.3 | 6.22
2019-10-04 00:30 | 5.67 | 5.57
2019-10-04 01:00 | 5.37 | 5.26
2019-10-04 01:30 | 4.99 | 4.87
2019-10-04 02:00 | 4.76 | 4.64
2019-10-04 02:30 | 4.63 | 4.49
2019-10-04 03:00 | 4.57 | 4.44
2019-10-04 03:30 | 4.55 | 4.42
2019-10-04 04:00 | 4.63 | 4.49
2019-10-04 04:30 | 4.76 | 4.62
2019-10-04 05:00 | 5 | 4.87
2019-10-04 05:30 | 5.24 | 5.09
2019-10-04 06:00 | 5.31 | 5.11
2019-10-04 06:30 | 5.08 | 4.88
2019-10-04 07:00 | 4.52 | 4.32
2019-10-04 07:30 | 4.16 | 3.97
2019-10-04 08:00 | 3.4 | 3.2
2019-10-04 08:30 | 2.67 | 2.45
2019-10-04 09:00 | 1.95 | 1.69
2019-10-04 09:30 | 1.45 | 1.15
2019-10-04 10:00 | 1.16 | 0.87
2019-10-04 10:30 | 0.91 | 0.64
2019-10-04 11:00 | 0.8 | 0.58
2019-10-04 11:30 | 0.74 | 0.54
2019-10-04 12:00 | 0.81 | 0.65
2019-10-04 12:30 | 1.1 | 1.01
2019-10-04 13:00 | 1.3 | 1.22
2019-10-04 13:30 | 1.67 | 1.61
2019-10-04 14:00 | 2.31 | 2.26
2019-10-04 14:30 | 3.04 | 3
2019-10-04 15:00 | 3.81 | 3.79
2019-10-04 15:30 | 4.99 | 4.97
2019-10-04 16:00 | 6 | 5.98
2019-10-04 16:30 | 7.05 | 7.04
2019-10-04 17:00 | 8.3 | 8.29
2019-10-04 17:30 | 9.01 | 9
2019-10-04 18:00 | 9.48 | 9.46
2019-10-04 18:30 | 10.31 | 10.31
2019-10-04 19:00 | 10.73 | 10.73
2019-10-04 19:30 | 10.51 | 10.51
2019-10-04 20:00 | 10.37 | 10.36
2019-10-04 20:30 | 10.31 | 10.3
2019-10-04 21:00 | 9.69 | 9.67
2019-10-04 21:30 | 9.08 | 9.06
2019-10-04 22:00 | 8.38 | 8.35
2019-10-04 22:30 | 8 | 7.96
2019-10-04 23:00 | 7.89 | 7.84
2019-10-04 23:30 | 7.1 | 7.03
2019-10-05 | 6.31 | 6.23
2019-10-05 00:30 | 5.69 | 5.6
2019-10-05 01:00 | 5.35 | 5.25
2019-10-05 01:30 | 4.98 | 4.86
2019-10-05 02:00 | 4.67 | 4.55
2019-10-05 02:30 | 4.56 | 4.42
2019-10-05 03:00 | 4.44 | 4.29
2019-10-05 03:30 | 4.46 | 4.32
2019-10-05 04:00 | 4.47 | 4.33
2019-10-05 04:30 | 4.45 | 4.3
2019-10-05 05:00 | 4.57 | 4.43
2019-10-05 05:30 | 4.68 | 4.49
2019-10-05 06:00 | 4.58 | 4.32
2019-10-05 06:30 | 4.32 | 4.05
2019-10-05 07:00 | 3.85 | 3.59
2019-10-05 07:30 | 3.59 | 3.36
2019-10-05 08:00 | 3.38 | 3.2
2019-10-05 08:30 | 2.99 | 2.83
2019-10-05 09:00 | 2.54 | 2.41
2019-10-05 09:30 | 2.08 | 1.96
2019-10-05 10:00 | 2.28 | 2.19
2019-10-05 10:30 | 1.85 | 1.76
2019-10-05 11:00 | 1.67 | 1.6
2019-10-05 11:30 | 1.7 | 1.63
2019-10-05 12:00 | 2.04 | 1.97
2019-10-05 12:30 | 2.41 | 2.36
2019-10-05 13:00 | 3.52 | 3.47
2019-10-05 13:30 | 4.64 | 4.6
2019-10-05 14:00 | 4.18 | 4.14
2019-10-05 14:30 | 4.87 | 4.84
2019-10-05 15:00 | 5.46 | 5.43
2019-10-05 15:30 | 7.06 | 7.04
2019-10-05 16:00 | 7.44 | 7.43
2019-10-05 16:30 | 7.82 | 7.8
2019-10-05 17:00 | 8.52 | 8.5
2019-10-05 17:30 | 9.19 | 9.17
2019-10-05 18:00 | 9.54 | 9.52
2019-10-05 18:30 | 10.21 | 10.2
2019-10-05 19:00 | 10.55 | 10.55
2019-10-05 19:30 | 10.16 | 10.15
2019-10-05 20:00 | 10.03 | 10.02
2019-10-05 20:30 | 9.78 | 9.77
2019-10-05 21:00 | 9.17 | 9.15
2019-10-05 21:30 | 8.65 | 8.62
2019-10-05 22:00 | 8.23 | 8.2
2019-10-05 22:30 | 7.83 | 7.79
2019-10-05 23:00 | 7.72 | 7.67
2019-10-05 23:30 | 7.04 | 6.98
2019-10-06 | 6.2 | 6.13
2019-10-06 00:30 | 5.58 | 5.49
2019-10-06 01:00 | 5.23 | 5.14
2019-10-06 01:30 | 4.91 | 4.8
2019-10-06 02:00 | 4.71 | 4.59
2019-10-06 02:30 | 4.59 | 4.45
2019-10-06 03:00 | 4.5 | 4.37
2019-10-06 03:30 | 4.48 | 4.34
2019-10-06 04:00 | 4.4 | 4.26
2019-10-06 04:30 | 4.44 | 4.3
2019-10-06 05:00 | 4.46 | 4.33
2019-10-06 05:30 | 4.33 | 4.14
2019-10-06 06:00 | 4.39 | 4.12
2019-10-06 06:30 | 4.35 | 4.09
2019-10-06 07:00 | 4.07 | 3.8
2019-10-06 07:30 | 3.84 | 3.6
2019-10-06 08:00 | 4.05 | 3.86
2019-10-06 08:30 | 3.94 | 3.77
2019-10-06 09:00 | 3.52 | 3.39
2019-10-06 09:30 | 3.07 | 2.96
2019-10-06 10:00 | 2.42 | 2.32
2019-10-06 10:30 | 2.23 | 2.13
2019-10-06 11:00 | 1.93 | 1.86
2019-10-06 11:30 | 2.15 | 2.1
2019-10-06 12:00 | 2.09 | 2.05
2019-10-06 12:30 | 2.31 | 2.26
2019-10-06 13:00 | 2.58 | 2.54
2019-10-06 13:30 | 3.09 | 3.05
2019-10-06 14:00 | 4 | 3.97
2019-10-06 14:30 | 4.92 | 4.9
2019-10-06 15:00 | 5.87 | 5.86
2019-10-06 15:30 | 6.92 | 6.91
2019-10-06 16:00 | 7.71 | 7.7
2019-10-06 16:30 | 8.45 | 8.44
2019-10-06 17:00 | 9.09 | 9.08
2019-10-06 17:30 | 9.8 | 9.79
2019-10-06 18:00 | 10.22 | 10.21
2019-10-06 18:30 | 10.84 | 10.84
2019-10-06 19:00 | 10.98 | 10.97
2019-10-06 19:30 | 10.34 | 10.33
2019-10-06 20:00 | 10.22 | 10.21
2019-10-06 20:30 | 9.95 | 9.93
2019-10-06 21:00 | 9.39 | 9.36
2019-10-06 21:30 | 8.88 | 8.86
2019-10-06 22:00 | 8.46 | 8.42
2019-10-06 22:30 | 8.15 | 8.11
2019-10-06 23:00 | 7.98 | 7.94
2019-10-06 23:30 | 7.12 | 7.06
2019-10-07 | 6.36 | 6.29
2019-10-07 00:30 | 5.79 | 5.71
2019-10-07 01:00 | 5.48 | 5.39
2019-10-07 01:30 | 5.05 | 4.96
2019-10-07 02:00 | 4.8 | 4.69
2019-10-07 02:30 | 4.69 | 4.57
2019-10-07 03:00 | 4.6 | 4.48
2019-10-07 03:30 | 4.54 | 4.41
2019-10-07 04:00 | 4.49 | 4.36
2019-10-07 04:30 | 4.48 | 4.34
2019-10-07 05:00 | 4.54 | 4.42
2019-10-07 05:30 | 4.51 | 4.32
2019-10-07 06:00 | 4.39 | 4.13
2019-10-07 06:30 | 4.06 | 3.76
2019-10-07 07:00 | 3.62 | 3.32
2019-10-07 07:30 | 3.35 | 3.1
2019-10-07 08:00 | 3.08 | 2.87
2019-10-07 08:30 | 2.87 | 2.71
2019-10-07 09:00 | 2.87 | 2.76
2019-10-07 09:30 | 2.83 | 2.76
2019-10-07 10:00 | 2.83 | 2.79
2019-10-07 10:30 | 3.03 | 3.01
2019-10-07 11:00 | 3.4 | 3.38
2019-10-07 11:30 | 4.17 | 4.14
2019-10-07 12:00 | 4.87 | 4.84
2019-10-07 12:30 | 6.13 | 6.1
2019-10-07 13:00 | 7.23 | 7.2
2019-10-07 13:30 | 8.77 | 8.75
2019-10-07 14:00 | 10.67 | 10.64
2019-10-07 14:30 | 12.24 | 12.19
2019-10-07 15:00 | 13.37 | 13.33
2019-10-07 15:30 | 13.84 | 13.79
2019-10-07 16:00 | 15.47 | 15.43
2019-10-07 16:30 | 15.55 | 15.52
2019-10-07 17:00 | 15.33 | 15.31
2019-10-07 17:30 | 15.18 | 15.16
2019-10-07 18:00 | 15.26 | 15.26
2019-10-07 18:30 | 15.53 | 15.52
2019-10-07 19:00 | 15.38 | 15.37
2019-10-07 19:30 | 14.33 | 14.32
2019-10-07 20:00 | 13.73 | 13.72
2019-10-07 20:30 | 13.08 | 13.08
2019-10-07 21:00 | 12.18 | 12.18
2019-10-07 21:30 | 11 | 11
2019-10-07 22:00 | 9.85 | 9.84
2019-10-07 22:30 | 9 | 8.98
2019-10-07 23:00 | 8.65 | 8.62
2019-10-07 23:30 | 7.61 | 7.58
2019-10-08 | 6.73 | 6.68
2019-10-08 00:30 | 6.16 | 6.1
2019-10-08 01:00 | 5.84 | 5.78
2019-10-08 01:30 | 5.54 | 5.47
2019-10-08 02:00 | 5.31 | 5.24
2019-10-08 02:30 | 5.12 | 5.04
2019-10-08 03:00 | 4.97 | 4.88
2019-10-08 03:30 | 4.93 | 4.83
2019-10-08 04:00 | 4.97 | 4.87
2019-10-08 04:30 | 5.07 | 4.99
2019-10-08 05:00 | 5.27 | 5.19
2019-10-08 05:30 | 5.5 | 5.4
2019-10-08 06:00 | 5.8 | 5.68
2019-10-08 06:30 | 6.6 | 6.51
2019-10-08 07:00 | 6.73 | 6.66
2019-10-08 07:30 | 6.59 | 6.55
2019-10-08 08:00 | 5.08 | 5.05
2019-10-08 08:30 | 4.07 | 4.05
2019-10-08 09:00 | 4.35 | 4.34
2019-10-08 09:30 | 4.32 | 4.3
2019-10-08 10:00 | 4.1 | 4.07
2019-10-08 10:30 | 5 | 4.97
2019-10-08 11:00 | 5.88 | 5.86
2019-10-08 11:30 | 7.67 | 7.65
2019-10-08 12:00 | 6.29 | 6.24
2019-10-08 12:30 | 10.01 | 9.98
2019-10-08 13:00 | 10.27 | 10.22
2019-10-08 13:30 | 12.61 | 12.57
2019-10-08 14:00 | 11.74 | 11.71
2019-10-08 14:30 | 12.95 | 12.93
2019-10-08 15:00 | 12.02 | 12
2019-10-08 15:30 | 12.23 | 12.22
2019-10-08 16:00 | 11.8 | 11.79
2019-10-08 16:30 | 12.6 | 12.58
2019-10-08 17:00 | 14.32 | 14.29
2019-10-08 17:30 | 15.61 | 15.59
2019-10-08 18:00 | 16.19 | 16.17
2019-10-08 18:30 | 17.07 | 17.02
2019-10-08 19:00 | 17.07 | 17.03
2019-10-08 19:30 | 16.25 | 16.22
2019-10-08 20:00 | 15.39 | 15.38
2019-10-08 20:30 | 14.71 | 14.69
2019-10-08 21:00 | 13.89 | 13.88
2019-10-08 21:30 | 12.57 | 12.57
2019-10-08 22:00 | 11.2 | 11.19
2019-10-08 22:30 | 10.21 | 10.21
2019-10-08 23:00 | 9.4 | 9.4
2019-10-08 23:30 | 8.14 | 8.13
2019-10-09 | 7.15 | 7.13
2019-10-09 00:30 | 6.51 | 6.47
2019-10-09 01:00 | 6.12 | 6.08
2019-10-09 01:30 | 5.72 | 5.67
2019-10-09 02:00 | 5.5 | 5.44
2019-10-09 02:30 | 5.3 | 5.23
2019-10-09 03:00 | 5.16 | 5.08
2019-10-09 03:30 | 5.19 | 5.11
2019-10-09 04:00 | 5.1 | 5
2019-10-09 04:30 | 5.16 | 5.07
2019-10-09 05:00 | 5.38 | 5.29
2019-10-09 05:30 | 5.62 | 5.52
2019-10-09 06:00 | 6.01 | 5.88
2019-10-09 06:30 | 6.14 | 6.04
2019-10-09 07:00 | 5.99 | 5.9
2019-10-09 07:30 | 6.16 | 6.09
2019-10-09 08:00 | 5.55 | 5.5
2019-10-09 08:30 | 4.15 | 4.1
2019-10-09 09:00 | 3 | 2.95
2019-10-09 09:30 | 3.27 | 3.24
2019-10-09 10:00 | 3.73 | 3.71
2019-10-09 10:30 | 3.47 | 3.45
2019-10-09 11:00 | 2.25 | 2.24
2019-10-09 11:30 | 2.37 | 2.35
2019-10-09 12:00 | 2.92 | 2.91
2019-10-09 12:30 | 3.75 | 3.74
2019-10-09 13:00 | 4.12 | 4.11
2019-10-09 13:30 | 4.8 | 4.79
2019-10-09 14:00 | 4.19 | 4.18
2019-10-09 14:30 | 3.97 | 3.96
2019-10-09 15:00 | 4.56 | 4.55
2019-10-09 15:30 | 5.55 | 5.55
2019-10-09 16:00 | 6.51 | 6.5
2019-10-09 16:30 | 7.45 | 7.43
2019-10-09 17:00 | 8.46 | 8.44
2019-10-09 17:30 | 9.35 | 9.33
2019-10-09 18:00 | 10.17 | 10.15
2019-10-09 18:30 | 11.15 | 11.15
2019-10-09 19:00 | 11.75 | 11.75
2019-10-09 19:30 | 11.37 | 11.36
2019-10-09 20:00 | 11.21 | 11.2
2019-10-09 20:30 | 11.01 | 11
2019-10-09 21:00 | 10.33 | 10.31
2019-10-09 21:30 | 9.38 | 9.35
2019-10-09 22:00 | 8.74 | 8.71
2019-10-09 22:30 | 8.26 | 8.22
2019-10-09 23:00 | 7.93 | 7.87
2019-10-09 23:30 | 6.78 | 6.71
2019-10-10 | 5.87 | 5.77
2019-10-10 00:30 | 5.28 | 5.16
2019-10-10 01:00 | 5.16 | 5.04
2019-10-10 01:30 | 4.81 | 4.68
2019-10-10 02:00 | 4.6 | 4.46
2019-10-10 02:30 | 4.42 | 4.26
2019-10-10 03:00 | 4.44 | 4.28
2019-10-10 03:30 | 4.41 | 4.25
2019-10-10 04:00 | 4.42 | 4.26
2019-10-10 04:30 | 4.64 | 4.49
2019-10-10 05:00 | 4.87 | 4.73
2019-10-10 05:30 | 5.24 | 5.08
2019-10-10 06:00 | 5.61 | 5.44
2019-10-10 06:30 | 5.97 | 5.84
2019-10-10 07:00 | 5.47 | 5.35
2019-10-10 07:30 | 6.37 | 6.26
2019-10-10 08:00 | 5.87 | 5.77
2019-10-10 08:30 | 4.38 | 4.25
2019-10-10 09:00 | 3.34 | 3.2
2019-10-10 09:30 | 3.2 | 3.06
2019-10-10 10:00 | 2.98 | 2.84
2019-10-10 10:30 | 3.36 | 3.24
2019-10-10 11:00 | 4.51 | 4.41
2019-10-10 11:30 | 4.24 | 4.14
2019-10-10 12:00 | 3.03 | 2.87
2019-10-10 12:30 | 3.13 | 2.99
2019-10-10 13:00 | 4.15 | 4.04
2019-10-10 13:30 | 6.22 | 6.16
2019-10-10 14:00 | 4.25 | 4.15
2019-10-10 14:30 | 4.15 | 4.04
2019-10-10 15:00 | 5 | 4.95
2019-10-10 15:30 | 8.41 | 8.38
2019-10-10 16:00 | 8.79 | 8.76
2019-10-10 16:30 | 9.34 | 9.31
2019-10-10 17:00 | 9.75 | 9.72
2019-10-10 17:30 | 10.45 | 10.42
2019-10-10 18:00 | 11.47 | 11.45
2019-10-10 18:30 | 11.88 | 11.87
2019-10-10 19:00 | 11.73 | 11.73
2019-10-10 19:30 | 11.52 | 11.52
2019-10-10 20:00 | 11.35 | 11.35
2019-10-10 20:30 | 11.12 | 11.11
2019-10-10 21:00 | 10.46 | 10.45
2019-10-10 21:30 | 9.49 | 9.46
2019-10-10 22:00 | 8.94 | 8.91
2019-10-10 22:30 | 8.21 | 8.17
2019-10-10 23:00 | 7.67 | 7.61
2019-10-10 23:30 | 6.75 | 6.68
2019-10-11 | 5.9 | 5.81
2019-10-11 00:30 | 5.19 | 5.08
2019-10-11 01:00 | 5.07 | 4.96
2019-10-11 01:30 | 4.82 | 4.69
2019-10-11 02:00 | 4.56 | 4.43
2019-10-11 02:30 | 4.39 | 4.24
2019-10-11 03:00 | 4.3 | 4.15
2019-10-11 03:30 | 4.4 | 4.24
2019-10-11 04:00 | 4.43 | 4.28
2019-10-11 04:30 | 4.53 | 4.38
2019-10-11 05:00 | 4.81 | 4.68
2019-10-11 05:30 | 5.22 | 5.06
2019-10-11 06:00 | 5.62 | 5.46
2019-10-11 06:30 | 5.89 | 5.74
2019-10-11 07:00 | 5.71 | 5.59
2019-10-11 07:30 | 5.49 | 5.39
2019-10-11 08:00 | 5.17 | 5.09
2019-10-11 08:30 | 3.41 | 3.32
2019-10-11 09:00 | 2.54 | 2.46
2019-10-11 09:30 | 3.25 | 3.18
2019-10-11 10:00 | 3.45 | 3.38
2019-10-11 10:30 | 4.09 | 4.02
2019-10-11 11:00 | 3.1 | 3.02
2019-10-11 11:30 | 3.47 | 3.39
2019-10-11 12:00 | 3.16 | 3.07
2019-10-11 12:30 | 5.08 | 5.02
2019-10-11 13:00 | 1.97 | 1.85
2019-10-11 13:30 | 0.99 | 0.75
2019-10-11 14:00 | 2.28 | 2.17
2019-10-11 14:30 | 2.82 | 2.73
2019-10-11 15:00 | 6.16 | 6.11
2019-10-11 15:30 | 7.41 | 7.36
2019-10-11 16:00 | 8.36 | 8.3
2019-10-11 16:30 | 8.95 | 8.9
2019-10-11 17:00 | 7.99 | 7.93
2019-10-11 17:30 | 8.53 | 8.47
2019-10-11 18:00 | 9.44 | 9.4
2019-10-11 18:30 | 10.42 | 10.41
2019-10-11 19:00 | 10.76 | 10.75
2019-10-11 19:30 | 10.54 | 10.52
2019-10-11 20:00 | 10.41 | 10.4
2019-10-11 20:30 | 10.31 | 10.3
2019-10-11 21:00 | 9.62 | 9.6
2019-10-11 21:30 | 8.97 | 8.94
2019-10-11 22:00 | 8.5 | 8.45
2019-10-11 22:30 | 8.3 | 8.25
2019-10-11 23:00 | 7.93 | 7.88
2019-10-11 23:30 | 7.2 | 7.13
2019-10-12 | 6.37 | 6.28
2019-10-12 00:30 | 5.64 | 5.54
2019-10-12 01:00 | 5.32 | 5.2
2019-10-12 01:30 | 5.02 | 4.9
2019-10-12 02:00 | 4.67 | 4.54
2019-10-12 02:30 | 4.38 | 4.23
2019-10-12 03:00 | 4.26 | 4.1
2019-10-12 03:30 | 4.39 | 4.24
2019-10-12 04:00 | 4.48 | 4.33
2019-10-12 04:30 | 4.46 | 4.32
2019-10-12 05:00 | 4.49 | 4.35
2019-10-12 05:30 | 4.65 | 4.5
2019-10-12 06:00 | 4.83 | 4.62
2019-10-12 06:30 | 5.21 | 5.01
2019-10-12 07:00 | 5.74 | 5.57
2019-10-12 07:30 | 6.35 | 6.19
2019-10-12 08:00 | 6.61 | 6.47
2019-10-12 08:30 | 6.69 | 6.57
2019-10-12 09:00 | 7.64 | 7.56
2019-10-12 09:30 | 7.79 | 7.71
2019-10-12 10:00 | 6.99 | 6.91
2019-10-12 10:30 | 7.73 | 7.65
2019-10-12 11:00 | 7.71 | 7.64
2019-10-12 11:30 | 8.34 | 8.28
2019-10-12 12:00 | 8.84 | 8.78
2019-10-12 12:30 | 6.45 | 6.39
2019-10-12 13:00 | 2.41 | 2.28
2019-10-12 13:30 | 2.11 | 1.96
2019-10-12 14:00 | 3.32 | 3.21
2019-10-12 14:30 | 3.36 | 3.24
2019-10-12 15:00 | 3.38 | 3.26
2019-10-12 15:30 | 4.02 | 3.92
2019-10-12 16:00 | 5.02 | 4.94
2019-10-12 16:30 | 6.1 | 6.04
2019-10-12 17:00 | 7.23 | 7.17
2019-10-12 17:30 | 8.37 | 8.31
2019-10-12 18:00 | 9.26 | 9.21
2019-10-12 18:30 | 10.17 | 10.15
2019-10-12 19:00 | 10.7 | 10.69
2019-10-12 19:30 | 10.38 | 10.37
2019-10-12 20:00 | 10.33 | 10.31
2019-10-12 20:30 | 10.15 | 10.12
2019-10-12 21:00 | 9.66 | 9.63
2019-10-12 21:30 | 8.97 | 8.93
2019-10-12 22:00 | 8.71 | 8.66
2019-10-12 22:30 | 8.36 | 8.3
2019-10-12 23:00 | 8.14 | 8.08
2019-10-12 23:30 | 7.46 | 7.39
2019-10-13 | 6.67 | 6.59
2019-10-13 00:30 | 5.92 | 5.82
2019-10-13 01:00 | 5.63 | 5.53
2019-10-13 01:30 | 5.16 | 5.03
2019-10-13 02:00 | 4.82 | 4.69
2019-10-13 02:30 | 4.63 | 4.49
2019-10-13 03:00 | 4.54 | 4.39
2019-10-13 03:30 | 4.6 | 4.46
2019-10-13 04:00 | 4.49 | 4.33
2019-10-13 04:30 | 4.52 | 4.36
2019-10-13 05:00 | 4.54 | 4.38
2019-10-13 05:30 | 4.56 | 4.31
2019-10-13 06:00 | 4.47 | 4.17
2019-10-13 06:30 | 4.13 | 3.83
2019-10-13 07:00 | 3.73 | 3.4
2019-10-13 07:30 | 3.42 | 3.12
2019-10-13 08:00 | 3.24 | 2.98
2019-10-13 08:30 | 2.99 | 2.78
2019-10-13 09:00 | 2.59 | 2.41
2019-10-13 09:30 | 2.29 | 2.11
2019-10-13 10:00 | 2.53 | 2.4
2019-10-13 10:30 | 2.38 | 2.27
2019-10-13 11:00 | 2.81 | 2.72
2019-10-13 11:30 | 3 | 2.92
2019-10-13 12:00 | 2.35 | 2.25
2019-10-13 12:30 | 2.23 | 2.14
2019-10-13 13:00 | 3.15 | 3.09
2019-10-13 13:30 | 4.15 | 4.09
2019-10-13 14:00 | 3.75 | 3.69
2019-10-13 14:30 | 2.87 | 2.8
2019-10-13 15:00 | 3.71 | 3.65
2019-10-13 15:30 | 6.03 | 5.99
2019-10-13 16:00 | 6.2 | 6.16
2019-10-13 16:30 | 6.82 | 6.77
2019-10-13 17:00 | 8.73 | 8.7
2019-10-13 17:30 | 9.42 | 9.39
2019-10-13 18:00 | 10.27 | 10.23
2019-10-13 18:30 | 11.23 | 11.22
2019-10-13 19:00 | 11.52 | 11.51
2019-10-13 19:30 | 11.15 | 11.14
2019-10-13 20:00 | 11.02 | 11
2019-10-13 20:30 | 10.82 | 10.81
2019-10-13 21:00 | 10.17 | 10.15
2019-10-13 21:30 | 9.35 | 9.32
2019-10-13 22:00 | 8.5 | 8.46
2019-10-13 22:30 | 7.91 | 7.86
2019-10-13 23:00 | 7.68 | 7.62
2019-10-13 23:30 | 6.76 | 6.69
2019-10-14 | 5.91 | 5.81
2019-10-14 00:30 | 5.35 | 5.23
2019-10-14 01:00 | 5.05 | 4.92
2019-10-14 01:30 | 4.78 | 4.64
2019-10-14 02:00 | 4.54 | 4.39
2019-10-14 02:30 | 4.38 | 4.21
2019-10-14 03:00 | 4.3 | 4.13
2019-10-14 03:30 | 4.31 | 4.14
2019-10-14 04:00 | 4.4 | 4.23
2019-10-14 04:30 | 4.58 | 4.42
2019-10-14 05:00 | 4.82 | 4.67
2019-10-14 05:30 | 5.21 | 5.03
2019-10-14 06:00 | 5.51 | 5.33
2019-10-14 06:30 | 5.85 | 5.72
2019-10-14 07:00 | 5.99 | 5.88
2019-10-14 07:30 | 5.33 | 5.23
2019-10-14 08:00 | 4.58 | 4.49
2019-10-14 08:30 | 3.42 | 3.32
2019-10-14 09:00 | 2.12 | 2
2019-10-14 09:30 | 1.75 | 1.63
2019-10-14 10:00 | 2.97 | 2.9
2019-10-14 10:30 | 2.18 | 2.11
2019-10-14 11:00 | 1.86 | 1.79
2019-10-14 11:30 | 1.75 | 1.69
2019-10-14 12:00 | 1.58 | 1.54
2019-10-14 12:30 | 2.1 | 2.07
2019-10-14 13:00 | 2.25 | 2.23
2019-10-14 13:30 | 2.66 | 2.64
2019-10-14 14:00 | 3.59 | 3.57
2019-10-14 14:30 | 3.13 | 3.11
2019-10-14 15:00 | 3.68 | 3.67
2019-10-14 15:30 | 4.85 | 4.84
2019-10-14 16:00 | 6.26 | 6.26
2019-10-14 16:30 | 7.51 | 7.5
2019-10-14 17:00 | 8.93 | 8.92
2019-10-14 17:30 | 10.1 | 10.09
2019-10-14 18:00 | 10.95 | 10.94
2019-10-14 18:30 | 11.93 | 11.92
2019-10-14 19:00 | 12.51 | 12.5
2019-10-14 19:30 | 11.98 | 11.97
2019-10-14 20:00 | 11.92 | 11.92
2019-10-14 20:30 | 11.63 | 11.63
2019-10-14 21:00 | 10.94 | 10.94
2019-10-14 21:30 | 9.85 | 9.83
2019-10-14 22:00 | 8.7 | 8.66
2019-10-14 22:30 | 8.14 | 8.09
2019-10-14 23:00 | 7.64 | 7.59
2019-10-14 23:30 | 6.71 | 6.64
2019-10-15 | 5.89 | 5.8
2019-10-15 00:30 | 5.33 | 5.24
2019-10-15 01:00 | 5.04 | 4.94
2019-10-15 01:30 | 4.78 | 4.66
2019-10-15 02:00 | 4.54 | 4.4
2019-10-15 02:30 | 4.35 | 4.2
2019-10-15 03:00 | 4.37 | 4.23
2019-10-15 03:30 | 4.34 | 4.19
2019-10-15 04:00 | 4.38 | 4.24
2019-10-15 04:30 | 4.57 | 4.44
2019-10-15 05:00 | 4.77 | 4.65
2019-10-15 05:30 | 5.08 | 4.95
2019-10-15 06:00 | 5.57 | 5.42
2019-10-15 06:30 | 5.93 | 5.8
2019-10-15 07:00 | 6.12 | 6.01
2019-10-15 07:30 | 6.71 | 6.63
2019-10-15 08:00 | 6.44 | 6.37
2019-10-15 08:30 | 5.37 | 5.29
2019-10-15 09:00 | 3.9 | 3.82
2019-10-15 09:30 | 3.92 | 3.84
2019-10-15 10:00 | 4.17 | 4.11
2019-10-15 10:30 | 3.31 | 3.25
2019-10-15 11:00 | 2.55 | 2.49
2019-10-15 11:30 | 1.9 | 1.85
2019-10-15 12:00 | 2.81 | 2.77
2019-10-15 12:30 | 2.77 | 2.75
2019-10-15 13:00 | 3.4 | 3.38
2019-10-15 13:30 | 3.89 | 3.87
2019-10-15 14:00 | 5.16 | 5.15
2019-10-15 14:30 | 5.53 | 5.52
2019-10-15 15:00 | 5.07 | 5.07
2019-10-15 15:30 | 6.04 | 6.03
2019-10-15 16:00 | 7.25 | 7.24
2019-10-15 16:30 | 8.39 | 8.38
2019-10-15 17:00 | 9.66 | 9.66
2019-10-15 17:30 | 10.52 | 10.52
2019-10-15 18:00 | 11.2 | 11.2
2019-10-15 18:30 | 12.47 | 12.47
2019-10-15 19:00 | 13.02 | 13.01
2019-10-15 19:30 | 12.6 | 12.6
2019-10-15 20:00 | 12.32 | 12.32
2019-10-15 20:30 | 12.19 | 12.18
2019-10-15 21:00 | 11.36 | 11.36
2019-10-15 21:30 | 10.37 | 10.36
2019-10-15 22:00 | 9.28 | 9.26
2019-10-15 22:30 | 8.49 | 8.46
2019-10-15 23:00 | 8.11 | 8.08
2019-10-15 23:30 | 7.13 | 7.08
2019-10-16 | 6.27 | 6.21
2019-10-16 00:30 | 5.7 | 5.62
2019-10-16 01:00 | 5.51 | 5.43
2019-10-16 01:30 | 5.16 | 5.07
2019-10-16 02:00 | 4.81 | 4.7
2019-10-16 02:30 | 4.73 | 4.61
2019-10-16 03:00 | 4.56 | 4.44
2019-10-16 03:30 | 4.61 | 4.48
2019-10-16 04:00 | 4.65 | 4.53
2019-10-16 04:30 | 4.87 | 4.76
2019-10-16 05:00 | 5.06 | 4.95
2019-10-16 05:30 | 5.31 | 5.16
2019-10-16 06:00 | 5.8 | 5.66
2019-10-16 06:30 | 6.05 | 5.95
2019-10-16 07:00 | 5.81 | 5.73
2019-10-16 07:30 | 6 | 5.94
2019-10-16 08:00 | 5.66 | 5.62
2019-10-16 08:30 | 4.44 | 4.41
2019-10-16 09:00 | 4.2 | 4.18
2019-10-16 09:30 | 4.17 | 4.16
2019-10-16 10:00 | 2.73 | 2.71
2019-10-16 10:30 | 2.42 | 2.41
2019-10-16 11:00 | 2.55 | 2.54
2019-10-16 11:30 | 2.96 | 2.94
2019-10-16 12:00 | 3.13 | 3.1
2019-10-16 12:30 | 3.68 | 3.66
2019-10-16 13:00 | 4.23 | 4.21
2019-10-16 13:30 | 4.89 | 4.87
2019-10-16 14:00 | 5.68 | 5.66
2019-10-16 14:30 | 6.31 | 6.29
2019-10-16 15:00 | 6.88 | 6.86
2019-10-16 15:30 | 8.16 | 8.14
2019-10-16 16:00 | 9.47 | 9.46
2019-10-16 16:30 | 10.53 | 10.52
2019-10-16 17:00 | 11.63 | 11.62
2019-10-16 17:30 | 12.28 | 12.27
2019-10-16 18:00 | 12.62 | 12.61
2019-10-16 18:30 | 13.47 | 13.46
2019-10-16 19:00 | 13.86 | 13.85
2019-10-16 19:30 | 13.2 | 13.2
2019-10-16 20:00 | 12.88 | 12.87
2019-10-16 20:30 | 12.65 | 12.64
2019-10-16 21:00 | 11.68 | 11.68
2019-10-16 21:30 | 10.58 | 10.57
2019-10-16 22:00 | 9.73 | 9.72
2019-10-16 22:30 | 9 | 8.98
2019-10-16 23:00 | 8.56 | 8.53
2019-10-16 23:30 | 7.57 | 7.53
2019-10-17 | 6.57 | 6.51
2019-10-17 00:30 | 5.86 | 5.79
2019-10-17 01:00 | 5.53 | 5.46
2019-10-17 01:30 | 5.27 | 5.19
2019-10-17 02:00 | 5.01 | 4.91
2019-10-17 02:30 | 4.96 | 4.85
2019-10-17 03:00 | 4.76 | 4.64
2019-10-17 03:30 | 4.81 | 4.7
2019-10-17 04:00 | 4.86 | 4.75
2019-10-17 04:30 | 5.04 | 4.94
2019-10-17 05:00 | 5.29 | 5.2
2019-10-17 05:30 | 5.37 | 5.22
2019-10-17 06:00 | 5.63 | 5.48
2019-10-17 06:30 | 5.46 | 5.35
2019-10-17 07:00 | 6.58 | 6.52
2019-10-17 07:30 | 6.16 | 6.12
2019-10-17 08:00 | 4.9 | 4.86
2019-10-17 08:30 | 4.79 | 4.77
2019-10-17 09:00 | 3.82 | 3.8
2019-10-17 09:30 | 4.53 | 4.52
2019-10-17 10:00 | 5.5 | 5.5
2019-10-17 10:30 | 3.94 | 3.94
2019-10-17 11:00 | 3.17 | 3.15
2019-10-17 11:30 | 3.7 | 3.68
2019-10-17 12:00 | 4.42 | 4.4
2019-10-17 12:30 | 5.31 | 5.28
2019-10-17 13:00 | 6.05 | 6.01
2019-10-17 13:30 | 6.87 | 6.83
2019-10-17 14:00 | 7.72 | 7.68
2019-10-17 14:30 | 10.97 | 10.94
2019-10-17 15:00 | 9.85 | 9.83
2019-10-17 15:30 | 11.37 | 11.36
2019-10-17 16:00 | 12.41 | 12.4
2019-10-17 16:30 | 12.58 | 12.57
2019-10-17 17:00 | 11.13 | 11.12
2019-10-17 17:30 | 11.53 | 11.52
2019-10-17 18:00 | 11.91 | 11.9
2019-10-17 18:30 | 12.78 | 12.77
2019-10-17 19:00 | 13.16 | 13.16
2019-10-17 19:30 | 12.91 | 12.9
2019-10-17 20:00 | 10.22 | 10.21
2019-10-17 20:30 | 9.77 | 9.76
2019-10-17 21:00 | 9.16 | 9.15
2019-10-17 21:30 | 8.56 | 8.54
2019-10-17 22:00 | 9.42 | 9.41
2019-10-17 22:30 | 9.78 | 9.77
2019-10-17 23:00 | 8.72 | 8.7
2019-10-17 23:30 | 7.48 | 7.44
2019-10-18 | 6.54 | 6.49
2019-10-18 00:30 | 5.96 | 5.9
2019-10-18 01:00 | 5.57 | 5.49
2019-10-18 01:30 | 5.36 | 5.27
2019-10-18 02:00 | 4.99 | 4.89
2019-10-18 02:30 | 4.94 | 4.83
2019-10-18 03:00 | 4.87 | 4.77
2019-10-18 03:30 | 4.93 | 4.83
2019-10-18 04:00 | 4.8 | 4.68
2019-10-18 04:30 | 4.89 | 4.78
2019-10-18 05:00 | 5.1 | 4.99
2019-10-18 05:30 | 5.33 | 5.18
2019-10-18 06:00 | 5.61 | 5.46
2019-10-18 06:30 | 5.68 | 5.59
2019-10-18 07:00 | 6.22 | 6.16
2019-10-18 07:30 | 5.41 | 5.35
2019-10-18 08:00 | 4.66 | 4.61
2019-10-18 08:30 | 4.07 | 4.03
2019-10-18 09:00 | 2.83 | 2.81
2019-10-18 09:30 | 2.59 | 2.58
2019-10-18 10:00 | 3.2 | 3.18
2019-10-18 10:30 | 2.47 | 2.44
2019-10-18 11:00 | 1.8 | 1.75
2019-10-18 11:30 | 1.89 | 1.84
2019-10-18 12:00 | 1.9 | 1.84
2019-10-18 12:30 | 2.25 | 2.19
2019-10-18 13:00 | 2.61 | 2.57
2019-10-18 13:30 | 3.13 | 3.09
2019-10-18 14:00 | 3.85 | 3.81
2019-10-18 14:30 | 4.46 | 4.43
2019-10-18 15:00 | 5.1 | 5.07
2019-10-18 15:30 | 6.29 | 6.26
2019-10-18 16:00 | 7.47 | 7.45
2019-10-18 16:30 | 8.56 | 8.54
2019-10-18 17:00 | 9.54 | 9.52
2019-10-18 17:30 | 10.08 | 10.06
2019-10-18 18:00 | 10.33 | 10.32
2019-10-18 18:30 | 10.89 | 10.88
2019-10-18 19:00 | 11.45 | 11.44
2019-10-18 19:30 | 11.08 | 11.08
2019-10-18 20:00 | 11 | 11
2019-10-18 20:30 | 10.72 | 10.71
2019-10-18 21:00 | 10.34 | 10.34
2019-10-18 21:30 | 9.59 | 9.57
2019-10-18 22:00 | 8.91 | 8.89
2019-10-18 22:30 | 8.52 | 8.49
2019-10-18 23:00 | 8.21 | 8.17
2019-10-18 23:30 | 7.26 | 7.21
2019-10-19 | 6.6 | 6.54
2019-10-19 00:30 | 5.9 | 5.82
2019-10-19 01:00 | 5.55 | 5.46
2019-10-19 01:30 | 5.15 | 5.04
2019-10-19 02:00 | 4.89 | 4.78
2019-10-19 02:30 | 4.81 | 4.69
2019-10-19 03:00 | 4.74 | 4.62
2019-10-19 03:30 | 4.66 | 4.53
2019-10-19 04:00 | 4.62 | 4.48
2019-10-19 04:30 | 4.62 | 4.49
2019-10-19 05:00 | 4.74 | 4.62
2019-10-19 05:30 | 4.61 | 4.4
2019-10-19 06:00 | 4.82 | 4.61
2019-10-19 06:30 | 4.8 | 4.59
2019-10-19 07:00 | 4.93 | 4.74
2019-10-19 07:30 | 4.09 | 3.91
2019-10-19 08:00 | 4.4 | 4.27
2019-10-19 08:30 | 4.74 | 4.65
2019-10-19 09:00 | 6.75 | 6.7
2019-10-19 09:30 | 5.82 | 5.77
2019-10-19 10:00 | 6.35 | 6.31
2019-10-19 10:30 | 3.45 | 3.41
2019-10-19 11:00 | 8.19 | 8.17
2019-10-19 11:30 | 8.34 | 8.32
2019-10-19 12:00 | 8.18 | 8.15
2019-10-19 12:30 | 4.1 | 4.06
2019-10-19 13:00 | 3.16 | 3.11
2019-10-19 13:30 | 3.01 | 2.96
2019-10-19 14:00 | 4.15 | 4.12
2019-10-19 14:30 | 6.41 | 6.39
2019-10-19 15:00 | 6.12 | 6.1
2019-10-19 15:30 | 5.97 | 5.95
2019-10-19 16:00 | 7.68 | 7.66
2019-10-19 16:30 | 8.76 | 8.74
2019-10-19 17:00 | 9.13 | 9.12
2019-10-19 17:30 | 9.78 | 9.77
2019-10-19 18:00 | 10.47 | 10.46
2019-10-19 18:30 | 11.01 | 11
2019-10-19 19:00 | 11.52 | 11.52
2019-10-19 19:30 | 11.37 | 11.36
2019-10-19 20:00 | 11.12 | 11.12
2019-10-19 20:30 | 10.84 | 10.83
2019-10-19 21:00 | 10.1 | 10.09
2019-10-19 21:30 | 9.5 | 9.48
2019-10-19 22:00 | 8.86 | 8.83
2019-10-19 22:30 | 8.51 | 8.47
2019-10-19 23:00 | 8.26 | 8.22
2019-10-19 23:30 | 7.4 | 7.34
2019-10-20 | 6.65 | 6.58
2019-10-20 00:30 | 6.06 | 5.97
2019-10-20 01:00 | 5.73 | 5.64
2019-10-20 01:30 | 5.31 | 5.2
2019-10-20 02:00 | 4.92 | 4.79
2019-10-20 02:30 | 4.73 | 4.59
2019-10-20 03:00 | 4.72 | 4.58
2019-10-20 03:30 | 4.58 | 4.44
2019-10-20 04:00 | 4.5 | 4.35
2019-10-20 04:30 | 4.5 | 4.34
2019-10-20 05:00 | 4.53 | 4.38
2019-10-20 05:30 | 4.46 | 4.22
2019-10-20 06:00 | 4.43 | 4.16
2019-10-20 06:30 | 4.37 | 4.11
2019-10-20 07:00 | 3.97 | 3.68
2019-10-20 07:30 | 3.41 | 3.13
2019-10-20 08:00 | 3.39 | 3.16
2019-10-20 08:30 | 3.12 | 2.94
2019-10-20 09:00 | 2.99 | 2.87
2019-10-20 09:30 | 2.93 | 2.85
2019-10-20 10:00 | 2.58 | 2.52
2019-10-20 10:30 | 2.11 | 2.05
2019-10-20 11:00 | 1.99 | 1.93
2019-10-20 11:30 | 2.17 | 2.11
2019-10-20 12:00 | 2.43 | 2.37
2019-10-20 12:30 | 2.76 | 2.71
2019-10-20 13:00 | 4.54 | 4.5
2019-10-20 13:30 | 6.27 | 6.25
2019-10-20 14:00 | 5.1 | 5.07
2019-10-20 14:30 | 4.89 | 4.86
2019-10-20 15:00 | 5.57 | 5.55
2019-10-20 15:30 | 6.47 | 6.46
2019-10-20 16:00 | 7.45 | 7.44
2019-10-20 16:30 | 8.37 | 8.36
2019-10-20 17:00 | 9.48 | 9.47
2019-10-20 17:30 | 10.52 | 10.51
2019-10-20 18:00 | 11.05 | 11.04
2019-10-20 18:30 | 11.53 | 11.53
2019-10-20 19:00 | 11.7 | 11.69
2019-10-20 19:30 | 11.1 | 11.09
2019-10-20 20:00 | 10.76 | 10.75
2019-10-20 20:30 | 10.5 | 10.49
2019-10-20 21:00 | 9.81 | 9.78
2019-10-20 21:30 | 9.22 | 9.19
2019-10-20 22:00 | 8.49 | 8.46
2019-10-20 22:30 | 8.01 | 7.96
2019-10-20 23:00 | 7.77 | 7.72
2019-10-20 23:30 | 6.95 | 6.88
2019-10-21 | 6.16 | 6.07
2019-10-21 00:30 | 5.73 | 5.64
2019-10-21 01:00 | 5.43 | 5.33
2019-10-21 01:30 | 5.17 | 5.06
2019-10-21 02:00 | 4.89 | 4.77
2019-10-21 02:30 | 4.65 | 4.52
2019-10-21 03:00 | 4.65 | 4.51
2019-10-21 03:30 | 4.58 | 4.44
2019-10-21 04:00 | 4.66 | 4.52
2019-10-21 04:30 | 4.84 | 4.71
2019-10-21 05:00 | 5.02 | 4.89
2019-10-21 05:30 | 5.25 | 5.06
2019-10-21 06:00 | 5.34 | 5.16
2019-10-21 06:30 | 4.97 | 4.8
2019-10-21 07:00 | 4.7 | 4.54
2019-10-21 07:30 | 4.42 | 4.29
2019-10-21 08:00 | 3.59 | 3.47
2019-10-21 08:30 | 3.29 | 3.21
2019-10-21 09:00 | 4.03 | 3.97
2019-10-21 09:30 | 3.35 | 3.29
2019-10-21 10:00 | 2.66 | 2.61
2019-10-21 10:30 | 2 | 1.95
2019-10-21 11:00 | 2 | 1.96
2019-10-21 11:30 | 2.15 | 2.11
2019-10-21 12:00 | 2.33 | 2.3
2019-10-21 12:30 | 2.7 | 2.68
2019-10-21 13:00 | 3.01 | 3
2019-10-21 13:30 | 3.05 | 3.03
2019-10-21 14:00 | 3.22 | 3.19
2019-10-21 14:30 | 3.11 | 3.09
2019-10-21 15:00 | 3.54 | 3.52
2019-10-21 15:30 | 4.3 | 4.27
2019-10-21 16:00 | 5.47 | 5.45
2019-10-21 16:30 | 6.73 | 6.7
2019-10-21 17:00 | 8.2 | 8.17
2019-10-21 17:30 | 9.51 | 9.49
2019-10-21 18:00 | 10.5 | 10.48
2019-10-21 18:30 | 11.38 | 11.37
2019-10-21 19:00 | 12 | 11.99
2019-10-21 19:30 | 11.65 | 11.65
2019-10-21 20:00 | 11.35 | 11.35
2019-10-21 20:30 | 11.12 | 11.11
2019-10-21 21:00 | 10.27 | 10.26
2019-10-21 21:30 | 9.47 | 9.44
2019-10-21 22:00 | 8.63 | 8.59
2019-10-21 22:30 | 8.04 | 8
2019-10-21 23:00 | 7.71 | 7.65
2019-10-21 23:30 | 6.9 | 6.83
2019-10-22 | 6.06 | 5.97
2019-10-22 00:30 | 5.55 | 5.44
2019-10-22 01:00 | 5.2 | 5.09
2019-10-22 01:30 | 4.87 | 4.74
2019-10-22 02:00 | 4.7 | 4.56
2019-10-22 02:30 | 4.6 | 4.46
2019-10-22 03:00 | 4.51 | 4.37
2019-10-22 03:30 | 4.49 | 4.33
2019-10-22 04:00 | 4.59 | 4.44
2019-10-22 04:30 | 4.75 | 4.61
2019-10-22 05:00 | 5.12 | 4.98
2019-10-22 05:30 | 5.64 | 5.47
2019-10-22 06:00 | 5.69 | 5.52
2019-10-22 06:30 | 5.8 | 5.67
2019-10-22 07:00 | 6.01 | 5.9
2019-10-22 07:30 | 5.25 | 5.15
2019-10-22 08:00 | 5.32 | 5.23
2019-10-22 08:30 | 5.14 | 5.07
2019-10-22 09:00 | 3.59 | 3.52
2019-10-22 09:30 | 3.64 | 3.58
2019-10-22 10:00 | 3.62 | 3.58
2019-10-22 10:30 | 2.97 | 2.94
2019-10-22 11:00 | 2.94 | 2.91
2019-10-22 11:30 | 3.43 | 3.4
2019-10-22 12:00 | 3.98 | 3.96
2019-10-22 12:30 | 3.74 | 3.72
2019-10-22 13:00 | 4.77 | 4.75
2019-10-22 13:30 | 3.86 | 3.83
2019-10-22 14:00 | 5.03 | 5
2019-10-22 14:30 | 4.5 | 4.48
2019-10-22 15:00 | 5.51 | 5.49
2019-10-22 15:30 | 5.88 | 5.86
2019-10-22 16:00 | 6.23 | 6.22
2019-10-22 16:30 | 6.94 | 6.92
2019-10-22 17:00 | 8.28 | 8.26
2019-10-22 17:30 | 9.45 | 9.44
2019-10-22 18:00 | 10.24 | 10.22
2019-10-22 18:30 | 11.13 | 11.12
2019-10-22 19:00 | 12.04 | 12.04
2019-10-22 19:30 | 11.54 | 11.54
2019-10-22 20:00 | 11.35 | 11.34
2019-10-22 20:30 | 11.04 | 11.03
2019-10-22 21:00 | 10.28 | 10.27
2019-10-22 21:30 | 9.32 | 9.29
2019-10-22 22:00 | 8.58 | 8.54
2019-10-22 22:30 | 8.06 | 8.01
2019-10-22 23:00 | 7.81 | 7.76
2019-10-22 23:30 | 6.9 | 6.83
2019-10-23 | 6 | 5.92
2019-10-23 00:30 | 5.48 | 5.37
2019-10-23 01:00 | 5.29 | 5.18
2019-10-23 01:30 | 4.92 | 4.79
2019-10-23 02:00 | 4.63 | 4.49
2019-10-23 02:30 | 4.55 | 4.41
2019-10-23 03:00 | 4.46 | 4.32
2019-10-23 03:30 | 4.51 | 4.36
2019-10-23 04:00 | 4.56 | 4.42
2019-10-23 04:30 | 4.71 | 4.57
2019-10-23 05:00 | 5.14 | 5.01
2019-10-23 05:30 | 5.61 | 5.44
2019-10-23 06:00 | 5.85 | 5.7
2019-10-23 06:30 | 5.52 | 5.38
2019-10-23 07:00 | 5.23 | 5.11
2019-10-23 07:30 | 4.79 | 4.7
2019-10-23 08:00 | 3.89 | 3.81
2019-10-23 08:30 | 3.36 | 3.3
2019-10-23 09:00 | 2.54 | 2.47
2019-10-23 09:30 | 1.66 | 1.59
2019-10-23 10:00 | 1.65 | 1.61
2019-10-23 10:30 | 1.45 | 1.42
2019-10-23 11:00 | 1.29 | 1.27
2019-10-23 11:30 | 1.15 | 1.12
2019-10-23 12:00 | 1.21 | 1.19
2019-10-23 12:30 | 1.45 | 1.43
2019-10-23 13:00 | 1.82 | 1.79
2019-10-23 13:30 | 1.92 | 1.89
2019-10-23 14:00 | 2.3 | 2.27
2019-10-23 14:30 | 3.06 | 3.04
2019-10-23 15:00 | 3.72 | 3.7
2019-10-23 15:30 | 4.81 | 4.79
2019-10-23 16:00 | 6.28 | 6.26
2019-10-23 16:30 | 7.47 | 7.46
2019-10-23 17:00 | 8.76 | 8.76
2019-10-23 17:30 | 9.75 | 9.74
2019-10-23 18:00 | 10.39 | 10.38
2019-10-23 18:30 | 11.35 | 11.34
2019-10-23 19:00 | 12.33 | 12.33
2019-10-23 19:30 | 11.86 | 11.86
2019-10-23 20:00 | 11.69 | 11.69
2019-10-23 20:30 | 11.19 | 11.18
2019-10-23 21:00 | 10.45 | 10.44
2019-10-23 21:30 | 9.66 | 9.65
2019-10-23 22:00 | 8.76 | 8.73
2019-10-23 22:30 | 8.22 | 8.18
2019-10-23 23:00 | 7.86 | 7.81
2019-10-23 23:30 | 7 | 6.93
2019-10-24 | 6.18 | 6.1
2019-10-24 00:30 | 5.47 | 5.37
2019-10-24 01:00 | 5.23 | 5.11
2019-10-24 01:30 | 4.96 | 4.83
2019-10-24 02:00 | 4.73 | 4.6
2019-10-24 02:30 | 4.58 | 4.43
2019-10-24 03:00 | 4.56 | 4.42
2019-10-24 03:30 | 4.6 | 4.44
2019-10-24 04:00 | 4.65 | 4.5
2019-10-24 04:30 | 4.79 | 4.65
2019-10-24 05:00 | 5.2 | 5.06
2019-10-24 05:30 | 5.47 | 5.28
2019-10-24 06:00 | 5.82 | 5.66
2019-10-24 06:30 | 5.62 | 5.47
2019-10-24 07:00 | 5.32 | 5.21
2019-10-24 07:30 | 4.83 | 4.72
2019-10-24 08:00 | 3.84 | 3.73
2019-10-24 08:30 | 3.03 | 2.93
2019-10-24 09:00 | 2.38 | 2.3
2019-10-24 09:30 | 2.02 | 1.95
2019-10-24 10:00 | 1.63 | 1.57
2019-10-24 10:30 | 1.39 | 1.34
2019-10-24 11:00 | 1.56 | 1.53
2019-10-24 11:30 | 1.49 | 1.47
2019-10-24 12:00 | 1.38 | 1.35
2019-10-24 12:30 | 1.57 | 1.55
2019-10-24 13:00 | 2.01 | 1.98
2019-10-24 13:30 | 2.34 | 2.3
2019-10-24 14:00 | 2.71 | 2.66
2019-10-24 14:30 | 3.37 | 3.35
2019-10-24 15:00 | 4.01 | 3.99
2019-10-24 15:30 | 5.18 | 5.17
2019-10-24 16:00 | 6.58 | 6.56
2019-10-24 16:30 | 7.88 | 7.87
2019-10-24 17:00 | 9.13 | 9.12
2019-10-24 17:30 | 9.9 | 9.89
2019-10-24 18:00 | 10.51 | 10.5
2019-10-24 18:30 | 11.21 | 11.21
2019-10-24 19:00 | 11.77 | 11.77
2019-10-24 19:30 | 11.66 | 11.66
2019-10-24 20:00 | 11.39 | 11.39
2019-10-24 20:30 | 11.12 | 11.11
2019-10-24 21:00 | 10.39 | 10.39
2019-10-24 21:30 | 9.51 | 9.49
2019-10-24 22:00 | 8.77 | 8.75
2019-10-24 22:30 | 8.24 | 8.2
2019-10-24 23:00 | 7.86 | 7.81
2019-10-24 23:30 | 7.08 | 7.02
2019-10-25 | 6.2 | 6.12
2019-10-25 00:30 | 5.62 | 5.53
2019-10-25 01:00 | 5.34 | 5.24
2019-10-25 01:30 | 5.01 | 4.89
2019-10-25 02:00 | 4.86 | 4.73
2019-10-25 02:30 | 4.68 | 4.55
2019-10-25 03:00 | 4.7 | 4.57
2019-10-25 03:30 | 4.61 | 4.47
2019-10-25 04:00 | 4.66 | 4.51
2019-10-25 04:30 | 4.77 | 4.63
2019-10-25 05:00 | 4.98 | 4.83
2019-10-25 05:30 | 5.19 | 4.99
2019-10-25 06:00 | 5.26 | 5.07
2019-10-25 06:30 | 5.11 | 4.93
2019-10-25 07:00 | 4.83 | 4.69
2019-10-25 07:30 | 4.44 | 4.32
2019-10-25 08:00 | 3.63 | 3.52
2019-10-25 08:30 | 2.75 | 2.63
2019-10-25 09:00 | 2.16 | 2.04
2019-10-25 09:30 | 1.34 | 1.22
2019-10-25 10:00 | 0.95 | 0.85
2019-10-25 10:30 | 0.73 | 0.59
2019-10-25 11:00 | 0.75 | 0.64
2019-10-25 11:30 | 1.1 | 1.01
2019-10-25 12:00 | 1.28 | 1.19
2019-10-25 12:30 | 1.56 | 1.5
2019-10-25 13:00 | 2.07 | 2.02
2019-10-25 13:30 | 2.54 | 2.49
2019-10-25 14:00 | 3.16 | 3.12
2019-10-25 14:30 | 3.88 | 3.84
2019-10-25 15:00 | 4.45 | 4.42
2019-10-25 15:30 | 5.55 | 5.53
2019-10-25 16:00 | 6.88 | 6.86
2019-10-25 16:30 | 8 | 7.98
2019-10-25 17:00 | 9.22 | 9.21
2019-10-25 17:30 | 9.69 | 9.68
2019-10-25 18:00 | 9.88 | 9.87
2019-10-25 18:30 | 10.38 | 10.37
2019-10-25 19:00 | 11.12 | 11.11
2019-10-25 19:30 | 10.88 | 10.88
2019-10-25 20:00 | 10.74 | 10.73
2019-10-25 20:30 | 10.67 | 10.66
2019-10-25 21:00 | 9.91 | 9.9
2019-10-25 21:30 | 9.16 | 9.14
2019-10-25 22:00 | 8.61 | 8.58
2019-10-25 22:30 | 8.26 | 8.23
2019-10-25 23:00 | 7.95 | 7.91
2019-10-25 23:30 | 7.19 | 7.13
2019-10-26 | 6.44 | 6.37
2019-10-26 00:30 | 5.79 | 5.7
2019-10-26 01:00 | 5.38 | 5.27
2019-10-26 01:30 | 5.1 | 4.99
2019-10-26 02:00 | 4.74 | 4.62
2019-10-26 02:30 | 4.56 | 4.42
2019-10-26 03:00 | 4.51 | 4.37
2019-10-26 03:30 | 4.48 | 4.33
2019-10-26 04:00 | 4.5 | 4.35
2019-10-26 04:30 | 4.54 | 4.39
2019-10-26 05:00 | 4.5 | 4.32
2019-10-26 05:30 | 4.44 | 4.17
2019-10-26 06:00 | 4.34 | 4.05
2019-10-26 06:30 | 4.05 | 3.79
2019-10-26 07:00 | 3.63 | 3.38
2019-10-26 07:30 | 3.48 | 3.28
2019-10-26 08:00 | 3.13 | 2.96
2019-10-26 08:30 | 2.78 | 2.66
2019-10-26 09:00 | 2.56 | 2.48
2019-10-26 09:30 | 2.44 | 2.39
2019-10-26 10:00 | 2.39 | 2.32
2019-10-26 10:30 | 2.19 | 2.12
2019-10-26 11:00 | 2.24 | 2.17
2019-10-26 11:30 | 2.41 | 2.34
2019-10-26 12:00 | 2.64 | 2.57
2019-10-26 12:30 | 3.1 | 3.03
2019-10-26 13:00 | 3.74 | 3.68
2019-10-26 13:30 | 4.41 | 4.34
2019-10-26 14:00 | 4.94 | 4.88
2019-10-26 14:30 | 5.7 | 5.66
2019-10-26 15:00 | 6.59 | 6.55
2019-10-26 15:30 | 7.33 | 7.3
2019-10-26 16:00 | 8.27 | 8.25
2019-10-26 16:30 | 9.17 | 9.15
2019-10-26 17:00 | 9.93 | 9.91
2019-10-26 17:30 | 10.28 | 10.27
2019-10-26 18:00 | 10.45 | 10.44
2019-10-26 18:30 | 10.86 | 10.85
2019-10-26 19:00 | 11.41 | 11.4
2019-10-26 19:30 | 10.92 | 10.92
2019-10-26 20:00 | 10.7 | 10.7
2019-10-26 20:30 | 10.43 | 10.43
2019-10-26 21:00 | 9.81 | 9.8
2019-10-26 21:30 | 9.19 | 9.17
2019-10-26 22:00 | 8.67 | 8.64
2019-10-26 22:30 | 8.36 | 8.33
2019-10-26 23:00 | 8.18 | 8.14
2019-10-26 23:30 | 7.32 | 7.27
2019-10-27 | 6.47 | 6.41
2019-10-27 00:30 | 5.94 | 5.87
2019-10-27 01:00 | 5.59 | 5.51
2019-10-27 01:30 | 5.21 | 5.11
2019-10-27 02:00 | 4.98 | 4.86
2019-10-27 02:30 | 4.83 | 4.72
2019-10-27 03:00 | 4.66 | 4.54
2019-10-27 03:30 | 4.57 | 4.44
2019-10-27 04:00 | 4.6 | 4.45
2019-10-27 04:30 | 4.54 | 4.4
2019-10-27 05:00 | 4.55 | 4.37
2019-10-27 05:30 | 4.48 | 4.2
2019-10-27 06:00 | 4.25 | 3.96
2019-10-27 06:30 | 3.94 | 3.66
2019-10-27 07:00 | 3.54 | 3.25
2019-10-27 07:30 | 3.32 | 3.09
2019-10-27 08:00 | 3.21 | 3.03
2019-10-27 08:30 | 2.97 | 2.87
2019-10-27 09:00 | 2.94 | 2.88
2019-10-27 09:30 | 2.93 | 2.89
2019-10-27 10:00 | 2.92 | 2.88
2019-10-27 10:30 | 2.93 | 2.88
2019-10-27 11:00 | 3.06 | 3.01
2019-10-27 11:30 | 3.56 | 3.51
2019-10-27 12:00 | 4.46 | 4.41
2019-10-27 12:30 | 5.16 | 5.12
2019-10-27 13:00 | 6.26 | 6.22
2019-10-27 13:30 | 6.55 | 6.5
2019-10-27 14:00 | 7.11 | 7.07
2019-10-27 14:30 | 7.75 | 7.71
2019-10-27 15:00 | 8.33 | 8.31
2019-10-27 15:30 | 9.19 | 9.16
2019-10-27 16:00 | 9.91 | 9.89
2019-10-27 16:30 | 10.59 | 10.58
2019-10-27 17:00 | 11.3 | 11.29
2019-10-27 17:30 | 11.7 | 11.69
2019-10-27 18:00 | 11.96 | 11.95
2019-10-27 18:30 | 12.22 | 12.21
2019-10-27 19:00 | 12.55 | 12.54
2019-10-27 19:30 | 12.15 | 12.14
2019-10-27 20:00 | 11.77 | 11.76
2019-10-27 20:30 | 11.43 | 11.43
2019-10-27 21:00 | 10.62 | 10.61
2019-10-27 21:30 | 9.68 | 9.67
2019-10-27 22:00 | 9 | 8.98
2019-10-27 22:30 | 8.29 | 8.26
2019-10-27 23:00 | 8.04 | 8
2019-10-27 23:30 | 7.11 | 7.05
2019-10-28 | 6.28 | 6.22
2019-10-28 00:30 | 5.76 | 5.69
2019-10-28 01:00 | 5.59 | 5.51
2019-10-28 01:30 | 5.32 | 5.24
2019-10-28 02:00 | 5.02 | 4.92
2019-10-28 02:30 | 4.88 | 4.77
2019-10-28 03:00 | 4.86 | 4.75
2019-10-28 03:30 | 4.84 | 4.72
2019-10-28 04:00 | 4.87 | 4.76
2019-10-28 04:30 | 5.01 | 4.91
2019-10-28 05:00 | 5.26 | 5.16
2019-10-28 05:30 | 5.63 | 5.49
2019-10-28 06:00 | 5.94 | 5.82
2019-10-28 06:30 | 6.05 | 5.94
2019-10-28 07:00 | 6.28 | 6.21
2019-10-28 07:30 | 6 | 5.95
2019-10-28 08:00 | 5.95 | 5.91
2019-10-28 08:30 | 6.16 | 6.13
2019-10-28 09:00 | 4.67 | 4.65
2019-10-28 09:30 | 3.72 | 3.7
2019-10-28 10:00 | 3.55 | 3.54
2019-10-28 10:30 | 3.45 | 3.44
2019-10-28 11:00 | 3.89 | 3.88
2019-10-28 11:30 | 4.25 | 4.25
2019-10-28 12:00 | 4.07 | 4.06
2019-10-28 12:30 | 6.48 | 6.47
2019-10-28 13:00 | 5.65 | 5.65
2019-10-28 13:30 | 5.63 | 5.62
2019-10-28 14:00 | 5.36 | 5.35
2019-10-28 14:30 | 5.74 | 5.74
2019-10-28 15:00 | 5.34 | 5.34
2019-10-28 15:30 | 6.39 | 6.38
2019-10-28 16:00 | 7.29 | 7.28
2019-10-28 16:30 | 8.68 | 8.67
2019-10-28 17:00 | 10.07 | 10.06
2019-10-28 17:30 | 10.71 | 10.7
2019-10-28 18:00 | 11.29 | 11.28
2019-10-28 18:30 | 11.99 | 11.99
2019-10-28 19:00 | 12.5 | 12.5
2019-10-28 19:30 | 12.12 | 12.12
2019-10-28 20:00 | 11.95 | 11.94
2019-10-28 20:30 | 11.57 | 11.57
2019-10-28 21:00 | 10.76 | 10.76
2019-10-28 21:30 | 9.65 | 9.63
2019-10-28 22:00 | 8.82 | 8.8
2019-10-28 22:30 | 8.16 | 8.12
2019-10-28 23:00 | 7.95 | 7.92
2019-10-28 23:30 | 7.06 | 7.01
2019-10-29 | 6.27 | 6.21
2019-10-29 00:30 | 5.78 | 5.7
2019-10-29 01:00 | 5.54 | 5.46
2019-10-29 01:30 | 5.2 | 5.1
2019-10-29 02:00 | 4.81 | 4.69
2019-10-29 02:30 | 4.81 | 4.7
2019-10-29 03:00 | 4.86 | 4.74
2019-10-29 03:30 | 4.8 | 4.68
2019-10-29 04:00 | 4.89 | 4.77
2019-10-29 04:30 | 5.01 | 4.9
2019-10-29 05:00 | 5.28 | 5.16
2019-10-29 05:30 | 5.79 | 5.64
2019-10-29 06:00 | 5.81 | 5.67
2019-10-29 06:30 | 5.44 | 5.31
2019-10-29 07:00 | 5.26 | 5.16
2019-10-29 07:30 | 4.83 | 4.76
2019-10-29 08:00 | 4.26 | 4.21
2019-10-29 08:30 | 3.39 | 3.35
2019-10-29 09:00 | 2.47 | 2.42
2019-10-29 09:30 | 2.13 | 2.1
2019-10-29 10:00 | 2.17 | 2.15
2019-10-29 10:30 | 1.9 | 1.89
2019-10-29 11:00 | 2.1 | 2.09
2019-10-29 11:30 | 2.3 | 2.3
2019-10-29 12:00 | 2.49 | 2.48
2019-10-29 12:30 | 2.67 | 2.66
2019-10-29 13:00 | 3.14 | 3.13
2019-10-29 13:30 | 3.21 | 3.2
2019-10-29 14:00 | 3.54 | 3.53
2019-10-29 14:30 | 4.03 | 4.02
2019-10-29 15:00 | 4.66 | 4.65
2019-10-29 15:30 | 5.31 | 5.3
2019-10-29 16:00 | 6.5 | 6.49
2019-10-29 16:30 | 7.78 | 7.77
2019-10-29 17:00 | 9.1 | 9.09
2019-10-29 17:30 | 10.01 | 10
2019-10-29 18:00 | 10.72 | 10.71
2019-10-29 18:30 | 11.64 | 11.64
2019-10-29 19:00 | 12.33 | 12.33
2019-10-29 19:30 | 12.02 | 12.02
2019-10-29 20:00 | 11.71 | 11.7
2019-10-29 20:30 | 11.42 | 11.41
2019-10-29 21:00 | 10.46 | 10.45
2019-10-29 21:30 | 9.61 | 9.59
2019-10-29 22:00 | 8.63 | 8.6
2019-10-29 22:30 | 8.34 | 8.31
2019-10-29 23:00 | 7.87 | 7.83
2019-10-29 23:30 | 6.97 | 6.91
2019-10-30 | 6.13 | 6.05
2019-10-30 00:30 | 5.55 | 5.45
2019-10-30 01:00 | 5.25 | 5.15
2019-10-30 01:30 | 5.06 | 4.95
2019-10-30 02:00 | 4.77 | 4.65
2019-10-30 02:30 | 4.65 | 4.52
2019-10-30 03:00 | 4.67 | 4.54
2019-10-30 03:30 | 4.69 | 4.55
2019-10-30 04:00 | 4.69 | 4.56
2019-10-30 04:30 | 4.81 | 4.67
2019-10-30 05:00 | 5.06 | 4.9
2019-10-30 05:30 | 5.42 | 5.24
2019-10-30 06:00 | 5.68 | 5.53
2019-10-30 06:30 | 5.82 | 5.7
2019-10-30 07:00 | 6.45 | 6.36
2019-10-30 07:30 | 5.72 | 5.64
2019-10-30 08:00 | 4.23 | 4.15
2019-10-30 08:30 | 5.36 | 5.31
2019-10-30 09:00 | 5.55 | 5.51
2019-10-30 09:30 | 3.72 | 3.68
2019-10-30 10:00 | 4.68 | 4.65
2019-10-30 10:30 | 5.85 | 5.82
2019-10-30 11:00 | 4.78 | 4.76
2019-10-30 11:30 | 3.78 | 3.76
2019-10-30 12:00 | 3.98 | 3.95
2019-10-30 12:30 | 4.04 | 4.02
2019-10-30 13:00 | 5.18 | 5.16
2019-10-30 13:30 | 4.08 | 4.06
2019-10-30 14:00 | 5.01 | 4.99
2019-10-30 14:30 | 6.06 | 6.03
2019-10-30 15:00 | 6.22 | 6.18
2019-10-30 15:30 | 5.85 | 5.81
2019-10-30 16:00 | 6.34 | 6.3
2019-10-30 16:30 | 7.34 | 7.32
2019-10-30 17:00 | 8.1 | 8.08
2019-10-30 17:30 | 9.1 | 9.08
2019-10-30 18:00 | 9.82 | 9.81
2019-10-30 18:30 | 10.83 | 10.82
2019-10-30 19:00 | 11.67 | 11.66
2019-10-30 19:30 | 11.32 | 11.32
2019-10-30 20:00 | 11.31 | 11.3
2019-10-30 20:30 | 10.96 | 10.95
2019-10-30 21:00 | 10.47 | 10.46
2019-10-30 21:30 | 9.49 | 9.47
2019-10-30 22:00 | 8.74 | 8.71
2019-10-30 22:30 | 8.26 | 8.22
2019-10-30 23:00 | 7.87 | 7.83
2019-10-30 23:30 | 6.98 | 6.91
2019-10-31 | 6.09 | 6.01
2019-10-31 00:30 | 5.54 | 5.44
2019-10-31 01:00 | 5.21 | 5.11
2019-10-31 01:30 | 4.98 | 4.86
2019-10-31 02:00 | 4.82 | 4.69
2019-10-31 02:30 | 4.68 | 4.56
2019-10-31 03:00 | 4.55 | 4.42
2019-10-31 03:30 | 4.63 | 4.5
2019-10-31 04:00 | 4.68 | 4.55
2019-10-31 04:30 | 4.79 | 4.65
2019-10-31 05:00 | 4.84 | 4.67
2019-10-31 05:30 | 4.99 | 4.78
2019-10-31 06:00 | 5.15 | 4.95
2019-10-31 06:30 | 5.18 | 5.01
2019-10-31 07:00 | 4.52 | 4.35
2019-10-31 07:30 | 4.27 | 4.15
2019-10-31 08:00 | 3.22 | 3.11
2019-10-31 08:30 | 2.99 | 2.89
2019-10-31 09:00 | 2.39 | 2.3
2019-10-31 09:30 | 2.01 | 1.92
2019-10-31 10:00 | 1.26 | 1.19
2019-10-31 10:30 | 1.48 | 1.41
2019-10-31 11:00 | 2.09 | 2.04
2019-10-31 11:30 | 2.77 | 2.74
2019-10-31 12:00 | 3.06 | 3.03
2019-10-31 12:30 | 2.62 | 2.59
2019-10-31 13:00 | 1.8 | 1.76
2019-10-31 13:30 | 2.2 | 2.16
2019-10-31 14:00 | 2.96 | 2.94
2019-10-31 14:30 | 3.22 | 3.2
2019-10-31 15:00 | 3.83 | 3.82
2019-10-31 15:30 | 3.96 | 3.95
2019-10-31 16:00 | 5.55 | 5.54
2019-10-31 16:30 | 6.92 | 6.91
2019-10-31 17:00 | 8.39 | 8.38
2019-10-31 17:30 | 9.33 | 9.32
2019-10-31 18:00 | 9.72 | 9.71
2019-10-31 18:30 | 9.96 | 9.96
2019-10-31 19:00 | 10.68 | 10.68
2019-10-31 19:30 | 10.71 | 10.71
2019-10-31 20:00 | 10.87 | 10.86
2019-10-31 20:30 | 10.69 | 10.68
2019-10-31 21:00 | 10.09 | 10.07
2019-10-31 21:30 | 9.45 | 9.43
2019-10-31 22:00 | 8.63 | 8.6
2019-10-31 22:30 | 8.15 | 8.12
2019-10-31 23:00 | 7.84 | 7.8
2019-10-31 23:30 | 6.98 | 6.92
2019-11-01 | 6.02 | 5.94
2019-11-01 00:30 | 5.38 | 5.28
2019-11-01 01:00 | 5.13 | 5.03
2019-11-01 01:30 | 4.82 | 4.71
2019-11-01 02:00 | 4.64 | 4.52
2019-11-01 02:30 | 4.58 | 4.46
2019-11-01 03:00 | 4.53 | 4.4
2019-11-01 03:30 | 4.6 | 4.48
2019-11-01 04:00 | 4.5 | 4.36
2019-11-01 04:30 | 4.57 | 4.43
2019-11-01 05:00 | 4.88 | 4.73
2019-11-01 05:30 | 5.04 | 4.85
2019-11-01 06:00 | 5.65 | 5.5
2019-11-01 06:30 | 5.49 | 5.36
2019-11-01 07:00 | 5.51 | 5.41
2019-11-01 07:30 | 6.05 | 5.98
2019-11-01 08:00 | 5.49 | 5.43
2019-11-01 08:30 | 4.81 | 4.75
2019-11-01 09:00 | 4.11 | 4.07
2019-11-01 09:30 | 4.48 | 4.45
2019-11-01 10:00 | 4.74 | 4.72
2019-11-01 10:30 | 4.68 | 4.66
2019-11-01 11:00 | 2.52 | 2.5
2019-11-01 11:30 | 5.29 | 5.27
2019-11-01 12:00 | 5.36 | 5.34
2019-11-01 12:30 | 5.98 | 5.95
2019-11-01 13:00 | 5.42 | 5.39
2019-11-01 13:30 | 6.01 | 5.97
2019-11-01 14:00 | 6.03 | 5.99
2019-11-01 14:30 | 5.92 | 5.87
2019-11-01 15:00 | 5.56 | 5.51
2019-11-01 15:30 | 6.71 | 6.66
2019-11-01 16:00 | 7.35 | 7.3
2019-11-01 16:30 | 8.07 | 8.03
2019-11-01 17:00 | 8.43 | 8.4
2019-11-01 17:30 | 8.99 | 8.96
2019-11-01 18:00 | 9.29 | 9.26
2019-11-01 18:30 | 9.92 | 9.9
2019-11-01 19:00 | 10.55 | 10.54
2019-11-01 19:30 | 10.32 | 10.31
2019-11-01 20:00 | 10.32 | 10.31
2019-11-01 20:30 | 10.17 | 10.16
2019-11-01 21:00 | 9.61 | 9.59
2019-11-01 21:30 | 8.9 | 8.87
2019-11-01 22:00 | 8.39 | 8.35
2019-11-01 22:30 | 8.08 | 8.04
2019-11-01 23:00 | 8 | 7.95
2019-11-01 23:30 | 7.1 | 7.04
2019-11-02 | 6.34 | 6.27
2019-11-02 00:30 | 5.62 | 5.53
2019-11-02 01:00 | 5.32 | 5.23
2019-11-02 01:30 | 4.99 | 4.88
2019-11-02 02:00 | 4.73 | 4.61
2019-11-02 02:30 | 4.56 | 4.42
2019-11-02 03:00 | 4.49 | 4.35
2019-11-02 03:30 | 4.42 | 4.28
2019-11-02 04:00 | 4.39 | 4.25
2019-11-02 04:30 | 4.4 | 4.26
2019-11-02 05:00 | 4.53 | 4.38
2019-11-02 05:30 | 4.46 | 4.21
2019-11-02 06:00 | 4.43 | 4.18
2019-11-02 06:30 | 3.66 | 3.38
2019-11-02 07:00 | 3.53 | 3.29
2019-11-02 07:30 | 3.4 | 3.23
2019-11-02 08:00 | 3.63 | 3.5
2019-11-02 08:30 | 3.5 | 3.4
2019-11-02 09:00 | 4.13 | 4.08
2019-11-02 09:30 | 4.71 | 4.67
2019-11-02 10:00 | 5.13 | 5.09
2019-11-02 10:30 | 3.94 | 3.91
2019-11-02 11:00 | 5.04 | 5.01
2019-11-02 11:30 | 2.43 | 2.38
2019-11-02 12:00 | 5.49 | 5.47
2019-11-02 12:30 | 3.88 | 3.84
2019-11-02 13:00 | 4.46 | 4.43
2019-11-02 13:30 | 7.04 | 7.02
2019-11-02 14:00 | 6.78 | 6.76
2019-11-02 14:30 | 4.79 | 4.77
2019-11-02 15:00 | 4.96 | 4.94
2019-11-02 15:30 | 5.26 | 5.23
2019-11-02 16:00 | 6.07 | 6.05
2019-11-02 16:30 | 6.79 | 6.76
2019-11-02 17:00 | 8.01 | 7.99
2019-11-02 17:30 | 8.88 | 8.86
2019-11-02 18:00 | 9.39 | 9.37
2019-11-02 18:30 | 9.94 | 9.93
2019-11-02 19:00 | 10.82 | 10.81
2019-11-02 19:30 | 10.56 | 10.55
2019-11-02 20:00 | 10.34 | 10.33
2019-11-02 20:30 | 10.01 | 10
2019-11-02 21:00 | 9.47 | 9.46
2019-11-02 21:30 | 8.96 | 8.93
2019-11-02 22:00 | 8.39 | 8.36
2019-11-02 22:30 | 8.11 | 8.06
2019-11-02 23:00 | 7.94 | 7.9
2019-11-02 23:30 | 7.18 | 7.12
2019-11-03 | 6.33 | 6.25
2019-11-03 00:30 | 5.76 | 5.67
2019-11-03 01:00 | 5.53 | 5.43
2019-11-03 01:30 | 5.12 | 5.01
2019-11-03 02:00 | 4.88 | 4.76
2019-11-03 02:30 | 4.76 | 4.63
2019-11-03 03:00 | 4.62 | 4.49
2019-11-03 03:30 | 4.57 | 4.44
2019-11-03 04:00 | 4.57 | 4.44
2019-11-03 04:30 | 4.57 | 4.44
2019-11-03 05:00 | 4.51 | 4.35
2019-11-03 05:30 | 4.49 | 4.25
2019-11-03 06:00 | 4.61 | 4.37
2019-11-03 06:30 | 4.82 | 4.6
2019-11-03 07:00 | 3.97 | 3.73
2019-11-03 07:30 | 3.35 | 3.12
2019-11-03 08:00 | 3.93 | 3.79
2019-11-03 08:30 | 3.72 | 3.61
2019-11-03 09:00 | 4.03 | 3.95
2019-11-03 09:30 | 4.87 | 4.83
2019-11-03 10:00 | 5.16 | 5.13
2019-11-03 10:30 | 4.56 | 4.54
2019-11-03 11:00 | 4.29 | 4.26
2019-11-03 11:30 | 4.19 | 4.17
2019-11-03 12:00 | 3.6 | 3.58
2019-11-03 12:30 | 3.65 | 3.62
2019-11-03 13:00 | 5.44 | 5.42
2019-11-03 13:30 | 4.19 | 4.16
2019-11-03 14:00 | 5.38 | 5.35
2019-11-03 14:30 | 5.42 | 5.39
2019-11-03 15:00 | 6.5 | 6.48
2019-11-03 15:30 | 6.77 | 6.75
2019-11-03 16:00 | 7.93 | 7.92
2019-11-03 16:30 | 9.1 | 9.09
2019-11-03 17:00 | 10.23 | 10.22
2019-11-03 17:30 | 11.11 | 11.1
2019-11-03 18:00 | 11.58 | 11.58
2019-11-03 18:30 | 12.13 | 12.13
2019-11-03 19:00 | 12.73 | 12.72
2019-11-03 19:30 | 12.25 | 12.25
2019-11-03 20:00 | 11.74 | 11.73
2019-11-03 20:30 | 11.4 | 11.39
2019-11-03 21:00 | 10.7 | 10.69
2019-11-03 21:30 | 9.84 | 9.82
2019-11-03 22:00 | 9.06 | 9.04
2019-11-03 22:30 | 8.45 | 8.42
2019-11-03 23:00 | 8.09 | 8.04
2019-11-03 23:30 | 7.3 | 7.25
2019-11-04 | 6.43 | 6.37
2019-11-04 00:30 | 5.74 | 5.67
2019-11-04 01:00 | 5.4 | 5.31
2019-11-04 01:30 | 5.12 | 5.03
2019-11-04 02:00 | 4.93 | 4.83
2019-11-04 02:30 | 4.82 | 4.71
2019-11-04 03:00 | 4.78 | 4.68
2019-11-04 03:30 | 4.9 | 4.81
2019-11-04 04:00 | 4.85 | 4.75
2019-11-04 04:30 | 4.92 | 4.82
2019-11-04 05:00 | 5.05 | 4.92
2019-11-04 05:30 | 5.23 | 5.06
2019-11-04 06:00 | 5.75 | 5.63
2019-11-04 06:30 | 5.88 | 5.8
2019-11-04 07:00 | 6.37 | 6.31
2019-11-04 07:30 | 6.92 | 6.88
2019-11-04 08:00 | 7.07 | 7.04
2019-11-04 08:30 | 6.25 | 6.23
2019-11-04 09:00 | 4.01 | 3.99
2019-11-04 09:30 | 2.43 | 2.42
2019-11-04 10:00 | 2.58 | 2.57
2019-11-04 10:30 | 2.95 | 2.94
2019-11-04 11:00 | 3.4 | 3.39
2019-11-04 11:30 | 4.7 | 4.69
2019-11-04 12:00 | 7.22 | 7.21
2019-11-04 12:30 | 7.57 | 7.57
2019-11-04 13:00 | 7.59 | 7.58
2019-11-04 13:30 | 8.35 | 8.34
2019-11-04 14:00 | 7.15 | 7.13
2019-11-04 14:30 | 9.1 | 9.08
2019-11-04 15:00 | 8.99 | 8.97
2019-11-04 15:30 | 10.77 | 10.75
2019-11-04 16:00 | 12.84 | 12.83
2019-11-04 16:30 | 12.13 | 12.12
2019-11-04 17:00 | 12.85 | 12.84
2019-11-04 17:30 | 14.03 | 14.02
2019-11-04 18:00 | 14.64 | 14.64
2019-11-04 18:30 | 14.99 | 14.99
2019-11-04 19:00 | 15.54 | 15.52
2019-11-04 19:30 | 15.26 | 15.25
2019-11-04 20:00 | 14.61 | 14.61
2019-11-04 20:30 | 14.07 | 14.06
2019-11-04 21:00 | 12.9 | 12.89
2019-11-04 21:30 | 11.75 | 11.74
2019-11-04 22:00 | 10.71 | 10.7
2019-11-04 22:30 | 9.61 | 9.6
2019-11-04 23:00 | 8.89 | 8.87
2019-11-04 23:30 | 7.83 | 7.8
2019-11-05 | 6.89 | 6.85
2019-11-05 00:30 | 6.14 | 6.08
2019-11-05 01:00 | 5.84 | 5.77
2019-11-05 01:30 | 5.55 | 5.47
2019-11-05 02:00 | 5.34 | 5.25
2019-11-05 02:30 | 5.12 | 5.03
2019-11-05 03:00 | 5.11 | 5.02
2019-11-05 03:30 | 5.14 | 5.05
2019-11-05 04:00 | 5.1 | 5
2019-11-05 04:30 | 5.18 | 5.09
2019-11-05 05:00 | 5.3 | 5.17
2019-11-05 05:30 | 5.41 | 5.26
2019-11-05 06:00 | 5.34 | 5.19
2019-11-05 06:30 | 5.22 | 5.09
2019-11-05 07:00 | 5.1 | 5.01
2019-11-05 07:30 | 4.93 | 4.87
2019-11-05 08:00 | 4.26 | 4.22
2019-11-05 08:30 | 3.26 | 3.23
2019-11-05 09:00 | 2.48 | 2.46
2019-11-05 09:30 | 2.25 | 2.23
2019-11-05 10:00 | 2.84 | 2.83
2019-11-05 10:30 | 3.7 | 3.69
2019-11-05 11:00 | 5.23 | 5.23
2019-11-05 11:30 | 2.72 | 2.71
2019-11-05 12:00 | 3.44 | 3.43
2019-11-05 12:30 | 3.59 | 3.58
2019-11-05 13:00 | 2.79 | 2.78
2019-11-05 13:30 | 2.22 | 2.21
2019-11-05 14:00 | 2.86 | 2.86
2019-11-05 14:30 | 3.54 | 3.53
2019-11-05 15:00 | 4.14 | 4.14
2019-11-05 15:30 | 5.12 | 5.12
2019-11-05 16:00 | 6.51 | 6.51
2019-11-05 16:30 | 7.88 | 7.88
2019-11-05 17:00 | 9.24 | 9.24
2019-11-05 17:30 | 10.24 | 10.23
2019-11-05 18:00 | 11.15 | 11.14
2019-11-05 18:30 | 11.88 | 11.88
2019-11-05 19:00 | 12.88 | 12.88
2019-11-05 19:30 | 12.7 | 12.7
2019-11-05 20:00 | 12.43 | 12.43
2019-11-05 20:30 | 12.04 | 12.03
2019-11-05 21:00 | 11.04 | 11.04
2019-11-05 21:30 | 10.19 | 10.17
2019-11-05 22:00 | 9.2 | 9.18
2019-11-05 22:30 | 8.57 | 8.54
2019-11-05 23:00 | 7.88 | 7.82
2019-11-05 23:30 | 6.86 | 6.8
2019-11-06 | 6 | 5.92
2019-11-06 00:30 | 5.42 | 5.32
2019-11-06 01:00 | 5.15 | 5.04
2019-11-06 01:30 | 4.87 | 4.74
2019-11-06 02:00 | 4.67 | 4.54
2019-11-06 02:30 | 4.57 | 4.42
2019-11-06 03:00 | 4.54 | 4.39
2019-11-06 03:30 | 4.55 | 4.4
2019-11-06 04:00 | 4.54 | 4.38
2019-11-06 04:30 | 4.7 | 4.55
2019-11-06 05:00 | 4.83 | 4.63
2019-11-06 05:30 | 5.17 | 4.96
2019-11-06 06:00 | 5.42 | 5.24
2019-11-06 06:30 | 5.24 | 5.08
2019-11-06 07:00 | 5.01 | 4.89
2019-11-06 07:30 | 4.56 | 4.46
2019-11-06 08:00 | 3.72 | 3.63
2019-11-06 08:30 | 2.61 | 2.5
2019-11-06 09:00 | 1.83 | 1.73
2019-11-06 09:30 | 1.49 | 1.41
2019-11-06 10:00 | 1.48 | 1.42
2019-11-06 10:30 | 1.55 | 1.52
2019-11-06 11:00 | 1.47 | 1.45
2019-11-06 11:30 | 1.4 | 1.38
2019-11-06 12:00 | 1.48 | 1.47
2019-11-06 12:30 | 1.73 | 1.72
2019-11-06 13:00 | 2.12 | 2.11
2019-11-06 13:30 | 2.65 | 2.64
2019-11-06 14:00 | 3.43 | 3.42
2019-11-06 14:30 | 4.29 | 4.29
2019-11-06 15:00 | 5.22 | 5.21
2019-11-06 15:30 | 6.38 | 6.38
2019-11-06 16:00 | 7.67 | 7.66
2019-11-06 16:30 | 8.72 | 8.72
2019-11-06 17:00 | 9.92 | 9.92
2019-11-06 17:30 | 10.83 | 10.83
2019-11-06 18:00 | 11.32 | 11.32
2019-11-06 18:30 | 11.8 | 11.79
2019-11-06 19:00 | 12.95 | 12.95
2019-11-06 19:30 | 12.75 | 12.75
2019-11-06 20:00 | 12.41 | 12.41
2019-11-06 20:30 | 12.01 | 12.01
2019-11-06 21:00 | 11.16 | 11.15
2019-11-06 21:30 | 10.07 | 10.05
2019-11-06 22:00 | 9.21 | 9.19
2019-11-06 22:30 | 8.36 | 8.33
2019-11-06 23:00 | 7.84 | 7.79
2019-11-06 23:30 | 7.06 | 7
2019-11-07 | 6.17 | 6.09
2019-11-07 00:30 | 5.51 | 5.41
2019-11-07 01:00 | 5.22 | 5.12
2019-11-07 01:30 | 4.87 | 4.74
2019-11-07 02:00 | 4.59 | 4.45
2019-11-07 02:30 | 4.53 | 4.38
2019-11-07 03:00 | 4.51 | 4.35
2019-11-07 03:30 | 4.48 | 4.32
2019-11-07 04:00 | 4.61 | 4.46
2019-11-07 04:30 | 4.68 | 4.52
2019-11-07 05:00 | 4.75 | 4.53
2019-11-07 05:30 | 5.05 | 4.81
2019-11-07 06:00 | 5.17 | 4.98
2019-11-07 06:30 | 5.24 | 5.09
2019-11-07 07:00 | 4.9 | 4.77
2019-11-07 07:30 | 4.51 | 4.41
2019-11-07 08:00 | 3.56 | 3.46
2019-11-07 08:30 | 2.46 | 2.36
2019-11-07 09:00 | 1.72 | 1.63
2019-11-07 09:30 | 1.68 | 1.64
2019-11-07 10:00 | 1.62 | 1.6
2019-11-07 10:30 | 1.62 | 1.61
2019-11-07 11:00 | 1.95 | 1.94
2019-11-07 11:30 | 2.24 | 2.22
2019-11-07 12:00 | 2.7 | 2.69
2019-11-07 12:30 | 3.55 | 3.53
2019-11-07 13:00 | 4.24 | 4.22
2019-11-07 13:30 | 5.03 | 5
2019-11-07 14:00 | 6.2 | 6.17
2019-11-07 14:30 | 7.43 | 7.4
2019-11-07 15:00 | 8.66 | 8.63
2019-11-07 15:30 | 10.32 | 10.29
2019-11-07 16:00 | 12.16 | 12.13
2019-11-07 16:30 | 13.32 | 13.29
2019-11-07 17:00 | 14.13 | 14.1
2019-11-07 17:30 | 14.29 | 14.27
2019-11-07 18:00 | 14.25 | 14.24
2019-11-07 18:30 | 14.3 | 14.29
2019-11-07 19:00 | 14.67 | 14.65
2019-11-07 19:30 | 14.27 | 14.26
2019-11-07 20:00 | 13.64 | 13.63
2019-11-07 20:30 | 13.01 | 13
2019-11-07 21:00 | 11.97 | 11.96
2019-11-07 21:30 | 10.74 | 10.74
2019-11-07 22:00 | 9.8 | 9.78
2019-11-07 22:30 | 9.11 | 9.09
2019-11-07 23:00 | 8.56 | 8.53
2019-11-07 23:30 | 7.53 | 7.49
2019-11-08 | 6.64 | 6.57
2019-11-08 00:30 | 5.93 | 5.85
2019-11-08 01:00 | 5.63 | 5.54
2019-11-08 01:30 | 5.26 | 5.16
2019-11-08 02:00 | 4.9 | 4.78
2019-11-08 02:30 | 4.79 | 4.67
2019-11-08 03:00 | 4.7 | 4.57
2019-11-08 03:30 | 4.73 | 4.59
2019-11-08 04:00 | 4.75 | 4.6
2019-11-08 04:30 | 4.85 | 4.71
2019-11-08 05:00 | 4.87 | 4.67
2019-11-08 05:30 | 5.11 | 4.9
2019-11-08 06:00 | 4.89 | 4.67
2019-11-08 06:30 | 4.83 | 4.64
2019-11-08 07:00 | 4.38 | 4.22
2019-11-08 07:30 | 3.97 | 3.83
2019-11-08 08:00 | 3.35 | 3.25
2019-11-08 08:30 | 2.67 | 2.59
2019-11-08 09:00 | 2.3 | 2.26
2019-11-08 09:30 | 2.63 | 2.6
2019-11-08 10:00 | 3.05 | 3.02
2019-11-08 10:30 | 3.62 | 3.59
2019-11-08 11:00 | 4.53 | 4.5
2019-11-08 11:30 | 5.43 | 5.4
2019-11-08 12:00 | 6.44 | 6.39
2019-11-08 12:30 | 7.59 | 7.54
2019-11-08 13:00 | 8.78 | 8.71
2019-11-08 13:30 | 9.87 | 9.8
2019-11-08 14:00 | 11.16 | 11.07
2019-11-08 14:30 | 12.15 | 12.06
2019-11-08 15:00 | 13.31 | 13.22
2019-11-08 15:30 | 14.88 | 14.79
2019-11-08 16:00 | 16.77 | 16.68
2019-11-08 16:30 | 18.21 | 18.11
2019-11-08 17:00 | 19.35 | 19.25
2019-11-08 17:30 | 19.8 | 19.71
2019-11-08 18:00 | 19.46 | 19.38
2019-11-08 18:30 | 19.08 | 19.01
2019-11-08 19:00 | 19.55 | 19.46
2019-11-08 19:30 | 18.88 | 18.8
2019-11-08 20:00 | 17.8 | 17.75
2019-11-08 20:30 | 16.52 | 16.48
2019-11-08 21:00 | 14.87 | 14.85
2019-11-08 21:30 | 13.31 | 13.3
2019-11-08 22:00 | 11.89 | 11.88
2019-11-08 22:30 | 10.99 | 10.99
2019-11-08 23:00 | 10.3 | 10.3
2019-11-08 23:30 | 9.03 | 9.02
2019-11-09 | 7.94 | 7.93
2019-11-09 00:30 | 7.18 | 7.16
2019-11-09 01:00 | 6.68 | 6.65
2019-11-09 01:30 | 6.22 | 6.17
2019-11-09 02:00 | 5.87 | 5.82
2019-11-09 02:30 | 5.65 | 5.59
2019-11-09 03:00 | 5.46 | 5.4
2019-11-09 03:30 | 5.37 | 5.3
2019-11-09 04:00 | 5.28 | 5.2
2019-11-09 04:30 | 5.24 | 5.16
2019-11-09 05:00 | 5 | 4.86
2019-11-09 05:30 | 5 | 4.81
2019-11-09 06:00 | 4.72 | 4.53
2019-11-09 06:30 | 4.52 | 4.36
2019-11-09 07:00 | 4.29 | 4.15
2019-11-09 07:30 | 4.19 | 4.09
2019-11-09 08:00 | 4.04 | 3.96
2019-11-09 08:30 | 3.89 | 3.85
2019-11-09 09:00 | 4.04 | 4.01
2019-11-09 09:30 | 4.18 | 4.15
2019-11-09 10:00 | 3.85 | 3.82
2019-11-09 10:30 | 3.67 | 3.63
2019-11-09 11:00 | 3.74 | 3.69
2019-11-09 11:30 | 3.86 | 3.81
2019-11-09 12:00 | 4.34 | 4.3
2019-11-09 12:30 | 4.98 | 4.94
2019-11-09 13:00 | 5.55 | 5.51
2019-11-09 13:30 | 6.09 | 6.06
2019-11-09 14:00 | 7.04 | 7.01
2019-11-09 14:30 | 8.05 | 8.02
2019-11-09 15:00 | 8.94 | 8.91
2019-11-09 15:30 | 9.72 | 9.7
2019-11-09 16:00 | 10.15 | 10.14
2019-11-09 16:30 | 11.19 | 11.18
2019-11-09 17:00 | 11.74 | 11.73
2019-11-09 17:30 | 11.89 | 11.88
2019-11-09 18:00 | 11.79 | 11.78
2019-11-09 18:30 | 11.73 | 11.72
2019-11-09 19:00 | 12.31 | 12.31
2019-11-09 19:30 | 12 | 11.99
2019-11-09 20:00 | 11.5 | 11.5
2019-11-09 20:30 | 11.12 | 11.12
2019-11-09 21:00 | 10.41 | 10.4
2019-11-09 21:30 | 9.64 | 9.63
2019-11-09 22:00 | 9.17 | 9.15
2019-11-09 22:30 | 8.72 | 8.7
2019-11-09 23:00 | 8.42 | 8.39
2019-11-09 23:30 | 7.61 | 7.57
2019-11-10 | 6.78 | 6.72
2019-11-10 00:30 | 6.12 | 6.04
2019-11-10 01:00 | 5.74 | 5.65
2019-11-10 01:30 | 5.39 | 5.29
2019-11-10 02:00 | 5.12 | 5
2019-11-10 02:30 | 4.96 | 4.84
2019-11-10 03:00 | 4.82 | 4.69
2019-11-10 03:30 | 4.73 | 4.59
2019-11-10 04:00 | 4.66 | 4.51
2019-11-10 04:30 | 4.63 | 4.47
2019-11-10 05:00 | 4.55 | 4.31
2019-11-10 05:30 | 4.44 | 4.12
2019-11-10 06:00 | 4.06 | 3.71
2019-11-10 06:30 | 3.62 | 3.27
2019-11-10 07:00 | 3.3 | 2.94
2019-11-10 07:30 | 3.02 | 2.7
2019-11-10 08:00 | 2.81 | 2.55
2019-11-10 08:30 | 2.45 | 2.22
2019-11-10 09:00 | 2.37 | 2.22
2019-11-10 09:30 | 2.26 | 2.14
2019-11-10 10:00 | 1.96 | 1.86
2019-11-10 10:30 | 1.82 | 1.74
2019-11-10 11:00 | 1.93 | 1.88
2019-11-10 11:30 | 2.33 | 2.3
2019-11-10 12:00 | 2.86 | 2.82
2019-11-10 12:30 | 3.56 | 3.53
2019-11-10 13:00 | 4.31 | 4.27
2019-11-10 13:30 | 5.21 | 5.18
2019-11-10 14:00 | 6.39 | 6.36
2019-11-10 14:30 | 7.44 | 7.42
2019-11-10 15:00 | 8.71 | 8.69
2019-11-10 15:30 | 10.04 | 10.02
2019-11-10 16:00 | 11.42 | 11.41
2019-11-10 16:30 | 12.79 | 12.78
2019-11-10 17:00 | 13.96 | 13.95
2019-11-10 17:30 | 14.58 | 14.56
2019-11-10 18:00 | 14.59 | 14.58
2019-11-10 18:30 | 14.25 | 14.24
2019-11-10 19:00 | 14.36 | 14.36
2019-11-10 19:30 | 13.71 | 13.7
2019-11-10 20:00 | 13.06 | 13.06
2019-11-10 20:30 | 12.24 | 12.24
2019-11-10 21:00 | 11.39 | 11.39
2019-11-10 21:30 | 10.41 | 10.4
2019-11-10 22:00 | 9.39 | 9.37
2019-11-10 22:30 | 8.8 | 8.78
2019-11-10 23:00 | 8.39 | 8.36
2019-11-10 23:30 | 7.41 | 7.37
2019-11-11 | 6.58 | 6.51
2019-11-11 00:30 | 5.95 | 5.88
2019-11-11 01:00 | 5.55 | 5.45
2019-11-11 01:30 | 5.23 | 5.13
2019-11-11 02:00 | 4.93 | 4.82
2019-11-11 02:30 | 4.76 | 4.64
2019-11-11 03:00 | 4.8 | 4.68
2019-11-11 03:30 | 4.78 | 4.65
2019-11-11 04:00 | 4.81 | 4.68
2019-11-11 04:30 | 4.93 | 4.8
2019-11-11 05:00 | 4.98 | 4.81
2019-11-11 05:30 | 5.13 | 4.93
2019-11-11 06:00 | 5.57 | 5.42
2019-11-11 06:30 | 5.63 | 5.51
2019-11-11 07:00 | 5.55 | 5.46
2019-11-11 07:30 | 5.4 | 5.33
2019-11-11 08:00 | 4.68 | 4.61
2019-11-11 08:30 | 4.21 | 4.14
2019-11-11 09:00 | 3.93 | 3.89
2019-11-11 09:30 | 4.75 | 4.71
2019-11-11 10:00 | 4.22 | 4.2
2019-11-11 10:30 | 2.87 | 2.86
2019-11-11 11:00 | 2.93 | 2.93
2019-11-11 11:30 | 3.14 | 3.13
2019-11-11 12:00 | 3.16 | 3.15
2019-11-11 12:30 | 3.85 | 3.84
2019-11-11 13:00 | 4.28 | 4.27
2019-11-11 13:30 | 5.11 | 5.1
2019-11-11 14:00 | 6.3 | 6.3
2019-11-11 14:30 | 6.68 | 6.67
2019-11-11 15:00 | 7.22 | 7.21
2019-11-11 15:30 | 8.35 | 8.34
2019-11-11 16:00 | 9.57 | 9.57
2019-11-11 16:30 | 10.62 | 10.62
2019-11-11 17:00 | 11.63 | 11.63
2019-11-11 17:30 | 12.33 | 12.32
2019-11-11 18:00 | 12.71 | 12.7
2019-11-11 18:30 | 12.96 | 12.96
2019-11-11 19:00 | 13.72 | 13.72
2019-11-11 19:30 | 13.34 | 13.34
2019-11-11 20:00 | 12.89 | 12.89
2019-11-11 20:30 | 12.68 | 12.68
2019-11-11 21:00 | 11.84 | 11.84
2019-11-11 21:30 | 10.66 | 10.65
2019-11-11 22:00 | 9.65 | 9.64
2019-11-11 22:30 | 8.66 | 8.63
2019-11-11 23:00 | 8.2 | 8.16
2019-11-11 23:30 | 7.23 | 7.18
2019-11-12 | 6.37 | 6.3
2019-11-12 00:30 | 5.92 | 5.85
2019-11-12 01:00 | 5.58 | 5.51
2019-11-12 01:30 | 5.32 | 5.23
2019-11-12 02:00 | 5.06 | 4.95
2019-11-12 02:30 | 4.81 | 4.7
2019-11-12 03:00 | 4.87 | 4.77
2019-11-12 03:30 | 4.87 | 4.75
2019-11-12 04:00 | 4.86 | 4.74
2019-11-12 04:30 | 4.94 | 4.82
2019-11-12 05:00 | 5.04 | 4.87
2019-11-12 05:30 | 5.34 | 5.16
2019-11-12 06:00 | 5.51 | 5.36
2019-11-12 06:30 | 5.4 | 5.28
2019-11-12 07:00 | 5.09 | 4.99
2019-11-12 07:30 | 4.85 | 4.78
2019-11-12 08:00 | 4.32 | 4.27
2019-11-12 08:30 | 3.35 | 3.32
2019-11-12 09:00 | 2.7 | 2.68
2019-11-12 09:30 | 2.83 | 2.81
2019-11-12 10:00 | 2.98 | 2.96
2019-11-12 10:30 | 3.01 | 3
2019-11-12 11:00 | 3.42 | 3.4
2019-11-12 11:30 | 4.13 | 4.11
2019-11-12 12:00 | 4.84 | 4.82
2019-11-12 12:30 | 6.01 | 5.98
2019-11-12 13:00 | 7 | 6.95
2019-11-12 13:30 | 8.04 | 7.99
2019-11-12 14:00 | 9.05 | 8.99
2019-11-12 14:30 | 10.18 | 10.12
2019-11-12 15:00 | 11.03 | 10.98
2019-11-12 15:30 | 12.36 | 12.31
2019-11-12 16:00 | 14.15 | 14.09
2019-11-12 16:30 | 15.64 | 15.58
2019-11-12 17:00 | 16.59 | 16.54
2019-11-12 17:30 | 17.36 | 17.31
2019-11-12 18:00 | 17.46 | 17.42
2019-11-12 18:30 | 17.18 | 17.15
2019-11-12 19:00 | 17.45 | 17.4
2019-11-12 19:30 | 16.62 | 16.58
2019-11-12 20:00 | 16.33 | 16.3
2019-11-12 20:30 | 15.53 | 15.51
2019-11-12 21:00 | 14.32 | 14.31
2019-11-12 21:30 | 12.72 | 12.71
2019-11-12 22:00 | 11.49 | 11.48
2019-11-12 22:30 | 10.26 | 10.25
2019-11-12 23:00 | 9.56 | 9.55
2019-11-12 23:30 | 8.38 | 8.36
2019-11-13 | 7.35 | 7.32
2019-11-13 00:30 | 6.63 | 6.59
2019-11-13 01:00 | 6.32 | 6.27
2019-11-13 01:30 | 5.94 | 5.88
2019-11-13 02:00 | 5.63 | 5.57
2019-11-13 02:30 | 5.6 | 5.54
2019-11-13 03:00 | 5.46 | 5.39
2019-11-13 03:30 | 5.47 | 5.4
2019-11-13 04:00 | 5.53 | 5.46
2019-11-13 04:30 | 5.56 | 5.49
2019-11-13 05:00 | 5.55 | 5.43
2019-11-13 05:30 | 5.63 | 5.49
2019-11-13 06:00 | 5.7 | 5.58
2019-11-13 06:30 | 5.66 | 5.57
2019-11-13 07:00 | 5.63 | 5.57
2019-11-13 07:30 | 5.64 | 5.61
2019-11-13 08:00 | 5.2 | 5.18
2019-11-13 08:30 | 4.58 | 4.57
2019-11-13 09:00 | 4.45 | 4.45
2019-11-13 09:30 | 4.77 | 4.77
2019-11-13 10:00 | 5.14 | 5.13
2019-11-13 10:30 | 5.77 | 5.74
2019-11-13 11:00 | 6.55 | 6.5
2019-11-13 11:30 | 7.41 | 7.35
2019-11-13 12:00 | 7.97 | 7.91
2019-11-13 12:30 | 8.25 | 8.18
2019-11-13 13:00 | 8.96 | 8.88
2019-11-13 13:30 | 9.21 | 9.14
2019-11-13 14:00 | 8.98 | 8.91
2019-11-13 14:30 | 9.26 | 9.19
2019-11-13 15:00 | 9.57 | 9.52
2019-11-13 15:30 | 11.04 | 11.01
2019-11-13 16:00 | 11.29 | 11.26
2019-11-13 16:30 | 12.12 | 12.1
2019-11-13 17:00 | 12.85 | 12.84
2019-11-13 17:30 | 13.22 | 13.21
2019-11-13 18:00 | 13.23 | 13.23
2019-11-13 18:30 | 13.56 | 13.56
2019-11-13 19:00 | 14.32 | 14.32
2019-11-13 19:30 | 13.83 | 13.82
2019-11-13 20:00 | 13.49 | 13.49
2019-11-13 20:30 | 12.95 | 12.95
2019-11-13 21:00 | 12.05 | 12.05
2019-11-13 21:30 | 11.01 | 11
2019-11-13 22:00 | 10 | 9.99
2019-11-13 22:30 | 9.16 | 9.15
2019-11-13 23:00 | 8.33 | 8.3
2019-11-13 23:30 | 7.28 | 7.23
2019-11-14 | 6.5 | 6.44
2019-11-14 00:30 | 5.85 | 5.77
2019-11-14 01:00 | 5.56 | 5.48
2019-11-14 01:30 | 5.32 | 5.23
2019-11-14 02:00 | 4.96 | 4.85
2019-11-14 02:30 | 4.88 | 4.77
2019-11-14 03:00 | 4.77 | 4.64
2019-11-14 03:30 | 4.88 | 4.76
2019-11-14 04:00 | 4.86 | 4.74
2019-11-14 04:30 | 4.92 | 4.79
2019-11-14 05:00 | 4.96 | 4.78
2019-11-14 05:30 | 5.12 | 4.93
2019-11-14 06:00 | 5.45 | 5.29
2019-11-14 06:30 | 5.5 | 5.39
2019-11-14 07:00 | 5.46 | 5.37
2019-11-14 07:30 | 5.16 | 5.11
2019-11-14 08:00 | 4.36 | 4.32
2019-11-14 08:30 | 4.02 | 4
2019-11-14 09:00 | 3.15 | 3.14
2019-11-14 09:30 | 2.79 | 2.78
2019-11-14 10:00 | 2.62 | 2.6
2019-11-14 10:30 | 2.61 | 2.6
2019-11-14 11:00 | 2.76 | 2.74
2019-11-14 11:30 | 3.26 | 3.24
2019-11-14 12:00 | 3.84 | 3.82
2019-11-14 12:30 | 4.34 | 4.32
2019-11-14 13:00 | 5.17 | 5.13
2019-11-14 13:30 | 6.16 | 6.12
2019-11-14 14:00 | 7.17 | 7.13
2019-11-14 14:30 | 8.15 | 8.11
2019-11-14 15:00 | 9.24 | 9.2
2019-11-14 15:30 | 10.72 | 10.68
2019-11-14 16:00 | 11.8 | 11.76
2019-11-14 16:30 | 12.68 | 12.65
2019-11-14 17:00 | 13.15 | 13.13
2019-11-14 17:30 | 13.47 | 13.46
2019-11-14 18:00 | 13.47 | 13.46
2019-11-14 18:30 | 13.5 | 13.5
2019-11-14 19:00 | 14.22 | 14.21
2019-11-14 19:30 | 14.03 | 14.03
2019-11-14 20:00 | 13.77 | 13.77
2019-11-14 20:30 | 13.16 | 13.16
2019-11-14 21:00 | 12.45 | 12.45
2019-11-14 21:30 | 11.47 | 11.46
2019-11-14 22:00 | 10.37 | 10.37
2019-11-14 22:30 | 9.42 | 9.41
2019-11-14 23:00 | 8.9 | 8.88
2019-11-14 23:30 | 7.97 | 7.94
2019-11-15 | 7.04 | 7.01
2019-11-15 00:30 | 6.25 | 6.19
2019-11-15 01:00 | 5.97 | 5.91
2019-11-15 01:30 | 5.69 | 5.62
2019-11-15 02:00 | 5.49 | 5.42
2019-11-15 02:30 | 5.31 | 5.23
2019-11-15 03:00 | 5.15 | 5.07
2019-11-15 03:30 | 5.18 | 5.09
2019-11-15 04:00 | 5.26 | 5.17
2019-11-15 04:30 | 5.23 | 5.14
2019-11-15 05:00 | 5.24 | 5.1
2019-11-15 05:30 | 5.36 | 5.19
2019-11-15 06:00 | 5.33 | 5.18
2019-11-15 06:30 | 5.29 | 5.17
2019-11-15 07:00 | 5.19 | 5.1
2019-11-15 07:30 | 5.06 | 5.01
2019-11-15 08:00 | 4.63 | 4.59
2019-11-15 08:30 | 3.66 | 3.64
2019-11-15 09:00 | 3.37 | 3.34
2019-11-15 09:30 | 3.35 | 3.32
2019-11-15 10:00 | 3.67 | 3.64
2019-11-15 10:30 | 3.78 | 3.74
2019-11-15 11:00 | 4.35 | 4.32
2019-11-15 11:30 | 5.12 | 5.09
2019-11-15 12:00 | 5.8 | 5.75
2019-11-15 12:30 | 6.58 | 6.53
2019-11-15 13:00 | 7.61 | 7.55
2019-11-15 13:30 | 8.78 | 8.71
2019-11-15 14:00 | 10.1 | 10.03
2019-11-15 14:30 | 11.26 | 11.19
2019-11-15 15:00 | 12.34 | 12.26
2019-11-15 15:30 | 13.69 | 13.61
2019-11-15 16:00 | 15.16 | 15.08
2019-11-15 16:30 | 16.52 | 16.43
2019-11-15 17:00 | 17.2 | 17.13
2019-11-15 17:30 | 17.24 | 17.18
2019-11-15 18:00 | 16.84 | 16.79
2019-11-15 18:30 | 16.45 | 16.41
2019-11-15 19:00 | 16.55 | 16.5
2019-11-15 19:30 | 16.18 | 16.13
2019-11-15 20:00 | 15.65 | 15.62
2019-11-15 20:30 | 15 | 14.97
2019-11-15 21:00 | 13.89 | 13.88
2019-11-15 21:30 | 12.72 | 12.71
2019-11-15 22:00 | 11.69 | 11.68
2019-11-15 22:30 | 10.98 | 10.98
2019-11-15 23:00 | 10.39 | 10.39
2019-11-15 23:30 | 9.29 | 9.28
2019-11-16 | 8.22 | 8.21
2019-11-16 00:30 | 7.55 | 7.53
2019-11-16 01:00 | 7 | 6.97
2019-11-16 01:30 | 6.56 | 6.52
2019-11-16 02:00 | 6.18 | 6.14
2019-11-16 02:30 | 5.99 | 5.94
2019-11-16 03:00 | 5.73 | 5.67
2019-11-16 03:30 | 5.62 | 5.56
2019-11-16 04:00 | 5.55 | 5.48
2019-11-16 04:30 | 5.54 | 5.47
2019-11-16 05:00 | 5.33 | 5.21
2019-11-16 05:30 | 5.17 | 5
2019-11-16 06:00 | 4.92 | 4.74
2019-11-16 06:30 | 4.65 | 4.5
2019-11-16 07:00 | 4.42 | 4.31
2019-11-16 07:30 | 4.4 | 4.33
2019-11-16 08:00 | 4.34 | 4.3
2019-11-16 08:30 | 4.39 | 4.37
2019-11-16 09:00 | 4.88 | 4.86
2019-11-16 09:30 | 5.53 | 5.5
2019-11-16 10:00 | 6.27 | 6.24
2019-11-16 10:30 | 7.27 | 7.23
2019-11-16 11:00 | 8.14 | 8.09
2019-11-16 11:30 | 9.17 | 9.11
2019-11-16 12:00 | 10.41 | 10.33
2019-11-16 12:30 | 11.8 | 11.7
2019-11-16 13:00 | 13.16 | 13.05
2019-11-16 13:30 | 14.34 | 14.22
2019-11-16 14:00 | 18.19 | 18.07
2019-11-16 14:30 | 16.47 | 16.35
2019-11-16 15:00 | 18.15 | 18.04
2019-11-16 15:30 | 19.29 | 19.18
2019-11-16 16:00 | 18.84 | 18.74
2019-11-16 16:30 | 18.67 | 18.57
2019-11-16 17:00 | 18.85 | 18.76
2019-11-16 17:30 | 18.64 | 18.57
2019-11-16 18:00 | 18.12 | 18.06
2019-11-16 18:30 | 17.25 | 17.21
2019-11-16 19:00 | 16.93 | 16.88
2019-11-16 19:30 | 16.51 | 16.46
2019-11-16 20:00 | 15.88 | 15.84
2019-11-16 20:30 | 15.13 | 15.1
2019-11-16 21:00 | 14.15 | 14.14
2019-11-16 21:30 | 12.99 | 12.98
2019-11-16 22:00 | 11.94 | 11.93
2019-11-16 22:30 | 11.18 | 11.17
2019-11-16 23:00 | 10.59 | 10.58
2019-11-16 23:30 | 9.37 | 9.36
2019-11-17 | 8.38 | 8.37
2019-11-17 00:30 | 7.55 | 7.53
2019-11-17 01:00 | 7.12 | 7.1
2019-11-17 01:30 | 6.69 | 6.66
2019-11-17 02:00 | 6.3 | 6.26
2019-11-17 02:30 | 6.11 | 6.07
2019-11-17 03:00 | 5.85 | 5.8
2019-11-17 03:30 | 5.75 | 5.7
2019-11-17 04:00 | 5.58 | 5.51
2019-11-17 04:30 | 5.54 | 5.47
2019-11-17 05:00 | 5.3 | 5.17
2019-11-17 05:30 | 5.16 | 5
2019-11-17 06:00 | 4.91 | 4.75
2019-11-17 06:30 | 4.92 | 4.78
2019-11-17 07:00 | 4.71 | 4.58
2019-11-17 07:30 | 4.92 | 4.83
2019-11-17 08:00 | 4.63 | 4.56
2019-11-17 08:30 | 4.04 | 4.01
2019-11-17 09:00 | 4.29 | 4.27
2019-11-17 09:30 | 4.71 | 4.69
2019-11-17 10:00 | 5.32 | 5.3
2019-11-17 10:30 | 6.12 | 6.09
2019-11-17 11:00 | 7.14 | 7.11
2019-11-17 11:30 | 8.45 | 8.4
2019-11-17 12:00 | 9.98 | 9.91
2019-11-17 12:30 | 12.49 | 12.41
2019-11-17 13:00 | 11.83 | 11.73
2019-11-17 13:30 | 12.85 | 12.74
2019-11-17 14:00 | 13.42 | 13.31
2019-11-17 14:30 | 13.89 | 13.79
2019-11-17 15:00 | 14.38 | 14.29
2019-11-17 15:30 | 15.38 | 15.31
2019-11-17 16:00 | 15.53 | 15.47
2019-11-17 16:30 | 17.16 | 17.1
2019-11-17 17:00 | 17.3 | 17.24
2019-11-17 17:30 | 17.35 | 17.3
2019-11-17 18:00 | 17.3 | 17.26
2019-11-17 18:30 | 16.72 | 16.69
2019-11-17 19:00 | 16.7 | 16.67
2019-11-17 19:30 | 16.38 | 16.35
2019-11-17 20:00 | 15.7 | 15.68
2019-11-17 20:30 | 14.94 | 14.93
2019-11-17 21:00 | 13.91 | 13.9
2019-11-17 21:30 | 12.58 | 12.57
2019-11-17 22:00 | 11.61 | 11.6
2019-11-17 22:30 | 10.8 | 10.79
2019-11-17 23:00 | 9.86 | 9.86
2019-11-17 23:30 | 8.5 | 8.49
2019-11-18 | 7.44 | 7.42
2019-11-18 00:30 | 6.76 | 6.72
2019-11-18 01:00 | 6.42 | 6.38
2019-11-18 01:30 | 6.15 | 6.1
2019-11-18 02:00 | 5.77 | 5.71
2019-11-18 02:30 | 5.57 | 5.5
2019-11-18 03:00 | 5.4 | 5.33
2019-11-18 03:30 | 5.36 | 5.28
2019-11-18 04:00 | 5.37 | 5.29
2019-11-18 04:30 | 5.41 | 5.33
2019-11-18 05:00 | 5.36 | 5.22
2019-11-18 05:30 | 5.45 | 5.3
2019-11-18 06:00 | 5.6 | 5.47
2019-11-18 06:30 | 5.76 | 5.66
2019-11-18 07:00 | 5.88 | 5.81
2019-11-18 07:30 | 5.92 | 5.87
2019-11-18 08:00 | 5.26 | 5.22
2019-11-18 08:30 | 5.12 | 5.1
2019-11-18 09:00 | 4.57 | 4.56
2019-11-18 09:30 | 3.94 | 3.94
2019-11-18 10:00 | 3.06 | 3.05
2019-11-18 10:30 | 2.74 | 2.74
2019-11-18 11:00 | 2.89 | 2.88
2019-11-18 11:30 | 2.82 | 2.81
2019-11-18 12:00 | 2.94 | 2.93
2019-11-18 12:30 | 3.56 | 3.54
2019-11-18 13:00 | 3.75 | 3.74
2019-11-18 13:30 | 4.23 | 4.22
2019-11-18 14:00 | 5.18 | 5.17
2019-11-18 14:30 | 5.98 | 5.97
2019-11-18 15:00 | 6.87 | 6.86
2019-11-18 15:30 | 8.16 | 8.15
2019-11-18 16:00 | 9.5 | 9.49
2019-11-18 16:30 | 10.66 | 10.65
2019-11-18 17:00 | 11.65 | 11.65
2019-11-18 17:30 | 12.86 | 12.86
2019-11-18 18:00 | 13.24 | 13.23
2019-11-18 18:30 | 13.44 | 13.44
2019-11-18 19:00 | 14.05 | 14.04
2019-11-18 19:30 | 13.46 | 13.45
2019-11-18 20:00 | 13.11 | 13.11
2019-11-18 20:30 | 12.5 | 12.5
2019-11-18 21:00 | 11.53 | 11.53
2019-11-18 21:30 | 10.76 | 10.75
2019-11-18 22:00 | 9.86 | 9.85
2019-11-18 22:30 | 8.86 | 8.83
2019-11-18 23:00 | 8.3 | 8.26
2019-11-18 23:30 | 7.22 | 7.16
2019-11-19 | 6.37 | 6.3
2019-11-19 00:30 | 5.85 | 5.78
2019-11-19 01:00 | 5.54 | 5.45
2019-11-19 01:30 | 5.32 | 5.22
2019-11-19 02:00 | 5.04 | 4.94
2019-11-19 02:30 | 4.93 | 4.81
2019-11-19 03:00 | 4.83 | 4.71
2019-11-19 03:30 | 4.83 | 4.7
2019-11-19 04:00 | 4.82 | 4.7
2019-11-19 04:30 | 4.93 | 4.81
2019-11-19 05:00 | 5.06 | 4.88
2019-11-19 05:30 | 5.21 | 5.01
2019-11-19 06:00 | 5.26 | 5.09
2019-11-19 06:30 | 4.99 | 4.83
2019-11-19 07:00 | 5.05 | 4.94
2019-11-19 07:30 | 5.15 | 5.08
2019-11-19 08:00 | 5.42 | 5.38
2019-11-19 08:30 | 4.55 | 4.51
2019-11-19 09:00 | 3.09 | 3.07
2019-11-19 09:30 | 2.34 | 2.33
2019-11-19 10:00 | 2.4 | 2.39
2019-11-19 10:30 | 2.33 | 2.32
2019-11-19 11:00 | 2.72 | 2.71
2019-11-19 11:30 | 3.29 | 3.28
2019-11-19 12:00 | 3.73 | 3.72
2019-11-19 12:30 | 4.85 | 4.82
2019-11-19 13:00 | 5.92 | 5.89
2019-11-19 13:30 | 7 | 6.96
2019-11-19 14:00 | 8.17 | 8.13
2019-11-19 14:30 | 9.6 | 9.55
2019-11-19 15:00 | 10.94 | 10.88
2019-11-19 15:30 | 12.43 | 12.37
2019-11-19 16:00 | 13.99 | 13.93
2019-11-19 16:30 | 15.13 | 15.08
2019-11-19 17:00 | 15.95 | 15.9
2019-11-19 17:30 | 16.44 | 16.39
2019-11-19 18:00 | 16.3 | 16.27
2019-11-19 18:30 | 16.2 | 16.18
2019-11-19 19:00 | 16.51 | 16.48
2019-11-19 19:30 | 15.83 | 15.81
2019-11-19 20:00 | 15.2 | 15.18
2019-11-19 20:30 | 14.73 | 14.72
2019-11-19 21:00 | 13.45 | 13.44
2019-11-19 21:30 | 11.95 | 11.94
2019-11-19 22:00 | 10.65 | 10.64
2019-11-19 22:30 | 9.85 | 9.85
2019-11-19 23:00 | 9.31 | 9.3
2019-11-19 23:30 | 8.25 | 8.24
2019-11-20 | 7.22 | 7.19
2019-11-20 00:30 | 6.56 | 6.52
2019-11-20 01:00 | 6.32 | 6.27
2019-11-20 01:30 | 6.02 | 5.97
2019-11-20 02:00 | 5.79 | 5.74
2019-11-20 02:30 | 5.54 | 5.48
2019-11-20 03:00 | 5.43 | 5.36
2019-11-20 03:30 | 5.42 | 5.35
2019-11-20 04:00 | 5.38 | 5.3
2019-11-20 04:30 | 5.44 | 5.35
2019-11-20 05:00 | 5.43 | 5.29
2019-11-20 05:30 | 5.6 | 5.46
2019-11-20 06:00 | 5.54 | 5.4
2019-11-20 06:30 | 5.49 | 5.38
2019-11-20 07:00 | 5.34 | 5.26
2019-11-20 07:30 | 5.14 | 5.09
2019-11-20 08:00 | 4.9 | 4.88
2019-11-20 08:30 | 4.64 | 4.63
2019-11-20 09:00 | 4.66 | 4.65
2019-11-20 09:30 | 4.88 | 4.87
2019-11-20 10:00 | 5.33 | 5.3
2019-11-20 10:30 | 5.7 | 5.67
2019-11-20 11:00 | 6.68 | 6.64
2019-11-20 11:30 | 7.66 | 7.6
2019-11-20 12:00 | 8.63 | 8.55
2019-11-20 12:30 | 9.94 | 9.84
2019-11-20 13:00 | 11.02 | 10.92
2019-11-20 13:30 | 12.03 | 11.92
2019-11-20 14:00 | 13.35 | 13.23
2019-11-20 14:30 | 14.34 | 14.23
2019-11-20 15:00 | 14.78 | 14.67
2019-11-20 15:30 | 16.11 | 15.98
2019-11-20 16:00 | 17.24 | 17.11
2019-11-20 16:30 | 17.63 | 17.53
2019-11-20 17:00 | 18.12 | 18.03
2019-11-20 17:30 | 18.33 | 18.26
2019-11-20 18:00 | 17.82 | 17.76
2019-11-20 18:30 | 17.44 | 17.4
2019-11-20 19:00 | 17.55 | 17.49
2019-11-20 19:30 | 17.05 | 17
2019-11-20 20:00 | 16.76 | 16.72
2019-11-20 20:30 | 15.78 | 15.76
2019-11-20 21:00 | 14.94 | 14.92
2019-11-20 21:30 | 13.73 | 13.72
2019-11-20 22:00 | 12.42 | 12.42
2019-11-20 22:30 | 11.25 | 11.25
2019-11-20 23:00 | 10.52 | 10.52
2019-11-20 23:30 | 9.36 | 9.35
2019-11-21 | 8.22 | 8.21
2019-11-21 00:30 | 7.53 | 7.51
2019-11-21 01:00 | 7.21 | 7.19
2019-11-21 01:30 | 7.02 | 7
2019-11-21 02:00 | 6.61 | 6.59
2019-11-21 02:30 | 6.4 | 6.36
2019-11-21 03:00 | 6.28 | 6.25
2019-11-21 03:30 | 6.17 | 6.13
2019-11-21 04:00 | 6.13 | 6.09
2019-11-21 04:30 | 6.11 | 6.07
2019-11-21 05:00 | 6.05 | 5.97
2019-11-21 05:30 | 6.18 | 6.08
2019-11-21 06:00 | 6.58 | 6.51
2019-11-21 06:30 | 7.01 | 6.96
2019-11-21 07:00 | 7.34 | 7.31
2019-11-21 07:30 | 6.9 | 6.89
2019-11-21 08:00 | 6.31 | 6.3
2019-11-21 08:30 | 5.68 | 5.67
2019-11-21 09:00 | 5.24 | 5.23
2019-11-21 09:30 | 5.11 | 5.09
2019-11-21 10:00 | 4.7 | 4.67
2019-11-21 10:30 | 4.26 | 4.23
2019-11-21 11:00 | 4.31 | 4.27
2019-11-21 11:30 | 4.62 | 4.59
2019-11-21 12:00 | 5.19 | 5.16
2019-11-21 12:30 | 5.79 | 5.75
2019-11-21 13:00 | 6.37 | 6.33
2019-11-21 13:30 | 7.21 | 7.16
2019-11-21 14:00 | 7.89 | 7.85
2019-11-21 14:30 | 8.6 | 8.57
2019-11-21 15:00 | 9.47 | 9.44
2019-11-21 15:30 | 10.46 | 10.42
2019-11-21 16:00 | 11.56 | 11.52
2019-11-21 16:30 | 12.81 | 12.78
2019-11-21 17:00 | 13.66 | 13.64
2019-11-21 17:30 | 14.14 | 14.12
2019-11-21 18:00 | 14.1 | 14.09
2019-11-21 18:30 | 14.27 | 14.26
2019-11-21 19:00 | 14.79 | 14.77
2019-11-21 19:30 | 14.51 | 14.5
2019-11-21 20:00 | 14.05 | 14.05
2019-11-21 20:30 | 13.23 | 13.23
2019-11-21 21:00 | 12.3 | 12.3
2019-11-21 21:30 | 11.66 | 11.66
2019-11-21 22:00 | 10.62 | 10.62
2019-11-21 22:30 | 9.57 | 9.56
2019-11-21 23:00 | 8.92 | 8.9
2019-11-21 23:30 | 7.94 | 7.91
2019-11-22 | 6.98 | 6.94
2019-11-22 00:30 | 6.42 | 6.37
2019-11-22 01:00 | 6.14 | 6.08
2019-11-22 01:30 | 5.81 | 5.74
2019-11-22 02:00 | 5.48 | 5.4
2019-11-22 02:30 | 5.34 | 5.26
2019-11-22 03:00 | 5.31 | 5.22
2019-11-22 03:30 | 5.23 | 5.14
2019-11-22 04:00 | 5.2 | 5.11
2019-11-22 04:30 | 5.32 | 5.22
2019-11-22 05:00 | 5.2 | 5.05
2019-11-22 05:30 | 5.29 | 5.13
2019-11-22 06:00 | 5.52 | 5.39
2019-11-22 06:30 | 5.89 | 5.81
2019-11-22 07:00 | 5.84 | 5.78
2019-11-22 07:30 | 5.67 | 5.62
2019-11-22 08:00 | 5.45 | 5.42
2019-11-22 08:30 | 5.41 | 5.38
2019-11-22 09:00 | 4.79 | 4.78
2019-11-22 09:30 | 4.9 | 4.9
2019-11-22 10:00 | 4.82 | 4.81
2019-11-22 10:30 | 4.2 | 4.19
2019-11-22 11:00 | 3.35 | 3.33
2019-11-22 11:30 | 3.65 | 3.63
2019-11-22 12:00 | 4.07 | 4.04
2019-11-22 12:30 | 4.97 | 4.94
2019-11-22 13:00 | 5.6 | 5.56
2019-11-22 13:30 | 6.67 | 6.64
2019-11-22 14:00 | 7.37 | 7.34
2019-11-22 14:30 | 8.24 | 8.21
2019-11-22 15:00 | 9.13 | 9.09
2019-11-22 15:30 | 9.97 | 9.95
2019-11-22 16:00 | 10.95 | 10.93
2019-11-22 16:30 | 11.79 | 11.78
2019-11-22 17:00 | 12.59 | 12.58
2019-11-22 17:30 | 12.75 | 12.73
2019-11-22 18:00 | 12.61 | 12.6
2019-11-22 18:30 | 12.78 | 12.77
2019-11-22 19:00 | 13.26 | 13.25
2019-11-22 19:30 | 13.06 | 13.05
2019-11-22 20:00 | 12.71 | 12.7
2019-11-22 20:30 | 12.36 | 12.35
2019-11-22 21:00 | 11.6 | 11.59
2019-11-22 21:30 | 10.72 | 10.72
2019-11-22 22:00 | 9.97 | 9.96
2019-11-22 22:30 | 9.4 | 9.38
2019-11-22 23:00 | 9.02 | 9
2019-11-22 23:30 | 8.03 | 8
2019-11-23 | 7.18 | 7.14
2019-11-23 00:30 | 6.59 | 6.54
2019-11-23 01:00 | 6.33 | 6.28
2019-11-23 01:30 | 5.96 | 5.89
2019-11-23 02:00 | 5.69 | 5.61
2019-11-23 02:30 | 5.43 | 5.34
2019-11-23 03:00 | 5.28 | 5.18
2019-11-23 03:30 | 5.24 | 5.15
2019-11-23 04:00 | 5.17 | 5.07
2019-11-23 04:30 | 5.11 | 5
2019-11-23 05:00 | 5 | 4.8
2019-11-23 05:30 | 4.85 | 4.62
2019-11-23 06:00 | 4.42 | 4.18
2019-11-23 06:30 | 4.18 | 3.96
2019-11-23 07:00 | 4.01 | 3.84
2019-11-23 07:30 | 4.23 | 4.11
2019-11-23 08:00 | 4.93 | 4.86
2019-11-23 08:30 | 4.31 | 4.26
2019-11-23 09:00 | 3.61 | 3.58
2019-11-23 09:30 | 4.11 | 4.07
2019-11-23 10:00 | 3.69 | 3.64
2019-11-23 10:30 | 3.88 | 3.83
2019-11-23 11:00 | 4.26 | 4.22
2019-11-23 11:30 | 4.91 | 4.86
2019-11-23 12:00 | 5.64 | 5.6
2019-11-23 12:30 | 6.37 | 6.32
2019-11-23 13:00 | 6.88 | 6.84
2019-11-23 13:30 | 7.85 | 7.8
2019-11-23 14:00 | 8.72 | 8.68
2019-11-23 14:30 | 9.36 | 9.32
2019-11-23 15:00 | 10.3 | 10.26
2019-11-23 15:30 | 11.08 | 11.04
2019-11-23 16:00 | 11.92 | 11.89
2019-11-23 16:30 | 12.74 | 12.72
2019-11-23 17:00 | 13.33 | 13.31
2019-11-23 17:30 | 13.62 | 13.6
2019-11-23 18:00 | 13.36 | 13.34
2019-11-23 18:30 | 13.01 | 12.99
2019-11-23 19:00 | 13.18 | 13.17
2019-11-23 19:30 | 13.02 | 13.01
2019-11-23 20:00 | 12.59 | 12.58
2019-11-23 20:30 | 12.09 | 12.08
2019-11-23 21:00 | 11.19 | 11.19
2019-11-23 21:30 | 10.4 | 10.39
2019-11-23 22:00 | 9.7 | 9.7
2019-11-23 22:30 | 9.26 | 9.24
2019-11-23 23:00 | 8.99 | 8.97
2019-11-23 23:30 | 8 | 7.97
2019-11-24 | 7.18 | 7.14
2019-11-24 00:30 | 6.64 | 6.59
2019-11-24 01:00 | 6.33 | 6.27
2019-11-24 01:30 | 6.02 | 5.96
2019-11-24 02:00 | 5.65 | 5.58
2019-11-24 02:30 | 5.51 | 5.43
2019-11-24 03:00 | 5.27 | 5.18
2019-11-24 03:30 | 5.2 | 5.09
2019-11-24 04:00 | 5.15 | 5.05
2019-11-24 04:30 | 5.1 | 4.99
2019-11-24 05:00 | 4.91 | 4.72
2019-11-24 05:30 | 4.76 | 4.53
2019-11-24 06:00 | 4.52 | 4.3
2019-11-24 06:30 | 4.16 | 3.94
2019-11-24 07:00 | 4.01 | 3.83
2019-11-24 07:30 | 4.11 | 4.01
2019-11-24 08:00 | 4.28 | 4.22
2019-11-24 08:30 | 4.48 | 4.45
2019-11-24 09:00 | 4.69 | 4.66
2019-11-24 09:30 | 5.65 | 5.61
2019-11-24 10:00 | 6.08 | 6.04
2019-11-24 10:30 | 6.35 | 6.31
2019-11-24 11:00 | 7.33 | 7.3
2019-11-24 11:30 | 8.46 | 8.43
2019-11-24 12:00 | 7.61 | 7.56
2019-11-24 12:30 | 8.06 | 8.01
2019-11-24 13:00 | 8.85 | 8.79
2019-11-24 13:30 | 10.64 | 10.57
2019-11-24 14:00 | 11.75 | 11.69
2019-11-24 14:30 | 13.77 | 13.72
2019-11-24 15:00 | 11.43 | 11.38
2019-11-24 15:30 | 11.2 | 11.17
2019-11-24 16:00 | 11.58 | 11.55
2019-11-24 16:30 | 13.26 | 13.24
2019-11-24 17:00 | 14.27 | 14.26
2019-11-24 17:30 | 14.09 | 14.08
2019-11-24 18:00 | 13.72 | 13.71
2019-11-24 18:30 | 13.67 | 13.66
2019-11-24 19:00 | 14.1 | 14.1
2019-11-24 19:30 | 13.74 | 13.73
2019-11-24 20:00 | 13.46 | 13.46
2019-11-24 20:30 | 12.88 | 12.88
2019-11-24 21:00 | 11.84 | 11.84
2019-11-24 21:30 | 10.82 | 10.82
2019-11-24 22:00 | 10.02 | 10.01
2019-11-24 22:30 | 9.25 | 9.23
2019-11-24 23:00 | 8.72 | 8.7
2019-11-24 23:30 | 7.76 | 7.72
2019-11-25 | 6.99 | 6.94
2019-11-25 00:30 | 6.5 | 6.45
2019-11-25 01:00 | 6.17 | 6.11
2019-11-25 01:30 | 5.81 | 5.74
2019-11-25 02:00 | 5.65 | 5.57
2019-11-25 02:30 | 5.46 | 5.37
2019-11-25 03:00 | 5.33 | 5.24
2019-11-25 03:30 | 5.29 | 5.19
2019-11-25 04:00 | 5.33 | 5.25
2019-11-25 04:30 | 5.39 | 5.31
2019-11-25 05:00 | 5.42 | 5.27
2019-11-25 05:30 | 5.43 | 5.27
2019-11-25 06:00 | 5.35 | 5.19
2019-11-25 06:30 | 5.39 | 5.26
2019-11-25 07:00 | 6.32 | 6.23
2019-11-25 07:30 | 4.69 | 4.6
2019-11-25 08:00 | 3.87 | 3.8
2019-11-25 08:30 | 4.48 | 4.44
2019-11-25 09:00 | 3.16 | 3.14
2019-11-25 09:30 | 4.69 | 4.68
2019-11-25 10:00 | 2.78 | 2.76
2019-11-25 10:30 | 2.9 | 2.86
2019-11-25 11:00 | 3.19 | 3.16
2019-11-25 11:30 | 3.74 | 3.71
2019-11-25 12:00 | 4.18 | 4.15
2019-11-25 12:30 | 4.74 | 4.71
2019-11-25 13:00 | 5.85 | 5.81
2019-11-25 13:30 | 7.11 | 7.06
2019-11-25 14:00 | 8.11 | 8.05
2019-11-25 14:30 | 9.03 | 8.97
2019-11-25 15:00 | 9.88 | 9.82
2019-11-25 15:30 | 10.79 | 10.75
2019-11-25 16:00 | 12.12 | 12.08
2019-11-25 16:30 | 13.32 | 13.28
2019-11-25 17:00 | 14.33 | 14.3
2019-11-25 17:30 | 15.19 | 15.16
2019-11-25 18:00 | 15.25 | 15.23
2019-11-25 18:30 | 14.77 | 14.76
2019-11-25 19:00 | 14.93 | 14.91
2019-11-25 19:30 | 14.82 | 14.81
2019-11-25 20:00 | 14.36 | 14.35
2019-11-25 20:30 | 13.65 | 13.64
2019-11-25 21:00 | 12.5 | 12.49
2019-11-25 21:30 | 11.34 | 11.34
2019-11-25 22:00 | 10.33 | 10.32
2019-11-25 22:30 | 9.69 | 9.68
2019-11-25 23:00 | 9.18 | 9.17
2019-11-25 23:30 | 8.05 | 8.02
2019-11-26 | 7.21 | 7.17
2019-11-26 00:30 | 6.6 | 6.55
2019-11-26 01:00 | 6.3 | 6.26
2019-11-26 01:30 | 6.05 | 5.99
2019-11-26 02:00 | 5.8 | 5.73
2019-11-26 02:30 | 5.61 | 5.55
2019-11-26 03:00 | 5.58 | 5.52
2019-11-26 03:30 | 5.54 | 5.47
2019-11-26 04:00 | 5.54 | 5.47
2019-11-26 04:30 | 5.55 | 5.48
2019-11-26 05:00 | 5.56 | 5.42
2019-11-26 05:30 | 5.79 | 5.66
2019-11-26 06:00 | 6 | 5.9
2019-11-26 06:30 | 5.72 | 5.63
2019-11-26 07:00 | 5.69 | 5.63
2019-11-26 07:30 | 5.68 | 5.65
2019-11-26 08:00 | 5.2 | 5.19
2019-11-26 08:30 | 5.7 | 5.7
2019-11-26 09:00 | 5.88 | 5.87
2019-11-26 09:30 | 5.84 | 5.84
2019-11-26 10:00 | 4.36 | 4.34
2019-11-26 10:30 | 4.22 | 4.19
2019-11-26 11:00 | 4.76 | 4.73
2019-11-26 11:30 | 6.01 | 5.97
2019-11-26 12:00 | 6.49 | 6.43
2019-11-26 12:30 | 7.7 | 7.66
2019-11-26 13:00 | 7.49 | 7.44
2019-11-26 13:30 | 8.12 | 8.05
2019-11-26 14:00 | 9.15 | 9.08
2019-11-26 14:30 | 9.93 | 9.85
2019-11-26 15:00 | 11.29 | 11.21
2019-11-26 15:30 | 12.89 | 12.81
2019-11-26 16:00 | 14.16 | 14.1
2019-11-26 16:30 | 15.05 | 14.98
2019-11-26 17:00 | 16.33 | 16.26
2019-11-26 17:30 | 16.93 | 16.87
2019-11-26 18:00 | 17.21 | 17.16
2019-11-26 18:30 | 16.95 | 16.91
2019-11-26 19:00 | 17.24 | 17.19
2019-11-26 19:30 | 16.86 | 16.82
2019-11-26 20:00 | 16.29 | 16.26
2019-11-26 20:30 | 15.06 | 15.05
2019-11-26 21:00 | 13.74 | 13.73
2019-11-26 21:30 | 12.36 | 12.35
2019-11-26 22:00 | 11.27 | 11.27
2019-11-26 22:30 | 10.66 | 10.66
2019-11-26 23:00 | 9.97 | 9.96
2019-11-26 23:30 | 8.71 | 8.7
2019-11-27 | 7.76 | 7.74
2019-11-27 00:30 | 7.03 | 7
2019-11-27 01:00 | 6.82 | 6.79
2019-11-27 01:30 | 6.56 | 6.53
2019-11-27 02:00 | 6.23 | 6.19
2019-11-27 02:30 | 6.03 | 5.98
2019-11-27 03:00 | 5.9 | 5.85
2019-11-27 03:30 | 5.84 | 5.79
2019-11-27 04:00 | 5.88 | 5.83
2019-11-27 04:30 | 5.95 | 5.9
2019-11-27 05:00 | 5.86 | 5.75
2019-11-27 05:30 | 5.65 | 5.53
2019-11-27 06:00 | 5.78 | 5.67
2019-11-27 06:30 | 5.81 | 5.73
2019-11-27 07:00 | 5.69 | 5.63
2019-11-27 07:30 | 6.07 | 6.05
2019-11-27 08:00 | 5.9 | 5.9
2019-11-27 08:30 | 5.68 | 5.67
2019-11-27 09:00 | 5.79 | 5.78
2019-11-27 09:30 | 6.24 | 6.22
2019-11-27 10:00 | 6.7 | 6.66
2019-11-27 10:30 | 7.59 | 7.55
2019-11-27 11:00 | 9.23 | 9.18
2019-11-27 11:30 | 9.95 | 9.9
2019-11-27 12:00 | 9.08 | 8.99
2019-11-27 12:30 | 9.96 | 9.86
2019-11-27 13:00 | 10.21 | 10.11
2019-11-27 13:30 | 10.57 | 10.46
2019-11-27 14:00 | 11.99 | 11.88
2019-11-27 14:30 | 11.74 | 11.64
2019-11-27 15:00 | 12.87 | 12.79
2019-11-27 15:30 | 13.87 | 13.81
2019-11-27 16:00 | 12.88 | 12.83
2019-11-27 16:30 | 13.33 | 13.28
2019-11-27 17:00 | 14.04 | 14.01
2019-11-27 17:30 | 14.24 | 14.22
2019-11-27 18:00 | 14.14 | 14.13
2019-11-27 18:30 | 14.23 | 14.23
2019-11-27 19:00 | 14.46 | 14.45
2019-11-27 19:30 | 14.21 | 14.2
2019-11-27 20:00 | 13.82 | 13.81
2019-11-27 20:30 | 13.27 | 13.27
2019-11-27 21:00 | 12.29 | 12.29
2019-11-27 21:30 | 11.29 | 11.29
2019-11-27 22:00 | 10.3 | 10.3
2019-11-27 22:30 | 9.67 | 9.67
2019-11-27 23:00 | 9.23 | 9.22
2019-11-27 23:30 | 8.22 | 8.2
2019-11-28 | 7.31 | 7.28
2019-11-28 00:30 | 6.7 | 6.66
2019-11-28 01:00 | 6.45 | 6.41
2019-11-28 01:30 | 6.14 | 6.09
2019-11-28 02:00 | 5.89 | 5.83
2019-11-28 02:30 | 5.73 | 5.67
2019-11-28 03:00 | 5.68 | 5.62
2019-11-28 03:30 | 5.63 | 5.58
2019-11-28 04:00 | 5.63 | 5.57
2019-11-28 04:30 | 5.69 | 5.63
2019-11-28 05:00 | 5.75 | 5.65
2019-11-28 05:30 | 5.9 | 5.79
2019-11-28 06:00 | 6.47 | 6.37
2019-11-28 06:30 | 6.59 | 6.51
2019-11-28 07:00 | 6.98 | 6.92
2019-11-28 07:30 | 7.32 | 7.27
2019-11-28 08:00 | 7.66 | 7.62
2019-11-28 08:30 | 7.49 | 7.46
2019-11-28 09:00 | 7.11 | 7.09
2019-11-28 09:30 | 5.42 | 5.41
2019-11-28 10:00 | 5.2 | 5.2
2019-11-28 10:30 | 4.64 | 4.63
2019-11-28 11:00 | 5.11 | 5.1
2019-11-28 11:30 | 4.37 | 4.35
2019-11-28 12:00 | 5.39 | 5.37
2019-11-28 12:30 | 6.24 | 6.22
2019-11-28 13:00 | 6.51 | 6.49
2019-11-28 13:30 | 6.4 | 6.37
2019-11-28 14:00 | 6.39 | 6.36
2019-11-28 14:30 | 7.47 | 7.44
2019-11-28 15:00 | 8.2 | 8.17
2019-11-28 15:30 | 9.52 | 9.49
2019-11-28 16:00 | 11.34 | 11.31
2019-11-28 16:30 | 12.69 | 12.66
2019-11-28 17:00 | 13.84 | 13.81
2019-11-28 17:30 | 14.55 | 14.53
2019-11-28 18:00 | 14.68 | 14.65
2019-11-28 18:30 | 14.87 | 14.86
2019-11-28 19:00 | 15.24 | 15.22
2019-11-28 19:30 | 15.08 | 15.06
2019-11-28 20:00 | 14.82 | 14.8
2019-11-28 20:30 | 14.24 | 14.23
2019-11-28 21:00 | 13.19 | 13.18
2019-11-28 21:30 | 12.11 | 12.11
2019-11-28 22:00 | 11.23 | 11.22
2019-11-28 22:30 | 10.48 | 10.48
2019-11-28 23:00 | 9.93 | 9.93
2019-11-28 23:30 | 8.87 | 8.86
2019-11-29 | 7.87 | 7.85
2019-11-29 00:30 | 7.23 | 7.21
2019-11-29 01:00 | 6.92 | 6.9
2019-11-29 01:30 | 6.59 | 6.56
2019-11-29 02:00 | 6.24 | 6.2
2019-11-29 02:30 | 6.06 | 6.02
2019-11-29 03:00 | 5.93 | 5.88
2019-11-29 03:30 | 5.89 | 5.84
2019-11-29 04:00 | 5.89 | 5.85
2019-11-29 04:30 | 6.01 | 5.97
2019-11-29 05:00 | 5.94 | 5.86
2019-11-29 05:30 | 5.98 | 5.89
2019-11-29 06:00 | 5.86 | 5.77
2019-11-29 06:30 | 5.57 | 5.5
2019-11-29 07:00 | 6.18 | 6.15
2019-11-29 07:30 | 5.93 | 5.9
2019-11-29 08:00 | 6.72 | 6.71
2019-11-29 08:30 | 5.94 | 5.93
2019-11-29 09:00 | 5.48 | 5.46
2019-11-29 09:30 | 6.44 | 6.42
2019-11-29 10:00 | 6.97 | 6.95
2019-11-29 10:30 | 5.78 | 5.76
2019-11-29 11:00 | 5.43 | 5.39
2019-11-29 11:30 | 6.05 | 6
2019-11-29 12:00 | 6.71 | 6.64
2019-11-29 12:30 | 7.69 | 7.62
2019-11-29 13:00 | 8.61 | 8.53
2019-11-29 13:30 | 9.5 | 9.42
2019-11-29 14:00 | 10.54 | 10.46
2019-11-29 14:30 | 11.51 | 11.42
2019-11-29 15:00 | 12.22 | 12.14
2019-11-29 15:30 | 13.2 | 13.13
2019-11-29 16:00 | 14.36 | 14.29
2019-11-29 16:30 | 15.13 | 15.07
2019-11-29 17:00 | 15.75 | 15.7
2019-11-29 17:30 | 15.91 | 15.86
2019-11-29 18:00 | 15.49 | 15.45
2019-11-29 18:30 | 14.9 | 14.88
2019-11-29 19:00 | 15.17 | 15.14
2019-11-29 19:30 | 14.78 | 14.76
2019-11-29 20:00 | 14.59 | 14.58
2019-11-29 20:30 | 14.09 | 14.08
2019-11-29 21:00 | 13.13 | 13.12
2019-11-29 21:30 | 12.21 | 12.21
2019-11-29 22:00 | 11.28 | 11.27
2019-11-29 22:30 | 10.69 | 10.68
2019-11-29 23:00 | 10.29 | 10.29
2019-11-29 23:30 | 9.07 | 9.06
2019-11-30 | 8.08 | 8.07
2019-11-30 00:30 | 7.47 | 7.45
2019-11-30 01:00 | 7.15 | 7.13
2019-11-30 01:30 | 6.77 | 6.74
2019-11-30 02:00 | 6.4 | 6.36
2019-11-30 02:30 | 6.19 | 6.15
2019-11-30 03:00 | 6.06 | 6.02
2019-11-30 03:30 | 6.01 | 5.97
2019-11-30 04:00 | 5.93 | 5.89
2019-11-30 04:30 | 5.78 | 5.73
2019-11-30 05:00 | 5.52 | 5.41
2019-11-30 05:30 | 5.42 | 5.29
2019-11-30 06:00 | 5.24 | 5.11
2019-11-30 06:30 | 5.12 | 5.02
2019-11-30 07:00 | 4.96 | 4.87
2019-11-30 07:30 | 5.04 | 4.99
2019-11-30 08:00 | 4.97 | 4.94
2019-11-30 08:30 | 5.37 | 5.35
2019-11-30 09:00 | 5.64 | 5.61
2019-11-30 09:30 | 6.11 | 6.08
2019-11-30 10:00 | 6.79 | 6.75
2019-11-30 10:30 | 7.48 | 7.44
2019-11-30 11:00 | 8.48 | 8.43
2019-11-30 11:30 | 9.79 | 9.7
2019-11-30 12:00 | 11.19 | 11.08
2019-11-30 12:30 | 12.35 | 12.24
2019-11-30 13:00 | 14.07 | 13.96
2019-11-30 13:30 | 13.83 | 13.7
2019-11-30 14:00 | 14.58 | 14.45
2019-11-30 14:30 | 15.06 | 14.93
2019-11-30 15:00 | 15.83 | 15.71
2019-11-30 15:30 | 16.5 | 16.39
2019-11-30 16:00 | 17.17 | 17.07
2019-11-30 16:30 | 18.64 | 18.55
2019-11-30 17:00 | 17.72 | 17.65
2019-11-30 17:30 | 16.88 | 16.83
2019-11-30 18:00 | 16.19 | 16.15
2019-11-30 18:30 | 15.96 | 15.93
2019-11-30 19:00 | 16.18 | 16.13
2019-11-30 19:30 | 15.79 | 15.75
2019-11-30 20:00 | 15.45 | 15.42
2019-11-30 20:30 | 14.83 | 14.8
2019-11-30 21:00 | 13.92 | 13.9
2019-11-30 21:30 | 12.9 | 12.89
2019-11-30 22:00 | 12.03 | 12.02
2019-11-30 22:30 | 11.46 | 11.46
2019-11-30 23:00 | 11.07 | 11.06
2019-11-30 23:30 | 9.88 | 9.88
2019-12-01 | 8.84 | 8.83
2019-12-01 00:30 | 8.27 | 8.26
2019-12-01 01:00 | 7.84 | 7.83
2019-12-01 01:30 | 7.32 | 7.31
2019-12-01 02:00 | 6.92 | 6.9
2019-12-01 02:30 | 6.71 | 6.69
2019-12-01 03:00 | 6.5 | 6.47
2019-12-01 03:30 | 6.42 | 6.39
2019-12-01 04:00 | 6.31 | 6.28
2019-12-01 04:30 | 6.21 | 6.17
2019-12-01 05:00 | 5.99 | 5.92
2019-12-01 05:30 | 5.91 | 5.82
2019-12-01 06:00 | 5.77 | 5.67
2019-12-01 06:30 | 5.25 | 5.17
2019-12-01 07:00 | 5.08 | 5.01
2019-12-01 07:30 | 5.27 | 5.23
2019-12-01 08:00 | 6.9 | 6.89
2019-12-01 08:30 | 5.81 | 5.79
2019-12-01 09:00 | 6.53 | 6.51
2019-12-01 09:30 | 7.35 | 7.32
2019-12-01 10:00 | 8.6 | 8.57
2019-12-01 10:30 | 9.91 | 9.85
2019-12-01 11:00 | 11.69 | 11.63
2019-12-01 11:30 | 12.24 | 12.16
2019-12-01 12:00 | 15.19 | 15.11
2019-12-01 12:30 | 13.72 | 13.6
2019-12-01 13:00 | 16.45 | 16.34
2019-12-01 13:30 | 15.81 | 15.68
2019-12-01 14:00 | 18.26 | 18.18
2019-12-01 14:30 | 10.68 | 10.61
2019-12-01 15:00 | 11.86 | 11.79
2019-12-01 15:30 | 15.01 | 14.96
2019-12-01 16:00 | 15.67 | 15.63
2019-12-01 16:30 | 16.34 | 16.31
2019-12-01 17:00 | 16.12 | 16.09
2019-12-01 17:30 | 16.13 | 16.11
2019-12-01 18:00 | 15.87 | 15.85
2019-12-01 18:30 | 15.78 | 15.76
2019-12-01 19:00 | 15.93 | 15.9
2019-12-01 19:30 | 15.52 | 15.5
2019-12-01 20:00 | 15.03 | 15.01
2019-12-01 20:30 | 14.32 | 14.31
2019-12-01 21:00 | 13.22 | 13.21
2019-12-01 21:30 | 12.21 | 12.2
2019-12-01 22:00 | 11.33 | 11.33
2019-12-01 22:30 | 10.55 | 10.55
2019-12-01 23:00 | 9.94 | 9.94
2019-12-01 23:30 | 8.79 | 8.78
2019-12-02 | 7.83 | 7.82
2019-12-02 00:30 | 7.31 | 7.29
2019-12-02 01:00 | 6.68 | 6.65
2019-12-02 01:30 | 6.38 | 6.34
2019-12-02 02:00 | 6.06 | 6.02
2019-12-02 02:30 | 5.8 | 5.75
2019-12-02 03:00 | 5.63 | 5.58
2019-12-02 03:30 | 5.65 | 5.59
2019-12-02 04:00 | 5.63 | 5.57
2019-12-02 04:30 | 5.77 | 5.72
2019-12-02 05:00 | 5.71 | 5.61
2019-12-02 05:30 | 5.66 | 5.54
2019-12-02 06:00 | 5.6 | 5.49
2019-12-02 06:30 | 5.41 | 5.32
2019-12-02 07:00 | 5.34 | 5.28
2019-12-02 07:30 | 5.28 | 5.24
2019-12-02 08:00 | 4.76 | 4.74
2019-12-02 08:30 | 4.44 | 4.42
2019-12-02 09:00 | 4.05 | 4.03
2019-12-02 09:30 | 3.56 | 3.53
2019-12-02 10:00 | 3.25 | 3.21
2019-12-02 10:30 | 3.12 | 3.07
2019-12-02 11:00 | 3.61 | 3.57
2019-12-02 11:30 | 4.51 | 4.49
2019-12-02 12:00 | 4.86 | 4.85
2019-12-02 12:30 | 4.97 | 4.95
2019-12-02 13:00 | 4.94 | 4.9
2019-12-02 13:30 | 5.54 | 5.51
2019-12-02 14:00 | 6.48 | 6.44
2019-12-02 14:30 | 7.44 | 7.4
2019-12-02 15:00 | 8.43 | 8.39
2019-12-02 15:30 | 9.9 | 9.87
2019-12-02 16:00 | 11.5 | 11.47
2019-12-02 16:30 | 13 | 12.97
2019-12-02 17:00 | 14.38 | 14.35
2019-12-02 17:30 | 15.41 | 15.38
2019-12-02 18:00 | 15.8 | 15.77
2019-12-02 18:30 | 15.84 | 15.83
2019-12-02 19:00 | 16.19 | 16.17
2019-12-02 19:30 | 16.31 | 16.28
2019-12-02 20:00 | 16.22 | 16.2
2019-12-02 20:30 | 15.49 | 15.48
2019-12-02 21:00 | 14.29 | 14.28
2019-12-02 21:30 | 12.68 | 12.68
2019-12-02 22:00 | 11.55 | 11.55
2019-12-02 22:30 | 10.46 | 10.45
2019-12-02 23:00 | 9.73 | 9.72
2019-12-02 23:30 | 8.7 | 8.69
2019-12-03 | 7.72 | 7.7
2019-12-03 00:30 | 7 | 6.98
2019-12-03 01:00 | 6.58 | 6.54
2019-12-03 01:30 | 6.16 | 6.12
2019-12-03 02:00 | 5.89 | 5.84
2019-12-03 02:30 | 5.64 | 5.58
2019-12-03 03:00 | 5.52 | 5.46
2019-12-03 03:30 | 5.52 | 5.45
2019-12-03 04:00 | 5.45 | 5.38
2019-12-03 04:30 | 5.48 | 5.4
2019-12-03 05:00 | 5.4 | 5.26
2019-12-03 05:30 | 5.53 | 5.39
2019-12-03 06:00 | 5.61 | 5.48
2019-12-03 06:30 | 5.43 | 5.33
2019-12-03 07:00 | 5.34 | 5.27
2019-12-03 07:30 | 4.85 | 4.8
2019-12-03 08:00 | 4.17 | 4.14
2019-12-03 08:30 | 3.66 | 3.64
2019-12-03 09:00 | 3.3 | 3.29
2019-12-03 09:30 | 3.26 | 3.25
2019-12-03 10:00 | 3.25 | 3.24
2019-12-03 10:30 | 3.27 | 3.24
2019-12-03 11:00 | 3.61 | 3.58
2019-12-03 11:30 | 4.14 | 4.11
2019-12-03 12:00 | 4.74 | 4.71
2019-12-03 12:30 | 5.29 | 5.25
2019-12-03 13:00 | 6.23 | 6.18
2019-12-03 13:30 | 7.11 | 7.05
2019-12-03 14:00 | 8.03 | 7.98
2019-12-03 14:30 | 8.71 | 8.66
2019-12-03 15:00 | 9.83 | 9.77
2019-12-03 15:30 | 11.38 | 11.32
2019-12-03 16:00 | 13.22 | 13.16
2019-12-03 16:30 | 14.84 | 14.78
2019-12-03 17:00 | 16.26 | 16.2
2019-12-03 17:30 | 17.09 | 17.04
2019-12-03 18:00 | 17.54 | 17.49
2019-12-03 18:30 | 17.42 | 17.38
2019-12-03 19:00 | 17.46 | 17.42
2019-12-03 19:30 | 17.12 | 17.08
2019-12-03 20:00 | 16.45 | 16.42
2019-12-03 20:30 | 15.43 | 15.42
2019-12-03 21:00 | 14.26 | 14.25
2019-12-03 21:30 | 12.99 | 12.99
2019-12-03 22:00 | 11.38 | 11.38
2019-12-03 22:30 | 10.26 | 10.26
2019-12-03 23:00 | 9.44 | 9.43
2019-12-03 23:30 | 8.16 | 8.14
2019-12-04 | 7.16 | 7.13
2019-12-04 00:30 | 6.45 | 6.4
2019-12-04 01:00 | 6.15 | 6.09
2019-12-04 01:30 | 5.83 | 5.77
2019-12-04 02:00 | 5.5 | 5.44
2019-12-04 02:30 | 5.32 | 5.24
2019-12-04 03:00 | 5.27 | 5.19
2019-12-04 03:30 | 5.24 | 5.15
2019-12-04 04:00 | 5.15 | 5.06
2019-12-04 04:30 | 5.25 | 5.15
2019-12-04 05:00 | 5.19 | 5.01
2019-12-04 05:30 | 5.38 | 5.2
2019-12-04 06:00 | 5.39 | 5.23
2019-12-04 06:30 | 5.29 | 5.18
2019-12-04 07:00 | 4.94 | 4.85
2019-12-04 07:30 | 4.49 | 4.42
2019-12-04 08:00 | 3.97 | 3.93
2019-12-04 08:30 | 3.35 | 3.32
2019-12-04 09:00 | 2.92 | 2.91
2019-12-04 09:30 | 2.87 | 2.85
2019-12-04 10:00 | 3.06 | 3.03
2019-12-04 10:30 | 3.47 | 3.44
2019-12-04 11:00 | 4.23 | 4.2
2019-12-04 11:30 | 5.13 | 5.09
2019-12-04 12:00 | 6.21 | 6.16
2019-12-04 12:30 | 7.1 | 7.04
2019-12-04 13:00 | 8.15 | 8.08
2019-12-04 13:30 | 9.07 | 9
2019-12-04 14:00 | 10 | 9.92
2019-12-04 14:30 | 10.81 | 10.73
2019-12-04 15:00 | 11.5 | 11.42
2019-12-04 15:30 | 12.61 | 12.54
2019-12-04 16:00 | 13.77 | 13.71
2019-12-04 16:30 | 14.76 | 14.69
2019-12-04 17:00 | 15.56 | 15.51
2019-12-04 17:30 | 16.07 | 16.02
2019-12-04 18:00 | 15.96 | 15.92
2019-12-04 18:30 | 15.62 | 15.6
2019-12-04 19:00 | 15.56 | 15.53
2019-12-04 19:30 | 15.28 | 15.26
2019-12-04 20:00 | 15.02 | 15.01
2019-12-04 20:30 | 14.41 | 14.4
2019-12-04 21:00 | 13.36 | 13.35
2019-12-04 21:30 | 12.31 | 12.3
2019-12-04 22:00 | 11.29 | 11.28
2019-12-04 22:30 | 10.38 | 10.38
2019-12-04 23:00 | 9.5 | 9.5
2019-12-04 23:30 | 8.33 | 8.32
2019-12-05 | 7.36 | 7.33
2019-12-05 00:30 | 6.68 | 6.64
2019-12-05 01:00 | 6.27 | 6.22
2019-12-05 01:30 | 5.96 | 5.89
2019-12-05 02:00 | 5.6 | 5.54
2019-12-05 02:30 | 5.41 | 5.33
2019-12-05 03:00 | 5.34 | 5.25
2019-12-05 03:30 | 5.3 | 5.21
2019-12-05 04:00 | 5.16 | 5.07
2019-12-05 04:30 | 5.37 | 5.28
2019-12-05 05:00 | 5.32 | 5.15
2019-12-05 05:30 | 5.44 | 5.27
2019-12-05 06:00 | 5.31 | 5.16
2019-12-05 06:30 | 5.08 | 4.95
2019-12-05 07:00 | 4.8 | 4.69
2019-12-05 07:30 | 4.27 | 4.18
2019-12-05 08:00 | 3.71 | 3.65
2019-12-05 08:30 | 3.39 | 3.35
2019-12-05 09:00 | 3.22 | 3.21
2019-12-05 09:30 | 3.8 | 3.79
2019-12-05 10:00 | 3.99 | 3.97
2019-12-05 10:30 | 4.55 | 4.53
2019-12-05 11:00 | 5.3 | 5.27
2019-12-05 11:30 | 5.81 | 5.76
2019-12-05 12:00 | 6.87 | 6.81
2019-12-05 12:30 | 8.06 | 7.99
2019-12-05 13:00 | 9.21 | 9.13
2019-12-05 13:30 | 10.3 | 10.2
2019-12-05 14:00 | 11.71 | 11.61
2019-12-05 14:30 | 12.95 | 12.85
2019-12-05 15:00 | 14.22 | 14.11
2019-12-05 15:30 | 16.07 | 15.96
2019-12-05 16:00 | 17.98 | 17.87
2019-12-05 16:30 | 19.59 | 19.47
2019-12-05 17:00 | 20.25 | 20.13
2019-12-05 17:30 | 20.62 | 20.51
2019-12-05 18:00 | 20.25 | 20.15
2019-12-05 18:30 | 19.23 | 19.17
2019-12-05 19:00 | 18.59 | 18.53
2019-12-05 19:30 | 18.06 | 17.99
2019-12-05 20:00 | 17.27 | 17.22
2019-12-05 20:30 | 16.32 | 16.28
2019-12-05 21:00 | 15.06 | 15.04
2019-12-05 21:30 | 13.89 | 13.88
2019-12-05 22:00 | 12.55 | 12.55
2019-12-05 22:30 | 11.59 | 11.59
2019-12-05 23:00 | 10.56 | 10.55
2019-12-05 23:30 | 9.26 | 9.25
2019-12-06 | 8.18 | 8.17
2019-12-06 00:30 | 7.37 | 7.35
2019-12-06 01:00 | 6.94 | 6.91
2019-12-06 01:30 | 6.5 | 6.46
2019-12-06 02:00 | 6.12 | 6.08
2019-12-06 02:30 | 5.95 | 5.9
2019-12-06 03:00 | 5.83 | 5.78
2019-12-06 03:30 | 5.64 | 5.58
2019-12-06 04:00 | 5.55 | 5.48
2019-12-06 04:30 | 5.59 | 5.52
2019-12-06 05:00 | 5.47 | 5.34
2019-12-06 05:30 | 5.78 | 5.66
2019-12-06 06:00 | 5.86 | 5.77
2019-12-06 06:30 | 5.65 | 5.56
2019-12-06 07:00 | 5.38 | 5.31
2019-12-06 07:30 | 5.03 | 4.99
2019-12-06 08:00 | 4.62 | 4.6
2019-12-06 08:30 | 4.41 | 4.4
2019-12-06 09:00 | 4.53 | 4.52
2019-12-06 09:30 | 5 | 4.98
2019-12-06 10:00 | 5.58 | 5.55
2019-12-06 10:30 | 6.53 | 6.48
2019-12-06 11:00 | 7.65 | 7.57
2019-12-06 11:30 | 8.71 | 8.62
2019-12-06 12:00 | 10.01 | 9.91
2019-12-06 12:30 | 11.2 | 11.09
2019-12-06 13:00 | 12.36 | 12.22
2019-12-06 13:30 | 13.7 | 13.55
2019-12-06 14:00 | 14.8 | 14.66
2019-12-06 14:30 | 16.2 | 16.06
2019-12-06 15:00 | 17.37 | 17.21
2019-12-06 15:30 | 18.9 | 18.73
2019-12-06 16:00 | 20.14 | 19.97
2019-12-06 16:30 | 20.79 | 20.64
2019-12-06 17:00 | 21.65 | 21.51
2019-12-06 17:30 | 22.09 | 21.95
2019-12-06 18:00 | 21.97 | 21.85
2019-12-06 18:30 | 21.42 | 21.31
2019-12-06 19:00 | 20.81 | 20.7
2019-12-06 19:30 | 20.46 | 20.34
2019-12-06 20:00 | 19.59 | 19.48
2019-12-06 20:30 | 19.63 | 19.54
2019-12-06 21:00 | 18.39 | 18.31
2019-12-06 21:30 | 17.6 | 17.53
2019-12-06 22:00 | 16.37 | 16.32
2019-12-06 22:30 | 15.67 | 15.64
2019-12-06 23:00 | 14.02 | 14
2019-12-06 23:30 | 12.32 | 12.31
2019-12-07 | 10.87 | 10.86
2019-12-07 00:30 | 9.79 | 9.78
2019-12-07 01:00 | 9.15 | 9.14
2019-12-07 01:30 | 8.47 | 8.46
2019-12-07 02:00 | 7.89 | 7.88
2019-12-07 02:30 | 7.57 | 7.56
2019-12-07 03:00 | 7.24 | 7.23
2019-12-07 03:30 | 7.04 | 7.03
2019-12-07 04:00 | 6.87 | 6.85
2019-12-07 04:30 | 6.72 | 6.7
2019-12-07 05:00 | 6.39 | 6.34
2019-12-07 05:30 | 6.18 | 6.11
2019-12-07 06:00 | 5.95 | 5.87
2019-12-07 06:30 | 5.85 | 5.79
2019-12-07 07:00 | 5.84 | 5.81
2019-12-07 07:30 | 6.06 | 6.05
2019-12-07 08:00 | 6.27 | 6.26
2019-12-07 08:30 | 6.77 | 6.76
2019-12-07 09:00 | 7.65 | 7.63
2019-12-07 09:30 | 8.69 | 8.66
2019-12-07 10:00 | 10.09 | 10.02
2019-12-07 10:30 | 11.55 | 11.45
2019-12-07 11:00 | 12.91 | 12.79
2019-12-07 11:30 | 14.32 | 14.18
2019-12-07 12:00 | 15.79 | 15.62
2019-12-07 12:30 | 16.96 | 16.78
2019-12-07 13:00 | 17.72 | 17.54
2019-12-07 13:30 | 18.85 | 18.67
2019-12-07 14:00 | 20.25 | 20.07
2019-12-07 14:30 | 20.83 | 20.65
2019-12-07 15:00 | 20.87 | 20.69
2019-12-07 15:30 | 21.6 | 21.43
2019-12-07 16:00 | 21.76 | 21.59
2019-12-07 16:30 | 21.86 | 21.71
2019-12-07 17:00 | 21.86 | 21.72
2019-12-07 17:30 | 21.11 | 20.99
2019-12-07 18:00 | 20.2 | 20.1
2019-12-07 18:30 | 19.02 | 18.94
2019-12-07 19:00 | 18.43 | 18.35
2019-12-07 19:30 | 17.87 | 17.79
2019-12-07 20:00 | 17.27 | 17.21
2019-12-07 20:30 | 16.32 | 16.28
2019-12-07 21:00 | 15.19 | 15.16
2019-12-07 21:30 | 13.97 | 13.95
2019-12-07 22:00 | 12.82 | 12.81
2019-12-07 22:30 | 12.11 | 12.1
2019-12-07 23:00 | 11.32 | 11.31
2019-12-07 23:30 | 10.03 | 10.03
2019-12-08 | 8.9 | 8.9
2019-12-08 00:30 | 8.15 | 8.14
2019-12-08 01:00 | 7.68 | 7.67
2019-12-08 01:30 | 7.21 | 7.19
2019-12-08 02:00 | 6.87 | 6.84
2019-12-08 02:30 | 6.59 | 6.56
2019-12-08 03:00 | 6.34 | 6.31
2019-12-08 03:30 | 6.24 | 6.2
2019-12-08 04:00 | 6.17 | 6.13
2019-12-08 04:30 | 6.13 | 6.09
2019-12-08 05:00 | 5.84 | 5.76
2019-12-08 05:30 | 5.67 | 5.56
2019-12-08 06:00 | 5.64 | 5.53
2019-12-08 06:30 | 5.77 | 5.68
2019-12-08 07:00 | 5.66 | 5.59
2019-12-08 07:30 | 5.7 | 5.65
2019-12-08 08:00 | 4.99 | 4.95
2019-12-08 08:30 | 5.37 | 5.35
2019-12-08 09:00 | 7.33 | 7.32
2019-12-08 09:30 | 7.59 | 7.58
2019-12-08 10:00 | 7.49 | 7.47
2019-12-08 10:30 | 7.42 | 7.39
2019-12-08 11:00 | 7.85 | 7.82
2019-12-08 11:30 | 9.57 | 9.54
2019-12-08 12:00 | 10.37 | 10.34
2019-12-08 12:30 | 10.64 | 10.6
2019-12-08 13:00 | 10.74 | 10.68
2019-12-08 13:30 | 11.47 | 11.39
2019-12-08 14:00 | 13.05 | 12.95
2019-12-08 14:30 | 13.85 | 13.75
2019-12-08 15:00 | 14.99 | 14.89
2019-12-08 15:30 | 15.82 | 15.74
2019-12-08 16:00 | 16.59 | 16.51
2019-12-08 16:30 | 17.33 | 17.25
2019-12-08 17:00 | 17.55 | 17.49
2019-12-08 17:30 | 17.42 | 17.37
2019-12-08 18:00 | 16.87 | 16.83
2019-12-08 18:30 | 16.23 | 16.21
2019-12-08 19:00 | 16.01 | 15.99
2019-12-08 19:30 | 15.53 | 15.5
2019-12-08 20:00 | 15.18 | 15.16
2019-12-08 20:30 | 14.53 | 14.51
2019-12-08 21:00 | 13.68 | 13.67
2019-12-08 21:30 | 12.64 | 12.63
2019-12-08 22:00 | 11.57 | 11.56
2019-12-08 22:30 | 10.83 | 10.82
2019-12-08 23:00 | 10.28 | 10.27
2019-12-08 23:30 | 9.13 | 9.12
2019-12-09 | 8.22 | 8.21
2019-12-09 00:30 | 7.68 | 7.67
2019-12-09 01:00 | 7.38 | 7.36
2019-12-09 01:30 | 6.95 | 6.93
2019-12-09 02:00 | 6.56 | 6.53
2019-12-09 02:30 | 6.31 | 6.28
2019-12-09 03:00 | 6.19 | 6.15
2019-12-09 03:30 | 6.08 | 6.04
2019-12-09 04:00 | 5.97 | 5.92
2019-12-09 04:30 | 5.98 | 5.93
2019-12-09 05:00 | 5.88 | 5.78
2019-12-09 05:30 | 5.92 | 5.82
2019-12-09 06:00 | 5.98 | 5.88
2019-12-09 06:30 | 6.16 | 6.1
2019-12-09 07:00 | 6.17 | 6.14
2019-12-09 07:30 | 5.91 | 5.88
2019-12-09 08:00 | 5.61 | 5.6
2019-12-09 08:30 | 5.59 | 5.59
2019-12-09 09:00 | 5.8 | 5.79
2019-12-09 09:30 | 6.74 | 6.73
2019-12-09 10:00 | 7.98 | 7.96
2019-12-09 10:30 | 8.51 | 8.48
2019-12-09 11:00 | 8.52 | 8.48
2019-12-09 11:30 | 9.35 | 9.3
2019-12-09 12:00 | 10.45 | 10.39
2019-12-09 12:30 | 12.09 | 12.03
2019-12-09 13:00 | 11.49 | 11.42
2019-12-09 13:30 | 11.77 | 11.69
2019-12-09 14:00 | 12.44 | 12.35
2019-12-09 14:30 | 13.62 | 13.53
2019-12-09 15:00 | 13.43 | 13.34
2019-12-09 15:30 | 14.7 | 14.61
2019-12-09 16:00 | 16.03 | 15.94
2019-12-09 16:30 | 17 | 16.91
2019-12-09 17:00 | 17.57 | 17.5
2019-12-09 17:30 | 18.07 | 18.01
2019-12-09 18:00 | 18.26 | 18.2
2019-12-09 18:30 | 18.27 | 18.23
2019-12-09 19:00 | 18.29 | 18.25
2019-12-09 19:30 | 18.62 | 18.55
2019-12-09 20:00 | 18.06 | 18.01
2019-12-09 20:30 | 17.31 | 17.26
2019-12-09 21:00 | 16.01 | 15.98
2019-12-09 21:30 | 14.76 | 14.74
2019-12-09 22:00 | 13.22 | 13.21
2019-12-09 22:30 | 12.03 | 12.03
2019-12-09 23:00 | 11.09 | 11.08
2019-12-09 23:30 | 9.9 | 9.9
2019-12-10 | 8.77 | 8.76
2019-12-10 00:30 | 8.05 | 8.05
2019-12-10 01:00 | 7.67 | 7.66
2019-12-10 01:30 | 7.25 | 7.23
2019-12-10 02:00 | 6.95 | 6.93
2019-12-10 02:30 | 6.65 | 6.63
2019-12-10 03:00 | 6.57 | 6.54
2019-12-10 03:30 | 6.46 | 6.44
2019-12-10 04:00 | 6.39 | 6.36
2019-12-10 04:30 | 6.42 | 6.39
2019-12-10 05:00 | 6.28 | 6.21
2019-12-10 05:30 | 6.37 | 6.29
2019-12-10 06:00 | 6.67 | 6.61
2019-12-10 06:30 | 6.83 | 6.79
2019-12-10 07:00 | 6.87 | 6.86
2019-12-10 07:30 | 6.87 | 6.87
2019-12-10 08:00 | 6.63 | 6.63
2019-12-10 08:30 | 7.96 | 7.96
2019-12-10 09:00 | 7.96 | 7.95
2019-12-10 09:30 | 7.38 | 7.37
2019-12-10 10:00 | 7.81 | 7.78
2019-12-10 10:30 | 7.47 | 7.41
2019-12-10 11:00 | 8.03 | 7.95
2019-12-10 11:30 | 9 | 8.91
2019-12-10 12:00 | 10.12 | 10.01
2019-12-10 12:30 | 11.24 | 11.12
2019-12-10 13:00 | 12.42 | 12.29
2019-12-10 13:30 | 13.44 | 13.3
2019-12-10 14:00 | 14.61 | 14.47
2019-12-10 14:30 | 15.7 | 15.55
2019-12-10 15:00 | 16.69 | 16.52
2019-12-10 15:30 | 17.92 | 17.76
2019-12-10 16:00 | 19.15 | 19.01
2019-12-10 16:30 | 20.3 | 20.16
2019-12-10 17:00 | 20.84 | 20.7
2019-12-10 17:30 | 21.1 | 20.97
2019-12-10 18:00 | 21.24 | 21.12
2019-12-10 18:30 | 20.79 | 20.7
2019-12-10 19:00 | 21.67 | 21.6
2019-12-10 19:30 | 20.95 | 20.87
2019-12-10 20:00 | 20.46 | 20.39
2019-12-10 20:30 | 19.62 | 19.57
2019-12-10 21:00 | 18.2 | 18.16
2019-12-10 21:30 | 15.74 | 15.7
2019-12-10 22:00 | 14.26 | 14.24
2019-12-10 22:30 | 13.07 | 13.06
2019-12-10 23:00 | 12.02 | 12.02
2019-12-10 23:30 | 10.71 | 10.7
2019-12-11 | 9.61 | 9.6
2019-12-11 00:30 | 8.87 | 8.86
2019-12-11 01:00 | 8.39 | 8.39
2019-12-11 01:30 | 8.14 | 8.14
2019-12-11 02:00 | 7.72 | 7.71
2019-12-11 02:30 | 7.31 | 7.31
2019-12-11 03:00 | 7.12 | 7.11
2019-12-11 03:30 | 7 | 6.99
2019-12-11 04:00 | 6.88 | 6.87
2019-12-11 04:30 | 6.91 | 6.9
2019-12-11 05:00 | 6.69 | 6.64
2019-12-11 05:30 | 6.67 | 6.62
2019-12-11 06:00 | 6.88 | 6.83
2019-12-11 06:30 | 7.15 | 7.13
2019-12-11 07:00 | 7.1 | 7.08
2019-12-11 07:30 | 7.39 | 7.38
2019-12-11 08:00 | 7.57 | 7.57
2019-12-11 08:30 | 7.48 | 7.47
2019-12-11 09:00 | 7.75 | 7.72
2019-12-11 09:30 | 8.23 | 8.18
2019-12-11 10:00 | 9.03 | 8.95
2019-12-11 10:30 | 9.87 | 9.76
2019-12-11 11:00 | 10.85 | 10.73
2019-12-11 11:30 | 11.8 | 11.65
2019-12-11 12:00 | 12.98 | 12.83
2019-12-11 12:30 | 14.34 | 14.17
2019-12-11 13:00 | 15.47 | 15.3
2019-12-11 13:30 | 16.71 | 16.54
2019-12-11 14:00 | 18.12 | 17.94
2019-12-11 14:30 | 17.7 | 17.52
2019-12-11 15:00 | 18.05 | 17.88
2019-12-11 15:30 | 19.88 | 19.73
2019-12-11 16:00 | 21.77 | 21.64
2019-12-11 16:30 | 21.1 | 20.98
2019-12-11 17:00 | 20.23 | 20.13
2019-12-11 17:30 | 19.61 | 19.53
2019-12-11 18:00 | 19.22 | 19.15
2019-12-11 18:30 | 18.79 | 18.73
2019-12-11 19:00 | 18.94 | 18.87
2019-12-11 19:30 | 19.02 | 18.94
2019-12-11 20:00 | 18.79 | 18.72
2019-12-11 20:30 | 18.22 | 18.15
2019-12-11 21:00 | 17.05 | 16.99
2019-12-11 21:30 | 15.74 | 15.71
2019-12-11 22:00 | 13.88 | 13.87
2019-12-11 22:30 | 11.61 | 11.61
2019-12-11 23:00 | 10.13 | 10.13
2019-12-11 23:30 | 9.03 | 9.03
2019-12-12 | 7.94 | 7.93
2019-12-12 00:30 | 7.23 | 7.21
2019-12-12 01:00 | 6.96 | 6.93
2019-12-12 01:30 | 6.58 | 6.55
2019-12-12 02:00 | 6.35 | 6.31
2019-12-12 02:30 | 6.17 | 6.14
2019-12-12 03:00 | 6.07 | 6.03
2019-12-12 03:30 | 5.93 | 5.88
2019-12-12 04:00 | 5.85 | 5.8
2019-12-12 04:30 | 5.9 | 5.84
2019-12-12 05:00 | 5.88 | 5.8
2019-12-12 05:30 | 5.77 | 5.65
2019-12-12 06:00 | 5.76 | 5.65
2019-12-12 06:30 | 5.71 | 5.62
2019-12-12 07:00 | 5.44 | 5.37
2019-12-12 07:30 | 5.39 | 5.36
2019-12-12 08:00 | 5.02 | 5
2019-12-12 08:30 | 4.67 | 4.66
2019-12-12 09:00 | 4.67 | 4.65
2019-12-12 09:30 | 5.09 | 5.06
2019-12-12 10:00 | 5.44 | 5.41
2019-12-12 10:30 | 6 | 5.96
2019-12-12 11:00 | 6.88 | 6.82
2019-12-12 11:30 | 7.71 | 7.64
2019-12-12 12:00 | 8.78 | 8.68
2019-12-12 12:30 | 9.8 | 9.7
2019-12-12 13:00 | 10.69 | 10.58
2019-12-12 13:30 | 11.57 | 11.44
2019-12-12 14:00 | 12.76 | 12.63
2019-12-12 14:30 | 13.73 | 13.58
2019-12-12 15:00 | 14.65 | 14.52
2019-12-12 15:30 | 16 | 15.86
2019-12-12 16:00 | 17.09 | 16.96
2019-12-12 16:30 | 18.69 | 18.58
2019-12-12 17:00 | 17.71 | 17.6
2019-12-12 17:30 | 18.04 | 17.94
2019-12-12 18:00 | 18.25 | 18.17
2019-12-12 18:30 | 18.68 | 18.61
2019-12-12 19:00 | 18.75 | 18.68
2019-12-12 19:30 | 18.61 | 18.53
2019-12-12 20:00 | 18.27 | 18.2
2019-12-12 20:30 | 17.63 | 17.57
2019-12-12 21:00 | 16.53 | 16.49
2019-12-12 21:30 | 15.24 | 15.21
2019-12-12 22:00 | 13.96 | 13.94
2019-12-12 22:30 | 13.01 | 13.01
2019-12-12 23:00 | 11.9 | 11.9
2019-12-12 23:30 | 10.57 | 10.56
2019-12-13 | 9.42 | 9.42
2019-12-13 00:30 | 8.7 | 8.69
2019-12-13 01:00 | 8.37 | 8.37
2019-12-13 01:30 | 7.83 | 7.83
2019-12-13 02:00 | 7.45 | 7.44
2019-12-13 02:30 | 7.22 | 7.21
2019-12-13 03:00 | 6.97 | 6.96
2019-12-13 03:30 | 6.9 | 6.88
2019-12-13 04:00 | 6.82 | 6.8
2019-12-13 04:30 | 6.77 | 6.76
2019-12-13 05:00 | 6.64 | 6.6
2019-12-13 05:30 | 6.77 | 6.72
2019-12-13 06:00 | 6.97 | 6.94
2019-12-13 06:30 | 7.38 | 7.36
2019-12-13 07:00 | 7.29 | 7.28
2019-12-13 07:30 | 6.72 | 6.72
2019-12-13 08:00 | 6.91 | 6.91
2019-12-13 08:30 | 7.59 | 7.58
2019-12-13 09:00 | 10.82 | 10.82
2019-12-13 09:30 | 11.08 | 11.08
2019-12-13 10:00 | 9.47 | 9.46
2019-12-13 10:30 | 8.23 | 8.21
2019-12-13 11:00 | 6.81 | 6.76
2019-12-13 11:30 | 9.29 | 9.25
2019-12-13 12:00 | 9.87 | 9.84
2019-12-13 12:30 | 10.65 | 10.62
2019-12-13 13:00 | 12.29 | 12.25
2019-12-13 13:30 | 12.44 | 12.41
2019-12-13 14:00 | 8.47 | 8.39
2019-12-13 14:30 | 10.05 | 9.97
2019-12-13 15:00 | 11.9 | 11.82
2019-12-13 15:30 | 15.49 | 15.43
2019-12-13 16:00 | 12.46 | 12.42
2019-12-13 16:30 | 11.03 | 11
2019-12-13 17:00 | 11.86 | 11.83
2019-12-13 17:30 | 12.84 | 12.82
2019-12-13 18:00 | 13.24 | 13.22
2019-12-13 18:30 | 13.23 | 13.21
2019-12-13 19:00 | 13.51 | 13.49
2019-12-13 19:30 | 13.66 | 13.64
2019-12-13 20:00 | 13.58 | 13.57
2019-12-13 20:30 | 13.15 | 13.14
2019-12-13 21:00 | 12.4 | 12.39
2019-12-13 21:30 | 11.76 | 11.75
2019-12-13 22:00 | 10.94 | 10.93
2019-12-13 22:30 | 10.43 | 10.42
2019-12-13 23:00 | 10 | 10
2019-12-13 23:30 | 8.97 | 8.96
2019-12-14 | 8.17 | 8.15
2019-12-14 00:30 | 7.45 | 7.43
2019-12-14 01:00 | 7.05 | 7.03
2019-12-14 01:30 | 6.69 | 6.66
2019-12-14 02:00 | 6.37 | 6.33
2019-12-14 02:30 | 6.09 | 6.05
2019-12-14 03:00 | 5.97 | 5.92
2019-12-14 03:30 | 5.93 | 5.88
2019-12-14 04:00 | 5.8 | 5.75
2019-12-14 04:30 | 5.74 | 5.68
2019-12-14 05:00 | 5.67 | 5.6
2019-12-14 05:30 | 5.63 | 5.51
2019-12-14 06:00 | 5.67 | 5.55
2019-12-14 06:30 | 5.81 | 5.72
2019-12-14 07:00 | 6.27 | 6.19
2019-12-14 07:30 | 6.54 | 6.47
2019-12-14 08:00 | 6.16 | 6.11
2019-12-14 08:30 | 5.1 | 5.06
2019-12-14 09:00 | 5.11 | 5.09
2019-12-14 09:30 | 6.87 | 6.85
2019-12-14 10:00 | 5.77 | 5.74
2019-12-14 10:30 | 5.52 | 5.49
2019-12-14 11:00 | 5.79 | 5.75
2019-12-14 11:30 | 7.21 | 7.17
2019-12-14 12:00 | 8.56 | 8.51
2019-12-14 12:30 | 9.22 | 9.14
2019-12-14 13:00 | 10.56 | 10.47
2019-12-14 13:30 | 11.81 | 11.71
2019-12-14 14:00 | 12.87 | 12.75
2019-12-14 14:30 | 14.02 | 13.9
2019-12-14 15:00 | 15.03 | 14.92
2019-12-14 15:30 | 16.18 | 16.06
2019-12-14 16:00 | 16.98 | 16.87
2019-12-14 16:30 | 17.53 | 17.44
2019-12-14 17:00 | 17.9 | 17.82
2019-12-14 17:30 | 17.87 | 17.8
2019-12-14 18:00 | 17.53 | 17.47
2019-12-14 18:30 | 17.02 | 16.97
2019-12-14 19:00 | 16.63 | 16.58
2019-12-14 19:30 | 16.33 | 16.28
2019-12-14 20:00 | 16.05 | 16
2019-12-14 20:30 | 15.22 | 15.19
2019-12-14 21:00 | 14.34 | 14.31
2019-12-14 21:30 | 13.71 | 13.69
2019-12-14 22:00 | 12.87 | 12.86
2019-12-14 22:30 | 12.33 | 12.32
2019-12-14 23:00 | 11.83 | 11.82
2019-12-14 23:30 | 10.73 | 10.72
2019-12-15 | 9.71 | 9.7
2019-12-15 00:30 | 8.85 | 8.85
2019-12-15 01:00 | 8.43 | 8.42
2019-12-15 01:30 | 7.88 | 7.87
2019-12-15 02:00 | 7.52 | 7.51
2019-12-15 02:30 | 7.18 | 7.17
2019-12-15 03:00 | 6.99 | 6.98
2019-12-15 03:30 | 6.85 | 6.83
2019-12-15 04:00 | 6.68 | 6.66
2019-12-15 04:30 | 6.61 | 6.59
2019-12-15 05:00 | 6.28 | 6.23
2019-12-15 05:30 | 6.15 | 6.07
2019-12-15 06:00 | 5.89 | 5.81
2019-12-15 06:30 | 5.76 | 5.7
2019-12-15 07:00 | 5.7 | 5.67
2019-12-15 07:30 | 5.96 | 5.95
2019-12-15 08:00 | 6.26 | 6.25
2019-12-15 08:30 | 7.13 | 7.11
2019-12-15 09:00 | 7.94 | 7.92
2019-12-15 09:30 | 8.51 | 8.48
2019-12-15 10:00 | 9.6 | 9.55
2019-12-15 10:30 | 10.09 | 10.02
2019-12-15 11:00 | 11.13 | 11.04
2019-12-15 11:30 | 12.35 | 12.23
2019-12-15 12:00 | 13.76 | 13.62
2019-12-15 12:30 | 14.75 | 14.59
2019-12-15 13:00 | 15.44 | 15.28
2019-12-15 13:30 | 16.47 | 16.29
2019-12-15 14:00 | 17.33 | 17.14
2019-12-15 14:30 | 17.84 | 17.65
2019-12-15 15:00 | 19.43 | 19.27
2019-12-15 15:30 | 18.87 | 18.7
2019-12-15 16:00 | 20.25 | 20.08
2019-12-15 16:30 | 21.62 | 21.47
2019-12-15 17:00 | 21.14 | 21
2019-12-15 17:30 | 20.96 | 20.85
2019-12-15 18:00 | 20.48 | 20.39
2019-12-15 18:30 | 19.7 | 19.63
2019-12-15 19:00 | 19.07 | 19
2019-12-15 19:30 | 18.62 | 18.55
2019-12-15 20:00 | 18.07 | 18
2019-12-15 20:30 | 17.08 | 17.03
2019-12-15 21:00 | 15.99 | 15.95
2019-12-15 21:30 | 15.05 | 15.02
2019-12-15 22:00 | 13.79 | 13.77
2019-12-15 22:30 | 12.74 | 12.73
2019-12-15 23:00 | 11.92 | 11.91
2019-12-15 23:30 | 10.62 | 10.61
2019-12-16 | 9.47 | 9.46
2019-12-16 00:30 | 8.65 | 8.64
2019-12-16 01:00 | 8.18 | 8.18
2019-12-16 01:30 | 7.67 | 7.67
2019-12-16 02:00 | 7.26 | 7.25
2019-12-16 02:30 | 6.94 | 6.93
2019-12-16 03:00 | 6.82 | 6.81
2019-12-16 03:30 | 6.63 | 6.61
2019-12-16 04:00 | 6.5 | 6.48
2019-12-16 04:30 | 6.53 | 6.51
2019-12-16 05:00 | 6.43 | 6.38
2019-12-16 05:30 | 6.55 | 6.49
2019-12-16 06:00 | 6.69 | 6.64
2019-12-16 06:30 | 6.8 | 6.78
2019-12-16 07:00 | 6.81 | 6.8
2019-12-16 07:30 | 6.49 | 6.48
2019-12-16 08:00 | 6.54 | 6.53
2019-12-16 08:30 | 7.12 | 7.11
2019-12-16 09:00 | 7.95 | 7.91
2019-12-16 09:30 | 8.92 | 8.85
2019-12-16 10:00 | 9.91 | 9.8
2019-12-16 10:30 | 11.12 | 10.99
2019-12-16 11:00 | 12.18 | 12.04
2019-12-16 11:30 | 13.24 | 13.09
2019-12-16 12:00 | 14.49 | 14.33
2019-12-16 12:30 | 15.7 | 15.48
2019-12-16 13:00 | 16.65 | 16.44
2019-12-16 13:30 | 17.6 | 17.42
2019-12-16 14:00 | 18.53 | 18.35
2019-12-16 14:30 | 20.36 | 20.17
2019-12-16 15:00 | 21.54 | 21.32
2019-12-16 15:30 | 21.22 | 21.01
2019-12-16 16:00 | 20.82 | 20.64
2019-12-16 16:30 | 21.22 | 21.05
2019-12-16 17:00 | 21.55 | 21.39
2019-12-16 17:30 | 21.65 | 21.51
2019-12-16 18:00 | 21.21 | 21.08
2019-12-16 18:30 | 20.48 | 20.39
2019-12-16 19:00 | 19.88 | 19.8
2019-12-16 19:30 | 19.38 | 19.29
2019-12-16 20:00 | 18.4 | 18.32
2019-12-16 20:30 | 17.89 | 17.84
2019-12-16 21:00 | 16.66 | 16.62
2019-12-16 21:30 | 14.98 | 14.96
2019-12-16 22:00 | 13.37 | 13.36
2019-12-16 22:30 | 11.53 | 11.52
2019-12-16 23:00 | 10.77 | 10.77
2019-12-16 23:30 | 9.7 | 9.69
2019-12-17 | 8.48 | 8.48
2019-12-17 00:30 | 7.72 | 7.71
2019-12-17 01:00 | 7.38 | 7.37
2019-12-17 01:30 | 6.96 | 6.94
2019-12-17 02:00 | 6.68 | 6.65
2019-12-17 02:30 | 6.7 | 6.67
2019-12-17 03:00 | 6.81 | 6.78
2019-12-17 03:30 | 6.41 | 6.38
2019-12-17 04:00 | 6.15 | 6.12
2019-12-17 04:30 | 6.12 | 6.08
2019-12-17 05:00 | 5.94 | 5.86
2019-12-17 05:30 | 6.02 | 5.92
2019-12-17 06:00 | 5.84 | 5.74
2019-12-17 06:30 | 5.89 | 5.82
2019-12-17 07:00 | 5.77 | 5.72
2019-12-17 07:30 | 5.23 | 5.2
2019-12-17 08:00 | 4.66 | 4.64
2019-12-17 08:30 | 4.72 | 4.7
2019-12-17 09:00 | 4.43 | 4.41
2019-12-17 09:30 | 4.09 | 4.07
2019-12-17 10:00 | 4.03 | 4
2019-12-17 10:30 | 4.09 | 4.05
2019-12-17 11:00 | 4.69 | 4.65
2019-12-17 11:30 | 5.23 | 5.19
2019-12-17 12:00 | 5.81 | 5.76
2019-12-17 12:30 | 6.71 | 6.66
2019-12-17 13:00 | 7.26 | 7.2
2019-12-17 13:30 | 7.69 | 7.62
2019-12-17 14:00 | 8.54 | 8.47
2019-12-17 14:30 | 9.17 | 9.1
2019-12-17 15:00 | 9.94 | 9.88
2019-12-17 15:30 | 10.85 | 10.79
2019-12-17 16:00 | 11.8 | 11.74
2019-12-17 16:30 | 12.52 | 12.48
2019-12-17 17:00 | 13.5 | 13.47
2019-12-17 17:30 | 14.47 | 14.44
2019-12-17 18:00 | 14.7 | 14.69
2019-12-17 18:30 | 14.33 | 14.32
2019-12-17 19:00 | 14.41 | 14.41
2019-12-17 19:30 | 14.56 | 14.54
2019-12-17 20:00 | 14.27 | 14.26
2019-12-17 20:30 | 13.57 | 13.57
2019-12-17 21:00 | 12.88 | 12.88
2019-12-17 21:30 | 11.84 | 11.83
2019-12-17 22:00 | 10.91 | 10.91
2019-12-17 22:30 | 10.08 | 10.08
2019-12-17 23:00 | 9.28 | 9.27
2019-12-17 23:30 | 8.17 | 8.15
2019-12-18 | 7.22 | 7.19
2019-12-18 00:30 | 6.49 | 6.45
2019-12-18 01:00 | 6.19 | 6.15
2019-12-18 01:30 | 5.95 | 5.9
2019-12-18 02:00 | 5.71 | 5.65
2019-12-18 02:30 | 5.48 | 5.41
2019-12-18 03:00 | 5.43 | 5.36
2019-12-18 03:30 | 5.38 | 5.31
2019-12-18 04:00 | 5.41 | 5.33
2019-12-18 04:30 | 5.46 | 5.39
2019-12-18 05:00 | 5.39 | 5.26
2019-12-18 05:30 | 5.5 | 5.35
2019-12-18 06:00 | 5.54 | 5.41
2019-12-18 06:30 | 5.41 | 5.31
2019-12-18 07:00 | 5.27 | 5.19
2019-12-18 07:30 | 4.76 | 4.68
2019-12-18 08:00 | 4.13 | 4.08
2019-12-18 08:30 | 4.36 | 4.34
2019-12-18 09:00 | 3.82 | 3.8
2019-12-18 09:30 | 3.14 | 3.13
2019-12-18 10:00 | 2.86 | 2.83
2019-12-18 10:30 | 2.88 | 2.85
2019-12-18 11:00 | 3.14 | 3.11
2019-12-18 11:30 | 3.48 | 3.45
2019-12-18 12:00 | 3.84 | 3.81
2019-12-18 12:30 | 4.28 | 4.25
2019-12-18 13:00 | 4.67 | 4.63
2019-12-18 13:30 | 5.44 | 5.4
2019-12-18 14:00 | 6.27 | 6.24
2019-12-18 14:30 | 6.94 | 6.91
2019-12-18 15:00 | 7.92 | 7.9
2019-12-18 15:30 | 8.81 | 8.78
2019-12-18 16:00 | 9.91 | 9.89
2019-12-18 16:30 | 11.02 | 11
2019-12-18 17:00 | 11.87 | 11.86
2019-12-18 17:30 | 12.55 | 12.54
2019-12-18 18:00 | 12.77 | 12.77
2019-12-18 18:30 | 12.8 | 12.8
2019-12-18 19:00 | 13.13 | 13.12
2019-12-18 19:30 | 13.37 | 13.37
2019-12-18 20:00 | 13.19 | 13.19
2019-12-18 20:30 | 12.63 | 12.62
2019-12-18 21:00 | 11.85 | 11.85
2019-12-18 21:30 | 11.06 | 11.06
2019-12-18 22:00 | 10.2 | 10.2
2019-12-18 22:30 | 9.33 | 9.32
2019-12-18 23:00 | 8.89 | 8.87
2019-12-18 23:30 | 7.82 | 7.79
2019-12-19 | 6.96 | 6.92
2019-12-19 00:30 | 6.27 | 6.22
2019-12-19 01:00 | 6.09 | 6.03
2019-12-19 01:30 | 5.74 | 5.67
2019-12-19 02:00 | 5.46 | 5.38
2019-12-19 02:30 | 5.27 | 5.18
2019-12-19 03:00 | 5.22 | 5.13
2019-12-19 03:30 | 5.2 | 5.11
2019-12-19 04:00 | 5.1 | 5
2019-12-19 04:30 | 5.24 | 5.14
2019-12-19 05:00 | 5.15 | 4.99
2019-12-19 05:30 | 5.3 | 5.12
2019-12-19 06:00 | 5.3 | 5.13
2019-12-19 06:30 | 5.21 | 5.07
2019-12-19 07:00 | 4.9 | 4.78
2019-12-19 07:30 | 4.38 | 4.28
2019-12-19 08:00 | 3.87 | 3.8
2019-12-19 08:30 | 3.38 | 3.34
2019-12-19 09:00 | 3.04 | 3.02
2019-12-19 09:30 | 2.93 | 2.91
2019-12-19 10:00 | 3.07 | 3.05
2019-12-19 10:30 | 3.32 | 3.3
2019-12-19 11:00 | 3.45 | 3.42
2019-12-19 11:30 | 3.8 | 3.77
2019-12-19 12:00 | 4.37 | 4.34
2019-12-19 12:30 | 5.11 | 5.08
2019-12-19 13:00 | 5.71 | 5.67
2019-12-19 13:30 | 6.71 | 6.66
2019-12-19 14:00 | 7.82 | 7.77
2019-12-19 14:30 | 8.69 | 8.64
2019-12-19 15:00 | 9.7 | 9.65
2019-12-19 15:30 | 10.69 | 10.64
2019-12-19 16:00 | 11.85 | 11.81
2019-12-19 16:30 | 12.96 | 12.92
2019-12-19 17:00 | 13.93 | 13.9
2019-12-19 17:30 | 14.32 | 14.3
2019-12-19 18:00 | 14.55 | 14.52
2019-12-19 18:30 | 14.52 | 14.5
2019-12-19 19:00 | 14.47 | 14.46
2019-12-19 19:30 | 14.69 | 14.67
2019-12-19 20:00 | 14.32 | 14.31
2019-12-19 20:30 | 13.84 | 13.83
2019-12-19 21:00 | 12.98 | 12.97
2019-12-19 21:30 | 12.11 | 12.1
2019-12-19 22:00 | 11.25 | 11.24
2019-12-19 22:30 | 10.5 | 10.49
2019-12-19 23:00 | 9.78 | 9.77
2019-12-19 23:30 | 8.62 | 8.61
2019-12-20 | 7.71 | 7.69
2019-12-20 00:30 | 7.06 | 7.03
2019-12-20 01:00 | 6.67 | 6.64
2019-12-20 01:30 | 6.36 | 6.32
2019-12-20 02:00 | 6.03 | 5.98
2019-12-20 02:30 | 5.75 | 5.69
2019-12-20 03:00 | 5.55 | 5.48
2019-12-20 03:30 | 5.54 | 5.48
2019-12-20 04:00 | 5.49 | 5.42
2019-12-20 04:30 | 5.52 | 5.45
2019-12-20 05:00 | 5.46 | 5.34
2019-12-20 05:30 | 5.5 | 5.36
2019-12-20 06:00 | 5.29 | 5.15
2019-12-20 06:30 | 5.09 | 4.95
2019-12-20 07:00 | 4.71 | 4.6
2019-12-20 07:30 | 4.4 | 4.31
2019-12-20 08:00 | 4.14 | 4.07
2019-12-20 08:30 | 3.98 | 3.93
2019-12-20 09:00 | 3.81 | 3.79
2019-12-20 09:30 | 3.81 | 3.78
2019-12-20 10:00 | 3.98 | 3.95
2019-12-20 10:30 | 4.5 | 4.47
2019-12-20 11:00 | 4.99 | 4.95
2019-12-20 11:30 | 5.73 | 5.69
2019-12-20 12:00 | 6.82 | 6.78
2019-12-20 12:30 | 8.18 | 8.14
2019-12-20 13:00 | 9.27 | 9.22
2019-12-20 13:30 | 10.58 | 10.52
2019-12-20 14:00 | 11.74 | 11.68
2019-12-20 14:30 | 12.46 | 12.39
2019-12-20 15:00 | 12.76 | 12.69
2019-12-20 15:30 | 12.99 | 12.94
2019-12-20 16:00 | 14.52 | 14.48
2019-12-20 16:30 | 15.07 | 15.04
2019-12-20 17:00 | 15.48 | 15.46
2019-12-20 17:30 | 15.14 | 15.11
2019-12-20 18:00 | 14.41 | 14.39
2019-12-20 18:30 | 14.2 | 14.19
2019-12-20 19:00 | 14.2 | 14.19
2019-12-20 19:30 | 14.28 | 14.26
2019-12-20 20:00 | 14.05 | 14.03
2019-12-20 20:30 | 13.53 | 13.52
2019-12-20 21:00 | 12.79 | 12.78
2019-12-20 21:30 | 12.02 | 12.01
2019-12-20 22:00 | 11.25 | 11.25
2019-12-20 22:30 | 10.62 | 10.62
2019-12-20 23:00 | 10.26 | 10.26
2019-12-20 23:30 | 9.22 | 9.21
2019-12-21 | 8.24 | 8.23
2019-12-21 00:30 | 7.62 | 7.6
2019-12-21 01:00 | 7.27 | 7.25
2019-12-21 01:30 | 6.81 | 6.78
2019-12-21 02:00 | 6.52 | 6.49
2019-12-21 02:30 | 6.29 | 6.25
2019-12-21 03:00 | 6.06 | 6.02
2019-12-21 03:30 | 5.93 | 5.88
2019-12-21 04:00 | 5.85 | 5.8
2019-12-21 04:30 | 5.92 | 5.87
2019-12-21 05:00 | 6.11 | 6.04
2019-12-21 05:30 | 6.07 | 5.97
2019-12-21 06:00 | 5.85 | 5.74
2019-12-21 06:30 | 5.64 | 5.55
2019-12-21 07:00 | 5.4 | 5.32
2019-12-21 07:30 | 5.32 | 5.27
2019-12-21 08:00 | 5.37 | 5.34
2019-12-21 08:30 | 5.63 | 5.62
2019-12-21 09:00 | 5.35 | 5.34
2019-12-21 09:30 | 5.59 | 5.58
2019-12-21 10:00 | 5.92 | 5.9
2019-12-21 10:30 | 6.55 | 6.51
2019-12-21 11:00 | 7.24 | 7.19
2019-12-21 11:30 | 7.81 | 7.75
2019-12-21 12:00 | 8.74 | 8.68
2019-12-21 12:30 | 9.75 | 9.67
2019-12-21 13:00 | 10.84 | 10.75
2019-12-21 13:30 | 11.95 | 11.85
2019-12-21 14:00 | 13.24 | 13.13
2019-12-21 14:30 | 14.14 | 14.03
2019-12-21 15:00 | 15.07 | 14.97
2019-12-21 15:30 | 16.01 | 15.91
2019-12-21 16:00 | 16.57 | 16.48
2019-12-21 16:30 | 17.15 | 17.07
2019-12-21 17:00 | 17.17 | 17.11
2019-12-21 17:30 | 17.08 | 17.02
2019-12-21 18:00 | 16.54 | 16.49
2019-12-21 18:30 | 15.93 | 15.89
2019-12-21 19:00 | 15.48 | 15.46
2019-12-21 19:30 | 15.19 | 15.16
2019-12-21 20:00 | 14.97 | 14.95
2019-12-21 20:30 | 14.18 | 14.16
2019-12-21 21:00 | 13.36 | 13.35
2019-12-21 21:30 | 12.68 | 12.67
2019-12-21 22:00 | 11.99 | 11.98
2019-12-21 22:30 | 11.34 | 11.34
2019-12-21 23:00 | 10.88 | 10.87
2019-12-21 23:30 | 9.75 | 9.74
2019-12-22 | 8.77 | 8.76
2019-12-22 00:30 | 8.04 | 8.03
2019-12-22 01:00 | 7.63 | 7.62
2019-12-22 01:30 | 7.1 | 7.08
2019-12-22 02:00 | 6.75 | 6.73
2019-12-22 02:30 | 6.35 | 6.31
2019-12-22 03:00 | 6.2 | 6.17
2019-12-22 03:30 | 6.07 | 6.03
2019-12-22 04:00 | 5.95 | 5.91
2019-12-22 04:30 | 5.88 | 5.83
2019-12-22 05:00 | 5.63 | 5.54
2019-12-22 05:30 | 5.55 | 5.43
2019-12-22 06:00 | 5.37 | 5.24
2019-12-22 06:30 | 5.13 | 4.99
2019-12-22 07:00 | 4.97 | 4.87
2019-12-22 07:30 | 4.98 | 4.91
2019-12-22 08:00 | 5.02 | 4.97
2019-12-22 08:30 | 5.5 | 5.48
2019-12-22 09:00 | 6.48 | 6.46
2019-12-22 09:30 | 6.33 | 6.32
2019-12-22 10:00 | 6.79 | 6.77
2019-12-22 10:30 | 7.4 | 7.38
2019-12-22 11:00 | 8.17 | 8.15
2019-12-22 11:30 | 8.38 | 8.36
2019-12-22 12:00 | 9.17 | 9.14
2019-12-22 12:30 | 10.51 | 10.47
2019-12-22 13:00 | 11.88 | 11.83
2019-12-22 13:30 | 12.94 | 12.88
2019-12-22 14:00 | 13.66 | 13.59
2019-12-22 14:30 | 14.14 | 14.08
2019-12-22 15:00 | 14.38 | 14.32
2019-12-22 15:30 | 14.68 | 14.63
2019-12-22 16:00 | 15.18 | 15.13
2019-12-22 16:30 | 15.26 | 15.22
2019-12-22 17:00 | 15.53 | 15.5
2019-12-22 17:30 | 15.44 | 15.42
2019-12-22 18:00 | 15.17 | 15.15
2019-12-22 18:30 | 14.81 | 14.8
2019-12-22 19:00 | 14.82 | 14.81
2019-12-22 19:30 | 14.45 | 14.43
2019-12-22 20:00 | 14.43 | 14.41
2019-12-22 20:30 | 13.79 | 13.78
2019-12-22 21:00 | 13.03 | 13.03
2019-12-22 21:30 | 12.34 | 12.33
2019-12-22 22:00 | 11.62 | 11.61
2019-12-22 22:30 | 11.16 | 11.15
2019-12-22 23:00 | 10.69 | 10.68
2019-12-22 23:30 | 9.6 | 9.6
2019-12-23 | 8.74 | 8.74
2019-12-23 00:30 | 8.09 | 8.09
2019-12-23 01:00 | 7.62 | 7.61
2019-12-23 01:30 | 7.21 | 7.19
2019-12-23 02:00 | 6.8 | 6.78
2019-12-23 02:30 | 6.52 | 6.49
2019-12-23 03:00 | 6.39 | 6.37
2019-12-23 03:30 | 6.41 | 6.38
2019-12-23 04:00 | 6.12 | 6.08
2019-12-23 04:30 | 6.09 | 6.05
2019-12-23 05:00 | 6.12 | 6.07
2019-12-23 05:30 | 6.13 | 6.05
2019-12-23 06:00 | 6.44 | 6.37
2019-12-23 06:30 | 6.87 | 6.82
2019-12-23 07:00 | 7.07 | 7.02
2019-12-23 07:30 | 7.28 | 7.25
2019-12-23 08:00 | 7.39 | 7.35
2019-12-23 08:30 | 7.57 | 7.54
2019-12-23 09:00 | 7.67 | 7.66
2019-12-23 09:30 | 7.48 | 7.47
2019-12-23 10:00 | 8.06 | 8.05
2019-12-23 10:30 | 6.96 | 6.96
2019-12-23 11:00 | 6.15 | 6.15
2019-12-23 11:30 | 7.12 | 7.11
2019-12-23 12:00 | 6.87 | 6.85
2019-12-23 12:30 | 6.92 | 6.9
2019-12-23 13:00 | 8.34 | 8.32
2019-12-23 13:30 | 8.82 | 8.78
2019-12-23 14:00 | 10.01 | 9.97
2019-12-23 14:30 | 11.12 | 11.07
2019-12-23 15:00 | 12.36 | 12.31
2019-12-23 15:30 | 13.45 | 13.4
2019-12-23 16:00 | 14.26 | 14.2
2019-12-23 16:30 | 15.63 | 15.57
2019-12-23 17:00 | 15.88 | 15.83
2019-12-23 17:30 | 16.27 | 16.22
2019-12-23 18:00 | 16.53 | 16.5
2019-12-23 18:30 | 16.73 | 16.7
2019-12-23 19:00 | 16.89 | 16.86
2019-12-23 19:30 | 16.84 | 16.81
2019-12-23 20:00 | 16.49 | 16.45
2019-12-23 20:30 | 15.67 | 15.64
2019-12-23 21:00 | 14.78 | 14.76
2019-12-23 21:30 | 13.66 | 13.65
2019-12-23 22:00 | 12.95 | 12.94
2019-12-23 22:30 | 12.38 | 12.37
2019-12-23 23:00 | 11.55 | 11.54
2019-12-23 23:30 | 10.62 | 10.61
2019-12-24 | 9.58 | 9.57
2019-12-24 00:30 | 8.88 | 8.87
2019-12-24 01:00 | 8.41 | 8.4
2019-12-24 01:30 | 7.95 | 7.95
2019-12-24 02:00 | 7.54 | 7.53
2019-12-24 02:30 | 7.23 | 7.22
2019-12-24 03:00 | 7 | 6.98
2019-12-24 03:30 | 6.89 | 6.88
2019-12-24 04:00 | 6.83 | 6.81
2019-12-24 04:30 | 6.9 | 6.88
2019-12-24 05:00 | 6.76 | 6.74
2019-12-24 05:30 | 6.61 | 6.55
2019-12-24 06:00 | 6.57 | 6.51
2019-12-24 06:30 | 6.34 | 6.3
2019-12-24 07:00 | 7.2 | 7.17
2019-12-24 07:30 | 7.57 | 7.55
2019-12-24 08:00 | 6.73 | 6.71
2019-12-24 08:30 | 7.05 | 7.04
2019-12-24 09:00 | 6.4 | 6.38
2019-12-24 09:30 | 9.24 | 9.22
2019-12-24 10:00 | 9.61 | 9.6
2019-12-24 10:30 | 10.65 | 10.63
2019-12-24 11:00 | 11 | 10.98
2019-12-24 11:30 | 9.69 | 9.67
2019-12-24 12:00 | 8.09 | 8.05
2019-12-24 12:30 | 10.33 | 10.29
2019-12-24 13:00 | 11.58 | 11.54
2019-12-24 13:30 | 11.92 | 11.87
2019-12-24 14:00 | 11.28 | 11.21
2019-12-24 14:30 | 14.39 | 14.33
2019-12-24 15:00 | 13.01 | 12.94
2019-12-24 15:30 | 13.05 | 12.98
2019-12-24 16:00 | 14.05 | 13.99
2019-12-24 16:30 | 15.07 | 15.02
2019-12-24 17:00 | 15.11 | 15.07
2019-12-24 17:30 | 16.29 | 16.25
2019-12-24 18:00 | 15.77 | 15.74
2019-12-24 18:30 | 15.25 | 15.23
2019-12-24 19:00 | 15.13 | 15.11
2019-12-24 19:30 | 14.58 | 14.56
2019-12-24 20:00 | 14.05 | 14.04
2019-12-24 20:30 | 13.31 | 13.3
2019-12-24 21:00 | 12.73 | 12.72
2019-12-24 21:30 | 12.04 | 12.04
2019-12-24 22:00 | 11.59 | 11.59
2019-12-24 22:30 | 11.13 | 11.12
2019-12-24 23:00 | 10.62 | 10.62
2019-12-24 23:30 | 7.55 | 7.55
2019-12-25 | 6.89 | 6.89
2019-12-25 00:30 | 6.31 | 6.3
2019-12-25 01:00 | 6.08 | 6.07
2019-12-25 01:30 | 5.58 | 5.56
2019-12-25 02:00 | 5.21 | 5.18
2019-12-25 02:30 | 5.67 | 5.65
2019-12-25 03:00 | 6.72 | 6.71
2019-12-25 03:30 | 6.23 | 6.2
2019-12-25 04:00 | 5.99 | 5.96
2019-12-25 04:30 | 5.87 | 5.83
2019-12-25 05:00 | 5.8 | 5.74
2019-12-25 05:30 | 5.84 | 5.73
2019-12-25 06:00 | 5.62 | 5.51
2019-12-25 06:30 | 6.1 | 6.01
2019-12-25 07:00 | 6.81 | 6.73
2019-12-25 07:30 | 7.04 | 6.97
2019-12-25 08:00 | 7.28 | 7.22
2019-12-25 08:30 | 7.43 | 7.39
2019-12-25 09:00 | 7.2 | 7.17
2019-12-25 09:30 | 6.53 | 6.51
2019-12-25 10:00 | 7.9 | 7.89
2019-12-25 10:30 | 7.29 | 7.28
2019-12-25 11:00 | 8.44 | 8.43
2019-12-25 11:30 | 8.64 | 8.63
2019-12-25 12:00 | 7.19 | 7.17
2019-12-25 12:30 | 8.14 | 8.12
2019-12-25 13:00 | 7.49 | 7.47
2019-12-25 13:30 | 7.42 | 7.4
2019-12-25 14:00 | 6.7 | 6.69
2019-12-25 14:30 | 5.17 | 5.16
2019-12-25 15:00 | 5.77 | 5.76
2019-12-25 15:30 | 5.5 | 5.49
2019-12-25 16:00 | 6.41 | 6.4
2019-12-25 16:30 | 7.31 | 7.3
2019-12-25 17:00 | 8.03 | 8.02
2019-12-25 17:30 | 9.07 | 9.06
2019-12-25 18:00 | 9.13 | 9.11
2019-12-25 18:30 | 9.2 | 9.18
2019-12-25 19:00 | 9.52 | 9.51
2019-12-25 19:30 | 9.9 | 9.9
2019-12-25 20:00 | 10.34 | 10.33
2019-12-25 20:30 | 10.16 | 10.16
2019-12-25 21:00 | 9.99 | 9.98
2019-12-25 21:30 | 9.5 | 9.49
2019-12-25 22:00 | 9.29 | 9.28
2019-12-25 22:30 | 9.16 | 9.15
2019-12-25 23:00 | 8.96 | 8.95
2019-12-25 23:30 | 8.07 | 8.05
2019-12-26 | 7.21 | 7.18
2019-12-26 00:30 | 6.62 | 6.58
2019-12-26 01:00 | 6.47 | 6.43
2019-12-26 01:30 | 6.13 | 6.08
2019-12-26 02:00 | 5.86 | 5.8
2019-12-26 02:30 | 5.64 | 5.58
2019-12-26 03:00 | 5.6 | 5.54
2019-12-26 03:30 | 5.52 | 5.46
2019-12-26 04:00 | 5.37 | 5.3
2019-12-26 04:30 | 5.35 | 5.28
2019-12-26 05:00 | 5.17 | 5.05
2019-12-26 05:30 | 4.93 | 4.75
2019-12-26 06:00 | 4.67 | 4.49
2019-12-26 06:30 | 4.51 | 4.34
2019-12-26 07:00 | 4.24 | 4.09
2019-12-26 07:30 | 4.06 | 3.94
2019-12-26 08:00 | 4.11 | 4.02
2019-12-26 08:30 | 4.76 | 4.71
2019-12-26 09:00 | 4.58 | 4.55
2019-12-26 09:30 | 6.4 | 6.38
2019-12-26 10:00 | 6.14 | 6.12
2019-12-26 10:30 | 6.54 | 6.52
2019-12-26 11:00 | 2.79 | 2.75
2019-12-26 11:30 | 5.03 | 5.01
2019-12-26 12:00 | 3.88 | 3.84
2019-12-26 12:30 | 6.15 | 6.12
2019-12-26 13:00 | 7.51 | 7.49
2019-12-26 13:30 | 6.09 | 6.07
2019-12-26 14:00 | 7.18 | 7.16
2019-12-26 14:30 | 7.02 | 7
2019-12-26 15:00 | 7.77 | 7.75
2019-12-26 15:30 | 8.63 | 8.62
2019-12-26 16:00 | 8.54 | 8.53
2019-12-26 16:30 | 8.74 | 8.73
2019-12-26 17:00 | 9.75 | 9.74
2019-12-26 17:30 | 10.35 | 10.34
2019-12-26 18:00 | 10.47 | 10.46
2019-12-26 18:30 | 10.57 | 10.56
2019-12-26 19:00 | 10.81 | 10.8
2019-12-26 19:30 | 11.12 | 11.12
2019-12-26 20:00 | 11.38 | 11.37
2019-12-26 20:30 | 11.03 | 11.02
2019-12-26 21:00 | 10.44 | 10.43
2019-12-26 21:30 | 9.93 | 9.92
2019-12-26 22:00 | 9.47 | 9.45
2019-12-26 22:30 | 9.06 | 9.04
2019-12-26 23:00 | 8.77 | 8.75
2019-12-26 23:30 | 7.88 | 7.85
2019-12-27 | 7.03 | 6.99
2019-12-27 00:30 | 6.45 | 6.39
2019-12-27 01:00 | 6.22 | 6.16
2019-12-27 01:30 | 5.9 | 5.83
2019-12-27 02:00 | 5.54 | 5.46
2019-12-27 02:30 | 5.36 | 5.28
2019-12-27 03:00 | 5.3 | 5.22
2019-12-27 03:30 | 5.34 | 5.26
2019-12-27 04:00 | 5.32 | 5.23
2019-12-27 04:30 | 5.26 | 5.18
2019-12-27 05:00 | 5.12 | 4.97
2019-12-27 05:30 | 5.02 | 4.84
2019-12-27 06:00 | 4.72 | 4.53
2019-12-27 06:30 | 4.38 | 4.21
2019-12-27 07:00 | 4.23 | 4.08
2019-12-27 07:30 | 3.69 | 3.57
2019-12-27 08:00 | 3.54 | 3.44
2019-12-27 08:30 | 4.03 | 3.97
2019-12-27 09:00 | 4.11 | 4.07
2019-12-27 09:30 | 5.7 | 5.68
2019-12-27 10:00 | 4.94 | 4.91
2019-12-27 10:30 | 7.72 | 7.7
2019-12-27 11:00 | 5.34 | 5.32
2019-12-27 11:30 | 7.32 | 7.31
2019-12-27 12:00 | 4.79 | 4.77
2019-12-27 12:30 | 3.07 | 3.02
2019-12-27 13:00 | 4.1 | 4.07
2019-12-27 13:30 | 5.49 | 5.46
2019-12-27 14:00 | 7.45 | 7.43
2019-12-27 14:30 | 7.61 | 7.6
2019-12-27 15:00 | 6.2 | 6.18
2019-12-27 15:30 | 6.71 | 6.69
2019-12-27 16:00 | 6.82 | 6.8
2019-12-27 16:30 | 8.14 | 8.12
2019-12-27 17:00 | 9.5 | 9.48
2019-12-27 17:30 | 10.62 | 10.61
2019-12-27 18:00 | 11.28 | 11.27
2019-12-27 18:30 | 11.53 | 11.52
2019-12-27 19:00 | 11.7 | 11.7
2019-12-27 19:30 | 12 | 11.99
2019-12-27 20:00 | 12.16 | 12.16
2019-12-27 20:30 | 11.94 | 11.93
2019-12-27 21:00 | 11.08 | 11.07
2019-12-27 21:30 | 10.21 | 10.21
2019-12-27 22:00 | 9.55 | 9.54
2019-12-27 22:30 | 9.23 | 9.21
2019-12-27 23:00 | 8.93 | 8.9
2019-12-27 23:30 | 8.04 | 8.01
2019-12-28 | 7.22 | 7.18
2019-12-28 00:30 | 6.55 | 6.5
2019-12-28 01:00 | 6.31 | 6.26
2019-12-28 01:30 | 6.08 | 6.02
2019-12-28 02:00 | 5.76 | 5.69
2019-12-28 02:30 | 5.54 | 5.46
2019-12-28 03:00 | 5.51 | 5.44
2019-12-28 03:30 | 5.48 | 5.41
2019-12-28 04:00 | 5.3 | 5.22
2019-12-28 04:30 | 5.17 | 5.09
2019-12-28 05:00 | 5.04 | 4.91
2019-12-28 05:30 | 5.02 | 4.82
2019-12-28 06:00 | 4.93 | 4.74
2019-12-28 06:30 | 4.91 | 4.74
2019-12-28 07:00 | 4.91 | 4.75
2019-12-28 07:30 | 4.01 | 3.86
2019-12-28 08:00 | 3.92 | 3.79
2019-12-28 08:30 | 5.67 | 5.6
2019-12-28 09:00 | 4.56 | 4.5
2019-12-28 09:30 | 4.49 | 4.46
2019-12-28 10:00 | 5.79 | 5.77
2019-12-28 10:30 | 7.03 | 7.01
2019-12-28 11:00 | 5.39 | 5.37
2019-12-28 11:30 | 4.57 | 4.54
2019-12-28 12:00 | 4.27 | 4.24
2019-12-28 12:30 | 3.82 | 3.78
2019-12-28 13:00 | 4.65 | 4.61
2019-12-28 13:30 | 5.59 | 5.56
2019-12-28 14:00 | 6.04 | 6.01
2019-12-28 14:30 | 5.64 | 5.61
2019-12-28 15:00 | 6 | 5.97
2019-12-28 15:30 | 7.54 | 7.52
2019-12-28 16:00 | 8.38 | 8.36
2019-12-28 16:30 | 9.27 | 9.25
2019-12-28 17:00 | 10.46 | 10.45
2019-12-28 17:30 | 10.83 | 10.82
2019-12-28 18:00 | 11.64 | 11.63
2019-12-28 18:30 | 11.8 | 11.79
2019-12-28 19:00 | 12.01 | 12
2019-12-28 19:30 | 12.33 | 12.33
2019-12-28 20:00 | 12.36 | 12.35
2019-12-28 20:30 | 12.17 | 12.17
2019-12-28 21:00 | 11.52 | 11.51
2019-12-28 21:30 | 10.84 | 10.83
2019-12-28 22:00 | 10.1 | 10.09
2019-12-28 22:30 | 9.64 | 9.63
2019-12-28 23:00 | 9.31 | 9.3
2019-12-28 23:30 | 8.42 | 8.39
2019-12-29 | 7.52 | 7.49
2019-12-29 00:30 | 6.89 | 6.85
2019-12-29 01:00 | 6.67 | 6.62
2019-12-29 01:30 | 6.29 | 6.23
2019-12-29 02:00 | 5.88 | 5.82
2019-12-29 02:30 | 5.68 | 5.61
2019-12-29 03:00 | 5.46 | 5.39
2019-12-29 03:30 | 5.37 | 5.29
2019-12-29 04:00 | 5.27 | 5.2
2019-12-29 04:30 | 5.27 | 5.18
2019-12-29 05:00 | 5.09 | 4.97
2019-12-29 05:30 | 4.95 | 4.77
2019-12-29 06:00 | 4.88 | 4.7
2019-12-29 06:30 | 4.5 | 4.32
2019-12-29 07:00 | 3.99 | 3.82
2019-12-29 07:30 | 3.92 | 3.8
2019-12-29 08:00 | 4.25 | 4.15
2019-12-29 08:30 | 3.23 | 3.15
2019-12-29 09:00 | 4.29 | 4.25
2019-12-29 09:30 | 4.61 | 4.59
2019-12-29 10:00 | 3.49 | 3.46
2019-12-29 10:30 | 3.44 | 3.41
2019-12-29 11:00 | 3.41 | 3.37
2019-12-29 11:30 | 3.87 | 3.83
2019-12-29 12:00 | 4.52 | 4.48
2019-12-29 12:30 | 5.1 | 5.06
2019-12-29 13:00 | 5.84 | 5.81
2019-12-29 13:30 | 6.7 | 6.66
2019-12-29 14:00 | 7.54 | 7.5
2019-12-29 14:30 | 8.61 | 8.58
2019-12-29 15:00 | 9.2 | 9.17
2019-12-29 15:30 | 10.42 | 10.4
2019-12-29 16:00 | 11.38 | 11.35
2019-12-29 16:30 | 12.14 | 12.12
2019-12-29 17:00 | 12.95 | 12.93
2019-12-29 17:30 | 13.82 | 13.8
2019-12-29 18:00 | 13.99 | 13.98
2019-12-29 18:30 | 13.87 | 13.86
2019-12-29 19:00 | 13.67 | 13.66
2019-12-29 19:30 | 13.59 | 13.58
2019-12-29 20:00 | 13.44 | 13.43
2019-12-29 20:30 | 12.85 | 12.85
2019-12-29 21:00 | 11.94 | 11.94
2019-12-29 21:30 | 11.21 | 11.2
2019-12-29 22:00 | 10.46 | 10.46
2019-12-29 22:30 | 9.82 | 9.81
2019-12-29 23:00 | 9.46 | 9.45
2019-12-29 23:30 | 8.35 | 8.33
2019-12-30 | 7.56 | 7.53
2019-12-30 00:30 | 6.82 | 6.77
2019-12-30 01:00 | 6.48 | 6.43
2019-12-30 01:30 | 6.17 | 6.11
2019-12-30 02:00 | 5.87 | 5.82
2019-12-30 02:30 | 5.62 | 5.56
2019-12-30 03:00 | 5.49 | 5.41
2019-12-30 03:30 | 5.42 | 5.34
2019-12-30 04:00 | 5.32 | 5.24
2019-12-30 04:30 | 5.25 | 5.17
2019-12-30 05:00 | 5.16 | 5.03
2019-12-30 05:30 | 5.1 | 4.93
2019-12-30 06:00 | 4.78 | 4.6
2019-12-30 06:30 | 4.62 | 4.47
2019-12-30 07:00 | 4.8 | 4.66
2019-12-30 07:30 | 3.79 | 3.67
2019-12-30 08:00 | 3.3 | 3.22
2019-12-30 08:30 | 5.82 | 5.78
2019-12-30 09:00 | 4.44 | 4.4
2019-12-30 09:30 | 3.55 | 3.52
2019-12-30 10:00 | 3.76 | 3.73
2019-12-30 10:30 | 4.99 | 4.96
2019-12-30 11:00 | 4.74 | 4.72
2019-12-30 11:30 | 5.06 | 5.04
2019-12-30 12:00 | 5.86 | 5.84
2019-12-30 12:30 | 5.91 | 5.89
2019-12-30 13:00 | 6.28 | 6.26
2019-12-30 13:30 | 7.01 | 6.98
2019-12-30 14:00 | 7.04 | 7.01
2019-12-30 14:30 | 7.65 | 7.61
2019-12-30 15:00 | 8.48 | 8.45
2019-12-30 15:30 | 9.61 | 9.58
2019-12-30 16:00 | 11 | 10.97
2019-12-30 16:30 | 12.08 | 12.06
2019-12-30 17:00 | 13.37 | 13.35
2019-12-30 17:30 | 14.28 | 14.25
2019-12-30 18:00 | 14.72 | 14.7
2019-12-30 18:30 | 14.81 | 14.79
2019-12-30 19:00 | 14.72 | 14.71
2019-12-30 19:30 | 14.97 | 14.95
2019-12-30 20:00 | 14.78 | 14.77
2019-12-30 20:30 | 14.24 | 14.23
2019-12-30 21:00 | 13.28 | 13.27
2019-12-30 21:30 | 12.43 | 12.43
2019-12-30 22:00 | 11.49 | 11.49
2019-12-30 22:30 | 10.87 | 10.86
2019-12-30 23:00 | 10.28 | 10.28
2019-12-30 23:30 | 9.32 | 9.31
2019-12-31 | 8.36 | 8.35
2019-12-31 00:30 | 7.61 | 7.6
2019-12-31 01:00 | 7.27 | 7.25
2019-12-31 01:30 | 6.96 | 6.94
2019-12-31 02:00 | 6.57 | 6.54
2019-12-31 02:30 | 6.41 | 6.38
2019-12-31 03:00 | 6.22 | 6.19
2019-12-31 03:30 | 6.12 | 6.08
2019-12-31 04:00 | 5.99 | 5.95
2019-12-31 04:30 | 6.07 | 6.03
2019-12-31 05:00 | 5.83 | 5.76
2019-12-31 05:30 | 5.76 | 5.65
2019-12-31 06:00 | 5.65 | 5.55
2019-12-31 06:30 | 5.36 | 5.27
2019-12-31 07:00 | 5.31 | 5.24
2019-12-31 07:30 | 6.18 | 6.13
2019-12-31 08:00 | 4.5 | 4.46
2019-12-31 08:30 | 5.2 | 5.18
2019-12-31 09:00 | 6.91 | 6.89
2019-12-31 09:30 | 5.49 | 5.47
2019-12-31 10:00 | 4.16 | 4.13
2019-12-31 10:30 | 4.45 | 4.41
2019-12-31 11:00 | 6.86 | 6.84
2019-12-31 11:30 | 6.87 | 6.84
2019-12-31 12:00 | 6.74 | 6.7
2019-12-31 12:30 | 8.29 | 8.25
2019-12-31 13:00 | 9.65 | 9.61
2019-12-31 13:30 | 9.44 | 9.39
2019-12-31 14:00 | 10.24 | 10.19
2019-12-31 14:30 | 11.15 | 11.1
2019-12-31 15:00 | 11.58 | 11.53
2019-12-31 15:30 | 11.67 | 11.62
2019-12-31 16:00 | 12.83 | 12.78
2019-12-31 16:30 | 13.84 | 13.8
2019-12-31 17:00 | 14.55 | 14.52
2019-12-31 17:30 | 15.01 | 14.97
2019-12-31 18:00 | 14.83 | 14.8
2019-12-31 18:30 | 14.42 | 14.41
2019-12-31 19:00 | 14.1 | 14.09
2019-12-31 19:30 | 13.66 | 13.64
2019-12-31 20:00 | 13.47 | 13.46
2019-12-31 20:30 | 12.87 | 12.87
2019-12-31 21:00 | 11.94 | 11.93
2019-12-31 21:30 | 11.35 | 11.34
2019-12-31 22:00 | 10.85 | 10.85
2019-12-31 22:30 | 10.51 | 10.51
2019-12-31 23:00 | 10.24 | 10.24
2019-12-31 23:30 | 9.4 | 9.39
2020-01-01 | 8.67 | 8.66
2020-01-01 00:30 | 8.01 | 7.99
2020-01-01 01:00 | 7.75 | 7.74
2020-01-01 01:30 | 7.31 | 7.29
2020-01-01 02:00 | 6.88 | 6.86
2020-01-01 02:30 | 6.79 | 6.77
2020-01-01 03:00 | 6.6 | 6.57
2020-01-01 03:30 | 6.47 | 6.45
2020-01-01 04:00 | 6.33 | 6.3
2020-01-01 04:30 | 6.16 | 6.12
2020-01-01 05:00 | 5.93 | 5.87
2020-01-01 05:30 | 5.73 | 5.63
2020-01-01 06:00 | 5.51 | 5.4
2020-01-01 06:30 | 5.34 | 5.23
2020-01-01 07:00 | 4.96 | 4.86
2020-01-01 07:30 | 4.57 | 4.5
2020-01-01 08:00 | 4.95 | 4.9
2020-01-01 08:30 | 4.84 | 4.82
2020-01-01 09:00 | 5.29 | 5.27
2020-01-01 09:30 | 5.74 | 5.72
2020-01-01 10:00 | 4.94 | 4.91
2020-01-01 10:30 | 6.23 | 6.2
2020-01-01 11:00 | 6.3 | 6.27
2020-01-01 11:30 | 6.93 | 6.89
2020-01-01 12:00 | 7.7 | 7.65
2020-01-01 12:30 | 8.57 | 8.52
2020-01-01 13:00 | 9.32 | 9.27
2020-01-01 13:30 | 10.06 | 10
2020-01-01 14:00 | 10.83 | 10.77
2020-01-01 14:30 | 11.59 | 11.52
2020-01-01 15:00 | 12.37 | 12.31
2020-01-01 15:30 | 13.41 | 13.35
2020-01-01 16:00 | 14.36 | 14.3
2020-01-01 16:30 | 15.29 | 15.23
2020-01-01 17:00 | 16.21 | 16.16
2020-01-01 17:30 | 16.7 | 16.66
2020-01-01 18:00 | 16.86 | 16.82
2020-01-01 18:30 | 16.37 | 16.35
2020-01-01 19:00 | 15.9 | 15.89
2020-01-01 19:30 | 15.66 | 15.64
2020-01-01 20:00 | 15.38 | 15.36
2020-01-01 20:30 | 14.82 | 14.81
2020-01-01 21:00 | 13.79 | 13.78
2020-01-01 21:30 | 12.81 | 12.8
2020-01-01 22:00 | 11.93 | 11.93
2020-01-01 22:30 | 11.43 | 11.42
2020-01-01 23:00 | 10.82 | 10.82
2020-01-01 23:30 | 9.78 | 9.78
2020-01-02 | 8.68 | 8.67
2020-01-02 00:30 | 8.03 | 8.01
2020-01-02 01:00 | 7.6 | 7.58
2020-01-02 01:30 | 7.12 | 7.1
2020-01-02 02:00 | 6.88 | 6.86
2020-01-02 02:30 | 6.6 | 6.57
2020-01-02 03:00 | 6.36 | 6.32
2020-01-02 03:30 | 6.2 | 6.16
2020-01-02 04:00 | 6.15 | 6.11
2020-01-02 04:30 | 6.06 | 6.02
2020-01-02 05:00 | 5.94 | 5.87
2020-01-02 05:30 | 5.83 | 5.73
2020-01-02 06:00 | 5.56 | 5.45
2020-01-02 06:30 | 5.32 | 5.22
2020-01-02 07:00 | 5.17 | 5.1
2020-01-02 07:30 | 4.96 | 4.92
2020-01-02 08:00 | 5.05 | 5.02
2020-01-02 08:30 | 5.23 | 5.21
2020-01-02 09:00 | 5.86 | 5.85
2020-01-02 09:30 | 6.45 | 6.42
2020-01-02 10:00 | 5.72 | 5.69
2020-01-02 10:30 | 5.91 | 5.87
2020-01-02 11:00 | 6.85 | 6.82
2020-01-02 11:30 | 7.26 | 7.22
2020-01-02 12:00 | 8.03 | 7.97
2020-01-02 12:30 | 8.88 | 8.81
2020-01-02 13:00 | 9.61 | 9.54
2020-01-02 13:30 | 10.75 | 10.66
2020-01-02 14:00 | 11.77 | 11.68
2020-01-02 14:30 | 12.53 | 12.44
2020-01-02 15:00 | 13.4 | 13.31
2020-01-02 15:30 | 14.38 | 14.29
2020-01-02 16:00 | 15.23 | 15.14
2020-01-02 16:30 | 16.11 | 16.04
2020-01-02 17:00 | 17.02 | 16.95
2020-01-02 17:30 | 17.7 | 17.63
2020-01-02 18:00 | 18 | 17.94
2020-01-02 18:30 | 17.28 | 17.23
2020-01-02 19:00 | 17.07 | 17.04
2020-01-02 19:30 | 16.72 | 16.67
2020-01-02 20:00 | 16.34 | 16.3
2020-01-02 20:30 | 15.49 | 15.47
2020-01-02 21:00 | 14.5 | 14.48
2020-01-02 21:30 | 13.29 | 13.29
2020-01-02 22:00 | 12.31 | 12.31
2020-01-02 22:30 | 11.61 | 11.61
2020-01-02 23:00 | 10.92 | 10.91
2020-01-02 23:30 | 9.83 | 9.82
2020-01-03 | 8.79 | 8.78
2020-01-03 00:30 | 8 | 7.98
2020-01-03 01:00 | 7.7 | 7.68
2020-01-03 01:30 | 7.25 | 7.23
2020-01-03 02:00 | 6.74 | 6.71
2020-01-03 02:30 | 6.55 | 6.52
2020-01-03 03:00 | 6.43 | 6.4
2020-01-03 03:30 | 6.23 | 6.2
2020-01-03 04:00 | 6.14 | 6.1
2020-01-03 04:30 | 6.01 | 5.97
2020-01-03 05:00 | 5.89 | 5.82
2020-01-03 05:30 | 5.74 | 5.62
2020-01-03 06:00 | 5.53 | 5.42
2020-01-03 06:30 | 5.34 | 5.25
2020-01-03 07:00 | 5.11 | 5.04
2020-01-03 07:30 | 5.01 | 4.97
2020-01-03 08:00 | 5.34 | 5.32
2020-01-03 08:30 | 5.41 | 5.39
2020-01-03 09:00 | 6.1 | 6.09
2020-01-03 09:30 | 5.34 | 5.31
2020-01-03 10:00 | 5.7 | 5.67
2020-01-03 10:30 | 5.99 | 5.96
2020-01-03 11:00 | 5.95 | 5.91
2020-01-03 11:30 | 6.51 | 6.47
2020-01-03 12:00 | 7.44 | 7.37
2020-01-03 12:30 | 8.41 | 8.34
2020-01-03 13:00 | 9.41 | 9.33
2020-01-03 13:30 | 10.25 | 10.16
2020-01-03 14:00 | 11.19 | 11.1
2020-01-03 14:30 | 11.96 | 11.87
2020-01-03 15:00 | 12.87 | 12.78
2020-01-03 15:30 | 13.73 | 13.65
2020-01-03 16:00 | 14.53 | 14.45
2020-01-03 16:30 | 15.62 | 15.54
2020-01-03 17:00 | 16.55 | 16.48
2020-01-03 17:30 | 17.06 | 17
2020-01-03 18:00 | 16.86 | 16.81
2020-01-03 18:30 | 16.64 | 16.61
2020-01-03 19:00 | 16.29 | 16.27
2020-01-03 19:30 | 15.81 | 15.77
2020-01-03 20:00 | 15.51 | 15.48
2020-01-03 20:30 | 14.98 | 14.96
2020-01-03 21:00 | 13.91 | 13.9
2020-01-03 21:30 | 13 | 13
2020-01-03 22:00 | 12.05 | 12.04
2020-01-03 22:30 | 11.41 | 11.41
2020-01-03 23:00 | 10.78 | 10.77
2020-01-03 23:30 | 9.6 | 9.59
2020-01-04 | 8.63 | 8.62
2020-01-04 00:30 | 7.9 | 7.89
2020-01-04 01:00 | 7.44 | 7.42
2020-01-04 01:30 | 6.97 | 6.94
2020-01-04 02:00 | 6.58 | 6.54
2020-01-04 02:30 | 6.36 | 6.33
2020-01-04 03:00 | 6.17 | 6.12
2020-01-04 03:30 | 6.14 | 6.09
2020-01-04 04:00 | 5.95 | 5.9
2020-01-04 04:30 | 5.87 | 5.81
2020-01-04 05:00 | 5.67 | 5.58
2020-01-04 05:30 | 5.6 | 5.47
2020-01-04 06:00 | 5.27 | 5.13
2020-01-04 06:30 | 5.06 | 4.94
2020-01-04 07:00 | 4.77 | 4.68
2020-01-04 07:30 | 4.53 | 4.46
2020-01-04 08:00 | 4.88 | 4.84
2020-01-04 08:30 | 4.83 | 4.81
2020-01-04 09:00 | 4.63 | 4.6
2020-01-04 09:30 | 5.12 | 5.08
2020-01-04 10:00 | 5.26 | 5.22
2020-01-04 10:30 | 5.72 | 5.67
2020-01-04 11:00 | 6.62 | 6.58
2020-01-04 11:30 | 7.4 | 7.34
2020-01-04 12:00 | 8.42 | 8.35
2020-01-04 12:30 | 9.47 | 9.38
2020-01-04 13:00 | 10.74 | 10.63
2020-01-04 13:30 | 11.79 | 11.68
2020-01-04 14:00 | 12.64 | 12.54
2020-01-04 14:30 | 13.73 | 13.63
2020-01-04 15:00 | 14.53 | 14.43
2020-01-04 15:30 | 15.71 | 15.59
2020-01-04 16:00 | 16.42 | 16.32
2020-01-04 16:30 | 16.98 | 16.9
2020-01-04 17:00 | 17.2 | 17.12
2020-01-04 17:30 | 17.01 | 16.96
2020-01-04 18:00 | 16.76 | 16.72
2020-01-04 18:30 | 16.17 | 16.14
2020-01-04 19:00 | 15.89 | 15.87
2020-01-04 19:30 | 15.52 | 15.49
2020-01-04 20:00 | 15.28 | 15.26
2020-01-04 20:30 | 14.63 | 14.61
2020-01-04 21:00 | 13.49 | 13.48
2020-01-04 21:30 | 12.65 | 12.64
2020-01-04 22:00 | 11.66 | 11.65
2020-01-04 22:30 | 11.11 | 11.1
2020-01-04 23:00 | 10.61 | 10.6
2020-01-04 23:30 | 9.57 | 9.57
2020-01-05 | 8.73 | 8.72
2020-01-05 00:30 | 8 | 7.99
2020-01-05 01:00 | 7.63 | 7.61
2020-01-05 01:30 | 7.18 | 7.15
2020-01-05 02:00 | 6.76 | 6.73
2020-01-05 02:30 | 6.48 | 6.44
2020-01-05 03:00 | 6.22 | 6.18
2020-01-05 03:30 | 6.11 | 6.07
2020-01-05 04:00 | 5.92 | 5.86
2020-01-05 04:30 | 5.9 | 5.85
2020-01-05 05:00 | 5.68 | 5.59
2020-01-05 05:30 | 5.46 | 5.31
2020-01-05 06:00 | 5.17 | 5.02
2020-01-05 06:30 | 4.89 | 4.74
2020-01-05 07:00 | 4.5 | 4.37
2020-01-05 07:30 | 4.4 | 4.3
2020-01-05 08:00 | 4.26 | 4.2
2020-01-05 08:30 | 4.47 | 4.44
2020-01-05 09:00 | 4.53 | 4.51
2020-01-05 09:30 | 4.79 | 4.77
2020-01-05 10:00 | 5.27 | 5.24
2020-01-05 10:30 | 5.76 | 5.73
2020-01-05 11:00 | 6.4 | 6.37
2020-01-05 11:30 | 7.31 | 7.28
2020-01-05 12:00 | 8.44 | 8.4
2020-01-05 12:30 | 9.42 | 9.37
2020-01-05 13:00 | 10.59 | 10.54
2020-01-05 13:30 | 11.88 | 11.82
2020-01-05 14:00 | 13.5 | 13.41
2020-01-05 14:30 | 14.39 | 14.3
2020-01-05 15:00 | 15.4 | 15.31
2020-01-05 15:30 | 16.04 | 15.96
2020-01-05 16:00 | 16.69 | 16.62
2020-01-05 16:30 | 17.11 | 17.05
2020-01-05 17:00 | 17.35 | 17.3
2020-01-05 17:30 | 17.42 | 17.38
2020-01-05 18:00 | 17.25 | 17.21
2020-01-05 18:30 | 16.85 | 16.83
2020-01-05 19:00 | 16.48 | 16.46
2020-01-05 19:30 | 16.17 | 16.14
2020-01-05 20:00 | 15.95 | 15.93
2020-01-05 20:30 | 15.14 | 15.13
2020-01-05 21:00 | 14.13 | 14.12
2020-01-05 21:30 | 13.11 | 13.11
2020-01-05 22:00 | 12.27 | 12.27
2020-01-05 22:30 | 11.62 | 11.62
2020-01-05 23:00 | 10.98 | 10.98
2020-01-05 23:30 | 9.84 | 9.84
2020-01-06 | 8.88 | 8.88
2020-01-06 00:30 | 8.22 | 8.21
2020-01-06 01:00 | 7.74 | 7.73
2020-01-06 01:30 | 7.4 | 7.39
2020-01-06 02:00 | 7.01 | 6.99
2020-01-06 02:30 | 6.77 | 6.75
2020-01-06 03:00 | 6.65 | 6.62
2020-01-06 03:30 | 6.55 | 6.52
2020-01-06 04:00 | 6.5 | 6.48
2020-01-06 04:30 | 6.52 | 6.5
2020-01-06 05:00 | 6.41 | 6.36
2020-01-06 05:30 | 6.35 | 6.28
2020-01-06 06:00 | 6.47 | 6.41
2020-01-06 06:30 | 6.48 | 6.44
2020-01-06 07:00 | 6.66 | 6.64
2020-01-06 07:30 | 6.49 | 6.48
2020-01-06 08:00 | 7.38 | 7.38
2020-01-06 08:30 | 7.35 | 7.35
2020-01-06 09:00 | 6.63 | 6.62
2020-01-06 09:30 | 7.99 | 7.98
2020-01-06 10:00 | 9.71 | 9.71
2020-01-06 10:30 | 9.7 | 9.69
2020-01-06 11:00 | 9.29 | 9.27
2020-01-06 11:30 | 8.89 | 8.86
2020-01-06 12:00 | 9.61 | 9.56
2020-01-06 12:30 | 10.16 | 10.09
2020-01-06 13:00 | 10.5 | 10.42
2020-01-06 13:30 | 11.37 | 11.28
2020-01-06 14:00 | 12.04 | 11.95
2020-01-06 14:30 | 13.19 | 13.1
2020-01-06 15:00 | 14.35 | 14.26
2020-01-06 15:30 | 15.27 | 15.18
2020-01-06 16:00 | 15.76 | 15.68
2020-01-06 16:30 | 15.91 | 15.83
2020-01-06 17:00 | 16.56 | 16.5
2020-01-06 17:30 | 16.76 | 16.7
2020-01-06 18:00 | 17.07 | 17.01
2020-01-06 18:30 | 17.29 | 17.25
2020-01-06 19:00 | 17.52 | 17.49
2020-01-06 19:30 | 17.5 | 17.46
2020-01-06 20:00 | 17.07 | 17.04
2020-01-06 20:30 | 16.67 | 16.65
2020-01-06 21:00 | 15.45 | 15.43
2020-01-06 21:30 | 14.19 | 14.18
2020-01-06 22:00 | 12.98 | 12.97
2020-01-06 22:30 | 12.07 | 12.06
2020-01-06 23:00 | 11.2 | 11.2
2020-01-06 23:30 | 10.06 | 10.06
2020-01-07 | 8.97 | 8.97
2020-01-07 00:30 | 8.21 | 8.2
2020-01-07 01:00 | 7.88 | 7.87
2020-01-07 01:30 | 7.44 | 7.43
2020-01-07 02:00 | 7.03 | 7.01
2020-01-07 02:30 | 6.81 | 6.79
2020-01-07 03:00 | 6.61 | 6.58
2020-01-07 03:30 | 6.62 | 6.6
2020-01-07 04:00 | 6.47 | 6.44
2020-01-07 04:30 | 6.54 | 6.51
2020-01-07 05:00 | 6.35 | 6.3
2020-01-07 05:30 | 6.34 | 6.26
2020-01-07 06:00 | 6.42 | 6.33
2020-01-07 06:30 | 6.64 | 6.58
2020-01-07 07:00 | 6.86 | 6.82
2020-01-07 07:30 | 6.07 | 6.05
2020-01-07 08:00 | 7.79 | 7.76
2020-01-07 08:30 | 7.78 | 7.77
2020-01-07 09:00 | 8.61 | 8.6
2020-01-07 09:30 | 8.4 | 8.4
2020-01-07 10:00 | 8.28 | 8.27
2020-01-07 10:30 | 9.51 | 9.5
2020-01-07 11:00 | 9.6 | 9.59
2020-01-07 11:30 | 8.99 | 8.98
2020-01-07 12:00 | 10.81 | 10.8
2020-01-07 12:30 | 10.14 | 10.12
2020-01-07 13:00 | 9.59 | 9.55
2020-01-07 13:30 | 11.3 | 11.25
2020-01-07 14:00 | 13.12 | 13.06
2020-01-07 14:30 | 13.9 | 13.85
2020-01-07 15:00 | 13.94 | 13.88
2020-01-07 15:30 | 13.88 | 13.81
2020-01-07 16:00 | 14.37 | 14.3
2020-01-07 16:30 | 15.48 | 15.42
2020-01-07 17:00 | 16.39 | 16.33
2020-01-07 17:30 | 17.4 | 17.34
2020-01-07 18:00 | 17.61 | 17.56
2020-01-07 18:30 | 17.59 | 17.55
2020-01-07 19:00 | 17.33 | 17.3
2020-01-07 19:30 | 17 | 16.96
2020-01-07 20:00 | 16.91 | 16.87
2020-01-07 20:30 | 16.43 | 16.4
2020-01-07 21:00 | 15.26 | 15.25
2020-01-07 21:30 | 14.01 | 14
2020-01-07 22:00 | 12.6 | 12.6
2020-01-07 22:30 | 11.73 | 11.73
2020-01-07 23:00 | 10.94 | 10.94
2020-01-07 23:30 | 9.74 | 9.74
2020-01-08 | 8.75 | 8.74
2020-01-08 00:30 | 8.05 | 8.05
2020-01-08 01:00 | 7.61 | 7.6
2020-01-08 01:30 | 7.24 | 7.22
2020-01-08 02:00 | 6.82 | 6.8
2020-01-08 02:30 | 6.58 | 6.56
2020-01-08 03:00 | 6.43 | 6.4
2020-01-08 03:30 | 6.38 | 6.35
2020-01-08 04:00 | 6.25 | 6.22
2020-01-08 04:30 | 6.27 | 6.23
2020-01-08 05:00 | 6.3 | 6.25
2020-01-08 05:30 | 6.24 | 6.16
2020-01-08 06:00 | 6.14 | 6.04
2020-01-08 06:30 | 6.06 | 5.99
2020-01-08 07:00 | 5.62 | 5.55
2020-01-08 07:30 | 5.45 | 5.41
2020-01-08 08:00 | 4.93 | 4.9
2020-01-08 08:30 | 5.85 | 5.83
2020-01-08 09:00 | 5.76 | 5.74
2020-01-08 09:30 | 5.87 | 5.84
2020-01-08 10:00 | 5.57 | 5.54
2020-01-08 10:30 | 6.3 | 6.27
2020-01-08 11:00 | 6.69 | 6.66
2020-01-08 11:30 | 7.24 | 7.19
2020-01-08 12:00 | 8.56 | 8.51
2020-01-08 12:30 | 9.1 | 9.04
2020-01-08 13:00 | 10.03 | 9.95
2020-01-08 13:30 | 11.04 | 10.95
2020-01-08 14:00 | 12.02 | 11.91
2020-01-08 14:30 | 12.97 | 12.86
2020-01-08 15:00 | 13.91 | 13.79
2020-01-08 15:30 | 15.03 | 14.92
2020-01-08 16:00 | 16.28 | 16.18
2020-01-08 16:30 | 16.87 | 16.78
2020-01-08 17:00 | 18.03 | 17.95
2020-01-08 17:30 | 18.86 | 18.79
2020-01-08 18:00 | 18.98 | 18.92
2020-01-08 18:30 | 18.95 | 18.9
2020-01-08 19:00 | 18.63 | 18.58
2020-01-08 19:30 | 17.99 | 17.94
2020-01-08 20:00 | 17.71 | 17.66
2020-01-08 20:30 | 17.25 | 17.21
2020-01-08 21:00 | 15.96 | 15.93
2020-01-08 21:30 | 14.46 | 14.45
2020-01-08 22:00 | 13.36 | 13.35
2020-01-08 22:30 | 12.26 | 12.26
2020-01-08 23:00 | 11.14 | 11.14
2020-01-08 23:30 | 10.05 | 10.04
2020-01-09 | 8.88 | 8.88
2020-01-09 00:30 | 8.28 | 8.27
2020-01-09 01:00 | 7.94 | 7.93
2020-01-09 01:30 | 7.48 | 7.47
2020-01-09 02:00 | 7.03 | 7.01
2020-01-09 02:30 | 6.78 | 6.75
2020-01-09 03:00 | 6.53 | 6.51
2020-01-09 03:30 | 6.45 | 6.42
2020-01-09 04:00 | 6.43 | 6.39
2020-01-09 04:30 | 6.42 | 6.4
2020-01-09 05:00 | 6.36 | 6.32
2020-01-09 05:30 | 6.36 | 6.28
2020-01-09 06:00 | 6.23 | 6.15
2020-01-09 06:30 | 6.06 | 5.99
2020-01-09 07:00 | 5.77 | 5.71
2020-01-09 07:30 | 5.91 | 5.88
2020-01-09 08:00 | 5.96 | 5.95
2020-01-09 08:30 | 8.14 | 8.13
2020-01-09 09:00 | 7.18 | 7.18
2020-01-09 09:30 | 6.36 | 6.36
2020-01-09 10:00 | 6.05 | 6.03
2020-01-09 10:30 | 6.4 | 6.36
2020-01-09 11:00 | 7.02 | 6.97
2020-01-09 11:30 | 7.88 | 7.81
2020-01-09 12:00 | 8.83 | 8.75
2020-01-09 12:30 | 9.86 | 9.76
2020-01-09 13:00 | 10.62 | 10.51
2020-01-09 13:30 | 11.4 | 11.29
2020-01-09 14:00 | 12.58 | 12.46
2020-01-09 14:30 | 14.8 | 14.71
2020-01-09 15:00 | 14.21 | 14.1
2020-01-09 15:30 | 14.88 | 14.77
2020-01-09 16:00 | 16.24 | 16.15
2020-01-09 16:30 | 17.82 | 17.73
2020-01-09 17:00 | 17.84 | 17.76
2020-01-09 17:30 | 17.66 | 17.59
2020-01-09 18:00 | 17.4 | 17.35
2020-01-09 18:30 | 17.54 | 17.5
2020-01-09 19:00 | 17.42 | 17.38
2020-01-09 19:30 | 17.06 | 17.01
2020-01-09 20:00 | 16.94 | 16.9
2020-01-09 20:30 | 16.46 | 16.43
2020-01-09 21:00 | 15.52 | 15.49
2020-01-09 21:30 | 14.34 | 14.33
2020-01-09 22:00 | 13.15 | 13.15
2020-01-09 22:30 | 12.26 | 12.25
2020-01-09 23:00 | 11.54 | 11.53
2020-01-09 23:30 | 10.1 | 10.1
2020-01-10 | 9.14 | 9.14
2020-01-10 00:30 | 8.52 | 8.51
2020-01-10 01:00 | 8.13 | 8.12
2020-01-10 01:30 | 7.76 | 7.75
2020-01-10 02:00 | 7.32 | 7.31
2020-01-10 02:30 | 7.16 | 7.15
2020-01-10 03:00 | 7.01 | 6.99
2020-01-10 03:30 | 6.84 | 6.82
2020-01-10 04:00 | 6.75 | 6.73
2020-01-10 04:30 | 6.62 | 6.59
2020-01-10 05:00 | 6.62 | 6.59
2020-01-10 05:30 | 6.64 | 6.58
2020-01-10 06:00 | 6.99 | 6.94
2020-01-10 06:30 | 6.29 | 6.24
2020-01-10 07:00 | 6.06 | 6.03
2020-01-10 07:30 | 6.69 | 6.68
2020-01-10 08:00 | 7.6 | 7.59
2020-01-10 08:30 | 7.99 | 7.99
2020-01-10 09:00 | 7.14 | 7.14
2020-01-10 09:30 | 7.22 | 7.21
2020-01-10 10:00 | 6.95 | 6.94
2020-01-10 10:30 | 6.96 | 6.94
2020-01-10 11:00 | 6.48 | 6.45
2020-01-10 11:30 | 6.69 | 6.64
2020-01-10 12:00 | 7.25 | 7.19
2020-01-10 12:30 | 8.32 | 8.25
2020-01-10 13:00 | 9.17 | 9.09
2020-01-10 13:30 | 10.09 | 10
2020-01-10 14:00 | 10.97 | 10.87
2020-01-10 14:30 | 11.82 | 11.73
2020-01-10 15:00 | 12.74 | 12.65
2020-01-10 15:30 | 14.74 | 14.65
2020-01-10 16:00 | 14.46 | 14.37
2020-01-10 16:30 | 16.07 | 15.99
2020-01-10 17:00 | 16.54 | 16.45
2020-01-10 17:30 | 17.61 | 17.54
2020-01-10 18:00 | 17.58 | 17.52
2020-01-10 18:30 | 17.28 | 17.24
2020-01-10 19:00 | 17.04 | 17.02
2020-01-10 19:30 | 16.98 | 16.93
2020-01-10 20:00 | 16.93 | 16.89
2020-01-10 20:30 | 16.22 | 16.18
2020-01-10 21:00 | 15.27 | 15.25
2020-01-10 21:30 | 14.28 | 14.26
2020-01-10 22:00 | 13.41 | 13.41
2020-01-10 22:30 | 12.64 | 12.64
2020-01-10 23:00 | 12.01 | 12.01
2020-01-10 23:30 | 10.93 | 10.92
2020-01-11 | 9.73 | 9.73
2020-01-11 00:30 | 8.95 | 8.94
2020-01-11 01:00 | 8.62 | 8.61
2020-01-11 01:30 | 8.11 | 8.1
2020-01-11 02:00 | 7.77 | 7.76
2020-01-11 02:30 | 7.39 | 7.38
2020-01-11 03:00 | 7.26 | 7.26
2020-01-11 03:30 | 7.01 | 7
2020-01-11 04:00 | 6.92 | 6.91
2020-01-11 04:30 | 6.81 | 6.79
2020-01-11 05:00 | 6.64 | 6.61
2020-01-11 05:30 | 6.36 | 6.3
2020-01-11 06:00 | 6.12 | 6.05
2020-01-11 06:30 | 6.06 | 6
2020-01-11 07:00 | 5.94 | 5.9
2020-01-11 07:30 | 6.12 | 6.1
2020-01-11 08:00 | 6.03 | 6.01
2020-01-11 08:30 | 6.58 | 6.57
2020-01-11 09:00 | 7.63 | 7.61
2020-01-11 09:30 | 8.43 | 8.41
2020-01-11 10:00 | 8.48 | 8.45
2020-01-11 10:30 | 8.91 | 8.87
2020-01-11 11:00 | 10 | 9.94
2020-01-11 11:30 | 11.81 | 11.74
2020-01-11 12:00 | 14.49 | 14.42
2020-01-11 12:30 | 15.09 | 15.02
2020-01-11 13:00 | 15.38 | 15.3
2020-01-11 13:30 | 14.78 | 14.67
2020-01-11 14:00 | 16.58 | 16.47
2020-01-11 14:30 | 17.87 | 17.76
2020-01-11 15:00 | 17.84 | 17.73
2020-01-11 15:30 | 17.38 | 17.28
2020-01-11 16:00 | 19.15 | 19.06
2020-01-11 16:30 | 18.4 | 18.33
2020-01-11 17:00 | 18.49 | 18.42
2020-01-11 17:30 | 18.27 | 18.21
2020-01-11 18:00 | 17.97 | 17.92
2020-01-11 18:30 | 17.6 | 17.56
2020-01-11 19:00 | 16.97 | 16.93
2020-01-11 19:30 | 16.53 | 16.48
2020-01-11 20:00 | 16.34 | 16.3
2020-01-11 20:30 | 15.67 | 15.64
2020-01-11 21:00 | 14.92 | 14.9
2020-01-11 21:30 | 13.86 | 13.85
2020-01-11 22:00 | 12.76 | 12.75
2020-01-11 22:30 | 12.21 | 12.2
2020-01-11 23:00 | 11.64 | 11.63
2020-01-11 23:30 | 10.58 | 10.57
2020-01-12 | 9.59 | 9.58
2020-01-12 00:30 | 8.88 | 8.87
2020-01-12 01:00 | 8.52 | 8.52
2020-01-12 01:30 | 7.98 | 7.98
2020-01-12 02:00 | 7.57 | 7.56
2020-01-12 02:30 | 7.29 | 7.28
2020-01-12 03:00 | 7.19 | 7.18
2020-01-12 03:30 | 7.05 | 7.03
2020-01-12 04:00 | 6.91 | 6.89
2020-01-12 04:30 | 6.88 | 6.86
2020-01-12 05:00 | 6.79 | 6.78
2020-01-12 05:30 | 6.58 | 6.54
2020-01-12 06:00 | 6.45 | 6.38
2020-01-12 06:30 | 6.69 | 6.63
2020-01-12 07:00 | 6.62 | 6.57
2020-01-12 07:30 | 6.58 | 6.53
2020-01-12 08:00 | 7.16 | 7.13
2020-01-12 08:30 | 6.2 | 6.18
2020-01-12 09:00 | 6.15 | 6.14
2020-01-12 09:30 | 5.72 | 5.71
2020-01-12 10:00 | 6.13 | 6.11
2020-01-12 10:30 | 7.55 | 7.53
2020-01-12 11:00 | 8.76 | 8.74
2020-01-12 11:30 | 10.74 | 10.72
2020-01-12 12:00 | 11.46 | 11.45
2020-01-12 12:30 | 11.16 | 11.15
2020-01-12 13:00 | 10.45 | 10.43
2020-01-12 13:30 | 10.8 | 10.79
2020-01-12 14:00 | 11.56 | 11.55
2020-01-12 14:30 | 12.04 | 12.02
2020-01-12 15:00 | 10.92 | 10.9
2020-01-12 15:30 | 10.83 | 10.82
2020-01-12 16:00 | 11.3 | 11.29
2020-01-12 16:30 | 11.89 | 11.88
2020-01-12 17:00 | 11.53 | 11.53
2020-01-12 17:30 | 12.08 | 12.07
2020-01-12 18:00 | 13.27 | 13.26
2020-01-12 18:30 | 13.45 | 13.45
2020-01-12 19:00 | 13.56 | 13.56
2020-01-12 19:30 | 13.23 | 13.22
2020-01-12 20:00 | 13 | 13
2020-01-12 20:30 | 12.49 | 12.49
2020-01-12 21:00 | 11.68 | 11.68
2020-01-12 21:30 | 10.97 | 10.96
2020-01-12 22:00 | 10.21 | 10.2
2020-01-12 22:30 | 9.81 | 9.8
2020-01-12 23:00 | 9.38 | 9.36
2020-01-12 23:30 | 8.47 | 8.45
2020-01-13 | 7.75 | 7.72
2020-01-13 00:30 | 7.2 | 7.17
2020-01-13 01:00 | 6.89 | 6.85
2020-01-13 01:30 | 6.57 | 6.53
2020-01-13 02:00 | 6.3 | 6.26
2020-01-13 02:30 | 6.11 | 6.06
2020-01-13 03:00 | 6.11 | 6.07
2020-01-13 03:30 | 5.99 | 5.94
2020-01-13 04:00 | 5.97 | 5.92
2020-01-13 04:30 | 6.18 | 6.13
2020-01-13 05:00 | 6.56 | 6.52
2020-01-13 05:30 | 6.54 | 6.46
2020-01-13 06:00 | 6.08 | 5.99
2020-01-13 06:30 | 6.45 | 6.38
2020-01-13 07:00 | 6.31 | 6.24
2020-01-13 07:30 | 6.08 | 6.03
2020-01-13 08:00 | 5.13 | 5.08
2020-01-13 08:30 | 4.6 | 4.58
2020-01-13 09:00 | 5.61 | 5.6
2020-01-13 09:30 | 4.05 | 4.05
2020-01-13 10:00 | 5.29 | 5.28
2020-01-13 10:30 | 6.34 | 6.33
2020-01-13 11:00 | 7.26 | 7.26
2020-01-13 11:30 | 7.71 | 7.71
2020-01-13 12:00 | 7.06 | 7.06
2020-01-13 12:30 | 6.62 | 6.61
2020-01-13 13:00 | 7.12 | 7.11
2020-01-13 13:30 | 7.29 | 7.29
2020-01-13 14:00 | 8.54 | 8.53
2020-01-13 14:30 | 9.39 | 9.38
2020-01-13 15:00 | 10.41 | 10.4
2020-01-13 15:30 | 11.24 | 11.24
2020-01-13 16:00 | 10.73 | 10.72
2020-01-13 16:30 | 10.64 | 10.64
2020-01-13 17:00 | 11.78 | 11.78
2020-01-13 17:30 | 12.73 | 12.73
2020-01-13 18:00 | 13.13 | 13.13
2020-01-13 18:30 | 13.43 | 13.43
2020-01-13 19:00 | 13.97 | 13.97
2020-01-13 19:30 | 14.15 | 14.15
2020-01-13 20:00 | 14.08 | 14.08
2020-01-13 20:30 | 13.59 | 13.59
2020-01-13 21:00 | 12.59 | 12.59
2020-01-13 21:30 | 11.48 | 11.47
2020-01-13 22:00 | 10.45 | 10.45
2020-01-13 22:30 | 9.96 | 9.95
2020-01-13 23:00 | 9.43 | 9.42
2020-01-13 23:30 | 8.4 | 8.37
2020-01-14 | 7.62 | 7.59
2020-01-14 00:30 | 6.98 | 6.94
2020-01-14 01:00 | 6.71 | 6.67
2020-01-14 01:30 | 6.28 | 6.22
2020-01-14 02:00 | 6 | 5.94
2020-01-14 02:30 | 5.74 | 5.67
2020-01-14 03:00 | 5.65 | 5.58
2020-01-14 03:30 | 5.7 | 5.63
2020-01-14 04:00 | 5.71 | 5.65
2020-01-14 04:30 | 6.06 | 6
2020-01-14 05:00 | 6.36 | 6.3
2020-01-14 05:30 | 6.34 | 6.25
2020-01-14 06:00 | 6.24 | 6.14
2020-01-14 06:30 | 5.7 | 5.59
2020-01-14 07:00 | 5.22 | 5.12
2020-01-14 07:30 | 6.38 | 6.31
2020-01-14 08:00 | 6.46 | 6.4
2020-01-14 08:30 | 6.53 | 6.49
2020-01-14 09:00 | 7.01 | 6.98
2020-01-14 09:30 | 5.5 | 5.49
2020-01-14 10:00 | 5.84 | 5.83
2020-01-14 10:30 | 4.33 | 4.33
2020-01-14 11:00 | 4.5 | 4.5
2020-01-14 11:30 | 6.53 | 6.52
2020-01-14 12:00 | 6.96 | 6.95
2020-01-14 12:30 | 8.41 | 8.4
2020-01-14 13:00 | 8.87 | 8.86
2020-01-14 13:30 | 9.89 | 9.88
2020-01-14 14:00 | 10.12 | 10.11
2020-01-14 14:30 | 10.95 | 10.93
2020-01-14 15:00 | 9.33 | 9.29
2020-01-14 15:30 | 12.12 | 12.09
2020-01-14 16:00 | 12.6 | 12.56
2020-01-14 16:30 | 14.61 | 14.57
2020-01-14 17:00 | 14.73 | 14.71
2020-01-14 17:30 | 14.16 | 14.15
2020-01-14 18:00 | 14.79 | 14.78
2020-01-14 18:30 | 14.99 | 14.99
2020-01-14 19:00 | 14.99 | 14.98
2020-01-14 19:30 | 14.96 | 14.95
2020-01-14 20:00 | 15.07 | 15.06
2020-01-14 20:30 | 14.27 | 14.26
2020-01-14 21:00 | 13.12 | 13.11
2020-01-14 21:30 | 12.2 | 12.2
2020-01-14 22:00 | 11.33 | 11.32
2020-01-14 22:30 | 10.53 | 10.53
2020-01-14 23:00 | 10.04 | 10.04
2020-01-14 23:30 | 8.88 | 8.87
2020-01-15 | 7.97 | 7.95
2020-01-15 00:30 | 7.42 | 7.39
2020-01-15 01:00 | 7.14 | 7.11
2020-01-15 01:30 | 6.69 | 6.66
2020-01-15 02:00 | 6.39 | 6.35
2020-01-15 02:30 | 6.18 | 6.14
2020-01-15 03:00 | 6.1 | 6.05
2020-01-15 03:30 | 6.15 | 6.1
2020-01-15 04:00 | 6.13 | 6.08
2020-01-15 04:30 | 6.2 | 6.15
2020-01-15 05:00 | 6.12 | 6.07
2020-01-15 05:30 | 6.1 | 6
2020-01-15 06:00 | 6.33 | 6.23
2020-01-15 06:30 | 6.04 | 5.95
2020-01-15 07:00 | 5.37 | 5.29
2020-01-15 07:30 | 5.54 | 5.49
2020-01-15 08:00 | 4.74 | 4.7
2020-01-15 08:30 | 5.13 | 5.12
2020-01-15 09:00 | 6.97 | 6.95
2020-01-15 09:30 | 7.76 | 7.75
2020-01-15 10:00 | 8.4 | 8.39
2020-01-15 10:30 | 5.1 | 5.08
2020-01-15 11:00 | 4.83 | 4.81
2020-01-15 11:30 | 6.48 | 6.46
2020-01-15 12:00 | 4.4 | 4.37
2020-01-15 12:30 | 4.65 | 4.61
2020-01-15 13:00 | 6.42 | 6.39
2020-01-15 13:30 | 7.05 | 7.01
2020-01-15 14:00 | 8.36 | 8.33
2020-01-15 14:30 | 8.79 | 8.77
2020-01-15 15:00 | 9.32 | 9.29
2020-01-15 15:30 | 10.06 | 10.03
2020-01-15 16:00 | 11.67 | 11.63
2020-01-15 16:30 | 13.91 | 13.88
2020-01-15 17:00 | 14.5 | 14.48
2020-01-15 17:30 | 15.2 | 15.18
2020-01-15 18:00 | 15.26 | 15.25
2020-01-15 18:30 | 15.39 | 15.37
2020-01-15 19:00 | 15.72 | 15.71
2020-01-15 19:30 | 16.05 | 16.02
2020-01-15 20:00 | 15.83 | 15.8
2020-01-15 20:30 | 15.33 | 15.31
2020-01-15 21:00 | 14.23 | 14.22
2020-01-15 21:30 | 13.13 | 13.13
2020-01-15 22:00 | 12 | 11.99
2020-01-15 22:30 | 11.35 | 11.35
2020-01-15 23:00 | 10.68 | 10.68
2020-01-15 23:30 | 9.6 | 9.59
2020-01-16 | 8.61 | 8.6
2020-01-16 00:30 | 8 | 7.99
2020-01-16 01:00 | 7.67 | 7.66
2020-01-16 01:30 | 7.29 | 7.27
2020-01-16 02:00 | 6.9 | 6.87
2020-01-16 02:30 | 6.66 | 6.64
2020-01-16 03:00 | 6.65 | 6.62
2020-01-16 03:30 | 6.61 | 6.58
2020-01-16 04:00 | 6.49 | 6.46
2020-01-16 04:30 | 6.54 | 6.51
2020-01-16 05:00 | 6.55 | 6.52
2020-01-16 05:30 | 6.55 | 6.48
2020-01-16 06:00 | 6.45 | 6.37
2020-01-16 06:30 | 6.23 | 6.16
2020-01-16 07:00 | 5.92 | 5.86
2020-01-16 07:30 | 6.49 | 6.45
2020-01-16 08:00 | 5.32 | 5.29
2020-01-16 08:30 | 5.01 | 4.99
2020-01-16 09:00 | 6.45 | 6.43
2020-01-16 09:30 | 6.74 | 6.72
2020-01-16 10:00 | 8.81 | 8.79
2020-01-16 10:30 | 9.73 | 9.73
2020-01-16 11:00 | 7.47 | 7.46
2020-01-16 11:30 | 6.16 | 6.14
2020-01-16 12:00 | 6.07 | 6.06
2020-01-16 12:30 | 7.37 | 7.36
2020-01-16 13:00 | 8.22 | 8.21
2020-01-16 13:30 | 9.06 | 9.06
2020-01-16 14:00 | 8.37 | 8.36
2020-01-16 14:30 | 8.94 | 8.94
2020-01-16 15:00 | 8.92 | 8.91
2020-01-16 15:30 | 9.82 | 9.82
2020-01-16 16:00 | 10.1 | 10.1
2020-01-16 16:30 | 10.34 | 10.34
2020-01-16 17:00 | 11.72 | 11.71
2020-01-16 17:30 | 12.38 | 12.38
2020-01-16 18:00 | 13.55 | 13.54
2020-01-16 18:30 | 14.26 | 14.26
2020-01-16 19:00 | 14.25 | 14.24
2020-01-16 19:30 | 14.37 | 14.37
2020-01-16 20:00 | 14.65 | 14.65
2020-01-16 20:30 | 14.47 | 14.46
2020-01-16 21:00 | 13.58 | 13.57
2020-01-16 21:30 | 12.34 | 12.34
2020-01-16 22:00 | 11.45 | 11.45
2020-01-16 22:30 | 10.92 | 10.91
2020-01-16 23:00 | 10.46 | 10.45
2020-01-16 23:30 | 9.39 | 9.39
2020-01-17 | 8.44 | 8.43
2020-01-17 00:30 | 7.77 | 7.76
2020-01-17 01:00 | 7.47 | 7.45
2020-01-17 01:30 | 7.08 | 7.05
2020-01-17 02:00 | 6.7 | 6.67
2020-01-17 02:30 | 6.55 | 6.51
2020-01-17 03:00 | 6.46 | 6.42
2020-01-17 03:30 | 6.39 | 6.36
2020-01-17 04:00 | 6.4 | 6.36
2020-01-17 04:30 | 6.63 | 6.6
2020-01-17 05:00 | 6.85 | 6.82
2020-01-17 05:30 | 6.86 | 6.79
2020-01-17 06:00 | 6.75 | 6.68
2020-01-17 06:30 | 6.82 | 6.76
2020-01-17 07:00 | 7.15 | 7.1
2020-01-17 07:30 | 5.91 | 5.87
2020-01-17 08:00 | 5.29 | 5.26
2020-01-17 08:30 | 5.03 | 5.02
2020-01-17 09:00 | 6.28 | 6.27
2020-01-17 09:30 | 6.57 | 6.55
2020-01-17 10:00 | 5.58 | 5.56
2020-01-17 10:30 | 5.64 | 5.62
2020-01-17 11:00 | 6.55 | 6.53
2020-01-17 11:30 | 9.95 | 9.93
2020-01-17 12:00 | 8.93 | 8.89
2020-01-17 12:30 | 7.48 | 7.45
2020-01-17 13:00 | 8.63 | 8.58
2020-01-17 13:30 | 9.21 | 9.15
2020-01-17 14:00 | 9.41 | 9.35
2020-01-17 14:30 | 11.09 | 11.04
2020-01-17 15:00 | 13.19 | 13.15
2020-01-17 15:30 | 12.49 | 12.46
2020-01-17 16:00 | 12.8 | 12.78
2020-01-17 16:30 | 12.39 | 12.38
2020-01-17 17:00 | 12.73 | 12.71
2020-01-17 17:30 | 12.82 | 12.8
2020-01-17 18:00 | 13.56 | 13.55
2020-01-17 18:30 | 13.87 | 13.87
2020-01-17 19:00 | 14.39 | 14.37
2020-01-17 19:30 | 14.47 | 14.46
2020-01-17 20:00 | 14.74 | 14.73
2020-01-17 20:30 | 14.23 | 14.22
2020-01-17 21:00 | 13.35 | 13.34
2020-01-17 21:30 | 12.1 | 12.09
2020-01-17 22:00 | 11.54 | 11.53
2020-01-17 22:30 | 11.12 | 11.12
2020-01-17 23:00 | 10.63 | 10.63
2020-01-17 23:30 | 9.64 | 9.64
2020-01-18 | 8.78 | 8.77
2020-01-18 00:30 | 7.94 | 7.92
2020-01-18 01:00 | 7.48 | 7.47
2020-01-18 01:30 | 7.08 | 7.05
2020-01-18 02:00 | 6.75 | 6.72
2020-01-18 02:30 | 6.49 | 6.46
2020-01-18 03:00 | 6.3 | 6.27
2020-01-18 03:30 | 6.25 | 6.2
2020-01-18 04:00 | 6.16 | 6.13
2020-01-18 04:30 | 6.13 | 6.09
2020-01-18 05:00 | 6.15 | 6.1
2020-01-18 05:30 | 6.03 | 5.98
2020-01-18 06:00 | 6.16 | 6.08
2020-01-18 06:30 | 6.25 | 6.17
2020-01-18 07:00 | 6.12 | 6.01
2020-01-18 07:30 | 6.14 | 6.05
2020-01-18 08:00 | 6.03 | 5.96
2020-01-18 08:30 | 5.88 | 5.81
2020-01-18 09:00 | 6.99 | 6.96
2020-01-18 09:30 | 5.76 | 5.74
2020-01-18 10:00 | 4.74 | 4.72
2020-01-18 10:30 | 5.48 | 5.46
2020-01-18 11:00 | 4.83 | 4.8
2020-01-18 11:30 | 4.98 | 4.95
2020-01-18 12:00 | 7.07 | 7.05
2020-01-18 12:30 | 8.17 | 8.15
2020-01-18 13:00 | 7.89 | 7.86
2020-01-18 13:30 | 6.97 | 6.94
2020-01-18 14:00 | 7.61 | 7.58
2020-01-18 14:30 | 8.7 | 8.68
2020-01-18 15:00 | 9.72 | 9.7
2020-01-18 15:30 | 11.24 | 11.23
2020-01-18 16:00 | 11.19 | 11.18
2020-01-18 16:30 | 11.97 | 11.96
2020-01-18 17:00 | 11.11 | 11.1
2020-01-18 17:30 | 12.71 | 12.7
2020-01-18 18:00 | 13.56 | 13.55
2020-01-18 18:30 | 13.42 | 13.41
2020-01-18 19:00 | 14.04 | 14.04
2020-01-18 19:30 | 14.1 | 14.09
2020-01-18 20:00 | 13.95 | 13.94
2020-01-18 20:30 | 13.73 | 13.73
2020-01-18 21:00 | 12.99 | 12.99
2020-01-18 21:30 | 12.17 | 12.17
2020-01-18 22:00 | 11.43 | 11.43
2020-01-18 22:30 | 10.93 | 10.92
2020-01-18 23:00 | 10.53 | 10.53
2020-01-18 23:30 | 9.46 | 9.45
2020-01-19 | 8.46 | 8.44
2020-01-19 00:30 | 7.79 | 7.77
2020-01-19 01:00 | 7.54 | 7.52
2020-01-19 01:30 | 7.17 | 7.15
2020-01-19 02:00 | 6.79 | 6.76
2020-01-19 02:30 | 6.5 | 6.47
2020-01-19 03:00 | 6.43 | 6.39
2020-01-19 03:30 | 6.58 | 6.55
2020-01-19 04:00 | 6.21 | 6.17
2020-01-19 04:30 | 6.22 | 6.18
2020-01-19 05:00 | 6.13 | 6.09
2020-01-19 05:30 | 6.02 | 5.94
2020-01-19 06:00 | 6.05 | 5.97
2020-01-19 06:30 | 5.95 | 5.86
2020-01-19 07:00 | 6.08 | 5.99
2020-01-19 07:30 | 5.36 | 5.29
2020-01-19 08:00 | 5.41 | 5.37
2020-01-19 08:30 | 5.15 | 5.13
2020-01-19 09:00 | 5.95 | 5.94
2020-01-19 09:30 | 6.47 | 6.46
2020-01-19 10:00 | 6.67 | 6.65
2020-01-19 10:30 | 9.57 | 9.55
2020-01-19 11:00 | 10.63 | 10.62
2020-01-19 11:30 | 12.56 | 12.55
2020-01-19 12:00 | 11.16 | 11.15
2020-01-19 12:30 | 6.31 | 6.28
2020-01-19 13:00 | 7.27 | 7.23
2020-01-19 13:30 | 8.19 | 8.13
2020-01-19 14:00 | 9.14 | 9.08
2020-01-19 14:30 | 12.12 | 12.07
2020-01-19 15:00 | 13.91 | 13.88
2020-01-19 15:30 | 11.94 | 11.9
2020-01-19 16:00 | 13.99 | 13.96
2020-01-19 16:30 | 15.55 | 15.53
2020-01-19 17:00 | 15.43 | 15.41
2020-01-19 17:30 | 15.12 | 15.1
2020-01-19 18:00 | 15.85 | 15.83
2020-01-19 18:30 | 16.33 | 16.32
2020-01-19 19:00 | 16.34 | 16.33
2020-01-19 19:30 | 16.46 | 16.43
2020-01-19 20:00 | 16.58 | 16.55
2020-01-19 20:30 | 15.9 | 15.88
2020-01-19 21:00 | 14.96 | 14.94
2020-01-19 21:30 | 13.95 | 13.94
2020-01-19 22:00 | 12.98 | 12.97
2020-01-19 22:30 | 12.07 | 12.07
2020-01-19 23:00 | 11.62 | 11.62
2020-01-19 23:30 | 10.44 | 10.43
2020-01-20 | 9.54 | 9.53
2020-01-20 00:30 | 8.79 | 8.79
2020-01-20 01:00 | 8.49 | 8.48
2020-01-20 01:30 | 7.99 | 7.99
2020-01-20 02:00 | 7.71 | 7.7
2020-01-20 02:30 | 7.48 | 7.48
2020-01-20 03:00 | 7.48 | 7.47
2020-01-20 03:30 | 7.32 | 7.31
2020-01-20 04:00 | 7.33 | 7.32
2020-01-20 04:30 | 7.45 | 7.43
2020-01-20 05:00 | 7.52 | 7.5
2020-01-20 05:30 | 7.48 | 7.44
2020-01-20 06:00 | 7.58 | 7.54
2020-01-20 06:30 | 7.69 | 7.67
2020-01-20 07:00 | 7.58 | 7.57
2020-01-20 07:30 | 7.58 | 7.57
2020-01-20 08:00 | 7.31 | 7.31
2020-01-20 08:30 | 8.01 | 8
2020-01-20 09:00 | 8.08 | 8.07
2020-01-20 09:30 | 9.57 | 9.54
2020-01-20 10:00 | 9.75 | 9.71
2020-01-20 10:30 | 11.08 | 11.04
2020-01-20 11:00 | 12.19 | 12.13
2020-01-20 11:30 | 11.82 | 11.74
2020-01-20 12:00 | 11.74 | 11.64
2020-01-20 12:30 | 12.69 | 12.58
2020-01-20 13:00 | 13.94 | 13.8
2020-01-20 13:30 | 15.57 | 15.41
2020-01-20 14:00 | 17.09 | 16.94
2020-01-20 14:30 | 19.99 | 19.87
2020-01-20 15:00 | 18.98 | 18.87
2020-01-20 15:30 | 18.14 | 18.06
2020-01-20 16:00 | 13.91 | 13.87
2020-01-20 16:30 | 14.2 | 14.14
2020-01-20 17:00 | 15.71 | 15.66
2020-01-20 17:30 | 17.03 | 16.99
2020-01-20 18:00 | 17.38 | 17.34
2020-01-20 18:30 | 17.82 | 17.79
2020-01-20 19:00 | 18.53 | 18.49
2020-01-20 19:30 | 18.84 | 18.78
2020-01-20 20:00 | 18.77 | 18.71
2020-01-20 20:30 | 17.86 | 17.81
2020-01-20 21:00 | 16.59 | 16.55
2020-01-20 21:30 | 14.99 | 14.97
2020-01-20 22:00 | 13.65 | 13.64
2020-01-20 22:30 | 12.81 | 12.8
2020-01-20 23:00 | 12.04 | 12.04
2020-01-20 23:30 | 10.88 | 10.87
2020-01-21 | 9.85 | 9.85
2020-01-21 00:30 | 9.18 | 9.18
2020-01-21 01:00 | 8.82 | 8.82
2020-01-21 01:30 | 8.37 | 8.37
2020-01-21 02:00 | 8.04 | 8.04
2020-01-21 02:30 | 7.72 | 7.72
2020-01-21 03:00 | 7.57 | 7.56
2020-01-21 03:30 | 7.45 | 7.44
2020-01-21 04:00 | 7.56 | 7.55
2020-01-21 04:30 | 7.54 | 7.53
2020-01-21 05:00 | 7.95 | 7.95
2020-01-21 05:30 | 8.12 | 8.11
2020-01-21 06:00 | 7.98 | 7.95
2020-01-21 06:30 | 7.91 | 7.88
2020-01-21 07:00 | 7.51 | 7.48
2020-01-21 07:30 | 7.35 | 7.33
2020-01-21 08:00 | 7.63 | 7.62
2020-01-21 08:30 | 5.54 | 5.54
2020-01-21 09:00 | 5.79 | 5.78
2020-01-21 09:30 | 6.12 | 6.1
2020-01-21 10:00 | 6.83 | 6.8
2020-01-21 10:30 | 7.56 | 7.51
2020-01-21 11:00 | 8.55 | 8.49
2020-01-21 11:30 | 10.52 | 10.44
2020-01-21 12:00 | 11.02 | 10.92
2020-01-21 12:30 | 12.49 | 12.37
2020-01-21 13:00 | 13.58 | 13.44
2020-01-21 13:30 | 15.06 | 14.92
2020-01-21 14:00 | 16 | 15.84
2020-01-21 14:30 | 17.09 | 16.91
2020-01-21 15:00 | 18.38 | 18.2
2020-01-21 15:30 | 19.6 | 19.42
2020-01-21 16:00 | 20.65 | 20.47
2020-01-21 16:30 | 21.8 | 21.65
2020-01-21 17:00 | 21.51 | 21.38
2020-01-21 17:30 | 22.43 | 22.3
2020-01-21 18:00 | 23.2 | 23.08
2020-01-21 18:30 | 23.13 | 23.02
2020-01-21 19:00 | 22.55 | 22.44
2020-01-21 19:30 | 22.31 | 22.18
2020-01-21 20:00 | 21.75 | 21.65
2020-01-21 20:30 | 20.39 | 20.31
2020-01-21 21:00 | 18.75 | 18.69
2020-01-21 21:30 | 17.22 | 17.17
2020-01-21 22:00 | 15.72 | 15.69
2020-01-21 22:30 | 14.42 | 14.4
2020-01-21 23:00 | 13.48 | 13.47
2020-01-21 23:30 | 12.02 | 12.02
2020-01-22 | 10.61 | 10.61
2020-01-22 00:30 | 9.88 | 9.88
2020-01-22 01:00 | 9.42 | 9.42
2020-01-22 01:30 | 9.01 | 9.01
2020-01-22 02:00 | 8.44 | 8.44
2020-01-22 02:30 | 8.1 | 8.09
2020-01-22 03:00 | 7.88 | 7.87
2020-01-22 03:30 | 7.74 | 7.73
2020-01-22 04:00 | 7.48 | 7.47
2020-01-22 04:30 | 7.59 | 7.58
2020-01-22 05:00 | 7.91 | 7.9
2020-01-22 05:30 | 7.75 | 7.72
2020-01-22 06:00 | 7.73 | 7.7
2020-01-22 06:30 | 7.63 | 7.61
2020-01-22 07:00 | 7.42 | 7.41
2020-01-22 07:30 | 7.54 | 7.53
2020-01-22 08:00 | 7.39 | 7.39
2020-01-22 08:30 | 7.52 | 7.51
2020-01-22 09:00 | 8.28 | 8.26
2020-01-22 09:30 | 7.95 | 7.92
2020-01-22 10:00 | 8.61 | 8.55
2020-01-22 10:30 | 9.27 | 9.2
2020-01-22 11:00 | 10.2 | 10.12
2020-01-22 11:30 | 11.39 | 11.28
2020-01-22 12:00 | 12.53 | 12.4
2020-01-22 12:30 | 13.5 | 13.35
2020-01-22 13:00 | 14.34 | 14.19
2020-01-22 13:30 | 16.38 | 16.22
2020-01-22 14:00 | 16.25 | 16.09
2020-01-22 14:30 | 17.52 | 17.35
2020-01-22 15:00 | 18.21 | 18.02
2020-01-22 15:30 | 20.86 | 20.69
2020-01-22 16:00 | 23.21 | 23.04
2020-01-22 16:30 | 22.75 | 22.6
2020-01-22 17:00 | 22.74 | 22.6
2020-01-22 17:30 | 23.07 | 22.93
2020-01-22 18:00 | 23.08 | 22.96
2020-01-22 18:30 | 22.85 | 22.74
2020-01-22 19:00 | 22.99 | 22.86
2020-01-22 19:30 | 22.96 | 22.81
2020-01-22 20:00 | 22.73 | 22.6
2020-01-22 20:30 | 21.53 | 21.42
2020-01-22 21:00 | 20.14 | 20.05
2020-01-22 21:30 | 18.13 | 18.07
2020-01-22 22:00 | 16.48 | 16.43
2020-01-22 22:30 | 15.09 | 15.06
2020-01-22 23:00 | 13.79 | 13.78
2020-01-22 23:30 | 12.47 | 12.46
2020-01-23 | 11.5 | 11.49
2020-01-23 00:30 | 10.78 | 10.78
2020-01-23 01:00 | 10.4 | 10.39
2020-01-23 01:30 | 9.97 | 9.97
2020-01-23 02:00 | 9.59 | 9.59
2020-01-23 02:30 | 9.27 | 9.26
2020-01-23 03:00 | 9 | 9
2020-01-23 03:30 | 8.79 | 8.78
2020-01-23 04:00 | 8.55 | 8.55
2020-01-23 04:30 | 8.54 | 8.53
2020-01-23 05:00 | 8.49 | 8.49
2020-01-23 05:30 | 8.59 | 8.58
2020-01-23 06:00 | 8.55 | 8.54
2020-01-23 06:30 | 8.4 | 8.4
2020-01-23 07:00 | 8.59 | 8.58
2020-01-23 07:30 | 9.4 | 9.39
2020-01-23 08:00 | 9.65 | 9.64
2020-01-23 08:30 | 9.98 | 9.97
2020-01-23 09:00 | 10.37 | 10.36
2020-01-23 09:30 | 10.4 | 10.38
2020-01-23 10:00 | 9.02 | 8.99
2020-01-23 10:30 | 10.6 | 10.57
2020-01-23 11:00 | 10.33 | 10.27
2020-01-23 11:30 | 12.08 | 12.01
2020-01-23 12:00 | 14.25 | 14.17
2020-01-23 12:30 | 11.99 | 11.9
2020-01-23 13:00 | 10.8 | 10.7
2020-01-23 13:30 | 11.34 | 11.24
2020-01-23 14:00 | 12.17 | 12.06
2020-01-23 14:30 | 13.69 | 13.57
2020-01-23 15:00 | 15.03 | 14.9
2020-01-23 15:30 | 17.21 | 17.09
2020-01-23 16:00 | 17.7 | 17.58
2020-01-23 16:30 | 18.3 | 18.18
2020-01-23 17:00 | 19.6 | 19.48
2020-01-23 17:30 | 20.14 | 20.03
2020-01-23 18:00 | 20.87 | 20.77
2020-01-23 18:30 | 21.06 | 20.96
2020-01-23 19:00 | 21.16 | 21.06
2020-01-23 19:30 | 21.18 | 21.07
2020-01-23 20:00 | 21.06 | 20.95
2020-01-23 20:30 | 20.09 | 20
2020-01-23 21:00 | 18.45 | 18.39
2020-01-23 21:30 | 16.97 | 16.93
2020-01-23 22:00 | 15.56 | 15.53
2020-01-23 22:30 | 14.47 | 14.46
2020-01-23 23:00 | 13.64 | 13.63
2020-01-23 23:30 | 12.21 | 12.21
2020-01-24 | 11.16 | 11.15
2020-01-24 00:30 | 10.28 | 10.28
2020-01-24 01:00 | 9.84 | 9.84
2020-01-24 01:30 | 9.34 | 9.34
2020-01-24 02:00 | 8.78 | 8.78
2020-01-24 02:30 | 8.65 | 8.65
2020-01-24 03:00 | 8.5 | 8.49
2020-01-24 03:30 | 8.46 | 8.45
2020-01-24 04:00 | 8.3 | 8.3
2020-01-24 04:30 | 8.24 | 8.24
2020-01-24 05:00 | 8.14 | 8.13
2020-01-24 05:30 | 8.03 | 8.02
2020-01-24 06:00 | 8.13 | 8.11
2020-01-24 06:30 | 8.28 | 8.27
2020-01-24 07:00 | 8.67 | 8.66
2020-01-24 07:30 | 8.33 | 8.33
2020-01-24 08:00 | 8.47 | 8.46
2020-01-24 08:30 | 8.97 | 8.96
2020-01-24 09:00 | 11.48 | 11.46
2020-01-24 09:30 | 11.32 | 11.29
2020-01-24 10:00 | 12.5 | 12.45
2020-01-24 10:30 | 12.37 | 12.31
2020-01-24 11:00 | 12.9 | 12.83
2020-01-24 11:30 | 12.86 | 12.78
2020-01-24 12:00 | 13.8 | 13.71
2020-01-24 12:30 | 14.65 | 14.55
2020-01-24 13:00 | 16.33 | 16.21
2020-01-24 13:30 | 17.44 | 17.29
2020-01-24 14:00 | 18.39 | 18.23
2020-01-24 14:30 | 19.02 | 18.86
2020-01-24 15:00 | 18.38 | 18.21
2020-01-24 15:30 | 20.28 | 20.11
2020-01-24 16:00 | 20.64 | 20.47
2020-01-24 16:30 | 21.16 | 20.98
2020-01-24 17:00 | 22.28 | 22.12
2020-01-24 17:30 | 22.19 | 22.04
2020-01-24 18:00 | 22.23 | 22.1
2020-01-24 18:30 | 21.6 | 21.5
2020-01-24 19:00 | 21.49 | 21.39
2020-01-24 19:30 | 21.41 | 21.28
2020-01-24 20:00 | 20.91 | 20.79
2020-01-24 20:30 | 19.99 | 19.89
2020-01-24 21:00 | 18.73 | 18.66
2020-01-24 21:30 | 17.23 | 17.17
2020-01-24 22:00 | 15.85 | 15.81
2020-01-24 22:30 | 14.89 | 14.86
2020-01-24 23:00 | 14.21 | 14.2
2020-01-24 23:30 | 12.91 | 12.9
2020-01-25 | 11.76 | 11.75
2020-01-25 00:30 | 10.8 | 10.8
2020-01-25 01:00 | 10.24 | 10.23
2020-01-25 01:30 | 9.69 | 9.69
2020-01-25 02:00 | 9.28 | 9.27
2020-01-25 02:30 | 9.07 | 9.06
2020-01-25 03:00 | 8.93 | 8.93
2020-01-25 03:30 | 8.63 | 8.62
2020-01-25 04:00 | 8.15 | 8.14
2020-01-25 04:30 | 8.04 | 8.03
2020-01-25 05:00 | 7.94 | 7.93
2020-01-25 05:30 | 7.54 | 7.52
2020-01-25 06:00 | 7.27 | 7.24
2020-01-25 06:30 | 6.84 | 6.82
2020-01-25 07:00 | 7.37 | 7.36
2020-01-25 07:30 | 7.24 | 7.22
2020-01-25 08:00 | 8.33 | 8.32
2020-01-25 08:30 | 8.45 | 8.44
2020-01-25 09:00 | 8.76 | 8.74
2020-01-25 09:30 | 9.68 | 9.64
2020-01-25 10:00 | 10.65 | 10.6
2020-01-25 10:30 | 11.85 | 11.79
2020-01-25 11:00 | 12.42 | 12.32
2020-01-25 11:30 | 14.28 | 14.18
2020-01-25 12:00 | 13.38 | 13.26
2020-01-25 12:30 | 14.26 | 14.14
2020-01-25 13:00 | 18.38 | 18.27
2020-01-25 13:30 | 19.25 | 19.15
2020-01-25 14:00 | 18.62 | 18.54
2020-01-25 14:30 | 17.44 | 17.38
2020-01-25 15:00 | 16.56 | 16.5
2020-01-25 15:30 | 15.85 | 15.81
2020-01-25 16:00 | 15.55 | 15.5
2020-01-25 16:30 | 15.85 | 15.81
2020-01-25 17:00 | 15.84 | 15.81
2020-01-25 17:30 | 15.45 | 15.43
2020-01-25 18:00 | 15.7 | 15.68
2020-01-25 18:30 | 15.71 | 15.69
2020-01-25 19:00 | 15.92 | 15.89
2020-01-25 19:30 | 15.93 | 15.9
2020-01-25 20:00 | 15.88 | 15.85
2020-01-25 20:30 | 15.34 | 15.32
2020-01-25 21:00 | 14.48 | 14.46
2020-01-25 21:30 | 13.62 | 13.61
2020-01-25 22:00 | 12.88 | 12.87
2020-01-25 22:30 | 12.27 | 12.26
2020-01-25 23:00 | 11.78 | 11.77
2020-01-25 23:30 | 10.69 | 10.68
2020-01-26 | 9.79 | 9.78
2020-01-26 00:30 | 9.08 | 9.07
2020-01-26 01:00 | 8.53 | 8.53
2020-01-26 01:30 | 8.08 | 8.07
2020-01-26 02:00 | 7.73 | 7.72
2020-01-26 02:30 | 7.44 | 7.42
2020-01-26 03:00 | 7.27 | 7.26
2020-01-26 03:30 | 7.13 | 7.12
2020-01-26 04:00 | 7.1 | 7.08
2020-01-26 04:30 | 6.98 | 6.96
2020-01-26 05:00 | 6.95 | 6.93
2020-01-26 05:30 | 6.53 | 6.48
2020-01-26 06:00 | 6.49 | 6.42
2020-01-26 06:30 | 6.28 | 6.21
2020-01-26 07:00 | 5.98 | 5.93
2020-01-26 07:30 | 6.09 | 6.07
2020-01-26 08:00 | 6.61 | 6.6
2020-01-26 08:30 | 8.76 | 8.75
2020-01-26 09:00 | 8.62 | 8.61
2020-01-26 09:30 | 7.93 | 7.91
2020-01-26 10:00 | 7.97 | 7.95
2020-01-26 10:30 | 9.17 | 9.14
2020-01-26 11:00 | 10.62 | 10.6
2020-01-26 11:30 | 9.21 | 9.17
2020-01-26 12:00 | 10.2 | 10.15
2020-01-26 12:30 | 11.31 | 11.26
2020-01-26 13:00 | 11.67 | 11.61
2020-01-26 13:30 | 10.35 | 10.26
2020-01-26 14:00 | 11.1 | 11.02
2020-01-26 14:30 | 12.95 | 12.88
2020-01-26 15:00 | 13.64 | 13.57
2020-01-26 15:30 | 14.59 | 14.52
2020-01-26 16:00 | 14.67 | 14.61
2020-01-26 16:30 | 15.27 | 15.22
2020-01-26 17:00 | 16.1 | 16.05
2020-01-26 17:30 | 16.59 | 16.55
2020-01-26 18:00 | 16.96 | 16.92
2020-01-26 18:30 | 17.01 | 16.98
2020-01-26 19:00 | 16.7 | 16.67
2020-01-26 19:30 | 16.75 | 16.71
2020-01-26 20:00 | 16.51 | 16.48
2020-01-26 20:30 | 16.02 | 15.99
2020-01-26 21:00 | 15.02 | 15
2020-01-26 21:30 | 14.18 | 14.17
2020-01-26 22:00 | 13.28 | 13.27
2020-01-26 22:30 | 12.68 | 12.68
2020-01-26 23:00 | 12.1 | 12.1
2020-01-26 23:30 | 10.89 | 10.89
2020-01-27 | 9.84 | 9.84
2020-01-27 00:30 | 9.18 | 9.18
2020-01-27 01:00 | 8.72 | 8.72
2020-01-27 01:30 | 8.17 | 8.16
2020-01-27 02:00 | 7.74 | 7.73
2020-01-27 02:30 | 7.43 | 7.41
2020-01-27 03:00 | 7.2 | 7.19
2020-01-27 03:30 | 7.16 | 7.14
2020-01-27 04:00 | 7.17 | 7.15
2020-01-27 04:30 | 6.97 | 6.95
2020-01-27 05:00 | 6.82 | 6.79
2020-01-27 05:30 | 6.63 | 6.58
2020-01-27 06:00 | 6.38 | 6.31
2020-01-27 06:30 | 6.11 | 6.04
2020-01-27 07:00 | 5.96 | 5.91
2020-01-27 07:30 | 6.21 | 6.19
2020-01-27 08:00 | 5.79 | 5.77
2020-01-27 08:30 | 6.49 | 6.48
2020-01-27 09:00 | 7.01 | 6.99
2020-01-27 09:30 | 7.21 | 7.18
2020-01-27 10:00 | 8.63 | 8.6
2020-01-27 10:30 | 9.97 | 9.95
2020-01-27 11:00 | 9.71 | 9.67
2020-01-27 11:30 | 10.62 | 10.57
2020-01-27 12:00 | 11.46 | 11.4
2020-01-27 12:30 | 11.64 | 11.57
2020-01-27 13:00 | 12.02 | 11.95
2020-01-27 13:30 | 12.32 | 12.24
2020-01-27 14:00 | 13.09 | 13.01
2020-01-27 14:30 | 12.89 | 12.81
2020-01-27 15:00 | 13.76 | 13.67
2020-01-27 15:30 | 14.97 | 14.89
2020-01-27 16:00 | 16.34 | 16.26
2020-01-27 16:30 | 17.78 | 17.7
2020-01-27 17:00 | 18.72 | 18.65
2020-01-27 17:30 | 19.17 | 19.1
2020-01-27 18:00 | 19.52 | 19.46
2020-01-27 18:30 | 19.1 | 19.05
2020-01-27 19:00 | 18.74 | 18.7
2020-01-27 19:30 | 18.37 | 18.32
2020-01-27 20:00 | 17.81 | 17.77
2020-01-27 20:30 | 16.95 | 16.92
2020-01-27 21:00 | 15.66 | 15.64
2020-01-27 21:30 | 14.59 | 14.58
2020-01-27 22:00 | 13.13 | 13.13
2020-01-27 22:30 | 12.06 | 12.06
2020-01-27 23:00 | 11.44 | 11.44
2020-01-27 23:30 | 10.27 | 10.27
2020-01-28 | 9.24 | 9.24
2020-01-28 00:30 | 8.58 | 8.57
2020-01-28 01:00 | 8.18 | 8.17
2020-01-28 01:30 | 7.82 | 7.81
2020-01-28 02:00 | 7.4 | 7.39
2020-01-28 02:30 | 7.19 | 7.18
2020-01-28 03:00 | 7.17 | 7.15
2020-01-28 03:30 | 7.05 | 7.03
2020-01-28 04:00 | 6.96 | 6.94
2020-01-28 04:30 | 6.93 | 6.9
2020-01-28 05:00 | 7.06 | 7.04
2020-01-28 05:30 | 7.04 | 7.01
2020-01-28 06:00 | 6.94 | 6.88
2020-01-28 06:30 | 7.55 | 7.51
2020-01-28 07:00 | 7.95 | 7.93
2020-01-28 07:30 | 8.25 | 8.24
2020-01-28 08:00 | 9.32 | 9.32
2020-01-28 08:30 | 9.7 | 9.7
2020-01-28 09:00 | 8.24 | 8.24
2020-01-28 09:30 | 7.69 | 7.68
2020-01-28 10:00 | 9.69 | 9.68
2020-01-28 10:30 | 6.88 | 6.86
2020-01-28 11:00 | 7.79 | 7.77
2020-01-28 11:30 | 9.25 | 9.22
2020-01-28 12:00 | 8.15 | 8.1
2020-01-28 12:30 | 8.32 | 8.26
2020-01-28 13:00 | 10.83 | 10.78
2020-01-28 13:30 | 13.18 | 13.13
2020-01-28 14:00 | 10.73 | 10.66
2020-01-28 14:30 | 11.13 | 11.04
2020-01-28 15:00 | 11.87 | 11.78
2020-01-28 15:30 | 13.74 | 13.65
2020-01-28 16:00 | 15.21 | 15.12
2020-01-28 16:30 | 16.85 | 16.76
2020-01-28 17:00 | 18.39 | 18.3
2020-01-28 17:30 | 19.61 | 19.52
2020-01-28 18:00 | 20.13 | 20.06
2020-01-28 18:30 | 20.24 | 20.17
2020-01-28 19:00 | 20.23 | 20.16
2020-01-28 19:30 | 20.26 | 20.17
2020-01-28 20:00 | 19.62 | 19.54
2020-01-28 20:30 | 18.15 | 18.1
2020-01-28 21:00 | 16.76 | 16.72
2020-01-28 21:30 | 15.37 | 15.35
2020-01-28 22:00 | 14.13 | 14.12
2020-01-28 22:30 | 13.03 | 13.02
2020-01-28 23:00 | 11.95 | 11.95
2020-01-28 23:30 | 10.52 | 10.52
2020-01-29 | 9.41 | 9.4
2020-01-29 00:30 | 8.64 | 8.64
2020-01-29 01:00 | 8.2 | 8.19
2020-01-29 01:30 | 7.76 | 7.75
2020-01-29 02:00 | 7.31 | 7.3
2020-01-29 02:30 | 7.12 | 7.11
2020-01-29 03:00 | 7.08 | 7.07
2020-01-29 03:30 | 7.11 | 7.1
2020-01-29 04:00 | 7.07 | 7.06
2020-01-29 04:30 | 7.14 | 7.13
2020-01-29 05:00 | 7.27 | 7.26
2020-01-29 05:30 | 7.44 | 7.41
2020-01-29 06:00 | 7.89 | 7.85
2020-01-29 06:30 | 8.09 | 8.07
2020-01-29 07:00 | 8.19 | 8.18
2020-01-29 07:30 | 8.23 | 8.22
2020-01-29 08:00 | 8.04 | 8.04
2020-01-29 08:30 | 7.83 | 7.82
2020-01-29 09:00 | 8.14 | 8.12
2020-01-29 09:30 | 8.17 | 8.14
2020-01-29 10:00 | 7.98 | 7.93
2020-01-29 10:30 | 8.39 | 8.33
2020-01-29 11:00 | 8.69 | 8.6
2020-01-29 11:30 | 9.6 | 9.5
2020-01-29 12:00 | 10.41 | 10.3
2020-01-29 12:30 | 11.94 | 11.82
2020-01-29 13:00 | 13.02 | 12.87
2020-01-29 13:30 | 14.11 | 13.95
2020-01-29 14:00 | 16.29 | 16.15
2020-01-29 14:30 | 16.76 | 16.62
2020-01-29 15:00 | 16.42 | 16.26
2020-01-29 15:30 | 17.38 | 17.21
2020-01-29 16:00 | 19.62 | 19.44
2020-01-29 16:30 | 21.96 | 21.79
2020-01-29 17:00 | 22.74 | 22.57
2020-01-29 17:30 | 23.76 | 23.59
2020-01-29 18:00 | 24.42 | 24.26
2020-01-29 18:30 | 24.21 | 24.07
2020-01-29 19:00 | 23.94 | 23.81
2020-01-29 19:30 | 23.22 | 23.07
2020-01-29 20:00 | 22.52 | 22.39
2020-01-29 20:30 | 21.11 | 21
2020-01-29 21:00 | 19.55 | 19.47
2020-01-29 21:30 | 17.84 | 17.78
2020-01-29 22:00 | 16.2 | 16.17
2020-01-29 22:30 | 14.83 | 14.81
2020-01-29 23:00 | 13.7 | 13.68
2020-01-29 23:30 | 12.12 | 12.11
2020-01-30 | 10.98 | 10.97
2020-01-30 00:30 | 10.16 | 10.16
2020-01-30 01:00 | 9.73 | 9.73
2020-01-30 01:30 | 9.23 | 9.23
2020-01-30 02:00 | 8.86 | 8.86
2020-01-30 02:30 | 8.54 | 8.54
2020-01-30 03:00 | 8.26 | 8.25
2020-01-30 03:30 | 8.1 | 8.1
2020-01-30 04:00 | 7.98 | 7.98
2020-01-30 04:30 | 7.84 | 7.84
2020-01-30 05:00 | 7.81 | 7.81
2020-01-30 05:30 | 7.76 | 7.74
2020-01-30 06:00 | 7.81 | 7.78
2020-01-30 06:30 | 8.26 | 8.24
2020-01-30 07:00 | 8.76 | 8.75
2020-01-30 07:30 | 9.58 | 9.58
2020-01-30 08:00 | 9.21 | 9.21
2020-01-30 08:30 | 9.63 | 9.63
2020-01-30 09:00 | 9.19 | 9.18
2020-01-30 09:30 | 9.4 | 9.38
2020-01-30 10:00 | 10.32 | 10.29
2020-01-30 10:30 | 10.81 | 10.77
2020-01-30 11:00 | 11.3 | 11.25
2020-01-30 11:30 | 11.29 | 11.23
2020-01-30 12:00 | 11.19 | 11.13
2020-01-30 12:30 | 12.1 | 12.04
2020-01-30 13:00 | 12.7 | 12.63
2020-01-30 13:30 | 12.35 | 12.26
2020-01-30 14:00 | 12.47 | 12.36
2020-01-30 14:30 | 12.53 | 12.41
2020-01-30 15:00 | 14.22 | 14.09
2020-01-30 15:30 | 16.33 | 16.21
2020-01-30 16:00 | 18.64 | 18.53
2020-01-30 16:30 | 18.96 | 18.84
2020-01-30 17:00 | 19.48 | 19.36
2020-01-30 17:30 | 20.77 | 20.65
2020-01-30 18:00 | 21.08 | 20.97
2020-01-30 18:30 | 21.33 | 21.23
2020-01-30 19:00 | 21.04 | 20.95
2020-01-30 19:30 | 21.09 | 20.99
2020-01-30 20:00 | 20.21 | 20.12
2020-01-30 20:30 | 18.97 | 18.9
2020-01-30 21:00 | 17.68 | 17.63
2020-01-30 21:30 | 16.19 | 16.16
2020-01-30 22:00 | 14.78 | 14.76
2020-01-30 22:30 | 13.59 | 13.59
2020-01-30 23:00 | 12.34 | 12.33
2020-01-30 23:30 | 10.92 | 10.92
2020-01-31 | 9.62 | 9.61
2020-01-31 00:30 | 8.88 | 8.87
2020-01-31 01:00 | 8.49 | 8.48
2020-01-31 01:30 | 7.96 | 7.96
2020-01-31 02:00 | 7.53 | 7.52
2020-01-31 02:30 | 7.24 | 7.22
2020-01-31 03:00 | 7.15 | 7.13
2020-01-31 03:30 | 7.08 | 7.06
2020-01-31 04:00 | 6.93 | 6.91
2020-01-31 04:30 | 6.9 | 6.88
2020-01-31 05:00 | 6.87 | 6.84
2020-01-31 05:30 | 6.95 | 6.91
2020-01-31 06:00 | 7.34 | 7.29
2020-01-31 06:30 | 7.68 | 7.65
2020-01-31 07:00 | 7.82 | 7.79
2020-01-31 07:30 | 8.6 | 8.59
2020-01-31 08:00 | 7.84 | 7.84
2020-01-31 08:30 | 8.04 | 8.03
2020-01-31 09:00 | 8.11 | 8.1
2020-01-31 09:30 | 8.19 | 8.18
2020-01-31 10:00 | 6.88 | 6.87
2020-01-31 10:30 | 9.09 | 9.08
2020-01-31 11:00 | 10.33 | 10.31
2020-01-31 11:30 | 10.09 | 10.07
2020-01-31 12:00 | 8.65 | 8.62
2020-01-31 12:30 | 9.99 | 9.96
2020-01-31 13:00 | 10.71 | 10.66
2020-01-31 13:30 | 11.65 | 11.6
2020-01-31 14:00 | 11.7 | 11.64
2020-01-31 14:30 | 11.71 | 11.64
2020-01-31 15:00 | 13.49 | 13.43
2020-01-31 15:30 | 13.51 | 13.44
2020-01-31 16:00 | 14.35 | 14.28
2020-01-31 16:30 | 15.43 | 15.36
2020-01-31 17:00 | 17.04 | 16.96
2020-01-31 17:30 | 18.03 | 17.95
2020-01-31 18:00 | 18.59 | 18.53
2020-01-31 18:30 | 18.5 | 18.45
2020-01-31 19:00 | 18.3 | 18.25
2020-01-31 19:30 | 18.17 | 18.1
2020-01-31 20:00 | 17.76 | 17.71
2020-01-31 20:30 | 16.93 | 16.89
2020-01-31 21:00 | 15.89 | 15.86
2020-01-31 21:30 | 14.52 | 14.5
2020-01-31 22:00 | 13.38 | 13.37
2020-01-31 22:30 | 12.61 | 12.6
2020-01-31 23:00 | 11.9 | 11.9
2020-01-31 23:30 | 10.63 | 10.63
2020-02-01 | 9.58 | 9.58
2020-02-01 00:30 | 8.89 | 8.89
2020-02-01 01:00 | 8.56 | 8.56
2020-02-01 01:30 | 8.21 | 8.21
2020-02-01 02:00 | 7.9 | 7.89
2020-02-01 02:30 | 7.64 | 7.63
2020-02-01 03:00 | 7.38 | 7.37
2020-02-01 03:30 | 7.31 | 7.3
2020-02-01 04:00 | 7.16 | 7.15
2020-02-01 04:30 | 7.08 | 7.06
2020-02-01 05:00 | 6.93 | 6.91
2020-02-01 05:30 | 6.73 | 6.69
2020-02-01 06:00 | 6.61 | 6.55
2020-02-01 06:30 | 6.12 | 6.06
2020-02-01 07:00 | 6.05 | 6.01
2020-02-01 07:30 | 6.81 | 6.79
2020-02-01 08:00 | 7.16 | 7.14
2020-02-01 08:30 | 8.13 | 8.12
2020-02-01 09:00 | 7.73 | 7.71
2020-02-01 09:30 | 8.04 | 8.02
2020-02-01 10:00 | 8.34 | 8.32
2020-02-01 10:30 | 8.73 | 8.7
2020-02-01 11:00 | 9.64 | 9.59
2020-02-01 11:30 | 10.36 | 10.29
2020-02-01 12:00 | 11.35 | 11.27
2020-02-01 12:30 | 11.97 | 11.88
2020-02-01 13:00 | 13.81 | 13.72
2020-02-01 13:30 | 15.74 | 15.64
2020-02-01 14:00 | 15.9 | 15.78
2020-02-01 14:30 | 16.23 | 16.1
2020-02-01 15:00 | 15.94 | 15.8
2020-02-01 15:30 | 16.89 | 16.76
2020-02-01 16:00 | 17.8 | 17.67
2020-02-01 16:30 | 18.89 | 18.77
2020-02-01 17:00 | 19.77 | 19.65
2020-02-01 17:30 | 20.21 | 20.11
2020-02-01 18:00 | 20.32 | 20.22
2020-02-01 18:30 | 19.76 | 19.68
2020-02-01 19:00 | 19.01 | 18.95
2020-02-01 19:30 | 18.66 | 18.58
2020-02-01 20:00 | 18.37 | 18.31
2020-02-01 20:30 | 17.27 | 17.23
2020-02-01 21:00 | 16.3 | 16.26
2020-02-01 21:30 | 15.27 | 15.24
2020-02-01 22:00 | 14.06 | 14.05
2020-02-01 22:30 | 13.35 | 13.35
2020-02-01 23:00 | 12.64 | 12.64
2020-02-01 23:30 | 11.17 | 11.17
2020-02-02 | 10.09 | 10.08
2020-02-02 00:30 | 9.33 | 9.33
2020-02-02 01:00 | 8.77 | 8.76
2020-02-02 01:30 | 8.28 | 8.27
2020-02-02 02:00 | 7.88 | 7.87
2020-02-02 02:30 | 7.5 | 7.48
2020-02-02 03:00 | 7.22 | 7.2
2020-02-02 03:30 | 7.08 | 7.06
2020-02-02 04:00 | 6.91 | 6.88
2020-02-02 04:30 | 6.71 | 6.69
2020-02-02 05:00 | 6.59 | 6.56
2020-02-02 05:30 | 6.28 | 6.21
2020-02-02 06:00 | 6.24 | 6.14
2020-02-02 06:30 | 6.05 | 5.97
2020-02-02 07:00 | 5.86 | 5.79
2020-02-02 07:30 | 5.88 | 5.84
2020-02-02 08:00 | 6 | 5.98
2020-02-02 08:30 | 6.23 | 6.22
2020-02-02 09:00 | 6.83 | 6.81
2020-02-02 09:30 | 7.49 | 7.46
2020-02-02 10:00 | 7.74 | 7.71
2020-02-02 10:30 | 8.33 | 8.28
2020-02-02 11:00 | 9.14 | 9.08
2020-02-02 11:30 | 10.14 | 10.06
2020-02-02 12:00 | 11.46 | 11.35
2020-02-02 12:30 | 12.55 | 12.44
2020-02-02 13:00 | 13.72 | 13.59
2020-02-02 13:30 | 14.71 | 14.57
2020-02-02 14:00 | 15.92 | 15.77
2020-02-02 14:30 | 17.06 | 16.9
2020-02-02 15:00 | 18.36 | 18.2
2020-02-02 15:30 | 19.44 | 19.29
2020-02-02 16:00 | 20.72 | 20.56
2020-02-02 16:30 | 21.98 | 21.83
2020-02-02 17:00 | 23.17 | 23.03
2020-02-02 17:30 | 24.09 | 23.94
2020-02-02 18:00 | 24.23 | 24.09
2020-02-02 18:30 | 23.53 | 23.42
2020-02-02 19:00 | 22.66 | 22.56
2020-02-02 19:30 | 22.3 | 22.19
2020-02-02 20:00 | 21.64 | 21.55
2020-02-02 20:30 | 20.35 | 20.27
2020-02-02 21:00 | 19.06 | 18.99
2020-02-02 21:30 | 17.21 | 17.17
2020-02-02 22:00 | 15.79 | 15.77
2020-02-02 22:30 | 14.49 | 14.47
2020-02-02 23:00 | 13.57 | 13.56
2020-02-02 23:30 | 11.97 | 11.96
2020-02-03 | 10.65 | 10.64
2020-02-03 00:30 | 9.75 | 9.75
2020-02-03 01:00 | 9.27 | 9.26
2020-02-03 01:30 | 8.71 | 8.71
2020-02-03 02:00 | 8.37 | 8.36
2020-02-03 02:30 | 7.99 | 7.98
2020-02-03 03:00 | 7.73 | 7.72
2020-02-03 03:30 | 7.65 | 7.64
2020-02-03 04:00 | 7.49 | 7.48
2020-02-03 04:30 | 7.48 | 7.47
2020-02-03 05:00 | 7.44 | 7.43
2020-02-03 05:30 | 7.52 | 7.5
2020-02-03 06:00 | 7.69 | 7.66
2020-02-03 06:30 | 8.1 | 8.08
2020-02-03 07:00 | 8.32 | 8.31
2020-02-03 07:30 | 8.24 | 8.23
2020-02-03 08:00 | 7.99 | 7.97
2020-02-03 08:30 | 7.56 | 7.55
2020-02-03 09:00 | 7.69 | 7.66
2020-02-03 09:30 | 8.15 | 8.11
2020-02-03 10:00 | 8.49 | 8.44
2020-02-03 10:30 | 9.19 | 9.12
2020-02-03 11:00 | 10.05 | 9.96
2020-02-03 11:30 | 11.05 | 10.94
2020-02-03 12:00 | 12.12 | 11.98
2020-02-03 12:30 | 13.24 | 13.08
2020-02-03 13:00 | 14.5 | 14.34
2020-02-03 13:30 | 16.01 | 15.84
2020-02-03 14:00 | 17.25 | 17.06
2020-02-03 14:30 | 18 | 17.81
2020-02-03 15:00 | 19.04 | 18.86
2020-02-03 15:30 | 20.57 | 20.37
2020-02-03 16:00 | 22.46 | 22.25
2020-02-03 16:30 | 23.89 | 23.68
2020-02-03 17:00 | 25.46 | 25.24
2020-02-03 17:30 | 26.73 | 26.52
2020-02-03 18:00 | 27.49 | 27.28
2020-02-03 18:30 | 27.01 | 26.84
2020-02-03 19:00 | 26.65 | 26.48
2020-02-03 19:30 | 26.42 | 26.23
2020-02-03 20:00 | 25.66 | 25.49
2020-02-03 20:30 | 23.11 | 22.98
2020-02-03 21:00 | 21.42 | 21.31
2020-02-03 21:30 | 19.93 | 19.84
2020-02-03 22:00 | 17.67 | 17.61
2020-02-03 22:30 | 15.17 | 15.14
2020-02-03 23:00 | 13.82 | 13.81
2020-02-03 23:30 | 12.51 | 12.49
2020-02-04 | 11.14 | 11.13
2020-02-04 00:30 | 10.3 | 10.29
2020-02-04 01:00 | 9.9 | 9.89
2020-02-04 01:30 | 9.27 | 9.26
2020-02-04 02:00 | 8.72 | 8.71
2020-02-04 02:30 | 8.42 | 8.42
2020-02-04 03:00 | 8.22 | 8.21
2020-02-04 03:30 | 8.16 | 8.16
2020-02-04 04:00 | 7.94 | 7.93
2020-02-04 04:30 | 7.97 | 7.97
2020-02-04 05:00 | 8.15 | 8.14
2020-02-04 05:30 | 8.35 | 8.34
2020-02-04 06:00 | 8.37 | 8.35
2020-02-04 06:30 | 8.71 | 8.7
2020-02-04 07:00 | 8.91 | 8.9
2020-02-04 07:30 | 9.61 | 9.61
2020-02-04 08:00 | 10 | 10
2020-02-04 08:30 | 9.64 | 9.64
2020-02-04 09:00 | 9.56 | 9.56
2020-02-04 09:30 | 9.33 | 9.33
2020-02-04 10:00 | 6.95 | 6.94
2020-02-04 10:30 | 8.56 | 8.55
2020-02-04 11:00 | 10.23 | 10.22
2020-02-04 11:30 | 10.04 | 10.04
2020-02-04 12:00 | 9.63 | 9.62
2020-02-04 12:30 | 9.42 | 9.42
2020-02-04 13:00 | 9.32 | 9.31
2020-02-04 13:30 | 9.15 | 9.14
2020-02-04 14:00 | 8.93 | 8.93
2020-02-04 14:30 | 8.03 | 8.02
2020-02-04 15:00 | 8.77 | 8.76
2020-02-04 15:30 | 9.98 | 9.98
2020-02-04 16:00 | 11.08 | 11.08
2020-02-04 16:30 | 10.89 | 10.89
2020-02-04 17:00 | 11.72 | 11.71
2020-02-04 17:30 | 12.34 | 12.34
2020-02-04 18:00 | 12.5 | 12.5
2020-02-04 18:30 | 13 | 12.99
2020-02-04 19:00 | 13.63 | 13.63
2020-02-04 19:30 | 13.4 | 13.4
2020-02-04 20:00 | 12.89 | 12.88
2020-02-04 20:30 | 12.45 | 12.45
2020-02-04 21:00 | 12.08 | 12.08
2020-02-04 21:30 | 11.24 | 11.23
2020-02-04 22:00 | 10.42 | 10.42
2020-02-04 22:30 | 9.42 | 9.41
2020-02-04 23:00 | 8.9 | 8.88
2020-02-04 23:30 | 7.95 | 7.91
2020-02-05 | 7.05 | 7.01
2020-02-05 00:30 | 6.45 | 6.4
2020-02-05 01:00 | 6.26 | 6.2
2020-02-05 01:30 | 6 | 5.94
2020-02-05 02:00 | 5.74 | 5.67
2020-02-05 02:30 | 5.62 | 5.55
2020-02-05 03:00 | 5.59 | 5.52
2020-02-05 03:30 | 5.54 | 5.46
2020-02-05 04:00 | 5.52 | 5.44
2020-02-05 04:30 | 5.68 | 5.61
2020-02-05 05:00 | 5.86 | 5.8
2020-02-05 05:30 | 6.14 | 6.07
2020-02-05 06:00 | 6.5 | 6.41
2020-02-05 06:30 | 7.16 | 7.08
2020-02-05 07:00 | 7.42 | 7.36
2020-02-05 07:30 | 7.81 | 7.77
2020-02-05 08:00 | 7.65 | 7.61
2020-02-05 08:30 | 7.81 | 7.78
2020-02-05 09:00 | 7.8 | 7.77
2020-02-05 09:30 | 7.9 | 7.88
2020-02-05 10:00 | 7.88 | 7.86
2020-02-05 10:30 | 7.04 | 7.02
2020-02-05 11:00 | 7.11 | 7.09
2020-02-05 11:30 | 5.87 | 5.85
2020-02-05 12:00 | 5.46 | 5.45
2020-02-05 12:30 | 7.82 | 7.81
2020-02-05 13:00 | 7.77 | 7.76
2020-02-05 13:30 | 8.24 | 8.23
2020-02-05 14:00 | 7.8 | 7.79
2020-02-05 14:30 | 7.54 | 7.52
2020-02-05 15:00 | 7.73 | 7.71
2020-02-05 15:30 | 7.66 | 7.64
2020-02-05 16:00 | 8.18 | 8.16
2020-02-05 16:30 | 8.61 | 8.59
2020-02-05 17:00 | 9.9 | 9.89
2020-02-05 17:30 | 10.93 | 10.92
2020-02-05 18:00 | 11.67 | 11.66
2020-02-05 18:30 | 11.97 | 11.97
2020-02-05 19:00 | 12.67 | 12.66
2020-02-05 19:30 | 12.72 | 12.72
2020-02-05 20:00 | 12.71 | 12.7
2020-02-05 20:30 | 12.4 | 12.4
2020-02-05 21:00 | 11.62 | 11.61
2020-02-05 21:30 | 10.59 | 10.58
2020-02-05 22:00 | 9.84 | 9.83
2020-02-05 22:30 | 8.87 | 8.84
2020-02-05 23:00 | 8.47 | 8.44
2020-02-05 23:30 | 7.59 | 7.54
2020-02-06 | 6.71 | 6.65
2020-02-06 00:30 | 6.16 | 6.08
2020-02-06 01:00 | 5.88 | 5.8
2020-02-06 01:30 | 5.52 | 5.43
2020-02-06 02:00 | 5.27 | 5.17
2020-02-06 02:30 | 5.31 | 5.21
2020-02-06 03:00 | 5.27 | 5.17
2020-02-06 03:30 | 5.34 | 5.25
2020-02-06 04:00 | 5.29 | 5.19
2020-02-06 04:30 | 5.39 | 5.3
2020-02-06 05:00 | 5.54 | 5.46
2020-02-06 05:30 | 6.13 | 6.06
2020-02-06 06:00 | 6.21 | 6.1
2020-02-06 06:30 | 6.67 | 6.57
2020-02-06 07:00 | 7.33 | 7.24
2020-02-06 07:30 | 7.77 | 7.7
2020-02-06 08:00 | 7.88 | 7.81
2020-02-06 08:30 | 7.18 | 7.12
2020-02-06 09:00 | 6.83 | 6.77
2020-02-06 09:30 | 7.66 | 7.61
2020-02-06 10:00 | 7.75 | 7.69
2020-02-06 10:30 | 6.98 | 6.92
2020-02-06 11:00 | 6 | 5.95
2020-02-06 11:30 | 6.44 | 6.4
2020-02-06 12:00 | 6.61 | 6.56
2020-02-06 12:30 | 5.53 | 5.48
2020-02-06 13:00 | 4.52 | 4.48
2020-02-06 13:30 | 5.04 | 5
2020-02-06 14:00 | 4.36 | 4.33
2020-02-06 14:30 | 7.73 | 7.7
2020-02-06 15:00 | 8 | 7.97
2020-02-06 15:30 | 8.08 | 8.04
2020-02-06 16:00 | 8.42 | 8.39
2020-02-06 16:30 | 9.11 | 9.08
2020-02-06 17:00 | 10.03 | 10
2020-02-06 17:30 | 10.68 | 10.66
2020-02-06 18:00 | 11.12 | 11.1
2020-02-06 18:30 | 11.32 | 11.3
2020-02-06 19:00 | 11.92 | 11.91
2020-02-06 19:30 | 11.87 | 11.86
2020-02-06 20:00 | 11.71 | 11.7
2020-02-06 20:30 | 11.36 | 11.35
2020-02-06 21:00 | 10.66 | 10.65
2020-02-06 21:30 | 9.87 | 9.85
2020-02-06 22:00 | 9.14 | 9.11
2020-02-06 22:30 | 8.76 | 8.73
2020-02-06 23:00 | 8.4 | 8.36
2020-02-06 23:30 | 7.47 | 7.41
2020-02-07 | 6.72 | 6.65
2020-02-07 00:30 | 6.12 | 6.04
2020-02-07 01:00 | 5.92 | 5.83
2020-02-07 01:30 | 5.67 | 5.58
2020-02-07 02:00 | 5.38 | 5.27
2020-02-07 02:30 | 5.35 | 5.25
2020-02-07 03:00 | 5.26 | 5.15
2020-02-07 03:30 | 5.32 | 5.22
2020-02-07 04:00 | 5.31 | 5.21
2020-02-07 04:30 | 5.5 | 5.4
2020-02-07 05:00 | 5.62 | 5.53
2020-02-07 05:30 | 5.97 | 5.89
2020-02-07 06:00 | 6.23 | 6.12
2020-02-07 06:30 | 6.94 | 6.85
2020-02-07 07:00 | 7.33 | 7.25
2020-02-07 07:30 | 7.67 | 7.61
2020-02-07 08:00 | 7.41 | 7.36
2020-02-07 08:30 | 6.4 | 6.34
2020-02-07 09:00 | 5.27 | 5.23
2020-02-07 09:30 | 4.71 | 4.68
2020-02-07 10:00 | 5.04 | 5.03
2020-02-07 10:30 | 6.01 | 6
2020-02-07 11:00 | 6.91 | 6.9
2020-02-07 11:30 | 5.97 | 5.96
2020-02-07 12:00 | 4.71 | 4.7
2020-02-07 12:30 | 7 | 6.99
2020-02-07 13:00 | 6.95 | 6.94
2020-02-07 13:30 | 6.91 | 6.9
2020-02-07 14:00 | 5.61 | 5.59
2020-02-07 14:30 | 5.81 | 5.79
2020-02-07 15:00 | 8.39 | 8.38
2020-02-07 15:30 | 8.72 | 8.71
2020-02-07 16:00 | 9.37 | 9.36
2020-02-07 16:30 | 10.61 | 10.6
2020-02-07 17:00 | 11.84 | 11.83
2020-02-07 17:30 | 11.58 | 11.58
2020-02-07 18:00 | 11.9 | 11.89
2020-02-07 18:30 | 12.24 | 12.23
2020-02-07 19:00 | 13.15 | 13.14
2020-02-07 19:30 | 13.43 | 13.43
2020-02-07 20:00 | 13.42 | 13.41
2020-02-07 20:30 | 12.81 | 12.8
2020-02-07 21:00 | 12.21 | 12.2
2020-02-07 21:30 | 11.42 | 11.41
2020-02-07 22:00 | 10.7 | 10.69
2020-02-07 22:30 | 10.15 | 10.14
2020-02-07 23:00 | 9.86 | 9.85
2020-02-07 23:30 | 8.92 | 8.91
2020-02-08 | 8.08 | 8.06
2020-02-08 00:30 | 7.43 | 7.41
2020-02-08 01:00 | 7.11 | 7.07
2020-02-08 01:30 | 6.75 | 6.71
2020-02-08 02:00 | 6.4 | 6.36
2020-02-08 02:30 | 6.28 | 6.23
2020-02-08 03:00 | 6.14 | 6.09
2020-02-08 03:30 | 6.04 | 5.98
2020-02-08 04:00 | 5.93 | 5.87
2020-02-08 04:30 | 5.95 | 5.9
2020-02-08 05:00 | 5.98 | 5.92
2020-02-08 05:30 | 5.9 | 5.83
2020-02-08 06:00 | 5.92 | 5.81
2020-02-08 06:30 | 6.15 | 6.05
2020-02-08 07:00 | 6.43 | 6.34
2020-02-08 07:30 | 6.31 | 6.22
2020-02-08 08:00 | 6.76 | 6.7
2020-02-08 08:30 | 7.03 | 6.99
2020-02-08 09:00 | 7.56 | 7.54
2020-02-08 09:30 | 8.47 | 8.46
2020-02-08 10:00 | 5.68 | 5.66
2020-02-08 10:30 | 5.26 | 5.24
2020-02-08 11:00 | 5.91 | 5.89
2020-02-08 11:30 | 6.06 | 6.03
2020-02-08 12:00 | 7.75 | 7.73
2020-02-08 12:30 | 10.12 | 10.11
2020-02-08 13:00 | 9.72 | 9.7
2020-02-08 13:30 | 9.22 | 9.2
2020-02-08 14:00 | 8.59 | 8.56
2020-02-08 14:30 | 11.03 | 11.01
2020-02-08 15:00 | 12.05 | 12.04
2020-02-08 15:30 | 11.43 | 11.41
2020-02-08 16:00 | 9.94 | 9.92
2020-02-08 16:30 | 11.35 | 11.34
2020-02-08 17:00 | 12.59 | 12.58
2020-02-08 17:30 | 12.96 | 12.95
2020-02-08 18:00 | 12.96 | 12.95
2020-02-08 18:30 | 13.09 | 13.08
2020-02-08 19:00 | 13.48 | 13.47
2020-02-08 19:30 | 13.24 | 13.23
2020-02-08 20:00 | 12.99 | 12.98
2020-02-08 20:30 | 12.52 | 12.52
2020-02-08 21:00 | 11.97 | 11.97
2020-02-08 21:30 | 11.36 | 11.35
2020-02-08 22:00 | 10.85 | 10.84
2020-02-08 22:30 | 10.43 | 10.43
2020-02-08 23:00 | 9.98 | 9.96
2020-02-08 23:30 | 9.11 | 9.1
2020-02-09 | 8.33 | 8.31
2020-02-09 00:30 | 7.76 | 7.74
2020-02-09 01:00 | 7.42 | 7.39
2020-02-09 01:30 | 6.94 | 6.9
2020-02-09 02:00 | 6.51 | 6.47
2020-02-09 02:30 | 6.4 | 6.35
2020-02-09 03:00 | 6.25 | 6.2
2020-02-09 03:30 | 6.16 | 6.11
2020-02-09 04:00 | 6.06 | 6
2020-02-09 04:30 | 6.05 | 6
2020-02-09 05:00 | 6.01 | 5.95
2020-02-09 05:30 | 6.01 | 5.95
2020-02-09 06:00 | 5.92 | 5.81
2020-02-09 06:30 | 6.08 | 5.98
2020-02-09 07:00 | 6.14 | 6.04
2020-02-09 07:30 | 6.32 | 6.24
2020-02-09 08:00 | 7.01 | 6.96
2020-02-09 08:30 | 6.46 | 6.41
2020-02-09 09:00 | 7.14 | 7.11
2020-02-09 09:30 | 9.03 | 9.02
2020-02-09 10:00 | 10.33 | 10.32
2020-02-09 10:30 | 11.24 | 11.24
2020-02-09 11:00 | 10.57 | 10.57
2020-02-09 11:30 | 10.07 | 10.06
2020-02-09 12:00 | 6.75 | 6.73
2020-02-09 12:30 | 5.86 | 5.84
2020-02-09 13:00 | 5.61 | 5.58
2020-02-09 13:30 | 8.66 | 8.64
2020-02-09 14:00 | 9.18 | 9.16
2020-02-09 14:30 | 9.1 | 9.08
2020-02-09 15:00 | 13.19 | 13.18
2020-02-09 15:30 | 13 | 12.99
2020-02-09 16:00 | 10.42 | 10.41
2020-02-09 16:30 | 12.2 | 12.19
2020-02-09 17:00 | 13.38 | 13.38
2020-02-09 17:30 | 13.38 | 13.37
2020-02-09 18:00 | 13.66 | 13.66
2020-02-09 18:30 | 14.19 | 14.18
2020-02-09 19:00 | 14.76 | 14.75
2020-02-09 19:30 | 14.89 | 14.88
2020-02-09 20:00 | 14.49 | 14.48
2020-02-09 20:30 | 13.85 | 13.84
2020-02-09 21:00 | 12.93 | 12.93
2020-02-09 21:30 | 11.99 | 11.99
2020-02-09 22:00 | 11.04 | 11.04
2020-02-09 22:30 | 10.45 | 10.44
2020-02-09 23:00 | 9.71 | 9.7
2020-02-09 23:30 | 8.83 | 8.81
2020-02-10 | 8.09 | 8.06
2020-02-10 00:30 | 7.47 | 7.44
2020-02-10 01:00 | 7.08 | 7.04
2020-02-10 01:30 | 6.79 | 6.75
2020-02-10 02:00 | 6.54 | 6.5
2020-02-10 02:30 | 6.39 | 6.35
2020-02-10 03:00 | 6.3 | 6.25
2020-02-10 03:30 | 6.19 | 6.14
2020-02-10 04:00 | 6.05 | 6
2020-02-10 04:30 | 6.15 | 6.1
2020-02-10 05:00 | 6.3 | 6.25
2020-02-10 05:30 | 6.64 | 6.59
2020-02-10 06:00 | 7.06 | 7
2020-02-10 06:30 | 7.14 | 7.08
2020-02-10 07:00 | 7.03 | 6.99
2020-02-10 07:30 | 6.87 | 6.85
2020-02-10 08:00 | 6.41 | 6.4
2020-02-10 08:30 | 5.83 | 5.82
2020-02-10 09:00 | 6.18 | 6.17
2020-02-10 09:30 | 5.99 | 5.98
2020-02-10 10:00 | 5.75 | 5.74
2020-02-10 10:30 | 7.37 | 7.36
2020-02-10 11:00 | 7.99 | 7.98
2020-02-10 11:30 | 9.47 | 9.46
2020-02-10 12:00 | 7.18 | 7.15
2020-02-10 12:30 | 7.94 | 7.9
2020-02-10 13:00 | 9.77 | 9.74
2020-02-10 13:30 | 10.46 | 10.42
2020-02-10 14:00 | 10.5 | 10.47
2020-02-10 14:30 | 10.1 | 10.05
2020-02-10 15:00 | 12.66 | 12.62
2020-02-10 15:30 | 14.51 | 14.49
2020-02-10 16:00 | 14.97 | 14.95
2020-02-10 16:30 | 14.3 | 14.28
2020-02-10 17:00 | 15.3 | 15.29
2020-02-10 17:30 | 15.66 | 15.65
2020-02-10 18:00 | 15.42 | 15.41
2020-02-10 18:30 | 15.56 | 15.55
2020-02-10 19:00 | 16 | 15.98
2020-02-10 19:30 | 15.57 | 15.56
2020-02-10 20:00 | 14.96 | 14.95
2020-02-10 20:30 | 14.13 | 14.13
2020-02-10 21:00 | 13.16 | 13.16
2020-02-10 21:30 | 12.1 | 12.1
2020-02-10 22:00 | 11.24 | 11.24
2020-02-10 22:30 | 10.24 | 10.23
2020-02-10 23:00 | 9.7 | 9.69
2020-02-10 23:30 | 8.63 | 8.62
2020-02-11 | 7.76 | 7.73
2020-02-11 00:30 | 7.17 | 7.14
2020-02-11 01:00 | 6.84 | 6.8
2020-02-11 01:30 | 6.52 | 6.47
2020-02-11 02:00 | 6.32 | 6.27
2020-02-11 02:30 | 6.18 | 6.13
2020-02-11 03:00 | 6.12 | 6.06
2020-02-11 03:30 | 6.14 | 6.08
2020-02-11 04:00 | 6.09 | 6.03
2020-02-11 04:30 | 6.13 | 6.08
2020-02-11 05:00 | 6.35 | 6.3
2020-02-11 05:30 | 6.78 | 6.74
2020-02-11 06:00 | 7.17 | 7.1
2020-02-11 06:30 | 7.51 | 7.45
2020-02-11 07:00 | 7.89 | 7.85
2020-02-11 07:30 | 8.14 | 8.11
2020-02-11 08:00 | 7.63 | 7.61
2020-02-11 08:30 | 7.36 | 7.34
2020-02-11 09:00 | 6.34 | 6.34
2020-02-11 09:30 | 5.47 | 5.46
2020-02-11 10:00 | 7.08 | 7.07
2020-02-11 10:30 | 8.66 | 8.66
2020-02-11 11:00 | 8.85 | 8.85
2020-02-11 11:30 | 9.13 | 9.13
2020-02-11 12:00 | 8.1 | 8.09
2020-02-11 12:30 | 5.12 | 5.11
2020-02-11 13:00 | 6.29 | 6.28
2020-02-11 13:30 | 7.05 | 7.03
2020-02-11 14:00 | 7.85 | 7.83
2020-02-11 14:30 | 9.14 | 9.12
2020-02-11 15:00 | 9.11 | 9.09
2020-02-11 15:30 | 9.63 | 9.6
2020-02-11 16:00 | 11.83 | 11.79
2020-02-11 16:30 | 14.06 | 14.01
2020-02-11 17:00 | 16.14 | 16.11
2020-02-11 17:30 | 17.21 | 17.17
2020-02-11 18:00 | 17.12 | 17.09
2020-02-11 18:30 | 17.68 | 17.65
2020-02-11 19:00 | 18.28 | 18.24
2020-02-11 19:30 | 18.17 | 18.12
2020-02-11 20:00 | 17.72 | 17.68
2020-02-11 20:30 | 17.1 | 17.07
2020-02-11 21:00 | 15.87 | 15.85
2020-02-11 21:30 | 14.41 | 14.4
2020-02-11 22:00 | 12.93 | 12.93
2020-02-11 22:30 | 11.8 | 11.79
2020-02-11 23:00 | 11.18 | 11.18
2020-02-11 23:30 | 9.87 | 9.87
2020-02-12 | 8.83 | 8.83
2020-02-12 00:30 | 8.14 | 8.13
2020-02-12 01:00 | 7.81 | 7.8
2020-02-12 01:30 | 7.5 | 7.48
2020-02-12 02:00 | 7.08 | 7.06
2020-02-12 02:30 | 6.84 | 6.82
2020-02-12 03:00 | 6.71 | 6.69
2020-02-12 03:30 | 6.67 | 6.64
2020-02-12 04:00 | 6.61 | 6.58
2020-02-12 04:30 | 6.72 | 6.7
2020-02-12 05:00 | 6.82 | 6.79
2020-02-12 05:30 | 7.12 | 7.1
2020-02-12 06:00 | 7.52 | 7.48
2020-02-12 06:30 | 8.16 | 8.12
2020-02-12 07:00 | 8.09 | 8.06
2020-02-12 07:30 | 8.24 | 8.23
2020-02-12 08:00 | 8.55 | 8.54
2020-02-12 08:30 | 9.26 | 9.26
2020-02-12 09:00 | 6.73 | 6.73
2020-02-12 09:30 | 6.23 | 6.22
2020-02-12 10:00 | 4.94 | 4.92
2020-02-12 10:30 | 6.67 | 6.65
2020-02-12 11:00 | 8.67 | 8.66
2020-02-12 11:30 | 7.81 | 7.8
2020-02-12 12:00 | 7.66 | 7.66
2020-02-12 12:30 | 6.49 | 6.47
2020-02-12 13:00 | 7.84 | 7.83
2020-02-12 13:30 | 8.49 | 8.48
2020-02-12 14:00 | 8.95 | 8.94
2020-02-12 14:30 | 9.08 | 9.06
2020-02-12 15:00 | 11.9 | 11.9
2020-02-12 15:30 | 11.25 | 11.25
2020-02-12 16:00 | 10.93 | 10.92
2020-02-12 16:30 | 12.53 | 12.52
2020-02-12 17:00 | 12.79 | 12.78
2020-02-12 17:30 | 13.86 | 13.86
2020-02-12 18:00 | 14.61 | 14.6
2020-02-12 18:30 | 14.84 | 14.83
2020-02-12 19:00 | 15.06 | 15.06
2020-02-12 19:30 | 14.32 | 14.31
2020-02-12 20:00 | 14.01 | 14
2020-02-12 20:30 | 13.59 | 13.59
2020-02-12 21:00 | 12.68 | 12.67
2020-02-12 21:30 | 11.68 | 11.68
2020-02-12 22:00 | 10.91 | 10.9
2020-02-12 22:30 | 10.19 | 10.19
2020-02-12 23:00 | 9.71 | 9.7
2020-02-12 23:30 | 8.68 | 8.66
2020-02-13 | 7.74 | 7.71
2020-02-13 00:30 | 7.1 | 7.06
2020-02-13 01:00 | 6.73 | 6.69
2020-02-13 01:30 | 6.37 | 6.31
2020-02-13 02:00 | 6.06 | 6
2020-02-13 02:30 | 6.03 | 5.97
2020-02-13 03:00 | 5.9 | 5.84
2020-02-13 03:30 | 6.07 | 6.01
2020-02-13 04:00 | 6.08 | 6.03
2020-02-13 04:30 | 6.09 | 6.03
2020-02-13 05:00 | 6.24 | 6.18
2020-02-13 05:30 | 6.75 | 6.71
2020-02-13 06:00 | 6.94 | 6.88
2020-02-13 06:30 | 7.27 | 7.2
2020-02-13 07:00 | 7.54 | 7.48
2020-02-13 07:30 | 7.6 | 7.56
2020-02-13 08:00 | 8.06 | 8.02
2020-02-13 08:30 | 7.84 | 7.8
2020-02-13 09:00 | 8.25 | 8.22
2020-02-13 09:30 | 9.37 | 9.35
2020-02-13 10:00 | 9.1 | 9.03
2020-02-13 10:30 | 8.78 | 8.71
2020-02-13 11:00 | 7.14 | 7.03
2020-02-13 11:30 | 7.22 | 7.1
2020-02-13 12:00 | 6.58 | 6.46
2020-02-13 12:30 | 8.13 | 8.03
2020-02-13 13:00 | 7.59 | 7.49
2020-02-13 13:30 | 8.41 | 8.33
2020-02-13 14:00 | 9.11 | 9.06
2020-02-13 14:30 | 7.72 | 7.71
2020-02-13 15:00 | 7.21 | 7.2
2020-02-13 15:30 | 8.4 | 8.39
2020-02-13 16:00 | 9.61 | 9.61
2020-02-13 16:30 | 10.28 | 10.27
2020-02-13 17:00 | 10.39 | 10.39
2020-02-13 17:30 | 11.21 | 11.2
2020-02-13 18:00 | 11.93 | 11.92
2020-02-13 18:30 | 12.4 | 12.39
2020-02-13 19:00 | 13.19 | 13.18
2020-02-13 19:30 | 13.11 | 13.11
2020-02-13 20:00 | 13.15 | 13.15
2020-02-13 20:30 | 12.56 | 12.55
2020-02-13 21:00 | 11.82 | 11.82
2020-02-13 21:30 | 11.02 | 11.01
2020-02-13 22:00 | 10.24 | 10.23
2020-02-13 22:30 | 9.54 | 9.52
2020-02-13 23:00 | 9.17 | 9.15
2020-02-13 23:30 | 8.23 | 8.2
2020-02-14 | 7.42 | 7.38
2020-02-14 00:30 | 6.66 | 6.6
2020-02-14 01:00 | 6.43 | 6.37
2020-02-14 01:30 | 6.15 | 6.09
2020-02-14 02:00 | 5.86 | 5.79
2020-02-14 02:30 | 5.75 | 5.67
2020-02-14 03:00 | 5.65 | 5.57
2020-02-14 03:30 | 5.76 | 5.68
2020-02-14 04:00 | 5.69 | 5.61
2020-02-14 04:30 | 5.81 | 5.74
2020-02-14 05:00 | 5.95 | 5.88
2020-02-14 05:30 | 6.31 | 6.24
2020-02-14 06:00 | 6.67 | 6.57
2020-02-14 06:30 | 7.12 | 7.04
2020-02-14 07:00 | 7.59 | 7.52
2020-02-14 07:30 | 7.49 | 7.45
2020-02-14 08:00 | 6.72 | 6.69
2020-02-14 08:30 | 5.63 | 5.61
2020-02-14 09:00 | 4.67 | 4.66
2020-02-14 09:30 | 5.19 | 5.18
2020-02-14 10:00 | 5.74 | 5.74
2020-02-14 10:30 | 6.71 | 6.7
2020-02-14 11:00 | 6.97 | 6.96
2020-02-14 11:30 | 5.77 | 5.74
2020-02-14 12:00 | 6.28 | 6.24
2020-02-14 12:30 | 7.25 | 7.21
2020-02-14 13:00 | 7.8 | 7.77
2020-02-14 13:30 | 9.03 | 9
2020-02-14 14:00 | 9.9 | 9.87
2020-02-14 14:30 | 10.78 | 10.76
2020-02-14 15:00 | 10.69 | 10.66
2020-02-14 15:30 | 12.59 | 12.56
2020-02-14 16:00 | 13.32 | 13.29
2020-02-14 16:30 | 14.46 | 14.44
2020-02-14 17:00 | 13.53 | 13.51
2020-02-14 17:30 | 14.18 | 14.15
2020-02-14 18:00 | 15.13 | 15.11
2020-02-14 18:30 | 15.39 | 15.38
2020-02-14 19:00 | 15.71 | 15.69
2020-02-14 19:30 | 15.85 | 15.82
2020-02-14 20:00 | 15.38 | 15.36
2020-02-14 20:30 | 14.63 | 14.61
2020-02-14 21:00 | 13.84 | 13.83
2020-02-14 21:30 | 12.71 | 12.71
2020-02-14 22:00 | 11.85 | 11.85
2020-02-14 22:30 | 11.38 | 11.38
2020-02-14 23:00 | 10.84 | 10.83
2020-02-14 23:30 | 9.84 | 9.84
2020-02-15 | 8.81 | 8.8
2020-02-15 00:30 | 8.05 | 8.03
2020-02-15 01:00 | 7.69 | 7.67
2020-02-15 01:30 | 7.29 | 7.27
2020-02-15 02:00 | 6.9 | 6.87
2020-02-15 02:30 | 6.68 | 6.65
2020-02-15 03:00 | 6.56 | 6.53
2020-02-15 03:30 | 6.55 | 6.52
2020-02-15 04:00 | 6.44 | 6.4
2020-02-15 04:30 | 6.36 | 6.31
2020-02-15 05:00 | 6.3 | 6.25
2020-02-15 05:30 | 6.24 | 6.18
2020-02-15 06:00 | 6.28 | 6.19
2020-02-15 06:30 | 6.3 | 6.21
2020-02-15 07:00 | 6.3 | 6.22
2020-02-15 07:30 | 6.36 | 6.32
2020-02-15 08:00 | 5.97 | 5.93
2020-02-15 08:30 | 5.93 | 5.92
2020-02-15 09:00 | 6.22 | 6.2
2020-02-15 09:30 | 6.83 | 6.81
2020-02-15 10:00 | 7.14 | 7.12
2020-02-15 10:30 | 7.88 | 7.86
2020-02-15 11:00 | 8.53 | 8.49
2020-02-15 11:30 | 9.18 | 9.12
2020-02-15 12:00 | 10.51 | 10.44
2020-02-15 12:30 | 11.76 | 11.69
2020-02-15 13:00 | 13.1 | 13.02
2020-02-15 13:30 | 14.07 | 13.98
2020-02-15 14:00 | 15.75 | 15.65
2020-02-15 14:30 | 16.26 | 16.16
2020-02-15 15:00 | 17.27 | 17.17
2020-02-15 15:30 | 19.33 | 19.22
2020-02-15 16:00 | 18.89 | 18.79
2020-02-15 16:30 | 19.02 | 18.92
2020-02-15 17:00 | 19.59 | 19.48
2020-02-15 17:30 | 20.51 | 20.41
2020-02-15 18:00 | 20.52 | 20.43
2020-02-15 18:30 | 20.01 | 19.94
2020-02-15 19:00 | 19.89 | 19.82
2020-02-15 19:30 | 19.79 | 19.71
2020-02-15 20:00 | 19.45 | 19.37
2020-02-15 20:30 | 18.58 | 18.52
2020-02-15 21:00 | 17.54 | 17.49
2020-02-15 21:30 | 16.21 | 16.17
2020-02-15 22:00 | 15.14 | 15.12
2020-02-15 22:30 | 14.23 | 14.22
2020-02-15 23:00 | 13.61 | 13.6
2020-02-15 23:30 | 12.2 | 12.19
2020-02-16 | 11 | 10.99
2020-02-16 00:30 | 10.04 | 10.03
2020-02-16 01:00 | 9.49 | 9.48
2020-02-16 01:30 | 9.01 | 9
2020-02-16 02:00 | 8.53 | 8.53
2020-02-16 02:30 | 8.13 | 8.12
2020-02-16 03:00 | 7.85 | 7.84
2020-02-16 03:30 | 7.56 | 7.56
2020-02-16 04:00 | 7.48 | 7.47
2020-02-16 04:30 | 7.34 | 7.32
2020-02-16 05:00 | 7.12 | 7.11
2020-02-16 05:30 | 6.95 | 6.92
2020-02-16 06:00 | 6.85 | 6.79
2020-02-16 06:30 | 6.68 | 6.62
2020-02-16 07:00 | 6.53 | 6.49
2020-02-16 07:30 | 6.66 | 6.64
2020-02-16 08:00 | 7.09 | 7.08
2020-02-16 08:30 | 8.61 | 8.6
2020-02-16 09:00 | 9.27 | 9.26
2020-02-16 09:30 | 9.48 | 9.47
2020-02-16 10:00 | 10.18 | 10.16
2020-02-16 10:30 | 11.05 | 11.01
2020-02-16 11:00 | 11.32 | 11.26
2020-02-16 11:30 | 12.84 | 12.76
2020-02-16 12:00 | 14.15 | 14.06
2020-02-16 12:30 | 15.07 | 14.96
2020-02-16 13:00 | 15.31 | 15.17
2020-02-16 13:30 | 16.93 | 16.79
2020-02-16 14:00 | 18.06 | 17.93
2020-02-16 14:30 | 17.73 | 17.59
2020-02-16 15:00 | 18.15 | 18
2020-02-16 15:30 | 19.43 | 19.28
2020-02-16 16:00 | 20.2 | 20.06
2020-02-16 16:30 | 21 | 20.87
2020-02-16 17:00 | 21.8 | 21.68
2020-02-16 17:30 | 22.33 | 22.21
2020-02-16 18:00 | 22.54 | 22.43
2020-02-16 18:30 | 21.79 | 21.71
2020-02-16 19:00 | 21.39 | 21.31
2020-02-16 19:30 | 20.83 | 20.75
2020-02-16 20:00 | 19.95 | 19.88
2020-02-16 20:30 | 18.93 | 18.87
2020-02-16 21:00 | 17.36 | 17.32
2020-02-16 21:30 | 16.02 | 16
2020-02-16 22:00 | 14.46 | 14.44
2020-02-16 22:30 | 13.19 | 13.18
2020-02-16 23:00 | 12.33 | 12.32
2020-02-16 23:30 | 10.96 | 10.96
2020-02-17 | 9.72 | 9.71
2020-02-17 00:30 | 8.82 | 8.81
2020-02-17 01:00 | 8.34 | 8.34
2020-02-17 01:30 | 8.01 | 8
2020-02-17 02:00 | 7.64 | 7.63
2020-02-17 02:30 | 7.32 | 7.31
2020-02-17 03:00 | 7.19 | 7.18
2020-02-17 03:30 | 7.21 | 7.2
2020-02-17 04:00 | 7.16 | 7.15
2020-02-17 04:30 | 7.15 | 7.13
2020-02-17 05:00 | 7.3 | 7.28
2020-02-17 05:30 | 7.36 | 7.34
2020-02-17 06:00 | 7.55 | 7.52
2020-02-17 06:30 | 7.74 | 7.71
2020-02-17 07:00 | 7.82 | 7.81
2020-02-17 07:30 | 7.9 | 7.89
2020-02-17 08:00 | 7.78 | 7.78
2020-02-17 08:30 | 7.14 | 7.13
2020-02-17 09:00 | 6.95 | 6.93
2020-02-17 09:30 | 7.56 | 7.54
2020-02-17 10:00 | 7.93 | 7.91
2020-02-17 10:30 | 8.3 | 8.27
2020-02-17 11:00 | 8.9 | 8.85
2020-02-17 11:30 | 9.9 | 9.85
2020-02-17 12:00 | 10.01 | 9.94
2020-02-17 12:30 | 10.8 | 10.72
2020-02-17 13:00 | 11.75 | 11.67
2020-02-17 13:30 | 12.93 | 12.84
2020-02-17 14:00 | 13.23 | 13.14
2020-02-17 14:30 | 13.33 | 13.22
2020-02-17 15:00 | 14.5 | 14.4
2020-02-17 15:30 | 15.31 | 15.19
2020-02-17 16:00 | 16.77 | 16.65
2020-02-17 16:30 | 18.03 | 17.92
2020-02-17 17:00 | 19.58 | 19.46
2020-02-17 17:30 | 20.7 | 20.6
2020-02-17 18:00 | 20.95 | 20.86
2020-02-17 18:30 | 20.87 | 20.8
2020-02-17 19:00 | 20.83 | 20.76
2020-02-17 19:30 | 20.19 | 20.11
2020-02-17 20:00 | 19.51 | 19.45
2020-02-17 20:30 | 18.66 | 18.61
2020-02-17 21:00 | 17.15 | 17.12
2020-02-17 21:30 | 15.57 | 15.55
2020-02-17 22:00 | 14.09 | 14.08
2020-02-17 22:30 | 12.96 | 12.95
2020-02-17 23:00 | 11.9 | 11.9
2020-02-17 23:30 | 10.39 | 10.39
2020-02-18 | 9.2 | 9.2
2020-02-18 00:30 | 8.52 | 8.51
2020-02-18 01:00 | 8.14 | 8.13
2020-02-18 01:30 | 7.68 | 7.67
2020-02-18 02:00 | 7.36 | 7.35
2020-02-18 02:30 | 7.07 | 7.06
2020-02-18 03:00 | 6.93 | 6.91
2020-02-18 03:30 | 6.76 | 6.73
2020-02-18 04:00 | 6.68 | 6.65
2020-02-18 04:30 | 6.74 | 6.71
2020-02-18 05:00 | 6.82 | 6.79
2020-02-18 05:30 | 6.93 | 6.9
2020-02-18 06:00 | 7.1 | 7.05
2020-02-18 06:30 | 7.64 | 7.6
2020-02-18 07:00 | 8.09 | 8.07
2020-02-18 07:30 | 7.91 | 7.9
2020-02-18 08:00 | 7.75 | 7.74
2020-02-18 08:30 | 6.73 | 6.73
2020-02-18 09:00 | 7.58 | 7.57
2020-02-18 09:30 | 7.41 | 7.4
2020-02-18 10:00 | 7.85 | 7.83
2020-02-18 10:30 | 7.45 | 7.42
2020-02-18 11:00 | 7.41 | 7.37
2020-02-18 11:30 | 8.1 | 8.05
2020-02-18 12:00 | 8.99 | 8.93
2020-02-18 12:30 | 10.06 | 9.97
2020-02-18 13:00 | 10.7 | 10.62
2020-02-18 13:30 | 11.93 | 11.85
2020-02-18 14:00 | 13.31 | 13.21
2020-02-18 14:30 | 13.26 | 13.14
2020-02-18 15:00 | 14.17 | 14.05
2020-02-18 15:30 | 15.85 | 15.72
2020-02-18 16:00 | 17.74 | 17.62
2020-02-18 16:30 | 19.26 | 19.14
2020-02-18 17:00 | 20.73 | 20.61
2020-02-18 17:30 | 22.04 | 21.92
2020-02-18 18:00 | 23 | 22.88
2020-02-18 18:30 | 23.08 | 22.97
2020-02-18 19:00 | 23.22 | 23.1
2020-02-18 19:30 | 22.72 | 22.6
2020-02-18 20:00 | 21.6 | 21.5
2020-02-18 20:30 | 20.68 | 20.59
2020-02-18 21:00 | 19.4 | 19.33
2020-02-18 21:30 | 17.62 | 17.58
2020-02-18 22:00 | 15.81 | 15.78
2020-02-18 22:30 | 14.37 | 14.35
2020-02-18 23:00 | 13.1 | 13.09
2020-02-18 23:30 | 11.79 | 11.78
2020-02-19 | 10.4 | 10.39
2020-02-19 00:30 | 9.73 | 9.73
2020-02-19 01:00 | 9.32 | 9.31
2020-02-19 01:30 | 8.8 | 8.8
2020-02-19 02:00 | 8.4 | 8.39
2020-02-19 02:30 | 8.09 | 8.09
2020-02-19 03:00 | 8.03 | 8.02
2020-02-19 03:30 | 7.92 | 7.91
2020-02-19 04:00 | 7.8 | 7.79
2020-02-19 04:30 | 7.64 | 7.63
2020-02-19 05:00 | 7.75 | 7.74
2020-02-19 05:30 | 8.05 | 8.04
2020-02-19 06:00 | 8.58 | 8.56
2020-02-19 06:30 | 8.96 | 8.95
2020-02-19 07:00 | 9.2 | 9.19
2020-02-19 07:30 | 10.1 | 10.1
2020-02-19 08:00 | 10.31 | 10.31
2020-02-19 08:30 | 8.53 | 8.52
2020-02-19 09:00 | 8.96 | 8.95
2020-02-19 09:30 | 9 | 8.98
2020-02-19 10:00 | 9.14 | 9.12
2020-02-19 10:30 | 8.88 | 8.84
2020-02-19 11:00 | 9.65 | 9.61
2020-02-19 11:30 | 10.28 | 10.23
2020-02-19 12:00 | 11.49 | 11.42
2020-02-19 12:30 | 11.79 | 11.69
2020-02-19 13:00 | 14.2 | 14.1
2020-02-19 13:30 | 15.04 | 14.93
2020-02-19 14:00 | 15.17 | 15.05
2020-02-19 14:30 | 16.06 | 15.91
2020-02-19 15:00 | 16.81 | 16.65
2020-02-19 15:30 | 18.52 | 18.37
2020-02-19 16:00 | 20.52 | 20.34
2020-02-19 16:30 | 21.91 | 21.72
2020-02-19 17:00 | 24.36 | 24.17
2020-02-19 17:30 | 25.38 | 25.21
2020-02-19 18:00 | 25 | 24.83
2020-02-19 18:30 | 24.98 | 24.82
2020-02-19 19:00 | 25.51 | 25.32
2020-02-19 19:30 | 24.61 | 24.42
2020-02-19 20:00 | 22.2 | 22.06
2020-02-19 20:30 | 20.96 | 20.85
2020-02-19 21:00 | 19.63 | 19.55
2020-02-19 21:30 | 17.77 | 17.72
2020-02-19 22:00 | 15.92 | 15.89
2020-02-19 22:30 | 13.53 | 13.52
2020-02-19 23:00 | 12.4 | 12.39
2020-02-19 23:30 | 11.18 | 11.18
2020-02-20 | 9.72 | 9.71
2020-02-20 00:30 | 9.27 | 9.27
2020-02-20 01:00 | 9.18 | 9.17
2020-02-20 01:30 | 8.56 | 8.55
2020-02-20 02:00 | 8.09 | 8.09
2020-02-20 02:30 | 7.79 | 7.78
2020-02-20 03:00 | 7.55 | 7.54
2020-02-20 03:30 | 7.43 | 7.42
2020-02-20 04:00 | 7.35 | 7.34
2020-02-20 04:30 | 7.25 | 7.23
2020-02-20 05:00 | 7.17 | 7.15
2020-02-20 05:30 | 7.36 | 7.34
2020-02-20 06:00 | 7.77 | 7.73
2020-02-20 06:30 | 8.27 | 8.24
2020-02-20 07:00 | 7.99 | 7.96
2020-02-20 07:30 | 7.74 | 7.72
2020-02-20 08:00 | 7.08 | 7.07
2020-02-20 08:30 | 6.04 | 6.04
2020-02-20 09:00 | 5.89 | 5.89
2020-02-20 09:30 | 6.87 | 6.87
2020-02-20 10:00 | 6.86 | 6.86
2020-02-20 10:30 | 6.08 | 6.06
2020-02-20 11:00 | 5.49 | 5.47
2020-02-20 11:30 | 5.99 | 5.95
2020-02-20 12:00 | 6.69 | 6.64
2020-02-20 12:30 | 7.27 | 7.22
2020-02-20 13:00 | 8.05 | 7.98
2020-02-20 13:30 | 8.99 | 8.92
2020-02-20 14:00 | 9.9 | 9.82
2020-02-20 14:30 | 10.97 | 10.89
2020-02-20 15:00 | 12.09 | 12.01
2020-02-20 15:30 | 13.57 | 13.48
2020-02-20 16:00 | 15.77 | 15.67
2020-02-20 16:30 | 17.44 | 17.34
2020-02-20 17:00 | 18.86 | 18.76
2020-02-20 17:30 | 19.69 | 19.6
2020-02-20 18:00 | 20.21 | 20.13
2020-02-20 18:30 | 19.96 | 19.89
2020-02-20 19:00 | 20.04 | 19.95
2020-02-20 19:30 | 19.43 | 19.35
2020-02-20 20:00 | 18.72 | 18.65
2020-02-20 20:30 | 17.46 | 17.41
2020-02-20 21:00 | 16.41 | 16.38
2020-02-20 21:30 | 14.92 | 14.9
2020-02-20 22:00 | 13.48 | 13.48
2020-02-20 22:30 | 12.37 | 12.37
2020-02-20 23:00 | 11.4 | 11.4
2020-02-20 23:30 | 10.08 | 10.07
2020-02-21 | 8.99 | 8.98
2020-02-21 00:30 | 8.33 | 8.33
2020-02-21 01:00 | 7.91 | 7.89
2020-02-21 01:30 | 7.49 | 7.47
2020-02-21 02:00 | 7.08 | 7.06
2020-02-21 02:30 | 6.83 | 6.8
2020-02-21 03:00 | 6.72 | 6.7
2020-02-21 03:30 | 6.82 | 6.79
2020-02-21 04:00 | 6.74 | 6.72
2020-02-21 04:30 | 6.72 | 6.68
2020-02-21 05:00 | 6.85 | 6.82
2020-02-21 05:30 | 6.97 | 6.93
2020-02-21 06:00 | 7.06 | 7
2020-02-21 06:30 | 7.21 | 7.16
2020-02-21 07:00 | 7.24 | 7.21
2020-02-21 07:30 | 7.29 | 7.27
2020-02-21 08:00 | 6.67 | 6.66
2020-02-21 08:30 | 5.9 | 5.88
2020-02-21 09:00 | 5.73 | 5.71
2020-02-21 09:30 | 5.21 | 5.19
2020-02-21 10:00 | 5.89 | 5.86
2020-02-21 10:30 | 6.35 | 6.33
2020-02-21 11:00 | 7.27 | 7.23
2020-02-21 11:30 | 7.99 | 7.94
2020-02-21 12:00 | 8.59 | 8.53
2020-02-21 12:30 | 10.21 | 10.15
2020-02-21 13:00 | 10.81 | 10.74
2020-02-21 13:30 | 10.97 | 10.9
2020-02-21 14:00 | 10.25 | 10.16
2020-02-21 14:30 | 10.3 | 10.21
2020-02-21 15:00 | 12 | 11.91
2020-02-21 15:30 | 13.1 | 13.03
2020-02-21 16:00 | 14.82 | 14.75
2020-02-21 16:30 | 15.54 | 15.48
2020-02-21 17:00 | 16.55 | 16.49
2020-02-21 17:30 | 17.37 | 17.31
2020-02-21 18:00 | 17.22 | 17.17
2020-02-21 18:30 | 17.01 | 16.98
2020-02-21 19:00 | 16.9 | 16.87
2020-02-21 19:30 | 16.47 | 16.44
2020-02-21 20:00 | 16.19 | 16.16
2020-02-21 20:30 | 15.49 | 15.47
2020-02-21 21:00 | 14.44 | 14.42
2020-02-21 21:30 | 13.39 | 13.38
2020-02-21 22:00 | 12.4 | 12.4
2020-02-21 22:30 | 11.54 | 11.54
2020-02-21 23:00 | 11.02 | 11.02
2020-02-21 23:30 | 9.99 | 9.98
2020-02-22 | 9.04 | 9.04
2020-02-22 00:30 | 8.32 | 8.31
2020-02-22 01:00 | 8.04 | 8.03
2020-02-22 01:30 | 7.51 | 7.49
2020-02-22 02:00 | 7.23 | 7.21
2020-02-22 02:30 | 6.89 | 6.87
2020-02-22 03:00 | 6.83 | 6.8
2020-02-22 03:30 | 6.67 | 6.64
2020-02-22 04:00 | 6.48 | 6.44
2020-02-22 04:30 | 6.38 | 6.33
2020-02-22 05:00 | 6.53 | 6.49
2020-02-22 05:30 | 6.49 | 6.45
2020-02-22 06:00 | 6.74 | 6.67
2020-02-22 06:30 | 6.73 | 6.67
2020-02-22 07:00 | 6.42 | 6.36
2020-02-22 07:30 | 6.49 | 6.46
2020-02-22 08:00 | 6.97 | 6.96
2020-02-22 08:30 | 6.96 | 6.95
2020-02-22 09:00 | 7.04 | 7.03
2020-02-22 09:30 | 7.58 | 7.57
2020-02-22 10:00 | 8.14 | 8.13
2020-02-22 10:30 | 6.42 | 6.38
2020-02-22 11:00 | 7.9 | 7.86
2020-02-22 11:30 | 9.76 | 9.74
2020-02-22 12:00 | 8.08 | 8.04
2020-02-22 12:30 | 10.22 | 10.19
2020-02-22 13:00 | 10.28 | 10.25
2020-02-22 13:30 | 10.41 | 10.38
2020-02-22 14:00 | 10.94 | 10.91
2020-02-22 14:30 | 10.05 | 10.03
2020-02-22 15:00 | 10.4 | 10.39
2020-02-22 15:30 | 10.41 | 10.4
2020-02-22 16:00 | 10.43 | 10.42
2020-02-22 16:30 | 10.39 | 10.38
2020-02-22 17:00 | 10.66 | 10.64
2020-02-22 17:30 | 10.72 | 10.71
2020-02-22 18:00 | 11.24 | 11.23
2020-02-22 18:30 | 11.99 | 11.98
2020-02-22 19:00 | 12.71 | 12.7
2020-02-22 19:30 | 12.53 | 12.52
2020-02-22 20:00 | 12.43 | 12.42
2020-02-22 20:30 | 12.09 | 12.09
2020-02-22 21:00 | 11.38 | 11.37
2020-02-22 21:30 | 10.9 | 10.89
2020-02-22 22:00 | 10.4 | 10.39
2020-02-22 22:30 | 10.03 | 10.03
2020-02-22 23:00 | 9.7 | 9.68
2020-02-22 23:30 | 8.82 | 8.81
2020-02-23 | 8.03 | 8
2020-02-23 00:30 | 7.47 | 7.44
2020-02-23 01:00 | 7.14 | 7.11
2020-02-23 01:30 | 6.78 | 6.74
2020-02-23 02:00 | 6.4 | 6.36
2020-02-23 02:30 | 6.23 | 6.18
2020-02-23 03:00 | 6.02 | 5.96
2020-02-23 03:30 | 6.06 | 6
2020-02-23 04:00 | 6.09 | 6.03
2020-02-23 04:30 | 5.82 | 5.76
2020-02-23 05:00 | 5.84 | 5.77
2020-02-23 05:30 | 5.83 | 5.76
2020-02-23 06:00 | 5.74 | 5.61
2020-02-23 06:30 | 5.9 | 5.77
2020-02-23 07:00 | 5.49 | 5.36
2020-02-23 07:30 | 5.33 | 5.21
2020-02-23 08:00 | 6.31 | 6.23
2020-02-23 08:30 | 6 | 5.93
2020-02-23 09:00 | 6.34 | 6.29
2020-02-23 09:30 | 7.89 | 7.87
2020-02-23 10:00 | 8.84 | 8.82
2020-02-23 10:30 | 8.21 | 8.19
2020-02-23 11:00 | 7.8 | 7.78
2020-02-23 11:30 | 6.7 | 6.68
2020-02-23 12:00 | 6.54 | 6.52
2020-02-23 12:30 | 6.7 | 6.68
2020-02-23 13:00 | 7.71 | 7.69
2020-02-23 13:30 | 8.71 | 8.7
2020-02-23 14:00 | 9.14 | 9.13
2020-02-23 14:30 | 8.43 | 8.41
2020-02-23 15:00 | 8.26 | 8.25
2020-02-23 15:30 | 9.22 | 9.2
2020-02-23 16:00 | 8.83 | 8.81
2020-02-23 16:30 | 9.4 | 9.38
2020-02-23 17:00 | 10.24 | 10.23
2020-02-23 17:30 | 11.39 | 11.38
2020-02-23 18:00 | 12.16 | 12.15
2020-02-23 18:30 | 12.53 | 12.53
2020-02-23 19:00 | 12.88 | 12.88
2020-02-23 19:30 | 12.55 | 12.55
2020-02-23 20:00 | 12.4 | 12.4
2020-02-23 20:30 | 11.96 | 11.96
2020-02-23 21:00 | 11.21 | 11.2
2020-02-23 21:30 | 10.48 | 10.47
2020-02-23 22:00 | 9.87 | 9.86
2020-02-23 22:30 | 9.45 | 9.43
2020-02-23 23:00 | 8.84 | 8.81
2020-02-23 23:30 | 8.03 | 7.99
2020-02-24 | 7.15 | 7.11
2020-02-24 00:30 | 6.6 | 6.55
2020-02-24 01:00 | 6.33 | 6.26
2020-02-24 01:30 | 6.05 | 5.98
2020-02-24 02:00 | 5.7 | 5.62
2020-02-24 02:30 | 5.4 | 5.3
2020-02-24 03:00 | 5.41 | 5.32
2020-02-24 03:30 | 5.45 | 5.36
2020-02-24 04:00 | 5.5 | 5.41
2020-02-24 04:30 | 5.58 | 5.49
2020-02-24 05:00 | 5.83 | 5.75
2020-02-24 05:30 | 6.14 | 6.08
2020-02-24 06:00 | 6.58 | 6.49
2020-02-24 06:30 | 7.18 | 7.09
2020-02-24 07:00 | 7.61 | 7.54
2020-02-24 07:30 | 7.89 | 7.85
2020-02-24 08:00 | 6.93 | 6.89
2020-02-24 08:30 | 6.87 | 6.84
2020-02-24 09:00 | 7.39 | 7.36
2020-02-24 09:30 | 7.95 | 7.94
2020-02-24 10:00 | 7.96 | 7.94
2020-02-24 10:30 | 7.51 | 7.49
2020-02-24 11:00 | 5.9 | 5.89
2020-02-24 11:30 | 6.67 | 6.66
2020-02-24 12:00 | 6.9 | 6.89
2020-02-24 12:30 | 6.56 | 6.55
2020-02-24 13:00 | 5.01 | 5
2020-02-24 13:30 | 4.93 | 4.91
2020-02-24 14:00 | 7.17 | 7.17
2020-02-24 14:30 | 7.66 | 7.65
2020-02-24 15:00 | 7.37 | 7.36
2020-02-24 15:30 | 8.06 | 8.05
2020-02-24 16:00 | 8.66 | 8.65
2020-02-24 16:30 | 10.65 | 10.65
2020-02-24 17:00 | 11.84 | 11.83
2020-02-24 17:30 | 12.79 | 12.79
2020-02-24 18:00 | 13.12 | 13.11
2020-02-24 18:30 | 13.65 | 13.64
2020-02-24 19:00 | 14.36 | 14.35
2020-02-24 19:30 | 14.02 | 14.01
2020-02-24 20:00 | 13.6 | 13.6
2020-02-24 20:30 | 13.32 | 13.32
2020-02-24 21:00 | 12.4 | 12.4
2020-02-24 21:30 | 11.3 | 11.29
2020-02-24 22:00 | 10.38 | 10.37
2020-02-24 22:30 | 9.73 | 9.71
2020-02-24 23:00 | 9.12 | 9.09
2020-02-24 23:30 | 8.07 | 8.04
2020-02-25 | 7.2 | 7.15
2020-02-25 00:30 | 6.56 | 6.5
2020-02-25 01:00 | 6.31 | 6.25
2020-02-25 01:30 | 6.06 | 5.99
2020-02-25 02:00 | 5.76 | 5.69
2020-02-25 02:30 | 5.6 | 5.51
2020-02-25 03:00 | 5.47 | 5.38
2020-02-25 03:30 | 5.55 | 5.46
2020-02-25 04:00 | 5.56 | 5.48
2020-02-25 04:30 | 5.68 | 5.6
2020-02-25 05:00 | 5.84 | 5.76
2020-02-25 05:30 | 6.21 | 6.14
2020-02-25 06:00 | 6.79 | 6.68
2020-02-25 06:30 | 7.74 | 7.64
2020-02-25 07:00 | 7.01 | 6.95
2020-02-25 07:30 | 6.44 | 6.4
2020-02-25 08:00 | 5.5 | 5.46
2020-02-25 08:30 | 4.59 | 4.57
2020-02-25 09:00 | 4.1 | 4.08
2020-02-25 09:30 | 4.66 | 4.64
2020-02-25 10:00 | 5.51 | 5.49
2020-02-25 10:30 | 5.25 | 5.24
2020-02-25 11:00 | 6.31 | 6.29
2020-02-25 11:30 | 7.13 | 7.12
2020-02-25 12:00 | 8.73 | 8.71
2020-02-25 12:30 | 8.26 | 8.25
2020-02-25 13:00 | 8.31 | 8.3
2020-02-25 13:30 | 7.55 | 7.53
2020-02-25 14:00 | 9.18 | 9.16
2020-02-25 14:30 | 10.03 | 10.02
2020-02-25 15:00 | 9.67 | 9.66
2020-02-25 15:30 | 9.27 | 9.25
2020-02-25 16:00 | 8.85 | 8.83
2020-02-25 16:30 | 10.44 | 10.42
2020-02-25 17:00 | 12.67 | 12.65
2020-02-25 17:30 | 13.41 | 13.39
2020-02-25 18:00 | 13.65 | 13.64
2020-02-25 18:30 | 14.71 | 14.7
2020-02-25 19:00 | 15.96 | 15.95
2020-02-25 19:30 | 15.78 | 15.76
2020-02-25 20:00 | 15.09 | 15.08
2020-02-25 20:30 | 14.71 | 14.7
2020-02-25 21:00 | 13.94 | 13.93
2020-02-25 21:30 | 12.69 | 12.69
2020-02-25 22:00 | 11.41 | 11.41
2020-02-25 22:30 | 10.44 | 10.43
2020-02-25 23:00 | 9.89 | 9.88
2020-02-25 23:30 | 8.66 | 8.64
2020-02-26 | 7.71 | 7.69
2020-02-26 00:30 | 7.09 | 7.05
2020-02-26 01:00 | 6.72 | 6.67
2020-02-26 01:30 | 6.42 | 6.37
2020-02-26 02:00 | 6.19 | 6.13
2020-02-26 02:30 | 5.99 | 5.93
2020-02-26 03:00 | 5.85 | 5.78
2020-02-26 03:30 | 5.85 | 5.78
2020-02-26 04:00 | 5.82 | 5.75
2020-02-26 04:30 | 5.93 | 5.86
2020-02-26 05:00 | 6.08 | 6.01
2020-02-26 05:30 | 6.33 | 6.27
2020-02-26 06:00 | 6.5 | 6.39
2020-02-26 06:30 | 6.82 | 6.73
2020-02-26 07:00 | 6.93 | 6.87
2020-02-26 07:30 | 6.7 | 6.66
2020-02-26 08:00 | 5.98 | 5.96
2020-02-26 08:30 | 5.26 | 5.25
2020-02-26 09:00 | 4.84 | 4.83
2020-02-26 09:30 | 5.2 | 5.19
2020-02-26 10:00 | 6.3 | 6.28
2020-02-26 10:30 | 6.3 | 6.28
2020-02-26 11:00 | 7.18 | 7.17
2020-02-26 11:30 | 6.33 | 6.31
2020-02-26 12:00 | 7.49 | 7.46
2020-02-26 12:30 | 8.82 | 8.79
2020-02-26 13:00 | 9.14 | 9.11
2020-02-26 13:30 | 10.98 | 10.94
2020-02-26 14:00 | 11.55 | 11.51
2020-02-26 14:30 | 10.89 | 10.84
2020-02-26 15:00 | 12.72 | 12.67
2020-02-26 15:30 | 13.99 | 13.94
2020-02-26 16:00 | 15.33 | 15.28
2020-02-26 16:30 | 16.48 | 16.44
2020-02-26 17:00 | 17.54 | 17.49
2020-02-26 17:30 | 18.09 | 18.04
2020-02-26 18:00 | 18.37 | 18.32
2020-02-26 18:30 | 18.63 | 18.59
2020-02-26 19:00 | 19.68 | 19.61
2020-02-26 19:30 | 19.32 | 19.24
2020-02-26 20:00 | 18.6 | 18.54
2020-02-26 20:30 | 17.81 | 17.76
2020-02-26 21:00 | 16.74 | 16.7
2020-02-26 21:30 | 15.51 | 15.48
2020-02-26 22:00 | 13.98 | 13.97
2020-02-26 22:30 | 12.78 | 12.78
2020-02-26 23:00 | 11.7 | 11.69
2020-02-26 23:30 | 10.4 | 10.4
2020-02-27 | 9.52 | 9.51
2020-02-27 00:30 | 8.77 | 8.76
2020-02-27 01:00 | 8.31 | 8.3
2020-02-27 01:30 | 7.95 | 7.94
2020-02-27 02:00 | 7.43 | 7.41
2020-02-27 02:30 | 7.1 | 7.08
2020-02-27 03:00 | 6.99 | 6.97
2020-02-27 03:30 | 6.94 | 6.91
2020-02-27 04:00 | 6.87 | 6.84
2020-02-27 04:30 | 7.48 | 7.44
2020-02-27 05:00 | 8.1 | 8.07
2020-02-27 05:30 | 8.59 | 8.57
2020-02-27 06:00 | 8.73 | 8.68
2020-02-27 06:30 | 9.14 | 9.1
2020-02-27 07:00 | 9.32 | 9.28
2020-02-27 07:30 | 8.99 | 8.97
2020-02-27 08:00 | 8.79 | 8.78
2020-02-27 08:30 | 9.09 | 9.08
2020-02-27 09:00 | 10.24 | 10.24
2020-02-27 09:30 | 10.44 | 10.44
2020-02-27 10:00 | 11.26 | 11.26
2020-02-27 10:30 | 9.2 | 9.19
2020-02-27 11:00 | 7.68 | 7.68
2020-02-27 11:30 | 4.89 | 4.88
2020-02-27 12:00 | 5.79 | 5.77
2020-02-27 12:30 | 7.1 | 7.08
2020-02-27 13:00 | 8.07 | 8.03
2020-02-27 13:30 | 9.52 | 9.48
2020-02-27 14:00 | 13.42 | 13.4
2020-02-27 14:30 | 10.15 | 10.13
2020-02-27 15:00 | 11.28 | 11.25
2020-02-27 15:30 | 11.41 | 11.38
2020-02-27 16:00 | 13.06 | 13.03
2020-02-27 16:30 | 15.65 | 15.63
2020-02-27 17:00 | 15.93 | 15.92
2020-02-27 17:30 | 15.04 | 15.02
2020-02-27 18:00 | 16.45 | 16.43
2020-02-27 18:30 | 16.89 | 16.88
2020-02-27 19:00 | 17.75 | 17.72
2020-02-27 19:30 | 17.37 | 17.34
2020-02-27 20:00 | 16.98 | 16.96
2020-02-27 20:30 | 16.04 | 16.03
2020-02-27 21:00 | 14.97 | 14.97
2020-02-27 21:30 | 13.81 | 13.8
2020-02-27 22:00 | 12.75 | 12.75
2020-02-27 22:30 | 11.93 | 11.93
2020-02-27 23:00 | 11.29 | 11.28
2020-02-27 23:30 | 10.12 | 10.1
2020-02-28 | 9.18 | 9.15
2020-02-28 00:30 | 8.54 | 8.51
2020-02-28 01:00 | 8.23 | 8.19
2020-02-28 01:30 | 7.88 | 7.83
2020-02-28 02:00 | 7.51 | 7.46
2020-02-28 02:30 | 7.25 | 7.19
2020-02-28 03:00 | 7.19 | 7.12
2020-02-28 03:30 | 7.16 | 7.1
2020-02-28 04:00 | 7.06 | 6.99
2020-02-28 04:30 | 7.19 | 7.12
2020-02-28 05:00 | 7.37 | 7.3
2020-02-28 05:30 | 7.54 | 7.48
2020-02-28 06:00 | 8.06 | 7.98
2020-02-28 06:30 | 8.31 | 8.24
2020-02-28 07:00 | 8.26 | 8.2
2020-02-28 07:30 | 7.67 | 7.63
2020-02-28 08:00 | 6.72 | 6.68
2020-02-28 08:30 | 6.38 | 6.36
2020-02-28 09:00 | 6.27 | 6.27
2020-02-28 09:30 | 6.35 | 6.35
2020-02-28 10:00 | 6.29 | 6.28
2020-02-28 10:30 | 6.74 | 6.72
2020-02-28 11:00 | 6.34 | 6.32
2020-02-28 11:30 | 7.17 | 7.13
2020-02-28 12:00 | 8.88 | 8.85
2020-02-28 12:30 | 9.51 | 9.46
2020-02-28 13:00 | 11.31 | 11.27
2020-02-28 13:30 | 12.2 | 12.15
2020-02-28 14:00 | 12.65 | 12.58
2020-02-28 14:30 | 14.48 | 14.42
2020-02-28 15:00 | 17.13 | 17.08
2020-02-28 15:30 | 17.61 | 17.56
2020-02-28 16:00 | 17.04 | 17
2020-02-28 16:30 | 16.31 | 16.28
2020-02-28 17:00 | 16.02 | 16
2020-02-28 17:30 | 15.8 | 15.78
2020-02-28 18:00 | 15.96 | 15.94
2020-02-28 18:30 | 16.48 | 16.45
2020-02-28 19:00 | 16.98 | 16.94
2020-02-28 19:30 | 16.9 | 16.87
2020-02-28 20:00 | 16.55 | 16.52
2020-02-28 20:30 | 16.11 | 16.08
2020-02-28 21:00 | 15.12 | 15.1
2020-02-28 21:30 | 14.12 | 14.11
2020-02-28 22:00 | 12.94 | 12.93
2020-02-28 22:30 | 12.25 | 12.25
2020-02-28 23:00 | 11.72 | 11.72
2020-02-28 23:30 | 10.45 | 10.44
2020-02-29 | 9.25 | 9.24
2020-02-29 00:30 | 8.37 | 8.36
2020-02-29 01:00 | 8.01 | 8
2020-02-29 01:30 | 7.56 | 7.54
2020-02-29 02:00 | 7.18 | 7.15
2020-02-29 02:30 | 6.82 | 6.79
2020-02-29 03:00 | 6.66 | 6.63
2020-02-29 03:30 | 6.63 | 6.6
2020-02-29 04:00 | 6.56 | 6.52
2020-02-29 04:30 | 6.48 | 6.45
2020-02-29 05:00 | 6.49 | 6.45
2020-02-29 05:30 | 6.4 | 6.35
2020-02-29 06:00 | 6.31 | 6.22
2020-02-29 06:30 | 6.34 | 6.25
2020-02-29 07:00 | 5.99 | 5.91
2020-02-29 07:30 | 5.97 | 5.92
2020-02-29 08:00 | 5.99 | 5.97
2020-02-29 08:30 | 6.07 | 6.05
2020-02-29 09:00 | 6.46 | 6.44
2020-02-29 09:30 | 8.58 | 8.56
2020-02-29 10:00 | 8.91 | 8.89
2020-02-29 10:30 | 9.24 | 9.22
2020-02-29 11:00 | 8.24 | 8.22
2020-02-29 11:30 | 6.55 | 6.52
2020-02-29 12:00 | 6.18 | 6.13
2020-02-29 12:30 | 8.33 | 8.29
2020-02-29 13:00 | 8.9 | 8.86
2020-02-29 13:30 | 10.64 | 10.6
2020-02-29 14:00 | 11.37 | 11.32
2020-02-29 14:30 | 13.88 | 13.84
2020-02-29 15:00 | 12.2 | 12.16
2020-02-29 15:30 | 13.52 | 13.49
2020-02-29 16:00 | 12.95 | 12.91
2020-02-29 16:30 | 14.05 | 14.02
2020-02-29 17:00 | 15.53 | 15.51
2020-02-29 17:30 | 14.9 | 14.88
2020-02-29 18:00 | 15.33 | 15.31
2020-02-29 18:30 | 15.4 | 15.38
2020-02-29 19:00 | 15.7 | 15.68
2020-02-29 19:30 | 15.43 | 15.41
2020-02-29 20:00 | 14.82 | 14.81
2020-02-29 20:30 | 14.41 | 14.4
2020-02-29 21:00 | 13.28 | 13.27
2020-02-29 21:30 | 12.32 | 12.32
2020-02-29 22:00 | 11.45 | 11.44
2020-02-29 22:30 | 10.95 | 10.94
2020-02-29 23:00 | 10.54 | 10.53
2020-02-29 23:30 | 9.49 | 9.48
2020-03-01 | 8.52 | 8.5
Formulas:
Date/Time = [Date/Time, row above]+30/24/60

## 24. Historic ratings
PQ Rating (MVA) |  | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer | 2019 Winter | 2019/20 Summer
|  | 65.5 | 65.5 | 65.5 | 65.5 | 65.5 | 65.5
Transfromers | T080T01 | 32.7 | 32.7 | 32.7 | 32.7 | 32.7 | 32.7
| T080T02 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8 | 32.8

## 26. Unplanned outages
Unplanned Outage Date/Time | Element Affected | Element Type | Outage Cause | Outage Duration (mins) | Customer Outage Duration (mins) | MW Lost (Instantaneous) | MW Minutes
2018-09-04 12:55 | 7296 - H038 Goodna to T080 Redbank Plains | FEEDER | HV Equipment malfunction or failure | 369.8833
2018-09-04 13:42 | T080 110KV 2 TRANSFORMER | TRANSFORMER | HV Maint | 329.8167
2018-09-18 10:39 | 7296 - H038 Goodna to T080 Redbank Plains | FEEDER | HV Maint | 279.0167
2018-11-06 05:04 | 7296 - H038 Goodna to T080 Redbank Plains | FEEDER | HV Equipment malfunction or failure | 584.6667
2019-01-22 10:37 | 7296 - H038 Goodna to T080 Redbank Plains | FEEDER | HV Maint | 171.5167
2019-11-14 15:23 | T080 110KV 2 TRANSFORMER | TRANSFORMER | HV equipt maintenance | 31.7833
2019-11-14 15:25 | 7296 - H038 Goodna to T080 Redbank Plains | FEEDER | HV equipt maintenance | 29.55