## Cover Page
AER Rule | Field Name | Value(s)
1 | Constrained connection point ID | S003 Greenbank
2 | Constraint primary driver | Asset condition
3 | Constraint investment type | Asset renewal
4 | Constrained connection point latitude (decimal degrees) | -27.7332
| Constrained connection point longitude (decimal degrees) | 152.9549
5 | Effect on residential customers
| Annual Energy | Not available
| Maximum Demand | Not available
6, 7 | Effect on industrial and commercial customers
| Annual Energy | Not available
| Maximum Demand | Not available
8 | Load profile (maximum day, MVA)
50% PoE
Load profile (minimum day, MVA)
Minimum demand data (MVA)
| Max. demand, maximum demand day (MVA) | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| 10% PoE | 1626.2 | 1625.4 | 1626.1 | 1599.4 | 1601.6 | 1605.6 | 1607.1 | 1621.7 | 1631.2 | 1629.9 | 1639.3
| 50% PoE | 1492 | 1501.2 | 1496.1 | 1484.6 | 1480.1 | 1486.8 | 1483.8 | 1485.1 | 1491.2 | 1493 | 1494.8
9 | Max. demand, minimum demand day (MW) | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Maximum demand data | 730.2 | 734.1 | 733.9 | 733.3 | 732.9 | 742.3 | 741.4 | 753.6 | 752.9 | 746.1 | 739.4
10 | Load profile (maximum day, MW)
Load profile 50%
| Max. demand, maximum demand day (MW) | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| 10% PoE | 1613.7 | 1616.9 | 1616.6 | 1591.6 | 1593.7 | 1607.1 | 1618.7 | 1612.9 | 1621.3 | 1620.2 | 1623.4
| 50% PoE | 1485.4 | 1487.1 | 1485.4 | 1473.1 | 1470.7 | 1478.9 | 1479.9 | 1481.8 | 1487.6 | 1484.4 | 1482.8
11 | Load profile (minimum day, MW)
Minimum demand data (MW)
| Min. demand, minimum demand day (MW) | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Mininum demand data | 375.9 | 369.2 | 352.4 | 334 | 319.2 | 311.3 | 291.7 | 267.7 | 244.3 | 215.8 | 190.6
12 | Voltage level (kv) | 275
13 | Maximum load at risk per year | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Load at risk (MW, peak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Load at risk (MVA, peak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Load duration curve
15 | Preferred investment | Greenbank 275kV secondary systems replacement
16 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Capital cost ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0
17 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Operating cost ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5
18 | Preferred investment cost accuracy | 0.3
19 | Preferred investment proposed timing | 2027-06-30
20 | Demand reduction to defer the investment by 1 year | 0
21 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Annual deferral value ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Load transfer capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Historic load trace
24 | Historic ratings
25 | Limitation asset | Feeders
26 | Unplanned outages
27 | Maximum fault level (kA) | 22.6
28 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Economic cost ($m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | VCR ($m/MWh) | 0.03971
30 |  | Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
| Annual unserved energy (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 8. Load profile max (50% PoE)
| Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:00 | 830.2 | 831.4 | 809.7 | 806.8 | 829.8 | 836.4 | 844.7 | 846.2 | 839.8 | 839.2 | 838.6
0:30 | 778.9 | 777.8 | 778.6 | 777.7 | 777.6 | 789.3 | 791.8 | 788.5 | 788.8 | 787.1 | 785.4
1:00 | 756.1 | 753 | 755.1 | 754.6 | 754.5 | 764.3 | 765.7 | 762.2 | 762.2 | 760.8 | 759.4
1:30 | 736.5 | 735.2 | 732 | 734.8 | 734.6 | 740.4 | 739.5 | 742.2 | 742.1 | 741.3 | 740.5
2:00 | 711.9 | 708.8 | 708 | 707.6 | 708 | 717.5 | 719.6 | 716.2 | 715.9 | 715.5 | 715.2
2:30 | 677.8 | 680.4 | 680.9 | 680.5 | 680 | 702.9 | 702.1 | 703.2 | 704.6 | 705.9 | 707.2
3:00 | 689.9 | 675.7 | 688.5 | 688.5 | 675.2 | 680.5 | 679.7 | 695.7 | 696.3 | 695.5 | 694.7
3:30 | 666.6 | 681.3 | 680.6 | 680.6 | 681 | 687.8 | 687.2 | 672.9 | 672.8 | 672.5 | 672.2
4:00 | 663.2 | 676.4 | 676 | 675.9 | 676.2 | 690 | 682.8 | 669.1 | 668.7 | 668.4 | 668.1
4:30 | 663.2 | 676.4 | 675.7 | 675.6 | 676 | 683.3 | 682.8 | 668.6 | 668.1 | 667.9 | 667.7
5:00 | 673.4 | 686.9 | 686.8 | 686.8 | 687 | 694.3 | 693.7 | 679.8 | 679.7 | 679.5 | 679.4
5:30 | 702.1 | 713.8 | 712.9 | 713.1 | 714.1 | 721.2 | 721.7 | 706.9 | 706.8 | 707.1 | 707.5
6:00 | 743.8 | 728.1 | 728.6 | 728.2 | 728.2 | 735.1 | 734.5 | 751.2 | 751.8 | 752.3 | 752.9
6:30 | 821.2 | 800.8 | 799.6 | 799.1 | 798.8 | 822.4 | 827.8 | 804 | 809.7 | 831.4 | 853.6
7:00 | 873.7 | 873.6 | 870 | 868.4 | 866.5 | 869.9 | 874.5 | 873.2 | 871.6 | 867 | 862.4
7:30 | 929.8 | 929.6 | 928.4 | 923.3 | 919.5 | 930.9 | 925.9 | 923.9 | 921.3 | 923.3 | 925.2
8:00 | 970.4 | 965.1 | 961.2 | 954.8 | 954.1 | 955.8 | 956.9 | 952.8 | 953.3 | 948.1 | 942.9
8:30 | 968.7 | 956.9 | 947.7 | 957.9 | 995.1 | 996.5 | 987.8 | 975.6 | 963.5 | 964 | 964.4
9:00 | 991.8 | 989.5 | 1004.7 | 1008.3 | 999.7 | 1002.6 | 993.9 | 977.8 | 972.2 | 952.8 | 933.8
9:30 | 1007.3 | 991.1 | 984.9 | 1026.7 | 1018.5 | 1018.4 | 1001.7 | 985.6 | 977.6 | 960.4 | 943.4
10:00 | 1020.9 | 1007.4 | 1001.4 | 1018 | 1034.3 | 1037.6 | 1018.1 | 995.2 | 977.9 | 962.7 | 947.7
10:30 | 1044.9 | 1027.8 | 1015 | 1004.5 | 1054.3 | 1050.6 | 1033.2 | 1009.8 | 989.1 | 973.4 | 958
11:00 | 1067.5 | 1053.1 | 1037.5 | 1018.7 | 1019.2 | 1064.6 | 1044.3 | 1020.3 | 998 | 983.4 | 969
11:30 | 1095.7 | 1079.1 | 1062.9 | 1041.7 | 1024.2 | 1026.8 | 1056.9 | 1033.6 | 1009.7 | 983.7 | 958.4
12:00 | 1131.1 | 1120.5 | 1099.5 | 1079.3 | 1062 | 1055.7 | 1087.1 | 1052.6 | 1032.5 | 1006.6 | 981.4
12:30 | 1166.8 | 1142 | 1127.4 | 1106.5 | 1087.7 | 1079.6 | 1062.6 | 1075.2 | 1049.8 | 1023.1 | 997.1
13:00 | 1182 | 1167.1 | 1154.4 | 1131.8 | 1114.8 | 1112.4 | 1087.6 | 1097.4 | 1078.1 | 1057.8 | 1037.9
13:30 | 1209.2 | 1189.8 | 1177.9 | 1162.3 | 1145.7 | 1136.4 | 1124.6 | 1129.3 | 1106 | 1082.8 | 1060.1
14:00 | 1237.8 | 1221.7 | 1205.5 | 1184.3 | 1174.8 | 1170.9 | 1150.4 | 1160.5 | 1142.1 | 1116.8 | 1092.1
14:30 | 1287.7 | 1270.8 | 1259 | 1242.7 | 1229.4 | 1223.3 | 1210.7 | 1193.5 | 1204.4 | 1183.2 | 1162.4
15:00 | 1312.8 | 1302.9 | 1293.6 | 1277.4 | 1261.2 | 1265 | 1248.6 | 1233.7 | 1272.7 | 1228.5 | 1185.8
15:30 | 1346.4 | 1332.5 | 1330 | 1311.8 | 1299.8 | 1296.6 | 1285 | 1270.9 | 1255.8 | 1271.9 | 1288.3
16:00 | 1433.1 | 1426.9 | 1419.2 | 1410.6 | 1399 | 1407 | 1395.8 | 1386.3 | 1373.7 | 1360.5 | 1347.4
16:30 | 1473.6 | 1472.9 | 1468.5 | 1451.3 | 1445.6 | 1445.3 | 1447.9 | 1438.3 | 1435.3 | 1424.9 | 1414.6
17:00 | 1492 | 1501.2 | 1496.1 | 1484.6 | 1480.1 | 1486.8 | 1483.8 | 1481.4 | 1484.4 | 1475.4 | 1466.6
17:30 | 1481.1 | 1488.9 | 1489.9 | 1481.2 | 1472.4 | 1485.1 | 1483.1 | 1485.1 | 1491.2 | 1493 | 1494.8
18:00 | 1451 | 1456.6 | 1461 | 1455 | 1437 | 1456.4 | 1474.9 | 1468.4 | 1489.9 | 1488.7 | 1487.5
18:30 | 1399.7 | 1396.5 | 1403.6 | 1402.3 | 1404.7 | 1428.5 | 1435.6 | 1443.5 | 1451.7 | 1456.8 | 1461.9
19:00 | 1381.9 | 1372.5 | 1380 | 1373.8 | 1375.8 | 1397.7 | 1410.3 | 1416.3 | 1425.9 | 1425.3 | 1424.6
19:30 | 1357.6 | 1348.5 | 1356 | 1353.4 | 1351.1 | 1375.3 | 1388 | 1395.3 | 1401.8 | 1400.1 | 1398.4
20:00 | 1302.1 | 1294.9 | 1297.2 | 1293.2 | 1295.1 | 1318 | 1320.2 | 1324.3 | 1338.1 | 1335.3 | 1332.5
20:30 | 1292.1 | 1282.9 | 1286.2 | 1279.3 | 1279.9 | 1304.5 | 1308 | 1311.7 | 1326.5 | 1325.3 | 1324.1
21:00 | 1256.9 | 1255.4 | 1256 | 1253.5 | 1254.2 | 1268 | 1273.3 | 1275.7 | 1282.9 | 1287.7 | 1292.6
21:30 | 1160.5 | 1161.1 | 1158.8 | 1157.8 | 1161.5 | 1182.4 | 1184.1 | 1180.5 | 1159.8 | 1158.5 | 1157.2
22:00 | 1099.7 | 1101.3 | 1101 | 1157.8 | 1102.3 | 1113.7 | 1118.4 | 1112.9 | 1112.7 | 1111.2 | 1109.7
22:30 | 1002.4 | 995.2 | 994.7 | 1000.3 | 1000.8 | 1009.4 | 1009.4 | 1011.4 | 1012 | 1008 | 1004.1
23:00 | 967.9 | 966.6 | 966 | 965.7 | 966.2 | 979.2 | 979.7 | 981.5 | 982.2 | 977.9 | 973.7
23:30 | 915.9 | 910.5 | 910.2 | 910 | 910.3 | 921 | 927.3 | 930.1 | 930.7 | 926.8 | 922.8

## 8. Load profile min
| Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
Time | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA) | Forecast Demand (MVA)
0:00 | 610.3 | 574.5 | 603.5 | 604.2 | 601.3 | 611.2 | 613.1 | 612.5 | 581.5 | 581.4 | 581.3
0:30 | 571.8 | 541.8 | 566.5 | 567.5 | 566.3 | 578.7 | 574.7 | 580.9 | 548.9 | 550 | 551.2
1:00 | 544.1 | 517.5 | 539.8 | 541.8 | 542.9 | 555.4 | 550.4 | 553.3 | 537.2 | 535.5 | 533.9
1:30 | 519.8 | 493 | 521.4 | 512 | 520.8 | 535.2 | 532 | 532.8 | 511.9 | 522.4 | 533
2:00 | 511.1 | 489.2 | 491.1 | 484.1 | 488.9 | 526.7 | 511.8 | 522.9 | 499.7 | 495.2 | 490.8
2:30 | 488.1 | 479.3 | 468.3 | 476 | 471.5 | 506.7 | 491.4 | 503.7 | 488.7 | 503.8 | 519.3
3:00 | 483.7 | 474.6 | 472.1 | 466.5 | 469.1 | 518.4 | 498.2 | 516.5 | 476.1 | 487.1 | 498.2
3:30 | 466 | 478.1 | 452.1 | 453 | 460.4 | 487 | 481.1 | 488.6 | 464.5 | 471.9 | 479.4
4:00 | 450 | 467.6 | 451.2 | 451.3 | 454.6 | 503.7 | 474 | 503.6 | 459.6 | 462.3 | 464.9
4:30 | 444.4 | 468.4 | 452.4 | 450.1 | 453.8 | 507.4 | 475.2 | 508.8 | 469.6 | 464.9 | 460.3
5:00 | 457.8 | 481.2 | 462.9 | 458.8 | 469.3 | 510.3 | 482.3 | 516 | 474.1 | 473.9 | 473.6
5:30 | 493.2 | 474 | 487.8 | 486.8 | 489.9 | 526.5 | 506.1 | 519 | 479.9 | 487.7 | 495.5
6:00 | 465.9 | 489.3 | 508.3 | 507.6 | 508.1 | 518.7 | 537 | 522.3 | 503.9 | 496.9 | 490
6:30 | 534 | 504.4 | 536.5 | 535.5 | 535.4 | 537 | 545.8 | 530.5 | 521.6 | 522.9 | 524.3
7:00 | 546.1 | 507.4 | 559.5 | 558 | 559.2 | 530.8 | 566 | 529.8 | 521.9 | 527.1 | 532.4
7:30 | 572.8 | 510.5 | 564 | 562.7 | 563.3 | 505.5 | 572.6 | 513.3 | 522.7 | 524.5 | 526.3
8:00 | 598.7 | 503.9 | 557.2 | 557.8 | 554.7 | 543.7 | 561.9 | 531.2 | 498.3 | 493.8 | 489.4
8:30 | 589.7 | 541.1 | 577.9 | 572.8 | 565.8 | 512.8 | 567.3 | 496.3 | 516.4 | 511.6 | 506.8
9:00 | 571.1 | 526.1 | 562.9 | 552.3 | 542.3 | 493.9 | 538.5 | 471.8 | 471.5 | 440.3 | 411.2
9:30 | 559.3 | 508.4 | 531.5 | 520.3 | 513.4 | 474 | 502.6 | 444.8 | 405.9 | 408.9 | 411.8
10:00 | 512.7 | 494.9 | 508.8 | 496.4 | 485.2 | 455.4 | 469.4 | 412.2 | 407.2 | 388.8 | 371.3
10:30 | 517 | 480.4 | 480.4 | 464.2 | 475.4 | 438.1 | 420.8 | 379.7 | 392.3 | 384.7 | 377.3
11:00 | 551.1 | 473.5 | 473.3 | 435.1 | 427.9 | 418.8 | 404.9 | 383.8 | 380.8 | 390.3 | 400
11:30 | 531.3 | 438 | 427.5 | 427.3 | 376 | 399.4 | 395.7 | 386.4 | 404.6 | 359 | 318.5
12:00 | 512.7 | 431.1 | 425.6 | 404.4 | 424.8 | 391.5 | 387.1 | 370.8 | 355.6 | 379.2 | 404.4
12:30 | 508 | 437.7 | 419.2 | 381.5 | 369.9 | 411.9 | 390.5 | 381.1 | 385.3 | 335.7 | 292.4
13:00 | 523.1 | 445.5 | 420.7 | 384.5 | 369.8 | 398.4 | 364.8 | 381.5 | 349.5 | 341.2 | 333
13:30 | 516.2 | 455.4 | 424.4 | 399.7 | 493.8 | 428.7 | 394.4 | 374.2 | 384.4 | 364.2 | 345
14:00 | 534.8 | 470.6 | 439.2 | 430.9 | 428.1 | 447.5 | 410.9 | 393.7 | 400.1 | 387.2 | 374.7
14:30 | 554.9 | 497.8 | 476.3 | 485.3 | 448.8 | 480.5 | 416.8 | 453.7 | 429.4 | 416.8 | 404.6
15:00 | 588.5 | 527.6 | 497.5 | 492.1 | 476.2 | 495.5 | 434.8 | 468.3 | 453.5 | 434.3 | 415.9
15:30 | 569.6 | 556.8 | 497.5 | 528.4 | 519.4 | 535.5 | 511.9 | 510.8 | 489.8 | 480.8 | 471.9
16:00 | 568.6 | 601.5 | 585.3 | 580.7 | 574 | 602.5 | 563 | 579.7 | 557.2 | 549.3 | 541.4
16:30 | 645.8 | 638.3 | 646.2 | 636.6 | 636 | 645.6 | 631.7 | 631.2 | 617.8 | 613 | 608.2
17:00 | 671.3 | 640.1 | 717.8 | 715.9 | 714.9 | 688.9 | 719.5 | 684.8 | 680.5 | 679.1 | 677.8
17:30 | 716.6 | 678.9 | 744.8 | 744.3 | 744.5 | 688.8 | 752.3 | 688.3 | 686.6 | 686.9 | 687.2
18:00 | 745.1 | 730.9 | 748.7 | 743.7 | 741.9 | 726.5 | 753.8 | 728.1 | 738.9 | 739.3 | 739.7
18:30 | 768.1 | 766.8 | 779 | 778.2 | 779 | 772.3 | 781.3 | 774 | 772.5 | 775.2 | 777.9
19:00 | 767 | 773.3 | 790.5 | 791.5 | 790.8 | 782.8 | 789.7 | 780.6 | 778.9 | 779.2 | 779.5
19:30 | 749.2 | 758.3 | 771.4 | 768.6 | 772 | 757.4 | 778.3 | 755.5 | 764.2 | 762.1 | 760
20:00 | 740.7 | 744.5 | 762.7 | 762.3 | 762.1 | 743.5 | 769.7 | 738.9 | 752.6 | 752.3 | 752
20:30 | 736.1 | 736.8 | 762.8 | 762.5 | 760.5 | 731.9 | 768.2 | 731.8 | 742.3 | 749 | 755.8
21:00 | 703.6 | 708 | 729 | 729.6 | 729.3 | 712.2 | 736.7 | 706.9 | 714.5 | 720.5 | 726.6
21:30 | 679.5 | 680.8 | 706.8 | 705.8 | 705.3 | 695.3 | 713.8 | 690.5 | 689.8 | 693.6 | 697.6
22:00 | 671.9 | 673.1 | 689.3 | 688.4 | 689.2 | 679.9 | 697 | 682.2 | 673.8 | 673.9 | 673.9
22:30 | 665.1 | 661.6 | 672.8 | 671.2 | 674.8 | 663.4 | 681.3 | 664.9 | 662.1 | 661.8 | 661.6
23:00 | 659.2 | 656.3 | 663.3 | 665.4 | 666 | 665.5 | 670.2 | 664.8 | 657.6 | 657.3 | 657.1
23:30 | 628.7 | 624.8 | 631.7 | 634 | 632.7 | 637.8 | 639.7 | 636.8 | 631.6 | 631.4 | 631.2

## 10. Load profile (50% PoE)
| Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:00 | 796.5 | 796.3 | 772.1 | 771.8 | 795.5 | 804.9 | 806.2 | 807.9 | 807.7 | 805.5 | 803.2
0:30 | 743.3 | 741.7 | 742.3 | 741.7 | 741.4 | 753.7 | 754.1 | 752.7 | 752.9 | 751.1 | 749.4
1:00 | 718.3 | 716.3 | 717.2 | 716.7 | 716.4 | 727.6 | 727.7 | 726.2 | 726.3 | 724.8 | 723.3
1:30 | 698.3 | 696.6 | 693.3 | 696.5 | 696.2 | 702.7 | 701.8 | 704.9 | 704.4 | 704.1 | 703.7
2:00 | 672 | 669 | 668.4 | 668.1 | 668.5 | 678.5 | 679.9 | 677.7 | 677.5 | 677 | 676.6
2:30 | 636.4 | 638.9 | 639.5 | 639 | 638.6 | 663.2 | 662.7 | 664 | 665.6 | 667 | 668.3
3:00 | 648.9 | 633.6 | 647.4 | 647.5 | 633.3 | 639.4 | 638.4 | 655.3 | 655.2 | 655.2 | 655.3
3:30 | 624.9 | 639.8 | 639.2 | 639.1 | 639.5 | 646.7 | 646.1 | 631.1 | 630.9 | 630.5 | 630.2
4:00 | 621.1 | 635 | 634.5 | 634.5 | 634.8 | 642.1 | 641.8 | 627.1 | 627 | 626.6 | 626.2
4:30 | 621.3 | 635 | 634.4 | 634.3 | 634.7 | 642.3 | 641.8 | 626.9 | 626.7 | 626.4 | 626.1
5:00 | 632.2 | 646.3 | 645.9 | 645.9 | 646.2 | 653.8 | 653.3 | 638.7 | 638.6 | 638.4 | 638.1
5:30 | 661.2 | 674.2 | 673.5 | 673.5 | 674.1 | 681.5 | 681.7 | 667.5 | 667.6 | 667 | 666.3
6:00 | 703.5 | 686.5 | 687.1 | 686.6 | 686.5 | 693.9 | 693.1 | 711.2 | 711.8 | 712.2 | 712.6
6:30 | 781 | 758.5 | 758.9 | 758.4 | 758.2 | 785.9 | 786.3 | 765.5 | 767.7 | 790.3 | 813.6
7:00 | 840.7 | 840.9 | 837 | 839.2 | 837.3 | 846.2 | 842.5 | 844.6 | 843.2 | 839.4 | 835.6
7:30 | 916.2 | 915.5 | 914.1 | 909.7 | 905.8 | 916.8 | 911.8 | 910 | 906.2 | 908.1 | 909.9
8:00 | 953.6 | 948.9 | 945 | 938.6 | 937.3 | 941.3 | 940.9 | 936.6 | 937.2 | 932.4 | 927.7
8:30 | 951.9 | 939.3 | 930.1 | 940.7 | 977.3 | 978.3 | 970.4 | 958.8 | 950 | 941.9 | 933.8
9:00 | 974.1 | 973 | 988.5 | 991.9 | 984 | 986.3 | 975.7 | 962.9 | 948.7 | 937.7 | 926.8
9:30 | 989.3 | 975.9 | 967.8 | 1013.6 | 1001.3 | 1000.6 | 986.1 | 971.1 | 953.8 | 938.5 | 923.4
10:00 | 1011.1 | 997.9 | 986.2 | 1003.6 | 1018.4 | 1018.7 | 1002.5 | 981.3 | 963.7 | 940.3 | 917.4
10:30 | 1034.2 | 1018.6 | 1005.7 | 989 | 1039.8 | 1035.6 | 1017.9 | 995.7 | 975.6 | 951.7 | 928.4
11:00 | 1055.1 | 1041.4 | 1027 | 1008.8 | 1002.2 | 1050.1 | 1027.3 | 1005.6 | 982.1 | 959.7 | 937.9
11:30 | 1083.7 | 1065.3 | 1050.1 | 1030.4 | 1014 | 1010.4 | 1041.2 | 1017.1 | 995.4 | 970.9 | 947
12:00 | 1118 | 1103.9 | 1086.9 | 1065.8 | 1049 | 1044.7 | 1068.4 | 1037.3 | 1014.8 | 990.5 | 966.8
12:30 | 1152 | 1130.6 | 1114.5 | 1094.1 | 1076.5 | 1070.6 | 1050.3 | 1058 | 1032.6 | 1009 | 986
13:00 | 1172.4 | 1152.4 | 1140.9 | 1120 | 1102.7 | 1100 | 1076.7 | 1087.3 | 1061.1 | 1039.3 | 1018
13:30 | 1198.9 | 1181.3 | 1169.6 | 1149.7 | 1133.9 | 1126.2 | 1110.7 | 1117.1 | 1094.8 | 1072.6 | 1050.8
14:00 | 1226.5 | 1209.9 | 1195.1 | 1175.8 | 1160.4 | 1157.9 | 1137.8 | 1148.5 | 1130.4 | 1105.9 | 1081.9
14:30 | 1270.1 | 1255.2 | 1243.5 | 1226.6 | 1213.7 | 1209.5 | 1189.9 | 1177.7 | 1190.3 | 1169.6 | 1149.3
15:00 | 1300.1 | 1286.2 | 1277.1 | 1262.1 | 1246.7 | 1251.4 | 1233.5 | 1220.3 | 1250.5 | 1213.1 | 1176.7
15:30 | 1332.1 | 1319.2 | 1312.9 | 1296.4 | 1283.3 | 1282.8 | 1271.2 | 1254.1 | 1241.7 | 1257.9 | 1274.3
16:00 | 1422.5 | 1414.6 | 1406.3 | 1391.8 | 1381.2 | 1386.4 | 1376.3 | 1366.3 | 1355.1 | 1343.4 | 1331.7
16:30 | 1459 | 1457.8 | 1452.5 | 1437.1 | 1431.1 | 1437.8 | 1433.8 | 1424.2 | 1418.6 | 1408.3 | 1398
17:00 | 1485.4 | 1487.1 | 1485.4 | 1473.1 | 1470.7 | 1478.5 | 1475.5 | 1472.2 | 1474.9 | 1466.1 | 1457.3
17:30 | 1469.8 | 1475 | 1477.7 | 1469.7 | 1465.7 | 1478.9 | 1479.9 | 1481.8 | 1487.6 | 1484.4 | 1481.1
18:00 | 1442.5 | 1447.3 | 1450.5 | 1445 | 1430.7 | 1446 | 1468.3 | 1456.1 | 1481.5 | 1482.1 | 1482.8
18:30 | 1388.5 | 1392.1 | 1398.5 | 1394.8 | 1396.9 | 1420.8 | 1428.5 | 1435.2 | 1445.8 | 1449.6 | 1453.3
19:00 | 1370.4 | 1364 | 1371.6 | 1361.8 | 1363.7 | 1387.6 | 1400.8 | 1406.6 | 1415.5 | 1416.6 | 1417.8
19:30 | 1347.8 | 1341.9 | 1347 | 1344.4 | 1341.8 | 1365.3 | 1379 | 1384.7 | 1391.3 | 1392.1 | 1392.8
20:00 | 1291.8 | 1286.5 | 1289.4 | 1283.2 | 1286 | 1308.3 | 1312.5 | 1316.5 | 1329.8 | 1328.8 | 1327.8
20:30 | 1279.8 | 1274.8 | 1278.5 | 1271.4 | 1271.8 | 1294.4 | 1299.3 | 1303 | 1317.1 | 1315.9 | 1314.7
21:00 | 1247.8 | 1246.4 | 1246.5 | 1244.5 | 1244.9 | 1258.8 | 1264.1 | 1267.5 | 1273.9 | 1279.3 | 1284.8
21:30 | 1150 | 1151.7 | 1152.6 | 1151.6 | 1151.3 | 1170.1 | 1171.9 | 1167.4 | 1150.7 | 1149.3 | 1147.9
22:00 | 1088.5 | 1089 | 1088.7 | 1151.6 | 1090 | 1106.3 | 1108.8 | 1103.7 | 1104.4 | 1101.6 | 1098.8
22:30 | 986.1 | 984.9 | 984.4 | 983.7 | 984.3 | 999.1 | 999.5 | 1001.4 | 1001.9 | 998.1 | 994.2
23:00 | 954 | 952.7 | 952.1 | 951.7 | 952.2 | 964.3 | 965.2 | 967 | 967.6 | 963.6 | 959.6
23:30 | 897.6 | 896.4 | 895.9 | 895.8 | 896.1 | 907.4 | 908.9 | 911 | 911.5 | 907.6 | 903.8

## 11. Load profile min
| Year 0 (FY 2020) | Year 1 (FY 2021) | Year 2 (FY 2022) | Year 3 (FY 2023) | Year 4 (FY 2024) | Year 5 (FY 2025) | Year 6 (FY 2026) | Year 7 (FY 2027) | Year 8 (FY 2028) | Year 9 (FY 2029) | Year 10 (FY 2030)
Time | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW) | Forecast Demand (MW)
0:00 | 541.3 | 507.3 | 507.3 | 506.8 | 506.5 | 516.8 | 516.1 | 546.8 | 546.6 | 544.6 | 542.6
0:30 | 498.5 | 473.6 | 473.5 | 473.3 | 472.6 | 482.2 | 482.1 | 502.8 | 502.3 | 512.4 | 522.6
1:00 | 469.9 | 454.9 | 455.9 | 454.6 | 454.5 | 462.9 | 462.6 | 474.5 | 474.8 | 490.7 | 507.1
1:30 | 451.4 | 435.5 | 435.2 | 434.4 | 434.8 | 443.1 | 442.1 | 452.6 | 452.3 | 470.6 | 489.6
2:00 | 438.6 | 415.6 | 415.4 | 414.9 | 414.7 | 424.8 | 424.2 | 425.4 | 425.5 | 455.2 | 487.1
2:30 | 426.3 | 407.8 | 407.7 | 407.3 | 406.9 | 416.8 | 416.6 | 412.2 | 410.8 | 432.3 | 454.9
3:00 | 410.7 | 405.2 | 405.4 | 405 | 404.8 | 412.5 | 413.4 | 415.1 | 413.1 | 439.1 | 466.7
3:30 | 383.5 | 401 | 400.6 | 400.1 | 399.5 | 408.3 | 409.8 | 396.1 | 395.9 | 416.3 | 437.8
4:00 | 375.9 | 395.2 | 395 | 394.5 | 394.2 | 401.9 | 403 | 393.4 | 392.3 | 424.9 | 460.2
4:30 | 376.8 | 397.3 | 396.7 | 395.8 | 395.8 | 404.6 | 404.4 | 394 | 393.5 | 431.2 | 472.5
5:00 | 379.5 | 403.6 | 403.1 | 402.7 | 402.2 | 411.7 | 410.9 | 401.7 | 401.5 | 440.2 | 482.6
5:30 | 421.1 | 410 | 409.7 | 409.3 | 409.1 | 418.7 | 417.9 | 420.9 | 420.7 | 450.5 | 482.3
6:00 | 402.4 | 421.9 | 420.3 | 421.1 | 421 | 428.9 | 430.1 | 447.4 | 447.4 | 452.3 | 457.2
6:30 | 458.6 | 435.4 | 435.4 | 434.9 | 434.7 | 443.5 | 443.1 | 471.5 | 471.3 | 465.2 | 459.1
7:00 | 473.2 | 441.3 | 440.8 | 440.3 | 440.3 | 450.4 | 440 | 495.4 | 495.9 | 453.1 | 414.1
7:30 | 513.1 | 449.2 | 447.9 | 449.4 | 447.7 | 456.2 | 457.9 | 501.6 | 504 | 482.9 | 462.6
8:00 | 535.6 | 443.1 | 442.6 | 437.9 | 438.1 | 445.7 | 444.3 | 494.4 | 490.5 | 456.7 | 425.3
8:30 | 525.6 | 485.9 | 480.1 | 475 | 470.2 | 476.8 | 470.7 | 503.6 | 495.5 | 402.2 | 326.5
9:00 | 516.3 | 470.4 | 461.4 | 452.5 | 444.4 | 447.9 | 436.5 | 466.2 | 454.7 | 367.5 | 297.1
9:30 | 500.2 | 452.4 | 440.5 | 429.7 | 418.5 | 418.6 | 401.5 | 425.2 | 408.4 | 339.7 | 282.6
10:00 | 452.3 | 435.9 | 422.3 | 407.6 | 393.7 | 391 | 373.7 | 385.5 | 368.4 | 305.3 | 253
10:30 | 456.3 | 417.5 | 402.1 | 386.3 | 373.6 | 369.4 | 349.2 | 351.3 | 328.7 | 277.7 | 234.7
11:00 | 504.9 | 396.1 | 381.3 | 365.1 | 348.5 | 340.4 | 321.8 | 310.8 | 287.4 | 254 | 224.6
11:30 | 489 | 384.3 | 367.5 | 349.7 | 334.7 | 324.2 | 305 | 284.1 | 260.1 | 235.4 | 212.9
12:00 | 463.2 | 375.4 | 358.7 | 342.7 | 326.7 | 315.6 | 295.1 | 272.6 | 248.2 | 224.5 | 203
12:30 | 457.6 | 369.2 | 352.4 | 334 | 319.2 | 312.6 | 293.1 | 267.7 | 244.3 | 215.8 | 190.6
13:00 | 478.8 | 379.1 | 361.8 | 344.9 | 330.8 | 311.3 | 291.7 | 272.1 | 246.6 | 226.4 | 207.9
13:30 | 467.5 | 390.8 | 374 | 359.1 | 345.2 | 338.2 | 318.7 | 278.7 | 272.7 | 251.3 | 231.5
14:00 | 485.4 | 413.9 | 400.3 | 386.1 | 372 | 365.7 | 346.8 | 308.4 | 288.1 | 288.7 | 289.3
14:30 | 499.8 | 443.3 | 430.9 | 418.4 | 405.3 | 399.9 | 384 | 354.6 | 345.3 | 336.1 | 327.1
15:00 | 537.3 | 470.1 | 456.3 | 445.1 | 435 | 431.4 | 415.9 | 383.5 | 366.1 | 364.8 | 363.5
15:30 | 517.6 | 501.4 | 492.8 | 483.5 | 473.8 | 475.4 | 464.7 | 437.2 | 424.4 | 428.1 | 431.9
16:00 | 511.3 | 551 | 543.6 | 536.1 | 529 | 532.3 | 522.7 | 504.4 | 494.3 | 505.6 | 517.1
16:30 | 583.7 | 589.9 | 585.7 | 581.8 | 577.7 | 586.4 | 578.1 | 575.2 | 569 | 569.4 | 569.8
17:00 | 624.6 | 589.8 | 586.7 | 600.9 | 620.7 | 647.5 | 643.8 | 656.4 | 654.7 | 636.5 | 618.9
17:30 | 674.7 | 637.5 | 637.4 | 636.1 | 635 | 643.7 | 647.2 | 705.6 | 705.6 | 643.1 | 586.1
18:00 | 710.6 | 692.6 | 692.3 | 691.7 | 691.4 | 701.7 | 700.7 | 709.9 | 709.4 | 689.1 | 669.4
18:30 | 730.2 | 727.3 | 727.2 | 726.7 | 726.2 | 736.7 | 735.6 | 739.3 | 739.2 | 737.8 | 736.4
19:00 | 728.7 | 734.1 | 733.9 | 733.3 | 732.9 | 742.3 | 741.4 | 753.6 | 752.9 | 746.1 | 739.4
19:30 | 709.8 | 720.1 | 720.1 | 719.4 | 718.9 | 728.3 | 727.4 | 736.4 | 738.6 | 717.5 | 697
20:00 | 700.6 | 706.5 | 707.2 | 706.2 | 705.8 | 715.7 | 714.7 | 728.9 | 727.6 | 699.3 | 672.2
20:30 | 694.2 | 695.9 | 695.9 | 695.5 | 694.7 | 705.2 | 703.6 | 724 | 723.8 | 690.5 | 658.8
21:00 | 659.1 | 665.9 | 665.8 | 665.2 | 664.8 | 674.4 | 673.4 | 691.2 | 690.3 | 664.4 | 639.5
21:30 | 633.1 | 637.4 | 637.2 | 636.8 | 636.2 | 647.2 | 645.7 | 660.3 | 659.4 | 638.5 | 618.2
22:00 | 611.3 | 613.9 | 613.9 | 613.4 | 613.1 | 623.1 | 622.2 | 635.9 | 635 | 622.4 | 610
22:30 | 599.7 | 601.3 | 601.3 | 600.7 | 600.6 | 610.8 | 609.8 | 617.9 | 616.5 | 604.3 | 592.4
23:00 | 595.3 | 595.6 | 595.5 | 594.9 | 594.8 | 605.3 | 604.6 | 606.9 | 606.2 | 604.8 | 603.4
23:30 | 566.7 | 559.2 | 559.1 | 558.5 | 558.4 | 568.3 | 567.6 | 573.9 | 573.1 | 571.8 | 570.6

## 14. Load duration curve
*The data range is from 01-03-18 to 01-03-19

## 23. Historic load trace
Date/Time | Load (MVA) | Load (MW)
2016-03-01 00:30 | 694 | 689
2016-03-01 01:00 | 688 | 682
2016-03-01 01:30 | 675 | 668
2016-03-01 02:00 | 656 | 647
2016-03-01 02:30 | 649 | 639
2016-03-01 03:00 | 651 | 642
2016-03-01 03:30 | 646 | 637
2016-03-01 04:00 | 649 | 640
2016-03-01 04:30 | 651 | 643
2016-03-01 05:00 | 671 | 666
2016-03-01 05:30 | 703 | 701
2016-03-01 06:00 | 748 | 745
2016-03-01 06:30 | 843 | 842
2016-03-01 07:00 | 905 | 903
2016-03-01 07:30 | 965 | 964
2016-03-01 08:00 | 996 | 994
2016-03-01 08:30 | 1022 | 1019
2016-03-01 09:00 | 1047 | 1044
2016-03-01 09:30 | 1075 | 1069
2016-03-01 10:00 | 1086 | 1078
2016-03-01 10:30 | 1088 | 1081
2016-03-01 11:00 | 1094 | 1088
2016-03-01 11:30 | 1098 | 1091
2016-03-01 12:00 | 1106 | 1100
2016-03-01 12:30 | 1089 | 1081
2016-03-01 13:00 | 1105 | 1097
2016-03-01 13:30 | 1100 | 1091
2016-03-01 14:00 | 1117 | 1106
2016-03-01 14:30 | 1115 | 1103
2016-03-01 15:00 | 1126 | 1112
2016-03-01 15:30 | 1116 | 1101
2016-03-01 16:00 | 1130 | 1113
2016-03-01 16:30 | 1141 | 1122
2016-03-01 17:00 | 1139 | 1116
2016-03-01 17:30 | 1121 | 1097
2016-03-01 18:00 | 1116 | 1099
2016-03-01 18:30 | 1090 | 1080
2016-03-01 19:00 | 1099 | 1093
2016-03-01 19:30 | 1097 | 1089
2016-03-01 20:00 | 1088 | 1078
2016-03-01 20:30 | 1054 | 1049
2016-03-01 21:00 | 985 | 983
2016-03-01 21:30 | 941 | 940
2016-03-01 22:00 | 905 | 904
2016-03-01 22:30 | 858 | 857
2016-03-01 23:00 | 836 | 834
2016-03-01 23:30 | 766 | 763
2016-03-02 | 732 | 727
2016-03-02 00:30 | 694 | 689
2016-03-02 01:00 | 669 | 662
2016-03-02 01:30 | 644 | 636
2016-03-02 02:00 | 633 | 624
2016-03-02 02:30 | 630 | 619
2016-03-02 03:00 | 625 | 614
2016-03-02 03:30 | 627 | 616
2016-03-02 04:00 | 624 | 613
2016-03-02 04:30 | 634 | 624
2016-03-02 05:00 | 647 | 640
2016-03-02 05:30 | 683 | 680
2016-03-02 06:00 | 721 | 719
2016-03-02 06:30 | 803 | 802
2016-03-02 07:00 | 881 | 880
2016-03-02 07:30 | 945 | 944
2016-03-02 08:00 | 974 | 972
2016-03-02 08:30 | 1001 | 1000
2016-03-02 09:00 | 1022 | 1020
2016-03-02 09:30 | 1037 | 1036
2016-03-02 10:00 | 1050 | 1050
2016-03-02 10:30 | 1048 | 1047
2016-03-02 11:00 | 1070 | 1070
2016-03-02 11:30 | 1075 | 1074
2016-03-02 12:00 | 1081 | 1081
2016-03-02 12:30 | 1092 | 1091
2016-03-02 13:00 | 1099 | 1098
2016-03-02 13:30 | 1111 | 1111
2016-03-02 14:00 | 1119 | 1119
2016-03-02 14:30 | 1136 | 1136
2016-03-02 15:00 | 1145 | 1143
2016-03-02 15:30 | 1156 | 1153
2016-03-02 16:00 | 1175 | 1172
2016-03-02 16:30 | 1190 | 1187
2016-03-02 17:00 | 1205 | 1200
2016-03-02 17:30 | 1187 | 1179
2016-03-02 18:00 | 1169 | 1159
2016-03-02 18:30 | 1157 | 1150
2016-03-02 19:00 | 1178 | 1174
2016-03-02 19:30 | 1155 | 1149
2016-03-02 20:00 | 1149 | 1148
2016-03-02 20:30 | 1125 | 1122
2016-03-02 21:00 | 1054 | 1052
2016-03-02 21:30 | 1004 | 1003
2016-03-02 22:00 | 963 | 959
2016-03-02 22:30 | 907 | 906
2016-03-02 23:00 | 878 | 874
2016-03-02 23:30 | 829 | 828
2016-03-03 | 775 | 775
2016-03-03 00:30 | 725 | 725
2016-03-03 01:00 | 704 | 703
2016-03-03 01:30 | 680 | 678
2016-03-03 02:00 | 662 | 659
2016-03-03 02:30 | 649 | 645
2016-03-03 03:00 | 646 | 642
2016-03-03 03:30 | 646 | 642
2016-03-03 04:00 | 646 | 641
2016-03-03 04:30 | 655 | 652
2016-03-03 05:00 | 672 | 670
2016-03-03 05:30 | 684 | 683
2016-03-03 06:00 | 740 | 738
2016-03-03 06:30 | 832 | 831
2016-03-03 07:00 | 911 | 911
2016-03-03 07:30 | 979 | 978
2016-03-03 08:00 | 1014 | 1008
2016-03-03 08:30 | 1036 | 1033
2016-03-03 09:00 | 1044 | 1040
2016-03-03 09:30 | 1048 | 1044
2016-03-03 10:00 | 1048 | 1045
2016-03-03 10:30 | 1042 | 1039
2016-03-03 11:00 | 1046 | 1044
2016-03-03 11:30 | 1050 | 1049
2016-03-03 12:00 | 1054 | 1053
2016-03-03 12:30 | 1060 | 1059
2016-03-03 13:00 | 1059 | 1058
2016-03-03 13:30 | 1074 | 1072
2016-03-03 14:00 | 1090 | 1086
2016-03-03 14:30 | 1104 | 1101
2016-03-03 15:00 | 1123 | 1119
2016-03-03 15:30 | 1130 | 1126
2016-03-03 16:00 | 1151 | 1147
2016-03-03 16:30 | 1187 | 1183
2016-03-03 17:00 | 1205 | 1198
2016-03-03 17:30 | 1195 | 1185
2016-03-03 18:00 | 1178 | 1171
2016-03-03 18:30 | 1168 | 1159
2016-03-03 19:00 | 1199 | 1194
2016-03-03 19:30 | 1169 | 1163
2016-03-03 20:00 | 1137 | 1131
2016-03-03 20:30 | 1122 | 1112
2016-03-03 21:00 | 1070 | 1066
2016-03-03 21:30 | 1006 | 1001
2016-03-03 22:00 | 942 | 940
2016-03-03 22:30 | 894 | 894
2016-03-03 23:00 | 851 | 851
2016-03-03 23:30 | 803 | 803
2016-03-04 | 756 | 755
2016-03-04 00:30 | 717 | 715
2016-03-04 01:00 | 691 | 688
2016-03-04 01:30 | 668 | 663
2016-03-04 02:00 | 654 | 647
2016-03-04 02:30 | 651 | 643
2016-03-04 03:00 | 646 | 637
2016-03-04 03:30 | 645 | 637
2016-03-04 04:00 | 642 | 635
2016-03-04 04:30 | 651 | 646
2016-03-04 05:00 | 667 | 663
2016-03-04 05:30 | 699 | 697
2016-03-04 06:00 | 738 | 735
2016-03-04 06:30 | 825 | 824
2016-03-04 07:00 | 894 | 893
2016-03-04 07:30 | 946 | 943
2016-03-04 08:00 | 982 | 972
2016-03-04 08:30 | 997 | 992
2016-03-04 09:00 | 1015 | 1014
2016-03-04 09:30 | 1020 | 1019
2016-03-04 10:00 | 1006 | 1005
2016-03-04 10:30 | 1026 | 1022
2016-03-04 11:00 | 1036 | 1032
2016-03-04 11:30 | 1032 | 1028
2016-03-04 12:00 | 1018 | 1014
2016-03-04 12:30 | 999 | 994
2016-03-04 13:00 | 1004 | 999
2016-03-04 13:30 | 1009 | 1004
2016-03-04 14:00 | 1029 | 1024
2016-03-04 14:30 | 1040 | 1035
2016-03-04 15:00 | 1048 | 1043
2016-03-04 15:30 | 1062 | 1057
2016-03-04 16:00 | 1085 | 1080
2016-03-04 16:30 | 1114 | 1109
2016-03-04 17:00 | 1131 | 1126
2016-03-04 17:30 | 1121 | 1113
2016-03-04 18:00 | 1096 | 1086
2016-03-04 18:30 | 1071 | 1062
2016-03-04 19:00 | 1090 | 1087
2016-03-04 19:30 | 1070 | 1067
2016-03-04 20:00 | 1045 | 1042
2016-03-04 20:30 | 1012 | 1010
2016-03-04 21:00 | 974 | 970
2016-03-04 21:30 | 939 | 935
2016-03-04 22:00 | 897 | 896
2016-03-04 22:30 | 865 | 865
2016-03-04 23:00 | 847 | 845
2016-03-04 23:30 | 808 | 804
2016-03-05 | 750 | 747
2016-03-05 00:30 | 707 | 704
2016-03-05 01:00 | 681 | 677
2016-03-05 01:30 | 661 | 654
2016-03-05 02:00 | 645 | 637
2016-03-05 02:30 | 635 | 627
2016-03-05 03:00 | 634 | 625
2016-03-05 03:30 | 634 | 625
2016-03-05 04:00 | 630 | 621
2016-03-05 04:30 | 624 | 615
2016-03-05 05:00 | 633 | 625
2016-03-05 05:30 | 643 | 636
2016-03-05 06:00 | 649 | 642
2016-03-05 06:30 | 669 | 663
2016-03-05 07:00 | 692 | 688
2016-03-05 07:30 | 725 | 724
2016-03-05 08:00 | 756 | 753
2016-03-05 08:30 | 784 | 780
2016-03-05 09:00 | 815 | 813
2016-03-05 09:30 | 856 | 851
2016-03-05 10:00 | 867 | 863
2016-03-05 10:30 | 875 | 872
2016-03-05 11:00 | 881 | 879
2016-03-05 11:30 | 880 | 878
2016-03-05 12:00 | 862 | 857
2016-03-05 12:30 | 851 | 846
2016-03-05 13:00 | 846 | 841
2016-03-05 13:30 | 851 | 845
2016-03-05 14:00 | 858 | 853
2016-03-05 14:30 | 862 | 857
2016-03-05 15:00 | 871 | 866
2016-03-05 15:30 | 887 | 882
2016-03-05 16:00 | 905 | 901
2016-03-05 16:30 | 914 | 909
2016-03-05 17:00 | 931 | 926
2016-03-05 17:30 | 926 | 920
2016-03-05 18:00 | 916 | 907
2016-03-05 18:30 | 928 | 921
2016-03-05 19:00 | 952 | 949
2016-03-05 19:30 | 944 | 940
2016-03-05 20:00 | 934 | 928
2016-03-05 20:30 | 915 | 909
2016-03-05 21:00 | 884 | 880
2016-03-05 21:30 | 862 | 860
2016-03-05 22:00 | 843 | 839
2016-03-05 22:30 | 820 | 816
2016-03-05 23:00 | 808 | 803
2016-03-05 23:30 | 777 | 770
2016-03-06 | 726 | 719
2016-03-06 00:30 | 683 | 679
2016-03-06 01:00 | 663 | 658
2016-03-06 01:30 | 642 | 636
2016-03-06 02:00 | 625 | 617
2016-03-06 02:30 | 621 | 611
2016-03-06 03:00 | 614 | 603
2016-03-06 03:30 | 609 | 597
2016-03-06 04:00 | 607 | 595
2016-03-06 04:30 | 608 | 597
2016-03-06 05:00 | 611 | 600
2016-03-06 05:30 | 615 | 605
2016-03-06 06:00 | 613 | 601
2016-03-06 06:30 | 628 | 616
2016-03-06 07:00 | 645 | 635
2016-03-06 07:30 | 670 | 664
2016-03-06 08:00 | 688 | 685
2016-03-06 08:30 | 721 | 719
2016-03-06 09:00 | 746 | 743
2016-03-06 09:30 | 772 | 768
2016-03-06 10:00 | 777 | 774
2016-03-06 10:30 | 777 | 775
2016-03-06 11:00 | 778 | 775
2016-03-06 11:30 | 778 | 776
2016-03-06 12:00 | 785 | 783
2016-03-06 12:30 | 801 | 799
2016-03-06 13:00 | 811 | 810
2016-03-06 13:30 | 827 | 826
2016-03-06 14:00 | 843 | 843
2016-03-06 14:30 | 873 | 872
2016-03-06 15:00 | 895 | 895
2016-03-06 15:30 | 920 | 920
2016-03-06 16:00 | 942 | 942
2016-03-06 16:30 | 968 | 965
2016-03-06 17:00 | 992 | 988
2016-03-06 17:30 | 1000 | 996
2016-03-06 18:00 | 1003 | 998
2016-03-06 18:30 | 1024 | 1020
2016-03-06 19:00 | 1053 | 1052
2016-03-06 19:30 | 1031 | 1028
2016-03-06 20:00 | 1024 | 1018
2016-03-06 20:30 | 1000 | 992
2016-03-06 21:00 | 970 | 958
2016-03-06 21:30 | 923 | 914
2016-03-06 22:00 | 882 | 880
2016-03-06 22:30 | 855 | 853
2016-03-06 23:00 | 825 | 822
2016-03-06 23:30 | 783 | 779
2016-03-07 | 735 | 732
2016-03-07 00:30 | 689 | 687
2016-03-07 01:00 | 668 | 665
2016-03-07 01:30 | 649 | 645
2016-03-07 02:00 | 638 | 632
2016-03-07 02:30 | 630 | 624
2016-03-07 03:00 | 628 | 622
2016-03-07 03:30 | 631 | 625
2016-03-07 04:00 | 629 | 623
2016-03-07 04:30 | 641 | 636
2016-03-07 05:00 | 656 | 653
2016-03-07 05:30 | 690 | 689
2016-03-07 06:00 | 726 | 726
2016-03-07 06:30 | 818 | 818
2016-03-07 07:00 | 889 | 888
2016-03-07 07:30 | 943 | 943
2016-03-07 08:00 | 968 | 968
2016-03-07 08:30 | 1007 | 1004
2016-03-07 09:00 | 1016 | 1013
2016-03-07 09:30 | 1025 | 1024
2016-03-07 10:00 | 1031 | 1029
2016-03-07 10:30 | 1033 | 1032
2016-03-07 11:00 | 1048 | 1047
2016-03-07 11:30 | 1052 | 1052
2016-03-07 12:00 | 1064 | 1063
2016-03-07 12:30 | 1058 | 1058
2016-03-07 13:00 | 1065 | 1064
2016-03-07 13:30 | 1067 | 1067
2016-03-07 14:00 | 1090 | 1090
2016-03-07 14:30 | 1093 | 1092
2016-03-07 15:00 | 1088 | 1085
2016-03-07 15:30 | 1103 | 1100
2016-03-07 16:00 | 1117 | 1114
2016-03-07 16:30 | 1121 | 1116
2016-03-07 17:00 | 1138 | 1132
2016-03-07 17:30 | 1137 | 1130
2016-03-07 18:00 | 1121 | 1113
2016-03-07 18:30 | 1116 | 1107
2016-03-07 19:00 | 1149 | 1143
2016-03-07 19:30 | 1123 | 1114
2016-03-07 20:00 | 1101 | 1093
2016-03-07 20:30 | 1066 | 1057
2016-03-07 21:00 | 1016 | 1010
2016-03-07 21:30 | 967 | 959
2016-03-07 22:00 | 910 | 908
2016-03-07 22:30 | 872 | 869
2016-03-07 23:00 | 844 | 841
2016-03-07 23:30 | 775 | 775
2016-03-08 | 725 | 724
2016-03-08 00:30 | 690 | 688
2016-03-08 01:00 | 673 | 670
2016-03-08 01:30 | 653 | 649
2016-03-08 02:00 | 640 | 635
2016-03-08 02:30 | 638 | 633
2016-03-08 03:00 | 634 | 629
2016-03-08 03:30 | 633 | 627
2016-03-08 04:00 | 634 | 628
2016-03-08 04:30 | 644 | 639
2016-03-08 05:00 | 655 | 652
2016-03-08 05:30 | 688 | 687
2016-03-08 06:00 | 740 | 739
2016-03-08 06:30 | 816 | 816
2016-03-08 07:00 | 890 | 889
2016-03-08 07:30 | 953 | 951
2016-03-08 08:00 | 977 | 975
2016-03-08 08:30 | 988 | 987
2016-03-08 09:00 | 994 | 993
2016-03-08 09:30 | 1033 | 1033
2016-03-08 10:00 | 1069 | 1064
2016-03-08 10:30 | 1079 | 1074
2016-03-08 11:00 | 1073 | 1067
2016-03-08 11:30 | 1057 | 1052
2016-03-08 12:00 | 1050 | 1045
2016-03-08 12:30 | 1071 | 1066
2016-03-08 13:00 | 1088 | 1084
2016-03-08 13:30 | 1102 | 1098
2016-03-08 14:00 | 1112 | 1109
2016-03-08 14:30 | 1125 | 1124
2016-03-08 15:00 | 1139 | 1138
2016-03-08 15:30 | 1151 | 1150
2016-03-08 16:00 | 1168 | 1165
2016-03-08 16:30 | 1167 | 1164
2016-03-08 17:00 | 1192 | 1187
2016-03-08 17:30 | 1180 | 1171
2016-03-08 18:00 | 1156 | 1143
2016-03-08 18:30 | 1149 | 1134
2016-03-08 19:00 | 1190 | 1181
2016-03-08 19:30 | 1164 | 1152
2016-03-08 20:00 | 1145 | 1133
2016-03-08 20:30 | 1103 | 1096
2016-03-08 21:00 | 1040 | 1038
2016-03-08 21:30 | 989 | 988
2016-03-08 22:00 | 948 | 945
2016-03-08 22:30 | 904 | 903
2016-03-08 23:00 | 881 | 880
2016-03-08 23:30 | 832 | 829
2016-03-09 | 766 | 763
2016-03-09 00:30 | 720 | 718
2016-03-09 01:00 | 677 | 674
2016-03-09 01:30 | 641 | 635
2016-03-09 02:00 | 618 | 611
2016-03-09 02:30 | 608 | 600
2016-03-09 03:00 | 601 | 593
2016-03-09 03:30 | 601 | 592
2016-03-09 04:00 | 604 | 595
2016-03-09 04:30 | 612 | 604
2016-03-09 05:00 | 626 | 621
2016-03-09 05:30 | 676 | 674
2016-03-09 06:00 | 730 | 721
2016-03-09 06:30 | 826 | 820
2016-03-09 07:00 | 914 | 910
2016-03-09 07:30 | 1019 | 1017
2016-03-09 08:00 | 1049 | 1044
2016-03-09 08:30 | 1059 | 1055
2016-03-09 09:00 | 1067 | 1064
2016-03-09 09:30 | 1089 | 1086
2016-03-09 10:00 | 1081 | 1078
2016-03-09 10:30 | 1075 | 1072
2016-03-09 11:00 | 1068 | 1065
2016-03-09 11:30 | 1064 | 1061
2016-03-09 12:00 | 1054 | 1051
2016-03-09 12:30 | 1054 | 1051
2016-03-09 13:00 | 1061 | 1058
2016-03-09 13:30 | 1076 | 1074
2016-03-09 14:00 | 1087 | 1085
2016-03-09 14:30 | 1088 | 1086
2016-03-09 15:00 | 1070 | 1068
2016-03-09 15:30 | 1068 | 1065
2016-03-09 16:00 | 1145 | 1143
2016-03-09 16:30 | 1168 | 1165
2016-03-09 17:00 | 1182 | 1179
2016-03-09 17:30 | 1127 | 1119
2016-03-09 18:00 | 1109 | 1101
2016-03-09 18:30 | 1103 | 1097
2016-03-09 19:00 | 1131 | 1129
2016-03-09 19:30 | 1113 | 1109
2016-03-09 20:00 | 1099 | 1095
2016-03-09 20:30 | 1072 | 1067
2016-03-09 21:00 | 1024 | 1016
2016-03-09 21:30 | 973 | 965
2016-03-09 22:00 | 912 | 910
2016-03-09 22:30 | 882 | 880
2016-03-09 23:00 | 840 | 839
2016-03-09 23:30 | 796 | 795
2016-03-10 | 752 | 748
2016-03-10 00:30 | 696 | 694
2016-03-10 01:00 | 669 | 665
2016-03-10 01:30 | 648 | 643
2016-03-10 02:00 | 634 | 628
2016-03-10 02:30 | 626 | 620
2016-03-10 03:00 | 619 | 612
2016-03-10 03:30 | 621 | 614
2016-03-10 04:00 | 621 | 615
2016-03-10 04:30 | 628 | 622
2016-03-10 05:00 | 645 | 640
2016-03-10 05:30 | 683 | 679
2016-03-10 06:00 | 727 | 718
2016-03-10 06:30 | 800 | 794
2016-03-10 07:00 | 880 | 867
2016-03-10 07:30 | 934 | 928
2016-03-10 08:00 | 959 | 950
2016-03-10 08:30 | 975 | 966
2016-03-10 09:00 | 1002 | 995
2016-03-10 09:30 | 1021 | 1016
2016-03-10 10:00 | 1039 | 1035
2016-03-10 10:30 | 1054 | 1050
2016-03-10 11:00 | 1062 | 1057
2016-03-10 11:30 | 1061 | 1055
2016-03-10 12:00 | 1076 | 1072
2016-03-10 12:30 | 1095 | 1091
2016-03-10 13:00 | 1113 | 1110
2016-03-10 13:30 | 1127 | 1123
2016-03-10 14:00 | 1158 | 1143
2016-03-10 14:30 | 1169 | 1153
2016-03-10 15:00 | 1177 | 1159
2016-03-10 15:30 | 1186 | 1168
2016-03-10 16:00 | 1208 | 1189
2016-03-10 16:30 | 1220 | 1200
2016-03-10 17:00 | 1222 | 1199
2016-03-10 17:30 | 1211 | 1186
2016-03-10 18:00 | 1188 | 1175
2016-03-10 18:30 | 1185 | 1176
2016-03-10 19:00 | 1211 | 1205
2016-03-10 19:30 | 1195 | 1187
2016-03-10 20:00 | 1173 | 1169
2016-03-10 20:30 | 1137 | 1130
2016-03-10 21:00 | 1099 | 1087
2016-03-10 21:30 | 1040 | 1031
2016-03-10 22:00 | 973 | 967
2016-03-10 22:30 | 925 | 923
2016-03-10 23:00 | 894 | 893
2016-03-10 23:30 | 848 | 845
2016-03-11 | 795 | 792
2016-03-11 00:30 | 745 | 744
2016-03-11 01:00 | 717 | 715
2016-03-11 01:30 | 694 | 691
2016-03-11 02:00 | 672 | 668
2016-03-11 02:30 | 670 | 665
2016-03-11 03:00 | 667 | 661
2016-03-11 03:30 | 664 | 658
2016-03-11 04:00 | 664 | 658
2016-03-11 04:30 | 673 | 668
2016-03-11 05:00 | 687 | 684
2016-03-11 05:30 | 720 | 719
2016-03-11 06:00 | 757 | 756
2016-03-11 06:30 | 849 | 849
2016-03-11 07:00 | 930 | 924
2016-03-11 07:30 | 994 | 989
2016-03-11 08:00 | 1018 | 1016
2016-03-11 08:30 | 1049 | 1047
2016-03-11 09:00 | 1066 | 1064
2016-03-11 09:30 | 1084 | 1084
2016-03-11 10:00 | 1087 | 1086
2016-03-11 10:30 | 1098 | 1098
2016-03-11 11:00 | 1083 | 1081
2016-03-11 11:30 | 1072 | 1070
2016-03-11 12:00 | 1072 | 1071
2016-03-11 12:30 | 1084 | 1083
2016-03-11 13:00 | 1100 | 1099
2016-03-11 13:30 | 1117 | 1117
2016-03-11 14:00 | 1145 | 1145
2016-03-11 14:30 | 1154 | 1154
2016-03-11 15:00 | 1163 | 1163
2016-03-11 15:30 | 1179 | 1179
2016-03-11 16:00 | 1185 | 1185
2016-03-11 16:30 | 1188 | 1187
2016-03-11 17:00 | 1190 | 1188
2016-03-11 17:30 | 1170 | 1163
2016-03-11 18:00 | 1142 | 1130
2016-03-11 18:30 | 1134 | 1124
2016-03-11 19:00 | 1152 | 1144
2016-03-11 19:30 | 1132 | 1122
2016-03-11 20:00 | 1109 | 1102
2016-03-11 20:30 | 1074 | 1068
2016-03-11 21:00 | 1032 | 1023
2016-03-11 21:30 | 988 | 985
2016-03-11 22:00 | 940 | 937
2016-03-11 22:30 | 907 | 905
2016-03-11 23:00 | 884 | 881
2016-03-11 23:30 | 842 | 838
2016-03-12 | 790 | 785
2016-03-12 00:30 | 734 | 732
2016-03-12 01:00 | 709 | 705
2016-03-12 01:30 | 681 | 676
2016-03-12 02:00 | 671 | 665
2016-03-12 02:30 | 662 | 654
2016-03-12 03:00 | 656 | 647
2016-03-12 03:30 | 652 | 642
2016-03-12 04:00 | 646 | 636
2016-03-12 04:30 | 647 | 636
2016-03-12 05:00 | 649 | 639
2016-03-12 05:30 | 661 | 653
2016-03-12 06:00 | 674 | 667
2016-03-12 06:30 | 693 | 687
2016-03-12 07:00 | 715 | 711
2016-03-12 07:30 | 750 | 747
2016-03-12 08:00 | 775 | 770
2016-03-12 08:30 | 809 | 805
2016-03-12 09:00 | 831 | 825
2016-03-12 09:30 | 860 | 855
2016-03-12 10:00 | 864 | 861
2016-03-12 10:30 | 868 | 867
2016-03-12 11:00 | 867 | 866
2016-03-12 11:30 | 854 | 853
2016-03-12 12:00 | 863 | 862
2016-03-12 12:30 | 861 | 860
2016-03-12 13:00 | 870 | 870
2016-03-12 13:30 | 889 | 886
2016-03-12 14:00 | 902 | 899
2016-03-12 14:30 | 921 | 916
2016-03-12 15:00 | 941 | 936
2016-03-12 15:30 | 956 | 951
2016-03-12 16:00 | 983 | 973
2016-03-12 16:30 | 1005 | 995
2016-03-12 17:00 | 1022 | 1012
2016-03-12 17:30 | 1011 | 998
2016-03-12 18:00 | 1004 | 986
2016-03-12 18:30 | 1011 | 994
2016-03-12 19:00 | 1036 | 1025
2016-03-12 19:30 | 1023 | 1009
2016-03-12 20:00 | 1000 | 987
2016-03-12 20:30 | 977 | 969
2016-03-12 21:00 | 933 | 928
2016-03-12 21:30 | 907 | 905
2016-03-12 22:00 | 884 | 882
2016-03-12 22:30 | 864 | 859
2016-03-12 23:00 | 851 | 845
2016-03-12 23:30 | 810 | 809
2016-03-13 | 764 | 763
2016-03-13 00:30 | 726 | 724
2016-03-13 01:00 | 703 | 699
2016-03-13 01:30 | 677 | 673
2016-03-13 02:00 | 655 | 649
2016-03-13 02:30 | 648 | 641
2016-03-13 03:00 | 648 | 641
2016-03-13 03:30 | 651 | 644
2016-03-13 04:00 | 647 | 639
2016-03-13 04:30 | 645 | 637
2016-03-13 05:00 | 645 | 638
2016-03-13 05:30 | 656 | 651
2016-03-13 06:00 | 660 | 654
2016-03-13 06:30 | 672 | 665
2016-03-13 07:00 | 692 | 687
2016-03-13 07:30 | 721 | 719
2016-03-13 08:00 | 748 | 748
2016-03-13 08:30 | 780 | 780
2016-03-13 09:00 | 815 | 814
2016-03-13 09:30 | 836 | 833
2016-03-13 10:00 | 833 | 831
2016-03-13 10:30 | 865 | 860
2016-03-13 11:00 | 875 | 870
2016-03-13 11:30 | 885 | 880
2016-03-13 12:00 | 874 | 869
2016-03-13 12:30 | 869 | 864
2016-03-13 13:00 | 883 | 879
2016-03-13 13:30 | 889 | 885
2016-03-13 14:00 | 909 | 905
2016-03-13 14:30 | 918 | 910
2016-03-13 15:00 | 918 | 911
2016-03-13 15:30 | 931 | 925
2016-03-13 16:00 | 942 | 936
2016-03-13 16:30 | 954 | 947
2016-03-13 17:00 | 971 | 964
2016-03-13 17:30 | 985 | 969
2016-03-13 18:00 | 989 | 973
2016-03-13 18:30 | 1008 | 995
2016-03-13 19:00 | 1034 | 1024
2016-03-13 19:30 | 1037 | 1025
2016-03-13 20:00 | 1014 | 1004
2016-03-13 20:30 | 993 | 983
2016-03-13 21:00 | 955 | 939
2016-03-13 21:30 | 907 | 900
2016-03-13 22:00 | 863 | 861
2016-03-13 22:30 | 835 | 834
2016-03-13 23:00 | 814 | 812
2016-03-13 23:30 | 775 | 772
2016-03-14 | 735 | 729
2016-03-14 00:30 | 691 | 688
2016-03-14 01:00 | 669 | 665
2016-03-14 01:30 | 649 | 643
2016-03-14 02:00 | 637 | 630
2016-03-14 02:30 | 631 | 622
2016-03-14 03:00 | 624 | 614
2016-03-14 03:30 | 625 | 616
2016-03-14 04:00 | 629 | 620
2016-03-14 04:30 | 635 | 627
2016-03-14 05:00 | 647 | 642
2016-03-14 05:30 | 684 | 681
2016-03-14 06:00 | 732 | 724
2016-03-14 06:30 | 811 | 808
2016-03-14 07:00 | 896 | 891
2016-03-14 07:30 | 954 | 950
2016-03-14 08:00 | 986 | 979
2016-03-14 08:30 | 1010 | 999
2016-03-14 09:00 | 1028 | 1021
2016-03-14 09:30 | 1045 | 1039
2016-03-14 10:00 | 1053 | 1045
2016-03-14 10:30 | 1064 | 1058
2016-03-14 11:00 | 1071 | 1065
2016-03-14 11:30 | 1056 | 1048
2016-03-14 12:00 | 1051 | 1043
2016-03-14 12:30 | 1071 | 1064
2016-03-14 13:00 | 1083 | 1077
2016-03-14 13:30 | 1085 | 1080
2016-03-14 14:00 | 1090 | 1085
2016-03-14 14:30 | 1095 | 1090
2016-03-14 15:00 | 1105 | 1100
2016-03-14 15:30 | 1117 | 1108
2016-03-14 16:00 | 1136 | 1126
2016-03-14 16:30 | 1150 | 1139
2016-03-14 17:00 | 1161 | 1150
2016-03-14 17:30 | 1147 | 1132
2016-03-14 18:00 | 1126 | 1106
2016-03-14 18:30 | 1117 | 1104
2016-03-14 19:00 | 1135 | 1128
2016-03-14 19:30 | 1110 | 1107
2016-03-14 20:00 | 1110 | 1106
2016-03-14 20:30 | 1085 | 1077
2016-03-14 21:00 | 1002 | 995
2016-03-14 21:30 | 959 | 956
2016-03-14 22:00 | 908 | 907
2016-03-14 22:30 | 855 | 854
2016-03-14 23:00 | 838 | 836
2016-03-14 23:30 | 797 | 795
2016-03-15 | 743 | 738
2016-03-15 00:30 | 694 | 685
2016-03-15 01:00 | 660 | 649
2016-03-15 01:30 | 641 | 626
2016-03-15 02:00 | 644 | 629
2016-03-15 02:30 | 639 | 622
2016-03-15 03:00 | 632 | 614
2016-03-15 03:30 | 630 | 612
2016-03-15 04:00 | 624 | 606
2016-03-15 04:30 | 639 | 623
2016-03-15 05:00 | 648 | 635
2016-03-15 05:30 | 680 | 673
2016-03-15 06:00 | 718 | 713
2016-03-15 06:30 | 783 | 783
2016-03-15 07:00 | 896 | 887
2016-03-15 07:30 | 945 | 935
2016-03-15 08:00 | 960 | 954
2016-03-15 08:30 | 962 | 956
2016-03-15 09:00 | 972 | 969
2016-03-15 09:30 | 1007 | 1005
2016-03-15 10:00 | 1023 | 1018
2016-03-15 10:30 | 1028 | 1024
2016-03-15 11:00 | 1033 | 1030
2016-03-15 11:30 | 1036 | 1033
2016-03-15 12:00 | 1048 | 1046
2016-03-15 12:30 | 1062 | 1059
2016-03-15 13:00 | 1079 | 1077
2016-03-15 13:30 | 1074 | 1072
2016-03-15 14:00 | 1095 | 1094
2016-03-15 14:30 | 1103 | 1100
2016-03-15 15:00 | 1102 | 1100
2016-03-15 15:30 | 1103 | 1099
2016-03-15 16:00 | 1124 | 1121
2016-03-15 16:30 | 1139 | 1136
2016-03-15 17:00 | 1159 | 1155
2016-03-15 17:30 | 1152 | 1144
2016-03-15 18:00 | 1128 | 1114
2016-03-15 18:30 | 1120 | 1107
2016-03-15 19:00 | 1152 | 1142
2016-03-15 19:30 | 1103 | 1089
2016-03-15 20:00 | 1074 | 1066
2016-03-15 20:30 | 1040 | 1034
2016-03-15 21:00 | 997 | 987
2016-03-15 21:30 | 956 | 952
2016-03-15 22:00 | 910 | 906
2016-03-15 22:30 | 868 | 865
2016-03-15 23:00 | 831 | 827
2016-03-15 23:30 | 795 | 791
2016-03-16 | 738 | 737
2016-03-16 00:30 | 663 | 661
2016-03-16 01:00 | 624 | 621
2016-03-16 01:30 | 629 | 623
2016-03-16 02:00 | 616 | 610
2016-03-16 02:30 | 612 | 606
2016-03-16 03:00 | 606 | 600
2016-03-16 03:30 | 606 | 600
2016-03-16 04:00 | 604 | 598
2016-03-16 04:30 | 617 | 611
2016-03-16 05:00 | 630 | 627
2016-03-16 05:30 | 670 | 669
2016-03-16 06:00 | 728 | 728
2016-03-16 06:30 | 825 | 825
2016-03-16 07:00 | 893 | 891
2016-03-16 07:30 | 954 | 952
2016-03-16 08:00 | 989 | 982
2016-03-16 08:30 | 982 | 976
2016-03-16 09:00 | 995 | 991
2016-03-16 09:30 | 1008 | 1005
2016-03-16 10:00 | 1013 | 1010
2016-03-16 10:30 | 1027 | 1023
2016-03-16 11:00 | 1047 | 1043
2016-03-16 11:30 | 1034 | 1029
2016-03-16 12:00 | 1039 | 1035
2016-03-16 12:30 | 1049 | 1046
2016-03-16 13:00 | 1049 | 1046
2016-03-16 13:30 | 1050 | 1044
2016-03-16 14:00 | 1081 | 1077
2016-03-16 14:30 | 1091 | 1087
2016-03-16 15:00 | 1095 | 1090
2016-03-16 15:30 | 1105 | 1098
2016-03-16 16:00 | 1113 | 1105
2016-03-16 16:30 | 1114 | 1103
2016-03-16 17:00 | 1114 | 1105
2016-03-16 17:30 | 1098 | 1085
2016-03-16 18:00 | 1066 | 1057
2016-03-16 18:30 | 1059 | 1052
2016-03-16 19:00 | 1071 | 1065
2016-03-16 19:30 | 1045 | 1038
2016-03-16 20:00 | 1027 | 1020
2016-03-16 20:30 | 990 | 982
2016-03-16 21:00 | 941 | 932
2016-03-16 21:30 | 892 | 890
2016-03-16 22:00 | 854 | 851
2016-03-16 22:30 | 824 | 819
2016-03-16 23:00 | 789 | 785
2016-03-16 23:30 | 756 | 752
2016-03-17 | 702 | 699
2016-03-17 00:30 | 654 | 651
2016-03-17 01:00 | 610 | 604
2016-03-17 01:30 | 576 | 569
2016-03-17 02:00 | 587 | 579
2016-03-17 02:30 | 586 | 579
2016-03-17 03:00 | 585 | 578
2016-03-17 03:30 | 585 | 578
2016-03-17 04:00 | 584 | 577
2016-03-17 04:30 | 585 | 579
2016-03-17 05:00 | 617 | 613
2016-03-17 05:30 | 647 | 646
2016-03-17 06:00 | 695 | 694
2016-03-17 06:30 | 791 | 791
2016-03-17 07:00 | 859 | 858
2016-03-17 07:30 | 936 | 934
2016-03-17 08:00 | 955 | 948
2016-03-17 08:30 | 975 | 972
2016-03-17 09:00 | 979 | 977
2016-03-17 09:30 | 978 | 977
2016-03-17 10:00 | 985 | 984
2016-03-17 10:30 | 998 | 992
2016-03-17 11:00 | 1001 | 991
2016-03-17 11:30 | 1007 | 999
2016-03-17 12:00 | 1044 | 1038
2016-03-17 12:30 | 1035 | 1027
2016-03-17 13:00 | 1043 | 1036
2016-03-17 13:30 | 1045 | 1039
2016-03-17 14:00 | 1049 | 1043
2016-03-17 14:30 | 1046 | 1040
2016-03-17 15:00 | 1038 | 1030
2016-03-17 15:30 | 1037 | 1028
2016-03-17 16:00 | 1062 | 1054
2016-03-17 16:30 | 1092 | 1082
2016-03-17 17:00 | 1106 | 1095
2016-03-17 17:30 | 1076 | 1069
2016-03-17 18:00 | 1078 | 1070
2016-03-17 18:30 | 1071 | 1063
2016-03-17 19:00 | 1093 | 1087
2016-03-17 19:30 | 1075 | 1070
2016-03-17 20:00 | 1052 | 1045
2016-03-17 20:30 | 1028 | 1019
2016-03-17 21:00 | 964 | 960
2016-03-17 21:30 | 917 | 912
2016-03-17 22:00 | 867 | 865
2016-03-17 22:30 | 831 | 826
2016-03-17 23:00 | 808 | 803
2016-03-17 23:30 | 762 | 759
2016-03-18 | 717 | 711
2016-03-18 00:30 | 660 | 657
2016-03-18 01:00 | 635 | 630
2016-03-18 01:30 | 612 | 606
2016-03-18 02:00 | 598 | 591
2016-03-18 02:30 | 592 | 583
2016-03-18 03:00 | 572 | 562
2016-03-18 03:30 | 571 | 562
2016-03-18 04:00 | 567 | 557
2016-03-18 04:30 | 585 | 577
2016-03-18 05:00 | 603 | 598
2016-03-18 05:30 | 637 | 636
2016-03-18 06:00 | 679 | 678
2016-03-18 06:30 | 772 | 772
2016-03-18 07:00 | 849 | 848
2016-03-18 07:30 | 906 | 905
2016-03-18 08:00 | 927 | 922
2016-03-18 08:30 | 945 | 935
2016-03-18 09:00 | 957 | 949
2016-03-18 09:30 | 972 | 966
2016-03-18 10:00 | 978 | 973
2016-03-18 10:30 | 985 | 979
2016-03-18 11:00 | 996 | 987
2016-03-18 11:30 | 1000 | 992
2016-03-18 12:00 | 1006 | 998
2016-03-18 12:30 | 1009 | 1002
2016-03-18 13:00 | 1020 | 1014
2016-03-18 13:30 | 1026 | 1022
2016-03-18 14:00 | 1039 | 1035
2016-03-18 14:30 | 1058 | 1054
2016-03-18 15:00 | 1065 | 1063
2016-03-18 15:30 | 1090 | 1088
2016-03-18 16:00 | 1116 | 1114
2016-03-18 16:30 | 1148 | 1141
2016-03-18 17:00 | 1161 | 1150
2016-03-18 17:30 | 1141 | 1122
2016-03-18 18:00 | 1109 | 1095
2016-03-18 18:30 | 1085 | 1078
2016-03-18 19:00 | 1109 | 1106
2016-03-18 19:30 | 1107 | 1102
2016-03-18 20:00 | 1083 | 1077
2016-03-18 20:30 | 1050 | 1043
2016-03-18 21:00 | 998 | 993
2016-03-18 21:30 | 956 | 956
2016-03-18 22:00 | 917 | 917
2016-03-18 22:30 | 878 | 878
2016-03-18 23:00 | 848 | 848
2016-03-18 23:30 | 804 | 804
2016-03-19 | 749 | 747
2016-03-19 00:30 | 692 | 690
2016-03-19 01:00 | 667 | 664
2016-03-19 01:30 | 636 | 634
2016-03-19 02:00 | 617 | 613
2016-03-19 02:30 | 600 | 596
2016-03-19 03:00 | 597 | 593
2016-03-19 03:30 | 593 | 589
2016-03-19 04:00 | 592 | 587
2016-03-19 04:30 | 590 | 585
2016-03-19 05:00 | 596 | 592
2016-03-19 05:30 | 604 | 601
2016-03-19 06:00 | 621 | 618
2016-03-19 06:30 | 653 | 651
2016-03-19 07:00 | 679 | 679
2016-03-19 07:30 | 724 | 724
2016-03-19 08:00 | 754 | 754
2016-03-19 08:30 | 794 | 794
2016-03-19 09:00 | 814 | 814
2016-03-19 09:30 | 838 | 837
2016-03-19 10:00 | 862 | 860
2016-03-19 10:30 | 875 | 871
2016-03-19 11:00 | 896 | 894
2016-03-19 11:30 | 905 | 903
2016-03-19 12:00 | 922 | 921
2016-03-19 12:30 | 942 | 939
2016-03-19 13:00 | 970 | 967
2016-03-19 13:30 | 1003 | 1000
2016-03-19 14:00 | 1031 | 1024
2016-03-19 14:30 | 1051 | 1039
2016-03-19 15:00 | 1055 | 1041
2016-03-19 15:30 | 1045 | 1029
2016-03-19 16:00 | 1020 | 1013
2016-03-19 16:30 | 1007 | 998
2016-03-19 17:00 | 1004 | 995
2016-03-19 17:30 | 1003 | 994
2016-03-19 18:00 | 993 | 984
2016-03-19 18:30 | 1002 | 995
2016-03-19 19:00 | 1011 | 1005
2016-03-19 19:30 | 1001 | 993
2016-03-19 20:00 | 989 | 979
2016-03-19 20:30 | 958 | 952
2016-03-19 21:00 | 926 | 918
2016-03-19 21:30 | 888 | 883
2016-03-19 22:00 | 864 | 860
2016-03-19 22:30 | 819 | 819
2016-03-19 23:00 | 797 | 797
2016-03-19 23:30 | 766 | 764
2016-03-20 | 718 | 712
2016-03-20 00:30 | 674 | 664
2016-03-20 01:00 | 632 | 627
2016-03-20 01:30 | 604 | 598
2016-03-20 02:00 | 587 | 580
2016-03-20 02:30 | 576 | 567
2016-03-20 03:00 | 571 | 561
2016-03-20 03:30 | 572 | 562
2016-03-20 04:00 | 568 | 557
2016-03-20 04:30 | 571 | 561
2016-03-20 05:00 | 569 | 559
2016-03-20 05:30 | 573 | 565
2016-03-20 06:00 | 580 | 571
2016-03-20 06:30 | 596 | 587
2016-03-20 07:00 | 612 | 605
2016-03-20 07:30 | 640 | 636
2016-03-20 08:00 | 655 | 654
2016-03-20 08:30 | 680 | 680
2016-03-20 09:00 | 695 | 695
2016-03-20 09:30 | 727 | 726
2016-03-20 10:00 | 733 | 733
2016-03-20 10:30 | 745 | 745
2016-03-20 11:00 | 765 | 765
2016-03-20 11:30 | 772 | 771
2016-03-20 12:00 | 790 | 789
2016-03-20 12:30 | 814 | 810
2016-03-20 13:00 | 812 | 803
2016-03-20 13:30 | 798 | 789
2016-03-20 14:00 | 798 | 798
2016-03-20 14:30 | 825 | 824
2016-03-20 15:00 | 843 | 842
2016-03-20 15:30 | 870 | 869
2016-03-20 16:00 | 896 | 895
2016-03-20 16:30 | 906 | 905
2016-03-20 17:00 | 915 | 914
2016-03-20 17:30 | 934 | 933
2016-03-20 18:00 | 945 | 943
2016-03-20 18:30 | 971 | 967
2016-03-20 19:00 | 990 | 986
2016-03-20 19:30 | 980 | 975
2016-03-20 20:00 | 969 | 961
2016-03-20 20:30 | 959 | 948
2016-03-20 21:00 | 912 | 902
2016-03-20 21:30 | 865 | 862
2016-03-20 22:00 | 834 | 832
2016-03-20 22:30 | 805 | 802
2016-03-20 23:00 | 788 | 784
2016-03-20 23:30 | 742 | 740
2016-03-21 | 707 | 704
2016-03-21 00:30 | 666 | 662
2016-03-21 01:00 | 648 | 643
2016-03-21 01:30 | 632 | 625
2016-03-21 02:00 | 616 | 608
2016-03-21 02:30 | 609 | 599
2016-03-21 03:00 | 607 | 597
2016-03-21 03:30 | 607 | 598
2016-03-21 04:00 | 607 | 599
2016-03-21 04:30 | 619 | 613
2016-03-21 05:00 | 639 | 634
2016-03-21 05:30 | 667 | 664
2016-03-21 06:00 | 714 | 711
2016-03-21 06:30 | 804 | 800
2016-03-21 07:00 | 867 | 864
2016-03-21 07:30 | 926 | 924
2016-03-21 08:00 | 939 | 937
2016-03-21 08:30 | 951 | 949
2016-03-21 09:00 | 947 | 942
2016-03-21 09:30 | 997 | 990
2016-03-21 10:00 | 1009 | 1003
2016-03-21 10:30 | 1012 | 1006
2016-03-21 11:00 | 1019 | 1014
2016-03-21 11:30 | 1012 | 1005
2016-03-21 12:00 | 1011 | 1005
2016-03-21 12:30 | 1020 | 1013
2016-03-21 13:00 | 1020 | 1014
2016-03-21 13:30 | 1032 | 1027
2016-03-21 14:00 | 1012 | 1006
2016-03-21 14:30 | 1043 | 1037
2016-03-21 15:00 | 1063 | 1056
2016-03-21 15:30 | 1074 | 1066
2016-03-21 16:00 | 1093 | 1083
2016-03-21 16:30 | 1097 | 1084
2016-03-21 17:00 | 1093 | 1077
2016-03-21 17:30 | 1079 | 1062
2016-03-21 18:00 | 1078 | 1065
2016-03-21 18:30 | 1072 | 1061
2016-03-21 19:00 | 1062 | 1049
2016-03-21 19:30 | 1021 | 1009
2016-03-21 20:00 | 1007 | 1003
2016-03-21 20:30 | 978 | 977
2016-03-21 21:00 | 931 | 927
2016-03-21 21:30 | 898 | 892
2016-03-21 22:00 | 855 | 849
2016-03-21 22:30 | 809 | 805
2016-03-21 23:00 | 789 | 783
2016-03-21 23:30 | 744 | 736
2016-03-22 | 695 | 694
2016-03-22 00:30 | 659 | 656
2016-03-22 01:00 | 637 | 633
2016-03-22 01:30 | 617 | 612
2016-03-22 02:00 | 604 | 599
2016-03-22 02:30 | 596 | 588
2016-03-22 03:00 | 591 | 583
2016-03-22 03:30 | 593 | 586
2016-03-22 04:00 | 590 | 583
2016-03-22 04:30 | 606 | 600
2016-03-22 05:00 | 621 | 618
2016-03-22 05:30 | 652 | 650
2016-03-22 06:00 | 700 | 697
2016-03-22 06:30 | 782 | 781
2016-03-22 07:00 | 838 | 837
2016-03-22 07:30 | 886 | 886
2016-03-22 08:00 | 899 | 897
2016-03-22 08:30 | 896 | 894
2016-03-22 09:00 | 897 | 893
2016-03-22 09:30 | 898 | 895
2016-03-22 10:00 | 899 | 896
2016-03-22 10:30 | 901 | 899
2016-03-22 11:00 | 916 | 914
2016-03-22 11:30 | 923 | 920
2016-03-22 12:00 | 942 | 939
2016-03-22 12:30 | 956 | 951
2016-03-22 13:00 | 971 | 967
2016-03-22 13:30 | 978 | 974
2016-03-22 14:00 | 989 | 985
2016-03-22 14:30 | 990 | 986
2016-03-22 15:00 | 1002 | 997
2016-03-22 15:30 | 1008 | 1002
2016-03-22 16:00 | 1027 | 1019
2016-03-22 16:30 | 1049 | 1040
2016-03-22 17:00 | 1069 | 1060
2016-03-22 17:30 | 1065 | 1052
2016-03-22 18:00 | 1069 | 1053
2016-03-22 18:30 | 1085 | 1071
2016-03-22 19:00 | 1084 | 1070
2016-03-22 19:30 | 1055 | 1045
2016-03-22 20:00 | 1035 | 1028
2016-03-22 20:30 | 1011 | 1006
2016-03-22 21:00 | 954 | 949
2016-03-22 21:30 | 913 | 908
2016-03-22 22:00 | 859 | 859
2016-03-22 22:30 | 825 | 824
2016-03-22 23:00 | 801 | 801
2016-03-22 23:30 | 753 | 753
2016-03-23 | 705 | 704
2016-03-23 00:30 | 660 | 657
2016-03-23 01:00 | 642 | 638
2016-03-23 01:30 | 623 | 617
2016-03-23 02:00 | 614 | 607
2016-03-23 02:30 | 604 | 596
2016-03-23 03:00 | 602 | 592
2016-03-23 03:30 | 602 | 593
2016-03-23 04:00 | 602 | 593
2016-03-23 04:30 | 612 | 605
2016-03-23 05:00 | 629 | 624
2016-03-23 05:30 | 664 | 660
2016-03-23 06:00 | 708 | 706
2016-03-23 06:30 | 794 | 793
2016-03-23 07:00 | 848 | 845
2016-03-23 07:30 | 919 | 914
2016-03-23 08:00 | 942 | 937
2016-03-23 08:30 | 947 | 942
2016-03-23 09:00 | 929 | 926
2016-03-23 09:30 | 933 | 931
2016-03-23 10:00 | 930 | 929
2016-03-23 10:30 | 928 | 927
2016-03-23 11:00 | 942 | 940
2016-03-23 11:30 | 948 | 946
2016-03-23 12:00 | 971 | 969
2016-03-23 12:30 | 978 | 976
2016-03-23 13:00 | 982 | 981
2016-03-23 13:30 | 988 | 987
2016-03-23 14:00 | 997 | 996
2016-03-23 14:30 | 985 | 981
2016-03-23 15:00 | 1011 | 1005
2016-03-23 15:30 | 1031 | 1025
2016-03-23 16:00 | 1049 | 1043
2016-03-23 16:30 | 1055 | 1047
2016-03-23 17:00 | 1071 | 1060
2016-03-23 17:30 | 1067 | 1051
2016-03-23 18:00 | 1048 | 1035
2016-03-23 18:30 | 1054 | 1044
2016-03-23 19:00 | 1132 | 1121
2016-03-23 19:30 | 1082 | 1070
2016-03-23 20:00 | 1050 | 1041
2016-03-23 20:30 | 1014 | 1007
2016-03-23 21:00 | 971 | 960
2016-03-23 21:30 | 920 | 916
2016-03-23 22:00 | 885 | 884
2016-03-23 22:30 | 843 | 841
2016-03-23 23:00 | 827 | 825
2016-03-23 23:30 | 784 | 781
2016-03-24 | 731 | 727
2016-03-24 00:30 | 684 | 680
2016-03-24 01:00 | 660 | 653
2016-03-24 01:30 | 638 | 630
2016-03-24 02:00 | 631 | 622
2016-03-24 02:30 | 620 | 611
2016-03-24 03:00 | 614 | 604
2016-03-24 03:30 | 614 | 603
2016-03-24 04:00 | 610 | 601
2016-03-24 04:30 | 620 | 614
2016-03-24 05:00 | 634 | 629
2016-03-24 05:30 | 671 | 668
2016-03-24 06:00 | 711 | 710
2016-03-24 06:30 | 784 | 783
2016-03-24 07:00 | 856 | 856
2016-03-24 07:30 | 913 | 913
2016-03-24 08:00 | 929 | 928
2016-03-24 08:30 | 940 | 939
2016-03-24 09:00 | 962 | 962
2016-03-24 09:30 | 961 | 961
2016-03-24 10:00 | 954 | 953
2016-03-24 10:30 | 945 | 945
2016-03-24 11:00 | 959 | 959
2016-03-24 11:30 | 960 | 960
2016-03-24 12:00 | 978 | 978
2016-03-24 12:30 | 989 | 989
2016-03-24 13:00 | 984 | 984
2016-03-24 13:30 | 987 | 987
2016-03-24 14:00 | 1001 | 1001
2016-03-24 14:30 | 1013 | 1013
2016-03-24 15:00 | 1017 | 1017
2016-03-24 15:30 | 1018 | 1017
2016-03-24 16:00 | 1050 | 1049
2016-03-24 16:30 | 1063 | 1062
2016-03-24 17:00 | 1067 | 1065
2016-03-24 17:30 | 1056 | 1053
2016-03-24 18:00 | 1047 | 1041
2016-03-24 18:30 | 1054 | 1050
2016-03-24 19:00 | 1062 | 1060
2016-03-24 19:30 | 1035 | 1031
2016-03-24 20:00 | 1015 | 1011
2016-03-24 20:30 | 994 | 989
2016-03-24 21:00 | 951 | 945
2016-03-24 21:30 | 902 | 899
2016-03-24 22:00 | 864 | 863
2016-03-24 22:30 | 840 | 840
2016-03-24 23:00 | 828 | 827
2016-03-24 23:30 | 773 | 773
2016-03-25 | 720 | 718
2016-03-25 00:30 | 667 | 663
2016-03-25 01:00 | 645 | 639
2016-03-25 01:30 | 620 | 612
2016-03-25 02:00 | 608 | 597
2016-03-25 02:30 | 598 | 585
2016-03-25 03:00 | 592 | 579
2016-03-25 03:30 | 590 | 576
2016-03-25 04:00 | 588 | 574
2016-03-25 04:30 | 585 | 571
2016-03-25 05:00 | 584 | 571
2016-03-25 05:30 | 594 | 583
2016-03-25 06:00 | 603 | 591
2016-03-25 06:30 | 623 | 611
2016-03-25 07:00 | 633 | 624
2016-03-25 07:30 | 654 | 650
2016-03-25 08:00 | 667 | 665
2016-03-25 08:30 | 681 | 680
2016-03-25 09:00 | 695 | 693
2016-03-25 09:30 | 709 | 708
2016-03-25 10:00 | 714 | 713
2016-03-25 10:30 | 716 | 715
2016-03-25 11:00 | 716 | 714
2016-03-25 11:30 | 701 | 699
2016-03-25 12:00 | 701 | 699
2016-03-25 12:30 | 711 | 709
2016-03-25 13:00 | 714 | 712
2016-03-25 13:30 | 727 | 726
2016-03-25 14:00 | 734 | 733
2016-03-25 14:30 | 748 | 747
2016-03-25 15:00 | 767 | 765
2016-03-25 15:30 | 797 | 795
2016-03-25 16:00 | 816 | 814
2016-03-25 16:30 | 840 | 838
2016-03-25 17:00 | 868 | 863
2016-03-25 17:30 | 880 | 871
2016-03-25 18:00 | 878 | 868
2016-03-25 18:30 | 897 | 891
2016-03-25 19:00 | 910 | 904
2016-03-25 19:30 | 878 | 874
2016-03-25 20:00 | 867 | 865
2016-03-25 20:30 | 851 | 847
2016-03-25 21:00 | 816 | 811
2016-03-25 21:30 | 794 | 793
2016-03-25 22:00 | 777 | 777
2016-03-25 22:30 | 763 | 762
2016-03-25 23:00 | 757 | 756
2016-03-25 23:30 | 724 | 721
2016-03-26 | 687 | 684
2016-03-26 00:30 | 651 | 645
2016-03-26 01:00 | 621 | 612
2016-03-26 01:30 | 604 | 592
2016-03-26 02:00 | 590 | 577
2016-03-26 02:30 | 587 | 572
2016-03-26 03:00 | 582 | 568
2016-03-26 03:30 | 580 | 566
2016-03-26 04:00 | 577 | 561
2016-03-26 04:30 | 576 | 560
2016-03-26 05:00 | 581 | 567
2016-03-26 05:30 | 586 | 574
2016-03-26 06:00 | 598 | 586
2016-03-26 06:30 | 615 | 602
2016-03-26 07:00 | 633 | 624
2016-03-26 07:30 | 658 | 653
2016-03-26 08:00 | 684 | 682
2016-03-26 08:30 | 713 | 711
2016-03-26 09:00 | 729 | 726
2016-03-26 09:30 | 737 | 735
2016-03-26 10:00 | 737 | 737
2016-03-26 10:30 | 741 | 740
2016-03-26 11:00 | 743 | 740
2016-03-26 11:30 | 742 | 740
2016-03-26 12:00 | 749 | 748
2016-03-26 12:30 | 758 | 756
2016-03-26 13:00 | 773 | 772
2016-03-26 13:30 | 806 | 804
2016-03-26 14:00 | 836 | 830
2016-03-26 14:30 | 837 | 831
2016-03-26 15:00 | 859 | 854
2016-03-26 15:30 | 900 | 897
2016-03-26 16:00 | 900 | 897
2016-03-26 16:30 | 931 | 923
2016-03-26 17:00 | 950 | 942
2016-03-26 17:30 | 950 | 940
2016-03-26 18:00 | 944 | 933
2016-03-26 18:30 | 954 | 945
2016-03-26 19:00 | 964 | 955
2016-03-26 19:30 | 943 | 933
2016-03-26 20:00 | 924 | 919
2016-03-26 20:30 | 915 | 910
2016-03-26 21:00 | 871 | 866
2016-03-26 21:30 | 843 | 839
2016-03-26 22:00 | 819 | 815
2016-03-26 22:30 | 804 | 798
2016-03-26 23:00 | 781 | 778
2016-03-26 23:30 | 739 | 737
2016-03-27 | 698 | 694
2016-03-27 00:30 | 657 | 651
2016-03-27 01:00 | 639 | 631
2016-03-27 01:30 | 618 | 609
2016-03-27 02:00 | 608 | 598
2016-03-27 02:30 | 597 | 585
2016-03-27 03:00 | 594 | 581
2016-03-27 03:30 | 589 | 576
2016-03-27 04:00 | 585 | 572
2016-03-27 04:30 | 582 | 568
2016-03-27 05:00 | 586 | 573
2016-03-27 05:30 | 594 | 581
2016-03-27 06:00 | 605 | 593
2016-03-27 06:30 | 616 | 604
2016-03-27 07:00 | 633 | 621
2016-03-27 07:30 | 656 | 648
2016-03-27 08:00 | 675 | 669
2016-03-27 08:30 | 697 | 694
2016-03-27 09:00 | 712 | 709
2016-03-27 09:30 | 715 | 714
2016-03-27 10:00 | 732 | 731
2016-03-27 10:30 | 751 | 751
2016-03-27 11:00 | 765 | 765
2016-03-27 11:30 | 761 | 759
2016-03-27 12:00 | 755 | 753
2016-03-27 12:30 | 745 | 743
2016-03-27 13:00 | 740 | 737
2016-03-27 13:30 | 731 | 728
2016-03-27 14:00 | 728 | 724
2016-03-27 14:30 | 723 | 719
2016-03-27 15:00 | 736 | 732
2016-03-27 15:30 | 760 | 757
2016-03-27 16:00 | 769 | 766
2016-03-27 16:30 | 780 | 777
2016-03-27 17:00 | 805 | 803
2016-03-27 17:30 | 814 | 812
2016-03-27 18:00 | 831 | 830
2016-03-27 18:30 | 853 | 851
2016-03-27 19:00 | 862 | 859
2016-03-27 19:30 | 846 | 842
2016-03-27 20:00 | 845 | 841
2016-03-27 20:30 | 834 | 827
2016-03-27 21:00 | 796 | 793
2016-03-27 21:30 | 780 | 779
2016-03-27 22:00 | 761 | 758
2016-03-27 22:30 | 743 | 741
2016-03-27 23:00 | 742 | 740
2016-03-27 23:30 | 713 | 710
2016-03-28 | 675 | 669
2016-03-28 00:30 | 646 | 637
2016-03-28 01:00 | 625 | 614
2016-03-28 01:30 | 606 | 593
2016-03-28 02:00 | 593 | 578
2016-03-28 02:30 | 590 | 575
2016-03-28 03:00 | 584 | 567
2016-03-28 03:30 | 582 | 565
2016-03-28 04:00 | 580 | 563
2016-03-28 04:30 | 581 | 566
2016-03-28 05:00 | 583 | 568
2016-03-28 05:30 | 598 | 585
2016-03-28 06:00 | 603 | 591
2016-03-28 06:30 | 623 | 614
2016-03-28 07:00 | 643 | 636
2016-03-28 07:30 | 668 | 665
2016-03-28 08:00 | 690 | 689
2016-03-28 08:30 | 715 | 715
2016-03-28 09:00 | 736 | 736
2016-03-28 09:30 | 768 | 767
2016-03-28 10:00 | 782 | 782
2016-03-28 10:30 | 779 | 779
2016-03-28 11:00 | 776 | 775
2016-03-28 11:30 | 768 | 767
2016-03-28 12:00 | 776 | 775
2016-03-28 12:30 | 786 | 785
2016-03-28 13:00 | 792 | 790
2016-03-28 13:30 | 792 | 790
2016-03-28 14:00 | 815 | 813
2016-03-28 14:30 | 828 | 826
2016-03-28 15:00 | 836 | 835
2016-03-28 15:30 | 854 | 854
2016-03-28 16:00 | 875 | 875
2016-03-28 16:30 | 893 | 893
2016-03-28 17:00 | 919 | 918
2016-03-28 17:30 | 933 | 930
2016-03-28 18:00 | 943 | 938
2016-03-28 18:30 | 955 | 952
2016-03-28 19:00 | 953 | 950
2016-03-28 19:30 | 964 | 959
2016-03-28 20:00 | 950 | 946
2016-03-28 20:30 | 940 | 935
2016-03-28 21:00 | 877 | 874
2016-03-28 21:30 | 842 | 841
2016-03-28 22:00 | 817 | 814
2016-03-28 22:30 | 786 | 784
2016-03-28 23:00 | 766 | 764
2016-03-28 23:30 | 731 | 727
2016-03-29 | 694 | 689
2016-03-29 00:30 | 653 | 647
2016-03-29 01:00 | 634 | 626
2016-03-29 01:30 | 621 | 611
2016-03-29 02:00 | 605 | 595
2016-03-29 02:30 | 601 | 590
2016-03-29 03:00 | 598 | 586
2016-03-29 03:30 | 599 | 587
2016-03-29 04:00 | 599 | 587
2016-03-29 04:30 | 606 | 596
2016-03-29 05:00 | 620 | 612
2016-03-29 05:30 | 649 | 644
2016-03-29 06:00 | 680 | 678
2016-03-29 06:30 | 750 | 750
2016-03-29 07:00 | 803 | 802
2016-03-29 07:30 | 864 | 859
2016-03-29 08:00 | 892 | 884
2016-03-29 08:30 | 920 | 917
2016-03-29 09:00 | 938 | 931
2016-03-29 09:30 | 945 | 938
2016-03-29 10:00 | 949 | 941
2016-03-29 10:30 | 967 | 954
2016-03-29 11:00 | 969 | 957
2016-03-29 11:30 | 969 | 957
2016-03-29 12:00 | 978 | 968
2016-03-29 12:30 | 979 | 970
2016-03-29 13:00 | 992 | 984
2016-03-29 13:30 | 1009 | 1001
2016-03-29 14:00 | 1029 | 1021
2016-03-29 14:30 | 1059 | 1052
2016-03-29 15:00 | 1082 | 1076
2016-03-29 15:30 | 1108 | 1102
2016-03-29 16:00 | 1137 | 1131
2016-03-29 16:30 | 1153 | 1147
2016-03-29 17:00 | 1167 | 1160
2016-03-29 17:30 | 1164 | 1152
2016-03-29 18:00 | 1136 | 1124
2016-03-29 18:30 | 1142 | 1132
2016-03-29 19:00 | 1149 | 1138
2016-03-29 19:30 | 1108 | 1096
2016-03-29 20:00 | 1081 | 1078
2016-03-29 20:30 | 1057 | 1053
2016-03-29 21:00 | 999 | 997
2016-03-29 21:30 | 948 | 944
2016-03-29 22:00 | 903 | 899
2016-03-29 22:30 | 863 | 859
2016-03-29 23:00 | 838 | 835
2016-03-29 23:30 | 787 | 787
2016-03-30 | 740 | 740
2016-03-30 00:30 | 695 | 693
2016-03-30 01:00 | 669 | 666
2016-03-30 01:30 | 658 | 654
2016-03-30 02:00 | 639 | 633
2016-03-30 02:30 | 640 | 634
2016-03-30 03:00 | 632 | 626
2016-03-30 03:30 | 634 | 627
2016-03-30 04:00 | 634 | 627
2016-03-30 04:30 | 643 | 637
2016-03-30 05:00 | 650 | 646
2016-03-30 05:30 | 682 | 680
2016-03-30 06:00 | 717 | 715
2016-03-30 06:30 | 782 | 780
2016-03-30 07:00 | 834 | 830
2016-03-30 07:30 | 901 | 899
2016-03-30 08:00 | 938 | 934
2016-03-30 08:30 | 952 | 947
2016-03-30 09:00 | 973 | 971
2016-03-30 09:30 | 988 | 987
2016-03-30 10:00 | 993 | 993
2016-03-30 10:30 | 985 | 984
2016-03-30 11:00 | 987 | 987
2016-03-30 11:30 | 993 | 993
2016-03-30 12:00 | 1003 | 1003
2016-03-30 12:30 | 1017 | 1017
2016-03-30 13:00 | 1062 | 1061
2016-03-30 13:30 | 1105 | 1102
2016-03-30 14:00 | 1125 | 1122
2016-03-30 14:30 | 1162 | 1160
2016-03-30 15:00 | 1184 | 1184
2016-03-30 15:30 | 1189 | 1188
2016-03-30 16:00 | 1184 | 1183
2016-03-30 16:30 | 1174 | 1170
2016-03-30 17:00 | 1163 | 1157
2016-03-30 17:30 | 1143 | 1137
2016-03-30 18:00 | 1129 | 1126
2016-03-30 18:30 | 1119 | 1116
2016-03-30 19:00 | 1120 | 1115
2016-03-30 19:30 | 1087 | 1080
2016-03-30 20:00 | 1060 | 1059
2016-03-30 20:30 | 1031 | 1031
2016-03-30 21:00 | 984 | 984
2016-03-30 21:30 | 936 | 936
2016-03-30 22:00 | 891 | 891
2016-03-30 22:30 | 860 | 859
2016-03-30 23:00 | 842 | 840
2016-03-30 23:30 | 795 | 795
2016-03-31 | 738 | 737
2016-03-31 00:30 | 699 | 696
2016-03-31 01:00 | 680 | 676
2016-03-31 01:30 | 650 | 646
2016-03-31 02:00 | 637 | 633
2016-03-31 02:30 | 635 | 630
2016-03-31 03:00 | 635 | 629
2016-03-31 03:30 | 633 | 628
2016-03-31 04:00 | 633 | 627
2016-03-31 04:30 | 638 | 633
2016-03-31 05:00 | 648 | 644
2016-03-31 05:30 | 681 | 680
2016-03-31 06:00 | 717 | 717
2016-03-31 06:30 | 778 | 778
2016-03-31 07:00 | 841 | 838
2016-03-31 07:30 | 885 | 884
2016-03-31 08:00 | 913 | 911
2016-03-31 08:30 | 933 | 929
2016-03-31 09:00 | 944 | 943
2016-03-31 09:30 | 953 | 952
2016-03-31 10:00 | 968 | 967
2016-03-31 10:30 | 976 | 976
2016-03-31 11:00 | 996 | 994
2016-03-31 11:30 | 1005 | 1000
2016-03-31 12:00 | 1023 | 1019
2016-03-31 12:30 | 1045 | 1036
2016-03-31 13:00 | 1051 | 1042
2016-03-31 13:30 | 1066 | 1059
2016-03-31 14:00 | 1089 | 1082
2016-03-31 14:30 | 1091 | 1084
2016-03-31 15:00 | 1102 | 1095
2016-03-31 15:30 | 1116 | 1107
2016-03-31 16:00 | 1134 | 1123
2016-03-31 16:30 | 1154 | 1142
2016-03-31 17:00 | 1166 | 1153
2016-03-31 17:30 | 1158 | 1139
2016-03-31 18:00 | 1144 | 1126
2016-03-31 18:30 | 1142 | 1132
2016-03-31 19:00 | 1145 | 1133
2016-03-31 19:30 | 1101 | 1091
2016-03-31 20:00 | 1075 | 1067
2016-03-31 20:30 | 1043 | 1035
2016-03-31 21:00 | 987 | 981
2016-03-31 21:30 | 935 | 931
2016-03-31 22:00 | 888 | 881
2016-03-31 22:30 | 857 | 854
2016-03-31 23:00 | 841 | 838
2016-03-31 23:30 | 787 | 787
2016-04-01 | 729 | 728
2016-04-01 00:30 | 692 | 689
2016-04-01 01:00 | 664 | 660
2016-04-01 01:30 | 635 | 629
2016-04-01 02:00 | 616 | 609
2016-04-01 02:30 | 598 | 590
2016-04-01 03:00 | 591 | 583
2016-04-01 03:30 | 594 | 586
2016-04-01 04:00 | 593 | 584
2016-04-01 04:30 | 593 | 586
2016-04-01 05:00 | 609 | 604
2016-04-01 05:30 | 645 | 643
2016-04-01 06:00 | 677 | 676
2016-04-01 06:30 | 754 | 754
2016-04-01 07:00 | 816 | 816
2016-04-01 07:30 | 865 | 865
2016-04-01 08:00 | 892 | 891
2016-04-01 08:30 | 920 | 917
2016-04-01 09:00 | 925 | 922
2016-04-01 09:30 | 930 | 928
2016-04-01 10:00 | 946 | 945
2016-04-01 10:30 | 957 | 955
2016-04-01 11:00 | 958 | 956
2016-04-01 11:30 | 945 | 944
2016-04-01 12:00 | 960 | 958
2016-04-01 12:30 | 966 | 964
2016-04-01 13:00 | 974 | 971
2016-04-01 13:30 | 978 | 976
2016-04-01 14:00 | 1012 | 1010
2016-04-01 14:30 | 1031 | 1030
2016-04-01 15:00 | 1048 | 1047
2016-04-01 15:30 | 1070 | 1067
2016-04-01 16:00 | 1087 | 1085
2016-04-01 16:30 | 1108 | 1105
2016-04-01 17:00 | 1116 | 1111
2016-04-01 17:30 | 1090 | 1082
2016-04-01 18:00 | 1075 | 1069
2016-04-01 18:30 | 1072 | 1066
2016-04-01 19:00 | 1069 | 1063
2016-04-01 19:30 | 1040 | 1033
2016-04-01 20:00 | 1023 | 1015
2016-04-01 20:30 | 1016 | 1007
2016-04-01 21:00 | 966 | 962
2016-04-01 21:30 | 932 | 926
2016-04-01 22:00 | 908 | 900
2016-04-01 22:30 | 883 | 882
2016-04-01 23:00 | 863 | 862
2016-04-01 23:30 | 816 | 813
2016-04-02 | 767 | 766
2016-04-02 00:30 | 721 | 720
2016-04-02 01:00 | 692 | 689
2016-04-02 01:30 | 658 | 653
2016-04-02 02:00 | 636 | 629
2016-04-02 02:30 | 627 | 620
2016-04-02 03:00 | 618 | 611
2016-04-02 03:30 | 617 | 608
2016-04-02 04:00 | 617 | 609
2016-04-02 04:30 | 615 | 606
2016-04-02 05:00 | 611 | 603
2016-04-02 05:30 | 622 | 615
2016-04-02 06:00 | 634 | 628
2016-04-02 06:30 | 667 | 662
2016-04-02 07:00 | 690 | 688
2016-04-02 07:30 | 728 | 727
2016-04-02 08:00 | 750 | 750
2016-04-02 08:30 | 775 | 775
2016-04-02 09:00 | 803 | 802
2016-04-02 09:30 | 831 | 831
2016-04-02 10:00 | 860 | 859
2016-04-02 10:30 | 859 | 857
2016-04-02 11:00 | 860 | 857
2016-04-02 11:30 | 849 | 845
2016-04-02 12:00 | 850 | 847
2016-04-02 12:30 | 856 | 853
2016-04-02 13:00 | 870 | 868
2016-04-02 13:30 | 885 | 884
2016-04-02 14:00 | 904 | 903
2016-04-02 14:30 | 910 | 910
2016-04-02 15:00 | 939 | 934
2016-04-02 15:30 | 969 | 967
2016-04-02 16:00 | 997 | 995
2016-04-02 16:30 | 1018 | 1016
2016-04-02 17:00 | 1034 | 1033
2016-04-02 17:30 | 1025 | 1022
2016-04-02 18:00 | 1011 | 1007
2016-04-02 18:30 | 1026 | 1024
2016-04-02 19:00 | 1030 | 1028
2016-04-02 19:30 | 1001 | 997
2016-04-02 20:00 | 986 | 980
2016-04-02 20:30 | 976 | 972
2016-04-02 21:00 | 929 | 926
2016-04-02 21:30 | 899 | 898
2016-04-02 22:00 | 875 | 871
2016-04-02 22:30 | 861 | 855
2016-04-02 23:00 | 854 | 847
2016-04-02 23:30 | 818 | 808
2016-04-03 | 754 | 750
2016-04-03 00:30 | 702 | 701
2016-04-03 01:00 | 671 | 669
2016-04-03 01:30 | 640 | 636
2016-04-03 02:00 | 616 | 611
2016-04-03 02:30 | 602 | 596
2016-04-03 03:00 | 592 | 585
2016-04-03 03:30 | 590 | 583
2016-04-03 04:00 | 586 | 577
2016-04-03 04:30 | 588 | 580
2016-04-03 05:00 | 587 | 578
2016-04-03 05:30 | 600 | 593
2016-04-03 06:00 | 610 | 602
2016-04-03 06:30 | 628 | 620
2016-04-03 07:00 | 647 | 641
2016-04-03 07:30 | 679 | 676
2016-04-03 08:00 | 701 | 700
2016-04-03 08:30 | 720 | 720
2016-04-03 09:00 | 738 | 737
2016-04-03 09:30 | 747 | 747
2016-04-03 10:00 | 755 | 755
2016-04-03 10:30 | 764 | 764
2016-04-03 11:00 | 775 | 775
2016-04-03 11:30 | 781 | 781
2016-04-03 12:00 | 793 | 793
2016-04-03 12:30 | 803 | 802
2016-04-03 13:00 | 808 | 807
2016-04-03 13:30 | 825 | 824
2016-04-03 14:00 | 844 | 844
2016-04-03 14:30 | 861 | 861
2016-04-03 15:00 | 890 | 890
2016-04-03 15:30 | 921 | 920
2016-04-03 16:00 | 942 | 941
2016-04-03 16:30 | 959 | 958
2016-04-03 17:00 | 979 | 978
2016-04-03 17:30 | 993 | 992
2016-04-03 18:00 | 1003 | 1003
2016-04-03 18:30 | 1043 | 1042
2016-04-03 19:00 | 1036 | 1035
2016-04-03 19:30 | 1004 | 1002
2016-04-03 20:00 | 1001 | 997
2016-04-03 20:30 | 976 | 973
2016-04-03 21:00 | 931 | 925
2016-04-03 21:30 | 893 | 892
2016-04-03 22:00 | 862 | 860
2016-04-03 22:30 | 839 | 834
2016-04-03 23:00 | 829 | 826
2016-04-03 23:30 | 787 | 786
2016-04-04 | 741 | 741
2016-04-04 00:30 | 689 | 688
2016-04-04 01:00 | 663 | 661
2016-04-04 01:30 | 634 | 630
2016-04-04 02:00 | 614 | 609
2016-04-04 02:30 | 602 | 596
2016-04-04 03:00 | 598 | 592
2016-04-04 03:30 | 598 | 592
2016-04-04 04:00 | 601 | 595
2016-04-04 04:30 | 610 | 605
2016-04-04 05:00 | 627 | 623
2016-04-04 05:30 | 672 | 671
2016-04-04 06:00 | 729 | 726
2016-04-04 06:30 | 789 | 787
2016-04-04 07:00 | 846 | 842
2016-04-04 07:30 | 906 | 904
2016-04-04 08:00 | 931 | 929
2016-04-04 08:30 | 952 | 952
2016-04-04 09:00 | 969 | 968
2016-04-04 09:30 | 977 | 977
2016-04-04 10:00 | 980 | 980
2016-04-04 10:30 | 978 | 978
2016-04-04 11:00 | 978 | 978
2016-04-04 11:30 | 967 | 967
2016-04-04 12:00 | 972 | 972
2016-04-04 12:30 | 965 | 965
2016-04-04 13:00 | 972 | 972
2016-04-04 13:30 | 970 | 969
2016-04-04 14:00 | 987 | 987
2016-04-04 14:30 | 1007 | 1007
2016-04-04 15:00 | 1031 | 1031
2016-04-04 15:30 | 1050 | 1050
2016-04-04 16:00 | 1064 | 1064
2016-04-04 16:30 | 1075 | 1074
2016-04-04 17:00 | 1092 | 1090
2016-04-04 17:30 | 1090 | 1088
2016-04-04 18:00 | 1085 | 1083
2016-04-04 18:30 | 1095 | 1094
2016-04-04 19:00 | 1088 | 1086
2016-04-04 19:30 | 1053 | 1051
2016-04-04 20:00 | 1040 | 1038
2016-04-04 20:30 | 1018 | 1016
2016-04-04 21:00 | 967 | 963
2016-04-04 21:30 | 924 | 922
2016-04-04 22:00 | 891 | 888
2016-04-04 22:30 | 876 | 871
2016-04-04 23:00 | 855 | 853
2016-04-04 23:30 | 809 | 808
2016-04-05 | 752 | 750
2016-04-05 00:30 | 706 | 705
2016-04-05 01:00 | 678 | 676
2016-04-05 01:30 | 651 | 647
2016-04-05 02:00 | 624 | 619
2016-04-05 02:30 | 606 | 601
2016-04-05 03:00 | 597 | 590
2016-04-05 03:30 | 595 | 589
2016-04-05 04:00 | 594 | 588
2016-04-05 04:30 | 621 | 617
2016-04-05 05:00 | 624 | 620
2016-04-05 05:30 | 661 | 660
2016-04-05 06:00 | 708 | 708
2016-04-05 06:30 | 773 | 772
2016-04-05 07:00 | 816 | 816
2016-04-05 07:30 | 887 | 883
2016-04-05 08:00 | 902 | 893
2016-04-05 08:30 | 912 | 908
2016-04-05 09:00 | 934 | 921
2016-04-05 09:30 | 941 | 931
2016-04-05 10:00 | 942 | 934
2016-04-05 10:30 | 955 | 949
2016-04-05 11:00 | 946 | 940
2016-04-05 11:30 | 932 | 926
2016-04-05 12:00 | 935 | 929
2016-04-05 12:30 | 929 | 922
2016-04-05 13:00 | 933 | 926
2016-04-05 13:30 | 942 | 936
2016-04-05 14:00 | 958 | 952
2016-04-05 14:30 | 967 | 962
2016-04-05 15:00 | 989 | 984
2016-04-05 15:30 | 1007 | 1002
2016-04-05 16:00 | 1036 | 1031
2016-04-05 16:30 | 1077 | 1072
2016-04-05 17:00 | 1090 | 1086
2016-04-05 17:30 | 1083 | 1075
2016-04-05 18:00 | 1083 | 1073
2016-04-05 18:30 | 1093 | 1085
2016-04-05 19:00 | 1083 | 1077
2016-04-05 19:30 | 1044 | 1039
2016-04-05 20:00 | 1021 | 1020
2016-04-05 20:30 | 997 | 995
2016-04-05 21:00 | 953 | 947
2016-04-05 21:30 | 908 | 906
2016-04-05 22:00 | 875 | 873
2016-04-05 22:30 | 840 | 837
2016-04-05 23:00 | 831 | 827
2016-04-05 23:30 | 785 | 778
2016-04-06 | 727 | 722
2016-04-06 00:30 | 680 | 678
2016-04-06 01:00 | 655 | 652
2016-04-06 01:30 | 630 | 625
2016-04-06 02:00 | 607 | 600
2016-04-06 02:30 | 597 | 590
2016-04-06 03:00 | 589 | 582
2016-04-06 03:30 | 588 | 581
2016-04-06 04:00 | 601 | 594
2016-04-06 04:30 | 610 | 604
2016-04-06 05:00 | 616 | 611
2016-04-06 05:30 | 658 | 656
2016-04-06 06:00 | 702 | 701
2016-04-06 06:30 | 766 | 766
2016-04-06 07:00 | 821 | 821
2016-04-06 07:30 | 878 | 878
2016-04-06 08:00 | 904 | 900
2016-04-06 08:30 | 919 | 915
2016-04-06 09:00 | 920 | 917
2016-04-06 09:30 | 933 | 931
2016-04-06 10:00 | 944 | 944
2016-04-06 10:30 | 951 | 951
2016-04-06 11:00 | 958 | 957
2016-04-06 11:30 | 954 | 950
2016-04-06 12:00 | 950 | 946
2016-04-06 12:30 | 957 | 953
2016-04-06 13:00 | 967 | 964
2016-04-06 13:30 | 977 | 975
2016-04-06 14:00 | 995 | 994
2016-04-06 14:30 | 1026 | 1024
2016-04-06 15:00 | 1047 | 1046
2016-04-06 15:30 | 1066 | 1065
2016-04-06 16:00 | 1089 | 1085
2016-04-06 16:30 | 1109 | 1104
2016-04-06 17:00 | 1124 | 1119
2016-04-06 17:30 | 1123 | 1113
2016-04-06 18:00 | 1114 | 1102
2016-04-06 18:30 | 1116 | 1106
2016-04-06 19:00 | 1116 | 1104
2016-04-06 19:30 | 1065 | 1056
2016-04-06 20:00 | 1046 | 1040
2016-04-06 20:30 | 1016 | 1013
2016-04-06 21:00 | 968 | 965
2016-04-06 21:30 | 932 | 927
2016-04-06 22:00 | 880 | 880
2016-04-06 22:30 | 857 | 857
2016-04-06 23:00 | 836 | 836
2016-04-06 23:30 | 791 | 791
2016-04-07 | 745 | 745
2016-04-07 00:30 | 699 | 697
2016-04-07 01:00 | 672 | 668
2016-04-07 01:30 | 647 | 641
2016-04-07 02:00 | 632 | 626
2016-04-07 02:30 | 626 | 619
2016-04-07 03:00 | 624 | 616
2016-04-07 03:30 | 622 | 615
2016-04-07 04:00 | 622 | 615
2016-04-07 04:30 | 633 | 627
2016-04-07 05:00 | 647 | 643
2016-04-07 05:30 | 674 | 672
2016-04-07 06:00 | 711 | 710
2016-04-07 06:30 | 776 | 776
2016-04-07 07:00 | 837 | 836
2016-04-07 07:30 | 882 | 882
2016-04-07 08:00 | 891 | 889
2016-04-07 08:30 | 868 | 868
2016-04-07 09:00 | 884 | 879
2016-04-07 09:30 | 888 | 885
2016-04-07 10:00 | 883 | 881
2016-04-07 10:30 | 884 | 883
2016-04-07 11:00 | 886 | 885
2016-04-07 11:30 | 887 | 886
2016-04-07 12:00 | 896 | 895
2016-04-07 12:30 | 913 | 911
2016-04-07 13:00 | 936 | 935
2016-04-07 13:30 | 952 | 951
2016-04-07 14:00 | 979 | 978
2016-04-07 14:30 | 993 | 992
2016-04-07 15:00 | 1015 | 1014
2016-04-07 15:30 | 1037 | 1036
2016-04-07 16:00 | 1057 | 1054
2016-04-07 16:30 | 1084 | 1081
2016-04-07 17:00 | 1145 | 1140
2016-04-07 17:30 | 1135 | 1125
2016-04-07 18:00 | 1135 | 1128
2016-04-07 18:30 | 1137 | 1132
2016-04-07 19:00 | 1128 | 1122
2016-04-07 19:30 | 1089 | 1080
2016-04-07 20:00 | 1065 | 1062
2016-04-07 20:30 | 1036 | 1036
2016-04-07 21:00 | 994 | 992
2016-04-07 21:30 | 942 | 936
2016-04-07 22:00 | 902 | 897
2016-04-07 22:30 | 874 | 872
2016-04-07 23:00 | 836 | 836
2016-04-07 23:30 | 791 | 790
2016-04-08 | 742 | 741
2016-04-08 00:30 | 693 | 692
2016-04-08 01:00 | 672 | 671
2016-04-08 01:30 | 649 | 647
2016-04-08 02:00 | 627 | 625
2016-04-08 02:30 | 619 | 615
2016-04-08 03:00 | 613 | 608
2016-04-08 03:30 | 615 | 610
2016-04-08 04:00 | 619 | 614
2016-04-08 04:30 | 625 | 622
2016-04-08 05:00 | 638 | 636
2016-04-08 05:30 | 673 | 673
2016-04-08 06:00 | 711 | 707
2016-04-08 06:30 | 767 | 766
2016-04-08 07:00 | 818 | 817
2016-04-08 07:30 | 892 | 888
2016-04-08 08:00 | 936 | 935
2016-04-08 08:30 | 963 | 962
2016-04-08 09:00 | 985 | 984
2016-04-08 09:30 | 1013 | 1013
2016-04-08 10:00 | 1030 | 1030
2016-04-08 10:30 | 1026 | 1026
2016-04-08 11:00 | 1021 | 1021
2016-04-08 11:30 | 1009 | 1009
2016-04-08 12:00 | 1024 | 1024
2016-04-08 12:30 | 1020 | 1020
2016-04-08 13:00 | 1012 | 1012
2016-04-08 13:30 | 1025 | 1025
2016-04-08 14:00 | 1031 | 1031
2016-04-08 14:30 | 1040 | 1039
2016-04-08 15:00 | 1040 | 1038
2016-04-08 15:30 | 1051 | 1049
2016-04-08 16:00 | 1078 | 1077
2016-04-08 16:30 | 1091 | 1090
2016-04-08 17:00 | 1104 | 1102
2016-04-08 17:30 | 1082 | 1078
2016-04-08 18:00 | 1069 | 1063
2016-04-08 18:30 | 1074 | 1068
2016-04-08 19:00 | 1059 | 1052
2016-04-08 19:30 | 1023 | 1018
2016-04-08 20:00 | 1008 | 1004
2016-04-08 20:30 | 984 | 981
2016-04-08 21:00 | 938 | 936
2016-04-08 21:30 | 906 | 901
2016-04-08 22:00 | 871 | 868
2016-04-08 22:30 | 848 | 848
2016-04-08 23:00 | 829 | 828
2016-04-08 23:30 | 779 | 779
2016-04-09 | 731 | 731
2016-04-09 00:30 | 685 | 683
2016-04-09 01:00 | 656 | 653
2016-04-09 01:30 | 631 | 626
2016-04-09 02:00 | 616 | 609
2016-04-09 02:30 | 611 | 603
2016-04-09 03:00 | 604 | 595
2016-04-09 03:30 | 601 | 592
2016-04-09 04:00 | 600 | 590
2016-04-09 04:30 | 599 | 590
2016-04-09 05:00 | 604 | 595
2016-04-09 05:30 | 620 | 613
2016-04-09 06:00 | 627 | 621
2016-04-09 06:30 | 648 | 642
2016-04-09 07:00 | 673 | 670
2016-04-09 07:30 | 716 | 715
2016-04-09 08:00 | 737 | 737
2016-04-09 08:30 | 767 | 767
2016-04-09 09:00 | 792 | 791
2016-04-09 09:30 | 819 | 819
2016-04-09 10:00 | 831 | 831
2016-04-09 10:30 | 829 | 829
2016-04-09 11:00 | 823 | 823
2016-04-09 11:30 | 818 | 817
2016-04-09 12:00 | 818 | 818
2016-04-09 12:30 | 814 | 814
2016-04-09 13:00 | 812 | 812
2016-04-09 13:30 | 831 | 831
2016-04-09 14:00 | 844 | 844
2016-04-09 14:30 | 853 | 853
2016-04-09 15:00 | 878 | 877
2016-04-09 15:30 | 896 | 896
2016-04-09 16:00 | 929 | 929
2016-04-09 16:30 | 955 | 953
2016-04-09 17:00 | 978 | 977
2016-04-09 17:30 | 974 | 971
2016-04-09 18:00 | 974 | 972
2016-04-09 18:30 | 996 | 995
2016-04-09 19:00 | 986 | 985
2016-04-09 19:30 | 962 | 958
2016-04-09 20:00 | 951 | 945
2016-04-09 20:30 | 934 | 931
2016-04-09 21:00 | 890 | 886
2016-04-09 21:30 | 854 | 850
2016-04-09 22:00 | 834 | 828
2016-04-09 22:30 | 820 | 812
2016-04-09 23:00 | 802 | 798
2016-04-09 23:30 | 771 | 765
2016-04-10 | 733 | 723
2016-04-10 00:30 | 679 | 676
2016-04-10 01:00 | 652 | 647
2016-04-10 01:30 | 633 | 626
2016-04-10 02:00 | 614 | 605
2016-04-10 02:30 | 608 | 598
2016-04-10 03:00 | 600 | 589
2016-04-10 03:30 | 594 | 583
2016-04-10 04:00 | 591 | 579
2016-04-10 04:30 | 589 | 577
2016-04-10 05:00 | 592 | 580
2016-04-10 05:30 | 597 | 586
2016-04-10 06:00 | 608 | 598
2016-04-10 06:30 | 617 | 605
2016-04-10 07:00 | 632 | 622
2016-04-10 07:30 | 650 | 644
2016-04-10 08:00 | 670 | 666
2016-04-10 08:30 | 694 | 694
2016-04-10 09:00 | 703 | 703
2016-04-10 09:30 | 727 | 727
2016-04-10 10:00 | 735 | 735
2016-04-10 10:30 | 747 | 747
2016-04-10 11:00 | 749 | 749
2016-04-10 11:30 | 756 | 756
2016-04-10 12:00 | 759 | 758
2016-04-10 12:30 | 771 | 770
2016-04-10 13:00 | 793 | 789
2016-04-10 13:30 | 794 | 791
2016-04-10 14:00 | 814 | 811
2016-04-10 14:30 | 836 | 832
2016-04-10 15:00 | 865 | 862
2016-04-10 15:30 | 895 | 890
2016-04-10 16:00 | 934 | 930
2016-04-10 16:30 | 951 | 947
2016-04-10 17:00 | 979 | 976
2016-04-10 17:30 | 995 | 992
2016-04-10 18:00 | 1015 | 1013
2016-04-10 18:30 | 1031 | 1029
2016-04-10 19:00 | 1027 | 1025
2016-04-10 19:30 | 992 | 988
2016-04-10 20:00 | 975 | 969
2016-04-10 20:30 | 948 | 939
2016-04-10 21:00 | 902 | 891
2016-04-10 21:30 | 866 | 857
2016-04-10 22:00 | 834 | 829
2016-04-10 22:30 | 806 | 797
2016-04-10 23:00 | 794 | 783
2016-04-10 23:30 | 756 | 747
2016-04-11 | 716 | 709
2016-04-11 00:30 | 682 | 672
2016-04-11 01:00 | 651 | 644
2016-04-11 01:30 | 629 | 621
2016-04-11 02:00 | 615 | 607
2016-04-11 02:30 | 609 | 601
2016-04-11 03:00 | 605 | 596
2016-04-11 03:30 | 605 | 596
2016-04-11 04:00 | 602 | 593
2016-04-11 04:30 | 613 | 604
2016-04-11 05:00 | 625 | 619
2016-04-11 05:30 | 660 | 657
2016-04-11 06:00 | 695 | 695
2016-04-11 06:30 | 775 | 773
2016-04-11 07:00 | 848 | 848
2016-04-11 07:30 | 915 | 914
2016-04-11 08:00 | 970 | 960
2016-04-11 08:30 | 990 | 984
2016-04-11 09:00 | 1015 | 1008
2016-04-11 09:30 | 1032 | 1026
2016-04-11 10:00 | 1050 | 1044
2016-04-11 10:30 | 1040 | 1035
2016-04-11 11:00 | 1044 | 1039
2016-04-11 11:30 | 1057 | 1049
2016-04-11 12:00 | 1063 | 1055
2016-04-11 12:30 | 1054 | 1045
2016-04-11 13:00 | 1058 | 1050
2016-04-11 13:30 | 1069 | 1060
2016-04-11 14:00 | 1068 | 1059
2016-04-11 14:30 | 1050 | 1039
2016-04-11 15:00 | 1058 | 1045
2016-04-11 15:30 | 1074 | 1059
2016-04-11 16:00 | 1085 | 1075
2016-04-11 16:30 | 1099 | 1089
2016-04-11 17:00 | 1120 | 1110
2016-04-11 17:30 | 1128 | 1117
2016-04-11 18:00 | 1143 | 1135
2016-04-11 18:30 | 1144 | 1134
2016-04-11 19:00 | 1136 | 1125
2016-04-11 19:30 | 1086 | 1082
2016-04-11 20:00 | 1069 | 1067
2016-04-11 20:30 | 1044 | 1038
2016-04-11 21:00 | 987 | 980
2016-04-11 21:30 | 938 | 936
2016-04-11 22:00 | 894 | 891
2016-04-11 22:30 | 863 | 857
2016-04-11 23:00 | 839 | 830
2016-04-11 23:30 | 792 | 778
2016-04-12 | 730 | 720
2016-04-12 00:30 | 687 | 681
2016-04-12 01:00 | 651 | 646
2016-04-12 01:30 | 622 | 617
2016-04-12 02:00 | 600 | 592
2016-04-12 02:30 | 594 | 585
2016-04-12 03:00 | 589 | 579
2016-04-12 03:30 | 590 | 580
2016-04-12 04:00 | 586 | 576
2016-04-12 04:30 | 593 | 584
2016-04-12 05:00 | 616 | 609
2016-04-12 05:30 | 664 | 662
2016-04-12 06:00 | 719 | 718
2016-04-12 06:30 | 802 | 800
2016-04-12 07:00 | 869 | 867
2016-04-12 07:30 | 951 | 949
2016-04-12 08:00 | 982 | 976
2016-04-12 08:30 | 992 | 987
2016-04-12 09:00 | 985 | 980
2016-04-12 09:30 | 991 | 988
2016-04-12 10:00 | 1000 | 996
2016-04-12 10:30 | 1018 | 1008
2016-04-12 11:00 | 1019 | 1008
2016-04-12 11:30 | 1011 | 999
2016-04-12 12:00 | 1006 | 994
2016-04-12 12:30 | 993 | 980
2016-04-12 13:00 | 987 | 974
2016-04-12 13:30 | 992 | 979
2016-04-12 14:00 | 1000 | 987
2016-04-12 14:30 | 988 | 974
2016-04-12 15:00 | 978 | 964
2016-04-12 15:30 | 993 | 979
2016-04-12 16:00 | 1021 | 1008
2016-04-12 16:30 | 1046 | 1033
2016-04-12 17:00 | 1070 | 1057
2016-04-12 17:30 | 1082 | 1070
2016-04-12 18:00 | 1081 | 1069
2016-04-12 18:30 | 1075 | 1061
2016-04-12 19:00 | 1070 | 1056
2016-04-12 19:30 | 1034 | 1025
2016-04-12 20:00 | 1026 | 1017
2016-04-12 20:30 | 1001 | 988
2016-04-12 21:00 | 957 | 937
2016-04-12 21:30 | 912 | 894
2016-04-12 22:00 | 856 | 848
2016-04-12 22:30 | 833 | 821
2016-04-12 23:00 | 822 | 809
2016-04-12 23:30 | 763 | 761
2016-04-13 | 709 | 707
2016-04-13 00:30 | 656 | 652
2016-04-13 01:00 | 628 | 622
2016-04-13 01:30 | 606 | 598
2016-04-13 02:00 | 581 | 572
2016-04-13 02:30 | 577 | 567
2016-04-13 03:00 | 575 | 563
2016-04-13 03:30 | 578 | 566
2016-04-13 04:00 | 578 | 568
2016-04-13 04:30 | 582 | 572
2016-04-13 05:00 | 598 | 592
2016-04-13 05:30 | 641 | 637
2016-04-13 06:00 | 702 | 696
2016-04-13 06:30 | 791 | 785
2016-04-13 07:00 | 848 | 843
2016-04-13 07:30 | 896 | 894
2016-04-13 08:00 | 915 | 912
2016-04-13 08:30 | 913 | 911
2016-04-13 09:00 | 914 | 914
2016-04-13 09:30 | 908 | 905
2016-04-13 10:00 | 901 | 897
2016-04-13 10:30 | 905 | 902
2016-04-13 11:00 | 907 | 905
2016-04-13 11:30 | 913 | 911
2016-04-13 12:00 | 918 | 916
2016-04-13 12:30 | 911 | 909
2016-04-13 13:00 | 907 | 905
2016-04-13 13:30 | 910 | 908
2016-04-13 14:00 | 941 | 939
2016-04-13 14:30 | 954 | 953
2016-04-13 15:00 | 963 | 962
2016-04-13 15:30 | 976 | 974
2016-04-13 16:00 | 994 | 992
2016-04-13 16:30 | 1018 | 1016
2016-04-13 17:00 | 1038 | 1035
2016-04-13 17:30 | 1023 | 1019
2016-04-13 18:00 | 1035 | 1032
2016-04-13 18:30 | 1045 | 1042
2016-04-13 19:00 | 1034 | 1030
2016-04-13 19:30 | 995 | 987
2016-04-13 20:00 | 970 | 962
2016-04-13 20:30 | 941 | 936
2016-04-13 21:00 | 907 | 897
2016-04-13 21:30 | 875 | 862
2016-04-13 22:00 | 834 | 826
2016-04-13 22:30 | 793 | 791
2016-04-13 23:00 | 781 | 781
2016-04-13 23:30 | 741 | 740
2016-04-14 | 688 | 684
2016-04-14 00:30 | 645 | 641
2016-04-14 01:00 | 615 | 611
2016-04-14 01:30 | 592 | 586
2016-04-14 02:00 | 570 | 562
2016-04-14 02:30 | 542 | 534
2016-04-14 03:00 | 528 | 519
2016-04-14 03:30 | 533 | 525
2016-04-14 04:00 | 553 | 545
2016-04-14 04:30 | 569 | 563
2016-04-14 05:00 | 586 | 581
2016-04-14 05:30 | 632 | 631
2016-04-14 06:00 | 699 | 699
2016-04-14 06:30 | 773 | 771
2016-04-14 07:00 | 844 | 841
2016-04-14 07:30 | 913 | 912
2016-04-14 08:00 | 936 | 932
2016-04-14 08:30 | 945 | 941
2016-04-14 09:00 | 935 | 932
2016-04-14 09:30 | 952 | 950
2016-04-14 10:00 | 962 | 958
2016-04-14 10:30 | 960 | 956
2016-04-14 11:00 | 944 | 940
2016-04-14 11:30 | 940 | 937
2016-04-14 12:00 | 941 | 938
2016-04-14 12:30 | 927 | 923
2016-04-14 13:00 | 914 | 910
2016-04-14 13:30 | 904 | 899
2016-04-14 14:00 | 925 | 920
2016-04-14 14:30 | 925 | 920
2016-04-14 15:00 | 928 | 921
2016-04-14 15:30 | 946 | 936
2016-04-14 16:00 | 976 | 967
2016-04-14 16:30 | 1002 | 993
2016-04-14 17:00 | 1023 | 1013
2016-04-14 17:30 | 1010 | 1000
2016-04-14 18:00 | 1027 | 1020
2016-04-14 18:30 | 1032 | 1026
2016-04-14 19:00 | 1036 | 1029
2016-04-14 19:30 | 1006 | 995
2016-04-14 20:00 | 987 | 976
2016-04-14 20:30 | 959 | 953
2016-04-14 21:00 | 900 | 897
2016-04-14 21:30 | 861 | 858
2016-04-14 22:00 | 820 | 816
2016-04-14 22:30 | 775 | 773
2016-04-14 23:00 | 754 | 751
2016-04-14 23:30 | 721 | 715
2016-04-15 | 673 | 665
2016-04-15 00:30 | 633 | 629
2016-04-15 01:00 | 613 | 606
2016-04-15 01:30 | 593 | 584
2016-04-15 02:00 | 577 | 566
2016-04-15 02:30 | 563 | 551
2016-04-15 03:00 | 556 | 543
2016-04-15 03:30 | 560 | 546
2016-04-15 04:00 | 561 | 546
2016-04-15 04:30 | 560 | 547
2016-04-15 05:00 | 578 | 568
2016-04-15 05:30 | 619 | 614
2016-04-15 06:00 | 674 | 668
2016-04-15 06:30 | 735 | 731
2016-04-15 07:00 | 801 | 794
2016-04-15 07:30 | 862 | 855
2016-04-15 08:00 | 883 | 868
2016-04-15 08:30 | 879 | 865
2016-04-15 09:00 | 876 | 865
2016-04-15 09:30 | 895 | 888
2016-04-15 10:00 | 898 | 888
2016-04-15 10:30 | 874 | 863
2016-04-15 11:00 | 916 | 908
2016-04-15 11:30 | 955 | 944
2016-04-15 12:00 | 937 | 921
2016-04-15 12:30 | 881 | 871
2016-04-15 13:00 | 891 | 886
2016-04-15 13:30 | 895 | 888
2016-04-15 14:00 | 887 | 878
2016-04-15 14:30 | 876 | 865
2016-04-15 15:00 | 890 | 881
2016-04-15 15:30 | 896 | 895
2016-04-15 16:00 | 926 | 925
2016-04-15 16:30 | 947 | 946
2016-04-15 17:00 | 968 | 966
2016-04-15 17:30 | 971 | 965
2016-04-15 18:00 | 979 | 973
2016-04-15 18:30 | 978 | 973
2016-04-15 19:00 | 969 | 963
2016-04-15 19:30 | 941 | 931
2016-04-15 20:00 | 939 | 931
2016-04-15 20:30 | 935 | 927
2016-04-15 21:00 | 888 | 878
2016-04-15 21:30 | 847 | 842
2016-04-15 22:00 | 810 | 802
2016-04-15 22:30 | 793 | 782
2016-04-15 23:00 | 774 | 766
2016-04-15 23:30 | 733 | 722
2016-04-16 | 676 | 665
2016-04-16 00:30 | 624 | 619
2016-04-16 01:00 | 608 | 600
2016-04-16 01:30 | 593 | 584
2016-04-16 02:00 | 574 | 561
2016-04-16 02:30 | 570 | 557
2016-04-16 03:00 | 571 | 556
2016-04-16 03:30 | 568 | 552
2016-04-16 04:00 | 566 | 550
2016-04-16 04:30 | 566 | 550
2016-04-16 05:00 | 566 | 551
2016-04-16 05:30 | 578 | 566
2016-04-16 06:00 | 595 | 585
2016-04-16 06:30 | 622 | 612
2016-04-16 07:00 | 649 | 643
2016-04-16 07:30 | 681 | 678
2016-04-16 08:00 | 705 | 704
2016-04-16 08:30 | 732 | 731
2016-04-16 09:00 | 749 | 747
2016-04-16 09:30 | 740 | 738
2016-04-16 10:00 | 752 | 751
2016-04-16 10:30 | 758 | 758
2016-04-16 11:00 | 756 | 752
2016-04-16 11:30 | 742 | 737
2016-04-16 12:00 | 744 | 739
2016-04-16 12:30 | 746 | 742
2016-04-16 13:00 | 764 | 759
2016-04-16 13:30 | 768 | 764
2016-04-16 14:00 | 769 | 765
2016-04-16 14:30 | 781 | 777
2016-04-16 15:00 | 803 | 799
2016-04-16 15:30 | 824 | 820
2016-04-16 16:00 | 839 | 835
2016-04-16 16:30 | 850 | 845
2016-04-16 17:00 | 865 | 862
2016-04-16 17:30 | 877 | 875
2016-04-16 18:00 | 895 | 895
2016-04-16 18:30 | 899 | 899
2016-04-16 19:00 | 898 | 897
2016-04-16 19:30 | 882 | 880
2016-04-16 20:00 | 869 | 865
2016-04-16 20:30 | 856 | 851
2016-04-16 21:00 | 822 | 815
2016-04-16 21:30 | 782 | 781
2016-04-16 22:00 | 763 | 762
2016-04-16 22:30 | 767 | 764
2016-04-16 23:00 | 767 | 763
2016-04-16 23:30 | 734 | 729
2016-04-17 | 682 | 680
2016-04-17 00:30 | 640 | 635
2016-04-17 01:00 | 617 | 610
2016-04-17 01:30 | 602 | 593
2016-04-17 02:00 | 574 | 562
2016-04-17 02:30 | 560 | 547
2016-04-17 03:00 | 558 | 544
2016-04-17 03:30 | 562 | 546
2016-04-17 04:00 | 563 | 548
2016-04-17 04:30 | 551 | 536
2016-04-17 05:00 | 544 | 528
2016-04-17 05:30 | 552 | 537
2016-04-17 06:00 | 565 | 551
2016-04-17 06:30 | 587 | 572
2016-04-17 07:00 | 594 | 579
2016-04-17 07:30 | 620 | 610
2016-04-17 08:00 | 644 | 639
2016-04-17 08:30 | 658 | 655
2016-04-17 09:00 | 680 | 676
2016-04-17 09:30 | 676 | 673
2016-04-17 10:00 | 678 | 674
2016-04-17 10:30 | 674 | 670
2016-04-17 11:00 | 682 | 679
2016-04-17 11:30 | 673 | 670
2016-04-17 12:00 | 688 | 686
2016-04-17 12:30 | 690 | 687
2016-04-17 13:00 | 701 | 699
2016-04-17 13:30 | 706 | 704
2016-04-17 14:00 | 723 | 721
2016-04-17 14:30 | 730 | 728
2016-04-17 15:00 | 751 | 748
2016-04-17 15:30 | 781 | 778
2016-04-17 16:00 | 818 | 812
2016-04-17 16:30 | 851 | 843
2016-04-17 17:00 | 878 | 872
2016-04-17 17:30 | 889 | 884
2016-04-17 18:00 | 920 | 919
2016-04-17 18:30 | 933 | 933
2016-04-17 19:00 | 934 | 933
2016-04-17 19:30 | 913 | 910
2016-04-17 20:00 | 893 | 887
2016-04-17 20:30 | 872 | 865
2016-04-17 21:00 | 836 | 823
2016-04-17 21:30 | 799 | 792
2016-04-17 22:00 | 765 | 760
2016-04-17 22:30 | 742 | 740
2016-04-17 23:00 | 739 | 738
2016-04-17 23:30 | 707 | 705
2016-04-18 | 662 | 658
2016-04-18 00:30 | 619 | 611
2016-04-18 01:00 | 590 | 579
2016-04-18 01:30 | 565 | 552
2016-04-18 02:00 | 548 | 534
2016-04-18 02:30 | 547 | 532
2016-04-18 03:00 | 545 | 530
2016-04-18 03:30 | 545 | 531
2016-04-18 04:00 | 549 | 534
2016-04-18 04:30 | 554 | 542
2016-04-18 05:00 | 566 | 558
2016-04-18 05:30 | 607 | 603
2016-04-18 06:00 | 652 | 651
2016-04-18 06:30 | 741 | 739
2016-04-18 07:00 | 801 | 796
2016-04-18 07:30 | 865 | 864
2016-04-18 08:00 | 891 | 886
2016-04-18 08:30 | 877 | 875
2016-04-18 09:00 | 883 | 873
2016-04-18 09:30 | 877 | 868
2016-04-18 10:00 | 865 | 858
2016-04-18 10:30 | 875 | 869
2016-04-18 11:00 | 882 | 877
2016-04-18 11:30 | 884 | 880
2016-04-18 12:00 | 908 | 902
2016-04-18 12:30 | 917 | 909
2016-04-18 13:00 | 940 | 934
2016-04-18 13:30 | 948 | 942
2016-04-18 14:00 | 960 | 954
2016-04-18 14:30 | 971 | 966
2016-04-18 15:00 | 968 | 962
2016-04-18 15:30 | 980 | 974
2016-04-18 16:00 | 1006 | 999
2016-04-18 16:30 | 1038 | 1031
2016-04-18 17:00 | 1063 | 1057
2016-04-18 17:30 | 1076 | 1069
2016-04-18 18:00 | 1089 | 1083
2016-04-18 18:30 | 1087 | 1080
2016-04-18 19:00 | 1075 | 1066
2016-04-18 19:30 | 1036 | 1026
2016-04-18 20:00 | 1003 | 996
2016-04-18 20:30 | 976 | 968
2016-04-18 21:00 | 923 | 916
2016-04-18 21:30 | 882 | 876
2016-04-18 22:00 | 832 | 832
2016-04-18 22:30 | 802 | 801
2016-04-18 23:00 | 788 | 786
2016-04-18 23:30 | 743 | 739
2016-04-19 | 690 | 686
2016-04-19 00:30 | 645 | 641
2016-04-19 01:00 | 621 | 614
2016-04-19 01:30 | 597 | 589
2016-04-19 02:00 | 569 | 559
2016-04-19 02:30 | 558 | 546
2016-04-19 03:00 | 549 | 537
2016-04-19 03:30 | 548 | 535
2016-04-19 04:00 | 548 | 536
2016-04-19 04:30 | 564 | 554
2016-04-19 05:00 | 586 | 579
2016-04-19 05:30 | 634 | 631
2016-04-19 06:00 | 694 | 689
2016-04-19 06:30 | 766 | 765
2016-04-19 07:00 | 841 | 838
2016-04-19 07:30 | 900 | 889
2016-04-19 08:00 | 914 | 898
2016-04-19 08:30 | 908 | 896
2016-04-19 09:00 | 890 | 882
2016-04-19 09:30 | 902 | 891
2016-04-19 10:00 | 871 | 860
2016-04-19 10:30 | 823 | 817
2016-04-19 11:00 | 825 | 812
2016-04-19 11:30 | 818 | 806
2016-04-19 12:00 | 831 | 819
2016-04-19 12:30 | 837 | 827
2016-04-19 13:00 | 850 | 840
2016-04-19 13:30 | 873 | 864
2016-04-19 14:00 | 903 | 895
2016-04-19 14:30 | 908 | 900
2016-04-19 15:00 | 929 | 922
2016-04-19 15:30 | 938 | 929
2016-04-19 16:00 | 951 | 940
2016-04-19 16:30 | 959 | 948
2016-04-19 17:00 | 972 | 961
2016-04-19 17:30 | 971 | 959
2016-04-19 18:00 | 983 | 974
2016-04-19 18:30 | 967 | 956
2016-04-19 19:00 | 964 | 950
2016-04-19 19:30 | 935 | 925
2016-04-19 20:00 | 903 | 899
2016-04-19 20:30 | 889 | 882
2016-04-19 21:00 | 843 | 833
2016-04-19 21:30 | 784 | 779
2016-04-19 22:00 | 752 | 751
2016-04-19 22:30 | 718 | 716
2016-04-19 23:00 | 705 | 704
2016-04-19 23:30 | 662 | 659
2016-04-20 | 621 | 615
2016-04-20 00:30 | 592 | 581
2016-04-20 01:00 | 564 | 555
2016-04-20 01:30 | 536 | 528
2016-04-20 02:00 | 512 | 502
2016-04-20 02:30 | 500 | 490
2016-04-20 03:00 | 500 | 487
2016-04-20 03:30 | 497 | 484
2016-04-20 04:00 | 495 | 482
2016-04-20 04:30 | 508 | 498
2016-04-20 05:00 | 526 | 518
2016-04-20 05:30 | 563 | 559
2016-04-20 06:00 | 621 | 616
2016-04-20 06:30 | 706 | 704
2016-04-20 07:00 | 773 | 770
2016-04-20 07:30 | 827 | 824
2016-04-20 08:00 | 837 | 828
2016-04-20 08:30 | 817 | 813
2016-04-20 09:00 | 805 | 803
2016-04-20 09:30 | 786 | 785
2016-04-20 10:00 | 781 | 778
2016-04-20 10:30 | 785 | 778
2016-04-20 11:00 | 812 | 806
2016-04-20 11:30 | 822 | 813
2016-04-20 12:00 | 837 | 828
2016-04-20 12:30 | 855 | 846
2016-04-20 13:00 | 866 | 857
2016-04-20 13:30 | 882 | 874
2016-04-20 14:00 | 893 | 886
2016-04-20 14:30 | 889 | 881
2016-04-20 15:00 | 898 | 890
2016-04-20 15:30 | 928 | 920
2016-04-20 16:00 | 949 | 941
2016-04-20 16:30 | 972 | 966
2016-04-20 17:00 | 991 | 983
2016-04-20 17:30 | 1007 | 994
2016-04-20 18:00 | 1025 | 1013
2016-04-20 18:30 | 1021 | 1007
2016-04-20 19:00 | 1014 | 1004
2016-04-20 19:30 | 980 | 965
2016-04-20 20:00 | 934 | 926
2016-04-20 20:30 | 917 | 909
2016-04-20 21:00 | 865 | 852
2016-04-20 21:30 | 802 | 796
2016-04-20 22:00 | 770 | 766
2016-04-20 22:30 | 742 | 739
2016-04-20 23:00 | 724 | 720
2016-04-20 23:30 | 682 | 681
2016-04-21 | 629 | 628
2016-04-21 00:30 | 588 | 585
2016-04-21 01:00 | 565 | 559
2016-04-21 01:30 | 537 | 530
2016-04-21 02:00 | 520 | 510
2016-04-21 02:30 | 520 | 509
2016-04-21 03:00 | 510 | 498
2016-04-21 03:30 | 502 | 489
2016-04-21 04:00 | 518 | 505
2016-04-21 04:30 | 520 | 509
2016-04-21 05:00 | 526 | 518
2016-04-21 05:30 | 564 | 561
2016-04-21 06:00 | 616 | 614
2016-04-21 06:30 | 708 | 703
2016-04-21 07:00 | 768 | 761
2016-04-21 07:30 | 826 | 820
2016-04-21 08:00 | 837 | 832
2016-04-21 08:30 | 847 | 836
2016-04-21 09:00 | 831 | 819
2016-04-21 09:30 | 830 | 821
2016-04-21 10:00 | 825 | 818
2016-04-21 10:30 | 846 | 841
2016-04-21 11:00 | 864 | 860
2016-04-21 11:30 | 877 | 874
2016-04-21 12:00 | 887 | 885
2016-04-21 12:30 | 885 | 882
2016-04-21 13:00 | 884 | 881
2016-04-21 13:30 | 873 | 868
2016-04-21 14:00 | 878 | 874
2016-04-21 14:30 | 880 | 876
2016-04-21 15:00 | 902 | 897
2016-04-21 15:30 | 898 | 893
2016-04-21 16:00 | 912 | 905
2016-04-21 16:30 | 933 | 923
2016-04-21 17:00 | 958 | 949
2016-04-21 17:30 | 966 | 957
2016-04-21 18:00 | 992 | 985
2016-04-21 18:30 | 986 | 978
2016-04-21 19:00 | 976 | 967
2016-04-21 19:30 | 944 | 931
2016-04-21 20:00 | 922 | 907
2016-04-21 20:30 | 907 | 887
2016-04-21 21:00 | 862 | 848
2016-04-21 21:30 | 811 | 798
2016-04-21 22:00 | 761 | 754
2016-04-21 22:30 | 727 | 718
2016-04-21 23:00 | 717 | 709
2016-04-21 23:30 | 667 | 664
2016-04-22 | 614 | 613
2016-04-22 00:30 | 585 | 581
2016-04-22 01:00 | 586 | 579
2016-04-22 01:30 | 547 | 539
2016-04-22 02:00 | 527 | 517
2016-04-22 02:30 | 523 | 511
2016-04-22 03:00 | 529 | 516
2016-04-22 03:30 | 527 | 513
2016-04-22 04:00 | 522 | 510
2016-04-22 04:30 | 532 | 520
2016-04-22 05:00 | 545 | 537
2016-04-22 05:30 | 586 | 582
2016-04-22 06:00 | 632 | 628
2016-04-22 06:30 | 696 | 694
2016-04-22 07:00 | 750 | 748
2016-04-22 07:30 | 818 | 816
2016-04-22 08:00 | 840 | 838
2016-04-22 08:30 | 856 | 853
2016-04-22 09:00 | 855 | 851
2016-04-22 09:30 | 858 | 855
2016-04-22 10:00 | 855 | 849
2016-04-22 10:30 | 860 | 855
2016-04-22 11:00 | 863 | 858
2016-04-22 11:30 | 860 | 855
2016-04-22 12:00 | 864 | 860
2016-04-22 12:30 | 875 | 870
2016-04-22 13:00 | 889 | 880
2016-04-22 13:30 | 891 | 881
2016-04-22 14:00 | 905 | 895
2016-04-22 14:30 | 907 | 898
2016-04-22 15:00 | 914 | 904
2016-04-22 15:30 | 922 | 913
2016-04-22 16:00 | 939 | 930
2016-04-22 16:30 | 954 | 945
2016-04-22 17:00 | 968 | 958
2016-04-22 17:30 | 955 | 943
2016-04-22 18:00 | 966 | 955
2016-04-22 18:30 | 952 | 939
2016-04-22 19:00 | 943 | 932
2016-04-22 19:30 | 925 | 910
2016-04-22 20:00 | 911 | 905
2016-04-22 20:30 | 885 | 883
2016-04-22 21:00 | 848 | 844
2016-04-22 21:30 | 804 | 798
2016-04-22 22:00 | 769 | 766
2016-04-22 22:30 | 753 | 750
2016-04-22 23:00 | 731 | 729
2016-04-22 23:30 | 688 | 687
2016-04-23 | 642 | 641
2016-04-23 00:30 | 604 | 600
2016-04-23 01:00 | 584 | 578
2016-04-23 01:30 | 574 | 566
2016-04-23 02:00 | 557 | 548
2016-04-23 02:30 | 547 | 537
2016-04-23 03:00 | 543 | 532
2016-04-23 03:30 | 541 | 529
2016-04-23 04:00 | 543 | 530
2016-04-23 04:30 | 551 | 538
2016-04-23 05:00 | 551 | 539
2016-04-23 05:30 | 564 | 554
2016-04-23 06:00 | 581 | 572
2016-04-23 06:30 | 597 | 588
2016-04-23 07:00 | 612 | 605
2016-04-23 07:30 | 633 | 630
2016-04-23 08:00 | 656 | 655
2016-04-23 08:30 | 681 | 681
2016-04-23 09:00 | 690 | 689
2016-04-23 09:30 | 691 | 691
2016-04-23 10:00 | 684 | 684
2016-04-23 10:30 | 676 | 676
2016-04-23 11:00 | 683 | 682
2016-04-23 11:30 | 675 | 674
2016-04-23 12:00 | 680 | 678
2016-04-23 12:30 | 685 | 684
2016-04-23 13:00 | 696 | 695
2016-04-23 13:30 | 706 | 704
2016-04-23 14:00 | 709 | 707
2016-04-23 14:30 | 709 | 706
2016-04-23 15:00 | 711 | 709
2016-04-23 15:30 | 723 | 721
2016-04-23 16:00 | 749 | 748
2016-04-23 16:30 | 766 | 765
2016-04-23 17:00 | 788 | 787
2016-04-23 17:30 | 779 | 778
2016-04-23 18:00 | 790 | 790
2016-04-23 18:30 | 805 | 802
2016-04-23 19:00 | 796 | 793
2016-04-23 19:30 | 779 | 777
2016-04-23 20:00 | 774 | 772
2016-04-23 20:30 | 758 | 755
2016-04-23 21:00 | 722 | 719
2016-04-23 21:30 | 705 | 701
2016-04-23 22:00 | 687 | 685
2016-04-23 22:30 | 685 | 682
2016-04-23 23:00 | 687 | 684
2016-04-23 23:30 | 655 | 649
2016-04-24 | 619 | 612
2016-04-24 00:30 | 594 | 583
2016-04-24 01:00 | 573 | 560
2016-04-24 01:30 | 551 | 536
2016-04-24 02:00 | 533 | 518
2016-04-24 02:30 | 528 | 511
2016-04-24 03:00 | 522 | 502
2016-04-24 03:30 | 517 | 499
2016-04-24 04:00 | 515 | 497
2016-04-24 04:30 | 508 | 491
2016-04-24 05:00 | 511 | 495
2016-04-24 05:30 | 512 | 498
2016-04-24 06:00 | 524 | 512
2016-04-24 06:30 | 533 | 519
2016-04-24 07:00 | 542 | 530
2016-04-24 07:30 | 558 | 551
2016-04-24 08:00 | 571 | 567
2016-04-24 08:30 | 592 | 589
2016-04-24 09:00 | 597 | 595
2016-04-24 09:30 | 603 | 600
2016-04-24 10:00 | 604 | 599
2016-04-24 10:30 | 604 | 599
2016-04-24 11:00 | 600 | 595
2016-04-24 11:30 | 580 | 575
2016-04-24 12:00 | 592 | 588
2016-04-24 12:30 | 592 | 588
2016-04-24 13:00 | 603 | 598
2016-04-24 13:30 | 617 | 613
2016-04-24 14:00 | 636 | 633
2016-04-24 14:30 | 643 | 640
2016-04-24 15:00 | 664 | 661
2016-04-24 15:30 | 679 | 677
2016-04-24 16:00 | 707 | 705
2016-04-24 16:30 | 723 | 721
2016-04-24 17:00 | 746 | 744
2016-04-24 17:30 | 747 | 746
2016-04-24 18:00 | 773 | 773
2016-04-24 18:30 | 786 | 781
2016-04-24 19:00 | 784 | 777
2016-04-24 19:30 | 760 | 751
2016-04-24 20:00 | 749 | 738
2016-04-24 20:30 | 737 | 727
2016-04-24 21:00 | 694 | 694
2016-04-24 21:30 | 674 | 674
2016-04-24 22:00 | 663 | 663
2016-04-24 22:30 | 660 | 659
2016-04-24 23:00 | 665 | 664
2016-04-24 23:30 | 630 | 627
2016-04-25 | 590 | 585
2016-04-25 00:30 | 572 | 563
2016-04-25 01:00 | 559 | 546
2016-04-25 01:30 | 495 | 480
2016-04-25 02:00 | 477 | 460
2016-04-25 02:30 | 475 | 457
2016-04-25 03:00 | 468 | 450
2016-04-25 03:30 | 475 | 456
2016-04-25 04:00 | 466 | 447
2016-04-25 04:30 | 463 | 444
2016-04-25 05:00 | 466 | 449
2016-04-25 05:30 | 456 | 441
2016-04-25 06:00 | 464 | 450
2016-04-25 06:30 | 483 | 469
2016-04-25 07:00 | 504 | 491
2016-04-25 07:30 | 523 | 513
2016-04-25 08:00 | 556 | 549
2016-04-25 08:30 | 577 | 573
2016-04-25 09:00 | 592 | 590
2016-04-25 09:30 | 604 | 603
2016-04-25 10:00 | 616 | 616
2016-04-25 10:30 | 613 | 613
2016-04-25 11:00 | 595 | 594
2016-04-25 11:30 | 598 | 597
2016-04-25 12:00 | 608 | 608
2016-04-25 12:30 | 612 | 612
2016-04-25 13:00 | 598 | 598
2016-04-25 13:30 | 609 | 609
2016-04-25 14:00 | 603 | 603
2016-04-25 14:30 | 636 | 636
2016-04-25 15:00 | 652 | 650
2016-04-25 15:30 | 660 | 658
2016-04-25 16:00 | 670 | 668
2016-04-25 16:30 | 711 | 709
2016-04-25 17:00 | 767 | 765
2016-04-25 17:30 | 787 | 783
2016-04-25 18:00 | 802 | 801
2016-04-25 18:30 | 789 | 788
2016-04-25 19:00 | 787 | 785
2016-04-25 19:30 | 774 | 771
2016-04-25 20:00 | 745 | 744
2016-04-25 20:30 | 743 | 742
2016-04-25 21:00 | 710 | 708
2016-04-25 21:30 | 668 | 668
2016-04-25 22:00 | 652 | 651
2016-04-25 22:30 | 644 | 643
2016-04-25 23:00 | 636 | 635
2016-04-25 23:30 | 611 | 609
2016-04-26 | 567 | 563
2016-04-26 00:30 | 544 | 537
2016-04-26 01:00 | 529 | 519
2016-04-26 01:30 | 483 | 470
2016-04-26 02:00 | 458 | 444
2016-04-26 02:30 | 450 | 434
2016-04-26 03:00 | 446 | 430
2016-04-26 03:30 | 451 | 435
2016-04-26 04:00 | 452 | 436
2016-04-26 04:30 | 459 | 446
2016-04-26 05:00 | 460 | 450
2016-04-26 05:30 | 494 | 489
2016-04-26 06:00 | 592 | 590
2016-04-26 06:30 | 671 | 669
2016-04-26 07:00 | 739 | 737
2016-04-26 07:30 | 806 | 805
2016-04-26 08:00 | 818 | 817
2016-04-26 08:30 | 808 | 807
2016-04-26 09:00 | 801 | 800
2016-04-26 09:30 | 796 | 796
2016-04-26 10:00 | 809 | 809
2016-04-26 10:30 | 800 | 798
2016-04-26 11:00 | 784 | 783
2016-04-26 11:30 | 758 | 756
2016-04-26 12:00 | 743 | 741
2016-04-26 12:30 | 760 | 759
2016-04-26 13:00 | 774 | 772
2016-04-26 13:30 | 785 | 783
2016-04-26 14:00 | 774 | 772
2016-04-26 14:30 | 783 | 782
2016-04-26 15:00 | 789 | 788
2016-04-26 15:30 | 808 | 807
2016-04-26 16:00 | 838 | 838
2016-04-26 16:30 | 851 | 850
2016-04-26 17:00 | 879 | 878
2016-04-26 17:30 | 893 | 892
2016-04-26 18:00 | 917 | 914
2016-04-26 18:30 | 905 | 897
2016-04-26 19:00 | 903 | 893
2016-04-26 19:30 | 880 | 865
2016-04-26 20:00 | 848 | 839
2016-04-26 20:30 | 823 | 816
2016-04-26 21:00 | 774 | 771
2016-04-26 21:30 | 738 | 732
2016-04-26 22:00 | 695 | 694
2016-04-26 22:30 | 693 | 693
2016-04-26 23:00 | 664 | 664
2016-04-26 23:30 | 626 | 626
2016-04-27 | 580 | 578
2016-04-27 00:30 | 521 | 515
2016-04-27 01:00 | 504 | 496
2016-04-27 01:30 | 458 | 447
2016-04-27 02:00 | 433 | 420
2016-04-27 02:30 | 434 | 420
2016-04-27 03:00 | 397 | 380
2016-04-27 03:30 | 411 | 395
2016-04-27 04:00 | 394 | 377
2016-04-27 04:30 | 443 | 432
2016-04-27 05:00 | 468 | 460
2016-04-27 05:30 | 518 | 515
2016-04-27 06:00 | 586 | 585
2016-04-27 06:30 | 642 | 642
2016-04-27 07:00 | 721 | 719
2016-04-27 07:30 | 774 | 773
2016-04-27 08:00 | 800 | 791
2016-04-27 08:30 | 785 | 779
2016-04-27 09:00 | 774 | 770
2016-04-27 09:30 | 777 | 772
2016-04-27 10:00 | 784 | 781
2016-04-27 10:30 | 796 | 793
2016-04-27 11:00 | 802 | 799
2016-04-27 11:30 | 800 | 792
2016-04-27 12:00 | 804 | 796
2016-04-27 12:30 | 822 | 813
2016-04-27 13:00 | 823 | 812
2016-04-27 13:30 | 808 | 796
2016-04-27 14:00 | 813 | 802
2016-04-27 14:30 | 806 | 795
2016-04-27 15:00 | 796 | 784
2016-04-27 15:30 | 809 | 798
2016-04-27 16:00 | 846 | 838
2016-04-27 16:30 | 875 | 866
2016-04-27 17:00 | 901 | 893
2016-04-27 17:30 | 913 | 907
2016-04-27 18:00 | 915 | 910
2016-04-27 18:30 | 902 | 893
2016-04-27 19:00 | 883 | 871
2016-04-27 19:30 | 851 | 836
2016-04-27 20:00 | 829 | 822
2016-04-27 20:30 | 813 | 808
2016-04-27 21:00 | 758 | 755
2016-04-27 21:30 | 723 | 721
2016-04-27 22:00 | 693 | 692
2016-04-27 22:30 | 665 | 663
2016-04-27 23:00 | 657 | 656
2016-04-27 23:30 | 620 | 620
2016-04-28 | 583 | 582
2016-04-28 00:30 | 548 | 545
2016-04-28 01:00 | 517 | 512
2016-04-28 01:30 | 504 | 497
2016-04-28 02:00 | 480 | 471
2016-04-28 02:30 | 479 | 469
2016-04-28 03:00 | 475 | 465
2016-04-28 03:30 | 475 | 465
2016-04-28 04:00 | 478 | 467
2016-04-28 04:30 | 485 | 476
2016-04-28 05:00 | 503 | 497
2016-04-28 05:30 | 529 | 527
2016-04-28 06:00 | 568 | 568
2016-04-28 06:30 | 660 | 660
2016-04-28 07:00 | 722 | 720
2016-04-28 07:30 | 769 | 766
2016-04-28 08:00 | 781 | 776
2016-04-28 08:30 | 769 | 766
2016-04-28 09:00 | 770 | 768
2016-04-28 09:30 | 777 | 771
2016-04-28 10:00 | 777 | 772
2016-04-28 10:30 | 788 | 787
2016-04-28 11:00 | 795 | 792
2016-04-28 11:30 | 773 | 769
2016-04-28 12:00 | 777 | 774
2016-04-28 12:30 | 774 | 770
2016-04-28 13:00 | 790 | 786
2016-04-28 13:30 | 806 | 802
2016-04-28 14:00 | 826 | 822
2016-04-28 14:30 | 822 | 818
2016-04-28 15:00 | 840 | 837
2016-04-28 15:30 | 855 | 852
2016-04-28 16:00 | 865 | 862
2016-04-28 16:30 | 881 | 878
2016-04-28 17:00 | 901 | 897
2016-04-28 17:30 | 881 | 877
2016-04-28 18:00 | 912 | 910
2016-04-28 18:30 | 897 | 890
2016-04-28 19:00 | 887 | 877
2016-04-28 19:30 | 866 | 857
2016-04-28 20:00 | 843 | 831
2016-04-28 20:30 | 823 | 810
2016-04-28 21:00 | 784 | 774
2016-04-28 21:30 | 746 | 737
2016-04-28 22:00 | 701 | 700
2016-04-28 22:30 | 670 | 669
2016-04-28 23:00 | 664 | 662
2016-04-28 23:30 | 630 | 628
2016-04-29 | 587 | 586
2016-04-29 00:30 | 549 | 545
2016-04-29 01:00 | 526 | 519
2016-04-29 01:30 | 504 | 494
2016-04-29 02:00 | 486 | 474
2016-04-29 02:30 | 471 | 458
2016-04-29 03:00 | 482 | 469
2016-04-29 03:30 | 479 | 466
2016-04-29 04:00 | 481 | 467
2016-04-29 04:30 | 434 | 422
2016-04-29 05:00 | 507 | 499
2016-04-29 05:30 | 542 | 539
2016-04-29 06:00 | 589 | 588
2016-04-29 06:30 | 671 | 668
2016-04-29 07:00 | 725 | 722
2016-04-29 07:30 | 793 | 787
2016-04-29 08:00 | 821 | 809
2016-04-29 08:30 | 823 | 812
2016-04-29 09:00 | 813 | 802
2016-04-29 09:30 | 828 | 820
2016-04-29 10:00 | 831 | 825
2016-04-29 10:30 | 821 | 815
2016-04-29 11:00 | 795 | 789
2016-04-29 11:30 | 790 | 786
2016-04-29 12:00 | 796 | 793
2016-04-29 12:30 | 817 | 815
2016-04-29 13:00 | 827 | 824
2016-04-29 13:30 | 812 | 808
2016-04-29 14:00 | 832 | 829
2016-04-29 14:30 | 840 | 836
2016-04-29 15:00 | 842 | 838
2016-04-29 15:30 | 836 | 831
2016-04-29 16:00 | 852 | 847
2016-04-29 16:30 | 868 | 862
2016-04-29 17:00 | 888 | 883
2016-04-29 17:30 | 884 | 880
2016-04-29 18:00 | 898 | 894
2016-04-29 18:30 | 874 | 868
2016-04-29 19:00 | 847 | 839
2016-04-29 19:30 | 818 | 809
2016-04-29 20:00 | 803 | 802
2016-04-29 20:30 | 795 | 793
2016-04-29 21:00 | 762 | 759
2016-04-29 21:30 | 731 | 729
2016-04-29 22:00 | 704 | 702
2016-04-29 22:30 | 687 | 685
2016-04-29 23:00 | 680 | 679
2016-04-29 23:30 | 647 | 645
2016-04-30 | 601 | 599
2016-04-30 00:30 | 566 | 565
2016-04-30 01:00 | 549 | 545
2016-04-30 01:30 | 530 | 524
2016-04-30 02:00 | 511 | 503
2016-04-30 02:30 | 503 | 495
2016-04-30 03:00 | 497 | 486
2016-04-30 03:30 | 492 | 481
2016-04-30 04:00 | 493 | 481
2016-04-30 04:30 | 487 | 476
2016-04-30 05:00 | 489 | 479
2016-04-30 05:30 | 508 | 499
2016-04-30 06:00 | 525 | 519
2016-04-30 06:30 | 548 | 544
2016-04-30 07:00 | 569 | 565
2016-04-30 07:30 | 603 | 603
2016-04-30 08:00 | 633 | 633
2016-04-30 08:30 | 664 | 664
2016-04-30 09:00 | 684 | 684
2016-04-30 09:30 | 693 | 692
2016-04-30 10:00 | 688 | 688
2016-04-30 10:30 | 698 | 698
2016-04-30 11:00 | 699 | 698
2016-04-30 11:30 | 683 | 682
2016-04-30 12:00 | 670 | 669
2016-04-30 12:30 | 662 | 661
2016-04-30 13:00 | 677 | 676
2016-04-30 13:30 | 671 | 670
2016-04-30 14:00 | 690 | 690
2016-04-30 14:30 | 699 | 698
2016-04-30 15:00 | 702 | 701
2016-04-30 15:30 | 720 | 720
2016-04-30 16:00 | 738 | 738
2016-04-30 16:30 | 763 | 762
2016-04-30 17:00 | 781 | 781
2016-04-30 17:30 | 793 | 789
2016-04-30 18:00 | 800 | 800
2016-04-30 18:30 | 793 | 793
2016-04-30 19:00 | 783 | 782
2016-04-30 19:30 | 771 | 770
2016-04-30 20:00 | 765 | 764
2016-04-30 20:30 | 755 | 753
2016-04-30 21:00 | 723 | 722
2016-04-30 21:30 | 698 | 697
2016-04-30 22:00 | 689 | 688
2016-04-30 22:30 | 674 | 674
2016-04-30 23:00 | 677 | 677
2016-04-30 23:30 | 642 | 641
2016-05-01 | 601 | 599
2016-05-01 00:30 | 563 | 558
2016-05-01 01:00 | 539 | 532
2016-05-01 01:30 | 483 | 473
2016-05-01 02:00 | 463 | 451
2016-05-01 02:30 | 425 | 410
2016-05-01 03:00 | 445 | 430
2016-05-01 03:30 | 447 | 432
2016-05-01 04:00 | 452 | 438
2016-05-01 04:30 | 455 | 442
2016-05-01 05:00 | 449 | 436
2016-05-01 05:30 | 461 | 451
2016-05-01 06:00 | 470 | 462
2016-05-01 06:30 | 490 | 483
2016-05-01 07:00 | 501 | 493
2016-05-01 07:30 | 541 | 537
2016-05-01 08:00 | 585 | 584
2016-05-01 08:30 | 628 | 628
2016-05-01 09:00 | 662 | 662
2016-05-01 09:30 | 693 | 693
2016-05-01 10:00 | 705 | 705
2016-05-01 10:30 | 713 | 713
2016-05-01 11:00 | 715 | 715
2016-05-01 11:30 | 703 | 703
2016-05-01 12:00 | 697 | 697
2016-05-01 12:30 | 694 | 694
2016-05-01 13:00 | 692 | 692
2016-05-01 13:30 | 683 | 682
2016-05-01 14:00 | 685 | 684
2016-05-01 14:30 | 684 | 683
2016-05-01 15:00 | 689 | 689
2016-05-01 15:30 | 674 | 673
2016-05-01 16:00 | 696 | 696
2016-05-01 16:30 | 709 | 709
2016-05-01 17:00 | 726 | 726
2016-05-01 17:30 | 739 | 739
2016-05-01 18:00 | 768 | 767
2016-05-01 18:30 | 773 | 770
2016-05-01 19:00 | 761 | 756
2016-05-01 19:30 | 743 | 735
2016-05-01 20:00 | 724 | 723
2016-05-01 20:30 | 714 | 713
2016-05-01 21:00 | 685 | 682
2016-05-01 21:30 | 670 | 668
2016-05-01 22:00 | 659 | 655
2016-05-01 22:30 | 643 | 642
2016-05-01 23:00 | 640 | 639
2016-05-01 23:30 | 608 | 606
2016-05-02 | 576 | 572
2016-05-02 00:30 | 538 | 530
2016-05-02 01:00 | 485 | 473
2016-05-02 01:30 | 466 | 452
2016-05-02 02:00 | 454 | 438
2016-05-02 02:30 | 452 | 434
2016-05-02 03:00 | 449 | 430
2016-05-02 03:30 | 447 | 428
2016-05-02 04:00 | 450 | 431
2016-05-02 04:30 | 448 | 430
2016-05-02 05:00 | 452 | 435
2016-05-02 05:30 | 452 | 438
2016-05-02 06:00 | 484 | 474
2016-05-02 06:30 | 507 | 497
2016-05-02 07:00 | 517 | 508
2016-05-02 07:30 | 546 | 542
2016-05-02 08:00 | 568 | 567
2016-05-02 08:30 | 601 | 600
2016-05-02 09:00 | 620 | 618
2016-05-02 09:30 | 634 | 633
2016-05-02 10:00 | 638 | 638
2016-05-02 10:30 | 656 | 656
2016-05-02 11:00 | 670 | 670
2016-05-02 11:30 | 667 | 667
2016-05-02 12:00 | 654 | 654
2016-05-02 12:30 | 654 | 654
2016-05-02 13:00 | 653 | 653
2016-05-02 13:30 | 653 | 653
2016-05-02 14:00 | 663 | 663
2016-05-02 14:30 | 674 | 674
2016-05-02 15:00 | 677 | 677
2016-05-02 15:30 | 715 | 715
2016-05-02 16:00 | 724 | 723
2016-05-02 16:30 | 745 | 745
2016-05-02 17:00 | 774 | 774
2016-05-02 17:30 | 813 | 813
2016-05-02 18:00 | 835 | 834
2016-05-02 18:30 | 821 | 815
2016-05-02 19:00 | 820 | 812
2016-05-02 19:30 | 800 | 791
2016-05-02 20:00 | 782 | 778
2016-05-02 20:30 | 778 | 775
2016-05-02 21:00 | 740 | 735
2016-05-02 21:30 | 703 | 701
2016-05-02 22:00 | 680 | 678
2016-05-02 22:30 | 663 | 663
2016-05-02 23:00 | 635 | 635
2016-05-02 23:30 | 633 | 631
2016-05-03 | 594 | 590
2016-05-03 00:30 | 559 | 551
2016-05-03 01:00 | 531 | 520
2016-05-03 01:30 | 428 | 413
2016-05-03 02:00 | 434 | 416
2016-05-03 02:30 | 434 | 415
2016-05-03 03:00 | 429 | 409
2016-05-03 03:30 | 423 | 403
2016-05-03 04:00 | 425 | 405
2016-05-03 04:30 | 437 | 422
2016-05-03 05:00 | 456 | 445
2016-05-03 05:30 | 465 | 458
2016-05-03 06:00 | 547 | 545
2016-05-03 06:30 | 658 | 658
2016-05-03 07:00 | 742 | 741
2016-05-03 07:30 | 794 | 794
2016-05-03 08:00 | 810 | 809
2016-05-03 08:30 | 810 | 810
2016-05-03 09:00 | 791 | 791
2016-05-03 09:30 | 792 | 792
2016-05-03 10:00 | 784 | 784
2016-05-03 10:30 | 784 | 784
2016-05-03 11:00 | 786 | 785
2016-05-03 11:30 | 777 | 777
2016-05-03 12:00 | 778 | 778
2016-05-03 12:30 | 795 | 794
2016-05-03 13:00 | 812 | 811
2016-05-03 13:30 | 822 | 821
2016-05-03 14:00 | 851 | 849
2016-05-03 14:30 | 866 | 864
2016-05-03 15:00 | 885 | 884
2016-05-03 15:30 | 904 | 902
2016-05-03 16:00 | 924 | 922
2016-05-03 16:30 | 949 | 948
2016-05-03 17:00 | 965 | 965
2016-05-03 17:30 | 980 | 980
2016-05-03 18:00 | 997 | 997
2016-05-03 18:30 | 974 | 974
2016-05-03 19:00 | 956 | 955
2016-05-03 19:30 | 924 | 922
2016-05-03 20:00 | 888 | 888
2016-05-03 20:30 | 861 | 861
2016-05-03 21:00 | 811 | 811
2016-05-03 21:30 | 764 | 764
2016-05-03 22:00 | 737 | 737
2016-05-03 22:30 | 714 | 714
2016-05-03 23:00 | 692 | 692
2016-05-03 23:30 | 654 | 654
2016-05-04 | 606 | 606
2016-05-04 00:30 | 575 | 573
2016-05-04 01:00 | 531 | 528
2016-05-04 01:30 | 492 | 488
2016-05-04 02:00 | 490 | 485
2016-05-04 02:30 | 463 | 457
2016-05-04 03:00 | 477 | 470
2016-05-04 03:30 | 479 | 473
2016-05-04 04:00 | 474 | 469
2016-05-04 04:30 | 477 | 472
2016-05-04 05:00 | 491 | 488
2016-05-04 05:30 | 522 | 521
2016-05-04 06:00 | 605 | 605
2016-05-04 06:30 | 683 | 680
2016-05-04 07:00 | 732 | 731
2016-05-04 07:30 | 808 | 808
2016-05-04 08:00 | 819 | 819
2016-05-04 08:30 | 800 | 800
2016-05-04 09:00 | 781 | 781
2016-05-04 09:30 | 769 | 769
2016-05-04 10:00 | 764 | 764
2016-05-04 10:30 | 751 | 751
2016-05-04 11:00 | 740 | 740
2016-05-04 11:30 | 727 | 727
2016-05-04 12:00 | 733 | 733
2016-05-04 12:30 | 737 | 737
2016-05-04 13:00 | 747 | 747
2016-05-04 13:30 | 753 | 753
2016-05-04 14:00 | 832 | 832
2016-05-04 14:30 | 843 | 841
2016-05-04 15:00 | 869 | 867
2016-05-04 15:30 | 891 | 890
2016-05-04 16:00 | 919 | 918
2016-05-04 16:30 | 955 | 954
2016-05-04 17:00 | 988 | 982
2016-05-04 17:30 | 1002 | 997
2016-05-04 18:00 | 1034 | 1031
2016-05-04 18:30 | 1012 | 1005
2016-05-04 19:00 | 992 | 984
2016-05-04 19:30 | 959 | 956
2016-05-04 20:00 | 937 | 936
2016-05-04 20:30 | 926 | 924
2016-05-04 21:00 | 871 | 869
2016-05-04 21:30 | 824 | 823
2016-05-04 22:00 | 794 | 792
2016-05-04 22:30 | 769 | 765
2016-05-04 23:00 | 753 | 749
2016-05-04 23:30 | 716 | 713
2016-05-05 | 666 | 660
2016-05-05 00:30 | 623 | 614
2016-05-05 01:00 | 595 | 582
2016-05-05 01:30 | 576 | 562
2016-05-05 02:00 | 564 | 548
2016-05-05 02:30 | 554 | 536
2016-05-05 03:00 | 550 | 532
2016-05-05 03:30 | 552 | 533
2016-05-05 04:00 | 522 | 502
2016-05-05 04:30 | 522 | 504
2016-05-05 05:00 | 546 | 532
2016-05-05 05:30 | 608 | 600
2016-05-05 06:00 | 646 | 640
2016-05-05 06:30 | 729 | 721
2016-05-05 07:00 | 802 | 794
2016-05-05 07:30 | 848 | 844
2016-05-05 08:00 | 849 | 847
2016-05-05 08:30 | 859 | 858
2016-05-05 09:00 | 830 | 830
2016-05-05 09:30 | 811 | 811
2016-05-05 10:00 | 807 | 807
2016-05-05 10:30 | 843 | 841
2016-05-05 11:00 | 842 | 841
2016-05-05 11:30 | 840 | 839
2016-05-05 12:00 | 845 | 844
2016-05-05 12:30 | 800 | 800
2016-05-05 13:00 | 813 | 813
2016-05-05 13:30 | 818 | 817
2016-05-05 14:00 | 834 | 834
2016-05-05 14:30 | 847 | 846
2016-05-05 15:00 | 864 | 864
2016-05-05 15:30 | 886 | 886
2016-05-05 16:00 | 912 | 912
2016-05-05 16:30 | 940 | 940
2016-05-05 17:00 | 958 | 958
2016-05-05 17:30 | 978 | 978
2016-05-05 18:00 | 1018 | 1017
2016-05-05 18:30 | 1001 | 1001
2016-05-05 19:00 | 989 | 988
2016-05-05 19:30 | 950 | 947
2016-05-05 20:00 | 934 | 929
2016-05-05 20:30 | 931 | 923
2016-05-05 21:00 | 870 | 863
2016-05-05 21:30 | 809 | 807
2016-05-05 22:00 | 771 | 768
2016-05-05 22:30 | 747 | 744
2016-05-05 23:00 | 729 | 728
2016-05-05 23:30 | 694 | 692
2016-05-06 | 645 | 640
2016-05-06 00:30 | 602 | 593
2016-05-06 01:00 | 574 | 562
2016-05-06 01:30 | 552 | 537
2016-05-06 02:00 | 552 | 535
2016-05-06 02:30 | 554 | 535
2016-05-06 03:00 | 525 | 504
2016-05-06 03:30 | 525 | 504
2016-05-06 04:00 | 527 | 507
2016-05-06 04:30 | 532 | 513
2016-05-06 05:00 | 546 | 531
2016-05-06 05:30 | 586 | 578
2016-05-06 06:00 | 628 | 624
2016-05-06 06:30 | 708 | 707
2016-05-06 07:00 | 786 | 784
2016-05-06 07:30 | 844 | 837
2016-05-06 08:00 | 843 | 837
2016-05-06 08:30 | 844 | 838
2016-05-06 09:00 | 843 | 838
2016-05-06 09:30 | 836 | 832
2016-05-06 10:00 | 833 | 831
2016-05-06 10:30 | 817 | 815
2016-05-06 11:00 | 812 | 811
2016-05-06 11:30 | 814 | 813
2016-05-06 12:00 | 825 | 824
2016-05-06 12:30 | 818 | 816
2016-05-06 13:00 | 826 | 824
2016-05-06 13:30 | 837 | 835
2016-05-06 14:00 | 864 | 862
2016-05-06 14:30 | 887 | 883
2016-05-06 15:00 | 882 | 878
2016-05-06 15:30 | 895 | 890
2016-05-06 16:00 | 920 | 915
2016-05-06 16:30 | 936 | 930
2016-05-06 17:00 | 961 | 955
2016-05-06 17:30 | 970 | 965
2016-05-06 18:00 | 997 | 989
2016-05-06 18:30 | 976 | 960
2016-05-06 19:00 | 961 | 942
2016-05-06 19:30 | 931 | 909
2016-05-06 20:00 | 906 | 889
2016-05-06 20:30 | 895 | 877
2016-05-06 21:00 | 845 | 829
2016-05-06 21:30 | 813 | 798
2016-05-06 22:00 | 781 | 770
2016-05-06 22:30 | 768 | 762
2016-05-06 23:00 | 750 | 744
2016-05-06 23:30 | 715 | 712
2016-05-07 | 672 | 667
2016-05-07 00:30 | 631 | 622
2016-05-07 01:00 | 603 | 591
2016-05-07 01:30 | 584 | 569
2016-05-07 02:00 | 543 | 524
2016-05-07 02:30 | 529 | 508
2016-05-07 03:00 | 524 | 503
2016-05-07 03:30 | 519 | 499
2016-05-07 04:00 | 520 | 500
2016-05-07 04:30 | 523 | 503
2016-05-07 05:00 | 527 | 508
2016-05-07 05:30 | 540 | 525
2016-05-07 06:00 | 555 | 543
2016-05-07 06:30 | 578 | 567
2016-05-07 07:00 | 603 | 595
2016-05-07 07:30 | 620 | 616
2016-05-07 08:00 | 667 | 665
2016-05-07 08:30 | 689 | 689
2016-05-07 09:00 | 699 | 698
2016-05-07 09:30 | 698 | 697
2016-05-07 10:00 | 695 | 694
2016-05-07 10:30 | 696 | 696
2016-05-07 11:00 | 689 | 689
2016-05-07 11:30 | 678 | 678
2016-05-07 12:00 | 678 | 678
2016-05-07 12:30 | 671 | 671
2016-05-07 13:00 | 672 | 671
2016-05-07 13:30 | 673 | 673
2016-05-07 14:00 | 687 | 686
2016-05-07 14:30 | 696 | 695
2016-05-07 15:00 | 709 | 709
2016-05-07 15:30 | 731 | 731
2016-05-07 16:00 | 754 | 754
2016-05-07 16:30 | 782 | 782
2016-05-07 17:00 | 805 | 805
2016-05-07 17:30 | 823 | 822
2016-05-07 18:00 | 868 | 863
2016-05-07 18:30 | 873 | 866
2016-05-07 19:00 | 858 | 849
2016-05-07 19:30 | 832 | 824
2016-05-07 20:00 | 821 | 819
2016-05-07 20:30 | 805 | 801
2016-05-07 21:00 | 773 | 768
2016-05-07 21:30 | 747 | 744
2016-05-07 22:00 | 731 | 727
2016-05-07 22:30 | 721 | 715
2016-05-07 23:00 | 721 | 715
2016-05-07 23:30 | 697 | 691
2016-05-08 | 652 | 647
2016-05-08 00:30 | 609 | 600
2016-05-08 01:00 | 583 | 571
2016-05-08 01:30 | 559 | 543
2016-05-08 02:00 | 522 | 503
2016-05-08 02:30 | 523 | 502
2016-05-08 03:00 | 514 | 492
2016-05-08 03:30 | 508 | 485
2016-05-08 04:00 | 508 | 484
2016-05-08 04:30 | 506 | 482
2016-05-08 05:00 | 512 | 490
2016-05-08 05:30 | 521 | 500
2016-05-08 06:00 | 529 | 510
2016-05-08 06:30 | 541 | 522
2016-05-08 07:00 | 556 | 539
2016-05-08 07:30 | 584 | 572
2016-05-08 08:00 | 585 | 576
2016-05-08 08:30 | 607 | 603
2016-05-08 09:00 | 636 | 634
2016-05-08 09:30 | 645 | 644
2016-05-08 10:00 | 652 | 652
2016-05-08 10:30 | 664 | 663
2016-05-08 11:00 | 665 | 665
2016-05-08 11:30 | 665 | 665
2016-05-08 12:00 | 659 | 659
2016-05-08 12:30 | 658 | 658
2016-05-08 13:00 | 652 | 652
2016-05-08 13:30 | 648 | 648
2016-05-08 14:00 | 655 | 655
2016-05-08 14:30 | 686 | 686
2016-05-08 15:00 | 706 | 706
2016-05-08 15:30 | 731 | 730
2016-05-08 16:00 | 757 | 756
2016-05-08 16:30 | 783 | 783
2016-05-08 17:00 | 812 | 812
2016-05-08 17:30 | 835 | 835
2016-05-08 18:00 | 873 | 871
2016-05-08 18:30 | 872 | 867
2016-05-08 19:00 | 863 | 856
2016-05-08 19:30 | 845 | 834
2016-05-08 20:00 | 831 | 825
2016-05-08 20:30 | 819 | 812
2016-05-08 21:00 | 780 | 772
2016-05-08 21:30 | 753 | 747
2016-05-08 22:00 | 732 | 725
2016-05-08 22:30 | 704 | 699
2016-05-08 23:00 | 695 | 689
2016-05-08 23:30 | 664 | 660
2016-05-09 | 632 | 625
2016-05-09 00:30 | 595 | 583
2016-05-09 01:00 | 549 | 533
2016-05-09 01:30 | 532 | 513
2016-05-09 02:00 | 521 | 499
2016-05-09 02:30 | 517 | 494
2016-05-09 03:00 | 517 | 495
2016-05-09 03:30 | 518 | 496
2016-05-09 04:00 | 523 | 502
2016-05-09 04:30 | 531 | 513
2016-05-09 05:00 | 546 | 532
2016-05-09 05:30 | 602 | 593
2016-05-09 06:00 | 647 | 640
2016-05-09 06:30 | 715 | 713
2016-05-09 07:00 | 772 | 772
2016-05-09 07:30 | 838 | 838
2016-05-09 08:00 | 860 | 858
2016-05-09 08:30 | 856 | 856
2016-05-09 09:00 | 845 | 845
2016-05-09 09:30 | 866 | 865
2016-05-09 10:00 | 876 | 875
2016-05-09 10:30 | 1028 | 1028
2016-05-09 11:00 | 1077 | 1077
2016-05-09 11:30 | 1083 | 1082
2016-05-09 12:00 | 1078 | 1078
2016-05-09 12:30 | 1078 | 1078
2016-05-09 13:00 | 1089 | 1089
2016-05-09 13:30 | 1091 | 1091
2016-05-09 14:00 | 1095 | 1095
2016-05-09 14:30 | 1110 | 1110
2016-05-09 15:00 | 1132 | 1132
2016-05-09 15:30 | 1148 | 1148
2016-05-09 16:00 | 1159 | 1159
2016-05-09 16:30 | 1177 | 1177
2016-05-09 17:00 | 1195 | 1195
2016-05-09 17:30 | 1257 | 1256
2016-05-09 18:00 | 1283 | 1282
2016-05-09 18:30 | 1239 | 1239
2016-05-09 19:00 | 1206 | 1205
2016-05-09 19:30 | 1148 | 1146
2016-05-09 20:00 | 1126 | 1125
2016-05-09 20:30 | 1112 | 1111
2016-05-09 21:00 | 1048 | 1047
2016-05-09 21:30 | 995 | 994
2016-05-09 22:00 | 957 | 955
2016-05-09 22:30 | 913 | 910
2016-05-09 23:00 | 893 | 892
2016-05-09 23:30 | 853 | 851
2016-05-10 | 802 | 800
2016-05-10 00:30 | 757 | 753
2016-05-10 01:00 | 721 | 716
2016-05-10 01:30 | 690 | 683
2016-05-10 02:00 | 665 | 657
2016-05-10 02:30 | 646 | 636
2016-05-10 03:00 | 639 | 629
2016-05-10 03:30 | 630 | 619
2016-05-10 04:00 | 641 | 631
2016-05-10 04:30 | 648 | 639
2016-05-10 05:00 | 676 | 669
2016-05-10 05:30 | 724 | 720
2016-05-10 06:00 | 777 | 774
2016-05-10 06:30 | 882 | 882
2016-05-10 07:00 | 982 | 982
2016-05-10 07:30 | 1032 | 1032
2016-05-10 08:00 | 1076 | 1075
2016-05-10 08:30 | 1103 | 1103
2016-05-10 09:00 | 1105 | 1103
2016-05-10 09:30 | 1132 | 1131
2016-05-10 10:00 | 1137 | 1134
2016-05-10 10:30 | 1123 | 1120
2016-05-10 11:00 | 1112 | 1109
2016-05-10 11:30 | 1095 | 1092
2016-05-10 12:00 | 1095 | 1092
2016-05-10 12:30 | 1090 | 1088
2016-05-10 13:00 | 1068 | 1064
2016-05-10 13:30 | 1057 | 1053
2016-05-10 14:00 | 1104 | 1102
2016-05-10 14:30 | 1075 | 1073
2016-05-10 15:00 | 1116 | 1113
2016-05-10 15:30 | 1131 | 1128
2016-05-10 16:00 | 1140 | 1136
2016-05-10 16:30 | 1152 | 1147
2016-05-10 17:00 | 1169 | 1165
2016-05-10 17:30 | 1200 | 1197
2016-05-10 18:00 | 1229 | 1226
2016-05-10 18:30 | 1191 | 1186
2016-05-10 19:00 | 1176 | 1170
2016-05-10 19:30 | 1130 | 1126
2016-05-10 20:00 | 1103 | 1101
2016-05-10 20:30 | 1086 | 1083
2016-05-10 21:00 | 1020 | 1018
2016-05-10 21:30 | 968 | 968
2016-05-10 22:00 | 929 | 929
2016-05-10 22:30 | 895 | 894
2016-05-10 23:00 | 862 | 862
2016-05-10 23:30 | 824 | 822
2016-05-11 | 772 | 768
2016-05-11 00:30 | 727 | 720
2016-05-11 01:00 | 703 | 693
2016-05-11 01:30 | 683 | 669
2016-05-11 02:00 | 657 | 642
2016-05-11 02:30 | 640 | 622
2016-05-11 03:00 | 632 | 614
2016-05-11 03:30 | 634 | 615
2016-05-11 04:00 | 632 | 613
2016-05-11 04:30 | 643 | 625
2016-05-11 05:00 | 663 | 648
2016-05-11 05:30 | 722 | 713
2016-05-11 06:00 | 765 | 760
2016-05-11 06:30 | 873 | 873
2016-05-11 07:00 | 959 | 959
2016-05-11 07:30 | 1052 | 1051
2016-05-11 08:00 | 1084 | 1080
2016-05-11 08:30 | 1082 | 1076
2016-05-11 09:00 | 1068 | 1063
2016-05-11 09:30 | 1057 | 1053
2016-05-11 10:00 | 1041 | 1036
2016-05-11 10:30 | 1006 | 1000
2016-05-11 11:00 | 1005 | 1000
2016-05-11 11:30 | 1027 | 1019
2016-05-11 12:00 | 1038 | 1025
2016-05-11 12:30 | 1016 | 1002
2016-05-11 13:00 | 1003 | 990
2016-05-11 13:30 | 953 | 943
2016-05-11 14:00 | 977 | 973
2016-05-11 14:30 | 998 | 995
2016-05-11 15:00 | 1053 | 1050
2016-05-11 15:30 | 1053 | 1049
2016-05-11 16:00 | 1055 | 1050
2016-05-11 16:30 | 1063 | 1058
2016-05-11 17:00 | 1104 | 1098
2016-05-11 17:30 | 1145 | 1139
2016-05-11 18:00 | 1179 | 1174
2016-05-11 18:30 | 1153 | 1146
2016-05-11 19:00 | 1137 | 1128
2016-05-11 19:30 | 1114 | 1101
2016-05-11 20:00 | 1090 | 1086
2016-05-11 20:30 | 1088 | 1085
2016-05-11 21:00 | 1031 | 1028
2016-05-11 21:30 | 972 | 971
2016-05-11 22:00 | 926 | 923
2016-05-11 22:30 | 892 | 889
2016-05-11 23:00 | 868 | 866
2016-05-11 23:30 | 825 | 824
2016-05-12 | 777 | 773
2016-05-12 00:30 | 730 | 722
2016-05-12 01:00 | 700 | 690
2016-05-12 01:30 | 672 | 660
2016-05-12 02:00 | 643 | 628
2016-05-12 02:30 | 634 | 618
2016-05-12 03:00 | 628 | 613
2016-05-12 03:30 | 627 | 612
2016-05-12 04:00 | 631 | 616
2016-05-12 04:30 | 645 | 632
2016-05-12 05:00 | 671 | 661
2016-05-12 05:30 | 711 | 707
2016-05-12 06:00 | 777 | 775
2016-05-12 06:30 | 872 | 871
2016-05-12 07:00 | 981 | 979
2016-05-12 07:30 | 1052 | 1046
2016-05-12 08:00 | 1057 | 1046
2016-05-12 08:30 | 1026 | 1009
2016-05-12 09:00 | 980 | 968
2016-05-12 09:30 | 947 | 935
2016-05-12 10:00 | 923 | 912
2016-05-12 10:30 | 903 | 892
2016-05-12 11:00 | 889 | 878
2016-05-12 11:30 | 880 | 869
2016-05-12 12:00 | 879 | 870
2016-05-12 12:30 | 884 | 876
2016-05-12 13:00 | 890 | 882
2016-05-12 13:30 | 898 | 892
2016-05-12 14:00 | 926 | 920
2016-05-12 14:30 | 945 | 940
2016-05-12 15:00 | 962 | 958
2016-05-12 15:30 | 986 | 982
2016-05-12 16:00 | 1032 | 1028
2016-05-12 16:30 | 1062 | 1058
2016-05-12 17:00 | 1092 | 1085
2016-05-12 17:30 | 1126 | 1120
2016-05-12 18:00 | 1183 | 1174
2016-05-12 18:30 | 1171 | 1152
2016-05-12 19:00 | 1167 | 1145
2016-05-12 19:30 | 1133 | 1112
2016-05-12 20:00 | 1105 | 1096
2016-05-12 20:30 | 1086 | 1078
2016-05-12 21:00 | 1045 | 1033
2016-05-12 21:30 | 983 | 974
2016-05-12 22:00 | 936 | 929
2016-05-12 22:30 | 909 | 907
2016-05-12 23:00 | 881 | 878
2016-05-12 23:30 | 850 | 845
2016-05-13 | 795 | 792
2016-05-13 00:30 | 753 | 748
2016-05-13 01:00 | 715 | 707
2016-05-13 01:30 | 683 | 672
2016-05-13 02:00 | 650 | 637
2016-05-13 02:30 | 632 | 617
2016-05-13 03:00 | 618 | 602
2016-05-13 03:30 | 623 | 607
2016-05-13 04:00 | 627 | 611
2016-05-13 04:30 | 638 | 624
2016-05-13 05:00 | 658 | 647
2016-05-13 05:30 | 699 | 693
2016-05-13 06:00 | 768 | 766
2016-05-13 06:30 | 873 | 873
2016-05-13 07:00 | 968 | 963
2016-05-13 07:30 | 1033 | 1030
2016-05-13 08:00 | 1047 | 1034
2016-05-13 08:30 | 1020 | 1008
2016-05-13 09:00 | 984 | 972
2016-05-13 09:30 | 970 | 957
2016-05-13 10:00 | 952 | 941
2016-05-13 10:30 | 940 | 929
2016-05-13 11:00 | 928 | 919
2016-05-13 11:30 | 914 | 905
2016-05-13 12:00 | 909 | 900
2016-05-13 12:30 | 910 | 902
2016-05-13 13:00 | 916 | 908
2016-05-13 13:30 | 929 | 922
2016-05-13 14:00 | 949 | 943
2016-05-13 14:30 | 971 | 965
2016-05-13 15:00 | 993 | 988
2016-05-13 15:30 | 1006 | 1001
2016-05-13 16:00 | 1043 | 1038
2016-05-13 16:30 | 1072 | 1067
2016-05-13 17:00 | 1104 | 1100
2016-05-13 17:30 | 1136 | 1133
2016-05-13 18:00 | 1168 | 1159
2016-05-13 18:30 | 1139 | 1124
2016-05-13 19:00 | 1127 | 1110
2016-05-13 19:30 | 1089 | 1070
2016-05-13 20:00 | 1054 | 1048
2016-05-13 20:30 | 1049 | 1041
2016-05-13 21:00 | 1002 | 995
2016-05-13 21:30 | 955 | 948
2016-05-13 22:00 | 918 | 911
2016-05-13 22:30 | 886 | 885
2016-05-13 23:00 | 881 | 880
2016-05-13 23:30 | 839 | 836
2016-05-14 | 790 | 785
2016-05-14 00:30 | 734 | 728
2016-05-14 01:00 | 700 | 689
2016-05-14 01:30 | 661 | 648
2016-05-14 02:00 | 641 | 624
2016-05-14 02:30 | 640 | 622
2016-05-14 03:00 | 628 | 609
2016-05-14 03:30 | 627 | 608
2016-05-14 04:00 | 621 | 598
2016-05-14 04:30 | 632 | 608
2016-05-14 05:00 | 639 | 617
2016-05-14 05:30 | 653 | 634
2016-05-14 06:00 | 672 | 657
2016-05-14 06:30 | 703 | 690
2016-05-14 07:00 | 751 | 740
2016-05-14 07:30 | 793 | 788
2016-05-14 08:00 | 809 | 806
2016-05-14 08:30 | 835 | 834
2016-05-14 09:00 | 849 | 846
2016-05-14 09:30 | 850 | 849
2016-05-14 10:00 | 838 | 837
2016-05-14 10:30 | 836 | 836
2016-05-14 11:00 | 844 | 844
2016-05-14 11:30 | 827 | 827
2016-05-14 12:00 | 818 | 817
2016-05-14 12:30 | 808 | 807
2016-05-14 13:00 | 812 | 811
2016-05-14 13:30 | 801 | 799
2016-05-14 14:00 | 805 | 804
2016-05-14 14:30 | 810 | 809
2016-05-14 15:00 | 831 | 830
2016-05-14 15:30 | 860 | 860
2016-05-14 16:00 | 893 | 892
2016-05-14 16:30 | 925 | 923
2016-05-14 17:00 | 964 | 962
2016-05-14 17:30 | 1005 | 1004
2016-05-14 18:00 | 1036 | 1033
2016-05-14 18:30 | 1026 | 1018
2016-05-14 19:00 | 1008 | 997
2016-05-14 19:30 | 971 | 958
2016-05-14 20:00 | 953 | 945
2016-05-14 20:30 | 947 | 937
2016-05-14 21:00 | 900 | 893
2016-05-14 21:30 | 869 | 864
2016-05-14 22:00 | 850 | 844
2016-05-14 22:30 | 838 | 834
2016-05-14 23:00 | 825 | 823
2016-05-14 23:30 | 805 | 801
2016-05-15 | 766 | 759
2016-05-15 00:30 | 726 | 716
2016-05-15 01:00 | 695 | 681
2016-05-15 01:30 | 656 | 640
2016-05-15 02:00 | 634 | 615
2016-05-15 02:30 | 613 | 591
2016-05-15 03:00 | 602 | 578
2016-05-15 03:30 | 600 | 576
2016-05-15 04:00 | 600 | 577
2016-05-15 04:30 | 602 | 578
2016-05-15 05:00 | 607 | 585
2016-05-15 05:30 | 615 | 595
2016-05-15 06:00 | 625 | 608
2016-05-15 06:30 | 640 | 622
2016-05-15 07:00 | 663 | 646
2016-05-15 07:30 | 694 | 680
2016-05-15 08:00 | 727 | 717
2016-05-15 08:30 | 754 | 748
2016-05-15 09:00 | 764 | 760
2016-05-15 09:30 | 767 | 765
2016-05-15 10:00 | 767 | 765
2016-05-15 10:30 | 761 | 760
2016-05-15 11:00 | 753 | 752
2016-05-15 11:30 | 738 | 738
2016-05-15 12:00 | 734 | 733
2016-05-15 12:30 | 729 | 729
2016-05-15 13:00 | 738 | 738
2016-05-15 13:30 | 743 | 743
2016-05-15 14:00 | 761 | 761
2016-05-15 14:30 | 775 | 774
2016-05-15 15:00 | 804 | 804
2016-05-15 15:30 | 835 | 835
2016-05-15 16:00 | 878 | 877
2016-05-15 16:30 | 914 | 913
2016-05-15 17:00 | 956 | 956
2016-05-15 17:30 | 1023 | 1023
2016-05-15 18:00 | 1073 | 1071
2016-05-15 18:30 | 1071 | 1067
2016-05-15 19:00 | 1054 | 1049
2016-05-15 19:30 | 1016 | 1007
2016-05-15 20:00 | 998 | 988
2016-05-15 20:30 | 984 | 978
2016-05-15 21:00 | 943 | 937
2016-05-15 21:30 | 912 | 904
2016-05-15 22:00 | 871 | 864
2016-05-15 22:30 | 839 | 837
2016-05-15 23:00 | 826 | 823
2016-05-15 23:30 | 789 | 785
2016-05-16 | 748 | 740
2016-05-16 00:30 | 692 | 679
2016-05-16 01:00 | 662 | 646
2016-05-16 01:30 | 635 | 617
2016-05-16 02:00 | 620 | 600
2016-05-16 02:30 | 605 | 583
2016-05-16 03:00 | 601 | 578
2016-05-16 03:30 | 599 | 576
2016-05-16 04:00 | 605 | 584
2016-05-16 04:30 | 621 | 603
2016-05-16 05:00 | 644 | 630
2016-05-16 05:30 | 687 | 679
2016-05-16 06:00 | 745 | 742
2016-05-16 06:30 | 850 | 846
2016-05-16 07:00 | 946 | 939
2016-05-16 07:30 | 1002 | 998
2016-05-16 08:00 | 1035 | 1013
2016-05-16 08:30 | 1006 | 981
2016-05-16 09:00 | 966 | 958
2016-05-16 09:30 | 946 | 938
2016-05-16 10:00 | 930 | 924
2016-05-16 10:30 | 920 | 915
2016-05-16 11:00 | 923 | 918
2016-05-16 11:30 | 904 | 899
2016-05-16 12:00 | 908 | 904
2016-05-16 12:30 | 905 | 901
2016-05-16 13:00 | 909 | 905
2016-05-16 13:30 | 924 | 921
2016-05-16 14:00 | 942 | 940
2016-05-16 14:30 | 958 | 956
2016-05-16 15:00 | 978 | 974
2016-05-16 15:30 | 995 | 990
2016-05-16 16:00 | 1030 | 1025
2016-05-16 16:30 | 1073 | 1069
2016-05-16 17:00 | 1120 | 1114
2016-05-16 17:30 | 1168 | 1161
2016-05-16 18:00 | 1204 | 1191
2016-05-16 18:30 | 1174 | 1153
2016-05-16 19:00 | 1155 | 1135
2016-05-16 19:30 | 1101 | 1092
2016-05-16 20:00 | 1090 | 1079
2016-05-16 20:30 | 1076 | 1063
2016-05-16 21:00 | 1016 | 1006
2016-05-16 21:30 | 967 | 960
2016-05-16 22:00 | 928 | 923
2016-05-16 22:30 | 895 | 889
2016-05-16 23:00 | 875 | 872
2016-05-16 23:30 | 834 | 829
2016-05-17 | 783 | 776
2016-05-17 00:30 | 726 | 721
2016-05-17 01:00 | 689 | 681
2016-05-17 01:30 | 664 | 654
2016-05-17 02:00 | 646 | 633
2016-05-17 02:30 | 636 | 622
2016-05-17 03:00 | 627 | 612
2016-05-17 03:30 | 628 | 613
2016-05-17 04:00 | 627 | 612
2016-05-17 04:30 | 638 | 625
2016-05-17 05:00 | 660 | 650
2016-05-17 05:30 | 718 | 713
2016-05-17 06:00 | 775 | 774
2016-05-17 06:30 | 871 | 865
2016-05-17 07:00 | 955 | 944
2016-05-17 07:30 | 1011 | 992
2016-05-17 08:00 | 1019 | 1006
2016-05-17 08:30 | 1006 | 992
2016-05-17 09:00 | 998 | 981
2016-05-17 09:30 | 997 | 984
2016-05-17 10:00 | 980 | 969
2016-05-17 10:30 | 964 | 953
2016-05-17 11:00 | 963 | 953
2016-05-17 11:30 | 949 | 940
2016-05-17 12:00 | 947 | 939
2016-05-17 12:30 | 956 | 948
2016-05-17 13:00 | 984 | 978
2016-05-17 13:30 | 1007 | 1002
2016-05-17 14:00 | 1029 | 1021
2016-05-17 14:30 | 1045 | 1034
2016-05-17 15:00 | 1062 | 1043
2016-05-17 15:30 | 1061 | 1039
2016-05-17 16:00 | 1098 | 1076
2016-05-17 16:30 | 1118 | 1098
2016-05-17 17:00 | 1152 | 1132
2016-05-17 17:30 | 1192 | 1176
2016-05-17 18:00 | 1236 | 1213
2016-05-17 18:30 | 1201 | 1171
2016-05-17 19:00 | 1185 | 1152
2016-05-17 19:30 | 1134 | 1114
2016-05-17 20:00 | 1113 | 1097
2016-05-17 20:30 | 1113 | 1097
2016-05-17 21:00 | 1046 | 1035
2016-05-17 21:30 | 999 | 984
2016-05-17 22:00 | 956 | 943
2016-05-17 22:30 | 930 | 917
2016-05-17 23:00 | 908 | 896
2016-05-17 23:30 | 877 | 867
2016-05-18 | 830 | 821
2016-05-18 00:30 | 769 | 765
2016-05-18 01:00 | 735 | 728
2016-05-18 01:30 | 710 | 701
2016-05-18 02:00 | 685 | 674
2016-05-18 02:30 | 667 | 655
2016-05-18 03:00 | 654 | 640
2016-05-18 03:30 | 645 | 630
2016-05-18 04:00 | 643 | 628
2016-05-18 04:30 | 656 | 642
2016-05-18 05:00 | 685 | 675
2016-05-18 05:30 | 740 | 734
2016-05-18 06:00 | 798 | 797
2016-05-18 06:30 | 900 | 897
2016-05-18 07:00 | 994 | 985
2016-05-18 07:30 | 1032 | 1027
2016-05-18 08:00 | 1041 | 1033
2016-05-18 08:30 | 1023 | 1008
2016-05-18 09:00 | 997 | 984
2016-05-18 09:30 | 990 | 978
2016-05-18 10:00 | 982 | 973
2016-05-18 10:30 | 977 | 969
2016-05-18 11:00 | 969 | 963
2016-05-18 11:30 | 971 | 966
2016-05-18 12:00 | 972 | 968
2016-05-18 12:30 | 979 | 974
2016-05-18 13:00 | 1001 | 994
2016-05-18 13:30 | 999 | 992
2016-05-18 14:00 | 1022 | 1016
2016-05-18 14:30 | 1045 | 1039
2016-05-18 15:00 | 1029 | 1021
2016-05-18 15:30 | 1049 | 1041
2016-05-18 16:00 | 1087 | 1079
2016-05-18 16:30 | 1108 | 1101
2016-05-18 17:00 | 1153 | 1146
2016-05-18 17:30 | 1188 | 1182
2016-05-18 18:00 | 1239 | 1230
2016-05-18 18:30 | 1200 | 1184
2016-05-18 19:00 | 1184 | 1165
2016-05-18 19:30 | 1141 | 1122
2016-05-18 20:00 | 1125 | 1118
2016-05-18 20:30 | 1119 | 1110
2016-05-18 21:00 | 1066 | 1052
2016-05-18 21:30 | 1009 | 993
2016-05-18 22:00 | 961 | 947
2016-05-18 22:30 | 925 | 918
2016-05-18 23:00 | 886 | 880
2016-05-18 23:30 | 843 | 838
2016-05-19 | 764 | 756
2016-05-19 00:30 | 705 | 696
2016-05-19 01:00 | 674 | 662
2016-05-19 01:30 | 673 | 657
2016-05-19 02:00 | 659 | 641
2016-05-19 02:30 | 651 | 632
2016-05-19 03:00 | 640 | 619
2016-05-19 03:30 | 635 | 611
2016-05-19 04:00 | 648 | 625
2016-05-19 04:30 | 657 | 637
2016-05-19 05:00 | 681 | 665
2016-05-19 05:30 | 725 | 716
2016-05-19 06:00 | 779 | 773
2016-05-19 06:30 | 878 | 871
2016-05-19 07:00 | 967 | 957
2016-05-19 07:30 | 1017 | 1009
2016-05-19 08:00 | 1038 | 1032
2016-05-19 08:30 | 1029 | 1024
2016-05-19 09:00 | 997 | 992
2016-05-19 09:30 | 990 | 987
2016-05-19 10:00 | 983 | 982
2016-05-19 10:30 | 999 | 996
2016-05-19 11:00 | 1015 | 1013
2016-05-19 11:30 | 1012 | 1010
2016-05-19 12:00 | 1039 | 1038
2016-05-19 12:30 | 1046 | 1045
2016-05-19 13:00 | 1038 | 1036
2016-05-19 13:30 | 1012 | 1010
2016-05-19 14:00 | 1029 | 1027
2016-05-19 14:30 | 1053 | 1051
2016-05-19 15:00 | 1062 | 1060
2016-05-19 15:30 | 1071 | 1068
2016-05-19 16:00 | 1084 | 1081
2016-05-19 16:30 | 1093 | 1089
2016-05-19 17:00 | 1131 | 1128
2016-05-19 17:30 | 1178 | 1177
2016-05-19 18:00 | 1216 | 1211
2016-05-19 18:30 | 1192 | 1181
2016-05-19 19:00 | 1175 | 1163
2016-05-19 19:30 | 1149 | 1131
2016-05-19 20:00 | 1123 | 1109
2016-05-19 20:30 | 1117 | 1106
2016-05-19 21:00 | 1062 | 1050
2016-05-19 21:30 | 996 | 981
2016-05-19 22:00 | 949 | 938
2016-05-19 22:30 | 920 | 910
2016-05-19 23:00 | 896 | 882
2016-05-19 23:30 | 856 | 845
2016-05-20 | 805 | 792
2016-05-20 00:30 | 749 | 730
2016-05-20 01:00 | 716 | 695
2016-05-20 01:30 | 690 | 669
2016-05-20 02:00 | 677 | 653
2016-05-20 02:30 | 662 | 636
2016-05-20 03:00 | 643 | 616
2016-05-20 03:30 | 632 | 603
2016-05-20 04:00 | 629 | 600
2016-05-20 04:30 | 648 | 623
2016-05-20 05:00 | 663 | 642
2016-05-20 05:30 | 737 | 724
2016-05-20 06:00 | 786 | 775
2016-05-20 06:30 | 881 | 872
2016-05-20 07:00 | 994 | 970
2016-05-20 07:30 | 1050 | 1028
2016-05-20 08:00 | 1052 | 1030
2016-05-20 08:30 | 1027 | 1007
2016-05-20 09:00 | 998 | 979
2016-05-20 09:30 | 979 | 960
2016-05-20 10:00 | 966 | 949
2016-05-20 10:30 | 957 | 942
2016-05-20 11:00 | 954 | 940
2016-05-20 11:30 | 935 | 921
2016-05-20 12:00 | 936 | 923
2016-05-20 12:30 | 932 | 920
2016-05-20 13:00 | 931 | 918
2016-05-20 13:30 | 937 | 924
2016-05-20 14:00 | 960 | 948
2016-05-20 14:30 | 975 | 964
2016-05-20 15:00 | 995 | 984
2016-05-20 15:30 | 1021 | 1010
2016-05-20 16:00 | 1055 | 1045
2016-05-20 16:30 | 1091 | 1076
2016-05-20 17:00 | 1118 | 1096
2016-05-20 17:30 | 1145 | 1121
2016-05-20 18:00 | 1170 | 1146
2016-05-20 18:30 | 1141 | 1109
2016-05-20 19:00 | 1116 | 1079
2016-05-20 19:30 | 1074 | 1048
2016-05-20 20:00 | 1055 | 1040
2016-05-20 20:30 | 1049 | 1036
2016-05-20 21:00 | 1017 | 1012
2016-05-20 21:30 | 974 | 967
2016-05-20 22:00 | 932 | 923
2016-05-20 22:30 | 911 | 904
2016-05-20 23:00 | 899 | 892
2016-05-20 23:30 | 854 | 850
2016-05-21 | 804 | 796
2016-05-21 00:30 | 757 | 745
2016-05-21 01:00 | 721 | 706
2016-05-21 01:30 | 692 | 673
2016-05-21 02:00 | 662 | 639
2016-05-21 02:30 | 650 | 625
2016-05-21 03:00 | 644 | 617
2016-05-21 03:30 | 638 | 610
2016-05-21 04:00 | 622 | 592
2016-05-21 04:30 | 627 | 598
2016-05-21 05:00 | 634 | 608
2016-05-21 05:30 | 653 | 631
2016-05-21 06:00 | 665 | 647
2016-05-21 06:30 | 702 | 688
2016-05-21 07:00 | 736 | 722
2016-05-21 07:30 | 789 | 781
2016-05-21 08:00 | 811 | 806
2016-05-21 08:30 | 839 | 835
2016-05-21 09:00 | 858 | 854
2016-05-21 09:30 | 857 | 854
2016-05-21 10:00 | 849 | 847
2016-05-21 10:30 | 836 | 835
2016-05-21 11:00 | 829 | 828
2016-05-21 11:30 | 820 | 818
2016-05-21 12:00 | 808 | 806
2016-05-21 12:30 | 803 | 797
2016-05-21 13:00 | 807 | 801
2016-05-21 13:30 | 807 | 800
2016-05-21 14:00 | 822 | 816
2016-05-21 14:30 | 841 | 834
2016-05-21 15:00 | 857 | 852
2016-05-21 15:30 | 879 | 874
2016-05-21 16:00 | 903 | 899
2016-05-21 16:30 | 944 | 941
2016-05-21 17:00 | 1001 | 999
2016-05-21 17:30 | 1055 | 1044
2016-05-21 18:00 | 1061 | 1050
2016-05-21 18:30 | 1041 | 1027
2016-05-21 19:00 | 1027 | 1010
2016-05-21 19:30 | 983 | 970
2016-05-21 20:00 | 965 | 956
2016-05-21 20:30 | 962 | 955
2016-05-21 21:00 | 910 | 907
2016-05-21 21:30 | 882 | 877
2016-05-21 22:00 | 859 | 852
2016-05-21 22:30 | 849 | 840
2016-05-21 23:00 | 846 | 836
2016-05-21 23:30 | 828 | 816
2016-05-22 | 796 | 778
2016-05-22 00:30 | 739 | 719
2016-05-22 01:00 | 704 | 687
2016-05-22 01:30 | 666 | 644
2016-05-22 02:00 | 655 | 632
2016-05-22 02:30 | 629 | 602
2016-05-22 03:00 | 617 | 587
2016-05-22 03:30 | 599 | 570
2016-05-22 04:00 | 608 | 580
2016-05-22 04:30 | 623 | 595
2016-05-22 05:00 | 628 | 602
2016-05-22 05:30 | 634 | 610
2016-05-22 06:00 | 643 | 621
2016-05-22 06:30 | 669 | 651
2016-05-22 07:00 | 686 | 667
2016-05-22 07:30 | 722 | 707
2016-05-22 08:00 | 766 | 756
2016-05-22 08:30 | 796 | 790
2016-05-22 09:00 | 805 | 801
2016-05-22 09:30 | 800 | 797
2016-05-22 10:00 | 810 | 809
2016-05-22 10:30 | 816 | 816
2016-05-22 11:00 | 826 | 826
2016-05-22 11:30 | 818 | 817
2016-05-22 12:00 | 800 | 798
2016-05-22 12:30 | 779 | 776
2016-05-22 13:00 | 773 | 770
2016-05-22 13:30 | 769 | 766
2016-05-22 14:00 | 786 | 783
2016-05-22 14:30 | 795 | 792
2016-05-22 15:00 | 813 | 810
2016-05-22 15:30 | 841 | 839
2016-05-22 16:00 | 879 | 876
2016-05-22 16:30 | 887 | 883
2016-05-22 17:00 | 955 | 949
2016-05-22 17:30 | 1039 | 1034
2016-05-22 18:00 | 1081 | 1073
2016-05-22 18:30 | 1071 | 1054
2016-05-22 19:00 | 1065 | 1045
2016-05-22 19:30 | 1030 | 1011
2016-05-22 20:00 | 1014 | 997
2016-05-22 20:30 | 1005 | 993
2016-05-22 21:00 | 948 | 937
2016-05-22 21:30 | 905 | 891
2016-05-22 22:00 | 873 | 862
2016-05-22 22:30 | 838 | 834
2016-05-22 23:00 | 833 | 830
2016-05-22 23:30 | 806 | 801
2016-05-23 | 772 | 764
2016-05-23 00:30 | 703 | 689
2016-05-23 01:00 | 670 | 654
2016-05-23 01:30 | 599 | 577
2016-05-23 02:00 | 602 | 577
2016-05-23 02:30 | 591 | 565
2016-05-23 03:00 | 558 | 530
2016-05-23 03:30 | 584 | 557
2016-05-23 04:00 | 560 | 533
2016-05-23 04:30 | 574 | 549
2016-05-23 05:00 | 598 | 578
2016-05-23 05:30 | 652 | 639
2016-05-23 06:00 | 732 | 719
2016-05-23 06:30 | 890 | 881
2016-05-23 07:00 | 988 | 973
2016-05-23 07:30 | 1074 | 1057
2016-05-23 08:00 | 1089 | 1072
2016-05-23 08:30 | 1060 | 1043
2016-05-23 09:00 | 1038 | 1022
2016-05-23 09:30 | 1014 | 999
2016-05-23 10:00 | 991 | 977
2016-05-23 10:30 | 980 | 968
2016-05-23 11:00 | 978 | 968
2016-05-23 11:30 | 968 | 958
2016-05-23 12:00 | 968 | 959
2016-05-23 12:30 | 976 | 968
2016-05-23 13:00 | 994 | 987
2016-05-23 13:30 | 1012 | 1007
2016-05-23 14:00 | 1032 | 1029
2016-05-23 14:30 | 1064 | 1058
2016-05-23 15:00 | 1090 | 1075
2016-05-23 15:30 | 1112 | 1091
2016-05-23 16:00 | 1139 | 1118
2016-05-23 16:30 | 1163 | 1143
2016-05-23 17:00 | 1197 | 1179
2016-05-23 17:30 | 1236 | 1224
2016-05-23 18:00 | 1262 | 1250
2016-05-23 18:30 | 1228 | 1209
2016-05-23 19:00 | 1204 | 1181
2016-05-23 19:30 | 1151 | 1141
2016-05-23 20:00 | 1136 | 1125
2016-05-23 20:30 | 1116 | 1102
2016-05-23 21:00 | 1057 | 1046
2016-05-23 21:30 | 989 | 980
2016-05-23 22:00 | 935 | 930
2016-05-23 22:30 | 919 | 911
2016-05-23 23:00 | 891 | 881
2016-05-23 23:30 | 849 | 842
2016-05-24 | 797 | 786
2016-05-24 00:30 | 738 | 728
2016-05-24 01:00 | 706 | 691
2016-05-24 01:30 | 683 | 664
2016-05-24 02:00 | 668 | 648
2016-05-24 02:30 | 661 | 639
2016-05-24 03:00 | 654 | 630
2016-05-24 03:30 | 651 | 628
2016-05-24 04:00 | 653 | 629
2016-05-24 04:30 | 662 | 641
2016-05-24 05:00 | 680 | 662
2016-05-24 05:30 | 732 | 721
2016-05-24 06:00 | 791 | 777
2016-05-24 06:30 | 900 | 885
2016-05-24 07:00 | 1003 | 987
2016-05-24 07:30 | 1065 | 1054
2016-05-24 08:00 | 1070 | 1057
2016-05-24 08:30 | 1056 | 1043
2016-05-24 09:00 | 1028 | 1016
2016-05-24 09:30 | 1009 | 997
2016-05-24 10:00 | 993 | 982
2016-05-24 10:30 | 981 | 971
2016-05-24 11:00 | 973 | 964
2016-05-24 11:30 | 959 | 950
2016-05-24 12:00 | 956 | 946
2016-05-24 12:30 | 949 | 939
2016-05-24 13:00 | 954 | 944
2016-05-24 13:30 | 965 | 956
2016-05-24 14:00 | 982 | 974
2016-05-24 14:30 | 995 | 987
2016-05-24 15:00 | 1017 | 1009
2016-05-24 15:30 | 1037 | 1028
2016-05-24 16:00 | 1075 | 1067
2016-05-24 16:30 | 1113 | 1105
2016-05-24 17:00 | 1158 | 1145
2016-05-24 17:30 | 1194 | 1186
2016-05-24 18:00 | 1230 | 1217
2016-05-24 18:30 | 1207 | 1182
2016-05-24 19:00 | 1203 | 1176
2016-05-24 19:30 | 1155 | 1133
2016-05-24 20:00 | 1133 | 1121
2016-05-24 20:30 | 1121 | 1108
2016-05-24 21:00 | 1065 | 1051
2016-05-24 21:30 | 1008 | 994
2016-05-24 22:00 | 954 | 937
2016-05-24 22:30 | 906 | 899
2016-05-24 23:00 | 873 | 871
2016-05-24 23:30 | 842 | 838
2016-05-25 | 806 | 800
2016-05-25 00:30 | 757 | 746
2016-05-25 01:00 | 724 | 708
2016-05-25 01:30 | 697 | 679
2016-05-25 02:00 | 674 | 652
2016-05-25 02:30 | 652 | 628
2016-05-25 03:00 | 648 | 623
2016-05-25 03:30 | 652 | 627
2016-05-25 04:00 | 619 | 593
2016-05-25 04:30 | 609 | 585
2016-05-25 05:00 | 700 | 682
2016-05-25 05:30 | 756 | 746
2016-05-25 06:00 | 811 | 802
2016-05-25 06:30 | 929 | 917
2016-05-25 07:00 | 1023 | 1016
2016-05-25 07:30 | 1078 | 1071
2016-05-25 08:00 | 1087 | 1070
2016-05-25 08:30 | 1049 | 1030
2016-05-25 09:00 | 1118 | 1092
2016-05-25 09:30 | 1184 | 1153
2016-05-25 10:00 | 1148 | 1114
2016-05-25 10:30 | 1134 | 1107
2016-05-25 11:00 | 1125 | 1107
2016-05-25 11:30 | 1110 | 1092
2016-05-25 12:00 | 1104 | 1087
2016-05-25 12:30 | 923 | 912
2016-05-25 13:00 | 921 | 912
2016-05-25 13:30 | 936 | 929
2016-05-25 14:00 | 950 | 943
2016-05-25 14:30 | 976 | 971
2016-05-25 15:00 | 1004 | 995
2016-05-25 15:30 | 1056 | 1038
2016-05-25 16:00 | 1093 | 1075
2016-05-25 16:30 | 1127 | 1111
2016-05-25 17:00 | 1168 | 1153
2016-05-25 17:30 | 1225 | 1213
2016-05-25 18:00 | 1260 | 1241
2016-05-25 18:30 | 1242 | 1216
2016-05-25 19:00 | 1238 | 1212
2016-05-25 19:30 | 1181 | 1159
2016-05-25 20:00 | 1162 | 1146
2016-05-25 20:30 | 1141 | 1124
2016-05-25 21:00 | 1077 | 1068
2016-05-25 21:30 | 1028 | 1020
2016-05-25 22:00 | 979 | 966
2016-05-25 22:30 | 948 | 935
2016-05-25 23:00 | 918 | 905
2016-05-25 23:30 | 876 | 867
2016-05-26 | 822 | 816
2016-05-26 00:30 | 783 | 773
2016-05-26 01:00 | 742 | 728
2016-05-26 01:30 | 712 | 695
2016-05-26 02:00 | 692 | 672
2016-05-26 02:30 | 675 | 653
2016-05-26 03:00 | 668 | 645
2016-05-26 03:30 | 660 | 636
2016-05-26 04:00 | 660 | 637
2016-05-26 04:30 | 680 | 660
2016-05-26 05:00 | 700 | 683
2016-05-26 05:30 | 762 | 753
2016-05-26 06:00 | 827 | 812
2016-05-26 06:30 | 934 | 919
2016-05-26 07:00 | 1029 | 1018
2016-05-26 07:30 | 1109 | 1105
2016-05-26 08:00 | 1128 | 1111
2016-05-26 08:30 | 1099 | 1078
2016-05-26 09:00 | 1068 | 1046
2016-05-26 09:30 | 1039 | 1014
2016-05-26 10:00 | 1023 | 999
2016-05-26 10:30 | 1014 | 992
2016-05-26 11:00 | 1055 | 1042
2016-05-26 11:30 | 1033 | 1019
2016-05-26 12:00 | 981 | 963
2016-05-26 12:30 | 968 | 949
2016-05-26 13:00 | 964 | 947
2016-05-26 13:30 | 985 | 971
2016-05-26 14:00 | 1013 | 1001
2016-05-26 14:30 | 1038 | 1029
2016-05-26 15:00 | 1051 | 1043
2016-05-26 15:30 | 1083 | 1076
2016-05-26 16:00 | 1110 | 1102
2016-05-26 16:30 | 1148 | 1139
2016-05-26 17:00 | 1187 | 1175
2016-05-26 17:30 | 1246 | 1239
2016-05-26 18:00 | 1291 | 1271
2016-05-26 18:30 | 1261 | 1238
2016-05-26 19:00 | 1252 | 1231
2016-05-26 19:30 | 1219 | 1202
2016-05-26 20:00 | 1202 | 1188
2016-05-26 20:30 | 1163 | 1153
2016-05-26 21:00 | 1109 | 1099
2016-05-26 21:30 | 1052 | 1034
2016-05-26 22:00 | 988 | 973
2016-05-26 22:30 | 950 | 947
2016-05-26 23:00 | 928 | 924
2016-05-26 23:30 | 896 | 892
2016-05-27 | 847 | 841
2016-05-27 00:30 | 792 | 781
2016-05-27 01:00 | 761 | 747
2016-05-27 01:30 | 722 | 712
2016-05-27 02:00 | 690 | 675
2016-05-27 02:30 | 680 | 661
2016-05-27 03:00 | 668 | 649
2016-05-27 03:30 | 662 | 642
2016-05-27 04:00 | 666 | 646
2016-05-27 04:30 | 680 | 662
2016-05-27 05:00 | 702 | 688
2016-05-27 05:30 | 745 | 737
2016-05-27 06:00 | 812 | 792
2016-05-27 06:30 | 912 | 895
2016-05-27 07:00 | 1015 | 996
2016-05-27 07:30 | 1084 | 1071
2016-05-27 08:00 | 1095 | 1081
2016-05-27 08:30 | 1072 | 1061
2016-05-27 09:00 | 1053 | 1045
2016-05-27 09:30 | 1061 | 1041
2016-05-27 10:00 | 1045 | 1033
2016-05-27 10:30 | 1002 | 996
2016-05-27 11:00 | 989 | 971
2016-05-27 11:30 | 973 | 946
2016-05-27 12:00 | 978 | 952
2016-05-27 12:30 | 979 | 953
2016-05-27 13:00 | 989 | 964
2016-05-27 13:30 | 996 | 970
2016-05-27 14:00 | 1006 | 980
2016-05-27 14:30 | 1014 | 988
2016-05-27 15:00 | 1019 | 993
2016-05-27 15:30 | 1042 | 1014
2016-05-27 16:00 | 1083 | 1057
2016-05-27 16:30 | 1110 | 1086
2016-05-27 17:00 | 1147 | 1125
2016-05-27 17:30 | 1196 | 1179
2016-05-27 18:00 | 1207 | 1191
2016-05-27 18:30 | 1175 | 1152
2016-05-27 19:00 | 1002 | 979
2016-05-27 19:30 | 934 | 919
2016-05-27 20:00 | 923 | 910
2016-05-27 20:30 | 908 | 893
2016-05-27 21:00 | 855 | 847
2016-05-27 21:30 | 825 | 819
2016-05-27 22:00 | 801 | 792
2016-05-27 22:30 | 786 | 775
2016-05-27 23:00 | 772 | 764
2016-05-27 23:30 | 735 | 730
2016-05-28 | 691 | 686
2016-05-28 00:30 | 651 | 644
2016-05-28 01:00 | 627 | 617
2016-05-28 01:30 | 612 | 598
2016-05-28 02:00 | 593 | 577
2016-05-28 02:30 | 584 | 566
2016-05-28 03:00 | 578 | 560
2016-05-28 03:30 | 581 | 562
2016-05-28 04:00 | 583 | 562
2016-05-28 04:30 | 583 | 562
2016-05-28 05:00 | 589 | 568
2016-05-28 05:30 | 598 | 580
2016-05-28 06:00 | 618 | 605
2016-05-28 06:30 | 647 | 638
2016-05-28 07:00 | 674 | 666
2016-05-28 07:30 | 698 | 692
2016-05-28 08:00 | 714 | 708
2016-05-28 08:30 | 726 | 723
2016-05-28 09:00 | 730 | 727
2016-05-28 09:30 | 718 | 716
2016-05-28 10:00 | 700 | 698
2016-05-28 10:30 | 700 | 699
2016-05-28 11:00 | 692 | 691
2016-05-28 11:30 | 711 | 707
2016-05-28 12:00 | 666 | 660
2016-05-28 12:30 | 667 | 660
2016-05-28 13:00 | 650 | 640
2016-05-28 13:30 | 673 | 664
2016-05-28 14:00 | 680 | 672
2016-05-28 14:30 | 677 | 671
2016-05-28 15:00 | 696 | 692
2016-05-28 15:30 | 716 | 713
2016-05-28 16:00 | 743 | 740
2016-05-28 16:30 | 787 | 785
2016-05-28 17:00 | 832 | 830
2016-05-28 17:30 | 867 | 863
2016-05-28 18:00 | 884 | 878
2016-05-28 18:30 | 867 | 860
2016-05-28 19:00 | 856 | 848
2016-05-28 19:30 | 848 | 835
2016-05-28 20:00 | 839 | 824
2016-05-28 20:30 | 833 | 817
2016-05-28 21:00 | 807 | 794
2016-05-28 21:30 | 780 | 770
2016-05-28 22:00 | 761 | 751
2016-05-28 22:30 | 741 | 733
2016-05-28 23:00 | 739 | 730
2016-05-28 23:30 | 708 | 703
2016-05-29 | 681 | 674
2016-05-29 00:30 | 636 | 626
2016-05-29 01:00 | 600 | 587
2016-05-29 01:30 | 578 | 562
2016-05-29 02:00 | 565 | 547
2016-05-29 02:30 | 567 | 547
2016-05-29 03:00 | 570 | 549
2016-05-29 03:30 | 565 | 544
2016-05-29 04:00 | 567 | 546
2016-05-29 04:30 | 567 | 546
2016-05-29 05:00 | 573 | 552
2016-05-29 05:30 | 583 | 564
2016-05-29 06:00 | 589 | 571
2016-05-29 06:30 | 604 | 588
2016-05-29 07:00 | 614 | 597
2016-05-29 07:30 | 646 | 633
2016-05-29 08:00 | 679 | 667
2016-05-29 08:30 | 695 | 687
2016-05-29 09:00 | 736 | 732
2016-05-29 09:30 | 699 | 695
2016-05-29 10:00 | 693 | 690
2016-05-29 10:30 | 631 | 625
2016-05-29 11:00 | 552 | 541
2016-05-29 11:30 | 530 | 518
2016-05-29 12:00 | 522 | 511
2016-05-29 12:30 | 520 | 513
2016-05-29 13:00 | 547 | 541
2016-05-29 13:30 | 580 | 575
2016-05-29 14:00 | 627 | 624
2016-05-29 14:30 | 639 | 637
2016-05-29 15:00 | 661 | 659
2016-05-29 15:30 | 689 | 688
2016-05-29 16:00 | 726 | 725
2016-05-29 16:30 | 774 | 774
2016-05-29 17:00 | 831 | 831
2016-05-29 17:30 | 896 | 893
2016-05-29 18:00 | 924 | 919
2016-05-29 18:30 | 915 | 909
2016-05-29 19:00 | 912 | 905
2016-05-29 19:30 | 897 | 888
2016-05-29 20:00 | 888 | 878
2016-05-29 20:30 | 883 | 874
2016-05-29 21:00 | 846 | 836
2016-05-29 21:30 | 833 | 820
2016-05-29 22:00 | 799 | 790
2016-05-29 22:30 | 774 | 767
2016-05-29 23:00 | 761 | 753
2016-05-29 23:30 | 717 | 711
2016-05-30 | 674 | 666
2016-05-30 00:30 | 644 | 634
2016-05-30 01:00 | 615 | 601
2016-05-30 01:30 | 594 | 579
2016-05-30 02:00 | 582 | 564
2016-05-30 02:30 | 577 | 556
2016-05-30 03:00 | 575 | 552
2016-05-30 03:30 | 576 | 552
2016-05-30 04:00 | 581 | 558
2016-05-30 04:30 | 593 | 572
2016-05-30 05:00 | 609 | 593
2016-05-30 05:30 | 638 | 630
2016-05-30 06:00 | 693 | 689
2016-05-30 06:30 | 806 | 803
2016-05-30 07:00 | 912 | 904
2016-05-30 07:30 | 984 | 971
2016-05-30 08:00 | 994 | 980
2016-05-30 08:30 | 956 | 943
2016-05-30 09:00 | 907 | 893
2016-05-30 09:30 | 909 | 896
2016-05-30 10:00 | 865 | 851
2016-05-30 10:30 | 831 | 821
2016-05-30 11:00 | 805 | 800
2016-05-30 11:30 | 781 | 777
2016-05-30 12:00 | 768 | 766
2016-05-30 12:30 | 773 | 771
2016-05-30 13:00 | 780 | 778
2016-05-30 13:30 | 783 | 782
2016-05-30 14:00 | 799 | 798
2016-05-30 14:30 | 808 | 807
2016-05-30 15:00 | 831 | 830
2016-05-30 15:30 | 851 | 848
2016-05-30 16:00 | 896 | 892
2016-05-30 16:30 | 962 | 952
2016-05-30 17:00 | 1017 | 1004
2016-05-30 17:30 | 1070 | 1062
2016-05-30 18:00 | 1092 | 1084
2016-05-30 18:30 | 1076 | 1064
2016-05-30 19:00 | 1067 | 1054
2016-05-30 19:30 | 1035 | 1026
2016-05-30 20:00 | 1022 | 1012
2016-05-30 20:30 | 1003 | 994
2016-05-30 21:00 | 951 | 945
2016-05-30 21:30 | 898 | 889
2016-05-30 22:00 | 841 | 839
2016-05-30 22:30 | 818 | 816
2016-05-30 23:00 | 798 | 795
2016-05-30 23:30 | 758 | 754
2016-05-31 | 707 | 704
2016-05-31 00:30 | 658 | 654
2016-05-31 01:00 | 648 | 643
2016-05-31 01:30 | 606 | 597
2016-05-31 02:00 | 603 | 594
2016-05-31 02:30 | 572 | 556
2016-05-31 03:00 | 573 | 557
2016-05-31 03:30 | 582 | 564
2016-05-31 04:00 | 589 | 571
2016-05-31 04:30 | 596 | 580
2016-05-31 05:00 | 607 | 595
2016-05-31 05:30 | 639 | 634
2016-05-31 06:00 | 688 | 686
2016-05-31 06:30 | 800 | 797
2016-05-31 07:00 | 951 | 946
2016-05-31 07:30 | 999 | 984
2016-05-31 08:00 | 1010 | 996
2016-05-31 08:30 | 995 | 979
2016-05-31 09:00 | 968 | 952
2016-05-31 09:30 | 939 | 925
2016-05-31 10:00 | 879 | 867
2016-05-31 10:30 | 865 | 859
2016-05-31 11:00 | 876 | 872
2016-05-31 11:30 | 813 | 807
2016-05-31 12:00 | 800 | 796
2016-05-31 12:30 | 875 | 875
2016-05-31 13:00 | 851 | 850
2016-05-31 13:30 | 877 | 875
2016-05-31 14:00 | 881 | 880
2016-05-31 14:30 | 945 | 944
2016-05-31 15:00 | 953 | 951
2016-05-31 15:30 | 908 | 902
2016-05-31 16:00 | 938 | 934
2016-05-31 16:30 | 973 | 969
2016-05-31 17:00 | 1022 | 1015
2016-05-31 17:30 | 1059 | 1052
2016-05-31 18:00 | 1075 | 1063
2016-05-31 18:30 | 1052 | 1034
2016-05-31 19:00 | 1042 | 1028
2016-05-31 19:30 | 1000 | 992
2016-05-31 20:00 | 975 | 973
2016-05-31 20:30 | 973 | 968
2016-05-31 21:00 | 922 | 916
2016-05-31 21:30 | 866 | 864
2016-05-31 22:00 | 819 | 817
2016-05-31 22:30 | 794 | 792
2016-05-31 23:00 | 782 | 777
2016-05-31 23:30 | 748 | 741
2016-06-01 | 723 | 719
2016-06-01 00:30 | 661 | 652
2016-06-01 01:00 | 657 | 649
2016-06-01 01:30 | 620 | 607
2016-06-01 02:00 | 580 | 561
2016-06-01 02:30 | 577 | 553
2016-06-01 03:00 | 577 | 553
2016-06-01 03:30 | 577 | 553
2016-06-01 04:00 | 580 | 556
2016-06-01 04:30 | 590 | 569
2016-06-01 05:00 | 610 | 593
2016-06-01 05:30 | 650 | 640
2016-06-01 06:00 | 683 | 678
2016-06-01 06:30 | 778 | 778
2016-06-01 07:00 | 887 | 886
2016-06-01 07:30 | 960 | 949
2016-06-01 08:00 | 976 | 966
2016-06-01 08:30 | 960 | 959
2016-06-01 09:00 | 936 | 935
2016-06-01 09:30 | 934 | 929
2016-06-01 10:00 | 861 | 859
2016-06-01 10:30 | 780 | 780
2016-06-01 11:00 | 764 | 763
2016-06-01 11:30 | 752 | 748
2016-06-01 12:00 | 752 | 746
2016-06-01 12:30 | 755 | 755
2016-06-01 13:00 | 762 | 755
2016-06-01 13:30 | 762 | 756
2016-06-01 14:00 | 779 | 775
2016-06-01 14:30 | 789 | 786
2016-06-01 15:00 | 775 | 771
2016-06-01 15:30 | 874 | 869
2016-06-01 16:00 | 956 | 952
2016-06-01 16:30 | 959 | 955
2016-06-01 17:00 | 1001 | 998
2016-06-01 17:30 | 1040 | 1038
2016-06-01 18:00 | 1065 | 1061
2016-06-01 18:30 | 1052 | 1048
2016-06-01 19:00 | 1024 | 1017
2016-06-01 19:30 | 1000 | 995
2016-06-01 20:00 | 1001 | 1001
2016-06-01 20:30 | 977 | 976
2016-06-01 21:00 | 964 | 964
2016-06-01 21:30 | 909 | 906
2016-06-01 22:00 | 830 | 827
2016-06-01 22:30 | 845 | 844
2016-06-01 23:00 | 794 | 789
2016-06-01 23:30 | 751 | 745
2016-06-02 | 701 | 698
2016-06-02 00:30 | 659 | 653
2016-06-02 01:00 | 616 | 607
2016-06-02 01:30 | 590 | 578
2016-06-02 02:00 | 602 | 591
2016-06-02 02:30 | 588 | 576
2016-06-02 03:00 | 570 | 556
2016-06-02 03:30 | 573 | 556
2016-06-02 04:00 | 579 | 561
2016-06-02 04:30 | 589 | 573
2016-06-02 05:00 | 598 | 587
2016-06-02 05:30 | 633 | 628
2016-06-02 06:00 | 696 | 693
2016-06-02 06:30 | 828 | 827
2016-06-02 07:00 | 873 | 869
2016-06-02 07:30 | 942 | 940
2016-06-02 08:00 | 964 | 962
2016-06-02 08:30 | 945 | 943
2016-06-02 09:00 | 921 | 919
2016-06-02 09:30 | 911 | 910
2016-06-02 10:00 | 785 | 784
2016-06-02 10:30 | 754 | 753
2016-06-02 11:00 | 754 | 754
2016-06-02 11:30 | 749 | 749
2016-06-02 12:00 | 757 | 756
2016-06-02 12:30 | 765 | 763
2016-06-02 13:00 | 772 | 769
2016-06-02 13:30 | 766 | 762
2016-06-02 14:00 | 773 | 768
2016-06-02 14:30 | 767 | 761
2016-06-02 15:00 | 902 | 895
2016-06-02 15:30 | 942 | 936
2016-06-02 16:00 | 953 | 946
2016-06-02 16:30 | 980 | 974
2016-06-02 17:00 | 1017 | 1013
2016-06-02 17:30 | 1057 | 1053
2016-06-02 18:00 | 1086 | 1078
2016-06-02 18:30 | 1068 | 1057
2016-06-02 19:00 | 1070 | 1057
2016-06-02 19:30 | 1031 | 1024
2016-06-02 20:00 | 1019 | 1011
2016-06-02 20:30 | 1033 | 1031
2016-06-02 21:00 | 996 | 993
2016-06-02 21:30 | 910 | 903
2016-06-02 22:00 | 848 | 845
2016-06-02 22:30 | 826 | 823
2016-06-02 23:00 | 800 | 799
2016-06-02 23:30 | 763 | 759
2016-06-03 | 714 | 709
2016-06-03 00:30 | 660 | 653
2016-06-03 01:00 | 641 | 630
2016-06-03 01:30 | 618 | 603
2016-06-03 02:00 | 596 | 576
2016-06-03 02:30 | 597 | 575
2016-06-03 03:00 | 599 | 574
2016-06-03 03:30 | 600 | 574
2016-06-03 04:00 | 602 | 578
2016-06-03 04:30 | 612 | 591
2016-06-03 05:00 | 626 | 609
2016-06-03 05:30 | 665 | 655
2016-06-03 06:00 | 726 | 716
2016-06-03 06:30 | 828 | 817
2016-06-03 07:00 | 896 | 884
2016-06-03 07:30 | 964 | 954
2016-06-03 08:00 | 999 | 984
2016-06-03 08:30 | 989 | 976
2016-06-03 09:00 | 962 | 948
2016-06-03 09:30 | 938 | 923
2016-06-03 10:00 | 925 | 909
2016-06-03 10:30 | 934 | 920
2016-06-03 11:00 | 952 | 939
2016-06-03 11:30 | 951 | 937
2016-06-03 12:00 | 959 | 947
2016-06-03 12:30 | 957 | 943
2016-06-03 13:00 | 951 | 936
2016-06-03 13:30 | 943 | 927
2016-06-03 14:00 | 942 | 927
2016-06-03 14:30 | 938 | 920
2016-06-03 15:00 | 931 | 913
2016-06-03 15:30 | 928 | 907
2016-06-03 16:00 | 962 | 944
2016-06-03 16:30 | 989 | 975
2016-06-03 17:00 | 1005 | 996
2016-06-03 17:30 | 1030 | 1026
2016-06-03 18:00 | 1046 | 1031
2016-06-03 18:30 | 1024 | 1004
2016-06-03 19:00 | 1009 | 990
2016-06-03 19:30 | 962 | 950
2016-06-03 20:00 | 943 | 938
2016-06-03 20:30 | 932 | 929
2016-06-03 21:00 | 897 | 895
2016-06-03 21:30 | 863 | 863
2016-06-03 22:00 | 833 | 832
2016-06-03 22:30 | 821 | 821
2016-06-03 23:00 | 805 | 803
2016-06-03 23:30 | 771 | 767
2016-06-04 | 726 | 721
2016-06-04 00:30 | 681 | 675
2016-06-04 01:00 | 649 | 642
2016-06-04 01:30 | 616 | 606
2016-06-04 02:00 | 597 | 583
2016-06-04 02:30 | 594 | 579
2016-06-04 03:00 | 589 | 570
2016-06-04 03:30 | 593 | 574
2016-06-04 04:00 | 593 | 573
2016-06-04 04:30 | 592 | 573
2016-06-04 05:00 | 599 | 583
2016-06-04 05:30 | 606 | 593
2016-06-04 06:00 | 625 | 615
2016-06-04 06:30 | 655 | 649
2016-06-04 07:00 | 691 | 687
2016-06-04 07:30 | 734 | 732
2016-06-04 08:00 | 781 | 780
2016-06-04 08:30 | 835 | 835
2016-06-04 09:00 | 886 | 885
2016-06-04 09:30 | 933 | 932
2016-06-04 10:00 | 955 | 955
2016-06-04 10:30 | 958 | 958
2016-06-04 11:00 | 968 | 967
2016-06-04 11:30 | 960 | 958
2016-06-04 12:00 | 959 | 957
2016-06-04 12:30 | 940 | 936
2016-06-04 13:00 | 919 | 915
2016-06-04 13:30 | 905 | 900
2016-06-04 14:00 | 892 | 885
2016-06-04 14:30 | 882 | 873
2016-06-04 15:00 | 876 | 867
2016-06-04 15:30 | 882 | 876
2016-06-04 16:00 | 902 | 899
2016-06-04 16:30 | 923 | 921
2016-06-04 17:00 | 954 | 953
2016-06-04 17:30 | 968 | 968
2016-06-04 18:00 | 968 | 964
2016-06-04 18:30 | 946 | 939
2016-06-04 19:00 | 939 | 930
2016-06-04 19:30 | 905 | 893
2016-06-04 20:00 | 876 | 874
2016-06-04 20:30 | 869 | 867
2016-06-04 21:00 | 827 | 826
2016-06-04 21:30 | 804 | 803
2016-06-04 22:00 | 781 | 779
2016-06-04 22:30 | 774 | 770
2016-06-04 23:00 | 769 | 765
2016-06-04 23:30 | 738 | 736
2016-06-05 | 698 | 694
2016-06-05 00:30 | 657 | 650
2016-06-05 01:00 | 628 | 618
2016-06-05 01:30 | 599 | 586
2016-06-05 02:00 | 563 | 544
2016-06-05 02:30 | 544 | 524
2016-06-05 03:00 | 538 | 516
2016-06-05 03:30 | 540 | 516
2016-06-05 04:00 | 536 | 511
2016-06-05 04:30 | 545 | 521
2016-06-05 05:00 | 547 | 523
2016-06-05 05:30 | 554 | 533
2016-06-05 06:00 | 582 | 563
2016-06-05 06:30 | 618 | 603
2016-06-05 07:00 | 637 | 621
2016-06-05 07:30 | 658 | 646
2016-06-05 08:00 | 679 | 671
2016-06-05 08:30 | 693 | 690
2016-06-05 09:00 | 707 | 705
2016-06-05 09:30 | 715 | 714
2016-06-05 10:00 | 714 | 713
2016-06-05 10:30 | 697 | 697
2016-06-05 11:00 | 679 | 679
2016-06-05 11:30 | 666 | 665
2016-06-05 12:00 | 659 | 658
2016-06-05 12:30 | 677 | 677
2016-06-05 13:00 | 646 | 645
2016-06-05 13:30 | 650 | 649
2016-06-05 14:00 | 669 | 668
2016-06-05 14:30 | 693 | 692
2016-06-05 15:00 | 717 | 716
2016-06-05 15:30 | 751 | 751
2016-06-05 16:00 | 777 | 776
2016-06-05 16:30 | 834 | 834
2016-06-05 17:00 | 897 | 897
2016-06-05 17:30 | 958 | 958
2016-06-05 18:00 | 990 | 987
2016-06-05 18:30 | 987 | 983
2016-06-05 19:00 | 976 | 972
2016-06-05 19:30 | 952 | 945
2016-06-05 20:00 | 927 | 922
2016-06-05 20:30 | 928 | 923
2016-06-05 21:00 | 873 | 870
2016-06-05 21:30 | 828 | 826
2016-06-05 22:00 | 799 | 795
2016-06-05 22:30 | 785 | 779
2016-06-05 23:00 | 760 | 757
2016-06-05 23:30 | 730 | 726
2016-06-06 | 691 | 683
2016-06-06 00:30 | 647 | 636
2016-06-06 01:00 | 623 | 608
2016-06-06 01:30 | 581 | 563
2016-06-06 02:00 | 562 | 541
2016-06-06 02:30 | 559 | 536
2016-06-06 03:00 | 550 | 525
2016-06-06 03:30 | 549 | 523
2016-06-06 04:00 | 551 | 526
2016-06-06 04:30 | 565 | 544
2016-06-06 05:00 | 590 | 574
2016-06-06 05:30 | 651 | 641
2016-06-06 06:00 | 694 | 688
2016-06-06 06:30 | 795 | 784
2016-06-06 07:00 | 878 | 872
2016-06-06 07:30 | 941 | 936
2016-06-06 08:00 | 955 | 950
2016-06-06 08:30 | 926 | 921
2016-06-06 09:00 | 928 | 923
2016-06-06 09:30 | 967 | 965
2016-06-06 10:00 | 943 | 940
2016-06-06 10:30 | 902 | 898
2016-06-06 11:00 | 910 | 907
2016-06-06 11:30 | 882 | 878
2016-06-06 12:00 | 852 | 847
2016-06-06 12:30 | 841 | 836
2016-06-06 13:00 | 857 | 852
2016-06-06 13:30 | 849 | 843
2016-06-06 14:00 | 859 | 852
2016-06-06 14:30 | 858 | 851
2016-06-06 15:00 | 859 | 851
2016-06-06 15:30 | 866 | 858
2016-06-06 16:00 | 883 | 876
2016-06-06 16:30 | 915 | 909
2016-06-06 17:00 | 983 | 981
2016-06-06 17:30 | 1067 | 1066
2016-06-06 18:00 | 1103 | 1100
2016-06-06 18:30 | 1090 | 1085
2016-06-06 19:00 | 1093 | 1086
2016-06-06 19:30 | 1056 | 1046
2016-06-06 20:00 | 1044 | 1037
2016-06-06 20:30 | 1048 | 1040
2016-06-06 21:00 | 989 | 984
2016-06-06 21:30 | 921 | 917
2016-06-06 22:00 | 881 | 873
2016-06-06 22:30 | 853 | 847
2016-06-06 23:00 | 828 | 825
2016-06-06 23:30 | 777 | 775
2016-06-07 | 722 | 717
2016-06-07 00:30 | 672 | 663
2016-06-07 01:00 | 645 | 632
2016-06-07 01:30 | 627 | 611
2016-06-07 02:00 | 606 | 588
2016-06-07 02:30 | 609 | 587
2016-06-07 03:00 | 601 | 579
2016-06-07 03:30 | 601 | 578
2016-06-07 04:00 | 602 | 581
2016-06-07 04:30 | 610 | 593
2016-06-07 05:00 | 631 | 618
2016-06-07 05:30 | 679 | 673
2016-06-07 06:00 | 743 | 735
2016-06-07 06:30 | 836 | 830
2016-06-07 07:00 | 939 | 932
2016-06-07 07:30 | 1002 | 994
2016-06-07 08:00 | 994 | 988
2016-06-07 08:30 | 958 | 951
2016-06-07 09:00 | 896 | 889
2016-06-07 09:30 | 845 | 839
2016-06-07 10:00 | 816 | 810
2016-06-07 10:30 | 793 | 785
2016-06-07 11:00 | 768 | 760
2016-06-07 11:30 | 747 | 737
2016-06-07 12:00 | 741 | 730
2016-06-07 12:30 | 740 | 732
2016-06-07 13:00 | 739 | 735
2016-06-07 13:30 | 744 | 740
2016-06-07 14:00 | 756 | 753
2016-06-07 14:30 | 767 | 765
2016-06-07 15:00 | 774 | 771
2016-06-07 15:30 | 800 | 798
2016-06-07 16:00 | 855 | 852
2016-06-07 16:30 | 915 | 911
2016-06-07 17:00 | 985 | 976
2016-06-07 17:30 | 1038 | 1032
2016-06-07 18:00 | 1076 | 1065
2016-06-07 18:30 | 1073 | 1059
2016-06-07 19:00 | 1078 | 1062
2016-06-07 19:30 | 1031 | 1024
2016-06-07 20:00 | 1014 | 1008
2016-06-07 20:30 | 1033 | 1027
2016-06-07 21:00 | 969 | 966
2016-06-07 21:30 | 919 | 915
2016-06-07 22:00 | 872 | 869
2016-06-07 22:30 | 838 | 838
2016-06-07 23:00 | 815 | 814
2016-06-07 23:30 | 782 | 779
2016-06-08 | 750 | 745
2016-06-08 00:30 | 681 | 672
2016-06-08 01:00 | 638 | 629
2016-06-08 01:30 | 606 | 594
2016-06-08 02:00 | 594 | 581
2016-06-08 02:30 | 589 | 572
2016-06-08 03:00 | 587 | 567
2016-06-08 03:30 | 592 | 571
2016-06-08 04:00 | 593 | 573
2016-06-08 04:30 | 603 | 586
2016-06-08 05:00 | 617 | 605
2016-06-08 05:30 | 658 | 651
2016-06-08 06:00 | 726 | 713
2016-06-08 06:30 | 832 | 817
2016-06-08 07:00 | 935 | 921
2016-06-08 07:30 | 990 | 979
2016-06-08 08:00 | 986 | 976
2016-06-08 08:30 | 945 | 934
2016-06-08 09:00 | 892 | 882
2016-06-08 09:30 | 853 | 841
2016-06-08 10:00 | 817 | 805
2016-06-08 10:30 | 804 | 790
2016-06-08 11:00 | 787 | 774
2016-06-08 11:30 | 770 | 757
2016-06-08 12:00 | 760 | 752
2016-06-08 12:30 | 758 | 750
2016-06-08 13:00 | 759 | 749
2016-06-08 13:30 | 768 | 761
2016-06-08 14:00 | 781 | 775
2016-06-08 14:30 | 795 | 789
2016-06-08 15:00 | 811 | 806
2016-06-08 15:30 | 836 | 831
2016-06-08 16:00 | 868 | 861
2016-06-08 16:30 | 907 | 898
2016-06-08 17:00 | 950 | 941
2016-06-08 17:30 | 1014 | 1002
2016-06-08 18:00 | 1041 | 1023
2016-06-08 18:30 | 1034 | 1012
2016-06-08 19:00 | 1031 | 1009
2016-06-08 19:30 | 996 | 987
2016-06-08 20:00 | 981 | 971
2016-06-08 20:30 | 970 | 961
2016-06-08 21:00 | 935 | 926
2016-06-08 21:30 | 888 | 876
2016-06-08 22:00 | 845 | 832
2016-06-08 22:30 | 815 | 803
2016-06-08 23:00 | 790 | 781
2016-06-08 23:30 | 754 | 748
2016-06-09 | 711 | 704
2016-06-09 00:30 | 675 | 664
2016-06-09 01:00 | 646 | 630
2016-06-09 01:30 | 614 | 599
2016-06-09 02:00 | 598 | 584
2016-06-09 02:30 | 596 | 581
2016-06-09 03:00 | 592 | 575
2016-06-09 03:30 | 591 | 575
2016-06-09 04:00 | 594 | 578
2016-06-09 04:30 | 608 | 594
2016-06-09 05:00 | 611 | 600
2016-06-09 05:30 | 642 | 636
2016-06-09 06:00 | 709 | 702
2016-06-09 06:30 | 805 | 799
2016-06-09 07:00 | 910 | 903
2016-06-09 07:30 | 962 | 954
2016-06-09 08:00 | 964 | 947
2016-06-09 08:30 | 928 | 913
2016-06-09 09:00 | 876 | 861
2016-06-09 09:30 | 848 | 834
2016-06-09 10:00 | 815 | 803
2016-06-09 10:30 | 805 | 794
2016-06-09 11:00 | 800 | 789
2016-06-09 11:30 | 788 | 777
2016-06-09 12:00 | 785 | 775
2016-06-09 12:30 | 791 | 781
2016-06-09 13:00 | 793 | 784
2016-06-09 13:30 | 802 | 795
2016-06-09 14:00 | 815 | 809
2016-06-09 14:30 | 829 | 822
2016-06-09 15:00 | 846 | 840
2016-06-09 15:30 | 868 | 860
2016-06-09 16:00 | 894 | 886
2016-06-09 16:30 | 922 | 914
2016-06-09 17:00 | 957 | 945
2016-06-09 17:30 | 990 | 983
2016-06-09 18:00 | 1024 | 1017
2016-06-09 18:30 | 1005 | 996
2016-06-09 19:00 | 1004 | 993
2016-06-09 19:30 | 975 | 960
2016-06-09 20:00 | 963 | 951
2016-06-09 20:30 | 954 | 943
2016-06-09 21:00 | 910 | 898
2016-06-09 21:30 | 872 | 858
2016-06-09 22:00 | 828 | 822
2016-06-09 22:30 | 809 | 799
2016-06-09 23:00 | 794 | 781
2016-06-09 23:30 | 752 | 742
2016-06-10 | 710 | 697
2016-06-10 00:30 | 668 | 649
2016-06-10 01:00 | 635 | 622
2016-06-10 01:30 | 619 | 603
2016-06-10 02:00 | 601 | 583
2016-06-10 02:30 | 591 | 571
2016-06-10 03:00 | 589 | 568
2016-06-10 03:30 | 586 | 565
2016-06-10 04:00 | 591 | 570
2016-06-10 04:30 | 582 | 563
2016-06-10 05:00 | 597 | 581
2016-06-10 05:30 | 635 | 626
2016-06-10 06:00 | 673 | 668
2016-06-10 06:30 | 756 | 753
2016-06-10 07:00 | 834 | 830
2016-06-10 07:30 | 904 | 899
2016-06-10 08:00 | 912 | 900
2016-06-10 08:30 | 889 | 880
2016-06-10 09:00 | 866 | 855
2016-06-10 09:30 | 838 | 827
2016-06-10 10:00 | 806 | 796
2016-06-10 10:30 | 790 | 778
2016-06-10 11:00 | 793 | 781
2016-06-10 11:30 | 801 | 790
2016-06-10 12:00 | 781 | 771
2016-06-10 12:30 | 784 | 774
2016-06-10 13:00 | 789 | 777
2016-06-10 13:30 | 785 | 773
2016-06-10 14:00 | 787 | 775
2016-06-10 14:30 | 797 | 785
2016-06-10 15:00 | 817 | 805
2016-06-10 15:30 | 832 | 820
2016-06-10 16:00 | 852 | 841
2016-06-10 16:30 | 884 | 875
2016-06-10 17:00 | 931 | 925
2016-06-10 17:30 | 954 | 951
2016-06-10 18:00 | 961 | 957
2016-06-10 18:30 | 941 | 934
2016-06-10 19:00 | 938 | 931
2016-06-10 19:30 | 923 | 915
2016-06-10 20:00 | 918 | 911
2016-06-10 20:30 | 907 | 899
2016-06-10 21:00 | 868 | 856
2016-06-10 21:30 | 826 | 819
2016-06-10 22:00 | 796 | 795
2016-06-10 22:30 | 778 | 776
2016-06-10 23:00 | 769 | 769
2016-06-10 23:30 | 734 | 733
2016-06-11 | 696 | 693
2016-06-11 00:30 | 656 | 649
2016-06-11 01:00 | 635 | 625
2016-06-11 01:30 | 605 | 591
2016-06-11 02:00 | 594 | 577
2016-06-11 02:30 | 584 | 565
2016-06-11 03:00 | 582 | 560
2016-06-11 03:30 | 580 | 558
2016-06-11 04:00 | 578 | 557
2016-06-11 04:30 | 582 | 562
2016-06-11 05:00 | 592 | 574
2016-06-11 05:30 | 603 | 589
2016-06-11 06:00 | 611 | 599
2016-06-11 06:30 | 637 | 629
2016-06-11 07:00 | 669 | 663
2016-06-11 07:30 | 711 | 707
2016-06-11 08:00 | 739 | 733
2016-06-11 08:30 | 756 | 751
2016-06-11 09:00 | 759 | 754
2016-06-11 09:30 | 765 | 757
2016-06-11 10:00 | 760 | 752
2016-06-11 10:30 | 749 | 741
2016-06-11 11:00 | 736 | 727
2016-06-11 11:30 | 731 | 721
2016-06-11 12:00 | 724 | 713
2016-06-11 12:30 | 697 | 683
2016-06-11 13:00 | 709 | 696
2016-06-11 13:30 | 708 | 694
2016-06-11 14:00 | 699 | 688
2016-06-11 14:30 | 690 | 684
2016-06-11 15:00 | 699 | 693
2016-06-11 15:30 | 717 | 712
2016-06-11 16:00 | 746 | 743
2016-06-11 16:30 | 774 | 771
2016-06-11 17:00 | 809 | 808
2016-06-11 17:30 | 863 | 861
2016-06-11 18:00 | 881 | 873
2016-06-11 18:30 | 877 | 863
2016-06-11 19:00 | 870 | 855
2016-06-11 19:30 | 852 | 839
2016-06-11 20:00 | 846 | 834
2016-06-11 20:30 | 847 | 834
2016-06-11 21:00 | 816 | 802
2016-06-11 21:30 | 796 | 783
2016-06-11 22:00 | 770 | 758
2016-06-11 22:30 | 768 | 755
2016-06-11 23:00 | 773 | 760
2016-06-11 23:30 | 742 | 735
2016-06-12 | 709 | 698
2016-06-12 00:30 | 673 | 664
2016-06-12 01:00 | 640 | 629
2016-06-12 01:30 | 604 | 590
2016-06-12 02:00 | 584 | 565
2016-06-12 02:30 | 578 | 558
2016-06-12 03:00 | 573 | 551
2016-06-12 03:30 | 572 | 548
2016-06-12 04:00 | 567 | 543
2016-06-12 04:30 | 569 | 544
2016-06-12 05:00 | 570 | 547
2016-06-12 05:30 | 579 | 559
2016-06-12 06:00 | 586 | 569
2016-06-12 06:30 | 598 | 584
2016-06-12 07:00 | 621 | 608
2016-06-12 07:30 | 659 | 650
2016-06-12 08:00 | 694 | 689
2016-06-12 08:30 | 729 | 727
2016-06-12 09:00 | 757 | 753
2016-06-12 09:30 | 769 | 767
2016-06-12 10:00 | 776 | 775
2016-06-12 10:30 | 777 | 776
2016-06-12 11:00 | 770 | 768
2016-06-12 11:30 | 742 | 738
2016-06-12 12:00 | 724 | 720
2016-06-12 12:30 | 716 | 711
2016-06-12 13:00 | 715 | 709
2016-06-12 13:30 | 702 | 696
2016-06-12 14:00 | 725 | 719
2016-06-12 14:30 | 746 | 742
2016-06-12 15:00 | 758 | 755
2016-06-12 15:30 | 770 | 767
2016-06-12 16:00 | 799 | 797
2016-06-12 16:30 | 837 | 837
2016-06-12 17:00 | 894 | 891
2016-06-12 17:30 | 938 | 934
2016-06-12 18:00 | 960 | 956
2016-06-12 18:30 | 949 | 943
2016-06-12 19:00 | 947 | 940
2016-06-12 19:30 | 929 | 919
2016-06-12 20:00 | 913 | 905
2016-06-12 20:30 | 910 | 901
2016-06-12 21:00 | 869 | 862
2016-06-12 21:30 | 856 | 849
2016-06-12 22:00 | 809 | 798
2016-06-12 22:30 | 779 | 766
2016-06-12 23:00 | 763 | 756
2016-06-12 23:30 | 735 | 728
2016-06-13 | 705 | 694
2016-06-13 00:30 | 646 | 637
2016-06-13 01:00 | 624 | 612
2016-06-13 01:30 | 604 | 589
2016-06-13 02:00 | 586 | 568
2016-06-13 02:30 | 579 | 558
2016-06-13 03:00 | 573 | 552
2016-06-13 03:30 | 572 | 550
2016-06-13 04:00 | 577 | 556
2016-06-13 04:30 | 587 | 568
2016-06-13 05:00 | 602 | 586
2016-06-13 05:30 | 640 | 632
2016-06-13 06:00 | 692 | 682
2016-06-13 06:30 | 782 | 764
2016-06-13 07:00 | 860 | 839
2016-06-13 07:30 | 923 | 907
2016-06-13 08:00 | 946 | 931
2016-06-13 08:30 | 943 | 930
2016-06-13 09:00 | 912 | 899
2016-06-13 09:30 | 894 | 880
2016-06-13 10:00 | 884 | 871
2016-06-13 10:30 | 869 | 854
2016-06-13 11:00 | 855 | 840
2016-06-13 11:30 | 864 | 847
2016-06-13 12:00 | 862 | 845
2016-06-13 12:30 | 835 | 814
2016-06-13 13:00 | 843 | 824
2016-06-13 13:30 | 850 | 833
2016-06-13 14:00 | 855 | 838
2016-06-13 14:30 | 863 | 845
2016-06-13 15:00 | 880 | 864
2016-06-13 15:30 | 883 | 867
2016-06-13 16:00 | 901 | 885
2016-06-13 16:30 | 945 | 933
2016-06-13 17:00 | 1007 | 1000
2016-06-13 17:30 | 1064 | 1056
2016-06-13 18:00 | 1085 | 1079
2016-06-13 18:30 | 1064 | 1055
2016-06-13 19:00 | 1052 | 1040
2016-06-13 19:30 | 1019 | 1010
2016-06-13 20:00 | 1006 | 999
2016-06-13 20:30 | 1001 | 993
2016-06-13 21:00 | 948 | 937
2016-06-13 21:30 | 885 | 876
2016-06-13 22:00 | 843 | 835
2016-06-13 22:30 | 825 | 813
2016-06-13 23:00 | 801 | 788
2016-06-13 23:30 | 755 | 748
2016-06-14 | 716 | 705
2016-06-14 00:30 | 665 | 648
2016-06-14 01:00 | 627 | 615
2016-06-14 01:30 | 597 | 582
2016-06-14 02:00 | 577 | 558
2016-06-14 02:30 | 579 | 557
2016-06-14 03:00 | 586 | 563
2016-06-14 03:30 | 587 | 563
2016-06-14 04:00 | 585 | 563
2016-06-14 04:30 | 594 | 574
2016-06-14 05:00 | 614 | 598
2016-06-14 05:30 | 653 | 644
2016-06-14 06:00 | 707 | 692
2016-06-14 06:30 | 788 | 779
2016-06-14 07:00 | 893 | 879
2016-06-14 07:30 | 953 | 941
2016-06-14 08:00 | 975 | 954
2016-06-14 08:30 | 962 | 936
2016-06-14 09:00 | 940 | 915
2016-06-14 09:30 | 898 | 871
2016-06-14 10:00 | 889 | 869
2016-06-14 10:30 | 884 | 874
2016-06-14 11:00 | 856 | 845
2016-06-14 11:30 | 823 | 810
2016-06-14 12:00 | 820 | 808
2016-06-14 12:30 | 823 | 810
2016-06-14 13:00 | 829 | 817
2016-06-14 13:30 | 830 | 818
2016-06-14 14:00 | 824 | 812
2016-06-14 14:30 | 825 | 812
2016-06-14 15:00 | 847 | 836
2016-06-14 15:30 | 867 | 856
2016-06-14 16:00 | 893 | 883
2016-06-14 16:30 | 922 | 914
2016-06-14 17:00 | 980 | 974
2016-06-14 17:30 | 1031 | 1026
2016-06-14 18:00 | 1067 | 1057
2016-06-14 18:30 | 1055 | 1040
2016-06-14 19:00 | 1042 | 1025
2016-06-14 19:30 | 1009 | 999
2016-06-14 20:00 | 1008 | 998
2016-06-14 20:30 | 992 | 980
2016-06-14 21:00 | 944 | 933
2016-06-14 21:30 | 890 | 879
2016-06-14 22:00 | 844 | 833
2016-06-14 22:30 | 825 | 817
2016-06-14 23:00 | 807 | 801
2016-06-14 23:30 | 773 | 763
2016-06-15 | 722 | 708
2016-06-15 00:30 | 677 | 664
2016-06-15 01:00 | 650 | 631
2016-06-15 01:30 | 618 | 602
2016-06-15 02:00 | 598 | 582
2016-06-15 02:30 | 588 | 571
2016-06-15 03:00 | 584 | 565
2016-06-15 03:30 | 582 | 563
2016-06-15 04:00 | 587 | 569
2016-06-15 04:30 | 596 | 580
2016-06-15 05:00 | 616 | 604
2016-06-15 05:30 | 649 | 643
2016-06-15 06:00 | 700 | 694
2016-06-15 06:30 | 807 | 790
2016-06-15 07:00 | 890 | 873
2016-06-15 07:30 | 955 | 938
2016-06-15 08:00 | 980 | 967
2016-06-15 08:30 | 969 | 948
2016-06-15 09:00 | 930 | 902
2016-06-15 09:30 | 906 | 877
2016-06-15 10:00 | 909 | 882
2016-06-15 10:30 | 883 | 854
2016-06-15 11:00 | 870 | 839
2016-06-15 11:30 | 856 | 820
2016-06-15 12:00 | 855 | 819
2016-06-15 12:30 | 842 | 811
2016-06-15 13:00 | 830 | 805
2016-06-15 13:30 | 827 | 801
2016-06-15 14:00 | 841 | 816
2016-06-15 14:30 | 850 | 826
2016-06-15 15:00 | 858 | 833
2016-06-15 15:30 | 880 | 856
2016-06-15 16:00 | 901 | 880
2016-06-15 16:30 | 943 | 926
2016-06-15 17:00 | 987 | 975
2016-06-15 17:30 | 1036 | 1025
2016-06-15 18:00 | 1050 | 1038
2016-06-15 18:30 | 1033 | 1018
2016-06-15 19:00 | 1035 | 1019
2016-06-15 19:30 | 1022 | 1002
2016-06-15 20:00 | 1004 | 990
2016-06-15 20:30 | 999 | 984
2016-06-15 21:00 | 941 | 925
2016-06-15 21:30 | 896 | 878
2016-06-15 22:00 | 850 | 833
2016-06-15 22:30 | 827 | 813
2016-06-15 23:00 | 805 | 788
2016-06-15 23:30 | 764 | 749
2016-06-16 | 717 | 699
2016-06-16 00:30 | 677 | 655
2016-06-16 01:00 | 636 | 619
2016-06-16 01:30 | 609 | 595
2016-06-16 02:00 | 597 | 581
2016-06-16 02:30 | 588 | 568
2016-06-16 03:00 | 585 | 565
2016-06-16 03:30 | 584 | 564
2016-06-16 04:00 | 586 | 567
2016-06-16 04:30 | 598 | 581
2016-06-16 05:00 | 616 | 603
2016-06-16 05:30 | 651 | 644
2016-06-16 06:00 | 692 | 680
2016-06-16 06:30 | 776 | 766
2016-06-16 07:00 | 871 | 857
2016-06-16 07:30 | 939 | 927
2016-06-16 08:00 | 953 | 943
2016-06-16 08:30 | 937 | 918
2016-06-16 09:00 | 915 | 893
2016-06-16 09:30 | 890 | 867
2016-06-16 10:00 | 860 | 835
2016-06-16 10:30 | 855 | 830
2016-06-16 11:00 | 850 | 826
2016-06-16 11:30 | 835 | 810
2016-06-16 12:00 | 820 | 796
2016-06-16 12:30 | 816 | 792
2016-06-16 13:00 | 826 | 803
2016-06-16 13:30 | 827 | 804
2016-06-16 14:00 | 841 | 817
2016-06-16 14:30 | 851 | 827
2016-06-16 15:00 | 855 | 830
2016-06-16 15:30 | 867 | 844
2016-06-16 16:00 | 890 | 868
2016-06-16 16:30 | 919 | 899
2016-06-16 17:00 | 955 | 941
2016-06-16 17:30 | 1008 | 1000
2016-06-16 18:00 | 1042 | 1025
2016-06-16 18:30 | 1031 | 1008
2016-06-16 19:00 | 1035 | 1012
2016-06-16 19:30 | 1008 | 995
2016-06-16 20:00 | 997 | 987
2016-06-16 20:30 | 991 | 982
2016-06-16 21:00 | 952 | 943
2016-06-16 21:30 | 905 | 895
2016-06-16 22:00 | 866 | 856
2016-06-16 22:30 | 827 | 820
2016-06-16 23:00 | 800 | 796
2016-06-16 23:30 | 754 | 749
2016-06-17 | 714 | 704
2016-06-17 00:30 | 678 | 665
2016-06-17 01:00 | 637 | 629
2016-06-17 01:30 | 611 | 599
2016-06-17 02:00 | 599 | 584
2016-06-17 02:30 | 589 | 571
2016-06-17 03:00 | 589 | 569
2016-06-17 03:30 | 600 | 579
2016-06-17 04:00 | 600 | 581
2016-06-17 04:30 | 614 | 596
2016-06-17 05:00 | 631 | 617
2016-06-17 05:30 | 669 | 661
2016-06-17 06:00 | 702 | 699
2016-06-17 06:30 | 776 | 776
2016-06-17 07:00 | 869 | 869
2016-06-17 07:30 | 934 | 933
2016-06-17 08:00 | 937 | 935
2016-06-17 08:30 | 932 | 925
2016-06-17 09:00 | 907 | 898
2016-06-17 09:30 | 874 | 864
2016-06-17 10:00 | 859 | 849
2016-06-17 10:30 | 839 | 830
2016-06-17 11:00 | 830 | 822
2016-06-17 11:30 | 826 | 818
2016-06-17 12:00 | 774 | 768
2016-06-17 12:30 | 784 | 778
2016-06-17 13:00 | 793 | 787
2016-06-17 13:30 | 790 | 783
2016-06-17 14:00 | 818 | 812
2016-06-17 14:30 | 814 | 807
2016-06-17 15:00 | 825 | 816
2016-06-17 15:30 | 866 | 856
2016-06-17 16:00 | 892 | 882
2016-06-17 16:30 | 921 | 913
2016-06-17 17:00 | 962 | 956
2016-06-17 17:30 | 994 | 987
2016-06-17 18:00 | 989 | 983
2016-06-17 18:30 | 965 | 955
2016-06-17 19:00 | 968 | 955
2016-06-17 19:30 | 938 | 928
2016-06-17 20:00 | 930 | 926
2016-06-17 20:30 | 918 | 915
2016-06-17 21:00 | 874 | 874
2016-06-17 21:30 | 837 | 837
2016-06-17 22:00 | 812 | 811
2016-06-17 22:30 | 790 | 789
2016-06-17 23:00 | 782 | 779
2016-06-17 23:30 | 746 | 742
2016-06-18 | 702 | 695
2016-06-18 00:30 | 665 | 655
2016-06-18 01:00 | 625 | 616
2016-06-18 01:30 | 594 | 582
2016-06-18 02:00 | 575 | 558
2016-06-18 02:30 | 563 | 545
2016-06-18 03:00 | 560 | 540
2016-06-18 03:30 | 558 | 538
2016-06-18 04:00 | 556 | 536
2016-06-18 04:30 | 559 | 537
2016-06-18 05:00 | 568 | 548
2016-06-18 05:30 | 592 | 577
2016-06-18 06:00 | 614 | 602
2016-06-18 06:30 | 646 | 638
2016-06-18 07:00 | 674 | 667
2016-06-18 07:30 | 718 | 710
2016-06-18 08:00 | 740 | 729
2016-06-18 08:30 | 745 | 737
2016-06-18 09:00 | 769 | 761
2016-06-18 09:30 | 785 | 777
2016-06-18 10:00 | 774 | 767
2016-06-18 10:30 | 780 | 773
2016-06-18 11:00 | 752 | 743
2016-06-18 11:30 | 737 | 729
2016-06-18 12:00 | 752 | 745
2016-06-18 12:30 | 748 | 740
2016-06-18 13:00 | 761 | 753
2016-06-18 13:30 | 756 | 747
2016-06-18 14:00 | 760 | 750
2016-06-18 14:30 | 762 | 753
2016-06-18 15:00 | 769 | 759
2016-06-18 15:30 | 779 | 769
2016-06-18 16:00 | 795 | 787
2016-06-18 16:30 | 828 | 822
2016-06-18 17:00 | 869 | 866
2016-06-18 17:30 | 899 | 895
2016-06-18 18:00 | 900 | 892
2016-06-18 18:30 | 892 | 881
2016-06-18 19:00 | 883 | 871
2016-06-18 19:30 | 864 | 859
2016-06-18 20:00 | 862 | 857
2016-06-18 20:30 | 853 | 847
2016-06-18 21:00 | 816 | 810
2016-06-18 21:30 | 794 | 787
2016-06-18 22:00 | 773 | 768
2016-06-18 22:30 | 765 | 759
2016-06-18 23:00 | 759 | 752
2016-06-18 23:30 | 732 | 723
2016-06-19 | 701 | 687
2016-06-19 00:30 | 659 | 648
2016-06-19 01:00 | 637 | 627
2016-06-19 01:30 | 615 | 603
2016-06-19 02:00 | 596 | 581
2016-06-19 02:30 | 591 | 574
2016-06-19 03:00 | 582 | 562
2016-06-19 03:30 | 582 | 562
2016-06-19 04:00 | 581 | 561
2016-06-19 04:30 | 577 | 557
2016-06-19 05:00 | 584 | 566
2016-06-19 05:30 | 587 | 571
2016-06-19 06:00 | 596 | 582
2016-06-19 06:30 | 609 | 598
2016-06-19 07:00 | 628 | 617
2016-06-19 07:30 | 657 | 649
2016-06-19 08:00 | 684 | 678
2016-06-19 08:30 | 726 | 719
2016-06-19 09:00 | 775 | 768
2016-06-19 09:30 | 795 | 790
2016-06-19 10:00 | 814 | 810
2016-06-19 10:30 | 841 | 835
2016-06-19 11:00 | 854 | 843
2016-06-19 11:30 | 845 | 832
2016-06-19 12:00 | 844 | 831
2016-06-19 12:30 | 843 | 830
2016-06-19 13:00 | 839 | 826
2016-06-19 13:30 | 841 | 829
2016-06-19 14:00 | 857 | 847
2016-06-19 14:30 | 861 | 850
2016-06-19 15:00 | 855 | 844
2016-06-19 15:30 | 864 | 854
2016-06-19 16:00 | 886 | 876
2016-06-19 16:30 | 922 | 914
2016-06-19 17:00 | 960 | 952
2016-06-19 17:30 | 1000 | 990
2016-06-19 18:00 | 995 | 983
2016-06-19 18:30 | 986 | 974
2016-06-19 19:00 | 977 | 964
2016-06-19 19:30 | 940 | 922
2016-06-19 20:00 | 922 | 902
2016-06-19 20:30 | 894 | 879
2016-06-19 21:00 | 842 | 830
2016-06-19 21:30 | 813 | 801
2016-06-19 22:00 | 787 | 778
2016-06-19 22:30 | 764 | 761
2016-06-19 23:00 | 749 | 748
2016-06-19 23:30 | 726 | 724
2016-06-20 | 677 | 673
2016-06-20 00:30 | 643 | 637
2016-06-20 01:00 | 621 | 612
2016-06-20 01:30 | 584 | 573
2016-06-20 02:00 | 558 | 544
2016-06-20 02:30 | 551 | 535
2016-06-20 03:00 | 552 | 535
2016-06-20 03:30 | 554 | 537
2016-06-20 04:00 | 557 | 541
2016-06-20 04:30 | 576 | 561
2016-06-20 05:00 | 596 | 586
2016-06-20 05:30 | 643 | 637
2016-06-20 06:00 | 695 | 683
2016-06-20 06:30 | 768 | 761
2016-06-20 07:00 | 842 | 838
2016-06-20 07:30 | 927 | 913
2016-06-20 08:00 | 943 | 927
2016-06-20 08:30 | 926 | 912
2016-06-20 09:00 | 893 | 877
2016-06-20 09:30 | 858 | 841
2016-06-20 10:00 | 836 | 817
2016-06-20 10:30 | 806 | 787
2016-06-20 11:00 | 770 | 751
2016-06-20 11:30 | 790 | 768
2016-06-20 12:00 | 765 | 742
2016-06-20 12:30 | 750 | 727
2016-06-20 13:00 | 755 | 736
2016-06-20 13:30 | 773 | 759
2016-06-20 14:00 | 806 | 793
2016-06-20 14:30 | 821 | 808
2016-06-20 15:00 | 843 | 831
2016-06-20 15:30 | 885 | 874
2016-06-20 16:00 | 917 | 909
2016-06-20 16:30 | 945 | 935
2016-06-20 17:00 | 990 | 980
2016-06-20 17:30 | 1071 | 1050
2016-06-20 18:00 | 1110 | 1088
2016-06-20 18:30 | 1113 | 1079
2016-06-20 19:00 | 1103 | 1071
2016-06-20 19:30 | 1058 | 1041
2016-06-20 20:00 | 1037 | 1026
2016-06-20 20:30 | 1027 | 1017
2016-06-20 21:00 | 987 | 969
2016-06-20 21:30 | 922 | 906
2016-06-20 22:00 | 878 | 866
2016-06-20 22:30 | 840 | 833
2016-06-20 23:00 | 813 | 807
2016-06-20 23:30 | 778 | 770
2016-06-21 | 741 | 729
2016-06-21 00:30 | 690 | 672
2016-06-21 01:00 | 656 | 642
2016-06-21 01:30 | 629 | 613
2016-06-21 02:00 | 606 | 592
2016-06-21 02:30 | 596 | 580
2016-06-21 03:00 | 590 | 573
2016-06-21 03:30 | 590 | 573
2016-06-21 04:00 | 590 | 573
2016-06-21 04:30 | 605 | 590
2016-06-21 05:00 | 623 | 612
2016-06-21 05:30 | 668 | 661
2016-06-21 06:00 | 722 | 710
2016-06-21 06:30 | 802 | 786
2016-06-21 07:00 | 889 | 872
2016-06-21 07:30 | 966 | 952
2016-06-21 08:00 | 986 | 965
2016-06-21 08:30 | 963 | 941
2016-06-21 09:00 | 928 | 901
2016-06-21 09:30 | 913 | 884
2016-06-21 10:00 | 878 | 861
2016-06-21 10:30 | 885 | 872
2016-06-21 11:00 | 867 | 854
2016-06-21 11:30 | 826 | 819
2016-06-21 12:00 | 812 | 808
2016-06-21 12:30 | 787 | 781
2016-06-21 13:00 | 771 | 764
2016-06-21 13:30 | 769 | 762
2016-06-21 14:00 | 821 | 816
2016-06-21 14:30 | 855 | 850
2016-06-21 15:00 | 879 | 871
2016-06-21 15:30 | 894 | 886
2016-06-21 16:00 | 907 | 901
2016-06-21 16:30 | 932 | 927
2016-06-21 17:00 | 993 | 984
2016-06-21 17:30 | 1054 | 1045
2016-06-21 18:00 | 1081 | 1067
2016-06-21 18:30 | 1074 | 1055
2016-06-21 19:00 | 1070 | 1052
2016-06-21 19:30 | 1042 | 1029
2016-06-21 20:00 | 1040 | 1028
2016-06-21 20:30 | 1033 | 1020
2016-06-21 21:00 | 979 | 973
2016-06-21 21:30 | 932 | 923
2016-06-21 22:00 | 900 | 884
2016-06-21 22:30 | 867 | 854
2016-06-21 23:00 | 843 | 827
2016-06-21 23:30 | 792 | 778
2016-06-22 | 750 | 727
2016-06-22 00:30 | 702 | 682
2016-06-22 01:00 | 662 | 644
2016-06-22 01:30 | 630 | 615
2016-06-22 02:00 | 608 | 591
2016-06-22 02:30 | 598 | 579
2016-06-22 03:00 | 582 | 560
2016-06-22 03:30 | 597 | 577
2016-06-22 04:00 | 583 | 562
2016-06-22 04:30 | 596 | 578
2016-06-22 05:00 | 605 | 590
2016-06-22 05:30 | 670 | 663
2016-06-22 06:00 | 730 | 709
2016-06-22 06:30 | 815 | 797
2016-06-22 07:00 | 892 | 878
2016-06-22 07:30 | 976 | 959
2016-06-22 08:00 | 1007 | 986
2016-06-22 08:30 | 991 | 971
2016-06-22 09:00 | 984 | 965
2016-06-22 09:30 | 975 | 954
2016-06-22 10:00 | 960 | 938
2016-06-22 10:30 | 965 | 944
2016-06-22 11:00 | 953 | 933
2016-06-22 11:30 | 929 | 907
2016-06-22 12:00 | 896 | 875
2016-06-22 12:30 | 845 | 834
2016-06-22 13:00 | 809 | 799
2016-06-22 13:30 | 803 | 792
2016-06-22 14:00 | 826 | 817
2016-06-22 14:30 | 812 | 801
2016-06-22 15:00 | 840 | 829
2016-06-22 15:30 | 862 | 851
2016-06-22 16:00 | 900 | 891
2016-06-22 16:30 | 943 | 936
2016-06-22 17:00 | 981 | 975
2016-06-22 17:30 | 1022 | 1019
2016-06-22 18:00 | 1059 | 1049
2016-06-22 18:30 | 1052 | 1039
2016-06-22 19:00 | 1051 | 1036
2016-06-22 19:30 | 1022 | 1015
2016-06-22 20:00 | 1020 | 1012
2016-06-22 20:30 | 1008 | 999
2016-06-22 21:00 | 951 | 939
2016-06-22 21:30 | 911 | 904
2016-06-22 22:00 | 879 | 869
2016-06-22 22:30 | 854 | 841
2016-06-22 23:00 | 845 | 829
2016-06-22 23:30 | 814 | 793
2016-06-23 | 761 | 737
2016-06-23 00:30 | 720 | 694
2016-06-23 01:00 | 687 | 655
2016-06-23 01:30 | 651 | 623
2016-06-23 02:00 | 628 | 600
2016-06-23 02:30 | 621 | 595
2016-06-23 03:00 | 600 | 581
2016-06-23 03:30 | 602 | 583
2016-06-23 04:00 | 606 | 587
2016-06-23 04:30 | 616 | 601
2016-06-23 05:00 | 631 | 620
2016-06-23 05:30 | 669 | 663
2016-06-23 06:00 | 716 | 709
2016-06-23 06:30 | 796 | 787
2016-06-23 07:00 | 880 | 863
2016-06-23 07:30 | 954 | 938
2016-06-23 08:00 | 1003 | 981
2016-06-23 08:30 | 1010 | 986
2016-06-23 09:00 | 1005 | 982
2016-06-23 09:30 | 989 | 964
2016-06-23 10:00 | 984 | 960
2016-06-23 10:30 | 977 | 952
2016-06-23 11:00 | 955 | 928
2016-06-23 11:30 | 947 | 920
2016-06-23 12:00 | 954 | 927
2016-06-23 12:30 | 954 | 926
2016-06-23 13:00 | 938 | 912
2016-06-23 13:30 | 935 | 918
2016-06-23 14:00 | 937 | 921
2016-06-23 14:30 | 949 | 933
2016-06-23 15:00 | 949 | 933
2016-06-23 15:30 | 954 | 938
2016-06-23 16:00 | 967 | 953
2016-06-23 16:30 | 998 | 985
2016-06-23 17:00 | 1046 | 1038
2016-06-23 17:30 | 1113 | 1105
2016-06-23 18:00 | 1136 | 1128
2016-06-23 18:30 | 1134 | 1117
2016-06-23 19:00 | 1132 | 1113
2016-06-23 19:30 | 1091 | 1082
2016-06-23 20:00 | 1079 | 1072
2016-06-23 20:30 | 1071 | 1066
2016-06-23 21:00 | 1008 | 1005
2016-06-23 21:30 | 939 | 934
2016-06-23 22:00 | 885 | 880
2016-06-23 22:30 | 855 | 851
2016-06-23 23:00 | 829 | 827
2016-06-23 23:30 | 787 | 785
2016-06-24 | 738 | 734
2016-06-24 00:30 | 686 | 680
2016-06-24 01:00 | 660 | 652
2016-06-24 01:30 | 633 | 622
2016-06-24 02:00 | 615 | 601
2016-06-24 02:30 | 604 | 588
2016-06-24 03:00 | 595 | 578
2016-06-24 03:30 | 591 | 573
2016-06-24 04:00 | 592 | 575
2016-06-24 04:30 | 604 | 589
2016-06-24 05:00 | 624 | 613
2016-06-24 05:30 | 661 | 654
2016-06-24 06:00 | 713 | 699
2016-06-24 06:30 | 784 | 774
2016-06-24 07:00 | 871 | 848
2016-06-24 07:30 | 942 | 926
2016-06-24 08:00 | 979 | 963
2016-06-24 08:30 | 979 | 965
2016-06-24 09:00 | 967 | 954
2016-06-24 09:30 | 949 | 934
2016-06-24 10:00 | 895 | 873
2016-06-24 10:30 | 847 | 830
2016-06-24 11:00 | 827 | 816
2016-06-24 11:30 | 818 | 806
2016-06-24 12:00 | 814 | 804
2016-06-24 12:30 | 794 | 786
2016-06-24 13:00 | 788 | 780
2016-06-24 13:30 | 786 | 777
2016-06-24 14:00 | 798 | 789
2016-06-24 14:30 | 824 | 817
2016-06-24 15:00 | 844 | 838
2016-06-24 15:30 | 850 | 844
2016-06-24 16:00 | 877 | 871
2016-06-24 16:30 | 901 | 896
2016-06-24 17:00 | 936 | 932
2016-06-24 17:30 | 978 | 972
2016-06-24 18:00 | 995 | 987
2016-06-24 18:30 | 985 | 972
2016-06-24 19:00 | 984 | 974
2016-06-24 19:30 | 962 | 959
2016-06-24 20:00 | 961 | 959
2016-06-24 20:30 | 959 | 957
2016-06-24 21:00 | 919 | 919
2016-06-24 21:30 | 888 | 888
2016-06-24 22:00 | 855 | 855
2016-06-24 22:30 | 835 | 834
2016-06-24 23:00 | 815 | 814
2016-06-24 23:30 | 783 | 780
2016-06-25 | 745 | 739
2016-06-25 00:30 | 701 | 692
2016-06-25 01:00 | 666 | 652
2016-06-25 01:30 | 638 | 620
2016-06-25 02:00 | 608 | 586
2016-06-25 02:30 | 599 | 575
2016-06-25 03:00 | 592 | 567
2016-06-25 03:30 | 595 | 568
2016-06-25 04:00 | 608 | 583
2016-06-25 04:30 | 587 | 568
2016-06-25 05:00 | 587 | 577
2016-06-25 05:30 | 605 | 598
2016-06-25 06:00 | 618 | 613
2016-06-25 06:30 | 651 | 648
2016-06-25 07:00 | 701 | 699
2016-06-25 07:30 | 762 | 762
2016-06-25 08:00 | 778 | 776
2016-06-25 08:30 | 782 | 778
2016-06-25 09:00 | 794 | 786
2016-06-25 09:30 | 773 | 765
2016-06-25 10:00 | 744 | 733
2016-06-25 10:30 | 721 | 707
2016-06-25 11:00 | 688 | 673
2016-06-25 11:30 | 655 | 643
2016-06-25 12:00 | 639 | 624
2016-06-25 12:30 | 621 | 606
2016-06-25 13:00 | 618 | 609
2016-06-25 13:30 | 628 | 620
2016-06-25 14:00 | 641 | 633
2016-06-25 14:30 | 660 | 653
2016-06-25 15:00 | 689 | 683
2016-06-25 15:30 | 717 | 713
2016-06-25 16:00 | 757 | 754
2016-06-25 16:30 | 801 | 800
2016-06-25 17:00 | 861 | 860
2016-06-25 17:30 | 938 | 936
2016-06-25 18:00 | 988 | 985
2016-06-25 18:30 | 993 | 989
2016-06-25 19:00 | 1002 | 997
2016-06-25 19:30 | 992 | 990
2016-06-25 20:00 | 995 | 993
2016-06-25 20:30 | 988 | 986
2016-06-25 21:00 | 956 | 954
2016-06-25 21:30 | 940 | 936
2016-06-25 22:00 | 904 | 903
2016-06-25 22:30 | 883 | 882
2016-06-25 23:00 | 864 | 863
2016-06-25 23:30 | 828 | 825
2016-06-26 | 784 | 777
2016-06-26 00:30 | 741 | 733
2016-06-26 01:00 | 707 | 698
2016-06-26 01:30 | 666 | 661
2016-06-26 02:00 | 632 | 623
2016-06-26 02:30 | 628 | 618
2016-06-26 03:00 | 622 | 611
2016-06-26 03:30 | 625 | 614
2016-06-26 04:00 | 620 | 608
2016-06-26 04:30 | 624 | 612
2016-06-26 05:00 | 631 | 622
2016-06-26 05:30 | 644 | 634
2016-06-26 06:00 | 659 | 651
2016-06-26 06:30 | 685 | 681
2016-06-26 07:00 | 718 | 714
2016-06-26 07:30 | 765 | 763
2016-06-26 08:00 | 823 | 816
2016-06-26 08:30 | 878 | 873
2016-06-26 09:00 | 891 | 886
2016-06-26 09:30 | 899 | 896
2016-06-26 10:00 | 869 | 865
2016-06-26 10:30 | 854 | 848
2016-06-26 11:00 | 843 | 836
2016-06-26 11:30 | 830 | 822
2016-06-26 12:00 | 812 | 802
2016-06-26 12:30 | 786 | 772
2016-06-26 13:00 | 768 | 753
2016-06-26 13:30 | 781 | 769
2016-06-26 14:00 | 796 | 785
2016-06-26 14:30 | 797 | 785
2016-06-26 15:00 | 820 | 810
2016-06-26 15:30 | 851 | 844
2016-06-26 16:00 | 882 | 878
2016-06-26 16:30 | 924 | 922
2016-06-26 17:00 | 988 | 988
2016-06-26 17:30 | 1044 | 1042
2016-06-26 18:00 | 1078 | 1076
2016-06-26 18:30 | 1077 | 1074
2016-06-26 19:00 | 1078 | 1074
2016-06-26 19:30 | 1053 | 1050
2016-06-26 20:00 | 1042 | 1038
2016-06-26 20:30 | 1035 | 1031
2016-06-26 21:00 | 995 | 993
2016-06-26 21:30 | 949 | 943
2016-06-26 22:00 | 889 | 882
2016-06-26 22:30 | 847 | 843
2016-06-26 23:00 | 822 | 815
2016-06-26 23:30 | 788 | 777
2016-06-27 | 736 | 722
2016-06-27 00:30 | 700 | 688
2016-06-27 01:00 | 666 | 658
2016-06-27 01:30 | 644 | 635
2016-06-27 02:00 | 625 | 614
2016-06-27 02:30 | 614 | 604
2016-06-27 03:00 | 606 | 594
2016-06-27 03:30 | 604 | 593
2016-06-27 04:00 | 602 | 591
2016-06-27 04:30 | 613 | 605
2016-06-27 05:00 | 629 | 624
2016-06-27 05:30 | 671 | 670
2016-06-27 06:00 | 714 | 712
2016-06-27 06:30 | 777 | 777
2016-06-27 07:00 | 869 | 867
2016-06-27 07:30 | 975 | 973
2016-06-27 08:00 | 1037 | 1033
2016-06-27 08:30 | 1068 | 1062
2016-06-27 09:00 | 1074 | 1066
2016-06-27 09:30 | 1051 | 1040
2016-06-27 10:00 | 991 | 977
2016-06-27 10:30 | 947 | 932
2016-06-27 11:00 | 934 | 921
2016-06-27 11:30 | 930 | 917
2016-06-27 12:00 | 955 | 943
2016-06-27 12:30 | 963 | 950
2016-06-27 13:00 | 920 | 907
2016-06-27 13:30 | 865 | 856
2016-06-27 14:00 | 855 | 846
2016-06-27 14:30 | 840 | 830
2016-06-27 15:00 | 847 | 837
2016-06-27 15:30 | 872 | 863
2016-06-27 16:00 | 902 | 895
2016-06-27 16:30 | 958 | 955
2016-06-27 17:00 | 1049 | 1045
2016-06-27 17:30 | 1145 | 1139
2016-06-27 18:00 | 1215 | 1209
2016-06-27 18:30 | 1215 | 1209
2016-06-27 19:00 | 1214 | 1209
2016-06-27 19:30 | 1174 | 1174
2016-06-27 20:00 | 1166 | 1165
2016-06-27 20:30 | 1158 | 1157
2016-06-27 21:00 | 1104 | 1102
2016-06-27 21:30 | 1040 | 1038
2016-06-27 22:00 | 985 | 981
2016-06-27 22:30 | 930 | 923
2016-06-27 23:00 | 897 | 889
2016-06-27 23:30 | 844 | 842
2016-06-28 | 788 | 785
2016-06-28 00:30 | 732 | 726
2016-06-28 01:00 | 698 | 689
2016-06-28 01:30 | 668 | 657
2016-06-28 02:00 | 640 | 634
2016-06-28 02:30 | 634 | 630
2016-06-28 03:00 | 639 | 634
2016-06-28 03:30 | 639 | 633
2016-06-28 04:00 | 640 | 634
2016-06-28 04:30 | 652 | 648
2016-06-28 05:00 | 664 | 661
2016-06-28 05:30 | 699 | 699
2016-06-28 06:00 | 785 | 782
2016-06-28 06:30 | 885 | 881
2016-06-28 07:00 | 975 | 971
2016-06-28 07:30 | 1070 | 1065
2016-06-28 08:00 | 1108 | 1103
2016-06-28 08:30 | 1090 | 1085
2016-06-28 09:00 | 1058 | 1050
2016-06-28 09:30 | 1003 | 995
2016-06-28 10:00 | 956 | 945
2016-06-28 10:30 | 908 | 902
2016-06-28 11:00 | 867 | 865
2016-06-28 11:30 | 834 | 831
2016-06-28 12:00 | 814 | 812
2016-06-28 12:30 | 798 | 796
2016-06-28 13:00 | 790 | 788
2016-06-28 13:30 | 792 | 790
2016-06-28 14:00 | 758 | 757
2016-06-28 14:30 | 737 | 735
2016-06-28 15:00 | 765 | 764
2016-06-28 15:30 | 798 | 796
2016-06-28 16:00 | 835 | 833
2016-06-28 16:30 | 870 | 869
2016-06-28 17:00 | 947 | 940
2016-06-28 17:30 | 1033 | 1031
2016-06-28 18:00 | 1101 | 1098
2016-06-28 18:30 | 1114 | 1109
2016-06-28 19:00 | 1120 | 1118
2016-06-28 19:30 | 1090 | 1088
2016-06-28 20:00 | 1078 | 1076
2016-06-28 20:30 | 1072 | 1071
2016-06-28 21:00 | 1006 | 1005
2016-06-28 21:30 | 940 | 940
2016-06-28 22:00 | 894 | 894
2016-06-28 22:30 | 834 | 834
2016-06-28 23:00 | 811 | 810
2016-06-28 23:30 | 777 | 775
2016-06-29 | 730 | 726
2016-06-29 00:30 | 673 | 669
2016-06-29 01:00 | 640 | 638
2016-06-29 01:30 | 605 | 602
2016-06-29 02:00 | 587 | 583
2016-06-29 02:30 | 579 | 575
2016-06-29 03:00 | 568 | 563
2016-06-29 03:30 | 585 | 580
2016-06-29 04:00 | 590 | 585
2016-06-29 04:30 | 607 | 603
2016-06-29 05:00 | 630 | 626
2016-06-29 05:30 | 671 | 669
2016-06-29 06:00 | 721 | 719
2016-06-29 06:30 | 814 | 809
2016-06-29 07:00 | 885 | 878
2016-06-29 07:30 | 970 | 961
2016-06-29 08:00 | 988 | 976
2016-06-29 08:30 | 957 | 946
2016-06-29 09:00 | 858 | 846
2016-06-29 09:30 | 782 | 767
2016-06-29 10:00 | 742 | 739
2016-06-29 10:30 | 705 | 703
2016-06-29 11:00 | 721 | 718
2016-06-29 11:30 | 691 | 688
2016-06-29 12:00 | 659 | 656
2016-06-29 12:30 | 667 | 666
2016-06-29 13:00 | 657 | 655
2016-06-29 13:30 | 660 | 658
2016-06-29 14:00 | 683 | 681
2016-06-29 14:30 | 704 | 702
2016-06-29 15:00 | 731 | 727
2016-06-29 15:30 | 762 | 758
2016-06-29 16:00 | 796 | 792
2016-06-29 16:30 | 841 | 837
2016-06-29 17:00 | 911 | 896
2016-06-29 17:30 | 981 | 962
2016-06-29 18:00 | 1029 | 1007
2016-06-29 18:30 | 1028 | 1005
2016-06-29 19:00 | 1038 | 1015
2016-06-29 19:30 | 1025 | 1002
2016-06-29 20:00 | 1016 | 995
2016-06-29 20:30 | 1019 | 997
2016-06-29 21:00 | 988 | 960
2016-06-29 21:30 | 917 | 908
2016-06-29 22:00 | 876 | 869
2016-06-29 22:30 | 834 | 829
2016-06-29 23:00 | 808 | 801
2016-06-29 23:30 | 763 | 759
2016-06-30 | 719 | 714
2016-06-30 00:30 | 683 | 672
2016-06-30 01:00 | 646 | 636
2016-06-30 01:30 | 609 | 604
2016-06-30 02:00 | 588 | 583
2016-06-30 02:30 | 583 | 577
2016-06-30 03:00 | 541 | 533
2016-06-30 03:30 | 560 | 553
2016-06-30 04:00 | 548 | 539
2016-06-30 04:30 | 541 | 534
2016-06-30 05:00 | 574 | 568
2016-06-30 05:30 | 620 | 617
2016-06-30 06:00 | 711 | 710
2016-06-30 06:30 | 800 | 798
2016-06-30 07:00 | 894 | 893
2016-06-30 07:30 | 976 | 976
2016-06-30 08:00 | 993 | 993
2016-06-30 08:30 | 977 | 977
2016-06-30 09:00 | 924 | 924
2016-06-30 09:30 | 866 | 866
2016-06-30 10:00 | 814 | 814
2016-06-30 10:30 | 779 | 778
2016-06-30 11:00 | 761 | 759
2016-06-30 11:30 | 740 | 738
2016-06-30 12:00 | 716 | 715
2016-06-30 12:30 | 705 | 705
2016-06-30 13:00 | 706 | 706
2016-06-30 13:30 | 722 | 721
2016-06-30 14:00 | 730 | 729
2016-06-30 14:30 | 741 | 741
2016-06-30 15:00 | 766 | 765
2016-06-30 15:30 | 789 | 789
2016-06-30 16:00 | 820 | 820
2016-06-30 16:30 | 853 | 852
2016-06-30 17:00 | 917 | 916
2016-06-30 17:30 | 981 | 981
2016-06-30 18:00 | 1026 | 1026
2016-06-30 18:30 | 1028 | 1028
2016-06-30 19:00 | 1046 | 1046
2016-06-30 19:30 | 1013 | 1012
2016-06-30 20:00 | 1006 | 1006
2016-06-30 20:30 | 1016 | 1015
2016-06-30 21:00 | 958 | 958
2016-06-30 21:30 | 890 | 888
2016-06-30 22:00 | 839 | 838
2016-06-30 22:30 | 803 | 799
2016-06-30 23:00 | 792 | 786
2016-06-30 23:30 | 751 | 743
2016-07-01 | 696 | 694
2016-07-01 00:30 | 645 | 641
2016-07-01 01:00 | 612 | 606
2016-07-01 01:30 | 574 | 567
2016-07-01 02:00 | 553 | 545
2016-07-01 02:30 | 548 | 538
2016-07-01 03:00 | 538 | 529
2016-07-01 03:30 | 540 | 531
2016-07-01 04:00 | 550 | 541
2016-07-01 04:30 | 569 | 561
2016-07-01 05:00 | 594 | 587
2016-07-01 05:30 | 632 | 628
2016-07-01 06:00 | 675 | 673
2016-07-01 06:30 | 747 | 746
2016-07-01 07:00 | 801 | 800
2016-07-01 07:30 | 878 | 877
2016-07-01 08:00 | 890 | 889
2016-07-01 08:30 | 874 | 873
2016-07-01 09:00 | 835 | 834
2016-07-01 09:30 | 795 | 794
2016-07-01 10:00 | 757 | 754
2016-07-01 10:30 | 728 | 726
2016-07-01 11:00 | 713 | 712
2016-07-01 11:30 | 691 | 689
2016-07-01 12:00 | 681 | 679
2016-07-01 12:30 | 686 | 686
2016-07-01 13:00 | 701 | 700
2016-07-01 13:30 | 707 | 707
2016-07-01 14:00 | 719 | 719
2016-07-01 14:30 | 729 | 729
2016-07-01 15:00 | 734 | 734
2016-07-01 15:30 | 764 | 764
2016-07-01 16:00 | 830 | 830
2016-07-01 16:30 | 890 | 890
2016-07-01 17:00 | 934 | 934
2016-07-01 17:30 | 991 | 989
2016-07-01 18:00 | 1032 | 1028
2016-07-01 18:30 | 1029 | 1023
2016-07-01 19:00 | 1029 | 1023
2016-07-01 19:30 | 1018 | 1011
2016-07-01 20:00 | 1010 | 1004
2016-07-01 20:30 | 1012 | 1008
2016-07-01 21:00 | 968 | 965
2016-07-01 21:30 | 939 | 936
2016-07-01 22:00 | 910 | 905
2016-07-01 22:30 | 886 | 882
2016-07-01 23:00 | 866 | 864
2016-07-01 23:30 | 820 | 819
2016-07-02 | 766 | 765
2016-07-02 00:30 | 717 | 715
2016-07-02 01:00 | 679 | 675
2016-07-02 01:30 | 645 | 639
2016-07-02 02:00 | 617 | 610
2016-07-02 02:30 | 609 | 600
2016-07-02 03:00 | 585 | 574
2016-07-02 03:30 | 575 | 564
2016-07-02 04:00 | 570 | 559
2016-07-02 04:30 | 576 | 565
2016-07-02 05:00 | 596 | 586
2016-07-02 05:30 | 624 | 616
2016-07-02 06:00 | 663 | 658
2016-07-02 06:30 | 700 | 698
2016-07-02 07:00 | 742 | 741
2016-07-02 07:30 | 805 | 805
2016-07-02 08:00 | 829 | 829
2016-07-02 08:30 | 845 | 843
2016-07-02 09:00 | 836 | 835
2016-07-02 09:30 | 812 | 810
2016-07-02 10:00 | 767 | 764
2016-07-02 10:30 | 738 | 734
2016-07-02 11:00 | 706 | 702
2016-07-02 11:30 | 663 | 663
2016-07-02 12:00 | 639 | 639
2016-07-02 12:30 | 630 | 629
2016-07-02 13:00 | 623 | 621
2016-07-02 13:30 | 626 | 624
2016-07-02 14:00 | 639 | 637
2016-07-02 14:30 | 651 | 649
2016-07-02 15:00 | 672 | 671
2016-07-02 15:30 | 700 | 700
2016-07-02 16:00 | 749 | 749
2016-07-02 16:30 | 789 | 789
2016-07-02 17:00 | 847 | 846
2016-07-02 17:30 | 932 | 926
2016-07-02 18:00 | 984 | 981
2016-07-02 18:30 | 998 | 993
2016-07-02 19:00 | 1003 | 998
2016-07-02 19:30 | 988 | 982
2016-07-02 20:00 | 984 | 977
2016-07-02 20:30 | 980 | 972
2016-07-02 21:00 | 961 | 953
2016-07-02 21:30 | 927 | 919
2016-07-02 22:00 | 905 | 894
2016-07-02 22:30 | 892 | 883
2016-07-02 23:00 | 878 | 871
2016-07-02 23:30 | 841 | 832
2016-07-03 | 799 | 787
2016-07-03 00:30 | 730 | 727
2016-07-03 01:00 | 695 | 691
2016-07-03 01:30 | 661 | 655
2016-07-03 02:00 | 638 | 629
2016-07-03 02:30 | 611 | 601
2016-07-03 03:00 | 592 | 580
2016-07-03 03:30 | 601 | 588
2016-07-03 04:00 | 611 | 599
2016-07-03 04:30 | 622 | 609
2016-07-03 05:00 | 631 | 619
2016-07-03 05:30 | 652 | 641
2016-07-03 06:00 | 669 | 659
2016-07-03 06:30 | 692 | 685
2016-07-03 07:00 | 723 | 717
2016-07-03 07:30 | 758 | 756
2016-07-03 08:00 | 781 | 780
2016-07-03 08:30 | 801 | 800
2016-07-03 09:00 | 806 | 805
2016-07-03 09:30 | 783 | 783
2016-07-03 10:00 | 751 | 750
2016-07-03 10:30 | 726 | 726
2016-07-03 11:00 | 686 | 685
2016-07-03 11:30 | 655 | 653
2016-07-03 12:00 | 655 | 653
2016-07-03 12:30 | 638 | 636
2016-07-03 13:00 | 639 | 637
2016-07-03 13:30 | 629 | 627
2016-07-03 14:00 | 643 | 640
2016-07-03 14:30 | 646 | 643
2016-07-03 15:00 | 680 | 678
2016-07-03 15:30 | 714 | 713
2016-07-03 16:00 | 754 | 753
2016-07-03 16:30 | 802 | 801
2016-07-03 17:00 | 863 | 862
2016-07-03 17:30 | 934 | 929
2016-07-03 18:00 | 995 | 990
2016-07-03 18:30 | 1013 | 997
2016-07-03 19:00 | 1017 | 1002
2016-07-03 19:30 | 1000 | 989
2016-07-03 20:00 | 993 | 981
2016-07-03 20:30 | 986 | 976
2016-07-03 21:00 | 942 | 937
2016-07-03 21:30 | 907 | 902
2016-07-03 22:00 | 869 | 864
2016-07-03 22:30 | 848 | 847
2016-07-03 23:00 | 828 | 827
2016-07-03 23:30 | 782 | 779
2016-07-04 | 732 | 728
2016-07-04 00:30 | 695 | 688
2016-07-04 01:00 | 663 | 655
2016-07-04 01:30 | 652 | 644
2016-07-04 02:00 | 634 | 624
2016-07-04 02:30 | 623 | 612
2016-07-04 03:00 | 619 | 606
2016-07-04 03:30 | 621 | 607
2016-07-04 04:00 | 622 | 608
2016-07-04 04:30 | 636 | 624
2016-07-04 05:00 | 658 | 649
2016-07-04 05:30 | 703 | 699
2016-07-04 06:00 | 749 | 748
2016-07-04 06:30 | 839 | 839
2016-07-04 07:00 | 908 | 908
2016-07-04 07:30 | 988 | 986
2016-07-04 08:00 | 1018 | 1009
2016-07-04 08:30 | 1008 | 1005
2016-07-04 09:00 | 984 | 981
2016-07-04 09:30 | 953 | 946
2016-07-04 10:00 | 918 | 908
2016-07-04 10:30 | 1026 | 1015
2016-07-04 11:00 | 1065 | 1058
2016-07-04 11:30 | 1016 | 1011
2016-07-04 12:00 | 980 | 975
2016-07-04 12:30 | 973 | 970
2016-07-04 13:00 | 963 | 960
2016-07-04 13:30 | 961 | 958
2016-07-04 14:00 | 967 | 963
2016-07-04 14:30 | 984 | 981
2016-07-04 15:00 | 1002 | 1000
2016-07-04 15:30 | 1024 | 1021
2016-07-04 16:00 | 1055 | 1052
2016-07-04 16:30 | 1097 | 1095
2016-07-04 17:00 | 1177 | 1169
2016-07-04 17:30 | 1272 | 1266
2016-07-04 18:00 | 1338 | 1324
2016-07-04 18:30 | 1329 | 1312
2016-07-04 19:00 | 1318 | 1301
2016-07-04 19:30 | 1283 | 1267
2016-07-04 20:00 | 1259 | 1247
2016-07-04 20:30 | 1257 | 1243
2016-07-04 21:00 | 1195 | 1185
2016-07-04 21:30 | 1140 | 1128
2016-07-04 22:00 | 1092 | 1079
2016-07-04 22:30 | 1032 | 1028
2016-07-04 23:00 | 1001 | 997
2016-07-04 23:30 | 963 | 957
2016-07-05 | 896 | 890
2016-07-05 00:30 | 840 | 837
2016-07-05 01:00 | 805 | 801
2016-07-05 01:30 | 769 | 761
2016-07-05 02:00 | 738 | 729
2016-07-05 02:30 | 715 | 705
2016-07-05 03:00 | 705 | 692
2016-07-05 03:30 | 697 | 682
2016-07-05 04:00 | 695 | 680
2016-07-05 04:30 | 712 | 700
2016-07-05 05:00 | 738 | 728
2016-07-05 05:30 | 782 | 777
2016-07-05 06:00 | 837 | 836
2016-07-05 06:30 | 937 | 935
2016-07-05 07:00 | 1025 | 1016
2016-07-05 07:30 | 1116 | 1111
2016-07-05 08:00 | 1175 | 1170
2016-07-05 08:30 | 1206 | 1200
2016-07-05 09:00 | 1225 | 1218
2016-07-05 09:30 | 1235 | 1226
2016-07-05 10:00 | 1234 | 1224
2016-07-05 10:30 | 1218 | 1203
2016-07-05 11:00 | 1192 | 1174
2016-07-05 11:30 | 1158 | 1143
2016-07-05 12:00 | 1150 | 1137
2016-07-05 12:30 | 1142 | 1132
2016-07-05 13:00 | 1137 | 1129
2016-07-05 13:30 | 1130 | 1123
2016-07-05 14:00 | 1136 | 1128
2016-07-05 14:30 | 1123 | 1115
2016-07-05 15:00 | 1106 | 1097
2016-07-05 15:30 | 1096 | 1086
2016-07-05 16:00 | 1113 | 1104
2016-07-05 16:30 | 1144 | 1136
2016-07-05 17:00 | 1201 | 1196
2016-07-05 17:30 | 1274 | 1269
2016-07-05 18:00 | 1341 | 1320
2016-07-05 18:30 | 1326 | 1299
2016-07-05 19:00 | 1323 | 1296
2016-07-05 19:30 | 1294 | 1268
2016-07-05 20:00 | 1274 | 1253
2016-07-05 20:30 | 1278 | 1255
2016-07-05 21:00 | 1231 | 1208
2016-07-05 21:30 | 1167 | 1147
2016-07-05 22:00 | 1103 | 1087
2016-07-05 22:30 | 1076 | 1056
2016-07-05 23:00 | 1046 | 1025
2016-07-05 23:30 | 997 | 978
2016-07-06 | 930 | 904
2016-07-06 00:30 | 869 | 842
2016-07-06 01:00 | 834 | 798
2016-07-06 01:30 | 767 | 746
2016-07-06 02:00 | 736 | 720
2016-07-06 02:30 | 722 | 705
2016-07-06 03:00 | 713 | 695
2016-07-06 03:30 | 710 | 691
2016-07-06 04:00 | 711 | 693
2016-07-06 04:30 | 729 | 713
2016-07-06 05:00 | 745 | 732
2016-07-06 05:30 | 793 | 786
2016-07-06 06:00 | 864 | 861
2016-07-06 06:30 | 1016 | 1013
2016-07-06 07:00 | 1124 | 1118
2016-07-06 07:30 | 1203 | 1196
2016-07-06 08:00 | 1229 | 1222
2016-07-06 08:30 | 1216 | 1210
2016-07-06 09:00 | 1179 | 1172
2016-07-06 09:30 | 1126 | 1118
2016-07-06 10:00 | 1082 | 1075
2016-07-06 10:30 | 1042 | 1033
2016-07-06 11:00 | 1006 | 995
2016-07-06 11:30 | 984 | 971
2016-07-06 12:00 | 962 | 954
2016-07-06 12:30 | 949 | 940
2016-07-06 13:00 | 934 | 928
2016-07-06 13:30 | 933 | 927
2016-07-06 14:00 | 946 | 941
2016-07-06 14:30 | 962 | 957
2016-07-06 15:00 | 1000 | 995
2016-07-06 15:30 | 1027 | 1023
2016-07-06 16:00 | 1079 | 1075
2016-07-06 16:30 | 1146 | 1142
2016-07-06 17:00 | 1228 | 1223
2016-07-06 17:30 | 1345 | 1341
2016-07-06 18:00 | 1429 | 1420
2016-07-06 18:30 | 1430 | 1416
2016-07-06 19:00 | 1443 | 1431
2016-07-06 19:30 | 1428 | 1415
2016-07-06 20:00 | 1411 | 1401
2016-07-06 20:30 | 1412 | 1401
2016-07-06 21:00 | 1354 | 1341
2016-07-06 21:30 | 1282 | 1265
2016-07-06 22:00 | 1209 | 1199
2016-07-06 22:30 | 1158 | 1145
2016-07-06 23:00 | 1115 | 1104
2016-07-06 23:30 | 1053 | 1041
2016-07-07 | 986 | 977
2016-07-07 00:30 | 923 | 914
2016-07-07 01:00 | 881 | 870
2016-07-07 01:30 | 830 | 822
2016-07-07 02:00 | 794 | 785
2016-07-07 02:30 | 766 | 755
2016-07-07 03:00 | 745 | 733
2016-07-07 03:30 | 743 | 730
2016-07-07 04:00 | 742 | 730
2016-07-07 04:30 | 757 | 746
2016-07-07 05:00 | 783 | 773
2016-07-07 05:30 | 839 | 834
2016-07-07 06:00 | 924 | 911
2016-07-07 06:30 | 1043 | 1038
2016-07-07 07:00 | 1135 | 1130
2016-07-07 07:30 | 1222 | 1218
2016-07-07 08:00 | 1240 | 1233
2016-07-07 08:30 | 1234 | 1228
2016-07-07 09:00 | 1195 | 1187
2016-07-07 09:30 | 1164 | 1154
2016-07-07 10:00 | 1118 | 1106
2016-07-07 10:30 | 1072 | 1058
2016-07-07 11:00 | 1017 | 1009
2016-07-07 11:30 | 983 | 975
2016-07-07 12:00 | 965 | 957
2016-07-07 12:30 | 951 | 949
2016-07-07 13:00 | 943 | 941
2016-07-07 13:30 | 946 | 944
2016-07-07 14:00 | 955 | 954
2016-07-07 14:30 | 969 | 967
2016-07-07 15:00 | 991 | 990
2016-07-07 15:30 | 1012 | 1011
2016-07-07 16:00 | 1059 | 1058
2016-07-07 16:30 | 1114 | 1111
2016-07-07 17:00 | 1186 | 1175
2016-07-07 17:30 | 1250 | 1244
2016-07-07 18:00 | 1277 | 1268
2016-07-07 18:30 | 1270 | 1261
2016-07-07 19:00 | 1277 | 1268
2016-07-07 19:30 | 1271 | 1260
2016-07-07 20:00 | 1261 | 1248
2016-07-07 20:30 | 1253 | 1239
2016-07-07 21:00 | 1217 | 1201
2016-07-07 21:30 | 1163 | 1146
2016-07-07 22:00 | 1103 | 1087
2016-07-07 22:30 | 1057 | 1046
2016-07-07 23:00 | 1025 | 1021
2016-07-07 23:30 | 982 | 975
2016-07-08 | 933 | 922
2016-07-08 00:30 | 869 | 855
2016-07-08 01:00 | 809 | 804
2016-07-08 01:30 | 773 | 767
2016-07-08 02:00 | 746 | 738
2016-07-08 02:30 | 725 | 715
2016-07-08 03:00 | 711 | 699
2016-07-08 03:30 | 705 | 692
2016-07-08 04:00 | 709 | 696
2016-07-08 04:30 | 723 | 710
2016-07-08 05:00 | 747 | 737
2016-07-08 05:30 | 795 | 789
2016-07-08 06:00 | 856 | 855
2016-07-08 06:30 | 956 | 955
2016-07-08 07:00 | 1034 | 1030
2016-07-08 07:30 | 1106 | 1098
2016-07-08 08:00 | 1120 | 1115
2016-07-08 08:30 | 1118 | 1113
2016-07-08 09:00 | 1084 | 1078
2016-07-08 09:30 | 1038 | 1030
2016-07-08 10:00 | 1008 | 998
2016-07-08 10:30 | 977 | 966
2016-07-08 11:00 | 940 | 931
2016-07-08 11:30 | 910 | 902
2016-07-08 12:00 | 899 | 890
2016-07-08 12:30 | 891 | 879
2016-07-08 13:00 | 850 | 843
2016-07-08 13:30 | 771 | 765
2016-07-08 14:00 | 785 | 780
2016-07-08 14:30 | 798 | 793
2016-07-08 15:00 | 812 | 806
2016-07-08 15:30 | 827 | 822
2016-07-08 16:00 | 852 | 850
2016-07-08 16:30 | 898 | 895
2016-07-08 17:00 | 936 | 934
2016-07-08 17:30 | 986 | 980
2016-07-08 18:00 | 1018 | 1012
2016-07-08 18:30 | 1019 | 1011
2016-07-08 19:00 | 1023 | 1012
2016-07-08 19:30 | 1014 | 1004
2016-07-08 20:00 | 1010 | 1002
2016-07-08 20:30 | 1011 | 1003
2016-07-08 21:00 | 989 | 978
2016-07-08 21:30 | 953 | 937
2016-07-08 22:00 | 920 | 903
2016-07-08 22:30 | 901 | 887
2016-07-08 23:00 | 882 | 873
2016-07-08 23:30 | 844 | 833
2016-07-09 | 792 | 786
2016-07-09 00:30 | 743 | 735
2016-07-09 01:00 | 708 | 697
2016-07-09 01:30 | 679 | 669
2016-07-09 02:00 | 653 | 643
2016-07-09 02:30 | 635 | 623
2016-07-09 03:00 | 625 | 612
2016-07-09 03:30 | 621 | 608
2016-07-09 04:00 | 620 | 607
2016-07-09 04:30 | 626 | 612
2016-07-09 05:00 | 631 | 620
2016-07-09 05:30 | 650 | 641
2016-07-09 06:00 | 671 | 663
2016-07-09 06:30 | 703 | 699
2016-07-09 07:00 | 738 | 734
2016-07-09 07:30 | 787 | 786
2016-07-09 08:00 | 814 | 813
2016-07-09 08:30 | 831 | 830
2016-07-09 09:00 | 825 | 824
2016-07-09 09:30 | 809 | 808
2016-07-09 10:00 | 786 | 785
2016-07-09 10:30 | 761 | 759
2016-07-09 11:00 | 735 | 733
2016-07-09 11:30 | 707 | 703
2016-07-09 12:00 | 695 | 692
2016-07-09 12:30 | 683 | 678
2016-07-09 13:00 | 679 | 674
2016-07-09 13:30 | 679 | 674
2016-07-09 14:00 | 692 | 687
2016-07-09 14:30 | 703 | 699
2016-07-09 15:00 | 722 | 718
2016-07-09 15:30 | 739 | 735
2016-07-09 16:00 | 769 | 765
2016-07-09 16:30 | 812 | 811
2016-07-09 17:00 | 864 | 864
2016-07-09 17:30 | 916 | 916
2016-07-09 18:00 | 950 | 950
2016-07-09 18:30 | 954 | 954
2016-07-09 19:00 | 957 | 957
2016-07-09 19:30 | 950 | 950
2016-07-09 20:00 | 947 | 947
2016-07-09 20:30 | 947 | 946
2016-07-09 21:00 | 927 | 926
2016-07-09 21:30 | 899 | 899
2016-07-09 22:00 | 872 | 871
2016-07-09 22:30 | 854 | 853
2016-07-09 23:00 | 843 | 842
2016-07-09 23:30 | 812 | 812
2016-07-10 | 774 | 773
2016-07-10 00:30 | 732 | 728
2016-07-10 01:00 | 703 | 698
2016-07-10 01:30 | 671 | 664
2016-07-10 02:00 | 647 | 637
2016-07-10 02:30 | 632 | 621
2016-07-10 03:00 | 619 | 606
2016-07-10 03:30 | 615 | 600
2016-07-10 04:00 | 616 | 600
2016-07-10 04:30 | 617 | 602
2016-07-10 05:00 | 618 | 603
2016-07-10 05:30 | 628 | 616
2016-07-10 06:00 | 642 | 632
2016-07-10 06:30 | 671 | 664
2016-07-10 07:00 | 698 | 691
2016-07-10 07:30 | 735 | 730
2016-07-10 08:00 | 763 | 761
2016-07-10 08:30 | 779 | 778
2016-07-10 09:00 | 781 | 780
2016-07-10 09:30 | 769 | 768
2016-07-10 10:00 | 748 | 747
2016-07-10 10:30 | 728 | 727
2016-07-10 11:00 | 712 | 711
2016-07-10 11:30 | 681 | 678
2016-07-10 12:00 | 671 | 669
2016-07-10 12:30 | 663 | 660
2016-07-10 13:00 | 655 | 652
2016-07-10 13:30 | 656 | 652
2016-07-10 14:00 | 665 | 663
2016-07-10 14:30 | 677 | 674
2016-07-10 15:00 | 697 | 695
2016-07-10 15:30 | 725 | 724
2016-07-10 16:00 | 757 | 757
2016-07-10 16:30 | 799 | 799
2016-07-10 17:00 | 853 | 853
2016-07-10 17:30 | 917 | 916
2016-07-10 18:00 | 974 | 972
2016-07-10 18:30 | 978 | 976
2016-07-10 19:00 | 981 | 979
2016-07-10 19:30 | 968 | 964
2016-07-10 20:00 | 960 | 954
2016-07-10 20:30 | 957 | 953
2016-07-10 21:00 | 920 | 915
2016-07-10 21:30 | 876 | 875
2016-07-10 22:00 | 843 | 840
2016-07-10 22:30 | 829 | 826
2016-07-10 23:00 | 817 | 813
2016-07-10 23:30 | 785 | 780
2016-07-11 | 745 | 742
2016-07-11 00:30 | 692 | 687
2016-07-11 01:00 | 676 | 669
2016-07-11 01:30 | 650 | 641
2016-07-11 02:00 | 633 | 622
2016-07-11 02:30 | 617 | 605
2016-07-11 03:00 | 612 | 598
2016-07-11 03:30 | 608 | 592
2016-07-11 04:00 | 596 | 579
2016-07-11 04:30 | 601 | 586
2016-07-11 05:00 | 645 | 635
2016-07-11 05:30 | 698 | 693
2016-07-11 06:00 | 746 | 737
2016-07-11 06:30 | 834 | 826
2016-07-11 07:00 | 908 | 900
2016-07-11 07:30 | 988 | 977
2016-07-11 08:00 | 1011 | 1004
2016-07-11 08:30 | 1012 | 1007
2016-07-11 09:00 | 984 | 978
2016-07-11 09:30 | 955 | 946
2016-07-11 10:00 | 926 | 916
2016-07-11 10:30 | 916 | 905
2016-07-11 11:00 | 899 | 887
2016-07-11 11:30 | 891 | 879
2016-07-11 12:00 | 893 | 882
2016-07-11 12:30 | 892 | 879
2016-07-11 13:00 | 887 | 874
2016-07-11 13:30 | 885 | 872
2016-07-11 14:00 | 880 | 868
2016-07-11 14:30 | 852 | 845
2016-07-11 15:00 | 862 | 855
2016-07-11 15:30 | 882 | 876
2016-07-11 16:00 | 917 | 912
2016-07-11 16:30 | 946 | 942
2016-07-11 17:00 | 1010 | 1007
2016-07-11 17:30 | 1066 | 1065
2016-07-11 18:00 | 1106 | 1103
2016-07-11 18:30 | 1099 | 1095
2016-07-11 19:00 | 1094 | 1090
2016-07-11 19:30 | 1076 | 1070
2016-07-11 20:00 | 1048 | 1045
2016-07-11 20:30 | 1030 | 1027
2016-07-11 21:00 | 980 | 978
2016-07-11 21:30 | 925 | 922
2016-07-11 22:00 | 882 | 881
2016-07-11 22:30 | 853 | 850
2016-07-11 23:00 | 834 | 828
2016-07-11 23:30 | 794 | 793
2016-07-12 | 705 | 701
2016-07-12 00:30 | 653 | 646
2016-07-12 01:00 | 662 | 654
2016-07-12 01:30 | 648 | 639
2016-07-12 02:00 | 634 | 623
2016-07-12 02:30 | 610 | 596
2016-07-12 03:00 | 619 | 604
2016-07-12 03:30 | 609 | 594
2016-07-12 04:00 | 607 | 592
2016-07-12 04:30 | 609 | 595
2016-07-12 05:00 | 634 | 623
2016-07-12 05:30 | 682 | 677
2016-07-12 06:00 | 735 | 730
2016-07-12 06:30 | 815 | 812
2016-07-12 07:00 | 894 | 890
2016-07-12 07:30 | 963 | 958
2016-07-12 08:00 | 996 | 993
2016-07-12 08:30 | 992 | 990
2016-07-12 09:00 | 976 | 973
2016-07-12 09:30 | 964 | 961
2016-07-12 10:00 | 906 | 902
2016-07-12 10:30 | 875 | 872
2016-07-12 11:00 | 868 | 864
2016-07-12 11:30 | 857 | 854
2016-07-12 12:00 | 827 | 823
2016-07-12 12:30 | 813 | 809
2016-07-12 13:00 | 792 | 790
2016-07-12 13:30 | 797 | 795
2016-07-12 14:00 | 812 | 811
2016-07-12 14:30 | 818 | 816
2016-07-12 15:00 | 820 | 818
2016-07-12 15:30 | 819 | 815
2016-07-12 16:00 | 857 | 853
2016-07-12 16:30 | 934 | 932
2016-07-12 17:00 | 989 | 988
2016-07-12 17:30 | 1042 | 1040
2016-07-12 18:00 | 1071 | 1070
2016-07-12 18:30 | 1058 | 1055
2016-07-12 19:00 | 1063 | 1059
2016-07-12 19:30 | 1049 | 1046
2016-07-12 20:00 | 1041 | 1038
2016-07-12 20:30 | 1037 | 1034
2016-07-12 21:00 | 972 | 971
2016-07-12 21:30 | 919 | 918
2016-07-12 22:00 | 883 | 882
2016-07-12 22:30 | 843 | 843
2016-07-12 23:00 | 821 | 821
2016-07-12 23:30 | 790 | 789
2016-07-13 | 751 | 749
2016-07-13 00:30 | 710 | 708
2016-07-13 01:00 | 676 | 672
2016-07-13 01:30 | 652 | 646
2016-07-13 02:00 | 627 | 618
2016-07-13 02:30 | 617 | 608
2016-07-13 03:00 | 608 | 598
2016-07-13 03:30 | 605 | 595
2016-07-13 04:00 | 604 | 595
2016-07-13 04:30 | 624 | 616
2016-07-13 05:00 | 631 | 624
2016-07-13 05:30 | 674 | 671
2016-07-13 06:00 | 733 | 726
2016-07-13 06:30 | 813 | 808
2016-07-13 07:00 | 890 | 884
2016-07-13 07:30 | 961 | 957
2016-07-13 08:00 | 999 | 994
2016-07-13 08:30 | 994 | 991
2016-07-13 09:00 | 988 | 984
2016-07-13 09:30 | 925 | 920
2016-07-13 10:00 | 886 | 879
2016-07-13 10:30 | 887 | 878
2016-07-13 11:00 | 857 | 847
2016-07-13 11:30 | 827 | 820
2016-07-13 12:00 | 832 | 826
2016-07-13 12:30 | 820 | 812
2016-07-13 13:00 | 826 | 819
2016-07-13 13:30 | 833 | 826
2016-07-13 14:00 | 843 | 836
2016-07-13 14:30 | 841 | 833
2016-07-13 15:00 | 854 | 847
2016-07-13 15:30 | 865 | 858
2016-07-13 16:00 | 894 | 888
2016-07-13 16:30 | 943 | 937
2016-07-13 17:00 | 1006 | 1001
2016-07-13 17:30 | 1079 | 1073
2016-07-13 18:00 | 1103 | 1094
2016-07-13 18:30 | 1096 | 1083
2016-07-13 19:00 | 1103 | 1089
2016-07-13 19:30 | 1086 | 1075
2016-07-13 20:00 | 1087 | 1077
2016-07-13 20:30 | 1085 | 1073
2016-07-13 21:00 | 1046 | 1033
2016-07-13 21:30 | 1007 | 990
2016-07-13 22:00 | 950 | 937
2016-07-13 22:30 | 925 | 909
2016-07-13 23:00 | 891 | 880
2016-07-13 23:30 | 841 | 830
2016-07-14 | 789 | 772
2016-07-14 00:30 | 744 | 730
2016-07-14 01:00 | 712 | 694
2016-07-14 01:30 | 685 | 663
2016-07-14 02:00 | 656 | 639
2016-07-14 02:30 | 641 | 624
2016-07-14 03:00 | 635 | 615
2016-07-14 03:30 | 634 | 615
2016-07-14 04:00 | 637 | 617
2016-07-14 04:30 | 647 | 630
2016-07-14 05:00 | 665 | 652
2016-07-14 05:30 | 707 | 700
2016-07-14 06:00 | 771 | 758
2016-07-14 06:30 | 850 | 845
2016-07-14 07:00 | 941 | 935
2016-07-14 07:30 | 1020 | 1014
2016-07-14 08:00 | 1040 | 1033
2016-07-14 08:30 | 1018 | 1011
2016-07-14 09:00 | 1124 | 1107
2016-07-14 09:30 | 1090 | 1071
2016-07-14 10:00 | 1075 | 1058
2016-07-14 10:30 | 990 | 974
2016-07-14 11:00 | 902 | 889
2016-07-14 11:30 | 903 | 890
2016-07-14 12:00 | 900 | 889
2016-07-14 12:30 | 902 | 898
2016-07-14 13:00 | 917 | 914
2016-07-14 13:30 | 916 | 913
2016-07-14 14:00 | 917 | 915
2016-07-14 14:30 | 926 | 924
2016-07-14 15:00 | 924 | 922
2016-07-14 15:30 | 937 | 935
2016-07-14 16:00 | 971 | 970
2016-07-14 16:30 | 1025 | 1023
2016-07-14 17:00 | 1088 | 1084
2016-07-14 17:30 | 1157 | 1154
2016-07-14 18:00 | 1196 | 1193
2016-07-14 18:30 | 1191 | 1188
2016-07-14 19:00 | 1198 | 1194
2016-07-14 19:30 | 1176 | 1173
2016-07-14 20:00 | 1163 | 1161
2016-07-14 20:30 | 1156 | 1155
2016-07-14 21:00 | 1113 | 1112
2016-07-14 21:30 | 1060 | 1057
2016-07-14 22:00 | 990 | 983
2016-07-14 22:30 | 938 | 932
2016-07-14 23:00 | 906 | 897
2016-07-14 23:30 | 853 | 845
2016-07-15 | 808 | 798
2016-07-15 00:30 | 756 | 740
2016-07-15 01:00 | 723 | 702
2016-07-15 01:30 | 678 | 669
2016-07-15 02:00 | 651 | 642
2016-07-15 02:30 | 639 | 628
2016-07-15 03:00 | 630 | 617
2016-07-15 03:30 | 633 | 620
2016-07-15 04:00 | 630 | 617
2016-07-15 04:30 | 644 | 634
2016-07-15 05:00 | 664 | 658
2016-07-15 05:30 | 706 | 703
2016-07-15 06:00 | 759 | 758
2016-07-15 06:30 | 851 | 847
2016-07-15 07:00 | 958 | 953
2016-07-15 07:30 | 1044 | 1042
2016-07-15 08:00 | 1089 | 1087
2016-07-15 08:30 | 1081 | 1079
2016-07-15 09:00 | 1052 | 1048
2016-07-15 09:30 | 1026 | 1020
2016-07-15 10:00 | 994 | 991
2016-07-15 10:30 | 980 | 977
2016-07-15 11:00 | 954 | 954
2016-07-15 11:30 | 938 | 935
2016-07-15 12:00 | 940 | 937
2016-07-15 12:30 | 933 | 929
2016-07-15 13:00 | 912 | 906
2016-07-15 13:30 | 901 | 896
2016-07-15 14:00 | 918 | 912
2016-07-15 14:30 | 926 | 921
2016-07-15 15:00 | 928 | 923
2016-07-15 15:30 | 930 | 924
2016-07-15 16:00 | 954 | 949
2016-07-15 16:30 | 994 | 991
2016-07-15 17:00 | 1067 | 1065
2016-07-15 17:30 | 1121 | 1118
2016-07-15 18:00 | 1147 | 1143
2016-07-15 18:30 | 1138 | 1129
2016-07-15 19:00 | 1138 | 1128
2016-07-15 19:30 | 1121 | 1109
2016-07-15 20:00 | 1099 | 1093
2016-07-15 20:30 | 1094 | 1091
2016-07-15 21:00 | 1057 | 1052
2016-07-15 21:30 | 1000 | 991
2016-07-15 22:00 | 958 | 949
2016-07-15 22:30 | 923 | 916
2016-07-15 23:00 | 901 | 896
2016-07-15 23:30 | 846 | 838
2016-07-16 | 782 | 776
2016-07-16 00:30 | 730 | 724
2016-07-16 01:00 | 685 | 681
2016-07-16 01:30 | 643 | 638
2016-07-16 02:00 | 615 | 608
2016-07-16 02:30 | 602 | 593
2016-07-16 03:00 | 591 | 580
2016-07-16 03:30 | 586 | 576
2016-07-16 04:00 | 581 | 570
2016-07-16 04:30 | 584 | 573
2016-07-16 05:00 | 587 | 577
2016-07-16 05:30 | 604 | 595
2016-07-16 06:00 | 625 | 618
2016-07-16 06:30 | 663 | 661
2016-07-16 07:00 | 699 | 697
2016-07-16 07:30 | 755 | 754
2016-07-16 08:00 | 800 | 800
2016-07-16 08:30 | 849 | 848
2016-07-16 09:00 | 881 | 881
2016-07-16 09:30 | 887 | 886
2016-07-16 10:00 | 875 | 873
2016-07-16 10:30 | 869 | 867
2016-07-16 11:00 | 871 | 868
2016-07-16 11:30 | 853 | 850
2016-07-16 12:00 | 850 | 847
2016-07-16 12:30 | 852 | 848
2016-07-16 13:00 | 862 | 859
2016-07-16 13:30 | 864 | 861
2016-07-16 14:00 | 872 | 869
2016-07-16 14:30 | 870 | 867
2016-07-16 15:00 | 873 | 870
2016-07-16 15:30 | 884 | 882
2016-07-16 16:00 | 899 | 896
2016-07-16 16:30 | 935 | 932
2016-07-16 17:00 | 988 | 986
2016-07-16 17:30 | 1027 | 1024
2016-07-16 18:00 | 1034 | 1030
2016-07-16 18:30 | 1035 | 1030
2016-07-16 19:00 | 1026 | 1020
2016-07-16 19:30 | 1007 | 999
2016-07-16 20:00 | 996 | 987
2016-07-16 20:30 | 978 | 971
2016-07-16 21:00 | 937 | 928
2016-07-16 21:30 | 908 | 896
2016-07-16 22:00 | 880 | 866
2016-07-16 22:30 | 850 | 842
2016-07-16 23:00 | 837 | 828
2016-07-16 23:30 | 803 | 795
2016-07-17 | 760 | 751
2016-07-17 00:30 | 710 | 703
2016-07-17 01:00 | 660 | 655
2016-07-17 01:30 | 629 | 622
2016-07-17 02:00 | 607 | 599
2016-07-17 02:30 | 593 | 583
2016-07-17 03:00 | 583 | 571
2016-07-17 03:30 | 580 | 568
2016-07-17 04:00 | 571 | 558
2016-07-17 04:30 | 570 | 555
2016-07-17 05:00 | 571 | 557
2016-07-17 05:30 | 578 | 565
2016-07-17 06:00 | 595 | 584
2016-07-17 06:30 | 618 | 610
2016-07-17 07:00 | 645 | 638
2016-07-17 07:30 | 677 | 673
2016-07-17 08:00 | 717 | 715
2016-07-17 08:30 | 767 | 767
2016-07-17 09:00 | 793 | 791
2016-07-17 09:30 | 804 | 803
2016-07-17 10:00 | 816 | 816
2016-07-17 10:30 | 819 | 819
2016-07-17 11:00 | 806 | 805
2016-07-17 11:30 | 768 | 767
2016-07-17 12:00 | 751 | 749
2016-07-17 12:30 | 738 | 736
2016-07-17 13:00 | 730 | 727
2016-07-17 13:30 | 729 | 726
2016-07-17 14:00 | 730 | 726
2016-07-17 14:30 | 742 | 738
2016-07-17 15:00 | 756 | 754
2016-07-17 15:30 | 758 | 756
2016-07-17 16:00 | 773 | 771
2016-07-17 16:30 | 802 | 801
2016-07-17 17:00 | 848 | 846
2016-07-17 17:30 | 909 | 908
2016-07-17 18:00 | 954 | 952
2016-07-17 18:30 | 968 | 964
2016-07-17 19:00 | 963 | 959
2016-07-17 19:30 | 946 | 940
2016-07-17 20:00 | 932 | 930
2016-07-17 20:30 | 932 | 929
2016-07-17 21:00 | 895 | 892
2016-07-17 21:30 | 858 | 854
2016-07-17 22:00 | 825 | 821
2016-07-17 22:30 | 800 | 794
2016-07-17 23:00 | 787 | 781
2016-07-17 23:30 | 740 | 737
2016-07-18 | 699 | 695
2016-07-18 00:30 | 658 | 653
2016-07-18 01:00 | 627 | 619
2016-07-18 01:30 | 605 | 596
2016-07-18 02:00 | 582 | 569
2016-07-18 02:30 | 573 | 558
2016-07-18 03:00 | 566 | 550
2016-07-18 03:30 | 543 | 524
2016-07-18 04:00 | 535 | 518
2016-07-18 04:30 | 570 | 555
2016-07-18 05:00 | 586 | 575
2016-07-18 05:30 | 618 | 611
2016-07-18 06:00 | 691 | 686
2016-07-18 06:30 | 771 | 768
2016-07-18 07:00 | 859 | 856
2016-07-18 07:30 | 918 | 917
2016-07-18 08:00 | 930 | 929
2016-07-18 08:30 | 907 | 906
2016-07-18 09:00 | 880 | 879
2016-07-18 09:30 | 851 | 850
2016-07-18 10:00 | 822 | 820
2016-07-18 10:30 | 836 | 834
2016-07-18 11:00 | 817 | 815
2016-07-18 11:30 | 804 | 802
2016-07-18 12:00 | 817 | 816
2016-07-18 12:30 | 823 | 821
2016-07-18 13:00 | 819 | 817
2016-07-18 13:30 | 814 | 812
2016-07-18 14:00 | 817 | 815
2016-07-18 14:30 | 820 | 818
2016-07-18 15:00 | 821 | 819
2016-07-18 15:30 | 841 | 838
2016-07-18 16:00 | 875 | 873
2016-07-18 16:30 | 901 | 900
2016-07-18 17:00 | 941 | 941
2016-07-18 17:30 | 982 | 981
2016-07-18 18:00 | 1036 | 1036
2016-07-18 18:30 | 1025 | 1022
2016-07-18 19:00 | 1021 | 1018
2016-07-18 19:30 | 990 | 983
2016-07-18 20:00 | 981 | 971
2016-07-18 20:30 | 992 | 981
2016-07-18 21:00 | 938 | 933
2016-07-18 21:30 | 897 | 887
2016-07-18 22:00 | 846 | 835
2016-07-18 22:30 | 807 | 803
2016-07-18 23:00 | 789 | 784
2016-07-18 23:30 | 750 | 745
2016-07-19 | 696 | 690
2016-07-19 00:30 | 631 | 629
2016-07-19 01:00 | 616 | 612
2016-07-19 01:30 | 589 | 582
2016-07-19 02:00 | 563 | 553
2016-07-19 02:30 | 545 | 534
2016-07-19 03:00 | 526 | 514
2016-07-19 03:30 | 525 | 511
2016-07-19 04:00 | 529 | 516
2016-07-19 04:30 | 544 | 533
2016-07-19 05:00 | 570 | 562
2016-07-19 05:30 | 625 | 622
2016-07-19 06:00 | 682 | 671
2016-07-19 06:30 | 787 | 780
2016-07-19 07:00 | 865 | 862
2016-07-19 07:30 | 946 | 942
2016-07-19 08:00 | 954 | 951
2016-07-19 08:30 | 910 | 907
2016-07-19 09:00 | 853 | 849
2016-07-19 09:30 | 798 | 794
2016-07-19 10:00 | 787 | 786
2016-07-19 10:30 | 778 | 777
2016-07-19 11:00 | 788 | 786
2016-07-19 11:30 | 775 | 773
2016-07-19 12:00 | 765 | 764
2016-07-19 12:30 | 774 | 770
2016-07-19 13:00 | 771 | 766
2016-07-19 13:30 | 782 | 777
2016-07-19 14:00 | 796 | 791
2016-07-19 14:30 | 813 | 805
2016-07-19 15:00 | 827 | 819
2016-07-19 15:30 | 852 | 845
2016-07-19 16:00 | 886 | 879
2016-07-19 16:30 | 925 | 919
2016-07-19 17:00 | 962 | 957
2016-07-19 17:30 | 987 | 985
2016-07-19 18:00 | 1045 | 1039
2016-07-19 18:30 | 1034 | 1024
2016-07-19 19:00 | 1029 | 1018
2016-07-19 19:30 | 988 | 981
2016-07-19 20:00 | 979 | 973
2016-07-19 20:30 | 990 | 985
2016-07-19 21:00 | 942 | 939
2016-07-19 21:30 | 903 | 898
2016-07-19 22:00 | 864 | 863
2016-07-19 22:30 | 838 | 836
2016-07-19 23:00 | 809 | 808
2016-07-19 23:30 | 767 | 765
2016-07-20 | 711 | 707
2016-07-20 00:30 | 675 | 670
2016-07-20 01:00 | 648 | 643
2016-07-20 01:30 | 620 | 612
2016-07-20 02:00 | 585 | 575
2016-07-20 02:30 | 571 | 559
2016-07-20 03:00 | 561 | 548
2016-07-20 03:30 | 556 | 543
2016-07-20 04:00 | 553 | 540
2016-07-20 04:30 | 563 | 552
2016-07-20 05:00 | 581 | 574
2016-07-20 05:30 | 637 | 634
2016-07-20 06:00 | 683 | 677
2016-07-20 06:30 | 782 | 777
2016-07-20 07:00 | 855 | 845
2016-07-20 07:30 | 913 | 906
2016-07-20 08:00 | 904 | 900
2016-07-20 08:30 | 872 | 868
2016-07-20 09:00 | 833 | 829
2016-07-20 09:30 | 802 | 796
2016-07-20 10:00 | 777 | 770
2016-07-20 10:30 | 768 | 762
2016-07-20 11:00 | 749 | 744
2016-07-20 11:30 | 764 | 760
2016-07-20 12:00 | 775 | 771
2016-07-20 12:30 | 776 | 772
2016-07-20 13:00 | 791 | 788
2016-07-20 13:30 | 795 | 793
2016-07-20 14:00 | 796 | 794
2016-07-20 14:30 | 801 | 798
2016-07-20 15:00 | 813 | 810
2016-07-20 15:30 | 831 | 828
2016-07-20 16:00 | 880 | 878
2016-07-20 16:30 | 918 | 916
2016-07-20 17:00 | 952 | 948
2016-07-20 17:30 | 975 | 971
2016-07-20 18:00 | 1004 | 999
2016-07-20 18:30 | 995 | 986
2016-07-20 19:00 | 992 | 981
2016-07-20 19:30 | 971 | 960
2016-07-20 20:00 | 953 | 945
2016-07-20 20:30 | 969 | 965
2016-07-20 21:00 | 926 | 920
2016-07-20 21:30 | 897 | 887
2016-07-20 22:00 | 844 | 838
2016-07-20 22:30 | 821 | 813
2016-07-20 23:00 | 809 | 800
2016-07-20 23:30 | 769 | 760
2016-07-21 | 721 | 708
2016-07-21 00:30 | 657 | 649
2016-07-21 01:00 | 634 | 628
2016-07-21 01:30 | 620 | 612
2016-07-21 02:00 | 603 | 593
2016-07-21 02:30 | 589 | 577
2016-07-21 03:00 | 584 | 572
2016-07-21 03:30 | 586 | 573
2016-07-21 04:00 | 600 | 588
2016-07-21 04:30 | 615 | 605
2016-07-21 05:00 | 634 | 625
2016-07-21 05:30 | 669 | 663
2016-07-21 06:00 | 710 | 700
2016-07-21 06:30 | 789 | 780
2016-07-21 07:00 | 859 | 851
2016-07-21 07:30 | 933 | 927
2016-07-21 08:00 | 930 | 921
2016-07-21 08:30 | 914 | 907
2016-07-21 09:00 | 903 | 896
2016-07-21 09:30 | 878 | 871
2016-07-21 10:00 | 848 | 842
2016-07-21 10:30 | 821 | 814
2016-07-21 11:00 | 805 | 797
2016-07-21 11:30 | 797 | 788
2016-07-21 12:00 | 803 | 796
2016-07-21 12:30 | 794 | 785
2016-07-21 13:00 | 798 | 790
2016-07-21 13:30 | 812 | 805
2016-07-21 14:00 | 826 | 819
2016-07-21 14:30 | 859 | 854
2016-07-21 15:00 | 877 | 873
2016-07-21 15:30 | 895 | 890
2016-07-21 16:00 | 921 | 908
2016-07-21 16:30 | 952 | 939
2016-07-21 17:00 | 978 | 966
2016-07-21 17:30 | 1006 | 996
2016-07-21 18:00 | 1001 | 996
2016-07-21 18:30 | 989 | 983
2016-07-21 19:00 | 994 | 987
2016-07-21 19:30 | 972 | 967
2016-07-21 20:00 | 952 | 951
2016-07-21 20:30 | 941 | 940
2016-07-21 21:00 | 892 | 889
2016-07-21 21:30 | 843 | 840
2016-07-21 22:00 | 803 | 798
2016-07-21 22:30 | 777 | 775
2016-07-21 23:00 | 766 | 765
2016-07-21 23:30 | 731 | 729
2016-07-22 | 684 | 681
2016-07-22 00:30 | 630 | 626
2016-07-22 01:00 | 596 | 590
2016-07-22 01:30 | 563 | 555
2016-07-22 02:00 | 537 | 526
2016-07-22 02:30 | 522 | 509
2016-07-22 03:00 | 520 | 506
2016-07-22 03:30 | 529 | 514
2016-07-22 04:00 | 534 | 518
2016-07-22 04:30 | 543 | 529
2016-07-22 05:00 | 564 | 555
2016-07-22 05:30 | 604 | 599
2016-07-22 06:00 | 664 | 660
2016-07-22 06:30 | 750 | 741
2016-07-22 07:00 | 815 | 811
2016-07-22 07:30 | 879 | 875
2016-07-22 08:00 | 890 | 886
2016-07-22 08:30 | 866 | 862
2016-07-22 09:00 | 844 | 841
2016-07-22 09:30 | 828 | 824
2016-07-22 10:00 | 807 | 804
2016-07-22 10:30 | 798 | 794
2016-07-22 11:00 | 787 | 784
2016-07-22 11:30 | 776 | 773
2016-07-22 12:00 | 781 | 779
2016-07-22 12:30 | 774 | 772
2016-07-22 13:00 | 776 | 774
2016-07-22 13:30 | 777 | 776
2016-07-22 14:00 | 811 | 810
2016-07-22 14:30 | 832 | 829
2016-07-22 15:00 | 847 | 843
2016-07-22 15:30 | 864 | 859
2016-07-22 16:00 | 890 | 885
2016-07-22 16:30 | 915 | 911
2016-07-22 17:00 | 940 | 935
2016-07-22 17:30 | 945 | 939
2016-07-22 18:00 | 958 | 954
2016-07-22 18:30 | 962 | 956
2016-07-22 19:00 | 964 | 957
2016-07-22 19:30 | 944 | 937
2016-07-22 20:00 | 925 | 921
2016-07-22 20:30 | 919 | 914
2016-07-22 21:00 | 880 | 876
2016-07-22 21:30 | 842 | 836
2016-07-22 22:00 | 804 | 800
2016-07-22 22:30 | 791 | 790
2016-07-22 23:00 | 787 | 786
2016-07-22 23:30 | 756 | 754
2016-07-23 | 701 | 699
2016-07-23 00:30 | 655 | 650
2016-07-23 01:00 | 618 | 611
2016-07-23 01:30 | 587 | 579
2016-07-23 02:00 | 562 | 550
2016-07-23 02:30 | 544 | 529
2016-07-23 03:00 | 539 | 523
2016-07-23 03:30 | 551 | 535
2016-07-23 04:00 | 556 | 541
2016-07-23 04:30 | 558 | 543
2016-07-23 05:00 | 555 | 541
2016-07-23 05:30 | 560 | 549
2016-07-23 06:00 | 575 | 566
2016-07-23 06:30 | 598 | 591
2016-07-23 07:00 | 623 | 617
2016-07-23 07:30 | 674 | 671
2016-07-23 08:00 | 694 | 693
2016-07-23 08:30 | 722 | 722
2016-07-23 09:00 | 743 | 743
2016-07-23 09:30 | 741 | 741
2016-07-23 10:00 | 726 | 726
2016-07-23 10:30 | 722 | 722
2016-07-23 11:00 | 724 | 724
2016-07-23 11:30 | 704 | 704
2016-07-23 12:00 | 688 | 688
2016-07-23 12:30 | 682 | 682
2016-07-23 13:00 | 668 | 668
2016-07-23 13:30 | 670 | 670
2016-07-23 14:00 | 670 | 670
2016-07-23 14:30 | 678 | 678
2016-07-23 15:00 | 705 | 705
2016-07-23 15:30 | 731 | 731
2016-07-23 16:00 | 751 | 751
2016-07-23 16:30 | 782 | 781
2016-07-23 17:00 | 813 | 813
2016-07-23 17:30 | 831 | 831
2016-07-23 18:00 | 840 | 840
2016-07-23 18:30 | 840 | 839
2016-07-23 19:00 | 839 | 837
2016-07-23 19:30 | 811 | 808
2016-07-23 20:00 | 800 | 798
2016-07-23 20:30 | 783 | 781
2016-07-23 21:00 | 755 | 751
2016-07-23 21:30 | 740 | 735
2016-07-23 22:00 | 719 | 716
2016-07-23 22:30 | 713 | 710
2016-07-23 23:00 | 712 | 709
2016-07-23 23:30 | 685 | 684
2016-07-24 | 651 | 647
2016-07-24 00:30 | 602 | 596
2016-07-24 01:00 | 586 | 576
2016-07-24 01:30 | 554 | 542
2016-07-24 02:00 | 523 | 508
2016-07-24 02:30 | 501 | 484
2016-07-24 03:00 | 498 | 478
2016-07-24 03:30 | 506 | 487
2016-07-24 04:00 | 509 | 489
2016-07-24 04:30 | 508 | 486
2016-07-24 05:00 | 504 | 482
2016-07-24 05:30 | 512 | 492
2016-07-24 06:00 | 526 | 510
2016-07-24 06:30 | 534 | 519
2016-07-24 07:00 | 554 | 541
2016-07-24 07:30 | 586 | 577
2016-07-24 08:00 | 595 | 589
2016-07-24 08:30 | 603 | 599
2016-07-24 09:00 | 611 | 608
2016-07-24 09:30 | 604 | 602
2016-07-24 10:00 | 598 | 596
2016-07-24 10:30 | 584 | 582
2016-07-24 11:00 | 572 | 570
2016-07-24 11:30 | 556 | 554
2016-07-24 12:00 | 543 | 542
2016-07-24 12:30 | 538 | 536
2016-07-24 13:00 | 542 | 540
2016-07-24 13:30 | 544 | 542
2016-07-24 14:00 | 550 | 547
2016-07-24 14:30 | 561 | 559
2016-07-24 15:00 | 583 | 581
2016-07-24 15:30 | 623 | 622
2016-07-24 16:00 | 667 | 667
2016-07-24 16:30 | 703 | 703
2016-07-24 17:00 | 750 | 749
2016-07-24 17:30 | 795 | 793
2016-07-24 18:00 | 842 | 842
2016-07-24 18:30 | 858 | 857
2016-07-24 19:00 | 855 | 855
2016-07-24 19:30 | 832 | 830
2016-07-24 20:00 | 824 | 822
2016-07-24 20:30 | 821 | 820
2016-07-24 21:00 | 790 | 788
2016-07-24 21:30 | 752 | 751
2016-07-24 22:00 | 730 | 728
2016-07-24 22:30 | 730 | 727
2016-07-24 23:00 | 729 | 725
2016-07-24 23:30 | 695 | 693
2016-07-25 | 656 | 651
2016-07-25 00:30 | 617 | 608
2016-07-25 01:00 | 584 | 575
2016-07-25 01:30 | 556 | 545
2016-07-25 02:00 | 531 | 518
2016-07-25 02:30 | 517 | 500
2016-07-25 03:00 | 510 | 492
2016-07-25 03:30 | 522 | 504
2016-07-25 04:00 | 523 | 505
2016-07-25 04:30 | 534 | 519
2016-07-25 05:00 | 548 | 537
2016-07-25 05:30 | 592 | 586
2016-07-25 06:00 | 656 | 654
2016-07-25 06:30 | 745 | 743
2016-07-25 07:00 | 813 | 808
2016-07-25 07:30 | 888 | 886
2016-07-25 08:00 | 880 | 879
2016-07-25 08:30 | 838 | 837
2016-07-25 09:00 | 796 | 794
2016-07-25 09:30 | 766 | 764
2016-07-25 10:00 | 749 | 748
2016-07-25 10:30 | 726 | 726
2016-07-25 11:00 | 707 | 707
2016-07-25 11:30 | 688 | 688
2016-07-25 12:00 | 683 | 682
2016-07-25 12:30 | 679 | 679
2016-07-25 13:00 | 680 | 680
2016-07-25 13:30 | 719 | 719
2016-07-25 14:00 | 727 | 727
2016-07-25 14:30 | 734 | 734
2016-07-25 15:00 | 745 | 745
2016-07-25 15:30 | 776 | 776
2016-07-25 16:00 | 812 | 812
2016-07-25 16:30 | 860 | 860
2016-07-25 17:00 | 909 | 908
2016-07-25 17:30 | 951 | 951
2016-07-25 18:00 | 1009 | 1009
2016-07-25 18:30 | 1004 | 1002
2016-07-25 19:00 | 1002 | 1000
2016-07-25 19:30 | 971 | 968
2016-07-25 20:00 | 963 | 961
2016-07-25 20:30 | 953 | 952
2016-07-25 21:00 | 909 | 907
2016-07-25 21:30 | 870 | 869
2016-07-25 22:00 | 829 | 826
2016-07-25 22:30 | 794 | 792
2016-07-25 23:00 | 773 | 770
2016-07-25 23:30 | 736 | 732
2016-07-26 | 693 | 684
2016-07-26 00:30 | 643 | 634
2016-07-26 01:00 | 609 | 600
2016-07-26 01:30 | 577 | 566
2016-07-26 02:00 | 548 | 534
2016-07-26 02:30 | 533 | 517
2016-07-26 03:00 | 525 | 508
2016-07-26 03:30 | 529 | 511
2016-07-26 04:00 | 532 | 514
2016-07-26 04:30 | 546 | 530
2016-07-26 05:00 | 564 | 552
2016-07-26 05:30 | 613 | 608
2016-07-26 06:00 | 675 | 669
2016-07-26 06:30 | 768 | 765
2016-07-26 07:00 | 858 | 857
2016-07-26 07:30 | 929 | 927
2016-07-26 08:00 | 949 | 944
2016-07-26 08:30 | 920 | 915
2016-07-26 09:00 | 862 | 855
2016-07-26 09:30 | 840 | 831
2016-07-26 10:00 | 820 | 811
2016-07-26 10:30 | 824 | 820
2016-07-26 11:00 | 798 | 794
2016-07-26 11:30 | 759 | 750
2016-07-26 12:00 | 711 | 709
2016-07-26 12:30 | 727 | 726
2016-07-26 13:00 | 745 | 744
2016-07-26 13:30 | 762 | 759
2016-07-26 14:00 | 754 | 751
2016-07-26 14:30 | 764 | 761
2016-07-26 15:00 | 790 | 787
2016-07-26 15:30 | 811 | 809
2016-07-26 16:00 | 843 | 841
2016-07-26 16:30 | 892 | 892
2016-07-26 17:00 | 955 | 953
2016-07-26 17:30 | 1014 | 1012
2016-07-26 18:00 | 1057 | 1056
2016-07-26 18:30 | 1056 | 1052
2016-07-26 19:00 | 1054 | 1050
2016-07-26 19:30 | 1032 | 1024
2016-07-26 20:00 | 1009 | 1002
2016-07-26 20:30 | 998 | 994
2016-07-26 21:00 | 944 | 940
2016-07-26 21:30 | 904 | 896
2016-07-26 22:00 | 852 | 846
2016-07-26 22:30 | 830 | 824
2016-07-26 23:00 | 803 | 796
2016-07-26 23:30 | 750 | 745
2016-07-27 | 700 | 693
2016-07-27 00:30 | 649 | 643
2016-07-27 01:00 | 611 | 603
2016-07-27 01:30 | 577 | 565
2016-07-27 02:00 | 546 | 531
2016-07-27 02:30 | 530 | 515
2016-07-27 03:00 | 527 | 510
2016-07-27 03:30 | 528 | 509
2016-07-27 04:00 | 530 | 512
2016-07-27 04:30 | 543 | 527
2016-07-27 05:00 | 561 | 549
2016-07-27 05:30 | 616 | 608
2016-07-27 06:00 | 697 | 676
2016-07-27 06:30 | 778 | 770
2016-07-27 07:00 | 857 | 852
2016-07-27 07:30 | 946 | 943
2016-07-27 08:00 | 972 | 966
2016-07-27 08:30 | 961 | 956
2016-07-27 09:00 | 927 | 922
2016-07-27 09:30 | 912 | 906
2016-07-27 10:00 | 893 | 888
2016-07-27 10:30 | 885 | 881
2016-07-27 11:00 | 904 | 900
2016-07-27 11:30 | 897 | 893
2016-07-27 12:00 | 851 | 845
2016-07-27 12:30 | 834 | 831
2016-07-27 13:00 | 832 | 831
2016-07-27 13:30 | 839 | 838
2016-07-27 14:00 | 836 | 835
2016-07-27 14:30 | 813 | 812
2016-07-27 15:00 | 793 | 792
2016-07-27 15:30 | 796 | 796
2016-07-27 16:00 | 832 | 831
2016-07-27 16:30 | 869 | 868
2016-07-27 17:00 | 917 | 917
2016-07-27 17:30 | 975 | 975
2016-07-27 18:00 | 1036 | 1036
2016-07-27 18:30 | 1041 | 1039
2016-07-27 19:00 | 1055 | 1053
2016-07-27 19:30 | 1057 | 1054
2016-07-27 20:00 | 1052 | 1048
2016-07-27 20:30 | 1059 | 1055
2016-07-27 21:00 | 1015 | 1013
2016-07-27 21:30 | 965 | 959
2016-07-27 22:00 | 915 | 906
2016-07-27 22:30 | 871 | 865
2016-07-27 23:00 | 831 | 830
2016-07-27 23:30 | 787 | 785
2016-07-28 | 731 | 725
2016-07-28 00:30 | 681 | 671
2016-07-28 01:00 | 634 | 626
2016-07-28 01:30 | 597 | 590
2016-07-28 02:00 | 566 | 557
2016-07-28 02:30 | 544 | 533
2016-07-28 03:00 | 534 | 522
2016-07-28 03:30 | 531 | 519
2016-07-28 04:00 | 532 | 520
2016-07-28 04:30 | 563 | 553
2016-07-28 05:00 | 588 | 582
2016-07-28 05:30 | 658 | 652
2016-07-28 06:00 | 731 | 722
2016-07-28 06:30 | 851 | 846
2016-07-28 07:00 | 957 | 956
2016-07-28 07:30 | 1028 | 1028
2016-07-28 08:00 | 1014 | 1012
2016-07-28 08:30 | 950 | 947
2016-07-28 09:00 | 857 | 850
2016-07-28 09:30 | 811 | 804
2016-07-28 10:00 | 761 | 758
2016-07-28 10:30 | 734 | 729
2016-07-28 11:00 | 706 | 703
2016-07-28 11:30 | 697 | 695
2016-07-28 12:00 | 684 | 683
2016-07-28 12:30 | 677 | 675
2016-07-28 13:00 | 670 | 668
2016-07-28 13:30 | 650 | 648
2016-07-28 14:00 | 663 | 662
2016-07-28 14:30 | 683 | 681
2016-07-28 15:00 | 736 | 735
2016-07-28 15:30 | 771 | 770
2016-07-28 16:00 | 804 | 803
2016-07-28 16:30 | 853 | 853
2016-07-28 17:00 | 899 | 898
2016-07-28 17:30 | 948 | 947
2016-07-28 18:00 | 1012 | 1011
2016-07-28 18:30 | 1036 | 1034
2016-07-28 19:00 | 1047 | 1045
2016-07-28 19:30 | 1035 | 1031
2016-07-28 20:00 | 1031 | 1031
2016-07-28 20:30 | 1032 | 1032
2016-07-28 21:00 | 989 | 987
2016-07-28 21:30 | 931 | 929
2016-07-28 22:00 | 882 | 877
2016-07-28 22:30 | 909 | 907
2016-07-28 23:00 | 856 | 851
2016-07-28 23:30 | 771 | 765
2016-07-29 | 705 | 700
2016-07-29 00:30 | 650 | 646
2016-07-29 01:00 | 619 | 614
2016-07-29 01:30 | 589 | 582
2016-07-29 02:00 | 560 | 551
2016-07-29 02:30 | 544 | 534
2016-07-29 03:00 | 539 | 528
2016-07-29 03:30 | 539 | 527
2016-07-29 04:00 | 545 | 535
2016-07-29 04:30 | 561 | 552
2016-07-29 05:00 | 581 | 575
2016-07-29 05:30 | 636 | 635
2016-07-29 06:00 | 708 | 708
2016-07-29 06:30 | 821 | 820
2016-07-29 07:00 | 929 | 929
2016-07-29 07:30 | 984 | 983
2016-07-29 08:00 | 966 | 965
2016-07-29 08:30 | 909 | 908
2016-07-29 09:00 | 840 | 836
2016-07-29 09:30 | 773 | 770
2016-07-29 10:00 | 733 | 733
2016-07-29 10:30 | 718 | 718
2016-07-29 11:00 | 706 | 705
2016-07-29 11:30 | 690 | 688
2016-07-29 12:00 | 686 | 685
2016-07-29 12:30 | 680 | 679
2016-07-29 13:00 | 682 | 681
2016-07-29 13:30 | 682 | 681
2016-07-29 14:00 | 699 | 698
2016-07-29 14:30 | 713 | 712
2016-07-29 15:00 | 731 | 729
2016-07-29 15:30 | 751 | 749
2016-07-29 16:00 | 788 | 786
2016-07-29 16:30 | 828 | 826
2016-07-29 17:00 | 874 | 872
2016-07-29 17:30 | 894 | 892
2016-07-29 18:00 | 917 | 917
2016-07-29 18:30 | 907 | 907
2016-07-29 19:00 | 923 | 923
2016-07-29 19:30 | 911 | 911
2016-07-29 20:00 | 908 | 908
2016-07-29 20:30 | 919 | 918
2016-07-29 21:00 | 885 | 885
2016-07-29 21:30 | 862 | 861
2016-07-29 22:00 | 830 | 830
2016-07-29 22:30 | 863 | 862
2016-07-29 23:00 | 816 | 815
2016-07-29 23:30 | 741 | 741
2016-07-30 | 689 | 689
2016-07-30 00:30 | 651 | 649
2016-07-30 01:00 | 632 | 629
2016-07-30 01:30 | 605 | 600
2016-07-30 02:00 | 583 | 577
2016-07-30 02:30 | 566 | 558
2016-07-30 03:00 | 558 | 549
2016-07-30 03:30 | 556 | 546
2016-07-30 04:00 | 551 | 542
2016-07-30 04:30 | 553 | 544
2016-07-30 05:00 | 560 | 552
2016-07-30 05:30 | 583 | 578
2016-07-30 06:00 | 613 | 609
2016-07-30 06:30 | 661 | 659
2016-07-30 07:00 | 715 | 713
2016-07-30 07:30 | 757 | 756
2016-07-30 08:00 | 773 | 771
2016-07-30 08:30 | 777 | 776
2016-07-30 09:00 | 759 | 758
2016-07-30 09:30 | 735 | 734
2016-07-30 10:00 | 691 | 690
2016-07-30 10:30 | 658 | 658
2016-07-30 11:00 | 629 | 629
2016-07-30 11:30 | 615 | 614
2016-07-30 12:00 | 589 | 589
2016-07-30 12:30 | 572 | 571
2016-07-30 13:00 | 572 | 570
2016-07-30 13:30 | 588 | 587
2016-07-30 14:00 | 601 | 600
2016-07-30 14:30 | 608 | 607
2016-07-30 15:00 | 625 | 624
2016-07-30 15:30 | 655 | 655
2016-07-30 16:00 | 687 | 687
2016-07-30 16:30 | 731 | 729
2016-07-30 17:00 | 782 | 780
2016-07-30 17:30 | 828 | 823
2016-07-30 18:00 | 864 | 860
2016-07-30 18:30 | 872 | 870
2016-07-30 19:00 | 882 | 880
2016-07-30 19:30 | 878 | 875
2016-07-30 20:00 | 868 | 864
2016-07-30 20:30 | 877 | 873
2016-07-30 21:00 | 861 | 854
2016-07-30 21:30 | 825 | 821
2016-07-30 22:00 | 811 | 809
2016-07-30 22:30 | 820 | 817
2016-07-30 23:00 | 780 | 776
2016-07-30 23:30 | 711 | 709
2016-07-31 | 673 | 669
2016-07-31 00:30 | 646 | 641
2016-07-31 01:00 | 627 | 620
2016-07-31 01:30 | 601 | 592
2016-07-31 02:00 | 569 | 557
2016-07-31 02:30 | 550 | 536
2016-07-31 03:00 | 547 | 532
2016-07-31 03:30 | 547 | 531
2016-07-31 04:00 | 539 | 522
2016-07-31 04:30 | 539 | 522
2016-07-31 05:00 | 542 | 526
2016-07-31 05:30 | 553 | 539
2016-07-31 06:00 | 570 | 558
2016-07-31 06:30 | 594 | 585
2016-07-31 07:00 | 623 | 616
2016-07-31 07:30 | 665 | 660
2016-07-31 08:00 | 681 | 678
2016-07-31 08:30 | 681 | 680
2016-07-31 09:00 | 676 | 675
2016-07-31 09:30 | 657 | 656
2016-07-31 10:00 | 638 | 636
2016-07-31 10:30 | 618 | 612
2016-07-31 11:00 | 593 | 585
2016-07-31 11:30 | 591 | 582
2016-07-31 12:00 | 586 | 576
2016-07-31 12:30 | 582 | 571
2016-07-31 13:00 | 568 | 562
2016-07-31 13:30 | 568 | 565
2016-07-31 14:00 | 577 | 574
2016-07-31 14:30 | 596 | 593
2016-07-31 15:00 | 621 | 620
2016-07-31 15:30 | 663 | 662
2016-07-31 16:00 | 694 | 693
2016-07-31 16:30 | 728 | 728
2016-07-31 17:00 | 776 | 776
2016-07-31 17:30 | 828 | 828
2016-07-31 18:00 | 891 | 890
2016-07-31 18:30 | 912 | 911
2016-07-31 19:00 | 922 | 921
2016-07-31 19:30 | 897 | 895
2016-07-31 20:00 | 896 | 894
2016-07-31 20:30 | 903 | 900
2016-07-31 21:00 | 866 | 864
2016-07-31 21:30 | 823 | 822
2016-07-31 22:00 | 794 | 792
2016-07-31 22:30 | 834 | 833
2016-07-31 23:00 | 804 | 801
2016-07-31 23:30 | 735 | 729
2016-08-01 | 677 | 672
2016-08-01 00:30 | 651 | 643
2016-08-01 01:00 | 634 | 624
2016-08-01 01:30 | 609 | 598
2016-08-01 02:00 | 585 | 573
2016-08-01 02:30 | 570 | 555
2016-08-01 03:00 | 566 | 551
2016-08-01 03:30 | 578 | 563
2016-08-01 04:00 | 581 | 566
2016-08-01 04:30 | 584 | 571
2016-08-01 05:00 | 607 | 598
2016-08-01 05:30 | 651 | 646
2016-08-01 06:00 | 720 | 717
2016-08-01 06:30 | 836 | 832
2016-08-01 07:00 | 909 | 906
2016-08-01 07:30 | 967 | 963
2016-08-01 08:00 | 960 | 956
2016-08-01 08:30 | 908 | 903
2016-08-01 09:00 | 838 | 831
2016-08-01 09:30 | 775 | 767
2016-08-01 10:00 | 738 | 733
2016-08-01 10:30 | 706 | 704
2016-08-01 11:00 | 702 | 702
2016-08-01 11:30 | 690 | 690
2016-08-01 12:00 | 685 | 685
2016-08-01 12:30 | 677 | 677
2016-08-01 13:00 | 681 | 681
2016-08-01 13:30 | 691 | 691
2016-08-01 14:00 | 713 | 713
2016-08-01 14:30 | 728 | 728
2016-08-01 15:00 | 750 | 750
2016-08-01 15:30 | 775 | 775
2016-08-01 16:00 | 809 | 809
2016-08-01 16:30 | 856 | 856
2016-08-01 17:00 | 911 | 911
2016-08-01 17:30 | 965 | 965
2016-08-01 18:00 | 1055 | 1054
2016-08-01 18:30 | 1059 | 1057
2016-08-01 19:00 | 1032 | 1029
2016-08-01 19:30 | 985 | 980
2016-08-01 20:00 | 935 | 935
2016-08-01 20:30 | 907 | 906
2016-08-01 21:00 | 890 | 889
2016-08-01 21:30 | 866 | 864
2016-08-01 22:00 | 823 | 819
2016-08-01 22:30 | 859 | 855
2016-08-01 23:00 | 814 | 810
2016-08-01 23:30 | 733 | 732
2016-08-02 | 680 | 679
2016-08-02 00:30 | 641 | 637
2016-08-02 01:00 | 606 | 600
2016-08-02 01:30 | 572 | 565
2016-08-02 02:00 | 551 | 539
2016-08-02 02:30 | 534 | 521
2016-08-02 03:00 | 531 | 517
2016-08-02 03:30 | 527 | 514
2016-08-02 04:00 | 531 | 518
2016-08-02 04:30 | 532 | 520
2016-08-02 05:00 | 544 | 535
2016-08-02 05:30 | 609 | 603
2016-08-02 06:00 | 676 | 671
2016-08-02 06:30 | 773 | 772
2016-08-02 07:00 | 854 | 854
2016-08-02 07:30 | 922 | 922
2016-08-02 08:00 | 949 | 947
2016-08-02 08:30 | 932 | 929
2016-08-02 09:00 | 903 | 899
2016-08-02 09:30 | 853 | 846
2016-08-02 10:00 | 803 | 802
2016-08-02 10:30 | 780 | 779
2016-08-02 11:00 | 762 | 762
2016-08-02 11:30 | 775 | 775
2016-08-02 12:00 | 793 | 793
2016-08-02 12:30 | 811 | 811
2016-08-02 13:00 | 822 | 822
2016-08-02 13:30 | 830 | 829
2016-08-02 14:00 | 835 | 835
2016-08-02 14:30 | 832 | 832
2016-08-02 15:00 | 827 | 827
2016-08-02 15:30 | 822 | 822
2016-08-02 16:00 | 838 | 838
2016-08-02 16:30 | 880 | 879
2016-08-02 17:00 | 925 | 924
2016-08-02 17:30 | 961 | 960
2016-08-02 18:00 | 999 | 999
2016-08-02 18:30 | 994 | 992
2016-08-02 19:00 | 994 | 992
2016-08-02 19:30 | 961 | 958
2016-08-02 20:00 | 944 | 943
2016-08-02 20:30 | 930 | 928
2016-08-02 21:00 | 875 | 872
2016-08-02 21:30 | 835 | 834
2016-08-02 22:00 | 787 | 784
2016-08-02 22:30 | 814 | 812
2016-08-02 23:00 | 794 | 789
2016-08-02 23:30 | 715 | 712
2016-08-03 | 651 | 647
2016-08-03 00:30 | 608 | 602
2016-08-03 01:00 | 578 | 572
2016-08-03 01:30 | 555 | 547
2016-08-03 02:00 | 537 | 527
2016-08-03 02:30 | 527 | 515
2016-08-03 03:00 | 515 | 500
2016-08-03 03:30 | 512 | 497
2016-08-03 04:00 | 504 | 490
2016-08-03 04:30 | 510 | 498
2016-08-03 05:00 | 524 | 514
2016-08-03 05:30 | 573 | 569
2016-08-03 06:00 | 643 | 641
2016-08-03 06:30 | 753 | 748
2016-08-03 07:00 | 833 | 827
2016-08-03 07:30 | 907 | 904
2016-08-03 08:00 | 914 | 906
2016-08-03 08:30 | 885 | 875
2016-08-03 09:00 | 843 | 832
2016-08-03 09:30 | 790 | 786
2016-08-03 10:00 | 752 | 750
2016-08-03 10:30 | 724 | 721
2016-08-03 11:00 | 713 | 713
2016-08-03 11:30 | 702 | 702
2016-08-03 12:00 | 687 | 686
2016-08-03 12:30 | 666 | 665
2016-08-03 13:00 | 663 | 663
2016-08-03 13:30 | 666 | 666
2016-08-03 14:00 | 678 | 677
2016-08-03 14:30 | 685 | 685
2016-08-03 15:00 | 706 | 705
2016-08-03 15:30 | 732 | 732
2016-08-03 16:00 | 770 | 769
2016-08-03 16:30 | 817 | 815
2016-08-03 17:00 | 870 | 869
2016-08-03 17:30 | 927 | 924
2016-08-03 18:00 | 1002 | 1000
2016-08-03 18:30 | 1027 | 1023
2016-08-03 19:00 | 1044 | 1040
2016-08-03 19:30 | 1025 | 1020
2016-08-03 20:00 | 1014 | 1007
2016-08-03 20:30 | 1012 | 1003
2016-08-03 21:00 | 964 | 954
2016-08-03 21:30 | 910 | 906
2016-08-03 22:00 | 871 | 868
2016-08-03 22:30 | 897 | 893
2016-08-03 23:00 | 848 | 843
2016-08-03 23:30 | 768 | 767
2016-08-04 | 702 | 699
2016-08-04 00:30 | 655 | 648
2016-08-04 01:00 | 616 | 609
2016-08-04 01:30 | 581 | 571
2016-08-04 02:00 | 555 | 542
2016-08-04 02:30 | 544 | 529
2016-08-04 03:00 | 533 | 518
2016-08-04 03:30 | 536 | 521
2016-08-04 04:00 | 535 | 519
2016-08-04 04:30 | 547 | 533
2016-08-04 05:00 | 560 | 549
2016-08-04 05:30 | 615 | 609
2016-08-04 06:00 | 677 | 672
2016-08-04 06:30 | 787 | 777
2016-08-04 07:00 | 867 | 862
2016-08-04 07:30 | 952 | 946
2016-08-04 08:00 | 964 | 962
2016-08-04 08:30 | 930 | 929
2016-08-04 09:00 | 849 | 846
2016-08-04 09:30 | 815 | 811
2016-08-04 10:00 | 805 | 803
2016-08-04 10:30 | 776 | 776
2016-08-04 11:00 | 727 | 727
2016-08-04 11:30 | 713 | 712
2016-08-04 12:00 | 727 | 727
2016-08-04 12:30 | 726 | 726
2016-08-04 13:00 | 742 | 742
2016-08-04 13:30 | 752 | 751
2016-08-04 14:00 | 773 | 772
2016-08-04 14:30 | 781 | 780
2016-08-04 15:00 | 804 | 804
2016-08-04 15:30 | 821 | 821
2016-08-04 16:00 | 839 | 838
2016-08-04 16:30 | 879 | 878
2016-08-04 17:00 | 926 | 926
2016-08-04 17:30 | 987 | 986
2016-08-04 18:00 | 1050 | 1049
2016-08-04 18:30 | 1068 | 1068
2016-08-04 19:00 | 1073 | 1073
2016-08-04 19:30 | 1058 | 1056
2016-08-04 20:00 | 1047 | 1047
2016-08-04 20:30 | 1032 | 1032
2016-08-04 21:00 | 998 | 997
2016-08-04 21:30 | 949 | 947
2016-08-04 22:00 | 897 | 889
2016-08-04 22:30 | 844 | 842
2016-08-04 23:00 | 825 | 824
2016-08-04 23:30 | 782 | 779
2016-08-05 | 736 | 735
2016-08-05 00:30 | 687 | 685
2016-08-05 01:00 | 654 | 650
2016-08-05 01:30 | 630 | 625
2016-08-05 02:00 | 612 | 607
2016-08-05 02:30 | 600 | 594
2016-08-05 03:00 | 592 | 584
2016-08-05 03:30 | 588 | 579
2016-08-05 04:00 | 587 | 578
2016-08-05 04:30 | 596 | 590
2016-08-05 05:00 | 621 | 617
2016-08-05 05:30 | 665 | 664
2016-08-05 06:00 | 714 | 714
2016-08-05 06:30 | 798 | 797
2016-08-05 07:00 | 888 | 888
2016-08-05 07:30 | 956 | 955
2016-08-05 08:00 | 962 | 957
2016-08-05 08:30 | 934 | 933
2016-08-05 09:00 | 888 | 887
2016-08-05 09:30 | 850 | 847
2016-08-05 10:00 | 831 | 831
2016-08-05 10:30 | 810 | 809
2016-08-05 11:00 | 792 | 792
2016-08-05 11:30 | 776 | 775
2016-08-05 12:00 | 757 | 757
2016-08-05 12:30 | 739 | 739
2016-08-05 13:00 | 743 | 743
2016-08-05 13:30 | 745 | 745
2016-08-05 14:00 | 753 | 753
2016-08-05 14:30 | 759 | 759
2016-08-05 15:00 | 770 | 770
2016-08-05 15:30 | 793 | 793
2016-08-05 16:00 | 820 | 819
2016-08-05 16:30 | 855 | 855
2016-08-05 17:00 | 901 | 901
2016-08-05 17:30 | 964 | 964
2016-08-05 18:00 | 999 | 999
2016-08-05 18:30 | 1006 | 1005
2016-08-05 19:00 | 1013 | 1012
2016-08-05 19:30 | 995 | 994
2016-08-05 20:00 | 993 | 993
2016-08-05 20:30 | 991 | 990
2016-08-05 21:00 | 949 | 949
2016-08-05 21:30 | 912 | 911
2016-08-05 22:00 | 883 | 880
2016-08-05 22:30 | 859 | 854
2016-08-05 23:00 | 837 | 829
2016-08-05 23:30 | 799 | 798
2016-08-06 | 756 | 754
2016-08-06 00:30 | 702 | 696
2016-08-06 01:00 | 670 | 666
2016-08-06 01:30 | 638 | 635
2016-08-06 02:00 | 605 | 600
2016-08-06 02:30 | 583 | 576
2016-08-06 03:00 | 569 | 561
2016-08-06 03:30 | 561 | 552
2016-08-06 04:00 | 561 | 552
2016-08-06 04:30 | 565 | 556
2016-08-06 05:00 | 572 | 564
2016-08-06 05:30 | 589 | 583
2016-08-06 06:00 | 619 | 614
2016-08-06 06:30 | 668 | 665
2016-08-06 07:00 | 699 | 697
2016-08-06 07:30 | 746 | 744
2016-08-06 08:00 | 775 | 774
2016-08-06 08:30 | 797 | 797
2016-08-06 09:00 | 791 | 790
2016-08-06 09:30 | 768 | 765
2016-08-06 10:00 | 745 | 741
2016-08-06 10:30 | 721 | 716
2016-08-06 11:00 | 710 | 706
2016-08-06 11:30 | 703 | 701
2016-08-06 12:00 | 691 | 688
2016-08-06 12:30 | 671 | 670
2016-08-06 13:00 | 669 | 669
2016-08-06 13:30 | 670 | 670
2016-08-06 14:00 | 668 | 667
2016-08-06 14:30 | 677 | 676
2016-08-06 15:00 | 697 | 697
2016-08-06 15:30 | 727 | 726
2016-08-06 16:00 | 753 | 753
2016-08-06 16:30 | 780 | 779
2016-08-06 17:00 | 822 | 822
2016-08-06 17:30 | 873 | 870
2016-08-06 18:00 | 917 | 916
2016-08-06 18:30 | 930 | 930
2016-08-06 19:00 | 929 | 929
2016-08-06 19:30 | 917 | 916
2016-08-06 20:00 | 910 | 909
2016-08-06 20:30 | 902 | 901
2016-08-06 21:00 | 862 | 862
2016-08-06 21:30 | 838 | 838
2016-08-06 22:00 | 818 | 818
2016-08-06 22:30 | 808 | 808
2016-08-06 23:00 | 795 | 795
2016-08-06 23:30 | 768 | 767
2016-08-07 | 734 | 732
2016-08-07 00:30 | 687 | 684
2016-08-07 01:00 | 664 | 660
2016-08-07 01:30 | 632 | 627
2016-08-07 02:00 | 600 | 593
2016-08-07 02:30 | 580 | 569
2016-08-07 03:00 | 573 | 561
2016-08-07 03:30 | 564 | 551
2016-08-07 04:00 | 561 | 547
2016-08-07 04:30 | 568 | 555
2016-08-07 05:00 | 576 | 564
2016-08-07 05:30 | 587 | 575
2016-08-07 06:00 | 605 | 597
2016-08-07 06:30 | 637 | 630
2016-08-07 07:00 | 669 | 663
2016-08-07 07:30 | 697 | 694
2016-08-07 08:00 | 717 | 715
2016-08-07 08:30 | 733 | 732
2016-08-07 09:00 | 731 | 730
2016-08-07 09:30 | 725 | 724
2016-08-07 10:00 | 700 | 700
2016-08-07 10:30 | 678 | 677
2016-08-07 11:00 | 651 | 650
2016-08-07 11:30 | 626 | 625
2016-08-07 12:00 | 614 | 613
2016-08-07 12:30 | 622 | 621
2016-08-07 13:00 | 620 | 619
2016-08-07 13:30 | 623 | 622
2016-08-07 14:00 | 637 | 637
2016-08-07 14:30 | 657 | 656
2016-08-07 15:00 | 677 | 676
2016-08-07 15:30 | 705 | 704
2016-08-07 16:00 | 741 | 741
2016-08-07 16:30 | 778 | 777
2016-08-07 17:00 | 823 | 820
2016-08-07 17:30 | 868 | 866
2016-08-07 18:00 | 924 | 921
2016-08-07 18:30 | 949 | 945
2016-08-07 19:00 | 941 | 937
2016-08-07 19:30 | 929 | 923
2016-08-07 20:00 | 920 | 914
2016-08-07 20:30 | 916 | 909
2016-08-07 21:00 | 874 | 870
2016-08-07 21:30 | 833 | 830
2016-08-07 22:00 | 795 | 794
2016-08-07 22:30 | 772 | 771
2016-08-07 23:00 | 765 | 764
2016-08-07 23:30 | 735 | 733
2016-08-08 | 699 | 696
2016-08-08 00:30 | 660 | 656
2016-08-08 01:00 | 634 | 629
2016-08-08 01:30 | 612 | 606
2016-08-08 02:00 | 581 | 574
2016-08-08 02:30 | 559 | 550
2016-08-08 03:00 | 547 | 537
2016-08-08 03:30 | 540 | 530
2016-08-08 04:00 | 544 | 535
2016-08-08 04:30 | 560 | 552
2016-08-08 05:00 | 582 | 576
2016-08-08 05:30 | 637 | 634
2016-08-08 06:00 | 685 | 684
2016-08-08 06:30 | 766 | 766
2016-08-08 07:00 | 843 | 843
2016-08-08 07:30 | 901 | 898
2016-08-08 08:00 | 905 | 903
2016-08-08 08:30 | 865 | 863
2016-08-08 09:00 | 817 | 815
2016-08-08 09:30 | 787 | 786
2016-08-08 10:00 | 755 | 753
2016-08-08 10:30 | 717 | 715
2016-08-08 11:00 | 697 | 696
2016-08-08 11:30 | 694 | 694
2016-08-08 12:00 | 713 | 713
2016-08-08 12:30 | 743 | 743
2016-08-08 13:00 | 757 | 756
2016-08-08 13:30 | 788 | 788
2016-08-08 14:00 | 778 | 777
2016-08-08 14:30 | 787 | 786
2016-08-08 15:00 | 791 | 790
2016-08-08 15:30 | 802 | 801
2016-08-08 16:00 | 820 | 819
2016-08-08 16:30 | 857 | 856
2016-08-08 17:00 | 895 | 895
2016-08-08 17:30 | 945 | 945
2016-08-08 18:00 | 1000 | 1000
2016-08-08 18:30 | 1010 | 1010
2016-08-08 19:00 | 1010 | 1010
2016-08-08 19:30 | 995 | 994
2016-08-08 20:00 | 980 | 979
2016-08-08 20:30 | 973 | 973
2016-08-08 21:00 | 929 | 929
2016-08-08 21:30 | 887 | 885
2016-08-08 22:00 | 864 | 861
2016-08-08 22:30 | 831 | 824
2016-08-08 23:00 | 802 | 800
2016-08-08 23:30 | 777 | 775
2016-08-09 | 732 | 730
2016-08-09 00:30 | 693 | 688
2016-08-09 01:00 | 667 | 661
2016-08-09 01:30 | 637 | 631
2016-08-09 02:00 | 589 | 583
2016-08-09 02:30 | 570 | 563
2016-08-09 03:00 | 566 | 558
2016-08-09 03:30 | 562 | 554
2016-08-09 04:00 | 564 | 556
2016-08-09 04:30 | 574 | 568
2016-08-09 05:00 | 601 | 597
2016-08-09 05:30 | 661 | 660
2016-08-09 06:00 | 723 | 722
2016-08-09 06:30 | 808 | 804
2016-08-09 07:00 | 903 | 897
2016-08-09 07:30 | 963 | 954
2016-08-09 08:00 | 961 | 953
2016-08-09 08:30 | 929 | 919
2016-08-09 09:00 | 869 | 861
2016-08-09 09:30 | 826 | 821
2016-08-09 10:00 | 788 | 787
2016-08-09 10:30 | 774 | 773
2016-08-09 11:00 | 755 | 755
2016-08-09 11:30 | 741 | 740
2016-08-09 12:00 | 736 | 736
2016-08-09 12:30 | 735 | 735
2016-08-09 13:00 | 733 | 732
2016-08-09 13:30 | 740 | 740
2016-08-09 14:00 | 747 | 746
2016-08-09 14:30 | 757 | 756
2016-08-09 15:00 | 773 | 773
2016-08-09 15:30 | 790 | 790
2016-08-09 16:00 | 816 | 816
2016-08-09 16:30 | 855 | 855
2016-08-09 17:00 | 887 | 887
2016-08-09 17:30 | 931 | 931
2016-08-09 18:00 | 987 | 987
2016-08-09 18:30 | 998 | 998
2016-08-09 19:00 | 1002 | 1001
2016-08-09 19:30 | 982 | 980
2016-08-09 20:00 | 973 | 970
2016-08-09 20:30 | 964 | 962
2016-08-09 21:00 | 923 | 920
2016-08-09 21:30 | 881 | 878
2016-08-09 22:00 | 867 | 863
2016-08-09 22:30 | 823 | 814
2016-08-09 23:00 | 809 | 802
2016-08-09 23:30 | 740 | 738
2016-08-10 | 727 | 722
2016-08-10 00:30 | 653 | 646
2016-08-10 01:00 | 595 | 588
2016-08-10 01:30 | 610 | 602
2016-08-10 02:00 | 588 | 580
2016-08-10 02:30 | 577 | 566
2016-08-10 03:00 | 574 | 562
2016-08-10 03:30 | 569 | 557
2016-08-10 04:00 | 574 | 561
2016-08-10 04:30 | 587 | 576
2016-08-10 05:00 | 596 | 588
2016-08-10 05:30 | 641 | 636
2016-08-10 06:00 | 680 | 678
2016-08-10 06:30 | 734 | 733
2016-08-10 07:00 | 801 | 800
2016-08-10 07:30 | 839 | 831
2016-08-10 08:00 | 873 | 867
2016-08-10 08:30 | 840 | 833
2016-08-10 09:00 | 795 | 788
2016-08-10 09:30 | 760 | 754
2016-08-10 10:00 | 727 | 724
2016-08-10 10:30 | 699 | 698
2016-08-10 11:00 | 674 | 673
2016-08-10 11:30 | 655 | 654
2016-08-10 12:00 | 643 | 643
2016-08-10 12:30 | 654 | 653
2016-08-10 13:00 | 645 | 645
2016-08-10 13:30 | 645 | 644
2016-08-10 14:00 | 662 | 662
2016-08-10 14:30 | 680 | 679
2016-08-10 15:00 | 706 | 706
2016-08-10 15:30 | 729 | 729
2016-08-10 16:00 | 766 | 766
2016-08-10 16:30 | 810 | 810
2016-08-10 17:00 | 857 | 853
2016-08-10 17:30 | 895 | 890
2016-08-10 18:00 | 932 | 930
2016-08-10 18:30 | 946 | 945
2016-08-10 19:00 | 940 | 939
2016-08-10 19:30 | 925 | 922
2016-08-10 20:00 | 921 | 917
2016-08-10 20:30 | 914 | 910
2016-08-10 21:00 | 880 | 877
2016-08-10 21:30 | 844 | 841
2016-08-10 22:00 | 860 | 860
2016-08-10 22:30 | 839 | 838
2016-08-10 23:00 | 818 | 816
2016-08-10 23:30 | 762 | 758
2016-08-11 | 716 | 709
2016-08-11 00:30 | 648 | 639
2016-08-11 01:00 | 624 | 614
2016-08-11 01:30 | 592 | 580
2016-08-11 02:00 | 571 | 562
2016-08-11 02:30 | 558 | 549
2016-08-11 03:00 | 557 | 546
2016-08-11 03:30 | 565 | 554
2016-08-11 04:00 | 541 | 529
2016-08-11 04:30 | 572 | 562
2016-08-11 05:00 | 598 | 591
2016-08-11 05:30 | 646 | 643
2016-08-11 06:00 | 694 | 692
2016-08-11 06:30 | 773 | 768
2016-08-11 07:00 | 849 | 847
2016-08-11 07:30 | 905 | 902
2016-08-11 08:00 | 907 | 903
2016-08-11 08:30 | 875 | 871
2016-08-11 09:00 | 837 | 832
2016-08-11 09:30 | 810 | 806
2016-08-11 10:00 | 787 | 782
2016-08-11 10:30 | 772 | 772
2016-08-11 11:00 | 764 | 764
2016-08-11 11:30 | 760 | 760
2016-08-11 12:00 | 754 | 754
2016-08-11 12:30 | 752 | 752
2016-08-11 13:00 | 778 | 778
2016-08-11 13:30 | 787 | 785
2016-08-11 14:00 | 794 | 791
2016-08-11 14:30 | 823 | 821
2016-08-11 15:00 | 836 | 834
2016-08-11 15:30 | 855 | 854
2016-08-11 16:00 | 874 | 873
2016-08-11 16:30 | 903 | 902
2016-08-11 17:00 | 941 | 939
2016-08-11 17:30 | 963 | 962
2016-08-11 18:00 | 987 | 987
2016-08-11 18:30 | 979 | 979
2016-08-11 19:00 | 989 | 989
2016-08-11 19:30 | 971 | 971
2016-08-11 20:00 | 956 | 955
2016-08-11 20:30 | 954 | 952
2016-08-11 21:00 | 914 | 912
2016-08-11 21:30 | 864 | 864
2016-08-11 22:00 | 844 | 842
2016-08-11 22:30 | 817 | 814
2016-08-11 23:00 | 793 | 791
2016-08-11 23:30 | 733 | 730
2016-08-12 | 691 | 687
2016-08-12 00:30 | 648 | 645
2016-08-12 01:00 | 617 | 613
2016-08-12 01:30 | 592 | 586
2016-08-12 02:00 | 566 | 558
2016-08-12 02:30 | 552 | 541
2016-08-12 03:00 | 546 | 534
2016-08-12 03:30 | 542 | 531
2016-08-12 04:00 | 543 | 532
2016-08-12 04:30 | 551 | 541
2016-08-12 05:00 | 573 | 566
2016-08-12 05:30 | 622 | 619
2016-08-12 06:00 | 695 | 687
2016-08-12 06:30 | 771 | 764
2016-08-12 07:00 | 839 | 836
2016-08-12 07:30 | 895 | 893
2016-08-12 08:00 | 904 | 900
2016-08-12 08:30 | 882 | 877
2016-08-12 09:00 | 842 | 837
2016-08-12 09:30 | 815 | 808
2016-08-12 10:00 | 783 | 782
2016-08-12 10:30 | 774 | 774
2016-08-12 11:00 | 783 | 782
2016-08-12 11:30 | 789 | 789
2016-08-12 12:00 | 767 | 766
2016-08-12 12:30 | 766 | 765
2016-08-12 13:00 | 759 | 759
2016-08-12 13:30 | 763 | 763
2016-08-12 14:00 | 775 | 774
2016-08-12 14:30 | 766 | 765
2016-08-12 15:00 | 772 | 771
2016-08-12 15:30 | 791 | 789
2016-08-12 16:00 | 812 | 810
2016-08-12 16:30 | 834 | 833
2016-08-12 17:00 | 873 | 873
2016-08-12 17:30 | 904 | 904
2016-08-12 18:00 | 941 | 941
2016-08-12 18:30 | 947 | 946
2016-08-12 19:00 | 953 | 951
2016-08-12 19:30 | 936 | 933
2016-08-12 20:00 | 926 | 923
2016-08-12 20:30 | 924 | 923
2016-08-12 21:00 | 892 | 891
2016-08-12 21:30 | 848 | 847
2016-08-12 22:00 | 829 | 828
2016-08-12 22:30 | 799 | 798
2016-08-12 23:00 | 811 | 809
2016-08-12 23:30 | 759 | 758
2016-08-13 | 712 | 711
2016-08-13 00:30 | 673 | 671
2016-08-13 01:00 | 619 | 614
2016-08-13 01:30 | 618 | 612
2016-08-13 02:00 | 589 | 582
2016-08-13 02:30 | 575 | 567
2016-08-13 03:00 | 567 | 558
2016-08-13 03:30 | 558 | 547
2016-08-13 04:00 | 547 | 535
2016-08-13 04:30 | 550 | 539
2016-08-13 05:00 | 555 | 546
2016-08-13 05:30 | 583 | 575
2016-08-13 06:00 | 617 | 612
2016-08-13 06:30 | 653 | 649
2016-08-13 07:00 | 682 | 679
2016-08-13 07:30 | 715 | 713
2016-08-13 08:00 | 750 | 746
2016-08-13 08:30 | 766 | 761
2016-08-13 09:00 | 767 | 763
2016-08-13 09:30 | 754 | 749
2016-08-13 10:00 | 730 | 727
2016-08-13 10:30 | 705 | 705
2016-08-13 11:00 | 690 | 690
2016-08-13 11:30 | 671 | 671
2016-08-13 12:00 | 664 | 664
2016-08-13 12:30 | 643 | 641
2016-08-13 13:00 | 627 | 624
2016-08-13 13:30 | 623 | 620
2016-08-13 14:00 | 632 | 629
2016-08-13 14:30 | 639 | 637
2016-08-13 15:00 | 665 | 663
2016-08-13 15:30 | 688 | 686
2016-08-13 16:00 | 715 | 714
2016-08-13 16:30 | 742 | 741
2016-08-13 17:00 | 779 | 776
2016-08-13 17:30 | 803 | 800
2016-08-13 18:00 | 846 | 845
2016-08-13 18:30 | 872 | 871
2016-08-13 19:00 | 876 | 875
2016-08-13 19:30 | 869 | 864
2016-08-13 20:00 | 860 | 853
2016-08-13 20:30 | 858 | 853
2016-08-13 21:00 | 827 | 822
2016-08-13 21:30 | 795 | 794
2016-08-13 22:00 | 777 | 777
2016-08-13 22:30 | 766 | 764
2016-08-13 23:00 | 776 | 774
2016-08-13 23:30 | 735 | 733
2016-08-14 | 693 | 691
2016-08-14 00:30 | 657 | 653
2016-08-14 01:00 | 634 | 629
2016-08-14 01:30 | 603 | 597
2016-08-14 02:00 | 575 | 566
2016-08-14 02:30 | 554 | 544
2016-08-14 03:00 | 549 | 537
2016-08-14 03:30 | 544 | 531
2016-08-14 04:00 | 540 | 528
2016-08-14 04:30 | 538 | 526
2016-08-14 05:00 | 536 | 524
2016-08-14 05:30 | 554 | 544
2016-08-14 06:00 | 572 | 564
2016-08-14 06:30 | 604 | 596
2016-08-14 07:00 | 638 | 631
2016-08-14 07:30 | 669 | 664
2016-08-14 08:00 | 682 | 679
2016-08-14 08:30 | 693 | 691
2016-08-14 09:00 | 694 | 693
2016-08-14 09:30 | 688 | 688
2016-08-14 10:00 | 676 | 676
2016-08-14 10:30 | 657 | 656
2016-08-14 11:00 | 640 | 638
2016-08-14 11:30 | 622 | 621
2016-08-14 12:00 | 607 | 605
2016-08-14 12:30 | 596 | 594
2016-08-14 13:00 | 598 | 597
2016-08-14 13:30 | 595 | 594
2016-08-14 14:00 | 606 | 605
2016-08-14 14:30 | 621 | 620
2016-08-14 15:00 | 643 | 642
2016-08-14 15:30 | 670 | 670
2016-08-14 16:00 | 707 | 707
2016-08-14 16:30 | 738 | 738
2016-08-14 17:00 | 780 | 780
2016-08-14 17:30 | 830 | 828
2016-08-14 18:00 | 877 | 877
2016-08-14 18:30 | 914 | 909
2016-08-14 19:00 | 924 | 913
2016-08-14 19:30 | 907 | 894
2016-08-14 20:00 | 890 | 879
2016-08-14 20:30 | 884 | 874
2016-08-14 21:00 | 840 | 838
2016-08-14 21:30 | 811 | 808
2016-08-14 22:00 | 781 | 779
2016-08-14 22:30 | 753 | 751
2016-08-14 23:00 | 760 | 758
2016-08-14 23:30 | 715 | 711
2016-08-15 | 674 | 671
2016-08-15 00:30 | 637 | 632
2016-08-15 01:00 | 612 | 606
2016-08-15 01:30 | 579 | 571
2016-08-15 02:00 | 553 | 542
2016-08-15 02:30 | 536 | 525
2016-08-15 03:00 | 534 | 522
2016-08-15 03:30 | 537 | 524
2016-08-15 04:00 | 538 | 526
2016-08-15 04:30 | 549 | 538
2016-08-15 05:00 | 566 | 558
2016-08-15 05:30 | 627 | 623
2016-08-15 06:00 | 681 | 680
2016-08-15 06:30 | 768 | 767
2016-08-15 07:00 | 848 | 845
2016-08-15 07:30 | 925 | 923
2016-08-15 08:00 | 937 | 931
2016-08-15 08:30 | 925 | 918
2016-08-15 09:00 | 895 | 888
2016-08-15 09:30 | 818 | 810
2016-08-15 10:00 | 774 | 771
2016-08-15 10:30 | 763 | 760
2016-08-15 11:00 | 752 | 751
2016-08-15 11:30 | 762 | 761
2016-08-15 12:00 | 750 | 750
2016-08-15 12:30 | 764 | 764
2016-08-15 13:00 | 774 | 774
2016-08-15 13:30 | 771 | 770
2016-08-15 14:00 | 778 | 778
2016-08-15 14:30 | 785 | 785
2016-08-15 15:00 | 804 | 803
2016-08-15 15:30 | 837 | 837
2016-08-15 16:00 | 866 | 865
2016-08-15 16:30 | 904 | 904
2016-08-15 17:00 | 941 | 938
2016-08-15 17:30 | 993 | 990
2016-08-15 18:00 | 1053 | 1048
2016-08-15 18:30 | 1063 | 1058
2016-08-15 19:00 | 1065 | 1059
2016-08-15 19:30 | 1042 | 1032
2016-08-15 20:00 | 1025 | 1019
2016-08-15 20:30 | 1012 | 1005
2016-08-15 21:00 | 963 | 958
2016-08-15 21:30 | 917 | 912
2016-08-15 22:00 | 884 | 876
2016-08-15 22:30 | 844 | 836
2016-08-15 23:00 | 840 | 836
2016-08-15 23:30 | 787 | 783
2016-08-16 | 742 | 737
2016-08-16 00:30 | 701 | 693
2016-08-16 01:00 | 674 | 663
2016-08-16 01:30 | 640 | 632
2016-08-16 02:00 | 608 | 601
2016-08-16 02:30 | 590 | 581
2016-08-16 03:00 | 584 | 574
2016-08-16 03:30 | 589 | 578
2016-08-16 04:00 | 600 | 590
2016-08-16 04:30 | 620 | 612
2016-08-16 05:00 | 640 | 634
2016-08-16 05:30 | 665 | 662
2016-08-16 06:00 | 732 | 730
2016-08-16 06:30 | 823 | 819
2016-08-16 07:00 | 898 | 897
2016-08-16 07:30 | 986 | 983
2016-08-16 08:00 | 975 | 973
2016-08-16 08:30 | 933 | 930
2016-08-16 09:00 | 860 | 855
2016-08-16 09:30 | 834 | 828
2016-08-16 10:00 | 816 | 810
2016-08-16 10:30 | 814 | 811
2016-08-16 11:00 | 802 | 802
2016-08-16 11:30 | 789 | 788
2016-08-16 12:00 | 765 | 764
2016-08-16 12:30 | 783 | 782
2016-08-16 13:00 | 768 | 767
2016-08-16 13:30 | 758 | 757
2016-08-16 14:00 | 784 | 784
2016-08-16 14:30 | 790 | 790
2016-08-16 15:00 | 799 | 799
2016-08-16 15:30 | 822 | 822
2016-08-16 16:00 | 853 | 852
2016-08-16 16:30 | 891 | 891
2016-08-16 17:00 | 921 | 920
2016-08-16 17:30 | 971 | 966
2016-08-16 18:00 | 1023 | 1022
2016-08-16 18:30 | 1046 | 1044
2016-08-16 19:00 | 1048 | 1045
2016-08-16 19:30 | 1030 | 1024
2016-08-16 20:00 | 1029 | 1023
2016-08-16 20:30 | 1023 | 1015
2016-08-16 21:00 | 971 | 966
2016-08-16 21:30 | 926 | 922
2016-08-16 22:00 | 889 | 889
2016-08-16 22:30 | 855 | 853
2016-08-16 23:00 | 850 | 847
2016-08-16 23:30 | 804 | 798
2016-08-17 | 749 | 745
2016-08-17 00:30 | 707 | 705
2016-08-17 01:00 | 678 | 673
2016-08-17 01:30 | 651 | 647
2016-08-17 02:00 | 621 | 615
2016-08-17 02:30 | 606 | 598
2016-08-17 03:00 | 601 | 592
2016-08-17 03:30 | 598 | 589
2016-08-17 04:00 | 602 | 593
2016-08-17 04:30 | 623 | 615
2016-08-17 05:00 | 640 | 635
2016-08-17 05:30 | 696 | 694
2016-08-17 06:00 | 748 | 747
2016-08-17 06:30 | 835 | 829
2016-08-17 07:00 | 923 | 918
2016-08-17 07:30 | 981 | 978
2016-08-17 08:00 | 998 | 985
2016-08-17 08:30 | 965 | 951
2016-08-17 09:00 | 895 | 886
2016-08-17 09:30 | 865 | 863
2016-08-17 10:00 | 854 | 852
2016-08-17 10:30 | 829 | 828
2016-08-17 11:00 | 809 | 806
2016-08-17 11:30 | 806 | 804
2016-08-17 12:00 | 797 | 795
2016-08-17 12:30 | 789 | 787
2016-08-17 13:00 | 777 | 774
2016-08-17 13:30 | 772 | 769
2016-08-17 14:00 | 783 | 781
2016-08-17 14:30 | 794 | 792
2016-08-17 15:00 | 803 | 801
2016-08-17 15:30 | 820 | 817
2016-08-17 16:00 | 853 | 851
2016-08-17 16:30 | 885 | 884
2016-08-17 17:00 | 921 | 920
2016-08-17 17:30 | 959 | 959
2016-08-17 18:00 | 1012 | 1012
2016-08-17 18:30 | 1034 | 1027
2016-08-17 19:00 | 1045 | 1032
2016-08-17 19:30 | 1028 | 1017
2016-08-17 20:00 | 1009 | 1003
2016-08-17 20:30 | 1005 | 1000
2016-08-17 21:00 | 964 | 960
2016-08-17 21:30 | 926 | 919
2016-08-17 22:00 | 888 | 880
2016-08-17 22:30 | 863 | 851
2016-08-17 23:00 | 860 | 847
2016-08-17 23:30 | 772 | 765
2016-08-18 | 733 | 731
2016-08-18 00:30 | 694 | 690
2016-08-18 01:00 | 668 | 662
2016-08-18 01:30 | 647 | 641
2016-08-18 02:00 | 629 | 621
2016-08-18 02:30 | 585 | 575
2016-08-18 03:00 | 580 | 568
2016-08-18 03:30 | 555 | 540
2016-08-18 04:00 | 562 | 548
2016-08-18 04:30 | 598 | 588
2016-08-18 05:00 | 592 | 584
2016-08-18 05:30 | 638 | 635
2016-08-18 06:00 | 734 | 731
2016-08-18 06:30 | 828 | 822
2016-08-18 07:00 | 916 | 911
2016-08-18 07:30 | 973 | 968
2016-08-18 08:00 | 985 | 981
2016-08-18 08:30 | 955 | 951
2016-08-18 09:00 | 894 | 887
2016-08-18 09:30 | 850 | 842
2016-08-18 10:00 | 839 | 829
2016-08-18 10:30 | 816 | 815
2016-08-18 11:00 | 830 | 829
2016-08-18 11:30 | 842 | 841
2016-08-18 12:00 | 843 | 842
2016-08-18 12:30 | 828 | 827
2016-08-18 13:00 | 827 | 825
2016-08-18 13:30 | 828 | 827
2016-08-18 14:00 | 849 | 849
2016-08-18 14:30 | 858 | 858
2016-08-18 15:00 | 868 | 867
2016-08-18 15:30 | 877 | 876
2016-08-18 16:00 | 887 | 887
2016-08-18 16:30 | 910 | 910
2016-08-18 17:00 | 920 | 920
2016-08-18 17:30 | 982 | 981
2016-08-18 18:00 | 1028 | 1027
2016-08-18 18:30 | 1050 | 1044
2016-08-18 19:00 | 1059 | 1053
2016-08-18 19:30 | 1027 | 1019
2016-08-18 20:00 | 1017 | 1016
2016-08-18 20:30 | 997 | 996
2016-08-18 21:00 | 974 | 971
2016-08-18 21:30 | 924 | 921
2016-08-18 22:00 | 886 | 882
2016-08-18 22:30 | 857 | 851
2016-08-18 23:00 | 843 | 841
2016-08-18 23:30 | 806 | 803
2016-08-19 | 752 | 745
2016-08-19 00:30 | 711 | 701
2016-08-19 01:00 | 675 | 669
2016-08-19 01:30 | 652 | 646
2016-08-19 02:00 | 626 | 619
2016-08-19 02:30 | 607 | 598
2016-08-19 03:00 | 602 | 592
2016-08-19 03:30 | 598 | 587
2016-08-19 04:00 | 600 | 589
2016-08-19 04:30 | 613 | 605
2016-08-19 05:00 | 634 | 628
2016-08-19 05:30 | 683 | 681
2016-08-19 06:00 | 738 | 735
2016-08-19 06:30 | 814 | 810
2016-08-19 07:00 | 887 | 881
2016-08-19 07:30 | 915 | 909
2016-08-19 08:00 | 937 | 930
2016-08-19 08:30 | 914 | 907
2016-08-19 09:00 | 888 | 881
2016-08-19 09:30 | 863 | 855
2016-08-19 10:00 | 855 | 847
2016-08-19 10:30 | 838 | 828
2016-08-19 11:00 | 826 | 817
2016-08-19 11:30 | 824 | 817
2016-08-19 12:00 | 812 | 807
2016-08-19 12:30 | 803 | 798
2016-08-19 13:00 | 787 | 780
2016-08-19 13:30 | 784 | 776
2016-08-19 14:00 | 790 | 783
2016-08-19 14:30 | 796 | 787
2016-08-19 15:00 | 808 | 798
2016-08-19 15:30 | 821 | 811
2016-08-19 16:00 | 850 | 841
2016-08-19 16:30 | 883 | 874
2016-08-19 17:00 | 910 | 903
2016-08-19 17:30 | 933 | 927
2016-08-19 18:00 | 957 | 953
2016-08-19 18:30 | 964 | 959
2016-08-19 19:00 | 973 | 967
2016-08-19 19:30 | 957 | 950
2016-08-19 20:00 | 952 | 945
2016-08-19 20:30 | 948 | 942
2016-08-19 21:00 | 915 | 909
2016-08-19 21:30 | 882 | 878
2016-08-19 22:00 | 849 | 849
2016-08-19 22:30 | 826 | 826
2016-08-19 23:00 | 802 | 802
2016-08-19 23:30 | 768 | 766
2016-08-20 | 715 | 711
2016-08-20 00:30 | 684 | 678
2016-08-20 01:00 | 650 | 642
2016-08-20 01:30 | 638 | 628
2016-08-20 02:00 | 617 | 605
2016-08-20 02:30 | 597 | 584
2016-08-20 03:00 | 588 | 573
2016-08-20 03:30 | 583 | 567
2016-08-20 04:00 | 577 | 560
2016-08-20 04:30 | 585 | 569
2016-08-20 05:00 | 597 | 583
2016-08-20 05:30 | 585 | 573
2016-08-20 06:00 | 588 | 577
2016-08-20 06:30 | 665 | 657
2016-08-20 07:00 | 695 | 689
2016-08-20 07:30 | 724 | 719
2016-08-20 08:00 | 740 | 738
2016-08-20 08:30 | 755 | 754
2016-08-20 09:00 | 754 | 754
2016-08-20 09:30 | 748 | 747
2016-08-20 10:00 | 721 | 718
2016-08-20 10:30 | 699 | 696
2016-08-20 11:00 | 685 | 682
2016-08-20 11:30 | 686 | 683
2016-08-20 12:00 | 680 | 676
2016-08-20 12:30 | 685 | 681
2016-08-20 13:00 | 707 | 703
2016-08-20 13:30 | 715 | 711
2016-08-20 14:00 | 727 | 724
2016-08-20 14:30 | 731 | 728
2016-08-20 15:00 | 719 | 715
2016-08-20 15:30 | 731 | 728
2016-08-20 16:00 | 774 | 772
2016-08-20 16:30 | 798 | 796
2016-08-20 17:00 | 822 | 821
2016-08-20 17:30 | 842 | 839
2016-08-20 18:00 | 873 | 871
2016-08-20 18:30 | 884 | 882
2016-08-20 19:00 | 884 | 882
2016-08-20 19:30 | 866 | 862
2016-08-20 20:00 | 856 | 850
2016-08-20 20:30 | 849 | 843
2016-08-20 21:00 | 819 | 814
2016-08-20 21:30 | 796 | 792
2016-08-20 22:00 | 779 | 775
2016-08-20 22:30 | 747 | 742
2016-08-20 23:00 | 756 | 752
2016-08-20 23:30 | 724 | 719
2016-08-21 | 706 | 701
2016-08-21 00:30 | 668 | 660
2016-08-21 01:00 | 636 | 626
2016-08-21 01:30 | 616 | 604
2016-08-21 02:00 | 605 | 590
2016-08-21 02:30 | 596 | 580
2016-08-21 03:00 | 592 | 575
2016-08-21 03:30 | 589 | 570
2016-08-21 04:00 | 589 | 570
2016-08-21 04:30 | 587 | 569
2016-08-21 05:00 | 589 | 573
2016-08-21 05:30 | 601 | 586
2016-08-21 06:00 | 617 | 603
2016-08-21 06:30 | 636 | 622
2016-08-21 07:00 | 660 | 648
2016-08-21 07:30 | 678 | 669
2016-08-21 08:00 | 689 | 683
2016-08-21 08:30 | 707 | 703
2016-08-21 09:00 | 703 | 701
2016-08-21 09:30 | 691 | 689
2016-08-21 10:00 | 679 | 677
2016-08-21 10:30 | 665 | 663
2016-08-21 11:00 | 637 | 635
2016-08-21 11:30 | 625 | 623
2016-08-21 12:00 | 618 | 615
2016-08-21 12:30 | 608 | 605
2016-08-21 13:00 | 610 | 607
2016-08-21 13:30 | 608 | 605
2016-08-21 14:00 | 618 | 615
2016-08-21 14:30 | 626 | 623
2016-08-21 15:00 | 652 | 650
2016-08-21 15:30 | 687 | 686
2016-08-21 16:00 | 723 | 723
2016-08-21 16:30 | 762 | 762
2016-08-21 17:00 | 809 | 809
2016-08-21 17:30 | 847 | 846
2016-08-21 18:00 | 904 | 904
2016-08-21 18:30 | 942 | 935
2016-08-21 19:00 | 945 | 937
2016-08-21 19:30 | 932 | 921
2016-08-21 20:00 | 914 | 907
2016-08-21 20:30 | 909 | 902
2016-08-21 21:00 | 849 | 847
2016-08-21 21:30 | 819 | 818
2016-08-21 22:00 | 806 | 805
2016-08-21 22:30 | 749 | 747
2016-08-21 23:00 | 750 | 750
2016-08-21 23:30 | 731 | 729
2016-08-22 | 703 | 698
2016-08-22 00:30 | 664 | 656
2016-08-22 01:00 | 638 | 628
2016-08-22 01:30 | 617 | 605
2016-08-22 02:00 | 601 | 588
2016-08-22 02:30 | 590 | 575
2016-08-22 03:00 | 585 | 569
2016-08-22 03:30 | 581 | 564
2016-08-22 04:00 | 583 | 568
2016-08-22 04:30 | 599 | 586
2016-08-22 05:00 | 617 | 606
2016-08-22 05:30 | 658 | 653
2016-08-22 06:00 | 716 | 708
2016-08-22 06:30 | 796 | 791
2016-08-22 07:00 | 871 | 867
2016-08-22 07:30 | 934 | 923
2016-08-22 08:00 | 932 | 915
2016-08-22 08:30 | 906 | 886
2016-08-22 09:00 | 868 | 853
2016-08-22 09:30 | 837 | 828
2016-08-22 10:00 | 816 | 808
2016-08-22 10:30 | 827 | 820
2016-08-22 11:00 | 821 | 814
2016-08-22 11:30 | 818 | 812
2016-08-22 12:00 | 818 | 813
2016-08-22 12:30 | 833 | 823
2016-08-22 13:00 | 833 | 825
2016-08-22 13:30 | 818 | 806
2016-08-22 14:00 | 807 | 801
2016-08-22 14:30 | 814 | 812
2016-08-22 15:00 | 824 | 822
2016-08-22 15:30 | 830 | 828
2016-08-22 16:00 | 855 | 854
2016-08-22 16:30 | 897 | 893
2016-08-22 17:00 | 945 | 937
2016-08-22 17:30 | 974 | 968
2016-08-22 18:00 | 1019 | 1016
2016-08-22 18:30 | 1031 | 1027
2016-08-22 19:00 | 1032 | 1027
2016-08-22 19:30 | 999 | 994
2016-08-22 20:00 | 988 | 982
2016-08-22 20:30 | 977 | 972
2016-08-22 21:00 | 926 | 921
2016-08-22 21:30 | 880 | 871
2016-08-22 22:00 | 843 | 836
2016-08-22 22:30 | 807 | 806
2016-08-22 23:00 | 813 | 812
2016-08-22 23:30 | 762 | 759
2016-08-23 | 711 | 706
2016-08-23 00:30 | 671 | 664
2016-08-23 01:00 | 640 | 634
2016-08-23 01:30 | 619 | 611
2016-08-23 02:00 | 599 | 589
2016-08-23 02:30 | 591 | 580
2016-08-23 03:00 | 585 | 572
2016-08-23 03:30 | 584 | 570
2016-08-23 04:00 | 586 | 574
2016-08-23 04:30 | 600 | 589
2016-08-23 05:00 | 613 | 604
2016-08-23 05:30 | 653 | 648
2016-08-23 06:00 | 702 | 698
2016-08-23 06:30 | 787 | 778
2016-08-23 07:00 | 854 | 842
2016-08-23 07:30 | 894 | 887
2016-08-23 08:00 | 897 | 892
2016-08-23 08:30 | 883 | 880
2016-08-23 09:00 | 870 | 865
2016-08-23 09:30 | 868 | 862
2016-08-23 10:00 | 855 | 850
2016-08-23 10:30 | 858 | 853
2016-08-23 11:00 | 866 | 861
2016-08-23 11:30 | 871 | 867
2016-08-23 12:00 | 876 | 870
2016-08-23 12:30 | 864 | 861
2016-08-23 13:00 | 851 | 849
2016-08-23 13:30 | 852 | 850
2016-08-23 14:00 | 880 | 878
2016-08-23 14:30 | 960 | 958
2016-08-23 15:00 | 923 | 922
2016-08-23 15:30 | 873 | 872
2016-08-23 16:00 | 907 | 906
2016-08-23 16:30 | 941 | 941
2016-08-23 17:00 | 967 | 966
2016-08-23 17:30 | 999 | 999
2016-08-23 18:00 | 1029 | 1027
2016-08-23 18:30 | 1023 | 1021
2016-08-23 19:00 | 1023 | 1020
2016-08-23 19:30 | 1002 | 998
2016-08-23 20:00 | 992 | 990
2016-08-23 20:30 | 986 | 982
2016-08-23 21:00 | 933 | 931
2016-08-23 21:30 | 878 | 878
2016-08-23 22:00 | 847 | 847
2016-08-23 22:30 | 827 | 826
2016-08-23 23:00 | 829 | 828
2016-08-23 23:30 | 782 | 779
2016-08-24 | 731 | 726
2016-08-24 00:30 | 684 | 679
2016-08-24 01:00 | 656 | 652
2016-08-24 01:30 | 629 | 624
2016-08-24 02:00 | 605 | 598
2016-08-24 02:30 | 589 | 581
2016-08-24 03:00 | 587 | 579
2016-08-24 03:30 | 577 | 568
2016-08-24 04:00 | 589 | 580
2016-08-24 04:30 | 595 | 587
2016-08-24 05:00 | 612 | 606
2016-08-24 05:30 | 657 | 652
2016-08-24 06:00 | 704 | 698
2016-08-24 06:30 | 776 | 774
2016-08-24 07:00 | 852 | 852
2016-08-24 07:30 | 944 | 936
2016-08-24 08:00 | 968 | 962
2016-08-24 08:30 | 979 | 974
2016-08-24 09:00 | 983 | 980
2016-08-24 09:30 | 990 | 987
2016-08-24 10:00 | 995 | 993
2016-08-24 10:30 | 1006 | 1004
2016-08-24 11:00 | 1010 | 1005
2016-08-24 11:30 | 995 | 989
2016-08-24 12:00 | 1000 | 993
2016-08-24 12:30 | 1004 | 996
2016-08-24 13:00 | 1002 | 994
2016-08-24 13:30 | 1122 | 1112
2016-08-24 14:00 | 1121 | 1111
2016-08-24 14:30 | 1085 | 1072
2016-08-24 15:00 | 980 | 967
2016-08-24 15:30 | 964 | 951
2016-08-24 16:00 | 990 | 978
2016-08-24 16:30 | 1013 | 1002
2016-08-24 17:00 | 1040 | 1031
2016-08-24 17:30 | 1067 | 1063
2016-08-24 18:00 | 1090 | 1088
2016-08-24 18:30 | 1090 | 1085
2016-08-24 19:00 | 1086 | 1079
2016-08-24 19:30 | 1051 | 1044
2016-08-24 20:00 | 1044 | 1037
2016-08-24 20:30 | 1021 | 1018
2016-08-24 21:00 | 977 | 971
2016-08-24 21:30 | 918 | 913
2016-08-24 22:00 | 880 | 875
2016-08-24 22:30 | 846 | 838
2016-08-24 23:00 | 841 | 836
2016-08-24 23:30 | 779 | 778
2016-08-25 | 726 | 724
2016-08-25 00:30 | 684 | 680
2016-08-25 01:00 | 653 | 648
2016-08-25 01:30 | 623 | 617
2016-08-25 02:00 | 595 | 587
2016-08-25 02:30 | 583 | 574
2016-08-25 03:00 | 578 | 568
2016-08-25 03:30 | 572 | 562
2016-08-25 04:00 | 574 | 564
2016-08-25 04:30 | 588 | 580
2016-08-25 05:00 | 613 | 607
2016-08-25 05:30 | 665 | 662
2016-08-25 06:00 | 719 | 712
2016-08-25 06:30 | 799 | 796
2016-08-25 07:00 | 885 | 883
2016-08-25 07:30 | 952 | 951
2016-08-25 08:00 | 947 | 943
2016-08-25 08:30 | 891 | 879
2016-08-25 09:00 | 835 | 830
2016-08-25 09:30 | 796 | 796
2016-08-25 10:00 | 772 | 771
2016-08-25 10:30 | 756 | 756
2016-08-25 11:00 | 738 | 737
2016-08-25 11:30 | 718 | 718
2016-08-25 12:00 | 709 | 709
2016-08-25 12:30 | 705 | 705
2016-08-25 13:00 | 709 | 709
2016-08-25 13:30 | 711 | 711
2016-08-25 14:00 | 720 | 720
2016-08-25 14:30 | 733 | 733
2016-08-25 15:00 | 746 | 746
2016-08-25 15:30 | 774 | 774
2016-08-25 16:00 | 811 | 811
2016-08-25 16:30 | 853 | 853
2016-08-25 17:00 | 901 | 899
2016-08-25 17:30 | 928 | 925
2016-08-25 18:00 | 980 | 979
2016-08-25 18:30 | 1009 | 1006
2016-08-25 19:00 | 1027 | 1025
2016-08-25 19:30 | 1021 | 1018
2016-08-25 20:00 | 1015 | 1011
2016-08-25 20:30 | 1010 | 1008
2016-08-25 21:00 | 984 | 979
2016-08-25 21:30 | 942 | 939
2016-08-25 22:00 | 900 | 896
2016-08-25 22:30 | 866 | 863
2016-08-25 23:00 | 860 | 857
2016-08-25 23:30 | 794 | 788
2016-08-26 | 740 | 735
2016-08-26 00:30 | 690 | 683
2016-08-26 01:00 | 656 | 651
2016-08-26 01:30 | 631 | 624
2016-08-26 02:00 | 610 | 600
2016-08-26 02:30 | 602 | 590
2016-08-26 03:00 | 599 | 586
2016-08-26 03:30 | 596 | 583
2016-08-26 04:00 | 597 | 586
2016-08-26 04:30 | 610 | 600
2016-08-26 05:00 | 629 | 622
2016-08-26 05:30 | 660 | 655
2016-08-26 06:00 | 705 | 703
2016-08-26 06:30 | 780 | 778
2016-08-26 07:00 | 841 | 839
2016-08-26 07:30 | 881 | 876
2016-08-26 08:00 | 884 | 879
2016-08-26 08:30 | 870 | 865
2016-08-26 09:00 | 837 | 830
2016-08-26 09:30 | 798 | 791
2016-08-26 10:00 | 767 | 766
2016-08-26 10:30 | 733 | 732
2016-08-26 11:00 | 712 | 709
2016-08-26 11:30 | 692 | 690
2016-08-26 12:00 | 687 | 684
2016-08-26 12:30 | 684 | 681
2016-08-26 13:00 | 691 | 688
2016-08-26 13:30 | 704 | 702
2016-08-26 14:00 | 727 | 724
2016-08-26 14:30 | 741 | 739
2016-08-26 15:00 | 752 | 750
2016-08-26 15:30 | 765 | 763
2016-08-26 16:00 | 783 | 782
2016-08-26 16:30 | 821 | 818
2016-08-26 17:00 | 863 | 858
2016-08-26 17:30 | 904 | 895
2016-08-26 18:00 | 945 | 942
2016-08-26 18:30 | 977 | 964
2016-08-26 19:00 | 989 | 975
2016-08-26 19:30 | 973 | 956
2016-08-26 20:00 | 966 | 956
2016-08-26 20:30 | 965 | 954
2016-08-26 21:00 | 932 | 921
2016-08-26 21:30 | 899 | 885
2016-08-26 22:00 | 861 | 853
2016-08-26 22:30 | 836 | 833
2016-08-26 23:00 | 835 | 831
2016-08-26 23:30 | 787 | 779
2016-08-27 | 739 | 734
2016-08-27 00:30 | 700 | 694
2016-08-27 01:00 | 670 | 663
2016-08-27 01:30 | 643 | 633
2016-08-27 02:00 | 625 | 613
2016-08-27 02:30 | 614 | 601
2016-08-27 03:00 | 603 | 589
2016-08-27 03:30 | 599 | 586
2016-08-27 04:00 | 598 | 584
2016-08-27 04:30 | 603 | 589
2016-08-27 05:00 | 610 | 597
2016-08-27 05:30 | 624 | 613
2016-08-27 06:00 | 642 | 633
2016-08-27 06:30 | 676 | 669
2016-08-27 07:00 | 699 | 693
2016-08-27 07:30 | 727 | 724
2016-08-27 08:00 | 740 | 738
2016-08-27 08:30 | 749 | 748
2016-08-27 09:00 | 743 | 743
2016-08-27 09:30 | 726 | 725
2016-08-27 10:00 | 705 | 704
2016-08-27 10:30 | 687 | 687
2016-08-27 11:00 | 661 | 661
2016-08-27 11:30 | 636 | 634
2016-08-27 12:00 | 627 | 625
2016-08-27 12:30 | 609 | 606
2016-08-27 13:00 | 623 | 620
2016-08-27 13:30 | 623 | 620
2016-08-27 14:00 | 633 | 630
2016-08-27 14:30 | 645 | 642
2016-08-27 15:00 | 652 | 649
2016-08-27 15:30 | 692 | 690
2016-08-27 16:00 | 723 | 722
2016-08-27 16:30 | 754 | 753
2016-08-27 17:00 | 798 | 796
2016-08-27 17:30 | 826 | 823
2016-08-27 18:00 | 862 | 861
2016-08-27 18:30 | 908 | 900
2016-08-27 19:00 | 924 | 912
2016-08-27 19:30 | 915 | 901
2016-08-27 20:00 | 912 | 897
2016-08-27 20:30 | 906 | 889
2016-08-27 21:00 | 876 | 858
2016-08-27 21:30 | 848 | 833
2016-08-27 22:00 | 824 | 815
2016-08-27 22:30 | 788 | 787
2016-08-27 23:00 | 799 | 797
2016-08-27 23:30 | 761 | 757
2016-08-28 | 732 | 727
2016-08-28 00:30 | 686 | 679
2016-08-28 01:00 | 662 | 653
2016-08-28 01:30 | 646 | 634
2016-08-28 02:00 | 625 | 611
2016-08-28 02:30 | 611 | 595
2016-08-28 03:00 | 604 | 586
2016-08-28 03:30 | 601 | 583
2016-08-28 04:00 | 597 | 578
2016-08-28 04:30 | 600 | 580
2016-08-28 05:00 | 605 | 586
2016-08-28 05:30 | 614 | 598
2016-08-28 06:00 | 628 | 613
2016-08-28 06:30 | 647 | 632
2016-08-28 07:00 | 662 | 648
2016-08-28 07:30 | 679 | 670
2016-08-28 08:00 | 695 | 688
2016-08-28 08:30 | 701 | 696
2016-08-28 09:00 | 701 | 696
2016-08-28 09:30 | 689 | 685
2016-08-28 10:00 | 675 | 671
2016-08-28 10:30 | 658 | 655
2016-08-28 11:00 | 645 | 641
2016-08-28 11:30 | 627 | 622
2016-08-28 12:00 | 622 | 618
2016-08-28 12:30 | 619 | 615
2016-08-28 13:00 | 615 | 610
2016-08-28 13:30 | 623 | 618
2016-08-28 14:00 | 635 | 631
2016-08-28 14:30 | 644 | 640
2016-08-28 15:00 | 664 | 660
2016-08-28 15:30 | 681 | 678
2016-08-28 16:00 | 712 | 709
2016-08-28 16:30 | 747 | 745
2016-08-28 17:00 | 795 | 794
2016-08-28 17:30 | 840 | 838
2016-08-28 18:00 | 892 | 891
2016-08-28 18:30 | 943 | 936
2016-08-28 19:00 | 954 | 947
2016-08-28 19:30 | 942 | 934
2016-08-28 20:00 | 930 | 920
2016-08-28 20:30 | 921 | 913
2016-08-28 21:00 | 875 | 872
2016-08-28 21:30 | 848 | 844
2016-08-28 22:00 | 812 | 806
2016-08-28 22:30 | 790 | 786
2016-08-28 23:00 | 804 | 801
2016-08-28 23:30 | 751 | 748
2016-08-29 | 694 | 690
2016-08-29 00:30 | 658 | 650
2016-08-29 01:00 | 631 | 620
2016-08-29 01:30 | 604 | 589
2016-08-29 02:00 | 577 | 560
2016-08-29 02:30 | 562 | 544
2016-08-29 03:00 | 553 | 533
2016-08-29 03:30 | 556 | 535
2016-08-29 04:00 | 559 | 539
2016-08-29 04:30 | 575 | 559
2016-08-29 05:00 | 601 | 589
2016-08-29 05:30 | 647 | 641
2016-08-29 06:00 | 709 | 701
2016-08-29 06:30 | 800 | 794
2016-08-29 07:00 | 868 | 862
2016-08-29 07:30 | 923 | 917
2016-08-29 08:00 | 910 | 901
2016-08-29 08:30 | 864 | 855
2016-08-29 09:00 | 840 | 830
2016-08-29 09:30 | 791 | 787
2016-08-29 10:00 | 748 | 748
2016-08-29 10:30 | 732 | 732
2016-08-29 11:00 | 719 | 719
2016-08-29 11:30 | 709 | 709
2016-08-29 12:00 | 726 | 726
2016-08-29 12:30 | 731 | 731
2016-08-29 13:00 | 744 | 744
2016-08-29 13:30 | 752 | 752
2016-08-29 14:00 | 765 | 765
2016-08-29 14:30 | 777 | 777
2016-08-29 15:00 | 801 | 801
2016-08-29 15:30 | 820 | 818
2016-08-29 16:00 | 856 | 855
2016-08-29 16:30 | 888 | 887
2016-08-29 17:00 | 938 | 936
2016-08-29 17:30 | 982 | 976
2016-08-29 18:00 | 1019 | 1015
2016-08-29 18:30 | 1042 | 1037
2016-08-29 19:00 | 1039 | 1032
2016-08-29 19:30 | 1012 | 1002
2016-08-29 20:00 | 986 | 982
2016-08-29 20:30 | 990 | 986
2016-08-29 21:00 | 941 | 936
2016-08-29 21:30 | 900 | 894
2016-08-29 22:00 | 862 | 854
2016-08-29 22:30 | 830 | 828
2016-08-29 23:00 | 830 | 827
2016-08-29 23:30 | 779 | 774
2016-08-30 | 723 | 719
2016-08-30 00:30 | 680 | 674
2016-08-30 01:00 | 651 | 642
2016-08-30 01:30 | 626 | 615
2016-08-30 02:00 | 606 | 593
2016-08-30 02:30 | 589 | 573
2016-08-30 03:00 | 576 | 560
2016-08-30 03:30 | 575 | 558
2016-08-30 04:00 | 575 | 559
2016-08-30 04:30 | 589 | 575
2016-08-30 05:00 | 609 | 598
2016-08-30 05:30 | 663 | 658
2016-08-30 06:00 | 731 | 717
2016-08-30 06:30 | 797 | 783
2016-08-30 07:00 | 850 | 845
2016-08-30 07:30 | 909 | 906
2016-08-30 08:00 | 910 | 906
2016-08-30 08:30 | 877 | 873
2016-08-30 09:00 | 843 | 840
2016-08-30 09:30 | 817 | 814
2016-08-30 10:00 | 798 | 797
2016-08-30 10:30 | 790 | 790
2016-08-30 11:00 | 777 | 776
2016-08-30 11:30 | 769 | 768
2016-08-30 12:00 | 768 | 767
2016-08-30 12:30 | 765 | 764
2016-08-30 13:00 | 756 | 755
2016-08-30 13:30 | 755 | 754
2016-08-30 14:00 | 780 | 779
2016-08-30 14:30 | 799 | 799
2016-08-30 15:00 | 809 | 808
2016-08-30 15:30 | 824 | 823
2016-08-30 16:00 | 848 | 846
2016-08-30 16:30 | 880 | 878
2016-08-30 17:00 | 923 | 921
2016-08-30 17:30 | 946 | 945
2016-08-30 18:00 | 996 | 996
2016-08-30 18:30 | 1030 | 1027
2016-08-30 19:00 | 1031 | 1025
2016-08-30 19:30 | 1005 | 997
2016-08-30 20:00 | 987 | 981
2016-08-30 20:30 | 979 | 973
2016-08-30 21:00 | 927 | 921
2016-08-30 21:30 | 895 | 884
2016-08-30 22:00 | 866 | 857
2016-08-30 22:30 | 832 | 825
2016-08-30 23:00 | 823 | 822
2016-08-30 23:30 | 777 | 773
2016-08-31 | 724 | 718
2016-08-31 00:30 | 680 | 672
2016-08-31 01:00 | 656 | 644
2016-08-31 01:30 | 626 | 615
2016-08-31 02:00 | 601 | 590
2016-08-31 02:30 | 586 | 572
2016-08-31 03:00 | 576 | 562
2016-08-31 03:30 | 571 | 556
2016-08-31 04:00 | 574 | 559
2016-08-31 04:30 | 590 | 578
2016-08-31 05:00 | 616 | 607
2016-08-31 05:30 | 676 | 669
2016-08-31 06:00 | 740 | 729
2016-08-31 06:30 | 822 | 815
2016-08-31 07:00 | 893 | 883
2016-08-31 07:30 | 944 | 940
2016-08-31 08:00 | 939 | 936
2016-08-31 08:30 | 926 | 921
2016-08-31 09:00 | 896 | 884
2016-08-31 09:30 | 881 | 869
2016-08-31 10:00 | 854 | 846
2016-08-31 10:30 | 821 | 812
2016-08-31 11:00 | 840 | 832
2016-08-31 11:30 | 836 | 829
2016-08-31 12:00 | 882 | 877
2016-08-31 12:30 | 861 | 855
2016-08-31 13:00 | 843 | 836
2016-08-31 13:30 | 851 | 845
2016-08-31 14:00 | 872 | 867
2016-08-31 14:30 | 869 | 863
2016-08-31 15:00 | 883 | 877
2016-08-31 15:30 | 886 | 879
2016-08-31 16:00 | 900 | 893
2016-08-31 16:30 | 933 | 926
2016-08-31 17:00 | 973 | 968
2016-08-31 17:30 | 1011 | 1000
2016-08-31 18:00 | 1049 | 1043
2016-08-31 18:30 | 1065 | 1055
2016-08-31 19:00 | 1066 | 1053
2016-08-31 19:30 | 1041 | 1027
2016-08-31 20:00 | 1014 | 999
2016-08-31 20:30 | 997 | 981
2016-08-31 21:00 | 954 | 939
2016-08-31 21:30 | 903 | 896
2016-08-31 22:00 | 870 | 859
2016-08-31 22:30 | 836 | 825
2016-08-31 23:00 | 837 | 832
2016-08-31 23:30 | 783 | 772
2016-09-01 | 715 | 707
2016-09-01 00:30 | 662 | 655
2016-09-01 01:00 | 630 | 621
2016-09-01 01:30 | 602 | 592
2016-09-01 02:00 | 573 | 560
2016-09-01 02:30 | 568 | 554
2016-09-01 03:00 | 576 | 562
2016-09-01 03:30 | 577 | 562
2016-09-01 04:00 | 577 | 563
2016-09-01 04:30 | 593 | 580
2016-09-01 05:00 | 618 | 608
2016-09-01 05:30 | 658 | 652
2016-09-01 06:00 | 704 | 699
2016-09-01 06:30 | 761 | 759
2016-09-01 07:00 | 818 | 815
2016-09-01 07:30 | 877 | 873
2016-09-01 08:00 | 879 | 876
2016-09-01 08:30 | 843 | 840
2016-09-01 09:00 | 829 | 825
2016-09-01 09:30 | 815 | 811
2016-09-01 10:00 | 792 | 788
2016-09-01 10:30 | 794 | 792
2016-09-01 11:00 | 776 | 774
2016-09-01 11:30 | 769 | 767
2016-09-01 12:00 | 773 | 771
2016-09-01 12:30 | 769 | 767
2016-09-01 13:00 | 790 | 789
2016-09-01 13:30 | 795 | 793
2016-09-01 14:00 | 834 | 833
2016-09-01 14:30 | 836 | 836
2016-09-01 15:00 | 848 | 847
2016-09-01 15:30 | 864 | 863
2016-09-01 16:00 | 895 | 894
2016-09-01 16:30 | 909 | 908
2016-09-01 17:00 | 943 | 941
2016-09-01 17:30 | 963 | 960
2016-09-01 18:00 | 1012 | 1008
2016-09-01 18:30 | 1029 | 1022
2016-09-01 19:00 | 1037 | 1027
2016-09-01 19:30 | 1015 | 1001
2016-09-01 20:00 | 1000 | 991
2016-09-01 20:30 | 985 | 975
2016-09-01 21:00 | 939 | 929
2016-09-01 21:30 | 882 | 876
2016-09-01 22:00 | 844 | 835
2016-09-01 22:30 | 828 | 818
2016-09-01 23:00 | 833 | 825
2016-09-01 23:30 | 782 | 772
2016-09-02 | 717 | 713
2016-09-02 00:30 | 672 | 667
2016-09-02 01:00 | 647 | 639
2016-09-02 01:30 | 626 | 617
2016-09-02 02:00 | 613 | 601
2016-09-02 02:30 | 603 | 590
2016-09-02 03:00 | 595 | 581
2016-09-02 03:30 | 591 | 577
2016-09-02 04:00 | 596 | 582
2016-09-02 04:30 | 601 | 589
2016-09-02 05:00 | 617 | 608
2016-09-02 05:30 | 659 | 652
2016-09-02 06:00 | 712 | 698
2016-09-02 06:30 | 783 | 777
2016-09-02 07:00 | 850 | 845
2016-09-02 07:30 | 920 | 911
2016-09-02 08:00 | 937 | 930
2016-09-02 08:30 | 929 | 924
2016-09-02 09:00 | 897 | 893
2016-09-02 09:30 | 895 | 891
2016-09-02 10:00 | 891 | 888
2016-09-02 10:30 | 910 | 908
2016-09-02 11:00 | 909 | 907
2016-09-02 11:30 | 882 | 879
2016-09-02 12:00 | 880 | 877
2016-09-02 12:30 | 875 | 872
2016-09-02 13:00 | 852 | 848
2016-09-02 13:30 | 830 | 826
2016-09-02 14:00 | 825 | 820
2016-09-02 14:30 | 822 | 815
2016-09-02 15:00 | 834 | 828
2016-09-02 15:30 | 850 | 844
2016-09-02 16:00 | 872 | 867
2016-09-02 16:30 | 897 | 892
2016-09-02 17:00 | 928 | 924
2016-09-02 17:30 | 933 | 929
2016-09-02 18:00 | 944 | 941
2016-09-02 18:30 | 950 | 945
2016-09-02 19:00 | 957 | 950
2016-09-02 19:30 | 937 | 927
2016-09-02 20:00 | 926 | 919
2016-09-02 20:30 | 911 | 905
2016-09-02 21:00 | 865 | 863
2016-09-02 21:30 | 813 | 809
2016-09-02 22:00 | 766 | 766
2016-09-02 22:30 | 772 | 772
2016-09-02 23:00 | 752 | 752
2016-09-02 23:30 | 707 | 706
2016-09-03 | 678 | 676
2016-09-03 00:30 | 627 | 622
2016-09-03 01:00 | 629 | 622
2016-09-03 01:30 | 603 | 594
2016-09-03 02:00 | 577 | 565
2016-09-03 02:30 | 566 | 550
2016-09-03 03:00 | 557 | 540
2016-09-03 03:30 | 554 | 537
2016-09-03 04:00 | 557 | 540
2016-09-03 04:30 | 558 | 542
2016-09-03 05:00 | 558 | 543
2016-09-03 05:30 | 570 | 558
2016-09-03 06:00 | 580 | 568
2016-09-03 06:30 | 610 | 599
2016-09-03 07:00 | 637 | 629
2016-09-03 07:30 | 662 | 658
2016-09-03 08:00 | 682 | 680
2016-09-03 08:30 | 709 | 709
2016-09-03 09:00 | 711 | 711
2016-09-03 09:30 | 704 | 704
2016-09-03 10:00 | 682 | 682
2016-09-03 10:30 | 656 | 656
2016-09-03 11:00 | 636 | 636
2016-09-03 11:30 | 618 | 618
2016-09-03 12:00 | 608 | 608
2016-09-03 12:30 | 603 | 603
2016-09-03 13:00 | 606 | 605
2016-09-03 13:30 | 606 | 605
2016-09-03 14:00 | 611 | 610
2016-09-03 14:30 | 628 | 627
2016-09-03 15:00 | 648 | 647
2016-09-03 15:30 | 659 | 659
2016-09-03 16:00 | 691 | 691
2016-09-03 16:30 | 717 | 716
2016-09-03 17:00 | 728 | 727
2016-09-03 17:30 | 771 | 770
2016-09-03 18:00 | 812 | 812
2016-09-03 18:30 | 849 | 849
2016-09-03 19:00 | 854 | 853
2016-09-03 19:30 | 838 | 836
2016-09-03 20:00 | 826 | 822
2016-09-03 20:30 | 814 | 813
2016-09-03 21:00 | 781 | 779
2016-09-03 21:30 | 758 | 755
2016-09-03 22:00 | 749 | 747
2016-09-03 22:30 | 726 | 724
2016-09-03 23:00 | 724 | 722
2016-09-03 23:30 | 685 | 682
2016-09-04 | 654 | 647
2016-09-04 00:30 | 622 | 612
2016-09-04 01:00 | 606 | 598
2016-09-04 01:30 | 585 | 575
2016-09-04 02:00 | 569 | 557
2016-09-04 02:30 | 558 | 543
2016-09-04 03:00 | 551 | 536
2016-09-04 03:30 | 547 | 531
2016-09-04 04:00 | 544 | 527
2016-09-04 04:30 | 548 | 531
2016-09-04 05:00 | 548 | 531
2016-09-04 05:30 | 558 | 542
2016-09-04 06:00 | 571 | 556
2016-09-04 06:30 | 586 | 571
2016-09-04 07:00 | 599 | 586
2016-09-04 07:30 | 618 | 608
2016-09-04 08:00 | 636 | 629
2016-09-04 08:30 | 644 | 639
2016-09-04 09:00 | 645 | 642
2016-09-04 09:30 | 638 | 635
2016-09-04 10:00 | 631 | 629
2016-09-04 10:30 | 618 | 616
2016-09-04 11:00 | 604 | 602
2016-09-04 11:30 | 589 | 587
2016-09-04 12:00 | 575 | 573
2016-09-04 12:30 | 570 | 567
2016-09-04 13:00 | 572 | 569
2016-09-04 13:30 | 570 | 568
2016-09-04 14:00 | 581 | 578
2016-09-04 14:30 | 589 | 587
2016-09-04 15:00 | 615 | 613
2016-09-04 15:30 | 636 | 634
2016-09-04 16:00 | 668 | 667
2016-09-04 16:30 | 705 | 705
2016-09-04 17:00 | 741 | 740
2016-09-04 17:30 | 771 | 771
2016-09-04 18:00 | 831 | 831
2016-09-04 18:30 | 864 | 863
2016-09-04 19:00 | 868 | 868
2016-09-04 19:30 | 854 | 852
2016-09-04 20:00 | 843 | 842
2016-09-04 20:30 | 847 | 846
2016-09-04 21:00 | 818 | 817
2016-09-04 21:30 | 784 | 780
2016-09-04 22:00 | 751 | 749
2016-09-04 22:30 | 728 | 726
2016-09-04 23:00 | 730 | 729
2016-09-04 23:30 | 682 | 680
2016-09-05 | 644 | 639
2016-09-05 00:30 | 610 | 602
2016-09-05 01:00 | 588 | 577
2016-09-05 01:30 | 570 | 558
2016-09-05 02:00 | 556 | 542
2016-09-05 02:30 | 548 | 533
2016-09-05 03:00 | 544 | 528
2016-09-05 03:30 | 544 | 528
2016-09-05 04:00 | 545 | 530
2016-09-05 04:30 | 558 | 544
2016-09-05 05:00 | 579 | 569
2016-09-05 05:30 | 610 | 604
2016-09-05 06:00 | 660 | 654
2016-09-05 06:30 | 734 | 729
2016-09-05 07:00 | 811 | 804
2016-09-05 07:30 | 868 | 859
2016-09-05 08:00 | 873 | 862
2016-09-05 08:30 | 845 | 834
2016-09-05 09:00 | 806 | 791
2016-09-05 09:30 | 779 | 765
2016-09-05 10:00 | 727 | 725
2016-09-05 10:30 | 730 | 729
2016-09-05 11:00 | 720 | 718
2016-09-05 11:30 | 735 | 733
2016-09-05 12:00 | 743 | 741
2016-09-05 12:30 | 730 | 727
2016-09-05 13:00 | 733 | 730
2016-09-05 13:30 | 734 | 732
2016-09-05 14:00 | 741 | 739
2016-09-05 14:30 | 754 | 752
2016-09-05 15:00 | 770 | 768
2016-09-05 15:30 | 781 | 780
2016-09-05 16:00 | 797 | 794
2016-09-05 16:30 | 824 | 820
2016-09-05 17:00 | 858 | 856
2016-09-05 17:30 | 900 | 896
2016-09-05 18:00 | 954 | 951
2016-09-05 18:30 | 979 | 971
2016-09-05 19:00 | 984 | 975
2016-09-05 19:30 | 951 | 943
2016-09-05 20:00 | 930 | 928
2016-09-05 20:30 | 919 | 916
2016-09-05 21:00 | 884 | 879
2016-09-05 21:30 | 839 | 832
2016-09-05 22:00 | 784 | 782
2016-09-05 22:30 | 761 | 759
2016-09-05 23:00 | 746 | 745
2016-09-05 23:30 | 690 | 686
2016-09-06 | 671 | 665
2016-09-06 00:30 | 627 | 623
2016-09-06 01:00 | 603 | 598
2016-09-06 01:30 | 583 | 576
2016-09-06 02:00 | 567 | 559
2016-09-06 02:30 | 559 | 551
2016-09-06 03:00 | 552 | 543
2016-09-06 03:30 | 554 | 543
2016-09-06 04:00 | 557 | 546
2016-09-06 04:30 | 568 | 559
2016-09-06 05:00 | 586 | 579
2016-09-06 05:30 | 624 | 620
2016-09-06 06:00 | 660 | 654
2016-09-06 06:30 | 744 | 733
2016-09-06 07:00 | 838 | 822
2016-09-06 07:30 | 887 | 874
2016-09-06 08:00 | 880 | 867
2016-09-06 08:30 | 848 | 835
2016-09-06 09:00 | 814 | 800
2016-09-06 09:30 | 786 | 772
2016-09-06 10:00 | 777 | 764
2016-09-06 10:30 | 771 | 757
2016-09-06 11:00 | 776 | 763
2016-09-06 11:30 | 776 | 763
2016-09-06 12:00 | 781 | 769
2016-09-06 12:30 | 780 | 768
2016-09-06 13:00 | 773 | 771
2016-09-06 13:30 | 768 | 766
2016-09-06 14:00 | 771 | 769
2016-09-06 14:30 | 781 | 779
2016-09-06 15:00 | 784 | 782
2016-09-06 15:30 | 799 | 797
2016-09-06 16:00 | 816 | 814
2016-09-06 16:30 | 845 | 843
2016-09-06 17:00 | 877 | 872
2016-09-06 17:30 | 907 | 899
2016-09-06 18:00 | 954 | 949
2016-09-06 18:30 | 984 | 969
2016-09-06 19:00 | 980 | 970
2016-09-06 19:30 | 957 | 942
2016-09-06 20:00 | 934 | 918
2016-09-06 20:30 | 910 | 892
2016-09-06 21:00 | 861 | 851
2016-09-06 21:30 | 818 | 810
2016-09-06 22:00 | 788 | 785
2016-09-06 22:30 | 736 | 734
2016-09-06 23:00 | 725 | 724
2016-09-06 23:30 | 690 | 689
2016-09-07 | 671 | 668
2016-09-07 00:30 | 635 | 630
2016-09-07 01:00 | 606 | 599
2016-09-07 01:30 | 588 | 580
2016-09-07 02:00 | 571 | 561
2016-09-07 02:30 | 550 | 538
2016-09-07 03:00 | 557 | 546
2016-09-07 03:30 | 555 | 544
2016-09-07 04:00 | 553 | 542
2016-09-07 04:30 | 541 | 532
2016-09-07 05:00 | 556 | 547
2016-09-07 05:30 | 618 | 614
2016-09-07 06:00 | 647 | 644
2016-09-07 06:30 | 725 | 724
2016-09-07 07:00 | 790 | 788
2016-09-07 07:30 | 825 | 820
2016-09-07 08:00 | 863 | 858
2016-09-07 08:30 | 846 | 841
2016-09-07 09:00 | 805 | 800
2016-09-07 09:30 | 780 | 774
2016-09-07 10:00 | 797 | 793
2016-09-07 10:30 | 809 | 805
2016-09-07 11:00 | 784 | 779
2016-09-07 11:30 | 776 | 770
2016-09-07 12:00 | 780 | 775
2016-09-07 12:30 | 786 | 781
2016-09-07 13:00 | 780 | 775
2016-09-07 13:30 | 779 | 773
2016-09-07 14:00 | 782 | 777
2016-09-07 14:30 | 797 | 791
2016-09-07 15:00 | 794 | 789
2016-09-07 15:30 | 756 | 749
2016-09-07 16:00 | 761 | 755
2016-09-07 16:30 | 793 | 787
2016-09-07 17:00 | 832 | 828
2016-09-07 17:30 | 861 | 855
2016-09-07 18:00 | 893 | 886
2016-09-07 18:30 | 911 | 905
2016-09-07 19:00 | 911 | 906
2016-09-07 19:30 | 889 | 881
2016-09-07 20:00 | 865 | 861
2016-09-07 20:30 | 851 | 846
2016-09-07 21:00 | 821 | 811
2016-09-07 21:30 | 785 | 770
2016-09-07 22:00 | 771 | 757
2016-09-07 22:30 | 729 | 722
2016-09-07 23:00 | 715 | 712
2016-09-07 23:30 | 664 | 661
2016-09-08 | 654 | 650
2016-09-08 00:30 | 597 | 591
2016-09-08 01:00 | 579 | 571
2016-09-08 01:30 | 540 | 529
2016-09-08 02:00 | 537 | 525
2016-09-08 02:30 | 560 | 547
2016-09-08 03:00 | 527 | 513
2016-09-08 03:30 | 528 | 515
2016-09-08 04:00 | 481 | 466
2016-09-08 04:30 | 529 | 518
2016-09-08 05:00 | 526 | 517
2016-09-08 05:30 | 572 | 567
2016-09-08 06:00 | 627 | 623
2016-09-08 06:30 | 673 | 670
2016-09-08 07:00 | 732 | 732
2016-09-08 07:30 | 773 | 771
2016-09-08 08:00 | 792 | 791
2016-09-08 08:30 | 792 | 792
2016-09-08 09:00 | 765 | 765
2016-09-08 09:30 | 761 | 761
2016-09-08 10:00 | 769 | 769
2016-09-08 10:30 | 735 | 735
2016-09-08 11:00 | 720 | 719
2016-09-08 11:30 | 718 | 717
2016-09-08 12:00 | 723 | 722
2016-09-08 12:30 | 728 | 727
2016-09-08 13:00 | 724 | 723
2016-09-08 13:30 | 724 | 723
2016-09-08 14:00 | 718 | 716
2016-09-08 14:30 | 701 | 700
2016-09-08 15:00 | 700 | 699
2016-09-08 15:30 | 722 | 721
2016-09-08 16:00 | 754 | 753
2016-09-08 16:30 | 783 | 782
2016-09-08 17:00 | 808 | 808
2016-09-08 17:30 | 830 | 829
2016-09-08 18:00 | 872 | 871
2016-09-08 18:30 | 896 | 895
2016-09-08 19:00 | 906 | 905
2016-09-08 19:30 | 887 | 887
2016-09-08 20:00 | 875 | 875
2016-09-08 20:30 | 847 | 847
2016-09-08 21:00 | 804 | 804
2016-09-08 21:30 | 752 | 752
2016-09-08 22:00 | 736 | 736
2016-09-08 22:30 | 698 | 697
2016-09-08 23:00 | 687 | 685
2016-09-08 23:30 | 660 | 659
2016-09-09 | 659 | 657
2016-09-09 00:30 | 608 | 604
2016-09-09 01:00 | 585 | 580
2016-09-09 01:30 | 550 | 543
2016-09-09 02:00 | 537 | 528
2016-09-09 02:30 | 541 | 531
2016-09-09 03:00 | 538 | 528
2016-09-09 03:30 | 538 | 526
2016-09-09 04:00 | 536 | 524
2016-09-09 04:30 | 546 | 536
2016-09-09 05:00 | 563 | 555
2016-09-09 05:30 | 577 | 572
2016-09-09 06:00 | 577 | 575
2016-09-09 06:30 | 631 | 631
2016-09-09 07:00 | 686 | 686
2016-09-09 07:30 | 727 | 726
2016-09-09 08:00 | 777 | 777
2016-09-09 08:30 | 797 | 797
2016-09-09 09:00 | 776 | 776
2016-09-09 09:30 | 745 | 745
2016-09-09 10:00 | 723 | 723
2016-09-09 10:30 | 703 | 703
2016-09-09 11:00 | 709 | 709
2016-09-09 11:30 | 728 | 727
2016-09-09 12:00 | 731 | 731
2016-09-09 12:30 | 720 | 720
2016-09-09 13:00 | 711 | 711
2016-09-09 13:30 | 696 | 696
2016-09-09 14:00 | 708 | 708
2016-09-09 14:30 | 716 | 716
2016-09-09 15:00 | 725 | 725
2016-09-09 15:30 | 739 | 738
2016-09-09 16:00 | 776 | 776
2016-09-09 16:30 | 781 | 781
2016-09-09 17:00 | 824 | 824
2016-09-09 17:30 | 846 | 845
2016-09-09 18:00 | 868 | 868
2016-09-09 18:30 | 843 | 842
2016-09-09 19:00 | 833 | 832
2016-09-09 19:30 | 812 | 810
2016-09-09 20:00 | 802 | 800
2016-09-09 20:30 | 787 | 786
2016-09-09 21:00 | 754 | 753
2016-09-09 21:30 | 735 | 734
2016-09-09 22:00 | 746 | 744
2016-09-09 22:30 | 743 | 742
2016-09-09 23:00 | 714 | 713
2016-09-09 23:30 | 671 | 669
2016-09-10 | 660 | 655
2016-09-10 00:30 | 614 | 607
2016-09-10 01:00 | 591 | 586
2016-09-10 01:30 | 565 | 559
2016-09-10 02:00 | 549 | 541
2016-09-10 02:30 | 542 | 532
2016-09-10 03:00 | 534 | 523
2016-09-10 03:30 | 528 | 517
2016-09-10 04:00 | 522 | 510
2016-09-10 04:30 | 526 | 513
2016-09-10 05:00 | 530 | 518
2016-09-10 05:30 | 545 | 535
2016-09-10 06:00 | 558 | 549
2016-09-10 06:30 | 585 | 577
2016-09-10 07:00 | 606 | 599
2016-09-10 07:30 | 642 | 638
2016-09-10 08:00 | 673 | 672
2016-09-10 08:30 | 707 | 707
2016-09-10 09:00 | 731 | 730
2016-09-10 09:30 | 728 | 728
2016-09-10 10:00 | 723 | 723
2016-09-10 10:30 | 739 | 739
2016-09-10 11:00 | 739 | 739
2016-09-10 11:30 | 729 | 729
2016-09-10 12:00 | 718 | 718
2016-09-10 12:30 | 718 | 717
2016-09-10 13:00 | 709 | 708
2016-09-10 13:30 | 707 | 706
2016-09-10 14:00 | 706 | 705
2016-09-10 14:30 | 708 | 707
2016-09-10 15:00 | 721 | 720
2016-09-10 15:30 | 675 | 674
2016-09-10 16:00 | 671 | 670
2016-09-10 16:30 | 687 | 686
2016-09-10 17:00 | 724 | 724
2016-09-10 17:30 | 776 | 776
2016-09-10 18:00 | 811 | 811
2016-09-10 18:30 | 810 | 809
2016-09-10 19:00 | 804 | 803
2016-09-10 19:30 | 797 | 794
2016-09-10 20:00 | 799 | 798
2016-09-10 20:30 | 749 | 748
2016-09-10 21:00 | 726 | 725
2016-09-10 21:30 | 707 | 707
2016-09-10 22:00 | 693 | 691
2016-09-10 22:30 | 637 | 636
2016-09-10 23:00 | 655 | 654
2016-09-10 23:30 | 643 | 642
2016-09-11 | 638 | 634
2016-09-11 00:30 | 603 | 597
2016-09-11 01:00 | 579 | 572
2016-09-11 01:30 | 558 | 549
2016-09-11 02:00 | 540 | 529
2016-09-11 02:30 | 531 | 517
2016-09-11 03:00 | 524 | 509
2016-09-11 03:30 | 522 | 507
2016-09-11 04:00 | 517 | 502
2016-09-11 04:30 | 521 | 508
2016-09-11 05:00 | 522 | 511
2016-09-11 05:30 | 529 | 518
2016-09-11 06:00 | 536 | 525
2016-09-11 06:30 | 553 | 540
2016-09-11 07:00 | 562 | 551
2016-09-11 07:30 | 579 | 570
2016-09-11 08:00 | 584 | 577
2016-09-11 08:30 | 602 | 599
2016-09-11 09:00 | 608 | 606
2016-09-11 09:30 | 608 | 606
2016-09-11 10:00 | 601 | 600
2016-09-11 10:30 | 591 | 590
2016-09-11 11:00 | 574 | 572
2016-09-11 11:30 | 568 | 567
2016-09-11 12:00 | 567 | 566
2016-09-11 12:30 | 565 | 564
2016-09-11 13:00 | 569 | 568
2016-09-11 13:30 | 571 | 571
2016-09-11 14:00 | 579 | 578
2016-09-11 14:30 | 595 | 594
2016-09-11 15:00 | 618 | 617
2016-09-11 15:30 | 643 | 643
2016-09-11 16:00 | 676 | 675
2016-09-11 16:30 | 702 | 700
2016-09-11 17:00 | 743 | 742
2016-09-11 17:30 | 769 | 767
2016-09-11 18:00 | 810 | 808
2016-09-11 18:30 | 850 | 846
2016-09-11 19:00 | 858 | 854
2016-09-11 19:30 | 843 | 837
2016-09-11 20:00 | 833 | 825
2016-09-11 20:30 | 821 | 814
2016-09-11 21:00 | 790 | 785
2016-09-11 21:30 | 755 | 754
2016-09-11 22:00 | 734 | 733
2016-09-11 22:30 | 718 | 716
2016-09-11 23:00 | 724 | 723
2016-09-11 23:30 | 689 | 686
2016-09-12 | 646 | 640
2016-09-12 00:30 | 608 | 600
2016-09-12 01:00 | 584 | 574
2016-09-12 01:30 | 565 | 553
2016-09-12 02:00 | 555 | 541
2016-09-12 02:30 | 544 | 529
2016-09-12 03:00 | 542 | 525
2016-09-12 03:30 | 543 | 527
2016-09-12 04:00 | 540 | 525
2016-09-12 04:30 | 553 | 540
2016-09-12 05:00 | 573 | 564
2016-09-12 05:30 | 608 | 604
2016-09-12 06:00 | 651 | 649
2016-09-12 06:30 | 719 | 719
2016-09-12 07:00 | 784 | 783
2016-09-12 07:30 | 816 | 816
2016-09-12 08:00 | 825 | 825
2016-09-12 08:30 | 817 | 816
2016-09-12 09:00 | 795 | 795
2016-09-12 09:30 | 781 | 781
2016-09-12 10:00 | 771 | 771
2016-09-12 10:30 | 767 | 767
2016-09-12 11:00 | 757 | 757
2016-09-12 11:30 | 758 | 758
2016-09-12 12:00 | 751 | 751
2016-09-12 12:30 | 751 | 751
2016-09-12 13:00 | 753 | 753
2016-09-12 13:30 | 753 | 753
2016-09-12 14:00 | 764 | 764
2016-09-12 14:30 | 770 | 770
2016-09-12 15:00 | 781 | 781
2016-09-12 15:30 | 794 | 794
2016-09-12 16:00 | 819 | 819
2016-09-12 16:30 | 848 | 848
2016-09-12 17:00 | 887 | 887
2016-09-12 17:30 | 905 | 904
2016-09-12 18:00 | 935 | 935
2016-09-12 18:30 | 959 | 955
2016-09-12 19:00 | 960 | 955
2016-09-12 19:30 | 925 | 921
2016-09-12 20:00 | 907 | 903
2016-09-12 20:30 | 891 | 889
2016-09-12 21:00 | 851 | 847
2016-09-12 21:30 | 818 | 813
2016-09-12 22:00 | 781 | 780
2016-09-12 22:30 | 755 | 754
2016-09-12 23:00 | 747 | 745
2016-09-12 23:30 | 704 | 702
2016-09-13 | 662 | 659
2016-09-13 00:30 | 624 | 618
2016-09-13 01:00 | 602 | 594
2016-09-13 01:30 | 583 | 574
2016-09-13 02:00 | 569 | 559
2016-09-13 02:30 | 564 | 553
2016-09-13 03:00 | 556 | 544
2016-09-13 03:30 | 553 | 541
2016-09-13 04:00 | 557 | 546
2016-09-13 04:30 | 569 | 559
2016-09-13 05:00 | 587 | 579
2016-09-13 05:30 | 619 | 614
2016-09-13 06:00 | 653 | 650
2016-09-13 06:30 | 718 | 716
2016-09-13 07:00 | 783 | 782
2016-09-13 07:30 | 840 | 840
2016-09-13 08:00 | 858 | 857
2016-09-13 08:30 | 860 | 858
2016-09-13 09:00 | 827 | 824
2016-09-13 09:30 | 815 | 813
2016-09-13 10:00 | 804 | 802
2016-09-13 10:30 | 797 | 795
2016-09-13 11:00 | 787 | 785
2016-09-13 11:30 | 779 | 777
2016-09-13 12:00 | 783 | 782
2016-09-13 12:30 | 781 | 780
2016-09-13 13:00 | 776 | 775
2016-09-13 13:30 | 779 | 778
2016-09-13 14:00 | 797 | 797
2016-09-13 14:30 | 807 | 807
2016-09-13 15:00 | 811 | 810
2016-09-13 15:30 | 828 | 827
2016-09-13 16:00 | 857 | 856
2016-09-13 16:30 | 883 | 882
2016-09-13 17:00 | 910 | 909
2016-09-13 17:30 | 932 | 927
2016-09-13 18:00 | 951 | 945
2016-09-13 18:30 | 967 | 964
2016-09-13 19:00 | 969 | 965
2016-09-13 19:30 | 942 | 936
2016-09-13 20:00 | 930 | 927
2016-09-13 20:30 | 915 | 914
2016-09-13 21:00 | 875 | 875
2016-09-13 21:30 | 828 | 828
2016-09-13 22:00 | 798 | 797
2016-09-13 22:30 | 776 | 776
2016-09-13 23:00 | 776 | 776
2016-09-13 23:30 | 727 | 726
2016-09-14 | 678 | 675
2016-09-14 00:30 | 634 | 630
2016-09-14 01:00 | 607 | 600
2016-09-14 01:30 | 586 | 578
2016-09-14 02:00 | 569 | 559
2016-09-14 02:30 | 561 | 550
2016-09-14 03:00 | 556 | 543
2016-09-14 03:30 | 554 | 542
2016-09-14 04:00 | 556 | 543
2016-09-14 04:30 | 566 | 555
2016-09-14 05:00 | 582 | 573
2016-09-14 05:30 | 620 | 616
2016-09-14 06:00 | 661 | 659
2016-09-14 06:30 | 727 | 726
2016-09-14 07:00 | 781 | 781
2016-09-14 07:30 | 826 | 826
2016-09-14 08:00 | 845 | 845
2016-09-14 08:30 | 808 | 808
2016-09-14 09:00 | 780 | 780
2016-09-14 09:30 | 775 | 775
2016-09-14 10:00 | 771 | 770
2016-09-14 10:30 | 768 | 767
2016-09-14 11:00 | 762 | 761
2016-09-14 11:30 | 751 | 750
2016-09-14 12:00 | 754 | 753
2016-09-14 12:30 | 761 | 760
2016-09-14 13:00 | 765 | 765
2016-09-14 13:30 | 777 | 777
2016-09-14 14:00 | 830 | 829
2016-09-14 14:30 | 839 | 838
2016-09-14 15:00 | 843 | 842
2016-09-14 15:30 | 867 | 867
2016-09-14 16:00 | 890 | 890
2016-09-14 16:30 | 903 | 903
2016-09-14 17:00 | 932 | 932
2016-09-14 17:30 | 946 | 946
2016-09-14 18:00 | 961 | 960
2016-09-14 18:30 | 961 | 961
2016-09-14 19:00 | 962 | 962
2016-09-14 19:30 | 934 | 934
2016-09-14 20:00 | 925 | 925
2016-09-14 20:30 | 914 | 914
2016-09-14 21:00 | 874 | 874
2016-09-14 21:30 | 837 | 837
2016-09-14 22:00 | 796 | 796
2016-09-14 22:30 | 780 | 780
2016-09-14 23:00 | 774 | 774
2016-09-14 23:30 | 714 | 713
2016-09-15 | 665 | 662
2016-09-15 00:30 | 625 | 620
2016-09-15 01:00 | 601 | 594
2016-09-15 01:30 | 579 | 569
2016-09-15 02:00 | 567 | 556
2016-09-15 02:30 | 559 | 545
2016-09-15 03:00 | 556 | 541
2016-09-15 03:30 | 556 | 540
2016-09-15 04:00 | 559 | 545
2016-09-15 04:30 | 572 | 560
2016-09-15 05:00 | 585 | 574
2016-09-15 05:30 | 618 | 612
2016-09-15 06:00 | 660 | 657
2016-09-15 06:30 | 718 | 715
2016-09-15 07:00 | 786 | 785
2016-09-15 07:30 | 854 | 853
2016-09-15 08:00 | 882 | 881
2016-09-15 08:30 | 885 | 885
2016-09-15 09:00 | 864 | 864
2016-09-15 09:30 | 860 | 859
2016-09-15 10:00 | 858 | 858
2016-09-15 10:30 | 847 | 847
2016-09-15 11:00 | 855 | 855
2016-09-15 11:30 | 897 | 897
2016-09-15 12:00 | 881 | 881
2016-09-15 12:30 | 855 | 854
2016-09-15 13:00 | 854 | 854
2016-09-15 13:30 | 871 | 871
2016-09-15 14:00 | 869 | 869
2016-09-15 14:30 | 884 | 884
2016-09-15 15:00 | 883 | 883
2016-09-15 15:30 | 885 | 885
2016-09-15 16:00 | 903 | 903
2016-09-15 16:30 | 926 | 926
2016-09-15 17:00 | 940 | 940
2016-09-15 17:30 | 949 | 949
2016-09-15 18:00 | 951 | 951
2016-09-15 18:30 | 950 | 949
2016-09-15 19:00 | 960 | 960
2016-09-15 19:30 | 941 | 940
2016-09-15 20:00 | 928 | 927
2016-09-15 20:30 | 918 | 918
2016-09-15 21:00 | 885 | 884
2016-09-15 21:30 | 841 | 839
2016-09-15 22:00 | 813 | 808
2016-09-15 22:30 | 792 | 790
2016-09-15 23:00 | 799 | 796
2016-09-15 23:30 | 743 | 738
2016-09-16 | 692 | 688
2016-09-16 00:30 | 657 | 650
2016-09-16 01:00 | 631 | 621
2016-09-16 01:30 | 611 | 600
2016-09-16 02:00 | 589 | 576
2016-09-16 02:30 | 579 | 564
2016-09-16 03:00 | 572 | 556
2016-09-16 03:30 | 575 | 559
2016-09-16 04:00 | 578 | 563
2016-09-16 04:30 | 585 | 572
2016-09-16 05:00 | 600 | 589
2016-09-16 05:30 | 628 | 621
2016-09-16 06:00 | 665 | 660
2016-09-16 06:30 | 733 | 731
2016-09-16 07:00 | 789 | 788
2016-09-16 07:30 | 827 | 825
2016-09-16 08:00 | 844 | 839
2016-09-16 08:30 | 816 | 812
2016-09-16 09:00 | 800 | 797
2016-09-16 09:30 | 785 | 782
2016-09-16 10:00 | 795 | 791
2016-09-16 10:30 | 829 | 825
2016-09-16 11:00 | 809 | 805
2016-09-16 11:30 | 797 | 792
2016-09-16 12:00 | 801 | 797
2016-09-16 12:30 | 785 | 780
2016-09-16 13:00 | 785 | 779
2016-09-16 13:30 | 785 | 778
2016-09-16 14:00 | 801 | 795
2016-09-16 14:30 | 805 | 799
2016-09-16 15:00 | 811 | 805
2016-09-16 15:30 | 820 | 813
2016-09-16 16:00 | 841 | 834
2016-09-16 16:30 | 861 | 854
2016-09-16 17:00 | 878 | 872
2016-09-16 17:30 | 883 | 875
2016-09-16 18:00 | 893 | 886
2016-09-16 18:30 | 912 | 907
2016-09-16 19:00 | 917 | 911
2016-09-16 19:30 | 905 | 897
2016-09-16 20:00 | 888 | 886
2016-09-16 20:30 | 873 | 873
2016-09-16 21:00 | 842 | 842
2016-09-16 21:30 | 813 | 813
2016-09-16 22:00 | 788 | 787
2016-09-16 22:30 | 775 | 774
2016-09-16 23:00 | 783 | 783
2016-09-16 23:30 | 727 | 726
2016-09-17 | 678 | 675
2016-09-17 00:30 | 632 | 625
2016-09-17 01:00 | 612 | 603
2016-09-17 01:30 | 589 | 577
2016-09-17 02:00 | 573 | 558
2016-09-17 02:30 | 563 | 547
2016-09-17 03:00 | 556 | 538
2016-09-17 03:30 | 557 | 539
2016-09-17 04:00 | 555 | 537
2016-09-17 04:30 | 557 | 539
2016-09-17 05:00 | 561 | 544
2016-09-17 05:30 | 570 | 555
2016-09-17 06:00 | 582 | 566
2016-09-17 06:30 | 600 | 586
2016-09-17 07:00 | 615 | 605
2016-09-17 07:30 | 635 | 629
2016-09-17 08:00 | 649 | 646
2016-09-17 08:30 | 666 | 665
2016-09-17 09:00 | 671 | 671
2016-09-17 09:30 | 672 | 672
2016-09-17 10:00 | 678 | 678
2016-09-17 10:30 | 674 | 674
2016-09-17 11:00 | 672 | 672
2016-09-17 11:30 | 661 | 661
2016-09-17 12:00 | 664 | 664
2016-09-17 12:30 | 652 | 652
2016-09-17 13:00 | 656 | 656
2016-09-17 13:30 | 658 | 657
2016-09-17 14:00 | 668 | 668
2016-09-17 14:30 | 684 | 684
2016-09-17 15:00 | 719 | 719
2016-09-17 15:30 | 748 | 748
2016-09-17 16:00 | 758 | 757
2016-09-17 16:30 | 765 | 764
2016-09-17 17:00 | 784 | 783
2016-09-17 17:30 | 795 | 794
2016-09-17 18:00 | 812 | 811
2016-09-17 18:30 | 843 | 841
2016-09-17 19:00 | 852 | 851
2016-09-17 19:30 | 832 | 829
2016-09-17 20:00 | 821 | 820
2016-09-17 20:30 | 816 | 814
2016-09-17 21:00 | 783 | 783
2016-09-17 21:30 | 767 | 766
2016-09-17 22:00 | 753 | 751
2016-09-17 22:30 | 739 | 737
2016-09-17 23:00 | 752 | 751
2016-09-17 23:30 | 717 | 715
2016-09-18 | 683 | 680
2016-09-18 00:30 | 637 | 631
2016-09-18 01:00 | 614 | 605
2016-09-18 01:30 | 599 | 591
2016-09-18 02:00 | 577 | 565
2016-09-18 02:30 | 568 | 554
2016-09-18 03:00 | 565 | 551
2016-09-18 03:30 | 561 | 547
2016-09-18 04:00 | 558 | 543
2016-09-18 04:30 | 557 | 542
2016-09-18 05:00 | 556 | 542
2016-09-18 05:30 | 566 | 554
2016-09-18 06:00 | 576 | 565
2016-09-18 06:30 | 593 | 581
2016-09-18 07:00 | 611 | 600
2016-09-18 07:30 | 639 | 631
2016-09-18 08:00 | 669 | 665
2016-09-18 08:30 | 696 | 694
2016-09-18 09:00 | 735 | 734
2016-09-18 09:30 | 764 | 764
2016-09-18 10:00 | 774 | 774
2016-09-18 10:30 | 756 | 756
2016-09-18 11:00 | 769 | 769
2016-09-18 11:30 | 748 | 748
2016-09-18 12:00 | 742 | 742
2016-09-18 12:30 | 762 | 762
2016-09-18 13:00 | 777 | 777
2016-09-18 13:30 | 771 | 770
2016-09-18 14:00 | 760 | 759
2016-09-18 14:30 | 750 | 750
2016-09-18 15:00 | 751 | 750
2016-09-18 15:30 | 760 | 760
2016-09-18 16:00 | 778 | 778
2016-09-18 16:30 | 798 | 798
2016-09-18 17:00 | 829 | 829
2016-09-18 17:30 | 850 | 849
2016-09-18 18:00 | 865 | 864
2016-09-18 18:30 | 885 | 878
2016-09-18 19:00 | 890 | 882
2016-09-18 19:30 | 875 | 867
2016-09-18 20:00 | 853 | 852
2016-09-18 20:30 | 847 | 844
2016-09-18 21:00 | 814 | 813
2016-09-18 21:30 | 786 | 786
2016-09-18 22:00 | 757 | 756
2016-09-18 22:30 | 740 | 738
2016-09-18 23:00 | 751 | 750
2016-09-18 23:30 | 708 | 706
2016-09-19 | 662 | 657
2016-09-19 00:30 | 622 | 615
2016-09-19 01:00 | 604 | 595
2016-09-19 01:30 | 580 | 570
2016-09-19 02:00 | 572 | 559
2016-09-19 02:30 | 567 | 553
2016-09-19 03:00 | 561 | 547
2016-09-19 03:30 | 559 | 545
2016-09-19 04:00 | 560 | 546
2016-09-19 04:30 | 569 | 557
2016-09-19 05:00 | 584 | 574
2016-09-19 05:30 | 613 | 607
2016-09-19 06:00 | 645 | 641
2016-09-19 06:30 | 706 | 705
2016-09-19 07:00 | 760 | 759
2016-09-19 07:30 | 816 | 816
2016-09-19 08:00 | 846 | 846
2016-09-19 08:30 | 863 | 862
2016-09-19 09:00 | 871 | 871
2016-09-19 09:30 | 842 | 842
2016-09-19 10:00 | 835 | 835
2016-09-19 10:30 | 818 | 818
2016-09-19 11:00 | 809 | 809
2016-09-19 11:30 | 790 | 789
2016-09-19 12:00 | 787 | 786
2016-09-19 12:30 | 783 | 783
2016-09-19 13:00 | 795 | 795
2016-09-19 13:30 | 806 | 805
2016-09-19 14:00 | 804 | 804
2016-09-19 14:30 | 819 | 819
2016-09-19 15:00 | 832 | 832
2016-09-19 15:30 | 827 | 827
2016-09-19 16:00 | 860 | 859
2016-09-19 16:30 | 870 | 869
2016-09-19 17:00 | 901 | 901
2016-09-19 17:30 | 926 | 926
2016-09-19 18:00 | 941 | 941
2016-09-19 18:30 | 959 | 959
2016-09-19 19:00 | 961 | 961
2016-09-19 19:30 | 942 | 940
2016-09-19 20:00 | 920 | 920
2016-09-19 20:30 | 903 | 902
2016-09-19 21:00 | 865 | 862
2016-09-19 21:30 | 825 | 824
2016-09-19 22:00 | 794 | 793
2016-09-19 22:30 | 773 | 771
2016-09-19 23:00 | 778 | 775
2016-09-19 23:30 | 734 | 731
2016-09-20 | 683 | 679
2016-09-20 00:30 | 638 | 633
2016-09-20 01:00 | 610 | 602
2016-09-20 01:30 | 593 | 583
2016-09-20 02:00 | 578 | 567
2016-09-20 02:30 | 567 | 554
2016-09-20 03:00 | 565 | 552
2016-09-20 03:30 | 563 | 551
2016-09-20 04:00 | 565 | 552
2016-09-20 04:30 | 577 | 566
2016-09-20 05:00 | 593 | 584
2016-09-20 05:30 | 628 | 622
2016-09-20 06:00 | 658 | 653
2016-09-20 06:30 | 709 | 707
2016-09-20 07:00 | 760 | 759
2016-09-20 07:30 | 789 | 789
2016-09-20 08:00 | 805 | 800
2016-09-20 08:30 | 799 | 796
2016-09-20 09:00 | 790 | 787
2016-09-20 09:30 | 775 | 772
2016-09-20 10:00 | 757 | 755
2016-09-20 10:30 | 755 | 752
2016-09-20 11:00 | 734 | 732
2016-09-20 11:30 | 720 | 717
2016-09-20 12:00 | 713 | 711
2016-09-20 12:30 | 716 | 714
2016-09-20 13:00 | 728 | 727
2016-09-20 13:30 | 740 | 739
2016-09-20 14:00 | 772 | 770
2016-09-20 14:30 | 806 | 800
2016-09-20 15:00 | 821 | 815
2016-09-20 15:30 | 825 | 819
2016-09-20 16:00 | 852 | 845
2016-09-20 16:30 | 881 | 875
2016-09-20 17:00 | 910 | 905
2016-09-20 17:30 | 923 | 918
2016-09-20 18:00 | 938 | 936
2016-09-20 18:30 | 944 | 942
2016-09-20 19:00 | 945 | 943
2016-09-20 19:30 | 923 | 919
2016-09-20 20:00 | 912 | 909
2016-09-20 20:30 | 900 | 895
2016-09-20 21:00 | 857 | 853
2016-09-20 21:30 | 825 | 822
2016-09-20 22:00 | 786 | 785
2016-09-20 22:30 | 772 | 770
2016-09-20 23:00 | 775 | 772
2016-09-20 23:30 | 732 | 727
2016-09-21 | 673 | 669
2016-09-21 00:30 | 639 | 635
2016-09-21 01:00 | 611 | 605
2016-09-21 01:30 | 592 | 583
2016-09-21 02:00 | 581 | 571
2016-09-21 02:30 | 568 | 558
2016-09-21 03:00 | 567 | 557
2016-09-21 03:30 | 565 | 555
2016-09-21 04:00 | 568 | 558
2016-09-21 04:30 | 577 | 568
2016-09-21 05:00 | 594 | 588
2016-09-21 05:30 | 630 | 626
2016-09-21 06:00 | 671 | 656
2016-09-21 06:30 | 723 | 715
2016-09-21 07:00 | 781 | 779
2016-09-21 07:30 | 830 | 829
2016-09-21 08:00 | 865 | 865
2016-09-21 08:30 | 907 | 907
2016-09-21 09:00 | 917 | 915
2016-09-21 09:30 | 924 | 921
2016-09-21 10:00 | 934 | 931
2016-09-21 10:30 | 931 | 929
2016-09-21 11:00 | 928 | 926
2016-09-21 11:30 | 921 | 918
2016-09-21 12:00 | 904 | 900
2016-09-21 12:30 | 885 | 880
2016-09-21 13:00 | 882 | 877
2016-09-21 13:30 | 884 | 880
2016-09-21 14:00 | 884 | 879
2016-09-21 14:30 | 903 | 900
2016-09-21 15:00 | 914 | 911
2016-09-21 15:30 | 919 | 916
2016-09-21 16:00 | 935 | 932
2016-09-21 16:30 | 950 | 947
2016-09-21 17:00 | 953 | 950
2016-09-21 17:30 | 959 | 955
2016-09-21 18:00 | 968 | 965
2016-09-21 18:30 | 986 | 982
2016-09-21 19:00 | 990 | 985
2016-09-21 19:30 | 970 | 964
2016-09-21 20:00 | 957 | 954
2016-09-21 20:30 | 941 | 938
2016-09-21 21:00 | 895 | 893
2016-09-21 21:30 | 853 | 852
2016-09-21 22:00 | 824 | 822
2016-09-21 22:30 | 800 | 795
2016-09-21 23:00 | 802 | 799
2016-09-21 23:30 | 749 | 749
2016-09-22 | 702 | 701
2016-09-22 00:30 | 671 | 670
2016-09-22 01:00 | 629 | 626
2016-09-22 01:30 | 605 | 600
2016-09-22 02:00 | 590 | 584
2016-09-22 02:30 | 581 | 573
2016-09-22 03:00 | 576 | 569
2016-09-22 03:30 | 580 | 573
2016-09-22 04:00 | 584 | 576
2016-09-22 04:30 | 599 | 593
2016-09-22 05:00 | 616 | 612
2016-09-22 05:30 | 639 | 637
2016-09-22 06:00 | 673 | 671
2016-09-22 06:30 | 741 | 741
2016-09-22 07:00 | 770 | 770
2016-09-22 07:30 | 800 | 799
2016-09-22 08:00 | 801 | 801
2016-09-22 08:30 | 804 | 804
2016-09-22 09:00 | 778 | 777
2016-09-22 09:30 | 759 | 758
2016-09-22 10:00 | 739 | 737
2016-09-22 10:30 | 721 | 720
2016-09-22 11:00 | 705 | 703
2016-09-22 11:30 | 710 | 709
2016-09-22 12:00 | 712 | 710
2016-09-22 12:30 | 722 | 720
2016-09-22 13:00 | 731 | 728
2016-09-22 13:30 | 753 | 750
2016-09-22 14:00 | 774 | 771
2016-09-22 14:30 | 789 | 786
2016-09-22 15:00 | 795 | 793
2016-09-22 15:30 | 818 | 815
2016-09-22 16:00 | 831 | 828
2016-09-22 16:30 | 855 | 852
2016-09-22 17:00 | 878 | 877
2016-09-22 17:30 | 884 | 883
2016-09-22 18:00 | 910 | 910
2016-09-22 18:30 | 938 | 937
2016-09-22 19:00 | 925 | 924
2016-09-22 19:30 | 919 | 918
2016-09-22 20:00 | 926 | 926
2016-09-22 20:30 | 913 | 913
2016-09-22 21:00 | 879 | 878
2016-09-22 21:30 | 840 | 839
2016-09-22 22:00 | 805 | 803
2016-09-22 22:30 | 778 | 776
2016-09-22 23:00 | 781 | 779
2016-09-22 23:30 | 733 | 732
2016-09-23 | 686 | 686
2016-09-23 00:30 | 641 | 640
2016-09-23 01:00 | 615 | 613
2016-09-23 01:30 | 594 | 591
2016-09-23 02:00 | 579 | 575
2016-09-23 02:30 | 572 | 568
2016-09-23 03:00 | 567 | 562
2016-09-23 03:30 | 566 | 561
2016-09-23 04:00 | 570 | 565
2016-09-23 04:30 | 578 | 574
2016-09-23 05:00 | 595 | 592
2016-09-23 05:30 | 621 | 619
2016-09-23 06:00 | 656 | 655
2016-09-23 06:30 | 712 | 712
2016-09-23 07:00 | 757 | 752
2016-09-23 07:30 | 779 | 776
2016-09-23 08:00 | 789 | 788
2016-09-23 08:30 | 786 | 786
2016-09-23 09:00 | 774 | 774
2016-09-23 09:30 | 761 | 761
2016-09-23 10:00 | 752 | 752
2016-09-23 10:30 | 740 | 739
2016-09-23 11:00 | 728 | 727
2016-09-23 11:30 | 722 | 722
2016-09-23 12:00 | 719 | 719
2016-09-23 12:30 | 715 | 715
2016-09-23 13:00 | 720 | 720
2016-09-23 13:30 | 726 | 726
2016-09-23 14:00 | 738 | 738
2016-09-23 14:30 | 752 | 752
2016-09-23 15:00 | 776 | 776
2016-09-23 15:30 | 801 | 801
2016-09-23 16:00 | 825 | 825
2016-09-23 16:30 | 851 | 851
2016-09-23 17:00 | 876 | 876
2016-09-23 17:30 | 880 | 880
2016-09-23 18:00 | 885 | 885
2016-09-23 18:30 | 896 | 896
2016-09-23 19:00 | 906 | 906
2016-09-23 19:30 | 881 | 881
2016-09-23 20:00 | 878 | 878
2016-09-23 20:30 | 867 | 867
2016-09-23 21:00 | 833 | 833
2016-09-23 21:30 | 811 | 810
2016-09-23 22:00 | 782 | 782
2016-09-23 22:30 | 771 | 770
2016-09-23 23:00 | 767 | 767
2016-09-23 23:30 | 728 | 728
2016-09-24 | 681 | 679
2016-09-24 00:30 | 633 | 629
2016-09-24 01:00 | 606 | 600
2016-09-24 01:30 | 580 | 574
2016-09-24 02:00 | 558 | 551
2016-09-24 02:30 | 553 | 545
2016-09-24 03:00 | 546 | 538
2016-09-24 03:30 | 544 | 537
2016-09-24 04:00 | 544 | 536
2016-09-24 04:30 | 546 | 537
2016-09-24 05:00 | 554 | 547
2016-09-24 05:30 | 568 | 562
2016-09-24 06:00 | 578 | 571
2016-09-24 06:30 | 597 | 592
2016-09-24 07:00 | 611 | 608
2016-09-24 07:30 | 639 | 639
2016-09-24 08:00 | 703 | 703
2016-09-24 08:30 | 725 | 723
2016-09-24 09:00 | 682 | 682
2016-09-24 09:30 | 671 | 671
2016-09-24 10:00 | 665 | 665
2016-09-24 10:30 | 655 | 655
2016-09-24 11:00 | 637 | 637
2016-09-24 11:30 | 628 | 626
2016-09-24 12:00 | 618 | 617
2016-09-24 12:30 | 619 | 618
2016-09-24 13:00 | 621 | 620
2016-09-24 13:30 | 631 | 629
2016-09-24 14:00 | 635 | 633
2016-09-24 14:30 | 649 | 647
2016-09-24 15:00 | 664 | 664
2016-09-24 15:30 | 681 | 681
2016-09-24 16:00 | 709 | 708
2016-09-24 16:30 | 736 | 736
2016-09-24 17:00 | 769 | 769
2016-09-24 17:30 | 778 | 778
2016-09-24 18:00 | 787 | 786
2016-09-24 18:30 | 819 | 819
2016-09-24 19:00 | 834 | 834
2016-09-24 19:30 | 813 | 813
2016-09-24 20:00 | 807 | 806
2016-09-24 20:30 | 801 | 801
2016-09-24 21:00 | 777 | 777
2016-09-24 21:30 | 757 | 757
2016-09-24 22:00 | 742 | 741
2016-09-24 22:30 | 731 | 729
2016-09-24 23:00 | 742 | 739
2016-09-24 23:30 | 701 | 697
2016-09-25 | 659 | 655
2016-09-25 00:30 | 615 | 607
2016-09-25 01:00 | 598 | 589
2016-09-25 01:30 | 577 | 566
2016-09-25 02:00 | 560 | 547
2016-09-25 02:30 | 554 | 539
2016-09-25 03:00 | 542 | 526
2016-09-25 03:30 | 544 | 527
2016-09-25 04:00 | 539 | 521
2016-09-25 04:30 | 544 | 528
2016-09-25 05:00 | 553 | 538
2016-09-25 05:30 | 560 | 546
2016-09-25 06:00 | 565 | 548
2016-09-25 06:30 | 584 | 570
2016-09-25 07:00 | 599 | 588
2016-09-25 07:30 | 631 | 623
2016-09-25 08:00 | 668 | 664
2016-09-25 08:30 | 685 | 683
2016-09-25 09:00 | 696 | 695
2016-09-25 09:30 | 687 | 686
2016-09-25 10:00 | 659 | 658
2016-09-25 10:30 | 635 | 635
2016-09-25 11:00 | 626 | 626
2016-09-25 11:30 | 641 | 641
2016-09-25 12:00 | 629 | 629
2016-09-25 12:30 | 633 | 632
2016-09-25 13:00 | 657 | 655
2016-09-25 13:30 | 673 | 672
2016-09-25 14:00 | 670 | 668
2016-09-25 14:30 | 683 | 682
2016-09-25 15:00 | 673 | 672
2016-09-25 15:30 | 675 | 674
2016-09-25 16:00 | 710 | 709
2016-09-25 16:30 | 737 | 737
2016-09-25 17:00 | 766 | 766
2016-09-25 17:30 | 790 | 789
2016-09-25 18:00 | 824 | 823
2016-09-25 18:30 | 864 | 862
2016-09-25 19:00 | 881 | 876
2016-09-25 19:30 | 863 | 855
2016-09-25 20:00 | 842 | 836
2016-09-25 20:30 | 830 | 828
2016-09-25 21:00 | 800 | 799
2016-09-25 21:30 | 772 | 771
2016-09-25 22:00 | 748 | 748
2016-09-25 22:30 | 728 | 726
2016-09-25 23:00 | 736 | 734
2016-09-25 23:30 | 695 | 691
2016-09-26 | 655 | 649
2016-09-26 00:30 | 613 | 606
2016-09-26 01:00 | 594 | 586
2016-09-26 01:30 | 579 | 571
2016-09-26 02:00 | 563 | 553
2016-09-26 02:30 | 557 | 547
2016-09-26 03:00 | 552 | 541
2016-09-26 03:30 | 554 | 543
2016-09-26 04:00 | 557 | 547
2016-09-26 04:30 | 565 | 556
2016-09-26 05:00 | 585 | 578
2016-09-26 05:30 | 613 | 608
2016-09-26 06:00 | 640 | 636
2016-09-26 06:30 | 687 | 686
2016-09-26 07:00 | 730 | 729
2016-09-26 07:30 | 762 | 761
2016-09-26 08:00 | 783 | 783
2016-09-26 08:30 | 782 | 782
2016-09-26 09:00 | 779 | 779
2016-09-26 09:30 | 765 | 765
2016-09-26 10:00 | 751 | 751
2016-09-26 10:30 | 745 | 745
2016-09-26 11:00 | 731 | 731
2016-09-26 11:30 | 725 | 725
2016-09-26 12:00 | 725 | 725
2016-09-26 12:30 | 727 | 727
2016-09-26 13:00 | 725 | 724
2016-09-26 13:30 | 741 | 740
2016-09-26 14:00 | 755 | 754
2016-09-26 14:30 | 769 | 768
2016-09-26 15:00 | 786 | 786
2016-09-26 15:30 | 810 | 810
2016-09-26 16:00 | 834 | 834
2016-09-26 16:30 | 866 | 864
2016-09-26 17:00 | 907 | 904
2016-09-26 17:30 | 925 | 919
2016-09-26 18:00 | 933 | 929
2016-09-26 18:30 | 957 | 956
2016-09-26 19:00 | 964 | 957
2016-09-26 19:30 | 939 | 930
2016-09-26 20:00 | 917 | 916
2016-09-26 20:30 | 907 | 906
2016-09-26 21:00 | 869 | 867
2016-09-26 21:30 | 826 | 824
2016-09-26 22:00 | 792 | 787
2016-09-26 22:30 | 759 | 758
2016-09-26 23:00 | 764 | 764
2016-09-26 23:30 | 720 | 719
2016-09-27 | 676 | 671
2016-09-27 00:30 | 633 | 625
2016-09-27 01:00 | 612 | 603
2016-09-27 01:30 | 595 | 584
2016-09-27 02:00 | 572 | 564
2016-09-27 02:30 | 566 | 558
2016-09-27 03:00 | 558 | 548
2016-09-27 03:30 | 560 | 551
2016-09-27 04:00 | 564 | 556
2016-09-27 04:30 | 575 | 567
2016-09-27 05:00 | 588 | 582
2016-09-27 05:30 | 621 | 618
2016-09-27 06:00 | 647 | 644
2016-09-27 06:30 | 704 | 703
2016-09-27 07:00 | 759 | 754
2016-09-27 07:30 | 797 | 790
2016-09-27 08:00 | 780 | 776
2016-09-27 08:30 | 796 | 793
2016-09-27 09:00 | 784 | 782
2016-09-27 09:30 | 727 | 724
2016-09-27 10:00 | 721 | 719
2016-09-27 10:30 | 725 | 722
2016-09-27 11:00 | 685 | 682
2016-09-27 11:30 | 680 | 677
2016-09-27 12:00 | 678 | 675
2016-09-27 12:30 | 668 | 666
2016-09-27 13:00 | 670 | 670
2016-09-27 13:30 | 679 | 679
2016-09-27 14:00 | 693 | 693
2016-09-27 14:30 | 710 | 710
2016-09-27 15:00 | 741 | 740
2016-09-27 15:30 | 770 | 770
2016-09-27 16:00 | 797 | 797
2016-09-27 16:30 | 838 | 838
2016-09-27 17:00 | 901 | 899
2016-09-27 17:30 | 906 | 903
2016-09-27 18:00 | 921 | 918
2016-09-27 18:30 | 945 | 944
2016-09-27 19:00 | 956 | 955
2016-09-27 19:30 | 934 | 932
2016-09-27 20:00 | 920 | 918
2016-09-27 20:30 | 910 | 909
2016-09-27 21:00 | 877 | 876
2016-09-27 21:30 | 843 | 840
2016-09-27 22:00 | 805 | 802
2016-09-27 22:30 | 781 | 777
2016-09-27 23:00 | 783 | 780
2016-09-27 23:30 | 726 | 723
2016-09-28 | 677 | 674
2016-09-28 00:30 | 639 | 634
2016-09-28 01:00 | 613 | 606
2016-09-28 01:30 | 588 | 578
2016-09-28 02:00 | 578 | 568
2016-09-28 02:30 | 567 | 556
2016-09-28 03:00 | 564 | 552
2016-09-28 03:30 | 564 | 552
2016-09-28 04:00 | 560 | 548
2016-09-28 04:30 | 575 | 564
2016-09-28 05:00 | 591 | 583
2016-09-28 05:30 | 619 | 613
2016-09-28 06:00 | 651 | 647
2016-09-28 06:30 | 702 | 701
2016-09-28 07:00 | 751 | 750
2016-09-28 07:30 | 777 | 772
2016-09-28 08:00 | 752 | 748
2016-09-28 08:30 | 743 | 740
2016-09-28 09:00 | 735 | 733
2016-09-28 09:30 | 726 | 724
2016-09-28 10:00 | 724 | 723
2016-09-28 10:30 | 719 | 718
2016-09-28 11:00 | 711 | 710
2016-09-28 11:30 | 700 | 700
2016-09-28 12:00 | 691 | 689
2016-09-28 12:30 | 694 | 691
2016-09-28 13:00 | 703 | 700
2016-09-28 13:30 | 705 | 702
2016-09-28 14:00 | 727 | 724
2016-09-28 14:30 | 741 | 739
2016-09-28 15:00 | 764 | 763
2016-09-28 15:30 | 791 | 789
2016-09-28 16:00 | 823 | 822
2016-09-28 16:30 | 852 | 850
2016-09-28 17:00 | 855 | 854
2016-09-28 17:30 | 873 | 869
2016-09-28 18:00 | 875 | 873
2016-09-28 18:30 | 897 | 891
2016-09-28 19:00 | 896 | 891
2016-09-28 19:30 | 897 | 888
2016-09-28 20:00 | 899 | 891
2016-09-28 20:30 | 887 | 881
2016-09-28 21:00 | 844 | 841
2016-09-28 21:30 | 794 | 792
2016-09-28 22:00 | 787 | 784
2016-09-28 22:30 | 768 | 764
2016-09-28 23:00 | 759 | 754
2016-09-28 23:30 | 706 | 702
2016-09-29 | 674 | 671
2016-09-29 00:30 | 632 | 627
2016-09-29 01:00 | 610 | 603
2016-09-29 01:30 | 588 | 578
2016-09-29 02:00 | 576 | 565
2016-09-29 02:30 | 565 | 553
2016-09-29 03:00 | 560 | 548
2016-09-29 03:30 | 561 | 547
2016-09-29 04:00 | 542 | 528
2016-09-29 04:30 | 569 | 558
2016-09-29 05:00 | 585 | 576
2016-09-29 05:30 | 621 | 615
2016-09-29 06:00 | 641 | 637
2016-09-29 06:30 | 695 | 694
2016-09-29 07:00 | 753 | 752
2016-09-29 07:30 | 816 | 815
2016-09-29 08:00 | 854 | 852
2016-09-29 08:30 | 869 | 867
2016-09-29 09:00 | 859 | 857
2016-09-29 09:30 | 848 | 846
2016-09-29 10:00 | 877 | 877
2016-09-29 10:30 | 840 | 839
2016-09-29 11:00 | 833 | 833
2016-09-29 11:30 | 873 | 873
2016-09-29 12:00 | 879 | 875
2016-09-29 12:30 | 860 | 851
2016-09-29 13:00 | 855 | 844
2016-09-29 13:30 | 853 | 842
2016-09-29 14:00 | 857 | 847
2016-09-29 14:30 | 859 | 848
2016-09-29 15:00 | 875 | 864
2016-09-29 15:30 | 849 | 836
2016-09-29 16:00 | 880 | 867
2016-09-29 16:30 | 890 | 876
2016-09-29 17:00 | 908 | 896
2016-09-29 17:30 | 919 | 908
2016-09-29 18:00 | 932 | 922
2016-09-29 18:30 | 947 | 940
2016-09-29 19:00 | 962 | 956
2016-09-29 19:30 | 942 | 932
2016-09-29 20:00 | 926 | 921
2016-09-29 20:30 | 923 | 919
2016-09-29 21:00 | 875 | 870
2016-09-29 21:30 | 829 | 828
2016-09-29 22:00 | 793 | 792
2016-09-29 22:30 | 783 | 781
2016-09-29 23:00 | 784 | 782
2016-09-29 23:30 | 716 | 713
2016-09-30 | 677 | 674
2016-09-30 00:30 | 637 | 632
2016-09-30 01:00 | 612 | 605
2016-09-30 01:30 | 593 | 585
2016-09-30 02:00 | 566 | 555
2016-09-30 02:30 | 524 | 509
2016-09-30 03:00 | 560 | 548
2016-09-30 03:30 | 560 | 548
2016-09-30 04:00 | 533 | 519
2016-09-30 04:30 | 513 | 498
2016-09-30 05:00 | 543 | 532
2016-09-30 05:30 | 614 | 608
2016-09-30 06:00 | 641 | 635
2016-09-30 06:30 | 683 | 681
2016-09-30 07:00 | 718 | 717
2016-09-30 07:30 | 752 | 752
2016-09-30 08:00 | 772 | 771
2016-09-30 08:30 | 767 | 760
2016-09-30 09:00 | 751 | 748
2016-09-30 09:30 | 734 | 733
2016-09-30 10:00 | 719 | 719
2016-09-30 10:30 | 709 | 709
2016-09-30 11:00 | 694 | 694
2016-09-30 11:30 | 685 | 685
2016-09-30 12:00 | 680 | 680
2016-09-30 12:30 | 677 | 677
2016-09-30 13:00 | 682 | 682
2016-09-30 13:30 | 675 | 675
2016-09-30 14:00 | 677 | 677
2016-09-30 14:30 | 666 | 666
2016-09-30 15:00 | 735 | 735
2016-09-30 15:30 | 756 | 756
2016-09-30 16:00 | 780 | 780
2016-09-30 16:30 | 800 | 800
2016-09-30 17:00 | 834 | 833
2016-09-30 17:30 | 842 | 841
2016-09-30 18:00 | 852 | 850
2016-09-30 18:30 | 870 | 870
2016-09-30 19:00 | 878 | 878
2016-09-30 19:30 | 860 | 858
2016-09-30 20:00 | 851 | 851
2016-09-30 20:30 | 840 | 840
2016-09-30 21:00 | 808 | 808
2016-09-30 21:30 | 771 | 770
2016-09-30 22:00 | 752 | 751
2016-09-30 22:30 | 736 | 735
2016-09-30 23:00 | 736 | 736
2016-09-30 23:30 | 711 | 710
2016-10-01 | 668 | 665
2016-10-01 00:30 | 640 | 635
2016-10-01 01:00 | 549 | 539
2016-10-01 01:30 | 555 | 543
2016-10-01 02:00 | 556 | 542
2016-10-01 02:30 | 562 | 548
2016-10-01 03:00 | 556 | 540
2016-10-01 03:30 | 553 | 537
2016-10-01 04:00 | 553 | 537
2016-10-01 04:30 | 552 | 537
2016-10-01 05:00 | 559 | 545
2016-10-01 05:30 | 564 | 550
2016-10-01 06:00 | 577 | 561
2016-10-01 06:30 | 589 | 575
2016-10-01 07:00 | 600 | 589
2016-10-01 07:30 | 616 | 610
2016-10-01 08:00 | 624 | 621
2016-10-01 08:30 | 633 | 630
2016-10-01 09:00 | 634 | 633
2016-10-01 09:30 | 637 | 636
2016-10-01 10:00 | 604 | 604
2016-10-01 10:30 | 568 | 567
2016-10-01 11:00 | 602 | 602
2016-10-01 11:30 | 602 | 602
2016-10-01 12:00 | 546 | 546
2016-10-01 12:30 | 567 | 566
2016-10-01 13:00 | 598 | 598
2016-10-01 13:30 | 604 | 604
2016-10-01 14:00 | 605 | 604
2016-10-01 14:30 | 602 | 602
2016-10-01 15:00 | 566 | 566
2016-10-01 15:30 | 645 | 645
2016-10-01 16:00 | 702 | 702
2016-10-01 16:30 | 672 | 672
2016-10-01 17:00 | 746 | 746
2016-10-01 17:30 | 722 | 721
2016-10-01 18:00 | 720 | 719
2016-10-01 18:30 | 795 | 795
2016-10-01 19:00 | 820 | 819
2016-10-01 19:30 | 804 | 802
2016-10-01 20:00 | 795 | 793
2016-10-01 20:30 | 792 | 791
2016-10-01 21:00 | 707 | 706
2016-10-01 21:30 | 675 | 674
2016-10-01 22:00 | 659 | 658
2016-10-01 22:30 | 675 | 674
2016-10-01 23:00 | 712 | 711
2016-10-01 23:30 | 685 | 683
2016-10-02 | 638 | 634
2016-10-02 00:30 | 605 | 597
2016-10-02 01:00 | 587 | 576
2016-10-02 01:30 | 531 | 516
2016-10-02 02:00 | 495 | 477
2016-10-02 02:30 | 521 | 503
2016-10-02 03:00 | 501 | 481
2016-10-02 03:30 | 512 | 492
2016-10-02 04:00 | 524 | 503
2016-10-02 04:30 | 546 | 528
2016-10-02 05:00 | 473 | 449
2016-10-02 05:30 | 522 | 500
2016-10-02 06:00 | 558 | 534
2016-10-02 06:30 | 560 | 537
2016-10-02 07:00 | 545 | 524
2016-10-02 07:30 | 529 | 511
2016-10-02 08:00 | 508 | 492
2016-10-02 08:30 | 557 | 547
2016-10-02 09:00 | 602 | 596
2016-10-02 09:30 | 606 | 602
2016-10-02 10:00 | 552 | 550
2016-10-02 10:30 | 512 | 510
2016-10-02 11:00 | 516 | 514
2016-10-02 11:30 | 553 | 551
2016-10-02 12:00 | 542 | 540
2016-10-02 12:30 | 535 | 533
2016-10-02 13:00 | 527 | 526
2016-10-02 13:30 | 543 | 541
2016-10-02 14:00 | 552 | 551
2016-10-02 14:30 | 611 | 611
2016-10-02 15:00 | 645 | 645
2016-10-02 15:30 | 668 | 667
2016-10-02 16:00 | 690 | 687
2016-10-02 16:30 | 685 | 683
2016-10-02 17:00 | 701 | 699
2016-10-02 17:30 | 751 | 748
2016-10-02 18:00 | 765 | 762
2016-10-02 18:30 | 766 | 765
2016-10-02 19:00 | 770 | 768
2016-10-02 19:30 | 757 | 754
2016-10-02 20:00 | 780 | 777
2016-10-02 20:30 | 762 | 760
2016-10-02 21:00 | 742 | 741
2016-10-02 21:30 | 728 | 726
2016-10-02 22:00 | 701 | 698
2016-10-02 22:30 | 669 | 665
2016-10-02 23:00 | 686 | 684
2016-10-02 23:30 | 637 | 634
2016-10-03 | 636 | 631
2016-10-03 00:30 | 595 | 589
2016-10-03 01:00 | 559 | 550
2016-10-03 01:30 | 547 | 535
2016-10-03 02:00 | 551 | 538
2016-10-03 02:30 | 541 | 528
2016-10-03 03:00 | 537 | 522
2016-10-03 03:30 | 493 | 477
2016-10-03 04:00 | 511 | 495
2016-10-03 04:30 | 506 | 490
2016-10-03 05:00 | 543 | 530
2016-10-03 05:30 | 550 | 539
2016-10-03 06:00 | 557 | 543
2016-10-03 06:30 | 539 | 527
2016-10-03 07:00 | 576 | 566
2016-10-03 07:30 | 610 | 605
2016-10-03 08:00 | 657 | 654
2016-10-03 08:30 | 665 | 665
2016-10-03 09:00 | 690 | 690
2016-10-03 09:30 | 737 | 737
2016-10-03 10:00 | 731 | 730
2016-10-03 10:30 | 771 | 769
2016-10-03 11:00 | 786 | 783
2016-10-03 11:30 | 793 | 791
2016-10-03 12:00 | 786 | 784
2016-10-03 12:30 | 781 | 778
2016-10-03 13:00 | 784 | 780
2016-10-03 13:30 | 777 | 773
2016-10-03 14:00 | 783 | 779
2016-10-03 14:30 | 789 | 785
2016-10-03 15:00 | 782 | 777
2016-10-03 15:30 | 770 | 765
2016-10-03 16:00 | 795 | 790
2016-10-03 16:30 | 799 | 795
2016-10-03 17:00 | 833 | 830
2016-10-03 17:30 | 857 | 848
2016-10-03 18:00 | 885 | 879
2016-10-03 18:30 | 873 | 868
2016-10-03 19:00 | 862 | 855
2016-10-03 19:30 | 838 | 829
2016-10-03 20:00 | 815 | 808
2016-10-03 20:30 | 796 | 787
2016-10-03 21:00 | 756 | 752
2016-10-03 21:30 | 737 | 731
2016-10-03 22:00 | 734 | 727
2016-10-03 22:30 | 712 | 710
2016-10-03 23:00 | 723 | 722
2016-10-03 23:30 | 667 | 664
2016-10-04 | 637 | 633
2016-10-04 00:30 | 591 | 584
2016-10-04 01:00 | 531 | 520
2016-10-04 01:30 | 535 | 522
2016-10-04 02:00 | 556 | 543
2016-10-04 02:30 | 501 | 485
2016-10-04 03:00 | 498 | 480
2016-10-04 03:30 | 485 | 466
2016-10-04 04:00 | 497 | 479
2016-10-04 04:30 | 508 | 492
2016-10-04 05:00 | 563 | 553
2016-10-04 05:30 | 571 | 564
2016-10-04 06:00 | 646 | 642
2016-10-04 06:30 | 710 | 706
2016-10-04 07:00 | 749 | 745
2016-10-04 07:30 | 782 | 777
2016-10-04 08:00 | 775 | 772
2016-10-04 08:30 | 744 | 741
2016-10-04 09:00 | 714 | 712
2016-10-04 09:30 | 695 | 693
2016-10-04 10:00 | 686 | 685
2016-10-04 10:30 | 674 | 674
2016-10-04 11:00 | 662 | 662
2016-10-04 11:30 | 651 | 651
2016-10-04 12:00 | 657 | 657
2016-10-04 12:30 | 655 | 655
2016-10-04 13:00 | 660 | 660
2016-10-04 13:30 | 674 | 673
2016-10-04 14:00 | 695 | 694
2016-10-04 14:30 | 703 | 703
2016-10-04 15:00 | 728 | 728
2016-10-04 15:30 | 765 | 761
2016-10-04 16:00 | 795 | 791
2016-10-04 16:30 | 802 | 799
2016-10-04 17:00 | 848 | 841
2016-10-04 17:30 | 894 | 884
2016-10-04 18:00 | 913 | 903
2016-10-04 18:30 | 924 | 916
2016-10-04 19:00 | 951 | 944
2016-10-04 19:30 | 922 | 913
2016-10-04 20:00 | 906 | 901
2016-10-04 20:30 | 880 | 875
2016-10-04 21:00 | 858 | 849
2016-10-04 21:30 | 810 | 806
2016-10-04 22:00 | 774 | 773
2016-10-04 22:30 | 756 | 753
2016-10-04 23:00 | 748 | 745
2016-10-04 23:30 | 707 | 700
2016-10-05 | 630 | 617
2016-10-05 00:30 | 598 | 580
2016-10-05 01:00 | 574 | 552
2016-10-05 01:30 | 581 | 557
2016-10-05 02:00 | 563 | 538
2016-10-05 02:30 | 546 | 533
2016-10-05 03:00 | 558 | 546
2016-10-05 03:30 | 556 | 543
2016-10-05 04:00 | 557 | 545
2016-10-05 04:30 | 567 | 556
2016-10-05 05:00 | 578 | 571
2016-10-05 05:30 | 614 | 610
2016-10-05 06:00 | 641 | 638
2016-10-05 06:30 | 702 | 700
2016-10-05 07:00 | 721 | 718
2016-10-05 07:30 | 770 | 764
2016-10-05 08:00 | 766 | 758
2016-10-05 08:30 | 751 | 745
2016-10-05 09:00 | 732 | 726
2016-10-05 09:30 | 722 | 717
2016-10-05 10:00 | 716 | 713
2016-10-05 10:30 | 707 | 704
2016-10-05 11:00 | 698 | 695
2016-10-05 11:30 | 694 | 692
2016-10-05 12:00 | 710 | 703
2016-10-05 12:30 | 718 | 707
2016-10-05 13:00 | 723 | 712
2016-10-05 13:30 | 734 | 724
2016-10-05 14:00 | 755 | 745
2016-10-05 14:30 | 768 | 759
2016-10-05 15:00 | 777 | 769
2016-10-05 15:30 | 805 | 798
2016-10-05 16:00 | 834 | 827
2016-10-05 16:30 | 874 | 868
2016-10-05 17:00 | 906 | 901
2016-10-05 17:30 | 913 | 906
2016-10-05 18:00 | 921 | 912
2016-10-05 18:30 | 945 | 939
2016-10-05 19:00 | 969 | 958
2016-10-05 19:30 | 948 | 934
2016-10-05 20:00 | 938 | 926
2016-10-05 20:30 | 932 | 916
2016-10-05 21:00 | 876 | 866
2016-10-05 21:30 | 833 | 818
2016-10-05 22:00 | 794 | 787
2016-10-05 22:30 | 766 | 763
2016-10-05 23:00 | 764 | 763
2016-10-05 23:30 | 712 | 711
2016-10-06 | 664 | 662
2016-10-06 00:30 | 627 | 624
2016-10-06 01:00 | 605 | 599
2016-10-06 01:30 | 582 | 573
2016-10-06 02:00 | 569 | 558
2016-10-06 02:30 | 560 | 547
2016-10-06 03:00 | 557 | 543
2016-10-06 03:30 | 557 | 542
2016-10-06 04:00 | 555 | 541
2016-10-06 04:30 | 563 | 551
2016-10-06 05:00 | 572 | 564
2016-10-06 05:30 | 606 | 601
2016-10-06 06:00 | 641 | 638
2016-10-06 06:30 | 702 | 700
2016-10-06 07:00 | 723 | 719
2016-10-06 07:30 | 767 | 761
2016-10-06 08:00 | 765 | 760
2016-10-06 08:30 | 751 | 747
2016-10-06 09:00 | 732 | 729
2016-10-06 09:30 | 718 | 716
2016-10-06 10:00 | 703 | 701
2016-10-06 10:30 | 704 | 703
2016-10-06 11:00 | 692 | 692
2016-10-06 11:30 | 685 | 684
2016-10-06 12:00 | 691 | 691
2016-10-06 12:30 | 699 | 698
2016-10-06 13:00 | 705 | 705
2016-10-06 13:30 | 729 | 729
2016-10-06 14:00 | 751 | 751
2016-10-06 14:30 | 781 | 780
2016-10-06 15:00 | 750 | 748
2016-10-06 15:30 | 796 | 795
2016-10-06 16:00 | 850 | 848
2016-10-06 16:30 | 874 | 872
2016-10-06 17:00 | 922 | 920
2016-10-06 17:30 | 945 | 942
2016-10-06 18:00 | 939 | 936
2016-10-06 18:30 | 900 | 898
2016-10-06 19:00 | 911 | 908
2016-10-06 19:30 | 897 | 888
2016-10-06 20:00 | 938 | 929
2016-10-06 20:30 | 881 | 875
2016-10-06 21:00 | 832 | 827
2016-10-06 21:30 | 815 | 811
2016-10-06 22:00 | 787 | 785
2016-10-06 22:30 | 774 | 774
2016-10-06 23:00 | 788 | 787
2016-10-06 23:30 | 736 | 731
2016-10-07 | 671 | 666
2016-10-07 00:30 | 634 | 627
2016-10-07 01:00 | 604 | 595
2016-10-07 01:30 | 586 | 574
2016-10-07 02:00 | 567 | 552
2016-10-07 02:30 | 560 | 543
2016-10-07 03:00 | 562 | 545
2016-10-07 03:30 | 564 | 547
2016-10-07 04:00 | 564 | 548
2016-10-07 04:30 | 581 | 567
2016-10-07 05:00 | 586 | 577
2016-10-07 05:30 | 624 | 618
2016-10-07 06:00 | 660 | 656
2016-10-07 06:30 | 712 | 711
2016-10-07 07:00 | 736 | 735
2016-10-07 07:30 | 784 | 777
2016-10-07 08:00 | 781 | 773
2016-10-07 08:30 | 767 | 762
2016-10-07 09:00 | 747 | 743
2016-10-07 09:30 | 733 | 731
2016-10-07 10:00 | 721 | 720
2016-10-07 10:30 | 706 | 706
2016-10-07 11:00 | 737 | 737
2016-10-07 11:30 | 746 | 746
2016-10-07 12:00 | 747 | 747
2016-10-07 12:30 | 751 | 751
2016-10-07 13:00 | 748 | 746
2016-10-07 13:30 | 760 | 758
2016-10-07 14:00 | 776 | 775
2016-10-07 14:30 | 740 | 737
2016-10-07 15:00 | 726 | 723
2016-10-07 15:30 | 758 | 755
2016-10-07 16:00 | 816 | 814
2016-10-07 16:30 | 861 | 858
2016-10-07 17:00 | 864 | 860
2016-10-07 17:30 | 876 | 871
2016-10-07 18:00 | 876 | 868
2016-10-07 18:30 | 873 | 868
2016-10-07 19:00 | 848 | 844
2016-10-07 19:30 | 874 | 867
2016-10-07 20:00 | 856 | 854
2016-10-07 20:30 | 830 | 828
2016-10-07 21:00 | 838 | 834
2016-10-07 21:30 | 793 | 786
2016-10-07 22:00 | 770 | 768
2016-10-07 22:30 | 758 | 756
2016-10-07 23:00 | 751 | 749
2016-10-07 23:30 | 723 | 719
2016-10-08 | 658 | 653
2016-10-08 00:30 | 633 | 628
2016-10-08 01:00 | 613 | 607
2016-10-08 01:30 | 594 | 585
2016-10-08 02:00 | 575 | 564
2016-10-08 02:30 | 571 | 559
2016-10-08 03:00 | 562 | 550
2016-10-08 03:30 | 559 | 547
2016-10-08 04:00 | 560 | 547
2016-10-08 04:30 | 563 | 550
2016-10-08 05:00 | 565 | 554
2016-10-08 05:30 | 575 | 562
2016-10-08 06:00 | 585 | 571
2016-10-08 06:30 | 603 | 593
2016-10-08 07:00 | 616 | 609
2016-10-08 07:30 | 641 | 638
2016-10-08 08:00 | 654 | 652
2016-10-08 08:30 | 682 | 682
2016-10-08 09:00 | 686 | 686
2016-10-08 09:30 | 686 | 686
2016-10-08 10:00 | 680 | 680
2016-10-08 10:30 | 686 | 686
2016-10-08 11:00 | 654 | 654
2016-10-08 11:30 | 654 | 654
2016-10-08 12:00 | 662 | 662
2016-10-08 12:30 | 663 | 662
2016-10-08 13:00 | 668 | 667
2016-10-08 13:30 | 680 | 680
2016-10-08 14:00 | 735 | 735
2016-10-08 14:30 | 745 | 744
2016-10-08 15:00 | 736 | 735
2016-10-08 15:30 | 748 | 747
2016-10-08 16:00 | 771 | 770
2016-10-08 16:30 | 796 | 795
2016-10-08 17:00 | 829 | 826
2016-10-08 17:30 | 836 | 833
2016-10-08 18:00 | 789 | 783
2016-10-08 18:30 | 813 | 811
2016-10-08 19:00 | 834 | 829
2016-10-08 19:30 | 816 | 805
2016-10-08 20:00 | 799 | 789
2016-10-08 20:30 | 831 | 824
2016-10-08 21:00 | 794 | 789
2016-10-08 21:30 | 764 | 761
2016-10-08 22:00 | 746 | 742
2016-10-08 22:30 | 725 | 717
2016-10-08 23:00 | 694 | 686
2016-10-08 23:30 | 669 | 660
2016-10-09 | 603 | 598
2016-10-09 00:30 | 596 | 590
2016-10-09 01:00 | 572 | 564
2016-10-09 01:30 | 546 | 535
2016-10-09 02:00 | 526 | 513
2016-10-09 02:30 | 515 | 500
2016-10-09 03:00 | 512 | 495
2016-10-09 03:30 | 510 | 493
2016-10-09 04:00 | 504 | 487
2016-10-09 04:30 | 501 | 483
2016-10-09 05:00 | 500 | 483
2016-10-09 05:30 | 504 | 484
2016-10-09 06:00 | 511 | 489
2016-10-09 06:30 | 515 | 497
2016-10-09 07:00 | 523 | 507
2016-10-09 07:30 | 548 | 538
2016-10-09 08:00 | 571 | 565
2016-10-09 08:30 | 622 | 619
2016-10-09 09:00 | 647 | 646
2016-10-09 09:30 | 650 | 650
2016-10-09 10:00 | 667 | 667
2016-10-09 10:30 | 672 | 671
2016-10-09 11:00 | 716 | 714
2016-10-09 11:30 | 665 | 658
2016-10-09 12:00 | 684 | 677
2016-10-09 12:30 | 689 | 681
2016-10-09 13:00 | 694 | 687
2016-10-09 13:30 | 681 | 673
2016-10-09 14:00 | 686 | 677
2016-10-09 14:30 | 688 | 681
2016-10-09 15:00 | 694 | 687
2016-10-09 15:30 | 704 | 696
2016-10-09 16:00 | 718 | 711
2016-10-09 16:30 | 733 | 726
2016-10-09 17:00 | 762 | 756
2016-10-09 17:30 | 802 | 798
2016-10-09 18:00 | 804 | 801
2016-10-09 18:30 | 804 | 801
2016-10-09 19:00 | 808 | 804
2016-10-09 19:30 | 790 | 786
2016-10-09 20:00 | 776 | 774
2016-10-09 20:30 | 763 | 761
2016-10-09 21:00 | 724 | 723
2016-10-09 21:30 | 702 | 699
2016-10-09 22:00 | 685 | 682
2016-10-09 22:30 | 684 | 683
2016-10-09 23:00 | 665 | 663
2016-10-09 23:30 | 638 | 633
2016-10-10 | 606 | 598
2016-10-10 00:30 | 545 | 533
2016-10-10 01:00 | 534 | 520
2016-10-10 01:30 | 501 | 483
2016-10-10 02:00 | 478 | 458
2016-10-10 02:30 | 464 | 443
2016-10-10 03:00 | 453 | 431
2016-10-10 03:30 | 448 | 427
2016-10-10 04:00 | 469 | 449
2016-10-10 04:30 | 490 | 473
2016-10-10 05:00 | 498 | 484
2016-10-10 05:30 | 535 | 525
2016-10-10 06:00 | 578 | 571
2016-10-10 06:30 | 667 | 666
2016-10-10 07:00 | 702 | 701
2016-10-10 07:30 | 756 | 756
2016-10-10 08:00 | 814 | 813
2016-10-10 08:30 | 814 | 814
2016-10-10 09:00 | 791 | 791
2016-10-10 09:30 | 769 | 768
2016-10-10 10:00 | 756 | 756
2016-10-10 10:30 | 749 | 749
2016-10-10 11:00 | 741 | 741
2016-10-10 11:30 | 740 | 740
2016-10-10 12:00 | 751 | 751
2016-10-10 12:30 | 751 | 751
2016-10-10 13:00 | 783 | 782
2016-10-10 13:30 | 783 | 783
2016-10-10 14:00 | 780 | 780
2016-10-10 14:30 | 797 | 797
2016-10-10 15:00 | 800 | 800
2016-10-10 15:30 | 835 | 835
2016-10-10 16:00 | 862 | 862
2016-10-10 16:30 | 890 | 888
2016-10-10 17:00 | 923 | 921
2016-10-10 17:30 | 931 | 929
2016-10-10 18:00 | 935 | 934
2016-10-10 18:30 | 961 | 961
2016-10-10 19:00 | 990 | 988
2016-10-10 19:30 | 953 | 948
2016-10-10 20:00 | 926 | 924
2016-10-10 20:30 | 913 | 910
2016-10-10 21:00 | 867 | 864
2016-10-10 21:30 | 823 | 820
2016-10-10 22:00 | 786 | 780
2016-10-10 22:30 | 719 | 716
2016-10-10 23:00 | 737 | 736
2016-10-10 23:30 | 685 | 682
2016-10-11 | 656 | 649
2016-10-11 00:30 | 596 | 583
2016-10-11 01:00 | 558 | 543
2016-10-11 01:30 | 559 | 547
2016-10-11 02:00 | 522 | 507
2016-10-11 02:30 | 520 | 503
2016-10-11 03:00 | 542 | 526
2016-10-11 03:30 | 544 | 528
2016-10-11 04:00 | 546 | 530
2016-10-11 04:30 | 559 | 546
2016-10-11 05:00 | 589 | 581
2016-10-11 05:30 | 623 | 617
2016-10-11 06:00 | 662 | 661
2016-10-11 06:30 | 725 | 724
2016-10-11 07:00 | 773 | 773
2016-10-11 07:30 | 817 | 817
2016-10-11 08:00 | 820 | 820
2016-10-11 08:30 | 818 | 818
2016-10-11 09:00 | 821 | 821
2016-10-11 09:30 | 823 | 823
2016-10-11 10:00 | 828 | 827
2016-10-11 10:30 | 855 | 853
2016-10-11 11:00 | 854 | 852
2016-10-11 11:30 | 839 | 837
2016-10-11 12:00 | 844 | 843
2016-10-11 12:30 | 843 | 842
2016-10-11 13:00 | 842 | 841
2016-10-11 13:30 | 849 | 849
2016-10-11 14:00 | 869 | 869
2016-10-11 14:30 | 880 | 879
2016-10-11 15:00 | 874 | 873
2016-10-11 15:30 | 825 | 822
2016-10-11 16:00 | 836 | 833
2016-10-11 16:30 | 900 | 897
2016-10-11 17:00 | 961 | 958
2016-10-11 17:30 | 943 | 941
2016-10-11 18:00 | 940 | 938
2016-10-11 18:30 | 952 | 951
2016-10-11 19:00 | 966 | 966
2016-10-11 19:30 | 942 | 941
2016-10-11 20:00 | 929 | 928
2016-10-11 20:30 | 921 | 919
2016-10-11 21:00 | 865 | 865
2016-10-11 21:30 | 823 | 823
2016-10-11 22:00 | 793 | 793
2016-10-11 22:30 | 777 | 776
2016-10-11 23:00 | 771 | 769
2016-10-11 23:30 | 695 | 689
2016-10-12 | 676 | 665
2016-10-12 00:30 | 639 | 626
2016-10-12 01:00 | 602 | 596
2016-10-12 01:30 | 585 | 577
2016-10-12 02:00 | 570 | 561
2016-10-12 02:30 | 564 | 554
2016-10-12 03:00 | 559 | 548
2016-10-12 03:30 | 559 | 546
2016-10-12 04:00 | 564 | 552
2016-10-12 04:30 | 574 | 565
2016-10-12 05:00 | 592 | 586
2016-10-12 05:30 | 618 | 615
2016-10-12 06:00 | 660 | 657
2016-10-12 06:30 | 728 | 726
2016-10-12 07:00 | 782 | 782
2016-10-12 07:30 | 823 | 823
2016-10-12 08:00 | 825 | 824
2016-10-12 08:30 | 829 | 829
2016-10-12 09:00 | 828 | 828
2016-10-12 09:30 | 823 | 822
2016-10-12 10:00 | 813 | 813
2016-10-12 10:30 | 817 | 816
2016-10-12 11:00 | 798 | 797
2016-10-12 11:30 | 801 | 800
2016-10-12 12:00 | 811 | 810
2016-10-12 12:30 | 800 | 800
2016-10-12 13:00 | 794 | 793
2016-10-12 13:30 | 798 | 797
2016-10-12 14:00 | 818 | 817
2016-10-12 14:30 | 815 | 815
2016-10-12 15:00 | 820 | 819
2016-10-12 15:30 | 834 | 834
2016-10-12 16:00 | 858 | 858
2016-10-12 16:30 | 882 | 882
2016-10-12 17:00 | 902 | 902
2016-10-12 17:30 | 918 | 918
2016-10-12 18:00 | 931 | 930
2016-10-12 18:30 | 942 | 942
2016-10-12 19:00 | 957 | 957
2016-10-12 19:30 | 929 | 928
2016-10-12 20:00 | 919 | 918
2016-10-12 20:30 | 902 | 901
2016-10-12 21:00 | 867 | 866
2016-10-12 21:30 | 833 | 829
2016-10-12 22:00 | 799 | 794
2016-10-12 22:30 | 771 | 770
2016-10-12 23:00 | 772 | 772
2016-10-12 23:30 | 729 | 727
2016-10-13 | 677 | 673
2016-10-13 00:30 | 637 | 634
2016-10-13 01:00 | 615 | 610
2016-10-13 01:30 | 589 | 582
2016-10-13 02:00 | 574 | 564
2016-10-13 02:30 | 564 | 552
2016-10-13 03:00 | 561 | 549
2016-10-13 03:30 | 559 | 547
2016-10-13 04:00 | 564 | 553
2016-10-13 04:30 | 577 | 569
2016-10-13 05:00 | 593 | 588
2016-10-13 05:30 | 626 | 624
2016-10-13 06:00 | 673 | 671
2016-10-13 06:30 | 738 | 737
2016-10-13 07:00 | 787 | 787
2016-10-13 07:30 | 818 | 817
2016-10-13 08:00 | 811 | 811
2016-10-13 08:30 | 797 | 796
2016-10-13 09:00 | 789 | 788
2016-10-13 09:30 | 773 | 771
2016-10-13 10:00 | 768 | 766
2016-10-13 10:30 | 768 | 765
2016-10-13 11:00 | 780 | 777
2016-10-13 11:30 | 798 | 794
2016-10-13 12:00 | 796 | 793
2016-10-13 12:30 | 803 | 800
2016-10-13 13:00 | 805 | 803
2016-10-13 13:30 | 786 | 785
2016-10-13 14:00 | 792 | 791
2016-10-13 14:30 | 799 | 799
2016-10-13 15:00 | 813 | 812
2016-10-13 15:30 | 837 | 836
2016-10-13 16:00 | 857 | 857
2016-10-13 16:30 | 867 | 867
2016-10-13 17:00 | 902 | 901
2016-10-13 17:30 | 919 | 919
2016-10-13 18:00 | 927 | 927
2016-10-13 18:30 | 958 | 958
2016-10-13 19:00 | 981 | 980
2016-10-13 19:30 | 968 | 967
2016-10-13 20:00 | 952 | 951
2016-10-13 20:30 | 926 | 925
2016-10-13 21:00 | 878 | 877
2016-10-13 21:30 | 831 | 830
2016-10-13 22:00 | 796 | 796
2016-10-13 22:30 | 780 | 780
2016-10-13 23:00 | 783 | 782
2016-10-13 23:30 | 723 | 723
2016-10-14 | 673 | 671
2016-10-14 00:30 | 636 | 633
2016-10-14 01:00 | 609 | 605
2016-10-14 01:30 | 586 | 580
2016-10-14 02:00 | 571 | 562
2016-10-14 02:30 | 567 | 557
2016-10-14 03:00 | 559 | 548
2016-10-14 03:30 | 559 | 548
2016-10-14 04:00 | 560 | 549
2016-10-14 04:30 | 570 | 561
2016-10-14 05:00 | 589 | 583
2016-10-14 05:30 | 619 | 614
2016-10-14 06:00 | 662 | 660
2016-10-14 06:30 | 722 | 721
2016-10-14 07:00 | 773 | 771
2016-10-14 07:30 | 809 | 808
2016-10-14 08:00 | 805 | 803
2016-10-14 08:30 | 775 | 774
2016-10-14 09:00 | 756 | 754
2016-10-14 09:30 | 749 | 748
2016-10-14 10:00 | 743 | 742
2016-10-14 10:30 | 744 | 743
2016-10-14 11:00 | 743 | 741
2016-10-14 11:30 | 737 | 736
2016-10-14 12:00 | 724 | 722
2016-10-14 12:30 | 718 | 717
2016-10-14 13:00 | 727 | 726
2016-10-14 13:30 | 715 | 713
2016-10-14 14:00 | 723 | 721
2016-10-14 14:30 | 718 | 716
2016-10-14 15:00 | 739 | 737
2016-10-14 15:30 | 752 | 750
2016-10-14 16:00 | 776 | 774
2016-10-14 16:30 | 806 | 804
2016-10-14 17:00 | 834 | 832
2016-10-14 17:30 | 837 | 835
2016-10-14 18:00 | 847 | 844
2016-10-14 18:30 | 861 | 860
2016-10-14 19:00 | 884 | 884
2016-10-14 19:30 | 868 | 868
2016-10-14 20:00 | 850 | 850
2016-10-14 20:30 | 845 | 845
2016-10-14 21:00 | 814 | 814
2016-10-14 21:30 | 792 | 792
2016-10-14 22:00 | 769 | 768
2016-10-14 22:30 | 758 | 756
2016-10-14 23:00 | 775 | 773
2016-10-14 23:30 | 714 | 708
2016-10-15 | 647 | 635
2016-10-15 00:30 | 615 | 602
2016-10-15 01:00 | 602 | 592
2016-10-15 01:30 | 568 | 556
2016-10-15 02:00 | 526 | 509
2016-10-15 02:30 | 517 | 500
2016-10-15 03:00 | 518 | 499
2016-10-15 03:30 | 499 | 478
2016-10-15 04:00 | 533 | 516
2016-10-15 04:30 | 545 | 532
2016-10-15 05:00 | 502 | 486
2016-10-15 05:30 | 570 | 555
2016-10-15 06:00 | 577 | 562
2016-10-15 06:30 | 555 | 544
2016-10-15 07:00 | 600 | 593
2016-10-15 07:30 | 622 | 618
2016-10-15 08:00 | 631 | 629
2016-10-15 08:30 | 648 | 647
2016-10-15 09:00 | 664 | 664
2016-10-15 09:30 | 668 | 666
2016-10-15 10:00 | 662 | 661
2016-10-15 10:30 | 657 | 656
2016-10-15 11:00 | 631 | 630
2016-10-15 11:30 | 632 | 631
2016-10-15 12:00 | 597 | 596
2016-10-15 12:30 | 607 | 606
2016-10-15 13:00 | 615 | 614
2016-10-15 13:30 | 614 | 612
2016-10-15 14:00 | 619 | 617
2016-10-15 14:30 | 580 | 578
2016-10-15 15:00 | 592 | 589
2016-10-15 15:30 | 645 | 644
2016-10-15 16:00 | 680 | 679
2016-10-15 16:30 | 711 | 710
2016-10-15 17:00 | 741 | 741
2016-10-15 17:30 | 753 | 752
2016-10-15 18:00 | 761 | 760
2016-10-15 18:30 | 793 | 792
2016-10-15 19:00 | 825 | 819
2016-10-15 19:30 | 808 | 801
2016-10-15 20:00 | 788 | 787
2016-10-15 20:30 | 782 | 782
2016-10-15 21:00 | 757 | 756
2016-10-15 21:30 | 721 | 719
2016-10-15 22:00 | 712 | 711
2016-10-15 22:30 | 636 | 634
2016-10-15 23:00 | 683 | 682
2016-10-15 23:30 | 623 | 619
2016-10-16 | 577 | 570
2016-10-16 00:30 | 540 | 527
2016-10-16 01:00 | 530 | 516
2016-10-16 01:30 | 485 | 467
2016-10-16 02:00 | 466 | 443
2016-10-16 02:30 | 457 | 431
2016-10-16 03:00 | 454 | 429
2016-10-16 03:30 | 451 | 424
2016-10-16 04:00 | 447 | 421
2016-10-16 04:30 | 486 | 462
2016-10-16 05:00 | 462 | 436
2016-10-16 05:30 | 468 | 439
2016-10-16 06:00 | 485 | 455
2016-10-16 06:30 | 546 | 523
2016-10-16 07:00 | 563 | 545
2016-10-16 07:30 | 572 | 560
2016-10-16 08:00 | 578 | 569
2016-10-16 08:30 | 587 | 581
2016-10-16 09:00 | 591 | 588
2016-10-16 09:30 | 597 | 596
2016-10-16 10:00 | 599 | 598
2016-10-16 10:30 | 591 | 591
2016-10-16 11:00 | 584 | 584
2016-10-16 11:30 | 570 | 570
2016-10-16 12:00 | 568 | 567
2016-10-16 12:30 | 566 | 565
2016-10-16 13:00 | 556 | 555
2016-10-16 13:30 | 565 | 564
2016-10-16 14:00 | 582 | 581
2016-10-16 14:30 | 600 | 600
2016-10-16 15:00 | 623 | 622
2016-10-16 15:30 | 650 | 648
2016-10-16 16:00 | 680 | 678
2016-10-16 16:30 | 708 | 706
2016-10-16 17:00 | 748 | 747
2016-10-16 17:30 | 765 | 765
2016-10-16 18:00 | 787 | 787
2016-10-16 18:30 | 829 | 828
2016-10-16 19:00 | 849 | 848
2016-10-16 19:30 | 839 | 837
2016-10-16 20:00 | 828 | 825
2016-10-16 20:30 | 810 | 808
2016-10-16 21:00 | 770 | 770
2016-10-16 21:30 | 743 | 742
2016-10-16 22:00 | 713 | 712
2016-10-16 22:30 | 702 | 701
2016-10-16 23:00 | 705 | 704
2016-10-16 23:30 | 664 | 661
2016-10-17 | 628 | 622
2016-10-17 00:30 | 596 | 588
2016-10-17 01:00 | 578 | 567
2016-10-17 01:30 | 564 | 551
2016-10-17 02:00 | 549 | 533
2016-10-17 02:30 | 543 | 527
2016-10-17 03:00 | 540 | 522
2016-10-17 03:30 | 539 | 521
2016-10-17 04:00 | 541 | 524
2016-10-17 04:30 | 555 | 541
2016-10-17 05:00 | 565 | 554
2016-10-17 05:30 | 589 | 579
2016-10-17 06:00 | 629 | 621
2016-10-17 06:30 | 685 | 681
2016-10-17 07:00 | 738 | 735
2016-10-17 07:30 | 772 | 766
2016-10-17 08:00 | 787 | 784
2016-10-17 08:30 | 787 | 785
2016-10-17 09:00 | 788 | 787
2016-10-17 09:30 | 784 | 782
2016-10-17 10:00 | 784 | 784
2016-10-17 10:30 | 791 | 791
2016-10-17 11:00 | 782 | 781
2016-10-17 11:30 | 801 | 801
2016-10-17 12:00 | 808 | 808
2016-10-17 12:30 | 808 | 808
2016-10-17 13:00 | 839 | 839
2016-10-17 13:30 | 847 | 841
2016-10-17 14:00 | 848 | 841
2016-10-17 14:30 | 833 | 826
2016-10-17 15:00 | 861 | 855
2016-10-17 15:30 | 885 | 880
2016-10-17 16:00 | 868 | 861
2016-10-17 16:30 | 906 | 900
2016-10-17 17:00 | 954 | 949
2016-10-17 17:30 | 981 | 978
2016-10-17 18:00 | 969 | 963
2016-10-17 18:30 | 957 | 951
2016-10-17 19:00 | 960 | 953
2016-10-17 19:30 | 934 | 927
2016-10-17 20:00 | 906 | 905
2016-10-17 20:30 | 881 | 878
2016-10-17 21:00 | 836 | 834
2016-10-17 21:30 | 798 | 797
2016-10-17 22:00 | 765 | 762
2016-10-17 22:30 | 743 | 737
2016-10-17 23:00 | 745 | 739
2016-10-17 23:30 | 676 | 668
2016-10-18 | 658 | 648
2016-10-18 00:30 | 623 | 610
2016-10-18 01:00 | 592 | 582
2016-10-18 01:30 | 578 | 566
2016-10-18 02:00 | 565 | 550
2016-10-18 02:30 | 559 | 544
2016-10-18 03:00 | 536 | 518
2016-10-18 03:30 | 540 | 522
2016-10-18 04:00 | 513 | 495
2016-10-18 04:30 | 570 | 556
2016-10-18 05:00 | 589 | 577
2016-10-18 05:30 | 617 | 608
2016-10-18 06:00 | 650 | 644
2016-10-18 06:30 | 701 | 696
2016-10-18 07:00 | 747 | 746
2016-10-18 07:30 | 764 | 764
2016-10-18 08:00 | 761 | 761
2016-10-18 08:30 | 746 | 746
2016-10-18 09:00 | 725 | 725
2016-10-18 09:30 | 714 | 714
2016-10-18 10:00 | 706 | 706
2016-10-18 10:30 | 691 | 691
2016-10-18 11:00 | 687 | 687
2016-10-18 11:30 | 683 | 683
2016-10-18 12:00 | 681 | 681
2016-10-18 12:30 | 679 | 678
2016-10-18 13:00 | 665 | 665
2016-10-18 13:30 | 656 | 656
2016-10-18 14:00 | 728 | 728
2016-10-18 14:30 | 749 | 749
2016-10-18 15:00 | 775 | 775
2016-10-18 15:30 | 800 | 800
2016-10-18 16:00 | 840 | 839
2016-10-18 16:30 | 868 | 867
2016-10-18 17:00 | 897 | 896
2016-10-18 17:30 | 910 | 909
2016-10-18 18:00 | 910 | 908
2016-10-18 18:30 | 928 | 926
2016-10-18 19:00 | 950 | 944
2016-10-18 19:30 | 928 | 919
2016-10-18 20:00 | 905 | 902
2016-10-18 20:30 | 890 | 887
2016-10-18 21:00 | 846 | 843
2016-10-18 21:30 | 814 | 812
2016-10-18 22:00 | 775 | 774
2016-10-18 22:30 | 755 | 755
2016-10-18 23:00 | 761 | 761
2016-10-18 23:30 | 708 | 707
2016-10-19 | 659 | 656
2016-10-19 00:30 | 626 | 622
2016-10-19 01:00 | 606 | 601
2016-10-19 01:30 | 587 | 579
2016-10-19 02:00 | 569 | 561
2016-10-19 02:30 | 563 | 553
2016-10-19 03:00 | 562 | 552
2016-10-19 03:30 | 565 | 555
2016-10-19 04:00 | 564 | 554
2016-10-19 04:30 | 580 | 573
2016-10-19 05:00 | 598 | 594
2016-10-19 05:30 | 642 | 639
2016-10-19 06:00 | 674 | 673
2016-10-19 06:30 | 721 | 721
2016-10-19 07:00 | 765 | 764
2016-10-19 07:30 | 793 | 793
2016-10-19 08:00 | 794 | 794
2016-10-19 08:30 | 787 | 787
2016-10-19 09:00 | 776 | 774
2016-10-19 09:30 | 750 | 749
2016-10-19 10:00 | 703 | 703
2016-10-19 10:30 | 697 | 697
2016-10-19 11:00 | 703 | 703
2016-10-19 11:30 | 752 | 752
2016-10-19 12:00 | 756 | 756
2016-10-19 12:30 | 765 | 765
2016-10-19 13:00 | 768 | 767
2016-10-19 13:30 | 773 | 773
2016-10-19 14:00 | 791 | 791
2016-10-19 14:30 | 808 | 808
2016-10-19 15:00 | 821 | 820
2016-10-19 15:30 | 836 | 836
2016-10-19 16:00 | 866 | 866
2016-10-19 16:30 | 899 | 898
2016-10-19 17:00 | 932 | 931
2016-10-19 17:30 | 936 | 935
2016-10-19 18:00 | 937 | 935
2016-10-19 18:30 | 952 | 951
2016-10-19 19:00 | 975 | 974
2016-10-19 19:30 | 955 | 954
2016-10-19 20:00 | 940 | 939
2016-10-19 20:30 | 919 | 917
2016-10-19 21:00 | 875 | 873
2016-10-19 21:30 | 830 | 826
2016-10-19 22:00 | 793 | 788
2016-10-19 22:30 | 767 | 766
2016-10-19 23:00 | 767 | 766
2016-10-19 23:30 | 727 | 725
2016-10-20 | 676 | 671
2016-10-20 00:30 | 633 | 625
2016-10-20 01:00 | 605 | 598
2016-10-20 01:30 | 596 | 587
2016-10-20 02:00 | 575 | 564
2016-10-20 02:30 | 568 | 554
2016-10-20 03:00 | 567 | 552
2016-10-20 03:30 | 563 | 547
2016-10-20 04:00 | 563 | 548
2016-10-20 04:30 | 580 | 567
2016-10-20 05:00 | 594 | 584
2016-10-20 05:30 | 617 | 610
2016-10-20 06:00 | 647 | 643
2016-10-20 06:30 | 709 | 708
2016-10-20 07:00 | 760 | 760
2016-10-20 07:30 | 799 | 799
2016-10-20 08:00 | 805 | 805
2016-10-20 08:30 | 801 | 800
2016-10-20 09:00 | 813 | 811
2016-10-20 09:30 | 825 | 824
2016-10-20 10:00 | 831 | 830
2016-10-20 10:30 | 846 | 844
2016-10-20 11:00 | 808 | 806
2016-10-20 11:30 | 819 | 816
2016-10-20 12:00 | 838 | 835
2016-10-20 12:30 | 842 | 842
2016-10-20 13:00 | 825 | 820
2016-10-20 13:30 | 835 | 833
2016-10-20 14:00 | 841 | 839
2016-10-20 14:30 | 846 | 844
2016-10-20 15:00 | 882 | 880
2016-10-20 15:30 | 892 | 891
2016-10-20 16:00 | 921 | 920
2016-10-20 16:30 | 948 | 946
2016-10-20 17:00 | 959 | 957
2016-10-20 17:30 | 979 | 977
2016-10-20 18:00 | 981 | 978
2016-10-20 18:30 | 990 | 988
2016-10-20 19:00 | 948 | 947
2016-10-20 19:30 | 941 | 939
2016-10-20 20:00 | 933 | 931
2016-10-20 20:30 | 893 | 890
2016-10-20 21:00 | 833 | 833
2016-10-20 21:30 | 824 | 824
2016-10-20 22:00 | 791 | 790
2016-10-20 22:30 | 767 | 765
2016-10-20 23:00 | 716 | 714
2016-10-20 23:30 | 721 | 718
2016-10-21 | 639 | 632
2016-10-21 00:30 | 642 | 637
2016-10-21 01:00 | 601 | 591
2016-10-21 01:30 | 563 | 549
2016-10-21 02:00 | 531 | 515
2016-10-21 02:30 | 489 | 470
2016-10-21 03:00 | 537 | 518
2016-10-21 03:30 | 550 | 531
2016-10-21 04:00 | 556 | 539
2016-10-21 04:30 | 563 | 547
2016-10-21 05:00 | 585 | 573
2016-10-21 05:30 | 622 | 613
2016-10-21 06:00 | 660 | 654
2016-10-21 06:30 | 716 | 712
2016-10-21 07:00 | 769 | 763
2016-10-21 07:30 | 807 | 802
2016-10-21 08:00 | 825 | 821
2016-10-21 08:30 | 833 | 827
2016-10-21 09:00 | 820 | 815
2016-10-21 09:30 | 812 | 807
2016-10-21 10:00 | 807 | 802
2016-10-21 10:30 | 801 | 798
2016-10-21 11:00 | 793 | 789
2016-10-21 11:30 | 796 | 793
2016-10-21 12:00 | 794 | 791
2016-10-21 12:30 | 788 | 785
2016-10-21 13:00 | 794 | 788
2016-10-21 13:30 | 793 | 785
2016-10-21 14:00 | 816 | 810
2016-10-21 14:30 | 810 | 802
2016-10-21 15:00 | 840 | 832
2016-10-21 15:30 | 862 | 853
2016-10-21 16:00 | 871 | 862
2016-10-21 16:30 | 899 | 890
2016-10-21 17:00 | 925 | 915
2016-10-21 17:30 | 925 | 912
2016-10-21 18:00 | 915 | 901
2016-10-21 18:30 | 921 | 913
2016-10-21 19:00 | 933 | 926
2016-10-21 19:30 | 923 | 915
2016-10-21 20:00 | 902 | 901
2016-10-21 20:30 | 882 | 880
2016-10-21 21:00 | 843 | 840
2016-10-21 21:30 | 808 | 805
2016-10-21 22:00 | 786 | 783
2016-10-21 22:30 | 776 | 771
2016-10-21 23:00 | 780 | 775
2016-10-21 23:30 | 724 | 720
2016-10-22 | 675 | 670
2016-10-22 00:30 | 641 | 635
2016-10-22 01:00 | 617 | 608
2016-10-22 01:30 | 591 | 580
2016-10-22 02:00 | 575 | 559
2016-10-22 02:30 | 569 | 553
2016-10-22 03:00 | 565 | 548
2016-10-22 03:30 | 564 | 546
2016-10-22 04:00 | 563 | 545
2016-10-22 04:30 | 563 | 545
2016-10-22 05:00 | 564 | 546
2016-10-22 05:30 | 574 | 554
2016-10-22 06:00 | 585 | 568
2016-10-22 06:30 | 610 | 599
2016-10-22 07:00 | 640 | 634
2016-10-22 07:30 | 660 | 658
2016-10-22 08:00 | 670 | 669
2016-10-22 08:30 | 713 | 711
2016-10-22 09:00 | 726 | 726
2016-10-22 09:30 | 714 | 713
2016-10-22 10:00 | 699 | 698
2016-10-22 10:30 | 684 | 683
2016-10-22 11:00 | 675 | 674
2016-10-22 11:30 | 673 | 672
2016-10-22 12:00 | 669 | 668
2016-10-22 12:30 | 648 | 646
2016-10-22 13:00 | 657 | 655
2016-10-22 13:30 | 660 | 658
2016-10-22 14:00 | 707 | 706
2016-10-22 14:30 | 749 | 748
2016-10-22 15:00 | 760 | 758
2016-10-22 15:30 | 777 | 775
2016-10-22 16:00 | 768 | 764
2016-10-22 16:30 | 778 | 774
2016-10-22 17:00 | 808 | 796
2016-10-22 17:30 | 808 | 803
2016-10-22 18:00 | 816 | 813
2016-10-22 18:30 | 836 | 835
2016-10-22 19:00 | 868 | 866
2016-10-22 19:30 | 851 | 848
2016-10-22 20:00 | 836 | 834
2016-10-22 20:30 | 824 | 822
2016-10-22 21:00 | 793 | 791
2016-10-22 21:30 | 769 | 765
2016-10-22 22:00 | 749 | 748
2016-10-22 22:30 | 737 | 736
2016-10-22 23:00 | 748 | 748
2016-10-22 23:30 | 705 | 704
2016-10-23 | 664 | 660
2016-10-23 00:30 | 633 | 628
2016-10-23 01:00 | 608 | 601
2016-10-23 01:30 | 589 | 582
2016-10-23 02:00 | 573 | 563
2016-10-23 02:30 | 565 | 553
2016-10-23 03:00 | 561 | 546
2016-10-23 03:30 | 558 | 543
2016-10-23 04:00 | 559 | 542
2016-10-23 04:30 | 556 | 540
2016-10-23 05:00 | 554 | 539
2016-10-23 05:30 | 561 | 545
2016-10-23 06:00 | 563 | 546
2016-10-23 06:30 | 578 | 563
2016-10-23 07:00 | 580 | 568
2016-10-23 07:30 | 620 | 613
2016-10-23 08:00 | 653 | 648
2016-10-23 08:30 | 616 | 614
2016-10-23 09:00 | 618 | 616
2016-10-23 09:30 | 612 | 611
2016-10-23 10:00 | 623 | 622
2016-10-23 10:30 | 629 | 629
2016-10-23 11:00 | 639 | 639
2016-10-23 11:30 | 638 | 638
2016-10-23 12:00 | 631 | 629
2016-10-23 12:30 | 623 | 621
2016-10-23 13:00 | 626 | 624
2016-10-23 13:30 | 624 | 622
2016-10-23 14:00 | 623 | 620
2016-10-23 14:30 | 673 | 669
2016-10-23 15:00 | 678 | 673
2016-10-23 15:30 | 694 | 691
2016-10-23 16:00 | 713 | 711
2016-10-23 16:30 | 740 | 737
2016-10-23 17:00 | 776 | 775
2016-10-23 17:30 | 808 | 808
2016-10-23 18:00 | 830 | 830
2016-10-23 18:30 | 851 | 851
2016-10-23 19:00 | 878 | 878
2016-10-23 19:30 | 860 | 859
2016-10-23 20:00 | 846 | 845
2016-10-23 20:30 | 843 | 841
2016-10-23 21:00 | 805 | 804
2016-10-23 21:30 | 771 | 770
2016-10-23 22:00 | 742 | 742
2016-10-23 22:30 | 732 | 731
2016-10-23 23:00 | 739 | 739
2016-10-23 23:30 | 700 | 698
2016-10-24 | 645 | 640
2016-10-24 00:30 | 608 | 601
2016-10-24 01:00 | 587 | 576
2016-10-24 01:30 | 567 | 555
2016-10-24 02:00 | 550 | 535
2016-10-24 02:30 | 542 | 526
2016-10-24 03:00 | 536 | 519
2016-10-24 03:30 | 541 | 524
2016-10-24 04:00 | 547 | 531
2016-10-24 04:30 | 558 | 545
2016-10-24 05:00 | 575 | 564
2016-10-24 05:30 | 603 | 594
2016-10-24 06:00 | 641 | 636
2016-10-24 06:30 | 701 | 700
2016-10-24 07:00 | 741 | 741
2016-10-24 07:30 | 786 | 786
2016-10-24 08:00 | 785 | 785
2016-10-24 08:30 | 779 | 779
2016-10-24 09:00 | 750 | 750
2016-10-24 09:30 | 741 | 741
2016-10-24 10:00 | 737 | 737
2016-10-24 10:30 | 736 | 735
2016-10-24 11:00 | 726 | 725
2016-10-24 11:30 | 724 | 723
2016-10-24 12:00 | 733 | 732
2016-10-24 12:30 | 736 | 735
2016-10-24 13:00 | 732 | 732
2016-10-24 13:30 | 739 | 739
2016-10-24 14:00 | 747 | 747
2016-10-24 14:30 | 754 | 754
2016-10-24 15:00 | 780 | 780
2016-10-24 15:30 | 803 | 803
2016-10-24 16:00 | 835 | 835
2016-10-24 16:30 | 863 | 863
2016-10-24 17:00 | 889 | 889
2016-10-24 17:30 | 908 | 908
2016-10-24 18:00 | 919 | 919
2016-10-24 18:30 | 938 | 938
2016-10-24 19:00 | 970 | 970
2016-10-24 19:30 | 944 | 943
2016-10-24 20:00 | 931 | 929
2016-10-24 20:30 | 920 | 918
2016-10-24 21:00 | 871 | 868
2016-10-24 21:30 | 827 | 825
2016-10-24 22:00 | 794 | 789
2016-10-24 22:30 | 771 | 768
2016-10-24 23:00 | 758 | 756
2016-10-24 23:30 | 717 | 715
2016-10-25 | 682 | 679
2016-10-25 00:30 | 639 | 634
2016-10-25 01:00 | 613 | 605
2016-10-25 01:30 | 589 | 577
2016-10-25 02:00 | 581 | 566
2016-10-25 02:30 | 573 | 558
2016-10-25 03:00 | 570 | 554
2016-10-25 03:30 | 557 | 542
2016-10-25 04:00 | 561 | 546
2016-10-25 04:30 | 582 | 570
2016-10-25 05:00 | 585 | 575
2016-10-25 05:30 | 621 | 612
2016-10-25 06:00 | 653 | 648
2016-10-25 06:30 | 711 | 710
2016-10-25 07:00 | 751 | 751
2016-10-25 07:30 | 787 | 786
2016-10-25 08:00 | 778 | 777
2016-10-25 08:30 | 768 | 768
2016-10-25 09:00 | 757 | 757
2016-10-25 09:30 | 743 | 743
2016-10-25 10:00 | 745 | 745
2016-10-25 10:30 | 745 | 744
2016-10-25 11:00 | 738 | 737
2016-10-25 11:30 | 737 | 736
2016-10-25 12:00 | 744 | 743
2016-10-25 12:30 | 745 | 744
2016-10-25 13:00 | 755 | 754
2016-10-25 13:30 | 758 | 757
2016-10-25 14:00 | 776 | 775
2016-10-25 14:30 | 790 | 789
2016-10-25 15:00 | 803 | 803
2016-10-25 15:30 | 824 | 824
2016-10-25 16:00 | 855 | 854
2016-10-25 16:30 | 884 | 883
2016-10-25 17:00 | 917 | 916
2016-10-25 17:30 | 923 | 920
2016-10-25 18:00 | 924 | 920
2016-10-25 18:30 | 940 | 937
2016-10-25 19:00 | 970 | 968
2016-10-25 19:30 | 951 | 948
2016-10-25 20:00 | 940 | 935
2016-10-25 20:30 | 909 | 908
2016-10-25 21:00 | 877 | 876
2016-10-25 21:30 | 826 | 823
2016-10-25 22:00 | 797 | 793
2016-10-25 22:30 | 769 | 764
2016-10-25 23:00 | 772 | 768
2016-10-25 23:30 | 725 | 718
2016-10-26 | 682 | 673
2016-10-26 00:30 | 642 | 635
2016-10-26 01:00 | 602 | 591
2016-10-26 01:30 | 596 | 583
2016-10-26 02:00 | 582 | 567
2016-10-26 02:30 | 577 | 561
2016-10-26 03:00 | 576 | 561
2016-10-26 03:30 | 575 | 561
2016-10-26 04:00 | 576 | 562
2016-10-26 04:30 | 588 | 576
2016-10-26 05:00 | 597 | 586
2016-10-26 05:30 | 622 | 613
2016-10-26 06:00 | 654 | 649
2016-10-26 06:30 | 721 | 720
2016-10-26 07:00 | 769 | 768
2016-10-26 07:30 | 806 | 806
2016-10-26 08:00 | 809 | 809
2016-10-26 08:30 | 808 | 808
2016-10-26 09:00 | 793 | 793
2016-10-26 09:30 | 792 | 792
2016-10-26 10:00 | 798 | 797
2016-10-26 10:30 | 798 | 797
2016-10-26 11:00 | 801 | 801
2016-10-26 11:30 | 803 | 803
2016-10-26 12:00 | 806 | 806
2016-10-26 12:30 | 807 | 806
2016-10-26 13:00 | 814 | 814
2016-10-26 13:30 | 815 | 815
2016-10-26 14:00 | 837 | 836
2016-10-26 14:30 | 866 | 865
2016-10-26 15:00 | 875 | 875
2016-10-26 15:30 | 890 | 889
2016-10-26 16:00 | 917 | 916
2016-10-26 16:30 | 950 | 949
2016-10-26 17:00 | 960 | 959
2016-10-26 17:30 | 960 | 958
2016-10-26 18:00 | 956 | 951
2016-10-26 18:30 | 960 | 956
2016-10-26 19:00 | 977 | 974
2016-10-26 19:30 | 960 | 956
2016-10-26 20:00 | 950 | 948
2016-10-26 20:30 | 924 | 923
2016-10-26 21:00 | 881 | 880
2016-10-26 21:30 | 841 | 837
2016-10-26 22:00 | 807 | 802
2016-10-26 22:30 | 776 | 768
2016-10-26 23:00 | 767 | 762
2016-10-26 23:30 | 735 | 728
2016-10-27 | 687 | 679
2016-10-27 00:30 | 643 | 637
2016-10-27 01:00 | 621 | 613
2016-10-27 01:30 | 601 | 590
2016-10-27 02:00 | 585 | 572
2016-10-27 02:30 | 577 | 563
2016-10-27 03:00 | 578 | 564
2016-10-27 03:30 | 577 | 562
2016-10-27 04:00 | 580 | 565
2016-10-27 04:30 | 587 | 574
2016-10-27 05:00 | 598 | 588
2016-10-27 05:30 | 627 | 619
2016-10-27 06:00 | 665 | 661
2016-10-27 06:30 | 708 | 707
2016-10-27 07:00 | 777 | 776
2016-10-27 07:30 | 823 | 819
2016-10-27 08:00 | 790 | 788
2016-10-27 08:30 | 826 | 825
2016-10-27 09:00 | 791 | 790
2016-10-27 09:30 | 776 | 773
2016-10-27 10:00 | 770 | 768
2016-10-27 10:30 | 775 | 774
2016-10-27 11:00 | 781 | 780
2016-10-27 11:30 | 793 | 793
2016-10-27 12:00 | 796 | 796
2016-10-27 12:30 | 816 | 815
2016-10-27 13:00 | 834 | 832
2016-10-27 13:30 | 833 | 832
2016-10-27 14:00 | 849 | 849
2016-10-27 14:30 | 866 | 865
2016-10-27 15:00 | 898 | 897
2016-10-27 15:30 | 934 | 933
2016-10-27 16:00 | 949 | 947
2016-10-27 16:30 | 956 | 953
2016-10-27 17:00 | 976 | 972
2016-10-27 17:30 | 973 | 967
2016-10-27 18:00 | 974 | 966
2016-10-27 18:30 | 971 | 964
2016-10-27 19:00 | 971 | 966
2016-10-27 19:30 | 941 | 934
2016-10-27 20:00 | 932 | 929
2016-10-27 20:30 | 929 | 926
2016-10-27 21:00 | 893 | 892
2016-10-27 21:30 | 849 | 847
2016-10-27 22:00 | 820 | 818
2016-10-27 22:30 | 796 | 793
2016-10-27 23:00 | 789 | 788
2016-10-27 23:30 | 737 | 736
2016-10-28 | 694 | 691
2016-10-28 00:30 | 657 | 652
2016-10-28 01:00 | 634 | 627
2016-10-28 01:30 | 611 | 600
2016-10-28 02:00 | 598 | 585
2016-10-28 02:30 | 588 | 574
2016-10-28 03:00 | 585 | 572
2016-10-28 03:30 | 585 | 572
2016-10-28 04:00 | 585 | 573
2016-10-28 04:30 | 595 | 584
2016-10-28 05:00 | 607 | 597
2016-10-28 05:30 | 637 | 628
2016-10-28 06:00 | 652 | 648
2016-10-28 06:30 | 717 | 717
2016-10-28 07:00 | 768 | 764
2016-10-28 07:30 | 833 | 829
2016-10-28 08:00 | 847 | 846
2016-10-28 08:30 | 861 | 860
2016-10-28 09:00 | 869 | 864
2016-10-28 09:30 | 854 | 849
2016-10-28 10:00 | 850 | 845
2016-10-28 10:30 | 849 | 846
2016-10-28 11:00 | 857 | 855
2016-10-28 11:30 | 868 | 866
2016-10-28 12:00 | 902 | 902
2016-10-28 12:30 | 887 | 885
2016-10-28 13:00 | 879 | 878
2016-10-28 13:30 | 873 | 871
2016-10-28 14:00 | 869 | 867
2016-10-28 14:30 | 867 | 864
2016-10-28 15:00 | 884 | 881
2016-10-28 15:30 | 905 | 902
2016-10-28 16:00 | 932 | 929
2016-10-28 16:30 | 944 | 940
2016-10-28 17:00 | 950 | 944
2016-10-28 17:30 | 946 | 938
2016-10-28 18:00 | 934 | 921
2016-10-28 18:30 | 925 | 917
2016-10-28 19:00 | 949 | 944
2016-10-28 19:30 | 937 | 929
2016-10-28 20:00 | 930 | 923
2016-10-28 20:30 | 905 | 901
2016-10-28 21:00 | 861 | 860
2016-10-28 21:30 | 832 | 832
2016-10-28 22:00 | 811 | 809
2016-10-28 22:30 | 795 | 793
2016-10-28 23:00 | 800 | 800
2016-10-28 23:30 | 750 | 748
2016-10-29 | 704 | 698
2016-10-29 00:30 | 668 | 662
2016-10-29 01:00 | 637 | 630
2016-10-29 01:30 | 617 | 608
2016-10-29 02:00 | 604 | 592
2016-10-29 02:30 | 594 | 581
2016-10-29 03:00 | 586 | 572
2016-10-29 03:30 | 582 | 568
2016-10-29 04:00 | 580 | 566
2016-10-29 04:30 | 580 | 566
2016-10-29 05:00 | 587 | 574
2016-10-29 05:30 | 597 | 580
2016-10-29 06:00 | 611 | 596
2016-10-29 06:30 | 633 | 623
2016-10-29 07:00 | 648 | 642
2016-10-29 07:30 | 654 | 651
2016-10-29 08:00 | 679 | 679
2016-10-29 08:30 | 731 | 731
2016-10-29 09:00 | 751 | 750
2016-10-29 09:30 | 756 | 753
2016-10-29 10:00 | 748 | 746
2016-10-29 10:30 | 728 | 726
2016-10-29 11:00 | 719 | 717
2016-10-29 11:30 | 708 | 706
2016-10-29 12:00 | 714 | 712
2016-10-29 12:30 | 707 | 705
2016-10-29 13:00 | 698 | 696
2016-10-29 13:30 | 704 | 701
2016-10-29 14:00 | 711 | 709
2016-10-29 14:30 | 726 | 724
2016-10-29 15:00 | 752 | 750
2016-10-29 15:30 | 765 | 762
2016-10-29 16:00 | 791 | 789
2016-10-29 16:30 | 805 | 803
2016-10-29 17:00 | 828 | 826
2016-10-29 17:30 | 831 | 829
2016-10-29 18:00 | 825 | 821
2016-10-29 18:30 | 840 | 837
2016-10-29 19:00 | 866 | 864
2016-10-29 19:30 | 849 | 847
2016-10-29 20:00 | 841 | 838
2016-10-29 20:30 | 823 | 822
2016-10-29 21:00 | 795 | 795
2016-10-29 21:30 | 772 | 772
2016-10-29 22:00 | 746 | 744
2016-10-29 22:30 | 706 | 703
2016-10-29 23:00 | 691 | 689
2016-10-29 23:30 | 659 | 656
2016-10-30 | 668 | 663
2016-10-30 00:30 | 606 | 597
2016-10-30 01:00 | 598 | 587
2016-10-30 01:30 | 537 | 521
2016-10-30 02:00 | 538 | 520
2016-10-30 02:30 | 525 | 505
2016-10-30 03:00 | 507 | 483
2016-10-30 03:30 | 503 | 479
2016-10-30 04:00 | 519 | 495
2016-10-30 04:30 | 499 | 474
2016-10-30 05:00 | 499 | 470
2016-10-30 05:30 | 549 | 521
2016-10-30 06:00 | 550 | 523
2016-10-30 06:30 | 580 | 561
2016-10-30 07:00 | 583 | 569
2016-10-30 07:30 | 605 | 597
2016-10-30 08:00 | 619 | 616
2016-10-30 08:30 | 645 | 643
2016-10-30 09:00 | 603 | 602
2016-10-30 09:30 | 620 | 620
2016-10-30 10:00 | 620 | 620
2016-10-30 10:30 | 646 | 646
2016-10-30 11:00 | 644 | 644
2016-10-30 11:30 | 630 | 630
2016-10-30 12:00 | 597 | 597
2016-10-30 12:30 | 632 | 632
2016-10-30 13:00 | 604 | 603
2016-10-30 13:30 | 629 | 629
2016-10-30 14:00 | 606 | 606
2016-10-30 14:30 | 624 | 624
2016-10-30 15:00 | 690 | 690
2016-10-30 15:30 | 693 | 693
2016-10-30 16:00 | 748 | 748
2016-10-30 16:30 | 787 | 786
2016-10-30 17:00 | 817 | 814
2016-10-30 17:30 | 828 | 820
2016-10-30 18:00 | 830 | 820
2016-10-30 18:30 | 861 | 856
2016-10-30 19:00 | 873 | 869
2016-10-30 19:30 | 873 | 864
2016-10-30 20:00 | 866 | 855
2016-10-30 20:30 | 854 | 845
2016-10-30 21:00 | 813 | 808
2016-10-30 21:30 | 777 | 775
2016-10-30 22:00 | 760 | 758
2016-10-30 22:30 | 706 | 703
2016-10-30 23:00 | 699 | 698
2016-10-30 23:30 | 706 | 703
2016-10-31 | 657 | 651
2016-10-31 00:30 | 626 | 617
2016-10-31 01:00 | 607 | 596
2016-10-31 01:30 | 594 | 582
2016-10-31 02:00 | 581 | 568
2016-10-31 02:30 | 575 | 561
2016-10-31 03:00 | 577 | 562
2016-10-31 03:30 | 570 | 556
2016-10-31 04:00 | 573 | 560
2016-10-31 04:30 | 586 | 575
2016-10-31 05:00 | 595 | 585
2016-10-31 05:30 | 622 | 613
2016-10-31 06:00 | 663 | 657
2016-10-31 06:30 | 734 | 727
2016-10-31 07:00 | 802 | 797
2016-10-31 07:30 | 854 | 853
2016-10-31 08:00 | 899 | 896
2016-10-31 08:30 | 911 | 905
2016-10-31 09:00 | 899 | 894
2016-10-31 09:30 | 915 | 908
2016-10-31 10:00 | 914 | 907
2016-10-31 10:30 | 901 | 894
2016-10-31 11:00 | 919 | 913
2016-10-31 11:30 | 897 | 890
2016-10-31 12:00 | 889 | 882
2016-10-31 12:30 | 885 | 878
2016-10-31 13:00 | 889 | 882
2016-10-31 13:30 | 913 | 908
2016-10-31 14:00 | 867 | 859
2016-10-31 14:30 | 853 | 845
2016-10-31 15:00 | 881 | 875
2016-10-31 15:30 | 893 | 887
2016-10-31 16:00 | 932 | 927
2016-10-31 16:30 | 942 | 938
2016-10-31 17:00 | 976 | 972
2016-10-31 17:30 | 977 | 969
2016-10-31 18:00 | 978 | 961
2016-10-31 18:30 | 967 | 954
2016-10-31 19:00 | 981 | 974
2016-10-31 19:30 | 985 | 976
2016-10-31 20:00 | 976 | 965
2016-10-31 20:30 | 954 | 945
2016-10-31 21:00 | 907 | 904
2016-10-31 21:30 | 869 | 863
2016-10-31 22:00 | 833 | 828
2016-10-31 22:30 | 805 | 805
2016-10-31 23:00 | 800 | 800
2016-10-31 23:30 | 750 | 748
2016-11-01 | 700 | 698
2016-11-01 00:30 | 658 | 655
2016-11-01 01:00 | 634 | 630
2016-11-01 01:30 | 617 | 611
2016-11-01 02:00 | 607 | 598
2016-11-01 02:30 | 598 | 589
2016-11-01 03:00 | 590 | 579
2016-11-01 03:30 | 579 | 568
2016-11-01 04:00 | 585 | 574
2016-11-01 04:30 | 604 | 595
2016-11-01 05:00 | 615 | 608
2016-11-01 05:30 | 643 | 637
2016-11-01 06:00 | 674 | 671
2016-11-01 06:30 | 746 | 745
2016-11-01 07:00 | 823 | 822
2016-11-01 07:30 | 891 | 889
2016-11-01 08:00 | 936 | 931
2016-11-01 08:30 | 965 | 962
2016-11-01 09:00 | 1005 | 1003
2016-11-01 09:30 | 1001 | 998
2016-11-01 10:00 | 1064 | 1061
2016-11-01 10:30 | 1169 | 1167
2016-11-01 11:00 | 1151 | 1149
2016-11-01 11:30 | 1091 | 1087
2016-11-01 12:00 | 1048 | 1042
2016-11-01 12:30 | 1047 | 1040
2016-11-01 13:00 | 1035 | 1028
2016-11-01 13:30 | 1040 | 1033
2016-11-01 14:00 | 1027 | 1020
2016-11-01 14:30 | 1055 | 1049
2016-11-01 15:00 | 1072 | 1067
2016-11-01 15:30 | 1065 | 1059
2016-11-01 16:00 | 1058 | 1050
2016-11-01 16:30 | 1074 | 1067
2016-11-01 17:00 | 1122 | 1115
2016-11-01 17:30 | 1117 | 1107
2016-11-01 18:00 | 1102 | 1090
2016-11-01 18:30 | 1107 | 1097
2016-11-01 19:00 | 1136 | 1130
2016-11-01 19:30 | 1123 | 1115
2016-11-01 20:00 | 1108 | 1101
2016-11-01 20:30 | 1095 | 1087
2016-11-01 21:00 | 1046 | 1036
2016-11-01 21:30 | 1002 | 992
2016-11-01 22:00 | 962 | 956
2016-11-01 22:30 | 924 | 915
2016-11-01 23:00 | 909 | 906
2016-11-01 23:30 | 850 | 845
2016-11-02 | 792 | 786
2016-11-02 00:30 | 748 | 741
2016-11-02 01:00 | 715 | 708
2016-11-02 01:30 | 691 | 681
2016-11-02 02:00 | 677 | 664
2016-11-02 02:30 | 666 | 652
2016-11-02 03:00 | 663 | 648
2016-11-02 03:30 | 662 | 647
2016-11-02 04:00 | 664 | 650
2016-11-02 04:30 | 677 | 665
2016-11-02 05:00 | 692 | 679
2016-11-02 05:30 | 719 | 708
2016-11-02 06:00 | 759 | 753
2016-11-02 06:30 | 816 | 814
2016-11-02 07:00 | 878 | 869
2016-11-02 07:30 | 919 | 913
2016-11-02 08:00 | 928 | 922
2016-11-02 08:30 | 923 | 914
2016-11-02 09:00 | 918 | 911
2016-11-02 09:30 | 904 | 898
2016-11-02 10:00 | 899 | 894
2016-11-02 10:30 | 910 | 907
2016-11-02 11:00 | 908 | 906
2016-11-02 11:30 | 908 | 907
2016-11-02 12:00 | 907 | 904
2016-11-02 12:30 | 910 | 902
2016-11-02 13:00 | 918 | 907
2016-11-02 13:30 | 926 | 915
2016-11-02 14:00 | 933 | 922
2016-11-02 14:30 | 957 | 946
2016-11-02 15:00 | 966 | 955
2016-11-02 15:30 | 991 | 980
2016-11-02 16:00 | 1026 | 1016
2016-11-02 16:30 | 1055 | 1046
2016-11-02 17:00 | 1086 | 1077
2016-11-02 17:30 | 1097 | 1084
2016-11-02 18:00 | 1094 | 1079
2016-11-02 18:30 | 1090 | 1082
2016-11-02 19:00 | 1111 | 1107
2016-11-02 19:30 | 1097 | 1090
2016-11-02 20:00 | 1077 | 1076
2016-11-02 20:30 | 1060 | 1059
2016-11-02 21:00 | 1012 | 1010
2016-11-02 21:30 | 967 | 963
2016-11-02 22:00 | 923 | 920
2016-11-02 22:30 | 901 | 898
2016-11-02 23:00 | 900 | 898
2016-11-02 23:30 | 848 | 846
2016-11-03 | 785 | 782
2016-11-03 00:30 | 740 | 736
2016-11-03 01:00 | 711 | 705
2016-11-03 01:30 | 692 | 684
2016-11-03 02:00 | 676 | 667
2016-11-03 02:30 | 666 | 656
2016-11-03 03:00 | 659 | 647
2016-11-03 03:30 | 656 | 645
2016-11-03 04:00 | 657 | 646
2016-11-03 04:30 | 677 | 668
2016-11-03 05:00 | 692 | 683
2016-11-03 05:30 | 708 | 701
2016-11-03 06:00 | 752 | 748
2016-11-03 06:30 | 821 | 819
2016-11-03 07:00 | 892 | 889
2016-11-03 07:30 | 941 | 939
2016-11-03 08:00 | 964 | 957
2016-11-03 08:30 | 976 | 971
2016-11-03 09:00 | 977 | 973
2016-11-03 09:30 | 971 | 968
2016-11-03 10:00 | 961 | 960
2016-11-03 10:30 | 966 | 965
2016-11-03 11:00 | 969 | 968
2016-11-03 11:30 | 968 | 968
2016-11-03 12:00 | 969 | 968
2016-11-03 12:30 | 979 | 978
2016-11-03 13:00 | 997 | 995
2016-11-03 13:30 | 1012 | 1009
2016-11-03 14:00 | 1004 | 1001
2016-11-03 14:30 | 1020 | 1018
2016-11-03 15:00 | 1013 | 1010
2016-11-03 15:30 | 1018 | 1014
2016-11-03 16:00 | 1044 | 1040
2016-11-03 16:30 | 1066 | 1062
2016-11-03 17:00 | 1088 | 1084
2016-11-03 17:30 | 1100 | 1093
2016-11-03 18:00 | 1112 | 1104
2016-11-03 18:30 | 1121 | 1116
2016-11-03 19:00 | 1158 | 1153
2016-11-03 19:30 | 1151 | 1140
2016-11-03 20:00 | 1132 | 1123
2016-11-03 20:30 | 1109 | 1102
2016-11-03 21:00 | 1055 | 1053
2016-11-03 21:30 | 991 | 989
2016-11-03 22:00 | 942 | 938
2016-11-03 22:30 | 912 | 909
2016-11-03 23:00 | 906 | 903
2016-11-03 23:30 | 852 | 848
2016-11-04 | 795 | 792
2016-11-04 00:30 | 754 | 749
2016-11-04 01:00 | 728 | 720
2016-11-04 01:30 | 708 | 698
2016-11-04 02:00 | 689 | 677
2016-11-04 02:30 | 681 | 668
2016-11-04 03:00 | 675 | 662
2016-11-04 03:30 | 671 | 658
2016-11-04 04:00 | 674 | 661
2016-11-04 04:30 | 690 | 678
2016-11-04 05:00 | 704 | 693
2016-11-04 05:30 | 734 | 724
2016-11-04 06:00 | 770 | 764
2016-11-04 06:30 | 833 | 832
2016-11-04 07:00 | 906 | 903
2016-11-04 07:30 | 950 | 948
2016-11-04 08:00 | 964 | 963
2016-11-04 08:30 | 963 | 963
2016-11-04 09:00 | 962 | 962
2016-11-04 09:30 | 961 | 961
2016-11-04 10:00 | 967 | 967
2016-11-04 10:30 | 966 | 965
2016-11-04 11:00 | 973 | 973
2016-11-04 11:30 | 973 | 973
2016-11-04 12:00 | 980 | 980
2016-11-04 12:30 | 997 | 996
2016-11-04 13:00 | 987 | 987
2016-11-04 13:30 | 1006 | 1005
2016-11-04 14:00 | 982 | 982
2016-11-04 14:30 | 1023 | 1023
2016-11-04 15:00 | 1047 | 1046
2016-11-04 15:30 | 1065 | 1064
2016-11-04 16:00 | 1094 | 1091
2016-11-04 16:30 | 1115 | 1112
2016-11-04 17:00 | 1128 | 1125
2016-11-04 17:30 | 1118 | 1114
2016-11-04 18:00 | 1084 | 1078
2016-11-04 18:30 | 1065 | 1063
2016-11-04 19:00 | 1094 | 1094
2016-11-04 19:30 | 1076 | 1075
2016-11-04 20:00 | 1059 | 1058
2016-11-04 20:30 | 1045 | 1045
2016-11-04 21:00 | 999 | 999
2016-11-04 21:30 | 960 | 960
2016-11-04 22:00 | 934 | 934
2016-11-04 22:30 | 892 | 891
2016-11-04 23:00 | 850 | 849
2016-11-04 23:30 | 835 | 834
2016-11-05 | 799 | 795
2016-11-05 00:30 | 707 | 700
2016-11-05 01:00 | 735 | 726
2016-11-05 01:30 | 710 | 700
2016-11-05 02:00 | 694 | 681
2016-11-05 02:30 | 672 | 657
2016-11-05 03:00 | 679 | 665
2016-11-05 03:30 | 642 | 625
2016-11-05 04:00 | 608 | 586
2016-11-05 04:30 | 667 | 648
2016-11-05 05:00 | 670 | 649
2016-11-05 05:30 | 671 | 648
2016-11-05 06:00 | 691 | 671
2016-11-05 06:30 | 709 | 695
2016-11-05 07:00 | 739 | 732
2016-11-05 07:30 | 765 | 762
2016-11-05 08:00 | 784 | 783
2016-11-05 08:30 | 798 | 798
2016-11-05 09:00 | 813 | 813
2016-11-05 09:30 | 827 | 827
2016-11-05 10:00 | 829 | 829
2016-11-05 10:30 | 840 | 840
2016-11-05 11:00 | 844 | 844
2016-11-05 11:30 | 839 | 839
2016-11-05 12:00 | 843 | 843
2016-11-05 12:30 | 859 | 859
2016-11-05 13:00 | 887 | 887
2016-11-05 13:30 | 903 | 903
2016-11-05 14:00 | 930 | 929
2016-11-05 14:30 | 957 | 956
2016-11-05 15:00 | 975 | 975
2016-11-05 15:30 | 971 | 971
2016-11-05 16:00 | 1030 | 1027
2016-11-05 16:30 | 1082 | 1078
2016-11-05 17:00 | 1109 | 1102
2016-11-05 17:30 | 1099 | 1089
2016-11-05 18:00 | 1070 | 1055
2016-11-05 18:30 | 1068 | 1058
2016-11-05 19:00 | 1092 | 1085
2016-11-05 19:30 | 1084 | 1077
2016-11-05 20:00 | 1064 | 1063
2016-11-05 20:30 | 1045 | 1044
2016-11-05 21:00 | 988 | 988
2016-11-05 21:30 | 952 | 952
2016-11-05 22:00 | 926 | 925
2016-11-05 22:30 | 908 | 906
2016-11-05 23:00 | 912 | 909
2016-11-05 23:30 | 832 | 825
2016-11-06 | 771 | 766
2016-11-06 00:30 | 747 | 743
2016-11-06 01:00 | 727 | 721
2016-11-06 01:30 | 708 | 699
2016-11-06 02:00 | 662 | 650
2016-11-06 02:30 | 648 | 633
2016-11-06 03:00 | 629 | 613
2016-11-06 03:30 | 601 | 582
2016-11-06 04:00 | 620 | 602
2016-11-06 04:30 | 595 | 575
2016-11-06 05:00 | 610 | 586
2016-11-06 05:30 | 658 | 634
2016-11-06 06:00 | 637 | 613
2016-11-06 06:30 | 669 | 650
2016-11-06 07:00 | 676 | 662
2016-11-06 07:30 | 701 | 693
2016-11-06 08:00 | 708 | 704
2016-11-06 08:30 | 727 | 725
2016-11-06 09:00 | 741 | 741
2016-11-06 09:30 | 751 | 751
2016-11-06 10:00 | 765 | 764
2016-11-06 10:30 | 771 | 771
2016-11-06 11:00 | 774 | 774
2016-11-06 11:30 | 779 | 779
2016-11-06 12:00 | 772 | 771
2016-11-06 12:30 | 741 | 738
2016-11-06 13:00 | 722 | 719
2016-11-06 13:30 | 748 | 746
2016-11-06 14:00 | 799 | 795
2016-11-06 14:30 | 875 | 867
2016-11-06 15:00 | 900 | 894
2016-11-06 15:30 | 940 | 931
2016-11-06 16:00 | 978 | 965
2016-11-06 16:30 | 1016 | 993
2016-11-06 17:00 | 1031 | 1009
2016-11-06 17:30 | 1038 | 1015
2016-11-06 18:00 | 1046 | 1018
2016-11-06 18:30 | 1055 | 1030
2016-11-06 19:00 | 1090 | 1074
2016-11-06 19:30 | 1075 | 1062
2016-11-06 20:00 | 1050 | 1042
2016-11-06 20:30 | 1034 | 1022
2016-11-06 21:00 | 987 | 970
2016-11-06 21:30 | 940 | 930
2016-11-06 22:00 | 901 | 894
2016-11-06 22:30 | 860 | 858
2016-11-06 23:00 | 853 | 852
2016-11-06 23:30 | 754 | 752
2016-11-07 | 761 | 757
2016-11-07 00:30 | 672 | 664
2016-11-07 01:00 | 646 | 635
2016-11-07 01:30 | 616 | 604
2016-11-07 02:00 | 605 | 590
2016-11-07 02:30 | 587 | 570
2016-11-07 03:00 | 572 | 554
2016-11-07 03:30 | 564 | 546
2016-11-07 04:00 | 617 | 601
2016-11-07 04:30 | 604 | 590
2016-11-07 05:00 | 681 | 670
2016-11-07 05:30 | 724 | 716
2016-11-07 06:00 | 771 | 765
2016-11-07 06:30 | 847 | 842
2016-11-07 07:00 | 927 | 923
2016-11-07 07:30 | 980 | 974
2016-11-07 08:00 | 1018 | 1009
2016-11-07 08:30 | 989 | 977
2016-11-07 09:00 | 957 | 942
2016-11-07 09:30 | 1008 | 995
2016-11-07 10:00 | 1031 | 1021
2016-11-07 10:30 | 1019 | 1011
2016-11-07 11:00 | 1015 | 1007
2016-11-07 11:30 | 1011 | 1004
2016-11-07 12:00 | 1017 | 1011
2016-11-07 12:30 | 1019 | 1012
2016-11-07 13:00 | 1028 | 1022
2016-11-07 13:30 | 1044 | 1038
2016-11-07 14:00 | 1073 | 1068
2016-11-07 14:30 | 1105 | 1102
2016-11-07 15:00 | 1124 | 1121
2016-11-07 15:30 | 1143 | 1140
2016-11-07 16:00 | 1170 | 1167
2016-11-07 16:30 | 1215 | 1209
2016-11-07 17:00 | 1241 | 1235
2016-11-07 17:30 | 1241 | 1231
2016-11-07 18:00 | 1230 | 1215
2016-11-07 18:30 | 1218 | 1203
2016-11-07 19:00 | 1248 | 1238
2016-11-07 19:30 | 1224 | 1211
2016-11-07 20:00 | 1183 | 1176
2016-11-07 20:30 | 1146 | 1141
2016-11-07 21:00 | 1084 | 1083
2016-11-07 21:30 | 1031 | 1031
2016-11-07 22:00 | 989 | 989
2016-11-07 22:30 | 958 | 958
2016-11-07 23:00 | 949 | 948
2016-11-07 23:30 | 885 | 885
2016-11-08 | 811 | 807
2016-11-08 00:30 | 778 | 774
2016-11-08 01:00 | 752 | 748
2016-11-08 01:30 | 739 | 734
2016-11-08 02:00 | 724 | 718
2016-11-08 02:30 | 717 | 711
2016-11-08 03:00 | 709 | 702
2016-11-08 03:30 | 710 | 703
2016-11-08 04:00 | 715 | 709
2016-11-08 04:30 | 727 | 722
2016-11-08 05:00 | 733 | 729
2016-11-08 05:30 | 767 | 764
2016-11-08 06:00 | 811 | 810
2016-11-08 06:30 | 908 | 905
2016-11-08 07:00 | 987 | 981
2016-11-08 07:30 | 1058 | 1055
2016-11-08 08:00 | 1084 | 1082
2016-11-08 08:30 | 1103 | 1099
2016-11-08 09:00 | 1113 | 1109
2016-11-08 09:30 | 1139 | 1138
2016-11-08 10:00 | 1155 | 1154
2016-11-08 10:30 | 1176 | 1173
2016-11-08 11:00 | 1177 | 1175
2016-11-08 11:30 | 1197 | 1197
2016-11-08 12:00 | 1234 | 1234
2016-11-08 12:30 | 1252 | 1251
2016-11-08 13:00 | 1268 | 1268
2016-11-08 13:30 | 1273 | 1272
2016-11-08 14:00 | 1302 | 1301
2016-11-08 14:30 | 1336 | 1334
2016-11-08 15:00 | 1360 | 1358
2016-11-08 15:30 | 1351 | 1346
2016-11-08 16:00 | 1355 | 1346
2016-11-08 16:30 | 1369 | 1359
2016-11-08 17:00 | 1359 | 1348
2016-11-08 17:30 | 1317 | 1310
2016-11-08 18:00 | 1280 | 1276
2016-11-08 18:30 | 1264 | 1262
2016-11-08 19:00 | 1273 | 1271
2016-11-08 19:30 | 1238 | 1236
2016-11-08 20:00 | 1217 | 1217
2016-11-08 20:30 | 1192 | 1192
2016-11-08 21:00 | 1130 | 1130
2016-11-08 21:30 | 1072 | 1071
2016-11-08 22:00 | 1015 | 1010
2016-11-08 22:30 | 983 | 980
2016-11-08 23:00 | 967 | 966
2016-11-08 23:30 | 910 | 906
2016-11-09 | 842 | 837
2016-11-09 00:30 | 799 | 797
2016-11-09 01:00 | 766 | 763
2016-11-09 01:30 | 735 | 731
2016-11-09 02:00 | 723 | 717
2016-11-09 02:30 | 711 | 705
2016-11-09 03:00 | 707 | 700
2016-11-09 03:30 | 710 | 703
2016-11-09 04:00 | 711 | 705
2016-11-09 04:30 | 725 | 720
2016-11-09 05:00 | 736 | 732
2016-11-09 05:30 | 772 | 769
2016-11-09 06:00 | 829 | 827
2016-11-09 06:30 | 906 | 906
2016-11-09 07:00 | 1001 | 1001
2016-11-09 07:30 | 1062 | 1062
2016-11-09 08:00 | 1077 | 1077
2016-11-09 08:30 | 1092 | 1092
2016-11-09 09:00 | 1081 | 1081
2016-11-09 09:30 | 1076 | 1076
2016-11-09 10:00 | 1113 | 1112
2016-11-09 10:30 | 1176 | 1176
2016-11-09 11:00 | 1208 | 1206
2016-11-09 11:30 | 1185 | 1183
2016-11-09 12:00 | 1155 | 1153
2016-11-09 12:30 | 1168 | 1166
2016-11-09 13:00 | 1187 | 1186
2016-11-09 13:30 | 1204 | 1202
2016-11-09 14:00 | 1228 | 1224
2016-11-09 14:30 | 1243 | 1241
2016-11-09 15:00 | 1273 | 1272
2016-11-09 15:30 | 1317 | 1316
2016-11-09 16:00 | 1327 | 1325
2016-11-09 16:30 | 1319 | 1314
2016-11-09 17:00 | 1320 | 1313
2016-11-09 17:30 | 1304 | 1296
2016-11-09 18:00 | 1278 | 1265
2016-11-09 18:30 | 1252 | 1237
2016-11-09 19:00 | 1260 | 1244
2016-11-09 19:30 | 1230 | 1211
2016-11-09 20:00 | 1204 | 1190
2016-11-09 20:30 | 1182 | 1167
2016-11-09 21:00 | 1101 | 1092
2016-11-09 21:30 | 1047 | 1040
2016-11-09 22:00 | 990 | 989
2016-11-09 22:30 | 961 | 957
2016-11-09 23:00 | 947 | 942
2016-11-09 23:30 | 883 | 874
2016-11-10 | 830 | 820
2016-11-10 00:30 | 786 | 771
2016-11-10 01:00 | 766 | 748
2016-11-10 01:30 | 742 | 720
2016-11-10 02:00 | 716 | 699
2016-11-10 02:30 | 699 | 691
2016-11-10 03:00 | 694 | 686
2016-11-10 03:30 | 697 | 689
2016-11-10 04:00 | 700 | 693
2016-11-10 04:30 | 712 | 706
2016-11-10 05:00 | 735 | 730
2016-11-10 05:30 | 772 | 770
2016-11-10 06:00 | 833 | 832
2016-11-10 06:30 | 908 | 903
2016-11-10 07:00 | 961 | 960
2016-11-10 07:30 | 1029 | 1027
2016-11-10 08:00 | 1055 | 1053
2016-11-10 08:30 | 1081 | 1081
2016-11-10 09:00 | 1109 | 1107
2016-11-10 09:30 | 1143 | 1138
2016-11-10 10:00 | 1152 | 1149
2016-11-10 10:30 | 1164 | 1158
2016-11-10 11:00 | 1160 | 1153
2016-11-10 11:30 | 1164 | 1158
2016-11-10 12:00 | 1189 | 1186
2016-11-10 12:30 | 1221 | 1218
2016-11-10 13:00 | 1256 | 1251
2016-11-10 13:30 | 1267 | 1264
2016-11-10 14:00 | 1286 | 1283
2016-11-10 14:30 | 1323 | 1317
2016-11-10 15:00 | 1343 | 1337
2016-11-10 15:30 | 1371 | 1365
2016-11-10 16:00 | 1396 | 1386
2016-11-10 16:30 | 1419 | 1409
2016-11-10 17:00 | 1427 | 1414
2016-11-10 17:30 | 1419 | 1400
2016-11-10 18:00 | 1389 | 1372
2016-11-10 18:30 | 1368 | 1355
2016-11-10 19:00 | 1401 | 1394
2016-11-10 19:30 | 1377 | 1368
2016-11-10 20:00 | 1351 | 1342
2016-11-10 20:30 | 1295 | 1288
2016-11-10 21:00 | 1209 | 1203
2016-11-10 21:30 | 1129 | 1122
2016-11-10 22:00 | 1057 | 1050
2016-11-10 22:30 | 1012 | 1011
2016-11-10 23:00 | 993 | 992
2016-11-10 23:30 | 916 | 912
2016-11-11 | 848 | 845
2016-11-11 00:30 | 803 | 798
2016-11-11 01:00 | 771 | 763
2016-11-11 01:30 | 732 | 727
2016-11-11 02:00 | 709 | 705
2016-11-11 02:30 | 699 | 693
2016-11-11 03:00 | 692 | 687
2016-11-11 03:30 | 693 | 688
2016-11-11 04:00 | 688 | 683
2016-11-11 04:30 | 694 | 689
2016-11-11 05:00 | 705 | 700
2016-11-11 05:30 | 728 | 725
2016-11-11 06:00 | 759 | 757
2016-11-11 06:30 | 830 | 830
2016-11-11 07:00 | 914 | 914
2016-11-11 07:30 | 989 | 989
2016-11-11 08:00 | 1018 | 1018
2016-11-11 08:30 | 1060 | 1060
2016-11-11 09:00 | 1081 | 1081
2016-11-11 09:30 | 1113 | 1112
2016-11-11 10:00 | 1104 | 1103
2016-11-11 10:30 | 1103 | 1101
2016-11-11 11:00 | 1108 | 1105
2016-11-11 11:30 | 1138 | 1137
2016-11-11 12:00 | 1156 | 1156
2016-11-11 12:30 | 1179 | 1179
2016-11-11 13:00 | 1220 | 1219
2016-11-11 13:30 | 1231 | 1230
2016-11-11 14:00 | 1255 | 1254
2016-11-11 14:30 | 1265 | 1264
2016-11-11 15:00 | 1248 | 1245
2016-11-11 15:30 | 1277 | 1274
2016-11-11 16:00 | 1286 | 1282
2016-11-11 16:30 | 1302 | 1296
2016-11-11 17:00 | 1299 | 1292
2016-11-11 17:30 | 1270 | 1256
2016-11-11 18:00 | 1230 | 1207
2016-11-11 18:30 | 1195 | 1171
2016-11-11 19:00 | 1219 | 1206
2016-11-11 19:30 | 1198 | 1186
2016-11-11 20:00 | 1174 | 1165
2016-11-11 20:30 | 1131 | 1126
2016-11-11 21:00 | 1082 | 1072
2016-11-11 21:30 | 1054 | 1041
2016-11-11 22:00 | 988 | 982
2016-11-11 22:30 | 941 | 939
2016-11-11 23:00 | 951 | 949
2016-11-11 23:30 | 875 | 873
2016-11-12 | 836 | 833
2016-11-12 00:30 | 761 | 756
2016-11-12 01:00 | 721 | 719
2016-11-12 01:30 | 723 | 719
2016-11-12 02:00 | 709 | 704
2016-11-12 02:30 | 698 | 692
2016-11-12 03:00 | 642 | 634
2016-11-12 03:30 | 655 | 648
2016-11-12 04:00 | 627 | 619
2016-11-12 04:30 | 681 | 673
2016-11-12 05:00 | 694 | 685
2016-11-12 05:30 | 708 | 700
2016-11-12 06:00 | 736 | 730
2016-11-12 06:30 | 782 | 780
2016-11-12 07:00 | 816 | 814
2016-11-12 07:30 | 863 | 862
2016-11-12 08:00 | 906 | 906
2016-11-12 08:30 | 886 | 886
2016-11-12 09:00 | 911 | 911
2016-11-12 09:30 | 935 | 934
2016-11-12 10:00 | 937 | 936
2016-11-12 10:30 | 948 | 948
2016-11-12 11:00 | 991 | 991
2016-11-12 11:30 | 1008 | 1007
2016-11-12 12:00 | 1016 | 1015
2016-11-12 12:30 | 1060 | 1060
2016-11-12 13:00 | 1145 | 1144
2016-11-12 13:30 | 1206 | 1204
2016-11-12 14:00 | 1245 | 1243
2016-11-12 14:30 | 1268 | 1265
2016-11-12 15:00 | 1268 | 1263
2016-11-12 15:30 | 1229 | 1218
2016-11-12 16:00 | 1172 | 1156
2016-11-12 16:30 | 1135 | 1121
2016-11-12 17:00 | 1095 | 1077
2016-11-12 17:30 | 1066 | 1057
2016-11-12 18:00 | 1065 | 1058
2016-11-12 18:30 | 1067 | 1061
2016-11-12 19:00 | 1088 | 1084
2016-11-12 19:30 | 1078 | 1074
2016-11-12 20:00 | 1077 | 1072
2016-11-12 20:30 | 1061 | 1054
2016-11-12 21:00 | 970 | 957
2016-11-12 21:30 | 936 | 931
2016-11-12 22:00 | 912 | 908
2016-11-12 22:30 | 864 | 862
2016-11-12 23:00 | 898 | 896
2016-11-12 23:30 | 814 | 811
2016-11-13 | 742 | 741
2016-11-13 00:30 | 704 | 701
2016-11-13 01:00 | 749 | 744
2016-11-13 01:30 | 727 | 720
2016-11-13 02:00 | 704 | 695
2016-11-13 02:30 | 687 | 676
2016-11-13 03:00 | 678 | 667
2016-11-13 03:30 | 642 | 630
2016-11-13 04:00 | 608 | 595
2016-11-13 04:30 | 657 | 644
2016-11-13 05:00 | 680 | 668
2016-11-13 05:30 | 687 | 671
2016-11-13 06:00 | 683 | 667
2016-11-13 06:30 | 640 | 628
2016-11-13 07:00 | 727 | 721
2016-11-13 07:30 | 773 | 769
2016-11-13 08:00 | 829 | 828
2016-11-13 08:30 | 869 | 869
2016-11-13 09:00 | 896 | 895
2016-11-13 09:30 | 912 | 912
2016-11-13 10:00 | 933 | 933
2016-11-13 10:30 | 967 | 966
2016-11-13 11:00 | 968 | 968
2016-11-13 11:30 | 998 | 997
2016-11-13 12:00 | 995 | 993
2016-11-13 12:30 | 972 | 970
2016-11-13 13:00 | 1005 | 1004
2016-11-13 13:30 | 1022 | 1022
2016-11-13 14:00 | 1084 | 1081
2016-11-13 14:30 | 1112 | 1110
2016-11-13 15:00 | 1161 | 1160
2016-11-13 15:30 | 1217 | 1214
2016-11-13 16:00 | 1244 | 1241
2016-11-13 16:30 | 1232 | 1224
2016-11-13 17:00 | 1258 | 1250
2016-11-13 17:30 | 1279 | 1270
2016-11-13 18:00 | 1253 | 1243
2016-11-13 18:30 | 1237 | 1226
2016-11-13 19:00 | 1256 | 1251
2016-11-13 19:30 | 1241 | 1234
2016-11-13 20:00 | 1219 | 1212
2016-11-13 20:30 | 1177 | 1172
2016-11-13 21:00 | 1114 | 1105
2016-11-13 21:30 | 1062 | 1058
2016-11-13 22:00 | 1008 | 1006
2016-11-13 22:30 | 904 | 903
2016-11-13 23:00 | 890 | 890
2016-11-13 23:30 | 846 | 845
2016-11-14 | 810 | 808
2016-11-14 00:30 | 782 | 779
2016-11-14 01:00 | 747 | 743
2016-11-14 01:30 | 722 | 716
2016-11-14 02:00 | 708 | 700
2016-11-14 02:30 | 694 | 685
2016-11-14 03:00 | 686 | 676
2016-11-14 03:30 | 683 | 672
2016-11-14 04:00 | 684 | 673
2016-11-14 04:30 | 692 | 682
2016-11-14 05:00 | 704 | 695
2016-11-14 05:30 | 739 | 731
2016-11-14 06:00 | 783 | 780
2016-11-14 06:30 | 852 | 852
2016-11-14 07:00 | 916 | 914
2016-11-14 07:30 | 935 | 934
2016-11-14 08:00 | 956 | 955
2016-11-14 08:30 | 948 | 948
2016-11-14 09:00 | 952 | 952
2016-11-14 09:30 | 956 | 956
2016-11-14 10:00 | 962 | 962
2016-11-14 10:30 | 962 | 962
2016-11-14 11:00 | 959 | 959
2016-11-14 11:30 | 957 | 957
2016-11-14 12:00 | 968 | 968
2016-11-14 12:30 | 980 | 979
2016-11-14 13:00 | 990 | 990
2016-11-14 13:30 | 1006 | 1006
2016-11-14 14:00 | 1015 | 1014
2016-11-14 14:30 | 1049 | 1049
2016-11-14 15:00 | 1066 | 1066
2016-11-14 15:30 | 1085 | 1085
2016-11-14 16:00 | 1133 | 1132
2016-11-14 16:30 | 1170 | 1168
2016-11-14 17:00 | 1184 | 1182
2016-11-14 17:30 | 1177 | 1173
2016-11-14 18:00 | 1145 | 1140
2016-11-14 18:30 | 1122 | 1115
2016-11-14 19:00 | 1152 | 1151
2016-11-14 19:30 | 1132 | 1130
2016-11-14 20:00 | 1129 | 1127
2016-11-14 20:30 | 1100 | 1098
2016-11-14 21:00 | 1041 | 1041
2016-11-14 21:30 | 996 | 996
2016-11-14 22:00 | 956 | 955
2016-11-14 22:30 | 929 | 928
2016-11-14 23:00 | 927 | 927
2016-11-14 23:30 | 866 | 863
2016-11-15 | 802 | 798
2016-11-15 00:30 | 752 | 747
2016-11-15 01:00 | 731 | 725
2016-11-15 01:30 | 707 | 697
2016-11-15 02:00 | 689 | 677
2016-11-15 02:30 | 676 | 662
2016-11-15 03:00 | 667 | 650
2016-11-15 03:30 | 656 | 639
2016-11-15 04:00 | 666 | 650
2016-11-15 04:30 | 685 | 672
2016-11-15 05:00 | 697 | 683
2016-11-15 05:30 | 734 | 723
2016-11-15 06:00 | 753 | 747
2016-11-15 06:30 | 816 | 815
2016-11-15 07:00 | 877 | 876
2016-11-15 07:30 | 924 | 923
2016-11-15 08:00 | 942 | 941
2016-11-15 08:30 | 954 | 953
2016-11-15 09:00 | 963 | 963
2016-11-15 09:30 | 973 | 973
2016-11-15 10:00 | 969 | 968
2016-11-15 10:30 | 965 | 965
2016-11-15 11:00 | 952 | 952
2016-11-15 11:30 | 948 | 948
2016-11-15 12:00 | 952 | 952
2016-11-15 12:30 | 949 | 949
2016-11-15 13:00 | 939 | 939
2016-11-15 13:30 | 955 | 955
2016-11-15 14:00 | 987 | 987
2016-11-15 14:30 | 997 | 997
2016-11-15 15:00 | 991 | 991
2016-11-15 15:30 | 993 | 993
2016-11-15 16:00 | 1008 | 1007
2016-11-15 16:30 | 1033 | 1033
2016-11-15 17:00 | 1095 | 1095
2016-11-15 17:30 | 1095 | 1094
2016-11-15 18:00 | 1089 | 1086
2016-11-15 18:30 | 1074 | 1070
2016-11-15 19:00 | 1116 | 1115
2016-11-15 19:30 | 1107 | 1105
2016-11-15 20:00 | 1077 | 1075
2016-11-15 20:30 | 1047 | 1045
2016-11-15 21:00 | 999 | 998
2016-11-15 21:30 | 957 | 955
2016-11-15 22:00 | 921 | 919
2016-11-15 22:30 | 890 | 886
2016-11-15 23:00 | 894 | 890
2016-11-15 23:30 | 822 | 818
2016-11-16 | 781 | 776
2016-11-16 00:30 | 740 | 734
2016-11-16 01:00 | 715 | 707
2016-11-16 01:30 | 688 | 677
2016-11-16 02:00 | 668 | 654
2016-11-16 02:30 | 662 | 646
2016-11-16 03:00 | 660 | 644
2016-11-16 03:30 | 664 | 648
2016-11-16 04:00 | 667 | 652
2016-11-16 04:30 | 683 | 670
2016-11-16 05:00 | 693 | 680
2016-11-16 05:30 | 733 | 723
2016-11-16 06:00 | 767 | 762
2016-11-16 06:30 | 833 | 833
2016-11-16 07:00 | 889 | 888
2016-11-16 07:30 | 936 | 936
2016-11-16 08:00 | 954 | 948
2016-11-16 08:30 | 965 | 961
2016-11-16 09:00 | 970 | 969
2016-11-16 09:30 | 969 | 968
2016-11-16 10:00 | 978 | 976
2016-11-16 10:30 | 975 | 973
2016-11-16 11:00 | 974 | 972
2016-11-16 11:30 | 973 | 970
2016-11-16 12:00 | 993 | 992
2016-11-16 12:30 | 996 | 994
2016-11-16 13:00 | 992 | 991
2016-11-16 13:30 | 990 | 989
2016-11-16 14:00 | 1010 | 1010
2016-11-16 14:30 | 1025 | 1023
2016-11-16 15:00 | 1039 | 1035
2016-11-16 15:30 | 1065 | 1061
2016-11-16 16:00 | 1086 | 1082
2016-11-16 16:30 | 1111 | 1107
2016-11-16 17:00 | 1126 | 1121
2016-11-16 17:30 | 1127 | 1118
2016-11-16 18:00 | 1114 | 1101
2016-11-16 18:30 | 1103 | 1091
2016-11-16 19:00 | 1132 | 1126
2016-11-16 19:30 | 1123 | 1116
2016-11-16 20:00 | 1100 | 1093
2016-11-16 20:30 | 1061 | 1056
2016-11-16 21:00 | 1013 | 1011
2016-11-16 21:30 | 979 | 976
2016-11-16 22:00 | 946 | 943
2016-11-16 22:30 | 918 | 915
2016-11-16 23:00 | 913 | 911
2016-11-16 23:30 | 857 | 854
2016-11-17 | 805 | 799
2016-11-17 00:30 | 757 | 749
2016-11-17 01:00 | 725 | 718
2016-11-17 01:30 | 708 | 699
2016-11-17 02:00 | 695 | 685
2016-11-17 02:30 | 682 | 671
2016-11-17 03:00 | 678 | 667
2016-11-17 03:30 | 679 | 666
2016-11-17 04:00 | 674 | 662
2016-11-17 04:30 | 694 | 684
2016-11-17 05:00 | 711 | 702
2016-11-17 05:30 | 746 | 740
2016-11-17 06:00 | 790 | 787
2016-11-17 06:30 | 862 | 859
2016-11-17 07:00 | 886 | 881
2016-11-17 07:30 | 925 | 922
2016-11-17 08:00 | 945 | 945
2016-11-17 08:30 | 948 | 948
2016-11-17 09:00 | 935 | 935
2016-11-17 09:30 | 974 | 974
2016-11-17 10:00 | 1015 | 1014
2016-11-17 10:30 | 1022 | 1022
2016-11-17 11:00 | 1018 | 1018
2016-11-17 11:30 | 1021 | 1021
2016-11-17 12:00 | 1006 | 1005
2016-11-17 12:30 | 1004 | 1003
2016-11-17 13:00 | 1013 | 1013
2016-11-17 13:30 | 1026 | 1025
2016-11-17 14:00 | 989 | 989
2016-11-17 14:30 | 911 | 910
2016-11-17 15:00 | 912 | 910
2016-11-17 15:30 | 915 | 913
2016-11-17 16:00 | 929 | 927
2016-11-17 16:30 | 949 | 947
2016-11-17 17:00 | 963 | 960
2016-11-17 17:30 | 968 | 964
2016-11-17 18:00 | 970 | 965
2016-11-17 18:30 | 962 | 958
2016-11-17 19:00 | 988 | 987
2016-11-17 19:30 | 978 | 976
2016-11-17 20:00 | 970 | 967
2016-11-17 20:30 | 953 | 951
2016-11-17 21:00 | 910 | 907
2016-11-17 21:30 | 872 | 869
2016-11-17 22:00 | 833 | 831
2016-11-17 22:30 | 813 | 808
2016-11-17 23:00 | 813 | 809
2016-11-17 23:30 | 755 | 753
2016-11-18 | 709 | 706
2016-11-18 00:30 | 667 | 661
2016-11-18 01:00 | 639 | 630
2016-11-18 01:30 | 622 | 612
2016-11-18 02:00 | 607 | 595
2016-11-18 02:30 | 597 | 582
2016-11-18 03:00 | 597 | 582
2016-11-18 03:30 | 596 | 582
2016-11-18 04:00 | 593 | 579
2016-11-18 04:30 | 605 | 593
2016-11-18 05:00 | 619 | 607
2016-11-18 05:30 | 646 | 637
2016-11-18 06:00 | 686 | 678
2016-11-18 06:30 | 727 | 725
2016-11-18 07:00 | 775 | 775
2016-11-18 07:30 | 831 | 830
2016-11-18 08:00 | 854 | 853
2016-11-18 08:30 | 857 | 857
2016-11-18 09:00 | 840 | 839
2016-11-18 09:30 | 836 | 836
2016-11-18 10:00 | 815 | 815
2016-11-18 10:30 | 812 | 812
2016-11-18 11:00 | 804 | 803
2016-11-18 11:30 | 804 | 804
2016-11-18 12:00 | 801 | 800
2016-11-18 12:30 | 802 | 801
2016-11-18 13:00 | 808 | 808
2016-11-18 13:30 | 817 | 817
2016-11-18 14:00 | 835 | 835
2016-11-18 14:30 | 849 | 849
2016-11-18 15:00 | 863 | 863
2016-11-18 15:30 | 887 | 887
2016-11-18 16:00 | 919 | 918
2016-11-18 16:30 | 951 | 951
2016-11-18 17:00 | 976 | 976
2016-11-18 17:30 | 984 | 982
2016-11-18 18:00 | 948 | 945
2016-11-18 18:30 | 924 | 921
2016-11-18 19:00 | 964 | 963
2016-11-18 19:30 | 960 | 959
2016-11-18 20:00 | 941 | 940
2016-11-18 20:30 | 915 | 915
2016-11-18 21:00 | 876 | 875
2016-11-18 21:30 | 838 | 838
2016-11-18 22:00 | 813 | 812
2016-11-18 22:30 | 797 | 794
2016-11-18 23:00 | 800 | 797
2016-11-18 23:30 | 747 | 742
2016-11-19 | 699 | 692
2016-11-19 00:30 | 661 | 648
2016-11-19 01:00 | 640 | 624
2016-11-19 01:30 | 623 | 607
2016-11-19 02:00 | 608 | 592
2016-11-19 02:30 | 598 | 581
2016-11-19 03:00 | 589 | 571
2016-11-19 03:30 | 589 | 570
2016-11-19 04:00 | 588 | 569
2016-11-19 04:30 | 593 | 574
2016-11-19 05:00 | 594 | 572
2016-11-19 05:30 | 601 | 578
2016-11-19 06:00 | 614 | 596
2016-11-19 06:30 | 636 | 622
2016-11-19 07:00 | 651 | 642
2016-11-19 07:30 | 683 | 680
2016-11-19 08:00 | 703 | 702
2016-11-19 08:30 | 713 | 713
2016-11-19 09:00 | 751 | 751
2016-11-19 09:30 | 776 | 776
2016-11-19 10:00 | 795 | 795
2016-11-19 10:30 | 789 | 789
2016-11-19 11:00 | 778 | 778
2016-11-19 11:30 | 758 | 758
2016-11-19 12:00 | 736 | 736
2016-11-19 12:30 | 715 | 715
2016-11-19 13:00 | 717 | 717
2016-11-19 13:30 | 736 | 736
2016-11-19 14:00 | 752 | 752
2016-11-19 14:30 | 752 | 752
2016-11-19 15:00 | 751 | 751
2016-11-19 15:30 | 758 | 758
2016-11-19 16:00 | 777 | 777
2016-11-19 16:30 | 812 | 812
2016-11-19 17:00 | 841 | 841
2016-11-19 17:30 | 839 | 839
2016-11-19 18:00 | 828 | 828
2016-11-19 18:30 | 827 | 827
2016-11-19 19:00 | 866 | 866
2016-11-19 19:30 | 863 | 861
2016-11-19 20:00 | 849 | 846
2016-11-19 20:30 | 834 | 831
2016-11-19 21:00 | 799 | 799
2016-11-19 21:30 | 789 | 789
2016-11-19 22:00 | 771 | 770
2016-11-19 22:30 | 762 | 760
2016-11-19 23:00 | 773 | 771
2016-11-19 23:30 | 733 | 728
2016-11-20 | 693 | 685
2016-11-20 00:30 | 659 | 648
2016-11-20 01:00 | 638 | 623
2016-11-20 01:30 | 623 | 606
2016-11-20 02:00 | 595 | 579
2016-11-20 02:30 | 584 | 566
2016-11-20 03:00 | 578 | 558
2016-11-20 03:30 | 576 | 556
2016-11-20 04:00 | 575 | 553
2016-11-20 04:30 | 579 | 557
2016-11-20 05:00 | 580 | 555
2016-11-20 05:30 | 585 | 556
2016-11-20 06:00 | 589 | 563
2016-11-20 06:30 | 592 | 570
2016-11-20 07:00 | 591 | 573
2016-11-20 07:30 | 611 | 601
2016-11-20 08:00 | 638 | 633
2016-11-20 08:30 | 659 | 657
2016-11-20 09:00 | 664 | 663
2016-11-20 09:30 | 673 | 673
2016-11-20 10:00 | 681 | 680
2016-11-20 10:30 | 684 | 684
2016-11-20 11:00 | 684 | 684
2016-11-20 11:30 | 679 | 679
2016-11-20 12:00 | 686 | 685
2016-11-20 12:30 | 688 | 687
2016-11-20 13:00 | 694 | 693
2016-11-20 13:30 | 708 | 708
2016-11-20 14:00 | 721 | 721
2016-11-20 14:30 | 738 | 738
2016-11-20 15:00 | 767 | 765
2016-11-20 15:30 | 797 | 795
2016-11-20 16:00 | 826 | 822
2016-11-20 16:30 | 845 | 841
2016-11-20 17:00 | 877 | 872
2016-11-20 17:30 | 894 | 881
2016-11-20 18:00 | 896 | 880
2016-11-20 18:30 | 905 | 889
2016-11-20 19:00 | 929 | 919
2016-11-20 19:30 | 927 | 917
2016-11-20 20:00 | 922 | 909
2016-11-20 20:30 | 896 | 887
2016-11-20 21:00 | 847 | 841
2016-11-20 21:30 | 809 | 806
2016-11-20 22:00 | 785 | 780
2016-11-20 22:30 | 764 | 762
2016-11-20 23:00 | 766 | 765
2016-11-20 23:30 | 716 | 712
2016-11-21 | 673 | 667
2016-11-21 00:30 | 648 | 639
2016-11-21 01:00 | 631 | 620
2016-11-21 01:30 | 615 | 602
2016-11-21 02:00 | 601 | 587
2016-11-21 02:30 | 597 | 581
2016-11-21 03:00 | 593 | 577
2016-11-21 03:30 | 593 | 577
2016-11-21 04:00 | 595 | 579
2016-11-21 04:30 | 603 | 587
2016-11-21 05:00 | 612 | 595
2016-11-21 05:30 | 618 | 602
2016-11-21 06:00 | 668 | 660
2016-11-21 06:30 | 720 | 716
2016-11-21 07:00 | 739 | 724
2016-11-21 07:30 | 785 | 780
2016-11-21 08:00 | 808 | 806
2016-11-21 08:30 | 812 | 809
2016-11-21 09:00 | 809 | 806
2016-11-21 09:30 | 818 | 817
2016-11-21 10:00 | 810 | 809
2016-11-21 10:30 | 805 | 804
2016-11-21 11:00 | 809 | 807
2016-11-21 11:30 | 820 | 815
2016-11-21 12:00 | 822 | 818
2016-11-21 12:30 | 825 | 822
2016-11-21 13:00 | 823 | 821
2016-11-21 13:30 | 841 | 838
2016-11-21 14:00 | 861 | 859
2016-11-21 14:30 | 880 | 878
2016-11-21 15:00 | 894 | 892
2016-11-21 15:30 | 913 | 912
2016-11-21 16:00 | 949 | 947
2016-11-21 16:30 | 989 | 988
2016-11-21 17:00 | 1024 | 1023
2016-11-21 17:30 | 1018 | 1014
2016-11-21 18:00 | 992 | 984
2016-11-21 18:30 | 985 | 975
2016-11-21 19:00 | 1005 | 1001
2016-11-21 19:30 | 994 | 990
2016-11-21 20:00 | 978 | 975
2016-11-21 20:30 | 954 | 952
2016-11-21 21:00 | 903 | 901
2016-11-21 21:30 | 860 | 856
2016-11-21 22:00 | 823 | 820
2016-11-21 22:30 | 797 | 794
2016-11-21 23:00 | 792 | 790
2016-11-21 23:30 | 741 | 737
2016-11-22 | 694 | 688
2016-11-22 00:30 | 661 | 651
2016-11-22 01:00 | 637 | 627
2016-11-22 01:30 | 621 | 608
2016-11-22 02:00 | 613 | 599
2016-11-22 02:30 | 603 | 586
2016-11-22 03:00 | 599 | 582
2016-11-22 03:30 | 602 | 583
2016-11-22 04:00 | 603 | 584
2016-11-22 04:30 | 614 | 598
2016-11-22 05:00 | 620 | 604
2016-11-22 05:30 | 641 | 627
2016-11-22 06:00 | 674 | 667
2016-11-22 06:30 | 718 | 717
2016-11-22 07:00 | 762 | 761
2016-11-22 07:30 | 828 | 827
2016-11-22 08:00 | 843 | 841
2016-11-22 08:30 | 857 | 857
2016-11-22 09:00 | 852 | 851
2016-11-22 09:30 | 851 | 851
2016-11-22 10:00 | 839 | 839
2016-11-22 10:30 | 833 | 833
2016-11-22 11:00 | 819 | 819
2016-11-22 11:30 | 804 | 804
2016-11-22 12:00 | 797 | 796
2016-11-22 12:30 | 797 | 796
2016-11-22 13:00 | 796 | 795
2016-11-22 13:30 | 811 | 810
2016-11-22 14:00 | 830 | 829
2016-11-22 14:30 | 846 | 846
2016-11-22 15:00 | 863 | 859
2016-11-22 15:30 | 922 | 917
2016-11-22 16:00 | 948 | 944
2016-11-22 16:30 | 969 | 964
2016-11-22 17:00 | 992 | 985
2016-11-22 17:30 | 988 | 980
2016-11-22 18:00 | 963 | 956
2016-11-22 18:30 | 948 | 942
2016-11-22 19:00 | 944 | 942
2016-11-22 19:30 | 934 | 932
2016-11-22 20:00 | 917 | 913
2016-11-22 20:30 | 892 | 888
2016-11-22 21:00 | 837 | 836
2016-11-22 21:30 | 814 | 813
2016-11-22 22:00 | 775 | 773
2016-11-22 22:30 | 752 | 750
2016-11-22 23:00 | 740 | 737
2016-11-22 23:30 | 692 | 685
2016-11-23 | 668 | 656
2016-11-23 00:30 | 629 | 613
2016-11-23 01:00 | 616 | 597
2016-11-23 01:30 | 595 | 578
2016-11-23 02:00 | 578 | 563
2016-11-23 02:30 | 572 | 556
2016-11-23 03:00 | 568 | 551
2016-11-23 03:30 | 565 | 548
2016-11-23 04:00 | 570 | 554
2016-11-23 04:30 | 577 | 562
2016-11-23 05:00 | 586 | 572
2016-11-23 05:30 | 616 | 604
2016-11-23 06:00 | 642 | 636
2016-11-23 06:30 | 692 | 691
2016-11-23 07:00 | 744 | 744
2016-11-23 07:30 | 798 | 797
2016-11-23 08:00 | 818 | 818
2016-11-23 08:30 | 827 | 827
2016-11-23 09:00 | 837 | 837
2016-11-23 09:30 | 831 | 831
2016-11-23 10:00 | 870 | 870
2016-11-23 10:30 | 861 | 861
2016-11-23 11:00 | 873 | 873
2016-11-23 11:30 | 900 | 900
2016-11-23 12:00 | 906 | 906
2016-11-23 12:30 | 908 | 908
2016-11-23 13:00 | 929 | 929
2016-11-23 13:30 | 952 | 952
2016-11-23 14:00 | 979 | 978
2016-11-23 14:30 | 991 | 989
2016-11-23 15:00 | 1015 | 1013
2016-11-23 15:30 | 996 | 994
2016-11-23 16:00 | 1035 | 1034
2016-11-23 16:30 | 1088 | 1083
2016-11-23 17:00 | 1103 | 1094
2016-11-23 17:30 | 1097 | 1086
2016-11-23 18:00 | 1077 | 1063
2016-11-23 18:30 | 1051 | 1035
2016-11-23 19:00 | 1074 | 1066
2016-11-23 19:30 | 1065 | 1056
2016-11-23 20:00 | 1050 | 1047
2016-11-23 20:30 | 1026 | 1021
2016-11-23 21:00 | 961 | 959
2016-11-23 21:30 | 911 | 910
2016-11-23 22:00 | 857 | 855
2016-11-23 22:30 | 826 | 826
2016-11-23 23:00 | 828 | 827
2016-11-23 23:30 | 763 | 760
2016-11-24 | 719 | 716
2016-11-24 00:30 | 678 | 672
2016-11-24 01:00 | 661 | 652
2016-11-24 01:30 | 641 | 632
2016-11-24 02:00 | 627 | 617
2016-11-24 02:30 | 620 | 608
2016-11-24 03:00 | 615 | 602
2016-11-24 03:30 | 613 | 598
2016-11-24 04:00 | 616 | 602
2016-11-24 04:30 | 625 | 613
2016-11-24 05:00 | 634 | 621
2016-11-24 05:30 | 659 | 649
2016-11-24 06:00 | 691 | 688
2016-11-24 06:30 | 753 | 752
2016-11-24 07:00 | 819 | 818
2016-11-24 07:30 | 880 | 878
2016-11-24 08:00 | 907 | 903
2016-11-24 08:30 | 922 | 920
2016-11-24 09:00 | 936 | 935
2016-11-24 09:30 | 945 | 944
2016-11-24 10:00 | 954 | 952
2016-11-24 10:30 | 955 | 955
2016-11-24 11:00 | 941 | 939
2016-11-24 11:30 | 980 | 971
2016-11-24 12:00 | 1001 | 993
2016-11-24 12:30 | 1006 | 998
2016-11-24 13:00 | 1016 | 1008
2016-11-24 13:30 | 1026 | 1015
2016-11-24 14:00 | 1041 | 1031
2016-11-24 14:30 | 1052 | 1041
2016-11-24 15:00 | 1061 | 1050
2016-11-24 15:30 | 1076 | 1063
2016-11-24 16:00 | 1088 | 1074
2016-11-24 16:30 | 1100 | 1084
2016-11-24 17:00 | 1101 | 1086
2016-11-24 17:30 | 1058 | 1049
2016-11-24 18:00 | 1036 | 1025
2016-11-24 18:30 | 1011 | 1003
2016-11-24 19:00 | 1020 | 1018
2016-11-24 19:30 | 994 | 989
2016-11-24 20:00 | 987 | 986
2016-11-24 20:30 | 976 | 974
2016-11-24 21:00 | 922 | 921
2016-11-24 21:30 | 875 | 873
2016-11-24 22:00 | 831 | 829
2016-11-24 22:30 | 817 | 814
2016-11-24 23:00 | 807 | 803
2016-11-24 23:30 | 741 | 738
2016-11-25 | 696 | 692
2016-11-25 00:30 | 659 | 654
2016-11-25 01:00 | 643 | 635
2016-11-25 01:30 | 627 | 618
2016-11-25 02:00 | 614 | 602
2016-11-25 02:30 | 607 | 594
2016-11-25 03:00 | 601 | 587
2016-11-25 03:30 | 603 | 589
2016-11-25 04:00 | 603 | 588
2016-11-25 04:30 | 613 | 601
2016-11-25 05:00 | 614 | 601
2016-11-25 05:30 | 639 | 630
2016-11-25 06:00 | 671 | 663
2016-11-25 06:30 | 723 | 717
2016-11-25 07:00 | 776 | 774
2016-11-25 07:30 | 823 | 821
2016-11-25 08:00 | 844 | 840
2016-11-25 08:30 | 863 | 861
2016-11-25 09:00 | 882 | 880
2016-11-25 09:30 | 880 | 878
2016-11-25 10:00 | 880 | 878
2016-11-25 10:30 | 869 | 868
2016-11-25 11:00 | 860 | 858
2016-11-25 11:30 | 861 | 861
2016-11-25 12:00 | 867 | 867
2016-11-25 12:30 | 881 | 881
2016-11-25 13:00 | 904 | 904
2016-11-25 13:30 | 923 | 923
2016-11-25 14:00 | 912 | 912
2016-11-25 14:30 | 920 | 920
2016-11-25 15:00 | 935 | 935
2016-11-25 15:30 | 938 | 938
2016-11-25 16:00 | 959 | 959
2016-11-25 16:30 | 982 | 982
2016-11-25 17:00 | 1009 | 1008
2016-11-25 17:30 | 994 | 991
2016-11-25 18:00 | 977 | 970
2016-11-25 18:30 | 953 | 945
2016-11-25 19:00 | 975 | 973
2016-11-25 19:30 | 975 | 972
2016-11-25 20:00 | 962 | 959
2016-11-25 20:30 | 949 | 945
2016-11-25 21:00 | 902 | 901
2016-11-25 21:30 | 879 | 876
2016-11-25 22:00 | 852 | 850
2016-11-25 22:30 | 830 | 830
2016-11-25 23:00 | 829 | 829
2016-11-25 23:30 | 771 | 770
2016-11-26 | 723 | 721
2016-11-26 00:30 | 692 | 688
2016-11-26 01:00 | 667 | 662
2016-11-26 01:30 | 650 | 644
2016-11-26 02:00 | 634 | 627
2016-11-26 02:30 | 625 | 616
2016-11-26 03:00 | 622 | 611
2016-11-26 03:30 | 618 | 606
2016-11-26 04:00 | 619 | 607
2016-11-26 04:30 | 623 | 611
2016-11-26 05:00 | 622 | 610
2016-11-26 05:30 | 631 | 618
2016-11-26 06:00 | 642 | 632
2016-11-26 06:30 | 667 | 661
2016-11-26 07:00 | 692 | 690
2016-11-26 07:30 | 727 | 727
2016-11-26 08:00 | 761 | 761
2016-11-26 08:30 | 805 | 804
2016-11-26 09:00 | 811 | 811
2016-11-26 09:30 | 796 | 796
2016-11-26 10:00 | 797 | 797
2016-11-26 10:30 | 810 | 810
2016-11-26 11:00 | 783 | 783
2016-11-26 11:30 | 771 | 771
2016-11-26 12:00 | 785 | 785
2016-11-26 12:30 | 762 | 762
2016-11-26 13:00 | 788 | 788
2016-11-26 13:30 | 802 | 802
2016-11-26 14:00 | 808 | 808
2016-11-26 14:30 | 814 | 814
2016-11-26 15:00 | 838 | 838
2016-11-26 15:30 | 846 | 846
2016-11-26 16:00 | 846 | 846
2016-11-26 16:30 | 846 | 846
2016-11-26 17:00 | 861 | 861
2016-11-26 17:30 | 860 | 854
2016-11-26 18:00 | 849 | 841
2016-11-26 18:30 | 853 | 844
2016-11-26 19:00 | 878 | 873
2016-11-26 19:30 | 874 | 869
2016-11-26 20:00 | 872 | 866
2016-11-26 20:30 | 853 | 851
2016-11-26 21:00 | 812 | 810
2016-11-26 21:30 | 797 | 794
2016-11-26 22:00 | 784 | 780
2016-11-26 22:30 | 764 | 764
2016-11-26 23:00 | 772 | 772
2016-11-26 23:30 | 730 | 729
2016-11-27 | 690 | 688
2016-11-27 00:30 | 653 | 650
2016-11-27 01:00 | 640 | 635
2016-11-27 01:30 | 616 | 609
2016-11-27 02:00 | 600 | 591
2016-11-27 02:30 | 596 | 585
2016-11-27 03:00 | 589 | 578
2016-11-27 03:30 | 587 | 574
2016-11-27 04:00 | 584 | 571
2016-11-27 04:30 | 581 | 569
2016-11-27 05:00 | 582 | 567
2016-11-27 05:30 | 578 | 561
2016-11-27 06:00 | 586 | 569
2016-11-27 06:30 | 599 | 587
2016-11-27 07:00 | 607 | 599
2016-11-27 07:30 | 638 | 634
2016-11-27 08:00 | 659 | 657
2016-11-27 08:30 | 685 | 685
2016-11-27 09:00 | 707 | 707
2016-11-27 09:30 | 722 | 722
2016-11-27 10:00 | 722 | 722
2016-11-27 10:30 | 718 | 717
2016-11-27 11:00 | 722 | 721
2016-11-27 11:30 | 725 | 725
2016-11-27 12:00 | 733 | 732
2016-11-27 12:30 | 743 | 742
2016-11-27 13:00 | 782 | 781
2016-11-27 13:30 | 793 | 792
2016-11-27 14:00 | 813 | 812
2016-11-27 14:30 | 814 | 813
2016-11-27 15:00 | 819 | 819
2016-11-27 15:30 | 826 | 826
2016-11-27 16:00 | 842 | 842
2016-11-27 16:30 | 861 | 860
2016-11-27 17:00 | 869 | 868
2016-11-27 17:30 | 875 | 875
2016-11-27 18:00 | 875 | 874
2016-11-27 18:30 | 882 | 881
2016-11-27 19:00 | 916 | 916
2016-11-27 19:30 | 908 | 908
2016-11-27 20:00 | 905 | 905
2016-11-27 20:30 | 892 | 891
2016-11-27 21:00 | 854 | 853
2016-11-27 21:30 | 827 | 826
2016-11-27 22:00 | 799 | 798
2016-11-27 22:30 | 783 | 783
2016-11-27 23:00 | 778 | 778
2016-11-27 23:30 | 728 | 727
2016-11-28 | 682 | 680
2016-11-28 00:30 | 649 | 645
2016-11-28 01:00 | 634 | 628
2016-11-28 01:30 | 614 | 607
2016-11-28 02:00 | 600 | 591
2016-11-28 02:30 | 594 | 584
2016-11-28 03:00 | 587 | 576
2016-11-28 03:30 | 588 | 576
2016-11-28 04:00 | 588 | 577
2016-11-28 04:30 | 595 | 585
2016-11-28 05:00 | 604 | 594
2016-11-28 05:30 | 638 | 631
2016-11-28 06:00 | 662 | 659
2016-11-28 06:30 | 731 | 731
2016-11-28 07:00 | 784 | 784
2016-11-28 07:30 | 843 | 843
2016-11-28 08:00 | 881 | 880
2016-11-28 08:30 | 909 | 909
2016-11-28 09:00 | 923 | 923
2016-11-28 09:30 | 924 | 924
2016-11-28 10:00 | 930 | 930
2016-11-28 10:30 | 930 | 930
2016-11-28 11:00 | 928 | 928
2016-11-28 11:30 | 931 | 931
2016-11-28 12:00 | 935 | 935
2016-11-28 12:30 | 938 | 938
2016-11-28 13:00 | 937 | 937
2016-11-28 13:30 | 950 | 950
2016-11-28 14:00 | 957 | 957
2016-11-28 14:30 | 974 | 974
2016-11-28 15:00 | 990 | 990
2016-11-28 15:30 | 1007 | 1006
2016-11-28 16:00 | 1042 | 1041
2016-11-28 16:30 | 1054 | 1053
2016-11-28 17:00 | 1068 | 1067
2016-11-28 17:30 | 1069 | 1065
2016-11-28 18:00 | 1052 | 1044
2016-11-28 18:30 | 1016 | 1012
2016-11-28 19:00 | 1035 | 1033
2016-11-28 19:30 | 1018 | 1016
2016-11-28 20:00 | 994 | 994
2016-11-28 20:30 | 968 | 967
2016-11-28 21:00 | 919 | 916
2016-11-28 21:30 | 878 | 877
2016-11-28 22:00 | 843 | 842
2016-11-28 22:30 | 819 | 817
2016-11-28 23:00 | 815 | 814
2016-11-28 23:30 | 754 | 750
2016-11-29 | 710 | 702
2016-11-29 00:30 | 681 | 670
2016-11-29 01:00 | 662 | 650
2016-11-29 01:30 | 643 | 628
2016-11-29 02:00 | 627 | 615
2016-11-29 02:30 | 616 | 606
2016-11-29 03:00 | 611 | 600
2016-11-29 03:30 | 611 | 601
2016-11-29 04:00 | 609 | 599
2016-11-29 04:30 | 618 | 609
2016-11-29 05:00 | 621 | 612
2016-11-29 05:30 | 646 | 640
2016-11-29 06:00 | 680 | 678
2016-11-29 06:30 | 752 | 752
2016-11-29 07:00 | 820 | 817
2016-11-29 07:30 | 866 | 865
2016-11-29 08:00 | 887 | 886
2016-11-29 08:30 | 892 | 891
2016-11-29 09:00 | 900 | 898
2016-11-29 09:30 | 906 | 905
2016-11-29 10:00 | 904 | 904
2016-11-29 10:30 | 912 | 912
2016-11-29 11:00 | 914 | 914
2016-11-29 11:30 | 935 | 925
2016-11-29 12:00 | 947 | 938
2016-11-29 12:30 | 952 | 944
2016-11-29 13:00 | 970 | 963
2016-11-29 13:30 | 984 | 976
2016-11-29 14:00 | 992 | 985
2016-11-29 14:30 | 1000 | 992
2016-11-29 15:00 | 1016 | 1008
2016-11-29 15:30 | 1030 | 1023
2016-11-29 16:00 | 1065 | 1059
2016-11-29 16:30 | 1087 | 1080
2016-11-29 17:00 | 1091 | 1083
2016-11-29 17:30 | 1066 | 1056
2016-11-29 18:00 | 1018 | 1008
2016-11-29 18:30 | 991 | 989
2016-11-29 19:00 | 1018 | 1018
2016-11-29 19:30 | 1010 | 1009
2016-11-29 20:00 | 992 | 992
2016-11-29 20:30 | 969 | 968
2016-11-29 21:00 | 930 | 929
2016-11-29 21:30 | 888 | 884
2016-11-29 22:00 | 850 | 845
2016-11-29 22:30 | 813 | 813
2016-11-29 23:00 | 808 | 808
2016-11-29 23:30 | 756 | 756
2016-11-30 | 711 | 710
2016-11-30 00:30 | 671 | 667
2016-11-30 01:00 | 656 | 652
2016-11-30 01:30 | 635 | 628
2016-11-30 02:00 | 623 | 615
2016-11-30 02:30 | 616 | 607
2016-11-30 03:00 | 614 | 605
2016-11-30 03:30 | 613 | 605
2016-11-30 04:00 | 610 | 602
2016-11-30 04:30 | 622 | 615
2016-11-30 05:00 | 636 | 628
2016-11-30 05:30 | 662 | 655
2016-11-30 06:00 | 695 | 689
2016-11-30 06:30 | 754 | 752
2016-11-30 07:00 | 812 | 810
2016-11-30 07:30 | 860 | 859
2016-11-30 08:00 | 880 | 876
2016-11-30 08:30 | 896 | 894
2016-11-30 09:00 | 909 | 907
2016-11-30 09:30 | 913 | 911
2016-11-30 10:00 | 926 | 926
2016-11-30 10:30 | 939 | 936
2016-11-30 11:00 | 943 | 938
2016-11-30 11:30 | 945 | 940
2016-11-30 12:00 | 965 | 961
2016-11-30 12:30 | 974 | 970
2016-11-30 13:00 | 994 | 992
2016-11-30 13:30 | 1017 | 1016
2016-11-30 14:00 | 1074 | 1071
2016-11-30 14:30 | 1112 | 1110
2016-11-30 15:00 | 1122 | 1119
2016-11-30 15:30 | 1112 | 1106
2016-11-30 16:00 | 1099 | 1089
2016-11-30 16:30 | 1064 | 1055
2016-11-30 17:00 | 1051 | 1044
2016-11-30 17:30 | 1048 | 1045
2016-11-30 18:00 | 1016 | 1011
2016-11-30 18:30 | 982 | 981
2016-11-30 19:00 | 1007 | 1007
2016-11-30 19:30 | 1001 | 1000
2016-11-30 20:00 | 1000 | 999
2016-11-30 20:30 | 976 | 974
2016-11-30 21:00 | 930 | 926
2016-11-30 21:30 | 886 | 880
2016-11-30 22:00 | 849 | 845
2016-11-30 22:30 | 821 | 817
2016-11-30 23:00 | 810 | 809
2016-11-30 23:30 | 754 | 752
2016-12-01 | 703 | 701
2016-12-01 00:30 | 677 | 672
2016-12-01 01:00 | 663 | 656
2016-12-01 01:30 | 649 | 641
2016-12-01 02:00 | 639 | 630
2016-12-01 02:30 | 629 | 619
2016-12-01 03:00 | 620 | 609
2016-12-01 03:30 | 614 | 602
2016-12-01 04:00 | 626 | 616
2016-12-01 04:30 | 600 | 589
2016-12-01 05:00 | 619 | 608
2016-12-01 05:30 | 680 | 675
2016-12-01 06:00 | 698 | 694
2016-12-01 06:30 | 749 | 748
2016-12-01 07:00 | 804 | 802
2016-12-01 07:30 | 860 | 856
2016-12-01 08:00 | 884 | 882
2016-12-01 08:30 | 898 | 898
2016-12-01 09:00 | 910 | 910
2016-12-01 09:30 | 908 | 908
2016-12-01 10:00 | 911 | 911
2016-12-01 10:30 | 911 | 911
2016-12-01 11:00 | 906 | 906
2016-12-01 11:30 | 938 | 937
2016-12-01 12:00 | 950 | 950
2016-12-01 12:30 | 960 | 959
2016-12-01 13:00 | 988 | 987
2016-12-01 13:30 | 985 | 984
2016-12-01 14:00 | 1005 | 1004
2016-12-01 14:30 | 1031 | 1028
2016-12-01 15:00 | 1080 | 1078
2016-12-01 15:30 | 1126 | 1125
2016-12-01 16:00 | 1141 | 1138
2016-12-01 16:30 | 1142 | 1137
2016-12-01 17:00 | 1144 | 1136
2016-12-01 17:30 | 1099 | 1084
2016-12-01 18:00 | 1055 | 1044
2016-12-01 18:30 | 1041 | 1031
2016-12-01 19:00 | 1066 | 1060
2016-12-01 19:30 | 1057 | 1051
2016-12-01 20:00 | 1046 | 1039
2016-12-01 20:30 | 1022 | 1016
2016-12-01 21:00 | 986 | 977
2016-12-01 21:30 | 918 | 911
2016-12-01 22:00 | 881 | 877
2016-12-01 22:30 | 856 | 850
2016-12-01 23:00 | 843 | 838
2016-12-01 23:30 | 778 | 775
2016-12-02 | 722 | 719
2016-12-02 00:30 | 684 | 681
2016-12-02 01:00 | 663 | 659
2016-12-02 01:30 | 642 | 636
2016-12-02 02:00 | 624 | 617
2016-12-02 02:30 | 619 | 611
2016-12-02 03:00 | 618 | 609
2016-12-02 03:30 | 616 | 607
2016-12-02 04:00 | 611 | 601
2016-12-02 04:30 | 622 | 614
2016-12-02 05:00 | 628 | 619
2016-12-02 05:30 | 643 | 636
2016-12-02 06:00 | 672 | 670
2016-12-02 06:30 | 756 | 756
2016-12-02 07:00 | 808 | 808
2016-12-02 07:30 | 862 | 862
2016-12-02 08:00 | 896 | 895
2016-12-02 08:30 | 916 | 915
2016-12-02 09:00 | 925 | 925
2016-12-02 09:30 | 938 | 938
2016-12-02 10:00 | 951 | 950
2016-12-02 10:30 | 963 | 962
2016-12-02 11:00 | 982 | 982
2016-12-02 11:30 | 995 | 992
2016-12-02 12:00 | 1018 | 1015
2016-12-02 12:30 | 1025 | 1023
2016-12-02 13:00 | 1047 | 1045
2016-12-02 13:30 | 1072 | 1071
2016-12-02 14:00 | 1104 | 1100
2016-12-02 14:30 | 1122 | 1118
2016-12-02 15:00 | 1139 | 1135
2016-12-02 15:30 | 1188 | 1183
2016-12-02 16:00 | 1214 | 1210
2016-12-02 16:30 | 1223 | 1219
2016-12-02 17:00 | 1240 | 1235
2016-12-02 17:30 | 1210 | 1204
2016-12-02 18:00 | 1144 | 1138
2016-12-02 18:30 | 1105 | 1093
2016-12-02 19:00 | 1111 | 1108
2016-12-02 19:30 | 1101 | 1098
2016-12-02 20:00 | 1076 | 1075
2016-12-02 20:30 | 1061 | 1060
2016-12-02 21:00 | 1012 | 1009
2016-12-02 21:30 | 975 | 974
2016-12-02 22:00 | 932 | 932
2016-12-02 22:30 | 907 | 906
2016-12-02 23:00 | 902 | 902
2016-12-02 23:30 | 849 | 847
2016-12-03 | 795 | 791
2016-12-03 00:30 | 744 | 743
2016-12-03 01:00 | 723 | 722
2016-12-03 01:30 | 702 | 701
2016-12-03 02:00 | 686 | 684
2016-12-03 02:30 | 679 | 676
2016-12-03 03:00 | 669 | 666
2016-12-03 03:30 | 664 | 661
2016-12-03 04:00 | 659 | 656
2016-12-03 04:30 | 663 | 661
2016-12-03 05:00 | 671 | 668
2016-12-03 05:30 | 677 | 674
2016-12-03 06:00 | 692 | 690
2016-12-03 06:30 | 724 | 724
2016-12-03 07:00 | 755 | 753
2016-12-03 07:30 | 802 | 800
2016-12-03 08:00 | 837 | 833
2016-12-03 08:30 | 876 | 875
2016-12-03 09:00 | 900 | 896
2016-12-03 09:30 | 929 | 920
2016-12-03 10:00 | 921 | 913
2016-12-03 10:30 | 899 | 890
2016-12-03 11:00 | 887 | 879
2016-12-03 11:30 | 870 | 863
2016-12-03 12:00 | 881 | 876
2016-12-03 12:30 | 886 | 882
2016-12-03 13:00 | 906 | 903
2016-12-03 13:30 | 913 | 911
2016-12-03 14:00 | 938 | 937
2016-12-03 14:30 | 984 | 982
2016-12-03 15:00 | 1030 | 1028
2016-12-03 15:30 | 1046 | 1039
2016-12-03 16:00 | 1054 | 1044
2016-12-03 16:30 | 1066 | 1056
2016-12-03 17:00 | 1075 | 1061
2016-12-03 17:30 | 1043 | 1033
2016-12-03 18:00 | 1021 | 1011
2016-12-03 18:30 | 999 | 986
2016-12-03 19:00 | 966 | 953
2016-12-03 19:30 | 930 | 918
2016-12-03 20:00 | 897 | 894
2016-12-03 20:30 | 901 | 898
2016-12-03 21:00 | 888 | 886
2016-12-03 21:30 | 847 | 843
2016-12-03 22:00 | 857 | 853
2016-12-03 22:30 | 853 | 847
2016-12-03 23:00 | 834 | 825
2016-12-03 23:30 | 789 | 773
2016-12-04 | 742 | 729
2016-12-04 00:30 | 707 | 699
2016-12-04 01:00 | 685 | 681
2016-12-04 01:30 | 664 | 659
2016-12-04 02:00 | 647 | 640
2016-12-04 02:30 | 639 | 631
2016-12-04 03:00 | 634 | 625
2016-12-04 03:30 | 632 | 622
2016-12-04 04:00 | 627 | 615
2016-12-04 04:30 | 619 | 607
2016-12-04 05:00 | 613 | 597
2016-12-04 05:30 | 615 | 598
2016-12-04 06:00 | 620 | 605
2016-12-04 06:30 | 635 | 625
2016-12-04 07:00 | 647 | 641
2016-12-04 07:30 | 674 | 672
2016-12-04 08:00 | 707 | 707
2016-12-04 08:30 | 732 | 731
2016-12-04 09:00 | 762 | 759
2016-12-04 09:30 | 782 | 781
2016-12-04 10:00 | 799 | 798
2016-12-04 10:30 | 811 | 809
2016-12-04 11:00 | 819 | 817
2016-12-04 11:30 | 821 | 819
2016-12-04 12:00 | 831 | 830
2016-12-04 12:30 | 836 | 835
2016-12-04 13:00 | 855 | 855
2016-12-04 13:30 | 865 | 865
2016-12-04 14:00 | 896 | 892
2016-12-04 14:30 | 886 | 881
2016-12-04 15:00 | 900 | 895
2016-12-04 15:30 | 956 | 953
2016-12-04 16:00 | 986 | 984
2016-12-04 16:30 | 1001 | 999
2016-12-04 17:00 | 1014 | 1012
2016-12-04 17:30 | 1016 | 1013
2016-12-04 18:00 | 1011 | 1007
2016-12-04 18:30 | 1007 | 1001
2016-12-04 19:00 | 1018 | 1016
2016-12-04 19:30 | 1029 | 1028
2016-12-04 20:00 | 1011 | 1007
2016-12-04 20:30 | 1002 | 998
2016-12-04 21:00 | 943 | 941
2016-12-04 21:30 | 897 | 895
2016-12-04 22:00 | 879 | 874
2016-12-04 22:30 | 845 | 843
2016-12-04 23:00 | 841 | 839
2016-12-04 23:30 | 794 | 789
2016-12-05 | 750 | 744
2016-12-05 00:30 | 721 | 712
2016-12-05 01:00 | 689 | 677
2016-12-05 01:30 | 667 | 662
2016-12-05 02:00 | 630 | 625
2016-12-05 02:30 | 633 | 628
2016-12-05 03:00 | 626 | 620
2016-12-05 03:30 | 654 | 648
2016-12-05 04:00 | 650 | 645
2016-12-05 04:30 | 658 | 655
2016-12-05 05:00 | 669 | 666
2016-12-05 05:30 | 693 | 691
2016-12-05 06:00 | 739 | 738
2016-12-05 06:30 | 811 | 807
2016-12-05 07:00 | 864 | 861
2016-12-05 07:30 | 934 | 934
2016-12-05 08:00 | 971 | 963
2016-12-05 08:30 | 997 | 991
2016-12-05 09:00 | 1006 | 1004
2016-12-05 09:30 | 1016 | 1015
2016-12-05 10:00 | 1037 | 1036
2016-12-05 10:30 | 1052 | 1052
2016-12-05 11:00 | 1068 | 1068
2016-12-05 11:30 | 1080 | 1080
2016-12-05 12:00 | 1097 | 1097
2016-12-05 12:30 | 1125 | 1115
2016-12-05 13:00 | 1132 | 1123
2016-12-05 13:30 | 1171 | 1164
2016-12-05 14:00 | 1214 | 1209
2016-12-05 14:30 | 1226 | 1221
2016-12-05 15:00 | 1235 | 1232
2016-12-05 15:30 | 1229 | 1224
2016-12-05 16:00 | 1244 | 1236
2016-12-05 16:30 | 1264 | 1254
2016-12-05 17:00 | 1285 | 1273
2016-12-05 17:30 | 1285 | 1271
2016-12-05 18:00 | 1261 | 1238
2016-12-05 18:30 | 1215 | 1190
2016-12-05 19:00 | 1204 | 1194
2016-12-05 19:30 | 1165 | 1161
2016-12-05 20:00 | 1119 | 1116
2016-12-05 20:30 | 1087 | 1083
2016-12-05 21:00 | 1027 | 1023
2016-12-05 21:30 | 965 | 965
2016-12-05 22:00 | 926 | 925
2016-12-05 22:30 | 901 | 901
2016-12-05 23:00 | 876 | 875
2016-12-05 23:30 | 822 | 819
2016-12-06 | 787 | 781
2016-12-06 00:30 | 739 | 736
2016-12-06 01:00 | 714 | 712
2016-12-06 01:30 | 695 | 691
2016-12-06 02:00 | 680 | 676
2016-12-06 02:30 | 673 | 668
2016-12-06 03:00 | 671 | 665
2016-12-06 03:30 | 668 | 663
2016-12-06 04:00 | 673 | 669
2016-12-06 04:30 | 681 | 676
2016-12-06 05:00 | 694 | 690
2016-12-06 05:30 | 715 | 714
2016-12-06 06:00 | 747 | 745
2016-12-06 06:30 | 810 | 805
2016-12-06 07:00 | 853 | 848
2016-12-06 07:30 | 904 | 901
2016-12-06 08:00 | 947 | 944
2016-12-06 08:30 | 963 | 962
2016-12-06 09:00 | 967 | 966
2016-12-06 09:30 | 975 | 974
2016-12-06 10:00 | 968 | 968
2016-12-06 10:30 | 988 | 985
2016-12-06 11:00 | 1000 | 995
2016-12-06 11:30 | 991 | 986
2016-12-06 12:00 | 989 | 984
2016-12-06 12:30 | 1016 | 1013
2016-12-06 13:00 | 1064 | 1063
2016-12-06 13:30 | 1111 | 1111
2016-12-06 14:00 | 1174 | 1172
2016-12-06 14:30 | 1225 | 1223
2016-12-06 15:00 | 1291 | 1288
2016-12-06 15:30 | 1335 | 1333
2016-12-06 16:00 | 1409 | 1408
2016-12-06 16:30 | 1436 | 1436
2016-12-06 17:00 | 1430 | 1428
2016-12-06 17:30 | 1384 | 1380
2016-12-06 18:00 | 1317 | 1310
2016-12-06 18:30 | 1291 | 1282
2016-12-06 19:00 | 1303 | 1301
2016-12-06 19:30 | 1235 | 1230
2016-12-06 20:00 | 1177 | 1169
2016-12-06 20:30 | 1133 | 1125
2016-12-06 21:00 | 1066 | 1061
2016-12-06 21:30 | 1002 | 997
2016-12-06 22:00 | 942 | 937
2016-12-06 22:30 | 905 | 899
2016-12-06 23:00 | 900 | 892
2016-12-06 23:30 | 830 | 819
2016-12-07 | 794 | 781
2016-12-07 00:30 | 750 | 741
2016-12-07 01:00 | 725 | 718
2016-12-07 01:30 | 706 | 698
2016-12-07 02:00 | 690 | 681
2016-12-07 02:30 | 673 | 667
2016-12-07 03:00 | 670 | 663
2016-12-07 03:30 | 661 | 655
2016-12-07 04:00 | 659 | 655
2016-12-07 04:30 | 668 | 665
2016-12-07 05:00 | 680 | 678
2016-12-07 05:30 | 714 | 712
2016-12-07 06:00 | 754 | 749
2016-12-07 06:30 | 826 | 819
2016-12-07 07:00 | 886 | 882
2016-12-07 07:30 | 936 | 931
2016-12-07 08:00 | 964 | 958
2016-12-07 08:30 | 999 | 993
2016-12-07 09:00 | 996 | 990
2016-12-07 09:30 | 1002 | 996
2016-12-07 10:00 | 1015 | 1009
2016-12-07 10:30 | 1042 | 1038
2016-12-07 11:00 | 1043 | 1039
2016-12-07 11:30 | 1033 | 1028
2016-12-07 12:00 | 1035 | 1029
2016-12-07 12:30 | 1077 | 1074
2016-12-07 13:00 | 1079 | 1077
2016-12-07 13:30 | 1126 | 1119
2016-12-07 14:00 | 1172 | 1164
2016-12-07 14:30 | 1196 | 1187
2016-12-07 15:00 | 1198 | 1187
2016-12-07 15:30 | 1229 | 1219
2016-12-07 16:00 | 1237 | 1225
2016-12-07 16:30 | 1222 | 1204
2016-12-07 17:00 | 1207 | 1187
2016-12-07 17:30 | 1186 | 1167
2016-12-07 18:00 | 1157 | 1139
2016-12-07 18:30 | 1121 | 1107
2016-12-07 19:00 | 1128 | 1120
2016-12-07 19:30 | 1102 | 1093
2016-12-07 20:00 | 1075 | 1069
2016-12-07 20:30 | 1043 | 1038
2016-12-07 21:00 | 988 | 982
2016-12-07 21:30 | 939 | 935
2016-12-07 22:00 | 901 | 896
2016-12-07 22:30 | 875 | 868
2016-12-07 23:00 | 859 | 853
2016-12-07 23:30 | 798 | 792
2016-12-08 | 760 | 750
2016-12-08 00:30 | 717 | 708
2016-12-08 01:00 | 687 | 682
2016-12-08 01:30 | 675 | 670
2016-12-08 02:00 | 658 | 652
2016-12-08 02:30 | 649 | 643
2016-12-08 03:00 | 648 | 641
2016-12-08 03:30 | 648 | 641
2016-12-08 04:00 | 646 | 640
2016-12-08 04:30 | 654 | 649
2016-12-08 05:00 | 666 | 661
2016-12-08 05:30 | 699 | 696
2016-12-08 06:00 | 739 | 736
2016-12-08 06:30 | 802 | 799
2016-12-08 07:00 | 859 | 855
2016-12-08 07:30 | 917 | 915
2016-12-08 08:00 | 951 | 951
2016-12-08 08:30 | 988 | 988
2016-12-08 09:00 | 1006 | 1005
2016-12-08 09:30 | 1048 | 1048
2016-12-08 10:00 | 1048 | 1047
2016-12-08 10:30 | 1038 | 1037
2016-12-08 11:00 | 1024 | 1023
2016-12-08 11:30 | 1054 | 1054
2016-12-08 12:00 | 1068 | 1067
2016-12-08 12:30 | 1063 | 1063
2016-12-08 13:00 | 1049 | 1048
2016-12-08 13:30 | 1049 | 1048
2016-12-08 14:00 | 1091 | 1090
2016-12-08 14:30 | 1087 | 1084
2016-12-08 15:00 | 1062 | 1058
2016-12-08 15:30 | 1047 | 1043
2016-12-08 16:00 | 1056 | 1053
2016-12-08 16:30 | 1095 | 1092
2016-12-08 17:00 | 1157 | 1149
2016-12-08 17:30 | 1153 | 1142
2016-12-08 18:00 | 1152 | 1143
2016-12-08 18:30 | 1114 | 1102
2016-12-08 19:00 | 1127 | 1123
2016-12-08 19:30 | 1097 | 1092
2016-12-08 20:00 | 1083 | 1082
2016-12-08 20:30 | 1044 | 1041
2016-12-08 21:00 | 992 | 991
2016-12-08 21:30 | 932 | 929
2016-12-08 22:00 | 904 | 898
2016-12-08 22:30 | 892 | 883
2016-12-08 23:00 | 870 | 859
2016-12-08 23:30 | 817 | 804
2016-12-09 | 764 | 758
2016-12-09 00:30 | 727 | 721
2016-12-09 01:00 | 704 | 697
2016-12-09 01:30 | 687 | 677
2016-12-09 02:00 | 666 | 658
2016-12-09 02:30 | 653 | 646
2016-12-09 03:00 | 649 | 641
2016-12-09 03:30 | 651 | 644
2016-12-09 04:00 | 652 | 645
2016-12-09 04:30 | 662 | 656
2016-12-09 05:00 | 676 | 670
2016-12-09 05:30 | 704 | 701
2016-12-09 06:00 | 748 | 745
2016-12-09 06:30 | 821 | 817
2016-12-09 07:00 | 905 | 898
2016-12-09 07:30 | 965 | 962
2016-12-09 08:00 | 1012 | 1009
2016-12-09 08:30 | 1052 | 1045
2016-12-09 09:00 | 1065 | 1060
2016-12-09 09:30 | 1077 | 1072
2016-12-09 10:00 | 1076 | 1072
2016-12-09 10:30 | 1073 | 1069
2016-12-09 11:00 | 1063 | 1059
2016-12-09 11:30 | 1059 | 1054
2016-12-09 12:00 | 1050 | 1044
2016-12-09 12:30 | 1052 | 1046
2016-12-09 13:00 | 1076 | 1072
2016-12-09 13:30 | 1071 | 1064
2016-12-09 14:00 | 1028 | 1018
2016-12-09 14:30 | 1013 | 1001
2016-12-09 15:00 | 998 | 987
2016-12-09 15:30 | 986 | 973
2016-12-09 16:00 | 1001 | 990
2016-12-09 16:30 | 1000 | 989
2016-12-09 17:00 | 1009 | 999
2016-12-09 17:30 | 1008 | 996
2016-12-09 18:00 | 981 | 973
2016-12-09 18:30 | 962 | 955
2016-12-09 19:00 | 966 | 962
2016-12-09 19:30 | 973 | 970
2016-12-09 20:00 | 989 | 985
2016-12-09 20:30 | 968 | 964
2016-12-09 21:00 | 931 | 930
2016-12-09 21:30 | 894 | 892
2016-12-09 22:00 | 871 | 869
2016-12-09 22:30 | 840 | 840
2016-12-09 23:00 | 836 | 836
2016-12-09 23:30 | 779 | 778
2016-12-10 | 730 | 725
2016-12-10 00:30 | 694 | 687
2016-12-10 01:00 | 667 | 661
2016-12-10 01:30 | 643 | 636
2016-12-10 02:00 | 629 | 620
2016-12-10 02:30 | 618 | 608
2016-12-10 03:00 | 609 | 597
2016-12-10 03:30 | 601 | 589
2016-12-10 04:00 | 597 | 585
2016-12-10 04:30 | 595 | 583
2016-12-10 05:00 | 596 | 582
2016-12-10 05:30 | 601 | 586
2016-12-10 06:00 | 614 | 601
2016-12-10 06:30 | 635 | 627
2016-12-10 07:00 | 653 | 648
2016-12-10 07:30 | 681 | 680
2016-12-10 08:00 | 713 | 713
2016-12-10 08:30 | 737 | 737
2016-12-10 09:00 | 759 | 759
2016-12-10 09:30 | 778 | 776
2016-12-10 10:00 | 794 | 792
2016-12-10 10:30 | 783 | 782
2016-12-10 11:00 | 760 | 759
2016-12-10 11:30 | 757 | 755
2016-12-10 12:00 | 768 | 766
2016-12-10 12:30 | 771 | 769
2016-12-10 13:00 | 787 | 785
2016-12-10 13:30 | 771 | 769
2016-12-10 14:00 | 762 | 760
2016-12-10 14:30 | 768 | 765
2016-12-10 15:00 | 778 | 775
2016-12-10 15:30 | 793 | 790
2016-12-10 16:00 | 810 | 807
2016-12-10 16:30 | 816 | 813
2016-12-10 17:00 | 825 | 822
2016-12-10 17:30 | 827 | 823
2016-12-10 18:00 | 819 | 815
2016-12-10 18:30 | 827 | 822
2016-12-10 19:00 | 848 | 845
2016-12-10 19:30 | 853 | 851
2016-12-10 20:00 | 854 | 852
2016-12-10 20:30 | 843 | 840
2016-12-10 21:00 | 813 | 808
2016-12-10 21:30 | 791 | 788
2016-12-10 22:00 | 776 | 772
2016-12-10 22:30 | 769 | 763
2016-12-10 23:00 | 777 | 775
2016-12-10 23:30 | 726 | 723
2016-12-11 | 686 | 680
2016-12-11 00:30 | 652 | 644
2016-12-11 01:00 | 633 | 622
2016-12-11 01:30 | 612 | 599
2016-12-11 02:00 | 598 | 583
2016-12-11 02:30 | 583 | 567
2016-12-11 03:00 | 575 | 558
2016-12-11 03:30 | 574 | 556
2016-12-11 04:00 | 574 | 555
2016-12-11 04:30 | 571 | 552
2016-12-11 05:00 | 562 | 538
2016-12-11 05:30 | 564 | 538
2016-12-11 06:00 | 568 | 543
2016-12-11 06:30 | 574 | 554
2016-12-11 07:00 | 580 | 565
2016-12-11 07:30 | 600 | 591
2016-12-11 08:00 | 618 | 614
2016-12-11 08:30 | 654 | 653
2016-12-11 09:00 | 656 | 654
2016-12-11 09:30 | 654 | 653
2016-12-11 10:00 | 660 | 660
2016-12-11 10:30 | 666 | 666
2016-12-11 11:00 | 651 | 651
2016-12-11 11:30 | 639 | 638
2016-12-11 12:00 | 653 | 652
2016-12-11 12:30 | 661 | 660
2016-12-11 13:00 | 650 | 649
2016-12-11 13:30 | 674 | 674
2016-12-11 14:00 | 691 | 690
2016-12-11 14:30 | 697 | 697
2016-12-11 15:00 | 712 | 711
2016-12-11 15:30 | 744 | 744
2016-12-11 16:00 | 755 | 755
2016-12-11 16:30 | 763 | 762
2016-12-11 17:00 | 776 | 776
2016-12-11 17:30 | 782 | 781
2016-12-11 18:00 | 781 | 780
2016-12-11 18:30 | 790 | 788
2016-12-11 19:00 | 818 | 818
2016-12-11 19:30 | 834 | 833
2016-12-11 20:00 | 836 | 834
2016-12-11 20:30 | 830 | 826
2016-12-11 21:00 | 800 | 794
2016-12-11 21:30 | 777 | 769
2016-12-11 22:00 | 751 | 744
2016-12-11 22:30 | 741 | 734
2016-12-11 23:00 | 753 | 746
2016-12-11 23:30 | 709 | 697
2016-12-12 | 668 | 651
2016-12-12 00:30 | 639 | 617
2016-12-12 01:00 | 620 | 594
2016-12-12 01:30 | 608 | 580
2016-12-12 02:00 | 589 | 567
2016-12-12 02:30 | 580 | 563
2016-12-12 03:00 | 579 | 561
2016-12-12 03:30 | 578 | 562
2016-12-12 04:00 | 579 | 563
2016-12-12 04:30 | 592 | 579
2016-12-12 05:00 | 594 | 580
2016-12-12 05:30 | 611 | 600
2016-12-12 06:00 | 646 | 639
2016-12-12 06:30 | 694 | 692
2016-12-12 07:00 | 738 | 736
2016-12-12 07:30 | 788 | 787
2016-12-12 08:00 | 818 | 818
2016-12-12 08:30 | 844 | 844
2016-12-12 09:00 | 851 | 851
2016-12-12 09:30 | 863 | 863
2016-12-12 10:00 | 861 | 861
2016-12-12 10:30 | 858 | 858
2016-12-12 11:00 | 859 | 859
2016-12-12 11:30 | 862 | 862
2016-12-12 12:00 | 864 | 864
2016-12-12 12:30 | 871 | 871
2016-12-12 13:00 | 872 | 872
2016-12-12 13:30 | 885 | 885
2016-12-12 14:00 | 906 | 905
2016-12-12 14:30 | 922 | 921
2016-12-12 15:00 | 943 | 943
2016-12-12 15:30 | 952 | 951
2016-12-12 16:00 | 965 | 965
2016-12-12 16:30 | 984 | 984
2016-12-12 17:00 | 1001 | 1000
2016-12-12 17:30 | 993 | 990
2016-12-12 18:00 | 983 | 977
2016-12-12 18:30 | 968 | 964
2016-12-12 19:00 | 987 | 985
2016-12-12 19:30 | 990 | 989
2016-12-12 20:00 | 983 | 980
2016-12-12 20:30 | 952 | 951
2016-12-12 21:00 | 909 | 907
2016-12-12 21:30 | 864 | 864
2016-12-12 22:00 | 825 | 824
2016-12-12 22:30 | 804 | 802
2016-12-12 23:00 | 804 | 803
2016-12-12 23:30 | 750 | 748
2016-12-13 | 697 | 692
2016-12-13 00:30 | 661 | 653
2016-12-13 01:00 | 638 | 630
2016-12-13 01:30 | 612 | 602
2016-12-13 02:00 | 602 | 591
2016-12-13 02:30 | 598 | 587
2016-12-13 03:00 | 598 | 586
2016-12-13 03:30 | 600 | 588
2016-12-13 04:00 | 596 | 584
2016-12-13 04:30 | 604 | 594
2016-12-13 05:00 | 609 | 598
2016-12-13 05:30 | 642 | 633
2016-12-13 06:00 | 668 | 663
2016-12-13 06:30 | 710 | 709
2016-12-13 07:00 | 751 | 749
2016-12-13 07:30 | 803 | 803
2016-12-13 08:00 | 828 | 828
2016-12-13 08:30 | 859 | 859
2016-12-13 09:00 | 868 | 868
2016-12-13 09:30 | 862 | 862
2016-12-13 10:00 | 861 | 861
2016-12-13 10:30 | 865 | 865
2016-12-13 11:00 | 855 | 855
2016-12-13 11:30 | 861 | 861
2016-12-13 12:00 | 862 | 862
2016-12-13 12:30 | 868 | 868
2016-12-13 13:00 | 877 | 877
2016-12-13 13:30 | 887 | 887
2016-12-13 14:00 | 899 | 899
2016-12-13 14:30 | 917 | 917
2016-12-13 15:00 | 940 | 940
2016-12-13 15:30 | 970 | 970
2016-12-13 16:00 | 999 | 995
2016-12-13 16:30 | 1022 | 1018
2016-12-13 17:00 | 1039 | 1034
2016-12-13 17:30 | 1038 | 1031
2016-12-13 18:00 | 1015 | 1011
2016-12-13 18:30 | 990 | 985
2016-12-13 19:00 | 1003 | 998
2016-12-13 19:30 | 1013 | 1010
2016-12-13 20:00 | 1006 | 1003
2016-12-13 20:30 | 984 | 979
2016-12-13 21:00 | 939 | 936
2016-12-13 21:30 | 887 | 886
2016-12-13 22:00 | 857 | 855
2016-12-13 22:30 | 834 | 832
2016-12-13 23:00 | 815 | 813
2016-12-13 23:30 | 765 | 760
2016-12-14 | 718 | 709
2016-12-14 00:30 | 681 | 668
2016-12-14 01:00 | 648 | 635
2016-12-14 01:30 | 630 | 623
2016-12-14 02:00 | 619 | 611
2016-12-14 02:30 | 616 | 608
2016-12-14 03:00 | 608 | 599
2016-12-14 03:30 | 607 | 597
2016-12-14 04:00 | 607 | 597
2016-12-14 04:30 | 611 | 602
2016-12-14 05:00 | 607 | 599
2016-12-14 05:30 | 643 | 636
2016-12-14 06:00 | 677 | 674
2016-12-14 06:30 | 725 | 724
2016-12-14 07:00 | 785 | 782
2016-12-14 07:30 | 834 | 832
2016-12-14 08:00 | 868 | 868
2016-12-14 08:30 | 896 | 895
2016-12-14 09:00 | 908 | 908
2016-12-14 09:30 | 905 | 905
2016-12-14 10:00 | 902 | 902
2016-12-14 10:30 | 907 | 907
2016-12-14 11:00 | 901 | 901
2016-12-14 11:30 | 902 | 902
2016-12-14 12:00 | 905 | 905
2016-12-14 12:30 | 905 | 904
2016-12-14 13:00 | 919 | 919
2016-12-14 13:30 | 926 | 925
2016-12-14 14:00 | 948 | 947
2016-12-14 14:30 | 967 | 967
2016-12-14 15:00 | 985 | 985
2016-12-14 15:30 | 1006 | 1006
2016-12-14 16:00 | 1046 | 1045
2016-12-14 16:30 | 1077 | 1073
2016-12-14 17:00 | 1097 | 1091
2016-12-14 17:30 | 1100 | 1091
2016-12-14 18:00 | 1068 | 1062
2016-12-14 18:30 | 1030 | 1025
2016-12-14 19:00 | 1043 | 1040
2016-12-14 19:30 | 1023 | 1021
2016-12-14 20:00 | 1006 | 1002
2016-12-14 20:30 | 980 | 976
2016-12-14 21:00 | 931 | 928
2016-12-14 21:30 | 889 | 886
2016-12-14 22:00 | 848 | 844
2016-12-14 22:30 | 839 | 834
2016-12-14 23:00 | 831 | 824
2016-12-14 23:30 | 764 | 760
2016-12-15 | 723 | 721
2016-12-15 00:30 | 687 | 682
2016-12-15 01:00 | 672 | 666
2016-12-15 01:30 | 647 | 640
2016-12-15 02:00 | 634 | 626
2016-12-15 02:30 | 625 | 615
2016-12-15 03:00 | 622 | 612
2016-12-15 03:30 | 624 | 614
2016-12-15 04:00 | 626 | 616
2016-12-15 04:30 | 631 | 622
2016-12-15 05:00 | 644 | 634
2016-12-15 05:30 | 673 | 665
2016-12-15 06:00 | 698 | 694
2016-12-15 06:30 | 754 | 751
2016-12-15 07:00 | 802 | 798
2016-12-15 07:30 | 838 | 837
2016-12-15 08:00 | 870 | 866
2016-12-15 08:30 | 875 | 873
2016-12-15 09:00 | 881 | 880
2016-12-15 09:30 | 900 | 898
2016-12-15 10:00 | 925 | 924
2016-12-15 10:30 | 916 | 915
2016-12-15 11:00 | 931 | 931
2016-12-15 11:30 | 943 | 943
2016-12-15 12:00 | 957 | 957
2016-12-15 12:30 | 974 | 973
2016-12-15 13:00 | 995 | 993
2016-12-15 13:30 | 1014 | 1010
2016-12-15 14:00 | 1018 | 1013
2016-12-15 14:30 | 1032 | 1026
2016-12-15 15:00 | 1058 | 1052
2016-12-15 15:30 | 1079 | 1072
2016-12-15 16:00 | 1119 | 1106
2016-12-15 16:30 | 1134 | 1124
2016-12-15 17:00 | 1146 | 1134
2016-12-15 17:30 | 1137 | 1120
2016-12-15 18:00 | 1120 | 1107
2016-12-15 18:30 | 1095 | 1084
2016-12-15 19:00 | 1113 | 1107
2016-12-15 19:30 | 1117 | 1112
2016-12-15 20:00 | 1108 | 1103
2016-12-15 20:30 | 1081 | 1075
2016-12-15 21:00 | 1023 | 1018
2016-12-15 21:30 | 976 | 971
2016-12-15 22:00 | 943 | 935
2016-12-15 22:30 | 915 | 914
2016-12-15 23:00 | 861 | 858
2016-12-15 23:30 | 790 | 787
2016-12-16 | 769 | 765
2016-12-16 00:30 | 735 | 728
2016-12-16 01:00 | 710 | 699
2016-12-16 01:30 | 689 | 677
2016-12-16 02:00 | 675 | 661
2016-12-16 02:30 | 667 | 652
2016-12-16 03:00 | 662 | 647
2016-12-16 03:30 | 661 | 645
2016-12-16 04:00 | 662 | 647
2016-12-16 04:30 | 668 | 655
2016-12-16 05:00 | 669 | 654
2016-12-16 05:30 | 682 | 669
2016-12-16 06:00 | 717 | 709
2016-12-16 06:30 | 727 | 726
2016-12-16 07:00 | 822 | 822
2016-12-16 07:30 | 892 | 891
2016-12-16 08:00 | 915 | 912
2016-12-16 08:30 | 971 | 971
2016-12-16 09:00 | 1004 | 1004
2016-12-16 09:30 | 994 | 991
2016-12-16 10:00 | 967 | 964
2016-12-16 10:30 | 982 | 979
2016-12-16 11:00 | 997 | 995
2016-12-16 11:30 | 1006 | 1003
2016-12-16 12:00 | 1019 | 1017
2016-12-16 12:30 | 1008 | 1005
2016-12-16 13:00 | 995 | 991
2016-12-16 13:30 | 952 | 947
2016-12-16 14:00 | 991 | 987
2016-12-16 14:30 | 1034 | 1026
2016-12-16 15:00 | 1039 | 1028
2016-12-16 15:30 | 1050 | 1039
2016-12-16 16:00 | 1058 | 1045
2016-12-16 16:30 | 1060 | 1045
2016-12-16 17:00 | 1073 | 1055
2016-12-16 17:30 | 1042 | 1019
2016-12-16 18:00 | 1020 | 996
2016-12-16 18:30 | 978 | 958
2016-12-16 19:00 | 991 | 979
2016-12-16 19:30 | 1003 | 994
2016-12-16 20:00 | 1010 | 1002
2016-12-16 20:30 | 991 | 988
2016-12-16 21:00 | 936 | 932
2016-12-16 21:30 | 894 | 891
2016-12-16 22:00 | 872 | 866
2016-12-16 22:30 | 877 | 869
2016-12-16 23:00 | 844 | 841
2016-12-16 23:30 | 778 | 773
2016-12-17 | 738 | 732
2016-12-17 00:30 | 675 | 668
2016-12-17 01:00 | 658 | 648
2016-12-17 01:30 | 659 | 646
2016-12-17 02:00 | 624 | 609
2016-12-17 02:30 | 621 | 605
2016-12-17 03:00 | 626 | 608
2016-12-17 03:30 | 616 | 597
2016-12-17 04:00 | 610 | 591
2016-12-17 04:30 | 599 | 580
2016-12-17 05:00 | 612 | 591
2016-12-17 05:30 | 640 | 620
2016-12-17 06:00 | 644 | 627
2016-12-17 06:30 | 669 | 658
2016-12-17 07:00 | 698 | 693
2016-12-17 07:30 | 727 | 726
2016-12-17 08:00 | 734 | 734
2016-12-17 08:30 | 750 | 750
2016-12-17 09:00 | 785 | 785
2016-12-17 09:30 | 813 | 813
2016-12-17 10:00 | 835 | 835
2016-12-17 10:30 | 834 | 834
2016-12-17 11:00 | 850 | 850
2016-12-17 11:30 | 807 | 807
2016-12-17 12:00 | 818 | 818
2016-12-17 12:30 | 830 | 830
2016-12-17 13:00 | 848 | 847
2016-12-17 13:30 | 894 | 894
2016-12-17 14:00 | 897 | 897
2016-12-17 14:30 | 904 | 904
2016-12-17 15:00 | 956 | 956
2016-12-17 15:30 | 989 | 989
2016-12-17 16:00 | 1011 | 1011
2016-12-17 16:30 | 1015 | 1014
2016-12-17 17:00 | 1033 | 1033
2016-12-17 17:30 | 1017 | 1016
2016-12-17 18:00 | 1008 | 1005
2016-12-17 18:30 | 989 | 982
2016-12-17 19:00 | 997 | 990
2016-12-17 19:30 | 986 | 981
2016-12-17 20:00 | 985 | 979
2016-12-17 20:30 | 952 | 949
2016-12-17 21:00 | 914 | 912
2016-12-17 21:30 | 887 | 884
2016-12-17 22:00 | 865 | 862
2016-12-17 22:30 | 898 | 893
2016-12-17 23:00 | 873 | 867
2016-12-17 23:30 | 795 | 790
2016-12-18 | 777 | 771
2016-12-18 00:30 | 733 | 728
2016-12-18 01:00 | 706 | 701
2016-12-18 01:30 | 673 | 666
2016-12-18 02:00 | 653 | 643
2016-12-18 02:30 | 643 | 632
2016-12-18 03:00 | 620 | 609
2016-12-18 03:30 | 624 | 612
2016-12-18 04:00 | 626 | 612
2016-12-18 04:30 | 624 | 611
2016-12-18 05:00 | 621 | 605
2016-12-18 05:30 | 619 | 599
2016-12-18 06:00 | 629 | 610
2016-12-18 06:30 | 639 | 624
2016-12-18 07:00 | 657 | 647
2016-12-18 07:30 | 687 | 683
2016-12-18 08:00 | 720 | 719
2016-12-18 08:30 | 722 | 722
2016-12-18 09:00 | 725 | 725
2016-12-18 09:30 | 741 | 741
2016-12-18 10:00 | 745 | 745
2016-12-18 10:30 | 763 | 763
2016-12-18 11:00 | 790 | 790
2016-12-18 11:30 | 837 | 837
2016-12-18 12:00 | 857 | 855
2016-12-18 12:30 | 856 | 848
2016-12-18 13:00 | 840 | 828
2016-12-18 13:30 | 811 | 802
2016-12-18 14:00 | 826 | 820
2016-12-18 14:30 | 865 | 861
2016-12-18 15:00 | 887 | 882
2016-12-18 15:30 | 849 | 840
2016-12-18 16:00 | 789 | 784
2016-12-18 16:30 | 806 | 803
2016-12-18 17:00 | 833 | 830
2016-12-18 17:30 | 846 | 844
2016-12-18 18:00 | 844 | 840
2016-12-18 18:30 | 836 | 831
2016-12-18 19:00 | 828 | 824
2016-12-18 19:30 | 840 | 838
2016-12-18 20:00 | 834 | 831
2016-12-18 20:30 | 826 | 823
2016-12-18 21:00 | 798 | 793
2016-12-18 21:30 | 755 | 752
2016-12-18 22:00 | 746 | 742
2016-12-18 22:30 | 722 | 717
2016-12-18 23:00 | 742 | 739
2016-12-18 23:30 | 680 | 674
2016-12-19 | 657 | 647
2016-12-19 00:30 | 626 | 612
2016-12-19 01:00 | 629 | 612
2016-12-19 01:30 | 593 | 573
2016-12-19 02:00 | 589 | 567
2016-12-19 02:30 | 593 | 570
2016-12-19 03:00 | 582 | 557
2016-12-19 03:30 | 588 | 564
2016-12-19 04:00 | 594 | 570
2016-12-19 04:30 | 605 | 585
2016-12-19 05:00 | 620 | 601
2016-12-19 05:30 | 651 | 635
2016-12-19 06:00 | 681 | 671
2016-12-19 06:30 | 709 | 697
2016-12-19 07:00 | 740 | 734
2016-12-19 07:30 | 797 | 792
2016-12-19 08:00 | 839 | 835
2016-12-19 08:30 | 862 | 856
2016-12-19 09:00 | 865 | 859
2016-12-19 09:30 | 869 | 861
2016-12-19 10:00 | 877 | 869
2016-12-19 10:30 | 883 | 876
2016-12-19 11:00 | 885 | 880
2016-12-19 11:30 | 878 | 871
2016-12-19 12:00 | 874 | 869
2016-12-19 12:30 | 870 | 864
2016-12-19 13:00 | 869 | 864
2016-12-19 13:30 | 880 | 877
2016-12-19 14:00 | 894 | 891
2016-12-19 14:30 | 894 | 891
2016-12-19 15:00 | 913 | 910
2016-12-19 15:30 | 925 | 921
2016-12-19 16:00 | 951 | 943
2016-12-19 16:30 | 950 | 942
2016-12-19 17:00 | 956 | 950
2016-12-19 17:30 | 958 | 951
2016-12-19 18:00 | 960 | 950
2016-12-19 18:30 | 942 | 928
2016-12-19 19:00 | 962 | 952
2016-12-19 19:30 | 968 | 962
2016-12-19 20:00 | 958 | 953
2016-12-19 20:30 | 962 | 955
2016-12-19 21:00 | 937 | 934
2016-12-19 21:30 | 905 | 900
2016-12-19 22:00 | 882 | 872
2016-12-19 22:30 | 853 | 846
2016-12-19 23:00 | 837 | 835
2016-12-19 23:30 | 782 | 779
2016-12-20 | 745 | 737
2016-12-20 00:30 | 704 | 694
2016-12-20 01:00 | 675 | 661
2016-12-20 01:30 | 665 | 650
2016-12-20 02:00 | 654 | 638
2016-12-20 02:30 | 647 | 629
2016-12-20 03:00 | 645 | 626
2016-12-20 03:30 | 649 | 630
2016-12-20 04:00 | 650 | 631
2016-12-20 04:30 | 656 | 640
2016-12-20 05:00 | 667 | 653
2016-12-20 05:30 | 692 | 679
2016-12-20 06:00 | 718 | 709
2016-12-20 06:30 | 765 | 762
2016-12-20 07:00 | 803 | 803
2016-12-20 07:30 | 848 | 848
2016-12-20 08:00 | 874 | 873
2016-12-20 08:30 | 899 | 898
2016-12-20 09:00 | 922 | 917
2016-12-20 09:30 | 953 | 944
2016-12-20 10:00 | 964 | 958
2016-12-20 10:30 | 945 | 940
2016-12-20 11:00 | 945 | 941
2016-12-20 11:30 | 947 | 944
2016-12-20 12:00 | 943 | 941
2016-12-20 12:30 | 950 | 948
2016-12-20 13:00 | 950 | 948
2016-12-20 13:30 | 958 | 956
2016-12-20 14:00 | 979 | 976
2016-12-20 14:30 | 1003 | 994
2016-12-20 15:00 | 1015 | 1008
2016-12-20 15:30 | 1022 | 1016
2016-12-20 16:00 | 1056 | 1050
2016-12-20 16:30 | 1076 | 1070
2016-12-20 17:00 | 1090 | 1082
2016-12-20 17:30 | 1074 | 1061
2016-12-20 18:00 | 1074 | 1055
2016-12-20 18:30 | 1042 | 1032
2016-12-20 19:00 | 1043 | 1038
2016-12-20 19:30 | 1025 | 1020
2016-12-20 20:00 | 1018 | 1017
2016-12-20 20:30 | 1014 | 1013
2016-12-20 21:00 | 977 | 974
2016-12-20 21:30 | 949 | 946
2016-12-20 22:00 | 914 | 908
2016-12-20 22:30 | 888 | 881
2016-12-20 23:00 | 879 | 872
2016-12-20 23:30 | 820 | 810
2016-12-21 | 770 | 760
2016-12-21 00:30 | 728 | 716
2016-12-21 01:00 | 700 | 692
2016-12-21 01:30 | 681 | 671
2016-12-21 02:00 | 666 | 655
2016-12-21 02:30 | 662 | 650
2016-12-21 03:00 | 655 | 642
2016-12-21 03:30 | 655 | 642
2016-12-21 04:00 | 649 | 636
2016-12-21 04:30 | 658 | 647
2016-12-21 05:00 | 669 | 657
2016-12-21 05:30 | 692 | 682
2016-12-21 06:00 | 720 | 714
2016-12-21 06:30 | 775 | 773
2016-12-21 07:00 | 826 | 822
2016-12-21 07:30 | 882 | 880
2016-12-21 08:00 | 919 | 918
2016-12-21 08:30 | 944 | 944
2016-12-21 09:00 | 980 | 976
2016-12-21 09:30 | 1005 | 997
2016-12-21 10:00 | 1027 | 1021
2016-12-21 10:30 | 1037 | 1033
2016-12-21 11:00 | 1062 | 1060
2016-12-21 11:30 | 1047 | 1045
2016-12-21 12:00 | 1065 | 1063
2016-12-21 12:30 | 1123 | 1120
2016-12-21 13:00 | 1142 | 1140
2016-12-21 13:30 | 1159 | 1155
2016-12-21 14:00 | 1172 | 1170
2016-12-21 14:30 | 1225 | 1224
2016-12-21 15:00 | 1282 | 1282
2016-12-21 15:30 | 1311 | 1310
2016-12-21 16:00 | 1315 | 1314
2016-12-21 16:30 | 1285 | 1282
2016-12-21 17:00 | 1269 | 1263
2016-12-21 17:30 | 1220 | 1212
2016-12-21 18:00 | 1202 | 1198
2016-12-21 18:30 | 1155 | 1153
2016-12-21 19:00 | 1158 | 1158
2016-12-21 19:30 | 1147 | 1147
2016-12-21 20:00 | 1127 | 1127
2016-12-21 20:30 | 1097 | 1097
2016-12-21 21:00 | 1048 | 1048
2016-12-21 21:30 | 1004 | 1003
2016-12-21 22:00 | 954 | 952
2016-12-21 22:30 | 920 | 917
2016-12-21 23:00 | 904 | 901
2016-12-21 23:30 | 836 | 829
2016-12-22 | 781 | 775
2016-12-22 00:30 | 742 | 732
2016-12-22 01:00 | 712 | 708
2016-12-22 01:30 | 688 | 685
2016-12-22 02:00 | 674 | 671
2016-12-22 02:30 | 660 | 657
2016-12-22 03:00 | 655 | 652
2016-12-22 03:30 | 656 | 653
2016-12-22 04:00 | 654 | 651
2016-12-22 04:30 | 662 | 660
2016-12-22 05:00 | 666 | 663
2016-12-22 05:30 | 687 | 685
2016-12-22 06:00 | 733 | 730
2016-12-22 06:30 | 781 | 777
2016-12-22 07:00 | 830 | 828
2016-12-22 07:30 | 882 | 879
2016-12-22 08:00 | 921 | 919
2016-12-22 08:30 | 946 | 946
2016-12-22 09:00 | 978 | 977
2016-12-22 09:30 | 984 | 984
2016-12-22 10:00 | 996 | 994
2016-12-22 10:30 | 1002 | 1000
2016-12-22 11:00 | 992 | 991
2016-12-22 11:30 | 968 | 966
2016-12-22 12:00 | 953 | 950
2016-12-22 12:30 | 957 | 955
2016-12-22 13:00 | 981 | 979
2016-12-22 13:30 | 987 | 985
2016-12-22 14:00 | 1016 | 1013
2016-12-22 14:30 | 1012 | 1009
2016-12-22 15:00 | 1020 | 1017
2016-12-22 15:30 | 1026 | 1022
2016-12-22 16:00 | 1030 | 1023
2016-12-22 16:30 | 1019 | 1008
2016-12-22 17:00 | 993 | 980
2016-12-22 17:30 | 993 | 986
2016-12-22 18:00 | 982 | 973
2016-12-22 18:30 | 965 | 960
2016-12-22 19:00 | 958 | 957
2016-12-22 19:30 | 961 | 960
2016-12-22 20:00 | 971 | 969
2016-12-22 20:30 | 963 | 962
2016-12-22 21:00 | 934 | 933
2016-12-22 21:30 | 894 | 893
2016-12-22 22:00 | 870 | 868
2016-12-22 22:30 | 855 | 851
2016-12-22 23:00 | 852 | 847
2016-12-22 23:30 | 799 | 789
2016-12-23 | 737 | 725
2016-12-23 00:30 | 694 | 690
2016-12-23 01:00 | 670 | 665
2016-12-23 01:30 | 648 | 640
2016-12-23 02:00 | 635 | 627
2016-12-23 02:30 | 628 | 620
2016-12-23 03:00 | 625 | 616
2016-12-23 03:30 | 620 | 611
2016-12-23 04:00 | 623 | 614
2016-12-23 04:30 | 630 | 622
2016-12-23 05:00 | 630 | 623
2016-12-23 05:30 | 657 | 651
2016-12-23 06:00 | 671 | 666
2016-12-23 06:30 | 716 | 715
2016-12-23 07:00 | 755 | 753
2016-12-23 07:30 | 799 | 799
2016-12-23 08:00 | 829 | 829
2016-12-23 08:30 | 848 | 847
2016-12-23 09:00 | 867 | 864
2016-12-23 09:30 | 881 | 878
2016-12-23 10:00 | 888 | 884
2016-12-23 10:30 | 894 | 890
2016-12-23 11:00 | 895 | 892
2016-12-23 11:30 | 905 | 902
2016-12-23 12:00 | 894 | 891
2016-12-23 12:30 | 891 | 887
2016-12-23 13:00 | 893 | 889
2016-12-23 13:30 | 904 | 900
2016-12-23 14:00 | 896 | 892
2016-12-23 14:30 | 892 | 887
2016-12-23 15:00 | 910 | 906
2016-12-23 15:30 | 926 | 921
2016-12-23 16:00 | 921 | 915
2016-12-23 16:30 | 934 | 928
2016-12-23 17:00 | 944 | 936
2016-12-23 17:30 | 937 | 928
2016-12-23 18:00 | 933 | 923
2016-12-23 18:30 | 934 | 923
2016-12-23 19:00 | 943 | 938
2016-12-23 19:30 | 942 | 939
2016-12-23 20:00 | 940 | 936
2016-12-23 20:30 | 927 | 922
2016-12-23 21:00 | 899 | 896
2016-12-23 21:30 | 872 | 870
2016-12-23 22:00 | 839 | 837
2016-12-23 22:30 | 823 | 823
2016-12-23 23:00 | 854 | 854
2016-12-23 23:30 | 806 | 805
2016-12-24 | 739 | 736
2016-12-24 00:30 | 680 | 673
2016-12-24 01:00 | 639 | 632
2016-12-24 01:30 | 604 | 595
2016-12-24 02:00 | 578 | 567
2016-12-24 02:30 | 565 | 552
2016-12-24 03:00 | 566 | 552
2016-12-24 03:30 | 562 | 547
2016-12-24 04:00 | 558 | 543
2016-12-24 04:30 | 556 | 540
2016-12-24 05:00 | 559 | 540
2016-12-24 05:30 | 564 | 543
2016-12-24 06:00 | 576 | 558
2016-12-24 06:30 | 605 | 594
2016-12-24 07:00 | 618 | 610
2016-12-24 07:30 | 646 | 643
2016-12-24 08:00 | 674 | 673
2016-12-24 08:30 | 715 | 715
2016-12-24 09:00 | 744 | 744
2016-12-24 09:30 | 754 | 754
2016-12-24 10:00 | 761 | 761
2016-12-24 10:30 | 759 | 759
2016-12-24 11:00 | 763 | 763
2016-12-24 11:30 | 775 | 775
2016-12-24 12:00 | 792 | 792
2016-12-24 12:30 | 800 | 799
2016-12-24 13:00 | 807 | 807
2016-12-24 13:30 | 806 | 806
2016-12-24 14:00 | 821 | 821
2016-12-24 14:30 | 831 | 831
2016-12-24 15:00 | 859 | 858
2016-12-24 15:30 | 887 | 887
2016-12-24 16:00 | 915 | 913
2016-12-24 16:30 | 921 | 920
2016-12-24 17:00 | 940 | 939
2016-12-24 17:30 | 942 | 940
2016-12-24 18:00 | 926 | 923
2016-12-24 18:30 | 921 | 915
2016-12-24 19:00 | 943 | 940
2016-12-24 19:30 | 960 | 957
2016-12-24 20:00 | 955 | 953
2016-12-24 20:30 | 942 | 937
2016-12-24 21:00 | 910 | 903
2016-12-24 21:30 | 877 | 875
2016-12-24 22:00 | 848 | 844
2016-12-24 22:30 | 833 | 830
2016-12-24 23:00 | 821 | 820
2016-12-24 23:30 | 769 | 767
2016-12-25 | 724 | 721
2016-12-25 00:30 | 679 | 673
2016-12-25 01:00 | 650 | 645
2016-12-25 01:30 | 626 | 619
2016-12-25 02:00 | 611 | 601
2016-12-25 02:30 | 601 | 590
2016-12-25 03:00 | 594 | 581
2016-12-25 03:30 | 592 | 577
2016-12-25 04:00 | 587 | 570
2016-12-25 04:30 | 587 | 570
2016-12-25 05:00 | 584 | 565
2016-12-25 05:30 | 588 | 570
2016-12-25 06:00 | 602 | 587
2016-12-25 06:30 | 617 | 606
2016-12-25 07:00 | 637 | 628
2016-12-25 07:30 | 673 | 668
2016-12-25 08:00 | 698 | 696
2016-12-25 08:30 | 733 | 732
2016-12-25 09:00 | 753 | 752
2016-12-25 09:30 | 778 | 777
2016-12-25 10:00 | 792 | 792
2016-12-25 10:30 | 784 | 783
2016-12-25 11:00 | 783 | 782
2016-12-25 11:30 | 769 | 768
2016-12-25 12:00 | 733 | 731
2016-12-25 12:30 | 713 | 711
2016-12-25 13:00 | 685 | 683
2016-12-25 13:30 | 663 | 660
2016-12-25 14:00 | 667 | 664
2016-12-25 14:30 | 679 | 677
2016-12-25 15:00 | 679 | 677
2016-12-25 15:30 | 678 | 676
2016-12-25 16:00 | 683 | 680
2016-12-25 16:30 | 686 | 684
2016-12-25 17:00 | 695 | 692
2016-12-25 17:30 | 697 | 694
2016-12-25 18:00 | 697 | 695
2016-12-25 18:30 | 709 | 706
2016-12-25 19:00 | 735 | 733
2016-12-25 19:30 | 766 | 765
2016-12-25 20:00 | 782 | 781
2016-12-25 20:30 | 787 | 786
2016-12-25 21:00 | 772 | 772
2016-12-25 21:30 | 759 | 759
2016-12-25 22:00 | 752 | 752
2016-12-25 22:30 | 755 | 754
2016-12-25 23:00 | 767 | 766
2016-12-25 23:30 | 721 | 717
2016-12-26 | 680 | 672
2016-12-26 00:30 | 652 | 641
2016-12-26 01:00 | 631 | 617
2016-12-26 01:30 | 608 | 592
2016-12-26 02:00 | 582 | 569
2016-12-26 02:30 | 570 | 556
2016-12-26 03:00 | 563 | 549
2016-12-26 03:30 | 559 | 544
2016-12-26 04:00 | 560 | 545
2016-12-26 04:30 | 569 | 555
2016-12-26 05:00 | 575 | 558
2016-12-26 05:30 | 569 | 550
2016-12-26 06:00 | 574 | 557
2016-12-26 06:30 | 588 | 578
2016-12-26 07:00 | 606 | 600
2016-12-26 07:30 | 643 | 642
2016-12-26 08:00 | 676 | 676
2016-12-26 08:30 | 717 | 717
2016-12-26 09:00 | 730 | 729
2016-12-26 09:30 | 743 | 743
2016-12-26 10:00 | 745 | 745
2016-12-26 10:30 | 771 | 770
2016-12-26 11:00 | 761 | 761
2016-12-26 11:30 | 753 | 753
2016-12-26 12:00 | 748 | 748
2016-12-26 12:30 | 752 | 751
2016-12-26 13:00 | 758 | 756
2016-12-26 13:30 | 770 | 769
2016-12-26 14:00 | 792 | 791
2016-12-26 14:30 | 815 | 813
2016-12-26 15:00 | 812 | 810
2016-12-26 15:30 | 819 | 817
2016-12-26 16:00 | 830 | 828
2016-12-26 16:30 | 839 | 836
2016-12-26 17:00 | 848 | 846
2016-12-26 17:30 | 845 | 842
2016-12-26 18:00 | 844 | 840
2016-12-26 18:30 | 842 | 836
2016-12-26 19:00 | 852 | 850
2016-12-26 19:30 | 870 | 870
2016-12-26 20:00 | 875 | 874
2016-12-26 20:30 | 862 | 861
2016-12-26 21:00 | 833 | 832
2016-12-26 21:30 | 814 | 812
2016-12-26 22:00 | 790 | 787
2016-12-26 22:30 | 770 | 769
2016-12-26 23:00 | 785 | 784
2016-12-26 23:30 | 734 | 732
2016-12-27 | 688 | 683
2016-12-27 00:30 | 658 | 651
2016-12-27 01:00 | 636 | 627
2016-12-27 01:30 | 618 | 606
2016-12-27 02:00 | 602 | 588
2016-12-27 02:30 | 596 | 582
2016-12-27 03:00 | 586 | 573
2016-12-27 03:30 | 581 | 568
2016-12-27 04:00 | 575 | 561
2016-12-27 04:30 | 575 | 561
2016-12-27 05:00 | 577 | 561
2016-12-27 05:30 | 580 | 562
2016-12-27 06:00 | 583 | 567
2016-12-27 06:30 | 602 | 593
2016-12-27 07:00 | 623 | 618
2016-12-27 07:30 | 656 | 655
2016-12-27 08:00 | 681 | 681
2016-12-27 08:30 | 721 | 720
2016-12-27 09:00 | 747 | 746
2016-12-27 09:30 | 761 | 759
2016-12-27 10:00 | 751 | 751
2016-12-27 10:30 | 765 | 765
2016-12-27 11:00 | 766 | 766
2016-12-27 11:30 | 771 | 771
2016-12-27 12:00 | 784 | 784
2016-12-27 12:30 | 784 | 783
2016-12-27 13:00 | 782 | 781
2016-12-27 13:30 | 778 | 777
2016-12-27 14:00 | 795 | 795
2016-12-27 14:30 | 816 | 816
2016-12-27 15:00 | 832 | 832
2016-12-27 15:30 | 859 | 854
2016-12-27 16:00 | 889 | 881
2016-12-27 16:30 | 908 | 899
2016-12-27 17:00 | 916 | 911
2016-12-27 17:30 | 927 | 923
2016-12-27 18:00 | 918 | 912
2016-12-27 18:30 | 911 | 903
2016-12-27 19:00 | 912 | 907
2016-12-27 19:30 | 921 | 918
2016-12-27 20:00 | 920 | 920
2016-12-27 20:30 | 905 | 905
2016-12-27 21:00 | 882 | 882
2016-12-27 21:30 | 858 | 857
2016-12-27 22:00 | 826 | 825
2016-12-27 22:30 | 814 | 813
2016-12-27 23:00 | 818 | 816
2016-12-27 23:30 | 759 | 757
2016-12-28 | 711 | 710
2016-12-28 00:30 | 678 | 675
2016-12-28 01:00 | 653 | 648
2016-12-28 01:30 | 632 | 626
2016-12-28 02:00 | 618 | 611
2016-12-28 02:30 | 611 | 602
2016-12-28 03:00 | 607 | 598
2016-12-28 03:30 | 604 | 594
2016-12-28 04:00 | 603 | 593
2016-12-28 04:30 | 609 | 599
2016-12-28 05:00 | 609 | 599
2016-12-28 05:30 | 624 | 616
2016-12-28 06:00 | 636 | 630
2016-12-28 06:30 | 667 | 665
2016-12-28 07:00 | 698 | 697
2016-12-28 07:30 | 750 | 750
2016-12-28 08:00 | 779 | 779
2016-12-28 08:30 | 808 | 808
2016-12-28 09:00 | 819 | 818
2016-12-28 09:30 | 818 | 818
2016-12-28 10:00 | 820 | 820
2016-12-28 10:30 | 814 | 813
2016-12-28 11:00 | 809 | 809
2016-12-28 11:30 | 805 | 804
2016-12-28 12:00 | 819 | 818
2016-12-28 12:30 | 827 | 827
2016-12-28 13:00 | 842 | 842
2016-12-28 13:30 | 853 | 853
2016-12-28 14:00 | 874 | 874
2016-12-28 14:30 | 889 | 888
2016-12-28 15:00 | 907 | 907
2016-12-28 15:30 | 940 | 939
2016-12-28 16:00 | 961 | 961
2016-12-28 16:30 | 991 | 991
2016-12-28 17:00 | 1006 | 1003
2016-12-28 17:30 | 1015 | 1011
2016-12-28 18:00 | 1000 | 992
2016-12-28 18:30 | 990 | 981
2016-12-28 19:00 | 991 | 983
2016-12-28 19:30 | 990 | 985
2016-12-28 20:00 | 1014 | 1011
2016-12-28 20:30 | 990 | 985
2016-12-28 21:00 | 958 | 951
2016-12-28 21:30 | 916 | 915
2016-12-28 22:00 | 880 | 879
2016-12-28 22:30 | 858 | 858
2016-12-28 23:00 | 830 | 830
2016-12-28 23:30 | 789 | 788
2016-12-29 | 747 | 744
2016-12-29 00:30 | 708 | 703
2016-12-29 01:00 | 679 | 675
2016-12-29 01:30 | 653 | 650
2016-12-29 02:00 | 644 | 639
2016-12-29 02:30 | 630 | 624
2016-12-29 03:00 | 623 | 617
2016-12-29 03:30 | 622 | 616
2016-12-29 04:00 | 619 | 613
2016-12-29 04:30 | 624 | 618
2016-12-29 05:00 | 626 | 619
2016-12-29 05:30 | 638 | 631
2016-12-29 06:00 | 654 | 649
2016-12-29 06:30 | 690 | 686
2016-12-29 07:00 | 725 | 723
2016-12-29 07:30 | 771 | 770
2016-12-29 08:00 | 804 | 804
2016-12-29 08:30 | 840 | 840
2016-12-29 09:00 | 857 | 857
2016-12-29 09:30 | 866 | 865
2016-12-29 10:00 | 868 | 867
2016-12-29 10:30 | 872 | 872
2016-12-29 11:00 | 873 | 872
2016-12-29 11:30 | 876 | 874
2016-12-29 12:00 | 883 | 881
2016-12-29 12:30 | 890 | 889
2016-12-29 13:00 | 896 | 894
2016-12-29 13:30 | 911 | 909
2016-12-29 14:00 | 928 | 928
2016-12-29 14:30 | 918 | 917
2016-12-29 15:00 | 951 | 949
2016-12-29 15:30 | 965 | 961
2016-12-29 16:00 | 993 | 988
2016-12-29 16:30 | 1045 | 1039
2016-12-29 17:00 | 1065 | 1060
2016-12-29 17:30 | 1083 | 1077
2016-12-29 18:00 | 1075 | 1067
2016-12-29 18:30 | 1052 | 1042
2016-12-29 19:00 | 1061 | 1053
2016-12-29 19:30 | 1061 | 1058
2016-12-29 20:00 | 1058 | 1056
2016-12-29 20:30 | 1025 | 1023
2016-12-29 21:00 | 978 | 976
2016-12-29 21:30 | 933 | 931
2016-12-29 22:00 | 894 | 894
2016-12-29 22:30 | 874 | 873
2016-12-29 23:00 | 866 | 864
2016-12-29 23:30 | 812 | 809
2016-12-30 | 758 | 752
2016-12-30 00:30 | 717 | 714
2016-12-30 01:00 | 693 | 690
2016-12-30 01:30 | 667 | 662
2016-12-30 02:00 | 655 | 649
2016-12-30 02:30 | 641 | 634
2016-12-30 03:00 | 630 | 624
2016-12-30 03:30 | 631 | 625
2016-12-30 04:00 | 627 | 621
2016-12-30 04:30 | 630 | 624
2016-12-30 05:00 | 628 | 620
2016-12-30 05:30 | 641 | 634
2016-12-30 06:00 | 658 | 653
2016-12-30 06:30 | 693 | 691
2016-12-30 07:00 | 733 | 731
2016-12-30 07:30 | 776 | 776
2016-12-30 08:00 | 810 | 805
2016-12-30 08:30 | 837 | 834
2016-12-30 09:00 | 863 | 861
2016-12-30 09:30 | 990 | 984
2016-12-30 10:00 | 1027 | 1019
2016-12-30 10:30 | 1044 | 1039
2016-12-30 11:00 | 1005 | 1002
2016-12-30 11:30 | 936 | 934
2016-12-30 12:00 | 951 | 946
2016-12-30 12:30 | 958 | 954
2016-12-30 13:00 | 961 | 957
2016-12-30 13:30 | 966 | 962
2016-12-30 14:00 | 966 | 963
2016-12-30 14:30 | 1030 | 1026
2016-12-30 15:00 | 1060 | 1058
2016-12-30 15:30 | 1092 | 1089
2016-12-30 16:00 | 1122 | 1120
2016-12-30 16:30 | 1141 | 1139
2016-12-30 17:00 | 1192 | 1190
2016-12-30 17:30 | 1173 | 1170
2016-12-30 18:00 | 1150 | 1143
2016-12-30 18:30 | 1116 | 1111
2016-12-30 19:00 | 1103 | 1101
2016-12-30 19:30 | 1110 | 1110
2016-12-30 20:00 | 1106 | 1105
2016-12-30 20:30 | 1081 | 1079
2016-12-30 21:00 | 1052 | 1048
2016-12-30 21:30 | 1007 | 1006
2016-12-30 22:00 | 988 | 984
2016-12-30 22:30 | 959 | 955
2016-12-30 23:00 | 914 | 909
2016-12-30 23:30 | 870 | 864
2016-12-31 | 825 | 822
2016-12-31 00:30 | 780 | 780
2016-12-31 01:00 | 747 | 747
2016-12-31 01:30 | 701 | 700
2016-12-31 02:00 | 676 | 674
2016-12-31 02:30 | 691 | 689
2016-12-31 03:00 | 681 | 679
2016-12-31 03:30 | 674 | 672
2016-12-31 04:00 | 668 | 666
2016-12-31 04:30 | 666 | 664
2016-12-31 05:00 | 667 | 664
2016-12-31 05:30 | 668 | 664
2016-12-31 06:00 | 683 | 679
2016-12-31 06:30 | 706 | 705
2016-12-31 07:00 | 734 | 734
2016-12-31 07:30 | 779 | 779
2016-12-31 08:00 | 819 | 818
2016-12-31 08:30 | 862 | 862
2016-12-31 09:00 | 901 | 900
2016-12-31 09:30 | 929 | 928
2016-12-31 10:00 | 951 | 951
2016-12-31 10:30 | 977 | 977
2016-12-31 11:00 | 987 | 987
2016-12-31 11:30 | 1007 | 1007
2016-12-31 12:00 | 999 | 998
2016-12-31 12:30 | 1042 | 1042
2016-12-31 13:00 | 1056 | 1056
2016-12-31 13:30 | 1057 | 1056
2016-12-31 14:00 | 1114 | 1114
2016-12-31 14:30 | 1136 | 1136
2016-12-31 15:00 | 1173 | 1172
2016-12-31 15:30 | 1176 | 1175
2016-12-31 16:00 | 1199 | 1198
2016-12-31 16:30 | 1230 | 1229
2016-12-31 17:00 | 1249 | 1247
2016-12-31 17:30 | 1232 | 1228
2016-12-31 18:00 | 1206 | 1198
2016-12-31 18:30 | 1167 | 1158
2016-12-31 19:00 | 1149 | 1140
2016-12-31 19:30 | 1123 | 1117
2016-12-31 20:00 | 1123 | 1114
2016-12-31 20:30 | 1089 | 1084
2016-12-31 21:00 | 1042 | 1039
2016-12-31 21:30 | 1018 | 1015
2016-12-31 22:00 | 1006 | 1003
2016-12-31 22:30 | 995 | 990
2016-12-31 23:00 | 993 | 987
2016-12-31 23:30 | 946 | 934
2017-01-01 | 890 | 884
2017-01-01 00:30 | 848 | 840
2017-01-01 01:00 | 833 | 832
2017-01-01 01:30 | 800 | 798
2017-01-01 02:00 | 774 | 770
2017-01-01 02:30 | 749 | 743
2017-01-01 03:00 | 738 | 730
2017-01-01 03:30 | 726 | 717
2017-01-01 04:00 | 715 | 704
2017-01-01 04:30 | 713 | 701
2017-01-01 05:00 | 707 | 693
2017-01-01 05:30 | 698 | 680
2017-01-01 06:00 | 707 | 688
2017-01-01 06:30 | 720 | 705
2017-01-01 07:00 | 732 | 722
2017-01-01 07:30 | 756 | 750
2017-01-01 08:00 | 786 | 784
2017-01-01 08:30 | 827 | 826
2017-01-01 09:00 | 861 | 861
2017-01-01 09:30 | 897 | 896
2017-01-01 10:00 | 939 | 938
2017-01-01 10:30 | 962 | 961
2017-01-01 11:00 | 1000 | 997
2017-01-01 11:30 | 1008 | 1006
2017-01-01 12:00 | 1014 | 1013
2017-01-01 12:30 | 1043 | 1040
2017-01-01 13:00 | 1066 | 1064
2017-01-01 13:30 | 1067 | 1062
2017-01-01 14:00 | 1062 | 1057
2017-01-01 14:30 | 1070 | 1064
2017-01-01 15:00 | 1094 | 1089
2017-01-01 15:30 | 1120 | 1117
2017-01-01 16:00 | 1151 | 1148
2017-01-01 16:30 | 1161 | 1158
2017-01-01 17:00 | 1179 | 1176
2017-01-01 17:30 | 1172 | 1167
2017-01-01 18:00 | 1177 | 1169
2017-01-01 18:30 | 1146 | 1134
2017-01-01 19:00 | 1134 | 1124
2017-01-01 19:30 | 1132 | 1126
2017-01-01 20:00 | 1130 | 1122
2017-01-01 20:30 | 1105 | 1096
2017-01-01 21:00 | 1073 | 1069
2017-01-01 21:30 | 1027 | 1024
2017-01-01 22:00 | 1008 | 1002
2017-01-01 22:30 | 977 | 971
2017-01-01 23:00 | 942 | 937
2017-01-01 23:30 | 893 | 886
2017-01-02 | 848 | 841
2017-01-02 00:30 | 788 | 782
2017-01-02 01:00 | 771 | 763
2017-01-02 01:30 | 749 | 742
2017-01-02 02:00 | 726 | 725
2017-01-02 02:30 | 713 | 712
2017-01-02 03:00 | 709 | 707
2017-01-02 03:30 | 703 | 700
2017-01-02 04:00 | 701 | 698
2017-01-02 04:30 | 695 | 693
2017-01-02 05:00 | 694 | 691
2017-01-02 05:30 | 694 | 690
2017-01-02 06:00 | 709 | 705
2017-01-02 06:30 | 745 | 740
2017-01-02 07:00 | 775 | 770
2017-01-02 07:30 | 822 | 820
2017-01-02 08:00 | 853 | 851
2017-01-02 08:30 | 858 | 857
2017-01-02 09:00 | 899 | 898
2017-01-02 09:30 | 943 | 939
2017-01-02 10:00 | 978 | 972
2017-01-02 10:30 | 972 | 967
2017-01-02 11:00 | 969 | 964
2017-01-02 11:30 | 983 | 978
2017-01-02 12:00 | 1001 | 993
2017-01-02 12:30 | 1049 | 1042
2017-01-02 13:00 | 1042 | 1036
2017-01-02 13:30 | 1039 | 1033
2017-01-02 14:00 | 1055 | 1050
2017-01-02 14:30 | 1077 | 1072
2017-01-02 15:00 | 1137 | 1128
2017-01-02 15:30 | 1154 | 1145
2017-01-02 16:00 | 1175 | 1166
2017-01-02 16:30 | 1162 | 1150
2017-01-02 17:00 | 1162 | 1148
2017-01-02 17:30 | 1155 | 1140
2017-01-02 18:00 | 1154 | 1141
2017-01-02 18:30 | 1136 | 1123
2017-01-02 19:00 | 1142 | 1131
2017-01-02 19:30 | 1132 | 1117
2017-01-02 20:00 | 1096 | 1088
2017-01-02 20:30 | 1057 | 1048
2017-01-02 21:00 | 993 | 988
2017-01-02 21:30 | 951 | 946
2017-01-02 22:00 | 905 | 898
2017-01-02 22:30 | 871 | 867
2017-01-02 23:00 | 865 | 861
2017-01-02 23:30 | 814 | 810
2017-01-03 | 753 | 751
2017-01-03 00:30 | 720 | 715
2017-01-03 01:00 | 694 | 689
2017-01-03 01:30 | 672 | 667
2017-01-03 02:00 | 661 | 655
2017-01-03 02:30 | 652 | 646
2017-01-03 03:00 | 648 | 641
2017-01-03 03:30 | 646 | 639
2017-01-03 04:00 | 643 | 637
2017-01-03 04:30 | 652 | 646
2017-01-03 05:00 | 657 | 651
2017-01-03 05:30 | 676 | 671
2017-01-03 06:00 | 701 | 697
2017-01-03 06:30 | 753 | 752
2017-01-03 07:00 | 799 | 798
2017-01-03 07:30 | 862 | 862
2017-01-03 08:00 | 904 | 904
2017-01-03 08:30 | 948 | 948
2017-01-03 09:00 | 966 | 966
2017-01-03 09:30 | 971 | 971
2017-01-03 10:00 | 987 | 987
2017-01-03 10:30 | 994 | 993
2017-01-03 11:00 | 981 | 979
2017-01-03 11:30 | 979 | 977
2017-01-03 12:00 | 972 | 970
2017-01-03 12:30 | 966 | 963
2017-01-03 13:00 | 963 | 959
2017-01-03 13:30 | 960 | 956
2017-01-03 14:00 | 956 | 952
2017-01-03 14:30 | 957 | 953
2017-01-03 15:00 | 960 | 956
2017-01-03 15:30 | 961 | 957
2017-01-03 16:00 | 966 | 961
2017-01-03 16:30 | 973 | 968
2017-01-03 17:00 | 986 | 981
2017-01-03 17:30 | 983 | 976
2017-01-03 18:00 | 979 | 969
2017-01-03 18:30 | 957 | 951
2017-01-03 19:00 | 965 | 962
2017-01-03 19:30 | 959 | 956
2017-01-03 20:00 | 957 | 954
2017-01-03 20:30 | 928 | 927
2017-01-03 21:00 | 889 | 888
2017-01-03 21:30 | 856 | 854
2017-01-03 22:00 | 827 | 826
2017-01-03 22:30 | 810 | 808
2017-01-03 23:00 | 811 | 809
2017-01-03 23:30 | 763 | 758
2017-01-04 | 717 | 711
2017-01-04 00:30 | 682 | 676
2017-01-04 01:00 | 655 | 648
2017-01-04 01:30 | 638 | 630
2017-01-04 02:00 | 626 | 618
2017-01-04 02:30 | 615 | 607
2017-01-04 03:00 | 611 | 602
2017-01-04 03:30 | 611 | 603
2017-01-04 04:00 | 614 | 607
2017-01-04 04:30 | 619 | 611
2017-01-04 05:00 | 625 | 617
2017-01-04 05:30 | 641 | 634
2017-01-04 06:00 | 664 | 660
2017-01-04 06:30 | 716 | 715
2017-01-04 07:00 | 763 | 760
2017-01-04 07:30 | 803 | 803
2017-01-04 08:00 | 835 | 835
2017-01-04 08:30 | 865 | 865
2017-01-04 09:00 | 879 | 879
2017-01-04 09:30 | 893 | 893
2017-01-04 10:00 | 901 | 901
2017-01-04 10:30 | 899 | 898
2017-01-04 11:00 | 893 | 893
2017-01-04 11:30 | 884 | 884
2017-01-04 12:00 | 875 | 874
2017-01-04 12:30 | 869 | 869
2017-01-04 13:00 | 872 | 872
2017-01-04 13:30 | 881 | 881
2017-01-04 14:00 | 908 | 908
2017-01-04 14:30 | 919 | 919
2017-01-04 15:00 | 950 | 950
2017-01-04 15:30 | 960 | 960
2017-01-04 16:00 | 983 | 982
2017-01-04 16:30 | 1001 | 1000
2017-01-04 17:00 | 1016 | 1015
2017-01-04 17:30 | 1013 | 1010
2017-01-04 18:00 | 1006 | 1000
2017-01-04 18:30 | 983 | 973
2017-01-04 19:00 | 996 | 992
2017-01-04 19:30 | 993 | 993
2017-01-04 20:00 | 989 | 988
2017-01-04 20:30 | 969 | 967
2017-01-04 21:00 | 930 | 928
2017-01-04 21:30 | 897 | 896
2017-01-04 22:00 | 868 | 868
2017-01-04 22:30 | 849 | 848
2017-01-04 23:00 | 847 | 844
2017-01-04 23:30 | 779 | 777
2017-01-05 | 736 | 733
2017-01-05 00:30 | 694 | 690
2017-01-05 01:00 | 675 | 670
2017-01-05 01:30 | 652 | 646
2017-01-05 02:00 | 637 | 630
2017-01-05 02:30 | 632 | 624
2017-01-05 03:00 | 620 | 612
2017-01-05 03:30 | 618 | 610
2017-01-05 04:00 | 618 | 610
2017-01-05 04:30 | 624 | 617
2017-01-05 05:00 | 632 | 625
2017-01-05 05:30 | 649 | 642
2017-01-05 06:00 | 668 | 664
2017-01-05 06:30 | 712 | 710
2017-01-05 07:00 | 753 | 752
2017-01-05 07:30 | 807 | 806
2017-01-05 08:00 | 843 | 841
2017-01-05 08:30 | 889 | 888
2017-01-05 09:00 | 916 | 913
2017-01-05 09:30 | 931 | 927
2017-01-05 10:00 | 936 | 933
2017-01-05 10:30 | 954 | 953
2017-01-05 11:00 | 958 | 956
2017-01-05 11:30 | 937 | 935
2017-01-05 12:00 | 932 | 930
2017-01-05 12:30 | 950 | 949
2017-01-05 13:00 | 961 | 959
2017-01-05 13:30 | 943 | 941
2017-01-05 14:00 | 946 | 944
2017-01-05 14:30 | 960 | 959
2017-01-05 15:00 | 991 | 990
2017-01-05 15:30 | 994 | 993
2017-01-05 16:00 | 1010 | 1009
2017-01-05 16:30 | 1024 | 1023
2017-01-05 17:00 | 1029 | 1028
2017-01-05 17:30 | 1038 | 1036
2017-01-05 18:00 | 1032 | 1029
2017-01-05 18:30 | 1021 | 1017
2017-01-05 19:00 | 1045 | 1041
2017-01-05 19:30 | 1047 | 1044
2017-01-05 20:00 | 1051 | 1048
2017-01-05 20:30 | 1033 | 1029
2017-01-05 21:00 | 989 | 987
2017-01-05 21:30 | 939 | 936
2017-01-05 22:00 | 898 | 894
2017-01-05 22:30 | 871 | 868
2017-01-05 23:00 | 867 | 863
2017-01-05 23:30 | 798 | 792
2017-01-06 | 747 | 738
2017-01-06 00:30 | 707 | 702
2017-01-06 01:00 | 684 | 679
2017-01-06 01:30 | 661 | 655
2017-01-06 02:00 | 645 | 638
2017-01-06 02:30 | 639 | 631
2017-01-06 03:00 | 627 | 618
2017-01-06 03:30 | 626 | 617
2017-01-06 04:00 | 631 | 622
2017-01-06 04:30 | 637 | 629
2017-01-06 05:00 | 643 | 634
2017-01-06 05:30 | 658 | 651
2017-01-06 06:00 | 677 | 672
2017-01-06 06:30 | 717 | 715
2017-01-06 07:00 | 767 | 766
2017-01-06 07:30 | 822 | 820
2017-01-06 08:00 | 859 | 859
2017-01-06 08:30 | 905 | 902
2017-01-06 09:00 | 934 | 931
2017-01-06 09:30 | 944 | 939
2017-01-06 10:00 | 950 | 947
2017-01-06 10:30 | 959 | 957
2017-01-06 11:00 | 944 | 941
2017-01-06 11:30 | 942 | 940
2017-01-06 12:00 | 960 | 959
2017-01-06 12:30 | 962 | 960
2017-01-06 13:00 | 964 | 962
2017-01-06 13:30 | 971 | 970
2017-01-06 14:00 | 989 | 988
2017-01-06 14:30 | 987 | 986
2017-01-06 15:00 | 1028 | 1027
2017-01-06 15:30 | 1037 | 1035
2017-01-06 16:00 | 1052 | 1051
2017-01-06 16:30 | 1061 | 1060
2017-01-06 17:00 | 1079 | 1075
2017-01-06 17:30 | 1072 | 1063
2017-01-06 18:00 | 1044 | 1031
2017-01-06 18:30 | 1021 | 1011
2017-01-06 19:00 | 1032 | 1023
2017-01-06 19:30 | 1026 | 1022
2017-01-06 20:00 | 1023 | 1018
2017-01-06 20:30 | 995 | 993
2017-01-06 21:00 | 956 | 955
2017-01-06 21:30 | 923 | 922
2017-01-06 22:00 | 894 | 892
2017-01-06 22:30 | 876 | 870
2017-01-06 23:00 | 872 | 867
2017-01-06 23:30 | 813 | 809
2017-01-07 | 758 | 754
2017-01-07 00:30 | 711 | 708
2017-01-07 01:00 | 692 | 688
2017-01-07 01:30 | 668 | 662
2017-01-07 02:00 | 656 | 649
2017-01-07 02:30 | 641 | 633
2017-01-07 03:00 | 633 | 626
2017-01-07 03:30 | 631 | 623
2017-01-07 04:00 | 624 | 616
2017-01-07 04:30 | 625 | 617
2017-01-07 05:00 | 628 | 619
2017-01-07 05:30 | 630 | 620
2017-01-07 06:00 | 641 | 631
2017-01-07 06:30 | 660 | 654
2017-01-07 07:00 | 676 | 672
2017-01-07 07:30 | 701 | 700
2017-01-07 08:00 | 714 | 713
2017-01-07 08:30 | 746 | 745
2017-01-07 09:00 | 786 | 786
2017-01-07 09:30 | 800 | 800
2017-01-07 10:00 | 799 | 799
2017-01-07 10:30 | 794 | 794
2017-01-07 11:00 | 786 | 786
2017-01-07 11:30 | 787 | 787
2017-01-07 12:00 | 795 | 795
2017-01-07 12:30 | 794 | 793
2017-01-07 13:00 | 784 | 783
2017-01-07 13:30 | 775 | 773
2017-01-07 14:00 | 759 | 757
2017-01-07 14:30 | 771 | 770
2017-01-07 15:00 | 786 | 784
2017-01-07 15:30 | 802 | 800
2017-01-07 16:00 | 831 | 830
2017-01-07 16:30 | 861 | 860
2017-01-07 17:00 | 892 | 891
2017-01-07 17:30 | 899 | 897
2017-01-07 18:00 | 902 | 900
2017-01-07 18:30 | 907 | 903
2017-01-07 19:00 | 918 | 914
2017-01-07 19:30 | 934 | 932
2017-01-07 20:00 | 938 | 936
2017-01-07 20:30 | 922 | 918
2017-01-07 21:00 | 889 | 885
2017-01-07 21:30 | 857 | 854
2017-01-07 22:00 | 834 | 829
2017-01-07 22:30 | 823 | 817
2017-01-07 23:00 | 826 | 821
2017-01-07 23:30 | 773 | 768
2017-01-08 | 725 | 718
2017-01-08 00:30 | 682 | 677
2017-01-08 01:00 | 662 | 655
2017-01-08 01:30 | 638 | 629
2017-01-08 02:00 | 621 | 610
2017-01-08 02:30 | 611 | 599
2017-01-08 03:00 | 604 | 591
2017-01-08 03:30 | 603 | 590
2017-01-08 04:00 | 600 | 586
2017-01-08 04:30 | 596 | 582
2017-01-08 05:00 | 597 | 582
2017-01-08 05:30 | 598 | 579
2017-01-08 06:00 | 599 | 579
2017-01-08 06:30 | 606 | 590
2017-01-08 07:00 | 619 | 606
2017-01-08 07:30 | 641 | 634
2017-01-08 08:00 | 659 | 655
2017-01-08 08:30 | 692 | 691
2017-01-08 09:00 | 705 | 704
2017-01-08 09:30 | 716 | 716
2017-01-08 10:00 | 717 | 717
2017-01-08 10:30 | 720 | 720
2017-01-08 11:00 | 715 | 715
2017-01-08 11:30 | 719 | 719
2017-01-08 12:00 | 724 | 724
2017-01-08 12:30 | 725 | 725
2017-01-08 13:00 | 736 | 736
2017-01-08 13:30 | 742 | 742
2017-01-08 14:00 | 751 | 751
2017-01-08 14:30 | 763 | 763
2017-01-08 15:00 | 778 | 778
2017-01-08 15:30 | 811 | 811
2017-01-08 16:00 | 843 | 841
2017-01-08 16:30 | 867 | 863
2017-01-08 17:00 | 892 | 889
2017-01-08 17:30 | 901 | 897
2017-01-08 18:00 | 910 | 906
2017-01-08 18:30 | 921 | 917
2017-01-08 19:00 | 931 | 926
2017-01-08 19:30 | 938 | 935
2017-01-08 20:00 | 940 | 937
2017-01-08 20:30 | 920 | 916
2017-01-08 21:00 | 878 | 876
2017-01-08 21:30 | 849 | 847
2017-01-08 22:00 | 814 | 813
2017-01-08 22:30 | 794 | 793
2017-01-08 23:00 | 792 | 790
2017-01-08 23:30 | 746 | 742
2017-01-09 | 699 | 693
2017-01-09 00:30 | 660 | 651
2017-01-09 01:00 | 648 | 637
2017-01-09 01:30 | 629 | 617
2017-01-09 02:00 | 614 | 601
2017-01-09 02:30 | 609 | 594
2017-01-09 03:00 | 601 | 585
2017-01-09 03:30 | 603 | 588
2017-01-09 04:00 | 600 | 586
2017-01-09 04:30 | 610 | 598
2017-01-09 05:00 | 617 | 606
2017-01-09 05:30 | 645 | 634
2017-01-09 06:00 | 666 | 659
2017-01-09 06:30 | 718 | 716
2017-01-09 07:00 | 765 | 764
2017-01-09 07:30 | 817 | 817
2017-01-09 08:00 | 856 | 856
2017-01-09 08:30 | 896 | 895
2017-01-09 09:00 | 933 | 931
2017-01-09 09:30 | 948 | 947
2017-01-09 10:00 | 952 | 951
2017-01-09 10:30 | 965 | 965
2017-01-09 11:00 | 968 | 968
2017-01-09 11:30 | 986 | 985
2017-01-09 12:00 | 988 | 987
2017-01-09 12:30 | 998 | 998
2017-01-09 13:00 | 1016 | 1016
2017-01-09 13:30 | 1015 | 1015
2017-01-09 14:00 | 1034 | 1034
2017-01-09 14:30 | 1041 | 1040
2017-01-09 15:00 | 1059 | 1058
2017-01-09 15:30 | 1084 | 1084
2017-01-09 16:00 | 1109 | 1108
2017-01-09 16:30 | 1125 | 1119
2017-01-09 17:00 | 1138 | 1132
2017-01-09 17:30 | 1131 | 1126
2017-01-09 18:00 | 1116 | 1110
2017-01-09 18:30 | 1094 | 1088
2017-01-09 19:00 | 1096 | 1092
2017-01-09 19:30 | 1107 | 1104
2017-01-09 20:00 | 1097 | 1095
2017-01-09 20:30 | 1067 | 1065
2017-01-09 21:00 | 1019 | 1018
2017-01-09 21:30 | 975 | 974
2017-01-09 22:00 | 943 | 940
2017-01-09 22:30 | 905 | 902
2017-01-09 23:00 | 899 | 897
2017-01-09 23:30 | 829 | 823
2017-01-10 | 776 | 770
2017-01-10 00:30 | 737 | 729
2017-01-10 01:00 | 708 | 704
2017-01-10 01:30 | 687 | 682
2017-01-10 02:00 | 672 | 666
2017-01-10 02:30 | 659 | 652
2017-01-10 03:00 | 653 | 645
2017-01-10 03:30 | 642 | 636
2017-01-10 04:00 | 647 | 640
2017-01-10 04:30 | 652 | 646
2017-01-10 05:00 | 662 | 656
2017-01-10 05:30 | 684 | 680
2017-01-10 06:00 | 711 | 706
2017-01-10 06:30 | 773 | 768
2017-01-10 07:00 | 836 | 827
2017-01-10 07:30 | 905 | 902
2017-01-10 08:00 | 948 | 942
2017-01-10 08:30 | 982 | 980
2017-01-10 09:00 | 1001 | 1000
2017-01-10 09:30 | 1019 | 1018
2017-01-10 10:00 | 1026 | 1025
2017-01-10 10:30 | 1019 | 1015
2017-01-10 11:00 | 1040 | 1035
2017-01-10 11:30 | 1049 | 1045
2017-01-10 12:00 | 1062 | 1058
2017-01-10 12:30 | 1069 | 1066
2017-01-10 13:00 | 1080 | 1078
2017-01-10 13:30 | 1096 | 1095
2017-01-10 14:00 | 1108 | 1108
2017-01-10 14:30 | 1131 | 1131
2017-01-10 15:00 | 1158 | 1158
2017-01-10 15:30 | 1183 | 1183
2017-01-10 16:00 | 1222 | 1219
2017-01-10 16:30 | 1243 | 1240
2017-01-10 17:00 | 1258 | 1255
2017-01-10 17:30 | 1250 | 1244
2017-01-10 18:00 | 1215 | 1204
2017-01-10 18:30 | 1179 | 1166
2017-01-10 19:00 | 1172 | 1162
2017-01-10 19:30 | 1178 | 1169
2017-01-10 20:00 | 1159 | 1155
2017-01-10 20:30 | 1127 | 1122
2017-01-10 21:00 | 1074 | 1072
2017-01-10 21:30 | 1023 | 1019
2017-01-10 22:00 | 984 | 978
2017-01-10 22:30 | 943 | 938
2017-01-10 23:00 | 909 | 904
2017-01-10 23:30 | 845 | 840
2017-01-11 | 784 | 781
2017-01-11 00:30 | 740 | 738
2017-01-11 01:00 | 712 | 711
2017-01-11 01:30 | 689 | 686
2017-01-11 02:00 | 678 | 675
2017-01-11 02:30 | 674 | 670
2017-01-11 03:00 | 661 | 657
2017-01-11 03:30 | 662 | 659
2017-01-11 04:00 | 659 | 656
2017-01-11 04:30 | 668 | 666
2017-01-11 05:00 | 677 | 675
2017-01-11 05:30 | 698 | 696
2017-01-11 06:00 | 732 | 731
2017-01-11 06:30 | 800 | 800
2017-01-11 07:00 | 863 | 862
2017-01-11 07:30 | 931 | 929
2017-01-11 08:00 | 977 | 974
2017-01-11 08:30 | 1016 | 1014
2017-01-11 09:00 | 1055 | 1054
2017-01-11 09:30 | 1087 | 1086
2017-01-11 10:00 | 1104 | 1098
2017-01-11 10:30 | 1122 | 1117
2017-01-11 11:00 | 1117 | 1112
2017-01-11 11:30 | 1118 | 1115
2017-01-11 12:00 | 1147 | 1145
2017-01-11 12:30 | 1155 | 1154
2017-01-11 13:00 | 1193 | 1191
2017-01-11 13:30 | 1230 | 1230
2017-01-11 14:00 | 1275 | 1275
2017-01-11 14:30 | 1313 | 1313
2017-01-11 15:00 | 1337 | 1336
2017-01-11 15:30 | 1367 | 1365
2017-01-11 16:00 | 1387 | 1385
2017-01-11 16:30 | 1421 | 1419
2017-01-11 17:00 | 1429 | 1428
2017-01-11 17:30 | 1411 | 1405
2017-01-11 18:00 | 1370 | 1358
2017-01-11 18:30 | 1296 | 1280
2017-01-11 19:00 | 1265 | 1256
2017-01-11 19:30 | 1258 | 1254
2017-01-11 20:00 | 1240 | 1237
2017-01-11 20:30 | 1187 | 1183
2017-01-11 21:00 | 1122 | 1116
2017-01-11 21:30 | 1071 | 1063
2017-01-11 22:00 | 1013 | 1009
2017-01-11 22:30 | 962 | 958
2017-01-11 23:00 | 954 | 949
2017-01-11 23:30 | 908 | 902
2017-01-12 | 833 | 828
2017-01-12 00:30 | 785 | 782
2017-01-12 01:00 | 759 | 759
2017-01-12 01:30 | 733 | 732
2017-01-12 02:00 | 714 | 713
2017-01-12 02:30 | 704 | 702
2017-01-12 03:00 | 694 | 693
2017-01-12 03:30 | 691 | 690
2017-01-12 04:00 | 689 | 687
2017-01-12 04:30 | 694 | 692
2017-01-12 05:00 | 704 | 702
2017-01-12 05:30 | 724 | 723
2017-01-12 06:00 | 759 | 758
2017-01-12 06:30 | 823 | 823
2017-01-12 07:00 | 883 | 883
2017-01-12 07:30 | 969 | 968
2017-01-12 08:00 | 1023 | 1019
2017-01-12 08:30 | 1084 | 1083
2017-01-12 09:00 | 1119 | 1118
2017-01-12 09:30 | 1134 | 1134
2017-01-12 10:00 | 1155 | 1155
2017-01-12 10:30 | 1203 | 1203
2017-01-12 11:00 | 1194 | 1194
2017-01-12 11:30 | 1228 | 1228
2017-01-12 12:00 | 1259 | 1259
2017-01-12 12:30 | 1289 | 1289
2017-01-12 13:00 | 1309 | 1309
2017-01-12 13:30 | 1364 | 1363
2017-01-12 14:00 | 1366 | 1366
2017-01-12 14:30 | 1359 | 1359
2017-01-12 15:00 | 1371 | 1371
2017-01-12 15:30 | 1390 | 1390
2017-01-12 16:00 | 1419 | 1419
2017-01-12 16:30 | 1463 | 1463
2017-01-12 17:00 | 1467 | 1467
2017-01-12 17:30 | 1456 | 1455
2017-01-12 18:00 | 1419 | 1416
2017-01-12 18:30 | 1376 | 1374
2017-01-12 19:00 | 1395 | 1394
2017-01-12 19:30 | 1399 | 1398
2017-01-12 20:00 | 1383 | 1383
2017-01-12 20:30 | 1336 | 1336
2017-01-12 21:00 | 1252 | 1251
2017-01-12 21:30 | 1183 | 1182
2017-01-12 22:00 | 1124 | 1123
2017-01-12 22:30 | 1061 | 1058
2017-01-12 23:00 | 1031 | 1027
2017-01-12 23:30 | 947 | 945
2017-01-13 | 901 | 896
2017-01-13 00:30 | 845 | 838
2017-01-13 01:00 | 815 | 806
2017-01-13 01:30 | 791 | 786
2017-01-13 02:00 | 768 | 761
2017-01-13 02:30 | 753 | 746
2017-01-13 03:00 | 738 | 736
2017-01-13 03:30 | 739 | 738
2017-01-13 04:00 | 733 | 733
2017-01-13 04:30 | 738 | 737
2017-01-13 05:00 | 754 | 752
2017-01-13 05:30 | 775 | 771
2017-01-13 06:00 | 809 | 805
2017-01-13 06:30 | 860 | 857
2017-01-13 07:00 | 927 | 925
2017-01-13 07:30 | 1053 | 1051
2017-01-13 08:00 | 1093 | 1092
2017-01-13 08:30 | 1120 | 1120
2017-01-13 09:00 | 1161 | 1160
2017-01-13 09:30 | 1200 | 1199
2017-01-13 10:00 | 1240 | 1238
2017-01-13 10:30 | 1244 | 1242
2017-01-13 11:00 | 1254 | 1252
2017-01-13 11:30 | 1279 | 1276
2017-01-13 12:00 | 1287 | 1284
2017-01-13 12:30 | 1290 | 1287
2017-01-13 13:00 | 1305 | 1303
2017-01-13 13:30 | 1340 | 1339
2017-01-13 14:00 | 1387 | 1386
2017-01-13 14:30 | 1412 | 1411
2017-01-13 15:00 | 1448 | 1448
2017-01-13 15:30 | 1462 | 1461
2017-01-13 16:00 | 1489 | 1488
2017-01-13 16:30 | 1508 | 1507
2017-01-13 17:00 | 1532 | 1532
2017-01-13 17:30 | 1508 | 1508
2017-01-13 18:00 | 1467 | 1465
2017-01-13 18:30 | 1440 | 1439
2017-01-13 19:00 | 1406 | 1405
2017-01-13 19:30 | 1420 | 1420
2017-01-13 20:00 | 1410 | 1410
2017-01-13 20:30 | 1383 | 1383
2017-01-13 21:00 | 1335 | 1333
2017-01-13 21:30 | 1283 | 1282
2017-01-13 22:00 | 1154 | 1154
2017-01-13 22:30 | 1085 | 1084
2017-01-13 23:00 | 1066 | 1065
2017-01-13 23:30 | 1000 | 1000
2017-01-14 | 927 | 927
2017-01-14 00:30 | 835 | 834
2017-01-14 01:00 | 794 | 793
2017-01-14 01:30 | 770 | 768
2017-01-14 02:00 | 789 | 787
2017-01-14 02:30 | 792 | 791
2017-01-14 03:00 | 769 | 767
2017-01-14 03:30 | 761 | 759
2017-01-14 04:00 | 749 | 746
2017-01-14 04:30 | 745 | 741
2017-01-14 05:00 | 738 | 734
2017-01-14 05:30 | 746 | 741
2017-01-14 06:00 | 768 | 764
2017-01-14 06:30 | 801 | 800
2017-01-14 07:00 | 834 | 834
2017-01-14 07:30 | 930 | 930
2017-01-14 08:00 | 953 | 953
2017-01-14 08:30 | 1003 | 1003
2017-01-14 09:00 | 1017 | 1017
2017-01-14 09:30 | 1068 | 1066
2017-01-14 10:00 | 1092 | 1088
2017-01-14 10:30 | 1148 | 1146
2017-01-14 11:00 | 1170 | 1169
2017-01-14 11:30 | 1187 | 1186
2017-01-14 12:00 | 1217 | 1216
2017-01-14 12:30 | 1261 | 1260
2017-01-14 13:00 | 1279 | 1279
2017-01-14 13:30 | 1287 | 1287
2017-01-14 14:00 | 1328 | 1328
2017-01-14 14:30 | 1344 | 1344
2017-01-14 15:00 | 1374 | 1373
2017-01-14 15:30 | 1389 | 1388
2017-01-14 16:00 | 1418 | 1418
2017-01-14 16:30 | 1440 | 1440
2017-01-14 17:00 | 1458 | 1458
2017-01-14 17:30 | 1455 | 1455
2017-01-14 18:00 | 1435 | 1435
2017-01-14 18:30 | 1412 | 1411
2017-01-14 19:00 | 1403 | 1401
2017-01-14 19:30 | 1406 | 1405
2017-01-14 20:00 | 1368 | 1365
2017-01-14 20:30 | 1372 | 1367
2017-01-14 21:00 | 1320 | 1316
2017-01-14 21:30 | 1227 | 1222
2017-01-14 22:00 | 1175 | 1170
2017-01-14 22:30 | 1120 | 1111
2017-01-14 23:00 | 1098 | 1087
2017-01-14 23:30 | 1014 | 1001
2017-01-15 | 953 | 942
2017-01-15 00:30 | 894 | 885
2017-01-15 01:00 | 832 | 827
2017-01-15 01:30 | 832 | 825
2017-01-15 02:00 | 817 | 808
2017-01-15 02:30 | 812 | 802
2017-01-15 03:00 | 800 | 789
2017-01-15 03:30 | 788 | 782
2017-01-15 04:00 | 776 | 769
2017-01-15 04:30 | 761 | 754
2017-01-15 05:00 | 754 | 747
2017-01-15 05:30 | 757 | 750
2017-01-15 06:00 | 755 | 746
2017-01-15 06:30 | 771 | 763
2017-01-15 07:00 | 783 | 775
2017-01-15 07:30 | 808 | 803
2017-01-15 08:00 | 827 | 824
2017-01-15 08:30 | 846 | 844
2017-01-15 09:00 | 863 | 862
2017-01-15 09:30 | 924 | 923
2017-01-15 10:00 | 971 | 966
2017-01-15 10:30 | 957 | 953
2017-01-15 11:00 | 959 | 956
2017-01-15 11:30 | 984 | 983
2017-01-15 12:00 | 1020 | 1020
2017-01-15 12:30 | 1081 | 1081
2017-01-15 13:00 | 1103 | 1103
2017-01-15 13:30 | 1079 | 1079
2017-01-15 14:00 | 1055 | 1055
2017-01-15 14:30 | 1070 | 1070
2017-01-15 15:00 | 1092 | 1092
2017-01-15 15:30 | 1140 | 1140
2017-01-15 16:00 | 1137 | 1137
2017-01-15 16:30 | 1120 | 1120
2017-01-15 17:00 | 1123 | 1123
2017-01-15 17:30 | 1125 | 1125
2017-01-15 18:00 | 1129 | 1129
2017-01-15 18:30 | 1114 | 1112
2017-01-15 19:00 | 1121 | 1120
2017-01-15 19:30 | 1118 | 1117
2017-01-15 20:00 | 1086 | 1083
2017-01-15 20:30 | 1073 | 1068
2017-01-15 21:00 | 1028 | 1026
2017-01-15 21:30 | 993 | 990
2017-01-15 22:00 | 954 | 951
2017-01-15 22:30 | 915 | 913
2017-01-15 23:00 | 905 | 902
2017-01-15 23:30 | 838 | 835
2017-01-16 | 787 | 787
2017-01-16 00:30 | 750 | 749
2017-01-16 01:00 | 730 | 728
2017-01-16 01:30 | 710 | 705
2017-01-16 02:00 | 689 | 683
2017-01-16 02:30 | 678 | 671
2017-01-16 03:00 | 666 | 659
2017-01-16 03:30 | 670 | 663
2017-01-16 04:00 | 665 | 658
2017-01-16 04:30 | 673 | 666
2017-01-16 05:00 | 680 | 674
2017-01-16 05:30 | 702 | 698
2017-01-16 06:00 | 739 | 736
2017-01-16 06:30 | 821 | 820
2017-01-16 07:00 | 890 | 890
2017-01-16 07:30 | 949 | 949
2017-01-16 08:00 | 992 | 992
2017-01-16 08:30 | 1047 | 1047
2017-01-16 09:00 | 1071 | 1071
2017-01-16 09:30 | 1085 | 1085
2017-01-16 10:00 | 1091 | 1091
2017-01-16 10:30 | 1105 | 1104
2017-01-16 11:00 | 1119 | 1116
2017-01-16 11:30 | 1124 | 1121
2017-01-16 12:00 | 1132 | 1129
2017-01-16 12:30 | 1149 | 1145
2017-01-16 13:00 | 1169 | 1164
2017-01-16 13:30 | 1186 | 1186
2017-01-16 14:00 | 1212 | 1212
2017-01-16 14:30 | 1232 | 1231
2017-01-16 15:00 | 1251 | 1251
2017-01-16 15:30 | 1278 | 1277
2017-01-16 16:00 | 1305 | 1304
2017-01-16 16:30 | 1323 | 1322
2017-01-16 17:00 | 1346 | 1346
2017-01-16 17:30 | 1328 | 1328
2017-01-16 18:00 | 1297 | 1295
2017-01-16 18:30 | 1268 | 1263
2017-01-16 19:00 | 1279 | 1275
2017-01-16 19:30 | 1275 | 1272
2017-01-16 20:00 | 1271 | 1268
2017-01-16 20:30 | 1232 | 1226
2017-01-16 21:00 | 1158 | 1156
2017-01-16 21:30 | 1101 | 1097
2017-01-16 22:00 | 1048 | 1040
2017-01-16 22:30 | 990 | 988
2017-01-16 23:00 | 960 | 958
2017-01-16 23:30 | 877 | 874
2017-01-17 | 815 | 810
2017-01-17 00:30 | 782 | 774
2017-01-17 01:00 | 758 | 753
2017-01-17 01:30 | 730 | 724
2017-01-17 02:00 | 708 | 701
2017-01-17 02:30 | 692 | 684
2017-01-17 03:00 | 680 | 672
2017-01-17 03:30 | 677 | 669
2017-01-17 04:00 | 683 | 676
2017-01-17 04:30 | 684 | 679
2017-01-17 05:00 | 675 | 671
2017-01-17 05:30 | 728 | 725
2017-01-17 06:00 | 765 | 764
2017-01-17 06:30 | 835 | 835
2017-01-17 07:00 | 913 | 911
2017-01-17 07:30 | 983 | 981
2017-01-17 08:00 | 1027 | 1025
2017-01-17 08:30 | 1070 | 1069
2017-01-17 09:00 | 1093 | 1091
2017-01-17 09:30 | 1093 | 1091
2017-01-17 10:00 | 1117 | 1117
2017-01-17 10:30 | 1146 | 1144
2017-01-17 11:00 | 1150 | 1149
2017-01-17 11:30 | 1170 | 1168
2017-01-17 12:00 | 1175 | 1172
2017-01-17 12:30 | 1205 | 1202
2017-01-17 13:00 | 1223 | 1221
2017-01-17 13:30 | 1257 | 1255
2017-01-17 14:00 | 1311 | 1310
2017-01-17 14:30 | 1329 | 1325
2017-01-17 15:00 | 1322 | 1317
2017-01-17 15:30 | 1344 | 1340
2017-01-17 16:00 | 1376 | 1373
2017-01-17 16:30 | 1394 | 1392
2017-01-17 17:00 | 1406 | 1404
2017-01-17 17:30 | 1423 | 1418
2017-01-17 18:00 | 1388 | 1380
2017-01-17 18:30 | 1339 | 1327
2017-01-17 19:00 | 1333 | 1325
2017-01-17 19:30 | 1315 | 1310
2017-01-17 20:00 | 1289 | 1288
2017-01-17 20:30 | 1260 | 1256
2017-01-17 21:00 | 1191 | 1189
2017-01-17 21:30 | 1120 | 1117
2017-01-17 22:00 | 1048 | 1044
2017-01-17 22:30 | 996 | 995
2017-01-17 23:00 | 975 | 973
2017-01-17 23:30 | 897 | 897
2017-01-18 | 833 | 832
2017-01-18 00:30 | 796 | 794
2017-01-18 01:00 | 757 | 754
2017-01-18 01:30 | 738 | 733
2017-01-18 02:00 | 715 | 714
2017-01-18 02:30 | 703 | 702
2017-01-18 03:00 | 697 | 696
2017-01-18 03:30 | 696 | 695
2017-01-18 04:00 | 698 | 697
2017-01-18 04:30 | 704 | 704
2017-01-18 05:00 | 719 | 718
2017-01-18 05:30 | 738 | 737
2017-01-18 06:00 | 775 | 774
2017-01-18 06:30 | 846 | 845
2017-01-18 07:00 | 916 | 915
2017-01-18 07:30 | 979 | 978
2017-01-18 08:00 | 1032 | 1030
2017-01-18 08:30 | 1059 | 1057
2017-01-18 09:00 | 1089 | 1087
2017-01-18 09:30 | 1111 | 1109
2017-01-18 10:00 | 1121 | 1119
2017-01-18 10:30 | 1153 | 1151
2017-01-18 11:00 | 1181 | 1179
2017-01-18 11:30 | 1207 | 1207
2017-01-18 12:00 | 1248 | 1248
2017-01-18 12:30 | 1276 | 1276
2017-01-18 13:00 | 1325 | 1324
2017-01-18 13:30 | 1384 | 1383
2017-01-18 14:00 | 1433 | 1432
2017-01-18 14:30 | 1481 | 1480
2017-01-18 15:00 | 1529 | 1529
2017-01-18 15:30 | 1565 | 1565
2017-01-18 16:00 | 1611 | 1611
2017-01-18 16:30 | 1627 | 1627
2017-01-18 17:00 | 1645 | 1645
2017-01-18 17:30 | 1661 | 1660
2017-01-18 18:00 | 1641 | 1639
2017-01-18 18:30 | 1597 | 1592
2017-01-18 19:00 | 1579 | 1576
2017-01-18 19:30 | 1561 | 1559
2017-01-18 20:00 | 1532 | 1530
2017-01-18 20:30 | 1480 | 1475
2017-01-18 21:00 | 1385 | 1383
2017-01-18 21:30 | 1271 | 1268
2017-01-18 22:00 | 1242 | 1239
2017-01-18 22:30 | 1203 | 1202
2017-01-18 23:00 | 1167 | 1165
2017-01-18 23:30 | 1072 | 1072
2017-01-19 | 982 | 981
2017-01-19 00:30 | 939 | 938
2017-01-19 01:00 | 913 | 911
2017-01-19 01:30 | 890 | 888
2017-01-19 02:00 | 864 | 864
2017-01-19 02:30 | 787 | 787
2017-01-19 03:00 | 777 | 777
2017-01-19 03:30 | 775 | 774
2017-01-19 04:00 | 771 | 770
2017-01-19 04:30 | 780 | 780
2017-01-19 05:00 | 791 | 790
2017-01-19 05:30 | 813 | 813
2017-01-19 06:00 | 850 | 849
2017-01-19 06:30 | 927 | 925
2017-01-19 07:00 | 1000 | 998
2017-01-19 07:30 | 1072 | 1070
2017-01-19 08:00 | 1109 | 1107
2017-01-19 08:30 | 1150 | 1148
2017-01-19 09:00 | 1167 | 1167
2017-01-19 09:30 | 1179 | 1179
2017-01-19 10:00 | 1210 | 1209
2017-01-19 10:30 | 1213 | 1213
2017-01-19 11:00 | 1209 | 1207
2017-01-19 11:30 | 1251 | 1250
2017-01-19 12:00 | 1242 | 1240
2017-01-19 12:30 | 1223 | 1221
2017-01-19 13:00 | 1194 | 1191
2017-01-19 13:30 | 1188 | 1184
2017-01-19 14:00 | 1212 | 1209
2017-01-19 14:30 | 1215 | 1211
2017-01-19 15:00 | 1213 | 1210
2017-01-19 15:30 | 1222 | 1219
2017-01-19 16:00 | 1225 | 1221
2017-01-19 16:30 | 1228 | 1224
2017-01-19 17:00 | 1226 | 1223
2017-01-19 17:30 | 1235 | 1229
2017-01-19 18:00 | 1217 | 1208
2017-01-19 18:30 | 1191 | 1179
2017-01-19 19:00 | 1173 | 1162
2017-01-19 19:30 | 1177 | 1169
2017-01-19 20:00 | 1161 | 1157
2017-01-19 20:30 | 1127 | 1120
2017-01-19 21:00 | 1083 | 1080
2017-01-19 21:30 | 1035 | 1028
2017-01-19 22:00 | 997 | 993
2017-01-19 22:30 | 967 | 962
2017-01-19 23:00 | 943 | 936
2017-01-19 23:30 | 882 | 876
2017-01-20 | 831 | 826
2017-01-20 00:30 | 793 | 787
2017-01-20 01:00 | 755 | 753
2017-01-20 01:30 | 732 | 730
2017-01-20 02:00 | 714 | 711
2017-01-20 02:30 | 705 | 702
2017-01-20 03:00 | 699 | 697
2017-01-20 03:30 | 699 | 697
2017-01-20 04:00 | 699 | 697
2017-01-20 04:30 | 709 | 708
2017-01-20 05:00 | 720 | 720
2017-01-20 05:30 | 739 | 739
2017-01-20 06:00 | 782 | 782
2017-01-20 06:30 | 849 | 848
2017-01-20 07:00 | 933 | 933
2017-01-20 07:30 | 1001 | 1001
2017-01-20 08:00 | 1027 | 1027
2017-01-20 08:30 | 1062 | 1062
2017-01-20 09:00 | 1065 | 1065
2017-01-20 09:30 | 1056 | 1055
2017-01-20 10:00 | 1104 | 1103
2017-01-20 10:30 | 1121 | 1119
2017-01-20 11:00 | 1150 | 1148
2017-01-20 11:30 | 1217 | 1217
2017-01-20 12:00 | 1219 | 1219
2017-01-20 12:30 | 1194 | 1194
2017-01-20 13:00 | 1189 | 1189
2017-01-20 13:30 | 1214 | 1214
2017-01-20 14:00 | 1237 | 1237
2017-01-20 14:30 | 1291 | 1291
2017-01-20 15:00 | 1327 | 1325
2017-01-20 15:30 | 1378 | 1377
2017-01-20 16:00 | 1448 | 1448
2017-01-20 16:30 | 1484 | 1484
2017-01-20 17:00 | 1503 | 1503
2017-01-20 17:30 | 1495 | 1493
2017-01-20 18:00 | 1473 | 1469
2017-01-20 18:30 | 1427 | 1420
2017-01-20 19:00 | 1428 | 1422
2017-01-20 19:30 | 1425 | 1421
2017-01-20 20:00 | 1424 | 1420
2017-01-20 20:30 | 1386 | 1383
2017-01-20 21:00 | 1333 | 1329
2017-01-20 21:30 | 1289 | 1280
2017-01-20 22:00 | 1240 | 1230
2017-01-20 22:30 | 1212 | 1202
2017-01-20 23:00 | 1186 | 1176
2017-01-20 23:30 | 1088 | 1077
2017-01-21 | 989 | 977
2017-01-21 00:30 | 911 | 897
2017-01-21 01:00 | 872 | 860
2017-01-21 01:30 | 826 | 817
2017-01-21 02:00 | 817 | 809
2017-01-21 02:30 | 806 | 797
2017-01-21 03:00 | 795 | 785
2017-01-21 03:30 | 790 | 780
2017-01-21 04:00 | 786 | 776
2017-01-21 04:30 | 785 | 775
2017-01-21 05:00 | 790 | 780
2017-01-21 05:30 | 789 | 779
2017-01-21 06:00 | 801 | 791
2017-01-21 06:30 | 823 | 815
2017-01-21 07:00 | 842 | 839
2017-01-21 07:30 | 898 | 895
2017-01-21 08:00 | 945 | 941
2017-01-21 08:30 | 994 | 989
2017-01-21 09:00 | 1057 | 1052
2017-01-21 09:30 | 1071 | 1067
2017-01-21 10:00 | 1090 | 1087
2017-01-21 10:30 | 1144 | 1144
2017-01-21 11:00 | 1163 | 1163
2017-01-21 11:30 | 1167 | 1167
2017-01-21 12:00 | 1162 | 1159
2017-01-21 12:30 | 1132 | 1126
2017-01-21 13:00 | 1107 | 1104
2017-01-21 13:30 | 1096 | 1091
2017-01-21 14:00 | 1108 | 1103
2017-01-21 14:30 | 1069 | 1061
2017-01-21 15:00 | 1051 | 1041
2017-01-21 15:30 | 1033 | 1025
2017-01-21 16:00 | 1045 | 1037
2017-01-21 16:30 | 1045 | 1038
2017-01-21 17:00 | 1036 | 1029
2017-01-21 17:30 | 1027 | 1018
2017-01-21 18:00 | 1013 | 1003
2017-01-21 18:30 | 998 | 993
2017-01-21 19:00 | 1002 | 1000
2017-01-21 19:30 | 1002 | 1001
2017-01-21 20:00 | 1000 | 998
2017-01-21 20:30 | 975 | 973
2017-01-21 21:00 | 928 | 923
2017-01-21 21:30 | 909 | 902
2017-01-21 22:00 | 885 | 878
2017-01-21 22:30 | 864 | 860
2017-01-21 23:00 | 868 | 866
2017-01-21 23:30 | 818 | 813
2017-01-22 | 770 | 761
2017-01-22 00:30 | 727 | 721
2017-01-22 01:00 | 703 | 698
2017-01-22 01:30 | 675 | 670
2017-01-22 02:00 | 662 | 656
2017-01-22 02:30 | 651 | 643
2017-01-22 03:00 | 644 | 637
2017-01-22 03:30 | 642 | 634
2017-01-22 04:00 | 636 | 628
2017-01-22 04:30 | 637 | 629
2017-01-22 05:00 | 637 | 628
2017-01-22 05:30 | 638 | 628
2017-01-22 06:00 | 644 | 635
2017-01-22 06:30 | 661 | 653
2017-01-22 07:00 | 679 | 673
2017-01-22 07:30 | 703 | 700
2017-01-22 08:00 | 731 | 729
2017-01-22 08:30 | 756 | 756
2017-01-22 09:00 | 759 | 759
2017-01-22 09:30 | 781 | 781
2017-01-22 10:00 | 790 | 790
2017-01-22 10:30 | 788 | 788
2017-01-22 11:00 | 784 | 784
2017-01-22 11:30 | 798 | 797
2017-01-22 12:00 | 799 | 797
2017-01-22 12:30 | 799 | 797
2017-01-22 13:00 | 798 | 796
2017-01-22 13:30 | 788 | 786
2017-01-22 14:00 | 797 | 795
2017-01-22 14:30 | 802 | 801
2017-01-22 15:00 | 825 | 825
2017-01-22 15:30 | 843 | 842
2017-01-22 16:00 | 871 | 871
2017-01-22 16:30 | 899 | 899
2017-01-22 17:00 | 928 | 928
2017-01-22 17:30 | 934 | 933
2017-01-22 18:00 | 943 | 942
2017-01-22 18:30 | 951 | 950
2017-01-22 19:00 | 948 | 947
2017-01-22 19:30 | 967 | 967
2017-01-22 20:00 | 958 | 958
2017-01-22 20:30 | 943 | 942
2017-01-22 21:00 | 906 | 904
2017-01-22 21:30 | 881 | 878
2017-01-22 22:00 | 849 | 845
2017-01-22 22:30 | 818 | 818
2017-01-22 23:00 | 815 | 815
2017-01-22 23:30 | 770 | 769
2017-01-23 | 716 | 715
2017-01-23 00:30 | 684 | 682
2017-01-23 01:00 | 667 | 663
2017-01-23 01:30 | 644 | 639
2017-01-23 02:00 | 630 | 623
2017-01-23 02:30 | 624 | 616
2017-01-23 03:00 | 619 | 611
2017-01-23 03:30 | 616 | 608
2017-01-23 04:00 | 613 | 606
2017-01-23 04:30 | 622 | 615
2017-01-23 05:00 | 638 | 634
2017-01-23 05:30 | 662 | 659
2017-01-23 06:00 | 717 | 711
2017-01-23 06:30 | 785 | 783
2017-01-23 07:00 | 866 | 862
2017-01-23 07:30 | 930 | 928
2017-01-23 08:00 | 945 | 943
2017-01-23 08:30 | 982 | 977
2017-01-23 09:00 | 997 | 994
2017-01-23 09:30 | 1000 | 998
2017-01-23 10:00 | 999 | 997
2017-01-23 10:30 | 980 | 978
2017-01-23 11:00 | 967 | 966
2017-01-23 11:30 | 966 | 965
2017-01-23 12:00 | 963 | 962
2017-01-23 12:30 | 949 | 948
2017-01-23 13:00 | 950 | 949
2017-01-23 13:30 | 965 | 964
2017-01-23 14:00 | 991 | 991
2017-01-23 14:30 | 1008 | 1008
2017-01-23 15:00 | 1029 | 1028
2017-01-23 15:30 | 1054 | 1052
2017-01-23 16:00 | 1098 | 1094
2017-01-23 16:30 | 1118 | 1114
2017-01-23 17:00 | 1155 | 1150
2017-01-23 17:30 | 1169 | 1161
2017-01-23 18:00 | 1152 | 1138
2017-01-23 18:30 | 1123 | 1108
2017-01-23 19:00 | 1124 | 1111
2017-01-23 19:30 | 1120 | 1117
2017-01-23 20:00 | 1108 | 1105
2017-01-23 20:30 | 1076 | 1069
2017-01-23 21:00 | 1009 | 1004
2017-01-23 21:30 | 954 | 948
2017-01-23 22:00 | 886 | 880
2017-01-23 22:30 | 865 | 861
2017-01-23 23:00 | 864 | 860
2017-01-23 23:30 | 797 | 793
2017-01-24 | 732 | 730
2017-01-24 00:30 | 693 | 690
2017-01-24 01:00 | 665 | 661
2017-01-24 01:30 | 635 | 628
2017-01-24 02:00 | 617 | 608
2017-01-24 02:30 | 601 | 591
2017-01-24 03:00 | 591 | 580
2017-01-24 03:30 | 584 | 574
2017-01-24 04:00 | 582 | 572
2017-01-24 04:30 | 598 | 589
2017-01-24 05:00 | 615 | 609
2017-01-24 05:30 | 643 | 637
2017-01-24 06:00 | 681 | 677
2017-01-24 06:30 | 756 | 755
2017-01-24 07:00 | 840 | 840
2017-01-24 07:30 | 906 | 906
2017-01-24 08:00 | 904 | 904
2017-01-24 08:30 | 918 | 917
2017-01-24 09:00 | 922 | 922
2017-01-24 09:30 | 938 | 938
2017-01-24 10:00 | 938 | 938
2017-01-24 10:30 | 943 | 942
2017-01-24 11:00 | 949 | 949
2017-01-24 11:30 | 963 | 962
2017-01-24 12:00 | 983 | 982
2017-01-24 12:30 | 1012 | 1011
2017-01-24 13:00 | 1026 | 1025
2017-01-24 13:30 | 1038 | 1038
2017-01-24 14:00 | 1114 | 1114
2017-01-24 14:30 | 1090 | 1090
2017-01-24 15:00 | 1120 | 1120
2017-01-24 15:30 | 1154 | 1154
2017-01-24 16:00 | 1209 | 1208
2017-01-24 16:30 | 1275 | 1274
2017-01-24 17:00 | 1290 | 1288
2017-01-24 17:30 | 1316 | 1315
2017-01-24 18:00 | 1287 | 1284
2017-01-24 18:30 | 1248 | 1242
2017-01-24 19:00 | 1248 | 1241
2017-01-24 19:30 | 1230 | 1225
2017-01-24 20:00 | 1185 | 1180
2017-01-24 20:30 | 1129 | 1124
2017-01-24 21:00 | 1080 | 1077
2017-01-24 21:30 | 1023 | 1019
2017-01-24 22:00 | 981 | 976
2017-01-24 22:30 | 950 | 944
2017-01-24 23:00 | 927 | 922
2017-01-24 23:30 | 849 | 847
2017-01-25 | 801 | 796
2017-01-25 00:30 | 769 | 761
2017-01-25 01:00 | 743 | 731
2017-01-25 01:30 | 710 | 701
2017-01-25 02:00 | 695 | 685
2017-01-25 02:30 | 686 | 675
2017-01-25 03:00 | 670 | 665
2017-01-25 03:30 | 664 | 662
2017-01-25 04:00 | 670 | 667
2017-01-25 04:30 | 680 | 678
2017-01-25 05:00 | 691 | 689
2017-01-25 05:30 | 728 | 720
2017-01-25 06:00 | 763 | 758
2017-01-25 06:30 | 826 | 824
2017-01-25 07:00 | 931 | 928
2017-01-25 07:30 | 982 | 977
2017-01-25 08:00 | 992 | 988
2017-01-25 08:30 | 1013 | 1012
2017-01-25 09:00 | 1034 | 1032
2017-01-25 09:30 | 1058 | 1057
2017-01-25 10:00 | 1072 | 1069
2017-01-25 10:30 | 1087 | 1085
2017-01-25 11:00 | 1098 | 1096
2017-01-25 11:30 | 1106 | 1105
2017-01-25 12:00 | 1133 | 1133
2017-01-25 12:30 | 1145 | 1143
2017-01-25 13:00 | 1155 | 1153
2017-01-25 13:30 | 1172 | 1170
2017-01-25 14:00 | 1185 | 1183
2017-01-25 14:30 | 1218 | 1216
2017-01-25 15:00 | 1254 | 1251
2017-01-25 15:30 | 1307 | 1304
2017-01-25 16:00 | 1338 | 1336
2017-01-25 16:30 | 1353 | 1351
2017-01-25 17:00 | 1374 | 1372
2017-01-25 17:30 | 1359 | 1357
2017-01-25 18:00 | 1335 | 1329
2017-01-25 18:30 | 1290 | 1277
2017-01-25 19:00 | 1279 | 1272
2017-01-25 19:30 | 1224 | 1219
2017-01-25 20:00 | 1182 | 1174
2017-01-25 20:30 | 1156 | 1147
2017-01-25 21:00 | 1100 | 1093
2017-01-25 21:30 | 1060 | 1051
2017-01-25 22:00 | 1004 | 999
2017-01-25 22:30 | 991 | 983
2017-01-25 23:00 | 965 | 954
2017-01-25 23:30 | 895 | 886
2017-01-26 | 834 | 827
2017-01-26 00:30 | 797 | 788
2017-01-26 01:00 | 768 | 755
2017-01-26 01:30 | 732 | 723
2017-01-26 02:00 | 710 | 706
2017-01-26 02:30 | 696 | 693
2017-01-26 03:00 | 683 | 680
2017-01-26 03:30 | 680 | 677
2017-01-26 04:00 | 676 | 673
2017-01-26 04:30 | 672 | 669
2017-01-26 05:00 | 678 | 676
2017-01-26 05:30 | 679 | 676
2017-01-26 06:00 | 686 | 682
2017-01-26 06:30 | 709 | 708
2017-01-26 07:00 | 744 | 739
2017-01-26 07:30 | 786 | 784
2017-01-26 08:00 | 810 | 808
2017-01-26 08:30 | 843 | 840
2017-01-26 09:00 | 847 | 843
2017-01-26 09:30 | 865 | 862
2017-01-26 10:00 | 908 | 907
2017-01-26 10:30 | 918 | 917
2017-01-26 11:00 | 922 | 919
2017-01-26 11:30 | 914 | 913
2017-01-26 12:00 | 918 | 916
2017-01-26 12:30 | 920 | 917
2017-01-26 13:00 | 953 | 951
2017-01-26 13:30 | 949 | 946
2017-01-26 14:00 | 971 | 969
2017-01-26 14:30 | 1007 | 1003
2017-01-26 15:00 | 1030 | 1028
2017-01-26 15:30 | 1054 | 1053
2017-01-26 16:00 | 1097 | 1096
2017-01-26 16:30 | 1127 | 1126
2017-01-26 17:00 | 1150 | 1148
2017-01-26 17:30 | 1165 | 1162
2017-01-26 18:00 | 1161 | 1156
2017-01-26 18:30 | 1168 | 1162
2017-01-26 19:00 | 1175 | 1170
2017-01-26 19:30 | 1169 | 1165
2017-01-26 20:00 | 1162 | 1157
2017-01-26 20:30 | 1142 | 1132
2017-01-26 21:00 | 1090 | 1075
2017-01-26 21:30 | 1031 | 1020
2017-01-26 22:00 | 972 | 959
2017-01-26 22:30 | 949 | 941
2017-01-26 23:00 | 927 | 920
2017-01-26 23:30 | 849 | 840
2017-01-27 | 804 | 792
2017-01-27 00:30 | 751 | 745
2017-01-27 01:00 | 733 | 727
2017-01-27 01:30 | 714 | 708
2017-01-27 02:00 | 701 | 694
2017-01-27 02:30 | 694 | 686
2017-01-27 03:00 | 685 | 677
2017-01-27 03:30 | 677 | 673
2017-01-27 04:00 | 677 | 673
2017-01-27 04:30 | 683 | 680
2017-01-27 05:00 | 694 | 692
2017-01-27 05:30 | 721 | 720
2017-01-27 06:00 | 744 | 744
2017-01-27 06:30 | 818 | 818
2017-01-27 07:00 | 906 | 906
2017-01-27 07:30 | 964 | 964
2017-01-27 08:00 | 974 | 974
2017-01-27 08:30 | 1000 | 1000
2017-01-27 09:00 | 1036 | 1036
2017-01-27 09:30 | 1059 | 1059
2017-01-27 10:00 | 1082 | 1082
2017-01-27 10:30 | 1119 | 1119
2017-01-27 11:00 | 1158 | 1158
2017-01-27 11:30 | 1179 | 1179
2017-01-27 12:00 | 1194 | 1194
2017-01-27 12:30 | 1187 | 1187
2017-01-27 13:00 | 1174 | 1174
2017-01-27 13:30 | 1169 | 1169
2017-01-27 14:00 | 1159 | 1159
2017-01-27 14:30 | 1156 | 1155
2017-01-27 15:00 | 1148 | 1148
2017-01-27 15:30 | 1157 | 1156
2017-01-27 16:00 | 1183 | 1182
2017-01-27 16:30 | 1191 | 1190
2017-01-27 17:00 | 1200 | 1199
2017-01-27 17:30 | 1177 | 1173
2017-01-27 18:00 | 1156 | 1150
2017-01-27 18:30 | 1112 | 1105
2017-01-27 19:00 | 1116 | 1111
2017-01-27 19:30 | 1113 | 1108
2017-01-27 20:00 | 1107 | 1102
2017-01-27 20:30 | 1071 | 1066
2017-01-27 21:00 | 1023 | 1021
2017-01-27 21:30 | 988 | 985
2017-01-27 22:00 | 956 | 953
2017-01-27 22:30 | 939 | 935
2017-01-27 23:00 | 930 | 926
2017-01-27 23:30 | 866 | 863
2017-01-28 | 815 | 808
2017-01-28 00:30 | 769 | 762
2017-01-28 01:00 | 741 | 735
2017-01-28 01:30 | 714 | 706
2017-01-28 02:00 | 696 | 691
2017-01-28 02:30 | 679 | 676
2017-01-28 03:00 | 672 | 668
2017-01-28 03:30 | 666 | 662
2017-01-28 04:00 | 664 | 660
2017-01-28 04:30 | 660 | 655
2017-01-28 05:00 | 666 | 662
2017-01-28 05:30 | 670 | 665
2017-01-28 06:00 | 682 | 677
2017-01-28 06:30 | 704 | 701
2017-01-28 07:00 | 728 | 727
2017-01-28 07:30 | 760 | 760
2017-01-28 08:00 | 795 | 793
2017-01-28 08:30 | 840 | 838
2017-01-28 09:00 | 872 | 872
2017-01-28 09:30 | 890 | 889
2017-01-28 10:00 | 903 | 903
2017-01-28 10:30 | 911 | 910
2017-01-28 11:00 | 923 | 923
2017-01-28 11:30 | 940 | 940
2017-01-28 12:00 | 949 | 949
2017-01-28 12:30 | 941 | 941
2017-01-28 13:00 | 953 | 953
2017-01-28 13:30 | 970 | 970
2017-01-28 14:00 | 982 | 981
2017-01-28 14:30 | 1007 | 1007
2017-01-28 15:00 | 1024 | 1024
2017-01-28 15:30 | 1041 | 1041
2017-01-28 16:00 | 1064 | 1063
2017-01-28 16:30 | 1086 | 1085
2017-01-28 17:00 | 1129 | 1128
2017-01-28 17:30 | 1124 | 1124
2017-01-28 18:00 | 1110 | 1110
2017-01-28 18:30 | 1094 | 1094
2017-01-28 19:00 | 1094 | 1094
2017-01-28 19:30 | 1108 | 1108
2017-01-28 20:00 | 1101 | 1101
2017-01-28 20:30 | 1074 | 1072
2017-01-28 21:00 | 1034 | 1029
2017-01-28 21:30 | 989 | 982
2017-01-28 22:00 | 961 | 952
2017-01-28 22:30 | 930 | 923
2017-01-28 23:00 | 912 | 908
2017-01-28 23:30 | 856 | 854
2017-01-29 | 807 | 802
2017-01-29 00:30 | 759 | 754
2017-01-29 01:00 | 731 | 728
2017-01-29 01:30 | 699 | 697
2017-01-29 02:00 | 682 | 679
2017-01-29 02:30 | 667 | 663
2017-01-29 03:00 | 659 | 655
2017-01-29 03:30 | 656 | 651
2017-01-29 04:00 | 651 | 646
2017-01-29 04:30 | 644 | 638
2017-01-29 05:00 | 650 | 644
2017-01-29 05:30 | 649 | 641
2017-01-29 06:00 | 651 | 641
2017-01-29 06:30 | 664 | 657
2017-01-29 07:00 | 685 | 681
2017-01-29 07:30 | 710 | 710
2017-01-29 08:00 | 741 | 741
2017-01-29 08:30 | 782 | 781
2017-01-29 09:00 | 806 | 806
2017-01-29 09:30 | 828 | 828
2017-01-29 10:00 | 849 | 849
2017-01-29 10:30 | 853 | 853
2017-01-29 11:00 | 848 | 848
2017-01-29 11:30 | 878 | 878
2017-01-29 12:00 | 926 | 926
2017-01-29 12:30 | 927 | 927
2017-01-29 13:00 | 950 | 949
2017-01-29 13:30 | 970 | 970
2017-01-29 14:00 | 985 | 985
2017-01-29 14:30 | 1011 | 1011
2017-01-29 15:00 | 1034 | 1033
2017-01-29 15:30 | 1060 | 1059
2017-01-29 16:00 | 1092 | 1091
2017-01-29 16:30 | 1117 | 1117
2017-01-29 17:00 | 1152 | 1150
2017-01-29 17:30 | 1149 | 1147
2017-01-29 18:00 | 1163 | 1158
2017-01-29 18:30 | 1168 | 1161
2017-01-29 19:00 | 1182 | 1176
2017-01-29 19:30 | 1188 | 1186
2017-01-29 20:00 | 1158 | 1158
2017-01-29 20:30 | 1129 | 1128
2017-01-29 21:00 | 1061 | 1061
2017-01-29 21:30 | 1029 | 1029
2017-01-29 22:00 | 996 | 995
2017-01-29 22:30 | 977 | 974
2017-01-29 23:00 | 935 | 929
2017-01-29 23:30 | 883 | 879
2017-01-30 | 819 | 812
2017-01-30 00:30 | 774 | 772
2017-01-30 01:00 | 746 | 744
2017-01-30 01:30 | 720 | 716
2017-01-30 02:00 | 700 | 695
2017-01-30 02:30 | 693 | 687
2017-01-30 03:00 | 681 | 675
2017-01-30 03:30 | 677 | 670
2017-01-30 04:00 | 682 | 675
2017-01-30 04:30 | 689 | 683
2017-01-30 05:00 | 699 | 696
2017-01-30 05:30 | 731 | 729
2017-01-30 06:00 | 770 | 768
2017-01-30 06:30 | 851 | 850
2017-01-30 07:00 | 920 | 919
2017-01-30 07:30 | 999 | 998
2017-01-30 08:00 | 1032 | 1031
2017-01-30 08:30 | 1063 | 1062
2017-01-30 09:00 | 1075 | 1073
2017-01-30 09:30 | 1109 | 1107
2017-01-30 10:00 | 1120 | 1115
2017-01-30 10:30 | 1121 | 1117
2017-01-30 11:00 | 1123 | 1119
2017-01-30 11:30 | 1137 | 1134
2017-01-30 12:00 | 1150 | 1148
2017-01-30 12:30 | 1157 | 1155
2017-01-30 13:00 | 1176 | 1174
2017-01-30 13:30 | 1197 | 1194
2017-01-30 14:00 | 1209 | 1205
2017-01-30 14:30 | 1215 | 1212
2017-01-30 15:00 | 1231 | 1228
2017-01-30 15:30 | 1258 | 1257
2017-01-30 16:00 | 1292 | 1292
2017-01-30 16:30 | 1351 | 1350
2017-01-30 17:00 | 1369 | 1369
2017-01-30 17:30 | 1380 | 1379
2017-01-30 18:00 | 1348 | 1345
2017-01-30 18:30 | 1313 | 1306
2017-01-30 19:00 | 1306 | 1299
2017-01-30 19:30 | 1288 | 1284
2017-01-30 20:00 | 1280 | 1274
2017-01-30 20:30 | 1229 | 1220
2017-01-30 21:00 | 1161 | 1157
2017-01-30 21:30 | 1098 | 1094
2017-01-30 22:00 | 1044 | 1042
2017-01-30 22:30 | 1003 | 1001
2017-01-30 23:00 | 977 | 973
2017-01-30 23:30 | 900 | 898
2017-01-31 | 822 | 822
2017-01-31 00:30 | 771 | 770
2017-01-31 01:00 | 740 | 739
2017-01-31 01:30 | 716 | 713
2017-01-31 02:00 | 700 | 697
2017-01-31 02:30 | 687 | 683
2017-01-31 03:00 | 679 | 674
2017-01-31 03:30 | 675 | 670
2017-01-31 04:00 | 678 | 672
2017-01-31 04:30 | 685 | 680
2017-01-31 05:00 | 698 | 694
2017-01-31 05:30 | 724 | 722
2017-01-31 06:00 | 764 | 762
2017-01-31 06:30 | 843 | 842
2017-01-31 07:00 | 926 | 923
2017-01-31 07:30 | 996 | 993
2017-01-31 08:00 | 1026 | 1022
2017-01-31 08:30 | 1052 | 1051
2017-01-31 09:00 | 1067 | 1067
2017-01-31 09:30 | 1091 | 1091
2017-01-31 10:00 | 1103 | 1103
2017-01-31 10:30 | 1111 | 1111
2017-01-31 11:00 | 1115 | 1115
2017-01-31 11:30 | 1122 | 1122
2017-01-31 12:00 | 1140 | 1140
2017-01-31 12:30 | 1168 | 1166
2017-01-31 13:00 | 1186 | 1185
2017-01-31 13:30 | 1215 | 1214
2017-01-31 14:00 | 1244 | 1244
2017-01-31 14:30 | 1285 | 1285
2017-01-31 15:00 | 1315 | 1315
2017-01-31 15:30 | 1335 | 1335
2017-01-31 16:00 | 1353 | 1353
2017-01-31 16:30 | 1415 | 1414
2017-01-31 17:00 | 1429 | 1428
2017-01-31 17:30 | 1420 | 1420
2017-01-31 18:00 | 1400 | 1399
2017-01-31 18:30 | 1343 | 1341
2017-01-31 19:00 | 1352 | 1350
2017-01-31 19:30 | 1295 | 1292
2017-01-31 20:00 | 1288 | 1286
2017-01-31 20:30 | 1241 | 1237
2017-01-31 21:00 | 1160 | 1159
2017-01-31 21:30 | 1100 | 1098
2017-01-31 22:00 | 1038 | 1034
2017-01-31 22:30 | 1000 | 997
2017-01-31 23:00 | 960 | 959
2017-01-31 23:30 | 863 | 859
2017-02-01 | 828 | 825
2017-02-01 00:30 | 797 | 793
2017-02-01 01:00 | 783 | 777
2017-02-01 01:30 | 765 | 759
2017-02-01 02:00 | 717 | 708
2017-02-01 02:30 | 724 | 714
2017-02-01 03:00 | 713 | 703
2017-02-01 03:30 | 714 | 703
2017-02-01 04:00 | 704 | 692
2017-02-01 04:30 | 709 | 698
2017-02-01 05:00 | 718 | 709
2017-02-01 05:30 | 735 | 728
2017-02-01 06:00 | 781 | 777
2017-02-01 06:30 | 879 | 877
2017-02-01 07:00 | 943 | 941
2017-02-01 07:30 | 1014 | 1010
2017-02-01 08:00 | 1033 | 1029
2017-02-01 08:30 | 1063 | 1061
2017-02-01 09:00 | 1091 | 1084
2017-02-01 09:30 | 1100 | 1095
2017-02-01 10:00 | 1113 | 1108
2017-02-01 10:30 | 1120 | 1116
2017-02-01 11:00 | 1137 | 1135
2017-02-01 11:30 | 1157 | 1156
2017-02-01 12:00 | 1194 | 1192
2017-02-01 12:30 | 1217 | 1217
2017-02-01 13:00 | 1242 | 1242
2017-02-01 13:30 | 1279 | 1279
2017-02-01 14:00 | 1303 | 1303
2017-02-01 14:30 | 1308 | 1308
2017-02-01 15:00 | 1326 | 1326
2017-02-01 15:30 | 1348 | 1348
2017-02-01 16:00 | 1412 | 1411
2017-02-01 16:30 | 1419 | 1419
2017-02-01 17:00 | 1431 | 1431
2017-02-01 17:30 | 1432 | 1431
2017-02-01 18:00 | 1413 | 1412
2017-02-01 18:30 | 1362 | 1356
2017-02-01 19:00 | 1356 | 1353
2017-02-01 19:30 | 1339 | 1338
2017-02-01 20:00 | 1292 | 1292
2017-02-01 20:30 | 1258 | 1257
2017-02-01 21:00 | 1208 | 1207
2017-02-01 21:30 | 1141 | 1138
2017-02-01 22:00 | 1084 | 1078
2017-02-01 22:30 | 1036 | 1030
2017-02-01 23:00 | 1016 | 1013
2017-02-01 23:30 | 942 | 935
2017-02-02 | 866 | 860
2017-02-02 00:30 | 824 | 818
2017-02-02 01:00 | 795 | 788
2017-02-02 01:30 | 769 | 763
2017-02-02 02:00 | 749 | 741
2017-02-02 02:30 | 734 | 727
2017-02-02 03:00 | 721 | 717
2017-02-02 03:30 | 723 | 719
2017-02-02 04:00 | 719 | 716
2017-02-02 04:30 | 731 | 728
2017-02-02 05:00 | 741 | 739
2017-02-02 05:30 | 772 | 768
2017-02-02 06:00 | 809 | 803
2017-02-02 06:30 | 896 | 893
2017-02-02 07:00 | 980 | 975
2017-02-02 07:30 | 1047 | 1046
2017-02-02 08:00 | 1080 | 1080
2017-02-02 08:30 | 1101 | 1101
2017-02-02 09:00 | 1108 | 1108
2017-02-02 09:30 | 1123 | 1123
2017-02-02 10:00 | 1156 | 1156
2017-02-02 10:30 | 1173 | 1173
2017-02-02 11:00 | 1195 | 1195
2017-02-02 11:30 | 1230 | 1230
2017-02-02 12:00 | 1284 | 1284
2017-02-02 12:30 | 1311 | 1310
2017-02-02 13:00 | 1337 | 1336
2017-02-02 13:30 | 1347 | 1347
2017-02-02 14:00 | 1370 | 1369
2017-02-02 14:30 | 1383 | 1382
2017-02-02 15:00 | 1387 | 1387
2017-02-02 15:30 | 1416 | 1416
2017-02-02 16:00 | 1454 | 1454
2017-02-02 16:30 | 1489 | 1489
2017-02-02 17:00 | 1505 | 1505
2017-02-02 17:30 | 1506 | 1506
2017-02-02 18:00 | 1476 | 1474
2017-02-02 18:30 | 1440 | 1438
2017-02-02 19:00 | 1426 | 1424
2017-02-02 19:30 | 1430 | 1428
2017-02-02 20:00 | 1400 | 1397
2017-02-02 20:30 | 1356 | 1349
2017-02-02 21:00 | 1255 | 1244
2017-02-02 21:30 | 1173 | 1164
2017-02-02 22:00 | 1110 | 1097
2017-02-02 22:30 | 1054 | 1049
2017-02-02 23:00 | 1019 | 1015
2017-02-02 23:30 | 939 | 932
2017-02-03 | 878 | 871
2017-02-03 00:30 | 835 | 827
2017-02-03 01:00 | 807 | 799
2017-02-03 01:30 | 783 | 772
2017-02-03 02:00 | 766 | 754
2017-02-03 02:30 | 758 | 745
2017-02-03 03:00 | 743 | 734
2017-02-03 03:30 | 746 | 737
2017-02-03 04:00 | 747 | 738
2017-02-03 04:30 | 750 | 742
2017-02-03 05:00 | 766 | 760
2017-02-03 05:30 | 791 | 787
2017-02-03 06:00 | 831 | 827
2017-02-03 06:30 | 916 | 915
2017-02-03 07:00 | 992 | 992
2017-02-03 07:30 | 1072 | 1071
2017-02-03 08:00 | 1108 | 1107
2017-02-03 08:30 | 1126 | 1123
2017-02-03 09:00 | 1137 | 1135
2017-02-03 09:30 | 1157 | 1156
2017-02-03 10:00 | 1169 | 1169
2017-02-03 10:30 | 1171 | 1171
2017-02-03 11:00 | 1183 | 1183
2017-02-03 11:30 | 1188 | 1188
2017-02-03 12:00 | 1190 | 1190
2017-02-03 12:30 | 1202 | 1202
2017-02-03 13:00 | 1220 | 1220
2017-02-03 13:30 | 1245 | 1245
2017-02-03 14:00 | 1277 | 1277
2017-02-03 14:30 | 1305 | 1305
2017-02-03 15:00 | 1326 | 1326
2017-02-03 15:30 | 1348 | 1348
2017-02-03 16:00 | 1392 | 1392
2017-02-03 16:30 | 1424 | 1424
2017-02-03 17:00 | 1417 | 1417
2017-02-03 17:30 | 1409 | 1408
2017-02-03 18:00 | 1372 | 1368
2017-02-03 18:30 | 1284 | 1279
2017-02-03 19:00 | 1268 | 1263
2017-02-03 19:30 | 1237 | 1233
2017-02-03 20:00 | 1219 | 1213
2017-02-03 20:30 | 1192 | 1185
2017-02-03 21:00 | 1133 | 1131
2017-02-03 21:30 | 1091 | 1088
2017-02-03 22:00 | 1043 | 1042
2017-02-03 22:30 | 1008 | 1006
2017-02-03 23:00 | 983 | 982
2017-02-03 23:30 | 912 | 908
2017-02-04 | 854 | 852
2017-02-04 00:30 | 802 | 802
2017-02-04 01:00 | 772 | 772
2017-02-04 01:30 | 743 | 743
2017-02-04 02:00 | 724 | 723
2017-02-04 02:30 | 710 | 710
2017-02-04 03:00 | 698 | 697
2017-02-04 03:30 | 692 | 691
2017-02-04 04:00 | 689 | 688
2017-02-04 04:30 | 685 | 684
2017-02-04 05:00 | 686 | 685
2017-02-04 05:30 | 695 | 693
2017-02-04 06:00 | 706 | 704
2017-02-04 06:30 | 731 | 730
2017-02-04 07:00 | 760 | 760
2017-02-04 07:30 | 804 | 803
2017-02-04 08:00 | 839 | 839
2017-02-04 08:30 | 894 | 893
2017-02-04 09:00 | 913 | 912
2017-02-04 09:30 | 943 | 941
2017-02-04 10:00 | 961 | 961
2017-02-04 10:30 | 982 | 982
2017-02-04 11:00 | 998 | 998
2017-02-04 11:30 | 1030 | 1029
2017-02-04 12:00 | 1034 | 1033
2017-02-04 12:30 | 1027 | 1027
2017-02-04 13:00 | 1035 | 1035
2017-02-04 13:30 | 1043 | 1043
2017-02-04 14:00 | 1074 | 1073
2017-02-04 14:30 | 1119 | 1119
2017-02-04 15:00 | 1139 | 1139
2017-02-04 15:30 | 1172 | 1171
2017-02-04 16:00 | 1200 | 1200
2017-02-04 16:30 | 1215 | 1214
2017-02-04 17:00 | 1266 | 1265
2017-02-04 17:30 | 1253 | 1253
2017-02-04 18:00 | 1228 | 1228
2017-02-04 18:30 | 1225 | 1225
2017-02-04 19:00 | 1237 | 1236
2017-02-04 19:30 | 1223 | 1223
2017-02-04 20:00 | 1204 | 1204
2017-02-04 20:30 | 1167 | 1165
2017-02-04 21:00 | 1119 | 1114
2017-02-04 21:30 | 1077 | 1072
2017-02-04 22:00 | 1030 | 1025
2017-02-04 22:30 | 1004 | 1002
2017-02-04 23:00 | 978 | 973
2017-02-04 23:30 | 922 | 918
2017-02-05 | 866 | 862
2017-02-05 00:30 | 822 | 817
2017-02-05 01:00 | 786 | 782
2017-02-05 01:30 | 748 | 747
2017-02-05 02:00 | 719 | 719
2017-02-05 02:30 | 709 | 708
2017-02-05 03:00 | 707 | 706
2017-02-05 03:30 | 706 | 705
2017-02-05 04:00 | 703 | 701
2017-02-05 04:30 | 700 | 698
2017-02-05 05:00 | 696 | 695
2017-02-05 05:30 | 700 | 698
2017-02-05 06:00 | 697 | 694
2017-02-05 06:30 | 710 | 709
2017-02-05 07:00 | 738 | 737
2017-02-05 07:30 | 775 | 775
2017-02-05 08:00 | 815 | 815
2017-02-05 08:30 | 859 | 859
2017-02-05 09:00 | 894 | 894
2017-02-05 09:30 | 923 | 923
2017-02-05 10:00 | 944 | 944
2017-02-05 10:30 | 957 | 956
2017-02-05 11:00 | 966 | 965
2017-02-05 11:30 | 983 | 981
2017-02-05 12:00 | 1009 | 1007
2017-02-05 12:30 | 1016 | 1015
2017-02-05 13:00 | 1053 | 1053
2017-02-05 13:30 | 1086 | 1083
2017-02-05 14:00 | 1111 | 1108
2017-02-05 14:30 | 1138 | 1136
2017-02-05 15:00 | 1152 | 1150
2017-02-05 15:30 | 1167 | 1164
2017-02-05 16:00 | 1190 | 1188
2017-02-05 16:30 | 1197 | 1194
2017-02-05 17:00 | 1225 | 1223
2017-02-05 17:30 | 1262 | 1260
2017-02-05 18:00 | 1266 | 1264
2017-02-05 18:30 | 1247 | 1244
2017-02-05 19:00 | 1236 | 1233
2017-02-05 19:30 | 1239 | 1236
2017-02-05 20:00 | 1217 | 1212
2017-02-05 20:30 | 1184 | 1179
2017-02-05 21:00 | 1122 | 1119
2017-02-05 21:30 | 1084 | 1081
2017-02-05 22:00 | 1023 | 1021
2017-02-05 22:30 | 980 | 976
2017-02-05 23:00 | 955 | 950
2017-02-05 23:30 | 879 | 877
2017-02-06 | 819 | 817
2017-02-06 00:30 | 765 | 765
2017-02-06 01:00 | 744 | 744
2017-02-06 01:30 | 723 | 723
2017-02-06 02:00 | 707 | 706
2017-02-06 02:30 | 692 | 692
2017-02-06 03:00 | 681 | 681
2017-02-06 03:30 | 678 | 677
2017-02-06 04:00 | 678 | 678
2017-02-06 04:30 | 686 | 686
2017-02-06 05:00 | 705 | 705
2017-02-06 05:30 | 739 | 739
2017-02-06 06:00 | 780 | 779
2017-02-06 06:30 | 872 | 872
2017-02-06 07:00 | 947 | 943
2017-02-06 07:30 | 1022 | 1018
2017-02-06 08:00 | 1070 | 1067
2017-02-06 08:30 | 1103 | 1103
2017-02-06 09:00 | 1126 | 1124
2017-02-06 09:30 | 1146 | 1145
2017-02-06 10:00 | 1152 | 1151
2017-02-06 10:30 | 1159 | 1158
2017-02-06 11:00 | 1169 | 1168
2017-02-06 11:30 | 1191 | 1189
2017-02-06 12:00 | 1211 | 1209
2017-02-06 12:30 | 1221 | 1220
2017-02-06 13:00 | 1238 | 1237
2017-02-06 13:30 | 1244 | 1243
2017-02-06 14:00 | 1258 | 1258
2017-02-06 14:30 | 1286 | 1286
2017-02-06 15:00 | 1305 | 1304
2017-02-06 15:30 | 1311 | 1311
2017-02-06 16:00 | 1346 | 1346
2017-02-06 16:30 | 1380 | 1380
2017-02-06 17:00 | 1416 | 1416
2017-02-06 17:30 | 1430 | 1430
2017-02-06 18:00 | 1408 | 1407
2017-02-06 18:30 | 1372 | 1368
2017-02-06 19:00 | 1385 | 1382
2017-02-06 19:30 | 1358 | 1354
2017-02-06 20:00 | 1318 | 1315
2017-02-06 20:30 | 1278 | 1275
2017-02-06 21:00 | 1213 | 1210
2017-02-06 21:30 | 1150 | 1147
2017-02-06 22:00 | 1087 | 1083
2017-02-06 22:30 | 1014 | 1013
2017-02-06 23:00 | 986 | 985
2017-02-06 23:30 | 916 | 911
2017-02-07 | 842 | 840
2017-02-07 00:30 | 802 | 800
2017-02-07 01:00 | 783 | 779
2017-02-07 01:30 | 754 | 752
2017-02-07 02:00 | 739 | 739
2017-02-07 02:30 | 719 | 718
2017-02-07 03:00 | 717 | 717
2017-02-07 03:30 | 712 | 711
2017-02-07 04:00 | 711 | 710
2017-02-07 04:30 | 717 | 717
2017-02-07 05:00 | 728 | 728
2017-02-07 05:30 | 760 | 759
2017-02-07 06:00 | 795 | 794
2017-02-07 06:30 | 883 | 883
2017-02-07 07:00 | 955 | 954
2017-02-07 07:30 | 1033 | 1033
2017-02-07 08:00 | 1066 | 1064
2017-02-07 08:30 | 1098 | 1098
2017-02-07 09:00 | 1114 | 1114
2017-02-07 09:30 | 1131 | 1131
2017-02-07 10:00 | 1149 | 1149
2017-02-07 10:30 | 1153 | 1152
2017-02-07 11:00 | 1161 | 1160
2017-02-07 11:30 | 1173 | 1172
2017-02-07 12:00 | 1179 | 1177
2017-02-07 12:30 | 1201 | 1200
2017-02-07 13:00 | 1213 | 1212
2017-02-07 13:30 | 1252 | 1251
2017-02-07 14:00 | 1304 | 1304
2017-02-07 14:30 | 1322 | 1322
2017-02-07 15:00 | 1347 | 1346
2017-02-07 15:30 | 1371 | 1371
2017-02-07 16:00 | 1419 | 1419
2017-02-07 16:30 | 1448 | 1447
2017-02-07 17:00 | 1467 | 1466
2017-02-07 17:30 | 1452 | 1450
2017-02-07 18:00 | 1430 | 1428
2017-02-07 18:30 | 1390 | 1384
2017-02-07 19:00 | 1392 | 1387
2017-02-07 19:30 | 1392 | 1387
2017-02-07 20:00 | 1315 | 1309
2017-02-07 20:30 | 1265 | 1262
2017-02-07 21:00 | 1191 | 1189
2017-02-07 21:30 | 1128 | 1123
2017-02-07 22:00 | 1069 | 1065
2017-02-07 22:30 | 1009 | 1007
2017-02-07 23:00 | 986 | 982
2017-02-07 23:30 | 909 | 902
2017-02-08 | 844 | 842
2017-02-08 00:30 | 811 | 807
2017-02-08 01:00 | 784 | 780
2017-02-08 01:30 | 753 | 752
2017-02-08 02:00 | 742 | 741
2017-02-08 02:30 | 724 | 724
2017-02-08 03:00 | 721 | 721
2017-02-08 03:30 | 715 | 714
2017-02-08 04:00 | 715 | 714
2017-02-08 04:30 | 726 | 726
2017-02-08 05:00 | 743 | 743
2017-02-08 05:30 | 776 | 776
2017-02-08 06:00 | 811 | 810
2017-02-08 06:30 | 894 | 893
2017-02-08 07:00 | 970 | 970
2017-02-08 07:30 | 1034 | 1034
2017-02-08 08:00 | 1073 | 1069
2017-02-08 08:30 | 1093 | 1092
2017-02-08 09:00 | 1107 | 1106
2017-02-08 09:30 | 1108 | 1107
2017-02-08 10:00 | 1118 | 1115
2017-02-08 10:30 | 1110 | 1106
2017-02-08 11:00 | 1103 | 1101
2017-02-08 11:30 | 1099 | 1097
2017-02-08 12:00 | 1103 | 1102
2017-02-08 12:30 | 1111 | 1109
2017-02-08 13:00 | 1125 | 1124
2017-02-08 13:30 | 1126 | 1126
2017-02-08 14:00 | 1145 | 1144
2017-02-08 14:30 | 1166 | 1163
2017-02-08 15:00 | 1171 | 1169
2017-02-08 15:30 | 1194 | 1192
2017-02-08 16:00 | 1229 | 1228
2017-02-08 16:30 | 1252 | 1251
2017-02-08 17:00 | 1268 | 1264
2017-02-08 17:30 | 1261 | 1251
2017-02-08 18:00 | 1233 | 1221
2017-02-08 18:30 | 1199 | 1191
2017-02-08 19:00 | 1206 | 1200
2017-02-08 19:30 | 1220 | 1215
2017-02-08 20:00 | 1203 | 1197
2017-02-08 20:30 | 1162 | 1160
2017-02-08 21:00 | 1112 | 1109
2017-02-08 21:30 | 1062 | 1060
2017-02-08 22:00 | 1012 | 1009
2017-02-08 22:30 | 971 | 967
2017-02-08 23:00 | 952 | 950
2017-02-08 23:30 | 883 | 881
2017-02-09 | 828 | 825
2017-02-09 00:30 | 777 | 777
2017-02-09 01:00 | 756 | 754
2017-02-09 01:30 | 734 | 732
2017-02-09 02:00 | 716 | 715
2017-02-09 02:30 | 710 | 709
2017-02-09 03:00 | 705 | 704
2017-02-09 03:30 | 700 | 700
2017-02-09 04:00 | 701 | 701
2017-02-09 04:30 | 712 | 711
2017-02-09 05:00 | 722 | 722
2017-02-09 05:30 | 753 | 753
2017-02-09 06:00 | 797 | 796
2017-02-09 06:30 | 870 | 869
2017-02-09 07:00 | 932 | 931
2017-02-09 07:30 | 1002 | 1001
2017-02-09 08:00 | 1039 | 1034
2017-02-09 08:30 | 1064 | 1061
2017-02-09 09:00 | 1089 | 1083
2017-02-09 09:30 | 1106 | 1102
2017-02-09 10:00 | 1096 | 1093
2017-02-09 10:30 | 1106 | 1103
2017-02-09 11:00 | 1109 | 1106
2017-02-09 11:30 | 1115 | 1112
2017-02-09 12:00 | 1122 | 1121
2017-02-09 12:30 | 1134 | 1133
2017-02-09 13:00 | 1140 | 1139
2017-02-09 13:30 | 1158 | 1157
2017-02-09 14:00 | 1176 | 1174
2017-02-09 14:30 | 1186 | 1185
2017-02-09 15:00 | 1204 | 1203
2017-02-09 15:30 | 1228 | 1226
2017-02-09 16:00 | 1259 | 1258
2017-02-09 16:30 | 1299 | 1295
2017-02-09 17:00 | 1330 | 1326
2017-02-09 17:30 | 1326 | 1319
2017-02-09 18:00 | 1290 | 1281
2017-02-09 18:30 | 1271 | 1260
2017-02-09 19:00 | 1277 | 1273
2017-02-09 19:30 | 1288 | 1286
2017-02-09 20:00 | 1272 | 1269
2017-02-09 20:30 | 1221 | 1218
2017-02-09 21:00 | 1156 | 1153
2017-02-09 21:30 | 1088 | 1087
2017-02-09 22:00 | 1021 | 1017
2017-02-09 22:30 | 976 | 975
2017-02-09 23:00 | 957 | 957
2017-02-09 23:30 | 893 | 892
2017-02-10 | 836 | 831
2017-02-10 00:30 | 792 | 786
2017-02-10 01:00 | 765 | 760
2017-02-10 01:30 | 735 | 729
2017-02-10 02:00 | 719 | 713
2017-02-10 02:30 | 709 | 702
2017-02-10 03:00 | 702 | 693
2017-02-10 03:30 | 697 | 688
2017-02-10 04:00 | 696 | 688
2017-02-10 04:30 | 709 | 700
2017-02-10 05:00 | 718 | 711
2017-02-10 05:30 | 755 | 749
2017-02-10 06:00 | 790 | 783
2017-02-10 06:30 | 853 | 849
2017-02-10 07:00 | 921 | 921
2017-02-10 07:30 | 989 | 989
2017-02-10 08:00 | 1021 | 1021
2017-02-10 08:30 | 1050 | 1050
2017-02-10 09:00 | 1083 | 1083
2017-02-10 09:30 | 1106 | 1105
2017-02-10 10:00 | 1111 | 1111
2017-02-10 10:30 | 1117 | 1117
2017-02-10 11:00 | 1131 | 1131
2017-02-10 11:30 | 1147 | 1145
2017-02-10 12:00 | 1165 | 1163
2017-02-10 12:30 | 1185 | 1184
2017-02-10 13:00 | 1204 | 1203
2017-02-10 13:30 | 1223 | 1223
2017-02-10 14:00 | 1247 | 1247
2017-02-10 14:30 | 1258 | 1258
2017-02-10 15:00 | 1276 | 1276
2017-02-10 15:30 | 1288 | 1288
2017-02-10 16:00 | 1326 | 1324
2017-02-10 16:30 | 1332 | 1330
2017-02-10 17:00 | 1351 | 1350
2017-02-10 17:30 | 1323 | 1315
2017-02-10 18:00 | 1276 | 1269
2017-02-10 18:30 | 1220 | 1217
2017-02-10 19:00 | 1240 | 1239
2017-02-10 19:30 | 1246 | 1246
2017-02-10 20:00 | 1235 | 1234
2017-02-10 20:30 | 1208 | 1206
2017-02-10 21:00 | 1154 | 1153
2017-02-10 21:30 | 1124 | 1121
2017-02-10 22:00 | 1081 | 1078
2017-02-10 22:30 | 1009 | 1006
2017-02-10 23:00 | 990 | 987
2017-02-10 23:30 | 919 | 915
2017-02-11 | 860 | 857
2017-02-11 00:30 | 813 | 808
2017-02-11 01:00 | 786 | 778
2017-02-11 01:30 | 743 | 737
2017-02-11 02:00 | 715 | 714
2017-02-11 02:30 | 704 | 703
2017-02-11 03:00 | 689 | 688
2017-02-11 03:30 | 685 | 684
2017-02-11 04:00 | 677 | 676
2017-02-11 04:30 | 679 | 678
2017-02-11 05:00 | 687 | 686
2017-02-11 05:30 | 697 | 696
2017-02-11 06:00 | 705 | 704
2017-02-11 06:30 | 739 | 739
2017-02-11 07:00 | 768 | 768
2017-02-11 07:30 | 815 | 815
2017-02-11 08:00 | 848 | 848
2017-02-11 08:30 | 897 | 896
2017-02-11 09:00 | 935 | 935
2017-02-11 09:30 | 978 | 978
2017-02-11 10:00 | 1014 | 1014
2017-02-11 10:30 | 1059 | 1059
2017-02-11 11:00 | 1093 | 1093
2017-02-11 11:30 | 1120 | 1120
2017-02-11 12:00 | 1163 | 1163
2017-02-11 12:30 | 1167 | 1164
2017-02-11 13:00 | 1201 | 1199
2017-02-11 13:30 | 1238 | 1238
2017-02-11 14:00 | 1241 | 1240
2017-02-11 14:30 | 1286 | 1286
2017-02-11 15:00 | 1317 | 1317
2017-02-11 15:30 | 1329 | 1329
2017-02-11 16:00 | 1347 | 1347
2017-02-11 16:30 | 1362 | 1362
2017-02-11 17:00 | 1378 | 1378
2017-02-11 17:30 | 1374 | 1374
2017-02-11 18:00 | 1347 | 1347
2017-02-11 18:30 | 1326 | 1326
2017-02-11 19:00 | 1322 | 1320
2017-02-11 19:30 | 1320 | 1319
2017-02-11 20:00 | 1291 | 1290
2017-02-11 20:30 | 1237 | 1235
2017-02-11 21:00 | 1190 | 1188
2017-02-11 21:30 | 1137 | 1132
2017-02-11 22:00 | 1065 | 1056
2017-02-11 22:30 | 1027 | 1021
2017-02-11 23:00 | 996 | 994
2017-02-11 23:30 | 927 | 924
2017-02-12 | 876 | 871
2017-02-12 00:30 | 828 | 823
2017-02-12 01:00 | 799 | 792
2017-02-12 01:30 | 763 | 757
2017-02-12 02:00 | 731 | 730
2017-02-12 02:30 | 709 | 709
2017-02-12 03:00 | 707 | 707
2017-02-12 03:30 | 699 | 699
2017-02-12 04:00 | 690 | 690
2017-02-12 04:30 | 702 | 702
2017-02-12 05:00 | 697 | 697
2017-02-12 05:30 | 693 | 693
2017-02-12 06:00 | 704 | 703
2017-02-12 06:30 | 725 | 725
2017-02-12 07:00 | 754 | 754
2017-02-12 07:30 | 798 | 796
2017-02-12 08:00 | 839 | 837
2017-02-12 08:30 | 887 | 886
2017-02-12 09:00 | 936 | 934
2017-02-12 09:30 | 980 | 980
2017-02-12 10:00 | 1040 | 1040
2017-02-12 10:30 | 1092 | 1092
2017-02-12 11:00 | 1154 | 1154
2017-02-12 11:30 | 1204 | 1203
2017-02-12 12:00 | 1262 | 1261
2017-02-12 12:30 | 1309 | 1309
2017-02-12 13:00 | 1335 | 1335
2017-02-12 13:30 | 1350 | 1350
2017-02-12 14:00 | 1379 | 1379
2017-02-12 14:30 | 1405 | 1405
2017-02-12 15:00 | 1434 | 1434
2017-02-12 15:30 | 1466 | 1466
2017-02-12 16:00 | 1502 | 1501
2017-02-12 16:30 | 1531 | 1530
2017-02-12 17:00 | 1547 | 1546
2017-02-12 17:30 | 1557 | 1556
2017-02-12 18:00 | 1550 | 1550
2017-02-12 18:30 | 1523 | 1523
2017-02-12 19:00 | 1524 | 1523
2017-02-12 19:30 | 1512 | 1511
2017-02-12 20:00 | 1476 | 1476
2017-02-12 20:30 | 1442 | 1440
2017-02-12 21:00 | 1344 | 1343
2017-02-12 21:30 | 1230 | 1228
2017-02-12 22:00 | 1157 | 1148
2017-02-12 22:30 | 1114 | 1109
2017-02-12 23:00 | 1059 | 1051
2017-02-12 23:30 | 988 | 977
2017-02-13 | 941 | 931
2017-02-13 00:30 | 888 | 880
2017-02-13 01:00 | 854 | 853
2017-02-13 01:30 | 831 | 831
2017-02-13 02:00 | 812 | 811
2017-02-13 02:30 | 800 | 799
2017-02-13 03:00 | 789 | 788
2017-02-13 03:30 | 788 | 786
2017-02-13 04:00 | 773 | 770
2017-02-13 04:30 | 812 | 812
2017-02-13 05:00 | 828 | 828
2017-02-13 05:30 | 866 | 866
2017-02-13 06:00 | 898 | 897
2017-02-13 06:30 | 993 | 991
2017-02-13 07:00 | 1048 | 1047
2017-02-13 07:30 | 1142 | 1141
2017-02-13 08:00 | 1197 | 1197
2017-02-13 08:30 | 1209 | 1208
2017-02-13 09:00 | 1218 | 1218
2017-02-13 09:30 | 1301 | 1300
2017-02-13 10:00 | 1359 | 1358
2017-02-13 10:30 | 1361 | 1361
2017-02-13 11:00 | 1374 | 1373
2017-02-13 11:30 | 1411 | 1411
2017-02-13 12:00 | 1423 | 1422
2017-02-13 12:30 | 1445 | 1444
2017-02-13 13:00 | 1458 | 1458
2017-02-13 13:30 | 1451 | 1451
2017-02-13 14:00 | 1455 | 1455
2017-02-13 14:30 | 1438 | 1438
2017-02-13 15:00 | 1440 | 1439
2017-02-13 15:30 | 1429 | 1426
2017-02-13 16:00 | 1436 | 1433
2017-02-13 16:30 | 1453 | 1450
2017-02-13 17:00 | 1440 | 1433
2017-02-13 17:30 | 1355 | 1345
2017-02-13 18:00 | 1292 | 1289
2017-02-13 18:30 | 1239 | 1229
2017-02-13 19:00 | 1222 | 1214
2017-02-13 19:30 | 1254 | 1244
2017-02-13 20:00 | 1210 | 1201
2017-02-13 20:30 | 1219 | 1211
2017-02-13 21:00 | 1203 | 1191
2017-02-13 21:30 | 1115 | 1110
2017-02-13 22:00 | 1062 | 1059
2017-02-13 22:30 | 968 | 964
2017-02-13 23:00 | 954 | 952
2017-02-13 23:30 | 903 | 901
2017-02-14 | 866 | 865
2017-02-14 00:30 | 831 | 829
2017-02-14 01:00 | 825 | 823
2017-02-14 01:30 | 780 | 775
2017-02-14 02:00 | 755 | 749
2017-02-14 02:30 | 741 | 736
2017-02-14 03:00 | 729 | 724
2017-02-14 03:30 | 731 | 726
2017-02-14 04:00 | 729 | 724
2017-02-14 04:30 | 736 | 732
2017-02-14 05:00 | 750 | 749
2017-02-14 05:30 | 788 | 787
2017-02-14 06:00 | 818 | 818
2017-02-14 06:30 | 893 | 893
2017-02-14 07:00 | 972 | 970
2017-02-14 07:30 | 1036 | 1035
2017-02-14 08:00 | 1067 | 1066
2017-02-14 08:30 | 1089 | 1088
2017-02-14 09:00 | 1100 | 1099
2017-02-14 09:30 | 1113 | 1111
2017-02-14 10:00 | 1138 | 1133
2017-02-14 10:30 | 1150 | 1143
2017-02-14 11:00 | 1135 | 1130
2017-02-14 11:30 | 1105 | 1099
2017-02-14 12:00 | 1085 | 1079
2017-02-14 12:30 | 1079 | 1072
2017-02-14 13:00 | 1073 | 1066
2017-02-14 13:30 | 1081 | 1075
2017-02-14 14:00 | 1090 | 1084
2017-02-14 14:30 | 1094 | 1090
2017-02-14 15:00 | 1112 | 1108
2017-02-14 15:30 | 1114 | 1109
2017-02-14 16:00 | 1136 | 1132
2017-02-14 16:30 | 1168 | 1164
2017-02-14 17:00 | 1192 | 1186
2017-02-14 17:30 | 1187 | 1178
2017-02-14 18:00 | 1169 | 1159
2017-02-14 18:30 | 1143 | 1131
2017-02-14 19:00 | 1157 | 1150
2017-02-14 19:30 | 1156 | 1149
2017-02-14 20:00 | 1140 | 1135
2017-02-14 20:30 | 1095 | 1088
2017-02-14 21:00 | 1030 | 1029
2017-02-14 21:30 | 989 | 988
2017-02-14 22:00 | 947 | 945
2017-02-14 22:30 | 916 | 911
2017-02-14 23:00 | 896 | 891
2017-02-14 23:30 | 831 | 826
2017-02-15 | 781 | 777
2017-02-15 00:30 | 746 | 743
2017-02-15 01:00 | 716 | 712
2017-02-15 01:30 | 695 | 692
2017-02-15 02:00 | 681 | 678
2017-02-15 02:30 | 674 | 671
2017-02-15 03:00 | 666 | 662
2017-02-15 03:30 | 664 | 661
2017-02-15 04:00 | 664 | 661
2017-02-15 04:30 | 677 | 674
2017-02-15 05:00 | 689 | 687
2017-02-15 05:30 | 725 | 725
2017-02-15 06:00 | 755 | 755
2017-02-15 06:30 | 821 | 819
2017-02-15 07:00 | 879 | 876
2017-02-15 07:30 | 935 | 935
2017-02-15 08:00 | 976 | 971
2017-02-15 08:30 | 1001 | 999
2017-02-15 09:00 | 1008 | 1006
2017-02-15 09:30 | 1011 | 1010
2017-02-15 10:00 | 1018 | 1016
2017-02-15 10:30 | 1033 | 1031
2017-02-15 11:00 | 1054 | 1053
2017-02-15 11:30 | 1082 | 1079
2017-02-15 12:00 | 1080 | 1077
2017-02-15 12:30 | 1050 | 1043
2017-02-15 13:00 | 1049 | 1044
2017-02-15 13:30 | 1061 | 1057
2017-02-15 14:00 | 1066 | 1062
2017-02-15 14:30 | 1078 | 1075
2017-02-15 15:00 | 1089 | 1086
2017-02-15 15:30 | 1101 | 1098
2017-02-15 16:00 | 1130 | 1127
2017-02-15 16:30 | 1156 | 1153
2017-02-15 17:00 | 1172 | 1168
2017-02-15 17:30 | 1167 | 1159
2017-02-15 18:00 | 1152 | 1140
2017-02-15 18:30 | 1129 | 1116
2017-02-15 19:00 | 1139 | 1139
2017-02-15 19:30 | 1135 | 1135
2017-02-15 20:00 | 1122 | 1121
2017-02-15 20:30 | 1091 | 1090
2017-02-15 21:00 | 1042 | 1042
2017-02-15 21:30 | 985 | 985
2017-02-15 22:00 | 934 | 934
2017-02-15 22:30 | 899 | 898
2017-02-15 23:00 | 881 | 881
2017-02-15 23:30 | 817 | 817
2017-02-16 | 772 | 772
2017-02-16 00:30 | 731 | 730
2017-02-16 01:00 | 707 | 705
2017-02-16 01:30 | 690 | 688
2017-02-16 02:00 | 675 | 672
2017-02-16 02:30 | 665 | 661
2017-02-16 03:00 | 657 | 653
2017-02-16 03:30 | 659 | 656
2017-02-16 04:00 | 659 | 657
2017-02-16 04:30 | 668 | 666
2017-02-16 05:00 | 683 | 682
2017-02-16 05:30 | 723 | 723
2017-02-16 06:00 | 754 | 754
2017-02-16 06:30 | 822 | 822
2017-02-16 07:00 | 883 | 882
2017-02-16 07:30 | 944 | 944
2017-02-16 08:00 | 965 | 964
2017-02-16 08:30 | 969 | 968
2017-02-16 09:00 | 983 | 982
2017-02-16 09:30 | 1004 | 1004
2017-02-16 10:00 | 1018 | 1017
2017-02-16 10:30 | 1022 | 1021
2017-02-16 11:00 | 1025 | 1025
2017-02-16 11:30 | 1029 | 1029
2017-02-16 12:00 | 1036 | 1036
2017-02-16 12:30 | 1046 | 1046
2017-02-16 13:00 | 1064 | 1063
2017-02-16 13:30 | 1076 | 1076
2017-02-16 14:00 | 1101 | 1100
2017-02-16 14:30 | 1124 | 1123
2017-02-16 15:00 | 1141 | 1141
2017-02-16 15:30 | 1179 | 1179
2017-02-16 16:00 | 1198 | 1198
2017-02-16 16:30 | 1221 | 1221
2017-02-16 17:00 | 1245 | 1245
2017-02-16 17:30 | 1239 | 1238
2017-02-16 18:00 | 1219 | 1217
2017-02-16 18:30 | 1192 | 1188
2017-02-16 19:00 | 1203 | 1200
2017-02-16 19:30 | 1196 | 1194
2017-02-16 20:00 | 1179 | 1179
2017-02-16 20:30 | 1146 | 1144
2017-02-16 21:00 | 1083 | 1081
2017-02-16 21:30 | 1018 | 1016
2017-02-16 22:00 | 945 | 944
2017-02-16 22:30 | 906 | 906
2017-02-16 23:00 | 895 | 895
2017-02-16 23:30 | 830 | 828
2017-02-17 | 783 | 781
2017-02-17 00:30 | 741 | 739
2017-02-17 01:00 | 717 | 715
2017-02-17 01:30 | 692 | 690
2017-02-17 02:00 | 669 | 666
2017-02-17 02:30 | 665 | 662
2017-02-17 03:00 | 657 | 655
2017-02-17 03:30 | 657 | 654
2017-02-17 04:00 | 659 | 656
2017-02-17 04:30 | 669 | 667
2017-02-17 05:00 | 681 | 679
2017-02-17 05:30 | 720 | 715
2017-02-17 06:00 | 753 | 748
2017-02-17 06:30 | 825 | 821
2017-02-17 07:00 | 889 | 885
2017-02-17 07:30 | 953 | 950
2017-02-17 08:00 | 982 | 980
2017-02-17 08:30 | 1004 | 1003
2017-02-17 09:00 | 1016 | 1015
2017-02-17 09:30 | 1029 | 1027
2017-02-17 10:00 | 1038 | 1036
2017-02-17 10:30 | 1028 | 1025
2017-02-17 11:00 | 1022 | 1019
2017-02-17 11:30 | 1028 | 1026
2017-02-17 12:00 | 1039 | 1037
2017-02-17 12:30 | 1055 | 1052
2017-02-17 13:00 | 1079 | 1077
2017-02-17 13:30 | 1106 | 1102
2017-02-17 14:00 | 1130 | 1127
2017-02-17 14:30 | 1154 | 1150
2017-02-17 15:00 | 1163 | 1159
2017-02-17 15:30 | 1190 | 1186
2017-02-17 16:00 | 1224 | 1220
2017-02-17 16:30 | 1242 | 1240
2017-02-17 17:00 | 1247 | 1245
2017-02-17 17:30 | 1223 | 1217
2017-02-17 18:00 | 1188 | 1176
2017-02-17 18:30 | 1136 | 1128
2017-02-17 19:00 | 1136 | 1135
2017-02-17 19:30 | 1132 | 1131
2017-02-17 20:00 | 1111 | 1110
2017-02-17 20:30 | 1082 | 1081
2017-02-17 21:00 | 1024 | 1024
2017-02-17 21:30 | 980 | 979
2017-02-17 22:00 | 938 | 937
2017-02-17 22:30 | 915 | 913
2017-02-17 23:00 | 899 | 897
2017-02-17 23:30 | 843 | 837
2017-02-18 | 783 | 782
2017-02-18 00:30 | 744 | 742
2017-02-18 01:00 | 720 | 719
2017-02-18 01:30 | 697 | 696
2017-02-18 02:00 | 681 | 679
2017-02-18 02:30 | 671 | 670
2017-02-18 03:00 | 665 | 663
2017-02-18 03:30 | 657 | 655
2017-02-18 04:00 | 656 | 653
2017-02-18 04:30 | 658 | 656
2017-02-18 05:00 | 665 | 662
2017-02-18 05:30 | 673 | 671
2017-02-18 06:00 | 678 | 675
2017-02-18 06:30 | 701 | 700
2017-02-18 07:00 | 725 | 725
2017-02-18 07:30 | 757 | 756
2017-02-18 08:00 | 787 | 786
2017-02-18 08:30 | 826 | 826
2017-02-18 09:00 | 842 | 842
2017-02-18 09:30 | 851 | 850
2017-02-18 10:00 | 864 | 863
2017-02-18 10:30 | 871 | 870
2017-02-18 11:00 | 885 | 883
2017-02-18 11:30 | 909 | 908
2017-02-18 12:00 | 921 | 920
2017-02-18 12:30 | 931 | 929
2017-02-18 13:00 | 944 | 943
2017-02-18 13:30 | 955 | 955
2017-02-18 14:00 | 973 | 971
2017-02-18 14:30 | 994 | 992
2017-02-18 15:00 | 1016 | 1014
2017-02-18 15:30 | 1047 | 1045
2017-02-18 16:00 | 1072 | 1064
2017-02-18 16:30 | 1093 | 1084
2017-02-18 17:00 | 1118 | 1110
2017-02-18 17:30 | 1115 | 1105
2017-02-18 18:00 | 1102 | 1087
2017-02-18 18:30 | 1089 | 1072
2017-02-18 19:00 | 1093 | 1087
2017-02-18 19:30 | 1089 | 1085
2017-02-18 20:00 | 1078 | 1075
2017-02-18 20:30 | 1045 | 1042
2017-02-18 21:00 | 1004 | 1003
2017-02-18 21:30 | 976 | 976
2017-02-18 22:00 | 945 | 944
2017-02-18 22:30 | 922 | 921
2017-02-18 23:00 | 919 | 918
2017-02-18 23:30 | 864 | 863
2017-02-19 | 817 | 817
2017-02-19 00:30 | 772 | 771
2017-02-19 01:00 | 742 | 741
2017-02-19 01:30 | 736 | 733
2017-02-19 02:00 | 706 | 701
2017-02-19 02:30 | 702 | 699
2017-02-19 03:00 | 693 | 691
2017-02-19 03:30 | 687 | 685
2017-02-19 04:00 | 676 | 674
2017-02-19 04:30 | 671 | 668
2017-02-19 05:00 | 671 | 668
2017-02-19 05:30 | 672 | 669
2017-02-19 06:00 | 675 | 671
2017-02-19 06:30 | 692 | 688
2017-02-19 07:00 | 707 | 705
2017-02-19 07:30 | 741 | 740
2017-02-19 08:00 | 764 | 764
2017-02-19 08:30 | 769 | 768
2017-02-19 09:00 | 789 | 789
2017-02-19 09:30 | 798 | 798
2017-02-19 10:00 | 821 | 820
2017-02-19 10:30 | 842 | 842
2017-02-19 11:00 | 866 | 865
2017-02-19 11:30 | 903 | 903
2017-02-19 12:00 | 957 | 957
2017-02-19 12:30 | 970 | 968
2017-02-19 13:00 | 1023 | 1022
2017-02-19 13:30 | 1076 | 1075
2017-02-19 14:00 | 1102 | 1102
2017-02-19 14:30 | 1130 | 1130
2017-02-19 15:00 | 1151 | 1151
2017-02-19 15:30 | 1166 | 1165
2017-02-19 16:00 | 1165 | 1165
2017-02-19 16:30 | 1151 | 1150
2017-02-19 17:00 | 1150 | 1149
2017-02-19 17:30 | 1140 | 1137
2017-02-19 18:00 | 1139 | 1135
2017-02-19 18:30 | 1138 | 1134
2017-02-19 19:00 | 1139 | 1136
2017-02-19 19:30 | 1111 | 1108
2017-02-19 20:00 | 1095 | 1094
2017-02-19 20:30 | 1055 | 1053
2017-02-19 21:00 | 990 | 990
2017-02-19 21:30 | 948 | 948
2017-02-19 22:00 | 918 | 918
2017-02-19 22:30 | 891 | 889
2017-02-19 23:00 | 867 | 866
2017-02-19 23:30 | 809 | 806
2017-02-20 | 759 | 753
2017-02-20 00:30 | 723 | 720
2017-02-20 01:00 | 701 | 699
2017-02-20 01:30 | 683 | 681
2017-02-20 02:00 | 670 | 667
2017-02-20 02:30 | 665 | 662
2017-02-20 03:00 | 658 | 655
2017-02-20 03:30 | 657 | 655
2017-02-20 04:00 | 658 | 655
2017-02-20 04:30 | 668 | 666
2017-02-20 05:00 | 684 | 683
2017-02-20 05:30 | 718 | 716
2017-02-20 06:00 | 757 | 752
2017-02-20 06:30 | 827 | 822
2017-02-20 07:00 | 884 | 882
2017-02-20 07:30 | 958 | 958
2017-02-20 08:00 | 979 | 978
2017-02-20 08:30 | 990 | 988
2017-02-20 09:00 | 990 | 989
2017-02-20 09:30 | 993 | 992
2017-02-20 10:00 | 993 | 993
2017-02-20 10:30 | 997 | 997
2017-02-20 11:00 | 1007 | 1006
2017-02-20 11:30 | 1032 | 1032
2017-02-20 12:00 | 1041 | 1041
2017-02-20 12:30 | 1051 | 1050
2017-02-20 13:00 | 1055 | 1054
2017-02-20 13:30 | 1065 | 1065
2017-02-20 14:00 | 1074 | 1074
2017-02-20 14:30 | 1085 | 1084
2017-02-20 15:00 | 1091 | 1090
2017-02-20 15:30 | 1122 | 1122
2017-02-20 16:00 | 1165 | 1165
2017-02-20 16:30 | 1197 | 1195
2017-02-20 17:00 | 1209 | 1207
2017-02-20 17:30 | 1206 | 1201
2017-02-20 18:00 | 1191 | 1180
2017-02-20 18:30 | 1163 | 1151
2017-02-20 19:00 | 1177 | 1170
2017-02-20 19:30 | 1166 | 1160
2017-02-20 20:00 | 1150 | 1144
2017-02-20 20:30 | 1113 | 1110
2017-02-20 21:00 | 1058 | 1056
2017-02-20 21:30 | 1018 | 1015
2017-02-20 22:00 | 967 | 965
2017-02-20 22:30 | 935 | 931
2017-02-20 23:00 | 917 | 912
2017-02-20 23:30 | 839 | 836
2017-02-21 | 787 | 784
2017-02-21 00:30 | 743 | 740
2017-02-21 01:00 | 719 | 716
2017-02-21 01:30 | 696 | 695
2017-02-21 02:00 | 680 | 678
2017-02-21 02:30 | 673 | 671
2017-02-21 03:00 | 664 | 661
2017-02-21 03:30 | 660 | 657
2017-02-21 04:00 | 661 | 658
2017-02-21 04:30 | 672 | 670
2017-02-21 05:00 | 685 | 684
2017-02-21 05:30 | 721 | 720
2017-02-21 06:00 | 766 | 762
2017-02-21 06:30 | 833 | 829
2017-02-21 07:00 | 905 | 898
2017-02-21 07:30 | 967 | 962
2017-02-21 08:00 | 992 | 989
2017-02-21 08:30 | 1018 | 1015
2017-02-21 09:00 | 1034 | 1030
2017-02-21 09:30 | 1051 | 1045
2017-02-21 10:00 | 1060 | 1056
2017-02-21 10:30 | 1062 | 1056
2017-02-21 11:00 | 1064 | 1056
2017-02-21 11:30 | 1066 | 1055
2017-02-21 12:00 | 1079 | 1068
2017-02-21 12:30 | 1090 | 1080
2017-02-21 13:00 | 1091 | 1080
2017-02-21 13:30 | 1104 | 1094
2017-02-21 14:00 | 1119 | 1111
2017-02-21 14:30 | 1144 | 1136
2017-02-21 15:00 | 1158 | 1146
2017-02-21 15:30 | 1180 | 1168
2017-02-21 16:00 | 1208 | 1196
2017-02-21 16:30 | 1222 | 1209
2017-02-21 17:00 | 1218 | 1202
2017-02-21 17:30 | 1191 | 1172
2017-02-21 18:00 | 1161 | 1141
2017-02-21 18:30 | 1134 | 1114
2017-02-21 19:00 | 1148 | 1134
2017-02-21 19:30 | 1131 | 1122
2017-02-21 20:00 | 1115 | 1108
2017-02-21 20:30 | 1081 | 1073
2017-02-21 21:00 | 1021 | 1018
2017-02-21 21:30 | 973 | 971
2017-02-21 22:00 | 930 | 929
2017-02-21 22:30 | 891 | 891
2017-02-21 23:00 | 881 | 880
2017-02-21 23:30 | 821 | 818
2017-02-22 | 764 | 761
2017-02-22 00:30 | 722 | 720
2017-02-22 01:00 | 701 | 698
2017-02-22 01:30 | 685 | 679
2017-02-22 02:00 | 670 | 664
2017-02-22 02:30 | 663 | 655
2017-02-22 03:00 | 653 | 645
2017-02-22 03:30 | 649 | 642
2017-02-22 04:00 | 649 | 642
2017-02-22 04:30 | 659 | 653
2017-02-22 05:00 | 673 | 669
2017-02-22 05:30 | 711 | 710
2017-02-22 06:00 | 749 | 748
2017-02-22 06:30 | 811 | 810
2017-02-22 07:00 | 874 | 869
2017-02-22 07:30 | 935 | 928
2017-02-22 08:00 | 947 | 941
2017-02-22 08:30 | 975 | 973
2017-02-22 09:00 | 971 | 969
2017-02-22 09:30 | 980 | 978
2017-02-22 10:00 | 984 | 982
2017-02-22 10:30 | 988 | 986
2017-02-22 11:00 | 994 | 993
2017-02-22 11:30 | 991 | 990
2017-02-22 12:00 | 991 | 990
2017-02-22 12:30 | 995 | 993
2017-02-22 13:00 | 998 | 997
2017-02-22 13:30 | 1014 | 1013
2017-02-22 14:00 | 1027 | 1025
2017-02-22 14:30 | 1024 | 1021
2017-02-22 15:00 | 1029 | 1026
2017-02-22 15:30 | 1049 | 1047
2017-02-22 16:00 | 1077 | 1075
2017-02-22 16:30 | 1101 | 1099
2017-02-22 17:00 | 1115 | 1113
2017-02-22 17:30 | 1114 | 1110
2017-02-22 18:00 | 1088 | 1082
2017-02-22 18:30 | 1068 | 1063
2017-02-22 19:00 | 1085 | 1083
2017-02-22 19:30 | 1078 | 1075
2017-02-22 20:00 | 1066 | 1061
2017-02-22 20:30 | 1032 | 1024
2017-02-22 21:00 | 975 | 973
2017-02-22 21:30 | 932 | 932
2017-02-22 22:00 | 893 | 892
2017-02-22 22:30 | 864 | 863
2017-02-22 23:00 | 856 | 854
2017-02-22 23:30 | 793 | 792
2017-02-23 | 744 | 743
2017-02-23 00:30 | 701 | 698
2017-02-23 01:00 | 682 | 679
2017-02-23 01:30 | 670 | 665
2017-02-23 02:00 | 655 | 649
2017-02-23 02:30 | 650 | 644
2017-02-23 03:00 | 646 | 640
2017-02-23 03:30 | 644 | 639
2017-02-23 04:00 | 645 | 638
2017-02-23 04:30 | 654 | 649
2017-02-23 05:00 | 670 | 666
2017-02-23 05:30 | 707 | 706
2017-02-23 06:00 | 736 | 735
2017-02-23 06:30 | 804 | 804
2017-02-23 07:00 | 864 | 863
2017-02-23 07:30 | 911 | 911
2017-02-23 08:00 | 918 | 918
2017-02-23 08:30 | 925 | 925
2017-02-23 09:00 | 926 | 926
2017-02-23 09:30 | 933 | 933
2017-02-23 10:00 | 948 | 946
2017-02-23 10:30 | 954 | 951
2017-02-23 11:00 | 970 | 968
2017-02-23 11:30 | 982 | 978
2017-02-23 12:00 | 998 | 995
2017-02-23 12:30 | 1005 | 1003
2017-02-23 13:00 | 1014 | 1012
2017-02-23 13:30 | 1023 | 1021
2017-02-23 14:00 | 1044 | 1042
2017-02-23 14:30 | 1046 | 1044
2017-02-23 15:00 | 1069 | 1065
2017-02-23 15:30 | 1081 | 1073
2017-02-23 16:00 | 1108 | 1101
2017-02-23 16:30 | 1140 | 1134
2017-02-23 17:00 | 1152 | 1147
2017-02-23 17:30 | 1158 | 1150
2017-02-23 18:00 | 1152 | 1141
2017-02-23 18:30 | 1129 | 1120
2017-02-23 19:00 | 1148 | 1142
2017-02-23 19:30 | 1137 | 1130
2017-02-23 20:00 | 1121 | 1115
2017-02-23 20:30 | 1084 | 1079
2017-02-23 21:00 | 1020 | 1018
2017-02-23 21:30 | 962 | 961
2017-02-23 22:00 | 916 | 914
2017-02-23 22:30 | 881 | 879
2017-02-23 23:00 | 865 | 864
2017-02-23 23:30 | 804 | 803
2017-02-24 | 738 | 735
2017-02-24 00:30 | 704 | 701
2017-02-24 01:00 | 689 | 686
2017-02-24 01:30 | 665 | 659
2017-02-24 02:00 | 656 | 650
2017-02-24 02:30 | 645 | 638
2017-02-24 03:00 | 642 | 635
2017-02-24 03:30 | 644 | 637
2017-02-24 04:00 | 643 | 636
2017-02-24 04:30 | 648 | 642
2017-02-24 05:00 | 664 | 660
2017-02-24 05:30 | 700 | 698
2017-02-24 06:00 | 737 | 734
2017-02-24 06:30 | 792 | 789
2017-02-24 07:00 | 848 | 845
2017-02-24 07:30 | 903 | 901
2017-02-24 08:00 | 917 | 915
2017-02-24 08:30 | 929 | 927
2017-02-24 09:00 | 942 | 942
2017-02-24 09:30 | 963 | 962
2017-02-24 10:00 | 970 | 969
2017-02-24 10:30 | 976 | 976
2017-02-24 11:00 | 995 | 993
2017-02-24 11:30 | 1015 | 1012
2017-02-24 12:00 | 1025 | 1021
2017-02-24 12:30 | 994 | 991
2017-02-24 13:00 | 1002 | 1001
2017-02-24 13:30 | 1025 | 1025
2017-02-24 14:00 | 1054 | 1054
2017-02-24 14:30 | 1050 | 1050
2017-02-24 15:00 | 1062 | 1062
2017-02-24 15:30 | 1079 | 1078
2017-02-24 16:00 | 1103 | 1103
2017-02-24 16:30 | 1125 | 1125
2017-02-24 17:00 | 1136 | 1136
2017-02-24 17:30 | 1117 | 1117
2017-02-24 18:00 | 1090 | 1090
2017-02-24 18:30 | 1053 | 1053
2017-02-24 19:00 | 1068 | 1067
2017-02-24 19:30 | 1062 | 1061
2017-02-24 20:00 | 1043 | 1043
2017-02-24 20:30 | 1019 | 1019
2017-02-24 21:00 | 981 | 980
2017-02-24 21:30 | 947 | 946
2017-02-24 22:00 | 912 | 909
2017-02-24 22:30 | 881 | 878
2017-02-24 23:00 | 874 | 869
2017-02-24 23:30 | 812 | 808
2017-02-25 | 755 | 754
2017-02-25 00:30 | 718 | 715
2017-02-25 01:00 | 693 | 689
2017-02-25 01:30 | 667 | 662
2017-02-25 02:00 | 651 | 644
2017-02-25 02:30 | 637 | 630
2017-02-25 03:00 | 636 | 629
2017-02-25 03:30 | 630 | 622
2017-02-25 04:00 | 627 | 619
2017-02-25 04:30 | 628 | 620
2017-02-25 05:00 | 631 | 623
2017-02-25 05:30 | 640 | 633
2017-02-25 06:00 | 653 | 644
2017-02-25 06:30 | 673 | 667
2017-02-25 07:00 | 687 | 684
2017-02-25 07:30 | 715 | 714
2017-02-25 08:00 | 736 | 736
2017-02-25 08:30 | 758 | 757
2017-02-25 09:00 | 771 | 770
2017-02-25 09:30 | 782 | 782
2017-02-25 10:00 | 789 | 787
2017-02-25 10:30 | 804 | 803
2017-02-25 11:00 | 813 | 812
2017-02-25 11:30 | 814 | 814
2017-02-25 12:00 | 822 | 822
2017-02-25 12:30 | 828 | 827
2017-02-25 13:00 | 841 | 840
2017-02-25 13:30 | 849 | 849
2017-02-25 14:00 | 865 | 865
2017-02-25 14:30 | 877 | 877
2017-02-25 15:00 | 892 | 892
2017-02-25 15:30 | 915 | 915
2017-02-25 16:00 | 942 | 939
2017-02-25 16:30 | 959 | 957
2017-02-25 17:00 | 982 | 977
2017-02-25 17:30 | 979 | 973
2017-02-25 18:00 | 976 | 970
2017-02-25 18:30 | 967 | 959
2017-02-25 19:00 | 986 | 981
2017-02-25 19:30 | 969 | 964
2017-02-25 20:00 | 956 | 951
2017-02-25 20:30 | 926 | 924
2017-02-25 21:00 | 886 | 886
2017-02-25 21:30 | 862 | 862
2017-02-25 22:00 | 840 | 839
2017-02-25 22:30 | 822 | 820
2017-02-25 23:00 | 825 | 822
2017-02-25 23:30 | 778 | 771
2017-02-26 | 735 | 723
2017-02-26 00:30 | 696 | 688
2017-02-26 01:00 | 672 | 667
2017-02-26 01:30 | 657 | 650
2017-02-26 02:00 | 641 | 633
2017-02-26 02:30 | 633 | 625
2017-02-26 03:00 | 628 | 619
2017-02-26 03:30 | 625 | 614
2017-02-26 04:00 | 623 | 611
2017-02-26 04:30 | 622 | 611
2017-02-26 05:00 | 622 | 612
2017-02-26 05:30 | 627 | 617
2017-02-26 06:00 | 634 | 621
2017-02-26 06:30 | 640 | 627
2017-02-26 07:00 | 650 | 639
2017-02-26 07:30 | 672 | 666
2017-02-26 08:00 | 694 | 692
2017-02-26 08:30 | 726 | 726
2017-02-26 09:00 | 746 | 746
2017-02-26 09:30 | 770 | 770
2017-02-26 10:00 | 784 | 783
2017-02-26 10:30 | 779 | 776
2017-02-26 11:00 | 769 | 767
2017-02-26 11:30 | 764 | 762
2017-02-26 12:00 | 768 | 767
2017-02-26 12:30 | 789 | 786
2017-02-26 13:00 | 806 | 804
2017-02-26 13:30 | 807 | 806
2017-02-26 14:00 | 844 | 843
2017-02-26 14:30 | 869 | 864
2017-02-26 15:00 | 888 | 883
2017-02-26 15:30 | 890 | 885
2017-02-26 16:00 | 890 | 884
2017-02-26 16:30 | 902 | 895
2017-02-26 17:00 | 932 | 928
2017-02-26 17:30 | 945 | 940
2017-02-26 18:00 | 952 | 946
2017-02-26 18:30 | 963 | 957
2017-02-26 19:00 | 993 | 990
2017-02-26 19:30 | 982 | 979
2017-02-26 20:00 | 960 | 959
2017-02-26 20:30 | 937 | 936
2017-02-26 21:00 | 891 | 891
2017-02-26 21:30 | 855 | 855
2017-02-26 22:00 | 825 | 825
2017-02-26 22:30 | 809 | 808
2017-02-26 23:00 | 804 | 802
2017-02-26 23:30 | 755 | 752
2017-02-27 | 710 | 707
2017-02-27 00:30 | 673 | 668
2017-02-27 01:00 | 658 | 652
2017-02-27 01:30 | 643 | 635
2017-02-27 02:00 | 632 | 623
2017-02-27 02:30 | 626 | 617
2017-02-27 03:00 | 621 | 611
2017-02-27 03:30 | 623 | 613
2017-02-27 04:00 | 625 | 615
2017-02-27 04:30 | 634 | 626
2017-02-27 05:00 | 662 | 657
2017-02-27 05:30 | 692 | 690
2017-02-27 06:00 | 722 | 720
2017-02-27 06:30 | 793 | 791
2017-02-27 07:00 | 852 | 851
2017-02-27 07:30 | 904 | 901
2017-02-27 08:00 | 930 | 928
2017-02-27 08:30 | 941 | 939
2017-02-27 09:00 | 938 | 937
2017-02-27 09:30 | 940 | 940
2017-02-27 10:00 | 951 | 950
2017-02-27 10:30 | 947 | 946
2017-02-27 11:00 | 947 | 947
2017-02-27 11:30 | 955 | 954
2017-02-27 12:00 | 979 | 978
2017-02-27 12:30 | 974 | 971
2017-02-27 13:00 | 958 | 954
2017-02-27 13:30 | 963 | 958
2017-02-27 14:00 | 963 | 958
2017-02-27 14:30 | 955 | 948
2017-02-27 15:00 | 950 | 943
2017-02-27 15:30 | 948 | 940
2017-02-27 16:00 | 985 | 977
2017-02-27 16:30 | 998 | 990
2017-02-27 17:00 | 1013 | 1004
2017-02-27 17:30 | 1015 | 1002
2017-02-27 18:00 | 1011 | 995
2017-02-27 18:30 | 991 | 983
2017-02-27 19:00 | 1019 | 1017
2017-02-27 19:30 | 1004 | 1000
2017-02-27 20:00 | 984 | 983
2017-02-27 20:30 | 958 | 956
2017-02-27 21:00 | 906 | 904
2017-02-27 21:30 | 862 | 862
2017-02-27 22:00 | 824 | 823
2017-02-27 22:30 | 797 | 796
2017-02-27 23:00 | 798 | 797
2017-02-27 23:30 | 745 | 744
2017-02-28 | 702 | 699
2017-02-28 00:30 | 661 | 656
2017-02-28 01:00 | 640 | 634
2017-02-28 01:30 | 622 | 614
2017-02-28 02:00 | 612 | 604
2017-02-28 02:30 | 607 | 598
2017-02-28 03:00 | 600 | 590
2017-02-28 03:30 | 603 | 594
2017-02-28 04:00 | 608 | 600
2017-02-28 04:30 | 620 | 613
2017-02-28 05:00 | 631 | 626
2017-02-28 05:30 | 671 | 669
2017-02-28 06:00 | 705 | 704
2017-02-28 06:30 | 774 | 772
2017-02-28 07:00 | 840 | 835
2017-02-28 07:30 | 887 | 886
2017-02-28 08:00 | 903 | 901
2017-02-28 08:30 | 911 | 907
2017-02-28 09:00 | 909 | 907
2017-02-28 09:30 | 911 | 909
2017-02-28 10:00 | 907 | 906
2017-02-28 10:30 | 908 | 908
2017-02-28 11:00 | 919 | 919
2017-02-28 11:30 | 919 | 918
2017-02-28 12:00 | 932 | 930
2017-02-28 12:30 | 963 | 962
2017-02-28 13:00 | 948 | 947
2017-02-28 13:30 | 950 | 949
2017-02-28 14:00 | 963 | 962
2017-02-28 14:30 | 981 | 981
2017-02-28 15:00 | 995 | 995
2017-02-28 15:30 | 1026 | 1024
2017-02-28 16:00 | 1064 | 1059
2017-02-28 16:30 | 1083 | 1078
2017-02-28 17:00 | 1103 | 1098
2017-02-28 17:30 | 1103 | 1093
2017-02-28 18:00 | 1086 | 1070
2017-02-28 18:30 | 1062 | 1048
2017-02-28 19:00 | 1082 | 1076
2017-02-28 19:30 | 1059 | 1051
2017-02-28 20:00 | 1039 | 1031
2017-02-28 20:30 | 1010 | 1000
2017-02-28 21:00 | 950 | 945
2017-02-28 21:30 | 904 | 899
2017-02-28 22:00 | 864 | 855
2017-02-28 22:30 | 834 | 829
2017-02-28 23:00 | 824 | 820
2017-02-28 23:30 | 768 | 764
2017-03-01 | 722 | 717
2017-03-01 00:30 | 691 | 684
2017-03-01 01:00 | 666 | 660
2017-03-01 01:30 | 645 | 640
2017-03-01 02:00 | 634 | 629
2017-03-01 02:30 | 626 | 620
2017-03-01 03:00 | 623 | 616
2017-03-01 03:30 | 623 | 615
2017-03-01 04:00 | 624 | 619
2017-03-01 04:30 | 636 | 630
2017-03-01 05:00 | 649 | 645
2017-03-01 05:30 | 685 | 684
2017-03-01 06:00 | 724 | 721
2017-03-01 06:30 | 800 | 800
2017-03-01 07:00 | 855 | 852
2017-03-01 07:30 | 900 | 898
2017-03-01 08:00 | 924 | 919
2017-03-01 08:30 | 935 | 932
2017-03-01 09:00 | 946 | 945
2017-03-01 09:30 | 963 | 963
2017-03-01 10:00 | 986 | 986
2017-03-01 10:30 | 1002 | 1002
2017-03-01 11:00 | 1009 | 1009
2017-03-01 11:30 | 1014 | 1013
2017-03-01 12:00 | 1029 | 1024
2017-03-01 12:30 | 1038 | 1033
2017-03-01 13:00 | 1050 | 1046
2017-03-01 13:30 | 1058 | 1055
2017-03-01 14:00 | 1072 | 1069
2017-03-01 14:30 | 1090 | 1085
2017-03-01 15:00 | 1106 | 1100
2017-03-01 15:30 | 1143 | 1137
2017-03-01 16:00 | 1157 | 1150
2017-03-01 16:30 | 1146 | 1135
2017-03-01 17:00 | 1157 | 1144
2017-03-01 17:30 | 1155 | 1140
2017-03-01 18:00 | 1138 | 1125
2017-03-01 18:30 | 1119 | 1104
2017-03-01 19:00 | 1136 | 1129
2017-03-01 19:30 | 1117 | 1107
2017-03-01 20:00 | 1094 | 1090
2017-03-01 20:30 | 1074 | 1070
2017-03-01 21:00 | 1023 | 1021
2017-03-01 21:30 | 976 | 972
2017-03-01 22:00 | 926 | 920
2017-03-01 22:30 | 897 | 891
2017-03-01 23:00 | 885 | 878
2017-03-01 23:30 | 816 | 812
2017-03-02 | 761 | 759
2017-03-02 00:30 | 725 | 721
2017-03-02 01:00 | 701 | 695
2017-03-02 01:30 | 675 | 672
2017-03-02 02:00 | 665 | 661
2017-03-02 02:30 | 657 | 653
2017-03-02 03:00 | 652 | 647
2017-03-02 03:30 | 648 | 644
2017-03-02 04:00 | 648 | 644
2017-03-02 04:30 | 659 | 655
2017-03-02 05:00 | 672 | 670
2017-03-02 05:30 | 718 | 713
2017-03-02 06:00 | 754 | 748
2017-03-02 06:30 | 822 | 819
2017-03-02 07:00 | 886 | 881
2017-03-02 07:30 | 940 | 938
2017-03-02 08:00 | 958 | 954
2017-03-02 08:30 | 983 | 979
2017-03-02 09:00 | 1011 | 1008
2017-03-02 09:30 | 1055 | 1052
2017-03-02 10:00 | 1074 | 1068
2017-03-02 10:30 | 1077 | 1070
2017-03-02 11:00 | 1085 | 1079
2017-03-02 11:30 | 1091 | 1087
2017-03-02 12:00 | 1113 | 1109
2017-03-02 12:30 | 1127 | 1121
2017-03-02 13:00 | 1128 | 1122
2017-03-02 13:30 | 1120 | 1115
2017-03-02 14:00 | 1142 | 1136
2017-03-02 14:30 | 1163 | 1156
2017-03-02 15:00 | 1177 | 1169
2017-03-02 15:30 | 1183 | 1176
2017-03-02 16:00 | 1197 | 1190
2017-03-02 16:30 | 1203 | 1195
2017-03-02 17:00 | 1194 | 1184
2017-03-02 17:30 | 1191 | 1178
2017-03-02 18:00 | 1181 | 1169
2017-03-02 18:30 | 1172 | 1160
2017-03-02 19:00 | 1194 | 1186
2017-03-02 19:30 | 1186 | 1177
2017-03-02 20:00 | 1167 | 1159
2017-03-02 20:30 | 1139 | 1131
2017-03-02 21:00 | 1077 | 1076
2017-03-02 21:30 | 1025 | 1023
2017-03-02 22:00 | 967 | 963
2017-03-02 22:30 | 931 | 928
2017-03-02 23:00 | 912 | 911
2017-03-02 23:30 | 848 | 846
2017-03-03 | 797 | 795
2017-03-03 00:30 | 749 | 748
2017-03-03 01:00 | 717 | 716
2017-03-03 01:30 | 695 | 693
2017-03-03 02:00 | 683 | 680
2017-03-03 02:30 | 676 | 672
2017-03-03 03:00 | 665 | 660
2017-03-03 03:30 | 662 | 657
2017-03-03 04:00 | 662 | 657
2017-03-03 04:30 | 671 | 667
2017-03-03 05:00 | 680 | 678
2017-03-03 05:30 | 718 | 717
2017-03-03 06:00 | 745 | 744
2017-03-03 06:30 | 818 | 814
2017-03-03 07:00 | 881 | 879
2017-03-03 07:30 | 940 | 938
2017-03-03 08:00 | 964 | 961
2017-03-03 08:30 | 976 | 976
2017-03-03 09:00 | 1003 | 1003
2017-03-03 09:30 | 1038 | 1038
2017-03-03 10:00 | 1066 | 1063
2017-03-03 10:30 | 1077 | 1071
2017-03-03 11:00 | 1084 | 1078
2017-03-03 11:30 | 1098 | 1094
2017-03-03 12:00 | 1110 | 1108
2017-03-03 12:30 | 1131 | 1127
2017-03-03 13:00 | 1149 | 1143
2017-03-03 13:30 | 1134 | 1129
2017-03-03 14:00 | 1135 | 1133
2017-03-03 14:30 | 1153 | 1151
2017-03-03 15:00 | 1153 | 1149
2017-03-03 15:30 | 1158 | 1153
2017-03-03 16:00 | 1178 | 1172
2017-03-03 16:30 | 1190 | 1185
2017-03-03 17:00 | 1198 | 1193
2017-03-03 17:30 | 1172 | 1162
2017-03-03 18:00 | 1138 | 1129
2017-03-03 18:30 | 1127 | 1121
2017-03-03 19:00 | 1141 | 1138
2017-03-03 19:30 | 1134 | 1130
2017-03-03 20:00 | 1114 | 1111
2017-03-03 20:30 | 1088 | 1082
2017-03-03 21:00 | 1036 | 1034
2017-03-03 21:30 | 1003 | 1000
2017-03-03 22:00 | 964 | 962
2017-03-03 22:30 | 938 | 934
2017-03-03 23:00 | 928 | 924
2017-03-03 23:30 | 868 | 862
2017-03-04 | 807 | 806
2017-03-04 00:30 | 764 | 763
2017-03-04 01:00 | 732 | 731
2017-03-04 01:30 | 713 | 712
2017-03-04 02:00 | 693 | 691
2017-03-04 02:30 | 682 | 680
2017-03-04 03:00 | 674 | 670
2017-03-04 03:30 | 664 | 660
2017-03-04 04:00 | 662 | 658
2017-03-04 04:30 | 662 | 658
2017-03-04 05:00 | 670 | 667
2017-03-04 05:30 | 682 | 680
2017-03-04 06:00 | 691 | 688
2017-03-04 06:30 | 709 | 707
2017-03-04 07:00 | 738 | 737
2017-03-04 07:30 | 772 | 772
2017-03-04 08:00 | 791 | 791
2017-03-04 08:30 | 829 | 828
2017-03-04 09:00 | 858 | 858
2017-03-04 09:30 | 908 | 907
2017-03-04 10:00 | 923 | 923
2017-03-04 10:30 | 943 | 942
2017-03-04 11:00 | 949 | 948
2017-03-04 11:30 | 954 | 953
2017-03-04 12:00 | 957 | 956
2017-03-04 12:30 | 955 | 953
2017-03-04 13:00 | 938 | 935
2017-03-04 13:30 | 939 | 936
2017-03-04 14:00 | 967 | 966
2017-03-04 14:30 | 1010 | 1009
2017-03-04 15:00 | 1033 | 1031
2017-03-04 15:30 | 1046 | 1044
2017-03-04 16:00 | 1059 | 1057
2017-03-04 16:30 | 1057 | 1054
2017-03-04 17:00 | 1059 | 1057
2017-03-04 17:30 | 1053 | 1049
2017-03-04 18:00 | 1044 | 1038
2017-03-04 18:30 | 1041 | 1039
2017-03-04 19:00 | 1055 | 1053
2017-03-04 19:30 | 1048 | 1047
2017-03-04 20:00 | 1035 | 1033
2017-03-04 20:30 | 1006 | 1004
2017-03-04 21:00 | 972 | 969
2017-03-04 21:30 | 940 | 938
2017-03-04 22:00 | 906 | 903
2017-03-04 22:30 | 889 | 885
2017-03-04 23:00 | 863 | 862
2017-03-04 23:30 | 833 | 830
2017-03-05 | 784 | 780
2017-03-05 00:30 | 740 | 736
2017-03-05 01:00 | 714 | 709
2017-03-05 01:30 | 688 | 685
2017-03-05 02:00 | 669 | 667
2017-03-05 02:30 | 655 | 653
2017-03-05 03:00 | 638 | 635
2017-03-05 03:30 | 632 | 629
2017-03-05 04:00 | 630 | 626
2017-03-05 04:30 | 629 | 626
2017-03-05 05:00 | 633 | 630
2017-03-05 05:30 | 640 | 638
2017-03-05 06:00 | 646 | 643
2017-03-05 06:30 | 659 | 656
2017-03-05 07:00 | 673 | 671
2017-03-05 07:30 | 690 | 689
2017-03-05 08:00 | 708 | 708
2017-03-05 08:30 | 759 | 759
2017-03-05 09:00 | 793 | 793
2017-03-05 09:30 | 810 | 810
2017-03-05 10:00 | 809 | 809
2017-03-05 10:30 | 828 | 828
2017-03-05 11:00 | 854 | 854
2017-03-05 11:30 | 871 | 871
2017-03-05 12:00 | 887 | 887
2017-03-05 12:30 | 899 | 899
2017-03-05 13:00 | 910 | 910
2017-03-05 13:30 | 932 | 931
2017-03-05 14:00 | 962 | 960
2017-03-05 14:30 | 988 | 987
2017-03-05 15:00 | 1001 | 1001
2017-03-05 15:30 | 1034 | 1034
2017-03-05 16:00 | 1047 | 1046
2017-03-05 16:30 | 1080 | 1079
2017-03-05 17:00 | 1109 | 1109
2017-03-05 17:30 | 1116 | 1116
2017-03-05 18:00 | 1110 | 1110
2017-03-05 18:30 | 1106 | 1106
2017-03-05 19:00 | 1132 | 1131
2017-03-05 19:30 | 1113 | 1112
2017-03-05 20:00 | 1084 | 1082
2017-03-05 20:30 | 1062 | 1059
2017-03-05 21:00 | 1020 | 1015
2017-03-05 21:30 | 972 | 969
2017-03-05 22:00 | 940 | 932
2017-03-05 22:30 | 894 | 888
2017-03-05 23:00 | 888 | 883
2017-03-05 23:30 | 826 | 823
2017-03-06 | 777 | 773
2017-03-06 00:30 | 734 | 730
2017-03-06 01:00 | 707 | 702
2017-03-06 01:30 | 688 | 681
2017-03-06 02:00 | 667 | 663
2017-03-06 02:30 | 655 | 651
2017-03-06 03:00 | 652 | 648
2017-03-06 03:30 | 644 | 640
2017-03-06 04:00 | 647 | 643
2017-03-06 04:30 | 660 | 658
2017-03-06 05:00 | 672 | 671
2017-03-06 05:30 | 706 | 704
2017-03-06 06:00 | 740 | 740
2017-03-06 06:30 | 811 | 811
2017-03-06 07:00 | 878 | 873
2017-03-06 07:30 | 936 | 931
2017-03-06 08:00 | 965 | 958
2017-03-06 08:30 | 975 | 972
2017-03-06 09:00 | 988 | 984
2017-03-06 09:30 | 1006 | 1003
2017-03-06 10:00 | 1027 | 1023
2017-03-06 10:30 | 1033 | 1030
2017-03-06 11:00 | 1045 | 1042
2017-03-06 11:30 | 1063 | 1060
2017-03-06 12:00 | 1075 | 1073
2017-03-06 12:30 | 1087 | 1084
2017-03-06 13:00 | 1100 | 1097
2017-03-06 13:30 | 1109 | 1103
2017-03-06 14:00 | 1104 | 1098
2017-03-06 14:30 | 1106 | 1100
2017-03-06 15:00 | 1109 | 1101
2017-03-06 15:30 | 1123 | 1114
2017-03-06 16:00 | 1160 | 1153
2017-03-06 16:30 | 1181 | 1175
2017-03-06 17:00 | 1200 | 1193
2017-03-06 17:30 | 1187 | 1176
2017-03-06 18:00 | 1165 | 1152
2017-03-06 18:30 | 1145 | 1138
2017-03-06 19:00 | 1149 | 1146
2017-03-06 19:30 | 1120 | 1119
2017-03-06 20:00 | 1113 | 1112
2017-03-06 20:30 | 1085 | 1083
2017-03-06 21:00 | 1019 | 1017
2017-03-06 21:30 | 970 | 968
2017-03-06 22:00 | 931 | 925
2017-03-06 22:30 | 900 | 891
2017-03-06 23:00 | 880 | 875
2017-03-06 23:30 | 821 | 816
2017-03-07 | 775 | 767
2017-03-07 00:30 | 736 | 723
2017-03-07 01:00 | 712 | 701
2017-03-07 01:30 | 674 | 666
2017-03-07 02:00 | 661 | 658
2017-03-07 02:30 | 653 | 649
2017-03-07 03:00 | 649 | 646
2017-03-07 03:30 | 635 | 631
2017-03-07 04:00 | 624 | 620
2017-03-07 04:30 | 663 | 661
2017-03-07 05:00 | 673 | 672
2017-03-07 05:30 | 712 | 710
2017-03-07 06:00 | 744 | 739
2017-03-07 06:30 | 808 | 806
2017-03-07 07:00 | 862 | 859
2017-03-07 07:30 | 911 | 906
2017-03-07 08:00 | 925 | 920
2017-03-07 08:30 | 932 | 928
2017-03-07 09:00 | 937 | 933
2017-03-07 09:30 | 970 | 965
2017-03-07 10:00 | 969 | 965
2017-03-07 10:30 | 963 | 960
2017-03-07 11:00 | 967 | 965
2017-03-07 11:30 | 967 | 965
2017-03-07 12:00 | 972 | 970
2017-03-07 12:30 | 957 | 954
2017-03-07 13:00 | 966 | 964
2017-03-07 13:30 | 994 | 990
2017-03-07 14:00 | 1019 | 1010
2017-03-07 14:30 | 1033 | 1025
2017-03-07 15:00 | 1044 | 1035
2017-03-07 15:30 | 1059 | 1049
2017-03-07 16:00 | 1089 | 1081
2017-03-07 16:30 | 1115 | 1108
2017-03-07 17:00 | 1126 | 1117
2017-03-07 17:30 | 1119 | 1107
2017-03-07 18:00 | 1092 | 1080
2017-03-07 18:30 | 1070 | 1061
2017-03-07 19:00 | 1085 | 1080
2017-03-07 19:30 | 1066 | 1057
2017-03-07 20:00 | 1041 | 1030
2017-03-07 20:30 | 1010 | 1002
2017-03-07 21:00 | 947 | 945
2017-03-07 21:30 | 908 | 904
2017-03-07 22:00 | 870 | 864
2017-03-07 22:30 | 840 | 835
2017-03-07 23:00 | 827 | 821
2017-03-07 23:30 | 765 | 761
2017-03-08 | 724 | 714
2017-03-08 00:30 | 688 | 674
2017-03-08 01:00 | 671 | 656
2017-03-08 01:30 | 654 | 637
2017-03-08 02:00 | 642 | 622
2017-03-08 02:30 | 632 | 615
2017-03-08 03:00 | 617 | 608
2017-03-08 03:30 | 617 | 607
2017-03-08 04:00 | 621 | 612
2017-03-08 04:30 | 630 | 623
2017-03-08 05:00 | 640 | 635
2017-03-08 05:30 | 677 | 675
2017-03-08 06:00 | 701 | 701
2017-03-08 06:30 | 772 | 772
2017-03-08 07:00 | 826 | 826
2017-03-08 07:30 | 869 | 868
2017-03-08 08:00 | 884 | 882
2017-03-08 08:30 | 894 | 893
2017-03-08 09:00 | 906 | 906
2017-03-08 09:30 | 919 | 919
2017-03-08 10:00 | 928 | 927
2017-03-08 10:30 | 913 | 912
2017-03-08 11:00 | 919 | 918
2017-03-08 11:30 | 900 | 900
2017-03-08 12:00 | 898 | 897
2017-03-08 12:30 | 902 | 901
2017-03-08 13:00 | 915 | 914
2017-03-08 13:30 | 929 | 928
2017-03-08 14:00 | 964 | 962
2017-03-08 14:30 | 981 | 980
2017-03-08 15:00 | 994 | 992
2017-03-08 15:30 | 1016 | 1014
2017-03-08 16:00 | 1015 | 1012
2017-03-08 16:30 | 1035 | 1032
2017-03-08 17:00 | 1044 | 1040
2017-03-08 17:30 | 1037 | 1029
2017-03-08 18:00 | 1032 | 1020
2017-03-08 18:30 | 1022 | 1013
2017-03-08 19:00 | 1038 | 1033
2017-03-08 19:30 | 1017 | 1009
2017-03-08 20:00 | 1008 | 998
2017-03-08 20:30 | 977 | 967
2017-03-08 21:00 | 923 | 917
2017-03-08 21:30 | 890 | 880
2017-03-08 22:00 | 862 | 847
2017-03-08 22:30 | 822 | 817
2017-03-08 23:00 | 819 | 814
2017-03-08 23:30 | 761 | 758
2017-03-09 | 711 | 709
2017-03-09 00:30 | 679 | 675
2017-03-09 01:00 | 662 | 656
2017-03-09 01:30 | 640 | 633
2017-03-09 02:00 | 629 | 622
2017-03-09 02:30 | 620 | 614
2017-03-09 03:00 | 611 | 605
2017-03-09 03:30 | 614 | 607
2017-03-09 04:00 | 615 | 607
2017-03-09 04:30 | 624 | 618
2017-03-09 05:00 | 636 | 633
2017-03-09 05:30 | 675 | 674
2017-03-09 06:00 | 711 | 707
2017-03-09 06:30 | 827 | 825
2017-03-09 07:00 | 917 | 913
2017-03-09 07:30 | 943 | 936
2017-03-09 08:00 | 974 | 962
2017-03-09 08:30 | 973 | 965
2017-03-09 09:00 | 961 | 958
2017-03-09 09:30 | 955 | 952
2017-03-09 10:00 | 960 | 958
2017-03-09 10:30 | 955 | 948
2017-03-09 11:00 | 960 | 954
2017-03-09 11:30 | 969 | 964
2017-03-09 12:00 | 990 | 986
2017-03-09 12:30 | 998 | 995
2017-03-09 13:00 | 1022 | 1017
2017-03-09 13:30 | 1028 | 1023
2017-03-09 14:00 | 1040 | 1036
2017-03-09 14:30 | 1026 | 1019
2017-03-09 15:00 | 983 | 974
2017-03-09 15:30 | 994 | 984
2017-03-09 16:00 | 1027 | 1019
2017-03-09 16:30 | 1053 | 1045
2017-03-09 17:00 | 1071 | 1063
2017-03-09 17:30 | 1077 | 1066
2017-03-09 18:00 | 1062 | 1051
2017-03-09 18:30 | 1060 | 1055
2017-03-09 19:00 | 1093 | 1090
2017-03-09 19:30 | 1078 | 1073
2017-03-09 20:00 | 1063 | 1057
2017-03-09 20:30 | 1031 | 1030
2017-03-09 21:00 | 974 | 974
2017-03-09 21:30 | 913 | 913
2017-03-09 22:00 | 862 | 862
2017-03-09 22:30 | 837 | 836
2017-03-09 23:00 | 831 | 831
2017-03-09 23:30 | 772 | 770
2017-03-10 | 718 | 713
2017-03-10 00:30 | 683 | 675
2017-03-10 01:00 | 659 | 649
2017-03-10 01:30 | 648 | 639
2017-03-10 02:00 | 625 | 618
2017-03-10 02:30 | 620 | 612
2017-03-10 03:00 | 612 | 603
2017-03-10 03:30 | 615 | 607
2017-03-10 04:00 | 612 | 605
2017-03-10 04:30 | 624 | 617
2017-03-10 05:00 | 636 | 631
2017-03-10 05:30 | 674 | 672
2017-03-10 06:00 | 703 | 701
2017-03-10 06:30 | 763 | 763
2017-03-10 07:00 | 816 | 816
2017-03-10 07:30 | 857 | 852
2017-03-10 08:00 | 866 | 863
2017-03-10 08:30 | 864 | 863
2017-03-10 09:00 | 863 | 861
2017-03-10 09:30 | 861 | 858
2017-03-10 10:00 | 860 | 856
2017-03-10 10:30 | 862 | 859
2017-03-10 11:00 | 859 | 855
2017-03-10 11:30 | 862 | 857
2017-03-10 12:00 | 880 | 875
2017-03-10 12:30 | 890 | 889
2017-03-10 13:00 | 905 | 903
2017-03-10 13:30 | 914 | 913
2017-03-10 14:00 | 941 | 939
2017-03-10 14:30 | 952 | 950
2017-03-10 15:00 | 967 | 967
2017-03-10 15:30 | 983 | 982
2017-03-10 16:00 | 1017 | 1017
2017-03-10 16:30 | 1043 | 1043
2017-03-10 17:00 | 1057 | 1057
2017-03-10 17:30 | 1045 | 1045
2017-03-10 18:00 | 1016 | 1011
2017-03-10 18:30 | 996 | 992
2017-03-10 19:00 | 1016 | 1013
2017-03-10 19:30 | 993 | 991
2017-03-10 20:00 | 967 | 965
2017-03-10 20:30 | 942 | 941
2017-03-10 21:00 | 910 | 909
2017-03-10 21:30 | 877 | 877
2017-03-10 22:00 | 854 | 853
2017-03-10 22:30 | 841 | 839
2017-03-10 23:00 | 832 | 832
2017-03-10 23:30 | 775 | 774
2017-03-11 | 724 | 721
2017-03-11 00:30 | 688 | 685
2017-03-11 01:00 | 665 | 660
2017-03-11 01:30 | 646 | 639
2017-03-11 02:00 | 633 | 626
2017-03-11 02:30 | 623 | 615
2017-03-11 03:00 | 619 | 610
2017-03-11 03:30 | 616 | 607
2017-03-11 04:00 | 613 | 605
2017-03-11 04:30 | 614 | 606
2017-03-11 05:00 | 615 | 608
2017-03-11 05:30 | 628 | 622
2017-03-11 06:00 | 640 | 633
2017-03-11 06:30 | 654 | 649
2017-03-11 07:00 | 672 | 670
2017-03-11 07:30 | 698 | 698
2017-03-11 08:00 | 719 | 718
2017-03-11 08:30 | 741 | 741
2017-03-11 09:00 | 754 | 754
2017-03-11 09:30 | 757 | 755
2017-03-11 10:00 | 765 | 760
2017-03-11 10:30 | 764 | 760
2017-03-11 11:00 | 764 | 761
2017-03-11 11:30 | 771 | 768
2017-03-11 12:00 | 766 | 764
2017-03-11 12:30 | 760 | 757
2017-03-11 13:00 | 766 | 762
2017-03-11 13:30 | 779 | 774
2017-03-11 14:00 | 777 | 774
2017-03-11 14:30 | 789 | 787
2017-03-11 15:00 | 804 | 802
2017-03-11 15:30 | 821 | 820
2017-03-11 16:00 | 847 | 846
2017-03-11 16:30 | 881 | 880
2017-03-11 17:00 | 903 | 901
2017-03-11 17:30 | 911 | 904
2017-03-11 18:00 | 904 | 893
2017-03-11 18:30 | 906 | 899
2017-03-11 19:00 | 931 | 928
2017-03-11 19:30 | 918 | 913
2017-03-11 20:00 | 908 | 902
2017-03-11 20:30 | 884 | 880
2017-03-11 21:00 | 845 | 844
2017-03-11 21:30 | 816 | 816
2017-03-11 22:00 | 800 | 799
2017-03-11 22:30 | 788 | 788
2017-03-11 23:00 | 787 | 787
2017-03-11 23:30 | 742 | 741
2017-03-12 | 697 | 694
2017-03-12 00:30 | 663 | 660
2017-03-12 01:00 | 649 | 644
2017-03-12 01:30 | 629 | 623
2017-03-12 02:00 | 611 | 603
2017-03-12 02:30 | 607 | 598
2017-03-12 03:00 | 599 | 589
2017-03-12 03:30 | 592 | 582
2017-03-12 04:00 | 595 | 584
2017-03-12 04:30 | 592 | 581
2017-03-12 05:00 | 593 | 582
2017-03-12 05:30 | 596 | 587
2017-03-12 06:00 | 604 | 594
2017-03-12 06:30 | 614 | 603
2017-03-12 07:00 | 626 | 617
2017-03-12 07:30 | 651 | 647
2017-03-12 08:00 | 669 | 668
2017-03-12 08:30 | 688 | 687
2017-03-12 09:00 | 713 | 713
2017-03-12 09:30 | 736 | 736
2017-03-12 10:00 | 744 | 744
2017-03-12 10:30 | 752 | 751
2017-03-12 11:00 | 767 | 767
2017-03-12 11:30 | 777 | 777
2017-03-12 12:00 | 796 | 795
2017-03-12 12:30 | 808 | 807
2017-03-12 13:00 | 815 | 814
2017-03-12 13:30 | 830 | 828
2017-03-12 14:00 | 853 | 850
2017-03-12 14:30 | 887 | 885
2017-03-12 15:00 | 920 | 919
2017-03-12 15:30 | 955 | 953
2017-03-12 16:00 | 993 | 990
2017-03-12 16:30 | 1024 | 1020
2017-03-12 17:00 | 1056 | 1050
2017-03-12 17:30 | 1064 | 1052
2017-03-12 18:00 | 1064 | 1051
2017-03-12 18:30 | 1076 | 1065
2017-03-12 19:00 | 1101 | 1095
2017-03-12 19:30 | 1088 | 1079
2017-03-12 20:00 | 1067 | 1058
2017-03-12 20:30 | 1028 | 1023
2017-03-12 21:00 | 976 | 975
2017-03-12 21:30 | 933 | 933
2017-03-12 22:00 | 889 | 886
2017-03-12 22:30 | 867 | 863
2017-03-12 23:00 | 854 | 850
2017-03-12 23:30 | 788 | 788
2017-03-13 | 744 | 744
2017-03-13 00:30 | 707 | 705
2017-03-13 01:00 | 688 | 687
2017-03-13 01:30 | 669 | 666
2017-03-13 02:00 | 653 | 650
2017-03-13 02:30 | 646 | 642
2017-03-13 03:00 | 641 | 636
2017-03-13 03:30 | 638 | 633
2017-03-13 04:00 | 641 | 636
2017-03-13 04:30 | 648 | 644
2017-03-13 05:00 | 660 | 657
2017-03-13 05:30 | 702 | 702
2017-03-13 06:00 | 738 | 738
2017-03-13 06:30 | 804 | 804
2017-03-13 07:00 | 871 | 870
2017-03-13 07:30 | 949 | 948
2017-03-13 08:00 | 994 | 994
2017-03-13 08:30 | 1032 | 1032
2017-03-13 09:00 | 1044 | 1044
2017-03-13 09:30 | 1053 | 1051
2017-03-13 10:00 | 1029 | 1024
2017-03-13 10:30 | 993 | 986
2017-03-13 11:00 | 985 | 980
2017-03-13 11:30 | 998 | 994
2017-03-13 12:00 | 999 | 995
2017-03-13 12:30 | 954 | 947
2017-03-13 13:00 | 950 | 944
2017-03-13 13:30 | 996 | 994
2017-03-13 14:00 | 1027 | 1026
2017-03-13 14:30 | 1039 | 1037
2017-03-13 15:00 | 1047 | 1045
2017-03-13 15:30 | 1052 | 1049
2017-03-13 16:00 | 1059 | 1055
2017-03-13 16:30 | 1065 | 1061
2017-03-13 17:00 | 1071 | 1066
2017-03-13 17:30 | 1069 | 1062
2017-03-13 18:00 | 1071 | 1063
2017-03-13 18:30 | 1076 | 1070
2017-03-13 19:00 | 1092 | 1089
2017-03-13 19:30 | 1077 | 1071
2017-03-13 20:00 | 1065 | 1059
2017-03-13 20:30 | 1030 | 1024
2017-03-13 21:00 | 964 | 961
2017-03-13 21:30 | 919 | 914
2017-03-13 22:00 | 884 | 874
2017-03-13 22:30 | 836 | 834
2017-03-13 23:00 | 830 | 828
2017-03-13 23:30 | 772 | 772
2017-03-14 | 723 | 723
2017-03-14 00:30 | 688 | 687
2017-03-14 01:00 | 669 | 667
2017-03-14 01:30 | 651 | 649
2017-03-14 02:00 | 636 | 633
2017-03-14 02:30 | 625 | 623
2017-03-14 03:00 | 619 | 616
2017-03-14 03:30 | 619 | 616
2017-03-14 04:00 | 616 | 614
2017-03-14 04:30 | 627 | 624
2017-03-14 05:00 | 646 | 645
2017-03-14 05:30 | 691 | 689
2017-03-14 06:00 | 743 | 737
2017-03-14 06:30 | 809 | 806
2017-03-14 07:00 | 881 | 874
2017-03-14 07:30 | 941 | 937
2017-03-14 08:00 | 974 | 972
2017-03-14 08:30 | 992 | 990
2017-03-14 09:00 | 1014 | 1012
2017-03-14 09:30 | 1039 | 1038
2017-03-14 10:00 | 1041 | 1041
2017-03-14 10:30 | 1028 | 1027
2017-03-14 11:00 | 1029 | 1027
2017-03-14 11:30 | 1069 | 1068
2017-03-14 12:00 | 1087 | 1085
2017-03-14 12:30 | 1056 | 1052
2017-03-14 13:00 | 974 | 968
2017-03-14 13:30 | 977 | 976
2017-03-14 14:00 | 1002 | 1001
2017-03-14 14:30 | 1016 | 1015
2017-03-14 15:00 | 1008 | 1007
2017-03-14 15:30 | 1006 | 1005
2017-03-14 16:00 | 1019 | 1018
2017-03-14 16:30 | 1056 | 1055
2017-03-14 17:00 | 1079 | 1078
2017-03-14 17:30 | 1076 | 1074
2017-03-14 18:00 | 1065 | 1062
2017-03-14 18:30 | 1061 | 1060
2017-03-14 19:00 | 1085 | 1085
2017-03-14 19:30 | 1061 | 1059
2017-03-14 20:00 | 1037 | 1035
2017-03-14 20:30 | 1007 | 1007
2017-03-14 21:00 | 959 | 957
2017-03-14 21:30 | 911 | 911
2017-03-14 22:00 | 876 | 876
2017-03-14 22:30 | 851 | 851
2017-03-14 23:00 | 835 | 834
2017-03-14 23:30 | 774 | 773
2017-03-15 | 722 | 720
2017-03-15 00:30 | 683 | 682
2017-03-15 01:00 | 671 | 669
2017-03-15 01:30 | 649 | 646
2017-03-15 02:00 | 631 | 627
2017-03-15 02:30 | 624 | 619
2017-03-15 03:00 | 624 | 619
2017-03-15 03:30 | 626 | 621
2017-03-15 04:00 | 627 | 622
2017-03-15 04:30 | 633 | 629
2017-03-15 05:00 | 634 | 632
2017-03-15 05:30 | 687 | 683
2017-03-15 06:00 | 732 | 730
2017-03-15 06:30 | 795 | 795
2017-03-15 07:00 | 863 | 862
2017-03-15 07:30 | 923 | 923
2017-03-15 08:00 | 936 | 936
2017-03-15 08:30 | 960 | 960
2017-03-15 09:00 | 972 | 972
2017-03-15 09:30 | 987 | 987
2017-03-15 10:00 | 993 | 993
2017-03-15 10:30 | 995 | 994
2017-03-15 11:00 | 1038 | 1036
2017-03-15 11:30 | 1041 | 1041
2017-03-15 12:00 | 1008 | 1008
2017-03-15 12:30 | 1000 | 1000
2017-03-15 13:00 | 1014 | 1013
2017-03-15 13:30 | 1017 | 1016
2017-03-15 14:00 | 1039 | 1036
2017-03-15 14:30 | 1033 | 1029
2017-03-15 15:00 | 1029 | 1024
2017-03-15 15:30 | 1048 | 1043
2017-03-15 16:00 | 1073 | 1068
2017-03-15 16:30 | 1082 | 1074
2017-03-15 17:00 | 1091 | 1079
2017-03-15 17:30 | 1084 | 1075
2017-03-15 18:00 | 1080 | 1069
2017-03-15 18:30 | 1070 | 1063
2017-03-15 19:00 | 1091 | 1084
2017-03-15 19:30 | 1064 | 1059
2017-03-15 20:00 | 1054 | 1050
2017-03-15 20:30 | 1026 | 1019
2017-03-15 21:00 | 957 | 954
2017-03-15 21:30 | 907 | 905
2017-03-15 22:00 | 868 | 866
2017-03-15 22:30 | 833 | 833
2017-03-15 23:00 | 822 | 822
2017-03-15 23:30 | 762 | 762
2017-03-16 | 707 | 707
2017-03-16 00:30 | 672 | 670
2017-03-16 01:00 | 653 | 649
2017-03-16 01:30 | 638 | 634
2017-03-16 02:00 | 623 | 619
2017-03-16 02:30 | 608 | 604
2017-03-16 03:00 | 605 | 599
2017-03-16 03:30 | 606 | 601
2017-03-16 04:00 | 609 | 605
2017-03-16 04:30 | 616 | 612
2017-03-16 05:00 | 634 | 632
2017-03-16 05:30 | 677 | 675
2017-03-16 06:00 | 718 | 716
2017-03-16 06:30 | 786 | 786
2017-03-16 07:00 | 853 | 853
2017-03-16 07:30 | 914 | 914
2017-03-16 08:00 | 942 | 939
2017-03-16 08:30 | 958 | 955
2017-03-16 09:00 | 961 | 960
2017-03-16 09:30 | 978 | 977
2017-03-16 10:00 | 989 | 986
2017-03-16 10:30 | 979 | 976
2017-03-16 11:00 | 981 | 979
2017-03-16 11:30 | 987 | 983
2017-03-16 12:00 | 999 | 996
2017-03-16 12:30 | 1032 | 1030
2017-03-16 13:00 | 1054 | 1052
2017-03-16 13:30 | 1076 | 1075
2017-03-16 14:00 | 1114 | 1108
2017-03-16 14:30 | 1111 | 1105
2017-03-16 15:00 | 1130 | 1125
2017-03-16 15:30 | 1115 | 1110
2017-03-16 16:00 | 1132 | 1127
2017-03-16 16:30 | 1147 | 1143
2017-03-16 17:00 | 1154 | 1149
2017-03-16 17:30 | 1161 | 1152
2017-03-16 18:00 | 1148 | 1138
2017-03-16 18:30 | 1152 | 1142
2017-03-16 19:00 | 1149 | 1139
2017-03-16 19:30 | 1116 | 1109
2017-03-16 20:00 | 1103 | 1097
2017-03-16 20:30 | 1074 | 1067
2017-03-16 21:00 | 1014 | 1006
2017-03-16 21:30 | 948 | 945
2017-03-16 22:00 | 894 | 892
2017-03-16 22:30 | 864 | 862
2017-03-16 23:00 | 851 | 848
2017-03-16 23:30 | 787 | 783
2017-03-17 | 729 | 721
2017-03-17 00:30 | 691 | 682
2017-03-17 01:00 | 660 | 655
2017-03-17 01:30 | 638 | 634
2017-03-17 02:00 | 623 | 618
2017-03-17 02:30 | 612 | 608
2017-03-17 03:00 | 606 | 600
2017-03-17 03:30 | 605 | 599
2017-03-17 04:00 | 603 | 598
2017-03-17 04:30 | 610 | 606
2017-03-17 05:00 | 625 | 622
2017-03-17 05:30 | 663 | 660
2017-03-17 06:00 | 707 | 700
2017-03-17 06:30 | 770 | 768
2017-03-17 07:00 | 823 | 823
2017-03-17 07:30 | 891 | 891
2017-03-17 08:00 | 914 | 913
2017-03-17 08:30 | 930 | 930
2017-03-17 09:00 | 940 | 940
2017-03-17 09:30 | 957 | 957
2017-03-17 10:00 | 967 | 967
2017-03-17 10:30 | 984 | 984
2017-03-17 11:00 | 992 | 992
2017-03-17 11:30 | 1009 | 1009
2017-03-17 12:00 | 1047 | 1046
2017-03-17 12:30 | 1089 | 1089
2017-03-17 13:00 | 1136 | 1135
2017-03-17 13:30 | 1166 | 1165
2017-03-17 14:00 | 1156 | 1154
2017-03-17 14:30 | 1130 | 1125
2017-03-17 15:00 | 1133 | 1128
2017-03-17 15:30 | 1139 | 1133
2017-03-17 16:00 | 1119 | 1110
2017-03-17 16:30 | 1089 | 1081
2017-03-17 17:00 | 1079 | 1070
2017-03-17 17:30 | 1057 | 1045
2017-03-17 18:00 | 1028 | 1022
2017-03-17 18:30 | 1005 | 1004
2017-03-17 19:00 | 1016 | 1016
2017-03-17 19:30 | 1001 | 1001
2017-03-17 20:00 | 991 | 990
2017-03-17 20:30 | 963 | 963
2017-03-17 21:00 | 921 | 921
2017-03-17 21:30 | 881 | 881
2017-03-17 22:00 | 846 | 846
2017-03-17 22:30 | 822 | 821
2017-03-17 23:00 | 818 | 817
2017-03-17 23:30 | 767 | 767
2017-03-18 | 716 | 714
2017-03-18 00:30 | 676 | 671
2017-03-18 01:00 | 656 | 651
2017-03-18 01:30 | 635 | 627
2017-03-18 02:00 | 619 | 610
2017-03-18 02:30 | 611 | 601
2017-03-18 03:00 | 604 | 593
2017-03-18 03:30 | 600 | 589
2017-03-18 04:00 | 602 | 592
2017-03-18 04:30 | 601 | 592
2017-03-18 05:00 | 601 | 592
2017-03-18 05:30 | 605 | 598
2017-03-18 06:00 | 618 | 611
2017-03-18 06:30 | 639 | 634
2017-03-18 07:00 | 667 | 664
2017-03-18 07:30 | 705 | 704
2017-03-18 08:00 | 738 | 736
2017-03-18 08:30 | 769 | 768
2017-03-18 09:00 | 791 | 791
2017-03-18 09:30 | 797 | 797
2017-03-18 10:00 | 804 | 804
2017-03-18 10:30 | 802 | 802
2017-03-18 11:00 | 811 | 811
2017-03-18 11:30 | 827 | 827
2017-03-18 12:00 | 865 | 864
2017-03-18 12:30 | 873 | 872
2017-03-18 13:00 | 881 | 881
2017-03-18 13:30 | 902 | 902
2017-03-18 14:00 | 938 | 938
2017-03-18 14:30 | 960 | 960
2017-03-18 15:00 | 996 | 996
2017-03-18 15:30 | 1036 | 1036
2017-03-18 16:00 | 1058 | 1057
2017-03-18 16:30 | 1067 | 1066
2017-03-18 17:00 | 1079 | 1079
2017-03-18 17:30 | 1077 | 1075
2017-03-18 18:00 | 1057 | 1055
2017-03-18 18:30 | 1061 | 1060
2017-03-18 19:00 | 1082 | 1082
2017-03-18 19:30 | 1062 | 1061
2017-03-18 20:00 | 1049 | 1048
2017-03-18 20:30 | 1027 | 1026
2017-03-18 21:00 | 991 | 989
2017-03-18 21:30 | 953 | 953
2017-03-18 22:00 | 926 | 925
2017-03-18 22:30 | 898 | 895
2017-03-18 23:00 | 887 | 883
2017-03-18 23:30 | 829 | 822
2017-03-19 | 760 | 759
2017-03-19 00:30 | 716 | 713
2017-03-19 01:00 | 687 | 682
2017-03-19 01:30 | 662 | 655
2017-03-19 02:00 | 643 | 635
2017-03-19 02:30 | 633 | 623
2017-03-19 03:00 | 623 | 612
2017-03-19 03:30 | 618 | 606
2017-03-19 04:00 | 609 | 599
2017-03-19 04:30 | 613 | 602
2017-03-19 05:00 | 612 | 601
2017-03-19 05:30 | 620 | 611
2017-03-19 06:00 | 629 | 620
2017-03-19 06:30 | 639 | 630
2017-03-19 07:00 | 658 | 650
2017-03-19 07:30 | 689 | 685
2017-03-19 08:00 | 713 | 712
2017-03-19 08:30 | 757 | 757
2017-03-19 09:00 | 795 | 795
2017-03-19 09:30 | 819 | 819
2017-03-19 10:00 | 826 | 826
2017-03-19 10:30 | 832 | 832
2017-03-19 11:00 | 821 | 821
2017-03-19 11:30 | 815 | 815
2017-03-19 12:00 | 831 | 831
2017-03-19 12:30 | 857 | 857
2017-03-19 13:00 | 886 | 886
2017-03-19 13:30 | 888 | 887
2017-03-19 14:00 | 883 | 882
2017-03-19 14:30 | 896 | 895
2017-03-19 15:00 | 897 | 896
2017-03-19 15:30 | 913 | 913
2017-03-19 16:00 | 950 | 949
2017-03-19 16:30 | 978 | 973
2017-03-19 17:00 | 986 | 980
2017-03-19 17:30 | 998 | 992
2017-03-19 18:00 | 1013 | 1008
2017-03-19 18:30 | 1038 | 1035
2017-03-19 19:00 | 1047 | 1044
2017-03-19 19:30 | 1022 | 1017
2017-03-19 20:00 | 974 | 973
2017-03-19 20:30 | 956 | 955
2017-03-19 21:00 | 914 | 914
2017-03-19 21:30 | 877 | 876
2017-03-19 22:00 | 839 | 838
2017-03-19 22:30 | 810 | 808
2017-03-19 23:00 | 804 | 803
2017-03-19 23:30 | 760 | 756
2017-03-20 | 713 | 707
2017-03-20 00:30 | 669 | 666
2017-03-20 01:00 | 652 | 648
2017-03-20 01:30 | 637 | 632
2017-03-20 02:00 | 627 | 620
2017-03-20 02:30 | 619 | 613
2017-03-20 03:00 | 609 | 603
2017-03-20 03:30 | 610 | 604
2017-03-20 04:00 | 610 | 604
2017-03-20 04:30 | 620 | 616
2017-03-20 05:00 | 639 | 636
2017-03-20 05:30 | 679 | 679
2017-03-20 06:00 | 730 | 728
2017-03-20 06:30 | 809 | 809
2017-03-20 07:00 | 883 | 881
2017-03-20 07:30 | 964 | 962
2017-03-20 08:00 | 994 | 988
2017-03-20 08:30 | 1029 | 1027
2017-03-20 09:00 | 1055 | 1054
2017-03-20 09:30 | 1089 | 1089
2017-03-20 10:00 | 1097 | 1094
2017-03-20 10:30 | 1101 | 1098
2017-03-20 11:00 | 1101 | 1099
2017-03-20 11:30 | 1090 | 1086
2017-03-20 12:00 | 1111 | 1108
2017-03-20 12:30 | 1132 | 1128
2017-03-20 13:00 | 1119 | 1114
2017-03-20 13:30 | 1100 | 1094
2017-03-20 14:00 | 1103 | 1097
2017-03-20 14:30 | 1103 | 1095
2017-03-20 15:00 | 1099 | 1091
2017-03-20 15:30 | 1101 | 1092
2017-03-20 16:00 | 1105 | 1101
2017-03-20 16:30 | 1116 | 1111
2017-03-20 17:00 | 1123 | 1118
2017-03-20 17:30 | 1115 | 1109
2017-03-20 18:00 | 1086 | 1079
2017-03-20 18:30 | 1084 | 1079
2017-03-20 19:00 | 1083 | 1079
2017-03-20 19:30 | 1052 | 1048
2017-03-20 20:00 | 1031 | 1030
2017-03-20 20:30 | 995 | 993
2017-03-20 21:00 | 942 | 938
2017-03-20 21:30 | 896 | 894
2017-03-20 22:00 | 858 | 858
2017-03-20 22:30 | 831 | 830
2017-03-20 23:00 | 822 | 820
2017-03-20 23:30 | 769 | 766
2017-03-21 | 718 | 711
2017-03-21 00:30 | 672 | 667
2017-03-21 01:00 | 653 | 651
2017-03-21 01:30 | 639 | 635
2017-03-21 02:00 | 624 | 620
2017-03-21 02:30 | 618 | 613
2017-03-21 03:00 | 610 | 604
2017-03-21 03:30 | 615 | 610
2017-03-21 04:00 | 617 | 612
2017-03-21 04:30 | 629 | 624
2017-03-21 05:00 | 670 | 668
2017-03-21 05:30 | 700 | 698
2017-03-21 06:00 | 737 | 736
2017-03-21 06:30 | 809 | 809
2017-03-21 07:00 | 889 | 888
2017-03-21 07:30 | 952 | 951
2017-03-21 08:00 | 973 | 972
2017-03-21 08:30 | 998 | 998
2017-03-21 09:00 | 1002 | 1002
2017-03-21 09:30 | 1012 | 1012
2017-03-21 10:00 | 1031 | 1030
2017-03-21 10:30 | 1039 | 1038
2017-03-21 11:00 | 1001 | 1001
2017-03-21 11:30 | 1018 | 1017
2017-03-21 12:00 | 981 | 980
2017-03-21 12:30 | 1040 | 1039
2017-03-21 13:00 | 1044 | 1038
2017-03-21 13:30 | 1049 | 1044
2017-03-21 14:00 | 1061 | 1058
2017-03-21 14:30 | 1075 | 1071
2017-03-21 15:00 | 1086 | 1079
2017-03-21 15:30 | 1097 | 1090
2017-03-21 16:00 | 1110 | 1103
2017-03-21 16:30 | 1129 | 1122
2017-03-21 17:00 | 1149 | 1141
2017-03-21 17:30 | 1144 | 1136
2017-03-21 18:00 | 1138 | 1132
2017-03-21 18:30 | 1151 | 1149
2017-03-21 19:00 | 1159 | 1156
2017-03-21 19:30 | 1132 | 1129
2017-03-21 20:00 | 1112 | 1111
2017-03-21 20:30 | 1081 | 1081
2017-03-21 21:00 | 1023 | 1021
2017-03-21 21:30 | 980 | 977
2017-03-21 22:00 | 930 | 927
2017-03-21 22:30 | 895 | 895
2017-03-21 23:00 | 885 | 884
2017-03-21 23:30 | 817 | 817
2017-03-22 | 755 | 753
2017-03-22 00:30 | 707 | 704
2017-03-22 01:00 | 681 | 677
2017-03-22 01:30 | 662 | 656
2017-03-22 02:00 | 648 | 641
2017-03-22 02:30 | 634 | 627
2017-03-22 03:00 | 627 | 622
2017-03-22 03:30 | 624 | 619
2017-03-22 04:00 | 627 | 623
2017-03-22 04:30 | 641 | 638
2017-03-22 05:00 | 683 | 681
2017-03-22 05:30 | 723 | 720
2017-03-22 06:00 | 765 | 762
2017-03-22 06:30 | 846 | 843
2017-03-22 07:00 | 917 | 916
2017-03-22 07:30 | 983 | 978
2017-03-22 08:00 | 989 | 986
2017-03-22 08:30 | 1011 | 1008
2017-03-22 09:00 | 1027 | 1025
2017-03-22 09:30 | 1049 | 1048
2017-03-22 10:00 | 1076 | 1075
2017-03-22 10:30 | 1089 | 1087
2017-03-22 11:00 | 1093 | 1091
2017-03-22 11:30 | 1090 | 1088
2017-03-22 12:00 | 1081 | 1079
2017-03-22 12:30 | 1088 | 1085
2017-03-22 13:00 | 1099 | 1097
2017-03-22 13:30 | 1105 | 1103
2017-03-22 14:00 | 1109 | 1106
2017-03-22 14:30 | 1100 | 1096
2017-03-22 15:00 | 1093 | 1089
2017-03-22 15:30 | 1091 | 1085
2017-03-22 16:00 | 1096 | 1090
2017-03-22 16:30 | 1109 | 1103
2017-03-22 17:00 | 1122 | 1114
2017-03-22 17:30 | 1116 | 1106
2017-03-22 18:00 | 1109 | 1096
2017-03-22 18:30 | 1107 | 1099
2017-03-22 19:00 | 1112 | 1105
2017-03-22 19:30 | 1085 | 1079
2017-03-22 20:00 | 1062 | 1061
2017-03-22 20:30 | 1033 | 1030
2017-03-22 21:00 | 989 | 985
2017-03-22 21:30 | 938 | 935
2017-03-22 22:00 | 882 | 880
2017-03-22 22:30 | 862 | 859
2017-03-22 23:00 | 860 | 860
2017-03-22 23:30 | 799 | 799
2017-03-23 | 748 | 746
2017-03-23 00:30 | 709 | 706
2017-03-23 01:00 | 687 | 682
2017-03-23 01:30 | 656 | 652
2017-03-23 02:00 | 641 | 636
2017-03-23 02:30 | 630 | 625
2017-03-23 03:00 | 622 | 616
2017-03-23 03:30 | 621 | 616
2017-03-23 04:00 | 619 | 615
2017-03-23 04:30 | 629 | 626
2017-03-23 05:00 | 659 | 657
2017-03-23 05:30 | 704 | 704
2017-03-23 06:00 | 747 | 747
2017-03-23 06:30 | 820 | 819
2017-03-23 07:00 | 898 | 898
2017-03-23 07:30 | 963 | 963
2017-03-23 08:00 | 985 | 984
2017-03-23 08:30 | 993 | 990
2017-03-23 09:00 | 1008 | 1003
2017-03-23 09:30 | 1025 | 1024
2017-03-23 10:00 | 1027 | 1027
2017-03-23 10:30 | 1035 | 1034
2017-03-23 11:00 | 1015 | 1014
2017-03-23 11:30 | 1004 | 1004
2017-03-23 12:00 | 1017 | 1017
2017-03-23 12:30 | 1026 | 1026
2017-03-23 13:00 | 1043 | 1042
2017-03-23 13:30 | 1052 | 1051
2017-03-23 14:00 | 1077 | 1076
2017-03-23 14:30 | 1099 | 1099
2017-03-23 15:00 | 1097 | 1097
2017-03-23 15:30 | 1098 | 1098
2017-03-23 16:00 | 1117 | 1117
2017-03-23 16:30 | 1126 | 1126
2017-03-23 17:00 | 1142 | 1142
2017-03-23 17:30 | 1136 | 1134
2017-03-23 18:00 | 1132 | 1129
2017-03-23 18:30 | 1148 | 1146
2017-03-23 19:00 | 1155 | 1153
2017-03-23 19:30 | 1141 | 1137
2017-03-23 20:00 | 1117 | 1113
2017-03-23 20:30 | 1077 | 1076
2017-03-23 21:00 | 1020 | 1019
2017-03-23 21:30 | 971 | 969
2017-03-23 22:00 | 922 | 919
2017-03-23 22:30 | 891 | 890
2017-03-23 23:00 | 885 | 885
2017-03-23 23:30 | 826 | 825
2017-03-24 | 771 | 769
2017-03-24 00:30 | 723 | 720
2017-03-24 01:00 | 690 | 688
2017-03-24 01:30 | 666 | 663
2017-03-24 02:00 | 644 | 640
2017-03-24 02:30 | 636 | 633
2017-03-24 03:00 | 631 | 627
2017-03-24 03:30 | 626 | 622
2017-03-24 04:00 | 626 | 622
2017-03-24 04:30 | 635 | 631
2017-03-24 05:00 | 668 | 665
2017-03-24 05:30 | 696 | 696
2017-03-24 06:00 | 750 | 749
2017-03-24 06:30 | 822 | 822
2017-03-24 07:00 | 880 | 879
2017-03-24 07:30 | 937 | 936
2017-03-24 08:00 | 951 | 951
2017-03-24 08:30 | 984 | 984
2017-03-24 09:00 | 1012 | 1011
2017-03-24 09:30 | 1022 | 1021
2017-03-24 10:00 | 1026 | 1025
2017-03-24 10:30 | 1023 | 1023
2017-03-24 11:00 | 1028 | 1028
2017-03-24 11:30 | 1053 | 1053
2017-03-24 12:00 | 1086 | 1086
2017-03-24 12:30 | 1093 | 1089
2017-03-24 13:00 | 1094 | 1089
2017-03-24 13:30 | 1082 | 1077
2017-03-24 14:00 | 1086 | 1083
2017-03-24 14:30 | 1081 | 1077
2017-03-24 15:00 | 1066 | 1060
2017-03-24 15:30 | 1057 | 1051
2017-03-24 16:00 | 1063 | 1057
2017-03-24 16:30 | 1074 | 1070
2017-03-24 17:00 | 1077 | 1074
2017-03-24 17:30 | 1066 | 1059
2017-03-24 18:00 | 1052 | 1043
2017-03-24 18:30 | 1049 | 1042
2017-03-24 19:00 | 1047 | 1041
2017-03-24 19:30 | 1033 | 1029
2017-03-24 20:00 | 997 | 997
2017-03-24 20:30 | 968 | 967
2017-03-24 21:00 | 918 | 917
2017-03-24 21:30 | 888 | 886
2017-03-24 22:00 | 854 | 854
2017-03-24 22:30 | 832 | 831
2017-03-24 23:00 | 832 | 831
2017-03-24 23:30 | 779 | 778
2017-03-25 | 732 | 731
2017-03-25 00:30 | 693 | 691
2017-03-25 01:00 | 669 | 665
2017-03-25 01:30 | 645 | 640
2017-03-25 02:00 | 626 | 620
2017-03-25 02:30 | 617 | 611
2017-03-25 03:00 | 612 | 606
2017-03-25 03:30 | 609 | 603
2017-03-25 04:00 | 612 | 605
2017-03-25 04:30 | 616 | 609
2017-03-25 05:00 | 618 | 612
2017-03-25 05:30 | 633 | 629
2017-03-25 06:00 | 650 | 647
2017-03-25 06:30 | 679 | 676
2017-03-25 07:00 | 697 | 696
2017-03-25 07:30 | 726 | 725
2017-03-25 08:00 | 752 | 751
2017-03-25 08:30 | 800 | 799
2017-03-25 09:00 | 808 | 805
2017-03-25 09:30 | 833 | 832
2017-03-25 10:00 | 844 | 844
2017-03-25 10:30 | 852 | 852
2017-03-25 11:00 | 854 | 854
2017-03-25 11:30 | 851 | 851
2017-03-25 12:00 | 856 | 856
2017-03-25 12:30 | 855 | 855
2017-03-25 13:00 | 848 | 848
2017-03-25 13:30 | 843 | 842
2017-03-25 14:00 | 838 | 838
2017-03-25 14:30 | 836 | 835
2017-03-25 15:00 | 840 | 839
2017-03-25 15:30 | 862 | 861
2017-03-25 16:00 | 882 | 881
2017-03-25 16:30 | 895 | 894
2017-03-25 17:00 | 923 | 922
2017-03-25 17:30 | 906 | 904
2017-03-25 18:00 | 910 | 908
2017-03-25 18:30 | 936 | 936
2017-03-25 19:00 | 939 | 938
2017-03-25 19:30 | 918 | 917
2017-03-25 20:00 | 903 | 903
2017-03-25 20:30 | 885 | 885
2017-03-25 21:00 | 849 | 849
2017-03-25 21:30 | 829 | 829
2017-03-25 22:00 | 806 | 806
2017-03-25 22:30 | 796 | 796
2017-03-25 23:00 | 800 | 799
2017-03-25 23:30 | 760 | 757
2017-03-26 | 714 | 708
2017-03-26 00:30 | 675 | 665
2017-03-26 01:00 | 647 | 636
2017-03-26 01:30 | 620 | 613
2017-03-26 02:00 | 601 | 593
2017-03-26 02:30 | 587 | 579
2017-03-26 03:00 | 581 | 572
2017-03-26 03:30 | 575 | 565
2017-03-26 04:00 | 576 | 565
2017-03-26 04:30 | 574 | 564
2017-03-26 05:00 | 577 | 567
2017-03-26 05:30 | 582 | 571
2017-03-26 06:00 | 594 | 585
2017-03-26 06:30 | 608 | 598
2017-03-26 07:00 | 624 | 616
2017-03-26 07:30 | 650 | 647
2017-03-26 08:00 | 669 | 667
2017-03-26 08:30 | 695 | 695
2017-03-26 09:00 | 725 | 725
2017-03-26 09:30 | 749 | 748
2017-03-26 10:00 | 746 | 744
2017-03-26 10:30 | 755 | 752
2017-03-26 11:00 | 758 | 756
2017-03-26 11:30 | 759 | 756
2017-03-26 12:00 | 782 | 778
2017-03-26 12:30 | 792 | 791
2017-03-26 13:00 | 805 | 804
2017-03-26 13:30 | 823 | 823
2017-03-26 14:00 | 849 | 849
2017-03-26 14:30 | 861 | 861
2017-03-26 15:00 | 899 | 899
2017-03-26 15:30 | 942 | 940
2017-03-26 16:00 | 972 | 970
2017-03-26 16:30 | 996 | 994
2017-03-26 17:00 | 1021 | 1017
2017-03-26 17:30 | 1027 | 1022
2017-03-26 18:00 | 1027 | 1021
2017-03-26 18:30 | 1053 | 1051
2017-03-26 19:00 | 1062 | 1060
2017-03-26 19:30 | 1036 | 1032
2017-03-26 20:00 | 1015 | 1008
2017-03-26 20:30 | 963 | 962
2017-03-26 21:00 | 924 | 923
2017-03-26 21:30 | 888 | 887
2017-03-26 22:00 | 842 | 841
2017-03-26 22:30 | 823 | 823
2017-03-26 23:00 | 814 | 814
2017-03-26 23:30 | 761 | 759
2017-03-27 | 713 | 712
2017-03-27 00:30 | 673 | 671
2017-03-27 01:00 | 650 | 647
2017-03-27 01:30 | 632 | 628
2017-03-27 02:00 | 619 | 612
2017-03-27 02:30 | 612 | 606
2017-03-27 03:00 | 607 | 600
2017-03-27 03:30 | 603 | 596
2017-03-27 04:00 | 607 | 601
2017-03-27 04:30 | 614 | 609
2017-03-27 05:00 | 631 | 627
2017-03-27 05:30 | 669 | 668
2017-03-27 06:00 | 722 | 722
2017-03-27 06:30 | 795 | 794
2017-03-27 07:00 | 868 | 867
2017-03-27 07:30 | 928 | 927
2017-03-27 08:00 | 959 | 957
2017-03-27 08:30 | 971 | 971
2017-03-27 09:00 | 983 | 983
2017-03-27 09:30 | 1001 | 999
2017-03-27 10:00 | 1006 | 1004
2017-03-27 10:30 | 1007 | 1007
2017-03-27 11:00 | 998 | 998
2017-03-27 11:30 | 989 | 989
2017-03-27 12:00 | 1002 | 1002
2017-03-27 12:30 | 1012 | 1012
2017-03-27 13:00 | 1025 | 1025
2017-03-27 13:30 | 1014 | 1013
2017-03-27 14:00 | 1032 | 1032
2017-03-27 14:30 | 1038 | 1038
2017-03-27 15:00 | 1051 | 1051
2017-03-27 15:30 | 1070 | 1070
2017-03-27 16:00 | 1099 | 1099
2017-03-27 16:30 | 1124 | 1124
2017-03-27 17:00 | 1130 | 1130
2017-03-27 17:30 | 1119 | 1118
2017-03-27 18:00 | 1105 | 1103
2017-03-27 18:30 | 1106 | 1105
2017-03-27 19:00 | 1109 | 1109
2017-03-27 19:30 | 1079 | 1078
2017-03-27 20:00 | 1062 | 1061
2017-03-27 20:30 | 1030 | 1028
2017-03-27 21:00 | 975 | 975
2017-03-27 21:30 | 933 | 931
2017-03-27 22:00 | 878 | 877
2017-03-27 22:30 | 848 | 847
2017-03-27 23:00 | 838 | 837
2017-03-27 23:30 | 778 | 776
2017-03-28 | 734 | 728
2017-03-28 00:30 | 688 | 684
2017-03-28 01:00 | 670 | 665
2017-03-28 01:30 | 643 | 641
2017-03-28 02:00 | 626 | 623
2017-03-28 02:30 | 616 | 612
2017-03-28 03:00 | 608 | 604
2017-03-28 03:30 | 604 | 600
2017-03-28 04:00 | 601 | 598
2017-03-28 04:30 | 615 | 613
2017-03-28 05:00 | 630 | 629
2017-03-28 05:30 | 676 | 675
2017-03-28 06:00 | 705 | 703
2017-03-28 06:30 | 766 | 766
2017-03-28 07:00 | 837 | 837
2017-03-28 07:30 | 896 | 896
2017-03-28 08:00 | 913 | 912
2017-03-28 08:30 | 925 | 924
2017-03-28 09:00 | 939 | 937
2017-03-28 09:30 | 960 | 957
2017-03-28 10:00 | 961 | 958
2017-03-28 10:30 | 956 | 956
2017-03-28 11:00 | 966 | 966
2017-03-28 11:30 | 966 | 966
2017-03-28 12:00 | 971 | 971
2017-03-28 12:30 | 975 | 974
2017-03-28 13:00 | 990 | 989
2017-03-28 13:30 | 1011 | 1009
2017-03-28 14:00 | 1039 | 1037
2017-03-28 14:30 | 1058 | 1056
2017-03-28 15:00 | 1073 | 1071
2017-03-28 15:30 | 1093 | 1092
2017-03-28 16:00 | 1133 | 1131
2017-03-28 16:30 | 1160 | 1160
2017-03-28 17:00 | 1162 | 1162
2017-03-28 17:30 | 1146 | 1145
2017-03-28 18:00 | 1133 | 1133
2017-03-28 18:30 | 1143 | 1138
2017-03-28 19:00 | 1147 | 1142
2017-03-28 19:30 | 1112 | 1110
2017-03-28 20:00 | 1096 | 1094
2017-03-28 20:30 | 1057 | 1054
2017-03-28 21:00 | 995 | 994
2017-03-28 21:30 | 942 | 940
2017-03-28 22:00 | 900 | 900
2017-03-28 22:30 | 870 | 870
2017-03-28 23:00 | 855 | 854
2017-03-28 23:30 | 792 | 790
2017-03-29 | 733 | 733
2017-03-29 00:30 | 689 | 688
2017-03-29 01:00 | 661 | 660
2017-03-29 01:30 | 630 | 629
2017-03-29 02:00 | 611 | 609
2017-03-29 02:30 | 597 | 594
2017-03-29 03:00 | 595 | 592
2017-03-29 03:30 | 590 | 586
2017-03-29 04:00 | 591 | 588
2017-03-29 04:30 | 602 | 599
2017-03-29 05:00 | 633 | 631
2017-03-29 05:30 | 680 | 680
2017-03-29 06:00 | 726 | 725
2017-03-29 06:30 | 797 | 796
2017-03-29 07:00 | 860 | 860
2017-03-29 07:30 | 928 | 928
2017-03-29 08:00 | 952 | 952
2017-03-29 08:30 | 978 | 977
2017-03-29 09:00 | 966 | 965
2017-03-29 09:30 | 1022 | 1021
2017-03-29 10:00 | 1050 | 1050
2017-03-29 10:30 | 1049 | 1049
2017-03-29 11:00 | 1063 | 1063
2017-03-29 11:30 | 1073 | 1073
2017-03-29 12:00 | 1083 | 1083
2017-03-29 12:30 | 1089 | 1089
2017-03-29 13:00 | 1099 | 1099
2017-03-29 13:30 | 1090 | 1090
2017-03-29 14:00 | 1115 | 1114
2017-03-29 14:30 | 1144 | 1144
2017-03-29 15:00 | 1154 | 1153
2017-03-29 15:30 | 1149 | 1148
2017-03-29 16:00 | 1153 | 1153
2017-03-29 16:30 | 1153 | 1153
2017-03-29 17:00 | 1165 | 1164
2017-03-29 17:30 | 1157 | 1156
2017-03-29 18:00 | 1154 | 1153
2017-03-29 18:30 | 1146 | 1144
2017-03-29 19:00 | 1142 | 1141
2017-03-29 19:30 | 1120 | 1118
2017-03-29 20:00 | 1107 | 1106
2017-03-29 20:30 | 1083 | 1082
2017-03-29 21:00 | 1034 | 1034
2017-03-29 21:30 | 990 | 990
2017-03-29 22:00 | 946 | 945
2017-03-29 22:30 | 912 | 908
2017-03-29 23:00 | 886 | 885
2017-03-29 23:30 | 827 | 827
2017-03-30 | 776 | 776
2017-03-30 00:30 | 730 | 730
2017-03-30 01:00 | 700 | 699
2017-03-30 01:30 | 680 | 679
2017-03-30 02:00 | 667 | 667
2017-03-30 02:30 | 659 | 658
2017-03-30 03:00 | 653 | 652
2017-03-30 03:30 | 652 | 651
2017-03-30 04:00 | 647 | 646
2017-03-30 04:30 | 654 | 653
2017-03-30 05:00 | 683 | 683
2017-03-30 05:30 | 730 | 730
2017-03-30 06:00 | 788 | 785
2017-03-30 06:30 | 871 | 871
2017-03-30 07:00 | 957 | 957
2017-03-30 07:30 | 1038 | 1037
2017-03-30 08:00 | 1066 | 1065
2017-03-30 08:30 | 1113 | 1111
2017-03-30 09:00 | 1130 | 1129
2017-03-30 09:30 | 1164 | 1163
2017-03-30 10:00 | 1165 | 1164
2017-03-30 10:30 | 1157 | 1155
2017-03-30 11:00 | 1145 | 1142
2017-03-30 11:30 | 1122 | 1116
2017-03-30 12:00 | 1105 | 1099
2017-03-30 12:30 | 1093 | 1086
2017-03-30 13:00 | 1076 | 1066
2017-03-30 13:30 | 1047 | 1036
2017-03-30 14:00 | 1034 | 1024
2017-03-30 14:30 | 1022 | 1013
2017-03-30 15:00 | 1001 | 994
2017-03-30 15:30 | 997 | 988
2017-03-30 16:00 | 994 | 985
2017-03-30 16:30 | 993 | 985
2017-03-30 17:00 | 1006 | 999
2017-03-30 17:30 | 1018 | 1010
2017-03-30 18:00 | 1026 | 1021
2017-03-30 18:30 | 1051 | 1048
2017-03-30 19:00 | 1105 | 1104
2017-03-30 19:30 | 1055 | 1051
2017-03-30 20:00 | 1040 | 1035
2017-03-30 20:30 | 1008 | 1001
2017-03-30 21:00 | 936 | 936
2017-03-30 21:30 | 860 | 860
2017-03-30 22:00 | 826 | 825
2017-03-30 22:30 | 811 | 810
2017-03-30 23:00 | 799 | 798
2017-03-30 23:30 | 747 | 747
2017-03-31 | 704 | 703
2017-03-31 00:30 | 661 | 657
2017-03-31 01:00 | 642 | 637
2017-03-31 01:30 | 583 | 576
2017-03-31 02:00 | 575 | 568
2017-03-31 02:30 | 579 | 572
2017-03-31 03:00 | 569 | 561
2017-03-31 03:30 | 562 | 553
2017-03-31 04:00 | 557 | 548
2017-03-31 04:30 | 553 | 545
2017-03-31 05:00 | 567 | 559
2017-03-31 05:30 | 600 | 595
2017-03-31 06:00 | 630 | 627
2017-03-31 06:30 | 669 | 668
2017-03-31 07:00 | 723 | 722
2017-03-31 07:30 | 796 | 796
2017-03-31 08:00 | 826 | 826
2017-03-31 08:30 | 837 | 837
2017-03-31 09:00 | 834 | 834
2017-03-31 09:30 | 824 | 824
2017-03-31 10:00 | 809 | 809
2017-03-31 10:30 | 817 | 817
2017-03-31 11:00 | 817 | 817
2017-03-31 11:30 | 814 | 814
2017-03-31 12:00 | 826 | 825
2017-03-31 12:30 | 841 | 840
2017-03-31 13:00 | 879 | 878
2017-03-31 13:30 | 915 | 914
2017-03-31 14:00 | 932 | 932
2017-03-31 14:30 | 934 | 934
2017-03-31 15:00 | 938 | 938
2017-03-31 15:30 | 948 | 947
2017-03-31 16:00 | 941 | 940
2017-03-31 16:30 | 940 | 938
2017-03-31 17:00 | 963 | 961
2017-03-31 17:30 | 956 | 953
2017-03-31 18:00 | 939 | 935
2017-03-31 18:30 | 943 | 940
2017-03-31 19:00 | 944 | 941
2017-03-31 19:30 | 922 | 918
2017-03-31 20:00 | 908 | 907
2017-03-31 20:30 | 884 | 883
2017-03-31 21:00 | 848 | 848
2017-03-31 21:30 | 820 | 820
2017-03-31 22:00 | 786 | 786
2017-03-31 22:30 | 775 | 775
2017-03-31 23:00 | 768 | 768
2017-03-31 23:30 | 710 | 709
2017-04-01 | 637 | 634
2017-04-01 00:30 | 594 | 589
2017-04-01 01:00 | 564 | 557
2017-04-01 01:30 | 541 | 532
2017-04-01 02:00 | 521 | 509
2017-04-01 02:30 | 521 | 506
2017-04-01 03:00 | 516 | 500
2017-04-01 03:30 | 511 | 495
2017-04-01 04:00 | 505 | 489
2017-04-01 04:30 | 503 | 489
2017-04-01 05:00 | 507 | 494
2017-04-01 05:30 | 518 | 508
2017-04-01 06:00 | 530 | 521
2017-04-01 06:30 | 547 | 539
2017-04-01 07:00 | 565 | 558
2017-04-01 07:30 | 596 | 593
2017-04-01 08:00 | 614 | 613
2017-04-01 08:30 | 634 | 633
2017-04-01 09:00 | 653 | 653
2017-04-01 09:30 | 664 | 664
2017-04-01 10:00 | 661 | 661
2017-04-01 10:30 | 653 | 652
2017-04-01 11:00 | 644 | 644
2017-04-01 11:30 | 631 | 630
2017-04-01 12:00 | 625 | 624
2017-04-01 12:30 | 626 | 625
2017-04-01 13:00 | 634 | 634
2017-04-01 13:30 | 650 | 649
2017-04-01 14:00 | 673 | 673
2017-04-01 14:30 | 700 | 700
2017-04-01 15:00 | 713 | 713
2017-04-01 15:30 | 742 | 742
2017-04-01 16:00 | 763 | 763
2017-04-01 16:30 | 792 | 791
2017-04-01 17:00 | 817 | 817
2017-04-01 17:30 | 830 | 828
2017-04-01 18:00 | 837 | 836
2017-04-01 18:30 | 863 | 863
2017-04-01 19:00 | 858 | 858
2017-04-01 19:30 | 838 | 836
2017-04-01 20:00 | 835 | 833
2017-04-01 20:30 | 814 | 812
2017-04-01 21:00 | 769 | 768
2017-04-01 21:30 | 750 | 749
2017-04-01 22:00 | 723 | 723
2017-04-01 22:30 | 725 | 724
2017-04-01 23:00 | 732 | 732
2017-04-01 23:30 | 678 | 677
2017-04-02 | 625 | 622
2017-04-02 00:30 | 580 | 575
2017-04-02 01:00 | 549 | 542
2017-04-02 01:30 | 524 | 516
2017-04-02 02:00 | 499 | 488
2017-04-02 02:30 | 484 | 472
2017-04-02 03:00 | 478 | 465
2017-04-02 03:30 | 473 | 460
2017-04-02 04:00 | 468 | 454
2017-04-02 04:30 | 467 | 452
2017-04-02 05:00 | 480 | 466
2017-04-02 05:30 | 491 | 479
2017-04-02 06:00 | 499 | 487
2017-04-02 06:30 | 515 | 502
2017-04-02 07:00 | 521 | 510
2017-04-02 07:30 | 536 | 528
2017-04-02 08:00 | 554 | 550
2017-04-02 08:30 | 582 | 581
2017-04-02 09:00 | 614 | 613
2017-04-02 09:30 | 643 | 642
2017-04-02 10:00 | 652 | 651
2017-04-02 10:30 | 661 | 661
2017-04-02 11:00 | 648 | 647
2017-04-02 11:30 | 643 | 642
2017-04-02 12:00 | 631 | 629
2017-04-02 12:30 | 614 | 612
2017-04-02 13:00 | 610 | 608
2017-04-02 13:30 | 613 | 612
2017-04-02 14:00 | 630 | 629
2017-04-02 14:30 | 664 | 663
2017-04-02 15:00 | 679 | 679
2017-04-02 15:30 | 711 | 711
2017-04-02 16:00 | 736 | 736
2017-04-02 16:30 | 768 | 768
2017-04-02 17:00 | 806 | 805
2017-04-02 17:30 | 834 | 833
2017-04-02 18:00 | 856 | 855
2017-04-02 18:30 | 892 | 891
2017-04-02 19:00 | 897 | 895
2017-04-02 19:30 | 857 | 854
2017-04-02 20:00 | 829 | 827
2017-04-02 20:30 | 824 | 821
2017-04-02 21:00 | 777 | 775
2017-04-02 21:30 | 745 | 744
2017-04-02 22:00 | 715 | 714
2017-04-02 22:30 | 706 | 705
2017-04-02 23:00 | 700 | 699
2017-04-02 23:30 | 653 | 651
2017-04-03 | 596 | 591
2017-04-03 00:30 | 544 | 535
2017-04-03 01:00 | 515 | 502
2017-04-03 01:30 | 496 | 480
2017-04-03 02:00 | 490 | 471
2017-04-03 02:30 | 475 | 455
2017-04-03 03:00 | 471 | 452
2017-04-03 03:30 | 471 | 452
2017-04-03 04:00 | 478 | 459
2017-04-03 04:30 | 490 | 473
2017-04-03 05:00 | 501 | 488
2017-04-03 05:30 | 533 | 526
2017-04-03 06:00 | 568 | 565
2017-04-03 06:30 | 628 | 623
2017-04-03 07:00 | 675 | 673
2017-04-03 07:30 | 710 | 710
2017-04-03 08:00 | 717 | 716
2017-04-03 08:30 | 728 | 728
2017-04-03 09:00 | 736 | 736
2017-04-03 09:30 | 753 | 753
2017-04-03 10:00 | 755 | 754
2017-04-03 10:30 | 735 | 735
2017-04-03 11:00 | 711 | 711
2017-04-03 11:30 | 731 | 730
2017-04-03 12:00 | 741 | 741
2017-04-03 12:30 | 743 | 743
2017-04-03 13:00 | 743 | 742
2017-04-03 13:30 | 746 | 746
2017-04-03 14:00 | 777 | 777
2017-04-03 14:30 | 788 | 787
2017-04-03 15:00 | 791 | 790
2017-04-03 15:30 | 797 | 796
2017-04-03 16:00 | 832 | 832
2017-04-03 16:30 | 860 | 860
2017-04-03 17:00 | 880 | 879
2017-04-03 17:30 | 897 | 897
2017-04-03 18:00 | 912 | 911
2017-04-03 18:30 | 922 | 922
2017-04-03 19:00 | 926 | 926
2017-04-03 19:30 | 875 | 874
2017-04-03 20:00 | 856 | 856
2017-04-03 20:30 | 830 | 830
2017-04-03 21:00 | 782 | 782
2017-04-03 21:30 | 758 | 757
2017-04-03 22:00 | 717 | 716
2017-04-03 22:30 | 709 | 709
2017-04-03 23:00 | 704 | 704
2017-04-03 23:30 | 653 | 651
2017-04-04 | 593 | 589
2017-04-04 00:30 | 544 | 537
2017-04-04 01:00 | 517 | 508
2017-04-04 01:30 | 502 | 492
2017-04-04 02:00 | 479 | 466
2017-04-04 02:30 | 471 | 458
2017-04-04 03:00 | 458 | 444
2017-04-04 03:30 | 446 | 428
2017-04-04 04:00 | 450 | 435
2017-04-04 04:30 | 462 | 448
2017-04-04 05:00 | 481 | 470
2017-04-04 05:30 | 517 | 510
2017-04-04 06:00 | 552 | 548
2017-04-04 06:30 | 606 | 604
2017-04-04 07:00 | 652 | 651
2017-04-04 07:30 | 691 | 691
2017-04-04 08:00 | 698 | 695
2017-04-04 08:30 | 704 | 703
2017-04-04 09:00 | 700 | 699
2017-04-04 09:30 | 707 | 706
2017-04-04 10:00 | 710 | 710
2017-04-04 10:30 | 731 | 731
2017-04-04 11:00 | 736 | 735
2017-04-04 11:30 | 760 | 759
2017-04-04 12:00 | 774 | 774
2017-04-04 12:30 | 749 | 747
2017-04-04 13:00 | 774 | 774
2017-04-04 13:30 | 800 | 799
2017-04-04 14:00 | 779 | 779
2017-04-04 14:30 | 800 | 800
2017-04-04 15:00 | 789 | 789
2017-04-04 15:30 | 824 | 824
2017-04-04 16:00 | 832 | 832
2017-04-04 16:30 | 860 | 860
2017-04-04 17:00 | 882 | 882
2017-04-04 17:30 | 890 | 890
2017-04-04 18:00 | 898 | 897
2017-04-04 18:30 | 916 | 916
2017-04-04 19:00 | 917 | 917
2017-04-04 19:30 | 891 | 891
2017-04-04 20:00 | 875 | 874
2017-04-04 20:30 | 857 | 855
2017-04-04 21:00 | 817 | 814
2017-04-04 21:30 | 772 | 769
2017-04-04 22:00 | 734 | 732
2017-04-04 22:30 | 725 | 725
2017-04-04 23:00 | 722 | 722
2017-04-04 23:30 | 670 | 669
2017-04-05 | 618 | 614
2017-04-05 00:30 | 570 | 565
2017-04-05 01:00 | 542 | 534
2017-04-05 01:30 | 524 | 515
2017-04-05 02:00 | 510 | 500
2017-04-05 02:30 | 498 | 486
2017-04-05 03:00 | 491 | 478
2017-04-05 03:30 | 496 | 484
2017-04-05 04:00 | 502 | 490
2017-04-05 04:30 | 516 | 505
2017-04-05 05:00 | 533 | 525
2017-04-05 05:30 | 576 | 572
2017-04-05 06:00 | 613 | 610
2017-04-05 06:30 | 669 | 668
2017-04-05 07:00 | 721 | 720
2017-04-05 07:30 | 755 | 755
2017-04-05 08:00 | 775 | 774
2017-04-05 08:30 | 797 | 794
2017-04-05 09:00 | 777 | 776
2017-04-05 09:30 | 768 | 768
2017-04-05 10:00 | 771 | 771
2017-04-05 10:30 | 771 | 771
2017-04-05 11:00 | 783 | 783
2017-04-05 11:30 | 787 | 787
2017-04-05 12:00 | 763 | 763
2017-04-05 12:30 | 755 | 755
2017-04-05 13:00 | 757 | 757
2017-04-05 13:30 | 765 | 765
2017-04-05 14:00 | 782 | 782
2017-04-05 14:30 | 810 | 809
2017-04-05 15:00 | 803 | 802
2017-04-05 15:30 | 834 | 833
2017-04-05 16:00 | 845 | 843
2017-04-05 16:30 | 870 | 868
2017-04-05 17:00 | 887 | 885
2017-04-05 17:30 | 905 | 903
2017-04-05 18:00 | 915 | 913
2017-04-05 18:30 | 918 | 917
2017-04-05 19:00 | 920 | 918
2017-04-05 19:30 | 895 | 893
2017-04-05 20:00 | 876 | 874
2017-04-05 20:30 | 860 | 856
2017-04-05 21:00 | 809 | 808
2017-04-05 21:30 | 773 | 772
2017-04-05 22:00 | 731 | 731
2017-04-05 22:30 | 726 | 726
2017-04-05 23:00 | 721 | 720
2017-04-05 23:30 | 680 | 678
2017-04-06 | 634 | 631
2017-04-06 00:30 | 582 | 577
2017-04-06 01:00 | 559 | 552
2017-04-06 01:30 | 545 | 537
2017-04-06 02:00 | 532 | 522
2017-04-06 02:30 | 524 | 512
2017-04-06 03:00 | 515 | 503
2017-04-06 03:30 | 515 | 502
2017-04-06 04:00 | 517 | 504
2017-04-06 04:30 | 526 | 516
2017-04-06 05:00 | 538 | 529
2017-04-06 05:30 | 573 | 568
2017-04-06 06:00 | 619 | 615
2017-04-06 06:30 | 687 | 684
2017-04-06 07:00 | 723 | 722
2017-04-06 07:30 | 766 | 765
2017-04-06 08:00 | 788 | 785
2017-04-06 08:30 | 802 | 801
2017-04-06 09:00 | 796 | 795
2017-04-06 09:30 | 810 | 810
2017-04-06 10:00 | 794 | 794
2017-04-06 10:30 | 817 | 817
2017-04-06 11:00 | 827 | 827
2017-04-06 11:30 | 805 | 804
2017-04-06 12:00 | 794 | 794
2017-04-06 12:30 | 792 | 792
2017-04-06 13:00 | 801 | 801
2017-04-06 13:30 | 815 | 815
2017-04-06 14:00 | 826 | 826
2017-04-06 14:30 | 841 | 841
2017-04-06 15:00 | 847 | 847
2017-04-06 15:30 | 850 | 850
2017-04-06 16:00 | 864 | 864
2017-04-06 16:30 | 865 | 865
2017-04-06 17:00 | 900 | 900
2017-04-06 17:30 | 912 | 912
2017-04-06 18:00 | 938 | 938
2017-04-06 18:30 | 950 | 950
2017-04-06 19:00 | 955 | 953
2017-04-06 19:30 | 925 | 923
2017-04-06 20:00 | 909 | 909
2017-04-06 20:30 | 895 | 895
2017-04-06 21:00 | 845 | 844
2017-04-06 21:30 | 802 | 802
2017-04-06 22:00 | 767 | 766
2017-04-06 22:30 | 751 | 751
2017-04-06 23:00 | 746 | 746
2017-04-06 23:30 | 692 | 692
2017-04-07 | 637 | 635
2017-04-07 00:30 | 588 | 584
2017-04-07 01:00 | 554 | 548
2017-04-07 01:30 | 539 | 531
2017-04-07 02:00 | 529 | 519
2017-04-07 02:30 | 525 | 515
2017-04-07 03:00 | 518 | 507
2017-04-07 03:30 | 520 | 509
2017-04-07 04:00 | 528 | 518
2017-04-07 04:30 | 544 | 535
2017-04-07 05:00 | 561 | 555
2017-04-07 05:30 | 593 | 590
2017-04-07 06:00 | 634 | 632
2017-04-07 06:30 | 687 | 685
2017-04-07 07:00 | 740 | 732
2017-04-07 07:30 | 762 | 758
2017-04-07 08:00 | 769 | 764
2017-04-07 08:30 | 774 | 770
2017-04-07 09:00 | 766 | 763
2017-04-07 09:30 | 831 | 829
2017-04-07 10:00 | 761 | 760
2017-04-07 10:30 | 757 | 756
2017-04-07 11:00 | 745 | 743
2017-04-07 11:30 | 736 | 733
2017-04-07 12:00 | 755 | 752
2017-04-07 12:30 | 789 | 785
2017-04-07 13:00 | 746 | 743
2017-04-07 13:30 | 747 | 744
2017-04-07 14:00 | 751 | 748
2017-04-07 14:30 | 774 | 772
2017-04-07 15:00 | 793 | 791
2017-04-07 15:30 | 805 | 802
2017-04-07 16:00 | 842 | 839
2017-04-07 16:30 | 859 | 857
2017-04-07 17:00 | 885 | 883
2017-04-07 17:30 | 888 | 885
2017-04-07 18:00 | 892 | 889
2017-04-07 18:30 | 898 | 896
2017-04-07 19:00 | 906 | 902
2017-04-07 19:30 | 887 | 876
2017-04-07 20:00 | 875 | 862
2017-04-07 20:30 | 838 | 829
2017-04-07 21:00 | 796 | 789
2017-04-07 21:30 | 764 | 760
2017-04-07 22:00 | 731 | 730
2017-04-07 22:30 | 740 | 739
2017-04-07 23:00 | 737 | 736
2017-04-07 23:30 | 681 | 680
2017-04-08 | 628 | 626
2017-04-08 00:30 | 586 | 582
2017-04-08 01:00 | 562 | 556
2017-04-08 01:30 | 543 | 534
2017-04-08 02:00 | 523 | 512
2017-04-08 02:30 | 508 | 496
2017-04-08 03:00 | 499 | 486
2017-04-08 03:30 | 500 | 485
2017-04-08 04:00 | 506 | 491
2017-04-08 04:30 | 512 | 497
2017-04-08 05:00 | 524 | 510
2017-04-08 05:30 | 538 | 527
2017-04-08 06:00 | 553 | 545
2017-04-08 06:30 | 591 | 582
2017-04-08 07:00 | 615 | 610
2017-04-08 07:30 | 627 | 625
2017-04-08 08:00 | 643 | 641
2017-04-08 08:30 | 653 | 652
2017-04-08 09:00 | 676 | 674
2017-04-08 09:30 | 689 | 687
2017-04-08 10:00 | 683 | 677
2017-04-08 10:30 | 669 | 665
2017-04-08 11:00 | 656 | 655
2017-04-08 11:30 | 666 | 661
2017-04-08 12:00 | 656 | 650
2017-04-08 12:30 | 652 | 645
2017-04-08 13:00 | 647 | 643
2017-04-08 13:30 | 648 | 646
2017-04-08 14:00 | 667 | 666
2017-04-08 14:30 | 665 | 663
2017-04-08 15:00 | 676 | 675
2017-04-08 15:30 | 710 | 709
2017-04-08 16:00 | 745 | 741
2017-04-08 16:30 | 771 | 767
2017-04-08 17:00 | 796 | 793
2017-04-08 17:30 | 810 | 807
2017-04-08 18:00 | 823 | 822
2017-04-08 18:30 | 846 | 844
2017-04-08 19:00 | 851 | 847
2017-04-08 19:30 | 828 | 822
2017-04-08 20:00 | 806 | 802
2017-04-08 20:30 | 787 | 785
2017-04-08 21:00 | 751 | 750
2017-04-08 21:30 | 720 | 719
2017-04-08 22:00 | 703 | 702
2017-04-08 22:30 | 707 | 705
2017-04-08 23:00 | 719 | 717
2017-04-08 23:30 | 682 | 677
2017-04-09 | 636 | 632
2017-04-09 00:30 | 591 | 584
2017-04-09 01:00 | 563 | 555
2017-04-09 01:30 | 546 | 536
2017-04-09 02:00 | 525 | 512
2017-04-09 02:30 | 518 | 502
2017-04-09 03:00 | 511 | 495
2017-04-09 03:30 | 504 | 487
2017-04-09 04:00 | 498 | 481
2017-04-09 04:30 | 499 | 482
2017-04-09 05:00 | 502 | 486
2017-04-09 05:30 | 511 | 497
2017-04-09 06:00 | 526 | 513
2017-04-09 06:30 | 546 | 532
2017-04-09 07:00 | 562 | 551
2017-04-09 07:30 | 577 | 568
2017-04-09 08:00 | 586 | 581
2017-04-09 08:30 | 593 | 591
2017-04-09 09:00 | 603 | 599
2017-04-09 09:30 | 615 | 612
2017-04-09 10:00 | 625 | 623
2017-04-09 10:30 | 639 | 638
2017-04-09 11:00 | 634 | 633
2017-04-09 11:30 | 629 | 627
2017-04-09 12:00 | 633 | 631
2017-04-09 12:30 | 651 | 649
2017-04-09 13:00 | 651 | 649
2017-04-09 13:30 | 654 | 652
2017-04-09 14:00 | 671 | 669
2017-04-09 14:30 | 698 | 697
2017-04-09 15:00 | 703 | 701
2017-04-09 15:30 | 674 | 673
2017-04-09 16:00 | 709 | 708
2017-04-09 16:30 | 749 | 748
2017-04-09 17:00 | 804 | 801
2017-04-09 17:30 | 801 | 799
2017-04-09 18:00 | 817 | 815
2017-04-09 18:30 | 846 | 844
2017-04-09 19:00 | 842 | 839
2017-04-09 19:30 | 817 | 813
2017-04-09 20:00 | 806 | 804
2017-04-09 20:30 | 788 | 785
2017-04-09 21:00 | 747 | 747
2017-04-09 21:30 | 724 | 724
2017-04-09 22:00 | 701 | 701
2017-04-09 22:30 | 699 | 699
2017-04-09 23:00 | 704 | 703
2017-04-09 23:30 | 659 | 657
2017-04-10 | 613 | 609
2017-04-10 00:30 | 568 | 561
2017-04-10 01:00 | 549 | 540
2017-04-10 01:30 | 530 | 519
2017-04-10 02:00 | 520 | 507
2017-04-10 02:30 | 517 | 504
2017-04-10 03:00 | 512 | 498
2017-04-10 03:30 | 510 | 495
2017-04-10 04:00 | 511 | 497
2017-04-10 04:30 | 521 | 509
2017-04-10 05:00 | 532 | 523
2017-04-10 05:30 | 568 | 563
2017-04-10 06:00 | 605 | 604
2017-04-10 06:30 | 666 | 665
2017-04-10 07:00 | 714 | 711
2017-04-10 07:30 | 752 | 752
2017-04-10 08:00 | 770 | 770
2017-04-10 08:30 | 780 | 779
2017-04-10 09:00 | 786 | 783
2017-04-10 09:30 | 785 | 782
2017-04-10 10:00 | 783 | 782
2017-04-10 10:30 | 788 | 788
2017-04-10 11:00 | 780 | 779
2017-04-10 11:30 | 773 | 773
2017-04-10 12:00 | 787 | 786
2017-04-10 12:30 | 792 | 792
2017-04-10 13:00 | 808 | 807
2017-04-10 13:30 | 808 | 807
2017-04-10 14:00 | 827 | 826
2017-04-10 14:30 | 844 | 843
2017-04-10 15:00 | 870 | 870
2017-04-10 15:30 | 884 | 883
2017-04-10 16:00 | 897 | 896
2017-04-10 16:30 | 915 | 914
2017-04-10 17:00 | 930 | 928
2017-04-10 17:30 | 925 | 922
2017-04-10 18:00 | 930 | 928
2017-04-10 18:30 | 938 | 933
2017-04-10 19:00 | 929 | 926
2017-04-10 19:30 | 902 | 899
2017-04-10 20:00 | 881 | 877
2017-04-10 20:30 | 871 | 866
2017-04-10 21:00 | 825 | 824
2017-04-10 21:30 | 783 | 781
2017-04-10 22:00 | 743 | 742
2017-04-10 22:30 | 740 | 737
2017-04-10 23:00 | 741 | 738
2017-04-10 23:30 | 688 | 684
2017-04-11 | 635 | 628
2017-04-11 00:30 | 575 | 568
2017-04-11 01:00 | 553 | 545
2017-04-11 01:30 | 534 | 524
2017-04-11 02:00 | 516 | 504
2017-04-11 02:30 | 495 | 481
2017-04-11 03:00 | 484 | 469
2017-04-11 03:30 | 485 | 470
2017-04-11 04:00 | 493 | 477
2017-04-11 04:30 | 503 | 490
2017-04-11 05:00 | 524 | 513
2017-04-11 05:30 | 574 | 568
2017-04-11 06:00 | 616 | 613
2017-04-11 06:30 | 673 | 673
2017-04-11 07:00 | 715 | 715
2017-04-11 07:30 | 750 | 749
2017-04-11 08:00 | 758 | 757
2017-04-11 08:30 | 759 | 756
2017-04-11 09:00 | 742 | 740
2017-04-11 09:30 | 707 | 706
2017-04-11 10:00 | 694 | 693
2017-04-11 10:30 | 694 | 691
2017-04-11 11:00 | 691 | 688
2017-04-11 11:30 | 682 | 679
2017-04-11 12:00 | 686 | 682
2017-04-11 12:30 | 700 | 694
2017-04-11 13:00 | 707 | 704
2017-04-11 13:30 | 717 | 714
2017-04-11 14:00 | 742 | 738
2017-04-11 14:30 | 761 | 756
2017-04-11 15:00 | 808 | 803
2017-04-11 15:30 | 833 | 829
2017-04-11 16:00 | 863 | 863
2017-04-11 16:30 | 887 | 887
2017-04-11 17:00 | 911 | 911
2017-04-11 17:30 | 920 | 919
2017-04-11 18:00 | 938 | 938
2017-04-11 18:30 | 949 | 949
2017-04-11 19:00 | 946 | 946
2017-04-11 19:30 | 919 | 917
2017-04-11 20:00 | 905 | 902
2017-04-11 20:30 | 889 | 884
2017-04-11 21:00 | 842 | 839
2017-04-11 21:30 | 803 | 803
2017-04-11 22:00 | 775 | 773
2017-04-11 22:30 | 759 | 755
2017-04-11 23:00 | 754 | 751
2017-04-11 23:30 | 709 | 707
2017-04-12 | 657 | 654
2017-04-12 00:30 | 616 | 610
2017-04-12 01:00 | 597 | 588
2017-04-12 01:30 | 579 | 568
2017-04-12 02:00 | 561 | 549
2017-04-12 02:30 | 545 | 531
2017-04-12 03:00 | 532 | 517
2017-04-12 03:30 | 529 | 512
2017-04-12 04:00 | 535 | 519
2017-04-12 04:30 | 547 | 533
2017-04-12 05:00 | 557 | 546
2017-04-12 05:30 | 597 | 592
2017-04-12 06:00 | 643 | 641
2017-04-12 06:30 | 693 | 691
2017-04-12 07:00 | 737 | 736
2017-04-12 07:30 | 780 | 780
2017-04-12 08:00 | 783 | 782
2017-04-12 08:30 | 779 | 778
2017-04-12 09:00 | 781 | 778
2017-04-12 09:30 | 793 | 789
2017-04-12 10:00 | 787 | 785
2017-04-12 10:30 | 782 | 780
2017-04-12 11:00 | 782 | 779
2017-04-12 11:30 | 793 | 793
2017-04-12 12:00 | 789 | 789
2017-04-12 12:30 | 799 | 799
2017-04-12 13:00 | 824 | 824
2017-04-12 13:30 | 839 | 838
2017-04-12 14:00 | 845 | 845
2017-04-12 14:30 | 851 | 851
2017-04-12 15:00 | 866 | 865
2017-04-12 15:30 | 896 | 896
2017-04-12 16:00 | 919 | 917
2017-04-12 16:30 | 935 | 935
2017-04-12 17:00 | 953 | 953
2017-04-12 17:30 | 951 | 951
2017-04-12 18:00 | 955 | 955
2017-04-12 18:30 | 962 | 962
2017-04-12 19:00 | 957 | 957
2017-04-12 19:30 | 933 | 932
2017-04-12 20:00 | 916 | 915
2017-04-12 20:30 | 898 | 896
2017-04-12 21:00 | 858 | 856
2017-04-12 21:30 | 815 | 814
2017-04-12 22:00 | 779 | 778
2017-04-12 22:30 | 767 | 764
2017-04-12 23:00 | 767 | 763
2017-04-12 23:30 | 711 | 708
2017-04-13 | 667 | 664
2017-04-13 00:30 | 618 | 613
2017-04-13 01:00 | 592 | 584
2017-04-13 01:30 | 576 | 566
2017-04-13 02:00 | 565 | 553
2017-04-13 02:30 | 558 | 545
2017-04-13 03:00 | 554 | 541
2017-04-13 03:30 | 556 | 543
2017-04-13 04:00 | 557 | 544
2017-04-13 04:30 | 568 | 556
2017-04-13 05:00 | 579 | 569
2017-04-13 05:30 | 614 | 609
2017-04-13 06:00 | 647 | 644
2017-04-13 06:30 | 696 | 695
2017-04-13 07:00 | 742 | 740
2017-04-13 07:30 | 779 | 779
2017-04-13 08:00 | 805 | 805
2017-04-13 08:30 | 825 | 819
2017-04-13 09:00 | 817 | 811
2017-04-13 09:30 | 810 | 805
2017-04-13 10:00 | 810 | 806
2017-04-13 10:30 | 803 | 801
2017-04-13 11:00 | 804 | 802
2017-04-13 11:30 | 806 | 804
2017-04-13 12:00 | 817 | 816
2017-04-13 12:30 | 819 | 818
2017-04-13 13:00 | 829 | 828
2017-04-13 13:30 | 844 | 843
2017-04-13 14:00 | 836 | 834
2017-04-13 14:30 | 836 | 834
2017-04-13 15:00 | 843 | 841
2017-04-13 15:30 | 856 | 854
2017-04-13 16:00 | 869 | 866
2017-04-13 16:30 | 888 | 884
2017-04-13 17:00 | 904 | 901
2017-04-13 17:30 | 908 | 904
2017-04-13 18:00 | 918 | 916
2017-04-13 18:30 | 928 | 925
2017-04-13 19:00 | 926 | 922
2017-04-13 19:30 | 902 | 895
2017-04-13 20:00 | 885 | 878
2017-04-13 20:30 | 866 | 861
2017-04-13 21:00 | 825 | 820
2017-04-13 21:30 | 784 | 781
2017-04-13 22:00 | 760 | 758
2017-04-13 22:30 | 749 | 745
2017-04-13 23:00 | 748 | 744
2017-04-13 23:30 | 698 | 695
2017-04-14 | 653 | 649
2017-04-14 00:30 | 608 | 600
2017-04-14 01:00 | 586 | 574
2017-04-14 01:30 | 565 | 550
2017-04-14 02:00 | 550 | 532
2017-04-14 02:30 | 540 | 521
2017-04-14 03:00 | 538 | 518
2017-04-14 03:30 | 537 | 516
2017-04-14 04:00 | 531 | 508
2017-04-14 04:30 | 532 | 508
2017-04-14 05:00 | 535 | 511
2017-04-14 05:30 | 544 | 521
2017-04-14 06:00 | 554 | 535
2017-04-14 06:30 | 565 | 547
2017-04-14 07:00 | 582 | 566
2017-04-14 07:30 | 601 | 590
2017-04-14 08:00 | 627 | 620
2017-04-14 08:30 | 639 | 635
2017-04-14 09:00 | 642 | 639
2017-04-14 09:30 | 659 | 653
2017-04-14 10:00 | 659 | 652
2017-04-14 10:30 | 650 | 643
2017-04-14 11:00 | 630 | 627
2017-04-14 11:30 | 613 | 611
2017-04-14 12:00 | 609 | 608
2017-04-14 12:30 | 604 | 602
2017-04-14 13:00 | 631 | 630
2017-04-14 13:30 | 616 | 615
2017-04-14 14:00 | 624 | 623
2017-04-14 14:30 | 621 | 619
2017-04-14 15:00 | 641 | 640
2017-04-14 15:30 | 672 | 665
2017-04-14 16:00 | 692 | 683
2017-04-14 16:30 | 703 | 695
2017-04-14 17:00 | 725 | 719
2017-04-14 17:30 | 750 | 745
2017-04-14 18:00 | 780 | 778
2017-04-14 18:30 | 794 | 793
2017-04-14 19:00 | 791 | 789
2017-04-14 19:30 | 778 | 775
2017-04-14 20:00 | 768 | 764
2017-04-14 20:30 | 760 | 754
2017-04-14 21:00 | 732 | 724
2017-04-14 21:30 | 717 | 706
2017-04-14 22:00 | 704 | 693
2017-04-14 22:30 | 694 | 690
2017-04-14 23:00 | 704 | 701
2017-04-14 23:30 | 669 | 664
2017-04-15 | 632 | 624
2017-04-15 00:30 | 590 | 579
2017-04-15 01:00 | 563 | 549
2017-04-15 01:30 | 551 | 534
2017-04-15 02:00 | 534 | 516
2017-04-15 02:30 | 529 | 510
2017-04-15 03:00 | 524 | 505
2017-04-15 03:30 | 519 | 501
2017-04-15 04:00 | 521 | 502
2017-04-15 04:30 | 523 | 504
2017-04-15 05:00 | 526 | 507
2017-04-15 05:30 | 530 | 511
2017-04-15 06:00 | 540 | 523
2017-04-15 06:30 | 554 | 535
2017-04-15 07:00 | 570 | 552
2017-04-15 07:30 | 583 | 571
2017-04-15 08:00 | 598 | 592
2017-04-15 08:30 | 613 | 610
2017-04-15 09:00 | 629 | 628
2017-04-15 09:30 | 632 | 631
2017-04-15 10:00 | 632 | 632
2017-04-15 10:30 | 622 | 622
2017-04-15 11:00 | 617 | 617
2017-04-15 11:30 | 626 | 626
2017-04-15 12:00 | 634 | 634
2017-04-15 12:30 | 636 | 636
2017-04-15 13:00 | 639 | 639
2017-04-15 13:30 | 640 | 640
2017-04-15 14:00 | 649 | 649
2017-04-15 14:30 | 656 | 654
2017-04-15 15:00 | 659 | 657
2017-04-15 15:30 | 677 | 675
2017-04-15 16:00 | 701 | 699
2017-04-15 16:30 | 725 | 723
2017-04-15 17:00 | 758 | 757
2017-04-15 17:30 | 770 | 769
2017-04-15 18:00 | 794 | 794
2017-04-15 18:30 | 819 | 812
2017-04-15 19:00 | 814 | 803
2017-04-15 19:30 | 800 | 786
2017-04-15 20:00 | 781 | 776
2017-04-15 20:30 | 774 | 769
2017-04-15 21:00 | 740 | 735
2017-04-15 21:30 | 712 | 711
2017-04-15 22:00 | 704 | 703
2017-04-15 22:30 | 700 | 698
2017-04-15 23:00 | 715 | 712
2017-04-15 23:30 | 673 | 669
2017-04-16 | 636 | 630
2017-04-16 00:30 | 597 | 586
2017-04-16 01:00 | 573 | 560
2017-04-16 01:30 | 552 | 537
2017-04-16 02:00 | 544 | 526
2017-04-16 02:30 | 532 | 513
2017-04-16 03:00 | 528 | 509
2017-04-16 03:30 | 530 | 510
2017-04-16 04:00 | 524 | 503
2017-04-16 04:30 | 522 | 501
2017-04-16 05:00 | 527 | 506
2017-04-16 05:30 | 534 | 514
2017-04-16 06:00 | 545 | 526
2017-04-16 06:30 | 562 | 541
2017-04-16 07:00 | 572 | 552
2017-04-16 07:30 | 579 | 565
2017-04-16 08:00 | 590 | 581
2017-04-16 08:30 | 606 | 601
2017-04-16 09:00 | 612 | 610
2017-04-16 09:30 | 624 | 622
2017-04-16 10:00 | 623 | 622
2017-04-16 10:30 | 639 | 637
2017-04-16 11:00 | 613 | 606
2017-04-16 11:30 | 608 | 600
2017-04-16 12:00 | 595 | 588
2017-04-16 12:30 | 598 | 591
2017-04-16 13:00 | 599 | 592
2017-04-16 13:30 | 610 | 605
2017-04-16 14:00 | 612 | 607
2017-04-16 14:30 | 607 | 601
2017-04-16 15:00 | 628 | 623
2017-04-16 15:30 | 648 | 643
2017-04-16 16:00 | 679 | 675
2017-04-16 16:30 | 709 | 707
2017-04-16 17:00 | 738 | 736
2017-04-16 17:30 | 749 | 747
2017-04-16 18:00 | 774 | 772
2017-04-16 18:30 | 792 | 789
2017-04-16 19:00 | 792 | 789
2017-04-16 19:30 | 767 | 765
2017-04-16 20:00 | 755 | 755
2017-04-16 20:30 | 750 | 750
2017-04-16 21:00 | 722 | 722
2017-04-16 21:30 | 702 | 701
2017-04-16 22:00 | 691 | 689
2017-04-16 22:30 | 693 | 691
2017-04-16 23:00 | 701 | 698
2017-04-16 23:30 | 667 | 662
2017-04-17 | 625 | 618
2017-04-17 00:30 | 586 | 575
2017-04-17 01:00 | 566 | 551
2017-04-17 01:30 | 552 | 536
2017-04-17 02:00 | 540 | 521
2017-04-17 02:30 | 530 | 510
2017-04-17 03:00 | 528 | 508
2017-04-17 03:30 | 521 | 500
2017-04-17 04:00 | 519 | 497
2017-04-17 04:30 | 522 | 500
2017-04-17 05:00 | 526 | 505
2017-04-17 05:30 | 537 | 518
2017-04-17 06:00 | 548 | 531
2017-04-17 06:30 | 564 | 546
2017-04-17 07:00 | 578 | 562
2017-04-17 07:30 | 595 | 585
2017-04-17 08:00 | 605 | 598
2017-04-17 08:30 | 623 | 620
2017-04-17 09:00 | 637 | 636
2017-04-17 09:30 | 642 | 641
2017-04-17 10:00 | 648 | 648
2017-04-17 10:30 | 653 | 653
2017-04-17 11:00 | 650 | 650
2017-04-17 11:30 | 649 | 649
2017-04-17 12:00 | 648 | 648
2017-04-17 12:30 | 651 | 651
2017-04-17 13:00 | 655 | 655
2017-04-17 13:30 | 666 | 666
2017-04-17 14:00 | 676 | 676
2017-04-17 14:30 | 690 | 690
2017-04-17 15:00 | 701 | 701
2017-04-17 15:30 | 724 | 724
2017-04-17 16:00 | 763 | 763
2017-04-17 16:30 | 803 | 799
2017-04-17 17:00 | 839 | 826
2017-04-17 17:30 | 859 | 847
2017-04-17 18:00 | 899 | 891
2017-04-17 18:30 | 904 | 893
2017-04-17 19:00 | 886 | 877
2017-04-17 19:30 | 845 | 843
2017-04-17 20:00 | 836 | 833
2017-04-17 20:30 | 813 | 811
2017-04-17 21:00 | 769 | 768
2017-04-17 21:30 | 736 | 735
2017-04-17 22:00 | 718 | 716
2017-04-17 22:30 | 712 | 709
2017-04-17 23:00 | 713 | 710
2017-04-17 23:30 | 676 | 671
2017-04-18 | 631 | 624
2017-04-18 00:30 | 588 | 577
2017-04-18 01:00 | 566 | 553
2017-04-18 01:30 | 553 | 538
2017-04-18 02:00 | 539 | 522
2017-04-18 02:30 | 533 | 516
2017-04-18 03:00 | 524 | 506
2017-04-18 03:30 | 528 | 510
2017-04-18 04:00 | 531 | 513
2017-04-18 04:30 | 545 | 529
2017-04-18 05:00 | 558 | 545
2017-04-18 05:30 | 597 | 590
2017-04-18 06:00 | 648 | 643
2017-04-18 06:30 | 709 | 706
2017-04-18 07:00 | 770 | 764
2017-04-18 07:30 | 811 | 804
2017-04-18 08:00 | 820 | 811
2017-04-18 08:30 | 810 | 804
2017-04-18 09:00 | 798 | 792
2017-04-18 09:30 | 806 | 801
2017-04-18 10:00 | 809 | 806
2017-04-18 10:30 | 806 | 803
2017-04-18 11:00 | 803 | 800
2017-04-18 11:30 | 794 | 791
2017-04-18 12:00 | 796 | 794
2017-04-18 12:30 | 801 | 798
2017-04-18 13:00 | 813 | 811
2017-04-18 13:30 | 816 | 815
2017-04-18 14:00 | 835 | 833
2017-04-18 14:30 | 856 | 854
2017-04-18 15:00 | 868 | 865
2017-04-18 15:30 | 869 | 865
2017-04-18 16:00 | 889 | 886
2017-04-18 16:30 | 913 | 909
2017-04-18 17:00 | 940 | 936
2017-04-18 17:30 | 958 | 954
2017-04-18 18:00 | 975 | 973
2017-04-18 18:30 | 970 | 966
2017-04-18 19:00 | 957 | 952
2017-04-18 19:30 | 929 | 928
2017-04-18 20:00 | 915 | 914
2017-04-18 20:30 | 897 | 896
2017-04-18 21:00 | 847 | 847
2017-04-18 21:30 | 806 | 806
2017-04-18 22:00 | 773 | 773
2017-04-18 22:30 | 762 | 761
2017-04-18 23:00 | 755 | 754
2017-04-18 23:30 | 710 | 706
2017-04-19 | 659 | 653
2017-04-19 00:30 | 622 | 613
2017-04-19 01:00 | 592 | 582
2017-04-19 01:30 | 573 | 561
2017-04-19 02:00 | 566 | 553
2017-04-19 02:30 | 558 | 545
2017-04-19 03:00 | 552 | 537
2017-04-19 03:30 | 550 | 534
2017-04-19 04:00 | 553 | 538
2017-04-19 04:30 | 561 | 548
2017-04-19 05:00 | 577 | 566
2017-04-19 05:30 | 616 | 610
2017-04-19 06:00 | 656 | 653
2017-04-19 06:30 | 720 | 718
2017-04-19 07:00 | 773 | 769
2017-04-19 07:30 | 818 | 818
2017-04-19 08:00 | 823 | 822
2017-04-19 08:30 | 813 | 812
2017-04-19 09:00 | 806 | 804
2017-04-19 09:30 | 809 | 808
2017-04-19 10:00 | 819 | 819
2017-04-19 10:30 | 841 | 840
2017-04-19 11:00 | 828 | 827
2017-04-19 11:30 | 812 | 810
2017-04-19 12:00 | 825 | 823
2017-04-19 12:30 | 802 | 799
2017-04-19 13:00 | 807 | 805
2017-04-19 13:30 | 808 | 805
2017-04-19 14:00 | 822 | 819
2017-04-19 14:30 | 833 | 828
2017-04-19 15:00 | 827 | 821
2017-04-19 15:30 | 850 | 844
2017-04-19 16:00 | 880 | 874
2017-04-19 16:30 | 903 | 897
2017-04-19 17:00 | 929 | 923
2017-04-19 17:30 | 945 | 940
2017-04-19 18:00 | 965 | 963
2017-04-19 18:30 | 966 | 963
2017-04-19 19:00 | 966 | 961
2017-04-19 19:30 | 930 | 925
2017-04-19 20:00 | 912 | 910
2017-04-19 20:30 | 890 | 888
2017-04-19 21:00 | 852 | 852
2017-04-19 21:30 | 815 | 815
2017-04-19 22:00 | 784 | 784
2017-04-19 22:30 | 767 | 766
2017-04-19 23:00 | 762 | 760
2017-04-19 23:30 | 720 | 717
2017-04-20 | 673 | 667
2017-04-20 00:30 | 617 | 608
2017-04-20 01:00 | 594 | 583
2017-04-20 01:30 | 579 | 567
2017-04-20 02:00 | 568 | 553
2017-04-20 02:30 | 561 | 544
2017-04-20 03:00 | 551 | 533
2017-04-20 03:30 | 549 | 532
2017-04-20 04:00 | 554 | 537
2017-04-20 04:30 | 561 | 546
2017-04-20 05:00 | 580 | 568
2017-04-20 05:30 | 618 | 611
2017-04-20 06:00 | 656 | 652
2017-04-20 06:30 | 721 | 715
2017-04-20 07:00 | 783 | 775
2017-04-20 07:30 | 830 | 828
2017-04-20 08:00 | 831 | 830
2017-04-20 08:30 | 832 | 832
2017-04-20 09:00 | 831 | 831
2017-04-20 09:30 | 822 | 822
2017-04-20 10:00 | 803 | 803
2017-04-20 10:30 | 809 | 809
2017-04-20 11:00 | 800 | 800
2017-04-20 11:30 | 779 | 779
2017-04-20 12:00 | 789 | 789
2017-04-20 12:30 | 785 | 785
2017-04-20 13:00 | 791 | 791
2017-04-20 13:30 | 803 | 803
2017-04-20 14:00 | 822 | 821
2017-04-20 14:30 | 848 | 848
2017-04-20 15:00 | 856 | 855
2017-04-20 15:30 | 853 | 853
2017-04-20 16:00 | 872 | 872
2017-04-20 16:30 | 906 | 906
2017-04-20 17:00 | 930 | 930
2017-04-20 17:30 | 950 | 950
2017-04-20 18:00 | 972 | 971
2017-04-20 18:30 | 972 | 972
2017-04-20 19:00 | 964 | 963
2017-04-20 19:30 | 939 | 937
2017-04-20 20:00 | 930 | 927
2017-04-20 20:30 | 909 | 907
2017-04-20 21:00 | 865 | 865
2017-04-20 21:30 | 819 | 819
2017-04-20 22:00 | 784 | 784
2017-04-20 22:30 | 772 | 771
2017-04-20 23:00 | 759 | 758
2017-04-20 23:30 | 718 | 714
2017-04-21 | 668 | 661
2017-04-21 00:30 | 618 | 608
2017-04-21 01:00 | 591 | 579
2017-04-21 01:30 | 568 | 553
2017-04-21 02:00 | 560 | 544
2017-04-21 02:30 | 553 | 538
2017-04-21 03:00 | 548 | 533
2017-04-21 03:30 | 550 | 535
2017-04-21 04:00 | 549 | 533
2017-04-21 04:30 | 558 | 544
2017-04-21 05:00 | 559 | 549
2017-04-21 05:30 | 575 | 567
2017-04-21 06:00 | 618 | 614
2017-04-21 06:30 | 678 | 677
2017-04-21 07:00 | 738 | 737
2017-04-21 07:30 | 780 | 780
2017-04-21 08:00 | 790 | 788
2017-04-21 08:30 | 787 | 787
2017-04-21 09:00 | 769 | 769
2017-04-21 09:30 | 777 | 777
2017-04-21 10:00 | 803 | 803
2017-04-21 10:30 | 803 | 803
2017-04-21 11:00 | 794 | 791
2017-04-21 11:30 | 787 | 784
2017-04-21 12:00 | 786 | 782
2017-04-21 12:30 | 781 | 777
2017-04-21 13:00 | 785 | 781
2017-04-21 13:30 | 795 | 791
2017-04-21 14:00 | 812 | 809
2017-04-21 14:30 | 819 | 815
2017-04-21 15:00 | 819 | 814
2017-04-21 15:30 | 818 | 813
2017-04-21 16:00 | 830 | 825
2017-04-21 16:30 | 846 | 842
2017-04-21 17:00 | 864 | 862
2017-04-21 17:30 | 874 | 872
2017-04-21 18:00 | 902 | 899
2017-04-21 18:30 | 890 | 883
2017-04-21 19:00 | 885 | 877
2017-04-21 19:30 | 855 | 850
2017-04-21 20:00 | 836 | 835
2017-04-21 20:30 | 826 | 825
2017-04-21 21:00 | 787 | 786
2017-04-21 21:30 | 757 | 756
2017-04-21 22:00 | 734 | 732
2017-04-21 22:30 | 720 | 715
2017-04-21 23:00 | 732 | 728
2017-04-21 23:30 | 676 | 673
2017-04-22 | 641 | 635
2017-04-22 00:30 | 600 | 591
2017-04-22 01:00 | 584 | 571
2017-04-22 01:30 | 562 | 547
2017-04-22 02:00 | 542 | 525
2017-04-22 02:30 | 535 | 516
2017-04-22 03:00 | 527 | 507
2017-04-22 03:30 | 525 | 505
2017-04-22 04:00 | 523 | 502
2017-04-22 04:30 | 527 | 508
2017-04-22 05:00 | 540 | 522
2017-04-22 05:30 | 557 | 543
2017-04-22 06:00 | 579 | 568
2017-04-22 06:30 | 605 | 596
2017-04-22 07:00 | 636 | 629
2017-04-22 07:30 | 675 | 672
2017-04-22 08:00 | 701 | 699
2017-04-22 08:30 | 723 | 722
2017-04-22 09:00 | 735 | 734
2017-04-22 09:30 | 738 | 737
2017-04-22 10:00 | 738 | 738
2017-04-22 10:30 | 735 | 734
2017-04-22 11:00 | 717 | 716
2017-04-22 11:30 | 707 | 706
2017-04-22 12:00 | 688 | 686
2017-04-22 12:30 | 669 | 667
2017-04-22 13:00 | 651 | 649
2017-04-22 13:30 | 639 | 637
2017-04-22 14:00 | 641 | 639
2017-04-22 14:30 | 657 | 655
2017-04-22 15:00 | 679 | 678
2017-04-22 15:30 | 695 | 694
2017-04-22 16:00 | 723 | 723
2017-04-22 16:30 | 761 | 760
2017-04-22 17:00 | 803 | 802
2017-04-22 17:30 | 824 | 822
2017-04-22 18:00 | 857 | 855
2017-04-22 18:30 | 865 | 861
2017-04-22 19:00 | 851 | 846
2017-04-22 19:30 | 834 | 827
2017-04-22 20:00 | 812 | 809
2017-04-22 20:30 | 793 | 791
2017-04-22 21:00 | 752 | 751
2017-04-22 21:30 | 724 | 724
2017-04-22 22:00 | 710 | 710
2017-04-22 22:30 | 715 | 714
2017-04-22 23:00 | 728 | 726
2017-04-22 23:30 | 685 | 682
2017-04-23 | 632 | 625
2017-04-23 00:30 | 581 | 570
2017-04-23 01:00 | 552 | 538
2017-04-23 01:30 | 532 | 515
2017-04-23 02:00 | 516 | 495
2017-04-23 02:30 | 506 | 483
2017-04-23 03:00 | 491 | 467
2017-04-23 03:30 | 488 | 463
2017-04-23 04:00 | 490 | 464
2017-04-23 04:30 | 489 | 463
2017-04-23 05:00 | 497 | 472
2017-04-23 05:30 | 502 | 479
2017-04-23 06:00 | 510 | 490
2017-04-23 06:30 | 530 | 509
2017-04-23 07:00 | 548 | 529
2017-04-23 07:30 | 561 | 547
2017-04-23 08:00 | 569 | 560
2017-04-23 08:30 | 583 | 578
2017-04-23 09:00 | 594 | 591
2017-04-23 09:30 | 599 | 597
2017-04-23 10:00 | 596 | 595
2017-04-23 10:30 | 605 | 604
2017-04-23 11:00 | 607 | 607
2017-04-23 11:30 | 620 | 620
2017-04-23 12:00 | 608 | 607
2017-04-23 12:30 | 605 | 604
2017-04-23 13:00 | 615 | 615
2017-04-23 13:30 | 624 | 624
2017-04-23 14:00 | 636 | 636
2017-04-23 14:30 | 623 | 623
2017-04-23 15:00 | 640 | 640
2017-04-23 15:30 | 668 | 668
2017-04-23 16:00 | 721 | 721
2017-04-23 16:30 | 767 | 766
2017-04-23 17:00 | 804 | 804
2017-04-23 17:30 | 834 | 831
2017-04-23 18:00 | 864 | 863
2017-04-23 18:30 | 879 | 876
2017-04-23 19:00 | 866 | 862
2017-04-23 19:30 | 845 | 838
2017-04-23 20:00 | 831 | 824
2017-04-23 20:30 | 819 | 812
2017-04-23 21:00 | 788 | 777
2017-04-23 21:30 | 739 | 735
2017-04-23 22:00 | 708 | 705
2017-04-23 22:30 | 704 | 702
2017-04-23 23:00 | 715 | 713
2017-04-23 23:30 | 664 | 659
2017-04-24 | 600 | 592
2017-04-24 00:30 | 554 | 542
2017-04-24 01:00 | 529 | 511
2017-04-24 01:30 | 512 | 492
2017-04-24 02:00 | 497 | 473
2017-04-24 02:30 | 490 | 465
2017-04-24 03:00 | 487 | 462
2017-04-24 03:30 | 487 | 462
2017-04-24 04:00 | 489 | 464
2017-04-24 04:30 | 496 | 474
2017-04-24 05:00 | 509 | 491
2017-04-24 05:30 | 559 | 549
2017-04-24 06:00 | 609 | 603
2017-04-24 06:30 | 683 | 672
2017-04-24 07:00 | 749 | 741
2017-04-24 07:30 | 794 | 786
2017-04-24 08:00 | 800 | 790
2017-04-24 08:30 | 786 | 778
2017-04-24 09:00 | 765 | 758
2017-04-24 09:30 | 763 | 758
2017-04-24 10:00 | 760 | 753
2017-04-24 10:30 | 777 | 772
2017-04-24 11:00 | 779 | 774
2017-04-24 11:30 | 773 | 769
2017-04-24 12:00 | 777 | 773
2017-04-24 12:30 | 782 | 778
2017-04-24 13:00 | 776 | 772
2017-04-24 13:30 | 779 | 776
2017-04-24 14:00 | 793 | 790
2017-04-24 14:30 | 817 | 814
2017-04-24 15:00 | 830 | 827
2017-04-24 15:30 | 842 | 838
2017-04-24 16:00 | 865 | 861
2017-04-24 16:30 | 890 | 887
2017-04-24 17:00 | 919 | 914
2017-04-24 17:30 | 933 | 925
2017-04-24 18:00 | 952 | 948
2017-04-24 18:30 | 943 | 938
2017-04-24 19:00 | 936 | 930
2017-04-24 19:30 | 911 | 902
2017-04-24 20:00 | 890 | 881
2017-04-24 20:30 | 850 | 848
2017-04-24 21:00 | 804 | 804
2017-04-24 21:30 | 771 | 770
2017-04-24 22:00 | 742 | 741
2017-04-24 22:30 | 741 | 739
2017-04-24 23:00 | 744 | 741
2017-04-24 23:30 | 698 | 694
2017-04-25 | 643 | 635
2017-04-25 00:30 | 597 | 585
2017-04-25 01:00 | 566 | 551
2017-04-25 01:30 | 556 | 539
2017-04-25 02:00 | 540 | 519
2017-04-25 02:30 | 531 | 508
2017-04-25 03:00 | 522 | 498
2017-04-25 03:30 | 523 | 499
2017-04-25 04:00 | 524 | 502
2017-04-25 04:30 | 528 | 504
2017-04-25 05:00 | 531 | 509
2017-04-25 05:30 | 537 | 516
2017-04-25 06:00 | 550 | 530
2017-04-25 06:30 | 575 | 554
2017-04-25 07:00 | 584 | 565
2017-04-25 07:30 | 595 | 580
2017-04-25 08:00 | 612 | 601
2017-04-25 08:30 | 619 | 611
2017-04-25 09:00 | 622 | 616
2017-04-25 09:30 | 642 | 638
2017-04-25 10:00 | 658 | 656
2017-04-25 10:30 | 665 | 664
2017-04-25 11:00 | 635 | 633
2017-04-25 11:30 | 623 | 621
2017-04-25 12:00 | 614 | 613
2017-04-25 12:30 | 614 | 613
2017-04-25 13:00 | 619 | 618
2017-04-25 13:30 | 615 | 614
2017-04-25 14:00 | 624 | 623
2017-04-25 14:30 | 634 | 633
2017-04-25 15:00 | 656 | 656
2017-04-25 15:30 | 671 | 671
2017-04-25 16:00 | 707 | 706
2017-04-25 16:30 | 745 | 745
2017-04-25 17:00 | 780 | 780
2017-04-25 17:30 | 811 | 811
2017-04-25 18:00 | 848 | 848
2017-04-25 18:30 | 864 | 860
2017-04-25 19:00 | 859 | 853
2017-04-25 19:30 | 840 | 836
2017-04-25 20:00 | 821 | 818
2017-04-25 20:30 | 808 | 807
2017-04-25 21:00 | 773 | 771
2017-04-25 21:30 | 745 | 743
2017-04-25 22:00 | 722 | 720
2017-04-25 22:30 | 713 | 710
2017-04-25 23:00 | 715 | 711
2017-04-25 23:30 | 677 | 671
2017-04-26 | 627 | 618
2017-04-26 00:30 | 588 | 574
2017-04-26 01:00 | 565 | 549
2017-04-26 01:30 | 551 | 532
2017-04-26 02:00 | 541 | 517
2017-04-26 02:30 | 534 | 512
2017-04-26 03:00 | 533 | 512
2017-04-26 03:30 | 526 | 505
2017-04-26 04:00 | 534 | 514
2017-04-26 04:30 | 547 | 529
2017-04-26 05:00 | 564 | 550
2017-04-26 05:30 | 598 | 589
2017-04-26 06:00 | 639 | 635
2017-04-26 06:30 | 703 | 701
2017-04-26 07:00 | 767 | 766
2017-04-26 07:30 | 805 | 805
2017-04-26 08:00 | 840 | 838
2017-04-26 08:30 | 835 | 834
2017-04-26 09:00 | 855 | 855
2017-04-26 09:30 | 888 | 888
2017-04-26 10:00 | 882 | 882
2017-04-26 10:30 | 863 | 863
2017-04-26 11:00 | 870 | 870
2017-04-26 11:30 | 892 | 892
2017-04-26 12:00 | 898 | 898
2017-04-26 12:30 | 901 | 901
2017-04-26 13:00 | 886 | 886
2017-04-26 13:30 | 867 | 867
2017-04-26 14:00 | 877 | 877
2017-04-26 14:30 | 882 | 882
2017-04-26 15:00 | 885 | 885
2017-04-26 15:30 | 871 | 871
2017-04-26 16:00 | 864 | 863
2017-04-26 16:30 | 894 | 894
2017-04-26 17:00 | 930 | 930
2017-04-26 17:30 | 959 | 959
2017-04-26 18:00 | 981 | 981
2017-04-26 18:30 | 954 | 954
2017-04-26 19:00 | 954 | 953
2017-04-26 19:30 | 929 | 928
2017-04-26 20:00 | 913 | 913
2017-04-26 20:30 | 892 | 891
2017-04-26 21:00 | 847 | 847
2017-04-26 21:30 | 801 | 800
2017-04-26 22:00 | 772 | 771
2017-04-26 22:30 | 760 | 756
2017-04-26 23:00 | 756 | 751
2017-04-26 23:30 | 712 | 704
2017-04-27 | 664 | 655
2017-04-27 00:30 | 612 | 602
2017-04-27 01:00 | 589 | 576
2017-04-27 01:30 | 569 | 553
2017-04-27 02:00 | 549 | 530
2017-04-27 02:30 | 545 | 526
2017-04-27 03:00 | 541 | 523
2017-04-27 03:30 | 542 | 523
2017-04-27 04:00 | 543 | 525
2017-04-27 04:30 | 553 | 537
2017-04-27 05:00 | 570 | 557
2017-04-27 05:30 | 610 | 603
2017-04-27 06:00 | 646 | 641
2017-04-27 06:30 | 710 | 708
2017-04-27 07:00 | 764 | 763
2017-04-27 07:30 | 803 | 802
2017-04-27 08:00 | 798 | 796
2017-04-27 08:30 | 778 | 776
2017-04-27 09:00 | 752 | 751
2017-04-27 09:30 | 729 | 728
2017-04-27 10:00 | 714 | 714
2017-04-27 10:30 | 702 | 702
2017-04-27 11:00 | 689 | 689
2017-04-27 11:30 | 680 | 680
2017-04-27 12:00 | 679 | 679
2017-04-27 12:30 | 678 | 678
2017-04-27 13:00 | 689 | 689
2017-04-27 13:30 | 698 | 697
2017-04-27 14:00 | 715 | 715
2017-04-27 14:30 | 739 | 739
2017-04-27 15:00 | 763 | 763
2017-04-27 15:30 | 784 | 784
2017-04-27 16:00 | 818 | 818
2017-04-27 16:30 | 850 | 850
2017-04-27 17:00 | 885 | 885
2017-04-27 17:30 | 908 | 908
2017-04-27 18:00 | 943 | 943
2017-04-27 18:30 | 941 | 941
2017-04-27 19:00 | 941 | 941
2017-04-27 19:30 | 921 | 921
2017-04-27 20:00 | 907 | 906
2017-04-27 20:30 | 891 | 891
2017-04-27 21:00 | 856 | 856
2017-04-27 21:30 | 811 | 810
2017-04-27 22:00 | 782 | 780
2017-04-27 22:30 | 766 | 761
2017-04-27 23:00 | 762 | 756
2017-04-27 23:30 | 720 | 711
2017-04-28 | 673 | 664
2017-04-28 00:30 | 614 | 601
2017-04-28 01:00 | 587 | 568
2017-04-28 01:30 | 569 | 549
2017-04-28 02:00 | 558 | 538
2017-04-28 02:30 | 552 | 532
2017-04-28 03:00 | 546 | 527
2017-04-28 03:30 | 547 | 527
2017-04-28 04:00 | 550 | 531
2017-04-28 04:30 | 560 | 543
2017-04-28 05:00 | 573 | 560
2017-04-28 05:30 | 609 | 600
2017-04-28 06:00 | 648 | 643
2017-04-28 06:30 | 708 | 706
2017-04-28 07:00 | 766 | 765
2017-04-28 07:30 | 814 | 812
2017-04-28 08:00 | 808 | 807
2017-04-28 08:30 | 787 | 786
2017-04-28 09:00 | 756 | 756
2017-04-28 09:30 | 730 | 730
2017-04-28 10:00 | 721 | 721
2017-04-28 10:30 | 707 | 707
2017-04-28 11:00 | 698 | 698
2017-04-28 11:30 | 691 | 691
2017-04-28 12:00 | 700 | 700
2017-04-28 12:30 | 714 | 714
2017-04-28 13:00 | 749 | 748
2017-04-28 13:30 | 767 | 767
2017-04-28 14:00 | 795 | 795
2017-04-28 14:30 | 790 | 789
2017-04-28 15:00 | 789 | 789
2017-04-28 15:30 | 809 | 809
2017-04-28 16:00 | 817 | 816
2017-04-28 16:30 | 849 | 849
2017-04-28 17:00 | 875 | 874
2017-04-28 17:30 | 888 | 887
2017-04-28 18:00 | 910 | 908
2017-04-28 18:30 | 902 | 898
2017-04-28 19:00 | 900 | 895
2017-04-28 19:30 | 877 | 871
2017-04-28 20:00 | 856 | 855
2017-04-28 20:30 | 849 | 849
2017-04-28 21:00 | 816 | 815
2017-04-28 21:30 | 784 | 782
2017-04-28 22:00 | 760 | 758
2017-04-28 22:30 | 753 | 750
2017-04-28 23:00 | 749 | 747
2017-04-28 23:30 | 706 | 703
2017-04-29 | 658 | 652
2017-04-29 00:30 | 612 | 601
2017-04-29 01:00 | 590 | 578
2017-04-29 01:30 | 573 | 558
2017-04-29 02:00 | 554 | 537
2017-04-29 02:30 | 546 | 528
2017-04-29 03:00 | 535 | 515
2017-04-29 03:30 | 531 | 510
2017-04-29 04:00 | 530 | 509
2017-04-29 04:30 | 535 | 514
2017-04-29 05:00 | 538 | 517
2017-04-29 05:30 | 552 | 534
2017-04-29 06:00 | 574 | 560
2017-04-29 06:30 | 598 | 584
2017-04-29 07:00 | 615 | 604
2017-04-29 07:30 | 644 | 637
2017-04-29 08:00 | 658 | 653
2017-04-29 08:30 | 664 | 662
2017-04-29 09:00 | 662 | 660
2017-04-29 09:30 | 657 | 656
2017-04-29 10:00 | 641 | 641
2017-04-29 10:30 | 626 | 626
2017-04-29 11:00 | 614 | 614
2017-04-29 11:30 | 599 | 598
2017-04-29 12:00 | 600 | 599
2017-04-29 12:30 | 594 | 594
2017-04-29 13:00 | 600 | 599
2017-04-29 13:30 | 603 | 602
2017-04-29 14:00 | 622 | 622
2017-04-29 14:30 | 641 | 640
2017-04-29 15:00 | 660 | 659
2017-04-29 15:30 | 684 | 684
2017-04-29 16:00 | 720 | 720
2017-04-29 16:30 | 746 | 746
2017-04-29 17:00 | 781 | 781
2017-04-29 17:30 | 801 | 801
2017-04-29 18:00 | 834 | 834
2017-04-29 18:30 | 839 | 837
2017-04-29 19:00 | 832 | 829
2017-04-29 19:30 | 818 | 814
2017-04-29 20:00 | 801 | 800
2017-04-29 20:30 | 789 | 789
2017-04-29 21:00 | 760 | 759
2017-04-29 21:30 | 736 | 734
2017-04-29 22:00 | 718 | 715
2017-04-29 22:30 | 719 | 715
2017-04-29 23:00 | 726 | 722
2017-04-29 23:30 | 687 | 680
2017-04-30 | 648 | 639
2017-04-30 00:30 | 605 | 592
2017-04-30 01:00 | 584 | 567
2017-04-30 01:30 | 564 | 544
2017-04-30 02:00 | 551 | 529
2017-04-30 02:30 | 537 | 514
2017-04-30 03:00 | 534 | 509
2017-04-30 03:30 | 530 | 504
2017-04-30 04:00 | 526 | 500
2017-04-30 04:30 | 531 | 504
2017-04-30 05:00 | 529 | 502
2017-04-30 05:30 | 540 | 514
2017-04-30 06:00 | 550 | 526
2017-04-30 06:30 | 568 | 545
2017-04-30 07:00 | 580 | 558
2017-04-30 07:30 | 593 | 575
2017-04-30 08:00 | 607 | 594
2017-04-30 08:30 | 617 | 607
2017-04-30 09:00 | 620 | 613
2017-04-30 09:30 | 621 | 615
2017-04-30 10:00 | 620 | 616
2017-04-30 10:30 | 621 | 618
2017-04-30 11:00 | 612 | 609
2017-04-30 11:30 | 607 | 598
2017-04-30 12:00 | 602 | 591
2017-04-30 12:30 | 600 | 591
2017-04-30 13:00 | 601 | 592
2017-04-30 13:30 | 604 | 595
2017-04-30 14:00 | 618 | 610
2017-04-30 14:30 | 630 | 622
2017-04-30 15:00 | 649 | 642
2017-04-30 15:30 | 676 | 670
2017-04-30 16:00 | 700 | 695
2017-04-30 16:30 | 731 | 728
2017-04-30 17:00 | 770 | 767
2017-04-30 17:30 | 800 | 798
2017-04-30 18:00 | 834 | 833
2017-04-30 18:30 | 837 | 835
2017-04-30 19:00 | 826 | 824
2017-04-30 19:30 | 813 | 810
2017-04-30 20:00 | 801 | 797
2017-04-30 20:30 | 782 | 778
2017-04-30 21:00 | 737 | 737
2017-04-30 21:30 | 723 | 722
2017-04-30 22:00 | 705 | 703
2017-04-30 22:30 | 708 | 705
2017-04-30 23:00 | 716 | 714
2017-04-30 23:30 | 673 | 668
2017-05-01 | 632 | 624
2017-05-01 00:30 | 592 | 580
2017-05-01 01:00 | 566 | 551
2017-05-01 01:30 | 549 | 532
2017-05-01 02:00 | 534 | 515
2017-05-01 02:30 | 529 | 509
2017-05-01 03:00 | 526 | 504
2017-05-01 03:30 | 524 | 501
2017-05-01 04:00 | 525 | 502
2017-05-01 04:30 | 527 | 503
2017-05-01 05:00 | 529 | 506
2017-05-01 05:30 | 538 | 518
2017-05-01 06:00 | 554 | 536
2017-05-01 06:30 | 574 | 557
2017-05-01 07:00 | 587 | 571
2017-05-01 07:30 | 605 | 592
2017-05-01 08:00 | 614 | 604
2017-05-01 08:30 | 622 | 615
2017-05-01 09:00 | 625 | 620
2017-05-01 09:30 | 628 | 626
2017-05-01 10:00 | 621 | 619
2017-05-01 10:30 | 613 | 612
2017-05-01 11:00 | 603 | 602
2017-05-01 11:30 | 605 | 604
2017-05-01 12:00 | 602 | 601
2017-05-01 12:30 | 605 | 604
2017-05-01 13:00 | 610 | 610
2017-05-01 13:30 | 616 | 615
2017-05-01 14:00 | 640 | 640
2017-05-01 14:30 | 644 | 643
2017-05-01 15:00 | 663 | 663
2017-05-01 15:30 | 687 | 687
2017-05-01 16:00 | 730 | 730
2017-05-01 16:30 | 759 | 759
2017-05-01 17:00 | 798 | 798
2017-05-01 17:30 | 843 | 842
2017-05-01 18:00 | 875 | 874
2017-05-01 18:30 | 871 | 868
2017-05-01 19:00 | 861 | 858
2017-05-01 19:30 | 836 | 835
2017-05-01 20:00 | 827 | 825
2017-05-01 20:30 | 810 | 807
2017-05-01 21:00 | 760 | 759
2017-05-01 21:30 | 730 | 729
2017-05-01 22:00 | 707 | 705
2017-05-01 22:30 | 703 | 700
2017-05-01 23:00 | 700 | 697
2017-05-01 23:30 | 669 | 664
2017-05-02 | 630 | 623
2017-05-02 00:30 | 594 | 583
2017-05-02 01:00 | 571 | 556
2017-05-02 01:30 | 556 | 540
2017-05-02 02:00 | 539 | 521
2017-05-02 02:30 | 531 | 513
2017-05-02 03:00 | 528 | 509
2017-05-02 03:30 | 525 | 506
2017-05-02 04:00 | 526 | 507
2017-05-02 04:30 | 538 | 522
2017-05-02 05:00 | 558 | 544
2017-05-02 05:30 | 597 | 589
2017-05-02 06:00 | 640 | 637
2017-05-02 06:30 | 718 | 718
2017-05-02 07:00 | 789 | 788
2017-05-02 07:30 | 832 | 831
2017-05-02 08:00 | 835 | 835
2017-05-02 08:30 | 813 | 813
2017-05-02 09:00 | 782 | 781
2017-05-02 09:30 | 758 | 754
2017-05-02 10:00 | 743 | 740
2017-05-02 10:30 | 738 | 737
2017-05-02 11:00 | 739 | 737
2017-05-02 11:30 | 737 | 736
2017-05-02 12:00 | 743 | 742
2017-05-02 12:30 | 759 | 759
2017-05-02 13:00 | 769 | 769
2017-05-02 13:30 | 789 | 789
2017-05-02 14:00 | 798 | 798
2017-05-02 14:30 | 810 | 810
2017-05-02 15:00 | 831 | 831
2017-05-02 15:30 | 856 | 856
2017-05-02 16:00 | 884 | 884
2017-05-02 16:30 | 910 | 910
2017-05-02 17:00 | 932 | 932
2017-05-02 17:30 | 957 | 957
2017-05-02 18:00 | 983 | 982
2017-05-02 18:30 | 966 | 962
2017-05-02 19:00 | 958 | 953
2017-05-02 19:30 | 930 | 929
2017-05-02 20:00 | 912 | 910
2017-05-02 20:30 | 889 | 888
2017-05-02 21:00 | 848 | 847
2017-05-02 21:30 | 810 | 810
2017-05-02 22:00 | 783 | 782
2017-05-02 22:30 | 771 | 768
2017-05-02 23:00 | 761 | 761
2017-05-02 23:30 | 717 | 716
2017-05-03 | 657 | 653
2017-05-03 00:30 | 613 | 607
2017-05-03 01:00 | 586 | 576
2017-05-03 01:30 | 568 | 557
2017-05-03 02:00 | 554 | 542
2017-05-03 02:30 | 549 | 535
2017-05-03 03:00 | 543 | 530
2017-05-03 03:30 | 546 | 532
2017-05-03 04:00 | 550 | 537
2017-05-03 04:30 | 559 | 547
2017-05-03 05:00 | 570 | 560
2017-05-03 05:30 | 609 | 604
2017-05-03 06:00 | 656 | 654
2017-05-03 06:30 | 729 | 728
2017-05-03 07:00 | 803 | 803
2017-05-03 07:30 | 847 | 847
2017-05-03 08:00 | 835 | 835
2017-05-03 08:30 | 824 | 823
2017-05-03 09:00 | 805 | 805
2017-05-03 09:30 | 791 | 790
2017-05-03 10:00 | 782 | 782
2017-05-03 10:30 | 770 | 770
2017-05-03 11:00 | 775 | 775
2017-05-03 11:30 | 777 | 777
2017-05-03 12:00 | 789 | 789
2017-05-03 12:30 | 795 | 793
2017-05-03 13:00 | 801 | 800
2017-05-03 13:30 | 825 | 824
2017-05-03 14:00 | 855 | 853
2017-05-03 14:30 | 871 | 869
2017-05-03 15:00 | 875 | 872
2017-05-03 15:30 | 865 | 862
2017-05-03 16:00 | 881 | 878
2017-05-03 16:30 | 903 | 900
2017-05-03 17:00 | 933 | 930
2017-05-03 17:30 | 950 | 947
2017-05-03 18:00 | 997 | 996
2017-05-03 18:30 | 990 | 988
2017-05-03 19:00 | 986 | 984
2017-05-03 19:30 | 951 | 947
2017-05-03 20:00 | 919 | 917
2017-05-03 20:30 | 903 | 902
2017-05-03 21:00 | 855 | 855
2017-05-03 21:30 | 813 | 813
2017-05-03 22:00 | 778 | 777
2017-05-03 22:30 | 760 | 759
2017-05-03 23:00 | 752 | 752
2017-05-03 23:30 | 703 | 701
2017-05-04 | 650 | 646
2017-05-04 00:30 | 604 | 597
2017-05-04 01:00 | 583 | 573
2017-05-04 01:30 | 565 | 552
2017-05-04 02:00 | 549 | 536
2017-05-04 02:30 | 551 | 538
2017-05-04 03:00 | 550 | 536
2017-05-04 03:30 | 549 | 535
2017-05-04 04:00 | 552 | 538
2017-05-04 04:30 | 561 | 549
2017-05-04 05:00 | 580 | 569
2017-05-04 05:30 | 615 | 609
2017-05-04 06:00 | 659 | 657
2017-05-04 06:30 | 727 | 726
2017-05-04 07:00 | 779 | 778
2017-05-04 07:30 | 827 | 827
2017-05-04 08:00 | 845 | 844
2017-05-04 08:30 | 833 | 833
2017-05-04 09:00 | 823 | 822
2017-05-04 09:30 | 815 | 815
2017-05-04 10:00 | 821 | 821
2017-05-04 10:30 | 813 | 813
2017-05-04 11:00 | 796 | 796
2017-05-04 11:30 | 801 | 801
2017-05-04 12:00 | 823 | 823
2017-05-04 12:30 | 820 | 820
2017-05-04 13:00 | 814 | 814
2017-05-04 13:30 | 807 | 807
2017-05-04 14:00 | 797 | 796
2017-05-04 14:30 | 820 | 820
2017-05-04 15:00 | 827 | 827
2017-05-04 15:30 | 828 | 828
2017-05-04 16:00 | 855 | 855
2017-05-04 16:30 | 876 | 875
2017-05-04 17:00 | 910 | 910
2017-05-04 17:30 | 940 | 940
2017-05-04 18:00 | 966 | 966
2017-05-04 18:30 | 959 | 957
2017-05-04 19:00 | 963 | 960
2017-05-04 19:30 | 943 | 937
2017-05-04 20:00 | 924 | 921
2017-05-04 20:30 | 909 | 908
2017-05-04 21:00 | 872 | 871
2017-05-04 21:30 | 819 | 818
2017-05-04 22:00 | 788 | 787
2017-05-04 22:30 | 779 | 779
2017-05-04 23:00 | 761 | 760
2017-05-04 23:30 | 717 | 714
2017-05-05 | 667 | 663
2017-05-05 00:30 | 618 | 610
2017-05-05 01:00 | 589 | 577
2017-05-05 01:30 | 565 | 551
2017-05-05 02:00 | 554 | 538
2017-05-05 02:30 | 549 | 532
2017-05-05 03:00 | 549 | 531
2017-05-05 03:30 | 547 | 529
2017-05-05 04:00 | 549 | 532
2017-05-05 04:30 | 560 | 545
2017-05-05 05:00 | 573 | 560
2017-05-05 05:30 | 608 | 601
2017-05-05 06:00 | 652 | 648
2017-05-05 06:30 | 721 | 719
2017-05-05 07:00 | 780 | 776
2017-05-05 07:30 | 817 | 816
2017-05-05 08:00 | 818 | 816
2017-05-05 08:30 | 803 | 802
2017-05-05 09:00 | 783 | 782
2017-05-05 09:30 | 765 | 765
2017-05-05 10:00 | 758 | 758
2017-05-05 10:30 | 752 | 752
2017-05-05 11:00 | 745 | 745
2017-05-05 11:30 | 738 | 738
2017-05-05 12:00 | 750 | 750
2017-05-05 12:30 | 745 | 745
2017-05-05 13:00 | 759 | 759
2017-05-05 13:30 | 745 | 745
2017-05-05 14:00 | 765 | 765
2017-05-05 14:30 | 787 | 787
2017-05-05 15:00 | 792 | 792
2017-05-05 15:30 | 798 | 798
2017-05-05 16:00 | 819 | 819
2017-05-05 16:30 | 846 | 846
2017-05-05 17:00 | 879 | 878
2017-05-05 17:30 | 901 | 901
2017-05-05 18:00 | 919 | 919
2017-05-05 18:30 | 900 | 899
2017-05-05 19:00 | 895 | 893
2017-05-05 19:30 | 874 | 871
2017-05-05 20:00 | 854 | 853
2017-05-05 20:30 | 847 | 846
2017-05-05 21:00 | 811 | 810
2017-05-05 21:30 | 779 | 776
2017-05-05 22:00 | 753 | 749
2017-05-05 22:30 | 747 | 745
2017-05-05 23:00 | 742 | 741
2017-05-05 23:30 | 703 | 701
2017-05-06 | 649 | 645
2017-05-06 00:30 | 604 | 597
2017-05-06 01:00 | 581 | 572
2017-05-06 01:30 | 564 | 553
2017-05-06 02:00 | 543 | 529
2017-05-06 02:30 | 530 | 513
2017-05-06 03:00 | 517 | 500
2017-05-06 03:30 | 516 | 498
2017-05-06 04:00 | 520 | 503
2017-05-06 04:30 | 530 | 513
2017-05-06 05:00 | 534 | 518
2017-05-06 05:30 | 549 | 536
2017-05-06 06:00 | 568 | 557
2017-05-06 06:30 | 588 | 578
2017-05-06 07:00 | 606 | 598
2017-05-06 07:30 | 633 | 629
2017-05-06 08:00 | 659 | 657
2017-05-06 08:30 | 678 | 677
2017-05-06 09:00 | 694 | 694
2017-05-06 09:30 | 695 | 695
2017-05-06 10:00 | 671 | 671
2017-05-06 10:30 | 658 | 658
2017-05-06 11:00 | 650 | 650
2017-05-06 11:30 | 636 | 636
2017-05-06 12:00 | 631 | 631
2017-05-06 12:30 | 608 | 608
2017-05-06 13:00 | 593 | 593
2017-05-06 13:30 | 600 | 600
2017-05-06 14:00 | 613 | 613
2017-05-06 14:30 | 629 | 629
2017-05-06 15:00 | 653 | 653
2017-05-06 15:30 | 671 | 671
2017-05-06 16:00 | 706 | 706
2017-05-06 16:30 | 749 | 748
2017-05-06 17:00 | 794 | 793
2017-05-06 17:30 | 827 | 827
2017-05-06 18:00 | 867 | 866
2017-05-06 18:30 | 847 | 845
2017-05-06 19:00 | 821 | 818
2017-05-06 19:30 | 807 | 803
2017-05-06 20:00 | 797 | 792
2017-05-06 20:30 | 784 | 780
2017-05-06 21:00 | 751 | 748
2017-05-06 21:30 | 728 | 727
2017-05-06 22:00 | 708 | 707
2017-05-06 22:30 | 713 | 711
2017-05-06 23:00 | 716 | 714
2017-05-06 23:30 | 677 | 673
2017-05-07 | 635 | 628
2017-05-07 00:30 | 593 | 583
2017-05-07 01:00 | 570 | 557
2017-05-07 01:30 | 547 | 533
2017-05-07 02:00 | 527 | 509
2017-05-07 02:30 | 517 | 498
2017-05-07 03:00 | 500 | 478
2017-05-07 03:30 | 493 | 472
2017-05-07 04:00 | 497 | 476
2017-05-07 04:30 | 494 | 473
2017-05-07 05:00 | 494 | 474
2017-05-07 05:30 | 507 | 489
2017-05-07 06:00 | 520 | 504
2017-05-07 06:30 | 537 | 522
2017-05-07 07:00 | 561 | 546
2017-05-07 07:30 | 588 | 577
2017-05-07 08:00 | 603 | 596
2017-05-07 08:30 | 618 | 614
2017-05-07 09:00 | 635 | 633
2017-05-07 09:30 | 637 | 636
2017-05-07 10:00 | 627 | 626
2017-05-07 10:30 | 616 | 616
2017-05-07 11:00 | 603 | 602
2017-05-07 11:30 | 598 | 598
2017-05-07 12:00 | 586 | 586
2017-05-07 12:30 | 577 | 577
2017-05-07 13:00 | 578 | 578
2017-05-07 13:30 | 583 | 583
2017-05-07 14:00 | 603 | 603
2017-05-07 14:30 | 627 | 627
2017-05-07 15:00 | 650 | 650
2017-05-07 15:30 | 669 | 669
2017-05-07 16:00 | 712 | 712
2017-05-07 16:30 | 764 | 764
2017-05-07 17:00 | 810 | 809
2017-05-07 17:30 | 823 | 822
2017-05-07 18:00 | 859 | 857
2017-05-07 18:30 | 862 | 858
2017-05-07 19:00 | 852 | 846
2017-05-07 19:30 | 833 | 827
2017-05-07 20:00 | 810 | 808
2017-05-07 20:30 | 799 | 799
2017-05-07 21:00 | 761 | 761
2017-05-07 21:30 | 733 | 732
2017-05-07 22:00 | 710 | 710
2017-05-07 22:30 | 704 | 703
2017-05-07 23:00 | 702 | 700
2017-05-07 23:30 | 666 | 662
2017-05-08 | 625 | 619
2017-05-08 00:30 | 578 | 567
2017-05-08 01:00 | 557 | 544
2017-05-08 01:30 | 540 | 526
2017-05-08 02:00 | 523 | 506
2017-05-08 02:30 | 514 | 496
2017-05-08 03:00 | 507 | 489
2017-05-08 03:30 | 514 | 496
2017-05-08 04:00 | 521 | 504
2017-05-08 04:30 | 525 | 510
2017-05-08 05:00 | 548 | 536
2017-05-08 05:30 | 586 | 580
2017-05-08 06:00 | 633 | 631
2017-05-08 06:30 | 707 | 706
2017-05-08 07:00 | 778 | 777
2017-05-08 07:30 | 836 | 835
2017-05-08 08:00 | 838 | 837
2017-05-08 08:30 | 841 | 840
2017-05-08 09:00 | 959 | 959
2017-05-08 09:30 | 969 | 969
2017-05-08 10:00 | 853 | 853
2017-05-08 10:30 | 877 | 877
2017-05-08 11:00 | 904 | 903
2017-05-08 11:30 | 759 | 759
2017-05-08 12:00 | 836 | 836
2017-05-08 12:30 | 838 | 838
2017-05-08 13:00 | 851 | 851
2017-05-08 13:30 | 838 | 838
2017-05-08 14:00 | 833 | 832
2017-05-08 14:30 | 840 | 840
2017-05-08 15:00 | 852 | 852
2017-05-08 15:30 | 858 | 857
2017-05-08 16:00 | 874 | 874
2017-05-08 16:30 | 892 | 892
2017-05-08 17:00 | 927 | 927
2017-05-08 17:30 | 963 | 962
2017-05-08 18:00 | 978 | 977
2017-05-08 18:30 | 961 | 957
2017-05-08 19:00 | 955 | 950
2017-05-08 19:30 | 924 | 918
2017-05-08 20:00 | 904 | 902
2017-05-08 20:30 | 886 | 885
2017-05-08 21:00 | 845 | 845
2017-05-08 21:30 | 812 | 811
2017-05-08 22:00 | 765 | 763
2017-05-08 22:30 | 747 | 746
2017-05-08 23:00 | 743 | 742
2017-05-08 23:30 | 704 | 702
2017-05-09 | 660 | 655
2017-05-09 00:30 | 609 | 601
2017-05-09 01:00 | 582 | 572
2017-05-09 01:30 | 561 | 548
2017-05-09 02:00 | 542 | 526
2017-05-09 02:30 | 537 | 521
2017-05-09 03:00 | 533 | 516
2017-05-09 03:30 | 530 | 513
2017-05-09 04:00 | 537 | 521
2017-05-09 04:30 | 548 | 533
2017-05-09 05:00 | 561 | 549
2017-05-09 05:30 | 597 | 591
2017-05-09 06:00 | 643 | 641
2017-05-09 06:30 | 719 | 718
2017-05-09 07:00 | 784 | 782
2017-05-09 07:30 | 838 | 836
2017-05-09 08:00 | 855 | 850
2017-05-09 08:30 | 849 | 841
2017-05-09 09:00 | 832 | 825
2017-05-09 09:30 | 804 | 803
2017-05-09 10:00 | 798 | 797
2017-05-09 10:30 | 797 | 796
2017-05-09 11:00 | 786 | 786
2017-05-09 11:30 | 769 | 768
2017-05-09 12:00 | 766 | 765
2017-05-09 12:30 | 765 | 764
2017-05-09 13:00 | 770 | 769
2017-05-09 13:30 | 763 | 762
2017-05-09 14:00 | 761 | 760
2017-05-09 14:30 | 777 | 776
2017-05-09 15:00 | 788 | 787
2017-05-09 15:30 | 801 | 800
2017-05-09 16:00 | 824 | 823
2017-05-09 16:30 | 855 | 854
2017-05-09 17:00 | 893 | 892
2017-05-09 17:30 | 922 | 922
2017-05-09 18:00 | 943 | 942
2017-05-09 18:30 | 924 | 921
2017-05-09 19:00 | 921 | 920
2017-05-09 19:30 | 899 | 897
2017-05-09 20:00 | 882 | 881
2017-05-09 20:30 | 868 | 868
2017-05-09 21:00 | 833 | 833
2017-05-09 21:30 | 790 | 790
2017-05-09 22:00 | 769 | 768
2017-05-09 22:30 | 754 | 752
2017-05-09 23:00 | 744 | 743
2017-05-09 23:30 | 706 | 703
2017-05-10 | 661 | 655
2017-05-10 00:30 | 611 | 603
2017-05-10 01:00 | 583 | 573
2017-05-10 01:30 | 564 | 553
2017-05-10 02:00 | 550 | 537
2017-05-10 02:30 | 540 | 526
2017-05-10 03:00 | 532 | 518
2017-05-10 03:30 | 528 | 514
2017-05-10 04:00 | 529 | 515
2017-05-10 04:30 | 546 | 534
2017-05-10 05:00 | 565 | 555
2017-05-10 05:30 | 602 | 597
2017-05-10 06:00 | 641 | 639
2017-05-10 06:30 | 720 | 719
2017-05-10 07:00 | 786 | 785
2017-05-10 07:30 | 848 | 848
2017-05-10 08:00 | 881 | 880
2017-05-10 08:30 | 885 | 881
2017-05-10 09:00 | 871 | 867
2017-05-10 09:30 | 878 | 877
2017-05-10 10:00 | 883 | 883
2017-05-10 10:30 | 886 | 886
2017-05-10 11:00 | 890 | 890
2017-05-10 11:30 | 883 | 882
2017-05-10 12:00 | 874 | 874
2017-05-10 12:30 | 861 | 860
2017-05-10 13:00 | 850 | 849
2017-05-10 13:30 | 848 | 847
2017-05-10 14:00 | 850 | 849
2017-05-10 14:30 | 854 | 853
2017-05-10 15:00 | 859 | 857
2017-05-10 15:30 | 862 | 860
2017-05-10 16:00 | 880 | 878
2017-05-10 16:30 | 903 | 902
2017-05-10 17:00 | 930 | 930
2017-05-10 17:30 | 970 | 969
2017-05-10 18:00 | 975 | 972
2017-05-10 18:30 | 961 | 957
2017-05-10 19:00 | 952 | 948
2017-05-10 19:30 | 930 | 924
2017-05-10 20:00 | 906 | 905
2017-05-10 20:30 | 892 | 891
2017-05-10 21:00 | 853 | 852
2017-05-10 21:30 | 817 | 814
2017-05-10 22:00 | 785 | 780
2017-05-10 22:30 | 762 | 761
2017-05-10 23:00 | 757 | 755
2017-05-10 23:30 | 715 | 711
2017-05-11 | 663 | 659
2017-05-11 00:30 | 617 | 610
2017-05-11 01:00 | 589 | 578
2017-05-11 01:30 | 565 | 553
2017-05-11 02:00 | 551 | 537
2017-05-11 02:30 | 538 | 523
2017-05-11 03:00 | 527 | 511
2017-05-11 03:30 | 524 | 508
2017-05-11 04:00 | 522 | 506
2017-05-11 04:30 | 541 | 527
2017-05-11 05:00 | 564 | 553
2017-05-11 05:30 | 606 | 600
2017-05-11 06:00 | 653 | 651
2017-05-11 06:30 | 728 | 727
2017-05-11 07:00 | 804 | 796
2017-05-11 07:30 | 837 | 834
2017-05-11 08:00 | 829 | 826
2017-05-11 08:30 | 807 | 804
2017-05-11 09:00 | 773 | 769
2017-05-11 09:30 | 754 | 751
2017-05-11 10:00 | 749 | 747
2017-05-11 10:30 | 778 | 777
2017-05-11 11:00 | 755 | 754
2017-05-11 11:30 | 729 | 727
2017-05-11 12:00 | 697 | 694
2017-05-11 12:30 | 696 | 694
2017-05-11 13:00 | 713 | 711
2017-05-11 13:30 | 720 | 719
2017-05-11 14:00 | 733 | 732
2017-05-11 14:30 | 743 | 742
2017-05-11 15:00 | 760 | 760
2017-05-11 15:30 | 788 | 788
2017-05-11 16:00 | 821 | 820
2017-05-11 16:30 | 848 | 848
2017-05-11 17:00 | 880 | 880
2017-05-11 17:30 | 914 | 913
2017-05-11 18:00 | 943 | 941
2017-05-11 18:30 | 936 | 933
2017-05-11 19:00 | 942 | 938
2017-05-11 19:30 | 925 | 920
2017-05-11 20:00 | 910 | 908
2017-05-11 20:30 | 898 | 897
2017-05-11 21:00 | 860 | 860
2017-05-11 21:30 | 824 | 824
2017-05-11 22:00 | 783 | 782
2017-05-11 22:30 | 769 | 768
2017-05-11 23:00 | 765 | 763
2017-05-11 23:30 | 720 | 718
2017-05-12 | 667 | 663
2017-05-12 00:30 | 617 | 609
2017-05-12 01:00 | 592 | 582
2017-05-12 01:30 | 570 | 560
2017-05-12 02:00 | 551 | 539
2017-05-12 02:30 | 537 | 524
2017-05-12 03:00 | 528 | 513
2017-05-12 03:30 | 519 | 504
2017-05-12 04:00 | 515 | 501
2017-05-12 04:30 | 525 | 512
2017-05-12 05:00 | 555 | 546
2017-05-12 05:30 | 602 | 597
2017-05-12 06:00 | 652 | 650
2017-05-12 06:30 | 725 | 721
2017-05-12 07:00 | 790 | 786
2017-05-12 07:30 | 844 | 838
2017-05-12 08:00 | 858 | 849
2017-05-12 08:30 | 852 | 844
2017-05-12 09:00 | 838 | 831
2017-05-12 09:30 | 815 | 807
2017-05-12 10:00 | 795 | 787
2017-05-12 10:30 | 770 | 766
2017-05-12 11:00 | 773 | 771
2017-05-12 11:30 | 766 | 765
2017-05-12 12:00 | 776 | 774
2017-05-12 12:30 | 788 | 786
2017-05-12 13:00 | 797 | 794
2017-05-12 13:30 | 791 | 789
2017-05-12 14:00 | 804 | 802
2017-05-12 14:30 | 800 | 798
2017-05-12 15:00 | 813 | 810
2017-05-12 15:30 | 813 | 810
2017-05-12 16:00 | 843 | 841
2017-05-12 16:30 | 870 | 868
2017-05-12 17:00 | 898 | 896
2017-05-12 17:30 | 923 | 921
2017-05-12 18:00 | 937 | 934
2017-05-12 18:30 | 918 | 909
2017-05-12 19:00 | 915 | 905
2017-05-12 19:30 | 889 | 879
2017-05-12 20:00 | 866 | 864
2017-05-12 20:30 | 860 | 857
2017-05-12 21:00 | 822 | 816
2017-05-12 21:30 | 787 | 785
2017-05-12 22:00 | 761 | 761
2017-05-12 22:30 | 758 | 757
2017-05-12 23:00 | 758 | 756
2017-05-12 23:30 | 714 | 711
2017-05-13 | 667 | 662
2017-05-13 00:30 | 613 | 605
2017-05-13 01:00 | 589 | 577
2017-05-13 01:30 | 571 | 556
2017-05-13 02:00 | 553 | 537
2017-05-13 02:30 | 546 | 528
2017-05-13 03:00 | 542 | 524
2017-05-13 03:30 | 535 | 517
2017-05-13 04:00 | 533 | 515
2017-05-13 04:30 | 531 | 514
2017-05-13 05:00 | 543 | 526
2017-05-13 05:30 | 555 | 540
2017-05-13 06:00 | 571 | 559
2017-05-13 06:30 | 595 | 587
2017-05-13 07:00 | 621 | 613
2017-05-13 07:30 | 661 | 657
2017-05-13 08:00 | 688 | 687
2017-05-13 08:30 | 700 | 699
2017-05-13 09:00 | 700 | 699
2017-05-13 09:30 | 695 | 695
2017-05-13 10:00 | 687 | 687
2017-05-13 10:30 | 674 | 674
2017-05-13 11:00 | 686 | 686
2017-05-13 11:30 | 711 | 711
2017-05-13 12:00 | 709 | 709
2017-05-13 12:30 | 701 | 701
2017-05-13 13:00 | 694 | 694
2017-05-13 13:30 | 713 | 713
2017-05-13 14:00 | 720 | 720
2017-05-13 14:30 | 730 | 730
2017-05-13 15:00 | 739 | 739
2017-05-13 15:30 | 741 | 741
2017-05-13 16:00 | 749 | 749
2017-05-13 16:30 | 767 | 766
2017-05-13 17:00 | 791 | 791
2017-05-13 17:30 | 816 | 816
2017-05-13 18:00 | 839 | 838
2017-05-13 18:30 | 835 | 834
2017-05-13 19:00 | 827 | 826
2017-05-13 19:30 | 811 | 809
2017-05-13 20:00 | 795 | 795
2017-05-13 20:30 | 779 | 779
2017-05-13 21:00 | 748 | 748
2017-05-13 21:30 | 726 | 725
2017-05-13 22:00 | 710 | 709
2017-05-13 22:30 | 709 | 708
2017-05-13 23:00 | 719 | 718
2017-05-13 23:30 | 685 | 683
2017-05-14 | 642 | 637
2017-05-14 00:30 | 593 | 585
2017-05-14 01:00 | 561 | 550
2017-05-14 01:30 | 539 | 527
2017-05-14 02:00 | 516 | 502
2017-05-14 02:30 | 502 | 486
2017-05-14 03:00 | 492 | 474
2017-05-14 03:30 | 489 | 471
2017-05-14 04:00 | 480 | 462
2017-05-14 04:30 | 481 | 463
2017-05-14 05:00 | 485 | 467
2017-05-14 05:30 | 499 | 483
2017-05-14 06:00 | 514 | 500
2017-05-14 06:30 | 537 | 525
2017-05-14 07:00 | 566 | 555
2017-05-14 07:30 | 611 | 604
2017-05-14 08:00 | 646 | 642
2017-05-14 08:30 | 684 | 682
2017-05-14 09:00 | 705 | 704
2017-05-14 09:30 | 704 | 703
2017-05-14 10:00 | 715 | 713
2017-05-14 10:30 | 712 | 710
2017-05-14 11:00 | 702 | 699
2017-05-14 11:30 | 711 | 709
2017-05-14 12:00 | 708 | 706
2017-05-14 12:30 | 691 | 687
2017-05-14 13:00 | 686 | 682
2017-05-14 13:30 | 695 | 692
2017-05-14 14:00 | 702 | 699
2017-05-14 14:30 | 698 | 695
2017-05-14 15:00 | 704 | 701
2017-05-14 15:30 | 720 | 717
2017-05-14 16:00 | 738 | 736
2017-05-14 16:30 | 767 | 766
2017-05-14 17:00 | 800 | 799
2017-05-14 17:30 | 831 | 831
2017-05-14 18:00 | 844 | 844
2017-05-14 18:30 | 842 | 842
2017-05-14 19:00 | 836 | 835
2017-05-14 19:30 | 819 | 818
2017-05-14 20:00 | 799 | 797
2017-05-14 20:30 | 786 | 786
2017-05-14 21:00 | 759 | 759
2017-05-14 21:30 | 735 | 735
2017-05-14 22:00 | 709 | 708
2017-05-14 22:30 | 702 | 700
2017-05-14 23:00 | 705 | 704
2017-05-14 23:30 | 671 | 668
2017-05-15 | 632 | 626
2017-05-15 00:30 | 591 | 582
2017-05-15 01:00 | 564 | 551
2017-05-15 01:30 | 544 | 529
2017-05-15 02:00 | 519 | 503
2017-05-15 02:30 | 513 | 495
2017-05-15 03:00 | 506 | 488
2017-05-15 03:30 | 505 | 486
2017-05-15 04:00 | 501 | 483
2017-05-15 04:30 | 514 | 498
2017-05-15 05:00 | 537 | 524
2017-05-15 05:30 | 583 | 577
2017-05-15 06:00 | 634 | 631
2017-05-15 06:30 | 708 | 707
2017-05-15 07:00 | 766 | 764
2017-05-15 07:30 | 811 | 809
2017-05-15 08:00 | 817 | 816
2017-05-15 08:30 | 799 | 799
2017-05-15 09:00 | 773 | 773
2017-05-15 09:30 | 755 | 754
2017-05-15 10:00 | 743 | 742
2017-05-15 10:30 | 730 | 729
2017-05-15 11:00 | 717 | 716
2017-05-15 11:30 | 714 | 714
2017-05-15 12:00 | 712 | 712
2017-05-15 12:30 | 711 | 711
2017-05-15 13:00 | 718 | 718
2017-05-15 13:30 | 735 | 735
2017-05-15 14:00 | 753 | 753
2017-05-15 14:30 | 768 | 768
2017-05-15 15:00 | 786 | 786
2017-05-15 15:30 | 803 | 803
2017-05-15 16:00 | 841 | 841
2017-05-15 16:30 | 864 | 863
2017-05-15 17:00 | 904 | 903
2017-05-15 17:30 | 940 | 940
2017-05-15 18:00 | 958 | 958
2017-05-15 18:30 | 938 | 938
2017-05-15 19:00 | 932 | 931
2017-05-15 19:30 | 911 | 908
2017-05-15 20:00 | 889 | 887
2017-05-15 20:30 | 875 | 875
2017-05-15 21:00 | 829 | 828
2017-05-15 21:30 | 783 | 782
2017-05-15 22:00 | 757 | 756
2017-05-15 22:30 | 743 | 742
2017-05-15 23:00 | 736 | 735
2017-05-15 23:30 | 689 | 687
2017-05-16 | 644 | 640
2017-05-16 00:30 | 599 | 590
2017-05-16 01:00 | 569 | 558
2017-05-16 01:30 | 548 | 535
2017-05-16 02:00 | 537 | 523
2017-05-16 02:30 | 527 | 513
2017-05-16 03:00 | 524 | 508
2017-05-16 03:30 | 527 | 511
2017-05-16 04:00 | 531 | 516
2017-05-16 04:30 | 540 | 527
2017-05-16 05:00 | 554 | 544
2017-05-16 05:30 | 600 | 595
2017-05-16 06:00 | 641 | 638
2017-05-16 06:30 | 710 | 709
2017-05-16 07:00 | 774 | 773
2017-05-16 07:30 | 808 | 808
2017-05-16 08:00 | 805 | 805
2017-05-16 08:30 | 785 | 785
2017-05-16 09:00 | 750 | 750
2017-05-16 09:30 | 735 | 735
2017-05-16 10:00 | 723 | 723
2017-05-16 10:30 | 706 | 706
2017-05-16 11:00 | 700 | 700
2017-05-16 11:30 | 692 | 692
2017-05-16 12:00 | 690 | 690
2017-05-16 12:30 | 691 | 690
2017-05-16 13:00 | 700 | 700
2017-05-16 13:30 | 712 | 711
2017-05-16 14:00 | 722 | 722
2017-05-16 14:30 | 735 | 734
2017-05-16 15:00 | 751 | 751
2017-05-16 15:30 | 780 | 780
2017-05-16 16:00 | 809 | 809
2017-05-16 16:30 | 852 | 852
2017-05-16 17:00 | 890 | 890
2017-05-16 17:30 | 922 | 922
2017-05-16 18:00 | 949 | 949
2017-05-16 18:30 | 932 | 930
2017-05-16 19:00 | 932 | 930
2017-05-16 19:30 | 912 | 909
2017-05-16 20:00 | 900 | 899
2017-05-16 20:30 | 881 | 881
2017-05-16 21:00 | 832 | 831
2017-05-16 21:30 | 791 | 790
2017-05-16 22:00 | 754 | 754
2017-05-16 22:30 | 739 | 739
2017-05-16 23:00 | 734 | 734
2017-05-16 23:30 | 689 | 687
2017-05-17 | 646 | 641
2017-05-17 00:30 | 597 | 588
2017-05-17 01:00 | 575 | 563
2017-05-17 01:30 | 557 | 544
2017-05-17 02:00 | 540 | 525
2017-05-17 02:30 | 533 | 516
2017-05-17 03:00 | 534 | 516
2017-05-17 03:30 | 528 | 511
2017-05-17 04:00 | 525 | 509
2017-05-17 04:30 | 533 | 519
2017-05-17 05:00 | 561 | 551
2017-05-17 05:30 | 597 | 592
2017-05-17 06:00 | 647 | 645
2017-05-17 06:30 | 722 | 717
2017-05-17 07:00 | 777 | 775
2017-05-17 07:30 | 821 | 820
2017-05-17 08:00 | 811 | 810
2017-05-17 08:30 | 786 | 785
2017-05-17 09:00 | 763 | 762
2017-05-17 09:30 | 738 | 737
2017-05-17 10:00 | 714 | 713
2017-05-17 10:30 | 711 | 710
2017-05-17 11:00 | 710 | 710
2017-05-17 11:30 | 721 | 720
2017-05-17 12:00 | 728 | 727
2017-05-17 12:30 | 720 | 720
2017-05-17 13:00 | 729 | 729
2017-05-17 13:30 | 725 | 724
2017-05-17 14:00 | 738 | 738
2017-05-17 14:30 | 749 | 749
2017-05-17 15:00 | 756 | 756
2017-05-17 15:30 | 770 | 770
2017-05-17 16:00 | 800 | 800
2017-05-17 16:30 | 830 | 830
2017-05-17 17:00 | 869 | 868
2017-05-17 17:30 | 908 | 908
2017-05-17 18:00 | 934 | 932
2017-05-17 18:30 | 914 | 910
2017-05-17 19:00 | 906 | 904
2017-05-17 19:30 | 881 | 880
2017-05-17 20:00 | 873 | 872
2017-05-17 20:30 | 859 | 859
2017-05-17 21:00 | 818 | 818
2017-05-17 21:30 | 780 | 779
2017-05-17 22:00 | 746 | 745
2017-05-17 22:30 | 726 | 726
2017-05-17 23:00 | 716 | 715
2017-05-17 23:30 | 669 | 667
2017-05-18 | 629 | 623
2017-05-18 00:30 | 590 | 580
2017-05-18 01:00 | 562 | 550
2017-05-18 01:30 | 550 | 536
2017-05-18 02:00 | 539 | 523
2017-05-18 02:30 | 527 | 511
2017-05-18 03:00 | 517 | 499
2017-05-18 03:30 | 520 | 502
2017-05-18 04:00 | 517 | 500
2017-05-18 04:30 | 527 | 512
2017-05-18 05:00 | 544 | 532
2017-05-18 05:30 | 587 | 581
2017-05-18 06:00 | 630 | 627
2017-05-18 06:30 | 699 | 697
2017-05-18 07:00 | 782 | 781
2017-05-18 07:30 | 860 | 859
2017-05-18 08:00 | 867 | 865
2017-05-18 08:30 | 851 | 850
2017-05-18 09:00 | 830 | 828
2017-05-18 09:30 | 815 | 813
2017-05-18 10:00 | 812 | 810
2017-05-18 10:30 | 814 | 813
2017-05-18 11:00 | 814 | 814
2017-05-18 11:30 | 801 | 800
2017-05-18 12:00 | 789 | 788
2017-05-18 12:30 | 774 | 773
2017-05-18 13:00 | 759 | 759
2017-05-18 13:30 | 778 | 778
2017-05-18 14:00 | 800 | 800
2017-05-18 14:30 | 802 | 802
2017-05-18 15:00 | 813 | 812
2017-05-18 15:30 | 834 | 834
2017-05-18 16:00 | 859 | 859
2017-05-18 16:30 | 878 | 878
2017-05-18 17:00 | 917 | 917
2017-05-18 17:30 | 947 | 946
2017-05-18 18:00 | 937 | 937
2017-05-18 18:30 | 921 | 921
2017-05-18 19:00 | 917 | 917
2017-05-18 19:30 | 899 | 898
2017-05-18 20:00 | 891 | 891
2017-05-18 20:30 | 879 | 878
2017-05-18 21:00 | 839 | 837
2017-05-18 21:30 | 799 | 794
2017-05-18 22:00 | 757 | 752
2017-05-18 22:30 | 737 | 735
2017-05-18 23:00 | 731 | 728
2017-05-18 23:30 | 690 | 684
2017-05-19 | 644 | 638
2017-05-19 00:30 | 601 | 593
2017-05-19 01:00 | 571 | 561
2017-05-19 01:30 | 553 | 540
2017-05-19 02:00 | 539 | 523
2017-05-19 02:30 | 533 | 515
2017-05-19 03:00 | 533 | 515
2017-05-19 03:30 | 529 | 512
2017-05-19 04:00 | 523 | 507
2017-05-19 04:30 | 541 | 527
2017-05-19 05:00 | 554 | 542
2017-05-19 05:30 | 586 | 579
2017-05-19 06:00 | 629 | 626
2017-05-19 06:30 | 701 | 699
2017-05-19 07:00 | 780 | 775
2017-05-19 07:30 | 863 | 858
2017-05-19 08:00 | 873 | 870
2017-05-19 08:30 | 884 | 882
2017-05-19 09:00 | 885 | 883
2017-05-19 09:30 | 870 | 868
2017-05-19 10:00 | 869 | 866
2017-05-19 10:30 | 874 | 872
2017-05-19 11:00 | 868 | 866
2017-05-19 11:30 | 861 | 859
2017-05-19 12:00 | 861 | 859
2017-05-19 12:30 | 863 | 861
2017-05-19 13:00 | 866 | 863
2017-05-19 13:30 | 855 | 852
2017-05-19 14:00 | 876 | 872
2017-05-19 14:30 | 871 | 867
2017-05-19 15:00 | 868 | 864
2017-05-19 15:30 | 873 | 868
2017-05-19 16:00 | 898 | 894
2017-05-19 16:30 | 927 | 923
2017-05-19 17:00 | 969 | 968
2017-05-19 17:30 | 961 | 958
2017-05-19 18:00 | 951 | 947
2017-05-19 18:30 | 930 | 924
2017-05-19 19:00 | 916 | 914
2017-05-19 19:30 | 883 | 880
2017-05-19 20:00 | 862 | 861
2017-05-19 20:30 | 844 | 843
2017-05-19 21:00 | 804 | 804
2017-05-19 21:30 | 773 | 772
2017-05-19 22:00 | 755 | 753
2017-05-19 22:30 | 747 | 744
2017-05-19 23:00 | 745 | 741
2017-05-19 23:30 | 708 | 705
2017-05-20 | 664 | 659
2017-05-20 00:30 | 609 | 600
2017-05-20 01:00 | 583 | 571
2017-05-20 01:30 | 558 | 542
2017-05-20 02:00 | 546 | 529
2017-05-20 02:30 | 537 | 518
2017-05-20 03:00 | 531 | 509
2017-05-20 03:30 | 532 | 509
2017-05-20 04:00 | 531 | 507
2017-05-20 04:30 | 534 | 512
2017-05-20 05:00 | 538 | 518
2017-05-20 05:30 | 553 | 535
2017-05-20 06:00 | 565 | 549
2017-05-20 06:30 | 590 | 580
2017-05-20 07:00 | 616 | 606
2017-05-20 07:30 | 651 | 646
2017-05-20 08:00 | 661 | 658
2017-05-20 08:30 | 680 | 679
2017-05-20 09:00 | 690 | 690
2017-05-20 09:30 | 692 | 692
2017-05-20 10:00 | 685 | 685
2017-05-20 10:30 | 684 | 684
2017-05-20 11:00 | 688 | 688
2017-05-20 11:30 | 679 | 679
2017-05-20 12:00 | 692 | 692
2017-05-20 12:30 | 696 | 696
2017-05-20 13:00 | 696 | 696
2017-05-20 13:30 | 684 | 684
2017-05-20 14:00 | 682 | 682
2017-05-20 14:30 | 695 | 695
2017-05-20 15:00 | 704 | 704
2017-05-20 15:30 | 719 | 719
2017-05-20 16:00 | 736 | 736
2017-05-20 16:30 | 757 | 757
2017-05-20 17:00 | 786 | 786
2017-05-20 17:30 | 819 | 819
2017-05-20 18:00 | 835 | 835
2017-05-20 18:30 | 827 | 826
2017-05-20 19:00 | 819 | 817
2017-05-20 19:30 | 805 | 803
2017-05-20 20:00 | 788 | 788
2017-05-20 20:30 | 780 | 780
2017-05-20 21:00 | 757 | 757
2017-05-20 21:30 | 734 | 734
2017-05-20 22:00 | 719 | 717
2017-05-20 22:30 | 719 | 716
2017-05-20 23:00 | 728 | 725
2017-05-20 23:30 | 694 | 690
2017-05-21 | 654 | 647
2017-05-21 00:30 | 608 | 595
2017-05-21 01:00 | 581 | 564
2017-05-21 01:30 | 559 | 537
2017-05-21 02:00 | 546 | 524
2017-05-21 02:30 | 541 | 519
2017-05-21 03:00 | 531 | 506
2017-05-21 03:30 | 529 | 504
2017-05-21 04:00 | 529 | 503
2017-05-21 04:30 | 527 | 504
2017-05-21 05:00 | 527 | 506
2017-05-21 05:30 | 534 | 514
2017-05-21 06:00 | 542 | 524
2017-05-21 06:30 | 555 | 540
2017-05-21 07:00 | 574 | 558
2017-05-21 07:30 | 598 | 587
2017-05-21 08:00 | 617 | 610
2017-05-21 08:30 | 634 | 630
2017-05-21 09:00 | 647 | 644
2017-05-21 09:30 | 644 | 643
2017-05-21 10:00 | 649 | 649
2017-05-21 10:30 | 650 | 650
2017-05-21 11:00 | 634 | 634
2017-05-21 11:30 | 624 | 623
2017-05-21 12:00 | 624 | 623
2017-05-21 12:30 | 617 | 616
2017-05-21 13:00 | 613 | 612
2017-05-21 13:30 | 625 | 624
2017-05-21 14:00 | 637 | 636
2017-05-21 14:30 | 650 | 650
2017-05-21 15:00 | 675 | 675
2017-05-21 15:30 | 698 | 697
2017-05-21 16:00 | 725 | 725
2017-05-21 16:30 | 754 | 754
2017-05-21 17:00 | 794 | 794
2017-05-21 17:30 | 841 | 841
2017-05-21 18:00 | 871 | 871
2017-05-21 18:30 | 855 | 854
2017-05-21 19:00 | 849 | 847
2017-05-21 19:30 | 824 | 823
2017-05-21 20:00 | 817 | 817
2017-05-21 20:30 | 805 | 805
2017-05-21 21:00 | 776 | 776
2017-05-21 21:30 | 748 | 747
2017-05-21 22:00 | 721 | 719
2017-05-21 22:30 | 714 | 710
2017-05-21 23:00 | 719 | 714
2017-05-21 23:30 | 677 | 672
2017-05-22 | 638 | 629
2017-05-22 00:30 | 596 | 583
2017-05-22 01:00 | 575 | 558
2017-05-22 01:30 | 555 | 537
2017-05-22 02:00 | 543 | 523
2017-05-22 02:30 | 535 | 515
2017-05-22 03:00 | 532 | 511
2017-05-22 03:30 | 531 | 510
2017-05-22 04:00 | 539 | 518
2017-05-22 04:30 | 546 | 526
2017-05-22 05:00 | 567 | 551
2017-05-22 05:30 | 605 | 596
2017-05-22 06:00 | 638 | 634
2017-05-22 06:30 | 706 | 705
2017-05-22 07:00 | 777 | 776
2017-05-22 07:30 | 823 | 821
2017-05-22 08:00 | 830 | 829
2017-05-22 08:30 | 814 | 813
2017-05-22 09:00 | 795 | 795
2017-05-22 09:30 | 782 | 782
2017-05-22 10:00 | 772 | 772
2017-05-22 10:30 | 773 | 772
2017-05-22 11:00 | 774 | 773
2017-05-22 11:30 | 775 | 774
2017-05-22 12:00 | 777 | 776
2017-05-22 12:30 | 785 | 785
2017-05-22 13:00 | 787 | 787
2017-05-22 13:30 | 793 | 793
2017-05-22 14:00 | 812 | 811
2017-05-22 14:30 | 809 | 808
2017-05-22 15:00 | 826 | 826
2017-05-22 15:30 | 848 | 847
2017-05-22 16:00 | 863 | 863
2017-05-22 16:30 | 890 | 889
2017-05-22 17:00 | 923 | 922
2017-05-22 17:30 | 964 | 960
2017-05-22 18:00 | 985 | 980
2017-05-22 18:30 | 963 | 956
2017-05-22 19:00 | 949 | 941
2017-05-22 19:30 | 915 | 913
2017-05-22 20:00 | 900 | 899
2017-05-22 20:30 | 879 | 879
2017-05-22 21:00 | 838 | 838
2017-05-22 21:30 | 799 | 799
2017-05-22 22:00 | 773 | 772
2017-05-22 22:30 | 756 | 753
2017-05-22 23:00 | 752 | 748
2017-05-22 23:30 | 707 | 701
2017-05-23 | 660 | 652
2017-05-23 00:30 | 609 | 599
2017-05-23 01:00 | 583 | 570
2017-05-23 01:30 | 561 | 548
2017-05-23 02:00 | 549 | 534
2017-05-23 02:30 | 545 | 530
2017-05-23 03:00 | 538 | 522
2017-05-23 03:30 | 540 | 523
2017-05-23 04:00 | 542 | 526
2017-05-23 04:30 | 552 | 538
2017-05-23 05:00 | 570 | 557
2017-05-23 05:30 | 608 | 600
2017-05-23 06:00 | 652 | 648
2017-05-23 06:30 | 724 | 723
2017-05-23 07:00 | 783 | 782
2017-05-23 07:30 | 827 | 827
2017-05-23 08:00 | 834 | 834
2017-05-23 08:30 | 820 | 820
2017-05-23 09:00 | 798 | 798
2017-05-23 09:30 | 777 | 777
2017-05-23 10:00 | 765 | 765
2017-05-23 10:30 | 759 | 759
2017-05-23 11:00 | 756 | 756
2017-05-23 11:30 | 752 | 751
2017-05-23 12:00 | 763 | 762
2017-05-23 12:30 | 760 | 758
2017-05-23 13:00 | 762 | 760
2017-05-23 13:30 | 774 | 773
2017-05-23 14:00 | 788 | 788
2017-05-23 14:30 | 808 | 808
2017-05-23 15:00 | 823 | 823
2017-05-23 15:30 | 841 | 840
2017-05-23 16:00 | 866 | 866
2017-05-23 16:30 | 890 | 890
2017-05-23 17:00 | 926 | 926
2017-05-23 17:30 | 970 | 970
2017-05-23 18:00 | 991 | 988
2017-05-23 18:30 | 967 | 959
2017-05-23 19:00 | 958 | 950
2017-05-23 19:30 | 926 | 922
2017-05-23 20:00 | 901 | 901
2017-05-23 20:30 | 884 | 883
2017-05-23 21:00 | 833 | 833
2017-05-23 21:30 | 797 | 797
2017-05-23 22:00 | 772 | 772
2017-05-23 22:30 | 759 | 758
2017-05-23 23:00 | 753 | 751
2017-05-23 23:30 | 706 | 702
2017-05-24 | 657 | 652
2017-05-24 00:30 | 610 | 600
2017-05-24 01:00 | 587 | 573
2017-05-24 01:30 | 568 | 553
2017-05-24 02:00 | 555 | 538
2017-05-24 02:30 | 546 | 528
2017-05-24 03:00 | 544 | 526
2017-05-24 03:30 | 544 | 526
2017-05-24 04:00 | 545 | 527
2017-05-24 04:30 | 558 | 543
2017-05-24 05:00 | 571 | 558
2017-05-24 05:30 | 612 | 604
2017-05-24 06:00 | 649 | 645
2017-05-24 06:30 | 725 | 721
2017-05-24 07:00 | 780 | 777
2017-05-24 07:30 | 834 | 830
2017-05-24 08:00 | 849 | 842
2017-05-24 08:30 | 835 | 830
2017-05-24 09:00 | 821 | 816
2017-05-24 09:30 | 806 | 801
2017-05-24 10:00 | 785 | 780
2017-05-24 10:30 | 771 | 767
2017-05-24 11:00 | 754 | 750
2017-05-24 11:30 | 742 | 739
2017-05-24 12:00 | 749 | 746
2017-05-24 12:30 | 759 | 756
2017-05-24 13:00 | 774 | 772
2017-05-24 13:30 | 788 | 786
2017-05-24 14:00 | 809 | 809
2017-05-24 14:30 | 823 | 823
2017-05-24 15:00 | 831 | 830
2017-05-24 15:30 | 843 | 842
2017-05-24 16:00 | 868 | 867
2017-05-24 16:30 | 890 | 889
2017-05-24 17:00 | 914 | 913
2017-05-24 17:30 | 951 | 951
2017-05-24 18:00 | 971 | 971
2017-05-24 18:30 | 949 | 947
2017-05-24 19:00 | 949 | 946
2017-05-24 19:30 | 925 | 921
2017-05-24 20:00 | 906 | 903
2017-05-24 20:30 | 895 | 893
2017-05-24 21:00 | 848 | 848
2017-05-24 21:30 | 812 | 811
2017-05-24 22:00 | 781 | 779
2017-05-24 22:30 | 758 | 755
2017-05-24 23:00 | 746 | 745
2017-05-24 23:30 | 702 | 698
2017-05-25 | 650 | 641
2017-05-25 00:30 | 604 | 593
2017-05-25 01:00 | 582 | 568
2017-05-25 01:30 | 566 | 550
2017-05-25 02:00 | 552 | 534
2017-05-25 02:30 | 544 | 525
2017-05-25 03:00 | 543 | 523
2017-05-25 03:30 | 542 | 522
2017-05-25 04:00 | 540 | 521
2017-05-25 04:30 | 558 | 540
2017-05-25 05:00 | 571 | 557
2017-05-25 05:30 | 603 | 595
2017-05-25 06:00 | 644 | 640
2017-05-25 06:30 | 713 | 711
2017-05-25 07:00 | 780 | 774
2017-05-25 07:30 | 816 | 812
2017-05-25 08:00 | 822 | 821
2017-05-25 08:30 | 803 | 802
2017-05-25 09:00 | 775 | 774
2017-05-25 09:30 | 755 | 755
2017-05-25 10:00 | 745 | 744
2017-05-25 10:30 | 732 | 732
2017-05-25 11:00 | 733 | 732
2017-05-25 11:30 | 714 | 714
2017-05-25 12:00 | 726 | 725
2017-05-25 12:30 | 737 | 737
2017-05-25 13:00 | 744 | 744
2017-05-25 13:30 | 750 | 750
2017-05-25 14:00 | 765 | 764
2017-05-25 14:30 | 776 | 776
2017-05-25 15:00 | 789 | 789
2017-05-25 15:30 | 803 | 803
2017-05-25 16:00 | 826 | 825
2017-05-25 16:30 | 850 | 850
2017-05-25 17:00 | 887 | 886
2017-05-25 17:30 | 926 | 925
2017-05-25 18:00 | 959 | 955
2017-05-25 18:30 | 944 | 936
2017-05-25 19:00 | 939 | 935
2017-05-25 19:30 | 924 | 918
2017-05-25 20:00 | 909 | 908
2017-05-25 20:30 | 885 | 884
2017-05-25 21:00 | 843 | 842
2017-05-25 21:30 | 797 | 796
2017-05-25 22:00 | 769 | 767
2017-05-25 22:30 | 752 | 748
2017-05-25 23:00 | 749 | 743
2017-05-25 23:30 | 706 | 697
2017-05-26 | 662 | 650
2017-05-26 00:30 | 611 | 600
2017-05-26 01:00 | 582 | 567
2017-05-26 01:30 | 560 | 543
2017-05-26 02:00 | 545 | 526
2017-05-26 02:30 | 542 | 520
2017-05-26 03:00 | 540 | 518
2017-05-26 03:30 | 535 | 513
2017-05-26 04:00 | 527 | 506
2017-05-26 04:30 | 545 | 528
2017-05-26 05:00 | 565 | 551
2017-05-26 05:30 | 599 | 590
2017-05-26 06:00 | 640 | 636
2017-05-26 06:30 | 706 | 705
2017-05-26 07:00 | 767 | 765
2017-05-26 07:30 | 814 | 814
2017-05-26 08:00 | 822 | 822
2017-05-26 08:30 | 804 | 804
2017-05-26 09:00 | 778 | 778
2017-05-26 09:30 | 760 | 760
2017-05-26 10:00 | 745 | 745
2017-05-26 10:30 | 736 | 736
2017-05-26 11:00 | 729 | 729
2017-05-26 11:30 | 731 | 731
2017-05-26 12:00 | 733 | 733
2017-05-26 12:30 | 732 | 732
2017-05-26 13:00 | 738 | 738
2017-05-26 13:30 | 745 | 745
2017-05-26 14:00 | 758 | 758
2017-05-26 14:30 | 768 | 768
2017-05-26 15:00 | 778 | 778
2017-05-26 15:30 | 792 | 792
2017-05-26 16:00 | 822 | 822
2017-05-26 16:30 | 847 | 847
2017-05-26 17:00 | 879 | 879
2017-05-26 17:30 | 906 | 906
2017-05-26 18:00 | 918 | 918
2017-05-26 18:30 | 900 | 898
2017-05-26 19:00 | 897 | 894
2017-05-26 19:30 | 877 | 872
2017-05-26 20:00 | 861 | 861
2017-05-26 20:30 | 853 | 853
2017-05-26 21:00 | 815 | 815
2017-05-26 21:30 | 787 | 786
2017-05-26 22:00 | 758 | 756
2017-05-26 22:30 | 753 | 749
2017-05-26 23:00 | 745 | 739
2017-05-26 23:30 | 707 | 699
2017-05-27 | 659 | 646
2017-05-27 00:30 | 612 | 597
2017-05-27 01:00 | 592 | 575
2017-05-27 01:30 | 567 | 547
2017-05-27 02:00 | 556 | 533
2017-05-27 02:30 | 548 | 525
2017-05-27 03:00 | 542 | 518
2017-05-27 03:30 | 537 | 514
2017-05-27 04:00 | 536 | 513
2017-05-27 04:30 | 535 | 511
2017-05-27 05:00 | 539 | 517
2017-05-27 05:30 | 553 | 534
2017-05-27 06:00 | 569 | 554
2017-05-27 06:30 | 596 | 583
2017-05-27 07:00 | 625 | 614
2017-05-27 07:30 | 653 | 646
2017-05-27 08:00 | 667 | 663
2017-05-27 08:30 | 679 | 677
2017-05-27 09:00 | 679 | 678
2017-05-27 09:30 | 676 | 675
2017-05-27 10:00 | 663 | 663
2017-05-27 10:30 | 657 | 656
2017-05-27 11:00 | 655 | 654
2017-05-27 11:30 | 645 | 645
2017-05-27 12:00 | 643 | 643
2017-05-27 12:30 | 634 | 632
2017-05-27 13:00 | 635 | 634
2017-05-27 13:30 | 633 | 631
2017-05-27 14:00 | 643 | 642
2017-05-27 14:30 | 653 | 652
2017-05-27 15:00 | 665 | 664
2017-05-27 15:30 | 690 | 690
2017-05-27 16:00 | 709 | 709
2017-05-27 16:30 | 738 | 738
2017-05-27 17:00 | 775 | 775
2017-05-27 17:30 | 819 | 817
2017-05-27 18:00 | 832 | 829
2017-05-27 18:30 | 823 | 819
2017-05-27 19:00 | 819 | 814
2017-05-27 19:30 | 806 | 800
2017-05-27 20:00 | 792 | 787
2017-05-27 20:30 | 789 | 784
2017-05-27 21:00 | 751 | 749
2017-05-27 21:30 | 726 | 723
2017-05-27 22:00 | 715 | 711
2017-05-27 22:30 | 715 | 710
2017-05-27 23:00 | 720 | 715
2017-05-27 23:30 | 686 | 678
2017-05-28 | 646 | 636
2017-05-28 00:30 | 603 | 590
2017-05-28 01:00 | 577 | 559
2017-05-28 01:30 | 561 | 541
2017-05-28 02:00 | 544 | 524
2017-05-28 02:30 | 534 | 510
2017-05-28 03:00 | 524 | 500
2017-05-28 03:30 | 529 | 505
2017-05-28 04:00 | 530 | 507
2017-05-28 04:30 | 527 | 504
2017-05-28 05:00 | 532 | 509
2017-05-28 05:30 | 540 | 518
2017-05-28 06:00 | 550 | 531
2017-05-28 06:30 | 568 | 551
2017-05-28 07:00 | 589 | 569
2017-05-28 07:30 | 610 | 595
2017-05-28 08:00 | 631 | 621
2017-05-28 08:30 | 639 | 633
2017-05-28 09:00 | 647 | 642
2017-05-28 09:30 | 648 | 645
2017-05-28 10:00 | 634 | 631
2017-05-28 10:30 | 625 | 622
2017-05-28 11:00 | 615 | 612
2017-05-28 11:30 | 603 | 600
2017-05-28 12:00 | 612 | 610
2017-05-28 12:30 | 612 | 609
2017-05-28 13:00 | 620 | 618
2017-05-28 13:30 | 621 | 619
2017-05-28 14:00 | 637 | 635
2017-05-28 14:30 | 662 | 661
2017-05-28 15:00 | 676 | 676
2017-05-28 15:30 | 687 | 687
2017-05-28 16:00 | 721 | 720
2017-05-28 16:30 | 756 | 755
2017-05-28 17:00 | 798 | 798
2017-05-28 17:30 | 848 | 848
2017-05-28 18:00 | 884 | 882
2017-05-28 18:30 | 871 | 868
2017-05-28 19:00 | 865 | 861
2017-05-28 19:30 | 838 | 835
2017-05-28 20:00 | 827 | 827
2017-05-28 20:30 | 813 | 813
2017-05-28 21:00 | 774 | 773
2017-05-28 21:30 | 753 | 750
2017-05-28 22:00 | 727 | 724
2017-05-28 22:30 | 711 | 708
2017-05-28 23:00 | 710 | 707
2017-05-28 23:30 | 678 | 673
2017-05-29 | 639 | 631
2017-05-29 00:30 | 596 | 584
2017-05-29 01:00 | 574 | 560
2017-05-29 01:30 | 560 | 543
2017-05-29 02:00 | 545 | 525
2017-05-29 02:30 | 534 | 514
2017-05-29 03:00 | 534 | 513
2017-05-29 03:30 | 533 | 513
2017-05-29 04:00 | 536 | 517
2017-05-29 04:30 | 548 | 531
2017-05-29 05:00 | 566 | 552
2017-05-29 05:30 | 603 | 595
2017-05-29 06:00 | 643 | 639
2017-05-29 06:30 | 719 | 717
2017-05-29 07:00 | 785 | 782
2017-05-29 07:30 | 829 | 829
2017-05-29 08:00 | 834 | 833
2017-05-29 08:30 | 821 | 818
2017-05-29 09:00 | 797 | 794
2017-05-29 09:30 | 778 | 776
2017-05-29 10:00 | 762 | 760
2017-05-29 10:30 | 754 | 752
2017-05-29 11:00 | 741 | 739
2017-05-29 11:30 | 733 | 732
2017-05-29 12:00 | 733 | 732
2017-05-29 12:30 | 733 | 732
2017-05-29 13:00 | 741 | 740
2017-05-29 13:30 | 750 | 750
2017-05-29 14:00 | 766 | 765
2017-05-29 14:30 | 773 | 773
2017-05-29 15:00 | 790 | 790
2017-05-29 15:30 | 809 | 808
2017-05-29 16:00 | 842 | 842
2017-05-29 16:30 | 878 | 878
2017-05-29 17:00 | 917 | 916
2017-05-29 17:30 | 961 | 957
2017-05-29 18:00 | 986 | 983
2017-05-29 18:30 | 963 | 957
2017-05-29 19:00 | 957 | 949
2017-05-29 19:30 | 934 | 921
2017-05-29 20:00 | 917 | 902
2017-05-29 20:30 | 883 | 883
2017-05-29 21:00 | 837 | 836
2017-05-29 21:30 | 804 | 801
2017-05-29 22:00 | 776 | 774
2017-05-29 22:30 | 750 | 747
2017-05-29 23:00 | 738 | 736
2017-05-29 23:30 | 699 | 696
2017-05-30 | 658 | 652
2017-05-30 00:30 | 611 | 601
2017-05-30 01:00 | 578 | 566
2017-05-30 01:30 | 567 | 553
2017-05-30 02:00 | 553 | 536
2017-05-30 02:30 | 544 | 524
2017-05-30 03:00 | 542 | 522
2017-05-30 03:30 | 537 | 518
2017-05-30 04:00 | 538 | 520
2017-05-30 04:30 | 556 | 540
2017-05-30 05:00 | 573 | 562
2017-05-30 05:30 | 605 | 599
2017-05-30 06:00 | 656 | 653
2017-05-30 06:30 | 736 | 735
2017-05-30 07:00 | 801 | 798
2017-05-30 07:30 | 868 | 867
2017-05-30 08:00 | 845 | 841
2017-05-30 08:30 | 823 | 818
2017-05-30 09:00 | 793 | 788
2017-05-30 09:30 | 768 | 761
2017-05-30 10:00 | 756 | 750
2017-05-30 10:30 | 737 | 733
2017-05-30 11:00 | 709 | 707
2017-05-30 11:30 | 705 | 704
2017-05-30 12:00 | 708 | 707
2017-05-30 12:30 | 717 | 716
2017-05-30 13:00 | 730 | 730
2017-05-30 13:30 | 755 | 754
2017-05-30 14:00 | 775 | 775
2017-05-30 14:30 | 784 | 784
2017-05-30 15:00 | 795 | 795
2017-05-30 15:30 | 814 | 814
2017-05-30 16:00 | 840 | 839
2017-05-30 16:30 | 877 | 876
2017-05-30 17:00 | 920 | 920
2017-05-30 17:30 | 981 | 981
2017-05-30 18:00 | 1002 | 1002
2017-05-30 18:30 | 981 | 980
2017-05-30 19:00 | 977 | 976
2017-05-30 19:30 | 955 | 953
2017-05-30 20:00 | 934 | 934
2017-05-30 20:30 | 908 | 908
2017-05-30 21:00 | 864 | 864
2017-05-30 21:30 | 817 | 815
2017-05-30 22:00 | 784 | 780
2017-05-30 22:30 | 775 | 771
2017-05-30 23:00 | 761 | 758
2017-05-30 23:30 | 724 | 720
2017-05-31 | 667 | 662
2017-05-31 00:30 | 617 | 609
2017-05-31 01:00 | 589 | 577
2017-05-31 01:30 | 569 | 556
2017-05-31 02:00 | 555 | 541
2017-05-31 02:30 | 545 | 529
2017-05-31 03:00 | 546 | 530
2017-05-31 03:30 | 542 | 526
2017-05-31 04:00 | 546 | 531
2017-05-31 04:30 | 560 | 548
2017-05-31 05:00 | 581 | 572
2017-05-31 05:30 | 618 | 614
2017-05-31 06:00 | 668 | 665
2017-05-31 06:30 | 748 | 746
2017-05-31 07:00 | 818 | 818
2017-05-31 07:30 | 873 | 873
2017-05-31 08:00 | 872 | 872
2017-05-31 08:30 | 843 | 843
2017-05-31 09:00 | 808 | 807
2017-05-31 09:30 | 778 | 777
2017-05-31 10:00 | 745 | 745
2017-05-31 10:30 | 730 | 729
2017-05-31 11:00 | 716 | 715
2017-05-31 11:30 | 702 | 702
2017-05-31 12:00 | 699 | 699
2017-05-31 12:30 | 696 | 696
2017-05-31 13:00 | 702 | 702
2017-05-31 13:30 | 707 | 707
2017-05-31 14:00 | 728 | 728
2017-05-31 14:30 | 743 | 742
2017-05-31 15:00 | 761 | 760
2017-05-31 15:30 | 783 | 782
2017-05-31 16:00 | 818 | 818
2017-05-31 16:30 | 866 | 865
2017-05-31 17:00 | 919 | 919
2017-05-31 17:30 | 961 | 961
2017-05-31 18:00 | 990 | 988
2017-05-31 18:30 | 978 | 975
2017-05-31 19:00 | 980 | 977
2017-05-31 19:30 | 956 | 952
2017-05-31 20:00 | 928 | 927
2017-05-31 20:30 | 915 | 913
2017-05-31 21:00 | 870 | 869
2017-05-31 21:30 | 839 | 839
2017-05-31 22:00 | 800 | 799
2017-05-31 22:30 | 782 | 781
2017-05-31 23:00 | 778 | 776
2017-05-31 23:30 | 734 | 728
2017-06-01 | 676 | 671
2017-06-01 00:30 | 630 | 621
2017-06-01 01:00 | 598 | 586
2017-06-01 01:30 | 580 | 565
2017-06-01 02:00 | 566 | 550
2017-06-01 02:30 | 555 | 538
2017-06-01 03:00 | 549 | 532
2017-06-01 03:30 | 551 | 535
2017-06-01 04:00 | 556 | 540
2017-06-01 04:30 | 572 | 558
2017-06-01 05:00 | 588 | 578
2017-06-01 05:30 | 629 | 624
2017-06-01 06:00 | 675 | 673
2017-06-01 06:30 | 777 | 771
2017-06-01 07:00 | 855 | 850
2017-06-01 07:30 | 906 | 901
2017-06-01 08:00 | 911 | 907
2017-06-01 08:30 | 874 | 869
2017-06-01 09:00 | 830 | 822
2017-06-01 09:30 | 801 | 792
2017-06-01 10:00 | 773 | 767
2017-06-01 10:30 | 747 | 744
2017-06-01 11:00 | 732 | 730
2017-06-01 11:30 | 712 | 709
2017-06-01 12:00 | 706 | 705
2017-06-01 12:30 | 709 | 708
2017-06-01 13:00 | 707 | 706
2017-06-01 13:30 | 715 | 715
2017-06-01 14:00 | 740 | 740
2017-06-01 14:30 | 751 | 751
2017-06-01 15:00 | 765 | 765
2017-06-01 15:30 | 787 | 787
2017-06-01 16:00 | 824 | 824
2017-06-01 16:30 | 865 | 865
2017-06-01 17:00 | 919 | 919
2017-06-01 17:30 | 975 | 975
2017-06-01 18:00 | 1008 | 1007
2017-06-01 18:30 | 1003 | 1001
2017-06-01 19:00 | 1008 | 1006
2017-06-01 19:30 | 988 | 987
2017-06-01 20:00 | 971 | 969
2017-06-01 20:30 | 954 | 952
2017-06-01 21:00 | 923 | 920
2017-06-01 21:30 | 868 | 866
2017-06-01 22:00 | 834 | 833
2017-06-01 22:30 | 812 | 810
2017-06-01 23:00 | 796 | 795
2017-06-01 23:30 | 746 | 745
2017-06-02 | 699 | 698
2017-06-02 00:30 | 646 | 642
2017-06-02 01:00 | 610 | 602
2017-06-02 01:30 | 584 | 575
2017-06-02 02:00 | 573 | 563
2017-06-02 02:30 | 561 | 550
2017-06-02 03:00 | 558 | 546
2017-06-02 03:30 | 556 | 545
2017-06-02 04:00 | 558 | 548
2017-06-02 04:30 | 571 | 562
2017-06-02 05:00 | 597 | 590
2017-06-02 05:30 | 635 | 633
2017-06-02 06:00 | 688 | 685
2017-06-02 06:30 | 777 | 776
2017-06-02 07:00 | 856 | 854
2017-06-02 07:30 | 918 | 909
2017-06-02 08:00 | 912 | 904
2017-06-02 08:30 | 880 | 872
2017-06-02 09:00 | 845 | 834
2017-06-02 09:30 | 810 | 801
2017-06-02 10:00 | 775 | 771
2017-06-02 10:30 | 748 | 745
2017-06-02 11:00 | 726 | 725
2017-06-02 11:30 | 713 | 711
2017-06-02 12:00 | 702 | 701
2017-06-02 12:30 | 696 | 696
2017-06-02 13:00 | 692 | 692
2017-06-02 13:30 | 700 | 700
2017-06-02 14:00 | 713 | 713
2017-06-02 14:30 | 727 | 727
2017-06-02 15:00 | 744 | 744
2017-06-02 15:30 | 770 | 770
2017-06-02 16:00 | 803 | 803
2017-06-02 16:30 | 843 | 843
2017-06-02 17:00 | 887 | 887
2017-06-02 17:30 | 931 | 931
2017-06-02 18:00 | 945 | 945
2017-06-02 18:30 | 927 | 926
2017-06-02 19:00 | 932 | 932
2017-06-02 19:30 | 918 | 917
2017-06-02 20:00 | 912 | 912
2017-06-02 20:30 | 908 | 908
2017-06-02 21:00 | 877 | 876
2017-06-02 21:30 | 842 | 840
2017-06-02 22:00 | 815 | 814
2017-06-02 22:30 | 797 | 797
2017-06-02 23:00 | 792 | 791
2017-06-02 23:30 | 753 | 751
2017-06-03 | 711 | 706
2017-06-03 00:30 | 655 | 647
2017-06-03 01:00 | 621 | 611
2017-06-03 01:30 | 592 | 583
2017-06-03 02:00 | 579 | 569
2017-06-03 02:30 | 570 | 558
2017-06-03 03:00 | 579 | 568
2017-06-03 03:30 | 582 | 572
2017-06-03 04:00 | 579 | 568
2017-06-03 04:30 | 580 | 571
2017-06-03 05:00 | 590 | 581
2017-06-03 05:30 | 607 | 601
2017-06-03 06:00 | 614 | 609
2017-06-03 06:30 | 645 | 642
2017-06-03 07:00 | 675 | 671
2017-06-03 07:30 | 713 | 711
2017-06-03 08:00 | 733 | 732
2017-06-03 08:30 | 750 | 748
2017-06-03 09:00 | 742 | 741
2017-06-03 09:30 | 740 | 739
2017-06-03 10:00 | 730 | 730
2017-06-03 10:30 | 711 | 710
2017-06-03 11:00 | 687 | 687
2017-06-03 11:30 | 663 | 663
2017-06-03 12:00 | 651 | 651
2017-06-03 12:30 | 644 | 644
2017-06-03 13:00 | 648 | 647
2017-06-03 13:30 | 652 | 652
2017-06-03 14:00 | 669 | 669
2017-06-03 14:30 | 685 | 685
2017-06-03 15:00 | 708 | 708
2017-06-03 15:30 | 732 | 732
2017-06-03 16:00 | 741 | 741
2017-06-03 16:30 | 777 | 777
2017-06-03 17:00 | 825 | 824
2017-06-03 17:30 | 875 | 875
2017-06-03 18:00 | 892 | 892
2017-06-03 18:30 | 890 | 889
2017-06-03 19:00 | 877 | 876
2017-06-03 19:30 | 867 | 865
2017-06-03 20:00 | 852 | 850
2017-06-03 20:30 | 887 | 886
2017-06-03 21:00 | 854 | 854
2017-06-03 21:30 | 794 | 794
2017-06-03 22:00 | 783 | 783
2017-06-03 22:30 | 787 | 787
2017-06-03 23:00 | 768 | 768
2017-06-03 23:30 | 735 | 734
2017-06-04 | 705 | 702
2017-06-04 00:30 | 648 | 641
2017-06-04 01:00 | 617 | 608
2017-06-04 01:30 | 620 | 612
2017-06-04 02:00 | 598 | 587
2017-06-04 02:30 | 585 | 573
2017-06-04 03:00 | 579 | 565
2017-06-04 03:30 | 574 | 560
2017-06-04 04:00 | 569 | 555
2017-06-04 04:30 | 574 | 560
2017-06-04 05:00 | 575 | 563
2017-06-04 05:30 | 589 | 578
2017-06-04 06:00 | 600 | 592
2017-06-04 06:30 | 621 | 615
2017-06-04 07:00 | 639 | 633
2017-06-04 07:30 | 650 | 644
2017-06-04 08:00 | 673 | 669
2017-06-04 08:30 | 697 | 695
2017-06-04 09:00 | 718 | 717
2017-06-04 09:30 | 717 | 716
2017-06-04 10:00 | 697 | 697
2017-06-04 10:30 | 663 | 662
2017-06-04 11:00 | 668 | 667
2017-06-04 11:30 | 658 | 657
2017-06-04 12:00 | 638 | 637
2017-06-04 12:30 | 625 | 624
2017-06-04 13:00 | 637 | 636
2017-06-04 13:30 | 633 | 631
2017-06-04 14:00 | 646 | 644
2017-06-04 14:30 | 670 | 669
2017-06-04 15:00 | 687 | 686
2017-06-04 15:30 | 711 | 711
2017-06-04 16:00 | 744 | 744
2017-06-04 16:30 | 782 | 782
2017-06-04 17:00 | 841 | 841
2017-06-04 17:30 | 889 | 888
2017-06-04 18:00 | 921 | 919
2017-06-04 18:30 | 914 | 912
2017-06-04 19:00 | 905 | 903
2017-06-04 19:30 | 895 | 890
2017-06-04 20:00 | 882 | 877
2017-06-04 20:30 | 870 | 868
2017-06-04 21:00 | 837 | 836
2017-06-04 21:30 | 809 | 807
2017-06-04 22:00 | 788 | 787
2017-06-04 22:30 | 769 | 769
2017-06-04 23:00 | 762 | 760
2017-06-04 23:30 | 728 | 725
2017-06-05 | 693 | 687
2017-06-05 00:30 | 645 | 636
2017-06-05 01:00 | 620 | 607
2017-06-05 01:30 | 606 | 592
2017-06-05 02:00 | 583 | 568
2017-06-05 02:30 | 578 | 562
2017-06-05 03:00 | 587 | 573
2017-06-05 03:30 | 586 | 571
2017-06-05 04:00 | 589 | 575
2017-06-05 04:30 | 600 | 589
2017-06-05 05:00 | 621 | 614
2017-06-05 05:30 | 649 | 645
2017-06-05 06:00 | 702 | 701
2017-06-05 06:30 | 790 | 789
2017-06-05 07:00 | 870 | 868
2017-06-05 07:30 | 920 | 919
2017-06-05 08:00 | 922 | 918
2017-06-05 08:30 | 892 | 883
2017-06-05 09:00 | 856 | 845
2017-06-05 09:30 | 829 | 817
2017-06-05 10:00 | 798 | 795
2017-06-05 10:30 | 771 | 769
2017-06-05 11:00 | 768 | 767
2017-06-05 11:30 | 765 | 765
2017-06-05 12:00 | 754 | 754
2017-06-05 12:30 | 760 | 760
2017-06-05 13:00 | 754 | 754
2017-06-05 13:30 | 760 | 760
2017-06-05 14:00 | 790 | 790
2017-06-05 14:30 | 801 | 801
2017-06-05 15:00 | 802 | 802
2017-06-05 15:30 | 823 | 822
2017-06-05 16:00 | 852 | 851
2017-06-05 16:30 | 888 | 887
2017-06-05 17:00 | 936 | 936
2017-06-05 17:30 | 1003 | 1002
2017-06-05 18:00 | 1031 | 1030
2017-06-05 18:30 | 1013 | 1011
2017-06-05 19:00 | 1012 | 1009
2017-06-05 19:30 | 984 | 980
2017-06-05 20:00 | 963 | 959
2017-06-05 20:30 | 956 | 951
2017-06-05 21:00 | 901 | 899
2017-06-05 21:30 | 857 | 855
2017-06-05 22:00 | 820 | 819
2017-06-05 22:30 | 800 | 800
2017-06-05 23:00 | 790 | 789
2017-06-05 23:30 | 751 | 749
2017-06-06 | 705 | 700
2017-06-06 00:30 | 655 | 648
2017-06-06 01:00 | 627 | 618
2017-06-06 01:30 | 603 | 592
2017-06-06 02:00 | 587 | 575
2017-06-06 02:30 | 578 | 564
2017-06-06 03:00 | 576 | 561
2017-06-06 03:30 | 576 | 561
2017-06-06 04:00 | 580 | 566
2017-06-06 04:30 | 591 | 580
2017-06-06 05:00 | 613 | 606
2017-06-06 05:30 | 651 | 648
2017-06-06 06:00 | 708 | 707
2017-06-06 06:30 | 789 | 789
2017-06-06 07:00 | 870 | 870
2017-06-06 07:30 | 920 | 920
2017-06-06 08:00 | 909 | 908
2017-06-06 08:30 | 866 | 865
2017-06-06 09:00 | 824 | 823
2017-06-06 09:30 | 792 | 791
2017-06-06 10:00 | 774 | 773
2017-06-06 10:30 | 752 | 751
2017-06-06 11:00 | 731 | 731
2017-06-06 11:30 | 720 | 720
2017-06-06 12:00 | 716 | 716
2017-06-06 12:30 | 714 | 714
2017-06-06 13:00 | 708 | 708
2017-06-06 13:30 | 718 | 718
2017-06-06 14:00 | 736 | 736
2017-06-06 14:30 | 748 | 748
2017-06-06 15:00 | 760 | 760
2017-06-06 15:30 | 780 | 780
2017-06-06 16:00 | 816 | 816
2017-06-06 16:30 | 859 | 858
2017-06-06 17:00 | 908 | 908
2017-06-06 17:30 | 959 | 959
2017-06-06 18:00 | 986 | 985
2017-06-06 18:30 | 980 | 978
2017-06-06 19:00 | 988 | 986
2017-06-06 19:30 | 972 | 969
2017-06-06 20:00 | 952 | 952
2017-06-06 20:30 | 942 | 942
2017-06-06 21:00 | 903 | 903
2017-06-06 21:30 | 864 | 862
2017-06-06 22:00 | 828 | 826
2017-06-06 22:30 | 807 | 805
2017-06-06 23:00 | 794 | 793
2017-06-06 23:30 | 750 | 748
2017-06-07 | 698 | 695
2017-06-07 00:30 | 640 | 633
2017-06-07 01:00 | 596 | 585
2017-06-07 01:30 | 568 | 556
2017-06-07 02:00 | 553 | 539
2017-06-07 02:30 | 549 | 534
2017-06-07 03:00 | 544 | 528
2017-06-07 03:30 | 538 | 522
2017-06-07 04:00 | 545 | 530
2017-06-07 04:30 | 572 | 560
2017-06-07 05:00 | 599 | 591
2017-06-07 05:30 | 655 | 652
2017-06-07 06:00 | 713 | 712
2017-06-07 06:30 | 818 | 818
2017-06-07 07:00 | 895 | 895
2017-06-07 07:30 | 954 | 953
2017-06-07 08:00 | 941 | 940
2017-06-07 08:30 | 900 | 898
2017-06-07 09:00 | 843 | 839
2017-06-07 09:30 | 781 | 776
2017-06-07 10:00 | 739 | 736
2017-06-07 10:30 | 704 | 704
2017-06-07 11:00 | 683 | 683
2017-06-07 11:30 | 665 | 665
2017-06-07 12:00 | 662 | 661
2017-06-07 12:30 | 675 | 674
2017-06-07 13:00 | 710 | 709
2017-06-07 13:30 | 718 | 717
2017-06-07 14:00 | 721 | 720
2017-06-07 14:30 | 733 | 732
2017-06-07 15:00 | 750 | 749
2017-06-07 15:30 | 778 | 777
2017-06-07 16:00 | 816 | 815
2017-06-07 16:30 | 866 | 864
2017-06-07 17:00 | 922 | 921
2017-06-07 17:30 | 1004 | 1003
2017-06-07 18:00 | 1048 | 1048
2017-06-07 18:30 | 1030 | 1029
2017-06-07 19:00 | 1034 | 1033
2017-06-07 19:30 | 1013 | 1010
2017-06-07 20:00 | 1002 | 999
2017-06-07 20:30 | 989 | 986
2017-06-07 21:00 | 950 | 949
2017-06-07 21:30 | 902 | 899
2017-06-07 22:00 | 854 | 849
2017-06-07 22:30 | 826 | 821
2017-06-07 23:00 | 803 | 803
2017-06-07 23:30 | 758 | 756
2017-06-08 | 710 | 705
2017-06-08 00:30 | 656 | 650
2017-06-08 01:00 | 625 | 617
2017-06-08 01:30 | 603 | 593
2017-06-08 02:00 | 581 | 569
2017-06-08 02:30 | 572 | 559
2017-06-08 03:00 | 570 | 557
2017-06-08 03:30 | 571 | 559
2017-06-08 04:00 | 579 | 567
2017-06-08 04:30 | 595 | 585
2017-06-08 05:00 | 624 | 617
2017-06-08 05:30 | 676 | 673
2017-06-08 06:00 | 736 | 735
2017-06-08 06:30 | 817 | 817
2017-06-08 07:00 | 883 | 883
2017-06-08 07:30 | 946 | 946
2017-06-08 08:00 | 934 | 933
2017-06-08 08:30 | 891 | 890
2017-06-08 09:00 | 837 | 836
2017-06-08 09:30 | 796 | 794
2017-06-08 10:00 | 764 | 761
2017-06-08 10:30 | 739 | 737
2017-06-08 11:00 | 718 | 717
2017-06-08 11:30 | 698 | 697
2017-06-08 12:00 | 686 | 685
2017-06-08 12:30 | 685 | 685
2017-06-08 13:00 | 690 | 690
2017-06-08 13:30 | 698 | 698
2017-06-08 14:00 | 715 | 715
2017-06-08 14:30 | 728 | 727
2017-06-08 15:00 | 741 | 741
2017-06-08 15:30 | 763 | 763
2017-06-08 16:00 | 822 | 821
2017-06-08 16:30 | 873 | 873
2017-06-08 17:00 | 932 | 932
2017-06-08 17:30 | 1000 | 999
2017-06-08 18:00 | 1028 | 1028
2017-06-08 18:30 | 1017 | 1015
2017-06-08 19:00 | 1020 | 1016
2017-06-08 19:30 | 1014 | 1010
2017-06-08 20:00 | 1004 | 1002
2017-06-08 20:30 | 1002 | 999
2017-06-08 21:00 | 971 | 969
2017-06-08 21:30 | 924 | 919
2017-06-08 22:00 | 882 | 878
2017-06-08 22:30 | 852 | 849
2017-06-08 23:00 | 834 | 833
2017-06-08 23:30 | 788 | 786
2017-06-09 | 741 | 736
2017-06-09 00:30 | 690 | 682
2017-06-09 01:00 | 657 | 646
2017-06-09 01:30 | 635 | 621
2017-06-09 02:00 | 612 | 595
2017-06-09 02:30 | 604 | 587
2017-06-09 03:00 | 599 | 582
2017-06-09 03:30 | 600 | 582
2017-06-09 04:00 | 644 | 634
2017-06-09 04:30 | 625 | 613
2017-06-09 05:00 | 637 | 627
2017-06-09 05:30 | 682 | 677
2017-06-09 06:00 | 732 | 730
2017-06-09 06:30 | 813 | 812
2017-06-09 07:00 | 893 | 891
2017-06-09 07:30 | 954 | 952
2017-06-09 08:00 | 923 | 921
2017-06-09 08:30 | 886 | 882
2017-06-09 09:00 | 781 | 777
2017-06-09 09:30 | 701 | 701
2017-06-09 10:00 | 784 | 784
2017-06-09 10:30 | 779 | 779
2017-06-09 11:00 | 763 | 763
2017-06-09 11:30 | 767 | 767
2017-06-09 12:00 | 784 | 784
2017-06-09 12:30 | 791 | 791
2017-06-09 13:00 | 794 | 794
2017-06-09 13:30 | 830 | 830
2017-06-09 14:00 | 838 | 838
2017-06-09 14:30 | 839 | 839
2017-06-09 15:00 | 847 | 846
2017-06-09 15:30 | 856 | 855
2017-06-09 16:00 | 875 | 875
2017-06-09 16:30 | 906 | 906
2017-06-09 17:00 | 940 | 939
2017-06-09 17:30 | 984 | 984
2017-06-09 18:00 | 998 | 997
2017-06-09 18:30 | 980 | 979
2017-06-09 19:00 | 980 | 978
2017-06-09 19:30 | 963 | 960
2017-06-09 20:00 | 949 | 947
2017-06-09 20:30 | 931 | 930
2017-06-09 21:00 | 900 | 900
2017-06-09 21:30 | 866 | 866
2017-06-09 22:00 | 843 | 842
2017-06-09 22:30 | 828 | 826
2017-06-09 23:00 | 825 | 823
2017-06-09 23:30 | 780 | 777
2017-06-10 | 733 | 728
2017-06-10 00:30 | 681 | 673
2017-06-10 01:00 | 654 | 642
2017-06-10 01:30 | 630 | 616
2017-06-10 02:00 | 613 | 596
2017-06-10 02:30 | 603 | 585
2017-06-10 03:00 | 592 | 573
2017-06-10 03:30 | 594 | 576
2017-06-10 04:00 | 590 | 572
2017-06-10 04:30 | 620 | 607
2017-06-10 05:00 | 613 | 601
2017-06-10 05:30 | 611 | 598
2017-06-10 06:00 | 627 | 616
2017-06-10 06:30 | 657 | 650
2017-06-10 07:00 | 685 | 679
2017-06-10 07:30 | 725 | 721
2017-06-10 08:00 | 743 | 741
2017-06-10 08:30 | 760 | 759
2017-06-10 09:00 | 753 | 753
2017-06-10 09:30 | 746 | 746
2017-06-10 10:00 | 734 | 734
2017-06-10 10:30 | 719 | 719
2017-06-10 11:00 | 706 | 706
2017-06-10 11:30 | 702 | 702
2017-06-10 12:00 | 704 | 704
2017-06-10 12:30 | 710 | 709
2017-06-10 13:00 | 714 | 714
2017-06-10 13:30 | 709 | 708
2017-06-10 14:00 | 709 | 708
2017-06-10 14:30 | 722 | 722
2017-06-10 15:00 | 729 | 728
2017-06-10 15:30 | 744 | 743
2017-06-10 16:00 | 772 | 772
2017-06-10 16:30 | 802 | 802
2017-06-10 17:00 | 858 | 858
2017-06-10 17:30 | 906 | 905
2017-06-10 18:00 | 916 | 916
2017-06-10 18:30 | 902 | 902
2017-06-10 19:00 | 902 | 901
2017-06-10 19:30 | 884 | 882
2017-06-10 20:00 | 878 | 875
2017-06-10 20:30 | 875 | 872
2017-06-10 21:00 | 848 | 844
2017-06-10 21:30 | 818 | 816
2017-06-10 22:00 | 801 | 798
2017-06-10 22:30 | 794 | 790
2017-06-10 23:00 | 802 | 798
2017-06-10 23:30 | 756 | 750
2017-06-11 | 721 | 716
2017-06-11 00:30 | 675 | 666
2017-06-11 01:00 | 642 | 630
2017-06-11 01:30 | 625 | 609
2017-06-11 02:00 | 599 | 581
2017-06-11 02:30 | 593 | 575
2017-06-11 03:00 | 586 | 566
2017-06-11 03:30 | 588 | 568
2017-06-11 04:00 | 586 | 566
2017-06-11 04:30 | 585 | 565
2017-06-11 05:00 | 584 | 564
2017-06-11 05:30 | 593 | 574
2017-06-11 06:00 | 606 | 589
2017-06-11 06:30 | 623 | 609
2017-06-11 07:00 | 644 | 630
2017-06-11 07:30 | 680 | 671
2017-06-11 08:00 | 713 | 707
2017-06-11 08:30 | 757 | 755
2017-06-11 09:00 | 803 | 801
2017-06-11 09:30 | 819 | 817
2017-06-11 10:00 | 836 | 836
2017-06-11 10:30 | 844 | 843
2017-06-11 11:00 | 833 | 832
2017-06-11 11:30 | 829 | 828
2017-06-11 12:00 | 803 | 802
2017-06-11 12:30 | 799 | 797
2017-06-11 13:00 | 781 | 779
2017-06-11 13:30 | 789 | 787
2017-06-11 14:00 | 806 | 805
2017-06-11 14:30 | 808 | 807
2017-06-11 15:00 | 809 | 807
2017-06-11 15:30 | 810 | 808
2017-06-11 16:00 | 830 | 829
2017-06-11 16:30 | 863 | 863
2017-06-11 17:00 | 905 | 904
2017-06-11 17:30 | 951 | 948
2017-06-11 18:00 | 969 | 966
2017-06-11 18:30 | 965 | 961
2017-06-11 19:00 | 956 | 950
2017-06-11 19:30 | 937 | 932
2017-06-11 20:00 | 920 | 915
2017-06-11 20:30 | 910 | 907
2017-06-11 21:00 | 871 | 869
2017-06-11 21:30 | 844 | 840
2017-06-11 22:00 | 823 | 816
2017-06-11 22:30 | 809 | 802
2017-06-11 23:00 | 797 | 795
2017-06-11 23:30 | 760 | 755
2017-06-12 | 713 | 706
2017-06-12 00:30 | 673 | 662
2017-06-12 01:00 | 643 | 629
2017-06-12 01:30 | 618 | 602
2017-06-12 02:00 | 601 | 584
2017-06-12 02:30 | 588 | 570
2017-06-12 03:00 | 600 | 586
2017-06-12 03:30 | 614 | 602
2017-06-12 04:00 | 611 | 599
2017-06-12 04:30 | 597 | 583
2017-06-12 05:00 | 614 | 602
2017-06-12 05:30 | 655 | 647
2017-06-12 06:00 | 703 | 700
2017-06-12 06:30 | 791 | 788
2017-06-12 07:00 | 861 | 853
2017-06-12 07:30 | 922 | 919
2017-06-12 08:00 | 936 | 932
2017-06-12 08:30 | 923 | 920
2017-06-12 09:00 | 894 | 891
2017-06-12 09:30 | 877 | 875
2017-06-12 10:00 | 865 | 863
2017-06-12 10:30 | 865 | 862
2017-06-12 11:00 | 847 | 844
2017-06-12 11:30 | 826 | 822
2017-06-12 12:00 | 809 | 804
2017-06-12 12:30 | 803 | 798
2017-06-12 13:00 | 814 | 809
2017-06-12 13:30 | 845 | 842
2017-06-12 14:00 | 861 | 859
2017-06-12 14:30 | 864 | 861
2017-06-12 15:00 | 870 | 867
2017-06-12 15:30 | 883 | 881
2017-06-12 16:00 | 901 | 899
2017-06-12 16:30 | 934 | 933
2017-06-12 17:00 | 984 | 984
2017-06-12 17:30 | 1034 | 1033
2017-06-12 18:00 | 1049 | 1046
2017-06-12 18:30 | 1029 | 1025
2017-06-12 19:00 | 1032 | 1027
2017-06-12 19:30 | 1016 | 1008
2017-06-12 20:00 | 991 | 988
2017-06-12 20:30 | 976 | 975
2017-06-12 21:00 | 931 | 930
2017-06-12 21:30 | 884 | 881
2017-06-12 22:00 | 858 | 853
2017-06-12 22:30 | 831 | 830
2017-06-12 23:00 | 816 | 816
2017-06-12 23:30 | 774 | 774
2017-06-13 | 723 | 721
2017-06-13 00:30 | 679 | 673
2017-06-13 01:00 | 646 | 638
2017-06-13 01:30 | 622 | 612
2017-06-13 02:00 | 608 | 596
2017-06-13 02:30 | 598 | 585
2017-06-13 03:00 | 592 | 579
2017-06-13 03:30 | 594 | 581
2017-06-13 04:00 | 621 | 612
2017-06-13 04:30 | 624 | 617
2017-06-13 05:00 | 650 | 646
2017-06-13 05:30 | 666 | 664
2017-06-13 06:00 | 714 | 714
2017-06-13 06:30 | 803 | 803
2017-06-13 07:00 | 869 | 869
2017-06-13 07:30 | 950 | 949
2017-06-13 08:00 | 971 | 970
2017-06-13 08:30 | 965 | 963
2017-06-13 09:00 | 963 | 961
2017-06-13 09:30 | 965 | 962
2017-06-13 10:00 | 964 | 961
2017-06-13 10:30 | 965 | 963
2017-06-13 11:00 | 961 | 959
2017-06-13 11:30 | 958 | 955
2017-06-13 12:00 | 966 | 963
2017-06-13 12:30 | 973 | 970
2017-06-13 13:00 | 975 | 972
2017-06-13 13:30 | 984 | 980
2017-06-13 14:00 | 969 | 966
2017-06-13 14:30 | 962 | 959
2017-06-13 15:00 | 965 | 962
2017-06-13 15:30 | 966 | 964
2017-06-13 16:00 | 989 | 986
2017-06-13 16:30 | 1012 | 1009
2017-06-13 17:00 | 1050 | 1047
2017-06-13 17:30 | 1102 | 1101
2017-06-13 18:00 | 1125 | 1125
2017-06-13 18:30 | 1107 | 1107
2017-06-13 19:00 | 1102 | 1102
2017-06-13 19:30 | 1075 | 1074
2017-06-13 20:00 | 1055 | 1053
2017-06-13 20:30 | 1046 | 1043
2017-06-13 21:00 | 998 | 991
2017-06-13 21:30 | 945 | 938
2017-06-13 22:00 | 905 | 898
2017-06-13 22:30 | 878 | 870
2017-06-13 23:00 | 854 | 849
2017-06-13 23:30 | 807 | 803
2017-06-14 | 748 | 746
2017-06-14 00:30 | 693 | 690
2017-06-14 01:00 | 660 | 654
2017-06-14 01:30 | 661 | 656
2017-06-14 02:00 | 666 | 661
2017-06-14 02:30 | 655 | 649
2017-06-14 03:00 | 651 | 646
2017-06-14 03:30 | 654 | 649
2017-06-14 04:00 | 643 | 638
2017-06-14 04:30 | 617 | 609
2017-06-14 05:00 | 681 | 678
2017-06-14 05:30 | 678 | 676
2017-06-14 06:00 | 728 | 727
2017-06-14 06:30 | 816 | 815
2017-06-14 07:00 | 887 | 884
2017-06-14 07:30 | 962 | 961
2017-06-14 08:00 | 979 | 976
2017-06-14 08:30 | 968 | 965
2017-06-14 09:00 | 947 | 944
2017-06-14 09:30 | 936 | 932
2017-06-14 10:00 | 944 | 941
2017-06-14 10:30 | 940 | 938
2017-06-14 11:00 | 924 | 921
2017-06-14 11:30 | 911 | 908
2017-06-14 12:00 | 914 | 911
2017-06-14 12:30 | 896 | 892
2017-06-14 13:00 | 915 | 911
2017-06-14 13:30 | 913 | 910
2017-06-14 14:00 | 922 | 919
2017-06-14 14:30 | 934 | 932
2017-06-14 15:00 | 923 | 921
2017-06-14 15:30 | 926 | 923
2017-06-14 16:00 | 955 | 952
2017-06-14 16:30 | 986 | 984
2017-06-14 17:00 | 1027 | 1026
2017-06-14 17:30 | 1084 | 1083
2017-06-14 18:00 | 1103 | 1101
2017-06-14 18:30 | 1085 | 1081
2017-06-14 19:00 | 1079 | 1072
2017-06-14 19:30 | 1048 | 1041
2017-06-14 20:00 | 1019 | 1016
2017-06-14 20:30 | 1006 | 1002
2017-06-14 21:00 | 954 | 953
2017-06-14 21:30 | 906 | 905
2017-06-14 22:00 | 871 | 868
2017-06-14 22:30 | 850 | 843
2017-06-14 23:00 | 831 | 826
2017-06-14 23:30 | 788 | 782
2017-06-15 | 730 | 725
2017-06-15 00:30 | 674 | 669
2017-06-15 01:00 | 641 | 634
2017-06-15 01:30 | 615 | 606
2017-06-15 02:00 | 598 | 587
2017-06-15 02:30 | 589 | 578
2017-06-15 03:00 | 589 | 577
2017-06-15 03:30 | 592 | 580
2017-06-15 04:00 | 606 | 596
2017-06-15 04:30 | 620 | 612
2017-06-15 05:00 | 622 | 615
2017-06-15 05:30 | 657 | 653
2017-06-15 06:00 | 700 | 698
2017-06-15 06:30 | 776 | 775
2017-06-15 07:00 | 846 | 843
2017-06-15 07:30 | 911 | 910
2017-06-15 08:00 | 931 | 930
2017-06-15 08:30 | 915 | 914
2017-06-15 09:00 | 884 | 884
2017-06-15 09:30 | 850 | 848
2017-06-15 10:00 | 825 | 822
2017-06-15 10:30 | 819 | 816
2017-06-15 11:00 | 836 | 835
2017-06-15 11:30 | 851 | 850
2017-06-15 12:00 | 812 | 810
2017-06-15 12:30 | 816 | 814
2017-06-15 13:00 | 802 | 800
2017-06-15 13:30 | 819 | 817
2017-06-15 14:00 | 843 | 842
2017-06-15 14:30 | 851 | 850
2017-06-15 15:00 | 853 | 851
2017-06-15 15:30 | 862 | 861
2017-06-15 16:00 | 890 | 889
2017-06-15 16:30 | 909 | 908
2017-06-15 17:00 | 945 | 945
2017-06-15 17:30 | 986 | 985
2017-06-15 18:00 | 1015 | 1012
2017-06-15 18:30 | 1010 | 1005
2017-06-15 19:00 | 1010 | 1005
2017-06-15 19:30 | 997 | 990
2017-06-15 20:00 | 976 | 973
2017-06-15 20:30 | 971 | 967
2017-06-15 21:00 | 935 | 930
2017-06-15 21:30 | 888 | 886
2017-06-15 22:00 | 851 | 847
2017-06-15 22:30 | 841 | 834
2017-06-15 23:00 | 832 | 827
2017-06-15 23:30 | 788 | 782
2017-06-16 | 734 | 729
2017-06-16 00:30 | 679 | 673
2017-06-16 01:00 | 648 | 639
2017-06-16 01:30 | 625 | 616
2017-06-16 02:00 | 614 | 604
2017-06-16 02:30 | 603 | 592
2017-06-16 03:00 | 599 | 589
2017-06-16 03:30 | 604 | 594
2017-06-16 04:00 | 606 | 596
2017-06-16 04:30 | 611 | 601
2017-06-16 05:00 | 630 | 622
2017-06-16 05:30 | 667 | 662
2017-06-16 06:00 | 713 | 712
2017-06-16 06:30 | 784 | 783
2017-06-16 07:00 | 846 | 846
2017-06-16 07:30 | 917 | 913
2017-06-16 08:00 | 931 | 925
2017-06-16 08:30 | 917 | 912
2017-06-16 09:00 | 898 | 892
2017-06-16 09:30 | 892 | 887
2017-06-16 10:00 | 886 | 884
2017-06-16 10:30 | 882 | 881
2017-06-16 11:00 | 878 | 877
2017-06-16 11:30 | 865 | 864
2017-06-16 12:00 | 866 | 865
2017-06-16 12:30 | 862 | 861
2017-06-16 13:00 | 847 | 845
2017-06-16 13:30 | 839 | 837
2017-06-16 14:00 | 847 | 845
2017-06-16 14:30 | 871 | 870
2017-06-16 15:00 | 874 | 873
2017-06-16 15:30 | 869 | 867
2017-06-16 16:00 | 900 | 898
2017-06-16 16:30 | 908 | 907
2017-06-16 17:00 | 917 | 917
2017-06-16 17:30 | 956 | 956
2017-06-16 18:00 | 963 | 962
2017-06-16 18:30 | 949 | 947
2017-06-16 19:00 | 944 | 940
2017-06-16 19:30 | 929 | 924
2017-06-16 20:00 | 910 | 904
2017-06-16 20:30 | 900 | 898
2017-06-16 21:00 | 872 | 871
2017-06-16 21:30 | 842 | 840
2017-06-16 22:00 | 815 | 813
2017-06-16 22:30 | 797 | 796
2017-06-16 23:00 | 789 | 789
2017-06-16 23:30 | 757 | 755
2017-06-17 | 702 | 700
2017-06-17 00:30 | 650 | 645
2017-06-17 01:00 | 629 | 622
2017-06-17 01:30 | 603 | 594
2017-06-17 02:00 | 584 | 573
2017-06-17 02:30 | 573 | 561
2017-06-17 03:00 | 564 | 552
2017-06-17 03:30 | 563 | 552
2017-06-17 04:00 | 572 | 563
2017-06-17 04:30 | 562 | 552
2017-06-17 05:00 | 568 | 558
2017-06-17 05:30 | 582 | 574
2017-06-17 06:00 | 598 | 592
2017-06-17 06:30 | 620 | 615
2017-06-17 07:00 | 638 | 635
2017-06-17 07:30 | 679 | 677
2017-06-17 08:00 | 713 | 712
2017-06-17 08:30 | 745 | 745
2017-06-17 09:00 | 761 | 761
2017-06-17 09:30 | 758 | 757
2017-06-17 10:00 | 732 | 732
2017-06-17 10:30 | 738 | 738
2017-06-17 11:00 | 724 | 724
2017-06-17 11:30 | 727 | 727
2017-06-17 12:00 | 721 | 721
2017-06-17 12:30 | 710 | 710
2017-06-17 13:00 | 715 | 715
2017-06-17 13:30 | 711 | 711
2017-06-17 14:00 | 722 | 722
2017-06-17 14:30 | 731 | 731
2017-06-17 15:00 | 742 | 742
2017-06-17 15:30 | 744 | 744
2017-06-17 16:00 | 755 | 755
2017-06-17 16:30 | 782 | 782
2017-06-17 17:00 | 840 | 840
2017-06-17 17:30 | 904 | 904
2017-06-17 18:00 | 925 | 924
2017-06-17 18:30 | 917 | 915
2017-06-17 19:00 | 898 | 894
2017-06-17 19:30 | 861 | 856
2017-06-17 20:00 | 835 | 834
2017-06-17 20:30 | 828 | 827
2017-06-17 21:00 | 783 | 782
2017-06-17 21:30 | 768 | 768
2017-06-17 22:00 | 751 | 751
2017-06-17 22:30 | 749 | 748
2017-06-17 23:00 | 747 | 745
2017-06-17 23:30 | 717 | 715
2017-06-18 | 683 | 678
2017-06-18 00:30 | 635 | 625
2017-06-18 01:00 | 609 | 597
2017-06-18 01:30 | 586 | 572
2017-06-18 02:00 | 562 | 548
2017-06-18 02:30 | 556 | 540
2017-06-18 03:00 | 553 | 534
2017-06-18 03:30 | 543 | 523
2017-06-18 04:00 | 532 | 512
2017-06-18 04:30 | 537 | 518
2017-06-18 05:00 | 547 | 530
2017-06-18 05:30 | 559 | 543
2017-06-18 06:00 | 577 | 563
2017-06-18 06:30 | 592 | 579
2017-06-18 07:00 | 610 | 597
2017-06-18 07:30 | 637 | 627
2017-06-18 08:00 | 653 | 646
2017-06-18 08:30 | 669 | 665
2017-06-18 09:00 | 672 | 669
2017-06-18 09:30 | 674 | 672
2017-06-18 10:00 | 664 | 662
2017-06-18 10:30 | 654 | 652
2017-06-18 11:00 | 636 | 634
2017-06-18 11:30 | 617 | 615
2017-06-18 12:00 | 613 | 611
2017-06-18 12:30 | 610 | 607
2017-06-18 13:00 | 615 | 613
2017-06-18 13:30 | 623 | 621
2017-06-18 14:00 | 634 | 632
2017-06-18 14:30 | 645 | 644
2017-06-18 15:00 | 663 | 661
2017-06-18 15:30 | 688 | 687
2017-06-18 16:00 | 720 | 719
2017-06-18 16:30 | 757 | 756
2017-06-18 17:00 | 808 | 807
2017-06-18 17:30 | 874 | 872
2017-06-18 18:00 | 903 | 899
2017-06-18 18:30 | 899 | 895
2017-06-18 19:00 | 891 | 884
2017-06-18 19:30 | 876 | 868
2017-06-18 20:00 | 855 | 850
2017-06-18 20:30 | 849 | 845
2017-06-18 21:00 | 810 | 807
2017-06-18 21:30 | 776 | 776
2017-06-18 22:00 | 757 | 756
2017-06-18 22:30 | 745 | 744
2017-06-18 23:00 | 746 | 744
2017-06-18 23:30 | 707 | 704
2017-06-19 | 672 | 665
2017-06-19 00:30 | 627 | 616
2017-06-19 01:00 | 600 | 586
2017-06-19 01:30 | 580 | 565
2017-06-19 02:00 | 567 | 549
2017-06-19 02:30 | 558 | 540
2017-06-19 03:00 | 555 | 537
2017-06-19 03:30 | 558 | 541
2017-06-19 04:00 | 565 | 551
2017-06-19 04:30 | 578 | 565
2017-06-19 05:00 | 593 | 583
2017-06-19 05:30 | 623 | 617
2017-06-19 06:00 | 669 | 666
2017-06-19 06:30 | 747 | 746
2017-06-19 07:00 | 819 | 814
2017-06-19 07:30 | 869 | 865
2017-06-19 08:00 | 877 | 876
2017-06-19 08:30 | 869 | 868
2017-06-19 09:00 | 843 | 841
2017-06-19 09:30 | 818 | 816
2017-06-19 10:00 | 799 | 797
2017-06-19 10:30 | 783 | 781
2017-06-19 11:00 | 780 | 778
2017-06-19 11:30 | 799 | 798
2017-06-19 12:00 | 827 | 827
2017-06-19 12:30 | 839 | 839
2017-06-19 13:00 | 835 | 834
2017-06-19 13:30 | 821 | 820
2017-06-19 14:00 | 817 | 816
2017-06-19 14:30 | 819 | 818
2017-06-19 15:00 | 829 | 828
2017-06-19 15:30 | 854 | 853
2017-06-19 16:00 | 875 | 874
2017-06-19 16:30 | 909 | 908
2017-06-19 17:00 | 960 | 956
2017-06-19 17:30 | 1015 | 1014
2017-06-19 18:00 | 1036 | 1034
2017-06-19 18:30 | 1015 | 1011
2017-06-19 19:00 | 993 | 989
2017-06-19 19:30 | 963 | 959
2017-06-19 20:00 | 940 | 939
2017-06-19 20:30 | 928 | 927
2017-06-19 21:00 | 892 | 890
2017-06-19 21:30 | 854 | 852
2017-06-19 22:00 | 814 | 812
2017-06-19 22:30 | 796 | 793
2017-06-19 23:00 | 790 | 787
2017-06-19 23:30 | 744 | 741
2017-06-20 | 697 | 692
2017-06-20 00:30 | 645 | 639
2017-06-20 01:00 | 617 | 608
2017-06-20 01:30 | 596 | 586
2017-06-20 02:00 | 580 | 568
2017-06-20 02:30 | 574 | 561
2017-06-20 03:00 | 566 | 552
2017-06-20 03:30 | 567 | 552
2017-06-20 04:00 | 572 | 559
2017-06-20 04:30 | 580 | 569
2017-06-20 05:00 | 595 | 585
2017-06-20 05:30 | 634 | 628
2017-06-20 06:00 | 683 | 678
2017-06-20 06:30 | 765 | 759
2017-06-20 07:00 | 827 | 822
2017-06-20 07:30 | 876 | 874
2017-06-20 08:00 | 883 | 882
2017-06-20 08:30 | 899 | 898
2017-06-20 09:00 | 888 | 887
2017-06-20 09:30 | 868 | 867
2017-06-20 10:00 | 847 | 845
2017-06-20 10:30 | 821 | 819
2017-06-20 11:00 | 819 | 818
2017-06-20 11:30 | 804 | 802
2017-06-20 12:00 | 807 | 805
2017-06-20 12:30 | 794 | 792
2017-06-20 13:00 | 794 | 792
2017-06-20 13:30 | 806 | 804
2017-06-20 14:00 | 829 | 828
2017-06-20 14:30 | 826 | 825
2017-06-20 15:00 | 844 | 843
2017-06-20 15:30 | 851 | 850
2017-06-20 16:00 | 878 | 877
2017-06-20 16:30 | 915 | 914
2017-06-20 17:00 | 946 | 946
2017-06-20 17:30 | 994 | 994
2017-06-20 18:00 | 1017 | 1015
2017-06-20 18:30 | 1001 | 997
2017-06-20 19:00 | 992 | 986
2017-06-20 19:30 | 967 | 962
2017-06-20 20:00 | 947 | 946
2017-06-20 20:30 | 940 | 939
2017-06-20 21:00 | 899 | 897
2017-06-20 21:30 | 854 | 848
2017-06-20 22:00 | 826 | 818
2017-06-20 22:30 | 800 | 797
2017-06-20 23:00 | 793 | 791
2017-06-20 23:30 | 755 | 752
2017-06-21 | 708 | 704
2017-06-21 00:30 | 660 | 653
2017-06-21 01:00 | 631 | 621
2017-06-21 01:30 | 609 | 598
2017-06-21 02:00 | 612 | 601
2017-06-21 02:30 | 628 | 619
2017-06-21 03:00 | 621 | 612
2017-06-21 03:30 | 627 | 619
2017-06-21 04:00 | 634 | 626
2017-06-21 04:30 | 648 | 642
2017-06-21 05:00 | 631 | 624
2017-06-21 05:30 | 652 | 646
2017-06-21 06:00 | 701 | 697
2017-06-21 06:30 | 776 | 774
2017-06-21 07:00 | 847 | 844
2017-06-21 07:30 | 895 | 893
2017-06-21 08:00 | 897 | 894
2017-06-21 08:30 | 876 | 872
2017-06-21 09:00 | 841 | 836
2017-06-21 09:30 | 820 | 815
2017-06-21 10:00 | 796 | 791
2017-06-21 10:30 | 782 | 777
2017-06-21 11:00 | 769 | 764
2017-06-21 11:30 | 760 | 755
2017-06-21 12:00 | 763 | 757
2017-06-21 12:30 | 774 | 769
2017-06-21 13:00 | 764 | 758
2017-06-21 13:30 | 783 | 778
2017-06-21 14:00 | 784 | 778
2017-06-21 14:30 | 792 | 788
2017-06-21 15:00 | 809 | 805
2017-06-21 15:30 | 828 | 824
2017-06-21 16:00 | 856 | 852
2017-06-21 16:30 | 885 | 882
2017-06-21 17:00 | 922 | 919
2017-06-21 17:30 | 978 | 977
2017-06-21 18:00 | 996 | 993
2017-06-21 18:30 | 986 | 980
2017-06-21 19:00 | 980 | 972
2017-06-21 19:30 | 960 | 951
2017-06-21 20:00 | 948 | 941
2017-06-21 20:30 | 936 | 928
2017-06-21 21:00 | 896 | 889
2017-06-21 21:30 | 850 | 848
2017-06-21 22:00 | 822 | 817
2017-06-21 22:30 | 809 | 802
2017-06-21 23:00 | 804 | 797
2017-06-21 23:30 | 751 | 748
2017-06-22 | 703 | 698
2017-06-22 00:30 | 645 | 638
2017-06-22 01:00 | 624 | 617
2017-06-22 01:30 | 629 | 622
2017-06-22 02:00 | 611 | 602
2017-06-22 02:30 | 595 | 585
2017-06-22 03:00 | 581 | 569
2017-06-22 03:30 | 578 | 567
2017-06-22 04:00 | 581 | 570
2017-06-22 04:30 | 584 | 573
2017-06-22 05:00 | 601 | 593
2017-06-22 05:30 | 646 | 641
2017-06-22 06:00 | 686 | 684
2017-06-22 06:30 | 759 | 758
2017-06-22 07:00 | 819 | 817
2017-06-22 07:30 | 889 | 888
2017-06-22 08:00 | 920 | 919
2017-06-22 08:30 | 906 | 905
2017-06-22 09:00 | 876 | 875
2017-06-22 09:30 | 844 | 842
2017-06-22 10:00 | 806 | 806
2017-06-22 10:30 | 784 | 784
2017-06-22 11:00 | 767 | 767
2017-06-22 11:30 | 758 | 758
2017-06-22 12:00 | 764 | 764
2017-06-22 12:30 | 759 | 759
2017-06-22 13:00 | 750 | 750
2017-06-22 13:30 | 755 | 755
2017-06-22 14:00 | 767 | 767
2017-06-22 14:30 | 777 | 777
2017-06-22 15:00 | 784 | 784
2017-06-22 15:30 | 802 | 802
2017-06-22 16:00 | 825 | 825
2017-06-22 16:30 | 860 | 860
2017-06-22 17:00 | 902 | 901
2017-06-22 17:30 | 951 | 951
2017-06-22 18:00 | 983 | 983
2017-06-22 18:30 | 982 | 982
2017-06-22 19:00 | 983 | 983
2017-06-22 19:30 | 973 | 972
2017-06-22 20:00 | 965 | 963
2017-06-22 20:30 | 961 | 959
2017-06-22 21:00 | 933 | 929
2017-06-22 21:30 | 884 | 882
2017-06-22 22:00 | 854 | 849
2017-06-22 22:30 | 837 | 830
2017-06-22 23:00 | 818 | 816
2017-06-22 23:30 | 769 | 764
2017-06-23 | 719 | 709
2017-06-23 00:30 | 666 | 657
2017-06-23 01:00 | 634 | 622
2017-06-23 01:30 | 614 | 600
2017-06-23 02:00 | 599 | 581
2017-06-23 02:30 | 589 | 569
2017-06-23 03:00 | 589 | 568
2017-06-23 03:30 | 582 | 562
2017-06-23 04:00 | 588 | 569
2017-06-23 04:30 | 597 | 583
2017-06-23 05:00 | 611 | 601
2017-06-23 05:30 | 657 | 652
2017-06-23 06:00 | 706 | 705
2017-06-23 06:30 | 789 | 785
2017-06-23 07:00 | 854 | 852
2017-06-23 07:30 | 907 | 906
2017-06-23 08:00 | 911 | 911
2017-06-23 08:30 | 875 | 875
2017-06-23 09:00 | 844 | 844
2017-06-23 09:30 | 817 | 816
2017-06-23 10:00 | 789 | 788
2017-06-23 10:30 | 764 | 763
2017-06-23 11:00 | 742 | 742
2017-06-23 11:30 | 723 | 723
2017-06-23 12:00 | 717 | 717
2017-06-23 12:30 | 720 | 720
2017-06-23 13:00 | 719 | 718
2017-06-23 13:30 | 731 | 730
2017-06-23 14:00 | 743 | 742
2017-06-23 14:30 | 751 | 751
2017-06-23 15:00 | 770 | 769
2017-06-23 15:30 | 788 | 788
2017-06-23 16:00 | 818 | 817
2017-06-23 16:30 | 848 | 848
2017-06-23 17:00 | 882 | 882
2017-06-23 17:30 | 923 | 922
2017-06-23 18:00 | 949 | 947
2017-06-23 18:30 | 936 | 932
2017-06-23 19:00 | 940 | 935
2017-06-23 19:30 | 927 | 925
2017-06-23 20:00 | 921 | 919
2017-06-23 20:30 | 916 | 913
2017-06-23 21:00 | 881 | 876
2017-06-23 21:30 | 845 | 844
2017-06-23 22:00 | 827 | 826
2017-06-23 22:30 | 811 | 809
2017-06-23 23:00 | 809 | 806
2017-06-23 23:30 | 766 | 760
2017-06-24 | 722 | 713
2017-06-24 00:30 | 669 | 656
2017-06-24 01:00 | 648 | 632
2017-06-24 01:30 | 625 | 604
2017-06-24 02:00 | 600 | 580
2017-06-24 02:30 | 592 | 571
2017-06-24 03:00 | 586 | 564
2017-06-24 03:30 | 582 | 560
2017-06-24 04:00 | 580 | 558
2017-06-24 04:30 | 584 | 563
2017-06-24 05:00 | 592 | 573
2017-06-24 05:30 | 606 | 590
2017-06-24 06:00 | 622 | 609
2017-06-24 06:30 | 653 | 644
2017-06-24 07:00 | 682 | 673
2017-06-24 07:30 | 722 | 718
2017-06-24 08:00 | 754 | 753
2017-06-24 08:30 | 765 | 764
2017-06-24 09:00 | 763 | 763
2017-06-24 09:30 | 743 | 742
2017-06-24 10:00 | 719 | 718
2017-06-24 10:30 | 695 | 694
2017-06-24 11:00 | 668 | 667
2017-06-24 11:30 | 652 | 650
2017-06-24 12:00 | 638 | 636
2017-06-24 12:30 | 635 | 632
2017-06-24 13:00 | 638 | 635
2017-06-24 13:30 | 639 | 636
2017-06-24 14:00 | 642 | 640
2017-06-24 14:30 | 652 | 650
2017-06-24 15:00 | 676 | 675
2017-06-24 15:30 | 696 | 695
2017-06-24 16:00 | 727 | 726
2017-06-24 16:30 | 758 | 757
2017-06-24 17:00 | 802 | 802
2017-06-24 17:30 | 844 | 844
2017-06-24 18:00 | 871 | 870
2017-06-24 18:30 | 871 | 871
2017-06-24 19:00 | 877 | 874
2017-06-24 19:30 | 858 | 853
2017-06-24 20:00 | 857 | 850
2017-06-24 20:30 | 841 | 835
2017-06-24 21:00 | 801 | 800
2017-06-24 21:30 | 776 | 775
2017-06-24 22:00 | 765 | 764
2017-06-24 22:30 | 764 | 762
2017-06-24 23:00 | 767 | 765
2017-06-24 23:30 | 738 | 734
2017-06-25 | 697 | 690
2017-06-25 00:30 | 644 | 634
2017-06-25 01:00 | 609 | 594
2017-06-25 01:30 | 589 | 572
2017-06-25 02:00 | 575 | 554
2017-06-25 02:30 | 559 | 535
2017-06-25 03:00 | 549 | 524
2017-06-25 03:30 | 544 | 517
2017-06-25 04:00 | 535 | 508
2017-06-25 04:30 | 537 | 510
2017-06-25 05:00 | 549 | 523
2017-06-25 05:30 | 559 | 535
2017-06-25 06:00 | 576 | 556
2017-06-25 06:30 | 600 | 584
2017-06-25 07:00 | 627 | 612
2017-06-25 07:30 | 672 | 662
2017-06-25 08:00 | 688 | 680
2017-06-25 08:30 | 698 | 693
2017-06-25 09:00 | 701 | 698
2017-06-25 09:30 | 695 | 692
2017-06-25 10:00 | 687 | 684
2017-06-25 10:30 | 662 | 659
2017-06-25 11:00 | 626 | 622
2017-06-25 11:30 | 600 | 595
2017-06-25 12:00 | 587 | 583
2017-06-25 12:30 | 589 | 584
2017-06-25 13:00 | 592 | 587
2017-06-25 13:30 | 595 | 590
2017-06-25 14:00 | 602 | 598
2017-06-25 14:30 | 615 | 610
2017-06-25 15:00 | 635 | 632
2017-06-25 15:30 | 672 | 670
2017-06-25 16:00 | 716 | 715
2017-06-25 16:30 | 762 | 760
2017-06-25 17:00 | 819 | 816
2017-06-25 17:30 | 886 | 884
2017-06-25 18:00 | 926 | 925
2017-06-25 18:30 | 916 | 916
2017-06-25 19:00 | 910 | 910
2017-06-25 19:30 | 888 | 887
2017-06-25 20:00 | 878 | 875
2017-06-25 20:30 | 874 | 870
2017-06-25 21:00 | 844 | 839
2017-06-25 21:30 | 811 | 805
2017-06-25 22:00 | 786 | 780
2017-06-25 22:30 | 778 | 772
2017-06-25 23:00 | 761 | 758
2017-06-25 23:30 | 723 | 718
2017-06-26 | 683 | 674
2017-06-26 00:30 | 626 | 612
2017-06-26 01:00 | 591 | 575
2017-06-26 01:30 | 569 | 549
2017-06-26 02:00 | 551 | 528
2017-06-26 02:30 | 539 | 513
2017-06-26 03:00 | 532 | 505
2017-06-26 03:30 | 530 | 504
2017-06-26 04:00 | 525 | 499
2017-06-26 04:30 | 542 | 519
2017-06-26 05:00 | 566 | 548
2017-06-26 05:30 | 619 | 609
2017-06-26 06:00 | 678 | 671
2017-06-26 06:30 | 756 | 754
2017-06-26 07:00 | 805 | 804
2017-06-26 07:30 | 875 | 875
2017-06-26 08:00 | 887 | 887
2017-06-26 08:30 | 872 | 872
2017-06-26 09:00 | 848 | 848
2017-06-26 09:30 | 819 | 819
2017-06-26 10:00 | 789 | 789
2017-06-26 10:30 | 767 | 766
2017-06-26 11:00 | 740 | 739
2017-06-26 11:30 | 710 | 709
2017-06-26 12:00 | 700 | 700
2017-06-26 12:30 | 708 | 708
2017-06-26 13:00 | 734 | 734
2017-06-26 13:30 | 745 | 744
2017-06-26 14:00 | 757 | 756
2017-06-26 14:30 | 774 | 773
2017-06-26 15:00 | 802 | 801
2017-06-26 15:30 | 831 | 830
2017-06-26 16:00 | 846 | 845
2017-06-26 16:30 | 874 | 873
2017-06-26 17:00 | 915 | 914
2017-06-26 17:30 | 964 | 962
2017-06-26 18:00 | 995 | 993
2017-06-26 18:30 | 982 | 977
2017-06-26 19:00 | 973 | 966
2017-06-26 19:30 | 952 | 948
2017-06-26 20:00 | 942 | 939
2017-06-26 20:30 | 933 | 930
2017-06-26 21:00 | 890 | 887
2017-06-26 21:30 | 842 | 841
2017-06-26 22:00 | 814 | 813
2017-06-26 22:30 | 793 | 792
2017-06-26 23:00 | 787 | 784
2017-06-26 23:30 | 742 | 738
2017-06-27 | 697 | 692
2017-06-27 00:30 | 645 | 637
2017-06-27 01:00 | 619 | 608
2017-06-27 01:30 | 599 | 587
2017-06-27 02:00 | 582 | 568
2017-06-27 02:30 | 576 | 560
2017-06-27 03:00 | 574 | 557
2017-06-27 03:30 | 569 | 552
2017-06-27 04:00 | 577 | 561
2017-06-27 04:30 | 589 | 575
2017-06-27 05:00 | 608 | 597
2017-06-27 05:30 | 641 | 635
2017-06-27 06:00 | 687 | 683
2017-06-27 06:30 | 764 | 760
2017-06-27 07:00 | 818 | 814
2017-06-27 07:30 | 852 | 842
2017-06-27 08:00 | 849 | 840
2017-06-27 08:30 | 856 | 851
2017-06-27 09:00 | 859 | 853
2017-06-27 09:30 | 840 | 832
2017-06-27 10:00 | 823 | 815
2017-06-27 10:30 | 796 | 786
2017-06-27 11:00 | 784 | 778
2017-06-27 11:30 | 777 | 771
2017-06-27 12:00 | 768 | 763
2017-06-27 12:30 | 793 | 789
2017-06-27 13:00 | 806 | 803
2017-06-27 13:30 | 785 | 780
2017-06-27 14:00 | 805 | 801
2017-06-27 14:30 | 793 | 789
2017-06-27 15:00 | 791 | 787
2017-06-27 15:30 | 804 | 800
2017-06-27 16:00 | 827 | 823
2017-06-27 16:30 | 855 | 851
2017-06-27 17:00 | 916 | 911
2017-06-27 17:30 | 988 | 986
2017-06-27 18:00 | 1015 | 1011
2017-06-27 18:30 | 1002 | 995
2017-06-27 19:00 | 999 | 989
2017-06-27 19:30 | 980 | 970
2017-06-27 20:00 | 958 | 954
2017-06-27 20:30 | 951 | 947
2017-06-27 21:00 | 898 | 895
2017-06-27 21:30 | 862 | 857
2017-06-27 22:00 | 835 | 826
2017-06-27 22:30 | 803 | 801
2017-06-27 23:00 | 794 | 792
2017-06-27 23:30 | 750 | 746
2017-06-28 | 703 | 697
2017-06-28 00:30 | 648 | 639
2017-06-28 01:00 | 617 | 606
2017-06-28 01:30 | 598 | 585
2017-06-28 02:00 | 582 | 566
2017-06-28 02:30 | 575 | 557
2017-06-28 03:00 | 571 | 553
2017-06-28 03:30 | 573 | 555
2017-06-28 04:00 | 575 | 558
2017-06-28 04:30 | 584 | 569
2017-06-28 05:00 | 603 | 591
2017-06-28 05:30 | 635 | 628
2017-06-28 06:00 | 679 | 676
2017-06-28 06:30 | 754 | 752
2017-06-28 07:00 | 802 | 802
2017-06-28 07:30 | 846 | 846
2017-06-28 08:00 | 855 | 855
2017-06-28 08:30 | 845 | 845
2017-06-28 09:00 | 834 | 834
2017-06-28 09:30 | 803 | 803
2017-06-28 10:00 | 781 | 781
2017-06-28 10:30 | 766 | 766
2017-06-28 11:00 | 761 | 761
2017-06-28 11:30 | 761 | 761
2017-06-28 12:00 | 760 | 760
2017-06-28 12:30 | 756 | 756
2017-06-28 13:00 | 764 | 764
2017-06-28 13:30 | 776 | 776
2017-06-28 14:00 | 785 | 785
2017-06-28 14:30 | 796 | 796
2017-06-28 15:00 | 806 | 806
2017-06-28 15:30 | 825 | 825
2017-06-28 16:00 | 854 | 853
2017-06-28 16:30 | 889 | 887
2017-06-28 17:00 | 926 | 924
2017-06-28 17:30 | 984 | 982
2017-06-28 18:00 | 1007 | 1005
2017-06-28 18:30 | 969 | 964
2017-06-28 19:00 | 962 | 955
2017-06-28 19:30 | 946 | 937
2017-06-28 20:00 | 939 | 933
2017-06-28 20:30 | 923 | 919
2017-06-28 21:00 | 888 | 885
2017-06-28 21:30 | 847 | 841
2017-06-28 22:00 | 820 | 812
2017-06-28 22:30 | 796 | 793
2017-06-28 23:00 | 784 | 781
2017-06-28 23:30 | 743 | 741
2017-06-29 | 697 | 693
2017-06-29 00:30 | 650 | 642
2017-06-29 01:00 | 620 | 609
2017-06-29 01:30 | 601 | 587
2017-06-29 02:00 | 583 | 567
2017-06-29 02:30 | 578 | 561
2017-06-29 03:00 | 577 | 560
2017-06-29 03:30 | 575 | 558
2017-06-29 04:00 | 575 | 558
2017-06-29 04:30 | 585 | 571
2017-06-29 05:00 | 605 | 593
2017-06-29 05:30 | 641 | 634
2017-06-29 06:00 | 680 | 678
2017-06-29 06:30 | 751 | 750
2017-06-29 07:00 | 805 | 799
2017-06-29 07:30 | 843 | 837
2017-06-29 08:00 | 867 | 858
2017-06-29 08:30 | 872 | 865
2017-06-29 09:00 | 856 | 847
2017-06-29 09:30 | 833 | 822
2017-06-29 10:00 | 807 | 796
2017-06-29 10:30 | 797 | 785
2017-06-29 11:00 | 770 | 763
2017-06-29 11:30 | 759 | 753
2017-06-29 12:00 | 749 | 743
2017-06-29 12:30 | 747 | 743
2017-06-29 13:00 | 753 | 748
2017-06-29 13:30 | 761 | 757
2017-06-29 14:00 | 783 | 778
2017-06-29 14:30 | 790 | 787
2017-06-29 15:00 | 806 | 803
2017-06-29 15:30 | 819 | 816
2017-06-29 16:00 | 847 | 844
2017-06-29 16:30 | 866 | 863
2017-06-29 17:00 | 904 | 902
2017-06-29 17:30 | 953 | 950
2017-06-29 18:00 | 979 | 972
2017-06-29 18:30 | 972 | 962
2017-06-29 19:00 | 961 | 954
2017-06-29 19:30 | 939 | 936
2017-06-29 20:00 | 937 | 932
2017-06-29 20:30 | 929 | 924
2017-06-29 21:00 | 893 | 884
2017-06-29 21:30 | 847 | 841
2017-06-29 22:00 | 813 | 811
2017-06-29 22:30 | 800 | 798
2017-06-29 23:00 | 795 | 792
2017-06-29 23:30 | 751 | 745
2017-06-30 | 702 | 694
2017-06-30 00:30 | 650 | 642
2017-06-30 01:00 | 623 | 614
2017-06-30 01:30 | 598 | 586
2017-06-30 02:00 | 590 | 575
2017-06-30 02:30 | 575 | 560
2017-06-30 03:00 | 573 | 557
2017-06-30 03:30 | 572 | 555
2017-06-30 04:00 | 570 | 554
2017-06-30 04:30 | 581 | 566
2017-06-30 05:00 | 592 | 580
2017-06-30 05:30 | 627 | 619
2017-06-30 06:00 | 662 | 659
2017-06-30 06:30 | 727 | 724
2017-06-30 07:00 | 780 | 777
2017-06-30 07:30 | 840 | 834
2017-06-30 08:00 | 869 | 858
2017-06-30 08:30 | 888 | 881
2017-06-30 09:00 | 886 | 877
2017-06-30 09:30 | 860 | 850
2017-06-30 10:00 | 822 | 810
2017-06-30 10:30 | 810 | 797
2017-06-30 11:00 | 787 | 773
2017-06-30 11:30 | 774 | 763
2017-06-30 12:00 | 771 | 764
2017-06-30 12:30 | 769 | 762
2017-06-30 13:00 | 779 | 772
2017-06-30 13:30 | 777 | 770
2017-06-30 14:00 | 790 | 784
2017-06-30 14:30 | 796 | 790
2017-06-30 15:00 | 808 | 802
2017-06-30 15:30 | 802 | 797
2017-06-30 16:00 | 827 | 822
2017-06-30 16:30 | 851 | 847
2017-06-30 17:00 | 891 | 889
2017-06-30 17:30 | 923 | 922
2017-06-30 18:00 | 946 | 946
2017-06-30 18:30 | 941 | 940
2017-06-30 19:00 | 937 | 934
2017-06-30 19:30 | 931 | 925
2017-06-30 20:00 | 925 | 918
2017-06-30 20:30 | 920 | 913
2017-06-30 21:00 | 887 | 880
2017-06-30 21:30 | 850 | 844
2017-06-30 22:00 | 818 | 816
2017-06-30 22:30 | 810 | 808
2017-06-30 23:00 | 805 | 802
2017-06-30 23:30 | 758 | 755
2017-07-01 | 711 | 708
2017-07-01 00:30 | 656 | 649
2017-07-01 01:00 | 626 | 616
2017-07-01 01:30 | 602 | 592
2017-07-01 02:00 | 583 | 570
2017-07-01 02:30 | 578 | 562
2017-07-01 03:00 | 571 | 554
2017-07-01 03:30 | 570 | 553
2017-07-01 04:00 | 572 | 556
2017-07-01 04:30 | 573 | 557
2017-07-01 05:00 | 578 | 563
2017-07-01 05:30 | 600 | 588
2017-07-01 06:00 | 613 | 604
2017-07-01 06:30 | 647 | 642
2017-07-01 07:00 | 673 | 669
2017-07-01 07:30 | 724 | 720
2017-07-01 08:00 | 749 | 746
2017-07-01 08:30 | 764 | 762
2017-07-01 09:00 | 766 | 762
2017-07-01 09:30 | 747 | 742
2017-07-01 10:00 | 720 | 713
2017-07-01 10:30 | 698 | 689
2017-07-01 11:00 | 673 | 665
2017-07-01 11:30 | 641 | 639
2017-07-01 12:00 | 647 | 646
2017-07-01 12:30 | 654 | 653
2017-07-01 13:00 | 659 | 658
2017-07-01 13:30 | 661 | 660
2017-07-01 14:00 | 674 | 673
2017-07-01 14:30 | 689 | 689
2017-07-01 15:00 | 682 | 681
2017-07-01 15:30 | 681 | 679
2017-07-01 16:00 | 719 | 718
2017-07-01 16:30 | 758 | 758
2017-07-01 17:00 | 827 | 826
2017-07-01 17:30 | 892 | 889
2017-07-01 18:00 | 927 | 924
2017-07-01 18:30 | 936 | 932
2017-07-01 19:00 | 937 | 932
2017-07-01 19:30 | 930 | 926
2017-07-01 20:00 | 928 | 925
2017-07-01 20:30 | 927 | 925
2017-07-01 21:00 | 893 | 889
2017-07-01 21:30 | 867 | 864
2017-07-01 22:00 | 835 | 830
2017-07-01 22:30 | 828 | 820
2017-07-01 23:00 | 820 | 812
2017-07-01 23:30 | 781 | 771
2017-07-02 | 745 | 728
2017-07-02 00:30 | 684 | 674
2017-07-02 01:00 | 648 | 638
2017-07-02 01:30 | 618 | 604
2017-07-02 02:00 | 598 | 582
2017-07-02 02:30 | 588 | 571
2017-07-02 03:00 | 579 | 561
2017-07-02 03:30 | 578 | 561
2017-07-02 04:00 | 575 | 558
2017-07-02 04:30 | 573 | 557
2017-07-02 05:00 | 580 | 566
2017-07-02 05:30 | 587 | 574
2017-07-02 06:00 | 601 | 590
2017-07-02 06:30 | 628 | 621
2017-07-02 07:00 | 655 | 649
2017-07-02 07:30 | 697 | 693
2017-07-02 08:00 | 728 | 723
2017-07-02 08:30 | 782 | 781
2017-07-02 09:00 | 760 | 759
2017-07-02 09:30 | 736 | 734
2017-07-02 10:00 | 716 | 713
2017-07-02 10:30 | 682 | 680
2017-07-02 11:00 | 655 | 654
2017-07-02 11:30 | 624 | 621
2017-07-02 12:00 | 611 | 608
2017-07-02 12:30 | 596 | 592
2017-07-02 13:00 | 601 | 597
2017-07-02 13:30 | 604 | 600
2017-07-02 14:00 | 634 | 631
2017-07-02 14:30 | 661 | 660
2017-07-02 15:00 | 658 | 656
2017-07-02 15:30 | 672 | 671
2017-07-02 16:00 | 708 | 708
2017-07-02 16:30 | 750 | 750
2017-07-02 17:00 | 811 | 811
2017-07-02 17:30 | 877 | 875
2017-07-02 18:00 | 914 | 914
2017-07-02 18:30 | 926 | 926
2017-07-02 19:00 | 927 | 926
2017-07-02 19:30 | 913 | 911
2017-07-02 20:00 | 903 | 902
2017-07-02 20:30 | 899 | 898
2017-07-02 21:00 | 864 | 861
2017-07-02 21:30 | 838 | 833
2017-07-02 22:00 | 817 | 809
2017-07-02 22:30 | 795 | 789
2017-07-02 23:00 | 788 | 782
2017-07-02 23:30 | 746 | 740
2017-07-03 | 698 | 693
2017-07-03 00:30 | 653 | 645
2017-07-03 01:00 | 628 | 617
2017-07-03 01:30 | 608 | 595
2017-07-03 02:00 | 594 | 580
2017-07-03 02:30 | 606 | 596
2017-07-03 03:00 | 620 | 611
2017-07-03 03:30 | 620 | 612
2017-07-03 04:00 | 623 | 615
2017-07-03 04:30 | 634 | 628
2017-07-03 05:00 | 652 | 649
2017-07-03 05:30 | 661 | 659
2017-07-03 06:00 | 707 | 706
2017-07-03 06:30 | 788 | 788
2017-07-03 07:00 | 858 | 858
2017-07-03 07:30 | 926 | 925
2017-07-03 08:00 | 944 | 944
2017-07-03 08:30 | 940 | 940
2017-07-03 09:00 | 941 | 941
2017-07-03 09:30 | 914 | 914
2017-07-03 10:00 | 888 | 888
2017-07-03 10:30 | 851 | 850
2017-07-03 11:00 | 809 | 807
2017-07-03 11:30 | 793 | 793
2017-07-03 12:00 | 798 | 797
2017-07-03 12:30 | 801 | 800
2017-07-03 13:00 | 813 | 812
2017-07-03 13:30 | 843 | 843
2017-07-03 14:00 | 862 | 862
2017-07-03 14:30 | 873 | 871
2017-07-03 15:00 | 849 | 846
2017-07-03 15:30 | 838 | 837
2017-07-03 16:00 | 848 | 847
2017-07-03 16:30 | 893 | 893
2017-07-03 17:00 | 957 | 957
2017-07-03 17:30 | 1013 | 1013
2017-07-03 18:00 | 1048 | 1048
2017-07-03 18:30 | 1033 | 1030
2017-07-03 19:00 | 1028 | 1025
2017-07-03 19:30 | 1008 | 1006
2017-07-03 20:00 | 998 | 996
2017-07-03 20:30 | 986 | 984
2017-07-03 21:00 | 945 | 941
2017-07-03 21:30 | 894 | 887
2017-07-03 22:00 | 853 | 849
2017-07-03 22:30 | 823 | 818
2017-07-03 23:00 | 812 | 806
2017-07-03 23:30 | 757 | 752
2017-07-04 | 712 | 708
2017-07-04 00:30 | 659 | 652
2017-07-04 01:00 | 630 | 619
2017-07-04 01:30 | 602 | 588
2017-07-04 02:00 | 587 | 570
2017-07-04 02:30 | 578 | 558
2017-07-04 03:00 | 573 | 553
2017-07-04 03:30 | 578 | 558
2017-07-04 04:00 | 576 | 558
2017-07-04 04:30 | 588 | 573
2017-07-04 05:00 | 602 | 592
2017-07-04 05:30 | 637 | 631
2017-07-04 06:00 | 686 | 684
2017-07-04 06:30 | 752 | 751
2017-07-04 07:00 | 811 | 808
2017-07-04 07:30 | 863 | 860
2017-07-04 08:00 | 880 | 877
2017-07-04 08:30 | 869 | 868
2017-07-04 09:00 | 828 | 827
2017-07-04 09:30 | 800 | 799
2017-07-04 10:00 | 776 | 774
2017-07-04 10:30 | 756 | 753
2017-07-04 11:00 | 731 | 731
2017-07-04 11:30 | 723 | 722
2017-07-04 12:00 | 716 | 716
2017-07-04 12:30 | 721 | 721
2017-07-04 13:00 | 727 | 727
2017-07-04 13:30 | 728 | 728
2017-07-04 14:00 | 746 | 746
2017-07-04 14:30 | 758 | 758
2017-07-04 15:00 | 783 | 782
2017-07-04 15:30 | 799 | 799
2017-07-04 16:00 | 830 | 830
2017-07-04 16:30 | 852 | 852
2017-07-04 17:00 | 891 | 891
2017-07-04 17:30 | 950 | 950
2017-07-04 18:00 | 982 | 982
2017-07-04 18:30 | 967 | 966
2017-07-04 19:00 | 964 | 962
2017-07-04 19:30 | 943 | 940
2017-07-04 20:00 | 923 | 920
2017-07-04 20:30 | 904 | 901
2017-07-04 21:00 | 874 | 869
2017-07-04 21:30 | 841 | 835
2017-07-04 22:00 | 808 | 805
2017-07-04 22:30 | 795 | 790
2017-07-04 23:00 | 789 | 785
2017-07-04 23:30 | 745 | 739
2017-07-05 | 700 | 692
2017-07-05 00:30 | 646 | 639
2017-07-05 01:00 | 614 | 605
2017-07-05 01:30 | 598 | 587
2017-07-05 02:00 | 586 | 572
2017-07-05 02:30 | 572 | 556
2017-07-05 03:00 | 592 | 580
2017-07-05 03:30 | 572 | 556
2017-07-05 04:00 | 572 | 558
2017-07-05 04:30 | 583 | 571
2017-07-05 05:00 | 602 | 592
2017-07-05 05:30 | 641 | 635
2017-07-05 06:00 | 685 | 683
2017-07-05 06:30 | 761 | 761
2017-07-05 07:00 | 817 | 816
2017-07-05 07:30 | 867 | 867
2017-07-05 08:00 | 877 | 876
2017-07-05 08:30 | 843 | 842
2017-07-05 09:00 | 811 | 810
2017-07-05 09:30 | 787 | 785
2017-07-05 10:00 | 762 | 760
2017-07-05 10:30 | 744 | 742
2017-07-05 11:00 | 727 | 726
2017-07-05 11:30 | 716 | 715
2017-07-05 12:00 | 699 | 698
2017-07-05 12:30 | 695 | 694
2017-07-05 13:00 | 704 | 703
2017-07-05 13:30 | 714 | 712
2017-07-05 14:00 | 730 | 728
2017-07-05 14:30 | 736 | 735
2017-07-05 15:00 | 758 | 757
2017-07-05 15:30 | 786 | 785
2017-07-05 16:00 | 824 | 823
2017-07-05 16:30 | 863 | 862
2017-07-05 17:00 | 923 | 923
2017-07-05 17:30 | 966 | 965
2017-07-05 18:00 | 975 | 975
2017-07-05 18:30 | 959 | 957
2017-07-05 19:00 | 956 | 954
2017-07-05 19:30 | 944 | 941
2017-07-05 20:00 | 920 | 919
2017-07-05 20:30 | 913 | 911
2017-07-05 21:00 | 870 | 868
2017-07-05 21:30 | 837 | 833
2017-07-05 22:00 | 811 | 804
2017-07-05 22:30 | 792 | 787
2017-07-05 23:00 | 780 | 779
2017-07-05 23:30 | 744 | 743
2017-07-06 | 699 | 696
2017-07-06 00:30 | 652 | 647
2017-07-06 01:00 | 622 | 614
2017-07-06 01:30 | 605 | 595
2017-07-06 02:00 | 602 | 592
2017-07-06 02:30 | 615 | 608
2017-07-06 03:00 | 613 | 605
2017-07-06 03:30 | 616 | 608
2017-07-06 04:00 | 615 | 607
2017-07-06 04:30 | 627 | 621
2017-07-06 05:00 | 611 | 604
2017-07-06 05:30 | 640 | 636
2017-07-06 06:00 | 680 | 679
2017-07-06 06:30 | 745 | 740
2017-07-06 07:00 | 797 | 793
2017-07-06 07:30 | 851 | 850
2017-07-06 08:00 | 855 | 853
2017-07-06 08:30 | 854 | 853
2017-07-06 09:00 | 833 | 831
2017-07-06 09:30 | 804 | 801
2017-07-06 10:00 | 779 | 775
2017-07-06 10:30 | 754 | 750
2017-07-06 11:00 | 741 | 737
2017-07-06 11:30 | 728 | 725
2017-07-06 12:00 | 722 | 719
2017-07-06 12:30 | 721 | 718
2017-07-06 13:00 | 722 | 719
2017-07-06 13:30 | 728 | 725
2017-07-06 14:00 | 746 | 743
2017-07-06 14:30 | 765 | 763
2017-07-06 15:00 | 789 | 787
2017-07-06 15:30 | 809 | 807
2017-07-06 16:00 | 827 | 826
2017-07-06 16:30 | 855 | 853
2017-07-06 17:00 | 892 | 891
2017-07-06 17:30 | 933 | 933
2017-07-06 18:00 | 972 | 971
2017-07-06 18:30 | 973 | 971
2017-07-06 19:00 | 974 | 972
2017-07-06 19:30 | 951 | 948
2017-07-06 20:00 | 936 | 936
2017-07-06 20:30 | 929 | 928
2017-07-06 21:00 | 898 | 896
2017-07-06 21:30 | 864 | 859
2017-07-06 22:00 | 830 | 826
2017-07-06 22:30 | 808 | 804
2017-07-06 23:00 | 800 | 799
2017-07-06 23:30 | 760 | 758
2017-07-07 | 716 | 710
2017-07-07 00:30 | 659 | 649
2017-07-07 01:00 | 628 | 614
2017-07-07 01:30 | 606 | 589
2017-07-07 02:00 | 595 | 579
2017-07-07 02:30 | 577 | 563
2017-07-07 03:00 | 606 | 596
2017-07-07 03:30 | 607 | 598
2017-07-07 04:00 | 611 | 603
2017-07-07 04:30 | 615 | 608
2017-07-07 05:00 | 621 | 615
2017-07-07 05:30 | 631 | 627
2017-07-07 06:00 | 672 | 670
2017-07-07 06:30 | 741 | 740
2017-07-07 07:00 | 805 | 804
2017-07-07 07:30 | 873 | 873
2017-07-07 08:00 | 914 | 913
2017-07-07 08:30 | 920 | 920
2017-07-07 09:00 | 916 | 916
2017-07-07 09:30 | 925 | 925
2017-07-07 10:00 | 942 | 941
2017-07-07 10:30 | 926 | 926
2017-07-07 11:00 | 906 | 906
2017-07-07 11:30 | 899 | 899
2017-07-07 12:00 | 918 | 917
2017-07-07 12:30 | 917 | 917
2017-07-07 13:00 | 895 | 895
2017-07-07 13:30 | 879 | 879
2017-07-07 14:00 | 873 | 873
2017-07-07 14:30 | 865 | 865
2017-07-07 15:00 | 869 | 869
2017-07-07 15:30 | 869 | 868
2017-07-07 16:00 | 884 | 884
2017-07-07 16:30 | 893 | 893
2017-07-07 17:00 | 928 | 928
2017-07-07 17:30 | 970 | 970
2017-07-07 18:00 | 996 | 995
2017-07-07 18:30 | 981 | 976
2017-07-07 19:00 | 975 | 972
2017-07-07 19:30 | 964 | 960
2017-07-07 20:00 | 945 | 944
2017-07-07 20:30 | 934 | 934
2017-07-07 21:00 | 905 | 904
2017-07-07 21:30 | 859 | 858
2017-07-07 22:00 | 818 | 813
2017-07-07 22:30 | 793 | 790
2017-07-07 23:00 | 782 | 782
2017-07-07 23:30 | 737 | 736
2017-07-08 | 686 | 683
2017-07-08 00:30 | 626 | 621
2017-07-08 01:00 | 596 | 588
2017-07-08 01:30 | 572 | 562
2017-07-08 02:00 | 554 | 541
2017-07-08 02:30 | 543 | 528
2017-07-08 03:00 | 533 | 517
2017-07-08 03:30 | 532 | 515
2017-07-08 04:00 | 536 | 518
2017-07-08 04:30 | 536 | 517
2017-07-08 05:00 | 542 | 525
2017-07-08 05:30 | 562 | 548
2017-07-08 06:00 | 571 | 560
2017-07-08 06:30 | 601 | 595
2017-07-08 07:00 | 636 | 631
2017-07-08 07:30 | 675 | 673
2017-07-08 08:00 | 700 | 699
2017-07-08 08:30 | 722 | 722
2017-07-08 09:00 | 718 | 718
2017-07-08 09:30 | 705 | 705
2017-07-08 10:00 | 673 | 673
2017-07-08 10:30 | 669 | 669
2017-07-08 11:00 | 634 | 633
2017-07-08 11:30 | 603 | 601
2017-07-08 12:00 | 588 | 586
2017-07-08 12:30 | 575 | 572
2017-07-08 13:00 | 568 | 564
2017-07-08 13:30 | 570 | 567
2017-07-08 14:00 | 583 | 580
2017-07-08 14:30 | 594 | 592
2017-07-08 15:00 | 615 | 613
2017-07-08 15:30 | 637 | 635
2017-07-08 16:00 | 672 | 671
2017-07-08 16:30 | 709 | 709
2017-07-08 17:00 | 768 | 768
2017-07-08 17:30 | 823 | 823
2017-07-08 18:00 | 858 | 857
2017-07-08 18:30 | 868 | 867
2017-07-08 19:00 | 874 | 872
2017-07-08 19:30 | 861 | 858
2017-07-08 20:00 | 858 | 855
2017-07-08 20:30 | 851 | 850
2017-07-08 21:00 | 821 | 819
2017-07-08 21:30 | 798 | 796
2017-07-08 22:00 | 776 | 775
2017-07-08 22:30 | 772 | 771
2017-07-08 23:00 | 773 | 771
2017-07-08 23:30 | 729 | 727
2017-07-09 | 690 | 687
2017-07-09 00:30 | 639 | 632
2017-07-09 01:00 | 606 | 597
2017-07-09 01:30 | 583 | 571
2017-07-09 02:00 | 564 | 549
2017-07-09 02:30 | 552 | 536
2017-07-09 03:00 | 545 | 528
2017-07-09 03:30 | 542 | 523
2017-07-09 04:00 | 539 | 519
2017-07-09 04:30 | 536 | 517
2017-07-09 05:00 | 546 | 529
2017-07-09 05:30 | 559 | 543
2017-07-09 06:00 | 568 | 555
2017-07-09 06:30 | 595 | 585
2017-07-09 07:00 | 625 | 616
2017-07-09 07:30 | 665 | 661
2017-07-09 08:00 | 693 | 690
2017-07-09 08:30 | 703 | 701
2017-07-09 09:00 | 697 | 695
2017-07-09 09:30 | 690 | 689
2017-07-09 10:00 | 692 | 691
2017-07-09 10:30 | 665 | 663
2017-07-09 11:00 | 642 | 639
2017-07-09 11:30 | 607 | 602
2017-07-09 12:00 | 594 | 589
2017-07-09 12:30 | 586 | 580
2017-07-09 13:00 | 580 | 573
2017-07-09 13:30 | 588 | 582
2017-07-09 14:00 | 592 | 586
2017-07-09 14:30 | 609 | 604
2017-07-09 15:00 | 634 | 630
2017-07-09 15:30 | 659 | 656
2017-07-09 16:00 | 712 | 708
2017-07-09 16:30 | 754 | 752
2017-07-09 17:00 | 823 | 821
2017-07-09 17:30 | 871 | 869
2017-07-09 18:00 | 916 | 911
2017-07-09 18:30 | 922 | 918
2017-07-09 19:00 | 931 | 927
2017-07-09 19:30 | 917 | 911
2017-07-09 20:00 | 906 | 900
2017-07-09 20:30 | 903 | 896
2017-07-09 21:00 | 867 | 858
2017-07-09 21:30 | 829 | 825
2017-07-09 22:00 | 802 | 796
2017-07-09 22:30 | 778 | 775
2017-07-09 23:00 | 776 | 772
2017-07-09 23:30 | 738 | 735
2017-07-10 | 695 | 692
2017-07-10 00:30 | 652 | 646
2017-07-10 01:00 | 633 | 625
2017-07-10 01:30 | 644 | 638
2017-07-10 02:00 | 606 | 598
2017-07-10 02:30 | 578 | 565
2017-07-10 03:00 | 578 | 565
2017-07-10 03:30 | 568 | 554
2017-07-10 04:00 | 567 | 554
2017-07-10 04:30 | 598 | 589
2017-07-10 05:00 | 618 | 612
2017-07-10 05:30 | 641 | 637
2017-07-10 06:00 | 692 | 690
2017-07-10 06:30 | 781 | 781
2017-07-10 07:00 | 862 | 861
2017-07-10 07:30 | 942 | 940
2017-07-10 08:00 | 972 | 967
2017-07-10 08:30 | 947 | 941
2017-07-10 09:00 | 910 | 902
2017-07-10 09:30 | 892 | 888
2017-07-10 10:00 | 850 | 847
2017-07-10 10:30 | 846 | 844
2017-07-10 11:00 | 830 | 829
2017-07-10 11:30 | 781 | 779
2017-07-10 12:00 | 793 | 793
2017-07-10 12:30 | 777 | 776
2017-07-10 13:00 | 790 | 790
2017-07-10 13:30 | 779 | 778
2017-07-10 14:00 | 810 | 809
2017-07-10 14:30 | 820 | 820
2017-07-10 15:00 | 838 | 838
2017-07-10 15:30 | 852 | 851
2017-07-10 16:00 | 885 | 883
2017-07-10 16:30 | 923 | 921
2017-07-10 17:00 | 978 | 973
2017-07-10 17:30 | 1043 | 1040
2017-07-10 18:00 | 1073 | 1066
2017-07-10 18:30 | 1062 | 1054
2017-07-10 19:00 | 1059 | 1049
2017-07-10 19:30 | 1031 | 1024
2017-07-10 20:00 | 1018 | 1010
2017-07-10 20:30 | 1001 | 990
2017-07-10 21:00 | 944 | 936
2017-07-10 21:30 | 888 | 886
2017-07-10 22:00 | 856 | 852
2017-07-10 22:30 | 824 | 818
2017-07-10 23:00 | 805 | 801
2017-07-10 23:30 | 756 | 753
2017-07-11 | 711 | 708
2017-07-11 00:30 | 659 | 654
2017-07-11 01:00 | 667 | 663
2017-07-11 01:30 | 654 | 649
2017-07-11 02:00 | 637 | 630
2017-07-11 02:30 | 618 | 611
2017-07-11 03:00 | 608 | 599
2017-07-11 03:30 | 609 | 601
2017-07-11 04:00 | 612 | 603
2017-07-11 04:30 | 615 | 608
2017-07-11 05:00 | 636 | 631
2017-07-11 05:30 | 653 | 649
2017-07-11 06:00 | 701 | 699
2017-07-11 06:30 | 787 | 786
2017-07-11 07:00 | 860 | 860
2017-07-11 07:30 | 925 | 925
2017-07-11 08:00 | 941 | 940
2017-07-11 08:30 | 918 | 918
2017-07-11 09:00 | 867 | 867
2017-07-11 09:30 | 846 | 846
2017-07-11 10:00 | 802 | 802
2017-07-11 10:30 | 796 | 795
2017-07-11 11:00 | 818 | 818
2017-07-11 11:30 | 799 | 799
2017-07-11 12:00 | 792 | 792
2017-07-11 12:30 | 788 | 788
2017-07-11 13:00 | 792 | 792
2017-07-11 13:30 | 796 | 795
2017-07-11 14:00 | 812 | 812
2017-07-11 14:30 | 806 | 806
2017-07-11 15:00 | 841 | 841
2017-07-11 15:30 | 800 | 800
2017-07-11 16:00 | 821 | 817
2017-07-11 16:30 | 857 | 854
2017-07-11 17:00 | 906 | 904
2017-07-11 17:30 | 970 | 968
2017-07-11 18:00 | 1013 | 1012
2017-07-11 18:30 | 1007 | 1006
2017-07-11 19:00 | 1022 | 1019
2017-07-11 19:30 | 1004 | 1000
2017-07-11 20:00 | 988 | 983
2017-07-11 20:30 | 978 | 975
2017-07-11 21:00 | 939 | 937
2017-07-11 21:30 | 906 | 902
2017-07-11 22:00 | 872 | 865
2017-07-11 22:30 | 835 | 830
2017-07-11 23:00 | 820 | 819
2017-07-11 23:30 | 772 | 771
2017-07-12 | 729 | 725
2017-07-12 00:30 | 679 | 673
2017-07-12 01:00 | 674 | 669
2017-07-12 01:30 | 654 | 648
2017-07-12 02:00 | 644 | 638
2017-07-12 02:30 | 630 | 622
2017-07-12 03:00 | 623 | 615
2017-07-12 03:30 | 618 | 611
2017-07-12 04:00 | 617 | 608
2017-07-12 04:30 | 639 | 633
2017-07-12 05:00 | 659 | 655
2017-07-12 05:30 | 668 | 665
2017-07-12 06:00 | 716 | 715
2017-07-12 06:30 | 810 | 810
2017-07-12 07:00 | 901 | 901
2017-07-12 07:30 | 969 | 969
2017-07-12 08:00 | 971 | 971
2017-07-12 08:30 | 935 | 935
2017-07-12 09:00 | 910 | 910
2017-07-12 09:30 | 907 | 907
2017-07-12 10:00 | 859 | 859
2017-07-12 10:30 | 840 | 840
2017-07-12 11:00 | 819 | 819
2017-07-12 11:30 | 792 | 792
2017-07-12 12:00 | 778 | 778
2017-07-12 12:30 | 779 | 779
2017-07-12 13:00 | 792 | 792
2017-07-12 13:30 | 804 | 804
2017-07-12 14:00 | 818 | 818
2017-07-12 14:30 | 824 | 824
2017-07-12 15:00 | 829 | 828
2017-07-12 15:30 | 854 | 852
2017-07-12 16:00 | 892 | 891
2017-07-12 16:30 | 910 | 909
2017-07-12 17:00 | 935 | 934
2017-07-12 17:30 | 998 | 997
2017-07-12 18:00 | 1038 | 1037
2017-07-12 18:30 | 1045 | 1044
2017-07-12 19:00 | 1046 | 1044
2017-07-12 19:30 | 1030 | 1027
2017-07-12 20:00 | 1011 | 1009
2017-07-12 20:30 | 1002 | 1002
2017-07-12 21:00 | 954 | 951
2017-07-12 21:30 | 914 | 913
2017-07-12 22:00 | 878 | 878
2017-07-12 22:30 | 865 | 864
2017-07-12 23:00 | 852 | 850
2017-07-12 23:30 | 794 | 793
2017-07-13 | 745 | 743
2017-07-13 00:30 | 707 | 704
2017-07-13 01:00 | 665 | 658
2017-07-13 01:30 | 670 | 664
2017-07-13 02:00 | 655 | 649
2017-07-13 02:30 | 642 | 637
2017-07-13 03:00 | 622 | 614
2017-07-13 03:30 | 616 | 607
2017-07-13 04:00 | 628 | 620
2017-07-13 04:30 | 634 | 628
2017-07-13 05:00 | 649 | 644
2017-07-13 05:30 | 683 | 677
2017-07-13 06:00 | 725 | 721
2017-07-13 06:30 | 809 | 806
2017-07-13 07:00 | 884 | 882
2017-07-13 07:30 | 956 | 956
2017-07-13 08:00 | 952 | 951
2017-07-13 08:30 | 921 | 920
2017-07-13 09:00 | 870 | 870
2017-07-13 09:30 | 822 | 822
2017-07-13 10:00 | 787 | 784
2017-07-13 10:30 | 756 | 751
2017-07-13 11:00 | 737 | 733
2017-07-13 11:30 | 723 | 721
2017-07-13 12:00 | 719 | 717
2017-07-13 12:30 | 735 | 734
2017-07-13 13:00 | 774 | 774
2017-07-13 13:30 | 803 | 802
2017-07-13 14:00 | 809 | 809
2017-07-13 14:30 | 819 | 819
2017-07-13 15:00 | 794 | 794
2017-07-13 15:30 | 849 | 849
2017-07-13 16:00 | 847 | 846
2017-07-13 16:30 | 901 | 901
2017-07-13 17:00 | 920 | 919
2017-07-13 17:30 | 972 | 971
2017-07-13 18:00 | 1032 | 1031
2017-07-13 18:30 | 1039 | 1038
2017-07-13 19:00 | 1049 | 1048
2017-07-13 19:30 | 1038 | 1036
2017-07-13 20:00 | 1026 | 1023
2017-07-13 20:30 | 1019 | 1017
2017-07-13 21:00 | 979 | 979
2017-07-13 21:30 | 932 | 930
2017-07-13 22:00 | 889 | 887
2017-07-13 22:30 | 864 | 862
2017-07-13 23:00 | 849 | 849
2017-07-13 23:30 | 790 | 789
2017-07-14 | 739 | 737
2017-07-14 00:30 | 689 | 685
2017-07-14 01:00 | 647 | 640
2017-07-14 01:30 | 620 | 611
2017-07-14 02:00 | 604 | 593
2017-07-14 02:30 | 594 | 583
2017-07-14 03:00 | 587 | 575
2017-07-14 03:30 | 590 | 577
2017-07-14 04:00 | 592 | 581
2017-07-14 04:30 | 606 | 598
2017-07-14 05:00 | 625 | 618
2017-07-14 05:30 | 668 | 665
2017-07-14 06:00 | 715 | 714
2017-07-14 06:30 | 808 | 807
2017-07-14 07:00 | 893 | 890
2017-07-14 07:30 | 960 | 958
2017-07-14 08:00 | 956 | 955
2017-07-14 08:30 | 917 | 915
2017-07-14 09:00 | 872 | 870
2017-07-14 09:30 | 835 | 833
2017-07-14 10:00 | 801 | 799
2017-07-14 10:30 | 786 | 786
2017-07-14 11:00 | 778 | 778
2017-07-14 11:30 | 757 | 757
2017-07-14 12:00 | 740 | 740
2017-07-14 12:30 | 729 | 729
2017-07-14 13:00 | 771 | 771
2017-07-14 13:30 | 779 | 779
2017-07-14 14:00 | 767 | 767
2017-07-14 14:30 | 757 | 756
2017-07-14 15:00 | 766 | 766
2017-07-14 15:30 | 781 | 780
2017-07-14 16:00 | 804 | 803
2017-07-14 16:30 | 841 | 841
2017-07-14 17:00 | 885 | 885
2017-07-14 17:30 | 920 | 919
2017-07-14 18:00 | 958 | 957
2017-07-14 18:30 | 954 | 950
2017-07-14 19:00 | 962 | 957
2017-07-14 19:30 | 949 | 943
2017-07-14 20:00 | 940 | 937
2017-07-14 20:30 | 929 | 927
2017-07-14 21:00 | 896 | 896
2017-07-14 21:30 | 861 | 859
2017-07-14 22:00 | 834 | 831
2017-07-14 22:30 | 811 | 809
2017-07-14 23:00 | 802 | 800
2017-07-14 23:30 | 760 | 757
2017-07-15 | 710 | 707
2017-07-15 00:30 | 653 | 648
2017-07-15 01:00 | 626 | 617
2017-07-15 01:30 | 599 | 589
2017-07-15 02:00 | 579 | 566
2017-07-15 02:30 | 569 | 554
2017-07-15 03:00 | 557 | 542
2017-07-15 03:30 | 560 | 544
2017-07-15 04:00 | 559 | 542
2017-07-15 04:30 | 561 | 545
2017-07-15 05:00 | 570 | 556
2017-07-15 05:30 | 586 | 574
2017-07-15 06:00 | 603 | 594
2017-07-15 06:30 | 633 | 627
2017-07-15 07:00 | 666 | 662
2017-07-15 07:30 | 712 | 710
2017-07-15 08:00 | 732 | 730
2017-07-15 08:30 | 742 | 742
2017-07-15 09:00 | 735 | 734
2017-07-15 09:30 | 710 | 709
2017-07-15 10:00 | 687 | 687
2017-07-15 10:30 | 669 | 668
2017-07-15 11:00 | 642 | 640
2017-07-15 11:30 | 625 | 622
2017-07-15 12:00 | 616 | 613
2017-07-15 12:30 | 612 | 609
2017-07-15 13:00 | 610 | 607
2017-07-15 13:30 | 615 | 612
2017-07-15 14:00 | 625 | 622
2017-07-15 14:30 | 642 | 639
2017-07-15 15:00 | 657 | 654
2017-07-15 15:30 | 677 | 675
2017-07-15 16:00 | 703 | 702
2017-07-15 16:30 | 736 | 735
2017-07-15 17:00 | 795 | 795
2017-07-15 17:30 | 837 | 837
2017-07-15 18:00 | 855 | 854
2017-07-15 18:30 | 852 | 850
2017-07-15 19:00 | 848 | 846
2017-07-15 19:30 | 833 | 829
2017-07-15 20:00 | 828 | 826
2017-07-15 20:30 | 822 | 820
2017-07-15 21:00 | 788 | 785
2017-07-15 21:30 | 764 | 763
2017-07-15 22:00 | 750 | 747
2017-07-15 22:30 | 748 | 745
2017-07-15 23:00 | 754 | 751
2017-07-15 23:30 | 716 | 711
2017-07-16 | 677 | 671
2017-07-16 00:30 | 626 | 619
2017-07-16 01:00 | 602 | 592
2017-07-16 01:30 | 573 | 561
2017-07-16 02:00 | 555 | 541
2017-07-16 02:30 | 546 | 532
2017-07-16 03:00 | 535 | 519
2017-07-16 03:30 | 537 | 520
2017-07-16 04:00 | 533 | 516
2017-07-16 04:30 | 545 | 529
2017-07-16 05:00 | 534 | 517
2017-07-16 05:30 | 546 | 530
2017-07-16 06:00 | 557 | 542
2017-07-16 06:30 | 578 | 566
2017-07-16 07:00 | 598 | 586
2017-07-16 07:30 | 629 | 618
2017-07-16 08:00 | 661 | 654
2017-07-16 08:30 | 686 | 681
2017-07-16 09:00 | 703 | 701
2017-07-16 09:30 | 701 | 700
2017-07-16 10:00 | 698 | 695
2017-07-16 10:30 | 695 | 692
2017-07-16 11:00 | 666 | 662
2017-07-16 11:30 | 639 | 635
2017-07-16 12:00 | 646 | 643
2017-07-16 12:30 | 641 | 638
2017-07-16 13:00 | 634 | 631
2017-07-16 13:30 | 626 | 622
2017-07-16 14:00 | 629 | 625
2017-07-16 14:30 | 634 | 630
2017-07-16 15:00 | 654 | 650
2017-07-16 15:30 | 670 | 666
2017-07-16 16:00 | 702 | 699
2017-07-16 16:30 | 754 | 752
2017-07-16 17:00 | 805 | 803
2017-07-16 17:30 | 848 | 848
2017-07-16 18:00 | 902 | 899
2017-07-16 18:30 | 904 | 899
2017-07-16 19:00 | 899 | 894
2017-07-16 19:30 | 877 | 871
2017-07-16 20:00 | 870 | 863
2017-07-16 20:30 | 868 | 860
2017-07-16 21:00 | 840 | 829
2017-07-16 21:30 | 809 | 798
2017-07-16 22:00 | 779 | 770
2017-07-16 22:30 | 757 | 747
2017-07-16 23:00 | 743 | 738
2017-07-16 23:30 | 710 | 703
2017-07-17 | 665 | 657
2017-07-17 00:30 | 621 | 610
2017-07-17 01:00 | 597 | 582
2017-07-17 01:30 | 583 | 565
2017-07-17 02:00 | 568 | 549
2017-07-17 02:30 | 560 | 539
2017-07-17 03:00 | 552 | 531
2017-07-17 03:30 | 555 | 533
2017-07-17 04:00 | 540 | 515
2017-07-17 04:30 | 495 | 469
2017-07-17 05:00 | 517 | 495
2017-07-17 05:30 | 587 | 575
2017-07-17 06:00 | 670 | 665
2017-07-17 06:30 | 757 | 755
2017-07-17 07:00 | 828 | 827
2017-07-17 07:30 | 896 | 893
2017-07-17 08:00 | 892 | 888
2017-07-17 08:30 | 861 | 857
2017-07-17 09:00 | 822 | 818
2017-07-17 09:30 | 792 | 788
2017-07-17 10:00 | 768 | 764
2017-07-17 10:30 | 745 | 744
2017-07-17 11:00 | 727 | 726
2017-07-17 11:30 | 727 | 726
2017-07-17 12:00 | 734 | 733
2017-07-17 12:30 | 751 | 750
2017-07-17 13:00 | 752 | 751
2017-07-17 13:30 | 753 | 753
2017-07-17 14:00 | 765 | 764
2017-07-17 14:30 | 770 | 769
2017-07-17 15:00 | 782 | 782
2017-07-17 15:30 | 794 | 794
2017-07-17 16:00 | 837 | 837
2017-07-17 16:30 | 878 | 877
2017-07-17 17:00 | 923 | 922
2017-07-17 17:30 | 971 | 969
2017-07-17 18:00 | 1011 | 1009
2017-07-17 18:30 | 1013 | 1009
2017-07-17 19:00 | 1005 | 1002
2017-07-17 19:30 | 983 | 980
2017-07-17 20:00 | 968 | 967
2017-07-17 20:30 | 960 | 959
2017-07-17 21:00 | 915 | 914
2017-07-17 21:30 | 870 | 869
2017-07-17 22:00 | 837 | 836
2017-07-17 22:30 | 814 | 813
2017-07-17 23:00 | 786 | 783
2017-07-17 23:30 | 740 | 736
2017-07-18 | 697 | 688
2017-07-18 00:30 | 638 | 629
2017-07-18 01:00 | 631 | 623
2017-07-18 01:30 | 620 | 613
2017-07-18 02:00 | 580 | 566
2017-07-18 02:30 | 567 | 548
2017-07-18 03:00 | 569 | 553
2017-07-18 03:30 | 563 | 546
2017-07-18 04:00 | 563 | 545
2017-07-18 04:30 | 576 | 561
2017-07-18 05:00 | 617 | 608
2017-07-18 05:30 | 632 | 626
2017-07-18 06:00 | 675 | 671
2017-07-18 06:30 | 752 | 748
2017-07-18 07:00 | 820 | 817
2017-07-18 07:30 | 878 | 877
2017-07-18 08:00 | 885 | 884
2017-07-18 08:30 | 858 | 856
2017-07-18 09:00 | 821 | 820
2017-07-18 09:30 | 798 | 796
2017-07-18 10:00 | 766 | 764
2017-07-18 10:30 | 744 | 742
2017-07-18 11:00 | 735 | 733
2017-07-18 11:30 | 724 | 722
2017-07-18 12:00 | 720 | 719
2017-07-18 12:30 | 721 | 719
2017-07-18 13:00 | 722 | 721
2017-07-18 13:30 | 733 | 732
2017-07-18 14:00 | 754 | 754
2017-07-18 14:30 | 767 | 767
2017-07-18 15:00 | 776 | 775
2017-07-18 15:30 | 792 | 792
2017-07-18 16:00 | 823 | 822
2017-07-18 16:30 | 855 | 854
2017-07-18 17:00 | 889 | 889
2017-07-18 17:30 | 927 | 927
2017-07-18 18:00 | 957 | 957
2017-07-18 18:30 | 957 | 954
2017-07-18 19:00 | 955 | 952
2017-07-18 19:30 | 930 | 929
2017-07-18 20:00 | 920 | 919
2017-07-18 20:30 | 911 | 908
2017-07-18 21:00 | 869 | 866
2017-07-18 21:30 | 840 | 837
2017-07-18 22:00 | 806 | 803
2017-07-18 22:30 | 786 | 783
2017-07-18 23:00 | 775 | 771
2017-07-18 23:30 | 727 | 724
2017-07-19 | 681 | 676
2017-07-19 00:30 | 659 | 654
2017-07-19 01:00 | 637 | 630
2017-07-19 01:30 | 620 | 611
2017-07-19 02:00 | 592 | 579
2017-07-19 02:30 | 587 | 571
2017-07-19 03:00 | 563 | 542
2017-07-19 03:30 | 561 | 540
2017-07-19 04:00 | 566 | 545
2017-07-19 04:30 | 579 | 560
2017-07-19 05:00 | 592 | 575
2017-07-19 05:30 | 624 | 614
2017-07-19 06:00 | 668 | 663
2017-07-19 06:30 | 750 | 741
2017-07-19 07:00 | 808 | 799
2017-07-19 07:30 | 875 | 868
2017-07-19 08:00 | 878 | 871
2017-07-19 08:30 | 851 | 843
2017-07-19 09:00 | 812 | 804
2017-07-19 09:30 | 780 | 773
2017-07-19 10:00 | 748 | 741
2017-07-19 10:30 | 751 | 747
2017-07-19 11:00 | 729 | 724
2017-07-19 11:30 | 739 | 734
2017-07-19 12:00 | 715 | 709
2017-07-19 12:30 | 716 | 712
2017-07-19 13:00 | 722 | 718
2017-07-19 13:30 | 724 | 721
2017-07-19 14:00 | 713 | 709
2017-07-19 14:30 | 731 | 727
2017-07-19 15:00 | 754 | 750
2017-07-19 15:30 | 771 | 767
2017-07-19 16:00 | 824 | 821
2017-07-19 16:30 | 864 | 862
2017-07-19 17:00 | 928 | 926
2017-07-19 17:30 | 986 | 985
2017-07-19 18:00 | 1049 | 1044
2017-07-19 18:30 | 1052 | 1045
2017-07-19 19:00 | 1061 | 1059
2017-07-19 19:30 | 1051 | 1048
2017-07-19 20:00 | 1041 | 1038
2017-07-19 20:30 | 1022 | 1016
2017-07-19 21:00 | 980 | 972
2017-07-19 21:30 | 920 | 919
2017-07-19 22:00 | 865 | 862
2017-07-19 22:30 | 826 | 825
2017-07-19 23:00 | 805 | 803
2017-07-19 23:30 | 763 | 761
2017-07-20 | 711 | 706
2017-07-20 00:30 | 658 | 649
2017-07-20 01:00 | 630 | 619
2017-07-20 01:30 | 609 | 594
2017-07-20 02:00 | 588 | 570
2017-07-20 02:30 | 583 | 563
2017-07-20 03:00 | 585 | 565
2017-07-20 03:30 | 600 | 585
2017-07-20 04:00 | 598 | 583
2017-07-20 04:30 | 599 | 582
2017-07-20 05:00 | 619 | 605
2017-07-20 05:30 | 657 | 649
2017-07-20 06:00 | 711 | 707
2017-07-20 06:30 | 809 | 802
2017-07-20 07:00 | 890 | 880
2017-07-20 07:30 | 952 | 947
2017-07-20 08:00 | 946 | 939
2017-07-20 08:30 | 896 | 889
2017-07-20 09:00 | 853 | 843
2017-07-20 09:30 | 811 | 804
2017-07-20 10:00 | 764 | 759
2017-07-20 10:30 | 749 | 745
2017-07-20 11:00 | 738 | 734
2017-07-20 11:30 | 725 | 721
2017-07-20 12:00 | 718 | 714
2017-07-20 12:30 | 723 | 718
2017-07-20 13:00 | 701 | 694
2017-07-20 13:30 | 679 | 673
2017-07-20 14:00 | 704 | 698
2017-07-20 14:30 | 711 | 706
2017-07-20 15:00 | 726 | 721
2017-07-20 15:30 | 747 | 743
2017-07-20 16:00 | 780 | 778
2017-07-20 16:30 | 818 | 816
2017-07-20 17:00 | 871 | 870
2017-07-20 17:30 | 937 | 936
2017-07-20 18:00 | 1000 | 1000
2017-07-20 18:30 | 1011 | 1008
2017-07-20 19:00 | 1025 | 1022
2017-07-20 19:30 | 1013 | 1009
2017-07-20 20:00 | 1011 | 1006
2017-07-20 20:30 | 999 | 994
2017-07-20 21:00 | 961 | 956
2017-07-20 21:30 | 906 | 895
2017-07-20 22:00 | 848 | 843
2017-07-20 22:30 | 820 | 815
2017-07-20 23:00 | 812 | 804
2017-07-20 23:30 | 762 | 758
2017-07-21 | 711 | 705
2017-07-21 00:30 | 660 | 649
2017-07-21 01:00 | 656 | 646
2017-07-21 01:30 | 607 | 589
2017-07-21 02:00 | 592 | 571
2017-07-21 02:30 | 584 | 562
2017-07-21 03:00 | 578 | 555
2017-07-21 03:30 | 590 | 571
2017-07-21 04:00 | 606 | 589
2017-07-21 04:30 | 601 | 583
2017-07-21 05:00 | 624 | 609
2017-07-21 05:30 | 667 | 658
2017-07-21 06:00 | 717 | 715
2017-07-21 06:30 | 833 | 833
2017-07-21 07:00 | 934 | 934
2017-07-21 07:30 | 1006 | 1002
2017-07-21 08:00 | 996 | 992
2017-07-21 08:30 | 953 | 948
2017-07-21 09:00 | 887 | 881
2017-07-21 09:30 | 827 | 817
2017-07-21 10:00 | 782 | 772
2017-07-21 10:30 | 743 | 731
2017-07-21 11:00 | 704 | 691
2017-07-21 11:30 | 687 | 675
2017-07-21 12:00 | 672 | 668
2017-07-21 12:30 | 669 | 664
2017-07-21 13:00 | 669 | 664
2017-07-21 13:30 | 672 | 669
2017-07-21 14:00 | 689 | 686
2017-07-21 14:30 | 706 | 703
2017-07-21 15:00 | 722 | 719
2017-07-21 15:30 | 748 | 744
2017-07-21 16:00 | 781 | 779
2017-07-21 16:30 | 823 | 821
2017-07-21 17:00 | 893 | 891
2017-07-21 17:30 | 958 | 955
2017-07-21 18:00 | 1011 | 1008
2017-07-21 18:30 | 1026 | 1023
2017-07-21 19:00 | 1038 | 1033
2017-07-21 19:30 | 1036 | 1027
2017-07-21 20:00 | 1023 | 1012
2017-07-21 20:30 | 1013 | 1005
2017-07-21 21:00 | 983 | 977
2017-07-21 21:30 | 941 | 939
2017-07-21 22:00 | 910 | 907
2017-07-21 22:30 | 882 | 877
2017-07-21 23:00 | 863 | 857
2017-07-21 23:30 | 803 | 799
2017-07-22 | 756 | 750
2017-07-22 00:30 | 694 | 686
2017-07-22 01:00 | 660 | 649
2017-07-22 01:30 | 638 | 623
2017-07-22 02:00 | 622 | 603
2017-07-22 02:30 | 611 | 590
2017-07-22 03:00 | 599 | 578
2017-07-22 03:30 | 579 | 556
2017-07-22 04:00 | 575 | 551
2017-07-22 04:30 | 555 | 530
2017-07-22 05:00 | 563 | 538
2017-07-22 05:30 | 582 | 562
2017-07-22 06:00 | 642 | 630
2017-07-22 06:30 | 688 | 682
2017-07-22 07:00 | 740 | 737
2017-07-22 07:30 | 794 | 790
2017-07-22 08:00 | 819 | 817
2017-07-22 08:30 | 824 | 823
2017-07-22 09:00 | 807 | 805
2017-07-22 09:30 | 778 | 776
2017-07-22 10:00 | 747 | 742
2017-07-22 10:30 | 700 | 695
2017-07-22 11:00 | 682 | 675
2017-07-22 11:30 | 646 | 638
2017-07-22 12:00 | 627 | 621
2017-07-22 12:30 | 606 | 601
2017-07-22 13:00 | 598 | 593
2017-07-22 13:30 | 603 | 597
2017-07-22 14:00 | 603 | 597
2017-07-22 14:30 | 600 | 593
2017-07-22 15:00 | 628 | 622
2017-07-22 15:30 | 665 | 661
2017-07-22 16:00 | 698 | 696
2017-07-22 16:30 | 737 | 736
2017-07-22 17:00 | 805 | 803
2017-07-22 17:30 | 856 | 853
2017-07-22 18:00 | 911 | 906
2017-07-22 18:30 | 929 | 924
2017-07-22 19:00 | 936 | 932
2017-07-22 19:30 | 924 | 920
2017-07-22 20:00 | 915 | 911
2017-07-22 20:30 | 910 | 906
2017-07-22 21:00 | 882 | 880
2017-07-22 21:30 | 857 | 855
2017-07-22 22:00 | 838 | 835
2017-07-22 22:30 | 820 | 815
2017-07-22 23:00 | 809 | 804
2017-07-22 23:30 | 764 | 758
2017-07-23 | 718 | 713
2017-07-23 00:30 | 674 | 665
2017-07-23 01:00 | 642 | 630
2017-07-23 01:30 | 615 | 600
2017-07-23 02:00 | 601 | 584
2017-07-23 02:30 | 589 | 570
2017-07-23 03:00 | 578 | 556
2017-07-23 03:30 | 572 | 549
2017-07-23 04:00 | 575 | 553
2017-07-23 04:30 | 573 | 550
2017-07-23 05:00 | 572 | 549
2017-07-23 05:30 | 585 | 566
2017-07-23 06:00 | 604 | 587
2017-07-23 06:30 | 621 | 608
2017-07-23 07:00 | 651 | 640
2017-07-23 07:30 | 679 | 671
2017-07-23 08:00 | 700 | 695
2017-07-23 08:30 | 712 | 709
2017-07-23 09:00 | 713 | 711
2017-07-23 09:30 | 691 | 690
2017-07-23 10:00 | 668 | 665
2017-07-23 10:30 | 653 | 650
2017-07-23 11:00 | 627 | 623
2017-07-23 11:30 | 604 | 598
2017-07-23 12:00 | 594 | 587
2017-07-23 12:30 | 585 | 578
2017-07-23 13:00 | 580 | 572
2017-07-23 13:30 | 582 | 574
2017-07-23 14:00 | 590 | 582
2017-07-23 14:30 | 604 | 597
2017-07-23 15:00 | 625 | 620
2017-07-23 15:30 | 651 | 647
2017-07-23 16:00 | 680 | 677
2017-07-23 16:30 | 718 | 716
2017-07-23 17:00 | 770 | 768
2017-07-23 17:30 | 839 | 836
2017-07-23 18:00 | 903 | 897
2017-07-23 18:30 | 925 | 918
2017-07-23 19:00 | 930 | 923
2017-07-23 19:30 | 925 | 917
2017-07-23 20:00 | 918 | 910
2017-07-23 20:30 | 910 | 908
2017-07-23 21:00 | 883 | 880
2017-07-23 21:30 | 856 | 851
2017-07-23 22:00 | 820 | 813
2017-07-23 22:30 | 795 | 788
2017-07-23 23:00 | 779 | 773
2017-07-23 23:30 | 741 | 736
2017-07-24 | 702 | 693
2017-07-24 00:30 | 662 | 649
2017-07-24 01:00 | 631 | 614
2017-07-24 01:30 | 610 | 590
2017-07-24 02:00 | 591 | 569
2017-07-24 02:30 | 582 | 560
2017-07-24 03:00 | 574 | 549
2017-07-24 03:30 | 575 | 552
2017-07-24 04:00 | 581 | 559
2017-07-24 04:30 | 596 | 577
2017-07-24 05:00 | 619 | 604
2017-07-24 05:30 | 665 | 657
2017-07-24 06:00 | 721 | 719
2017-07-24 06:30 | 827 | 827
2017-07-24 07:00 | 928 | 927
2017-07-24 07:30 | 1002 | 1002
2017-07-24 08:00 | 1005 | 1005
2017-07-24 08:30 | 975 | 975
2017-07-24 09:00 | 907 | 906
2017-07-24 09:30 | 859 | 856
2017-07-24 10:00 | 813 | 809
2017-07-24 10:30 | 778 | 772
2017-07-24 11:00 | 749 | 743
2017-07-24 11:30 | 726 | 725
2017-07-24 12:00 | 715 | 713
2017-07-24 12:30 | 708 | 706
2017-07-24 13:00 | 709 | 707
2017-07-24 13:30 | 712 | 710
2017-07-24 14:00 | 726 | 724
2017-07-24 14:30 | 733 | 731
2017-07-24 15:00 | 750 | 749
2017-07-24 15:30 | 771 | 770
2017-07-24 16:00 | 805 | 804
2017-07-24 16:30 | 841 | 841
2017-07-24 17:00 | 885 | 885
2017-07-24 17:30 | 940 | 940
2017-07-24 18:00 | 1018 | 1017
2017-07-24 18:30 | 1025 | 1023
2017-07-24 19:00 | 1039 | 1036
2017-07-24 19:30 | 1024 | 1020
2017-07-24 20:00 | 1020 | 1015
2017-07-24 20:30 | 1005 | 998
2017-07-24 21:00 | 964 | 958
2017-07-24 21:30 | 906 | 903
2017-07-24 22:00 | 866 | 863
2017-07-24 22:30 | 835 | 830
2017-07-24 23:00 | 825 | 817
2017-07-24 23:30 | 774 | 761
2017-07-25 | 718 | 712
2017-07-25 00:30 | 672 | 662
2017-07-25 01:00 | 638 | 626
2017-07-25 01:30 | 619 | 602
2017-07-25 02:00 | 608 | 587
2017-07-25 02:30 | 602 | 578
2017-07-25 03:00 | 595 | 569
2017-07-25 03:30 | 591 | 565
2017-07-25 04:00 | 577 | 548
2017-07-25 04:30 | 583 | 560
2017-07-25 05:00 | 576 | 556
2017-07-25 05:30 | 678 | 669
2017-07-25 06:00 | 746 | 739
2017-07-25 06:30 | 851 | 841
2017-07-25 07:00 | 942 | 936
2017-07-25 07:30 | 1021 | 1018
2017-07-25 08:00 | 1020 | 1017
2017-07-25 08:30 | 972 | 966
2017-07-25 09:00 | 903 | 893
2017-07-25 09:30 | 848 | 840
2017-07-25 10:00 | 796 | 792
2017-07-25 10:30 | 756 | 751
2017-07-25 11:00 | 729 | 727
2017-07-25 11:30 | 698 | 697
2017-07-25 12:00 | 691 | 690
2017-07-25 12:30 | 686 | 686
2017-07-25 13:00 | 687 | 687
2017-07-25 13:30 | 689 | 689
2017-07-25 14:00 | 706 | 706
2017-07-25 14:30 | 721 | 721
2017-07-25 15:00 | 726 | 726
2017-07-25 15:30 | 755 | 755
2017-07-25 16:00 | 788 | 788
2017-07-25 16:30 | 833 | 833
2017-07-25 17:00 | 909 | 909
2017-07-25 17:30 | 966 | 966
2017-07-25 18:00 | 1032 | 1032
2017-07-25 18:30 | 1052 | 1049
2017-07-25 19:00 | 1059 | 1056
2017-07-25 19:30 | 1054 | 1050
2017-07-25 20:00 | 1048 | 1044
2017-07-25 20:30 | 1038 | 1033
2017-07-25 21:00 | 996 | 993
2017-07-25 21:30 | 934 | 929
2017-07-25 22:00 | 890 | 884
2017-07-25 22:30 | 859 | 852
2017-07-25 23:00 | 832 | 831
2017-07-25 23:30 | 784 | 781
2017-07-26 | 733 | 728
2017-07-26 00:30 | 682 | 677
2017-07-26 01:00 | 649 | 641
2017-07-26 01:30 | 631 | 621
2017-07-26 02:00 | 614 | 601
2017-07-26 02:30 | 602 | 588
2017-07-26 03:00 | 595 | 581
2017-07-26 03:30 | 590 | 575
2017-07-26 04:00 | 603 | 588
2017-07-26 04:30 | 621 | 608
2017-07-26 05:00 | 639 | 630
2017-07-26 05:30 | 683 | 679
2017-07-26 06:00 | 761 | 760
2017-07-26 06:30 | 870 | 867
2017-07-26 07:00 | 965 | 961
2017-07-26 07:30 | 1027 | 1025
2017-07-26 08:00 | 1024 | 1022
2017-07-26 08:30 | 969 | 965
2017-07-26 09:00 | 918 | 912
2017-07-26 09:30 | 870 | 862
2017-07-26 10:00 | 809 | 809
2017-07-26 10:30 | 766 | 766
2017-07-26 11:00 | 736 | 736
2017-07-26 11:30 | 712 | 712
2017-07-26 12:00 | 705 | 705
2017-07-26 12:30 | 701 | 701
2017-07-26 13:00 | 710 | 710
2017-07-26 13:30 | 719 | 719
2017-07-26 14:00 | 733 | 733
2017-07-26 14:30 | 742 | 741
2017-07-26 15:00 | 760 | 760
2017-07-26 15:30 | 781 | 781
2017-07-26 16:00 | 816 | 816
2017-07-26 16:30 | 850 | 849
2017-07-26 17:00 | 893 | 893
2017-07-26 17:30 | 969 | 969
2017-07-26 18:00 | 1042 | 1042
2017-07-26 18:30 | 1028 | 1026
2017-07-26 19:00 | 1042 | 1040
2017-07-26 19:30 | 1047 | 1045
2017-07-26 20:00 | 1031 | 1029
2017-07-26 20:30 | 1032 | 1030
2017-07-26 21:00 | 940 | 939
2017-07-26 21:30 | 885 | 883
2017-07-26 22:00 | 852 | 849
2017-07-26 22:30 | 826 | 823
2017-07-26 23:00 | 809 | 804
2017-07-26 23:30 | 742 | 737
2017-07-27 | 699 | 693
2017-07-27 00:30 | 648 | 637
2017-07-27 01:00 | 622 | 606
2017-07-27 01:30 | 594 | 583
2017-07-27 02:00 | 577 | 564
2017-07-27 02:30 | 563 | 548
2017-07-27 03:00 | 553 | 537
2017-07-27 03:30 | 550 | 533
2017-07-27 04:00 | 556 | 540
2017-07-27 04:30 | 569 | 556
2017-07-27 05:00 | 589 | 580
2017-07-27 05:30 | 638 | 634
2017-07-27 06:00 | 712 | 710
2017-07-27 06:30 | 822 | 818
2017-07-27 07:00 | 925 | 922
2017-07-27 07:30 | 994 | 992
2017-07-27 08:00 | 960 | 952
2017-07-27 08:30 | 884 | 876
2017-07-27 09:00 | 813 | 807
2017-07-27 09:30 | 774 | 765
2017-07-27 10:00 | 723 | 717
2017-07-27 10:30 | 694 | 689
2017-07-27 11:00 | 663 | 660
2017-07-27 11:30 | 648 | 645
2017-07-27 12:00 | 639 | 636
2017-07-27 12:30 | 624 | 624
2017-07-27 13:00 | 626 | 626
2017-07-27 13:30 | 629 | 629
2017-07-27 14:00 | 646 | 646
2017-07-27 14:30 | 664 | 664
2017-07-27 15:00 | 687 | 687
2017-07-27 15:30 | 720 | 719
2017-07-27 16:00 | 769 | 769
2017-07-27 16:30 | 823 | 823
2017-07-27 17:00 | 881 | 881
2017-07-27 17:30 | 940 | 940
2017-07-27 18:00 | 1004 | 1004
2017-07-27 18:30 | 1018 | 1018
2017-07-27 19:00 | 1027 | 1027
2017-07-27 19:30 | 1012 | 1011
2017-07-27 20:00 | 1001 | 1000
2017-07-27 20:30 | 993 | 991
2017-07-27 21:00 | 960 | 959
2017-07-27 21:30 | 915 | 911
2017-07-27 22:00 | 874 | 871
2017-07-27 22:30 | 840 | 838
2017-07-27 23:00 | 824 | 822
2017-07-27 23:30 | 779 | 774
2017-07-28 | 731 | 722
2017-07-28 00:30 | 680 | 665
2017-07-28 01:00 | 641 | 622
2017-07-28 01:30 | 604 | 594
2017-07-28 02:00 | 580 | 569
2017-07-28 02:30 | 573 | 559
2017-07-28 03:00 | 564 | 550
2017-07-28 03:30 | 569 | 555
2017-07-28 04:00 | 564 | 550
2017-07-28 04:30 | 574 | 562
2017-07-28 05:00 | 603 | 594
2017-07-28 05:30 | 646 | 643
2017-07-28 06:00 | 708 | 706
2017-07-28 06:30 | 820 | 818
2017-07-28 07:00 | 921 | 914
2017-07-28 07:30 | 998 | 990
2017-07-28 08:00 | 989 | 980
2017-07-28 08:30 | 928 | 917
2017-07-28 09:00 | 861 | 845
2017-07-28 09:30 | 829 | 809
2017-07-28 10:00 | 791 | 768
2017-07-28 10:30 | 759 | 754
2017-07-28 11:00 | 722 | 717
2017-07-28 11:30 | 708 | 702
2017-07-28 12:00 | 700 | 693
2017-07-28 12:30 | 667 | 658
2017-07-28 13:00 | 660 | 651
2017-07-28 13:30 | 667 | 662
2017-07-28 14:00 | 677 | 673
2017-07-28 14:30 | 689 | 685
2017-07-28 15:00 | 712 | 708
2017-07-28 15:30 | 748 | 745
2017-07-28 16:00 | 796 | 794
2017-07-28 16:30 | 843 | 841
2017-07-28 17:00 | 881 | 880
2017-07-28 17:30 | 912 | 910
2017-07-28 18:00 | 959 | 956
2017-07-28 18:30 | 960 | 954
2017-07-28 19:00 | 963 | 955
2017-07-28 19:30 | 944 | 935
2017-07-28 20:00 | 940 | 931
2017-07-28 20:30 | 926 | 922
2017-07-28 21:00 | 895 | 889
2017-07-28 21:30 | 866 | 857
2017-07-28 22:00 | 837 | 825
2017-07-28 22:30 | 809 | 805
2017-07-28 23:00 | 804 | 802
2017-07-28 23:30 | 761 | 759
2017-07-29 | 711 | 707
2017-07-29 00:30 | 659 | 652
2017-07-29 01:00 | 632 | 622
2017-07-29 01:30 | 597 | 585
2017-07-29 02:00 | 572 | 557
2017-07-29 02:30 | 555 | 537
2017-07-29 03:00 | 541 | 523
2017-07-29 03:30 | 537 | 517
2017-07-29 04:00 | 537 | 516
2017-07-29 04:30 | 542 | 522
2017-07-29 05:00 | 547 | 527
2017-07-29 05:30 | 560 | 545
2017-07-29 06:00 | 574 | 563
2017-07-29 06:30 | 614 | 609
2017-07-29 07:00 | 661 | 657
2017-07-29 07:30 | 721 | 719
2017-07-29 08:00 | 734 | 733
2017-07-29 08:30 | 729 | 729
2017-07-29 09:00 | 714 | 714
2017-07-29 09:30 | 685 | 685
2017-07-29 10:00 | 652 | 651
2017-07-29 10:30 | 622 | 620
2017-07-29 11:00 | 597 | 595
2017-07-29 11:30 | 576 | 573
2017-07-29 12:00 | 563 | 559
2017-07-29 12:30 | 553 | 548
2017-07-29 13:00 | 553 | 547
2017-07-29 13:30 | 551 | 545
2017-07-29 14:00 | 563 | 557
2017-07-29 14:30 | 571 | 566
2017-07-29 15:00 | 589 | 585
2017-07-29 15:30 | 621 | 618
2017-07-29 16:00 | 657 | 655
2017-07-29 16:30 | 708 | 707
2017-07-29 17:00 | 775 | 774
2017-07-29 17:30 | 828 | 827
2017-07-29 18:00 | 878 | 878
2017-07-29 18:30 | 897 | 896
2017-07-29 19:00 | 894 | 893
2017-07-29 19:30 | 890 | 889
2017-07-29 20:00 | 884 | 883
2017-07-29 20:30 | 878 | 877
2017-07-29 21:00 | 853 | 851
2017-07-29 21:30 | 810 | 808
2017-07-29 22:00 | 789 | 789
2017-07-29 22:30 | 781 | 781
2017-07-29 23:00 | 781 | 780
2017-07-29 23:30 | 748 | 747
2017-07-30 | 683 | 680
2017-07-30 00:30 | 630 | 624
2017-07-30 01:00 | 599 | 590
2017-07-30 01:30 | 585 | 571
2017-07-30 02:00 | 567 | 550
2017-07-30 02:30 | 557 | 538
2017-07-30 03:00 | 555 | 534
2017-07-30 03:30 | 558 | 536
2017-07-30 04:00 | 554 | 531
2017-07-30 04:30 | 556 | 533
2017-07-30 05:00 | 561 | 539
2017-07-30 05:30 | 572 | 553
2017-07-30 06:00 | 586 | 571
2017-07-30 06:30 | 599 | 588
2017-07-30 07:00 | 625 | 616
2017-07-30 07:30 | 665 | 660
2017-07-30 08:00 | 685 | 682
2017-07-30 08:30 | 698 | 696
2017-07-30 09:00 | 686 | 685
2017-07-30 09:30 | 664 | 662
2017-07-30 10:00 | 636 | 634
2017-07-30 10:30 | 601 | 597
2017-07-30 11:00 | 582 | 577
2017-07-30 11:30 | 554 | 548
2017-07-30 12:00 | 547 | 540
2017-07-30 12:30 | 536 | 529
2017-07-30 13:00 | 538 | 530
2017-07-30 13:30 | 541 | 533
2017-07-30 14:00 | 550 | 543
2017-07-30 14:30 | 559 | 552
2017-07-30 15:00 | 585 | 580
2017-07-30 15:30 | 623 | 619
2017-07-30 16:00 | 658 | 656
2017-07-30 16:30 | 718 | 717
2017-07-30 17:00 | 780 | 779
2017-07-30 17:30 | 839 | 835
2017-07-30 18:00 | 892 | 892
2017-07-30 18:30 | 909 | 908
2017-07-30 19:00 | 913 | 910
2017-07-30 19:30 | 896 | 893
2017-07-30 20:00 | 887 | 883
2017-07-30 20:30 | 876 | 874
2017-07-30 21:00 | 852 | 851
2017-07-30 21:30 | 818 | 817
2017-07-30 22:00 | 781 | 779
2017-07-30 22:30 | 764 | 760
2017-07-30 23:00 | 757 | 754
2017-07-30 23:30 | 720 | 717
2017-07-31 | 681 | 676
2017-07-31 00:30 | 635 | 625
2017-07-31 01:00 | 603 | 589
2017-07-31 01:30 | 572 | 555
2017-07-31 02:00 | 551 | 531
2017-07-31 02:30 | 539 | 517
2017-07-31 03:00 | 528 | 507
2017-07-31 03:30 | 525 | 503
2017-07-31 04:00 | 523 | 503
2017-07-31 04:30 | 541 | 524
2017-07-31 05:00 | 572 | 559
2017-07-31 05:30 | 623 | 617
2017-07-31 06:00 | 690 | 688
2017-07-31 06:30 | 774 | 773
2017-07-31 07:00 | 864 | 863
2017-07-31 07:30 | 929 | 929
2017-07-31 08:00 | 927 | 927
2017-07-31 08:30 | 895 | 895
2017-07-31 09:00 | 850 | 850
2017-07-31 09:30 | 808 | 808
2017-07-31 10:00 | 766 | 765
2017-07-31 10:30 | 722 | 721
2017-07-31 11:00 | 698 | 697
2017-07-31 11:30 | 681 | 680
2017-07-31 12:00 | 678 | 677
2017-07-31 12:30 | 678 | 678
2017-07-31 13:00 | 677 | 677
2017-07-31 13:30 | 684 | 684
2017-07-31 14:00 | 696 | 696
2017-07-31 14:30 | 715 | 715
2017-07-31 15:00 | 734 | 734
2017-07-31 15:30 | 758 | 758
2017-07-31 16:00 | 799 | 798
2017-07-31 16:30 | 839 | 839
2017-07-31 17:00 | 900 | 900
2017-07-31 17:30 | 951 | 951
2017-07-31 18:00 | 1003 | 1002
2017-07-31 18:30 | 1004 | 1003
2017-07-31 19:00 | 1002 | 1002
2017-07-31 19:30 | 975 | 974
2017-07-31 20:00 | 950 | 950
2017-07-31 20:30 | 939 | 939
2017-07-31 21:00 | 896 | 895
2017-07-31 21:30 | 851 | 851
2017-07-31 22:00 | 808 | 806
2017-07-31 22:30 | 778 | 774
2017-07-31 23:00 | 758 | 754
2017-07-31 23:30 | 708 | 704
2017-08-01 | 661 | 659
2017-08-01 00:30 | 612 | 607
2017-08-01 01:00 | 580 | 573
2017-08-01 01:30 | 559 | 550
2017-08-01 02:00 | 541 | 529
2017-08-01 02:30 | 531 | 519
2017-08-01 03:00 | 522 | 509
2017-08-01 03:30 | 511 | 498
2017-08-01 04:00 | 513 | 500
2017-08-01 04:30 | 532 | 522
2017-08-01 05:00 | 554 | 547
2017-08-01 05:30 | 609 | 607
2017-08-01 06:00 | 680 | 680
2017-08-01 06:30 | 771 | 770
2017-08-01 07:00 | 819 | 818
2017-08-01 07:30 | 879 | 879
2017-08-01 08:00 | 854 | 854
2017-08-01 08:30 | 780 | 780
2017-08-01 09:00 | 720 | 719
2017-08-01 09:30 | 694 | 692
2017-08-01 10:00 | 656 | 654
2017-08-01 10:30 | 631 | 629
2017-08-01 11:00 | 610 | 609
2017-08-01 11:30 | 594 | 593
2017-08-01 12:00 | 589 | 587
2017-08-01 12:30 | 580 | 579
2017-08-01 13:00 | 578 | 578
2017-08-01 13:30 | 587 | 587
2017-08-01 14:00 | 601 | 601
2017-08-01 14:30 | 616 | 616
2017-08-01 15:00 | 635 | 635
2017-08-01 15:30 | 658 | 658
2017-08-01 16:00 | 708 | 707
2017-08-01 16:30 | 758 | 758
2017-08-01 17:00 | 819 | 819
2017-08-01 17:30 | 881 | 881
2017-08-01 18:00 | 954 | 954
2017-08-01 18:30 | 967 | 966
2017-08-01 19:00 | 965 | 965
2017-08-01 19:30 | 948 | 947
2017-08-01 20:00 | 927 | 925
2017-08-01 20:30 | 916 | 914
2017-08-01 21:00 | 863 | 861
2017-08-01 21:30 | 817 | 813
2017-08-01 22:00 | 767 | 762
2017-08-01 22:30 | 748 | 744
2017-08-01 23:00 | 736 | 732
2017-08-01 23:30 | 684 | 678
2017-08-02 | 634 | 625
2017-08-02 00:30 | 572 | 566
2017-08-02 01:00 | 546 | 536
2017-08-02 01:30 | 526 | 512
2017-08-02 02:00 | 507 | 491
2017-08-02 02:30 | 493 | 475
2017-08-02 03:00 | 489 | 471
2017-08-02 03:30 | 488 | 470
2017-08-02 04:00 | 491 | 473
2017-08-02 04:30 | 502 | 487
2017-08-02 05:00 | 523 | 512
2017-08-02 05:30 | 570 | 566
2017-08-02 06:00 | 638 | 638
2017-08-02 06:30 | 747 | 747
2017-08-02 07:00 | 846 | 845
2017-08-02 07:30 | 920 | 920
2017-08-02 08:00 | 894 | 894
2017-08-02 08:30 | 829 | 828
2017-08-02 09:00 | 763 | 760
2017-08-02 09:30 | 715 | 711
2017-08-02 10:00 | 666 | 664
2017-08-02 10:30 | 639 | 638
2017-08-02 11:00 | 619 | 618
2017-08-02 11:30 | 607 | 606
2017-08-02 12:00 | 602 | 601
2017-08-02 12:30 | 600 | 599
2017-08-02 13:00 | 622 | 621
2017-08-02 13:30 | 631 | 630
2017-08-02 14:00 | 643 | 642
2017-08-02 14:30 | 657 | 657
2017-08-02 15:00 | 672 | 672
2017-08-02 15:30 | 697 | 697
2017-08-02 16:00 | 735 | 735
2017-08-02 16:30 | 786 | 786
2017-08-02 17:00 | 848 | 848
2017-08-02 17:30 | 907 | 907
2017-08-02 18:00 | 975 | 975
2017-08-02 18:30 | 994 | 994
2017-08-02 19:00 | 1001 | 1001
2017-08-02 19:30 | 974 | 973
2017-08-02 20:00 | 956 | 955
2017-08-02 20:30 | 943 | 943
2017-08-02 21:00 | 899 | 897
2017-08-02 21:30 | 855 | 851
2017-08-02 22:00 | 802 | 796
2017-08-02 22:30 | 786 | 781
2017-08-02 23:00 | 761 | 761
2017-08-02 23:30 | 699 | 698
2017-08-03 | 632 | 629
2017-08-03 00:30 | 577 | 570
2017-08-03 01:00 | 542 | 531
2017-08-03 01:30 | 520 | 506
2017-08-03 02:00 | 498 | 482
2017-08-03 02:30 | 486 | 469
2017-08-03 03:00 | 477 | 459
2017-08-03 03:30 | 477 | 458
2017-08-03 04:00 | 484 | 466
2017-08-03 04:30 | 498 | 483
2017-08-03 05:00 | 515 | 504
2017-08-03 05:30 | 576 | 571
2017-08-03 06:00 | 644 | 643
2017-08-03 06:30 | 754 | 748
2017-08-03 07:00 | 845 | 841
2017-08-03 07:30 | 906 | 904
2017-08-03 08:00 | 885 | 880
2017-08-03 08:30 | 833 | 827
2017-08-03 09:00 | 781 | 772
2017-08-03 09:30 | 737 | 725
2017-08-03 10:00 | 688 | 675
2017-08-03 10:30 | 662 | 650
2017-08-03 11:00 | 639 | 627
2017-08-03 11:30 | 626 | 625
2017-08-03 12:00 | 631 | 630
2017-08-03 12:30 | 663 | 662
2017-08-03 13:00 | 657 | 655
2017-08-03 13:30 | 655 | 653
2017-08-03 14:00 | 655 | 653
2017-08-03 14:30 | 666 | 665
2017-08-03 15:00 | 675 | 674
2017-08-03 15:30 | 690 | 689
2017-08-03 16:00 | 715 | 714
2017-08-03 16:30 | 749 | 749
2017-08-03 17:00 | 807 | 806
2017-08-03 17:30 | 905 | 905
2017-08-03 18:00 | 977 | 977
2017-08-03 18:30 | 985 | 985
2017-08-03 19:00 | 995 | 995
2017-08-03 19:30 | 983 | 982
2017-08-03 20:00 | 977 | 975
2017-08-03 20:30 | 968 | 966
2017-08-03 21:00 | 924 | 921
2017-08-03 21:30 | 863 | 861
2017-08-03 22:00 | 818 | 817
2017-08-03 22:30 | 782 | 782
2017-08-03 23:00 | 781 | 780
2017-08-03 23:30 | 743 | 742
2017-08-04 | 691 | 689
2017-08-04 00:30 | 627 | 622
2017-08-04 01:00 | 597 | 591
2017-08-04 01:30 | 578 | 568
2017-08-04 02:00 | 560 | 548
2017-08-04 02:30 | 550 | 535
2017-08-04 03:00 | 540 | 524
2017-08-04 03:30 | 536 | 520
2017-08-04 04:00 | 540 | 525
2017-08-04 04:30 | 550 | 536
2017-08-04 05:00 | 568 | 558
2017-08-04 05:30 | 605 | 601
2017-08-04 06:00 | 653 | 651
2017-08-04 06:30 | 735 | 735
2017-08-04 07:00 | 814 | 814
2017-08-04 07:30 | 878 | 878
2017-08-04 08:00 | 864 | 864
2017-08-04 08:30 | 821 | 820
2017-08-04 09:00 | 777 | 775
2017-08-04 09:30 | 737 | 734
2017-08-04 10:00 | 708 | 707
2017-08-04 10:30 | 687 | 686
2017-08-04 11:00 | 663 | 662
2017-08-04 11:30 | 644 | 644
2017-08-04 12:00 | 633 | 633
2017-08-04 12:30 | 627 | 627
2017-08-04 13:00 | 627 | 627
2017-08-04 13:30 | 634 | 634
2017-08-04 14:00 | 645 | 645
2017-08-04 14:30 | 664 | 663
2017-08-04 15:00 | 704 | 704
2017-08-04 15:30 | 770 | 769
2017-08-04 16:00 | 823 | 822
2017-08-04 16:30 | 857 | 857
2017-08-04 17:00 | 893 | 893
2017-08-04 17:30 | 910 | 910
2017-08-04 18:00 | 939 | 938
2017-08-04 18:30 | 938 | 937
2017-08-04 19:00 | 949 | 948
2017-08-04 19:30 | 937 | 937
2017-08-04 20:00 | 926 | 926
2017-08-04 20:30 | 924 | 924
2017-08-04 21:00 | 889 | 889
2017-08-04 21:30 | 847 | 847
2017-08-04 22:00 | 822 | 821
2017-08-04 22:30 | 813 | 811
2017-08-04 23:00 | 806 | 806
2017-08-04 23:30 | 753 | 751
2017-08-05 | 698 | 696
2017-08-05 00:30 | 651 | 646
2017-08-05 01:00 | 624 | 616
2017-08-05 01:30 | 602 | 591
2017-08-05 02:00 | 579 | 565
2017-08-05 02:30 | 580 | 565
2017-08-05 03:00 | 578 | 561
2017-08-05 03:30 | 575 | 557
2017-08-05 04:00 | 575 | 556
2017-08-05 04:30 | 568 | 550
2017-08-05 05:00 | 586 | 569
2017-08-05 05:30 | 594 | 580
2017-08-05 06:00 | 602 | 593
2017-08-05 06:30 | 634 | 628
2017-08-05 07:00 | 671 | 668
2017-08-05 07:30 | 717 | 716
2017-08-05 08:00 | 739 | 739
2017-08-05 08:30 | 738 | 738
2017-08-05 09:00 | 723 | 723
2017-08-05 09:30 | 689 | 689
2017-08-05 10:00 | 653 | 653
2017-08-05 10:30 | 624 | 623
2017-08-05 11:00 | 599 | 597
2017-08-05 11:30 | 569 | 567
2017-08-05 12:00 | 554 | 552
2017-08-05 12:30 | 537 | 533
2017-08-05 13:00 | 535 | 531
2017-08-05 13:30 | 540 | 535
2017-08-05 14:00 | 564 | 560
2017-08-05 14:30 | 574 | 569
2017-08-05 15:00 | 615 | 609
2017-08-05 15:30 | 656 | 652
2017-08-05 16:00 | 684 | 681
2017-08-05 16:30 | 722 | 721
2017-08-05 17:00 | 774 | 774
2017-08-05 17:30 | 807 | 806
2017-08-05 18:00 | 853 | 852
2017-08-05 18:30 | 875 | 873
2017-08-05 19:00 | 880 | 877
2017-08-05 19:30 | 877 | 873
2017-08-05 20:00 | 874 | 869
2017-08-05 20:30 | 868 | 863
2017-08-05 21:00 | 845 | 841
2017-08-05 21:30 | 814 | 814
2017-08-05 22:00 | 797 | 797
2017-08-05 22:30 | 786 | 786
2017-08-05 23:00 | 793 | 792
2017-08-05 23:30 | 754 | 753
2017-08-06 | 718 | 714
2017-08-06 00:30 | 673 | 664
2017-08-06 01:00 | 642 | 630
2017-08-06 01:30 | 625 | 609
2017-08-06 02:00 | 606 | 586
2017-08-06 02:30 | 595 | 571
2017-08-06 03:00 | 584 | 559
2017-08-06 03:30 | 575 | 549
2017-08-06 04:00 | 568 | 542
2017-08-06 04:30 | 569 | 543
2017-08-06 05:00 | 571 | 545
2017-08-06 05:30 | 584 | 562
2017-08-06 06:00 | 596 | 577
2017-08-06 06:30 | 620 | 606
2017-08-06 07:00 | 646 | 633
2017-08-06 07:30 | 685 | 678
2017-08-06 08:00 | 723 | 720
2017-08-06 08:30 | 740 | 738
2017-08-06 09:00 | 741 | 740
2017-08-06 09:30 | 709 | 706
2017-08-06 10:00 | 693 | 690
2017-08-06 10:30 | 669 | 665
2017-08-06 11:00 | 633 | 626
2017-08-06 11:30 | 617 | 610
2017-08-06 12:00 | 611 | 603
2017-08-06 12:30 | 594 | 585
2017-08-06 13:00 | 587 | 577
2017-08-06 13:30 | 593 | 583
2017-08-06 14:00 | 609 | 600
2017-08-06 14:30 | 620 | 611
2017-08-06 15:00 | 651 | 644
2017-08-06 15:30 | 680 | 676
2017-08-06 16:00 | 713 | 711
2017-08-06 16:30 | 751 | 750
2017-08-06 17:00 | 815 | 815
2017-08-06 17:30 | 874 | 873
2017-08-06 18:00 | 914 | 905
2017-08-06 18:30 | 924 | 916
2017-08-06 19:00 | 916 | 907
2017-08-06 19:30 | 899 | 893
2017-08-06 20:00 | 881 | 876
2017-08-06 20:30 | 874 | 869
2017-08-06 21:00 | 837 | 836
2017-08-06 21:30 | 808 | 805
2017-08-06 22:00 | 777 | 771
2017-08-06 22:30 | 753 | 749
2017-08-06 23:00 | 749 | 746
2017-08-06 23:30 | 713 | 709
2017-08-07 | 657 | 650
2017-08-07 00:30 | 607 | 596
2017-08-07 01:00 | 580 | 566
2017-08-07 01:30 | 570 | 551
2017-08-07 02:00 | 567 | 543
2017-08-07 02:30 | 558 | 534
2017-08-07 03:00 | 553 | 527
2017-08-07 03:30 | 559 | 534
2017-08-07 04:00 | 561 | 537
2017-08-07 04:30 | 567 | 544
2017-08-07 05:00 | 572 | 554
2017-08-07 05:30 | 611 | 600
2017-08-07 06:00 | 663 | 658
2017-08-07 06:30 | 739 | 738
2017-08-07 07:00 | 810 | 810
2017-08-07 07:30 | 874 | 872
2017-08-07 08:00 | 888 | 888
2017-08-07 08:30 | 853 | 853
2017-08-07 09:00 | 789 | 788
2017-08-07 09:30 | 763 | 762
2017-08-07 10:00 | 764 | 763
2017-08-07 10:30 | 754 | 754
2017-08-07 11:00 | 728 | 728
2017-08-07 11:30 | 716 | 716
2017-08-07 12:00 | 697 | 696
2017-08-07 12:30 | 690 | 689
2017-08-07 13:00 | 688 | 687
2017-08-07 13:30 | 687 | 686
2017-08-07 14:00 | 699 | 698
2017-08-07 14:30 | 711 | 710
2017-08-07 15:00 | 732 | 731
2017-08-07 15:30 | 759 | 759
2017-08-07 16:00 | 805 | 804
2017-08-07 16:30 | 849 | 849
2017-08-07 17:00 | 902 | 902
2017-08-07 17:30 | 944 | 944
2017-08-07 18:00 | 994 | 994
2017-08-07 18:30 | 1002 | 998
2017-08-07 19:00 | 998 | 994
2017-08-07 19:30 | 965 | 961
2017-08-07 20:00 | 939 | 938
2017-08-07 20:30 | 927 | 926
2017-08-07 21:00 | 891 | 889
2017-08-07 21:30 | 839 | 836
2017-08-07 22:00 | 797 | 796
2017-08-07 22:30 | 794 | 793
2017-08-07 23:00 | 791 | 789
2017-08-07 23:30 | 736 | 732
2017-08-08 | 676 | 671
2017-08-08 00:30 | 624 | 616
2017-08-08 01:00 | 600 | 587
2017-08-08 01:30 | 582 | 566
2017-08-08 02:00 | 565 | 547
2017-08-08 02:30 | 554 | 534
2017-08-08 03:00 | 546 | 524
2017-08-08 03:30 | 551 | 529
2017-08-08 04:00 | 559 | 537
2017-08-08 04:30 | 564 | 546
2017-08-08 05:00 | 574 | 560
2017-08-08 05:30 | 619 | 612
2017-08-08 06:00 | 680 | 678
2017-08-08 06:30 | 782 | 780
2017-08-08 07:00 | 862 | 859
2017-08-08 07:30 | 929 | 925
2017-08-08 08:00 | 899 | 894
2017-08-08 08:30 | 851 | 845
2017-08-08 09:00 | 800 | 791
2017-08-08 09:30 | 756 | 747
2017-08-08 10:00 | 715 | 712
2017-08-08 10:30 | 686 | 682
2017-08-08 11:00 | 665 | 660
2017-08-08 11:30 | 644 | 642
2017-08-08 12:00 | 634 | 631
2017-08-08 12:30 | 627 | 625
2017-08-08 13:00 | 629 | 626
2017-08-08 13:30 | 639 | 637
2017-08-08 14:00 | 663 | 662
2017-08-08 14:30 | 677 | 676
2017-08-08 15:00 | 695 | 694
2017-08-08 15:30 | 725 | 725
2017-08-08 16:00 | 774 | 774
2017-08-08 16:30 | 831 | 830
2017-08-08 17:00 | 897 | 897
2017-08-08 17:30 | 947 | 947
2017-08-08 18:00 | 1002 | 1002
2017-08-08 18:30 | 1019 | 1019
2017-08-08 19:00 | 1022 | 1022
2017-08-08 19:30 | 1010 | 1009
2017-08-08 20:00 | 1001 | 1000
2017-08-08 20:30 | 994 | 993
2017-08-08 21:00 | 948 | 947
2017-08-08 21:30 | 905 | 903
2017-08-08 22:00 | 863 | 858
2017-08-08 22:30 | 844 | 836
2017-08-08 23:00 | 828 | 823
2017-08-08 23:30 | 769 | 767
2017-08-09 | 712 | 707
2017-08-09 00:30 | 650 | 643
2017-08-09 01:00 | 620 | 610
2017-08-09 01:30 | 598 | 585
2017-08-09 02:00 | 580 | 564
2017-08-09 02:30 | 568 | 551
2017-08-09 03:00 | 562 | 544
2017-08-09 03:30 | 564 | 545
2017-08-09 04:00 | 562 | 544
2017-08-09 04:30 | 575 | 560
2017-08-09 05:00 | 602 | 591
2017-08-09 05:30 | 655 | 649
2017-08-09 06:00 | 727 | 726
2017-08-09 06:30 | 847 | 843
2017-08-09 07:00 | 937 | 933
2017-08-09 07:30 | 995 | 992
2017-08-09 08:00 | 982 | 980
2017-08-09 08:30 | 916 | 911
2017-08-09 09:00 | 847 | 839
2017-08-09 09:30 | 786 | 783
2017-08-09 10:00 | 743 | 739
2017-08-09 10:30 | 707 | 703
2017-08-09 11:00 | 680 | 678
2017-08-09 11:30 | 657 | 655
2017-08-09 12:00 | 650 | 649
2017-08-09 12:30 | 639 | 639
2017-08-09 13:00 | 640 | 640
2017-08-09 13:30 | 641 | 641
2017-08-09 14:00 | 655 | 655
2017-08-09 14:30 | 684 | 684
2017-08-09 15:00 | 713 | 712
2017-08-09 15:30 | 762 | 762
2017-08-09 16:00 | 792 | 792
2017-08-09 16:30 | 840 | 840
2017-08-09 17:00 | 895 | 895
2017-08-09 17:30 | 944 | 943
2017-08-09 18:00 | 999 | 998
2017-08-09 18:30 | 1019 | 1016
2017-08-09 19:00 | 1030 | 1027
2017-08-09 19:30 | 1018 | 1015
2017-08-09 20:00 | 1011 | 1009
2017-08-09 20:30 | 1006 | 1003
2017-08-09 21:00 | 965 | 962
2017-08-09 21:30 | 920 | 919
2017-08-09 22:00 | 870 | 868
2017-08-09 22:30 | 827 | 826
2017-08-09 23:00 | 810 | 809
2017-08-09 23:30 | 762 | 760
2017-08-10 | 709 | 702
2017-08-10 00:30 | 657 | 647
2017-08-10 01:00 | 619 | 609
2017-08-10 01:30 | 593 | 581
2017-08-10 02:00 | 573 | 558
2017-08-10 02:30 | 562 | 546
2017-08-10 03:00 | 553 | 536
2017-08-10 03:30 | 559 | 542
2017-08-10 04:00 | 562 | 545
2017-08-10 04:30 | 585 | 571
2017-08-10 05:00 | 609 | 599
2017-08-10 05:30 | 661 | 656
2017-08-10 06:00 | 728 | 726
2017-08-10 06:30 | 833 | 832
2017-08-10 07:00 | 926 | 920
2017-08-10 07:30 | 983 | 976
2017-08-10 08:00 | 969 | 963
2017-08-10 08:30 | 907 | 900
2017-08-10 09:00 | 837 | 830
2017-08-10 09:30 | 784 | 782
2017-08-10 10:00 | 745 | 744
2017-08-10 10:30 | 702 | 702
2017-08-10 11:00 | 674 | 673
2017-08-10 11:30 | 653 | 653
2017-08-10 12:00 | 639 | 639
2017-08-10 12:30 | 642 | 642
2017-08-10 13:00 | 653 | 653
2017-08-10 13:30 | 668 | 668
2017-08-10 14:00 | 703 | 702
2017-08-10 14:30 | 725 | 725
2017-08-10 15:00 | 741 | 740
2017-08-10 15:30 | 756 | 755
2017-08-10 16:00 | 783 | 782
2017-08-10 16:30 | 834 | 832
2017-08-10 17:00 | 877 | 876
2017-08-10 17:30 | 918 | 918
2017-08-10 18:00 | 968 | 968
2017-08-10 18:30 | 990 | 984
2017-08-10 19:00 | 997 | 991
2017-08-10 19:30 | 984 | 977
2017-08-10 20:00 | 977 | 969
2017-08-10 20:30 | 961 | 956
2017-08-10 21:00 | 919 | 919
2017-08-10 21:30 | 871 | 870
2017-08-10 22:00 | 835 | 834
2017-08-10 22:30 | 810 | 809
2017-08-10 23:00 | 801 | 800
2017-08-10 23:30 | 754 | 752
2017-08-11 | 699 | 695
2017-08-11 00:30 | 642 | 634
2017-08-11 01:00 | 604 | 594
2017-08-11 01:30 | 583 | 570
2017-08-11 02:00 | 570 | 553
2017-08-11 02:30 | 565 | 546
2017-08-11 03:00 | 548 | 529
2017-08-11 03:30 | 551 | 532
2017-08-11 04:00 | 560 | 540
2017-08-11 04:30 | 577 | 559
2017-08-11 05:00 | 599 | 585
2017-08-11 05:30 | 631 | 623
2017-08-11 06:00 | 692 | 689
2017-08-11 06:30 | 781 | 780
2017-08-11 07:00 | 859 | 859
2017-08-11 07:30 | 907 | 906
2017-08-11 08:00 | 897 | 896
2017-08-11 08:30 | 849 | 846
2017-08-11 09:00 | 791 | 787
2017-08-11 09:30 | 757 | 754
2017-08-11 10:00 | 721 | 721
2017-08-11 10:30 | 699 | 699
2017-08-11 11:00 | 685 | 684
2017-08-11 11:30 | 675 | 674
2017-08-11 12:00 | 668 | 667
2017-08-11 12:30 | 663 | 662
2017-08-11 13:00 | 663 | 663
2017-08-11 13:30 | 662 | 662
2017-08-11 14:00 | 688 | 687
2017-08-11 14:30 | 700 | 699
2017-08-11 15:00 | 720 | 720
2017-08-11 15:30 | 745 | 745
2017-08-11 16:00 | 793 | 793
2017-08-11 16:30 | 832 | 832
2017-08-11 17:00 | 866 | 865
2017-08-11 17:30 | 883 | 882
2017-08-11 18:00 | 911 | 909
2017-08-11 18:30 | 917 | 910
2017-08-11 19:00 | 919 | 913
2017-08-11 19:30 | 893 | 891
2017-08-11 20:00 | 887 | 885
2017-08-11 20:30 | 884 | 881
2017-08-11 21:00 | 856 | 853
2017-08-11 21:30 | 821 | 820
2017-08-11 22:00 | 791 | 789
2017-08-11 22:30 | 791 | 790
2017-08-11 23:00 | 792 | 791
2017-08-11 23:30 | 753 | 750
2017-08-12 | 703 | 698
2017-08-12 00:30 | 646 | 639
2017-08-12 01:00 | 609 | 598
2017-08-12 01:30 | 576 | 563
2017-08-12 02:00 | 566 | 548
2017-08-12 02:30 | 565 | 543
2017-08-12 03:00 | 561 | 538
2017-08-12 03:30 | 562 | 539
2017-08-12 04:00 | 564 | 539
2017-08-12 04:30 | 565 | 542
2017-08-12 05:00 | 565 | 543
2017-08-12 05:30 | 576 | 557
2017-08-12 06:00 | 589 | 575
2017-08-12 06:30 | 605 | 593
2017-08-12 07:00 | 640 | 631
2017-08-12 07:30 | 668 | 663
2017-08-12 08:00 | 675 | 671
2017-08-12 08:30 | 683 | 681
2017-08-12 09:00 | 667 | 666
2017-08-12 09:30 | 646 | 645
2017-08-12 10:00 | 626 | 624
2017-08-12 10:30 | 655 | 654
2017-08-12 11:00 | 697 | 696
2017-08-12 11:30 | 657 | 656
2017-08-12 12:00 | 601 | 599
2017-08-12 12:30 | 623 | 621
2017-08-12 13:00 | 629 | 628
2017-08-12 13:30 | 641 | 640
2017-08-12 14:00 | 638 | 636
2017-08-12 14:30 | 633 | 631
2017-08-12 15:00 | 627 | 626
2017-08-12 15:30 | 646 | 645
2017-08-12 16:00 | 671 | 671
2017-08-12 16:30 | 711 | 711
2017-08-12 17:00 | 759 | 758
2017-08-12 17:30 | 794 | 788
2017-08-12 18:00 | 831 | 829
2017-08-12 18:30 | 852 | 847
2017-08-12 19:00 | 846 | 840
2017-08-12 19:30 | 833 | 826
2017-08-12 20:00 | 819 | 816
2017-08-12 20:30 | 802 | 801
2017-08-12 21:00 | 773 | 773
2017-08-12 21:30 | 746 | 745
2017-08-12 22:00 | 723 | 722
2017-08-12 22:30 | 732 | 730
2017-08-12 23:00 | 744 | 741
2017-08-12 23:30 | 707 | 702
2017-08-13 | 655 | 647
2017-08-13 00:30 | 597 | 585
2017-08-13 01:00 | 570 | 553
2017-08-13 01:30 | 550 | 528
2017-08-13 02:00 | 532 | 506
2017-08-13 02:30 | 522 | 495
2017-08-13 03:00 | 511 | 483
2017-08-13 03:30 | 508 | 479
2017-08-13 04:00 | 510 | 482
2017-08-13 04:30 | 507 | 478
2017-08-13 05:00 | 510 | 482
2017-08-13 05:30 | 519 | 493
2017-08-13 06:00 | 529 | 506
2017-08-13 06:30 | 550 | 528
2017-08-13 07:00 | 571 | 551
2017-08-13 07:30 | 621 | 605
2017-08-13 08:00 | 635 | 623
2017-08-13 08:30 | 650 | 641
2017-08-13 09:00 | 647 | 639
2017-08-13 09:30 | 637 | 630
2017-08-13 10:00 | 630 | 624
2017-08-13 10:30 | 611 | 605
2017-08-13 11:00 | 578 | 571
2017-08-13 11:30 | 589 | 584
2017-08-13 12:00 | 580 | 573
2017-08-13 12:30 | 535 | 530
2017-08-13 13:00 | 533 | 528
2017-08-13 13:30 | 533 | 527
2017-08-13 14:00 | 554 | 549
2017-08-13 14:30 | 575 | 571
2017-08-13 15:00 | 607 | 604
2017-08-13 15:30 | 630 | 627
2017-08-13 16:00 | 661 | 660
2017-08-13 16:30 | 701 | 700
2017-08-13 17:00 | 752 | 749
2017-08-13 17:30 | 799 | 798
2017-08-13 18:00 | 846 | 845
2017-08-13 18:30 | 873 | 872
2017-08-13 19:00 | 865 | 863
2017-08-13 19:30 | 851 | 848
2017-08-13 20:00 | 836 | 835
2017-08-13 20:30 | 829 | 829
2017-08-13 21:00 | 796 | 796
2017-08-13 21:30 | 756 | 756
2017-08-13 22:00 | 726 | 725
2017-08-13 22:30 | 730 | 727
2017-08-13 23:00 | 730 | 727
2017-08-13 23:30 | 682 | 677
2017-08-14 | 631 | 622
2017-08-14 00:30 | 585 | 571
2017-08-14 01:00 | 560 | 543
2017-08-14 01:30 | 544 | 522
2017-08-14 02:00 | 531 | 505
2017-08-14 02:30 | 518 | 491
2017-08-14 03:00 | 511 | 483
2017-08-14 03:30 | 513 | 485
2017-08-14 04:00 | 512 | 484
2017-08-14 04:30 | 522 | 497
2017-08-14 05:00 | 536 | 516
2017-08-14 05:30 | 570 | 557
2017-08-14 06:00 | 620 | 613
2017-08-14 06:30 | 703 | 700
2017-08-14 07:00 | 774 | 773
2017-08-14 07:30 | 842 | 840
2017-08-14 08:00 | 834 | 833
2017-08-14 08:30 | 801 | 800
2017-08-14 09:00 | 753 | 752
2017-08-14 09:30 | 735 | 734
2017-08-14 10:00 | 718 | 716
2017-08-14 10:30 | 696 | 695
2017-08-14 11:00 | 691 | 690
2017-08-14 11:30 | 684 | 683
2017-08-14 12:00 | 669 | 668
2017-08-14 12:30 | 664 | 663
2017-08-14 13:00 | 672 | 671
2017-08-14 13:30 | 697 | 697
2017-08-14 14:00 | 713 | 713
2017-08-14 14:30 | 733 | 732
2017-08-14 15:00 | 725 | 725
2017-08-14 15:30 | 738 | 738
2017-08-14 16:00 | 778 | 777
2017-08-14 16:30 | 824 | 824
2017-08-14 17:00 | 877 | 876
2017-08-14 17:30 | 922 | 922
2017-08-14 18:00 | 969 | 969
2017-08-14 18:30 | 976 | 974
2017-08-14 19:00 | 976 | 973
2017-08-14 19:30 | 952 | 947
2017-08-14 20:00 | 925 | 924
2017-08-14 20:30 | 911 | 910
2017-08-14 21:00 | 863 | 861
2017-08-14 21:30 | 827 | 824
2017-08-14 22:00 | 794 | 789
2017-08-14 22:30 | 774 | 769
2017-08-14 23:00 | 753 | 753
2017-08-14 23:30 | 705 | 704
2017-08-15 | 655 | 651
2017-08-15 00:30 | 603 | 594
2017-08-15 01:00 | 573 | 561
2017-08-15 01:30 | 548 | 534
2017-08-15 02:00 | 534 | 518
2017-08-15 02:30 | 533 | 515
2017-08-15 03:00 | 541 | 521
2017-08-15 03:30 | 544 | 524
2017-08-15 04:00 | 544 | 524
2017-08-15 04:30 | 557 | 540
2017-08-15 05:00 | 564 | 550
2017-08-15 05:30 | 601 | 593
2017-08-15 06:00 | 661 | 658
2017-08-15 06:30 | 761 | 757
2017-08-15 07:00 | 827 | 826
2017-08-15 07:30 | 877 | 876
2017-08-15 08:00 | 860 | 859
2017-08-15 08:30 | 815 | 814
2017-08-15 09:00 | 759 | 757
2017-08-15 09:30 | 733 | 731
2017-08-15 10:00 | 701 | 699
2017-08-15 10:30 | 681 | 678
2017-08-15 11:00 | 669 | 666
2017-08-15 11:30 | 661 | 659
2017-08-15 12:00 | 656 | 654
2017-08-15 12:30 | 654 | 651
2017-08-15 13:00 | 660 | 659
2017-08-15 13:30 | 670 | 670
2017-08-15 14:00 | 695 | 695
2017-08-15 14:30 | 718 | 717
2017-08-15 15:00 | 739 | 739
2017-08-15 15:30 | 760 | 760
2017-08-15 16:00 | 790 | 790
2017-08-15 16:30 | 840 | 840
2017-08-15 17:00 | 887 | 887
2017-08-15 17:30 | 929 | 927
2017-08-15 18:00 | 966 | 965
2017-08-15 18:30 | 983 | 982
2017-08-15 19:00 | 978 | 976
2017-08-15 19:30 | 956 | 953
2017-08-15 20:00 | 940 | 937
2017-08-15 20:30 | 920 | 919
2017-08-15 21:00 | 869 | 869
2017-08-15 21:30 | 825 | 825
2017-08-15 22:00 | 796 | 795
2017-08-15 22:30 | 771 | 768
2017-08-15 23:00 | 764 | 761
2017-08-15 23:30 | 715 | 713
2017-08-16 | 663 | 658
2017-08-16 00:30 | 607 | 598
2017-08-16 01:00 | 577 | 564
2017-08-16 01:30 | 563 | 547
2017-08-16 02:00 | 552 | 534
2017-08-16 02:30 | 565 | 543
2017-08-16 03:00 | 565 | 542
2017-08-16 03:30 | 563 | 539
2017-08-16 04:00 | 570 | 546
2017-08-16 04:30 | 582 | 559
2017-08-16 05:00 | 590 | 570
2017-08-16 05:30 | 613 | 599
2017-08-16 06:00 | 651 | 643
2017-08-16 06:30 | 694 | 690
2017-08-16 07:00 | 741 | 740
2017-08-16 07:30 | 784 | 783
2017-08-16 08:00 | 786 | 785
2017-08-16 08:30 | 768 | 767
2017-08-16 09:00 | 735 | 734
2017-08-16 09:30 | 705 | 704
2017-08-16 10:00 | 687 | 687
2017-08-16 10:30 | 682 | 682
2017-08-16 11:00 | 668 | 667
2017-08-16 11:30 | 654 | 654
2017-08-16 12:00 | 657 | 656
2017-08-16 12:30 | 674 | 673
2017-08-16 13:00 | 675 | 675
2017-08-16 13:30 | 684 | 683
2017-08-16 14:00 | 706 | 706
2017-08-16 14:30 | 703 | 703
2017-08-16 15:00 | 746 | 746
2017-08-16 15:30 | 773 | 773
2017-08-16 16:00 | 805 | 805
2017-08-16 16:30 | 845 | 845
2017-08-16 17:00 | 882 | 880
2017-08-16 17:30 | 913 | 911
2017-08-16 18:00 | 942 | 942
2017-08-16 18:30 | 954 | 953
2017-08-16 19:00 | 950 | 948
2017-08-16 19:30 | 933 | 931
2017-08-16 20:00 | 919 | 918
2017-08-16 20:30 | 909 | 908
2017-08-16 21:00 | 868 | 866
2017-08-16 21:30 | 819 | 818
2017-08-16 22:00 | 783 | 781
2017-08-16 22:30 | 759 | 756
2017-08-16 23:00 | 755 | 751
2017-08-16 23:30 | 718 | 712
2017-08-17 | 680 | 671
2017-08-17 00:30 | 629 | 620
2017-08-17 01:00 | 598 | 586
2017-08-17 01:30 | 577 | 564
2017-08-17 02:00 | 568 | 552
2017-08-17 02:30 | 566 | 547
2017-08-17 03:00 | 562 | 542
2017-08-17 03:30 | 564 | 543
2017-08-17 04:00 | 567 | 546
2017-08-17 04:30 | 578 | 559
2017-08-17 05:00 | 594 | 578
2017-08-17 05:30 | 624 | 615
2017-08-17 06:00 | 665 | 660
2017-08-17 06:30 | 721 | 717
2017-08-17 07:00 | 779 | 777
2017-08-17 07:30 | 828 | 827
2017-08-17 08:00 | 829 | 827
2017-08-17 08:30 | 810 | 809
2017-08-17 09:00 | 793 | 792
2017-08-17 09:30 | 772 | 771
2017-08-17 10:00 | 752 | 752
2017-08-17 10:30 | 745 | 745
2017-08-17 11:00 | 737 | 737
2017-08-17 11:30 | 737 | 737
2017-08-17 12:00 | 742 | 742
2017-08-17 12:30 | 742 | 742
2017-08-17 13:00 | 759 | 759
2017-08-17 13:30 | 772 | 772
2017-08-17 14:00 | 798 | 798
2017-08-17 14:30 | 824 | 824
2017-08-17 15:00 | 842 | 842
2017-08-17 15:30 | 860 | 860
2017-08-17 16:00 | 894 | 894
2017-08-17 16:30 | 925 | 924
2017-08-17 17:00 | 945 | 944
2017-08-17 17:30 | 952 | 951
2017-08-17 18:00 | 990 | 989
2017-08-17 18:30 | 997 | 995
2017-08-17 19:00 | 1000 | 997
2017-08-17 19:30 | 982 | 977
2017-08-17 20:00 | 956 | 952
2017-08-17 20:30 | 939 | 936
2017-08-17 21:00 | 885 | 883
2017-08-17 21:30 | 842 | 839
2017-08-17 22:00 | 790 | 786
2017-08-17 22:30 | 795 | 790
2017-08-17 23:00 | 782 | 780
2017-08-17 23:30 | 723 | 721
2017-08-18 | 662 | 659
2017-08-18 00:30 | 609 | 601
2017-08-18 01:00 | 586 | 575
2017-08-18 01:30 | 564 | 552
2017-08-18 02:00 | 554 | 538
2017-08-18 02:30 | 548 | 530
2017-08-18 03:00 | 544 | 525
2017-08-18 03:30 | 538 | 518
2017-08-18 04:00 | 548 | 528
2017-08-18 04:30 | 559 | 542
2017-08-18 05:00 | 567 | 553
2017-08-18 05:30 | 592 | 583
2017-08-18 06:00 | 635 | 632
2017-08-18 06:30 | 712 | 711
2017-08-18 07:00 | 789 | 788
2017-08-18 07:30 | 824 | 823
2017-08-18 08:00 | 814 | 813
2017-08-18 08:30 | 790 | 789
2017-08-18 09:00 | 752 | 751
2017-08-18 09:30 | 728 | 727
2017-08-18 10:00 | 706 | 705
2017-08-18 10:30 | 685 | 685
2017-08-18 11:00 | 670 | 670
2017-08-18 11:30 | 663 | 663
2017-08-18 12:00 | 658 | 658
2017-08-18 12:30 | 658 | 658
2017-08-18 13:00 | 658 | 658
2017-08-18 13:30 | 661 | 661
2017-08-18 14:00 | 680 | 680
2017-08-18 14:30 | 698 | 697
2017-08-18 15:00 | 707 | 707
2017-08-18 15:30 | 737 | 737
2017-08-18 16:00 | 772 | 772
2017-08-18 16:30 | 811 | 811
2017-08-18 17:00 | 851 | 850
2017-08-18 17:30 | 883 | 882
2017-08-18 18:00 | 898 | 897
2017-08-18 18:30 | 910 | 909
2017-08-18 19:00 | 905 | 904
2017-08-18 19:30 | 873 | 871
2017-08-18 20:00 | 854 | 853
2017-08-18 20:30 | 844 | 843
2017-08-18 21:00 | 812 | 810
2017-08-18 21:30 | 781 | 780
2017-08-18 22:00 | 753 | 752
2017-08-18 22:30 | 745 | 744
2017-08-18 23:00 | 749 | 747
2017-08-18 23:30 | 706 | 704
2017-08-19 | 659 | 655
2017-08-19 00:30 | 612 | 605
2017-08-19 01:00 | 577 | 566
2017-08-19 01:30 | 557 | 543
2017-08-19 02:00 | 534 | 517
2017-08-19 02:30 | 524 | 504
2017-08-19 03:00 | 518 | 496
2017-08-19 03:30 | 514 | 491
2017-08-19 04:00 | 519 | 494
2017-08-19 04:30 | 522 | 498
2017-08-19 05:00 | 529 | 507
2017-08-19 05:30 | 541 | 523
2017-08-19 06:00 | 556 | 542
2017-08-19 06:30 | 590 | 577
2017-08-19 07:00 | 618 | 609
2017-08-19 07:30 | 648 | 644
2017-08-19 08:00 | 654 | 651
2017-08-19 08:30 | 665 | 663
2017-08-19 09:00 | 664 | 663
2017-08-19 09:30 | 652 | 651
2017-08-19 10:00 | 622 | 621
2017-08-19 10:30 | 595 | 593
2017-08-19 11:00 | 571 | 568
2017-08-19 11:30 | 552 | 547
2017-08-19 12:00 | 538 | 533
2017-08-19 12:30 | 526 | 519
2017-08-19 13:00 | 526 | 519
2017-08-19 13:30 | 527 | 520
2017-08-19 14:00 | 538 | 531
2017-08-19 14:30 | 554 | 547
2017-08-19 15:00 | 582 | 576
2017-08-19 15:30 | 606 | 602
2017-08-19 16:00 | 638 | 635
2017-08-19 16:30 | 675 | 674
2017-08-19 17:00 | 722 | 722
2017-08-19 17:30 | 771 | 769
2017-08-19 18:00 | 829 | 827
2017-08-19 18:30 | 869 | 864
2017-08-19 19:00 | 873 | 869
2017-08-19 19:30 | 861 | 856
2017-08-19 20:00 | 850 | 844
2017-08-19 20:30 | 846 | 839
2017-08-19 21:00 | 815 | 805
2017-08-19 21:30 | 782 | 778
2017-08-19 22:00 | 760 | 758
2017-08-19 22:30 | 764 | 764
2017-08-19 23:00 | 765 | 765
2017-08-19 23:30 | 721 | 720
2017-08-20 | 679 | 676
2017-08-20 00:30 | 627 | 619
2017-08-20 01:00 | 601 | 590
2017-08-20 01:30 | 571 | 557
2017-08-20 02:00 | 557 | 539
2017-08-20 02:30 | 545 | 526
2017-08-20 03:00 | 537 | 516
2017-08-20 03:30 | 539 | 517
2017-08-20 04:00 | 539 | 516
2017-08-20 04:30 | 536 | 514
2017-08-20 05:00 | 537 | 515
2017-08-20 05:30 | 544 | 524
2017-08-20 06:00 | 556 | 539
2017-08-20 06:30 | 579 | 563
2017-08-20 07:00 | 602 | 589
2017-08-20 07:30 | 635 | 626
2017-08-20 08:00 | 651 | 645
2017-08-20 08:30 | 663 | 658
2017-08-20 09:00 | 663 | 659
2017-08-20 09:30 | 646 | 642
2017-08-20 10:00 | 623 | 619
2017-08-20 10:30 | 601 | 596
2017-08-20 11:00 | 573 | 566
2017-08-20 11:30 | 553 | 545
2017-08-20 12:00 | 545 | 536
2017-08-20 12:30 | 531 | 520
2017-08-20 13:00 | 534 | 523
2017-08-20 13:30 | 534 | 523
2017-08-20 14:00 | 546 | 535
2017-08-20 14:30 | 565 | 556
2017-08-20 15:00 | 587 | 580
2017-08-20 15:30 | 612 | 606
2017-08-20 16:00 | 649 | 645
2017-08-20 16:30 | 693 | 691
2017-08-20 17:00 | 751 | 750
2017-08-20 17:30 | 810 | 809
2017-08-20 18:00 | 879 | 879
2017-08-20 18:30 | 923 | 922
2017-08-20 19:00 | 924 | 921
2017-08-20 19:30 | 911 | 908
2017-08-20 20:00 | 898 | 894
2017-08-20 20:30 | 883 | 880
2017-08-20 21:00 | 850 | 847
2017-08-20 21:30 | 810 | 807
2017-08-20 22:00 | 779 | 774
2017-08-20 22:30 | 769 | 768
2017-08-20 23:00 | 762 | 761
2017-08-20 23:30 | 710 | 707
2017-08-21 | 664 | 658
2017-08-21 00:30 | 616 | 607
2017-08-21 01:00 | 586 | 573
2017-08-21 01:30 | 564 | 548
2017-08-21 02:00 | 551 | 532
2017-08-21 02:30 | 543 | 522
2017-08-21 03:00 | 537 | 515
2017-08-21 03:30 | 538 | 515
2017-08-21 04:00 | 545 | 523
2017-08-21 04:30 | 550 | 531
2017-08-21 05:00 | 565 | 551
2017-08-21 05:30 | 620 | 613
2017-08-21 06:00 | 693 | 691
2017-08-21 06:30 | 796 | 795
2017-08-21 07:00 | 881 | 879
2017-08-21 07:30 | 902 | 902
2017-08-21 08:00 | 897 | 897
2017-08-21 08:30 | 856 | 856
2017-08-21 09:00 | 804 | 804
2017-08-21 09:30 | 769 | 768
2017-08-21 10:00 | 750 | 749
2017-08-21 10:30 | 725 | 725
2017-08-21 11:00 | 668 | 668
2017-08-21 11:30 | 662 | 661
2017-08-21 12:00 | 661 | 661
2017-08-21 12:30 | 661 | 660
2017-08-21 13:00 | 685 | 684
2017-08-21 13:30 | 701 | 699
2017-08-21 14:00 | 720 | 720
2017-08-21 14:30 | 715 | 715
2017-08-21 15:00 | 739 | 739
2017-08-21 15:30 | 778 | 778
2017-08-21 16:00 | 824 | 824
2017-08-21 16:30 | 861 | 860
2017-08-21 17:00 | 910 | 909
2017-08-21 17:30 | 966 | 966
2017-08-21 18:00 | 1012 | 1012
2017-08-21 18:30 | 1012 | 1011
2017-08-21 19:00 | 1010 | 1009
2017-08-21 19:30 | 987 | 985
2017-08-21 20:00 | 975 | 973
2017-08-21 20:30 | 959 | 958
2017-08-21 21:00 | 905 | 905
2017-08-21 21:30 | 857 | 857
2017-08-21 22:00 | 817 | 815
2017-08-21 22:30 | 804 | 801
2017-08-21 23:00 | 795 | 793
2017-08-21 23:30 | 748 | 746
2017-08-22 | 680 | 677
2017-08-22 00:30 | 631 | 625
2017-08-22 01:00 | 596 | 587
2017-08-22 01:30 | 567 | 556
2017-08-22 02:00 | 546 | 533
2017-08-22 02:30 | 531 | 515
2017-08-22 03:00 | 520 | 504
2017-08-22 03:30 | 519 | 503
2017-08-22 04:00 | 529 | 514
2017-08-22 04:30 | 545 | 533
2017-08-22 05:00 | 559 | 550
2017-08-22 05:30 | 604 | 599
2017-08-22 06:00 | 666 | 665
2017-08-22 06:30 | 756 | 755
2017-08-22 07:00 | 825 | 824
2017-08-22 07:30 | 868 | 868
2017-08-22 08:00 | 857 | 857
2017-08-22 08:30 | 820 | 820
2017-08-22 09:00 | 783 | 783
2017-08-22 09:30 | 742 | 741
2017-08-22 10:00 | 723 | 722
2017-08-22 10:30 | 704 | 704
2017-08-22 11:00 | 696 | 696
2017-08-22 11:30 | 679 | 679
2017-08-22 12:00 | 677 | 677
2017-08-22 12:30 | 671 | 671
2017-08-22 13:00 | 675 | 675
2017-08-22 13:30 | 689 | 689
2017-08-22 14:00 | 720 | 720
2017-08-22 14:30 | 729 | 729
2017-08-22 15:00 | 751 | 750
2017-08-22 15:30 | 765 | 764
2017-08-22 16:00 | 801 | 800
2017-08-22 16:30 | 840 | 840
2017-08-22 17:00 | 891 | 891
2017-08-22 17:30 | 936 | 935
2017-08-22 18:00 | 972 | 972
2017-08-22 18:30 | 982 | 982
2017-08-22 19:00 | 984 | 983
2017-08-22 19:30 | 957 | 955
2017-08-22 20:00 | 949 | 946
2017-08-22 20:30 | 935 | 931
2017-08-22 21:00 | 883 | 881
2017-08-22 21:30 | 847 | 846
2017-08-22 22:00 | 803 | 802
2017-08-22 22:30 | 795 | 793
2017-08-22 23:00 | 778 | 776
2017-08-22 23:30 | 729 | 728
2017-08-23 | 669 | 665
2017-08-23 00:30 | 623 | 617
2017-08-23 01:00 | 586 | 576
2017-08-23 01:30 | 563 | 551
2017-08-23 02:00 | 542 | 528
2017-08-23 02:30 | 535 | 519
2017-08-23 03:00 | 523 | 504
2017-08-23 03:30 | 521 | 502
2017-08-23 04:00 | 524 | 505
2017-08-23 04:30 | 531 | 515
2017-08-23 05:00 | 545 | 532
2017-08-23 05:30 | 590 | 584
2017-08-23 06:00 | 649 | 646
2017-08-23 06:30 | 717 | 715
2017-08-23 07:00 | 777 | 777
2017-08-23 07:30 | 838 | 837
2017-08-23 08:00 | 835 | 834
2017-08-23 08:30 | 820 | 820
2017-08-23 09:00 | 789 | 788
2017-08-23 09:30 | 765 | 764
2017-08-23 10:00 | 746 | 746
2017-08-23 10:30 | 738 | 738
2017-08-23 11:00 | 709 | 708
2017-08-23 11:30 | 690 | 689
2017-08-23 12:00 | 686 | 685
2017-08-23 12:30 | 686 | 685
2017-08-23 13:00 | 672 | 672
2017-08-23 13:30 | 684 | 684
2017-08-23 14:00 | 700 | 700
2017-08-23 14:30 | 731 | 731
2017-08-23 15:00 | 753 | 753
2017-08-23 15:30 | 769 | 769
2017-08-23 16:00 | 817 | 817
2017-08-23 16:30 | 856 | 855
2017-08-23 17:00 | 891 | 891
2017-08-23 17:30 | 932 | 932
2017-08-23 18:00 | 966 | 966
2017-08-23 18:30 | 972 | 971
2017-08-23 19:00 | 974 | 972
2017-08-23 19:30 | 946 | 943
2017-08-23 20:00 | 934 | 933
2017-08-23 20:30 | 921 | 921
2017-08-23 21:00 | 878 | 878
2017-08-23 21:30 | 837 | 834
2017-08-23 22:00 | 803 | 800
2017-08-23 22:30 | 780 | 779
2017-08-23 23:00 | 765 | 764
2017-08-23 23:30 | 730 | 728
2017-08-24 | 683 | 679
2017-08-24 00:30 | 629 | 623
2017-08-24 01:00 | 592 | 583
2017-08-24 01:30 | 562 | 551
2017-08-24 02:00 | 544 | 531
2017-08-24 02:30 | 540 | 526
2017-08-24 03:00 | 530 | 513
2017-08-24 03:30 | 540 | 523
2017-08-24 04:00 | 543 | 527
2017-08-24 04:30 | 555 | 540
2017-08-24 05:00 | 566 | 554
2017-08-24 05:30 | 610 | 604
2017-08-24 06:00 | 663 | 662
2017-08-24 06:30 | 735 | 735
2017-08-24 07:00 | 804 | 803
2017-08-24 07:30 | 875 | 874
2017-08-24 08:00 | 891 | 891
2017-08-24 08:30 | 888 | 887
2017-08-24 09:00 | 863 | 862
2017-08-24 09:30 | 826 | 825
2017-08-24 10:00 | 820 | 819
2017-08-24 10:30 | 849 | 848
2017-08-24 11:00 | 833 | 832
2017-08-24 11:30 | 795 | 793
2017-08-24 12:00 | 776 | 775
2017-08-24 12:30 | 744 | 743
2017-08-24 13:00 | 713 | 713
2017-08-24 13:30 | 717 | 717
2017-08-24 14:00 | 752 | 752
2017-08-24 14:30 | 767 | 767
2017-08-24 15:00 | 783 | 783
2017-08-24 15:30 | 839 | 839
2017-08-24 16:00 | 870 | 870
2017-08-24 16:30 | 906 | 906
2017-08-24 17:00 | 926 | 926
2017-08-24 17:30 | 942 | 942
2017-08-24 18:00 | 982 | 982
2017-08-24 18:30 | 1005 | 1004
2017-08-24 19:00 | 1010 | 1009
2017-08-24 19:30 | 994 | 992
2017-08-24 20:00 | 978 | 978
2017-08-24 20:30 | 963 | 962
2017-08-24 21:00 | 914 | 913
2017-08-24 21:30 | 868 | 866
2017-08-24 22:00 | 816 | 816
2017-08-24 22:30 | 810 | 810
2017-08-24 23:00 | 796 | 796
2017-08-24 23:30 | 743 | 743
2017-08-25 | 680 | 677
2017-08-25 00:30 | 629 | 624
2017-08-25 01:00 | 595 | 587
2017-08-25 01:30 | 577 | 565
2017-08-25 02:00 | 560 | 546
2017-08-25 02:30 | 549 | 534
2017-08-25 03:00 | 541 | 524
2017-08-25 03:30 | 539 | 523
2017-08-25 04:00 | 541 | 525
2017-08-25 04:30 | 551 | 536
2017-08-25 05:00 | 570 | 559
2017-08-25 05:30 | 612 | 606
2017-08-25 06:00 | 670 | 669
2017-08-25 06:30 | 753 | 753
2017-08-25 07:00 | 821 | 821
2017-08-25 07:30 | 869 | 869
2017-08-25 08:00 | 858 | 854
2017-08-25 08:30 | 806 | 801
2017-08-25 09:00 | 752 | 745
2017-08-25 09:30 | 722 | 714
2017-08-25 10:00 | 698 | 695
2017-08-25 10:30 | 673 | 672
2017-08-25 11:00 | 670 | 669
2017-08-25 11:30 | 676 | 676
2017-08-25 12:00 | 676 | 676
2017-08-25 12:30 | 693 | 693
2017-08-25 13:00 | 694 | 694
2017-08-25 13:30 | 703 | 703
2017-08-25 14:00 | 711 | 711
2017-08-25 14:30 | 716 | 716
2017-08-25 15:00 | 704 | 704
2017-08-25 15:30 | 727 | 726
2017-08-25 16:00 | 771 | 771
2017-08-25 16:30 | 824 | 823
2017-08-25 17:00 | 872 | 872
2017-08-25 17:30 | 900 | 900
2017-08-25 18:00 | 944 | 944
2017-08-25 18:30 | 963 | 962
2017-08-25 19:00 | 977 | 975
2017-08-25 19:30 | 959 | 957
2017-08-25 20:00 | 953 | 952
2017-08-25 20:30 | 944 | 943
2017-08-25 21:00 | 908 | 907
2017-08-25 21:30 | 871 | 871
2017-08-25 22:00 | 843 | 843
2017-08-25 22:30 | 826 | 826
2017-08-25 23:00 | 826 | 826
2017-08-25 23:30 | 771 | 770
2017-08-26 | 704 | 700
2017-08-26 00:30 | 648 | 641
2017-08-26 01:00 | 624 | 613
2017-08-26 01:30 | 600 | 586
2017-08-26 02:00 | 583 | 566
2017-08-26 02:30 | 562 | 541
2017-08-26 03:00 | 551 | 529
2017-08-26 03:30 | 548 | 524
2017-08-26 04:00 | 541 | 518
2017-08-26 04:30 | 547 | 526
2017-08-26 05:00 | 558 | 537
2017-08-26 05:30 | 575 | 559
2017-08-26 06:00 | 600 | 586
2017-08-26 06:30 | 619 | 607
2017-08-26 07:00 | 650 | 641
2017-08-26 07:30 | 676 | 671
2017-08-26 08:00 | 683 | 680
2017-08-26 08:30 | 682 | 680
2017-08-26 09:00 | 665 | 664
2017-08-26 09:30 | 640 | 638
2017-08-26 10:00 | 614 | 612
2017-08-26 10:30 | 587 | 585
2017-08-26 11:00 | 568 | 565
2017-08-26 11:30 | 552 | 549
2017-08-26 12:00 | 546 | 542
2017-08-26 12:30 | 545 | 539
2017-08-26 13:00 | 555 | 547
2017-08-26 13:30 | 562 | 555
2017-08-26 14:00 | 574 | 567
2017-08-26 14:30 | 586 | 580
2017-08-26 15:00 | 601 | 595
2017-08-26 15:30 | 619 | 614
2017-08-26 16:00 | 649 | 646
2017-08-26 16:30 | 704 | 702
2017-08-26 17:00 | 759 | 758
2017-08-26 17:30 | 795 | 795
2017-08-26 18:00 | 836 | 836
2017-08-26 18:30 | 866 | 860
2017-08-26 19:00 | 867 | 862
2017-08-26 19:30 | 856 | 848
2017-08-26 20:00 | 844 | 836
2017-08-26 20:30 | 842 | 834
2017-08-26 21:00 | 798 | 797
2017-08-26 21:30 | 770 | 770
2017-08-26 22:00 | 756 | 754
2017-08-26 22:30 | 760 | 758
2017-08-26 23:00 | 763 | 760
2017-08-26 23:30 | 728 | 724
2017-08-27 | 692 | 684
2017-08-27 00:30 | 632 | 620
2017-08-27 01:00 | 597 | 580
2017-08-27 01:30 | 569 | 549
2017-08-27 02:00 | 547 | 523
2017-08-27 02:30 | 536 | 510
2017-08-27 03:00 | 530 | 503
2017-08-27 03:30 | 515 | 492
2017-08-27 04:00 | 514 | 490
2017-08-27 04:30 | 518 | 494
2017-08-27 05:00 | 533 | 511
2017-08-27 05:30 | 540 | 520
2017-08-27 06:00 | 550 | 532
2017-08-27 06:30 | 563 | 544
2017-08-27 07:00 | 584 | 567
2017-08-27 07:30 | 605 | 593
2017-08-27 08:00 | 626 | 617
2017-08-27 08:30 | 618 | 612
2017-08-27 09:00 | 617 | 611
2017-08-27 09:30 | 617 | 613
2017-08-27 10:00 | 612 | 608
2017-08-27 10:30 | 592 | 588
2017-08-27 11:00 | 587 | 584
2017-08-27 11:30 | 590 | 587
2017-08-27 12:00 | 562 | 558
2017-08-27 12:30 | 552 | 547
2017-08-27 13:00 | 552 | 547
2017-08-27 13:30 | 579 | 575
2017-08-27 14:00 | 592 | 588
2017-08-27 14:30 | 600 | 597
2017-08-27 15:00 | 607 | 603
2017-08-27 15:30 | 620 | 617
2017-08-27 16:00 | 657 | 655
2017-08-27 16:30 | 684 | 683
2017-08-27 17:00 | 742 | 741
2017-08-27 17:30 | 787 | 787
2017-08-27 18:00 | 836 | 835
2017-08-27 18:30 | 874 | 869
2017-08-27 19:00 | 880 | 874
2017-08-27 19:30 | 865 | 856
2017-08-27 20:00 | 849 | 841
2017-08-27 20:30 | 846 | 840
2017-08-27 21:00 | 813 | 810
2017-08-27 21:30 | 781 | 781
2017-08-27 22:00 | 752 | 752
2017-08-27 22:30 | 744 | 743
2017-08-27 23:00 | 740 | 738
2017-08-27 23:30 | 702 | 699
2017-08-28 | 654 | 648
2017-08-28 00:30 | 605 | 595
2017-08-28 01:00 | 578 | 567
2017-08-28 01:30 | 551 | 536
2017-08-28 02:00 | 537 | 520
2017-08-28 02:30 | 534 | 514
2017-08-28 03:00 | 520 | 501
2017-08-28 03:30 | 524 | 505
2017-08-28 04:00 | 526 | 507
2017-08-28 04:30 | 540 | 525
2017-08-28 05:00 | 569 | 559
2017-08-28 05:30 | 618 | 611
2017-08-28 06:00 | 679 | 675
2017-08-28 06:30 | 774 | 772
2017-08-28 07:00 | 852 | 849
2017-08-28 07:30 | 897 | 892
2017-08-28 08:00 | 860 | 856
2017-08-28 08:30 | 812 | 806
2017-08-28 09:00 | 762 | 755
2017-08-28 09:30 | 718 | 714
2017-08-28 10:00 | 687 | 685
2017-08-28 10:30 | 661 | 661
2017-08-28 11:00 | 636 | 635
2017-08-28 11:30 | 619 | 618
2017-08-28 12:00 | 616 | 615
2017-08-28 12:30 | 614 | 613
2017-08-28 13:00 | 615 | 614
2017-08-28 13:30 | 624 | 623
2017-08-28 14:00 | 638 | 637
2017-08-28 14:30 | 651 | 651
2017-08-28 15:00 | 671 | 671
2017-08-28 15:30 | 697 | 696
2017-08-28 16:00 | 740 | 740
2017-08-28 16:30 | 800 | 800
2017-08-28 17:00 | 860 | 860
2017-08-28 17:30 | 920 | 920
2017-08-28 18:00 | 982 | 981
2017-08-28 18:30 | 1006 | 1004
2017-08-28 19:00 | 1015 | 1012
2017-08-28 19:30 | 973 | 970
2017-08-28 20:00 | 956 | 956
2017-08-28 20:30 | 948 | 947
2017-08-28 21:00 | 902 | 900
2017-08-28 21:30 | 845 | 845
2017-08-28 22:00 | 809 | 809
2017-08-28 22:30 | 789 | 787
2017-08-28 23:00 | 776 | 776
2017-08-28 23:30 | 725 | 725
2017-08-29 | 673 | 672
2017-08-29 00:30 | 625 | 622
2017-08-29 01:00 | 591 | 585
2017-08-29 01:30 | 563 | 555
2017-08-29 02:00 | 545 | 536
2017-08-29 02:30 | 536 | 525
2017-08-29 03:00 | 526 | 513
2017-08-29 03:30 | 522 | 509
2017-08-29 04:00 | 522 | 511
2017-08-29 04:30 | 537 | 528
2017-08-29 05:00 | 556 | 550
2017-08-29 05:30 | 602 | 600
2017-08-29 06:00 | 671 | 670
2017-08-29 06:30 | 785 | 784
2017-08-29 07:00 | 874 | 869
2017-08-29 07:30 | 922 | 920
2017-08-29 08:00 | 902 | 897
2017-08-29 08:30 | 838 | 828
2017-08-29 09:00 | 783 | 770
2017-08-29 09:30 | 729 | 724
2017-08-29 10:00 | 695 | 692
2017-08-29 10:30 | 665 | 663
2017-08-29 11:00 | 640 | 638
2017-08-29 11:30 | 627 | 625
2017-08-29 12:00 | 629 | 628
2017-08-29 12:30 | 623 | 622
2017-08-29 13:00 | 630 | 630
2017-08-29 13:30 | 634 | 634
2017-08-29 14:00 | 650 | 649
2017-08-29 14:30 | 666 | 665
2017-08-29 15:00 | 693 | 692
2017-08-29 15:30 | 722 | 722
2017-08-29 16:00 | 765 | 764
2017-08-29 16:30 | 813 | 813
2017-08-29 17:00 | 867 | 867
2017-08-29 17:30 | 904 | 904
2017-08-29 18:00 | 961 | 959
2017-08-29 18:30 | 982 | 978
2017-08-29 19:00 | 986 | 981
2017-08-29 19:30 | 964 | 960
2017-08-29 20:00 | 942 | 941
2017-08-29 20:30 | 929 | 928
2017-08-29 21:00 | 878 | 877
2017-08-29 21:30 | 843 | 843
2017-08-29 22:00 | 807 | 806
2017-08-29 22:30 | 777 | 777
2017-08-29 23:00 | 769 | 769
2017-08-29 23:30 | 720 | 720
2017-08-30 | 664 | 662
2017-08-30 00:30 | 616 | 611
2017-08-30 01:00 | 582 | 574
2017-08-30 01:30 | 556 | 545
2017-08-30 02:00 | 538 | 524
2017-08-30 02:30 | 524 | 509
2017-08-30 03:00 | 520 | 504
2017-08-30 03:30 | 519 | 503
2017-08-30 04:00 | 525 | 510
2017-08-30 04:30 | 535 | 522
2017-08-30 05:00 | 559 | 549
2017-08-30 05:30 | 611 | 607
2017-08-30 06:00 | 670 | 668
2017-08-30 06:30 | 756 | 756
2017-08-30 07:00 | 821 | 821
2017-08-30 07:30 | 855 | 855
2017-08-30 08:00 | 840 | 840
2017-08-30 08:30 | 787 | 787
2017-08-30 09:00 | 731 | 731
2017-08-30 09:30 | 698 | 698
2017-08-30 10:00 | 676 | 676
2017-08-30 10:30 | 662 | 662
2017-08-30 11:00 | 641 | 640
2017-08-30 11:30 | 631 | 631
2017-08-30 12:00 | 633 | 633
2017-08-30 12:30 | 623 | 622
2017-08-30 13:00 | 624 | 624
2017-08-30 13:30 | 634 | 634
2017-08-30 14:00 | 654 | 654
2017-08-30 14:30 | 662 | 661
2017-08-30 15:00 | 680 | 680
2017-08-30 15:30 | 714 | 713
2017-08-30 16:00 | 763 | 762
2017-08-30 16:30 | 812 | 812
2017-08-30 17:00 | 861 | 861
2017-08-30 17:30 | 893 | 893
2017-08-30 18:00 | 934 | 933
2017-08-30 18:30 | 968 | 965
2017-08-30 19:00 | 979 | 976
2017-08-30 19:30 | 957 | 953
2017-08-30 20:00 | 944 | 942
2017-08-30 20:30 | 930 | 929
2017-08-30 21:00 | 890 | 889
2017-08-30 21:30 | 852 | 851
2017-08-30 22:00 | 804 | 804
2017-08-30 22:30 | 779 | 779
2017-08-30 23:00 | 769 | 767
2017-08-30 23:30 | 724 | 721
2017-08-31 | 673 | 669
2017-08-31 00:30 | 626 | 619
2017-08-31 01:00 | 591 | 582
2017-08-31 01:30 | 569 | 556
2017-08-31 02:00 | 550 | 535
2017-08-31 02:30 | 538 | 523
2017-08-31 03:00 | 532 | 515
2017-08-31 03:30 | 534 | 517
2017-08-31 04:00 | 532 | 516
2017-08-31 04:30 | 538 | 525
2017-08-31 05:00 | 556 | 547
2017-08-31 05:30 | 609 | 605
2017-08-31 06:00 | 669 | 669
2017-08-31 06:30 | 753 | 753
2017-08-31 07:00 | 824 | 824
2017-08-31 07:30 | 857 | 857
2017-08-31 08:00 | 836 | 836
2017-08-31 08:30 | 791 | 791
2017-08-31 09:00 | 726 | 726
2017-08-31 09:30 | 683 | 683
2017-08-31 10:00 | 654 | 654
2017-08-31 10:30 | 634 | 634
2017-08-31 11:00 | 657 | 657
2017-08-31 11:30 | 650 | 650
2017-08-31 12:00 | 645 | 644
2017-08-31 12:30 | 657 | 657
2017-08-31 13:00 | 667 | 667
2017-08-31 13:30 | 659 | 659
2017-08-31 14:00 | 659 | 658
2017-08-31 14:30 | 688 | 688
2017-08-31 15:00 | 698 | 697
2017-08-31 15:30 | 718 | 718
2017-08-31 16:00 | 755 | 755
2017-08-31 16:30 | 801 | 801
2017-08-31 17:00 | 851 | 850
2017-08-31 17:30 | 895 | 895
2017-08-31 18:00 | 948 | 948
2017-08-31 18:30 | 982 | 981
2017-08-31 19:00 | 984 | 983
2017-08-31 19:30 | 969 | 968
2017-08-31 20:00 | 962 | 961
2017-08-31 20:30 | 956 | 954
2017-08-31 21:00 | 910 | 909
2017-08-31 21:30 | 868 | 867
2017-08-31 22:00 | 820 | 819
2017-08-31 22:30 | 809 | 808
2017-08-31 23:00 | 805 | 805
2017-08-31 23:30 | 750 | 750
2017-09-01 | 688 | 686
2017-09-01 00:30 | 630 | 626
2017-09-01 01:00 | 591 | 584
2017-09-01 01:30 | 569 | 560
2017-09-01 02:00 | 560 | 548
2017-09-01 02:30 | 546 | 533
2017-09-01 03:00 | 537 | 523
2017-09-01 03:30 | 536 | 522
2017-09-01 04:00 | 527 | 514
2017-09-01 04:30 | 539 | 526
2017-09-01 05:00 | 560 | 551
2017-09-01 05:30 | 591 | 586
2017-09-01 06:00 | 636 | 631
2017-09-01 06:30 | 713 | 711
2017-09-01 07:00 | 767 | 765
2017-09-01 07:30 | 804 | 803
2017-09-01 08:00 | 796 | 795
2017-09-01 08:30 | 755 | 752
2017-09-01 09:00 | 715 | 713
2017-09-01 09:30 | 689 | 689
2017-09-01 10:00 | 659 | 658
2017-09-01 10:30 | 640 | 639
2017-09-01 11:00 | 618 | 617
2017-09-01 11:30 | 623 | 621
2017-09-01 12:00 | 623 | 621
2017-09-01 12:30 | 608 | 606
2017-09-01 13:00 | 604 | 603
2017-09-01 13:30 | 595 | 594
2017-09-01 14:00 | 611 | 611
2017-09-01 14:30 | 617 | 617
2017-09-01 15:00 | 643 | 642
2017-09-01 15:30 | 678 | 677
2017-09-01 16:00 | 722 | 722
2017-09-01 16:30 | 771 | 771
2017-09-01 17:00 | 822 | 822
2017-09-01 17:30 | 853 | 852
2017-09-01 18:00 | 897 | 897
2017-09-01 18:30 | 924 | 923
2017-09-01 19:00 | 923 | 921
2017-09-01 19:30 | 912 | 910
2017-09-01 20:00 | 903 | 901
2017-09-01 20:30 | 901 | 900
2017-09-01 21:00 | 865 | 865
2017-09-01 21:30 | 826 | 825
2017-09-01 22:00 | 800 | 798
2017-09-01 22:30 | 791 | 789
2017-09-01 23:00 | 788 | 787
2017-09-01 23:30 | 747 | 745
2017-09-02 | 689 | 684
2017-09-02 00:30 | 636 | 626
2017-09-02 01:00 | 616 | 603
2017-09-02 01:30 | 595 | 578
2017-09-02 02:00 | 571 | 551
2017-09-02 02:30 | 561 | 539
2017-09-02 03:00 | 548 | 525
2017-09-02 03:30 | 547 | 523
2017-09-02 04:00 | 544 | 520
2017-09-02 04:30 | 548 | 523
2017-09-02 05:00 | 549 | 526
2017-09-02 05:30 | 566 | 547
2017-09-02 06:00 | 585 | 570
2017-09-02 06:30 | 605 | 592
2017-09-02 07:00 | 625 | 615
2017-09-02 07:30 | 656 | 649
2017-09-02 08:00 | 663 | 658
2017-09-02 08:30 | 657 | 654
2017-09-02 09:00 | 650 | 648
2017-09-02 09:30 | 635 | 632
2017-09-02 10:00 | 608 | 606
2017-09-02 10:30 | 597 | 594
2017-09-02 11:00 | 581 | 578
2017-09-02 11:30 | 566 | 562
2017-09-02 12:00 | 549 | 545
2017-09-02 12:30 | 538 | 533
2017-09-02 13:00 | 527 | 521
2017-09-02 13:30 | 529 | 523
2017-09-02 14:00 | 543 | 537
2017-09-02 14:30 | 555 | 550
2017-09-02 15:00 | 574 | 570
2017-09-02 15:30 | 606 | 603
2017-09-02 16:00 | 637 | 634
2017-09-02 16:30 | 683 | 682
2017-09-02 17:00 | 733 | 733
2017-09-02 17:30 | 759 | 759
2017-09-02 18:00 | 793 | 792
2017-09-02 18:30 | 829 | 828
2017-09-02 19:00 | 836 | 834
2017-09-02 19:30 | 822 | 819
2017-09-02 20:00 | 814 | 810
2017-09-02 20:30 | 804 | 803
2017-09-02 21:00 | 770 | 769
2017-09-02 21:30 | 750 | 749
2017-09-02 22:00 | 739 | 737
2017-09-02 22:30 | 735 | 732
2017-09-02 23:00 | 741 | 738
2017-09-02 23:30 | 703 | 698
2017-09-03 | 669 | 661
2017-09-03 00:30 | 622 | 610
2017-09-03 01:00 | 591 | 576
2017-09-03 01:30 | 567 | 548
2017-09-03 02:00 | 546 | 523
2017-09-03 02:30 | 541 | 514
2017-09-03 03:00 | 536 | 509
2017-09-03 03:30 | 538 | 510
2017-09-03 04:00 | 535 | 505
2017-09-03 04:30 | 541 | 512
2017-09-03 05:00 | 548 | 520
2017-09-03 05:30 | 550 | 525
2017-09-03 06:00 | 553 | 529
2017-09-03 06:30 | 554 | 530
2017-09-03 07:00 | 566 | 545
2017-09-03 07:30 | 581 | 565
2017-09-03 08:00 | 583 | 571
2017-09-03 08:30 | 599 | 590
2017-09-03 09:00 | 601 | 595
2017-09-03 09:30 | 598 | 593
2017-09-03 10:00 | 586 | 581
2017-09-03 10:30 | 571 | 566
2017-09-03 11:00 | 559 | 553
2017-09-03 11:30 | 542 | 535
2017-09-03 12:00 | 537 | 530
2017-09-03 12:30 | 534 | 526
2017-09-03 13:00 | 544 | 537
2017-09-03 13:30 | 545 | 538
2017-09-03 14:00 | 569 | 562
2017-09-03 14:30 | 574 | 569
2017-09-03 15:00 | 591 | 586
2017-09-03 15:30 | 622 | 619
2017-09-03 16:00 | 665 | 663
2017-09-03 16:30 | 704 | 702
2017-09-03 17:00 | 733 | 732
2017-09-03 17:30 | 754 | 754
2017-09-03 18:00 | 793 | 793
2017-09-03 18:30 | 825 | 824
2017-09-03 19:00 | 833 | 831
2017-09-03 19:30 | 825 | 821
2017-09-03 20:00 | 806 | 803
2017-09-03 20:30 | 800 | 798
2017-09-03 21:00 | 772 | 769
2017-09-03 21:30 | 745 | 744
2017-09-03 22:00 | 728 | 727
2017-09-03 22:30 | 721 | 718
2017-09-03 23:00 | 718 | 715
2017-09-03 23:30 | 686 | 682
2017-09-04 | 650 | 642
2017-09-04 00:30 | 603 | 590
2017-09-04 01:00 | 575 | 557
2017-09-04 01:30 | 552 | 532
2017-09-04 02:00 | 543 | 518
2017-09-04 02:30 | 542 | 515
2017-09-04 03:00 | 546 | 517
2017-09-04 03:30 | 547 | 518
2017-09-04 04:00 | 556 | 528
2017-09-04 04:30 | 556 | 531
2017-09-04 05:00 | 573 | 552
2017-09-04 05:30 | 601 | 588
2017-09-04 06:00 | 650 | 640
2017-09-04 06:30 | 703 | 699
2017-09-04 07:00 | 753 | 753
2017-09-04 07:30 | 790 | 790
2017-09-04 08:00 | 793 | 793
2017-09-04 08:30 | 773 | 773
2017-09-04 09:00 | 751 | 750
2017-09-04 09:30 | 734 | 734
2017-09-04 10:00 | 723 | 723
2017-09-04 10:30 | 712 | 711
2017-09-04 11:00 | 693 | 691
2017-09-04 11:30 | 689 | 687
2017-09-04 12:00 | 699 | 696
2017-09-04 12:30 | 708 | 706
2017-09-04 13:00 | 723 | 719
2017-09-04 13:30 | 744 | 741
2017-09-04 14:00 | 770 | 769
2017-09-04 14:30 | 791 | 790
2017-09-04 15:00 | 800 | 800
2017-09-04 15:30 | 820 | 819
2017-09-04 16:00 | 846 | 845
2017-09-04 16:30 | 875 | 875
2017-09-04 17:00 | 909 | 909
2017-09-04 17:30 | 928 | 928
2017-09-04 18:00 | 939 | 939
2017-09-04 18:30 | 950 | 950
2017-09-04 19:00 | 949 | 949
2017-09-04 19:30 | 924 | 921
2017-09-04 20:00 | 904 | 902
2017-09-04 20:30 | 895 | 893
2017-09-04 21:00 | 858 | 854
2017-09-04 21:30 | 817 | 813
2017-09-04 22:00 | 782 | 777
2017-09-04 22:30 | 762 | 759
2017-09-04 23:00 | 749 | 747
2017-09-04 23:30 | 714 | 711
2017-09-05 | 668 | 661
2017-09-05 00:30 | 623 | 611
2017-09-05 01:00 | 603 | 590
2017-09-05 01:30 | 578 | 563
2017-09-05 02:00 | 553 | 535
2017-09-05 02:30 | 556 | 536
2017-09-05 03:00 | 566 | 545
2017-09-05 03:30 | 553 | 531
2017-09-05 04:00 | 540 | 518
2017-09-05 04:30 | 563 | 543
2017-09-05 05:00 | 564 | 549
2017-09-05 05:30 | 596 | 588
2017-09-05 06:00 | 635 | 629
2017-09-05 06:30 | 715 | 712
2017-09-05 07:00 | 761 | 759
2017-09-05 07:30 | 799 | 798
2017-09-05 08:00 | 776 | 774
2017-09-05 08:30 | 745 | 742
2017-09-05 09:00 | 699 | 696
2017-09-05 09:30 | 671 | 670
2017-09-05 10:00 | 671 | 671
2017-09-05 10:30 | 657 | 657
2017-09-05 11:00 | 648 | 647
2017-09-05 11:30 | 647 | 646
2017-09-05 12:00 | 640 | 638
2017-09-05 12:30 | 641 | 641
2017-09-05 13:00 | 658 | 658
2017-09-05 13:30 | 656 | 656
2017-09-05 14:00 | 685 | 685
2017-09-05 14:30 | 705 | 705
2017-09-05 15:00 | 729 | 729
2017-09-05 15:30 | 760 | 760
2017-09-05 16:00 | 802 | 801
2017-09-05 16:30 | 847 | 847
2017-09-05 17:00 | 871 | 871
2017-09-05 17:30 | 889 | 889
2017-09-05 18:00 | 917 | 917
2017-09-05 18:30 | 950 | 949
2017-09-05 19:00 | 948 | 946
2017-09-05 19:30 | 924 | 921
2017-09-05 20:00 | 906 | 905
2017-09-05 20:30 | 893 | 892
2017-09-05 21:00 | 857 | 857
2017-09-05 21:30 | 810 | 809
2017-09-05 22:00 | 779 | 777
2017-09-05 22:30 | 763 | 761
2017-09-05 23:00 | 748 | 747
2017-09-05 23:30 | 709 | 707
2017-09-06 | 650 | 646
2017-09-06 00:30 | 594 | 586
2017-09-06 01:00 | 569 | 557
2017-09-06 01:30 | 547 | 533
2017-09-06 02:00 | 538 | 522
2017-09-06 02:30 | 538 | 518
2017-09-06 03:00 | 541 | 520
2017-09-06 03:30 | 552 | 532
2017-09-06 04:00 | 555 | 535
2017-09-06 04:30 | 562 | 544
2017-09-06 05:00 | 580 | 567
2017-09-06 05:30 | 620 | 612
2017-09-06 06:00 | 666 | 661
2017-09-06 06:30 | 739 | 736
2017-09-06 07:00 | 786 | 784
2017-09-06 07:30 | 819 | 816
2017-09-06 08:00 | 805 | 803
2017-09-06 08:30 | 771 | 769
2017-09-06 09:00 | 729 | 726
2017-09-06 09:30 | 692 | 689
2017-09-06 10:00 | 662 | 659
2017-09-06 10:30 | 641 | 638
2017-09-06 11:00 | 631 | 627
2017-09-06 11:30 | 618 | 614
2017-09-06 12:00 | 616 | 613
2017-09-06 12:30 | 617 | 614
2017-09-06 13:00 | 632 | 630
2017-09-06 13:30 | 648 | 646
2017-09-06 14:00 | 670 | 669
2017-09-06 14:30 | 689 | 689
2017-09-06 15:00 | 717 | 717
2017-09-06 15:30 | 746 | 746
2017-09-06 16:00 | 793 | 793
2017-09-06 16:30 | 835 | 834
2017-09-06 17:00 | 874 | 873
2017-09-06 17:30 | 897 | 895
2017-09-06 18:00 | 930 | 928
2017-09-06 18:30 | 963 | 957
2017-09-06 19:00 | 964 | 957
2017-09-06 19:30 | 948 | 938
2017-09-06 20:00 | 932 | 923
2017-09-06 20:30 | 911 | 908
2017-09-06 21:00 | 860 | 860
2017-09-06 21:30 | 819 | 819
2017-09-06 22:00 | 778 | 778
2017-09-06 22:30 | 775 | 773
2017-09-06 23:00 | 767 | 765
2017-09-06 23:30 | 721 | 719
2017-09-07 | 663 | 659
2017-09-07 00:30 | 625 | 617
2017-09-07 01:00 | 588 | 577
2017-09-07 01:30 | 568 | 555
2017-09-07 02:00 | 556 | 540
2017-09-07 02:30 | 551 | 532
2017-09-07 03:00 | 542 | 522
2017-09-07 03:30 | 543 | 522
2017-09-07 04:00 | 544 | 523
2017-09-07 04:30 | 554 | 536
2017-09-07 05:00 | 575 | 560
2017-09-07 05:30 | 627 | 618
2017-09-07 06:00 | 675 | 670
2017-09-07 06:30 | 734 | 732
2017-09-07 07:00 | 781 | 779
2017-09-07 07:30 | 818 | 815
2017-09-07 08:00 | 792 | 790
2017-09-07 08:30 | 747 | 744
2017-09-07 09:00 | 707 | 704
2017-09-07 09:30 | 671 | 668
2017-09-07 10:00 | 661 | 658
2017-09-07 10:30 | 648 | 646
2017-09-07 11:00 | 637 | 635
2017-09-07 11:30 | 637 | 635
2017-09-07 12:00 | 623 | 622
2017-09-07 12:30 | 626 | 624
2017-09-07 13:00 | 632 | 632
2017-09-07 13:30 | 634 | 634
2017-09-07 14:00 | 656 | 656
2017-09-07 14:30 | 677 | 676
2017-09-07 15:00 | 698 | 697
2017-09-07 15:30 | 732 | 731
2017-09-07 16:00 | 782 | 780
2017-09-07 16:30 | 826 | 826
2017-09-07 17:00 | 873 | 872
2017-09-07 17:30 | 895 | 893
2017-09-07 18:00 | 925 | 924
2017-09-07 18:30 | 950 | 949
2017-09-07 19:00 | 957 | 957
2017-09-07 19:30 | 938 | 937
2017-09-07 20:00 | 929 | 927
2017-09-07 20:30 | 912 | 911
2017-09-07 21:00 | 866 | 866
2017-09-07 21:30 | 827 | 825
2017-09-07 22:00 | 786 | 785
2017-09-07 22:30 | 781 | 781
2017-09-07 23:00 | 773 | 772
2017-09-07 23:30 | 723 | 721
2017-09-08 | 664 | 660
2017-09-08 00:30 | 619 | 611
2017-09-08 01:00 | 585 | 575
2017-09-08 01:30 | 561 | 548
2017-09-08 02:00 | 543 | 528
2017-09-08 02:30 | 538 | 522
2017-09-08 03:00 | 537 | 520
2017-09-08 03:30 | 533 | 515
2017-09-08 04:00 | 531 | 513
2017-09-08 04:30 | 545 | 529
2017-09-08 05:00 | 568 | 556
2017-09-08 05:30 | 618 | 612
2017-09-08 06:00 | 670 | 666
2017-09-08 06:30 | 740 | 738
2017-09-08 07:00 | 790 | 789
2017-09-08 07:30 | 830 | 830
2017-09-08 08:00 | 817 | 816
2017-09-08 08:30 | 778 | 777
2017-09-08 09:00 | 721 | 721
2017-09-08 09:30 | 681 | 680
2017-09-08 10:00 | 654 | 654
2017-09-08 10:30 | 641 | 641
2017-09-08 11:00 | 631 | 631
2017-09-08 11:30 | 622 | 622
2017-09-08 12:00 | 620 | 618
2017-09-08 12:30 | 621 | 618
2017-09-08 13:00 | 627 | 624
2017-09-08 13:30 | 634 | 632
2017-09-08 14:00 | 643 | 642
2017-09-08 14:30 | 660 | 659
2017-09-08 15:00 | 677 | 677
2017-09-08 15:30 | 706 | 705
2017-09-08 16:00 | 752 | 752
2017-09-08 16:30 | 797 | 797
2017-09-08 17:00 | 837 | 837
2017-09-08 17:30 | 851 | 851
2017-09-08 18:00 | 870 | 869
2017-09-08 18:30 | 890 | 888
2017-09-08 19:00 | 894 | 891
2017-09-08 19:30 | 877 | 874
2017-09-08 20:00 | 865 | 864
2017-09-08 20:30 | 846 | 845
2017-09-08 21:00 | 805 | 803
2017-09-08 21:30 | 777 | 776
2017-09-08 22:00 | 752 | 752
2017-09-08 22:30 | 750 | 749
2017-09-08 23:00 | 752 | 750
2017-09-08 23:30 | 704 | 702
2017-09-09 | 657 | 653
2017-09-09 00:30 | 617 | 610
2017-09-09 01:00 | 589 | 579
2017-09-09 01:30 | 560 | 548
2017-09-09 02:00 | 544 | 528
2017-09-09 02:30 | 540 | 522
2017-09-09 03:00 | 529 | 509
2017-09-09 03:30 | 526 | 505
2017-09-09 04:00 | 513 | 491
2017-09-09 04:30 | 512 | 491
2017-09-09 05:00 | 518 | 499
2017-09-09 05:30 | 534 | 519
2017-09-09 06:00 | 558 | 544
2017-09-09 06:30 | 588 | 576
2017-09-09 07:00 | 606 | 597
2017-09-09 07:30 | 617 | 611
2017-09-09 08:00 | 613 | 609
2017-09-09 08:30 | 616 | 614
2017-09-09 09:00 | 605 | 603
2017-09-09 09:30 | 591 | 589
2017-09-09 10:00 | 574 | 572
2017-09-09 10:30 | 552 | 550
2017-09-09 11:00 | 535 | 533
2017-09-09 11:30 | 524 | 521
2017-09-09 12:00 | 512 | 508
2017-09-09 12:30 | 502 | 498
2017-09-09 13:00 | 503 | 499
2017-09-09 13:30 | 511 | 507
2017-09-09 14:00 | 526 | 522
2017-09-09 14:30 | 544 | 540
2017-09-09 15:00 | 570 | 567
2017-09-09 15:30 | 596 | 594
2017-09-09 16:00 | 642 | 641
2017-09-09 16:30 | 689 | 689
2017-09-09 17:00 | 734 | 734
2017-09-09 17:30 | 767 | 767
2017-09-09 18:00 | 794 | 794
2017-09-09 18:30 | 826 | 825
2017-09-09 19:00 | 834 | 833
2017-09-09 19:30 | 816 | 815
2017-09-09 20:00 | 806 | 804
2017-09-09 20:30 | 799 | 796
2017-09-09 21:00 | 767 | 762
2017-09-09 21:30 | 738 | 737
2017-09-09 22:00 | 722 | 721
2017-09-09 22:30 | 715 | 713
2017-09-09 23:00 | 725 | 722
2017-09-09 23:30 | 692 | 688
2017-09-10 | 651 | 645
2017-09-10 00:30 | 604 | 593
2017-09-10 01:00 | 573 | 560
2017-09-10 01:30 | 541 | 525
2017-09-10 02:00 | 522 | 503
2017-09-10 02:30 | 511 | 489
2017-09-10 03:00 | 504 | 480
2017-09-10 03:30 | 497 | 470
2017-09-10 04:00 | 490 | 463
2017-09-10 04:30 | 484 | 458
2017-09-10 05:00 | 485 | 459
2017-09-10 05:30 | 502 | 479
2017-09-10 06:00 | 522 | 500
2017-09-10 06:30 | 535 | 512
2017-09-10 07:00 | 538 | 518
2017-09-10 07:30 | 537 | 522
2017-09-10 08:00 | 547 | 535
2017-09-10 08:30 | 553 | 543
2017-09-10 09:00 | 554 | 547
2017-09-10 09:30 | 545 | 538
2017-09-10 10:00 | 534 | 528
2017-09-10 10:30 | 527 | 522
2017-09-10 11:00 | 512 | 507
2017-09-10 11:30 | 503 | 498
2017-09-10 12:00 | 495 | 490
2017-09-10 12:30 | 488 | 483
2017-09-10 13:00 | 489 | 483
2017-09-10 13:30 | 493 | 488
2017-09-10 14:00 | 506 | 501
2017-09-10 14:30 | 520 | 516
2017-09-10 15:00 | 550 | 546
2017-09-10 15:30 | 580 | 578
2017-09-10 16:00 | 635 | 634
2017-09-10 16:30 | 685 | 684
2017-09-10 17:00 | 738 | 738
2017-09-10 17:30 | 787 | 785
2017-09-10 18:00 | 823 | 821
2017-09-10 18:30 | 864 | 857
2017-09-10 19:00 | 880 | 874
2017-09-10 19:30 | 862 | 852
2017-09-10 20:00 | 841 | 836
2017-09-10 20:30 | 833 | 831
2017-09-10 21:00 | 802 | 798
2017-09-10 21:30 | 769 | 767
2017-09-10 22:00 | 737 | 736
2017-09-10 22:30 | 737 | 735
2017-09-10 23:00 | 742 | 739
2017-09-10 23:30 | 702 | 698
2017-09-11 | 647 | 640
2017-09-11 00:30 | 594 | 582
2017-09-11 01:00 | 562 | 547
2017-09-11 01:30 | 544 | 526
2017-09-11 02:00 | 529 | 509
2017-09-11 02:30 | 527 | 505
2017-09-11 03:00 | 527 | 503
2017-09-11 03:30 | 529 | 506
2017-09-11 04:00 | 525 | 502
2017-09-11 04:30 | 536 | 516
2017-09-11 05:00 | 549 | 533
2017-09-11 05:30 | 604 | 595
2017-09-11 06:00 | 648 | 643
2017-09-11 06:30 | 713 | 710
2017-09-11 07:00 | 774 | 767
2017-09-11 07:30 | 803 | 800
2017-09-11 08:00 | 792 | 790
2017-09-11 08:30 | 771 | 766
2017-09-11 09:00 | 731 | 727
2017-09-11 09:30 | 704 | 700
2017-09-11 10:00 | 680 | 677
2017-09-11 10:30 | 663 | 660
2017-09-11 11:00 | 649 | 646
2017-09-11 11:30 | 643 | 640
2017-09-11 12:00 | 646 | 643
2017-09-11 12:30 | 652 | 649
2017-09-11 13:00 | 660 | 658
2017-09-11 13:30 | 674 | 673
2017-09-11 14:00 | 693 | 691
2017-09-11 14:30 | 710 | 709
2017-09-11 15:00 | 734 | 732
2017-09-11 15:30 | 768 | 763
2017-09-11 16:00 | 815 | 808
2017-09-11 16:30 | 848 | 842
2017-09-11 17:00 | 875 | 869
2017-09-11 17:30 | 902 | 896
2017-09-11 18:00 | 934 | 930
2017-09-11 18:30 | 952 | 948
2017-09-11 19:00 | 955 | 950
2017-09-11 19:30 | 932 | 925
2017-09-11 20:00 | 899 | 896
2017-09-11 20:30 | 893 | 891
2017-09-11 21:00 | 849 | 847
2017-09-11 21:30 | 801 | 800
2017-09-11 22:00 | 768 | 768
2017-09-11 22:30 | 750 | 749
2017-09-11 23:00 | 747 | 745
2017-09-11 23:30 | 705 | 702
2017-09-12 | 665 | 660
2017-09-12 00:30 | 620 | 610
2017-09-12 01:00 | 592 | 579
2017-09-12 01:30 | 575 | 560
2017-09-12 02:00 | 558 | 540
2017-09-12 02:30 | 546 | 527
2017-09-12 03:00 | 540 | 519
2017-09-12 03:30 | 540 | 519
2017-09-12 04:00 | 539 | 519
2017-09-12 04:30 | 550 | 532
2017-09-12 05:00 | 563 | 549
2017-09-12 05:30 | 612 | 604
2017-09-12 06:00 | 657 | 651
2017-09-12 06:30 | 710 | 708
2017-09-12 07:00 | 767 | 767
2017-09-12 07:30 | 809 | 807
2017-09-12 08:00 | 793 | 791
2017-09-12 08:30 | 766 | 765
2017-09-12 09:00 | 734 | 733
2017-09-12 09:30 | 695 | 694
2017-09-12 10:00 | 677 | 676
2017-09-12 10:30 | 680 | 680
2017-09-12 11:00 | 674 | 674
2017-09-12 11:30 | 673 | 672
2017-09-12 12:00 | 682 | 682
2017-09-12 12:30 | 689 | 689
2017-09-12 13:00 | 706 | 706
2017-09-12 13:30 | 725 | 725
2017-09-12 14:00 | 743 | 743
2017-09-12 14:30 | 764 | 764
2017-09-12 15:00 | 795 | 794
2017-09-12 15:30 | 805 | 805
2017-09-12 16:00 | 837 | 837
2017-09-12 16:30 | 866 | 866
2017-09-12 17:00 | 896 | 896
2017-09-12 17:30 | 919 | 919
2017-09-12 18:00 | 933 | 933
2017-09-12 18:30 | 956 | 956
2017-09-12 19:00 | 964 | 953
2017-09-12 19:30 | 932 | 927
2017-09-12 20:00 | 906 | 906
2017-09-12 20:30 | 893 | 892
2017-09-12 21:00 | 851 | 851
2017-09-12 21:30 | 811 | 811
2017-09-12 22:00 | 773 | 772
2017-09-12 22:30 | 758 | 757
2017-09-12 23:00 | 749 | 748
2017-09-12 23:30 | 708 | 704
2017-09-13 | 664 | 658
2017-09-13 00:30 | 613 | 604
2017-09-13 01:00 | 577 | 565
2017-09-13 01:30 | 559 | 545
2017-09-13 02:00 | 548 | 532
2017-09-13 02:30 | 541 | 522
2017-09-13 03:00 | 532 | 511
2017-09-13 03:30 | 533 | 511
2017-09-13 04:00 | 540 | 519
2017-09-13 04:30 | 557 | 537
2017-09-13 05:00 | 571 | 555
2017-09-13 05:30 | 613 | 603
2017-09-13 06:00 | 659 | 652
2017-09-13 06:30 | 713 | 706
2017-09-13 07:00 | 756 | 754
2017-09-13 07:30 | 796 | 796
2017-09-13 08:00 | 792 | 792
2017-09-13 08:30 | 776 | 776
2017-09-13 09:00 | 748 | 748
2017-09-13 09:30 | 733 | 733
2017-09-13 10:00 | 718 | 718
2017-09-13 10:30 | 712 | 711
2017-09-13 11:00 | 706 | 706
2017-09-13 11:30 | 702 | 702
2017-09-13 12:00 | 710 | 708
2017-09-13 12:30 | 715 | 713
2017-09-13 13:00 | 732 | 730
2017-09-13 13:30 | 741 | 740
2017-09-13 14:00 | 763 | 763
2017-09-13 14:30 | 779 | 778
2017-09-13 15:00 | 802 | 802
2017-09-13 15:30 | 834 | 834
2017-09-13 16:00 | 871 | 871
2017-09-13 16:30 | 888 | 887
2017-09-13 17:00 | 924 | 924
2017-09-13 17:30 | 931 | 930
2017-09-13 18:00 | 957 | 956
2017-09-13 18:30 | 975 | 969
2017-09-13 19:00 | 975 | 968
2017-09-13 19:30 | 954 | 944
2017-09-13 20:00 | 929 | 923
2017-09-13 20:30 | 912 | 908
2017-09-13 21:00 | 868 | 867
2017-09-13 21:30 | 821 | 820
2017-09-13 22:00 | 798 | 795
2017-09-13 22:30 | 776 | 770
2017-09-13 23:00 | 761 | 752
2017-09-13 23:30 | 722 | 710
2017-09-14 | 675 | 658
2017-09-14 00:30 | 623 | 609
2017-09-14 01:00 | 602 | 585
2017-09-14 01:30 | 574 | 556
2017-09-14 02:00 | 559 | 539
2017-09-14 02:30 | 557 | 535
2017-09-14 03:00 | 554 | 531
2017-09-14 03:30 | 552 | 528
2017-09-14 04:00 | 545 | 521
2017-09-14 04:30 | 564 | 543
2017-09-14 05:00 | 577 | 560
2017-09-14 05:30 | 618 | 607
2017-09-14 06:00 | 654 | 646
2017-09-14 06:30 | 710 | 705
2017-09-14 07:00 | 744 | 741
2017-09-14 07:30 | 808 | 803
2017-09-14 08:00 | 856 | 851
2017-09-14 08:30 | 887 | 884
2017-09-14 09:00 | 861 | 855
2017-09-14 09:30 | 825 | 817
2017-09-14 10:00 | 779 | 770
2017-09-14 10:30 | 718 | 706
2017-09-14 11:00 | 667 | 657
2017-09-14 11:30 | 650 | 639
2017-09-14 12:00 | 671 | 662
2017-09-14 12:30 | 669 | 667
2017-09-14 13:00 | 672 | 671
2017-09-14 13:30 | 672 | 670
2017-09-14 14:00 | 673 | 671
2017-09-14 14:30 | 694 | 690
2017-09-14 15:00 | 711 | 707
2017-09-14 15:30 | 739 | 736
2017-09-14 16:00 | 784 | 782
2017-09-14 16:30 | 817 | 815
2017-09-14 17:00 | 866 | 864
2017-09-14 17:30 | 887 | 885
2017-09-14 18:00 | 916 | 916
2017-09-14 18:30 | 956 | 951
2017-09-14 19:00 | 960 | 952
2017-09-14 19:30 | 939 | 928
2017-09-14 20:00 | 913 | 903
2017-09-14 20:30 | 890 | 885
2017-09-14 21:00 | 851 | 849
2017-09-14 21:30 | 803 | 803
2017-09-14 22:00 | 779 | 778
2017-09-14 22:30 | 768 | 765
2017-09-14 23:00 | 760 | 756
2017-09-14 23:30 | 721 | 715
2017-09-15 | 675 | 666
2017-09-15 00:30 | 622 | 608
2017-09-15 01:00 | 597 | 581
2017-09-15 01:30 | 577 | 559
2017-09-15 02:00 | 565 | 544
2017-09-15 02:30 | 561 | 538
2017-09-15 03:00 | 561 | 536
2017-09-15 03:30 | 562 | 536
2017-09-15 04:00 | 567 | 543
2017-09-15 04:30 | 582 | 560
2017-09-15 05:00 | 600 | 583
2017-09-15 05:30 | 638 | 627
2017-09-15 06:00 | 673 | 665
2017-09-15 06:30 | 730 | 727
2017-09-15 07:00 | 766 | 762
2017-09-15 07:30 | 797 | 792
2017-09-15 08:00 | 790 | 786
2017-09-15 08:30 | 771 | 768
2017-09-15 09:00 | 731 | 727
2017-09-15 09:30 | 704 | 700
2017-09-15 10:00 | 681 | 678
2017-09-15 10:30 | 656 | 656
2017-09-15 11:00 | 652 | 652
2017-09-15 11:30 | 648 | 648
2017-09-15 12:00 | 643 | 643
2017-09-15 12:30 | 641 | 641
2017-09-15 13:00 | 644 | 644
2017-09-15 13:30 | 652 | 652
2017-09-15 14:00 | 665 | 665
2017-09-15 14:30 | 677 | 676
2017-09-15 15:00 | 694 | 694
2017-09-15 15:30 | 705 | 705
2017-09-15 16:00 | 748 | 748
2017-09-15 16:30 | 784 | 783
2017-09-15 17:00 | 810 | 810
2017-09-15 17:30 | 829 | 828
2017-09-15 18:00 | 852 | 852
2017-09-15 18:30 | 880 | 880
2017-09-15 19:00 | 893 | 892
2017-09-15 19:30 | 881 | 880
2017-09-15 20:00 | 874 | 871
2017-09-15 20:30 | 869 | 868
2017-09-15 21:00 | 835 | 835
2017-09-15 21:30 | 808 | 808
2017-09-15 22:00 | 788 | 788
2017-09-15 22:30 | 775 | 773
2017-09-15 23:00 | 765 | 763
2017-09-15 23:30 | 731 | 726
2017-09-16 | 688 | 680
2017-09-16 00:30 | 646 | 632
2017-09-16 01:00 | 622 | 606
2017-09-16 01:30 | 603 | 584
2017-09-16 02:00 | 589 | 567
2017-09-16 02:30 | 578 | 555
2017-09-16 03:00 | 574 | 551
2017-09-16 03:30 | 569 | 545
2017-09-16 04:00 | 570 | 546
2017-09-16 04:30 | 574 | 550
2017-09-16 05:00 | 582 | 558
2017-09-16 05:30 | 599 | 579
2017-09-16 06:00 | 611 | 591
2017-09-16 06:30 | 633 | 616
2017-09-16 07:00 | 642 | 628
2017-09-16 07:30 | 653 | 643
2017-09-16 08:00 | 652 | 647
2017-09-16 08:30 | 658 | 655
2017-09-16 09:00 | 651 | 649
2017-09-16 09:30 | 637 | 636
2017-09-16 10:00 | 620 | 618
2017-09-16 10:30 | 608 | 606
2017-09-16 11:00 | 589 | 587
2017-09-16 11:30 | 575 | 572
2017-09-16 12:00 | 567 | 564
2017-09-16 12:30 | 558 | 556
2017-09-16 13:00 | 558 | 555
2017-09-16 13:30 | 564 | 561
2017-09-16 14:00 | 578 | 576
2017-09-16 14:30 | 593 | 591
2017-09-16 15:00 | 615 | 613
2017-09-16 15:30 | 641 | 640
2017-09-16 16:00 | 669 | 668
2017-09-16 16:30 | 713 | 712
2017-09-16 17:00 | 744 | 743
2017-09-16 17:30 | 758 | 758
2017-09-16 18:00 | 795 | 794
2017-09-16 18:30 | 836 | 835
2017-09-16 19:00 | 847 | 846
2017-09-16 19:30 | 836 | 834
2017-09-16 20:00 | 818 | 816
2017-09-16 20:30 | 810 | 810
2017-09-16 21:00 | 789 | 788
2017-09-16 21:30 | 754 | 752
2017-09-16 22:00 | 735 | 732
2017-09-16 22:30 | 734 | 730
2017-09-16 23:00 | 730 | 725
2017-09-16 23:30 | 699 | 691
2017-09-17 | 659 | 648
2017-09-17 00:30 | 615 | 600
2017-09-17 01:00 | 592 | 575
2017-09-17 01:30 | 577 | 559
2017-09-17 02:00 | 566 | 543
2017-09-17 02:30 | 556 | 530
2017-09-17 03:00 | 554 | 527
2017-09-17 03:30 | 554 | 526
2017-09-17 04:00 | 549 | 522
2017-09-17 04:30 | 547 | 520
2017-09-17 05:00 | 551 | 525
2017-09-17 05:30 | 558 | 534
2017-09-17 06:00 | 556 | 527
2017-09-17 06:30 | 574 | 548
2017-09-17 07:00 | 588 | 564
2017-09-17 07:30 | 605 | 588
2017-09-17 08:00 | 625 | 612
2017-09-17 08:30 | 639 | 631
2017-09-17 09:00 | 643 | 636
2017-09-17 09:30 | 643 | 637
2017-09-17 10:00 | 644 | 640
2017-09-17 10:30 | 628 | 623
2017-09-17 11:00 | 609 | 603
2017-09-17 11:30 | 592 | 586
2017-09-17 12:00 | 573 | 566
2017-09-17 12:30 | 580 | 573
2017-09-17 13:00 | 587 | 580
2017-09-17 13:30 | 583 | 576
2017-09-17 14:00 | 593 | 587
2017-09-17 14:30 | 608 | 603
2017-09-17 15:00 | 626 | 621
2017-09-17 15:30 | 651 | 646
2017-09-17 16:00 | 676 | 673
2017-09-17 16:30 | 686 | 683
2017-09-17 17:00 | 710 | 708
2017-09-17 17:30 | 735 | 734
2017-09-17 18:00 | 779 | 779
2017-09-17 18:30 | 833 | 832
2017-09-17 19:00 | 841 | 840
2017-09-17 19:30 | 824 | 821
2017-09-17 20:00 | 813 | 810
2017-09-17 20:30 | 809 | 805
2017-09-17 21:00 | 780 | 774
2017-09-17 21:30 | 749 | 747
2017-09-17 22:00 | 730 | 727
2017-09-17 22:30 | 728 | 724
2017-09-17 23:00 | 731 | 725
2017-09-17 23:30 | 695 | 688
2017-09-18 | 650 | 638
2017-09-18 00:30 | 598 | 582
2017-09-18 01:00 | 572 | 551
2017-09-18 01:30 | 547 | 524
2017-09-18 02:00 | 533 | 508
2017-09-18 02:30 | 528 | 501
2017-09-18 03:00 | 526 | 498
2017-09-18 03:30 | 528 | 499
2017-09-18 04:00 | 531 | 503
2017-09-18 04:30 | 538 | 512
2017-09-18 05:00 | 554 | 533
2017-09-18 05:30 | 600 | 586
2017-09-18 06:00 | 648 | 638
2017-09-18 06:30 | 693 | 687
2017-09-18 07:00 | 728 | 726
2017-09-18 07:30 | 756 | 756
2017-09-18 08:00 | 759 | 759
2017-09-18 08:30 | 758 | 757
2017-09-18 09:00 | 749 | 748
2017-09-18 09:30 | 752 | 751
2017-09-18 10:00 | 734 | 734
2017-09-18 10:30 | 708 | 708
2017-09-18 11:00 | 688 | 685
2017-09-18 11:30 | 671 | 669
2017-09-18 12:00 | 658 | 656
2017-09-18 12:30 | 655 | 652
2017-09-18 13:00 | 664 | 661
2017-09-18 13:30 | 672 | 669
2017-09-18 14:00 | 686 | 683
2017-09-18 14:30 | 696 | 694
2017-09-18 15:00 | 721 | 720
2017-09-18 15:30 | 745 | 743
2017-09-18 16:00 | 779 | 778
2017-09-18 16:30 | 823 | 822
2017-09-18 17:00 | 857 | 856
2017-09-18 17:30 | 878 | 876
2017-09-18 18:00 | 901 | 899
2017-09-18 18:30 | 923 | 922
2017-09-18 19:00 | 931 | 928
2017-09-18 19:30 | 904 | 900
2017-09-18 20:00 | 892 | 887
2017-09-18 20:30 | 874 | 869
2017-09-18 21:00 | 849 | 842
2017-09-18 21:30 | 806 | 802
2017-09-18 22:00 | 772 | 769
2017-09-18 22:30 | 765 | 760
2017-09-18 23:00 | 761 | 755
2017-09-18 23:30 | 720 | 710
2017-09-19 | 674 | 660
2017-09-19 00:30 | 622 | 602
2017-09-19 01:00 | 593 | 569
2017-09-19 01:30 | 573 | 544
2017-09-19 02:00 | 563 | 530
2017-09-19 02:30 | 552 | 517
2017-09-19 03:00 | 533 | 506
2017-09-19 03:30 | 533 | 505
2017-09-19 04:00 | 530 | 503
2017-09-19 04:30 | 538 | 515
2017-09-19 05:00 | 556 | 537
2017-09-19 05:30 | 601 | 589
2017-09-19 06:00 | 646 | 636
2017-09-19 06:30 | 687 | 682
2017-09-19 07:00 | 725 | 723
2017-09-19 07:30 | 750 | 750
2017-09-19 08:00 | 743 | 743
2017-09-19 08:30 | 741 | 741
2017-09-19 09:00 | 727 | 727
2017-09-19 09:30 | 710 | 710
2017-09-19 10:00 | 689 | 688
2017-09-19 10:30 | 678 | 678
2017-09-19 11:00 | 677 | 676
2017-09-19 11:30 | 673 | 673
2017-09-19 12:00 | 682 | 682
2017-09-19 12:30 | 687 | 687
2017-09-19 13:00 | 710 | 710
2017-09-19 13:30 | 722 | 722
2017-09-19 14:00 | 741 | 740
2017-09-19 14:30 | 767 | 766
2017-09-19 15:00 | 798 | 797
2017-09-19 15:30 | 820 | 820
2017-09-19 16:00 | 847 | 846
2017-09-19 16:30 | 871 | 871
2017-09-19 17:00 | 897 | 896
2017-09-19 17:30 | 912 | 911
2017-09-19 18:00 | 936 | 935
2017-09-19 18:30 | 954 | 953
2017-09-19 19:00 | 955 | 952
2017-09-19 19:30 | 937 | 932
2017-09-19 20:00 | 926 | 920
2017-09-19 20:30 | 913 | 904
2017-09-19 21:00 | 874 | 868
2017-09-19 21:30 | 847 | 839
2017-09-19 22:00 | 816 | 809
2017-09-19 22:30 | 796 | 789
2017-09-19 23:00 | 784 | 783
2017-09-19 23:30 | 738 | 736
2017-09-20 | 686 | 680
2017-09-20 00:30 | 630 | 620
2017-09-20 01:00 | 600 | 585
2017-09-20 01:30 | 577 | 561
2017-09-20 02:00 | 562 | 541
2017-09-20 02:30 | 547 | 524
2017-09-20 03:00 | 546 | 522
2017-09-20 03:30 | 551 | 526
2017-09-20 04:00 | 558 | 535
2017-09-20 04:30 | 555 | 533
2017-09-20 05:00 | 571 | 553
2017-09-20 05:30 | 604 | 592
2017-09-20 06:00 | 645 | 635
2017-09-20 06:30 | 698 | 694
2017-09-20 07:00 | 736 | 735
2017-09-20 07:30 | 768 | 768
2017-09-20 08:00 | 767 | 767
2017-09-20 08:30 | 753 | 753
2017-09-20 09:00 | 739 | 739
2017-09-20 09:30 | 717 | 717
2017-09-20 10:00 | 698 | 697
2017-09-20 10:30 | 691 | 691
2017-09-20 11:00 | 681 | 681
2017-09-20 11:30 | 677 | 676
2017-09-20 12:00 | 678 | 678
2017-09-20 12:30 | 679 | 679
2017-09-20 13:00 | 689 | 689
2017-09-20 13:30 | 695 | 695
2017-09-20 14:00 | 720 | 720
2017-09-20 14:30 | 730 | 730
2017-09-20 15:00 | 753 | 753
2017-09-20 15:30 | 781 | 781
2017-09-20 16:00 | 814 | 814
2017-09-20 16:30 | 849 | 848
2017-09-20 17:00 | 880 | 879
2017-09-20 17:30 | 894 | 893
2017-09-20 18:00 | 914 | 913
2017-09-20 18:30 | 930 | 930
2017-09-20 19:00 | 930 | 929
2017-09-20 19:30 | 912 | 910
2017-09-20 20:00 | 897 | 895
2017-09-20 20:30 | 885 | 883
2017-09-20 21:00 | 840 | 840
2017-09-20 21:30 | 808 | 807
2017-09-20 22:00 | 785 | 784
2017-09-20 22:30 | 768 | 765
2017-09-20 23:00 | 762 | 759
2017-09-20 23:30 | 717 | 714
2017-09-21 | 670 | 663
2017-09-21 00:30 | 607 | 596
2017-09-21 01:00 | 589 | 574
2017-09-21 01:30 | 565 | 548
2017-09-21 02:00 | 549 | 527
2017-09-21 02:30 | 546 | 523
2017-09-21 03:00 | 540 | 516
2017-09-21 03:30 | 540 | 514
2017-09-21 04:00 | 538 | 513
2017-09-21 04:30 | 548 | 525
2017-09-21 05:00 | 568 | 549
2017-09-21 05:30 | 601 | 588
2017-09-21 06:00 | 635 | 624
2017-09-21 06:30 | 689 | 684
2017-09-21 07:00 | 722 | 720
2017-09-21 07:30 | 756 | 756
2017-09-21 08:00 | 762 | 762
2017-09-21 08:30 | 755 | 755
2017-09-21 09:00 | 760 | 759
2017-09-21 09:30 | 788 | 788
2017-09-21 10:00 | 770 | 770
2017-09-21 10:30 | 754 | 754
2017-09-21 11:00 | 735 | 735
2017-09-21 11:30 | 729 | 728
2017-09-21 12:00 | 727 | 725
2017-09-21 12:30 | 723 | 721
2017-09-21 13:00 | 726 | 723
2017-09-21 13:30 | 732 | 730
2017-09-21 14:00 | 748 | 746
2017-09-21 14:30 | 757 | 755
2017-09-21 15:00 | 769 | 767
2017-09-21 15:30 | 800 | 798
2017-09-21 16:00 | 841 | 839
2017-09-21 16:30 | 874 | 873
2017-09-21 17:00 | 911 | 909
2017-09-21 17:30 | 928 | 926
2017-09-21 18:00 | 950 | 949
2017-09-21 18:30 | 969 | 968
2017-09-21 19:00 | 971 | 969
2017-09-21 19:30 | 954 | 951
2017-09-21 20:00 | 944 | 942
2017-09-21 20:30 | 924 | 922
2017-09-21 21:00 | 887 | 887
2017-09-21 21:30 | 845 | 843
2017-09-21 22:00 | 800 | 798
2017-09-21 22:30 | 792 | 788
2017-09-21 23:00 | 786 | 782
2017-09-21 23:30 | 731 | 729
2017-09-22 | 677 | 672
2017-09-22 00:30 | 624 | 614
2017-09-22 01:00 | 595 | 581
2017-09-22 01:30 | 574 | 558
2017-09-22 02:00 | 558 | 540
2017-09-22 02:30 | 557 | 538
2017-09-22 03:00 | 552 | 532
2017-09-22 03:30 | 556 | 535
2017-09-22 04:00 | 550 | 529
2017-09-22 04:30 | 563 | 545
2017-09-22 05:00 | 575 | 559
2017-09-22 05:30 | 612 | 603
2017-09-22 06:00 | 650 | 642
2017-09-22 06:30 | 700 | 697
2017-09-22 07:00 | 739 | 738
2017-09-22 07:30 | 778 | 778
2017-09-22 08:00 | 788 | 788
2017-09-22 08:30 | 801 | 801
2017-09-22 09:00 | 798 | 797
2017-09-22 09:30 | 792 | 792
2017-09-22 10:00 | 771 | 771
2017-09-22 10:30 | 754 | 754
2017-09-22 11:00 | 750 | 750
2017-09-22 11:30 | 751 | 751
2017-09-22 12:00 | 753 | 753
2017-09-22 12:30 | 756 | 756
2017-09-22 13:00 | 767 | 767
2017-09-22 13:30 | 767 | 766
2017-09-22 14:00 | 790 | 790
2017-09-22 14:30 | 804 | 804
2017-09-22 15:00 | 837 | 837
2017-09-22 15:30 | 874 | 874
2017-09-22 16:00 | 898 | 898
2017-09-22 16:30 | 910 | 909
2017-09-22 17:00 | 923 | 922
2017-09-22 17:30 | 918 | 916
2017-09-22 18:00 | 922 | 920
2017-09-22 18:30 | 920 | 918
2017-09-22 19:00 | 924 | 921
2017-09-22 19:30 | 906 | 902
2017-09-22 20:00 | 885 | 881
2017-09-22 20:30 | 859 | 857
2017-09-22 21:00 | 809 | 808
2017-09-22 21:30 | 774 | 772
2017-09-22 22:00 | 755 | 751
2017-09-22 22:30 | 750 | 745
2017-09-22 23:00 | 751 | 744
2017-09-22 23:30 | 715 | 705
2017-09-23 | 670 | 657
2017-09-23 00:30 | 611 | 600
2017-09-23 01:00 | 585 | 570
2017-09-23 01:30 | 559 | 542
2017-09-23 02:00 | 544 | 524
2017-09-23 02:30 | 535 | 513
2017-09-23 03:00 | 524 | 500
2017-09-23 03:30 | 517 | 492
2017-09-23 04:00 | 513 | 488
2017-09-23 04:30 | 517 | 492
2017-09-23 05:00 | 527 | 504
2017-09-23 05:30 | 534 | 513
2017-09-23 06:00 | 542 | 520
2017-09-23 06:30 | 556 | 537
2017-09-23 07:00 | 568 | 552
2017-09-23 07:30 | 583 | 573
2017-09-23 08:00 | 594 | 589
2017-09-23 08:30 | 610 | 608
2017-09-23 09:00 | 614 | 613
2017-09-23 09:30 | 615 | 615
2017-09-23 10:00 | 609 | 609
2017-09-23 10:30 | 593 | 593
2017-09-23 11:00 | 577 | 577
2017-09-23 11:30 | 572 | 571
2017-09-23 12:00 | 574 | 574
2017-09-23 12:30 | 573 | 573
2017-09-23 13:00 | 593 | 593
2017-09-23 13:30 | 616 | 616
2017-09-23 14:00 | 632 | 632
2017-09-23 14:30 | 661 | 660
2017-09-23 15:00 | 674 | 674
2017-09-23 15:30 | 695 | 695
2017-09-23 16:00 | 729 | 729
2017-09-23 16:30 | 757 | 757
2017-09-23 17:00 | 789 | 788
2017-09-23 17:30 | 789 | 789
2017-09-23 18:00 | 804 | 804
2017-09-23 18:30 | 841 | 841
2017-09-23 19:00 | 844 | 844
2017-09-23 19:30 | 831 | 831
2017-09-23 20:00 | 812 | 811
2017-09-23 20:30 | 798 | 798
2017-09-23 21:00 | 765 | 765
2017-09-23 21:30 | 734 | 734
2017-09-23 22:00 | 725 | 725
2017-09-23 22:30 | 719 | 718
2017-09-23 23:00 | 721 | 719
2017-09-23 23:30 | 682 | 678
2017-09-24 | 642 | 636
2017-09-24 00:30 | 594 | 584
2017-09-24 01:00 | 559 | 545
2017-09-24 01:30 | 545 | 528
2017-09-24 02:00 | 534 | 513
2017-09-24 02:30 | 532 | 508
2017-09-24 03:00 | 524 | 500
2017-09-24 03:30 | 522 | 497
2017-09-24 04:00 | 524 | 499
2017-09-24 04:30 | 520 | 494
2017-09-24 05:00 | 520 | 494
2017-09-24 05:30 | 525 | 502
2017-09-24 06:00 | 529 | 501
2017-09-24 06:30 | 543 | 517
2017-09-24 07:00 | 549 | 526
2017-09-24 07:30 | 555 | 537
2017-09-24 08:00 | 552 | 539
2017-09-24 08:30 | 562 | 553
2017-09-24 09:00 | 571 | 566
2017-09-24 09:30 | 574 | 572
2017-09-24 10:00 | 572 | 571
2017-09-24 10:30 | 574 | 574
2017-09-24 11:00 | 562 | 562
2017-09-24 11:30 | 561 | 561
2017-09-24 12:00 | 567 | 567
2017-09-24 12:30 | 574 | 574
2017-09-24 13:00 | 587 | 587
2017-09-24 13:30 | 598 | 598
2017-09-24 14:00 | 570 | 570
2017-09-24 14:30 | 580 | 580
2017-09-24 15:00 | 633 | 633
2017-09-24 15:30 | 702 | 702
2017-09-24 16:00 | 678 | 676
2017-09-24 16:30 | 718 | 716
2017-09-24 17:00 | 790 | 788
2017-09-24 17:30 | 802 | 799
2017-09-24 18:00 | 824 | 822
2017-09-24 18:30 | 871 | 869
2017-09-24 19:00 | 874 | 871
2017-09-24 19:30 | 856 | 851
2017-09-24 20:00 | 839 | 837
2017-09-24 20:30 | 820 | 820
2017-09-24 21:00 | 786 | 786
2017-09-24 21:30 | 754 | 754
2017-09-24 22:00 | 726 | 725
2017-09-24 22:30 | 716 | 715
2017-09-24 23:00 | 713 | 711
2017-09-24 23:30 | 676 | 672
2017-09-25 | 633 | 625
2017-09-25 00:30 | 595 | 583
2017-09-25 01:00 | 568 | 554
2017-09-25 01:30 | 556 | 540
2017-09-25 02:00 | 552 | 534
2017-09-25 02:30 | 554 | 533
2017-09-25 03:00 | 556 | 535
2017-09-25 03:30 | 557 | 536
2017-09-25 04:00 | 558 | 537
2017-09-25 04:30 | 561 | 543
2017-09-25 05:00 | 571 | 558
2017-09-25 05:30 | 600 | 592
2017-09-25 06:00 | 632 | 625
2017-09-25 06:30 | 683 | 680
2017-09-25 07:00 | 727 | 727
2017-09-25 07:30 | 768 | 768
2017-09-25 08:00 | 790 | 787
2017-09-25 08:30 | 807 | 802
2017-09-25 09:00 | 810 | 808
2017-09-25 09:30 | 818 | 817
2017-09-25 10:00 | 802 | 801
2017-09-25 10:30 | 796 | 795
2017-09-25 11:00 | 795 | 794
2017-09-25 11:30 | 803 | 801
2017-09-25 12:00 | 808 | 805
2017-09-25 12:30 | 820 | 816
2017-09-25 13:00 | 849 | 845
2017-09-25 13:30 | 855 | 855
2017-09-25 14:00 | 880 | 880
2017-09-25 14:30 | 901 | 901
2017-09-25 15:00 | 925 | 925
2017-09-25 15:30 | 944 | 944
2017-09-25 16:00 | 968 | 968
2017-09-25 16:30 | 986 | 986
2017-09-25 17:00 | 1001 | 1000
2017-09-25 17:30 | 1009 | 1007
2017-09-25 18:00 | 1009 | 1005
2017-09-25 18:30 | 1019 | 1015
2017-09-25 19:00 | 1018 | 1014
2017-09-25 19:30 | 993 | 987
2017-09-25 20:00 | 971 | 970
2017-09-25 20:30 | 946 | 944
2017-09-25 21:00 | 888 | 887
2017-09-25 21:30 | 846 | 845
2017-09-25 22:00 | 806 | 806
2017-09-25 22:30 | 784 | 783
2017-09-25 23:00 | 774 | 773
2017-09-25 23:30 | 722 | 721
2017-09-26 | 678 | 674
2017-09-26 00:30 | 630 | 623
2017-09-26 01:00 | 611 | 601
2017-09-26 01:30 | 591 | 578
2017-09-26 02:00 | 578 | 564
2017-09-26 02:30 | 574 | 559
2017-09-26 03:00 | 571 | 555
2017-09-26 03:30 | 571 | 553
2017-09-26 04:00 | 572 | 555
2017-09-26 04:30 | 579 | 563
2017-09-26 05:00 | 593 | 581
2017-09-26 05:30 | 623 | 615
2017-09-26 06:00 | 644 | 637
2017-09-26 06:30 | 695 | 693
2017-09-26 07:00 | 743 | 742
2017-09-26 07:30 | 783 | 783
2017-09-26 08:00 | 805 | 805
2017-09-26 08:30 | 821 | 820
2017-09-26 09:00 | 820 | 820
2017-09-26 09:30 | 822 | 822
2017-09-26 10:00 | 863 | 863
2017-09-26 10:30 | 873 | 872
2017-09-26 11:00 | 862 | 859
2017-09-26 11:30 | 813 | 809
2017-09-26 12:00 | 839 | 837
2017-09-26 12:30 | 810 | 808
2017-09-26 13:00 | 795 | 792
2017-09-26 13:30 | 801 | 798
2017-09-26 14:00 | 810 | 808
2017-09-26 14:30 | 828 | 826
2017-09-26 15:00 | 835 | 832
2017-09-26 15:30 | 863 | 860
2017-09-26 16:00 | 884 | 881
2017-09-26 16:30 | 910 | 907
2017-09-26 17:00 | 933 | 930
2017-09-26 17:30 | 946 | 943
2017-09-26 18:00 | 956 | 954
2017-09-26 18:30 | 984 | 983
2017-09-26 19:00 | 982 | 981
2017-09-26 19:30 | 956 | 953
2017-09-26 20:00 | 938 | 934
2017-09-26 20:30 | 905 | 902
2017-09-26 21:00 | 843 | 842
2017-09-26 21:30 | 804 | 803
2017-09-26 22:00 | 783 | 780
2017-09-26 22:30 | 761 | 756
2017-09-26 23:00 | 752 | 748
2017-09-26 23:30 | 712 | 706
2017-09-27 | 665 | 655
2017-09-27 00:30 | 617 | 603
2017-09-27 01:00 | 590 | 575
2017-09-27 01:30 | 582 | 564
2017-09-27 02:00 | 570 | 549
2017-09-27 02:30 | 565 | 544
2017-09-27 03:00 | 564 | 542
2017-09-27 03:30 | 565 | 542
2017-09-27 04:00 | 565 | 544
2017-09-27 04:30 | 573 | 553
2017-09-27 05:00 | 589 | 572
2017-09-27 05:30 | 617 | 606
2017-09-27 06:00 | 639 | 629
2017-09-27 06:30 | 696 | 693
2017-09-27 07:00 | 755 | 754
2017-09-27 07:30 | 798 | 798
2017-09-27 08:00 | 817 | 817
2017-09-27 08:30 | 829 | 827
2017-09-27 09:00 | 841 | 839
2017-09-27 09:30 | 836 | 834
2017-09-27 10:00 | 844 | 843
2017-09-27 10:30 | 838 | 838
2017-09-27 11:00 | 840 | 840
2017-09-27 11:30 | 844 | 844
2017-09-27 12:00 | 855 | 855
2017-09-27 12:30 | 856 | 856
2017-09-27 13:00 | 850 | 849
2017-09-27 13:30 | 857 | 857
2017-09-27 14:00 | 867 | 866
2017-09-27 14:30 | 898 | 898
2017-09-27 15:00 | 893 | 893
2017-09-27 15:30 | 892 | 891
2017-09-27 16:00 | 897 | 896
2017-09-27 16:30 | 916 | 914
2017-09-27 17:00 | 925 | 924
2017-09-27 17:30 | 937 | 936
2017-09-27 18:00 | 951 | 950
2017-09-27 18:30 | 952 | 951
2017-09-27 19:00 | 958 | 956
2017-09-27 19:30 | 935 | 932
2017-09-27 20:00 | 925 | 922
2017-09-27 20:30 | 898 | 895
2017-09-27 21:00 | 858 | 857
2017-09-27 21:30 | 808 | 808
2017-09-27 22:00 | 777 | 776
2017-09-27 22:30 | 764 | 762
2017-09-27 23:00 | 751 | 748
2017-09-27 23:30 | 716 | 713
2017-09-28 | 667 | 660
2017-09-28 00:30 | 625 | 613
2017-09-28 01:00 | 600 | 586
2017-09-28 01:30 | 586 | 569
2017-09-28 02:00 | 578 | 558
2017-09-28 02:30 | 539 | 515
2017-09-28 03:00 | 545 | 524
2017-09-28 03:30 | 565 | 546
2017-09-28 04:00 | 564 | 543
2017-09-28 04:30 | 571 | 552
2017-09-28 05:00 | 588 | 575
2017-09-28 05:30 | 615 | 605
2017-09-28 06:00 | 641 | 633
2017-09-28 06:30 | 687 | 683
2017-09-28 07:00 | 723 | 720
2017-09-28 07:30 | 768 | 766
2017-09-28 08:00 | 777 | 777
2017-09-28 08:30 | 785 | 785
2017-09-28 09:00 | 790 | 790
2017-09-28 09:30 | 789 | 788
2017-09-28 10:00 | 780 | 779
2017-09-28 10:30 | 789 | 787
2017-09-28 11:00 | 786 | 786
2017-09-28 11:30 | 794 | 794
2017-09-28 12:00 | 804 | 804
2017-09-28 12:30 | 826 | 826
2017-09-28 13:00 | 847 | 847
2017-09-28 13:30 | 871 | 870
2017-09-28 14:00 | 902 | 901
2017-09-28 14:30 | 928 | 928
2017-09-28 15:00 | 969 | 969
2017-09-28 15:30 | 1008 | 1004
2017-09-28 16:00 | 1045 | 1041
2017-09-28 16:30 | 1075 | 1072
2017-09-28 17:00 | 1096 | 1092
2017-09-28 17:30 | 1091 | 1085
2017-09-28 18:00 | 1085 | 1078
2017-09-28 18:30 | 1100 | 1093
2017-09-28 19:00 | 1109 | 1103
2017-09-28 19:30 | 1068 | 1063
2017-09-28 20:00 | 1042 | 1039
2017-09-28 20:30 | 1012 | 1009
2017-09-28 21:00 | 964 | 961
2017-09-28 21:30 | 914 | 912
2017-09-28 22:00 | 884 | 879
2017-09-28 22:30 | 858 | 853
2017-09-28 23:00 | 841 | 834
2017-09-28 23:30 | 764 | 754
2017-09-29 | 699 | 688
2017-09-29 00:30 | 642 | 633
2017-09-29 01:00 | 618 | 606
2017-09-29 01:30 | 590 | 577
2017-09-29 02:00 | 588 | 573
2017-09-29 02:30 | 585 | 569
2017-09-29 03:00 | 583 | 566
2017-09-29 03:30 | 583 | 566
2017-09-29 04:00 | 579 | 561
2017-09-29 04:30 | 592 | 577
2017-09-29 05:00 | 599 | 586
2017-09-29 05:30 | 626 | 618
2017-09-29 06:00 | 649 | 641
2017-09-29 06:30 | 692 | 689
2017-09-29 07:00 | 728 | 727
2017-09-29 07:30 | 769 | 769
2017-09-29 08:00 | 803 | 803
2017-09-29 08:30 | 825 | 823
2017-09-29 09:00 | 835 | 834
2017-09-29 09:30 | 850 | 850
2017-09-29 10:00 | 841 | 841
2017-09-29 10:30 | 854 | 853
2017-09-29 11:00 | 864 | 864
2017-09-29 11:30 | 875 | 874
2017-09-29 12:00 | 880 | 877
2017-09-29 12:30 | 889 | 887
2017-09-29 13:00 | 919 | 917
2017-09-29 13:30 | 936 | 935
2017-09-29 14:00 | 985 | 984
2017-09-29 14:30 | 1020 | 1014
2017-09-29 15:00 | 1032 | 1022
2017-09-29 15:30 | 1048 | 1039
2017-09-29 16:00 | 1075 | 1065
2017-09-29 16:30 | 1085 | 1073
2017-09-29 17:00 | 1082 | 1072
2017-09-29 17:30 | 1055 | 1047
2017-09-29 18:00 | 1026 | 1018
2017-09-29 18:30 | 1026 | 1020
2017-09-29 19:00 | 1028 | 1020
2017-09-29 19:30 | 996 | 986
2017-09-29 20:00 | 966 | 960
2017-09-29 20:30 | 937 | 932
2017-09-29 21:00 | 897 | 892
2017-09-29 21:30 | 852 | 844
2017-09-29 22:00 | 815 | 807
2017-09-29 22:30 | 791 | 785
2017-09-29 23:00 | 786 | 779
2017-09-29 23:30 | 735 | 727
2017-09-30 | 681 | 676
2017-09-30 00:30 | 637 | 629
2017-09-30 01:00 | 609 | 601
2017-09-30 01:30 | 595 | 585
2017-09-30 02:00 | 579 | 566
2017-09-30 02:30 | 574 | 557
2017-09-30 03:00 | 574 | 556
2017-09-30 03:30 | 571 | 552
2017-09-30 04:00 | 566 | 545
2017-09-30 04:30 | 562 | 540
2017-09-30 05:00 | 567 | 547
2017-09-30 05:30 | 573 | 554
2017-09-30 06:00 | 580 | 559
2017-09-30 06:30 | 594 | 577
2017-09-30 07:00 | 601 | 589
2017-09-30 07:30 | 613 | 607
2017-09-30 08:00 | 631 | 629
2017-09-30 08:30 | 655 | 655
2017-09-30 09:00 | 679 | 679
2017-09-30 09:30 | 705 | 705
2017-09-30 10:00 | 675 | 674
2017-09-30 10:30 | 685 | 683
2017-09-30 11:00 | 684 | 682
2017-09-30 11:30 | 679 | 677
2017-09-30 12:00 | 684 | 682
2017-09-30 12:30 | 688 | 688
2017-09-30 13:00 | 703 | 703
2017-09-30 13:30 | 715 | 715
2017-09-30 14:00 | 742 | 742
2017-09-30 14:30 | 759 | 759
2017-09-30 15:00 | 777 | 777
2017-09-30 15:30 | 805 | 803
2017-09-30 16:00 | 820 | 814
2017-09-30 16:30 | 828 | 821
2017-09-30 17:00 | 836 | 829
2017-09-30 17:30 | 822 | 815
2017-09-30 18:00 | 816 | 811
2017-09-30 18:30 | 837 | 834
2017-09-30 19:00 | 837 | 834
2017-09-30 19:30 | 821 | 816
2017-09-30 20:00 | 809 | 804
2017-09-30 20:30 | 792 | 791
2017-09-30 21:00 | 761 | 758
2017-09-30 21:30 | 746 | 743
2017-09-30 22:00 | 719 | 717
2017-09-30 22:30 | 713 | 711
2017-09-30 23:00 | 720 | 717
2017-09-30 23:30 | 675 | 669
2017-10-01 | 636 | 627
2017-10-01 00:30 | 599 | 586
2017-10-01 01:00 | 577 | 561
2017-10-01 01:30 | 564 | 547
2017-10-01 02:00 | 551 | 533
2017-10-01 02:30 | 545 | 523
2017-10-01 03:00 | 542 | 518
2017-10-01 03:30 | 542 | 517
2017-10-01 04:00 | 538 | 514
2017-10-01 04:30 | 535 | 510
2017-10-01 05:00 | 537 | 513
2017-10-01 05:30 | 547 | 525
2017-10-01 06:00 | 551 | 527
2017-10-01 06:30 | 566 | 544
2017-10-01 07:00 | 581 | 562
2017-10-01 07:30 | 607 | 594
2017-10-01 08:00 | 630 | 620
2017-10-01 08:30 | 647 | 640
2017-10-01 09:00 | 647 | 641
2017-10-01 09:30 | 648 | 644
2017-10-01 10:00 | 648 | 645
2017-10-01 10:30 | 668 | 667
2017-10-01 11:00 | 696 | 695
2017-10-01 11:30 | 689 | 689
2017-10-01 12:00 | 697 | 696
2017-10-01 12:30 | 701 | 700
2017-10-01 13:00 | 692 | 691
2017-10-01 13:30 | 688 | 686
2017-10-01 14:00 | 693 | 692
2017-10-01 14:30 | 695 | 693
2017-10-01 15:00 | 704 | 702
2017-10-01 15:30 | 715 | 713
2017-10-01 16:00 | 721 | 720
2017-10-01 16:30 | 736 | 735
2017-10-01 17:00 | 759 | 759
2017-10-01 17:30 | 771 | 771
2017-10-01 18:00 | 785 | 785
2017-10-01 18:30 | 779 | 779
2017-10-01 19:00 | 771 | 771
2017-10-01 19:30 | 751 | 750
2017-10-01 20:00 | 753 | 752
2017-10-01 20:30 | 735 | 734
2017-10-01 21:00 | 713 | 711
2017-10-01 21:30 | 694 | 690
2017-10-01 22:00 | 687 | 682
2017-10-01 22:30 | 688 | 682
2017-10-01 23:00 | 686 | 678
2017-10-01 23:30 | 660 | 649
2017-10-02 | 624 | 608
2017-10-02 00:30 | 587 | 565
2017-10-02 01:00 | 566 | 540
2017-10-02 01:30 | 553 | 527
2017-10-02 02:00 | 547 | 518
2017-10-02 02:30 | 539 | 508
2017-10-02 03:00 | 534 | 504
2017-10-02 03:30 | 532 | 502
2017-10-02 04:00 | 528 | 498
2017-10-02 04:30 | 523 | 494
2017-10-02 05:00 | 522 | 494
2017-10-02 05:30 | 536 | 513
2017-10-02 06:00 | 547 | 522
2017-10-02 06:30 | 568 | 547
2017-10-02 07:00 | 592 | 576
2017-10-02 07:30 | 617 | 608
2017-10-02 08:00 | 656 | 652
2017-10-02 08:30 | 702 | 700
2017-10-02 09:00 | 725 | 724
2017-10-02 09:30 | 736 | 735
2017-10-02 10:00 | 744 | 744
2017-10-02 10:30 | 757 | 756
2017-10-02 11:00 | 746 | 745
2017-10-02 11:30 | 730 | 730
2017-10-02 12:00 | 738 | 737
2017-10-02 12:30 | 721 | 720
2017-10-02 13:00 | 708 | 707
2017-10-02 13:30 | 698 | 698
2017-10-02 14:00 | 697 | 696
2017-10-02 14:30 | 702 | 702
2017-10-02 15:00 | 706 | 706
2017-10-02 15:30 | 715 | 715
2017-10-02 16:00 | 737 | 737
2017-10-02 16:30 | 760 | 760
2017-10-02 17:00 | 800 | 800
2017-10-02 17:30 | 818 | 818
2017-10-02 18:00 | 835 | 834
2017-10-02 18:30 | 847 | 846
2017-10-02 19:00 | 841 | 839
2017-10-02 19:30 | 822 | 819
2017-10-02 20:00 | 808 | 804
2017-10-02 20:30 | 793 | 790
2017-10-02 21:00 | 755 | 753
2017-10-02 21:30 | 721 | 719
2017-10-02 22:00 | 699 | 696
2017-10-02 22:30 | 678 | 675
2017-10-02 23:00 | 664 | 660
2017-10-02 23:30 | 632 | 625
2017-10-03 | 596 | 584
2017-10-03 00:30 | 561 | 545
2017-10-03 01:00 | 537 | 517
2017-10-03 01:30 | 511 | 487
2017-10-03 02:00 | 488 | 463
2017-10-03 02:30 | 482 | 457
2017-10-03 03:00 | 476 | 450
2017-10-03 03:30 | 472 | 445
2017-10-03 04:00 | 478 | 453
2017-10-03 04:30 | 487 | 464
2017-10-03 05:00 | 504 | 485
2017-10-03 05:30 | 549 | 538
2017-10-03 06:00 | 597 | 589
2017-10-03 06:30 | 666 | 663
2017-10-03 07:00 | 741 | 740
2017-10-03 07:30 | 798 | 798
2017-10-03 08:00 | 813 | 813
2017-10-03 08:30 | 813 | 813
2017-10-03 09:00 | 807 | 807
2017-10-03 09:30 | 781 | 781
2017-10-03 10:00 | 767 | 767
2017-10-03 10:30 | 761 | 761
2017-10-03 11:00 | 755 | 755
2017-10-03 11:30 | 742 | 742
2017-10-03 12:00 | 730 | 730
2017-10-03 12:30 | 744 | 744
2017-10-03 13:00 | 743 | 743
2017-10-03 13:30 | 749 | 749
2017-10-03 14:00 | 758 | 758
2017-10-03 14:30 | 770 | 770
2017-10-03 15:00 | 783 | 783
2017-10-03 15:30 | 806 | 805
2017-10-03 16:00 | 831 | 830
2017-10-03 16:30 | 861 | 860
2017-10-03 17:00 | 886 | 885
2017-10-03 17:30 | 910 | 908
2017-10-03 18:00 | 928 | 927
2017-10-03 18:30 | 936 | 935
2017-10-03 19:00 | 943 | 942
2017-10-03 19:30 | 916 | 914
2017-10-03 20:00 | 903 | 901
2017-10-03 20:30 | 880 | 878
2017-10-03 21:00 | 837 | 834
2017-10-03 21:30 | 801 | 796
2017-10-03 22:00 | 762 | 759
2017-10-03 22:30 | 734 | 734
2017-10-03 23:00 | 726 | 726
2017-10-03 23:30 | 665 | 663
2017-10-04 | 616 | 612
2017-10-04 00:30 | 577 | 570
2017-10-04 01:00 | 550 | 539
2017-10-04 01:30 | 533 | 519
2017-10-04 02:00 | 524 | 509
2017-10-04 02:30 | 517 | 501
2017-10-04 03:00 | 513 | 496
2017-10-04 03:30 | 510 | 494
2017-10-04 04:00 | 507 | 489
2017-10-04 04:30 | 521 | 507
2017-10-04 05:00 | 536 | 525
2017-10-04 05:30 | 564 | 557
2017-10-04 06:00 | 608 | 602
2017-10-04 06:30 | 666 | 665
2017-10-04 07:00 | 725 | 723
2017-10-04 07:30 | 769 | 768
2017-10-04 08:00 | 775 | 775
2017-10-04 08:30 | 759 | 759
2017-10-04 09:00 | 751 | 751
2017-10-04 09:30 | 767 | 766
2017-10-04 10:00 | 782 | 782
2017-10-04 10:30 | 815 | 813
2017-10-04 11:00 | 804 | 802
2017-10-04 11:30 | 771 | 768
2017-10-04 12:00 | 751 | 747
2017-10-04 12:30 | 750 | 745
2017-10-04 13:00 | 755 | 751
2017-10-04 13:30 | 768 | 765
2017-10-04 14:00 | 784 | 781
2017-10-04 14:30 | 808 | 806
2017-10-04 15:00 | 829 | 827
2017-10-04 15:30 | 843 | 840
2017-10-04 16:00 | 870 | 867
2017-10-04 16:30 | 894 | 892
2017-10-04 17:00 | 915 | 912
2017-10-04 17:30 | 922 | 918
2017-10-04 18:00 | 930 | 925
2017-10-04 18:30 | 955 | 952
2017-10-04 19:00 | 970 | 968
2017-10-04 19:30 | 944 | 940
2017-10-04 20:00 | 921 | 916
2017-10-04 20:30 | 892 | 887
2017-10-04 21:00 | 841 | 840
2017-10-04 21:30 | 806 | 804
2017-10-04 22:00 | 777 | 775
2017-10-04 22:30 | 749 | 748
2017-10-04 23:00 | 736 | 735
2017-10-04 23:30 | 692 | 690
2017-10-05 | 646 | 642
2017-10-05 00:30 | 601 | 594
2017-10-05 01:00 | 571 | 562
2017-10-05 01:30 | 554 | 544
2017-10-05 02:00 | 546 | 533
2017-10-05 02:30 | 537 | 523
2017-10-05 03:00 | 539 | 523
2017-10-05 03:30 | 533 | 518
2017-10-05 04:00 | 538 | 525
2017-10-05 04:30 | 549 | 537
2017-10-05 05:00 | 560 | 550
2017-10-05 05:30 | 590 | 583
2017-10-05 06:00 | 626 | 620
2017-10-05 06:30 | 678 | 677
2017-10-05 07:00 | 720 | 720
2017-10-05 07:30 | 752 | 752
2017-10-05 08:00 | 766 | 765
2017-10-05 08:30 | 761 | 760
2017-10-05 09:00 | 751 | 751
2017-10-05 09:30 | 756 | 756
2017-10-05 10:00 | 754 | 754
2017-10-05 10:30 | 753 | 753
2017-10-05 11:00 | 754 | 754
2017-10-05 11:30 | 747 | 747
2017-10-05 12:00 | 747 | 747
2017-10-05 12:30 | 759 | 758
2017-10-05 13:00 | 769 | 769
2017-10-05 13:30 | 789 | 788
2017-10-05 14:00 | 814 | 813
2017-10-05 14:30 | 835 | 835
2017-10-05 15:00 | 869 | 869
2017-10-05 15:30 | 894 | 890
2017-10-05 16:00 | 920 | 914
2017-10-05 16:30 | 939 | 933
2017-10-05 17:00 | 959 | 953
2017-10-05 17:30 | 969 | 961
2017-10-05 18:00 | 982 | 975
2017-10-05 18:30 | 997 | 992
2017-10-05 19:00 | 1009 | 1005
2017-10-05 19:30 | 982 | 975
2017-10-05 20:00 | 971 | 965
2017-10-05 20:30 | 949 | 940
2017-10-05 21:00 | 904 | 898
2017-10-05 21:30 | 858 | 849
2017-10-05 22:00 | 817 | 808
2017-10-05 22:30 | 802 | 790
2017-10-05 23:00 | 782 | 771
2017-10-05 23:30 | 739 | 726
2017-10-06 | 678 | 672
2017-10-06 00:30 | 629 | 620
2017-10-06 01:00 | 606 | 596
2017-10-06 01:30 | 590 | 579
2017-10-06 02:00 | 580 | 566
2017-10-06 02:30 | 577 | 561
2017-10-06 03:00 | 571 | 554
2017-10-06 03:30 | 568 | 550
2017-10-06 04:00 | 571 | 554
2017-10-06 04:30 | 577 | 561
2017-10-06 05:00 | 592 | 581
2017-10-06 05:30 | 622 | 613
2017-10-06 06:00 | 649 | 643
2017-10-06 06:30 | 708 | 705
2017-10-06 07:00 | 745 | 745
2017-10-06 07:30 | 800 | 799
2017-10-06 08:00 | 820 | 817
2017-10-06 08:30 | 824 | 821
2017-10-06 09:00 | 817 | 814
2017-10-06 09:30 | 821 | 819
2017-10-06 10:00 | 841 | 840
2017-10-06 10:30 | 854 | 853
2017-10-06 11:00 | 839 | 838
2017-10-06 11:30 | 822 | 821
2017-10-06 12:00 | 832 | 832
2017-10-06 12:30 | 841 | 839
2017-10-06 13:00 | 868 | 865
2017-10-06 13:30 | 901 | 899
2017-10-06 14:00 | 945 | 942
2017-10-06 14:30 | 1017 | 1007
2017-10-06 15:00 | 1052 | 1042
2017-10-06 15:30 | 1010 | 991
2017-10-06 16:00 | 973 | 960
2017-10-06 16:30 | 961 | 946
2017-10-06 17:00 | 949 | 946
2017-10-06 17:30 | 957 | 952
2017-10-06 18:00 | 948 | 943
2017-10-06 18:30 | 953 | 948
2017-10-06 19:00 | 956 | 950
2017-10-06 19:30 | 927 | 927
2017-10-06 20:00 | 925 | 924
2017-10-06 20:30 | 904 | 903
2017-10-06 21:00 | 853 | 851
2017-10-06 21:30 | 817 | 813
2017-10-06 22:00 | 782 | 775
2017-10-06 22:30 | 770 | 765
2017-10-06 23:00 | 765 | 760
2017-10-06 23:30 | 707 | 697
2017-10-07 | 658 | 648
2017-10-07 00:30 | 614 | 602
2017-10-07 01:00 | 583 | 573
2017-10-07 01:30 | 567 | 557
2017-10-07 02:00 | 557 | 545
2017-10-07 02:30 | 544 | 530
2017-10-07 03:00 | 535 | 521
2017-10-07 03:30 | 527 | 511
2017-10-07 04:00 | 527 | 511
2017-10-07 04:30 | 527 | 512
2017-10-07 05:00 | 526 | 511
2017-10-07 05:30 | 538 | 524
2017-10-07 06:00 | 550 | 535
2017-10-07 06:30 | 573 | 561
2017-10-07 07:00 | 594 | 587
2017-10-07 07:30 | 637 | 634
2017-10-07 08:00 | 663 | 662
2017-10-07 08:30 | 695 | 695
2017-10-07 09:00 | 710 | 710
2017-10-07 09:30 | 717 | 717
2017-10-07 10:00 | 705 | 705
2017-10-07 10:30 | 701 | 699
2017-10-07 11:00 | 691 | 687
2017-10-07 11:30 | 698 | 694
2017-10-07 12:00 | 707 | 704
2017-10-07 12:30 | 680 | 676
2017-10-07 13:00 | 671 | 666
2017-10-07 13:30 | 690 | 684
2017-10-07 14:00 | 709 | 704
2017-10-07 14:30 | 718 | 712
2017-10-07 15:00 | 709 | 702
2017-10-07 15:30 | 711 | 705
2017-10-07 16:00 | 731 | 724
2017-10-07 16:30 | 740 | 733
2017-10-07 17:00 | 759 | 754
2017-10-07 17:30 | 766 | 761
2017-10-07 18:00 | 771 | 766
2017-10-07 18:30 | 787 | 785
2017-10-07 19:00 | 797 | 795
2017-10-07 19:30 | 774 | 772
2017-10-07 20:00 | 759 | 757
2017-10-07 20:30 | 742 | 742
2017-10-07 21:00 | 711 | 711
2017-10-07 21:30 | 694 | 693
2017-10-07 22:00 | 678 | 677
2017-10-07 22:30 | 680 | 678
2017-10-07 23:00 | 681 | 678
2017-10-07 23:30 | 649 | 644
2017-10-08 | 606 | 599
2017-10-08 00:30 | 564 | 552
2017-10-08 01:00 | 544 | 529
2017-10-08 01:30 | 537 | 519
2017-10-08 02:00 | 523 | 501
2017-10-08 02:30 | 492 | 467
2017-10-08 03:00 | 493 | 468
2017-10-08 03:30 | 490 | 463
2017-10-08 04:00 | 488 | 462
2017-10-08 04:30 | 486 | 458
2017-10-08 05:00 | 485 | 458
2017-10-08 05:30 | 490 | 464
2017-10-08 06:00 | 499 | 470
2017-10-08 06:30 | 510 | 485
2017-10-08 07:00 | 529 | 510
2017-10-08 07:30 | 556 | 545
2017-10-08 08:00 | 557 | 550
2017-10-08 08:30 | 573 | 568
2017-10-08 09:00 | 581 | 579
2017-10-08 09:30 | 601 | 600
2017-10-08 10:00 | 629 | 628
2017-10-08 10:30 | 649 | 649
2017-10-08 11:00 | 654 | 654
2017-10-08 11:30 | 639 | 639
2017-10-08 12:00 | 616 | 616
2017-10-08 12:30 | 600 | 600
2017-10-08 13:00 | 615 | 614
2017-10-08 13:30 | 628 | 628
2017-10-08 14:00 | 656 | 656
2017-10-08 14:30 | 675 | 675
2017-10-08 15:00 | 691 | 691
2017-10-08 15:30 | 698 | 698
2017-10-08 16:00 | 699 | 699
2017-10-08 16:30 | 710 | 709
2017-10-08 17:00 | 741 | 741
2017-10-08 17:30 | 758 | 757
2017-10-08 18:00 | 785 | 785
2017-10-08 18:30 | 843 | 841
2017-10-08 19:00 | 854 | 850
2017-10-08 19:30 | 829 | 825
2017-10-08 20:00 | 804 | 804
2017-10-08 20:30 | 791 | 791
2017-10-08 21:00 | 754 | 753
2017-10-08 21:30 | 726 | 725
2017-10-08 22:00 | 705 | 704
2017-10-08 22:30 | 693 | 691
2017-10-08 23:00 | 689 | 686
2017-10-08 23:30 | 647 | 642
2017-10-09 | 604 | 596
2017-10-09 00:30 | 564 | 552
2017-10-09 01:00 | 543 | 529
2017-10-09 01:30 | 534 | 517
2017-10-09 02:00 | 531 | 511
2017-10-09 02:30 | 527 | 506
2017-10-09 03:00 | 522 | 500
2017-10-09 03:30 | 519 | 498
2017-10-09 04:00 | 521 | 501
2017-10-09 04:30 | 530 | 513
2017-10-09 05:00 | 537 | 522
2017-10-09 05:30 | 568 | 559
2017-10-09 06:00 | 606 | 602
2017-10-09 06:30 | 683 | 683
2017-10-09 07:00 | 792 | 791
2017-10-09 07:30 | 866 | 866
2017-10-09 08:00 | 902 | 902
2017-10-09 08:30 | 917 | 916
2017-10-09 09:00 | 883 | 882
2017-10-09 09:30 | 808 | 807
2017-10-09 10:00 | 787 | 786
2017-10-09 10:30 | 778 | 775
2017-10-09 11:00 | 794 | 790
2017-10-09 11:30 | 798 | 794
2017-10-09 12:00 | 825 | 819
2017-10-09 12:30 | 840 | 837
2017-10-09 13:00 | 856 | 856
2017-10-09 13:30 | 865 | 865
2017-10-09 14:00 | 903 | 903
2017-10-09 14:30 | 941 | 941
2017-10-09 15:00 | 961 | 961
2017-10-09 15:30 | 1004 | 1004
2017-10-09 16:00 | 1068 | 1068
2017-10-09 16:30 | 1066 | 1066
2017-10-09 17:00 | 1060 | 1060
2017-10-09 17:30 | 1056 | 1056
2017-10-09 18:00 | 1063 | 1062
2017-10-09 18:30 | 1091 | 1091
2017-10-09 19:00 | 1108 | 1108
2017-10-09 19:30 | 1058 | 1058
2017-10-09 20:00 | 1036 | 1035
2017-10-09 20:30 | 1004 | 1001
2017-10-09 21:00 | 959 | 951
2017-10-09 21:30 | 912 | 901
2017-10-09 22:00 | 815 | 808
2017-10-09 22:30 | 776 | 773
2017-10-09 23:00 | 749 | 748
2017-10-09 23:30 | 706 | 705
2017-10-10 | 658 | 655
2017-10-10 00:30 | 613 | 607
2017-10-10 01:00 | 590 | 581
2017-10-10 01:30 | 572 | 561
2017-10-10 02:00 | 561 | 548
2017-10-10 02:30 | 560 | 546
2017-10-10 03:00 | 556 | 541
2017-10-10 03:30 | 556 | 541
2017-10-10 04:00 | 557 | 542
2017-10-10 04:30 | 565 | 552
2017-10-10 05:00 | 583 | 571
2017-10-10 05:30 | 605 | 597
2017-10-10 06:00 | 645 | 640
2017-10-10 06:30 | 699 | 699
2017-10-10 07:00 | 758 | 758
2017-10-10 07:30 | 825 | 825
2017-10-10 08:00 | 857 | 857
2017-10-10 08:30 | 882 | 882
2017-10-10 09:00 | 895 | 895
2017-10-10 09:30 | 906 | 905
2017-10-10 10:00 | 960 | 960
2017-10-10 10:30 | 974 | 971
2017-10-10 11:00 | 971 | 966
2017-10-10 11:30 | 997 | 993
2017-10-10 12:00 | 974 | 970
2017-10-10 12:30 | 994 | 991
2017-10-10 13:00 | 1023 | 1020
2017-10-10 13:30 | 983 | 978
2017-10-10 14:00 | 1020 | 1015
2017-10-10 14:30 | 1066 | 1062
2017-10-10 15:00 | 1070 | 1065
2017-10-10 15:30 | 1092 | 1087
2017-10-10 16:00 | 1132 | 1128
2017-10-10 16:30 | 1157 | 1152
2017-10-10 17:00 | 1169 | 1162
2017-10-10 17:30 | 1152 | 1142
2017-10-10 18:00 | 1136 | 1130
2017-10-10 18:30 | 1144 | 1138
2017-10-10 19:00 | 1149 | 1143
2017-10-10 19:30 | 1114 | 1106
2017-10-10 20:00 | 1088 | 1085
2017-10-10 20:30 | 1041 | 1038
2017-10-10 21:00 | 993 | 991
2017-10-10 21:30 | 947 | 944
2017-10-10 22:00 | 853 | 850
2017-10-10 22:30 | 825 | 823
2017-10-10 23:00 | 802 | 801
2017-10-10 23:30 | 745 | 743
2017-10-11 | 708 | 706
2017-10-11 00:30 | 654 | 651
2017-10-11 01:00 | 617 | 611
2017-10-11 01:30 | 603 | 594
2017-10-11 02:00 | 594 | 582
2017-10-11 02:30 | 582 | 569
2017-10-11 03:00 | 575 | 560
2017-10-11 03:30 | 571 | 555
2017-10-11 04:00 | 570 | 555
2017-10-11 04:30 | 581 | 569
2017-10-11 05:00 | 598 | 590
2017-10-11 05:30 | 627 | 622
2017-10-11 06:00 | 668 | 665
2017-10-11 06:30 | 733 | 733
2017-10-11 07:00 | 807 | 807
2017-10-11 07:30 | 924 | 923
2017-10-11 08:00 | 952 | 952
2017-10-11 08:30 | 983 | 983
2017-10-11 09:00 | 992 | 992
2017-10-11 09:30 | 1001 | 1001
2017-10-11 10:00 | 1004 | 1004
2017-10-11 10:30 | 1018 | 1017
2017-10-11 11:00 | 1015 | 1013
2017-10-11 11:30 | 981 | 979
2017-10-11 12:00 | 976 | 975
2017-10-11 12:30 | 976 | 975
2017-10-11 13:00 | 985 | 985
2017-10-11 13:30 | 997 | 997
2017-10-11 14:00 | 1005 | 1005
2017-10-11 14:30 | 988 | 987
2017-10-11 15:00 | 1008 | 1008
2017-10-11 15:30 | 1040 | 1040
2017-10-11 16:00 | 1056 | 1055
2017-10-11 16:30 | 1068 | 1067
2017-10-11 17:00 | 1085 | 1084
2017-10-11 17:30 | 1077 | 1074
2017-10-11 18:00 | 1073 | 1070
2017-10-11 18:30 | 1082 | 1081
2017-10-11 19:00 | 1082 | 1081
2017-10-11 19:30 | 1048 | 1044
2017-10-11 20:00 | 1027 | 1025
2017-10-11 20:30 | 1005 | 1003
2017-10-11 21:00 | 950 | 947
2017-10-11 21:30 | 898 | 898
2017-10-11 22:00 | 851 | 851
2017-10-11 22:30 | 824 | 823
2017-10-11 23:00 | 820 | 820
2017-10-11 23:30 | 775 | 775
2017-10-12 | 734 | 733
2017-10-12 00:30 | 681 | 677
2017-10-12 01:00 | 636 | 630
2017-10-12 01:30 | 588 | 580
2017-10-12 02:00 | 574 | 564
2017-10-12 02:30 | 583 | 573
2017-10-12 03:00 | 578 | 566
2017-10-12 03:30 | 558 | 545
2017-10-12 04:00 | 557 | 544
2017-10-12 04:30 | 565 | 554
2017-10-12 05:00 | 579 | 572
2017-10-12 05:30 | 627 | 623
2017-10-12 06:00 | 699 | 698
2017-10-12 06:30 | 775 | 775
2017-10-12 07:00 | 836 | 836
2017-10-12 07:30 | 932 | 929
2017-10-12 08:00 | 971 | 969
2017-10-12 08:30 | 977 | 976
2017-10-12 09:00 | 985 | 985
2017-10-12 09:30 | 988 | 988
2017-10-12 10:00 | 988 | 988
2017-10-12 10:30 | 999 | 999
2017-10-12 11:00 | 996 | 995
2017-10-12 11:30 | 975 | 974
2017-10-12 12:00 | 980 | 979
2017-10-12 12:30 | 980 | 978
2017-10-12 13:00 | 981 | 980
2017-10-12 13:30 | 983 | 982
2017-10-12 14:00 | 984 | 982
2017-10-12 14:30 | 981 | 979
2017-10-12 15:00 | 962 | 960
2017-10-12 15:30 | 972 | 970
2017-10-12 16:00 | 996 | 993
2017-10-12 16:30 | 1010 | 1007
2017-10-12 17:00 | 1023 | 1020
2017-10-12 17:30 | 1028 | 1024
2017-10-12 18:00 | 1032 | 1028
2017-10-12 18:30 | 1063 | 1061
2017-10-12 19:00 | 1077 | 1075
2017-10-12 19:30 | 1051 | 1046
2017-10-12 20:00 | 1040 | 1034
2017-10-12 20:30 | 1008 | 1002
2017-10-12 21:00 | 951 | 947
2017-10-12 21:30 | 900 | 894
2017-10-12 22:00 | 849 | 848
2017-10-12 22:30 | 816 | 814
2017-10-12 23:00 | 810 | 808
2017-10-12 23:30 | 762 | 758
2017-10-13 | 704 | 701
2017-10-13 00:30 | 659 | 651
2017-10-13 01:00 | 633 | 623
2017-10-13 01:30 | 577 | 563
2017-10-13 02:00 | 552 | 537
2017-10-13 02:30 | 551 | 535
2017-10-13 03:00 | 545 | 528
2017-10-13 03:30 | 544 | 527
2017-10-13 04:00 | 548 | 531
2017-10-13 04:30 | 561 | 546
2017-10-13 05:00 | 572 | 559
2017-10-13 05:30 | 630 | 621
2017-10-13 06:00 | 690 | 686
2017-10-13 06:30 | 749 | 748
2017-10-13 07:00 | 810 | 810
2017-10-13 07:30 | 869 | 865
2017-10-13 08:00 | 874 | 866
2017-10-13 08:30 | 863 | 859
2017-10-13 09:00 | 855 | 853
2017-10-13 09:30 | 867 | 865
2017-10-13 10:00 | 877 | 874
2017-10-13 10:30 | 882 | 879
2017-10-13 11:00 | 893 | 890
2017-10-13 11:30 | 904 | 902
2017-10-13 12:00 | 923 | 922
2017-10-13 12:30 | 926 | 925
2017-10-13 13:00 | 933 | 931
2017-10-13 13:30 | 947 | 945
2017-10-13 14:00 | 962 | 959
2017-10-13 14:30 | 962 | 959
2017-10-13 15:00 | 990 | 988
2017-10-13 15:30 | 1028 | 1027
2017-10-13 16:00 | 1038 | 1035
2017-10-13 16:30 | 1052 | 1048
2017-10-13 17:00 | 1042 | 1036
2017-10-13 17:30 | 1031 | 1024
2017-10-13 18:00 | 1021 | 1013
2017-10-13 18:30 | 1018 | 1012
2017-10-13 19:00 | 1025 | 1020
2017-10-13 19:30 | 991 | 990
2017-10-13 20:00 | 977 | 977
2017-10-13 20:30 | 956 | 956
2017-10-13 21:00 | 904 | 903
2017-10-13 21:30 | 869 | 868
2017-10-13 22:00 | 829 | 825
2017-10-13 22:30 | 806 | 804
2017-10-13 23:00 | 807 | 803
2017-10-13 23:30 | 764 | 760
2017-10-14 | 689 | 687
2017-10-14 00:30 | 644 | 641
2017-10-14 01:00 | 608 | 603
2017-10-14 01:30 | 569 | 561
2017-10-14 02:00 | 554 | 544
2017-10-14 02:30 | 548 | 536
2017-10-14 03:00 | 541 | 527
2017-10-14 03:30 | 540 | 525
2017-10-14 04:00 | 538 | 522
2017-10-14 04:30 | 536 | 522
2017-10-14 05:00 | 545 | 532
2017-10-14 05:30 | 556 | 543
2017-10-14 06:00 | 597 | 587
2017-10-14 06:30 | 646 | 641
2017-10-14 07:00 | 635 | 632
2017-10-14 07:30 | 661 | 660
2017-10-14 08:00 | 686 | 686
2017-10-14 08:30 | 724 | 724
2017-10-14 09:00 | 762 | 762
2017-10-14 09:30 | 788 | 788
2017-10-14 10:00 | 804 | 804
2017-10-14 10:30 | 810 | 810
2017-10-14 11:00 | 793 | 793
2017-10-14 11:30 | 779 | 778
2017-10-14 12:00 | 770 | 769
2017-10-14 12:30 | 775 | 773
2017-10-14 13:00 | 760 | 757
2017-10-14 13:30 | 743 | 739
2017-10-14 14:00 | 743 | 739
2017-10-14 14:30 | 749 | 744
2017-10-14 15:00 | 737 | 733
2017-10-14 15:30 | 736 | 734
2017-10-14 16:00 | 758 | 756
2017-10-14 16:30 | 813 | 811
2017-10-14 17:00 | 843 | 842
2017-10-14 17:30 | 849 | 848
2017-10-14 18:00 | 862 | 862
2017-10-14 18:30 | 879 | 879
2017-10-14 19:00 | 872 | 872
2017-10-14 19:30 | 842 | 842
2017-10-14 20:00 | 830 | 830
2017-10-14 20:30 | 805 | 805
2017-10-14 21:00 | 785 | 785
2017-10-14 21:30 | 754 | 754
2017-10-14 22:00 | 723 | 722
2017-10-14 22:30 | 725 | 723
2017-10-14 23:00 | 729 | 727
2017-10-14 23:30 | 685 | 681
2017-10-15 | 637 | 630
2017-10-15 00:30 | 595 | 586
2017-10-15 01:00 | 573 | 561
2017-10-15 01:30 | 561 | 546
2017-10-15 02:00 | 549 | 531
2017-10-15 02:30 | 540 | 521
2017-10-15 03:00 | 534 | 515
2017-10-15 03:30 | 534 | 515
2017-10-15 04:00 | 537 | 517
2017-10-15 04:30 | 532 | 512
2017-10-15 05:00 | 527 | 508
2017-10-15 05:30 | 532 | 512
2017-10-15 06:00 | 586 | 568
2017-10-15 06:30 | 596 | 582
2017-10-15 07:00 | 588 | 575
2017-10-15 07:30 | 614 | 606
2017-10-15 08:00 | 646 | 642
2017-10-15 08:30 | 677 | 676
2017-10-15 09:00 | 696 | 695
2017-10-15 09:30 | 684 | 683
2017-10-15 10:00 | 684 | 684
2017-10-15 10:30 | 719 | 719
2017-10-15 11:00 | 719 | 719
2017-10-15 11:30 | 705 | 705
2017-10-15 12:00 | 711 | 711
2017-10-15 12:30 | 718 | 717
2017-10-15 13:00 | 716 | 716
2017-10-15 13:30 | 726 | 725
2017-10-15 14:00 | 727 | 726
2017-10-15 14:30 | 742 | 742
2017-10-15 15:00 | 759 | 759
2017-10-15 15:30 | 774 | 774
2017-10-15 16:00 | 784 | 784
2017-10-15 16:30 | 797 | 796
2017-10-15 17:00 | 818 | 818
2017-10-15 17:30 | 831 | 831
2017-10-15 18:00 | 849 | 848
2017-10-15 18:30 | 886 | 886
2017-10-15 19:00 | 889 | 888
2017-10-15 19:30 | 868 | 867
2017-10-15 20:00 | 838 | 836
2017-10-15 20:30 | 827 | 826
2017-10-15 21:00 | 794 | 794
2017-10-15 21:30 | 770 | 769
2017-10-15 22:00 | 755 | 755
2017-10-15 22:30 | 752 | 751
2017-10-15 23:00 | 747 | 746
2017-10-15 23:30 | 711 | 709
2017-10-16 | 671 | 667
2017-10-16 00:30 | 632 | 624
2017-10-16 01:00 | 612 | 602
2017-10-16 01:30 | 598 | 587
2017-10-16 02:00 | 584 | 571
2017-10-16 02:30 | 581 | 567
2017-10-16 03:00 | 579 | 565
2017-10-16 03:30 | 579 | 564
2017-10-16 04:00 | 579 | 566
2017-10-16 04:30 | 588 | 576
2017-10-16 05:00 | 604 | 596
2017-10-16 05:30 | 633 | 628
2017-10-16 06:00 | 713 | 711
2017-10-16 06:30 | 809 | 808
2017-10-16 07:00 | 864 | 863
2017-10-16 07:30 | 918 | 916
2017-10-16 08:00 | 937 | 936
2017-10-16 08:30 | 957 | 957
2017-10-16 09:00 | 971 | 971
2017-10-16 09:30 | 963 | 961
2017-10-16 10:00 | 951 | 949
2017-10-16 10:30 | 962 | 961
2017-10-16 11:00 | 940 | 939
2017-10-16 11:30 | 873 | 870
2017-10-16 12:00 | 853 | 851
2017-10-16 12:30 | 852 | 852
2017-10-16 13:00 | 843 | 843
2017-10-16 13:30 | 844 | 844
2017-10-16 14:00 | 852 | 852
2017-10-16 14:30 | 852 | 851
2017-10-16 15:00 | 862 | 861
2017-10-16 15:30 | 858 | 858
2017-10-16 16:00 | 869 | 868
2017-10-16 16:30 | 891 | 890
2017-10-16 17:00 | 937 | 936
2017-10-16 17:30 | 950 | 950
2017-10-16 18:00 | 969 | 969
2017-10-16 18:30 | 987 | 987
2017-10-16 19:00 | 984 | 983
2017-10-16 19:30 | 944 | 942
2017-10-16 20:00 | 921 | 918
2017-10-16 20:30 | 906 | 903
2017-10-16 21:00 | 867 | 865
2017-10-16 21:30 | 829 | 828
2017-10-16 22:00 | 798 | 797
2017-10-16 22:30 | 782 | 780
2017-10-16 23:00 | 781 | 777
2017-10-16 23:30 | 744 | 740
2017-10-17 | 691 | 686
2017-10-17 00:30 | 651 | 644
2017-10-17 01:00 | 627 | 618
2017-10-17 01:30 | 607 | 596
2017-10-17 02:00 | 599 | 587
2017-10-17 02:30 | 593 | 579
2017-10-17 03:00 | 579 | 564
2017-10-17 03:30 | 592 | 578
2017-10-17 04:00 | 591 | 578
2017-10-17 04:30 | 611 | 599
2017-10-17 05:00 | 619 | 611
2017-10-17 05:30 | 652 | 646
2017-10-17 06:00 | 693 | 689
2017-10-17 06:30 | 757 | 756
2017-10-17 07:00 | 812 | 812
2017-10-17 07:30 | 880 | 879
2017-10-17 08:00 | 893 | 892
2017-10-17 08:30 | 943 | 938
2017-10-17 09:00 | 929 | 925
2017-10-17 09:30 | 936 | 932
2017-10-17 10:00 | 929 | 926
2017-10-17 10:30 | 903 | 899
2017-10-17 11:00 | 921 | 918
2017-10-17 11:30 | 928 | 925
2017-10-17 12:00 | 895 | 890
2017-10-17 12:30 | 911 | 907
2017-10-17 13:00 | 898 | 892
2017-10-17 13:30 | 901 | 896
2017-10-17 14:00 | 904 | 899
2017-10-17 14:30 | 892 | 887
2017-10-17 15:00 | 895 | 889
2017-10-17 15:30 | 895 | 888
2017-10-17 16:00 | 916 | 910
2017-10-17 16:30 | 957 | 951
2017-10-17 17:00 | 976 | 971
2017-10-17 17:30 | 992 | 988
2017-10-17 18:00 | 993 | 988
2017-10-17 18:30 | 1004 | 1001
2017-10-17 19:00 | 1009 | 1006
2017-10-17 19:30 | 974 | 968
2017-10-17 20:00 | 947 | 942
2017-10-17 20:30 | 928 | 925
2017-10-17 21:00 | 884 | 883
2017-10-17 21:30 | 842 | 842
2017-10-17 22:00 | 809 | 809
2017-10-17 22:30 | 787 | 786
2017-10-17 23:00 | 784 | 782
2017-10-17 23:30 | 746 | 741
2017-10-18 | 705 | 698
2017-10-18 00:30 | 653 | 646
2017-10-18 01:00 | 623 | 612
2017-10-18 01:30 | 608 | 593
2017-10-18 02:00 | 598 | 581
2017-10-18 02:30 | 594 | 576
2017-10-18 03:00 | 592 | 575
2017-10-18 03:30 | 544 | 523
2017-10-18 04:00 | 581 | 563
2017-10-18 04:30 | 591 | 575
2017-10-18 05:00 | 617 | 605
2017-10-18 05:30 | 652 | 644
2017-10-18 06:00 | 698 | 693
2017-10-18 06:30 | 777 | 773
2017-10-18 07:00 | 822 | 820
2017-10-18 07:30 | 868 | 867
2017-10-18 08:00 | 874 | 873
2017-10-18 08:30 | 877 | 876
2017-10-18 09:00 | 870 | 869
2017-10-18 09:30 | 869 | 869
2017-10-18 10:00 | 852 | 852
2017-10-18 10:30 | 851 | 851
2017-10-18 11:00 | 858 | 857
2017-10-18 11:30 | 844 | 844
2017-10-18 12:00 | 834 | 833
2017-10-18 12:30 | 824 | 823
2017-10-18 13:00 | 830 | 829
2017-10-18 13:30 | 831 | 831
2017-10-18 14:00 | 843 | 843
2017-10-18 14:30 | 840 | 840
2017-10-18 15:00 | 850 | 850
2017-10-18 15:30 | 862 | 862
2017-10-18 16:00 | 902 | 901
2017-10-18 16:30 | 917 | 917
2017-10-18 17:00 | 956 | 956
2017-10-18 17:30 | 976 | 976
2017-10-18 18:00 | 984 | 983
2017-10-18 18:30 | 1003 | 998
2017-10-18 19:00 | 1002 | 998
2017-10-18 19:30 | 976 | 969
2017-10-18 20:00 | 941 | 938
2017-10-18 20:30 | 925 | 922
2017-10-18 21:00 | 886 | 883
2017-10-18 21:30 | 836 | 835
2017-10-18 22:00 | 807 | 807
2017-10-18 22:30 | 815 | 815
2017-10-18 23:00 | 787 | 786
2017-10-18 23:30 | 741 | 739
2017-10-19 | 698 | 693
2017-10-19 00:30 | 650 | 641
2017-10-19 01:00 | 625 | 615
2017-10-19 01:30 | 608 | 596
2017-10-19 02:00 | 597 | 583
2017-10-19 02:30 | 590 | 576
2017-10-19 03:00 | 587 | 572
2017-10-19 03:30 | 586 | 571
2017-10-19 04:00 | 594 | 581
2017-10-19 04:30 | 603 | 591
2017-10-19 05:00 | 614 | 604
2017-10-19 05:30 | 644 | 636
2017-10-19 06:00 | 685 | 680
2017-10-19 06:30 | 729 | 727
2017-10-19 07:00 | 776 | 774
2017-10-19 07:30 | 813 | 812
2017-10-19 08:00 | 827 | 827
2017-10-19 08:30 | 837 | 836
2017-10-19 09:00 | 831 | 830
2017-10-19 09:30 | 838 | 837
2017-10-19 10:00 | 814 | 814
2017-10-19 10:30 | 819 | 819
2017-10-19 11:00 | 817 | 817
2017-10-19 11:30 | 804 | 804
2017-10-19 12:00 | 812 | 812
2017-10-19 12:30 | 803 | 803
2017-10-19 13:00 | 803 | 803
2017-10-19 13:30 | 804 | 804
2017-10-19 14:00 | 808 | 808
2017-10-19 14:30 | 812 | 812
2017-10-19 15:00 | 833 | 833
2017-10-19 15:30 | 853 | 853
2017-10-19 16:00 | 875 | 874
2017-10-19 16:30 | 901 | 897
2017-10-19 17:00 | 915 | 911
2017-10-19 17:30 | 925 | 919
2017-10-19 18:00 | 937 | 931
2017-10-19 18:30 | 959 | 955
2017-10-19 19:00 | 979 | 975
2017-10-19 19:30 | 960 | 955
2017-10-19 20:00 | 944 | 941
2017-10-19 20:30 | 924 | 922
2017-10-19 21:00 | 883 | 882
2017-10-19 21:30 | 844 | 843
2017-10-19 22:00 | 816 | 815
2017-10-19 22:30 | 802 | 798
2017-10-19 23:00 | 794 | 792
2017-10-19 23:30 | 745 | 742
2017-10-20 | 701 | 697
2017-10-20 00:30 | 658 | 651
2017-10-20 01:00 | 636 | 626
2017-10-20 01:30 | 614 | 602
2017-10-20 02:00 | 602 | 588
2017-10-20 02:30 | 595 | 581
2017-10-20 03:00 | 597 | 582
2017-10-20 03:30 | 595 | 580
2017-10-20 04:00 | 592 | 579
2017-10-20 04:30 | 605 | 592
2017-10-20 05:00 | 622 | 611
2017-10-20 05:30 | 651 | 642
2017-10-20 06:00 | 732 | 726
2017-10-20 06:30 | 797 | 796
2017-10-20 07:00 | 845 | 842
2017-10-20 07:30 | 870 | 868
2017-10-20 08:00 | 888 | 887
2017-10-20 08:30 | 894 | 893
2017-10-20 09:00 | 884 | 884
2017-10-20 09:30 | 892 | 892
2017-10-20 10:00 | 896 | 896
2017-10-20 10:30 | 904 | 904
2017-10-20 11:00 | 913 | 913
2017-10-20 11:30 | 894 | 894
2017-10-20 12:00 | 887 | 887
2017-10-20 12:30 | 882 | 882
2017-10-20 13:00 | 891 | 891
2017-10-20 13:30 | 899 | 899
2017-10-20 14:00 | 897 | 897
2017-10-20 14:30 | 899 | 899
2017-10-20 15:00 | 892 | 891
2017-10-20 15:30 | 895 | 895
2017-10-20 16:00 | 928 | 928
2017-10-20 16:30 | 964 | 964
2017-10-20 17:00 | 980 | 980
2017-10-20 17:30 | 920 | 919
2017-10-20 18:00 | 905 | 902
2017-10-20 18:30 | 924 | 922
2017-10-20 19:00 | 936 | 934
2017-10-20 19:30 | 915 | 914
2017-10-20 20:00 | 897 | 897
2017-10-20 20:30 | 881 | 881
2017-10-20 21:00 | 845 | 845
2017-10-20 21:30 | 816 | 816
2017-10-20 22:00 | 802 | 802
2017-10-20 22:30 | 795 | 795
2017-10-20 23:00 | 794 | 794
2017-10-20 23:30 | 748 | 746
2017-10-21 | 701 | 697
2017-10-21 00:30 | 652 | 644
2017-10-21 01:00 | 632 | 623
2017-10-21 01:30 | 617 | 607
2017-10-21 02:00 | 605 | 592
2017-10-21 02:30 | 594 | 581
2017-10-21 03:00 | 593 | 577
2017-10-21 03:30 | 593 | 575
2017-10-21 04:00 | 591 | 573
2017-10-21 04:30 | 593 | 577
2017-10-21 05:00 | 599 | 584
2017-10-21 05:30 | 608 | 593
2017-10-21 06:00 | 624 | 610
2017-10-21 06:30 | 659 | 649
2017-10-21 07:00 | 681 | 675
2017-10-21 07:30 | 725 | 723
2017-10-21 08:00 | 753 | 751
2017-10-21 08:30 | 794 | 794
2017-10-21 09:00 | 824 | 824
2017-10-21 09:30 | 847 | 846
2017-10-21 10:00 | 855 | 854
2017-10-21 10:30 | 846 | 845
2017-10-21 11:00 | 831 | 829
2017-10-21 11:30 | 814 | 812
2017-10-21 12:00 | 810 | 808
2017-10-21 12:30 | 810 | 807
2017-10-21 13:00 | 802 | 798
2017-10-21 13:30 | 802 | 798
2017-10-21 14:00 | 808 | 803
2017-10-21 14:30 | 799 | 794
2017-10-21 15:00 | 796 | 790
2017-10-21 15:30 | 800 | 794
2017-10-21 16:00 | 807 | 801
2017-10-21 16:30 | 821 | 816
2017-10-21 17:00 | 840 | 836
2017-10-21 17:30 | 842 | 839
2017-10-21 18:00 | 844 | 841
2017-10-21 18:30 | 867 | 866
2017-10-21 19:00 | 876 | 874
2017-10-21 19:30 | 862 | 858
2017-10-21 20:00 | 848 | 843
2017-10-21 20:30 | 839 | 833
2017-10-21 21:00 | 806 | 801
2017-10-21 21:30 | 775 | 774
2017-10-21 22:00 | 763 | 761
2017-10-21 22:30 | 765 | 762
2017-10-21 23:00 | 766 | 763
2017-10-21 23:30 | 737 | 732
2017-10-22 | 694 | 686
2017-10-22 00:30 | 648 | 636
2017-10-22 01:00 | 624 | 609
2017-10-22 01:30 | 602 | 585
2017-10-22 02:00 | 587 | 568
2017-10-22 02:30 | 577 | 557
2017-10-22 03:00 | 576 | 554
2017-10-22 03:30 | 568 | 544
2017-10-22 04:00 | 574 | 550
2017-10-22 04:30 | 572 | 547
2017-10-22 05:00 | 575 | 551
2017-10-22 05:30 | 574 | 545
2017-10-22 06:00 | 576 | 547
2017-10-22 06:30 | 577 | 550
2017-10-22 07:00 | 579 | 554
2017-10-22 07:30 | 585 | 567
2017-10-22 08:00 | 595 | 581
2017-10-22 08:30 | 602 | 591
2017-10-22 09:00 | 591 | 583
2017-10-22 09:30 | 586 | 581
2017-10-22 10:00 | 582 | 578
2017-10-22 10:30 | 580 | 577
2017-10-22 11:00 | 596 | 594
2017-10-22 11:30 | 610 | 608
2017-10-22 12:00 | 622 | 621
2017-10-22 12:30 | 623 | 622
2017-10-22 13:00 | 618 | 616
2017-10-22 13:30 | 613 | 611
2017-10-22 14:00 | 616 | 614
2017-10-22 14:30 | 626 | 624
2017-10-22 15:00 | 645 | 643
2017-10-22 15:30 | 668 | 667
2017-10-22 16:00 | 699 | 698
2017-10-22 16:30 | 723 | 722
2017-10-22 17:00 | 757 | 757
2017-10-22 17:30 | 779 | 779
2017-10-22 18:00 | 803 | 803
2017-10-22 18:30 | 847 | 847
2017-10-22 19:00 | 870 | 869
2017-10-22 19:30 | 851 | 849
2017-10-22 20:00 | 845 | 842
2017-10-22 20:30 | 832 | 829
2017-10-22 21:00 | 805 | 799
2017-10-22 21:30 | 771 | 765
2017-10-22 22:00 | 741 | 739
2017-10-22 22:30 | 734 | 732
2017-10-22 23:00 | 737 | 734
2017-10-22 23:30 | 703 | 699
2017-10-23 | 659 | 652
2017-10-23 00:30 | 624 | 614
2017-10-23 01:00 | 602 | 589
2017-10-23 01:30 | 580 | 564
2017-10-23 02:00 | 571 | 555
2017-10-23 02:30 | 565 | 548
2017-10-23 03:00 | 561 | 542
2017-10-23 03:30 | 559 | 540
2017-10-23 04:00 | 572 | 553
2017-10-23 04:30 | 580 | 563
2017-10-23 05:00 | 598 | 585
2017-10-23 05:30 | 626 | 614
2017-10-23 06:00 | 699 | 692
2017-10-23 06:30 | 779 | 777
2017-10-23 07:00 | 834 | 834
2017-10-23 07:30 | 852 | 852
2017-10-23 08:00 | 854 | 854
2017-10-23 08:30 | 837 | 836
2017-10-23 09:00 | 837 | 837
2017-10-23 09:30 | 879 | 879
2017-10-23 10:00 | 950 | 949
2017-10-23 10:30 | 977 | 976
2017-10-23 11:00 | 957 | 956
2017-10-23 11:30 | 931 | 930
2017-10-23 12:00 | 936 | 934
2017-10-23 12:30 | 911 | 909
2017-10-23 13:00 | 880 | 876
2017-10-23 13:30 | 861 | 857
2017-10-23 14:00 | 861 | 856
2017-10-23 14:30 | 862 | 857
2017-10-23 15:00 | 860 | 854
2017-10-23 15:30 | 906 | 901
2017-10-23 16:00 | 925 | 922
2017-10-23 16:30 | 940 | 935
2017-10-23 17:00 | 966 | 963
2017-10-23 17:30 | 964 | 960
2017-10-23 18:00 | 919 | 913
2017-10-23 18:30 | 943 | 938
2017-10-23 19:00 | 955 | 951
2017-10-23 19:30 | 933 | 927
2017-10-23 20:00 | 919 | 914
2017-10-23 20:30 | 903 | 898
2017-10-23 21:00 | 859 | 854
2017-10-23 21:30 | 818 | 816
2017-10-23 22:00 | 789 | 787
2017-10-23 22:30 | 773 | 770
2017-10-23 23:00 | 766 | 762
2017-10-23 23:30 | 728 | 723
2017-10-24 | 685 | 678
2017-10-24 00:30 | 639 | 627
2017-10-24 01:00 | 619 | 606
2017-10-24 01:30 | 600 | 587
2017-10-24 02:00 | 586 | 571
2017-10-24 02:30 | 581 | 565
2017-10-24 03:00 | 577 | 561
2017-10-24 03:30 | 576 | 560
2017-10-24 04:00 | 581 | 565
2017-10-24 04:30 | 592 | 578
2017-10-24 05:00 | 610 | 598
2017-10-24 05:30 | 644 | 635
2017-10-24 06:00 | 715 | 709
2017-10-24 06:30 | 776 | 774
2017-10-24 07:00 | 810 | 810
2017-10-24 07:30 | 837 | 837
2017-10-24 08:00 | 832 | 832
2017-10-24 08:30 | 820 | 820
2017-10-24 09:00 | 798 | 798
2017-10-24 09:30 | 797 | 797
2017-10-24 10:00 | 795 | 795
2017-10-24 10:30 | 787 | 787
2017-10-24 11:00 | 780 | 780
2017-10-24 11:30 | 782 | 782
2017-10-24 12:00 | 796 | 796
2017-10-24 12:30 | 793 | 793
2017-10-24 13:00 | 799 | 799
2017-10-24 13:30 | 802 | 802
2017-10-24 14:00 | 810 | 810
2017-10-24 14:30 | 820 | 820
2017-10-24 15:00 | 832 | 832
2017-10-24 15:30 | 748 | 748
2017-10-24 16:00 | 766 | 764
2017-10-24 16:30 | 852 | 851
2017-10-24 17:00 | 889 | 889
2017-10-24 17:30 | 990 | 990
2017-10-24 18:00 | 993 | 992
2017-10-24 18:30 | 1023 | 1022
2017-10-24 19:00 | 1026 | 1024
2017-10-24 19:30 | 945 | 940
2017-10-24 20:00 | 899 | 894
2017-10-24 20:30 | 857 | 856
2017-10-24 21:00 | 855 | 855
2017-10-24 21:30 | 818 | 818
2017-10-24 22:00 | 791 | 790
2017-10-24 22:30 | 773 | 770
2017-10-24 23:00 | 762 | 759
2017-10-24 23:30 | 719 | 716
2017-10-25 | 679 | 674
2017-10-25 00:30 | 639 | 631
2017-10-25 01:00 | 617 | 608
2017-10-25 01:30 | 596 | 585
2017-10-25 02:00 | 587 | 573
2017-10-25 02:30 | 584 | 568
2017-10-25 03:00 | 572 | 556
2017-10-25 03:30 | 569 | 551
2017-10-25 04:00 | 570 | 553
2017-10-25 04:30 | 578 | 563
2017-10-25 05:00 | 595 | 581
2017-10-25 05:30 | 666 | 654
2017-10-25 06:00 | 713 | 706
2017-10-25 06:30 | 751 | 748
2017-10-25 07:00 | 787 | 787
2017-10-25 07:30 | 833 | 831
2017-10-25 08:00 | 851 | 845
2017-10-25 08:30 | 836 | 832
2017-10-25 09:00 | 811 | 808
2017-10-25 09:30 | 797 | 794
2017-10-25 10:00 | 792 | 790
2017-10-25 10:30 | 793 | 792
2017-10-25 11:00 | 797 | 796
2017-10-25 11:30 | 802 | 796
2017-10-25 12:00 | 806 | 801
2017-10-25 12:30 | 820 | 817
2017-10-25 13:00 | 846 | 844
2017-10-25 13:30 | 871 | 869
2017-10-25 14:00 | 871 | 869
2017-10-25 14:30 | 899 | 898
2017-10-25 15:00 | 921 | 920
2017-10-25 15:30 | 942 | 941
2017-10-25 16:00 | 961 | 960
2017-10-25 16:30 | 984 | 983
2017-10-25 17:00 | 1005 | 1003
2017-10-25 17:30 | 1020 | 1016
2017-10-25 18:00 | 1018 | 1011
2017-10-25 18:30 | 1032 | 1026
2017-10-25 19:00 | 1055 | 1050
2017-10-25 19:30 | 987 | 978
2017-10-25 20:00 | 936 | 934
2017-10-25 20:30 | 915 | 913
2017-10-25 21:00 | 877 | 875
2017-10-25 21:30 | 833 | 833
2017-10-25 22:00 | 802 | 801
2017-10-25 22:30 | 788 | 784
2017-10-25 23:00 | 774 | 771
2017-10-25 23:30 | 727 | 725
2017-10-26 | 686 | 683
2017-10-26 00:30 | 642 | 636
2017-10-26 01:00 | 614 | 606
2017-10-26 01:30 | 602 | 592
2017-10-26 02:00 | 588 | 576
2017-10-26 02:30 | 583 | 571
2017-10-26 03:00 | 558 | 544
2017-10-26 03:30 | 533 | 515
2017-10-26 04:00 | 539 | 521
2017-10-26 04:30 | 552 | 537
2017-10-26 05:00 | 570 | 558
2017-10-26 05:30 | 598 | 587
2017-10-26 06:00 | 631 | 624
2017-10-26 06:30 | 674 | 673
2017-10-26 07:00 | 726 | 726
2017-10-26 07:30 | 762 | 761
2017-10-26 08:00 | 760 | 760
2017-10-26 08:30 | 765 | 765
2017-10-26 09:00 | 755 | 754
2017-10-26 09:30 | 767 | 766
2017-10-26 10:00 | 777 | 777
2017-10-26 10:30 | 788 | 788
2017-10-26 11:00 | 779 | 779
2017-10-26 11:30 | 789 | 789
2017-10-26 12:00 | 805 | 805
2017-10-26 12:30 | 826 | 825
2017-10-26 13:00 | 838 | 837
2017-10-26 13:30 | 853 | 853
2017-10-26 14:00 | 883 | 883
2017-10-26 14:30 | 916 | 915
2017-10-26 15:00 | 932 | 932
2017-10-26 15:30 | 958 | 958
2017-10-26 16:00 | 1004 | 1004
2017-10-26 16:30 | 1045 | 1045
2017-10-26 17:00 | 1066 | 1066
2017-10-26 17:30 | 1069 | 1068
2017-10-26 18:00 | 1052 | 1051
2017-10-26 18:30 | 1021 | 1019
2017-10-26 19:00 | 1022 | 1020
2017-10-26 19:30 | 996 | 993
2017-10-26 20:00 | 977 | 974
2017-10-26 20:30 | 952 | 948
2017-10-26 21:00 | 910 | 907
2017-10-26 21:30 | 869 | 864
2017-10-26 22:00 | 830 | 829
2017-10-26 22:30 | 811 | 811
2017-10-26 23:00 | 794 | 792
2017-10-26 23:30 | 748 | 743
2017-10-27 | 701 | 693
2017-10-27 00:30 | 661 | 652
2017-10-27 01:00 | 630 | 624
2017-10-27 01:30 | 617 | 609
2017-10-27 02:00 | 606 | 596
2017-10-27 02:30 | 605 | 593
2017-10-27 03:00 | 600 | 588
2017-10-27 03:30 | 599 | 587
2017-10-27 04:00 | 599 | 588
2017-10-27 04:30 | 608 | 597
2017-10-27 05:00 | 614 | 604
2017-10-27 05:30 | 639 | 631
2017-10-27 06:00 | 704 | 700
2017-10-27 06:30 | 779 | 776
2017-10-27 07:00 | 821 | 817
2017-10-27 07:30 | 856 | 856
2017-10-27 08:00 | 852 | 851
2017-10-27 08:30 | 847 | 847
2017-10-27 09:00 | 835 | 835
2017-10-27 09:30 | 823 | 823
2017-10-27 10:00 | 815 | 815
2017-10-27 10:30 | 808 | 808
2017-10-27 11:00 | 817 | 815
2017-10-27 11:30 | 816 | 815
2017-10-27 12:00 | 824 | 824
2017-10-27 12:30 | 835 | 834
2017-10-27 13:00 | 853 | 852
2017-10-27 13:30 | 866 | 866
2017-10-27 14:00 | 894 | 894
2017-10-27 14:30 | 917 | 916
2017-10-27 15:00 | 950 | 949
2017-10-27 15:30 | 968 | 967
2017-10-27 16:00 | 992 | 991
2017-10-27 16:30 | 1006 | 1003
2017-10-27 17:00 | 1000 | 995
2017-10-27 17:30 | 990 | 980
2017-10-27 18:00 | 1001 | 990
2017-10-27 18:30 | 953 | 942
2017-10-27 19:00 | 970 | 964
2017-10-27 19:30 | 957 | 947
2017-10-27 20:00 | 935 | 927
2017-10-27 20:30 | 905 | 904
2017-10-27 21:00 | 865 | 864
2017-10-27 21:30 | 830 | 830
2017-10-27 22:00 | 796 | 795
2017-10-27 22:30 | 773 | 771
2017-10-27 23:00 | 770 | 768
2017-10-27 23:30 | 726 | 723
2017-10-28 | 682 | 676
2017-10-28 00:30 | 632 | 621
2017-10-28 01:00 | 603 | 589
2017-10-28 01:30 | 590 | 574
2017-10-28 02:00 | 576 | 560
2017-10-28 02:30 | 566 | 550
2017-10-28 03:00 | 558 | 540
2017-10-28 03:30 | 557 | 538
2017-10-28 04:00 | 558 | 539
2017-10-28 04:30 | 559 | 540
2017-10-28 05:00 | 564 | 545
2017-10-28 05:30 | 566 | 545
2017-10-28 06:00 | 612 | 597
2017-10-28 06:30 | 579 | 564
2017-10-28 07:00 | 585 | 574
2017-10-28 07:30 | 609 | 604
2017-10-28 08:00 | 624 | 621
2017-10-28 08:30 | 645 | 644
2017-10-28 09:00 | 651 | 650
2017-10-28 09:30 | 653 | 653
2017-10-28 10:00 | 654 | 653
2017-10-28 10:30 | 662 | 662
2017-10-28 11:00 | 665 | 665
2017-10-28 11:30 | 662 | 662
2017-10-28 12:00 | 674 | 673
2017-10-28 12:30 | 691 | 690
2017-10-28 13:00 | 685 | 684
2017-10-28 13:30 | 690 | 689
2017-10-28 14:00 | 703 | 702
2017-10-28 14:30 | 719 | 718
2017-10-28 15:00 | 737 | 737
2017-10-28 15:30 | 766 | 766
2017-10-28 16:00 | 803 | 801
2017-10-28 16:30 | 818 | 816
2017-10-28 17:00 | 838 | 835
2017-10-28 17:30 | 845 | 841
2017-10-28 18:00 | 847 | 843
2017-10-28 18:30 | 871 | 869
2017-10-28 19:00 | 891 | 888
2017-10-28 19:30 | 871 | 866
2017-10-28 20:00 | 866 | 859
2017-10-28 20:30 | 845 | 838
2017-10-28 21:00 | 809 | 806
2017-10-28 21:30 | 782 | 778
2017-10-28 22:00 | 769 | 763
2017-10-28 22:30 | 760 | 752
2017-10-28 23:00 | 759 | 750
2017-10-28 23:30 | 714 | 704
2017-10-29 | 661 | 657
2017-10-29 00:30 | 622 | 615
2017-10-29 01:00 | 597 | 587
2017-10-29 01:30 | 588 | 576
2017-10-29 02:00 | 579 | 565
2017-10-29 02:30 | 570 | 554
2017-10-29 03:00 | 553 | 535
2017-10-29 03:30 | 523 | 502
2017-10-29 04:00 | 479 | 454
2017-10-29 04:30 | 553 | 531
2017-10-29 05:00 | 559 | 538
2017-10-29 05:30 | 558 | 534
2017-10-29 06:00 | 599 | 580
2017-10-29 06:30 | 578 | 558
2017-10-29 07:00 | 567 | 548
2017-10-29 07:30 | 581 | 568
2017-10-29 08:00 | 593 | 585
2017-10-29 08:30 | 611 | 608
2017-10-29 09:00 | 562 | 560
2017-10-29 09:30 | 581 | 580
2017-10-29 10:00 | 648 | 647
2017-10-29 10:30 | 655 | 654
2017-10-29 11:00 | 633 | 633
2017-10-29 11:30 | 687 | 687
2017-10-29 12:00 | 699 | 699
2017-10-29 12:30 | 712 | 712
2017-10-29 13:00 | 734 | 734
2017-10-29 13:30 | 757 | 757
2017-10-29 14:00 | 780 | 780
2017-10-29 14:30 | 809 | 809
2017-10-29 15:00 | 849 | 848
2017-10-29 15:30 | 894 | 890
2017-10-29 16:00 | 935 | 932
2017-10-29 16:30 | 975 | 971
2017-10-29 17:00 | 1010 | 1005
2017-10-29 17:30 | 1010 | 1004
2017-10-29 18:00 | 1007 | 1002
2017-10-29 18:30 | 1027 | 1023
2017-10-29 19:00 | 1058 | 1053
2017-10-29 19:30 | 1011 | 1003
2017-10-29 20:00 | 959 | 955
2017-10-29 20:30 | 930 | 926
2017-10-29 21:00 | 870 | 867
2017-10-29 21:30 | 824 | 824
2017-10-29 22:00 | 777 | 776
2017-10-29 22:30 | 761 | 759
2017-10-29 23:00 | 751 | 748
2017-10-29 23:30 | 710 | 705
2017-10-30 | 665 | 659
2017-10-30 00:30 | 619 | 610
2017-10-30 01:00 | 603 | 593
2017-10-30 01:30 | 590 | 579
2017-10-30 02:00 | 579 | 566
2017-10-30 02:30 | 578 | 564
2017-10-30 03:00 | 570 | 555
2017-10-30 03:30 | 571 | 556
2017-10-30 04:00 | 570 | 556
2017-10-30 04:30 | 585 | 572
2017-10-30 05:00 | 595 | 585
2017-10-30 05:30 | 620 | 613
2017-10-30 06:00 | 683 | 681
2017-10-30 06:30 | 721 | 721
2017-10-30 07:00 | 784 | 784
2017-10-30 07:30 | 842 | 842
2017-10-30 08:00 | 850 | 850
2017-10-30 08:30 | 868 | 867
2017-10-30 09:00 | 903 | 903
2017-10-30 09:30 | 930 | 930
2017-10-30 10:00 | 931 | 929
2017-10-30 10:30 | 937 | 934
2017-10-30 11:00 | 935 | 932
2017-10-30 11:30 | 966 | 964
2017-10-30 12:00 | 981 | 980
2017-10-30 12:30 | 968 | 967
2017-10-30 13:00 | 987 | 986
2017-10-30 13:30 | 1002 | 1001
2017-10-30 14:00 | 1034 | 1033
2017-10-30 14:30 | 1113 | 1112
2017-10-30 15:00 | 1149 | 1148
2017-10-30 15:30 | 1137 | 1134
2017-10-30 16:00 | 1119 | 1115
2017-10-30 16:30 | 1119 | 1114
2017-10-30 17:00 | 1153 | 1148
2017-10-30 17:30 | 1150 | 1144
2017-10-30 18:00 | 1121 | 1112
2017-10-30 18:30 | 1112 | 1106
2017-10-30 19:00 | 1134 | 1132
2017-10-30 19:30 | 1096 | 1091
2017-10-30 20:00 | 1062 | 1060
2017-10-30 20:30 | 1024 | 1023
2017-10-30 21:00 | 963 | 963
2017-10-30 21:30 | 915 | 914
2017-10-30 22:00 | 876 | 875
2017-10-30 22:30 | 849 | 848
2017-10-30 23:00 | 829 | 828
2017-10-30 23:30 | 768 | 765
2017-10-31 | 713 | 709
2017-10-31 00:30 | 666 | 659
2017-10-31 01:00 | 634 | 630
2017-10-31 01:30 | 618 | 613
2017-10-31 02:00 | 610 | 603
2017-10-31 02:30 | 599 | 591
2017-10-31 03:00 | 597 | 588
2017-10-31 03:30 | 591 | 583
2017-10-31 04:00 | 593 | 585
2017-10-31 04:30 | 604 | 597
2017-10-31 05:00 | 613 | 606
2017-10-31 05:30 | 645 | 638
2017-10-31 06:00 | 668 | 665
2017-10-31 06:30 | 721 | 720
2017-10-31 07:00 | 773 | 773
2017-10-31 07:30 | 825 | 825
2017-10-31 08:00 | 796 | 795
2017-10-31 08:30 | 810 | 810
2017-10-31 09:00 | 808 | 808
2017-10-31 09:30 | 795 | 795
2017-10-31 10:00 | 794 | 794
2017-10-31 10:30 | 785 | 785
2017-10-31 11:00 | 777 | 777
2017-10-31 11:30 | 772 | 772
2017-10-31 12:00 | 775 | 775
2017-10-31 12:30 | 791 | 791
2017-10-31 13:00 | 784 | 784
2017-10-31 13:30 | 792 | 792
2017-10-31 14:00 | 807 | 807
2017-10-31 14:30 | 830 | 830
2017-10-31 15:00 | 849 | 848
2017-10-31 15:30 | 870 | 869
2017-10-31 16:00 | 908 | 907
2017-10-31 16:30 | 942 | 942
2017-10-31 17:00 | 961 | 960
2017-10-31 17:30 | 963 | 962
2017-10-31 18:00 | 941 | 937
2017-10-31 18:30 | 939 | 933
2017-10-31 19:00 | 963 | 959
2017-10-31 19:30 | 935 | 929
2017-10-31 20:00 | 921 | 917
2017-10-31 20:30 | 899 | 898
2017-10-31 21:00 | 846 | 845
2017-10-31 21:30 | 791 | 791
2017-10-31 22:00 | 760 | 758
2017-10-31 22:30 | 738 | 734
2017-10-31 23:00 | 720 | 714
2017-10-31 23:30 | 665 | 659
2017-11-01 | 609 | 602
2017-11-01 00:30 | 559 | 548
2017-11-01 01:00 | 544 | 529
2017-11-01 01:30 | 533 | 517
2017-11-01 02:00 | 524 | 506
2017-11-01 02:30 | 520 | 501
2017-11-01 03:00 | 515 | 497
2017-11-01 03:30 | 514 | 495
2017-11-01 04:00 | 514 | 497
2017-11-01 04:30 | 527 | 513
2017-11-01 05:00 | 540 | 526
2017-11-01 05:30 | 567 | 554
2017-11-01 06:00 | 601 | 593
2017-11-01 06:30 | 700 | 699
2017-11-01 07:00 | 737 | 737
2017-11-01 07:30 | 762 | 762
2017-11-01 08:00 | 781 | 780
2017-11-01 08:30 | 766 | 766
2017-11-01 09:00 | 763 | 763
2017-11-01 09:30 | 764 | 764
2017-11-01 10:00 | 770 | 770
2017-11-01 10:30 | 788 | 788
2017-11-01 11:00 | 766 | 766
2017-11-01 11:30 | 771 | 771
2017-11-01 12:00 | 766 | 766
2017-11-01 12:30 | 765 | 765
2017-11-01 13:00 | 750 | 750
2017-11-01 13:30 | 747 | 747
2017-11-01 14:00 | 767 | 767
2017-11-01 14:30 | 777 | 776
2017-11-01 15:00 | 784 | 783
2017-11-01 15:30 | 796 | 796
2017-11-01 16:00 | 831 | 831
2017-11-01 16:30 | 866 | 866
2017-11-01 17:00 | 924 | 924
2017-11-01 17:30 | 933 | 933
2017-11-01 18:00 | 913 | 913
2017-11-01 18:30 | 921 | 920
2017-11-01 19:00 | 964 | 964
2017-11-01 19:30 | 943 | 942
2017-11-01 20:00 | 906 | 905
2017-11-01 20:30 | 892 | 891
2017-11-01 21:00 | 838 | 838
2017-11-01 21:30 | 785 | 785
2017-11-01 22:00 | 745 | 744
2017-11-01 22:30 | 725 | 724
2017-11-01 23:00 | 716 | 715
2017-11-01 23:30 | 673 | 671
2017-11-02 | 625 | 619
2017-11-02 00:30 | 580 | 569
2017-11-02 01:00 | 562 | 549
2017-11-02 01:30 | 551 | 537
2017-11-02 02:00 | 543 | 526
2017-11-02 02:30 | 536 | 518
2017-11-02 03:00 | 535 | 516
2017-11-02 03:30 | 534 | 515
2017-11-02 04:00 | 538 | 520
2017-11-02 04:30 | 556 | 539
2017-11-02 05:00 | 566 | 548
2017-11-02 05:30 | 594 | 577
2017-11-02 06:00 | 621 | 611
2017-11-02 06:30 | 669 | 666
2017-11-02 07:00 | 709 | 707
2017-11-02 07:30 | 751 | 750
2017-11-02 08:00 | 762 | 761
2017-11-02 08:30 | 760 | 760
2017-11-02 09:00 | 757 | 757
2017-11-02 09:30 | 763 | 763
2017-11-02 10:00 | 764 | 764
2017-11-02 10:30 | 764 | 764
2017-11-02 11:00 | 770 | 770
2017-11-02 11:30 | 765 | 764
2017-11-02 12:00 | 771 | 771
2017-11-02 12:30 | 782 | 782
2017-11-02 13:00 | 808 | 808
2017-11-02 13:30 | 829 | 829
2017-11-02 14:00 | 850 | 850
2017-11-02 14:30 | 854 | 854
2017-11-02 15:00 | 866 | 866
2017-11-02 15:30 | 882 | 882
2017-11-02 16:00 | 916 | 916
2017-11-02 16:30 | 942 | 942
2017-11-02 17:00 | 964 | 964
2017-11-02 17:30 | 965 | 964
2017-11-02 18:00 | 962 | 960
2017-11-02 18:30 | 965 | 965
2017-11-02 19:00 | 1010 | 1010
2017-11-02 19:30 | 987 | 985
2017-11-02 20:00 | 966 | 966
2017-11-02 20:30 | 950 | 948
2017-11-02 21:00 | 912 | 910
2017-11-02 21:30 | 861 | 860
2017-11-02 22:00 | 829 | 829
2017-11-02 22:30 | 815 | 814
2017-11-02 23:00 | 799 | 797
2017-11-02 23:30 | 746 | 743
2017-11-03 | 692 | 687
2017-11-03 00:30 | 655 | 647
2017-11-03 01:00 | 624 | 613
2017-11-03 01:30 | 607 | 594
2017-11-03 02:00 | 603 | 587
2017-11-03 02:30 | 597 | 581
2017-11-03 03:00 | 593 | 577
2017-11-03 03:30 | 596 | 580
2017-11-03 04:00 | 597 | 583
2017-11-03 04:30 | 607 | 594
2017-11-03 05:00 | 639 | 626
2017-11-03 05:30 | 639 | 623
2017-11-03 06:00 | 657 | 647
2017-11-03 06:30 | 700 | 697
2017-11-03 07:00 | 752 | 751
2017-11-03 07:30 | 804 | 801
2017-11-03 08:00 | 828 | 825
2017-11-03 08:30 | 830 | 828
2017-11-03 09:00 | 839 | 836
2017-11-03 09:30 | 833 | 831
2017-11-03 10:00 | 826 | 825
2017-11-03 10:30 | 817 | 816
2017-11-03 11:00 | 823 | 822
2017-11-03 11:30 | 829 | 828
2017-11-03 12:00 | 833 | 831
2017-11-03 12:30 | 860 | 859
2017-11-03 13:00 | 880 | 879
2017-11-03 13:30 | 859 | 857
2017-11-03 14:00 | 853 | 851
2017-11-03 14:30 | 873 | 871
2017-11-03 15:00 | 896 | 895
2017-11-03 15:30 | 909 | 908
2017-11-03 16:00 | 938 | 937
2017-11-03 16:30 | 959 | 958
2017-11-03 17:00 | 976 | 974
2017-11-03 17:30 | 977 | 973
2017-11-03 18:00 | 956 | 948
2017-11-03 18:30 | 938 | 935
2017-11-03 19:00 | 967 | 966
2017-11-03 19:30 | 948 | 946
2017-11-03 20:00 | 937 | 934
2017-11-03 20:30 | 914 | 913
2017-11-03 21:00 | 881 | 880
2017-11-03 21:30 | 856 | 852
2017-11-03 22:00 | 826 | 822
2017-11-03 22:30 | 815 | 808
2017-11-03 23:00 | 801 | 798
2017-11-03 23:30 | 745 | 741
2017-11-04 | 698 | 691
2017-11-04 00:30 | 662 | 652
2017-11-04 01:00 | 636 | 623
2017-11-04 01:30 | 621 | 606
2017-11-04 02:00 | 605 | 588
2017-11-04 02:30 | 600 | 581
2017-11-04 03:00 | 599 | 578
2017-11-04 03:30 | 596 | 575
2017-11-04 04:00 | 592 | 571
2017-11-04 04:30 | 598 | 577
2017-11-04 05:00 | 596 | 573
2017-11-04 05:30 | 602 | 578
2017-11-04 06:00 | 605 | 584
2017-11-04 06:30 | 627 | 612
2017-11-04 07:00 | 634 | 623
2017-11-04 07:30 | 656 | 651
2017-11-04 08:00 | 663 | 661
2017-11-04 08:30 | 685 | 685
2017-11-04 09:00 | 696 | 695
2017-11-04 09:30 | 679 | 678
2017-11-04 10:00 | 683 | 683
2017-11-04 10:30 | 696 | 696
2017-11-04 11:00 | 673 | 673
2017-11-04 11:30 | 700 | 700
2017-11-04 12:00 | 686 | 684
2017-11-04 12:30 | 684 | 682
2017-11-04 13:00 | 730 | 729
2017-11-04 13:30 | 737 | 736
2017-11-04 14:00 | 765 | 764
2017-11-04 14:30 | 771 | 769
2017-11-04 15:00 | 798 | 796
2017-11-04 15:30 | 815 | 813
2017-11-04 16:00 | 846 | 844
2017-11-04 16:30 | 868 | 866
2017-11-04 17:00 | 899 | 897
2017-11-04 17:30 | 900 | 897
2017-11-04 18:00 | 897 | 891
2017-11-04 18:30 | 913 | 908
2017-11-04 19:00 | 941 | 939
2017-11-04 19:30 | 920 | 916
2017-11-04 20:00 | 896 | 890
2017-11-04 20:30 | 877 | 873
2017-11-04 21:00 | 853 | 849
2017-11-04 21:30 | 823 | 818
2017-11-04 22:00 | 805 | 800
2017-11-04 22:30 | 800 | 793
2017-11-04 23:00 | 788 | 785
2017-11-04 23:30 | 748 | 745
2017-11-05 | 699 | 694
2017-11-05 00:30 | 659 | 651
2017-11-05 01:00 | 634 | 623
2017-11-05 01:30 | 621 | 610
2017-11-05 02:00 | 610 | 596
2017-11-05 02:30 | 603 | 587
2017-11-05 03:00 | 598 | 581
2017-11-05 03:30 | 595 | 578
2017-11-05 04:00 | 592 | 575
2017-11-05 04:30 | 591 | 574
2017-11-05 05:00 | 588 | 570
2017-11-05 05:30 | 601 | 583
2017-11-05 06:00 | 605 | 587
2017-11-05 06:30 | 611 | 596
2017-11-05 07:00 | 625 | 614
2017-11-05 07:30 | 653 | 648
2017-11-05 08:00 | 683 | 680
2017-11-05 08:30 | 701 | 700
2017-11-05 09:00 | 707 | 707
2017-11-05 09:30 | 704 | 704
2017-11-05 10:00 | 718 | 718
2017-11-05 10:30 | 687 | 687
2017-11-05 11:00 | 646 | 646
2017-11-05 11:30 | 712 | 712
2017-11-05 12:00 | 696 | 696
2017-11-05 12:30 | 692 | 691
2017-11-05 13:00 | 704 | 703
2017-11-05 13:30 | 719 | 718
2017-11-05 14:00 | 741 | 740
2017-11-05 14:30 | 766 | 766
2017-11-05 15:00 | 777 | 777
2017-11-05 15:30 | 807 | 807
2017-11-05 16:00 | 841 | 841
2017-11-05 16:30 | 861 | 860
2017-11-05 17:00 | 901 | 901
2017-11-05 17:30 | 924 | 922
2017-11-05 18:00 | 926 | 925
2017-11-05 18:30 | 944 | 943
2017-11-05 19:00 | 970 | 970
2017-11-05 19:30 | 939 | 938
2017-11-05 20:00 | 912 | 911
2017-11-05 20:30 | 893 | 893
2017-11-05 21:00 | 854 | 854
2017-11-05 21:30 | 813 | 813
2017-11-05 22:00 | 781 | 780
2017-11-05 22:30 | 775 | 772
2017-11-05 23:00 | 771 | 769
2017-11-05 23:30 | 722 | 718
2017-11-06 | 662 | 655
2017-11-06 00:30 | 624 | 611
2017-11-06 01:00 | 605 | 588
2017-11-06 01:30 | 594 | 576
2017-11-06 02:00 | 589 | 569
2017-11-06 02:30 | 581 | 559
2017-11-06 03:00 | 587 | 564
2017-11-06 03:30 | 583 | 561
2017-11-06 04:00 | 583 | 562
2017-11-06 04:30 | 592 | 575
2017-11-06 05:00 | 591 | 575
2017-11-06 05:30 | 620 | 606
2017-11-06 06:00 | 648 | 640
2017-11-06 06:30 | 718 | 717
2017-11-06 07:00 | 772 | 770
2017-11-06 07:30 | 817 | 816
2017-11-06 08:00 | 814 | 814
2017-11-06 08:30 | 853 | 853
2017-11-06 09:00 | 866 | 866
2017-11-06 09:30 | 882 | 881
2017-11-06 10:00 | 868 | 867
2017-11-06 10:30 | 840 | 838
2017-11-06 11:00 | 852 | 851
2017-11-06 11:30 | 867 | 867
2017-11-06 12:00 | 906 | 906
2017-11-06 12:30 | 871 | 871
2017-11-06 13:00 | 886 | 885
2017-11-06 13:30 | 917 | 917
2017-11-06 14:00 | 883 | 883
2017-11-06 14:30 | 902 | 902
2017-11-06 15:00 | 909 | 908
2017-11-06 15:30 | 939 | 938
2017-11-06 16:00 | 978 | 975
2017-11-06 16:30 | 1010 | 1004
2017-11-06 17:00 | 1047 | 1042
2017-11-06 17:30 | 1055 | 1047
2017-11-06 18:00 | 1043 | 1032
2017-11-06 18:30 | 1050 | 1041
2017-11-06 19:00 | 1083 | 1076
2017-11-06 19:30 | 1051 | 1043
2017-11-06 20:00 | 1016 | 1010
2017-11-06 20:30 | 986 | 985
2017-11-06 21:00 | 939 | 936
2017-11-06 21:30 | 885 | 883
2017-11-06 22:00 | 832 | 828
2017-11-06 22:30 | 813 | 808
2017-11-06 23:00 | 785 | 781
2017-11-06 23:30 | 731 | 725
2017-11-07 | 681 | 674
2017-11-07 00:30 | 643 | 634
2017-11-07 01:00 | 621 | 609
2017-11-07 01:30 | 608 | 593
2017-11-07 02:00 | 601 | 583
2017-11-07 02:30 | 594 | 575
2017-11-07 03:00 | 593 | 574
2017-11-07 03:30 | 591 | 572
2017-11-07 04:00 | 586 | 568
2017-11-07 04:30 | 593 | 576
2017-11-07 05:00 | 604 | 590
2017-11-07 05:30 | 626 | 614
2017-11-07 06:00 | 651 | 643
2017-11-07 06:30 | 712 | 710
2017-11-07 07:00 | 754 | 753
2017-11-07 07:30 | 788 | 788
2017-11-07 08:00 | 808 | 807
2017-11-07 08:30 | 821 | 819
2017-11-07 09:00 | 827 | 827
2017-11-07 09:30 | 844 | 844
2017-11-07 10:00 | 856 | 856
2017-11-07 10:30 | 872 | 872
2017-11-07 11:00 | 891 | 889
2017-11-07 11:30 | 882 | 878
2017-11-07 12:00 | 857 | 851
2017-11-07 12:30 | 813 | 808
2017-11-07 13:00 | 835 | 831
2017-11-07 13:30 | 827 | 824
2017-11-07 14:00 | 876 | 875
2017-11-07 14:30 | 873 | 870
2017-11-07 15:00 | 894 | 891
2017-11-07 15:30 | 904 | 901
2017-11-07 16:00 | 922 | 918
2017-11-07 16:30 | 926 | 921
2017-11-07 17:00 | 949 | 945
2017-11-07 17:30 | 944 | 939
2017-11-07 18:00 | 927 | 920
2017-11-07 18:30 | 926 | 919
2017-11-07 19:00 | 954 | 949
2017-11-07 19:30 | 934 | 928
2017-11-07 20:00 | 924 | 919
2017-11-07 20:30 | 918 | 915
2017-11-07 21:00 | 879 | 876
2017-11-07 21:30 | 834 | 832
2017-11-07 22:00 | 804 | 802
2017-11-07 22:30 | 791 | 789
2017-11-07 23:00 | 790 | 787
2017-11-07 23:30 | 743 | 738
2017-11-08 | 699 | 693
2017-11-08 00:30 | 658 | 651
2017-11-08 01:00 | 636 | 625
2017-11-08 01:30 | 618 | 606
2017-11-08 02:00 | 612 | 597
2017-11-08 02:30 | 610 | 592
2017-11-08 03:00 | 605 | 588
2017-11-08 03:30 | 606 | 589
2017-11-08 04:00 | 609 | 593
2017-11-08 04:30 | 620 | 605
2017-11-08 05:00 | 633 | 618
2017-11-08 05:30 | 659 | 647
2017-11-08 06:00 | 685 | 677
2017-11-08 06:30 | 736 | 734
2017-11-08 07:00 | 787 | 784
2017-11-08 07:30 | 822 | 819
2017-11-08 08:00 | 817 | 813
2017-11-08 08:30 | 830 | 828
2017-11-08 09:00 | 827 | 826
2017-11-08 09:30 | 809 | 808
2017-11-08 10:00 | 817 | 817
2017-11-08 10:30 | 825 | 825
2017-11-08 11:00 | 832 | 832
2017-11-08 11:30 | 837 | 837
2017-11-08 12:00 | 868 | 868
2017-11-08 12:30 | 859 | 859
2017-11-08 13:00 | 846 | 846
2017-11-08 13:30 | 875 | 875
2017-11-08 14:00 | 896 | 896
2017-11-08 14:30 | 872 | 871
2017-11-08 15:00 | 844 | 843
2017-11-08 15:30 | 852 | 850
2017-11-08 16:00 | 871 | 869
2017-11-08 16:30 | 878 | 876
2017-11-08 17:00 | 898 | 895
2017-11-08 17:30 | 920 | 917
2017-11-08 18:00 | 919 | 915
2017-11-08 18:30 | 923 | 921
2017-11-08 19:00 | 965 | 964
2017-11-08 19:30 | 938 | 937
2017-11-08 20:00 | 923 | 920
2017-11-08 20:30 | 907 | 903
2017-11-08 21:00 | 861 | 860
2017-11-08 21:30 | 820 | 820
2017-11-08 22:00 | 798 | 797
2017-11-08 22:30 | 788 | 785
2017-11-08 23:00 | 781 | 777
2017-11-08 23:30 | 729 | 723
2017-11-09 | 676 | 666
2017-11-09 00:30 | 630 | 616
2017-11-09 01:00 | 610 | 592
2017-11-09 01:30 | 596 | 575
2017-11-09 02:00 | 588 | 566
2017-11-09 02:30 | 582 | 557
2017-11-09 03:00 | 583 | 558
2017-11-09 03:30 | 580 | 555
2017-11-09 04:00 | 585 | 562
2017-11-09 04:30 | 590 | 570
2017-11-09 05:00 | 601 | 581
2017-11-09 05:30 | 630 | 612
2017-11-09 06:00 | 644 | 633
2017-11-09 06:30 | 680 | 675
2017-11-09 07:00 | 718 | 712
2017-11-09 07:30 | 750 | 746
2017-11-09 08:00 | 744 | 742
2017-11-09 08:30 | 746 | 745
2017-11-09 09:00 | 750 | 750
2017-11-09 09:30 | 751 | 751
2017-11-09 10:00 | 756 | 755
2017-11-09 10:30 | 754 | 754
2017-11-09 11:00 | 752 | 749
2017-11-09 11:30 | 766 | 764
2017-11-09 12:00 | 777 | 774
2017-11-09 12:30 | 775 | 772
2017-11-09 13:00 | 758 | 754
2017-11-09 13:30 | 752 | 748
2017-11-09 14:00 | 771 | 767
2017-11-09 14:30 | 803 | 800
2017-11-09 15:00 | 822 | 818
2017-11-09 15:30 | 835 | 831
2017-11-09 16:00 | 867 | 864
2017-11-09 16:30 | 896 | 893
2017-11-09 17:00 | 920 | 919
2017-11-09 17:30 | 933 | 932
2017-11-09 18:00 | 945 | 944
2017-11-09 18:30 | 959 | 958
2017-11-09 19:00 | 996 | 992
2017-11-09 19:30 | 974 | 967
2017-11-09 20:00 | 957 | 949
2017-11-09 20:30 | 906 | 902
2017-11-09 21:00 | 851 | 850
2017-11-09 21:30 | 807 | 805
2017-11-09 22:00 | 777 | 775
2017-11-09 22:30 | 766 | 765
2017-11-09 23:00 | 765 | 763
2017-11-09 23:30 | 717 | 712
2017-11-10 | 671 | 662
2017-11-10 00:30 | 633 | 618
2017-11-10 01:00 | 609 | 592
2017-11-10 01:30 | 596 | 576
2017-11-10 02:00 | 590 | 567
2017-11-10 02:30 | 558 | 536
2017-11-10 03:00 | 551 | 528
2017-11-10 03:30 | 552 | 531
2017-11-10 04:00 | 553 | 532
2017-11-10 04:30 | 561 | 543
2017-11-10 05:00 | 575 | 555
2017-11-10 05:30 | 621 | 603
2017-11-10 06:00 | 649 | 637
2017-11-10 06:30 | 691 | 687
2017-11-10 07:00 | 730 | 728
2017-11-10 07:30 | 765 | 765
2017-11-10 08:00 | 797 | 795
2017-11-10 08:30 | 805 | 803
2017-11-10 09:00 | 826 | 824
2017-11-10 09:30 | 816 | 813
2017-11-10 10:00 | 806 | 801
2017-11-10 10:30 | 789 | 783
2017-11-10 11:00 | 767 | 761
2017-11-10 11:30 | 775 | 770
2017-11-10 12:00 | 786 | 781
2017-11-10 12:30 | 772 | 766
2017-11-10 13:00 | 759 | 754
2017-11-10 13:30 | 760 | 754
2017-11-10 14:00 | 760 | 754
2017-11-10 14:30 | 769 | 763
2017-11-10 15:00 | 784 | 778
2017-11-10 15:30 | 792 | 785
2017-11-10 16:00 | 823 | 817
2017-11-10 16:30 | 847 | 841
2017-11-10 17:00 | 863 | 856
2017-11-10 17:30 | 873 | 864
2017-11-10 18:00 | 868 | 856
2017-11-10 18:30 | 874 | 863
2017-11-10 19:00 | 892 | 884
2017-11-10 19:30 | 882 | 871
2017-11-10 20:00 | 863 | 856
2017-11-10 20:30 | 843 | 840
2017-11-10 21:00 | 811 | 808
2017-11-10 21:30 | 781 | 778
2017-11-10 22:00 | 763 | 760
2017-11-10 22:30 | 753 | 751
2017-11-10 23:00 | 755 | 752
2017-11-10 23:30 | 717 | 712
2017-11-11 | 672 | 664
2017-11-11 00:30 | 631 | 618
2017-11-11 01:00 | 604 | 588
2017-11-11 01:30 | 592 | 574
2017-11-11 02:00 | 582 | 562
2017-11-11 02:30 | 576 | 555
2017-11-11 03:00 | 572 | 550
2017-11-11 03:30 | 569 | 547
2017-11-11 04:00 | 575 | 554
2017-11-11 04:30 | 579 | 560
2017-11-11 05:00 | 573 | 550
2017-11-11 05:30 | 584 | 560
2017-11-11 06:00 | 594 | 571
2017-11-11 06:30 | 612 | 593
2017-11-11 07:00 | 633 | 619
2017-11-11 07:30 | 656 | 648
2017-11-11 08:00 | 689 | 685
2017-11-11 08:30 | 713 | 711
2017-11-11 09:00 | 722 | 720
2017-11-11 09:30 | 712 | 710
2017-11-11 10:00 | 709 | 707
2017-11-11 10:30 | 702 | 701
2017-11-11 11:00 | 683 | 682
2017-11-11 11:30 | 672 | 670
2017-11-11 12:00 | 655 | 653
2017-11-11 12:30 | 660 | 656
2017-11-11 13:00 | 683 | 680
2017-11-11 13:30 | 668 | 665
2017-11-11 14:00 | 669 | 666
2017-11-11 14:30 | 693 | 690
2017-11-11 15:00 | 718 | 715
2017-11-11 15:30 | 714 | 711
2017-11-11 16:00 | 728 | 725
2017-11-11 16:30 | 749 | 746
2017-11-11 17:00 | 770 | 768
2017-11-11 17:30 | 778 | 776
2017-11-11 18:00 | 784 | 782
2017-11-11 18:30 | 802 | 801
2017-11-11 19:00 | 831 | 830
2017-11-11 19:30 | 819 | 818
2017-11-11 20:00 | 811 | 810
2017-11-11 20:30 | 799 | 797
2017-11-11 21:00 | 770 | 768
2017-11-11 21:30 | 749 | 746
2017-11-11 22:00 | 735 | 732
2017-11-11 22:30 | 731 | 726
2017-11-11 23:00 | 739 | 734
2017-11-11 23:30 | 703 | 695
2017-11-12 | 667 | 656
2017-11-12 00:30 | 629 | 612
2017-11-12 01:00 | 603 | 583
2017-11-12 01:30 | 591 | 569
2017-11-12 02:00 | 575 | 550
2017-11-12 02:30 | 569 | 543
2017-11-12 03:00 | 565 | 537
2017-11-12 03:30 | 557 | 530
2017-11-12 04:00 | 565 | 541
2017-11-12 04:30 | 566 | 543
2017-11-12 05:00 | 564 | 537
2017-11-12 05:30 | 586 | 559
2017-11-12 06:00 | 571 | 543
2017-11-12 06:30 | 559 | 530
2017-11-12 07:00 | 601 | 584
2017-11-12 07:30 | 612 | 600
2017-11-12 08:00 | 620 | 611
2017-11-12 08:30 | 641 | 636
2017-11-12 09:00 | 639 | 635
2017-11-12 09:30 | 620 | 617
2017-11-12 10:00 | 623 | 620
2017-11-12 10:30 | 623 | 622
2017-11-12 11:00 | 611 | 609
2017-11-12 11:30 | 592 | 589
2017-11-12 12:00 | 591 | 589
2017-11-12 12:30 | 584 | 581
2017-11-12 13:00 | 582 | 579
2017-11-12 13:30 | 589 | 587
2017-11-12 14:00 | 608 | 606
2017-11-12 14:30 | 622 | 620
2017-11-12 15:00 | 632 | 631
2017-11-12 15:30 | 651 | 649
2017-11-12 16:00 | 682 | 680
2017-11-12 16:30 | 716 | 715
2017-11-12 17:00 | 751 | 750
2017-11-12 17:30 | 768 | 768
2017-11-12 18:00 | 790 | 789
2017-11-12 18:30 | 818 | 817
2017-11-12 19:00 | 861 | 857
2017-11-12 19:30 | 852 | 846
2017-11-12 20:00 | 840 | 832
2017-11-12 20:30 | 828 | 818
2017-11-12 21:00 | 794 | 784
2017-11-12 21:30 | 758 | 753
2017-11-12 22:00 | 734 | 731
2017-11-12 22:30 | 726 | 721
2017-11-12 23:00 | 725 | 720
2017-11-12 23:30 | 693 | 685
2017-11-13 | 656 | 644
2017-11-13 00:30 | 610 | 595
2017-11-13 01:00 | 568 | 550
2017-11-13 01:30 | 562 | 542
2017-11-13 02:00 | 565 | 543
2017-11-13 02:30 | 562 | 539
2017-11-13 03:00 | 562 | 539
2017-11-13 03:30 | 564 | 542
2017-11-13 04:00 | 581 | 562
2017-11-13 04:30 | 577 | 557
2017-11-13 05:00 | 594 | 574
2017-11-13 05:30 | 619 | 603
2017-11-13 06:00 | 643 | 633
2017-11-13 06:30 | 690 | 686
2017-11-13 07:00 | 727 | 725
2017-11-13 07:30 | 762 | 761
2017-11-13 08:00 | 777 | 776
2017-11-13 08:30 | 785 | 785
2017-11-13 09:00 | 775 | 775
2017-11-13 09:30 | 774 | 774
2017-11-13 10:00 | 763 | 763
2017-11-13 10:30 | 760 | 760
2017-11-13 11:00 | 758 | 757
2017-11-13 11:30 | 746 | 745
2017-11-13 12:00 | 754 | 754
2017-11-13 12:30 | 750 | 750
2017-11-13 13:00 | 748 | 747
2017-11-13 13:30 | 744 | 743
2017-11-13 14:00 | 755 | 754
2017-11-13 14:30 | 765 | 763
2017-11-13 15:00 | 784 | 783
2017-11-13 15:30 | 811 | 810
2017-11-13 16:00 | 844 | 844
2017-11-13 16:30 | 873 | 873
2017-11-13 17:00 | 910 | 906
2017-11-13 17:30 | 918 | 911
2017-11-13 18:00 | 922 | 912
2017-11-13 18:30 | 918 | 914
2017-11-13 19:00 | 949 | 948
2017-11-13 19:30 | 935 | 934
2017-11-13 20:00 | 919 | 916
2017-11-13 20:30 | 898 | 896
2017-11-13 21:00 | 855 | 855
2017-11-13 21:30 | 820 | 819
2017-11-13 22:00 | 787 | 787
2017-11-13 22:30 | 766 | 765
2017-11-13 23:00 | 753 | 751
2017-11-13 23:30 | 711 | 707
2017-11-14 | 657 | 648
2017-11-14 00:30 | 627 | 615
2017-11-14 01:00 | 601 | 585
2017-11-14 01:30 | 584 | 565
2017-11-14 02:00 | 576 | 555
2017-11-14 02:30 | 570 | 548
2017-11-14 03:00 | 568 | 545
2017-11-14 03:30 | 566 | 543
2017-11-14 04:00 | 569 | 547
2017-11-14 04:30 | 577 | 557
2017-11-14 05:00 | 586 | 566
2017-11-14 05:30 | 614 | 597
2017-11-14 06:00 | 640 | 628
2017-11-14 06:30 | 676 | 672
2017-11-14 07:00 | 714 | 709
2017-11-14 07:30 | 739 | 732
2017-11-14 08:00 | 752 | 743
2017-11-14 08:30 | 756 | 750
2017-11-14 09:00 | 765 | 760
2017-11-14 09:30 | 764 | 758
2017-11-14 10:00 | 758 | 749
2017-11-14 10:30 | 755 | 746
2017-11-14 11:00 | 752 | 745
2017-11-14 11:30 | 747 | 739
2017-11-14 12:00 | 747 | 740
2017-11-14 12:30 | 741 | 735
2017-11-14 13:00 | 745 | 738
2017-11-14 13:30 | 748 | 742
2017-11-14 14:00 | 759 | 754
2017-11-14 14:30 | 758 | 752
2017-11-14 15:00 | 772 | 767
2017-11-14 15:30 | 796 | 792
2017-11-14 16:00 | 827 | 823
2017-11-14 16:30 | 855 | 851
2017-11-14 17:00 | 882 | 877
2017-11-14 17:30 | 894 | 887
2017-11-14 18:00 | 896 | 887
2017-11-14 18:30 | 897 | 887
2017-11-14 19:00 | 937 | 930
2017-11-14 19:30 | 916 | 907
2017-11-14 20:00 | 907 | 896
2017-11-14 20:30 | 888 | 884
2017-11-14 21:00 | 846 | 842
2017-11-14 21:30 | 809 | 804
2017-11-14 22:00 | 778 | 774
2017-11-14 22:30 | 756 | 754
2017-11-14 23:00 | 748 | 745
2017-11-14 23:30 | 705 | 700
2017-11-15 | 658 | 650
2017-11-15 00:30 | 615 | 601
2017-11-15 01:00 | 583 | 567
2017-11-15 01:30 | 571 | 552
2017-11-15 02:00 | 564 | 543
2017-11-15 02:30 | 549 | 527
2017-11-15 03:00 | 548 | 524
2017-11-15 03:30 | 548 | 524
2017-11-15 04:00 | 552 | 529
2017-11-15 04:30 | 560 | 541
2017-11-15 05:00 | 570 | 550
2017-11-15 05:30 | 599 | 582
2017-11-15 06:00 | 631 | 619
2017-11-15 06:30 | 671 | 667
2017-11-15 07:00 | 712 | 711
2017-11-15 07:30 | 747 | 747
2017-11-15 08:00 | 753 | 752
2017-11-15 08:30 | 769 | 769
2017-11-15 09:00 | 761 | 761
2017-11-15 09:30 | 750 | 749
2017-11-15 10:00 | 760 | 760
2017-11-15 10:30 | 764 | 763
2017-11-15 11:00 | 761 | 761
2017-11-15 11:30 | 762 | 762
2017-11-15 12:00 | 761 | 761
2017-11-15 12:30 | 784 | 783
2017-11-15 13:00 | 815 | 815
2017-11-15 13:30 | 823 | 823
2017-11-15 14:00 | 826 | 826
2017-11-15 14:30 | 860 | 860
2017-11-15 15:00 | 840 | 840
2017-11-15 15:30 | 821 | 819
2017-11-15 16:00 | 836 | 833
2017-11-15 16:30 | 861 | 859
2017-11-15 17:00 | 886 | 884
2017-11-15 17:30 | 892 | 890
2017-11-15 18:00 | 886 | 884
2017-11-15 18:30 | 892 | 891
2017-11-15 19:00 | 940 | 939
2017-11-15 19:30 | 921 | 917
2017-11-15 20:00 | 907 | 901
2017-11-15 20:30 | 886 | 880
2017-11-15 21:00 | 833 | 832
2017-11-15 21:30 | 801 | 799
2017-11-15 22:00 | 770 | 767
2017-11-15 22:30 | 749 | 746
2017-11-15 23:00 | 742 | 737
2017-11-15 23:30 | 701 | 694
2017-11-16 | 658 | 646
2017-11-16 00:30 | 617 | 600
2017-11-16 01:00 | 582 | 565
2017-11-16 01:30 | 571 | 555
2017-11-16 02:00 | 565 | 547
2017-11-16 02:30 | 560 | 540
2017-11-16 03:00 | 557 | 537
2017-11-16 03:30 | 561 | 541
2017-11-16 04:00 | 573 | 556
2017-11-16 04:30 | 589 | 574
2017-11-16 05:00 | 605 | 588
2017-11-16 05:30 | 631 | 617
2017-11-16 06:00 | 662 | 648
2017-11-16 06:30 | 700 | 695
2017-11-16 07:00 | 743 | 741
2017-11-16 07:30 | 777 | 777
2017-11-16 08:00 | 803 | 802
2017-11-16 08:30 | 826 | 826
2017-11-16 09:00 | 814 | 814
2017-11-16 09:30 | 816 | 816
2017-11-16 10:00 | 834 | 833
2017-11-16 10:30 | 814 | 814
2017-11-16 11:00 | 811 | 811
2017-11-16 11:30 | 809 | 809
2017-11-16 12:00 | 807 | 807
2017-11-16 12:30 | 800 | 799
2017-11-16 13:00 | 827 | 824
2017-11-16 13:30 | 845 | 842
2017-11-16 14:00 | 863 | 861
2017-11-16 14:30 | 889 | 887
2017-11-16 15:00 | 894 | 892
2017-11-16 15:30 | 895 | 892
2017-11-16 16:00 | 889 | 884
2017-11-16 16:30 | 906 | 900
2017-11-16 17:00 | 934 | 929
2017-11-16 17:30 | 940 | 932
2017-11-16 18:00 | 930 | 920
2017-11-16 18:30 | 940 | 932
2017-11-16 19:00 | 976 | 971
2017-11-16 19:30 | 964 | 958
2017-11-16 20:00 | 955 | 946
2017-11-16 20:30 | 921 | 913
2017-11-16 21:00 | 878 | 876
2017-11-16 21:30 | 839 | 834
2017-11-16 22:00 | 811 | 804
2017-11-16 22:30 | 797 | 788
2017-11-16 23:00 | 778 | 773
2017-11-16 23:30 | 733 | 729
2017-11-17 | 684 | 677
2017-11-17 00:30 | 638 | 628
2017-11-17 01:00 | 620 | 606
2017-11-17 01:30 | 604 | 589
2017-11-17 02:00 | 595 | 579
2017-11-17 02:30 | 591 | 575
2017-11-17 03:00 | 587 | 570
2017-11-17 03:30 | 584 | 567
2017-11-17 04:00 | 589 | 573
2017-11-17 04:30 | 597 | 583
2017-11-17 05:00 | 613 | 597
2017-11-17 05:30 | 634 | 620
2017-11-17 06:00 | 663 | 655
2017-11-17 06:30 | 705 | 703
2017-11-17 07:00 | 734 | 733
2017-11-17 07:30 | 799 | 798
2017-11-17 08:00 | 831 | 831
2017-11-17 08:30 | 846 | 846
2017-11-17 09:00 | 838 | 838
2017-11-17 09:30 | 831 | 830
2017-11-17 10:00 | 831 | 831
2017-11-17 10:30 | 825 | 825
2017-11-17 11:00 | 797 | 797
2017-11-17 11:30 | 783 | 782
2017-11-17 12:00 | 787 | 787
2017-11-17 12:30 | 800 | 800
2017-11-17 13:00 | 807 | 807
2017-11-17 13:30 | 815 | 815
2017-11-17 14:00 | 819 | 819
2017-11-17 14:30 | 822 | 822
2017-11-17 15:00 | 833 | 833
2017-11-17 15:30 | 845 | 845
2017-11-17 16:00 | 875 | 874
2017-11-17 16:30 | 890 | 890
2017-11-17 17:00 | 901 | 900
2017-11-17 17:30 | 894 | 892
2017-11-17 18:00 | 885 | 880
2017-11-17 18:30 | 875 | 873
2017-11-17 19:00 | 909 | 909
2017-11-17 19:30 | 893 | 893
2017-11-17 20:00 | 882 | 882
2017-11-17 20:30 | 865 | 865
2017-11-17 21:00 | 835 | 833
2017-11-17 21:30 | 806 | 803
2017-11-17 22:00 | 782 | 776
2017-11-17 22:30 | 766 | 765
2017-11-17 23:00 | 766 | 765
2017-11-17 23:30 | 727 | 724
2017-11-18 | 685 | 680
2017-11-18 00:30 | 641 | 632
2017-11-18 01:00 | 618 | 607
2017-11-18 01:30 | 598 | 586
2017-11-18 02:00 | 585 | 571
2017-11-18 02:30 | 580 | 564
2017-11-18 03:00 | 569 | 553
2017-11-18 03:30 | 574 | 558
2017-11-18 04:00 | 574 | 558
2017-11-18 04:30 | 575 | 559
2017-11-18 05:00 | 578 | 561
2017-11-18 05:30 | 578 | 559
2017-11-18 06:00 | 595 | 579
2017-11-18 06:30 | 615 | 602
2017-11-18 07:00 | 643 | 634
2017-11-18 07:30 | 686 | 682
2017-11-18 08:00 | 716 | 714
2017-11-18 08:30 | 750 | 750
2017-11-18 09:00 | 775 | 775
2017-11-18 09:30 | 796 | 796
2017-11-18 10:00 | 806 | 805
2017-11-18 10:30 | 802 | 802
2017-11-18 11:00 | 796 | 795
2017-11-18 11:30 | 784 | 783
2017-11-18 12:00 | 784 | 783
2017-11-18 12:30 | 774 | 774
2017-11-18 13:00 | 778 | 778
2017-11-18 13:30 | 774 | 774
2017-11-18 14:00 | 763 | 763
2017-11-18 14:30 | 759 | 759
2017-11-18 15:00 | 765 | 765
2017-11-18 15:30 | 767 | 767
2017-11-18 16:00 | 780 | 780
2017-11-18 16:30 | 791 | 791
2017-11-18 17:00 | 799 | 798
2017-11-18 17:30 | 804 | 804
2017-11-18 18:00 | 804 | 804
2017-11-18 18:30 | 816 | 816
2017-11-18 19:00 | 845 | 844
2017-11-18 19:30 | 830 | 830
2017-11-18 20:00 | 821 | 821
2017-11-18 20:30 | 803 | 803
2017-11-18 21:00 | 782 | 781
2017-11-18 21:30 | 758 | 757
2017-11-18 22:00 | 745 | 744
2017-11-18 22:30 | 741 | 738
2017-11-18 23:00 | 743 | 740
2017-11-18 23:30 | 706 | 701
2017-11-19 | 670 | 662
2017-11-19 00:30 | 625 | 613
2017-11-19 01:00 | 600 | 585
2017-11-19 01:30 | 581 | 563
2017-11-19 02:00 | 569 | 550
2017-11-19 02:30 | 559 | 538
2017-11-19 03:00 | 548 | 526
2017-11-19 03:30 | 551 | 530
2017-11-19 04:00 | 548 | 525
2017-11-19 04:30 | 547 | 523
2017-11-19 05:00 | 548 | 517
2017-11-19 05:30 | 550 | 517
2017-11-19 06:00 | 561 | 530
2017-11-19 06:30 | 559 | 532
2017-11-19 07:00 | 557 | 532
2017-11-19 07:30 | 580 | 565
2017-11-19 08:00 | 617 | 607
2017-11-19 08:30 | 657 | 652
2017-11-19 09:00 | 676 | 673
2017-11-19 09:30 | 670 | 668
2017-11-19 10:00 | 680 | 679
2017-11-19 10:30 | 680 | 680
2017-11-19 11:00 | 674 | 674
2017-11-19 11:30 | 676 | 676
2017-11-19 12:00 | 679 | 678
2017-11-19 12:30 | 675 | 675
2017-11-19 13:00 | 662 | 661
2017-11-19 13:30 | 668 | 667
2017-11-19 14:00 | 673 | 672
2017-11-19 14:30 | 667 | 665
2017-11-19 15:00 | 660 | 659
2017-11-19 15:30 | 680 | 678
2017-11-19 16:00 | 703 | 702
2017-11-19 16:30 | 736 | 735
2017-11-19 17:00 | 755 | 754
2017-11-19 17:30 | 768 | 767
2017-11-19 18:00 | 784 | 784
2017-11-19 18:30 | 814 | 814
2017-11-19 19:00 | 860 | 859
2017-11-19 19:30 | 848 | 848
2017-11-19 20:00 | 836 | 836
2017-11-19 20:30 | 820 | 820
2017-11-19 21:00 | 788 | 787
2017-11-19 21:30 | 756 | 755
2017-11-19 22:00 | 739 | 736
2017-11-19 22:30 | 729 | 725
2017-11-19 23:00 | 726 | 721
2017-11-19 23:30 | 700 | 692
2017-11-20 | 658 | 646
2017-11-20 00:30 | 620 | 606
2017-11-20 01:00 | 599 | 581
2017-11-20 01:30 | 577 | 557
2017-11-20 02:00 | 569 | 545
2017-11-20 02:30 | 567 | 543
2017-11-20 03:00 | 569 | 545
2017-11-20 03:30 | 568 | 543
2017-11-20 04:00 | 568 | 544
2017-11-20 04:30 | 580 | 558
2017-11-20 05:00 | 591 | 569
2017-11-20 05:30 | 621 | 602
2017-11-20 06:00 | 643 | 630
2017-11-20 06:30 | 690 | 685
2017-11-20 07:00 | 733 | 729
2017-11-20 07:30 | 764 | 761
2017-11-20 08:00 | 770 | 768
2017-11-20 08:30 | 771 | 769
2017-11-20 09:00 | 768 | 767
2017-11-20 09:30 | 767 | 766
2017-11-20 10:00 | 760 | 759
2017-11-20 10:30 | 762 | 762
2017-11-20 11:00 | 751 | 751
2017-11-20 11:30 | 753 | 753
2017-11-20 12:00 | 746 | 746
2017-11-20 12:30 | 750 | 750
2017-11-20 13:00 | 765 | 765
2017-11-20 13:30 | 773 | 772
2017-11-20 14:00 | 801 | 801
2017-11-20 14:30 | 813 | 813
2017-11-20 15:00 | 823 | 823
2017-11-20 15:30 | 836 | 836
2017-11-20 16:00 | 866 | 866
2017-11-20 16:30 | 896 | 895
2017-11-20 17:00 | 929 | 923
2017-11-20 17:30 | 934 | 927
2017-11-20 18:00 | 935 | 924
2017-11-20 18:30 | 948 | 936
2017-11-20 19:00 | 981 | 975
2017-11-20 19:30 | 955 | 947
2017-11-20 20:00 | 927 | 918
2017-11-20 20:30 | 911 | 903
2017-11-20 21:00 | 866 | 863
2017-11-20 21:30 | 822 | 820
2017-11-20 22:00 | 794 | 792
2017-11-20 22:30 | 778 | 773
2017-11-20 23:00 | 782 | 779
2017-11-20 23:30 | 743 | 738
2017-11-21 | 696 | 687
2017-11-21 00:30 | 653 | 641
2017-11-21 01:00 | 626 | 610
2017-11-21 01:30 | 609 | 591
2017-11-21 02:00 | 601 | 580
2017-11-21 02:30 | 594 | 572
2017-11-21 03:00 | 586 | 563
2017-11-21 03:30 | 589 | 566
2017-11-21 04:00 | 591 | 569
2017-11-21 04:30 | 602 | 581
2017-11-21 05:00 | 613 | 592
2017-11-21 05:30 | 639 | 621
2017-11-21 06:00 | 668 | 656
2017-11-21 06:30 | 711 | 707
2017-11-21 07:00 | 752 | 750
2017-11-21 07:30 | 787 | 787
2017-11-21 08:00 | 799 | 798
2017-11-21 08:30 | 822 | 821
2017-11-21 09:00 | 814 | 814
2017-11-21 09:30 | 786 | 785
2017-11-21 10:00 | 775 | 774
2017-11-21 10:30 | 775 | 775
2017-11-21 11:00 | 768 | 768
2017-11-21 11:30 | 795 | 795
2017-11-21 12:00 | 814 | 814
2017-11-21 12:30 | 800 | 800
2017-11-21 13:00 | 801 | 801
2017-11-21 13:30 | 791 | 791
2017-11-21 14:00 | 823 | 823
2017-11-21 14:30 | 817 | 817
2017-11-21 15:00 | 804 | 804
2017-11-21 15:30 | 810 | 810
2017-11-21 16:00 | 853 | 852
2017-11-21 16:30 | 899 | 898
2017-11-21 17:00 | 920 | 916
2017-11-21 17:30 | 935 | 931
2017-11-21 18:00 | 944 | 939
2017-11-21 18:30 | 947 | 944
2017-11-21 19:00 | 965 | 964
2017-11-21 19:30 | 952 | 951
2017-11-21 20:00 | 950 | 949
2017-11-21 20:30 | 921 | 920
2017-11-21 21:00 | 879 | 879
2017-11-21 21:30 | 830 | 828
2017-11-21 22:00 | 806 | 802
2017-11-21 22:30 | 785 | 782
2017-11-21 23:00 | 781 | 778
2017-11-21 23:30 | 737 | 732
2017-11-22 | 696 | 688
2017-11-22 00:30 | 655 | 644
2017-11-22 01:00 | 634 | 620
2017-11-22 01:30 | 606 | 589
2017-11-22 02:00 | 599 | 580
2017-11-22 02:30 | 590 | 570
2017-11-22 03:00 | 582 | 560
2017-11-22 03:30 | 584 | 563
2017-11-22 04:00 | 580 | 558
2017-11-22 04:30 | 555 | 530
2017-11-22 05:00 | 608 | 587
2017-11-22 05:30 | 634 | 616
2017-11-22 06:00 | 660 | 648
2017-11-22 06:30 | 712 | 706
2017-11-22 07:00 | 755 | 752
2017-11-22 07:30 | 796 | 792
2017-11-22 08:00 | 795 | 793
2017-11-22 08:30 | 804 | 803
2017-11-22 09:00 | 797 | 796
2017-11-22 09:30 | 787 | 785
2017-11-22 10:00 | 770 | 765
2017-11-22 10:30 | 762 | 757
2017-11-22 11:00 | 765 | 761
2017-11-22 11:30 | 768 | 764
2017-11-22 12:00 | 772 | 769
2017-11-22 12:30 | 776 | 772
2017-11-22 13:00 | 765 | 760
2017-11-22 13:30 | 773 | 769
2017-11-22 14:00 | 794 | 790
2017-11-22 14:30 | 828 | 825
2017-11-22 15:00 | 830 | 826
2017-11-22 15:30 | 841 | 835
2017-11-22 16:00 | 875 | 870
2017-11-22 16:30 | 911 | 905
2017-11-22 17:00 | 955 | 950
2017-11-22 17:30 | 960 | 954
2017-11-22 18:00 | 961 | 953
2017-11-22 18:30 | 961 | 951
2017-11-22 19:00 | 984 | 977
2017-11-22 19:30 | 985 | 984
2017-11-22 20:00 | 974 | 972
2017-11-22 20:30 | 923 | 920
2017-11-22 21:00 | 869 | 866
2017-11-22 21:30 | 836 | 834
2017-11-22 22:00 | 803 | 800
2017-11-22 22:30 | 786 | 782
2017-11-22 23:00 | 790 | 788
2017-11-22 23:30 | 751 | 747
2017-11-23 | 705 | 697
2017-11-23 00:30 | 657 | 644
2017-11-23 01:00 | 621 | 606
2017-11-23 01:30 | 607 | 588
2017-11-23 02:00 | 595 | 576
2017-11-23 02:30 | 590 | 569
2017-11-23 03:00 | 587 | 566
2017-11-23 03:30 | 588 | 568
2017-11-23 04:00 | 591 | 569
2017-11-23 04:30 | 602 | 582
2017-11-23 05:00 | 610 | 590
2017-11-23 05:30 | 638 | 621
2017-11-23 06:00 | 665 | 653
2017-11-23 06:30 | 706 | 703
2017-11-23 07:00 | 746 | 746
2017-11-23 07:30 | 788 | 787
2017-11-23 08:00 | 800 | 798
2017-11-23 08:30 | 816 | 816
2017-11-23 09:00 | 814 | 813
2017-11-23 09:30 | 817 | 816
2017-11-23 10:00 | 818 | 818
2017-11-23 10:30 | 805 | 804
2017-11-23 11:00 | 803 | 802
2017-11-23 11:30 | 810 | 809
2017-11-23 12:00 | 797 | 795
2017-11-23 12:30 | 797 | 795
2017-11-23 13:00 | 801 | 799
2017-11-23 13:30 | 788 | 787
2017-11-23 14:00 | 798 | 796
2017-11-23 14:30 | 812 | 810
2017-11-23 15:00 | 841 | 839
2017-11-23 15:30 | 851 | 849
2017-11-23 16:00 | 874 | 872
2017-11-23 16:30 | 895 | 894
2017-11-23 17:00 | 918 | 916
2017-11-23 17:30 | 925 | 924
2017-11-23 18:00 | 926 | 926
2017-11-23 18:30 | 918 | 917
2017-11-23 19:00 | 955 | 955
2017-11-23 19:30 | 949 | 948
2017-11-23 20:00 | 939 | 939
2017-11-23 20:30 | 912 | 912
2017-11-23 21:00 | 880 | 879
2017-11-23 21:30 | 838 | 834
2017-11-23 22:00 | 798 | 795
2017-11-23 22:30 | 782 | 779
2017-11-23 23:00 | 769 | 767
2017-11-23 23:30 | 732 | 728
2017-11-24 | 688 | 681
2017-11-24 00:30 | 635 | 625
2017-11-24 01:00 | 605 | 594
2017-11-24 01:30 | 588 | 574
2017-11-24 02:00 | 577 | 561
2017-11-24 02:30 | 580 | 561
2017-11-24 03:00 | 580 | 562
2017-11-24 03:30 | 574 | 556
2017-11-24 04:00 | 581 | 563
2017-11-24 04:30 | 590 | 573
2017-11-24 05:00 | 601 | 583
2017-11-24 05:30 | 620 | 604
2017-11-24 06:00 | 647 | 635
2017-11-24 06:30 | 687 | 683
2017-11-24 07:00 | 738 | 738
2017-11-24 07:30 | 778 | 777
2017-11-24 08:00 | 790 | 788
2017-11-24 08:30 | 809 | 807
2017-11-24 09:00 | 814 | 814
2017-11-24 09:30 | 797 | 797
2017-11-24 10:00 | 803 | 803
2017-11-24 10:30 | 806 | 806
2017-11-24 11:00 | 803 | 803
2017-11-24 11:30 | 805 | 805
2017-11-24 12:00 | 806 | 805
2017-11-24 12:30 | 805 | 805
2017-11-24 13:00 | 807 | 806
2017-11-24 13:30 | 814 | 814
2017-11-24 14:00 | 834 | 834
2017-11-24 14:30 | 843 | 842
2017-11-24 15:00 | 861 | 860
2017-11-24 15:30 | 875 | 874
2017-11-24 16:00 | 899 | 898
2017-11-24 16:30 | 930 | 930
2017-11-24 17:00 | 949 | 949
2017-11-24 17:30 | 947 | 946
2017-11-24 18:00 | 935 | 932
2017-11-24 18:30 | 916 | 915
2017-11-24 19:00 | 942 | 941
2017-11-24 19:30 | 936 | 935
2017-11-24 20:00 | 927 | 927
2017-11-24 20:30 | 900 | 900
2017-11-24 21:00 | 866 | 866
2017-11-24 21:30 | 838 | 838
2017-11-24 22:00 | 828 | 827
2017-11-24 22:30 | 800 | 799
2017-11-24 23:00 | 793 | 793
2017-11-24 23:30 | 759 | 758
2017-11-25 | 709 | 708
2017-11-25 00:30 | 662 | 658
2017-11-25 01:00 | 623 | 617
2017-11-25 01:30 | 597 | 589
2017-11-25 02:00 | 588 | 578
2017-11-25 02:30 | 582 | 571
2017-11-25 03:00 | 575 | 563
2017-11-25 03:30 | 572 | 560
2017-11-25 04:00 | 572 | 560
2017-11-25 04:30 | 572 | 559
2017-11-25 05:00 | 570 | 554
2017-11-25 05:30 | 580 | 564
2017-11-25 06:00 | 580 | 566
2017-11-25 06:30 | 603 | 594
2017-11-25 07:00 | 617 | 611
2017-11-25 07:30 | 640 | 638
2017-11-25 08:00 | 677 | 677
2017-11-25 08:30 | 704 | 704
2017-11-25 09:00 | 724 | 723
2017-11-25 09:30 | 739 | 739
2017-11-25 10:00 | 740 | 740
2017-11-25 10:30 | 728 | 728
2017-11-25 11:00 | 723 | 723
2017-11-25 11:30 | 727 | 727
2017-11-25 12:00 | 715 | 715
2017-11-25 12:30 | 719 | 718
2017-11-25 13:00 | 726 | 725
2017-11-25 13:30 | 722 | 722
2017-11-25 14:00 | 735 | 734
2017-11-25 14:30 | 758 | 758
2017-11-25 15:00 | 776 | 776
2017-11-25 15:30 | 800 | 800
2017-11-25 16:00 | 824 | 824
2017-11-25 16:30 | 832 | 832
2017-11-25 17:00 | 856 | 855
2017-11-25 17:30 | 854 | 853
2017-11-25 18:00 | 849 | 847
2017-11-25 18:30 | 858 | 856
2017-11-25 19:00 | 881 | 880
2017-11-25 19:30 | 880 | 880
2017-11-25 20:00 | 876 | 875
2017-11-25 20:30 | 856 | 855
2017-11-25 21:00 | 823 | 823
2017-11-25 21:30 | 800 | 799
2017-11-25 22:00 | 782 | 780
2017-11-25 22:30 | 779 | 777
2017-11-25 23:00 | 782 | 778
2017-11-25 23:30 | 744 | 738
2017-11-26 | 691 | 687
2017-11-26 00:30 | 656 | 650
2017-11-26 01:00 | 632 | 623
2017-11-26 01:30 | 604 | 593
2017-11-26 02:00 | 589 | 576
2017-11-26 02:30 | 584 | 569
2017-11-26 03:00 | 576 | 560
2017-11-26 03:30 | 572 | 555
2017-11-26 04:00 | 569 | 552
2017-11-26 04:30 | 565 | 548
2017-11-26 05:00 | 559 | 539
2017-11-26 05:30 | 569 | 547
2017-11-26 06:00 | 570 | 549
2017-11-26 06:30 | 578 | 562
2017-11-26 07:00 | 580 | 568
2017-11-26 07:30 | 600 | 593
2017-11-26 08:00 | 638 | 636
2017-11-26 08:30 | 675 | 675
2017-11-26 09:00 | 698 | 698
2017-11-26 09:30 | 705 | 705
2017-11-26 10:00 | 709 | 709
2017-11-26 10:30 | 717 | 717
2017-11-26 11:00 | 712 | 712
2017-11-26 11:30 | 697 | 697
2017-11-26 12:00 | 687 | 687
2017-11-26 12:30 | 689 | 689
2017-11-26 13:00 | 693 | 693
2017-11-26 13:30 | 703 | 703
2017-11-26 14:00 | 726 | 726
2017-11-26 14:30 | 743 | 743
2017-11-26 15:00 | 761 | 761
2017-11-26 15:30 | 778 | 777
2017-11-26 16:00 | 824 | 823
2017-11-26 16:30 | 843 | 842
2017-11-26 17:00 | 871 | 870
2017-11-26 17:30 | 880 | 877
2017-11-26 18:00 | 891 | 881
2017-11-26 18:30 | 904 | 893
2017-11-26 19:00 | 925 | 919
2017-11-26 19:30 | 916 | 912
2017-11-26 20:00 | 903 | 902
2017-11-26 20:30 | 883 | 880
2017-11-26 21:00 | 851 | 846
2017-11-26 21:30 | 824 | 816
2017-11-26 22:00 | 800 | 788
2017-11-26 22:30 | 778 | 773
2017-11-26 23:00 | 771 | 766
2017-11-26 23:30 | 727 | 720
2017-11-27 | 683 | 677
2017-11-27 00:30 | 643 | 635
2017-11-27 01:00 | 619 | 608
2017-11-27 01:30 | 607 | 595
2017-11-27 02:00 | 601 | 588
2017-11-27 02:30 | 593 | 578
2017-11-27 03:00 | 587 | 573
2017-11-27 03:30 | 584 | 569
2017-11-27 04:00 | 584 | 571
2017-11-27 04:30 | 599 | 588
2017-11-27 05:00 | 607 | 595
2017-11-27 05:30 | 628 | 619
2017-11-27 06:00 | 664 | 660
2017-11-27 06:30 | 722 | 721
2017-11-27 07:00 | 770 | 770
2017-11-27 07:30 | 823 | 823
2017-11-27 08:00 | 845 | 845
2017-11-27 08:30 | 875 | 874
2017-11-27 09:00 | 874 | 873
2017-11-27 09:30 | 876 | 874
2017-11-27 10:00 | 875 | 872
2017-11-27 10:30 | 888 | 884
2017-11-27 11:00 | 907 | 903
2017-11-27 11:30 | 920 | 914
2017-11-27 12:00 | 925 | 918
2017-11-27 12:30 | 918 | 912
2017-11-27 13:00 | 914 | 908
2017-11-27 13:30 | 918 | 912
2017-11-27 14:00 | 939 | 932
2017-11-27 14:30 | 952 | 945
2017-11-27 15:00 | 968 | 962
2017-11-27 15:30 | 983 | 980
2017-11-27 16:00 | 1006 | 1003
2017-11-27 16:30 | 1032 | 1029
2017-11-27 17:00 | 1047 | 1045
2017-11-27 17:30 | 1041 | 1041
2017-11-27 18:00 | 1025 | 1025
2017-11-27 18:30 | 1012 | 1012
2017-11-27 19:00 | 1037 | 1037
2017-11-27 19:30 | 1024 | 1023
2017-11-27 20:00 | 1003 | 1002
2017-11-27 20:30 | 977 | 977
2017-11-27 21:00 | 936 | 936
2017-11-27 21:30 | 893 | 892
2017-11-27 22:00 | 860 | 856
2017-11-27 22:30 | 833 | 828
2017-11-27 23:00 | 818 | 814
2017-11-27 23:30 | 776 | 769
2017-11-28 | 729 | 721
2017-11-28 00:30 | 688 | 676
2017-11-28 01:00 | 665 | 650
2017-11-28 01:30 | 655 | 639
2017-11-28 02:00 | 641 | 625
2017-11-28 02:30 | 637 | 618
2017-11-28 03:00 | 634 | 614
2017-11-28 03:30 | 627 | 606
2017-11-28 04:00 | 669 | 652
2017-11-28 04:30 | 699 | 686
2017-11-28 05:00 | 703 | 689
2017-11-28 05:30 | 737 | 726
2017-11-28 06:00 | 766 | 761
2017-11-28 06:30 | 818 | 814
2017-11-28 07:00 | 864 | 863
2017-11-28 07:30 | 925 | 925
2017-11-28 08:00 | 955 | 955
2017-11-28 08:30 | 972 | 972
2017-11-28 09:00 | 973 | 973
2017-11-28 09:30 | 982 | 982
2017-11-28 10:00 | 984 | 984
2017-11-28 10:30 | 986 | 986
2017-11-28 11:00 | 996 | 996
2017-11-28 11:30 | 1009 | 1006
2017-11-28 12:00 | 1018 | 1015
2017-11-28 12:30 | 1034 | 1032
2017-11-28 13:00 | 1052 | 1050
2017-11-28 13:30 | 1061 | 1059
2017-11-28 14:00 | 1082 | 1081
2017-11-28 14:30 | 1094 | 1092
2017-11-28 15:00 | 1098 | 1095
2017-11-28 15:30 | 1117 | 1114
2017-11-28 16:00 | 1142 | 1139
2017-11-28 16:30 | 1160 | 1157
2017-11-28 17:00 | 1176 | 1173
2017-11-28 17:30 | 1175 | 1170
2017-11-28 18:00 | 1162 | 1153
2017-11-28 18:30 | 1147 | 1139
2017-11-28 19:00 | 1137 | 1132
2017-11-28 19:30 | 1089 | 1085
2017-11-28 20:00 | 1075 | 1072
2017-11-28 20:30 | 1052 | 1050
2017-11-28 21:00 | 999 | 999
2017-11-28 21:30 | 932 | 932
2017-11-28 22:00 | 883 | 883
2017-11-28 22:30 | 862 | 861
2017-11-28 23:00 | 846 | 845
2017-11-28 23:30 | 797 | 795
2017-11-29 | 746 | 742
2017-11-29 00:30 | 703 | 696
2017-11-29 01:00 | 680 | 671
2017-11-29 01:30 | 665 | 655
2017-11-29 02:00 | 657 | 646
2017-11-29 02:30 | 651 | 639
2017-11-29 03:00 | 645 | 633
2017-11-29 03:30 | 643 | 631
2017-11-29 04:00 | 646 | 635
2017-11-29 04:30 | 651 | 642
2017-11-29 05:00 | 667 | 658
2017-11-29 05:30 | 700 | 693
2017-11-29 06:00 | 733 | 730
2017-11-29 06:30 | 800 | 799
2017-11-29 07:00 | 856 | 854
2017-11-29 07:30 | 923 | 922
2017-11-29 08:00 | 960 | 959
2017-11-29 08:30 | 979 | 979
2017-11-29 09:00 | 986 | 985
2017-11-29 09:30 | 996 | 995
2017-11-29 10:00 | 1002 | 1001
2017-11-29 10:30 | 1012 | 1011
2017-11-29 11:00 | 1034 | 1033
2017-11-29 11:30 | 1044 | 1043
2017-11-29 12:00 | 1031 | 1030
2017-11-29 12:30 | 1022 | 1020
2017-11-29 13:00 | 1033 | 1031
2017-11-29 13:30 | 1024 | 1023
2017-11-29 14:00 | 1038 | 1038
2017-11-29 14:30 | 1030 | 1029
2017-11-29 15:00 | 1022 | 1022
2017-11-29 15:30 | 1009 | 1008
2017-11-29 16:00 | 1028 | 1027
2017-11-29 16:30 | 1033 | 1031
2017-11-29 17:00 | 1049 | 1048
2017-11-29 17:30 | 1047 | 1043
2017-11-29 18:00 | 1039 | 1034
2017-11-29 18:30 | 1030 | 1026
2017-11-29 19:00 | 1057 | 1056
2017-11-29 19:30 | 1042 | 1041
2017-11-29 20:00 | 1025 | 1025
2017-11-29 20:30 | 991 | 991
2017-11-29 21:00 | 950 | 948
2017-11-29 21:30 | 906 | 903
2017-11-29 22:00 | 865 | 860
2017-11-29 22:30 | 839 | 834
2017-11-29 23:00 | 836 | 832
2017-11-29 23:30 | 781 | 779
2017-11-30 | 735 | 730
2017-11-30 00:30 | 685 | 677
2017-11-30 01:00 | 661 | 651
2017-11-30 01:30 | 647 | 634
2017-11-30 02:00 | 640 | 625
2017-11-30 02:30 | 629 | 614
2017-11-30 03:00 | 619 | 603
2017-11-30 03:30 | 616 | 599
2017-11-30 04:00 | 668 | 654
2017-11-30 04:30 | 691 | 679
2017-11-30 05:00 | 702 | 691
2017-11-30 05:30 | 725 | 715
2017-11-30 06:00 | 756 | 750
2017-11-30 06:30 | 827 | 826
2017-11-30 07:00 | 891 | 891
2017-11-30 07:30 | 923 | 922
2017-11-30 08:00 | 987 | 987
2017-11-30 08:30 | 996 | 996
2017-11-30 09:00 | 1003 | 1003
2017-11-30 09:30 | 1030 | 1029
2017-11-30 10:00 | 1044 | 1044
2017-11-30 10:30 | 1040 | 1040
2017-11-30 11:00 | 1028 | 1028
2017-11-30 11:30 | 1015 | 1015
2017-11-30 12:00 | 1017 | 1017
2017-11-30 12:30 | 1003 | 1003
2017-11-30 13:00 | 1001 | 1001
2017-11-30 13:30 | 1013 | 1012
2017-11-30 14:00 | 1057 | 1057
2017-11-30 14:30 | 1069 | 1069
2017-11-30 15:00 | 1085 | 1085
2017-11-30 15:30 | 1059 | 1058
2017-11-30 16:00 | 1077 | 1076
2017-11-30 16:30 | 1068 | 1067
2017-11-30 17:00 | 1074 | 1071
2017-11-30 17:30 | 1061 | 1058
2017-11-30 18:00 | 1044 | 1039
2017-11-30 18:30 | 1029 | 1025
2017-11-30 19:00 | 1046 | 1046
2017-11-30 19:30 | 1033 | 1032
2017-11-30 20:00 | 1025 | 1025
2017-11-30 20:30 | 1009 | 1009
2017-11-30 21:00 | 970 | 970
2017-11-30 21:30 | 905 | 904
2017-11-30 22:00 | 867 | 865
2017-11-30 22:30 | 844 | 842
2017-11-30 23:00 | 828 | 824
2017-11-30 23:30 | 769 | 766
2017-12-01 | 718 | 715
2017-12-01 00:30 | 674 | 668
2017-12-01 01:00 | 648 | 639
2017-12-01 01:30 | 639 | 629
2017-12-01 02:00 | 630 | 618
2017-12-01 02:30 | 623 | 610
2017-12-01 03:00 | 620 | 606
2017-12-01 03:30 | 618 | 604
2017-12-01 04:00 | 618 | 605
2017-12-01 04:30 | 630 | 619
2017-12-01 05:00 | 638 | 626
2017-12-01 05:30 | 664 | 655
2017-12-01 06:00 | 692 | 688
2017-12-01 06:30 | 751 | 751
2017-12-01 07:00 | 797 | 797
2017-12-01 07:30 | 853 | 853
2017-12-01 08:00 | 865 | 865
2017-12-01 08:30 | 891 | 890
2017-12-01 09:00 | 902 | 901
2017-12-01 09:30 | 909 | 908
2017-12-01 10:00 | 922 | 921
2017-12-01 10:30 | 917 | 916
2017-12-01 11:00 | 926 | 925
2017-12-01 11:30 | 916 | 915
2017-12-01 12:00 | 922 | 920
2017-12-01 12:30 | 931 | 930
2017-12-01 13:00 | 936 | 935
2017-12-01 13:30 | 941 | 940
2017-12-01 14:00 | 955 | 954
2017-12-01 14:30 | 965 | 964
2017-12-01 15:00 | 973 | 973
2017-12-01 15:30 | 998 | 998
2017-12-01 16:00 | 1008 | 1007
2017-12-01 16:30 | 1014 | 1014
2017-12-01 17:00 | 1024 | 1023
2017-12-01 17:30 | 1005 | 1001
2017-12-01 18:00 | 967 | 960
2017-12-01 18:30 | 949 | 943
2017-12-01 19:00 | 974 | 971
2017-12-01 19:30 | 967 | 964
2017-12-01 20:00 | 958 | 955
2017-12-01 20:30 | 933 | 933
2017-12-01 21:00 | 898 | 898
2017-12-01 21:30 | 870 | 870
2017-12-01 22:00 | 841 | 840
2017-12-01 22:30 | 829 | 828
2017-12-01 23:00 | 820 | 818
2017-12-01 23:30 | 769 | 765
2017-12-02 | 722 | 718
2017-12-02 00:30 | 676 | 672
2017-12-02 01:00 | 641 | 636
2017-12-02 01:30 | 625 | 617
2017-12-02 02:00 | 610 | 598
2017-12-02 02:30 | 603 | 590
2017-12-02 03:00 | 601 | 586
2017-12-02 03:30 | 596 | 579
2017-12-02 04:00 | 595 | 579
2017-12-02 04:30 | 597 | 580
2017-12-02 05:00 | 596 | 577
2017-12-02 05:30 | 600 | 581
2017-12-02 06:00 | 604 | 589
2017-12-02 06:30 | 628 | 619
2017-12-02 07:00 | 645 | 641
2017-12-02 07:30 | 674 | 673
2017-12-02 08:00 | 701 | 700
2017-12-02 08:30 | 734 | 734
2017-12-02 09:00 | 766 | 765
2017-12-02 09:30 | 794 | 794
2017-12-02 10:00 | 803 | 803
2017-12-02 10:30 | 810 | 809
2017-12-02 11:00 | 790 | 790
2017-12-02 11:30 | 756 | 756
2017-12-02 12:00 | 745 | 745
2017-12-02 12:30 | 741 | 741
2017-12-02 13:00 | 760 | 760
2017-12-02 13:30 | 767 | 767
2017-12-02 14:00 | 790 | 790
2017-12-02 14:30 | 823 | 823
2017-12-02 15:00 | 852 | 852
2017-12-02 15:30 | 866 | 866
2017-12-02 16:00 | 877 | 877
2017-12-02 16:30 | 903 | 903
2017-12-02 17:00 | 928 | 928
2017-12-02 17:30 | 942 | 940
2017-12-02 18:00 | 932 | 929
2017-12-02 18:30 | 930 | 927
2017-12-02 19:00 | 965 | 964
2017-12-02 19:30 | 959 | 957
2017-12-02 20:00 | 943 | 940
2017-12-02 20:30 | 923 | 920
2017-12-02 21:00 | 881 | 879
2017-12-02 21:30 | 857 | 856
2017-12-02 22:00 | 831 | 828
2017-12-02 22:30 | 804 | 803
2017-12-02 23:00 | 801 | 800
2017-12-02 23:30 | 757 | 754
2017-12-03 | 707 | 701
2017-12-03 00:30 | 656 | 650
2017-12-03 01:00 | 636 | 629
2017-12-03 01:30 | 615 | 606
2017-12-03 02:00 | 608 | 597
2017-12-03 02:30 | 594 | 581
2017-12-03 03:00 | 590 | 576
2017-12-03 03:30 | 588 | 573
2017-12-03 04:00 | 590 | 574
2017-12-03 04:30 | 584 | 568
2017-12-03 05:00 | 588 | 571
2017-12-03 05:30 | 581 | 558
2017-12-03 06:00 | 588 | 567
2017-12-03 06:30 | 595 | 578
2017-12-03 07:00 | 599 | 586
2017-12-03 07:30 | 630 | 623
2017-12-03 08:00 | 653 | 649
2017-12-03 08:30 | 664 | 663
2017-12-03 09:00 | 693 | 693
2017-12-03 09:30 | 712 | 712
2017-12-03 10:00 | 723 | 723
2017-12-03 10:30 | 737 | 736
2017-12-03 11:00 | 759 | 759
2017-12-03 11:30 | 780 | 780
2017-12-03 12:00 | 788 | 788
2017-12-03 12:30 | 810 | 809
2017-12-03 13:00 | 842 | 842
2017-12-03 13:30 | 859 | 858
2017-12-03 14:00 | 879 | 878
2017-12-03 14:30 | 893 | 892
2017-12-03 15:00 | 882 | 882
2017-12-03 15:30 | 885 | 884
2017-12-03 16:00 | 927 | 926
2017-12-03 16:30 | 981 | 981
2017-12-03 17:00 | 1012 | 1011
2017-12-03 17:30 | 1021 | 1018
2017-12-03 18:00 | 1014 | 1010
2017-12-03 18:30 | 1005 | 1001
2017-12-03 19:00 | 1003 | 999
2017-12-03 19:30 | 1000 | 996
2017-12-03 20:00 | 978 | 974
2017-12-03 20:30 | 957 | 953
2017-12-03 21:00 | 909 | 908
2017-12-03 21:30 | 865 | 865
2017-12-03 22:00 | 826 | 825
2017-12-03 22:30 | 805 | 802
2017-12-03 23:00 | 796 | 790
2017-12-03 23:30 | 741 | 735
2017-12-04 | 697 | 687
2017-12-04 00:30 | 647 | 637
2017-12-04 01:00 | 620 | 611
2017-12-04 01:30 | 606 | 596
2017-12-04 02:00 | 599 | 587
2017-12-04 02:30 | 590 | 577
2017-12-04 03:00 | 587 | 574
2017-12-04 03:30 | 584 | 571
2017-12-04 04:00 | 587 | 575
2017-12-04 04:30 | 597 | 585
2017-12-04 05:00 | 611 | 599
2017-12-04 05:30 | 631 | 621
2017-12-04 06:00 | 663 | 659
2017-12-04 06:30 | 723 | 721
2017-12-04 07:00 | 766 | 766
2017-12-04 07:30 | 828 | 827
2017-12-04 08:00 | 890 | 889
2017-12-04 08:30 | 916 | 915
2017-12-04 09:00 | 940 | 939
2017-12-04 09:30 | 932 | 931
2017-12-04 10:00 | 960 | 959
2017-12-04 10:30 | 975 | 975
2017-12-04 11:00 | 1017 | 1017
2017-12-04 11:30 | 1053 | 1053
2017-12-04 12:00 | 1071 | 1069
2017-12-04 12:30 | 1080 | 1076
2017-12-04 13:00 | 1066 | 1062
2017-12-04 13:30 | 1051 | 1046
2017-12-04 14:00 | 1032 | 1027
2017-12-04 14:30 | 1014 | 1012
2017-12-04 15:00 | 980 | 975
2017-12-04 15:30 | 963 | 958
2017-12-04 16:00 | 961 | 958
2017-12-04 16:30 | 964 | 961
2017-12-04 17:00 | 973 | 970
2017-12-04 17:30 | 978 | 974
2017-12-04 18:00 | 962 | 961
2017-12-04 18:30 | 940 | 938
2017-12-04 19:00 | 954 | 953
2017-12-04 19:30 | 951 | 951
2017-12-04 20:00 | 938 | 936
2017-12-04 20:30 | 903 | 902
2017-12-04 21:00 | 859 | 858
2017-12-04 21:30 | 811 | 809
2017-12-04 22:00 | 774 | 773
2017-12-04 22:30 | 754 | 753
2017-12-04 23:00 | 742 | 740
2017-12-04 23:30 | 705 | 702
2017-12-05 | 656 | 650
2017-12-05 00:30 | 614 | 604
2017-12-05 01:00 | 592 | 581
2017-12-05 01:30 | 574 | 561
2017-12-05 02:00 | 566 | 549
2017-12-05 02:30 | 568 | 550
2017-12-05 03:00 | 565 | 546
2017-12-05 03:30 | 560 | 541
2017-12-05 04:00 | 562 | 544
2017-12-05 04:30 | 572 | 556
2017-12-05 05:00 | 583 | 569
2017-12-05 05:30 | 610 | 598
2017-12-05 06:00 | 631 | 624
2017-12-05 06:30 | 684 | 680
2017-12-05 07:00 | 715 | 713
2017-12-05 07:30 | 769 | 768
2017-12-05 08:00 | 808 | 808
2017-12-05 08:30 | 854 | 854
2017-12-05 09:00 | 874 | 873
2017-12-05 09:30 | 848 | 847
2017-12-05 10:00 | 828 | 827
2017-12-05 10:30 | 822 | 822
2017-12-05 11:00 | 838 | 838
2017-12-05 11:30 | 817 | 816
2017-12-05 12:00 | 814 | 813
2017-12-05 12:30 | 837 | 837
2017-12-05 13:00 | 851 | 851
2017-12-05 13:30 | 850 | 850
2017-12-05 14:00 | 877 | 877
2017-12-05 14:30 | 891 | 891
2017-12-05 15:00 | 938 | 938
2017-12-05 15:30 | 978 | 977
2017-12-05 16:00 | 1007 | 1006
2017-12-05 16:30 | 1008 | 1007
2017-12-05 17:00 | 1006 | 1005
2017-12-05 17:30 | 1026 | 1023
2017-12-05 18:00 | 1015 | 1008
2017-12-05 18:30 | 989 | 985
2017-12-05 19:00 | 1008 | 1007
2017-12-05 19:30 | 997 | 997
2017-12-05 20:00 | 967 | 966
2017-12-05 20:30 | 948 | 946
2017-12-05 21:00 | 898 | 898
2017-12-05 21:30 | 854 | 854
2017-12-05 22:00 | 811 | 809
2017-12-05 22:30 | 787 | 784
2017-12-05 23:00 | 772 | 768
2017-12-05 23:30 | 717 | 714
2017-12-06 | 668 | 663
2017-12-06 00:30 | 623 | 615
2017-12-06 01:00 | 596 | 585
2017-12-06 01:30 | 589 | 575
2017-12-06 02:00 | 575 | 560
2017-12-06 02:30 | 566 | 550
2017-12-06 03:00 | 557 | 540
2017-12-06 03:30 | 559 | 542
2017-12-06 04:00 | 565 | 547
2017-12-06 04:30 | 571 | 553
2017-12-06 05:00 | 584 | 566
2017-12-06 05:30 | 607 | 592
2017-12-06 06:00 | 634 | 625
2017-12-06 06:30 | 686 | 684
2017-12-06 07:00 | 729 | 729
2017-12-06 07:30 | 771 | 771
2017-12-06 08:00 | 778 | 778
2017-12-06 08:30 | 784 | 783
2017-12-06 09:00 | 783 | 783
2017-12-06 09:30 | 783 | 783
2017-12-06 10:00 | 805 | 803
2017-12-06 10:30 | 814 | 814
2017-12-06 11:00 | 810 | 810
2017-12-06 11:30 | 796 | 796
2017-12-06 12:00 | 797 | 797
2017-12-06 12:30 | 805 | 805
2017-12-06 13:00 | 823 | 823
2017-12-06 13:30 | 839 | 839
2017-12-06 14:00 | 867 | 867
2017-12-06 14:30 | 899 | 899
2017-12-06 15:00 | 928 | 928
2017-12-06 15:30 | 955 | 955
2017-12-06 16:00 | 1004 | 1003
2017-12-06 16:30 | 1048 | 1046
2017-12-06 17:00 | 1080 | 1078
2017-12-06 17:30 | 1088 | 1085
2017-12-06 18:00 | 1051 | 1043
2017-12-06 18:30 | 1027 | 1014
2017-12-06 19:00 | 1041 | 1034
2017-12-06 19:30 | 1046 | 1040
2017-12-06 20:00 | 1029 | 1021
2017-12-06 20:30 | 993 | 986
2017-12-06 21:00 | 940 | 937
2017-12-06 21:30 | 894 | 891
2017-12-06 22:00 | 861 | 855
2017-12-06 22:30 | 835 | 827
2017-12-06 23:00 | 813 | 811
2017-12-06 23:30 | 754 | 749
2017-12-07 | 701 | 696
2017-12-07 00:30 | 660 | 653
2017-12-07 01:00 | 633 | 624
2017-12-07 01:30 | 617 | 606
2017-12-07 02:00 | 606 | 594
2017-12-07 02:30 | 600 | 587
2017-12-07 03:00 | 591 | 578
2017-12-07 03:30 | 596 | 582
2017-12-07 04:00 | 597 | 584
2017-12-07 04:30 | 601 | 588
2017-12-07 05:00 | 610 | 595
2017-12-07 05:30 | 630 | 616
2017-12-07 06:00 | 655 | 648
2017-12-07 06:30 | 696 | 694
2017-12-07 07:00 | 737 | 737
2017-12-07 07:30 | 781 | 781
2017-12-07 08:00 | 801 | 800
2017-12-07 08:30 | 817 | 816
2017-12-07 09:00 | 827 | 825
2017-12-07 09:30 | 832 | 828
2017-12-07 10:00 | 841 | 838
2017-12-07 10:30 | 843 | 841
2017-12-07 11:00 | 851 | 851
2017-12-07 11:30 | 867 | 864
2017-12-07 12:00 | 869 | 868
2017-12-07 12:30 | 881 | 880
2017-12-07 13:00 | 901 | 901
2017-12-07 13:30 | 932 | 931
2017-12-07 14:00 | 960 | 960
2017-12-07 14:30 | 997 | 995
2017-12-07 15:00 | 1020 | 1018
2017-12-07 15:30 | 1048 | 1047
2017-12-07 16:00 | 1090 | 1089
2017-12-07 16:30 | 1129 | 1126
2017-12-07 17:00 | 1157 | 1154
2017-12-07 17:30 | 1149 | 1146
2017-12-07 18:00 | 1134 | 1130
2017-12-07 18:30 | 1111 | 1106
2017-12-07 19:00 | 1133 | 1130
2017-12-07 19:30 | 1145 | 1143
2017-12-07 20:00 | 1127 | 1124
2017-12-07 20:30 | 1087 | 1085
2017-12-07 21:00 | 1040 | 1040
2017-12-07 21:30 | 973 | 973
2017-12-07 22:00 | 914 | 912
2017-12-07 22:30 | 901 | 896
2017-12-07 23:00 | 898 | 894
2017-12-07 23:30 | 828 | 819
2017-12-08 | 763 | 756
2017-12-08 00:30 | 707 | 704
2017-12-08 01:00 | 676 | 671
2017-12-08 01:30 | 651 | 643
2017-12-08 02:00 | 646 | 637
2017-12-08 02:30 | 646 | 637
2017-12-08 03:00 | 625 | 614
2017-12-08 03:30 | 617 | 605
2017-12-08 04:00 | 622 | 610
2017-12-08 04:30 | 639 | 629
2017-12-08 05:00 | 648 | 638
2017-12-08 05:30 | 674 | 666
2017-12-08 06:00 | 699 | 695
2017-12-08 06:30 | 745 | 745
2017-12-08 07:00 | 799 | 798
2017-12-08 07:30 | 853 | 853
2017-12-08 08:00 | 896 | 896
2017-12-08 08:30 | 912 | 911
2017-12-08 09:00 | 939 | 935
2017-12-08 09:30 | 964 | 960
2017-12-08 10:00 | 976 | 972
2017-12-08 10:30 | 1004 | 1002
2017-12-08 11:00 | 1045 | 1044
2017-12-08 11:30 | 1104 | 1103
2017-12-08 12:00 | 1192 | 1191
2017-12-08 12:30 | 1241 | 1241
2017-12-08 13:00 | 1211 | 1205
2017-12-08 13:30 | 1123 | 1111
2017-12-08 14:00 | 1090 | 1080
2017-12-08 14:30 | 1065 | 1054
2017-12-08 15:00 | 1053 | 1040
2017-12-08 15:30 | 1033 | 1021
2017-12-08 16:00 | 1036 | 1028
2017-12-08 16:30 | 1028 | 1020
2017-12-08 17:00 | 1038 | 1029
2017-12-08 17:30 | 1033 | 1023
2017-12-08 18:00 | 1007 | 996
2017-12-08 18:30 | 968 | 958
2017-12-08 19:00 | 980 | 976
2017-12-08 19:30 | 970 | 965
2017-12-08 20:00 | 953 | 947
2017-12-08 20:30 | 934 | 929
2017-12-08 21:00 | 893 | 892
2017-12-08 21:30 | 859 | 857
2017-12-08 22:00 | 829 | 827
2017-12-08 22:30 | 828 | 823
2017-12-08 23:00 | 830 | 826
2017-12-08 23:30 | 783 | 778
2017-12-09 | 734 | 727
2017-12-09 00:30 | 683 | 675
2017-12-09 01:00 | 653 | 643
2017-12-09 01:30 | 639 | 626
2017-12-09 02:00 | 625 | 609
2017-12-09 02:30 | 616 | 597
2017-12-09 03:00 | 609 | 589
2017-12-09 03:30 | 597 | 576
2017-12-09 04:00 | 588 | 567
2017-12-09 04:30 | 585 | 565
2017-12-09 05:00 | 586 | 562
2017-12-09 05:30 | 595 | 572
2017-12-09 06:00 | 603 | 584
2017-12-09 06:30 | 621 | 609
2017-12-09 07:00 | 636 | 629
2017-12-09 07:30 | 663 | 661
2017-12-09 08:00 | 686 | 686
2017-12-09 08:30 | 709 | 709
2017-12-09 09:00 | 718 | 718
2017-12-09 09:30 | 684 | 684
2017-12-09 10:00 | 699 | 699
2017-12-09 10:30 | 711 | 711
2017-12-09 11:00 | 718 | 718
2017-12-09 11:30 | 745 | 745
2017-12-09 12:00 | 801 | 801
2017-12-09 12:30 | 815 | 815
2017-12-09 13:00 | 835 | 835
2017-12-09 13:30 | 852 | 852
2017-12-09 14:00 | 886 | 884
2017-12-09 14:30 | 910 | 909
2017-12-09 15:00 | 950 | 948
2017-12-09 15:30 | 987 | 985
2017-12-09 16:00 | 1007 | 1006
2017-12-09 16:30 | 1024 | 1023
2017-12-09 17:00 | 1023 | 1020
2017-12-09 17:30 | 1009 | 1004
2017-12-09 18:00 | 975 | 969
2017-12-09 18:30 | 954 | 945
2017-12-09 19:00 | 950 | 940
2017-12-09 19:30 | 934 | 928
2017-12-09 20:00 | 912 | 910
2017-12-09 20:30 | 892 | 890
2017-12-09 21:00 | 852 | 851
2017-12-09 21:30 | 837 | 836
2017-12-09 22:00 | 804 | 803
2017-12-09 22:30 | 797 | 796
2017-12-09 23:00 | 814 | 812
2017-12-09 23:30 | 774 | 770
2017-12-10 | 707 | 699
2017-12-10 00:30 | 649 | 637
2017-12-10 01:00 | 620 | 605
2017-12-10 01:30 | 604 | 587
2017-12-10 02:00 | 587 | 568
2017-12-10 02:30 | 577 | 556
2017-12-10 03:00 | 580 | 558
2017-12-10 03:30 | 577 | 554
2017-12-10 04:00 | 573 | 550
2017-12-10 04:30 | 575 | 551
2017-12-10 05:00 | 581 | 550
2017-12-10 05:30 | 576 | 545
2017-12-10 06:00 | 570 | 542
2017-12-10 06:30 | 581 | 558
2017-12-10 07:00 | 586 | 569
2017-12-10 07:30 | 598 | 587
2017-12-10 08:00 | 609 | 602
2017-12-10 08:30 | 643 | 640
2017-12-10 09:00 | 657 | 655
2017-12-10 09:30 | 674 | 674
2017-12-10 10:00 | 677 | 677
2017-12-10 10:30 | 691 | 691
2017-12-10 11:00 | 689 | 688
2017-12-10 11:30 | 680 | 680
2017-12-10 12:00 | 689 | 688
2017-12-10 12:30 | 685 | 685
2017-12-10 13:00 | 689 | 689
2017-12-10 13:30 | 696 | 696
2017-12-10 14:00 | 727 | 727
2017-12-10 14:30 | 760 | 759
2017-12-10 15:00 | 791 | 791
2017-12-10 15:30 | 823 | 823
2017-12-10 16:00 | 831 | 830
2017-12-10 16:30 | 836 | 836
2017-12-10 17:00 | 873 | 873
2017-12-10 17:30 | 895 | 892
2017-12-10 18:00 | 902 | 898
2017-12-10 18:30 | 911 | 906
2017-12-10 19:00 | 938 | 935
2017-12-10 19:30 | 955 | 954
2017-12-10 20:00 | 941 | 939
2017-12-10 20:30 | 925 | 921
2017-12-10 21:00 | 880 | 880
2017-12-10 21:30 | 846 | 846
2017-12-10 22:00 | 813 | 812
2017-12-10 22:30 | 792 | 791
2017-12-10 23:00 | 787 | 786
2017-12-10 23:30 | 733 | 730
2017-12-11 | 677 | 670
2017-12-11 00:30 | 630 | 619
2017-12-11 01:00 | 601 | 588
2017-12-11 01:30 | 588 | 573
2017-12-11 02:00 | 584 | 567
2017-12-11 02:30 | 592 | 575
2017-12-11 03:00 | 587 | 567
2017-12-11 03:30 | 584 | 564
2017-12-11 04:00 | 577 | 559
2017-12-11 04:30 | 587 | 571
2017-12-11 05:00 | 601 | 585
2017-12-11 05:30 | 628 | 615
2017-12-11 06:00 | 664 | 657
2017-12-11 06:30 | 727 | 725
2017-12-11 07:00 | 779 | 771
2017-12-11 07:30 | 809 | 806
2017-12-11 08:00 | 845 | 840
2017-12-11 08:30 | 863 | 861
2017-12-11 09:00 | 881 | 878
2017-12-11 09:30 | 900 | 898
2017-12-11 10:00 | 908 | 907
2017-12-11 10:30 | 912 | 910
2017-12-11 11:00 | 906 | 903
2017-12-11 11:30 | 889 | 887
2017-12-11 12:00 | 903 | 902
2017-12-11 12:30 | 903 | 901
2017-12-11 13:00 | 897 | 896
2017-12-11 13:30 | 898 | 896
2017-12-11 14:00 | 901 | 896
2017-12-11 14:30 | 918 | 911
2017-12-11 15:00 | 946 | 941
2017-12-11 15:30 | 983 | 978
2017-12-11 16:00 | 1027 | 1021
2017-12-11 16:30 | 1055 | 1049
2017-12-11 17:00 | 1076 | 1069
2017-12-11 17:30 | 1085 | 1076
2017-12-11 18:00 | 1080 | 1067
2017-12-11 18:30 | 1074 | 1057
2017-12-11 19:00 | 1090 | 1084
2017-12-11 19:30 | 1094 | 1089
2017-12-11 20:00 | 1070 | 1063
2017-12-11 20:30 | 1030 | 1023
2017-12-11 21:00 | 975 | 969
2017-12-11 21:30 | 917 | 912
2017-12-11 22:00 | 869 | 867
2017-12-11 22:30 | 845 | 841
2017-12-11 23:00 | 842 | 839
2017-12-11 23:30 | 781 | 775
2017-12-12 | 717 | 709
2017-12-12 00:30 | 663 | 656
2017-12-12 01:00 | 631 | 621
2017-12-12 01:30 | 612 | 600
2017-12-12 02:00 | 611 | 597
2017-12-12 02:30 | 600 | 585
2017-12-12 03:00 | 585 | 570
2017-12-12 03:30 | 585 | 570
2017-12-12 04:00 | 591 | 577
2017-12-12 04:30 | 604 | 591
2017-12-12 05:00 | 609 | 595
2017-12-12 05:30 | 643 | 633
2017-12-12 06:00 | 670 | 665
2017-12-12 06:30 | 727 | 725
2017-12-12 07:00 | 768 | 766
2017-12-12 07:30 | 797 | 797
2017-12-12 08:00 | 813 | 813
2017-12-12 08:30 | 846 | 845
2017-12-12 09:00 | 881 | 881
2017-12-12 09:30 | 917 | 916
2017-12-12 10:00 | 912 | 912
2017-12-12 10:30 | 885 | 885
2017-12-12 11:00 | 873 | 873
2017-12-12 11:30 | 858 | 858
2017-12-12 12:00 | 849 | 849
2017-12-12 12:30 | 840 | 840
2017-12-12 13:00 | 842 | 842
2017-12-12 13:30 | 851 | 851
2017-12-12 14:00 | 860 | 860
2017-12-12 14:30 | 880 | 880
2017-12-12 15:00 | 916 | 916
2017-12-12 15:30 | 962 | 961
2017-12-12 16:00 | 994 | 993
2017-12-12 16:30 | 1026 | 1025
2017-12-12 17:00 | 1056 | 1056
2017-12-12 17:30 | 1072 | 1071
2017-12-12 18:00 | 1052 | 1049
2017-12-12 18:30 | 1039 | 1037
2017-12-12 19:00 | 1063 | 1062
2017-12-12 19:30 | 1069 | 1068
2017-12-12 20:00 | 1046 | 1046
2017-12-12 20:30 | 1001 | 1001
2017-12-12 21:00 | 942 | 940
2017-12-12 21:30 | 899 | 896
2017-12-12 22:00 | 862 | 858
2017-12-12 22:30 | 851 | 848
2017-12-12 23:00 | 853 | 852
2017-12-12 23:30 | 802 | 798
2017-12-13 | 728 | 723
2017-12-13 00:30 | 671 | 666
2017-12-13 01:00 | 640 | 632
2017-12-13 01:30 | 623 | 613
2017-12-13 02:00 | 609 | 597
2017-12-13 02:30 | 591 | 578
2017-12-13 03:00 | 584 | 570
2017-12-13 03:30 | 584 | 570
2017-12-13 04:00 | 588 | 575
2017-12-13 04:30 | 608 | 597
2017-12-13 05:00 | 600 | 589
2017-12-13 05:30 | 618 | 610
2017-12-13 06:00 | 645 | 640
2017-12-13 06:30 | 698 | 697
2017-12-13 07:00 | 729 | 729
2017-12-13 07:30 | 785 | 785
2017-12-13 08:00 | 808 | 808
2017-12-13 08:30 | 847 | 847
2017-12-13 09:00 | 870 | 870
2017-12-13 09:30 | 869 | 869
2017-12-13 10:00 | 867 | 867
2017-12-13 10:30 | 860 | 860
2017-12-13 11:00 | 858 | 858
2017-12-13 11:30 | 867 | 867
2017-12-13 12:00 | 882 | 882
2017-12-13 12:30 | 891 | 891
2017-12-13 13:00 | 899 | 898
2017-12-13 13:30 | 914 | 914
2017-12-13 14:00 | 936 | 936
2017-12-13 14:30 | 947 | 947
2017-12-13 15:00 | 970 | 970
2017-12-13 15:30 | 1012 | 1012
2017-12-13 16:00 | 1038 | 1038
2017-12-13 16:30 | 1063 | 1063
2017-12-13 17:00 | 1091 | 1091
2017-12-13 17:30 | 1097 | 1097
2017-12-13 18:00 | 1083 | 1081
2017-12-13 18:30 | 1076 | 1072
2017-12-13 19:00 | 1094 | 1091
2017-12-13 19:30 | 1098 | 1097
2017-12-13 20:00 | 1056 | 1055
2017-12-13 20:30 | 1019 | 1018
2017-12-13 21:00 | 975 | 975
2017-12-13 21:30 | 931 | 930
2017-12-13 22:00 | 888 | 888
2017-12-13 22:30 | 867 | 867
2017-12-13 23:00 | 854 | 854
2017-12-13 23:30 | 803 | 802
2017-12-14 | 744 | 740
2017-12-14 00:30 | 690 | 686
2017-12-14 01:00 | 648 | 642
2017-12-14 01:30 | 625 | 618
2017-12-14 02:00 | 612 | 603
2017-12-14 02:30 | 618 | 608
2017-12-14 03:00 | 606 | 595
2017-12-14 03:30 | 602 | 590
2017-12-14 04:00 | 606 | 594
2017-12-14 04:30 | 617 | 607
2017-12-14 05:00 | 629 | 619
2017-12-14 05:30 | 657 | 649
2017-12-14 06:00 | 692 | 685
2017-12-14 06:30 | 743 | 739
2017-12-14 07:00 | 770 | 769
2017-12-14 07:30 | 823 | 823
2017-12-14 08:00 | 846 | 846
2017-12-14 08:30 | 874 | 873
2017-12-14 09:00 | 876 | 874
2017-12-14 09:30 | 887 | 887
2017-12-14 10:00 | 890 | 890
2017-12-14 10:30 | 889 | 889
2017-12-14 11:00 | 893 | 893
2017-12-14 11:30 | 914 | 914
2017-12-14 12:00 | 928 | 928
2017-12-14 12:30 | 936 | 935
2017-12-14 13:00 | 954 | 954
2017-12-14 13:30 | 974 | 974
2017-12-14 14:00 | 997 | 996
2017-12-14 14:30 | 1017 | 1016
2017-12-14 15:00 | 1041 | 1040
2017-12-14 15:30 | 1051 | 1049
2017-12-14 16:00 | 1066 | 1066
2017-12-14 16:30 | 1100 | 1100
2017-12-14 17:00 | 1134 | 1133
2017-12-14 17:30 | 1137 | 1136
2017-12-14 18:00 | 1121 | 1119
2017-12-14 18:30 | 1106 | 1099
2017-12-14 19:00 | 1117 | 1111
2017-12-14 19:30 | 1114 | 1111
2017-12-14 20:00 | 1096 | 1093
2017-12-14 20:30 | 1067 | 1064
2017-12-14 21:00 | 1011 | 1010
2017-12-14 21:30 | 964 | 962
2017-12-14 22:00 | 915 | 911
2017-12-14 22:30 | 880 | 880
2017-12-14 23:00 | 882 | 882
2017-12-14 23:30 | 834 | 832
2017-12-15 | 771 | 765
2017-12-15 00:30 | 708 | 698
2017-12-15 01:00 | 673 | 659
2017-12-15 01:30 | 633 | 628
2017-12-15 02:00 | 623 | 617
2017-12-15 02:30 | 613 | 606
2017-12-15 03:00 | 609 | 602
2017-12-15 03:30 | 602 | 594
2017-12-15 04:00 | 604 | 597
2017-12-15 04:30 | 622 | 616
2017-12-15 05:00 | 635 | 627
2017-12-15 05:30 | 665 | 659
2017-12-15 06:00 | 691 | 689
2017-12-15 06:30 | 759 | 755
2017-12-15 07:00 | 808 | 807
2017-12-15 07:30 | 856 | 855
2017-12-15 08:00 | 912 | 904
2017-12-15 08:30 | 930 | 925
2017-12-15 09:00 | 929 | 927
2017-12-15 09:30 | 943 | 941
2017-12-15 10:00 | 943 | 941
2017-12-15 10:30 | 947 | 947
2017-12-15 11:00 | 942 | 941
2017-12-15 11:30 | 940 | 940
2017-12-15 12:00 | 948 | 946
2017-12-15 12:30 | 953 | 949
2017-12-15 13:00 | 959 | 955
2017-12-15 13:30 | 940 | 936
2017-12-15 14:00 | 956 | 952
2017-12-15 14:30 | 973 | 970
2017-12-15 15:00 | 1006 | 1002
2017-12-15 15:30 | 1021 | 1018
2017-12-15 16:00 | 1057 | 1054
2017-12-15 16:30 | 1076 | 1073
2017-12-15 17:00 | 1100 | 1097
2017-12-15 17:30 | 1112 | 1106
2017-12-15 18:00 | 1088 | 1077
2017-12-15 18:30 | 1037 | 1030
2017-12-15 19:00 | 1055 | 1052
2017-12-15 19:30 | 1051 | 1048
2017-12-15 20:00 | 1038 | 1035
2017-12-15 20:30 | 1007 | 1005
2017-12-15 21:00 | 965 | 964
2017-12-15 21:30 | 926 | 923
2017-12-15 22:00 | 889 | 886
2017-12-15 22:30 | 866 | 865
2017-12-15 23:00 | 851 | 850
2017-12-15 23:30 | 801 | 800
2017-12-16 | 742 | 741
2017-12-16 00:30 | 691 | 690
2017-12-16 01:00 | 671 | 669
2017-12-16 01:30 | 648 | 645
2017-12-16 02:00 | 637 | 633
2017-12-16 02:30 | 631 | 627
2017-12-16 03:00 | 620 | 615
2017-12-16 03:30 | 617 | 611
2017-12-16 04:00 | 615 | 609
2017-12-16 04:30 | 611 | 605
2017-12-16 05:00 | 611 | 602
2017-12-16 05:30 | 617 | 608
2017-12-16 06:00 | 625 | 618
2017-12-16 06:30 | 651 | 648
2017-12-16 07:00 | 676 | 674
2017-12-16 07:30 | 708 | 705
2017-12-16 08:00 | 734 | 733
2017-12-16 08:30 | 765 | 765
2017-12-16 09:00 | 793 | 793
2017-12-16 09:30 | 821 | 819
2017-12-16 10:00 | 824 | 823
2017-12-16 10:30 | 837 | 835
2017-12-16 11:00 | 849 | 847
2017-12-16 11:30 | 854 | 852
2017-12-16 12:00 | 866 | 865
2017-12-16 12:30 | 865 | 864
2017-12-16 13:00 | 862 | 860
2017-12-16 13:30 | 877 | 875
2017-12-16 14:00 | 886 | 884
2017-12-16 14:30 | 899 | 898
2017-12-16 15:00 | 915 | 914
2017-12-16 15:30 | 928 | 927
2017-12-16 16:00 | 959 | 959
2017-12-16 16:30 | 978 | 977
2017-12-16 17:00 | 999 | 999
2017-12-16 17:30 | 992 | 991
2017-12-16 18:00 | 972 | 968
2017-12-16 18:30 | 958 | 952
2017-12-16 19:00 | 963 | 960
2017-12-16 19:30 | 970 | 968
2017-12-16 20:00 | 956 | 953
2017-12-16 20:30 | 929 | 926
2017-12-16 21:00 | 892 | 892
2017-12-16 21:30 | 872 | 872
2017-12-16 22:00 | 852 | 852
2017-12-16 22:30 | 834 | 833
2017-12-16 23:00 | 826 | 825
2017-12-16 23:30 | 776 | 773
2017-12-17 | 734 | 728
2017-12-17 00:30 | 689 | 681
2017-12-17 01:00 | 650 | 640
2017-12-17 01:30 | 628 | 619
2017-12-17 02:00 | 613 | 605
2017-12-17 02:30 | 603 | 595
2017-12-17 03:00 | 593 | 583
2017-12-17 03:30 | 588 | 577
2017-12-17 04:00 | 580 | 568
2017-12-17 04:30 | 575 | 562
2017-12-17 05:00 | 569 | 552
2017-12-17 05:30 | 564 | 547
2017-12-17 06:00 | 561 | 545
2017-12-17 06:30 | 570 | 559
2017-12-17 07:00 | 583 | 577
2017-12-17 07:30 | 606 | 603
2017-12-17 08:00 | 624 | 624
2017-12-17 08:30 | 654 | 654
2017-12-17 09:00 | 677 | 676
2017-12-17 09:30 | 696 | 696
2017-12-17 10:00 | 722 | 722
2017-12-17 10:30 | 742 | 742
2017-12-17 11:00 | 749 | 749
2017-12-17 11:30 | 760 | 760
2017-12-17 12:00 | 769 | 769
2017-12-17 12:30 | 791 | 790
2017-12-17 13:00 | 811 | 811
2017-12-17 13:30 | 821 | 821
2017-12-17 14:00 | 830 | 830
2017-12-17 14:30 | 858 | 858
2017-12-17 15:00 | 882 | 881
2017-12-17 15:30 | 906 | 906
2017-12-17 16:00 | 926 | 926
2017-12-17 16:30 | 946 | 946
2017-12-17 17:00 | 958 | 958
2017-12-17 17:30 | 954 | 953
2017-12-17 18:00 | 945 | 944
2017-12-17 18:30 | 935 | 932
2017-12-17 19:00 | 952 | 950
2017-12-17 19:30 | 953 | 951
2017-12-17 20:00 | 951 | 949
2017-12-17 20:30 | 933 | 930
2017-12-17 21:00 | 904 | 899
2017-12-17 21:30 | 868 | 866
2017-12-17 22:00 | 842 | 840
2017-12-17 22:30 | 826 | 822
2017-12-17 23:00 | 812 | 806
2017-12-17 23:30 | 755 | 751
2017-12-18 | 706 | 705
2017-12-18 00:30 | 669 | 666
2017-12-18 01:00 | 649 | 644
2017-12-18 01:30 | 628 | 622
2017-12-18 02:00 | 614 | 606
2017-12-18 02:30 | 604 | 595
2017-12-18 03:00 | 594 | 585
2017-12-18 03:30 | 595 | 585
2017-12-18 04:00 | 603 | 594
2017-12-18 04:30 | 610 | 602
2017-12-18 05:00 | 617 | 609
2017-12-18 05:30 | 645 | 640
2017-12-18 06:00 | 643 | 639
2017-12-18 06:30 | 693 | 693
2017-12-18 07:00 | 747 | 747
2017-12-18 07:30 | 802 | 801
2017-12-18 08:00 | 839 | 834
2017-12-18 08:30 | 858 | 857
2017-12-18 09:00 | 864 | 862
2017-12-18 09:30 | 879 | 874
2017-12-18 10:00 | 876 | 871
2017-12-18 10:30 | 876 | 871
2017-12-18 11:00 | 881 | 876
2017-12-18 11:30 | 886 | 882
2017-12-18 12:00 | 888 | 884
2017-12-18 12:30 | 885 | 881
2017-12-18 13:00 | 896 | 893
2017-12-18 13:30 | 905 | 903
2017-12-18 14:00 | 921 | 919
2017-12-18 14:30 | 945 | 943
2017-12-18 15:00 | 984 | 981
2017-12-18 15:30 | 1046 | 1045
2017-12-18 16:00 | 1069 | 1068
2017-12-18 16:30 | 1088 | 1087
2017-12-18 17:00 | 1115 | 1114
2017-12-18 17:30 | 1108 | 1106
2017-12-18 18:00 | 1086 | 1081
2017-12-18 18:30 | 1067 | 1060
2017-12-18 19:00 | 1071 | 1070
2017-12-18 19:30 | 1069 | 1067
2017-12-18 20:00 | 1051 | 1049
2017-12-18 20:30 | 1014 | 1013
2017-12-18 21:00 | 973 | 973
2017-12-18 21:30 | 929 | 929
2017-12-18 22:00 | 892 | 892
2017-12-18 22:30 | 868 | 868
2017-12-18 23:00 | 851 | 849
2017-12-18 23:30 | 785 | 782
2017-12-19 | 734 | 732
2017-12-19 00:30 | 688 | 684
2017-12-19 01:00 | 652 | 649
2017-12-19 01:30 | 628 | 624
2017-12-19 02:00 | 620 | 616
2017-12-19 02:30 | 624 | 619
2017-12-19 03:00 | 622 | 616
2017-12-19 03:30 | 612 | 606
2017-12-19 04:00 | 616 | 609
2017-12-19 04:30 | 618 | 613
2017-12-19 05:00 | 620 | 615
2017-12-19 05:30 | 635 | 631
2017-12-19 06:00 | 671 | 669
2017-12-19 06:30 | 722 | 722
2017-12-19 07:00 | 774 | 774
2017-12-19 07:30 | 832 | 832
2017-12-19 08:00 | 855 | 855
2017-12-19 08:30 | 884 | 884
2017-12-19 09:00 | 910 | 908
2017-12-19 09:30 | 913 | 912
2017-12-19 10:00 | 916 | 916
2017-12-19 10:30 | 923 | 922
2017-12-19 11:00 | 934 | 933
2017-12-19 11:30 | 941 | 940
2017-12-19 12:00 | 961 | 961
2017-12-19 12:30 | 982 | 982
2017-12-19 13:00 | 1006 | 1006
2017-12-19 13:30 | 1034 | 1034
2017-12-19 14:00 | 1075 | 1074
2017-12-19 14:30 | 1095 | 1095
2017-12-19 15:00 | 1142 | 1142
2017-12-19 15:30 | 1224 | 1224
2017-12-19 16:00 | 1208 | 1208
2017-12-19 16:30 | 1176 | 1175
2017-12-19 17:00 | 1169 | 1166
2017-12-19 17:30 | 1184 | 1178
2017-12-19 18:00 | 1153 | 1141
2017-12-19 18:30 | 1107 | 1099
2017-12-19 19:00 | 1113 | 1110
2017-12-19 19:30 | 1117 | 1115
2017-12-19 20:00 | 1106 | 1103
2017-12-19 20:30 | 1064 | 1062
2017-12-19 21:00 | 1016 | 1014
2017-12-19 21:30 | 973 | 972
2017-12-19 22:00 | 930 | 926
2017-12-19 22:30 | 901 | 897
2017-12-19 23:00 | 878 | 873
2017-12-19 23:30 | 818 | 815
2017-12-20 | 762 | 761
2017-12-20 00:30 | 712 | 712
2017-12-20 01:00 | 685 | 684
2017-12-20 01:30 | 670 | 669
2017-12-20 02:00 | 659 | 657
2017-12-20 02:30 | 650 | 647
2017-12-20 03:00 | 643 | 639
2017-12-20 03:30 | 640 | 637
2017-12-20 04:00 | 640 | 637
2017-12-20 04:30 | 650 | 647
2017-12-20 05:00 | 654 | 651
2017-12-20 05:30 | 677 | 674
2017-12-20 06:00 | 704 | 702
2017-12-20 06:30 | 757 | 756
2017-12-20 07:00 | 810 | 809
2017-12-20 07:30 | 885 | 884
2017-12-20 08:00 | 932 | 932
2017-12-20 08:30 | 963 | 963
2017-12-20 09:00 | 977 | 977
2017-12-20 09:30 | 982 | 982
2017-12-20 10:00 | 991 | 990
2017-12-20 10:30 | 998 | 997
2017-12-20 11:00 | 1007 | 1006
2017-12-20 11:30 | 1019 | 1017
2017-12-20 12:00 | 1032 | 1031
2017-12-20 12:30 | 1051 | 1050
2017-12-20 13:00 | 1071 | 1070
2017-12-20 13:30 | 1080 | 1080
2017-12-20 14:00 | 1111 | 1109
2017-12-20 14:30 | 1130 | 1129
2017-12-20 15:00 | 1147 | 1146
2017-12-20 15:30 | 1165 | 1164
2017-12-20 16:00 | 1191 | 1190
2017-12-20 16:30 | 1222 | 1221
2017-12-20 17:00 | 1224 | 1222
2017-12-20 17:30 | 1205 | 1202
2017-12-20 18:00 | 1178 | 1171
2017-12-20 18:30 | 1134 | 1127
2017-12-20 19:00 | 1128 | 1126
2017-12-20 19:30 | 1132 | 1130
2017-12-20 20:00 | 1124 | 1121
2017-12-20 20:30 | 1095 | 1092
2017-12-20 21:00 | 1042 | 1041
2017-12-20 21:30 | 1002 | 1000
2017-12-20 22:00 | 959 | 954
2017-12-20 22:30 | 934 | 932
2017-12-20 23:00 | 912 | 911
2017-12-20 23:30 | 855 | 851
2017-12-21 | 798 | 794
2017-12-21 00:30 | 744 | 744
2017-12-21 01:00 | 714 | 714
2017-12-21 01:30 | 691 | 691
2017-12-21 02:00 | 678 | 678
2017-12-21 02:30 | 668 | 667
2017-12-21 03:00 | 658 | 658
2017-12-21 03:30 | 656 | 656
2017-12-21 04:00 | 652 | 651
2017-12-21 04:30 | 662 | 661
2017-12-21 05:00 | 662 | 661
2017-12-21 05:30 | 672 | 670
2017-12-21 06:00 | 696 | 692
2017-12-21 06:30 | 754 | 754
2017-12-21 07:00 | 806 | 806
2017-12-21 07:30 | 861 | 861
2017-12-21 08:00 | 896 | 896
2017-12-21 08:30 | 952 | 951
2017-12-21 09:00 | 978 | 978
2017-12-21 09:30 | 987 | 987
2017-12-21 10:00 | 1010 | 1010
2017-12-21 10:30 | 1029 | 1029
2017-12-21 11:00 | 1046 | 1046
2017-12-21 11:30 | 1049 | 1049
2017-12-21 12:00 | 1063 | 1063
2017-12-21 12:30 | 1076 | 1076
2017-12-21 13:00 | 1095 | 1095
2017-12-21 13:30 | 1109 | 1109
2017-12-21 14:00 | 1146 | 1145
2017-12-21 14:30 | 1183 | 1182
2017-12-21 15:00 | 1199 | 1199
2017-12-21 15:30 | 1171 | 1171
2017-12-21 16:00 | 1176 | 1176
2017-12-21 16:30 | 1171 | 1171
2017-12-21 17:00 | 1163 | 1162
2017-12-21 17:30 | 1158 | 1155
2017-12-21 18:00 | 1178 | 1174
2017-12-21 18:30 | 1158 | 1153
2017-12-21 19:00 | 1159 | 1158
2017-12-21 19:30 | 1169 | 1169
2017-12-21 20:00 | 1163 | 1163
2017-12-21 20:30 | 1140 | 1138
2017-12-21 21:00 | 1099 | 1098
2017-12-21 21:30 | 1048 | 1047
2017-12-21 22:00 | 1005 | 1004
2017-12-21 22:30 | 966 | 965
2017-12-21 23:00 | 942 | 939
2017-12-21 23:30 | 871 | 868
2017-12-22 | 813 | 811
2017-12-22 00:30 | 748 | 747
2017-12-22 01:00 | 715 | 714
2017-12-22 01:30 | 699 | 697
2017-12-22 02:00 | 688 | 685
2017-12-22 02:30 | 674 | 672
2017-12-22 03:00 | 670 | 667
2017-12-22 03:30 | 667 | 663
2017-12-22 04:00 | 660 | 656
2017-12-22 04:30 | 666 | 663
2017-12-22 05:00 | 669 | 665
2017-12-22 05:30 | 688 | 685
2017-12-22 06:00 | 715 | 715
2017-12-22 06:30 | 757 | 756
2017-12-22 07:00 | 804 | 803
2017-12-22 07:30 | 857 | 857
2017-12-22 08:00 | 893 | 892
2017-12-22 08:30 | 914 | 914
2017-12-22 09:00 | 946 | 946
2017-12-22 09:30 | 956 | 956
2017-12-22 10:00 | 960 | 960
2017-12-22 10:30 | 939 | 939
2017-12-22 11:00 | 934 | 933
2017-12-22 11:30 | 929 | 928
2017-12-22 12:00 | 954 | 954
2017-12-22 12:30 | 978 | 978
2017-12-22 13:00 | 949 | 949
2017-12-22 13:30 | 946 | 946
2017-12-22 14:00 | 985 | 985
2017-12-22 14:30 | 1026 | 1026
2017-12-22 15:00 | 1053 | 1052
2017-12-22 15:30 | 1049 | 1049
2017-12-22 16:00 | 1068 | 1068
2017-12-22 16:30 | 1077 | 1077
2017-12-22 17:00 | 1075 | 1075
2017-12-22 17:30 | 1056 | 1056
2017-12-22 18:00 | 1033 | 1030
2017-12-22 18:30 | 1014 | 1007
2017-12-22 19:00 | 1024 | 1018
2017-12-22 19:30 | 1024 | 1018
2017-12-22 20:00 | 1017 | 1011
2017-12-22 20:30 | 995 | 991
2017-12-22 21:00 | 961 | 960
2017-12-22 21:30 | 935 | 934
2017-12-22 22:00 | 911 | 909
2017-12-22 22:30 | 896 | 894
2017-12-22 23:00 | 887 | 884
2017-12-22 23:30 | 827 | 824
2017-12-23 | 778 | 776
2017-12-23 00:30 | 723 | 718
2017-12-23 01:00 | 696 | 693
2017-12-23 01:30 | 676 | 673
2017-12-23 02:00 | 665 | 661
2017-12-23 02:30 | 655 | 649
2017-12-23 03:00 | 644 | 637
2017-12-23 03:30 | 636 | 629
2017-12-23 04:00 | 639 | 632
2017-12-23 04:30 | 634 | 628
2017-12-23 05:00 | 635 | 626
2017-12-23 05:30 | 636 | 626
2017-12-23 06:00 | 639 | 631
2017-12-23 06:30 | 655 | 649
2017-12-23 07:00 | 672 | 669
2017-12-23 07:30 | 693 | 692
2017-12-23 08:00 | 725 | 725
2017-12-23 08:30 | 766 | 766
2017-12-23 09:00 | 789 | 788
2017-12-23 09:30 | 813 | 813
2017-12-23 10:00 | 811 | 811
2017-12-23 10:30 | 823 | 823
2017-12-23 11:00 | 831 | 831
2017-12-23 11:30 | 854 | 854
2017-12-23 12:00 | 874 | 874
2017-12-23 12:30 | 886 | 885
2017-12-23 13:00 | 902 | 899
2017-12-23 13:30 | 919 | 911
2017-12-23 14:00 | 915 | 905
2017-12-23 14:30 | 935 | 926
2017-12-23 15:00 | 962 | 954
2017-12-23 15:30 | 984 | 979
2017-12-23 16:00 | 995 | 991
2017-12-23 16:30 | 996 | 992
2017-12-23 17:00 | 1021 | 1017
2017-12-23 17:30 | 1033 | 1029
2017-12-23 18:00 | 1024 | 1017
2017-12-23 18:30 | 1010 | 1000
2017-12-23 19:00 | 1014 | 1004
2017-12-23 19:30 | 1020 | 1015
2017-12-23 20:00 | 1012 | 1006
2017-12-23 20:30 | 989 | 984
2017-12-23 21:00 | 952 | 948
2017-12-23 21:30 | 907 | 903
2017-12-23 22:00 | 880 | 874
2017-12-23 22:30 | 848 | 843
2017-12-23 23:00 | 830 | 824
2017-12-23 23:30 | 755 | 752
2017-12-24 | 685 | 680
2017-12-24 00:30 | 634 | 629
2017-12-24 01:00 | 601 | 594
2017-12-24 01:30 | 571 | 565
2017-12-24 02:00 | 561 | 552
2017-12-24 02:30 | 551 | 540
2017-12-24 03:00 | 544 | 532
2017-12-24 03:30 | 535 | 521
2017-12-24 04:00 | 528 | 514
2017-12-24 04:30 | 516 | 501
2017-12-24 05:00 | 509 | 490
2017-12-24 05:30 | 500 | 479
2017-12-24 06:00 | 509 | 489
2017-12-24 06:30 | 553 | 541
2017-12-24 07:00 | 605 | 599
2017-12-24 07:30 | 631 | 629
2017-12-24 08:00 | 659 | 659
2017-12-24 08:30 | 692 | 691
2017-12-24 09:00 | 712 | 712
2017-12-24 09:30 | 734 | 734
2017-12-24 10:00 | 753 | 753
2017-12-24 10:30 | 775 | 775
2017-12-24 11:00 | 794 | 794
2017-12-24 11:30 | 807 | 807
2017-12-24 12:00 | 828 | 828
2017-12-24 12:30 | 857 | 856
2017-12-24 13:00 | 888 | 888
2017-12-24 13:30 | 905 | 905
2017-12-24 14:00 | 935 | 935
2017-12-24 14:30 | 973 | 973
2017-12-24 15:00 | 970 | 970
2017-12-24 15:30 | 987 | 987
2017-12-24 16:00 | 1012 | 1012
2017-12-24 16:30 | 1034 | 1033
2017-12-24 17:00 | 1050 | 1050
2017-12-24 17:30 | 1053 | 1052
2017-12-24 18:00 | 1050 | 1049
2017-12-24 18:30 | 1021 | 1016
2017-12-24 19:00 | 1010 | 1007
2017-12-24 19:30 | 1019 | 1018
2017-12-24 20:00 | 1018 | 1017
2017-12-24 20:30 | 1004 | 1002
2017-12-24 21:00 | 953 | 953
2017-12-24 21:30 | 924 | 924
2017-12-24 22:00 | 888 | 888
2017-12-24 22:30 | 869 | 868
2017-12-24 23:00 | 855 | 853
2017-12-24 23:30 | 780 | 777
2017-12-25 | 698 | 697
2017-12-25 00:30 | 634 | 632
2017-12-25 01:00 | 595 | 591
2017-12-25 01:30 | 572 | 565
2017-12-25 02:00 | 556 | 547
2017-12-25 02:30 | 536 | 527
2017-12-25 03:00 | 525 | 515
2017-12-25 03:30 | 525 | 510
2017-12-25 04:00 | 528 | 513
2017-12-25 04:30 | 516 | 501
2017-12-25 05:00 | 512 | 496
2017-12-25 05:30 | 512 | 494
2017-12-25 06:00 | 522 | 505
2017-12-25 06:30 | 560 | 552
2017-12-25 07:00 | 621 | 619
2017-12-25 07:30 | 714 | 714
2017-12-25 08:00 | 742 | 742
2017-12-25 08:30 | 768 | 768
2017-12-25 09:00 | 777 | 777
2017-12-25 09:30 | 791 | 791
2017-12-25 10:00 | 811 | 808
2017-12-25 10:30 | 825 | 823
2017-12-25 11:00 | 841 | 841
2017-12-25 11:30 | 854 | 854
2017-12-25 12:00 | 870 | 870
2017-12-25 12:30 | 884 | 884
2017-12-25 13:00 | 885 | 885
2017-12-25 13:30 | 900 | 900
2017-12-25 14:00 | 917 | 917
2017-12-25 14:30 | 937 | 937
2017-12-25 15:00 | 909 | 909
2017-12-25 15:30 | 924 | 924
2017-12-25 16:00 | 984 | 984
2017-12-25 16:30 | 1008 | 1006
2017-12-25 17:00 | 1001 | 998
2017-12-25 17:30 | 988 | 982
2017-12-25 18:00 | 971 | 967
2017-12-25 18:30 | 959 | 955
2017-12-25 19:00 | 942 | 940
2017-12-25 19:30 | 896 | 894
2017-12-25 20:00 | 857 | 857
2017-12-25 20:30 | 832 | 832
2017-12-25 21:00 | 793 | 792
2017-12-25 21:30 | 768 | 767
2017-12-25 22:00 | 736 | 735
2017-12-25 22:30 | 736 | 734
2017-12-25 23:00 | 722 | 719
2017-12-25 23:30 | 658 | 652
2017-12-26 | 614 | 602
2017-12-26 00:30 | 584 | 567
2017-12-26 01:00 | 607 | 594
2017-12-26 01:30 | 588 | 578
2017-12-26 02:00 | 586 | 574
2017-12-26 02:30 | 579 | 566
2017-12-26 03:00 | 571 | 557
2017-12-26 03:30 | 571 | 555
2017-12-26 04:00 | 567 | 551
2017-12-26 04:30 | 573 | 557
2017-12-26 05:00 | 573 | 555
2017-12-26 05:30 | 571 | 552
2017-12-26 06:00 | 573 | 554
2017-12-26 06:30 | 594 | 582
2017-12-26 07:00 | 604 | 595
2017-12-26 07:30 | 634 | 631
2017-12-26 08:00 | 661 | 660
2017-12-26 08:30 | 688 | 688
2017-12-26 09:00 | 705 | 704
2017-12-26 09:30 | 709 | 708
2017-12-26 10:00 | 707 | 706
2017-12-26 10:30 | 706 | 706
2017-12-26 11:00 | 726 | 726
2017-12-26 11:30 | 758 | 758
2017-12-26 12:00 | 765 | 765
2017-12-26 12:30 | 773 | 773
2017-12-26 13:00 | 781 | 780
2017-12-26 13:30 | 770 | 770
2017-12-26 14:00 | 788 | 788
2017-12-26 14:30 | 801 | 801
2017-12-26 15:00 | 830 | 830
2017-12-26 15:30 | 904 | 904
2017-12-26 16:00 | 867 | 867
2017-12-26 16:30 | 838 | 837
2017-12-26 17:00 | 872 | 871
2017-12-26 17:30 | 883 | 882
2017-12-26 18:00 | 874 | 872
2017-12-26 18:30 | 866 | 862
2017-12-26 19:00 | 871 | 868
2017-12-26 19:30 | 857 | 853
2017-12-26 20:00 | 842 | 838
2017-12-26 20:30 | 815 | 812
2017-12-26 21:00 | 774 | 773
2017-12-26 21:30 | 750 | 749
2017-12-26 22:00 | 722 | 719
2017-12-26 22:30 | 717 | 713
2017-12-26 23:00 | 710 | 706
2017-12-26 23:30 | 661 | 653
2017-12-27 | 605 | 591
2017-12-27 00:30 | 566 | 547
2017-12-27 01:00 | 571 | 548
2017-12-27 01:30 | 598 | 574
2017-12-27 02:00 | 585 | 562
2017-12-27 02:30 | 578 | 560
2017-12-27 03:00 | 576 | 559
2017-12-27 03:30 | 573 | 553
2017-12-27 04:00 | 570 | 551
2017-12-27 04:30 | 570 | 551
2017-12-27 05:00 | 577 | 559
2017-12-27 05:30 | 586 | 568
2017-12-27 06:00 | 597 | 583
2017-12-27 06:30 | 633 | 625
2017-12-27 07:00 | 658 | 655
2017-12-27 07:30 | 702 | 701
2017-12-27 08:00 | 730 | 728
2017-12-27 08:30 | 764 | 763
2017-12-27 09:00 | 792 | 790
2017-12-27 09:30 | 825 | 824
2017-12-27 10:00 | 839 | 839
2017-12-27 10:30 | 836 | 835
2017-12-27 11:00 | 822 | 822
2017-12-27 11:30 | 805 | 804
2017-12-27 12:00 | 807 | 807
2017-12-27 12:30 | 832 | 832
2017-12-27 13:00 | 865 | 865
2017-12-27 13:30 | 896 | 896
2017-12-27 14:00 | 886 | 885
2017-12-27 14:30 | 878 | 878
2017-12-27 15:00 | 897 | 897
2017-12-27 15:30 | 929 | 929
2017-12-27 16:00 | 934 | 934
2017-12-27 16:30 | 972 | 972
2017-12-27 17:00 | 1000 | 1000
2017-12-27 17:30 | 995 | 995
2017-12-27 18:00 | 981 | 978
2017-12-27 18:30 | 959 | 955
2017-12-27 19:00 | 941 | 940
2017-12-27 19:30 | 934 | 934
2017-12-27 20:00 | 934 | 933
2017-12-27 20:30 | 913 | 913
2017-12-27 21:00 | 875 | 875
2017-12-27 21:30 | 849 | 847
2017-12-27 22:00 | 821 | 820
2017-12-27 22:30 | 800 | 799
2017-12-27 23:00 | 784 | 783
2017-12-27 23:30 | 737 | 736
2017-12-28 | 692 | 689
2017-12-28 00:30 | 651 | 645
2017-12-28 01:00 | 627 | 619
2017-12-28 01:30 | 618 | 606
2017-12-28 02:00 | 608 | 592
2017-12-28 02:30 | 602 | 587
2017-12-28 03:00 | 597 | 581
2017-12-28 03:30 | 595 | 579
2017-12-28 04:00 | 591 | 576
2017-12-28 04:30 | 598 | 584
2017-12-28 05:00 | 596 | 580
2017-12-28 05:30 | 610 | 594
2017-12-28 06:00 | 618 | 605
2017-12-28 06:30 | 645 | 639
2017-12-28 07:00 | 667 | 665
2017-12-28 07:30 | 704 | 704
2017-12-28 08:00 | 742 | 742
2017-12-28 08:30 | 876 | 875
2017-12-28 09:00 | 910 | 910
2017-12-28 09:30 | 950 | 950
2017-12-28 10:00 | 956 | 956
2017-12-28 10:30 | 946 | 946
2017-12-28 11:00 | 950 | 950
2017-12-28 11:30 | 951 | 950
2017-12-28 12:00 | 963 | 962
2017-12-28 12:30 | 898 | 897
2017-12-28 13:00 | 848 | 848
2017-12-28 13:30 | 860 | 860
2017-12-28 14:00 | 885 | 885
2017-12-28 14:30 | 926 | 926
2017-12-28 15:00 | 963 | 963
2017-12-28 15:30 | 981 | 980
2017-12-28 16:00 | 1012 | 1010
2017-12-28 16:30 | 1011 | 1011
2017-12-28 17:00 | 1020 | 1019
2017-12-28 17:30 | 1026 | 1025
2017-12-28 18:00 | 1037 | 1035
2017-12-28 18:30 | 1022 | 1018
2017-12-28 19:00 | 1030 | 1028
2017-12-28 19:30 | 1041 | 1040
2017-12-28 20:00 | 1040 | 1038
2017-12-28 20:30 | 1013 | 1011
2017-12-28 21:00 | 961 | 959
2017-12-28 21:30 | 918 | 916
2017-12-28 22:00 | 878 | 874
2017-12-28 22:30 | 843 | 840
2017-12-28 23:00 | 824 | 820
2017-12-28 23:30 | 766 | 765
2017-12-29 | 717 | 714
2017-12-29 00:30 | 676 | 672
2017-12-29 01:00 | 652 | 646
2017-12-29 01:30 | 638 | 630
2017-12-29 02:00 | 628 | 619
2017-12-29 02:30 | 620 | 609
2017-12-29 03:00 | 615 | 603
2017-12-29 03:30 | 611 | 599
2017-12-29 04:00 | 612 | 600
2017-12-29 04:30 | 613 | 603
2017-12-29 05:00 | 620 | 609
2017-12-29 05:30 | 626 | 615
2017-12-29 06:00 | 643 | 632
2017-12-29 06:30 | 665 | 661
2017-12-29 07:00 | 690 | 689
2017-12-29 07:30 | 749 | 749
2017-12-29 08:00 | 785 | 785
2017-12-29 08:30 | 905 | 905
2017-12-29 09:00 | 936 | 936
2017-12-29 09:30 | 959 | 957
2017-12-29 10:00 | 958 | 957
2017-12-29 10:30 | 959 | 959
2017-12-29 11:00 | 970 | 970
2017-12-29 11:30 | 973 | 973
2017-12-29 12:00 | 954 | 953
2017-12-29 12:30 | 889 | 889
2017-12-29 13:00 | 896 | 896
2017-12-29 13:30 | 930 | 930
2017-12-29 14:00 | 958 | 958
2017-12-29 14:30 | 980 | 980
2017-12-29 15:00 | 993 | 993
2017-12-29 15:30 | 1002 | 1002
2017-12-29 16:00 | 1026 | 1025
2017-12-29 16:30 | 1060 | 1059
2017-12-29 17:00 | 1071 | 1071
2017-12-29 17:30 | 1064 | 1063
2017-12-29 18:00 | 1046 | 1044
2017-12-29 18:30 | 1021 | 1015
2017-12-29 19:00 | 1023 | 1019
2017-12-29 19:30 | 1031 | 1028
2017-12-29 20:00 | 1026 | 1023
2017-12-29 20:30 | 999 | 998
2017-12-29 21:00 | 964 | 964
2017-12-29 21:30 | 928 | 928
2017-12-29 22:00 | 892 | 890
2017-12-29 22:30 | 872 | 869
2017-12-29 23:00 | 855 | 854
2017-12-29 23:30 | 794 | 792
2017-12-30 | 738 | 735
2017-12-30 00:30 | 689 | 686
2017-12-30 01:00 | 670 | 666
2017-12-30 01:30 | 647 | 641
2017-12-30 02:00 | 638 | 629
2017-12-30 02:30 | 632 | 621
2017-12-30 03:00 | 626 | 615
2017-12-30 03:30 | 614 | 603
2017-12-30 04:00 | 614 | 602
2017-12-30 04:30 | 613 | 601
2017-12-30 05:00 | 613 | 596
2017-12-30 05:30 | 616 | 597
2017-12-30 06:00 | 626 | 610
2017-12-30 06:30 | 639 | 628
2017-12-30 07:00 | 647 | 641
2017-12-30 07:30 | 666 | 664
2017-12-30 08:00 | 698 | 698
2017-12-30 08:30 | 741 | 741
2017-12-30 09:00 | 782 | 782
2017-12-30 09:30 | 783 | 783
2017-12-30 10:00 | 777 | 777
2017-12-30 10:30 | 829 | 829
2017-12-30 11:00 | 858 | 858
2017-12-30 11:30 | 857 | 857
2017-12-30 12:00 | 857 | 857
2017-12-30 12:30 | 882 | 882
2017-12-30 13:00 | 937 | 937
2017-12-30 13:30 | 947 | 947
2017-12-30 14:00 | 947 | 947
2017-12-30 14:30 | 922 | 921
2017-12-30 15:00 | 940 | 939
2017-12-30 15:30 | 954 | 953
2017-12-30 16:00 | 1004 | 1004
2017-12-30 16:30 | 1040 | 1039
2017-12-30 17:00 | 1068 | 1068
2017-12-30 17:30 | 1075 | 1075
2017-12-30 18:00 | 1071 | 1071
2017-12-30 18:30 | 1068 | 1068
2017-12-30 19:00 | 1080 | 1080
2017-12-30 19:30 | 1085 | 1085
2017-12-30 20:00 | 1086 | 1086
2017-12-30 20:30 | 1065 | 1065
2017-12-30 21:00 | 1033 | 1032
2017-12-30 21:30 | 990 | 989
2017-12-30 22:00 | 959 | 956
2017-12-30 22:30 | 940 | 935
2017-12-30 23:00 | 915 | 911
2017-12-30 23:30 | 858 | 855
2017-12-31 | 798 | 795
2017-12-31 00:30 | 746 | 742
2017-12-31 01:00 | 724 | 718
2017-12-31 01:30 | 695 | 693
2017-12-31 02:00 | 683 | 680
2017-12-31 02:30 | 674 | 669
2017-12-31 03:00 | 663 | 658
2017-12-31 03:30 | 664 | 658
2017-12-31 04:00 | 657 | 650
2017-12-31 04:30 | 647 | 639
2017-12-31 05:00 | 641 | 632
2017-12-31 05:30 | 636 | 624
2017-12-31 06:00 | 638 | 626
2017-12-31 06:30 | 646 | 637
2017-12-31 07:00 | 651 | 645
2017-12-31 07:30 | 672 | 669
2017-12-31 08:00 | 700 | 699
2017-12-31 08:30 | 741 | 740
2017-12-31 09:00 | 777 | 777
2017-12-31 09:30 | 814 | 814
2017-12-31 10:00 | 848 | 848
2017-12-31 10:30 | 877 | 877
2017-12-31 11:00 | 919 | 919
2017-12-31 11:30 | 932 | 932
2017-12-31 12:00 | 948 | 948
2017-12-31 12:30 | 977 | 977
2017-12-31 13:00 | 1006 | 1005
2017-12-31 13:30 | 1028 | 1028
2017-12-31 14:00 | 1062 | 1061
2017-12-31 14:30 | 1077 | 1076
2017-12-31 15:00 | 1104 | 1104
2017-12-31 15:30 | 1097 | 1096
2017-12-31 16:00 | 1092 | 1090
2017-12-31 16:30 | 1053 | 1048
2017-12-31 17:00 | 1018 | 1013
2017-12-31 17:30 | 997 | 992
2017-12-31 18:00 | 973 | 970
2017-12-31 18:30 | 966 | 962
2017-12-31 19:00 | 958 | 953
2017-12-31 19:30 | 958 | 956
2017-12-31 20:00 | 948 | 947
2017-12-31 20:30 | 928 | 928
2017-12-31 21:00 | 901 | 901
2017-12-31 21:30 | 885 | 885
2017-12-31 22:00 | 880 | 880
2017-12-31 22:30 | 877 | 877
2017-12-31 23:00 | 873 | 872
2017-12-31 23:30 | 832 | 830
2018-01-01 | 779 | 778
2018-01-01 00:30 | 736 | 734
2018-01-01 01:00 | 723 | 721
2018-01-01 01:30 | 702 | 701
2018-01-01 02:00 | 681 | 679
2018-01-01 02:30 | 663 | 661
2018-01-01 03:00 | 651 | 648
2018-01-01 03:30 | 643 | 638
2018-01-01 04:00 | 641 | 637
2018-01-01 04:30 | 639 | 635
2018-01-01 05:00 | 637 | 632
2018-01-01 05:30 | 632 | 625
2018-01-01 06:00 | 642 | 636
2018-01-01 06:30 | 658 | 655
2018-01-01 07:00 | 668 | 667
2018-01-01 07:30 | 711 | 710
2018-01-01 08:00 | 751 | 750
2018-01-01 08:30 | 803 | 803
2018-01-01 09:00 | 836 | 836
2018-01-01 09:30 | 860 | 859
2018-01-01 10:00 | 904 | 904
2018-01-01 10:30 | 933 | 933
2018-01-01 11:00 | 935 | 935
2018-01-01 11:30 | 960 | 960
2018-01-01 12:00 | 974 | 974
2018-01-01 12:30 | 975 | 974
2018-01-01 13:00 | 1001 | 1001
2018-01-01 13:30 | 1037 | 1036
2018-01-01 14:00 | 1039 | 1038
2018-01-01 14:30 | 1044 | 1043
2018-01-01 15:00 | 1076 | 1076
2018-01-01 15:30 | 1075 | 1075
2018-01-01 16:00 | 1101 | 1101
2018-01-01 16:30 | 1105 | 1105
2018-01-01 17:00 | 1114 | 1111
2018-01-01 17:30 | 1120 | 1117
2018-01-01 18:00 | 1082 | 1076
2018-01-01 18:30 | 1050 | 1043
2018-01-01 19:00 | 1047 | 1044
2018-01-01 19:30 | 1044 | 1041
2018-01-01 20:00 | 1035 | 1032
2018-01-01 20:30 | 996 | 995
2018-01-01 21:00 | 955 | 953
2018-01-01 21:30 | 918 | 912
2018-01-01 22:00 | 881 | 871
2018-01-01 22:30 | 858 | 854
2018-01-01 23:00 | 845 | 838
2018-01-01 23:30 | 797 | 784
2018-01-02 | 735 | 732
2018-01-02 00:30 | 687 | 683
2018-01-02 01:00 | 660 | 656
2018-01-02 01:30 | 643 | 637
2018-01-02 02:00 | 632 | 625
2018-01-02 02:30 | 624 | 616
2018-01-02 03:00 | 622 | 613
2018-01-02 03:30 | 615 | 606
2018-01-02 04:00 | 616 | 608
2018-01-02 04:30 | 625 | 617
2018-01-02 05:00 | 626 | 618
2018-01-02 05:30 | 639 | 631
2018-01-02 06:00 | 657 | 653
2018-01-02 06:30 | 717 | 717
2018-01-02 07:00 | 752 | 752
2018-01-02 07:30 | 831 | 830
2018-01-02 08:00 | 874 | 873
2018-01-02 08:30 | 913 | 911
2018-01-02 09:00 | 933 | 932
2018-01-02 09:30 | 960 | 958
2018-01-02 10:00 | 1001 | 1001
2018-01-02 10:30 | 1018 | 1018
2018-01-02 11:00 | 1029 | 1029
2018-01-02 11:30 | 1033 | 1033
2018-01-02 12:00 | 1030 | 1030
2018-01-02 12:30 | 1023 | 1023
2018-01-02 13:00 | 1027 | 1027
2018-01-02 13:30 | 1080 | 1080
2018-01-02 14:00 | 1120 | 1120
2018-01-02 14:30 | 1164 | 1164
2018-01-02 15:00 | 1186 | 1186
2018-01-02 15:30 | 1178 | 1178
2018-01-02 16:00 | 1159 | 1158
2018-01-02 16:30 | 1119 | 1118
2018-01-02 17:00 | 1099 | 1098
2018-01-02 17:30 | 1079 | 1076
2018-01-02 18:00 | 1072 | 1067
2018-01-02 18:30 | 1053 | 1050
2018-01-02 19:00 | 1066 | 1065
2018-01-02 19:30 | 1038 | 1036
2018-01-02 20:00 | 1007 | 1006
2018-01-02 20:30 | 980 | 980
2018-01-02 21:00 | 936 | 936
2018-01-02 21:30 | 902 | 902
2018-01-02 22:00 | 869 | 869
2018-01-02 22:30 | 840 | 839
2018-01-02 23:00 | 827 | 825
2018-01-02 23:30 | 768 | 765
2018-01-03 | 718 | 715
2018-01-03 00:30 | 668 | 666
2018-01-03 01:00 | 651 | 647
2018-01-03 01:30 | 638 | 633
2018-01-03 02:00 | 625 | 619
2018-01-03 02:30 | 616 | 609
2018-01-03 03:00 | 613 | 606
2018-01-03 03:30 | 608 | 601
2018-01-03 04:00 | 610 | 602
2018-01-03 04:30 | 613 | 605
2018-01-03 05:00 | 618 | 610
2018-01-03 05:30 | 634 | 627
2018-01-03 06:00 | 652 | 648
2018-01-03 06:30 | 701 | 697
2018-01-03 07:00 | 740 | 735
2018-01-03 07:30 | 801 | 798
2018-01-03 08:00 | 839 | 837
2018-01-03 08:30 | 870 | 869
2018-01-03 09:00 | 898 | 893
2018-01-03 09:30 | 913 | 909
2018-01-03 10:00 | 933 | 927
2018-01-03 10:30 | 933 | 927
2018-01-03 11:00 | 937 | 932
2018-01-03 11:30 | 941 | 937
2018-01-03 12:00 | 950 | 947
2018-01-03 12:30 | 963 | 961
2018-01-03 13:00 | 973 | 971
2018-01-03 13:30 | 1000 | 1000
2018-01-03 14:00 | 1113 | 1112
2018-01-03 14:30 | 1121 | 1119
2018-01-03 15:00 | 1099 | 1095
2018-01-03 15:30 | 1059 | 1056
2018-01-03 16:00 | 1038 | 1034
2018-01-03 16:30 | 1027 | 1022
2018-01-03 17:00 | 1042 | 1036
2018-01-03 17:30 | 1051 | 1044
2018-01-03 18:00 | 1052 | 1044
2018-01-03 18:30 | 1028 | 1022
2018-01-03 19:00 | 1021 | 1020
2018-01-03 19:30 | 1026 | 1025
2018-01-03 20:00 | 1026 | 1025
2018-01-03 20:30 | 1001 | 999
2018-01-03 21:00 | 955 | 954
2018-01-03 21:30 | 905 | 905
2018-01-03 22:00 | 875 | 874
2018-01-03 22:30 | 843 | 840
2018-01-03 23:00 | 822 | 815
2018-01-03 23:30 | 766 | 761
2018-01-04 | 708 | 705
2018-01-04 00:30 | 663 | 660
2018-01-04 01:00 | 634 | 630
2018-01-04 01:30 | 621 | 615
2018-01-04 02:00 | 610 | 603
2018-01-04 02:30 | 603 | 595
2018-01-04 03:00 | 596 | 586
2018-01-04 03:30 | 591 | 581
2018-01-04 04:00 | 592 | 582
2018-01-04 04:30 | 597 | 587
2018-01-04 05:00 | 603 | 594
2018-01-04 05:30 | 617 | 608
2018-01-04 06:00 | 637 | 631
2018-01-04 06:30 | 673 | 672
2018-01-04 07:00 | 704 | 703
2018-01-04 07:30 | 766 | 766
2018-01-04 08:00 | 802 | 802
2018-01-04 08:30 | 831 | 830
2018-01-04 09:00 | 851 | 851
2018-01-04 09:30 | 863 | 863
2018-01-04 10:00 | 904 | 904
2018-01-04 10:30 | 923 | 923
2018-01-04 11:00 | 929 | 929
2018-01-04 11:30 | 937 | 937
2018-01-04 12:00 | 948 | 948
2018-01-04 12:30 | 960 | 960
2018-01-04 13:00 | 963 | 963
2018-01-04 13:30 | 977 | 977
2018-01-04 14:00 | 983 | 983
2018-01-04 14:30 | 983 | 983
2018-01-04 15:00 | 982 | 982
2018-01-04 15:30 | 971 | 971
2018-01-04 16:00 | 976 | 976
2018-01-04 16:30 | 998 | 998
2018-01-04 17:00 | 1030 | 1030
2018-01-04 17:30 | 1034 | 1034
2018-01-04 18:00 | 1046 | 1046
2018-01-04 18:30 | 1023 | 1022
2018-01-04 19:00 | 997 | 997
2018-01-04 19:30 | 1011 | 1011
2018-01-04 20:00 | 1025 | 1024
2018-01-04 20:30 | 981 | 980
2018-01-04 21:00 | 944 | 943
2018-01-04 21:30 | 907 | 904
2018-01-04 22:00 | 870 | 869
2018-01-04 22:30 | 830 | 830
2018-01-04 23:00 | 792 | 791
2018-01-04 23:30 | 753 | 751
2018-01-05 | 704 | 702
2018-01-05 00:30 | 663 | 660
2018-01-05 01:00 | 642 | 637
2018-01-05 01:30 | 626 | 619
2018-01-05 02:00 | 618 | 610
2018-01-05 02:30 | 613 | 604
2018-01-05 03:00 | 605 | 595
2018-01-05 03:30 | 603 | 592
2018-01-05 04:00 | 607 | 597
2018-01-05 04:30 | 609 | 600
2018-01-05 05:00 | 610 | 600
2018-01-05 05:30 | 625 | 615
2018-01-05 06:00 | 643 | 636
2018-01-05 06:30 | 680 | 678
2018-01-05 07:00 | 710 | 709
2018-01-05 07:30 | 772 | 772
2018-01-05 08:00 | 807 | 807
2018-01-05 08:30 | 839 | 839
2018-01-05 09:00 | 871 | 871
2018-01-05 09:30 | 901 | 901
2018-01-05 10:00 | 944 | 944
2018-01-05 10:30 | 929 | 928
2018-01-05 11:00 | 893 | 892
2018-01-05 11:30 | 898 | 898
2018-01-05 12:00 | 896 | 896
2018-01-05 12:30 | 898 | 898
2018-01-05 13:00 | 915 | 915
2018-01-05 13:30 | 934 | 933
2018-01-05 14:00 | 947 | 947
2018-01-05 14:30 | 959 | 959
2018-01-05 15:00 | 975 | 975
2018-01-05 15:30 | 989 | 989
2018-01-05 16:00 | 1013 | 1013
2018-01-05 16:30 | 1041 | 1041
2018-01-05 17:00 | 1051 | 1051
2018-01-05 17:30 | 1027 | 1025
2018-01-05 18:00 | 999 | 995
2018-01-05 18:30 | 977 | 975
2018-01-05 19:00 | 984 | 983
2018-01-05 19:30 | 986 | 985
2018-01-05 20:00 | 979 | 978
2018-01-05 20:30 | 955 | 955
2018-01-05 21:00 | 930 | 928
2018-01-05 21:30 | 906 | 903
2018-01-05 22:00 | 872 | 870
2018-01-05 22:30 | 841 | 838
2018-01-05 23:00 | 826 | 823
2018-01-05 23:30 | 771 | 768
2018-01-06 | 719 | 716
2018-01-06 00:30 | 673 | 669
2018-01-06 01:00 | 652 | 646
2018-01-06 01:30 | 640 | 633
2018-01-06 02:00 | 623 | 614
2018-01-06 02:30 | 614 | 605
2018-01-06 03:00 | 607 | 595
2018-01-06 03:30 | 602 | 590
2018-01-06 04:00 | 600 | 587
2018-01-06 04:30 | 597 | 583
2018-01-06 05:00 | 597 | 581
2018-01-06 05:30 | 595 | 577
2018-01-06 06:00 | 601 | 587
2018-01-06 06:30 | 611 | 601
2018-01-06 07:00 | 624 | 618
2018-01-06 07:30 | 652 | 648
2018-01-06 08:00 | 673 | 670
2018-01-06 08:30 | 698 | 697
2018-01-06 09:00 | 716 | 716
2018-01-06 09:30 | 736 | 736
2018-01-06 10:00 | 744 | 744
2018-01-06 10:30 | 749 | 749
2018-01-06 11:00 | 748 | 748
2018-01-06 11:30 | 760 | 760
2018-01-06 12:00 | 769 | 769
2018-01-06 12:30 | 772 | 772
2018-01-06 13:00 | 784 | 784
2018-01-06 13:30 | 805 | 805
2018-01-06 14:00 | 830 | 828
2018-01-06 14:30 | 855 | 850
2018-01-06 15:00 | 872 | 869
2018-01-06 15:30 | 891 | 888
2018-01-06 16:00 | 921 | 918
2018-01-06 16:30 | 966 | 963
2018-01-06 17:00 | 998 | 995
2018-01-06 17:30 | 1000 | 996
2018-01-06 18:00 | 993 | 988
2018-01-06 18:30 | 984 | 976
2018-01-06 19:00 | 985 | 975
2018-01-06 19:30 | 984 | 982
2018-01-06 20:00 | 956 | 956
2018-01-06 20:30 | 928 | 928
2018-01-06 21:00 | 892 | 890
2018-01-06 21:30 | 861 | 861
2018-01-06 22:00 | 831 | 831
2018-01-06 22:30 | 814 | 814
2018-01-06 23:00 | 806 | 806
2018-01-06 23:30 | 751 | 751
2018-01-07 | 702 | 700
2018-01-07 00:30 | 658 | 654
2018-01-07 01:00 | 637 | 631
2018-01-07 01:30 | 624 | 616
2018-01-07 02:00 | 604 | 595
2018-01-07 02:30 | 600 | 588
2018-01-07 03:00 | 591 | 579
2018-01-07 03:30 | 589 | 576
2018-01-07 04:00 | 587 | 572
2018-01-07 04:30 | 581 | 565
2018-01-07 05:00 | 582 | 563
2018-01-07 05:30 | 583 | 561
2018-01-07 06:00 | 581 | 562
2018-01-07 06:30 | 590 | 575
2018-01-07 07:00 | 597 | 588
2018-01-07 07:30 | 615 | 610
2018-01-07 08:00 | 625 | 624
2018-01-07 08:30 | 662 | 662
2018-01-07 09:00 | 686 | 686
2018-01-07 09:30 | 701 | 701
2018-01-07 10:00 | 714 | 713
2018-01-07 10:30 | 734 | 734
2018-01-07 11:00 | 742 | 742
2018-01-07 11:30 | 753 | 752
2018-01-07 12:00 | 763 | 763
2018-01-07 12:30 | 780 | 780
2018-01-07 13:00 | 779 | 779
2018-01-07 13:30 | 792 | 791
2018-01-07 14:00 | 802 | 801
2018-01-07 14:30 | 853 | 853
2018-01-07 15:00 | 904 | 904
2018-01-07 15:30 | 935 | 934
2018-01-07 16:00 | 971 | 969
2018-01-07 16:30 | 1016 | 1015
2018-01-07 17:00 | 1052 | 1051
2018-01-07 17:30 | 1063 | 1060
2018-01-07 18:00 | 1071 | 1068
2018-01-07 18:30 | 1056 | 1054
2018-01-07 19:00 | 1050 | 1049
2018-01-07 19:30 | 1058 | 1056
2018-01-07 20:00 | 1039 | 1037
2018-01-07 20:30 | 1005 | 1001
2018-01-07 21:00 | 958 | 953
2018-01-07 21:30 | 918 | 912
2018-01-07 22:00 | 870 | 866
2018-01-07 22:30 | 841 | 839
2018-01-07 23:00 | 825 | 822
2018-01-07 23:30 | 762 | 761
2018-01-08 | 717 | 713
2018-01-08 00:30 | 675 | 669
2018-01-08 01:00 | 650 | 641
2018-01-08 01:30 | 638 | 630
2018-01-08 02:00 | 626 | 619
2018-01-08 02:30 | 615 | 607
2018-01-08 03:00 | 610 | 601
2018-01-08 03:30 | 610 | 600
2018-01-08 04:00 | 611 | 601
2018-01-08 04:30 | 615 | 606
2018-01-08 05:00 | 624 | 615
2018-01-08 05:30 | 642 | 634
2018-01-08 06:00 | 666 | 662
2018-01-08 06:30 | 724 | 724
2018-01-08 07:00 | 772 | 771
2018-01-08 07:30 | 847 | 847
2018-01-08 08:00 | 885 | 884
2018-01-08 08:30 | 921 | 920
2018-01-08 09:00 | 937 | 937
2018-01-08 09:30 | 948 | 947
2018-01-08 10:00 | 958 | 957
2018-01-08 10:30 | 965 | 964
2018-01-08 11:00 | 980 | 979
2018-01-08 11:30 | 991 | 990
2018-01-08 12:00 | 1011 | 1011
2018-01-08 12:30 | 1028 | 1027
2018-01-08 13:00 | 1063 | 1062
2018-01-08 13:30 | 1088 | 1088
2018-01-08 14:00 | 1116 | 1115
2018-01-08 14:30 | 1137 | 1136
2018-01-08 15:00 | 1169 | 1168
2018-01-08 15:30 | 1189 | 1188
2018-01-08 16:00 | 1213 | 1213
2018-01-08 16:30 | 1237 | 1237
2018-01-08 17:00 | 1256 | 1256
2018-01-08 17:30 | 1252 | 1252
2018-01-08 18:00 | 1227 | 1227
2018-01-08 18:30 | 1193 | 1192
2018-01-08 19:00 | 1181 | 1180
2018-01-08 19:30 | 1172 | 1171
2018-01-08 20:00 | 1156 | 1156
2018-01-08 20:30 | 1116 | 1114
2018-01-08 21:00 | 1054 | 1052
2018-01-08 21:30 | 1004 | 1002
2018-01-08 22:00 | 954 | 953
2018-01-08 22:30 | 907 | 907
2018-01-08 23:00 | 876 | 875
2018-01-08 23:30 | 815 | 814
2018-01-09 | 765 | 762
2018-01-09 00:30 | 723 | 717
2018-01-09 01:00 | 697 | 688
2018-01-09 01:30 | 681 | 671
2018-01-09 02:00 | 675 | 663
2018-01-09 02:30 | 666 | 651
2018-01-09 03:00 | 656 | 640
2018-01-09 03:30 | 654 | 637
2018-01-09 04:00 | 651 | 634
2018-01-09 04:30 | 660 | 644
2018-01-09 05:00 | 667 | 651
2018-01-09 05:30 | 683 | 669
2018-01-09 06:00 | 693 | 683
2018-01-09 06:30 | 737 | 735
2018-01-09 07:00 | 784 | 783
2018-01-09 07:30 | 850 | 850
2018-01-09 08:00 | 887 | 887
2018-01-09 08:30 | 918 | 918
2018-01-09 09:00 | 933 | 933
2018-01-09 09:30 | 946 | 945
2018-01-09 10:00 | 944 | 944
2018-01-09 10:30 | 950 | 949
2018-01-09 11:00 | 960 | 959
2018-01-09 11:30 | 974 | 973
2018-01-09 12:00 | 1001 | 1001
2018-01-09 12:30 | 1027 | 1027
2018-01-09 13:00 | 1059 | 1059
2018-01-09 13:30 | 1088 | 1088
2018-01-09 14:00 | 1112 | 1111
2018-01-09 14:30 | 1137 | 1136
2018-01-09 15:00 | 1146 | 1145
2018-01-09 15:30 | 1163 | 1163
2018-01-09 16:00 | 1196 | 1195
2018-01-09 16:30 | 1225 | 1225
2018-01-09 17:00 | 1244 | 1244
2018-01-09 17:30 | 1241 | 1239
2018-01-09 18:00 | 1214 | 1208
2018-01-09 18:30 | 1172 | 1164
2018-01-09 19:00 | 1160 | 1154
2018-01-09 19:30 | 1140 | 1135
2018-01-09 20:00 | 1121 | 1118
2018-01-09 20:30 | 1081 | 1078
2018-01-09 21:00 | 1042 | 1040
2018-01-09 21:30 | 989 | 989
2018-01-09 22:00 | 949 | 948
2018-01-09 22:30 | 887 | 886
2018-01-09 23:00 | 855 | 855
2018-01-09 23:30 | 798 | 795
2018-01-10 | 749 | 744
2018-01-10 00:30 | 698 | 695
2018-01-10 01:00 | 676 | 675
2018-01-10 01:30 | 658 | 656
2018-01-10 02:00 | 650 | 647
2018-01-10 02:30 | 642 | 636
2018-01-10 03:00 | 636 | 629
2018-01-10 03:30 | 631 | 623
2018-01-10 04:00 | 632 | 624
2018-01-10 04:30 | 637 | 630
2018-01-10 05:00 | 648 | 643
2018-01-10 05:30 | 666 | 662
2018-01-10 06:00 | 695 | 693
2018-01-10 06:30 | 752 | 752
2018-01-10 07:00 | 797 | 796
2018-01-10 07:30 | 877 | 877
2018-01-10 08:00 | 920 | 919
2018-01-10 08:30 | 959 | 958
2018-01-10 09:00 | 978 | 978
2018-01-10 09:30 | 996 | 995
2018-01-10 10:00 | 1012 | 1011
2018-01-10 10:30 | 1042 | 1042
2018-01-10 11:00 | 1065 | 1064
2018-01-10 11:30 | 1056 | 1055
2018-01-10 12:00 | 1061 | 1060
2018-01-10 12:30 | 1068 | 1065
2018-01-10 13:00 | 1075 | 1072
2018-01-10 13:30 | 1091 | 1088
2018-01-10 14:00 | 1104 | 1103
2018-01-10 14:30 | 1125 | 1124
2018-01-10 15:00 | 1148 | 1147
2018-01-10 15:30 | 1170 | 1170
2018-01-10 16:00 | 1186 | 1185
2018-01-10 16:30 | 1220 | 1220
2018-01-10 17:00 | 1242 | 1241
2018-01-10 17:30 | 1244 | 1243
2018-01-10 18:00 | 1231 | 1227
2018-01-10 18:30 | 1189 | 1179
2018-01-10 19:00 | 1188 | 1181
2018-01-10 19:30 | 1182 | 1179
2018-01-10 20:00 | 1167 | 1163
2018-01-10 20:30 | 1139 | 1133
2018-01-10 21:00 | 1077 | 1070
2018-01-10 21:30 | 1049 | 1037
2018-01-10 22:00 | 1008 | 992
2018-01-10 22:30 | 948 | 938
2018-01-10 23:00 | 916 | 904
2018-01-10 23:30 | 847 | 840
2018-01-11 | 796 | 791
2018-01-11 00:30 | 742 | 737
2018-01-11 01:00 | 711 | 705
2018-01-11 01:30 | 692 | 687
2018-01-11 02:00 | 682 | 677
2018-01-11 02:30 | 675 | 669
2018-01-11 03:00 | 667 | 661
2018-01-11 03:30 | 666 | 660
2018-01-11 04:00 | 666 | 660
2018-01-11 04:30 | 669 | 663
2018-01-11 05:00 | 674 | 669
2018-01-11 05:30 | 691 | 686
2018-01-11 06:00 | 713 | 711
2018-01-11 06:30 | 766 | 766
2018-01-11 07:00 | 833 | 832
2018-01-11 07:30 | 933 | 932
2018-01-11 08:00 | 963 | 963
2018-01-11 08:30 | 991 | 991
2018-01-11 09:00 | 1016 | 1015
2018-01-11 09:30 | 1033 | 1032
2018-01-11 10:00 | 1047 | 1046
2018-01-11 10:30 | 1057 | 1056
2018-01-11 11:00 | 1072 | 1070
2018-01-11 11:30 | 1119 | 1117
2018-01-11 12:00 | 1124 | 1123
2018-01-11 12:30 | 1132 | 1131
2018-01-11 13:00 | 1108 | 1108
2018-01-11 13:30 | 1143 | 1143
2018-01-11 14:00 | 1191 | 1191
2018-01-11 14:30 | 1227 | 1227
2018-01-11 15:00 | 1248 | 1248
2018-01-11 15:30 | 1257 | 1257
2018-01-11 16:00 | 1273 | 1272
2018-01-11 16:30 | 1288 | 1286
2018-01-11 17:00 | 1275 | 1272
2018-01-11 17:30 | 1298 | 1297
2018-01-11 18:00 | 1304 | 1302
2018-01-11 18:30 | 1270 | 1262
2018-01-11 19:00 | 1271 | 1265
2018-01-11 19:30 | 1280 | 1277
2018-01-11 20:00 | 1264 | 1261
2018-01-11 20:30 | 1227 | 1226
2018-01-11 21:00 | 1171 | 1170
2018-01-11 21:30 | 1104 | 1101
2018-01-11 22:00 | 1040 | 1037
2018-01-11 22:30 | 965 | 961
2018-01-11 23:00 | 902 | 900
2018-01-11 23:30 | 856 | 854
2018-01-12 | 790 | 786
2018-01-12 00:30 | 716 | 714
2018-01-12 01:00 | 691 | 688
2018-01-12 01:30 | 666 | 663
2018-01-12 02:00 | 657 | 652
2018-01-12 02:30 | 649 | 643
2018-01-12 03:00 | 640 | 634
2018-01-12 03:30 | 637 | 631
2018-01-12 04:00 | 634 | 627
2018-01-12 04:30 | 638 | 632
2018-01-12 05:00 | 647 | 643
2018-01-12 05:30 | 670 | 666
2018-01-12 06:00 | 700 | 699
2018-01-12 06:30 | 758 | 758
2018-01-12 07:00 | 830 | 829
2018-01-12 07:30 | 934 | 929
2018-01-12 08:00 | 959 | 952
2018-01-12 08:30 | 988 | 985
2018-01-12 09:00 | 1003 | 1001
2018-01-12 09:30 | 1028 | 1028
2018-01-12 10:00 | 1047 | 1046
2018-01-12 10:30 | 1041 | 1041
2018-01-12 11:00 | 1044 | 1044
2018-01-12 11:30 | 1054 | 1054
2018-01-12 12:00 | 1080 | 1079
2018-01-12 12:30 | 1091 | 1090
2018-01-12 13:00 | 1114 | 1114
2018-01-12 13:30 | 1133 | 1130
2018-01-12 14:00 | 1152 | 1151
2018-01-12 14:30 | 1180 | 1179
2018-01-12 15:00 | 1210 | 1209
2018-01-12 15:30 | 1239 | 1238
2018-01-12 16:00 | 1262 | 1262
2018-01-12 16:30 | 1281 | 1280
2018-01-12 17:00 | 1300 | 1299
2018-01-12 17:30 | 1290 | 1287
2018-01-12 18:00 | 1244 | 1238
2018-01-12 18:30 | 1200 | 1193
2018-01-12 19:00 | 1191 | 1186
2018-01-12 19:30 | 1191 | 1186
2018-01-12 20:00 | 1179 | 1176
2018-01-12 20:30 | 1151 | 1148
2018-01-12 21:00 | 1098 | 1097
2018-01-12 21:30 | 1052 | 1052
2018-01-12 22:00 | 1014 | 1014
2018-01-12 22:30 | 967 | 966
2018-01-12 23:00 | 913 | 913
2018-01-12 23:30 | 844 | 844
2018-01-13 | 777 | 777
2018-01-13 00:30 | 724 | 724
2018-01-13 01:00 | 700 | 699
2018-01-13 01:30 | 700 | 696
2018-01-13 02:00 | 680 | 674
2018-01-13 02:30 | 677 | 668
2018-01-13 03:00 | 669 | 659
2018-01-13 03:30 | 661 | 650
2018-01-13 04:00 | 657 | 646
2018-01-13 04:30 | 667 | 655
2018-01-13 05:00 | 664 | 652
2018-01-13 05:30 | 653 | 641
2018-01-13 06:00 | 660 | 653
2018-01-13 06:30 | 683 | 681
2018-01-13 07:00 | 709 | 709
2018-01-13 07:30 | 777 | 777
2018-01-13 08:00 | 818 | 818
2018-01-13 08:30 | 852 | 851
2018-01-13 09:00 | 885 | 884
2018-01-13 09:30 | 917 | 916
2018-01-13 10:00 | 954 | 952
2018-01-13 10:30 | 982 | 981
2018-01-13 11:00 | 1000 | 999
2018-01-13 11:30 | 1018 | 1018
2018-01-13 12:00 | 1044 | 1044
2018-01-13 12:30 | 1102 | 1102
2018-01-13 13:00 | 1130 | 1129
2018-01-13 13:30 | 1136 | 1136
2018-01-13 14:00 | 1196 | 1194
2018-01-13 14:30 | 1208 | 1205
2018-01-13 15:00 | 1233 | 1231
2018-01-13 15:30 | 1278 | 1277
2018-01-13 16:00 | 1312 | 1310
2018-01-13 16:30 | 1328 | 1328
2018-01-13 17:00 | 1356 | 1356
2018-01-13 17:30 | 1346 | 1346
2018-01-13 18:00 | 1330 | 1328
2018-01-13 18:30 | 1299 | 1295
2018-01-13 19:00 | 1286 | 1283
2018-01-13 19:30 | 1285 | 1283
2018-01-13 20:00 | 1266 | 1264
2018-01-13 20:30 | 1214 | 1213
2018-01-13 21:00 | 1154 | 1153
2018-01-13 21:30 | 1118 | 1115
2018-01-13 22:00 | 1062 | 1058
2018-01-13 22:30 | 1037 | 1031
2018-01-13 23:00 | 1004 | 1001
2018-01-13 23:30 | 912 | 910
2018-01-14 | 847 | 843
2018-01-14 00:30 | 797 | 794
2018-01-14 01:00 | 777 | 774
2018-01-14 01:30 | 760 | 757
2018-01-14 02:00 | 733 | 729
2018-01-14 02:30 | 715 | 711
2018-01-14 03:00 | 705 | 701
2018-01-14 03:30 | 698 | 693
2018-01-14 04:00 | 692 | 685
2018-01-14 04:30 | 698 | 690
2018-01-14 05:00 | 697 | 688
2018-01-14 05:30 | 687 | 675
2018-01-14 06:00 | 683 | 672
2018-01-14 06:30 | 691 | 684
2018-01-14 07:00 | 723 | 720
2018-01-14 07:30 | 772 | 772
2018-01-14 08:00 | 833 | 833
2018-01-14 08:30 | 902 | 902
2018-01-14 09:00 | 963 | 962
2018-01-14 09:30 | 1023 | 1022
2018-01-14 10:00 | 1049 | 1049
2018-01-14 10:30 | 1054 | 1054
2018-01-14 11:00 | 1065 | 1065
2018-01-14 11:30 | 1078 | 1078
2018-01-14 12:00 | 1100 | 1100
2018-01-14 12:30 | 1129 | 1129
2018-01-14 13:00 | 1167 | 1165
2018-01-14 13:30 | 1190 | 1187
2018-01-14 14:00 | 1198 | 1195
2018-01-14 14:30 | 1217 | 1215
2018-01-14 15:00 | 1226 | 1222
2018-01-14 15:30 | 1229 | 1223
2018-01-14 16:00 | 1218 | 1211
2018-01-14 16:30 | 1192 | 1184
2018-01-14 17:00 | 1157 | 1150
2018-01-14 17:30 | 1108 | 1100
2018-01-14 18:00 | 1059 | 1052
2018-01-14 18:30 | 1018 | 1010
2018-01-14 19:00 | 993 | 987
2018-01-14 19:30 | 971 | 969
2018-01-14 20:00 | 949 | 948
2018-01-14 20:30 | 922 | 922
2018-01-14 21:00 | 879 | 877
2018-01-14 21:30 | 835 | 832
2018-01-14 22:00 | 793 | 789
2018-01-14 22:30 | 769 | 763
2018-01-14 23:00 | 752 | 746
2018-01-14 23:30 | 688 | 681
2018-01-15 | 619 | 610
2018-01-15 00:30 | 571 | 556
2018-01-15 01:00 | 544 | 525
2018-01-15 01:30 | 542 | 520
2018-01-15 02:00 | 542 | 518
2018-01-15 02:30 | 530 | 503
2018-01-15 03:00 | 514 | 486
2018-01-15 03:30 | 509 | 482
2018-01-15 04:00 | 499 | 472
2018-01-15 04:30 | 514 | 489
2018-01-15 05:00 | 545 | 522
2018-01-15 05:30 | 587 | 567
2018-01-15 06:00 | 638 | 625
2018-01-15 06:30 | 699 | 696
2018-01-15 07:00 | 740 | 740
2018-01-15 07:30 | 792 | 792
2018-01-15 08:00 | 823 | 823
2018-01-15 08:30 | 833 | 833
2018-01-15 09:00 | 829 | 828
2018-01-15 09:30 | 836 | 835
2018-01-15 10:00 | 841 | 840
2018-01-15 10:30 | 842 | 842
2018-01-15 11:00 | 842 | 842
2018-01-15 11:30 | 849 | 849
2018-01-15 12:00 | 866 | 865
2018-01-15 12:30 | 875 | 875
2018-01-15 13:00 | 896 | 896
2018-01-15 13:30 | 906 | 906
2018-01-15 14:00 | 915 | 915
2018-01-15 14:30 | 927 | 927
2018-01-15 15:00 | 940 | 940
2018-01-15 15:30 | 950 | 950
2018-01-15 16:00 | 957 | 957
2018-01-15 16:30 | 975 | 975
2018-01-15 17:00 | 994 | 994
2018-01-15 17:30 | 996 | 995
2018-01-15 18:00 | 981 | 978
2018-01-15 18:30 | 969 | 964
2018-01-15 19:00 | 971 | 966
2018-01-15 19:30 | 979 | 975
2018-01-15 20:00 | 968 | 964
2018-01-15 20:30 | 938 | 936
2018-01-15 21:00 | 897 | 896
2018-01-15 21:30 | 859 | 859
2018-01-15 22:00 | 826 | 825
2018-01-15 22:30 | 784 | 782
2018-01-15 23:00 | 765 | 761
2018-01-15 23:30 | 714 | 709
2018-01-16 | 669 | 662
2018-01-16 00:30 | 634 | 623
2018-01-16 01:00 | 613 | 600
2018-01-16 01:30 | 604 | 587
2018-01-16 02:00 | 596 | 577
2018-01-16 02:30 | 592 | 574
2018-01-16 03:00 | 590 | 571
2018-01-16 03:30 | 584 | 565
2018-01-16 04:00 | 585 | 566
2018-01-16 04:30 | 594 | 576
2018-01-16 05:00 | 604 | 589
2018-01-16 05:30 | 624 | 610
2018-01-16 06:00 | 646 | 636
2018-01-16 06:30 | 691 | 689
2018-01-16 07:00 | 725 | 725
2018-01-16 07:30 | 780 | 780
2018-01-16 08:00 | 811 | 810
2018-01-16 08:30 | 824 | 822
2018-01-16 09:00 | 822 | 821
2018-01-16 09:30 | 814 | 813
2018-01-16 10:00 | 811 | 811
2018-01-16 10:30 | 821 | 821
2018-01-16 11:00 | 826 | 826
2018-01-16 11:30 | 836 | 836
2018-01-16 12:00 | 849 | 849
2018-01-16 12:30 | 861 | 861
2018-01-16 13:00 | 871 | 870
2018-01-16 13:30 | 868 | 867
2018-01-16 14:00 | 885 | 885
2018-01-16 14:30 | 884 | 884
2018-01-16 15:00 | 905 | 905
2018-01-16 15:30 | 920 | 920
2018-01-16 16:00 | 941 | 941
2018-01-16 16:30 | 967 | 967
2018-01-16 17:00 | 1005 | 1004
2018-01-16 17:30 | 1048 | 1047
2018-01-16 18:00 | 1056 | 1053
2018-01-16 18:30 | 1010 | 1002
2018-01-16 19:00 | 986 | 981
2018-01-16 19:30 | 994 | 992
2018-01-16 20:00 | 979 | 976
2018-01-16 20:30 | 939 | 939
2018-01-16 21:00 | 895 | 895
2018-01-16 21:30 | 862 | 862
2018-01-16 22:00 | 831 | 829
2018-01-16 22:30 | 790 | 786
2018-01-16 23:00 | 771 | 767
2018-01-16 23:30 | 727 | 717
2018-01-17 | 681 | 666
2018-01-17 00:30 | 647 | 626
2018-01-17 01:00 | 632 | 607
2018-01-17 01:30 | 619 | 596
2018-01-17 02:00 | 602 | 585
2018-01-17 02:30 | 598 | 581
2018-01-17 03:00 | 596 | 578
2018-01-17 03:30 | 591 | 574
2018-01-17 04:00 | 589 | 572
2018-01-17 04:30 | 600 | 583
2018-01-17 05:00 | 610 | 596
2018-01-17 05:30 | 629 | 616
2018-01-17 06:00 | 651 | 641
2018-01-17 06:30 | 692 | 688
2018-01-17 07:00 | 729 | 727
2018-01-17 07:30 | 785 | 784
2018-01-17 08:00 | 806 | 805
2018-01-17 08:30 | 821 | 820
2018-01-17 09:00 | 824 | 824
2018-01-17 09:30 | 822 | 822
2018-01-17 10:00 | 813 | 812
2018-01-17 10:30 | 813 | 813
2018-01-17 11:00 | 811 | 811
2018-01-17 11:30 | 815 | 815
2018-01-17 12:00 | 823 | 823
2018-01-17 12:30 | 833 | 833
2018-01-17 13:00 | 847 | 847
2018-01-17 13:30 | 858 | 857
2018-01-17 14:00 | 877 | 876
2018-01-17 14:30 | 895 | 895
2018-01-17 15:00 | 910 | 910
2018-01-17 15:30 | 928 | 928
2018-01-17 16:00 | 949 | 949
2018-01-17 16:30 | 977 | 977
2018-01-17 17:00 | 1013 | 1013
2018-01-17 17:30 | 1013 | 1013
2018-01-17 18:00 | 1008 | 1006
2018-01-17 18:30 | 990 | 985
2018-01-17 19:00 | 998 | 994
2018-01-17 19:30 | 1002 | 1000
2018-01-17 20:00 | 996 | 993
2018-01-17 20:30 | 967 | 963
2018-01-17 21:00 | 923 | 920
2018-01-17 21:30 | 887 | 887
2018-01-17 22:00 | 857 | 856
2018-01-17 22:30 | 821 | 818
2018-01-17 23:00 | 795 | 791
2018-01-17 23:30 | 741 | 734
2018-01-18 | 702 | 690
2018-01-18 00:30 | 661 | 644
2018-01-18 01:00 | 641 | 620
2018-01-18 01:30 | 621 | 602
2018-01-18 02:00 | 590 | 577
2018-01-18 02:30 | 610 | 597
2018-01-18 03:00 | 603 | 589
2018-01-18 03:30 | 602 | 589
2018-01-18 04:00 | 599 | 586
2018-01-18 04:30 | 612 | 600
2018-01-18 05:00 | 621 | 612
2018-01-18 05:30 | 638 | 629
2018-01-18 06:00 | 667 | 660
2018-01-18 06:30 | 714 | 712
2018-01-18 07:00 | 759 | 756
2018-01-18 07:30 | 810 | 810
2018-01-18 08:00 | 836 | 836
2018-01-18 08:30 | 847 | 847
2018-01-18 09:00 | 855 | 855
2018-01-18 09:30 | 856 | 855
2018-01-18 10:00 | 852 | 852
2018-01-18 10:30 | 855 | 855
2018-01-18 11:00 | 862 | 861
2018-01-18 11:30 | 869 | 869
2018-01-18 12:00 | 877 | 877
2018-01-18 12:30 | 887 | 887
2018-01-18 13:00 | 901 | 901
2018-01-18 13:30 | 918 | 918
2018-01-18 14:00 | 928 | 927
2018-01-18 14:30 | 911 | 910
2018-01-18 15:00 | 927 | 927
2018-01-18 15:30 | 879 | 878
2018-01-18 16:00 | 928 | 927
2018-01-18 16:30 | 998 | 998
2018-01-18 17:00 | 1018 | 1018
2018-01-18 17:30 | 1017 | 1017
2018-01-18 18:00 | 1013 | 1009
2018-01-18 18:30 | 956 | 951
2018-01-18 19:00 | 1000 | 994
2018-01-18 19:30 | 1017 | 1012
2018-01-18 20:00 | 1000 | 996
2018-01-18 20:30 | 977 | 973
2018-01-18 21:00 | 938 | 934
2018-01-18 21:30 | 891 | 885
2018-01-18 22:00 | 841 | 836
2018-01-18 22:30 | 816 | 813
2018-01-18 23:00 | 803 | 798
2018-01-18 23:30 | 750 | 741
2018-01-19 | 707 | 693
2018-01-19 00:30 | 659 | 647
2018-01-19 01:00 | 637 | 622
2018-01-19 01:30 | 625 | 605
2018-01-19 02:00 | 623 | 601
2018-01-19 02:30 | 605 | 588
2018-01-19 03:00 | 597 | 582
2018-01-19 03:30 | 590 | 575
2018-01-19 04:00 | 593 | 579
2018-01-19 04:30 | 595 | 583
2018-01-19 05:00 | 608 | 599
2018-01-19 05:30 | 631 | 621
2018-01-19 06:00 | 657 | 650
2018-01-19 06:30 | 701 | 696
2018-01-19 07:00 | 724 | 723
2018-01-19 07:30 | 787 | 787
2018-01-19 08:00 | 810 | 809
2018-01-19 08:30 | 828 | 828
2018-01-19 09:00 | 843 | 839
2018-01-19 09:30 | 840 | 837
2018-01-19 10:00 | 826 | 824
2018-01-19 10:30 | 821 | 820
2018-01-19 11:00 | 813 | 813
2018-01-19 11:30 | 786 | 785
2018-01-19 12:00 | 848 | 847
2018-01-19 12:30 | 836 | 835
2018-01-19 13:00 | 830 | 828
2018-01-19 13:30 | 937 | 937
2018-01-19 14:00 | 964 | 963
2018-01-19 14:30 | 988 | 987
2018-01-19 15:00 | 1028 | 1028
2018-01-19 15:30 | 1061 | 1061
2018-01-19 16:00 | 1100 | 1099
2018-01-19 16:30 | 1126 | 1125
2018-01-19 17:00 | 1157 | 1154
2018-01-19 17:30 | 1157 | 1154
2018-01-19 18:00 | 1122 | 1120
2018-01-19 18:30 | 1103 | 1101
2018-01-19 19:00 | 1110 | 1109
2018-01-19 19:30 | 1115 | 1115
2018-01-19 20:00 | 1109 | 1108
2018-01-19 20:30 | 972 | 966
2018-01-19 21:00 | 935 | 932
2018-01-19 21:30 | 911 | 908
2018-01-19 22:00 | 883 | 879
2018-01-19 22:30 | 842 | 839
2018-01-19 23:00 | 821 | 816
2018-01-19 23:30 | 762 | 759
2018-01-20 | 706 | 702
2018-01-20 00:30 | 662 | 656
2018-01-20 01:00 | 660 | 655
2018-01-20 01:30 | 678 | 673
2018-01-20 02:00 | 664 | 657
2018-01-20 02:30 | 651 | 643
2018-01-20 03:00 | 646 | 637
2018-01-20 03:30 | 650 | 640
2018-01-20 04:00 | 654 | 643
2018-01-20 04:30 | 655 | 644
2018-01-20 05:00 | 659 | 647
2018-01-20 05:30 | 666 | 654
2018-01-20 06:00 | 674 | 663
2018-01-20 06:30 | 688 | 681
2018-01-20 07:00 | 703 | 699
2018-01-20 07:30 | 740 | 739
2018-01-20 08:00 | 760 | 760
2018-01-20 08:30 | 790 | 789
2018-01-20 09:00 | 811 | 811
2018-01-20 09:30 | 760 | 758
2018-01-20 10:00 | 759 | 758
2018-01-20 10:30 | 767 | 767
2018-01-20 11:00 | 764 | 764
2018-01-20 11:30 | 766 | 766
2018-01-20 12:00 | 760 | 760
2018-01-20 12:30 | 763 | 763
2018-01-20 13:00 | 771 | 771
2018-01-20 13:30 | 793 | 793
2018-01-20 14:00 | 817 | 817
2018-01-20 14:30 | 839 | 838
2018-01-20 15:00 | 858 | 858
2018-01-20 15:30 | 884 | 884
2018-01-20 16:00 | 911 | 911
2018-01-20 16:30 | 943 | 943
2018-01-20 17:00 | 966 | 966
2018-01-20 17:30 | 976 | 975
2018-01-20 18:00 | 966 | 965
2018-01-20 18:30 | 962 | 960
2018-01-20 19:00 | 971 | 968
2018-01-20 19:30 | 977 | 975
2018-01-20 20:00 | 971 | 969
2018-01-20 20:30 | 953 | 949
2018-01-20 21:00 | 908 | 906
2018-01-20 21:30 | 878 | 877
2018-01-20 22:00 | 853 | 851
2018-01-20 22:30 | 823 | 823
2018-01-20 23:00 | 805 | 804
2018-01-20 23:30 | 753 | 751
2018-01-21 | 712 | 708
2018-01-21 00:30 | 666 | 662
2018-01-21 01:00 | 643 | 638
2018-01-21 01:30 | 631 | 625
2018-01-21 02:00 | 615 | 606
2018-01-21 02:30 | 604 | 595
2018-01-21 03:00 | 603 | 593
2018-01-21 03:30 | 598 | 586
2018-01-21 04:00 | 595 | 584
2018-01-21 04:30 | 590 | 578
2018-01-21 05:00 | 588 | 575
2018-01-21 05:30 | 588 | 572
2018-01-21 06:00 | 592 | 577
2018-01-21 06:30 | 602 | 590
2018-01-21 07:00 | 609 | 601
2018-01-21 07:30 | 638 | 635
2018-01-21 08:00 | 674 | 673
2018-01-21 08:30 | 701 | 701
2018-01-21 09:00 | 733 | 733
2018-01-21 09:30 | 764 | 764
2018-01-21 10:00 | 779 | 779
2018-01-21 10:30 | 775 | 775
2018-01-21 11:00 | 773 | 773
2018-01-21 11:30 | 772 | 772
2018-01-21 12:00 | 788 | 788
2018-01-21 12:30 | 791 | 791
2018-01-21 13:00 | 820 | 820
2018-01-21 13:30 | 824 | 824
2018-01-21 14:00 | 843 | 843
2018-01-21 14:30 | 876 | 876
2018-01-21 15:00 | 922 | 922
2018-01-21 15:30 | 947 | 946
2018-01-21 16:00 | 969 | 969
2018-01-21 16:30 | 984 | 984
2018-01-21 17:00 | 997 | 997
2018-01-21 17:30 | 1005 | 1004
2018-01-21 18:00 | 1010 | 1008
2018-01-21 18:30 | 1009 | 1006
2018-01-21 19:00 | 1020 | 1018
2018-01-21 19:30 | 1036 | 1035
2018-01-21 20:00 | 1030 | 1029
2018-01-21 20:30 | 997 | 994
2018-01-21 21:00 | 945 | 944
2018-01-21 21:30 | 912 | 910
2018-01-21 22:00 | 881 | 876
2018-01-21 22:30 | 828 | 828
2018-01-21 23:00 | 807 | 807
2018-01-21 23:30 | 756 | 756
2018-01-22 | 708 | 706
2018-01-22 00:30 | 664 | 660
2018-01-22 01:00 | 647 | 641
2018-01-22 01:30 | 633 | 626
2018-01-22 02:00 | 620 | 612
2018-01-22 02:30 | 616 | 608
2018-01-22 03:00 | 611 | 603
2018-01-22 03:30 | 609 | 600
2018-01-22 04:00 | 611 | 602
2018-01-22 04:30 | 622 | 613
2018-01-22 05:00 | 634 | 629
2018-01-22 05:30 | 659 | 655
2018-01-22 06:00 | 689 | 687
2018-01-22 06:30 | 764 | 762
2018-01-22 07:00 | 821 | 818
2018-01-22 07:30 | 900 | 897
2018-01-22 08:00 | 949 | 947
2018-01-22 08:30 | 988 | 987
2018-01-22 09:00 | 998 | 997
2018-01-22 09:30 | 1011 | 1011
2018-01-22 10:00 | 1019 | 1018
2018-01-22 10:30 | 1020 | 1020
2018-01-22 11:00 | 1031 | 1031
2018-01-22 11:30 | 1038 | 1038
2018-01-22 12:00 | 1053 | 1052
2018-01-22 12:30 | 1062 | 1062
2018-01-22 13:00 | 1080 | 1080
2018-01-22 13:30 | 1098 | 1098
2018-01-22 14:00 | 1122 | 1121
2018-01-22 14:30 | 1138 | 1138
2018-01-22 15:00 | 1147 | 1147
2018-01-22 15:30 | 1169 | 1168
2018-01-22 16:00 | 1199 | 1199
2018-01-22 16:30 | 1216 | 1215
2018-01-22 17:00 | 1226 | 1224
2018-01-22 17:30 | 1215 | 1211
2018-01-22 18:00 | 1187 | 1183
2018-01-22 18:30 | 1159 | 1152
2018-01-22 19:00 | 1161 | 1156
2018-01-22 19:30 | 1159 | 1155
2018-01-22 20:00 | 1149 | 1147
2018-01-22 20:30 | 1121 | 1120
2018-01-22 21:00 | 1063 | 1062
2018-01-22 21:30 | 1006 | 1005
2018-01-22 22:00 | 962 | 959
2018-01-22 22:30 | 913 | 908
2018-01-22 23:00 | 880 | 877
2018-01-22 23:30 | 817 | 813
2018-01-23 | 766 | 758
2018-01-23 00:30 | 730 | 718
2018-01-23 01:00 | 705 | 692
2018-01-23 01:30 | 681 | 674
2018-01-23 02:00 | 674 | 665
2018-01-23 02:30 | 663 | 654
2018-01-23 03:00 | 658 | 648
2018-01-23 03:30 | 659 | 648
2018-01-23 04:00 | 656 | 646
2018-01-23 04:30 | 668 | 659
2018-01-23 05:00 | 677 | 670
2018-01-23 05:30 | 698 | 691
2018-01-23 06:00 | 727 | 723
2018-01-23 06:30 | 747 | 747
2018-01-23 07:00 | 791 | 791
2018-01-23 07:30 | 868 | 867
2018-01-23 08:00 | 887 | 887
2018-01-23 08:30 | 914 | 914
2018-01-23 09:00 | 917 | 917
2018-01-23 09:30 | 960 | 958
2018-01-23 10:00 | 955 | 954
2018-01-23 10:30 | 1006 | 1005
2018-01-23 11:00 | 1026 | 1026
2018-01-23 11:30 | 1030 | 1030
2018-01-23 12:00 | 1034 | 1034
2018-01-23 12:30 | 1045 | 1045
2018-01-23 13:00 | 1059 | 1059
2018-01-23 13:30 | 1079 | 1079
2018-01-23 14:00 | 1101 | 1101
2018-01-23 14:30 | 1126 | 1126
2018-01-23 15:00 | 1140 | 1139
2018-01-23 15:30 | 1160 | 1160
2018-01-23 16:00 | 1199 | 1199
2018-01-23 16:30 | 1233 | 1233
2018-01-23 17:00 | 1252 | 1252
2018-01-23 17:30 | 1252 | 1251
2018-01-23 18:00 | 1228 | 1223
2018-01-23 18:30 | 1192 | 1185
2018-01-23 19:00 | 1187 | 1186
2018-01-23 19:30 | 1194 | 1193
2018-01-23 20:00 | 1183 | 1182
2018-01-23 20:30 | 1148 | 1146
2018-01-23 21:00 | 1097 | 1095
2018-01-23 21:30 | 1037 | 1036
2018-01-23 22:00 | 980 | 979
2018-01-23 22:30 | 927 | 927
2018-01-23 23:00 | 888 | 887
2018-01-23 23:30 | 829 | 827
2018-01-24 | 776 | 774
2018-01-24 00:30 | 725 | 724
2018-01-24 01:00 | 706 | 704
2018-01-24 01:30 | 690 | 688
2018-01-24 02:00 | 681 | 678
2018-01-24 02:30 | 673 | 669
2018-01-24 03:00 | 664 | 660
2018-01-24 03:30 | 663 | 659
2018-01-24 04:00 | 665 | 661
2018-01-24 04:30 | 671 | 667
2018-01-24 05:00 | 687 | 684
2018-01-24 05:30 | 710 | 708
2018-01-24 06:00 | 744 | 743
2018-01-24 06:30 | 802 | 802
2018-01-24 07:00 | 858 | 858
2018-01-24 07:30 | 941 | 940
2018-01-24 08:00 | 982 | 980
2018-01-24 08:30 | 1015 | 1013
2018-01-24 09:00 | 1022 | 1018
2018-01-24 09:30 | 1060 | 1057
2018-01-24 10:00 | 1076 | 1073
2018-01-24 10:30 | 1089 | 1088
2018-01-24 11:00 | 1100 | 1099
2018-01-24 11:30 | 1088 | 1087
2018-01-24 12:00 | 1087 | 1085
2018-01-24 12:30 | 1106 | 1103
2018-01-24 13:00 | 1131 | 1128
2018-01-24 13:30 | 1140 | 1139
2018-01-24 14:00 | 1151 | 1150
2018-01-24 14:30 | 1165 | 1165
2018-01-24 15:00 | 1180 | 1180
2018-01-24 15:30 | 1201 | 1201
2018-01-24 16:00 | 1231 | 1230
2018-01-24 16:30 | 1250 | 1249
2018-01-24 17:00 | 1266 | 1265
2018-01-24 17:30 | 1259 | 1259
2018-01-24 18:00 | 1238 | 1237
2018-01-24 18:30 | 1210 | 1207
2018-01-24 19:00 | 1211 | 1210
2018-01-24 19:30 | 1211 | 1210
2018-01-24 20:00 | 1198 | 1196
2018-01-24 20:30 | 1162 | 1158
2018-01-24 21:00 | 1107 | 1105
2018-01-24 21:30 | 1065 | 1062
2018-01-24 22:00 | 1022 | 1015
2018-01-24 22:30 | 959 | 952
2018-01-24 23:00 | 928 | 924
2018-01-24 23:30 | 860 | 857
2018-01-25 | 815 | 810
2018-01-25 00:30 | 765 | 761
2018-01-25 01:00 | 736 | 735
2018-01-25 01:30 | 716 | 714
2018-01-25 02:00 | 695 | 692
2018-01-25 02:30 | 694 | 692
2018-01-25 03:00 | 691 | 689
2018-01-25 03:30 | 690 | 688
2018-01-25 04:00 | 686 | 683
2018-01-25 04:30 | 694 | 692
2018-01-25 05:00 | 704 | 703
2018-01-25 05:30 | 729 | 728
2018-01-25 06:00 | 764 | 763
2018-01-25 06:30 | 834 | 833
2018-01-25 07:00 | 894 | 893
2018-01-25 07:30 | 981 | 981
2018-01-25 08:00 | 1022 | 1022
2018-01-25 08:30 | 1043 | 1043
2018-01-25 09:00 | 1061 | 1061
2018-01-25 09:30 | 1079 | 1079
2018-01-25 10:00 | 1094 | 1094
2018-01-25 10:30 | 1110 | 1110
2018-01-25 11:00 | 1111 | 1110
2018-01-25 11:30 | 1133 | 1133
2018-01-25 12:00 | 1145 | 1145
2018-01-25 12:30 | 1153 | 1153
2018-01-25 13:00 | 1157 | 1157
2018-01-25 13:30 | 1177 | 1176
2018-01-25 14:00 | 1196 | 1194
2018-01-25 14:30 | 1222 | 1221
2018-01-25 15:00 | 1226 | 1225
2018-01-25 15:30 | 1224 | 1222
2018-01-25 16:00 | 1247 | 1246
2018-01-25 16:30 | 1263 | 1260
2018-01-25 17:00 | 1281 | 1278
2018-01-25 17:30 | 1266 | 1262
2018-01-25 18:00 | 1246 | 1240
2018-01-25 18:30 | 1223 | 1214
2018-01-25 19:00 | 1220 | 1214
2018-01-25 19:30 | 1221 | 1217
2018-01-25 20:00 | 1217 | 1212
2018-01-25 20:30 | 1181 | 1177
2018-01-25 21:00 | 1132 | 1130
2018-01-25 21:30 | 1082 | 1079
2018-01-25 22:00 | 1034 | 1030
2018-01-25 22:30 | 991 | 984
2018-01-25 23:00 | 949 | 946
2018-01-25 23:30 | 884 | 880
2018-01-26 | 824 | 822
2018-01-26 00:30 | 770 | 769
2018-01-26 01:00 | 743 | 742
2018-01-26 01:30 | 723 | 722
2018-01-26 02:00 | 709 | 707
2018-01-26 02:30 | 697 | 695
2018-01-26 03:00 | 687 | 684
2018-01-26 03:30 | 680 | 677
2018-01-26 04:00 | 676 | 673
2018-01-26 04:30 | 677 | 673
2018-01-26 05:00 | 674 | 671
2018-01-26 05:30 | 674 | 669
2018-01-26 06:00 | 685 | 680
2018-01-26 06:30 | 704 | 703
2018-01-26 07:00 | 733 | 733
2018-01-26 07:30 | 795 | 795
2018-01-26 08:00 | 842 | 841
2018-01-26 08:30 | 883 | 883
2018-01-26 09:00 | 911 | 911
2018-01-26 09:30 | 931 | 931
2018-01-26 10:00 | 953 | 952
2018-01-26 10:30 | 967 | 967
2018-01-26 11:00 | 969 | 969
2018-01-26 11:30 | 980 | 980
2018-01-26 12:00 | 985 | 985
2018-01-26 12:30 | 989 | 989
2018-01-26 13:00 | 995 | 995
2018-01-26 13:30 | 991 | 991
2018-01-26 14:00 | 1004 | 1003
2018-01-26 14:30 | 1018 | 1017
2018-01-26 15:00 | 1037 | 1037
2018-01-26 15:30 | 1050 | 1050
2018-01-26 16:00 | 1083 | 1083
2018-01-26 16:30 | 1111 | 1110
2018-01-26 17:00 | 1130 | 1128
2018-01-26 17:30 | 1137 | 1135
2018-01-26 18:00 | 1132 | 1128
2018-01-26 18:30 | 1125 | 1118
2018-01-26 19:00 | 1125 | 1118
2018-01-26 19:30 | 1131 | 1128
2018-01-26 20:00 | 1129 | 1125
2018-01-26 20:30 | 1109 | 1105
2018-01-26 21:00 | 1072 | 1069
2018-01-26 21:30 | 1036 | 1035
2018-01-26 22:00 | 1005 | 1003
2018-01-26 22:30 | 967 | 963
2018-01-26 23:00 | 935 | 934
2018-01-26 23:30 | 870 | 869
2018-01-27 | 823 | 821
2018-01-27 00:30 | 776 | 775
2018-01-27 01:00 | 751 | 751
2018-01-27 01:30 | 733 | 732
2018-01-27 02:00 | 719 | 718
2018-01-27 02:30 | 711 | 710
2018-01-27 03:00 | 705 | 703
2018-01-27 03:30 | 695 | 693
2018-01-27 04:00 | 695 | 693
2018-01-27 04:30 | 692 | 690
2018-01-27 05:00 | 697 | 695
2018-01-27 05:30 | 696 | 694
2018-01-27 06:00 | 697 | 695
2018-01-27 06:30 | 726 | 726
2018-01-27 07:00 | 743 | 743
2018-01-27 07:30 | 799 | 799
2018-01-27 08:00 | 835 | 834
2018-01-27 08:30 | 883 | 883
2018-01-27 09:00 | 910 | 909
2018-01-27 09:30 | 936 | 936
2018-01-27 10:00 | 945 | 945
2018-01-27 10:30 | 962 | 962
2018-01-27 11:00 | 966 | 965
2018-01-27 11:30 | 965 | 963
2018-01-27 12:00 | 965 | 963
2018-01-27 12:30 | 976 | 974
2018-01-27 13:00 | 996 | 993
2018-01-27 13:30 | 1009 | 1005
2018-01-27 14:00 | 1032 | 1032
2018-01-27 14:30 | 1048 | 1048
2018-01-27 15:00 | 1073 | 1073
2018-01-27 15:30 | 1094 | 1094
2018-01-27 16:00 | 1124 | 1123
2018-01-27 16:30 | 1139 | 1139
2018-01-27 17:00 | 1165 | 1165
2018-01-27 17:30 | 1179 | 1178
2018-01-27 18:00 | 1156 | 1154
2018-01-27 18:30 | 1132 | 1128
2018-01-27 19:00 | 1127 | 1125
2018-01-27 19:30 | 1127 | 1127
2018-01-27 20:00 | 1114 | 1113
2018-01-27 20:30 | 1086 | 1085
2018-01-27 21:00 | 1043 | 1043
2018-01-27 21:30 | 1014 | 1014
2018-01-27 22:00 | 980 | 979
2018-01-27 22:30 | 946 | 945
2018-01-27 23:00 | 920 | 919
2018-01-27 23:30 | 862 | 859
2018-01-28 | 814 | 811
2018-01-28 00:30 | 760 | 759
2018-01-28 01:00 | 740 | 739
2018-01-28 01:30 | 726 | 725
2018-01-28 02:00 | 702 | 700
2018-01-28 02:30 | 691 | 687
2018-01-28 03:00 | 684 | 679
2018-01-28 03:30 | 677 | 673
2018-01-28 04:00 | 670 | 664
2018-01-28 04:30 | 667 | 662
2018-01-28 05:00 | 667 | 662
2018-01-28 05:30 | 670 | 663
2018-01-28 06:00 | 666 | 660
2018-01-28 06:30 | 674 | 670
2018-01-28 07:00 | 695 | 693
2018-01-28 07:30 | 728 | 728
2018-01-28 08:00 | 764 | 764
2018-01-28 08:30 | 803 | 803
2018-01-28 09:00 | 826 | 826
2018-01-28 09:30 | 846 | 846
2018-01-28 10:00 | 848 | 848
2018-01-28 10:30 | 848 | 848
2018-01-28 11:00 | 862 | 862
2018-01-28 11:30 | 871 | 869
2018-01-28 12:00 | 870 | 867
2018-01-28 12:30 | 894 | 892
2018-01-28 13:00 | 879 | 877
2018-01-28 13:30 | 905 | 904
2018-01-28 14:00 | 905 | 904
2018-01-28 14:30 | 914 | 913
2018-01-28 15:00 | 926 | 925
2018-01-28 15:30 | 962 | 962
2018-01-28 16:00 | 981 | 981
2018-01-28 16:30 | 1009 | 1008
2018-01-28 17:00 | 1024 | 1023
2018-01-28 17:30 | 1028 | 1026
2018-01-28 18:00 | 1040 | 1038
2018-01-28 18:30 | 1040 | 1037
2018-01-28 19:00 | 1057 | 1055
2018-01-28 19:30 | 1069 | 1065
2018-01-28 20:00 | 1061 | 1056
2018-01-28 20:30 | 1033 | 1030
2018-01-28 21:00 | 986 | 986
2018-01-28 21:30 | 952 | 952
2018-01-28 22:00 | 911 | 910
2018-01-28 22:30 | 873 | 872
2018-01-28 23:00 | 857 | 856
2018-01-28 23:30 | 804 | 802
2018-01-29 | 755 | 749
2018-01-29 00:30 | 705 | 701
2018-01-29 01:00 | 685 | 679
2018-01-29 01:30 | 672 | 666
2018-01-29 02:00 | 659 | 653
2018-01-29 02:30 | 658 | 651
2018-01-29 03:00 | 652 | 644
2018-01-29 03:30 | 649 | 642
2018-01-29 04:00 | 650 | 644
2018-01-29 04:30 | 659 | 654
2018-01-29 05:00 | 673 | 670
2018-01-29 05:30 | 704 | 702
2018-01-29 06:00 | 737 | 736
2018-01-29 06:30 | 804 | 804
2018-01-29 07:00 | 864 | 864
2018-01-29 07:30 | 945 | 945
2018-01-29 08:00 | 980 | 980
2018-01-29 08:30 | 1001 | 1000
2018-01-29 09:00 | 1017 | 1017
2018-01-29 09:30 | 1029 | 1029
2018-01-29 10:00 | 1046 | 1046
2018-01-29 10:30 | 1052 | 1051
2018-01-29 11:00 | 1035 | 1035
2018-01-29 11:30 | 1027 | 1027
2018-01-29 12:00 | 1045 | 1045
2018-01-29 12:30 | 1047 | 1047
2018-01-29 13:00 | 1058 | 1057
2018-01-29 13:30 | 1090 | 1089
2018-01-29 14:00 | 1108 | 1107
2018-01-29 14:30 | 1112 | 1110
2018-01-29 15:00 | 1126 | 1126
2018-01-29 15:30 | 1127 | 1126
2018-01-29 16:00 | 1168 | 1167
2018-01-29 16:30 | 1181 | 1180
2018-01-29 17:00 | 1208 | 1207
2018-01-29 17:30 | 1205 | 1202
2018-01-29 18:00 | 1184 | 1177
2018-01-29 18:30 | 1153 | 1147
2018-01-29 19:00 | 1160 | 1156
2018-01-29 19:30 | 1151 | 1147
2018-01-29 20:00 | 1137 | 1136
2018-01-29 20:30 | 1102 | 1101
2018-01-29 21:00 | 1052 | 1052
2018-01-29 21:30 | 996 | 996
2018-01-29 22:00 | 970 | 969
2018-01-29 22:30 | 920 | 917
2018-01-29 23:00 | 895 | 893
2018-01-29 23:30 | 830 | 828
2018-01-30 | 778 | 776
2018-01-30 00:30 | 727 | 725
2018-01-30 01:00 | 700 | 696
2018-01-30 01:30 | 682 | 677
2018-01-30 02:00 | 675 | 669
2018-01-30 02:30 | 662 | 655
2018-01-30 03:00 | 665 | 658
2018-01-30 03:30 | 663 | 656
2018-01-30 04:00 | 661 | 654
2018-01-30 04:30 | 674 | 669
2018-01-30 05:00 | 691 | 688
2018-01-30 05:30 | 722 | 718
2018-01-30 06:00 | 753 | 750
2018-01-30 06:30 | 815 | 814
2018-01-30 07:00 | 881 | 881
2018-01-30 07:30 | 954 | 954
2018-01-30 08:00 | 983 | 983
2018-01-30 08:30 | 1006 | 1006
2018-01-30 09:00 | 1025 | 1025
2018-01-30 09:30 | 1047 | 1046
2018-01-30 10:00 | 1058 | 1058
2018-01-30 10:30 | 1065 | 1064
2018-01-30 11:00 | 1056 | 1055
2018-01-30 11:30 | 1071 | 1070
2018-01-30 12:00 | 1084 | 1084
2018-01-30 12:30 | 1093 | 1093
2018-01-30 13:00 | 1031 | 1030
2018-01-30 13:30 | 1059 | 1059
2018-01-30 14:00 | 1106 | 1104
2018-01-30 14:30 | 1129 | 1126
2018-01-30 15:00 | 1134 | 1131
2018-01-30 15:30 | 1141 | 1139
2018-01-30 16:00 | 1201 | 1196
2018-01-30 16:30 | 1227 | 1220
2018-01-30 17:00 | 1258 | 1251
2018-01-30 17:30 | 1259 | 1250
2018-01-30 18:00 | 1223 | 1212
2018-01-30 18:30 | 1214 | 1205
2018-01-30 19:00 | 1218 | 1213
2018-01-30 19:30 | 1220 | 1216
2018-01-30 20:00 | 1209 | 1204
2018-01-30 20:30 | 1166 | 1162
2018-01-30 21:00 | 1111 | 1107
2018-01-30 21:30 | 1063 | 1058
2018-01-30 22:00 | 1011 | 1004
2018-01-30 22:30 | 955 | 949
2018-01-30 23:00 | 879 | 874
2018-01-30 23:30 | 806 | 802
2018-01-31 | 796 | 793
2018-01-31 00:30 | 746 | 744
2018-01-31 01:00 | 720 | 717
2018-01-31 01:30 | 665 | 661
2018-01-31 02:00 | 664 | 659
2018-01-31 02:30 | 640 | 634
2018-01-31 03:00 | 653 | 648
2018-01-31 03:30 | 647 | 640
2018-01-31 04:00 | 581 | 573
2018-01-31 04:30 | 594 | 587
2018-01-31 05:00 | 652 | 647
2018-01-31 05:30 | 628 | 624
2018-01-31 06:00 | 728 | 726
2018-01-31 06:30 | 815 | 815
2018-01-31 07:00 | 873 | 872
2018-01-31 07:30 | 957 | 953
2018-01-31 08:00 | 987 | 984
2018-01-31 08:30 | 1006 | 1001
2018-01-31 09:00 | 965 | 965
2018-01-31 09:30 | 1013 | 1013
2018-01-31 10:00 | 1051 | 1050
2018-01-31 10:30 | 1043 | 1042
2018-01-31 11:00 | 1068 | 1067
2018-01-31 11:30 | 1125 | 1124
2018-01-31 12:00 | 1140 | 1140
2018-01-31 12:30 | 1159 | 1159
2018-01-31 13:00 | 1174 | 1174
2018-01-31 13:30 | 1194 | 1194
2018-01-31 14:00 | 1219 | 1219
2018-01-31 14:30 | 1237 | 1236
2018-01-31 15:00 | 1247 | 1247
2018-01-31 15:30 | 1277 | 1277
2018-01-31 16:00 | 1316 | 1315
2018-01-31 16:30 | 1335 | 1335
2018-01-31 17:00 | 1343 | 1343
2018-01-31 17:30 | 1305 | 1304
2018-01-31 18:00 | 1288 | 1284
2018-01-31 18:30 | 1250 | 1247
2018-01-31 19:00 | 1261 | 1259
2018-01-31 19:30 | 1222 | 1219
2018-01-31 20:00 | 1195 | 1194
2018-01-31 20:30 | 1135 | 1134
2018-01-31 21:00 | 1083 | 1083
2018-01-31 21:30 | 1035 | 1034
2018-01-31 22:00 | 990 | 987
2018-01-31 22:30 | 936 | 933
2018-01-31 23:00 | 900 | 894
2018-01-31 23:30 | 836 | 833
2018-02-01 | 781 | 780
2018-02-01 00:30 | 741 | 738
2018-02-01 01:00 | 716 | 712
2018-02-01 01:30 | 699 | 694
2018-02-01 02:00 | 691 | 685
2018-02-01 02:30 | 687 | 681
2018-02-01 03:00 | 681 | 675
2018-02-01 03:30 | 677 | 671
2018-02-01 04:00 | 678 | 671
2018-02-01 04:30 | 683 | 677
2018-02-01 05:00 | 696 | 692
2018-02-01 05:30 | 731 | 728
2018-02-01 06:00 | 756 | 752
2018-02-01 06:30 | 819 | 817
2018-02-01 07:00 | 868 | 866
2018-02-01 07:30 | 944 | 943
2018-02-01 08:00 | 967 | 965
2018-02-01 08:30 | 979 | 977
2018-02-01 09:00 | 973 | 971
2018-02-01 09:30 | 968 | 966
2018-02-01 10:00 | 976 | 974
2018-02-01 10:30 | 954 | 952
2018-02-01 11:00 | 932 | 930
2018-02-01 11:30 | 968 | 967
2018-02-01 12:00 | 977 | 976
2018-02-01 12:30 | 958 | 955
2018-02-01 13:00 | 941 | 938
2018-02-01 13:30 | 947 | 945
2018-02-01 14:00 | 976 | 974
2018-02-01 14:30 | 979 | 977
2018-02-01 15:00 | 987 | 984
2018-02-01 15:30 | 981 | 977
2018-02-01 16:00 | 998 | 994
2018-02-01 16:30 | 1002 | 997
2018-02-01 17:00 | 1009 | 1004
2018-02-01 17:30 | 1007 | 1002
2018-02-01 18:00 | 1004 | 999
2018-02-01 18:30 | 997 | 990
2018-02-01 19:00 | 1016 | 1011
2018-02-01 19:30 | 1003 | 998
2018-02-01 20:00 | 991 | 988
2018-02-01 20:30 | 964 | 963
2018-02-01 21:00 | 932 | 931
2018-02-01 21:30 | 892 | 889
2018-02-01 22:00 | 859 | 858
2018-02-01 22:30 | 819 | 817
2018-02-01 23:00 | 808 | 804
2018-02-01 23:30 | 761 | 754
2018-02-02 | 717 | 707
2018-02-02 00:30 | 677 | 666
2018-02-02 01:00 | 654 | 641
2018-02-02 01:30 | 643 | 628
2018-02-02 02:00 | 639 | 621
2018-02-02 02:30 | 633 | 615
2018-02-02 03:00 | 625 | 607
2018-02-02 03:30 | 630 | 612
2018-02-02 04:00 | 629 | 610
2018-02-02 04:30 | 631 | 614
2018-02-02 05:00 | 641 | 626
2018-02-02 05:30 | 671 | 662
2018-02-02 06:00 | 699 | 692
2018-02-02 06:30 | 769 | 768
2018-02-02 07:00 | 830 | 830
2018-02-02 07:30 | 908 | 908
2018-02-02 08:00 | 931 | 931
2018-02-02 08:30 | 928 | 928
2018-02-02 09:00 | 916 | 916
2018-02-02 09:30 | 939 | 939
2018-02-02 10:00 | 948 | 947
2018-02-02 10:30 | 929 | 928
2018-02-02 11:00 | 931 | 931
2018-02-02 11:30 | 916 | 915
2018-02-02 12:00 | 901 | 900
2018-02-02 12:30 | 916 | 915
2018-02-02 13:00 | 900 | 898
2018-02-02 13:30 | 893 | 891
2018-02-02 14:00 | 896 | 894
2018-02-02 14:30 | 912 | 910
2018-02-02 15:00 | 918 | 915
2018-02-02 15:30 | 914 | 910
2018-02-02 16:00 | 920 | 916
2018-02-02 16:30 | 937 | 933
2018-02-02 17:00 | 944 | 939
2018-02-02 17:30 | 939 | 932
2018-02-02 18:00 | 927 | 920
2018-02-02 18:30 | 909 | 906
2018-02-02 19:00 | 930 | 929
2018-02-02 19:30 | 924 | 924
2018-02-02 20:00 | 920 | 919
2018-02-02 20:30 | 904 | 903
2018-02-02 21:00 | 874 | 874
2018-02-02 21:30 | 836 | 835
2018-02-02 22:00 | 822 | 820
2018-02-02 22:30 | 793 | 790
2018-02-02 23:00 | 783 | 780
2018-02-02 23:30 | 739 | 733
2018-02-03 | 695 | 688
2018-02-03 00:30 | 650 | 638
2018-02-03 01:00 | 624 | 610
2018-02-03 01:30 | 617 | 600
2018-02-03 02:00 | 604 | 585
2018-02-03 02:30 | 598 | 577
2018-02-03 03:00 | 594 | 573
2018-02-03 03:30 | 592 | 570
2018-02-03 04:00 | 592 | 568
2018-02-03 04:30 | 591 | 568
2018-02-03 05:00 | 594 | 574
2018-02-03 05:30 | 605 | 588
2018-02-03 06:00 | 616 | 595
2018-02-03 06:30 | 639 | 621
2018-02-03 07:00 | 664 | 651
2018-02-03 07:30 | 689 | 682
2018-02-03 08:00 | 717 | 713
2018-02-03 08:30 | 748 | 746
2018-02-03 09:00 | 770 | 766
2018-02-03 09:30 | 790 | 788
2018-02-03 10:00 | 793 | 789
2018-02-03 10:30 | 792 | 788
2018-02-03 11:00 | 788 | 784
2018-02-03 11:30 | 784 | 779
2018-02-03 12:00 | 799 | 795
2018-02-03 12:30 | 789 | 783
2018-02-03 13:00 | 798 | 792
2018-02-03 13:30 | 797 | 791
2018-02-03 14:00 | 791 | 784
2018-02-03 14:30 | 792 | 785
2018-02-03 15:00 | 793 | 786
2018-02-03 15:30 | 787 | 779
2018-02-03 16:00 | 787 | 779
2018-02-03 16:30 | 796 | 787
2018-02-03 17:00 | 811 | 803
2018-02-03 17:30 | 808 | 799
2018-02-03 18:00 | 806 | 797
2018-02-03 18:30 | 815 | 806
2018-02-03 19:00 | 836 | 831
2018-02-03 19:30 | 842 | 838
2018-02-03 20:00 | 834 | 829
2018-02-03 20:30 | 822 | 817
2018-02-03 21:00 | 785 | 783
2018-02-03 21:30 | 750 | 746
2018-02-03 22:00 | 741 | 738
2018-02-03 22:30 | 745 | 742
2018-02-03 23:00 | 755 | 750
2018-02-03 23:30 | 721 | 714
2018-02-04 | 679 | 668
2018-02-04 00:30 | 638 | 621
2018-02-04 01:00 | 618 | 598
2018-02-04 01:30 | 606 | 583
2018-02-04 02:00 | 592 | 567
2018-02-04 02:30 | 585 | 559
2018-02-04 03:00 | 581 | 553
2018-02-04 03:30 | 578 | 550
2018-02-04 04:00 | 576 | 549
2018-02-04 04:30 | 573 | 547
2018-02-04 05:00 | 575 | 550
2018-02-04 05:30 | 584 | 558
2018-02-04 06:00 | 592 | 565
2018-02-04 06:30 | 606 | 581
2018-02-04 07:00 | 612 | 590
2018-02-04 07:30 | 624 | 608
2018-02-04 08:00 | 637 | 625
2018-02-04 08:30 | 643 | 635
2018-02-04 09:00 | 663 | 659
2018-02-04 09:30 | 672 | 669
2018-02-04 10:00 | 673 | 672
2018-02-04 10:30 | 667 | 667
2018-02-04 11:00 | 678 | 678
2018-02-04 11:30 | 677 | 677
2018-02-04 12:00 | 665 | 665
2018-02-04 12:30 | 656 | 656
2018-02-04 13:00 | 652 | 651
2018-02-04 13:30 | 649 | 649
2018-02-04 14:00 | 648 | 648
2018-02-04 14:30 | 649 | 649
2018-02-04 15:00 | 662 | 662
2018-02-04 15:30 | 687 | 687
2018-02-04 16:00 | 727 | 727
2018-02-04 16:30 | 758 | 757
2018-02-04 17:00 | 791 | 791
2018-02-04 17:30 | 817 | 816
2018-02-04 18:00 | 835 | 833
2018-02-04 18:30 | 848 | 846
2018-02-04 19:00 | 876 | 874
2018-02-04 19:30 | 882 | 880
2018-02-04 20:00 | 868 | 867
2018-02-04 20:30 | 857 | 854
2018-02-04 21:00 | 828 | 823
2018-02-04 21:30 | 795 | 791
2018-02-04 22:00 | 774 | 769
2018-02-04 22:30 | 758 | 755
2018-02-04 23:00 | 752 | 749
2018-02-04 23:30 | 715 | 709
2018-02-05 | 674 | 665
2018-02-05 00:30 | 635 | 621
2018-02-05 01:00 | 614 | 599
2018-02-05 01:30 | 602 | 586
2018-02-05 02:00 | 597 | 579
2018-02-05 02:30 | 591 | 572
2018-02-05 03:00 | 590 | 569
2018-02-05 03:30 | 588 | 568
2018-02-05 04:00 | 589 | 570
2018-02-05 04:30 | 600 | 584
2018-02-05 05:00 | 609 | 596
2018-02-05 05:30 | 636 | 625
2018-02-05 06:00 | 664 | 658
2018-02-05 06:30 | 719 | 717
2018-02-05 07:00 | 773 | 772
2018-02-05 07:30 | 831 | 830
2018-02-05 08:00 | 850 | 850
2018-02-05 08:30 | 848 | 848
2018-02-05 09:00 | 845 | 844
2018-02-05 09:30 | 859 | 859
2018-02-05 10:00 | 856 | 856
2018-02-05 10:30 | 842 | 842
2018-02-05 11:00 | 843 | 843
2018-02-05 11:30 | 842 | 842
2018-02-05 12:00 | 846 | 846
2018-02-05 12:30 | 852 | 852
2018-02-05 13:00 | 877 | 877
2018-02-05 13:30 | 900 | 900
2018-02-05 14:00 | 908 | 908
2018-02-05 14:30 | 912 | 912
2018-02-05 15:00 | 928 | 928
2018-02-05 15:30 | 956 | 956
2018-02-05 16:00 | 972 | 972
2018-02-05 16:30 | 999 | 999
2018-02-05 17:00 | 1001 | 1000
2018-02-05 17:30 | 998 | 996
2018-02-05 18:00 | 986 | 982
2018-02-05 18:30 | 984 | 977
2018-02-05 19:00 | 1001 | 996
2018-02-05 19:30 | 997 | 992
2018-02-05 20:00 | 986 | 984
2018-02-05 20:30 | 960 | 958
2018-02-05 21:00 | 922 | 922
2018-02-05 21:30 | 887 | 887
2018-02-05 22:00 | 853 | 853
2018-02-05 22:30 | 813 | 812
2018-02-05 23:00 | 792 | 790
2018-02-05 23:30 | 743 | 740
2018-02-06 | 704 | 698
2018-02-06 00:30 | 663 | 654
2018-02-06 01:00 | 643 | 632
2018-02-06 01:30 | 628 | 616
2018-02-06 02:00 | 618 | 605
2018-02-06 02:30 | 605 | 590
2018-02-06 03:00 | 604 | 588
2018-02-06 03:30 | 599 | 582
2018-02-06 04:00 | 600 | 583
2018-02-06 04:30 | 607 | 593
2018-02-06 05:00 | 622 | 611
2018-02-06 05:30 | 652 | 643
2018-02-06 06:00 | 685 | 677
2018-02-06 06:30 | 738 | 736
2018-02-06 07:00 | 789 | 789
2018-02-06 07:30 | 857 | 857
2018-02-06 08:00 | 867 | 867
2018-02-06 08:30 | 873 | 872
2018-02-06 09:00 | 869 | 869
2018-02-06 09:30 | 894 | 894
2018-02-06 10:00 | 884 | 884
2018-02-06 10:30 | 866 | 866
2018-02-06 11:00 | 864 | 864
2018-02-06 11:30 | 871 | 871
2018-02-06 12:00 | 869 | 869
2018-02-06 12:30 | 879 | 879
2018-02-06 13:00 | 891 | 890
2018-02-06 13:30 | 913 | 912
2018-02-06 14:00 | 921 | 920
2018-02-06 14:30 | 929 | 928
2018-02-06 15:00 | 936 | 935
2018-02-06 15:30 | 948 | 947
2018-02-06 16:00 | 974 | 973
2018-02-06 16:30 | 982 | 981
2018-02-06 17:00 | 992 | 992
2018-02-06 17:30 | 1003 | 1003
2018-02-06 18:00 | 992 | 991
2018-02-06 18:30 | 987 | 985
2018-02-06 19:00 | 1011 | 1010
2018-02-06 19:30 | 1005 | 1004
2018-02-06 20:00 | 993 | 993
2018-02-06 20:30 | 967 | 966
2018-02-06 21:00 | 926 | 925
2018-02-06 21:30 | 887 | 885
2018-02-06 22:00 | 852 | 850
2018-02-06 22:30 | 813 | 808
2018-02-06 23:00 | 798 | 792
2018-02-06 23:30 | 746 | 738
2018-02-07 | 697 | 690
2018-02-07 00:30 | 660 | 650
2018-02-07 01:00 | 639 | 626
2018-02-07 01:30 | 625 | 611
2018-02-07 02:00 | 622 | 605
2018-02-07 02:30 | 618 | 599
2018-02-07 03:00 | 613 | 595
2018-02-07 03:30 | 612 | 594
2018-02-07 04:00 | 612 | 594
2018-02-07 04:30 | 623 | 609
2018-02-07 05:00 | 636 | 625
2018-02-07 05:30 | 662 | 653
2018-02-07 06:00 | 692 | 685
2018-02-07 06:30 | 746 | 745
2018-02-07 07:00 | 794 | 794
2018-02-07 07:30 | 853 | 853
2018-02-07 08:00 | 871 | 870
2018-02-07 08:30 | 854 | 854
2018-02-07 09:00 | 851 | 850
2018-02-07 09:30 | 859 | 859
2018-02-07 10:00 | 848 | 846
2018-02-07 10:30 | 855 | 854
2018-02-07 11:00 | 855 | 853
2018-02-07 11:30 | 841 | 840
2018-02-07 12:00 | 839 | 838
2018-02-07 12:30 | 842 | 840
2018-02-07 13:00 | 845 | 844
2018-02-07 13:30 | 809 | 804
2018-02-07 14:00 | 789 | 783
2018-02-07 14:30 | 821 | 815
2018-02-07 15:00 | 824 | 819
2018-02-07 15:30 | 825 | 820
2018-02-07 16:00 | 877 | 873
2018-02-07 16:30 | 933 | 930
2018-02-07 17:00 | 957 | 954
2018-02-07 17:30 | 980 | 975
2018-02-07 18:00 | 940 | 938
2018-02-07 18:30 | 971 | 967
2018-02-07 19:00 | 1005 | 1001
2018-02-07 19:30 | 1018 | 1016
2018-02-07 20:00 | 1006 | 1005
2018-02-07 20:30 | 987 | 986
2018-02-07 21:00 | 940 | 940
2018-02-07 21:30 | 905 | 904
2018-02-07 22:00 | 858 | 857
2018-02-07 22:30 | 816 | 813
2018-02-07 23:00 | 796 | 794
2018-02-07 23:30 | 746 | 743
2018-02-08 | 677 | 669
2018-02-08 00:30 | 621 | 608
2018-02-08 01:00 | 586 | 569
2018-02-08 01:30 | 567 | 548
2018-02-08 02:00 | 555 | 532
2018-02-08 02:30 | 550 | 527
2018-02-08 03:00 | 549 | 525
2018-02-08 03:30 | 550 | 526
2018-02-08 04:00 | 549 | 526
2018-02-08 04:30 | 560 | 539
2018-02-08 05:00 | 636 | 623
2018-02-08 05:30 | 670 | 661
2018-02-08 06:00 | 698 | 690
2018-02-08 06:30 | 760 | 752
2018-02-08 07:00 | 805 | 797
2018-02-08 07:30 | 866 | 862
2018-02-08 08:00 | 882 | 880
2018-02-08 08:30 | 877 | 873
2018-02-08 09:00 | 883 | 880
2018-02-08 09:30 | 905 | 901
2018-02-08 10:00 | 907 | 905
2018-02-08 10:30 | 909 | 908
2018-02-08 11:00 | 882 | 880
2018-02-08 11:30 | 859 | 857
2018-02-08 12:00 | 875 | 872
2018-02-08 12:30 | 852 | 848
2018-02-08 13:00 | 850 | 850
2018-02-08 13:30 | 863 | 863
2018-02-08 14:00 | 876 | 876
2018-02-08 14:30 | 861 | 861
2018-02-08 15:00 | 853 | 852
2018-02-08 15:30 | 866 | 866
2018-02-08 16:00 | 897 | 897
2018-02-08 16:30 | 937 | 936
2018-02-08 17:00 | 965 | 965
2018-02-08 17:30 | 977 | 976
2018-02-08 18:00 | 972 | 970
2018-02-08 18:30 | 972 | 968
2018-02-08 19:00 | 988 | 986
2018-02-08 19:30 | 993 | 992
2018-02-08 20:00 | 984 | 982
2018-02-08 20:30 | 956 | 953
2018-02-08 21:00 | 906 | 903
2018-02-08 21:30 | 865 | 862
2018-02-08 22:00 | 827 | 825
2018-02-08 22:30 | 800 | 796
2018-02-08 23:00 | 788 | 782
2018-02-08 23:30 | 738 | 728
2018-02-09 | 694 | 678
2018-02-09 00:30 | 642 | 633
2018-02-09 01:00 | 618 | 608
2018-02-09 01:30 | 608 | 598
2018-02-09 02:00 | 594 | 582
2018-02-09 02:30 | 585 | 573
2018-02-09 03:00 | 579 | 567
2018-02-09 03:30 | 579 | 566
2018-02-09 04:00 | 579 | 566
2018-02-09 04:30 | 590 | 578
2018-02-09 05:00 | 606 | 595
2018-02-09 05:30 | 629 | 622
2018-02-09 06:00 | 661 | 656
2018-02-09 06:30 | 710 | 710
2018-02-09 07:00 | 717 | 717
2018-02-09 07:30 | 741 | 741
2018-02-09 08:00 | 736 | 736
2018-02-09 08:30 | 737 | 736
2018-02-09 09:00 | 745 | 743
2018-02-09 09:30 | 762 | 761
2018-02-09 10:00 | 767 | 767
2018-02-09 10:30 | 761 | 759
2018-02-09 11:00 | 762 | 760
2018-02-09 11:30 | 756 | 754
2018-02-09 12:00 | 756 | 755
2018-02-09 12:30 | 751 | 750
2018-02-09 13:00 | 762 | 761
2018-02-09 13:30 | 768 | 768
2018-02-09 14:00 | 790 | 790
2018-02-09 14:30 | 826 | 826
2018-02-09 15:00 | 847 | 847
2018-02-09 15:30 | 905 | 905
2018-02-09 16:00 | 987 | 987
2018-02-09 16:30 | 1023 | 1022
2018-02-09 17:00 | 1055 | 1055
2018-02-09 17:30 | 1060 | 1058
2018-02-09 18:00 | 1041 | 1037
2018-02-09 18:30 | 1026 | 1017
2018-02-09 19:00 | 1030 | 1024
2018-02-09 19:30 | 1048 | 1044
2018-02-09 20:00 | 1035 | 1033
2018-02-09 20:30 | 1003 | 1001
2018-02-09 21:00 | 961 | 958
2018-02-09 21:30 | 918 | 913
2018-02-09 22:00 | 887 | 884
2018-02-09 22:30 | 852 | 848
2018-02-09 23:00 | 829 | 825
2018-02-09 23:30 | 771 | 767
2018-02-10 | 719 | 713
2018-02-10 00:30 | 666 | 657
2018-02-10 01:00 | 651 | 640
2018-02-10 01:30 | 638 | 625
2018-02-10 02:00 | 622 | 612
2018-02-10 02:30 | 618 | 607
2018-02-10 03:00 | 606 | 594
2018-02-10 03:30 | 607 | 595
2018-02-10 04:00 | 604 | 592
2018-02-10 04:30 | 604 | 591
2018-02-10 05:00 | 611 | 599
2018-02-10 05:30 | 622 | 611
2018-02-10 06:00 | 621 | 609
2018-02-10 06:30 | 637 | 629
2018-02-10 07:00 | 659 | 654
2018-02-10 07:30 | 703 | 702
2018-02-10 08:00 | 721 | 721
2018-02-10 08:30 | 745 | 745
2018-02-10 09:00 | 743 | 742
2018-02-10 09:30 | 752 | 752
2018-02-10 10:00 | 748 | 747
2018-02-10 10:30 | 756 | 756
2018-02-10 11:00 | 767 | 767
2018-02-10 11:30 | 779 | 778
2018-02-10 12:00 | 799 | 799
2018-02-10 12:30 | 807 | 807
2018-02-10 13:00 | 827 | 826
2018-02-10 13:30 | 849 | 848
2018-02-10 14:00 | 876 | 875
2018-02-10 14:30 | 907 | 907
2018-02-10 15:00 | 941 | 941
2018-02-10 15:30 | 969 | 969
2018-02-10 16:00 | 1027 | 1027
2018-02-10 16:30 | 1060 | 1060
2018-02-10 17:00 | 1067 | 1067
2018-02-10 17:30 | 1069 | 1068
2018-02-10 18:00 | 1055 | 1051
2018-02-10 18:30 | 1031 | 1026
2018-02-10 19:00 | 1035 | 1033
2018-02-10 19:30 | 1031 | 1030
2018-02-10 20:00 | 1010 | 1009
2018-02-10 20:30 | 979 | 978
2018-02-10 21:00 | 925 | 923
2018-02-10 21:30 | 889 | 887
2018-02-10 22:00 | 853 | 851
2018-02-10 22:30 | 839 | 837
2018-02-10 23:00 | 831 | 828
2018-02-10 23:30 | 770 | 764
2018-02-11 | 704 | 698
2018-02-11 00:30 | 640 | 636
2018-02-11 01:00 | 603 | 597
2018-02-11 01:30 | 585 | 576
2018-02-11 02:00 | 571 | 561
2018-02-11 02:30 | 565 | 554
2018-02-11 03:00 | 559 | 546
2018-02-11 03:30 | 550 | 537
2018-02-11 04:00 | 546 | 532
2018-02-11 04:30 | 542 | 527
2018-02-11 05:00 | 547 | 531
2018-02-11 05:30 | 546 | 530
2018-02-11 06:00 | 546 | 526
2018-02-11 06:30 | 560 | 544
2018-02-11 07:00 | 573 | 562
2018-02-11 07:30 | 606 | 601
2018-02-11 08:00 | 634 | 632
2018-02-11 08:30 | 663 | 663
2018-02-11 09:00 | 691 | 690
2018-02-11 09:30 | 726 | 726
2018-02-11 10:00 | 759 | 759
2018-02-11 10:30 | 795 | 794
2018-02-11 11:00 | 830 | 830
2018-02-11 11:30 | 863 | 863
2018-02-11 12:00 | 908 | 908
2018-02-11 12:30 | 949 | 948
2018-02-11 13:00 | 992 | 992
2018-02-11 13:30 | 1048 | 1048
2018-02-11 14:00 | 1086 | 1086
2018-02-11 14:30 | 1141 | 1141
2018-02-11 15:00 | 1180 | 1179
2018-02-11 15:30 | 1220 | 1219
2018-02-11 16:00 | 1269 | 1269
2018-02-11 16:30 | 1327 | 1327
2018-02-11 17:00 | 1349 | 1347
2018-02-11 17:30 | 1341 | 1339
2018-02-11 18:00 | 1343 | 1341
2018-02-11 18:30 | 1224 | 1222
2018-02-11 19:00 | 1128 | 1128
2018-02-11 19:30 | 1074 | 1073
2018-02-11 20:00 | 1035 | 1034
2018-02-11 20:30 | 999 | 998
2018-02-11 21:00 | 940 | 937
2018-02-11 21:30 | 883 | 880
2018-02-11 22:00 | 832 | 828
2018-02-11 22:30 | 810 | 807
2018-02-11 23:00 | 783 | 781
2018-02-11 23:30 | 709 | 705
2018-02-12 | 650 | 647
2018-02-12 00:30 | 613 | 609
2018-02-12 01:00 | 582 | 577
2018-02-12 01:30 | 566 | 559
2018-02-12 02:00 | 554 | 545
2018-02-12 02:30 | 552 | 543
2018-02-12 03:00 | 552 | 542
2018-02-12 03:30 | 546 | 536
2018-02-12 04:00 | 543 | 533
2018-02-12 04:30 | 550 | 542
2018-02-12 05:00 | 573 | 567
2018-02-12 05:30 | 615 | 611
2018-02-12 06:00 | 660 | 659
2018-02-12 06:30 | 749 | 747
2018-02-12 07:00 | 817 | 816
2018-02-12 07:30 | 902 | 900
2018-02-12 08:00 | 941 | 940
2018-02-12 08:30 | 971 | 969
2018-02-12 09:00 | 993 | 991
2018-02-12 09:30 | 1028 | 1027
2018-02-12 10:00 | 1044 | 1044
2018-02-12 10:30 | 1070 | 1070
2018-02-12 11:00 | 1097 | 1097
2018-02-12 11:30 | 1125 | 1123
2018-02-12 12:00 | 1137 | 1135
2018-02-12 12:30 | 1156 | 1156
2018-02-12 13:00 | 1189 | 1189
2018-02-12 13:30 | 1218 | 1218
2018-02-12 14:00 | 1259 | 1259
2018-02-12 14:30 | 1290 | 1290
2018-02-12 15:00 | 1309 | 1309
2018-02-12 15:30 | 1345 | 1345
2018-02-12 16:00 | 1408 | 1407
2018-02-12 16:30 | 1452 | 1452
2018-02-12 17:00 | 1493 | 1493
2018-02-12 17:30 | 1495 | 1495
2018-02-12 18:00 | 1467 | 1466
2018-02-12 18:30 | 1444 | 1442
2018-02-12 19:00 | 1458 | 1458
2018-02-12 19:30 | 1461 | 1461
2018-02-12 20:00 | 1444 | 1444
2018-02-12 20:30 | 1378 | 1377
2018-02-12 21:00 | 1306 | 1305
2018-02-12 21:30 | 1232 | 1231
2018-02-12 22:00 | 1160 | 1159
2018-02-12 22:30 | 1098 | 1096
2018-02-12 23:00 | 1042 | 1040
2018-02-12 23:30 | 974 | 974
2018-02-13 | 914 | 913
2018-02-13 00:30 | 857 | 852
2018-02-13 01:00 | 838 | 832
2018-02-13 01:30 | 817 | 814
2018-02-13 02:00 | 801 | 798
2018-02-13 02:30 | 794 | 791
2018-02-13 03:00 | 786 | 783
2018-02-13 03:30 | 782 | 778
2018-02-13 04:00 | 782 | 779
2018-02-13 04:30 | 791 | 788
2018-02-13 05:00 | 809 | 807
2018-02-13 05:30 | 839 | 839
2018-02-13 06:00 | 872 | 872
2018-02-13 06:30 | 963 | 958
2018-02-13 07:00 | 1025 | 1022
2018-02-13 07:30 | 1124 | 1121
2018-02-13 08:00 | 1165 | 1165
2018-02-13 08:30 | 1209 | 1209
2018-02-13 09:00 | 1238 | 1238
2018-02-13 09:30 | 1200 | 1200
2018-02-13 10:00 | 1181 | 1180
2018-02-13 10:30 | 1201 | 1200
2018-02-13 11:00 | 1222 | 1220
2018-02-13 11:30 | 1230 | 1228
2018-02-13 12:00 | 1250 | 1249
2018-02-13 12:30 | 1267 | 1267
2018-02-13 13:00 | 1290 | 1290
2018-02-13 13:30 | 1308 | 1308
2018-02-13 14:00 | 1327 | 1327
2018-02-13 14:30 | 1352 | 1351
2018-02-13 15:00 | 1390 | 1389
2018-02-13 15:30 | 1416 | 1414
2018-02-13 16:00 | 1476 | 1476
2018-02-13 16:30 | 1528 | 1528
2018-02-13 17:00 | 1532 | 1532
2018-02-13 17:30 | 1511 | 1510
2018-02-13 18:00 | 1473 | 1473
2018-02-13 18:30 | 1457 | 1455
2018-02-13 19:00 | 1475 | 1473
2018-02-13 19:30 | 1406 | 1399
2018-02-13 20:00 | 1333 | 1325
2018-02-13 20:30 | 1244 | 1235
2018-02-13 21:00 | 1143 | 1141
2018-02-13 21:30 | 1080 | 1076
2018-02-13 22:00 | 1038 | 1032
2018-02-13 22:30 | 964 | 964
2018-02-13 23:00 | 928 | 927
2018-02-13 23:30 | 863 | 862
2018-02-14 | 802 | 802
2018-02-14 00:30 | 753 | 753
2018-02-14 01:00 | 725 | 725
2018-02-14 01:30 | 711 | 710
2018-02-14 02:00 | 701 | 699
2018-02-14 02:30 | 692 | 690
2018-02-14 03:00 | 686 | 683
2018-02-14 03:30 | 684 | 680
2018-02-14 04:00 | 685 | 681
2018-02-14 04:30 | 694 | 691
2018-02-14 05:00 | 701 | 699
2018-02-14 05:30 | 731 | 731
2018-02-14 06:00 | 771 | 771
2018-02-14 06:30 | 838 | 837
2018-02-14 07:00 | 901 | 901
2018-02-14 07:30 | 983 | 983
2018-02-14 08:00 | 1032 | 1031
2018-02-14 08:30 | 1060 | 1057
2018-02-14 09:00 | 1078 | 1077
2018-02-14 09:30 | 1107 | 1105
2018-02-14 10:00 | 1122 | 1119
2018-02-14 10:30 | 1145 | 1144
2018-02-14 11:00 | 1164 | 1162
2018-02-14 11:30 | 1182 | 1181
2018-02-14 12:00 | 1209 | 1209
2018-02-14 12:30 | 1231 | 1231
2018-02-14 13:00 | 1266 | 1266
2018-02-14 13:30 | 1302 | 1302
2018-02-14 14:00 | 1346 | 1346
2018-02-14 14:30 | 1387 | 1385
2018-02-14 15:00 | 1402 | 1398
2018-02-14 15:30 | 1443 | 1441
2018-02-14 16:00 | 1494 | 1493
2018-02-14 16:30 | 1549 | 1549
2018-02-14 17:00 | 1569 | 1569
2018-02-14 17:30 | 1570 | 1569
2018-02-14 18:00 | 1532 | 1529
2018-02-14 18:30 | 1482 | 1477
2018-02-14 19:00 | 1485 | 1482
2018-02-14 19:30 | 1465 | 1460
2018-02-14 20:00 | 1411 | 1407
2018-02-14 20:30 | 1393 | 1389
2018-02-14 21:00 | 1375 | 1373
2018-02-14 21:30 | 1291 | 1286
2018-02-14 22:00 | 1221 | 1214
2018-02-14 22:30 | 1107 | 1099
2018-02-14 23:00 | 1056 | 1053
2018-02-14 23:30 | 1003 | 998
2018-02-15 | 947 | 946
2018-02-15 00:30 | 889 | 888
2018-02-15 01:00 | 841 | 841
2018-02-15 01:30 | 818 | 818
2018-02-15 02:00 | 852 | 851
2018-02-15 02:30 | 829 | 829
2018-02-15 03:00 | 799 | 799
2018-02-15 03:30 | 783 | 783
2018-02-15 04:00 | 777 | 777
2018-02-15 04:30 | 787 | 787
2018-02-15 05:00 | 795 | 795
2018-02-15 05:30 | 825 | 825
2018-02-15 06:00 | 865 | 864
2018-02-15 06:30 | 938 | 937
2018-02-15 07:00 | 1006 | 1006
2018-02-15 07:30 | 1104 | 1102
2018-02-15 08:00 | 1149 | 1149
2018-02-15 08:30 | 1182 | 1182
2018-02-15 09:00 | 1205 | 1205
2018-02-15 09:30 | 1245 | 1244
2018-02-15 10:00 | 1270 | 1270
2018-02-15 10:30 | 1277 | 1277
2018-02-15 11:00 | 1281 | 1281
2018-02-15 11:30 | 1289 | 1289
2018-02-15 12:00 | 1309 | 1308
2018-02-15 12:30 | 1334 | 1334
2018-02-15 13:00 | 1369 | 1368
2018-02-15 13:30 | 1398 | 1398
2018-02-15 14:00 | 1429 | 1429
2018-02-15 14:30 | 1451 | 1451
2018-02-15 15:00 | 1462 | 1462
2018-02-15 15:30 | 1492 | 1492
2018-02-15 16:00 | 1542 | 1542
2018-02-15 16:30 | 1531 | 1531
2018-02-15 17:00 | 1504 | 1504
2018-02-15 17:30 | 1479 | 1479
2018-02-15 18:00 | 1477 | 1477
2018-02-15 18:30 | 1440 | 1437
2018-02-15 19:00 | 1443 | 1442
2018-02-15 19:30 | 1435 | 1434
2018-02-15 20:00 | 1403 | 1401
2018-02-15 20:30 | 1406 | 1403
2018-02-15 21:00 | 1370 | 1367
2018-02-15 21:30 | 1264 | 1255
2018-02-15 22:00 | 1189 | 1182
2018-02-15 22:30 | 1065 | 1054
2018-02-15 23:00 | 1026 | 1021
2018-02-15 23:30 | 967 | 960
2018-02-16 | 906 | 904
2018-02-16 00:30 | 839 | 838
2018-02-16 01:00 | 789 | 789
2018-02-16 01:30 | 761 | 761
2018-02-16 02:00 | 789 | 789
2018-02-16 02:30 | 772 | 771
2018-02-16 03:00 | 728 | 727
2018-02-16 03:30 | 712 | 711
2018-02-16 04:00 | 702 | 701
2018-02-16 04:30 | 711 | 710
2018-02-16 05:00 | 736 | 736
2018-02-16 05:30 | 793 | 792
2018-02-16 06:00 | 822 | 819
2018-02-16 06:30 | 897 | 896
2018-02-16 07:00 | 982 | 980
2018-02-16 07:30 | 1077 | 1076
2018-02-16 08:00 | 1133 | 1132
2018-02-16 08:30 | 1170 | 1170
2018-02-16 09:00 | 1199 | 1197
2018-02-16 09:30 | 1217 | 1216
2018-02-16 10:00 | 1214 | 1213
2018-02-16 10:30 | 1221 | 1221
2018-02-16 11:00 | 1242 | 1242
2018-02-16 11:30 | 1269 | 1269
2018-02-16 12:00 | 1284 | 1284
2018-02-16 12:30 | 1287 | 1286
2018-02-16 13:00 | 1309 | 1309
2018-02-16 13:30 | 1332 | 1331
2018-02-16 14:00 | 1350 | 1349
2018-02-16 14:30 | 1376 | 1375
2018-02-16 15:00 | 1438 | 1438
2018-02-16 15:30 | 1488 | 1488
2018-02-16 16:00 | 1501 | 1501
2018-02-16 16:30 | 1491 | 1490
2018-02-16 17:00 | 1486 | 1484
2018-02-16 17:30 | 1417 | 1416
2018-02-16 18:00 | 1353 | 1347
2018-02-16 18:30 | 1289 | 1280
2018-02-16 19:00 | 1277 | 1271
2018-02-16 19:30 | 1260 | 1254
2018-02-16 20:00 | 1240 | 1237
2018-02-16 20:30 | 1205 | 1201
2018-02-16 21:00 | 1150 | 1150
2018-02-16 21:30 | 1097 | 1095
2018-02-16 22:00 | 1065 | 1063
2018-02-16 22:30 | 1020 | 1015
2018-02-16 23:00 | 983 | 979
2018-02-16 23:30 | 920 | 919
2018-02-17 | 869 | 867
2018-02-17 00:30 | 825 | 822
2018-02-17 01:00 | 796 | 792
2018-02-17 01:30 | 772 | 768
2018-02-17 02:00 | 748 | 746
2018-02-17 02:30 | 737 | 735
2018-02-17 03:00 | 731 | 728
2018-02-17 03:30 | 730 | 726
2018-02-17 04:00 | 725 | 722
2018-02-17 04:30 | 719 | 715
2018-02-17 05:00 | 722 | 719
2018-02-17 05:30 | 734 | 731
2018-02-17 06:00 | 730 | 728
2018-02-17 06:30 | 764 | 763
2018-02-17 07:00 | 792 | 792
2018-02-17 07:30 | 835 | 835
2018-02-17 08:00 | 879 | 878
2018-02-17 08:30 | 923 | 923
2018-02-17 09:00 | 947 | 946
2018-02-17 09:30 | 960 | 960
2018-02-17 10:00 | 962 | 961
2018-02-17 10:30 | 969 | 969
2018-02-17 11:00 | 979 | 978
2018-02-17 11:30 | 976 | 976
2018-02-17 12:00 | 977 | 977
2018-02-17 12:30 | 981 | 981
2018-02-17 13:00 | 992 | 992
2018-02-17 13:30 | 1004 | 1003
2018-02-17 14:00 | 1015 | 1014
2018-02-17 14:30 | 1028 | 1028
2018-02-17 15:00 | 1046 | 1046
2018-02-17 15:30 | 1091 | 1090
2018-02-17 16:00 | 1129 | 1129
2018-02-17 16:30 | 1148 | 1148
2018-02-17 17:00 | 1167 | 1167
2018-02-17 17:30 | 1157 | 1157
2018-02-17 18:00 | 1149 | 1148
2018-02-17 18:30 | 1142 | 1138
2018-02-17 19:00 | 1148 | 1146
2018-02-17 19:30 | 1124 | 1122
2018-02-17 20:00 | 1110 | 1107
2018-02-17 20:30 | 1074 | 1071
2018-02-17 21:00 | 1035 | 1035
2018-02-17 21:30 | 998 | 998
2018-02-17 22:00 | 968 | 967
2018-02-17 22:30 | 942 | 942
2018-02-17 23:00 | 926 | 926
2018-02-17 23:30 | 881 | 879
2018-02-18 | 838 | 833
2018-02-18 00:30 | 789 | 779
2018-02-18 01:00 | 756 | 748
2018-02-18 01:30 | 726 | 719
2018-02-18 02:00 | 709 | 701
2018-02-18 02:30 | 694 | 687
2018-02-18 03:00 | 681 | 673
2018-02-18 03:30 | 674 | 665
2018-02-18 04:00 | 665 | 655
2018-02-18 04:30 | 661 | 651
2018-02-18 05:00 | 654 | 643
2018-02-18 05:30 | 655 | 645
2018-02-18 06:00 | 651 | 637
2018-02-18 06:30 | 663 | 653
2018-02-18 07:00 | 682 | 676
2018-02-18 07:30 | 705 | 702
2018-02-18 08:00 | 729 | 728
2018-02-18 08:30 | 767 | 767
2018-02-18 09:00 | 806 | 806
2018-02-18 09:30 | 837 | 837
2018-02-18 10:00 | 867 | 867
2018-02-18 10:30 | 873 | 873
2018-02-18 11:00 | 887 | 886
2018-02-18 11:30 | 904 | 903
2018-02-18 12:00 | 917 | 917
2018-02-18 12:30 | 927 | 926
2018-02-18 13:00 | 939 | 938
2018-02-18 13:30 | 950 | 949
2018-02-18 14:00 | 970 | 970
2018-02-18 14:30 | 991 | 990
2018-02-18 15:00 | 1021 | 1021
2018-02-18 15:30 | 1079 | 1078
2018-02-18 16:00 | 1115 | 1114
2018-02-18 16:30 | 1137 | 1136
2018-02-18 17:00 | 1149 | 1149
2018-02-18 17:30 | 1149 | 1148
2018-02-18 18:00 | 1145 | 1142
2018-02-18 18:30 | 1135 | 1130
2018-02-18 19:00 | 1151 | 1148
2018-02-18 19:30 | 1124 | 1120
2018-02-18 20:00 | 1093 | 1089
2018-02-18 20:30 | 1054 | 1047
2018-02-18 21:00 | 1001 | 998
2018-02-18 21:30 | 956 | 952
2018-02-18 22:00 | 920 | 913
2018-02-18 22:30 | 892 | 887
2018-02-18 23:00 | 864 | 861
2018-02-18 23:30 | 821 | 814
2018-02-19 | 768 | 763
2018-02-19 00:30 | 717 | 713
2018-02-19 01:00 | 679 | 672
2018-02-19 01:30 | 656 | 649
2018-02-19 02:00 | 638 | 630
2018-02-19 02:30 | 632 | 623
2018-02-19 03:00 | 630 | 620
2018-02-19 03:30 | 630 | 619
2018-02-19 04:00 | 629 | 618
2018-02-19 04:30 | 636 | 626
2018-02-19 05:00 | 652 | 645
2018-02-19 05:30 | 691 | 688
2018-02-19 06:00 | 734 | 732
2018-02-19 06:30 | 807 | 805
2018-02-19 07:00 | 858 | 857
2018-02-19 07:30 | 927 | 927
2018-02-19 08:00 | 968 | 964
2018-02-19 08:30 | 974 | 969
2018-02-19 09:00 | 985 | 982
2018-02-19 09:30 | 993 | 990
2018-02-19 10:00 | 1007 | 1002
2018-02-19 10:30 | 1011 | 1007
2018-02-19 11:00 | 1020 | 1017
2018-02-19 11:30 | 1027 | 1025
2018-02-19 12:00 | 1010 | 1009
2018-02-19 12:30 | 1013 | 1012
2018-02-19 13:00 | 1034 | 1033
2018-02-19 13:30 | 1057 | 1057
2018-02-19 14:00 | 1089 | 1089
2018-02-19 14:30 | 1121 | 1121
2018-02-19 15:00 | 1137 | 1135
2018-02-19 15:30 | 1170 | 1170
2018-02-19 16:00 | 1214 | 1213
2018-02-19 16:30 | 1249 | 1248
2018-02-19 17:00 | 1277 | 1275
2018-02-19 17:30 | 1280 | 1275
2018-02-19 18:00 | 1247 | 1236
2018-02-19 18:30 | 1205 | 1199
2018-02-19 19:00 | 1216 | 1215
2018-02-19 19:30 | 1195 | 1193
2018-02-19 20:00 | 1181 | 1178
2018-02-19 20:30 | 1136 | 1133
2018-02-19 21:00 | 1069 | 1068
2018-02-19 21:30 | 1024 | 1023
2018-02-19 22:00 | 978 | 977
2018-02-19 22:30 | 929 | 927
2018-02-19 23:00 | 892 | 890
2018-02-19 23:30 | 828 | 822
2018-02-20 | 783 | 773
2018-02-20 00:30 | 733 | 729
2018-02-20 01:00 | 711 | 708
2018-02-20 01:30 | 695 | 691
2018-02-20 02:00 | 684 | 678
2018-02-20 02:30 | 675 | 669
2018-02-20 03:00 | 672 | 666
2018-02-20 03:30 | 670 | 664
2018-02-20 04:00 | 672 | 665
2018-02-20 04:30 | 683 | 677
2018-02-20 05:00 | 703 | 698
2018-02-20 05:30 | 744 | 740
2018-02-20 06:00 | 759 | 747
2018-02-20 06:30 | 826 | 823
2018-02-20 07:00 | 871 | 871
2018-02-20 07:30 | 951 | 950
2018-02-20 08:00 | 984 | 984
2018-02-20 08:30 | 1000 | 1000
2018-02-20 09:00 | 1008 | 1007
2018-02-20 09:30 | 999 | 999
2018-02-20 10:00 | 998 | 998
2018-02-20 10:30 | 1016 | 1016
2018-02-20 11:00 | 1009 | 1009
2018-02-20 11:30 | 993 | 993
2018-02-20 12:00 | 993 | 993
2018-02-20 12:30 | 988 | 987
2018-02-20 13:00 | 998 | 998
2018-02-20 13:30 | 1004 | 1004
2018-02-20 14:00 | 1041 | 1040
2018-02-20 14:30 | 1037 | 1037
2018-02-20 15:00 | 1056 | 1056
2018-02-20 15:30 | 1071 | 1071
2018-02-20 16:00 | 1093 | 1093
2018-02-20 16:30 | 1115 | 1115
2018-02-20 17:00 | 1132 | 1132
2018-02-20 17:30 | 1138 | 1138
2018-02-20 18:00 | 1115 | 1115
2018-02-20 18:30 | 1104 | 1104
2018-02-20 19:00 | 1122 | 1122
2018-02-20 19:30 | 1107 | 1107
2018-02-20 20:00 | 1091 | 1090
2018-02-20 20:30 | 1060 | 1060
2018-02-20 21:00 | 1011 | 1010
2018-02-20 21:30 | 975 | 973
2018-02-20 22:00 | 940 | 935
2018-02-20 22:30 | 895 | 885
2018-02-20 23:00 | 863 | 858
2018-02-20 23:30 | 807 | 806
2018-02-21 | 757 | 755
2018-02-21 00:30 | 723 | 721
2018-02-21 01:00 | 700 | 697
2018-02-21 01:30 | 679 | 674
2018-02-21 02:00 | 666 | 660
2018-02-21 02:30 | 661 | 654
2018-02-21 03:00 | 664 | 657
2018-02-21 03:30 | 667 | 660
2018-02-21 04:00 | 672 | 666
2018-02-21 04:30 | 680 | 674
2018-02-21 05:00 | 691 | 687
2018-02-21 05:30 | 727 | 725
2018-02-21 06:00 | 759 | 758
2018-02-21 06:30 | 826 | 826
2018-02-21 07:00 | 889 | 889
2018-02-21 07:30 | 957 | 957
2018-02-21 08:00 | 982 | 981
2018-02-21 08:30 | 992 | 992
2018-02-21 09:00 | 1018 | 1018
2018-02-21 09:30 | 1025 | 1025
2018-02-21 10:00 | 1019 | 1018
2018-02-21 10:30 | 996 | 995
2018-02-21 11:00 | 983 | 982
2018-02-21 11:30 | 965 | 964
2018-02-21 12:00 | 963 | 962
2018-02-21 12:30 | 971 | 969
2018-02-21 13:00 | 955 | 953
2018-02-21 13:30 | 930 | 928
2018-02-21 14:00 | 943 | 943
2018-02-21 14:30 | 972 | 972
2018-02-21 15:00 | 981 | 980
2018-02-21 15:30 | 986 | 985
2018-02-21 16:00 | 997 | 996
2018-02-21 16:30 | 1014 | 1012
2018-02-21 17:00 | 1024 | 1023
2018-02-21 17:30 | 1023 | 1020
2018-02-21 18:00 | 1004 | 1000
2018-02-21 18:30 | 985 | 983
2018-02-21 19:00 | 1008 | 1008
2018-02-21 19:30 | 1002 | 1001
2018-02-21 20:00 | 993 | 992
2018-02-21 20:30 | 959 | 957
2018-02-21 21:00 | 921 | 921
2018-02-21 21:30 | 895 | 893
2018-02-21 22:00 | 867 | 865
2018-02-21 22:30 | 821 | 821
2018-02-21 23:00 | 803 | 802
2018-02-21 23:30 | 755 | 754
2018-02-22 | 708 | 704
2018-02-22 00:30 | 670 | 662
2018-02-22 01:00 | 636 | 626
2018-02-22 01:30 | 620 | 608
2018-02-22 02:00 | 606 | 593
2018-02-22 02:30 | 603 | 590
2018-02-22 03:00 | 606 | 593
2018-02-22 03:30 | 611 | 598
2018-02-22 04:00 | 614 | 601
2018-02-22 04:30 | 623 | 611
2018-02-22 05:00 | 640 | 630
2018-02-22 05:30 | 682 | 678
2018-02-22 06:00 | 713 | 710
2018-02-22 06:30 | 778 | 777
2018-02-22 07:00 | 835 | 831
2018-02-22 07:30 | 915 | 913
2018-02-22 08:00 | 930 | 930
2018-02-22 08:30 | 937 | 937
2018-02-22 09:00 | 945 | 945
2018-02-22 09:30 | 954 | 953
2018-02-22 10:00 | 944 | 944
2018-02-22 10:30 | 947 | 947
2018-02-22 11:00 | 960 | 960
2018-02-22 11:30 | 947 | 947
2018-02-22 12:00 | 946 | 946
2018-02-22 12:30 | 953 | 952
2018-02-22 13:00 | 956 | 955
2018-02-22 13:30 | 969 | 969
2018-02-22 14:00 | 967 | 966
2018-02-22 14:30 | 970 | 969
2018-02-22 15:00 | 960 | 959
2018-02-22 15:30 | 968 | 966
2018-02-22 16:00 | 987 | 985
2018-02-22 16:30 | 995 | 993
2018-02-22 17:00 | 1008 | 1005
2018-02-22 17:30 | 1010 | 1006
2018-02-22 18:00 | 1013 | 1010
2018-02-22 18:30 | 1013 | 1008
2018-02-22 19:00 | 1030 | 1027
2018-02-22 19:30 | 1017 | 1012
2018-02-22 20:00 | 1004 | 999
2018-02-22 20:30 | 985 | 984
2018-02-22 21:00 | 948 | 945
2018-02-22 21:30 | 905 | 901
2018-02-22 22:00 | 873 | 869
2018-02-22 22:30 | 844 | 841
2018-02-22 23:00 | 823 | 819
2018-02-22 23:30 | 770 | 768
2018-02-23 | 725 | 720
2018-02-23 00:30 | 688 | 679
2018-02-23 01:00 | 665 | 654
2018-02-23 01:30 | 654 | 642
2018-02-23 02:00 | 640 | 626
2018-02-23 02:30 | 635 | 620
2018-02-23 03:00 | 631 | 617
2018-02-23 03:30 | 632 | 617
2018-02-23 04:00 | 636 | 623
2018-02-23 04:30 | 648 | 636
2018-02-23 05:00 | 667 | 658
2018-02-23 05:30 | 705 | 700
2018-02-23 06:00 | 740 | 738
2018-02-23 06:30 | 815 | 813
2018-02-23 07:00 | 887 | 886
2018-02-23 07:30 | 967 | 965
2018-02-23 08:00 | 1008 | 1008
2018-02-23 08:30 | 1027 | 1026
2018-02-23 09:00 | 1041 | 1040
2018-02-23 09:30 | 1052 | 1051
2018-02-23 10:00 | 1075 | 1074
2018-02-23 10:30 | 1081 | 1078
2018-02-23 11:00 | 1071 | 1068
2018-02-23 11:30 | 1072 | 1068
2018-02-23 12:00 | 1072 | 1068
2018-02-23 12:30 | 1066 | 1061
2018-02-23 13:00 | 1057 | 1057
2018-02-23 13:30 | 1047 | 1046
2018-02-23 14:00 | 1044 | 1043
2018-02-23 14:30 | 1042 | 1040
2018-02-23 15:00 | 1028 | 1026
2018-02-23 15:30 | 1022 | 1019
2018-02-23 16:00 | 1030 | 1026
2018-02-23 16:30 | 1038 | 1035
2018-02-23 17:00 | 1045 | 1041
2018-02-23 17:30 | 1039 | 1034
2018-02-23 18:00 | 1018 | 1012
2018-02-23 18:30 | 1005 | 1000
2018-02-23 19:00 | 1022 | 1021
2018-02-23 19:30 | 1006 | 1004
2018-02-23 20:00 | 990 | 990
2018-02-23 20:30 | 973 | 973
2018-02-23 21:00 | 940 | 939
2018-02-23 21:30 | 912 | 910
2018-02-23 22:00 | 894 | 891
2018-02-23 22:30 | 858 | 855
2018-02-23 23:00 | 841 | 839
2018-02-23 23:30 | 796 | 792
2018-02-24 | 750 | 745
2018-02-24 00:30 | 699 | 694
2018-02-24 01:00 | 680 | 673
2018-02-24 01:30 | 672 | 663
2018-02-24 02:00 | 656 | 645
2018-02-24 02:30 | 651 | 639
2018-02-24 03:00 | 647 | 633
2018-02-24 03:30 | 641 | 627
2018-02-24 04:00 | 639 | 626
2018-02-24 04:30 | 645 | 631
2018-02-24 05:00 | 650 | 637
2018-02-24 05:30 | 666 | 656
2018-02-24 06:00 | 676 | 668
2018-02-24 06:30 | 693 | 687
2018-02-24 07:00 | 717 | 713
2018-02-24 07:30 | 759 | 758
2018-02-24 08:00 | 799 | 799
2018-02-24 08:30 | 828 | 828
2018-02-24 09:00 | 850 | 847
2018-02-24 09:30 | 853 | 851
2018-02-24 10:00 | 866 | 865
2018-02-24 10:30 | 884 | 882
2018-02-24 11:00 | 888 | 883
2018-02-24 11:30 | 870 | 865
2018-02-24 12:00 | 869 | 864
2018-02-24 12:30 | 845 | 838
2018-02-24 13:00 | 843 | 836
2018-02-24 13:30 | 857 | 851
2018-02-24 14:00 | 864 | 858
2018-02-24 14:30 | 864 | 858
2018-02-24 15:00 | 886 | 881
2018-02-24 15:30 | 911 | 906
2018-02-24 16:00 | 934 | 930
2018-02-24 16:30 | 951 | 946
2018-02-24 17:00 | 969 | 959
2018-02-24 17:30 | 976 | 967
2018-02-24 18:00 | 976 | 965
2018-02-24 18:30 | 975 | 964
2018-02-24 19:00 | 996 | 990
2018-02-24 19:30 | 988 | 980
2018-02-24 20:00 | 976 | 966
2018-02-24 20:30 | 964 | 953
2018-02-24 21:00 | 928 | 922
2018-02-24 21:30 | 894 | 891
2018-02-24 22:00 | 874 | 874
2018-02-24 22:30 | 858 | 857
2018-02-24 23:00 | 859 | 858
2018-02-24 23:30 | 811 | 807
2018-02-25 | 767 | 761
2018-02-25 00:30 | 718 | 710
2018-02-25 01:00 | 689 | 684
2018-02-25 01:30 | 670 | 663
2018-02-25 02:00 | 662 | 653
2018-02-25 02:30 | 643 | 633
2018-02-25 03:00 | 634 | 624
2018-02-25 03:30 | 626 | 613
2018-02-25 04:00 | 623 | 610
2018-02-25 04:30 | 623 | 610
2018-02-25 05:00 | 624 | 610
2018-02-25 05:30 | 635 | 623
2018-02-25 06:00 | 638 | 625
2018-02-25 06:30 | 664 | 652
2018-02-25 07:00 | 671 | 663
2018-02-25 07:30 | 699 | 696
2018-02-25 08:00 | 728 | 727
2018-02-25 08:30 | 765 | 765
2018-02-25 09:00 | 792 | 792
2018-02-25 09:30 | 825 | 825
2018-02-25 10:00 | 839 | 839
2018-02-25 10:30 | 859 | 859
2018-02-25 11:00 | 885 | 883
2018-02-25 11:30 | 902 | 901
2018-02-25 12:00 | 938 | 932
2018-02-25 12:30 | 949 | 944
2018-02-25 13:00 | 966 | 963
2018-02-25 13:30 | 974 | 972
2018-02-25 14:00 | 998 | 994
2018-02-25 14:30 | 1009 | 1005
2018-02-25 15:00 | 1027 | 1025
2018-02-25 15:30 | 1038 | 1037
2018-02-25 16:00 | 1114 | 1114
2018-02-25 16:30 | 1154 | 1153
2018-02-25 17:00 | 1177 | 1175
2018-02-25 17:30 | 1163 | 1161
2018-02-25 18:00 | 1138 | 1133
2018-02-25 18:30 | 1128 | 1123
2018-02-25 19:00 | 1150 | 1148
2018-02-25 19:30 | 1136 | 1133
2018-02-25 20:00 | 1121 | 1117
2018-02-25 20:30 | 1094 | 1085
2018-02-25 21:00 | 1031 | 1021
2018-02-25 21:30 | 974 | 966
2018-02-25 22:00 | 931 | 925
2018-02-25 22:30 | 897 | 894
2018-02-25 23:00 | 877 | 872
2018-02-25 23:30 | 820 | 819
2018-02-26 | 776 | 776
2018-02-26 00:30 | 733 | 731
2018-02-26 01:00 | 709 | 706
2018-02-26 01:30 | 701 | 697
2018-02-26 02:00 | 687 | 682
2018-02-26 02:30 | 682 | 676
2018-02-26 03:00 | 672 | 666
2018-02-26 03:30 | 670 | 663
2018-02-26 04:00 | 669 | 662
2018-02-26 04:30 | 672 | 667
2018-02-26 05:00 | 687 | 684
2018-02-26 05:30 | 719 | 718
2018-02-26 06:00 | 760 | 759
2018-02-26 06:30 | 835 | 834
2018-02-26 07:00 | 902 | 901
2018-02-26 07:30 | 984 | 984
2018-02-26 08:00 | 1028 | 1028
2018-02-26 08:30 | 1044 | 1044
2018-02-26 09:00 | 1065 | 1064
2018-02-26 09:30 | 1090 | 1089
2018-02-26 10:00 | 1108 | 1108
2018-02-26 10:30 | 1119 | 1119
2018-02-26 11:00 | 1142 | 1141
2018-02-26 11:30 | 1154 | 1152
2018-02-26 12:00 | 1171 | 1169
2018-02-26 12:30 | 1182 | 1181
2018-02-26 13:00 | 1207 | 1205
2018-02-26 13:30 | 1242 | 1240
2018-02-26 14:00 | 1275 | 1274
2018-02-26 14:30 | 1296 | 1295
2018-02-26 15:00 | 1336 | 1335
2018-02-26 15:30 | 1356 | 1356
2018-02-26 16:00 | 1387 | 1387
2018-02-26 16:30 | 1438 | 1438
2018-02-26 17:00 | 1480 | 1480
2018-02-26 17:30 | 1485 | 1483
2018-02-26 18:00 | 1466 | 1458
2018-02-26 18:30 | 1421 | 1409
2018-02-26 19:00 | 1398 | 1383
2018-02-26 19:30 | 1330 | 1319
2018-02-26 20:00 | 1256 | 1246
2018-02-26 20:30 | 1166 | 1161
2018-02-26 21:00 | 1087 | 1082
2018-02-26 21:30 | 1027 | 1022
2018-02-26 22:00 | 977 | 974
2018-02-26 22:30 | 930 | 928
2018-02-26 23:00 | 893 | 889
2018-02-26 23:30 | 831 | 823
2018-02-27 | 783 | 769
2018-02-27 00:30 | 738 | 726
2018-02-27 01:00 | 699 | 694
2018-02-27 01:30 | 675 | 669
2018-02-27 02:00 | 658 | 651
2018-02-27 02:30 | 658 | 649
2018-02-27 03:00 | 655 | 646
2018-02-27 03:30 | 652 | 642
2018-02-27 04:00 | 649 | 640
2018-02-27 04:30 | 652 | 643
2018-02-27 05:00 | 678 | 671
2018-02-27 05:30 | 719 | 715
2018-02-27 06:00 | 756 | 752
2018-02-27 06:30 | 820 | 819
2018-02-27 07:00 | 892 | 892
2018-02-27 07:30 | 953 | 953
2018-02-27 08:00 | 979 | 978
2018-02-27 08:30 | 992 | 990
2018-02-27 09:00 | 996 | 994
2018-02-27 09:30 | 1003 | 1002
2018-02-27 10:00 | 994 | 992
2018-02-27 10:30 | 973 | 971
2018-02-27 11:00 | 962 | 961
2018-02-27 11:30 | 976 | 975
2018-02-27 12:00 | 961 | 960
2018-02-27 12:30 | 948 | 946
2018-02-27 13:00 | 951 | 950
2018-02-27 13:30 | 964 | 964
2018-02-27 14:00 | 991 | 991
2018-02-27 14:30 | 1007 | 1007
2018-02-27 15:00 | 1018 | 1018
2018-02-27 15:30 | 1021 | 1021
2018-02-27 16:00 | 1059 | 1059
2018-02-27 16:30 | 1074 | 1073
2018-02-27 17:00 | 1075 | 1074
2018-02-27 17:30 | 1071 | 1069
2018-02-27 18:00 | 1065 | 1060
2018-02-27 18:30 | 1059 | 1053
2018-02-27 19:00 | 1082 | 1078
2018-02-27 19:30 | 1063 | 1057
2018-02-27 20:00 | 1041 | 1039
2018-02-27 20:30 | 1015 | 1013
2018-02-27 21:00 | 962 | 962
2018-02-27 21:30 | 921 | 921
2018-02-27 22:00 | 891 | 891
2018-02-27 22:30 | 852 | 851
2018-02-27 23:00 | 830 | 829
2018-02-27 23:30 | 775 | 774
2018-02-28 | 726 | 722
2018-02-28 00:30 | 689 | 682
2018-02-28 01:00 | 657 | 647
2018-02-28 01:30 | 638 | 626
2018-02-28 02:00 | 630 | 616
2018-02-28 02:30 | 623 | 606
2018-02-28 03:00 | 623 | 605
2018-02-28 03:30 | 622 | 605
2018-02-28 04:00 | 624 | 606
2018-02-28 04:30 | 639 | 623
2018-02-28 05:00 | 647 | 635
2018-02-28 05:30 | 677 | 670
2018-02-28 06:00 | 710 | 705
2018-02-28 06:30 | 766 | 764
2018-02-28 07:00 | 840 | 839
2018-02-28 07:30 | 891 | 890
2018-02-28 08:00 | 893 | 893
2018-02-28 08:30 | 908 | 906
2018-02-28 09:00 | 896 | 895
2018-02-28 09:30 | 898 | 898
2018-02-28 10:00 | 913 | 913
2018-02-28 10:30 | 921 | 921
2018-02-28 11:00 | 930 | 930
2018-02-28 11:30 | 929 | 929
2018-02-28 12:00 | 938 | 938
2018-02-28 12:30 | 942 | 941
2018-02-28 13:00 | 943 | 942
2018-02-28 13:30 | 949 | 948
2018-02-28 14:00 | 971 | 970
2018-02-28 14:30 | 994 | 994
2018-02-28 15:00 | 1007 | 1006
2018-02-28 15:30 | 1028 | 1028
2018-02-28 16:00 | 1058 | 1058
2018-02-28 16:30 | 1093 | 1091
2018-02-28 17:00 | 1125 | 1123
2018-02-28 17:30 | 1125 | 1122
2018-02-28 18:00 | 1113 | 1105
2018-02-28 18:30 | 1094 | 1087
2018-02-28 19:00 | 1106 | 1105
2018-02-28 19:30 | 1093 | 1091
2018-02-28 20:00 | 1080 | 1078
2018-02-28 20:30 | 1042 | 1039
2018-02-28 21:00 | 996 | 995
2018-02-28 21:30 | 959 | 956
2018-02-28 22:00 | 926 | 921
2018-02-28 22:30 | 876 | 876
2018-02-28 23:00 | 847 | 845
2018-02-28 23:30 | 784 | 780
2018-03-01 | 734 | 728
2018-03-01 00:30 | 685 | 679
2018-03-01 01:00 | 650 | 640
2018-03-01 01:30 | 632 | 621
2018-03-01 02:00 | 631 | 620
2018-03-01 02:30 | 642 | 630
2018-03-01 03:00 | 636 | 623
2018-03-01 03:30 | 636 | 623
2018-03-01 04:00 | 634 | 622
2018-03-01 04:30 | 643 | 632
2018-03-01 05:00 | 661 | 652
2018-03-01 05:30 | 691 | 687
2018-03-01 06:00 | 704 | 700
2018-03-01 06:30 | 761 | 760
2018-03-01 07:00 | 837 | 836
2018-03-01 07:30 | 895 | 895
2018-03-01 08:00 | 908 | 908
2018-03-01 08:30 | 923 | 923
2018-03-01 09:00 | 929 | 928
2018-03-01 09:30 | 942 | 942
2018-03-01 10:00 | 961 | 961
2018-03-01 10:30 | 979 | 979
2018-03-01 11:00 | 1012 | 1011
2018-03-01 11:30 | 1038 | 1038
2018-03-01 12:00 | 1085 | 1085
2018-03-01 12:30 | 1122 | 1122
2018-03-01 13:00 | 1168 | 1168
2018-03-01 13:30 | 1215 | 1215
2018-03-01 14:00 | 1265 | 1265
2018-03-01 14:30 | 1313 | 1312
2018-03-01 15:00 | 1350 | 1350
2018-03-01 15:30 | 1395 | 1395
2018-03-01 16:00 | 1442 | 1442
2018-03-01 16:30 | 1479 | 1479
2018-03-01 17:00 | 1499 | 1498
2018-03-01 17:30 | 1474 | 1472
2018-03-01 18:00 | 1463 | 1458
2018-03-01 18:30 | 1430 | 1427
2018-03-01 19:00 | 1451 | 1451
2018-03-01 19:30 | 1426 | 1425
2018-03-01 20:00 | 1396 | 1394
2018-03-01 20:30 | 1347 | 1342
2018-03-01 21:00 | 1253 | 1252
2018-03-01 21:30 | 1171 | 1168
2018-03-01 22:00 | 1093 | 1090
2018-03-01 22:30 | 1040 | 1038
2018-03-01 23:00 | 988 | 984
2018-03-01 23:30 | 910 | 904
2018-03-02 | 848 | 846
2018-03-02 00:30 | 797 | 796
2018-03-02 01:00 | 768 | 766
2018-03-02 01:30 | 743 | 741
2018-03-02 02:00 | 730 | 726
2018-03-02 02:30 | 719 | 715
2018-03-02 03:00 | 707 | 706
2018-03-02 03:30 | 705 | 703
2018-03-02 04:00 | 704 | 702
2018-03-02 04:30 | 712 | 710
2018-03-02 05:00 | 724 | 723
2018-03-02 05:30 | 758 | 758
2018-03-02 06:00 | 789 | 788
2018-03-02 06:30 | 850 | 849
2018-03-02 07:00 | 921 | 920
2018-03-02 07:30 | 990 | 990
2018-03-02 08:00 | 1016 | 1015
2018-03-02 08:30 | 1031 | 1031
2018-03-02 09:00 | 1049 | 1049
2018-03-02 09:30 | 1073 | 1073
2018-03-02 10:00 | 1079 | 1079
2018-03-02 10:30 | 1100 | 1099
2018-03-02 11:00 | 1133 | 1132
2018-03-02 11:30 | 1148 | 1147
2018-03-02 12:00 | 1141 | 1141
2018-03-02 12:30 | 1131 | 1131
2018-03-02 13:00 | 1129 | 1129
2018-03-02 13:30 | 1147 | 1147
2018-03-02 14:00 | 1148 | 1148
2018-03-02 14:30 | 1138 | 1138
2018-03-02 15:00 | 1128 | 1127
2018-03-02 15:30 | 1111 | 1110
2018-03-02 16:00 | 1148 | 1147
2018-03-02 16:30 | 1159 | 1158
2018-03-02 17:00 | 1153 | 1152
2018-03-02 17:30 | 1139 | 1135
2018-03-02 18:00 | 1110 | 1108
2018-03-02 18:30 | 1097 | 1095
2018-03-02 19:00 | 1107 | 1106
2018-03-02 19:30 | 1094 | 1092
2018-03-02 20:00 | 1075 | 1073
2018-03-02 20:30 | 1049 | 1046
2018-03-02 21:00 | 1014 | 1012
2018-03-02 21:30 | 984 | 983
2018-03-02 22:00 | 966 | 964
2018-03-02 22:30 | 937 | 932
2018-03-02 23:00 | 903 | 899
2018-03-02 23:30 | 839 | 838
2018-03-03 | 792 | 790
2018-03-03 00:30 | 743 | 741
2018-03-03 01:00 | 722 | 719
2018-03-03 01:30 | 709 | 706
2018-03-03 02:00 | 695 | 691
2018-03-03 02:30 | 686 | 681
2018-03-03 03:00 | 682 | 676
2018-03-03 03:30 | 677 | 671
2018-03-03 04:00 | 673 | 666
2018-03-03 04:30 | 672 | 665
2018-03-03 05:00 | 680 | 673
2018-03-03 05:30 | 690 | 685
2018-03-03 06:00 | 698 | 693
2018-03-03 06:30 | 724 | 720
2018-03-03 07:00 | 741 | 739
2018-03-03 07:30 | 781 | 781
2018-03-03 08:00 | 811 | 811
2018-03-03 08:30 | 855 | 854
2018-03-03 09:00 | 886 | 886
2018-03-03 09:30 | 899 | 899
2018-03-03 10:00 | 917 | 916
2018-03-03 10:30 | 948 | 947
2018-03-03 11:00 | 948 | 948
2018-03-03 11:30 | 923 | 923
2018-03-03 12:00 | 920 | 920
2018-03-03 12:30 | 930 | 929
2018-03-03 13:00 | 943 | 943
2018-03-03 13:30 | 988 | 988
2018-03-03 14:00 | 1004 | 1004
2018-03-03 14:30 | 1013 | 1013
2018-03-03 15:00 | 1032 | 1032
2018-03-03 15:30 | 1048 | 1048
2018-03-03 16:00 | 1070 | 1070
2018-03-03 16:30 | 1092 | 1092
2018-03-03 17:00 | 1113 | 1113
2018-03-03 17:30 | 1112 | 1111
2018-03-03 18:00 | 1106 | 1105
2018-03-03 18:30 | 1102 | 1101
2018-03-03 19:00 | 1115 | 1113
2018-03-03 19:30 | 1103 | 1099
2018-03-03 20:00 | 1079 | 1077
2018-03-03 20:30 | 1052 | 1051
2018-03-03 21:00 | 1016 | 1015
2018-03-03 21:30 | 982 | 982
2018-03-03 22:00 | 959 | 958
2018-03-03 22:30 | 942 | 941
2018-03-03 23:00 | 933 | 932
2018-03-03 23:30 | 879 | 876
2018-03-04 | 828 | 825
2018-03-04 00:30 | 782 | 779
2018-03-04 01:00 | 751 | 750
2018-03-04 01:30 | 728 | 726
2018-03-04 02:00 | 714 | 711
2018-03-04 02:30 | 701 | 697
2018-03-04 03:00 | 689 | 684
2018-03-04 03:30 | 676 | 671
2018-03-04 04:00 | 674 | 669
2018-03-04 04:30 | 667 | 660
2018-03-04 05:00 | 665 | 658
2018-03-04 05:30 | 674 | 668
2018-03-04 06:00 | 672 | 664
2018-03-04 06:30 | 679 | 672
2018-03-04 07:00 | 704 | 700
2018-03-04 07:30 | 732 | 731
2018-03-04 08:00 | 762 | 762
2018-03-04 08:30 | 795 | 794
2018-03-04 09:00 | 819 | 819
2018-03-04 09:30 | 849 | 849
2018-03-04 10:00 | 872 | 871
2018-03-04 10:30 | 909 | 907
2018-03-04 11:00 | 927 | 925
2018-03-04 11:30 | 943 | 942
2018-03-04 12:00 | 976 | 976
2018-03-04 12:30 | 1003 | 1003
2018-03-04 13:00 | 1052 | 1052
2018-03-04 13:30 | 1108 | 1108
2018-03-04 14:00 | 1129 | 1129
2018-03-04 14:30 | 1190 | 1190
2018-03-04 15:00 | 1232 | 1230
2018-03-04 15:30 | 1243 | 1242
2018-03-04 16:00 | 1249 | 1248
2018-03-04 16:30 | 1256 | 1256
2018-03-04 17:00 | 1279 | 1279
2018-03-04 17:30 | 1276 | 1276
2018-03-04 18:00 | 1275 | 1274
2018-03-04 18:30 | 1277 | 1276
2018-03-04 19:00 | 1291 | 1291
2018-03-04 19:30 | 1256 | 1256
2018-03-04 20:00 | 1224 | 1223
2018-03-04 20:30 | 1181 | 1181
2018-03-04 21:00 | 1115 | 1114
2018-03-04 21:30 | 1061 | 1059
2018-03-04 22:00 | 1013 | 1009
2018-03-04 22:30 | 975 | 972
2018-03-04 23:00 | 948 | 946
2018-03-04 23:30 | 885 | 883
2018-03-05 | 833 | 831
2018-03-05 00:30 | 789 | 783
2018-03-05 01:00 | 765 | 758
2018-03-05 01:30 | 747 | 737
2018-03-05 02:00 | 731 | 722
2018-03-05 02:30 | 708 | 704
2018-03-05 03:00 | 698 | 694
2018-03-05 03:30 | 698 | 694
2018-03-05 04:00 | 699 | 694
2018-03-05 04:30 | 706 | 702
2018-03-05 05:00 | 717 | 714
2018-03-05 05:30 | 748 | 748
2018-03-05 06:00 | 796 | 792
2018-03-05 06:30 | 870 | 864
2018-03-05 07:00 | 948 | 945
2018-03-05 07:30 | 1030 | 1027
2018-03-05 08:00 | 1053 | 1050
2018-03-05 08:30 | 1065 | 1064
2018-03-05 09:00 | 1052 | 1050
2018-03-05 09:30 | 1072 | 1071
2018-03-05 10:00 | 1085 | 1084
2018-03-05 10:30 | 1090 | 1090
2018-03-05 11:00 | 1098 | 1095
2018-03-05 11:30 | 1101 | 1097
2018-03-05 12:00 | 1099 | 1096
2018-03-05 12:30 | 1099 | 1095
2018-03-05 13:00 | 1084 | 1080
2018-03-05 13:30 | 1077 | 1073
2018-03-05 14:00 | 1107 | 1104
2018-03-05 14:30 | 1109 | 1107
2018-03-05 15:00 | 1117 | 1115
2018-03-05 15:30 | 1139 | 1137
2018-03-05 16:00 | 1168 | 1166
2018-03-05 16:30 | 1174 | 1171
2018-03-05 17:00 | 1192 | 1190
2018-03-05 17:30 | 1195 | 1191
2018-03-05 18:00 | 1187 | 1180
2018-03-05 18:30 | 1182 | 1177
2018-03-05 19:00 | 1201 | 1198
2018-03-05 19:30 | 1170 | 1166
2018-03-05 20:00 | 1147 | 1145
2018-03-05 20:30 | 1111 | 1109
2018-03-05 21:00 | 1058 | 1057
2018-03-05 21:30 | 1011 | 1008
2018-03-05 22:00 | 975 | 970
2018-03-05 22:30 | 937 | 932
2018-03-05 23:00 | 903 | 899
2018-03-05 23:30 | 841 | 833
2018-03-06 | 793 | 779
2018-03-06 00:30 | 735 | 730
2018-03-06 01:00 | 707 | 702
2018-03-06 01:30 | 687 | 680
2018-03-06 02:00 | 679 | 671
2018-03-06 02:30 | 667 | 657
2018-03-06 03:00 | 662 | 651
2018-03-06 03:30 | 664 | 652
2018-03-06 04:00 | 663 | 652
2018-03-06 04:30 | 671 | 662
2018-03-06 05:00 | 681 | 675
2018-03-06 05:30 | 708 | 706
2018-03-06 06:00 | 747 | 745
2018-03-06 06:30 | 816 | 814
2018-03-06 07:00 | 901 | 898
2018-03-06 07:30 | 971 | 969
2018-03-06 08:00 | 991 | 990
2018-03-06 08:30 | 1005 | 1004
2018-03-06 09:00 | 1012 | 1012
2018-03-06 09:30 | 1019 | 1019
2018-03-06 10:00 | 1022 | 1022
2018-03-06 10:30 | 1016 | 1015
2018-03-06 11:00 | 1011 | 1011
2018-03-06 11:30 | 991 | 990
2018-03-06 12:00 | 989 | 987
2018-03-06 12:30 | 980 | 976
2018-03-06 13:00 | 978 | 974
2018-03-06 13:30 | 979 | 975
2018-03-06 14:00 | 987 | 985
2018-03-06 14:30 | 991 | 989
2018-03-06 15:00 | 988 | 985
2018-03-06 15:30 | 980 | 976
2018-03-06 16:00 | 985 | 981
2018-03-06 16:30 | 1003 | 999
2018-03-06 17:00 | 1010 | 1006
2018-03-06 17:30 | 1000 | 995
2018-03-06 18:00 | 985 | 980
2018-03-06 18:30 | 988 | 984
2018-03-06 19:00 | 993 | 990
2018-03-06 19:30 | 971 | 966
2018-03-06 20:00 | 955 | 953
2018-03-06 20:30 | 933 | 932
2018-03-06 21:00 | 892 | 890
2018-03-06 21:30 | 863 | 861
2018-03-06 22:00 | 842 | 838
2018-03-06 22:30 | 814 | 808
2018-03-06 23:00 | 788 | 783
2018-03-06 23:30 | 740 | 737
2018-03-07 | 699 | 693
2018-03-07 00:30 | 658 | 648
2018-03-07 01:00 | 635 | 622
2018-03-07 01:30 | 623 | 608
2018-03-07 02:00 | 623 | 608
2018-03-07 02:30 | 620 | 604
2018-03-07 03:00 | 615 | 598
2018-03-07 03:30 | 617 | 601
2018-03-07 04:00 | 621 | 605
2018-03-07 04:30 | 630 | 616
2018-03-07 05:00 | 645 | 634
2018-03-07 05:30 | 676 | 670
2018-03-07 06:00 | 711 | 707
2018-03-07 06:30 | 779 | 778
2018-03-07 07:00 | 857 | 854
2018-03-07 07:30 | 928 | 928
2018-03-07 08:00 | 965 | 953
2018-03-07 08:30 | 968 | 965
2018-03-07 09:00 | 969 | 967
2018-03-07 09:30 | 977 | 976
2018-03-07 10:00 | 967 | 966
2018-03-07 10:30 | 955 | 954
2018-03-07 11:00 | 953 | 952
2018-03-07 11:30 | 967 | 966
2018-03-07 12:00 | 950 | 949
2018-03-07 12:30 | 919 | 918
2018-03-07 13:00 | 894 | 892
2018-03-07 13:30 | 889 | 886
2018-03-07 14:00 | 902 | 901
2018-03-07 14:30 | 897 | 895
2018-03-07 15:00 | 916 | 914
2018-03-07 15:30 | 921 | 918
2018-03-07 16:00 | 934 | 932
2018-03-07 16:30 | 965 | 962
2018-03-07 17:00 | 989 | 986
2018-03-07 17:30 | 991 | 987
2018-03-07 18:00 | 994 | 990
2018-03-07 18:30 | 1001 | 998
2018-03-07 19:00 | 1013 | 1010
2018-03-07 19:30 | 992 | 988
2018-03-07 20:00 | 974 | 970
2018-03-07 20:30 | 941 | 938
2018-03-07 21:00 | 900 | 900
2018-03-07 21:30 | 869 | 867
2018-03-07 22:00 | 845 | 843
2018-03-07 22:30 | 813 | 811
2018-03-07 23:00 | 784 | 783
2018-03-07 23:30 | 741 | 738
2018-03-08 | 692 | 687
2018-03-08 00:30 | 653 | 645
2018-03-08 01:00 | 628 | 619
2018-03-08 01:30 | 616 | 605
2018-03-08 02:00 | 609 | 596
2018-03-08 02:30 | 601 | 587
2018-03-08 03:00 | 603 | 589
2018-03-08 03:30 | 602 | 588
2018-03-08 04:00 | 608 | 593
2018-03-08 04:30 | 614 | 601
2018-03-08 05:00 | 617 | 608
2018-03-08 05:30 | 658 | 653
2018-03-08 06:00 | 697 | 693
2018-03-08 06:30 | 759 | 758
2018-03-08 07:00 | 829 | 829
2018-03-08 07:30 | 885 | 885
2018-03-08 08:00 | 892 | 892
2018-03-08 08:30 | 897 | 897
2018-03-08 09:00 | 915 | 915
2018-03-08 09:30 | 885 | 885
2018-03-08 10:00 | 876 | 876
2018-03-08 10:30 | 883 | 883
2018-03-08 11:00 | 887 | 887
2018-03-08 11:30 | 869 | 868
2018-03-08 12:00 | 895 | 895
2018-03-08 12:30 | 908 | 908
2018-03-08 13:00 | 900 | 900
2018-03-08 13:30 | 889 | 889
2018-03-08 14:00 | 897 | 897
2018-03-08 14:30 | 883 | 883
2018-03-08 15:00 | 888 | 888
2018-03-08 15:30 | 902 | 902
2018-03-08 16:00 | 924 | 923
2018-03-08 16:30 | 950 | 950
2018-03-08 17:00 | 966 | 965
2018-03-08 17:30 | 962 | 960
2018-03-08 18:00 | 973 | 971
2018-03-08 18:30 | 1000 | 999
2018-03-08 19:00 | 1024 | 1022
2018-03-08 19:30 | 1004 | 1001
2018-03-08 20:00 | 996 | 991
2018-03-08 20:30 | 969 | 965
2018-03-08 21:00 | 928 | 926
2018-03-08 21:30 | 882 | 882
2018-03-08 22:00 | 846 | 845
2018-03-08 22:30 | 816 | 814
2018-03-08 23:00 | 796 | 793
2018-03-08 23:30 | 747 | 742
2018-03-09 | 696 | 689
2018-03-09 00:30 | 654 | 644
2018-03-09 01:00 | 629 | 617
2018-03-09 01:30 | 618 | 606
2018-03-09 02:00 | 611 | 597
2018-03-09 02:30 | 608 | 593
2018-03-09 03:00 | 607 | 592
2018-03-09 03:30 | 604 | 588
2018-03-09 04:00 | 607 | 592
2018-03-09 04:30 | 612 | 599
2018-03-09 05:00 | 627 | 617
2018-03-09 05:30 | 659 | 652
2018-03-09 06:00 | 692 | 687
2018-03-09 06:30 | 752 | 750
2018-03-09 07:00 | 814 | 814
2018-03-09 07:30 | 877 | 877
2018-03-09 08:00 | 885 | 885
2018-03-09 08:30 | 882 | 882
2018-03-09 09:00 | 864 | 864
2018-03-09 09:30 | 879 | 879
2018-03-09 10:00 | 874 | 874
2018-03-09 10:30 | 878 | 878
2018-03-09 11:00 | 886 | 886
2018-03-09 11:30 | 889 | 889
2018-03-09 12:00 | 882 | 881
2018-03-09 12:30 | 865 | 864
2018-03-09 13:00 | 875 | 875
2018-03-09 13:30 | 872 | 872
2018-03-09 14:00 | 874 | 874
2018-03-09 14:30 | 871 | 871
2018-03-09 15:00 | 876 | 875
2018-03-09 15:30 | 905 | 904
2018-03-09 16:00 | 924 | 923
2018-03-09 16:30 | 955 | 954
2018-03-09 17:00 | 972 | 971
2018-03-09 17:30 | 972 | 970
2018-03-09 18:00 | 959 | 958
2018-03-09 18:30 | 966 | 965
2018-03-09 19:00 | 984 | 984
2018-03-09 19:30 | 967 | 966
2018-03-09 20:00 | 954 | 953
2018-03-09 20:30 | 934 | 934
2018-03-09 21:00 | 905 | 905
2018-03-09 21:30 | 875 | 875
2018-03-09 22:00 | 849 | 848
2018-03-09 22:30 | 824 | 823
2018-03-09 23:00 | 805 | 803
2018-03-09 23:30 | 758 | 754
2018-03-10 | 710 | 702
2018-03-10 00:30 | 672 | 661
2018-03-10 01:00 | 646 | 634
2018-03-10 01:30 | 636 | 623
2018-03-10 02:00 | 623 | 607
2018-03-10 02:30 | 616 | 599
2018-03-10 03:00 | 618 | 600
2018-03-10 03:30 | 612 | 594
2018-03-10 04:00 | 612 | 594
2018-03-10 04:30 | 612 | 594
2018-03-10 05:00 | 619 | 602
2018-03-10 05:30 | 632 | 618
2018-03-10 06:00 | 637 | 622
2018-03-10 06:30 | 664 | 652
2018-03-10 07:00 | 684 | 676
2018-03-10 07:30 | 708 | 704
2018-03-10 08:00 | 726 | 724
2018-03-10 08:30 | 731 | 730
2018-03-10 09:00 | 765 | 765
2018-03-10 09:30 | 778 | 778
2018-03-10 10:00 | 774 | 774
2018-03-10 10:30 | 767 | 767
2018-03-10 11:00 | 736 | 736
2018-03-10 11:30 | 731 | 731
2018-03-10 12:00 | 706 | 706
2018-03-10 12:30 | 711 | 711
2018-03-10 13:00 | 733 | 732
2018-03-10 13:30 | 750 | 747
2018-03-10 14:00 | 734 | 732
2018-03-10 14:30 | 732 | 731
2018-03-10 15:00 | 772 | 772
2018-03-10 15:30 | 797 | 796
2018-03-10 16:00 | 808 | 808
2018-03-10 16:30 | 810 | 809
2018-03-10 17:00 | 837 | 837
2018-03-10 17:30 | 846 | 845
2018-03-10 18:00 | 849 | 848
2018-03-10 18:30 | 855 | 855
2018-03-10 19:00 | 878 | 878
2018-03-10 19:30 | 863 | 862
2018-03-10 20:00 | 846 | 845
2018-03-10 20:30 | 832 | 831
2018-03-10 21:00 | 803 | 800
2018-03-10 21:30 | 780 | 778
2018-03-10 22:00 | 770 | 767
2018-03-10 22:30 | 767 | 763
2018-03-10 23:00 | 767 | 764
2018-03-10 23:30 | 732 | 727
2018-03-11 | 693 | 683
2018-03-11 00:30 | 657 | 644
2018-03-11 01:00 | 632 | 617
2018-03-11 01:30 | 618 | 600
2018-03-11 02:00 | 604 | 583
2018-03-11 02:30 | 599 | 578
2018-03-11 03:00 | 596 | 574
2018-03-11 03:30 | 596 | 573
2018-03-11 04:00 | 596 | 574
2018-03-11 04:30 | 593 | 569
2018-03-11 05:00 | 597 | 574
2018-03-11 05:30 | 602 | 580
2018-03-11 06:00 | 606 | 583
2018-03-11 06:30 | 622 | 601
2018-03-11 07:00 | 635 | 616
2018-03-11 07:30 | 649 | 636
2018-03-11 08:00 | 666 | 657
2018-03-11 08:30 | 685 | 680
2018-03-11 09:00 | 728 | 721
2018-03-11 09:30 | 754 | 750
2018-03-11 10:00 | 758 | 754
2018-03-11 10:30 | 743 | 739
2018-03-11 11:00 | 725 | 722
2018-03-11 11:30 | 721 | 717
2018-03-11 12:00 | 714 | 711
2018-03-11 12:30 | 697 | 693
2018-03-11 13:00 | 761 | 759
2018-03-11 13:30 | 765 | 762
2018-03-11 14:00 | 740 | 736
2018-03-11 14:30 | 752 | 749
2018-03-11 15:00 | 762 | 758
2018-03-11 15:30 | 776 | 774
2018-03-11 16:00 | 782 | 779
2018-03-11 16:30 | 813 | 810
2018-03-11 17:00 | 825 | 823
2018-03-11 17:30 | 838 | 836
2018-03-11 18:00 | 854 | 852
2018-03-11 18:30 | 877 | 877
2018-03-11 19:00 | 906 | 906
2018-03-11 19:30 | 889 | 886
2018-03-11 20:00 | 872 | 869
2018-03-11 20:30 | 853 | 850
2018-03-11 21:00 | 822 | 822
2018-03-11 21:30 | 796 | 795
2018-03-11 22:00 | 774 | 772
2018-03-11 22:30 | 764 | 760
2018-03-11 23:00 | 759 | 754
2018-03-11 23:30 | 727 | 720
2018-03-12 | 686 | 675
2018-03-12 00:30 | 647 | 631
2018-03-12 01:00 | 625 | 606
2018-03-12 01:30 | 618 | 598
2018-03-12 02:00 | 610 | 585
2018-03-12 02:30 | 604 | 580
2018-03-12 03:00 | 598 | 574
2018-03-12 03:30 | 600 | 575
2018-03-12 04:00 | 606 | 582
2018-03-12 04:30 | 612 | 590
2018-03-12 05:00 | 623 | 605
2018-03-12 05:30 | 652 | 641
2018-03-12 06:00 | 660 | 650
2018-03-12 06:30 | 724 | 722
2018-03-12 07:00 | 809 | 804
2018-03-12 07:30 | 856 | 855
2018-03-12 08:00 | 852 | 852
2018-03-12 08:30 | 840 | 839
2018-03-12 09:00 | 817 | 817
2018-03-12 09:30 | 823 | 823
2018-03-12 10:00 | 833 | 833
2018-03-12 10:30 | 819 | 819
2018-03-12 11:00 | 806 | 806
2018-03-12 11:30 | 787 | 787
2018-03-12 12:00 | 787 | 787
2018-03-12 12:30 | 840 | 840
2018-03-12 13:00 | 820 | 820
2018-03-12 13:30 | 824 | 823
2018-03-12 14:00 | 835 | 835
2018-03-12 14:30 | 856 | 856
2018-03-12 15:00 | 877 | 876
2018-03-12 15:30 | 909 | 907
2018-03-12 16:00 | 961 | 960
2018-03-12 16:30 | 989 | 988
2018-03-12 17:00 | 1015 | 1014
2018-03-12 17:30 | 1026 | 1024
2018-03-12 18:00 | 1019 | 1017
2018-03-12 18:30 | 1024 | 1021
2018-03-12 19:00 | 1047 | 1045
2018-03-12 19:30 | 1021 | 1018
2018-03-12 20:00 | 995 | 994
2018-03-12 20:30 | 974 | 972
2018-03-12 21:00 | 932 | 931
2018-03-12 21:30 | 899 | 897
2018-03-12 22:00 | 873 | 869
2018-03-12 22:30 | 836 | 831
2018-03-12 23:00 | 805 | 802
2018-03-12 23:30 | 749 | 745
2018-03-13 | 708 | 701
2018-03-13 00:30 | 670 | 659
2018-03-13 01:00 | 646 | 633
2018-03-13 01:30 | 632 | 617
2018-03-13 02:00 | 627 | 610
2018-03-13 02:30 | 622 | 604
2018-03-13 03:00 | 616 | 598
2018-03-13 03:30 | 619 | 600
2018-03-13 04:00 | 618 | 599
2018-03-13 04:30 | 625 | 609
2018-03-13 05:00 | 638 | 624
2018-03-13 05:30 | 670 | 662
2018-03-13 06:00 | 706 | 700
2018-03-13 06:30 | 764 | 763
2018-03-13 07:00 | 826 | 825
2018-03-13 07:30 | 878 | 878
2018-03-13 08:00 | 892 | 891
2018-03-13 08:30 | 877 | 877
2018-03-13 09:00 | 890 | 890
2018-03-13 09:30 | 906 | 906
2018-03-13 10:00 | 923 | 923
2018-03-13 10:30 | 932 | 932
2018-03-13 11:00 | 934 | 934
2018-03-13 11:30 | 932 | 932
2018-03-13 12:00 | 926 | 926
2018-03-13 12:30 | 919 | 919
2018-03-13 13:00 | 949 | 949
2018-03-13 13:30 | 949 | 948
2018-03-13 14:00 | 946 | 945
2018-03-13 14:30 | 950 | 950
2018-03-13 15:00 | 958 | 957
2018-03-13 15:30 | 970 | 969
2018-03-13 16:00 | 986 | 984
2018-03-13 16:30 | 1002 | 1001
2018-03-13 17:00 | 1011 | 1010
2018-03-13 17:30 | 1013 | 1012
2018-03-13 18:00 | 1016 | 1014
2018-03-13 18:30 | 1020 | 1018
2018-03-13 19:00 | 1038 | 1036
2018-03-13 19:30 | 1014 | 1011
2018-03-13 20:00 | 997 | 992
2018-03-13 20:30 | 972 | 968
2018-03-13 21:00 | 930 | 929
2018-03-13 21:30 | 893 | 892
2018-03-13 22:00 | 868 | 866
2018-03-13 22:30 | 836 | 835
2018-03-13 23:00 | 815 | 811
2018-03-13 23:30 | 768 | 761
2018-03-14 | 718 | 711
2018-03-14 00:30 | 674 | 665
2018-03-14 01:00 | 655 | 643
2018-03-14 01:30 | 641 | 628
2018-03-14 02:00 | 632 | 618
2018-03-14 02:30 | 630 | 615
2018-03-14 03:00 | 626 | 609
2018-03-14 03:30 | 623 | 605
2018-03-14 04:00 | 627 | 609
2018-03-14 04:30 | 639 | 624
2018-03-14 05:00 | 643 | 631
2018-03-14 05:30 | 682 | 675
2018-03-14 06:00 | 725 | 722
2018-03-14 06:30 | 779 | 778
2018-03-14 07:00 | 844 | 843
2018-03-14 07:30 | 906 | 905
2018-03-14 08:00 | 912 | 910
2018-03-14 08:30 | 899 | 898
2018-03-14 09:00 | 885 | 884
2018-03-14 09:30 | 897 | 897
2018-03-14 10:00 | 891 | 891
2018-03-14 10:30 | 888 | 887
2018-03-14 11:00 | 885 | 885
2018-03-14 11:30 | 877 | 877
2018-03-14 12:00 | 868 | 868
2018-03-14 12:30 | 889 | 889
2018-03-14 13:00 | 899 | 899
2018-03-14 13:30 | 902 | 902
2018-03-14 14:00 | 906 | 906
2018-03-14 14:30 | 910 | 910
2018-03-14 15:00 | 929 | 928
2018-03-14 15:30 | 941 | 941
2018-03-14 16:00 | 968 | 968
2018-03-14 16:30 | 1005 | 1004
2018-03-14 17:00 | 1027 | 1027
2018-03-14 17:30 | 1029 | 1029
2018-03-14 18:00 | 1024 | 1023
2018-03-14 18:30 | 1029 | 1028
2018-03-14 19:00 | 1052 | 1051
2018-03-14 19:30 | 1028 | 1027
2018-03-14 20:00 | 1009 | 1008
2018-03-14 20:30 | 983 | 981
2018-03-14 21:00 | 940 | 939
2018-03-14 21:30 | 907 | 907
2018-03-14 22:00 | 878 | 878
2018-03-14 22:30 | 837 | 836
2018-03-14 23:00 | 818 | 818
2018-03-14 23:30 | 769 | 767
2018-03-15 | 721 | 716
2018-03-15 00:30 | 680 | 672
2018-03-15 01:00 | 659 | 649
2018-03-15 01:30 | 647 | 634
2018-03-15 02:00 | 634 | 619
2018-03-15 02:30 | 620 | 602
2018-03-15 03:00 | 619 | 600
2018-03-15 03:30 | 612 | 593
2018-03-15 04:00 | 612 | 594
2018-03-15 04:30 | 624 | 608
2018-03-15 05:00 | 638 | 625
2018-03-15 05:30 | 674 | 667
2018-03-15 06:00 | 712 | 707
2018-03-15 06:30 | 777 | 776
2018-03-15 07:00 | 841 | 840
2018-03-15 07:30 | 898 | 898
2018-03-15 08:00 | 922 | 922
2018-03-15 08:30 | 915 | 914
2018-03-15 09:00 | 907 | 905
2018-03-15 09:30 | 899 | 897
2018-03-15 10:00 | 868 | 867
2018-03-15 10:30 | 862 | 862
2018-03-15 11:00 | 891 | 891
2018-03-15 11:30 | 908 | 906
2018-03-15 12:00 | 912 | 911
2018-03-15 12:30 | 910 | 908
2018-03-15 13:00 | 920 | 920
2018-03-15 13:30 | 925 | 925
2018-03-15 14:00 | 941 | 940
2018-03-15 14:30 | 968 | 966
2018-03-15 15:00 | 993 | 991
2018-03-15 15:30 | 984 | 981
2018-03-15 16:00 | 1024 | 1021
2018-03-15 16:30 | 1049 | 1046
2018-03-15 17:00 | 1076 | 1073
2018-03-15 17:30 | 1077 | 1074
2018-03-15 18:00 | 1070 | 1066
2018-03-15 18:30 | 1075 | 1071
2018-03-15 19:00 | 1091 | 1089
2018-03-15 19:30 | 1064 | 1062
2018-03-15 20:00 | 1044 | 1044
2018-03-15 20:30 | 1014 | 1013
2018-03-15 21:00 | 967 | 965
2018-03-15 21:30 | 922 | 920
2018-03-15 22:00 | 886 | 880
2018-03-15 22:30 | 847 | 842
2018-03-15 23:00 | 817 | 814
2018-03-15 23:30 | 765 | 762
2018-03-16 | 716 | 710
2018-03-16 00:30 | 676 | 667
2018-03-16 01:00 | 653 | 642
2018-03-16 01:30 | 635 | 622
2018-03-16 02:00 | 630 | 614
2018-03-16 02:30 | 622 | 605
2018-03-16 03:00 | 622 | 605
2018-03-16 03:30 | 620 | 603
2018-03-16 04:00 | 622 | 605
2018-03-16 04:30 | 629 | 613
2018-03-16 05:00 | 646 | 633
2018-03-16 05:30 | 675 | 667
2018-03-16 06:00 | 700 | 695
2018-03-16 06:30 | 750 | 748
2018-03-16 07:00 | 809 | 809
2018-03-16 07:30 | 867 | 865
2018-03-16 08:00 | 871 | 869
2018-03-16 08:30 | 872 | 870
2018-03-16 09:00 | 873 | 870
2018-03-16 09:30 | 866 | 865
2018-03-16 10:00 | 868 | 868
2018-03-16 10:30 | 866 | 865
2018-03-16 11:00 | 861 | 861
2018-03-16 11:30 | 859 | 859
2018-03-16 12:00 | 869 | 869
2018-03-16 12:30 | 881 | 881
2018-03-16 13:00 | 894 | 894
2018-03-16 13:30 | 911 | 911
2018-03-16 14:00 | 931 | 930
2018-03-16 14:30 | 950 | 949
2018-03-16 15:00 | 968 | 967
2018-03-16 15:30 | 994 | 994
2018-03-16 16:00 | 1034 | 1034
2018-03-16 16:30 | 1064 | 1064
2018-03-16 17:00 | 1087 | 1086
2018-03-16 17:30 | 1084 | 1082
2018-03-16 18:00 | 1064 | 1059
2018-03-16 18:30 | 1049 | 1041
2018-03-16 19:00 | 1063 | 1058
2018-03-16 19:30 | 1038 | 1033
2018-03-16 20:00 | 1015 | 1012
2018-03-16 20:30 | 988 | 988
2018-03-16 21:00 | 954 | 954
2018-03-16 21:30 | 923 | 921
2018-03-16 22:00 | 891 | 889
2018-03-16 22:30 | 858 | 856
2018-03-16 23:00 | 833 | 832
2018-03-16 23:30 | 780 | 777
2018-03-17 | 731 | 727
2018-03-17 00:30 | 693 | 687
2018-03-17 01:00 | 671 | 663
2018-03-17 01:30 | 656 | 646
2018-03-17 02:00 | 643 | 631
2018-03-17 02:30 | 637 | 623
2018-03-17 03:00 | 626 | 610
2018-03-17 03:30 | 624 | 608
2018-03-17 04:00 | 621 | 605
2018-03-17 04:30 | 621 | 604
2018-03-17 05:00 | 624 | 608
2018-03-17 05:30 | 634 | 620
2018-03-17 06:00 | 642 | 629
2018-03-17 06:30 | 659 | 647
2018-03-17 07:00 | 677 | 669
2018-03-17 07:30 | 700 | 697
2018-03-17 08:00 | 727 | 727
2018-03-17 08:30 | 755 | 755
2018-03-17 09:00 | 764 | 764
2018-03-17 09:30 | 773 | 773
2018-03-17 10:00 | 771 | 771
2018-03-17 10:30 | 774 | 774
2018-03-17 11:00 | 775 | 775
2018-03-17 11:30 | 776 | 775
2018-03-17 12:00 | 785 | 785
2018-03-17 12:30 | 790 | 790
2018-03-17 13:00 | 800 | 800
2018-03-17 13:30 | 820 | 820
2018-03-17 14:00 | 839 | 839
2018-03-17 14:30 | 863 | 863
2018-03-17 15:00 | 884 | 884
2018-03-17 15:30 | 914 | 914
2018-03-17 16:00 | 949 | 949
2018-03-17 16:30 | 970 | 970
2018-03-17 17:00 | 1006 | 1005
2018-03-17 17:30 | 1005 | 999
2018-03-17 18:00 | 994 | 984
2018-03-17 18:30 | 997 | 990
2018-03-17 19:00 | 1010 | 1006
2018-03-17 19:30 | 991 | 987
2018-03-17 20:00 | 971 | 969
2018-03-17 20:30 | 947 | 945
2018-03-17 21:00 | 906 | 906
2018-03-17 21:30 | 884 | 884
2018-03-17 22:00 | 863 | 861
2018-03-17 22:30 | 839 | 837
2018-03-17 23:00 | 825 | 822
2018-03-17 23:30 | 771 | 768
2018-03-18 | 729 | 725
2018-03-18 00:30 | 687 | 679
2018-03-18 01:00 | 666 | 655
2018-03-18 01:30 | 653 | 640
2018-03-18 02:00 | 642 | 627
2018-03-18 02:30 | 633 | 615
2018-03-18 03:00 | 627 | 607
2018-03-18 03:30 | 622 | 602
2018-03-18 04:00 | 622 | 601
2018-03-18 04:30 | 616 | 594
2018-03-18 05:00 | 618 | 598
2018-03-18 05:30 | 627 | 607
2018-03-18 06:00 | 630 | 607
2018-03-18 06:30 | 644 | 623
2018-03-18 07:00 | 649 | 632
2018-03-18 07:30 | 688 | 675
2018-03-18 08:00 | 702 | 693
2018-03-18 08:30 | 724 | 720
2018-03-18 09:00 | 738 | 737
2018-03-18 09:30 | 762 | 762
2018-03-18 10:00 | 789 | 789
2018-03-18 10:30 | 785 | 785
2018-03-18 11:00 | 769 | 769
2018-03-18 11:30 | 738 | 738
2018-03-18 12:00 | 800 | 799
2018-03-18 12:30 | 821 | 821
2018-03-18 13:00 | 831 | 831
2018-03-18 13:30 | 847 | 847
2018-03-18 14:00 | 871 | 871
2018-03-18 14:30 | 901 | 901
2018-03-18 15:00 | 929 | 929
2018-03-18 15:30 | 966 | 965
2018-03-18 16:00 | 1007 | 1006
2018-03-18 16:30 | 1050 | 1050
2018-03-18 17:00 | 1082 | 1082
2018-03-18 17:30 | 1090 | 1090
2018-03-18 18:00 | 1091 | 1090
2018-03-18 18:30 | 1104 | 1104
2018-03-18 19:00 | 1120 | 1120
2018-03-18 19:30 | 1092 | 1092
2018-03-18 20:00 | 1068 | 1067
2018-03-18 20:30 | 1027 | 1026
2018-03-18 21:00 | 973 | 972
2018-03-18 21:30 | 934 | 933
2018-03-18 22:00 | 900 | 897
2018-03-18 22:30 | 865 | 860
2018-03-18 23:00 | 851 | 846
2018-03-18 23:30 | 802 | 794
2018-03-19 | 743 | 740
2018-03-19 00:30 | 701 | 695
2018-03-19 01:00 | 680 | 671
2018-03-19 01:30 | 663 | 653
2018-03-19 02:00 | 655 | 643
2018-03-19 02:30 | 648 | 634
2018-03-19 03:00 | 645 | 631
2018-03-19 03:30 | 643 | 629
2018-03-19 04:00 | 644 | 630
2018-03-19 04:30 | 650 | 639
2018-03-19 05:00 | 661 | 652
2018-03-19 05:30 | 696 | 692
2018-03-19 06:00 | 728 | 726
2018-03-19 06:30 | 796 | 795
2018-03-19 07:00 | 846 | 846
2018-03-19 07:30 | 921 | 919
2018-03-19 08:00 | 951 | 949
2018-03-19 08:30 | 971 | 970
2018-03-19 09:00 | 990 | 990
2018-03-19 09:30 | 1004 | 1004
2018-03-19 10:00 | 1006 | 1006
2018-03-19 10:30 | 1015 | 1015
2018-03-19 11:00 | 1029 | 1029
2018-03-19 11:30 | 1034 | 1034
2018-03-19 12:00 | 1039 | 1039
2018-03-19 12:30 | 1046 | 1046
2018-03-19 13:00 | 1069 | 1069
2018-03-19 13:30 | 1083 | 1083
2018-03-19 14:00 | 1104 | 1104
2018-03-19 14:30 | 1128 | 1128
2018-03-19 15:00 | 1145 | 1145
2018-03-19 15:30 | 1176 | 1176
2018-03-19 16:00 | 1216 | 1216
2018-03-19 16:30 | 1247 | 1247
2018-03-19 17:00 | 1269 | 1269
2018-03-19 17:30 | 1263 | 1259
2018-03-19 18:00 | 1246 | 1238
2018-03-19 18:30 | 1244 | 1236
2018-03-19 19:00 | 1263 | 1256
2018-03-19 19:30 | 1227 | 1215
2018-03-19 20:00 | 1198 | 1193
2018-03-19 20:30 | 1154 | 1149
2018-03-19 21:00 | 1098 | 1094
2018-03-19 21:30 | 1053 | 1046
2018-03-19 22:00 | 1007 | 1001
2018-03-19 22:30 | 956 | 954
2018-03-19 23:00 | 929 | 925
2018-03-19 23:30 | 857 | 854
2018-03-20 | 808 | 804
2018-03-20 00:30 | 755 | 754
2018-03-20 01:00 | 725 | 722
2018-03-20 01:30 | 703 | 700
2018-03-20 02:00 | 696 | 691
2018-03-20 02:30 | 682 | 675
2018-03-20 03:00 | 680 | 672
2018-03-20 03:30 | 671 | 664
2018-03-20 04:00 | 674 | 667
2018-03-20 04:30 | 684 | 677
2018-03-20 05:00 | 702 | 697
2018-03-20 05:30 | 731 | 729
2018-03-20 06:00 | 768 | 766
2018-03-20 06:30 | 824 | 824
2018-03-20 07:00 | 882 | 881
2018-03-20 07:30 | 944 | 944
2018-03-20 08:00 | 980 | 980
2018-03-20 08:30 | 996 | 996
2018-03-20 09:00 | 1010 | 1009
2018-03-20 09:30 | 1007 | 1006
2018-03-20 10:00 | 1006 | 1005
2018-03-20 10:30 | 1010 | 1010
2018-03-20 11:00 | 1010 | 1010
2018-03-20 11:30 | 996 | 996
2018-03-20 12:00 | 991 | 991
2018-03-20 12:30 | 997 | 996
2018-03-20 13:00 | 1006 | 1004
2018-03-20 13:30 | 1021 | 1020
2018-03-20 14:00 | 1038 | 1038
2018-03-20 14:30 | 1049 | 1048
2018-03-20 15:00 | 1055 | 1054
2018-03-20 15:30 | 1073 | 1072
2018-03-20 16:00 | 1108 | 1106
2018-03-20 16:30 | 1130 | 1127
2018-03-20 17:00 | 1144 | 1140
2018-03-20 17:30 | 1143 | 1137
2018-03-20 18:00 | 1129 | 1117
2018-03-20 18:30 | 1127 | 1119
2018-03-20 19:00 | 1148 | 1142
2018-03-20 19:30 | 1117 | 1111
2018-03-20 20:00 | 1092 | 1089
2018-03-20 20:30 | 1056 | 1054
2018-03-20 21:00 | 1010 | 1008
2018-03-20 21:30 | 970 | 969
2018-03-20 22:00 | 938 | 937
2018-03-20 22:30 | 895 | 892
2018-03-20 23:00 | 868 | 863
2018-03-20 23:30 | 822 | 815
2018-03-21 | 762 | 759
2018-03-21 00:30 | 720 | 713
2018-03-21 01:00 | 697 | 688
2018-03-21 01:30 | 689 | 677
2018-03-21 02:00 | 678 | 664
2018-03-21 02:30 | 670 | 657
2018-03-21 03:00 | 671 | 658
2018-03-21 03:30 | 668 | 654
2018-03-21 04:00 | 661 | 648
2018-03-21 04:30 | 662 | 650
2018-03-21 05:00 | 671 | 663
2018-03-21 05:30 | 705 | 701
2018-03-21 06:00 | 736 | 734
2018-03-21 06:30 | 809 | 809
2018-03-21 07:00 | 904 | 904
2018-03-21 07:30 | 963 | 962
2018-03-21 08:00 | 987 | 987
2018-03-21 08:30 | 1001 | 1001
2018-03-21 09:00 | 1023 | 1022
2018-03-21 09:30 | 1046 | 1045
2018-03-21 10:00 | 1054 | 1054
2018-03-21 10:30 | 1025 | 1025
2018-03-21 11:00 | 1006 | 1006
2018-03-21 11:30 | 1023 | 1023
2018-03-21 12:00 | 1000 | 999
2018-03-21 12:30 | 1009 | 1008
2018-03-21 13:00 | 990 | 989
2018-03-21 13:30 | 967 | 966
2018-03-21 14:00 | 968 | 967
2018-03-21 14:30 | 973 | 972
2018-03-21 15:00 | 990 | 988
2018-03-21 15:30 | 1013 | 1011
2018-03-21 16:00 | 1035 | 1033
2018-03-21 16:30 | 1046 | 1044
2018-03-21 17:00 | 1057 | 1055
2018-03-21 17:30 | 1060 | 1057
2018-03-21 18:00 | 1059 | 1055
2018-03-21 18:30 | 1066 | 1063
2018-03-21 19:00 | 1070 | 1066
2018-03-21 19:30 | 1056 | 1050
2018-03-21 20:00 | 1029 | 1025
2018-03-21 20:30 | 1002 | 999
2018-03-21 21:00 | 957 | 954
2018-03-21 21:30 | 923 | 921
2018-03-21 22:00 | 903 | 900
2018-03-21 22:30 | 863 | 861
2018-03-21 23:00 | 844 | 843
2018-03-21 23:30 | 790 | 787
2018-03-22 | 748 | 740
2018-03-22 00:30 | 708 | 696
2018-03-22 01:00 | 684 | 676
2018-03-22 01:30 | 670 | 660
2018-03-22 02:00 | 657 | 645
2018-03-22 02:30 | 646 | 634
2018-03-22 03:00 | 644 | 633
2018-03-22 03:30 | 641 | 631
2018-03-22 04:00 | 635 | 624
2018-03-22 04:30 | 641 | 631
2018-03-22 05:00 | 647 | 638
2018-03-22 05:30 | 680 | 676
2018-03-22 06:00 | 701 | 698
2018-03-22 06:30 | 777 | 775
2018-03-22 07:00 | 844 | 844
2018-03-22 07:30 | 907 | 907
2018-03-22 08:00 | 916 | 916
2018-03-22 08:30 | 930 | 930
2018-03-22 09:00 | 926 | 926
2018-03-22 09:30 | 912 | 910
2018-03-22 10:00 | 919 | 916
2018-03-22 10:30 | 937 | 936
2018-03-22 11:00 | 945 | 944
2018-03-22 11:30 | 914 | 909
2018-03-22 12:00 | 884 | 879
2018-03-22 12:30 | 861 | 856
2018-03-22 13:00 | 890 | 886
2018-03-22 13:30 | 885 | 881
2018-03-22 14:00 | 914 | 911
2018-03-22 14:30 | 928 | 926
2018-03-22 15:00 | 956 | 953
2018-03-22 15:30 | 985 | 982
2018-03-22 16:00 | 1021 | 1019
2018-03-22 16:30 | 1030 | 1028
2018-03-22 17:00 | 1048 | 1045
2018-03-22 17:30 | 1044 | 1039
2018-03-22 18:00 | 1055 | 1050
2018-03-22 18:30 | 1076 | 1071
2018-03-22 19:00 | 1086 | 1081
2018-03-22 19:30 | 1065 | 1057
2018-03-22 20:00 | 1040 | 1039
2018-03-22 20:30 | 1024 | 1022
2018-03-22 21:00 | 977 | 975
2018-03-22 21:30 | 935 | 933
2018-03-22 22:00 | 895 | 895
2018-03-22 22:30 | 862 | 862
2018-03-22 23:00 | 834 | 834
2018-03-22 23:30 | 781 | 780
2018-03-23 | 738 | 734
2018-03-23 00:30 | 697 | 689
2018-03-23 01:00 | 671 | 661
2018-03-23 01:30 | 661 | 649
2018-03-23 02:00 | 651 | 637
2018-03-23 02:30 | 645 | 631
2018-03-23 03:00 | 638 | 623
2018-03-23 03:30 | 640 | 625
2018-03-23 04:00 | 638 | 623
2018-03-23 04:30 | 644 | 631
2018-03-23 05:00 | 660 | 649
2018-03-23 05:30 | 694 | 687
2018-03-23 06:00 | 734 | 729
2018-03-23 06:30 | 785 | 784
2018-03-23 07:00 | 852 | 851
2018-03-23 07:30 | 902 | 902
2018-03-23 08:00 | 926 | 926
2018-03-23 08:30 | 944 | 943
2018-03-23 09:00 | 936 | 936
2018-03-23 09:30 | 950 | 950
2018-03-23 10:00 | 961 | 961
2018-03-23 10:30 | 946 | 946
2018-03-23 11:00 | 936 | 936
2018-03-23 11:30 | 937 | 937
2018-03-23 12:00 | 949 | 949
2018-03-23 12:30 | 930 | 929
2018-03-23 13:00 | 924 | 922
2018-03-23 13:30 | 923 | 922
2018-03-23 14:00 | 926 | 925
2018-03-23 14:30 | 950 | 950
2018-03-23 15:00 | 973 | 973
2018-03-23 15:30 | 989 | 988
2018-03-23 16:00 | 1015 | 1014
2018-03-23 16:30 | 1036 | 1036
2018-03-23 17:00 | 1048 | 1047
2018-03-23 17:30 | 1043 | 1041
2018-03-23 18:00 | 1031 | 1026
2018-03-23 18:30 | 1030 | 1027
2018-03-23 19:00 | 1041 | 1039
2018-03-23 19:30 | 1020 | 1015
2018-03-23 20:00 | 1011 | 1004
2018-03-23 20:30 | 996 | 987
2018-03-23 21:00 | 960 | 949
2018-03-23 21:30 | 918 | 912
2018-03-23 22:00 | 892 | 888
2018-03-23 22:30 | 860 | 857
2018-03-23 23:00 | 840 | 837
2018-03-23 23:30 | 788 | 782
2018-03-24 | 734 | 727
2018-03-24 00:30 | 694 | 684
2018-03-24 01:00 | 678 | 667
2018-03-24 01:30 | 661 | 649
2018-03-24 02:00 | 652 | 638
2018-03-24 02:30 | 644 | 629
2018-03-24 03:00 | 639 | 623
2018-03-24 03:30 | 634 | 617
2018-03-24 04:00 | 630 | 613
2018-03-24 04:30 | 631 | 615
2018-03-24 05:00 | 635 | 619
2018-03-24 05:30 | 649 | 636
2018-03-24 06:00 | 660 | 648
2018-03-24 06:30 | 681 | 670
2018-03-24 07:00 | 700 | 692
2018-03-24 07:30 | 726 | 723
2018-03-24 08:00 | 745 | 743
2018-03-24 08:30 | 765 | 764
2018-03-24 09:00 | 797 | 797
2018-03-24 09:30 | 798 | 797
2018-03-24 10:00 | 799 | 798
2018-03-24 10:30 | 808 | 807
2018-03-24 11:00 | 811 | 810
2018-03-24 11:30 | 805 | 805
2018-03-24 12:00 | 812 | 812
2018-03-24 12:30 | 797 | 797
2018-03-24 13:00 | 788 | 788
2018-03-24 13:30 | 790 | 789
2018-03-24 14:00 | 795 | 795
2018-03-24 14:30 | 807 | 806
2018-03-24 15:00 | 831 | 831
2018-03-24 15:30 | 853 | 853
2018-03-24 16:00 | 882 | 882
2018-03-24 16:30 | 901 | 901
2018-03-24 17:00 | 909 | 909
2018-03-24 17:30 | 910 | 909
2018-03-24 18:00 | 912 | 910
2018-03-24 18:30 | 933 | 932
2018-03-24 19:00 | 944 | 944
2018-03-24 19:30 | 923 | 922
2018-03-24 20:00 | 913 | 910
2018-03-24 20:30 | 885 | 882
2018-03-24 21:00 | 857 | 857
2018-03-24 21:30 | 829 | 828
2018-03-24 22:00 | 815 | 813
2018-03-24 22:30 | 805 | 802
2018-03-24 23:00 | 798 | 796
2018-03-24 23:30 | 758 | 754
2018-03-25 | 722 | 715
2018-03-25 00:30 | 677 | 664
2018-03-25 01:00 | 659 | 643
2018-03-25 01:30 | 648 | 630
2018-03-25 02:00 | 638 | 617
2018-03-25 02:30 | 637 | 616
2018-03-25 03:00 | 630 | 609
2018-03-25 03:30 | 626 | 604
2018-03-25 04:00 | 614 | 590
2018-03-25 04:30 | 620 | 595
2018-03-25 05:00 | 621 | 596
2018-03-25 05:30 | 626 | 604
2018-03-25 06:00 | 632 | 611
2018-03-25 06:30 | 642 | 621
2018-03-25 07:00 | 654 | 636
2018-03-25 07:30 | 679 | 667
2018-03-25 08:00 | 697 | 690
2018-03-25 08:30 | 715 | 711
2018-03-25 09:00 | 731 | 729
2018-03-25 09:30 | 758 | 758
2018-03-25 10:00 | 788 | 787
2018-03-25 10:30 | 801 | 800
2018-03-25 11:00 | 794 | 794
2018-03-25 11:30 | 780 | 780
2018-03-25 12:00 | 769 | 769
2018-03-25 12:30 | 795 | 795
2018-03-25 13:00 | 776 | 773
2018-03-25 13:30 | 769 | 766
2018-03-25 14:00 | 773 | 770
2018-03-25 14:30 | 821 | 815
2018-03-25 15:00 | 828 | 820
2018-03-25 15:30 | 865 | 859
2018-03-25 16:00 | 890 | 885
2018-03-25 16:30 | 916 | 912
2018-03-25 17:00 | 932 | 927
2018-03-25 17:30 | 937 | 933
2018-03-25 18:00 | 940 | 935
2018-03-25 18:30 | 968 | 963
2018-03-25 19:00 | 985 | 982
2018-03-25 19:30 | 965 | 960
2018-03-25 20:00 | 950 | 945
2018-03-25 20:30 | 931 | 926
2018-03-25 21:00 | 894 | 890
2018-03-25 21:30 | 848 | 845
2018-03-25 22:00 | 836 | 832
2018-03-25 22:30 | 816 | 815
2018-03-25 23:00 | 815 | 813
2018-03-25 23:30 | 773 | 770
2018-03-26 | 731 | 724
2018-03-26 00:30 | 694 | 684
2018-03-26 01:00 | 669 | 658
2018-03-26 01:30 | 653 | 641
2018-03-26 02:00 | 649 | 636
2018-03-26 02:30 | 645 | 631
2018-03-26 03:00 | 641 | 627
2018-03-26 03:30 | 643 | 628
2018-03-26 04:00 | 647 | 633
2018-03-26 04:30 | 649 | 637
2018-03-26 05:00 | 670 | 660
2018-03-26 05:30 | 705 | 700
2018-03-26 06:00 | 743 | 741
2018-03-26 06:30 | 805 | 805
2018-03-26 07:00 | 878 | 878
2018-03-26 07:30 | 947 | 947
2018-03-26 08:00 | 967 | 967
2018-03-26 08:30 | 985 | 984
2018-03-26 09:00 | 998 | 996
2018-03-26 09:30 | 1017 | 1016
2018-03-26 10:00 | 1030 | 1030
2018-03-26 10:30 | 1047 | 1046
2018-03-26 11:00 | 1054 | 1053
2018-03-26 11:30 | 1046 | 1046
2018-03-26 12:00 | 1051 | 1051
2018-03-26 12:30 | 1063 | 1062
2018-03-26 13:00 | 1067 | 1067
2018-03-26 13:30 | 1080 | 1080
2018-03-26 14:00 | 1091 | 1091
2018-03-26 14:30 | 1104 | 1104
2018-03-26 15:00 | 1122 | 1122
2018-03-26 15:30 | 1143 | 1143
2018-03-26 16:00 | 1166 | 1165
2018-03-26 16:30 | 1169 | 1169
2018-03-26 17:00 | 1188 | 1188
2018-03-26 17:30 | 1190 | 1190
2018-03-26 18:00 | 1192 | 1192
2018-03-26 18:30 | 1202 | 1202
2018-03-26 19:00 | 1200 | 1200
2018-03-26 19:30 | 1171 | 1170
2018-03-26 20:00 | 1151 | 1150
2018-03-26 20:30 | 1122 | 1120
2018-03-26 21:00 | 1067 | 1065
2018-03-26 21:30 | 1013 | 1011
2018-03-26 22:00 | 966 | 966
2018-03-26 22:30 | 937 | 936
2018-03-26 23:00 | 906 | 903
2018-03-26 23:30 | 835 | 835
2018-03-27 | 784 | 784
2018-03-27 00:30 | 740 | 739
2018-03-27 01:00 | 716 | 714
2018-03-27 01:30 | 706 | 703
2018-03-27 02:00 | 692 | 688
2018-03-27 02:30 | 682 | 678
2018-03-27 03:00 | 676 | 671
2018-03-27 03:30 | 677 | 672
2018-03-27 04:00 | 677 | 672
2018-03-27 04:30 | 684 | 680
2018-03-27 05:00 | 702 | 699
2018-03-27 05:30 | 741 | 740
2018-03-27 06:00 | 783 | 783
2018-03-27 06:30 | 856 | 856
2018-03-27 07:00 | 926 | 926
2018-03-27 07:30 | 1015 | 1014
2018-03-27 08:00 | 1049 | 1047
2018-03-27 08:30 | 1063 | 1062
2018-03-27 09:00 | 1076 | 1076
2018-03-27 09:30 | 1081 | 1081
2018-03-27 10:00 | 1101 | 1100
2018-03-27 10:30 | 1126 | 1125
2018-03-27 11:00 | 1128 | 1126
2018-03-27 11:30 | 1127 | 1125
2018-03-27 12:00 | 1145 | 1143
2018-03-27 12:30 | 1130 | 1128
2018-03-27 13:00 | 1104 | 1102
2018-03-27 13:30 | 1050 | 1047
2018-03-27 14:00 | 1015 | 1010
2018-03-27 14:30 | 1041 | 1037
2018-03-27 15:00 | 1080 | 1077
2018-03-27 15:30 | 1106 | 1104
2018-03-27 16:00 | 1120 | 1118
2018-03-27 16:30 | 1125 | 1122
2018-03-27 17:00 | 1134 | 1131
2018-03-27 17:30 | 1133 | 1128
2018-03-27 18:00 | 1123 | 1114
2018-03-27 18:30 | 1126 | 1116
2018-03-27 19:00 | 1128 | 1117
2018-03-27 19:30 | 1094 | 1081
2018-03-27 20:00 | 1071 | 1063
2018-03-27 20:30 | 1046 | 1038
2018-03-27 21:00 | 994 | 989
2018-03-27 21:30 | 944 | 943
2018-03-27 22:00 | 919 | 918
2018-03-27 22:30 | 880 | 877
2018-03-27 23:00 | 852 | 850
2018-03-27 23:30 | 806 | 803
2018-03-28 | 753 | 749
2018-03-28 00:30 | 712 | 706
2018-03-28 01:00 | 687 | 680
2018-03-28 01:30 | 676 | 668
2018-03-28 02:00 | 668 | 659
2018-03-28 02:30 | 659 | 649
2018-03-28 03:00 | 650 | 639
2018-03-28 03:30 | 652 | 640
2018-03-28 04:00 | 651 | 639
2018-03-28 04:30 | 664 | 654
2018-03-28 05:00 | 706 | 700
2018-03-28 05:30 | 718 | 714
2018-03-28 06:00 | 749 | 745
2018-03-28 06:30 | 805 | 803
2018-03-28 07:00 | 863 | 863
2018-03-28 07:30 | 919 | 919
2018-03-28 08:00 | 941 | 941
2018-03-28 08:30 | 952 | 951
2018-03-28 09:00 | 958 | 958
2018-03-28 09:30 | 951 | 951
2018-03-28 10:00 | 962 | 962
2018-03-28 10:30 | 962 | 962
2018-03-28 11:00 | 962 | 962
2018-03-28 11:30 | 966 | 966
2018-03-28 12:00 | 970 | 970
2018-03-28 12:30 | 961 | 961
2018-03-28 13:00 | 971 | 971
2018-03-28 13:30 | 980 | 980
2018-03-28 14:00 | 1000 | 1000
2018-03-28 14:30 | 1023 | 1023
2018-03-28 15:00 | 1046 | 1046
2018-03-28 15:30 | 1068 | 1068
2018-03-28 16:00 | 1087 | 1086
2018-03-28 16:30 | 1118 | 1117
2018-03-28 17:00 | 1135 | 1133
2018-03-28 17:30 | 1135 | 1133
2018-03-28 18:00 | 1114 | 1111
2018-03-28 18:30 | 1120 | 1117
2018-03-28 19:00 | 1125 | 1121
2018-03-28 19:30 | 1093 | 1087
2018-03-28 20:00 | 1057 | 1056
2018-03-28 20:30 | 1031 | 1029
2018-03-28 21:00 | 986 | 983
2018-03-28 21:30 | 943 | 943
2018-03-28 22:00 | 909 | 909
2018-03-28 22:30 | 878 | 877
2018-03-28 23:00 | 855 | 853
2018-03-28 23:30 | 806 | 803
2018-03-29 | 756 | 751
2018-03-29 00:30 | 708 | 703
2018-03-29 01:00 | 685 | 678
2018-03-29 01:30 | 672 | 664
2018-03-29 02:00 | 661 | 651
2018-03-29 02:30 | 650 | 639
2018-03-29 03:00 | 647 | 636
2018-03-29 03:30 | 641 | 630
2018-03-29 04:00 | 647 | 636
2018-03-29 04:30 | 660 | 651
2018-03-29 05:00 | 679 | 671
2018-03-29 05:30 | 718 | 714
2018-03-29 06:00 | 760 | 755
2018-03-29 06:30 | 817 | 813
2018-03-29 07:00 | 902 | 901
2018-03-29 07:30 | 973 | 972
2018-03-29 08:00 | 985 | 979
2018-03-29 08:30 | 991 | 988
2018-03-29 09:00 | 1005 | 1003
2018-03-29 09:30 | 1011 | 1010
2018-03-29 10:00 | 999 | 998
2018-03-29 10:30 | 998 | 998
2018-03-29 11:00 | 1006 | 1005
2018-03-29 11:30 | 1010 | 1010
2018-03-29 12:00 | 1006 | 1005
2018-03-29 12:30 | 995 | 994
2018-03-29 13:00 | 1004 | 1003
2018-03-29 13:30 | 1001 | 1001
2018-03-29 14:00 | 1009 | 1009
2018-03-29 14:30 | 1019 | 1018
2018-03-29 15:00 | 1029 | 1028
2018-03-29 15:30 | 1033 | 1033
2018-03-29 16:00 | 1041 | 1039
2018-03-29 16:30 | 1055 | 1053
2018-03-29 17:00 | 1069 | 1067
2018-03-29 17:30 | 1069 | 1065
2018-03-29 18:00 | 1068 | 1064
2018-03-29 18:30 | 1072 | 1068
2018-03-29 19:00 | 1082 | 1078
2018-03-29 19:30 | 1052 | 1050
2018-03-29 20:00 | 1029 | 1029
2018-03-29 20:30 | 1004 | 1004
2018-03-29 21:00 | 966 | 965
2018-03-29 21:30 | 926 | 925
2018-03-29 22:00 | 891 | 889
2018-03-29 22:30 | 861 | 858
2018-03-29 23:00 | 842 | 837
2018-03-29 23:30 | 783 | 778
2018-03-30 | 736 | 730
2018-03-30 00:30 | 694 | 684
2018-03-30 01:00 | 667 | 657
2018-03-30 01:30 | 652 | 639
2018-03-30 02:00 | 640 | 626
2018-03-30 02:30 | 627 | 612
2018-03-30 03:00 | 623 | 606
2018-03-30 03:30 | 620 | 603
2018-03-30 04:00 | 615 | 597
2018-03-30 04:30 | 612 | 594
2018-03-30 05:00 | 616 | 598
2018-03-30 05:30 | 627 | 611
2018-03-30 06:00 | 634 | 619
2018-03-30 06:30 | 652 | 639
2018-03-30 07:00 | 680 | 669
2018-03-30 07:30 | 710 | 703
2018-03-30 08:00 | 724 | 720
2018-03-30 08:30 | 752 | 750
2018-03-30 09:00 | 771 | 770
2018-03-30 09:30 | 781 | 781
2018-03-30 10:00 | 782 | 781
2018-03-30 10:30 | 803 | 802
2018-03-30 11:00 | 804 | 803
2018-03-30 11:30 | 780 | 778
2018-03-30 12:00 | 785 | 784
2018-03-30 12:30 | 793 | 792
2018-03-30 13:00 | 795 | 794
2018-03-30 13:30 | 794 | 793
2018-03-30 14:00 | 804 | 804
2018-03-30 14:30 | 828 | 828
2018-03-30 15:00 | 844 | 843
2018-03-30 15:30 | 852 | 850
2018-03-30 16:00 | 868 | 867
2018-03-30 16:30 | 889 | 888
2018-03-30 17:00 | 909 | 908
2018-03-30 17:30 | 928 | 927
2018-03-30 18:00 | 937 | 936
2018-03-30 18:30 | 963 | 963
2018-03-30 19:00 | 971 | 971
2018-03-30 19:30 | 946 | 945
2018-03-30 20:00 | 936 | 935
2018-03-30 20:30 | 914 | 911
2018-03-30 21:00 | 874 | 874
2018-03-30 21:30 | 851 | 851
2018-03-30 22:00 | 838 | 838
2018-03-30 22:30 | 818 | 817
2018-03-30 23:00 | 805 | 804
2018-03-30 23:30 | 769 | 765
2018-03-31 | 723 | 717
2018-03-31 00:30 | 685 | 676
2018-03-31 01:00 | 659 | 646
2018-03-31 01:30 | 649 | 634
2018-03-31 02:00 | 641 | 625
2018-03-31 02:30 | 634 | 615
2018-03-31 03:00 | 624 | 605
2018-03-31 03:30 | 627 | 608
2018-03-31 04:00 | 625 | 605
2018-03-31 04:30 | 625 | 605
2018-03-31 05:00 | 631 | 612
2018-03-31 05:30 | 639 | 622
2018-03-31 06:00 | 649 | 632
2018-03-31 06:30 | 660 | 643
2018-03-31 07:00 | 672 | 660
2018-03-31 07:30 | 689 | 682
2018-03-31 08:00 | 709 | 705
2018-03-31 08:30 | 734 | 733
2018-03-31 09:00 | 761 | 761
2018-03-31 09:30 | 780 | 780
2018-03-31 10:00 | 768 | 768
2018-03-31 10:30 | 743 | 743
2018-03-31 11:00 | 733 | 733
2018-03-31 11:30 | 728 | 728
2018-03-31 12:00 | 728 | 728
2018-03-31 12:30 | 725 | 725
2018-03-31 13:00 | 733 | 732
2018-03-31 13:30 | 744 | 744
2018-03-31 14:00 | 762 | 762
2018-03-31 14:30 | 775 | 775
2018-03-31 15:00 | 794 | 793
2018-03-31 15:30 | 815 | 815
2018-03-31 16:00 | 845 | 845
2018-03-31 16:30 | 864 | 864
2018-03-31 17:00 | 892 | 891
2018-03-31 17:30 | 898 | 897
2018-03-31 18:00 | 906 | 905
2018-03-31 18:30 | 922 | 922
2018-03-31 19:00 | 923 | 922
2018-03-31 19:30 | 907 | 906
2018-03-31 20:00 | 893 | 890
2018-03-31 20:30 | 869 | 867
2018-03-31 21:00 | 835 | 834
2018-03-31 21:30 | 811 | 811
2018-03-31 22:00 | 793 | 792
2018-03-31 22:30 | 787 | 786
2018-03-31 23:00 | 785 | 784
2018-03-31 23:30 | 741 | 738
2018-04-01 | 697 | 691
2018-04-01 00:30 | 654 | 646
2018-04-01 01:00 | 641 | 629
2018-04-01 01:30 | 631 | 618
2018-04-01 02:00 | 617 | 601
2018-04-01 02:30 | 610 | 592
2018-04-01 03:00 | 600 | 580
2018-04-01 03:30 | 598 | 578
2018-04-01 04:00 | 596 | 576
2018-04-01 04:30 | 598 | 577
2018-04-01 05:00 | 600 | 580
2018-04-01 05:30 | 606 | 586
2018-04-01 06:00 | 611 | 591
2018-04-01 06:30 | 623 | 601
2018-04-01 07:00 | 634 | 616
2018-04-01 07:30 | 650 | 637
2018-04-01 08:00 | 661 | 653
2018-04-01 08:30 | 678 | 675
2018-04-01 09:00 | 697 | 696
2018-04-01 09:30 | 734 | 734
2018-04-01 10:00 | 733 | 732
2018-04-01 10:30 | 730 | 729
2018-04-01 11:00 | 729 | 729
2018-04-01 11:30 | 722 | 721
2018-04-01 12:00 | 720 | 720
2018-04-01 12:30 | 710 | 710
2018-04-01 13:00 | 715 | 715
2018-04-01 13:30 | 726 | 726
2018-04-01 14:00 | 744 | 744
2018-04-01 14:30 | 766 | 766
2018-04-01 15:00 | 785 | 784
2018-04-01 15:30 | 816 | 815
2018-04-01 16:00 | 839 | 836
2018-04-01 16:30 | 863 | 861
2018-04-01 17:00 | 891 | 889
2018-04-01 17:30 | 897 | 895
2018-04-01 18:00 | 899 | 896
2018-04-01 18:30 | 923 | 922
2018-04-01 19:00 | 927 | 925
2018-04-01 19:30 | 917 | 914
2018-04-01 20:00 | 901 | 897
2018-04-01 20:30 | 873 | 873
2018-04-01 21:00 | 841 | 841
2018-04-01 21:30 | 821 | 820
2018-04-01 22:00 | 799 | 797
2018-04-01 22:30 | 794 | 791
2018-04-01 23:00 | 789 | 787
2018-04-01 23:30 | 749 | 746
2018-04-02 | 705 | 699
2018-04-02 00:30 | 665 | 656
2018-04-02 01:00 | 648 | 636
2018-04-02 01:30 | 630 | 617
2018-04-02 02:00 | 623 | 608
2018-04-02 02:30 | 616 | 600
2018-04-02 03:00 | 609 | 592
2018-04-02 03:30 | 607 | 590
2018-04-02 04:00 | 604 | 586
2018-04-02 04:30 | 603 | 586
2018-04-02 05:00 | 609 | 592
2018-04-02 05:30 | 617 | 602
2018-04-02 06:00 | 626 | 613
2018-04-02 06:30 | 645 | 633
2018-04-02 07:00 | 659 | 649
2018-04-02 07:30 | 684 | 680
2018-04-02 08:00 | 704 | 703
2018-04-02 08:30 | 729 | 729
2018-04-02 09:00 | 767 | 766
2018-04-02 09:30 | 780 | 779
2018-04-02 10:00 | 791 | 790
2018-04-02 10:30 | 785 | 785
2018-04-02 11:00 | 780 | 780
2018-04-02 11:30 | 783 | 782
2018-04-02 12:00 | 782 | 781
2018-04-02 12:30 | 772 | 771
2018-04-02 13:00 | 775 | 773
2018-04-02 13:30 | 780 | 779
2018-04-02 14:00 | 796 | 796
2018-04-02 14:30 | 817 | 817
2018-04-02 15:00 | 835 | 835
2018-04-02 15:30 | 862 | 862
2018-04-02 16:00 | 894 | 894
2018-04-02 16:30 | 925 | 925
2018-04-02 17:00 | 949 | 948
2018-04-02 17:30 | 961 | 960
2018-04-02 18:00 | 973 | 971
2018-04-02 18:30 | 987 | 986
2018-04-02 19:00 | 987 | 985
2018-04-02 19:30 | 955 | 951
2018-04-02 20:00 | 931 | 929
2018-04-02 20:30 | 901 | 900
2018-04-02 21:00 | 864 | 863
2018-04-02 21:30 | 829 | 827
2018-04-02 22:00 | 806 | 802
2018-04-02 22:30 | 792 | 789
2018-04-02 23:00 | 785 | 784
2018-04-02 23:30 | 740 | 738
2018-04-03 | 689 | 684
2018-04-03 00:30 | 656 | 650
2018-04-03 01:00 | 634 | 625
2018-04-03 01:30 | 619 | 609
2018-04-03 02:00 | 609 | 598
2018-04-03 02:30 | 607 | 596
2018-04-03 03:00 | 603 | 591
2018-04-03 03:30 | 602 | 589
2018-04-03 04:00 | 605 | 590
2018-04-03 04:30 | 615 | 603
2018-04-03 05:00 | 627 | 618
2018-04-03 05:30 | 658 | 652
2018-04-03 06:00 | 685 | 682
2018-04-03 06:30 | 744 | 743
2018-04-03 07:00 | 793 | 792
2018-04-03 07:30 | 841 | 841
2018-04-03 08:00 | 866 | 866
2018-04-03 08:30 | 903 | 903
2018-04-03 09:00 | 924 | 924
2018-04-03 09:30 | 924 | 922
2018-04-03 10:00 | 899 | 898
2018-04-03 10:30 | 886 | 885
2018-04-03 11:00 | 881 | 880
2018-04-03 11:30 | 870 | 869
2018-04-03 12:00 | 867 | 866
2018-04-03 12:30 | 873 | 872
2018-04-03 13:00 | 883 | 882
2018-04-03 13:30 | 892 | 891
2018-04-03 14:00 | 900 | 900
2018-04-03 14:30 | 911 | 911
2018-04-03 15:00 | 932 | 931
2018-04-03 15:30 | 955 | 955
2018-04-03 16:00 | 977 | 976
2018-04-03 16:30 | 1003 | 1000
2018-04-03 17:00 | 1028 | 1025
2018-04-03 17:30 | 1032 | 1027
2018-04-03 18:00 | 1033 | 1027
2018-04-03 18:30 | 1047 | 1042
2018-04-03 19:00 | 1047 | 1041
2018-04-03 19:30 | 1021 | 1010
2018-04-03 20:00 | 985 | 979
2018-04-03 20:30 | 951 | 948
2018-04-03 21:00 | 900 | 899
2018-04-03 21:30 | 864 | 863
2018-04-03 22:00 | 835 | 831
2018-04-03 22:30 | 807 | 806
2018-04-03 23:00 | 797 | 796
2018-04-03 23:30 | 755 | 754
2018-04-04 | 708 | 705
2018-04-04 00:30 | 663 | 656
2018-04-04 01:00 | 648 | 639
2018-04-04 01:30 | 631 | 621
2018-04-04 02:00 | 625 | 614
2018-04-04 02:30 | 619 | 608
2018-04-04 03:00 | 615 | 603
2018-04-04 03:30 | 612 | 600
2018-04-04 04:00 | 618 | 607
2018-04-04 04:30 | 624 | 615
2018-04-04 05:00 | 633 | 625
2018-04-04 05:30 | 664 | 659
2018-04-04 06:00 | 740 | 739
2018-04-04 06:30 | 760 | 757
2018-04-04 07:00 | 804 | 802
2018-04-04 07:30 | 865 | 865
2018-04-04 08:00 | 889 | 889
2018-04-04 08:30 | 923 | 923
2018-04-04 09:00 | 937 | 937
2018-04-04 09:30 | 921 | 921
2018-04-04 10:00 | 902 | 901
2018-04-04 10:30 | 881 | 880
2018-04-04 11:00 | 883 | 883
2018-04-04 11:30 | 902 | 901
2018-04-04 12:00 | 919 | 919
2018-04-04 12:30 | 892 | 891
2018-04-04 13:00 | 875 | 874
2018-04-04 13:30 | 889 | 889
2018-04-04 14:00 | 906 | 906
2018-04-04 14:30 | 914 | 914
2018-04-04 15:00 | 940 | 940
2018-04-04 15:30 | 945 | 945
2018-04-04 16:00 | 961 | 960
2018-04-04 16:30 | 972 | 972
2018-04-04 17:00 | 990 | 989
2018-04-04 17:30 | 994 | 994
2018-04-04 18:00 | 1011 | 1011
2018-04-04 18:30 | 1021 | 1019
2018-04-04 19:00 | 1019 | 1016
2018-04-04 19:30 | 990 | 985
2018-04-04 20:00 | 970 | 964
2018-04-04 20:30 | 929 | 929
2018-04-04 21:00 | 886 | 885
2018-04-04 21:30 | 859 | 859
2018-04-04 22:00 | 826 | 825
2018-04-04 22:30 | 824 | 822
2018-04-04 23:00 | 825 | 824
2018-04-04 23:30 | 783 | 782
2018-04-05 | 726 | 724
2018-04-05 00:30 | 682 | 678
2018-04-05 01:00 | 662 | 654
2018-04-05 01:30 | 640 | 631
2018-04-05 02:00 | 631 | 620
2018-04-05 02:30 | 616 | 606
2018-04-05 03:00 | 609 | 598
2018-04-05 03:30 | 607 | 595
2018-04-05 04:00 | 610 | 599
2018-04-05 04:30 | 617 | 608
2018-04-05 05:00 | 634 | 626
2018-04-05 05:30 | 663 | 659
2018-04-05 06:00 | 693 | 690
2018-04-05 06:30 | 741 | 740
2018-04-05 07:00 | 779 | 779
2018-04-05 07:30 | 826 | 826
2018-04-05 08:00 | 853 | 853
2018-04-05 08:30 | 863 | 863
2018-04-05 09:00 | 859 | 859
2018-04-05 09:30 | 864 | 864
2018-04-05 10:00 | 860 | 860
2018-04-05 10:30 | 850 | 850
2018-04-05 11:00 | 851 | 851
2018-04-05 11:30 | 873 | 873
2018-04-05 12:00 | 877 | 877
2018-04-05 12:30 | 872 | 872
2018-04-05 13:00 | 889 | 889
2018-04-05 13:30 | 909 | 909
2018-04-05 14:00 | 910 | 910
2018-04-05 14:30 | 925 | 925
2018-04-05 15:00 | 911 | 909
2018-04-05 15:30 | 927 | 926
2018-04-05 16:00 | 956 | 955
2018-04-05 16:30 | 968 | 967
2018-04-05 17:00 | 981 | 980
2018-04-05 17:30 | 984 | 982
2018-04-05 18:00 | 995 | 993
2018-04-05 18:30 | 1008 | 1006
2018-04-05 19:00 | 1006 | 1003
2018-04-05 19:30 | 983 | 978
2018-04-05 20:00 | 972 | 965
2018-04-05 20:30 | 940 | 937
2018-04-05 21:00 | 901 | 900
2018-04-05 21:30 | 863 | 862
2018-04-05 22:00 | 828 | 825
2018-04-05 22:30 | 814 | 813
2018-04-05 23:00 | 800 | 800
2018-04-05 23:30 | 763 | 763
2018-04-06 | 705 | 702
2018-04-06 00:30 | 662 | 657
2018-04-06 01:00 | 642 | 635
2018-04-06 01:30 | 628 | 618
2018-04-06 02:00 | 616 | 605
2018-04-06 02:30 | 612 | 599
2018-04-06 03:00 | 604 | 591
2018-04-06 03:30 | 604 | 591
2018-04-06 04:00 | 605 | 593
2018-04-06 04:30 | 614 | 603
2018-04-06 05:00 | 627 | 618
2018-04-06 05:30 | 660 | 655
2018-04-06 06:00 | 686 | 682
2018-04-06 06:30 | 733 | 731
2018-04-06 07:00 | 780 | 777
2018-04-06 07:30 | 806 | 805
2018-04-06 08:00 | 832 | 831
2018-04-06 08:30 | 840 | 839
2018-04-06 09:00 | 842 | 842
2018-04-06 09:30 | 851 | 851
2018-04-06 10:00 | 865 | 862
2018-04-06 10:30 | 875 | 868
2018-04-06 11:00 | 855 | 848
2018-04-06 11:30 | 828 | 822
2018-04-06 12:00 | 820 | 813
2018-04-06 12:30 | 804 | 800
2018-04-06 13:00 | 803 | 800
2018-04-06 13:30 | 818 | 816
2018-04-06 14:00 | 834 | 833
2018-04-06 14:30 | 865 | 864
2018-04-06 15:00 | 900 | 900
2018-04-06 15:30 | 930 | 930
2018-04-06 16:00 | 960 | 959
2018-04-06 16:30 | 983 | 981
2018-04-06 17:00 | 994 | 992
2018-04-06 17:30 | 989 | 985
2018-04-06 18:00 | 985 | 981
2018-04-06 18:30 | 993 | 989
2018-04-06 19:00 | 993 | 987
2018-04-06 19:30 | 965 | 963
2018-04-06 20:00 | 942 | 940
2018-04-06 20:30 | 920 | 918
2018-04-06 21:00 | 885 | 884
2018-04-06 21:30 | 861 | 860
2018-04-06 22:00 | 835 | 832
2018-04-06 22:30 | 825 | 821
2018-04-06 23:00 | 817 | 815
2018-04-06 23:30 | 775 | 772
2018-04-07 | 716 | 714
2018-04-07 00:30 | 671 | 666
2018-04-07 01:00 | 650 | 643
2018-04-07 01:30 | 638 | 629
2018-04-07 02:00 | 621 | 611
2018-04-07 02:30 | 613 | 601
2018-04-07 03:00 | 604 | 592
2018-04-07 03:30 | 606 | 594
2018-04-07 04:00 | 603 | 589
2018-04-07 04:30 | 610 | 597
2018-04-07 05:00 | 608 | 594
2018-04-07 05:30 | 623 | 611
2018-04-07 06:00 | 636 | 625
2018-04-07 06:30 | 653 | 643
2018-04-07 07:00 | 660 | 652
2018-04-07 07:30 | 685 | 682
2018-04-07 08:00 | 700 | 698
2018-04-07 08:30 | 714 | 714
2018-04-07 09:00 | 728 | 728
2018-04-07 09:30 | 749 | 749
2018-04-07 10:00 | 744 | 740
2018-04-07 10:30 | 733 | 728
2018-04-07 11:00 | 740 | 735
2018-04-07 11:30 | 727 | 722
2018-04-07 12:00 | 721 | 716
2018-04-07 12:30 | 723 | 718
2018-04-07 13:00 | 741 | 737
2018-04-07 13:30 | 753 | 749
2018-04-07 14:00 | 748 | 744
2018-04-07 14:30 | 766 | 762
2018-04-07 15:00 | 778 | 775
2018-04-07 15:30 | 807 | 805
2018-04-07 16:00 | 837 | 835
2018-04-07 16:30 | 869 | 867
2018-04-07 17:00 | 902 | 901
2018-04-07 17:30 | 889 | 886
2018-04-07 18:00 | 909 | 908
2018-04-07 18:30 | 955 | 953
2018-04-07 19:00 | 954 | 951
2018-04-07 19:30 | 919 | 917
2018-04-07 20:00 | 893 | 892
2018-04-07 20:30 | 866 | 865
2018-04-07 21:00 | 833 | 833
2018-04-07 21:30 | 813 | 813
2018-04-07 22:00 | 787 | 787
2018-04-07 22:30 | 783 | 782
2018-04-07 23:00 | 781 | 781
2018-04-07 23:30 | 737 | 735
2018-04-08 | 693 | 688
2018-04-08 00:30 | 649 | 641
2018-04-08 01:00 | 631 | 619
2018-04-08 01:30 | 617 | 606
2018-04-08 02:00 | 609 | 594
2018-04-08 02:30 | 597 | 580
2018-04-08 03:00 | 594 | 576
2018-04-08 03:30 | 592 | 571
2018-04-08 04:00 | 593 | 572
2018-04-08 04:30 | 593 | 571
2018-04-08 05:00 | 592 | 571
2018-04-08 05:30 | 604 | 585
2018-04-08 06:00 | 616 | 597
2018-04-08 06:30 | 633 | 611
2018-04-08 07:00 | 640 | 619
2018-04-08 07:30 | 619 | 604
2018-04-08 08:00 | 625 | 614
2018-04-08 08:30 | 636 | 629
2018-04-08 09:00 | 643 | 639
2018-04-08 09:30 | 670 | 669
2018-04-08 10:00 | 686 | 685
2018-04-08 10:30 | 660 | 660
2018-04-08 11:00 | 679 | 679
2018-04-08 11:30 | 688 | 688
2018-04-08 12:00 | 666 | 666
2018-04-08 12:30 | 667 | 667
2018-04-08 13:00 | 685 | 685
2018-04-08 13:30 | 693 | 693
2018-04-08 14:00 | 700 | 700
2018-04-08 14:30 | 727 | 727
2018-04-08 15:00 | 763 | 763
2018-04-08 15:30 | 790 | 790
2018-04-08 16:00 | 822 | 822
2018-04-08 16:30 | 850 | 849
2018-04-08 17:00 | 884 | 884
2018-04-08 17:30 | 899 | 899
2018-04-08 18:00 | 921 | 921
2018-04-08 18:30 | 950 | 945
2018-04-08 19:00 | 944 | 937
2018-04-08 19:30 | 918 | 910
2018-04-08 20:00 | 896 | 890
2018-04-08 20:30 | 873 | 868
2018-04-08 21:00 | 847 | 839
2018-04-08 21:30 | 818 | 812
2018-04-08 22:00 | 797 | 790
2018-04-08 22:30 | 787 | 776
2018-04-08 23:00 | 785 | 773
2018-04-08 23:30 | 744 | 733
2018-04-09 | 693 | 685
2018-04-09 00:30 | 657 | 645
2018-04-09 01:00 | 634 | 618
2018-04-09 01:30 | 619 | 601
2018-04-09 02:00 | 609 | 589
2018-04-09 02:30 | 604 | 583
2018-04-09 03:00 | 598 | 577
2018-04-09 03:30 | 599 | 577
2018-04-09 04:00 | 605 | 584
2018-04-09 04:30 | 612 | 594
2018-04-09 05:00 | 626 | 610
2018-04-09 05:30 | 652 | 642
2018-04-09 06:00 | 686 | 679
2018-04-09 06:30 | 734 | 732
2018-04-09 07:00 | 780 | 780
2018-04-09 07:30 | 815 | 812
2018-04-09 08:00 | 831 | 829
2018-04-09 08:30 | 842 | 841
2018-04-09 09:00 | 845 | 845
2018-04-09 09:30 | 850 | 850
2018-04-09 10:00 | 849 | 848
2018-04-09 10:30 | 854 | 854
2018-04-09 11:00 | 842 | 842
2018-04-09 11:30 | 837 | 837
2018-04-09 12:00 | 840 | 840
2018-04-09 12:30 | 843 | 842
2018-04-09 13:00 | 854 | 854
2018-04-09 13:30 | 874 | 873
2018-04-09 14:00 | 892 | 892
2018-04-09 14:30 | 914 | 914
2018-04-09 15:00 | 938 | 938
2018-04-09 15:30 | 965 | 965
2018-04-09 16:00 | 999 | 998
2018-04-09 16:30 | 1020 | 1019
2018-04-09 17:00 | 1047 | 1047
2018-04-09 17:30 | 1050 | 1048
2018-04-09 18:00 | 1051 | 1048
2018-04-09 18:30 | 1052 | 1049
2018-04-09 19:00 | 1037 | 1032
2018-04-09 19:30 | 1002 | 993
2018-04-09 20:00 | 969 | 962
2018-04-09 20:30 | 948 | 936
2018-04-09 21:00 | 896 | 889
2018-04-09 21:30 | 854 | 850
2018-04-09 22:00 | 829 | 827
2018-04-09 22:30 | 815 | 811
2018-04-09 23:00 | 812 | 807
2018-04-09 23:30 | 766 | 758
2018-04-10 | 719 | 707
2018-04-10 00:30 | 672 | 661
2018-04-10 01:00 | 644 | 634
2018-04-10 01:30 | 631 | 618
2018-04-10 02:00 | 622 | 606
2018-04-10 02:30 | 611 | 594
2018-04-10 03:00 | 609 | 592
2018-04-10 03:30 | 612 | 594
2018-04-10 04:00 | 615 | 598
2018-04-10 04:30 | 617 | 601
2018-04-10 05:00 | 629 | 616
2018-04-10 05:30 | 659 | 651
2018-04-10 06:00 | 683 | 678
2018-04-10 06:30 | 731 | 728
2018-04-10 07:00 | 766 | 762
2018-04-10 07:30 | 797 | 794
2018-04-10 08:00 | 812 | 809
2018-04-10 08:30 | 821 | 820
2018-04-10 09:00 | 828 | 827
2018-04-10 09:30 | 830 | 829
2018-04-10 10:00 | 835 | 835
2018-04-10 10:30 | 847 | 847
2018-04-10 11:00 | 849 | 849
2018-04-10 11:30 | 853 | 853
2018-04-10 12:00 | 868 | 867
2018-04-10 12:30 | 872 | 871
2018-04-10 13:00 | 879 | 878
2018-04-10 13:30 | 907 | 907
2018-04-10 14:00 | 947 | 947
2018-04-10 14:30 | 961 | 960
2018-04-10 15:00 | 971 | 969
2018-04-10 15:30 | 981 | 979
2018-04-10 16:00 | 997 | 994
2018-04-10 16:30 | 1006 | 1003
2018-04-10 17:00 | 1022 | 1019
2018-04-10 17:30 | 1028 | 1021
2018-04-10 18:00 | 1027 | 1023
2018-04-10 18:30 | 1031 | 1028
2018-04-10 19:00 | 1026 | 1022
2018-04-10 19:30 | 995 | 987
2018-04-10 20:00 | 968 | 960
2018-04-10 20:30 | 943 | 936
2018-04-10 21:00 | 898 | 894
2018-04-10 21:30 | 861 | 857
2018-04-10 22:00 | 838 | 835
2018-04-10 22:30 | 820 | 818
2018-04-10 23:00 | 818 | 815
2018-04-10 23:30 | 776 | 771
2018-04-11 | 728 | 721
2018-04-11 00:30 | 678 | 673
2018-04-11 01:00 | 648 | 642
2018-04-11 01:30 | 635 | 628
2018-04-11 02:00 | 624 | 615
2018-04-11 02:30 | 612 | 601
2018-04-11 03:00 | 611 | 599
2018-04-11 03:30 | 615 | 603
2018-04-11 04:00 | 618 | 606
2018-04-11 04:30 | 627 | 616
2018-04-11 05:00 | 636 | 626
2018-04-11 05:30 | 668 | 663
2018-04-11 06:00 | 698 | 695
2018-04-11 06:30 | 743 | 741
2018-04-11 07:00 | 777 | 777
2018-04-11 07:30 | 823 | 822
2018-04-11 08:00 | 844 | 844
2018-04-11 08:30 | 856 | 856
2018-04-11 09:00 | 865 | 863
2018-04-11 09:30 | 866 | 861
2018-04-11 10:00 | 856 | 851
2018-04-11 10:30 | 847 | 844
2018-04-11 11:00 | 846 | 843
2018-04-11 11:30 | 833 | 829
2018-04-11 12:00 | 825 | 821
2018-04-11 12:30 | 823 | 819
2018-04-11 13:00 | 822 | 819
2018-04-11 13:30 | 826 | 823
2018-04-11 14:00 | 839 | 836
2018-04-11 14:30 | 857 | 855
2018-04-11 15:00 | 897 | 896
2018-04-11 15:30 | 918 | 916
2018-04-11 16:00 | 942 | 940
2018-04-11 16:30 | 946 | 944
2018-04-11 17:00 | 958 | 954
2018-04-11 17:30 | 958 | 951
2018-04-11 18:00 | 964 | 960
2018-04-11 18:30 | 981 | 978
2018-04-11 19:00 | 975 | 971
2018-04-11 19:30 | 948 | 946
2018-04-11 20:00 | 917 | 917
2018-04-11 20:30 | 895 | 895
2018-04-11 21:00 | 856 | 856
2018-04-11 21:30 | 818 | 818
2018-04-11 22:00 | 794 | 793
2018-04-11 22:30 | 777 | 776
2018-04-11 23:00 | 789 | 788
2018-04-11 23:30 | 739 | 737
2018-04-12 | 693 | 689
2018-04-12 00:30 | 653 | 645
2018-04-12 01:00 | 639 | 627
2018-04-12 01:30 | 616 | 603
2018-04-12 02:00 | 609 | 595
2018-04-12 02:30 | 602 | 588
2018-04-12 03:00 | 601 | 587
2018-04-12 03:30 | 601 | 586
2018-04-12 04:00 | 603 | 590
2018-04-12 04:30 | 614 | 601
2018-04-12 05:00 | 623 | 612
2018-04-12 05:30 | 655 | 649
2018-04-12 06:00 | 689 | 685
2018-04-12 06:30 | 735 | 733
2018-04-12 07:00 | 773 | 773
2018-04-12 07:30 | 811 | 811
2018-04-12 08:00 | 833 | 833
2018-04-12 08:30 | 856 | 856
2018-04-12 09:00 | 862 | 862
2018-04-12 09:30 | 853 | 853
2018-04-12 10:00 | 849 | 849
2018-04-12 10:30 | 845 | 843
2018-04-12 11:00 | 862 | 860
2018-04-12 11:30 | 853 | 851
2018-04-12 12:00 | 846 | 844
2018-04-12 12:30 | 849 | 846
2018-04-12 13:00 | 857 | 854
2018-04-12 13:30 | 873 | 870
2018-04-12 14:00 | 878 | 876
2018-04-12 14:30 | 892 | 890
2018-04-12 15:00 | 894 | 892
2018-04-12 15:30 | 921 | 920
2018-04-12 16:00 | 944 | 943
2018-04-12 16:30 | 904 | 901
2018-04-12 17:00 | 963 | 961
2018-04-12 17:30 | 983 | 981
2018-04-12 18:00 | 1002 | 1001
2018-04-12 18:30 | 1023 | 1020
2018-04-12 19:00 | 1012 | 1007
2018-04-12 19:30 | 989 | 984
2018-04-12 20:00 | 966 | 962
2018-04-12 20:30 | 937 | 934
2018-04-12 21:00 | 892 | 891
2018-04-12 21:30 | 857 | 857
2018-04-12 22:00 | 828 | 826
2018-04-12 22:30 | 813 | 810
2018-04-12 23:00 | 799 | 797
2018-04-12 23:30 | 751 | 749
2018-04-13 | 709 | 703
2018-04-13 00:30 | 664 | 655
2018-04-13 01:00 | 642 | 633
2018-04-13 01:30 | 622 | 612
2018-04-13 02:00 | 613 | 602
2018-04-13 02:30 | 598 | 586
2018-04-13 03:00 | 596 | 584
2018-04-13 03:30 | 599 | 586
2018-04-13 04:00 | 606 | 593
2018-04-13 04:30 | 610 | 597
2018-04-13 05:00 | 623 | 612
2018-04-13 05:30 | 651 | 645
2018-04-13 06:00 | 692 | 688
2018-04-13 06:30 | 737 | 733
2018-04-13 07:00 | 770 | 767
2018-04-13 07:30 | 817 | 815
2018-04-13 08:00 | 846 | 846
2018-04-13 08:30 | 862 | 860
2018-04-13 09:00 | 860 | 859
2018-04-13 09:30 | 875 | 874
2018-04-13 10:00 | 873 | 872
2018-04-13 10:30 | 866 | 866
2018-04-13 11:00 | 855 | 854
2018-04-13 11:30 | 838 | 836
2018-04-13 12:00 | 806 | 805
2018-04-13 12:30 | 781 | 779
2018-04-13 13:00 | 801 | 799
2018-04-13 13:30 | 870 | 869
2018-04-13 14:00 | 876 | 874
2018-04-13 14:30 | 882 | 881
2018-04-13 15:00 | 903 | 902
2018-04-13 15:30 | 922 | 921
2018-04-13 16:00 | 936 | 935
2018-04-13 16:30 | 968 | 967
2018-04-13 17:00 | 962 | 961
2018-04-13 17:30 | 970 | 967
2018-04-13 18:00 | 972 | 969
2018-04-13 18:30 | 959 | 956
2018-04-13 19:00 | 968 | 964
2018-04-13 19:30 | 946 | 943
2018-04-13 20:00 | 934 | 934
2018-04-13 20:30 | 917 | 915
2018-04-13 21:00 | 884 | 882
2018-04-13 21:30 | 850 | 849
2018-04-13 22:00 | 833 | 831
2018-04-13 22:30 | 821 | 819
2018-04-13 23:00 | 817 | 816
2018-04-13 23:30 | 775 | 772
2018-04-14 | 729 | 724
2018-04-14 00:30 | 688 | 677
2018-04-14 01:00 | 667 | 655
2018-04-14 01:30 | 650 | 636
2018-04-14 02:00 | 638 | 621
2018-04-14 02:30 | 622 | 601
2018-04-14 03:00 | 607 | 584
2018-04-14 03:30 | 597 | 573
2018-04-14 04:00 | 536 | 512
2018-04-14 04:30 | 541 | 518
2018-04-14 05:00 | 530 | 505
2018-04-14 05:30 | 540 | 519
2018-04-14 06:00 | 572 | 556
2018-04-14 06:30 | 638 | 626
2018-04-14 07:00 | 644 | 634
2018-04-14 07:30 | 669 | 665
2018-04-14 08:00 | 663 | 662
2018-04-14 08:30 | 686 | 686
2018-04-14 09:00 | 724 | 724
2018-04-14 09:30 | 793 | 793
2018-04-14 10:00 | 837 | 836
2018-04-14 10:30 | 841 | 841
2018-04-14 11:00 | 839 | 839
2018-04-14 11:30 | 838 | 838
2018-04-14 12:00 | 822 | 821
2018-04-14 12:30 | 788 | 787
2018-04-14 13:00 | 798 | 797
2018-04-14 13:30 | 788 | 787
2018-04-14 14:00 | 787 | 785
2018-04-14 14:30 | 739 | 736
2018-04-14 15:00 | 751 | 749
2018-04-14 15:30 | 777 | 776
2018-04-14 16:00 | 827 | 826
2018-04-14 16:30 | 852 | 851
2018-04-14 17:00 | 870 | 870
2018-04-14 17:30 | 888 | 886
2018-04-14 18:00 | 907 | 906
2018-04-14 18:30 | 908 | 907
2018-04-14 19:00 | 897 | 894
2018-04-14 19:30 | 837 | 834
2018-04-14 20:00 | 853 | 853
2018-04-14 20:30 | 877 | 877
2018-04-14 21:00 | 852 | 852
2018-04-14 21:30 | 825 | 824
2018-04-14 22:00 | 803 | 803
2018-04-14 22:30 | 804 | 804
2018-04-14 23:00 | 802 | 802
2018-04-14 23:30 | 750 | 747
2018-04-15 | 717 | 712
2018-04-15 00:30 | 659 | 650
2018-04-15 01:00 | 652 | 641
2018-04-15 01:30 | 623 | 609
2018-04-15 02:00 | 583 | 564
2018-04-15 02:30 | 588 | 568
2018-04-15 03:00 | 522 | 496
2018-04-15 03:30 | 486 | 458
2018-04-15 04:00 | 520 | 491
2018-04-15 04:30 | 511 | 481
2018-04-15 05:00 | 521 | 493
2018-04-15 05:30 | 548 | 523
2018-04-15 06:00 | 568 | 544
2018-04-15 06:30 | 633 | 611
2018-04-15 07:00 | 643 | 623
2018-04-15 07:30 | 646 | 632
2018-04-15 08:00 | 643 | 633
2018-04-15 08:30 | 651 | 647
2018-04-15 09:00 | 661 | 660
2018-04-15 09:30 | 670 | 670
2018-04-15 10:00 | 678 | 678
2018-04-15 10:30 | 687 | 687
2018-04-15 11:00 | 682 | 681
2018-04-15 11:30 | 693 | 693
2018-04-15 12:00 | 714 | 714
2018-04-15 12:30 | 731 | 731
2018-04-15 13:00 | 765 | 765
2018-04-15 13:30 | 803 | 803
2018-04-15 14:00 | 842 | 842
2018-04-15 14:30 | 891 | 891
2018-04-15 15:00 | 912 | 912
2018-04-15 15:30 | 928 | 928
2018-04-15 16:00 | 964 | 964
2018-04-15 16:30 | 988 | 987
2018-04-15 17:00 | 1013 | 1012
2018-04-15 17:30 | 1007 | 1001
2018-04-15 18:00 | 1027 | 1023
2018-04-15 18:30 | 1056 | 1053
2018-04-15 19:00 | 1057 | 1053
2018-04-15 19:30 | 1015 | 1011
2018-04-15 20:00 | 982 | 980
2018-04-15 20:30 | 952 | 950
2018-04-15 21:00 | 899 | 899
2018-04-15 21:30 | 861 | 860
2018-04-15 22:00 | 784 | 782
2018-04-15 22:30 | 825 | 821
2018-04-15 23:00 | 830 | 825
2018-04-15 23:30 | 768 | 763
2018-04-16 | 713 | 707
2018-04-16 00:30 | 668 | 655
2018-04-16 01:00 | 653 | 636
2018-04-16 01:30 | 587 | 567
2018-04-16 02:00 | 569 | 548
2018-04-16 02:30 | 601 | 580
2018-04-16 03:00 | 612 | 591
2018-04-16 03:30 | 608 | 587
2018-04-16 04:00 | 606 | 585
2018-04-16 04:30 | 614 | 594
2018-04-16 05:00 | 624 | 608
2018-04-16 05:30 | 652 | 641
2018-04-16 06:00 | 684 | 677
2018-04-16 06:30 | 725 | 721
2018-04-16 07:00 | 760 | 758
2018-04-16 07:30 | 800 | 799
2018-04-16 08:00 | 811 | 811
2018-04-16 08:30 | 824 | 824
2018-04-16 09:00 | 836 | 836
2018-04-16 09:30 | 834 | 834
2018-04-16 10:00 | 836 | 836
2018-04-16 10:30 | 839 | 839
2018-04-16 11:00 | 842 | 842
2018-04-16 11:30 | 845 | 845
2018-04-16 12:00 | 856 | 855
2018-04-16 12:30 | 861 | 860
2018-04-16 13:00 | 886 | 886
2018-04-16 13:30 | 902 | 902
2018-04-16 14:00 | 926 | 926
2018-04-16 14:30 | 953 | 953
2018-04-16 15:00 | 990 | 990
2018-04-16 15:30 | 1026 | 1026
2018-04-16 16:00 | 1051 | 1050
2018-04-16 16:30 | 1075 | 1075
2018-04-16 17:00 | 1091 | 1090
2018-04-16 17:30 | 1087 | 1084
2018-04-16 18:00 | 1101 | 1099
2018-04-16 18:30 | 1103 | 1099
2018-04-16 19:00 | 1088 | 1083
2018-04-16 19:30 | 1072 | 1066
2018-04-16 20:00 | 1048 | 1046
2018-04-16 20:30 | 1023 | 1021
2018-04-16 21:00 | 962 | 962
2018-04-16 21:30 | 920 | 919
2018-04-16 22:00 | 893 | 891
2018-04-16 22:30 | 859 | 857
2018-04-16 23:00 | 827 | 823
2018-04-16 23:30 | 780 | 772
2018-04-17 | 738 | 726
2018-04-17 00:30 | 683 | 667
2018-04-17 01:00 | 653 | 635
2018-04-17 01:30 | 641 | 620
2018-04-17 02:00 | 624 | 604
2018-04-17 02:30 | 606 | 589
2018-04-17 03:00 | 606 | 588
2018-04-17 03:30 | 605 | 587
2018-04-17 04:00 | 610 | 592
2018-04-17 04:30 | 614 | 595
2018-04-17 05:00 | 627 | 612
2018-04-17 05:30 | 661 | 651
2018-04-17 06:00 | 693 | 686
2018-04-17 06:30 | 745 | 742
2018-04-17 07:00 | 770 | 769
2018-04-17 07:30 | 794 | 793
2018-04-17 08:00 | 793 | 793
2018-04-17 08:30 | 790 | 790
2018-04-17 09:00 | 780 | 780
2018-04-17 09:30 | 785 | 785
2018-04-17 10:00 | 787 | 787
2018-04-17 10:30 | 783 | 783
2018-04-17 11:00 | 786 | 786
2018-04-17 11:30 | 795 | 794
2018-04-17 12:00 | 812 | 812
2018-04-17 12:30 | 826 | 825
2018-04-17 13:00 | 849 | 849
2018-04-17 13:30 | 860 | 860
2018-04-17 14:00 | 875 | 875
2018-04-17 14:30 | 906 | 905
2018-04-17 15:00 | 928 | 927
2018-04-17 15:30 | 964 | 963
2018-04-17 16:00 | 1011 | 1009
2018-04-17 16:30 | 1052 | 1051
2018-04-17 17:00 | 1077 | 1075
2018-04-17 17:30 | 1080 | 1076
2018-04-17 18:00 | 1097 | 1095
2018-04-17 18:30 | 1094 | 1090
2018-04-17 19:00 | 1082 | 1075
2018-04-17 19:30 | 1050 | 1042
2018-04-17 20:00 | 1028 | 1022
2018-04-17 20:30 | 998 | 992
2018-04-17 21:00 | 952 | 949
2018-04-17 21:30 | 917 | 915
2018-04-17 22:00 | 886 | 883
2018-04-17 22:30 | 853 | 851
2018-04-17 23:00 | 822 | 821
2018-04-17 23:30 | 771 | 770
2018-04-18 | 717 | 714
2018-04-18 00:30 | 674 | 668
2018-04-18 01:00 | 656 | 647
2018-04-18 01:30 | 641 | 631
2018-04-18 02:00 | 631 | 619
2018-04-18 02:30 | 627 | 615
2018-04-18 03:00 | 626 | 612
2018-04-18 03:30 | 623 | 608
2018-04-18 04:00 | 627 | 612
2018-04-18 04:30 | 631 | 618
2018-04-18 05:00 | 646 | 636
2018-04-18 05:30 | 679 | 674
2018-04-18 06:00 | 751 | 748
2018-04-18 06:30 | 785 | 783
2018-04-18 07:00 | 841 | 839
2018-04-18 07:30 | 890 | 887
2018-04-18 08:00 | 914 | 913
2018-04-18 08:30 | 923 | 923
2018-04-18 09:00 | 945 | 944
2018-04-18 09:30 | 951 | 950
2018-04-18 10:00 | 918 | 916
2018-04-18 10:30 | 908 | 907
2018-04-18 11:00 | 921 | 920
2018-04-18 11:30 | 919 | 918
2018-04-18 12:00 | 914 | 913
2018-04-18 12:30 | 905 | 903
2018-04-18 13:00 | 881 | 879
2018-04-18 13:30 | 863 | 861
2018-04-18 14:00 | 859 | 856
2018-04-18 14:30 | 872 | 868
2018-04-18 15:00 | 882 | 878
2018-04-18 15:30 | 895 | 892
2018-04-18 16:00 | 923 | 920
2018-04-18 16:30 | 969 | 966
2018-04-18 17:00 | 1003 | 1001
2018-04-18 17:30 | 1011 | 1009
2018-04-18 18:00 | 1028 | 1026
2018-04-18 18:30 | 1027 | 1025
2018-04-18 19:00 | 1025 | 1021
2018-04-18 19:30 | 994 | 989
2018-04-18 20:00 | 975 | 973
2018-04-18 20:30 | 948 | 947
2018-04-18 21:00 | 886 | 884
2018-04-18 21:30 | 859 | 858
2018-04-18 22:00 | 826 | 824
2018-04-18 22:30 | 798 | 794
2018-04-18 23:00 | 778 | 773
2018-04-18 23:30 | 729 | 722
2018-04-19 | 681 | 675
2018-04-19 00:30 | 636 | 625
2018-04-19 01:00 | 617 | 603
2018-04-19 01:30 | 600 | 584
2018-04-19 02:00 | 582 | 564
2018-04-19 02:30 | 579 | 560
2018-04-19 03:00 | 571 | 553
2018-04-19 03:30 | 576 | 557
2018-04-19 04:00 | 579 | 560
2018-04-19 04:30 | 589 | 571
2018-04-19 05:00 | 604 | 588
2018-04-19 05:30 | 636 | 626
2018-04-19 06:00 | 672 | 666
2018-04-19 06:30 | 744 | 741
2018-04-19 07:00 | 793 | 792
2018-04-19 07:30 | 836 | 834
2018-04-19 08:00 | 846 | 845
2018-04-19 08:30 | 844 | 844
2018-04-19 09:00 | 828 | 827
2018-04-19 09:30 | 826 | 825
2018-04-19 10:00 | 822 | 822
2018-04-19 10:30 | 832 | 832
2018-04-19 11:00 | 841 | 841
2018-04-19 11:30 | 826 | 826
2018-04-19 12:00 | 815 | 815
2018-04-19 12:30 | 830 | 830
2018-04-19 13:00 | 841 | 840
2018-04-19 13:30 | 846 | 846
2018-04-19 14:00 | 853 | 853
2018-04-19 14:30 | 873 | 873
2018-04-19 15:00 | 891 | 890
2018-04-19 15:30 | 911 | 909
2018-04-19 16:00 | 934 | 931
2018-04-19 16:30 | 958 | 955
2018-04-19 17:00 | 979 | 976
2018-04-19 17:30 | 991 | 988
2018-04-19 18:00 | 1013 | 1011
2018-04-19 18:30 | 1009 | 1006
2018-04-19 19:00 | 1004 | 999
2018-04-19 19:30 | 973 | 966
2018-04-19 20:00 | 961 | 959
2018-04-19 20:30 | 931 | 930
2018-04-19 21:00 | 897 | 895
2018-04-19 21:30 | 849 | 844
2018-04-19 22:00 | 821 | 813
2018-04-19 22:30 | 788 | 785
2018-04-19 23:00 | 784 | 783
2018-04-19 23:30 | 738 | 735
2018-04-20 | 697 | 692
2018-04-20 00:30 | 651 | 641
2018-04-20 01:00 | 627 | 614
2018-04-20 01:30 | 606 | 591
2018-04-20 02:00 | 594 | 576
2018-04-20 02:30 | 591 | 572
2018-04-20 03:00 | 591 | 572
2018-04-20 03:30 | 589 | 570
2018-04-20 04:00 | 596 | 576
2018-04-20 04:30 | 604 | 585
2018-04-20 05:00 | 610 | 593
2018-04-20 05:30 | 641 | 630
2018-04-20 06:00 | 681 | 673
2018-04-20 06:30 | 741 | 735
2018-04-20 07:00 | 794 | 793
2018-04-20 07:30 | 840 | 838
2018-04-20 08:00 | 845 | 841
2018-04-20 08:30 | 852 | 842
2018-04-20 09:00 | 855 | 845
2018-04-20 09:30 | 855 | 848
2018-04-20 10:00 | 864 | 860
2018-04-20 10:30 | 864 | 862
2018-04-20 11:00 | 859 | 857
2018-04-20 11:30 | 862 | 858
2018-04-20 12:00 | 904 | 896
2018-04-20 12:30 | 936 | 929
2018-04-20 13:00 | 956 | 948
2018-04-20 13:30 | 957 | 946
2018-04-20 14:00 | 948 | 937
2018-04-20 14:30 | 952 | 941
2018-04-20 15:00 | 956 | 945
2018-04-20 15:30 | 956 | 943
2018-04-20 16:00 | 973 | 961
2018-04-20 16:30 | 983 | 970
2018-04-20 17:00 | 986 | 973
2018-04-20 17:30 | 982 | 968
2018-04-20 18:00 | 980 | 966
2018-04-20 18:30 | 967 | 948
2018-04-20 19:00 | 956 | 937
2018-04-20 19:30 | 918 | 909
2018-04-20 20:00 | 893 | 891
2018-04-20 20:30 | 885 | 883
2018-04-20 21:00 | 845 | 841
2018-04-20 21:30 | 794 | 791
2018-04-20 22:00 | 774 | 774
2018-04-20 22:30 | 765 | 764
2018-04-20 23:00 | 755 | 754
2018-04-20 23:30 | 712 | 709
2018-04-21 | 666 | 660
2018-04-21 00:30 | 630 | 621
2018-04-21 01:00 | 606 | 593
2018-04-21 01:30 | 593 | 578
2018-04-21 02:00 | 573 | 555
2018-04-21 02:30 | 564 | 544
2018-04-21 03:00 | 555 | 533
2018-04-21 03:30 | 554 | 531
2018-04-21 04:00 | 550 | 526
2018-04-21 04:30 | 553 | 527
2018-04-21 05:00 | 548 | 524
2018-04-21 05:30 | 564 | 543
2018-04-21 06:00 | 580 | 563
2018-04-21 06:30 | 611 | 596
2018-04-21 07:00 | 638 | 626
2018-04-21 07:30 | 658 | 652
2018-04-21 08:00 | 671 | 668
2018-04-21 08:30 | 674 | 673
2018-04-21 09:00 | 683 | 683
2018-04-21 09:30 | 677 | 677
2018-04-21 10:00 | 681 | 680
2018-04-21 10:30 | 680 | 679
2018-04-21 11:00 | 690 | 690
2018-04-21 11:30 | 695 | 694
2018-04-21 12:00 | 704 | 703
2018-04-21 12:30 | 704 | 702
2018-04-21 13:00 | 706 | 703
2018-04-21 13:30 | 703 | 699
2018-04-21 14:00 | 733 | 730
2018-04-21 14:30 | 746 | 744
2018-04-21 15:00 | 756 | 754
2018-04-21 15:30 | 765 | 763
2018-04-21 16:00 | 776 | 773
2018-04-21 16:30 | 795 | 792
2018-04-21 17:00 | 815 | 812
2018-04-21 17:30 | 823 | 820
2018-04-21 18:00 | 849 | 847
2018-04-21 18:30 | 854 | 853
2018-04-21 19:00 | 845 | 843
2018-04-21 19:30 | 822 | 818
2018-04-21 20:00 | 809 | 805
2018-04-21 20:30 | 796 | 794
2018-04-21 21:00 | 760 | 759
2018-04-21 21:30 | 735 | 733
2018-04-21 22:00 | 724 | 721
2018-04-21 22:30 | 718 | 715
2018-04-21 23:00 | 723 | 720
2018-04-21 23:30 | 693 | 687
2018-04-22 | 654 | 645
2018-04-22 00:30 | 611 | 596
2018-04-22 01:00 | 583 | 565
2018-04-22 01:30 | 562 | 541
2018-04-22 02:00 | 554 | 529
2018-04-22 02:30 | 547 | 517
2018-04-22 03:00 | 543 | 513
2018-04-22 03:30 | 537 | 507
2018-04-22 04:00 | 530 | 499
2018-04-22 04:30 | 529 | 497
2018-04-22 05:00 | 538 | 506
2018-04-22 05:30 | 545 | 516
2018-04-22 06:00 | 552 | 525
2018-04-22 06:30 | 568 | 543
2018-04-22 07:00 | 585 | 564
2018-04-22 07:30 | 594 | 577
2018-04-22 08:00 | 603 | 592
2018-04-22 08:30 | 624 | 617
2018-04-22 09:00 | 633 | 629
2018-04-22 09:30 | 659 | 658
2018-04-22 10:00 | 671 | 670
2018-04-22 10:30 | 657 | 657
2018-04-22 11:00 | 629 | 628
2018-04-22 11:30 | 661 | 661
2018-04-22 12:00 | 634 | 633
2018-04-22 12:30 | 621 | 620
2018-04-22 13:00 | 628 | 627
2018-04-22 13:30 | 627 | 626
2018-04-22 14:00 | 646 | 645
2018-04-22 14:30 | 652 | 651
2018-04-22 15:00 | 671 | 671
2018-04-22 15:30 | 702 | 701
2018-04-22 16:00 | 734 | 733
2018-04-22 16:30 | 769 | 767
2018-04-22 17:00 | 811 | 809
2018-04-22 17:30 | 839 | 836
2018-04-22 18:00 | 881 | 879
2018-04-22 18:30 | 886 | 882
2018-04-22 19:00 | 876 | 869
2018-04-22 19:30 | 844 | 839
2018-04-22 20:00 | 828 | 826
2018-04-22 20:30 | 812 | 808
2018-04-22 21:00 | 778 | 773
2018-04-22 21:30 | 748 | 744
2018-04-22 22:00 | 728 | 724
2018-04-22 22:30 | 731 | 726
2018-04-22 23:00 | 736 | 731
2018-04-22 23:30 | 705 | 697
2018-04-23 | 675 | 663
2018-04-23 00:30 | 630 | 614
2018-04-23 01:00 | 572 | 547
2018-04-23 01:30 | 555 | 527
2018-04-23 02:00 | 543 | 515
2018-04-23 02:30 | 541 | 511
2018-04-23 03:00 | 540 | 510
2018-04-23 03:30 | 543 | 514
2018-04-23 04:00 | 540 | 510
2018-04-23 04:30 | 539 | 511
2018-04-23 05:00 | 556 | 533
2018-04-23 05:30 | 591 | 576
2018-04-23 06:00 | 632 | 624
2018-04-23 06:30 | 700 | 696
2018-04-23 07:00 | 754 | 751
2018-04-23 07:30 | 796 | 795
2018-04-23 08:00 | 799 | 797
2018-04-23 08:30 | 787 | 784
2018-04-23 09:00 | 772 | 771
2018-04-23 09:30 | 760 | 760
2018-04-23 10:00 | 755 | 754
2018-04-23 10:30 | 754 | 753
2018-04-23 11:00 | 755 | 754
2018-04-23 11:30 | 764 | 763
2018-04-23 12:00 | 772 | 772
2018-04-23 12:30 | 780 | 779
2018-04-23 13:00 | 807 | 806
2018-04-23 13:30 | 828 | 827
2018-04-23 14:00 | 833 | 832
2018-04-23 14:30 | 855 | 854
2018-04-23 15:00 | 846 | 844
2018-04-23 15:30 | 851 | 848
2018-04-23 16:00 | 869 | 866
2018-04-23 16:30 | 900 | 897
2018-04-23 17:00 | 927 | 925
2018-04-23 17:30 | 946 | 943
2018-04-23 18:00 | 980 | 979
2018-04-23 18:30 | 970 | 968
2018-04-23 19:00 | 961 | 957
2018-04-23 19:30 | 925 | 921
2018-04-23 20:00 | 904 | 901
2018-04-23 20:30 | 882 | 880
2018-04-23 21:00 | 839 | 838
2018-04-23 21:30 | 805 | 802
2018-04-23 22:00 | 777 | 773
2018-04-23 22:30 | 753 | 751
2018-04-23 23:00 | 749 | 746
2018-04-23 23:30 | 701 | 697
2018-04-24 | 656 | 649
2018-04-24 00:30 | 612 | 601
2018-04-24 01:00 | 588 | 573
2018-04-24 01:30 | 576 | 559
2018-04-24 02:00 | 563 | 543
2018-04-24 02:30 | 557 | 536
2018-04-24 03:00 | 555 | 532
2018-04-24 03:30 | 557 | 534
2018-04-24 04:00 | 561 | 539
2018-04-24 04:30 | 573 | 552
2018-04-24 05:00 | 581 | 563
2018-04-24 05:30 | 618 | 607
2018-04-24 06:00 | 656 | 650
2018-04-24 06:30 | 722 | 719
2018-04-24 07:00 | 778 | 776
2018-04-24 07:30 | 807 | 806
2018-04-24 08:00 | 843 | 843
2018-04-24 08:30 | 923 | 922
2018-04-24 09:00 | 901 | 900
2018-04-24 09:30 | 888 | 887
2018-04-24 10:00 | 873 | 873
2018-04-24 10:30 | 864 | 864
2018-04-24 11:00 | 859 | 859
2018-04-24 11:30 | 828 | 828
2018-04-24 12:00 | 743 | 743
2018-04-24 12:30 | 873 | 872
2018-04-24 13:00 | 921 | 920
2018-04-24 13:30 | 959 | 957
2018-04-24 14:00 | 957 | 955
2018-04-24 14:30 | 966 | 963
2018-04-24 15:00 | 873 | 870
2018-04-24 15:30 | 869 | 866
2018-04-24 16:00 | 890 | 887
2018-04-24 16:30 | 906 | 902
2018-04-24 17:00 | 928 | 924
2018-04-24 17:30 | 947 | 944
2018-04-24 18:00 | 963 | 961
2018-04-24 18:30 | 955 | 951
2018-04-24 19:00 | 952 | 947
2018-04-24 19:30 | 919 | 914
2018-04-24 20:00 | 895 | 894
2018-04-24 20:30 | 872 | 871
2018-04-24 21:00 | 832 | 831
2018-04-24 21:30 | 796 | 792
2018-04-24 22:00 | 777 | 773
2018-04-24 22:30 | 757 | 750
2018-04-24 23:00 | 753 | 745
2018-04-24 23:30 | 706 | 700
2018-04-25 | 658 | 652
2018-04-25 00:30 | 612 | 600
2018-04-25 01:00 | 589 | 576
2018-04-25 01:30 | 580 | 563
2018-04-25 02:00 | 566 | 547
2018-04-25 02:30 | 559 | 539
2018-04-25 03:00 | 555 | 533
2018-04-25 03:30 | 552 | 528
2018-04-25 04:00 | 549 | 525
2018-04-25 04:30 | 552 | 529
2018-04-25 05:00 | 554 | 533
2018-04-25 05:30 | 560 | 538
2018-04-25 06:00 | 575 | 556
2018-04-25 06:30 | 595 | 576
2018-04-25 07:00 | 608 | 590
2018-04-25 07:30 | 621 | 608
2018-04-25 08:00 | 624 | 613
2018-04-25 08:30 | 631 | 624
2018-04-25 09:00 | 627 | 622
2018-04-25 09:30 | 632 | 630
2018-04-25 10:00 | 630 | 628
2018-04-25 10:30 | 633 | 632
2018-04-25 11:00 | 647 | 647
2018-04-25 11:30 | 642 | 641
2018-04-25 12:00 | 641 | 641
2018-04-25 12:30 | 642 | 642
2018-04-25 13:00 | 652 | 651
2018-04-25 13:30 | 656 | 655
2018-04-25 14:00 | 680 | 680
2018-04-25 14:30 | 701 | 701
2018-04-25 15:00 | 700 | 700
2018-04-25 15:30 | 703 | 702
2018-04-25 16:00 | 738 | 737
2018-04-25 16:30 | 761 | 761
2018-04-25 17:00 | 793 | 793
2018-04-25 17:30 | 820 | 819
2018-04-25 18:00 | 858 | 858
2018-04-25 18:30 | 869 | 869
2018-04-25 19:00 | 866 | 865
2018-04-25 19:30 | 843 | 841
2018-04-25 20:00 | 832 | 830
2018-04-25 20:30 | 816 | 813
2018-04-25 21:00 | 782 | 777
2018-04-25 21:30 | 744 | 742
2018-04-25 22:00 | 722 | 719
2018-04-25 22:30 | 713 | 708
2018-04-25 23:00 | 708 | 703
2018-04-25 23:30 | 671 | 664
2018-04-26 | 639 | 630
2018-04-26 00:30 | 598 | 584
2018-04-26 01:00 | 572 | 555
2018-04-26 01:30 | 561 | 542
2018-04-26 02:00 | 557 | 536
2018-04-26 02:30 | 547 | 524
2018-04-26 03:00 | 549 | 525
2018-04-26 03:30 | 546 | 521
2018-04-26 04:00 | 548 | 523
2018-04-26 04:30 | 558 | 536
2018-04-26 05:00 | 580 | 561
2018-04-26 05:30 | 613 | 601
2018-04-26 06:00 | 651 | 644
2018-04-26 06:30 | 715 | 711
2018-04-26 07:00 | 767 | 765
2018-04-26 07:30 | 817 | 810
2018-04-26 08:00 | 822 | 818
2018-04-26 08:30 | 821 | 809
2018-04-26 09:00 | 809 | 803
2018-04-26 09:30 | 800 | 795
2018-04-26 10:00 | 800 | 795
2018-04-26 10:30 | 790 | 787
2018-04-26 11:00 | 786 | 783
2018-04-26 11:30 | 782 | 780
2018-04-26 12:00 | 780 | 777
2018-04-26 12:30 | 770 | 767
2018-04-26 13:00 | 792 | 789
2018-04-26 13:30 | 826 | 823
2018-04-26 14:00 | 847 | 844
2018-04-26 14:30 | 827 | 823
2018-04-26 15:00 | 838 | 833
2018-04-26 15:30 | 860 | 855
2018-04-26 16:00 | 904 | 900
2018-04-26 16:30 | 931 | 927
2018-04-26 17:00 | 958 | 953
2018-04-26 17:30 | 965 | 960
2018-04-26 18:00 | 993 | 990
2018-04-26 18:30 | 988 | 984
2018-04-26 19:00 | 987 | 982
2018-04-26 19:30 | 964 | 955
2018-04-26 20:00 | 947 | 940
2018-04-26 20:30 | 926 | 919
2018-04-26 21:00 | 885 | 879
2018-04-26 21:30 | 833 | 827
2018-04-26 22:00 | 787 | 785
2018-04-26 22:30 | 772 | 768
2018-04-26 23:00 | 755 | 751
2018-04-26 23:30 | 708 | 706
2018-04-27 | 667 | 663
2018-04-27 00:30 | 621 | 612
2018-04-27 01:00 | 597 | 585
2018-04-27 01:30 | 578 | 564
2018-04-27 02:00 | 567 | 551
2018-04-27 02:30 | 562 | 545
2018-04-27 03:00 | 560 | 542
2018-04-27 03:30 | 558 | 540
2018-04-27 04:00 | 556 | 539
2018-04-27 04:30 | 567 | 552
2018-04-27 05:00 | 581 | 568
2018-04-27 05:30 | 614 | 606
2018-04-27 06:00 | 644 | 639
2018-04-27 06:30 | 708 | 706
2018-04-27 07:00 | 763 | 759
2018-04-27 07:30 | 810 | 807
2018-04-27 08:00 | 810 | 808
2018-04-27 08:30 | 812 | 808
2018-04-27 09:00 | 796 | 793
2018-04-27 09:30 | 775 | 772
2018-04-27 10:00 | 761 | 759
2018-04-27 10:30 | 761 | 759
2018-04-27 11:00 | 755 | 753
2018-04-27 11:30 | 756 | 755
2018-04-27 12:00 | 760 | 758
2018-04-27 12:30 | 760 | 759
2018-04-27 13:00 | 759 | 757
2018-04-27 13:30 | 771 | 770
2018-04-27 14:00 | 803 | 803
2018-04-27 14:30 | 814 | 814
2018-04-27 15:00 | 835 | 835
2018-04-27 15:30 | 847 | 847
2018-04-27 16:00 | 876 | 876
2018-04-27 16:30 | 888 | 887
2018-04-27 17:00 | 895 | 892
2018-04-27 17:30 | 907 | 904
2018-04-27 18:00 | 926 | 924
2018-04-27 18:30 | 914 | 910
2018-04-27 19:00 | 909 | 903
2018-04-27 19:30 | 882 | 877
2018-04-27 20:00 | 866 | 860
2018-04-27 20:30 | 848 | 843
2018-04-27 21:00 | 811 | 809
2018-04-27 21:30 | 785 | 783
2018-04-27 22:00 | 758 | 755
2018-04-27 22:30 | 744 | 739
2018-04-27 23:00 | 736 | 729
2018-04-27 23:30 | 696 | 686
2018-04-28 | 657 | 641
2018-04-28 00:30 | 604 | 591
2018-04-28 01:00 | 576 | 562
2018-04-28 01:30 | 563 | 546
2018-04-28 02:00 | 552 | 532
2018-04-28 02:30 | 547 | 525
2018-04-28 03:00 | 544 | 519
2018-04-28 03:30 | 542 | 516
2018-04-28 04:00 | 541 | 514
2018-04-28 04:30 | 542 | 515
2018-04-28 05:00 | 547 | 521
2018-04-28 05:30 | 553 | 531
2018-04-28 06:00 | 567 | 547
2018-04-28 06:30 | 595 | 577
2018-04-28 07:00 | 612 | 597
2018-04-28 07:30 | 637 | 629
2018-04-28 08:00 | 651 | 647
2018-04-28 08:30 | 665 | 663
2018-04-28 09:00 | 695 | 694
2018-04-28 09:30 | 693 | 693
2018-04-28 10:00 | 687 | 687
2018-04-28 10:30 | 708 | 708
2018-04-28 11:00 | 652 | 652
2018-04-28 11:30 | 613 | 613
2018-04-28 12:00 | 622 | 622
2018-04-28 12:30 | 613 | 612
2018-04-28 13:00 | 626 | 626
2018-04-28 13:30 | 630 | 630
2018-04-28 14:00 | 684 | 684
2018-04-28 14:30 | 693 | 692
2018-04-28 15:00 | 696 | 695
2018-04-28 15:30 | 706 | 705
2018-04-28 16:00 | 729 | 729
2018-04-28 16:30 | 752 | 752
2018-04-28 17:00 | 789 | 789
2018-04-28 17:30 | 811 | 811
2018-04-28 18:00 | 833 | 832
2018-04-28 18:30 | 834 | 832
2018-04-28 19:00 | 833 | 829
2018-04-28 19:30 | 805 | 799
2018-04-28 20:00 | 793 | 786
2018-04-28 20:30 | 774 | 770
2018-04-28 21:00 | 734 | 732
2018-04-28 21:30 | 719 | 716
2018-04-28 22:00 | 710 | 706
2018-04-28 22:30 | 702 | 697
2018-04-28 23:00 | 706 | 701
2018-04-28 23:30 | 672 | 664
2018-04-29 | 633 | 622
2018-04-29 00:30 | 593 | 576
2018-04-29 01:00 | 571 | 550
2018-04-29 01:30 | 562 | 538
2018-04-29 02:00 | 553 | 526
2018-04-29 02:30 | 540 | 512
2018-04-29 03:00 | 531 | 500
2018-04-29 03:30 | 532 | 500
2018-04-29 04:00 | 532 | 500
2018-04-29 04:30 | 532 | 499
2018-04-29 05:00 | 534 | 503
2018-04-29 05:30 | 537 | 508
2018-04-29 06:00 | 548 | 522
2018-04-29 06:30 | 564 | 537
2018-04-29 07:00 | 574 | 548
2018-04-29 07:30 | 589 | 570
2018-04-29 08:00 | 596 | 582
2018-04-29 08:30 | 599 | 589
2018-04-29 09:00 | 601 | 595
2018-04-29 09:30 | 601 | 597
2018-04-29 10:00 | 587 | 584
2018-04-29 10:30 | 584 | 581
2018-04-29 11:00 | 602 | 601
2018-04-29 11:30 | 613 | 613
2018-04-29 12:00 | 608 | 607
2018-04-29 12:30 | 597 | 595
2018-04-29 13:00 | 591 | 589
2018-04-29 13:30 | 602 | 600
2018-04-29 14:00 | 625 | 624
2018-04-29 14:30 | 657 | 656
2018-04-29 15:00 | 671 | 670
2018-04-29 15:30 | 688 | 687
2018-04-29 16:00 | 717 | 717
2018-04-29 16:30 | 744 | 743
2018-04-29 17:00 | 774 | 774
2018-04-29 17:30 | 811 | 811
2018-04-29 18:00 | 859 | 858
2018-04-29 18:30 | 863 | 861
2018-04-29 19:00 | 853 | 851
2018-04-29 19:30 | 823 | 819
2018-04-29 20:00 | 804 | 803
2018-04-29 20:30 | 791 | 790
2018-04-29 21:00 | 765 | 764
2018-04-29 21:30 | 742 | 739
2018-04-29 22:00 | 720 | 715
2018-04-29 22:30 | 716 | 708
2018-04-29 23:00 | 714 | 706
2018-04-29 23:30 | 676 | 666
2018-04-30 | 637 | 623
2018-04-30 00:30 | 600 | 580
2018-04-30 01:00 | 575 | 550
2018-04-30 01:30 | 566 | 538
2018-04-30 02:00 | 555 | 526
2018-04-30 02:30 | 548 | 518
2018-04-30 03:00 | 542 | 510
2018-04-30 03:30 | 541 | 510
2018-04-30 04:00 | 541 | 511
2018-04-30 04:30 | 553 | 525
2018-04-30 05:00 | 567 | 544
2018-04-30 05:30 | 595 | 579
2018-04-30 06:00 | 638 | 627
2018-04-30 06:30 | 702 | 694
2018-04-30 07:00 | 757 | 755
2018-04-30 07:30 | 799 | 799
2018-04-30 08:00 | 800 | 799
2018-04-30 08:30 | 778 | 777
2018-04-30 09:00 | 765 | 765
2018-04-30 09:30 | 745 | 745
2018-04-30 10:00 | 731 | 731
2018-04-30 10:30 | 723 | 723
2018-04-30 11:00 | 727 | 727
2018-04-30 11:30 | 731 | 730
2018-04-30 12:00 | 739 | 739
2018-04-30 12:30 | 723 | 723
2018-04-30 13:00 | 737 | 737
2018-04-30 13:30 | 755 | 755
2018-04-30 14:00 | 775 | 775
2018-04-30 14:30 | 799 | 799
2018-04-30 15:00 | 796 | 795
2018-04-30 15:30 | 797 | 796
2018-04-30 16:00 | 819 | 817
2018-04-30 16:30 | 848 | 847
2018-04-30 17:00 | 891 | 890
2018-04-30 17:30 | 924 | 924
2018-04-30 18:00 | 961 | 961
2018-04-30 18:30 | 959 | 959
2018-04-30 19:00 | 940 | 938
2018-04-30 19:30 | 914 | 911
2018-04-30 20:00 | 891 | 890
2018-04-30 20:30 | 868 | 868
2018-04-30 21:00 | 833 | 833
2018-04-30 21:30 | 791 | 790
2018-04-30 22:00 | 771 | 768
2018-04-30 22:30 | 752 | 748
2018-04-30 23:00 | 749 | 744
2018-04-30 23:30 | 708 | 700
2018-05-01 | 666 | 655
2018-05-01 00:30 | 616 | 604
2018-05-01 01:00 | 595 | 579
2018-05-01 01:30 | 576 | 558
2018-05-01 02:00 | 562 | 543
2018-05-01 02:30 | 558 | 539
2018-05-01 03:00 | 555 | 534
2018-05-01 03:30 | 554 | 532
2018-05-01 04:00 | 557 | 536
2018-05-01 04:30 | 570 | 550
2018-05-01 05:00 | 582 | 565
2018-05-01 05:30 | 611 | 600
2018-05-01 06:00 | 652 | 645
2018-05-01 06:30 | 721 | 715
2018-05-01 07:00 | 778 | 776
2018-05-01 07:30 | 823 | 821
2018-05-01 08:00 | 821 | 820
2018-05-01 08:30 | 805 | 804
2018-05-01 09:00 | 786 | 786
2018-05-01 09:30 | 771 | 771
2018-05-01 10:00 | 761 | 761
2018-05-01 10:30 | 766 | 766
2018-05-01 11:00 | 761 | 761
2018-05-01 11:30 | 764 | 764
2018-05-01 12:00 | 756 | 756
2018-05-01 12:30 | 745 | 745
2018-05-01 13:00 | 738 | 738
2018-05-01 13:30 | 761 | 761
2018-05-01 14:00 | 789 | 788
2018-05-01 14:30 | 796 | 794
2018-05-01 15:00 | 800 | 797
2018-05-01 15:30 | 825 | 822
2018-05-01 16:00 | 854 | 852
2018-05-01 16:30 | 886 | 884
2018-05-01 17:00 | 927 | 926
2018-05-01 17:30 | 966 | 965
2018-05-01 18:00 | 998 | 996
2018-05-01 18:30 | 992 | 988
2018-05-01 19:00 | 961 | 955
2018-05-01 19:30 | 925 | 920
2018-05-01 20:00 | 901 | 899
2018-05-01 20:30 | 891 | 890
2018-05-01 21:00 | 846 | 845
2018-05-01 21:30 | 811 | 810
2018-05-01 22:00 | 791 | 789
2018-05-01 22:30 | 771 | 767
2018-05-01 23:00 | 758 | 755
2018-05-01 23:30 | 717 | 714
2018-05-02 | 670 | 665
2018-05-02 00:30 | 627 | 618
2018-05-02 01:00 | 604 | 592
2018-05-02 01:30 | 591 | 577
2018-05-02 02:00 | 583 | 567
2018-05-02 02:30 | 578 | 562
2018-05-02 03:00 | 573 | 556
2018-05-02 03:30 | 574 | 557
2018-05-02 04:00 | 575 | 558
2018-05-02 04:30 | 586 | 571
2018-05-02 05:00 | 600 | 587
2018-05-02 05:30 | 634 | 625
2018-05-02 06:00 | 686 | 682
2018-05-02 06:30 | 766 | 765
2018-05-02 07:00 | 845 | 843
2018-05-02 07:30 | 885 | 885
2018-05-02 08:00 | 909 | 907
2018-05-02 08:30 | 893 | 892
2018-05-02 09:00 | 862 | 861
2018-05-02 09:30 | 833 | 832
2018-05-02 10:00 | 827 | 827
2018-05-02 10:30 | 869 | 869
2018-05-02 11:00 | 876 | 876
2018-05-02 11:30 | 865 | 864
2018-05-02 12:00 | 852 | 851
2018-05-02 12:30 | 853 | 853
2018-05-02 13:00 | 838 | 837
2018-05-02 13:30 | 878 | 878
2018-05-02 14:00 | 842 | 841
2018-05-02 14:30 | 846 | 845
2018-05-02 15:00 | 882 | 881
2018-05-02 15:30 | 903 | 902
2018-05-02 16:00 | 939 | 939
2018-05-02 16:30 | 963 | 962
2018-05-02 17:00 | 1007 | 1007
2018-05-02 17:30 | 1035 | 1034
2018-05-02 18:00 | 1063 | 1062
2018-05-02 18:30 | 1059 | 1053
2018-05-02 19:00 | 1040 | 1032
2018-05-02 19:30 | 996 | 991
2018-05-02 20:00 | 933 | 932
2018-05-02 20:30 | 904 | 904
2018-05-02 21:00 | 868 | 867
2018-05-02 21:30 | 836 | 836
2018-05-02 22:00 | 831 | 830
2018-05-02 22:30 | 778 | 775
2018-05-02 23:00 | 763 | 758
2018-05-02 23:30 | 764 | 757
2018-05-03 | 740 | 735
2018-05-03 00:30 | 702 | 693
2018-05-03 01:00 | 668 | 659
2018-05-03 01:30 | 655 | 644
2018-05-03 02:00 | 639 | 628
2018-05-03 02:30 | 629 | 615
2018-05-03 03:00 | 625 | 611
2018-05-03 03:30 | 619 | 605
2018-05-03 04:00 | 625 | 610
2018-05-03 04:30 | 629 | 615
2018-05-03 05:00 | 648 | 637
2018-05-03 05:30 | 663 | 656
2018-05-03 06:00 | 692 | 688
2018-05-03 06:30 | 735 | 733
2018-05-03 07:00 | 783 | 783
2018-05-03 07:30 | 822 | 822
2018-05-03 08:00 | 833 | 833
2018-05-03 08:30 | 856 | 856
2018-05-03 09:00 | 850 | 850
2018-05-03 09:30 | 844 | 844
2018-05-03 10:00 | 858 | 858
2018-05-03 10:30 | 797 | 797
2018-05-03 11:00 | 779 | 779
2018-05-03 11:30 | 781 | 781
2018-05-03 12:00 | 809 | 809
2018-05-03 12:30 | 828 | 828
2018-05-03 13:00 | 822 | 822
2018-05-03 13:30 | 818 | 818
2018-05-03 14:00 | 832 | 832
2018-05-03 14:30 | 834 | 834
2018-05-03 15:00 | 854 | 854
2018-05-03 15:30 | 860 | 860
2018-05-03 16:00 | 880 | 880
2018-05-03 16:30 | 908 | 908
2018-05-03 17:00 | 946 | 946
2018-05-03 17:30 | 986 | 986
2018-05-03 18:00 | 1020 | 1019
2018-05-03 18:30 | 1008 | 1004
2018-05-03 19:00 | 998 | 994
2018-05-03 19:30 | 964 | 961
2018-05-03 20:00 | 953 | 951
2018-05-03 20:30 | 907 | 905
2018-05-03 21:00 | 828 | 828
2018-05-03 21:30 | 789 | 789
2018-05-03 22:00 | 759 | 758
2018-05-03 22:30 | 742 | 740
2018-05-03 23:00 | 733 | 731
2018-05-03 23:30 | 690 | 686
2018-05-04 | 648 | 643
2018-05-04 00:30 | 600 | 591
2018-05-04 01:00 | 575 | 562
2018-05-04 01:30 | 559 | 543
2018-05-04 02:00 | 551 | 532
2018-05-04 02:30 | 546 | 526
2018-05-04 03:00 | 544 | 524
2018-05-04 03:30 | 548 | 528
2018-05-04 04:00 | 559 | 539
2018-05-04 04:30 | 575 | 557
2018-05-04 05:00 | 590 | 575
2018-05-04 05:30 | 615 | 606
2018-05-04 06:00 | 634 | 628
2018-05-04 06:30 | 689 | 687
2018-05-04 07:00 | 772 | 771
2018-05-04 07:30 | 803 | 802
2018-05-04 08:00 | 801 | 801
2018-05-04 08:30 | 800 | 800
2018-05-04 09:00 | 773 | 773
2018-05-04 09:30 | 751 | 751
2018-05-04 10:00 | 726 | 726
2018-05-04 10:30 | 723 | 723
2018-05-04 11:00 | 716 | 716
2018-05-04 11:30 | 734 | 734
2018-05-04 12:00 | 757 | 757
2018-05-04 12:30 | 749 | 749
2018-05-04 13:00 | 751 | 751
2018-05-04 13:30 | 761 | 761
2018-05-04 14:00 | 794 | 794
2018-05-04 14:30 | 817 | 817
2018-05-04 15:00 | 835 | 835
2018-05-04 15:30 | 858 | 858
2018-05-04 16:00 | 899 | 898
2018-05-04 16:30 | 921 | 919
2018-05-04 17:00 | 936 | 934
2018-05-04 17:30 | 950 | 948
2018-05-04 18:00 | 940 | 938
2018-05-04 18:30 | 904 | 899
2018-05-04 19:00 | 896 | 890
2018-05-04 19:30 | 870 | 865
2018-05-04 20:00 | 855 | 851
2018-05-04 20:30 | 840 | 838
2018-05-04 21:00 | 808 | 806
2018-05-04 21:30 | 781 | 777
2018-05-04 22:00 | 754 | 750
2018-05-04 22:30 | 736 | 732
2018-05-04 23:00 | 734 | 730
2018-05-04 23:30 | 693 | 688
2018-05-05 | 643 | 636
2018-05-05 00:30 | 598 | 588
2018-05-05 01:00 | 582 | 570
2018-05-05 01:30 | 566 | 552
2018-05-05 02:00 | 551 | 534
2018-05-05 02:30 | 549 | 531
2018-05-05 03:00 | 542 | 523
2018-05-05 03:30 | 539 | 520
2018-05-05 04:00 | 538 | 518
2018-05-05 04:30 | 542 | 524
2018-05-05 05:00 | 544 | 526
2018-05-05 05:30 | 553 | 536
2018-05-05 06:00 | 564 | 550
2018-05-05 06:30 | 589 | 576
2018-05-05 07:00 | 606 | 595
2018-05-05 07:30 | 635 | 629
2018-05-05 08:00 | 649 | 647
2018-05-05 08:30 | 662 | 662
2018-05-05 09:00 | 666 | 666
2018-05-05 09:30 | 663 | 663
2018-05-05 10:00 | 652 | 652
2018-05-05 10:30 | 640 | 640
2018-05-05 11:00 | 628 | 628
2018-05-05 11:30 | 620 | 620
2018-05-05 12:00 | 616 | 616
2018-05-05 12:30 | 607 | 606
2018-05-05 13:00 | 613 | 612
2018-05-05 13:30 | 623 | 623
2018-05-05 14:00 | 639 | 638
2018-05-05 14:30 | 664 | 663
2018-05-05 15:00 | 683 | 683
2018-05-05 15:30 | 699 | 699
2018-05-05 16:00 | 725 | 725
2018-05-05 16:30 | 753 | 753
2018-05-05 17:00 | 786 | 786
2018-05-05 17:30 | 802 | 802
2018-05-05 18:00 | 818 | 818
2018-05-05 18:30 | 815 | 814
2018-05-05 19:00 | 804 | 802
2018-05-05 19:30 | 788 | 786
2018-05-05 20:00 | 773 | 773
2018-05-05 20:30 | 765 | 764
2018-05-05 21:00 | 737 | 737
2018-05-05 21:30 | 718 | 717
2018-05-05 22:00 | 707 | 705
2018-05-05 22:30 | 696 | 694
2018-05-05 23:00 | 704 | 701
2018-05-05 23:30 | 664 | 659
2018-05-06 | 621 | 612
2018-05-06 00:30 | 577 | 565
2018-05-06 01:00 | 550 | 535
2018-05-06 01:30 | 535 | 515
2018-05-06 02:00 | 526 | 503
2018-05-06 02:30 | 519 | 494
2018-05-06 03:00 | 517 | 491
2018-05-06 03:30 | 523 | 497
2018-05-06 04:00 | 523 | 497
2018-05-06 04:30 | 525 | 499
2018-05-06 05:00 | 529 | 503
2018-05-06 05:30 | 536 | 511
2018-05-06 06:00 | 544 | 521
2018-05-06 06:30 | 558 | 535
2018-05-06 07:00 | 571 | 549
2018-05-06 07:30 | 585 | 567
2018-05-06 08:00 | 595 | 582
2018-05-06 08:30 | 600 | 591
2018-05-06 09:00 | 600 | 593
2018-05-06 09:30 | 590 | 585
2018-05-06 10:00 | 583 | 580
2018-05-06 10:30 | 577 | 575
2018-05-06 11:00 | 566 | 564
2018-05-06 11:30 | 558 | 556
2018-05-06 12:00 | 569 | 567
2018-05-06 12:30 | 569 | 567
2018-05-06 13:00 | 581 | 578
2018-05-06 13:30 | 596 | 594
2018-05-06 14:00 | 617 | 615
2018-05-06 14:30 | 640 | 639
2018-05-06 15:00 | 654 | 653
2018-05-06 15:30 | 668 | 667
2018-05-06 16:00 | 688 | 687
2018-05-06 16:30 | 720 | 719
2018-05-06 17:00 | 751 | 751
2018-05-06 17:30 | 788 | 788
2018-05-06 18:00 | 807 | 807
2018-05-06 18:30 | 810 | 809
2018-05-06 19:00 | 802 | 801
2018-05-06 19:30 | 779 | 777
2018-05-06 20:00 | 766 | 766
2018-05-06 20:30 | 758 | 758
2018-05-06 21:00 | 728 | 727
2018-05-06 21:30 | 706 | 704
2018-05-06 22:00 | 698 | 695
2018-05-06 22:30 | 689 | 685
2018-05-06 23:00 | 695 | 689
2018-05-06 23:30 | 662 | 654
2018-05-07 | 622 | 611
2018-05-07 00:30 | 586 | 569
2018-05-07 01:00 | 569 | 547
2018-05-07 01:30 | 554 | 527
2018-05-07 02:00 | 532 | 502
2018-05-07 02:30 | 510 | 480
2018-05-07 03:00 | 513 | 483
2018-05-07 03:30 | 503 | 472
2018-05-07 04:00 | 496 | 464
2018-05-07 04:30 | 444 | 409
2018-05-07 05:00 | 501 | 470
2018-05-07 05:30 | 522 | 494
2018-05-07 06:00 | 540 | 519
2018-05-07 06:30 | 558 | 540
2018-05-07 07:00 | 575 | 558
2018-05-07 07:30 | 610 | 596
2018-05-07 08:00 | 637 | 628
2018-05-07 08:30 | 662 | 657
2018-05-07 09:00 | 664 | 660
2018-05-07 09:30 | 678 | 676
2018-05-07 10:00 | 702 | 700
2018-05-07 10:30 | 696 | 691
2018-05-07 11:00 | 696 | 691
2018-05-07 11:30 | 698 | 693
2018-05-07 12:00 | 719 | 715
2018-05-07 12:30 | 710 | 704
2018-05-07 13:00 | 717 | 712
2018-05-07 13:30 | 750 | 745
2018-05-07 14:00 | 778 | 774
2018-05-07 14:30 | 795 | 793
2018-05-07 15:00 | 798 | 795
2018-05-07 15:30 | 809 | 806
2018-05-07 16:00 | 838 | 836
2018-05-07 16:30 | 865 | 863
2018-05-07 17:00 | 906 | 905
2018-05-07 17:30 | 951 | 949
2018-05-07 18:00 | 959 | 957
2018-05-07 18:30 | 944 | 941
2018-05-07 19:00 | 931 | 926
2018-05-07 19:30 | 912 | 907
2018-05-07 20:00 | 893 | 888
2018-05-07 20:30 | 880 | 875
2018-05-07 21:00 | 837 | 836
2018-05-07 21:30 | 803 | 801
2018-05-07 22:00 | 786 | 783
2018-05-07 22:30 | 752 | 748
2018-05-07 23:00 | 749 | 743
2018-05-07 23:30 | 711 | 703
2018-05-08 | 673 | 662
2018-05-08 00:30 | 635 | 620
2018-05-08 01:00 | 615 | 597
2018-05-08 01:30 | 600 | 581
2018-05-08 02:00 | 593 | 572
2018-05-08 02:30 | 586 | 564
2018-05-08 03:00 | 585 | 562
2018-05-08 03:30 | 587 | 565
2018-05-08 04:00 | 589 | 568
2018-05-08 04:30 | 603 | 585
2018-05-08 05:00 | 617 | 601
2018-05-08 05:30 | 651 | 640
2018-05-08 06:00 | 689 | 684
2018-05-08 06:30 | 766 | 762
2018-05-08 07:00 | 847 | 840
2018-05-08 07:30 | 915 | 911
2018-05-08 08:00 | 930 | 925
2018-05-08 08:30 | 919 | 914
2018-05-08 09:00 | 919 | 915
2018-05-08 09:30 | 904 | 896
2018-05-08 10:00 | 881 | 873
2018-05-08 10:30 | 878 | 871
2018-05-08 11:00 | 883 | 877
2018-05-08 11:30 | 860 | 852
2018-05-08 12:00 | 851 | 843
2018-05-08 12:30 | 885 | 878
2018-05-08 13:00 | 881 | 874
2018-05-08 13:30 | 899 | 893
2018-05-08 14:00 | 906 | 901
2018-05-08 14:30 | 920 | 913
2018-05-08 15:00 | 916 | 908
2018-05-08 15:30 | 938 | 929
2018-05-08 16:00 | 956 | 947
2018-05-08 16:30 | 985 | 977
2018-05-08 17:00 | 1031 | 1024
2018-05-08 17:30 | 1066 | 1063
2018-05-08 18:00 | 1083 | 1076
2018-05-08 18:30 | 1089 | 1079
2018-05-08 19:00 | 1085 | 1073
2018-05-08 19:30 | 1043 | 1037
2018-05-08 20:00 | 1032 | 1029
2018-05-08 20:30 | 1009 | 1005
2018-05-08 21:00 | 914 | 913
2018-05-08 21:30 | 872 | 870
2018-05-08 22:00 | 845 | 841
2018-05-08 22:30 | 810 | 807
2018-05-08 23:00 | 787 | 784
2018-05-08 23:30 | 746 | 743
2018-05-09 | 702 | 696
2018-05-09 00:30 | 656 | 647
2018-05-09 01:00 | 631 | 618
2018-05-09 01:30 | 614 | 598
2018-05-09 02:00 | 608 | 590
2018-05-09 02:30 | 596 | 576
2018-05-09 03:00 | 601 | 580
2018-05-09 03:30 | 594 | 573
2018-05-09 04:00 | 598 | 579
2018-05-09 04:30 | 609 | 592
2018-05-09 05:00 | 626 | 611
2018-05-09 05:30 | 651 | 642
2018-05-09 06:00 | 700 | 691
2018-05-09 06:30 | 767 | 764
2018-05-09 07:00 | 840 | 838
2018-05-09 07:30 | 905 | 902
2018-05-09 08:00 | 915 | 912
2018-05-09 08:30 | 891 | 889
2018-05-09 09:00 | 853 | 851
2018-05-09 09:30 | 823 | 820
2018-05-09 10:00 | 793 | 791
2018-05-09 10:30 | 774 | 772
2018-05-09 11:00 | 774 | 773
2018-05-09 11:30 | 770 | 768
2018-05-09 12:00 | 776 | 775
2018-05-09 12:30 | 780 | 779
2018-05-09 13:00 | 792 | 791
2018-05-09 13:30 | 807 | 806
2018-05-09 14:00 | 821 | 818
2018-05-09 14:30 | 845 | 843
2018-05-09 15:00 | 860 | 858
2018-05-09 15:30 | 893 | 890
2018-05-09 16:00 | 932 | 930
2018-05-09 16:30 | 964 | 962
2018-05-09 17:00 | 995 | 993
2018-05-09 17:30 | 1028 | 1027
2018-05-09 18:00 | 1061 | 1060
2018-05-09 18:30 | 1045 | 1042
2018-05-09 19:00 | 1033 | 1030
2018-05-09 19:30 | 1000 | 994
2018-05-09 20:00 | 989 | 984
2018-05-09 20:30 | 974 | 968
2018-05-09 21:00 | 924 | 920
2018-05-09 21:30 | 881 | 877
2018-05-09 22:00 | 846 | 842
2018-05-09 22:30 | 811 | 807
2018-05-09 23:00 | 781 | 777
2018-05-09 23:30 | 746 | 740
2018-05-10 | 700 | 689
2018-05-10 00:30 | 651 | 634
2018-05-10 01:00 | 632 | 612
2018-05-10 01:30 | 620 | 597
2018-05-10 02:00 | 612 | 586
2018-05-10 02:30 | 609 | 581
2018-05-10 03:00 | 606 | 578
2018-05-10 03:30 | 609 | 580
2018-05-10 04:00 | 609 | 580
2018-05-10 04:30 | 620 | 594
2018-05-10 05:00 | 631 | 609
2018-05-10 05:30 | 670 | 656
2018-05-10 06:00 | 704 | 696
2018-05-10 06:30 | 758 | 755
2018-05-10 07:00 | 819 | 818
2018-05-10 07:30 | 841 | 840
2018-05-10 08:00 | 738 | 737
2018-05-10 08:30 | 721 | 721
2018-05-10 09:00 | 702 | 702
2018-05-10 09:30 | 692 | 692
2018-05-10 10:00 | 677 | 677
2018-05-10 10:30 | 669 | 669
2018-05-10 11:00 | 656 | 656
2018-05-10 11:30 | 651 | 651
2018-05-10 12:00 | 654 | 653
2018-05-10 12:30 | 657 | 656
2018-05-10 13:00 | 664 | 664
2018-05-10 13:30 | 682 | 680
2018-05-10 14:00 | 699 | 697
2018-05-10 14:30 | 718 | 717
2018-05-10 15:00 | 841 | 839
2018-05-10 15:30 | 868 | 867
2018-05-10 16:00 | 903 | 902
2018-05-10 16:30 | 933 | 932
2018-05-10 17:00 | 961 | 960
2018-05-10 17:30 | 993 | 992
2018-05-10 18:00 | 1038 | 1037
2018-05-10 18:30 | 1025 | 1022
2018-05-10 19:00 | 1017 | 1013
2018-05-10 19:30 | 992 | 985
2018-05-10 20:00 | 980 | 970
2018-05-10 20:30 | 955 | 949
2018-05-10 21:00 | 916 | 910
2018-05-10 21:30 | 866 | 865
2018-05-10 22:00 | 831 | 828
2018-05-10 22:30 | 814 | 811
2018-05-10 23:00 | 805 | 801
2018-05-10 23:30 | 755 | 751
2018-05-11 | 706 | 697
2018-05-11 00:30 | 656 | 644
2018-05-11 01:00 | 635 | 621
2018-05-11 01:30 | 616 | 599
2018-05-11 02:00 | 606 | 588
2018-05-11 02:30 | 600 | 580
2018-05-11 03:00 | 603 | 582
2018-05-11 03:30 | 608 | 586
2018-05-11 04:00 | 605 | 583
2018-05-11 04:30 | 612 | 591
2018-05-11 05:00 | 622 | 604
2018-05-11 05:30 | 652 | 641
2018-05-11 06:00 | 692 | 687
2018-05-11 06:30 | 750 | 748
2018-05-11 07:00 | 807 | 807
2018-05-11 07:30 | 850 | 850
2018-05-11 08:00 | 843 | 842
2018-05-11 08:30 | 780 | 780
2018-05-11 09:00 | 729 | 729
2018-05-11 09:30 | 704 | 704
2018-05-11 10:00 | 690 | 689
2018-05-11 10:30 | 674 | 673
2018-05-11 11:00 | 664 | 663
2018-05-11 11:30 | 650 | 649
2018-05-11 12:00 | 642 | 642
2018-05-11 12:30 | 629 | 629
2018-05-11 13:00 | 634 | 634
2018-05-11 13:30 | 706 | 706
2018-05-11 14:00 | 729 | 729
2018-05-11 14:30 | 755 | 755
2018-05-11 15:00 | 770 | 770
2018-05-11 15:30 | 812 | 812
2018-05-11 16:00 | 852 | 852
2018-05-11 16:30 | 902 | 902
2018-05-11 17:00 | 937 | 936
2018-05-11 17:30 | 966 | 966
2018-05-11 18:00 | 987 | 987
2018-05-11 18:30 | 972 | 970
2018-05-11 19:00 | 967 | 964
2018-05-11 19:30 | 952 | 950
2018-05-11 20:00 | 939 | 938
2018-05-11 20:30 | 925 | 924
2018-05-11 21:00 | 890 | 890
2018-05-11 21:30 | 862 | 861
2018-05-11 22:00 | 842 | 840
2018-05-11 22:30 | 806 | 804
2018-05-11 23:00 | 792 | 789
2018-05-11 23:30 | 758 | 752
2018-05-12 | 709 | 699
2018-05-12 00:30 | 669 | 655
2018-05-12 01:00 | 654 | 635
2018-05-12 01:30 | 630 | 608
2018-05-12 02:00 | 616 | 589
2018-05-12 02:30 | 610 | 582
2018-05-12 03:00 | 604 | 575
2018-05-12 03:30 | 606 | 576
2018-05-12 04:00 | 607 | 575
2018-05-12 04:30 | 611 | 579
2018-05-12 05:00 | 613 | 583
2018-05-12 05:30 | 627 | 601
2018-05-12 06:00 | 645 | 623
2018-05-12 06:30 | 668 | 649
2018-05-12 07:00 | 696 | 682
2018-05-12 07:30 | 733 | 723
2018-05-12 08:00 | 744 | 738
2018-05-12 08:30 | 742 | 738
2018-05-12 09:00 | 732 | 728
2018-05-12 09:30 | 715 | 712
2018-05-12 10:00 | 700 | 696
2018-05-12 10:30 | 685 | 677
2018-05-12 11:00 | 668 | 659
2018-05-12 11:30 | 644 | 635
2018-05-12 12:00 | 633 | 623
2018-05-12 12:30 | 620 | 609
2018-05-12 13:00 | 624 | 614
2018-05-12 13:30 | 629 | 620
2018-05-12 14:00 | 648 | 639
2018-05-12 14:30 | 666 | 658
2018-05-12 15:00 | 687 | 680
2018-05-12 15:30 | 714 | 709
2018-05-12 16:00 | 747 | 744
2018-05-12 16:30 | 772 | 770
2018-05-12 17:00 | 811 | 810
2018-05-12 17:30 | 841 | 841
2018-05-12 18:00 | 876 | 876
2018-05-12 18:30 | 876 | 876
2018-05-12 19:00 | 873 | 873
2018-05-12 19:30 | 849 | 849
2018-05-12 20:00 | 825 | 824
2018-05-12 20:30 | 807 | 806
2018-05-12 21:00 | 786 | 783
2018-05-12 21:30 | 765 | 760
2018-05-12 22:00 | 755 | 749
2018-05-12 22:30 | 746 | 739
2018-05-12 23:00 | 752 | 744
2018-05-12 23:30 | 722 | 716
2018-05-13 | 675 | 667
2018-05-13 00:30 | 634 | 620
2018-05-13 01:00 | 609 | 589
2018-05-13 01:30 | 592 | 566
2018-05-13 02:00 | 584 | 552
2018-05-13 02:30 | 574 | 542
2018-05-13 03:00 | 550 | 519
2018-05-13 03:30 | 548 | 516
2018-05-13 04:00 | 542 | 510
2018-05-13 04:30 | 544 | 512
2018-05-13 05:00 | 545 | 515
2018-05-13 05:30 | 556 | 528
2018-05-13 06:00 | 569 | 543
2018-05-13 06:30 | 585 | 561
2018-05-13 07:00 | 605 | 583
2018-05-13 07:30 | 646 | 629
2018-05-13 08:00 | 659 | 647
2018-05-13 08:30 | 660 | 653
2018-05-13 09:00 | 653 | 647
2018-05-13 09:30 | 646 | 641
2018-05-13 10:00 | 628 | 623
2018-05-13 10:30 | 604 | 600
2018-05-13 11:00 | 599 | 593
2018-05-13 11:30 | 577 | 570
2018-05-13 12:00 | 567 | 560
2018-05-13 12:30 | 556 | 549
2018-05-13 13:00 | 558 | 551
2018-05-13 13:30 | 565 | 558
2018-05-13 14:00 | 585 | 579
2018-05-13 14:30 | 611 | 605
2018-05-13 15:00 | 636 | 632
2018-05-13 15:30 | 664 | 661
2018-05-13 16:00 | 703 | 700
2018-05-13 16:30 | 737 | 735
2018-05-13 17:00 | 788 | 787
2018-05-13 17:30 | 825 | 825
2018-05-13 18:00 | 856 | 855
2018-05-13 18:30 | 855 | 853
2018-05-13 19:00 | 853 | 851
2018-05-13 19:30 | 835 | 831
2018-05-13 20:00 | 824 | 822
2018-05-13 20:30 | 817 | 814
2018-05-13 21:00 | 781 | 780
2018-05-13 21:30 | 756 | 754
2018-05-13 22:00 | 736 | 733
2018-05-13 22:30 | 723 | 718
2018-05-13 23:00 | 722 | 717
2018-05-13 23:30 | 694 | 687
2018-05-14 | 654 | 641
2018-05-14 00:30 | 622 | 604
2018-05-14 01:00 | 599 | 575
2018-05-14 01:30 | 587 | 559
2018-05-14 02:00 | 579 | 548
2018-05-14 02:30 | 568 | 538
2018-05-14 03:00 | 568 | 536
2018-05-14 03:30 | 567 | 537
2018-05-14 04:00 | 573 | 543
2018-05-14 04:30 | 582 | 555
2018-05-14 05:00 | 600 | 578
2018-05-14 05:30 | 632 | 619
2018-05-14 06:00 | 676 | 668
2018-05-14 06:30 | 752 | 747
2018-05-14 07:00 | 816 | 815
2018-05-14 07:30 | 860 | 858
2018-05-14 08:00 | 853 | 850
2018-05-14 08:30 | 821 | 818
2018-05-14 09:00 | 784 | 780
2018-05-14 09:30 | 759 | 755
2018-05-14 10:00 | 738 | 734
2018-05-14 10:30 | 724 | 722
2018-05-14 11:00 | 710 | 708
2018-05-14 11:30 | 699 | 698
2018-05-14 12:00 | 702 | 700
2018-05-14 12:30 | 702 | 700
2018-05-14 13:00 | 712 | 711
2018-05-14 13:30 | 724 | 723
2018-05-14 14:00 | 752 | 752
2018-05-14 14:30 | 775 | 775
2018-05-14 15:00 | 788 | 788
2018-05-14 15:30 | 811 | 810
2018-05-14 16:00 | 835 | 834
2018-05-14 16:30 | 870 | 869
2018-05-14 17:00 | 912 | 911
2018-05-14 17:30 | 960 | 960
2018-05-14 18:00 | 987 | 986
2018-05-14 18:30 | 967 | 965
2018-05-14 19:00 | 958 | 958
2018-05-14 19:30 | 934 | 932
2018-05-14 20:00 | 910 | 907
2018-05-14 20:30 | 898 | 895
2018-05-14 21:00 | 851 | 850
2018-05-14 21:30 | 819 | 819
2018-05-14 22:00 | 784 | 783
2018-05-14 22:30 | 760 | 759
2018-05-14 23:00 | 757 | 756
2018-05-14 23:30 | 723 | 720
2018-05-15 | 677 | 671
2018-05-15 00:30 | 629 | 619
2018-05-15 01:00 | 600 | 586
2018-05-15 01:30 | 587 | 570
2018-05-15 02:00 | 575 | 556
2018-05-15 02:30 | 574 | 553
2018-05-15 03:00 | 570 | 549
2018-05-15 03:30 | 566 | 546
2018-05-15 04:00 | 569 | 548
2018-05-15 04:30 | 588 | 567
2018-05-15 05:00 | 603 | 585
2018-05-15 05:30 | 639 | 628
2018-05-15 06:00 | 683 | 678
2018-05-15 06:30 | 757 | 755
2018-05-15 07:00 | 831 | 830
2018-05-15 07:30 | 864 | 862
2018-05-15 08:00 | 851 | 850
2018-05-15 08:30 | 813 | 812
2018-05-15 09:00 | 784 | 782
2018-05-15 09:30 | 762 | 762
2018-05-15 10:00 | 740 | 740
2018-05-15 10:30 | 719 | 718
2018-05-15 11:00 | 706 | 705
2018-05-15 11:30 | 697 | 696
2018-05-15 12:00 | 694 | 694
2018-05-15 12:30 | 693 | 693
2018-05-15 13:00 | 699 | 699
2018-05-15 13:30 | 716 | 716
2018-05-15 14:00 | 734 | 734
2018-05-15 14:30 | 753 | 753
2018-05-15 15:00 | 771 | 771
2018-05-15 15:30 | 793 | 793
2018-05-15 16:00 | 826 | 826
2018-05-15 16:30 | 864 | 864
2018-05-15 17:00 | 908 | 907
2018-05-15 17:30 | 953 | 953
2018-05-15 18:00 | 980 | 980
2018-05-15 18:30 | 969 | 969
2018-05-15 19:00 | 972 | 971
2018-05-15 19:30 | 944 | 941
2018-05-15 20:00 | 925 | 921
2018-05-15 20:30 | 914 | 913
2018-05-15 21:00 | 854 | 853
2018-05-15 21:30 | 808 | 807
2018-05-15 22:00 | 784 | 784
2018-05-15 22:30 | 759 | 758
2018-05-15 23:00 | 757 | 756
2018-05-15 23:30 | 720 | 716
2018-05-16 | 670 | 663
2018-05-16 00:30 | 623 | 612
2018-05-16 01:00 | 596 | 581
2018-05-16 01:30 | 579 | 559
2018-05-16 02:00 | 574 | 552
2018-05-16 02:30 | 565 | 541
2018-05-16 03:00 | 568 | 543
2018-05-16 03:30 | 568 | 542
2018-05-16 04:00 | 564 | 540
2018-05-16 04:30 | 575 | 553
2018-05-16 05:00 | 589 | 570
2018-05-16 05:30 | 630 | 618
2018-05-16 06:00 | 677 | 672
2018-05-16 06:30 | 763 | 760
2018-05-16 07:00 | 824 | 823
2018-05-16 07:30 | 859 | 856
2018-05-16 08:00 | 845 | 841
2018-05-16 08:30 | 814 | 809
2018-05-16 09:00 | 775 | 768
2018-05-16 09:30 | 744 | 741
2018-05-16 10:00 | 714 | 713
2018-05-16 10:30 | 693 | 693
2018-05-16 11:00 | 682 | 682
2018-05-16 11:30 | 673 | 673
2018-05-16 12:00 | 686 | 685
2018-05-16 12:30 | 690 | 690
2018-05-16 13:00 | 683 | 683
2018-05-16 13:30 | 687 | 687
2018-05-16 14:00 | 707 | 707
2018-05-16 14:30 | 732 | 732
2018-05-16 15:00 | 752 | 752
2018-05-16 15:30 | 771 | 771
2018-05-16 16:00 | 805 | 805
2018-05-16 16:30 | 844 | 844
2018-05-16 17:00 | 885 | 884
2018-05-16 17:30 | 935 | 935
2018-05-16 18:00 | 973 | 972
2018-05-16 18:30 | 958 | 954
2018-05-16 19:00 | 956 | 951
2018-05-16 19:30 | 928 | 920
2018-05-16 20:00 | 901 | 900
2018-05-16 20:30 | 890 | 889
2018-05-16 21:00 | 845 | 845
2018-05-16 21:30 | 812 | 812
2018-05-16 22:00 | 784 | 783
2018-05-16 22:30 | 762 | 759
2018-05-16 23:00 | 754 | 750
2018-05-16 23:30 | 719 | 713
2018-05-17 | 669 | 658
2018-05-17 00:30 | 621 | 604
2018-05-17 01:00 | 598 | 576
2018-05-17 01:30 | 586 | 560
2018-05-17 02:00 | 582 | 551
2018-05-17 02:30 | 568 | 537
2018-05-17 03:00 | 557 | 528
2018-05-17 03:30 | 560 | 532
2018-05-17 04:00 | 560 | 531
2018-05-17 04:30 | 574 | 548
2018-05-17 05:00 | 594 | 572
2018-05-17 05:30 | 629 | 616
2018-05-17 06:00 | 677 | 671
2018-05-17 06:30 | 759 | 755
2018-05-17 07:00 | 813 | 812
2018-05-17 07:30 | 873 | 869
2018-05-17 08:00 | 851 | 842
2018-05-17 08:30 | 821 | 815
2018-05-17 09:00 | 794 | 786
2018-05-17 09:30 | 765 | 760
2018-05-17 10:00 | 734 | 733
2018-05-17 10:30 | 723 | 723
2018-05-17 11:00 | 733 | 733
2018-05-17 11:30 | 740 | 740
2018-05-17 12:00 | 746 | 746
2018-05-17 12:30 | 758 | 758
2018-05-17 13:00 | 765 | 765
2018-05-17 13:30 | 791 | 791
2018-05-17 14:00 | 801 | 800
2018-05-17 14:30 | 804 | 803
2018-05-17 15:00 | 811 | 809
2018-05-17 15:30 | 798 | 796
2018-05-17 16:00 | 825 | 822
2018-05-17 16:30 | 857 | 855
2018-05-17 17:00 | 909 | 908
2018-05-17 17:30 | 964 | 963
2018-05-17 18:00 | 997 | 992
2018-05-17 18:30 | 994 | 989
2018-05-17 19:00 | 987 | 980
2018-05-17 19:30 | 950 | 946
2018-05-17 20:00 | 940 | 939
2018-05-17 20:30 | 929 | 928
2018-05-17 21:00 | 889 | 886
2018-05-17 21:30 | 839 | 836
2018-05-17 22:00 | 802 | 801
2018-05-17 22:30 | 780 | 778
2018-05-17 23:00 | 773 | 771
2018-05-17 23:30 | 730 | 727
2018-05-18 | 685 | 680
2018-05-18 00:30 | 637 | 629
2018-05-18 01:00 | 608 | 596
2018-05-18 01:30 | 590 | 575
2018-05-18 02:00 | 577 | 557
2018-05-18 02:30 | 575 | 554
2018-05-18 03:00 | 571 | 549
2018-05-18 03:30 | 571 | 549
2018-05-18 04:00 | 571 | 549
2018-05-18 04:30 | 586 | 567
2018-05-18 05:00 | 595 | 581
2018-05-18 05:30 | 637 | 629
2018-05-18 06:00 | 684 | 679
2018-05-18 06:30 | 756 | 754
2018-05-18 07:00 | 829 | 827
2018-05-18 07:30 | 873 | 871
2018-05-18 08:00 | 858 | 856
2018-05-18 08:30 | 838 | 837
2018-05-18 09:00 | 796 | 795
2018-05-18 09:30 | 769 | 768
2018-05-18 10:00 | 740 | 740
2018-05-18 10:30 | 726 | 725
2018-05-18 11:00 | 712 | 712
2018-05-18 11:30 | 707 | 706
2018-05-18 12:00 | 708 | 708
2018-05-18 12:30 | 712 | 712
2018-05-18 13:00 | 720 | 720
2018-05-18 13:30 | 736 | 736
2018-05-18 14:00 | 749 | 748
2018-05-18 14:30 | 760 | 759
2018-05-18 15:00 | 779 | 779
2018-05-18 15:30 | 804 | 804
2018-05-18 16:00 | 838 | 838
2018-05-18 16:30 | 871 | 870
2018-05-18 17:00 | 906 | 905
2018-05-18 17:30 | 924 | 924
2018-05-18 18:00 | 937 | 936
2018-05-18 18:30 | 919 | 918
2018-05-18 19:00 | 916 | 913
2018-05-18 19:30 | 893 | 890
2018-05-18 20:00 | 880 | 880
2018-05-18 20:30 | 877 | 877
2018-05-18 21:00 | 861 | 861
2018-05-18 21:30 | 814 | 813
2018-05-18 22:00 | 786 | 785
2018-05-18 22:30 | 777 | 776
2018-05-18 23:00 | 777 | 775
2018-05-18 23:30 | 737 | 735
2018-05-19 | 694 | 689
2018-05-19 00:30 | 686 | 680
2018-05-19 01:00 | 656 | 648
2018-05-19 01:30 | 624 | 613
2018-05-19 02:00 | 583 | 566
2018-05-19 02:30 | 575 | 554
2018-05-19 03:00 | 568 | 544
2018-05-19 03:30 | 567 | 545
2018-05-19 04:00 | 569 | 547
2018-05-19 04:30 | 567 | 545
2018-05-19 05:00 | 579 | 558
2018-05-19 05:30 | 591 | 573
2018-05-19 06:00 | 607 | 592
2018-05-19 06:30 | 637 | 626
2018-05-19 07:00 | 668 | 658
2018-05-19 07:30 | 701 | 697
2018-05-19 08:00 | 741 | 740
2018-05-19 08:30 | 743 | 743
2018-05-19 09:00 | 748 | 748
2018-05-19 09:30 | 734 | 734
2018-05-19 10:00 | 714 | 714
2018-05-19 10:30 | 688 | 688
2018-05-19 11:00 | 671 | 671
2018-05-19 11:30 | 643 | 642
2018-05-19 12:00 | 618 | 617
2018-05-19 12:30 | 626 | 625
2018-05-19 13:00 | 615 | 613
2018-05-19 13:30 | 613 | 610
2018-05-19 14:00 | 633 | 630
2018-05-19 14:30 | 648 | 646
2018-05-19 15:00 | 671 | 669
2018-05-19 15:30 | 697 | 696
2018-05-19 16:00 | 729 | 729
2018-05-19 16:30 | 767 | 767
2018-05-19 17:00 | 807 | 807
2018-05-19 17:30 | 842 | 842
2018-05-19 18:00 | 864 | 864
2018-05-19 18:30 | 853 | 852
2018-05-19 19:00 | 854 | 853
2018-05-19 19:30 | 833 | 831
2018-05-19 20:00 | 823 | 821
2018-05-19 20:30 | 807 | 807
2018-05-19 21:00 | 774 | 773
2018-05-19 21:30 | 750 | 748
2018-05-19 22:00 | 760 | 759
2018-05-19 22:30 | 750 | 747
2018-05-19 23:00 | 766 | 763
2018-05-19 23:30 | 731 | 726
2018-05-20 | 681 | 672
2018-05-20 00:30 | 634 | 619
2018-05-20 01:00 | 615 | 595
2018-05-20 01:30 | 596 | 573
2018-05-20 02:00 | 584 | 558
2018-05-20 02:30 | 577 | 549
2018-05-20 03:00 | 568 | 537
2018-05-20 03:30 | 572 | 542
2018-05-20 04:00 | 564 | 533
2018-05-20 04:30 | 574 | 542
2018-05-20 05:00 | 573 | 541
2018-05-20 05:30 | 584 | 553
2018-05-20 06:00 | 594 | 566
2018-05-20 06:30 | 610 | 584
2018-05-20 07:00 | 628 | 603
2018-05-20 07:30 | 641 | 622
2018-05-20 08:00 | 646 | 632
2018-05-20 08:30 | 646 | 636
2018-05-20 09:00 | 649 | 642
2018-05-20 09:30 | 647 | 640
2018-05-20 10:00 | 635 | 629
2018-05-20 10:30 | 623 | 617
2018-05-20 11:00 | 603 | 597
2018-05-20 11:30 | 588 | 581
2018-05-20 12:00 | 586 | 579
2018-05-20 12:30 | 582 | 575
2018-05-20 13:00 | 581 | 575
2018-05-20 13:30 | 591 | 585
2018-05-20 14:00 | 605 | 600
2018-05-20 14:30 | 627 | 622
2018-05-20 15:00 | 655 | 651
2018-05-20 15:30 | 682 | 679
2018-05-20 16:00 | 721 | 720
2018-05-20 16:30 | 755 | 754
2018-05-20 17:00 | 801 | 801
2018-05-20 17:30 | 851 | 851
2018-05-20 18:00 | 880 | 879
2018-05-20 18:30 | 873 | 871
2018-05-20 19:00 | 863 | 861
2018-05-20 19:30 | 848 | 844
2018-05-20 20:00 | 833 | 831
2018-05-20 20:30 | 826 | 824
2018-05-20 21:00 | 793 | 792
2018-05-20 21:30 | 765 | 763
2018-05-20 22:00 | 744 | 741
2018-05-20 22:30 | 734 | 728
2018-05-20 23:00 | 735 | 728
2018-05-20 23:30 | 701 | 692
2018-05-21 | 661 | 648
2018-05-21 00:30 | 617 | 599
2018-05-21 01:00 | 600 | 577
2018-05-21 01:30 | 587 | 562
2018-05-21 02:00 | 577 | 549
2018-05-21 02:30 | 573 | 541
2018-05-21 03:00 | 570 | 537
2018-05-21 03:30 | 574 | 540
2018-05-21 04:00 | 579 | 546
2018-05-21 04:30 | 600 | 569
2018-05-21 05:00 | 612 | 586
2018-05-21 05:30 | 644 | 628
2018-05-21 06:00 | 689 | 681
2018-05-21 06:30 | 767 | 761
2018-05-21 07:00 | 840 | 832
2018-05-21 07:30 | 883 | 878
2018-05-21 08:00 | 871 | 867
2018-05-21 08:30 | 837 | 833
2018-05-21 09:00 | 793 | 788
2018-05-21 09:30 | 759 | 753
2018-05-21 10:00 | 728 | 725
2018-05-21 10:30 | 710 | 709
2018-05-21 11:00 | 705 | 704
2018-05-21 11:30 | 692 | 692
2018-05-21 12:00 | 692 | 692
2018-05-21 12:30 | 691 | 691
2018-05-21 13:00 | 689 | 689
2018-05-21 13:30 | 703 | 703
2018-05-21 14:00 | 725 | 725
2018-05-21 14:30 | 747 | 747
2018-05-21 15:00 | 767 | 766
2018-05-21 15:30 | 788 | 787
2018-05-21 16:00 | 823 | 823
2018-05-21 16:30 | 857 | 857
2018-05-21 17:00 | 894 | 894
2018-05-21 17:30 | 955 | 954
2018-05-21 18:00 | 980 | 976
2018-05-21 18:30 | 961 | 955
2018-05-21 19:00 | 954 | 949
2018-05-21 19:30 | 923 | 920
2018-05-21 20:00 | 908 | 907
2018-05-21 20:30 | 894 | 893
2018-05-21 21:00 | 855 | 852
2018-05-21 21:30 | 813 | 813
2018-05-21 22:00 | 805 | 804
2018-05-21 22:30 | 776 | 774
2018-05-21 23:00 | 756 | 753
2018-05-21 23:30 | 716 | 713
2018-05-22 | 677 | 671
2018-05-22 00:30 | 632 | 621
2018-05-22 01:00 | 608 | 595
2018-05-22 01:30 | 587 | 570
2018-05-22 02:00 | 586 | 565
2018-05-22 02:30 | 577 | 556
2018-05-22 03:00 | 577 | 555
2018-05-22 03:30 | 577 | 555
2018-05-22 04:00 | 584 | 562
2018-05-22 04:30 | 596 | 576
2018-05-22 05:00 | 611 | 595
2018-05-22 05:30 | 650 | 641
2018-05-22 06:00 | 696 | 691
2018-05-22 06:30 | 778 | 776
2018-05-22 07:00 | 847 | 847
2018-05-22 07:30 | 885 | 885
2018-05-22 08:00 | 867 | 867
2018-05-22 08:30 | 825 | 825
2018-05-22 09:00 | 788 | 788
2018-05-22 09:30 | 767 | 767
2018-05-22 10:00 | 731 | 731
2018-05-22 10:30 | 714 | 713
2018-05-22 11:00 | 694 | 693
2018-05-22 11:30 | 655 | 653
2018-05-22 12:00 | 643 | 640
2018-05-22 12:30 | 649 | 646
2018-05-22 13:00 | 661 | 659
2018-05-22 13:30 | 671 | 669
2018-05-22 14:00 | 696 | 694
2018-05-22 14:30 | 725 | 722
2018-05-22 15:00 | 747 | 745
2018-05-22 15:30 | 773 | 772
2018-05-22 16:00 | 806 | 805
2018-05-22 16:30 | 849 | 849
2018-05-22 17:00 | 892 | 890
2018-05-22 17:30 | 933 | 933
2018-05-22 18:00 | 968 | 964
2018-05-22 18:30 | 953 | 948
2018-05-22 19:00 | 959 | 956
2018-05-22 19:30 | 935 | 931
2018-05-22 20:00 | 922 | 918
2018-05-22 20:30 | 953 | 950
2018-05-22 21:00 | 890 | 888
2018-05-22 21:30 | 835 | 835
2018-05-22 22:00 | 793 | 792
2018-05-22 22:30 | 789 | 787
2018-05-22 23:00 | 762 | 759
2018-05-22 23:30 | 728 | 723
2018-05-23 | 682 | 674
2018-05-23 00:30 | 639 | 627
2018-05-23 01:00 | 616 | 600
2018-05-23 01:30 | 622 | 608
2018-05-23 02:00 | 598 | 583
2018-05-23 02:30 | 577 | 559
2018-05-23 03:00 | 577 | 560
2018-05-23 03:30 | 571 | 552
2018-05-23 04:00 | 568 | 548
2018-05-23 04:30 | 587 | 569
2018-05-23 05:00 | 608 | 591
2018-05-23 05:30 | 644 | 632
2018-05-23 06:00 | 699 | 693
2018-05-23 06:30 | 789 | 779
2018-05-23 07:00 | 856 | 847
2018-05-23 07:30 | 895 | 890
2018-05-23 08:00 | 912 | 909
2018-05-23 08:30 | 949 | 944
2018-05-23 09:00 | 907 | 900
2018-05-23 09:30 | 880 | 872
2018-05-23 10:00 | 851 | 849
2018-05-23 10:30 | 849 | 848
2018-05-23 11:00 | 849 | 848
2018-05-23 11:30 | 841 | 840
2018-05-23 12:00 | 835 | 833
2018-05-23 12:30 | 839 | 837
2018-05-23 13:00 | 839 | 837
2018-05-23 13:30 | 846 | 845
2018-05-23 14:00 | 859 | 858
2018-05-23 14:30 | 883 | 883
2018-05-23 15:00 | 799 | 798
2018-05-23 15:30 | 803 | 801
2018-05-23 16:00 | 839 | 838
2018-05-23 16:30 | 867 | 866
2018-05-23 17:00 | 914 | 911
2018-05-23 17:30 | 950 | 948
2018-05-23 18:00 | 978 | 975
2018-05-23 18:30 | 956 | 949
2018-05-23 19:00 | 961 | 953
2018-05-23 19:30 | 927 | 925
2018-05-23 20:00 | 914 | 912
2018-05-23 20:30 | 902 | 899
2018-05-23 21:00 | 858 | 856
2018-05-23 21:30 | 819 | 818
2018-05-23 22:00 | 786 | 784
2018-05-23 22:30 | 775 | 772
2018-05-23 23:00 | 760 | 757
2018-05-23 23:30 | 721 | 715
2018-05-24 | 675 | 666
2018-05-24 00:30 | 635 | 625
2018-05-24 01:00 | 603 | 589
2018-05-24 01:30 | 588 | 572
2018-05-24 02:00 | 580 | 560
2018-05-24 02:30 | 562 | 540
2018-05-24 03:00 | 566 | 543
2018-05-24 03:30 | 570 | 544
2018-05-24 04:00 | 572 | 547
2018-05-24 04:30 | 586 | 563
2018-05-24 05:00 | 603 | 584
2018-05-24 05:30 | 647 | 636
2018-05-24 06:00 | 688 | 683
2018-05-24 06:30 | 763 | 759
2018-05-24 07:00 | 824 | 819
2018-05-24 07:30 | 862 | 859
2018-05-24 08:00 | 850 | 847
2018-05-24 08:30 | 817 | 812
2018-05-24 09:00 | 788 | 786
2018-05-24 09:30 | 763 | 762
2018-05-24 10:00 | 737 | 736
2018-05-24 10:30 | 716 | 716
2018-05-24 11:00 | 711 | 711
2018-05-24 11:30 | 708 | 708
2018-05-24 12:00 | 717 | 716
2018-05-24 12:30 | 717 | 716
2018-05-24 13:00 | 744 | 743
2018-05-24 13:30 | 761 | 761
2018-05-24 14:00 | 793 | 792
2018-05-24 14:30 | 809 | 809
2018-05-24 15:00 | 792 | 792
2018-05-24 15:30 | 792 | 792
2018-05-24 16:00 | 825 | 825
2018-05-24 16:30 | 868 | 868
2018-05-24 17:00 | 907 | 907
2018-05-24 17:30 | 958 | 958
2018-05-24 18:00 | 988 | 988
2018-05-24 18:30 | 966 | 965
2018-05-24 19:00 | 972 | 970
2018-05-24 19:30 | 946 | 943
2018-05-24 20:00 | 931 | 930
2018-05-24 20:30 | 922 | 921
2018-05-24 21:00 | 886 | 885
2018-05-24 21:30 | 837 | 835
2018-05-24 22:00 | 800 | 797
2018-05-24 22:30 | 788 | 783
2018-05-24 23:00 | 777 | 773
2018-05-24 23:30 | 728 | 726
2018-05-25 | 678 | 673
2018-05-25 00:30 | 631 | 621
2018-05-25 01:00 | 607 | 594
2018-05-25 01:30 | 590 | 573
2018-05-25 02:00 | 580 | 560
2018-05-25 02:30 | 577 | 556
2018-05-25 03:00 | 574 | 550
2018-05-25 03:30 | 577 | 553
2018-05-25 04:00 | 577 | 553
2018-05-25 04:30 | 590 | 569
2018-05-25 05:00 | 606 | 589
2018-05-25 05:30 | 643 | 631
2018-05-25 06:00 | 681 | 675
2018-05-25 06:30 | 756 | 754
2018-05-25 07:00 | 823 | 820
2018-05-25 07:30 | 876 | 872
2018-05-25 08:00 | 883 | 881
2018-05-25 08:30 | 881 | 879
2018-05-25 09:00 | 851 | 849
2018-05-25 09:30 | 822 | 820
2018-05-25 10:00 | 786 | 783
2018-05-25 10:30 | 773 | 770
2018-05-25 11:00 | 756 | 752
2018-05-25 11:30 | 746 | 746
2018-05-25 12:00 | 744 | 744
2018-05-25 12:30 | 732 | 732
2018-05-25 13:00 | 740 | 740
2018-05-25 13:30 | 751 | 751
2018-05-25 14:00 | 773 | 773
2018-05-25 14:30 | 789 | 789
2018-05-25 15:00 | 801 | 801
2018-05-25 15:30 | 817 | 817
2018-05-25 16:00 | 841 | 841
2018-05-25 16:30 | 876 | 876
2018-05-25 17:00 | 913 | 913
2018-05-25 17:30 | 949 | 947
2018-05-25 18:00 | 957 | 954
2018-05-25 18:30 | 943 | 938
2018-05-25 19:00 | 940 | 933
2018-05-25 19:30 | 916 | 910
2018-05-25 20:00 | 893 | 891
2018-05-25 20:30 | 884 | 881
2018-05-25 21:00 | 845 | 844
2018-05-25 21:30 | 807 | 807
2018-05-25 22:00 | 782 | 781
2018-05-25 22:30 | 774 | 773
2018-05-25 23:00 | 776 | 774
2018-05-25 23:30 | 731 | 728
2018-05-26 | 688 | 681
2018-05-26 00:30 | 635 | 625
2018-05-26 01:00 | 608 | 594
2018-05-26 01:30 | 593 | 575
2018-05-26 02:00 | 585 | 562
2018-05-26 02:30 | 583 | 557
2018-05-26 03:00 | 577 | 550
2018-05-26 03:30 | 574 | 545
2018-05-26 04:00 | 577 | 548
2018-05-26 04:30 | 579 | 552
2018-05-26 05:00 | 581 | 556
2018-05-26 05:30 | 597 | 575
2018-05-26 06:00 | 610 | 590
2018-05-26 06:30 | 641 | 626
2018-05-26 07:00 | 662 | 650
2018-05-26 07:30 | 687 | 679
2018-05-26 08:00 | 705 | 701
2018-05-26 08:30 | 737 | 736
2018-05-26 09:00 | 760 | 760
2018-05-26 09:30 | 771 | 771
2018-05-26 10:00 | 746 | 745
2018-05-26 10:30 | 704 | 703
2018-05-26 11:00 | 679 | 677
2018-05-26 11:30 | 672 | 671
2018-05-26 12:00 | 657 | 654
2018-05-26 12:30 | 656 | 653
2018-05-26 13:00 | 646 | 643
2018-05-26 13:30 | 673 | 670
2018-05-26 14:00 | 707 | 705
2018-05-26 14:30 | 719 | 717
2018-05-26 15:00 | 727 | 725
2018-05-26 15:30 | 741 | 739
2018-05-26 16:00 | 757 | 755
2018-05-26 16:30 | 788 | 787
2018-05-26 17:00 | 830 | 830
2018-05-26 17:30 | 881 | 880
2018-05-26 18:00 | 893 | 890
2018-05-26 18:30 | 889 | 886
2018-05-26 19:00 | 875 | 870
2018-05-26 19:30 | 845 | 844
2018-05-26 20:00 | 842 | 841
2018-05-26 20:30 | 831 | 831
2018-05-26 21:00 | 801 | 800
2018-05-26 21:30 | 776 | 775
2018-05-26 22:00 | 763 | 760
2018-05-26 22:30 | 752 | 748
2018-05-26 23:00 | 761 | 756
2018-05-26 23:30 | 725 | 719
2018-05-27 | 682 | 672
2018-05-27 00:30 | 640 | 624
2018-05-27 01:00 | 619 | 600
2018-05-27 01:30 | 605 | 582
2018-05-27 02:00 | 587 | 561
2018-05-27 02:30 | 581 | 552
2018-05-27 03:00 | 573 | 543
2018-05-27 03:30 | 569 | 537
2018-05-27 04:00 | 566 | 533
2018-05-27 04:30 | 569 | 537
2018-05-27 05:00 | 567 | 535
2018-05-27 05:30 | 574 | 545
2018-05-27 06:00 | 582 | 556
2018-05-27 06:30 | 605 | 582
2018-05-27 07:00 | 626 | 603
2018-05-27 07:30 | 652 | 634
2018-05-27 08:00 | 663 | 649
2018-05-27 08:30 | 679 | 670
2018-05-27 09:00 | 685 | 677
2018-05-27 09:30 | 676 | 671
2018-05-27 10:00 | 658 | 652
2018-05-27 10:30 | 647 | 642
2018-05-27 11:00 | 670 | 666
2018-05-27 11:30 | 660 | 655
2018-05-27 12:00 | 649 | 644
2018-05-27 12:30 | 638 | 632
2018-05-27 13:00 | 639 | 633
2018-05-27 13:30 | 636 | 631
2018-05-27 14:00 | 650 | 646
2018-05-27 14:30 | 678 | 674
2018-05-27 15:00 | 690 | 687
2018-05-27 15:30 | 691 | 687
2018-05-27 16:00 | 732 | 730
2018-05-27 16:30 | 783 | 779
2018-05-27 17:00 | 832 | 829
2018-05-27 17:30 | 884 | 881
2018-05-27 18:00 | 902 | 895
2018-05-27 18:30 | 896 | 888
2018-05-27 19:00 | 890 | 881
2018-05-27 19:30 | 855 | 853
2018-05-27 20:00 | 849 | 849
2018-05-27 20:30 | 842 | 842
2018-05-27 21:00 | 807 | 807
2018-05-27 21:30 | 777 | 775
2018-05-27 22:00 | 752 | 749
2018-05-27 22:30 | 739 | 734
2018-05-27 23:00 | 742 | 737
2018-05-27 23:30 | 706 | 699
2018-05-28 | 671 | 658
2018-05-28 00:30 | 631 | 614
2018-05-28 01:00 | 609 | 589
2018-05-28 01:30 | 596 | 571
2018-05-28 02:00 | 584 | 555
2018-05-28 02:30 | 577 | 546
2018-05-28 03:00 | 575 | 543
2018-05-28 03:30 | 572 | 541
2018-05-28 04:00 | 575 | 545
2018-05-28 04:30 | 586 | 557
2018-05-28 05:00 | 607 | 584
2018-05-28 05:30 | 635 | 620
2018-05-28 06:00 | 676 | 668
2018-05-28 06:30 | 748 | 743
2018-05-28 07:00 | 821 | 818
2018-05-28 07:30 | 879 | 877
2018-05-28 08:00 | 883 | 880
2018-05-28 08:30 | 866 | 864
2018-05-28 09:00 | 832 | 829
2018-05-28 09:30 | 811 | 809
2018-05-28 10:00 | 800 | 798
2018-05-28 10:30 | 799 | 798
2018-05-28 11:00 | 785 | 784
2018-05-28 11:30 | 766 | 765
2018-05-28 12:00 | 809 | 808
2018-05-28 12:30 | 796 | 794
2018-05-28 13:00 | 787 | 784
2018-05-28 13:30 | 819 | 817
2018-05-28 14:00 | 838 | 836
2018-05-28 14:30 | 840 | 839
2018-05-28 15:00 | 844 | 842
2018-05-28 15:30 | 878 | 876
2018-05-28 16:00 | 906 | 904
2018-05-28 16:30 | 943 | 942
2018-05-28 17:00 | 996 | 996
2018-05-28 17:30 | 1058 | 1057
2018-05-28 18:00 | 1071 | 1068
2018-05-28 18:30 | 1051 | 1045
2018-05-28 19:00 | 1035 | 1030
2018-05-28 19:30 | 1012 | 1010
2018-05-28 20:00 | 987 | 985
2018-05-28 20:30 | 968 | 966
2018-05-28 21:00 | 924 | 921
2018-05-28 21:30 | 880 | 875
2018-05-28 22:00 | 845 | 841
2018-05-28 22:30 | 812 | 807
2018-05-28 23:00 | 796 | 789
2018-05-28 23:30 | 759 | 750
2018-05-29 | 715 | 707
2018-05-29 00:30 | 667 | 654
2018-05-29 01:00 | 637 | 621
2018-05-29 01:30 | 618 | 600
2018-05-29 02:00 | 608 | 587
2018-05-29 02:30 | 608 | 587
2018-05-29 03:00 | 609 | 585
2018-05-29 03:30 | 605 | 581
2018-05-29 04:00 | 598 | 572
2018-05-29 04:30 | 620 | 597
2018-05-29 05:00 | 637 | 619
2018-05-29 05:30 | 666 | 655
2018-05-29 06:00 | 708 | 701
2018-05-29 06:30 | 794 | 790
2018-05-29 07:00 | 833 | 832
2018-05-29 07:30 | 891 | 891
2018-05-29 08:00 | 888 | 887
2018-05-29 08:30 | 865 | 865
2018-05-29 09:00 | 846 | 846
2018-05-29 09:30 | 822 | 822
2018-05-29 10:00 | 808 | 808
2018-05-29 10:30 | 786 | 786
2018-05-29 11:00 | 780 | 780
2018-05-29 11:30 | 790 | 790
2018-05-29 12:00 | 807 | 806
2018-05-29 12:30 | 814 | 814
2018-05-29 13:00 | 836 | 835
2018-05-29 13:30 | 835 | 835
2018-05-29 14:00 | 820 | 820
2018-05-29 14:30 | 809 | 809
2018-05-29 15:00 | 840 | 840
2018-05-29 15:30 | 858 | 858
2018-05-29 16:00 | 893 | 893
2018-05-29 16:30 | 931 | 931
2018-05-29 17:00 | 974 | 974
2018-05-29 17:30 | 1028 | 1028
2018-05-29 18:00 | 1054 | 1053
2018-05-29 18:30 | 1034 | 1030
2018-05-29 19:00 | 1034 | 1030
2018-05-29 19:30 | 1018 | 1013
2018-05-29 20:00 | 1003 | 1001
2018-05-29 20:30 | 988 | 986
2018-05-29 21:00 | 919 | 918
2018-05-29 21:30 | 868 | 865
2018-05-29 22:00 | 830 | 826
2018-05-29 22:30 | 811 | 809
2018-05-29 23:00 | 809 | 807
2018-05-29 23:30 | 760 | 756
2018-05-30 | 712 | 707
2018-05-30 00:30 | 663 | 653
2018-05-30 01:00 | 638 | 625
2018-05-30 01:30 | 618 | 601
2018-05-30 02:00 | 611 | 591
2018-05-30 02:30 | 602 | 580
2018-05-30 03:00 | 597 | 574
2018-05-30 03:30 | 596 | 574
2018-05-30 04:00 | 599 | 579
2018-05-30 04:30 | 613 | 594
2018-05-30 05:00 | 628 | 613
2018-05-30 05:30 | 666 | 656
2018-05-30 06:00 | 711 | 706
2018-05-30 06:30 | 792 | 792
2018-05-30 07:00 | 881 | 880
2018-05-30 07:30 | 926 | 922
2018-05-30 08:00 | 928 | 924
2018-05-30 08:30 | 895 | 890
2018-05-30 09:00 | 852 | 848
2018-05-30 09:30 | 826 | 824
2018-05-30 10:00 | 784 | 781
2018-05-30 10:30 | 757 | 755
2018-05-30 11:00 | 742 | 741
2018-05-30 11:30 | 732 | 731
2018-05-30 12:00 | 735 | 734
2018-05-30 12:30 | 735 | 734
2018-05-30 13:00 | 743 | 743
2018-05-30 13:30 | 757 | 757
2018-05-30 14:00 | 770 | 770
2018-05-30 14:30 | 797 | 797
2018-05-30 15:00 | 822 | 822
2018-05-30 15:30 | 840 | 840
2018-05-30 16:00 | 869 | 868
2018-05-30 16:30 | 914 | 914
2018-05-30 17:00 | 959 | 959
2018-05-30 17:30 | 1020 | 1020
2018-05-30 18:00 | 1037 | 1037
2018-05-30 18:30 | 1016 | 1015
2018-05-30 19:00 | 1010 | 1008
2018-05-30 19:30 | 977 | 976
2018-05-30 20:00 | 958 | 957
2018-05-30 20:30 | 947 | 947
2018-05-30 21:00 | 897 | 897
2018-05-30 21:30 | 858 | 857
2018-05-30 22:00 | 822 | 820
2018-05-30 22:30 | 807 | 805
2018-05-30 23:00 | 793 | 791
2018-05-30 23:30 | 760 | 757
2018-05-31 | 712 | 704
2018-05-31 00:30 | 665 | 652
2018-05-31 01:00 | 636 | 620
2018-05-31 01:30 | 624 | 605
2018-05-31 02:00 | 612 | 591
2018-05-31 02:30 | 609 | 586
2018-05-31 03:00 | 605 | 582
2018-05-31 03:30 | 605 | 583
2018-05-31 04:00 | 608 | 586
2018-05-31 04:30 | 621 | 601
2018-05-31 05:00 | 638 | 622
2018-05-31 05:30 | 678 | 668
2018-05-31 06:00 | 724 | 719
2018-05-31 06:30 | 810 | 807
2018-05-31 07:00 | 898 | 898
2018-05-31 07:30 | 941 | 941
2018-05-31 08:00 | 924 | 924
2018-05-31 08:30 | 886 | 886
2018-05-31 09:00 | 839 | 839
2018-05-31 09:30 | 798 | 798
2018-05-31 10:00 | 754 | 754
2018-05-31 10:30 | 731 | 731
2018-05-31 11:00 | 710 | 710
2018-05-31 11:30 | 695 | 695
2018-05-31 12:00 | 689 | 689
2018-05-31 12:30 | 688 | 688
2018-05-31 13:00 | 691 | 691
2018-05-31 13:30 | 699 | 699
2018-05-31 14:00 | 726 | 726
2018-05-31 14:30 | 743 | 743
2018-05-31 15:00 | 765 | 765
2018-05-31 15:30 | 794 | 793
2018-05-31 16:00 | 830 | 829
2018-05-31 16:30 | 882 | 880
2018-05-31 17:00 | 927 | 925
2018-05-31 17:30 | 997 | 996
2018-05-31 18:00 | 1041 | 1041
2018-05-31 18:30 | 1044 | 1044
2018-05-31 19:00 | 1054 | 1053
2018-05-31 19:30 | 1034 | 1032
2018-05-31 20:00 | 1002 | 1001
2018-05-31 20:30 | 990 | 990
2018-05-31 21:00 | 953 | 952
2018-05-31 21:30 | 927 | 924
2018-05-31 22:00 | 892 | 889
2018-05-31 22:30 | 845 | 844
2018-05-31 23:00 | 830 | 828
2018-05-31 23:30 | 785 | 780
2018-06-01 | 737 | 728
2018-06-01 00:30 | 688 | 675
2018-06-01 01:00 | 654 | 643
2018-06-01 01:30 | 637 | 622
2018-06-01 02:00 | 622 | 604
2018-06-01 02:30 | 620 | 600
2018-06-01 03:00 | 614 | 591
2018-06-01 03:30 | 616 | 594
2018-06-01 04:00 | 617 | 596
2018-06-01 04:30 | 632 | 614
2018-06-01 05:00 | 654 | 640
2018-06-01 05:30 | 690 | 682
2018-06-01 06:00 | 739 | 736
2018-06-01 06:30 | 833 | 833
2018-06-01 07:00 | 931 | 931
2018-06-01 07:30 | 1010 | 1010
2018-06-01 08:00 | 1000 | 1000
2018-06-01 08:30 | 941 | 941
2018-06-01 09:00 | 897 | 895
2018-06-01 09:30 | 858 | 855
2018-06-01 10:00 | 824 | 823
2018-06-01 10:30 | 790 | 788
2018-06-01 11:00 | 770 | 767
2018-06-01 11:30 | 750 | 748
2018-06-01 12:00 | 735 | 734
2018-06-01 12:30 | 733 | 733
2018-06-01 13:00 | 732 | 732
2018-06-01 13:30 | 741 | 741
2018-06-01 14:00 | 755 | 755
2018-06-01 14:30 | 778 | 778
2018-06-01 15:00 | 795 | 795
2018-06-01 15:30 | 820 | 820
2018-06-01 16:00 | 863 | 862
2018-06-01 16:30 | 910 | 909
2018-06-01 17:00 | 960 | 960
2018-06-01 17:30 | 1010 | 1009
2018-06-01 18:00 | 1031 | 1031
2018-06-01 18:30 | 1021 | 1021
2018-06-01 19:00 | 1023 | 1022
2018-06-01 19:30 | 993 | 992
2018-06-01 20:00 | 966 | 966
2018-06-01 20:30 | 961 | 961
2018-06-01 21:00 | 923 | 923
2018-06-01 21:30 | 870 | 870
2018-06-01 22:00 | 846 | 846
2018-06-01 22:30 | 834 | 834
2018-06-01 23:00 | 822 | 822
2018-06-01 23:30 | 781 | 780
2018-06-02 | 731 | 727
2018-06-02 00:30 | 679 | 673
2018-06-02 01:00 | 638 | 626
2018-06-02 01:30 | 617 | 602
2018-06-02 02:00 | 602 | 583
2018-06-02 02:30 | 598 | 577
2018-06-02 03:00 | 591 | 569
2018-06-02 03:30 | 587 | 566
2018-06-02 04:00 | 590 | 568
2018-06-02 04:30 | 598 | 578
2018-06-02 05:00 | 605 | 588
2018-06-02 05:30 | 628 | 614
2018-06-02 06:00 | 650 | 640
2018-06-02 06:30 | 689 | 682
2018-06-02 07:00 | 729 | 725
2018-06-02 07:30 | 766 | 764
2018-06-02 08:00 | 777 | 775
2018-06-02 08:30 | 776 | 775
2018-06-02 09:00 | 761 | 760
2018-06-02 09:30 | 744 | 743
2018-06-02 10:00 | 709 | 707
2018-06-02 10:30 | 675 | 674
2018-06-02 11:00 | 649 | 648
2018-06-02 11:30 | 618 | 617
2018-06-02 12:00 | 606 | 604
2018-06-02 12:30 | 594 | 591
2018-06-02 13:00 | 593 | 589
2018-06-02 13:30 | 599 | 595
2018-06-02 14:00 | 612 | 609
2018-06-02 14:30 | 635 | 632
2018-06-02 15:00 | 662 | 660
2018-06-02 15:30 | 687 | 685
2018-06-02 16:00 | 718 | 717
2018-06-02 16:30 | 762 | 762
2018-06-02 17:00 | 822 | 822
2018-06-02 17:30 | 876 | 875
2018-06-02 18:00 | 896 | 896
2018-06-02 18:30 | 896 | 893
2018-06-02 19:00 | 896 | 892
2018-06-02 19:30 | 880 | 875
2018-06-02 20:00 | 870 | 868
2018-06-02 20:30 | 872 | 871
2018-06-02 21:00 | 832 | 829
2018-06-02 21:30 | 801 | 801
2018-06-02 22:00 | 779 | 778
2018-06-02 22:30 | 778 | 777
2018-06-02 23:00 | 779 | 778
2018-06-02 23:30 | 741 | 738
2018-06-03 | 699 | 693
2018-06-03 00:30 | 655 | 645
2018-06-03 01:00 | 632 | 619
2018-06-03 01:30 | 609 | 594
2018-06-03 02:00 | 591 | 571
2018-06-03 02:30 | 584 | 565
2018-06-03 03:00 | 575 | 554
2018-06-03 03:30 | 577 | 555
2018-06-03 04:00 | 575 | 553
2018-06-03 04:30 | 578 | 556
2018-06-03 05:00 | 585 | 563
2018-06-03 05:30 | 589 | 569
2018-06-03 06:00 | 599 | 582
2018-06-03 06:30 | 623 | 610
2018-06-03 07:00 | 646 | 632
2018-06-03 07:30 | 672 | 663
2018-06-03 08:00 | 684 | 677
2018-06-03 08:30 | 695 | 690
2018-06-03 09:00 | 692 | 689
2018-06-03 09:30 | 675 | 673
2018-06-03 10:00 | 666 | 664
2018-06-03 10:30 | 643 | 640
2018-06-03 11:00 | 625 | 622
2018-06-03 11:30 | 606 | 602
2018-06-03 12:00 | 602 | 598
2018-06-03 12:30 | 602 | 598
2018-06-03 13:00 | 608 | 604
2018-06-03 13:30 | 616 | 612
2018-06-03 14:00 | 628 | 626
2018-06-03 14:30 | 654 | 651
2018-06-03 15:00 | 678 | 675
2018-06-03 15:30 | 704 | 703
2018-06-03 16:00 | 741 | 741
2018-06-03 16:30 | 782 | 781
2018-06-03 17:00 | 835 | 832
2018-06-03 17:30 | 884 | 884
2018-06-03 18:00 | 902 | 902
2018-06-03 18:30 | 893 | 893
2018-06-03 19:00 | 891 | 890
2018-06-03 19:30 | 866 | 865
2018-06-03 20:00 | 857 | 855
2018-06-03 20:30 | 852 | 850
2018-06-03 21:00 | 816 | 816
2018-06-03 21:30 | 785 | 784
2018-06-03 22:00 | 764 | 763
2018-06-03 22:30 | 754 | 751
2018-06-03 23:00 | 752 | 749
2018-06-03 23:30 | 717 | 712
2018-06-04 | 675 | 666
2018-06-04 00:30 | 635 | 621
2018-06-04 01:00 | 610 | 593
2018-06-04 01:30 | 595 | 577
2018-06-04 02:00 | 580 | 561
2018-06-04 02:30 | 577 | 556
2018-06-04 03:00 | 572 | 550
2018-06-04 03:30 | 572 | 551
2018-06-04 04:00 | 573 | 552
2018-06-04 04:30 | 591 | 571
2018-06-04 05:00 | 610 | 595
2018-06-04 05:30 | 652 | 644
2018-06-04 06:00 | 698 | 694
2018-06-04 06:30 | 781 | 781
2018-06-04 07:00 | 818 | 818
2018-06-04 07:30 | 871 | 871
2018-06-04 08:00 | 852 | 852
2018-06-04 08:30 | 794 | 793
2018-06-04 09:00 | 743 | 742
2018-06-04 09:30 | 699 | 697
2018-06-04 10:00 | 673 | 670
2018-06-04 10:30 | 659 | 658
2018-06-04 11:00 | 648 | 647
2018-06-04 11:30 | 639 | 638
2018-06-04 12:00 | 625 | 625
2018-06-04 12:30 | 629 | 629
2018-06-04 13:00 | 651 | 651
2018-06-04 13:30 | 686 | 686
2018-06-04 14:00 | 698 | 697
2018-06-04 14:30 | 729 | 728
2018-06-04 15:00 | 738 | 737
2018-06-04 15:30 | 771 | 770
2018-06-04 16:00 | 854 | 853
2018-06-04 16:30 | 904 | 904
2018-06-04 17:00 | 939 | 939
2018-06-04 17:30 | 998 | 998
2018-06-04 18:00 | 1026 | 1025
2018-06-04 18:30 | 1009 | 1008
2018-06-04 19:00 | 1012 | 1011
2018-06-04 19:30 | 982 | 980
2018-06-04 20:00 | 966 | 964
2018-06-04 20:30 | 963 | 960
2018-06-04 21:00 | 907 | 906
2018-06-04 21:30 | 858 | 858
2018-06-04 22:00 | 825 | 822
2018-06-04 22:30 | 801 | 801
2018-06-04 23:00 | 791 | 791
2018-06-04 23:30 | 753 | 752
2018-06-05 | 700 | 697
2018-06-05 00:30 | 649 | 643
2018-06-05 01:00 | 621 | 611
2018-06-05 01:30 | 601 | 589
2018-06-05 02:00 | 590 | 577
2018-06-05 02:30 | 583 | 569
2018-06-05 03:00 | 580 | 564
2018-06-05 03:30 | 578 | 562
2018-06-05 04:00 | 585 | 569
2018-06-05 04:30 | 602 | 587
2018-06-05 05:00 | 621 | 608
2018-06-05 05:30 | 664 | 658
2018-06-05 06:00 | 712 | 710
2018-06-05 06:30 | 807 | 806
2018-06-05 07:00 | 889 | 889
2018-06-05 07:30 | 938 | 938
2018-06-05 08:00 | 923 | 923
2018-06-05 08:30 | 873 | 871
2018-06-05 09:00 | 824 | 819
2018-06-05 09:30 | 784 | 778
2018-06-05 10:00 | 748 | 745
2018-06-05 10:30 | 725 | 723
2018-06-05 11:00 | 710 | 707
2018-06-05 11:30 | 691 | 688
2018-06-05 12:00 | 698 | 694
2018-06-05 12:30 | 696 | 694
2018-06-05 13:00 | 692 | 691
2018-06-05 13:30 | 701 | 700
2018-06-05 14:00 | 716 | 715
2018-06-05 14:30 | 729 | 729
2018-06-05 15:00 | 753 | 752
2018-06-05 15:30 | 784 | 783
2018-06-05 16:00 | 834 | 834
2018-06-05 16:30 | 882 | 882
2018-06-05 17:00 | 944 | 944
2018-06-05 17:30 | 1011 | 1010
2018-06-05 18:00 | 1019 | 1014
2018-06-05 18:30 | 1011 | 1005
2018-06-05 19:00 | 999 | 992
2018-06-05 19:30 | 963 | 958
2018-06-05 20:00 | 963 | 963
2018-06-05 20:30 | 953 | 952
2018-06-05 21:00 | 902 | 902
2018-06-05 21:30 | 859 | 858
2018-06-05 22:00 | 814 | 813
2018-06-05 22:30 | 792 | 790
2018-06-05 23:00 | 786 | 782
2018-06-05 23:30 | 740 | 735
2018-06-06 | 691 | 682
2018-06-06 00:30 | 635 | 625
2018-06-06 01:00 | 605 | 593
2018-06-06 01:30 | 585 | 571
2018-06-06 02:00 | 571 | 555
2018-06-06 02:30 | 562 | 545
2018-06-06 03:00 | 556 | 538
2018-06-06 03:30 | 558 | 539
2018-06-06 04:00 | 562 | 542
2018-06-06 04:30 | 579 | 562
2018-06-06 05:00 | 599 | 585
2018-06-06 05:30 | 640 | 633
2018-06-06 06:00 | 695 | 693
2018-06-06 06:30 | 785 | 785
2018-06-06 07:00 | 867 | 867
2018-06-06 07:30 | 915 | 915
2018-06-06 08:00 | 893 | 891
2018-06-06 08:30 | 856 | 854
2018-06-06 09:00 | 823 | 823
2018-06-06 09:30 | 822 | 821
2018-06-06 10:00 | 758 | 757
2018-06-06 10:30 | 717 | 715
2018-06-06 11:00 | 696 | 695
2018-06-06 11:30 | 692 | 691
2018-06-06 12:00 | 719 | 718
2018-06-06 12:30 | 765 | 763
2018-06-06 13:00 | 778 | 777
2018-06-06 13:30 | 765 | 764
2018-06-06 14:00 | 768 | 767
2018-06-06 14:30 | 780 | 779
2018-06-06 15:00 | 795 | 794
2018-06-06 15:30 | 821 | 820
2018-06-06 16:00 | 867 | 865
2018-06-06 16:30 | 916 | 916
2018-06-06 17:00 | 1014 | 1014
2018-06-06 17:30 | 1028 | 1028
2018-06-06 18:00 | 1038 | 1037
2018-06-06 18:30 | 1021 | 1018
2018-06-06 19:00 | 1009 | 1007
2018-06-06 19:30 | 987 | 984
2018-06-06 20:00 | 977 | 977
2018-06-06 20:30 | 962 | 962
2018-06-06 21:00 | 913 | 913
2018-06-06 21:30 | 872 | 872
2018-06-06 22:00 | 837 | 836
2018-06-06 22:30 | 813 | 812
2018-06-06 23:00 | 813 | 811
2018-06-06 23:30 | 770 | 766
2018-06-07 | 720 | 713
2018-06-07 00:30 | 664 | 651
2018-06-07 01:00 | 630 | 617
2018-06-07 01:30 | 608 | 593
2018-06-07 02:00 | 592 | 575
2018-06-07 02:30 | 592 | 573
2018-06-07 03:00 | 588 | 568
2018-06-07 03:30 | 590 | 571
2018-06-07 04:00 | 596 | 577
2018-06-07 04:30 | 604 | 587
2018-06-07 05:00 | 622 | 607
2018-06-07 05:30 | 661 | 652
2018-06-07 06:00 | 705 | 700
2018-06-07 06:30 | 796 | 795
2018-06-07 07:00 | 875 | 875
2018-06-07 07:30 | 945 | 943
2018-06-07 08:00 | 976 | 974
2018-06-07 08:30 | 978 | 975
2018-06-07 09:00 | 967 | 964
2018-06-07 09:30 | 960 | 957
2018-06-07 10:00 | 928 | 927
2018-06-07 10:30 | 892 | 892
2018-06-07 11:00 | 851 | 851
2018-06-07 11:30 | 804 | 804
2018-06-07 12:00 | 783 | 782
2018-06-07 12:30 | 798 | 795
2018-06-07 13:00 | 823 | 821
2018-06-07 13:30 | 820 | 818
2018-06-07 14:00 | 816 | 815
2018-06-07 14:30 | 810 | 808
2018-06-07 15:00 | 826 | 824
2018-06-07 15:30 | 853 | 851
2018-06-07 16:00 | 880 | 879
2018-06-07 16:30 | 916 | 915
2018-06-07 17:00 | 961 | 961
2018-06-07 17:30 | 1023 | 1023
2018-06-07 18:00 | 1047 | 1047
2018-06-07 18:30 | 1024 | 1024
2018-06-07 19:00 | 1040 | 1040
2018-06-07 19:30 | 1006 | 1005
2018-06-07 20:00 | 991 | 990
2018-06-07 20:30 | 982 | 982
2018-06-07 21:00 | 939 | 939
2018-06-07 21:30 | 892 | 891
2018-06-07 22:00 | 850 | 847
2018-06-07 22:30 | 822 | 819
2018-06-07 23:00 | 814 | 809
2018-06-07 23:30 | 768 | 765
2018-06-08 | 714 | 712
2018-06-08 00:30 | 690 | 686
2018-06-08 01:00 | 634 | 627
2018-06-08 01:30 | 614 | 604
2018-06-08 02:00 | 598 | 586
2018-06-08 02:30 | 593 | 578
2018-06-08 03:00 | 584 | 570
2018-06-08 03:30 | 588 | 574
2018-06-08 04:00 | 593 | 578
2018-06-08 04:30 | 606 | 592
2018-06-08 05:00 | 623 | 611
2018-06-08 05:30 | 662 | 655
2018-06-08 06:00 | 701 | 699
2018-06-08 06:30 | 783 | 783
2018-06-08 07:00 | 867 | 866
2018-06-08 07:30 | 930 | 926
2018-06-08 08:00 | 935 | 931
2018-06-08 08:30 | 919 | 916
2018-06-08 09:00 | 887 | 886
2018-06-08 09:30 | 861 | 860
2018-06-08 10:00 | 847 | 846
2018-06-08 10:30 | 793 | 793
2018-06-08 11:00 | 763 | 763
2018-06-08 11:30 | 774 | 773
2018-06-08 12:00 | 763 | 763
2018-06-08 12:30 | 753 | 753
2018-06-08 13:00 | 786 | 786
2018-06-08 13:30 | 791 | 790
2018-06-08 14:00 | 802 | 801
2018-06-08 14:30 | 824 | 824
2018-06-08 15:00 | 827 | 826
2018-06-08 15:30 | 877 | 877
2018-06-08 16:00 | 944 | 943
2018-06-08 16:30 | 981 | 980
2018-06-08 17:00 | 1031 | 1031
2018-06-08 17:30 | 1065 | 1063
2018-06-08 18:00 | 1073 | 1070
2018-06-08 18:30 | 1058 | 1056
2018-06-08 19:00 | 1049 | 1047
2018-06-08 19:30 | 1012 | 1011
2018-06-08 20:00 | 1016 | 1016
2018-06-08 20:30 | 1004 | 1004
2018-06-08 21:00 | 923 | 922
2018-06-08 21:30 | 894 | 894
2018-06-08 22:00 | 882 | 881
2018-06-08 22:30 | 816 | 813
2018-06-08 23:00 | 808 | 808
2018-06-08 23:30 | 770 | 769
2018-06-09 | 728 | 726
2018-06-09 00:30 | 704 | 701
2018-06-09 01:00 | 672 | 668
2018-06-09 01:30 | 605 | 596
2018-06-09 02:00 | 583 | 570
2018-06-09 02:30 | 567 | 552
2018-06-09 03:00 | 565 | 550
2018-06-09 03:30 | 561 | 545
2018-06-09 04:00 | 564 | 548
2018-06-09 04:30 | 566 | 551
2018-06-09 05:00 | 576 | 562
2018-06-09 05:30 | 590 | 578
2018-06-09 06:00 | 606 | 595
2018-06-09 06:30 | 640 | 634
2018-06-09 07:00 | 676 | 671
2018-06-09 07:30 | 720 | 718
2018-06-09 08:00 | 756 | 755
2018-06-09 08:30 | 779 | 779
2018-06-09 09:00 | 799 | 799
2018-06-09 09:30 | 815 | 815
2018-06-09 10:00 | 816 | 816
2018-06-09 10:30 | 804 | 803
2018-06-09 11:00 | 799 | 798
2018-06-09 11:30 | 793 | 792
2018-06-09 12:00 | 782 | 782
2018-06-09 12:30 | 759 | 759
2018-06-09 13:00 | 727 | 727
2018-06-09 13:30 | 713 | 713
2018-06-09 14:00 | 725 | 725
2018-06-09 14:30 | 730 | 730
2018-06-09 15:00 | 727 | 727
2018-06-09 15:30 | 727 | 727
2018-06-09 16:00 | 746 | 746
2018-06-09 16:30 | 784 | 784
2018-06-09 17:00 | 841 | 840
2018-06-09 17:30 | 909 | 909
2018-06-09 18:00 | 900 | 899
2018-06-09 18:30 | 897 | 896
2018-06-09 19:00 | 905 | 905
2018-06-09 19:30 | 901 | 900
2018-06-09 20:00 | 884 | 883
2018-06-09 20:30 | 879 | 877
2018-06-09 21:00 | 835 | 834
2018-06-09 21:30 | 792 | 792
2018-06-09 22:00 | 776 | 776
2018-06-09 22:30 | 762 | 761
2018-06-09 23:00 | 772 | 772
2018-06-09 23:30 | 741 | 740
2018-06-10 | 695 | 691
2018-06-10 00:30 | 653 | 646
2018-06-10 01:00 | 624 | 614
2018-06-10 01:30 | 601 | 587
2018-06-10 02:00 | 581 | 564
2018-06-10 02:30 | 569 | 549
2018-06-10 03:00 | 561 | 539
2018-06-10 03:30 | 559 | 538
2018-06-10 04:00 | 558 | 536
2018-06-10 04:30 | 563 | 542
2018-06-10 05:00 | 564 | 544
2018-06-10 05:30 | 578 | 559
2018-06-10 06:00 | 590 | 572
2018-06-10 06:30 | 606 | 592
2018-06-10 07:00 | 622 | 610
2018-06-10 07:30 | 653 | 642
2018-06-10 08:00 | 674 | 668
2018-06-10 08:30 | 704 | 700
2018-06-10 09:00 | 711 | 709
2018-06-10 09:30 | 736 | 736
2018-06-10 10:00 | 712 | 712
2018-06-10 10:30 | 693 | 692
2018-06-10 11:00 | 646 | 644
2018-06-10 11:30 | 654 | 653
2018-06-10 12:00 | 637 | 635
2018-06-10 12:30 | 620 | 617
2018-06-10 13:00 | 622 | 619
2018-06-10 13:30 | 613 | 610
2018-06-10 14:00 | 632 | 629
2018-06-10 14:30 | 669 | 667
2018-06-10 15:00 | 699 | 697
2018-06-10 15:30 | 716 | 715
2018-06-10 16:00 | 743 | 741
2018-06-10 16:30 | 783 | 783
2018-06-10 17:00 | 837 | 836
2018-06-10 17:30 | 896 | 896
2018-06-10 18:00 | 919 | 915
2018-06-10 18:30 | 918 | 910
2018-06-10 19:00 | 900 | 896
2018-06-10 19:30 | 885 | 881
2018-06-10 20:00 | 861 | 859
2018-06-10 20:30 | 857 | 856
2018-06-10 21:00 | 822 | 822
2018-06-10 21:30 | 791 | 790
2018-06-10 22:00 | 774 | 773
2018-06-10 22:30 | 764 | 762
2018-06-10 23:00 | 768 | 765
2018-06-10 23:30 | 727 | 722
2018-06-11 | 683 | 675
2018-06-11 00:30 | 637 | 624
2018-06-11 01:00 | 611 | 598
2018-06-11 01:30 | 597 | 581
2018-06-11 02:00 | 582 | 564
2018-06-11 02:30 | 573 | 554
2018-06-11 03:00 | 569 | 548
2018-06-11 03:30 | 570 | 548
2018-06-11 04:00 | 580 | 558
2018-06-11 04:30 | 592 | 572
2018-06-11 05:00 | 614 | 599
2018-06-11 05:30 | 653 | 644
2018-06-11 06:00 | 696 | 691
2018-06-11 06:30 | 769 | 769
2018-06-11 07:00 | 847 | 846
2018-06-11 07:30 | 902 | 902
2018-06-11 08:00 | 891 | 891
2018-06-11 08:30 | 853 | 853
2018-06-11 09:00 | 820 | 820
2018-06-11 09:30 | 789 | 789
2018-06-11 10:00 | 747 | 746
2018-06-11 10:30 | 726 | 724
2018-06-11 11:00 | 705 | 704
2018-06-11 11:30 | 698 | 696
2018-06-11 12:00 | 698 | 695
2018-06-11 12:30 | 687 | 685
2018-06-11 13:00 | 729 | 727
2018-06-11 13:30 | 749 | 748
2018-06-11 14:00 | 765 | 764
2018-06-11 14:30 | 773 | 772
2018-06-11 15:00 | 783 | 782
2018-06-11 15:30 | 809 | 808
2018-06-11 16:00 | 846 | 846
2018-06-11 16:30 | 881 | 880
2018-06-11 17:00 | 931 | 930
2018-06-11 17:30 | 999 | 999
2018-06-11 18:00 | 1029 | 1026
2018-06-11 18:30 | 1016 | 1012
2018-06-11 19:00 | 1014 | 1009
2018-06-11 19:30 | 1002 | 994
2018-06-11 20:00 | 972 | 971
2018-06-11 20:30 | 962 | 961
2018-06-11 21:00 | 917 | 917
2018-06-11 21:30 | 875 | 873
2018-06-11 22:00 | 838 | 835
2018-06-11 22:30 | 810 | 809
2018-06-11 23:00 | 803 | 802
2018-06-11 23:30 | 759 | 756
2018-06-12 | 716 | 709
2018-06-12 00:30 | 668 | 657
2018-06-12 01:00 | 642 | 629
2018-06-12 01:30 | 622 | 606
2018-06-12 02:00 | 610 | 592
2018-06-12 02:30 | 600 | 581
2018-06-12 03:00 | 596 | 576
2018-06-12 03:30 | 601 | 582
2018-06-12 04:00 | 603 | 585
2018-06-12 04:30 | 616 | 601
2018-06-12 05:00 | 641 | 629
2018-06-12 05:30 | 683 | 677
2018-06-12 06:00 | 740 | 737
2018-06-12 06:30 | 836 | 831
2018-06-12 07:00 | 918 | 915
2018-06-12 07:30 | 976 | 973
2018-06-12 08:00 | 969 | 963
2018-06-12 08:30 | 926 | 918
2018-06-12 09:00 | 865 | 861
2018-06-12 09:30 | 843 | 841
2018-06-12 10:00 | 812 | 810
2018-06-12 10:30 | 753 | 753
2018-06-12 11:00 | 721 | 721
2018-06-12 11:30 | 717 | 716
2018-06-12 12:00 | 716 | 716
2018-06-12 12:30 | 714 | 714
2018-06-12 13:00 | 725 | 725
2018-06-12 13:30 | 750 | 750
2018-06-12 14:00 | 774 | 773
2018-06-12 14:30 | 790 | 789
2018-06-12 15:00 | 795 | 794
2018-06-12 15:30 | 816 | 815
2018-06-12 16:00 | 844 | 844
2018-06-12 16:30 | 886 | 886
2018-06-12 17:00 | 946 | 944
2018-06-12 17:30 | 1013 | 1013
2018-06-12 18:00 | 1044 | 1042
2018-06-12 18:30 | 1030 | 1026
2018-06-12 19:00 | 1028 | 1023
2018-06-12 19:30 | 1006 | 1003
2018-06-12 20:00 | 988 | 986
2018-06-12 20:30 | 980 | 979
2018-06-12 21:00 | 934 | 933
2018-06-12 21:30 | 891 | 888
2018-06-12 22:00 | 850 | 849
2018-06-12 22:30 | 824 | 823
2018-06-12 23:00 | 813 | 810
2018-06-12 23:30 | 767 | 765
2018-06-13 | 720 | 715
2018-06-13 00:30 | 674 | 665
2018-06-13 01:00 | 643 | 631
2018-06-13 01:30 | 620 | 605
2018-06-13 02:00 | 602 | 584
2018-06-13 02:30 | 598 | 580
2018-06-13 03:00 | 599 | 580
2018-06-13 03:30 | 598 | 579
2018-06-13 04:00 | 600 | 582
2018-06-13 04:30 | 616 | 601
2018-06-13 05:00 | 635 | 623
2018-06-13 05:30 | 679 | 673
2018-06-13 06:00 | 729 | 726
2018-06-13 06:30 | 820 | 817
2018-06-13 07:00 | 906 | 900
2018-06-13 07:30 | 960 | 953
2018-06-13 08:00 | 953 | 945
2018-06-13 08:30 | 915 | 906
2018-06-13 09:00 | 865 | 852
2018-06-13 09:30 | 818 | 812
2018-06-13 10:00 | 785 | 782
2018-06-13 10:30 | 785 | 783
2018-06-13 11:00 | 772 | 772
2018-06-13 11:30 | 789 | 789
2018-06-13 12:00 | 786 | 786
2018-06-13 12:30 | 787 | 786
2018-06-13 13:00 | 810 | 810
2018-06-13 13:30 | 781 | 781
2018-06-13 14:00 | 802 | 802
2018-06-13 14:30 | 830 | 830
2018-06-13 15:00 | 813 | 813
2018-06-13 15:30 | 821 | 821
2018-06-13 16:00 | 863 | 863
2018-06-13 16:30 | 898 | 898
2018-06-13 17:00 | 947 | 947
2018-06-13 17:30 | 1009 | 1007
2018-06-13 18:00 | 1019 | 1017
2018-06-13 18:30 | 1001 | 999
2018-06-13 19:00 | 999 | 997
2018-06-13 19:30 | 980 | 977
2018-06-13 20:00 | 970 | 965
2018-06-13 20:30 | 953 | 949
2018-06-13 21:00 | 921 | 920
2018-06-13 21:30 | 869 | 868
2018-06-13 22:00 | 831 | 830
2018-06-13 22:30 | 807 | 804
2018-06-13 23:00 | 800 | 796
2018-06-13 23:30 | 755 | 747
2018-06-14 | 704 | 692
2018-06-14 00:30 | 657 | 641
2018-06-14 01:00 | 628 | 612
2018-06-14 01:30 | 607 | 588
2018-06-14 02:00 | 595 | 574
2018-06-14 02:30 | 590 | 568
2018-06-14 03:00 | 583 | 560
2018-06-14 03:30 | 585 | 561
2018-06-14 04:00 | 590 | 567
2018-06-14 04:30 | 602 | 580
2018-06-14 05:00 | 621 | 603
2018-06-14 05:30 | 654 | 641
2018-06-14 06:00 | 696 | 689
2018-06-14 06:30 | 774 | 771
2018-06-14 07:00 | 850 | 849
2018-06-14 07:30 | 899 | 899
2018-06-14 08:00 | 883 | 883
2018-06-14 08:30 | 852 | 852
2018-06-14 09:00 | 825 | 825
2018-06-14 09:30 | 790 | 790
2018-06-14 10:00 | 777 | 777
2018-06-14 10:30 | 781 | 781
2018-06-14 11:00 | 773 | 773
2018-06-14 11:30 | 750 | 749
2018-06-14 12:00 | 743 | 742
2018-06-14 12:30 | 745 | 745
2018-06-14 13:00 | 728 | 728
2018-06-14 13:30 | 739 | 739
2018-06-14 14:00 | 770 | 770
2018-06-14 14:30 | 793 | 793
2018-06-14 15:00 | 798 | 798
2018-06-14 15:30 | 821 | 821
2018-06-14 16:00 | 851 | 849
2018-06-14 16:30 | 884 | 881
2018-06-14 17:00 | 919 | 917
2018-06-14 17:30 | 973 | 969
2018-06-14 18:00 | 990 | 982
2018-06-14 18:30 | 985 | 974
2018-06-14 19:00 | 983 | 973
2018-06-14 19:30 | 958 | 956
2018-06-14 20:00 | 950 | 947
2018-06-14 20:30 | 941 | 936
2018-06-14 21:00 | 902 | 896
2018-06-14 21:30 | 851 | 850
2018-06-14 22:00 | 815 | 814
2018-06-14 22:30 | 790 | 787
2018-06-14 23:00 | 783 | 778
2018-06-14 23:30 | 740 | 732
2018-06-15 | 697 | 684
2018-06-15 00:30 | 653 | 634
2018-06-15 01:00 | 630 | 606
2018-06-15 01:30 | 616 | 587
2018-06-15 02:00 | 596 | 563
2018-06-15 02:30 | 596 | 563
2018-06-15 03:00 | 594 | 559
2018-06-15 03:30 | 596 | 561
2018-06-15 04:00 | 597 | 561
2018-06-15 04:30 | 608 | 574
2018-06-15 05:00 | 628 | 598
2018-06-15 05:30 | 657 | 636
2018-06-15 06:00 | 701 | 689
2018-06-15 06:30 | 781 | 774
2018-06-15 07:00 | 854 | 849
2018-06-15 07:30 | 925 | 923
2018-06-15 08:00 | 924 | 917
2018-06-15 08:30 | 888 | 880
2018-06-15 09:00 | 839 | 832
2018-06-15 09:30 | 792 | 788
2018-06-15 10:00 | 748 | 746
2018-06-15 10:30 | 716 | 716
2018-06-15 11:00 | 701 | 701
2018-06-15 11:30 | 683 | 682
2018-06-15 12:00 | 678 | 677
2018-06-15 12:30 | 668 | 667
2018-06-15 13:00 | 667 | 666
2018-06-15 13:30 | 676 | 675
2018-06-15 14:00 | 692 | 691
2018-06-15 14:30 | 718 | 718
2018-06-15 15:00 | 740 | 739
2018-06-15 15:30 | 766 | 766
2018-06-15 16:00 | 805 | 805
2018-06-15 16:30 | 840 | 840
2018-06-15 17:00 | 885 | 885
2018-06-15 17:30 | 938 | 938
2018-06-15 18:00 | 958 | 957
2018-06-15 18:30 | 945 | 945
2018-06-15 19:00 | 947 | 947
2018-06-15 19:30 | 932 | 932
2018-06-15 20:00 | 929 | 928
2018-06-15 20:30 | 925 | 924
2018-06-15 21:00 | 888 | 888
2018-06-15 21:30 | 849 | 848
2018-06-15 22:00 | 828 | 826
2018-06-15 22:30 | 814 | 810
2018-06-15 23:00 | 815 | 811
2018-06-15 23:30 | 772 | 764
2018-06-16 | 724 | 711
2018-06-16 00:30 | 676 | 655
2018-06-16 01:00 | 642 | 617
2018-06-16 01:30 | 624 | 594
2018-06-16 02:00 | 609 | 574
2018-06-16 02:30 | 603 | 566
2018-06-16 03:00 | 605 | 566
2018-06-16 03:30 | 601 | 560
2018-06-16 04:00 | 589 | 559
2018-06-16 04:30 | 594 | 566
2018-06-16 05:00 | 602 | 575
2018-06-16 05:30 | 591 | 567
2018-06-16 06:00 | 612 | 593
2018-06-16 06:30 | 649 | 638
2018-06-16 07:00 | 629 | 620
2018-06-16 07:30 | 736 | 730
2018-06-16 08:00 | 748 | 744
2018-06-16 08:30 | 758 | 755
2018-06-16 09:00 | 738 | 734
2018-06-16 09:30 | 712 | 708
2018-06-16 10:00 | 675 | 670
2018-06-16 10:30 | 644 | 640
2018-06-16 11:00 | 611 | 606
2018-06-16 11:30 | 588 | 582
2018-06-16 12:00 | 574 | 566
2018-06-16 12:30 | 567 | 557
2018-06-16 13:00 | 560 | 550
2018-06-16 13:30 | 573 | 563
2018-06-16 14:00 | 584 | 575
2018-06-16 14:30 | 603 | 595
2018-06-16 15:00 | 630 | 624
2018-06-16 15:30 | 648 | 643
2018-06-16 16:00 | 682 | 679
2018-06-16 16:30 | 732 | 731
2018-06-16 17:00 | 787 | 786
2018-06-16 17:30 | 854 | 854
2018-06-16 18:00 | 887 | 883
2018-06-16 18:30 | 889 | 884
2018-06-16 19:00 | 886 | 880
2018-06-16 19:30 | 878 | 872
2018-06-16 20:00 | 863 | 859
2018-06-16 20:30 | 847 | 846
2018-06-16 21:00 | 824 | 824
2018-06-16 21:30 | 797 | 796
2018-06-16 22:00 | 782 | 781
2018-06-16 22:30 | 775 | 773
2018-06-16 23:00 | 782 | 779
2018-06-16 23:30 | 749 | 745
2018-06-17 | 707 | 700
2018-06-17 00:30 | 662 | 650
2018-06-17 01:00 | 637 | 622
2018-06-17 01:30 | 621 | 601
2018-06-17 02:00 | 605 | 582
2018-06-17 02:30 | 590 | 564
2018-06-17 03:00 | 586 | 558
2018-06-17 03:30 | 586 | 558
2018-06-17 04:00 | 582 | 551
2018-06-17 04:30 | 585 | 552
2018-06-17 05:00 | 594 | 562
2018-06-17 05:30 | 599 | 570
2018-06-17 06:00 | 613 | 589
2018-06-17 06:30 | 646 | 627
2018-06-17 07:00 | 665 | 647
2018-06-17 07:30 | 707 | 696
2018-06-17 08:00 | 715 | 706
2018-06-17 08:30 | 719 | 714
2018-06-17 09:00 | 716 | 711
2018-06-17 09:30 | 698 | 693
2018-06-17 10:00 | 672 | 666
2018-06-17 10:30 | 646 | 638
2018-06-17 11:00 | 629 | 621
2018-06-17 11:30 | 601 | 590
2018-06-17 12:00 | 587 | 576
2018-06-17 12:30 | 579 | 567
2018-06-17 13:00 | 582 | 569
2018-06-17 13:30 | 591 | 578
2018-06-17 14:00 | 606 | 593
2018-06-17 14:30 | 621 | 609
2018-06-17 15:00 | 644 | 634
2018-06-17 15:30 | 676 | 668
2018-06-17 16:00 | 719 | 714
2018-06-17 16:30 | 770 | 767
2018-06-17 17:00 | 833 | 832
2018-06-17 17:30 | 918 | 916
2018-06-17 18:00 | 968 | 962
2018-06-17 18:30 | 972 | 966
2018-06-17 19:00 | 970 | 964
2018-06-17 19:30 | 959 | 954
2018-06-17 20:00 | 944 | 938
2018-06-17 20:30 | 931 | 929
2018-06-17 21:00 | 890 | 888
2018-06-17 21:30 | 853 | 853
2018-06-17 22:00 | 822 | 822
2018-06-17 22:30 | 796 | 794
2018-06-17 23:00 | 791 | 788
2018-06-17 23:30 | 754 | 748
2018-06-18 | 702 | 694
2018-06-18 00:30 | 662 | 648
2018-06-18 01:00 | 638 | 620
2018-06-18 01:30 | 619 | 598
2018-06-18 02:00 | 608 | 583
2018-06-18 02:30 | 599 | 574
2018-06-18 03:00 | 590 | 564
2018-06-18 03:30 | 595 | 567
2018-06-18 04:00 | 595 | 567
2018-06-18 04:30 | 612 | 588
2018-06-18 05:00 | 635 | 617
2018-06-18 05:30 | 679 | 670
2018-06-18 06:00 | 740 | 735
2018-06-18 06:30 | 841 | 837
2018-06-18 07:00 | 956 | 954
2018-06-18 07:30 | 1019 | 1018
2018-06-18 08:00 | 1010 | 1009
2018-06-18 08:30 | 958 | 957
2018-06-18 09:00 | 901 | 896
2018-06-18 09:30 | 849 | 841
2018-06-18 10:00 | 803 | 800
2018-06-18 10:30 | 764 | 761
2018-06-18 11:00 | 731 | 730
2018-06-18 11:30 | 713 | 713
2018-06-18 12:00 | 710 | 709
2018-06-18 12:30 | 691 | 690
2018-06-18 13:00 | 694 | 694
2018-06-18 13:30 | 695 | 695
2018-06-18 14:00 | 714 | 714
2018-06-18 14:30 | 738 | 738
2018-06-18 15:00 | 754 | 754
2018-06-18 15:30 | 788 | 788
2018-06-18 16:00 | 839 | 838
2018-06-18 16:30 | 910 | 909
2018-06-18 17:00 | 1016 | 1013
2018-06-18 17:30 | 1125 | 1123
2018-06-18 18:00 | 1178 | 1177
2018-06-18 18:30 | 1176 | 1173
2018-06-18 19:00 | 1175 | 1172
2018-06-18 19:30 | 1158 | 1153
2018-06-18 20:00 | 1140 | 1135
2018-06-18 20:30 | 1129 | 1124
2018-06-18 21:00 | 1064 | 1060
2018-06-18 21:30 | 1008 | 1001
2018-06-18 22:00 | 957 | 949
2018-06-18 22:30 | 889 | 887
2018-06-18 23:00 | 856 | 855
2018-06-18 23:30 | 809 | 807
2018-06-19 | 756 | 751
2018-06-19 00:30 | 710 | 701
2018-06-19 01:00 | 674 | 662
2018-06-19 01:30 | 649 | 633
2018-06-19 02:00 | 632 | 613
2018-06-19 02:30 | 625 | 607
2018-06-19 03:00 | 624 | 605
2018-06-19 03:30 | 620 | 602
2018-06-19 04:00 | 627 | 609
2018-06-19 04:30 | 646 | 630
2018-06-19 05:00 | 676 | 665
2018-06-19 05:30 | 724 | 719
2018-06-19 06:00 | 791 | 784
2018-06-19 06:30 | 904 | 902
2018-06-19 07:00 | 1022 | 1020
2018-06-19 07:30 | 1075 | 1073
2018-06-19 08:00 | 1060 | 1054
2018-06-19 08:30 | 1000 | 990
2018-06-19 09:00 | 925 | 911
2018-06-19 09:30 | 863 | 858
2018-06-19 10:00 | 815 | 810
2018-06-19 10:30 | 774 | 772
2018-06-19 11:00 | 754 | 750
2018-06-19 11:30 | 729 | 724
2018-06-19 12:00 | 721 | 715
2018-06-19 12:30 | 714 | 709
2018-06-19 13:00 | 726 | 721
2018-06-19 13:30 | 734 | 729
2018-06-19 14:00 | 744 | 740
2018-06-19 14:30 | 764 | 760
2018-06-19 15:00 | 776 | 773
2018-06-19 15:30 | 804 | 801
2018-06-19 16:00 | 843 | 842
2018-06-19 16:30 | 901 | 900
2018-06-19 17:00 | 976 | 976
2018-06-19 17:30 | 1083 | 1082
2018-06-19 18:00 | 1138 | 1137
2018-06-19 18:30 | 1143 | 1141
2018-06-19 19:00 | 1152 | 1150
2018-06-19 19:30 | 1132 | 1129
2018-06-19 20:00 | 1115 | 1114
2018-06-19 20:30 | 1105 | 1103
2018-06-19 21:00 | 1049 | 1047
2018-06-19 21:30 | 996 | 993
2018-06-19 22:00 | 949 | 945
2018-06-19 22:30 | 917 | 914
2018-06-19 23:00 | 899 | 895
2018-06-19 23:30 | 846 | 843
2018-06-20 | 778 | 772
2018-06-20 00:30 | 723 | 715
2018-06-20 01:00 | 693 | 682
2018-06-20 01:30 | 666 | 653
2018-06-20 02:00 | 653 | 637
2018-06-20 02:30 | 643 | 626
2018-06-20 03:00 | 643 | 622
2018-06-20 03:30 | 644 | 623
2018-06-20 04:00 | 647 | 627
2018-06-20 04:30 | 668 | 651
2018-06-20 05:00 | 690 | 678
2018-06-20 05:30 | 726 | 720
2018-06-20 06:00 | 783 | 781
2018-06-20 06:30 | 889 | 889
2018-06-20 07:00 | 999 | 999
2018-06-20 07:30 | 1088 | 1087
2018-06-20 08:00 | 1082 | 1080
2018-06-20 08:30 | 1025 | 1020
2018-06-20 09:00 | 951 | 945
2018-06-20 09:30 | 890 | 888
2018-06-20 10:00 | 833 | 830
2018-06-20 10:30 | 794 | 792
2018-06-20 11:00 | 763 | 762
2018-06-20 11:30 | 747 | 747
2018-06-20 12:00 | 750 | 750
2018-06-20 12:30 | 744 | 744
2018-06-20 13:00 | 740 | 740
2018-06-20 13:30 | 767 | 767
2018-06-20 14:00 | 783 | 782
2018-06-20 14:30 | 799 | 798
2018-06-20 15:00 | 801 | 800
2018-06-20 15:30 | 821 | 821
2018-06-20 16:00 | 867 | 867
2018-06-20 16:30 | 906 | 906
2018-06-20 17:00 | 982 | 982
2018-06-20 17:30 | 1061 | 1060
2018-06-20 18:00 | 1115 | 1112
2018-06-20 18:30 | 1118 | 1112
2018-06-20 19:00 | 1127 | 1120
2018-06-20 19:30 | 1099 | 1092
2018-06-20 20:00 | 1080 | 1074
2018-06-20 20:30 | 1056 | 1051
2018-06-20 21:00 | 1014 | 1005
2018-06-20 21:30 | 953 | 942
2018-06-20 22:00 | 909 | 894
2018-06-20 22:30 | 865 | 863
2018-06-20 23:00 | 851 | 848
2018-06-20 23:30 | 804 | 798
2018-06-21 | 752 | 743
2018-06-21 00:30 | 704 | 694
2018-06-21 01:00 | 676 | 662
2018-06-21 01:30 | 650 | 634
2018-06-21 02:00 | 636 | 618
2018-06-21 02:30 | 628 | 608
2018-06-21 03:00 | 620 | 599
2018-06-21 03:30 | 622 | 601
2018-06-21 04:00 | 620 | 599
2018-06-21 04:30 | 634 | 616
2018-06-21 05:00 | 652 | 638
2018-06-21 05:30 | 702 | 696
2018-06-21 06:00 | 759 | 757
2018-06-21 06:30 | 862 | 861
2018-06-21 07:00 | 953 | 953
2018-06-21 07:30 | 1025 | 1025
2018-06-21 08:00 | 1015 | 1015
2018-06-21 08:30 | 1007 | 1007
2018-06-21 09:00 | 963 | 963
2018-06-21 09:30 | 909 | 909
2018-06-21 10:00 | 835 | 834
2018-06-21 10:30 | 808 | 807
2018-06-21 11:00 | 810 | 810
2018-06-21 11:30 | 790 | 790
2018-06-21 12:00 | 783 | 783
2018-06-21 12:30 | 779 | 779
2018-06-21 13:00 | 788 | 787
2018-06-21 13:30 | 791 | 790
2018-06-21 14:00 | 828 | 827
2018-06-21 14:30 | 835 | 835
2018-06-21 15:00 | 849 | 849
2018-06-21 15:30 | 881 | 881
2018-06-21 16:00 | 878 | 878
2018-06-21 16:30 | 923 | 923
2018-06-21 17:00 | 981 | 981
2018-06-21 17:30 | 1073 | 1069
2018-06-21 18:00 | 1152 | 1150
2018-06-21 18:30 | 1164 | 1163
2018-06-21 19:00 | 1133 | 1132
2018-06-21 19:30 | 1106 | 1106
2018-06-21 20:00 | 1073 | 1073
2018-06-21 20:30 | 1084 | 1084
2018-06-21 21:00 | 1029 | 1027
2018-06-21 21:30 | 954 | 945
2018-06-21 22:00 | 901 | 892
2018-06-21 22:30 | 878 | 872
2018-06-21 23:00 | 862 | 857
2018-06-21 23:30 | 814 | 813
2018-06-22 | 758 | 755
2018-06-22 00:30 | 709 | 704
2018-06-22 01:00 | 676 | 668
2018-06-22 01:30 | 656 | 645
2018-06-22 02:00 | 637 | 623
2018-06-22 02:30 | 626 | 613
2018-06-22 03:00 | 619 | 604
2018-06-22 03:30 | 620 | 604
2018-06-22 04:00 | 623 | 607
2018-06-22 04:30 | 639 | 624
2018-06-22 05:00 | 658 | 647
2018-06-22 05:30 | 697 | 691
2018-06-22 06:00 | 769 | 768
2018-06-22 06:30 | 872 | 872
2018-06-22 07:00 | 962 | 962
2018-06-22 07:30 | 1035 | 1035
2018-06-22 08:00 | 1032 | 1032
2018-06-22 08:30 | 996 | 994
2018-06-22 09:00 | 902 | 895
2018-06-22 09:30 | 843 | 839
2018-06-22 10:00 | 800 | 796
2018-06-22 10:30 | 777 | 774
2018-06-22 11:00 | 731 | 727
2018-06-22 11:30 | 714 | 713
2018-06-22 12:00 | 700 | 700
2018-06-22 12:30 | 690 | 690
2018-06-22 13:00 | 697 | 697
2018-06-22 13:30 | 703 | 703
2018-06-22 14:00 | 724 | 724
2018-06-22 14:30 | 739 | 738
2018-06-22 15:00 | 748 | 747
2018-06-22 15:30 | 770 | 769
2018-06-22 16:00 | 807 | 807
2018-06-22 16:30 | 864 | 864
2018-06-22 17:00 | 920 | 920
2018-06-22 17:30 | 979 | 978
2018-06-22 18:00 | 997 | 996
2018-06-22 18:30 | 1003 | 1002
2018-06-22 19:00 | 1034 | 1034
2018-06-22 19:30 | 1032 | 1031
2018-06-22 20:00 | 1000 | 997
2018-06-22 20:30 | 985 | 984
2018-06-22 21:00 | 943 | 943
2018-06-22 21:30 | 939 | 939
2018-06-22 22:00 | 884 | 884
2018-06-22 22:30 | 841 | 841
2018-06-22 23:00 | 827 | 827
2018-06-22 23:30 | 778 | 776
2018-06-23 | 727 | 723
2018-06-23 00:30 | 675 | 669
2018-06-23 01:00 | 644 | 633
2018-06-23 01:30 | 622 | 607
2018-06-23 02:00 | 601 | 585
2018-06-23 02:30 | 598 | 580
2018-06-23 03:00 | 589 | 568
2018-06-23 03:30 | 591 | 570
2018-06-23 04:00 | 591 | 568
2018-06-23 04:30 | 594 | 571
2018-06-23 05:00 | 609 | 587
2018-06-23 05:30 | 623 | 605
2018-06-23 06:00 | 645 | 630
2018-06-23 06:30 | 676 | 668
2018-06-23 07:00 | 719 | 713
2018-06-23 07:30 | 764 | 762
2018-06-23 08:00 | 784 | 783
2018-06-23 08:30 | 789 | 788
2018-06-23 09:00 | 777 | 775
2018-06-23 09:30 | 805 | 805
2018-06-23 10:00 | 771 | 770
2018-06-23 10:30 | 740 | 738
2018-06-23 11:00 | 689 | 688
2018-06-23 11:30 | 654 | 652
2018-06-23 12:00 | 624 | 619
2018-06-23 12:30 | 612 | 607
2018-06-23 13:00 | 612 | 605
2018-06-23 13:30 | 616 | 609
2018-06-23 14:00 | 628 | 620
2018-06-23 14:30 | 642 | 635
2018-06-23 15:00 | 656 | 650
2018-06-23 15:30 | 677 | 672
2018-06-23 16:00 | 728 | 725
2018-06-23 16:30 | 718 | 716
2018-06-23 17:00 | 810 | 810
2018-06-23 17:30 | 862 | 862
2018-06-23 18:00 | 899 | 897
2018-06-23 18:30 | 900 | 897
2018-06-23 19:00 | 898 | 894
2018-06-23 19:30 | 890 | 886
2018-06-23 20:00 | 884 | 883
2018-06-23 20:30 | 880 | 879
2018-06-23 21:00 | 857 | 855
2018-06-23 21:30 | 828 | 827
2018-06-23 22:00 | 806 | 806
2018-06-23 22:30 | 796 | 795
2018-06-23 23:00 | 798 | 797
2018-06-23 23:30 | 768 | 766
2018-06-24 | 716 | 711
2018-06-24 00:30 | 676 | 666
2018-06-24 01:00 | 655 | 641
2018-06-24 01:30 | 628 | 610
2018-06-24 02:00 | 607 | 586
2018-06-24 02:30 | 597 | 573
2018-06-24 03:00 | 591 | 565
2018-06-24 03:30 | 585 | 560
2018-06-24 04:00 | 582 | 557
2018-06-24 04:30 | 590 | 565
2018-06-24 05:00 | 599 | 574
2018-06-24 05:30 | 611 | 588
2018-06-24 06:00 | 623 | 602
2018-06-24 06:30 | 643 | 627
2018-06-24 07:00 | 676 | 662
2018-06-24 07:30 | 710 | 701
2018-06-24 08:00 | 728 | 722
2018-06-24 08:30 | 732 | 729
2018-06-24 09:00 | 726 | 723
2018-06-24 09:30 | 709 | 706
2018-06-24 10:00 | 681 | 677
2018-06-24 10:30 | 659 | 654
2018-06-24 11:00 | 635 | 629
2018-06-24 11:30 | 614 | 606
2018-06-24 12:00 | 605 | 596
2018-06-24 12:30 | 605 | 595
2018-06-24 13:00 | 602 | 592
2018-06-24 13:30 | 607 | 597
2018-06-24 14:00 | 615 | 607
2018-06-24 14:30 | 643 | 635
2018-06-24 15:00 | 667 | 661
2018-06-24 15:30 | 692 | 688
2018-06-24 16:00 | 730 | 727
2018-06-24 16:30 | 775 | 773
2018-06-24 17:00 | 841 | 841
2018-06-24 17:30 | 911 | 911
2018-06-24 18:00 | 956 | 955
2018-06-24 18:30 | 963 | 962
2018-06-24 19:00 | 961 | 960
2018-06-24 19:30 | 952 | 950
2018-06-24 20:00 | 943 | 940
2018-06-24 20:30 | 939 | 936
2018-06-24 21:00 | 901 | 900
2018-06-24 21:30 | 873 | 872
2018-06-24 22:00 | 838 | 836
2018-06-24 22:30 | 816 | 815
2018-06-24 23:00 | 807 | 805
2018-06-24 23:30 | 765 | 761
2018-06-25 | 711 | 704
2018-06-25 00:30 | 667 | 654
2018-06-25 01:00 | 645 | 628
2018-06-25 01:30 | 630 | 609
2018-06-25 02:00 | 610 | 587
2018-06-25 02:30 | 599 | 574
2018-06-25 03:00 | 595 | 570
2018-06-25 03:30 | 592 | 568
2018-06-25 04:00 | 599 | 575
2018-06-25 04:30 | 616 | 595
2018-06-25 05:00 | 630 | 613
2018-06-25 05:30 | 675 | 665
2018-06-25 06:00 | 730 | 725
2018-06-25 06:30 | 822 | 821
2018-06-25 07:00 | 907 | 906
2018-06-25 07:30 | 963 | 963
2018-06-25 08:00 | 1007 | 1006
2018-06-25 08:30 | 990 | 990
2018-06-25 09:00 | 953 | 952
2018-06-25 09:30 | 918 | 915
2018-06-25 10:00 | 879 | 874
2018-06-25 10:30 | 843 | 841
2018-06-25 11:00 | 792 | 790
2018-06-25 11:30 | 751 | 751
2018-06-25 12:00 | 736 | 735
2018-06-25 12:30 | 746 | 744
2018-06-25 13:00 | 770 | 769
2018-06-25 13:30 | 775 | 773
2018-06-25 14:00 | 778 | 776
2018-06-25 14:30 | 793 | 790
2018-06-25 15:00 | 803 | 800
2018-06-25 15:30 | 818 | 816
2018-06-25 16:00 | 849 | 847
2018-06-25 16:30 | 894 | 894
2018-06-25 17:00 | 963 | 963
2018-06-25 17:30 | 1039 | 1039
2018-06-25 18:00 | 1080 | 1080
2018-06-25 18:30 | 1067 | 1066
2018-06-25 19:00 | 1053 | 1053
2018-06-25 19:30 | 1030 | 1027
2018-06-25 20:00 | 1013 | 1009
2018-06-25 20:30 | 1000 | 997
2018-06-25 21:00 | 951 | 947
2018-06-25 21:30 | 904 | 897
2018-06-25 22:00 | 862 | 856
2018-06-25 22:30 | 866 | 864
2018-06-25 23:00 | 816 | 809
2018-06-25 23:30 | 768 | 756
2018-06-26 | 723 | 703
2018-06-26 00:30 | 680 | 655
2018-06-26 01:00 | 640 | 625
2018-06-26 01:30 | 615 | 598
2018-06-26 02:00 | 601 | 581
2018-06-26 02:30 | 594 | 573
2018-06-26 03:00 | 590 | 568
2018-06-26 03:30 | 597 | 574
2018-06-26 04:00 | 596 | 572
2018-06-26 04:30 | 607 | 587
2018-06-26 05:00 | 627 | 611
2018-06-26 05:30 | 665 | 655
2018-06-26 06:00 | 715 | 711
2018-06-26 06:30 | 800 | 793
2018-06-26 07:00 | 879 | 877
2018-06-26 07:30 | 925 | 924
2018-06-26 08:00 | 908 | 907
2018-06-26 08:30 | 874 | 873
2018-06-26 09:00 | 847 | 845
2018-06-26 09:30 | 810 | 806
2018-06-26 10:00 | 767 | 766
2018-06-26 10:30 | 753 | 752
2018-06-26 11:00 | 737 | 736
2018-06-26 11:30 | 721 | 721
2018-06-26 12:00 | 725 | 725
2018-06-26 12:30 | 724 | 724
2018-06-26 13:00 | 732 | 731
2018-06-26 13:30 | 760 | 759
2018-06-26 14:00 | 755 | 755
2018-06-26 14:30 | 776 | 776
2018-06-26 15:00 | 791 | 791
2018-06-26 15:30 | 823 | 823
2018-06-26 16:00 | 849 | 849
2018-06-26 16:30 | 892 | 892
2018-06-26 17:00 | 955 | 955
2018-06-26 17:30 | 1023 | 1022
2018-06-26 18:00 | 1037 | 1034
2018-06-26 18:30 | 1027 | 1022
2018-06-26 19:00 | 1026 | 1020
2018-06-26 19:30 | 1002 | 994
2018-06-26 20:00 | 983 | 976
2018-06-26 20:30 | 971 | 966
2018-06-26 21:00 | 933 | 925
2018-06-26 21:30 | 882 | 875
2018-06-26 22:00 | 830 | 828
2018-06-26 22:30 | 798 | 796
2018-06-26 23:00 | 801 | 798
2018-06-26 23:30 | 757 | 752
2018-06-27 | 710 | 700
2018-06-27 00:30 | 669 | 654
2018-06-27 01:00 | 639 | 618
2018-06-27 01:30 | 619 | 593
2018-06-27 02:00 | 603 | 577
2018-06-27 02:30 | 588 | 564
2018-06-27 03:00 | 580 | 555
2018-06-27 03:30 | 578 | 553
2018-06-27 04:00 | 582 | 558
2018-06-27 04:30 | 594 | 574
2018-06-27 05:00 | 615 | 599
2018-06-27 05:30 | 654 | 644
2018-06-27 06:00 | 698 | 693
2018-06-27 06:30 | 774 | 771
2018-06-27 07:00 | 849 | 843
2018-06-27 07:30 | 915 | 912
2018-06-27 08:00 | 929 | 927
2018-06-27 08:30 | 918 | 915
2018-06-27 09:00 | 900 | 897
2018-06-27 09:30 | 866 | 861
2018-06-27 10:00 | 865 | 860
2018-06-27 10:30 | 886 | 881
2018-06-27 11:00 | 890 | 886
2018-06-27 11:30 | 886 | 882
2018-06-27 12:00 | 879 | 875
2018-06-27 12:30 | 874 | 869
2018-06-27 13:00 | 877 | 873
2018-06-27 13:30 | 875 | 871
2018-06-27 14:00 | 868 | 863
2018-06-27 14:30 | 885 | 877
2018-06-27 15:00 | 885 | 875
2018-06-27 15:30 | 905 | 897
2018-06-27 16:00 | 938 | 933
2018-06-27 16:30 | 972 | 969
2018-06-27 17:00 | 1013 | 1010
2018-06-27 17:30 | 1085 | 1077
2018-06-27 18:00 | 1084 | 1077
2018-06-27 18:30 | 1069 | 1061
2018-06-27 19:00 | 1071 | 1063
2018-06-27 19:30 | 1054 | 1044
2018-06-27 20:00 | 1027 | 1024
2018-06-27 20:30 | 1007 | 1004
2018-06-27 21:00 | 958 | 954
2018-06-27 21:30 | 898 | 895
2018-06-27 22:00 | 871 | 865
2018-06-27 22:30 | 821 | 818
2018-06-27 23:00 | 814 | 811
2018-06-27 23:30 | 784 | 777
2018-06-28 | 727 | 715
2018-06-28 00:30 | 684 | 666
2018-06-28 01:00 | 648 | 632
2018-06-28 01:30 | 617 | 602
2018-06-28 02:00 | 600 | 582
2018-06-28 02:30 | 587 | 567
2018-06-28 03:00 | 578 | 556
2018-06-28 03:30 | 579 | 557
2018-06-28 04:00 | 581 | 560
2018-06-28 04:30 | 599 | 581
2018-06-28 05:00 | 625 | 611
2018-06-28 05:30 | 673 | 665
2018-06-28 06:00 | 729 | 724
2018-06-28 06:30 | 806 | 800
2018-06-28 07:00 | 872 | 866
2018-06-28 07:30 | 930 | 928
2018-06-28 08:00 | 931 | 929
2018-06-28 08:30 | 916 | 911
2018-06-28 09:00 | 887 | 881
2018-06-28 09:30 | 847 | 839
2018-06-28 10:00 | 842 | 833
2018-06-28 10:30 | 823 | 816
2018-06-28 11:00 | 803 | 796
2018-06-28 11:30 | 778 | 772
2018-06-28 12:00 | 798 | 792
2018-06-28 12:30 | 802 | 796
2018-06-28 13:00 | 780 | 774
2018-06-28 13:30 | 755 | 746
2018-06-28 14:00 | 771 | 763
2018-06-28 14:30 | 773 | 764
2018-06-28 15:00 | 774 | 766
2018-06-28 15:30 | 822 | 816
2018-06-28 16:00 | 863 | 859
2018-06-28 16:30 | 887 | 883
2018-06-28 17:00 | 970 | 967
2018-06-28 17:30 | 1018 | 1014
2018-06-28 18:00 | 1068 | 1065
2018-06-28 18:30 | 1074 | 1066
2018-06-28 19:00 | 1045 | 1037
2018-06-28 19:30 | 1023 | 1018
2018-06-28 20:00 | 1007 | 1003
2018-06-28 20:30 | 1001 | 998
2018-06-28 21:00 | 964 | 961
2018-06-28 21:30 | 910 | 906
2018-06-28 22:00 | 863 | 863
2018-06-28 22:30 | 838 | 837
2018-06-28 23:00 | 834 | 833
2018-06-28 23:30 | 784 | 783
2018-06-29 | 734 | 731
2018-06-29 00:30 | 679 | 671
2018-06-29 01:00 | 652 | 641
2018-06-29 01:30 | 632 | 619
2018-06-29 02:00 | 616 | 599
2018-06-29 02:30 | 611 | 593
2018-06-29 03:00 | 606 | 585
2018-06-29 03:30 | 605 | 584
2018-06-29 04:00 | 609 | 589
2018-06-29 04:30 | 623 | 605
2018-06-29 05:00 | 637 | 623
2018-06-29 05:30 | 681 | 671
2018-06-29 06:00 | 715 | 711
2018-06-29 06:30 | 783 | 780
2018-06-29 07:00 | 869 | 865
2018-06-29 07:30 | 937 | 933
2018-06-29 08:00 | 948 | 945
2018-06-29 08:30 | 921 | 919
2018-06-29 09:00 | 882 | 878
2018-06-29 09:30 | 857 | 853
2018-06-29 10:00 | 818 | 815
2018-06-29 10:30 | 782 | 779
2018-06-29 11:00 | 744 | 742
2018-06-29 11:30 | 720 | 717
2018-06-29 12:00 | 700 | 700
2018-06-29 12:30 | 697 | 697
2018-06-29 13:00 | 704 | 704
2018-06-29 13:30 | 710 | 710
2018-06-29 14:00 | 717 | 717
2018-06-29 14:30 | 737 | 736
2018-06-29 15:00 | 750 | 749
2018-06-29 15:30 | 773 | 772
2018-06-29 16:00 | 808 | 807
2018-06-29 16:30 | 844 | 843
2018-06-29 17:00 | 893 | 893
2018-06-29 17:30 | 946 | 945
2018-06-29 18:00 | 969 | 962
2018-06-29 18:30 | 960 | 949
2018-06-29 19:00 | 955 | 943
2018-06-29 19:30 | 934 | 922
2018-06-29 20:00 | 919 | 917
2018-06-29 20:30 | 910 | 908
2018-06-29 21:00 | 878 | 878
2018-06-29 21:30 | 844 | 844
2018-06-29 22:00 | 816 | 815
2018-06-29 22:30 | 797 | 796
2018-06-29 23:00 | 791 | 790
2018-06-29 23:30 | 753 | 751
2018-06-30 | 707 | 701
2018-06-30 00:30 | 660 | 648
2018-06-30 01:00 | 639 | 624
2018-06-30 01:30 | 621 | 602
2018-06-30 02:00 | 603 | 579
2018-06-30 02:30 | 594 | 566
2018-06-30 03:00 | 590 | 561
2018-06-30 03:30 | 588 | 559
2018-06-30 04:00 | 582 | 553
2018-06-30 04:30 | 584 | 555
2018-06-30 05:00 | 595 | 567
2018-06-30 05:30 | 610 | 587
2018-06-30 06:00 | 625 | 606
2018-06-30 06:30 | 655 | 640
2018-06-30 07:00 | 674 | 661
2018-06-30 07:30 | 709 | 702
2018-06-30 08:00 | 724 | 722
2018-06-30 08:30 | 749 | 748
2018-06-30 09:00 | 762 | 762
2018-06-30 09:30 | 765 | 765
2018-06-30 10:00 | 750 | 750
2018-06-30 10:30 | 728 | 727
2018-06-30 11:00 | 700 | 699
2018-06-30 11:30 | 670 | 667
2018-06-30 12:00 | 660 | 656
2018-06-30 12:30 | 637 | 633
2018-06-30 13:00 | 635 | 630
2018-06-30 13:30 | 638 | 632
2018-06-30 14:00 | 663 | 658
2018-06-30 14:30 | 667 | 662
2018-06-30 15:00 | 685 | 680
2018-06-30 15:30 | 708 | 704
2018-06-30 16:00 | 727 | 724
2018-06-30 16:30 | 756 | 754
2018-06-30 17:00 | 803 | 802
2018-06-30 17:30 | 854 | 853
2018-06-30 18:00 | 871 | 868
2018-06-30 18:30 | 865 | 860
2018-06-30 19:00 | 859 | 853
2018-06-30 19:30 | 841 | 833
2018-06-30 20:00 | 826 | 823
2018-06-30 20:30 | 822 | 820
2018-06-30 21:00 | 791 | 791
2018-06-30 21:30 | 774 | 773
2018-06-30 22:00 | 766 | 765
2018-06-30 22:30 | 748 | 747
2018-06-30 23:00 | 759 | 757
2018-06-30 23:30 | 715 | 711
2018-07-01 | 676 | 668
2018-07-01 00:30 | 628 | 615
2018-07-01 01:00 | 610 | 592
2018-07-01 01:30 | 590 | 569
2018-07-01 02:00 | 588 | 563
2018-07-01 02:30 | 572 | 545
2018-07-01 03:00 | 568 | 538
2018-07-01 03:30 | 564 | 534
2018-07-01 04:00 | 568 | 537
2018-07-01 04:30 | 568 | 537
2018-07-01 05:00 | 573 | 542
2018-07-01 05:30 | 579 | 551
2018-07-01 06:00 | 587 | 561
2018-07-01 06:30 | 606 | 586
2018-07-01 07:00 | 623 | 604
2018-07-01 07:30 | 655 | 639
2018-07-01 08:00 | 674 | 664
2018-07-01 08:30 | 697 | 691
2018-07-01 09:00 | 713 | 710
2018-07-01 09:30 | 725 | 723
2018-07-01 10:00 | 721 | 719
2018-07-01 10:30 | 730 | 729
2018-07-01 11:00 | 717 | 715
2018-07-01 11:30 | 709 | 705
2018-07-01 12:00 | 720 | 716
2018-07-01 12:30 | 724 | 721
2018-07-01 13:00 | 703 | 699
2018-07-01 13:30 | 707 | 703
2018-07-01 14:00 | 723 | 719
2018-07-01 14:30 | 738 | 735
2018-07-01 15:00 | 747 | 744
2018-07-01 15:30 | 757 | 755
2018-07-01 16:00 | 765 | 763
2018-07-01 16:30 | 789 | 788
2018-07-01 17:00 | 828 | 827
2018-07-01 17:30 | 883 | 881
2018-07-01 18:00 | 911 | 906
2018-07-01 18:30 | 907 | 901
2018-07-01 19:00 | 900 | 891
2018-07-01 19:30 | 876 | 865
2018-07-01 20:00 | 851 | 849
2018-07-01 20:30 | 846 | 844
2018-07-01 21:00 | 814 | 813
2018-07-01 21:30 | 776 | 775
2018-07-01 22:00 | 762 | 760
2018-07-01 22:30 | 749 | 745
2018-07-01 23:00 | 748 | 744
2018-07-01 23:30 | 712 | 705
2018-07-02 | 673 | 660
2018-07-02 00:30 | 634 | 614
2018-07-02 01:00 | 612 | 588
2018-07-02 01:30 | 592 | 565
2018-07-02 02:00 | 583 | 554
2018-07-02 02:30 | 577 | 545
2018-07-02 03:00 | 573 | 540
2018-07-02 03:30 | 571 | 538
2018-07-02 04:00 | 572 | 540
2018-07-02 04:30 | 585 | 556
2018-07-02 05:00 | 605 | 580
2018-07-02 05:30 | 642 | 623
2018-07-02 06:00 | 670 | 659
2018-07-02 06:30 | 733 | 729
2018-07-02 07:00 | 789 | 783
2018-07-02 07:30 | 849 | 846
2018-07-02 08:00 | 870 | 867
2018-07-02 08:30 | 889 | 886
2018-07-02 09:00 | 864 | 848
2018-07-02 09:30 | 825 | 808
2018-07-02 10:00 | 788 | 777
2018-07-02 10:30 | 753 | 749
2018-07-02 11:00 | 731 | 728
2018-07-02 11:30 | 733 | 730
2018-07-02 12:00 | 733 | 731
2018-07-02 12:30 | 738 | 735
2018-07-02 13:00 | 752 | 749
2018-07-02 13:30 | 761 | 758
2018-07-02 14:00 | 771 | 769
2018-07-02 14:30 | 790 | 788
2018-07-02 15:00 | 784 | 782
2018-07-02 15:30 | 797 | 795
2018-07-02 16:00 | 838 | 837
2018-07-02 16:30 | 881 | 880
2018-07-02 17:00 | 931 | 930
2018-07-02 17:30 | 987 | 986
2018-07-02 18:00 | 1005 | 1002
2018-07-02 18:30 | 991 | 986
2018-07-02 19:00 | 982 | 975
2018-07-02 19:30 | 949 | 942
2018-07-02 20:00 | 926 | 925
2018-07-02 20:30 | 918 | 917
2018-07-02 21:00 | 876 | 876
2018-07-02 21:30 | 834 | 832
2018-07-02 22:00 | 794 | 789
2018-07-02 22:30 | 767 | 763
2018-07-02 23:00 | 762 | 757
2018-07-02 23:30 | 729 | 723
2018-07-03 | 684 | 676
2018-07-03 00:30 | 637 | 623
2018-07-03 01:00 | 618 | 600
2018-07-03 01:30 | 597 | 575
2018-07-03 02:00 | 585 | 559
2018-07-03 02:30 | 583 | 556
2018-07-03 03:00 | 576 | 548
2018-07-03 03:30 | 581 | 552
2018-07-03 04:00 | 581 | 554
2018-07-03 04:30 | 592 | 568
2018-07-03 05:00 | 608 | 588
2018-07-03 05:30 | 637 | 624
2018-07-03 06:00 | 672 | 664
2018-07-03 06:30 | 730 | 728
2018-07-03 07:00 | 792 | 792
2018-07-03 07:30 | 835 | 835
2018-07-03 08:00 | 842 | 842
2018-07-03 08:30 | 826 | 826
2018-07-03 09:00 | 797 | 797
2018-07-03 09:30 | 764 | 763
2018-07-03 10:00 | 737 | 736
2018-07-03 10:30 | 708 | 707
2018-07-03 11:00 | 694 | 692
2018-07-03 11:30 | 677 | 675
2018-07-03 12:00 | 674 | 672
2018-07-03 12:30 | 690 | 688
2018-07-03 13:00 | 700 | 697
2018-07-03 13:30 | 715 | 713
2018-07-03 14:00 | 736 | 735
2018-07-03 14:30 | 742 | 740
2018-07-03 15:00 | 749 | 748
2018-07-03 15:30 | 771 | 769
2018-07-03 16:00 | 795 | 794
2018-07-03 16:30 | 829 | 828
2018-07-03 17:00 | 871 | 871
2018-07-03 17:30 | 929 | 929
2018-07-03 18:00 | 975 | 974
2018-07-03 18:30 | 970 | 967
2018-07-03 19:00 | 972 | 968
2018-07-03 19:30 | 946 | 940
2018-07-03 20:00 | 933 | 930
2018-07-03 20:30 | 914 | 912
2018-07-03 21:00 | 874 | 873
2018-07-03 21:30 | 838 | 836
2018-07-03 22:00 | 806 | 801
2018-07-03 22:30 | 788 | 782
2018-07-03 23:00 | 780 | 775
2018-07-03 23:30 | 736 | 728
2018-07-04 | 689 | 679
2018-07-04 00:30 | 647 | 632
2018-07-04 01:00 | 621 | 601
2018-07-04 01:30 | 598 | 575
2018-07-04 02:00 | 583 | 559
2018-07-04 02:30 | 574 | 547
2018-07-04 03:00 | 565 | 537
2018-07-04 03:30 | 568 | 539
2018-07-04 04:00 | 568 | 541
2018-07-04 04:30 | 579 | 553
2018-07-04 05:00 | 595 | 573
2018-07-04 05:30 | 629 | 614
2018-07-04 06:00 | 666 | 658
2018-07-04 06:30 | 720 | 716
2018-07-04 07:00 | 768 | 767
2018-07-04 07:30 | 829 | 828
2018-07-04 08:00 | 839 | 836
2018-07-04 08:30 | 841 | 839
2018-07-04 09:00 | 815 | 813
2018-07-04 09:30 | 787 | 783
2018-07-04 10:00 | 755 | 752
2018-07-04 10:30 | 748 | 747
2018-07-04 11:00 | 733 | 732
2018-07-04 11:30 | 719 | 717
2018-07-04 12:00 | 704 | 701
2018-07-04 12:30 | 687 | 684
2018-07-04 13:00 | 681 | 681
2018-07-04 13:30 | 687 | 687
2018-07-04 14:00 | 709 | 709
2018-07-04 14:30 | 744 | 743
2018-07-04 15:00 | 778 | 778
2018-07-04 15:30 | 816 | 816
2018-07-04 16:00 | 842 | 842
2018-07-04 16:30 | 872 | 872
2018-07-04 17:00 | 870 | 870
2018-07-04 17:30 | 905 | 905
2018-07-04 18:00 | 939 | 938
2018-07-04 18:30 | 931 | 929
2018-07-04 19:00 | 933 | 930
2018-07-04 19:30 | 913 | 908
2018-07-04 20:00 | 894 | 893
2018-07-04 20:30 | 859 | 857
2018-07-04 21:00 | 799 | 798
2018-07-04 21:30 | 819 | 817
2018-07-04 22:00 | 794 | 790
2018-07-04 22:30 | 776 | 769
2018-07-04 23:00 | 761 | 758
2018-07-04 23:30 | 722 | 716
2018-07-05 | 679 | 669
2018-07-05 00:30 | 602 | 585
2018-07-05 01:00 | 610 | 590
2018-07-05 01:30 | 593 | 568
2018-07-05 02:00 | 582 | 555
2018-07-05 02:30 | 569 | 541
2018-07-05 03:00 | 569 | 539
2018-07-05 03:30 | 571 | 542
2018-07-05 04:00 | 550 | 521
2018-07-05 04:30 | 582 | 558
2018-07-05 05:00 | 593 | 572
2018-07-05 05:30 | 627 | 613
2018-07-05 06:00 | 663 | 654
2018-07-05 06:30 | 711 | 708
2018-07-05 07:00 | 759 | 756
2018-07-05 07:30 | 814 | 812
2018-07-05 08:00 | 831 | 829
2018-07-05 08:30 | 829 | 827
2018-07-05 09:00 | 810 | 808
2018-07-05 09:30 | 806 | 805
2018-07-05 10:00 | 820 | 819
2018-07-05 10:30 | 810 | 809
2018-07-05 11:00 | 798 | 798
2018-07-05 11:30 | 786 | 785
2018-07-05 12:00 | 790 | 789
2018-07-05 12:30 | 789 | 788
2018-07-05 13:00 | 797 | 796
2018-07-05 13:30 | 791 | 790
2018-07-05 14:00 | 808 | 807
2018-07-05 14:30 | 820 | 820
2018-07-05 15:00 | 828 | 827
2018-07-05 15:30 | 827 | 826
2018-07-05 16:00 | 838 | 837
2018-07-05 16:30 | 859 | 858
2018-07-05 17:00 | 894 | 893
2018-07-05 17:30 | 937 | 935
2018-07-05 18:00 | 957 | 956
2018-07-05 18:30 | 948 | 945
2018-07-05 19:00 | 952 | 949
2018-07-05 19:30 | 929 | 926
2018-07-05 20:00 | 902 | 900
2018-07-05 20:30 | 883 | 883
2018-07-05 21:00 | 863 | 863
2018-07-05 21:30 | 820 | 820
2018-07-05 22:00 | 794 | 793
2018-07-05 22:30 | 773 | 770
2018-07-05 23:00 | 766 | 762
2018-07-05 23:30 | 725 | 720
2018-07-06 | 684 | 674
2018-07-06 00:30 | 643 | 627
2018-07-06 01:00 | 614 | 595
2018-07-06 01:30 | 595 | 573
2018-07-06 02:00 | 582 | 556
2018-07-06 02:30 | 574 | 549
2018-07-06 03:00 | 573 | 548
2018-07-06 03:30 | 563 | 537
2018-07-06 04:00 | 575 | 549
2018-07-06 04:30 | 584 | 561
2018-07-06 05:00 | 598 | 578
2018-07-06 05:30 | 615 | 601
2018-07-06 06:00 | 654 | 645
2018-07-06 06:30 | 706 | 702
2018-07-06 07:00 | 746 | 744
2018-07-06 07:30 | 795 | 795
2018-07-06 08:00 | 813 | 813
2018-07-06 08:30 | 823 | 822
2018-07-06 09:00 | 808 | 808
2018-07-06 09:30 | 796 | 796
2018-07-06 10:00 | 809 | 809
2018-07-06 10:30 | 813 | 813
2018-07-06 11:00 | 817 | 817
2018-07-06 11:30 | 801 | 800
2018-07-06 12:00 | 809 | 809
2018-07-06 12:30 | 798 | 798
2018-07-06 13:00 | 779 | 778
2018-07-06 13:30 | 776 | 776
2018-07-06 14:00 | 793 | 793
2018-07-06 14:30 | 796 | 796
2018-07-06 15:00 | 794 | 794
2018-07-06 15:30 | 819 | 819
2018-07-06 16:00 | 833 | 833
2018-07-06 16:30 | 857 | 857
2018-07-06 17:00 | 886 | 886
2018-07-06 17:30 | 912 | 912
2018-07-06 18:00 | 926 | 926
2018-07-06 18:30 | 918 | 916
2018-07-06 19:00 | 916 | 913
2018-07-06 19:30 | 895 | 891
2018-07-06 20:00 | 890 | 884
2018-07-06 20:30 | 874 | 870
2018-07-06 21:00 | 840 | 837
2018-07-06 21:30 | 806 | 805
2018-07-06 22:00 | 786 | 785
2018-07-06 22:30 | 777 | 775
2018-07-06 23:00 | 778 | 776
2018-07-06 23:30 | 742 | 738
2018-07-07 | 694 | 685
2018-07-07 00:30 | 644 | 629
2018-07-07 01:00 | 620 | 602
2018-07-07 01:30 | 599 | 578
2018-07-07 02:00 | 593 | 568
2018-07-07 02:30 | 580 | 553
2018-07-07 03:00 | 583 | 555
2018-07-07 03:30 | 564 | 533
2018-07-07 04:00 | 570 | 540
2018-07-07 04:30 | 572 | 543
2018-07-07 05:00 | 578 | 550
2018-07-07 05:30 | 588 | 562
2018-07-07 06:00 | 587 | 566
2018-07-07 06:30 | 626 | 609
2018-07-07 07:00 | 647 | 631
2018-07-07 07:30 | 675 | 663
2018-07-07 08:00 | 700 | 693
2018-07-07 08:30 | 724 | 720
2018-07-07 09:00 | 747 | 746
2018-07-07 09:30 | 760 | 759
2018-07-07 10:00 | 759 | 758
2018-07-07 10:30 | 763 | 762
2018-07-07 11:00 | 721 | 720
2018-07-07 11:30 | 707 | 706
2018-07-07 12:00 | 692 | 691
2018-07-07 12:30 | 720 | 719
2018-07-07 13:00 | 734 | 732
2018-07-07 13:30 | 739 | 738
2018-07-07 14:00 | 712 | 710
2018-07-07 14:30 | 704 | 701
2018-07-07 15:00 | 695 | 692
2018-07-07 15:30 | 704 | 701
2018-07-07 16:00 | 721 | 719
2018-07-07 16:30 | 741 | 739
2018-07-07 17:00 | 777 | 776
2018-07-07 17:30 | 808 | 808
2018-07-07 18:00 | 832 | 832
2018-07-07 18:30 | 828 | 828
2018-07-07 19:00 | 823 | 823
2018-07-07 19:30 | 798 | 798
2018-07-07 20:00 | 788 | 787
2018-07-07 20:30 | 789 | 788
2018-07-07 21:00 | 764 | 761
2018-07-07 21:30 | 744 | 741
2018-07-07 22:00 | 738 | 734
2018-07-07 22:30 | 734 | 729
2018-07-07 23:00 | 742 | 736
2018-07-07 23:30 | 719 | 710
2018-07-08 | 677 | 664
2018-07-08 00:30 | 637 | 617
2018-07-08 01:00 | 614 | 588
2018-07-08 01:30 | 598 | 569
2018-07-08 02:00 | 586 | 553
2018-07-08 02:30 | 575 | 539
2018-07-08 03:00 | 572 | 533
2018-07-08 03:30 | 572 | 533
2018-07-08 04:00 | 567 | 528
2018-07-08 04:30 | 567 | 529
2018-07-08 05:00 | 561 | 523
2018-07-08 05:30 | 572 | 537
2018-07-08 06:00 | 589 | 559
2018-07-08 06:30 | 613 | 587
2018-07-08 07:00 | 635 | 611
2018-07-08 07:30 | 661 | 639
2018-07-08 08:00 | 670 | 655
2018-07-08 08:30 | 675 | 663
2018-07-08 09:00 | 673 | 663
2018-07-08 09:30 | 661 | 651
2018-07-08 10:00 | 627 | 615
2018-07-08 10:30 | 588 | 574
2018-07-08 11:00 | 550 | 532
2018-07-08 11:30 | 535 | 517
2018-07-08 12:00 | 572 | 557
2018-07-08 12:30 | 564 | 548
2018-07-08 13:00 | 564 | 548
2018-07-08 13:30 | 568 | 552
2018-07-08 14:00 | 582 | 568
2018-07-08 14:30 | 599 | 585
2018-07-08 15:00 | 626 | 615
2018-07-08 15:30 | 662 | 652
2018-07-08 16:00 | 697 | 690
2018-07-08 16:30 | 743 | 738
2018-07-08 17:00 | 800 | 799
2018-07-08 17:30 | 857 | 856
2018-07-08 18:00 | 912 | 911
2018-07-08 18:30 | 935 | 932
2018-07-08 19:00 | 936 | 933
2018-07-08 19:30 | 925 | 921
2018-07-08 20:00 | 920 | 915
2018-07-08 20:30 | 903 | 899
2018-07-08 21:00 | 864 | 864
2018-07-08 21:30 | 834 | 833
2018-07-08 22:00 | 805 | 803
2018-07-08 22:30 | 786 | 783
2018-07-08 23:00 | 781 | 777
2018-07-08 23:30 | 749 | 742
2018-07-09 | 704 | 691
2018-07-09 00:30 | 662 | 644
2018-07-09 01:00 | 638 | 615
2018-07-09 01:30 | 619 | 593
2018-07-09 02:00 | 605 | 576
2018-07-09 02:30 | 597 | 566
2018-07-09 03:00 | 592 | 561
2018-07-09 03:30 | 595 | 563
2018-07-09 04:00 | 599 | 569
2018-07-09 04:30 | 621 | 596
2018-07-09 05:00 | 638 | 616
2018-07-09 05:30 | 680 | 668
2018-07-09 06:00 | 723 | 717
2018-07-09 06:30 | 806 | 801
2018-07-09 07:00 | 876 | 875
2018-07-09 07:30 | 927 | 927
2018-07-09 08:00 | 928 | 928
2018-07-09 08:30 | 914 | 914
2018-07-09 09:00 | 876 | 876
2018-07-09 09:30 | 833 | 833
2018-07-09 10:00 | 788 | 787
2018-07-09 10:30 | 744 | 742
2018-07-09 11:00 | 694 | 692
2018-07-09 11:30 | 662 | 660
2018-07-09 12:00 | 669 | 668
2018-07-09 12:30 | 663 | 662
2018-07-09 13:00 | 648 | 647
2018-07-09 13:30 | 648 | 648
2018-07-09 14:00 | 668 | 668
2018-07-09 14:30 | 724 | 724
2018-07-09 15:00 | 751 | 751
2018-07-09 15:30 | 789 | 789
2018-07-09 16:00 | 820 | 820
2018-07-09 16:30 | 856 | 855
2018-07-09 17:00 | 906 | 905
2018-07-09 17:30 | 980 | 980
2018-07-09 18:00 | 1044 | 1043
2018-07-09 18:30 | 1049 | 1047
2018-07-09 19:00 | 1049 | 1046
2018-07-09 19:30 | 1035 | 1030
2018-07-09 20:00 | 1019 | 1017
2018-07-09 20:30 | 1011 | 1008
2018-07-09 21:00 | 965 | 964
2018-07-09 21:30 | 917 | 915
2018-07-09 22:00 | 875 | 870
2018-07-09 22:30 | 832 | 829
2018-07-09 23:00 | 816 | 812
2018-07-09 23:30 | 772 | 766
2018-07-10 | 729 | 723
2018-07-10 00:30 | 681 | 669
2018-07-10 01:00 | 652 | 636
2018-07-10 01:30 | 623 | 603
2018-07-10 02:00 | 613 | 590
2018-07-10 02:30 | 599 | 572
2018-07-10 03:00 | 595 | 567
2018-07-10 03:30 | 599 | 573
2018-07-10 04:00 | 604 | 579
2018-07-10 04:30 | 620 | 599
2018-07-10 05:00 | 638 | 621
2018-07-10 05:30 | 684 | 674
2018-07-10 06:00 | 735 | 726
2018-07-10 06:30 | 807 | 805
2018-07-10 07:00 | 889 | 887
2018-07-10 07:30 | 939 | 938
2018-07-10 08:00 | 976 | 973
2018-07-10 08:30 | 969 | 962
2018-07-10 09:00 | 937 | 927
2018-07-10 09:30 | 881 | 873
2018-07-10 10:00 | 822 | 820
2018-07-10 10:30 | 778 | 775
2018-07-10 11:00 | 732 | 731
2018-07-10 11:30 | 704 | 704
2018-07-10 12:00 | 696 | 696
2018-07-10 12:30 | 699 | 699
2018-07-10 13:00 | 706 | 706
2018-07-10 13:30 | 707 | 707
2018-07-10 14:00 | 724 | 724
2018-07-10 14:30 | 743 | 742
2018-07-10 15:00 | 765 | 765
2018-07-10 15:30 | 783 | 783
2018-07-10 16:00 | 817 | 817
2018-07-10 16:30 | 863 | 862
2018-07-10 17:00 | 924 | 924
2018-07-10 17:30 | 991 | 989
2018-07-10 18:00 | 1038 | 1037
2018-07-10 18:30 | 1032 | 1032
2018-07-10 19:00 | 1035 | 1035
2018-07-10 19:30 | 1010 | 1010
2018-07-10 20:00 | 1006 | 1006
2018-07-10 20:30 | 1003 | 1003
2018-07-10 21:00 | 963 | 961
2018-07-10 21:30 | 904 | 903
2018-07-10 22:00 | 862 | 859
2018-07-10 22:30 | 831 | 827
2018-07-10 23:00 | 825 | 819
2018-07-10 23:30 | 774 | 770
2018-07-11 | 726 | 720
2018-07-11 00:30 | 674 | 663
2018-07-11 01:00 | 645 | 629
2018-07-11 01:30 | 624 | 606
2018-07-11 02:00 | 610 | 587
2018-07-11 02:30 | 597 | 573
2018-07-11 03:00 | 596 | 570
2018-07-11 03:30 | 593 | 566
2018-07-11 04:00 | 600 | 574
2018-07-11 04:30 | 607 | 585
2018-07-11 05:00 | 632 | 615
2018-07-11 05:30 | 674 | 663
2018-07-11 06:00 | 715 | 709
2018-07-11 06:30 | 806 | 805
2018-07-11 07:00 | 882 | 882
2018-07-11 07:30 | 945 | 944
2018-07-11 08:00 | 954 | 954
2018-07-11 08:30 | 927 | 927
2018-07-11 09:00 | 882 | 882
2018-07-11 09:30 | 843 | 842
2018-07-11 10:00 | 803 | 801
2018-07-11 10:30 | 755 | 752
2018-07-11 11:00 | 734 | 733
2018-07-11 11:30 | 727 | 727
2018-07-11 12:00 | 731 | 731
2018-07-11 12:30 | 745 | 745
2018-07-11 13:00 | 759 | 758
2018-07-11 13:30 | 774 | 774
2018-07-11 14:00 | 785 | 785
2018-07-11 14:30 | 817 | 817
2018-07-11 15:00 | 830 | 830
2018-07-11 15:30 | 839 | 839
2018-07-11 16:00 | 854 | 854
2018-07-11 16:30 | 883 | 883
2018-07-11 17:00 | 933 | 932
2018-07-11 17:30 | 990 | 989
2018-07-11 18:00 | 1027 | 1026
2018-07-11 18:30 | 1026 | 1024
2018-07-11 19:00 | 1038 | 1035
2018-07-11 19:30 | 1017 | 1015
2018-07-11 20:00 | 1008 | 1006
2018-07-11 20:30 | 985 | 982
2018-07-11 21:00 | 937 | 936
2018-07-11 21:30 | 896 | 893
2018-07-11 22:00 | 852 | 850
2018-07-11 22:30 | 833 | 831
2018-07-11 23:00 | 820 | 818
2018-07-11 23:30 | 776 | 770
2018-07-12 | 714 | 709
2018-07-12 00:30 | 664 | 654
2018-07-12 01:00 | 634 | 619
2018-07-12 01:30 | 612 | 593
2018-07-12 02:00 | 593 | 572
2018-07-12 02:30 | 590 | 567
2018-07-12 03:00 | 583 | 559
2018-07-12 03:30 | 583 | 559
2018-07-12 04:00 | 589 | 566
2018-07-12 04:30 | 598 | 576
2018-07-12 05:00 | 615 | 597
2018-07-12 05:30 | 650 | 638
2018-07-12 06:00 | 695 | 686
2018-07-12 06:30 | 771 | 765
2018-07-12 07:00 | 838 | 830
2018-07-12 07:30 | 907 | 899
2018-07-12 08:00 | 930 | 924
2018-07-12 08:30 | 994 | 992
2018-07-12 09:00 | 979 | 976
2018-07-12 09:30 | 974 | 972
2018-07-12 10:00 | 912 | 906
2018-07-12 10:30 | 808 | 801
2018-07-12 11:00 | 760 | 758
2018-07-12 11:30 | 728 | 725
2018-07-12 12:00 | 706 | 705
2018-07-12 12:30 | 706 | 706
2018-07-12 13:00 | 727 | 727
2018-07-12 13:30 | 758 | 757
2018-07-12 14:00 | 769 | 768
2018-07-12 14:30 | 781 | 780
2018-07-12 15:00 | 784 | 784
2018-07-12 15:30 | 799 | 798
2018-07-12 16:00 | 813 | 812
2018-07-12 16:30 | 851 | 851
2018-07-12 17:00 | 896 | 896
2018-07-12 17:30 | 955 | 955
2018-07-12 18:00 | 1017 | 1016
2018-07-12 18:30 | 1041 | 1040
2018-07-12 19:00 | 1017 | 1014
2018-07-12 19:30 | 1001 | 995
2018-07-12 20:00 | 1014 | 1009
2018-07-12 20:30 | 1018 | 1013
2018-07-12 21:00 | 981 | 979
2018-07-12 21:30 | 942 | 938
2018-07-12 22:00 | 866 | 858
2018-07-12 22:30 | 829 | 827
2018-07-12 23:00 | 813 | 811
2018-07-12 23:30 | 778 | 775
2018-07-13 | 751 | 746
2018-07-13 00:30 | 664 | 655
2018-07-13 01:00 | 634 | 621
2018-07-13 01:30 | 613 | 597
2018-07-13 02:00 | 601 | 582
2018-07-13 02:30 | 595 | 573
2018-07-13 03:00 | 586 | 564
2018-07-13 03:30 | 592 | 570
2018-07-13 04:00 | 588 | 566
2018-07-13 04:30 | 600 | 579
2018-07-13 05:00 | 620 | 603
2018-07-13 05:30 | 653 | 642
2018-07-13 06:00 | 705 | 695
2018-07-13 06:30 | 783 | 777
2018-07-13 07:00 | 851 | 849
2018-07-13 07:30 | 905 | 904
2018-07-13 08:00 | 910 | 909
2018-07-13 08:30 | 891 | 890
2018-07-13 09:00 | 875 | 875
2018-07-13 09:30 | 812 | 811
2018-07-13 10:00 | 768 | 765
2018-07-13 10:30 | 723 | 722
2018-07-13 11:00 | 700 | 698
2018-07-13 11:30 | 677 | 677
2018-07-13 12:00 | 664 | 663
2018-07-13 12:30 | 654 | 654
2018-07-13 13:00 | 657 | 657
2018-07-13 13:30 | 661 | 660
2018-07-13 14:00 | 667 | 667
2018-07-13 14:30 | 691 | 691
2018-07-13 15:00 | 710 | 710
2018-07-13 15:30 | 734 | 733
2018-07-13 16:00 | 772 | 772
2018-07-13 16:30 | 819 | 819
2018-07-13 17:00 | 875 | 875
2018-07-13 17:30 | 945 | 940
2018-07-13 18:00 | 987 | 985
2018-07-13 18:30 | 998 | 996
2018-07-13 19:00 | 1006 | 1004
2018-07-13 19:30 | 1001 | 997
2018-07-13 20:00 | 1008 | 1004
2018-07-13 20:30 | 1007 | 1002
2018-07-13 21:00 | 977 | 973
2018-07-13 21:30 | 942 | 940
2018-07-13 22:00 | 915 | 911
2018-07-13 22:30 | 888 | 884
2018-07-13 23:00 | 873 | 871
2018-07-13 23:30 | 822 | 818
2018-07-14 | 768 | 762
2018-07-14 00:30 | 697 | 690
2018-07-14 01:00 | 663 | 654
2018-07-14 01:30 | 641 | 629
2018-07-14 02:00 | 625 | 609
2018-07-14 02:30 | 615 | 595
2018-07-14 03:00 | 608 | 585
2018-07-14 03:30 | 604 | 581
2018-07-14 04:00 | 604 | 581
2018-07-14 04:30 | 608 | 585
2018-07-14 05:00 | 614 | 592
2018-07-14 05:30 | 639 | 621
2018-07-14 06:00 | 661 | 648
2018-07-14 06:30 | 704 | 696
2018-07-14 07:00 | 749 | 744
2018-07-14 07:30 | 803 | 799
2018-07-14 08:00 | 831 | 830
2018-07-14 08:30 | 843 | 843
2018-07-14 09:00 | 834 | 833
2018-07-14 09:30 | 812 | 809
2018-07-14 10:00 | 766 | 760
2018-07-14 10:30 | 704 | 701
2018-07-14 11:00 | 670 | 667
2018-07-14 11:30 | 640 | 635
2018-07-14 12:00 | 604 | 595
2018-07-14 12:30 | 590 | 578
2018-07-14 13:00 | 602 | 591
2018-07-14 13:30 | 608 | 596
2018-07-14 14:00 | 616 | 605
2018-07-14 14:30 | 633 | 624
2018-07-14 15:00 | 650 | 642
2018-07-14 15:30 | 681 | 674
2018-07-14 16:00 | 718 | 712
2018-07-14 16:30 | 765 | 762
2018-07-14 17:00 | 834 | 832
2018-07-14 17:30 | 903 | 902
2018-07-14 18:00 | 964 | 963
2018-07-14 18:30 | 982 | 982
2018-07-14 19:00 | 992 | 992
2018-07-14 19:30 | 984 | 984
2018-07-14 20:00 | 978 | 977
2018-07-14 20:30 | 975 | 974
2018-07-14 21:00 | 953 | 950
2018-07-14 21:30 | 899 | 898
2018-07-14 22:00 | 872 | 870
2018-07-14 22:30 | 846 | 845
2018-07-14 23:00 | 836 | 835
2018-07-14 23:30 | 800 | 798
2018-07-15 | 757 | 752
2018-07-15 00:30 | 702 | 691
2018-07-15 01:00 | 682 | 666
2018-07-15 01:30 | 656 | 636
2018-07-15 02:00 | 635 | 610
2018-07-15 02:30 | 629 | 604
2018-07-15 03:00 | 615 | 591
2018-07-15 03:30 | 610 | 586
2018-07-15 04:00 | 608 | 584
2018-07-15 04:30 | 611 | 588
2018-07-15 05:00 | 618 | 595
2018-07-15 05:30 | 631 | 611
2018-07-15 06:00 | 649 | 633
2018-07-15 06:30 | 673 | 661
2018-07-15 07:00 | 706 | 697
2018-07-15 07:30 | 749 | 745
2018-07-15 08:00 | 780 | 775
2018-07-15 08:30 | 797 | 792
2018-07-15 09:00 | 783 | 778
2018-07-15 09:30 | 760 | 754
2018-07-15 10:00 | 728 | 720
2018-07-15 10:30 | 689 | 678
2018-07-15 11:00 | 644 | 634
2018-07-15 11:30 | 608 | 597
2018-07-15 12:00 | 585 | 576
2018-07-15 12:30 | 571 | 560
2018-07-15 13:00 | 576 | 564
2018-07-15 13:30 | 582 | 570
2018-07-15 14:00 | 593 | 582
2018-07-15 14:30 | 609 | 597
2018-07-15 15:00 | 633 | 623
2018-07-15 15:30 | 665 | 657
2018-07-15 16:00 | 704 | 698
2018-07-15 16:30 | 765 | 763
2018-07-15 17:00 | 836 | 836
2018-07-15 17:30 | 920 | 919
2018-07-15 18:00 | 988 | 987
2018-07-15 18:30 | 1008 | 1007
2018-07-15 19:00 | 1017 | 1017
2018-07-15 19:30 | 1005 | 1004
2018-07-15 20:00 | 997 | 997
2018-07-15 20:30 | 994 | 994
2018-07-15 21:00 | 951 | 950
2018-07-15 21:30 | 912 | 910
2018-07-15 22:00 | 869 | 862
2018-07-15 22:30 | 835 | 825
2018-07-15 23:00 | 808 | 801
2018-07-15 23:30 | 771 | 762
2018-07-16 | 722 | 712
2018-07-16 00:30 | 685 | 667
2018-07-16 01:00 | 652 | 636
2018-07-16 01:30 | 631 | 615
2018-07-16 02:00 | 617 | 598
2018-07-16 02:30 | 606 | 586
2018-07-16 03:00 | 594 | 571
2018-07-16 03:30 | 590 | 567
2018-07-16 04:00 | 601 | 579
2018-07-16 04:30 | 611 | 592
2018-07-16 05:00 | 629 | 615
2018-07-16 05:30 | 678 | 670
2018-07-16 06:00 | 723 | 719
2018-07-16 06:30 | 854 | 851
2018-07-16 07:00 | 956 | 954
2018-07-16 07:30 | 1022 | 1021
2018-07-16 08:00 | 1014 | 1009
2018-07-16 08:30 | 963 | 955
2018-07-16 09:00 | 902 | 890
2018-07-16 09:30 | 836 | 823
2018-07-16 10:00 | 779 | 773
2018-07-16 10:30 | 735 | 731
2018-07-16 11:00 | 711 | 706
2018-07-16 11:30 | 689 | 686
2018-07-16 12:00 | 681 | 678
2018-07-16 12:30 | 669 | 665
2018-07-16 13:00 | 665 | 664
2018-07-16 13:30 | 670 | 670
2018-07-16 14:00 | 684 | 684
2018-07-16 14:30 | 700 | 700
2018-07-16 15:00 | 729 | 729
2018-07-16 15:30 | 759 | 759
2018-07-16 16:00 | 796 | 796
2018-07-16 16:30 | 853 | 853
2018-07-16 17:00 | 928 | 927
2018-07-16 17:30 | 995 | 995
2018-07-16 18:00 | 1055 | 1054
2018-07-16 18:30 | 1064 | 1058
2018-07-16 19:00 | 1079 | 1073
2018-07-16 19:30 | 1067 | 1060
2018-07-16 20:00 | 1056 | 1051
2018-07-16 20:30 | 1044 | 1037
2018-07-16 21:00 | 992 | 991
2018-07-16 21:30 | 940 | 938
2018-07-16 22:00 | 894 | 890
2018-07-16 22:30 | 857 | 851
2018-07-16 23:00 | 825 | 821
2018-07-16 23:30 | 776 | 771
2018-07-17 | 726 | 721
2018-07-17 00:30 | 679 | 669
2018-07-17 01:00 | 652 | 638
2018-07-17 01:30 | 633 | 617
2018-07-17 02:00 | 618 | 599
2018-07-17 02:30 | 608 | 587
2018-07-17 03:00 | 605 | 582
2018-07-17 03:30 | 604 | 581
2018-07-17 04:00 | 607 | 585
2018-07-17 04:30 | 628 | 610
2018-07-17 05:00 | 652 | 639
2018-07-17 05:30 | 708 | 702
2018-07-17 06:00 | 780 | 775
2018-07-17 06:30 | 898 | 893
2018-07-17 07:00 | 1004 | 1000
2018-07-17 07:30 | 1068 | 1066
2018-07-17 08:00 | 1050 | 1048
2018-07-17 08:30 | 991 | 986
2018-07-17 09:00 | 931 | 924
2018-07-17 09:30 | 875 | 869
2018-07-17 10:00 | 815 | 814
2018-07-17 10:30 | 764 | 763
2018-07-17 11:00 | 724 | 724
2018-07-17 11:30 | 701 | 701
2018-07-17 12:00 | 690 | 690
2018-07-17 12:30 | 676 | 675
2018-07-17 13:00 | 677 | 677
2018-07-17 13:30 | 685 | 685
2018-07-17 14:00 | 683 | 682
2018-07-17 14:30 | 703 | 703
2018-07-17 15:00 | 722 | 722
2018-07-17 15:30 | 748 | 748
2018-07-17 16:00 | 790 | 790
2018-07-17 16:30 | 844 | 844
2018-07-17 17:00 | 911 | 910
2018-07-17 17:30 | 978 | 976
2018-07-17 18:00 | 1056 | 1053
2018-07-17 18:30 | 1072 | 1065
2018-07-17 19:00 | 1087 | 1082
2018-07-17 19:30 | 1079 | 1072
2018-07-17 20:00 | 1076 | 1068
2018-07-17 20:30 | 1069 | 1064
2018-07-17 21:00 | 1028 | 1027
2018-07-17 21:30 | 986 | 983
2018-07-17 22:00 | 933 | 927
2018-07-17 22:30 | 883 | 878
2018-07-17 23:00 | 858 | 850
2018-07-17 23:30 | 808 | 797
2018-07-18 | 745 | 739
2018-07-18 00:30 | 693 | 680
2018-07-18 01:00 | 661 | 644
2018-07-18 01:30 | 642 | 623
2018-07-18 02:00 | 631 | 607
2018-07-18 02:30 | 624 | 598
2018-07-18 03:00 | 619 | 590
2018-07-18 03:30 | 626 | 596
2018-07-18 04:00 | 630 | 601
2018-07-18 04:30 | 650 | 624
2018-07-18 05:00 | 670 | 651
2018-07-18 05:30 | 725 | 715
2018-07-18 06:00 | 795 | 788
2018-07-18 06:30 | 913 | 908
2018-07-18 07:00 | 1009 | 1009
2018-07-18 07:30 | 1083 | 1083
2018-07-18 08:00 | 1064 | 1062
2018-07-18 08:30 | 1005 | 999
2018-07-18 09:00 | 924 | 915
2018-07-18 09:30 | 871 | 866
2018-07-18 10:00 | 815 | 810
2018-07-18 10:30 | 767 | 762
2018-07-18 11:00 | 732 | 726
2018-07-18 11:30 | 703 | 700
2018-07-18 12:00 | 692 | 690
2018-07-18 12:30 | 689 | 687
2018-07-18 13:00 | 684 | 684
2018-07-18 13:30 | 680 | 680
2018-07-18 14:00 | 689 | 689
2018-07-18 14:30 | 707 | 707
2018-07-18 15:00 | 738 | 738
2018-07-18 15:30 | 764 | 764
2018-07-18 16:00 | 801 | 800
2018-07-18 16:30 | 846 | 845
2018-07-18 17:00 | 906 | 905
2018-07-18 17:30 | 970 | 967
2018-07-18 18:00 | 1028 | 1027
2018-07-18 18:30 | 1039 | 1036
2018-07-18 19:00 | 1051 | 1049
2018-07-18 19:30 | 1046 | 1044
2018-07-18 20:00 | 1045 | 1042
2018-07-18 20:30 | 1049 | 1046
2018-07-18 21:00 | 1005 | 1004
2018-07-18 21:30 | 955 | 955
2018-07-18 22:00 | 911 | 911
2018-07-18 22:30 | 871 | 870
2018-07-18 23:00 | 855 | 854
2018-07-18 23:30 | 805 | 804
2018-07-19 | 749 | 744
2018-07-19 00:30 | 706 | 697
2018-07-19 01:00 | 675 | 663
2018-07-19 01:30 | 658 | 641
2018-07-19 02:00 | 644 | 625
2018-07-19 02:30 | 631 | 611
2018-07-19 03:00 | 626 | 607
2018-07-19 03:30 | 628 | 609
2018-07-19 04:00 | 630 | 611
2018-07-19 04:30 | 649 | 633
2018-07-19 05:00 | 676 | 664
2018-07-19 05:30 | 729 | 724
2018-07-19 06:00 | 801 | 797
2018-07-19 06:30 | 906 | 904
2018-07-19 07:00 | 1007 | 1005
2018-07-19 07:30 | 1083 | 1080
2018-07-19 08:00 | 1064 | 1058
2018-07-19 08:30 | 997 | 992
2018-07-19 09:00 | 911 | 905
2018-07-19 09:30 | 842 | 840
2018-07-19 10:00 | 780 | 780
2018-07-19 10:30 | 731 | 730
2018-07-19 11:00 | 699 | 699
2018-07-19 11:30 | 686 | 686
2018-07-19 12:00 | 678 | 678
2018-07-19 12:30 | 672 | 672
2018-07-19 13:00 | 678 | 678
2018-07-19 13:30 | 683 | 682
2018-07-19 14:00 | 697 | 697
2018-07-19 14:30 | 715 | 715
2018-07-19 15:00 | 733 | 733
2018-07-19 15:30 | 751 | 751
2018-07-19 16:00 | 790 | 790
2018-07-19 16:30 | 839 | 839
2018-07-19 17:00 | 888 | 887
2018-07-19 17:30 | 958 | 958
2018-07-19 18:00 | 1018 | 1018
2018-07-19 18:30 | 1030 | 1028
2018-07-19 19:00 | 1042 | 1039
2018-07-19 19:30 | 1033 | 1031
2018-07-19 20:00 | 1033 | 1031
2018-07-19 20:30 | 1030 | 1028
2018-07-19 21:00 | 1000 | 994
2018-07-19 21:30 | 957 | 947
2018-07-19 22:00 | 912 | 899
2018-07-19 22:30 | 881 | 865
2018-07-19 23:00 | 848 | 837
2018-07-19 23:30 | 798 | 784
2018-07-20 | 731 | 721
2018-07-20 00:30 | 668 | 661
2018-07-20 01:00 | 642 | 630
2018-07-20 01:30 | 625 | 612
2018-07-20 02:00 | 610 | 593
2018-07-20 02:30 | 605 | 586
2018-07-20 03:00 | 599 | 579
2018-07-20 03:30 | 602 | 581
2018-07-20 04:00 | 602 | 582
2018-07-20 04:30 | 619 | 601
2018-07-20 05:00 | 646 | 633
2018-07-20 05:30 | 698 | 689
2018-07-20 06:00 | 783 | 776
2018-07-20 06:30 | 891 | 884
2018-07-20 07:00 | 950 | 947
2018-07-20 07:30 | 1012 | 1007
2018-07-20 08:00 | 1008 | 1002
2018-07-20 08:30 | 948 | 940
2018-07-20 09:00 | 869 | 864
2018-07-20 09:30 | 813 | 809
2018-07-20 10:00 | 776 | 773
2018-07-20 10:30 | 769 | 766
2018-07-20 11:00 | 719 | 714
2018-07-20 11:30 | 702 | 701
2018-07-20 12:00 | 702 | 702
2018-07-20 12:30 | 743 | 743
2018-07-20 13:00 | 782 | 782
2018-07-20 13:30 | 740 | 740
2018-07-20 14:00 | 768 | 768
2018-07-20 14:30 | 850 | 850
2018-07-20 15:00 | 858 | 858
2018-07-20 15:30 | 818 | 818
2018-07-20 16:00 | 826 | 826
2018-07-20 16:30 | 856 | 856
2018-07-20 17:00 | 889 | 889
2018-07-20 17:30 | 932 | 931
2018-07-20 18:00 | 982 | 977
2018-07-20 18:30 | 978 | 969
2018-07-20 19:00 | 978 | 968
2018-07-20 19:30 | 952 | 949
2018-07-20 20:00 | 943 | 942
2018-07-20 20:30 | 941 | 939
2018-07-20 21:00 | 913 | 909
2018-07-20 21:30 | 882 | 877
2018-07-20 22:00 | 844 | 842
2018-07-20 22:30 | 827 | 825
2018-07-20 23:00 | 821 | 819
2018-07-20 23:30 | 788 | 785
2018-07-21 | 735 | 732
2018-07-21 00:30 | 674 | 667
2018-07-21 01:00 | 645 | 634
2018-07-21 01:30 | 627 | 613
2018-07-21 02:00 | 608 | 590
2018-07-21 02:30 | 603 | 583
2018-07-21 03:00 | 601 | 581
2018-07-21 03:30 | 593 | 571
2018-07-21 04:00 | 596 | 575
2018-07-21 04:30 | 600 | 580
2018-07-21 05:00 | 606 | 586
2018-07-21 05:30 | 621 | 604
2018-07-21 06:00 | 642 | 630
2018-07-21 06:30 | 685 | 677
2018-07-21 07:00 | 723 | 717
2018-07-21 07:30 | 769 | 765
2018-07-21 08:00 | 780 | 778
2018-07-21 08:30 | 779 | 778
2018-07-21 09:00 | 772 | 771
2018-07-21 09:30 | 758 | 757
2018-07-21 10:00 | 726 | 725
2018-07-21 10:30 | 681 | 679
2018-07-21 11:00 | 649 | 647
2018-07-21 11:30 | 618 | 615
2018-07-21 12:00 | 600 | 596
2018-07-21 12:30 | 587 | 581
2018-07-21 13:00 | 584 | 579
2018-07-21 13:30 | 586 | 580
2018-07-21 14:00 | 601 | 595
2018-07-21 14:30 | 615 | 611
2018-07-21 15:00 | 633 | 628
2018-07-21 15:30 | 678 | 675
2018-07-21 16:00 | 706 | 704
2018-07-21 16:30 | 736 | 735
2018-07-21 17:00 | 807 | 807
2018-07-21 17:30 | 897 | 894
2018-07-21 18:00 | 965 | 961
2018-07-21 18:30 | 979 | 977
2018-07-21 19:00 | 984 | 981
2018-07-21 19:30 | 969 | 966
2018-07-21 20:00 | 970 | 968
2018-07-21 20:30 | 966 | 963
2018-07-21 21:00 | 933 | 929
2018-07-21 21:30 | 898 | 896
2018-07-21 22:00 | 880 | 879
2018-07-21 22:30 | 866 | 863
2018-07-21 23:00 | 860 | 857
2018-07-21 23:30 | 820 | 818
2018-07-22 | 767 | 765
2018-07-22 00:30 | 708 | 701
2018-07-22 01:00 | 678 | 667
2018-07-22 01:30 | 655 | 642
2018-07-22 02:00 | 634 | 617
2018-07-22 02:30 | 626 | 608
2018-07-22 03:00 | 611 | 591
2018-07-22 03:30 | 606 | 585
2018-07-22 04:00 | 601 | 580
2018-07-22 04:30 | 602 | 580
2018-07-22 05:00 | 610 | 590
2018-07-22 05:30 | 615 | 597
2018-07-22 06:00 | 634 | 619
2018-07-22 06:30 | 662 | 650
2018-07-22 07:00 | 694 | 685
2018-07-22 07:30 | 732 | 726
2018-07-22 08:00 | 755 | 749
2018-07-22 08:30 | 760 | 756
2018-07-22 09:00 | 756 | 754
2018-07-22 09:30 | 740 | 738
2018-07-22 10:00 | 718 | 714
2018-07-22 10:30 | 673 | 670
2018-07-22 11:00 | 642 | 637
2018-07-22 11:30 | 590 | 582
2018-07-22 12:00 | 584 | 574
2018-07-22 12:30 | 586 | 576
2018-07-22 13:00 | 593 | 584
2018-07-22 13:30 | 587 | 577
2018-07-22 14:00 | 592 | 581
2018-07-22 14:30 | 613 | 605
2018-07-22 15:00 | 650 | 644
2018-07-22 15:30 | 679 | 674
2018-07-22 16:00 | 712 | 707
2018-07-22 16:30 | 765 | 762
2018-07-22 17:00 | 828 | 827
2018-07-22 17:30 | 897 | 896
2018-07-22 18:00 | 976 | 976
2018-07-22 18:30 | 995 | 995
2018-07-22 19:00 | 1007 | 1007
2018-07-22 19:30 | 991 | 991
2018-07-22 20:00 | 981 | 981
2018-07-22 20:30 | 969 | 969
2018-07-22 21:00 | 928 | 927
2018-07-22 21:30 | 887 | 885
2018-07-22 22:00 | 858 | 854
2018-07-22 22:30 | 818 | 816
2018-07-22 23:00 | 803 | 802
2018-07-22 23:30 | 769 | 767
2018-07-23 | 720 | 713
2018-07-23 00:30 | 679 | 667
2018-07-23 01:00 | 639 | 624
2018-07-23 01:30 | 630 | 613
2018-07-23 02:00 | 611 | 592
2018-07-23 02:30 | 607 | 586
2018-07-23 03:00 | 599 | 576
2018-07-23 03:30 | 600 | 577
2018-07-23 04:00 | 602 | 580
2018-07-23 04:30 | 620 | 601
2018-07-23 05:00 | 641 | 626
2018-07-23 05:30 | 695 | 689
2018-07-23 06:00 | 772 | 768
2018-07-23 06:30 | 885 | 883
2018-07-23 07:00 | 975 | 973
2018-07-23 07:30 | 1028 | 1026
2018-07-23 08:00 | 1010 | 1005
2018-07-23 08:30 | 924 | 917
2018-07-23 09:00 | 850 | 839
2018-07-23 09:30 | 781 | 776
2018-07-23 10:00 | 722 | 718
2018-07-23 10:30 | 682 | 677
2018-07-23 11:00 | 647 | 644
2018-07-23 11:30 | 623 | 623
2018-07-23 12:00 | 638 | 638
2018-07-23 12:30 | 645 | 644
2018-07-23 13:00 | 650 | 650
2018-07-23 13:30 | 657 | 656
2018-07-23 14:00 | 667 | 666
2018-07-23 14:30 | 689 | 689
2018-07-23 15:00 | 700 | 700
2018-07-23 15:30 | 721 | 721
2018-07-23 16:00 | 767 | 767
2018-07-23 16:30 | 815 | 815
2018-07-23 17:00 | 865 | 864
2018-07-23 17:30 | 968 | 967
2018-07-23 18:00 | 1055 | 1054
2018-07-23 18:30 | 1067 | 1066
2018-07-23 19:00 | 1070 | 1069
2018-07-23 19:30 | 1055 | 1053
2018-07-23 20:00 | 1040 | 1039
2018-07-23 20:30 | 1032 | 1032
2018-07-23 21:00 | 981 | 980
2018-07-23 21:30 | 926 | 926
2018-07-23 22:00 | 881 | 879
2018-07-23 22:30 | 854 | 850
2018-07-23 23:00 | 823 | 820
2018-07-23 23:30 | 773 | 771
2018-07-24 | 724 | 721
2018-07-24 00:30 | 681 | 674
2018-07-24 01:00 | 648 | 638
2018-07-24 01:30 | 625 | 611
2018-07-24 02:00 | 609 | 593
2018-07-24 02:30 | 600 | 582
2018-07-24 03:00 | 588 | 569
2018-07-24 03:30 | 587 | 569
2018-07-24 04:00 | 593 | 574
2018-07-24 04:30 | 614 | 598
2018-07-24 05:00 | 652 | 641
2018-07-24 05:30 | 718 | 713
2018-07-24 06:00 | 784 | 783
2018-07-24 06:30 | 894 | 894
2018-07-24 07:00 | 997 | 997
2018-07-24 07:30 | 1063 | 1063
2018-07-24 08:00 | 1035 | 1035
2018-07-24 08:30 | 962 | 961
2018-07-24 09:00 | 890 | 888
2018-07-24 09:30 | 824 | 820
2018-07-24 10:00 | 773 | 772
2018-07-24 10:30 | 731 | 731
2018-07-24 11:00 | 698 | 698
2018-07-24 11:30 | 682 | 682
2018-07-24 12:00 | 663 | 663
2018-07-24 12:30 | 657 | 657
2018-07-24 13:00 | 648 | 648
2018-07-24 13:30 | 662 | 662
2018-07-24 14:00 | 681 | 681
2018-07-24 14:30 | 707 | 707
2018-07-24 15:00 | 727 | 727
2018-07-24 15:30 | 747 | 746
2018-07-24 16:00 | 795 | 795
2018-07-24 16:30 | 840 | 840
2018-07-24 17:00 | 896 | 896
2018-07-24 17:30 | 964 | 963
2018-07-24 18:00 | 1027 | 1022
2018-07-24 18:30 | 1041 | 1035
2018-07-24 19:00 | 1044 | 1040
2018-07-24 19:30 | 1014 | 1012
2018-07-24 20:00 | 1011 | 1008
2018-07-24 20:30 | 994 | 992
2018-07-24 21:00 | 944 | 943
2018-07-24 21:30 | 912 | 911
2018-07-24 22:00 | 880 | 878
2018-07-24 22:30 | 849 | 847
2018-07-24 23:00 | 840 | 837
2018-07-24 23:30 | 782 | 779
2018-07-25 | 729 | 723
2018-07-25 00:30 | 686 | 676
2018-07-25 01:00 | 650 | 635
2018-07-25 01:30 | 627 | 609
2018-07-25 02:00 | 612 | 591
2018-07-25 02:30 | 599 | 574
2018-07-25 03:00 | 590 | 565
2018-07-25 03:30 | 593 | 567
2018-07-25 04:00 | 597 | 572
2018-07-25 04:30 | 616 | 594
2018-07-25 05:00 | 641 | 625
2018-07-25 05:30 | 707 | 696
2018-07-25 06:00 | 778 | 769
2018-07-25 06:30 | 865 | 863
2018-07-25 07:00 | 945 | 945
2018-07-25 07:30 | 1013 | 1013
2018-07-25 08:00 | 1018 | 1018
2018-07-25 08:30 | 989 | 989
2018-07-25 09:00 | 959 | 959
2018-07-25 09:30 | 931 | 929
2018-07-25 10:00 | 896 | 894
2018-07-25 10:30 | 852 | 850
2018-07-25 11:00 | 811 | 809
2018-07-25 11:30 | 768 | 763
2018-07-25 12:00 | 760 | 755
2018-07-25 12:30 | 733 | 727
2018-07-25 13:00 | 733 | 726
2018-07-25 13:30 | 740 | 738
2018-07-25 14:00 | 762 | 761
2018-07-25 14:30 | 784 | 782
2018-07-25 15:00 | 803 | 802
2018-07-25 15:30 | 829 | 828
2018-07-25 16:00 | 859 | 858
2018-07-25 16:30 | 874 | 872
2018-07-25 17:00 | 912 | 911
2018-07-25 17:30 | 980 | 978
2018-07-25 18:00 | 1022 | 1019
2018-07-25 18:30 | 1029 | 1022
2018-07-25 19:00 | 1027 | 1023
2018-07-25 19:30 | 998 | 995
2018-07-25 20:00 | 985 | 982
2018-07-25 20:30 | 979 | 977
2018-07-25 21:00 | 929 | 928
2018-07-25 21:30 | 864 | 861
2018-07-25 22:00 | 820 | 819
2018-07-25 22:30 | 797 | 796
2018-07-25 23:00 | 786 | 783
2018-07-25 23:30 | 751 | 745
2018-07-26 | 698 | 691
2018-07-26 00:30 | 648 | 637
2018-07-26 01:00 | 616 | 601
2018-07-26 01:30 | 602 | 583
2018-07-26 02:00 | 582 | 560
2018-07-26 02:30 | 580 | 554
2018-07-26 03:00 | 574 | 549
2018-07-26 03:30 | 570 | 545
2018-07-26 04:00 | 573 | 548
2018-07-26 04:30 | 583 | 559
2018-07-26 05:00 | 602 | 583
2018-07-26 05:30 | 640 | 629
2018-07-26 06:00 | 682 | 677
2018-07-26 06:30 | 772 | 769
2018-07-26 07:00 | 853 | 851
2018-07-26 07:30 | 918 | 918
2018-07-26 08:00 | 913 | 913
2018-07-26 08:30 | 865 | 865
2018-07-26 09:00 | 792 | 792
2018-07-26 09:30 | 747 | 745
2018-07-26 10:00 | 717 | 716
2018-07-26 10:30 | 695 | 693
2018-07-26 11:00 | 689 | 687
2018-07-26 11:30 | 668 | 667
2018-07-26 12:00 | 664 | 663
2018-07-26 12:30 | 660 | 659
2018-07-26 13:00 | 666 | 665
2018-07-26 13:30 | 677 | 676
2018-07-26 14:00 | 688 | 687
2018-07-26 14:30 | 704 | 703
2018-07-26 15:00 | 723 | 722
2018-07-26 15:30 | 744 | 743
2018-07-26 16:00 | 780 | 778
2018-07-26 16:30 | 814 | 812
2018-07-26 17:00 | 860 | 859
2018-07-26 17:30 | 899 | 898
2018-07-26 18:00 | 957 | 956
2018-07-26 18:30 | 978 | 970
2018-07-26 19:00 | 982 | 973
2018-07-26 19:30 | 967 | 955
2018-07-26 20:00 | 948 | 941
2018-07-26 20:30 | 937 | 935
2018-07-26 21:00 | 901 | 898
2018-07-26 21:30 | 862 | 855
2018-07-26 22:00 | 817 | 810
2018-07-26 22:30 | 784 | 781
2018-07-26 23:00 | 779 | 775
2018-07-26 23:30 | 740 | 732
2018-07-27 | 686 | 676
2018-07-27 00:30 | 634 | 621
2018-07-27 01:00 | 613 | 596
2018-07-27 01:30 | 590 | 570
2018-07-27 02:00 | 533 | 508
2018-07-27 02:30 | 489 | 458
2018-07-27 03:00 | 479 | 446
2018-07-27 03:30 | 534 | 505
2018-07-27 04:00 | 577 | 554
2018-07-27 04:30 | 564 | 539
2018-07-27 05:00 | 595 | 575
2018-07-27 05:30 | 637 | 624
2018-07-27 06:00 | 687 | 679
2018-07-27 06:30 | 772 | 767
2018-07-27 07:00 | 844 | 843
2018-07-27 07:30 | 899 | 899
2018-07-27 08:00 | 887 | 886
2018-07-27 08:30 | 836 | 835
2018-07-27 09:00 | 769 | 768
2018-07-27 09:30 | 733 | 731
2018-07-27 10:00 | 708 | 705
2018-07-27 10:30 | 682 | 680
2018-07-27 11:00 | 670 | 669
2018-07-27 11:30 | 662 | 660
2018-07-27 12:00 | 645 | 644
2018-07-27 12:30 | 562 | 561
2018-07-27 13:00 | 625 | 624
2018-07-27 13:30 | 655 | 655
2018-07-27 14:00 | 630 | 629
2018-07-27 14:30 | 677 | 676
2018-07-27 15:00 | 647 | 646
2018-07-27 15:30 | 634 | 633
2018-07-27 16:00 | 757 | 756
2018-07-27 16:30 | 809 | 809
2018-07-27 17:00 | 849 | 847
2018-07-27 17:30 | 875 | 873
2018-07-27 18:00 | 917 | 912
2018-07-27 18:30 | 910 | 899
2018-07-27 19:00 | 912 | 900
2018-07-27 19:30 | 899 | 884
2018-07-27 20:00 | 893 | 876
2018-07-27 20:30 | 874 | 866
2018-07-27 21:00 | 829 | 828
2018-07-27 21:30 | 800 | 798
2018-07-27 22:00 | 778 | 775
2018-07-27 22:30 | 721 | 719
2018-07-27 23:00 | 758 | 756
2018-07-27 23:30 | 721 | 716
2018-07-28 | 672 | 665
2018-07-28 00:30 | 629 | 615
2018-07-28 01:00 | 605 | 588
2018-07-28 01:30 | 583 | 563
2018-07-28 02:00 | 570 | 544
2018-07-28 02:30 | 565 | 535
2018-07-28 03:00 | 562 | 530
2018-07-28 03:30 | 561 | 529
2018-07-28 04:00 | 559 | 524
2018-07-28 04:30 | 562 | 527
2018-07-28 05:00 | 569 | 536
2018-07-28 05:30 | 584 | 556
2018-07-28 06:00 | 598 | 574
2018-07-28 06:30 | 626 | 607
2018-07-28 07:00 | 647 | 629
2018-07-28 07:30 | 693 | 681
2018-07-28 08:00 | 709 | 701
2018-07-28 08:30 | 712 | 706
2018-07-28 09:00 | 707 | 700
2018-07-28 09:30 | 691 | 684
2018-07-28 10:00 | 671 | 664
2018-07-28 10:30 | 650 | 643
2018-07-28 11:00 | 640 | 632
2018-07-28 11:30 | 615 | 605
2018-07-28 12:00 | 608 | 600
2018-07-28 12:30 | 595 | 589
2018-07-28 13:00 | 598 | 591
2018-07-28 13:30 | 595 | 588
2018-07-28 14:00 | 583 | 575
2018-07-28 14:30 | 643 | 637
2018-07-28 15:00 | 661 | 656
2018-07-28 15:30 | 643 | 637
2018-07-28 16:00 | 708 | 703
2018-07-28 16:30 | 747 | 742
2018-07-28 17:00 | 800 | 789
2018-07-28 17:30 | 828 | 820
2018-07-28 18:00 | 854 | 849
2018-07-28 18:30 | 833 | 828
2018-07-28 19:00 | 831 | 826
2018-07-28 19:30 | 812 | 807
2018-07-28 20:00 | 802 | 801
2018-07-28 20:30 | 792 | 791
2018-07-28 21:00 | 754 | 752
2018-07-28 21:30 | 741 | 738
2018-07-28 22:00 | 728 | 723
2018-07-28 22:30 | 683 | 676
2018-07-28 23:00 | 733 | 727
2018-07-28 23:30 | 681 | 672
2018-07-29 | 672 | 659
2018-07-29 00:30 | 628 | 608
2018-07-29 01:00 | 603 | 579
2018-07-29 01:30 | 579 | 550
2018-07-29 02:00 | 571 | 536
2018-07-29 02:30 | 563 | 526
2018-07-29 03:00 | 559 | 521
2018-07-29 03:30 | 546 | 506
2018-07-29 04:00 | 541 | 499
2018-07-29 04:30 | 555 | 514
2018-07-29 05:00 | 559 | 519
2018-07-29 05:30 | 566 | 527
2018-07-29 06:00 | 569 | 534
2018-07-29 06:30 | 596 | 566
2018-07-29 07:00 | 614 | 584
2018-07-29 07:30 | 645 | 621
2018-07-29 08:00 | 656 | 636
2018-07-29 08:30 | 668 | 653
2018-07-29 09:00 | 668 | 656
2018-07-29 09:30 | 655 | 644
2018-07-29 10:00 | 625 | 614
2018-07-29 10:30 | 612 | 601
2018-07-29 11:00 | 592 | 581
2018-07-29 11:30 | 578 | 567
2018-07-29 12:00 | 556 | 544
2018-07-29 12:30 | 494 | 478
2018-07-29 13:00 | 533 | 520
2018-07-29 13:30 | 478 | 462
2018-07-29 14:00 | 570 | 559
2018-07-29 14:30 | 584 | 574
2018-07-29 15:00 | 617 | 609
2018-07-29 15:30 | 665 | 658
2018-07-29 16:00 | 701 | 695
2018-07-29 16:30 | 736 | 731
2018-07-29 17:00 | 769 | 765
2018-07-29 17:30 | 798 | 797
2018-07-29 18:00 | 853 | 852
2018-07-29 18:30 | 854 | 852
2018-07-29 19:00 | 848 | 846
2018-07-29 19:30 | 826 | 822
2018-07-29 20:00 | 818 | 816
2018-07-29 20:30 | 809 | 808
2018-07-29 21:00 | 775 | 772
2018-07-29 21:30 | 752 | 747
2018-07-29 22:00 | 724 | 718
2018-07-29 22:30 | 723 | 715
2018-07-29 23:00 | 723 | 715
2018-07-29 23:30 | 692 | 681
2018-07-30 | 658 | 643
2018-07-30 00:30 | 588 | 563
2018-07-30 01:00 | 583 | 553
2018-07-30 01:30 | 574 | 542
2018-07-30 02:00 | 556 | 519
2018-07-30 02:30 | 552 | 512
2018-07-30 03:00 | 556 | 517
2018-07-30 03:30 | 569 | 531
2018-07-30 04:00 | 571 | 534
2018-07-30 04:30 | 586 | 552
2018-07-30 05:00 | 590 | 560
2018-07-30 05:30 | 626 | 606
2018-07-30 06:00 | 657 | 645
2018-07-30 06:30 | 714 | 708
2018-07-30 07:00 | 787 | 785
2018-07-30 07:30 | 841 | 837
2018-07-30 08:00 | 833 | 830
2018-07-30 08:30 | 806 | 802
2018-07-30 09:00 | 757 | 753
2018-07-30 09:30 | 727 | 721
2018-07-30 10:00 | 701 | 695
2018-07-30 10:30 | 674 | 668
2018-07-30 11:00 | 650 | 646
2018-07-30 11:30 | 642 | 638
2018-07-30 12:00 | 644 | 639
2018-07-30 12:30 | 638 | 633
2018-07-30 13:00 | 604 | 600
2018-07-30 13:30 | 644 | 643
2018-07-30 14:00 | 654 | 653
2018-07-30 14:30 | 674 | 674
2018-07-30 15:00 | 686 | 685
2018-07-30 15:30 | 720 | 719
2018-07-30 16:00 | 758 | 758
2018-07-30 16:30 | 798 | 798
2018-07-30 17:00 | 833 | 833
2018-07-30 17:30 | 888 | 887
2018-07-30 18:00 | 944 | 943
2018-07-30 18:30 | 950 | 949
2018-07-30 19:00 | 951 | 949
2018-07-30 19:30 | 933 | 929
2018-07-30 20:00 | 922 | 915
2018-07-30 20:30 | 902 | 896
2018-07-30 21:00 | 865 | 858
2018-07-30 21:30 | 831 | 823
2018-07-30 22:00 | 794 | 785
2018-07-30 22:30 | 765 | 760
2018-07-30 23:00 | 755 | 752
2018-07-30 23:30 | 720 | 714
2018-07-31 | 673 | 662
2018-07-31 00:30 | 630 | 614
2018-07-31 01:00 | 603 | 581
2018-07-31 01:30 | 585 | 560
2018-07-31 02:00 | 576 | 547
2018-07-31 02:30 | 569 | 536
2018-07-31 03:00 | 567 | 533
2018-07-31 03:30 | 571 | 538
2018-07-31 04:00 | 563 | 531
2018-07-31 04:30 | 583 | 553
2018-07-31 05:00 | 603 | 580
2018-07-31 05:30 | 637 | 622
2018-07-31 06:00 | 706 | 697
2018-07-31 06:30 | 805 | 802
2018-07-31 07:00 | 902 | 902
2018-07-31 07:30 | 956 | 956
2018-07-31 08:00 | 935 | 934
2018-07-31 08:30 | 878 | 875
2018-07-31 09:00 | 817 | 811
2018-07-31 09:30 | 774 | 767
2018-07-31 10:00 | 729 | 724
2018-07-31 10:30 | 687 | 684
2018-07-31 11:00 | 662 | 660
2018-07-31 11:30 | 629 | 626
2018-07-31 12:00 | 590 | 587
2018-07-31 12:30 | 548 | 544
2018-07-31 13:00 | 564 | 560
2018-07-31 13:30 | 559 | 556
2018-07-31 14:00 | 580 | 577
2018-07-31 14:30 | 655 | 653
2018-07-31 15:00 | 703 | 702
2018-07-31 15:30 | 724 | 723
2018-07-31 16:00 | 760 | 759
2018-07-31 16:30 | 802 | 802
2018-07-31 17:00 | 849 | 848
2018-07-31 17:30 | 904 | 902
2018-07-31 18:00 | 967 | 964
2018-07-31 18:30 | 993 | 974
2018-07-31 19:00 | 1000 | 986
2018-07-31 19:30 | 987 | 978
2018-07-31 20:00 | 981 | 970
2018-07-31 20:30 | 977 | 965
2018-07-31 21:00 | 937 | 925
2018-07-31 21:30 | 882 | 868
2018-07-31 22:00 | 842 | 831
2018-07-31 22:30 | 810 | 800
2018-07-31 23:00 | 798 | 787
2018-07-31 23:30 | 747 | 740
2018-08-01 | 702 | 693
2018-08-01 00:30 | 657 | 644
2018-08-01 01:00 | 631 | 613
2018-08-01 01:30 | 606 | 586
2018-08-01 02:00 | 595 | 572
2018-08-01 02:30 | 588 | 562
2018-08-01 03:00 | 582 | 556
2018-08-01 03:30 | 589 | 561
2018-08-01 04:00 | 590 | 564
2018-08-01 04:30 | 606 | 582
2018-08-01 05:00 | 623 | 603
2018-08-01 05:30 | 683 | 671
2018-08-01 06:00 | 742 | 734
2018-08-01 06:30 | 845 | 843
2018-08-01 07:00 | 944 | 944
2018-08-01 07:30 | 1005 | 1005
2018-08-01 08:00 | 981 | 981
2018-08-01 08:30 | 913 | 910
2018-08-01 09:00 | 844 | 837
2018-08-01 09:30 | 800 | 792
2018-08-01 10:00 | 757 | 750
2018-08-01 10:30 | 708 | 704
2018-08-01 11:00 | 671 | 670
2018-08-01 11:30 | 648 | 647
2018-08-01 12:00 | 641 | 641
2018-08-01 12:30 | 637 | 636
2018-08-01 13:00 | 636 | 636
2018-08-01 13:30 | 643 | 642
2018-08-01 14:00 | 670 | 669
2018-08-01 14:30 | 693 | 692
2018-08-01 15:00 | 706 | 705
2018-08-01 15:30 | 720 | 719
2018-08-01 16:00 | 760 | 760
2018-08-01 16:30 | 801 | 801
2018-08-01 17:00 | 844 | 844
2018-08-01 17:30 | 906 | 906
2018-08-01 18:00 | 978 | 977
2018-08-01 18:30 | 991 | 986
2018-08-01 19:00 | 1000 | 996
2018-08-01 19:30 | 990 | 984
2018-08-01 20:00 | 980 | 975
2018-08-01 20:30 | 973 | 967
2018-08-01 21:00 | 938 | 936
2018-08-01 21:30 | 887 | 883
2018-08-01 22:00 | 846 | 840
2018-08-01 22:30 | 819 | 813
2018-08-01 23:00 | 801 | 797
2018-08-01 23:30 | 754 | 751
2018-08-02 | 707 | 703
2018-08-02 00:30 | 656 | 647
2018-08-02 01:00 | 624 | 610
2018-08-02 01:30 | 608 | 591
2018-08-02 02:00 | 594 | 575
2018-08-02 02:30 | 586 | 564
2018-08-02 03:00 | 584 | 560
2018-08-02 03:30 | 586 | 561
2018-08-02 04:00 | 577 | 553
2018-08-02 04:30 | 598 | 576
2018-08-02 05:00 | 617 | 600
2018-08-02 05:30 | 661 | 652
2018-08-02 06:00 | 716 | 711
2018-08-02 06:30 | 817 | 815
2018-08-02 07:00 | 910 | 908
2018-08-02 07:30 | 966 | 965
2018-08-02 08:00 | 949 | 942
2018-08-02 08:30 | 889 | 881
2018-08-02 09:00 | 823 | 817
2018-08-02 09:30 | 770 | 768
2018-08-02 10:00 | 731 | 730
2018-08-02 10:30 | 693 | 693
2018-08-02 11:00 | 673 | 672
2018-08-02 11:30 | 656 | 655
2018-08-02 12:00 | 611 | 610
2018-08-02 12:30 | 644 | 643
2018-08-02 13:00 | 643 | 642
2018-08-02 13:30 | 656 | 655
2018-08-02 14:00 | 666 | 665
2018-08-02 14:30 | 679 | 679
2018-08-02 15:00 | 694 | 693
2018-08-02 15:30 | 721 | 720
2018-08-02 16:00 | 754 | 754
2018-08-02 16:30 | 796 | 795
2018-08-02 17:00 | 845 | 845
2018-08-02 17:30 | 899 | 898
2018-08-02 18:00 | 954 | 952
2018-08-02 18:30 | 968 | 966
2018-08-02 19:00 | 980 | 978
2018-08-02 19:30 | 966 | 963
2018-08-02 20:00 | 960 | 960
2018-08-02 20:30 | 955 | 955
2018-08-02 21:00 | 918 | 918
2018-08-02 21:30 | 870 | 868
2018-08-02 22:00 | 830 | 828
2018-08-02 22:30 | 800 | 799
2018-08-02 23:00 | 789 | 788
2018-08-02 23:30 | 742 | 739
2018-08-03 | 691 | 684
2018-08-03 00:30 | 649 | 638
2018-08-03 01:00 | 616 | 602
2018-08-03 01:30 | 597 | 579
2018-08-03 02:00 | 581 | 561
2018-08-03 02:30 | 570 | 548
2018-08-03 03:00 | 567 | 544
2018-08-03 03:30 | 570 | 547
2018-08-03 04:00 | 575 | 553
2018-08-03 04:30 | 585 | 564
2018-08-03 05:00 | 602 | 585
2018-08-03 05:30 | 638 | 628
2018-08-03 06:00 | 693 | 686
2018-08-03 06:30 | 781 | 777
2018-08-03 07:00 | 864 | 858
2018-08-03 07:30 | 866 | 862
2018-08-03 08:00 | 891 | 888
2018-08-03 08:30 | 853 | 848
2018-08-03 09:00 | 796 | 790
2018-08-03 09:30 | 739 | 737
2018-08-03 10:00 | 705 | 704
2018-08-03 10:30 | 674 | 674
2018-08-03 11:00 | 657 | 657
2018-08-03 11:30 | 651 | 651
2018-08-03 12:00 | 649 | 649
2018-08-03 12:30 | 631 | 631
2018-08-03 13:00 | 637 | 637
2018-08-03 13:30 | 632 | 632
2018-08-03 14:00 | 641 | 640
2018-08-03 14:30 | 654 | 653
2018-08-03 15:00 | 662 | 661
2018-08-03 15:30 | 678 | 678
2018-08-03 16:00 | 716 | 716
2018-08-03 16:30 | 756 | 756
2018-08-03 17:00 | 805 | 805
2018-08-03 17:30 | 845 | 845
2018-08-03 18:00 | 878 | 878
2018-08-03 18:30 | 884 | 882
2018-08-03 19:00 | 897 | 895
2018-08-03 19:30 | 873 | 870
2018-08-03 20:00 | 864 | 860
2018-08-03 20:30 | 844 | 840
2018-08-03 21:00 | 809 | 808
2018-08-03 21:30 | 785 | 784
2018-08-03 22:00 | 758 | 757
2018-08-03 22:30 | 741 | 739
2018-08-03 23:00 | 731 | 728
2018-08-03 23:30 | 688 | 683
2018-08-04 | 650 | 641
2018-08-04 00:30 | 601 | 585
2018-08-04 01:00 | 577 | 558
2018-08-04 01:30 | 554 | 531
2018-08-04 02:00 | 547 | 519
2018-08-04 02:30 | 537 | 507
2018-08-04 03:00 | 534 | 503
2018-08-04 03:30 | 534 | 502
2018-08-04 04:00 | 533 | 501
2018-08-04 04:30 | 524 | 490
2018-08-04 05:00 | 539 | 506
2018-08-04 05:30 | 553 | 525
2018-08-04 06:00 | 565 | 542
2018-08-04 06:30 | 597 | 579
2018-08-04 07:00 | 623 | 607
2018-08-04 07:30 | 647 | 637
2018-08-04 08:00 | 659 | 652
2018-08-04 08:30 | 657 | 652
2018-08-04 09:00 | 646 | 642
2018-08-04 09:30 | 627 | 623
2018-08-04 10:00 | 609 | 604
2018-08-04 10:30 | 582 | 575
2018-08-04 11:00 | 567 | 560
2018-08-04 11:30 | 550 | 543
2018-08-04 12:00 | 540 | 532
2018-08-04 12:30 | 480 | 469
2018-08-04 13:00 | 448 | 436
2018-08-04 13:30 | 536 | 527
2018-08-04 14:00 | 529 | 521
2018-08-04 14:30 | 558 | 551
2018-08-04 15:00 | 557 | 550
2018-08-04 15:30 | 604 | 598
2018-08-04 16:00 | 635 | 630
2018-08-04 16:30 | 669 | 666
2018-08-04 17:00 | 712 | 711
2018-08-04 17:30 | 740 | 737
2018-08-04 18:00 | 769 | 768
2018-08-04 18:30 | 788 | 786
2018-08-04 19:00 | 790 | 788
2018-08-04 19:30 | 772 | 769
2018-08-04 20:00 | 764 | 761
2018-08-04 20:30 | 755 | 753
2018-08-04 21:00 | 724 | 723
2018-08-04 21:30 | 702 | 699
2018-08-04 22:00 | 693 | 688
2018-08-04 22:30 | 691 | 686
2018-08-04 23:00 | 695 | 690
2018-08-04 23:30 | 664 | 656
2018-08-05 | 629 | 617
2018-08-05 00:30 | 590 | 572
2018-08-05 01:00 | 566 | 543
2018-08-05 01:30 | 550 | 524
2018-08-05 02:00 | 540 | 508
2018-08-05 02:30 | 531 | 495
2018-08-05 03:00 | 503 | 461
2018-08-05 03:30 | 448 | 401
2018-08-05 04:00 | 438 | 389
2018-08-05 04:30 | 438 | 390
2018-08-05 05:00 | 442 | 396
2018-08-05 05:30 | 489 | 451
2018-08-05 06:00 | 456 | 422
2018-08-05 06:30 | 548 | 520
2018-08-05 07:00 | 553 | 526
2018-08-05 07:30 | 602 | 581
2018-08-05 08:00 | 626 | 611
2018-08-05 08:30 | 617 | 605
2018-08-05 09:00 | 614 | 603
2018-08-05 09:30 | 597 | 586
2018-08-05 10:00 | 543 | 529
2018-08-05 10:30 | 557 | 544
2018-08-05 11:00 | 499 | 482
2018-08-05 11:30 | 475 | 456
2018-08-05 12:00 | 504 | 487
2018-08-05 12:30 | 493 | 476
2018-08-05 13:00 | 452 | 433
2018-08-05 13:30 | 497 | 479
2018-08-05 14:00 | 498 | 481
2018-08-05 14:30 | 531 | 518
2018-08-05 15:00 | 529 | 517
2018-08-05 15:30 | 518 | 507
2018-08-05 16:00 | 586 | 579
2018-08-05 16:30 | 665 | 660
2018-08-05 17:00 | 710 | 707
2018-08-05 17:30 | 759 | 757
2018-08-05 18:00 | 798 | 796
2018-08-05 18:30 | 822 | 816
2018-08-05 19:00 | 819 | 812
2018-08-05 19:30 | 805 | 796
2018-08-05 20:00 | 790 | 783
2018-08-05 20:30 | 780 | 775
2018-08-05 21:00 | 740 | 738
2018-08-05 21:30 | 713 | 709
2018-08-05 22:00 | 693 | 687
2018-08-05 22:30 | 680 | 673
2018-08-05 23:00 | 679 | 671
2018-08-05 23:30 | 658 | 648
2018-08-06 | 621 | 606
2018-08-06 00:30 | 584 | 563
2018-08-06 01:00 | 567 | 540
2018-08-06 01:30 | 549 | 518
2018-08-06 02:00 | 537 | 503
2018-08-06 02:30 | 533 | 498
2018-08-06 03:00 | 533 | 495
2018-08-06 03:30 | 541 | 505
2018-08-06 04:00 | 536 | 500
2018-08-06 04:30 | 508 | 473
2018-08-06 05:00 | 559 | 532
2018-08-06 05:30 | 595 | 576
2018-08-06 06:00 | 636 | 626
2018-08-06 06:30 | 703 | 698
2018-08-06 07:00 | 766 | 764
2018-08-06 07:30 | 818 | 813
2018-08-06 08:00 | 808 | 802
2018-08-06 08:30 | 773 | 768
2018-08-06 09:00 | 736 | 730
2018-08-06 09:30 | 709 | 703
2018-08-06 10:00 | 680 | 674
2018-08-06 10:30 | 660 | 652
2018-08-06 11:00 | 641 | 638
2018-08-06 11:30 | 624 | 621
2018-08-06 12:00 | 614 | 612
2018-08-06 12:30 | 620 | 618
2018-08-06 13:00 | 625 | 624
2018-08-06 13:30 | 623 | 623
2018-08-06 14:00 | 655 | 655
2018-08-06 14:30 | 673 | 673
2018-08-06 15:00 | 692 | 692
2018-08-06 15:30 | 734 | 734
2018-08-06 16:00 | 777 | 777
2018-08-06 16:30 | 816 | 815
2018-08-06 17:00 | 859 | 858
2018-08-06 17:30 | 908 | 907
2018-08-06 18:00 | 948 | 947
2018-08-06 18:30 | 937 | 934
2018-08-06 19:00 | 935 | 930
2018-08-06 19:30 | 906 | 897
2018-08-06 20:00 | 883 | 880
2018-08-06 20:30 | 866 | 863
2018-08-06 21:00 | 820 | 820
2018-08-06 21:30 | 770 | 770
2018-08-06 22:00 | 734 | 732
2018-08-06 22:30 | 714 | 711
2018-08-06 23:00 | 709 | 704
2018-08-06 23:30 | 670 | 663
2018-08-07 | 627 | 616
2018-08-07 00:30 | 585 | 569
2018-08-07 01:00 | 558 | 537
2018-08-07 01:30 | 540 | 516
2018-08-07 02:00 | 530 | 500
2018-08-07 02:30 | 524 | 491
2018-08-07 03:00 | 507 | 473
2018-08-07 03:30 | 509 | 472
2018-08-07 04:00 | 510 | 476
2018-08-07 04:30 | 522 | 490
2018-08-07 05:00 | 555 | 529
2018-08-07 05:30 | 587 | 571
2018-08-07 06:00 | 623 | 614
2018-08-07 06:30 | 691 | 685
2018-08-07 07:00 | 763 | 760
2018-08-07 07:30 | 812 | 812
2018-08-07 08:00 | 831 | 830
2018-08-07 08:30 | 816 | 814
2018-08-07 09:00 | 769 | 766
2018-08-07 09:30 | 731 | 728
2018-08-07 10:00 | 691 | 687
2018-08-07 10:30 | 636 | 634
2018-08-07 11:00 | 623 | 620
2018-08-07 11:30 | 611 | 610
2018-08-07 12:00 | 613 | 613
2018-08-07 12:30 | 617 | 617
2018-08-07 13:00 | 659 | 659
2018-08-07 13:30 | 667 | 667
2018-08-07 14:00 | 669 | 669
2018-08-07 14:30 | 663 | 662
2018-08-07 15:00 | 664 | 663
2018-08-07 15:30 | 687 | 687
2018-08-07 16:00 | 729 | 728
2018-08-07 16:30 | 756 | 756
2018-08-07 17:00 | 798 | 798
2018-08-07 17:30 | 858 | 856
2018-08-07 18:00 | 920 | 917
2018-08-07 18:30 | 936 | 931
2018-08-07 19:00 | 947 | 942
2018-08-07 19:30 | 931 | 924
2018-08-07 20:00 | 924 | 918
2018-08-07 20:30 | 911 | 908
2018-08-07 21:00 | 874 | 871
2018-08-07 21:30 | 835 | 828
2018-08-07 22:00 | 804 | 793
2018-08-07 22:30 | 779 | 763
2018-08-07 23:00 | 750 | 742
2018-08-07 23:30 | 706 | 698
2018-08-08 | 659 | 652
2018-08-08 00:30 | 611 | 598
2018-08-08 01:00 | 580 | 563
2018-08-08 01:30 | 570 | 547
2018-08-08 02:00 | 557 | 531
2018-08-08 02:30 | 549 | 521
2018-08-08 03:00 | 514 | 481
2018-08-08 03:30 | 549 | 518
2018-08-08 04:00 | 550 | 520
2018-08-08 04:30 | 525 | 497
2018-08-08 05:00 | 530 | 506
2018-08-08 05:30 | 626 | 615
2018-08-08 06:00 | 692 | 686
2018-08-08 06:30 | 782 | 781
2018-08-08 07:00 | 877 | 876
2018-08-08 07:30 | 915 | 914
2018-08-08 08:00 | 897 | 896
2018-08-08 08:30 | 839 | 836
2018-08-08 09:00 | 766 | 762
2018-08-08 09:30 | 715 | 712
2018-08-08 10:00 | 672 | 669
2018-08-08 10:30 | 637 | 636
2018-08-08 11:00 | 611 | 611
2018-08-08 11:30 | 588 | 588
2018-08-08 12:00 | 585 | 585
2018-08-08 12:30 | 571 | 570
2018-08-08 13:00 | 583 | 583
2018-08-08 13:30 | 591 | 590
2018-08-08 14:00 | 593 | 592
2018-08-08 14:30 | 618 | 618
2018-08-08 15:00 | 623 | 622
2018-08-08 15:30 | 660 | 660
2018-08-08 16:00 | 708 | 708
2018-08-08 16:30 | 756 | 756
2018-08-08 17:00 | 816 | 812
2018-08-08 17:30 | 872 | 870
2018-08-08 18:00 | 937 | 934
2018-08-08 18:30 | 954 | 950
2018-08-08 19:00 | 967 | 964
2018-08-08 19:30 | 949 | 945
2018-08-08 20:00 | 943 | 942
2018-08-08 20:30 | 944 | 942
2018-08-08 21:00 | 912 | 912
2018-08-08 21:30 | 863 | 863
2018-08-08 22:00 | 821 | 821
2018-08-08 22:30 | 791 | 791
2018-08-08 23:00 | 777 | 776
2018-08-08 23:30 | 736 | 734
2018-08-09 | 682 | 678
2018-08-09 00:30 | 633 | 623
2018-08-09 01:00 | 594 | 578
2018-08-09 01:30 | 565 | 544
2018-08-09 02:00 | 542 | 517
2018-08-09 02:30 | 515 | 489
2018-08-09 03:00 | 490 | 462
2018-08-09 03:30 | 537 | 513
2018-08-09 04:00 | 557 | 534
2018-08-09 04:30 | 575 | 555
2018-08-09 05:00 | 606 | 591
2018-08-09 05:30 | 649 | 641
2018-08-09 06:00 | 714 | 712
2018-08-09 06:30 | 823 | 822
2018-08-09 07:00 | 921 | 919
2018-08-09 07:30 | 978 | 974
2018-08-09 08:00 | 949 | 943
2018-08-09 08:30 | 889 | 881
2018-08-09 09:00 | 808 | 801
2018-08-09 09:30 | 743 | 742
2018-08-09 10:00 | 694 | 693
2018-08-09 10:30 | 662 | 661
2018-08-09 11:00 | 638 | 637
2018-08-09 11:30 | 614 | 613
2018-08-09 12:00 | 563 | 562
2018-08-09 12:30 | 567 | 565
2018-08-09 13:00 | 508 | 506
2018-08-09 13:30 | 617 | 616
2018-08-09 14:00 | 564 | 562
2018-08-09 14:30 | 652 | 652
2018-08-09 15:00 | 663 | 663
2018-08-09 15:30 | 692 | 692
2018-08-09 16:00 | 735 | 735
2018-08-09 16:30 | 772 | 772
2018-08-09 17:00 | 822 | 821
2018-08-09 17:30 | 882 | 880
2018-08-09 18:00 | 958 | 955
2018-08-09 18:30 | 980 | 977
2018-08-09 19:00 | 990 | 987
2018-08-09 19:30 | 980 | 977
2018-08-09 20:00 | 978 | 974
2018-08-09 20:30 | 971 | 966
2018-08-09 21:00 | 931 | 922
2018-08-09 21:30 | 881 | 869
2018-08-09 22:00 | 831 | 820
2018-08-09 22:30 | 798 | 795
2018-08-09 23:00 | 773 | 769
2018-08-09 23:30 | 705 | 699
2018-08-10 | 664 | 657
2018-08-10 00:30 | 631 | 622
2018-08-10 01:00 | 615 | 602
2018-08-10 01:30 | 593 | 576
2018-08-10 02:00 | 580 | 561
2018-08-10 02:30 | 568 | 546
2018-08-10 03:00 | 562 | 539
2018-08-10 03:30 | 568 | 546
2018-08-10 04:00 | 572 | 551
2018-08-10 04:30 | 596 | 578
2018-08-10 05:00 | 617 | 603
2018-08-10 05:30 | 659 | 651
2018-08-10 06:00 | 680 | 673
2018-08-10 06:30 | 776 | 773
2018-08-10 07:00 | 864 | 862
2018-08-10 07:30 | 905 | 905
2018-08-10 08:00 | 886 | 886
2018-08-10 08:30 | 833 | 832
2018-08-10 09:00 | 765 | 760
2018-08-10 09:30 | 711 | 705
2018-08-10 10:00 | 676 | 675
2018-08-10 10:30 | 647 | 645
2018-08-10 11:00 | 635 | 634
2018-08-10 11:30 | 614 | 614
2018-08-10 12:00 | 612 | 611
2018-08-10 12:30 | 592 | 591
2018-08-10 13:00 | 597 | 595
2018-08-10 13:30 | 606 | 604
2018-08-10 14:00 | 612 | 610
2018-08-10 14:30 | 627 | 625
2018-08-10 15:00 | 639 | 636
2018-08-10 15:30 | 662 | 662
2018-08-10 16:00 | 700 | 700
2018-08-10 16:30 | 747 | 747
2018-08-10 17:00 | 791 | 791
2018-08-10 17:30 | 831 | 831
2018-08-10 18:00 | 879 | 876
2018-08-10 18:30 | 895 | 888
2018-08-10 19:00 | 900 | 893
2018-08-10 19:30 | 881 | 876
2018-08-10 20:00 | 872 | 869
2018-08-10 20:30 | 864 | 861
2018-08-10 21:00 | 843 | 838
2018-08-10 21:30 | 798 | 797
2018-08-10 22:00 | 774 | 772
2018-08-10 22:30 | 747 | 745
2018-08-10 23:00 | 735 | 734
2018-08-10 23:30 | 696 | 693
2018-08-11 | 650 | 644
2018-08-11 00:30 | 601 | 588
2018-08-11 01:00 | 575 | 558
2018-08-11 01:30 | 556 | 535
2018-08-11 02:00 | 541 | 515
2018-08-11 02:30 | 529 | 500
2018-08-11 03:00 | 527 | 496
2018-08-11 03:30 | 529 | 497
2018-08-11 04:00 | 531 | 498
2018-08-11 04:30 | 534 | 503
2018-08-11 05:00 | 535 | 505
2018-08-11 05:30 | 555 | 529
2018-08-11 06:00 | 564 | 544
2018-08-11 06:30 | 585 | 568
2018-08-11 07:00 | 630 | 616
2018-08-11 07:30 | 658 | 651
2018-08-11 08:00 | 681 | 677
2018-08-11 08:30 | 702 | 698
2018-08-11 09:00 | 699 | 695
2018-08-11 09:30 | 682 | 679
2018-08-11 10:00 | 646 | 643
2018-08-11 10:30 | 609 | 606
2018-08-11 11:00 | 574 | 570
2018-08-11 11:30 | 542 | 535
2018-08-11 12:00 | 526 | 518
2018-08-11 12:30 | 521 | 513
2018-08-11 13:00 | 514 | 505
2018-08-11 13:30 | 506 | 497
2018-08-11 14:00 | 533 | 523
2018-08-11 14:30 | 545 | 535
2018-08-11 15:00 | 559 | 551
2018-08-11 15:30 | 588 | 581
2018-08-11 16:00 | 615 | 609
2018-08-11 16:30 | 650 | 647
2018-08-11 17:00 | 698 | 696
2018-08-11 17:30 | 731 | 728
2018-08-11 18:00 | 771 | 770
2018-08-11 18:30 | 789 | 785
2018-08-11 19:00 | 790 | 785
2018-08-11 19:30 | 777 | 771
2018-08-11 20:00 | 762 | 758
2018-08-11 20:30 | 755 | 752
2018-08-11 21:00 | 732 | 731
2018-08-11 21:30 | 714 | 712
2018-08-11 22:00 | 694 | 692
2018-08-11 22:30 | 694 | 691
2018-08-11 23:00 | 698 | 694
2018-08-11 23:30 | 672 | 666
2018-08-12 | 628 | 619
2018-08-12 00:30 | 588 | 571
2018-08-12 01:00 | 566 | 544
2018-08-12 01:30 | 552 | 528
2018-08-12 02:00 | 531 | 503
2018-08-12 02:30 | 524 | 492
2018-08-12 03:00 | 521 | 485
2018-08-12 03:30 | 519 | 483
2018-08-12 04:00 | 525 | 487
2018-08-12 04:30 | 521 | 484
2018-08-12 05:00 | 528 | 491
2018-08-12 05:30 | 536 | 503
2018-08-12 06:00 | 546 | 516
2018-08-12 06:30 | 566 | 537
2018-08-12 07:00 | 585 | 557
2018-08-12 07:30 | 601 | 581
2018-08-12 08:00 | 607 | 591
2018-08-12 08:30 | 609 | 597
2018-08-12 09:00 | 605 | 595
2018-08-12 09:30 | 592 | 582
2018-08-12 10:00 | 575 | 565
2018-08-12 10:30 | 554 | 544
2018-08-12 11:00 | 557 | 549
2018-08-12 11:30 | 533 | 525
2018-08-12 12:00 | 527 | 518
2018-08-12 12:30 | 514 | 503
2018-08-12 13:00 | 508 | 497
2018-08-12 13:30 | 489 | 476
2018-08-12 14:00 | 494 | 478
2018-08-12 14:30 | 522 | 509
2018-08-12 15:00 | 560 | 546
2018-08-12 15:30 | 587 | 575
2018-08-12 16:00 | 621 | 609
2018-08-12 16:30 | 667 | 659
2018-08-12 17:00 | 713 | 709
2018-08-12 17:30 | 766 | 763
2018-08-12 18:00 | 822 | 818
2018-08-12 18:30 | 854 | 848
2018-08-12 19:00 | 858 | 851
2018-08-12 19:30 | 844 | 837
2018-08-12 20:00 | 831 | 829
2018-08-12 20:30 | 826 | 825
2018-08-12 21:00 | 795 | 794
2018-08-12 21:30 | 770 | 768
2018-08-12 22:00 | 741 | 737
2018-08-12 22:30 | 724 | 719
2018-08-12 23:00 | 719 | 714
2018-08-12 23:30 | 684 | 677
2018-08-13 | 643 | 631
2018-08-13 00:30 | 604 | 586
2018-08-13 01:00 | 513 | 486
2018-08-13 01:30 | 522 | 492
2018-08-13 02:00 | 528 | 496
2018-08-13 02:30 | 554 | 525
2018-08-13 03:00 | 550 | 518
2018-08-13 03:30 | 554 | 522
2018-08-13 04:00 | 566 | 537
2018-08-13 04:30 | 575 | 548
2018-08-13 05:00 | 563 | 540
2018-08-13 05:30 | 602 | 587
2018-08-13 06:00 | 654 | 646
2018-08-13 06:30 | 748 | 744
2018-08-13 07:00 | 835 | 833
2018-08-13 07:30 | 878 | 878
2018-08-13 08:00 | 869 | 868
2018-08-13 08:30 | 830 | 830
2018-08-13 09:00 | 771 | 770
2018-08-13 09:30 | 725 | 721
2018-08-13 10:00 | 685 | 680
2018-08-13 10:30 | 644 | 637
2018-08-13 11:00 | 607 | 606
2018-08-13 11:30 | 596 | 594
2018-08-13 12:00 | 591 | 589
2018-08-13 12:30 | 584 | 581
2018-08-13 13:00 | 581 | 579
2018-08-13 13:30 | 583 | 582
2018-08-13 14:00 | 606 | 606
2018-08-13 14:30 | 619 | 619
2018-08-13 15:00 | 647 | 647
2018-08-13 15:30 | 674 | 674
2018-08-13 16:00 | 714 | 714
2018-08-13 16:30 | 767 | 767
2018-08-13 17:00 | 833 | 826
2018-08-13 17:30 | 890 | 886
2018-08-13 18:00 | 963 | 959
2018-08-13 18:30 | 984 | 980
2018-08-13 19:00 | 990 | 986
2018-08-13 19:30 | 975 | 970
2018-08-13 20:00 | 974 | 970
2018-08-13 20:30 | 960 | 956
2018-08-13 21:00 | 921 | 920
2018-08-13 21:30 | 892 | 892
2018-08-13 22:00 | 856 | 856
2018-08-13 22:30 | 810 | 809
2018-08-13 23:00 | 787 | 786
2018-08-13 23:30 | 745 | 744
2018-08-14 | 718 | 716
2018-08-14 00:30 | 648 | 641
2018-08-14 01:00 | 615 | 605
2018-08-14 01:30 | 598 | 586
2018-08-14 02:00 | 580 | 565
2018-08-14 02:30 | 531 | 508
2018-08-14 03:00 | 550 | 529
2018-08-14 03:30 | 576 | 556
2018-08-14 04:00 | 593 | 573
2018-08-14 04:30 | 611 | 594
2018-08-14 05:00 | 639 | 627
2018-08-14 05:30 | 694 | 688
2018-08-14 06:00 | 729 | 727
2018-08-14 06:30 | 837 | 834
2018-08-14 07:00 | 933 | 932
2018-08-14 07:30 | 978 | 978
2018-08-14 08:00 | 960 | 959
2018-08-14 08:30 | 896 | 892
2018-08-14 09:00 | 815 | 813
2018-08-14 09:30 | 755 | 753
2018-08-14 10:00 | 710 | 708
2018-08-14 10:30 | 656 | 650
2018-08-14 11:00 | 554 | 552
2018-08-14 11:30 | 652 | 652
2018-08-14 12:00 | 645 | 645
2018-08-14 12:30 | 630 | 630
2018-08-14 13:00 | 628 | 628
2018-08-14 13:30 | 626 | 625
2018-08-14 14:00 | 634 | 633
2018-08-14 14:30 | 657 | 657
2018-08-14 15:00 | 684 | 684
2018-08-14 15:30 | 714 | 714
2018-08-14 16:00 | 747 | 747
2018-08-14 16:30 | 782 | 781
2018-08-14 17:00 | 818 | 817
2018-08-14 17:30 | 876 | 875
2018-08-14 18:00 | 940 | 939
2018-08-14 18:30 | 964 | 958
2018-08-14 19:00 | 974 | 968
2018-08-14 19:30 | 957 | 948
2018-08-14 20:00 | 938 | 936
2018-08-14 20:30 | 926 | 925
2018-08-14 21:00 | 890 | 887
2018-08-14 21:30 | 834 | 833
2018-08-14 22:00 | 805 | 803
2018-08-14 22:30 | 785 | 783
2018-08-14 23:00 | 766 | 764
2018-08-14 23:30 | 711 | 707
2018-08-15 | 668 | 661
2018-08-15 00:30 | 623 | 610
2018-08-15 01:00 | 593 | 580
2018-08-15 01:30 | 538 | 519
2018-08-15 02:00 | 506 | 481
2018-08-15 02:30 | 560 | 537
2018-08-15 03:00 | 557 | 533
2018-08-15 03:30 | 559 | 536
2018-08-15 04:00 | 562 | 540
2018-08-15 04:30 | 579 | 559
2018-08-15 05:00 | 595 | 579
2018-08-15 05:30 | 613 | 602
2018-08-15 06:00 | 644 | 639
2018-08-15 06:30 | 728 | 725
2018-08-15 07:00 | 804 | 803
2018-08-15 07:30 | 850 | 849
2018-08-15 08:00 | 840 | 838
2018-08-15 08:30 | 793 | 788
2018-08-15 09:00 | 739 | 730
2018-08-15 09:30 | 696 | 684
2018-08-15 10:00 | 666 | 650
2018-08-15 10:30 | 638 | 619
2018-08-15 11:00 | 592 | 590
2018-08-15 11:30 | 577 | 575
2018-08-15 12:00 | 566 | 563
2018-08-15 12:30 | 527 | 524
2018-08-15 13:00 | 518 | 514
2018-08-15 13:30 | 534 | 531
2018-08-15 14:00 | 512 | 509
2018-08-15 14:30 | 516 | 513
2018-08-15 15:00 | 561 | 559
2018-08-15 15:30 | 652 | 651
2018-08-15 16:00 | 696 | 695
2018-08-15 16:30 | 743 | 743
2018-08-15 17:00 | 781 | 781
2018-08-15 17:30 | 821 | 821
2018-08-15 18:00 | 877 | 876
2018-08-15 18:30 | 897 | 894
2018-08-15 19:00 | 898 | 895
2018-08-15 19:30 | 889 | 885
2018-08-15 20:00 | 879 | 878
2018-08-15 20:30 | 863 | 861
2018-08-15 21:00 | 832 | 830
2018-08-15 21:30 | 797 | 793
2018-08-15 22:00 | 762 | 757
2018-08-15 22:30 | 744 | 741
2018-08-15 23:00 | 730 | 727
2018-08-15 23:30 | 699 | 694
2018-08-16 | 656 | 650
2018-08-16 00:30 | 606 | 594
2018-08-16 01:00 | 584 | 567
2018-08-16 01:30 | 567 | 546
2018-08-16 02:00 | 553 | 527
2018-08-16 02:30 | 528 | 498
2018-08-16 03:00 | 478 | 443
2018-08-16 03:30 | 496 | 463
2018-08-16 04:00 | 545 | 516
2018-08-16 04:30 | 565 | 540
2018-08-16 05:00 | 582 | 563
2018-08-16 05:30 | 622 | 612
2018-08-16 06:00 | 674 | 670
2018-08-16 06:30 | 767 | 765
2018-08-16 07:00 | 847 | 847
2018-08-16 07:30 | 886 | 886
2018-08-16 08:00 | 863 | 863
2018-08-16 08:30 | 815 | 815
2018-08-16 09:00 | 748 | 746
2018-08-16 09:30 | 700 | 697
2018-08-16 10:00 | 664 | 659
2018-08-16 10:30 | 625 | 621
2018-08-16 11:00 | 609 | 607
2018-08-16 11:30 | 595 | 595
2018-08-16 12:00 | 591 | 591
2018-08-16 12:30 | 590 | 590
2018-08-16 13:00 | 602 | 601
2018-08-16 13:30 | 609 | 609
2018-08-16 14:00 | 629 | 629
2018-08-16 14:30 | 656 | 655
2018-08-16 15:00 | 679 | 679
2018-08-16 15:30 | 699 | 699
2018-08-16 16:00 | 740 | 740
2018-08-16 16:30 | 777 | 777
2018-08-16 17:00 | 834 | 828
2018-08-16 17:30 | 872 | 866
2018-08-16 18:00 | 922 | 919
2018-08-16 18:30 | 950 | 947
2018-08-16 19:00 | 940 | 935
2018-08-16 19:30 | 924 | 917
2018-08-16 20:00 | 933 | 929
2018-08-16 20:30 | 915 | 911
2018-08-16 21:00 | 882 | 873
2018-08-16 21:30 | 822 | 816
2018-08-16 22:00 | 789 | 784
2018-08-16 22:30 | 758 | 753
2018-08-16 23:00 | 734 | 733
2018-08-16 23:30 | 692 | 690
2018-08-17 | 645 | 640
2018-08-17 00:30 | 596 | 586
2018-08-17 01:00 | 567 | 553
2018-08-17 01:30 | 551 | 535
2018-08-17 02:00 | 536 | 517
2018-08-17 02:30 | 533 | 511
2018-08-17 03:00 | 532 | 509
2018-08-17 03:30 | 529 | 505
2018-08-17 04:00 | 527 | 503
2018-08-17 04:30 | 547 | 526
2018-08-17 05:00 | 561 | 544
2018-08-17 05:30 | 605 | 595
2018-08-17 06:00 | 662 | 659
2018-08-17 06:30 | 757 | 755
2018-08-17 07:00 | 836 | 833
2018-08-17 07:30 | 881 | 876
2018-08-17 08:00 | 854 | 847
2018-08-17 08:30 | 811 | 803
2018-08-17 09:00 | 764 | 760
2018-08-17 09:30 | 711 | 705
2018-08-17 10:00 | 667 | 663
2018-08-17 10:30 | 646 | 644
2018-08-17 11:00 | 633 | 633
2018-08-17 11:30 | 619 | 619
2018-08-17 12:00 | 618 | 618
2018-08-17 12:30 | 610 | 610
2018-08-17 13:00 | 595 | 595
2018-08-17 13:30 | 601 | 601
2018-08-17 14:00 | 617 | 617
2018-08-17 14:30 | 626 | 626
2018-08-17 15:00 | 638 | 638
2018-08-17 15:30 | 659 | 659
2018-08-17 16:00 | 723 | 723
2018-08-17 16:30 | 761 | 760
2018-08-17 17:00 | 795 | 795
2018-08-17 17:30 | 827 | 827
2018-08-17 18:00 | 864 | 864
2018-08-17 18:30 | 871 | 870
2018-08-17 19:00 | 878 | 876
2018-08-17 19:30 | 859 | 856
2018-08-17 20:00 | 849 | 847
2018-08-17 20:30 | 863 | 861
2018-08-17 21:00 | 831 | 831
2018-08-17 21:30 | 791 | 791
2018-08-17 22:00 | 766 | 765
2018-08-17 22:30 | 758 | 758
2018-08-17 23:00 | 751 | 751
2018-08-17 23:30 | 716 | 714
2018-08-18 | 668 | 664
2018-08-18 00:30 | 620 | 612
2018-08-18 01:00 | 579 | 566
2018-08-18 01:30 | 565 | 546
2018-08-18 02:00 | 537 | 515
2018-08-18 02:30 | 497 | 469
2018-08-18 03:00 | 491 | 459
2018-08-18 03:30 | 487 | 456
2018-08-18 04:00 | 528 | 499
2018-08-18 04:30 | 528 | 499
2018-08-18 05:00 | 534 | 508
2018-08-18 05:30 | 554 | 531
2018-08-18 06:00 | 580 | 563
2018-08-18 06:30 | 597 | 583
2018-08-18 07:00 | 617 | 606
2018-08-18 07:30 | 643 | 638
2018-08-18 08:00 | 651 | 648
2018-08-18 08:30 | 646 | 643
2018-08-18 09:00 | 636 | 633
2018-08-18 09:30 | 600 | 597
2018-08-18 10:00 | 516 | 510
2018-08-18 10:30 | 496 | 489
2018-08-18 11:00 | 523 | 518
2018-08-18 11:30 | 496 | 489
2018-08-18 12:00 | 461 | 452
2018-08-18 12:30 | 456 | 444
2018-08-18 13:00 | 451 | 441
2018-08-18 13:30 | 457 | 447
2018-08-18 14:00 | 497 | 490
2018-08-18 14:30 | 512 | 505
2018-08-18 15:00 | 533 | 526
2018-08-18 15:30 | 589 | 583
2018-08-18 16:00 | 622 | 618
2018-08-18 16:30 | 664 | 662
2018-08-18 17:00 | 691 | 689
2018-08-18 17:30 | 716 | 715
2018-08-18 18:00 | 746 | 746
2018-08-18 18:30 | 784 | 782
2018-08-18 19:00 | 782 | 779
2018-08-18 19:30 | 771 | 767
2018-08-18 20:00 | 765 | 764
2018-08-18 20:30 | 755 | 754
2018-08-18 21:00 | 732 | 731
2018-08-18 21:30 | 710 | 708
2018-08-18 22:00 | 691 | 689
2018-08-18 22:30 | 693 | 689
2018-08-18 23:00 | 690 | 686
2018-08-18 23:30 | 662 | 658
2018-08-19 | 628 | 618
2018-08-19 00:30 | 577 | 559
2018-08-19 01:00 | 553 | 531
2018-08-19 01:30 | 534 | 508
2018-08-19 02:00 | 502 | 469
2018-08-19 02:30 | 484 | 448
2018-08-19 03:00 | 495 | 459
2018-08-19 03:30 | 472 | 432
2018-08-19 04:00 | 472 | 432
2018-08-19 04:30 | 474 | 434
2018-08-19 05:00 | 479 | 439
2018-08-19 05:30 | 496 | 462
2018-08-19 06:00 | 530 | 501
2018-08-19 06:30 | 560 | 534
2018-08-19 07:00 | 580 | 557
2018-08-19 07:30 | 585 | 566
2018-08-19 08:00 | 596 | 581
2018-08-19 08:30 | 594 | 581
2018-08-19 09:00 | 583 | 570
2018-08-19 09:30 | 568 | 558
2018-08-19 10:00 | 550 | 539
2018-08-19 10:30 | 527 | 515
2018-08-19 11:00 | 511 | 499
2018-08-19 11:30 | 490 | 475
2018-08-19 12:00 | 481 | 465
2018-08-19 12:30 | 473 | 456
2018-08-19 13:00 | 472 | 455
2018-08-19 13:30 | 481 | 465
2018-08-19 14:00 | 479 | 463
2018-08-19 14:30 | 474 | 457
2018-08-19 15:00 | 531 | 520
2018-08-19 15:30 | 571 | 562
2018-08-19 16:00 | 606 | 600
2018-08-19 16:30 | 653 | 648
2018-08-19 17:00 | 711 | 710
2018-08-19 17:30 | 753 | 753
2018-08-19 18:00 | 813 | 811
2018-08-19 18:30 | 843 | 843
2018-08-19 19:00 | 851 | 851
2018-08-19 19:30 | 836 | 836
2018-08-19 20:00 | 832 | 831
2018-08-19 20:30 | 831 | 831
2018-08-19 21:00 | 795 | 794
2018-08-19 21:30 | 763 | 759
2018-08-19 22:00 | 737 | 731
2018-08-19 22:30 | 711 | 705
2018-08-19 23:00 | 697 | 695
2018-08-19 23:30 | 664 | 661
2018-08-20 | 620 | 612
2018-08-20 00:30 | 582 | 570
2018-08-20 01:00 | 567 | 551
2018-08-20 01:30 | 546 | 527
2018-08-20 02:00 | 532 | 511
2018-08-20 02:30 | 525 | 501
2018-08-20 03:00 | 518 | 493
2018-08-20 03:30 | 520 | 493
2018-08-20 04:00 | 527 | 502
2018-08-20 04:30 | 539 | 517
2018-08-20 05:00 | 567 | 550
2018-08-20 05:30 | 611 | 602
2018-08-20 06:00 | 670 | 666
2018-08-20 06:30 | 768 | 762
2018-08-20 07:00 | 846 | 842
2018-08-20 07:30 | 880 | 878
2018-08-20 08:00 | 844 | 841
2018-08-20 08:30 | 792 | 786
2018-08-20 09:00 | 733 | 724
2018-08-20 09:30 | 674 | 669
2018-08-20 10:00 | 640 | 637
2018-08-20 10:30 | 624 | 620
2018-08-20 11:00 | 595 | 591
2018-08-20 11:30 | 567 | 566
2018-08-20 12:00 | 552 | 550
2018-08-20 12:30 | 548 | 546
2018-08-20 13:00 | 547 | 546
2018-08-20 13:30 | 565 | 564
2018-08-20 14:00 | 587 | 587
2018-08-20 14:30 | 609 | 609
2018-08-20 15:00 | 642 | 642
2018-08-20 15:30 | 675 | 675
2018-08-20 16:00 | 718 | 718
2018-08-20 16:30 | 775 | 772
2018-08-20 17:00 | 835 | 830
2018-08-20 17:30 | 903 | 898
2018-08-20 18:00 | 990 | 990
2018-08-20 18:30 | 1010 | 1009
2018-08-20 19:00 | 1004 | 1002
2018-08-20 19:30 | 995 | 993
2018-08-20 20:00 | 990 | 988
2018-08-20 20:30 | 984 | 980
2018-08-20 21:00 | 951 | 945
2018-08-20 21:30 | 903 | 896
2018-08-20 22:00 | 861 | 850
2018-08-20 22:30 | 817 | 809
2018-08-20 23:00 | 797 | 787
2018-08-20 23:30 | 742 | 738
2018-08-21 | 690 | 685
2018-08-21 00:30 | 636 | 627
2018-08-21 01:00 | 593 | 580
2018-08-21 01:30 | 583 | 568
2018-08-21 02:00 | 573 | 555
2018-08-21 02:30 | 566 | 546
2018-08-21 03:00 | 563 | 541
2018-08-21 03:30 | 560 | 537
2018-08-21 04:00 | 568 | 547
2018-08-21 04:30 | 584 | 567
2018-08-21 05:00 | 608 | 595
2018-08-21 05:30 | 679 | 672
2018-08-21 06:00 | 764 | 760
2018-08-21 06:30 | 882 | 882
2018-08-21 07:00 | 964 | 964
2018-08-21 07:30 | 997 | 996
2018-08-21 08:00 | 983 | 983
2018-08-21 08:30 | 892 | 889
2018-08-21 09:00 | 813 | 804
2018-08-21 09:30 | 757 | 746
2018-08-21 10:00 | 706 | 700
2018-08-21 10:30 | 660 | 655
2018-08-21 11:00 | 632 | 628
2018-08-21 11:30 | 604 | 603
2018-08-21 12:00 | 593 | 593
2018-08-21 12:30 | 592 | 591
2018-08-21 13:00 | 595 | 595
2018-08-21 13:30 | 598 | 598
2018-08-21 14:00 | 616 | 616
2018-08-21 14:30 | 631 | 631
2018-08-21 15:00 | 650 | 650
2018-08-21 15:30 | 685 | 685
2018-08-21 16:00 | 728 | 728
2018-08-21 16:30 | 776 | 776
2018-08-21 17:00 | 824 | 824
2018-08-21 17:30 | 884 | 884
2018-08-21 18:00 | 954 | 951
2018-08-21 18:30 | 983 | 977
2018-08-21 19:00 | 994 | 989
2018-08-21 19:30 | 986 | 978
2018-08-21 20:00 | 987 | 979
2018-08-21 20:30 | 980 | 972
2018-08-21 21:00 | 930 | 928
2018-08-21 21:30 | 880 | 877
2018-08-21 22:00 | 847 | 841
2018-08-21 22:30 | 806 | 804
2018-08-21 23:00 | 785 | 782
2018-08-21 23:30 | 740 | 738
2018-08-22 | 692 | 687
2018-08-22 00:30 | 642 | 632
2018-08-22 01:00 | 607 | 594
2018-08-22 01:30 | 583 | 566
2018-08-22 02:00 | 562 | 542
2018-08-22 02:30 | 557 | 535
2018-08-22 03:00 | 556 | 533
2018-08-22 03:30 | 559 | 535
2018-08-22 04:00 | 564 | 540
2018-08-22 04:30 | 587 | 568
2018-08-22 05:00 | 628 | 613
2018-08-22 05:30 | 685 | 678
2018-08-22 06:00 | 754 | 750
2018-08-22 06:30 | 839 | 838
2018-08-22 07:00 | 894 | 893
2018-08-22 07:30 | 938 | 938
2018-08-22 08:00 | 908 | 907
2018-08-22 08:30 | 841 | 838
2018-08-22 09:00 | 773 | 766
2018-08-22 09:30 | 718 | 712
2018-08-22 10:00 | 668 | 664
2018-08-22 10:30 | 639 | 633
2018-08-22 11:00 | 619 | 611
2018-08-22 11:30 | 607 | 599
2018-08-22 12:00 | 580 | 578
2018-08-22 12:30 | 577 | 574
2018-08-22 13:00 | 583 | 581
2018-08-22 13:30 | 587 | 586
2018-08-22 14:00 | 607 | 606
2018-08-22 14:30 | 622 | 622
2018-08-22 15:00 | 642 | 641
2018-08-22 15:30 | 673 | 672
2018-08-22 16:00 | 712 | 710
2018-08-22 16:30 | 751 | 750
2018-08-22 17:00 | 800 | 799
2018-08-22 17:30 | 849 | 847
2018-08-22 18:00 | 918 | 917
2018-08-22 18:30 | 958 | 955
2018-08-22 19:00 | 983 | 977
2018-08-22 19:30 | 965 | 957
2018-08-22 20:00 | 950 | 941
2018-08-22 20:30 | 945 | 938
2018-08-22 21:00 | 890 | 887
2018-08-22 21:30 | 838 | 838
2018-08-22 22:00 | 809 | 808
2018-08-22 22:30 | 775 | 772
2018-08-22 23:00 | 757 | 752
2018-08-22 23:30 | 717 | 709
2018-08-23 | 677 | 666
2018-08-23 00:30 | 628 | 613
2018-08-23 01:00 | 591 | 575
2018-08-23 01:30 | 575 | 554
2018-08-23 02:00 | 560 | 537
2018-08-23 02:30 | 552 | 527
2018-08-23 03:00 | 549 | 523
2018-08-23 03:30 | 550 | 524
2018-08-23 04:00 | 533 | 506
2018-08-23 04:30 | 568 | 544
2018-08-23 05:00 | 589 | 569
2018-08-23 05:30 | 631 | 621
2018-08-23 06:00 | 684 | 677
2018-08-23 06:30 | 807 | 805
2018-08-23 07:00 | 919 | 919
2018-08-23 07:30 | 906 | 905
2018-08-23 08:00 | 885 | 885
2018-08-23 08:30 | 829 | 828
2018-08-23 09:00 | 759 | 756
2018-08-23 09:30 | 711 | 707
2018-08-23 10:00 | 676 | 673
2018-08-23 10:30 | 648 | 647
2018-08-23 11:00 | 637 | 636
2018-08-23 11:30 | 627 | 627
2018-08-23 12:00 | 619 | 619
2018-08-23 12:30 | 611 | 611
2018-08-23 13:00 | 608 | 608
2018-08-23 13:30 | 607 | 607
2018-08-23 14:00 | 622 | 622
2018-08-23 14:30 | 639 | 639
2018-08-23 15:00 | 656 | 656
2018-08-23 15:30 | 675 | 675
2018-08-23 16:00 | 702 | 702
2018-08-23 16:30 | 747 | 747
2018-08-23 17:00 | 795 | 795
2018-08-23 17:30 | 857 | 857
2018-08-23 18:00 | 923 | 923
2018-08-23 18:30 | 955 | 953
2018-08-23 19:00 | 977 | 974
2018-08-23 19:30 | 958 | 954
2018-08-23 20:00 | 953 | 950
2018-08-23 20:30 | 935 | 931
2018-08-23 21:00 | 898 | 895
2018-08-23 21:30 | 846 | 842
2018-08-23 22:00 | 806 | 799
2018-08-23 22:30 | 782 | 776
2018-08-23 23:00 | 756 | 755
2018-08-23 23:30 | 711 | 708
2018-08-24 | 659 | 654
2018-08-24 00:30 | 616 | 606
2018-08-24 01:00 | 589 | 575
2018-08-24 01:30 | 565 | 547
2018-08-24 02:00 | 554 | 533
2018-08-24 02:30 | 548 | 524
2018-08-24 03:00 | 544 | 518
2018-08-24 03:30 | 545 | 520
2018-08-24 04:00 | 546 | 521
2018-08-24 04:30 | 560 | 537
2018-08-24 05:00 | 584 | 566
2018-08-24 05:30 | 622 | 612
2018-08-24 06:00 | 681 | 676
2018-08-24 06:30 | 781 | 775
2018-08-24 07:00 | 843 | 841
2018-08-24 07:30 | 871 | 866
2018-08-24 08:00 | 834 | 828
2018-08-24 08:30 | 786 | 782
2018-08-24 09:00 | 728 | 727
2018-08-24 09:30 | 691 | 689
2018-08-24 10:00 | 671 | 669
2018-08-24 10:30 | 663 | 661
2018-08-24 11:00 | 650 | 648
2018-08-24 11:30 | 645 | 643
2018-08-24 12:00 | 647 | 646
2018-08-24 12:30 | 642 | 642
2018-08-24 13:00 | 684 | 683
2018-08-24 13:30 | 705 | 705
2018-08-24 14:00 | 709 | 709
2018-08-24 14:30 | 696 | 695
2018-08-24 15:00 | 704 | 703
2018-08-24 15:30 | 716 | 716
2018-08-24 16:00 | 755 | 755
2018-08-24 16:30 | 796 | 796
2018-08-24 17:00 | 843 | 841
2018-08-24 17:30 | 880 | 879
2018-08-24 18:00 | 922 | 921
2018-08-24 18:30 | 937 | 934
2018-08-24 19:00 | 945 | 941
2018-08-24 19:30 | 920 | 915
2018-08-24 20:00 | 895 | 892
2018-08-24 20:30 | 882 | 877
2018-08-24 21:00 | 839 | 836
2018-08-24 21:30 | 811 | 808
2018-08-24 22:00 | 768 | 768
2018-08-24 22:30 | 753 | 753
2018-08-24 23:00 | 744 | 743
2018-08-24 23:30 | 704 | 701
2018-08-25 | 656 | 650
2018-08-25 00:30 | 604 | 592
2018-08-25 01:00 | 579 | 565
2018-08-25 01:30 | 557 | 540
2018-08-25 02:00 | 536 | 518
2018-08-25 02:30 | 531 | 511
2018-08-25 03:00 | 526 | 506
2018-08-25 03:30 | 525 | 505
2018-08-25 04:00 | 520 | 501
2018-08-25 04:30 | 523 | 503
2018-08-25 05:00 | 530 | 511
2018-08-25 05:30 | 542 | 526
2018-08-25 06:00 | 556 | 543
2018-08-25 06:30 | 583 | 572
2018-08-25 07:00 | 613 | 604
2018-08-25 07:30 | 645 | 640
2018-08-25 08:00 | 658 | 655
2018-08-25 08:30 | 666 | 664
2018-08-25 09:00 | 656 | 654
2018-08-25 09:30 | 645 | 643
2018-08-25 10:00 | 620 | 617
2018-08-25 10:30 | 592 | 590
2018-08-25 11:00 | 573 | 571
2018-08-25 11:30 | 570 | 567
2018-08-25 12:00 | 525 | 520
2018-08-25 12:30 | 567 | 562
2018-08-25 13:00 | 573 | 568
2018-08-25 13:30 | 621 | 615
2018-08-25 14:00 | 643 | 636
2018-08-25 14:30 | 652 | 646
2018-08-25 15:00 | 601 | 595
2018-08-25 15:30 | 622 | 618
2018-08-25 16:00 | 685 | 684
2018-08-25 16:30 | 751 | 750
2018-08-25 17:00 | 792 | 791
2018-08-25 17:30 | 798 | 797
2018-08-25 18:00 | 865 | 865
2018-08-25 18:30 | 891 | 891
2018-08-25 19:00 | 904 | 904
2018-08-25 19:30 | 881 | 881
2018-08-25 20:00 | 859 | 857
2018-08-25 20:30 | 831 | 830
2018-08-25 21:00 | 786 | 786
2018-08-25 21:30 | 765 | 765
2018-08-25 22:00 | 775 | 774
2018-08-25 22:30 | 769 | 769
2018-08-25 23:00 | 761 | 760
2018-08-25 23:30 | 763 | 762
2018-08-26 | 717 | 714
2018-08-26 00:30 | 673 | 667
2018-08-26 01:00 | 644 | 637
2018-08-26 01:30 | 617 | 607
2018-08-26 02:00 | 593 | 578
2018-08-26 02:30 | 583 | 567
2018-08-26 03:00 | 573 | 555
2018-08-26 03:30 | 574 | 556
2018-08-26 04:00 | 570 | 551
2018-08-26 04:30 | 563 | 542
2018-08-26 05:00 | 545 | 520
2018-08-26 05:30 | 569 | 549
2018-08-26 06:00 | 584 | 567
2018-08-26 06:30 | 607 | 593
2018-08-26 07:00 | 628 | 615
2018-08-26 07:30 | 673 | 666
2018-08-26 08:00 | 712 | 708
2018-08-26 08:30 | 754 | 753
2018-08-26 09:00 | 781 | 781
2018-08-26 09:30 | 805 | 805
2018-08-26 10:00 | 817 | 817
2018-08-26 10:30 | 833 | 833
2018-08-26 11:00 | 821 | 821
2018-08-26 11:30 | 784 | 784
2018-08-26 12:00 | 779 | 779
2018-08-26 12:30 | 724 | 723
2018-08-26 13:00 | 738 | 737
2018-08-26 13:30 | 721 | 720
2018-08-26 14:00 | 732 | 730
2018-08-26 14:30 | 736 | 735
2018-08-26 15:00 | 739 | 737
2018-08-26 15:30 | 759 | 759
2018-08-26 16:00 | 784 | 784
2018-08-26 16:30 | 818 | 818
2018-08-26 17:00 | 852 | 852
2018-08-26 17:30 | 898 | 898
2018-08-26 18:00 | 920 | 920
2018-08-26 18:30 | 960 | 960
2018-08-26 19:00 | 942 | 942
2018-08-26 19:30 | 915 | 913
2018-08-26 20:00 | 901 | 898
2018-08-26 20:30 | 886 | 884
2018-08-26 21:00 | 850 | 847
2018-08-26 21:30 | 804 | 803
2018-08-26 22:00 | 770 | 768
2018-08-26 22:30 | 742 | 741
2018-08-26 23:00 | 733 | 731
2018-08-26 23:30 | 689 | 685
2018-08-27 | 643 | 636
2018-08-27 00:30 | 600 | 588
2018-08-27 01:00 | 582 | 566
2018-08-27 01:30 | 555 | 536
2018-08-27 02:00 | 526 | 503
2018-08-27 02:30 | 524 | 500
2018-08-27 03:00 | 514 | 488
2018-08-27 03:30 | 533 | 507
2018-08-27 04:00 | 537 | 513
2018-08-27 04:30 | 554 | 533
2018-08-27 05:00 | 580 | 564
2018-08-27 05:30 | 628 | 619
2018-08-27 06:00 | 685 | 681
2018-08-27 06:30 | 769 | 767
2018-08-27 07:00 | 828 | 826
2018-08-27 07:30 | 863 | 858
2018-08-27 08:00 | 831 | 825
2018-08-27 08:30 | 770 | 762
2018-08-27 09:00 | 718 | 712
2018-08-27 09:30 | 676 | 673
2018-08-27 10:00 | 646 | 643
2018-08-27 10:30 | 621 | 618
2018-08-27 11:00 | 604 | 604
2018-08-27 11:30 | 588 | 588
2018-08-27 12:00 | 585 | 584
2018-08-27 12:30 | 586 | 585
2018-08-27 13:00 | 608 | 608
2018-08-27 13:30 | 624 | 624
2018-08-27 14:00 | 640 | 640
2018-08-27 14:30 | 653 | 652
2018-08-27 15:00 | 658 | 658
2018-08-27 15:30 | 677 | 677
2018-08-27 16:00 | 708 | 708
2018-08-27 16:30 | 756 | 754
2018-08-27 17:00 | 806 | 803
2018-08-27 17:30 | 873 | 868
2018-08-27 18:00 | 933 | 930
2018-08-27 18:30 | 954 | 953
2018-08-27 19:00 | 959 | 957
2018-08-27 19:30 | 945 | 943
2018-08-27 20:00 | 926 | 921
2018-08-27 20:30 | 916 | 913
2018-08-27 21:00 | 865 | 862
2018-08-27 21:30 | 809 | 808
2018-08-27 22:00 | 771 | 771
2018-08-27 22:30 | 744 | 743
2018-08-27 23:00 | 731 | 729
2018-08-27 23:30 | 697 | 694
2018-08-28 | 651 | 646
2018-08-28 00:30 | 606 | 596
2018-08-28 01:00 | 578 | 564
2018-08-28 01:30 | 556 | 539
2018-08-28 02:00 | 538 | 518
2018-08-28 02:30 | 535 | 514
2018-08-28 03:00 | 529 | 504
2018-08-28 03:30 | 530 | 503
2018-08-28 04:00 | 529 | 501
2018-08-28 04:30 | 541 | 516
2018-08-28 05:00 | 557 | 536
2018-08-28 05:30 | 590 | 578
2018-08-28 06:00 | 635 | 630
2018-08-28 06:30 | 715 | 712
2018-08-28 07:00 | 790 | 789
2018-08-28 07:30 | 829 | 824
2018-08-28 08:00 | 824 | 820
2018-08-28 08:30 | 784 | 778
2018-08-28 09:00 | 722 | 716
2018-08-28 09:30 | 680 | 674
2018-08-28 10:00 | 643 | 640
2018-08-28 10:30 | 625 | 621
2018-08-28 11:00 | 622 | 619
2018-08-28 11:30 | 608 | 608
2018-08-28 12:00 | 611 | 611
2018-08-28 12:30 | 604 | 604
2018-08-28 13:00 | 612 | 612
2018-08-28 13:30 | 608 | 608
2018-08-28 14:00 | 618 | 618
2018-08-28 14:30 | 629 | 629
2018-08-28 15:00 | 645 | 645
2018-08-28 15:30 | 669 | 669
2018-08-28 16:00 | 710 | 710
2018-08-28 16:30 | 755 | 755
2018-08-28 17:00 | 803 | 802
2018-08-28 17:30 | 858 | 852
2018-08-28 18:00 | 909 | 906
2018-08-28 18:30 | 949 | 946
2018-08-28 19:00 | 956 | 953
2018-08-28 19:30 | 961 | 957
2018-08-28 20:00 | 930 | 925
2018-08-28 20:30 | 923 | 921
2018-08-28 21:00 | 861 | 861
2018-08-28 21:30 | 821 | 819
2018-08-28 22:00 | 784 | 780
2018-08-28 22:30 | 755 | 749
2018-08-28 23:00 | 739 | 738
2018-08-28 23:30 | 703 | 701
2018-08-29 | 657 | 652
2018-08-29 00:30 | 603 | 593
2018-08-29 01:00 | 575 | 560
2018-08-29 01:30 | 554 | 537
2018-08-29 02:00 | 539 | 518
2018-08-29 02:30 | 528 | 504
2018-08-29 03:00 | 527 | 502
2018-08-29 03:30 | 528 | 503
2018-08-29 04:00 | 529 | 503
2018-08-29 04:30 | 497 | 469
2018-08-29 05:00 | 544 | 523
2018-08-29 05:30 | 572 | 559
2018-08-29 06:00 | 641 | 635
2018-08-29 06:30 | 736 | 735
2018-08-29 07:00 | 796 | 794
2018-08-29 07:30 | 842 | 839
2018-08-29 08:00 | 806 | 801
2018-08-29 08:30 | 791 | 787
2018-08-29 09:00 | 730 | 723
2018-08-29 09:30 | 657 | 647
2018-08-29 10:00 | 596 | 593
2018-08-29 10:30 | 598 | 596
2018-08-29 11:00 | 580 | 580
2018-08-29 11:30 | 559 | 559
2018-08-29 12:00 | 546 | 545
2018-08-29 12:30 | 514 | 514
2018-08-29 13:00 | 477 | 476
2018-08-29 13:30 | 523 | 522
2018-08-29 14:00 | 552 | 551
2018-08-29 14:30 | 593 | 593
2018-08-29 15:00 | 612 | 612
2018-08-29 15:30 | 610 | 609
2018-08-29 16:00 | 656 | 655
2018-08-29 16:30 | 725 | 721
2018-08-29 17:00 | 792 | 791
2018-08-29 17:30 | 819 | 818
2018-08-29 18:00 | 881 | 880
2018-08-29 18:30 | 964 | 957
2018-08-29 19:00 | 978 | 970
2018-08-29 19:30 | 941 | 928
2018-08-29 20:00 | 886 | 880
2018-08-29 20:30 | 891 | 888
2018-08-29 21:00 | 856 | 852
2018-08-29 21:30 | 807 | 799
2018-08-29 22:00 | 765 | 756
2018-08-29 22:30 | 740 | 733
2018-08-29 23:00 | 726 | 722
2018-08-29 23:30 | 670 | 664
2018-08-30 | 623 | 618
2018-08-30 00:30 | 607 | 598
2018-08-30 01:00 | 580 | 568
2018-08-30 01:30 | 563 | 548
2018-08-30 02:00 | 538 | 519
2018-08-30 02:30 | 539 | 518
2018-08-30 03:00 | 500 | 476
2018-08-30 03:30 | 484 | 457
2018-08-30 04:00 | 479 | 452
2018-08-30 04:30 | 509 | 486
2018-08-30 05:00 | 514 | 495
2018-08-30 05:30 | 585 | 576
2018-08-30 06:00 | 652 | 649
2018-08-30 06:30 | 743 | 741
2018-08-30 07:00 | 817 | 817
2018-08-30 07:30 | 845 | 845
2018-08-30 08:00 | 821 | 821
2018-08-30 08:30 | 770 | 770
2018-08-30 09:00 | 719 | 719
2018-08-30 09:30 | 678 | 676
2018-08-30 10:00 | 642 | 640
2018-08-30 10:30 | 608 | 608
2018-08-30 11:00 | 598 | 598
2018-08-30 11:30 | 582 | 582
2018-08-30 12:00 | 584 | 584
2018-08-30 12:30 | 583 | 583
2018-08-30 13:00 | 586 | 586
2018-08-30 13:30 | 596 | 596
2018-08-30 14:00 | 615 | 614
2018-08-30 14:30 | 633 | 633
2018-08-30 15:00 | 650 | 650
2018-08-30 15:30 | 670 | 670
2018-08-30 16:00 | 715 | 715
2018-08-30 16:30 | 757 | 757
2018-08-30 17:00 | 786 | 786
2018-08-30 17:30 | 828 | 828
2018-08-30 18:00 | 888 | 888
2018-08-30 18:30 | 935 | 931
2018-08-30 19:00 | 938 | 933
2018-08-30 19:30 | 921 | 915
2018-08-30 20:00 | 922 | 918
2018-08-30 20:30 | 910 | 905
2018-08-30 21:00 | 868 | 866
2018-08-30 21:30 | 813 | 812
2018-08-30 22:00 | 767 | 767
2018-08-30 22:30 | 746 | 745
2018-08-30 23:00 | 734 | 732
2018-08-30 23:30 | 691 | 688
2018-08-31 | 643 | 636
2018-08-31 00:30 | 599 | 585
2018-08-31 01:00 | 571 | 555
2018-08-31 01:30 | 552 | 532
2018-08-31 02:00 | 536 | 515
2018-08-31 02:30 | 528 | 506
2018-08-31 03:00 | 526 | 502
2018-08-31 03:30 | 524 | 501
2018-08-31 04:00 | 526 | 502
2018-08-31 04:30 | 535 | 512
2018-08-31 05:00 | 550 | 530
2018-08-31 05:30 | 561 | 546
2018-08-31 06:00 | 609 | 599
2018-08-31 06:30 | 672 | 668
2018-08-31 07:00 | 716 | 714
2018-08-31 07:30 | 760 | 757
2018-08-31 08:00 | 763 | 758
2018-08-31 08:30 | 728 | 722
2018-08-31 09:00 | 683 | 682
2018-08-31 09:30 | 656 | 656
2018-08-31 10:00 | 630 | 629
2018-08-31 10:30 | 607 | 606
2018-08-31 11:00 | 590 | 589
2018-08-31 11:30 | 587 | 586
2018-08-31 12:00 | 574 | 573
2018-08-31 12:30 | 562 | 561
2018-08-31 13:00 | 555 | 555
2018-08-31 13:30 | 558 | 558
2018-08-31 14:00 | 572 | 572
2018-08-31 14:30 | 592 | 592
2018-08-31 15:00 | 617 | 617
2018-08-31 15:30 | 642 | 642
2018-08-31 16:00 | 673 | 673
2018-08-31 16:30 | 726 | 726
2018-08-31 17:00 | 769 | 769
2018-08-31 17:30 | 800 | 800
2018-08-31 18:00 | 828 | 828
2018-08-31 18:30 | 854 | 853
2018-08-31 19:00 | 853 | 852
2018-08-31 19:30 | 838 | 837
2018-08-31 20:00 | 829 | 827
2018-08-31 20:30 | 825 | 822
2018-08-31 21:00 | 809 | 806
2018-08-31 21:30 | 763 | 761
2018-08-31 22:00 | 730 | 729
2018-08-31 22:30 | 722 | 720
2018-08-31 23:00 | 736 | 734
2018-08-31 23:30 | 702 | 700
2018-09-01 | 656 | 651
2018-09-01 00:30 | 588 | 575
2018-09-01 01:00 | 564 | 546
2018-09-01 01:30 | 545 | 523
2018-09-01 02:00 | 530 | 504
2018-09-01 02:30 | 527 | 497
2018-09-01 03:00 | 517 | 485
2018-09-01 03:30 | 520 | 484
2018-09-01 04:00 | 517 | 481
2018-09-01 04:30 | 522 | 487
2018-09-01 05:00 | 528 | 495
2018-09-01 05:30 | 536 | 507
2018-09-01 06:00 | 548 | 523
2018-09-01 06:30 | 567 | 544
2018-09-01 07:00 | 577 | 558
2018-09-01 07:30 | 590 | 576
2018-09-01 08:00 | 596 | 586
2018-09-01 08:30 | 617 | 611
2018-09-01 09:00 | 622 | 618
2018-09-01 09:30 | 599 | 595
2018-09-01 10:00 | 573 | 568
2018-09-01 10:30 | 562 | 557
2018-09-01 11:00 | 572 | 566
2018-09-01 11:30 | 529 | 519
2018-09-01 12:00 | 504 | 492
2018-09-01 12:30 | 494 | 481
2018-09-01 13:00 | 494 | 481
2018-09-01 13:30 | 444 | 427
2018-09-01 14:00 | 482 | 468
2018-09-01 14:30 | 491 | 476
2018-09-01 15:00 | 559 | 550
2018-09-01 15:30 | 590 | 582
2018-09-01 16:00 | 614 | 607
2018-09-01 16:30 | 651 | 647
2018-09-01 17:00 | 691 | 689
2018-09-01 17:30 | 711 | 710
2018-09-01 18:00 | 746 | 745
2018-09-01 18:30 | 782 | 781
2018-09-01 19:00 | 791 | 790
2018-09-01 19:30 | 766 | 763
2018-09-01 20:00 | 756 | 755
2018-09-01 20:30 | 753 | 752
2018-09-01 21:00 | 729 | 728
2018-09-01 21:30 | 703 | 701
2018-09-01 22:00 | 692 | 689
2018-09-01 22:30 | 678 | 672
2018-09-01 23:00 | 680 | 675
2018-09-01 23:30 | 651 | 643
2018-09-02 | 611 | 599
2018-09-02 00:30 | 572 | 553
2018-09-02 01:00 | 555 | 530
2018-09-02 01:30 | 534 | 506
2018-09-02 02:00 | 517 | 483
2018-09-02 02:30 | 510 | 471
2018-09-02 03:00 | 509 | 469
2018-09-02 03:30 | 506 | 466
2018-09-02 04:00 | 503 | 463
2018-09-02 04:30 | 505 | 466
2018-09-02 05:00 | 507 | 468
2018-09-02 05:30 | 516 | 480
2018-09-02 06:00 | 527 | 493
2018-09-02 06:30 | 543 | 506
2018-09-02 07:00 | 553 | 520
2018-09-02 07:30 | 561 | 534
2018-09-02 08:00 | 565 | 542
2018-09-02 08:30 | 566 | 548
2018-09-02 09:00 | 561 | 546
2018-09-02 09:30 | 551 | 538
2018-09-02 10:00 | 536 | 524
2018-09-02 10:30 | 516 | 503
2018-09-02 11:00 | 499 | 485
2018-09-02 11:30 | 485 | 469
2018-09-02 12:00 | 478 | 462
2018-09-02 12:30 | 467 | 449
2018-09-02 13:00 | 468 | 449
2018-09-02 13:30 | 474 | 457
2018-09-02 14:00 | 481 | 465
2018-09-02 14:30 | 501 | 485
2018-09-02 15:00 | 528 | 513
2018-09-02 15:30 | 562 | 550
2018-09-02 16:00 | 592 | 583
2018-09-02 16:30 | 639 | 632
2018-09-02 17:00 | 676 | 671
2018-09-02 17:30 | 716 | 712
2018-09-02 18:00 | 766 | 765
2018-09-02 18:30 | 806 | 806
2018-09-02 19:00 | 816 | 815
2018-09-02 19:30 | 800 | 797
2018-09-02 20:00 | 785 | 784
2018-09-02 20:30 | 775 | 774
2018-09-02 21:00 | 743 | 741
2018-09-02 21:30 | 714 | 711
2018-09-02 22:00 | 689 | 685
2018-09-02 22:30 | 670 | 664
2018-09-02 23:00 | 668 | 661
2018-09-02 23:30 | 634 | 624
2018-09-03 | 603 | 589
2018-09-03 00:30 | 567 | 547
2018-09-03 01:00 | 545 | 519
2018-09-03 01:30 | 532 | 501
2018-09-03 02:00 | 521 | 483
2018-09-03 02:30 | 513 | 475
2018-09-03 03:00 | 508 | 470
2018-09-03 03:30 | 508 | 471
2018-09-03 04:00 | 509 | 472
2018-09-03 04:30 | 521 | 487
2018-09-03 05:00 | 533 | 502
2018-09-03 05:30 | 567 | 546
2018-09-03 06:00 | 607 | 594
2018-09-03 06:30 | 671 | 665
2018-09-03 07:00 | 740 | 739
2018-09-03 07:30 | 796 | 793
2018-09-03 08:00 | 796 | 793
2018-09-03 08:30 | 805 | 803
2018-09-03 09:00 | 768 | 765
2018-09-03 09:30 | 733 | 732
2018-09-03 10:00 | 710 | 710
2018-09-03 10:30 | 691 | 690
2018-09-03 11:00 | 699 | 699
2018-09-03 11:30 | 707 | 707
2018-09-03 12:00 | 707 | 707
2018-09-03 12:30 | 705 | 704
2018-09-03 13:00 | 703 | 703
2018-09-03 13:30 | 692 | 691
2018-09-03 14:00 | 704 | 703
2018-09-03 14:30 | 720 | 720
2018-09-03 15:00 | 720 | 719
2018-09-03 15:30 | 751 | 751
2018-09-03 16:00 | 768 | 768
2018-09-03 16:30 | 781 | 781
2018-09-03 17:00 | 854 | 854
2018-09-03 17:30 | 897 | 897
2018-09-03 18:00 | 956 | 956
2018-09-03 18:30 | 974 | 973
2018-09-03 19:00 | 979 | 976
2018-09-03 19:30 | 949 | 944
2018-09-03 20:00 | 884 | 884
2018-09-03 20:30 | 873 | 873
2018-09-03 21:00 | 878 | 878
2018-09-03 21:30 | 821 | 821
2018-09-03 22:00 | 772 | 772
2018-09-03 22:30 | 742 | 741
2018-09-03 23:00 | 730 | 728
2018-09-03 23:30 | 687 | 682
2018-09-04 | 639 | 629
2018-09-04 00:30 | 594 | 579
2018-09-04 01:00 | 569 | 550
2018-09-04 01:30 | 549 | 527
2018-09-04 02:00 | 535 | 508
2018-09-04 02:30 | 529 | 499
2018-09-04 03:00 | 528 | 497
2018-09-04 03:30 | 523 | 492
2018-09-04 04:00 | 528 | 497
2018-09-04 04:30 | 538 | 510
2018-09-04 05:00 | 553 | 530
2018-09-04 05:30 | 587 | 573
2018-09-04 06:00 | 630 | 623
2018-09-04 06:30 | 728 | 725
2018-09-04 07:00 | 800 | 798
2018-09-04 07:30 | 847 | 846
2018-09-04 08:00 | 853 | 852
2018-09-04 08:30 | 837 | 835
2018-09-04 09:00 | 798 | 795
2018-09-04 09:30 | 775 | 771
2018-09-04 10:00 | 732 | 728
2018-09-04 10:30 | 681 | 676
2018-09-04 11:00 | 677 | 671
2018-09-04 11:30 | 656 | 649
2018-09-04 12:00 | 644 | 642
2018-09-04 12:30 | 671 | 669
2018-09-04 13:00 | 659 | 657
2018-09-04 13:30 | 641 | 639
2018-09-04 14:00 | 671 | 670
2018-09-04 14:30 | 681 | 680
2018-09-04 15:00 | 680 | 679
2018-09-04 15:30 | 710 | 708
2018-09-04 16:00 | 763 | 763
2018-09-04 16:30 | 826 | 826
2018-09-04 17:00 | 878 | 877
2018-09-04 17:30 | 931 | 930
2018-09-04 18:00 | 991 | 990
2018-09-04 18:30 | 1008 | 1007
2018-09-04 19:00 | 1008 | 1007
2018-09-04 19:30 | 982 | 982
2018-09-04 20:00 | 957 | 957
2018-09-04 20:30 | 938 | 937
2018-09-04 21:00 | 903 | 902
2018-09-04 21:30 | 847 | 846
2018-09-04 22:00 | 796 | 792
2018-09-04 22:30 | 756 | 755
2018-09-04 23:00 | 735 | 732
2018-09-04 23:30 | 693 | 689
2018-09-05 | 647 | 639
2018-09-05 00:30 | 597 | 584
2018-09-05 01:00 | 577 | 559
2018-09-05 01:30 | 555 | 536
2018-09-05 02:00 | 540 | 515
2018-09-05 02:30 | 536 | 507
2018-09-05 03:00 | 528 | 496
2018-09-05 03:30 | 530 | 499
2018-09-05 04:00 | 528 | 499
2018-09-05 04:30 | 542 | 515
2018-09-05 05:00 | 556 | 534
2018-09-05 05:30 | 592 | 578
2018-09-05 06:00 | 642 | 635
2018-09-05 06:30 | 727 | 725
2018-09-05 07:00 | 803 | 801
2018-09-05 07:30 | 853 | 850
2018-09-05 08:00 | 858 | 850
2018-09-05 08:30 | 772 | 762
2018-09-05 09:00 | 613 | 609
2018-09-05 09:30 | 576 | 573
2018-09-05 10:00 | 558 | 554
2018-09-05 10:30 | 546 | 544
2018-09-05 11:00 | 529 | 529
2018-09-05 11:30 | 519 | 518
2018-09-05 12:00 | 513 | 512
2018-09-05 12:30 | 498 | 496
2018-09-05 13:00 | 515 | 514
2018-09-05 13:30 | 527 | 527
2018-09-05 14:00 | 558 | 558
2018-09-05 14:30 | 587 | 587
2018-09-05 15:00 | 581 | 580
2018-09-05 15:30 | 581 | 580
2018-09-05 16:00 | 616 | 616
2018-09-05 16:30 | 632 | 632
2018-09-05 17:00 | 692 | 692
2018-09-05 17:30 | 740 | 740
2018-09-05 18:00 | 789 | 788
2018-09-05 18:30 | 811 | 811
2018-09-05 19:00 | 813 | 810
2018-09-05 19:30 | 804 | 799
2018-09-05 20:00 | 798 | 795
2018-09-05 20:30 | 771 | 771
2018-09-05 21:00 | 722 | 719
2018-09-05 21:30 | 681 | 680
2018-09-05 22:00 | 650 | 650
2018-09-05 22:30 | 607 | 607
2018-09-05 23:00 | 574 | 573
2018-09-05 23:30 | 558 | 557
2018-09-06 | 509 | 505
2018-09-06 00:30 | 471 | 461
2018-09-06 01:00 | 452 | 439
2018-09-06 01:30 | 433 | 417
2018-09-06 02:00 | 431 | 413
2018-09-06 02:30 | 414 | 393
2018-09-06 03:00 | 410 | 391
2018-09-06 03:30 | 406 | 387
2018-09-06 04:00 | 406 | 389
2018-09-06 04:30 | 426 | 410
2018-09-06 05:00 | 438 | 427
2018-09-06 05:30 | 484 | 478
2018-09-06 06:00 | 508 | 505
2018-09-06 06:30 | 570 | 569
2018-09-06 07:00 | 640 | 640
2018-09-06 07:30 | 690 | 686
2018-09-06 08:00 | 685 | 680
2018-09-06 08:30 | 645 | 640
2018-09-06 09:00 | 573 | 569
2018-09-06 09:30 | 569 | 566
2018-09-06 10:00 | 565 | 563
2018-09-06 10:30 | 541 | 540
2018-09-06 11:00 | 534 | 533
2018-09-06 11:30 | 529 | 529
2018-09-06 12:00 | 537 | 537
2018-09-06 12:30 | 529 | 528
2018-09-06 13:00 | 520 | 519
2018-09-06 13:30 | 488 | 488
2018-09-06 14:00 | 524 | 524
2018-09-06 14:30 | 510 | 510
2018-09-06 15:00 | 543 | 542
2018-09-06 15:30 | 581 | 580
2018-09-06 16:00 | 606 | 606
2018-09-06 16:30 | 632 | 631
2018-09-06 17:00 | 648 | 648
2018-09-06 17:30 | 724 | 722
2018-09-06 18:00 | 768 | 767
2018-09-06 18:30 | 802 | 797
2018-09-06 19:00 | 815 | 810
2018-09-06 19:30 | 801 | 796
2018-09-06 20:00 | 785 | 781
2018-09-06 20:30 | 787 | 785
2018-09-06 21:00 | 743 | 742
2018-09-06 21:30 | 687 | 685
2018-09-06 22:00 | 647 | 647
2018-09-06 22:30 | 629 | 629
2018-09-06 23:00 | 631 | 630
2018-09-06 23:30 | 570 | 568
2018-09-07 | 509 | 503
2018-09-07 00:30 | 467 | 457
2018-09-07 01:00 | 446 | 433
2018-09-07 01:30 | 424 | 409
2018-09-07 02:00 | 391 | 369
2018-09-07 02:30 | 409 | 388
2018-09-07 03:00 | 378 | 351
2018-09-07 03:30 | 377 | 351
2018-09-07 04:00 | 392 | 368
2018-09-07 04:30 | 428 | 410
2018-09-07 05:00 | 448 | 433
2018-09-07 05:30 | 484 | 475
2018-09-07 06:00 | 519 | 514
2018-09-07 06:30 | 582 | 579
2018-09-07 07:00 | 621 | 619
2018-09-07 07:30 | 640 | 640
2018-09-07 08:00 | 631 | 631
2018-09-07 08:30 | 657 | 656
2018-09-07 09:00 | 631 | 630
2018-09-07 09:30 | 619 | 619
2018-09-07 10:00 | 588 | 588
2018-09-07 10:30 | 519 | 519
2018-09-07 11:00 | 507 | 507
2018-09-07 11:30 | 510 | 510
2018-09-07 12:00 | 508 | 508
2018-09-07 12:30 | 503 | 503
2018-09-07 13:00 | 492 | 492
2018-09-07 13:30 | 461 | 461
2018-09-07 14:00 | 465 | 465
2018-09-07 14:30 | 477 | 477
2018-09-07 15:00 | 503 | 503
2018-09-07 15:30 | 543 | 542
2018-09-07 16:00 | 591 | 590
2018-09-07 16:30 | 602 | 602
2018-09-07 17:00 | 650 | 650
2018-09-07 17:30 | 683 | 683
2018-09-07 18:00 | 695 | 693
2018-09-07 18:30 | 699 | 699
2018-09-07 19:00 | 707 | 706
2018-09-07 19:30 | 703 | 702
2018-09-07 20:00 | 685 | 683
2018-09-07 20:30 | 682 | 681
2018-09-07 21:00 | 655 | 655
2018-09-07 21:30 | 619 | 619
2018-09-07 22:00 | 585 | 584
2018-09-07 22:30 | 633 | 633
2018-09-07 23:00 | 653 | 653
2018-09-07 23:30 | 619 | 619
2018-09-08 | 586 | 584
2018-09-08 00:30 | 547 | 542
2018-09-08 01:00 | 524 | 517
2018-09-08 01:30 | 517 | 508
2018-09-08 02:00 | 501 | 488
2018-09-08 02:30 | 488 | 473
2018-09-08 03:00 | 484 | 467
2018-09-08 03:30 | 484 | 467
2018-09-08 04:00 | 479 | 462
2018-09-08 04:30 | 484 | 467
2018-09-08 05:00 | 493 | 477
2018-09-08 05:30 | 499 | 485
2018-09-08 06:00 | 512 | 500
2018-09-08 06:30 | 526 | 514
2018-09-08 07:00 | 553 | 546
2018-09-08 07:30 | 589 | 587
2018-09-08 08:00 | 613 | 613
2018-09-08 08:30 | 635 | 635
2018-09-08 09:00 | 592 | 592
2018-09-08 09:30 | 578 | 577
2018-09-08 10:00 | 576 | 576
2018-09-08 10:30 | 602 | 601
2018-09-08 11:00 | 579 | 578
2018-09-08 11:30 | 522 | 520
2018-09-08 12:00 | 483 | 483
2018-09-08 12:30 | 466 | 465
2018-09-08 13:00 | 490 | 489
2018-09-08 13:30 | 599 | 597
2018-09-08 14:00 | 635 | 634
2018-09-08 14:30 | 633 | 632
2018-09-08 15:00 | 654 | 652
2018-09-08 15:30 | 672 | 671
2018-09-08 16:00 | 683 | 682
2018-09-08 16:30 | 721 | 720
2018-09-08 17:00 | 749 | 749
2018-09-08 17:30 | 768 | 766
2018-09-08 18:00 | 794 | 793
2018-09-08 18:30 | 825 | 824
2018-09-08 19:00 | 828 | 825
2018-09-08 19:30 | 811 | 807
2018-09-08 20:00 | 798 | 796
2018-09-08 20:30 | 795 | 794
2018-09-08 21:00 | 753 | 752
2018-09-08 21:30 | 720 | 720
2018-09-08 22:00 | 702 | 701
2018-09-08 22:30 | 697 | 695
2018-09-08 23:00 | 702 | 699
2018-09-08 23:30 | 670 | 666
2018-09-09 | 628 | 621
2018-09-09 00:30 | 583 | 573
2018-09-09 01:00 | 556 | 541
2018-09-09 01:30 | 541 | 520
2018-09-09 02:00 | 525 | 500
2018-09-09 02:30 | 526 | 496
2018-09-09 03:00 | 520 | 488
2018-09-09 03:30 | 516 | 483
2018-09-09 04:00 | 514 | 482
2018-09-09 04:30 | 517 | 485
2018-09-09 05:00 | 517 | 486
2018-09-09 05:30 | 479 | 444
2018-09-09 06:00 | 482 | 445
2018-09-09 06:30 | 509 | 473
2018-09-09 07:00 | 525 | 494
2018-09-09 07:30 | 511 | 484
2018-09-09 08:00 | 541 | 521
2018-09-09 08:30 | 516 | 496
2018-09-09 09:00 | 552 | 539
2018-09-09 09:30 | 548 | 538
2018-09-09 10:00 | 539 | 530
2018-09-09 10:30 | 531 | 522
2018-09-09 11:00 | 508 | 498
2018-09-09 11:30 | 501 | 491
2018-09-09 12:00 | 441 | 426
2018-09-09 12:30 | 477 | 463
2018-09-09 13:00 | 488 | 475
2018-09-09 13:30 | 477 | 464
2018-09-09 14:00 | 494 | 481
2018-09-09 14:30 | 483 | 469
2018-09-09 15:00 | 544 | 533
2018-09-09 15:30 | 574 | 564
2018-09-09 16:00 | 610 | 603
2018-09-09 16:30 | 660 | 654
2018-09-09 17:00 | 702 | 699
2018-09-09 17:30 | 736 | 735
2018-09-09 18:00 | 781 | 781
2018-09-09 18:30 | 825 | 824
2018-09-09 19:00 | 829 | 828
2018-09-09 19:30 | 810 | 809
2018-09-09 20:00 | 794 | 793
2018-09-09 20:30 | 782 | 782
2018-09-09 21:00 | 755 | 753
2018-09-09 21:30 | 723 | 721
2018-09-09 22:00 | 703 | 699
2018-09-09 22:30 | 687 | 682
2018-09-09 23:00 | 681 | 675
2018-09-09 23:30 | 659 | 652
2018-09-10 | 617 | 606
2018-09-10 00:30 | 577 | 559
2018-09-10 01:00 | 552 | 530
2018-09-10 01:30 | 540 | 514
2018-09-10 02:00 | 524 | 496
2018-09-10 02:30 | 519 | 488
2018-09-10 03:00 | 515 | 483
2018-09-10 03:30 | 515 | 483
2018-09-10 04:00 | 521 | 489
2018-09-10 04:30 | 536 | 507
2018-09-10 05:00 | 547 | 524
2018-09-10 05:30 | 584 | 570
2018-09-10 06:00 | 625 | 617
2018-09-10 06:30 | 699 | 692
2018-09-10 07:00 | 756 | 749
2018-09-10 07:30 | 790 | 783
2018-09-10 08:00 | 772 | 763
2018-09-10 08:30 | 736 | 728
2018-09-10 09:00 | 693 | 683
2018-09-10 09:30 | 659 | 656
2018-09-10 10:00 | 632 | 630
2018-09-10 10:30 | 617 | 615
2018-09-10 11:00 | 605 | 603
2018-09-10 11:30 | 588 | 586
2018-09-10 12:00 | 586 | 585
2018-09-10 12:30 | 586 | 585
2018-09-10 13:00 | 591 | 590
2018-09-10 13:30 | 594 | 594
2018-09-10 14:00 | 609 | 608
2018-09-10 14:30 | 632 | 632
2018-09-10 15:00 | 653 | 653
2018-09-10 15:30 | 678 | 677
2018-09-10 16:00 | 714 | 714
2018-09-10 16:30 | 760 | 759
2018-09-10 17:00 | 809 | 807
2018-09-10 17:30 | 851 | 849
2018-09-10 18:00 | 898 | 897
2018-09-10 18:30 | 917 | 916
2018-09-10 19:00 | 917 | 915
2018-09-10 19:30 | 933 | 931
2018-09-10 20:00 | 893 | 891
2018-09-10 20:30 | 859 | 858
2018-09-10 21:00 | 814 | 814
2018-09-10 21:30 | 778 | 777
2018-09-10 22:00 | 751 | 749
2018-09-10 22:30 | 730 | 726
2018-09-10 23:00 | 710 | 709
2018-09-10 23:30 | 686 | 683
2018-09-11 | 636 | 632
2018-09-11 00:30 | 588 | 576
2018-09-11 01:00 | 562 | 546
2018-09-11 01:30 | 548 | 528
2018-09-11 02:00 | 535 | 513
2018-09-11 02:30 | 525 | 501
2018-09-11 03:00 | 508 | 482
2018-09-11 03:30 | 527 | 502
2018-09-11 04:00 | 495 | 466
2018-09-11 04:30 | 526 | 500
2018-09-11 05:00 | 537 | 517
2018-09-11 05:30 | 577 | 564
2018-09-11 06:00 | 634 | 627
2018-09-11 06:30 | 697 | 694
2018-09-11 07:00 | 748 | 748
2018-09-11 07:30 | 788 | 785
2018-09-11 08:00 | 777 | 773
2018-09-11 08:30 | 736 | 732
2018-09-11 09:00 | 704 | 697
2018-09-11 09:30 | 678 | 670
2018-09-11 10:00 | 642 | 641
2018-09-11 10:30 | 625 | 624
2018-09-11 11:00 | 624 | 624
2018-09-11 11:30 | 619 | 618
2018-09-11 12:00 | 620 | 619
2018-09-11 12:30 | 614 | 613
2018-09-11 13:00 | 628 | 627
2018-09-11 13:30 | 644 | 644
2018-09-11 14:00 | 659 | 659
2018-09-11 14:30 | 673 | 673
2018-09-11 15:00 | 674 | 674
2018-09-11 15:30 | 691 | 691
2018-09-11 16:00 | 726 | 726
2018-09-11 16:30 | 761 | 759
2018-09-11 17:00 | 807 | 804
2018-09-11 17:30 | 848 | 846
2018-09-11 18:00 | 883 | 883
2018-09-11 18:30 | 908 | 908
2018-09-11 19:00 | 907 | 906
2018-09-11 19:30 | 889 | 888
2018-09-11 20:00 | 873 | 871
2018-09-11 20:30 | 868 | 866
2018-09-11 21:00 | 825 | 822
2018-09-11 21:30 | 773 | 772
2018-09-11 22:00 | 750 | 749
2018-09-11 22:30 | 716 | 714
2018-09-11 23:00 | 705 | 703
2018-09-11 23:30 | 678 | 673
2018-09-12 | 631 | 623
2018-09-12 00:30 | 590 | 577
2018-09-12 01:00 | 560 | 543
2018-09-12 01:30 | 548 | 528
2018-09-12 02:00 | 538 | 516
2018-09-12 02:30 | 507 | 482
2018-09-12 03:00 | 526 | 501
2018-09-12 03:30 | 527 | 502
2018-09-12 04:00 | 529 | 502
2018-09-12 04:30 | 543 | 518
2018-09-12 05:00 | 556 | 535
2018-09-12 05:30 | 590 | 578
2018-09-12 06:00 | 630 | 622
2018-09-12 06:30 | 689 | 685
2018-09-12 07:00 | 739 | 734
2018-09-12 07:30 | 718 | 713
2018-09-12 08:00 | 665 | 662
2018-09-12 08:30 | 641 | 639
2018-09-12 09:00 | 627 | 625
2018-09-12 09:30 | 603 | 600
2018-09-12 10:00 | 596 | 596
2018-09-12 10:30 | 591 | 591
2018-09-12 11:00 | 574 | 574
2018-09-12 11:30 | 542 | 542
2018-09-12 12:00 | 546 | 546
2018-09-12 12:30 | 549 | 549
2018-09-12 13:00 | 542 | 542
2018-09-12 13:30 | 545 | 545
2018-09-12 14:00 | 557 | 557
2018-09-12 14:30 | 568 | 568
2018-09-12 15:00 | 578 | 578
2018-09-12 15:30 | 596 | 596
2018-09-12 16:00 | 625 | 625
2018-09-12 16:30 | 667 | 667
2018-09-12 17:00 | 704 | 703
2018-09-12 17:30 | 740 | 738
2018-09-12 18:00 | 769 | 768
2018-09-12 18:30 | 803 | 801
2018-09-12 19:00 | 805 | 803
2018-09-12 19:30 | 794 | 789
2018-09-12 20:00 | 781 | 775
2018-09-12 20:30 | 759 | 757
2018-09-12 21:00 | 726 | 725
2018-09-12 21:30 | 694 | 692
2018-09-12 22:00 | 665 | 662
2018-09-12 22:30 | 646 | 644
2018-09-12 23:00 | 634 | 633
2018-09-12 23:30 | 595 | 593
2018-09-13 | 558 | 553
2018-09-13 00:30 | 515 | 504
2018-09-13 01:00 | 492 | 479
2018-09-13 01:30 | 478 | 463
2018-09-13 02:00 | 456 | 438
2018-09-13 02:30 | 430 | 404
2018-09-13 03:00 | 425 | 398
2018-09-13 03:30 | 464 | 440
2018-09-13 04:00 | 465 | 441
2018-09-13 04:30 | 475 | 453
2018-09-13 05:00 | 483 | 465
2018-09-13 05:30 | 514 | 501
2018-09-13 06:00 | 527 | 517
2018-09-13 06:30 | 598 | 591
2018-09-13 07:00 | 658 | 649
2018-09-13 07:30 | 682 | 675
2018-09-13 08:00 | 678 | 666
2018-09-13 08:30 | 651 | 638
2018-09-13 09:00 | 621 | 606
2018-09-13 09:30 | 586 | 579
2018-09-13 10:00 | 568 | 563
2018-09-13 10:30 | 556 | 551
2018-09-13 11:00 | 542 | 536
2018-09-13 11:30 | 535 | 533
2018-09-13 12:00 | 535 | 533
2018-09-13 12:30 | 537 | 535
2018-09-13 13:00 | 538 | 536
2018-09-13 13:30 | 547 | 546
2018-09-13 14:00 | 560 | 559
2018-09-13 14:30 | 579 | 578
2018-09-13 15:00 | 593 | 592
2018-09-13 15:30 | 613 | 612
2018-09-13 16:00 | 646 | 645
2018-09-13 16:30 | 686 | 682
2018-09-13 17:00 | 720 | 717
2018-09-13 17:30 | 743 | 740
2018-09-13 18:00 | 775 | 772
2018-09-13 18:30 | 809 | 804
2018-09-13 19:00 | 806 | 801
2018-09-13 19:30 | 785 | 781
2018-09-13 20:00 | 781 | 777
2018-09-13 20:30 | 766 | 763
2018-09-13 21:00 | 736 | 733
2018-09-13 21:30 | 696 | 691
2018-09-13 22:00 | 666 | 657
2018-09-13 22:30 | 644 | 637
2018-09-13 23:00 | 634 | 626
2018-09-13 23:30 | 595 | 591
2018-09-14 | 557 | 550
2018-09-14 00:30 | 518 | 505
2018-09-14 01:00 | 496 | 480
2018-09-14 01:30 | 484 | 465
2018-09-14 02:00 | 471 | 450
2018-09-14 02:30 | 469 | 448
2018-09-14 03:00 | 468 | 445
2018-09-14 03:30 | 466 | 443
2018-09-14 04:00 | 478 | 457
2018-09-14 04:30 | 475 | 454
2018-09-14 05:00 | 469 | 449
2018-09-14 05:30 | 514 | 501
2018-09-14 06:00 | 535 | 524
2018-09-14 06:30 | 579 | 573
2018-09-14 07:00 | 621 | 619
2018-09-14 07:30 | 644 | 640
2018-09-14 08:00 | 632 | 626
2018-09-14 08:30 | 628 | 623
2018-09-14 09:00 | 671 | 665
2018-09-14 09:30 | 690 | 687
2018-09-14 10:00 | 672 | 669
2018-09-14 10:30 | 641 | 638
2018-09-14 11:00 | 610 | 607
2018-09-14 11:30 | 590 | 586
2018-09-14 12:00 | 540 | 535
2018-09-14 12:30 | 566 | 562
2018-09-14 13:00 | 572 | 568
2018-09-14 13:30 | 560 | 556
2018-09-14 14:00 | 591 | 588
2018-09-14 14:30 | 607 | 603
2018-09-14 15:00 | 632 | 629
2018-09-14 15:30 | 668 | 666
2018-09-14 16:00 | 692 | 689
2018-09-14 16:30 | 729 | 727
2018-09-14 17:00 | 790 | 788
2018-09-14 17:30 | 819 | 818
2018-09-14 18:00 | 819 | 817
2018-09-14 18:30 | 840 | 837
2018-09-14 19:00 | 854 | 850
2018-09-14 19:30 | 827 | 823
2018-09-14 20:00 | 819 | 817
2018-09-14 20:30 | 809 | 807
2018-09-14 21:00 | 771 | 771
2018-09-14 21:30 | 742 | 742
2018-09-14 22:00 | 722 | 721
2018-09-14 22:30 | 707 | 705
2018-09-14 23:00 | 706 | 704
2018-09-14 23:30 | 674 | 670
2018-09-15 | 621 | 613
2018-09-15 00:30 | 588 | 576
2018-09-15 01:00 | 563 | 546
2018-09-15 01:30 | 551 | 533
2018-09-15 02:00 | 488 | 460
2018-09-15 02:30 | 472 | 442
2018-09-15 03:00 | 473 | 441
2018-09-15 03:30 | 479 | 448
2018-09-15 04:00 | 475 | 443
2018-09-15 04:30 | 460 | 428
2018-09-15 05:00 | 469 | 439
2018-09-15 05:30 | 515 | 492
2018-09-15 06:00 | 495 | 467
2018-09-15 06:30 | 522 | 498
2018-09-15 07:00 | 539 | 520
2018-09-15 07:30 | 540 | 526
2018-09-15 08:00 | 559 | 551
2018-09-15 08:30 | 582 | 577
2018-09-15 09:00 | 579 | 575
2018-09-15 09:30 | 567 | 564
2018-09-15 10:00 | 550 | 548
2018-09-15 10:30 | 492 | 488
2018-09-15 11:00 | 522 | 519
2018-09-15 11:30 | 462 | 458
2018-09-15 12:00 | 457 | 453
2018-09-15 12:30 | 451 | 446
2018-09-15 13:00 | 466 | 462
2018-09-15 13:30 | 438 | 433
2018-09-15 14:00 | 503 | 500
2018-09-15 14:30 | 525 | 522
2018-09-15 15:00 | 508 | 504
2018-09-15 15:30 | 554 | 551
2018-09-15 16:00 | 630 | 629
2018-09-15 16:30 | 663 | 663
2018-09-15 17:00 | 701 | 701
2018-09-15 17:30 | 721 | 721
2018-09-15 18:00 | 746 | 746
2018-09-15 18:30 | 781 | 780
2018-09-15 19:00 | 791 | 791
2018-09-15 19:30 | 770 | 769
2018-09-15 20:00 | 755 | 754
2018-09-15 20:30 | 744 | 744
2018-09-15 21:00 | 714 | 713
2018-09-15 21:30 | 698 | 696
2018-09-15 22:00 | 679 | 677
2018-09-15 22:30 | 684 | 681
2018-09-15 23:00 | 684 | 681
2018-09-15 23:30 | 649 | 643
2018-09-16 | 605 | 596
2018-09-16 00:30 | 563 | 548
2018-09-16 01:00 | 547 | 527
2018-09-16 01:30 | 530 | 508
2018-09-16 02:00 | 499 | 471
2018-09-16 02:30 | 491 | 461
2018-09-16 03:00 | 478 | 442
2018-09-16 03:30 | 465 | 431
2018-09-16 04:00 | 468 | 433
2018-09-16 04:30 | 497 | 467
2018-09-16 05:00 | 464 | 431
2018-09-16 05:30 | 457 | 424
2018-09-16 06:00 | 490 | 454
2018-09-16 06:30 | 517 | 483
2018-09-16 07:00 | 524 | 497
2018-09-16 07:30 | 504 | 480
2018-09-16 08:00 | 515 | 497
2018-09-16 08:30 | 552 | 543
2018-09-16 09:00 | 535 | 528
2018-09-16 09:30 | 541 | 533
2018-09-16 10:00 | 562 | 557
2018-09-16 10:30 | 571 | 568
2018-09-16 11:00 | 531 | 527
2018-09-16 11:30 | 495 | 489
2018-09-16 12:00 | 443 | 433
2018-09-16 12:30 | 441 | 432
2018-09-16 13:00 | 464 | 455
2018-09-16 13:30 | 480 | 472
2018-09-16 14:00 | 516 | 509
2018-09-16 14:30 | 497 | 488
2018-09-16 15:00 | 541 | 534
2018-09-16 15:30 | 548 | 541
2018-09-16 16:00 | 602 | 597
2018-09-16 16:30 | 634 | 631
2018-09-16 17:00 | 663 | 660
2018-09-16 17:30 | 705 | 705
2018-09-16 18:00 | 760 | 759
2018-09-16 18:30 | 814 | 814
2018-09-16 19:00 | 816 | 816
2018-09-16 19:30 | 794 | 793
2018-09-16 20:00 | 782 | 781
2018-09-16 20:30 | 771 | 770
2018-09-16 21:00 | 740 | 740
2018-09-16 21:30 | 698 | 696
2018-09-16 22:00 | 672 | 669
2018-09-16 22:30 | 660 | 656
2018-09-16 23:00 | 654 | 648
2018-09-16 23:30 | 628 | 621
2018-09-17 | 592 | 581
2018-09-17 00:30 | 554 | 535
2018-09-17 01:00 | 534 | 513
2018-09-17 01:30 | 519 | 494
2018-09-17 02:00 | 510 | 483
2018-09-17 02:30 | 504 | 475
2018-09-17 03:00 | 505 | 474
2018-09-17 03:30 | 501 | 470
2018-09-17 04:00 | 501 | 471
2018-09-17 04:30 | 512 | 487
2018-09-17 05:00 | 529 | 506
2018-09-17 05:30 | 557 | 544
2018-09-17 06:00 | 591 | 580
2018-09-17 06:30 | 657 | 647
2018-09-17 07:00 | 665 | 654
2018-09-17 07:30 | 679 | 671
2018-09-17 08:00 | 652 | 645
2018-09-17 08:30 | 608 | 601
2018-09-17 09:00 | 574 | 565
2018-09-17 09:30 | 554 | 544
2018-09-17 10:00 | 534 | 529
2018-09-17 10:30 | 531 | 527
2018-09-17 11:00 | 533 | 529
2018-09-17 11:30 | 533 | 529
2018-09-17 12:00 | 529 | 525
2018-09-17 12:30 | 552 | 549
2018-09-17 13:00 | 563 | 560
2018-09-17 13:30 | 580 | 576
2018-09-17 14:00 | 591 | 588
2018-09-17 14:30 | 613 | 610
2018-09-17 15:00 | 631 | 629
2018-09-17 15:30 | 655 | 653
2018-09-17 16:00 | 690 | 688
2018-09-17 16:30 | 780 | 779
2018-09-17 17:00 | 823 | 820
2018-09-17 17:30 | 865 | 856
2018-09-17 18:00 | 895 | 889
2018-09-17 18:30 | 923 | 919
2018-09-17 19:00 | 934 | 930
2018-09-17 19:30 | 913 | 907
2018-09-17 20:00 | 887 | 886
2018-09-17 20:30 | 864 | 863
2018-09-17 21:00 | 822 | 820
2018-09-17 21:30 | 790 | 789
2018-09-17 22:00 | 758 | 756
2018-09-17 22:30 | 736 | 734
2018-09-17 23:00 | 732 | 730
2018-09-17 23:30 | 701 | 697
2018-09-18 | 652 | 645
2018-09-18 00:30 | 615 | 603
2018-09-18 01:00 | 584 | 568
2018-09-18 01:30 | 566 | 547
2018-09-18 02:00 | 556 | 536
2018-09-18 02:30 | 549 | 527
2018-09-18 03:00 | 542 | 519
2018-09-18 03:30 | 533 | 510
2018-09-18 04:00 | 545 | 520
2018-09-18 04:30 | 562 | 541
2018-09-18 05:00 | 536 | 515
2018-09-18 05:30 | 588 | 574
2018-09-18 06:00 | 648 | 634
2018-09-18 06:30 | 709 | 700
2018-09-18 07:00 | 742 | 737
2018-09-18 07:30 | 763 | 761
2018-09-18 08:00 | 729 | 728
2018-09-18 08:30 | 700 | 699
2018-09-18 09:00 | 687 | 686
2018-09-18 09:30 | 682 | 681
2018-09-18 10:00 | 682 | 681
2018-09-18 10:30 | 683 | 683
2018-09-18 11:00 | 699 | 698
2018-09-18 11:30 | 675 | 675
2018-09-18 12:00 | 649 | 649
2018-09-18 12:30 | 644 | 644
2018-09-18 13:00 | 639 | 638
2018-09-18 13:30 | 622 | 621
2018-09-18 14:00 | 637 | 637
2018-09-18 14:30 | 650 | 650
2018-09-18 15:00 | 658 | 658
2018-09-18 15:30 | 678 | 677
2018-09-18 16:00 | 715 | 714
2018-09-18 16:30 | 753 | 752
2018-09-18 17:00 | 809 | 809
2018-09-18 17:30 | 838 | 838
2018-09-18 18:00 | 860 | 860
2018-09-18 18:30 | 921 | 921
2018-09-18 19:00 | 922 | 921
2018-09-18 19:30 | 897 | 895
2018-09-18 20:00 | 875 | 871
2018-09-18 20:30 | 873 | 869
2018-09-18 21:00 | 821 | 820
2018-09-18 21:30 | 782 | 782
2018-09-18 22:00 | 747 | 747
2018-09-18 22:30 | 721 | 720
2018-09-18 23:00 | 716 | 714
2018-09-18 23:30 | 686 | 682
2018-09-19 | 638 | 629
2018-09-19 00:30 | 598 | 583
2018-09-19 01:00 | 571 | 552
2018-09-19 01:30 | 557 | 535
2018-09-19 02:00 | 541 | 516
2018-09-19 02:30 | 540 | 515
2018-09-19 03:00 | 541 | 514
2018-09-19 03:30 | 546 | 519
2018-09-19 04:00 | 544 | 518
2018-09-19 04:30 | 552 | 527
2018-09-19 05:00 | 566 | 546
2018-09-19 05:30 | 605 | 591
2018-09-19 06:00 | 631 | 620
2018-09-19 06:30 | 683 | 679
2018-09-19 07:00 | 720 | 719
2018-09-19 07:30 | 747 | 747
2018-09-19 08:00 | 732 | 732
2018-09-19 08:30 | 699 | 699
2018-09-19 09:00 | 672 | 671
2018-09-19 09:30 | 653 | 653
2018-09-19 10:00 | 628 | 628
2018-09-19 10:30 | 608 | 608
2018-09-19 11:00 | 594 | 594
2018-09-19 11:30 | 578 | 578
2018-09-19 12:00 | 571 | 571
2018-09-19 12:30 | 564 | 564
2018-09-19 13:00 | 572 | 572
2018-09-19 13:30 | 575 | 575
2018-09-19 14:00 | 586 | 586
2018-09-19 14:30 | 624 | 624
2018-09-19 15:00 | 645 | 645
2018-09-19 15:30 | 673 | 670
2018-09-19 16:00 | 718 | 713
2018-09-19 16:30 | 750 | 747
2018-09-19 17:00 | 799 | 796
2018-09-19 17:30 | 837 | 834
2018-09-19 18:00 | 857 | 855
2018-09-19 18:30 | 900 | 900
2018-09-19 19:00 | 903 | 902
2018-09-19 19:30 | 871 | 869
2018-09-19 20:00 | 854 | 852
2018-09-19 20:30 | 843 | 843
2018-09-19 21:00 | 797 | 797
2018-09-19 21:30 | 760 | 759
2018-09-19 22:00 | 730 | 725
2018-09-19 22:30 | 696 | 696
2018-09-19 23:00 | 691 | 690
2018-09-19 23:30 | 656 | 654
2018-09-20 | 618 | 614
2018-09-20 00:30 | 568 | 560
2018-09-20 01:00 | 547 | 535
2018-09-20 01:30 | 533 | 519
2018-09-20 02:00 | 523 | 508
2018-09-20 02:30 | 517 | 499
2018-09-20 03:00 | 510 | 490
2018-09-20 03:30 | 517 | 497
2018-09-20 04:00 | 518 | 499
2018-09-20 04:30 | 527 | 510
2018-09-20 05:00 | 545 | 529
2018-09-20 05:30 | 571 | 561
2018-09-20 06:00 | 604 | 597
2018-09-20 06:30 | 657 | 654
2018-09-20 07:00 | 701 | 699
2018-09-20 07:30 | 708 | 703
2018-09-20 08:00 | 690 | 686
2018-09-20 08:30 | 663 | 659
2018-09-20 09:00 | 640 | 637
2018-09-20 09:30 | 615 | 612
2018-09-20 10:00 | 631 | 630
2018-09-20 10:30 | 630 | 629
2018-09-20 11:00 | 616 | 616
2018-09-20 11:30 | 617 | 617
2018-09-20 12:00 | 629 | 628
2018-09-20 12:30 | 641 | 641
2018-09-20 13:00 | 654 | 654
2018-09-20 13:30 | 660 | 660
2018-09-20 14:00 | 674 | 673
2018-09-20 14:30 | 642 | 641
2018-09-20 15:00 | 663 | 662
2018-09-20 15:30 | 699 | 698
2018-09-20 16:00 | 722 | 721
2018-09-20 16:30 | 766 | 765
2018-09-20 17:00 | 808 | 807
2018-09-20 17:30 | 842 | 841
2018-09-20 18:00 | 866 | 866
2018-09-20 18:30 | 900 | 899
2018-09-20 19:00 | 910 | 906
2018-09-20 19:30 | 885 | 879
2018-09-20 20:00 | 866 | 862
2018-09-20 20:30 | 845 | 843
2018-09-20 21:00 | 793 | 789
2018-09-20 21:30 | 736 | 732
2018-09-20 22:00 | 749 | 742
2018-09-20 22:30 | 736 | 732
2018-09-20 23:00 | 713 | 711
2018-09-20 23:30 | 674 | 670
2018-09-21 | 627 | 621
2018-09-21 00:30 | 582 | 570
2018-09-21 01:00 | 547 | 532
2018-09-21 01:30 | 534 | 518
2018-09-21 02:00 | 528 | 510
2018-09-21 02:30 | 520 | 501
2018-09-21 03:00 | 517 | 497
2018-09-21 03:30 | 523 | 501
2018-09-21 04:00 | 522 | 502
2018-09-21 04:30 | 528 | 510
2018-09-21 05:00 | 531 | 514
2018-09-21 05:30 | 570 | 558
2018-09-21 06:00 | 612 | 603
2018-09-21 06:30 | 614 | 609
2018-09-21 07:00 | 671 | 670
2018-09-21 07:30 | 725 | 725
2018-09-21 08:00 | 722 | 720
2018-09-21 08:30 | 689 | 687
2018-09-21 09:00 | 640 | 638
2018-09-21 09:30 | 633 | 631
2018-09-21 10:00 | 616 | 615
2018-09-21 10:30 | 604 | 602
2018-09-21 11:00 | 602 | 601
2018-09-21 11:30 | 600 | 599
2018-09-21 12:00 | 612 | 611
2018-09-21 12:30 | 611 | 611
2018-09-21 13:00 | 621 | 620
2018-09-21 13:30 | 619 | 619
2018-09-21 14:00 | 624 | 624
2018-09-21 14:30 | 633 | 633
2018-09-21 15:00 | 646 | 646
2018-09-21 15:30 | 672 | 672
2018-09-21 16:00 | 711 | 711
2018-09-21 16:30 | 743 | 743
2018-09-21 17:00 | 781 | 781
2018-09-21 17:30 | 804 | 804
2018-09-21 18:00 | 821 | 821
2018-09-21 18:30 | 847 | 845
2018-09-21 19:00 | 862 | 853
2018-09-21 19:30 | 840 | 838
2018-09-21 20:00 | 808 | 807
2018-09-21 20:30 | 801 | 799
2018-09-21 21:00 | 792 | 790
2018-09-21 21:30 | 761 | 758
2018-09-21 22:00 | 740 | 735
2018-09-21 22:30 | 751 | 745
2018-09-21 23:00 | 731 | 723
2018-09-21 23:30 | 689 | 686
2018-09-22 | 654 | 648
2018-09-22 00:30 | 596 | 583
2018-09-22 01:00 | 565 | 548
2018-09-22 01:30 | 552 | 533
2018-09-22 02:00 | 538 | 516
2018-09-22 02:30 | 531 | 507
2018-09-22 03:00 | 525 | 501
2018-09-22 03:30 | 525 | 500
2018-09-22 04:00 | 526 | 500
2018-09-22 04:30 | 527 | 502
2018-09-22 05:00 | 531 | 506
2018-09-22 05:30 | 546 | 524
2018-09-22 06:00 | 561 | 537
2018-09-22 06:30 | 577 | 557
2018-09-22 07:00 | 586 | 570
2018-09-22 07:30 | 594 | 582
2018-09-22 08:00 | 598 | 590
2018-09-22 08:30 | 588 | 583
2018-09-22 09:00 | 577 | 572
2018-09-22 09:30 | 563 | 559
2018-09-22 10:00 | 568 | 565
2018-09-22 10:30 | 571 | 569
2018-09-22 11:00 | 572 | 570
2018-09-22 11:30 | 562 | 558
2018-09-22 12:00 | 551 | 547
2018-09-22 12:30 | 525 | 519
2018-09-22 13:00 | 510 | 502
2018-09-22 13:30 | 510 | 502
2018-09-22 14:00 | 513 | 504
2018-09-22 14:30 | 523 | 515
2018-09-22 15:00 | 543 | 536
2018-09-22 15:30 | 564 | 558
2018-09-22 16:00 | 599 | 594
2018-09-22 16:30 | 646 | 643
2018-09-22 17:00 | 683 | 681
2018-09-22 17:30 | 702 | 701
2018-09-22 18:00 | 724 | 723
2018-09-22 18:30 | 761 | 758
2018-09-22 19:00 | 774 | 771
2018-09-22 19:30 | 758 | 753
2018-09-22 20:00 | 746 | 741
2018-09-22 20:30 | 735 | 730
2018-09-22 21:00 | 707 | 703
2018-09-22 21:30 | 681 | 678
2018-09-22 22:00 | 673 | 669
2018-09-22 22:30 | 664 | 659
2018-09-22 23:00 | 666 | 662
2018-09-22 23:30 | 638 | 631
2018-09-23 | 605 | 594
2018-09-23 00:30 | 568 | 549
2018-09-23 01:00 | 546 | 522
2018-09-23 01:30 | 530 | 502
2018-09-23 02:00 | 519 | 485
2018-09-23 02:30 | 494 | 457
2018-09-23 03:00 | 507 | 472
2018-09-23 03:30 | 477 | 441
2018-09-23 04:00 | 491 | 456
2018-09-23 04:30 | 497 | 463
2018-09-23 05:00 | 505 | 470
2018-09-23 05:30 | 513 | 479
2018-09-23 06:00 | 521 | 484
2018-09-23 06:30 | 533 | 498
2018-09-23 07:00 | 530 | 497
2018-09-23 07:30 | 528 | 500
2018-09-23 08:00 | 527 | 504
2018-09-23 08:30 | 526 | 508
2018-09-23 09:00 | 522 | 508
2018-09-23 09:30 | 512 | 499
2018-09-23 10:00 | 503 | 492
2018-09-23 10:30 | 490 | 480
2018-09-23 11:00 | 477 | 467
2018-09-23 11:30 | 471 | 460
2018-09-23 12:00 | 468 | 457
2018-09-23 12:30 | 467 | 456
2018-09-23 13:00 | 471 | 460
2018-09-23 13:30 | 475 | 465
2018-09-23 14:00 | 495 | 485
2018-09-23 14:30 | 490 | 480
2018-09-23 15:00 | 533 | 525
2018-09-23 15:30 | 542 | 535
2018-09-23 16:00 | 587 | 582
2018-09-23 16:30 | 631 | 628
2018-09-23 17:00 | 666 | 665
2018-09-23 17:30 | 706 | 705
2018-09-23 18:00 | 734 | 733
2018-09-23 18:30 | 785 | 784
2018-09-23 19:00 | 794 | 793
2018-09-23 19:30 | 763 | 762
2018-09-23 20:00 | 745 | 743
2018-09-23 20:30 | 735 | 733
2018-09-23 21:00 | 709 | 707
2018-09-23 21:30 | 681 | 678
2018-09-23 22:00 | 661 | 656
2018-09-23 22:30 | 650 | 644
2018-09-23 23:00 | 659 | 652
2018-09-23 23:30 | 628 | 619
2018-09-24 | 589 | 576
2018-09-24 00:30 | 548 | 528
2018-09-24 01:00 | 529 | 505
2018-09-24 01:30 | 516 | 489
2018-09-24 02:00 | 511 | 480
2018-09-24 02:30 | 507 | 474
2018-09-24 03:00 | 502 | 467
2018-09-24 03:30 | 505 | 470
2018-09-24 04:00 | 507 | 473
2018-09-24 04:30 | 515 | 483
2018-09-24 05:00 | 533 | 505
2018-09-24 05:30 | 562 | 542
2018-09-24 06:00 | 586 | 569
2018-09-24 06:30 | 623 | 614
2018-09-24 07:00 | 652 | 646
2018-09-24 07:30 | 673 | 668
2018-09-24 08:00 | 665 | 663
2018-09-24 08:30 | 659 | 658
2018-09-24 09:00 | 613 | 609
2018-09-24 09:30 | 592 | 589
2018-09-24 10:00 | 581 | 579
2018-09-24 10:30 | 581 | 581
2018-09-24 11:00 | 581 | 581
2018-09-24 11:30 | 578 | 578
2018-09-24 12:00 | 603 | 603
2018-09-24 12:30 | 617 | 617
2018-09-24 13:00 | 644 | 644
2018-09-24 13:30 | 658 | 658
2018-09-24 14:00 | 682 | 682
2018-09-24 14:30 | 685 | 685
2018-09-24 15:00 | 675 | 675
2018-09-24 15:30 | 695 | 695
2018-09-24 16:00 | 735 | 735
2018-09-24 16:30 | 771 | 771
2018-09-24 17:00 | 803 | 802
2018-09-24 17:30 | 835 | 835
2018-09-24 18:00 | 867 | 867
2018-09-24 18:30 | 897 | 896
2018-09-24 19:00 | 900 | 899
2018-09-24 19:30 | 875 | 874
2018-09-24 20:00 | 857 | 856
2018-09-24 20:30 | 842 | 840
2018-09-24 21:00 | 803 | 801
2018-09-24 21:30 | 759 | 755
2018-09-24 22:00 | 722 | 719
2018-09-24 22:30 | 697 | 694
2018-09-24 23:00 | 688 | 685
2018-09-24 23:30 | 651 | 647
2018-09-25 | 613 | 605
2018-09-25 00:30 | 570 | 557
2018-09-25 01:00 | 545 | 529
2018-09-25 01:30 | 530 | 511
2018-09-25 02:00 | 518 | 496
2018-09-25 02:30 | 520 | 497
2018-09-25 03:00 | 512 | 488
2018-09-25 03:30 | 505 | 480
2018-09-25 04:00 | 516 | 492
2018-09-25 04:30 | 521 | 499
2018-09-25 05:00 | 532 | 513
2018-09-25 05:30 | 567 | 554
2018-09-25 06:00 | 595 | 584
2018-09-25 06:30 | 643 | 638
2018-09-25 07:00 | 687 | 683
2018-09-25 07:30 | 731 | 728
2018-09-25 08:00 | 758 | 754
2018-09-25 08:30 | 773 | 771
2018-09-25 09:00 | 740 | 737
2018-09-25 09:30 | 707 | 704
2018-09-25 10:00 | 681 | 677
2018-09-25 10:30 | 661 | 657
2018-09-25 11:00 | 728 | 726
2018-09-25 11:30 | 754 | 753
2018-09-25 12:00 | 780 | 779
2018-09-25 12:30 | 796 | 796
2018-09-25 13:00 | 782 | 781
2018-09-25 13:30 | 733 | 731
2018-09-25 14:00 | 728 | 726
2018-09-25 14:30 | 771 | 769
2018-09-25 15:00 | 772 | 771
2018-09-25 15:30 | 783 | 782
2018-09-25 16:00 | 803 | 801
2018-09-25 16:30 | 834 | 833
2018-09-25 17:00 | 890 | 886
2018-09-25 17:30 | 918 | 913
2018-09-25 18:00 | 924 | 920
2018-09-25 18:30 | 945 | 942
2018-09-25 19:00 | 956 | 953
2018-09-25 19:30 | 894 | 891
2018-09-25 20:00 | 859 | 859
2018-09-25 20:30 | 841 | 841
2018-09-25 21:00 | 801 | 800
2018-09-25 21:30 | 758 | 758
2018-09-25 22:00 | 728 | 728
2018-09-25 22:30 | 707 | 706
2018-09-25 23:00 | 697 | 695
2018-09-25 23:30 | 661 | 658
2018-09-26 | 618 | 610
2018-09-26 00:30 | 573 | 559
2018-09-26 01:00 | 547 | 529
2018-09-26 01:30 | 579 | 563
2018-09-26 02:00 | 593 | 577
2018-09-26 02:30 | 580 | 562
2018-09-26 03:00 | 534 | 510
2018-09-26 03:30 | 514 | 489
2018-09-26 04:00 | 515 | 490
2018-09-26 04:30 | 528 | 504
2018-09-26 05:00 | 540 | 520
2018-09-26 05:30 | 571 | 557
2018-09-26 06:00 | 601 | 590
2018-09-26 06:30 | 651 | 645
2018-09-26 07:00 | 684 | 680
2018-09-26 07:30 | 714 | 713
2018-09-26 08:00 | 691 | 686
2018-09-26 08:30 | 669 | 663
2018-09-26 09:00 | 648 | 642
2018-09-26 09:30 | 653 | 649
2018-09-26 10:00 | 668 | 665
2018-09-26 10:30 | 676 | 674
2018-09-26 11:00 | 655 | 652
2018-09-26 11:30 | 655 | 651
2018-09-26 12:00 | 661 | 657
2018-09-26 12:30 | 642 | 638
2018-09-26 13:00 | 645 | 645
2018-09-26 13:30 | 643 | 643
2018-09-26 14:00 | 653 | 652
2018-09-26 14:30 | 675 | 674
2018-09-26 15:00 | 702 | 701
2018-09-26 15:30 | 704 | 702
2018-09-26 16:00 | 708 | 704
2018-09-26 16:30 | 752 | 749
2018-09-26 17:00 | 795 | 791
2018-09-26 17:30 | 832 | 823
2018-09-26 18:00 | 856 | 848
2018-09-26 18:30 | 876 | 870
2018-09-26 19:00 | 882 | 876
2018-09-26 19:30 | 844 | 842
2018-09-26 20:00 | 832 | 829
2018-09-26 20:30 | 816 | 816
2018-09-26 21:00 | 768 | 768
2018-09-26 21:30 | 736 | 736
2018-09-26 22:00 | 699 | 699
2018-09-26 22:30 | 692 | 691
2018-09-26 23:00 | 695 | 694
2018-09-26 23:30 | 650 | 648
2018-09-27 | 604 | 598
2018-09-27 00:30 | 567 | 557
2018-09-27 01:00 | 545 | 531
2018-09-27 01:30 | 528 | 511
2018-09-27 02:00 | 513 | 495
2018-09-27 02:30 | 500 | 481
2018-09-27 03:00 | 498 | 476
2018-09-27 03:30 | 503 | 482
2018-09-27 04:00 | 511 | 489
2018-09-27 04:30 | 517 | 496
2018-09-27 05:00 | 534 | 518
2018-09-27 05:30 | 561 | 551
2018-09-27 06:00 | 590 | 581
2018-09-27 06:30 | 639 | 630
2018-09-27 07:00 | 676 | 673
2018-09-27 07:30 | 705 | 704
2018-09-27 08:00 | 705 | 703
2018-09-27 08:30 | 706 | 705
2018-09-27 09:00 | 701 | 700
2018-09-27 09:30 | 707 | 706
2018-09-27 10:00 | 707 | 706
2018-09-27 10:30 | 713 | 713
2018-09-27 11:00 | 731 | 731
2018-09-27 11:30 | 744 | 744
2018-09-27 12:00 | 751 | 751
2018-09-27 12:30 | 746 | 746
2018-09-27 13:00 | 739 | 739
2018-09-27 13:30 | 716 | 716
2018-09-27 14:00 | 699 | 699
2018-09-27 14:30 | 677 | 676
2018-09-27 15:00 | 693 | 693
2018-09-27 15:30 | 709 | 709
2018-09-27 16:00 | 732 | 732
2018-09-27 16:30 | 771 | 771
2018-09-27 17:00 | 796 | 796
2018-09-27 17:30 | 824 | 824
2018-09-27 18:00 | 865 | 865
2018-09-27 18:30 | 910 | 910
2018-09-27 19:00 | 914 | 913
2018-09-27 19:30 | 892 | 888
2018-09-27 20:00 | 861 | 860
2018-09-27 20:30 | 839 | 839
2018-09-27 21:00 | 795 | 795
2018-09-27 21:30 | 753 | 751
2018-09-27 22:00 | 707 | 704
2018-09-27 22:30 | 686 | 682
2018-09-27 23:00 | 680 | 676
2018-09-27 23:30 | 635 | 630
2018-09-28 | 582 | 573
2018-09-28 00:30 | 549 | 535
2018-09-28 01:00 | 529 | 513
2018-09-28 01:30 | 509 | 491
2018-09-28 02:00 | 509 | 488
2018-09-28 02:30 | 508 | 487
2018-09-28 03:00 | 494 | 473
2018-09-28 03:30 | 501 | 479
2018-09-28 04:00 | 495 | 472
2018-09-28 04:30 | 501 | 481
2018-09-28 05:00 | 525 | 507
2018-09-28 05:30 | 559 | 547
2018-09-28 06:00 | 583 | 572
2018-09-28 06:30 | 628 | 622
2018-09-28 07:00 | 655 | 653
2018-09-28 07:30 | 686 | 683
2018-09-28 08:00 | 678 | 676
2018-09-28 08:30 | 673 | 673
2018-09-28 09:00 | 681 | 681
2018-09-28 09:30 | 703 | 703
2018-09-28 10:00 | 689 | 689
2018-09-28 10:30 | 664 | 663
2018-09-28 11:00 | 634 | 634
2018-09-28 11:30 | 634 | 633
2018-09-28 12:00 | 639 | 638
2018-09-28 12:30 | 636 | 635
2018-09-28 13:00 | 633 | 631
2018-09-28 13:30 | 637 | 636
2018-09-28 14:00 | 653 | 651
2018-09-28 14:30 | 671 | 670
2018-09-28 15:00 | 689 | 688
2018-09-28 15:30 | 707 | 705
2018-09-28 16:00 | 743 | 741
2018-09-28 16:30 | 774 | 774
2018-09-28 17:00 | 804 | 804
2018-09-28 17:30 | 817 | 816
2018-09-28 18:00 | 836 | 835
2018-09-28 18:30 | 872 | 872
2018-09-28 19:00 | 883 | 883
2018-09-28 19:30 | 857 | 857
2018-09-28 20:00 | 829 | 829
2018-09-28 20:30 | 809 | 809
2018-09-28 21:00 | 783 | 783
2018-09-28 21:30 | 748 | 748
2018-09-28 22:00 | 729 | 729
2018-09-28 22:30 | 708 | 707
2018-09-28 23:00 | 694 | 692
2018-09-28 23:30 | 651 | 648
2018-09-29 | 614 | 608
2018-09-29 00:30 | 570 | 559
2018-09-29 01:00 | 551 | 535
2018-09-29 01:30 | 531 | 513
2018-09-29 02:00 | 516 | 495
2018-09-29 02:30 | 512 | 490
2018-09-29 03:00 | 506 | 481
2018-09-29 03:30 | 518 | 494
2018-09-29 04:00 | 506 | 479
2018-09-29 04:30 | 510 | 482
2018-09-29 05:00 | 514 | 490
2018-09-29 05:30 | 521 | 496
2018-09-29 06:00 | 530 | 501
2018-09-29 06:30 | 541 | 517
2018-09-29 07:00 | 545 | 526
2018-09-29 07:30 | 552 | 540
2018-09-29 08:00 | 559 | 551
2018-09-29 08:30 | 565 | 562
2018-09-29 09:00 | 575 | 573
2018-09-29 09:30 | 566 | 564
2018-09-29 10:00 | 555 | 553
2018-09-29 10:30 | 535 | 533
2018-09-29 11:00 | 536 | 534
2018-09-29 11:30 | 520 | 518
2018-09-29 12:00 | 527 | 525
2018-09-29 12:30 | 535 | 534
2018-09-29 13:00 | 542 | 541
2018-09-29 13:30 | 549 | 548
2018-09-29 14:00 | 557 | 557
2018-09-29 14:30 | 585 | 585
2018-09-29 15:00 | 663 | 663
2018-09-29 15:30 | 697 | 697
2018-09-29 16:00 | 725 | 724
2018-09-29 16:30 | 738 | 738
2018-09-29 17:00 | 735 | 734
2018-09-29 17:30 | 728 | 721
2018-09-29 18:00 | 738 | 733
2018-09-29 18:30 | 773 | 771
2018-09-29 19:00 | 782 | 780
2018-09-29 19:30 | 759 | 755
2018-09-29 20:00 | 751 | 746
2018-09-29 20:30 | 740 | 735
2018-09-29 21:00 | 709 | 707
2018-09-29 21:30 | 682 | 680
2018-09-29 22:00 | 669 | 666
2018-09-29 22:30 | 663 | 659
2018-09-29 23:00 | 668 | 664
2018-09-29 23:30 | 634 | 629
2018-09-30 | 601 | 591
2018-09-30 00:30 | 562 | 549
2018-09-30 01:00 | 552 | 533
2018-09-30 01:30 | 538 | 516
2018-09-30 02:00 | 525 | 499
2018-09-30 02:30 | 518 | 491
2018-09-30 03:00 | 513 | 486
2018-09-30 03:30 | 517 | 489
2018-09-30 04:00 | 531 | 502
2018-09-30 04:30 | 527 | 498
2018-09-30 05:00 | 510 | 480
2018-09-30 05:30 | 520 | 492
2018-09-30 06:00 | 520 | 489
2018-09-30 06:30 | 526 | 496
2018-09-30 07:00 | 546 | 522
2018-09-30 07:30 | 580 | 564
2018-09-30 08:00 | 613 | 602
2018-09-30 08:30 | 651 | 646
2018-09-30 09:00 | 693 | 690
2018-09-30 09:30 | 704 | 702
2018-09-30 10:00 | 710 | 708
2018-09-30 10:30 | 722 | 721
2018-09-30 11:00 | 732 | 731
2018-09-30 11:30 | 733 | 732
2018-09-30 12:00 | 739 | 738
2018-09-30 12:30 | 739 | 738
2018-09-30 13:00 | 717 | 715
2018-09-30 13:30 | 652 | 648
2018-09-30 14:00 | 590 | 582
2018-09-30 14:30 | 582 | 575
2018-09-30 15:00 | 597 | 591
2018-09-30 15:30 | 613 | 608
2018-09-30 16:00 | 617 | 610
2018-09-30 16:30 | 646 | 640
2018-09-30 17:00 | 685 | 682
2018-09-30 17:30 | 718 | 716
2018-09-30 18:00 | 746 | 744
2018-09-30 18:30 | 808 | 806
2018-09-30 19:00 | 815 | 812
2018-09-30 19:30 | 782 | 776
2018-09-30 20:00 | 769 | 761
2018-09-30 20:30 | 749 | 741
2018-09-30 21:00 | 729 | 723
2018-09-30 21:30 | 700 | 695
2018-09-30 22:00 | 691 | 685
2018-09-30 22:30 | 688 | 682
2018-09-30 23:00 | 693 | 687
2018-09-30 23:30 | 661 | 652
2018-10-01 | 622 | 607
2018-10-01 00:30 | 581 | 560
2018-10-01 01:00 | 556 | 532
2018-10-01 01:30 | 542 | 515
2018-10-01 02:00 | 527 | 497
2018-10-01 02:30 | 517 | 486
2018-10-01 03:00 | 512 | 480
2018-10-01 03:30 | 514 | 481
2018-10-01 04:00 | 514 | 480
2018-10-01 04:30 | 516 | 482
2018-10-01 05:00 | 521 | 489
2018-10-01 05:30 | 528 | 497
2018-10-01 06:00 | 537 | 504
2018-10-01 06:30 | 548 | 519
2018-10-01 07:00 | 541 | 515
2018-10-01 07:30 | 545 | 523
2018-10-01 08:00 | 538 | 520
2018-10-01 08:30 | 526 | 510
2018-10-01 09:00 | 513 | 500
2018-10-01 09:30 | 506 | 496
2018-10-01 10:00 | 506 | 497
2018-10-01 10:30 | 511 | 504
2018-10-01 11:00 | 514 | 507
2018-10-01 11:30 | 493 | 486
2018-10-01 12:00 | 497 | 490
2018-10-01 12:30 | 505 | 498
2018-10-01 13:00 | 514 | 507
2018-10-01 13:30 | 504 | 496
2018-10-01 14:00 | 513 | 506
2018-10-01 14:30 | 524 | 516
2018-10-01 15:00 | 556 | 550
2018-10-01 15:30 | 589 | 584
2018-10-01 16:00 | 627 | 624
2018-10-01 16:30 | 671 | 669
2018-10-01 17:00 | 717 | 716
2018-10-01 17:30 | 756 | 756
2018-10-01 18:00 | 788 | 788
2018-10-01 18:30 | 838 | 838
2018-10-01 19:00 | 848 | 848
2018-10-01 19:30 | 823 | 822
2018-10-01 20:00 | 806 | 804
2018-10-01 20:30 | 788 | 785
2018-10-01 21:00 | 753 | 752
2018-10-01 21:30 | 727 | 724
2018-10-01 22:00 | 704 | 701
2018-10-01 22:30 | 688 | 683
2018-10-01 23:00 | 689 | 684
2018-10-01 23:30 | 662 | 654
2018-10-02 | 625 | 612
2018-10-02 00:30 | 584 | 566
2018-10-02 01:00 | 559 | 539
2018-10-02 01:30 | 543 | 520
2018-10-02 02:00 | 532 | 506
2018-10-02 02:30 | 515 | 488
2018-10-02 03:00 | 512 | 483
2018-10-02 03:30 | 507 | 478
2018-10-02 04:00 | 515 | 487
2018-10-02 04:30 | 523 | 498
2018-10-02 05:00 | 545 | 523
2018-10-02 05:30 | 575 | 558
2018-10-02 06:00 | 609 | 596
2018-10-02 06:30 | 644 | 638
2018-10-02 07:00 | 654 | 652
2018-10-02 07:30 | 673 | 672
2018-10-02 08:00 | 661 | 657
2018-10-02 08:30 | 639 | 636
2018-10-02 09:00 | 624 | 622
2018-10-02 09:30 | 633 | 632
2018-10-02 10:00 | 645 | 645
2018-10-02 10:30 | 648 | 647
2018-10-02 11:00 | 645 | 644
2018-10-02 11:30 | 615 | 614
2018-10-02 12:00 | 611 | 610
2018-10-02 12:30 | 591 | 590
2018-10-02 13:00 | 590 | 589
2018-10-02 13:30 | 582 | 581
2018-10-02 14:00 | 576 | 574
2018-10-02 14:30 | 617 | 616
2018-10-02 15:00 | 637 | 636
2018-10-02 15:30 | 652 | 652
2018-10-02 16:00 | 683 | 683
2018-10-02 16:30 | 729 | 728
2018-10-02 17:00 | 773 | 772
2018-10-02 17:30 | 800 | 798
2018-10-02 18:00 | 829 | 825
2018-10-02 18:30 | 874 | 872
2018-10-02 19:00 | 886 | 884
2018-10-02 19:30 | 865 | 861
2018-10-02 20:00 | 837 | 833
2018-10-02 20:30 | 812 | 811
2018-10-02 21:00 | 781 | 780
2018-10-02 21:30 | 733 | 733
2018-10-02 22:00 | 708 | 707
2018-10-02 22:30 | 698 | 696
2018-10-02 23:00 | 687 | 685
2018-10-02 23:30 | 645 | 642
2018-10-03 | 602 | 595
2018-10-03 00:30 | 555 | 543
2018-10-03 01:00 | 536 | 519
2018-10-03 01:30 | 523 | 502
2018-10-03 02:00 | 515 | 492
2018-10-03 02:30 | 509 | 487
2018-10-03 03:00 | 510 | 483
2018-10-03 03:30 | 509 | 482
2018-10-03 04:00 | 513 | 487
2018-10-03 04:30 | 518 | 495
2018-10-03 05:00 | 534 | 513
2018-10-03 05:30 | 561 | 546
2018-10-03 06:00 | 591 | 578
2018-10-03 06:30 | 637 | 631
2018-10-03 07:00 | 650 | 647
2018-10-03 07:30 | 670 | 669
2018-10-03 08:00 | 655 | 653
2018-10-03 08:30 | 649 | 648
2018-10-03 09:00 | 609 | 608
2018-10-03 09:30 | 581 | 580
2018-10-03 10:00 | 566 | 563
2018-10-03 10:30 | 557 | 554
2018-10-03 11:00 | 552 | 550
2018-10-03 11:30 | 535 | 533
2018-10-03 12:00 | 512 | 509
2018-10-03 12:30 | 502 | 500
2018-10-03 13:00 | 502 | 500
2018-10-03 13:30 | 502 | 501
2018-10-03 14:00 | 528 | 525
2018-10-03 14:30 | 603 | 593
2018-10-03 15:00 | 641 | 633
2018-10-03 15:30 | 670 | 664
2018-10-03 16:00 | 717 | 711
2018-10-03 16:30 | 759 | 755
2018-10-03 17:00 | 804 | 801
2018-10-03 17:30 | 821 | 818
2018-10-03 18:00 | 842 | 838
2018-10-03 18:30 | 886 | 885
2018-10-03 19:00 | 903 | 901
2018-10-03 19:30 | 870 | 867
2018-10-03 20:00 | 852 | 848
2018-10-03 20:30 | 840 | 837
2018-10-03 21:00 | 805 | 799
2018-10-03 21:30 | 769 | 760
2018-10-03 22:00 | 726 | 723
2018-10-03 22:30 | 690 | 688
2018-10-03 23:00 | 678 | 676
2018-10-03 23:30 | 643 | 640
2018-10-04 | 595 | 588
2018-10-04 00:30 | 555 | 543
2018-10-04 01:00 | 530 | 514
2018-10-04 01:30 | 516 | 497
2018-10-04 02:00 | 513 | 489
2018-10-04 02:30 | 505 | 480
2018-10-04 03:00 | 501 | 472
2018-10-04 03:30 | 499 | 472
2018-10-04 04:00 | 497 | 471
2018-10-04 04:30 | 512 | 487
2018-10-04 05:00 | 521 | 500
2018-10-04 05:30 | 547 | 531
2018-10-04 06:00 | 573 | 559
2018-10-04 06:30 | 605 | 599
2018-10-04 07:00 | 593 | 588
2018-10-04 07:30 | 610 | 601
2018-10-04 08:00 | 577 | 571
2018-10-04 08:30 | 550 | 546
2018-10-04 09:00 | 533 | 530
2018-10-04 09:30 | 514 | 511
2018-10-04 10:00 | 497 | 494
2018-10-04 10:30 | 498 | 497
2018-10-04 11:00 | 483 | 482
2018-10-04 11:30 | 479 | 477
2018-10-04 12:00 | 479 | 478
2018-10-04 12:30 | 487 | 486
2018-10-04 13:00 | 486 | 485
2018-10-04 13:30 | 489 | 488
2018-10-04 14:00 | 522 | 522
2018-10-04 14:30 | 558 | 558
2018-10-04 15:00 | 590 | 590
2018-10-04 15:30 | 629 | 629
2018-10-04 16:00 | 673 | 673
2018-10-04 16:30 | 722 | 722
2018-10-04 17:00 | 764 | 764
2018-10-04 17:30 | 806 | 805
2018-10-04 18:00 | 830 | 829
2018-10-04 18:30 | 882 | 882
2018-10-04 19:00 | 898 | 898
2018-10-04 19:30 | 875 | 874
2018-10-04 20:00 | 838 | 837
2018-10-04 20:30 | 823 | 821
2018-10-04 21:00 | 777 | 775
2018-10-04 21:30 | 737 | 732
2018-10-04 22:00 | 707 | 704
2018-10-04 22:30 | 688 | 687
2018-10-04 23:00 | 682 | 680
2018-10-04 23:30 | 643 | 640
2018-10-05 | 600 | 593
2018-10-05 00:30 | 564 | 551
2018-10-05 01:00 | 540 | 524
2018-10-05 01:30 | 522 | 502
2018-10-05 02:00 | 508 | 486
2018-10-05 02:30 | 498 | 475
2018-10-05 03:00 | 498 | 473
2018-10-05 03:30 | 502 | 476
2018-10-05 04:00 | 501 | 476
2018-10-05 04:30 | 504 | 481
2018-10-05 05:00 | 520 | 499
2018-10-05 05:30 | 545 | 529
2018-10-05 06:00 | 567 | 552
2018-10-05 06:30 | 606 | 599
2018-10-05 07:00 | 639 | 637
2018-10-05 07:30 | 687 | 686
2018-10-05 08:00 | 679 | 676
2018-10-05 08:30 | 658 | 656
2018-10-05 09:00 | 665 | 665
2018-10-05 09:30 | 681 | 681
2018-10-05 10:00 | 668 | 668
2018-10-05 10:30 | 668 | 668
2018-10-05 11:00 | 666 | 666
2018-10-05 11:30 | 666 | 665
2018-10-05 12:00 | 675 | 674
2018-10-05 12:30 | 685 | 684
2018-10-05 13:00 | 700 | 700
2018-10-05 13:30 | 705 | 704
2018-10-05 14:00 | 710 | 709
2018-10-05 14:30 | 745 | 744
2018-10-05 15:00 | 780 | 779
2018-10-05 15:30 | 793 | 791
2018-10-05 16:00 | 814 | 812
2018-10-05 16:30 | 818 | 815
2018-10-05 17:00 | 832 | 829
2018-10-05 17:30 | 831 | 827
2018-10-05 18:00 | 827 | 823
2018-10-05 18:30 | 848 | 845
2018-10-05 19:00 | 859 | 856
2018-10-05 19:30 | 840 | 836
2018-10-05 20:00 | 818 | 815
2018-10-05 20:30 | 804 | 801
2018-10-05 21:00 | 769 | 767
2018-10-05 21:30 | 750 | 747
2018-10-05 22:00 | 727 | 725
2018-10-05 22:30 | 716 | 714
2018-10-05 23:00 | 718 | 716
2018-10-05 23:30 | 680 | 676
2018-10-06 | 634 | 627
2018-10-06 00:30 | 589 | 577
2018-10-06 01:00 | 577 | 561
2018-10-06 01:30 | 559 | 538
2018-10-06 02:00 | 543 | 520
2018-10-06 02:30 | 535 | 511
2018-10-06 03:00 | 529 | 504
2018-10-06 03:30 | 530 | 503
2018-10-06 04:00 | 528 | 501
2018-10-06 04:30 | 534 | 508
2018-10-06 05:00 | 534 | 509
2018-10-06 05:30 | 545 | 523
2018-10-06 06:00 | 559 | 534
2018-10-06 06:30 | 582 | 561
2018-10-06 07:00 | 600 | 583
2018-10-06 07:30 | 615 | 602
2018-10-06 08:00 | 636 | 628
2018-10-06 08:30 | 671 | 668
2018-10-06 09:00 | 690 | 688
2018-10-06 09:30 | 693 | 693
2018-10-06 10:00 | 706 | 706
2018-10-06 10:30 | 682 | 681
2018-10-06 11:00 | 678 | 678
2018-10-06 11:30 | 674 | 673
2018-10-06 12:00 | 677 | 675
2018-10-06 12:30 | 690 | 689
2018-10-06 13:00 | 704 | 703
2018-10-06 13:30 | 709 | 708
2018-10-06 14:00 | 703 | 702
2018-10-06 14:30 | 690 | 689
2018-10-06 15:00 | 718 | 716
2018-10-06 15:30 | 747 | 746
2018-10-06 16:00 | 732 | 731
2018-10-06 16:30 | 735 | 734
2018-10-06 17:00 | 765 | 764
2018-10-06 17:30 | 786 | 785
2018-10-06 18:00 | 801 | 801
2018-10-06 18:30 | 840 | 839
2018-10-06 19:00 | 853 | 853
2018-10-06 19:30 | 801 | 801
2018-10-06 20:00 | 772 | 772
2018-10-06 20:30 | 766 | 765
2018-10-06 21:00 | 736 | 735
2018-10-06 21:30 | 712 | 710
2018-10-06 22:00 | 700 | 697
2018-10-06 22:30 | 696 | 692
2018-10-06 23:00 | 702 | 698
2018-10-06 23:30 | 677 | 669
2018-10-07 | 637 | 624
2018-10-07 00:30 | 597 | 578
2018-10-07 01:00 | 569 | 546
2018-10-07 01:30 | 553 | 527
2018-10-07 02:00 | 543 | 513
2018-10-07 02:30 | 532 | 502
2018-10-07 03:00 | 529 | 497
2018-10-07 03:30 | 527 | 497
2018-10-07 04:00 | 523 | 490
2018-10-07 04:30 | 530 | 497
2018-10-07 05:00 | 535 | 503
2018-10-07 05:30 | 539 | 505
2018-10-07 06:00 | 543 | 505
2018-10-07 06:30 | 548 | 513
2018-10-07 07:00 | 546 | 514
2018-10-07 07:30 | 550 | 524
2018-10-07 08:00 | 546 | 524
2018-10-07 08:30 | 548 | 531
2018-10-07 09:00 | 546 | 533
2018-10-07 09:30 | 560 | 549
2018-10-07 10:00 | 566 | 558
2018-10-07 10:30 | 559 | 552
2018-10-07 11:00 | 571 | 565
2018-10-07 11:30 | 574 | 567
2018-10-07 12:00 | 573 | 566
2018-10-07 12:30 | 573 | 567
2018-10-07 13:00 | 562 | 555
2018-10-07 13:30 | 554 | 546
2018-10-07 14:00 | 560 | 553
2018-10-07 14:30 | 588 | 582
2018-10-07 15:00 | 604 | 599
2018-10-07 15:30 | 621 | 616
2018-10-07 16:00 | 650 | 646
2018-10-07 16:30 | 682 | 679
2018-10-07 17:00 | 716 | 714
2018-10-07 17:30 | 742 | 741
2018-10-07 18:00 | 764 | 763
2018-10-07 18:30 | 808 | 807
2018-10-07 19:00 | 818 | 817
2018-10-07 19:30 | 798 | 796
2018-10-07 20:00 | 790 | 786
2018-10-07 20:30 | 776 | 774
2018-10-07 21:00 | 750 | 748
2018-10-07 21:30 | 714 | 711
2018-10-07 22:00 | 698 | 692
2018-10-07 22:30 | 688 | 681
2018-10-07 23:00 | 685 | 677
2018-10-07 23:30 | 659 | 648
2018-10-08 | 621 | 604
2018-10-08 00:30 | 582 | 561
2018-10-08 01:00 | 555 | 531
2018-10-08 01:30 | 540 | 513
2018-10-08 02:00 | 530 | 500
2018-10-08 02:30 | 526 | 494
2018-10-08 03:00 | 521 | 488
2018-10-08 03:30 | 520 | 488
2018-10-08 04:00 | 521 | 489
2018-10-08 04:30 | 529 | 502
2018-10-08 05:00 | 540 | 516
2018-10-08 05:30 | 568 | 550
2018-10-08 06:00 | 605 | 591
2018-10-08 06:30 | 653 | 646
2018-10-08 07:00 | 683 | 680
2018-10-08 07:30 | 718 | 717
2018-10-08 08:00 | 713 | 710
2018-10-08 08:30 | 699 | 697
2018-10-08 09:00 | 650 | 648
2018-10-08 09:30 | 645 | 644
2018-10-08 10:00 | 612 | 612
2018-10-08 10:30 | 601 | 601
2018-10-08 11:00 | 613 | 613
2018-10-08 11:30 | 612 | 612
2018-10-08 12:00 | 625 | 625
2018-10-08 12:30 | 629 | 629
2018-10-08 13:00 | 637 | 637
2018-10-08 13:30 | 663 | 663
2018-10-08 14:00 | 716 | 715
2018-10-08 14:30 | 762 | 761
2018-10-08 15:00 | 743 | 741
2018-10-08 15:30 | 730 | 728
2018-10-08 16:00 | 772 | 770
2018-10-08 16:30 | 824 | 823
2018-10-08 17:00 | 859 | 854
2018-10-08 17:30 | 891 | 882
2018-10-08 18:00 | 902 | 895
2018-10-08 18:30 | 915 | 911
2018-10-08 19:00 | 918 | 912
2018-10-08 19:30 | 894 | 886
2018-10-08 20:00 | 876 | 865
2018-10-08 20:30 | 854 | 847
2018-10-08 21:00 | 815 | 807
2018-10-08 21:30 | 760 | 756
2018-10-08 22:00 | 727 | 724
2018-10-08 22:30 | 713 | 709
2018-10-08 23:00 | 697 | 694
2018-10-08 23:30 | 656 | 652
2018-10-09 | 614 | 606
2018-10-09 00:30 | 569 | 556
2018-10-09 01:00 | 543 | 526
2018-10-09 01:30 | 522 | 503
2018-10-09 02:00 | 508 | 484
2018-10-09 02:30 | 506 | 479
2018-10-09 03:00 | 501 | 472
2018-10-09 03:30 | 503 | 475
2018-10-09 04:00 | 501 | 474
2018-10-09 04:30 | 509 | 485
2018-10-09 05:00 | 523 | 504
2018-10-09 05:30 | 554 | 537
2018-10-09 06:00 | 587 | 573
2018-10-09 06:30 | 637 | 630
2018-10-09 07:00 | 667 | 663
2018-10-09 07:30 | 690 | 689
2018-10-09 08:00 | 667 | 666
2018-10-09 08:30 | 642 | 641
2018-10-09 09:00 | 645 | 643
2018-10-09 09:30 | 644 | 641
2018-10-09 10:00 | 644 | 644
2018-10-09 10:30 | 665 | 665
2018-10-09 11:00 | 677 | 677
2018-10-09 11:30 | 668 | 668
2018-10-09 12:00 | 606 | 606
2018-10-09 12:30 | 590 | 590
2018-10-09 13:00 | 587 | 587
2018-10-09 13:30 | 599 | 598
2018-10-09 14:00 | 642 | 642
2018-10-09 14:30 | 663 | 662
2018-10-09 15:00 | 700 | 700
2018-10-09 15:30 | 769 | 767
2018-10-09 16:00 | 787 | 785
2018-10-09 16:30 | 824 | 822
2018-10-09 17:00 | 847 | 845
2018-10-09 17:30 | 874 | 872
2018-10-09 18:00 | 880 | 878
2018-10-09 18:30 | 894 | 893
2018-10-09 19:00 | 895 | 893
2018-10-09 19:30 | 873 | 870
2018-10-09 20:00 | 852 | 850
2018-10-09 20:30 | 838 | 835
2018-10-09 21:00 | 797 | 795
2018-10-09 21:30 | 762 | 758
2018-10-09 22:00 | 726 | 724
2018-10-09 22:30 | 713 | 711
2018-10-09 23:00 | 701 | 699
2018-10-09 23:30 | 659 | 655
2018-10-10 | 620 | 611
2018-10-10 00:30 | 579 | 564
2018-10-10 01:00 | 549 | 531
2018-10-10 01:30 | 538 | 517
2018-10-10 02:00 | 527 | 503
2018-10-10 02:30 | 525 | 500
2018-10-10 03:00 | 523 | 497
2018-10-10 03:30 | 524 | 497
2018-10-10 04:00 | 521 | 494
2018-10-10 04:30 | 536 | 512
2018-10-10 05:00 | 545 | 526
2018-10-10 05:30 | 564 | 548
2018-10-10 06:00 | 600 | 589
2018-10-10 06:30 | 648 | 644
2018-10-10 07:00 | 694 | 688
2018-10-10 07:30 | 715 | 709
2018-10-10 08:00 | 682 | 674
2018-10-10 08:30 | 656 | 651
2018-10-10 09:00 | 641 | 638
2018-10-10 09:30 | 650 | 650
2018-10-10 10:00 | 636 | 636
2018-10-10 10:30 | 620 | 619
2018-10-10 11:00 | 617 | 617
2018-10-10 11:30 | 608 | 605
2018-10-10 12:00 | 616 | 613
2018-10-10 12:30 | 612 | 611
2018-10-10 13:00 | 629 | 628
2018-10-10 13:30 | 658 | 657
2018-10-10 14:00 | 703 | 700
2018-10-10 14:30 | 733 | 728
2018-10-10 15:00 | 774 | 767
2018-10-10 15:30 | 811 | 802
2018-10-10 16:00 | 855 | 846
2018-10-10 16:30 | 884 | 876
2018-10-10 17:00 | 910 | 900
2018-10-10 17:30 | 922 | 910
2018-10-10 18:00 | 929 | 917
2018-10-10 18:30 | 940 | 930
2018-10-10 19:00 | 946 | 938
2018-10-10 19:30 | 919 | 910
2018-10-10 20:00 | 894 | 889
2018-10-10 20:30 | 875 | 868
2018-10-10 21:00 | 828 | 824
2018-10-10 21:30 | 771 | 769
2018-10-10 22:00 | 738 | 735
2018-10-10 22:30 | 723 | 720
2018-10-10 23:00 | 707 | 702
2018-10-10 23:30 | 661 | 657
2018-10-11 | 623 | 617
2018-10-11 00:30 | 577 | 565
2018-10-11 01:00 | 550 | 535
2018-10-11 01:30 | 535 | 516
2018-10-11 02:00 | 532 | 511
2018-10-11 02:30 | 527 | 503
2018-10-11 03:00 | 528 | 503
2018-10-11 03:30 | 531 | 506
2018-10-11 04:00 | 524 | 499
2018-10-11 04:30 | 532 | 511
2018-10-11 05:00 | 544 | 527
2018-10-11 05:30 | 568 | 555
2018-10-11 06:00 | 596 | 587
2018-10-11 06:30 | 653 | 649
2018-10-11 07:00 | 718 | 715
2018-10-11 07:30 | 730 | 727
2018-10-11 08:00 | 726 | 721
2018-10-11 08:30 | 711 | 706
2018-10-11 09:00 | 691 | 686
2018-10-11 09:30 | 685 | 682
2018-10-11 10:00 | 683 | 680
2018-10-11 10:30 | 718 | 714
2018-10-11 11:00 | 765 | 758
2018-10-11 11:30 | 785 | 776
2018-10-11 12:00 | 798 | 789
2018-10-11 12:30 | 814 | 804
2018-10-11 13:00 | 849 | 843
2018-10-11 13:30 | 845 | 839
2018-10-11 14:00 | 767 | 761
2018-10-11 14:30 | 713 | 712
2018-10-11 15:00 | 764 | 764
2018-10-11 15:30 | 781 | 781
2018-10-11 16:00 | 789 | 789
2018-10-11 16:30 | 806 | 804
2018-10-11 17:00 | 832 | 830
2018-10-11 17:30 | 858 | 857
2018-10-11 18:00 | 892 | 892
2018-10-11 18:30 | 933 | 933
2018-10-11 19:00 | 919 | 917
2018-10-11 19:30 | 944 | 941
2018-10-11 20:00 | 943 | 941
2018-10-11 20:30 | 921 | 919
2018-10-11 21:00 | 815 | 814
2018-10-11 21:30 | 766 | 765
2018-10-11 22:00 | 725 | 723
2018-10-11 22:30 | 710 | 707
2018-10-11 23:00 | 702 | 698
2018-10-11 23:30 | 662 | 656
2018-10-12 | 609 | 600
2018-10-12 00:30 | 573 | 558
2018-10-12 01:00 | 543 | 523
2018-10-12 01:30 | 531 | 507
2018-10-12 02:00 | 524 | 499
2018-10-12 02:30 | 517 | 489
2018-10-12 03:00 | 513 | 484
2018-10-12 03:30 | 516 | 487
2018-10-12 04:00 | 517 | 488
2018-10-12 04:30 | 524 | 497
2018-10-12 05:00 | 536 | 513
2018-10-12 05:30 | 564 | 546
2018-10-12 06:00 | 597 | 585
2018-10-12 06:30 | 657 | 653
2018-10-12 07:00 | 692 | 691
2018-10-12 07:30 | 727 | 725
2018-10-12 08:00 | 740 | 739
2018-10-12 08:30 | 769 | 769
2018-10-12 09:00 | 769 | 769
2018-10-12 09:30 | 747 | 747
2018-10-12 10:00 | 759 | 759
2018-10-12 10:30 | 753 | 753
2018-10-12 11:00 | 755 | 755
2018-10-12 11:30 | 746 | 746
2018-10-12 12:00 | 744 | 744
2018-10-12 12:30 | 749 | 749
2018-10-12 13:00 | 758 | 758
2018-10-12 13:30 | 764 | 764
2018-10-12 14:00 | 795 | 795
2018-10-12 14:30 | 808 | 808
2018-10-12 15:00 | 805 | 805
2018-10-12 15:30 | 794 | 794
2018-10-12 16:00 | 796 | 795
2018-10-12 16:30 | 819 | 819
2018-10-12 17:00 | 848 | 848
2018-10-12 17:30 | 859 | 859
2018-10-12 18:00 | 855 | 855
2018-10-12 18:30 | 864 | 862
2018-10-12 19:00 | 868 | 866
2018-10-12 19:30 | 848 | 845
2018-10-12 20:00 | 831 | 825
2018-10-12 20:30 | 806 | 805
2018-10-12 21:00 | 773 | 772
2018-10-12 21:30 | 737 | 734
2018-10-12 22:00 | 716 | 712
2018-10-12 22:30 | 697 | 692
2018-10-12 23:00 | 695 | 692
2018-10-12 23:30 | 660 | 654
2018-10-13 | 619 | 609
2018-10-13 00:30 | 582 | 567
2018-10-13 01:00 | 550 | 529
2018-10-13 01:30 | 536 | 512
2018-10-13 02:00 | 526 | 497
2018-10-13 02:30 | 515 | 485
2018-10-13 03:00 | 514 | 483
2018-10-13 03:30 | 512 | 480
2018-10-13 04:00 | 515 | 482
2018-10-13 04:30 | 511 | 478
2018-10-13 05:00 | 517 | 484
2018-10-13 05:30 | 525 | 494
2018-10-13 06:00 | 533 | 500
2018-10-13 06:30 | 581 | 558
2018-10-13 07:00 | 624 | 610
2018-10-13 07:30 | 662 | 655
2018-10-13 08:00 | 642 | 636
2018-10-13 08:30 | 679 | 676
2018-10-13 09:00 | 720 | 719
2018-10-13 09:30 | 743 | 742
2018-10-13 10:00 | 747 | 747
2018-10-13 10:30 | 741 | 741
2018-10-13 11:00 | 730 | 730
2018-10-13 11:30 | 720 | 719
2018-10-13 12:00 | 706 | 705
2018-10-13 12:30 | 702 | 700
2018-10-13 13:00 | 705 | 703
2018-10-13 13:30 | 695 | 693
2018-10-13 14:00 | 695 | 693
2018-10-13 14:30 | 708 | 706
2018-10-13 15:00 | 705 | 703
2018-10-13 15:30 | 713 | 710
2018-10-13 16:00 | 719 | 716
2018-10-13 16:30 | 734 | 733
2018-10-13 17:00 | 762 | 760
2018-10-13 17:30 | 768 | 767
2018-10-13 18:00 | 787 | 787
2018-10-13 18:30 | 809 | 809
2018-10-13 19:00 | 825 | 824
2018-10-13 19:30 | 805 | 803
2018-10-13 20:00 | 788 | 784
2018-10-13 20:30 | 772 | 767
2018-10-13 21:00 | 743 | 740
2018-10-13 21:30 | 715 | 712
2018-10-13 22:00 | 703 | 698
2018-10-13 22:30 | 701 | 695
2018-10-13 23:00 | 708 | 702
2018-10-13 23:30 | 678 | 670
2018-10-14 | 640 | 627
2018-10-14 00:30 | 599 | 580
2018-10-14 01:00 | 575 | 552
2018-10-14 01:30 | 561 | 535
2018-10-14 02:00 | 554 | 525
2018-10-14 02:30 | 548 | 516
2018-10-14 03:00 | 547 | 513
2018-10-14 03:30 | 539 | 505
2018-10-14 04:00 | 539 | 504
2018-10-14 04:30 | 542 | 507
2018-10-14 05:00 | 543 | 507
2018-10-14 05:30 | 543 | 508
2018-10-14 06:00 | 541 | 504
2018-10-14 06:30 | 556 | 522
2018-10-14 07:00 | 563 | 533
2018-10-14 07:30 | 593 | 571
2018-10-14 08:00 | 629 | 614
2018-10-14 08:30 | 666 | 658
2018-10-14 09:00 | 696 | 690
2018-10-14 09:30 | 712 | 708
2018-10-14 10:00 | 726 | 723
2018-10-14 10:30 | 745 | 743
2018-10-14 11:00 | 722 | 720
2018-10-14 11:30 | 723 | 721
2018-10-14 12:00 | 734 | 732
2018-10-14 12:30 | 741 | 739
2018-10-14 13:00 | 723 | 720
2018-10-14 13:30 | 718 | 716
2018-10-14 14:00 | 721 | 719
2018-10-14 14:30 | 732 | 729
2018-10-14 15:00 | 729 | 727
2018-10-14 15:30 | 739 | 736
2018-10-14 16:00 | 751 | 749
2018-10-14 16:30 | 775 | 774
2018-10-14 17:00 | 808 | 806
2018-10-14 17:30 | 833 | 831
2018-10-14 18:00 | 846 | 845
2018-10-14 18:30 | 871 | 869
2018-10-14 19:00 | 883 | 882
2018-10-14 19:30 | 863 | 860
2018-10-14 20:00 | 845 | 841
2018-10-14 20:30 | 830 | 829
2018-10-14 21:00 | 802 | 801
2018-10-14 21:30 | 765 | 762
2018-10-14 22:00 | 738 | 735
2018-10-14 22:30 | 728 | 723
2018-10-14 23:00 | 723 | 718
2018-10-14 23:30 | 693 | 686
2018-10-15 | 661 | 651
2018-10-15 00:30 | 625 | 609
2018-10-15 01:00 | 593 | 572
2018-10-15 01:30 | 575 | 551
2018-10-15 02:00 | 570 | 543
2018-10-15 02:30 | 561 | 531
2018-10-15 03:00 | 555 | 523
2018-10-15 03:30 | 551 | 518
2018-10-15 04:00 | 550 | 519
2018-10-15 04:30 | 571 | 543
2018-10-15 05:00 | 581 | 557
2018-10-15 05:30 | 604 | 588
2018-10-15 06:00 | 637 | 627
2018-10-15 06:30 | 702 | 697
2018-10-15 07:00 | 769 | 767
2018-10-15 07:30 | 846 | 845
2018-10-15 08:00 | 866 | 865
2018-10-15 08:30 | 864 | 863
2018-10-15 09:00 | 858 | 858
2018-10-15 09:30 | 857 | 856
2018-10-15 10:00 | 854 | 854
2018-10-15 10:30 | 858 | 858
2018-10-15 11:00 | 860 | 860
2018-10-15 11:30 | 861 | 861
2018-10-15 12:00 | 850 | 850
2018-10-15 12:30 | 824 | 824
2018-10-15 13:00 | 790 | 789
2018-10-15 13:30 | 783 | 782
2018-10-15 14:00 | 808 | 808
2018-10-15 14:30 | 827 | 827
2018-10-15 15:00 | 826 | 826
2018-10-15 15:30 | 831 | 830
2018-10-15 16:00 | 841 | 840
2018-10-15 16:30 | 866 | 866
2018-10-15 17:00 | 903 | 902
2018-10-15 17:30 | 926 | 926
2018-10-15 18:00 | 941 | 940
2018-10-15 18:30 | 968 | 968
2018-10-15 19:00 | 976 | 976
2018-10-15 19:30 | 954 | 949
2018-10-15 20:00 | 939 | 934
2018-10-15 20:30 | 907 | 907
2018-10-15 21:00 | 870 | 870
2018-10-15 21:30 | 823 | 822
2018-10-15 22:00 | 783 | 780
2018-10-15 22:30 | 763 | 761
2018-10-15 23:00 | 755 | 754
2018-10-15 23:30 | 717 | 713
2018-10-16 | 673 | 666
2018-10-16 00:30 | 628 | 616
2018-10-16 01:00 | 605 | 589
2018-10-16 01:30 | 590 | 570
2018-10-16 02:00 | 577 | 554
2018-10-16 02:30 | 570 | 547
2018-10-16 03:00 | 567 | 543
2018-10-16 03:30 | 565 | 542
2018-10-16 04:00 | 570 | 546
2018-10-16 04:30 | 583 | 563
2018-10-16 05:00 | 593 | 576
2018-10-16 05:30 | 611 | 599
2018-10-16 06:00 | 640 | 632
2018-10-16 06:30 | 711 | 709
2018-10-16 07:00 | 749 | 748
2018-10-16 07:30 | 809 | 809
2018-10-16 08:00 | 816 | 816
2018-10-16 08:30 | 810 | 810
2018-10-16 09:00 | 798 | 797
2018-10-16 09:30 | 786 | 785
2018-10-16 10:00 | 775 | 775
2018-10-16 10:30 | 765 | 764
2018-10-16 11:00 | 740 | 739
2018-10-16 11:30 | 737 | 736
2018-10-16 12:00 | 732 | 731
2018-10-16 12:30 | 721 | 720
2018-10-16 13:00 | 705 | 704
2018-10-16 13:30 | 738 | 737
2018-10-16 14:00 | 760 | 759
2018-10-16 14:30 | 774 | 772
2018-10-16 15:00 | 781 | 780
2018-10-16 15:30 | 793 | 792
2018-10-16 16:00 | 838 | 837
2018-10-16 16:30 | 875 | 875
2018-10-16 17:00 | 901 | 900
2018-10-16 17:30 | 926 | 925
2018-10-16 18:00 | 932 | 932
2018-10-16 18:30 | 962 | 962
2018-10-16 19:00 | 962 | 961
2018-10-16 19:30 | 937 | 937
2018-10-16 20:00 | 921 | 921
2018-10-16 20:30 | 909 | 909
2018-10-16 21:00 | 865 | 863
2018-10-16 21:30 | 821 | 818
2018-10-16 22:00 | 781 | 779
2018-10-16 22:30 | 766 | 762
2018-10-16 23:00 | 758 | 753
2018-10-16 23:30 | 711 | 709
2018-10-17 | 665 | 660
2018-10-17 00:30 | 621 | 612
2018-10-17 01:00 | 597 | 583
2018-10-17 01:30 | 582 | 566
2018-10-17 02:00 | 571 | 552
2018-10-17 02:30 | 570 | 550
2018-10-17 03:00 | 564 | 542
2018-10-17 03:30 | 558 | 537
2018-10-17 04:00 | 565 | 544
2018-10-17 04:30 | 570 | 552
2018-10-17 05:00 | 584 | 569
2018-10-17 05:30 | 609 | 598
2018-10-17 06:00 | 642 | 635
2018-10-17 06:30 | 698 | 697
2018-10-17 07:00 | 744 | 741
2018-10-17 07:30 | 782 | 780
2018-10-17 08:00 | 801 | 798
2018-10-17 08:30 | 792 | 789
2018-10-17 09:00 | 792 | 790
2018-10-17 09:30 | 783 | 782
2018-10-17 10:00 | 764 | 762
2018-10-17 10:30 | 761 | 758
2018-10-17 11:00 | 762 | 759
2018-10-17 11:30 | 751 | 748
2018-10-17 12:00 | 748 | 745
2018-10-17 12:30 | 749 | 746
2018-10-17 13:00 | 750 | 747
2018-10-17 13:30 | 740 | 736
2018-10-17 14:00 | 778 | 776
2018-10-17 14:30 | 828 | 826
2018-10-17 15:00 | 825 | 823
2018-10-17 15:30 | 806 | 803
2018-10-17 16:00 | 843 | 841
2018-10-17 16:30 | 875 | 873
2018-10-17 17:00 | 900 | 898
2018-10-17 17:30 | 916 | 913
2018-10-17 18:00 | 922 | 918
2018-10-17 18:30 | 940 | 938
2018-10-17 19:00 | 958 | 956
2018-10-17 19:30 | 928 | 926
2018-10-17 20:00 | 908 | 908
2018-10-17 20:30 | 896 | 896
2018-10-17 21:00 | 859 | 859
2018-10-17 21:30 | 817 | 817
2018-10-17 22:00 | 791 | 791
2018-10-17 22:30 | 766 | 766
2018-10-17 23:00 | 754 | 753
2018-10-17 23:30 | 718 | 716
2018-10-18 | 678 | 675
2018-10-18 00:30 | 628 | 619
2018-10-18 01:00 | 591 | 578
2018-10-18 01:30 | 568 | 553
2018-10-18 02:00 | 570 | 552
2018-10-18 02:30 | 609 | 591
2018-10-18 03:00 | 610 | 591
2018-10-18 03:30 | 607 | 589
2018-10-18 04:00 | 615 | 599
2018-10-18 04:30 | 623 | 608
2018-10-18 05:00 | 619 | 606
2018-10-18 05:30 | 615 | 606
2018-10-18 06:00 | 648 | 642
2018-10-18 06:30 | 718 | 716
2018-10-18 07:00 | 776 | 770
2018-10-18 07:30 | 825 | 819
2018-10-18 08:00 | 828 | 823
2018-10-18 08:30 | 827 | 821
2018-10-18 09:00 | 825 | 821
2018-10-18 09:30 | 821 | 818
2018-10-18 10:00 | 806 | 804
2018-10-18 10:30 | 798 | 797
2018-10-18 11:00 | 795 | 793
2018-10-18 11:30 | 778 | 776
2018-10-18 12:00 | 829 | 827
2018-10-18 12:30 | 846 | 846
2018-10-18 13:00 | 800 | 800
2018-10-18 13:30 | 835 | 835
2018-10-18 14:00 | 866 | 865
2018-10-18 14:30 | 885 | 885
2018-10-18 15:00 | 911 | 911
2018-10-18 15:30 | 917 | 916
2018-10-18 16:00 | 912 | 912
2018-10-18 16:30 | 926 | 925
2018-10-18 17:00 | 917 | 916
2018-10-18 17:30 | 948 | 947
2018-10-18 18:00 | 1005 | 1004
2018-10-18 18:30 | 1020 | 1020
2018-10-18 19:00 | 1000 | 997
2018-10-18 19:30 | 1012 | 1008
2018-10-18 20:00 | 931 | 926
2018-10-18 20:30 | 914 | 912
2018-10-18 21:00 | 875 | 874
2018-10-18 21:30 | 841 | 841
2018-10-18 22:00 | 794 | 793
2018-10-18 22:30 | 777 | 777
2018-10-18 23:00 | 765 | 764
2018-10-18 23:30 | 725 | 723
2018-10-19 | 683 | 679
2018-10-19 00:30 | 632 | 624
2018-10-19 01:00 | 591 | 579
2018-10-19 01:30 | 575 | 559
2018-10-19 02:00 | 568 | 551
2018-10-19 02:30 | 565 | 546
2018-10-19 03:00 | 561 | 540
2018-10-19 03:30 | 561 | 540
2018-10-19 04:00 | 560 | 539
2018-10-19 04:30 | 566 | 547
2018-10-19 05:00 | 580 | 565
2018-10-19 05:30 | 604 | 591
2018-10-19 06:00 | 575 | 561
2018-10-19 06:30 | 610 | 605
2018-10-19 07:00 | 647 | 645
2018-10-19 07:30 | 685 | 685
2018-10-19 08:00 | 699 | 696
2018-10-19 08:30 | 692 | 691
2018-10-19 09:00 | 687 | 687
2018-10-19 09:30 | 671 | 670
2018-10-19 10:00 | 653 | 653
2018-10-19 10:30 | 684 | 683
2018-10-19 11:00 | 693 | 693
2018-10-19 11:30 | 722 | 721
2018-10-19 12:00 | 716 | 716
2018-10-19 12:30 | 679 | 679
2018-10-19 13:00 | 719 | 718
2018-10-19 13:30 | 774 | 774
2018-10-19 14:00 | 781 | 781
2018-10-19 14:30 | 746 | 745
2018-10-19 15:00 | 725 | 724
2018-10-19 15:30 | 739 | 738
2018-10-19 16:00 | 781 | 780
2018-10-19 16:30 | 873 | 872
2018-10-19 17:00 | 857 | 856
2018-10-19 17:30 | 837 | 836
2018-10-19 18:00 | 832 | 829
2018-10-19 18:30 | 850 | 848
2018-10-19 19:00 | 869 | 868
2018-10-19 19:30 | 851 | 849
2018-10-19 20:00 | 832 | 831
2018-10-19 20:30 | 809 | 809
2018-10-19 21:00 | 774 | 774
2018-10-19 21:30 | 740 | 740
2018-10-19 22:00 | 715 | 714
2018-10-19 22:30 | 706 | 704
2018-10-19 23:00 | 699 | 696
2018-10-19 23:30 | 658 | 652
2018-10-20 | 622 | 613
2018-10-20 00:30 | 579 | 562
2018-10-20 01:00 | 555 | 532
2018-10-20 01:30 | 542 | 516
2018-10-20 02:00 | 533 | 504
2018-10-20 02:30 | 527 | 496
2018-10-20 03:00 | 522 | 489
2018-10-20 03:30 | 519 | 486
2018-10-20 04:00 | 517 | 484
2018-10-20 04:30 | 517 | 485
2018-10-20 05:00 | 523 | 492
2018-10-20 05:30 | 530 | 496
2018-10-20 06:00 | 539 | 506
2018-10-20 06:30 | 543 | 516
2018-10-20 07:00 | 546 | 529
2018-10-20 07:30 | 556 | 548
2018-10-20 08:00 | 581 | 576
2018-10-20 08:30 | 621 | 620
2018-10-20 09:00 | 624 | 624
2018-10-20 09:30 | 629 | 629
2018-10-20 10:00 | 619 | 618
2018-10-20 10:30 | 604 | 602
2018-10-20 11:00 | 586 | 583
2018-10-20 11:30 | 569 | 564
2018-10-20 12:00 | 550 | 548
2018-10-20 12:30 | 550 | 549
2018-10-20 13:00 | 551 | 549
2018-10-20 13:30 | 552 | 551
2018-10-20 14:00 | 556 | 555
2018-10-20 14:30 | 570 | 568
2018-10-20 15:00 | 588 | 587
2018-10-20 15:30 | 626 | 625
2018-10-20 16:00 | 659 | 659
2018-10-20 16:30 | 694 | 694
2018-10-20 17:00 | 728 | 728
2018-10-20 17:30 | 751 | 751
2018-10-20 18:00 | 764 | 764
2018-10-20 18:30 | 795 | 795
2018-10-20 19:00 | 821 | 820
2018-10-20 19:30 | 795 | 793
2018-10-20 20:00 | 806 | 805
2018-10-20 20:30 | 814 | 812
2018-10-20 21:00 | 764 | 764
2018-10-20 21:30 | 699 | 697
2018-10-20 22:00 | 684 | 680
2018-10-20 22:30 | 674 | 671
2018-10-20 23:00 | 675 | 670
2018-10-20 23:30 | 649 | 642
2018-10-21 | 612 | 601
2018-10-21 00:30 | 571 | 551
2018-10-21 01:00 | 543 | 518
2018-10-21 01:30 | 532 | 503
2018-10-21 02:00 | 519 | 488
2018-10-21 02:30 | 512 | 479
2018-10-21 03:00 | 505 | 471
2018-10-21 03:30 | 508 | 472
2018-10-21 04:00 | 503 | 467
2018-10-21 04:30 | 505 | 470
2018-10-21 05:00 | 506 | 471
2018-10-21 05:30 | 507 | 471
2018-10-21 06:00 | 511 | 476
2018-10-21 06:30 | 528 | 495
2018-10-21 07:00 | 533 | 504
2018-10-21 07:30 | 541 | 519
2018-10-21 08:00 | 552 | 536
2018-10-21 08:30 | 583 | 574
2018-10-21 09:00 | 589 | 582
2018-10-21 09:30 | 593 | 589
2018-10-21 10:00 | 585 | 582
2018-10-21 10:30 | 604 | 603
2018-10-21 11:00 | 593 | 593
2018-10-21 11:30 | 598 | 597
2018-10-21 12:00 | 601 | 600
2018-10-21 12:30 | 596 | 595
2018-10-21 13:00 | 601 | 600
2018-10-21 13:30 | 585 | 584
2018-10-21 14:00 | 665 | 665
2018-10-21 14:30 | 747 | 747
2018-10-21 15:00 | 764 | 764
2018-10-21 15:30 | 767 | 766
2018-10-21 16:00 | 757 | 757
2018-10-21 16:30 | 749 | 749
2018-10-21 17:00 | 752 | 752
2018-10-21 17:30 | 738 | 738
2018-10-21 18:00 | 732 | 731
2018-10-21 18:30 | 755 | 755
2018-10-21 19:00 | 774 | 774
2018-10-21 19:30 | 754 | 754
2018-10-21 20:00 | 739 | 739
2018-10-21 20:30 | 724 | 723
2018-10-21 21:00 | 699 | 697
2018-10-21 21:30 | 666 | 662
2018-10-21 22:00 | 657 | 650
2018-10-21 22:30 | 652 | 643
2018-10-21 23:00 | 650 | 641
2018-10-21 23:30 | 622 | 610
2018-10-22 | 579 | 561
2018-10-22 00:30 | 545 | 521
2018-10-22 01:00 | 519 | 490
2018-10-22 01:30 | 510 | 480
2018-10-22 02:00 | 501 | 469
2018-10-22 02:30 | 499 | 465
2018-10-22 03:00 | 500 | 461
2018-10-22 03:30 | 511 | 472
2018-10-22 04:00 | 510 | 471
2018-10-22 04:30 | 516 | 480
2018-10-22 05:00 | 525 | 494
2018-10-22 05:30 | 555 | 524
2018-10-22 06:00 | 578 | 554
2018-10-22 06:30 | 603 | 592
2018-10-22 07:00 | 624 | 619
2018-10-22 07:30 | 646 | 645
2018-10-22 08:00 | 652 | 652
2018-10-22 08:30 | 661 | 661
2018-10-22 09:00 | 675 | 675
2018-10-22 09:30 | 687 | 687
2018-10-22 10:00 | 671 | 671
2018-10-22 10:30 | 672 | 672
2018-10-22 11:00 | 671 | 670
2018-10-22 11:30 | 686 | 686
2018-10-22 12:00 | 695 | 694
2018-10-22 12:30 | 701 | 701
2018-10-22 13:00 | 705 | 705
2018-10-22 13:30 | 719 | 719
2018-10-22 14:00 | 733 | 732
2018-10-22 14:30 | 743 | 741
2018-10-22 15:00 | 752 | 751
2018-10-22 15:30 | 761 | 759
2018-10-22 16:00 | 780 | 778
2018-10-22 16:30 | 806 | 804
2018-10-22 17:00 | 831 | 830
2018-10-22 17:30 | 856 | 854
2018-10-22 18:00 | 859 | 854
2018-10-22 18:30 | 871 | 868
2018-10-22 19:00 | 896 | 894
2018-10-22 19:30 | 869 | 865
2018-10-22 20:00 | 851 | 848
2018-10-22 20:30 | 834 | 829
2018-10-22 21:00 | 788 | 784
2018-10-22 21:30 | 737 | 735
2018-10-22 22:00 | 704 | 699
2018-10-22 22:30 | 685 | 680
2018-10-22 23:00 | 676 | 671
2018-10-22 23:30 | 648 | 640
2018-10-23 | 605 | 592
2018-10-23 00:30 | 564 | 545
2018-10-23 01:00 | 538 | 515
2018-10-23 01:30 | 524 | 498
2018-10-23 02:00 | 515 | 487
2018-10-23 02:30 | 514 | 483
2018-10-23 03:00 | 508 | 476
2018-10-23 03:30 | 511 | 479
2018-10-23 04:00 | 512 | 480
2018-10-23 04:30 | 521 | 493
2018-10-23 05:00 | 533 | 507
2018-10-23 05:30 | 555 | 533
2018-10-23 06:00 | 584 | 568
2018-10-23 06:30 | 616 | 610
2018-10-23 07:00 | 649 | 648
2018-10-23 07:30 | 676 | 676
2018-10-23 08:00 | 691 | 690
2018-10-23 08:30 | 679 | 679
2018-10-23 09:00 | 669 | 668
2018-10-23 09:30 | 664 | 664
2018-10-23 10:00 | 667 | 667
2018-10-23 10:30 | 658 | 658
2018-10-23 11:00 | 654 | 654
2018-10-23 11:30 | 654 | 653
2018-10-23 12:00 | 665 | 664
2018-10-23 12:30 | 669 | 668
2018-10-23 13:00 | 671 | 671
2018-10-23 13:30 | 687 | 686
2018-10-23 14:00 | 707 | 707
2018-10-23 14:30 | 730 | 729
2018-10-23 15:00 | 747 | 746
2018-10-23 15:30 | 759 | 758
2018-10-23 16:00 | 809 | 803
2018-10-23 16:30 | 842 | 836
2018-10-23 17:00 | 867 | 861
2018-10-23 17:30 | 879 | 870
2018-10-23 18:00 | 877 | 867
2018-10-23 18:30 | 889 | 882
2018-10-23 19:00 | 909 | 903
2018-10-23 19:30 | 877 | 876
2018-10-23 20:00 | 860 | 857
2018-10-23 20:30 | 839 | 836
2018-10-23 21:00 | 788 | 787
2018-10-23 21:30 | 744 | 743
2018-10-23 22:00 | 706 | 704
2018-10-23 22:30 | 694 | 692
2018-10-23 23:00 | 680 | 676
2018-10-23 23:30 | 645 | 637
2018-10-24 | 604 | 591
2018-10-24 00:30 | 561 | 543
2018-10-24 01:00 | 543 | 521
2018-10-24 01:30 | 535 | 509
2018-10-24 02:00 | 525 | 497
2018-10-24 02:30 | 521 | 493
2018-10-24 03:00 | 519 | 489
2018-10-24 03:30 | 522 | 492
2018-10-24 04:00 | 519 | 489
2018-10-24 04:30 | 530 | 502
2018-10-24 05:00 | 536 | 512
2018-10-24 05:30 | 556 | 535
2018-10-24 06:00 | 565 | 551
2018-10-24 06:30 | 598 | 594
2018-10-24 07:00 | 637 | 637
2018-10-24 07:30 | 683 | 683
2018-10-24 08:00 | 697 | 697
2018-10-24 08:30 | 698 | 697
2018-10-24 09:00 | 688 | 688
2018-10-24 09:30 | 688 | 688
2018-10-24 10:00 | 687 | 687
2018-10-24 10:30 | 692 | 691
2018-10-24 11:00 | 706 | 705
2018-10-24 11:30 | 714 | 714
2018-10-24 12:00 | 737 | 737
2018-10-24 12:30 | 744 | 743
2018-10-24 13:00 | 764 | 763
2018-10-24 13:30 | 810 | 810
2018-10-24 14:00 | 833 | 832
2018-10-24 14:30 | 847 | 847
2018-10-24 15:00 | 858 | 858
2018-10-24 15:30 | 865 | 865
2018-10-24 16:00 | 920 | 920
2018-10-24 16:30 | 953 | 952
2018-10-24 17:00 | 957 | 956
2018-10-24 17:30 | 957 | 955
2018-10-24 18:00 | 943 | 937
2018-10-24 18:30 | 951 | 945
2018-10-24 19:00 | 969 | 964
2018-10-24 19:30 | 948 | 939
2018-10-24 20:00 | 930 | 918
2018-10-24 20:30 | 891 | 887
2018-10-24 21:00 | 850 | 850
2018-10-24 21:30 | 799 | 799
2018-10-24 22:00 | 761 | 760
2018-10-24 22:30 | 741 | 740
2018-10-24 23:00 | 724 | 723
2018-10-24 23:30 | 678 | 675
2018-10-25 | 627 | 620
2018-10-25 00:30 | 581 | 571
2018-10-25 01:00 | 563 | 547
2018-10-25 01:30 | 549 | 530
2018-10-25 02:00 | 539 | 518
2018-10-25 02:30 | 535 | 514
2018-10-25 03:00 | 527 | 505
2018-10-25 03:30 | 526 | 503
2018-10-25 04:00 | 526 | 504
2018-10-25 04:30 | 532 | 512
2018-10-25 05:00 | 542 | 523
2018-10-25 05:30 | 559 | 544
2018-10-25 06:00 | 567 | 557
2018-10-25 06:30 | 613 | 610
2018-10-25 07:00 | 682 | 680
2018-10-25 07:30 | 728 | 724
2018-10-25 08:00 | 751 | 747
2018-10-25 08:30 | 770 | 768
2018-10-25 09:00 | 769 | 768
2018-10-25 09:30 | 759 | 759
2018-10-25 10:00 | 759 | 758
2018-10-25 10:30 | 773 | 773
2018-10-25 11:00 | 789 | 788
2018-10-25 11:30 | 750 | 748
2018-10-25 12:00 | 717 | 715
2018-10-25 12:30 | 724 | 722
2018-10-25 13:00 | 724 | 723
2018-10-25 13:30 | 724 | 723
2018-10-25 14:00 | 761 | 760
2018-10-25 14:30 | 781 | 781
2018-10-25 15:00 | 790 | 789
2018-10-25 15:30 | 849 | 849
2018-10-25 16:00 | 868 | 867
2018-10-25 16:30 | 892 | 890
2018-10-25 17:00 | 919 | 916
2018-10-25 17:30 | 934 | 931
2018-10-25 18:00 | 936 | 932
2018-10-25 18:30 | 951 | 947
2018-10-25 19:00 | 971 | 968
2018-10-25 19:30 | 946 | 943
2018-10-25 20:00 | 944 | 944
2018-10-25 20:30 | 897 | 896
2018-10-25 21:00 | 858 | 857
2018-10-25 21:30 | 800 | 799
2018-10-25 22:00 | 754 | 753
2018-10-25 22:30 | 727 | 727
2018-10-25 23:00 | 712 | 711
2018-10-25 23:30 | 671 | 668
2018-10-26 | 630 | 621
2018-10-26 00:30 | 590 | 575
2018-10-26 01:00 | 569 | 548
2018-10-26 01:30 | 561 | 537
2018-10-26 02:00 | 553 | 528
2018-10-26 02:30 | 554 | 528
2018-10-26 03:00 | 556 | 529
2018-10-26 03:30 | 559 | 532
2018-10-26 04:00 | 554 | 528
2018-10-26 04:30 | 561 | 537
2018-10-26 05:00 | 566 | 545
2018-10-26 05:30 | 589 | 572
2018-10-26 06:00 | 613 | 601
2018-10-26 06:30 | 663 | 658
2018-10-26 07:00 | 704 | 703
2018-10-26 07:30 | 745 | 745
2018-10-26 08:00 | 757 | 757
2018-10-26 08:30 | 759 | 759
2018-10-26 09:00 | 767 | 767
2018-10-26 09:30 | 782 | 782
2018-10-26 10:00 | 773 | 772
2018-10-26 10:30 | 781 | 780
2018-10-26 11:00 | 801 | 801
2018-10-26 11:30 | 807 | 806
2018-10-26 12:00 | 833 | 832
2018-10-26 12:30 | 841 | 839
2018-10-26 13:00 | 874 | 873
2018-10-26 13:30 | 896 | 895
2018-10-26 14:00 | 927 | 926
2018-10-26 14:30 | 958 | 957
2018-10-26 15:00 | 994 | 990
2018-10-26 15:30 | 1012 | 1008
2018-10-26 16:00 | 1044 | 1041
2018-10-26 16:30 | 1077 | 1074
2018-10-26 17:00 | 1088 | 1085
2018-10-26 17:30 | 1072 | 1064
2018-10-26 18:00 | 1029 | 1019
2018-10-26 18:30 | 1007 | 998
2018-10-26 19:00 | 1010 | 1004
2018-10-26 19:30 | 982 | 980
2018-10-26 20:00 | 958 | 957
2018-10-26 20:30 | 928 | 926
2018-10-26 21:00 | 880 | 880
2018-10-26 21:30 | 838 | 837
2018-10-26 22:00 | 808 | 806
2018-10-26 22:30 | 789 | 786
2018-10-26 23:00 | 777 | 772
2018-10-26 23:30 | 737 | 729
2018-10-27 | 697 | 681
2018-10-27 00:30 | 658 | 635
2018-10-27 01:00 | 637 | 607
2018-10-27 01:30 | 616 | 593
2018-10-27 02:00 | 598 | 581
2018-10-27 02:30 | 589 | 570
2018-10-27 03:00 | 585 | 564
2018-10-27 03:30 | 583 | 562
2018-10-27 04:00 | 582 | 559
2018-10-27 04:30 | 579 | 557
2018-10-27 05:00 | 579 | 556
2018-10-27 05:30 | 582 | 558
2018-10-27 06:00 | 590 | 568
2018-10-27 06:30 | 604 | 588
2018-10-27 07:00 | 607 | 597
2018-10-27 07:30 | 619 | 615
2018-10-27 08:00 | 637 | 636
2018-10-27 08:30 | 649 | 649
2018-10-27 09:00 | 660 | 660
2018-10-27 09:30 | 660 | 659
2018-10-27 10:00 | 656 | 655
2018-10-27 10:30 | 658 | 655
2018-10-27 11:00 | 650 | 648
2018-10-27 11:30 | 641 | 637
2018-10-27 12:00 | 641 | 637
2018-10-27 12:30 | 643 | 638
2018-10-27 13:00 | 644 | 640
2018-10-27 13:30 | 660 | 656
2018-10-27 14:00 | 674 | 671
2018-10-27 14:30 | 683 | 680
2018-10-27 15:00 | 709 | 706
2018-10-27 15:30 | 732 | 730
2018-10-27 16:00 | 761 | 759
2018-10-27 16:30 | 785 | 784
2018-10-27 17:00 | 813 | 812
2018-10-27 17:30 | 818 | 817
2018-10-27 18:00 | 820 | 817
2018-10-27 18:30 | 844 | 843
2018-10-27 19:00 | 870 | 869
2018-10-27 19:30 | 854 | 853
2018-10-27 20:00 | 838 | 836
2018-10-27 20:30 | 815 | 813
2018-10-27 21:00 | 774 | 774
2018-10-27 21:30 | 749 | 749
2018-10-27 22:00 | 730 | 729
2018-10-27 22:30 | 728 | 726
2018-10-27 23:00 | 726 | 724
2018-10-27 23:30 | 690 | 686
2018-10-28 | 658 | 649
2018-10-28 00:30 | 617 | 603
2018-10-28 01:00 | 598 | 580
2018-10-28 01:30 | 582 | 561
2018-10-28 02:00 | 572 | 549
2018-10-28 02:30 | 568 | 543
2018-10-28 03:00 | 562 | 538
2018-10-28 03:30 | 560 | 534
2018-10-28 04:00 | 553 | 527
2018-10-28 04:30 | 555 | 529
2018-10-28 05:00 | 555 | 527
2018-10-28 05:30 | 552 | 519
2018-10-28 06:00 | 559 | 528
2018-10-28 06:30 | 551 | 523
2018-10-28 07:00 | 558 | 538
2018-10-28 07:30 | 586 | 573
2018-10-28 08:00 | 582 | 573
2018-10-28 08:30 | 621 | 617
2018-10-28 09:00 | 649 | 647
2018-10-28 09:30 | 609 | 607
2018-10-28 10:00 | 695 | 695
2018-10-28 10:30 | 618 | 614
2018-10-28 11:00 | 561 | 560
2018-10-28 11:30 | 559 | 558
2018-10-28 12:00 | 568 | 567
2018-10-28 12:30 | 578 | 578
2018-10-28 13:00 | 589 | 589
2018-10-28 13:30 | 604 | 604
2018-10-28 14:00 | 626 | 626
2018-10-28 14:30 | 652 | 652
2018-10-28 15:00 | 696 | 695
2018-10-28 15:30 | 709 | 709
2018-10-28 16:00 | 725 | 725
2018-10-28 16:30 | 750 | 749
2018-10-28 17:00 | 774 | 773
2018-10-28 17:30 | 790 | 789
2018-10-28 18:00 | 800 | 800
2018-10-28 18:30 | 824 | 824
2018-10-28 19:00 | 833 | 833
2018-10-28 19:30 | 812 | 811
2018-10-28 20:00 | 793 | 791
2018-10-28 20:30 | 769 | 766
2018-10-28 21:00 | 735 | 731
2018-10-28 21:30 | 704 | 702
2018-10-28 22:00 | 675 | 671
2018-10-28 22:30 | 661 | 656
2018-10-28 23:00 | 663 | 656
2018-10-28 23:30 | 627 | 618
2018-10-29 | 590 | 578
2018-10-29 00:30 | 557 | 538
2018-10-29 01:00 | 534 | 512
2018-10-29 01:30 | 526 | 500
2018-10-29 02:00 | 518 | 490
2018-10-29 02:30 | 515 | 487
2018-10-29 03:00 | 512 | 483
2018-10-29 03:30 | 513 | 483
2018-10-29 04:00 | 515 | 487
2018-10-29 04:30 | 525 | 498
2018-10-29 05:00 | 536 | 515
2018-10-29 05:30 | 564 | 546
2018-10-29 06:00 | 599 | 589
2018-10-29 06:30 | 669 | 666
2018-10-29 07:00 | 724 | 723
2018-10-29 07:30 | 774 | 774
2018-10-29 08:00 | 808 | 808
2018-10-29 08:30 | 810 | 809
2018-10-29 09:00 | 814 | 814
2018-10-29 09:30 | 816 | 816
2018-10-29 10:00 | 817 | 817
2018-10-29 10:30 | 799 | 798
2018-10-29 11:00 | 809 | 809
2018-10-29 11:30 | 804 | 804
2018-10-29 12:00 | 805 | 805
2018-10-29 12:30 | 814 | 813
2018-10-29 13:00 | 821 | 821
2018-10-29 13:30 | 813 | 813
2018-10-29 14:00 | 803 | 802
2018-10-29 14:30 | 792 | 790
2018-10-29 15:00 | 792 | 790
2018-10-29 15:30 | 806 | 804
2018-10-29 16:00 | 829 | 827
2018-10-29 16:30 | 843 | 841
2018-10-29 17:00 | 864 | 862
2018-10-29 17:30 | 869 | 866
2018-10-29 18:00 | 873 | 872
2018-10-29 18:30 | 876 | 876
2018-10-29 19:00 | 891 | 891
2018-10-29 19:30 | 867 | 865
2018-10-29 20:00 | 839 | 839
2018-10-29 20:30 | 819 | 819
2018-10-29 21:00 | 783 | 783
2018-10-29 21:30 | 744 | 742
2018-10-29 22:00 | 716 | 713
2018-10-29 22:30 | 693 | 688
2018-10-29 23:00 | 688 | 682
2018-10-29 23:30 | 647 | 638
2018-10-30 | 613 | 598
2018-10-30 00:30 | 574 | 554
2018-10-30 01:00 | 549 | 526
2018-10-30 01:30 | 539 | 512
2018-10-30 02:00 | 530 | 502
2018-10-30 02:30 | 525 | 496
2018-10-30 03:00 | 519 | 490
2018-10-30 03:30 | 520 | 490
2018-10-30 04:00 | 519 | 489
2018-10-30 04:30 | 530 | 502
2018-10-30 05:00 | 542 | 517
2018-10-30 05:30 | 565 | 542
2018-10-30 06:00 | 594 | 578
2018-10-30 06:30 | 630 | 625
2018-10-30 07:00 | 664 | 662
2018-10-30 07:30 | 687 | 687
2018-10-30 08:00 | 682 | 682
2018-10-30 08:30 | 690 | 690
2018-10-30 09:00 | 706 | 706
2018-10-30 09:30 | 715 | 714
2018-10-30 10:00 | 723 | 722
2018-10-30 10:30 | 720 | 719
2018-10-30 11:00 | 711 | 711
2018-10-30 11:30 | 691 | 691
2018-10-30 12:00 | 678 | 678
2018-10-30 12:30 | 683 | 683
2018-10-30 13:00 | 677 | 676
2018-10-30 13:30 | 666 | 666
2018-10-30 14:00 | 672 | 672
2018-10-30 14:30 | 672 | 672
2018-10-30 15:00 | 681 | 681
2018-10-30 15:30 | 706 | 706
2018-10-30 16:00 | 748 | 747
2018-10-30 16:30 | 791 | 790
2018-10-30 17:00 | 833 | 833
2018-10-30 17:30 | 852 | 851
2018-10-30 18:00 | 855 | 853
2018-10-30 18:30 | 874 | 873
2018-10-30 19:00 | 905 | 905
2018-10-30 19:30 | 888 | 887
2018-10-30 20:00 | 873 | 871
2018-10-30 20:30 | 852 | 849
2018-10-30 21:00 | 803 | 803
2018-10-30 21:30 | 758 | 758
2018-10-30 22:00 | 727 | 726
2018-10-30 22:30 | 701 | 698
2018-10-30 23:00 | 692 | 688
2018-10-30 23:30 | 654 | 648
2018-10-31 | 609 | 598
2018-10-31 00:30 | 573 | 557
2018-10-31 01:00 | 546 | 526
2018-10-31 01:30 | 540 | 516
2018-10-31 02:00 | 528 | 501
2018-10-31 02:30 | 524 | 498
2018-10-31 03:00 | 520 | 493
2018-10-31 03:30 | 521 | 493
2018-10-31 04:00 | 523 | 497
2018-10-31 04:30 | 533 | 509
2018-10-31 05:00 | 544 | 520
2018-10-31 05:30 | 570 | 549
2018-10-31 06:00 | 595 | 582
2018-10-31 06:30 | 630 | 625
2018-10-31 07:00 | 674 | 673
2018-10-31 07:30 | 692 | 692
2018-10-31 08:00 | 692 | 692
2018-10-31 08:30 | 687 | 687
2018-10-31 09:00 | 677 | 677
2018-10-31 09:30 | 685 | 684
2018-10-31 10:00 | 664 | 664
2018-10-31 10:30 | 639 | 639
2018-10-31 11:00 | 624 | 623
2018-10-31 11:30 | 629 | 629
2018-10-31 12:00 | 634 | 634
2018-10-31 12:30 | 648 | 648
2018-10-31 13:00 | 669 | 668
2018-10-31 13:30 | 679 | 678
2018-10-31 14:00 | 702 | 701
2018-10-31 14:30 | 741 | 741
2018-10-31 15:00 | 762 | 762
2018-10-31 15:30 | 797 | 797
2018-10-31 16:00 | 843 | 843
2018-10-31 16:30 | 881 | 880
2018-10-31 17:00 | 905 | 905
2018-10-31 17:30 | 910 | 910
2018-10-31 18:00 | 891 | 890
2018-10-31 18:30 | 892 | 892
2018-10-31 19:00 | 919 | 918
2018-10-31 19:30 | 903 | 903
2018-10-31 20:00 | 889 | 889
2018-10-31 20:30 | 863 | 863
2018-10-31 21:00 | 822 | 822
2018-10-31 21:30 | 781 | 780
2018-10-31 22:00 | 745 | 742
2018-10-31 22:30 | 722 | 717
2018-10-31 23:00 | 686 | 682
2018-10-31 23:30 | 661 | 655
2018-11-01 | 620 | 609
2018-11-01 00:30 | 576 | 559
2018-11-01 01:00 | 551 | 530
2018-11-01 01:30 | 541 | 517
2018-11-01 02:00 | 528 | 502
2018-11-01 02:30 | 524 | 496
2018-11-01 03:00 | 521 | 493
2018-11-01 03:30 | 524 | 497
2018-11-01 04:00 | 525 | 499
2018-11-01 04:30 | 533 | 509
2018-11-01 05:00 | 544 | 521
2018-11-01 05:30 | 566 | 546
2018-11-01 06:00 | 593 | 581
2018-11-01 06:30 | 632 | 628
2018-11-01 07:00 | 664 | 664
2018-11-01 07:30 | 695 | 695
2018-11-01 08:00 | 695 | 695
2018-11-01 08:30 | 701 | 701
2018-11-01 09:00 | 697 | 697
2018-11-01 09:30 | 693 | 693
2018-11-01 10:00 | 686 | 686
2018-11-01 10:30 | 674 | 674
2018-11-01 11:00 | 663 | 663
2018-11-01 11:30 | 665 | 665
2018-11-01 12:00 | 672 | 672
2018-11-01 12:30 | 675 | 675
2018-11-01 13:00 | 687 | 687
2018-11-01 13:30 | 697 | 697
2018-11-01 14:00 | 718 | 718
2018-11-01 14:30 | 746 | 744
2018-11-01 15:00 | 770 | 769
2018-11-01 15:30 | 794 | 793
2018-11-01 16:00 | 830 | 829
2018-11-01 16:30 | 869 | 868
2018-11-01 17:00 | 902 | 902
2018-11-01 17:30 | 917 | 916
2018-11-01 18:00 | 912 | 909
2018-11-01 18:30 | 920 | 917
2018-11-01 19:00 | 950 | 948
2018-11-01 19:30 | 932 | 930
2018-11-01 20:00 | 912 | 912
2018-11-01 20:30 | 891 | 890
2018-11-01 21:00 | 842 | 841
2018-11-01 21:30 | 790 | 790
2018-11-01 22:00 | 748 | 746
2018-11-01 22:30 | 727 | 723
2018-11-01 23:00 | 714 | 708
2018-11-01 23:30 | 674 | 666
2018-11-02 | 619 | 610
2018-11-02 00:30 | 579 | 566
2018-11-02 01:00 | 558 | 540
2018-11-02 01:30 | 544 | 524
2018-11-02 02:00 | 538 | 515
2018-11-02 02:30 | 532 | 508
2018-11-02 03:00 | 529 | 504
2018-11-02 03:30 | 529 | 504
2018-11-02 04:00 | 530 | 506
2018-11-02 04:30 | 536 | 514
2018-11-02 05:00 | 546 | 525
2018-11-02 05:30 | 576 | 558
2018-11-02 06:00 | 595 | 583
2018-11-02 06:30 | 642 | 639
2018-11-02 07:00 | 679 | 678
2018-11-02 07:30 | 708 | 708
2018-11-02 08:00 | 719 | 719
2018-11-02 08:30 | 717 | 717
2018-11-02 09:00 | 704 | 703
2018-11-02 09:30 | 684 | 684
2018-11-02 10:00 | 679 | 679
2018-11-02 10:30 | 663 | 663
2018-11-02 11:00 | 651 | 651
2018-11-02 11:30 | 616 | 616
2018-11-02 12:00 | 639 | 639
2018-11-02 12:30 | 646 | 646
2018-11-02 13:00 | 622 | 622
2018-11-02 13:30 | 677 | 675
2018-11-02 14:00 | 709 | 707
2018-11-02 14:30 | 725 | 723
2018-11-02 15:00 | 741 | 740
2018-11-02 15:30 | 773 | 772
2018-11-02 16:00 | 813 | 812
2018-11-02 16:30 | 858 | 857
2018-11-02 17:00 | 880 | 878
2018-11-02 17:30 | 882 | 876
2018-11-02 18:00 | 863 | 856
2018-11-02 18:30 | 862 | 857
2018-11-02 19:00 | 880 | 877
2018-11-02 19:30 | 861 | 856
2018-11-02 20:00 | 845 | 844
2018-11-02 20:30 | 831 | 829
2018-11-02 21:00 | 788 | 787
2018-11-02 21:30 | 756 | 754
2018-11-02 22:00 | 735 | 731
2018-11-02 22:30 | 719 | 716
2018-11-02 23:00 | 717 | 713
2018-11-02 23:30 | 677 | 671
2018-11-03 | 623 | 613
2018-11-03 00:30 | 580 | 564
2018-11-03 01:00 | 566 | 545
2018-11-03 01:30 | 566 | 541
2018-11-03 02:00 | 555 | 527
2018-11-03 02:30 | 526 | 495
2018-11-03 03:00 | 528 | 496
2018-11-03 03:30 | 528 | 497
2018-11-03 04:00 | 531 | 499
2018-11-03 04:30 | 528 | 497
2018-11-03 05:00 | 534 | 500
2018-11-03 05:30 | 539 | 504
2018-11-03 06:00 | 546 | 513
2018-11-03 06:30 | 558 | 531
2018-11-03 07:00 | 558 | 537
2018-11-03 07:30 | 577 | 563
2018-11-03 08:00 | 581 | 572
2018-11-03 08:30 | 577 | 572
2018-11-03 09:00 | 579 | 577
2018-11-03 09:30 | 582 | 581
2018-11-03 10:00 | 591 | 590
2018-11-03 10:30 | 578 | 578
2018-11-03 11:00 | 580 | 580
2018-11-03 11:30 | 579 | 578
2018-11-03 12:00 | 584 | 583
2018-11-03 12:30 | 596 | 596
2018-11-03 13:00 | 612 | 612
2018-11-03 13:30 | 634 | 634
2018-11-03 14:00 | 664 | 664
2018-11-03 14:30 | 706 | 705
2018-11-03 15:00 | 733 | 731
2018-11-03 15:30 | 766 | 764
2018-11-03 16:00 | 795 | 794
2018-11-03 16:30 | 826 | 825
2018-11-03 17:00 | 854 | 853
2018-11-03 17:30 | 863 | 861
2018-11-03 18:00 | 856 | 853
2018-11-03 18:30 | 872 | 869
2018-11-03 19:00 | 905 | 902
2018-11-03 19:30 | 892 | 886
2018-11-03 20:00 | 877 | 870
2018-11-03 20:30 | 853 | 847
2018-11-03 21:00 | 812 | 809
2018-11-03 21:30 | 768 | 765
2018-11-03 22:00 | 746 | 743
2018-11-03 22:30 | 728 | 725
2018-11-03 23:00 | 689 | 685
2018-11-03 23:30 | 671 | 664
2018-11-04 | 646 | 635
2018-11-04 00:30 | 607 | 591
2018-11-04 01:00 | 585 | 564
2018-11-04 01:30 | 571 | 548
2018-11-04 02:00 | 560 | 533
2018-11-04 02:30 | 552 | 524
2018-11-04 03:00 | 548 | 518
2018-11-04 03:30 | 542 | 512
2018-11-04 04:00 | 540 | 509
2018-11-04 04:30 | 535 | 503
2018-11-04 05:00 | 529 | 493
2018-11-04 05:30 | 537 | 496
2018-11-04 06:00 | 536 | 496
2018-11-04 06:30 | 538 | 504
2018-11-04 07:00 | 538 | 509
2018-11-04 07:30 | 541 | 521
2018-11-04 08:00 | 543 | 530
2018-11-04 08:30 | 555 | 546
2018-11-04 09:00 | 573 | 568
2018-11-04 09:30 | 584 | 582
2018-11-04 10:00 | 602 | 601
2018-11-04 10:30 | 616 | 616
2018-11-04 11:00 | 633 | 631
2018-11-04 11:30 | 652 | 650
2018-11-04 12:00 | 663 | 662
2018-11-04 12:30 | 681 | 681
2018-11-04 13:00 | 709 | 709
2018-11-04 13:30 | 734 | 733
2018-11-04 14:00 | 764 | 756
2018-11-04 14:30 | 798 | 792
2018-11-04 15:00 | 812 | 808
2018-11-04 15:30 | 853 | 847
2018-11-04 16:00 | 902 | 898
2018-11-04 16:30 | 929 | 921
2018-11-04 17:00 | 937 | 927
2018-11-04 17:30 | 977 | 967
2018-11-04 18:00 | 979 | 967
2018-11-04 18:30 | 992 | 983
2018-11-04 19:00 | 1008 | 1003
2018-11-04 19:30 | 988 | 980
2018-11-04 20:00 | 967 | 961
2018-11-04 20:30 | 941 | 937
2018-11-04 21:00 | 893 | 888
2018-11-04 21:30 | 826 | 825
2018-11-04 22:00 | 789 | 788
2018-11-04 22:30 | 736 | 733
2018-11-04 23:00 | 734 | 733
2018-11-04 23:30 | 713 | 709
2018-11-05 | 669 | 661
2018-11-05 00:30 | 624 | 612
2018-11-05 01:00 | 597 | 580
2018-11-05 01:30 | 584 | 566
2018-11-05 02:00 | 565 | 545
2018-11-05 02:30 | 559 | 539
2018-11-05 03:00 | 557 | 536
2018-11-05 03:30 | 555 | 533
2018-11-05 04:00 | 555 | 534
2018-11-05 04:30 | 580 | 561
2018-11-05 05:00 | 597 | 580
2018-11-05 05:30 | 626 | 612
2018-11-05 06:00 | 655 | 647
2018-11-05 06:30 | 719 | 718
2018-11-05 07:00 | 785 | 784
2018-11-05 07:30 | 840 | 840
2018-11-05 08:00 | 871 | 867
2018-11-05 08:30 | 875 | 873
2018-11-05 09:00 | 876 | 875
2018-11-05 09:30 | 878 | 876
2018-11-05 10:00 | 878 | 876
2018-11-05 10:30 | 881 | 880
2018-11-05 11:00 | 882 | 881
2018-11-05 11:30 | 899 | 897
2018-11-05 12:00 | 933 | 929
2018-11-05 12:30 | 953 | 950
2018-11-05 13:00 | 984 | 982
2018-11-05 13:30 | 1009 | 1008
2018-11-05 14:00 | 1035 | 1034
2018-11-05 14:30 | 1073 | 1073
2018-11-05 15:00 | 1103 | 1102
2018-11-05 15:30 | 1088 | 1087
2018-11-05 16:00 | 1114 | 1113
2018-11-05 16:30 | 1181 | 1179
2018-11-05 17:00 | 1225 | 1223
2018-11-05 17:30 | 1223 | 1218
2018-11-05 18:00 | 1191 | 1181
2018-11-05 18:30 | 1179 | 1167
2018-11-05 19:00 | 1202 | 1194
2018-11-05 19:30 | 1179 | 1169
2018-11-05 20:00 | 1139 | 1136
2018-11-05 20:30 | 1086 | 1081
2018-11-05 21:00 | 1018 | 1015
2018-11-05 21:30 | 952 | 946
2018-11-05 22:00 | 904 | 899
2018-11-05 22:30 | 850 | 846
2018-11-05 23:00 | 830 | 826
2018-11-05 23:30 | 780 | 775
2018-11-06 | 723 | 717
2018-11-06 00:30 | 661 | 654
2018-11-06 01:00 | 620 | 609
2018-11-06 01:30 | 615 | 601
2018-11-06 02:00 | 605 | 589
2018-11-06 02:30 | 602 | 585
2018-11-06 03:00 | 598 | 580
2018-11-06 03:30 | 596 | 577
2018-11-06 04:00 | 597 | 579
2018-11-06 04:30 | 603 | 588
2018-11-06 05:00 | 616 | 602
2018-11-06 05:30 | 651 | 641
2018-11-06 06:00 | 698 | 692
2018-11-06 06:30 | 770 | 770
2018-11-06 07:00 | 840 | 840
2018-11-06 07:30 | 914 | 910
2018-11-06 08:00 | 943 | 943
2018-11-06 08:30 | 955 | 954
2018-11-06 09:00 | 945 | 943
2018-11-06 09:30 | 962 | 959
2018-11-06 10:00 | 962 | 958
2018-11-06 10:30 | 974 | 968
2018-11-06 11:00 | 1004 | 999
2018-11-06 11:30 | 1011 | 1011
2018-11-06 12:00 | 1033 | 1033
2018-11-06 12:30 | 1061 | 1061
2018-11-06 13:00 | 1054 | 1054
2018-11-06 13:30 | 1057 | 1057
2018-11-06 14:00 | 1109 | 1109
2018-11-06 14:30 | 1143 | 1143
2018-11-06 15:00 | 1183 | 1183
2018-11-06 15:30 | 1255 | 1253
2018-11-06 16:00 | 1284 | 1283
2018-11-06 16:30 | 1284 | 1282
2018-11-06 17:00 | 1278 | 1274
2018-11-06 17:30 | 1270 | 1264
2018-11-06 18:00 | 1254 | 1245
2018-11-06 18:30 | 1240 | 1227
2018-11-06 19:00 | 1240 | 1228
2018-11-06 19:30 | 1172 | 1154
2018-11-06 20:00 | 1113 | 1103
2018-11-06 20:30 | 1110 | 1100
2018-11-06 21:00 | 1067 | 1062
2018-11-06 21:30 | 985 | 976
2018-11-06 22:00 | 965 | 957
2018-11-06 22:30 | 869 | 864
2018-11-06 23:00 | 840 | 837
2018-11-06 23:30 | 805 | 801
2018-11-07 | 763 | 759
2018-11-07 00:30 | 715 | 709
2018-11-07 01:00 | 668 | 662
2018-11-07 01:30 | 608 | 603
2018-11-07 02:00 | 576 | 568
2018-11-07 02:30 | 570 | 559
2018-11-07 03:00 | 589 | 577
2018-11-07 03:30 | 592 | 579
2018-11-07 04:00 | 585 | 573
2018-11-07 04:30 | 572 | 561
2018-11-07 05:00 | 582 | 571
2018-11-07 05:30 | 641 | 633
2018-11-07 06:00 | 687 | 684
2018-11-07 06:30 | 772 | 772
2018-11-07 07:00 | 852 | 849
2018-11-07 07:30 | 905 | 903
2018-11-07 08:00 | 926 | 925
2018-11-07 08:30 | 933 | 933
2018-11-07 09:00 | 928 | 928
2018-11-07 09:30 | 933 | 933
2018-11-07 10:00 | 933 | 933
2018-11-07 10:30 | 941 | 941
2018-11-07 11:00 | 936 | 935
2018-11-07 11:30 | 948 | 947
2018-11-07 12:00 | 967 | 966
2018-11-07 12:30 | 979 | 979
2018-11-07 13:00 | 1001 | 1001
2018-11-07 13:30 | 1032 | 1030
2018-11-07 14:00 | 1093 | 1092
2018-11-07 14:30 | 1156 | 1154
2018-11-07 15:00 | 1150 | 1145
2018-11-07 15:30 | 1189 | 1186
2018-11-07 16:00 | 1236 | 1234
2018-11-07 16:30 | 1281 | 1280
2018-11-07 17:00 | 1307 | 1306
2018-11-07 17:30 | 1305 | 1302
2018-11-07 18:00 | 1276 | 1270
2018-11-07 18:30 | 1255 | 1246
2018-11-07 19:00 | 1262 | 1256
2018-11-07 19:30 | 1181 | 1167
2018-11-07 20:00 | 1154 | 1140
2018-11-07 20:30 | 1107 | 1092
2018-11-07 21:00 | 1026 | 1017
2018-11-07 21:30 | 959 | 955
2018-11-07 22:00 | 947 | 938
2018-11-07 22:30 | 899 | 892
2018-11-07 23:00 | 869 | 860
2018-11-07 23:30 | 809 | 800
2018-11-08 | 751 | 738
2018-11-08 00:30 | 651 | 634
2018-11-08 01:00 | 618 | 605
2018-11-08 01:30 | 626 | 611
2018-11-08 02:00 | 579 | 562
2018-11-08 02:30 | 575 | 558
2018-11-08 03:00 | 579 | 561
2018-11-08 03:30 | 595 | 577
2018-11-08 04:00 | 606 | 590
2018-11-08 04:30 | 600 | 585
2018-11-08 05:00 | 604 | 591
2018-11-08 05:30 | 628 | 618
2018-11-08 06:00 | 698 | 691
2018-11-08 06:30 | 803 | 796
2018-11-08 07:00 | 865 | 859
2018-11-08 07:30 | 940 | 930
2018-11-08 08:00 | 964 | 952
2018-11-08 08:30 | 967 | 958
2018-11-08 09:00 | 951 | 941
2018-11-08 09:30 | 965 | 957
2018-11-08 10:00 | 958 | 949
2018-11-08 10:30 | 957 | 946
2018-11-08 11:00 | 948 | 935
2018-11-08 11:30 | 934 | 922
2018-11-08 12:00 | 882 | 873
2018-11-08 12:30 | 846 | 836
2018-11-08 13:00 | 807 | 797
2018-11-08 13:30 | 811 | 807
2018-11-08 14:00 | 811 | 807
2018-11-08 14:30 | 792 | 787
2018-11-08 15:00 | 735 | 732
2018-11-08 15:30 | 763 | 762
2018-11-08 16:00 | 800 | 799
2018-11-08 16:30 | 836 | 836
2018-11-08 17:00 | 864 | 864
2018-11-08 17:30 | 878 | 877
2018-11-08 18:00 | 883 | 882
2018-11-08 18:30 | 895 | 893
2018-11-08 19:00 | 928 | 927
2018-11-08 19:30 | 925 | 921
2018-11-08 20:00 | 909 | 902
2018-11-08 20:30 | 894 | 890
2018-11-08 21:00 | 857 | 856
2018-11-08 21:30 | 814 | 813
2018-11-08 22:00 | 784 | 783
2018-11-08 22:30 | 761 | 759
2018-11-08 23:00 | 750 | 747
2018-11-08 23:30 | 716 | 710
2018-11-09 | 664 | 653
2018-11-09 00:30 | 630 | 614
2018-11-09 01:00 | 606 | 586
2018-11-09 01:30 | 594 | 571
2018-11-09 02:00 | 581 | 557
2018-11-09 02:30 | 572 | 549
2018-11-09 03:00 | 569 | 545
2018-11-09 03:30 | 571 | 547
2018-11-09 04:00 | 571 | 547
2018-11-09 04:30 | 577 | 555
2018-11-09 05:00 | 590 | 569
2018-11-09 05:30 | 616 | 599
2018-11-09 06:00 | 646 | 635
2018-11-09 06:30 | 684 | 679
2018-11-09 07:00 | 719 | 717
2018-11-09 07:30 | 748 | 748
2018-11-09 08:00 | 732 | 732
2018-11-09 08:30 | 705 | 705
2018-11-09 09:00 | 698 | 697
2018-11-09 09:30 | 710 | 710
2018-11-09 10:00 | 712 | 711
2018-11-09 10:30 | 715 | 715
2018-11-09 11:00 | 737 | 737
2018-11-09 11:30 | 726 | 726
2018-11-09 12:00 | 703 | 703
2018-11-09 12:30 | 698 | 698
2018-11-09 13:00 | 695 | 695
2018-11-09 13:30 | 692 | 691
2018-11-09 14:00 | 711 | 710
2018-11-09 14:30 | 704 | 703
2018-11-09 15:00 | 693 | 692
2018-11-09 15:30 | 714 | 713
2018-11-09 16:00 | 753 | 752
2018-11-09 16:30 | 778 | 778
2018-11-09 17:00 | 806 | 805
2018-11-09 17:30 | 822 | 820
2018-11-09 18:00 | 827 | 824
2018-11-09 18:30 | 832 | 829
2018-11-09 19:00 | 856 | 854
2018-11-09 19:30 | 852 | 850
2018-11-09 20:00 | 836 | 836
2018-11-09 20:30 | 819 | 819
2018-11-09 21:00 | 787 | 786
2018-11-09 21:30 | 755 | 753
2018-11-09 22:00 | 732 | 729
2018-11-09 22:30 | 721 | 716
2018-11-09 23:00 | 715 | 710
2018-11-09 23:30 | 683 | 674
2018-11-10 | 641 | 626
2018-11-10 00:30 | 602 | 580
2018-11-10 01:00 | 584 | 556
2018-11-10 01:30 | 574 | 544
2018-11-10 02:00 | 561 | 528
2018-11-10 02:30 | 559 | 524
2018-11-10 03:00 | 551 | 514
2018-11-10 03:30 | 553 | 516
2018-11-10 04:00 | 548 | 512
2018-11-10 04:30 | 547 | 510
2018-11-10 05:00 | 552 | 513
2018-11-10 05:30 | 553 | 512
2018-11-10 06:00 | 560 | 521
2018-11-10 06:30 | 565 | 533
2018-11-10 07:00 | 566 | 539
2018-11-10 07:30 | 573 | 552
2018-11-10 08:00 | 578 | 563
2018-11-10 08:30 | 583 | 574
2018-11-10 09:00 | 610 | 605
2018-11-10 09:30 | 622 | 620
2018-11-10 10:00 | 623 | 621
2018-11-10 10:30 | 608 | 606
2018-11-10 11:00 | 592 | 590
2018-11-10 11:30 | 575 | 574
2018-11-10 12:00 | 571 | 569
2018-11-10 12:30 | 570 | 567
2018-11-10 13:00 | 583 | 581
2018-11-10 13:30 | 592 | 591
2018-11-10 14:00 | 613 | 611
2018-11-10 14:30 | 610 | 608
2018-11-10 15:00 | 635 | 633
2018-11-10 15:30 | 650 | 648
2018-11-10 16:00 | 680 | 679
2018-11-10 16:30 | 718 | 715
2018-11-10 17:00 | 752 | 747
2018-11-10 17:30 | 763 | 759
2018-11-10 18:00 | 765 | 760
2018-11-10 18:30 | 781 | 776
2018-11-10 19:00 | 812 | 811
2018-11-10 19:30 | 804 | 802
2018-11-10 20:00 | 789 | 788
2018-11-10 20:30 | 774 | 773
2018-11-10 21:00 | 748 | 746
2018-11-10 21:30 | 724 | 719
2018-11-10 22:00 | 716 | 710
2018-11-10 22:30 | 706 | 698
2018-11-10 23:00 | 703 | 696
2018-11-10 23:30 | 673 | 663
2018-11-11 | 641 | 624
2018-11-11 00:30 | 602 | 578
2018-11-11 01:00 | 582 | 553
2018-11-11 01:30 | 567 | 536
2018-11-11 02:00 | 556 | 520
2018-11-11 02:30 | 550 | 512
2018-11-11 03:00 | 547 | 509
2018-11-11 03:30 | 541 | 501
2018-11-11 04:00 | 537 | 496
2018-11-11 04:30 | 537 | 495
2018-11-11 05:00 | 549 | 503
2018-11-11 05:30 | 556 | 507
2018-11-11 06:00 | 560 | 512
2018-11-11 06:30 | 555 | 512
2018-11-11 07:00 | 558 | 521
2018-11-11 07:30 | 562 | 534
2018-11-11 08:00 | 566 | 543
2018-11-11 08:30 | 576 | 560
2018-11-11 09:00 | 562 | 550
2018-11-11 09:30 | 561 | 553
2018-11-11 10:00 | 564 | 557
2018-11-11 10:30 | 569 | 564
2018-11-11 11:00 | 569 | 564
2018-11-11 11:30 | 554 | 548
2018-11-11 12:00 | 545 | 538
2018-11-11 12:30 | 536 | 530
2018-11-11 13:00 | 543 | 537
2018-11-11 13:30 | 551 | 546
2018-11-11 14:00 | 572 | 568
2018-11-11 14:30 | 591 | 588
2018-11-11 15:00 | 631 | 629
2018-11-11 15:30 | 660 | 659
2018-11-11 16:00 | 695 | 694
2018-11-11 16:30 | 733 | 732
2018-11-11 17:00 | 764 | 764
2018-11-11 17:30 | 783 | 782
2018-11-11 18:00 | 788 | 788
2018-11-11 18:30 | 806 | 806
2018-11-11 19:00 | 846 | 845
2018-11-11 19:30 | 837 | 832
2018-11-11 20:00 | 829 | 821
2018-11-11 20:30 | 812 | 803
2018-11-11 21:00 | 771 | 767
2018-11-11 21:30 | 740 | 735
2018-11-11 22:00 | 719 | 712
2018-11-11 22:30 | 702 | 693
2018-11-11 23:00 | 701 | 691
2018-11-11 23:30 | 668 | 655
2018-11-12 | 634 | 615
2018-11-12 00:30 | 602 | 576
2018-11-12 01:00 | 583 | 552
2018-11-12 01:30 | 573 | 539
2018-11-12 02:00 | 564 | 529
2018-11-12 02:30 | 563 | 526
2018-11-12 03:00 | 560 | 522
2018-11-12 03:30 | 556 | 518
2018-11-12 04:00 | 558 | 521
2018-11-12 04:30 | 571 | 537
2018-11-12 05:00 | 582 | 546
2018-11-12 05:30 | 604 | 573
2018-11-12 06:00 | 623 | 601
2018-11-12 06:30 | 662 | 653
2018-11-12 07:00 | 692 | 689
2018-11-12 07:30 | 737 | 728
2018-11-12 08:00 | 726 | 719
2018-11-12 08:30 | 729 | 725
2018-11-12 09:00 | 721 | 719
2018-11-12 09:30 | 715 | 714
2018-11-12 10:00 | 703 | 703
2018-11-12 10:30 | 699 | 699
2018-11-12 11:00 | 709 | 708
2018-11-12 11:30 | 695 | 695
2018-11-12 12:00 | 689 | 689
2018-11-12 12:30 | 682 | 682
2018-11-12 13:00 | 695 | 695
2018-11-12 13:30 | 704 | 704
2018-11-12 14:00 | 716 | 716
2018-11-12 14:30 | 734 | 734
2018-11-12 15:00 | 752 | 751
2018-11-12 15:30 | 772 | 771
2018-11-12 16:00 | 817 | 816
2018-11-12 16:30 | 854 | 854
2018-11-12 17:00 | 884 | 884
2018-11-12 17:30 | 899 | 898
2018-11-12 18:00 | 899 | 896
2018-11-12 18:30 | 909 | 903
2018-11-12 19:00 | 933 | 930
2018-11-12 19:30 | 913 | 909
2018-11-12 20:00 | 892 | 885
2018-11-12 20:30 | 878 | 869
2018-11-12 21:00 | 835 | 829
2018-11-12 21:30 | 790 | 787
2018-11-12 22:00 | 767 | 761
2018-11-12 22:30 | 741 | 738
2018-11-12 23:00 | 736 | 731
2018-11-12 23:30 | 692 | 684
2018-11-13 | 654 | 640
2018-11-13 00:30 | 614 | 594
2018-11-13 01:00 | 592 | 567
2018-11-13 01:30 | 586 | 558
2018-11-13 02:00 | 575 | 547
2018-11-13 02:30 | 578 | 550
2018-11-13 03:00 | 567 | 537
2018-11-13 03:30 | 570 | 540
2018-11-13 04:00 | 570 | 541
2018-11-13 04:30 | 581 | 555
2018-11-13 05:00 | 589 | 563
2018-11-13 05:30 | 614 | 591
2018-11-13 06:00 | 639 | 624
2018-11-13 06:30 | 683 | 677
2018-11-13 07:00 | 711 | 709
2018-11-13 07:30 | 726 | 726
2018-11-13 08:00 | 724 | 724
2018-11-13 08:30 | 736 | 736
2018-11-13 09:00 | 758 | 758
2018-11-13 09:30 | 762 | 761
2018-11-13 10:00 | 741 | 740
2018-11-13 10:30 | 723 | 722
2018-11-13 11:00 | 728 | 727
2018-11-13 11:30 | 728 | 727
2018-11-13 12:00 | 719 | 718
2018-11-13 12:30 | 717 | 716
2018-11-13 13:00 | 724 | 723
2018-11-13 13:30 | 719 | 718
2018-11-13 14:00 | 731 | 730
2018-11-13 14:30 | 748 | 747
2018-11-13 15:00 | 767 | 766
2018-11-13 15:30 | 788 | 788
2018-11-13 16:00 | 838 | 838
2018-11-13 16:30 | 865 | 865
2018-11-13 17:00 | 895 | 895
2018-11-13 17:30 | 915 | 915
2018-11-13 18:00 | 904 | 902
2018-11-13 18:30 | 911 | 908
2018-11-13 19:00 | 941 | 940
2018-11-13 19:30 | 921 | 919
2018-11-13 20:00 | 909 | 906
2018-11-13 20:30 | 888 | 886
2018-11-13 21:00 | 852 | 849
2018-11-13 21:30 | 805 | 802
2018-11-13 22:00 | 773 | 768
2018-11-13 22:30 | 743 | 740
2018-11-13 23:00 | 730 | 724
2018-11-13 23:30 | 690 | 682
2018-11-14 | 653 | 640
2018-11-14 00:30 | 616 | 598
2018-11-14 01:00 | 590 | 567
2018-11-14 01:30 | 586 | 559
2018-11-14 02:00 | 577 | 548
2018-11-14 02:30 | 572 | 545
2018-11-14 03:00 | 568 | 541
2018-11-14 03:30 | 567 | 539
2018-11-14 04:00 | 571 | 543
2018-11-14 04:30 | 576 | 551
2018-11-14 05:00 | 580 | 553
2018-11-14 05:30 | 604 | 581
2018-11-14 06:00 | 622 | 606
2018-11-14 06:30 | 664 | 657
2018-11-14 07:00 | 711 | 707
2018-11-14 07:30 | 750 | 748
2018-11-14 08:00 | 750 | 749
2018-11-14 08:30 | 764 | 764
2018-11-14 09:00 | 776 | 776
2018-11-14 09:30 | 788 | 788
2018-11-14 10:00 | 782 | 782
2018-11-14 10:30 | 775 | 775
2018-11-14 11:00 | 764 | 764
2018-11-14 11:30 | 750 | 749
2018-11-14 12:00 | 775 | 775
2018-11-14 12:30 | 789 | 787
2018-11-14 13:00 | 798 | 796
2018-11-14 13:30 | 821 | 821
2018-11-14 14:00 | 829 | 824
2018-11-14 14:30 | 845 | 841
2018-11-14 15:00 | 836 | 831
2018-11-14 15:30 | 872 | 868
2018-11-14 16:00 | 871 | 866
2018-11-14 16:30 | 902 | 897
2018-11-14 17:00 | 923 | 917
2018-11-14 17:30 | 941 | 930
2018-11-14 18:00 | 943 | 928
2018-11-14 18:30 | 956 | 939
2018-11-14 19:00 | 977 | 964
2018-11-14 19:30 | 962 | 946
2018-11-14 20:00 | 947 | 936
2018-11-14 20:30 | 930 | 919
2018-11-14 21:00 | 884 | 879
2018-11-14 21:30 | 838 | 833
2018-11-14 22:00 | 803 | 797
2018-11-14 22:30 | 778 | 777
2018-11-14 23:00 | 765 | 763
2018-11-14 23:30 | 721 | 717
2018-11-15 | 672 | 664
2018-11-15 00:30 | 635 | 621
2018-11-15 01:00 | 622 | 604
2018-11-15 01:30 | 606 | 584
2018-11-15 02:00 | 596 | 573
2018-11-15 02:30 | 589 | 565
2018-11-15 03:00 | 591 | 565
2018-11-15 03:30 | 591 | 565
2018-11-15 04:00 | 587 | 562
2018-11-15 04:30 | 596 | 573
2018-11-15 05:00 | 604 | 581
2018-11-15 05:30 | 630 | 611
2018-11-15 06:00 | 656 | 644
2018-11-15 06:30 | 700 | 696
2018-11-15 07:00 | 748 | 747
2018-11-15 07:30 | 793 | 793
2018-11-15 08:00 | 822 | 821
2018-11-15 08:30 | 821 | 821
2018-11-15 09:00 | 818 | 818
2018-11-15 09:30 | 815 | 815
2018-11-15 10:00 | 814 | 814
2018-11-15 10:30 | 808 | 807
2018-11-15 11:00 | 811 | 810
2018-11-15 11:30 | 796 | 796
2018-11-15 12:00 | 804 | 802
2018-11-15 12:30 | 827 | 827
2018-11-15 13:00 | 833 | 833
2018-11-15 13:30 | 840 | 840
2018-11-15 14:00 | 856 | 855
2018-11-15 14:30 | 886 | 886
2018-11-15 15:00 | 892 | 892
2018-11-15 15:30 | 895 | 895
2018-11-15 16:00 | 922 | 921
2018-11-15 16:30 | 948 | 948
2018-11-15 17:00 | 988 | 988
2018-11-15 17:30 | 997 | 996
2018-11-15 18:00 | 976 | 973
2018-11-15 18:30 | 975 | 970
2018-11-15 19:00 | 972 | 969
2018-11-15 19:30 | 966 | 962
2018-11-15 20:00 | 975 | 970
2018-11-15 20:30 | 958 | 953
2018-11-15 21:00 | 910 | 908
2018-11-15 21:30 | 856 | 856
2018-11-15 22:00 | 821 | 820
2018-11-15 22:30 | 800 | 797
2018-11-15 23:00 | 783 | 782
2018-11-15 23:30 | 738 | 735
2018-11-16 | 687 | 681
2018-11-16 00:30 | 648 | 637
2018-11-16 01:00 | 624 | 609
2018-11-16 01:30 | 606 | 588
2018-11-16 02:00 | 598 | 577
2018-11-16 02:30 | 589 | 567
2018-11-16 03:00 | 583 | 560
2018-11-16 03:30 | 581 | 558
2018-11-16 04:00 | 584 | 562
2018-11-16 04:30 | 589 | 569
2018-11-16 05:00 | 599 | 578
2018-11-16 05:30 | 626 | 609
2018-11-16 06:00 | 653 | 643
2018-11-16 06:30 | 692 | 689
2018-11-16 07:00 | 739 | 738
2018-11-16 07:30 | 790 | 790
2018-11-16 08:00 | 820 | 820
2018-11-16 08:30 | 826 | 826
2018-11-16 09:00 | 824 | 824
2018-11-16 09:30 | 818 | 818
2018-11-16 10:00 | 816 | 816
2018-11-16 10:30 | 806 | 806
2018-11-16 11:00 | 812 | 812
2018-11-16 11:30 | 818 | 817
2018-11-16 12:00 | 823 | 823
2018-11-16 12:30 | 825 | 825
2018-11-16 13:00 | 821 | 820
2018-11-16 13:30 | 832 | 832
2018-11-16 14:00 | 844 | 844
2018-11-16 14:30 | 859 | 858
2018-11-16 15:00 | 873 | 873
2018-11-16 15:30 | 901 | 901
2018-11-16 16:00 | 939 | 939
2018-11-16 16:30 | 967 | 967
2018-11-16 17:00 | 987 | 987
2018-11-16 17:30 | 988 | 988
2018-11-16 18:00 | 950 | 947
2018-11-16 18:30 | 934 | 930
2018-11-16 19:00 | 957 | 955
2018-11-16 19:30 | 944 | 942
2018-11-16 20:00 | 924 | 924
2018-11-16 20:30 | 912 | 912
2018-11-16 21:00 | 869 | 869
2018-11-16 21:30 | 830 | 830
2018-11-16 22:00 | 811 | 811
2018-11-16 22:30 | 796 | 796
2018-11-16 23:00 | 788 | 788
2018-11-16 23:30 | 745 | 743
2018-11-17 | 701 | 696
2018-11-17 00:30 | 655 | 645
2018-11-17 01:00 | 627 | 613
2018-11-17 01:30 | 608 | 591
2018-11-17 02:00 | 595 | 575
2018-11-17 02:30 | 588 | 568
2018-11-17 03:00 | 581 | 561
2018-11-17 03:30 | 578 | 559
2018-11-17 04:00 | 577 | 556
2018-11-17 04:30 | 581 | 559
2018-11-17 05:00 | 582 | 555
2018-11-17 05:30 | 584 | 557
2018-11-17 06:00 | 593 | 568
2018-11-17 06:30 | 601 | 583
2018-11-17 07:00 | 615 | 604
2018-11-17 07:30 | 643 | 639
2018-11-17 08:00 | 667 | 665
2018-11-17 08:30 | 688 | 686
2018-11-17 09:00 | 711 | 711
2018-11-17 09:30 | 719 | 719
2018-11-17 10:00 | 702 | 702
2018-11-17 10:30 | 705 | 705
2018-11-17 11:00 | 718 | 718
2018-11-17 11:30 | 705 | 705
2018-11-17 12:00 | 685 | 685
2018-11-17 12:30 | 717 | 716
2018-11-17 13:00 | 733 | 733
2018-11-17 13:30 | 712 | 710
2018-11-17 14:00 | 734 | 732
2018-11-17 14:30 | 753 | 751
2018-11-17 15:00 | 841 | 841
2018-11-17 15:30 | 882 | 882
2018-11-17 16:00 | 881 | 881
2018-11-17 16:30 | 891 | 890
2018-11-17 17:00 | 879 | 878
2018-11-17 17:30 | 872 | 869
2018-11-17 18:00 | 861 | 858
2018-11-17 18:30 | 871 | 868
2018-11-17 19:00 | 874 | 870
2018-11-17 19:30 | 848 | 842
2018-11-17 20:00 | 817 | 813
2018-11-17 20:30 | 794 | 792
2018-11-17 21:00 | 763 | 762
2018-11-17 21:30 | 742 | 741
2018-11-17 22:00 | 730 | 727
2018-11-17 22:30 | 715 | 710
2018-11-17 23:00 | 715 | 710
2018-11-17 23:30 | 685 | 677
2018-11-18 | 646 | 635
2018-11-18 00:30 | 611 | 594
2018-11-18 01:00 | 590 | 570
2018-11-18 01:30 | 581 | 557
2018-11-18 02:00 | 569 | 541
2018-11-18 02:30 | 560 | 532
2018-11-18 03:00 | 557 | 529
2018-11-18 03:30 | 557 | 528
2018-11-18 04:00 | 551 | 520
2018-11-18 04:30 | 551 | 520
2018-11-18 05:00 | 551 | 517
2018-11-18 05:30 | 558 | 522
2018-11-18 06:00 | 559 | 523
2018-11-18 06:30 | 566 | 536
2018-11-18 07:00 | 578 | 554
2018-11-18 07:30 | 594 | 577
2018-11-18 08:00 | 618 | 606
2018-11-18 08:30 | 635 | 628
2018-11-18 09:00 | 647 | 643
2018-11-18 09:30 | 643 | 640
2018-11-18 10:00 | 647 | 646
2018-11-18 10:30 | 671 | 671
2018-11-18 11:00 | 670 | 666
2018-11-18 11:30 | 662 | 656
2018-11-18 12:00 | 671 | 666
2018-11-18 12:30 | 678 | 674
2018-11-18 13:00 | 661 | 657
2018-11-18 13:30 | 664 | 660
2018-11-18 14:00 | 652 | 644
2018-11-18 14:30 | 653 | 646
2018-11-18 15:00 | 676 | 671
2018-11-18 15:30 | 688 | 683
2018-11-18 16:00 | 707 | 702
2018-11-18 16:30 | 721 | 716
2018-11-18 17:00 | 746 | 740
2018-11-18 17:30 | 775 | 769
2018-11-18 18:00 | 796 | 790
2018-11-18 18:30 | 814 | 810
2018-11-18 19:00 | 847 | 843
2018-11-18 19:30 | 838 | 832
2018-11-18 20:00 | 824 | 817
2018-11-18 20:30 | 812 | 804
2018-11-18 21:00 | 773 | 767
2018-11-18 21:30 | 736 | 733
2018-11-18 22:00 | 710 | 705
2018-11-18 22:30 | 692 | 686
2018-11-18 23:00 | 697 | 691
2018-11-18 23:30 | 667 | 658
2018-11-19 | 625 | 611
2018-11-19 00:30 | 590 | 570
2018-11-19 01:00 | 570 | 546
2018-11-19 01:30 | 562 | 538
2018-11-19 02:00 | 552 | 525
2018-11-19 02:30 | 550 | 522
2018-11-19 03:00 | 545 | 516
2018-11-19 03:30 | 550 | 520
2018-11-19 04:00 | 549 | 521
2018-11-19 04:30 | 555 | 530
2018-11-19 05:00 | 568 | 543
2018-11-19 05:30 | 590 | 568
2018-11-19 06:00 | 611 | 597
2018-11-19 06:30 | 659 | 654
2018-11-19 07:00 | 695 | 693
2018-11-19 07:30 | 720 | 719
2018-11-19 08:00 | 718 | 717
2018-11-19 08:30 | 711 | 710
2018-11-19 09:00 | 712 | 712
2018-11-19 09:30 | 735 | 735
2018-11-19 10:00 | 742 | 742
2018-11-19 10:30 | 750 | 750
2018-11-19 11:00 | 747 | 747
2018-11-19 11:30 | 728 | 728
2018-11-19 12:00 | 726 | 726
2018-11-19 12:30 | 737 | 737
2018-11-19 13:00 | 731 | 731
2018-11-19 13:30 | 738 | 738
2018-11-19 14:00 | 752 | 752
2018-11-19 14:30 | 764 | 764
2018-11-19 15:00 | 768 | 768
2018-11-19 15:30 | 786 | 786
2018-11-19 16:00 | 823 | 823
2018-11-19 16:30 | 857 | 857
2018-11-19 17:00 | 879 | 879
2018-11-19 17:30 | 895 | 894
2018-11-19 18:00 | 893 | 892
2018-11-19 18:30 | 893 | 890
2018-11-19 19:00 | 925 | 924
2018-11-19 19:30 | 910 | 908
2018-11-19 20:00 | 889 | 885
2018-11-19 20:30 | 861 | 859
2018-11-19 21:00 | 825 | 825
2018-11-19 21:30 | 787 | 787
2018-11-19 22:00 | 754 | 753
2018-11-19 22:30 | 739 | 737
2018-11-19 23:00 | 730 | 727
2018-11-19 23:30 | 688 | 683
2018-11-20 | 644 | 634
2018-11-20 00:30 | 609 | 593
2018-11-20 01:00 | 588 | 568
2018-11-20 01:30 | 572 | 549
2018-11-20 02:00 | 565 | 539
2018-11-20 02:30 | 563 | 537
2018-11-20 03:00 | 557 | 530
2018-11-20 03:30 | 559 | 533
2018-11-20 04:00 | 561 | 536
2018-11-20 04:30 | 570 | 546
2018-11-20 05:00 | 577 | 553
2018-11-20 05:30 | 605 | 585
2018-11-20 06:00 | 622 | 609
2018-11-20 06:30 | 657 | 652
2018-11-20 07:00 | 697 | 694
2018-11-20 07:30 | 731 | 727
2018-11-20 08:00 | 722 | 718
2018-11-20 08:30 | 726 | 725
2018-11-20 09:00 | 727 | 726
2018-11-20 09:30 | 747 | 742
2018-11-20 10:00 | 744 | 740
2018-11-20 10:30 | 729 | 725
2018-11-20 11:00 | 711 | 707
2018-11-20 11:30 | 709 | 706
2018-11-20 12:00 | 719 | 716
2018-11-20 12:30 | 716 | 714
2018-11-20 13:00 | 724 | 722
2018-11-20 13:30 | 731 | 729
2018-11-20 14:00 | 758 | 753
2018-11-20 14:30 | 783 | 777
2018-11-20 15:00 | 802 | 797
2018-11-20 15:30 | 821 | 816
2018-11-20 16:00 | 862 | 858
2018-11-20 16:30 | 921 | 918
2018-11-20 17:00 | 962 | 956
2018-11-20 17:30 | 990 | 983
2018-11-20 18:00 | 996 | 985
2018-11-20 18:30 | 993 | 981
2018-11-20 19:00 | 1026 | 1020
2018-11-20 19:30 | 1016 | 1008
2018-11-20 20:00 | 981 | 980
2018-11-20 20:30 | 945 | 943
2018-11-20 21:00 | 911 | 910
2018-11-20 21:30 | 865 | 864
2018-11-20 22:00 | 792 | 789
2018-11-20 22:30 | 776 | 771
2018-11-20 23:00 | 760 | 754
2018-11-20 23:30 | 717 | 707
2018-11-21 | 670 | 656
2018-11-21 00:30 | 622 | 610
2018-11-21 01:00 | 602 | 586
2018-11-21 01:30 | 588 | 570
2018-11-21 02:00 | 580 | 560
2018-11-21 02:30 | 574 | 552
2018-11-21 03:00 | 572 | 550
2018-11-21 03:30 | 573 | 550
2018-11-21 04:00 | 577 | 555
2018-11-21 04:30 | 585 | 565
2018-11-21 05:00 | 593 | 571
2018-11-21 05:30 | 616 | 599
2018-11-21 06:00 | 646 | 636
2018-11-21 06:30 | 683 | 680
2018-11-21 07:00 | 719 | 718
2018-11-21 07:30 | 752 | 751
2018-11-21 08:00 | 765 | 764
2018-11-21 08:30 | 765 | 765
2018-11-21 09:00 | 772 | 770
2018-11-21 09:30 | 773 | 772
2018-11-21 10:00 | 778 | 777
2018-11-21 10:30 | 779 | 778
2018-11-21 11:00 | 792 | 792
2018-11-21 11:30 | 803 | 802
2018-11-21 12:00 | 812 | 811
2018-11-21 12:30 | 817 | 816
2018-11-21 13:00 | 843 | 843
2018-11-21 13:30 | 874 | 869
2018-11-21 14:00 | 922 | 919
2018-11-21 14:30 | 980 | 979
2018-11-21 15:00 | 1030 | 1029
2018-11-21 15:30 | 1077 | 1077
2018-11-21 16:00 | 1109 | 1108
2018-11-21 16:30 | 1124 | 1123
2018-11-21 17:00 | 1130 | 1129
2018-11-21 17:30 | 1127 | 1125
2018-11-21 18:00 | 1122 | 1118
2018-11-21 18:30 | 1122 | 1119
2018-11-21 19:00 | 1142 | 1140
2018-11-21 19:30 | 1130 | 1127
2018-11-21 20:00 | 1098 | 1097
2018-11-21 20:30 | 1081 | 1079
2018-11-21 21:00 | 1026 | 1024
2018-11-21 21:30 | 974 | 974
2018-11-21 22:00 | 921 | 920
2018-11-21 22:30 | 880 | 875
2018-11-21 23:00 | 850 | 846
2018-11-21 23:30 | 808 | 805
2018-11-22 | 765 | 760
2018-11-22 00:30 | 721 | 710
2018-11-22 01:00 | 686 | 671
2018-11-22 01:30 | 650 | 631
2018-11-22 02:00 | 627 | 613
2018-11-22 02:30 | 620 | 607
2018-11-22 03:00 | 619 | 606
2018-11-22 03:30 | 613 | 599
2018-11-22 04:00 | 611 | 597
2018-11-22 04:30 | 618 | 606
2018-11-22 05:00 | 626 | 615
2018-11-22 05:30 | 656 | 647
2018-11-22 06:00 | 716 | 712
2018-11-22 06:30 | 806 | 805
2018-11-22 07:00 | 842 | 841
2018-11-22 07:30 | 911 | 910
2018-11-22 08:00 | 951 | 950
2018-11-22 08:30 | 958 | 957
2018-11-22 09:00 | 964 | 962
2018-11-22 09:30 | 977 | 974
2018-11-22 10:00 | 982 | 980
2018-11-22 10:30 | 1004 | 1004
2018-11-22 11:00 | 1093 | 1093
2018-11-22 11:30 | 1081 | 1074
2018-11-22 12:00 | 1027 | 1019
2018-11-22 12:30 | 933 | 926
2018-11-22 13:00 | 863 | 856
2018-11-22 13:30 | 805 | 804
2018-11-22 14:00 | 792 | 791
2018-11-22 14:30 | 836 | 835
2018-11-22 15:00 | 847 | 846
2018-11-22 15:30 | 883 | 882
2018-11-22 16:00 | 940 | 940
2018-11-22 16:30 | 1012 | 1009
2018-11-22 17:00 | 1066 | 1064
2018-11-22 17:30 | 1106 | 1104
2018-11-22 18:00 | 1106 | 1102
2018-11-22 18:30 | 1098 | 1091
2018-11-22 19:00 | 1134 | 1130
2018-11-22 19:30 | 1122 | 1118
2018-11-22 20:00 | 1103 | 1097
2018-11-22 20:30 | 1078 | 1072
2018-11-22 21:00 | 1026 | 1019
2018-11-22 21:30 | 955 | 949
2018-11-22 22:00 | 874 | 873
2018-11-22 22:30 | 848 | 846
2018-11-22 23:00 | 828 | 825
2018-11-22 23:30 | 776 | 774
2018-11-23 | 716 | 711
2018-11-23 00:30 | 667 | 658
2018-11-23 01:00 | 647 | 634
2018-11-23 01:30 | 612 | 595
2018-11-23 02:00 | 596 | 577
2018-11-23 02:30 | 587 | 566
2018-11-23 03:00 | 585 | 563
2018-11-23 03:30 | 584 | 562
2018-11-23 04:00 | 584 | 562
2018-11-23 04:30 | 589 | 568
2018-11-23 05:00 | 595 | 572
2018-11-23 05:30 | 619 | 599
2018-11-23 06:00 | 628 | 615
2018-11-23 06:30 | 673 | 669
2018-11-23 07:00 | 700 | 699
2018-11-23 07:30 | 727 | 727
2018-11-23 08:00 | 726 | 726
2018-11-23 08:30 | 719 | 719
2018-11-23 09:00 | 712 | 712
2018-11-23 09:30 | 697 | 696
2018-11-23 10:00 | 690 | 690
2018-11-23 10:30 | 678 | 678
2018-11-23 11:00 | 682 | 682
2018-11-23 11:30 | 682 | 682
2018-11-23 12:00 | 685 | 685
2018-11-23 12:30 | 693 | 693
2018-11-23 13:00 | 704 | 704
2018-11-23 13:30 | 723 | 723
2018-11-23 14:00 | 744 | 744
2018-11-23 14:30 | 769 | 768
2018-11-23 15:00 | 794 | 794
2018-11-23 15:30 | 825 | 825
2018-11-23 16:00 | 875 | 874
2018-11-23 16:30 | 927 | 926
2018-11-23 17:00 | 980 | 979
2018-11-23 17:30 | 996 | 994
2018-11-23 18:00 | 982 | 977
2018-11-23 18:30 | 968 | 962
2018-11-23 19:00 | 996 | 994
2018-11-23 19:30 | 990 | 986
2018-11-23 20:00 | 975 | 970
2018-11-23 20:30 | 925 | 917
2018-11-23 21:00 | 892 | 890
2018-11-23 21:30 | 829 | 828
2018-11-23 22:00 | 791 | 787
2018-11-23 22:30 | 779 | 772
2018-11-23 23:00 | 775 | 767
2018-11-23 23:30 | 722 | 712
2018-11-24 | 664 | 656
2018-11-24 00:30 | 626 | 612
2018-11-24 01:00 | 604 | 586
2018-11-24 01:30 | 588 | 566
2018-11-24 02:00 | 581 | 554
2018-11-24 02:30 | 572 | 544
2018-11-24 03:00 | 570 | 540
2018-11-24 03:30 | 566 | 535
2018-11-24 04:00 | 567 | 536
2018-11-24 04:30 | 565 | 534
2018-11-24 05:00 | 563 | 527
2018-11-24 05:30 | 572 | 536
2018-11-24 06:00 | 574 | 541
2018-11-24 06:30 | 576 | 550
2018-11-24 07:00 | 584 | 566
2018-11-24 07:30 | 590 | 579
2018-11-24 08:00 | 586 | 578
2018-11-24 08:30 | 590 | 586
2018-11-24 09:00 | 585 | 582
2018-11-24 09:30 | 590 | 589
2018-11-24 10:00 | 578 | 577
2018-11-24 10:30 | 568 | 567
2018-11-24 11:00 | 568 | 567
2018-11-24 11:30 | 559 | 559
2018-11-24 12:00 | 553 | 553
2018-11-24 12:30 | 555 | 554
2018-11-24 13:00 | 564 | 564
2018-11-24 13:30 | 569 | 568
2018-11-24 14:00 | 596 | 596
2018-11-24 14:30 | 631 | 631
2018-11-24 15:00 | 674 | 673
2018-11-24 15:30 | 712 | 711
2018-11-24 16:00 | 749 | 749
2018-11-24 16:30 | 791 | 791
2018-11-24 17:00 | 828 | 826
2018-11-24 17:30 | 877 | 875
2018-11-24 18:00 | 886 | 883
2018-11-24 18:30 | 901 | 896
2018-11-24 19:00 | 933 | 930
2018-11-24 19:30 | 931 | 928
2018-11-24 20:00 | 889 | 884
2018-11-24 20:30 | 847 | 844
2018-11-24 21:00 | 808 | 808
2018-11-24 21:30 | 770 | 770
2018-11-24 22:00 | 743 | 741
2018-11-24 22:30 | 736 | 734
2018-11-24 23:00 | 728 | 724
2018-11-24 23:30 | 693 | 687
2018-11-25 | 651 | 641
2018-11-25 00:30 | 613 | 597
2018-11-25 01:00 | 592 | 573
2018-11-25 01:30 | 581 | 559
2018-11-25 02:00 | 572 | 548
2018-11-25 02:30 | 567 | 541
2018-11-25 03:00 | 565 | 539
2018-11-25 03:30 | 556 | 528
2018-11-25 04:00 | 553 | 524
2018-11-25 04:30 | 553 | 524
2018-11-25 05:00 | 554 | 516
2018-11-25 05:30 | 554 | 514
2018-11-25 06:00 | 555 | 516
2018-11-25 06:30 | 555 | 521
2018-11-25 07:00 | 546 | 519
2018-11-25 07:30 | 555 | 536
2018-11-25 08:00 | 569 | 555
2018-11-25 08:30 | 559 | 548
2018-11-25 09:00 | 578 | 573
2018-11-25 09:30 | 653 | 652
2018-11-25 10:00 | 623 | 622
2018-11-25 10:30 | 620 | 619
2018-11-25 11:00 | 653 | 653
2018-11-25 11:30 | 701 | 700
2018-11-25 12:00 | 678 | 676
2018-11-25 12:30 | 638 | 635
2018-11-25 13:00 | 660 | 657
2018-11-25 13:30 | 704 | 704
2018-11-25 14:00 | 785 | 785
2018-11-25 14:30 | 778 | 777
2018-11-25 15:00 | 806 | 806
2018-11-25 15:30 | 847 | 846
2018-11-25 16:00 | 837 | 834
2018-11-25 16:30 | 843 | 840
2018-11-25 17:00 | 888 | 886
2018-11-25 17:30 | 910 | 909
2018-11-25 18:00 | 930 | 929
2018-11-25 18:30 | 934 | 932
2018-11-25 19:00 | 964 | 963
2018-11-25 19:30 | 957 | 957
2018-11-25 20:00 | 939 | 938
2018-11-25 20:30 | 917 | 915
2018-11-25 21:00 | 876 | 875
2018-11-25 21:30 | 825 | 824
2018-11-25 22:00 | 801 | 799
2018-11-25 22:30 | 774 | 773
2018-11-25 23:00 | 761 | 760
2018-11-25 23:30 | 712 | 708
2018-11-26 | 665 | 657
2018-11-26 00:30 | 625 | 611
2018-11-26 01:00 | 605 | 588
2018-11-26 01:30 | 592 | 572
2018-11-26 02:00 | 577 | 554
2018-11-26 02:30 | 573 | 547
2018-11-26 03:00 | 568 | 543
2018-11-26 03:30 | 567 | 541
2018-11-26 04:00 | 566 | 541
2018-11-26 04:30 | 572 | 548
2018-11-26 05:00 | 584 | 558
2018-11-26 05:30 | 604 | 585
2018-11-26 06:00 | 631 | 619
2018-11-26 06:30 | 671 | 668
2018-11-26 07:00 | 711 | 711
2018-11-26 07:30 | 755 | 755
2018-11-26 08:00 | 769 | 769
2018-11-26 08:30 | 770 | 770
2018-11-26 09:00 | 772 | 772
2018-11-26 09:30 | 781 | 780
2018-11-26 10:00 | 783 | 782
2018-11-26 10:30 | 789 | 787
2018-11-26 11:00 | 794 | 791
2018-11-26 11:30 | 802 | 798
2018-11-26 12:00 | 807 | 803
2018-11-26 12:30 | 816 | 812
2018-11-26 13:00 | 831 | 826
2018-11-26 13:30 | 854 | 848
2018-11-26 14:00 | 878 | 873
2018-11-26 14:30 | 907 | 906
2018-11-26 15:00 | 927 | 925
2018-11-26 15:30 | 952 | 950
2018-11-26 16:00 | 1002 | 1001
2018-11-26 16:30 | 1033 | 1032
2018-11-26 17:00 | 1069 | 1068
2018-11-26 17:30 | 1078 | 1078
2018-11-26 18:00 | 1062 | 1061
2018-11-26 18:30 | 1049 | 1046
2018-11-26 19:00 | 1085 | 1083
2018-11-26 19:30 | 1063 | 1059
2018-11-26 20:00 | 1012 | 1006
2018-11-26 20:30 | 979 | 973
2018-11-26 21:00 | 923 | 919
2018-11-26 21:30 | 861 | 860
2018-11-26 22:00 | 816 | 814
2018-11-26 22:30 | 782 | 781
2018-11-26 23:00 | 770 | 769
2018-11-26 23:30 | 730 | 727
2018-11-27 | 689 | 684
2018-11-27 00:30 | 643 | 633
2018-11-27 01:00 | 610 | 597
2018-11-27 01:30 | 598 | 583
2018-11-27 02:00 | 585 | 568
2018-11-27 02:30 | 581 | 563
2018-11-27 03:00 | 576 | 558
2018-11-27 03:30 | 577 | 559
2018-11-27 04:00 | 577 | 559
2018-11-27 04:30 | 582 | 565
2018-11-27 05:00 | 591 | 572
2018-11-27 05:30 | 611 | 596
2018-11-27 06:00 | 640 | 630
2018-11-27 06:30 | 678 | 675
2018-11-27 07:00 | 725 | 725
2018-11-27 07:30 | 762 | 762
2018-11-27 08:00 | 794 | 792
2018-11-27 08:30 | 818 | 817
2018-11-27 09:00 | 831 | 831
2018-11-27 09:30 | 840 | 840
2018-11-27 10:00 | 840 | 840
2018-11-27 10:30 | 826 | 825
2018-11-27 11:00 | 838 | 837
2018-11-27 11:30 | 856 | 856
2018-11-27 12:00 | 884 | 883
2018-11-27 12:30 | 882 | 880
2018-11-27 13:00 | 862 | 859
2018-11-27 13:30 | 823 | 820
2018-11-27 14:00 | 835 | 833
2018-11-27 14:30 | 856 | 854
2018-11-27 15:00 | 840 | 838
2018-11-27 15:30 | 886 | 885
2018-11-27 16:00 | 954 | 954
2018-11-27 16:30 | 1010 | 1010
2018-11-27 17:00 | 1050 | 1049
2018-11-27 17:30 | 1069 | 1066
2018-11-27 18:00 | 1062 | 1054
2018-11-27 18:30 | 1052 | 1043
2018-11-27 19:00 | 1093 | 1090
2018-11-27 19:30 | 1083 | 1078
2018-11-27 20:00 | 1038 | 1034
2018-11-27 20:30 | 1003 | 1000
2018-11-27 21:00 | 966 | 965
2018-11-27 21:30 | 922 | 918
2018-11-27 22:00 | 864 | 861
2018-11-27 22:30 | 831 | 830
2018-11-27 23:00 | 820 | 819
2018-11-27 23:30 | 769 | 767
2018-11-28 | 722 | 718
2018-11-28 00:30 | 690 | 689
2018-11-28 01:00 | 667 | 665
2018-11-28 01:30 | 635 | 631
2018-11-28 02:00 | 616 | 611
2018-11-28 02:30 | 611 | 606
2018-11-28 03:00 | 605 | 600
2018-11-28 03:30 | 603 | 598
2018-11-28 04:00 | 610 | 605
2018-11-28 04:30 | 620 | 616
2018-11-28 05:00 | 627 | 623
2018-11-28 05:30 | 641 | 639
2018-11-28 06:00 | 686 | 685
2018-11-28 06:30 | 765 | 764
2018-11-28 07:00 | 814 | 814
2018-11-28 07:30 | 887 | 887
2018-11-28 08:00 | 924 | 924
2018-11-28 08:30 | 934 | 934
2018-11-28 09:00 | 945 | 943
2018-11-28 09:30 | 940 | 939
2018-11-28 10:00 | 929 | 928
2018-11-28 10:30 | 953 | 953
2018-11-28 11:00 | 995 | 994
2018-11-28 11:30 | 1024 | 1023
2018-11-28 12:00 | 1073 | 1073
2018-11-28 12:30 | 1179 | 1179
2018-11-28 13:00 | 1143 | 1142
2018-11-28 13:30 | 1078 | 1076
2018-11-28 14:00 | 1093 | 1092
2018-11-28 14:30 | 1113 | 1113
2018-11-28 15:00 | 1127 | 1127
2018-11-28 15:30 | 1147 | 1146
2018-11-28 16:00 | 1209 | 1209
2018-11-28 16:30 | 1254 | 1253
2018-11-28 17:00 | 1323 | 1322
2018-11-28 17:30 | 1333 | 1333
2018-11-28 18:00 | 1302 | 1301
2018-11-28 18:30 | 1272 | 1270
2018-11-28 19:00 | 1288 | 1286
2018-11-28 19:30 | 1265 | 1261
2018-11-28 20:00 | 1219 | 1214
2018-11-28 20:30 | 1157 | 1152
2018-11-28 21:00 | 1088 | 1088
2018-11-28 21:30 | 1031 | 1030
2018-11-28 22:00 | 971 | 967
2018-11-28 22:30 | 925 | 922
2018-11-28 23:00 | 905 | 900
2018-11-28 23:30 | 835 | 833
2018-11-29 | 767 | 765
2018-11-29 00:30 | 712 | 709
2018-11-29 01:00 | 678 | 675
2018-11-29 01:30 | 642 | 637
2018-11-29 02:00 | 627 | 620
2018-11-29 02:30 | 620 | 613
2018-11-29 03:00 | 616 | 609
2018-11-29 03:30 | 614 | 605
2018-11-29 04:00 | 610 | 601
2018-11-29 04:30 | 617 | 610
2018-11-29 05:00 | 615 | 607
2018-11-29 05:30 | 644 | 638
2018-11-29 06:00 | 669 | 667
2018-11-29 06:30 | 716 | 716
2018-11-29 07:00 | 763 | 763
2018-11-29 07:30 | 798 | 798
2018-11-29 08:00 | 806 | 806
2018-11-29 08:30 | 812 | 811
2018-11-29 09:00 | 812 | 810
2018-11-29 09:30 | 816 | 814
2018-11-29 10:00 | 819 | 818
2018-11-29 10:30 | 827 | 827
2018-11-29 11:00 | 836 | 835
2018-11-29 11:30 | 846 | 845
2018-11-29 12:00 | 859 | 858
2018-11-29 12:30 | 878 | 877
2018-11-29 13:00 | 904 | 902
2018-11-29 13:30 | 934 | 934
2018-11-29 14:00 | 971 | 970
2018-11-29 14:30 | 1029 | 1028
2018-11-29 15:00 | 1053 | 1051
2018-11-29 15:30 | 1072 | 1071
2018-11-29 16:00 | 1096 | 1096
2018-11-29 16:30 | 1110 | 1110
2018-11-29 17:00 | 1130 | 1130
2018-11-29 17:30 | 1138 | 1137
2018-11-29 18:00 | 1125 | 1123
2018-11-29 18:30 | 1107 | 1104
2018-11-29 19:00 | 1134 | 1132
2018-11-29 19:30 | 1120 | 1118
2018-11-29 20:00 | 1090 | 1088
2018-11-29 20:30 | 1056 | 1055
2018-11-29 21:00 | 1009 | 1007
2018-11-29 21:30 | 951 | 948
2018-11-29 22:00 | 889 | 887
2018-11-29 22:30 | 862 | 861
2018-11-29 23:00 | 837 | 837
2018-11-29 23:30 | 778 | 777
2018-11-30 | 723 | 722
2018-11-30 00:30 | 680 | 676
2018-11-30 01:00 | 652 | 646
2018-11-30 01:30 | 635 | 627
2018-11-30 02:00 | 622 | 613
2018-11-30 02:30 | 615 | 605
2018-11-30 03:00 | 608 | 599
2018-11-30 03:30 | 609 | 599
2018-11-30 04:00 | 605 | 595
2018-11-30 04:30 | 613 | 603
2018-11-30 05:00 | 623 | 612
2018-11-30 05:30 | 653 | 645
2018-11-30 06:00 | 677 | 673
2018-11-30 06:30 | 721 | 721
2018-11-30 07:00 | 758 | 758
2018-11-30 07:30 | 804 | 804
2018-11-30 08:00 | 811 | 811
2018-11-30 08:30 | 813 | 813
2018-11-30 09:00 | 813 | 813
2018-11-30 09:30 | 825 | 825
2018-11-30 10:00 | 828 | 828
2018-11-30 10:30 | 823 | 823
2018-11-30 11:00 | 835 | 835
2018-11-30 11:30 | 895 | 895
2018-11-30 12:00 | 937 | 936
2018-11-30 12:30 | 922 | 920
2018-11-30 13:00 | 895 | 891
2018-11-30 13:30 | 966 | 965
2018-11-30 14:00 | 941 | 940
2018-11-30 14:30 | 940 | 938
2018-11-30 15:00 | 965 | 964
2018-11-30 15:30 | 1001 | 1000
2018-11-30 16:00 | 1040 | 1038
2018-11-30 16:30 | 1075 | 1073
2018-11-30 17:00 | 1104 | 1102
2018-11-30 17:30 | 1102 | 1098
2018-11-30 18:00 | 1080 | 1073
2018-11-30 18:30 | 1055 | 1046
2018-11-30 19:00 | 1065 | 1065
2018-11-30 19:30 | 1058 | 1057
2018-11-30 20:00 | 1037 | 1036
2018-11-30 20:30 | 1003 | 1001
2018-11-30 21:00 | 960 | 959
2018-11-30 21:30 | 922 | 919
2018-11-30 22:00 | 890 | 886
2018-11-30 22:30 | 870 | 866
2018-11-30 23:00 | 852 | 852
2018-11-30 23:30 | 796 | 795
2018-12-01 | 737 | 734
2018-12-01 00:30 | 683 | 680
2018-12-01 01:00 | 656 | 651
2018-12-01 01:30 | 636 | 629
2018-12-01 02:00 | 620 | 611
2018-12-01 02:30 | 612 | 602
2018-12-01 03:00 | 602 | 592
2018-12-01 03:30 | 598 | 585
2018-12-01 04:00 | 597 | 584
2018-12-01 04:30 | 598 | 586
2018-12-01 05:00 | 591 | 574
2018-12-01 05:30 | 599 | 582
2018-12-01 06:00 | 611 | 597
2018-12-01 06:30 | 626 | 618
2018-12-01 07:00 | 648 | 645
2018-12-01 07:30 | 670 | 670
2018-12-01 08:00 | 688 | 688
2018-12-01 08:30 | 715 | 715
2018-12-01 09:00 | 727 | 727
2018-12-01 09:30 | 740 | 740
2018-12-01 10:00 | 759 | 759
2018-12-01 10:30 | 769 | 769
2018-12-01 11:00 | 796 | 795
2018-12-01 11:30 | 816 | 814
2018-12-01 12:00 | 826 | 824
2018-12-01 12:30 | 841 | 840
2018-12-01 13:00 | 867 | 867
2018-12-01 13:30 | 893 | 893
2018-12-01 14:00 | 925 | 925
2018-12-01 14:30 | 964 | 962
2018-12-01 15:00 | 1007 | 1005
2018-12-01 15:30 | 1056 | 1054
2018-12-01 16:00 | 1099 | 1098
2018-12-01 16:30 | 1133 | 1131
2018-12-01 17:00 | 1172 | 1170
2018-12-01 17:30 | 1173 | 1172
2018-12-01 18:00 | 1158 | 1157
2018-12-01 18:30 | 1142 | 1142
2018-12-01 19:00 | 1151 | 1151
2018-12-01 19:30 | 1139 | 1139
2018-12-01 20:00 | 1129 | 1129
2018-12-01 20:30 | 1100 | 1098
2018-12-01 21:00 | 1048 | 1046
2018-12-01 21:30 | 1001 | 997
2018-12-01 22:00 | 967 | 960
2018-12-01 22:30 | 939 | 935
2018-12-01 23:00 | 909 | 906
2018-12-01 23:30 | 835 | 828
2018-12-02 | 770 | 762
2018-12-02 00:30 | 715 | 708
2018-12-02 01:00 | 687 | 682
2018-12-02 01:30 | 668 | 661
2018-12-02 02:00 | 653 | 644
2018-12-02 02:30 | 640 | 629
2018-12-02 03:00 | 632 | 619
2018-12-02 03:30 | 626 | 612
2018-12-02 04:00 | 621 | 607
2018-12-02 04:30 | 618 | 602
2018-12-02 05:00 | 612 | 592
2018-12-02 05:30 | 622 | 600
2018-12-02 06:00 | 611 | 596
2018-12-02 06:30 | 617 | 607
2018-12-02 07:00 | 631 | 625
2018-12-02 07:30 | 655 | 653
2018-12-02 08:00 | 679 | 679
2018-12-02 08:30 | 711 | 711
2018-12-02 09:00 | 738 | 738
2018-12-02 09:30 | 757 | 756
2018-12-02 10:00 | 758 | 758
2018-12-02 10:30 | 797 | 797
2018-12-02 11:00 | 852 | 850
2018-12-02 11:30 | 891 | 890
2018-12-02 12:00 | 955 | 954
2018-12-02 12:30 | 1016 | 1016
2018-12-02 13:00 | 1016 | 1015
2018-12-02 13:30 | 1065 | 1065
2018-12-02 14:00 | 1112 | 1112
2018-12-02 14:30 | 1152 | 1152
2018-12-02 15:00 | 1195 | 1195
2018-12-02 15:30 | 1242 | 1241
2018-12-02 16:00 | 1274 | 1274
2018-12-02 16:30 | 1295 | 1294
2018-12-02 17:00 | 1343 | 1343
2018-12-02 17:30 | 1354 | 1352
2018-12-02 18:00 | 1353 | 1350
2018-12-02 18:30 | 1347 | 1343
2018-12-02 19:00 | 1352 | 1351
2018-12-02 19:30 | 1339 | 1336
2018-12-02 20:00 | 1301 | 1293
2018-12-02 20:30 | 1255 | 1245
2018-12-02 21:00 | 1191 | 1185
2018-12-02 21:30 | 1128 | 1120
2018-12-02 22:00 | 1036 | 1032
2018-12-02 22:30 | 990 | 988
2018-12-02 23:00 | 960 | 956
2018-12-02 23:30 | 889 | 884
2018-12-03 | 816 | 810
2018-12-03 00:30 | 769 | 764
2018-12-03 01:00 | 739 | 732
2018-12-03 01:30 | 686 | 679
2018-12-03 02:00 | 667 | 659
2018-12-03 02:30 | 660 | 652
2018-12-03 03:00 | 649 | 643
2018-12-03 03:30 | 648 | 642
2018-12-03 04:00 | 653 | 648
2018-12-03 04:30 | 653 | 648
2018-12-03 05:00 | 663 | 659
2018-12-03 05:30 | 689 | 686
2018-12-03 06:00 | 730 | 728
2018-12-03 06:30 | 798 | 797
2018-12-03 07:00 | 848 | 848
2018-12-03 07:30 | 903 | 903
2018-12-03 08:00 | 932 | 932
2018-12-03 08:30 | 949 | 949
2018-12-03 09:00 | 956 | 956
2018-12-03 09:30 | 963 | 963
2018-12-03 10:00 | 965 | 965
2018-12-03 10:30 | 959 | 959
2018-12-03 11:00 | 961 | 961
2018-12-03 11:30 | 954 | 954
2018-12-03 12:00 | 965 | 965
2018-12-03 12:30 | 1018 | 1016
2018-12-03 13:00 | 997 | 994
2018-12-03 13:30 | 1009 | 1007
2018-12-03 14:00 | 1019 | 1017
2018-12-03 14:30 | 1051 | 1049
2018-12-03 15:00 | 1075 | 1073
2018-12-03 15:30 | 1126 | 1124
2018-12-03 16:00 | 1158 | 1156
2018-12-03 16:30 | 1188 | 1186
2018-12-03 17:00 | 1203 | 1200
2018-12-03 17:30 | 1202 | 1196
2018-12-03 18:00 | 1178 | 1165
2018-12-03 18:30 | 1152 | 1142
2018-12-03 19:00 | 1162 | 1156
2018-12-03 19:30 | 1136 | 1129
2018-12-03 20:00 | 1092 | 1088
2018-12-03 20:30 | 1064 | 1059
2018-12-03 21:00 | 1017 | 1011
2018-12-03 21:30 | 957 | 949
2018-12-03 22:00 | 908 | 898
2018-12-03 22:30 | 875 | 863
2018-12-03 23:00 | 847 | 838
2018-12-03 23:30 | 772 | 768
2018-12-04 | 713 | 707
2018-12-04 00:30 | 665 | 658
2018-12-04 01:00 | 637 | 628
2018-12-04 01:30 | 630 | 618
2018-12-04 02:00 | 621 | 607
2018-12-04 02:30 | 612 | 596
2018-12-04 03:00 | 608 | 591
2018-12-04 03:30 | 607 | 591
2018-12-04 04:00 | 606 | 591
2018-12-04 04:30 | 616 | 602
2018-12-04 05:00 | 618 | 604
2018-12-04 05:30 | 641 | 631
2018-12-04 06:00 | 661 | 655
2018-12-04 06:30 | 721 | 719
2018-12-04 07:00 | 763 | 763
2018-12-04 07:30 | 823 | 820
2018-12-04 08:00 | 836 | 835
2018-12-04 08:30 | 874 | 874
2018-12-04 09:00 | 884 | 884
2018-12-04 09:30 | 914 | 914
2018-12-04 10:00 | 918 | 917
2018-12-04 10:30 | 944 | 944
2018-12-04 11:00 | 913 | 912
2018-12-04 11:30 | 949 | 948
2018-12-04 12:00 | 929 | 929
2018-12-04 12:30 | 896 | 895
2018-12-04 13:00 | 942 | 942
2018-12-04 13:30 | 989 | 989
2018-12-04 14:00 | 1040 | 1038
2018-12-04 14:30 | 1085 | 1084
2018-12-04 15:00 | 1083 | 1081
2018-12-04 15:30 | 1074 | 1071
2018-12-04 16:00 | 1072 | 1067
2018-12-04 16:30 | 1084 | 1078
2018-12-04 17:00 | 1089 | 1084
2018-12-04 17:30 | 1094 | 1090
2018-12-04 18:00 | 1073 | 1069
2018-12-04 18:30 | 1065 | 1063
2018-12-04 19:00 | 1103 | 1102
2018-12-04 19:30 | 1087 | 1085
2018-12-04 20:00 | 1070 | 1067
2018-12-04 20:30 | 1047 | 1043
2018-12-04 21:00 | 994 | 993
2018-12-04 21:30 | 932 | 929
2018-12-04 22:00 | 889 | 884
2018-12-04 22:30 | 864 | 857
2018-12-04 23:00 | 836 | 830
2018-12-04 23:30 | 774 | 766
2018-12-05 | 711 | 707
2018-12-05 00:30 | 676 | 669
2018-12-05 01:00 | 661 | 651
2018-12-05 01:30 | 630 | 617
2018-12-05 02:00 | 613 | 597
2018-12-05 02:30 | 609 | 591
2018-12-05 03:00 | 604 | 582
2018-12-05 03:30 | 600 | 578
2018-12-05 04:00 | 603 | 582
2018-12-05 04:30 | 611 | 592
2018-12-05 05:00 | 623 | 604
2018-12-05 05:30 | 656 | 644
2018-12-05 06:00 | 685 | 678
2018-12-05 06:30 | 717 | 713
2018-12-05 07:00 | 763 | 759
2018-12-05 07:30 | 809 | 809
2018-12-05 08:00 | 841 | 840
2018-12-05 08:30 | 841 | 841
2018-12-05 09:00 | 848 | 848
2018-12-05 09:30 | 864 | 863
2018-12-05 10:00 | 874 | 874
2018-12-05 10:30 | 899 | 899
2018-12-05 11:00 | 919 | 919
2018-12-05 11:30 | 883 | 883
2018-12-05 12:00 | 858 | 857
2018-12-05 12:30 | 877 | 876
2018-12-05 13:00 | 894 | 894
2018-12-05 13:30 | 882 | 880
2018-12-05 14:00 | 881 | 879
2018-12-05 14:30 | 883 | 881
2018-12-05 15:00 | 880 | 877
2018-12-05 15:30 | 881 | 877
2018-12-05 16:00 | 910 | 907
2018-12-05 16:30 | 932 | 928
2018-12-05 17:00 | 956 | 953
2018-12-05 17:30 | 971 | 967
2018-12-05 18:00 | 985 | 978
2018-12-05 18:30 | 992 | 982
2018-12-05 19:00 | 1031 | 1025
2018-12-05 19:30 | 1032 | 1027
2018-12-05 20:00 | 1012 | 1005
2018-12-05 20:30 | 980 | 976
2018-12-05 21:00 | 925 | 922
2018-12-05 21:30 | 873 | 871
2018-12-05 22:00 | 818 | 817
2018-12-05 22:30 | 797 | 796
2018-12-05 23:00 | 785 | 784
2018-12-05 23:30 | 732 | 729
2018-12-06 | 681 | 675
2018-12-06 00:30 | 636 | 625
2018-12-06 01:00 | 611 | 596
2018-12-06 01:30 | 599 | 580
2018-12-06 02:00 | 586 | 566
2018-12-06 02:30 | 586 | 563
2018-12-06 03:00 | 584 | 560
2018-12-06 03:30 | 584 | 560
2018-12-06 04:00 | 587 | 563
2018-12-06 04:30 | 593 | 571
2018-12-06 05:00 | 604 | 582
2018-12-06 05:30 | 638 | 621
2018-12-06 06:00 | 672 | 662
2018-12-06 06:30 | 724 | 721
2018-12-06 07:00 | 757 | 756
2018-12-06 07:30 | 812 | 808
2018-12-06 08:00 | 831 | 825
2018-12-06 08:30 | 839 | 835
2018-12-06 09:00 | 818 | 815
2018-12-06 09:30 | 818 | 817
2018-12-06 10:00 | 805 | 804
2018-12-06 10:30 | 795 | 794
2018-12-06 11:00 | 783 | 782
2018-12-06 11:30 | 763 | 763
2018-12-06 12:00 | 751 | 750
2018-12-06 12:30 | 749 | 748
2018-12-06 13:00 | 742 | 742
2018-12-06 13:30 | 754 | 754
2018-12-06 14:00 | 780 | 780
2018-12-06 14:30 | 789 | 788
2018-12-06 15:00 | 789 | 788
2018-12-06 15:30 | 806 | 806
2018-12-06 16:00 | 843 | 842
2018-12-06 16:30 | 875 | 875
2018-12-06 17:00 | 922 | 922
2018-12-06 17:30 | 945 | 944
2018-12-06 18:00 | 941 | 939
2018-12-06 18:30 | 942 | 938
2018-12-06 19:00 | 977 | 975
2018-12-06 19:30 | 992 | 990
2018-12-06 20:00 | 986 | 984
2018-12-06 20:30 | 979 | 975
2018-12-06 21:00 | 942 | 939
2018-12-06 21:30 | 888 | 883
2018-12-06 22:00 | 818 | 814
2018-12-06 22:30 | 803 | 797
2018-12-06 23:00 | 783 | 779
2018-12-06 23:30 | 735 | 729
2018-12-07 | 689 | 678
2018-12-07 00:30 | 641 | 626
2018-12-07 01:00 | 618 | 600
2018-12-07 01:30 | 601 | 580
2018-12-07 02:00 | 597 | 573
2018-12-07 02:30 | 593 | 569
2018-12-07 03:00 | 595 | 569
2018-12-07 03:30 | 595 | 570
2018-12-07 04:00 | 591 | 565
2018-12-07 04:30 | 599 | 575
2018-12-07 05:00 | 607 | 581
2018-12-07 05:30 | 622 | 601
2018-12-07 06:00 | 645 | 631
2018-12-07 06:30 | 681 | 676
2018-12-07 07:00 | 724 | 723
2018-12-07 07:30 | 759 | 758
2018-12-07 08:00 | 782 | 782
2018-12-07 08:30 | 796 | 795
2018-12-07 09:00 | 812 | 808
2018-12-07 09:30 | 823 | 820
2018-12-07 10:00 | 828 | 825
2018-12-07 10:30 | 839 | 838
2018-12-07 11:00 | 820 | 819
2018-12-07 11:30 | 795 | 794
2018-12-07 12:00 | 797 | 795
2018-12-07 12:30 | 798 | 796
2018-12-07 13:00 | 805 | 803
2018-12-07 13:30 | 834 | 832
2018-12-07 14:00 | 839 | 837
2018-12-07 14:30 | 839 | 837
2018-12-07 15:00 | 805 | 802
2018-12-07 15:30 | 793 | 788
2018-12-07 16:00 | 832 | 826
2018-12-07 16:30 | 800 | 794
2018-12-07 17:00 | 845 | 841
2018-12-07 17:30 | 888 | 884
2018-12-07 18:00 | 876 | 870
2018-12-07 18:30 | 855 | 850
2018-12-07 19:00 | 875 | 874
2018-12-07 19:30 | 885 | 885
2018-12-07 20:00 | 875 | 875
2018-12-07 20:30 | 854 | 853
2018-12-07 21:00 | 845 | 844
2018-12-07 21:30 | 828 | 826
2018-12-07 22:00 | 788 | 786
2018-12-07 22:30 | 772 | 770
2018-12-07 23:00 | 764 | 762
2018-12-07 23:30 | 721 | 716
2018-12-08 | 686 | 678
2018-12-08 00:30 | 644 | 631
2018-12-08 01:00 | 620 | 604
2018-12-08 01:30 | 605 | 586
2018-12-08 02:00 | 595 | 572
2018-12-08 02:30 | 590 | 565
2018-12-08 03:00 | 586 | 562
2018-12-08 03:30 | 579 | 553
2018-12-08 04:00 | 585 | 559
2018-12-08 04:30 | 588 | 562
2018-12-08 05:00 | 592 | 565
2018-12-08 05:30 | 599 | 571
2018-12-08 06:00 | 610 | 584
2018-12-08 06:30 | 632 | 613
2018-12-08 07:00 | 655 | 642
2018-12-08 07:30 | 688 | 681
2018-12-08 08:00 | 711 | 708
2018-12-08 08:30 | 728 | 727
2018-12-08 09:00 | 719 | 719
2018-12-08 09:30 | 729 | 729
2018-12-08 10:00 | 711 | 711
2018-12-08 10:30 | 737 | 737
2018-12-08 11:00 | 748 | 748
2018-12-08 11:30 | 758 | 758
2018-12-08 12:00 | 755 | 754
2018-12-08 12:30 | 750 | 749
2018-12-08 13:00 | 762 | 761
2018-12-08 13:30 | 767 | 765
2018-12-08 14:00 | 752 | 749
2018-12-08 14:30 | 740 | 736
2018-12-08 15:00 | 737 | 732
2018-12-08 15:30 | 730 | 725
2018-12-08 16:00 | 729 | 724
2018-12-08 16:30 | 756 | 752
2018-12-08 17:00 | 767 | 764
2018-12-08 17:30 | 774 | 770
2018-12-08 18:00 | 776 | 772
2018-12-08 18:30 | 791 | 787
2018-12-08 19:00 | 823 | 821
2018-12-08 19:30 | 839 | 836
2018-12-08 20:00 | 824 | 819
2018-12-08 20:30 | 808 | 806
2018-12-08 21:00 | 792 | 790
2018-12-08 21:30 | 761 | 759
2018-12-08 22:00 | 747 | 745
2018-12-08 22:30 | 742 | 739
2018-12-08 23:00 | 745 | 742
2018-12-08 23:30 | 707 | 701
2018-12-09 | 669 | 658
2018-12-09 00:30 | 630 | 614
2018-12-09 01:00 | 605 | 586
2018-12-09 01:30 | 600 | 578
2018-12-09 02:00 | 588 | 561
2018-12-09 02:30 | 581 | 553
2018-12-09 03:00 | 574 | 545
2018-12-09 03:30 | 573 | 543
2018-12-09 04:00 | 570 | 540
2018-12-09 04:30 | 568 | 537
2018-12-09 05:00 | 570 | 533
2018-12-09 05:30 | 578 | 539
2018-12-09 06:00 | 573 | 536
2018-12-09 06:30 | 578 | 547
2018-12-09 07:00 | 580 | 553
2018-12-09 07:30 | 595 | 576
2018-12-09 08:00 | 600 | 586
2018-12-09 08:30 | 634 | 628
2018-12-09 09:00 | 646 | 642
2018-12-09 09:30 | 636 | 633
2018-12-09 10:00 | 635 | 633
2018-12-09 10:30 | 633 | 633
2018-12-09 11:00 | 632 | 632
2018-12-09 11:30 | 630 | 630
2018-12-09 12:00 | 647 | 645
2018-12-09 12:30 | 673 | 670
2018-12-09 13:00 | 675 | 673
2018-12-09 13:30 | 686 | 684
2018-12-09 14:00 | 717 | 714
2018-12-09 14:30 | 726 | 723
2018-12-09 15:00 | 732 | 729
2018-12-09 15:30 | 737 | 734
2018-12-09 16:00 | 752 | 749
2018-12-09 16:30 | 782 | 780
2018-12-09 17:00 | 799 | 797
2018-12-09 17:30 | 838 | 834
2018-12-09 18:00 | 868 | 863
2018-12-09 18:30 | 887 | 882
2018-12-09 19:00 | 921 | 918
2018-12-09 19:30 | 938 | 934
2018-12-09 20:00 | 919 | 913
2018-12-09 20:30 | 903 | 895
2018-12-09 21:00 | 865 | 860
2018-12-09 21:30 | 821 | 816
2018-12-09 22:00 | 781 | 776
2018-12-09 22:30 | 760 | 758
2018-12-09 23:00 | 761 | 760
2018-12-09 23:30 | 715 | 711
2018-12-10 | 670 | 663
2018-12-10 00:30 | 637 | 625
2018-12-10 01:00 | 613 | 598
2018-12-10 01:30 | 601 | 584
2018-12-10 02:00 | 592 | 573
2018-12-10 02:30 | 586 | 564
2018-12-10 03:00 | 586 | 563
2018-12-10 03:30 | 589 | 565
2018-12-10 04:00 | 592 | 569
2018-12-10 04:30 | 601 | 581
2018-12-10 05:00 | 605 | 585
2018-12-10 05:30 | 631 | 615
2018-12-10 06:00 | 657 | 649
2018-12-10 06:30 | 700 | 697
2018-12-10 07:00 | 750 | 747
2018-12-10 07:30 | 808 | 806
2018-12-10 08:00 | 844 | 841
2018-12-10 08:30 | 852 | 851
2018-12-10 09:00 | 846 | 846
2018-12-10 09:30 | 839 | 838
2018-12-10 10:00 | 838 | 838
2018-12-10 10:30 | 849 | 848
2018-12-10 11:00 | 860 | 860
2018-12-10 11:30 | 857 | 857
2018-12-10 12:00 | 856 | 856
2018-12-10 12:30 | 863 | 863
2018-12-10 13:00 | 861 | 861
2018-12-10 13:30 | 885 | 885
2018-12-10 14:00 | 903 | 903
2018-12-10 14:30 | 932 | 932
2018-12-10 15:00 | 946 | 946
2018-12-10 15:30 | 1039 | 1038
2018-12-10 16:00 | 1086 | 1085
2018-12-10 16:30 | 1066 | 1066
2018-12-10 17:00 | 1103 | 1103
2018-12-10 17:30 | 1123 | 1123
2018-12-10 18:00 | 1116 | 1115
2018-12-10 18:30 | 1106 | 1104
2018-12-10 19:00 | 1120 | 1119
2018-12-10 19:30 | 1118 | 1117
2018-12-10 20:00 | 1093 | 1091
2018-12-10 20:30 | 1057 | 1051
2018-12-10 21:00 | 1008 | 1000
2018-12-10 21:30 | 942 | 936
2018-12-10 22:00 | 888 | 883
2018-12-10 22:30 | 853 | 849
2018-12-10 23:00 | 832 | 827
2018-12-10 23:30 | 779 | 774
2018-12-11 | 722 | 711
2018-12-11 00:30 | 665 | 657
2018-12-11 01:00 | 632 | 620
2018-12-11 01:30 | 615 | 599
2018-12-11 02:00 | 607 | 590
2018-12-11 02:30 | 602 | 584
2018-12-11 03:00 | 596 | 578
2018-12-11 03:30 | 596 | 577
2018-12-11 04:00 | 595 | 577
2018-12-11 04:30 | 604 | 589
2018-12-11 05:00 | 611 | 595
2018-12-11 05:30 | 633 | 619
2018-12-11 06:00 | 656 | 648
2018-12-11 06:30 | 702 | 699
2018-12-11 07:00 | 748 | 745
2018-12-11 07:30 | 796 | 796
2018-12-11 08:00 | 821 | 821
2018-12-11 08:30 | 846 | 845
2018-12-11 09:00 | 843 | 843
2018-12-11 09:30 | 851 | 851
2018-12-11 10:00 | 839 | 839
2018-12-11 10:30 | 839 | 839
2018-12-11 11:00 | 851 | 851
2018-12-11 11:30 | 874 | 873
2018-12-11 12:00 | 860 | 858
2018-12-11 12:30 | 884 | 883
2018-12-11 13:00 | 878 | 877
2018-12-11 13:30 | 904 | 903
2018-12-11 14:00 | 923 | 922
2018-12-11 14:30 | 956 | 956
2018-12-11 15:00 | 969 | 969
2018-12-11 15:30 | 1022 | 1021
2018-12-11 16:00 | 1076 | 1076
2018-12-11 16:30 | 1121 | 1120
2018-12-11 17:00 | 1105 | 1104
2018-12-11 17:30 | 1090 | 1086
2018-12-11 18:00 | 1105 | 1099
2018-12-11 18:30 | 1096 | 1088
2018-12-11 19:00 | 1120 | 1113
2018-12-11 19:30 | 1115 | 1112
2018-12-11 20:00 | 1093 | 1091
2018-12-11 20:30 | 1059 | 1055
2018-12-11 21:00 | 1021 | 1012
2018-12-11 21:30 | 964 | 956
2018-12-11 22:00 | 900 | 894
2018-12-11 22:30 | 863 | 859
2018-12-11 23:00 | 845 | 841
2018-12-11 23:30 | 800 | 792
2018-12-12 | 729 | 725
2018-12-12 00:30 | 672 | 665
2018-12-12 01:00 | 638 | 628
2018-12-12 01:30 | 621 | 609
2018-12-12 02:00 | 611 | 596
2018-12-12 02:30 | 600 | 584
2018-12-12 03:00 | 602 | 587
2018-12-12 03:30 | 603 | 587
2018-12-12 04:00 | 603 | 588
2018-12-12 04:30 | 611 | 597
2018-12-12 05:00 | 619 | 602
2018-12-12 05:30 | 644 | 631
2018-12-12 06:00 | 665 | 659
2018-12-12 06:30 | 714 | 712
2018-12-12 07:00 | 755 | 754
2018-12-12 07:30 | 817 | 816
2018-12-12 08:00 | 835 | 835
2018-12-12 08:30 | 859 | 859
2018-12-12 09:00 | 854 | 854
2018-12-12 09:30 | 840 | 840
2018-12-12 10:00 | 837 | 836
2018-12-12 10:30 | 835 | 835
2018-12-12 11:00 | 830 | 830
2018-12-12 11:30 | 820 | 819
2018-12-12 12:00 | 820 | 819
2018-12-12 12:30 | 828 | 827
2018-12-12 13:00 | 848 | 845
2018-12-12 13:30 | 859 | 857
2018-12-12 14:00 | 877 | 872
2018-12-12 14:30 | 898 | 891
2018-12-12 15:00 | 929 | 924
2018-12-12 15:30 | 983 | 979
2018-12-12 16:00 | 1040 | 1037
2018-12-12 16:30 | 1084 | 1082
2018-12-12 17:00 | 1111 | 1107
2018-12-12 17:30 | 1137 | 1131
2018-12-12 18:00 | 1128 | 1119
2018-12-12 18:30 | 1090 | 1081
2018-12-12 19:00 | 1112 | 1106
2018-12-12 19:30 | 1098 | 1095
2018-12-12 20:00 | 1088 | 1085
2018-12-12 20:30 | 1066 | 1064
2018-12-12 21:00 | 1020 | 1019
2018-12-12 21:30 | 965 | 962
2018-12-12 22:00 | 909 | 903
2018-12-12 22:30 | 871 | 867
2018-12-12 23:00 | 852 | 849
2018-12-12 23:30 | 804 | 801
2018-12-13 | 738 | 734
2018-12-13 00:30 | 699 | 692
2018-12-13 01:00 | 652 | 642
2018-12-13 01:30 | 631 | 617
2018-12-13 02:00 | 628 | 612
2018-12-13 02:30 | 614 | 596
2018-12-13 03:00 | 618 | 600
2018-12-13 03:30 | 618 | 600
2018-12-13 04:00 | 612 | 595
2018-12-13 04:30 | 622 | 607
2018-12-13 05:00 | 628 | 613
2018-12-13 05:30 | 648 | 635
2018-12-13 06:00 | 675 | 668
2018-12-13 06:30 | 730 | 728
2018-12-13 07:00 | 774 | 773
2018-12-13 07:30 | 826 | 822
2018-12-13 08:00 | 849 | 848
2018-12-13 08:30 | 897 | 897
2018-12-13 09:00 | 869 | 868
2018-12-13 09:30 | 871 | 870
2018-12-13 10:00 | 894 | 892
2018-12-13 10:30 | 892 | 891
2018-12-13 11:00 | 867 | 865
2018-12-13 11:30 | 850 | 849
2018-12-13 12:00 | 865 | 864
2018-12-13 12:30 | 882 | 882
2018-12-13 13:00 | 912 | 912
2018-12-13 13:30 | 957 | 957
2018-12-13 14:00 | 984 | 983
2018-12-13 14:30 | 1012 | 1004
2018-12-13 15:00 | 1034 | 1026
2018-12-13 15:30 | 1076 | 1068
2018-12-13 16:00 | 1110 | 1104
2018-12-13 16:30 | 1143 | 1138
2018-12-13 17:00 | 1167 | 1161
2018-12-13 17:30 | 1151 | 1143
2018-12-13 18:00 | 1169 | 1162
2018-12-13 18:30 | 1159 | 1148
2018-12-13 19:00 | 1176 | 1170
2018-12-13 19:30 | 1165 | 1160
2018-12-13 20:00 | 1138 | 1135
2018-12-13 20:30 | 1110 | 1108
2018-12-13 21:00 | 1075 | 1071
2018-12-13 21:30 | 1007 | 1002
2018-12-13 22:00 | 955 | 943
2018-12-13 22:30 | 921 | 915
2018-12-13 23:00 | 905 | 901
2018-12-13 23:30 | 847 | 840
2018-12-14 | 771 | 765
2018-12-14 00:30 | 728 | 717
2018-12-14 01:00 | 704 | 692
2018-12-14 01:30 | 686 | 676
2018-12-14 02:00 | 678 | 667
2018-12-14 02:30 | 668 | 656
2018-12-14 03:00 | 664 | 650
2018-12-14 03:30 | 664 | 651
2018-12-14 04:00 | 663 | 649
2018-12-14 04:30 | 662 | 650
2018-12-14 05:00 | 674 | 663
2018-12-14 05:30 | 685 | 676
2018-12-14 06:00 | 708 | 705
2018-12-14 06:30 | 776 | 774
2018-12-14 07:00 | 846 | 846
2018-12-14 07:30 | 949 | 944
2018-12-14 08:00 | 1006 | 1003
2018-12-14 08:30 | 1065 | 1062
2018-12-14 09:00 | 1072 | 1070
2018-12-14 09:30 | 1059 | 1058
2018-12-14 10:00 | 1045 | 1044
2018-12-14 10:30 | 998 | 996
2018-12-14 11:00 | 937 | 934
2018-12-14 11:30 | 919 | 916
2018-12-14 12:00 | 926 | 924
2018-12-14 12:30 | 951 | 950
2018-12-14 13:00 | 966 | 966
2018-12-14 13:30 | 1001 | 1001
2018-12-14 14:00 | 1038 | 1038
2018-12-14 14:30 | 1067 | 1065
2018-12-14 15:00 | 1057 | 1054
2018-12-14 15:30 | 1079 | 1076
2018-12-14 16:00 | 1165 | 1164
2018-12-14 16:30 | 1191 | 1190
2018-12-14 17:00 | 1192 | 1189
2018-12-14 17:30 | 1157 | 1150
2018-12-14 18:00 | 1101 | 1092
2018-12-14 18:30 | 1087 | 1075
2018-12-14 19:00 | 1096 | 1088
2018-12-14 19:30 | 1076 | 1074
2018-12-14 20:00 | 1063 | 1062
2018-12-14 20:30 | 1037 | 1034
2018-12-14 21:00 | 994 | 994
2018-12-14 21:30 | 948 | 947
2018-12-14 22:00 | 918 | 914
2018-12-14 22:30 | 896 | 890
2018-12-14 23:00 | 880 | 876
2018-12-14 23:30 | 826 | 824
2018-12-15 | 766 | 760
2018-12-15 00:30 | 717 | 708
2018-12-15 01:00 | 682 | 679
2018-12-15 01:30 | 668 | 663
2018-12-15 02:00 | 651 | 644
2018-12-15 02:30 | 641 | 633
2018-12-15 03:00 | 632 | 624
2018-12-15 03:30 | 631 | 623
2018-12-15 04:00 | 628 | 620
2018-12-15 04:30 | 631 | 622
2018-12-15 05:00 | 632 | 624
2018-12-15 05:30 | 635 | 625
2018-12-15 06:00 | 648 | 640
2018-12-15 06:30 | 673 | 669
2018-12-15 07:00 | 677 | 675
2018-12-15 07:30 | 707 | 707
2018-12-15 08:00 | 744 | 744
2018-12-15 08:30 | 787 | 787
2018-12-15 09:00 | 789 | 789
2018-12-15 09:30 | 794 | 794
2018-12-15 10:00 | 802 | 802
2018-12-15 10:30 | 823 | 823
2018-12-15 11:00 | 849 | 848
2018-12-15 11:30 | 875 | 875
2018-12-15 12:00 | 876 | 876
2018-12-15 12:30 | 867 | 867
2018-12-15 13:00 | 884 | 884
2018-12-15 13:30 | 908 | 908
2018-12-15 14:00 | 906 | 906
2018-12-15 14:30 | 911 | 911
2018-12-15 15:00 | 938 | 938
2018-12-15 15:30 | 950 | 949
2018-12-15 16:00 | 966 | 966
2018-12-15 16:30 | 984 | 983
2018-12-15 17:00 | 1028 | 1027
2018-12-15 17:30 | 1052 | 1045
2018-12-15 18:00 | 1045 | 1035
2018-12-15 18:30 | 1040 | 1027
2018-12-15 19:00 | 1030 | 1025
2018-12-15 19:30 | 1005 | 1000
2018-12-15 20:00 | 984 | 979
2018-12-15 20:30 | 955 | 950
2018-12-15 21:00 | 919 | 917
2018-12-15 21:30 | 891 | 891
2018-12-15 22:00 | 863 | 862
2018-12-15 22:30 | 853 | 852
2018-12-15 23:00 | 842 | 840
2018-12-15 23:30 | 796 | 793
2018-12-16 | 747 | 742
2018-12-16 00:30 | 706 | 698
2018-12-16 01:00 | 678 | 667
2018-12-16 01:30 | 657 | 649
2018-12-16 02:00 | 642 | 635
2018-12-16 02:30 | 632 | 625
2018-12-16 03:00 | 623 | 614
2018-12-16 03:30 | 624 | 615
2018-12-16 04:00 | 618 | 609
2018-12-16 04:30 | 620 | 609
2018-12-16 05:00 | 616 | 603
2018-12-16 05:30 | 623 | 609
2018-12-16 06:00 | 634 | 621
2018-12-16 06:30 | 649 | 640
2018-12-16 07:00 | 665 | 659
2018-12-16 07:30 | 696 | 694
2018-12-16 08:00 | 736 | 736
2018-12-16 08:30 | 780 | 780
2018-12-16 09:00 | 798 | 798
2018-12-16 09:30 | 834 | 834
2018-12-16 10:00 | 866 | 866
2018-12-16 10:30 | 867 | 867
2018-12-16 11:00 | 861 | 861
2018-12-16 11:30 | 856 | 856
2018-12-16 12:00 | 838 | 838
2018-12-16 12:30 | 843 | 843
2018-12-16 13:00 | 834 | 834
2018-12-16 13:30 | 830 | 830
2018-12-16 14:00 | 826 | 826
2018-12-16 14:30 | 828 | 828
2018-12-16 15:00 | 835 | 834
2018-12-16 15:30 | 842 | 841
2018-12-16 16:00 | 868 | 868
2018-12-16 16:30 | 873 | 873
2018-12-16 17:00 | 888 | 888
2018-12-16 17:30 | 895 | 895
2018-12-16 18:00 | 901 | 901
2018-12-16 18:30 | 905 | 905
2018-12-16 19:00 | 916 | 916
2018-12-16 19:30 | 899 | 898
2018-12-16 20:00 | 893 | 893
2018-12-16 20:30 | 878 | 876
2018-12-16 21:00 | 845 | 842
2018-12-16 21:30 | 814 | 808
2018-12-16 22:00 | 789 | 781
2018-12-16 22:30 | 769 | 766
2018-12-16 23:00 | 765 | 762
2018-12-16 23:30 | 713 | 709
2018-12-17 | 667 | 660
2018-12-17 00:30 | 625 | 613
2018-12-17 01:00 | 605 | 591
2018-12-17 01:30 | 601 | 587
2018-12-17 02:00 | 602 | 586
2018-12-17 02:30 | 586 | 569
2018-12-17 03:00 | 583 | 566
2018-12-17 03:30 | 589 | 571
2018-12-17 04:00 | 584 | 567
2018-12-17 04:30 | 597 | 581
2018-12-17 05:00 | 610 | 594
2018-12-17 05:30 | 637 | 625
2018-12-17 06:00 | 669 | 662
2018-12-17 06:30 | 719 | 717
2018-12-17 07:00 | 754 | 751
2018-12-17 07:30 | 822 | 819
2018-12-17 08:00 | 878 | 875
2018-12-17 08:30 | 920 | 916
2018-12-17 09:00 | 932 | 930
2018-12-17 09:30 | 915 | 914
2018-12-17 10:00 | 916 | 913
2018-12-17 10:30 | 888 | 886
2018-12-17 11:00 | 880 | 880
2018-12-17 11:30 | 915 | 914
2018-12-17 12:00 | 914 | 913
2018-12-17 12:30 | 919 | 919
2018-12-17 13:00 | 928 | 928
2018-12-17 13:30 | 921 | 920
2018-12-17 14:00 | 930 | 930
2018-12-17 14:30 | 949 | 949
2018-12-17 15:00 | 967 | 967
2018-12-17 15:30 | 976 | 975
2018-12-17 16:00 | 992 | 991
2018-12-17 16:30 | 1006 | 1005
2018-12-17 17:00 | 1008 | 1006
2018-12-17 17:30 | 1010 | 1007
2018-12-17 18:00 | 997 | 993
2018-12-17 18:30 | 986 | 984
2018-12-17 19:00 | 999 | 998
2018-12-17 19:30 | 1001 | 1000
2018-12-17 20:00 | 989 | 988
2018-12-17 20:30 | 967 | 965
2018-12-17 21:00 | 924 | 921
2018-12-17 21:30 | 873 | 871
2018-12-17 22:00 | 830 | 829
2018-12-17 22:30 | 812 | 810
2018-12-17 23:00 | 795 | 790
2018-12-17 23:30 | 746 | 739
2018-12-18 | 698 | 687
2018-12-18 00:30 | 658 | 641
2018-12-18 01:00 | 624 | 612
2018-12-18 01:30 | 615 | 603
2018-12-18 02:00 | 607 | 595
2018-12-18 02:30 | 601 | 587
2018-12-18 03:00 | 599 | 584
2018-12-18 03:30 | 598 | 583
2018-12-18 04:00 | 601 | 588
2018-12-18 04:30 | 606 | 595
2018-12-18 05:00 | 618 | 606
2018-12-18 05:30 | 644 | 637
2018-12-18 06:00 | 666 | 661
2018-12-18 06:30 | 708 | 707
2018-12-18 07:00 | 757 | 757
2018-12-18 07:30 | 799 | 799
2018-12-18 08:00 | 831 | 831
2018-12-18 08:30 | 851 | 851
2018-12-18 09:00 | 869 | 868
2018-12-18 09:30 | 860 | 860
2018-12-18 10:00 | 850 | 849
2018-12-18 10:30 | 856 | 856
2018-12-18 11:00 | 855 | 855
2018-12-18 11:30 | 876 | 876
2018-12-18 12:00 | 883 | 883
2018-12-18 12:30 | 899 | 899
2018-12-18 13:00 | 928 | 928
2018-12-18 13:30 | 936 | 936
2018-12-18 14:00 | 961 | 961
2018-12-18 14:30 | 982 | 982
2018-12-18 15:00 | 991 | 991
2018-12-18 15:30 | 1010 | 1010
2018-12-18 16:00 | 1024 | 1024
2018-12-18 16:30 | 1052 | 1052
2018-12-18 17:00 | 1107 | 1107
2018-12-18 17:30 | 1131 | 1128
2018-12-18 18:00 | 1128 | 1121
2018-12-18 18:30 | 1104 | 1102
2018-12-18 19:00 | 1123 | 1121
2018-12-18 19:30 | 1135 | 1134
2018-12-18 20:00 | 1091 | 1089
2018-12-18 20:30 | 1046 | 1043
2018-12-18 21:00 | 1010 | 1007
2018-12-18 21:30 | 938 | 936
2018-12-18 22:00 | 899 | 895
2018-12-18 22:30 | 860 | 855
2018-12-18 23:00 | 849 | 846
2018-12-18 23:30 | 794 | 791
2018-12-19 | 731 | 728
2018-12-19 00:30 | 684 | 677
2018-12-19 01:00 | 660 | 650
2018-12-19 01:30 | 645 | 633
2018-12-19 02:00 | 638 | 625
2018-12-19 02:30 | 632 | 619
2018-12-19 03:00 | 626 | 612
2018-12-19 03:30 | 625 | 610
2018-12-19 04:00 | 614 | 596
2018-12-19 04:30 | 626 | 610
2018-12-19 05:00 | 636 | 621
2018-12-19 05:30 | 656 | 645
2018-12-19 06:00 | 677 | 671
2018-12-19 06:30 | 724 | 723
2018-12-19 07:00 | 775 | 774
2018-12-19 07:30 | 830 | 829
2018-12-19 08:00 | 858 | 858
2018-12-19 08:30 | 889 | 888
2018-12-19 09:00 | 897 | 895
2018-12-19 09:30 | 895 | 894
2018-12-19 10:00 | 896 | 894
2018-12-19 10:30 | 900 | 898
2018-12-19 11:00 | 903 | 901
2018-12-19 11:30 | 921 | 920
2018-12-19 12:00 | 931 | 929
2018-12-19 12:30 | 945 | 943
2018-12-19 13:00 | 955 | 954
2018-12-19 13:30 | 970 | 969
2018-12-19 14:00 | 998 | 998
2018-12-19 14:30 | 1032 | 1031
2018-12-19 15:00 | 1080 | 1079
2018-12-19 15:30 | 1116 | 1115
2018-12-19 16:00 | 1134 | 1133
2018-12-19 16:30 | 1167 | 1167
2018-12-19 17:00 | 1199 | 1199
2018-12-19 17:30 | 1201 | 1201
2018-12-19 18:00 | 1196 | 1196
2018-12-19 18:30 | 1182 | 1180
2018-12-19 19:00 | 1187 | 1185
2018-12-19 19:30 | 1188 | 1187
2018-12-19 20:00 | 1158 | 1156
2018-12-19 20:30 | 1127 | 1124
2018-12-19 21:00 | 1074 | 1072
2018-12-19 21:30 | 1014 | 1012
2018-12-19 22:00 | 967 | 966
2018-12-19 22:30 | 913 | 913
2018-12-19 23:00 | 896 | 895
2018-12-19 23:30 | 839 | 836
2018-12-20 | 778 | 776
2018-12-20 00:30 | 711 | 706
2018-12-20 01:00 | 688 | 679
2018-12-20 01:30 | 676 | 664
2018-12-20 02:00 | 667 | 652
2018-12-20 02:30 | 664 | 649
2018-12-20 03:00 | 661 | 646
2018-12-20 03:30 | 656 | 640
2018-12-20 04:00 | 658 | 642
2018-12-20 04:30 | 664 | 651
2018-12-20 05:00 | 671 | 657
2018-12-20 05:30 | 692 | 681
2018-12-20 06:00 | 718 | 713
2018-12-20 06:30 | 762 | 761
2018-12-20 07:00 | 824 | 823
2018-12-20 07:30 | 870 | 870
2018-12-20 08:00 | 896 | 894
2018-12-20 08:30 | 929 | 927
2018-12-20 09:00 | 937 | 935
2018-12-20 09:30 | 940 | 938
2018-12-20 10:00 | 951 | 948
2018-12-20 10:30 | 961 | 957
2018-12-20 11:00 | 972 | 970
2018-12-20 11:30 | 992 | 991
2018-12-20 12:00 | 1017 | 1016
2018-12-20 12:30 | 1041 | 1040
2018-12-20 13:00 | 1042 | 1041
2018-12-20 13:30 | 1086 | 1086
2018-12-20 14:00 | 1112 | 1112
2018-12-20 14:30 | 1136 | 1136
2018-12-20 15:00 | 1161 | 1161
2018-12-20 15:30 | 1220 | 1220
2018-12-20 16:00 | 1302 | 1302
2018-12-20 16:30 | 1360 | 1360
2018-12-20 17:00 | 1388 | 1388
2018-12-20 17:30 | 1395 | 1395
2018-12-20 18:00 | 1385 | 1383
2018-12-20 18:30 | 1361 | 1356
2018-12-20 19:00 | 1352 | 1348
2018-12-20 19:30 | 1335 | 1335
2018-12-20 20:00 | 1317 | 1317
2018-12-20 20:30 | 1290 | 1290
2018-12-20 21:00 | 1233 | 1231
2018-12-20 21:30 | 1157 | 1153
2018-12-20 22:00 | 1098 | 1094
2018-12-20 22:30 | 1057 | 1055
2018-12-20 23:00 | 1023 | 1020
2018-12-20 23:30 | 934 | 933
2018-12-21 | 863 | 860
2018-12-21 00:30 | 795 | 787
2018-12-21 01:00 | 755 | 746
2018-12-21 01:30 | 731 | 727
2018-12-21 02:00 | 717 | 711
2018-12-21 02:30 | 705 | 698
2018-12-21 03:00 | 703 | 696
2018-12-21 03:30 | 703 | 696
2018-12-21 04:00 | 695 | 687
2018-12-21 04:30 | 698 | 690
2018-12-21 05:00 | 701 | 693
2018-12-21 05:30 | 720 | 713
2018-12-21 06:00 | 743 | 740
2018-12-21 06:30 | 793 | 793
2018-12-21 07:00 | 856 | 856
2018-12-21 07:30 | 927 | 927
2018-12-21 08:00 | 980 | 979
2018-12-21 08:30 | 1013 | 1013
2018-12-21 09:00 | 1060 | 1059
2018-12-21 09:30 | 1090 | 1089
2018-12-21 10:00 | 1067 | 1066
2018-12-21 10:30 | 1061 | 1060
2018-12-21 11:00 | 1099 | 1098
2018-12-21 11:30 | 1126 | 1125
2018-12-21 12:00 | 1151 | 1151
2018-12-21 12:30 | 1172 | 1171
2018-12-21 13:00 | 1209 | 1207
2018-12-21 13:30 | 1263 | 1263
2018-12-21 14:00 | 1308 | 1308
2018-12-21 14:30 | 1353 | 1353
2018-12-21 15:00 | 1406 | 1405
2018-12-21 15:30 | 1463 | 1461
2018-12-21 16:00 | 1559 | 1557
2018-12-21 16:30 | 1586 | 1585
2018-12-21 17:00 | 1574 | 1573
2018-12-21 17:30 | 1515 | 1514
2018-12-21 18:00 | 1395 | 1389
2018-12-21 18:30 | 1255 | 1249
2018-12-21 19:00 | 1200 | 1193
2018-12-21 19:30 | 1150 | 1144
2018-12-21 20:00 | 1097 | 1093
2018-12-21 20:30 | 1086 | 1083
2018-12-21 21:00 | 1051 | 1047
2018-12-21 21:30 | 989 | 982
2018-12-21 22:00 | 955 | 943
2018-12-21 22:30 | 881 | 871
2018-12-21 23:00 | 864 | 861
2018-12-21 23:30 | 821 | 820
2018-12-22 | 775 | 772
2018-12-22 00:30 | 738 | 736
2018-12-22 01:00 | 723 | 721
2018-12-22 01:30 | 695 | 690
2018-12-22 02:00 | 671 | 664
2018-12-22 02:30 | 659 | 651
2018-12-22 03:00 | 650 | 641
2018-12-22 03:30 | 641 | 630
2018-12-22 04:00 | 636 | 625
2018-12-22 04:30 | 636 | 625
2018-12-22 05:00 | 638 | 627
2018-12-22 05:30 | 642 | 628
2018-12-22 06:00 | 646 | 633
2018-12-22 06:30 | 671 | 663
2018-12-22 07:00 | 701 | 697
2018-12-22 07:30 | 726 | 725
2018-12-22 08:00 | 732 | 731
2018-12-22 08:30 | 769 | 768
2018-12-22 09:00 | 819 | 817
2018-12-22 09:30 | 856 | 854
2018-12-22 10:00 | 855 | 853
2018-12-22 10:30 | 839 | 837
2018-12-22 11:00 | 838 | 836
2018-12-22 11:30 | 868 | 866
2018-12-22 12:00 | 886 | 885
2018-12-22 12:30 | 918 | 917
2018-12-22 13:00 | 963 | 962
2018-12-22 13:30 | 998 | 998
2018-12-22 14:00 | 1044 | 1044
2018-12-22 14:30 | 1138 | 1138
2018-12-22 15:00 | 1150 | 1150
2018-12-22 15:30 | 1189 | 1189
2018-12-22 16:00 | 1224 | 1223
2018-12-22 16:30 | 1207 | 1204
2018-12-22 17:00 | 1173 | 1165
2018-12-22 17:30 | 1107 | 1084
2018-12-22 18:00 | 1019 | 1006
2018-12-22 18:30 | 989 | 978
2018-12-22 19:00 | 986 | 974
2018-12-22 19:30 | 970 | 963
2018-12-22 20:00 | 949 | 939
2018-12-22 20:30 | 926 | 914
2018-12-22 21:00 | 878 | 872
2018-12-22 21:30 | 839 | 833
2018-12-22 22:00 | 801 | 797
2018-12-22 22:30 | 789 | 785
2018-12-22 23:00 | 777 | 772
2018-12-22 23:30 | 721 | 713
2018-12-23 | 649 | 643
2018-12-23 00:30 | 611 | 602
2018-12-23 01:00 | 598 | 585
2018-12-23 01:30 | 583 | 569
2018-12-23 02:00 | 572 | 554
2018-12-23 02:30 | 570 | 550
2018-12-23 03:00 | 568 | 547
2018-12-23 03:30 | 563 | 540
2018-12-23 04:00 | 558 | 535
2018-12-23 04:30 | 555 | 532
2018-12-23 05:00 | 552 | 526
2018-12-23 05:30 | 550 | 519
2018-12-23 06:00 | 545 | 516
2018-12-23 06:30 | 545 | 521
2018-12-23 07:00 | 532 | 513
2018-12-23 07:30 | 533 | 519
2018-12-23 08:00 | 532 | 521
2018-12-23 08:30 | 540 | 534
2018-12-23 09:00 | 558 | 554
2018-12-23 09:30 | 557 | 555
2018-12-23 10:00 | 561 | 560
2018-12-23 10:30 | 567 | 566
2018-12-23 11:00 | 579 | 578
2018-12-23 11:30 | 583 | 583
2018-12-23 12:00 | 575 | 575
2018-12-23 12:30 | 584 | 582
2018-12-23 13:00 | 588 | 586
2018-12-23 13:30 | 584 | 582
2018-12-23 14:00 | 589 | 588
2018-12-23 14:30 | 611 | 610
2018-12-23 15:00 | 643 | 642
2018-12-23 15:30 | 663 | 662
2018-12-23 16:00 | 694 | 693
2018-12-23 16:30 | 722 | 722
2018-12-23 17:00 | 754 | 754
2018-12-23 17:30 | 775 | 774
2018-12-23 18:00 | 786 | 783
2018-12-23 18:30 | 802 | 799
2018-12-23 19:00 | 826 | 823
2018-12-23 19:30 | 844 | 843
2018-12-23 20:00 | 837 | 836
2018-12-23 20:30 | 824 | 822
2018-12-23 21:00 | 793 | 789
2018-12-23 21:30 | 760 | 753
2018-12-23 22:00 | 745 | 736
2018-12-23 22:30 | 745 | 737
2018-12-23 23:00 | 745 | 738
2018-12-23 23:30 | 698 | 694
2018-12-24 | 648 | 640
2018-12-24 00:30 | 612 | 598
2018-12-24 01:00 | 586 | 569
2018-12-24 01:30 | 579 | 559
2018-12-24 02:00 | 570 | 548
2018-12-24 02:30 | 555 | 529
2018-12-24 03:00 | 545 | 519
2018-12-24 03:30 | 545 | 517
2018-12-24 04:00 | 547 | 520
2018-12-24 04:30 | 543 | 517
2018-12-24 05:00 | 549 | 521
2018-12-24 05:30 | 559 | 533
2018-12-24 06:00 | 564 | 541
2018-12-24 06:30 | 588 | 574
2018-12-24 07:00 | 599 | 592
2018-12-24 07:30 | 619 | 617
2018-12-24 08:00 | 645 | 645
2018-12-24 08:30 | 650 | 650
2018-12-24 09:00 | 690 | 690
2018-12-24 09:30 | 736 | 736
2018-12-24 10:00 | 722 | 722
2018-12-24 10:30 | 708 | 708
2018-12-24 11:00 | 702 | 702
2018-12-24 11:30 | 692 | 692
2018-12-24 12:00 | 667 | 667
2018-12-24 12:30 | 646 | 646
2018-12-24 13:00 | 665 | 665
2018-12-24 13:30 | 665 | 665
2018-12-24 14:00 | 677 | 677
2018-12-24 14:30 | 694 | 694
2018-12-24 15:00 | 719 | 719
2018-12-24 15:30 | 754 | 754
2018-12-24 16:00 | 795 | 795
2018-12-24 16:30 | 828 | 828
2018-12-24 17:00 | 867 | 865
2018-12-24 17:30 | 880 | 878
2018-12-24 18:00 | 865 | 861
2018-12-24 18:30 | 847 | 842
2018-12-24 19:00 | 851 | 847
2018-12-24 19:30 | 855 | 852
2018-12-24 20:00 | 852 | 849
2018-12-24 20:30 | 834 | 833
2018-12-24 21:00 | 805 | 804
2018-12-24 21:30 | 776 | 775
2018-12-24 22:00 | 760 | 759
2018-12-24 22:30 | 748 | 746
2018-12-24 23:00 | 748 | 745
2018-12-24 23:30 | 705 | 699
2018-12-25 | 661 | 652
2018-12-25 00:30 | 616 | 602
2018-12-25 01:00 | 580 | 563
2018-12-25 01:30 | 556 | 534
2018-12-25 02:00 | 543 | 517
2018-12-25 02:30 | 532 | 506
2018-12-25 03:00 | 524 | 495
2018-12-25 03:30 | 518 | 487
2018-12-25 04:00 | 517 | 484
2018-12-25 04:30 | 517 | 484
2018-12-25 05:00 | 521 | 484
2018-12-25 05:30 | 534 | 498
2018-12-25 06:00 | 537 | 503
2018-12-25 06:30 | 540 | 511
2018-12-25 07:00 | 536 | 513
2018-12-25 07:30 | 545 | 529
2018-12-25 08:00 | 534 | 521
2018-12-25 08:30 | 548 | 539
2018-12-25 09:00 | 556 | 550
2018-12-25 09:30 | 568 | 564
2018-12-25 10:00 | 576 | 573
2018-12-25 10:30 | 576 | 574
2018-12-25 11:00 | 578 | 576
2018-12-25 11:30 | 556 | 554
2018-12-25 12:00 | 549 | 546
2018-12-25 12:30 | 544 | 542
2018-12-25 13:00 | 520 | 518
2018-12-25 13:30 | 517 | 515
2018-12-25 14:00 | 536 | 534
2018-12-25 14:30 | 553 | 551
2018-12-25 15:00 | 570 | 569
2018-12-25 15:30 | 599 | 598
2018-12-25 16:00 | 623 | 622
2018-12-25 16:30 | 666 | 666
2018-12-25 17:00 | 691 | 691
2018-12-25 17:30 | 717 | 717
2018-12-25 18:00 | 724 | 724
2018-12-25 18:30 | 728 | 727
2018-12-25 19:00 | 733 | 732
2018-12-25 19:30 | 756 | 756
2018-12-25 20:00 | 760 | 760
2018-12-25 20:30 | 754 | 754
2018-12-25 21:00 | 737 | 736
2018-12-25 21:30 | 720 | 717
2018-12-25 22:00 | 706 | 703
2018-12-25 22:30 | 703 | 698
2018-12-25 23:00 | 702 | 697
2018-12-25 23:30 | 673 | 665
2018-12-26 | 635 | 621
2018-12-26 00:30 | 600 | 583
2018-12-26 01:00 | 580 | 559
2018-12-26 01:30 | 568 | 546
2018-12-26 02:00 | 561 | 535
2018-12-26 02:30 | 555 | 528
2018-12-26 03:00 | 550 | 522
2018-12-26 03:30 | 552 | 522
2018-12-26 04:00 | 550 | 519
2018-12-26 04:30 | 543 | 513
2018-12-26 05:00 | 546 | 512
2018-12-26 05:30 | 549 | 513
2018-12-26 06:00 | 549 | 514
2018-12-26 06:30 | 552 | 523
2018-12-26 07:00 | 552 | 528
2018-12-26 07:30 | 550 | 535
2018-12-26 08:00 | 548 | 538
2018-12-26 08:30 | 563 | 558
2018-12-26 09:00 | 587 | 585
2018-12-26 09:30 | 596 | 595
2018-12-26 10:00 | 581 | 580
2018-12-26 10:30 | 576 | 576
2018-12-26 11:00 | 578 | 577
2018-12-26 11:30 | 559 | 558
2018-12-26 12:00 | 556 | 552
2018-12-26 12:30 | 546 | 542
2018-12-26 13:00 | 542 | 537
2018-12-26 13:30 | 545 | 541
2018-12-26 14:00 | 557 | 554
2018-12-26 14:30 | 578 | 576
2018-12-26 15:00 | 608 | 607
2018-12-26 15:30 | 649 | 649
2018-12-26 16:00 | 686 | 686
2018-12-26 16:30 | 728 | 728
2018-12-26 17:00 | 778 | 777
2018-12-26 17:30 | 803 | 803
2018-12-26 18:00 | 810 | 809
2018-12-26 18:30 | 817 | 815
2018-12-26 19:00 | 828 | 827
2018-12-26 19:30 | 841 | 841
2018-12-26 20:00 | 836 | 836
2018-12-26 20:30 | 822 | 822
2018-12-26 21:00 | 786 | 786
2018-12-26 21:30 | 757 | 757
2018-12-26 22:00 | 739 | 739
2018-12-26 22:30 | 729 | 727
2018-12-26 23:00 | 723 | 721
2018-12-26 23:30 | 683 | 679
2018-12-27 | 644 | 636
2018-12-27 00:30 | 605 | 594
2018-12-27 01:00 | 577 | 562
2018-12-27 01:30 | 560 | 543
2018-12-27 02:00 | 552 | 533
2018-12-27 02:30 | 553 | 532
2018-12-27 03:00 | 558 | 537
2018-12-27 03:30 | 561 | 540
2018-12-27 04:00 | 561 | 537
2018-12-27 04:30 | 562 | 539
2018-12-27 05:00 | 568 | 543
2018-12-27 05:30 | 580 | 554
2018-12-27 06:00 | 582 | 561
2018-12-27 06:30 | 600 | 586
2018-12-27 07:00 | 616 | 608
2018-12-27 07:30 | 630 | 627
2018-12-27 08:00 | 621 | 621
2018-12-27 08:30 | 634 | 634
2018-12-27 09:00 | 653 | 653
2018-12-27 09:30 | 659 | 659
2018-12-27 10:00 | 662 | 661
2018-12-27 10:30 | 652 | 652
2018-12-27 11:00 | 647 | 647
2018-12-27 11:30 | 646 | 646
2018-12-27 12:00 | 650 | 650
2018-12-27 12:30 | 650 | 650
2018-12-27 13:00 | 660 | 660
2018-12-27 13:30 | 671 | 671
2018-12-27 14:00 | 724 | 724
2018-12-27 14:30 | 741 | 741
2018-12-27 15:00 | 769 | 769
2018-12-27 15:30 | 805 | 804
2018-12-27 16:00 | 827 | 826
2018-12-27 16:30 | 870 | 870
2018-12-27 17:00 | 908 | 908
2018-12-27 17:30 | 930 | 929
2018-12-27 18:00 | 927 | 925
2018-12-27 18:30 | 921 | 916
2018-12-27 19:00 | 917 | 912
2018-12-27 19:30 | 928 | 926
2018-12-27 20:00 | 916 | 912
2018-12-27 20:30 | 892 | 889
2018-12-27 21:00 | 853 | 852
2018-12-27 21:30 | 812 | 811
2018-12-27 22:00 | 781 | 781
2018-12-27 22:30 | 769 | 768
2018-12-27 23:00 | 757 | 756
2018-12-27 23:30 | 716 | 713
2018-12-28 | 671 | 665
2018-12-28 00:30 | 628 | 618
2018-12-28 01:00 | 605 | 593
2018-12-28 01:30 | 593 | 579
2018-12-28 02:00 | 586 | 569
2018-12-28 02:30 | 577 | 558
2018-12-28 03:00 | 572 | 551
2018-12-28 03:30 | 560 | 539
2018-12-28 04:00 | 560 | 538
2018-12-28 04:30 | 570 | 549
2018-12-28 05:00 | 578 | 556
2018-12-28 05:30 | 584 | 563
2018-12-28 06:00 | 588 | 572
2018-12-28 06:30 | 615 | 605
2018-12-28 07:00 | 631 | 626
2018-12-28 07:30 | 663 | 662
2018-12-28 08:00 | 688 | 687
2018-12-28 08:30 | 717 | 716
2018-12-28 09:00 | 723 | 722
2018-12-28 09:30 | 732 | 732
2018-12-28 10:00 | 738 | 737
2018-12-28 10:30 | 738 | 738
2018-12-28 11:00 | 725 | 725
2018-12-28 11:30 | 725 | 724
2018-12-28 12:00 | 727 | 727
2018-12-28 12:30 | 725 | 725
2018-12-28 13:00 | 735 | 735
2018-12-28 13:30 | 732 | 732
2018-12-28 14:00 | 765 | 764
2018-12-28 14:30 | 793 | 793
2018-12-28 15:00 | 823 | 823
2018-12-28 15:30 | 852 | 852
2018-12-28 16:00 | 865 | 865
2018-12-28 16:30 | 897 | 897
2018-12-28 17:00 | 926 | 926
2018-12-28 17:30 | 937 | 937
2018-12-28 18:00 | 929 | 927
2018-12-28 18:30 | 915 | 911
2018-12-28 19:00 | 916 | 912
2018-12-28 19:30 | 918 | 914
2018-12-28 20:00 | 903 | 903
2018-12-28 20:30 | 878 | 877
2018-12-28 21:00 | 837 | 837
2018-12-28 21:30 | 808 | 808
2018-12-28 22:00 | 790 | 790
2018-12-28 22:30 | 776 | 775
2018-12-28 23:00 | 767 | 765
2018-12-28 23:30 | 725 | 720
2018-12-29 | 677 | 671
2018-12-29 00:30 | 636 | 626
2018-12-29 01:00 | 615 | 601
2018-12-29 01:30 | 600 | 584
2018-12-29 02:00 | 597 | 577
2018-12-29 02:30 | 591 | 569
2018-12-29 03:00 | 583 | 559
2018-12-29 03:30 | 582 | 557
2018-12-29 04:00 | 578 | 554
2018-12-29 04:30 | 580 | 555
2018-12-29 05:00 | 578 | 550
2018-12-29 05:30 | 574 | 545
2018-12-29 06:00 | 575 | 549
2018-12-29 06:30 | 584 | 564
2018-12-29 07:00 | 597 | 581
2018-12-29 07:30 | 616 | 608
2018-12-29 08:00 | 624 | 620
2018-12-29 08:30 | 644 | 643
2018-12-29 09:00 | 658 | 658
2018-12-29 09:30 | 667 | 667
2018-12-29 10:00 | 667 | 667
2018-12-29 10:30 | 662 | 662
2018-12-29 11:00 | 652 | 652
2018-12-29 11:30 | 619 | 619
2018-12-29 12:00 | 623 | 623
2018-12-29 12:30 | 631 | 631
2018-12-29 13:00 | 646 | 646
2018-12-29 13:30 | 667 | 667
2018-12-29 14:00 | 692 | 691
2018-12-29 14:30 | 724 | 723
2018-12-29 15:00 | 758 | 758
2018-12-29 15:30 | 798 | 798
2018-12-29 16:00 | 835 | 835
2018-12-29 16:30 | 880 | 879
2018-12-29 17:00 | 906 | 905
2018-12-29 17:30 | 919 | 917
2018-12-29 18:00 | 916 | 912
2018-12-29 18:30 | 924 | 919
2018-12-29 19:00 | 946 | 941
2018-12-29 19:30 | 955 | 953
2018-12-29 20:00 | 952 | 949
2018-12-29 20:30 | 926 | 920
2018-12-29 21:00 | 888 | 885
2018-12-29 21:30 | 857 | 856
2018-12-29 22:00 | 837 | 835
2018-12-29 22:30 | 815 | 812
2018-12-29 23:00 | 804 | 802
2018-12-29 23:30 | 760 | 756
2018-12-30 | 709 | 707
2018-12-30 00:30 | 668 | 663
2018-12-30 01:00 | 646 | 639
2018-12-30 01:30 | 633 | 625
2018-12-30 02:00 | 617 | 606
2018-12-30 02:30 | 608 | 596
2018-12-30 03:00 | 602 | 589
2018-12-30 03:30 | 600 | 586
2018-12-30 04:00 | 598 | 583
2018-12-30 04:30 | 600 | 584
2018-12-30 05:00 | 601 | 583
2018-12-30 05:30 | 595 | 574
2018-12-30 06:00 | 593 | 572
2018-12-30 06:30 | 592 | 577
2018-12-30 07:00 | 602 | 592
2018-12-30 07:30 | 619 | 613
2018-12-30 08:00 | 629 | 625
2018-12-30 08:30 | 643 | 642
2018-12-30 09:00 | 647 | 647
2018-12-30 09:30 | 647 | 647
2018-12-30 10:00 | 662 | 662
2018-12-30 10:30 | 670 | 670
2018-12-30 11:00 | 672 | 672
2018-12-30 11:30 | 671 | 671
2018-12-30 12:00 | 675 | 674
2018-12-30 12:30 | 673 | 672
2018-12-30 13:00 | 679 | 679
2018-12-30 13:30 | 700 | 700
2018-12-30 14:00 | 714 | 714
2018-12-30 14:30 | 742 | 742
2018-12-30 15:00 | 771 | 771
2018-12-30 15:30 | 815 | 815
2018-12-30 16:00 | 855 | 855
2018-12-30 16:30 | 898 | 898
2018-12-30 17:00 | 956 | 956
2018-12-30 17:30 | 999 | 998
2018-12-30 18:00 | 1015 | 1013
2018-12-30 18:30 | 1021 | 1018
2018-12-30 19:00 | 1021 | 1017
2018-12-30 19:30 | 1026 | 1023
2018-12-30 20:00 | 1014 | 1009
2018-12-30 20:30 | 989 | 986
2018-12-30 21:00 | 947 | 944
2018-12-30 21:30 | 892 | 891
2018-12-30 22:00 | 852 | 851
2018-12-30 22:30 | 841 | 840
2018-12-30 23:00 | 837 | 836
2018-12-30 23:30 | 771 | 768
2018-12-31 | 699 | 696
2018-12-31 00:30 | 650 | 644
2018-12-31 01:00 | 627 | 618
2018-12-31 01:30 | 614 | 604
2018-12-31 02:00 | 606 | 594
2018-12-31 02:30 | 606 | 593
2018-12-31 03:00 | 600 | 586
2018-12-31 03:30 | 601 | 586
2018-12-31 04:00 | 596 | 580
2018-12-31 04:30 | 600 | 584
2018-12-31 05:00 | 600 | 584
2018-12-31 05:30 | 605 | 590
2018-12-31 06:00 | 612 | 600
2018-12-31 06:30 | 640 | 634
2018-12-31 07:00 | 665 | 663
2018-12-31 07:30 | 694 | 694
2018-12-31 08:00 | 726 | 725
2018-12-31 08:30 | 753 | 752
2018-12-31 09:00 | 762 | 761
2018-12-31 09:30 | 767 | 766
2018-12-31 10:00 | 770 | 768
2018-12-31 10:30 | 778 | 777
2018-12-31 11:00 | 764 | 763
2018-12-31 11:30 | 768 | 765
2018-12-31 12:00 | 764 | 761
2018-12-31 12:30 | 763 | 760
2018-12-31 13:00 | 781 | 778
2018-12-31 13:30 | 798 | 796
2018-12-31 14:00 | 827 | 826
2018-12-31 14:30 | 854 | 853
2018-12-31 15:00 | 893 | 892
2018-12-31 15:30 | 931 | 931
2018-12-31 16:00 | 969 | 969
2018-12-31 16:30 | 1035 | 1035
2018-12-31 17:00 | 1089 | 1088
2018-12-31 17:30 | 1117 | 1117
2018-12-31 18:00 | 1102 | 1100
2018-12-31 18:30 | 1063 | 1058
2018-12-31 19:00 | 1047 | 1042
2018-12-31 19:30 | 1040 | 1034
2018-12-31 20:00 | 1011 | 1006
2018-12-31 20:30 | 967 | 962
2018-12-31 21:00 | 919 | 919
2018-12-31 21:30 | 883 | 882
2018-12-31 22:00 | 865 | 863
2018-12-31 22:30 | 855 | 852
2018-12-31 23:00 | 844 | 843
2018-12-31 23:30 | 802 | 801
2019-01-01 | 754 | 751
2019-01-01 00:30 | 708 | 704
2019-01-01 01:00 | 698 | 693
2019-01-01 01:30 | 686 | 680
2019-01-01 02:00 | 675 | 667
2019-01-01 02:30 | 657 | 646
2019-01-01 03:00 | 653 | 641
2019-01-01 03:30 | 641 | 627
2019-01-01 04:00 | 638 | 623
2019-01-01 04:30 | 634 | 617
2019-01-01 05:00 | 629 | 609
2019-01-01 05:30 | 628 | 605
2019-01-01 06:00 | 623 | 601
2019-01-01 06:30 | 629 | 611
2019-01-01 07:00 | 633 | 621
2019-01-01 07:30 | 649 | 644
2019-01-01 08:00 | 665 | 664
2019-01-01 08:30 | 676 | 676
2019-01-01 09:00 | 687 | 686
2019-01-01 09:30 | 693 | 692
2019-01-01 10:00 | 702 | 701
2019-01-01 10:30 | 710 | 710
2019-01-01 11:00 | 717 | 717
2019-01-01 11:30 | 714 | 714
2019-01-01 12:00 | 722 | 722
2019-01-01 12:30 | 732 | 732
2019-01-01 13:00 | 755 | 755
2019-01-01 13:30 | 771 | 770
2019-01-01 14:00 | 796 | 796
2019-01-01 14:30 | 813 | 813
2019-01-01 15:00 | 848 | 848
2019-01-01 15:30 | 877 | 876
2019-01-01 16:00 | 925 | 925
2019-01-01 16:30 | 953 | 953
2019-01-01 17:00 | 959 | 959
2019-01-01 17:30 | 986 | 985
2019-01-01 18:00 | 989 | 989
2019-01-01 18:30 | 970 | 968
2019-01-01 19:00 | 975 | 972
2019-01-01 19:30 | 979 | 978
2019-01-01 20:00 | 969 | 968
2019-01-01 20:30 | 951 | 950
2019-01-01 21:00 | 911 | 908
2019-01-01 21:30 | 872 | 871
2019-01-01 22:00 | 846 | 844
2019-01-01 22:30 | 829 | 826
2019-01-01 23:00 | 812 | 810
2019-01-01 23:30 | 765 | 762
2019-01-02 | 717 | 712
2019-01-02 00:30 | 681 | 672
2019-01-02 01:00 | 658 | 646
2019-01-02 01:30 | 646 | 632
2019-01-02 02:00 | 634 | 618
2019-01-02 02:30 | 630 | 612
2019-01-02 03:00 | 623 | 603
2019-01-02 03:30 | 626 | 605
2019-01-02 04:00 | 625 | 605
2019-01-02 04:30 | 629 | 608
2019-01-02 05:00 | 630 | 609
2019-01-02 05:30 | 643 | 624
2019-01-02 06:00 | 652 | 639
2019-01-02 06:30 | 679 | 674
2019-01-02 07:00 | 673 | 671
2019-01-02 07:30 | 715 | 715
2019-01-02 08:00 | 758 | 757
2019-01-02 08:30 | 798 | 798
2019-01-02 09:00 | 863 | 862
2019-01-02 09:30 | 871 | 871
2019-01-02 10:00 | 864 | 862
2019-01-02 10:30 | 874 | 873
2019-01-02 11:00 | 883 | 882
2019-01-02 11:30 | 880 | 879
2019-01-02 12:00 | 886 | 885
2019-01-02 12:30 | 893 | 892
2019-01-02 13:00 | 914 | 914
2019-01-02 13:30 | 922 | 922
2019-01-02 14:00 | 936 | 936
2019-01-02 14:30 | 961 | 961
2019-01-02 15:00 | 988 | 988
2019-01-02 15:30 | 1019 | 1019
2019-01-02 16:00 | 1049 | 1049
2019-01-02 16:30 | 1075 | 1075
2019-01-02 17:00 | 1098 | 1098
2019-01-02 17:30 | 1115 | 1115
2019-01-02 18:00 | 1104 | 1102
2019-01-02 18:30 | 1073 | 1070
2019-01-02 19:00 | 1075 | 1073
2019-01-02 19:30 | 1075 | 1073
2019-01-02 20:00 | 1056 | 1054
2019-01-02 20:30 | 1033 | 1030
2019-01-02 21:00 | 991 | 990
2019-01-02 21:30 | 947 | 946
2019-01-02 22:00 | 915 | 911
2019-01-02 22:30 | 881 | 872
2019-01-02 23:00 | 853 | 844
2019-01-02 23:30 | 793 | 787
2019-01-03 | 741 | 736
2019-01-03 00:30 | 699 | 690
2019-01-03 01:00 | 676 | 664
2019-01-03 01:30 | 659 | 646
2019-01-03 02:00 | 651 | 634
2019-01-03 02:30 | 644 | 627
2019-01-03 03:00 | 640 | 621
2019-01-03 03:30 | 639 | 619
2019-01-03 04:00 | 640 | 620
2019-01-03 04:30 | 643 | 623
2019-01-03 05:00 | 647 | 628
2019-01-03 05:30 | 661 | 643
2019-01-03 06:00 | 675 | 661
2019-01-03 06:30 | 701 | 694
2019-01-03 07:00 | 733 | 732
2019-01-03 07:30 | 807 | 807
2019-01-03 08:00 | 842 | 842
2019-01-03 08:30 | 863 | 862
2019-01-03 09:00 | 859 | 859
2019-01-03 09:30 | 893 | 893
2019-01-03 10:00 | 932 | 932
2019-01-03 10:30 | 950 | 950
2019-01-03 11:00 | 956 | 956
2019-01-03 11:30 | 951 | 951
2019-01-03 12:00 | 952 | 951
2019-01-03 12:30 | 921 | 919
2019-01-03 13:00 | 915 | 914
2019-01-03 13:30 | 939 | 939
2019-01-03 14:00 | 938 | 937
2019-01-03 14:30 | 949 | 949
2019-01-03 15:00 | 979 | 979
2019-01-03 15:30 | 993 | 993
2019-01-03 16:00 | 1003 | 1003
2019-01-03 16:30 | 1031 | 1031
2019-01-03 17:00 | 1058 | 1058
2019-01-03 17:30 | 1077 | 1077
2019-01-03 18:00 | 1077 | 1075
2019-01-03 18:30 | 1066 | 1062
2019-01-03 19:00 | 1073 | 1068
2019-01-03 19:30 | 1088 | 1085
2019-01-03 20:00 | 1092 | 1088
2019-01-03 20:30 | 1072 | 1067
2019-01-03 21:00 | 1034 | 1031
2019-01-03 21:30 | 989 | 985
2019-01-03 22:00 | 951 | 944
2019-01-03 22:30 | 909 | 902
2019-01-03 23:00 | 884 | 880
2019-01-03 23:30 | 838 | 831
2019-01-04 | 783 | 776
2019-01-04 00:30 | 731 | 724
2019-01-04 01:00 | 702 | 693
2019-01-04 01:30 | 690 | 680
2019-01-04 02:00 | 677 | 664
2019-01-04 02:30 | 669 | 655
2019-01-04 03:00 | 667 | 652
2019-01-04 03:30 | 665 | 649
2019-01-04 04:00 | 662 | 646
2019-01-04 04:30 | 667 | 652
2019-01-04 05:00 | 668 | 653
2019-01-04 05:30 | 684 | 670
2019-01-04 06:00 | 696 | 685
2019-01-04 06:30 | 735 | 732
2019-01-04 07:00 | 763 | 763
2019-01-04 07:30 | 830 | 830
2019-01-04 08:00 | 875 | 875
2019-01-04 08:30 | 897 | 897
2019-01-04 09:00 | 907 | 907
2019-01-04 09:30 | 908 | 908
2019-01-04 10:00 | 892 | 892
2019-01-04 10:30 | 877 | 877
2019-01-04 11:00 | 870 | 869
2019-01-04 11:30 | 868 | 868
2019-01-04 12:00 | 885 | 885
2019-01-04 12:30 | 898 | 898
2019-01-04 13:00 | 920 | 920
2019-01-04 13:30 | 922 | 922
2019-01-04 14:00 | 926 | 926
2019-01-04 14:30 | 979 | 978
2019-01-04 15:00 | 999 | 999
2019-01-04 15:30 | 974 | 973
2019-01-04 16:00 | 1000 | 1000
2019-01-04 16:30 | 1106 | 1106
2019-01-04 17:00 | 1123 | 1122
2019-01-04 17:30 | 1137 | 1136
2019-01-04 18:00 | 1117 | 1117
2019-01-04 18:30 | 1087 | 1086
2019-01-04 19:00 | 1086 | 1084
2019-01-04 19:30 | 1097 | 1096
2019-01-04 20:00 | 1093 | 1091
2019-01-04 20:30 | 1071 | 1069
2019-01-04 21:00 | 1028 | 1028
2019-01-04 21:30 | 993 | 993
2019-01-04 22:00 | 956 | 955
2019-01-04 22:30 | 924 | 921
2019-01-04 23:00 | 897 | 894
2019-01-04 23:30 | 845 | 839
2019-01-05 | 785 | 780
2019-01-05 00:30 | 734 | 728
2019-01-05 01:00 | 706 | 698
2019-01-05 01:30 | 688 | 678
2019-01-05 02:00 | 674 | 660
2019-01-05 02:30 | 662 | 647
2019-01-05 03:00 | 658 | 641
2019-01-05 03:30 | 650 | 633
2019-01-05 04:00 | 645 | 626
2019-01-05 04:30 | 641 | 621
2019-01-05 05:00 | 643 | 621
2019-01-05 05:30 | 647 | 624
2019-01-05 06:00 | 645 | 623
2019-01-05 06:30 | 661 | 646
2019-01-05 07:00 | 676 | 668
2019-01-05 07:30 | 695 | 693
2019-01-05 08:00 | 731 | 731
2019-01-05 08:30 | 767 | 767
2019-01-05 09:00 | 783 | 782
2019-01-05 09:30 | 801 | 801
2019-01-05 10:00 | 821 | 820
2019-01-05 10:30 | 824 | 823
2019-01-05 11:00 | 829 | 827
2019-01-05 11:30 | 824 | 823
2019-01-05 12:00 | 831 | 831
2019-01-05 12:30 | 832 | 831
2019-01-05 13:00 | 838 | 838
2019-01-05 13:30 | 865 | 865
2019-01-05 14:00 | 879 | 879
2019-01-05 14:30 | 906 | 905
2019-01-05 15:00 | 913 | 913
2019-01-05 15:30 | 955 | 955
2019-01-05 16:00 | 975 | 975
2019-01-05 16:30 | 1008 | 1008
2019-01-05 17:00 | 1036 | 1036
2019-01-05 17:30 | 1050 | 1049
2019-01-05 18:00 | 1034 | 1031
2019-01-05 18:30 | 1030 | 1025
2019-01-05 19:00 | 1031 | 1027
2019-01-05 19:30 | 1037 | 1033
2019-01-05 20:00 | 1035 | 1031
2019-01-05 20:30 | 1009 | 1004
2019-01-05 21:00 | 967 | 965
2019-01-05 21:30 | 938 | 937
2019-01-05 22:00 | 919 | 917
2019-01-05 22:30 | 902 | 898
2019-01-05 23:00 | 891 | 887
2019-01-05 23:30 | 838 | 836
2019-01-06 | 789 | 787
2019-01-06 00:30 | 741 | 735
2019-01-06 01:00 | 717 | 709
2019-01-06 01:30 | 694 | 685
2019-01-06 02:00 | 683 | 670
2019-01-06 02:30 | 676 | 662
2019-01-06 03:00 | 664 | 648
2019-01-06 03:30 | 662 | 644
2019-01-06 04:00 | 661 | 643
2019-01-06 04:30 | 659 | 640
2019-01-06 05:00 | 655 | 634
2019-01-06 05:30 | 658 | 634
2019-01-06 06:00 | 659 | 633
2019-01-06 06:30 | 670 | 649
2019-01-06 07:00 | 670 | 654
2019-01-06 07:30 | 695 | 686
2019-01-06 08:00 | 717 | 713
2019-01-06 08:30 | 732 | 731
2019-01-06 09:00 | 754 | 754
2019-01-06 09:30 | 762 | 762
2019-01-06 10:00 | 790 | 790
2019-01-06 10:30 | 816 | 816
2019-01-06 11:00 | 839 | 838
2019-01-06 11:30 | 845 | 845
2019-01-06 12:00 | 867 | 864
2019-01-06 12:30 | 870 | 863
2019-01-06 13:00 | 886 | 880
2019-01-06 13:30 | 902 | 897
2019-01-06 14:00 | 914 | 910
2019-01-06 14:30 | 925 | 922
2019-01-06 15:00 | 946 | 944
2019-01-06 15:30 | 966 | 964
2019-01-06 16:00 | 990 | 989
2019-01-06 16:30 | 990 | 989
2019-01-06 17:00 | 1015 | 1014
2019-01-06 17:30 | 1039 | 1038
2019-01-06 18:00 | 1036 | 1033
2019-01-06 18:30 | 1047 | 1044
2019-01-06 19:00 | 1054 | 1050
2019-01-06 19:30 | 1065 | 1063
2019-01-06 20:00 | 1067 | 1064
2019-01-06 20:30 | 1039 | 1036
2019-01-06 21:00 | 999 | 996
2019-01-06 21:30 | 966 | 963
2019-01-06 22:00 | 938 | 932
2019-01-06 22:30 | 916 | 910
2019-01-06 23:00 | 890 | 886
2019-01-06 23:30 | 838 | 833
2019-01-07 | 787 | 776
2019-01-07 00:30 | 745 | 729
2019-01-07 01:00 | 722 | 701
2019-01-07 01:30 | 713 | 689
2019-01-07 02:00 | 702 | 675
2019-01-07 02:30 | 679 | 662
2019-01-07 03:00 | 675 | 661
2019-01-07 03:30 | 673 | 659
2019-01-07 04:00 | 674 | 660
2019-01-07 04:30 | 678 | 665
2019-01-07 05:00 | 686 | 675
2019-01-07 05:30 | 707 | 697
2019-01-07 06:00 | 736 | 729
2019-01-07 06:30 | 790 | 788
2019-01-07 07:00 | 840 | 840
2019-01-07 07:30 | 913 | 913
2019-01-07 08:00 | 963 | 962
2019-01-07 08:30 | 988 | 987
2019-01-07 09:00 | 1006 | 1006
2019-01-07 09:30 | 1007 | 1007
2019-01-07 10:00 | 1019 | 1019
2019-01-07 10:30 | 1017 | 1016
2019-01-07 11:00 | 1000 | 999
2019-01-07 11:30 | 989 | 988
2019-01-07 12:00 | 997 | 997
2019-01-07 12:30 | 1010 | 1010
2019-01-07 13:00 | 1052 | 1052
2019-01-07 13:30 | 1088 | 1088
2019-01-07 14:00 | 1119 | 1119
2019-01-07 14:30 | 1120 | 1120
2019-01-07 15:00 | 1106 | 1105
2019-01-07 15:30 | 1105 | 1104
2019-01-07 16:00 | 1104 | 1102
2019-01-07 16:30 | 1115 | 1111
2019-01-07 17:00 | 1109 | 1105
2019-01-07 17:30 | 1097 | 1094
2019-01-07 18:00 | 1086 | 1083
2019-01-07 18:30 | 1067 | 1066
2019-01-07 19:00 | 1070 | 1069
2019-01-07 19:30 | 1067 | 1066
2019-01-07 20:00 | 1066 | 1065
2019-01-07 20:30 | 1049 | 1047
2019-01-07 21:00 | 1013 | 1011
2019-01-07 21:30 | 977 | 974
2019-01-07 22:00 | 936 | 932
2019-01-07 22:30 | 897 | 893
2019-01-07 23:00 | 879 | 873
2019-01-07 23:30 | 827 | 822
2019-01-08 | 778 | 771
2019-01-08 00:30 | 730 | 720
2019-01-08 01:00 | 700 | 689
2019-01-08 01:30 | 691 | 679
2019-01-08 02:00 | 679 | 665
2019-01-08 02:30 | 671 | 655
2019-01-08 03:00 | 667 | 650
2019-01-08 03:30 | 667 | 650
2019-01-08 04:00 | 663 | 646
2019-01-08 04:30 | 669 | 652
2019-01-08 05:00 | 676 | 661
2019-01-08 05:30 | 695 | 682
2019-01-08 06:00 | 724 | 714
2019-01-08 06:30 | 775 | 773
2019-01-08 07:00 | 828 | 828
2019-01-08 07:30 | 898 | 898
2019-01-08 08:00 | 951 | 951
2019-01-08 08:30 | 981 | 979
2019-01-08 09:00 | 971 | 970
2019-01-08 09:30 | 980 | 980
2019-01-08 10:00 | 972 | 972
2019-01-08 10:30 | 936 | 936
2019-01-08 11:00 | 921 | 920
2019-01-08 11:30 | 936 | 935
2019-01-08 12:00 | 959 | 959
2019-01-08 12:30 | 965 | 965
2019-01-08 13:00 | 984 | 984
2019-01-08 13:30 | 1011 | 1011
2019-01-08 14:00 | 1033 | 1033
2019-01-08 14:30 | 1030 | 1030
2019-01-08 15:00 | 1035 | 1035
2019-01-08 15:30 | 1039 | 1039
2019-01-08 16:00 | 1064 | 1064
2019-01-08 16:30 | 1086 | 1085
2019-01-08 17:00 | 1098 | 1098
2019-01-08 17:30 | 1114 | 1114
2019-01-08 18:00 | 1110 | 1108
2019-01-08 18:30 | 1092 | 1090
2019-01-08 19:00 | 1101 | 1099
2019-01-08 19:30 | 1106 | 1104
2019-01-08 20:00 | 1103 | 1101
2019-01-08 20:30 | 1076 | 1073
2019-01-08 21:00 | 1029 | 1026
2019-01-08 21:30 | 988 | 986
2019-01-08 22:00 | 949 | 944
2019-01-08 22:30 | 909 | 904
2019-01-08 23:00 | 885 | 878
2019-01-08 23:30 | 827 | 822
2019-01-09 | 774 | 769
2019-01-09 00:30 | 733 | 725
2019-01-09 01:00 | 714 | 703
2019-01-09 01:30 | 695 | 680
2019-01-09 02:00 | 686 | 669
2019-01-09 02:30 | 675 | 657
2019-01-09 03:00 | 672 | 653
2019-01-09 03:30 | 668 | 649
2019-01-09 04:00 | 670 | 651
2019-01-09 04:30 | 672 | 655
2019-01-09 05:00 | 678 | 662
2019-01-09 05:30 | 697 | 682
2019-01-09 06:00 | 713 | 702
2019-01-09 06:30 | 760 | 757
2019-01-09 07:00 | 802 | 801
2019-01-09 07:30 | 894 | 893
2019-01-09 08:00 | 980 | 979
2019-01-09 08:30 | 1022 | 1022
2019-01-09 09:00 | 1017 | 1017
2019-01-09 09:30 | 1019 | 1019
2019-01-09 10:00 | 1030 | 1030
2019-01-09 10:30 | 1041 | 1040
2019-01-09 11:00 | 1036 | 1036
2019-01-09 11:30 | 1041 | 1041
2019-01-09 12:00 | 1026 | 1026
2019-01-09 12:30 | 995 | 994
2019-01-09 13:00 | 1028 | 1025
2019-01-09 13:30 | 1057 | 1053
2019-01-09 14:00 | 1057 | 1054
2019-01-09 14:30 | 1058 | 1055
2019-01-09 15:00 | 1077 | 1075
2019-01-09 15:30 | 1094 | 1093
2019-01-09 16:00 | 1119 | 1118
2019-01-09 16:30 | 1131 | 1129
2019-01-09 17:00 | 1149 | 1147
2019-01-09 17:30 | 1152 | 1149
2019-01-09 18:00 | 1125 | 1120
2019-01-09 18:30 | 1106 | 1104
2019-01-09 19:00 | 1127 | 1125
2019-01-09 19:30 | 1122 | 1121
2019-01-09 20:00 | 1130 | 1128
2019-01-09 20:30 | 1099 | 1095
2019-01-09 21:00 | 1041 | 1036
2019-01-09 21:30 | 1018 | 1011
2019-01-09 22:00 | 979 | 970
2019-01-09 22:30 | 905 | 900
2019-01-09 23:00 | 901 | 897
2019-01-09 23:30 | 851 | 843
2019-01-10 | 799 | 788
2019-01-10 00:30 | 748 | 737
2019-01-10 01:00 | 727 | 713
2019-01-10 01:30 | 712 | 694
2019-01-10 02:00 | 696 | 679
2019-01-10 02:30 | 681 | 667
2019-01-10 03:00 | 682 | 668
2019-01-10 03:30 | 680 | 665
2019-01-10 04:00 | 680 | 665
2019-01-10 04:30 | 687 | 673
2019-01-10 05:00 | 696 | 684
2019-01-10 05:30 | 713 | 702
2019-01-10 06:00 | 740 | 732
2019-01-10 06:30 | 793 | 791
2019-01-10 07:00 | 838 | 837
2019-01-10 07:30 | 920 | 920
2019-01-10 08:00 | 956 | 956
2019-01-10 08:30 | 976 | 976
2019-01-10 09:00 | 998 | 998
2019-01-10 09:30 | 999 | 998
2019-01-10 10:00 | 1008 | 1007
2019-01-10 10:30 | 1023 | 1023
2019-01-10 11:00 | 1023 | 1023
2019-01-10 11:30 | 1020 | 1020
2019-01-10 12:00 | 1034 | 1034
2019-01-10 12:30 | 1020 | 1020
2019-01-10 13:00 | 1033 | 1032
2019-01-10 13:30 | 1038 | 1038
2019-01-10 14:00 | 1062 | 1062
2019-01-10 14:30 | 1058 | 1057
2019-01-10 15:00 | 1057 | 1057
2019-01-10 15:30 | 1074 | 1074
2019-01-10 16:00 | 1091 | 1091
2019-01-10 16:30 | 1134 | 1134
2019-01-10 17:00 | 1164 | 1164
2019-01-10 17:30 | 1175 | 1175
2019-01-10 18:00 | 1179 | 1178
2019-01-10 18:30 | 1174 | 1172
2019-01-10 19:00 | 1199 | 1197
2019-01-10 19:30 | 1237 | 1236
2019-01-10 20:00 | 1231 | 1230
2019-01-10 20:30 | 1202 | 1200
2019-01-10 21:00 | 1153 | 1151
2019-01-10 21:30 | 1090 | 1088
2019-01-10 22:00 | 1046 | 1039
2019-01-10 22:30 | 1001 | 994
2019-01-10 23:00 | 968 | 966
2019-01-10 23:30 | 902 | 898
2019-01-11 | 829 | 825
2019-01-11 00:30 | 739 | 732
2019-01-11 01:00 | 713 | 703
2019-01-11 01:30 | 696 | 684
2019-01-11 02:00 | 682 | 670
2019-01-11 02:30 | 676 | 662
2019-01-11 03:00 | 668 | 653
2019-01-11 03:30 | 663 | 647
2019-01-11 04:00 | 658 | 642
2019-01-11 04:30 | 660 | 644
2019-01-11 05:00 | 671 | 658
2019-01-11 05:30 | 691 | 678
2019-01-11 06:00 | 712 | 703
2019-01-11 06:30 | 759 | 758
2019-01-11 07:00 | 802 | 802
2019-01-11 07:30 | 872 | 872
2019-01-11 08:00 | 914 | 914
2019-01-11 08:30 | 949 | 949
2019-01-11 09:00 | 962 | 962
2019-01-11 09:30 | 976 | 975
2019-01-11 10:00 | 969 | 968
2019-01-11 10:30 | 962 | 961
2019-01-11 11:00 | 953 | 953
2019-01-11 11:30 | 953 | 953
2019-01-11 12:00 | 956 | 955
2019-01-11 12:30 | 956 | 955
2019-01-11 13:00 | 965 | 964
2019-01-11 13:30 | 976 | 976
2019-01-11 14:00 | 1004 | 1002
2019-01-11 14:30 | 1026 | 1024
2019-01-11 15:00 | 1043 | 1042
2019-01-11 15:30 | 1068 | 1067
2019-01-11 16:00 | 1089 | 1088
2019-01-11 16:30 | 1115 | 1113
2019-01-11 17:00 | 1134 | 1132
2019-01-11 17:30 | 1138 | 1134
2019-01-11 18:00 | 1117 | 1112
2019-01-11 18:30 | 1086 | 1080
2019-01-11 19:00 | 1080 | 1074
2019-01-11 19:30 | 1086 | 1080
2019-01-11 20:00 | 1082 | 1077
2019-01-11 20:30 | 1052 | 1050
2019-01-11 21:00 | 1016 | 1015
2019-01-11 21:30 | 975 | 972
2019-01-11 22:00 | 944 | 941
2019-01-11 22:30 | 915 | 913
2019-01-11 23:00 | 872 | 868
2019-01-11 23:30 | 813 | 807
2019-01-12 | 753 | 748
2019-01-12 00:30 | 709 | 701
2019-01-12 01:00 | 686 | 674
2019-01-12 01:30 | 668 | 655
2019-01-12 02:00 | 648 | 632
2019-01-12 02:30 | 633 | 614
2019-01-12 03:00 | 614 | 592
2019-01-12 03:30 | 608 | 585
2019-01-12 04:00 | 603 | 580
2019-01-12 04:30 | 605 | 582
2019-01-12 05:00 | 599 | 576
2019-01-12 05:30 | 610 | 583
2019-01-12 06:00 | 614 | 588
2019-01-12 06:30 | 623 | 604
2019-01-12 07:00 | 632 | 621
2019-01-12 07:30 | 657 | 652
2019-01-12 08:00 | 676 | 675
2019-01-12 08:30 | 706 | 705
2019-01-12 09:00 | 731 | 731
2019-01-12 09:30 | 737 | 736
2019-01-12 10:00 | 740 | 740
2019-01-12 10:30 | 731 | 730
2019-01-12 11:00 | 723 | 723
2019-01-12 11:30 | 722 | 722
2019-01-12 12:00 | 733 | 731
2019-01-12 12:30 | 733 | 732
2019-01-12 13:00 | 746 | 745
2019-01-12 13:30 | 762 | 762
2019-01-12 14:00 | 788 | 788
2019-01-12 14:30 | 810 | 810
2019-01-12 15:00 | 847 | 847
2019-01-12 15:30 | 877 | 876
2019-01-12 16:00 | 905 | 905
2019-01-12 16:30 | 930 | 930
2019-01-12 17:00 | 969 | 969
2019-01-12 17:30 | 981 | 980
2019-01-12 18:00 | 988 | 986
2019-01-12 18:30 | 972 | 971
2019-01-12 19:00 | 983 | 982
2019-01-12 19:30 | 992 | 992
2019-01-12 20:00 | 990 | 989
2019-01-12 20:30 | 964 | 964
2019-01-12 21:00 | 931 | 930
2019-01-12 21:30 | 892 | 892
2019-01-12 22:00 | 869 | 867
2019-01-12 22:30 | 856 | 851
2019-01-12 23:00 | 843 | 839
2019-01-12 23:30 | 792 | 788
2019-01-13 | 747 | 739
2019-01-13 00:30 | 700 | 691
2019-01-13 01:00 | 680 | 669
2019-01-13 01:30 | 664 | 652
2019-01-13 02:00 | 649 | 635
2019-01-13 02:30 | 641 | 624
2019-01-13 03:00 | 636 | 617
2019-01-13 03:30 | 632 | 612
2019-01-13 04:00 | 630 | 609
2019-01-13 04:30 | 632 | 610
2019-01-13 05:00 | 627 | 602
2019-01-13 05:30 | 626 | 598
2019-01-13 06:00 | 627 | 600
2019-01-13 06:30 | 635 | 613
2019-01-13 07:00 | 643 | 627
2019-01-13 07:30 | 662 | 652
2019-01-13 08:00 | 674 | 669
2019-01-13 08:30 | 700 | 698
2019-01-13 09:00 | 717 | 717
2019-01-13 09:30 | 734 | 734
2019-01-13 10:00 | 751 | 751
2019-01-13 10:30 | 764 | 764
2019-01-13 11:00 | 766 | 765
2019-01-13 11:30 | 772 | 771
2019-01-13 12:00 | 784 | 783
2019-01-13 12:30 | 787 | 786
2019-01-13 13:00 | 800 | 798
2019-01-13 13:30 | 812 | 809
2019-01-13 14:00 | 825 | 825
2019-01-13 14:30 | 848 | 848
2019-01-13 15:00 | 869 | 869
2019-01-13 15:30 | 899 | 899
2019-01-13 16:00 | 929 | 929
2019-01-13 16:30 | 957 | 957
2019-01-13 17:00 | 988 | 988
2019-01-13 17:30 | 1012 | 1012
2019-01-13 18:00 | 1015 | 1015
2019-01-13 18:30 | 1017 | 1017
2019-01-13 19:00 | 1017 | 1016
2019-01-13 19:30 | 1019 | 1019
2019-01-13 20:00 | 1016 | 1015
2019-01-13 20:30 | 986 | 985
2019-01-13 21:00 | 944 | 942
2019-01-13 21:30 | 908 | 904
2019-01-13 22:00 | 880 | 876
2019-01-13 22:30 | 859 | 855
2019-01-13 23:00 | 840 | 837
2019-01-13 23:30 | 793 | 788
2019-01-14 | 739 | 733
2019-01-14 00:30 | 703 | 693
2019-01-14 01:00 | 684 | 672
2019-01-14 01:30 | 669 | 655
2019-01-14 02:00 | 654 | 637
2019-01-14 02:30 | 651 | 634
2019-01-14 03:00 | 646 | 629
2019-01-14 03:30 | 645 | 628
2019-01-14 04:00 | 641 | 625
2019-01-14 04:30 | 654 | 639
2019-01-14 05:00 | 663 | 648
2019-01-14 05:30 | 682 | 669
2019-01-14 06:00 | 707 | 699
2019-01-14 06:30 | 762 | 761
2019-01-14 07:00 | 804 | 803
2019-01-14 07:30 | 870 | 870
2019-01-14 08:00 | 905 | 904
2019-01-14 08:30 | 921 | 921
2019-01-14 09:00 | 957 | 956
2019-01-14 09:30 | 962 | 962
2019-01-14 10:00 | 960 | 960
2019-01-14 10:30 | 965 | 965
2019-01-14 11:00 | 956 | 955
2019-01-14 11:30 | 955 | 955
2019-01-14 12:00 | 959 | 959
2019-01-14 12:30 | 969 | 969
2019-01-14 13:00 | 996 | 996
2019-01-14 13:30 | 1015 | 1015
2019-01-14 14:00 | 1042 | 1042
2019-01-14 14:30 | 1073 | 1073
2019-01-14 15:00 | 1109 | 1108
2019-01-14 15:30 | 1155 | 1155
2019-01-14 16:00 | 1188 | 1187
2019-01-14 16:30 | 1214 | 1214
2019-01-14 17:00 | 1227 | 1227
2019-01-14 17:30 | 1225 | 1223
2019-01-14 18:00 | 1208 | 1203
2019-01-14 18:30 | 1188 | 1181
2019-01-14 19:00 | 1187 | 1185
2019-01-14 19:30 | 1203 | 1203
2019-01-14 20:00 | 1191 | 1190
2019-01-14 20:30 | 1160 | 1158
2019-01-14 21:00 | 1106 | 1103
2019-01-14 21:30 | 1043 | 1042
2019-01-14 22:00 | 990 | 990
2019-01-14 22:30 | 963 | 962
2019-01-14 23:00 | 917 | 917
2019-01-14 23:30 | 847 | 843
2019-01-15 | 776 | 773
2019-01-15 00:30 | 721 | 717
2019-01-15 01:00 | 694 | 688
2019-01-15 01:30 | 675 | 667
2019-01-15 02:00 | 669 | 658
2019-01-15 02:30 | 661 | 649
2019-01-15 03:00 | 657 | 643
2019-01-15 03:30 | 652 | 637
2019-01-15 04:00 | 652 | 637
2019-01-15 04:30 | 660 | 647
2019-01-15 05:00 | 664 | 652
2019-01-15 05:30 | 690 | 679
2019-01-15 06:00 | 707 | 700
2019-01-15 06:30 | 761 | 758
2019-01-15 07:00 | 801 | 801
2019-01-15 07:30 | 873 | 873
2019-01-15 08:00 | 924 | 923
2019-01-15 08:30 | 954 | 953
2019-01-15 09:00 | 983 | 982
2019-01-15 09:30 | 997 | 995
2019-01-15 10:00 | 1004 | 1003
2019-01-15 10:30 | 1000 | 999
2019-01-15 11:00 | 998 | 996
2019-01-15 11:30 | 999 | 997
2019-01-15 12:00 | 1021 | 1018
2019-01-15 12:30 | 1031 | 1028
2019-01-15 13:00 | 1051 | 1050
2019-01-15 13:30 | 1063 | 1062
2019-01-15 14:00 | 1095 | 1093
2019-01-15 14:30 | 1132 | 1131
2019-01-15 15:00 | 1153 | 1152
2019-01-15 15:30 | 1172 | 1171
2019-01-15 16:00 | 1240 | 1240
2019-01-15 16:30 | 1318 | 1318
2019-01-15 17:00 | 1349 | 1349
2019-01-15 17:30 | 1357 | 1357
2019-01-15 18:00 | 1325 | 1324
2019-01-15 18:30 | 1275 | 1274
2019-01-15 19:00 | 1242 | 1238
2019-01-15 19:30 | 1237 | 1234
2019-01-15 20:00 | 1249 | 1246
2019-01-15 20:30 | 1202 | 1199
2019-01-15 21:00 | 1093 | 1093
2019-01-15 21:30 | 1035 | 1033
2019-01-15 22:00 | 996 | 991
2019-01-15 22:30 | 958 | 956
2019-01-15 23:00 | 907 | 905
2019-01-15 23:30 | 835 | 831
2019-01-16 | 771 | 770
2019-01-16 00:30 | 726 | 724
2019-01-16 01:00 | 694 | 690
2019-01-16 01:30 | 674 | 669
2019-01-16 02:00 | 663 | 657
2019-01-16 02:30 | 662 | 654
2019-01-16 03:00 | 661 | 652
2019-01-16 03:30 | 663 | 654
2019-01-16 04:00 | 661 | 652
2019-01-16 04:30 | 664 | 656
2019-01-16 05:00 | 670 | 663
2019-01-16 05:30 | 693 | 687
2019-01-16 06:00 | 720 | 716
2019-01-16 06:30 | 777 | 776
2019-01-16 07:00 | 821 | 821
2019-01-16 07:30 | 894 | 894
2019-01-16 08:00 | 932 | 932
2019-01-16 08:30 | 967 | 966
2019-01-16 09:00 | 1011 | 1011
2019-01-16 09:30 | 995 | 995
2019-01-16 10:00 | 985 | 984
2019-01-16 10:30 | 997 | 996
2019-01-16 11:00 | 1026 | 1024
2019-01-16 11:30 | 1018 | 1016
2019-01-16 12:00 | 1038 | 1038
2019-01-16 12:30 | 1061 | 1061
2019-01-16 13:00 | 1088 | 1088
2019-01-16 13:30 | 1132 | 1131
2019-01-16 14:00 | 1181 | 1181
2019-01-16 14:30 | 1190 | 1190
2019-01-16 15:00 | 1236 | 1236
2019-01-16 15:30 | 1253 | 1253
2019-01-16 16:00 | 1267 | 1267
2019-01-16 16:30 | 1317 | 1317
2019-01-16 17:00 | 1383 | 1383
2019-01-16 17:30 | 1339 | 1339
2019-01-16 18:00 | 1311 | 1308
2019-01-16 18:30 | 1266 | 1262
2019-01-16 19:00 | 1260 | 1257
2019-01-16 19:30 | 1259 | 1257
2019-01-16 20:00 | 1250 | 1248
2019-01-16 20:30 | 1258 | 1256
2019-01-16 21:00 | 1171 | 1169
2019-01-16 21:30 | 1101 | 1097
2019-01-16 22:00 | 1048 | 1041
2019-01-16 22:30 | 1008 | 1000
2019-01-16 23:00 | 953 | 949
2019-01-16 23:30 | 863 | 861
2019-01-17 | 804 | 800
2019-01-17 00:30 | 751 | 747
2019-01-17 01:00 | 724 | 721
2019-01-17 01:30 | 708 | 704
2019-01-17 02:00 | 690 | 685
2019-01-17 02:30 | 687 | 680
2019-01-17 03:00 | 676 | 669
2019-01-17 03:30 | 674 | 666
2019-01-17 04:00 | 674 | 666
2019-01-17 04:30 | 675 | 668
2019-01-17 05:00 | 689 | 683
2019-01-17 05:30 | 703 | 698
2019-01-17 06:00 | 735 | 733
2019-01-17 06:30 | 790 | 790
2019-01-17 07:00 | 845 | 839
2019-01-17 07:30 | 918 | 916
2019-01-17 08:00 | 965 | 961
2019-01-17 08:30 | 982 | 978
2019-01-17 09:00 | 997 | 994
2019-01-17 09:30 | 1002 | 998
2019-01-17 10:00 | 984 | 980
2019-01-17 10:30 | 989 | 987
2019-01-17 11:00 | 996 | 994
2019-01-17 11:30 | 996 | 994
2019-01-17 12:00 | 1009 | 1008
2019-01-17 12:30 | 1056 | 1056
2019-01-17 13:00 | 1046 | 1046
2019-01-17 13:30 | 1088 | 1088
2019-01-17 14:00 | 1134 | 1134
2019-01-17 14:30 | 1149 | 1149
2019-01-17 15:00 | 1192 | 1192
2019-01-17 15:30 | 1188 | 1186
2019-01-17 16:00 | 1251 | 1250
2019-01-17 16:30 | 1293 | 1293
2019-01-17 17:00 | 1318 | 1318
2019-01-17 17:30 | 1337 | 1336
2019-01-17 18:00 | 1276 | 1270
2019-01-17 18:30 | 1251 | 1246
2019-01-17 19:00 | 1232 | 1227
2019-01-17 19:30 | 1220 | 1215
2019-01-17 20:00 | 1213 | 1209
2019-01-17 20:30 | 1176 | 1174
2019-01-17 21:00 | 1124 | 1123
2019-01-17 21:30 | 1061 | 1057
2019-01-17 22:00 | 1016 | 1010
2019-01-17 22:30 | 977 | 976
2019-01-17 23:00 | 926 | 925
2019-01-17 23:30 | 844 | 841
2019-01-18 | 776 | 775
2019-01-18 00:30 | 731 | 729
2019-01-18 01:00 | 702 | 698
2019-01-18 01:30 | 689 | 683
2019-01-18 02:00 | 670 | 663
2019-01-18 02:30 | 667 | 659
2019-01-18 03:00 | 665 | 656
2019-01-18 03:30 | 657 | 649
2019-01-18 04:00 | 659 | 650
2019-01-18 04:30 | 662 | 653
2019-01-18 05:00 | 671 | 664
2019-01-18 05:30 | 691 | 685
2019-01-18 06:00 | 723 | 720
2019-01-18 06:30 | 780 | 778
2019-01-18 07:00 | 812 | 811
2019-01-18 07:30 | 884 | 883
2019-01-18 08:00 | 929 | 928
2019-01-18 08:30 | 968 | 967
2019-01-18 09:00 | 991 | 989
2019-01-18 09:30 | 1001 | 997
2019-01-18 10:00 | 999 | 999
2019-01-18 10:30 | 999 | 999
2019-01-18 11:00 | 1006 | 1006
2019-01-18 11:30 | 993 | 993
2019-01-18 12:00 | 1000 | 999
2019-01-18 12:30 | 999 | 999
2019-01-18 13:00 | 1017 | 1016
2019-01-18 13:30 | 1037 | 1036
2019-01-18 14:00 | 1063 | 1062
2019-01-18 14:30 | 1096 | 1096
2019-01-18 15:00 | 1118 | 1117
2019-01-18 15:30 | 1158 | 1158
2019-01-18 16:00 | 1186 | 1186
2019-01-18 16:30 | 1229 | 1229
2019-01-18 17:00 | 1267 | 1267
2019-01-18 17:30 | 1268 | 1268
2019-01-18 18:00 | 1245 | 1245
2019-01-18 18:30 | 1207 | 1204
2019-01-18 19:00 | 1191 | 1187
2019-01-18 19:30 | 1185 | 1183
2019-01-18 20:00 | 1174 | 1171
2019-01-18 20:30 | 1147 | 1145
2019-01-18 21:00 | 1097 | 1096
2019-01-18 21:30 | 1051 | 1051
2019-01-18 22:00 | 1011 | 1011
2019-01-18 22:30 | 983 | 983
2019-01-18 23:00 | 936 | 936
2019-01-18 23:30 | 860 | 860
2019-01-19 | 795 | 794
2019-01-19 00:30 | 744 | 742
2019-01-19 01:00 | 717 | 713
2019-01-19 01:30 | 699 | 693
2019-01-19 02:00 | 685 | 677
2019-01-19 02:30 | 680 | 671
2019-01-19 03:00 | 668 | 657
2019-01-19 03:30 | 664 | 651
2019-01-19 04:00 | 659 | 646
2019-01-19 04:30 | 658 | 645
2019-01-19 05:00 | 661 | 648
2019-01-19 05:30 | 660 | 644
2019-01-19 06:00 | 659 | 644
2019-01-19 06:30 | 675 | 666
2019-01-19 07:00 | 684 | 679
2019-01-19 07:30 | 710 | 709
2019-01-19 08:00 | 743 | 742
2019-01-19 08:30 | 782 | 781
2019-01-19 09:00 | 801 | 801
2019-01-19 09:30 | 811 | 811
2019-01-19 10:00 | 815 | 815
2019-01-19 10:30 | 839 | 839
2019-01-19 11:00 | 848 | 848
2019-01-19 11:30 | 873 | 873
2019-01-19 12:00 | 897 | 897
2019-01-19 12:30 | 898 | 898
2019-01-19 13:00 | 909 | 909
2019-01-19 13:30 | 915 | 915
2019-01-19 14:00 | 931 | 931
2019-01-19 14:30 | 957 | 957
2019-01-19 15:00 | 1002 | 1000
2019-01-19 15:30 | 1032 | 1031
2019-01-19 16:00 | 1069 | 1069
2019-01-19 16:30 | 1100 | 1100
2019-01-19 17:00 | 1126 | 1126
2019-01-19 17:30 | 1133 | 1133
2019-01-19 18:00 | 1120 | 1119
2019-01-19 18:30 | 1119 | 1116
2019-01-19 19:00 | 1111 | 1107
2019-01-19 19:30 | 1103 | 1099
2019-01-19 20:00 | 1097 | 1090
2019-01-19 20:30 | 1072 | 1065
2019-01-19 21:00 | 1025 | 1021
2019-01-19 21:30 | 989 | 984
2019-01-19 22:00 | 957 | 951
2019-01-19 22:30 | 925 | 922
2019-01-19 23:00 | 909 | 904
2019-01-19 23:30 | 856 | 848
2019-01-20 | 783 | 781
2019-01-20 00:30 | 737 | 733
2019-01-20 01:00 | 718 | 713
2019-01-20 01:30 | 695 | 688
2019-01-20 02:00 | 682 | 672
2019-01-20 02:30 | 670 | 657
2019-01-20 03:00 | 666 | 652
2019-01-20 03:30 | 655 | 641
2019-01-20 04:00 | 654 | 640
2019-01-20 04:30 | 653 | 639
2019-01-20 05:00 | 657 | 643
2019-01-20 05:30 | 656 | 639
2019-01-20 06:00 | 658 | 641
2019-01-20 06:30 | 671 | 657
2019-01-20 07:00 | 676 | 667
2019-01-20 07:30 | 701 | 697
2019-01-20 08:00 | 720 | 718
2019-01-20 08:30 | 740 | 739
2019-01-20 09:00 | 767 | 767
2019-01-20 09:30 | 789 | 789
2019-01-20 10:00 | 799 | 798
2019-01-20 10:30 | 805 | 805
2019-01-20 11:00 | 811 | 811
2019-01-20 11:30 | 820 | 820
2019-01-20 12:00 | 835 | 835
2019-01-20 12:30 | 859 | 859
2019-01-20 13:00 | 899 | 899
2019-01-20 13:30 | 931 | 931
2019-01-20 14:00 | 960 | 959
2019-01-20 14:30 | 959 | 959
2019-01-20 15:00 | 993 | 993
2019-01-20 15:30 | 1013 | 1013
2019-01-20 16:00 | 1037 | 1037
2019-01-20 16:30 | 1080 | 1080
2019-01-20 17:00 | 1126 | 1126
2019-01-20 17:30 | 1131 | 1128
2019-01-20 18:00 | 1142 | 1139
2019-01-20 18:30 | 1145 | 1141
2019-01-20 19:00 | 1147 | 1142
2019-01-20 19:30 | 1138 | 1138
2019-01-20 20:00 | 1133 | 1132
2019-01-20 20:30 | 1120 | 1118
2019-01-20 21:00 | 1042 | 1038
2019-01-20 21:30 | 1002 | 999
2019-01-20 22:00 | 958 | 956
2019-01-20 22:30 | 929 | 926
2019-01-20 23:00 | 897 | 897
2019-01-20 23:30 | 837 | 837
2019-01-21 | 776 | 774
2019-01-21 00:30 | 734 | 731
2019-01-21 01:00 | 717 | 713
2019-01-21 01:30 | 703 | 698
2019-01-21 02:00 | 694 | 688
2019-01-21 02:30 | 684 | 677
2019-01-21 03:00 | 683 | 676
2019-01-21 03:30 | 681 | 673
2019-01-21 04:00 | 680 | 671
2019-01-21 04:30 | 687 | 680
2019-01-21 05:00 | 697 | 692
2019-01-21 05:30 | 722 | 718
2019-01-21 06:00 | 750 | 749
2019-01-21 06:30 | 813 | 812
2019-01-21 07:00 | 871 | 870
2019-01-21 07:30 | 951 | 951
2019-01-21 08:00 | 1006 | 1005
2019-01-21 08:30 | 1036 | 1036
2019-01-21 09:00 | 1044 | 1043
2019-01-21 09:30 | 1055 | 1054
2019-01-21 10:00 | 1046 | 1046
2019-01-21 10:30 | 1043 | 1043
2019-01-21 11:00 | 1048 | 1048
2019-01-21 11:30 | 1051 | 1051
2019-01-21 12:00 | 1076 | 1076
2019-01-21 12:30 | 1088 | 1088
2019-01-21 13:00 | 1113 | 1112
2019-01-21 13:30 | 1136 | 1136
2019-01-21 14:00 | 1167 | 1167
2019-01-21 14:30 | 1192 | 1192
2019-01-21 15:00 | 1212 | 1211
2019-01-21 15:30 | 1239 | 1239
2019-01-21 16:00 | 1264 | 1264
2019-01-21 16:30 | 1286 | 1286
2019-01-21 17:00 | 1315 | 1315
2019-01-21 17:30 | 1306 | 1305
2019-01-21 18:00 | 1282 | 1280
2019-01-21 18:30 | 1250 | 1245
2019-01-21 19:00 | 1250 | 1247
2019-01-21 19:30 | 1253 | 1250
2019-01-21 20:00 | 1237 | 1234
2019-01-21 20:30 | 1203 | 1198
2019-01-21 21:00 | 1134 | 1132
2019-01-21 21:30 | 1076 | 1072
2019-01-21 22:00 | 1034 | 1029
2019-01-21 22:30 | 994 | 985
2019-01-21 23:00 | 935 | 931
2019-01-21 23:30 | 853 | 848
2019-01-22 | 787 | 786
2019-01-22 00:30 | 739 | 737
2019-01-22 01:00 | 710 | 706
2019-01-22 01:30 | 699 | 692
2019-01-22 02:00 | 684 | 676
2019-01-22 02:30 | 675 | 666
2019-01-22 03:00 | 669 | 660
2019-01-22 03:30 | 669 | 659
2019-01-22 04:00 | 666 | 657
2019-01-22 04:30 | 672 | 664
2019-01-22 05:00 | 682 | 676
2019-01-22 05:30 | 705 | 699
2019-01-22 06:00 | 728 | 725
2019-01-22 06:30 | 780 | 778
2019-01-22 07:00 | 837 | 837
2019-01-22 07:30 | 918 | 918
2019-01-22 08:00 | 981 | 981
2019-01-22 08:30 | 1010 | 1010
2019-01-22 09:00 | 1033 | 1033
2019-01-22 09:30 | 1049 | 1048
2019-01-22 10:00 | 1058 | 1058
2019-01-22 10:30 | 1072 | 1072
2019-01-22 11:00 | 1089 | 1088
2019-01-22 11:30 | 1093 | 1092
2019-01-22 12:00 | 1101 | 1101
2019-01-22 12:30 | 1114 | 1114
2019-01-22 13:00 | 1128 | 1128
2019-01-22 13:30 | 1146 | 1145
2019-01-22 14:00 | 1171 | 1169
2019-01-22 14:30 | 1214 | 1212
2019-01-22 15:00 | 1248 | 1247
2019-01-22 15:30 | 1258 | 1256
2019-01-22 16:00 | 1322 | 1318
2019-01-22 16:30 | 1373 | 1371
2019-01-22 17:00 | 1369 | 1368
2019-01-22 17:30 | 1354 | 1354
2019-01-22 18:00 | 1341 | 1340
2019-01-22 18:30 | 1306 | 1304
2019-01-22 19:00 | 1322 | 1321
2019-01-22 19:30 | 1316 | 1316
2019-01-22 20:00 | 1280 | 1278
2019-01-22 20:30 | 1242 | 1236
2019-01-22 21:00 | 1180 | 1177
2019-01-22 21:30 | 1122 | 1116
2019-01-22 22:00 | 1076 | 1064
2019-01-22 22:30 | 1027 | 1020
2019-01-22 23:00 | 967 | 961
2019-01-22 23:30 | 893 | 887
2019-01-23 | 826 | 823
2019-01-23 00:30 | 774 | 767
2019-01-23 01:00 | 744 | 736
2019-01-23 01:30 | 724 | 717
2019-01-23 02:00 | 711 | 704
2019-01-23 02:30 | 705 | 697
2019-01-23 03:00 | 700 | 691
2019-01-23 03:30 | 695 | 685
2019-01-23 04:00 | 692 | 682
2019-01-23 04:30 | 694 | 689
2019-01-23 05:00 | 706 | 703
2019-01-23 05:30 | 726 | 723
2019-01-23 06:00 | 753 | 752
2019-01-23 06:30 | 810 | 810
2019-01-23 07:00 | 856 | 855
2019-01-23 07:30 | 944 | 943
2019-01-23 08:00 | 999 | 999
2019-01-23 08:30 | 1032 | 1032
2019-01-23 09:00 | 1059 | 1058
2019-01-23 09:30 | 1063 | 1060
2019-01-23 10:00 | 1074 | 1072
2019-01-23 10:30 | 1082 | 1082
2019-01-23 11:00 | 1111 | 1111
2019-01-23 11:30 | 1117 | 1117
2019-01-23 12:00 | 1151 | 1151
2019-01-23 12:30 | 1164 | 1164
2019-01-23 13:00 | 1177 | 1177
2019-01-23 13:30 | 1190 | 1190
2019-01-23 14:00 | 1222 | 1221
2019-01-23 14:30 | 1248 | 1247
2019-01-23 15:00 | 1276 | 1275
2019-01-23 15:30 | 1315 | 1313
2019-01-23 16:00 | 1404 | 1401
2019-01-23 16:30 | 1441 | 1438
2019-01-23 17:00 | 1439 | 1438
2019-01-23 17:30 | 1409 | 1408
2019-01-23 18:00 | 1372 | 1368
2019-01-23 18:30 | 1320 | 1317
2019-01-23 19:00 | 1304 | 1302
2019-01-23 19:30 | 1273 | 1271
2019-01-23 20:00 | 1251 | 1249
2019-01-23 20:30 | 1222 | 1216
2019-01-23 21:00 | 1160 | 1157
2019-01-23 21:30 | 1107 | 1103
2019-01-23 22:00 | 1060 | 1056
2019-01-23 22:30 | 1022 | 1015
2019-01-23 23:00 | 976 | 966
2019-01-23 23:30 | 901 | 892
2019-01-24 | 829 | 828
2019-01-24 00:30 | 775 | 774
2019-01-24 01:00 | 751 | 748
2019-01-24 01:30 | 729 | 725
2019-01-24 02:00 | 716 | 712
2019-01-24 02:30 | 707 | 702
2019-01-24 03:00 | 700 | 695
2019-01-24 03:30 | 696 | 690
2019-01-24 04:00 | 694 | 688
2019-01-24 04:30 | 696 | 691
2019-01-24 05:00 | 707 | 703
2019-01-24 05:30 | 730 | 727
2019-01-24 06:00 | 754 | 753
2019-01-24 06:30 | 820 | 820
2019-01-24 07:00 | 877 | 877
2019-01-24 07:30 | 957 | 957
2019-01-24 08:00 | 995 | 995
2019-01-24 08:30 | 1038 | 1038
2019-01-24 09:00 | 1063 | 1063
2019-01-24 09:30 | 1095 | 1095
2019-01-24 10:00 | 1102 | 1102
2019-01-24 10:30 | 1097 | 1097
2019-01-24 11:00 | 1095 | 1095
2019-01-24 11:30 | 1132 | 1132
2019-01-24 12:00 | 1150 | 1149
2019-01-24 12:30 | 1148 | 1148
2019-01-24 13:00 | 1129 | 1129
2019-01-24 13:30 | 1139 | 1139
2019-01-24 14:00 | 1146 | 1146
2019-01-24 14:30 | 1227 | 1226
2019-01-24 15:00 | 1253 | 1252
2019-01-24 15:30 | 1276 | 1275
2019-01-24 16:00 | 1317 | 1315
2019-01-24 16:30 | 1345 | 1344
2019-01-24 17:00 | 1368 | 1368
2019-01-24 17:30 | 1381 | 1381
2019-01-24 18:00 | 1351 | 1350
2019-01-24 18:30 | 1316 | 1312
2019-01-24 19:00 | 1318 | 1314
2019-01-24 19:30 | 1326 | 1323
2019-01-24 20:00 | 1314 | 1311
2019-01-24 20:30 | 1266 | 1260
2019-01-24 21:00 | 1205 | 1199
2019-01-24 21:30 | 1148 | 1139
2019-01-24 22:00 | 1112 | 1096
2019-01-24 22:30 | 1053 | 1047
2019-01-24 23:00 | 991 | 989
2019-01-24 23:30 | 912 | 910
2019-01-25 | 852 | 850
2019-01-25 00:30 | 807 | 803
2019-01-25 01:00 | 783 | 780
2019-01-25 01:30 | 759 | 755
2019-01-25 02:00 | 748 | 742
2019-01-25 02:30 | 740 | 734
2019-01-25 03:00 | 730 | 723
2019-01-25 03:30 | 724 | 717
2019-01-25 04:00 | 722 | 715
2019-01-25 04:30 | 726 | 719
2019-01-25 05:00 | 738 | 732
2019-01-25 05:30 | 765 | 760
2019-01-25 06:00 | 795 | 790
2019-01-25 06:30 | 855 | 854
2019-01-25 07:00 | 907 | 907
2019-01-25 07:30 | 993 | 993
2019-01-25 08:00 | 1054 | 1052
2019-01-25 08:30 | 1094 | 1093
2019-01-25 09:00 | 1130 | 1128
2019-01-25 09:30 | 1136 | 1135
2019-01-25 10:00 | 1138 | 1138
2019-01-25 10:30 | 1153 | 1153
2019-01-25 11:00 | 1138 | 1138
2019-01-25 11:30 | 1101 | 1098
2019-01-25 12:00 | 1111 | 1110
2019-01-25 12:30 | 1163 | 1163
2019-01-25 13:00 | 1162 | 1162
2019-01-25 13:30 | 1187 | 1187
2019-01-25 14:00 | 1210 | 1210
2019-01-25 14:30 | 1282 | 1281
2019-01-25 15:00 | 1304 | 1303
2019-01-25 15:30 | 1318 | 1318
2019-01-25 16:00 | 1317 | 1316
2019-01-25 16:30 | 1338 | 1337
2019-01-25 17:00 | 1379 | 1379
2019-01-25 17:30 | 1379 | 1379
2019-01-25 18:00 | 1356 | 1355
2019-01-25 18:30 | 1346 | 1344
2019-01-25 19:00 | 1350 | 1348
2019-01-25 19:30 | 1371 | 1371
2019-01-25 20:00 | 1350 | 1350
2019-01-25 20:30 | 1249 | 1245
2019-01-25 21:00 | 1218 | 1217
2019-01-25 21:30 | 1160 | 1154
2019-01-25 22:00 | 1109 | 1103
2019-01-25 22:30 | 1064 | 1058
2019-01-25 23:00 | 1011 | 1005
2019-01-25 23:30 | 920 | 918
2019-01-26 | 857 | 852
2019-01-26 00:30 | 798 | 793
2019-01-26 01:00 | 761 | 757
2019-01-26 01:30 | 741 | 737
2019-01-26 02:00 | 724 | 719
2019-01-26 02:30 | 711 | 704
2019-01-26 03:00 | 700 | 692
2019-01-26 03:30 | 691 | 682
2019-01-26 04:00 | 684 | 674
2019-01-26 04:30 | 683 | 673
2019-01-26 05:00 | 687 | 678
2019-01-26 05:30 | 690 | 680
2019-01-26 06:00 | 700 | 689
2019-01-26 06:30 | 714 | 706
2019-01-26 07:00 | 730 | 726
2019-01-26 07:30 | 758 | 757
2019-01-26 08:00 | 785 | 785
2019-01-26 08:30 | 820 | 819
2019-01-26 09:00 | 855 | 852
2019-01-26 09:30 | 874 | 874
2019-01-26 10:00 | 870 | 870
2019-01-26 10:30 | 905 | 904
2019-01-26 11:00 | 929 | 929
2019-01-26 11:30 | 929 | 929
2019-01-26 12:00 | 957 | 956
2019-01-26 12:30 | 954 | 954
2019-01-26 13:00 | 964 | 963
2019-01-26 13:30 | 994 | 992
2019-01-26 14:00 | 1010 | 1009
2019-01-26 14:30 | 1009 | 1007
2019-01-26 15:00 | 1056 | 1053
2019-01-26 15:30 | 1092 | 1090
2019-01-26 16:00 | 1125 | 1124
2019-01-26 16:30 | 1144 | 1144
2019-01-26 17:00 | 1218 | 1216
2019-01-26 17:30 | 1212 | 1212
2019-01-26 18:00 | 1153 | 1153
2019-01-26 18:30 | 1135 | 1134
2019-01-26 19:00 | 1128 | 1128
2019-01-26 19:30 | 1131 | 1131
2019-01-26 20:00 | 1107 | 1106
2019-01-26 20:30 | 1071 | 1071
2019-01-26 21:00 | 1035 | 1035
2019-01-26 21:30 | 1002 | 1002
2019-01-26 22:00 | 973 | 972
2019-01-26 22:30 | 947 | 947
2019-01-26 23:00 | 924 | 924
2019-01-26 23:30 | 868 | 867
2019-01-27 | 813 | 810
2019-01-27 00:30 | 749 | 745
2019-01-27 01:00 | 723 | 717
2019-01-27 01:30 | 709 | 702
2019-01-27 02:00 | 695 | 685
2019-01-27 02:30 | 679 | 668
2019-01-27 03:00 | 671 | 659
2019-01-27 03:30 | 665 | 652
2019-01-27 04:00 | 658 | 645
2019-01-27 04:30 | 659 | 645
2019-01-27 05:00 | 655 | 640
2019-01-27 05:30 | 660 | 642
2019-01-27 06:00 | 663 | 644
2019-01-27 06:30 | 668 | 655
2019-01-27 07:00 | 683 | 676
2019-01-27 07:30 | 703 | 700
2019-01-27 08:00 | 728 | 727
2019-01-27 08:30 | 758 | 757
2019-01-27 09:00 | 776 | 775
2019-01-27 09:30 | 780 | 780
2019-01-27 10:00 | 788 | 788
2019-01-27 10:30 | 783 | 782
2019-01-27 11:00 | 789 | 787
2019-01-27 11:30 | 797 | 795
2019-01-27 12:00 | 838 | 835
2019-01-27 12:30 | 845 | 845
2019-01-27 13:00 | 866 | 866
2019-01-27 13:30 | 886 | 886
2019-01-27 14:00 | 918 | 918
2019-01-27 14:30 | 948 | 948
2019-01-27 15:00 | 980 | 980
2019-01-27 15:30 | 1014 | 1014
2019-01-27 16:00 | 1044 | 1044
2019-01-27 16:30 | 1084 | 1084
2019-01-27 17:00 | 1108 | 1108
2019-01-27 17:30 | 1124 | 1124
2019-01-27 18:00 | 1118 | 1117
2019-01-27 18:30 | 1108 | 1106
2019-01-27 19:00 | 1109 | 1106
2019-01-27 19:30 | 1115 | 1113
2019-01-27 20:00 | 1109 | 1106
2019-01-27 20:30 | 1079 | 1076
2019-01-27 21:00 | 1041 | 1041
2019-01-27 21:30 | 1008 | 1008
2019-01-27 22:00 | 976 | 976
2019-01-27 22:30 | 938 | 938
2019-01-27 23:00 | 905 | 905
2019-01-27 23:30 | 843 | 843
2019-01-28 | 789 | 788
2019-01-28 00:30 | 745 | 743
2019-01-28 01:00 | 720 | 715
2019-01-28 01:30 | 699 | 692
2019-01-28 02:00 | 677 | 667
2019-01-28 02:30 | 667 | 656
2019-01-28 03:00 | 664 | 651
2019-01-28 03:30 | 666 | 653
2019-01-28 04:00 | 671 | 659
2019-01-28 04:30 | 665 | 653
2019-01-28 05:00 | 666 | 654
2019-01-28 05:30 | 710 | 700
2019-01-28 06:00 | 714 | 706
2019-01-28 06:30 | 684 | 676
2019-01-28 07:00 | 704 | 700
2019-01-28 07:30 | 744 | 743
2019-01-28 08:00 | 771 | 771
2019-01-28 08:30 | 802 | 801
2019-01-28 09:00 | 829 | 829
2019-01-28 09:30 | 839 | 839
2019-01-28 10:00 | 848 | 847
2019-01-28 10:30 | 854 | 854
2019-01-28 11:00 | 858 | 857
2019-01-28 11:30 | 858 | 858
2019-01-28 12:00 | 880 | 880
2019-01-28 12:30 | 901 | 901
2019-01-28 13:00 | 919 | 918
2019-01-28 13:30 | 945 | 945
2019-01-28 14:00 | 972 | 972
2019-01-28 14:30 | 1003 | 1003
2019-01-28 15:00 | 1042 | 1042
2019-01-28 15:30 | 1081 | 1080
2019-01-28 16:00 | 1123 | 1121
2019-01-28 16:30 | 1193 | 1193
2019-01-28 17:00 | 1210 | 1210
2019-01-28 17:30 | 1233 | 1232
2019-01-28 18:00 | 1221 | 1221
2019-01-28 18:30 | 1209 | 1209
2019-01-28 19:00 | 1207 | 1207
2019-01-28 19:30 | 1220 | 1220
2019-01-28 20:00 | 1210 | 1210
2019-01-28 20:30 | 1168 | 1168
2019-01-28 21:00 | 1117 | 1116
2019-01-28 21:30 | 1067 | 1066
2019-01-28 22:00 | 1025 | 1022
2019-01-28 22:30 | 973 | 970
2019-01-28 23:00 | 930 | 929
2019-01-28 23:30 | 864 | 864
2019-01-29 | 803 | 802
2019-01-29 00:30 | 756 | 755
2019-01-29 01:00 | 734 | 733
2019-01-29 01:30 | 718 | 715
2019-01-29 02:00 | 705 | 701
2019-01-29 02:30 | 697 | 693
2019-01-29 03:00 | 688 | 683
2019-01-29 03:30 | 684 | 678
2019-01-29 04:00 | 684 | 678
2019-01-29 04:30 | 692 | 686
2019-01-29 05:00 | 699 | 694
2019-01-29 05:30 | 728 | 724
2019-01-29 06:00 | 754 | 752
2019-01-29 06:30 | 827 | 827
2019-01-29 07:00 | 894 | 894
2019-01-29 07:30 | 984 | 983
2019-01-29 08:00 | 1044 | 1044
2019-01-29 08:30 | 1061 | 1059
2019-01-29 09:00 | 1078 | 1077
2019-01-29 09:30 | 1101 | 1100
2019-01-29 10:00 | 1096 | 1095
2019-01-29 10:30 | 1089 | 1089
2019-01-29 11:00 | 1093 | 1092
2019-01-29 11:30 | 1102 | 1102
2019-01-29 12:00 | 1116 | 1116
2019-01-29 12:30 | 1105 | 1105
2019-01-29 13:00 | 1124 | 1123
2019-01-29 13:30 | 1155 | 1155
2019-01-29 14:00 | 1170 | 1169
2019-01-29 14:30 | 1194 | 1193
2019-01-29 15:00 | 1221 | 1219
2019-01-29 15:30 | 1250 | 1248
2019-01-29 16:00 | 1288 | 1287
2019-01-29 16:30 | 1315 | 1314
2019-01-29 17:00 | 1359 | 1358
2019-01-29 17:30 | 1363 | 1360
2019-01-29 18:00 | 1322 | 1318
2019-01-29 18:30 | 1305 | 1300
2019-01-29 19:00 | 1327 | 1325
2019-01-29 19:30 | 1310 | 1307
2019-01-29 20:00 | 1284 | 1279
2019-01-29 20:30 | 1238 | 1234
2019-01-29 21:00 | 1177 | 1175
2019-01-29 21:30 | 1108 | 1107
2019-01-29 22:00 | 1061 | 1057
2019-01-29 22:30 | 1007 | 1004
2019-01-29 23:00 | 954 | 953
2019-01-29 23:30 | 884 | 882
2019-01-30 | 822 | 821
2019-01-30 00:30 | 780 | 778
2019-01-30 01:00 | 756 | 753
2019-01-30 01:30 | 736 | 731
2019-01-30 02:00 | 720 | 714
2019-01-30 02:30 | 710 | 703
2019-01-30 03:00 | 705 | 697
2019-01-30 03:30 | 703 | 695
2019-01-30 04:00 | 701 | 693
2019-01-30 04:30 | 710 | 703
2019-01-30 05:00 | 722 | 716
2019-01-30 05:30 | 750 | 747
2019-01-30 06:00 | 780 | 778
2019-01-30 06:30 | 845 | 845
2019-01-30 07:00 | 914 | 914
2019-01-30 07:30 | 1016 | 1014
2019-01-30 08:00 | 1066 | 1064
2019-01-30 08:30 | 1116 | 1116
2019-01-30 09:00 | 1103 | 1103
2019-01-30 09:30 | 1118 | 1118
2019-01-30 10:00 | 1093 | 1092
2019-01-30 10:30 | 1086 | 1085
2019-01-30 11:00 | 1092 | 1091
2019-01-30 11:30 | 1094 | 1094
2019-01-30 12:00 | 1110 | 1110
2019-01-30 12:30 | 1142 | 1142
2019-01-30 13:00 | 1165 | 1165
2019-01-30 13:30 | 1193 | 1192
2019-01-30 14:00 | 1240 | 1238
2019-01-30 14:30 | 1241 | 1239
2019-01-30 15:00 | 1270 | 1267
2019-01-30 15:30 | 1289 | 1287
2019-01-30 16:00 | 1289 | 1288
2019-01-30 16:30 | 1289 | 1289
2019-01-30 17:00 | 1318 | 1318
2019-01-30 17:30 | 1317 | 1317
2019-01-30 18:00 | 1291 | 1291
2019-01-30 18:30 | 1249 | 1246
2019-01-30 19:00 | 1271 | 1270
2019-01-30 19:30 | 1275 | 1275
2019-01-30 20:00 | 1258 | 1257
2019-01-30 20:30 | 1222 | 1220
2019-01-30 21:00 | 1175 | 1173
2019-01-30 21:30 | 1114 | 1111
2019-01-30 22:00 | 1056 | 1051
2019-01-30 22:30 | 994 | 994
2019-01-30 23:00 | 927 | 926
2019-01-30 23:30 | 851 | 849
2019-01-31 | 792 | 792
2019-01-31 00:30 | 749 | 746
2019-01-31 01:00 | 725 | 721
2019-01-31 01:30 | 708 | 701
2019-01-31 02:00 | 694 | 687
2019-01-31 02:30 | 686 | 678
2019-01-31 03:00 | 678 | 669
2019-01-31 03:30 | 679 | 670
2019-01-31 04:00 | 675 | 665
2019-01-31 04:30 | 677 | 669
2019-01-31 05:00 | 689 | 683
2019-01-31 05:30 | 716 | 712
2019-01-31 06:00 | 745 | 742
2019-01-31 06:30 | 815 | 814
2019-01-31 07:00 | 869 | 869
2019-01-31 07:30 | 954 | 954
2019-01-31 08:00 | 1002 | 1002
2019-01-31 08:30 | 1019 | 1019
2019-01-31 09:00 | 1051 | 1051
2019-01-31 09:30 | 1064 | 1061
2019-01-31 10:00 | 1068 | 1067
2019-01-31 10:30 | 1087 | 1086
2019-01-31 11:00 | 1104 | 1104
2019-01-31 11:30 | 1112 | 1112
2019-01-31 12:00 | 1109 | 1109
2019-01-31 12:30 | 1102 | 1102
2019-01-31 13:00 | 1144 | 1144
2019-01-31 13:30 | 1191 | 1189
2019-01-31 14:00 | 1203 | 1202
2019-01-31 14:30 | 1195 | 1195
2019-01-31 15:00 | 1212 | 1212
2019-01-31 15:30 | 1250 | 1250
2019-01-31 16:00 | 1279 | 1278
2019-01-31 16:30 | 1327 | 1326
2019-01-31 17:00 | 1372 | 1370
2019-01-31 17:30 | 1347 | 1347
2019-01-31 18:00 | 1340 | 1340
2019-01-31 18:30 | 1317 | 1316
2019-01-31 19:00 | 1328 | 1328
2019-01-31 19:30 | 1313 | 1312
2019-01-31 20:00 | 1296 | 1294
2019-01-31 20:30 | 1260 | 1258
2019-01-31 21:00 | 1202 | 1202
2019-01-31 21:30 | 1127 | 1127
2019-01-31 22:00 | 1065 | 1064
2019-01-31 22:30 | 1017 | 1016
2019-01-31 23:00 | 965 | 964
2019-01-31 23:30 | 881 | 880
2019-02-01 | 819 | 816
2019-02-01 00:30 | 765 | 761
2019-02-01 01:00 | 739 | 736
2019-02-01 01:30 | 722 | 717
2019-02-01 02:00 | 704 | 696
2019-02-01 02:30 | 692 | 683
2019-02-01 03:00 | 686 | 675
2019-02-01 03:30 | 679 | 668
2019-02-01 04:00 | 674 | 664
2019-02-01 04:30 | 680 | 669
2019-02-01 05:00 | 689 | 681
2019-02-01 05:30 | 716 | 710
2019-02-01 06:00 | 730 | 725
2019-02-01 06:30 | 805 | 805
2019-02-01 07:00 | 871 | 871
2019-02-01 07:30 | 948 | 948
2019-02-01 08:00 | 998 | 998
2019-02-01 08:30 | 1017 | 1017
2019-02-01 09:00 | 1021 | 1020
2019-02-01 09:30 | 1034 | 1033
2019-02-01 10:00 | 1025 | 1024
2019-02-01 10:30 | 1024 | 1024
2019-02-01 11:00 | 1040 | 1040
2019-02-01 11:30 | 1038 | 1038
2019-02-01 12:00 | 1038 | 1038
2019-02-01 12:30 | 1064 | 1063
2019-02-01 13:00 | 1090 | 1090
2019-02-01 13:30 | 1120 | 1120
2019-02-01 14:00 | 1150 | 1150
2019-02-01 14:30 | 1218 | 1218
2019-02-01 15:00 | 1233 | 1232
2019-02-01 15:30 | 1211 | 1208
2019-02-01 16:00 | 1220 | 1217
2019-02-01 16:30 | 1247 | 1245
2019-02-01 17:00 | 1247 | 1243
2019-02-01 17:30 | 1216 | 1207
2019-02-01 18:00 | 1176 | 1167
2019-02-01 18:30 | 1152 | 1138
2019-02-01 19:00 | 1158 | 1150
2019-02-01 19:30 | 1161 | 1155
2019-02-01 20:00 | 1153 | 1149
2019-02-01 20:30 | 1129 | 1125
2019-02-01 21:00 | 1081 | 1081
2019-02-01 21:30 | 1073 | 1072
2019-02-01 22:00 | 1018 | 1016
2019-02-01 22:30 | 961 | 960
2019-02-01 23:00 | 921 | 919
2019-02-01 23:30 | 843 | 842
2019-02-02 | 791 | 788
2019-02-02 00:30 | 742 | 739
2019-02-02 01:00 | 718 | 713
2019-02-02 01:30 | 702 | 696
2019-02-02 02:00 | 691 | 682
2019-02-02 02:30 | 677 | 667
2019-02-02 03:00 | 672 | 662
2019-02-02 03:30 | 667 | 657
2019-02-02 04:00 | 661 | 649
2019-02-02 04:30 | 664 | 652
2019-02-02 05:00 | 663 | 650
2019-02-02 05:30 | 674 | 659
2019-02-02 06:00 | 672 | 657
2019-02-02 06:30 | 697 | 686
2019-02-02 07:00 | 710 | 703
2019-02-02 07:30 | 736 | 734
2019-02-02 08:00 | 772 | 769
2019-02-02 08:30 | 810 | 809
2019-02-02 09:00 | 820 | 819
2019-02-02 09:30 | 819 | 818
2019-02-02 10:00 | 830 | 830
2019-02-02 10:30 | 814 | 813
2019-02-02 11:00 | 829 | 828
2019-02-02 11:30 | 811 | 808
2019-02-02 12:00 | 840 | 837
2019-02-02 12:30 | 851 | 849
2019-02-02 13:00 | 866 | 864
2019-02-02 13:30 | 883 | 882
2019-02-02 14:00 | 917 | 917
2019-02-02 14:30 | 946 | 946
2019-02-02 15:00 | 941 | 941
2019-02-02 15:30 | 965 | 964
2019-02-02 16:00 | 991 | 991
2019-02-02 16:30 | 1009 | 1008
2019-02-02 17:00 | 1036 | 1035
2019-02-02 17:30 | 1065 | 1059
2019-02-02 18:00 | 1053 | 1043
2019-02-02 18:30 | 1059 | 1048
2019-02-02 19:00 | 1071 | 1060
2019-02-02 19:30 | 1082 | 1073
2019-02-02 20:00 | 1075 | 1066
2019-02-02 20:30 | 1040 | 1034
2019-02-02 21:00 | 1003 | 998
2019-02-02 21:30 | 969 | 962
2019-02-02 22:00 | 934 | 930
2019-02-02 22:30 | 912 | 910
2019-02-02 23:00 | 894 | 892
2019-02-02 23:30 | 842 | 839
2019-02-03 | 781 | 776
2019-02-03 00:30 | 717 | 710
2019-02-03 01:00 | 691 | 682
2019-02-03 01:30 | 680 | 669
2019-02-03 02:00 | 663 | 650
2019-02-03 02:30 | 658 | 642
2019-02-03 03:00 | 647 | 630
2019-02-03 03:30 | 644 | 626
2019-02-03 04:00 | 641 | 622
2019-02-03 04:30 | 640 | 621
2019-02-03 05:00 | 641 | 622
2019-02-03 05:30 | 645 | 624
2019-02-03 06:00 | 644 | 621
2019-02-03 06:30 | 665 | 646
2019-02-03 07:00 | 679 | 665
2019-02-03 07:30 | 694 | 685
2019-02-03 08:00 | 713 | 708
2019-02-03 08:30 | 733 | 731
2019-02-03 09:00 | 755 | 754
2019-02-03 09:30 | 759 | 759
2019-02-03 10:00 | 769 | 768
2019-02-03 10:30 | 790 | 790
2019-02-03 11:00 | 768 | 768
2019-02-03 11:30 | 751 | 751
2019-02-03 12:00 | 779 | 779
2019-02-03 12:30 | 767 | 767
2019-02-03 13:00 | 772 | 772
2019-02-03 13:30 | 789 | 788
2019-02-03 14:00 | 833 | 833
2019-02-03 14:30 | 837 | 837
2019-02-03 15:00 | 874 | 874
2019-02-03 15:30 | 908 | 908
2019-02-03 16:00 | 953 | 953
2019-02-03 16:30 | 999 | 999
2019-02-03 17:00 | 1031 | 1031
2019-02-03 17:30 | 1056 | 1056
2019-02-03 18:00 | 1069 | 1069
2019-02-03 18:30 | 1071 | 1071
2019-02-03 19:00 | 1080 | 1080
2019-02-03 19:30 | 1089 | 1089
2019-02-03 20:00 | 1079 | 1079
2019-02-03 20:30 | 1065 | 1064
2019-02-03 21:00 | 1020 | 1018
2019-02-03 21:30 | 970 | 969
2019-02-03 22:00 | 939 | 937
2019-02-03 22:30 | 914 | 912
2019-02-03 23:00 | 895 | 891
2019-02-03 23:30 | 837 | 836
2019-02-04 | 776 | 774
2019-02-04 00:30 | 713 | 707
2019-02-04 01:00 | 684 | 676
2019-02-04 01:30 | 679 | 670
2019-02-04 02:00 | 663 | 651
2019-02-04 02:30 | 657 | 646
2019-02-04 03:00 | 652 | 639
2019-02-04 03:30 | 651 | 638
2019-02-04 04:00 | 654 | 642
2019-02-04 04:30 | 663 | 653
2019-02-04 05:00 | 678 | 670
2019-02-04 05:30 | 711 | 705
2019-02-04 06:00 | 747 | 744
2019-02-04 06:30 | 816 | 816
2019-02-04 07:00 | 884 | 884
2019-02-04 07:30 | 967 | 967
2019-02-04 08:00 | 999 | 999
2019-02-04 08:30 | 1026 | 1026
2019-02-04 09:00 | 1030 | 1030
2019-02-04 09:30 | 1029 | 1029
2019-02-04 10:00 | 1011 | 1011
2019-02-04 10:30 | 990 | 990
2019-02-04 11:00 | 976 | 975
2019-02-04 11:30 | 970 | 969
2019-02-04 12:00 | 972 | 970
2019-02-04 12:30 | 988 | 987
2019-02-04 13:00 | 1007 | 1005
2019-02-04 13:30 | 1015 | 1012
2019-02-04 14:00 | 1043 | 1039
2019-02-04 14:30 | 1060 | 1055
2019-02-04 15:00 | 1067 | 1067
2019-02-04 15:30 | 1090 | 1089
2019-02-04 16:00 | 1159 | 1157
2019-02-04 16:30 | 1202 | 1200
2019-02-04 17:00 | 1240 | 1239
2019-02-04 17:30 | 1252 | 1251
2019-02-04 18:00 | 1247 | 1247
2019-02-04 18:30 | 1206 | 1205
2019-02-04 19:00 | 1202 | 1201
2019-02-04 19:30 | 1207 | 1206
2019-02-04 20:00 | 1189 | 1187
2019-02-04 20:30 | 1156 | 1154
2019-02-04 21:00 | 1093 | 1093
2019-02-04 21:30 | 1037 | 1036
2019-02-04 22:00 | 1005 | 1002
2019-02-04 22:30 | 963 | 959
2019-02-04 23:00 | 912 | 911
2019-02-04 23:30 | 844 | 841
2019-02-05 | 781 | 778
2019-02-05 00:30 | 737 | 730
2019-02-05 01:00 | 707 | 702
2019-02-05 01:30 | 690 | 683
2019-02-05 02:00 | 679 | 671
2019-02-05 02:30 | 677 | 668
2019-02-05 03:00 | 669 | 659
2019-02-05 03:30 | 666 | 656
2019-02-05 04:00 | 665 | 656
2019-02-05 04:30 | 674 | 665
2019-02-05 05:00 | 689 | 683
2019-02-05 05:30 | 717 | 713
2019-02-05 06:00 | 746 | 744
2019-02-05 06:30 | 814 | 814
2019-02-05 07:00 | 881 | 881
2019-02-05 07:30 | 955 | 955
2019-02-05 08:00 | 991 | 991
2019-02-05 08:30 | 1014 | 1014
2019-02-05 09:00 | 1023 | 1023
2019-02-05 09:30 | 1015 | 1014
2019-02-05 10:00 | 984 | 984
2019-02-05 10:30 | 983 | 983
2019-02-05 11:00 | 987 | 987
2019-02-05 11:30 | 988 | 988
2019-02-05 12:00 | 997 | 997
2019-02-05 12:30 | 999 | 999
2019-02-05 13:00 | 1027 | 1026
2019-02-05 13:30 | 1067 | 1067
2019-02-05 14:00 | 1097 | 1095
2019-02-05 14:30 | 1096 | 1094
2019-02-05 15:00 | 1104 | 1104
2019-02-05 15:30 | 1124 | 1123
2019-02-05 16:00 | 1141 | 1141
2019-02-05 16:30 | 1179 | 1179
2019-02-05 17:00 | 1218 | 1217
2019-02-05 17:30 | 1224 | 1223
2019-02-05 18:00 | 1197 | 1194
2019-02-05 18:30 | 1171 | 1167
2019-02-05 19:00 | 1179 | 1176
2019-02-05 19:30 | 1154 | 1151
2019-02-05 20:00 | 1131 | 1129
2019-02-05 20:30 | 1100 | 1098
2019-02-05 21:00 | 1053 | 1050
2019-02-05 21:30 | 1012 | 1006
2019-02-05 22:00 | 980 | 972
2019-02-05 22:30 | 948 | 942
2019-02-05 23:00 | 902 | 902
2019-02-05 23:30 | 837 | 837
2019-02-06 | 783 | 780
2019-02-06 00:30 | 737 | 730
2019-02-06 01:00 | 706 | 700
2019-02-06 01:30 | 692 | 687
2019-02-06 02:00 | 679 | 672
2019-02-06 02:30 | 674 | 666
2019-02-06 03:00 | 664 | 655
2019-02-06 03:30 | 662 | 653
2019-02-06 04:00 | 667 | 658
2019-02-06 04:30 | 670 | 662
2019-02-06 05:00 | 685 | 679
2019-02-06 05:30 | 719 | 715
2019-02-06 06:00 | 748 | 746
2019-02-06 06:30 | 815 | 814
2019-02-06 07:00 | 877 | 875
2019-02-06 07:30 | 951 | 951
2019-02-06 08:00 | 978 | 978
2019-02-06 08:30 | 992 | 992
2019-02-06 09:00 | 980 | 980
2019-02-06 09:30 | 1003 | 1001
2019-02-06 10:00 | 1008 | 1007
2019-02-06 10:30 | 1037 | 1037
2019-02-06 11:00 | 1021 | 1020
2019-02-06 11:30 | 1020 | 1020
2019-02-06 12:00 | 1016 | 1016
2019-02-06 12:30 | 1014 | 1014
2019-02-06 13:00 | 1020 | 1020
2019-02-06 13:30 | 1004 | 1004
2019-02-06 14:00 | 1038 | 1037
2019-02-06 14:30 | 1030 | 1030
2019-02-06 15:00 | 1051 | 1051
2019-02-06 15:30 | 1066 | 1066
2019-02-06 16:00 | 1129 | 1129
2019-02-06 16:30 | 1174 | 1174
2019-02-06 17:00 | 1166 | 1164
2019-02-06 17:30 | 1164 | 1159
2019-02-06 18:00 | 1162 | 1156
2019-02-06 18:30 | 1141 | 1136
2019-02-06 19:00 | 1156 | 1154
2019-02-06 19:30 | 1155 | 1154
2019-02-06 20:00 | 1140 | 1138
2019-02-06 20:30 | 1111 | 1109
2019-02-06 21:00 | 1067 | 1067
2019-02-06 21:30 | 1022 | 1020
2019-02-06 22:00 | 993 | 988
2019-02-06 22:30 | 945 | 942
2019-02-06 23:00 | 906 | 905
2019-02-06 23:30 | 843 | 840
2019-02-07 | 774 | 771
2019-02-07 00:30 | 722 | 719
2019-02-07 01:00 | 701 | 696
2019-02-07 01:30 | 685 | 678
2019-02-07 02:00 | 673 | 664
2019-02-07 02:30 | 666 | 657
2019-02-07 03:00 | 665 | 654
2019-02-07 03:30 | 657 | 647
2019-02-07 04:00 | 661 | 650
2019-02-07 04:30 | 670 | 662
2019-02-07 05:00 | 686 | 679
2019-02-07 05:30 | 708 | 702
2019-02-07 06:00 | 736 | 733
2019-02-07 06:30 | 795 | 795
2019-02-07 07:00 | 854 | 854
2019-02-07 07:30 | 932 | 932
2019-02-07 08:00 | 974 | 974
2019-02-07 08:30 | 975 | 975
2019-02-07 09:00 | 991 | 991
2019-02-07 09:30 | 992 | 992
2019-02-07 10:00 | 985 | 984
2019-02-07 10:30 | 992 | 991
2019-02-07 11:00 | 1003 | 1003
2019-02-07 11:30 | 1042 | 1041
2019-02-07 12:00 | 1028 | 1026
2019-02-07 12:30 | 1006 | 1002
2019-02-07 13:00 | 1030 | 1028
2019-02-07 13:30 | 1057 | 1056
2019-02-07 14:00 | 1092 | 1091
2019-02-07 14:30 | 1087 | 1086
2019-02-07 15:00 | 1117 | 1116
2019-02-07 15:30 | 1160 | 1160
2019-02-07 16:00 | 1168 | 1167
2019-02-07 16:30 | 1156 | 1154
2019-02-07 17:00 | 1158 | 1155
2019-02-07 17:30 | 1146 | 1140
2019-02-07 18:00 | 1143 | 1138
2019-02-07 18:30 | 1143 | 1136
2019-02-07 19:00 | 1161 | 1160
2019-02-07 19:30 | 1158 | 1157
2019-02-07 20:00 | 1159 | 1157
2019-02-07 20:30 | 1126 | 1124
2019-02-07 21:00 | 1083 | 1082
2019-02-07 21:30 | 1025 | 1024
2019-02-07 22:00 | 975 | 975
2019-02-07 22:30 | 941 | 940
2019-02-07 23:00 | 906 | 905
2019-02-07 23:30 | 838 | 838
2019-02-08 | 774 | 773
2019-02-08 00:30 | 726 | 722
2019-02-08 01:00 | 702 | 697
2019-02-08 01:30 | 689 | 681
2019-02-08 02:00 | 681 | 672
2019-02-08 02:30 | 674 | 665
2019-02-08 03:00 | 669 | 659
2019-02-08 03:30 | 664 | 655
2019-02-08 04:00 | 673 | 663
2019-02-08 04:30 | 677 | 668
2019-02-08 05:00 | 690 | 683
2019-02-08 05:30 | 720 | 715
2019-02-08 06:00 | 754 | 749
2019-02-08 06:30 | 816 | 814
2019-02-08 07:00 | 885 | 885
2019-02-08 07:30 | 968 | 968
2019-02-08 08:00 | 1011 | 1011
2019-02-08 08:30 | 1030 | 1029
2019-02-08 09:00 | 1036 | 1034
2019-02-08 09:30 | 1048 | 1048
2019-02-08 10:00 | 1019 | 1017
2019-02-08 10:30 | 1013 | 1013
2019-02-08 11:00 | 1009 | 1008
2019-02-08 11:30 | 1005 | 1005
2019-02-08 12:00 | 1017 | 1017
2019-02-08 12:30 | 1023 | 1022
2019-02-08 13:00 | 1016 | 1016
2019-02-08 13:30 | 1025 | 1025
2019-02-08 14:00 | 1048 | 1047
2019-02-08 14:30 | 1068 | 1068
2019-02-08 15:00 | 1095 | 1094
2019-02-08 15:30 | 1118 | 1118
2019-02-08 16:00 | 1163 | 1162
2019-02-08 16:30 | 1209 | 1208
2019-02-08 17:00 | 1227 | 1226
2019-02-08 17:30 | 1221 | 1221
2019-02-08 18:00 | 1189 | 1188
2019-02-08 18:30 | 1157 | 1153
2019-02-08 19:00 | 1162 | 1162
2019-02-08 19:30 | 1163 | 1163
2019-02-08 20:00 | 1159 | 1158
2019-02-08 20:30 | 1130 | 1128
2019-02-08 21:00 | 1094 | 1090
2019-02-08 21:30 | 1058 | 1052
2019-02-08 22:00 | 1034 | 1024
2019-02-08 22:30 | 989 | 986
2019-02-08 23:00 | 956 | 953
2019-02-08 23:30 | 889 | 883
2019-02-09 | 824 | 816
2019-02-09 00:30 | 765 | 755
2019-02-09 01:00 | 734 | 724
2019-02-09 01:30 | 714 | 703
2019-02-09 02:00 | 690 | 679
2019-02-09 02:30 | 685 | 673
2019-02-09 03:00 | 681 | 667
2019-02-09 03:30 | 673 | 659
2019-02-09 04:00 | 663 | 647
2019-02-09 04:30 | 657 | 640
2019-02-09 05:00 | 664 | 646
2019-02-09 05:30 | 669 | 652
2019-02-09 06:00 | 678 | 660
2019-02-09 06:30 | 693 | 679
2019-02-09 07:00 | 702 | 692
2019-02-09 07:30 | 730 | 727
2019-02-09 08:00 | 763 | 762
2019-02-09 08:30 | 815 | 813
2019-02-09 09:00 | 834 | 834
2019-02-09 09:30 | 848 | 847
2019-02-09 10:00 | 867 | 867
2019-02-09 10:30 | 860 | 859
2019-02-09 11:00 | 877 | 877
2019-02-09 11:30 | 881 | 880
2019-02-09 12:00 | 886 | 886
2019-02-09 12:30 | 892 | 892
2019-02-09 13:00 | 908 | 908
2019-02-09 13:30 | 931 | 931
2019-02-09 14:00 | 956 | 956
2019-02-09 14:30 | 986 | 984
2019-02-09 15:00 | 1012 | 1011
2019-02-09 15:30 | 1039 | 1038
2019-02-09 16:00 | 1061 | 1060
2019-02-09 16:30 | 1119 | 1116
2019-02-09 17:00 | 1172 | 1171
2019-02-09 17:30 | 1208 | 1207
2019-02-09 18:00 | 1211 | 1209
2019-02-09 18:30 | 1248 | 1246
2019-02-09 19:00 | 1238 | 1235
2019-02-09 19:30 | 1231 | 1229
2019-02-09 20:00 | 1222 | 1219
2019-02-09 20:30 | 1196 | 1195
2019-02-09 21:00 | 1148 | 1145
2019-02-09 21:30 | 1109 | 1107
2019-02-09 22:00 | 1070 | 1067
2019-02-09 22:30 | 1045 | 1040
2019-02-09 23:00 | 1013 | 1009
2019-02-09 23:30 | 878 | 876
2019-02-10 | 817 | 811
2019-02-10 00:30 | 764 | 759
2019-02-10 01:00 | 733 | 729
2019-02-10 01:30 | 715 | 709
2019-02-10 02:00 | 704 | 697
2019-02-10 02:30 | 696 | 688
2019-02-10 03:00 | 685 | 676
2019-02-10 03:30 | 676 | 666
2019-02-10 04:00 | 669 | 658
2019-02-10 04:30 | 667 | 655
2019-02-10 05:00 | 664 | 651
2019-02-10 05:30 | 670 | 654
2019-02-10 06:00 | 670 | 652
2019-02-10 06:30 | 683 | 668
2019-02-10 07:00 | 695 | 684
2019-02-10 07:30 | 714 | 710
2019-02-10 08:00 | 733 | 732
2019-02-10 08:30 | 764 | 764
2019-02-10 09:00 | 783 | 783
2019-02-10 09:30 | 813 | 812
2019-02-10 10:00 | 862 | 860
2019-02-10 10:30 | 879 | 873
2019-02-10 11:00 | 875 | 869
2019-02-10 11:30 | 868 | 863
2019-02-10 12:00 | 866 | 861
2019-02-10 12:30 | 871 | 867
2019-02-10 13:00 | 882 | 878
2019-02-10 13:30 | 895 | 892
2019-02-10 14:00 | 918 | 916
2019-02-10 14:30 | 923 | 922
2019-02-10 15:00 | 949 | 948
2019-02-10 15:30 | 977 | 977
2019-02-10 16:00 | 1019 | 1019
2019-02-10 16:30 | 1065 | 1063
2019-02-10 17:00 | 1117 | 1114
2019-02-10 17:30 | 1120 | 1116
2019-02-10 18:00 | 1120 | 1115
2019-02-10 18:30 | 1118 | 1113
2019-02-10 19:00 | 1129 | 1127
2019-02-10 19:30 | 1123 | 1119
2019-02-10 20:00 | 1111 | 1108
2019-02-10 20:30 | 1083 | 1082
2019-02-10 21:00 | 1037 | 1036
2019-02-10 21:30 | 1006 | 1003
2019-02-10 22:00 | 967 | 964
2019-02-10 22:30 | 928 | 925
2019-02-10 23:00 | 892 | 890
2019-02-10 23:30 | 839 | 837
2019-02-11 | 784 | 782
2019-02-11 00:30 | 747 | 741
2019-02-11 01:00 | 722 | 715
2019-02-11 01:30 | 711 | 702
2019-02-11 02:00 | 700 | 691
2019-02-11 02:30 | 700 | 691
2019-02-11 03:00 | 690 | 680
2019-02-11 03:30 | 685 | 676
2019-02-11 04:00 | 687 | 677
2019-02-11 04:30 | 693 | 683
2019-02-11 05:00 | 709 | 701
2019-02-11 05:30 | 744 | 739
2019-02-11 06:00 | 772 | 770
2019-02-11 06:30 | 844 | 842
2019-02-11 07:00 | 896 | 896
2019-02-11 07:30 | 971 | 971
2019-02-11 08:00 | 989 | 989
2019-02-11 08:30 | 999 | 999
2019-02-11 09:00 | 1022 | 1022
2019-02-11 09:30 | 1052 | 1051
2019-02-11 10:00 | 1034 | 1034
2019-02-11 10:30 | 1015 | 1015
2019-02-11 11:00 | 1009 | 1009
2019-02-11 11:30 | 1013 | 1013
2019-02-11 12:00 | 1021 | 1021
2019-02-11 12:30 | 1026 | 1026
2019-02-11 13:00 | 1040 | 1040
2019-02-11 13:30 | 1065 | 1064
2019-02-11 14:00 | 1080 | 1080
2019-02-11 14:30 | 1096 | 1096
2019-02-11 15:00 | 1112 | 1112
2019-02-11 15:30 | 1140 | 1140
2019-02-11 16:00 | 1187 | 1187
2019-02-11 16:30 | 1233 | 1233
2019-02-11 17:00 | 1266 | 1266
2019-02-11 17:30 | 1278 | 1277
2019-02-11 18:00 | 1257 | 1255
2019-02-11 18:30 | 1236 | 1234
2019-02-11 19:00 | 1223 | 1222
2019-02-11 19:30 | 1223 | 1222
2019-02-11 20:00 | 1207 | 1205
2019-02-11 20:30 | 1170 | 1167
2019-02-11 21:00 | 1114 | 1113
2019-02-11 21:30 | 1067 | 1065
2019-02-11 22:00 | 1015 | 1011
2019-02-11 22:30 | 973 | 968
2019-02-11 23:00 | 918 | 910
2019-02-11 23:30 | 861 | 853
2019-02-12 | 811 | 806
2019-02-12 00:30 | 761 | 755
2019-02-12 01:00 | 734 | 729
2019-02-12 01:30 | 717 | 712
2019-02-12 02:00 | 682 | 675
2019-02-12 02:30 | 697 | 690
2019-02-12 03:00 | 697 | 689
2019-02-12 03:30 | 690 | 681
2019-02-12 04:00 | 690 | 681
2019-02-12 04:30 | 699 | 692
2019-02-12 05:00 | 716 | 711
2019-02-12 05:30 | 747 | 744
2019-02-12 06:00 | 770 | 768
2019-02-12 06:30 | 847 | 846
2019-02-12 07:00 | 911 | 911
2019-02-12 07:30 | 984 | 983
2019-02-12 08:00 | 1016 | 1016
2019-02-12 08:30 | 1031 | 1031
2019-02-12 09:00 | 1043 | 1041
2019-02-12 09:30 | 1058 | 1057
2019-02-12 10:00 | 1070 | 1070
2019-02-12 10:30 | 1087 | 1087
2019-02-12 11:00 | 1105 | 1104
2019-02-12 11:30 | 1127 | 1127
2019-02-12 12:00 | 1147 | 1147
2019-02-12 12:30 | 1180 | 1179
2019-02-12 13:00 | 1212 | 1212
2019-02-12 13:30 | 1257 | 1256
2019-02-12 14:00 | 1312 | 1308
2019-02-12 14:30 | 1377 | 1372
2019-02-12 15:00 | 1431 | 1429
2019-02-12 15:30 | 1463 | 1461
2019-02-12 16:00 | 1511 | 1508
2019-02-12 16:30 | 1529 | 1527
2019-02-12 17:00 | 1533 | 1531
2019-02-12 17:30 | 1537 | 1536
2019-02-12 18:00 | 1539 | 1539
2019-02-12 18:30 | 1467 | 1467
2019-02-12 19:00 | 1454 | 1454
2019-02-12 19:30 | 1464 | 1464
2019-02-12 20:00 | 1436 | 1435
2019-02-12 20:30 | 1394 | 1393
2019-02-12 21:00 | 1341 | 1338
2019-02-12 21:30 | 1277 | 1270
2019-02-12 22:00 | 1219 | 1209
2019-02-12 22:30 | 1132 | 1127
2019-02-12 23:00 | 1058 | 1056
2019-02-12 23:30 | 986 | 980
2019-02-13 | 920 | 914
2019-02-13 00:30 | 856 | 850
2019-02-13 01:00 | 821 | 820
2019-02-13 01:30 | 801 | 798
2019-02-13 02:00 | 783 | 780
2019-02-13 02:30 | 766 | 763
2019-02-13 03:00 | 757 | 751
2019-02-13 03:30 | 745 | 739
2019-02-13 04:00 | 738 | 731
2019-02-13 04:30 | 737 | 730
2019-02-13 05:00 | 745 | 739
2019-02-13 05:30 | 778 | 775
2019-02-13 06:00 | 807 | 806
2019-02-13 06:30 | 880 | 879
2019-02-13 07:00 | 942 | 940
2019-02-13 07:30 | 1031 | 1031
2019-02-13 08:00 | 1079 | 1079
2019-02-13 08:30 | 1105 | 1105
2019-02-13 09:00 | 1130 | 1130
2019-02-13 09:30 | 1149 | 1148
2019-02-13 10:00 | 1169 | 1168
2019-02-13 10:30 | 1184 | 1184
2019-02-13 11:00 | 1215 | 1215
2019-02-13 11:30 | 1242 | 1242
2019-02-13 12:00 | 1280 | 1279
2019-02-13 12:30 | 1308 | 1307
2019-02-13 13:00 | 1336 | 1334
2019-02-13 13:30 | 1367 | 1365
2019-02-13 14:00 | 1389 | 1388
2019-02-13 14:30 | 1417 | 1416
2019-02-13 15:00 | 1448 | 1447
2019-02-13 15:30 | 1485 | 1482
2019-02-13 16:00 | 1552 | 1550
2019-02-13 16:30 | 1580 | 1578
2019-02-13 17:00 | 1610 | 1608
2019-02-13 17:30 | 1616 | 1615
2019-02-13 18:00 | 1602 | 1602
2019-02-13 18:30 | 1562 | 1561
2019-02-13 19:00 | 1545 | 1543
2019-02-13 19:30 | 1522 | 1520
2019-02-13 20:00 | 1462 | 1462
2019-02-13 20:30 | 1455 | 1455
2019-02-13 21:00 | 1418 | 1418
2019-02-13 21:30 | 1322 | 1320
2019-02-13 22:00 | 1264 | 1260
2019-02-13 22:30 | 1151 | 1145
2019-02-13 23:00 | 1099 | 1095
2019-02-13 23:30 | 1031 | 1025
2019-02-14 | 960 | 957
2019-02-14 00:30 | 915 | 912
2019-02-14 01:00 | 890 | 884
2019-02-14 01:30 | 829 | 826
2019-02-14 02:00 | 788 | 787
2019-02-14 02:30 | 770 | 770
2019-02-14 03:00 | 760 | 759
2019-02-14 03:30 | 752 | 751
2019-02-14 04:00 | 745 | 744
2019-02-14 04:30 | 752 | 751
2019-02-14 05:00 | 760 | 760
2019-02-14 05:30 | 792 | 792
2019-02-14 06:00 | 818 | 818
2019-02-14 06:30 | 938 | 938
2019-02-14 07:00 | 1004 | 1004
2019-02-14 07:30 | 1022 | 1021
2019-02-14 08:00 | 1057 | 1057
2019-02-14 08:30 | 1087 | 1087
2019-02-14 09:00 | 1107 | 1106
2019-02-14 09:30 | 1105 | 1105
2019-02-14 10:00 | 1103 | 1103
2019-02-14 10:30 | 1100 | 1100
2019-02-14 11:00 | 1095 | 1095
2019-02-14 11:30 | 1091 | 1090
2019-02-14 12:00 | 1110 | 1109
2019-02-14 12:30 | 1088 | 1088
2019-02-14 13:00 | 1108 | 1108
2019-02-14 13:30 | 1135 | 1135
2019-02-14 14:00 | 1139 | 1139
2019-02-14 14:30 | 1153 | 1153
2019-02-14 15:00 | 1137 | 1137
2019-02-14 15:30 | 1137 | 1137
2019-02-14 16:00 | 1149 | 1148
2019-02-14 16:30 | 1154 | 1153
2019-02-14 17:00 | 1159 | 1157
2019-02-14 17:30 | 1147 | 1143
2019-02-14 18:00 | 1133 | 1128
2019-02-14 18:30 | 1120 | 1115
2019-02-14 19:00 | 1134 | 1132
2019-02-14 19:30 | 1125 | 1123
2019-02-14 20:00 | 1115 | 1112
2019-02-14 20:30 | 1090 | 1083
2019-02-14 21:00 | 1040 | 1035
2019-02-14 21:30 | 988 | 985
2019-02-14 22:00 | 948 | 944
2019-02-14 22:30 | 897 | 894
2019-02-14 23:00 | 854 | 851
2019-02-14 23:30 | 794 | 792
2019-02-15 | 750 | 745
2019-02-15 00:30 | 712 | 706
2019-02-15 01:00 | 692 | 684
2019-02-15 01:30 | 681 | 670
2019-02-15 02:00 | 670 | 658
2019-02-15 02:30 | 656 | 642
2019-02-15 03:00 | 653 | 638
2019-02-15 03:30 | 655 | 639
2019-02-15 04:00 | 659 | 642
2019-02-15 04:30 | 665 | 649
2019-02-15 05:00 | 673 | 661
2019-02-15 05:30 | 704 | 696
2019-02-15 06:00 | 730 | 724
2019-02-15 06:30 | 785 | 784
2019-02-15 07:00 | 829 | 828
2019-02-15 07:30 | 890 | 890
2019-02-15 08:00 | 908 | 908
2019-02-15 08:30 | 908 | 907
2019-02-15 09:00 | 911 | 911
2019-02-15 09:30 | 912 | 912
2019-02-15 10:00 | 912 | 912
2019-02-15 10:30 | 919 | 919
2019-02-15 11:00 | 914 | 914
2019-02-15 11:30 | 924 | 922
2019-02-15 12:00 | 950 | 949
2019-02-15 12:30 | 944 | 943
2019-02-15 13:00 | 950 | 949
2019-02-15 13:30 | 954 | 953
2019-02-15 14:00 | 978 | 978
2019-02-15 14:30 | 996 | 995
2019-02-15 15:00 | 1001 | 1000
2019-02-15 15:30 | 1018 | 1017
2019-02-15 16:00 | 1060 | 1060
2019-02-15 16:30 | 1104 | 1103
2019-02-15 17:00 | 1135 | 1135
2019-02-15 17:30 | 1128 | 1123
2019-02-15 18:00 | 1100 | 1095
2019-02-15 18:30 | 1079 | 1070
2019-02-15 19:00 | 1084 | 1076
2019-02-15 19:30 | 1078 | 1070
2019-02-15 20:00 | 1057 | 1049
2019-02-15 20:30 | 1021 | 1017
2019-02-15 21:00 | 986 | 982
2019-02-15 21:30 | 951 | 945
2019-02-15 22:00 | 923 | 920
2019-02-15 22:30 | 901 | 897
2019-02-15 23:00 | 859 | 854
2019-02-15 23:30 | 798 | 792
2019-02-16 | 742 | 735
2019-02-16 00:30 | 701 | 690
2019-02-16 01:00 | 682 | 668
2019-02-16 01:30 | 668 | 651
2019-02-16 02:00 | 657 | 638
2019-02-16 02:30 | 647 | 628
2019-02-16 03:00 | 642 | 621
2019-02-16 03:30 | 638 | 616
2019-02-16 04:00 | 638 | 615
2019-02-16 04:30 | 637 | 614
2019-02-16 05:00 | 638 | 615
2019-02-16 05:30 | 648 | 626
2019-02-16 06:00 | 654 | 631
2019-02-16 06:30 | 671 | 652
2019-02-16 07:00 | 687 | 673
2019-02-16 07:30 | 706 | 698
2019-02-16 08:00 | 723 | 720
2019-02-16 08:30 | 736 | 735
2019-02-16 09:00 | 743 | 742
2019-02-16 09:30 | 751 | 750
2019-02-16 10:00 | 769 | 769
2019-02-16 10:30 | 785 | 784
2019-02-16 11:00 | 766 | 765
2019-02-16 11:30 | 777 | 777
2019-02-16 12:00 | 797 | 797
2019-02-16 12:30 | 806 | 806
2019-02-16 13:00 | 805 | 804
2019-02-16 13:30 | 814 | 814
2019-02-16 14:00 | 833 | 833
2019-02-16 14:30 | 835 | 835
2019-02-16 15:00 | 860 | 860
2019-02-16 15:30 | 854 | 854
2019-02-16 16:00 | 870 | 870
2019-02-16 16:30 | 898 | 898
2019-02-16 17:00 | 928 | 928
2019-02-16 17:30 | 948 | 948
2019-02-16 18:00 | 948 | 948
2019-02-16 18:30 | 958 | 957
2019-02-16 19:00 | 977 | 977
2019-02-16 19:30 | 979 | 979
2019-02-16 20:00 | 968 | 968
2019-02-16 20:30 | 953 | 951
2019-02-16 21:00 | 920 | 918
2019-02-16 21:30 | 870 | 870
2019-02-16 22:00 | 840 | 839
2019-02-16 22:30 | 827 | 825
2019-02-16 23:00 | 811 | 809
2019-02-16 23:30 | 764 | 758
2019-02-17 | 723 | 713
2019-02-17 00:30 | 681 | 665
2019-02-17 01:00 | 661 | 641
2019-02-17 01:30 | 653 | 632
2019-02-17 02:00 | 637 | 613
2019-02-17 02:30 | 629 | 604
2019-02-17 03:00 | 622 | 596
2019-02-17 03:30 | 623 | 596
2019-02-17 04:00 | 621 | 593
2019-02-17 04:30 | 617 | 587
2019-02-17 05:00 | 621 | 591
2019-02-17 05:30 | 623 | 594
2019-02-17 06:00 | 630 | 597
2019-02-17 06:30 | 634 | 606
2019-02-17 07:00 | 637 | 612
2019-02-17 07:30 | 647 | 630
2019-02-17 08:00 | 654 | 643
2019-02-17 08:30 | 658 | 652
2019-02-17 09:00 | 672 | 668
2019-02-17 09:30 | 690 | 689
2019-02-17 10:00 | 703 | 703
2019-02-17 10:30 | 710 | 710
2019-02-17 11:00 | 712 | 712
2019-02-17 11:30 | 716 | 715
2019-02-17 12:00 | 717 | 717
2019-02-17 12:30 | 714 | 714
2019-02-17 13:00 | 720 | 720
2019-02-17 13:30 | 732 | 732
2019-02-17 14:00 | 753 | 752
2019-02-17 14:30 | 773 | 773
2019-02-17 15:00 | 803 | 803
2019-02-17 15:30 | 841 | 841
2019-02-17 16:00 | 888 | 887
2019-02-17 16:30 | 927 | 926
2019-02-17 17:00 | 964 | 964
2019-02-17 17:30 | 992 | 992
2019-02-17 18:00 | 1000 | 1000
2019-02-17 18:30 | 1002 | 1001
2019-02-17 19:00 | 1020 | 1020
2019-02-17 19:30 | 1019 | 1019
2019-02-17 20:00 | 1004 | 1003
2019-02-17 20:30 | 987 | 985
2019-02-17 21:00 | 933 | 930
2019-02-17 21:30 | 891 | 889
2019-02-17 22:00 | 858 | 857
2019-02-17 22:30 | 830 | 829
2019-02-17 23:00 | 803 | 800
2019-02-17 23:30 | 760 | 754
2019-02-18 | 711 | 700
2019-02-18 00:30 | 675 | 659
2019-02-18 01:00 | 654 | 636
2019-02-18 01:30 | 647 | 627
2019-02-18 02:00 | 635 | 613
2019-02-18 02:30 | 631 | 608
2019-02-18 03:00 | 628 | 604
2019-02-18 03:30 | 629 | 604
2019-02-18 04:00 | 628 | 603
2019-02-18 04:30 | 637 | 615
2019-02-18 05:00 | 648 | 629
2019-02-18 05:30 | 678 | 664
2019-02-18 06:00 | 709 | 699
2019-02-18 06:30 | 765 | 762
2019-02-18 07:00 | 811 | 808
2019-02-18 07:30 | 870 | 870
2019-02-18 08:00 | 871 | 871
2019-02-18 08:30 | 875 | 874
2019-02-18 09:00 | 920 | 920
2019-02-18 09:30 | 962 | 962
2019-02-18 10:00 | 967 | 966
2019-02-18 10:30 | 963 | 962
2019-02-18 11:00 | 931 | 930
2019-02-18 11:30 | 916 | 915
2019-02-18 12:00 | 913 | 912
2019-02-18 12:30 | 925 | 924
2019-02-18 13:00 | 930 | 930
2019-02-18 13:30 | 974 | 974
2019-02-18 14:00 | 1001 | 1001
2019-02-18 14:30 | 1027 | 1026
2019-02-18 15:00 | 1053 | 1050
2019-02-18 15:30 | 1080 | 1078
2019-02-18 16:00 | 1126 | 1125
2019-02-18 16:30 | 1172 | 1171
2019-02-18 17:00 | 1201 | 1200
2019-02-18 17:30 | 1214 | 1213
2019-02-18 18:00 | 1203 | 1198
2019-02-18 18:30 | 1177 | 1170
2019-02-18 19:00 | 1186 | 1182
2019-02-18 19:30 | 1177 | 1172
2019-02-18 20:00 | 1153 | 1149
2019-02-18 20:30 | 1114 | 1112
2019-02-18 21:00 | 1048 | 1048
2019-02-18 21:30 | 998 | 997
2019-02-18 22:00 | 949 | 948
2019-02-18 22:30 | 906 | 905
2019-02-18 23:00 | 852 | 852
2019-02-18 23:30 | 797 | 796
2019-02-19 | 746 | 743
2019-02-19 00:30 | 701 | 694
2019-02-19 01:00 | 681 | 671
2019-02-19 01:30 | 671 | 658
2019-02-19 02:00 | 662 | 649
2019-02-19 02:30 | 653 | 637
2019-02-19 03:00 | 645 | 629
2019-02-19 03:30 | 642 | 626
2019-02-19 04:00 | 645 | 627
2019-02-19 04:30 | 652 | 636
2019-02-19 05:00 | 667 | 654
2019-02-19 05:30 | 702 | 688
2019-02-19 06:00 | 714 | 703
2019-02-19 06:30 | 762 | 760
2019-02-19 07:00 | 806 | 806
2019-02-19 07:30 | 859 | 859
2019-02-19 08:00 | 871 | 870
2019-02-19 08:30 | 874 | 874
2019-02-19 09:00 | 879 | 879
2019-02-19 09:30 | 893 | 893
2019-02-19 10:00 | 907 | 907
2019-02-19 10:30 | 916 | 916
2019-02-19 11:00 | 935 | 935
2019-02-19 11:30 | 942 | 942
2019-02-19 12:00 | 964 | 964
2019-02-19 12:30 | 1003 | 1003
2019-02-19 13:00 | 1030 | 1029
2019-02-19 13:30 | 1043 | 1041
2019-02-19 14:00 | 1076 | 1075
2019-02-19 14:30 | 1117 | 1117
2019-02-19 15:00 | 1152 | 1151
2019-02-19 15:30 | 1186 | 1185
2019-02-19 16:00 | 1246 | 1246
2019-02-19 16:30 | 1303 | 1303
2019-02-19 17:00 | 1331 | 1331
2019-02-19 17:30 | 1332 | 1332
2019-02-19 18:00 | 1306 | 1303
2019-02-19 18:30 | 1276 | 1273
2019-02-19 19:00 | 1278 | 1275
2019-02-19 19:30 | 1273 | 1270
2019-02-19 20:00 | 1258 | 1254
2019-02-19 20:30 | 1214 | 1211
2019-02-19 21:00 | 1146 | 1143
2019-02-19 21:30 | 1087 | 1084
2019-02-19 22:00 | 1029 | 1027
2019-02-19 22:30 | 983 | 981
2019-02-19 23:00 | 936 | 935
2019-02-19 23:30 | 864 | 861
2019-02-20 | 807 | 801
2019-02-20 00:30 | 758 | 747
2019-02-20 01:00 | 735 | 720
2019-02-20 01:30 | 718 | 701
2019-02-20 02:00 | 698 | 687
2019-02-20 02:30 | 688 | 679
2019-02-20 03:00 | 682 | 672
2019-02-20 03:30 | 684 | 674
2019-02-20 04:00 | 682 | 672
2019-02-20 04:30 | 689 | 680
2019-02-20 05:00 | 704 | 697
2019-02-20 05:30 | 738 | 735
2019-02-20 06:00 | 773 | 771
2019-02-20 06:30 | 842 | 842
2019-02-20 07:00 | 901 | 901
2019-02-20 07:30 | 982 | 982
2019-02-20 08:00 | 1023 | 1023
2019-02-20 08:30 | 1049 | 1049
2019-02-20 09:00 | 1054 | 1054
2019-02-20 09:30 | 1056 | 1055
2019-02-20 10:00 | 1052 | 1051
2019-02-20 10:30 | 1056 | 1053
2019-02-20 11:00 | 1074 | 1072
2019-02-20 11:30 | 1076 | 1075
2019-02-20 12:00 | 1093 | 1092
2019-02-20 12:30 | 1099 | 1097
2019-02-20 13:00 | 1101 | 1099
2019-02-20 13:30 | 1123 | 1123
2019-02-20 14:00 | 1153 | 1153
2019-02-20 14:30 | 1179 | 1179
2019-02-20 15:00 | 1203 | 1202
2019-02-20 15:30 | 1235 | 1235
2019-02-20 16:00 | 1284 | 1284
2019-02-20 16:30 | 1323 | 1323
2019-02-20 17:00 | 1350 | 1350
2019-02-20 17:30 | 1353 | 1353
2019-02-20 18:00 | 1328 | 1326
2019-02-20 18:30 | 1295 | 1293
2019-02-20 19:00 | 1313 | 1312
2019-02-20 19:30 | 1305 | 1304
2019-02-20 20:00 | 1292 | 1289
2019-02-20 20:30 | 1260 | 1254
2019-02-20 21:00 | 1207 | 1204
2019-02-20 21:30 | 1147 | 1142
2019-02-20 22:00 | 1087 | 1084
2019-02-20 22:30 | 1036 | 1033
2019-02-20 23:00 | 988 | 985
2019-02-20 23:30 | 916 | 909
2019-02-21 | 853 | 846
2019-02-21 00:30 | 804 | 794
2019-02-21 01:00 | 772 | 768
2019-02-21 01:30 | 752 | 749
2019-02-21 02:00 | 735 | 731
2019-02-21 02:30 | 731 | 725
2019-02-21 03:00 | 722 | 715
2019-02-21 03:30 | 722 | 715
2019-02-21 04:00 | 718 | 711
2019-02-21 04:30 | 726 | 719
2019-02-21 05:00 | 739 | 734
2019-02-21 05:30 | 773 | 771
2019-02-21 06:00 | 801 | 800
2019-02-21 06:30 | 872 | 871
2019-02-21 07:00 | 928 | 928
2019-02-21 07:30 | 1016 | 1016
2019-02-21 08:00 | 1050 | 1050
2019-02-21 08:30 | 1081 | 1081
2019-02-21 09:00 | 1101 | 1101
2019-02-21 09:30 | 1113 | 1113
2019-02-21 10:00 | 1118 | 1118
2019-02-21 10:30 | 1114 | 1114
2019-02-21 11:00 | 1129 | 1129
2019-02-21 11:30 | 1124 | 1124
2019-02-21 12:00 | 1139 | 1139
2019-02-21 12:30 | 1108 | 1108
2019-02-21 13:00 | 1131 | 1131
2019-02-21 13:30 | 1148 | 1147
2019-02-21 14:00 | 1149 | 1148
2019-02-21 14:30 | 1154 | 1154
2019-02-21 15:00 | 1159 | 1159
2019-02-21 15:30 | 1197 | 1197
2019-02-21 16:00 | 1256 | 1256
2019-02-21 16:30 | 1294 | 1294
2019-02-21 17:00 | 1316 | 1316
2019-02-21 17:30 | 1316 | 1316
2019-02-21 18:00 | 1304 | 1303
2019-02-21 18:30 | 1278 | 1275
2019-02-21 19:00 | 1297 | 1294
2019-02-21 19:30 | 1281 | 1275
2019-02-21 20:00 | 1259 | 1251
2019-02-21 20:30 | 1216 | 1211
2019-02-21 21:00 | 1154 | 1151
2019-02-21 21:30 | 1089 | 1082
2019-02-21 22:00 | 1031 | 1026
2019-02-21 22:30 | 993 | 988
2019-02-21 23:00 | 951 | 944
2019-02-21 23:30 | 870 | 865
2019-02-22 | 819 | 813
2019-02-22 00:30 | 768 | 764
2019-02-22 01:00 | 741 | 737
2019-02-22 01:30 | 725 | 719
2019-02-22 02:00 | 708 | 701
2019-02-22 02:30 | 699 | 691
2019-02-22 03:00 | 692 | 682
2019-02-22 03:30 | 688 | 678
2019-02-22 04:00 | 690 | 679
2019-02-22 04:30 | 694 | 684
2019-02-22 05:00 | 707 | 698
2019-02-22 05:30 | 741 | 736
2019-02-22 06:00 | 764 | 760
2019-02-22 06:30 | 825 | 824
2019-02-22 07:00 | 867 | 866
2019-02-22 07:30 | 935 | 935
2019-02-22 08:00 | 961 | 961
2019-02-22 08:30 | 961 | 961
2019-02-22 09:00 | 964 | 964
2019-02-22 09:30 | 969 | 969
2019-02-22 10:00 | 976 | 976
2019-02-22 10:30 | 952 | 952
2019-02-22 11:00 | 924 | 924
2019-02-22 11:30 | 929 | 929
2019-02-22 12:00 | 961 | 960
2019-02-22 12:30 | 1001 | 1001
2019-02-22 13:00 | 1001 | 1001
2019-02-22 13:30 | 947 | 946
2019-02-22 14:00 | 922 | 920
2019-02-22 14:30 | 938 | 935
2019-02-22 15:00 | 956 | 954
2019-02-22 15:30 | 1003 | 1002
2019-02-22 16:00 | 1037 | 1037
2019-02-22 16:30 | 1047 | 1046
2019-02-22 17:00 | 1082 | 1081
2019-02-22 17:30 | 1079 | 1076
2019-02-22 18:00 | 1055 | 1051
2019-02-22 18:30 | 1031 | 1023
2019-02-22 19:00 | 1046 | 1040
2019-02-22 19:30 | 1035 | 1028
2019-02-22 20:00 | 1016 | 1011
2019-02-22 20:30 | 989 | 988
2019-02-22 21:00 | 951 | 950
2019-02-22 21:30 | 906 | 906
2019-02-22 22:00 | 875 | 874
2019-02-22 22:30 | 848 | 847
2019-02-22 23:00 | 821 | 819
2019-02-22 23:30 | 766 | 762
2019-02-23 | 714 | 705
2019-02-23 00:30 | 671 | 658
2019-02-23 01:00 | 652 | 635
2019-02-23 01:30 | 636 | 617
2019-02-23 02:00 | 622 | 602
2019-02-23 02:30 | 619 | 597
2019-02-23 03:00 | 614 | 590
2019-02-23 03:30 | 612 | 588
2019-02-23 04:00 | 612 | 588
2019-02-23 04:30 | 608 | 582
2019-02-23 05:00 | 615 | 590
2019-02-23 05:30 | 627 | 605
2019-02-23 06:00 | 628 | 604
2019-02-23 06:30 | 644 | 626
2019-02-23 07:00 | 661 | 647
2019-02-23 07:30 | 673 | 666
2019-02-23 08:00 | 677 | 673
2019-02-23 08:30 | 690 | 687
2019-02-23 09:00 | 702 | 701
2019-02-23 09:30 | 720 | 720
2019-02-23 10:00 | 722 | 722
2019-02-23 10:30 | 720 | 720
2019-02-23 11:00 | 709 | 705
2019-02-23 11:30 | 713 | 710
2019-02-23 12:00 | 717 | 713
2019-02-23 12:30 | 720 | 717
2019-02-23 13:00 | 737 | 734
2019-02-23 13:30 | 748 | 745
2019-02-23 14:00 | 753 | 750
2019-02-23 14:30 | 766 | 763
2019-02-23 15:00 | 798 | 796
2019-02-23 15:30 | 793 | 790
2019-02-23 16:00 | 828 | 827
2019-02-23 16:30 | 854 | 853
2019-02-23 17:00 | 885 | 884
2019-02-23 17:30 | 900 | 899
2019-02-23 18:00 | 909 | 907
2019-02-23 18:30 | 907 | 905
2019-02-23 19:00 | 933 | 932
2019-02-23 19:30 | 921 | 920
2019-02-23 20:00 | 910 | 907
2019-02-23 20:30 | 886 | 885
2019-02-23 21:00 | 854 | 853
2019-02-23 21:30 | 827 | 826
2019-02-23 22:00 | 806 | 804
2019-02-23 22:30 | 791 | 787
2019-02-23 23:00 | 790 | 785
2019-02-23 23:30 | 748 | 739
2019-02-24 | 707 | 693
2019-02-24 00:30 | 672 | 652
2019-02-24 01:00 | 651 | 629
2019-02-24 01:30 | 641 | 617
2019-02-24 02:00 | 629 | 603
2019-02-24 02:30 | 623 | 596
2019-02-24 03:00 | 613 | 585
2019-02-24 03:30 | 614 | 586
2019-02-24 04:00 | 607 | 577
2019-02-24 04:30 | 611 | 580
2019-02-24 05:00 | 608 | 578
2019-02-24 05:30 | 621 | 592
2019-02-24 06:00 | 627 | 595
2019-02-24 06:30 | 636 | 606
2019-02-24 07:00 | 641 | 614
2019-02-24 07:30 | 652 | 634
2019-02-24 08:00 | 658 | 647
2019-02-24 08:30 | 668 | 661
2019-02-24 09:00 | 689 | 685
2019-02-24 09:30 | 716 | 714
2019-02-24 10:00 | 724 | 723
2019-02-24 10:30 | 720 | 720
2019-02-24 11:00 | 721 | 721
2019-02-24 11:30 | 718 | 717
2019-02-24 12:00 | 708 | 707
2019-02-24 12:30 | 676 | 676
2019-02-24 13:00 | 685 | 685
2019-02-24 13:30 | 677 | 676
2019-02-24 14:00 | 695 | 695
2019-02-24 14:30 | 726 | 725
2019-02-24 15:00 | 733 | 733
2019-02-24 15:30 | 755 | 755
2019-02-24 16:00 | 793 | 793
2019-02-24 16:30 | 830 | 830
2019-02-24 17:00 | 862 | 862
2019-02-24 17:30 | 898 | 896
2019-02-24 18:00 | 920 | 918
2019-02-24 18:30 | 941 | 939
2019-02-24 19:00 | 964 | 963
2019-02-24 19:30 | 955 | 954
2019-02-24 20:00 | 931 | 929
2019-02-24 20:30 | 912 | 909
2019-02-24 21:00 | 872 | 870
2019-02-24 21:30 | 833 | 829
2019-02-24 22:00 | 802 | 798
2019-02-24 22:30 | 787 | 783
2019-02-24 23:00 | 780 | 776
2019-02-24 23:30 | 743 | 735
2019-02-25 | 692 | 678
2019-02-25 00:30 | 657 | 637
2019-02-25 01:00 | 639 | 616
2019-02-25 01:30 | 628 | 605
2019-02-25 02:00 | 624 | 599
2019-02-25 02:30 | 619 | 594
2019-02-25 03:00 | 616 | 590
2019-02-25 03:30 | 618 | 593
2019-02-25 04:00 | 623 | 598
2019-02-25 04:30 | 628 | 605
2019-02-25 05:00 | 640 | 620
2019-02-25 05:30 | 672 | 658
2019-02-25 06:00 | 702 | 693
2019-02-25 06:30 | 762 | 759
2019-02-25 07:00 | 802 | 801
2019-02-25 07:30 | 874 | 874
2019-02-25 08:00 | 897 | 896
2019-02-25 08:30 | 916 | 916
2019-02-25 09:00 | 909 | 909
2019-02-25 09:30 | 906 | 905
2019-02-25 10:00 | 895 | 895
2019-02-25 10:30 | 891 | 890
2019-02-25 11:00 | 882 | 882
2019-02-25 11:30 | 873 | 873
2019-02-25 12:00 | 863 | 862
2019-02-25 12:30 | 895 | 895
2019-02-25 13:00 | 881 | 881
2019-02-25 13:30 | 901 | 901
2019-02-25 14:00 | 899 | 899
2019-02-25 14:30 | 924 | 924
2019-02-25 15:00 | 921 | 921
2019-02-25 15:30 | 935 | 935
2019-02-25 16:00 | 934 | 933
2019-02-25 16:30 | 975 | 974
2019-02-25 17:00 | 1000 | 999
2019-02-25 17:30 | 1006 | 1005
2019-02-25 18:00 | 1007 | 1004
2019-02-25 18:30 | 1006 | 1002
2019-02-25 19:00 | 1026 | 1025
2019-02-25 19:30 | 1007 | 1005
2019-02-25 20:00 | 995 | 993
2019-02-25 20:30 | 970 | 969
2019-02-25 21:00 | 933 | 933
2019-02-25 21:30 | 895 | 895
2019-02-25 22:00 | 860 | 860
2019-02-25 22:30 | 840 | 839
2019-02-25 23:00 | 813 | 810
2019-02-25 23:30 | 761 | 756
2019-02-26 | 715 | 704
2019-02-26 00:30 | 677 | 663
2019-02-26 01:00 | 655 | 638
2019-02-26 01:30 | 642 | 623
2019-02-26 02:00 | 633 | 611
2019-02-26 02:30 | 628 | 606
2019-02-26 03:00 | 628 | 605
2019-02-26 03:30 | 625 | 601
2019-02-26 04:00 | 629 | 605
2019-02-26 04:30 | 634 | 612
2019-02-26 05:00 | 645 | 626
2019-02-26 05:30 | 676 | 665
2019-02-26 06:00 | 701 | 692
2019-02-26 06:30 | 763 | 755
2019-02-26 07:00 | 812 | 803
2019-02-26 07:30 | 875 | 870
2019-02-26 08:00 | 897 | 888
2019-02-26 08:30 | 903 | 897
2019-02-26 09:00 | 900 | 896
2019-02-26 09:30 | 861 | 857
2019-02-26 10:00 | 878 | 875
2019-02-26 10:30 | 876 | 876
2019-02-26 11:00 | 869 | 869
2019-02-26 11:30 | 862 | 862
2019-02-26 12:00 | 869 | 869
2019-02-26 12:30 | 861 | 861
2019-02-26 13:00 | 864 | 864
2019-02-26 13:30 | 867 | 867
2019-02-26 14:00 | 879 | 878
2019-02-26 14:30 | 887 | 887
2019-02-26 15:00 | 900 | 900
2019-02-26 15:30 | 911 | 911
2019-02-26 16:00 | 930 | 930
2019-02-26 16:30 | 957 | 956
2019-02-26 17:00 | 982 | 982
2019-02-26 17:30 | 1005 | 1004
2019-02-26 18:00 | 995 | 993
2019-02-26 18:30 | 998 | 993
2019-02-26 19:00 | 1031 | 1029
2019-02-26 19:30 | 1020 | 1018
2019-02-26 20:00 | 1001 | 996
2019-02-26 20:30 | 973 | 972
2019-02-26 21:00 | 936 | 934
2019-02-26 21:30 | 893 | 891
2019-02-26 22:00 | 872 | 869
2019-02-26 22:30 | 843 | 837
2019-02-26 23:00 | 815 | 806
2019-02-26 23:30 | 765 | 752
2019-02-27 | 718 | 701
2019-02-27 00:30 | 679 | 659
2019-02-27 01:00 | 650 | 629
2019-02-27 01:30 | 640 | 617
2019-02-27 02:00 | 630 | 605
2019-02-27 02:30 | 622 | 595
2019-02-27 03:00 | 624 | 597
2019-02-27 03:30 | 623 | 595
2019-02-27 04:00 | 628 | 602
2019-02-27 04:30 | 635 | 612
2019-02-27 05:00 | 651 | 632
2019-02-27 05:30 | 683 | 670
2019-02-27 06:00 | 709 | 700
2019-02-27 06:30 | 760 | 757
2019-02-27 07:00 | 800 | 800
2019-02-27 07:30 | 853 | 853
2019-02-27 08:00 | 875 | 875
2019-02-27 08:30 | 881 | 881
2019-02-27 09:00 | 889 | 889
2019-02-27 09:30 | 878 | 878
2019-02-27 10:00 | 895 | 893
2019-02-27 10:30 | 903 | 900
2019-02-27 11:00 | 902 | 902
2019-02-27 11:30 | 917 | 917
2019-02-27 12:00 | 923 | 923
2019-02-27 12:30 | 898 | 898
2019-02-27 13:00 | 890 | 890
2019-02-27 13:30 | 892 | 891
2019-02-27 14:00 | 905 | 905
2019-02-27 14:30 | 928 | 928
2019-02-27 15:00 | 920 | 920
2019-02-27 15:30 | 925 | 925
2019-02-27 16:00 | 942 | 942
2019-02-27 16:30 | 961 | 960
2019-02-27 17:00 | 984 | 983
2019-02-27 17:30 | 996 | 995
2019-02-27 18:00 | 991 | 988
2019-02-27 18:30 | 985 | 982
2019-02-27 19:00 | 1010 | 1010
2019-02-27 19:30 | 997 | 996
2019-02-27 20:00 | 985 | 984
2019-02-27 20:30 | 964 | 963
2019-02-27 21:00 | 923 | 922
2019-02-27 21:30 | 894 | 892
2019-02-27 22:00 | 863 | 860
2019-02-27 22:30 | 839 | 833
2019-02-27 23:00 | 813 | 804
2019-02-27 23:30 | 764 | 752
2019-02-28 | 709 | 698
2019-02-28 00:30 | 668 | 653
2019-02-28 01:00 | 647 | 628
2019-02-28 01:30 | 627 | 607
2019-02-28 02:00 | 614 | 591
2019-02-28 02:30 | 609 | 584
2019-02-28 03:00 | 604 | 578
2019-02-28 03:30 | 607 | 580
2019-02-28 04:00 | 610 | 584
2019-02-28 04:30 | 626 | 604
2019-02-28 05:00 | 642 | 623
2019-02-28 05:30 | 676 | 665
2019-02-28 06:00 | 704 | 696
2019-02-28 06:30 | 764 | 763
2019-02-28 07:00 | 806 | 805
2019-02-28 07:30 | 880 | 880
2019-02-28 08:00 | 909 | 909
2019-02-28 08:30 | 917 | 916
2019-02-28 09:00 | 912 | 912
2019-02-28 09:30 | 909 | 909
2019-02-28 10:00 | 897 | 896
2019-02-28 10:30 | 873 | 872
2019-02-28 11:00 | 878 | 877
2019-02-28 11:30 | 848 | 846
2019-02-28 12:00 | 842 | 840
2019-02-28 12:30 | 828 | 826
2019-02-28 13:00 | 843 | 841
2019-02-28 13:30 | 855 | 854
2019-02-28 14:00 | 868 | 867
2019-02-28 14:30 | 886 | 885
2019-02-28 15:00 | 924 | 924
2019-02-28 15:30 | 905 | 904
2019-02-28 16:00 | 922 | 920
2019-02-28 16:30 | 948 | 946
2019-02-28 17:00 | 976 | 974
2019-02-28 17:30 | 985 | 983
2019-02-28 18:00 | 996 | 996
2019-02-28 18:30 | 1007 | 1007
2019-02-28 19:00 | 1037 | 1037
2019-02-28 19:30 | 1026 | 1026
2019-02-28 20:00 | 1012 | 1012
2019-02-28 20:30 | 985 | 985
2019-02-28 21:00 | 949 | 949
2019-02-28 21:30 | 902 | 902
2019-02-28 22:00 | 862 | 860
2019-02-28 22:30 | 845 | 842
2019-02-28 23:00 | 816 | 812
2019-02-28 23:30 | 763 | 760
2019-03-01 | 722 | 716

## 24. Historic ratings
|  | 2016 Winter | 2016/17 Summer | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer
PQ Rating (MVA) |  | 3802 | 3393 | 3802 | 3407 | 3828 | 3407
Feeders | 8822 | 931 | 852 | 931 | 857 | 945 | 857
| 8813 | 957 | 847 | 957 | 850 | 961 | 850
| 8825 | 957 | 847 | 957 | 850 | 961 | 850
| 8824 | 957 | 847 | 957 | 850 | 961 | 850

## 26. Unplanned outages
Unplanned Outage Date/Time | Element Affected | Element Type | Outage Cause | Outage Duration (mins) | Customer Outage Duration (mins) | MW Lost (Instantaneous) | MW Minutes
42394.7243 | 8848 - H014 Middle Ridge to S003 Greenbank | FEEDER | Storm | 0.083333 | - | - | -
42448.6502 | 8825 - S003 Greenbank to H031 Molendinar | FEEDER | Storm | 0.16667 | - | - | -
42452.5992 | 8822 - S003 Greenbank to H003 Belmont | FEEDER | HV Maint | 252.9167 | - | - | -
42499.3761 | S003 275KV 11 SVC | STATIC VAR COMPENSATOR | SVC Equipment malfunction or failure | 3243.7 | - | - | -
42797.475 | 0835 - S003 Greenbank to H004 Mudgeeraba | FEEDER | HV Maint | 192.5833 | - | - | -
42931.7365 | S003 275KV 11 SVC | STATIC VAR COMPENSATOR | SVC Equipment malfunction or failure | 5680.2167 | - | - | -
43031.0539 | 8849 - H014 Middle Ridge to S003 Greenbank | FEEDER | Storm | 0.083333 | - | - | -
43155.2887 | S003 275KV 11 SVC | STATIC VAR COMPENSATOR | SVC Equipment malfunction or failure | 618.1 | - | - | -
43184.5815 | S003 275KV 11 SVC | STATIC VAR COMPENSATOR | HV Equipment malfunction or failure | 4234.8167 | - | - | -
43187.6169 | S003 275KV 11 SVC | STATIC VAR COMPENSATOR | SVC Equipment malfunction or failure | 1245.5333 | - | - | -
43230.3107 | 8813 - H022 Loganlea to S003 Greenbank | FEEDER | HV Maint | 423.1 | - | - | -
43242.5694 | S003 275KV 11 SVC | STATIC VAR COMPENSATOR | HV Equipment malfunction or failure | 1406.6333 | - | - | -