## Cover Page
AER Rule | Field Name | Value(s)
1 | Transmission line ID | 275kV F8857, F8858 from H035 Strathmore to H013 Ross
2 | Constraint primary driver | Asset condition
3 | Location of constraint (start, decimal degrees, latitude and longitude) | -20.499 | 147.775
4 | Location of constraint (end, decimal degrees, latitude and longitude) | -19.404 | 146.726
Financial year
|  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
5 | Forecast asset rating (MVA) | 1292 | 1292 | 1292 | 1292 | 1292 | 1292 | 1292 | 1292 | 1292 | 1292 | 1292
6 | Forecast maximum demand 10% PoE (MVA) | 395.14 | 398.61 | 404.92 | 398.75 | 399.94 | 398.62 | 399.84 | 398.7 | 399.26 | 403.83 | 403.65
| Forecast maximum demand 50% PoE (MVA) | 354.65 | 357.46 | 358.57 | 355.7 | 357.78 | 368.51 | 368.15 | 367.75 | 365.99 | 368.92 | 373.41
7 | Voltage Level (kV) | Financial year 2020: 275
Financial year
|  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
8 | Maximum load at risk (MVA) | 0 | 0 | 0 | 0 | 268.9816 | 266.9177 | 275.2157 | 270.3123 | 273.8187 | 277.3375 | 280.8828
| Maximum load at risk (MW) | 0 | 0 | 0 | 0 | 242.0835 | 240.2259 | 247.6941 | 243.2811 | 246.4368 | 249.6038 | 252.7945
9 | Energy at risk (MWh) | 0 | 0 | 0 | 0 | 4.219 | 4.156 | 4.1041 | 4.0217 | 3.9653 | 3.9217 | 3.8806
10 | Preferred investment | Financial year 2020: Line refit works on the 275kV transmission line between Strathmore and Ross Substations
Financial year
|  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
11 | Capital cost ($m, nominal) | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0
12 | Operating cost ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
13 | Preferred investment cost accuracy | Financial year 2020: 0.3
14 | Preferred investment proposed timing | Financial year 2020: 2024-06-30
Financial year
|  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
15 | Demand reduction to defer by 1 year (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Annual deferall value ($m, nominal) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Historic load trace
18 | Historic line rating
Financial year
|  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
19 | Annual economic cost of constraint ($m, nominal) | 0 | 0 | 0 | 0 | 0.16754 | 0.16503 | 0.16297 | 0.1597 | 0.15746 | 0.15573 | 0.1541
20 | VCR ($m/MWh) | Financial year 2020: 0.03971
21 | Annual constraint duration
22 | Constraint duration on peak demand day

## 17. Historic load trace
Date/Time | Load (MVA) | Load (MW) | Load switching affected?
2016-03-01 00:30 | 307 | 303
2016-03-01 01:00 | 300 | 296
2016-03-01 01:30 | 293 | 288
2016-03-01 02:00 | 283 | 278
2016-03-01 02:30 | 278 | 273
2016-03-01 03:00 | 278 | 272
2016-03-01 03:30 | 278 | 272
2016-03-01 04:00 | 278 | 272
2016-03-01 04:30 | 276 | 271
2016-03-01 05:00 | 271 | 266
2016-03-01 05:30 | 273 | 268
2016-03-01 06:00 | 282 | 277
2016-03-01 06:30 | 283 | 278
2016-03-01 07:00 | 291 | 286
2016-03-01 07:30 | 324 | 320
2016-03-01 08:00 | 334 | 330
2016-03-01 08:30 | 333 | 329
2016-03-01 09:00 | 334 | 330
2016-03-01 09:30 | 327 | 322
2016-03-01 10:00 | 313 | 308
2016-03-01 10:30 | 315 | 310
2016-03-01 11:00 | 318 | 313
2016-03-01 11:30 | 321 | 316
2016-03-01 12:00 | 326 | 321
2016-03-01 12:30 | 321 | 316
2016-03-01 13:00 | 338 | 333
2016-03-01 13:30 | 351 | 347
2016-03-01 14:00 | 367 | 363
2016-03-01 14:30 | 345 | 339
2016-03-01 15:00 | 373 | 368
2016-03-01 15:30 | 379 | 374
2016-03-01 16:00 | 365 | 360
2016-03-01 16:30 | 399 | 395
2016-03-01 17:00 | 398 | 394
2016-03-01 17:30 | 401 | 397
2016-03-01 18:00 | 402 | 398
2016-03-01 18:30 | 404 | 400
2016-03-01 19:00 | 383 | 379
2016-03-01 19:30 | 394 | 391
2016-03-01 20:00 | 414 | 411
2016-03-01 20:30 | 405 | 401
2016-03-01 21:00 | 394 | 389
2016-03-01 21:30 | 378 | 374
2016-03-01 22:00 | 362 | 357
2016-03-01 22:30 | 325 | 320
2016-03-01 23:00 | 310 | 304
2016-03-01 23:30 | 309 | 304
2016-03-02 | 298 | 293
2016-03-02 00:30 | 290 | 285
2016-03-02 01:00 | 286 | 280
2016-03-02 01:30 | 280 | 275
2016-03-02 02:00 | 277 | 272
2016-03-02 02:30 | 272 | 266
2016-03-02 03:00 | 269 | 263
2016-03-02 03:30 | 267 | 261
2016-03-02 04:00 | 264 | 258
2016-03-02 04:30 | 262 | 256
2016-03-02 05:00 | 263 | 258
2016-03-02 05:30 | 269 | 263
2016-03-02 06:00 | 275 | 270
2016-03-02 06:30 | 275 | 270
2016-03-02 07:00 | 289 | 284
2016-03-02 07:30 | 318 | 314
2016-03-02 08:00 | 330 | 325
2016-03-02 08:30 | 335 | 330
2016-03-02 09:00 | 346 | 341
2016-03-02 09:30 | 340 | 335
2016-03-02 10:00 | 329 | 325
2016-03-02 10:30 | 334 | 330
2016-03-02 11:00 | 337 | 333
2016-03-02 11:30 | 344 | 339
2016-03-02 12:00 | 353 | 349
2016-03-02 12:30 | 366 | 360
2016-03-02 13:00 | 321 | 315
2016-03-02 13:30 | 287 | 283
2016-03-02 14:00 | 305 | 301
2016-03-02 14:30 | 305 | 301
2016-03-02 15:00 | 306 | 302
2016-03-02 15:30 | 310 | 306
2016-03-02 16:00 | 318 | 314
2016-03-02 16:30 | 320 | 315
2016-03-02 17:00 | 320 | 315
2016-03-02 17:30 | 316 | 311
2016-03-02 18:00 | 313 | 308
2016-03-02 18:30 | 325 | 320
2016-03-02 19:00 | 316 | 311
2016-03-02 19:30 | 297 | 293
2016-03-02 20:00 | 288 | 284
2016-03-02 20:30 | 319 | 315
2016-03-02 21:00 | 314 | 310
2016-03-02 21:30 | 302 | 297
2016-03-02 22:00 | 346 | 343
2016-03-02 22:30 | 345 | 341
2016-03-02 23:00 | 328 | 324
2016-03-02 23:30 | 315 | 311
2016-03-03 | 307 | 303
2016-03-03 00:30 | 299 | 295
2016-03-03 01:00 | 286 | 282
2016-03-03 01:30 | 278 | 274
2016-03-03 02:00 | 274 | 270
2016-03-03 02:30 | 273 | 268
2016-03-03 03:00 | 271 | 267
2016-03-03 03:30 | 269 | 265
2016-03-03 04:00 | 269 | 265
2016-03-03 04:30 | 269 | 265
2016-03-03 05:00 | 271 | 267
2016-03-03 05:30 | 276 | 272
2016-03-03 06:00 | 283 | 279
2016-03-03 06:30 | 299 | 295
2016-03-03 07:00 | 314 | 310
2016-03-03 07:30 | 332 | 328
2016-03-03 08:00 | 343 | 339
2016-03-03 08:30 | 348 | 344
2016-03-03 09:00 | 350 | 346
2016-03-03 09:30 | 348 | 344
2016-03-03 10:00 | 339 | 335
2016-03-03 10:30 | 344 | 340
2016-03-03 11:00 | 341 | 337
2016-03-03 11:30 | 332 | 327
2016-03-03 12:00 | 320 | 316
2016-03-03 12:30 | 321 | 316
2016-03-03 13:00 | 316 | 312
2016-03-03 13:30 | 320 | 316
2016-03-03 14:00 | 321 | 317
2016-03-03 14:30 | 320 | 317
2016-03-03 15:00 | 325 | 321
2016-03-03 15:30 | 323 | 319
2016-03-03 16:00 | 326 | 322
2016-03-03 16:30 | 328 | 325
2016-03-03 17:00 | 312 | 308
2016-03-03 17:30 | 305 | 300
2016-03-03 18:00 | 304 | 300
2016-03-03 18:30 | 294 | 290
2016-03-03 19:00 | 296 | 292
2016-03-03 19:30 | 297 | 292
2016-03-03 20:00 | 290 | 285
2016-03-03 20:30 | 319 | 315
2016-03-03 21:00 | 306 | 302
2016-03-03 21:30 | 318 | 314
2016-03-03 22:00 | 306 | 302
2016-03-03 22:30 | 300 | 296
2016-03-03 23:00 | 293 | 289
2016-03-03 23:30 | 279 | 275
2016-03-04 | 270 | 266
2016-03-04 00:30 | 262 | 258
2016-03-04 01:00 | 257 | 253
2016-03-04 01:30 | 255 | 251
2016-03-04 02:00 | 252 | 248
2016-03-04 02:30 | 251 | 247
2016-03-04 03:00 | 252 | 248
2016-03-04 03:30 | 251 | 248
2016-03-04 04:00 | 249 | 245
2016-03-04 04:30 | 248 | 244
2016-03-04 05:00 | 249 | 245
2016-03-04 05:30 | 253 | 249
2016-03-04 06:00 | 263 | 259
2016-03-04 06:30 | 283 | 280
2016-03-04 07:00 | 300 | 297
2016-03-04 07:30 | 317 | 314
2016-03-04 08:00 | 328 | 325
2016-03-04 08:30 | 332 | 329
2016-03-04 09:00 | 337 | 331
2016-03-04 09:30 | 335 | 330
2016-03-04 10:00 | 329 | 323
2016-03-04 10:30 | 319 | 313
2016-03-04 11:00 | 305 | 298
2016-03-04 11:30 | 294 | 287
2016-03-04 12:00 | 293 | 288
2016-03-04 12:30 | 293 | 288
2016-03-04 13:00 | 249 | 243
2016-03-04 13:30 | 225 | 218
2016-03-04 14:00 | 235 | 228
2016-03-04 14:30 | 237 | 230
2016-03-04 15:00 | 239 | 233
2016-03-04 15:30 | 240 | 233
2016-03-04 16:00 | 238 | 231
2016-03-04 16:30 | 236 | 229
2016-03-04 17:00 | 241 | 234
2016-03-04 17:30 | 246 | 239
2016-03-04 18:00 | 241 | 234
2016-03-04 18:30 | 239 | 231
2016-03-04 19:00 | 242 | 236
2016-03-04 19:30 | 245 | 239
2016-03-04 20:00 | 240 | 235
2016-03-04 20:30 | 287 | 285
2016-03-04 21:00 | 296 | 294
2016-03-04 21:30 | 288 | 286
2016-03-04 22:00 | 279 | 277
2016-03-04 22:30 | 281 | 278
2016-03-04 23:00 | 277 | 274
2016-03-04 23:30 | 267 | 264
2016-03-05 | 260 | 258
2016-03-05 00:30 | 255 | 252
2016-03-05 01:00 | 248 | 245
2016-03-05 01:30 | 243 | 240
2016-03-05 02:00 | 240 | 237
2016-03-05 02:30 | 239 | 236
2016-03-05 03:00 | 236 | 233
2016-03-05 03:30 | 234 | 231
2016-03-05 04:00 | 233 | 230
2016-03-05 04:30 | 233 | 231
2016-03-05 05:00 | 234 | 231
2016-03-05 05:30 | 237 | 235
2016-03-05 06:00 | 239 | 237
2016-03-05 06:30 | 245 | 243
2016-03-05 07:00 | 251 | 249
2016-03-05 07:30 | 263 | 261
2016-03-05 08:00 | 276 | 273
2016-03-05 08:30 | 287 | 284
2016-03-05 09:00 | 292 | 290
2016-03-05 09:30 | 287 | 284
2016-03-05 10:00 | 260 | 258
2016-03-05 10:30 | 253 | 250
2016-03-05 11:00 | 254 | 251
2016-03-05 11:30 | 253 | 250
2016-03-05 12:00 | 254 | 251
2016-03-05 12:30 | 250 | 247
2016-03-05 13:00 | 242 | 239
2016-03-05 13:30 | 251 | 248
2016-03-05 14:00 | 263 | 260
2016-03-05 14:30 | 269 | 266
2016-03-05 15:00 | 276 | 274
2016-03-05 15:30 | 280 | 277
2016-03-05 16:00 | 285 | 282
2016-03-05 16:30 | 288 | 285
2016-03-05 17:00 | 293 | 290
2016-03-05 17:30 | 299 | 297
2016-03-05 18:00 | 303 | 301
2016-03-05 18:30 | 307 | 305
2016-03-05 19:00 | 314 | 312
2016-03-05 19:30 | 319 | 316
2016-03-05 20:00 | 312 | 309
2016-03-05 20:30 | 304 | 301
2016-03-05 21:00 | 297 | 293
2016-03-05 21:30 | 292 | 289
2016-03-05 22:00 | 283 | 280
2016-03-05 22:30 | 285 | 283
2016-03-05 23:00 | 282 | 279
2016-03-05 23:30 | 271 | 269
2016-03-06 | 263 | 260
2016-03-06 00:30 | 256 | 253
2016-03-06 01:00 | 251 | 248
2016-03-06 01:30 | 244 | 242
2016-03-06 02:00 | 242 | 239
2016-03-06 02:30 | 240 | 237
2016-03-06 03:00 | 237 | 234
2016-03-06 03:30 | 235 | 233
2016-03-06 04:00 | 235 | 233
2016-03-06 04:30 | 235 | 233
2016-03-06 05:00 | 235 | 232
2016-03-06 05:30 | 234 | 231
2016-03-06 06:00 | 234 | 232
2016-03-06 06:30 | 239 | 237
2016-03-06 07:00 | 241 | 239
2016-03-06 07:30 | 247 | 245
2016-03-06 08:00 | 249 | 247
2016-03-06 08:30 | 238 | 236
2016-03-06 09:00 | 247 | 245
2016-03-06 09:30 | 261 | 258
2016-03-06 10:00 | 257 | 254
2016-03-06 10:30 | 255 | 252
2016-03-06 11:00 | 252 | 248
2016-03-06 11:30 | 253 | 250
2016-03-06 12:00 | 255 | 252
2016-03-06 12:30 | 254 | 251
2016-03-06 13:00 | 257 | 254
2016-03-06 13:30 | 269 | 266
2016-03-06 14:00 | 281 | 279
2016-03-06 14:30 | 286 | 283
2016-03-06 15:00 | 289 | 287
2016-03-06 15:30 | 292 | 290
2016-03-06 16:00 | 299 | 297
2016-03-06 16:30 | 303 | 301
2016-03-06 17:00 | 310 | 307
2016-03-06 17:30 | 317 | 315
2016-03-06 18:00 | 325 | 323
2016-03-06 18:30 | 333 | 331
2016-03-06 19:00 | 326 | 323
2016-03-06 19:30 | 326 | 323
2016-03-06 20:00 | 338 | 335
2016-03-06 20:30 | 341 | 339
2016-03-06 21:00 | 336 | 334
2016-03-06 21:30 | 323 | 321
2016-03-06 22:00 | 313 | 310
2016-03-06 22:30 | 299 | 296
2016-03-06 23:00 | 287 | 284
2016-03-06 23:30 | 276 | 273
2016-03-07 | 266 | 264
2016-03-07 00:30 | 260 | 256
2016-03-07 01:00 | 252 | 249
2016-03-07 01:30 | 245 | 243
2016-03-07 02:00 | 241 | 240
2016-03-07 02:30 | 240 | 238
2016-03-07 03:00 | 238 | 236
2016-03-07 03:30 | 235 | 233
2016-03-07 04:00 | 235 | 233
2016-03-07 04:30 | 235 | 233
2016-03-07 05:00 | 237 | 235
2016-03-07 05:30 | 243 | 241
2016-03-07 06:00 | 253 | 251
2016-03-07 06:30 | 270 | 268
2016-03-07 07:00 | 283 | 280
2016-03-07 07:30 | 303 | 301
2016-03-07 08:00 | 316 | 313
2016-03-07 08:30 | 322 | 320
2016-03-07 09:00 | 325 | 323
2016-03-07 09:30 | 322 | 320
2016-03-07 10:00 | 313 | 311
2016-03-07 10:30 | 309 | 307
2016-03-07 11:00 | 287 | 284
2016-03-07 11:30 | 295 | 293
2016-03-07 12:00 | 301 | 299
2016-03-07 12:30 | 307 | 304
2016-03-07 13:00 | 309 | 307
2016-03-07 13:30 | 315 | 312
2016-03-07 14:00 | 330 | 328
2016-03-07 14:30 | 294 | 291
2016-03-07 15:00 | 263 | 260
2016-03-07 15:30 | 263 | 259
2016-03-07 16:00 | 267 | 264
2016-03-07 16:30 | 266 | 263
2016-03-07 17:00 | 257 | 254
2016-03-07 17:30 | 248 | 245
2016-03-07 18:00 | 246 | 243
2016-03-07 18:30 | 251 | 247
2016-03-07 19:00 | 277 | 274
2016-03-07 19:30 | 299 | 297
2016-03-07 20:00 | 296 | 294
2016-03-07 20:30 | 286 | 284
2016-03-07 21:00 | 277 | 275
2016-03-07 21:30 | 322 | 320
2016-03-07 22:00 | 327 | 325
2016-03-07 22:30 | 310 | 308
2016-03-07 23:00 | 299 | 296
2016-03-07 23:30 | 266 | 263
2016-03-08 | 271 | 269
2016-03-08 00:30 | 262 | 260
2016-03-08 01:00 | 258 | 256
2016-03-08 01:30 | 252 | 251
2016-03-08 02:00 | 250 | 248
2016-03-08 02:30 | 246 | 244
2016-03-08 03:00 | 243 | 241
2016-03-08 03:30 | 244 | 242
2016-03-08 04:00 | 245 | 243
2016-03-08 04:30 | 246 | 244
2016-03-08 05:00 | 246 | 244
2016-03-08 05:30 | 253 | 251
2016-03-08 06:00 | 259 | 258
2016-03-08 06:30 | 275 | 273
2016-03-08 07:00 | 294 | 292
2016-03-08 07:30 | 313 | 311
2016-03-08 08:00 | 324 | 322
2016-03-08 08:30 | 330 | 328
2016-03-08 09:00 | 332 | 330
2016-03-08 09:30 | 329 | 327
2016-03-08 10:00 | 309 | 307
2016-03-08 10:30 | 306 | 304
2016-03-08 11:00 | 309 | 307
2016-03-08 11:30 | 312 | 310
2016-03-08 12:00 | 314 | 312
2016-03-08 12:30 | 313 | 311
2016-03-08 13:00 | 317 | 316
2016-03-08 13:30 | 281 | 279
2016-03-08 14:00 | 263 | 261
2016-03-08 14:30 | 268 | 266
2016-03-08 15:00 | 242 | 240
2016-03-08 15:30 | 198 | 195
2016-03-08 16:00 | 229 | 227
2016-03-08 16:30 | 256 | 254
2016-03-08 17:00 | 264 | 262
2016-03-08 17:30 | 265 | 263
2016-03-08 18:00 | 265 | 263
2016-03-08 18:30 | 271 | 269
2016-03-08 19:00 | 297 | 295
2016-03-08 19:30 | 306 | 304
2016-03-08 20:00 | 328 | 326
2016-03-08 20:30 | 307 | 305
2016-03-08 21:00 | 308 | 306
2016-03-08 21:30 | 329 | 327
2016-03-08 22:00 | 323 | 320
2016-03-08 22:30 | 311 | 308
2016-03-08 23:00 | 295 | 293
2016-03-08 23:30 | 285 | 282
2016-03-09 | 277 | 274
2016-03-09 00:30 | 268 | 265
2016-03-09 01:00 | 261 | 259
2016-03-09 01:30 | 257 | 254
2016-03-09 02:00 | 253 | 250
2016-03-09 02:30 | 248 | 245
2016-03-09 03:00 | 246 | 244
2016-03-09 03:30 | 246 | 244
2016-03-09 04:00 | 245 | 243
2016-03-09 04:30 | 245 | 243
2016-03-09 05:00 | 248 | 246
2016-03-09 05:30 | 255 | 253
2016-03-09 06:00 | 265 | 263
2016-03-09 06:30 | 280 | 278
2016-03-09 07:00 | 295 | 293
2016-03-09 07:30 | 312 | 311
2016-03-09 08:00 | 324 | 322
2016-03-09 08:30 | 331 | 330
2016-03-09 09:00 | 335 | 334
2016-03-09 09:30 | 332 | 331
2016-03-09 10:00 | 312 | 310
2016-03-09 10:30 | 307 | 305
2016-03-09 11:00 | 306 | 304
2016-03-09 11:30 | 306 | 304
2016-03-09 12:00 | 307 | 305
2016-03-09 12:30 | 290 | 288
2016-03-09 13:00 | 293 | 291
2016-03-09 13:30 | 294 | 292
2016-03-09 14:00 | 295 | 293
2016-03-09 14:30 | 283 | 281
2016-03-09 15:00 | 191 | 188
2016-03-09 15:30 | 154 | 151
2016-03-09 16:00 | 148 | 146
2016-03-09 16:30 | 130 | 128
2016-03-09 17:00 | 210 | 208
2016-03-09 17:30 | 220 | 217
2016-03-09 18:00 | 244 | 242
2016-03-09 18:30 | 253 | 250
2016-03-09 19:00 | 262 | 259
2016-03-09 19:30 | 292 | 289
2016-03-09 20:00 | 316 | 313
2016-03-09 20:30 | 360 | 357
2016-03-09 21:00 | 358 | 355
2016-03-09 21:30 | 345 | 343
2016-03-09 22:00 | 332 | 329
2016-03-09 22:30 | 316 | 313
2016-03-09 23:00 | 303 | 301
2016-03-09 23:30 | 291 | 288
2016-03-10 | 280 | 276
2016-03-10 00:30 | 271 | 267
2016-03-10 01:00 | 264 | 261
2016-03-10 01:30 | 260 | 257
2016-03-10 02:00 | 257 | 253
2016-03-10 02:30 | 256 | 252
2016-03-10 03:00 | 252 | 249
2016-03-10 03:30 | 251 | 247
2016-03-10 04:00 | 248 | 244
2016-03-10 04:30 | 250 | 246
2016-03-10 05:00 | 252 | 249
2016-03-10 05:30 | 257 | 254
2016-03-10 06:00 | 269 | 266
2016-03-10 06:30 | 287 | 283
2016-03-10 07:00 | 302 | 299
2016-03-10 07:30 | 323 | 320
2016-03-10 08:00 | 334 | 331
2016-03-10 08:30 | 340 | 336
2016-03-10 09:00 | 340 | 337
2016-03-10 09:30 | 337 | 333
2016-03-10 10:00 | 325 | 321
2016-03-10 10:30 | 322 | 318
2016-03-10 11:00 | 314 | 310
2016-03-10 11:30 | 311 | 307
2016-03-10 12:00 | 315 | 310
2016-03-10 12:30 | 316 | 312
2016-03-10 13:00 | 316 | 312
2016-03-10 13:30 | 321 | 317
2016-03-10 14:00 | 332 | 328
2016-03-10 14:30 | 297 | 293
2016-03-10 15:00 | 283 | 279
2016-03-10 15:30 | 298 | 295
2016-03-10 16:00 | 307 | 304
2016-03-10 16:30 | 277 | 273
2016-03-10 17:00 | 271 | 267
2016-03-10 17:30 | 269 | 265
2016-03-10 18:00 | 272 | 268
2016-03-10 18:30 | 276 | 272
2016-03-10 19:00 | 285 | 281
2016-03-10 19:30 | 288 | 284
2016-03-10 20:00 | 310 | 306
2016-03-10 20:30 | 307 | 304
2016-03-10 21:00 | 334 | 330
2016-03-10 21:30 | 326 | 322
2016-03-10 22:00 | 311 | 308
2016-03-10 22:30 | 309 | 305
2016-03-10 23:00 | 296 | 293
2016-03-10 23:30 | 284 | 281
2016-03-11 | 274 | 271
2016-03-11 00:30 | 266 | 262
2016-03-11 01:00 | 258 | 254
2016-03-11 01:30 | 252 | 249
2016-03-11 02:00 | 249 | 246
2016-03-11 02:30 | 248 | 245
2016-03-11 03:00 | 247 | 244
2016-03-11 03:30 | 246 | 243
2016-03-11 04:00 | 246 | 243
2016-03-11 04:30 | 244 | 241
2016-03-11 05:00 | 245 | 242
2016-03-11 05:30 | 252 | 248
2016-03-11 06:00 | 260 | 257
2016-03-11 06:30 | 279 | 275
2016-03-11 07:00 | 294 | 289
2016-03-11 07:30 | 310 | 306
2016-03-11 08:00 | 322 | 318
2016-03-11 08:30 | 325 | 321
2016-03-11 09:00 | 326 | 322
2016-03-11 09:30 | 324 | 320
2016-03-11 10:00 | 314 | 310
2016-03-11 10:30 | 309 | 305
2016-03-11 11:00 | 312 | 308
2016-03-11 11:30 | 281 | 277
2016-03-11 12:00 | 243 | 238
2016-03-11 12:30 | 243 | 238
2016-03-11 13:00 | 240 | 234
2016-03-11 13:30 | 237 | 231
2016-03-11 14:00 | 245 | 240
2016-03-11 14:30 | 228 | 223
2016-03-11 15:00 | 190 | 184
2016-03-11 15:30 | 189 | 184
2016-03-11 16:00 | 201 | 197
2016-03-11 16:30 | 228 | 224
2016-03-11 17:00 | 240 | 236
2016-03-11 17:30 | 252 | 248
2016-03-11 18:00 | 257 | 253
2016-03-11 18:30 | 257 | 252
2016-03-11 19:00 | 267 | 263
2016-03-11 19:30 | 272 | 268
2016-03-11 20:00 | 296 | 292
2016-03-11 20:30 | 293 | 289
2016-03-11 21:00 | 319 | 316
2016-03-11 21:30 | 314 | 311
2016-03-11 22:00 | 304 | 301
2016-03-11 22:30 | 293 | 289
2016-03-11 23:00 | 281 | 277
2016-03-11 23:30 | 270 | 265
2016-03-12 | 262 | 257
2016-03-12 00:30 | 264 | 260
2016-03-12 01:00 | 261 | 257
2016-03-12 01:30 | 256 | 251
2016-03-12 02:00 | 251 | 247
2016-03-12 02:30 | 248 | 243
2016-03-12 03:00 | 244 | 239
2016-03-12 03:30 | 242 | 238
2016-03-12 04:00 | 238 | 234
2016-03-12 04:30 | 240 | 236
2016-03-12 05:00 | 238 | 234
2016-03-12 05:30 | 240 | 236
2016-03-12 06:00 | 237 | 234
2016-03-12 06:30 | 244 | 240
2016-03-12 07:00 | 250 | 246
2016-03-12 07:30 | 260 | 257
2016-03-12 08:00 | 269 | 265
2016-03-12 08:30 | 280 | 276
2016-03-12 09:00 | 263 | 258
2016-03-12 09:30 | 247 | 243
2016-03-12 10:00 | 233 | 229
2016-03-12 10:30 | 232 | 228
2016-03-12 11:00 | 232 | 227
2016-03-12 11:30 | 239 | 235
2016-03-12 12:00 | 244 | 239
2016-03-12 12:30 | 242 | 237
2016-03-12 13:00 | 236 | 231
2016-03-12 13:30 | 236 | 231
2016-03-12 14:00 | 220 | 214
2016-03-12 14:30 | 219 | 213
2016-03-12 15:00 | 219 | 213
2016-03-12 15:30 | 220 | 214
2016-03-12 16:00 | 228 | 222
2016-03-12 16:30 | 229 | 223
2016-03-12 17:00 | 234 | 229
2016-03-12 17:30 | 238 | 232
2016-03-12 18:00 | 238 | 233
2016-03-12 18:30 | 273 | 268
2016-03-12 19:00 | 261 | 256
2016-03-12 19:30 | 314 | 310
2016-03-12 20:00 | 328 | 324
2016-03-12 20:30 | 317 | 313
2016-03-12 21:00 | 312 | 307
2016-03-12 21:30 | 304 | 299
2016-03-12 22:00 | 294 | 289
2016-03-12 22:30 | 293 | 288
2016-03-12 23:00 | 285 | 280
2016-03-12 23:30 | 277 | 272
2016-03-13 | 269 | 264
2016-03-13 00:30 | 261 | 256
2016-03-13 01:00 | 255 | 250
2016-03-13 01:30 | 248 | 243
2016-03-13 02:00 | 246 | 240
2016-03-13 02:30 | 242 | 237
2016-03-13 03:00 | 238 | 234
2016-03-13 03:30 | 235 | 231
2016-03-13 04:00 | 234 | 229
2016-03-13 04:30 | 232 | 228
2016-03-13 05:00 | 232 | 228
2016-03-13 05:30 | 232 | 228
2016-03-13 06:00 | 234 | 229
2016-03-13 06:30 | 236 | 232
2016-03-13 07:00 | 237 | 233
2016-03-13 07:30 | 245 | 241
2016-03-13 08:00 | 252 | 248
2016-03-13 08:30 | 261 | 258
2016-03-13 09:00 | 266 | 263
2016-03-13 09:30 | 266 | 262
2016-03-13 10:00 | 263 | 258
2016-03-13 10:30 | 263 | 259
2016-03-13 11:00 | 263 | 259
2016-03-13 11:30 | 269 | 264
2016-03-13 12:00 | 275 | 271
2016-03-13 12:30 | 280 | 276
2016-03-13 13:00 | 283 | 279
2016-03-13 13:30 | 282 | 278
2016-03-13 14:00 | 292 | 288
2016-03-13 14:30 | 297 | 293
2016-03-13 15:00 | 302 | 299
2016-03-13 15:30 | 306 | 303
2016-03-13 16:00 | 316 | 313
2016-03-13 16:30 | 316 | 313
2016-03-13 17:00 | 319 | 315
2016-03-13 17:30 | 329 | 326
2016-03-13 18:00 | 336 | 333
2016-03-13 18:30 | 343 | 339
2016-03-13 19:00 | 312 | 308
2016-03-13 19:30 | 333 | 330
2016-03-13 20:00 | 346 | 343
2016-03-13 20:30 | 336 | 333
2016-03-13 21:00 | 327 | 324
2016-03-13 21:30 | 318 | 314
2016-03-13 22:00 | 303 | 300
2016-03-13 22:30 | 299 | 296
2016-03-13 23:00 | 292 | 288
2016-03-13 23:30 | 278 | 274
2016-03-14 | 268 | 264
2016-03-14 00:30 | 261 | 258
2016-03-14 01:00 | 255 | 252
2016-03-14 01:30 | 249 | 246
2016-03-14 02:00 | 247 | 244
2016-03-14 02:30 | 245 | 241
2016-03-14 03:00 | 242 | 239
2016-03-14 03:30 | 241 | 237
2016-03-14 04:00 | 238 | 234
2016-03-14 04:30 | 238 | 234
2016-03-14 05:00 | 240 | 236
2016-03-14 05:30 | 246 | 243
2016-03-14 06:00 | 258 | 255
2016-03-14 06:30 | 272 | 269
2016-03-14 07:00 | 290 | 288
2016-03-14 07:30 | 312 | 309
2016-03-14 08:00 | 325 | 322
2016-03-14 08:30 | 328 | 325
2016-03-14 09:00 | 334 | 330
2016-03-14 09:30 | 334 | 330
2016-03-14 10:00 | 325 | 321
2016-03-14 10:30 | 321 | 317
2016-03-14 11:00 | 324 | 320
2016-03-14 11:30 | 328 | 324
2016-03-14 12:00 | 302 | 298
2016-03-14 12:30 | 290 | 286
2016-03-14 13:00 | 273 | 269
2016-03-14 13:30 | 277 | 272
2016-03-14 14:00 | 277 | 273
2016-03-14 14:30 | 304 | 300
2016-03-14 15:00 | 321 | 317
2016-03-14 15:30 | 288 | 284
2016-03-14 16:00 | 291 | 287
2016-03-14 16:30 | 292 | 288
2016-03-14 17:00 | 294 | 290
2016-03-14 17:30 | 255 | 251
2016-03-14 18:00 | 275 | 272
2016-03-14 18:30 | 290 | 287
2016-03-14 19:00 | 279 | 275
2016-03-14 19:30 | 293 | 290
2016-03-14 20:00 | 299 | 296
2016-03-14 20:30 | 290 | 288
2016-03-14 21:00 | 309 | 306
2016-03-14 21:30 | 299 | 296
2016-03-14 22:00 | 284 | 281
2016-03-14 22:30 | 276 | 272
2016-03-14 23:00 | 263 | 259
2016-03-14 23:30 | 279 | 276
2016-03-15 | 277 | 274
2016-03-15 00:30 | 269 | 266
2016-03-15 01:00 | 264 | 260
2016-03-15 01:30 | 255 | 253
2016-03-15 02:00 | 252 | 250
2016-03-15 02:30 | 251 | 248
2016-03-15 03:00 | 251 | 248
2016-03-15 03:30 | 249 | 247
2016-03-15 04:00 | 247 | 245
2016-03-15 04:30 | 247 | 245
2016-03-15 05:00 | 248 | 246
2016-03-15 05:30 | 255 | 253
2016-03-15 06:00 | 263 | 261
2016-03-15 06:30 | 207 | 202
2016-03-15 07:00 | 232 | 229
2016-03-15 07:30 | 308 | 305
2016-03-15 08:00 | 323 | 319
2016-03-15 08:30 | 324 | 321
2016-03-15 09:00 | 308 | 304
2016-03-15 09:30 | 320 | 317
2016-03-15 10:00 | 309 | 305
2016-03-15 10:30 | 313 | 310
2016-03-15 11:00 | 315 | 312
2016-03-15 11:30 | 315 | 312
2016-03-15 12:00 | 323 | 320
2016-03-15 12:30 | 329 | 326
2016-03-15 13:00 | 334 | 331
2016-03-15 13:30 | 330 | 327
2016-03-15 14:00 | 336 | 333
2016-03-15 14:30 | 304 | 300
2016-03-15 15:00 | 305 | 301
2016-03-15 15:30 | 278 | 274
2016-03-15 16:00 | 282 | 278
2016-03-15 16:30 | 280 | 276
2016-03-15 17:00 | 278 | 273
2016-03-15 17:30 | 276 | 271
2016-03-15 18:00 | 275 | 270
2016-03-15 18:30 | 280 | 275
2016-03-15 19:00 | 291 | 287
2016-03-15 19:30 | 293 | 289
2016-03-15 20:00 | 285 | 281
2016-03-15 20:30 | 302 | 298
2016-03-15 21:00 | 332 | 328
2016-03-15 21:30 | 326 | 323
2016-03-15 22:00 | 312 | 308
2016-03-15 22:30 | 306 | 302
2016-03-15 23:00 | 278 | 275
2016-03-15 23:30 | 280 | 278
2016-03-16 | 272 | 269
2016-03-16 00:30 | 263 | 261
2016-03-16 01:00 | 257 | 255
2016-03-16 01:30 | 255 | 252
2016-03-16 02:00 | 251 | 248
2016-03-16 02:30 | 247 | 244
2016-03-16 03:00 | 246 | 243
2016-03-16 03:30 | 244 | 241
2016-03-16 04:00 | 243 | 240
2016-03-16 04:30 | 245 | 242
2016-03-16 05:00 | 248 | 246
2016-03-16 05:30 | 254 | 251
2016-03-16 06:00 | 265 | 262
2016-03-16 06:30 | 280 | 277
2016-03-16 07:00 | 258 | 254
2016-03-16 07:30 | 295 | 293
2016-03-16 08:00 | 315 | 312
2016-03-16 08:30 | 325 | 322
2016-03-16 09:00 | 304 | 300
2016-03-16 09:30 | 305 | 302
2016-03-16 10:00 | 297 | 294
2016-03-16 10:30 | 275 | 270
2016-03-16 11:00 | 252 | 247
2016-03-16 11:30 | 250 | 244
2016-03-16 12:00 | 259 | 254
2016-03-16 12:30 | 246 | 241
2016-03-16 13:00 | 225 | 219
2016-03-16 13:30 | 209 | 204
2016-03-16 14:00 | 135 | 130
2016-03-16 14:30 | 189 | 186
2016-03-16 15:00 | 252 | 248
2016-03-16 15:30 | 250 | 247
2016-03-16 16:00 | 220 | 216
2016-03-16 16:30 | 213 | 209
2016-03-16 17:00 | 239 | 235
2016-03-16 17:30 | 267 | 263
2016-03-16 18:00 | 281 | 277
2016-03-16 18:30 | 287 | 284
2016-03-16 19:00 | 265 | 261
2016-03-16 19:30 | 265 | 261
2016-03-16 20:00 | 285 | 281
2016-03-16 20:30 | 276 | 272
2016-03-16 21:00 | 302 | 299
2016-03-16 21:30 | 296 | 292
2016-03-16 22:00 | 283 | 279
2016-03-16 22:30 | 283 | 279
2016-03-16 23:00 | 276 | 273
2016-03-16 23:30 | 265 | 261
2016-03-17 | 256 | 252
2016-03-17 00:30 | 248 | 244
2016-03-17 01:00 | 246 | 242
2016-03-17 01:30 | 237 | 237
2016-03-17 02:00 | 233 | 233
2016-03-17 02:30 | 231 | 230
2016-03-17 03:00 | 229 | 228
2016-03-17 03:30 | 227 | 226
2016-03-17 04:00 | 227 | 226
2016-03-17 04:30 | 227 | 226
2016-03-17 05:00 | 230 | 229
2016-03-17 05:30 | 238 | 237
2016-03-17 06:00 | 247 | 246
2016-03-17 06:30 | 264 | 263
2016-03-17 07:00 | 279 | 278
2016-03-17 07:30 | 301 | 300
2016-03-17 08:00 | 312 | 310
2016-03-17 08:30 | 305 | 303
2016-03-17 09:00 | 319 | 317
2016-03-17 09:30 | 312 | 310
2016-03-17 10:00 | 292 | 290
2016-03-17 10:30 | 288 | 286
2016-03-17 11:00 | 272 | 270
2016-03-17 11:30 | 252 | 249
2016-03-17 12:00 | 240 | 237
2016-03-17 12:30 | 261 | 259
2016-03-17 13:00 | 268 | 265
2016-03-17 13:30 | 215 | 213
2016-03-17 14:00 | 188 | 185
2016-03-17 14:30 | 196 | 194
2016-03-17 15:00 | 220 | 218
2016-03-17 15:30 | 190 | 188
2016-03-17 16:00 | 187 | 184
2016-03-17 16:30 | 187 | 185
2016-03-17 17:00 | 187 | 185
2016-03-17 17:30 | 189 | 187
2016-03-17 18:00 | 196 | 194
2016-03-17 18:30 | 200 | 198
2016-03-17 19:00 | 187 | 184
2016-03-17 19:30 | 181 | 178
2016-03-17 20:00 | 197 | 195
2016-03-17 20:30 | 196 | 194
2016-03-17 21:00 | 190 | 188
2016-03-17 21:30 | 182 | 180
2016-03-17 22:00 | 170 | 168
2016-03-17 22:30 | 169 | 167
2016-03-17 23:00 | 179 | 178
2016-03-17 23:30 | 182 | 180
2016-03-18 | 209 | 207
2016-03-18 00:30 | 215 | 214
2016-03-18 01:00 | 212 | 211
2016-03-18 01:30 | 209 | 207
2016-03-18 02:00 | 206 | 204
2016-03-18 02:30 | 213 | 211
2016-03-18 03:00 | 214 | 213
2016-03-18 03:30 | 214 | 213
2016-03-18 04:00 | 214 | 213
2016-03-18 04:30 | 214 | 213
2016-03-18 05:00 | 216 | 214
2016-03-18 05:30 | 224 | 223
2016-03-18 06:00 | 233 | 232
2016-03-18 06:30 | 253 | 252
2016-03-18 07:00 | 269 | 266
2016-03-18 07:30 | 287 | 285
2016-03-18 08:00 | 300 | 297
2016-03-18 08:30 | 307 | 305
2016-03-18 09:00 | 305 | 303
2016-03-18 09:30 | 292 | 289
2016-03-18 10:00 | 283 | 280
2016-03-18 10:30 | 280 | 277
2016-03-18 11:00 | 276 | 272
2016-03-18 11:30 | 240 | 236
2016-03-18 12:00 | 228 | 224
2016-03-18 12:30 | 228 | 224
2016-03-18 13:00 | 242 | 238
2016-03-18 13:30 | 218 | 214
2016-03-18 14:00 | 221 | 218
2016-03-18 14:30 | 223 | 219
2016-03-18 15:00 | 224 | 220
2016-03-18 15:30 | 222 | 219
2016-03-18 16:00 | 229 | 225
2016-03-18 16:30 | 216 | 212
2016-03-18 17:00 | 197 | 193
2016-03-18 17:30 | 191 | 188
2016-03-18 18:00 | 214 | 211
2016-03-18 18:30 | 207 | 204
2016-03-18 19:00 | 215 | 212
2016-03-18 19:30 | 236 | 233
2016-03-18 20:00 | 232 | 229
2016-03-18 20:30 | 224 | 222
2016-03-18 21:00 | 245 | 242
2016-03-18 21:30 | 241 | 238
2016-03-18 22:00 | 232 | 229
2016-03-18 22:30 | 194 | 190
2016-03-18 23:00 | 209 | 206
2016-03-18 23:30 | 215 | 212
2016-03-19 | 208 | 206
2016-03-19 00:30 | 233 | 231
2016-03-19 01:00 | 235 | 233
2016-03-19 01:30 | 232 | 230
2016-03-19 02:00 | 228 | 226
2016-03-19 02:30 | 224 | 222
2016-03-19 03:00 | 222 | 220
2016-03-19 03:30 | 222 | 219
2016-03-19 04:00 | 219 | 216
2016-03-19 04:30 | 218 | 216
2016-03-19 05:00 | 218 | 216
2016-03-19 05:30 | 220 | 218
2016-03-19 06:00 | 223 | 221
2016-03-19 06:30 | 229 | 227
2016-03-19 07:00 | 233 | 231
2016-03-19 07:30 | 245 | 243
2016-03-19 08:00 | 256 | 253
2016-03-19 08:30 | 261 | 259
2016-03-19 09:00 | 268 | 266
2016-03-19 09:30 | 255 | 252
2016-03-19 10:00 | 254 | 251
2016-03-19 10:30 | 253 | 250
2016-03-19 11:00 | 255 | 253
2016-03-19 11:30 | 259 | 257
2016-03-19 12:00 | 263 | 260
2016-03-19 12:30 | 245 | 242
2016-03-19 13:00 | 194 | 190
2016-03-19 13:30 | 205 | 202
2016-03-19 14:00 | 199 | 196
2016-03-19 14:30 | 222 | 219
2016-03-19 15:00 | 231 | 229
2016-03-19 15:30 | 238 | 236
2016-03-19 16:00 | 245 | 243
2016-03-19 16:30 | 223 | 219
2016-03-19 17:00 | 223 | 219
2016-03-19 17:30 | 233 | 230
2016-03-19 18:00 | 254 | 252
2016-03-19 18:30 | 292 | 290
2016-03-19 19:00 | 307 | 305
2016-03-19 19:30 | 347 | 345
2016-03-19 20:00 | 345 | 343
2016-03-19 20:30 | 333 | 331
2016-03-19 21:00 | 325 | 323
2016-03-19 21:30 | 316 | 313
2016-03-19 22:00 | 305 | 302
2016-03-19 22:30 | 265 | 263
2016-03-19 23:00 | 253 | 251
2016-03-19 23:30 | 244 | 241
2016-03-20 | 248 | 246
2016-03-20 00:30 | 247 | 245
2016-03-20 01:00 | 242 | 240
2016-03-20 01:30 | 236 | 234
2016-03-20 02:00 | 231 | 230
2016-03-20 02:30 | 229 | 228
2016-03-20 03:00 | 224 | 223
2016-03-20 03:30 | 224 | 222
2016-03-20 04:00 | 222 | 221
2016-03-20 04:30 | 225 | 223
2016-03-20 05:00 | 224 | 222
2016-03-20 05:30 | 224 | 223
2016-03-20 06:00 | 225 | 223
2016-03-20 06:30 | 228 | 226
2016-03-20 07:00 | 231 | 229
2016-03-20 07:30 | 235 | 233
2016-03-20 08:00 | 240 | 238
2016-03-20 08:30 | 249 | 247
2016-03-20 09:00 | 255 | 253
2016-03-20 09:30 | 256 | 254
2016-03-20 10:00 | 251 | 249
2016-03-20 10:30 | 254 | 252
2016-03-20 11:00 | 259 | 257
2016-03-20 11:30 | 259 | 256
2016-03-20 12:00 | 262 | 260
2016-03-20 12:30 | 272 | 270
2016-03-20 13:00 | 277 | 275
2016-03-20 13:30 | 289 | 287
2016-03-20 14:00 | 305 | 303
2016-03-20 14:30 | 313 | 311
2016-03-20 15:00 | 320 | 317
2016-03-20 15:30 | 327 | 324
2016-03-20 16:00 | 333 | 331
2016-03-20 16:30 | 340 | 338
2016-03-20 17:00 | 346 | 344
2016-03-20 17:30 | 347 | 346
2016-03-20 18:00 | 327 | 325
2016-03-20 18:30 | 323 | 321
2016-03-20 19:00 | 322 | 320
2016-03-20 19:30 | 348 | 346
2016-03-20 20:00 | 339 | 337
2016-03-20 20:30 | 357 | 354
2016-03-20 21:00 | 352 | 349
2016-03-20 21:30 | 337 | 334
2016-03-20 22:00 | 322 | 319
2016-03-20 22:30 | 304 | 301
2016-03-20 23:00 | 290 | 288
2016-03-20 23:30 | 279 | 276
2016-03-21 | 270 | 267
2016-03-21 00:30 | 261 | 259
2016-03-21 01:00 | 255 | 253
2016-03-21 01:30 | 248 | 246
2016-03-21 02:00 | 246 | 244
2016-03-21 02:30 | 242 | 240
2016-03-21 03:00 | 240 | 237
2016-03-21 03:30 | 239 | 237
2016-03-21 04:00 | 239 | 237
2016-03-21 04:30 | 240 | 238
2016-03-21 05:00 | 242 | 239
2016-03-21 05:30 | 246 | 243
2016-03-21 06:00 | 252 | 249
2016-03-21 06:30 | 272 | 270
2016-03-21 07:00 | 290 | 288
2016-03-21 07:30 | 311 | 309
2016-03-21 08:00 | 339 | 337
2016-03-21 08:30 | 347 | 345
2016-03-21 09:00 | 327 | 323
2016-03-21 09:30 | 315 | 311
2016-03-21 10:00 | 331 | 328
2016-03-21 10:30 | 337 | 333
2016-03-21 11:00 | 340 | 337
2016-03-21 11:30 | 340 | 337
2016-03-21 12:00 | 344 | 340
2016-03-21 12:30 | 347 | 344
2016-03-21 13:00 | 350 | 347
2016-03-21 13:30 | 350 | 347
2016-03-21 14:00 | 347 | 343
2016-03-21 14:30 | 359 | 356
2016-03-21 15:00 | 376 | 372
2016-03-21 15:30 | 379 | 375
2016-03-21 16:00 | 387 | 384
2016-03-21 16:30 | 385 | 382
2016-03-21 17:00 | 358 | 354
2016-03-21 17:30 | 339 | 334
2016-03-21 18:00 | 351 | 347
2016-03-21 18:30 | 374 | 371
2016-03-21 19:00 | 371 | 368
2016-03-21 19:30 | 359 | 356
2016-03-21 20:00 | 367 | 363
2016-03-21 20:30 | 352 | 348
2016-03-21 21:00 | 341 | 337
2016-03-21 21:30 | 325 | 321
2016-03-21 22:00 | 306 | 302
2016-03-21 22:30 | 278 | 274
2016-03-21 23:00 | 254 | 250
2016-03-21 23:30 | 255 | 251
2016-03-22 | 259 | 255
2016-03-22 00:30 | 250 | 247
2016-03-22 01:00 | 245 | 241
2016-03-22 01:30 | 241 | 238
2016-03-22 02:00 | 236 | 233
2016-03-22 02:30 | 256 | 253
2016-03-22 03:00 | 259 | 256
2016-03-22 03:30 | 259 | 256
2016-03-22 04:00 | 259 | 256
2016-03-22 04:30 | 259 | 256
2016-03-22 05:00 | 260 | 257
2016-03-22 05:30 | 265 | 263
2016-03-22 06:00 | 268 | 265
2016-03-22 06:30 | 269 | 266
2016-03-22 07:00 | 266 | 262
2016-03-22 07:30 | 296 | 292
2016-03-22 08:00 | 320 | 314
2016-03-22 08:30 | 324 | 319
2016-03-22 09:00 | 330 | 325
2016-03-22 09:30 | 329 | 323
2016-03-22 10:00 | 321 | 315
2016-03-22 10:30 | 322 | 316
2016-03-22 11:00 | 325 | 319
2016-03-22 11:30 | 326 | 320
2016-03-22 12:00 | 332 | 327
2016-03-22 12:30 | 335 | 329
2016-03-22 13:00 | 339 | 333
2016-03-22 13:30 | 351 | 346
2016-03-22 14:00 | 363 | 358
2016-03-22 14:30 | 370 | 365
2016-03-22 15:00 | 374 | 369
2016-03-22 15:30 | 376 | 371
2016-03-22 16:00 | 387 | 382
2016-03-22 16:30 | 391 | 387
2016-03-22 17:00 | 394 | 389
2016-03-22 17:30 | 395 | 391
2016-03-22 18:00 | 394 | 389
2016-03-22 18:30 | 396 | 392
2016-03-22 19:00 | 381 | 375
2016-03-22 19:30 | 387 | 382
2016-03-22 20:00 | 401 | 398
2016-03-22 20:30 | 396 | 391
2016-03-22 21:00 | 385 | 380
2016-03-22 21:30 | 366 | 361
2016-03-22 22:00 | 347 | 343
2016-03-22 22:30 | 313 | 307
2016-03-22 23:00 | 276 | 274
2016-03-22 23:30 | 282 | 280
2016-03-23 | 281 | 279
2016-03-23 00:30 | 263 | 261
2016-03-23 01:00 | 267 | 265
2016-03-23 01:30 | 261 | 259
2016-03-23 02:00 | 255 | 253
2016-03-23 02:30 | 252 | 250
2016-03-23 03:00 | 247 | 245
2016-03-23 03:30 | 246 | 244
2016-03-23 04:00 | 246 | 244
2016-03-23 04:30 | 246 | 244
2016-03-23 05:00 | 246 | 244
2016-03-23 05:30 | 251 | 249
2016-03-23 06:00 | 262 | 260
2016-03-23 06:30 | 277 | 275
2016-03-23 07:00 | 302 | 300
2016-03-23 07:30 | 328 | 325
2016-03-23 08:00 | 339 | 336
2016-03-23 08:30 | 345 | 341
2016-03-23 09:00 | 349 | 343
2016-03-23 09:30 | 346 | 341
2016-03-23 10:00 | 327 | 321
2016-03-23 10:30 | 281 | 276
2016-03-23 11:00 | 285 | 280
2016-03-23 11:30 | 287 | 282
2016-03-23 12:00 | 288 | 283
2016-03-23 12:30 | 293 | 288
2016-03-23 13:00 | 295 | 290
2016-03-23 13:30 | 304 | 300
2016-03-23 14:00 | 317 | 313
2016-03-23 14:30 | 324 | 320
2016-03-23 15:00 | 326 | 321
2016-03-23 15:30 | 324 | 319
2016-03-23 16:00 | 330 | 325
2016-03-23 16:30 | 332 | 328
2016-03-23 17:00 | 302 | 297
2016-03-23 17:30 | 286 | 281
2016-03-23 18:00 | 286 | 280
2016-03-23 18:30 | 288 | 283
2016-03-23 19:00 | 302 | 298
2016-03-23 19:30 | 305 | 301
2016-03-23 20:00 | 298 | 294
2016-03-23 20:30 | 315 | 311
2016-03-23 21:00 | 311 | 307
2016-03-23 21:30 | 299 | 294
2016-03-23 22:00 | 281 | 276
2016-03-23 22:30 | 220 | 214
2016-03-23 23:00 | 221 | 215
2016-03-23 23:30 | 224 | 218
2016-03-24 | 214 | 208
2016-03-24 00:30 | 260 | 255
2016-03-24 01:00 | 273 | 268
2016-03-24 01:30 | 265 | 260
2016-03-24 02:00 | 261 | 256
2016-03-24 02:30 | 256 | 252
2016-03-24 03:00 | 253 | 248
2016-03-24 03:30 | 251 | 247
2016-03-24 04:00 | 251 | 247
2016-03-24 04:30 | 250 | 245
2016-03-24 05:00 | 252 | 248
2016-03-24 05:30 | 258 | 254
2016-03-24 06:00 | 269 | 265
2016-03-24 06:30 | 284 | 280
2016-03-24 07:00 | 273 | 267
2016-03-24 07:30 | 293 | 288
2016-03-24 08:00 | 328 | 323
2016-03-24 08:30 | 331 | 326
2016-03-24 09:00 | 328 | 323
2016-03-24 09:30 | 322 | 317
2016-03-24 10:00 | 320 | 315
2016-03-24 10:30 | 309 | 304
2016-03-24 11:00 | 308 | 303
2016-03-24 11:30 | 312 | 307
2016-03-24 12:00 | 293 | 287
2016-03-24 12:30 | 278 | 272
2016-03-24 13:00 | 280 | 274
2016-03-24 13:30 | 261 | 255
2016-03-24 14:00 | 271 | 266
2016-03-24 14:30 | 274 | 269
2016-03-24 15:00 | 272 | 266
2016-03-24 15:30 | 268 | 263
2016-03-24 16:00 | 264 | 259
2016-03-24 16:30 | 263 | 257
2016-03-24 17:00 | 265 | 260
2016-03-24 17:30 | 263 | 258
2016-03-24 18:00 | 266 | 261
2016-03-24 18:30 | 267 | 262
2016-03-24 19:00 | 276 | 272
2016-03-24 19:30 | 276 | 271
2016-03-24 20:00 | 272 | 268
2016-03-24 20:30 | 267 | 262
2016-03-24 21:00 | 258 | 253
2016-03-24 21:30 | 244 | 238
2016-03-24 22:00 | 232 | 226
2016-03-24 22:30 | 229 | 223
2016-03-24 23:00 | 221 | 215
2016-03-24 23:30 | 211 | 205
2016-03-25 | 198 | 192
2016-03-25 00:30 | 245 | 241
2016-03-25 01:00 | 256 | 252
2016-03-25 01:30 | 249 | 245
2016-03-25 02:00 | 244 | 240
2016-03-25 02:30 | 240 | 236
2016-03-25 03:00 | 237 | 233
2016-03-25 03:30 | 237 | 232
2016-03-25 04:00 | 235 | 231
2016-03-25 04:30 | 235 | 230
2016-03-25 05:00 | 234 | 230
2016-03-25 05:30 | 236 | 231
2016-03-25 06:00 | 238 | 234
2016-03-25 06:30 | 242 | 238
2016-03-25 07:00 | 243 | 239
2016-03-25 07:30 | 251 | 247
2016-03-25 08:00 | 258 | 253
2016-03-25 08:30 | 262 | 257
2016-03-25 09:00 | 264 | 259
2016-03-25 09:30 | 259 | 254
2016-03-25 10:00 | 256 | 251
2016-03-25 10:30 | 252 | 247
2016-03-25 11:00 | 254 | 249
2016-03-25 11:30 | 257 | 252
2016-03-25 12:00 | 259 | 254
2016-03-25 12:30 | 264 | 259
2016-03-25 13:00 | 263 | 258
2016-03-25 13:30 | 257 | 252
2016-03-25 14:00 | 265 | 260
2016-03-25 14:30 | 267 | 262
2016-03-25 15:00 | 271 | 266
2016-03-25 15:30 | 278 | 273
2016-03-25 16:00 | 283 | 278
2016-03-25 16:30 | 289 | 285
2016-03-25 17:00 | 296 | 291
2016-03-25 17:30 | 302 | 298
2016-03-25 18:00 | 309 | 305
2016-03-25 18:30 | 313 | 309
2016-03-25 19:00 | 325 | 321
2016-03-25 19:30 | 327 | 323
2016-03-25 20:00 | 317 | 313
2016-03-25 20:30 | 310 | 306
2016-03-25 21:00 | 299 | 295
2016-03-25 21:30 | 292 | 287
2016-03-25 22:00 | 287 | 283
2016-03-25 22:30 | 288 | 284
2016-03-25 23:00 | 280 | 275
2016-03-25 23:30 | 270 | 265
2016-03-26 | 262 | 256
2016-03-26 00:30 | 255 | 249
2016-03-26 01:00 | 248 | 243
2016-03-26 01:30 | 243 | 238
2016-03-26 02:00 | 238 | 234
2016-03-26 02:30 | 236 | 232
2016-03-26 03:00 | 233 | 229
2016-03-26 03:30 | 232 | 227
2016-03-26 04:00 | 229 | 225
2016-03-26 04:30 | 229 | 225
2016-03-26 05:00 | 229 | 225
2016-03-26 05:30 | 230 | 226
2016-03-26 06:00 | 232 | 228
2016-03-26 06:30 | 235 | 231
2016-03-26 07:00 | 237 | 233
2016-03-26 07:30 | 247 | 243
2016-03-26 08:00 | 253 | 248
2016-03-26 08:30 | 260 | 255
2016-03-26 09:00 | 266 | 261
2016-03-26 09:30 | 263 | 257
2016-03-26 10:00 | 252 | 247
2016-03-26 10:30 | 251 | 246
2016-03-26 11:00 | 251 | 246
2016-03-26 11:30 | 251 | 246
2016-03-26 12:00 | 251 | 246
2016-03-26 12:30 | 252 | 247
2016-03-26 13:00 | 252 | 247
2016-03-26 13:30 | 252 | 247
2016-03-26 14:00 | 262 | 257
2016-03-26 14:30 | 271 | 267
2016-03-26 15:00 | 277 | 273
2016-03-26 15:30 | 284 | 280
2016-03-26 16:00 | 291 | 286
2016-03-26 16:30 | 298 | 294
2016-03-26 17:00 | 307 | 302
2016-03-26 17:30 | 314 | 310
2016-03-26 18:00 | 319 | 315
2016-03-26 18:30 | 321 | 317
2016-03-26 19:00 | 329 | 325
2016-03-26 19:30 | 332 | 327
2016-03-26 20:00 | 323 | 318
2016-03-26 20:30 | 313 | 308
2016-03-26 21:00 | 304 | 300
2016-03-26 21:30 | 297 | 292
2016-03-26 22:00 | 289 | 285
2016-03-26 22:30 | 287 | 282
2016-03-26 23:00 | 281 | 277
2016-03-26 23:30 | 273 | 268
2016-03-27 | 264 | 260
2016-03-27 00:30 | 257 | 252
2016-03-27 01:00 | 250 | 245
2016-03-27 01:30 | 246 | 241
2016-03-27 02:00 | 241 | 237
2016-03-27 02:30 | 238 | 233
2016-03-27 03:00 | 235 | 230
2016-03-27 03:30 | 234 | 230
2016-03-27 04:00 | 233 | 228
2016-03-27 04:30 | 232 | 227
2016-03-27 05:00 | 231 | 226
2016-03-27 05:30 | 232 | 227
2016-03-27 06:00 | 233 | 229
2016-03-27 06:30 | 235 | 231
2016-03-27 07:00 | 236 | 232
2016-03-27 07:30 | 242 | 239
2016-03-27 08:00 | 246 | 242
2016-03-27 08:30 | 253 | 249
2016-03-27 09:00 | 255 | 252
2016-03-27 09:30 | 254 | 251
2016-03-27 10:00 | 247 | 244
2016-03-27 10:30 | 246 | 243
2016-03-27 11:00 | 247 | 243
2016-03-27 11:30 | 252 | 248
2016-03-27 12:00 | 253 | 250
2016-03-27 12:30 | 256 | 252
2016-03-27 13:00 | 258 | 255
2016-03-27 13:30 | 259 | 255
2016-03-27 14:00 | 269 | 266
2016-03-27 14:30 | 276 | 272
2016-03-27 15:00 | 282 | 278
2016-03-27 15:30 | 290 | 287
2016-03-27 16:00 | 298 | 294
2016-03-27 16:30 | 302 | 298
2016-03-27 17:00 | 306 | 303
2016-03-27 17:30 | 312 | 308
2016-03-27 18:00 | 319 | 316
2016-03-27 18:30 | 322 | 319
2016-03-27 19:00 | 332 | 329
2016-03-27 19:30 | 333 | 331
2016-03-27 20:00 | 327 | 325
2016-03-27 20:30 | 319 | 317
2016-03-27 21:00 | 313 | 310
2016-03-27 21:30 | 305 | 302
2016-03-27 22:00 | 296 | 292
2016-03-27 22:30 | 295 | 292
2016-03-27 23:00 | 289 | 286
2016-03-27 23:30 | 279 | 275
2016-03-28 | 271 | 267
2016-03-28 00:30 | 262 | 258
2016-03-28 01:00 | 255 | 252
2016-03-28 01:30 | 252 | 249
2016-03-28 02:00 | 247 | 244
2016-03-28 02:30 | 245 | 241
2016-03-28 03:00 | 243 | 239
2016-03-28 03:30 | 242 | 238
2016-03-28 04:00 | 240 | 236
2016-03-28 04:30 | 240 | 236
2016-03-28 05:00 | 240 | 236
2016-03-28 05:30 | 240 | 236
2016-03-28 06:00 | 240 | 237
2016-03-28 06:30 | 246 | 242
2016-03-28 07:00 | 248 | 244
2016-03-28 07:30 | 256 | 253
2016-03-28 08:00 | 262 | 259
2016-03-28 08:30 | 269 | 266
2016-03-28 09:00 | 271 | 268
2016-03-28 09:30 | 269 | 266
2016-03-28 10:00 | 262 | 259
2016-03-28 10:30 | 263 | 260
2016-03-28 11:00 | 264 | 261
2016-03-28 11:30 | 268 | 265
2016-03-28 12:00 | 273 | 270
2016-03-28 12:30 | 276 | 273
2016-03-28 13:00 | 279 | 276
2016-03-28 13:30 | 280 | 277
2016-03-28 14:00 | 289 | 286
2016-03-28 14:30 | 295 | 292
2016-03-28 15:00 | 301 | 298
2016-03-28 15:30 | 308 | 305
2016-03-28 16:00 | 314 | 310
2016-03-28 16:30 | 318 | 315
2016-03-28 17:00 | 326 | 323
2016-03-28 17:30 | 335 | 333
2016-03-28 18:00 | 341 | 338
2016-03-28 18:30 | 346 | 343
2016-03-28 19:00 | 349 | 345
2016-03-28 19:30 | 329 | 325
2016-03-28 20:00 | 345 | 343
2016-03-28 20:30 | 341 | 338
2016-03-28 21:00 | 330 | 327
2016-03-28 21:30 | 319 | 316
2016-03-28 22:00 | 307 | 304
2016-03-28 22:30 | 302 | 298
2016-03-28 23:00 | 293 | 289
2016-03-28 23:30 | 281 | 278
2016-03-29 | 273 | 269
2016-03-29 00:30 | 264 | 260
2016-03-29 01:00 | 259 | 255
2016-03-29 01:30 | 254 | 250
2016-03-29 02:00 | 249 | 245
2016-03-29 02:30 | 247 | 244
2016-03-29 03:00 | 245 | 241
2016-03-29 03:30 | 244 | 240
2016-03-29 04:00 | 242 | 239
2016-03-29 04:30 | 240 | 237
2016-03-29 05:00 | 241 | 238
2016-03-29 05:30 | 246 | 243
2016-03-29 06:00 | 254 | 251
2016-03-29 06:30 | 267 | 264
2016-03-29 07:00 | 278 | 275
2016-03-29 07:30 | 297 | 294
2016-03-29 08:00 | 308 | 305
2016-03-29 08:30 | 318 | 315
2016-03-29 09:00 | 324 | 321
2016-03-29 09:30 | 321 | 318
2016-03-29 10:00 | 312 | 309
2016-03-29 10:30 | 314 | 310
2016-03-29 11:00 | 315 | 312
2016-03-29 11:30 | 321 | 317
2016-03-29 12:00 | 324 | 320
2016-03-29 12:30 | 325 | 322
2016-03-29 13:00 | 324 | 321
2016-03-29 13:30 | 326 | 322
2016-03-29 14:00 | 339 | 336
2016-03-29 14:30 | 345 | 341
2016-03-29 15:00 | 347 | 344
2016-03-29 15:30 | 348 | 345
2016-03-29 16:00 | 355 | 352
2016-03-29 16:30 | 342 | 338
2016-03-29 17:00 | 290 | 285
2016-03-29 17:30 | 286 | 281
2016-03-29 18:00 | 285 | 280
2016-03-29 18:30 | 289 | 285
2016-03-29 19:00 | 304 | 300
2016-03-29 19:30 | 306 | 302
2016-03-29 20:00 | 307 | 303
2016-03-29 20:30 | 297 | 294
2016-03-29 21:00 | 285 | 281
2016-03-29 21:30 | 273 | 269
2016-03-29 22:00 | 260 | 256
2016-03-29 22:30 | 244 | 240
2016-03-29 23:00 | 229 | 225
2016-03-29 23:30 | 238 | 235
2016-03-30 | 243 | 241
2016-03-30 00:30 | 264 | 262
2016-03-30 01:00 | 267 | 265
2016-03-30 01:30 | 262 | 260
2016-03-30 02:00 | 255 | 253
2016-03-30 02:30 | 253 | 251
2016-03-30 03:00 | 250 | 248
2016-03-30 03:30 | 250 | 247
2016-03-30 04:00 | 249 | 247
2016-03-30 04:30 | 249 | 247
2016-03-30 05:00 | 250 | 247
2016-03-30 05:30 | 253 | 251
2016-03-30 06:00 | 258 | 256
2016-03-30 06:30 | 272 | 270
2016-03-30 07:00 | 284 | 282
2016-03-30 07:30 | 300 | 298
2016-03-30 08:00 | 311 | 309
2016-03-30 08:30 | 318 | 315
2016-03-30 09:00 | 325 | 319
2016-03-30 09:30 | 323 | 317
2016-03-30 10:00 | 314 | 307
2016-03-30 10:30 | 316 | 310
2016-03-30 11:00 | 317 | 310
2016-03-30 11:30 | 310 | 303
2016-03-30 12:00 | 292 | 284
2016-03-30 12:30 | 295 | 288
2016-03-30 13:00 | 297 | 290
2016-03-30 13:30 | 298 | 291
2016-03-30 14:00 | 307 | 299
2016-03-30 14:30 | 307 | 305
2016-03-30 15:00 | 316 | 313
2016-03-30 15:30 | 322 | 320
2016-03-30 16:00 | 318 | 316
2016-03-30 16:30 | 284 | 281
2016-03-30 17:00 | 254 | 251
2016-03-30 17:30 | 253 | 250
2016-03-30 18:00 | 252 | 249
2016-03-30 18:30 | 256 | 252
2016-03-30 19:00 | 268 | 265
2016-03-30 19:30 | 281 | 278
2016-03-30 20:00 | 274 | 271
2016-03-30 20:30 | 262 | 259
2016-03-30 21:00 | 249 | 245
2016-03-30 21:30 | 237 | 233
2016-03-30 22:00 | 227 | 222
2016-03-30 22:30 | 210 | 205
2016-03-30 23:00 | 228 | 224
2016-03-30 23:30 | 228 | 224
2016-03-31 | 217 | 214
2016-03-31 00:30 | 208 | 204
2016-03-31 01:00 | 198 | 194
2016-03-31 01:30 | 190 | 185
2016-03-31 02:00 | 183 | 181
2016-03-31 02:30 | 180 | 179
2016-03-31 03:00 | 184 | 182
2016-03-31 03:30 | 187 | 186
2016-03-31 04:00 | 182 | 180
2016-03-31 04:30 | 179 | 178
2016-03-31 05:00 | 180 | 179
2016-03-31 05:30 | 185 | 183
2016-03-31 06:00 | 192 | 191
2016-03-31 06:30 | 170 | 169
2016-03-31 07:00 | 170 | 169
2016-03-31 07:30 | 184 | 182
2016-03-31 08:00 | 195 | 194
2016-03-31 08:30 | 203 | 201
2016-03-31 09:00 | 209 | 206
2016-03-31 09:30 | 206 | 203
2016-03-31 10:00 | 196 | 193
2016-03-31 10:30 | 198 | 195
2016-03-31 11:00 | 198 | 195
2016-03-31 11:30 | 201 | 198
2016-03-31 12:00 | 205 | 202
2016-03-31 12:30 | 208 | 205
2016-03-31 13:00 | 209 | 206
2016-03-31 13:30 | 195 | 191
2016-03-31 14:00 | 218 | 216
2016-03-31 14:30 | 226 | 224
2016-03-31 15:00 | 230 | 227
2016-03-31 15:30 | 239 | 236
2016-03-31 16:00 | 242 | 240
2016-03-31 16:30 | 247 | 245
2016-03-31 17:00 | 250 | 248
2016-03-31 17:30 | 247 | 244
2016-03-31 18:00 | 249 | 247
2016-03-31 18:30 | 256 | 254
2016-03-31 19:00 | 268 | 266
2016-03-31 19:30 | 267 | 264
2016-03-31 20:00 | 259 | 256
2016-03-31 20:30 | 257 | 255
2016-03-31 21:00 | 249 | 247
2016-03-31 21:30 | 267 | 264
2016-03-31 22:00 | 270 | 268
2016-03-31 22:30 | 254 | 251
2016-03-31 23:00 | 240 | 237
2016-03-31 23:30 | 228 | 225
2016-04-01 | 220 | 216
2016-04-01 00:30 | 210 | 207
2016-04-01 01:00 | 202 | 199
2016-04-01 01:30 | 195 | 192
2016-04-01 02:00 | 190 | 187
2016-04-01 02:30 | 186 | 184
2016-04-01 03:00 | 184 | 181
2016-04-01 03:30 | 182 | 180
2016-04-01 04:00 | 180 | 178
2016-04-01 04:30 | 179 | 176
2016-04-01 05:00 | 181 | 179
2016-04-01 05:30 | 188 | 185
2016-04-01 06:00 | 195 | 193
2016-04-01 06:30 | 207 | 205
2016-04-01 07:00 | 183 | 181
2016-04-01 07:30 | 188 | 186
2016-04-01 08:00 | 199 | 197
2016-04-01 08:30 | 184 | 181
2016-04-01 09:00 | 145 | 143
2016-04-01 09:30 | 143 | 140
2016-04-01 10:00 | 137 | 134
2016-04-01 10:30 | 141 | 137
2016-04-01 11:00 | 142 | 137
2016-04-01 11:30 | 142 | 137
2016-04-01 12:00 | 141 | 137
2016-04-01 12:30 | 145 | 140
2016-04-01 13:00 | 146 | 142
2016-04-01 13:30 | 152 | 148
2016-04-01 14:00 | 159 | 155
2016-04-01 14:30 | 154 | 150
2016-04-01 15:00 | 154 | 150
2016-04-01 15:30 | 157 | 154
2016-04-01 16:00 | 165 | 161
2016-04-01 16:30 | 248 | 241
2016-04-01 17:00 | 252 | 245
2016-04-01 17:30 | 251 | 244
2016-04-01 18:00 | 246 | 239
2016-04-01 18:30 | 248 | 241
2016-04-01 19:00 | 258 | 252
2016-04-01 19:30 | 268 | 262
2016-04-01 20:00 | 262 | 256
2016-04-01 20:30 | 283 | 276
2016-04-01 21:00 | 304 | 299
2016-04-01 21:30 | 337 | 332
2016-04-01 22:00 | 337 | 333
2016-04-01 22:30 | 324 | 319
2016-04-01 23:00 | 309 | 304
2016-04-01 23:30 | 299 | 294
2016-04-02 | 292 | 286
2016-04-02 00:30 | 279 | 276
2016-04-02 01:00 | 270 | 267
2016-04-02 01:30 | 263 | 260
2016-04-02 02:00 | 258 | 255
2016-04-02 02:30 | 257 | 254
2016-04-02 03:00 | 253 | 250
2016-04-02 03:30 | 252 | 249
2016-04-02 04:00 | 250 | 247
2016-04-02 04:30 | 249 | 246
2016-04-02 05:00 | 248 | 245
2016-04-02 05:30 | 251 | 248
2016-04-02 06:00 | 254 | 251
2016-04-02 06:30 | 257 | 255
2016-04-02 07:00 | 261 | 258
2016-04-02 07:30 | 272 | 268
2016-04-02 08:00 | 282 | 279
2016-04-02 08:30 | 295 | 291
2016-04-02 09:00 | 303 | 299
2016-04-02 09:30 | 303 | 299
2016-04-02 10:00 | 297 | 292
2016-04-02 10:30 | 294 | 290
2016-04-02 11:00 | 295 | 291
2016-04-02 11:30 | 252 | 247
2016-04-02 12:00 | 219 | 213
2016-04-02 12:30 | 222 | 217
2016-04-02 13:00 | 224 | 219
2016-04-02 13:30 | 231 | 226
2016-04-02 14:00 | 242 | 237
2016-04-02 14:30 | 236 | 231
2016-04-02 15:00 | 233 | 228
2016-04-02 15:30 | 237 | 232
2016-04-02 16:00 | 246 | 241
2016-04-02 16:30 | 250 | 246
2016-04-02 17:00 | 257 | 252
2016-04-02 17:30 | 260 | 255
2016-04-02 18:00 | 263 | 259
2016-04-02 18:30 | 266 | 262
2016-04-02 19:00 | 274 | 270
2016-04-02 19:30 | 273 | 269
2016-04-02 20:00 | 265 | 261
2016-04-02 20:30 | 328 | 325
2016-04-02 21:00 | 342 | 339
2016-04-02 21:30 | 335 | 332
2016-04-02 22:00 | 325 | 322
2016-04-02 22:30 | 314 | 311
2016-04-02 23:00 | 302 | 299
2016-04-02 23:30 | 293 | 290
2016-04-03 | 286 | 282
2016-04-03 00:30 | 277 | 273
2016-04-03 01:00 | 268 | 264
2016-04-03 01:30 | 261 | 258
2016-04-03 02:00 | 256 | 252
2016-04-03 02:30 | 253 | 250
2016-04-03 03:00 | 249 | 246
2016-04-03 03:30 | 248 | 244
2016-04-03 04:00 | 244 | 241
2016-04-03 04:30 | 244 | 241
2016-04-03 05:00 | 244 | 241
2016-04-03 05:30 | 244 | 241
2016-04-03 06:00 | 245 | 242
2016-04-03 06:30 | 246 | 243
2016-04-03 07:00 | 248 | 244
2016-04-03 07:30 | 255 | 251
2016-04-03 08:00 | 262 | 258
2016-04-03 08:30 | 266 | 263
2016-04-03 09:00 | 269 | 266
2016-04-03 09:30 | 266 | 263
2016-04-03 10:00 | 258 | 255
2016-04-03 10:30 | 257 | 253
2016-04-03 11:00 | 249 | 245
2016-04-03 11:30 | 244 | 240
2016-04-03 12:00 | 246 | 242
2016-04-03 12:30 | 250 | 246
2016-04-03 13:00 | 256 | 253
2016-04-03 13:30 | 260 | 257
2016-04-03 14:00 | 262 | 259
2016-04-03 14:30 | 274 | 271
2016-04-03 15:00 | 289 | 286
2016-04-03 15:30 | 299 | 295
2016-04-03 16:00 | 305 | 302
2016-04-03 16:30 | 312 | 309
2016-04-03 17:00 | 320 | 317
2016-04-03 17:30 | 329 | 326
2016-04-03 18:00 | 337 | 334
2016-04-03 18:30 | 339 | 336
2016-04-03 19:00 | 359 | 357
2016-04-03 19:30 | 360 | 357
2016-04-03 20:00 | 349 | 347
2016-04-03 20:30 | 349 | 347
2016-04-03 21:00 | 343 | 340
2016-04-03 21:30 | 332 | 329
2016-04-03 22:00 | 320 | 317
2016-04-03 22:30 | 307 | 303
2016-04-03 23:00 | 292 | 288
2016-04-03 23:30 | 278 | 276
2016-04-04 | 272 | 269
2016-04-04 00:30 | 263 | 260
2016-04-04 01:00 | 257 | 253
2016-04-04 01:30 | 253 | 249
2016-04-04 02:00 | 248 | 244
2016-04-04 02:30 | 247 | 243
2016-04-04 03:00 | 244 | 240
2016-04-04 03:30 | 242 | 238
2016-04-04 04:00 | 241 | 237
2016-04-04 04:30 | 239 | 234
2016-04-04 05:00 | 242 | 238
2016-04-04 05:30 | 247 | 243
2016-04-04 06:00 | 255 | 252
2016-04-04 06:30 | 268 | 265
2016-04-04 07:00 | 281 | 278
2016-04-04 07:30 | 295 | 292
2016-04-04 08:00 | 307 | 303
2016-04-04 08:30 | 317 | 314
2016-04-04 09:00 | 321 | 318
2016-04-04 09:30 | 313 | 310
2016-04-04 10:00 | 302 | 298
2016-04-04 10:30 | 303 | 300
2016-04-04 11:00 | 306 | 303
2016-04-04 11:30 | 310 | 306
2016-04-04 12:00 | 311 | 308
2016-04-04 12:30 | 314 | 310
2016-04-04 13:00 | 319 | 316
2016-04-04 13:30 | 323 | 319
2016-04-04 14:00 | 340 | 337
2016-04-04 14:30 | 289 | 285
2016-04-04 15:00 | 258 | 254
2016-04-04 15:30 | 263 | 259
2016-04-04 16:00 | 269 | 265
2016-04-04 16:30 | 273 | 269
2016-04-04 17:00 | 278 | 274
2016-04-04 17:30 | 277 | 273
2016-04-04 18:00 | 276 | 272
2016-04-04 18:30 | 282 | 278
2016-04-04 19:00 | 296 | 292
2016-04-04 19:30 | 309 | 306
2016-04-04 20:00 | 301 | 298
2016-04-04 20:30 | 290 | 287
2016-04-04 21:00 | 339 | 337
2016-04-04 21:30 | 344 | 342
2016-04-04 22:00 | 334 | 331
2016-04-04 22:30 | 318 | 315
2016-04-04 23:00 | 303 | 300
2016-04-04 23:30 | 290 | 287
2016-04-05 | 279 | 276
2016-04-05 00:30 | 272 | 268
2016-04-05 01:00 | 265 | 261
2016-04-05 01:30 | 260 | 256
2016-04-05 02:00 | 254 | 251
2016-04-05 02:30 | 249 | 245
2016-04-05 03:00 | 246 | 242
2016-04-05 03:30 | 245 | 241
2016-04-05 04:00 | 243 | 239
2016-04-05 04:30 | 244 | 240
2016-04-05 05:00 | 245 | 241
2016-04-05 05:30 | 251 | 247
2016-04-05 06:00 | 259 | 255
2016-04-05 06:30 | 271 | 268
2016-04-05 07:00 | 283 | 280
2016-04-05 07:30 | 298 | 295
2016-04-05 08:00 | 308 | 305
2016-04-05 08:30 | 315 | 313
2016-04-05 09:00 | 321 | 319
2016-04-05 09:30 | 316 | 313
2016-04-05 10:00 | 307 | 304
2016-04-05 10:30 | 309 | 306
2016-04-05 11:00 | 310 | 306
2016-04-05 11:30 | 311 | 308
2016-04-05 12:00 | 314 | 311
2016-04-05 12:30 | 316 | 313
2016-04-05 13:00 | 319 | 316
2016-04-05 13:30 | 331 | 328
2016-04-05 14:00 | 347 | 342
2016-04-05 14:30 | 339 | 333
2016-04-05 15:00 | 337 | 330
2016-04-05 15:30 | 339 | 332
2016-04-05 16:00 | 280 | 272
2016-04-05 16:30 | 263 | 258
2016-04-05 17:00 | 269 | 264
2016-04-05 17:30 | 270 | 264
2016-04-05 18:00 | 269 | 263
2016-04-05 18:30 | 277 | 271
2016-04-05 19:00 | 290 | 284
2016-04-05 19:30 | 302 | 297
2016-04-05 20:00 | 298 | 293
2016-04-05 20:30 | 287 | 282
2016-04-05 21:00 | 336 | 331
2016-04-05 21:30 | 342 | 338
2016-04-05 22:00 | 333 | 328
2016-04-05 22:30 | 315 | 311
2016-04-05 23:00 | 304 | 300
2016-04-05 23:30 | 292 | 287
2016-04-06 | 279 | 275
2016-04-06 00:30 | 271 | 268
2016-04-06 01:00 | 264 | 260
2016-04-06 01:30 | 258 | 254
2016-04-06 02:00 | 255 | 250
2016-04-06 02:30 | 251 | 247
2016-04-06 03:00 | 248 | 244
2016-04-06 03:30 | 247 | 242
2016-04-06 04:00 | 245 | 240
2016-04-06 04:30 | 245 | 240
2016-04-06 05:00 | 248 | 243
2016-04-06 05:30 | 250 | 245
2016-04-06 06:00 | 258 | 254
2016-04-06 06:30 | 272 | 268
2016-04-06 07:00 | 284 | 280
2016-04-06 07:30 | 299 | 296
2016-04-06 08:00 | 309 | 306
2016-04-06 08:30 | 336 | 332
2016-04-06 09:00 | 339 | 335
2016-04-06 09:30 | 339 | 331
2016-04-06 10:00 | 327 | 318
2016-04-06 10:30 | 329 | 319
2016-04-06 11:00 | 328 | 318
2016-04-06 11:30 | 332 | 322
2016-04-06 12:00 | 336 | 327
2016-04-06 12:30 | 340 | 331
2016-04-06 13:00 | 346 | 337
2016-04-06 13:30 | 358 | 350
2016-04-06 14:00 | 371 | 362
2016-04-06 14:30 | 310 | 300
2016-04-06 15:00 | 278 | 266
2016-04-06 15:30 | 279 | 268
2016-04-06 16:00 | 284 | 272
2016-04-06 16:30 | 289 | 278
2016-04-06 17:00 | 294 | 283
2016-04-06 17:30 | 295 | 284
2016-04-06 18:00 | 292 | 281
2016-04-06 18:30 | 302 | 291
2016-04-06 19:00 | 316 | 306
2016-04-06 19:30 | 328 | 319
2016-04-06 20:00 | 324 | 315
2016-04-06 20:30 | 314 | 305
2016-04-06 21:00 | 304 | 293
2016-04-06 21:30 | 356 | 347
2016-04-06 22:00 | 365 | 357
2016-04-06 22:30 | 347 | 338
2016-04-06 23:00 | 333 | 324
2016-04-06 23:30 | 321 | 312
2016-04-07 | 311 | 302
2016-04-07 00:30 | 302 | 292
2016-04-07 01:00 | 294 | 284
2016-04-07 01:30 | 287 | 277
2016-04-07 02:00 | 280 | 270
2016-04-07 02:30 | 276 | 267
2016-04-07 03:00 | 274 | 264
2016-04-07 03:30 | 273 | 263
2016-04-07 04:00 | 269 | 261
2016-04-07 04:30 | 269 | 261
2016-04-07 05:00 | 269 | 261
2016-04-07 05:30 | 273 | 265
2016-04-07 06:00 | 285 | 277
2016-04-07 06:30 | 303 | 294
2016-04-07 07:00 | 316 | 308
2016-04-07 07:30 | 330 | 322
2016-04-07 08:00 | 347 | 340
2016-04-07 08:30 | 355 | 348
2016-04-07 09:00 | 359 | 352
2016-04-07 09:30 | 356 | 349
2016-04-07 10:00 | 338 | 330
2016-04-07 10:30 | 337 | 329
2016-04-07 11:00 | 342 | 334
2016-04-07 11:30 | 350 | 342
2016-04-07 12:00 | 344 | 336
2016-04-07 12:30 | 342 | 333
2016-04-07 13:00 | 345 | 337
2016-04-07 13:30 | 352 | 344
2016-04-07 14:00 | 365 | 357
2016-04-07 14:30 | 358 | 349
2016-04-07 15:00 | 355 | 346
2016-04-07 15:30 | 357 | 348
2016-04-07 16:00 | 362 | 353
2016-04-07 16:30 | 364 | 355
2016-04-07 17:00 | 367 | 358
2016-04-07 17:30 | 339 | 329
2016-04-07 18:00 | 298 | 287
2016-04-07 18:30 | 294 | 283
2016-04-07 19:00 | 307 | 298
2016-04-07 19:30 | 319 | 310
2016-04-07 20:00 | 315 | 306
2016-04-07 20:30 | 303 | 294
2016-04-07 21:00 | 358 | 351
2016-04-07 21:30 | 366 | 359
2016-04-07 22:00 | 356 | 348
2016-04-07 22:30 | 342 | 333
2016-04-07 23:00 | 330 | 320
2016-04-07 23:30 | 318 | 308
2016-04-08 | 306 | 296
2016-04-08 00:30 | 297 | 288
2016-04-08 01:00 | 284 | 279
2016-04-08 01:30 | 277 | 273
2016-04-08 02:00 | 271 | 267
2016-04-08 02:30 | 269 | 265
2016-04-08 03:00 | 264 | 260
2016-04-08 03:30 | 264 | 260
2016-04-08 04:00 | 264 | 260
2016-04-08 04:30 | 263 | 259
2016-04-08 05:00 | 262 | 259
2016-04-08 05:30 | 270 | 267
2016-04-08 06:00 | 281 | 277
2016-04-08 06:30 | 299 | 294
2016-04-08 07:00 | 309 | 304
2016-04-08 07:30 | 324 | 319
2016-04-08 08:00 | 332 | 327
2016-04-08 08:30 | 340 | 336
2016-04-08 09:00 | 345 | 340
2016-04-08 09:30 | 334 | 329
2016-04-08 10:00 | 314 | 308
2016-04-08 10:30 | 315 | 310
2016-04-08 11:00 | 314 | 309
2016-04-08 11:30 | 311 | 305
2016-04-08 12:00 | 290 | 284
2016-04-08 12:30 | 253 | 247
2016-04-08 13:00 | 263 | 258
2016-04-08 13:30 | 268 | 263
2016-04-08 14:00 | 281 | 276
2016-04-08 14:30 | 270 | 265
2016-04-08 15:00 | 228 | 221
2016-04-08 15:30 | 212 | 204
2016-04-08 16:00 | 207 | 199
2016-04-08 16:30 | 218 | 211
2016-04-08 17:00 | 203 | 195
2016-04-08 17:30 | 211 | 203
2016-04-08 18:00 | 218 | 211
2016-04-08 18:30 | 255 | 249
2016-04-08 19:00 | 243 | 236
2016-04-08 19:30 | 289 | 284
2016-04-08 20:00 | 311 | 307
2016-04-08 20:30 | 304 | 300
2016-04-08 21:00 | 288 | 283
2016-04-08 21:30 | 334 | 330
2016-04-08 22:00 | 330 | 325
2016-04-08 22:30 | 314 | 309
2016-04-08 23:00 | 303 | 298
2016-04-08 23:30 | 293 | 288
2016-04-09 | 284 | 279
2016-04-09 00:30 | 271 | 266
2016-04-09 01:00 | 264 | 259
2016-04-09 01:30 | 257 | 252
2016-04-09 02:00 | 253 | 247
2016-04-09 02:30 | 249 | 243
2016-04-09 03:00 | 249 | 243
2016-04-09 03:30 | 247 | 241
2016-04-09 04:00 | 244 | 238
2016-04-09 04:30 | 244 | 238
2016-04-09 05:00 | 246 | 239
2016-04-09 05:30 | 246 | 240
2016-04-09 06:00 | 249 | 243
2016-04-09 06:30 | 252 | 246
2016-04-09 07:00 | 260 | 254
2016-04-09 07:30 | 269 | 264
2016-04-09 08:00 | 279 | 275
2016-04-09 08:30 | 291 | 286
2016-04-09 09:00 | 298 | 293
2016-04-09 09:30 | 276 | 271
2016-04-09 10:00 | 243 | 237
2016-04-09 10:30 | 252 | 247
2016-04-09 11:00 | 258 | 253
2016-04-09 11:30 | 267 | 262
2016-04-09 12:00 | 269 | 263
2016-04-09 12:30 | 283 | 278
2016-04-09 13:00 | 289 | 284
2016-04-09 13:30 | 294 | 289
2016-04-09 14:00 | 303 | 298
2016-04-09 14:30 | 305 | 299
2016-04-09 15:00 | 301 | 295
2016-04-09 15:30 | 301 | 296
2016-04-09 16:00 | 302 | 297
2016-04-09 16:30 | 208 | 201
2016-04-09 17:00 | 167 | 158
2016-04-09 17:30 | 162 | 154
2016-04-09 18:00 | 162 | 154
2016-04-09 18:30 | 90 | 77
2016-04-09 19:00 | 89 | 80
2016-04-09 19:30 | 168 | 163
2016-04-09 20:00 | 188 | 182
2016-04-09 20:30 | 195 | 190
2016-04-09 21:00 | 242 | 238
2016-04-09 21:30 | 255 | 250
2016-04-09 22:00 | 250 | 246
2016-04-09 22:30 | 242 | 237
2016-04-09 23:00 | 203 | 196
2016-04-09 23:30 | 205 | 198
2016-04-10 | 214 | 208
2016-04-10 00:30 | 268 | 263
2016-04-10 01:00 | 269 | 264
2016-04-10 01:30 | 264 | 258
2016-04-10 02:00 | 259 | 254
2016-04-10 02:30 | 256 | 251
2016-04-10 03:00 | 255 | 249
2016-04-10 03:30 | 251 | 245
2016-04-10 04:00 | 248 | 243
2016-04-10 04:30 | 248 | 243
2016-04-10 05:00 | 249 | 243
2016-04-10 05:30 | 249 | 243
2016-04-10 06:00 | 251 | 246
2016-04-10 06:30 | 257 | 252
2016-04-10 07:00 | 259 | 253
2016-04-10 07:30 | 265 | 260
2016-04-10 08:00 | 273 | 268
2016-04-10 08:30 | 282 | 277
2016-04-10 09:00 | 288 | 284
2016-04-10 09:30 | 289 | 284
2016-04-10 10:00 | 280 | 275
2016-04-10 10:30 | 277 | 271
2016-04-10 11:00 | 278 | 272
2016-04-10 11:30 | 277 | 271
2016-04-10 12:00 | 286 | 281
2016-04-10 12:30 | 288 | 282
2016-04-10 13:00 | 282 | 276
2016-04-10 13:30 | 288 | 282
2016-04-10 14:00 | 301 | 295
2016-04-10 14:30 | 293 | 287
2016-04-10 15:00 | 291 | 285
2016-04-10 15:30 | 297 | 291
2016-04-10 16:00 | 305 | 299
2016-04-10 16:30 | 311 | 305
2016-04-10 17:00 | 315 | 310
2016-04-10 17:30 | 295 | 290
2016-04-10 18:00 | 199 | 191
2016-04-10 18:30 | 192 | 184
2016-04-10 19:00 | 210 | 204
2016-04-10 19:30 | 258 | 252
2016-04-10 20:00 | 246 | 240
2016-04-10 20:30 | 239 | 233
2016-04-10 21:00 | 275 | 270
2016-04-10 21:30 | 316 | 312
2016-04-10 22:00 | 295 | 290
2016-04-10 22:30 | 251 | 245
2016-04-10 23:00 | 240 | 233
2016-04-10 23:30 | 234 | 228
2016-04-11 | 277 | 271
2016-04-11 00:30 | 268 | 262
2016-04-11 01:00 | 259 | 255
2016-04-11 01:30 | 257 | 253
2016-04-11 02:00 | 252 | 248
2016-04-11 02:30 | 248 | 244
2016-04-11 03:00 | 248 | 244
2016-04-11 03:30 | 247 | 243
2016-04-11 04:00 | 244 | 240
2016-04-11 04:30 | 246 | 242
2016-04-11 05:00 | 250 | 246
2016-04-11 05:30 | 257 | 253
2016-04-11 06:00 | 267 | 264
2016-04-11 06:30 | 246 | 243
2016-04-11 07:00 | 234 | 230
2016-04-11 07:30 | 303 | 300
2016-04-11 08:00 | 336 | 333
2016-04-11 08:30 | 343 | 339
2016-04-11 09:00 | 342 | 338
2016-04-11 09:30 | 336 | 332
2016-04-11 10:00 | 324 | 319
2016-04-11 10:30 | 327 | 322
2016-04-11 11:00 | 331 | 327
2016-04-11 11:30 | 336 | 332
2016-04-11 12:00 | 335 | 332
2016-04-11 12:30 | 336 | 332
2016-04-11 13:00 | 337 | 333
2016-04-11 13:30 | 347 | 344
2016-04-11 14:00 | 333 | 329
2016-04-11 14:30 | 282 | 277
2016-04-11 15:00 | 277 | 272
2016-04-11 15:30 | 285 | 280
2016-04-11 16:00 | 296 | 292
2016-04-11 16:30 | 243 | 238
2016-04-11 17:00 | 162 | 157
2016-04-11 17:30 | 156 | 151
2016-04-11 18:00 | 154 | 150
2016-04-11 18:30 | 169 | 165
2016-04-11 19:00 | 151 | 147
2016-04-11 19:30 | 142 | 138
2016-04-11 20:00 | 132 | 128
2016-04-11 20:30 | 169 | 166
2016-04-11 21:00 | 230 | 226
2016-04-11 21:30 | 306 | 302
2016-04-11 22:00 | 313 | 308
2016-04-11 22:30 | 312 | 307
2016-04-11 23:00 | 304 | 299
2016-04-11 23:30 | 288 | 283
2016-04-12 | 278 | 273
2016-04-12 00:30 | 268 | 263
2016-04-12 01:00 | 263 | 257
2016-04-12 01:30 | 259 | 254
2016-04-12 02:00 | 256 | 251
2016-04-12 02:30 | 255 | 249
2016-04-12 03:00 | 252 | 246
2016-04-12 03:30 | 250 | 244
2016-04-12 04:00 | 248 | 242
2016-04-12 04:30 | 248 | 242
2016-04-12 05:00 | 247 | 241
2016-04-12 05:30 | 234 | 228
2016-04-12 06:00 | 237 | 231
2016-04-12 06:30 | 240 | 234
2016-04-12 07:00 | 256 | 250
2016-04-12 07:30 | 273 | 268
2016-04-12 08:00 | 285 | 280
2016-04-12 08:30 | 286 | 281
2016-04-12 09:00 | 288 | 283
2016-04-12 09:30 | 280 | 275
2016-04-12 10:00 | 268 | 262
2016-04-12 10:30 | 268 | 262
2016-04-12 11:00 | 273 | 268
2016-04-12 11:30 | 277 | 271
2016-04-12 12:00 | 280 | 274
2016-04-12 12:30 | 285 | 280
2016-04-12 13:00 | 290 | 285
2016-04-12 13:30 | 297 | 293
2016-04-12 14:00 | 310 | 306
2016-04-12 14:30 | 265 | 259
2016-04-12 15:00 | 234 | 229
2016-04-12 15:30 | 218 | 211
2016-04-12 16:00 | 202 | 195
2016-04-12 16:30 | 203 | 196
2016-04-12 17:00 | 206 | 199
2016-04-12 17:30 | 204 | 197
2016-04-12 18:00 | 173 | 164
2016-04-12 18:30 | 87 | 77
2016-04-12 19:00 | 101 | 93
2016-04-12 19:30 | 235 | 231
2016-04-12 20:00 | 241 | 235
2016-04-12 20:30 | 276 | 271
2016-04-12 21:00 | 272 | 267
2016-04-12 21:30 | 325 | 322
2016-04-12 22:00 | 332 | 328
2016-04-12 22:30 | 320 | 315
2016-04-12 23:00 | 309 | 304
2016-04-12 23:30 | 296 | 291
2016-04-13 | 284 | 278
2016-04-13 00:30 | 270 | 265
2016-04-13 01:00 | 264 | 258
2016-04-13 01:30 | 258 | 252
2016-04-13 02:00 | 254 | 249
2016-04-13 02:30 | 250 | 245
2016-04-13 03:00 | 249 | 243
2016-04-13 03:30 | 249 | 243
2016-04-13 04:00 | 248 | 242
2016-04-13 04:30 | 246 | 240
2016-04-13 05:00 | 249 | 243
2016-04-13 05:30 | 257 | 252
2016-04-13 06:00 | 267 | 262
2016-04-13 06:30 | 286 | 281
2016-04-13 07:00 | 305 | 300
2016-04-13 07:30 | 321 | 317
2016-04-13 08:00 | 328 | 323
2016-04-13 08:30 | 330 | 325
2016-04-13 09:00 | 330 | 325
2016-04-13 09:30 | 325 | 320
2016-04-13 10:00 | 314 | 309
2016-04-13 10:30 | 314 | 308
2016-04-13 11:00 | 314 | 309
2016-04-13 11:30 | 317 | 312
2016-04-13 12:00 | 324 | 319
2016-04-13 12:30 | 327 | 323
2016-04-13 13:00 | 331 | 326
2016-04-13 13:30 | 341 | 337
2016-04-13 14:00 | 355 | 352
2016-04-13 14:30 | 349 | 345
2016-04-13 15:00 | 349 | 345
2016-04-13 15:30 | 353 | 349
2016-04-13 16:00 | 346 | 342
2016-04-13 16:30 | 284 | 279
2016-04-13 17:00 | 234 | 228
2016-04-13 17:30 | 183 | 176
2016-04-13 18:00 | 142 | 135
2016-04-13 18:30 | 149 | 142
2016-04-13 19:00 | 163 | 156
2016-04-13 19:30 | 189 | 184
2016-04-13 20:00 | 187 | 182
2016-04-13 20:30 | 191 | 185
2016-04-13 21:00 | 194 | 188
2016-04-13 21:30 | 281 | 277
2016-04-13 22:00 | 324 | 320
2016-04-13 22:30 | 256 | 251
2016-04-13 23:00 | 244 | 239
2016-04-13 23:30 | 238 | 233
2016-04-14 | 234 | 229
2016-04-14 00:30 | 231 | 227
2016-04-14 01:00 | 264 | 260
2016-04-14 01:30 | 271 | 268
2016-04-14 02:00 | 267 | 263
2016-04-14 02:30 | 265 | 261
2016-04-14 03:00 | 264 | 260
2016-04-14 03:30 | 240 | 236
2016-04-14 04:00 | 257 | 254
2016-04-14 04:30 | 259 | 255
2016-04-14 05:00 | 262 | 259
2016-04-14 05:30 | 271 | 266
2016-04-14 06:00 | 283 | 279
2016-04-14 06:30 | 300 | 296
2016-04-14 07:00 | 278 | 272
2016-04-14 07:30 | 306 | 302
2016-04-14 08:00 | 326 | 322
2016-04-14 08:30 | 350 | 346
2016-04-14 09:00 | 350 | 347
2016-04-14 09:30 | 342 | 338
2016-04-14 10:00 | 331 | 327
2016-04-14 10:30 | 328 | 324
2016-04-14 11:00 | 328 | 324
2016-04-14 11:30 | 328 | 324
2016-04-14 12:00 | 310 | 306
2016-04-14 12:30 | 274 | 269
2016-04-14 13:00 | 256 | 251
2016-04-14 13:30 | 266 | 261
2016-04-14 14:00 | 331 | 327
2016-04-14 14:30 | 345 | 342
2016-04-14 15:00 | 340 | 337
2016-04-14 15:30 | 299 | 293
2016-04-14 16:00 | 253 | 246
2016-04-14 16:30 | 253 | 246
2016-04-14 17:00 | 204 | 198
2016-04-14 17:30 | 158 | 151
2016-04-14 18:00 | 61 | 50
2016-04-14 18:30 | 19 | 2
2016-04-14 19:00 | 22 | 8
2016-04-14 19:30 | 97 | 93
2016-04-14 20:00 | 139 | 134
2016-04-14 20:30 | 175 | 170
2016-04-14 21:00 | 208 | 203
2016-04-14 21:30 | 202 | 197
2016-04-14 22:00 | 198 | 193
2016-04-14 22:30 | 123 | 117
2016-04-14 23:00 | 101 | 93
2016-04-14 23:30 | 168 | 163
2016-04-15 | 176 | 171
2016-04-15 00:30 | 210 | 205
2016-04-15 01:00 | 257 | 253
2016-04-15 01:30 | 255 | 250
2016-04-15 02:00 | 249 | 244
2016-04-15 02:30 | 247 | 242
2016-04-15 03:00 | 245 | 240
2016-04-15 03:30 | 243 | 238
2016-04-15 04:00 | 242 | 237
2016-04-15 04:30 | 242 | 237
2016-04-15 05:00 | 244 | 239
2016-04-15 05:30 | 253 | 249
2016-04-15 06:00 | 263 | 259
2016-04-15 06:30 | 284 | 280
2016-04-15 07:00 | 281 | 276
2016-04-15 07:30 | 305 | 301
2016-04-15 08:00 | 326 | 321
2016-04-15 08:30 | 331 | 326
2016-04-15 09:00 | 331 | 326
2016-04-15 09:30 | 328 | 323
2016-04-15 10:00 | 315 | 311
2016-04-15 10:30 | 314 | 309
2016-04-15 11:00 | 319 | 314
2016-04-15 11:30 | 325 | 320
2016-04-15 12:00 | 325 | 321
2016-04-15 12:30 | 326 | 322
2016-04-15 13:00 | 327 | 322
2016-04-15 13:30 | 327 | 323
2016-04-15 14:00 | 332 | 327
2016-04-15 14:30 | 325 | 320
2016-04-15 15:00 | 318 | 314
2016-04-15 15:30 | 275 | 268
2016-04-15 16:00 | 293 | 289
2016-04-15 16:30 | 320 | 316
2016-04-15 17:00 | 325 | 320
2016-04-15 17:30 | 322 | 317
2016-04-15 18:00 | 317 | 312
2016-04-15 18:30 | 315 | 310
2016-04-15 19:00 | 322 | 317
2016-04-15 19:30 | 332 | 327
2016-04-15 20:00 | 333 | 328
2016-04-15 20:30 | 328 | 323
2016-04-15 21:00 | 323 | 319
2016-04-15 21:30 | 315 | 311
2016-04-15 22:00 | 316 | 313
2016-04-15 22:30 | 312 | 308
2016-04-15 23:00 | 302 | 297
2016-04-15 23:30 | 261 | 256
2016-04-16 | 233 | 228
2016-04-16 00:30 | 209 | 203
2016-04-16 01:00 | 244 | 239
2016-04-16 01:30 | 255 | 251
2016-04-16 02:00 | 249 | 244
2016-04-16 02:30 | 245 | 240
2016-04-16 03:00 | 241 | 236
2016-04-16 03:30 | 237 | 232
2016-04-16 04:00 | 237 | 232
2016-04-16 04:30 | 235 | 230
2016-04-16 05:00 | 194 | 188
2016-04-16 05:30 | 192 | 186
2016-04-16 06:00 | 197 | 191
2016-04-16 06:30 | 205 | 199
2016-04-16 07:00 | 211 | 205
2016-04-16 07:30 | 238 | 233
2016-04-16 08:00 | 254 | 249
2016-04-16 08:30 | 265 | 261
2016-04-16 09:00 | 272 | 268
2016-04-16 09:30 | 274 | 270
2016-04-16 10:00 | 272 | 267
2016-04-16 10:30 | 274 | 269
2016-04-16 11:00 | 274 | 269
2016-04-16 11:30 | 275 | 270
2016-04-16 12:00 | 270 | 265
2016-04-16 12:30 | 270 | 265
2016-04-16 13:00 | 270 | 265
2016-04-16 13:30 | 272 | 267
2016-04-16 14:00 | 267 | 262
2016-04-16 14:30 | 255 | 250
2016-04-16 15:00 | 260 | 255
2016-04-16 15:30 | 262 | 257
2016-04-16 16:00 | 261 | 256
2016-04-16 16:30 | 265 | 260
2016-04-16 17:00 | 271 | 266
2016-04-16 17:30 | 278 | 273
2016-04-16 18:00 | 285 | 280
2016-04-16 18:30 | 292 | 287
2016-04-16 19:00 | 298 | 295
2016-04-16 19:30 | 308 | 304
2016-04-16 20:00 | 307 | 303
2016-04-16 20:30 | 300 | 296
2016-04-16 21:00 | 291 | 287
2016-04-16 21:30 | 283 | 279
2016-04-16 22:00 | 279 | 275
2016-04-16 22:30 | 274 | 269
2016-04-16 23:00 | 280 | 275
2016-04-16 23:30 | 264 | 258
2016-04-17 | 268 | 264
2016-04-17 00:30 | 260 | 257
2016-04-17 01:00 | 255 | 251
2016-04-17 01:30 | 248 | 245
2016-04-17 02:00 | 242 | 238
2016-04-17 02:30 | 237 | 233
2016-04-17 03:00 | 235 | 231
2016-04-17 03:30 | 232 | 228
2016-04-17 04:00 | 229 | 225
2016-04-17 04:30 | 226 | 222
2016-04-17 05:00 | 226 | 222
2016-04-17 05:30 | 229 | 225
2016-04-17 06:00 | 230 | 226
2016-04-17 06:30 | 236 | 232
2016-04-17 07:00 | 239 | 235
2016-04-17 07:30 | 245 | 241
2016-04-17 08:00 | 256 | 251
2016-04-17 08:30 | 262 | 257
2016-04-17 09:00 | 265 | 260
2016-04-17 09:30 | 264 | 260
2016-04-17 10:00 | 260 | 256
2016-04-17 10:30 | 259 | 255
2016-04-17 11:00 | 261 | 257
2016-04-17 11:30 | 261 | 256
2016-04-17 12:00 | 261 | 256
2016-04-17 12:30 | 269 | 264
2016-04-17 13:00 | 270 | 265
2016-04-17 13:30 | 280 | 275
2016-04-17 14:00 | 292 | 288
2016-04-17 14:30 | 281 | 277
2016-04-17 15:00 | 280 | 276
2016-04-17 15:30 | 279 | 275
2016-04-17 16:00 | 287 | 283
2016-04-17 16:30 | 294 | 289
2016-04-17 17:00 | 257 | 252
2016-04-17 17:30 | 258 | 253
2016-04-17 18:00 | 249 | 244
2016-04-17 18:30 | 260 | 255
2016-04-17 19:00 | 286 | 282
2016-04-17 19:30 | 292 | 288
2016-04-17 20:00 | 287 | 283
2016-04-17 20:30 | 276 | 272
2016-04-17 21:00 | 311 | 307
2016-04-17 21:30 | 319 | 315
2016-04-17 22:00 | 312 | 307
2016-04-17 22:30 | 300 | 296
2016-04-17 23:00 | 290 | 286
2016-04-17 23:30 | 279 | 274
2016-04-18 | 271 | 265
2016-04-18 00:30 | 260 | 255
2016-04-18 01:00 | 255 | 251
2016-04-18 01:30 | 246 | 242
2016-04-18 02:00 | 241 | 236
2016-04-18 02:30 | 238 | 233
2016-04-18 03:00 | 235 | 230
2016-04-18 03:30 | 234 | 229
2016-04-18 04:00 | 234 | 229
2016-04-18 04:30 | 234 | 229
2016-04-18 05:00 | 237 | 233
2016-04-18 05:30 | 245 | 240
2016-04-18 06:00 | 258 | 253
2016-04-18 06:30 | 277 | 273
2016-04-18 07:00 | 294 | 290
2016-04-18 07:30 | 312 | 308
2016-04-18 08:00 | 325 | 321
2016-04-18 08:30 | 332 | 328
2016-04-18 09:00 | 330 | 326
2016-04-18 09:30 | 323 | 319
2016-04-18 10:00 | 307 | 303
2016-04-18 10:30 | 304 | 299
2016-04-18 11:00 | 294 | 289
2016-04-18 11:30 | 288 | 282
2016-04-18 12:00 | 290 | 284
2016-04-18 12:30 | 293 | 287
2016-04-18 13:00 | 295 | 290
2016-04-18 13:30 | 302 | 297
2016-04-18 14:00 | 304 | 299
2016-04-18 14:30 | 304 | 299
2016-04-18 15:00 | 303 | 298
2016-04-18 15:30 | 321 | 316
2016-04-18 16:00 | 327 | 322
2016-04-18 16:30 | 332 | 327
2016-04-18 17:00 | 335 | 330
2016-04-18 17:30 | 292 | 286
2016-04-18 18:00 | 232 | 225
2016-04-18 18:30 | 214 | 208
2016-04-18 19:00 | 225 | 219
2016-04-18 19:30 | 272 | 267
2016-04-18 20:00 | 277 | 272
2016-04-18 20:30 | 277 | 272
2016-04-18 21:00 | 330 | 327
2016-04-18 21:30 | 322 | 318
2016-04-18 22:00 | 320 | 316
2016-04-18 22:30 | 314 | 310
2016-04-18 23:00 | 294 | 289
2016-04-18 23:30 | 232 | 226
2016-04-19 | 242 | 237
2016-04-19 00:30 | 267 | 263
2016-04-19 01:00 | 260 | 256
2016-04-19 01:30 | 251 | 246
2016-04-19 02:00 | 245 | 240
2016-04-19 02:30 | 242 | 236
2016-04-19 03:00 | 240 | 234
2016-04-19 03:30 | 237 | 231
2016-04-19 04:00 | 237 | 231
2016-04-19 04:30 | 237 | 231
2016-04-19 05:00 | 240 | 235
2016-04-19 05:30 | 248 | 242
2016-04-19 06:00 | 259 | 254
2016-04-19 06:30 | 274 | 269
2016-04-19 07:00 | 262 | 255
2016-04-19 07:30 | 293 | 287
2016-04-19 08:00 | 314 | 309
2016-04-19 08:30 | 328 | 322
2016-04-19 09:00 | 331 | 325
2016-04-19 09:30 | 325 | 319
2016-04-19 10:00 | 313 | 307
2016-04-19 10:30 | 312 | 306
2016-04-19 11:00 | 312 | 305
2016-04-19 11:30 | 321 | 315
2016-04-19 12:00 | 328 | 322
2016-04-19 12:30 | 327 | 322
2016-04-19 13:00 | 320 | 315
2016-04-19 13:30 | 411 | 406
2016-04-19 14:00 | 542 | 539
2016-04-19 14:30 | 533 | 531
2016-04-19 15:00 | 528 | 525
2016-04-19 15:30 | 532 | 529
2016-04-19 16:00 | 489 | 486
2016-04-19 16:30 | 436 | 432
2016-04-19 17:00 | 423 | 419
2016-04-19 17:30 | 433 | 428
2016-04-19 18:00 | 369 | 362
2016-04-19 18:30 | 254 | 247
2016-04-19 19:00 | 339 | 334
2016-04-19 19:30 | 445 | 441
2016-04-19 20:00 | 455 | 452
2016-04-19 20:30 | 488 | 486
2016-04-19 21:00 | 505 | 502
2016-04-19 21:30 | 484 | 481
2016-04-19 22:00 | 480 | 476
2016-04-19 22:30 | 411 | 407
2016-04-19 23:00 | 381 | 375
2016-04-19 23:30 | 331 | 324
2016-04-20 | 363 | 358
2016-04-20 00:30 | 398 | 393
2016-04-20 01:00 | 413 | 408
2016-04-20 01:30 | 402 | 397
2016-04-20 02:00 | 394 | 388
2016-04-20 02:30 | 388 | 383
2016-04-20 03:00 | 387 | 381
2016-04-20 03:30 | 387 | 381
2016-04-20 04:00 | 385 | 379
2016-04-20 04:30 | 384 | 378
2016-04-20 05:00 | 390 | 384
2016-04-20 05:30 | 404 | 399
2016-04-20 06:00 | 422 | 418
2016-04-20 06:30 | 450 | 446
2016-04-20 07:00 | 416 | 410
2016-04-20 07:30 | 457 | 452
2016-04-20 08:00 | 505 | 502
2016-04-20 08:30 | 514 | 512
2016-04-20 09:00 | 530 | 527
2016-04-20 09:30 | 517 | 514
2016-04-20 10:00 | 495 | 492
2016-04-20 10:30 | 499 | 496
2016-04-20 11:00 | 503 | 500
2016-04-20 11:30 | 510 | 507
2016-04-20 12:00 | 512 | 509
2016-04-20 12:30 | 515 | 512
2016-04-20 13:00 | 515 | 512
2016-04-20 13:30 | 532 | 529
2016-04-20 14:00 | 552 | 549
2016-04-20 14:30 | 539 | 537
2016-04-20 15:00 | 528 | 526
2016-04-20 15:30 | 528 | 526
2016-04-20 16:00 | 533 | 530
2016-04-20 16:30 | 543 | 541
2016-04-20 17:00 | 545 | 543
2016-04-20 17:30 | 539 | 536
2016-04-20 18:00 | 538 | 535
2016-04-20 18:30 | 541 | 538
2016-04-20 19:00 | 550 | 547
2016-04-20 19:30 | 563 | 560
2016-04-20 20:00 | 566 | 563
2016-04-20 20:30 | 552 | 550
2016-04-20 21:00 | 542 | 539
2016-04-20 21:30 | 526 | 523
2016-04-20 22:00 | 525 | 522
2016-04-20 22:30 | 519 | 516
2016-04-20 23:00 | 505 | 502
2016-04-20 23:30 | 487 | 483
2016-04-21 | 469 | 465
2016-04-21 00:30 | 448 | 443
2016-04-21 01:00 | 431 | 426
2016-04-21 01:30 | 416 | 411
2016-04-21 02:00 | 404 | 399
2016-04-21 02:30 | 398 | 393
2016-04-21 03:00 | 396 | 391
2016-04-21 03:30 | 393 | 388
2016-04-21 04:00 | 393 | 387
2016-04-21 04:30 | 394 | 388
2016-04-21 05:00 | 397 | 391
2016-04-21 05:30 | 410 | 405
2016-04-21 06:00 | 426 | 421
2016-04-21 06:30 | 451 | 447
2016-04-21 07:00 | 477 | 473
2016-04-21 07:30 | 501 | 497
2016-04-21 08:00 | 521 | 518
2016-04-21 08:30 | 532 | 529
2016-04-21 09:00 | 531 | 529
2016-04-21 09:30 | 522 | 519
2016-04-21 10:00 | 499 | 496
2016-04-21 10:30 | 498 | 494
2016-04-21 11:00 | 498 | 494
2016-04-21 11:30 | 502 | 498
2016-04-21 12:00 | 452 | 448
2016-04-21 12:30 | 434 | 429
2016-04-21 13:00 | 439 | 434
2016-04-21 13:30 | 442 | 436
2016-04-21 14:00 | 427 | 421
2016-04-21 14:30 | 420 | 414
2016-04-21 15:00 | 421 | 415
2016-04-21 15:30 | 442 | 436
2016-04-21 16:00 | 467 | 462
2016-04-21 16:30 | 468 | 463
2016-04-21 17:00 | 443 | 438
2016-04-21 17:30 | 406 | 400
2016-04-21 18:00 | 368 | 361
2016-04-21 18:30 | 275 | 269
2016-04-21 19:00 | 214 | 207
2016-04-21 19:30 | 301 | 295
2016-04-21 20:00 | 300 | 295
2016-04-21 20:30 | 300 | 294
2016-04-21 21:00 | 427 | 424
2016-04-21 21:30 | 478 | 475
2016-04-21 22:00 | 501 | 498
2016-04-21 22:30 | 416 | 410
2016-04-21 23:00 | 436 | 432
2016-04-21 23:30 | 433 | 429
2016-04-22 | 461 | 457
2016-04-22 00:30 | 450 | 446
2016-04-22 01:00 | 428 | 424
2016-04-22 01:30 | 407 | 403
2016-04-22 02:00 | 401 | 396
2016-04-22 02:30 | 395 | 389
2016-04-22 03:00 | 392 | 387
2016-04-22 03:30 | 390 | 385
2016-04-22 04:00 | 389 | 384
2016-04-22 04:30 | 392 | 387
2016-04-22 05:00 | 396 | 391
2016-04-22 05:30 | 405 | 400
2016-04-22 06:00 | 418 | 413
2016-04-22 06:30 | 406 | 400
2016-04-22 07:00 | 407 | 402
2016-04-22 07:30 | 483 | 480
2016-04-22 08:00 | 505 | 502
2016-04-22 08:30 | 520 | 518
2016-04-22 09:00 | 522 | 519
2016-04-22 09:30 | 502 | 499
2016-04-22 10:00 | 489 | 485
2016-04-22 10:30 | 488 | 485
2016-04-22 11:00 | 486 | 483
2016-04-22 11:30 | 488 | 484
2016-04-22 12:00 | 490 | 486
2016-04-22 12:30 | 502 | 498
2016-04-22 13:00 | 505 | 502
2016-04-22 13:30 | 497 | 494
2016-04-22 14:00 | 461 | 458
2016-04-22 14:30 | 382 | 378
2016-04-22 15:00 | 378 | 374
2016-04-22 15:30 | 353 | 349
2016-04-22 16:00 | 320 | 318
2016-04-22 16:30 | 337 | 335
2016-04-22 17:00 | 357 | 355
2016-04-22 17:30 | 345 | 343
2016-04-22 18:00 | 284 | 282
2016-04-22 18:30 | 274 | 272
2016-04-22 19:00 | 300 | 299
2016-04-22 19:30 | 402 | 401
2016-04-22 20:00 | 413 | 412
2016-04-22 20:30 | 404 | 403
2016-04-22 21:00 | 453 | 451
2016-04-22 21:30 | 439 | 438
2016-04-22 22:00 | 439 | 438
2016-04-22 22:30 | 375 | 373
2016-04-22 23:00 | 281 | 278
2016-04-22 23:30 | 283 | 281
2016-04-23 | 296 | 294
2016-04-23 00:30 | 336 | 334
2016-04-23 01:00 | 406 | 405
2016-04-23 01:30 | 401 | 400
2016-04-23 02:00 | 390 | 389
2016-04-23 02:30 | 383 | 381
2016-04-23 03:00 | 378 | 376
2016-04-23 03:30 | 375 | 373
2016-04-23 04:00 | 373 | 371
2016-04-23 04:30 | 372 | 371
2016-04-23 05:00 | 372 | 371
2016-04-23 05:30 | 375 | 374
2016-04-23 06:00 | 381 | 380
2016-04-23 06:30 | 393 | 391
2016-04-23 07:00 | 402 | 401
2016-04-23 07:30 | 417 | 416
2016-04-23 08:00 | 433 | 432
2016-04-23 08:30 | 444 | 442
2016-04-23 09:00 | 448 | 447
2016-04-23 09:30 | 442 | 440
2016-04-23 10:00 | 424 | 422
2016-04-23 10:30 | 429 | 427
2016-04-23 11:00 | 430 | 429
2016-04-23 11:30 | 423 | 422
2016-04-23 12:00 | 424 | 423
2016-04-23 12:30 | 427 | 426
2016-04-23 13:00 | 434 | 432
2016-04-23 13:30 | 442 | 440
2016-04-23 14:00 | 459 | 457
2016-04-23 14:30 | 440 | 439
2016-04-23 15:00 | 439 | 437
2016-04-23 15:30 | 442 | 440
2016-04-23 16:00 | 455 | 453
2016-04-23 16:30 | 389 | 387
2016-04-23 17:00 | 350 | 348
2016-04-23 17:30 | 361 | 359
2016-04-23 18:00 | 333 | 331
2016-04-23 18:30 | 350 | 349
2016-04-23 19:00 | 373 | 372
2016-04-23 19:30 | 523 | 522
2016-04-23 20:00 | 530 | 529
2016-04-23 20:30 | 520 | 518
2016-04-23 21:00 | 512 | 511
2016-04-23 21:30 | 495 | 493
2016-04-23 22:00 | 494 | 493
2016-04-23 22:30 | 472 | 471
2016-04-23 23:00 | 467 | 466
2016-04-23 23:30 | 458 | 457
2016-04-24 | 449 | 448
2016-04-24 00:30 | 429 | 427
2016-04-24 01:00 | 415 | 414
2016-04-24 01:30 | 398 | 396
2016-04-24 02:00 | 388 | 387
2016-04-24 02:30 | 382 | 381
2016-04-24 03:00 | 377 | 375
2016-04-24 03:30 | 372 | 369
2016-04-24 04:00 | 370 | 368
2016-04-24 04:30 | 373 | 370
2016-04-24 05:00 | 374 | 371
2016-04-24 05:30 | 376 | 373
2016-04-24 06:00 | 377 | 374
2016-04-24 06:30 | 380 | 377
2016-04-24 07:00 | 384 | 381
2016-04-24 07:30 | 392 | 389
2016-04-24 08:00 | 404 | 401
2016-04-24 08:30 | 416 | 414
2016-04-24 09:00 | 422 | 419
2016-04-24 09:30 | 419 | 417
2016-04-24 10:00 | 408 | 405
2016-04-24 10:30 | 407 | 405
2016-04-24 11:00 | 412 | 409
2016-04-24 11:30 | 415 | 412
2016-04-24 12:00 | 413 | 410
2016-04-24 12:30 | 414 | 411
2016-04-24 13:00 | 410 | 407
2016-04-24 13:30 | 425 | 422
2016-04-24 14:00 | 429 | 426
2016-04-24 14:30 | 414 | 411
2016-04-24 15:00 | 412 | 409
2016-04-24 15:30 | 424 | 421
2016-04-24 16:00 | 429 | 426
2016-04-24 16:30 | 441 | 438
2016-04-24 17:00 | 452 | 450
2016-04-24 17:30 | 461 | 458
2016-04-24 18:00 | 382 | 379
2016-04-24 18:30 | 375 | 371
2016-04-24 19:00 | 397 | 394
2016-04-24 19:30 | 413 | 410
2016-04-24 20:00 | 409 | 406
2016-04-24 20:30 | 400 | 397
2016-04-24 21:00 | 468 | 465
2016-04-24 21:30 | 490 | 488
2016-04-24 22:00 | 489 | 487
2016-04-24 22:30 | 461 | 458
2016-04-24 23:00 | 445 | 441
2016-04-24 23:30 | 398 | 394
2016-04-25 | 355 | 351
2016-04-25 00:30 | 390 | 387
2016-04-25 01:00 | 376 | 373
2016-04-25 01:30 | 394 | 392
2016-04-25 02:00 | 389 | 386
2016-04-25 02:30 | 383 | 380
2016-04-25 03:00 | 378 | 375
2016-04-25 03:30 | 374 | 371
2016-04-25 04:00 | 377 | 374
2016-04-25 04:30 | 377 | 374
2016-04-25 05:00 | 377 | 374
2016-04-25 05:30 | 380 | 377
2016-04-25 06:00 | 380 | 377
2016-04-25 06:30 | 391 | 388
2016-04-25 07:00 | 396 | 394
2016-04-25 07:30 | 404 | 402
2016-04-25 08:00 | 412 | 410
2016-04-25 08:30 | 421 | 419
2016-04-25 09:00 | 423 | 421
2016-04-25 09:30 | 412 | 409
2016-04-25 10:00 | 394 | 392
2016-04-25 10:30 | 394 | 392
2016-04-25 11:00 | 395 | 392
2016-04-25 11:30 | 393 | 390
2016-04-25 12:00 | 396 | 393
2016-04-25 12:30 | 396 | 394
2016-04-25 13:00 | 405 | 402
2016-04-25 13:30 | 420 | 418
2016-04-25 14:00 | 439 | 436
2016-04-25 14:30 | 426 | 423
2016-04-25 15:00 | 421 | 418
2016-04-25 15:30 | 429 | 426
2016-04-25 16:00 | 436 | 433
2016-04-25 16:30 | 451 | 449
2016-04-25 17:00 | 471 | 469
2016-04-25 17:30 | 487 | 484
2016-04-25 18:00 | 428 | 425
2016-04-25 18:30 | 345 | 341
2016-04-25 19:00 | 388 | 385
2016-04-25 19:30 | 505 | 504
2016-04-25 20:00 | 515 | 513
2016-04-25 20:30 | 476 | 474
2016-04-25 21:00 | 507 | 505
2016-04-25 21:30 | 496 | 494
2016-04-25 22:00 | 490 | 488
2016-04-25 22:30 | 459 | 456
2016-04-25 23:00 | 454 | 451
2016-04-25 23:30 | 409 | 406
2016-04-26 | 414 | 412
2016-04-26 00:30 | 416 | 414
2016-04-26 01:00 | 406 | 404
2016-04-26 01:30 | 395 | 392
2016-04-26 02:00 | 383 | 380
2016-04-26 02:30 | 378 | 374
2016-04-26 03:00 | 374 | 371
2016-04-26 03:30 | 372 | 369
2016-04-26 04:00 | 371 | 368
2016-04-26 04:30 | 373 | 370
2016-04-26 05:00 | 379 | 376
2016-04-26 05:30 | 391 | 388
2016-04-26 06:00 | 407 | 404
2016-04-26 06:30 | 366 | 362
2016-04-26 07:00 | 387 | 383
2016-04-26 07:30 | 452 | 450
2016-04-26 08:00 | 494 | 492
2016-04-26 08:30 | 502 | 500
2016-04-26 09:00 | 512 | 510
2016-04-26 09:30 | 500 | 498
2016-04-26 10:00 | 488 | 486
2016-04-26 10:30 | 486 | 484
2016-04-26 11:00 | 484 | 482
2016-04-26 11:30 | 487 | 485
2016-04-26 12:00 | 463 | 459
2016-04-26 12:30 | 484 | 481
2016-04-26 13:00 | 472 | 469
2016-04-26 13:30 | 486 | 483
2016-04-26 14:00 | 436 | 432
2016-04-26 14:30 | 372 | 368
2016-04-26 15:00 | 375 | 370
2016-04-26 15:30 | 367 | 362
2016-04-26 16:00 | 300 | 294
2016-04-26 16:30 | 258 | 252
2016-04-26 17:00 | 281 | 276
2016-04-26 17:30 | 382 | 377
2016-04-26 18:00 | 283 | 277
2016-04-26 18:30 | 300 | 295
2016-04-26 19:00 | 347 | 343
2016-04-26 19:30 | 417 | 414
2016-04-26 20:00 | 495 | 493
2016-04-26 20:30 | 455 | 453
2016-04-26 21:00 | 487 | 484
2016-04-26 21:30 | 470 | 468
2016-04-26 22:00 | 472 | 469
2016-04-26 22:30 | 333 | 330
2016-04-26 23:00 | 310 | 307
2016-04-26 23:30 | 328 | 325
2016-04-27 | 354 | 352
2016-04-27 00:30 | 404 | 402
2016-04-27 01:00 | 410 | 408
2016-04-27 01:30 | 400 | 398
2016-04-27 02:00 | 373 | 370
2016-04-27 02:30 | 379 | 376
2016-04-27 03:00 | 379 | 377
2016-04-27 03:30 | 378 | 375
2016-04-27 04:00 | 370 | 367
2016-04-27 04:30 | 365 | 361
2016-04-27 05:00 | 384 | 381
2016-04-27 05:30 | 399 | 397
2016-04-27 06:00 | 414 | 412
2016-04-27 06:30 | 378 | 375
2016-04-27 07:00 | 399 | 396
2016-04-27 07:30 | 467 | 465
2016-04-27 08:00 | 508 | 507
2016-04-27 08:30 | 517 | 516
2016-04-27 09:00 | 531 | 529
2016-04-27 09:30 | 514 | 512
2016-04-27 10:00 | 453 | 451
2016-04-27 10:30 | 441 | 438
2016-04-27 11:00 | 451 | 448
2016-04-27 11:30 | 452 | 449
2016-04-27 12:00 | 446 | 444
2016-04-27 12:30 | 453 | 450
2016-04-27 13:00 | 443 | 441
2016-04-27 13:30 | 370 | 367
2016-04-27 14:00 | 349 | 344
2016-04-27 14:30 | 277 | 271
2016-04-27 15:00 | 231 | 224
2016-04-27 15:30 | 231 | 225
2016-04-27 16:00 | 220 | 213
2016-04-27 16:30 | 215 | 208
2016-04-27 17:00 | 242 | 236
2016-04-27 17:30 | 162 | 155
2016-04-27 18:00 | 62 | 51
2016-04-27 18:30 | 116 | 109
2016-04-27 19:00 | 155 | 149
2016-04-27 19:30 | 194 | 188
2016-04-27 20:00 | 196 | 190
2016-04-27 20:30 | 181 | 175
2016-04-27 21:00 | 245 | 240
2016-04-27 21:30 | 204 | 199
2016-04-27 22:00 | 316 | 311
2016-04-27 22:30 | 76 | 67
2016-04-27 23:00 | 41 | 29
2016-04-27 23:30 | 66 | 57
2016-04-28 | 116 | 107
2016-04-28 00:30 | 243 | 237
2016-04-28 01:00 | 237 | 232
2016-04-28 01:30 | 281 | 276
2016-04-28 02:00 | 230 | 224
2016-04-28 02:30 | 269 | 263
2016-04-28 03:00 | 272 | 267
2016-04-28 03:30 | 274 | 268
2016-04-28 04:00 | 271 | 265
2016-04-28 04:30 | 273 | 267
2016-04-28 05:00 | 274 | 269
2016-04-28 05:30 | 205 | 199
2016-04-28 06:00 | 263 | 257
2016-04-28 06:30 | 232 | 226
2016-04-28 07:00 | 211 | 205
2016-04-28 07:30 | 270 | 265
2016-04-28 08:00 | 296 | 291
2016-04-28 08:30 | 285 | 280
2016-04-28 09:00 | 289 | 285
2016-04-28 09:30 | 265 | 261
2016-04-28 10:00 | 273 | 269
2016-04-28 10:30 | 326 | 323
2016-04-28 11:00 | 309 | 305
2016-04-28 11:30 | 371 | 368
2016-04-28 12:00 | 382 | 377
2016-04-28 12:30 | 383 | 379
2016-04-28 13:00 | 387 | 380
2016-04-28 13:30 | 398 | 390
2016-04-28 14:00 | 395 | 387
2016-04-28 14:30 | 339 | 330
2016-04-28 15:00 | 344 | 336
2016-04-28 15:30 | 384 | 377
2016-04-28 16:00 | 340 | 332
2016-04-28 16:30 | 245 | 234
2016-04-28 17:00 | 239 | 228
2016-04-28 17:30 | 239 | 228
2016-04-28 18:00 | 237 | 226
2016-04-28 18:30 | 237 | 226
2016-04-28 19:00 | 175 | 162
2016-04-28 19:30 | 268 | 259
2016-04-28 20:00 | 216 | 204
2016-04-28 20:30 | 172 | 159
2016-04-28 21:00 | 169 | 155
2016-04-28 21:30 | 330 | 322
2016-04-28 22:00 | 323 | 315
2016-04-28 22:30 | 181 | 166
2016-04-28 23:00 | 141 | 123
2016-04-28 23:30 | 211 | 197
2016-04-29 | 260 | 249
2016-04-29 00:30 | 257 | 246
2016-04-29 01:00 | 294 | 285
2016-04-29 01:30 | 292 | 283
2016-04-29 02:00 | 287 | 279
2016-04-29 02:30 | 283 | 275
2016-04-29 03:00 | 278 | 269
2016-04-29 03:30 | 281 | 272
2016-04-29 04:00 | 282 | 273
2016-04-29 04:30 | 284 | 276
2016-04-29 05:00 | 289 | 281
2016-04-29 05:30 | 248 | 238
2016-04-29 06:00 | 295 | 287
2016-04-29 06:30 | 285 | 277
2016-04-29 07:00 | 236 | 225
2016-04-29 07:30 | 358 | 350
2016-04-29 08:00 | 413 | 403
2016-04-29 08:30 | 421 | 411
2016-04-29 09:00 | 418 | 408
2016-04-29 09:30 | 420 | 411
2016-04-29 10:00 | 398 | 388
2016-04-29 10:30 | 410 | 400
2016-04-29 11:00 | 421 | 411
2016-04-29 11:30 | 408 | 398
2016-04-29 12:00 | 407 | 397
2016-04-29 12:30 | 402 | 392
2016-04-29 13:00 | 391 | 379
2016-04-29 13:30 | 403 | 390
2016-04-29 14:00 | 426 | 414
2016-04-29 14:30 | 414 | 402
2016-04-29 15:00 | 399 | 387
2016-04-29 15:30 | 399 | 386
2016-04-29 16:00 | 422 | 411
2016-04-29 16:30 | 366 | 353
2016-04-29 17:00 | 358 | 345
2016-04-29 17:30 | 345 | 331
2016-04-29 18:00 | 263 | 247
2016-04-29 18:30 | 240 | 224
2016-04-29 19:00 | 251 | 234
2016-04-29 19:30 | 293 | 280
2016-04-29 20:00 | 375 | 364
2016-04-29 20:30 | 387 | 376
2016-04-29 21:00 | 433 | 423
2016-04-29 21:30 | 421 | 411
2016-04-29 22:00 | 408 | 399
2016-04-29 22:30 | 391 | 381
2016-04-29 23:00 | 418 | 410
2016-04-29 23:30 | 466 | 458
2016-04-30 | 455 | 446
2016-04-30 00:30 | 439 | 431
2016-04-30 01:00 | 425 | 417
2016-04-30 01:30 | 393 | 384
2016-04-30 02:00 | 406 | 398
2016-04-30 02:30 | 402 | 393
2016-04-30 03:00 | 397 | 389
2016-04-30 03:30 | 394 | 386
2016-04-30 04:00 | 394 | 385
2016-04-30 04:30 | 393 | 385
2016-04-30 05:00 | 391 | 385
2016-04-30 05:30 | 398 | 392
2016-04-30 06:00 | 401 | 394
2016-04-30 06:30 | 416 | 410
2016-04-30 07:00 | 424 | 419
2016-04-30 07:30 | 443 | 438
2016-04-30 08:00 | 460 | 456
2016-04-30 08:30 | 477 | 473
2016-04-30 09:00 | 485 | 482
2016-04-30 09:30 | 466 | 461
2016-04-30 10:00 | 463 | 459
2016-04-30 10:30 | 462 | 458
2016-04-30 11:00 | 446 | 442
2016-04-30 11:30 | 440 | 436
2016-04-30 12:00 | 441 | 437
2016-04-30 12:30 | 439 | 435
2016-04-30 13:00 | 435 | 430
2016-04-30 13:30 | 436 | 432
2016-04-30 14:00 | 437 | 433
2016-04-30 14:30 | 445 | 441
2016-04-30 15:00 | 452 | 448
2016-04-30 15:30 | 461 | 457
2016-04-30 16:00 | 468 | 464
2016-04-30 16:30 | 478 | 474
2016-04-30 17:00 | 486 | 483
2016-04-30 17:30 | 507 | 504
2016-04-30 18:00 | 471 | 467
2016-04-30 18:30 | 454 | 450
2016-04-30 19:00 | 507 | 503
2016-04-30 19:30 | 524 | 521
2016-04-30 20:00 | 511 | 508
2016-04-30 20:30 | 515 | 512
2016-04-30 21:00 | 529 | 526
2016-04-30 21:30 | 518 | 515
2016-04-30 22:00 | 500 | 496
2016-04-30 22:30 | 466 | 462
2016-04-30 23:00 | 450 | 445
2016-04-30 23:30 | 435 | 429
2016-05-01 | 444 | 440
2016-05-01 00:30 | 436 | 431
2016-05-01 01:00 | 425 | 421
2016-05-01 01:30 | 414 | 410
2016-05-01 02:00 | 404 | 400
2016-05-01 02:30 | 398 | 394
2016-05-01 03:00 | 394 | 390
2016-05-01 03:30 | 392 | 388
2016-05-01 04:00 | 389 | 385
2016-05-01 04:30 | 388 | 384
2016-05-01 05:00 | 389 | 385
2016-05-01 05:30 | 389 | 385
2016-05-01 06:00 | 391 | 387
2016-05-01 06:30 | 400 | 397
2016-05-01 07:00 | 405 | 401
2016-05-01 07:30 | 415 | 412
2016-05-01 08:00 | 432 | 428
2016-05-01 08:30 | 444 | 440
2016-05-01 09:00 | 460 | 457
2016-05-01 09:30 | 449 | 445
2016-05-01 10:00 | 436 | 433
2016-05-01 10:30 | 445 | 441
2016-05-01 11:00 | 444 | 440
2016-05-01 11:30 | 440 | 437
2016-05-01 12:00 | 440 | 436
2016-05-01 12:30 | 440 | 436
2016-05-01 13:00 | 426 | 422
2016-05-01 13:30 | 419 | 414
2016-05-01 14:00 | 425 | 420
2016-05-01 14:30 | 431 | 427
2016-05-01 15:00 | 437 | 433
2016-05-01 15:30 | 443 | 439
2016-05-01 16:00 | 465 | 462
2016-05-01 16:30 | 492 | 488
2016-05-01 17:00 | 503 | 499
2016-05-01 17:30 | 494 | 490
2016-05-01 18:00 | 435 | 430
2016-05-01 18:30 | 359 | 353
2016-05-01 19:00 | 347 | 342
2016-05-01 19:30 | 370 | 366
2016-05-01 20:00 | 359 | 356
2016-05-01 20:30 | 329 | 325
2016-05-01 21:00 | 402 | 398
2016-05-01 21:30 | 419 | 415
2016-05-01 22:00 | 495 | 493
2016-05-01 22:30 | 491 | 488
2016-05-01 23:00 | 472 | 469
2016-05-01 23:30 | 444 | 440
2016-05-02 | 423 | 420
2016-05-02 00:30 | 432 | 429
2016-05-02 01:00 | 421 | 419
2016-05-02 01:30 | 412 | 409
2016-05-02 02:00 | 404 | 401
2016-05-02 02:30 | 399 | 396
2016-05-02 03:00 | 395 | 391
2016-05-02 03:30 | 394 | 391
2016-05-02 04:00 | 392 | 389
2016-05-02 04:30 | 391 | 388
2016-05-02 05:00 | 391 | 388
2016-05-02 05:30 | 393 | 390
2016-05-02 06:00 | 396 | 393
2016-05-02 06:30 | 406 | 403
2016-05-02 07:00 | 414 | 411
2016-05-02 07:30 | 426 | 423
2016-05-02 08:00 | 438 | 435
2016-05-02 08:30 | 449 | 446
2016-05-02 09:00 | 459 | 456
2016-05-02 09:30 | 450 | 447
2016-05-02 10:00 | 415 | 412
2016-05-02 10:30 | 408 | 405
2016-05-02 11:00 | 409 | 406
2016-05-02 11:30 | 410 | 406
2016-05-02 12:00 | 418 | 414
2016-05-02 12:30 | 421 | 417
2016-05-02 13:00 | 424 | 420
2016-05-02 13:30 | 429 | 425
2016-05-02 14:00 | 436 | 433
2016-05-02 14:30 | 453 | 450
2016-05-02 15:00 | 475 | 473
2016-05-02 15:30 | 491 | 487
2016-05-02 16:00 | 506 | 502
2016-05-02 16:30 | 508 | 505
2016-05-02 17:00 | 455 | 451
2016-05-02 17:30 | 421 | 417
2016-05-02 18:00 | 308 | 302
2016-05-02 18:30 | 319 | 313
2016-05-02 19:00 | 403 | 400
2016-05-02 19:30 | 507 | 504
2016-05-02 20:00 | 522 | 520
2016-05-02 20:30 | 562 | 560
2016-05-02 21:00 | 558 | 556
2016-05-02 21:30 | 541 | 539
2016-05-02 22:00 | 524 | 521
2016-05-02 22:30 | 498 | 495
2016-05-02 23:00 | 437 | 433
2016-05-02 23:30 | 434 | 430
2016-05-03 | 430 | 427
2016-05-03 00:30 | 436 | 433
2016-05-03 01:00 | 428 | 425
2016-05-03 01:30 | 415 | 412
2016-05-03 02:00 | 410 | 406
2016-05-03 02:30 | 407 | 403
2016-05-03 03:00 | 402 | 398
2016-05-03 03:30 | 400 | 395
2016-05-03 04:00 | 399 | 395
2016-05-03 04:30 | 402 | 398
2016-05-03 05:00 | 407 | 403
2016-05-03 05:30 | 415 | 411
2016-05-03 06:00 | 433 | 430
2016-05-03 06:30 | 434 | 430
2016-05-03 07:00 | 432 | 430
2016-05-03 07:30 | 354 | 350
2016-05-03 08:00 | 307 | 300
2016-05-03 08:30 | 383 | 379
2016-05-03 09:00 | 419 | 415
2016-05-03 09:30 | 444 | 441
2016-05-03 10:00 | 442 | 438
2016-05-03 10:30 | 441 | 438
2016-05-03 11:00 | 445 | 441
2016-05-03 11:30 | 450 | 447
2016-05-03 12:00 | 446 | 443
2016-05-03 12:30 | 390 | 386
2016-05-03 13:00 | 384 | 379
2016-05-03 13:30 | 408 | 404
2016-05-03 14:00 | 413 | 409
2016-05-03 14:30 | 422 | 418
2016-05-03 15:00 | 425 | 421
2016-05-03 15:30 | 425 | 421
2016-05-03 16:00 | 431 | 427
2016-05-03 16:30 | 432 | 428
2016-05-03 17:00 | 448 | 445
2016-05-03 17:30 | 445 | 441
2016-05-03 18:00 | 419 | 414
2016-05-03 18:30 | 435 | 431
2016-05-03 19:00 | 479 | 476
2016-05-03 19:30 | 470 | 467
2016-05-03 20:00 | 454 | 451
2016-05-03 20:30 | 455 | 451
2016-05-03 21:00 | 438 | 434
2016-05-03 21:30 | 417 | 413
2016-05-03 22:00 | 396 | 392
2016-05-03 22:30 | 384 | 379
2016-05-03 23:00 | 375 | 371
2016-05-03 23:30 | 359 | 355
2016-05-04 | 343 | 338
2016-05-04 00:30 | 328 | 322
2016-05-04 01:00 | 321 | 314
2016-05-04 01:30 | 312 | 305
2016-05-04 02:00 | 305 | 298
2016-05-04 02:30 | 302 | 295
2016-05-04 03:00 | 299 | 292
2016-05-04 03:30 | 297 | 289
2016-05-04 04:00 | 296 | 288
2016-05-04 04:30 | 296 | 289
2016-05-04 05:00 | 299 | 292
2016-05-04 05:30 | 311 | 304
2016-05-04 06:00 | 325 | 319
2016-05-04 06:30 | 354 | 348
2016-05-04 07:00 | 329 | 322
2016-05-04 07:30 | 323 | 316
2016-05-04 08:00 | 372 | 366
2016-05-04 08:30 | 375 | 368
2016-05-04 09:00 | 378 | 371
2016-05-04 09:30 | 375 | 368
2016-05-04 10:00 | 376 | 369
2016-05-04 10:30 | 380 | 374
2016-05-04 11:00 | 384 | 377
2016-05-04 11:30 | 386 | 380
2016-05-04 12:00 | 400 | 393
2016-05-04 12:30 | 404 | 397
2016-05-04 13:00 | 407 | 400
2016-05-04 13:30 | 411 | 404
2016-05-04 14:00 | 417 | 410
2016-05-04 14:30 | 418 | 412
2016-05-04 15:00 | 389 | 382
2016-05-04 15:30 | 394 | 387
2016-05-04 16:00 | 407 | 400
2016-05-04 16:30 | 441 | 434
2016-05-04 17:00 | 428 | 422
2016-05-04 17:30 | 359 | 350
2016-05-04 18:00 | 316 | 306
2016-05-04 18:30 | 331 | 323
2016-05-04 19:00 | 357 | 351
2016-05-04 19:30 | 349 | 342
2016-05-04 20:00 | 387 | 380
2016-05-04 20:30 | 414 | 408
2016-05-04 21:00 | 435 | 429
2016-05-04 21:30 | 417 | 410
2016-05-04 22:00 | 397 | 391
2016-05-04 22:30 | 425 | 419
2016-05-04 23:00 | 489 | 485
2016-05-04 23:30 | 472 | 467
2016-05-05 | 455 | 451
2016-05-05 00:30 | 443 | 439
2016-05-05 01:00 | 435 | 430
2016-05-05 01:30 | 424 | 419
2016-05-05 02:00 | 415 | 409
2016-05-05 02:30 | 414 | 407
2016-05-05 03:00 | 411 | 404
2016-05-05 03:30 | 409 | 402
2016-05-05 04:00 | 404 | 397
2016-05-05 04:30 | 406 | 399
2016-05-05 05:00 | 411 | 404
2016-05-05 05:30 | 425 | 418
2016-05-05 06:00 | 437 | 431
2016-05-05 06:30 | 452 | 446
2016-05-05 07:00 | 422 | 416
2016-05-05 07:30 | 418 | 412
2016-05-05 08:00 | 423 | 417
2016-05-05 08:30 | 407 | 401
2016-05-05 09:00 | 472 | 466
2016-05-05 09:30 | 501 | 494
2016-05-05 10:00 | 504 | 498
2016-05-05 10:30 | 507 | 501
2016-05-05 11:00 | 526 | 521
2016-05-05 11:30 | 524 | 519
2016-05-05 12:00 | 504 | 498
2016-05-05 12:30 | 504 | 499
2016-05-05 13:00 | 503 | 498
2016-05-05 13:30 | 508 | 503
2016-05-05 14:00 | 516 | 511
2016-05-05 14:30 | 524 | 519
2016-05-05 15:00 | 514 | 510
2016-05-05 15:30 | 510 | 505
2016-05-05 16:00 | 515 | 510
2016-05-05 16:30 | 520 | 515
2016-05-05 17:00 | 526 | 521
2016-05-05 17:30 | 466 | 461
2016-05-05 18:00 | 446 | 442
2016-05-05 18:30 | 490 | 487
2016-05-05 19:00 | 489 | 486
2016-05-05 19:30 | 523 | 521
2016-05-05 20:00 | 550 | 547
2016-05-05 20:30 | 547 | 544
2016-05-05 21:00 | 530 | 527
2016-05-05 21:30 | 492 | 488
2016-05-05 22:00 | 468 | 464
2016-05-05 22:30 | 474 | 470
2016-05-05 23:00 | 487 | 483
2016-05-05 23:30 | 473 | 469
2016-05-06 | 461 | 457
2016-05-06 00:30 | 445 | 441
2016-05-06 01:00 | 428 | 424
2016-05-06 01:30 | 419 | 415
2016-05-06 02:00 | 411 | 407
2016-05-06 02:30 | 408 | 403
2016-05-06 03:00 | 405 | 401
2016-05-06 03:30 | 404 | 399
2016-05-06 04:00 | 403 | 399
2016-05-06 04:30 | 400 | 396
2016-05-06 05:00 | 402 | 398
2016-05-06 05:30 | 414 | 410
2016-05-06 06:00 | 431 | 427
2016-05-06 06:30 | 454 | 450
2016-05-06 07:00 | 424 | 419
2016-05-06 07:30 | 417 | 412
2016-05-06 08:00 | 404 | 398
2016-05-06 08:30 | 437 | 433
2016-05-06 09:00 | 473 | 470
2016-05-06 09:30 | 467 | 464
2016-05-06 10:00 | 473 | 469
2016-05-06 10:30 | 472 | 469
2016-05-06 11:00 | 472 | 468
2016-05-06 11:30 | 497 | 494
2016-05-06 12:00 | 501 | 498
2016-05-06 12:30 | 501 | 497
2016-05-06 13:00 | 504 | 501
2016-05-06 13:30 | 507 | 504
2016-05-06 14:00 | 509 | 506
2016-05-06 14:30 | 479 | 475
2016-05-06 15:00 | 486 | 483
2016-05-06 15:30 | 494 | 490
2016-05-06 16:00 | 481 | 477
2016-05-06 16:30 | 494 | 491
2016-05-06 17:00 | 507 | 504
2016-05-06 17:30 | 497 | 494
2016-05-06 18:00 | 443 | 438
2016-05-06 18:30 | 472 | 468
2016-05-06 19:00 | 527 | 525
2016-05-06 19:30 | 520 | 517
2016-05-06 20:00 | 508 | 505
2016-05-06 20:30 | 495 | 491
2016-05-06 21:00 | 479 | 475
2016-05-06 21:30 | 468 | 464
2016-05-06 22:00 | 450 | 446
2016-05-06 22:30 | 442 | 438
2016-05-06 23:00 | 432 | 429
2016-05-06 23:30 | 434 | 431
2016-05-07 | 443 | 440
2016-05-07 00:30 | 438 | 435
2016-05-07 01:00 | 425 | 422
2016-05-07 01:30 | 417 | 414
2016-05-07 02:00 | 410 | 406
2016-05-07 02:30 | 401 | 398
2016-05-07 03:00 | 394 | 392
2016-05-07 03:30 | 394 | 391
2016-05-07 04:00 | 391 | 388
2016-05-07 04:30 | 389 | 386
2016-05-07 05:00 | 390 | 388
2016-05-07 05:30 | 395 | 392
2016-05-07 06:00 | 400 | 397
2016-05-07 06:30 | 407 | 404
2016-05-07 07:00 | 387 | 384
2016-05-07 07:30 | 391 | 388
2016-05-07 08:00 | 406 | 403
2016-05-07 08:30 | 423 | 420
2016-05-07 09:00 | 433 | 430
2016-05-07 09:30 | 412 | 408
2016-05-07 10:00 | 435 | 432
2016-05-07 10:30 | 433 | 430
2016-05-07 11:00 | 414 | 410
2016-05-07 11:30 | 410 | 406
2016-05-07 12:00 | 407 | 403
2016-05-07 12:30 | 406 | 402
2016-05-07 13:00 | 407 | 403
2016-05-07 13:30 | 411 | 407
2016-05-07 14:00 | 414 | 410
2016-05-07 14:30 | 416 | 412
2016-05-07 15:00 | 417 | 414
2016-05-07 15:30 | 429 | 425
2016-05-07 16:00 | 440 | 437
2016-05-07 16:30 | 446 | 442
2016-05-07 17:00 | 449 | 446
2016-05-07 17:30 | 458 | 456
2016-05-07 18:00 | 406 | 401
2016-05-07 18:30 | 431 | 426
2016-05-07 19:00 | 469 | 466
2016-05-07 19:30 | 498 | 496
2016-05-07 20:00 | 495 | 491
2016-05-07 20:30 | 491 | 488
2016-05-07 21:00 | 477 | 474
2016-05-07 21:30 | 466 | 462
2016-05-07 22:00 | 455 | 451
2016-05-07 22:30 | 412 | 407
2016-05-07 23:00 | 433 | 428
2016-05-07 23:30 | 433 | 428
2016-05-08 | 431 | 427
2016-05-08 00:30 | 428 | 424
2016-05-08 01:00 | 418 | 414
2016-05-08 01:30 | 408 | 403
2016-05-08 02:00 | 401 | 396
2016-05-08 02:30 | 394 | 389
2016-05-08 03:00 | 388 | 384
2016-05-08 03:30 | 384 | 380
2016-05-08 04:00 | 383 | 378
2016-05-08 04:30 | 384 | 379
2016-05-08 05:00 | 384 | 380
2016-05-08 05:30 | 387 | 383
2016-05-08 06:00 | 388 | 383
2016-05-08 06:30 | 397 | 392
2016-05-08 07:00 | 369 | 363
2016-05-08 07:30 | 368 | 363
2016-05-08 08:00 | 383 | 377
2016-05-08 08:30 | 399 | 394
2016-05-08 09:00 | 408 | 403
2016-05-08 09:30 | 376 | 370
2016-05-08 10:00 | 368 | 362
2016-05-08 10:30 | 364 | 358
2016-05-08 11:00 | 388 | 382
2016-05-08 11:30 | 394 | 388
2016-05-08 12:00 | 396 | 391
2016-05-08 12:30 | 395 | 390
2016-05-08 13:00 | 394 | 389
2016-05-08 13:30 | 394 | 389
2016-05-08 14:00 | 397 | 392
2016-05-08 14:30 | 363 | 357
2016-05-08 15:00 | 393 | 388
2016-05-08 15:30 | 406 | 402
2016-05-08 16:00 | 417 | 412
2016-05-08 16:30 | 428 | 423
2016-05-08 17:00 | 434 | 429
2016-05-08 17:30 | 429 | 424
2016-05-08 18:00 | 427 | 422
2016-05-08 18:30 | 444 | 439
2016-05-08 19:00 | 488 | 486
2016-05-08 19:30 | 509 | 506
2016-05-08 20:00 | 501 | 499
2016-05-08 20:30 | 484 | 481
2016-05-08 21:00 | 479 | 476
2016-05-08 21:30 | 471 | 468
2016-05-08 22:00 | 458 | 454
2016-05-08 22:30 | 447 | 443
2016-05-08 23:00 | 459 | 456
2016-05-08 23:30 | 445 | 442
2016-05-09 | 427 | 423
2016-05-09 00:30 | 425 | 421
2016-05-09 01:00 | 416 | 411
2016-05-09 01:30 | 405 | 400
2016-05-09 02:00 | 400 | 395
2016-05-09 02:30 | 394 | 390
2016-05-09 03:00 | 391 | 387
2016-05-09 03:30 | 390 | 386
2016-05-09 04:00 | 391 | 387
2016-05-09 04:30 | 390 | 386
2016-05-09 05:00 | 392 | 388
2016-05-09 05:30 | 410 | 406
2016-05-09 06:00 | 427 | 423
2016-05-09 06:30 | 454 | 450
2016-05-09 07:00 | 451 | 448
2016-05-09 07:30 | 474 | 470
2016-05-09 08:00 | 485 | 480
2016-05-09 08:30 | 489 | 483
2016-05-09 09:00 | 479 | 474
2016-05-09 09:30 | 407 | 399
2016-05-09 10:00 | 418 | 411
2016-05-09 10:30 | 366 | 357
2016-05-09 11:00 | 356 | 348
2016-05-09 11:30 | 349 | 341
2016-05-09 12:00 | 351 | 343
2016-05-09 12:30 | 367 | 361
2016-05-09 13:00 | 361 | 354
2016-05-09 13:30 | 346 | 338
2016-05-09 14:00 | 331 | 323
2016-05-09 14:30 | 354 | 347
2016-05-09 15:00 | 360 | 354
2016-05-09 15:30 | 365 | 358
2016-05-09 16:00 | 325 | 317
2016-05-09 16:30 | 383 | 374
2016-05-09 17:00 | 386 | 377
2016-05-09 17:30 | 240 | 228
2016-05-09 18:00 | 222 | 212
2016-05-09 18:30 | 168 | 159
2016-05-09 19:00 | 210 | 204
2016-05-09 19:30 | 248 | 241
2016-05-09 20:00 | 229 | 220
2016-05-09 20:30 | 209 | 201
2016-05-09 21:00 | 223 | 216
2016-05-09 21:30 | 212 | 205
2016-05-09 22:00 | 201 | 194
2016-05-09 22:30 | 230 | 222
2016-05-09 23:00 | 269 | 261
2016-05-09 23:30 | 265 | 259
2016-05-10 | 260 | 253
2016-05-10 00:30 | 260 | 254
2016-05-10 01:00 | 253 | 245
2016-05-10 01:30 | 258 | 251
2016-05-10 02:00 | 257 | 250
2016-05-10 02:30 | 255 | 248
2016-05-10 03:00 | 253 | 246
2016-05-10 03:30 | 251 | 244
2016-05-10 04:00 | 250 | 243
2016-05-10 04:30 | 250 | 243
2016-05-10 05:00 | 231 | 223
2016-05-10 05:30 | 216 | 207
2016-05-10 06:00 | 223 | 215
2016-05-10 06:30 | 243 | 235
2016-05-10 07:00 | 266 | 257
2016-05-10 07:30 | 278 | 270
2016-05-10 08:00 | 296 | 289
2016-05-10 08:30 | 269 | 260
2016-05-10 09:00 | 257 | 248
2016-05-10 09:30 | 263 | 256
2016-05-10 10:00 | 264 | 257
2016-05-10 10:30 | 267 | 259
2016-05-10 11:00 | 270 | 263
2016-05-10 11:30 | 254 | 248
2016-05-10 12:00 | 200 | 197
2016-05-10 12:30 | 166 | 162
2016-05-10 13:00 | 170 | 166
2016-05-10 13:30 | 174 | 170
2016-05-10 14:00 | 180 | 176
2016-05-10 14:30 | 183 | 179
2016-05-10 15:00 | 184 | 179
2016-05-10 15:30 | 184 | 180
2016-05-10 16:00 | 187 | 184
2016-05-10 16:30 | 191 | 188
2016-05-10 17:00 | 191 | 188
2016-05-10 17:30 | 189 | 186
2016-05-10 18:00 | 152 | 147
2016-05-10 18:30 | 170 | 165
2016-05-10 19:00 | 182 | 178
2016-05-10 19:30 | 201 | 198
2016-05-10 20:00 | 206 | 203
2016-05-10 20:30 | 197 | 193
2016-05-10 21:00 | 187 | 184
2016-05-10 21:30 | 175 | 171
2016-05-10 22:00 | 162 | 158
2016-05-10 22:30 | 193 | 190
2016-05-10 23:00 | 241 | 239
2016-05-10 23:30 | 232 | 229
2016-05-11 | 223 | 220
2016-05-11 00:30 | 218 | 214
2016-05-11 01:00 | 212 | 208
2016-05-11 01:30 | 207 | 203
2016-05-11 02:00 | 203 | 199
2016-05-11 02:30 | 201 | 197
2016-05-11 03:00 | 200 | 196
2016-05-11 03:30 | 198 | 194
2016-05-11 04:00 | 198 | 194
2016-05-11 04:30 | 199 | 194
2016-05-11 05:00 | 199 | 195
2016-05-11 05:30 | 206 | 203
2016-05-11 06:00 | 213 | 210
2016-05-11 06:30 | 210 | 206
2016-05-11 07:00 | 213 | 210
2016-05-11 07:30 | 230 | 227
2016-05-11 08:00 | 235 | 232
2016-05-11 08:30 | 227 | 224
2016-05-11 09:00 | 231 | 228
2016-05-11 09:30 | 234 | 231
2016-05-11 10:00 | 235 | 232
2016-05-11 10:30 | 232 | 230
2016-05-11 11:00 | 233 | 230
2016-05-11 11:30 | 232 | 229
2016-05-11 12:00 | 232 | 229
2016-05-11 12:30 | 222 | 219
2016-05-11 13:00 | 219 | 215
2016-05-11 13:30 | 222 | 219
2016-05-11 14:00 | 221 | 218
2016-05-11 14:30 | 226 | 223
2016-05-11 15:00 | 226 | 223
2016-05-11 15:30 | 224 | 221
2016-05-11 16:00 | 224 | 221
2016-05-11 16:30 | 226 | 222
2016-05-11 17:00 | 225 | 221
2016-05-11 17:30 | 226 | 223
2016-05-11 18:00 | 221 | 217
2016-05-11 18:30 | 238 | 235
2016-05-11 19:00 | 247 | 244
2016-05-11 19:30 | 239 | 236
2016-05-11 20:00 | 231 | 228
2016-05-11 20:30 | 222 | 219
2016-05-11 21:00 | 212 | 210
2016-05-11 21:30 | 203 | 200
2016-05-11 22:00 | 194 | 190
2016-05-11 22:30 | 194 | 191
2016-05-11 23:00 | 189 | 185
2016-05-11 23:30 | 177 | 173
2016-05-12 | 174 | 170
2016-05-12 00:30 | 186 | 183
2016-05-12 01:00 | 183 | 180
2016-05-12 01:30 | 179 | 176
2016-05-12 02:00 | 176 | 173
2016-05-12 02:30 | 175 | 171
2016-05-12 03:00 | 173 | 169
2016-05-12 03:30 | 172 | 169
2016-05-12 04:00 | 173 | 170
2016-05-12 04:30 | 174 | 171
2016-05-12 05:00 | 176 | 173
2016-05-12 05:30 | 184 | 181
2016-05-12 06:00 | 190 | 188
2016-05-12 06:30 | 207 | 203
2016-05-12 07:00 | 203 | 199
2016-05-12 07:30 | 208 | 205
2016-05-12 08:00 | 218 | 215
2016-05-12 08:30 | 220 | 217
2016-05-12 09:00 | 197 | 193
2016-05-12 09:30 | 194 | 190
2016-05-12 10:00 | 188 | 184
2016-05-12 10:30 | 179 | 175
2016-05-12 11:00 | 178 | 174
2016-05-12 11:30 | 177 | 173
2016-05-12 12:00 | 179 | 176
2016-05-12 12:30 | 191 | 187
2016-05-12 13:00 | 193 | 189
2016-05-12 13:30 | 194 | 191
2016-05-12 14:00 | 200 | 196
2016-05-12 14:30 | 200 | 197
2016-05-12 15:00 | 203 | 200
2016-05-12 15:30 | 207 | 204
2016-05-12 16:00 | 214 | 211
2016-05-12 16:30 | 217 | 213
2016-05-12 17:00 | 220 | 217
2016-05-12 17:30 | 221 | 218
2016-05-12 18:00 | 213 | 210
2016-05-12 18:30 | 226 | 223
2016-05-12 19:00 | 242 | 239
2016-05-12 19:30 | 250 | 248
2016-05-12 20:00 | 243 | 241
2016-05-12 20:30 | 241 | 238
2016-05-12 21:00 | 233 | 230
2016-05-12 21:30 | 222 | 219
2016-05-12 22:00 | 212 | 208
2016-05-12 22:30 | 197 | 193
2016-05-12 23:00 | 188 | 184
2016-05-12 23:30 | 179 | 175
2016-05-13 | 183 | 179
2016-05-13 00:30 | 179 | 176
2016-05-13 01:00 | 175 | 171
2016-05-13 01:30 | 171 | 167
2016-05-13 02:00 | 168 | 164
2016-05-13 02:30 | 167 | 162
2016-05-13 03:00 | 165 | 161
2016-05-13 03:30 | 165 | 161
2016-05-13 04:00 | 166 | 162
2016-05-13 04:30 | 167 | 163
2016-05-13 05:00 | 169 | 165
2016-05-13 05:30 | 175 | 171
2016-05-13 06:00 | 173 | 169
2016-05-13 06:30 | 182 | 178
2016-05-13 07:00 | 195 | 191
2016-05-13 07:30 | 205 | 202
2016-05-13 08:00 | 209 | 206
2016-05-13 08:30 | 213 | 210
2016-05-13 09:00 | 216 | 213
2016-05-13 09:30 | 213 | 210
2016-05-13 10:00 | 207 | 204
2016-05-13 10:30 | 206 | 203
2016-05-13 11:00 | 203 | 200
2016-05-13 11:30 | 201 | 197
2016-05-13 12:00 | 201 | 197
2016-05-13 12:30 | 195 | 191
2016-05-13 13:00 | 193 | 189
2016-05-13 13:30 | 197 | 193
2016-05-13 14:00 | 198 | 194
2016-05-13 14:30 | 201 | 197
2016-05-13 15:00 | 202 | 198
2016-05-13 15:30 | 202 | 198
2016-05-13 16:00 | 207 | 203
2016-05-13 16:30 | 213 | 209
2016-05-13 17:00 | 215 | 211
2016-05-13 17:30 | 217 | 214
2016-05-13 18:00 | 211 | 207
2016-05-13 18:30 | 220 | 217
2016-05-13 19:00 | 228 | 226
2016-05-13 19:30 | 222 | 219
2016-05-13 20:00 | 226 | 223
2016-05-13 20:30 | 220 | 217
2016-05-13 21:00 | 214 | 211
2016-05-13 21:30 | 207 | 204
2016-05-13 22:00 | 199 | 195
2016-05-13 22:30 | 191 | 187
2016-05-13 23:00 | 201 | 198
2016-05-13 23:30 | 193 | 190
2016-05-14 | 189 | 185
2016-05-14 00:30 | 185 | 181
2016-05-14 01:00 | 177 | 173
2016-05-14 01:30 | 172 | 169
2016-05-14 02:00 | 168 | 165
2016-05-14 02:30 | 168 | 165
2016-05-14 03:00 | 166 | 163
2016-05-14 03:30 | 166 | 163
2016-05-14 04:00 | 165 | 162
2016-05-14 04:30 | 168 | 165
2016-05-14 05:00 | 167 | 164
2016-05-14 05:30 | 170 | 167
2016-05-14 06:00 | 174 | 171
2016-05-14 06:30 | 167 | 164
2016-05-14 07:00 | 171 | 168
2016-05-14 07:30 | 172 | 169
2016-05-14 08:00 | 179 | 175
2016-05-14 08:30 | 185 | 182
2016-05-14 09:00 | 187 | 184
2016-05-14 09:30 | 193 | 190
2016-05-14 10:00 | 190 | 187
2016-05-14 10:30 | 187 | 184
2016-05-14 11:00 | 177 | 173
2016-05-14 11:30 | 173 | 169
2016-05-14 12:00 | 171 | 167
2016-05-14 12:30 | 175 | 171
2016-05-14 13:00 | 173 | 169
2016-05-14 13:30 | 174 | 171
2016-05-14 14:00 | 177 | 173
2016-05-14 14:30 | 177 | 173
2016-05-14 15:00 | 178 | 174
2016-05-14 15:30 | 181 | 178
2016-05-14 16:00 | 185 | 181
2016-05-14 16:30 | 190 | 187
2016-05-14 17:00 | 197 | 194
2016-05-14 17:30 | 202 | 199
2016-05-14 18:00 | 208 | 205
2016-05-14 18:30 | 212 | 210
2016-05-14 19:00 | 220 | 218
2016-05-14 19:30 | 223 | 221
2016-05-14 20:00 | 220 | 217
2016-05-14 20:30 | 214 | 211
2016-05-14 21:00 | 209 | 205
2016-05-14 21:30 | 202 | 198
2016-05-14 22:00 | 198 | 195
2016-05-14 22:30 | 214 | 211
2016-05-14 23:00 | 210 | 207
2016-05-14 23:30 | 203 | 199
2016-05-15 | 198 | 194
2016-05-15 00:30 | 193 | 189
2016-05-15 01:00 | 188 | 184
2016-05-15 01:30 | 184 | 181
2016-05-15 02:00 | 179 | 177
2016-05-15 02:30 | 176 | 174
2016-05-15 03:00 | 175 | 173
2016-05-15 03:30 | 174 | 172
2016-05-15 04:00 | 172 | 170
2016-05-15 04:30 | 171 | 169
2016-05-15 05:00 | 171 | 169
2016-05-15 05:30 | 173 | 171
2016-05-15 06:00 | 174 | 173
2016-05-15 06:30 | 178 | 177
2016-05-15 07:00 | 181 | 179
2016-05-15 07:30 | 166 | 163
2016-05-15 08:00 | 165 | 163
2016-05-15 08:30 | 171 | 169
2016-05-15 09:00 | 175 | 172
2016-05-15 09:30 | 175 | 173
2016-05-15 10:00 | 177 | 175
2016-05-15 10:30 | 174 | 172
2016-05-15 11:00 | 164 | 162
2016-05-15 11:30 | 162 | 159
2016-05-15 12:00 | 157 | 155
2016-05-15 12:30 | 162 | 160
2016-05-15 13:00 | 162 | 159
2016-05-15 13:30 | 160 | 158
2016-05-15 14:00 | 162 | 160
2016-05-15 14:30 | 166 | 164
2016-05-15 15:00 | 171 | 169
2016-05-15 15:30 | 177 | 175
2016-05-15 16:00 | 179 | 178
2016-05-15 16:30 | 185 | 183
2016-05-15 17:00 | 195 | 193
2016-05-15 17:30 | 203 | 202
2016-05-15 18:00 | 196 | 193
2016-05-15 18:30 | 202 | 200
2016-05-15 19:00 | 218 | 216
2016-05-15 19:30 | 231 | 230
2016-05-15 20:00 | 226 | 225
2016-05-15 20:30 | 217 | 215
2016-05-15 21:00 | 210 | 208
2016-05-15 21:30 | 202 | 200
2016-05-15 22:00 | 189 | 186
2016-05-15 22:30 | 196 | 194
2016-05-15 23:00 | 189 | 187
2016-05-15 23:30 | 181 | 179
2016-05-16 | 172 | 170
2016-05-16 00:30 | 170 | 168
2016-05-16 01:00 | 159 | 156
2016-05-16 01:30 | 153 | 150
2016-05-16 02:00 | 151 | 148
2016-05-16 02:30 | 150 | 147
2016-05-16 03:00 | 149 | 146
2016-05-16 03:30 | 149 | 146
2016-05-16 04:00 | 148 | 145
2016-05-16 04:30 | 155 | 153
2016-05-16 05:00 | 168 | 166
2016-05-16 05:30 | 170 | 168
2016-05-16 06:00 | 187 | 186
2016-05-16 06:30 | 203 | 201
2016-05-16 07:00 | 218 | 217
2016-05-16 07:30 | 211 | 210
2016-05-16 08:00 | 212 | 210
2016-05-16 08:30 | 214 | 212
2016-05-16 09:00 | 216 | 214
2016-05-16 09:30 | 217 | 215
2016-05-16 10:00 | 216 | 214
2016-05-16 10:30 | 212 | 210
2016-05-16 11:00 | 208 | 206
2016-05-16 11:30 | 211 | 209
2016-05-16 12:00 | 211 | 209
2016-05-16 12:30 | 215 | 213
2016-05-16 13:00 | 215 | 213
2016-05-16 13:30 | 207 | 205
2016-05-16 14:00 | 213 | 212
2016-05-16 14:30 | 218 | 216
2016-05-16 15:00 | 213 | 211
2016-05-16 15:30 | 215 | 213
2016-05-16 16:00 | 220 | 218
2016-05-16 16:30 | 222 | 220
2016-05-16 17:00 | 226 | 225
2016-05-16 17:30 | 227 | 225
2016-05-16 18:00 | 225 | 223
2016-05-16 18:30 | 239 | 237
2016-05-16 19:00 | 244 | 243
2016-05-16 19:30 | 237 | 235
2016-05-16 20:00 | 226 | 224
2016-05-16 20:30 | 214 | 212
2016-05-16 21:00 | 192 | 189
2016-05-16 21:30 | 171 | 168
2016-05-16 22:00 | 161 | 159
2016-05-16 22:30 | 161 | 158
2016-05-16 23:00 | 162 | 159
2016-05-16 23:30 | 155 | 152
2016-05-17 | 148 | 145
2016-05-17 00:30 | 161 | 158
2016-05-17 01:00 | 155 | 153
2016-05-17 01:30 | 158 | 155
2016-05-17 02:00 | 173 | 171
2016-05-17 02:30 | 175 | 172
2016-05-17 03:00 | 177 | 175
2016-05-17 03:30 | 179 | 178
2016-05-17 04:00 | 179 | 177
2016-05-17 04:30 | 178 | 176
2016-05-17 05:00 | 183 | 181
2016-05-17 05:30 | 191 | 189
2016-05-17 06:00 | 197 | 195
2016-05-17 06:30 | 214 | 212
2016-05-17 07:00 | 225 | 223
2016-05-17 07:30 | 223 | 221
2016-05-17 08:00 | 223 | 221
2016-05-17 08:30 | 224 | 223
2016-05-17 09:00 | 224 | 222
2016-05-17 09:30 | 221 | 220
2016-05-17 10:00 | 216 | 214
2016-05-17 10:30 | 215 | 213
2016-05-17 11:00 | 202 | 200
2016-05-17 11:30 | 198 | 196
2016-05-17 12:00 | 196 | 193
2016-05-17 12:30 | 200 | 198
2016-05-17 13:00 | 201 | 199
2016-05-17 13:30 | 202 | 200
2016-05-17 14:00 | 205 | 203
2016-05-17 14:30 | 208 | 206
2016-05-17 15:00 | 201 | 199
2016-05-17 15:30 | 204 | 202
2016-05-17 16:00 | 208 | 207
2016-05-17 16:30 | 202 | 200
2016-05-17 17:00 | 211 | 209
2016-05-17 17:30 | 210 | 208
2016-05-17 18:00 | 193 | 190
2016-05-17 18:30 | 205 | 203
2016-05-17 19:00 | 220 | 219
2016-05-17 19:30 | 222 | 220
2016-05-17 20:00 | 222 | 221
2016-05-17 20:30 | 209 | 207
2016-05-17 21:00 | 208 | 206
2016-05-17 21:30 | 202 | 199
2016-05-17 22:00 | 191 | 189
2016-05-17 22:30 | 190 | 188
2016-05-17 23:00 | 184 | 182
2016-05-17 23:30 | 172 | 169
2016-05-18 | 158 | 155
2016-05-18 00:30 | 166 | 164
2016-05-18 01:00 | 186 | 184
2016-05-18 01:30 | 182 | 180
2016-05-18 02:00 | 183 | 180
2016-05-18 02:30 | 182 | 180
2016-05-18 03:00 | 181 | 178
2016-05-18 03:30 | 180 | 178
2016-05-18 04:00 | 180 | 178
2016-05-18 04:30 | 180 | 178
2016-05-18 05:00 | 183 | 181
2016-05-18 05:30 | 191 | 189
2016-05-18 06:00 | 199 | 198
2016-05-18 06:30 | 192 | 190
2016-05-18 07:00 | 193 | 191
2016-05-18 07:30 | 207 | 205
2016-05-18 08:00 | 218 | 216
2016-05-18 08:30 | 220 | 219
2016-05-18 09:00 | 222 | 220
2016-05-18 09:30 | 221 | 219
2016-05-18 10:00 | 218 | 217
2016-05-18 10:30 | 218 | 216
2016-05-18 11:00 | 209 | 207
2016-05-18 11:30 | 205 | 203
2016-05-18 12:00 | 206 | 204
2016-05-18 12:30 | 207 | 205
2016-05-18 13:00 | 207 | 205
2016-05-18 13:30 | 206 | 204
2016-05-18 14:00 | 208 | 206
2016-05-18 14:30 | 209 | 207
2016-05-18 15:00 | 211 | 209
2016-05-18 15:30 | 212 | 210
2016-05-18 16:00 | 216 | 214
2016-05-18 16:30 | 219 | 217
2016-05-18 17:00 | 186 | 184
2016-05-18 17:30 | 158 | 155
2016-05-18 18:00 | 145 | 142
2016-05-18 18:30 | 165 | 163
2016-05-18 19:00 | 173 | 172
2016-05-18 19:30 | 177 | 175
2016-05-18 20:00 | 172 | 170
2016-05-18 20:30 | 159 | 157
2016-05-18 21:00 | 158 | 156
2016-05-18 21:30 | 150 | 148
2016-05-18 22:00 | 146 | 143
2016-05-18 22:30 | 133 | 131
2016-05-18 23:00 | 124 | 122
2016-05-18 23:30 | 115 | 113
2016-05-19 | 132 | 130
2016-05-19 00:30 | 178 | 176
2016-05-19 01:00 | 188 | 186
2016-05-19 01:30 | 183 | 181
2016-05-19 02:00 | 180 | 178
2016-05-19 02:30 | 178 | 176
2016-05-19 03:00 | 177 | 175
2016-05-19 03:30 | 176 | 174
2016-05-19 04:00 | 176 | 174
2016-05-19 04:30 | 176 | 174
2016-05-19 05:00 | 178 | 176
2016-05-19 05:30 | 185 | 183
2016-05-19 06:00 | 195 | 193
2016-05-19 06:30 | 211 | 209
2016-05-19 07:00 | 201 | 200
2016-05-19 07:30 | 210 | 209
2016-05-19 08:00 | 214 | 212
2016-05-19 08:30 | 212 | 211
2016-05-19 09:00 | 211 | 210
2016-05-19 09:30 | 214 | 213
2016-05-19 10:00 | 212 | 210
2016-05-19 10:30 | 212 | 210
2016-05-19 11:00 | 203 | 200
2016-05-19 11:30 | 193 | 190
2016-05-19 12:00 | 199 | 196
2016-05-19 12:30 | 207 | 205
2016-05-19 13:00 | 207 | 205
2016-05-19 13:30 | 207 | 205
2016-05-19 14:00 | 209 | 207
2016-05-19 14:30 | 215 | 213
2016-05-19 15:00 | 216 | 214
2016-05-19 15:30 | 216 | 214
2016-05-19 16:00 | 217 | 216
2016-05-19 16:30 | 174 | 171
2016-05-19 17:00 | 151 | 148
2016-05-19 17:30 | 153 | 151
2016-05-19 18:00 | 154 | 151
2016-05-19 18:30 | 173 | 171
2016-05-19 19:00 | 177 | 175
2016-05-19 19:30 | 171 | 169
2016-05-19 20:00 | 164 | 161
2016-05-19 20:30 | 155 | 152
2016-05-19 21:00 | 158 | 155
2016-05-19 21:30 | 199 | 197
2016-05-19 22:00 | 204 | 202
2016-05-19 22:30 | 194 | 192
2016-05-19 23:00 | 187 | 184
2016-05-19 23:30 | 176 | 174
2016-05-20 | 173 | 171
2016-05-20 00:30 | 194 | 192
2016-05-20 01:00 | 188 | 186
2016-05-20 01:30 | 185 | 182
2016-05-20 02:00 | 182 | 180
2016-05-20 02:30 | 179 | 177
2016-05-20 03:00 | 177 | 175
2016-05-20 03:30 | 177 | 174
2016-05-20 04:00 | 176 | 173
2016-05-20 04:30 | 177 | 175
2016-05-20 05:00 | 178 | 176
2016-05-20 05:30 | 186 | 184
2016-05-20 06:00 | 194 | 193
2016-05-20 06:30 | 201 | 200
2016-05-20 07:00 | 191 | 188
2016-05-20 07:30 | 202 | 199
2016-05-20 08:00 | 200 | 197
2016-05-20 08:30 | 216 | 214
2016-05-20 09:00 | 218 | 216
2016-05-20 09:30 | 221 | 220
2016-05-20 10:00 | 215 | 213
2016-05-20 10:30 | 213 | 211
2016-05-20 11:00 | 201 | 199
2016-05-20 11:30 | 199 | 197
2016-05-20 12:00 | 200 | 197
2016-05-20 12:30 | 199 | 197
2016-05-20 13:00 | 200 | 198
2016-05-20 13:30 | 202 | 200
2016-05-20 14:00 | 213 | 211
2016-05-20 14:30 | 216 | 215
2016-05-20 15:00 | 211 | 209
2016-05-20 15:30 | 210 | 208
2016-05-20 16:00 | 209 | 207
2016-05-20 16:30 | 211 | 208
2016-05-20 17:00 | 212 | 210
2016-05-20 17:30 | 211 | 208
2016-05-20 18:00 | 214 | 211
2016-05-20 18:30 | 220 | 218
2016-05-20 19:00 | 227 | 225
2016-05-20 19:30 | 220 | 218
2016-05-20 20:00 | 215 | 213
2016-05-20 20:30 | 198 | 195
2016-05-20 21:00 | 195 | 193
2016-05-20 21:30 | 204 | 202
2016-05-20 22:00 | 205 | 203
2016-05-20 22:30 | 169 | 166
2016-05-20 23:00 | 195 | 193
2016-05-20 23:30 | 188 | 185
2016-05-21 | 182 | 180
2016-05-21 00:30 | 188 | 186
2016-05-21 01:00 | 185 | 183
2016-05-21 01:30 | 187 | 185
2016-05-21 02:00 | 184 | 182
2016-05-21 02:30 | 182 | 179
2016-05-21 03:00 | 180 | 178
2016-05-21 03:30 | 177 | 174
2016-05-21 04:00 | 177 | 174
2016-05-21 04:30 | 177 | 175
2016-05-21 05:00 | 178 | 175
2016-05-21 05:30 | 180 | 178
2016-05-21 06:00 | 184 | 181
2016-05-21 06:30 | 191 | 188
2016-05-21 07:00 | 173 | 171
2016-05-21 07:30 | 175 | 173
2016-05-21 08:00 | 187 | 185
2016-05-21 08:30 | 198 | 195
2016-05-21 09:00 | 204 | 202
2016-05-21 09:30 | 204 | 201
2016-05-21 10:00 | 203 | 201
2016-05-21 10:30 | 201 | 198
2016-05-21 11:00 | 191 | 189
2016-05-21 11:30 | 188 | 185
2016-05-21 12:00 | 187 | 185
2016-05-21 12:30 | 186 | 183
2016-05-21 13:00 | 184 | 181
2016-05-21 13:30 | 180 | 177
2016-05-21 14:00 | 180 | 177
2016-05-21 14:30 | 185 | 182
2016-05-21 15:00 | 183 | 180
2016-05-21 15:30 | 182 | 178
2016-05-21 16:00 | 182 | 179
2016-05-21 16:30 | 183 | 180
2016-05-21 17:00 | 165 | 161
2016-05-21 17:30 | 161 | 158
2016-05-21 18:00 | 160 | 157
2016-05-21 18:30 | 174 | 172
2016-05-21 19:00 | 186 | 183
2016-05-21 19:30 | 185 | 183
2016-05-21 20:00 | 182 | 179
2016-05-21 20:30 | 173 | 171
2016-05-21 21:00 | 169 | 166
2016-05-21 21:30 | 165 | 162
2016-05-21 22:00 | 172 | 169
2016-05-21 22:30 | 167 | 164
2016-05-21 23:00 | 161 | 158
2016-05-21 23:30 | 154 | 151
2016-05-22 | 148 | 145
2016-05-22 00:30 | 145 | 141
2016-05-22 01:00 | 153 | 150
2016-05-22 01:30 | 177 | 174
2016-05-22 02:00 | 175 | 173
2016-05-22 02:30 | 168 | 166
2016-05-22 03:00 | 145 | 142
2016-05-22 03:30 | 140 | 137
2016-05-22 04:00 | 130 | 126
2016-05-22 04:30 | 123 | 120
2016-05-22 05:00 | 115 | 111
2016-05-22 05:30 | 117 | 113
2016-05-22 06:00 | 119 | 115
2016-05-22 06:30 | 124 | 120
2016-05-22 07:00 | 127 | 123
2016-05-22 07:30 | 134 | 130
2016-05-22 08:00 | 142 | 139
2016-05-22 08:30 | 151 | 149
2016-05-22 09:00 | 157 | 154
2016-05-22 09:30 | 162 | 159
2016-05-22 10:00 | 165 | 163
2016-05-22 10:30 | 165 | 162
2016-05-22 11:00 | 163 | 160
2016-05-22 11:30 | 163 | 160
2016-05-22 12:00 | 166 | 163
2016-05-22 12:30 | 169 | 166
2016-05-22 13:00 | 161 | 158
2016-05-22 13:30 | 163 | 160
2016-05-22 14:00 | 160 | 158
2016-05-22 14:30 | 160 | 157
2016-05-22 15:00 | 163 | 160
2016-05-22 15:30 | 163 | 160
2016-05-22 16:00 | 167 | 164
2016-05-22 16:30 | 170 | 167
2016-05-22 17:00 | 165 | 162
2016-05-22 17:30 | 170 | 166
2016-05-22 18:00 | 160 | 157
2016-05-22 18:30 | 168 | 165
2016-05-22 19:00 | 186 | 184
2016-05-22 19:30 | 186 | 184
2016-05-22 20:00 | 179 | 177
2016-05-22 20:30 | 172 | 169
2016-05-22 21:00 | 165 | 162
2016-05-22 21:30 | 160 | 157
2016-05-22 22:00 | 155 | 152
2016-05-22 22:30 | 160 | 157
2016-05-22 23:00 | 145 | 142
2016-05-22 23:30 | 130 | 126
2016-05-23 | 123 | 119
2016-05-23 00:30 | 120 | 116
2016-05-23 01:00 | 114 | 110
2016-05-23 01:30 | 109 | 105
2016-05-23 02:00 | 107 | 104
2016-05-23 02:30 | 106 | 103
2016-05-23 03:00 | 105 | 102
2016-05-23 03:30 | 104 | 100
2016-05-23 04:00 | 104 | 100
2016-05-23 04:30 | 107 | 103
2016-05-23 05:00 | 109 | 106
2016-05-23 05:30 | 116 | 112
2016-05-23 06:00 | 123 | 120
2016-05-23 06:30 | 141 | 138
2016-05-23 07:00 | 125 | 120
2016-05-23 07:30 | 153 | 149
2016-05-23 08:00 | 174 | 172
2016-05-23 08:30 | 183 | 181
2016-05-23 09:00 | 189 | 187
2016-05-23 09:30 | 196 | 194
2016-05-23 10:00 | 192 | 190
2016-05-23 10:30 | 190 | 188
2016-05-23 11:00 | 191 | 189
2016-05-23 11:30 | 190 | 188
2016-05-23 12:00 | 189 | 186
2016-05-23 12:30 | 191 | 189
2016-05-23 13:00 | 185 | 182
2016-05-23 13:30 | 177 | 173
2016-05-23 14:00 | 177 | 174
2016-05-23 14:30 | 179 | 176
2016-05-23 15:00 | 187 | 184
2016-05-23 15:30 | 186 | 183
2016-05-23 16:00 | 181 | 178
2016-05-23 16:30 | 144 | 141
2016-05-23 17:00 | 121 | 117
2016-05-23 17:30 | 117 | 113
2016-05-23 18:00 | 125 | 121
2016-05-23 18:30 | 142 | 139
2016-05-23 19:00 | 146 | 143
2016-05-23 19:30 | 137 | 133
2016-05-23 20:00 | 130 | 126
2016-05-23 20:30 | 121 | 117
2016-05-23 21:00 | 162 | 159
2016-05-23 21:30 | 171 | 168
2016-05-23 22:00 | 163 | 160
2016-05-23 22:30 | 161 | 158
2016-05-23 23:00 | 153 | 150
2016-05-23 23:30 | 146 | 142
2016-05-24 | 141 | 138
2016-05-24 00:30 | 135 | 131
2016-05-24 01:00 | 131 | 127
2016-05-24 01:30 | 125 | 121
2016-05-24 02:00 | 122 | 118
2016-05-24 02:30 | 121 | 117
2016-05-24 03:00 | 119 | 114
2016-05-24 03:30 | 118 | 114
2016-05-24 04:00 | 118 | 113
2016-05-24 04:30 | 118 | 114
2016-05-24 05:00 | 117 | 113
2016-05-24 05:30 | 114 | 110
2016-05-24 06:00 | 105 | 100
2016-05-24 06:30 | 115 | 110
2016-05-24 07:00 | 129 | 125
2016-05-24 07:30 | 146 | 143
2016-05-24 08:00 | 156 | 153
2016-05-24 08:30 | 158 | 156
2016-05-24 09:00 | 159 | 157
2016-05-24 09:30 | 155 | 152
2016-05-24 10:00 | 148 | 145
2016-05-24 10:30 | 148 | 145
2016-05-24 11:00 | 147 | 145
2016-05-24 11:30 | 147 | 144
2016-05-24 12:00 | 147 | 144
2016-05-24 12:30 | 147 | 144
2016-05-24 13:00 | 140 | 138
2016-05-24 13:30 | 138 | 137
2016-05-24 14:00 | 145 | 144
2016-05-24 14:30 | 150 | 148
2016-05-24 15:00 | 151 | 149
2016-05-24 15:30 | 162 | 160
2016-05-24 16:00 | 161 | 160
2016-05-24 16:30 | 148 | 146
2016-05-24 17:00 | 150 | 148
2016-05-24 17:30 | 157 | 155
2016-05-24 18:00 | 164 | 163
2016-05-24 18:30 | 175 | 173
2016-05-24 19:00 | 181 | 179
2016-05-24 19:30 | 182 | 180
2016-05-24 20:00 | 167 | 165
2016-05-24 20:30 | 173 | 171
2016-05-24 21:00 | 171 | 170
2016-05-24 21:30 | 164 | 162
2016-05-24 22:00 | 150 | 148
2016-05-24 22:30 | 148 | 146
2016-05-24 23:00 | 143 | 142
2016-05-24 23:30 | 136 | 134
2016-05-25 | 130 | 128
2016-05-25 00:30 | 125 | 123
2016-05-25 01:00 | 119 | 117
2016-05-25 01:30 | 116 | 114
2016-05-25 02:00 | 114 | 112
2016-05-25 02:30 | 111 | 108
2016-05-25 03:00 | 110 | 108
2016-05-25 03:30 | 111 | 109
2016-05-25 04:00 | 111 | 109
2016-05-25 04:30 | 115 | 113
2016-05-25 05:00 | 119 | 117
2016-05-25 05:30 | 124 | 122
2016-05-25 06:00 | 134 | 132
2016-05-25 06:30 | 154 | 153
2016-05-25 07:00 | 173 | 171
2016-05-25 07:30 | 199 | 198
2016-05-25 08:00 | 217 | 216
2016-05-25 08:30 | 227 | 226
2016-05-25 09:00 | 217 | 216
2016-05-25 09:30 | 209 | 208
2016-05-25 10:00 | 189 | 188
2016-05-25 10:30 | 175 | 173
2016-05-25 11:00 | 172 | 171
2016-05-25 11:30 | 163 | 162
2016-05-25 12:00 | 165 | 164
2016-05-25 12:30 | 168 | 167
2016-05-25 13:00 | 167 | 165
2016-05-25 13:30 | 165 | 163
2016-05-25 14:00 | 147 | 146
2016-05-25 14:30 | 118 | 116
2016-05-25 15:00 | 105 | 102
2016-05-25 15:30 | 106 | 104
2016-05-25 16:00 | 110 | 108
2016-05-25 16:30 | 119 | 117
2016-05-25 17:00 | 109 | 107
2016-05-25 17:30 | 97 | 95
2016-05-25 18:00 | 97 | 95
2016-05-25 18:30 | 115 | 113
2016-05-25 19:00 | 126 | 124
2016-05-25 19:30 | 125 | 123
2016-05-25 20:00 | 120 | 118
2016-05-25 20:30 | 113 | 111
2016-05-25 21:00 | 106 | 104
2016-05-25 21:30 | 124 | 122
2016-05-25 22:00 | 128 | 126
2016-05-25 22:30 | 118 | 116
2016-05-25 23:00 | 110 | 107
2016-05-25 23:30 | 104 | 101
2016-05-26 | 97 | 95
2016-05-26 00:30 | 95 | 92
2016-05-26 01:00 | 85 | 82
2016-05-26 01:30 | 95 | 92
2016-05-26 02:00 | 101 | 99
2016-05-26 02:30 | 115 | 112
2016-05-26 03:00 | 114 | 112
2016-05-26 03:30 | 114 | 112
2016-05-26 04:00 | 114 | 111
2016-05-26 04:30 | 114 | 111
2016-05-26 05:00 | 117 | 115
2016-05-26 05:30 | 123 | 121
2016-05-26 06:00 | 132 | 130
2016-05-26 06:30 | 96 | 94
2016-05-26 07:00 | 86 | 83
2016-05-26 07:30 | 88 | 85
2016-05-26 08:00 | 87 | 84
2016-05-26 08:30 | 83 | 80
2016-05-26 09:00 | 75 | 71
2016-05-26 09:30 | 80 | 77
2016-05-26 10:00 | 91 | 88
2016-05-26 10:30 | 86 | 83
2016-05-26 11:00 | 103 | 100
2016-05-26 11:30 | 114 | 112
2016-05-26 12:00 | 131 | 129
2016-05-26 12:30 | 143 | 141
2016-05-26 13:00 | 150 | 149
2016-05-26 13:30 | 153 | 152
2016-05-26 14:00 | 130 | 128
2016-05-26 14:30 | 118 | 117
2016-05-26 15:00 | 122 | 120
2016-05-26 15:30 | 129 | 127
2016-05-26 16:00 | 128 | 127
2016-05-26 16:30 | 129 | 128
2016-05-26 17:00 | 125 | 123
2016-05-26 17:30 | 122 | 120
2016-05-26 18:00 | 123 | 121
2016-05-26 18:30 | 140 | 138
2016-05-26 19:00 | 152 | 151
2016-05-26 19:30 | 146 | 145
2016-05-26 20:00 | 140 | 138
2016-05-26 20:30 | 132 | 130
2016-05-26 21:00 | 130 | 128
2016-05-26 21:30 | 120 | 118
2016-05-26 22:00 | 111 | 109
2016-05-26 22:30 | 99 | 96
2016-05-26 23:00 | 89 | 86
2016-05-26 23:30 | 79 | 75
2016-05-27 | 75 | 71
2016-05-27 00:30 | 96 | 93
2016-05-27 01:00 | 121 | 119
2016-05-27 01:30 | 153 | 152
2016-05-27 02:00 | 151 | 150
2016-05-27 02:30 | 149 | 148
2016-05-27 03:00 | 147 | 145
2016-05-27 03:30 | 145 | 144
2016-05-27 04:00 | 147 | 146
2016-05-27 04:30 | 147 | 146
2016-05-27 05:00 | 149 | 147
2016-05-27 05:30 | 154 | 152
2016-05-27 06:00 | 161 | 160
2016-05-27 06:30 | 172 | 171
2016-05-27 07:00 | 189 | 187
2016-05-27 07:30 | 208 | 207
2016-05-27 08:00 | 208 | 207
2016-05-27 08:30 | 210 | 209
2016-05-27 09:00 | 214 | 213
2016-05-27 09:30 | 212 | 211
2016-05-27 10:00 | 201 | 200
2016-05-27 10:30 | 201 | 200
2016-05-27 11:00 | 206 | 205
2016-05-27 11:30 | 207 | 205
2016-05-27 12:00 | 209 | 208
2016-05-27 12:30 | 200 | 199
2016-05-27 13:00 | 203 | 201
2016-05-27 13:30 | 203 | 202
2016-05-27 14:00 | 205 | 204
2016-05-27 14:30 | 214 | 213
2016-05-27 15:00 | 215 | 214
2016-05-27 15:30 | 213 | 212
2016-05-27 16:00 | 218 | 217
2016-05-27 16:30 | 226 | 225
2016-05-27 17:00 | 230 | 229
2016-05-27 17:30 | 228 | 227
2016-05-27 18:00 | 220 | 219
2016-05-27 18:30 | 228 | 227
2016-05-27 19:00 | 229 | 228
2016-05-27 19:30 | 223 | 222
2016-05-27 20:00 | 215 | 214
2016-05-27 20:30 | 213 | 211
2016-05-27 21:00 | 210 | 209
2016-05-27 21:30 | 203 | 202
2016-05-27 22:00 | 196 | 195
2016-05-27 22:30 | 191 | 189
2016-05-27 23:00 | 186 | 185
2016-05-27 23:30 | 177 | 175
2016-05-28 | 171 | 169
2016-05-28 00:30 | 171 | 169
2016-05-28 01:00 | 166 | 165
2016-05-28 01:30 | 161 | 160
2016-05-28 02:00 | 157 | 155
2016-05-28 02:30 | 154 | 152
2016-05-28 03:00 | 151 | 149
2016-05-28 03:30 | 149 | 147
2016-05-28 04:00 | 147 | 146
2016-05-28 04:30 | 149 | 147
2016-05-28 05:00 | 148 | 146
2016-05-28 05:30 | 151 | 149
2016-05-28 06:00 | 153 | 152
2016-05-28 06:30 | 159 | 158
2016-05-28 07:00 | 160 | 159
2016-05-28 07:30 | 168 | 167
2016-05-28 08:00 | 174 | 172
2016-05-28 08:30 | 180 | 178
2016-05-28 09:00 | 180 | 178
2016-05-28 09:30 | 161 | 158
2016-05-28 10:00 | 152 | 150
2016-05-28 10:30 | 168 | 166
2016-05-28 11:00 | 166 | 165
2016-05-28 11:30 | 171 | 170
2016-05-28 12:00 | 172 | 170
2016-05-28 12:30 | 172 | 171
2016-05-28 13:00 | 174 | 173
2016-05-28 13:30 | 176 | 175
2016-05-28 14:00 | 181 | 179
2016-05-28 14:30 | 183 | 182
2016-05-28 15:00 | 188 | 187
2016-05-28 15:30 | 193 | 191
2016-05-28 16:00 | 197 | 195
2016-05-28 16:30 | 202 | 201
2016-05-28 17:00 | 155 | 154
2016-05-28 17:30 | 139 | 137
2016-05-28 18:00 | 141 | 139
2016-05-28 18:30 | 149 | 147
2016-05-28 19:00 | 154 | 152
2016-05-28 19:30 | 215 | 214
2016-05-28 20:00 | 229 | 228
2016-05-28 20:30 | 221 | 220
2016-05-28 21:00 | 215 | 214
2016-05-28 21:30 | 208 | 206
2016-05-28 22:00 | 202 | 201
2016-05-28 22:30 | 195 | 194
2016-05-28 23:00 | 188 | 186
2016-05-28 23:30 | 180 | 179
2016-05-29 | 176 | 174
2016-05-29 00:30 | 170 | 168
2016-05-29 01:00 | 163 | 161
2016-05-29 01:30 | 158 | 156
2016-05-29 02:00 | 153 | 151
2016-05-29 02:30 | 151 | 148
2016-05-29 03:00 | 148 | 146
2016-05-29 03:30 | 147 | 145
2016-05-29 04:00 | 146 | 144
2016-05-29 04:30 | 146 | 144
2016-05-29 05:00 | 146 | 144
2016-05-29 05:30 | 148 | 146
2016-05-29 06:00 | 150 | 148
2016-05-29 06:30 | 154 | 152
2016-05-29 07:00 | 156 | 154
2016-05-29 07:30 | 161 | 160
2016-05-29 08:00 | 169 | 167
2016-05-29 08:30 | 175 | 173
2016-05-29 09:00 | 176 | 175
2016-05-29 09:30 | 181 | 179
2016-05-29 10:00 | 181 | 180
2016-05-29 10:30 | 179 | 178
2016-05-29 11:00 | 169 | 167
2016-05-29 11:30 | 164 | 162
2016-05-29 12:00 | 167 | 165
2016-05-29 12:30 | 168 | 166
2016-05-29 13:00 | 170 | 169
2016-05-29 13:30 | 172 | 171
2016-05-29 14:00 | 175 | 174
2016-05-29 14:30 | 179 | 178
2016-05-29 15:00 | 183 | 182
2016-05-29 15:30 | 187 | 186
2016-05-29 16:00 | 190 | 188
2016-05-29 16:30 | 194 | 192
2016-05-29 17:00 | 201 | 200
2016-05-29 17:30 | 200 | 199
2016-05-29 18:00 | 193 | 192
2016-05-29 18:30 | 205 | 204
2016-05-29 19:00 | 219 | 218
2016-05-29 19:30 | 215 | 214
2016-05-29 20:00 | 208 | 207
2016-05-29 20:30 | 200 | 199
2016-05-29 21:00 | 193 | 192
2016-05-29 21:30 | 187 | 186
2016-05-29 22:00 | 180 | 179
2016-05-29 22:30 | 188 | 187
2016-05-29 23:00 | 184 | 183
2016-05-29 23:30 | 177 | 176
2016-05-30 | 172 | 170
2016-05-30 00:30 | 166 | 164
2016-05-30 01:00 | 161 | 159
2016-05-30 01:30 | 156 | 154
2016-05-30 02:00 | 153 | 151
2016-05-30 02:30 | 151 | 149
2016-05-30 03:00 | 150 | 148
2016-05-30 03:30 | 149 | 147
2016-05-30 04:00 | 149 | 147
2016-05-30 04:30 | 147 | 145
2016-05-30 05:00 | 131 | 129
2016-05-30 05:30 | 132 | 130
2016-05-30 06:00 | 140 | 138
2016-05-30 06:30 | 138 | 136
2016-05-30 07:00 | 136 | 133
2016-05-30 07:30 | 150 | 147
2016-05-30 08:00 | 159 | 156
2016-05-30 08:30 | 161 | 158
2016-05-30 09:00 | 153 | 150
2016-05-30 09:30 | 154 | 152
2016-05-30 10:00 | 164 | 161
2016-05-30 10:30 | 166 | 162
2016-05-30 11:00 | 158 | 154
2016-05-30 11:30 | 156 | 153
2016-05-30 12:00 | 158 | 154
2016-05-30 12:30 | 155 | 151
2016-05-30 13:00 | 154 | 150
2016-05-30 13:30 | 154 | 151
2016-05-30 14:00 | 156 | 152
2016-05-30 14:30 | 156 | 152
2016-05-30 15:00 | 151 | 148
2016-05-30 15:30 | 145 | 141
2016-05-30 16:00 | 108 | 103
2016-05-30 16:30 | 139 | 135
2016-05-30 17:00 | 109 | 104
2016-05-30 17:30 | 104 | 100
2016-05-30 18:00 | 100 | 95
2016-05-30 18:30 | 112 | 108
2016-05-30 19:00 | 115 | 110
2016-05-30 19:30 | 134 | 131
2016-05-30 20:00 | 132 | 129
2016-05-30 20:30 | 124 | 121
2016-05-30 21:00 | 144 | 141
2016-05-30 21:30 | 147 | 144
2016-05-30 22:00 | 140 | 137
2016-05-30 22:30 | 126 | 123
2016-05-30 23:00 | 123 | 119
2016-05-30 23:30 | 114 | 110
2016-05-31 | 110 | 106
2016-05-31 00:30 | 103 | 99
2016-05-31 01:00 | 101 | 97
2016-05-31 01:30 | 96 | 92
2016-05-31 02:00 | 93 | 89
2016-05-31 02:30 | 91 | 87
2016-05-31 03:00 | 90 | 86
2016-05-31 03:30 | 89 | 85
2016-05-31 04:00 | 90 | 86
2016-05-31 04:30 | 91 | 87
2016-05-31 05:00 | 94 | 90
2016-05-31 05:30 | 100 | 96
2016-05-31 06:00 | 107 | 103
2016-05-31 06:30 | 78 | 73
2016-05-31 07:00 | 76 | 70
2016-05-31 07:30 | 119 | 116
2016-05-31 08:00 | 141 | 138
2016-05-31 08:30 | 150 | 147
2016-05-31 09:00 | 159 | 156
2016-05-31 09:30 | 160 | 156
2016-05-31 10:00 | 157 | 153
2016-05-31 10:30 | 160 | 157
2016-05-31 11:00 | 155 | 151
2016-05-31 11:30 | 143 | 139
2016-05-31 12:00 | 116 | 111
2016-05-31 12:30 | 90 | 85
2016-05-31 13:00 | 95 | 90
2016-05-31 13:30 | 110 | 104
2016-05-31 14:00 | 109 | 103
2016-05-31 14:30 | 114 | 109
2016-05-31 15:00 | 134 | 130
2016-05-31 15:30 | 141 | 138
2016-05-31 16:00 | 144 | 140
2016-05-31 16:30 | 150 | 147
2016-05-31 17:00 | 144 | 141
2016-05-31 17:30 | 115 | 110
2016-05-31 18:00 | 85 | 79
2016-05-31 18:30 | 98 | 93
2016-05-31 19:00 | 99 | 94
2016-05-31 19:30 | 101 | 96
2016-05-31 20:00 | 104 | 99
2016-05-31 20:30 | 117 | 113
2016-05-31 21:00 | 153 | 150
2016-05-31 21:30 | 148 | 145
2016-05-31 22:00 | 140 | 137
2016-05-31 22:30 | 130 | 126
2016-05-31 23:00 | 122 | 118
2016-05-31 23:30 | 116 | 111
2016-06-01 | 109 | 105
2016-06-01 00:30 | 102 | 97
2016-06-01 01:00 | 90 | 84
2016-06-01 01:30 | 87 | 82
2016-06-01 02:00 | 89 | 83
2016-06-01 02:30 | 88 | 82
2016-06-01 03:00 | 86 | 80
2016-06-01 03:30 | 85 | 79
2016-06-01 04:00 | 85 | 79
2016-06-01 04:30 | 87 | 81
2016-06-01 05:00 | 89 | 84
2016-06-01 05:30 | 95 | 89
2016-06-01 06:00 | 104 | 99
2016-06-01 06:30 | 89 | 83
2016-06-01 07:00 | 70 | 63
2016-06-01 07:30 | 107 | 103
2016-06-01 08:00 | 123 | 118
2016-06-01 08:30 | 134 | 130
2016-06-01 09:00 | 144 | 140
2016-06-01 09:30 | 146 | 142
2016-06-01 10:00 | 150 | 147
2016-06-01 10:30 | 148 | 144
2016-06-01 11:00 | 119 | 114
2016-06-01 11:30 | 107 | 103
2016-06-01 12:00 | 126 | 122
2016-06-01 12:30 | 114 | 109
2016-06-01 13:00 | 131 | 127
2016-06-01 13:30 | 133 | 129
2016-06-01 14:00 | 136 | 132
2016-06-01 14:30 | 139 | 135
2016-06-01 15:00 | 144 | 140
2016-06-01 15:30 | 143 | 139
2016-06-01 16:00 | 124 | 120
2016-06-01 16:30 | 134 | 130
2016-06-01 17:00 | 120 | 116
2016-06-01 17:30 | 91 | 86
2016-06-01 18:00 | 67 | 59
2016-06-01 18:30 | 25 | 5
2016-06-01 19:00 | 51 | 43
2016-06-01 19:30 | 54 | 46
2016-06-01 20:00 | 25 | 11
2016-06-01 20:30 | 42 | 34
2016-06-01 21:00 | 61 | 55
2016-06-01 21:30 | 82 | 78
2016-06-01 22:00 | 96 | 92
2016-06-01 22:30 | 25 | 11
2016-06-01 23:00 | 29 | 19
2016-06-01 23:30 | 67 | 61
2016-06-02 | 88 | 83
2016-06-02 00:30 | 151 | 148
2016-06-02 01:00 | 156 | 154
2016-06-02 01:30 | 151 | 148
2016-06-02 02:00 | 147 | 144
2016-06-02 02:30 | 145 | 142
2016-06-02 03:00 | 145 | 142
2016-06-02 03:30 | 144 | 141
2016-06-02 04:00 | 144 | 141
2016-06-02 04:30 | 145 | 142
2016-06-02 05:00 | 146 | 143
2016-06-02 05:30 | 152 | 149
2016-06-02 06:00 | 152 | 149
2016-06-02 06:30 | 161 | 158
2016-06-02 07:00 | 154 | 151
2016-06-02 07:30 | 168 | 165
2016-06-02 08:00 | 175 | 172
2016-06-02 08:30 | 176 | 173
2016-06-02 09:00 | 183 | 180
2016-06-02 09:30 | 183 | 181
2016-06-02 10:00 | 181 | 179
2016-06-02 10:30 | 178 | 176
2016-06-02 11:00 | 174 | 172
2016-06-02 11:30 | 172 | 170
2016-06-02 12:00 | 135 | 132
2016-06-02 12:30 | 134 | 130
2016-06-02 13:00 | 135 | 132
2016-06-02 13:30 | 137 | 134
2016-06-02 14:00 | 133 | 130
2016-06-02 14:30 | 137 | 134
2016-06-02 15:00 | 155 | 152
2016-06-02 15:30 | 139 | 135
2016-06-02 16:00 | 159 | 155
2016-06-02 16:30 | 180 | 177
2016-06-02 17:00 | 188 | 185
2016-06-02 17:30 | 190 | 187
2016-06-02 18:00 | 187 | 183
2016-06-02 18:30 | 196 | 193
2016-06-02 19:00 | 205 | 203
2016-06-02 19:30 | 213 | 210
2016-06-02 20:00 | 209 | 207
2016-06-02 20:30 | 195 | 192
2016-06-02 21:00 | 187 | 184
2016-06-02 21:30 | 188 | 185
2016-06-02 22:00 | 180 | 177
2016-06-02 22:30 | 179 | 176
2016-06-02 23:00 | 170 | 168
2016-06-02 23:30 | 168 | 165
2016-06-03 | 156 | 153
2016-06-03 00:30 | 155 | 152
2016-06-03 01:00 | 152 | 149
2016-06-03 01:30 | 149 | 146
2016-06-03 02:00 | 146 | 143
2016-06-03 02:30 | 143 | 140
2016-06-03 03:00 | 141 | 137
2016-06-03 03:30 | 141 | 137
2016-06-03 04:00 | 140 | 137
2016-06-03 04:30 | 141 | 137
2016-06-03 05:00 | 144 | 141
2016-06-03 05:30 | 149 | 146
2016-06-03 06:00 | 137 | 133
2016-06-03 06:30 | 141 | 137
2016-06-03 07:00 | 152 | 148
2016-06-03 07:30 | 168 | 165
2016-06-03 08:00 | 176 | 173
2016-06-03 08:30 | 178 | 175
2016-06-03 09:00 | 177 | 174
2016-06-03 09:30 | 176 | 173
2016-06-03 10:00 | 185 | 182
2016-06-03 10:30 | 185 | 182
2016-06-03 11:00 | 178 | 175
2016-06-03 11:30 | 174 | 172
2016-06-03 12:00 | 178 | 176
2016-06-03 12:30 | 184 | 182
2016-06-03 13:00 | 157 | 153
2016-06-03 13:30 | 158 | 155
2016-06-03 14:00 | 163 | 160
2016-06-03 14:30 | 175 | 171
2016-06-03 15:00 | 179 | 176
2016-06-03 15:30 | 179 | 176
2016-06-03 16:00 | 167 | 163
2016-06-03 16:30 | 132 | 127
2016-06-03 17:00 | 103 | 97
2016-06-03 17:30 | 101 | 96
2016-06-03 18:00 | 89 | 84
2016-06-03 18:30 | 109 | 105
2016-06-03 19:00 | 121 | 118
2016-06-03 19:30 | 115 | 111
2016-06-03 20:00 | 125 | 122
2016-06-03 20:30 | 133 | 129
2016-06-03 21:00 | 135 | 132
2016-06-03 21:30 | 127 | 125
2016-06-03 22:00 | 132 | 130
2016-06-03 22:30 | 128 | 125
2016-06-03 23:00 | 163 | 162
2016-06-03 23:30 | 181 | 180
2016-06-04 | 175 | 174
2016-06-04 00:30 | 167 | 166
2016-06-04 01:00 | 158 | 157
2016-06-04 01:30 | 152 | 150
2016-06-04 02:00 | 146 | 145
2016-06-04 02:30 | 143 | 142
2016-06-04 03:00 | 139 | 138
2016-06-04 03:30 | 138 | 136
2016-06-04 04:00 | 138 | 137
2016-06-04 04:30 | 138 | 137
2016-06-04 05:00 | 139 | 137
2016-06-04 05:30 | 143 | 141
2016-06-04 06:00 | 146 | 144
2016-06-04 06:30 | 153 | 151
2016-06-04 07:00 | 156 | 155
2016-06-04 07:30 | 165 | 163
2016-06-04 08:00 | 171 | 169
2016-06-04 08:30 | 170 | 168
2016-06-04 09:00 | 171 | 169
2016-06-04 09:30 | 143 | 141
2016-06-04 10:00 | 139 | 136
2016-06-04 10:30 | 137 | 135
2016-06-04 11:00 | 136 | 134
2016-06-04 11:30 | 133 | 131
2016-06-04 12:00 | 130 | 128
2016-06-04 12:30 | 136 | 134
2016-06-04 13:00 | 137 | 134
2016-06-04 13:30 | 137 | 135
2016-06-04 14:00 | 140 | 138
2016-06-04 14:30 | 145 | 144
2016-06-04 15:00 | 146 | 144
2016-06-04 15:30 | 148 | 146
2016-06-04 16:00 | 145 | 143
2016-06-04 16:30 | 150 | 148
2016-06-04 17:00 | 162 | 160
2016-06-04 17:30 | 167 | 166
2016-06-04 18:00 | 174 | 172
2016-06-04 18:30 | 187 | 185
2016-06-04 19:00 | 193 | 191
2016-06-04 19:30 | 185 | 184
2016-06-04 20:00 | 194 | 193
2016-06-04 20:30 | 193 | 191
2016-06-04 21:00 | 189 | 188
2016-06-04 21:30 | 183 | 181
2016-06-04 22:00 | 183 | 182
2016-06-04 22:30 | 175 | 173
2016-06-04 23:00 | 170 | 168
2016-06-04 23:30 | 165 | 163
2016-06-05 | 162 | 160
2016-06-05 00:30 | 157 | 155
2016-06-05 01:00 | 149 | 147
2016-06-05 01:30 | 142 | 139
2016-06-05 02:00 | 133 | 131
2016-06-05 02:30 | 133 | 130
2016-06-05 03:00 | 131 | 129
2016-06-05 03:30 | 130 | 128
2016-06-05 04:00 | 128 | 126
2016-06-05 04:30 | 129 | 127
2016-06-05 05:00 | 130 | 128
2016-06-05 05:30 | 130 | 128
2016-06-05 06:00 | 132 | 130
2016-06-05 06:30 | 137 | 135
2016-06-05 07:00 | 139 | 137
2016-06-05 07:30 | 143 | 141
2016-06-05 08:00 | 149 | 147
2016-06-05 08:30 | 153 | 151
2016-06-05 09:00 | 146 | 144
2016-06-05 09:30 | 141 | 139
2016-06-05 10:00 | 139 | 136
2016-06-05 10:30 | 141 | 139
2016-06-05 11:00 | 133 | 131
2016-06-05 11:30 | 128 | 125
2016-06-05 12:00 | 125 | 122
2016-06-05 12:30 | 118 | 116
2016-06-05 13:00 | 117 | 115
2016-06-05 13:30 | 123 | 120
2016-06-05 14:00 | 124 | 121
2016-06-05 14:30 | 125 | 122
2016-06-05 15:00 | 116 | 113
2016-06-05 15:30 | 120 | 117
2016-06-05 16:00 | 127 | 124
2016-06-05 16:30 | 121 | 119
2016-06-05 17:00 | 140 | 138
2016-06-05 17:30 | 140 | 138
2016-06-05 18:00 | 147 | 145
2016-06-05 18:30 | 158 | 157
2016-06-05 19:00 | 159 | 157
2016-06-05 19:30 | 170 | 168
2016-06-05 20:00 | 173 | 172
2016-06-05 20:30 | 167 | 166
2016-06-05 21:00 | 169 | 168
2016-06-05 21:30 | 174 | 173
2016-06-05 22:00 | 177 | 175
2016-06-05 22:30 | 168 | 166
2016-06-05 23:00 | 161 | 160
2016-06-05 23:30 | 158 | 156
2016-06-06 | 156 | 154
2016-06-06 00:30 | 152 | 149
2016-06-06 01:00 | 146 | 143
2016-06-06 01:30 | 136 | 134
2016-06-06 02:00 | 131 | 129
2016-06-06 02:30 | 129 | 126
2016-06-06 03:00 | 126 | 124
2016-06-06 03:30 | 125 | 122
2016-06-06 04:00 | 125 | 123
2016-06-06 04:30 | 126 | 123
2016-06-06 05:00 | 131 | 129
2016-06-06 05:30 | 136 | 134
2016-06-06 06:00 | 144 | 143
2016-06-06 06:30 | 155 | 154
2016-06-06 07:00 | 164 | 163
2016-06-06 07:30 | 171 | 170
2016-06-06 08:00 | 180 | 179
2016-06-06 08:30 | 182 | 181
2016-06-06 09:00 | 175 | 174
2016-06-06 09:30 | 171 | 169
2016-06-06 10:00 | 167 | 165
2016-06-06 10:30 | 169 | 167
2016-06-06 11:00 | 162 | 161
2016-06-06 11:30 | 157 | 155
2016-06-06 12:00 | 157 | 155
2016-06-06 12:30 | 159 | 157
2016-06-06 13:00 | 160 | 158
2016-06-06 13:30 | 161 | 160
2016-06-06 14:00 | 164 | 162
2016-06-06 14:30 | 167 | 165
2016-06-06 15:00 | 171 | 169
2016-06-06 15:30 | 174 | 172
2016-06-06 16:00 | 182 | 180
2016-06-06 16:30 | 188 | 187
2016-06-06 17:00 | 180 | 178
2016-06-06 17:30 | 174 | 172
2016-06-06 18:00 | 159 | 156
2016-06-06 18:30 | 164 | 161
2016-06-06 19:00 | 169 | 167
2016-06-06 19:30 | 174 | 172
2016-06-06 20:00 | 171 | 169
2016-06-06 20:30 | 168 | 166
2016-06-06 21:00 | 173 | 171
2016-06-06 21:30 | 170 | 168
2016-06-06 22:00 | 174 | 172
2016-06-06 22:30 | 161 | 159
2016-06-06 23:00 | 164 | 162
2016-06-06 23:30 | 173 | 172
2016-06-07 | 171 | 169
2016-06-07 00:30 | 159 | 157
2016-06-07 01:00 | 149 | 148
2016-06-07 01:30 | 146 | 144
2016-06-07 02:00 | 140 | 138
2016-06-07 02:30 | 137 | 135
2016-06-07 03:00 | 134 | 132
2016-06-07 03:30 | 136 | 133
2016-06-07 04:00 | 135 | 133
2016-06-07 04:30 | 134 | 132
2016-06-07 05:00 | 137 | 135
2016-06-07 05:30 | 143 | 141
2016-06-07 06:00 | 150 | 148
2016-06-07 06:30 | 149 | 147
2016-06-07 07:00 | 166 | 164
2016-06-07 07:30 | 180 | 177
2016-06-07 08:00 | 191 | 187
2016-06-07 08:30 | 200 | 197
2016-06-07 09:00 | 203 | 201
2016-06-07 09:30 | 188 | 185
2016-06-07 10:00 | 165 | 162
2016-06-07 10:30 | 163 | 160
2016-06-07 11:00 | 166 | 163
2016-06-07 11:30 | 163 | 160
2016-06-07 12:00 | 165 | 162
2016-06-07 12:30 | 167 | 164
2016-06-07 13:00 | 159 | 156
2016-06-07 13:30 | 155 | 152
2016-06-07 14:00 | 129 | 126
2016-06-07 14:30 | 130 | 127
2016-06-07 15:00 | 123 | 120
2016-06-07 15:30 | 89 | 84
2016-06-07 16:00 | 78 | 73
2016-06-07 16:30 | 84 | 80
2016-06-07 17:00 | 98 | 95
2016-06-07 17:30 | 96 | 92
2016-06-07 18:00 | 80 | 75
2016-06-07 18:30 | 88 | 83
2016-06-07 19:00 | 93 | 89
2016-06-07 19:30 | 92 | 87
2016-06-07 20:00 | 88 | 84
2016-06-07 20:30 | 90 | 86
2016-06-07 21:00 | 94 | 91
2016-06-07 21:30 | 123 | 121
2016-06-07 22:00 | 134 | 132
2016-06-07 22:30 | 114 | 111
2016-06-07 23:00 | 86 | 83
2016-06-07 23:30 | 80 | 76
2016-06-08 | 85 | 82
2016-06-08 00:30 | 97 | 94
2016-06-08 01:00 | 99 | 96
2016-06-08 01:30 | 91 | 87
2016-06-08 02:00 | 62 | 57
2016-06-08 02:30 | 79 | 75
2016-06-08 03:00 | 79 | 75
2016-06-08 03:30 | 79 | 74
2016-06-08 04:00 | 76 | 71
2016-06-08 04:30 | 77 | 73
2016-06-08 05:00 | 80 | 76
2016-06-08 05:30 | 87 | 83
2016-06-08 06:00 | 95 | 91
2016-06-08 06:30 | 75 | 71
2016-06-08 07:00 | 80 | 77
2016-06-08 07:30 | 86 | 82
2016-06-08 08:00 | 104 | 101
2016-06-08 08:30 | 119 | 117
2016-06-08 09:00 | 135 | 133
2016-06-08 09:30 | 132 | 129
2016-06-08 10:00 | 131 | 128
2016-06-08 10:30 | 131 | 129
2016-06-08 11:00 | 122 | 119
2016-06-08 11:30 | 120 | 117
2016-06-08 12:00 | 122 | 119
2016-06-08 12:30 | 123 | 120
2016-06-08 13:00 | 125 | 123
2016-06-08 13:30 | 126 | 124
2016-06-08 14:00 | 130 | 127
2016-06-08 14:30 | 136 | 133
2016-06-08 15:00 | 137 | 135
2016-06-08 15:30 | 134 | 131
2016-06-08 16:00 | 129 | 126
2016-06-08 16:30 | 133 | 130
2016-06-08 17:00 | 100 | 97
2016-06-08 17:30 | 100 | 97
2016-06-08 18:00 | 94 | 91
2016-06-08 18:30 | 99 | 96
2016-06-08 19:00 | 105 | 101
2016-06-08 19:30 | 99 | 96
2016-06-08 20:00 | 95 | 92
2016-06-08 20:30 | 102 | 100
2016-06-08 21:00 | 100 | 97
2016-06-08 21:30 | 118 | 116
2016-06-08 22:00 | 128 | 125
2016-06-08 22:30 | 123 | 121
2016-06-08 23:00 | 143 | 141
2016-06-08 23:30 | 173 | 171
2016-06-09 | 171 | 169
2016-06-09 00:30 | 159 | 156
2016-06-09 01:00 | 150 | 147
2016-06-09 01:30 | 142 | 139
2016-06-09 02:00 | 135 | 131
2016-06-09 02:30 | 133 | 129
2016-06-09 03:00 | 136 | 132
2016-06-09 03:30 | 133 | 130
2016-06-09 04:00 | 132 | 129
2016-06-09 04:30 | 133 | 130
2016-06-09 05:00 | 137 | 134
2016-06-09 05:30 | 142 | 139
2016-06-09 06:00 | 149 | 147
2016-06-09 06:30 | 167 | 165
2016-06-09 07:00 | 169 | 166
2016-06-09 07:30 | 183 | 181
2016-06-09 08:00 | 189 | 187
2016-06-09 08:30 | 197 | 195
2016-06-09 09:00 | 203 | 201
2016-06-09 09:30 | 200 | 199
2016-06-09 10:00 | 200 | 198
2016-06-09 10:30 | 201 | 199
2016-06-09 11:00 | 192 | 190
2016-06-09 11:30 | 187 | 185
2016-06-09 12:00 | 186 | 184
2016-06-09 12:30 | 186 | 184
2016-06-09 13:00 | 187 | 185
2016-06-09 13:30 | 189 | 187
2016-06-09 14:00 | 190 | 188
2016-06-09 14:30 | 193 | 191
2016-06-09 15:00 | 196 | 194
2016-06-09 15:30 | 196 | 194
2016-06-09 16:00 | 200 | 196
2016-06-09 16:30 | 202 | 195
2016-06-09 17:00 | 198 | 190
2016-06-09 17:30 | 235 | 229
2016-06-09 18:00 | 247 | 240
2016-06-09 18:30 | 257 | 250
2016-06-09 19:00 | 265 | 259
2016-06-09 19:30 | 253 | 247
2016-06-09 20:00 | 246 | 241
2016-06-09 20:30 | 253 | 250
2016-06-09 21:00 | 254 | 250
2016-06-09 21:30 | 238 | 234
2016-06-09 22:00 | 232 | 227
2016-06-09 22:30 | 225 | 221
2016-06-09 23:00 | 218 | 214
2016-06-09 23:30 | 212 | 208
2016-06-10 | 207 | 204
2016-06-10 00:30 | 197 | 194
2016-06-10 01:00 | 182 | 178
2016-06-10 01:30 | 176 | 171
2016-06-10 02:00 | 166 | 162
2016-06-10 02:30 | 161 | 156
2016-06-10 03:00 | 160 | 155
2016-06-10 03:30 | 160 | 155
2016-06-10 04:00 | 160 | 155
2016-06-10 04:30 | 160 | 155
2016-06-10 05:00 | 160 | 156
2016-06-10 05:30 | 166 | 162
2016-06-10 06:00 | 175 | 171
2016-06-10 06:30 | 190 | 186
2016-06-10 07:00 | 198 | 196
2016-06-10 07:30 | 208 | 205
2016-06-10 08:00 | 230 | 226
2016-06-10 08:30 | 240 | 236
2016-06-10 09:00 | 244 | 241
2016-06-10 09:30 | 240 | 237
2016-06-10 10:00 | 235 | 232
2016-06-10 10:30 | 232 | 229
2016-06-10 11:00 | 219 | 216
2016-06-10 11:30 | 213 | 210
2016-06-10 12:00 | 215 | 212
2016-06-10 12:30 | 219 | 216
2016-06-10 13:00 | 216 | 214
2016-06-10 13:30 | 225 | 223
2016-06-10 14:00 | 229 | 228
2016-06-10 14:30 | 235 | 234
2016-06-10 15:00 | 237 | 235
2016-06-10 15:30 | 235 | 233
2016-06-10 16:00 | 243 | 241
2016-06-10 16:30 | 244 | 242
2016-06-10 17:00 | 242 | 240
2016-06-10 17:30 | 228 | 225
2016-06-10 18:00 | 220 | 217
2016-06-10 18:30 | 230 | 228
2016-06-10 19:00 | 228 | 226
2016-06-10 19:30 | 222 | 220
2016-06-10 20:00 | 219 | 217
2016-06-10 20:30 | 230 | 229
2016-06-10 21:00 | 229 | 227
2016-06-10 21:30 | 220 | 218
2016-06-10 22:00 | 216 | 214
2016-06-10 22:30 | 213 | 211
2016-06-10 23:00 | 210 | 208
2016-06-10 23:30 | 200 | 198
2016-06-11 | 196 | 194
2016-06-11 00:30 | 183 | 181
2016-06-11 01:00 | 173 | 171
2016-06-11 01:30 | 164 | 161
2016-06-11 02:00 | 154 | 151
2016-06-11 02:30 | 148 | 145
2016-06-11 03:00 | 147 | 143
2016-06-11 03:30 | 147 | 144
2016-06-11 04:00 | 147 | 144
2016-06-11 04:30 | 148 | 145
2016-06-11 05:00 | 149 | 146
2016-06-11 05:30 | 151 | 148
2016-06-11 06:00 | 153 | 150
2016-06-11 06:30 | 164 | 161
2016-06-11 07:00 | 170 | 167
2016-06-11 07:30 | 183 | 181
2016-06-11 08:00 | 191 | 189
2016-06-11 08:30 | 192 | 189
2016-06-11 09:00 | 196 | 194
2016-06-11 09:30 | 201 | 199
2016-06-11 10:00 | 200 | 198
2016-06-11 10:30 | 197 | 195
2016-06-11 11:00 | 185 | 182
2016-06-11 11:30 | 181 | 178
2016-06-11 12:00 | 178 | 176
2016-06-11 12:30 | 179 | 176
2016-06-11 13:00 | 178 | 175
2016-06-11 13:30 | 182 | 179
2016-06-11 14:00 | 184 | 181
2016-06-11 14:30 | 183 | 180
2016-06-11 15:00 | 187 | 184
2016-06-11 15:30 | 193 | 191
2016-06-11 16:00 | 199 | 196
2016-06-11 16:30 | 204 | 201
2016-06-11 17:00 | 193 | 190
2016-06-11 17:30 | 190 | 186
2016-06-11 18:00 | 193 | 191
2016-06-11 18:30 | 215 | 213
2016-06-11 19:00 | 226 | 224
2016-06-11 19:30 | 217 | 215
2016-06-11 20:00 | 212 | 210
2016-06-11 20:30 | 208 | 206
2016-06-11 21:00 | 217 | 215
2016-06-11 21:30 | 213 | 211
2016-06-11 22:00 | 209 | 207
2016-06-11 22:30 | 180 | 177
2016-06-11 23:00 | 192 | 190
2016-06-11 23:30 | 185 | 183
2016-06-12 | 182 | 180
2016-06-12 00:30 | 178 | 175
2016-06-12 01:00 | 171 | 168
2016-06-12 01:30 | 163 | 160
2016-06-12 02:00 | 157 | 154
2016-06-12 02:30 | 153 | 150
2016-06-12 03:00 | 151 | 148
2016-06-12 03:30 | 148 | 145
2016-06-12 04:00 | 147 | 144
2016-06-12 04:30 | 147 | 144
2016-06-12 05:00 | 147 | 144
2016-06-12 05:30 | 151 | 148
2016-06-12 06:00 | 152 | 149
2016-06-12 06:30 | 160 | 157
2016-06-12 07:00 | 162 | 159
2016-06-12 07:30 | 169 | 166
2016-06-12 08:00 | 179 | 177
2016-06-12 08:30 | 178 | 175
2016-06-12 09:00 | 180 | 178
2016-06-12 09:30 | 176 | 173
2016-06-12 10:00 | 190 | 187
2016-06-12 10:30 | 203 | 201
2016-06-12 11:00 | 204 | 202
2016-06-12 11:30 | 205 | 203
2016-06-12 12:00 | 204 | 201
2016-06-12 12:30 | 202 | 199
2016-06-12 13:00 | 205 | 203
2016-06-12 13:30 | 204 | 201
2016-06-12 14:00 | 184 | 182
2016-06-12 14:30 | 185 | 182
2016-06-12 15:00 | 189 | 187
2016-06-12 15:30 | 186 | 184
2016-06-12 16:00 | 192 | 190
2016-06-12 16:30 | 182 | 179
2016-06-12 17:00 | 193 | 190
2016-06-12 17:30 | 196 | 194
2016-06-12 18:00 | 181 | 178
2016-06-12 18:30 | 196 | 194
2016-06-12 19:00 | 206 | 204
2016-06-12 19:30 | 210 | 208
2016-06-12 20:00 | 207 | 205
2016-06-12 20:30 | 191 | 189
2016-06-12 21:00 | 164 | 161
2016-06-12 21:30 | 133 | 126
2016-06-12 22:00 | 118 | 112
2016-06-12 22:30 | 115 | 108
2016-06-12 23:00 | 105 | 98
2016-06-12 23:30 | 117 | 110
2016-06-13 | 174 | 169
2016-06-13 00:30 | 178 | 174
2016-06-13 01:00 | 174 | 169
2016-06-13 01:30 | 163 | 158
2016-06-13 02:00 | 159 | 153
2016-06-13 02:30 | 155 | 150
2016-06-13 03:00 | 152 | 146
2016-06-13 03:30 | 151 | 146
2016-06-13 04:00 | 151 | 146
2016-06-13 04:30 | 149 | 144
2016-06-13 05:00 | 156 | 151
2016-06-13 05:30 | 165 | 160
2016-06-13 06:00 | 174 | 170
2016-06-13 06:30 | 194 | 190
2016-06-13 07:00 | 207 | 204
2016-06-13 07:30 | 218 | 215
2016-06-13 08:00 | 229 | 226
2016-06-13 08:30 | 238 | 234
2016-06-13 09:00 | 239 | 235
2016-06-13 09:30 | 204 | 198
2016-06-13 10:00 | 205 | 200
2016-06-13 10:30 | 196 | 191
2016-06-13 11:00 | 198 | 194
2016-06-13 11:30 | 210 | 207
2016-06-13 12:00 | 214 | 211
2016-06-13 12:30 | 211 | 207
2016-06-13 13:00 | 203 | 199
2016-06-13 13:30 | 202 | 198
2016-06-13 14:00 | 204 | 201
2016-06-13 14:30 | 203 | 199
2016-06-13 15:00 | 214 | 210
2016-06-13 15:30 | 223 | 220
2016-06-13 16:00 | 196 | 191
2016-06-13 16:30 | 177 | 172
2016-06-13 17:00 | 176 | 171
2016-06-13 17:30 | 143 | 137
2016-06-13 18:00 | 46 | 38
2016-06-13 18:30 | 47 | 40
2016-06-13 19:00 | 104 | 99
2016-06-13 19:30 | 131 | 128
2016-06-13 20:00 | 146 | 143
2016-06-13 20:30 | 146 | 144
2016-06-13 21:00 | 143 | 140
2016-06-13 21:30 | 137 | 134
2016-06-13 22:00 | 146 | 144
2016-06-13 22:30 | 137 | 134
2016-06-13 23:00 | 197 | 195
2016-06-13 23:30 | 212 | 210
2016-06-14 | 206 | 203
2016-06-14 00:30 | 193 | 191
2016-06-14 01:00 | 183 | 180
2016-06-14 01:30 | 173 | 170
2016-06-14 02:00 | 167 | 163
2016-06-14 02:30 | 169 | 165
2016-06-14 03:00 | 168 | 164
2016-06-14 03:30 | 166 | 163
2016-06-14 04:00 | 172 | 168
2016-06-14 04:30 | 171 | 167
2016-06-14 05:00 | 175 | 171
2016-06-14 05:30 | 179 | 176
2016-06-14 06:00 | 186 | 183
2016-06-14 06:30 | 189 | 186
2016-06-14 07:00 | 197 | 194
2016-06-14 07:30 | 222 | 220
2016-06-14 08:00 | 251 | 249
2016-06-14 08:30 | 258 | 256
2016-06-14 09:00 | 253 | 251
2016-06-14 09:30 | 251 | 249
2016-06-14 10:00 | 242 | 240
2016-06-14 10:30 | 241 | 239
2016-06-14 11:00 | 229 | 227
2016-06-14 11:30 | 186 | 183
2016-06-14 12:00 | 179 | 176
2016-06-14 12:30 | 176 | 173
2016-06-14 13:00 | 176 | 173
2016-06-14 13:30 | 176 | 173
2016-06-14 14:00 | 181 | 178
2016-06-14 14:30 | 190 | 188
2016-06-14 15:00 | 191 | 188
2016-06-14 15:30 | 147 | 144
2016-06-14 16:00 | 124 | 121
2016-06-14 16:30 | 118 | 115
2016-06-14 17:00 | 109 | 105
2016-06-14 17:30 | 74 | 70
2016-06-14 18:00 | 48 | 39
2016-06-14 18:30 | 37 | 30
2016-06-14 19:00 | 34 | 30
2016-06-14 19:30 | 76 | 74
2016-06-14 20:00 | 93 | 91
2016-06-14 20:30 | 100 | 98
2016-06-14 21:00 | 152 | 151
2016-06-14 21:30 | 145 | 143
2016-06-14 22:00 | 142 | 140
2016-06-14 22:30 | 103 | 100
2016-06-14 23:00 | 105 | 102
2016-06-14 23:30 | 98 | 96
2016-06-15 | 95 | 93
2016-06-15 00:30 | 113 | 111
2016-06-15 01:00 | 124 | 122
2016-06-15 01:30 | 110 | 108
2016-06-15 02:00 | 100 | 98
2016-06-15 02:30 | 93 | 90
2016-06-15 03:00 | 89 | 87
2016-06-15 03:30 | 89 | 87
2016-06-15 04:00 | 88 | 86
2016-06-15 04:30 | 91 | 89
2016-06-15 05:00 | 89 | 87
2016-06-15 05:30 | 96 | 94
2016-06-15 06:00 | 101 | 99
2016-06-15 06:30 | 91 | 89
2016-06-15 07:00 | 61 | 58
2016-06-15 07:30 | 78 | 75
2016-06-15 08:00 | 57 | 53
2016-06-15 08:30 | 55 | 50
2016-06-15 09:00 | 80 | 78
2016-06-15 09:30 | 106 | 103
2016-06-15 10:00 | 69 | 66
2016-06-15 10:30 | 91 | 89
2016-06-15 11:00 | 104 | 101
2016-06-15 11:30 | 111 | 109
2016-06-15 12:00 | 118 | 116
2016-06-15 12:30 | 128 | 126
2016-06-15 13:00 | 145 | 143
2016-06-15 13:30 | 141 | 139
2016-06-15 14:00 | 143 | 141
2016-06-15 14:30 | 145 | 143
2016-06-15 15:00 | 123 | 121
2016-06-15 15:30 | 77 | 74
2016-06-15 16:00 | 57 | 54
2016-06-15 16:30 | 97 | 94
2016-06-15 17:00 | 87 | 84
2016-06-15 17:30 | 83 | 80
2016-06-15 18:00 | 70 | 62
2016-06-15 18:30 | 105 | 101
2016-06-15 19:00 | 120 | 118
2016-06-15 19:30 | 136 | 134
2016-06-15 20:00 | 135 | 132
2016-06-15 20:30 | 133 | 130
2016-06-15 21:00 | 158 | 156
2016-06-15 21:30 | 141 | 139
2016-06-15 22:00 | 151 | 148
2016-06-15 22:30 | 168 | 165
2016-06-15 23:00 | 218 | 215
2016-06-15 23:30 | 213 | 211
2016-06-16 | 205 | 203
2016-06-16 00:30 | 193 | 191
2016-06-16 01:00 | 185 | 183
2016-06-16 01:30 | 175 | 173
2016-06-16 02:00 | 165 | 162
2016-06-16 02:30 | 158 | 155
2016-06-16 03:00 | 156 | 154
2016-06-16 03:30 | 156 | 153
2016-06-16 04:00 | 156 | 153
2016-06-16 04:30 | 151 | 149
2016-06-16 05:00 | 152 | 150
2016-06-16 05:30 | 160 | 157
2016-06-16 06:00 | 167 | 165
2016-06-16 06:30 | 185 | 183
2016-06-16 07:00 | 201 | 199
2016-06-16 07:30 | 213 | 211
2016-06-16 08:00 | 221 | 219
2016-06-16 08:30 | 225 | 223
2016-06-16 09:00 | 229 | 227
2016-06-16 09:30 | 232 | 230
2016-06-16 10:00 | 227 | 225
2016-06-16 10:30 | 221 | 219
2016-06-16 11:00 | 220 | 219
2016-06-16 11:30 | 214 | 212
2016-06-16 12:00 | 221 | 219
2016-06-16 12:30 | 215 | 213
2016-06-16 13:00 | 214 | 213
2016-06-16 13:30 | 211 | 209
2016-06-16 14:00 | 219 | 217
2016-06-16 14:30 | 222 | 221
2016-06-16 15:00 | 220 | 218
2016-06-16 15:30 | 196 | 194
2016-06-16 16:00 | 195 | 193
2016-06-16 16:30 | 195 | 192
2016-06-16 17:00 | 165 | 162
2016-06-16 17:30 | 115 | 112
2016-06-16 18:00 | 74 | 70
2016-06-16 18:30 | 71 | 68
2016-06-16 19:00 | 105 | 103
2016-06-16 19:30 | 114 | 113
2016-06-16 20:00 | 109 | 107
2016-06-16 20:30 | 89 | 87
2016-06-16 21:00 | 87 | 85
2016-06-16 21:30 | 93 | 91
2016-06-16 22:00 | 170 | 168
2016-06-16 22:30 | 159 | 157
2016-06-16 23:00 | 182 | 180
2016-06-16 23:30 | 186 | 184
2016-06-17 | 184 | 182
2016-06-17 00:30 | 172 | 170
2016-06-17 01:00 | 172 | 169
2016-06-17 01:30 | 162 | 160
2016-06-17 02:00 | 153 | 150
2016-06-17 02:30 | 149 | 147
2016-06-17 03:00 | 147 | 145
2016-06-17 03:30 | 144 | 142
2016-06-17 04:00 | 145 | 143
2016-06-17 04:30 | 147 | 145
2016-06-17 05:00 | 150 | 147
2016-06-17 05:30 | 156 | 154
2016-06-17 06:00 | 158 | 155
2016-06-17 06:30 | 163 | 160
2016-06-17 07:00 | 180 | 178
2016-06-17 07:30 | 197 | 194
2016-06-17 08:00 | 211 | 209
2016-06-17 08:30 | 226 | 224
2016-06-17 09:00 | 228 | 227
2016-06-17 09:30 | 226 | 224
2016-06-17 10:00 | 218 | 216
2016-06-17 10:30 | 221 | 219
2016-06-17 11:00 | 183 | 181
2016-06-17 11:30 | 198 | 196
2016-06-17 12:00 | 189 | 187
2016-06-17 12:30 | 182 | 180
2016-06-17 13:00 | 169 | 167
2016-06-17 13:30 | 159 | 156
2016-06-17 14:00 | 162 | 160
2016-06-17 14:30 | 168 | 166
2016-06-17 15:00 | 169 | 167
2016-06-17 15:30 | 172 | 169
2016-06-17 16:00 | 168 | 166
2016-06-17 16:30 | 130 | 127
2016-06-17 17:00 | 45 | 39
2016-06-17 17:30 | 64 | 51
2016-06-17 18:00 | 67 | 54
2016-06-17 18:30 | 13 | 5
2016-06-17 19:00 | 74 | 72
2016-06-17 19:30 | 91 | 89
2016-06-17 20:00 | 87 | 84
2016-06-17 20:30 | 81 | 78
2016-06-17 21:00 | 89 | 87
2016-06-17 21:30 | 81 | 80
2016-06-17 22:00 | 86 | 84
2016-06-17 22:30 | 91 | 89
2016-06-17 23:00 | 91 | 90
2016-06-17 23:30 | 91 | 90
2016-06-18 | 133 | 132
2016-06-18 00:30 | 127 | 126
2016-06-18 01:00 | 116 | 115
2016-06-18 01:30 | 102 | 101
2016-06-18 02:00 | 95 | 93
2016-06-18 02:30 | 89 | 88
2016-06-18 03:00 | 87 | 85
2016-06-18 03:30 | 86 | 84
2016-06-18 04:00 | 85 | 83
2016-06-18 04:30 | 86 | 84
2016-06-18 05:00 | 86 | 84
2016-06-18 05:30 | 89 | 88
2016-06-18 06:00 | 90 | 88
2016-06-18 06:30 | 98 | 96
2016-06-18 07:00 | 105 | 103
2016-06-18 07:30 | 112 | 111
2016-06-18 08:00 | 115 | 114
2016-06-18 08:30 | 123 | 121
2016-06-18 09:00 | 90 | 88
2016-06-18 09:30 | 67 | 65
2016-06-18 10:00 | 76 | 75
2016-06-18 10:30 | 113 | 112
2016-06-18 11:00 | 120 | 118
2016-06-18 11:30 | 76 | 74
2016-06-18 12:00 | 66 | 63
2016-06-18 12:30 | 63 | 61
2016-06-18 13:00 | 61 | 59
2016-06-18 13:30 | 61 | 59
2016-06-18 14:00 | 65 | 62
2016-06-18 14:30 | 65 | 63
2016-06-18 15:00 | 73 | 71
2016-06-18 15:30 | 74 | 72
2016-06-18 16:00 | 68 | 66
2016-06-18 16:30 | 73 | 70
2016-06-18 17:00 | 83 | 81
2016-06-18 17:30 | 85 | 83
2016-06-18 18:00 | 100 | 98
2016-06-18 18:30 | 115 | 113
2016-06-18 19:00 | 128 | 127
2016-06-18 19:30 | 179 | 178
2016-06-18 20:00 | 242 | 241
2016-06-18 20:30 | 244 | 243
2016-06-18 21:00 | 234 | 233
2016-06-18 21:30 | 223 | 221
2016-06-18 22:00 | 228 | 226
2016-06-18 22:30 | 221 | 219
2016-06-18 23:00 | 216 | 213
2016-06-18 23:30 | 205 | 203
2016-06-19 | 202 | 200
2016-06-19 00:30 | 195 | 192
2016-06-19 01:00 | 190 | 187
2016-06-19 01:30 | 178 | 174
2016-06-19 02:00 | 172 | 168
2016-06-19 02:30 | 168 | 165
2016-06-19 03:00 | 166 | 163
2016-06-19 03:30 | 165 | 163
2016-06-19 04:00 | 169 | 167
2016-06-19 04:30 | 169 | 167
2016-06-19 05:00 | 169 | 166
2016-06-19 05:30 | 173 | 171
2016-06-19 06:00 | 174 | 172
2016-06-19 06:30 | 183 | 181
2016-06-19 07:00 | 187 | 185
2016-06-19 07:30 | 188 | 186
2016-06-19 08:00 | 198 | 197
2016-06-19 08:30 | 213 | 211
2016-06-19 09:00 | 220 | 219
2016-06-19 09:30 | 226 | 224
2016-06-19 10:00 | 218 | 217
2016-06-19 10:30 | 213 | 211
2016-06-19 11:00 | 203 | 202
2016-06-19 11:30 | 195 | 193
2016-06-19 12:00 | 191 | 189
2016-06-19 12:30 | 181 | 180
2016-06-19 13:00 | 179 | 177
2016-06-19 13:30 | 177 | 175
2016-06-19 14:00 | 171 | 169
2016-06-19 14:30 | 180 | 178
2016-06-19 15:00 | 180 | 178
2016-06-19 15:30 | 179 | 177
2016-06-19 16:00 | 181 | 179
2016-06-19 16:30 | 181 | 179
2016-06-19 17:00 | 173 | 170
2016-06-19 17:30 | 195 | 193
2016-06-19 18:00 | 208 | 207
2016-06-19 18:30 | 216 | 215
2016-06-19 19:00 | 225 | 223
2016-06-19 19:30 | 219 | 217
2016-06-19 20:00 | 212 | 211
2016-06-19 20:30 | 205 | 203
2016-06-19 21:00 | 198 | 196
2016-06-19 21:30 | 190 | 189
2016-06-19 22:00 | 188 | 186
2016-06-19 22:30 | 191 | 189
2016-06-19 23:00 | 186 | 184
2016-06-19 23:30 | 180 | 178
2016-06-20 | 180 | 177
2016-06-20 00:30 | 171 | 169
2016-06-20 01:00 | 166 | 163
2016-06-20 01:30 | 158 | 155
2016-06-20 02:00 | 152 | 150
2016-06-20 02:30 | 147 | 144
2016-06-20 03:00 | 144 | 142
2016-06-20 03:30 | 147 | 144
2016-06-20 04:00 | 152 | 149
2016-06-20 04:30 | 154 | 152
2016-06-20 05:00 | 157 | 155
2016-06-20 05:30 | 166 | 164
2016-06-20 06:00 | 175 | 173
2016-06-20 06:30 | 193 | 192
2016-06-20 07:00 | 208 | 207
2016-06-20 07:30 | 225 | 223
2016-06-20 08:00 | 229 | 228
2016-06-20 08:30 | 232 | 230
2016-06-20 09:00 | 233 | 231
2016-06-20 09:30 | 229 | 227
2016-06-20 10:00 | 222 | 220
2016-06-20 10:30 | 218 | 216
2016-06-20 11:00 | 202 | 200
2016-06-20 11:30 | 194 | 192
2016-06-20 12:00 | 193 | 191
2016-06-20 12:30 | 196 | 194
2016-06-20 13:00 | 196 | 194
2016-06-20 13:30 | 191 | 188
2016-06-20 14:00 | 197 | 195
2016-06-20 14:30 | 202 | 199
2016-06-20 15:00 | 205 | 203
2016-06-20 15:30 | 207 | 205
2016-06-20 16:00 | 166 | 164
2016-06-20 16:30 | 135 | 132
2016-06-20 17:00 | 135 | 132
2016-06-20 17:30 | 88 | 85
2016-06-20 18:00 | 32 | 26
2016-06-20 18:30 | 45 | 39
2016-06-20 19:00 | 87 | 84
2016-06-20 19:30 | 113 | 111
2016-06-20 20:00 | 104 | 102
2016-06-20 20:30 | 99 | 96
2016-06-20 21:00 | 141 | 139
2016-06-20 21:30 | 134 | 132
2016-06-20 22:00 | 135 | 133
2016-06-20 22:30 | 134 | 132
2016-06-20 23:00 | 130 | 128
2016-06-20 23:30 | 194 | 192
2016-06-21 | 205 | 204
2016-06-21 00:30 | 192 | 191
2016-06-21 01:00 | 180 | 178
2016-06-21 01:30 | 167 | 165
2016-06-21 02:00 | 160 | 157
2016-06-21 02:30 | 154 | 152
2016-06-21 03:00 | 152 | 150
2016-06-21 03:30 | 152 | 149
2016-06-21 04:00 | 149 | 147
2016-06-21 04:30 | 149 | 147
2016-06-21 05:00 | 154 | 151
2016-06-21 05:30 | 161 | 158
2016-06-21 06:00 | 172 | 170
2016-06-21 06:30 | 193 | 191
2016-06-21 07:00 | 210 | 208
2016-06-21 07:30 | 226 | 225
2016-06-21 08:00 | 231 | 229
2016-06-21 08:30 | 236 | 235
2016-06-21 09:00 | 237 | 235
2016-06-21 09:30 | 232 | 230
2016-06-21 10:00 | 223 | 221
2016-06-21 10:30 | 218 | 216
2016-06-21 11:00 | 203 | 201
2016-06-21 11:30 | 194 | 192
2016-06-21 12:00 | 196 | 194
2016-06-21 12:30 | 196 | 194
2016-06-21 13:00 | 198 | 197
2016-06-21 13:30 | 200 | 199
2016-06-21 14:00 | 202 | 201
2016-06-21 14:30 | 205 | 204
2016-06-21 15:00 | 205 | 204
2016-06-21 15:30 | 209 | 207
2016-06-21 16:00 | 214 | 212
2016-06-21 16:30 | 170 | 167
2016-06-21 17:00 | 136 | 133
2016-06-21 17:30 | 136 | 134
2016-06-21 18:00 | 135 | 132
2016-06-21 18:30 | 119 | 116
2016-06-21 19:00 | 106 | 103
2016-06-21 19:30 | 106 | 103
2016-06-21 20:00 | 131 | 129
2016-06-21 20:30 | 125 | 123
2016-06-21 21:00 | 123 | 121
2016-06-21 21:30 | 181 | 179
2016-06-21 22:00 | 201 | 199
2016-06-21 22:30 | 216 | 214
2016-06-21 23:00 | 218 | 216
2016-06-21 23:30 | 213 | 211
2016-06-22 | 207 | 205
2016-06-22 00:30 | 195 | 193
2016-06-22 01:00 | 184 | 182
2016-06-22 01:30 | 173 | 171
2016-06-22 02:00 | 163 | 161
2016-06-22 02:30 | 158 | 156
2016-06-22 03:00 | 153 | 151
2016-06-22 03:30 | 153 | 150
2016-06-22 04:00 | 153 | 150
2016-06-22 04:30 | 155 | 153
2016-06-22 05:00 | 158 | 155
2016-06-22 05:30 | 164 | 162
2016-06-22 06:00 | 174 | 172
2016-06-22 06:30 | 194 | 192
2016-06-22 07:00 | 211 | 209
2016-06-22 07:30 | 230 | 228
2016-06-22 08:00 | 230 | 229
2016-06-22 08:30 | 239 | 237
2016-06-22 09:00 | 241 | 240
2016-06-22 09:30 | 241 | 239
2016-06-22 10:00 | 241 | 239
2016-06-22 10:30 | 236 | 234
2016-06-22 11:00 | 220 | 218
2016-06-22 11:30 | 214 | 212
2016-06-22 12:00 | 210 | 207
2016-06-22 12:30 | 210 | 208
2016-06-22 13:00 | 214 | 212
2016-06-22 13:30 | 220 | 218
2016-06-22 14:00 | 224 | 222
2016-06-22 14:30 | 228 | 226
2016-06-22 15:00 | 225 | 223
2016-06-22 15:30 | 179 | 176
2016-06-22 16:00 | 146 | 143
2016-06-22 16:30 | 150 | 147
2016-06-22 17:00 | 152 | 149
2016-06-22 17:30 | 154 | 151
2016-06-22 18:00 | 151 | 148
2016-06-22 18:30 | 151 | 149
2016-06-22 19:00 | 151 | 149
2016-06-22 19:30 | 148 | 146
2016-06-22 20:00 | 146 | 143
2016-06-22 20:30 | 140 | 138
2016-06-22 21:00 | 133 | 131
2016-06-22 21:30 | 124 | 121
2016-06-22 22:00 | 125 | 122
2016-06-22 22:30 | 132 | 129
2016-06-22 23:00 | 205 | 203
2016-06-22 23:30 | 214 | 212
2016-06-23 | 204 | 202
2016-06-23 00:30 | 189 | 187
2016-06-23 01:00 | 180 | 178
2016-06-23 01:30 | 169 | 167
2016-06-23 02:00 | 161 | 158
2016-06-23 02:30 | 157 | 154
2016-06-23 03:00 | 154 | 150
2016-06-23 03:30 | 151 | 148
2016-06-23 04:00 | 151 | 148
2016-06-23 04:30 | 153 | 150
2016-06-23 05:00 | 157 | 154
2016-06-23 05:30 | 165 | 162
2016-06-23 06:00 | 174 | 171
2016-06-23 06:30 | 192 | 189
2016-06-23 07:00 | 205 | 203
2016-06-23 07:30 | 219 | 217
2016-06-23 08:00 | 231 | 229
2016-06-23 08:30 | 239 | 237
2016-06-23 09:00 | 239 | 237
2016-06-23 09:30 | 242 | 241
2016-06-23 10:00 | 243 | 241
2016-06-23 10:30 | 242 | 240
2016-06-23 11:00 | 224 | 222
2016-06-23 11:30 | 226 | 224
2016-06-23 12:00 | 225 | 223
2016-06-23 12:30 | 219 | 217
2016-06-23 13:00 | 214 | 211
2016-06-23 13:30 | 215 | 212
2016-06-23 14:00 | 216 | 213
2016-06-23 14:30 | 217 | 215
2016-06-23 15:00 | 217 | 215
2016-06-23 15:30 | 173 | 170
2016-06-23 16:00 | 150 | 148
2016-06-23 16:30 | 147 | 143
2016-06-23 17:00 | 158 | 156
2016-06-23 17:30 | 149 | 146
2016-06-23 18:00 | 102 | 97
2016-06-23 18:30 | 95 | 90
2016-06-23 19:00 | 95 | 90
2016-06-23 19:30 | 89 | 85
2016-06-23 20:00 | 132 | 129
2016-06-23 20:30 | 148 | 145
2016-06-23 21:00 | 138 | 136
2016-06-23 21:30 | 136 | 134
2016-06-23 22:00 | 160 | 158
2016-06-23 22:30 | 159 | 157
2016-06-23 23:00 | 167 | 165
2016-06-23 23:30 | 216 | 214
2016-06-24 | 208 | 206
2016-06-24 00:30 | 194 | 192
2016-06-24 01:00 | 180 | 178
2016-06-24 01:30 | 172 | 170
2016-06-24 02:00 | 164 | 162
2016-06-24 02:30 | 161 | 159
2016-06-24 03:00 | 158 | 156
2016-06-24 03:30 | 157 | 155
2016-06-24 04:00 | 157 | 155
2016-06-24 04:30 | 157 | 155
2016-06-24 05:00 | 159 | 157
2016-06-24 05:30 | 167 | 165
2016-06-24 06:00 | 178 | 176
2016-06-24 06:30 | 198 | 196
2016-06-24 07:00 | 194 | 191
2016-06-24 07:30 | 205 | 202
2016-06-24 08:00 | 230 | 228
2016-06-24 08:30 | 242 | 240
2016-06-24 09:00 | 248 | 246
2016-06-24 09:30 | 244 | 242
2016-06-24 10:00 | 247 | 245
2016-06-24 10:30 | 246 | 244
2016-06-24 11:00 | 233 | 232
2016-06-24 11:30 | 228 | 226
2016-06-24 12:00 | 228 | 226
2016-06-24 12:30 | 231 | 229
2016-06-24 13:00 | 229 | 227
2016-06-24 13:30 | 230 | 228
2016-06-24 14:00 | 235 | 233
2016-06-24 14:30 | 240 | 238
2016-06-24 15:00 | 243 | 242
2016-06-24 15:30 | 246 | 244
2016-06-24 16:00 | 219 | 217
2016-06-24 16:30 | 200 | 197
2016-06-24 17:00 | 178 | 176
2016-06-24 17:30 | 174 | 172
2016-06-24 18:00 | 153 | 150
2016-06-24 18:30 | 154 | 152
2016-06-24 19:00 | 159 | 157
2016-06-24 19:30 | 179 | 177
2016-06-24 20:00 | 153 | 151
2016-06-24 20:30 | 141 | 139
2016-06-24 21:00 | 153 | 151
2016-06-24 21:30 | 172 | 170
2016-06-24 22:00 | 189 | 187
2016-06-24 22:30 | 144 | 142
2016-06-24 23:00 | 156 | 154
2016-06-24 23:30 | 158 | 156
2016-06-25 | 142 | 140
2016-06-25 00:30 | 191 | 189
2016-06-25 01:00 | 186 | 183
2016-06-25 01:30 | 176 | 173
2016-06-25 02:00 | 165 | 162
2016-06-25 02:30 | 161 | 157
2016-06-25 03:00 | 158 | 155
2016-06-25 03:30 | 155 | 152
2016-06-25 04:00 | 150 | 147
2016-06-25 04:30 | 159 | 156
2016-06-25 05:00 | 160 | 157
2016-06-25 05:30 | 161 | 158
2016-06-25 06:00 | 166 | 163
2016-06-25 06:30 | 170 | 168
2016-06-25 07:00 | 174 | 171
2016-06-25 07:30 | 180 | 178
2016-06-25 08:00 | 165 | 162
2016-06-25 08:30 | 180 | 177
2016-06-25 09:00 | 201 | 199
2016-06-25 09:30 | 201 | 199
2016-06-25 10:00 | 202 | 200
2016-06-25 10:30 | 198 | 196
2016-06-25 11:00 | 181 | 180
2016-06-25 11:30 | 173 | 171
2016-06-25 12:00 | 174 | 172
2016-06-25 12:30 | 174 | 172
2016-06-25 13:00 | 172 | 170
2016-06-25 13:30 | 168 | 166
2016-06-25 14:00 | 169 | 167
2016-06-25 14:30 | 175 | 173
2016-06-25 15:00 | 179 | 177
2016-06-25 15:30 | 183 | 181
2016-06-25 16:00 | 138 | 135
2016-06-25 16:30 | 104 | 101
2016-06-25 17:00 | 106 | 102
2016-06-25 17:30 | 111 | 107
2016-06-25 18:00 | 107 | 103
2016-06-25 18:30 | 118 | 115
2016-06-25 19:00 | 126 | 124
2016-06-25 19:30 | 181 | 179
2016-06-25 20:00 | 195 | 193
2016-06-25 20:30 | 179 | 177
2016-06-25 21:00 | 170 | 168
2016-06-25 21:30 | 180 | 177
2016-06-25 22:00 | 179 | 176
2016-06-25 22:30 | 187 | 185
2016-06-25 23:00 | 185 | 183
2016-06-25 23:30 | 178 | 176
2016-06-26 | 177 | 175
2016-06-26 00:30 | 177 | 175
2016-06-26 01:00 | 172 | 170
2016-06-26 01:30 | 163 | 160
2016-06-26 02:00 | 157 | 154
2016-06-26 02:30 | 154 | 151
2016-06-26 03:00 | 152 | 149
2016-06-26 03:30 | 148 | 146
2016-06-26 04:00 | 144 | 141
2016-06-26 04:30 | 148 | 146
2016-06-26 05:00 | 149 | 146
2016-06-26 05:30 | 151 | 148
2016-06-26 06:00 | 155 | 152
2016-06-26 06:30 | 160 | 157
2016-06-26 07:00 | 169 | 166
2016-06-26 07:30 | 169 | 166
2016-06-26 08:00 | 168 | 166
2016-06-26 08:30 | 156 | 152
2016-06-26 09:00 | 177 | 174
2016-06-26 09:30 | 167 | 164
2016-06-26 10:00 | 171 | 168
2016-06-26 10:30 | 185 | 182
2016-06-26 11:00 | 182 | 180
2016-06-26 11:30 | 178 | 177
2016-06-26 12:00 | 184 | 182
2016-06-26 12:30 | 188 | 186
2016-06-26 13:00 | 187 | 185
2016-06-26 13:30 | 188 | 186
2016-06-26 14:00 | 181 | 179
2016-06-26 14:30 | 175 | 173
2016-06-26 15:00 | 178 | 175
2016-06-26 15:30 | 181 | 179
2016-06-26 16:00 | 119 | 116
2016-06-26 16:30 | 75 | 70
2016-06-26 17:00 | 15 | 1
2016-06-26 17:30 | 29 | 18
2016-06-26 18:00 | 23 | 11
2016-06-26 18:30 | 18 | 11
2016-06-26 19:00 | 89 | 86
2016-06-26 19:30 | 144 | 142
2016-06-26 20:00 | 151 | 149
2016-06-26 20:30 | 146 | 144
2016-06-26 21:00 | 164 | 161
2016-06-26 21:30 | 175 | 173
2016-06-26 22:00 | 181 | 179
2016-06-26 22:30 | 193 | 191
2016-06-26 23:00 | 193 | 191
2016-06-26 23:30 | 184 | 182
2016-06-27 | 185 | 183
2016-06-27 00:30 | 178 | 176
2016-06-27 01:00 | 171 | 169
2016-06-27 01:30 | 162 | 160
2016-06-27 02:00 | 159 | 156
2016-06-27 02:30 | 156 | 153
2016-06-27 03:00 | 152 | 150
2016-06-27 03:30 | 153 | 151
2016-06-27 04:00 | 152 | 150
2016-06-27 04:30 | 147 | 145
2016-06-27 05:00 | 131 | 129
2016-06-27 05:30 | 130 | 128
2016-06-27 06:00 | 140 | 138
2016-06-27 06:30 | 147 | 145
2016-06-27 07:00 | 133 | 131
2016-06-27 07:30 | 153 | 151
2016-06-27 08:00 | 164 | 162
2016-06-27 08:30 | 167 | 165
2016-06-27 09:00 | 152 | 149
2016-06-27 09:30 | 120 | 117
2016-06-27 10:00 | 133 | 131
2016-06-27 10:30 | 146 | 144
2016-06-27 11:00 | 149 | 147
2016-06-27 11:30 | 149 | 146
2016-06-27 12:00 | 161 | 160
2016-06-27 12:30 | 159 | 157
2016-06-27 13:00 | 144 | 142
2016-06-27 13:30 | 141 | 139
2016-06-27 14:00 | 145 | 144
2016-06-27 14:30 | 147 | 144
2016-06-27 15:00 | 151 | 149
2016-06-27 15:30 | 151 | 149
2016-06-27 16:00 | 144 | 142
2016-06-27 16:30 | 148 | 146
2016-06-27 17:00 | 112 | 110
2016-06-27 17:30 | 81 | 78
2016-06-27 18:00 | 23 | 15
2016-06-27 18:30 | 35 | 29
2016-06-27 19:00 | 43 | 39
2016-06-27 19:30 | 55 | 53
2016-06-27 20:00 | 76 | 75
2016-06-27 20:30 | 49 | 47
2016-06-27 21:00 | 43 | 40
2016-06-27 21:30 | 92 | 90
2016-06-27 22:00 | 130 | 128
2016-06-27 22:30 | 107 | 105
2016-06-27 23:00 | 103 | 101
2016-06-27 23:30 | 134 | 132
2016-06-28 | 130 | 128
2016-06-28 00:30 | 118 | 116
2016-06-28 01:00 | 107 | 105
2016-06-28 01:30 | 95 | 93
2016-06-28 02:00 | 85 | 82
2016-06-28 02:30 | 82 | 79
2016-06-28 03:00 | 80 | 76
2016-06-28 03:30 | 79 | 76
2016-06-28 04:00 | 84 | 81
2016-06-28 04:30 | 90 | 87
2016-06-28 05:00 | 95 | 93
2016-06-28 05:30 | 99 | 97
2016-06-28 06:00 | 109 | 107
2016-06-28 06:30 | 73 | 70
2016-06-28 07:00 | 42 | 35
2016-06-28 07:30 | 66 | 62
2016-06-28 08:00 | 33 | 27
2016-06-28 08:30 | 13 | 1
2016-06-28 09:00 | 61 | 58
2016-06-28 09:30 | 84 | 82
2016-06-28 10:00 | 80 | 77
2016-06-28 10:30 | 87 | 84
2016-06-28 11:00 | 75 | 71
2016-06-28 11:30 | 82 | 79
2016-06-28 12:00 | 69 | 65
2016-06-28 12:30 | 74 | 70
2016-06-28 13:00 | 92 | 89
2016-06-28 13:30 | 104 | 102
2016-06-28 14:00 | 124 | 122
2016-06-28 14:30 | 119 | 116
2016-06-28 15:00 | 116 | 114
2016-06-28 15:30 | 124 | 122
2016-06-28 16:00 | 125 | 123
2016-06-28 16:30 | 102 | 99
2016-06-28 17:00 | 79 | 75
2016-06-28 17:30 | 27 | 6
2016-06-28 18:00 | 47 | 39
2016-06-28 18:30 | 21 | 10
2016-06-28 19:00 | 49 | 40
2016-06-28 19:30 | 58 | 49
2016-06-28 20:00 | 64 | 54
2016-06-28 20:30 | 79 | 68
2016-06-28 21:00 | 76 | 66
2016-06-28 21:30 | 70 | 62
2016-06-28 22:00 | 36 | 33
2016-06-28 22:30 | 28 | 23
2016-06-28 23:00 | 43 | 40
2016-06-28 23:30 | 153 | 152
2016-06-29 | 184 | 182
2016-06-29 00:30 | 172 | 170
2016-06-29 01:00 | 163 | 161
2016-06-29 01:30 | 153 | 151
2016-06-29 02:00 | 147 | 144
2016-06-29 02:30 | 142 | 140
2016-06-29 03:00 | 138 | 136
2016-06-29 03:30 | 138 | 136
2016-06-29 04:00 | 138 | 136
2016-06-29 04:30 | 142 | 140
2016-06-29 05:00 | 146 | 144
2016-06-29 05:30 | 149 | 147
2016-06-29 06:00 | 158 | 156
2016-06-29 06:30 | 169 | 167
2016-06-29 07:00 | 146 | 142
2016-06-29 07:30 | 161 | 157
2016-06-29 08:00 | 167 | 164
2016-06-29 08:30 | 170 | 167
2016-06-29 09:00 | 186 | 183
2016-06-29 09:30 | 190 | 188
2016-06-29 10:00 | 197 | 196
2016-06-29 10:30 | 196 | 194
2016-06-29 11:00 | 193 | 191
2016-06-29 11:30 | 192 | 190
2016-06-29 12:00 | 190 | 188
2016-06-29 12:30 | 187 | 185
2016-06-29 13:00 | 186 | 184
2016-06-29 13:30 | 188 | 186
2016-06-29 14:00 | 192 | 190
2016-06-29 14:30 | 180 | 178
2016-06-29 15:00 | 180 | 178
2016-06-29 15:30 | 184 | 182
2016-06-29 16:00 | 188 | 186
2016-06-29 16:30 | 195 | 193
2016-06-29 17:00 | 156 | 153
2016-06-29 17:30 | 106 | 102
2016-06-29 18:00 | 81 | 75
2016-06-29 18:30 | 96 | 93
2016-06-29 19:00 | 106 | 104
2016-06-29 19:30 | 100 | 98
2016-06-29 20:00 | 105 | 103
2016-06-29 20:30 | 103 | 101
2016-06-29 21:00 | 132 | 130
2016-06-29 21:30 | 154 | 152
2016-06-29 22:00 | 155 | 153
2016-06-29 22:30 | 93 | 91
2016-06-29 23:00 | 84 | 82
2016-06-29 23:30 | 93 | 92
2016-06-30 | 113 | 112
2016-06-30 00:30 | 168 | 166
2016-06-30 01:00 | 166 | 164
2016-06-30 01:30 | 156 | 154
2016-06-30 02:00 | 144 | 142
2016-06-30 02:30 | 135 | 132
2016-06-30 03:00 | 134 | 132
2016-06-30 03:30 | 135 | 132
2016-06-30 04:00 | 131 | 129
2016-06-30 04:30 | 143 | 140
2016-06-30 05:00 | 148 | 145
2016-06-30 05:30 | 155 | 153
2016-06-30 06:00 | 165 | 163
2016-06-30 06:30 | 175 | 174
2016-06-30 07:00 | 145 | 141
2016-06-30 07:30 | 155 | 152
2016-06-30 08:00 | 163 | 159
2016-06-30 08:30 | 170 | 167
2016-06-30 09:00 | 170 | 167
2016-06-30 09:30 | 175 | 173
2016-06-30 10:00 | 197 | 195
2016-06-30 10:30 | 197 | 193
2016-06-30 11:00 | 203 | 200
2016-06-30 11:30 | 200 | 197
2016-06-30 12:00 | 199 | 196
2016-06-30 12:30 | 201 | 198
2016-06-30 13:00 | 195 | 191
2016-06-30 13:30 | 176 | 172
2016-06-30 14:00 | 187 | 183
2016-06-30 14:30 | 189 | 186
2016-06-30 15:00 | 188 | 185
2016-06-30 15:30 | 199 | 197
2016-06-30 16:00 | 198 | 194
2016-06-30 16:30 | 201 | 197
2016-06-30 17:00 | 165 | 160
2016-06-30 17:30 | 163 | 159
2016-06-30 18:00 | 104 | 98
2016-06-30 18:30 | 105 | 101
2016-06-30 19:00 | 136 | 133
2016-06-30 19:30 | 133 | 130
2016-06-30 20:00 | 124 | 121
2016-06-30 20:30 | 100 | 95
2016-06-30 21:00 | 87 | 81
2016-06-30 21:30 | 104 | 100
2016-06-30 22:00 | 133 | 130
2016-06-30 22:30 | 88 | 81
2016-06-30 23:00 | 93 | 88
2016-06-30 23:30 | 155 | 152
2016-07-01 | 176 | 173
2016-07-01 00:30 | 169 | 166
2016-07-01 01:00 | 167 | 164
2016-07-01 01:30 | 158 | 155
2016-07-01 02:00 | 151 | 148
2016-07-01 02:30 | 148 | 145
2016-07-01 03:00 | 145 | 141
2016-07-01 03:30 | 142 | 139
2016-07-01 04:00 | 141 | 138
2016-07-01 04:30 | 141 | 138
2016-07-01 05:00 | 145 | 141
2016-07-01 05:30 | 152 | 149
2016-07-01 06:00 | 163 | 160
2016-07-01 06:30 | 176 | 173
2016-07-01 07:00 | 155 | 150
2016-07-01 07:30 | 165 | 161
2016-07-01 08:00 | 171 | 167
2016-07-01 08:30 | 172 | 169
2016-07-01 09:00 | 183 | 180
2016-07-01 09:30 | 188 | 184
2016-07-01 10:00 | 194 | 191
2016-07-01 10:30 | 188 | 184
2016-07-01 11:00 | 188 | 184
2016-07-01 11:30 | 185 | 181
2016-07-01 12:00 | 193 | 190
2016-07-01 12:30 | 190 | 187
2016-07-01 13:00 | 183 | 178
2016-07-01 13:30 | 199 | 196
2016-07-01 14:00 | 196 | 193
2016-07-01 14:30 | 191 | 187
2016-07-01 15:00 | 186 | 183
2016-07-01 15:30 | 186 | 182
2016-07-01 16:00 | 190 | 186
2016-07-01 16:30 | 198 | 195
2016-07-01 17:00 | 198 | 195
2016-07-01 17:30 | 194 | 190
2016-07-01 18:00 | 163 | 158
2016-07-01 18:30 | 165 | 161
2016-07-01 19:00 | 174 | 170
2016-07-01 19:30 | 178 | 175
2016-07-01 20:00 | 182 | 179
2016-07-01 20:30 | 178 | 175
2016-07-01 21:00 | 169 | 165
2016-07-01 21:30 | 182 | 180
2016-07-01 22:00 | 206 | 204
2016-07-01 22:30 | 207 | 204
2016-07-01 23:00 | 199 | 195
2016-07-01 23:30 | 192 | 190
2016-07-02 | 187 | 184
2016-07-02 00:30 | 182 | 179
2016-07-02 01:00 | 169 | 166
2016-07-02 01:30 | 161 | 158
2016-07-02 02:00 | 154 | 151
2016-07-02 02:30 | 153 | 150
2016-07-02 03:00 | 151 | 147
2016-07-02 03:30 | 153 | 149
2016-07-02 04:00 | 150 | 146
2016-07-02 04:30 | 147 | 143
2016-07-02 05:00 | 149 | 145
2016-07-02 05:30 | 152 | 149
2016-07-02 06:00 | 159 | 156
2016-07-02 06:30 | 164 | 161
2016-07-02 07:00 | 168 | 165
2016-07-02 07:30 | 165 | 162
2016-07-02 08:00 | 166 | 163
2016-07-02 08:30 | 163 | 159
2016-07-02 09:00 | 152 | 148
2016-07-02 09:30 | 174 | 170
2016-07-02 10:00 | 187 | 183
2016-07-02 10:30 | 190 | 186
2016-07-02 11:00 | 188 | 184
2016-07-02 11:30 | 189 | 185
2016-07-02 12:00 | 184 | 180
2016-07-02 12:30 | 186 | 182
2016-07-02 13:00 | 189 | 185
2016-07-02 13:30 | 184 | 181
2016-07-02 14:00 | 172 | 168
2016-07-02 14:30 | 166 | 162
2016-07-02 15:00 | 166 | 162
2016-07-02 15:30 | 172 | 167
2016-07-02 16:00 | 179 | 175
2016-07-02 16:30 | 187 | 183
2016-07-02 17:00 | 186 | 182
2016-07-02 17:30 | 191 | 187
2016-07-02 18:00 | 171 | 166
2016-07-02 18:30 | 197 | 194
2016-07-02 19:00 | 209 | 205
2016-07-02 19:30 | 203 | 199
2016-07-02 20:00 | 196 | 192
2016-07-02 20:30 | 188 | 184
2016-07-02 21:00 | 186 | 182
2016-07-02 21:30 | 178 | 173
2016-07-02 22:00 | 180 | 175
2016-07-02 22:30 | 189 | 185
2016-07-02 23:00 | 178 | 174
2016-07-02 23:30 | 167 | 163
2016-07-03 | 180 | 176
2016-07-03 00:30 | 172 | 167
2016-07-03 01:00 | 162 | 158
2016-07-03 01:30 | 158 | 154
2016-07-03 02:00 | 151 | 147
2016-07-03 02:30 | 154 | 149
2016-07-03 03:00 | 153 | 148
2016-07-03 03:30 | 148 | 144
2016-07-03 04:00 | 146 | 142
2016-07-03 04:30 | 146 | 141
2016-07-03 05:00 | 143 | 139
2016-07-03 05:30 | 148 | 143
2016-07-03 06:00 | 152 | 148
2016-07-03 06:30 | 159 | 155
2016-07-03 07:00 | 158 | 154
2016-07-03 07:30 | 161 | 157
2016-07-03 08:00 | 163 | 158
2016-07-03 08:30 | 161 | 157
2016-07-03 09:00 | 166 | 162
2016-07-03 09:30 | 175 | 171
2016-07-03 10:00 | 179 | 177
2016-07-03 10:30 | 184 | 181
2016-07-03 11:00 | 176 | 173
2016-07-03 11:30 | 172 | 169
2016-07-03 12:00 | 173 | 171
2016-07-03 12:30 | 176 | 173
2016-07-03 13:00 | 168 | 165
2016-07-03 13:30 | 169 | 167
2016-07-03 14:00 | 164 | 162
2016-07-03 14:30 | 162 | 160
2016-07-03 15:00 | 167 | 165
2016-07-03 15:30 | 174 | 171
2016-07-03 16:00 | 178 | 175
2016-07-03 16:30 | 183 | 180
2016-07-03 17:00 | 179 | 177
2016-07-03 17:30 | 186 | 184
2016-07-03 18:00 | 180 | 178
2016-07-03 18:30 | 192 | 190
2016-07-03 19:00 | 210 | 208
2016-07-03 19:30 | 203 | 200
2016-07-03 20:00 | 195 | 193
2016-07-03 20:30 | 188 | 185
2016-07-03 21:00 | 181 | 179
2016-07-03 21:30 | 175 | 172
2016-07-03 22:00 | 177 | 175
2016-07-03 22:30 | 183 | 181
2016-07-03 23:00 | 176 | 174
2016-07-03 23:30 | 170 | 167
2016-07-04 | 172 | 170
2016-07-04 00:30 | 164 | 161
2016-07-04 01:00 | 155 | 152
2016-07-04 01:30 | 146 | 143
2016-07-04 02:00 | 138 | 135
2016-07-04 02:30 | 134 | 131
2016-07-04 03:00 | 130 | 127
2016-07-04 03:30 | 131 | 128
2016-07-04 04:00 | 134 | 131
2016-07-04 04:30 | 133 | 130
2016-07-04 05:00 | 134 | 131
2016-07-04 05:30 | 138 | 136
2016-07-04 06:00 | 144 | 142
2016-07-04 06:30 | 155 | 152
2016-07-04 07:00 | 136 | 132
2016-07-04 07:30 | 149 | 145
2016-07-04 08:00 | 155 | 151
2016-07-04 08:30 | 182 | 179
2016-07-04 09:00 | 191 | 188
2016-07-04 09:30 | 176 | 174
2016-07-04 10:00 | 181 | 179
2016-07-04 10:30 | 184 | 182
2016-07-04 11:00 | 186 | 183
2016-07-04 11:30 | 189 | 187
2016-07-04 12:00 | 202 | 200
2016-07-04 12:30 | 202 | 199
2016-07-04 13:00 | 190 | 185
2016-07-04 13:30 | 189 | 185
2016-07-04 14:00 | 197 | 193
2016-07-04 14:30 | 191 | 187
2016-07-04 15:00 | 190 | 186
2016-07-04 15:30 | 193 | 189
2016-07-04 16:00 | 195 | 191
2016-07-04 16:30 | 194 | 190
2016-07-04 17:00 | 201 | 198
2016-07-04 17:30 | 168 | 164
2016-07-04 18:00 | 64 | 59
2016-07-04 18:30 | 61 | 55
2016-07-04 19:00 | 82 | 77
2016-07-04 19:30 | 112 | 108
2016-07-04 20:00 | 137 | 134
2016-07-04 20:30 | 116 | 113
2016-07-04 21:00 | 110 | 106
2016-07-04 21:30 | 162 | 159
2016-07-04 22:00 | 176 | 173
2016-07-04 22:30 | 180 | 177
2016-07-04 23:00 | 188 | 186
2016-07-04 23:30 | 189 | 186
2016-07-05 | 179 | 176
2016-07-05 00:30 | 174 | 172
2016-07-05 01:00 | 165 | 163
2016-07-05 01:30 | 159 | 156
2016-07-05 02:00 | 157 | 154
2016-07-05 02:30 | 147 | 144
2016-07-05 03:00 | 137 | 134
2016-07-05 03:30 | 139 | 136
2016-07-05 04:00 | 139 | 136
2016-07-05 04:30 | 139 | 136
2016-07-05 05:00 | 140 | 137
2016-07-05 05:30 | 148 | 145
2016-07-05 06:00 | 153 | 150
2016-07-05 06:30 | 148 | 145
2016-07-05 07:00 | 149 | 145
2016-07-05 07:30 | 159 | 155
2016-07-05 08:00 | 162 | 158
2016-07-05 08:30 | 173 | 170
2016-07-05 09:00 | 172 | 169
2016-07-05 09:30 | 169 | 165
2016-07-05 10:00 | 162 | 158
2016-07-05 10:30 | 162 | 158
2016-07-05 11:00 | 163 | 159
2016-07-05 11:30 | 173 | 170
2016-07-05 12:00 | 176 | 172
2016-07-05 12:30 | 180 | 174
2016-07-05 13:00 | 166 | 161
2016-07-05 13:30 | 163 | 158
2016-07-05 14:00 | 172 | 168
2016-07-05 14:30 | 166 | 162
2016-07-05 15:00 | 167 | 163
2016-07-05 15:30 | 130 | 125
2016-07-05 16:00 | 106 | 102
2016-07-05 16:30 | 113 | 110
2016-07-05 17:00 | 101 | 98
2016-07-05 17:30 | 26 | 20
2016-07-05 18:00 | 15 | 3
2016-07-05 18:30 | 27 | 23
2016-07-05 19:00 | 58 | 56
2016-07-05 19:30 | 111 | 109
2016-07-05 20:00 | 110 | 107
2016-07-05 20:30 | 102 | 99
2016-07-05 21:00 | 99 | 96
2016-07-05 21:30 | 105 | 102
2016-07-05 22:00 | 112 | 107
2016-07-05 22:30 | 117 | 111
2016-07-05 23:00 | 123 | 117
2016-07-05 23:30 | 119 | 113
2016-07-06 | 114 | 108
2016-07-06 00:30 | 135 | 131
2016-07-06 01:00 | 168 | 163
2016-07-06 01:30 | 158 | 153
2016-07-06 02:00 | 147 | 142
2016-07-06 02:30 | 139 | 135
2016-07-06 03:00 | 134 | 129
2016-07-06 03:30 | 134 | 129
2016-07-06 04:00 | 129 | 124
2016-07-06 04:30 | 131 | 127
2016-07-06 05:00 | 135 | 130
2016-07-06 05:30 | 146 | 142
2016-07-06 06:00 | 155 | 151
2016-07-06 06:30 | 171 | 165
2016-07-06 07:00 | 152 | 145
2016-07-06 07:30 | 170 | 166
2016-07-06 08:00 | 152 | 146
2016-07-06 08:30 | 119 | 113
2016-07-06 09:00 | 115 | 109
2016-07-06 09:30 | 114 | 107
2016-07-06 10:00 | 120 | 115
2016-07-06 10:30 | 110 | 104
2016-07-06 11:00 | 105 | 99
2016-07-06 11:30 | 172 | 168
2016-07-06 12:00 | 191 | 186
2016-07-06 12:30 | 190 | 186
2016-07-06 13:00 | 187 | 183
2016-07-06 13:30 | 188 | 184
2016-07-06 14:00 | 191 | 186
2016-07-06 14:30 | 186 | 181
2016-07-06 15:00 | 181 | 176
2016-07-06 15:30 | 176 | 170
2016-07-06 16:00 | 137 | 129
2016-07-06 16:30 | 109 | 103
2016-07-06 17:00 | 107 | 102
2016-07-06 17:30 | 54 | 42
2016-07-06 18:00 | 21 | 7
2016-07-06 18:30 | 24 | 3
2016-07-06 19:00 | 25 | 0
2016-07-06 19:30 | 26 | 2
2016-07-06 20:00 | 27 | 14
2016-07-06 20:30 | 25 | 11
2016-07-06 21:00 | 39 | 33
2016-07-06 21:30 | 74 | 68
2016-07-06 22:00 | 99 | 95
2016-07-06 22:30 | 77 | 68
2016-07-06 23:00 | 81 | 74
2016-07-06 23:30 | 87 | 83
2016-07-07 | 151 | 148
2016-07-07 00:30 | 160 | 158
2016-07-07 01:00 | 152 | 149
2016-07-07 01:30 | 141 | 138
2016-07-07 02:00 | 132 | 129
2016-07-07 02:30 | 128 | 124
2016-07-07 03:00 | 126 | 123
2016-07-07 03:30 | 125 | 121
2016-07-07 04:00 | 126 | 122
2016-07-07 04:30 | 127 | 123
2016-07-07 05:00 | 129 | 125
2016-07-07 05:30 | 129 | 125
2016-07-07 06:00 | 135 | 131
2016-07-07 06:30 | 124 | 119
2016-07-07 07:00 | 127 | 122
2016-07-07 07:30 | 153 | 149
2016-07-07 08:00 | 137 | 133
2016-07-07 08:30 | 95 | 89
2016-07-07 09:00 | 106 | 100
2016-07-07 09:30 | 121 | 117
2016-07-07 10:00 | 148 | 145
2016-07-07 10:30 | 152 | 148
2016-07-07 11:00 | 148 | 144
2016-07-07 11:30 | 147 | 144
2016-07-07 12:00 | 148 | 145
2016-07-07 12:30 | 147 | 144
2016-07-07 13:00 | 158 | 155
2016-07-07 13:30 | 164 | 161
2016-07-07 14:00 | 159 | 156
2016-07-07 14:30 | 161 | 158
2016-07-07 15:00 | 146 | 142
2016-07-07 15:30 | 149 | 145
2016-07-07 16:00 | 157 | 153
2016-07-07 16:30 | 131 | 126
2016-07-07 17:00 | 114 | 109
2016-07-07 17:30 | 126 | 121
2016-07-07 18:00 | 115 | 110
2016-07-07 18:30 | 94 | 88
2016-07-07 19:00 | 107 | 102
2016-07-07 19:30 | 109 | 105
2016-07-07 20:00 | 112 | 109
2016-07-07 20:30 | 104 | 101
2016-07-07 21:00 | 109 | 106
2016-07-07 21:30 | 128 | 125
2016-07-07 22:00 | 144 | 142
2016-07-07 22:30 | 93 | 89
2016-07-07 23:00 | 87 | 84
2016-07-07 23:30 | 86 | 83
2016-07-08 | 152 | 149
2016-07-08 00:30 | 155 | 152
2016-07-08 01:00 | 147 | 144
2016-07-08 01:30 | 140 | 136
2016-07-08 02:00 | 135 | 131
2016-07-08 02:30 | 127 | 123
2016-07-08 03:00 | 123 | 119
2016-07-08 03:30 | 120 | 116
2016-07-08 04:00 | 119 | 115
2016-07-08 04:30 | 125 | 121
2016-07-08 05:00 | 126 | 122
2016-07-08 05:30 | 133 | 129
2016-07-08 06:00 | 141 | 138
2016-07-08 06:30 | 154 | 151
2016-07-08 07:00 | 163 | 160
2016-07-08 07:30 | 172 | 168
2016-07-08 08:00 | 176 | 172
2016-07-08 08:30 | 178 | 174
2016-07-08 09:00 | 178 | 174
2016-07-08 09:30 | 175 | 172
2016-07-08 10:00 | 150 | 145
2016-07-08 10:30 | 157 | 153
2016-07-08 11:00 | 184 | 181
2016-07-08 11:30 | 192 | 189
2016-07-08 12:00 | 172 | 170
2016-07-08 12:30 | 171 | 169
2016-07-08 13:00 | 166 | 163
2016-07-08 13:30 | 164 | 161
2016-07-08 14:00 | 162 | 158
2016-07-08 14:30 | 157 | 153
2016-07-08 15:00 | 165 | 161
2016-07-08 15:30 | 172 | 169
2016-07-08 16:00 | 173 | 170
2016-07-08 16:30 | 179 | 175
2016-07-08 17:00 | 178 | 174
2016-07-08 17:30 | 175 | 172
2016-07-08 18:00 | 171 | 167
2016-07-08 18:30 | 176 | 173
2016-07-08 19:00 | 178 | 174
2016-07-08 19:30 | 173 | 169
2016-07-08 20:00 | 168 | 165
2016-07-08 20:30 | 164 | 162
2016-07-08 21:00 | 162 | 160
2016-07-08 21:30 | 154 | 151
2016-07-08 22:00 | 167 | 164
2016-07-08 22:30 | 180 | 178
2016-07-08 23:00 | 177 | 175
2016-07-08 23:30 | 172 | 169
2016-07-09 | 173 | 171
2016-07-09 00:30 | 160 | 157
2016-07-09 01:00 | 150 | 147
2016-07-09 01:30 | 137 | 134
2016-07-09 02:00 | 131 | 128
2016-07-09 02:30 | 122 | 119
2016-07-09 03:00 | 124 | 121
2016-07-09 03:30 | 123 | 120
2016-07-09 04:00 | 122 | 118
2016-07-09 04:30 | 123 | 119
2016-07-09 05:00 | 126 | 121
2016-07-09 05:30 | 126 | 122
2016-07-09 06:00 | 130 | 127
2016-07-09 06:30 | 136 | 133
2016-07-09 07:00 | 142 | 139
2016-07-09 07:30 | 153 | 150
2016-07-09 08:00 | 161 | 158
2016-07-09 08:30 | 171 | 167
2016-07-09 09:00 | 171 | 167
2016-07-09 09:30 | 170 | 166
2016-07-09 10:00 | 167 | 163
2016-07-09 10:30 | 163 | 159
2016-07-09 11:00 | 160 | 156
2016-07-09 11:30 | 159 | 155
2016-07-09 12:00 | 157 | 152
2016-07-09 12:30 | 159 | 154
2016-07-09 13:00 | 159 | 155
2016-07-09 13:30 | 153 | 148
2016-07-09 14:00 | 146 | 141
2016-07-09 14:30 | 150 | 145
2016-07-09 15:00 | 153 | 149
2016-07-09 15:30 | 152 | 148
2016-07-09 16:00 | 157 | 153
2016-07-09 16:30 | 162 | 158
2016-07-09 17:00 | 172 | 168
2016-07-09 17:30 | 179 | 175
2016-07-09 18:00 | 184 | 181
2016-07-09 18:30 | 194 | 191
2016-07-09 19:00 | 198 | 195
2016-07-09 19:30 | 196 | 193
2016-07-09 20:00 | 189 | 186
2016-07-09 20:30 | 182 | 179
2016-07-09 21:00 | 178 | 175
2016-07-09 21:30 | 169 | 166
2016-07-09 22:00 | 166 | 163
2016-07-09 22:30 | 169 | 166
2016-07-09 23:00 | 165 | 161
2016-07-09 23:30 | 160 | 156
2016-07-10 | 158 | 154
2016-07-10 00:30 | 153 | 149
2016-07-10 01:00 | 144 | 140
2016-07-10 01:30 | 138 | 134
2016-07-10 02:00 | 129 | 125
2016-07-10 02:30 | 120 | 115
2016-07-10 03:00 | 120 | 116
2016-07-10 03:30 | 108 | 102
2016-07-10 04:00 | 88 | 78
2016-07-10 04:30 | 80 | 64
2016-07-10 05:00 | 81 | 65
2016-07-10 05:30 | 82 | 68
2016-07-10 06:00 | 84 | 72
2016-07-10 06:30 | 90 | 81
2016-07-10 07:00 | 92 | 83
2016-07-10 07:30 | 97 | 90
2016-07-10 08:00 | 107 | 100
2016-07-10 08:30 | 141 | 137
2016-07-10 09:00 | 156 | 152
2016-07-10 09:30 | 163 | 159
2016-07-10 10:00 | 161 | 157
2016-07-10 10:30 | 154 | 150
2016-07-10 11:00 | 155 | 151
2016-07-10 11:30 | 150 | 146
2016-07-10 12:00 | 151 | 147
2016-07-10 12:30 | 152 | 148
2016-07-10 13:00 | 151 | 147
2016-07-10 13:30 | 148 | 143
2016-07-10 14:00 | 140 | 136
2016-07-10 14:30 | 146 | 141
2016-07-10 15:00 | 150 | 146
2016-07-10 15:30 | 156 | 153
2016-07-10 16:00 | 164 | 161
2016-07-10 16:30 | 169 | 165
2016-07-10 17:00 | 173 | 169
2016-07-10 17:30 | 182 | 179
2016-07-10 18:00 | 193 | 190
2016-07-10 18:30 | 208 | 205
2016-07-10 19:00 | 212 | 209
2016-07-10 19:30 | 201 | 198
2016-07-10 20:00 | 195 | 193
2016-07-10 20:30 | 189 | 187
2016-07-10 21:00 | 183 | 180
2016-07-10 21:30 | 176 | 174
2016-07-10 22:00 | 175 | 172
2016-07-10 22:30 | 173 | 170
2016-07-10 23:00 | 169 | 166
2016-07-10 23:30 | 160 | 157
2016-07-11 | 158 | 155
2016-07-11 00:30 | 151 | 148
2016-07-11 01:00 | 147 | 144
2016-07-11 01:30 | 141 | 138
2016-07-11 02:00 | 131 | 127
2016-07-11 02:30 | 128 | 124
2016-07-11 03:00 | 123 | 119
2016-07-11 03:30 | 124 | 120
2016-07-11 04:00 | 125 | 121
2016-07-11 04:30 | 130 | 127
2016-07-11 05:00 | 138 | 135
2016-07-11 05:30 | 144 | 141
2016-07-11 06:00 | 153 | 149
2016-07-11 06:30 | 172 | 168
2016-07-11 07:00 | 186 | 183
2016-07-11 07:30 | 204 | 201
2016-07-11 08:00 | 218 | 215
2016-07-11 08:30 | 222 | 219
2016-07-11 09:00 | 215 | 212
2016-07-11 09:30 | 213 | 211
2016-07-11 10:00 | 210 | 207
2016-07-11 10:30 | 217 | 215
2016-07-11 11:00 | 219 | 216
2016-07-11 11:30 | 245 | 243
2016-07-11 12:00 | 242 | 239
2016-07-11 12:30 | 236 | 233
2016-07-11 13:00 | 232 | 229
2016-07-11 13:30 | 231 | 227
2016-07-11 14:00 | 231 | 228
2016-07-11 14:30 | 236 | 232
2016-07-11 15:00 | 235 | 232
2016-07-11 15:30 | 233 | 230
2016-07-11 16:00 | 241 | 238
2016-07-11 16:30 | 247 | 244
2016-07-11 17:00 | 202 | 199
2016-07-11 17:30 | 148 | 143
2016-07-11 18:00 | 152 | 146
2016-07-11 18:30 | 147 | 141
2016-07-11 19:00 | 147 | 141
2016-07-11 19:30 | 138 | 132
2016-07-11 20:00 | 132 | 128
2016-07-11 20:30 | 129 | 126
2016-07-11 21:00 | 136 | 133
2016-07-11 21:30 | 203 | 201
2016-07-11 22:00 | 221 | 219
2016-07-11 22:30 | 228 | 226
2016-07-11 23:00 | 225 | 223
2016-07-11 23:30 | 224 | 222
2016-07-12 | 221 | 218
2016-07-12 00:30 | 207 | 205
2016-07-12 01:00 | 189 | 186
2016-07-12 01:30 | 167 | 164
2016-07-12 02:00 | 159 | 155
2016-07-12 02:30 | 154 | 151
2016-07-12 03:00 | 153 | 149
2016-07-12 03:30 | 157 | 153
2016-07-12 04:00 | 153 | 150
2016-07-12 04:30 | 152 | 149
2016-07-12 05:00 | 155 | 152
2016-07-12 05:30 | 169 | 166
2016-07-12 06:00 | 179 | 177
2016-07-12 06:30 | 196 | 193
2016-07-12 07:00 | 212 | 209
2016-07-12 07:30 | 227 | 225
2016-07-12 08:00 | 239 | 236
2016-07-12 08:30 | 245 | 242
2016-07-12 09:00 | 236 | 233
2016-07-12 09:30 | 226 | 223
2016-07-12 10:00 | 224 | 221
2016-07-12 10:30 | 222 | 220
2016-07-12 11:00 | 225 | 222
2016-07-12 11:30 | 225 | 222
2016-07-12 12:00 | 226 | 223
2016-07-12 12:30 | 226 | 223
2016-07-12 13:00 | 225 | 222
2016-07-12 13:30 | 227 | 225
2016-07-12 14:00 | 225 | 223
2016-07-12 14:30 | 225 | 223
2016-07-12 15:00 | 227 | 224
2016-07-12 15:30 | 226 | 223
2016-07-12 16:00 | 229 | 227
2016-07-12 16:30 | 238 | 236
2016-07-12 17:00 | 188 | 185
2016-07-12 17:30 | 136 | 132
2016-07-12 18:00 | 113 | 107
2016-07-12 18:30 | 103 | 96
2016-07-12 19:00 | 124 | 119
2016-07-12 19:30 | 136 | 133
2016-07-12 20:00 | 131 | 128
2016-07-12 20:30 | 129 | 126
2016-07-12 21:00 | 126 | 123
2016-07-12 21:30 | 193 | 191
2016-07-12 22:00 | 213 | 211
2016-07-12 22:30 | 222 | 219
2016-07-12 23:00 | 219 | 217
2016-07-12 23:30 | 215 | 212
2016-07-13 | 204 | 202
2016-07-13 00:30 | 191 | 188
2016-07-13 01:00 | 176 | 172
2016-07-13 01:30 | 162 | 159
2016-07-13 02:00 | 158 | 156
2016-07-13 02:30 | 154 | 151
2016-07-13 03:00 | 151 | 148
2016-07-13 03:30 | 149 | 145
2016-07-13 04:00 | 150 | 146
2016-07-13 04:30 | 156 | 152
2016-07-13 05:00 | 160 | 157
2016-07-13 05:30 | 167 | 165
2016-07-13 06:00 | 173 | 170
2016-07-13 06:30 | 192 | 189
2016-07-13 07:00 | 210 | 207
2016-07-13 07:30 | 229 | 227
2016-07-13 08:00 | 241 | 237
2016-07-13 08:30 | 248 | 244
2016-07-13 09:00 | 247 | 243
2016-07-13 09:30 | 230 | 226
2016-07-13 10:00 | 199 | 195
2016-07-13 10:30 | 197 | 192
2016-07-13 11:00 | 198 | 193
2016-07-13 11:30 | 193 | 188
2016-07-13 12:00 | 188 | 184
2016-07-13 12:30 | 188 | 183
2016-07-13 13:00 | 186 | 182
2016-07-13 13:30 | 159 | 153
2016-07-13 14:00 | 144 | 138
2016-07-13 14:30 | 149 | 143
2016-07-13 15:00 | 149 | 143
2016-07-13 15:30 | 150 | 145
2016-07-13 16:00 | 153 | 147
2016-07-13 16:30 | 160 | 155
2016-07-13 17:00 | 159 | 154
2016-07-13 17:30 | 116 | 110
2016-07-13 18:00 | 109 | 103
2016-07-13 18:30 | 102 | 96
2016-07-13 19:00 | 119 | 114
2016-07-13 19:30 | 116 | 110
2016-07-13 20:00 | 110 | 105
2016-07-13 20:30 | 86 | 77
2016-07-13 21:00 | 100 | 93
2016-07-13 21:30 | 96 | 90
2016-07-13 22:00 | 103 | 97
2016-07-13 22:30 | 147 | 143
2016-07-13 23:00 | 144 | 141
2016-07-13 23:30 | 134 | 130
2016-07-14 | 120 | 115
2016-07-14 00:30 | 104 | 99
2016-07-14 01:00 | 109 | 103
2016-07-14 01:30 | 92 | 86
2016-07-14 02:00 | 84 | 77
2016-07-14 02:30 | 81 | 73
2016-07-14 03:00 | 78 | 68
2016-07-14 03:30 | 78 | 69
2016-07-14 04:00 | 76 | 67
2016-07-14 04:30 | 78 | 69
2016-07-14 05:00 | 83 | 76
2016-07-14 05:30 | 87 | 81
2016-07-14 06:00 | 96 | 90
2016-07-14 06:30 | 118 | 114
2016-07-14 07:00 | 125 | 120
2016-07-14 07:30 | 106 | 100
2016-07-14 08:00 | 130 | 125
2016-07-14 08:30 | 176 | 172
2016-07-14 09:00 | 175 | 171
2016-07-14 09:30 | 180 | 177
2016-07-14 10:00 | 172 | 168
2016-07-14 10:30 | 183 | 180
2016-07-14 11:00 | 180 | 177
2016-07-14 11:30 | 173 | 170
2016-07-14 12:00 | 169 | 165
2016-07-14 12:30 | 170 | 167
2016-07-14 13:00 | 168 | 165
2016-07-14 13:30 | 161 | 157
2016-07-14 14:00 | 157 | 153
2016-07-14 14:30 | 157 | 153
2016-07-14 15:00 | 155 | 151
2016-07-14 15:30 | 157 | 152
2016-07-14 16:00 | 161 | 157
2016-07-14 16:30 | 166 | 162
2016-07-14 17:00 | 173 | 169
2016-07-14 17:30 | 123 | 119
2016-07-14 18:00 | 103 | 96
2016-07-14 18:30 | 112 | 106
2016-07-14 19:00 | 125 | 120
2016-07-14 19:30 | 116 | 110
2016-07-14 20:00 | 92 | 83
2016-07-14 20:30 | 74 | 59
2016-07-14 21:00 | 88 | 80
2016-07-14 21:30 | 107 | 101
2016-07-14 22:00 | 147 | 141
2016-07-14 22:30 | 125 | 120
2016-07-14 23:00 | 131 | 126
2016-07-14 23:30 | 148 | 144
2016-07-15 | 137 | 132
2016-07-15 00:30 | 126 | 120
2016-07-15 01:00 | 114 | 108
2016-07-15 01:30 | 101 | 94
2016-07-15 02:00 | 93 | 85
2016-07-15 02:30 | 87 | 77
2016-07-15 03:00 | 85 | 75
2016-07-15 03:30 | 89 | 80
2016-07-15 04:00 | 90 | 81
2016-07-15 04:30 | 91 | 82
2016-07-15 05:00 | 94 | 86
2016-07-15 05:30 | 99 | 92
2016-07-15 06:00 | 111 | 105
2016-07-15 06:30 | 127 | 122
2016-07-15 07:00 | 115 | 109
2016-07-15 07:30 | 127 | 122
2016-07-15 08:00 | 133 | 128
2016-07-15 08:30 | 143 | 138
2016-07-15 09:00 | 166 | 163
2016-07-15 09:30 | 155 | 149
2016-07-15 10:00 | 145 | 140
2016-07-15 10:30 | 147 | 142
2016-07-15 11:00 | 152 | 146
2016-07-15 11:30 | 188 | 183
2016-07-15 12:00 | 189 | 185
2016-07-15 12:30 | 189 | 184
2016-07-15 13:00 | 186 | 180
2016-07-15 13:30 | 177 | 172
2016-07-15 14:00 | 176 | 170
2016-07-15 14:30 | 179 | 174
2016-07-15 15:00 | 181 | 175
2016-07-15 15:30 | 163 | 157
2016-07-15 16:00 | 164 | 159
2016-07-15 16:30 | 168 | 162
2016-07-15 17:00 | 118 | 111
2016-07-15 17:30 | 110 | 102
2016-07-15 18:00 | 91 | 79
2016-07-15 18:30 | 105 | 98
2016-07-15 19:00 | 112 | 104
2016-07-15 19:30 | 99 | 91
2016-07-15 20:00 | 114 | 109
2016-07-15 20:30 | 114 | 108
2016-07-15 21:00 | 122 | 117
2016-07-15 21:30 | 130 | 125
2016-07-15 22:00 | 151 | 147
2016-07-15 22:30 | 111 | 108
2016-07-15 23:00 | 133 | 130
2016-07-15 23:30 | 169 | 166
2016-07-16 | 207 | 205
2016-07-16 00:30 | 200 | 197
2016-07-16 01:00 | 187 | 184
2016-07-16 01:30 | 175 | 171
2016-07-16 02:00 | 166 | 162
2016-07-16 02:30 | 161 | 157
2016-07-16 03:00 | 157 | 153
2016-07-16 03:30 | 152 | 148
2016-07-16 04:00 | 152 | 148
2016-07-16 04:30 | 155 | 151
2016-07-16 05:00 | 156 | 152
2016-07-16 05:30 | 159 | 155
2016-07-16 06:00 | 166 | 162
2016-07-16 06:30 | 172 | 169
2016-07-16 07:00 | 179 | 176
2016-07-16 07:30 | 189 | 186
2016-07-16 08:00 | 205 | 201
2016-07-16 08:30 | 217 | 213
2016-07-16 09:00 | 218 | 215
2016-07-16 09:30 | 207 | 203
2016-07-16 10:00 | 215 | 211
2016-07-16 10:30 | 217 | 212
2016-07-16 11:00 | 234 | 230
2016-07-16 11:30 | 229 | 225
2016-07-16 12:00 | 225 | 220
2016-07-16 12:30 | 219 | 214
2016-07-16 13:00 | 216 | 211
2016-07-16 13:30 | 214 | 208
2016-07-16 14:00 | 206 | 200
2016-07-16 14:30 | 181 | 175
2016-07-16 15:00 | 180 | 173
2016-07-16 15:30 | 181 | 174
2016-07-16 16:00 | 187 | 181
2016-07-16 16:30 | 194 | 188
2016-07-16 17:00 | 204 | 198
2016-07-16 17:30 | 211 | 206
2016-07-16 18:00 | 222 | 217
2016-07-16 18:30 | 234 | 230
2016-07-16 19:00 | 238 | 234
2016-07-16 19:30 | 229 | 225
2016-07-16 20:00 | 222 | 219
2016-07-16 20:30 | 214 | 211
2016-07-16 21:00 | 209 | 206
2016-07-16 21:30 | 202 | 198
2016-07-16 22:00 | 198 | 194
2016-07-16 22:30 | 203 | 199
2016-07-16 23:00 | 198 | 194
2016-07-16 23:30 | 190 | 186
2016-07-17 | 189 | 185
2016-07-17 00:30 | 184 | 180
2016-07-17 01:00 | 176 | 172
2016-07-17 01:30 | 167 | 163
2016-07-17 02:00 | 159 | 155
2016-07-17 02:30 | 153 | 149
2016-07-17 03:00 | 148 | 143
2016-07-17 03:30 | 148 | 143
2016-07-17 04:00 | 144 | 140
2016-07-17 04:30 | 145 | 141
2016-07-17 05:00 | 146 | 141
2016-07-17 05:30 | 147 | 143
2016-07-17 06:00 | 150 | 145
2016-07-17 06:30 | 156 | 152
2016-07-17 07:00 | 159 | 155
2016-07-17 07:30 | 165 | 162
2016-07-17 08:00 | 177 | 173
2016-07-17 08:30 | 186 | 182
2016-07-17 09:00 | 188 | 184
2016-07-17 09:30 | 193 | 189
2016-07-17 10:00 | 180 | 175
2016-07-17 10:30 | 182 | 178
2016-07-17 11:00 | 183 | 179
2016-07-17 11:30 | 186 | 182
2016-07-17 12:00 | 177 | 172
2016-07-17 12:30 | 168 | 162
2016-07-17 13:00 | 170 | 164
2016-07-17 13:30 | 161 | 155
2016-07-17 14:00 | 153 | 146
2016-07-17 14:30 | 161 | 155
2016-07-17 15:00 | 168 | 162
2016-07-17 15:30 | 168 | 160
2016-07-17 16:00 | 182 | 174
2016-07-17 16:30 | 189 | 180
2016-07-17 17:00 | 196 | 188
2016-07-17 17:30 | 205 | 198
2016-07-17 18:00 | 224 | 218
2016-07-17 18:30 | 236 | 229
2016-07-17 19:00 | 244 | 237
2016-07-17 19:30 | 235 | 229
2016-07-17 20:00 | 231 | 225
2016-07-17 20:30 | 226 | 220
2016-07-17 21:00 | 217 | 211
2016-07-17 21:30 | 208 | 201
2016-07-17 22:00 | 199 | 195
2016-07-17 22:30 | 208 | 204
2016-07-17 23:00 | 204 | 200
2016-07-17 23:30 | 197 | 194
2016-07-18 | 194 | 190
2016-07-18 00:30 | 188 | 184
2016-07-18 01:00 | 182 | 178
2016-07-18 01:30 | 173 | 169
2016-07-18 02:00 | 166 | 162
2016-07-18 02:30 | 162 | 158
2016-07-18 03:00 | 158 | 154
2016-07-18 03:30 | 157 | 154
2016-07-18 04:00 | 157 | 154
2016-07-18 04:30 | 154 | 151
2016-07-18 05:00 | 133 | 129
2016-07-18 05:30 | 135 | 131
2016-07-18 06:00 | 146 | 142
2016-07-18 06:30 | 165 | 161
2016-07-18 07:00 | 179 | 176
2016-07-18 07:30 | 201 | 197
2016-07-18 08:00 | 209 | 204
2016-07-18 08:30 | 184 | 179
2016-07-18 09:00 | 187 | 183
2016-07-18 09:30 | 186 | 183
2016-07-18 10:00 | 179 | 176
2016-07-18 10:30 | 178 | 174
2016-07-18 11:00 | 177 | 173
2016-07-18 11:30 | 178 | 172
2016-07-18 12:00 | 174 | 167
2016-07-18 12:30 | 172 | 166
2016-07-18 13:00 | 165 | 159
2016-07-18 13:30 | 164 | 157
2016-07-18 14:00 | 162 | 156
2016-07-18 14:30 | 162 | 155
2016-07-18 15:00 | 154 | 147
2016-07-18 15:30 | 150 | 143
2016-07-18 16:00 | 151 | 144
2016-07-18 16:30 | 154 | 148
2016-07-18 17:00 | 111 | 104
2016-07-18 17:30 | 96 | 88
2016-07-18 18:00 | 98 | 90
2016-07-18 18:30 | 104 | 97
2016-07-18 19:00 | 107 | 100
2016-07-18 19:30 | 98 | 90
2016-07-18 20:00 | 95 | 88
2016-07-18 20:30 | 94 | 86
2016-07-18 21:00 | 90 | 81
2016-07-18 21:30 | 83 | 72
2016-07-18 22:00 | 109 | 103
2016-07-18 22:30 | 140 | 138
2016-07-18 23:00 | 138 | 136
2016-07-18 23:30 | 133 | 131
2016-07-19 | 126 | 124
2016-07-19 00:30 | 91 | 88
2016-07-19 01:00 | 82 | 79
2016-07-19 01:30 | 72 | 68
2016-07-19 02:00 | 64 | 60
2016-07-19 02:30 | 59 | 55
2016-07-19 03:00 | 59 | 55
2016-07-19 03:30 | 56 | 51
2016-07-19 04:00 | 59 | 55
2016-07-19 04:30 | 71 | 68
2016-07-19 05:00 | 73 | 70
2016-07-19 05:30 | 82 | 79
2016-07-19 06:00 | 81 | 78
2016-07-19 06:30 | 96 | 91
2016-07-19 07:00 | 106 | 101
2016-07-19 07:30 | 118 | 115
2016-07-19 08:00 | 145 | 141
2016-07-19 08:30 | 154 | 152
2016-07-19 09:00 | 148 | 146
2016-07-19 09:30 | 150 | 148
2016-07-19 10:00 | 145 | 143
2016-07-19 10:30 | 145 | 143
2016-07-19 11:00 | 144 | 142
2016-07-19 11:30 | 148 | 146
2016-07-19 12:00 | 142 | 140
2016-07-19 12:30 | 142 | 140
2016-07-19 13:00 | 144 | 142
2016-07-19 13:30 | 141 | 139
2016-07-19 14:00 | 134 | 132
2016-07-19 14:30 | 134 | 132
2016-07-19 15:00 | 127 | 124
2016-07-19 15:30 | 126 | 123
2016-07-19 16:00 | 133 | 131
2016-07-19 16:30 | 136 | 133
2016-07-19 17:00 | 88 | 85
2016-07-19 17:30 | 72 | 69
2016-07-19 18:00 | 73 | 70
2016-07-19 18:30 | 77 | 74
2016-07-19 19:00 | 83 | 80
2016-07-19 19:30 | 94 | 92
2016-07-19 20:00 | 95 | 93
2016-07-19 20:30 | 89 | 87
2016-07-19 21:00 | 80 | 78
2016-07-19 21:30 | 105 | 102
2016-07-19 22:00 | 137 | 135
2016-07-19 22:30 | 155 | 153
2016-07-19 23:00 | 157 | 156
2016-07-19 23:30 | 152 | 150
2016-07-20 | 147 | 145
2016-07-20 00:30 | 136 | 134
2016-07-20 01:00 | 124 | 122
2016-07-20 01:30 | 102 | 99
2016-07-20 02:00 | 79 | 76
2016-07-20 02:30 | 82 | 79
2016-07-20 03:00 | 82 | 79
2016-07-20 03:30 | 91 | 89
2016-07-20 04:00 | 94 | 93
2016-07-20 04:30 | 88 | 87
2016-07-20 05:00 | 90 | 88
2016-07-20 05:30 | 98 | 97
2016-07-20 06:00 | 109 | 108
2016-07-20 06:30 | 132 | 131
2016-07-20 07:00 | 151 | 149
2016-07-20 07:30 | 155 | 153
2016-07-20 08:00 | 165 | 164
2016-07-20 08:30 | 191 | 190
2016-07-20 09:00 | 191 | 189
2016-07-20 09:30 | 190 | 189
2016-07-20 10:00 | 185 | 183
2016-07-20 10:30 | 182 | 181
2016-07-20 11:00 | 179 | 177
2016-07-20 11:30 | 179 | 178
2016-07-20 12:00 | 171 | 169
2016-07-20 12:30 | 168 | 167
2016-07-20 13:00 | 167 | 165
2016-07-20 13:30 | 165 | 164
2016-07-20 14:00 | 157 | 155
2016-07-20 14:30 | 158 | 156
2016-07-20 15:00 | 161 | 159
2016-07-20 15:30 | 160 | 158
2016-07-20 16:00 | 164 | 162
2016-07-20 16:30 | 160 | 158
2016-07-20 17:00 | 118 | 115
2016-07-20 17:30 | 109 | 106
2016-07-20 18:00 | 109 | 107
2016-07-20 18:30 | 112 | 110
2016-07-20 19:00 | 116 | 114
2016-07-20 19:30 | 99 | 96
2016-07-20 20:00 | 93 | 91
2016-07-20 20:30 | 89 | 87
2016-07-20 21:00 | 86 | 84
2016-07-20 21:30 | 122 | 121
2016-07-20 22:00 | 138 | 136
2016-07-20 22:30 | 116 | 114
2016-07-20 23:00 | 126 | 124
2016-07-20 23:30 | 148 | 147
2016-07-21 | 187 | 185
2016-07-21 00:30 | 175 | 173
2016-07-21 01:00 | 167 | 165
2016-07-21 01:30 | 168 | 166
2016-07-21 02:00 | 165 | 163
2016-07-21 02:30 | 161 | 159
2016-07-21 03:00 | 157 | 155
2016-07-21 03:30 | 153 | 151
2016-07-21 04:00 | 155 | 153
2016-07-21 04:30 | 156 | 154
2016-07-21 05:00 | 158 | 156
2016-07-21 05:30 | 167 | 165
2016-07-21 06:00 | 177 | 175
2016-07-21 06:30 | 197 | 195
2016-07-21 07:00 | 212 | 211
2016-07-21 07:30 | 222 | 221
2016-07-21 08:00 | 244 | 243
2016-07-21 08:30 | 254 | 253
2016-07-21 09:00 | 253 | 251
2016-07-21 09:30 | 251 | 250
2016-07-21 10:00 | 247 | 246
2016-07-21 10:30 | 246 | 245
2016-07-21 11:00 | 245 | 243
2016-07-21 11:30 | 248 | 246
2016-07-21 12:00 | 242 | 241
2016-07-21 12:30 | 240 | 239
2016-07-21 13:00 | 238 | 236
2016-07-21 13:30 | 237 | 235
2016-07-21 14:00 | 238 | 237
2016-07-21 14:30 | 242 | 241
2016-07-21 15:00 | 241 | 239
2016-07-21 15:30 | 237 | 236
2016-07-21 16:00 | 229 | 228
2016-07-21 16:30 | 230 | 228
2016-07-21 17:00 | 231 | 229
2016-07-21 17:30 | 226 | 224
2016-07-21 18:00 | 227 | 225
2016-07-21 18:30 | 232 | 230
2016-07-21 19:00 | 235 | 234
2016-07-21 19:30 | 225 | 223
2016-07-21 20:00 | 221 | 220
2016-07-21 20:30 | 218 | 216
2016-07-21 21:00 | 215 | 213
2016-07-21 21:30 | 203 | 201
2016-07-21 22:00 | 202 | 200
2016-07-21 22:30 | 208 | 206
2016-07-21 23:00 | 206 | 205
2016-07-21 23:30 | 201 | 200
2016-07-22 | 194 | 193
2016-07-22 00:30 | 181 | 179
2016-07-22 01:00 | 168 | 166
2016-07-22 01:30 | 170 | 167
2016-07-22 02:00 | 166 | 164
2016-07-22 02:30 | 160 | 158
2016-07-22 03:00 | 155 | 153
2016-07-22 03:30 | 152 | 150
2016-07-22 04:00 | 152 | 150
2016-07-22 04:30 | 152 | 150
2016-07-22 05:00 | 153 | 152
2016-07-22 05:30 | 160 | 158
2016-07-22 06:00 | 166 | 164
2016-07-22 06:30 | 182 | 181
2016-07-22 07:00 | 195 | 194
2016-07-22 07:30 | 212 | 211
2016-07-22 08:00 | 221 | 220
2016-07-22 08:30 | 221 | 219
2016-07-22 09:00 | 219 | 217
2016-07-22 09:30 | 217 | 216
2016-07-22 10:00 | 214 | 213
2016-07-22 10:30 | 210 | 209
2016-07-22 11:00 | 201 | 200
2016-07-22 11:30 | 200 | 199
2016-07-22 12:00 | 194 | 193
2016-07-22 12:30 | 191 | 190
2016-07-22 13:00 | 190 | 188
2016-07-22 13:30 | 190 | 188
2016-07-22 14:00 | 191 | 190
2016-07-22 14:30 | 193 | 192
2016-07-22 15:00 | 195 | 194
2016-07-22 15:30 | 198 | 197
2016-07-22 16:00 | 206 | 205
2016-07-22 16:30 | 211 | 210
2016-07-22 17:00 | 217 | 216
2016-07-22 17:30 | 209 | 208
2016-07-22 18:00 | 207 | 206
2016-07-22 18:30 | 208 | 207
2016-07-22 19:00 | 212 | 211
2016-07-22 19:30 | 203 | 202
2016-07-22 20:00 | 201 | 200
2016-07-22 20:30 | 198 | 197
2016-07-22 21:00 | 194 | 193
2016-07-22 21:30 | 185 | 184
2016-07-22 22:00 | 188 | 187
2016-07-22 22:30 | 204 | 202
2016-07-22 23:00 | 207 | 206
2016-07-22 23:30 | 203 | 201
2016-07-23 | 197 | 195
2016-07-23 00:30 | 198 | 197
2016-07-23 01:00 | 191 | 189
2016-07-23 01:30 | 180 | 178
2016-07-23 02:00 | 171 | 170
2016-07-23 02:30 | 163 | 161
2016-07-23 03:00 | 160 | 157
2016-07-23 03:30 | 158 | 156
2016-07-23 04:00 | 156 | 154
2016-07-23 04:30 | 149 | 147
2016-07-23 05:00 | 151 | 150
2016-07-23 05:30 | 153 | 152
2016-07-23 06:00 | 157 | 156
2016-07-23 06:30 | 165 | 163
2016-07-23 07:00 | 170 | 168
2016-07-23 07:30 | 178 | 177
2016-07-23 08:00 | 177 | 175
2016-07-23 08:30 | 179 | 178
2016-07-23 09:00 | 180 | 179
2016-07-23 09:30 | 181 | 180
2016-07-23 10:00 | 181 | 180
2016-07-23 10:30 | 179 | 178
2016-07-23 11:00 | 177 | 176
2016-07-23 11:30 | 187 | 186
2016-07-23 12:00 | 192 | 191
2016-07-23 12:30 | 189 | 188
2016-07-23 13:00 | 189 | 188
2016-07-23 13:30 | 189 | 188
2016-07-23 14:00 | 190 | 188
2016-07-23 14:30 | 191 | 189
2016-07-23 15:00 | 193 | 192
2016-07-23 15:30 | 196 | 195
2016-07-23 16:00 | 195 | 194
2016-07-23 16:30 | 193 | 192
2016-07-23 17:00 | 194 | 193
2016-07-23 17:30 | 202 | 201
2016-07-23 18:00 | 206 | 205
2016-07-23 18:30 | 214 | 213
2016-07-23 19:00 | 221 | 220
2016-07-23 19:30 | 213 | 212
2016-07-23 20:00 | 208 | 207
2016-07-23 20:30 | 202 | 200
2016-07-23 21:00 | 196 | 195
2016-07-23 21:30 | 188 | 187
2016-07-23 22:00 | 188 | 186
2016-07-23 22:30 | 189 | 188
2016-07-23 23:00 | 201 | 200
2016-07-23 23:30 | 197 | 195
2016-07-24 | 192 | 191
2016-07-24 00:30 | 184 | 182
2016-07-24 01:00 | 176 | 175
2016-07-24 01:30 | 166 | 164
2016-07-24 02:00 | 170 | 168
2016-07-24 02:30 | 179 | 177
2016-07-24 03:00 | 175 | 174
2016-07-24 03:30 | 174 | 173
2016-07-24 04:00 | 173 | 171
2016-07-24 04:30 | 173 | 171
2016-07-24 05:00 | 164 | 162
2016-07-24 05:30 | 152 | 150
2016-07-24 06:00 | 153 | 151
2016-07-24 06:30 | 155 | 154
2016-07-24 07:00 | 159 | 158
2016-07-24 07:30 | 168 | 166
2016-07-24 08:00 | 173 | 172
2016-07-24 08:30 | 173 | 172
2016-07-24 09:00 | 174 | 173
2016-07-24 09:30 | 177 | 176
2016-07-24 10:00 | 176 | 174
2016-07-24 10:30 | 179 | 177
2016-07-24 11:00 | 177 | 176
2016-07-24 11:30 | 177 | 176
2016-07-24 12:00 | 178 | 177
2016-07-24 12:30 | 175 | 174
2016-07-24 13:00 | 175 | 174
2016-07-24 13:30 | 174 | 173
2016-07-24 14:00 | 177 | 175
2016-07-24 14:30 | 179 | 178
2016-07-24 15:00 | 182 | 180
2016-07-24 15:30 | 181 | 180
2016-07-24 16:00 | 187 | 186
2016-07-24 16:30 | 197 | 196
2016-07-24 17:00 | 202 | 201
2016-07-24 17:30 | 204 | 203
2016-07-24 18:00 | 210 | 209
2016-07-24 18:30 | 224 | 222
2016-07-24 19:00 | 232 | 231
2016-07-24 19:30 | 224 | 223
2016-07-24 20:00 | 218 | 216
2016-07-24 20:30 | 209 | 207
2016-07-24 21:00 | 202 | 200
2016-07-24 21:30 | 190 | 188
2016-07-24 22:00 | 184 | 183
2016-07-24 22:30 | 193 | 192
2016-07-24 23:00 | 190 | 189
2016-07-24 23:30 | 195 | 194
2016-07-25 | 192 | 191
2016-07-25 00:30 | 183 | 182
2016-07-25 01:00 | 177 | 175
2016-07-25 01:30 | 181 | 179
2016-07-25 02:00 | 174 | 172
2016-07-25 02:30 | 170 | 168
2016-07-25 03:00 | 168 | 167
2016-07-25 03:30 | 167 | 165
2016-07-25 04:00 | 155 | 153
2016-07-25 04:30 | 152 | 150
2016-07-25 05:00 | 151 | 149
2016-07-25 05:30 | 155 | 154
2016-07-25 06:00 | 164 | 163
2016-07-25 06:30 | 185 | 184
2016-07-25 07:00 | 202 | 201
2016-07-25 07:30 | 218 | 216
2016-07-25 08:00 | 227 | 225
2016-07-25 08:30 | 228 | 227
2016-07-25 09:00 | 222 | 220
2016-07-25 09:30 | 218 | 217
2016-07-25 10:00 | 215 | 214
2016-07-25 10:30 | 212 | 211
2016-07-25 11:00 | 211 | 209
2016-07-25 11:30 | 209 | 208
2016-07-25 12:00 | 212 | 211
2016-07-25 12:30 | 215 | 214
2016-07-25 13:00 | 212 | 211
2016-07-25 13:30 | 210 | 209
2016-07-25 14:00 | 206 | 204
2016-07-25 14:30 | 208 | 207
2016-07-25 15:00 | 212 | 210
2016-07-25 15:30 | 216 | 214
2016-07-25 16:00 | 222 | 220
2016-07-25 16:30 | 228 | 226
2016-07-25 17:00 | 224 | 222
2016-07-25 17:30 | 221 | 219
2016-07-25 18:00 | 213 | 211
2016-07-25 18:30 | 220 | 218
2016-07-25 19:00 | 224 | 222
2016-07-25 19:30 | 214 | 212
2016-07-25 20:00 | 210 | 208
2016-07-25 20:30 | 207 | 205
2016-07-25 21:00 | 215 | 213
2016-07-25 21:30 | 224 | 222
2016-07-25 22:00 | 228 | 226
2016-07-25 22:30 | 221 | 219
2016-07-25 23:00 | 213 | 211
2016-07-25 23:30 | 207 | 205
2016-07-26 | 202 | 200
2016-07-26 00:30 | 186 | 184
2016-07-26 01:00 | 174 | 171
2016-07-26 01:30 | 162 | 159
2016-07-26 02:00 | 152 | 149
2016-07-26 02:30 | 147 | 144
2016-07-26 03:00 | 147 | 145
2016-07-26 03:30 | 144 | 143
2016-07-26 04:00 | 145 | 143
2016-07-26 04:30 | 145 | 144
2016-07-26 05:00 | 146 | 144
2016-07-26 05:30 | 152 | 151
2016-07-26 06:00 | 161 | 160
2016-07-26 06:30 | 181 | 180
2016-07-26 07:00 | 198 | 197
2016-07-26 07:30 | 215 | 214
2016-07-26 08:00 | 224 | 222
2016-07-26 08:30 | 227 | 226
2016-07-26 09:00 | 220 | 219
2016-07-26 09:30 | 217 | 215
2016-07-26 10:00 | 216 | 214
2016-07-26 10:30 | 215 | 214
2016-07-26 11:00 | 211 | 210
2016-07-26 11:30 | 211 | 210
2016-07-26 12:00 | 213 | 211
2016-07-26 12:30 | 214 | 212
2016-07-26 13:00 | 202 | 200
2016-07-26 13:30 | 201 | 199
2016-07-26 14:00 | 199 | 197
2016-07-26 14:30 | 193 | 191
2016-07-26 15:00 | 195 | 193
2016-07-26 15:30 | 195 | 193
2016-07-26 16:00 | 201 | 199
2016-07-26 16:30 | 207 | 205
2016-07-26 17:00 | 211 | 209
2016-07-26 17:30 | 213 | 211
2016-07-26 18:00 | 215 | 213
2016-07-26 18:30 | 221 | 219
2016-07-26 19:00 | 228 | 226
2016-07-26 19:30 | 220 | 218
2016-07-26 20:00 | 215 | 213
2016-07-26 20:30 | 211 | 210
2016-07-26 21:00 | 207 | 205
2016-07-26 21:30 | 207 | 205
2016-07-26 22:00 | 208 | 207
2016-07-26 22:30 | 227 | 226
2016-07-26 23:00 | 238 | 237
2016-07-26 23:30 | 233 | 232
2016-07-27 | 227 | 226
2016-07-27 00:30 | 216 | 215
2016-07-27 01:00 | 205 | 203
2016-07-27 01:30 | 194 | 192
2016-07-27 02:00 | 185 | 183
2016-07-27 02:30 | 181 | 179
2016-07-27 03:00 | 179 | 176
2016-07-27 03:30 | 175 | 174
2016-07-27 04:00 | 174 | 173
2016-07-27 04:30 | 176 | 174
2016-07-27 05:00 | 177 | 175
2016-07-27 05:30 | 174 | 173
2016-07-27 06:00 | 171 | 170
2016-07-27 06:30 | 188 | 187
2016-07-27 07:00 | 212 | 211
2016-07-27 07:30 | 228 | 227
2016-07-27 08:00 | 238 | 237
2016-07-27 08:30 | 242 | 241
2016-07-27 09:00 | 239 | 238
2016-07-27 09:30 | 230 | 229
2016-07-27 10:00 | 228 | 226
2016-07-27 10:30 | 226 | 225
2016-07-27 11:00 | 223 | 222
2016-07-27 11:30 | 228 | 226
2016-07-27 12:00 | 228 | 227
2016-07-27 12:30 | 218 | 217
2016-07-27 13:00 | 185 | 183
2016-07-27 13:30 | 179 | 178
2016-07-27 14:00 | 184 | 182
2016-07-27 14:30 | 185 | 184
2016-07-27 15:00 | 181 | 179
2016-07-27 15:30 | 182 | 181
2016-07-27 16:00 | 185 | 184
2016-07-27 16:30 | 169 | 168
2016-07-27 17:00 | 128 | 126
2016-07-27 17:30 | 93 | 90
2016-07-27 18:00 | 90 | 88
2016-07-27 18:30 | 94 | 92
2016-07-27 19:00 | 102 | 99
2016-07-27 19:30 | 92 | 90
2016-07-27 20:00 | 87 | 84
2016-07-27 20:30 | 83 | 81
2016-07-27 21:00 | 79 | 77
2016-07-27 21:30 | 88 | 87
2016-07-27 22:00 | 123 | 122
2016-07-27 22:30 | 144 | 143
2016-07-27 23:00 | 141 | 140
2016-07-27 23:30 | 134 | 133
2016-07-28 | 129 | 128
2016-07-28 00:30 | 115 | 113
2016-07-28 01:00 | 104 | 103
2016-07-28 01:30 | 92 | 91
2016-07-28 02:00 | 85 | 84
2016-07-28 02:30 | 80 | 78
2016-07-28 03:00 | 77 | 76
2016-07-28 03:30 | 75 | 73
2016-07-28 04:00 | 74 | 72
2016-07-28 04:30 | 76 | 75
2016-07-28 05:00 | 82 | 80
2016-07-28 05:30 | 88 | 87
2016-07-28 06:00 | 97 | 95
2016-07-28 06:30 | 119 | 118
2016-07-28 07:00 | 133 | 132
2016-07-28 07:30 | 143 | 143
2016-07-28 08:00 | 156 | 155
2016-07-28 08:30 | 157 | 156
2016-07-28 09:00 | 151 | 150
2016-07-28 09:30 | 146 | 145
2016-07-28 10:00 | 139 | 138
2016-07-28 10:30 | 135 | 134
2016-07-28 11:00 | 131 | 130
2016-07-28 11:30 | 131 | 130
2016-07-28 12:00 | 126 | 125
2016-07-28 12:30 | 125 | 123
2016-07-28 13:00 | 124 | 123
2016-07-28 13:30 | 125 | 123
2016-07-28 14:00 | 125 | 124
2016-07-28 14:30 | 120 | 119
2016-07-28 15:00 | 119 | 118
2016-07-28 15:30 | 121 | 120
2016-07-28 16:00 | 128 | 126
2016-07-28 16:30 | 134 | 133
2016-07-28 17:00 | 137 | 136
2016-07-28 17:30 | 94 | 92
2016-07-28 18:00 | 72 | 70
2016-07-28 18:30 | 74 | 73
2016-07-28 19:00 | 83 | 82
2016-07-28 19:30 | 75 | 73
2016-07-28 20:00 | 77 | 76
2016-07-28 20:30 | 90 | 89
2016-07-28 21:00 | 88 | 87
2016-07-28 21:30 | 88 | 87
2016-07-28 22:00 | 92 | 90
2016-07-28 22:30 | 128 | 127
2016-07-28 23:00 | 124 | 123
2016-07-28 23:30 | 129 | 128
2016-07-29 | 123 | 122
2016-07-29 00:30 | 112 | 111
2016-07-29 01:00 | 102 | 101
2016-07-29 01:30 | 88 | 86
2016-07-29 02:00 | 77 | 75
2016-07-29 02:30 | 71 | 69
2016-07-29 03:00 | 69 | 67
2016-07-29 03:30 | 70 | 67
2016-07-29 04:00 | 68 | 65
2016-07-29 04:30 | 67 | 65
2016-07-29 05:00 | 72 | 70
2016-07-29 05:30 | 77 | 76
2016-07-29 06:00 | 87 | 86
2016-07-29 06:30 | 107 | 106
2016-07-29 07:00 | 127 | 126
2016-07-29 07:30 | 140 | 139
2016-07-29 08:00 | 133 | 132
2016-07-29 08:30 | 147 | 146
2016-07-29 09:00 | 144 | 143
2016-07-29 09:30 | 140 | 139
2016-07-29 10:00 | 133 | 132
2016-07-29 10:30 | 130 | 129
2016-07-29 11:00 | 126 | 125
2016-07-29 11:30 | 123 | 122
2016-07-29 12:00 | 121 | 120
2016-07-29 12:30 | 120 | 119
2016-07-29 13:00 | 119 | 118
2016-07-29 13:30 | 120 | 119
2016-07-29 14:00 | 120 | 119
2016-07-29 14:30 | 113 | 111
2016-07-29 15:00 | 111 | 110
2016-07-29 15:30 | 114 | 112
2016-07-29 16:00 | 121 | 120
2016-07-29 16:30 | 128 | 127
2016-07-29 17:00 | 133 | 132
2016-07-29 17:30 | 91 | 90
2016-07-29 18:00 | 57 | 55
2016-07-29 18:30 | 68 | 66
2016-07-29 19:00 | 78 | 76
2016-07-29 19:30 | 70 | 68
2016-07-29 20:00 | 67 | 65
2016-07-29 20:30 | 81 | 79
2016-07-29 21:00 | 114 | 113
2016-07-29 21:30 | 137 | 136
2016-07-29 22:00 | 140 | 140
2016-07-29 22:30 | 132 | 131
2016-07-29 23:00 | 131 | 130
2016-07-29 23:30 | 153 | 153
2016-07-30 | 193 | 192
2016-07-30 00:30 | 178 | 177
2016-07-30 01:00 | 168 | 167
2016-07-30 01:30 | 157 | 157
2016-07-30 02:00 | 148 | 148
2016-07-30 02:30 | 141 | 140
2016-07-30 03:00 | 142 | 141
2016-07-30 03:30 | 139 | 138
2016-07-30 04:00 | 139 | 138
2016-07-30 04:30 | 137 | 136
2016-07-30 05:00 | 140 | 139
2016-07-30 05:30 | 144 | 143
2016-07-30 06:00 | 145 | 144
2016-07-30 06:30 | 153 | 152
2016-07-30 07:00 | 160 | 160
2016-07-30 07:30 | 172 | 171
2016-07-30 08:00 | 184 | 184
2016-07-30 08:30 | 190 | 189
2016-07-30 09:00 | 188 | 187
2016-07-30 09:30 | 195 | 194
2016-07-30 10:00 | 190 | 189
2016-07-30 10:30 | 189 | 188
2016-07-30 11:00 | 189 | 188
2016-07-30 11:30 | 186 | 185
2016-07-30 12:00 | 180 | 179
2016-07-30 12:30 | 178 | 177
2016-07-30 13:00 | 172 | 171
2016-07-30 13:30 | 172 | 171
2016-07-30 14:00 | 171 | 170
2016-07-30 14:30 | 162 | 161
2016-07-30 15:00 | 160 | 158
2016-07-30 15:30 | 164 | 162
2016-07-30 16:00 | 171 | 169
2016-07-30 16:30 | 180 | 179
2016-07-30 17:00 | 190 | 189
2016-07-30 17:30 | 198 | 197
2016-07-30 18:00 | 190 | 188
2016-07-30 18:30 | 194 | 193
2016-07-30 19:00 | 200 | 199
2016-07-30 19:30 | 205 | 204
2016-07-30 20:00 | 204 | 203
2016-07-30 20:30 | 209 | 209
2016-07-30 21:00 | 209 | 208
2016-07-30 21:30 | 198 | 197
2016-07-30 22:00 | 196 | 195
2016-07-30 22:30 | 189 | 188
2016-07-30 23:00 | 186 | 185
2016-07-30 23:30 | 182 | 181
2016-07-31 | 180 | 179
2016-07-31 00:30 | 169 | 168
2016-07-31 01:00 | 163 | 162
2016-07-31 01:30 | 155 | 153
2016-07-31 02:00 | 150 | 148
2016-07-31 02:30 | 146 | 144
2016-07-31 03:00 | 144 | 142
2016-07-31 03:30 | 140 | 139
2016-07-31 04:00 | 132 | 130
2016-07-31 04:30 | 134 | 133
2016-07-31 05:00 | 135 | 134
2016-07-31 05:30 | 138 | 137
2016-07-31 06:00 | 142 | 141
2016-07-31 06:30 | 150 | 149
2016-07-31 07:00 | 158 | 157
2016-07-31 07:30 | 164 | 162
2016-07-31 08:00 | 173 | 172
2016-07-31 08:30 | 182 | 181
2016-07-31 09:00 | 182 | 180
2016-07-31 09:30 | 185 | 183
2016-07-31 10:00 | 186 | 184
2016-07-31 10:30 | 186 | 185
2016-07-31 11:00 | 186 | 184
2016-07-31 11:30 | 182 | 181
2016-07-31 12:00 | 180 | 178
2016-07-31 12:30 | 178 | 177
2016-07-31 13:00 | 177 | 175
2016-07-31 13:30 | 177 | 175
2016-07-31 14:00 | 174 | 172
2016-07-31 14:30 | 168 | 166
2016-07-31 15:00 | 164 | 162
2016-07-31 15:30 | 169 | 168
2016-07-31 16:00 | 174 | 173
2016-07-31 16:30 | 179 | 178
2016-07-31 17:00 | 187 | 186
2016-07-31 17:30 | 192 | 190
2016-07-31 18:00 | 181 | 180
2016-07-31 18:30 | 192 | 191
2016-07-31 19:00 | 193 | 192
2016-07-31 19:30 | 184 | 182
2016-07-31 20:00 | 188 | 187
2016-07-31 20:30 | 202 | 201
2016-07-31 21:00 | 217 | 216
2016-07-31 21:30 | 211 | 211
2016-07-31 22:00 | 205 | 205
2016-07-31 22:30 | 192 | 191
2016-07-31 23:00 | 185 | 184
2016-07-31 23:30 | 181 | 179
2016-08-01 | 178 | 177
2016-08-01 00:30 | 171 | 170
2016-08-01 01:00 | 166 | 165
2016-08-01 01:30 | 156 | 155
2016-08-01 02:00 | 148 | 146
2016-08-01 02:30 | 144 | 142
2016-08-01 03:00 | 141 | 139
2016-08-01 03:30 | 141 | 139
2016-08-01 04:00 | 140 | 138
2016-08-01 04:30 | 138 | 137
2016-08-01 05:00 | 138 | 136
2016-08-01 05:30 | 145 | 144
2016-08-01 06:00 | 155 | 154
2016-08-01 06:30 | 172 | 171
2016-08-01 07:00 | 177 | 176
2016-08-01 07:30 | 194 | 193
2016-08-01 08:00 | 206 | 206
2016-08-01 08:30 | 216 | 215
2016-08-01 09:00 | 223 | 222
2016-08-01 09:30 | 225 | 223
2016-08-01 10:00 | 220 | 218
2016-08-01 10:30 | 219 | 217
2016-08-01 11:00 | 215 | 213
2016-08-01 11:30 | 219 | 218
2016-08-01 12:00 | 221 | 220
2016-08-01 12:30 | 225 | 221
2016-08-01 13:00 | 228 | 222
2016-08-01 13:30 | 227 | 221
2016-08-01 14:00 | 225 | 220
2016-08-01 14:30 | 215 | 210
2016-08-01 15:00 | 213 | 207
2016-08-01 15:30 | 211 | 206
2016-08-01 16:00 | 210 | 207
2016-08-01 16:30 | 211 | 207
2016-08-01 17:00 | 215 | 211
2016-08-01 17:30 | 203 | 199
2016-08-01 18:00 | 194 | 189
2016-08-01 18:30 | 200 | 195
2016-08-01 19:00 | 207 | 202
2016-08-01 19:30 | 218 | 214
2016-08-01 20:00 | 220 | 217
2016-08-01 20:30 | 236 | 232
2016-08-01 21:00 | 236 | 232
2016-08-01 21:30 | 225 | 221
2016-08-01 22:00 | 229 | 225
2016-08-01 22:30 | 223 | 219
2016-08-01 23:00 | 212 | 208
2016-08-01 23:30 | 205 | 201
2016-08-02 | 197 | 193
2016-08-02 00:30 | 186 | 182
2016-08-02 01:00 | 176 | 171
2016-08-02 01:30 | 164 | 160
2016-08-02 02:00 | 160 | 157
2016-08-02 02:30 | 158 | 155
2016-08-02 03:00 | 157 | 153
2016-08-02 03:30 | 154 | 150
2016-08-02 04:00 | 153 | 149
2016-08-02 04:30 | 152 | 148
2016-08-02 05:00 | 152 | 149
2016-08-02 05:30 | 160 | 157
2016-08-02 06:00 | 174 | 170
2016-08-02 06:30 | 194 | 191
2016-08-02 07:00 | 203 | 199
2016-08-02 07:30 | 209 | 204
2016-08-02 08:00 | 216 | 213
2016-08-02 08:30 | 216 | 212
2016-08-02 09:00 | 219 | 216
2016-08-02 09:30 | 223 | 220
2016-08-02 10:00 | 215 | 212
2016-08-02 10:30 | 216 | 213
2016-08-02 11:00 | 220 | 217
2016-08-02 11:30 | 225 | 222
2016-08-02 12:00 | 223 | 219
2016-08-02 12:30 | 224 | 220
2016-08-02 13:00 | 223 | 220
2016-08-02 13:30 | 225 | 221
2016-08-02 14:00 | 226 | 222
2016-08-02 14:30 | 221 | 217
2016-08-02 15:00 | 217 | 213
2016-08-02 15:30 | 219 | 215
2016-08-02 16:00 | 226 | 222
2016-08-02 16:30 | 227 | 223
2016-08-02 17:00 | 234 | 230
2016-08-02 17:30 | 221 | 216
2016-08-02 18:00 | 211 | 206
2016-08-02 18:30 | 214 | 208
2016-08-02 19:00 | 220 | 215
2016-08-02 19:30 | 213 | 208
2016-08-02 20:00 | 206 | 201
2016-08-02 20:30 | 197 | 192
2016-08-02 21:00 | 192 | 188
2016-08-02 21:30 | 214 | 210
2016-08-02 22:00 | 229 | 226
2016-08-02 22:30 | 224 | 221
2016-08-02 23:00 | 219 | 216
2016-08-02 23:30 | 212 | 209
2016-08-03 | 208 | 204
2016-08-03 00:30 | 193 | 189
2016-08-03 01:00 | 180 | 176
2016-08-03 01:30 | 163 | 160
2016-08-03 02:00 | 156 | 153
2016-08-03 02:30 | 151 | 148
2016-08-03 03:00 | 148 | 145
2016-08-03 03:30 | 149 | 146
2016-08-03 04:00 | 148 | 145
2016-08-03 04:30 | 141 | 138
2016-08-03 05:00 | 122 | 119
2016-08-03 05:30 | 124 | 120
2016-08-03 06:00 | 133 | 130
2016-08-03 06:30 | 149 | 146
2016-08-03 07:00 | 157 | 154
2016-08-03 07:30 | 170 | 167
2016-08-03 08:00 | 178 | 175
2016-08-03 08:30 | 171 | 168
2016-08-03 09:00 | 146 | 142
2016-08-03 09:30 | 141 | 137
2016-08-03 10:00 | 132 | 128
2016-08-03 10:30 | 130 | 126
2016-08-03 11:00 | 131 | 127
2016-08-03 11:30 | 124 | 121
2016-08-03 12:00 | 120 | 116
2016-08-03 12:30 | 119 | 116
2016-08-03 13:00 | 118 | 115
2016-08-03 13:30 | 119 | 116
2016-08-03 14:00 | 120 | 116
2016-08-03 14:30 | 113 | 110
2016-08-03 15:00 | 113 | 109
2016-08-03 15:30 | 117 | 113
2016-08-03 16:00 | 116 | 112
2016-08-03 16:30 | 123 | 119
2016-08-03 17:00 | 80 | 73
2016-08-03 17:30 | 71 | 62
2016-08-03 18:00 | 56 | 50
2016-08-03 18:30 | 65 | 57
2016-08-03 19:00 | 71 | 63
2016-08-03 19:30 | 63 | 56
2016-08-03 20:00 | 51 | 47
2016-08-03 20:30 | 48 | 45
2016-08-03 21:00 | 56 | 51
2016-08-03 21:30 | 58 | 54
2016-08-03 22:00 | 68 | 64
2016-08-03 22:30 | 81 | 78
2016-08-03 23:00 | 86 | 83
2016-08-03 23:30 | 120 | 118
2016-08-04 | 129 | 127
2016-08-04 00:30 | 118 | 116
2016-08-04 01:00 | 105 | 102
2016-08-04 01:30 | 93 | 90
2016-08-04 02:00 | 81 | 79
2016-08-04 02:30 | 80 | 77
2016-08-04 03:00 | 76 | 72
2016-08-04 03:30 | 77 | 74
2016-08-04 04:00 | 77 | 74
2016-08-04 04:30 | 79 | 76
2016-08-04 05:00 | 80 | 77
2016-08-04 05:30 | 82 | 79
2016-08-04 06:00 | 94 | 91
2016-08-04 06:30 | 118 | 116
2016-08-04 07:00 | 105 | 102
2016-08-04 07:30 | 95 | 93
2016-08-04 08:00 | 89 | 86
2016-08-04 08:30 | 91 | 88
2016-08-04 09:00 | 117 | 115
2016-08-04 09:30 | 135 | 133
2016-08-04 10:00 | 134 | 133
2016-08-04 10:30 | 123 | 121
2016-08-04 11:00 | 114 | 112
2016-08-04 11:30 | 109 | 107
2016-08-04 12:00 | 111 | 109
2016-08-04 12:30 | 109 | 107
2016-08-04 13:00 | 108 | 106
2016-08-04 13:30 | 108 | 106
2016-08-04 14:00 | 112 | 110
2016-08-04 14:30 | 104 | 102
2016-08-04 15:00 | 104 | 102
2016-08-04 15:30 | 108 | 106
2016-08-04 16:00 | 118 | 116
2016-08-04 16:30 | 119 | 117
2016-08-04 17:00 | 82 | 80
2016-08-04 17:30 | 79 | 77
2016-08-04 18:00 | 63 | 60
2016-08-04 18:30 | 74 | 71
2016-08-04 19:00 | 81 | 79
2016-08-04 19:30 | 88 | 85
2016-08-04 20:00 | 88 | 85
2016-08-04 20:30 | 92 | 90
2016-08-04 21:00 | 92 | 89
2016-08-04 21:30 | 123 | 121
2016-08-04 22:00 | 140 | 138
2016-08-04 22:30 | 139 | 137
2016-08-04 23:00 | 137 | 135
2016-08-04 23:30 | 150 | 148
2016-08-05 | 195 | 193
2016-08-05 00:30 | 196 | 195
2016-08-05 01:00 | 178 | 176
2016-08-05 01:30 | 161 | 159
2016-08-05 02:00 | 151 | 149
2016-08-05 02:30 | 148 | 145
2016-08-05 03:00 | 143 | 140
2016-08-05 03:30 | 141 | 139
2016-08-05 04:00 | 141 | 138
2016-08-05 04:30 | 142 | 139
2016-08-05 05:00 | 144 | 142
2016-08-05 05:30 | 150 | 148
2016-08-05 06:00 | 166 | 164
2016-08-05 06:30 | 178 | 176
2016-08-05 07:00 | 184 | 182
2016-08-05 07:30 | 195 | 193
2016-08-05 08:00 | 202 | 200
2016-08-05 08:30 | 201 | 199
2016-08-05 09:00 | 202 | 200
2016-08-05 09:30 | 197 | 195
2016-08-05 10:00 | 194 | 192
2016-08-05 10:30 | 185 | 182
2016-08-05 11:00 | 183 | 180
2016-08-05 11:30 | 184 | 181
2016-08-05 12:00 | 181 | 179
2016-08-05 12:30 | 181 | 179
2016-08-05 13:00 | 185 | 183
2016-08-05 13:30 | 186 | 184
2016-08-05 14:00 | 186 | 183
2016-08-05 14:30 | 175 | 172
2016-08-05 15:00 | 176 | 173
2016-08-05 15:30 | 178 | 175
2016-08-05 16:00 | 184 | 181
2016-08-05 16:30 | 193 | 190
2016-08-05 17:00 | 196 | 193
2016-08-05 17:30 | 194 | 191
2016-08-05 18:00 | 177 | 174
2016-08-05 18:30 | 177 | 173
2016-08-05 19:00 | 184 | 181
2016-08-05 19:30 | 185 | 182
2016-08-05 20:00 | 185 | 182
2016-08-05 20:30 | 178 | 174
2016-08-05 21:00 | 174 | 170
2016-08-05 21:30 | 170 | 167
2016-08-05 22:00 | 183 | 180
2016-08-05 22:30 | 174 | 171
2016-08-05 23:00 | 167 | 163
2016-08-05 23:30 | 174 | 171
2016-08-06 | 174 | 171
2016-08-06 00:30 | 175 | 172
2016-08-06 01:00 | 166 | 163
2016-08-06 01:30 | 159 | 156
2016-08-06 02:00 | 147 | 144
2016-08-06 02:30 | 139 | 136
2016-08-06 03:00 | 138 | 135
2016-08-06 03:30 | 137 | 134
2016-08-06 04:00 | 137 | 134
2016-08-06 04:30 | 135 | 132
2016-08-06 05:00 | 134 | 131
2016-08-06 05:30 | 137 | 135
2016-08-06 06:00 | 141 | 139
2016-08-06 06:30 | 154 | 152
2016-08-06 07:00 | 163 | 161
2016-08-06 07:30 | 173 | 172
2016-08-06 08:00 | 177 | 175
2016-08-06 08:30 | 183 | 181
2016-08-06 09:00 | 189 | 187
2016-08-06 09:30 | 177 | 175
2016-08-06 10:00 | 186 | 183
2016-08-06 10:30 | 195 | 193
2016-08-06 11:00 | 189 | 187
2016-08-06 11:30 | 184 | 182
2016-08-06 12:00 | 182 | 180
2016-08-06 12:30 | 178 | 176
2016-08-06 13:00 | 176 | 174
2016-08-06 13:30 | 176 | 174
2016-08-06 14:00 | 180 | 177
2016-08-06 14:30 | 171 | 169
2016-08-06 15:00 | 167 | 165
2016-08-06 15:30 | 165 | 163
2016-08-06 16:00 | 170 | 168
2016-08-06 16:30 | 179 | 177
2016-08-06 17:00 | 184 | 182
2016-08-06 17:30 | 191 | 189
2016-08-06 18:00 | 182 | 180
2016-08-06 18:30 | 181 | 178
2016-08-06 19:00 | 187 | 185
2016-08-06 19:30 | 202 | 201
2016-08-06 20:00 | 200 | 198
2016-08-06 20:30 | 214 | 212
2016-08-06 21:00 | 208 | 206
2016-08-06 21:30 | 205 | 203
2016-08-06 22:00 | 199 | 198
2016-08-06 22:30 | 192 | 191
2016-08-06 23:00 | 183 | 181
2016-08-06 23:30 | 178 | 176
2016-08-07 | 183 | 182
2016-08-07 00:30 | 174 | 172
2016-08-07 01:00 | 170 | 169
2016-08-07 01:30 | 163 | 161
2016-08-07 02:00 | 154 | 152
2016-08-07 02:30 | 148 | 146
2016-08-07 03:00 | 145 | 142
2016-08-07 03:30 | 142 | 140
2016-08-07 04:00 | 144 | 142
2016-08-07 04:30 | 153 | 150
2016-08-07 05:00 | 154 | 151
2016-08-07 05:30 | 160 | 158
2016-08-07 06:00 | 159 | 157
2016-08-07 06:30 | 167 | 165
2016-08-07 07:00 | 174 | 172
2016-08-07 07:30 | 188 | 186
2016-08-07 08:00 | 199 | 198
2016-08-07 08:30 | 206 | 204
2016-08-07 09:00 | 208 | 206
2016-08-07 09:30 | 206 | 204
2016-08-07 10:00 | 204 | 202
2016-08-07 10:30 | 207 | 205
2016-08-07 11:00 | 204 | 203
2016-08-07 11:30 | 200 | 199
2016-08-07 12:00 | 195 | 193
2016-08-07 12:30 | 189 | 188
2016-08-07 13:00 | 193 | 191
2016-08-07 13:30 | 194 | 192
2016-08-07 14:00 | 196 | 195
2016-08-07 14:30 | 178 | 176
2016-08-07 15:00 | 180 | 178
2016-08-07 15:30 | 179 | 177
2016-08-07 16:00 | 184 | 182
2016-08-07 16:30 | 194 | 193
2016-08-07 17:00 | 207 | 205
2016-08-07 17:30 | 213 | 211
2016-08-07 18:00 | 199 | 196
2016-08-07 18:30 | 212 | 209
2016-08-07 19:00 | 222 | 220
2016-08-07 19:30 | 224 | 222
2016-08-07 20:00 | 232 | 230
2016-08-07 20:30 | 244 | 242
2016-08-07 21:00 | 238 | 235
2016-08-07 21:30 | 235 | 233
2016-08-07 22:00 | 230 | 228
2016-08-07 22:30 | 219 | 217
2016-08-07 23:00 | 210 | 207
2016-08-07 23:30 | 200 | 197
2016-08-08 | 198 | 195
2016-08-08 00:30 | 193 | 190
2016-08-08 01:00 | 197 | 194
2016-08-08 01:30 | 193 | 190
2016-08-08 02:00 | 185 | 182
2016-08-08 02:30 | 181 | 177
2016-08-08 03:00 | 180 | 177
2016-08-08 03:30 | 176 | 173
2016-08-08 04:00 | 176 | 173
2016-08-08 04:30 | 170 | 166
2016-08-08 05:00 | 173 | 169
2016-08-08 05:30 | 186 | 183
2016-08-08 06:00 | 202 | 199
2016-08-08 06:30 | 225 | 223
2016-08-08 07:00 | 235 | 233
2016-08-08 07:30 | 258 | 256
2016-08-08 08:00 | 267 | 265
2016-08-08 08:30 | 265 | 263
2016-08-08 09:00 | 264 | 263
2016-08-08 09:30 | 263 | 262
2016-08-08 10:00 | 262 | 260
2016-08-08 10:30 | 249 | 247
2016-08-08 11:00 | 246 | 244
2016-08-08 11:30 | 247 | 246
2016-08-08 12:00 | 244 | 242
2016-08-08 12:30 | 251 | 249
2016-08-08 13:00 | 251 | 249
2016-08-08 13:30 | 252 | 250
2016-08-08 14:00 | 253 | 251
2016-08-08 14:30 | 244 | 242
2016-08-08 15:00 | 240 | 238
2016-08-08 15:30 | 242 | 240
2016-08-08 16:00 | 244 | 242
2016-08-08 16:30 | 248 | 246
2016-08-08 17:00 | 257 | 255
2016-08-08 17:30 | 251 | 249
2016-08-08 18:00 | 230 | 228
2016-08-08 18:30 | 235 | 232
2016-08-08 19:00 | 238 | 235
2016-08-08 19:30 | 226 | 223
2016-08-08 20:00 | 230 | 227
2016-08-08 20:30 | 225 | 222
2016-08-08 21:00 | 233 | 230
2016-08-08 21:30 | 227 | 224
2016-08-08 22:00 | 229 | 226
2016-08-08 22:30 | 239 | 237
2016-08-08 23:00 | 242 | 240
2016-08-08 23:30 | 239 | 236
2016-08-09 | 235 | 233
2016-08-09 00:30 | 226 | 223
2016-08-09 01:00 | 213 | 210
2016-08-09 01:30 | 197 | 194
2016-08-09 02:00 | 189 | 186
2016-08-09 02:30 | 180 | 176
2016-08-09 03:00 | 175 | 171
2016-08-09 03:30 | 174 | 170
2016-08-09 04:00 | 175 | 172
2016-08-09 04:30 | 175 | 171
2016-08-09 05:00 | 177 | 174
2016-08-09 05:30 | 186 | 184
2016-08-09 06:00 | 193 | 191
2016-08-09 06:30 | 216 | 214
2016-08-09 07:00 | 225 | 223
2016-08-09 07:30 | 236 | 233
2016-08-09 08:00 | 242 | 238
2016-08-09 08:30 | 248 | 245
2016-08-09 09:00 | 256 | 254
2016-08-09 09:30 | 255 | 253
2016-08-09 10:00 | 249 | 246
2016-08-09 10:30 | 245 | 242
2016-08-09 11:00 | 241 | 238
2016-08-09 11:30 | 241 | 238
2016-08-09 12:00 | 238 | 235
2016-08-09 12:30 | 238 | 235
2016-08-09 13:00 | 240 | 237
2016-08-09 13:30 | 241 | 238
2016-08-09 14:00 | 243 | 239
2016-08-09 14:30 | 231 | 228
2016-08-09 15:00 | 228 | 225
2016-08-09 15:30 | 239 | 236
2016-08-09 16:00 | 218 | 213
2016-08-09 16:30 | 237 | 233
2016-08-09 17:00 | 248 | 245
2016-08-09 17:30 | 256 | 253
2016-08-09 18:00 | 236 | 232
2016-08-09 18:30 | 233 | 230
2016-08-09 19:00 | 235 | 232
2016-08-09 19:30 | 241 | 238
2016-08-09 20:00 | 245 | 243
2016-08-09 20:30 | 256 | 254
2016-08-09 21:00 | 253 | 250
2016-08-09 21:30 | 244 | 241
2016-08-09 22:00 | 247 | 244
2016-08-09 22:30 | 246 | 243
2016-08-09 23:00 | 245 | 242
2016-08-09 23:30 | 243 | 240
2016-08-10 | 236 | 233
2016-08-10 00:30 | 226 | 223
2016-08-10 01:00 | 217 | 214
2016-08-10 01:30 | 199 | 195
2016-08-10 02:00 | 188 | 185
2016-08-10 02:30 | 186 | 182
2016-08-10 03:00 | 185 | 181
2016-08-10 03:30 | 189 | 187
2016-08-10 04:00 | 193 | 190
2016-08-10 04:30 | 193 | 190
2016-08-10 05:00 | 195 | 193
2016-08-10 05:30 | 204 | 201
2016-08-10 06:00 | 214 | 212
2016-08-10 06:30 | 233 | 230
2016-08-10 07:00 | 250 | 248
2016-08-10 07:30 | 263 | 260
2016-08-10 08:00 | 272 | 269
2016-08-10 08:30 | 268 | 266
2016-08-10 09:00 | 253 | 250
2016-08-10 09:30 | 252 | 249
2016-08-10 10:00 | 249 | 246
2016-08-10 10:30 | 245 | 242
2016-08-10 11:00 | 240 | 237
2016-08-10 11:30 | 235 | 231
2016-08-10 12:00 | 233 | 229
2016-08-10 12:30 | 232 | 228
2016-08-10 13:00 | 226 | 222
2016-08-10 13:30 | 219 | 215
2016-08-10 14:00 | 220 | 217
2016-08-10 14:30 | 227 | 224
2016-08-10 15:00 | 232 | 229
2016-08-10 15:30 | 235 | 230
2016-08-10 16:00 | 237 | 233
2016-08-10 16:30 | 242 | 238
2016-08-10 17:00 | 247 | 243
2016-08-10 17:30 | 247 | 241
2016-08-10 18:00 | 232 | 226
2016-08-10 18:30 | 229 | 226
2016-08-10 19:00 | 238 | 235
2016-08-10 19:30 | 234 | 231
2016-08-10 20:00 | 232 | 229
2016-08-10 20:30 | 238 | 235
2016-08-10 21:00 | 234 | 232
2016-08-10 21:30 | 224 | 221
2016-08-10 22:00 | 229 | 226
2016-08-10 22:30 | 245 | 242
2016-08-10 23:00 | 242 | 239
2016-08-10 23:30 | 238 | 235
2016-08-11 | 232 | 229
2016-08-11 00:30 | 221 | 218
2016-08-11 01:00 | 212 | 208
2016-08-11 01:30 | 197 | 192
2016-08-11 02:00 | 186 | 181
2016-08-11 02:30 | 180 | 176
2016-08-11 03:00 | 177 | 173
2016-08-11 03:30 | 173 | 169
2016-08-11 04:00 | 172 | 169
2016-08-11 04:30 | 174 | 171
2016-08-11 05:00 | 178 | 175
2016-08-11 05:30 | 186 | 183
2016-08-11 06:00 | 194 | 191
2016-08-11 06:30 | 216 | 213
2016-08-11 07:00 | 229 | 226
2016-08-11 07:30 | 224 | 220
2016-08-11 08:00 | 213 | 208
2016-08-11 08:30 | 209 | 205
2016-08-11 09:00 | 201 | 198
2016-08-11 09:30 | 205 | 202
2016-08-11 10:00 | 216 | 213
2016-08-11 10:30 | 230 | 228
2016-08-11 11:00 | 223 | 219
2016-08-11 11:30 | 216 | 213
2016-08-11 12:00 | 191 | 189
2016-08-11 12:30 | 185 | 184
2016-08-11 13:00 | 193 | 191
2016-08-11 13:30 | 195 | 193
2016-08-11 14:00 | 200 | 198
2016-08-11 14:30 | 195 | 192
2016-08-11 15:00 | 193 | 191
2016-08-11 15:30 | 181 | 179
2016-08-11 16:00 | 155 | 152
2016-08-11 16:30 | 150 | 148
2016-08-11 17:00 | 128 | 126
2016-08-11 17:30 | 121 | 116
2016-08-11 18:00 | 102 | 97
2016-08-11 18:30 | 102 | 97
2016-08-11 19:00 | 109 | 104
2016-08-11 19:30 | 107 | 102
2016-08-11 20:00 | 102 | 97
2016-08-11 20:30 | 97 | 93
2016-08-11 21:00 | 98 | 93
2016-08-11 21:30 | 101 | 97
2016-08-11 22:00 | 110 | 106
2016-08-11 22:30 | 111 | 107
2016-08-11 23:00 | 120 | 116
2016-08-11 23:30 | 152 | 149
2016-08-12 | 157 | 154
2016-08-12 00:30 | 146 | 143
2016-08-12 01:00 | 180 | 177
2016-08-12 01:30 | 196 | 194
2016-08-12 02:00 | 180 | 177
2016-08-12 02:30 | 176 | 173
2016-08-12 03:00 | 135 | 129
2016-08-12 03:30 | 105 | 100
2016-08-12 04:00 | 105 | 101
2016-08-12 04:30 | 103 | 99
2016-08-12 05:00 | 102 | 99
2016-08-12 05:30 | 112 | 108
2016-08-12 06:00 | 119 | 115
2016-08-12 06:30 | 133 | 129
2016-08-12 07:00 | 137 | 133
2016-08-12 07:30 | 153 | 149
2016-08-12 08:00 | 166 | 162
2016-08-12 08:30 | 168 | 165
2016-08-12 09:00 | 173 | 169
2016-08-12 09:30 | 170 | 165
2016-08-12 10:00 | 168 | 163
2016-08-12 10:30 | 167 | 162
2016-08-12 11:00 | 163 | 159
2016-08-12 11:30 | 160 | 156
2016-08-12 12:00 | 159 | 155
2016-08-12 12:30 | 158 | 154
2016-08-12 13:00 | 157 | 152
2016-08-12 13:30 | 158 | 154
2016-08-12 14:00 | 158 | 154
2016-08-12 14:30 | 152 | 147
2016-08-12 15:00 | 149 | 144
2016-08-12 15:30 | 159 | 154
2016-08-12 16:00 | 166 | 162
2016-08-12 16:30 | 175 | 170
2016-08-12 17:00 | 124 | 118
2016-08-12 17:30 | 97 | 92
2016-08-12 18:00 | 89 | 83
2016-08-12 18:30 | 88 | 82
2016-08-12 19:00 | 94 | 89
2016-08-12 19:30 | 82 | 76
2016-08-12 20:00 | 76 | 69
2016-08-12 20:30 | 78 | 72
2016-08-12 21:00 | 92 | 88
2016-08-12 21:30 | 143 | 140
2016-08-12 22:00 | 165 | 162
2016-08-12 22:30 | 171 | 168
2016-08-12 23:00 | 167 | 165
2016-08-12 23:30 | 183 | 180
2016-08-13 | 225 | 223
2016-08-13 00:30 | 218 | 216
2016-08-13 01:00 | 199 | 197
2016-08-13 01:30 | 185 | 182
2016-08-13 02:00 | 175 | 172
2016-08-13 02:30 | 170 | 167
2016-08-13 03:00 | 166 | 163
2016-08-13 03:30 | 164 | 161
2016-08-13 04:00 | 163 | 160
2016-08-13 04:30 | 163 | 160
2016-08-13 05:00 | 165 | 162
2016-08-13 05:30 | 175 | 172
2016-08-13 06:00 | 192 | 189
2016-08-13 06:30 | 198 | 195
2016-08-13 07:00 | 203 | 200
2016-08-13 07:30 | 210 | 207
2016-08-13 08:00 | 217 | 214
2016-08-13 08:30 | 225 | 222
2016-08-13 09:00 | 226 | 224
2016-08-13 09:30 | 233 | 231
2016-08-13 10:00 | 227 | 224
2016-08-13 10:30 | 225 | 223
2016-08-13 11:00 | 226 | 223
2016-08-13 11:30 | 220 | 217
2016-08-13 12:00 | 209 | 206
2016-08-13 12:30 | 208 | 205
2016-08-13 13:00 | 206 | 203
2016-08-13 13:30 | 211 | 208
2016-08-13 14:00 | 213 | 210
2016-08-13 14:30 | 201 | 198
2016-08-13 15:00 | 197 | 194
2016-08-13 15:30 | 204 | 201
2016-08-13 16:00 | 216 | 213
2016-08-13 16:30 | 223 | 221
2016-08-13 17:00 | 221 | 218
2016-08-13 17:30 | 220 | 218
2016-08-13 18:00 | 226 | 223
2016-08-13 18:30 | 208 | 206
2016-08-13 19:00 | 211 | 208
2016-08-13 19:30 | 214 | 211
2016-08-13 20:00 | 218 | 215
2016-08-13 20:30 | 210 | 207
2016-08-13 21:00 | 218 | 216
2016-08-13 21:30 | 229 | 226
2016-08-13 22:00 | 233 | 231
2016-08-13 22:30 | 226 | 223
2016-08-13 23:00 | 219 | 217
2016-08-13 23:30 | 213 | 210
2016-08-14 | 208 | 205
2016-08-14 00:30 | 199 | 196
2016-08-14 01:00 | 193 | 189
2016-08-14 01:30 | 182 | 177
2016-08-14 02:00 | 171 | 167
2016-08-14 02:30 | 169 | 165
2016-08-14 03:00 | 167 | 163
2016-08-14 03:30 | 162 | 158
2016-08-14 04:00 | 161 | 156
2016-08-14 04:30 | 161 | 157
2016-08-14 05:00 | 163 | 159
2016-08-14 05:30 | 166 | 162
2016-08-14 06:00 | 170 | 166
2016-08-14 06:30 | 176 | 173
2016-08-14 07:00 | 176 | 172
2016-08-14 07:30 | 183 | 179
2016-08-14 08:00 | 191 | 188
2016-08-14 08:30 | 196 | 193
2016-08-14 09:00 | 200 | 197
2016-08-14 09:30 | 202 | 199
2016-08-14 10:00 | 204 | 202
2016-08-14 10:30 | 204 | 202
2016-08-14 11:00 | 204 | 201
2016-08-14 11:30 | 201 | 199
2016-08-14 12:00 | 199 | 197
2016-08-14 12:30 | 200 | 198
2016-08-14 13:00 | 202 | 199
2016-08-14 13:30 | 203 | 200
2016-08-14 14:00 | 202 | 199
2016-08-14 14:30 | 193 | 190
2016-08-14 15:00 | 192 | 190
2016-08-14 15:30 | 198 | 196
2016-08-14 16:00 | 204 | 201
2016-08-14 16:30 | 204 | 201
2016-08-14 17:00 | 203 | 200
2016-08-14 17:30 | 205 | 202
2016-08-14 18:00 | 213 | 211
2016-08-14 18:30 | 218 | 215
2016-08-14 19:00 | 219 | 216
2016-08-14 19:30 | 222 | 219
2016-08-14 20:00 | 224 | 222
2016-08-14 20:30 | 219 | 217
2016-08-14 21:00 | 224 | 222
2016-08-14 21:30 | 230 | 228
2016-08-14 22:00 | 230 | 227
2016-08-14 22:30 | 214 | 212
2016-08-14 23:00 | 209 | 207
2016-08-14 23:30 | 206 | 203
2016-08-15 | 203 | 200
2016-08-15 00:30 | 195 | 192
2016-08-15 01:00 | 190 | 186
2016-08-15 01:30 | 181 | 177
2016-08-15 02:00 | 172 | 168
2016-08-15 02:30 | 169 | 165
2016-08-15 03:00 | 168 | 165
2016-08-15 03:30 | 170 | 166
2016-08-15 04:00 | 170 | 166
2016-08-15 04:30 | 172 | 169
2016-08-15 05:00 | 173 | 170
2016-08-15 05:30 | 177 | 173
2016-08-15 06:00 | 184 | 181
2016-08-15 06:30 | 208 | 205
2016-08-15 07:00 | 212 | 209
2016-08-15 07:30 | 225 | 223
2016-08-15 08:00 | 229 | 227
2016-08-15 08:30 | 243 | 241
2016-08-15 09:00 | 245 | 243
2016-08-15 09:30 | 253 | 251
2016-08-15 10:00 | 263 | 261
2016-08-15 10:30 | 256 | 254
2016-08-15 11:00 | 254 | 252
2016-08-15 11:30 | 247 | 245
2016-08-15 12:00 | 218 | 215
2016-08-15 12:30 | 212 | 207
2016-08-15 13:00 | 211 | 205
2016-08-15 13:30 | 217 | 212
2016-08-15 14:00 | 211 | 205
2016-08-15 14:30 | 212 | 207
2016-08-15 15:00 | 207 | 202
2016-08-15 15:30 | 188 | 182
2016-08-15 16:00 | 169 | 162
2016-08-15 16:30 | 177 | 170
2016-08-15 17:00 | 181 | 174
2016-08-15 17:30 | 140 | 132
2016-08-15 18:00 | 133 | 123
2016-08-15 18:30 | 125 | 115
2016-08-15 19:00 | 118 | 110
2016-08-15 19:30 | 114 | 108
2016-08-15 20:00 | 105 | 98
2016-08-15 20:30 | 111 | 104
2016-08-15 21:00 | 121 | 115
2016-08-15 21:30 | 153 | 147
2016-08-15 22:00 | 169 | 164
2016-08-15 22:30 | 170 | 165
2016-08-15 23:00 | 170 | 165
2016-08-15 23:30 | 168 | 162
2016-08-16 | 162 | 157
2016-08-16 00:30 | 152 | 147
2016-08-16 01:00 | 140 | 134
2016-08-16 01:30 | 128 | 122
2016-08-16 02:00 | 114 | 108
2016-08-16 02:30 | 105 | 99
2016-08-16 03:00 | 101 | 95
2016-08-16 03:30 | 105 | 99
2016-08-16 04:00 | 104 | 98
2016-08-16 04:30 | 102 | 96
2016-08-16 05:00 | 106 | 99
2016-08-16 05:30 | 113 | 106
2016-08-16 06:00 | 122 | 116
2016-08-16 06:30 | 141 | 135
2016-08-16 07:00 | 156 | 150
2016-08-16 07:30 | 182 | 177
2016-08-16 08:00 | 199 | 193
2016-08-16 08:30 | 212 | 205
2016-08-16 09:00 | 206 | 199
2016-08-16 09:30 | 206 | 199
2016-08-16 10:00 | 207 | 200
2016-08-16 10:30 | 201 | 194
2016-08-16 11:00 | 203 | 196
2016-08-16 11:30 | 189 | 181
2016-08-16 12:00 | 176 | 167
2016-08-16 12:30 | 170 | 162
2016-08-16 13:00 | 165 | 158
2016-08-16 13:30 | 166 | 160
2016-08-16 14:00 | 164 | 158
2016-08-16 14:30 | 152 | 146
2016-08-16 15:00 | 149 | 142
2016-08-16 15:30 | 164 | 158
2016-08-16 16:00 | 177 | 171
2016-08-16 16:30 | 181 | 175
2016-08-16 17:00 | 166 | 159
2016-08-16 17:30 | 113 | 103
2016-08-16 18:00 | 102 | 95
2016-08-16 18:30 | 114 | 104
2016-08-16 19:00 | 117 | 107
2016-08-16 19:30 | 104 | 95
2016-08-16 20:00 | 95 | 88
2016-08-16 20:30 | 107 | 101
2016-08-16 21:00 | 117 | 112
2016-08-16 21:30 | 158 | 153
2016-08-16 22:00 | 180 | 176
2016-08-16 22:30 | 177 | 173
2016-08-16 23:00 | 172 | 168
2016-08-16 23:30 | 167 | 163
2016-08-17 | 164 | 159
2016-08-17 00:30 | 152 | 146
2016-08-17 01:00 | 140 | 133
2016-08-17 01:30 | 123 | 118
2016-08-17 02:00 | 112 | 107
2016-08-17 02:30 | 105 | 99
2016-08-17 03:00 | 103 | 97
2016-08-17 03:30 | 103 | 97
2016-08-17 04:00 | 104 | 98
2016-08-17 04:30 | 115 | 110
2016-08-17 05:00 | 122 | 117
2016-08-17 05:30 | 128 | 123
2016-08-17 06:00 | 138 | 134
2016-08-17 06:30 | 162 | 158
2016-08-17 07:00 | 152 | 148
2016-08-17 07:30 | 178 | 174
2016-08-17 08:00 | 195 | 191
2016-08-17 08:30 | 199 | 195
2016-08-17 09:00 | 196 | 192
2016-08-17 09:30 | 196 | 191
2016-08-17 10:00 | 192 | 187
2016-08-17 10:30 | 190 | 185
2016-08-17 11:00 | 195 | 189
2016-08-17 11:30 | 197 | 192
2016-08-17 12:00 | 196 | 191
2016-08-17 12:30 | 196 | 192
2016-08-17 13:00 | 196 | 191
2016-08-17 13:30 | 192 | 187
2016-08-17 14:00 | 194 | 189
2016-08-17 14:30 | 144 | 138
2016-08-17 15:00 | 131 | 127
2016-08-17 15:30 | 133 | 128
2016-08-17 16:00 | 142 | 138
2016-08-17 16:30 | 146 | 142
2016-08-17 17:00 | 144 | 139
2016-08-17 17:30 | 132 | 127
2016-08-17 18:00 | 127 | 121
2016-08-17 18:30 | 123 | 119
2016-08-17 19:00 | 126 | 121
2016-08-17 19:30 | 116 | 112
2016-08-17 20:00 | 113 | 110
2016-08-17 20:30 | 109 | 106
2016-08-17 21:00 | 118 | 115
2016-08-17 21:30 | 125 | 123
2016-08-17 22:00 | 131 | 128
2016-08-17 22:30 | 119 | 116
2016-08-17 23:00 | 159 | 156
2016-08-17 23:30 | 198 | 196
2016-08-18 | 236 | 234
2016-08-18 00:30 | 228 | 226
2016-08-18 01:00 | 220 | 218
2016-08-18 01:30 | 201 | 200
2016-08-18 02:00 | 189 | 188
2016-08-18 02:30 | 178 | 177
2016-08-18 03:00 | 172 | 171
2016-08-18 03:30 | 169 | 168
2016-08-18 04:00 | 170 | 169
2016-08-18 04:30 | 174 | 173
2016-08-18 05:00 | 178 | 177
2016-08-18 05:30 | 186 | 185
2016-08-18 06:00 | 197 | 196
2016-08-18 06:30 | 217 | 216
2016-08-18 07:00 | 225 | 224
2016-08-18 07:30 | 237 | 236
2016-08-18 08:00 | 249 | 248
2016-08-18 08:30 | 254 | 253
2016-08-18 09:00 | 251 | 250
2016-08-18 09:30 | 252 | 251
2016-08-18 10:00 | 257 | 256
2016-08-18 10:30 | 249 | 248
2016-08-18 11:00 | 244 | 243
2016-08-18 11:30 | 245 | 244
2016-08-18 12:00 | 242 | 241
2016-08-18 12:30 | 242 | 241
2016-08-18 13:00 | 234 | 233
2016-08-18 13:30 | 235 | 234
2016-08-18 14:00 | 239 | 237
2016-08-18 14:30 | 231 | 230
2016-08-18 15:00 | 227 | 226
2016-08-18 15:30 | 232 | 231
2016-08-18 16:00 | 240 | 238
2016-08-18 16:30 | 242 | 241
2016-08-18 17:00 | 235 | 233
2016-08-18 17:30 | 231 | 230
2016-08-18 18:00 | 232 | 231
2016-08-18 18:30 | 235 | 233
2016-08-18 19:00 | 241 | 240
2016-08-18 19:30 | 233 | 231
2016-08-18 20:00 | 231 | 229
2016-08-18 20:30 | 240 | 239
2016-08-18 21:00 | 257 | 256
2016-08-18 21:30 | 246 | 245
2016-08-18 22:00 | 250 | 248
2016-08-18 22:30 | 242 | 240
2016-08-18 23:00 | 243 | 242
2016-08-18 23:30 | 238 | 237
2016-08-19 | 230 | 228
2016-08-19 00:30 | 219 | 216
2016-08-19 01:00 | 209 | 206
2016-08-19 01:30 | 198 | 195
2016-08-19 02:00 | 184 | 182
2016-08-19 02:30 | 176 | 174
2016-08-19 03:00 | 176 | 174
2016-08-19 03:30 | 175 | 173
2016-08-19 04:00 | 172 | 170
2016-08-19 04:30 | 173 | 171
2016-08-19 05:00 | 173 | 171
2016-08-19 05:30 | 179 | 177
2016-08-19 06:00 | 189 | 187
2016-08-19 06:30 | 209 | 207
2016-08-19 07:00 | 228 | 226
2016-08-19 07:30 | 245 | 243
2016-08-19 08:00 | 256 | 255
2016-08-19 08:30 | 267 | 266
2016-08-19 09:00 | 268 | 266
2016-08-19 09:30 | 262 | 260
2016-08-19 10:00 | 251 | 249
2016-08-19 10:30 | 246 | 244
2016-08-19 11:00 | 248 | 246
2016-08-19 11:30 | 246 | 244
2016-08-19 12:00 | 246 | 244
2016-08-19 12:30 | 247 | 245
2016-08-19 13:00 | 258 | 257
2016-08-19 13:30 | 244 | 242
2016-08-19 14:00 | 238 | 235
2016-08-19 14:30 | 231 | 228
2016-08-19 15:00 | 228 | 226
2016-08-19 15:30 | 230 | 228
2016-08-19 16:00 | 233 | 230
2016-08-19 16:30 | 236 | 233
2016-08-19 17:00 | 233 | 231
2016-08-19 17:30 | 225 | 222
2016-08-19 18:00 | 223 | 221
2016-08-19 18:30 | 224 | 221
2016-08-19 19:00 | 229 | 226
2016-08-19 19:30 | 222 | 219
2016-08-19 20:00 | 219 | 216
2016-08-19 20:30 | 214 | 211
2016-08-19 21:00 | 223 | 220
2016-08-19 21:30 | 234 | 231
2016-08-19 22:00 | 246 | 244
2016-08-19 22:30 | 246 | 244
2016-08-19 23:00 | 242 | 240
2016-08-19 23:30 | 237 | 235
2016-08-20 | 230 | 228
2016-08-20 00:30 | 219 | 217
2016-08-20 01:00 | 201 | 199
2016-08-20 01:30 | 191 | 189
2016-08-20 02:00 | 182 | 180
2016-08-20 02:30 | 173 | 172
2016-08-20 03:00 | 170 | 170
2016-08-20 03:30 | 172 | 171
2016-08-20 04:00 | 175 | 174
2016-08-20 04:30 | 178 | 178
2016-08-20 05:00 | 177 | 176
2016-08-20 05:30 | 173 | 172
2016-08-20 06:00 | 170 | 169
2016-08-20 06:30 | 178 | 177
2016-08-20 07:00 | 189 | 188
2016-08-20 07:30 | 202 | 201
2016-08-20 08:00 | 214 | 212
2016-08-20 08:30 | 223 | 222
2016-08-20 09:00 | 227 | 226
2016-08-20 09:30 | 225 | 224
2016-08-20 10:00 | 226 | 225
2016-08-20 10:30 | 228 | 227
2016-08-20 11:00 | 226 | 225
2016-08-20 11:30 | 223 | 222
2016-08-20 12:00 | 218 | 217
2016-08-20 12:30 | 217 | 216
2016-08-20 13:00 | 221 | 220
2016-08-20 13:30 | 214 | 213
2016-08-20 14:00 | 209 | 208
2016-08-20 14:30 | 197 | 196
2016-08-20 15:00 | 194 | 193
2016-08-20 15:30 | 205 | 204
2016-08-20 16:00 | 207 | 206
2016-08-20 16:30 | 214 | 213
2016-08-20 17:00 | 219 | 218
2016-08-20 17:30 | 223 | 222
2016-08-20 18:00 | 222 | 221
2016-08-20 18:30 | 217 | 216
2016-08-20 19:00 | 228 | 227
2016-08-20 19:30 | 234 | 233
2016-08-20 20:00 | 250 | 249
2016-08-20 20:30 | 245 | 244
2016-08-20 21:00 | 240 | 239
2016-08-20 21:30 | 231 | 230
2016-08-20 22:00 | 233 | 232
2016-08-20 22:30 | 227 | 226
2016-08-20 23:00 | 217 | 216
2016-08-20 23:30 | 211 | 209
2016-08-21 | 209 | 207
2016-08-21 00:30 | 200 | 198
2016-08-21 01:00 | 190 | 189
2016-08-21 01:30 | 182 | 181
2016-08-21 02:00 | 172 | 171
2016-08-21 02:30 | 166 | 165
2016-08-21 03:00 | 162 | 161
2016-08-21 03:30 | 161 | 159
2016-08-21 04:00 | 159 | 158
2016-08-21 04:30 | 158 | 157
2016-08-21 05:00 | 159 | 158
2016-08-21 05:30 | 160 | 159
2016-08-21 06:00 | 162 | 161
2016-08-21 06:30 | 165 | 164
2016-08-21 07:00 | 171 | 171
2016-08-21 07:30 | 180 | 179
2016-08-21 08:00 | 189 | 188
2016-08-21 08:30 | 199 | 198
2016-08-21 09:00 | 201 | 200
2016-08-21 09:30 | 204 | 203
2016-08-21 10:00 | 206 | 205
2016-08-21 10:30 | 209 | 208
2016-08-21 11:00 | 206 | 205
2016-08-21 11:30 | 205 | 204
2016-08-21 12:00 | 198 | 197
2016-08-21 12:30 | 194 | 193
2016-08-21 13:00 | 191 | 190
2016-08-21 13:30 | 190 | 189
2016-08-21 14:00 | 190 | 189
2016-08-21 14:30 | 182 | 181
2016-08-21 15:00 | 182 | 181
2016-08-21 15:30 | 192 | 191
2016-08-21 16:00 | 196 | 195
2016-08-21 16:30 | 195 | 194
2016-08-21 17:00 | 195 | 194
2016-08-21 17:30 | 201 | 200
2016-08-21 18:00 | 209 | 208
2016-08-21 18:30 | 217 | 216
2016-08-21 19:00 | 228 | 228
2016-08-21 19:30 | 223 | 222
2016-08-21 20:00 | 216 | 215
2016-08-21 20:30 | 211 | 210
2016-08-21 21:00 | 220 | 219
2016-08-21 21:30 | 243 | 242
2016-08-21 22:00 | 245 | 244
2016-08-21 22:30 | 232 | 231
2016-08-21 23:00 | 220 | 219
2016-08-21 23:30 | 212 | 211
2016-08-22 | 208 | 207
2016-08-22 00:30 | 202 | 201
2016-08-22 01:00 | 195 | 193
2016-08-22 01:30 | 185 | 183
2016-08-22 02:00 | 177 | 176
2016-08-22 02:30 | 173 | 172
2016-08-22 03:00 | 170 | 168
2016-08-22 03:30 | 168 | 166
2016-08-22 04:00 | 165 | 164
2016-08-22 04:30 | 167 | 166
2016-08-22 05:00 | 174 | 173
2016-08-22 05:30 | 180 | 179
2016-08-22 06:00 | 188 | 187
2016-08-22 06:30 | 203 | 202
2016-08-22 07:00 | 212 | 211
2016-08-22 07:30 | 221 | 220
2016-08-22 08:00 | 229 | 227
2016-08-22 08:30 | 235 | 232
2016-08-22 09:00 | 239 | 236
2016-08-22 09:30 | 233 | 231
2016-08-22 10:00 | 228 | 225
2016-08-22 10:30 | 226 | 223
2016-08-22 11:00 | 231 | 229
2016-08-22 11:30 | 232 | 230
2016-08-22 12:00 | 229 | 227
2016-08-22 12:30 | 276 | 274
2016-08-22 13:00 | 286 | 283
2016-08-22 13:30 | 283 | 281
2016-08-22 14:00 | 279 | 277
2016-08-22 14:30 | 276 | 274
2016-08-22 15:00 | 279 | 277
2016-08-22 15:30 | 280 | 278
2016-08-22 16:00 | 280 | 277
2016-08-22 16:30 | 290 | 288
2016-08-22 17:00 | 301 | 299
2016-08-22 17:30 | 304 | 302
2016-08-22 18:00 | 296 | 293
2016-08-22 18:30 | 292 | 289
2016-08-22 19:00 | 310 | 307
2016-08-22 19:30 | 305 | 302
2016-08-22 20:00 | 302 | 298
2016-08-22 20:30 | 289 | 287
2016-08-22 21:00 | 277 | 275
2016-08-22 21:30 | 271 | 268
2016-08-22 22:00 | 291 | 289
2016-08-22 22:30 | 289 | 287
2016-08-22 23:00 | 282 | 280
2016-08-22 23:30 | 277 | 275
2016-08-23 | 274 | 272
2016-08-23 00:30 | 267 | 264
2016-08-23 01:00 | 263 | 261
2016-08-23 01:30 | 246 | 244
2016-08-23 02:00 | 229 | 226
2016-08-23 02:30 | 227 | 225
2016-08-23 03:00 | 222 | 220
2016-08-23 03:30 | 222 | 219
2016-08-23 04:00 | 222 | 220
2016-08-23 04:30 | 226 | 224
2016-08-23 05:00 | 229 | 227
2016-08-23 05:30 | 223 | 220
2016-08-23 06:00 | 208 | 206
2016-08-23 06:30 | 210 | 207
2016-08-23 07:00 | 231 | 229
2016-08-23 07:30 | 248 | 246
2016-08-23 08:00 | 258 | 256
2016-08-23 08:30 | 265 | 263
2016-08-23 09:00 | 258 | 256
2016-08-23 09:30 | 255 | 253
2016-08-23 10:00 | 248 | 245
2016-08-23 10:30 | 248 | 246
2016-08-23 11:00 | 249 | 247
2016-08-23 11:30 | 251 | 249
2016-08-23 12:00 | 254 | 252
2016-08-23 12:30 | 246 | 244
2016-08-23 13:00 | 251 | 249
2016-08-23 13:30 | 258 | 256
2016-08-23 14:00 | 261 | 258
2016-08-23 14:30 | 248 | 246
2016-08-23 15:00 | 245 | 243
2016-08-23 15:30 | 242 | 240
2016-08-23 16:00 | 244 | 242
2016-08-23 16:30 | 249 | 247
2016-08-23 17:00 | 260 | 258
2016-08-23 17:30 | 260 | 258
2016-08-23 18:00 | 263 | 261
2016-08-23 18:30 | 285 | 283
2016-08-23 19:00 | 297 | 295
2016-08-23 19:30 | 300 | 298
2016-08-23 20:00 | 295 | 293
2016-08-23 20:30 | 285 | 282
2016-08-23 21:00 | 280 | 278
2016-08-23 21:30 | 273 | 271
2016-08-23 22:00 | 280 | 278
2016-08-23 22:30 | 298 | 296
2016-08-23 23:00 | 288 | 286
2016-08-23 23:30 | 279 | 277
2016-08-24 | 275 | 272
2016-08-24 00:30 | 258 | 256
2016-08-24 01:00 | 257 | 255
2016-08-24 01:30 | 243 | 240
2016-08-24 02:00 | 237 | 235
2016-08-24 02:30 | 232 | 229
2016-08-24 03:00 | 230 | 227
2016-08-24 03:30 | 230 | 227
2016-08-24 04:00 | 224 | 221
2016-08-24 04:30 | 224 | 221
2016-08-24 05:00 | 226 | 223
2016-08-24 05:30 | 236 | 233
2016-08-24 06:00 | 241 | 239
2016-08-24 06:30 | 261 | 259
2016-08-24 07:00 | 260 | 258
2016-08-24 07:30 | 279 | 277
2016-08-24 08:00 | 278 | 277
2016-08-24 08:30 | 279 | 277
2016-08-24 09:00 | 281 | 280
2016-08-24 09:30 | 271 | 269
2016-08-24 10:00 | 264 | 263
2016-08-24 10:30 | 262 | 260
2016-08-24 11:00 | 272 | 270
2016-08-24 11:30 | 261 | 259
2016-08-24 12:00 | 259 | 257
2016-08-24 12:30 | 261 | 260
2016-08-24 13:00 | 268 | 267
2016-08-24 13:30 | 267 | 265
2016-08-24 14:00 | 266 | 265
2016-08-24 14:30 | 269 | 268
2016-08-24 15:00 | 266 | 265
2016-08-24 15:30 | 260 | 258
2016-08-24 16:00 | 264 | 263
2016-08-24 16:30 | 278 | 276
2016-08-24 17:00 | 284 | 283
2016-08-24 17:30 | 297 | 295
2016-08-24 18:00 | 265 | 263
2016-08-24 18:30 | 226 | 224
2016-08-24 19:00 | 234 | 232
2016-08-24 19:30 | 263 | 262
2016-08-24 20:00 | 270 | 268
2016-08-24 20:30 | 228 | 226
2016-08-24 21:00 | 254 | 253
2016-08-24 21:30 | 275 | 274
2016-08-24 22:00 | 284 | 283
2016-08-24 22:30 | 278 | 277
2016-08-24 23:00 | 283 | 281
2016-08-24 23:30 | 282 | 281
2016-08-25 | 274 | 273
2016-08-25 00:30 | 264 | 262
2016-08-25 01:00 | 251 | 249
2016-08-25 01:30 | 238 | 236
2016-08-25 02:00 | 230 | 228
2016-08-25 02:30 | 223 | 220
2016-08-25 03:00 | 214 | 212
2016-08-25 03:30 | 217 | 215
2016-08-25 04:00 | 219 | 217
2016-08-25 04:30 | 219 | 217
2016-08-25 05:00 | 227 | 226
2016-08-25 05:30 | 230 | 228
2016-08-25 06:00 | 224 | 222
2016-08-25 06:30 | 243 | 241
2016-08-25 07:00 | 261 | 260
2016-08-25 07:30 | 292 | 291
2016-08-25 08:00 | 304 | 303
2016-08-25 08:30 | 309 | 308
2016-08-25 09:00 | 314 | 313
2016-08-25 09:30 | 311 | 310
2016-08-25 10:00 | 316 | 314
2016-08-25 10:30 | 324 | 323
2016-08-25 11:00 | 326 | 325
2016-08-25 11:30 | 324 | 323
2016-08-25 12:00 | 325 | 324
2016-08-25 12:30 | 321 | 320
2016-08-25 13:00 | 321 | 320
2016-08-25 13:30 | 322 | 320
2016-08-25 14:00 | 321 | 320
2016-08-25 14:30 | 314 | 313
2016-08-25 15:00 | 314 | 313
2016-08-25 15:30 | 310 | 309
2016-08-25 16:00 | 306 | 304
2016-08-25 16:30 | 304 | 302
2016-08-25 17:00 | 306 | 304
2016-08-25 17:30 | 311 | 309
2016-08-25 18:00 | 305 | 303
2016-08-25 18:30 | 305 | 303
2016-08-25 19:00 | 314 | 312
2016-08-25 19:30 | 307 | 305
2016-08-25 20:00 | 302 | 300
2016-08-25 20:30 | 290 | 288
2016-08-25 21:00 | 282 | 280
2016-08-25 21:30 | 272 | 270
2016-08-25 22:00 | 284 | 282
2016-08-25 22:30 | 282 | 280
2016-08-25 23:00 | 288 | 287
2016-08-25 23:30 | 277 | 275
2016-08-26 | 247 | 245
2016-08-26 00:30 | 248 | 247
2016-08-26 01:00 | 242 | 240
2016-08-26 01:30 | 230 | 228
2016-08-26 02:00 | 232 | 230
2016-08-26 02:30 | 226 | 224
2016-08-26 03:00 | 223 | 222
2016-08-26 03:30 | 220 | 219
2016-08-26 04:00 | 214 | 212
2016-08-26 04:30 | 214 | 212
2016-08-26 05:00 | 214 | 212
2016-08-26 05:30 | 218 | 216
2016-08-26 06:00 | 223 | 221
2016-08-26 06:30 | 239 | 238
2016-08-26 07:00 | 249 | 248
2016-08-26 07:30 | 273 | 272
2016-08-26 08:00 | 295 | 294
2016-08-26 08:30 | 308 | 307
2016-08-26 09:00 | 315 | 314
2016-08-26 09:30 | 305 | 304
2016-08-26 10:00 | 300 | 298
2016-08-26 10:30 | 307 | 306
2016-08-26 11:00 | 308 | 307
2016-08-26 11:30 | 312 | 311
2016-08-26 12:00 | 325 | 324
2016-08-26 12:30 | 327 | 326
2016-08-26 13:00 | 319 | 318
2016-08-26 13:30 | 319 | 318
2016-08-26 14:00 | 312 | 311
2016-08-26 14:30 | 304 | 302
2016-08-26 15:00 | 301 | 300
2016-08-26 15:30 | 301 | 299
2016-08-26 16:00 | 312 | 311
2016-08-26 16:30 | 283 | 282
2016-08-26 17:00 | 232 | 230
2016-08-26 17:30 | 231 | 229
2016-08-26 18:00 | 222 | 220
2016-08-26 18:30 | 220 | 218
2016-08-26 19:00 | 233 | 231
2016-08-26 19:30 | 226 | 224
2016-08-26 20:00 | 224 | 222
2016-08-26 20:30 | 221 | 219
2016-08-26 21:00 | 217 | 215
2016-08-26 21:30 | 205 | 202
2016-08-26 22:00 | 216 | 214
2016-08-26 22:30 | 285 | 284
2016-08-26 23:00 | 304 | 303
2016-08-26 23:30 | 302 | 301
2016-08-27 | 284 | 283
2016-08-27 00:30 | 276 | 275
2016-08-27 01:00 | 267 | 266
2016-08-27 01:30 | 255 | 254
2016-08-27 02:00 | 245 | 244
2016-08-27 02:30 | 239 | 238
2016-08-27 03:00 | 232 | 231
2016-08-27 03:30 | 229 | 228
2016-08-27 04:00 | 227 | 225
2016-08-27 04:30 | 225 | 224
2016-08-27 05:00 | 224 | 223
2016-08-27 05:30 | 230 | 228
2016-08-27 06:00 | 230 | 229
2016-08-27 06:30 | 235 | 234
2016-08-27 07:00 | 245 | 243
2016-08-27 07:30 | 257 | 256
2016-08-27 08:00 | 268 | 267
2016-08-27 08:30 | 275 | 273
2016-08-27 09:00 | 274 | 273
2016-08-27 09:30 | 269 | 268
2016-08-27 10:00 | 263 | 261
2016-08-27 10:30 | 261 | 260
2016-08-27 11:00 | 253 | 252
2016-08-27 11:30 | 252 | 251
2016-08-27 12:00 | 255 | 254
2016-08-27 12:30 | 253 | 252
2016-08-27 13:00 | 250 | 249
2016-08-27 13:30 | 251 | 249
2016-08-27 14:00 | 243 | 242
2016-08-27 14:30 | 240 | 239
2016-08-27 15:00 | 238 | 237
2016-08-27 15:30 | 243 | 241
2016-08-27 16:00 | 251 | 250
2016-08-27 16:30 | 259 | 258
2016-08-27 17:00 | 270 | 268
2016-08-27 17:30 | 281 | 279
2016-08-27 18:00 | 280 | 279
2016-08-27 18:30 | 278 | 276
2016-08-27 19:00 | 288 | 287
2016-08-27 19:30 | 286 | 285
2016-08-27 20:00 | 295 | 294
2016-08-27 20:30 | 286 | 285
2016-08-27 21:00 | 280 | 279
2016-08-27 21:30 | 275 | 274
2016-08-27 22:00 | 273 | 271
2016-08-27 22:30 | 272 | 270
2016-08-27 23:00 | 256 | 254
2016-08-27 23:30 | 245 | 243
2016-08-28 | 244 | 242
2016-08-28 00:30 | 232 | 230
2016-08-28 01:00 | 223 | 221
2016-08-28 01:30 | 212 | 211
2016-08-28 02:00 | 212 | 211
2016-08-28 02:30 | 215 | 215
2016-08-28 03:00 | 217 | 217
2016-08-28 03:30 | 220 | 220
2016-08-28 04:00 | 217 | 216
2016-08-28 04:30 | 217 | 216
2016-08-28 05:00 | 215 | 215
2016-08-28 05:30 | 222 | 221
2016-08-28 06:00 | 229 | 228
2016-08-28 06:30 | 232 | 231
2016-08-28 07:00 | 236 | 235
2016-08-28 07:30 | 241 | 240
2016-08-28 08:00 | 245 | 244
2016-08-28 08:30 | 249 | 248
2016-08-28 09:00 | 253 | 252
2016-08-28 09:30 | 251 | 250
2016-08-28 10:00 | 245 | 244
2016-08-28 10:30 | 249 | 248
2016-08-28 11:00 | 248 | 247
2016-08-28 11:30 | 228 | 227
2016-08-28 12:00 | 194 | 193
2016-08-28 12:30 | 193 | 192
2016-08-28 13:00 | 192 | 191
2016-08-28 13:30 | 187 | 186
2016-08-28 14:00 | 187 | 186
2016-08-28 14:30 | 181 | 180
2016-08-28 15:00 | 180 | 179
2016-08-28 15:30 | 182 | 181
2016-08-28 16:00 | 181 | 180
2016-08-28 16:30 | 189 | 187
2016-08-28 17:00 | 197 | 196
2016-08-28 17:30 | 214 | 213
2016-08-28 18:00 | 214 | 213
2016-08-28 18:30 | 215 | 214
2016-08-28 19:00 | 225 | 224
2016-08-28 19:30 | 221 | 220
2016-08-28 20:00 | 221 | 220
2016-08-28 20:30 | 224 | 223
2016-08-28 21:00 | 220 | 220
2016-08-28 21:30 | 211 | 211
2016-08-28 22:00 | 206 | 205
2016-08-28 22:30 | 206 | 205
2016-08-28 23:00 | 202 | 201
2016-08-28 23:30 | 192 | 191
2016-08-29 | 194 | 193
2016-08-29 00:30 | 189 | 188
2016-08-29 01:00 | 186 | 185
2016-08-29 01:30 | 177 | 176
2016-08-29 02:00 | 167 | 167
2016-08-29 02:30 | 161 | 161
2016-08-29 03:00 | 159 | 158
2016-08-29 03:30 | 157 | 156
2016-08-29 04:00 | 155 | 154
2016-08-29 04:30 | 156 | 155
2016-08-29 05:00 | 156 | 155
2016-08-29 05:30 | 163 | 162
2016-08-29 06:00 | 172 | 171
2016-08-29 06:30 | 192 | 191
2016-08-29 07:00 | 199 | 197
2016-08-29 07:30 | 205 | 202
2016-08-29 08:00 | 215 | 214
2016-08-29 08:30 | 222 | 219
2016-08-29 09:00 | 228 | 225
2016-08-29 09:30 | 228 | 226
2016-08-29 10:00 | 230 | 227
2016-08-29 10:30 | 227 | 223
2016-08-29 11:00 | 220 | 217
2016-08-29 11:30 | 227 | 223
2016-08-29 12:00 | 224 | 221
2016-08-29 12:30 | 223 | 220
2016-08-29 13:00 | 224 | 220
2016-08-29 13:30 | 226 | 222
2016-08-29 14:00 | 225 | 221
2016-08-29 14:30 | 218 | 214
2016-08-29 15:00 | 217 | 213
2016-08-29 15:30 | 222 | 218
2016-08-29 16:00 | 224 | 220
2016-08-29 16:30 | 232 | 228
2016-08-29 17:00 | 233 | 229
2016-08-29 17:30 | 232 | 227
2016-08-29 18:00 | 231 | 226
2016-08-29 18:30 | 225 | 220
2016-08-29 19:00 | 225 | 221
2016-08-29 19:30 | 224 | 220
2016-08-29 20:00 | 225 | 221
2016-08-29 20:30 | 206 | 202
2016-08-29 21:00 | 219 | 216
2016-08-29 21:30 | 215 | 213
2016-08-29 22:00 | 219 | 218
2016-08-29 22:30 | 215 | 213
2016-08-29 23:00 | 215 | 212
2016-08-29 23:30 | 213 | 210
2016-08-30 | 218 | 216
2016-08-30 00:30 | 210 | 208
2016-08-30 01:00 | 197 | 196
2016-08-30 01:30 | 184 | 183
2016-08-30 02:00 | 176 | 174
2016-08-30 02:30 | 168 | 166
2016-08-30 03:00 | 164 | 162
2016-08-30 03:30 | 163 | 161
2016-08-30 04:00 | 165 | 163
2016-08-30 04:30 | 165 | 164
2016-08-30 05:00 | 168 | 167
2016-08-30 05:30 | 175 | 174
2016-08-30 06:00 | 185 | 184
2016-08-30 06:30 | 197 | 194
2016-08-30 07:00 | 205 | 203
2016-08-30 07:30 | 235 | 233
2016-08-30 08:00 | 242 | 238
2016-08-30 08:30 | 245 | 241
2016-08-30 09:00 | 239 | 235
2016-08-30 09:30 | 234 | 230
2016-08-30 10:00 | 234 | 230
2016-08-30 10:30 | 230 | 228
2016-08-30 11:00 | 225 | 223
2016-08-30 11:30 | 232 | 230
2016-08-30 12:00 | 245 | 242
2016-08-30 12:30 | 245 | 243
2016-08-30 13:00 | 238 | 235
2016-08-30 13:30 | 234 | 231
2016-08-30 14:00 | 237 | 234
2016-08-30 14:30 | 236 | 233
2016-08-30 15:00 | 228 | 225
2016-08-30 15:30 | 219 | 216
2016-08-30 16:00 | 225 | 222
2016-08-30 16:30 | 231 | 228
2016-08-30 17:00 | 236 | 233
2016-08-30 17:30 | 236 | 233
2016-08-30 18:00 | 228 | 225
2016-08-30 18:30 | 229 | 227
2016-08-30 19:00 | 236 | 234
2016-08-30 19:30 | 231 | 228
2016-08-30 20:00 | 226 | 223
2016-08-30 20:30 | 224 | 221
2016-08-30 21:00 | 226 | 224
2016-08-30 21:30 | 220 | 217
2016-08-30 22:00 | 226 | 224
2016-08-30 22:30 | 240 | 238
2016-08-30 23:00 | 241 | 239
2016-08-30 23:30 | 235 | 233
2016-08-31 | 226 | 224
2016-08-31 00:30 | 213 | 210
2016-08-31 01:00 | 204 | 201
2016-08-31 01:30 | 188 | 185
2016-08-31 02:00 | 177 | 175
2016-08-31 02:30 | 174 | 172
2016-08-31 03:00 | 167 | 166
2016-08-31 03:30 | 167 | 165
2016-08-31 04:00 | 167 | 166
2016-08-31 04:30 | 170 | 169
2016-08-31 05:00 | 172 | 170
2016-08-31 05:30 | 178 | 176
2016-08-31 06:00 | 194 | 193
2016-08-31 06:30 | 216 | 215
2016-08-31 07:00 | 232 | 230
2016-08-31 07:30 | 249 | 248
2016-08-31 08:00 | 259 | 257
2016-08-31 08:30 | 262 | 260
2016-08-31 09:00 | 263 | 259
2016-08-31 09:30 | 263 | 259
2016-08-31 10:00 | 258 | 255
2016-08-31 10:30 | 248 | 244
2016-08-31 11:00 | 259 | 256
2016-08-31 11:30 | 250 | 247
2016-08-31 12:00 | 221 | 217
2016-08-31 12:30 | 206 | 201
2016-08-31 13:00 | 214 | 209
2016-08-31 13:30 | 209 | 205
2016-08-31 14:00 | 210 | 205
2016-08-31 14:30 | 202 | 197
2016-08-31 15:00 | 198 | 193
2016-08-31 15:30 | 203 | 198
2016-08-31 16:00 | 195 | 190
2016-08-31 16:30 | 163 | 157
2016-08-31 17:00 | 152 | 146
2016-08-31 17:30 | 143 | 137
2016-08-31 18:00 | 137 | 133
2016-08-31 18:30 | 137 | 133
2016-08-31 19:00 | 135 | 131
2016-08-31 19:30 | 134 | 131
2016-08-31 20:00 | 127 | 125
2016-08-31 20:30 | 118 | 115
2016-08-31 21:00 | 129 | 127
2016-08-31 21:30 | 129 | 127
2016-08-31 22:00 | 173 | 171
2016-08-31 22:30 | 124 | 121
2016-08-31 23:00 | 109 | 107
2016-08-31 23:30 | 150 | 148
2016-09-01 | 142 | 139
2016-09-01 00:30 | 137 | 134
2016-09-01 01:00 | 109 | 106
2016-09-01 01:30 | 115 | 112
2016-09-01 02:00 | 110 | 107
2016-09-01 02:30 | 105 | 102
2016-09-01 03:00 | 105 | 102
2016-09-01 03:30 | 102 | 99
2016-09-01 04:00 | 101 | 98
2016-09-01 04:30 | 103 | 100
2016-09-01 05:00 | 108 | 106
2016-09-01 05:30 | 94 | 91
2016-09-01 06:00 | 111 | 108
2016-09-01 06:30 | 79 | 76
2016-09-01 07:00 | 83 | 80
2016-09-01 07:30 | 110 | 107
2016-09-01 08:00 | 125 | 123
2016-09-01 08:30 | 140 | 136
2016-09-01 09:00 | 138 | 133
2016-09-01 09:30 | 132 | 128
2016-09-01 10:00 | 130 | 125
2016-09-01 10:30 | 135 | 130
2016-09-01 11:00 | 128 | 122
2016-09-01 11:30 | 129 | 124
2016-09-01 12:00 | 126 | 120
2016-09-01 12:30 | 118 | 110
2016-09-01 13:00 | 114 | 106
2016-09-01 13:30 | 110 | 102
2016-09-01 14:00 | 110 | 102
2016-09-01 14:30 | 104 | 95
2016-09-01 15:00 | 98 | 89
2016-09-01 15:30 | 103 | 95
2016-09-01 16:00 | 107 | 99
2016-09-01 16:30 | 112 | 104
2016-09-01 17:00 | 116 | 108
2016-09-01 17:30 | 122 | 114
2016-09-01 18:00 | 129 | 123
2016-09-01 18:30 | 139 | 133
2016-09-01 19:00 | 157 | 152
2016-09-01 19:30 | 152 | 147
2016-09-01 20:00 | 137 | 132
2016-09-01 20:30 | 125 | 122
2016-09-01 21:00 | 123 | 121
2016-09-01 21:30 | 136 | 134
2016-09-01 22:00 | 152 | 150
2016-09-01 22:30 | 111 | 108
2016-09-01 23:00 | 93 | 90
2016-09-01 23:30 | 82 | 79
2016-09-02 | 87 | 84
2016-09-02 00:30 | 115 | 113
2016-09-02 01:00 | 117 | 115
2016-09-02 01:30 | 113 | 111
2016-09-02 02:00 | 108 | 106
2016-09-02 02:30 | 109 | 107
2016-09-02 03:00 | 110 | 108
2016-09-02 03:30 | 108 | 106
2016-09-02 04:00 | 107 | 104
2016-09-02 04:30 | 107 | 104
2016-09-02 05:00 | 108 | 106
2016-09-02 05:30 | 115 | 113
2016-09-02 06:00 | 121 | 120
2016-09-02 06:30 | 100 | 98
2016-09-02 07:00 | 95 | 93
2016-09-02 07:30 | 117 | 115
2016-09-02 08:00 | 125 | 123
2016-09-02 08:30 | 124 | 122
2016-09-02 09:00 | 125 | 124
2016-09-02 09:30 | 119 | 118
2016-09-02 10:00 | 125 | 124
2016-09-02 10:30 | 122 | 120
2016-09-02 11:00 | 121 | 119
2016-09-02 11:30 | 126 | 125
2016-09-02 12:00 | 128 | 126
2016-09-02 12:30 | 121 | 119
2016-09-02 13:00 | 117 | 116
2016-09-02 13:30 | 116 | 114
2016-09-02 14:00 | 121 | 119
2016-09-02 14:30 | 113 | 111
2016-09-02 15:00 | 107 | 104
2016-09-02 15:30 | 105 | 103
2016-09-02 16:00 | 115 | 112
2016-09-02 16:30 | 120 | 117
2016-09-02 17:00 | 121 | 117
2016-09-02 17:30 | 123 | 119
2016-09-02 18:00 | 125 | 120
2016-09-02 18:30 | 128 | 123
2016-09-02 19:00 | 136 | 133
2016-09-02 19:30 | 136 | 133
2016-09-02 20:00 | 130 | 127
2016-09-02 20:30 | 123 | 120
2016-09-02 21:00 | 114 | 111
2016-09-02 21:30 | 106 | 103
2016-09-02 22:00 | 104 | 101
2016-09-02 22:30 | 98 | 95
2016-09-02 23:00 | 102 | 99
2016-09-02 23:30 | 94 | 91
2016-09-03 | 83 | 79
2016-09-03 00:30 | 101 | 99
2016-09-03 01:00 | 121 | 118
2016-09-03 01:30 | 117 | 114
2016-09-03 02:00 | 138 | 135
2016-09-03 02:30 | 183 | 181
2016-09-03 03:00 | 181 | 179
2016-09-03 03:30 | 179 | 177
2016-09-03 04:00 | 178 | 176
2016-09-03 04:30 | 176 | 174
2016-09-03 05:00 | 179 | 177
2016-09-03 05:30 | 181 | 179
2016-09-03 06:00 | 186 | 184
2016-09-03 06:30 | 193 | 191
2016-09-03 07:00 | 196 | 194
2016-09-03 07:30 | 208 | 206
2016-09-03 08:00 | 220 | 218
2016-09-03 08:30 | 220 | 218
2016-09-03 09:00 | 220 | 218
2016-09-03 09:30 | 220 | 218
2016-09-03 10:00 | 227 | 225
2016-09-03 10:30 | 230 | 228
2016-09-03 11:00 | 229 | 227
2016-09-03 11:30 | 223 | 221
2016-09-03 12:00 | 223 | 221
2016-09-03 12:30 | 224 | 222
2016-09-03 13:00 | 228 | 226
2016-09-03 13:30 | 226 | 225
2016-09-03 14:00 | 221 | 220
2016-09-03 14:30 | 206 | 205
2016-09-03 15:00 | 205 | 204
2016-09-03 15:30 | 211 | 210
2016-09-03 16:00 | 218 | 217
2016-09-03 16:30 | 223 | 223
2016-09-03 17:00 | 233 | 232
2016-09-03 17:30 | 241 | 240
2016-09-03 18:00 | 237 | 236
2016-09-03 18:30 | 231 | 229
2016-09-03 19:00 | 239 | 238
2016-09-03 19:30 | 246 | 245
2016-09-03 20:00 | 242 | 241
2016-09-03 20:30 | 241 | 239
2016-09-03 21:00 | 247 | 246
2016-09-03 21:30 | 245 | 244
2016-09-03 22:00 | 234 | 233
2016-09-03 22:30 | 227 | 225
2016-09-03 23:00 | 217 | 216
2016-09-03 23:30 | 208 | 206
2016-09-04 | 200 | 198
2016-09-04 00:30 | 191 | 189
2016-09-04 01:00 | 185 | 183
2016-09-04 01:30 | 181 | 180
2016-09-04 02:00 | 177 | 175
2016-09-04 02:30 | 177 | 175
2016-09-04 03:00 | 172 | 170
2016-09-04 03:30 | 171 | 169
2016-09-04 04:00 | 170 | 168
2016-09-04 04:30 | 172 | 169
2016-09-04 05:00 | 175 | 172
2016-09-04 05:30 | 176 | 173
2016-09-04 06:00 | 175 | 173
2016-09-04 06:30 | 180 | 178
2016-09-04 07:00 | 187 | 185
2016-09-04 07:30 | 193 | 191
2016-09-04 08:00 | 200 | 198
2016-09-04 08:30 | 207 | 206
2016-09-04 09:00 | 215 | 213
2016-09-04 09:30 | 219 | 217
2016-09-04 10:00 | 217 | 215
2016-09-04 10:30 | 220 | 219
2016-09-04 11:00 | 215 | 214
2016-09-04 11:30 | 217 | 215
2016-09-04 12:00 | 222 | 220
2016-09-04 12:30 | 216 | 214
2016-09-04 13:00 | 213 | 211
2016-09-04 13:30 | 214 | 213
2016-09-04 14:00 | 213 | 211
2016-09-04 14:30 | 202 | 200
2016-09-04 15:00 | 203 | 201
2016-09-04 15:30 | 202 | 200
2016-09-04 16:00 | 211 | 209
2016-09-04 16:30 | 221 | 220
2016-09-04 17:00 | 230 | 228
2016-09-04 17:30 | 243 | 241
2016-09-04 18:00 | 244 | 242
2016-09-04 18:30 | 247 | 245
2016-09-04 19:00 | 254 | 252
2016-09-04 19:30 | 252 | 250
2016-09-04 20:00 | 245 | 243
2016-09-04 20:30 | 248 | 246
2016-09-04 21:00 | 240 | 238
2016-09-04 21:30 | 232 | 230
2016-09-04 22:00 | 221 | 219
2016-09-04 22:30 | 207 | 205
2016-09-04 23:00 | 201 | 199
2016-09-04 23:30 | 196 | 193
2016-09-05 | 188 | 185
2016-09-05 00:30 | 182 | 179
2016-09-05 01:00 | 179 | 177
2016-09-05 01:30 | 176 | 173
2016-09-05 02:00 | 178 | 175
2016-09-05 02:30 | 174 | 172
2016-09-05 03:00 | 174 | 171
2016-09-05 03:30 | 173 | 170
2016-09-05 04:00 | 169 | 166
2016-09-05 04:30 | 167 | 164
2016-09-05 05:00 | 169 | 166
2016-09-05 05:30 | 177 | 174
2016-09-05 06:00 | 179 | 176
2016-09-05 06:30 | 196 | 193
2016-09-05 07:00 | 203 | 200
2016-09-05 07:30 | 229 | 226
2016-09-05 08:00 | 241 | 238
2016-09-05 08:30 | 243 | 240
2016-09-05 09:00 | 248 | 246
2016-09-05 09:30 | 253 | 251
2016-09-05 10:00 | 251 | 248
2016-09-05 10:30 | 255 | 249
2016-09-05 11:00 | 255 | 248
2016-09-05 11:30 | 257 | 251
2016-09-05 12:00 | 256 | 250
2016-09-05 12:30 | 251 | 245
2016-09-05 13:00 | 252 | 246
2016-09-05 13:30 | 253 | 247
2016-09-05 14:00 | 251 | 245
2016-09-05 14:30 | 251 | 245
2016-09-05 15:00 | 245 | 239
2016-09-05 15:30 | 242 | 237
2016-09-05 16:00 | 245 | 240
2016-09-05 16:30 | 204 | 198
2016-09-05 17:00 | 167 | 158
2016-09-05 17:30 | 165 | 157
2016-09-05 18:00 | 170 | 161
2016-09-05 18:30 | 170 | 161
2016-09-05 19:00 | 187 | 179
2016-09-05 19:30 | 188 | 180
2016-09-05 20:00 | 178 | 170
2016-09-05 20:30 | 177 | 169
2016-09-05 21:00 | 195 | 187
2016-09-05 21:30 | 195 | 187
2016-09-05 22:00 | 199 | 192
2016-09-05 22:30 | 145 | 136
2016-09-05 23:00 | 135 | 127
2016-09-05 23:30 | 194 | 187
2016-09-06 | 205 | 198
2016-09-06 00:30 | 199 | 192
2016-09-06 01:00 | 190 | 183
2016-09-06 01:30 | 185 | 177
2016-09-06 02:00 | 182 | 175
2016-09-06 02:30 | 181 | 174
2016-09-06 03:00 | 177 | 170
2016-09-06 03:30 | 178 | 171
2016-09-06 04:00 | 180 | 172
2016-09-06 04:30 | 179 | 171
2016-09-06 05:00 | 183 | 175
2016-09-06 05:30 | 191 | 184
2016-09-06 06:00 | 201 | 195
2016-09-06 06:30 | 212 | 207
2016-09-06 07:00 | 228 | 223
2016-09-06 07:30 | 249 | 244
2016-09-06 08:00 | 257 | 252
2016-09-06 08:30 | 251 | 245
2016-09-06 09:00 | 249 | 244
2016-09-06 09:30 | 247 | 242
2016-09-06 10:00 | 253 | 248
2016-09-06 10:30 | 252 | 247
2016-09-06 11:00 | 255 | 250
2016-09-06 11:30 | 253 | 248
2016-09-06 12:00 | 251 | 246
2016-09-06 12:30 | 253 | 248
2016-09-06 13:00 | 269 | 264
2016-09-06 13:30 | 277 | 272
2016-09-06 14:00 | 267 | 262
2016-09-06 14:30 | 257 | 252
2016-09-06 15:00 | 258 | 253
2016-09-06 15:30 | 258 | 253
2016-09-06 16:00 | 253 | 247
2016-09-06 16:30 | 259 | 254
2016-09-06 17:00 | 187 | 180
2016-09-06 17:30 | 172 | 165
2016-09-06 18:00 | 174 | 168
2016-09-06 18:30 | 184 | 177
2016-09-06 19:00 | 196 | 189
2016-09-06 19:30 | 221 | 215
2016-09-06 20:00 | 218 | 213
2016-09-06 20:30 | 201 | 196
2016-09-06 21:00 | 193 | 188
2016-09-06 21:30 | 189 | 185
2016-09-06 22:00 | 205 | 202
2016-09-06 22:30 | 154 | 151
2016-09-06 23:00 | 132 | 131
2016-09-06 23:30 | 187 | 186
2016-09-07 | 198 | 196
2016-09-07 00:30 | 193 | 190
2016-09-07 01:00 | 186 | 184
2016-09-07 01:30 | 182 | 180
2016-09-07 02:00 | 177 | 175
2016-09-07 02:30 | 175 | 173
2016-09-07 03:00 | 173 | 171
2016-09-07 03:30 | 176 | 174
2016-09-07 04:00 | 175 | 172
2016-09-07 04:30 | 175 | 173
2016-09-07 05:00 | 176 | 174
2016-09-07 05:30 | 181 | 179
2016-09-07 06:00 | 192 | 190
2016-09-07 06:30 | 209 | 205
2016-09-07 07:00 | 225 | 221
2016-09-07 07:30 | 240 | 237
2016-09-07 08:00 | 250 | 247
2016-09-07 08:30 | 256 | 253
2016-09-07 09:00 | 249 | 246
2016-09-07 09:30 | 252 | 248
2016-09-07 10:00 | 249 | 245
2016-09-07 10:30 | 242 | 238
2016-09-07 11:00 | 249 | 244
2016-09-07 11:30 | 257 | 253
2016-09-07 12:00 | 253 | 249
2016-09-07 12:30 | 245 | 241
2016-09-07 13:00 | 243 | 238
2016-09-07 13:30 | 249 | 245
2016-09-07 14:00 | 246 | 242
2016-09-07 14:30 | 234 | 230
2016-09-07 15:00 | 230 | 226
2016-09-07 15:30 | 231 | 227
2016-09-07 16:00 | 233 | 228
2016-09-07 16:30 | 192 | 187
2016-09-07 17:00 | 153 | 149
2016-09-07 17:30 | 158 | 154
2016-09-07 18:00 | 165 | 161
2016-09-07 18:30 | 179 | 175
2016-09-07 19:00 | 221 | 218
2016-09-07 19:30 | 228 | 224
2016-09-07 20:00 | 215 | 211
2016-09-07 20:30 | 197 | 193
2016-09-07 21:00 | 197 | 194
2016-09-07 21:30 | 197 | 193
2016-09-07 22:00 | 186 | 182
2016-09-07 22:30 | 149 | 147
2016-09-07 23:00 | 132 | 130
2016-09-07 23:30 | 182 | 181
2016-09-08 | 192 | 190
2016-09-08 00:30 | 190 | 189
2016-09-08 01:00 | 184 | 182
2016-09-08 01:30 | 180 | 178
2016-09-08 02:00 | 176 | 175
2016-09-08 02:30 | 173 | 171
2016-09-08 03:00 | 173 | 172
2016-09-08 03:30 | 172 | 170
2016-09-08 04:00 | 172 | 171
2016-09-08 04:30 | 171 | 170
2016-09-08 05:00 | 175 | 173
2016-09-08 05:30 | 185 | 184
2016-09-08 06:00 | 190 | 188
2016-09-08 06:30 | 211 | 209
2016-09-08 07:00 | 223 | 220
2016-09-08 07:30 | 247 | 244
2016-09-08 08:00 | 258 | 255
2016-09-08 08:30 | 261 | 259
2016-09-08 09:00 | 254 | 252
2016-09-08 09:30 | 254 | 252
2016-09-08 10:00 | 251 | 249
2016-09-08 10:30 | 251 | 249
2016-09-08 11:00 | 249 | 247
2016-09-08 11:30 | 246 | 244
2016-09-08 12:00 | 254 | 252
2016-09-08 12:30 | 256 | 253
2016-09-08 13:00 | 253 | 251
2016-09-08 13:30 | 258 | 256
2016-09-08 14:00 | 262 | 260
2016-09-08 14:30 | 257 | 254
2016-09-08 15:00 | 254 | 252
2016-09-08 15:30 | 257 | 254
2016-09-08 16:00 | 261 | 258
2016-09-08 16:30 | 261 | 258
2016-09-08 17:00 | 264 | 262
2016-09-08 17:30 | 266 | 263
2016-09-08 18:00 | 272 | 269
2016-09-08 18:30 | 274 | 271
2016-09-08 19:00 | 244 | 241
2016-09-08 19:30 | 244 | 241
2016-09-08 20:00 | 246 | 243
2016-09-08 20:30 | 210 | 207
2016-09-08 21:00 | 200 | 196
2016-09-08 21:30 | 182 | 178
2016-09-08 22:00 | 190 | 187
2016-09-08 22:30 | 158 | 154
2016-09-08 23:00 | 131 | 127
2016-09-08 23:30 | 189 | 187
2016-09-09 | 202 | 200
2016-09-09 00:30 | 196 | 194
2016-09-09 01:00 | 189 | 186
2016-09-09 01:30 | 181 | 178
2016-09-09 02:00 | 178 | 175
2016-09-09 02:30 | 178 | 175
2016-09-09 03:00 | 177 | 174
2016-09-09 03:30 | 179 | 176
2016-09-09 04:00 | 177 | 174
2016-09-09 04:30 | 176 | 173
2016-09-09 05:00 | 179 | 177
2016-09-09 05:30 | 184 | 182
2016-09-09 06:00 | 194 | 192
2016-09-09 06:30 | 209 | 207
2016-09-09 07:00 | 233 | 231
2016-09-09 07:30 | 253 | 250
2016-09-09 08:00 | 264 | 261
2016-09-09 08:30 | 267 | 263
2016-09-09 09:00 | 264 | 260
2016-09-09 09:30 | 265 | 262
2016-09-09 10:00 | 265 | 263
2016-09-09 10:30 | 258 | 256
2016-09-09 11:00 | 253 | 251
2016-09-09 11:30 | 254 | 251
2016-09-09 12:00 | 250 | 247
2016-09-09 12:30 | 248 | 245
2016-09-09 13:00 | 249 | 246
2016-09-09 13:30 | 248 | 245
2016-09-09 14:00 | 251 | 248
2016-09-09 14:30 | 235 | 232
2016-09-09 15:00 | 227 | 224
2016-09-09 15:30 | 235 | 232
2016-09-09 16:00 | 234 | 231
2016-09-09 16:30 | 238 | 234
2016-09-09 17:00 | 242 | 239
2016-09-09 17:30 | 250 | 247
2016-09-09 18:00 | 251 | 248
2016-09-09 18:30 | 256 | 253
2016-09-09 19:00 | 266 | 263
2016-09-09 19:30 | 264 | 261
2016-09-09 20:00 | 254 | 250
2016-09-09 20:30 | 247 | 243
2016-09-09 21:00 | 240 | 235
2016-09-09 21:30 | 254 | 250
2016-09-09 22:00 | 249 | 245
2016-09-09 22:30 | 231 | 226
2016-09-09 23:00 | 220 | 215
2016-09-09 23:30 | 216 | 212
2016-09-10 | 211 | 206
2016-09-10 00:30 | 205 | 200
2016-09-10 01:00 | 195 | 191
2016-09-10 01:30 | 191 | 187
2016-09-10 02:00 | 185 | 181
2016-09-10 02:30 | 184 | 180
2016-09-10 03:00 | 179 | 175
2016-09-10 03:30 | 178 | 174
2016-09-10 04:00 | 175 | 171
2016-09-10 04:30 | 176 | 173
2016-09-10 05:00 | 178 | 174
2016-09-10 05:30 | 180 | 177
2016-09-10 06:00 | 182 | 179
2016-09-10 06:30 | 271 | 269
2016-09-10 07:00 | 316 | 313
2016-09-10 07:30 | 345 | 341
2016-09-10 08:00 | 368 | 365
2016-09-10 08:30 | 380 | 377
2016-09-10 09:00 | 378 | 375
2016-09-10 09:30 | 386 | 383
2016-09-10 10:00 | 394 | 391
2016-09-10 10:30 | 393 | 390
2016-09-10 11:00 | 366 | 363
2016-09-10 11:30 | 233 | 229
2016-09-10 12:00 | 228 | 223
2016-09-10 12:30 | 225 | 220
2016-09-10 13:00 | 222 | 217
2016-09-10 13:30 | 223 | 218
2016-09-10 14:00 | 223 | 218
2016-09-10 14:30 | 216 | 212
2016-09-10 15:00 | 217 | 213
2016-09-10 15:30 | 219 | 215
2016-09-10 16:00 | 217 | 213
2016-09-10 16:30 | 216 | 212
2016-09-10 17:00 | 216 | 212
2016-09-10 17:30 | 229 | 226
2016-09-10 18:00 | 236 | 233
2016-09-10 18:30 | 240 | 237
2016-09-10 19:00 | 245 | 242
2016-09-10 19:30 | 251 | 248
2016-09-10 20:00 | 246 | 243
2016-09-10 20:30 | 237 | 234
2016-09-10 21:00 | 235 | 232
2016-09-10 21:30 | 232 | 229
2016-09-10 22:00 | 223 | 220
2016-09-10 22:30 | 216 | 213
2016-09-10 23:00 | 209 | 206
2016-09-10 23:30 | 202 | 198
2016-09-11 | 204 | 201
2016-09-11 00:30 | 198 | 195
2016-09-11 01:00 | 193 | 189
2016-09-11 01:30 | 188 | 185
2016-09-11 02:00 | 180 | 177
2016-09-11 02:30 | 182 | 179
2016-09-11 03:00 | 180 | 176
2016-09-11 03:30 | 178 | 174
2016-09-11 04:00 | 175 | 171
2016-09-11 04:30 | 174 | 170
2016-09-11 05:00 | 164 | 160
2016-09-11 05:30 | 161 | 156
2016-09-11 06:00 | 163 | 159
2016-09-11 06:30 | 174 | 170
2016-09-11 07:00 | 183 | 179
2016-09-11 07:30 | 187 | 184
2016-09-11 08:00 | 195 | 192
2016-09-11 08:30 | 201 | 198
2016-09-11 09:00 | 204 | 201
2016-09-11 09:30 | 210 | 208
2016-09-11 10:00 | 217 | 214
2016-09-11 10:30 | 217 | 214
2016-09-11 11:00 | 216 | 213
2016-09-11 11:30 | 212 | 209
2016-09-11 12:00 | 209 | 206
2016-09-11 12:30 | 214 | 211
2016-09-11 13:00 | 213 | 210
2016-09-11 13:30 | 219 | 215
2016-09-11 14:00 | 226 | 223
2016-09-11 14:30 | 210 | 207
2016-09-11 15:00 | 212 | 209
2016-09-11 15:30 | 220 | 217
2016-09-11 16:00 | 217 | 214
2016-09-11 16:30 | 227 | 224
2016-09-11 17:00 | 235 | 232
2016-09-11 17:30 | 248 | 245
2016-09-11 18:00 | 255 | 253
2016-09-11 18:30 | 251 | 248
2016-09-11 19:00 | 277 | 275
2016-09-11 19:30 | 284 | 282
2016-09-11 20:00 | 278 | 276
2016-09-11 20:30 | 268 | 265
2016-09-11 21:00 | 267 | 264
2016-09-11 21:30 | 256 | 253
2016-09-11 22:00 | 248 | 244
2016-09-11 22:30 | 230 | 226
2016-09-11 23:00 | 218 | 214
2016-09-11 23:30 | 205 | 201
2016-09-12 | 203 | 199
2016-09-12 00:30 | 204 | 201
2016-09-12 01:00 | 192 | 189
2016-09-12 01:30 | 189 | 185
2016-09-12 02:00 | 186 | 182
2016-09-12 02:30 | 182 | 179
2016-09-12 03:00 | 180 | 177
2016-09-12 03:30 | 180 | 177
2016-09-12 04:00 | 177 | 174
2016-09-12 04:30 | 181 | 178
2016-09-12 05:00 | 184 | 181
2016-09-12 05:30 | 190 | 188
2016-09-12 06:00 | 200 | 198
2016-09-12 06:30 | 220 | 217
2016-09-12 07:00 | 232 | 230
2016-09-12 07:30 | 261 | 259
2016-09-12 08:00 | 273 | 271
2016-09-12 08:30 | 275 | 271
2016-09-12 09:00 | 284 | 280
2016-09-12 09:30 | 279 | 276
2016-09-12 10:00 | 285 | 282
2016-09-12 10:30 | 277 | 273
2016-09-12 11:00 | 280 | 276
2016-09-12 11:30 | 272 | 269
2016-09-12 12:00 | 254 | 250
2016-09-12 12:30 | 247 | 242
2016-09-12 13:00 | 240 | 235
2016-09-12 13:30 | 245 | 241
2016-09-12 14:00 | 244 | 240
2016-09-12 14:30 | 235 | 230
2016-09-12 15:00 | 231 | 226
2016-09-12 15:30 | 225 | 219
2016-09-12 16:00 | 183 | 176
2016-09-12 16:30 | 141 | 134
2016-09-12 17:00 | 130 | 126
2016-09-12 17:30 | 129 | 126
2016-09-12 18:00 | 132 | 129
2016-09-12 18:30 | 140 | 137
2016-09-12 19:00 | 168 | 165
2016-09-12 19:30 | 171 | 168
2016-09-12 20:00 | 162 | 159
2016-09-12 20:30 | 149 | 146
2016-09-12 21:00 | 150 | 147
2016-09-12 21:30 | 184 | 182
2016-09-12 22:00 | 172 | 170
2016-09-12 22:30 | 126 | 123
2016-09-12 23:00 | 140 | 137
2016-09-12 23:30 | 121 | 117
2016-09-13 | 131 | 127
2016-09-13 00:30 | 127 | 123
2016-09-13 01:00 | 120 | 116
2016-09-13 01:30 | 118 | 114
2016-09-13 02:00 | 116 | 112
2016-09-13 02:30 | 112 | 109
2016-09-13 03:00 | 110 | 107
2016-09-13 03:30 | 112 | 109
2016-09-13 04:00 | 113 | 110
2016-09-13 04:30 | 115 | 112
2016-09-13 05:00 | 122 | 119
2016-09-13 05:30 | 131 | 129
2016-09-13 06:00 | 140 | 138
2016-09-13 06:30 | 136 | 133
2016-09-13 07:00 | 119 | 117
2016-09-13 07:30 | 133 | 130
2016-09-13 08:00 | 144 | 141
2016-09-13 08:30 | 150 | 147
2016-09-13 09:00 | 155 | 152
2016-09-13 09:30 | 155 | 152
2016-09-13 10:00 | 147 | 144
2016-09-13 10:30 | 148 | 145
2016-09-13 11:00 | 165 | 162
2016-09-13 11:30 | 151 | 147
2016-09-13 12:00 | 146 | 143
2016-09-13 12:30 | 148 | 144
2016-09-13 13:00 | 152 | 149
2016-09-13 13:30 | 156 | 152
2016-09-13 14:00 | 148 | 145
2016-09-13 14:30 | 134 | 130
2016-09-13 15:00 | 124 | 123
2016-09-13 15:30 | 127 | 126
2016-09-13 16:00 | 131 | 129
2016-09-13 16:30 | 135 | 133
2016-09-13 17:00 | 145 | 143
2016-09-13 17:30 | 163 | 161
2016-09-13 18:00 | 163 | 162
2016-09-13 18:30 | 157 | 156
2016-09-13 19:00 | 167 | 166
2016-09-13 19:30 | 160 | 159
2016-09-13 20:00 | 149 | 148
2016-09-13 20:30 | 140 | 139
2016-09-13 21:00 | 141 | 141
2016-09-13 21:30 | 180 | 179
2016-09-13 22:00 | 175 | 174
2016-09-13 22:30 | 134 | 134
2016-09-13 23:00 | 145 | 145
2016-09-13 23:30 | 163 | 162
2016-09-14 | 202 | 201
2016-09-14 00:30 | 198 | 197
2016-09-14 01:00 | 189 | 189
2016-09-14 01:30 | 185 | 184
2016-09-14 02:00 | 177 | 176
2016-09-14 02:30 | 175 | 175
2016-09-14 03:00 | 173 | 172
2016-09-14 03:30 | 172 | 171
2016-09-14 04:00 | 172 | 171
2016-09-14 04:30 | 174 | 173
2016-09-14 05:00 | 176 | 176
2016-09-14 05:30 | 181 | 180
2016-09-14 06:00 | 194 | 193
2016-09-14 06:30 | 207 | 206
2016-09-14 07:00 | 222 | 222
2016-09-14 07:30 | 246 | 245
2016-09-14 08:00 | 254 | 254
2016-09-14 08:30 | 252 | 251
2016-09-14 09:00 | 249 | 248
2016-09-14 09:30 | 251 | 250
2016-09-14 10:00 | 244 | 244
2016-09-14 10:30 | 246 | 245
2016-09-14 11:00 | 245 | 244
2016-09-14 11:30 | 246 | 245
2016-09-14 12:00 | 248 | 247
2016-09-14 12:30 | 254 | 253
2016-09-14 13:00 | 243 | 242
2016-09-14 13:30 | 242 | 241
2016-09-14 14:00 | 237 | 236
2016-09-14 14:30 | 234 | 233
2016-09-14 15:00 | 229 | 228
2016-09-14 15:30 | 234 | 233
2016-09-14 16:00 | 245 | 244
2016-09-14 16:30 | 235 | 234
2016-09-14 17:00 | 244 | 243
2016-09-14 17:30 | 252 | 251
2016-09-14 18:00 | 248 | 247
2016-09-14 18:30 | 263 | 262
2016-09-14 19:00 | 279 | 278
2016-09-14 19:30 | 280 | 279
2016-09-14 20:00 | 274 | 273
2016-09-14 20:30 | 263 | 262
2016-09-14 21:00 | 256 | 255
2016-09-14 21:30 | 244 | 243
2016-09-14 22:00 | 227 | 226
2016-09-14 22:30 | 211 | 210
2016-09-14 23:00 | 214 | 213
2016-09-14 23:30 | 205 | 205
2016-09-15 | 196 | 196
2016-09-15 00:30 | 193 | 193
2016-09-15 01:00 | 190 | 189
2016-09-15 01:30 | 180 | 179
2016-09-15 02:00 | 179 | 179
2016-09-15 02:30 | 172 | 172
2016-09-15 03:00 | 175 | 174
2016-09-15 03:30 | 172 | 172
2016-09-15 04:00 | 175 | 175
2016-09-15 04:30 | 183 | 182
2016-09-15 05:00 | 189 | 188
2016-09-15 05:30 | 197 | 196
2016-09-15 06:00 | 202 | 202
2016-09-15 06:30 | 223 | 222
2016-09-15 07:00 | 235 | 235
2016-09-15 07:30 | 245 | 244
2016-09-15 08:00 | 252 | 251
2016-09-15 08:30 | 256 | 256
2016-09-15 09:00 | 249 | 249
2016-09-15 09:30 | 250 | 249
2016-09-15 10:00 | 256 | 256
2016-09-15 10:30 | 259 | 258
2016-09-15 11:00 | 258 | 257
2016-09-15 11:30 | 257 | 257
2016-09-15 12:00 | 254 | 254
2016-09-15 12:30 | 264 | 263
2016-09-15 13:00 | 268 | 267
2016-09-15 13:30 | 265 | 265
2016-09-15 14:00 | 266 | 266
2016-09-15 14:30 | 259 | 258
2016-09-15 15:00 | 252 | 252
2016-09-15 15:30 | 252 | 251
2016-09-15 16:00 | 256 | 255
2016-09-15 16:30 | 265 | 265
2016-09-15 17:00 | 261 | 260
2016-09-15 17:30 | 267 | 266
2016-09-15 18:00 | 269 | 267
2016-09-15 18:30 | 283 | 282
2016-09-15 19:00 | 291 | 290
2016-09-15 19:30 | 287 | 286
2016-09-15 20:00 | 277 | 276
2016-09-15 20:30 | 270 | 269
2016-09-15 21:00 | 266 | 265
2016-09-15 21:30 | 250 | 249
2016-09-15 22:00 | 238 | 237
2016-09-15 22:30 | 232 | 231
2016-09-15 23:00 | 226 | 226
2016-09-15 23:30 | 217 | 217
2016-09-16 | 211 | 211
2016-09-16 00:30 | 208 | 208
2016-09-16 01:00 | 201 | 200
2016-09-16 01:30 | 191 | 190
2016-09-16 02:00 | 186 | 185
2016-09-16 02:30 | 181 | 181
2016-09-16 03:00 | 180 | 179
2016-09-16 03:30 | 181 | 180
2016-09-16 04:00 | 181 | 181
2016-09-16 04:30 | 178 | 177
2016-09-16 05:00 | 180 | 180
2016-09-16 05:30 | 185 | 185
2016-09-16 06:00 | 189 | 188
2016-09-16 06:30 | 197 | 197
2016-09-16 07:00 | 212 | 212
2016-09-16 07:30 | 233 | 233
2016-09-16 08:00 | 238 | 237
2016-09-16 08:30 | 247 | 246
2016-09-16 09:00 | 252 | 252
2016-09-16 09:30 | 254 | 253
2016-09-16 10:00 | 269 | 268
2016-09-16 10:30 | 273 | 272
2016-09-16 11:00 | 267 | 266
2016-09-16 11:30 | 264 | 263
2016-09-16 12:00 | 264 | 263
2016-09-16 12:30 | 261 | 260
2016-09-16 13:00 | 260 | 259
2016-09-16 13:30 | 259 | 258
2016-09-16 14:00 | 272 | 271
2016-09-16 14:30 | 257 | 256
2016-09-16 15:00 | 243 | 242
2016-09-16 15:30 | 244 | 243
2016-09-16 16:00 | 254 | 253
2016-09-16 16:30 | 259 | 258
2016-09-16 17:00 | 258 | 256
2016-09-16 17:30 | 249 | 248
2016-09-16 18:00 | 245 | 244
2016-09-16 18:30 | 253 | 252
2016-09-16 19:00 | 262 | 261
2016-09-16 19:30 | 255 | 254
2016-09-16 20:00 | 254 | 253
2016-09-16 20:30 | 249 | 248
2016-09-16 21:00 | 237 | 236
2016-09-16 21:30 | 228 | 227
2016-09-16 22:00 | 216 | 215
2016-09-16 22:30 | 213 | 212
2016-09-16 23:00 | 210 | 209
2016-09-16 23:30 | 210 | 210
2016-09-17 | 207 | 206
2016-09-17 00:30 | 201 | 200
2016-09-17 01:00 | 190 | 189
2016-09-17 01:30 | 183 | 182
2016-09-17 02:00 | 178 | 178
2016-09-17 02:30 | 173 | 172
2016-09-17 03:00 | 170 | 170
2016-09-17 03:30 | 168 | 167
2016-09-17 04:00 | 167 | 167
2016-09-17 04:30 | 166 | 165
2016-09-17 05:00 | 166 | 166
2016-09-17 05:30 | 166 | 166
2016-09-17 06:00 | 169 | 169
2016-09-17 06:30 | 173 | 172
2016-09-17 07:00 | 182 | 181
2016-09-17 07:30 | 188 | 188
2016-09-17 08:00 | 198 | 197
2016-09-17 08:30 | 220 | 219
2016-09-17 09:00 | 230 | 229
2016-09-17 09:30 | 232 | 232
2016-09-17 10:00 | 233 | 232
2016-09-17 10:30 | 234 | 233
2016-09-17 11:00 | 233 | 233
2016-09-17 11:30 | 234 | 233
2016-09-17 12:00 | 232 | 231
2016-09-17 12:30 | 232 | 231
2016-09-17 13:00 | 229 | 228
2016-09-17 13:30 | 231 | 230
2016-09-17 14:00 | 236 | 235
2016-09-17 14:30 | 230 | 229
2016-09-17 15:00 | 221 | 220
2016-09-17 15:30 | 222 | 222
2016-09-17 16:00 | 221 | 220
2016-09-17 16:30 | 229 | 228
2016-09-17 17:00 | 230 | 229
2016-09-17 17:30 | 239 | 238
2016-09-17 18:00 | 243 | 242
2016-09-17 18:30 | 239 | 238
2016-09-17 19:00 | 251 | 250
2016-09-17 19:30 | 257 | 256
2016-09-17 20:00 | 251 | 250
2016-09-17 20:30 | 240 | 238
2016-09-17 21:00 | 232 | 231
2016-09-17 21:30 | 224 | 222
2016-09-17 22:00 | 218 | 217
2016-09-17 22:30 | 220 | 219
2016-09-17 23:00 | 215 | 214
2016-09-17 23:30 | 209 | 208
2016-09-18 | 201 | 200
2016-09-18 00:30 | 191 | 190
2016-09-18 01:00 | 185 | 185
2016-09-18 01:30 | 180 | 179
2016-09-18 02:00 | 178 | 178
2016-09-18 02:30 | 171 | 171
2016-09-18 03:00 | 168 | 168
2016-09-18 03:30 | 172 | 172
2016-09-18 04:00 | 171 | 171
2016-09-18 04:30 | 172 | 171
2016-09-18 05:00 | 171 | 170
2016-09-18 05:30 | 166 | 166
2016-09-18 06:00 | 166 | 165
2016-09-18 06:30 | 169 | 169
2016-09-18 07:00 | 173 | 172
2016-09-18 07:30 | 178 | 177
2016-09-18 08:00 | 187 | 187
2016-09-18 08:30 | 197 | 196
2016-09-18 09:00 | 201 | 199
2016-09-18 09:30 | 199 | 198
2016-09-18 10:00 | 204 | 203
2016-09-18 10:30 | 212 | 211
2016-09-18 11:00 | 211 | 211
2016-09-18 11:30 | 213 | 212
2016-09-18 12:00 | 207 | 206
2016-09-18 12:30 | 207 | 206
2016-09-18 13:00 | 211 | 210
2016-09-18 13:30 | 214 | 213
2016-09-18 14:00 | 213 | 212
2016-09-18 14:30 | 203 | 202
2016-09-18 15:00 | 203 | 202
2016-09-18 15:30 | 209 | 208
2016-09-18 16:00 | 214 | 213
2016-09-18 16:30 | 217 | 216
2016-09-18 17:00 | 215 | 214
2016-09-18 17:30 | 226 | 225
2016-09-18 18:00 | 239 | 237
2016-09-18 18:30 | 249 | 247
2016-09-18 19:00 | 258 | 257
2016-09-18 19:30 | 255 | 253
2016-09-18 20:00 | 244 | 243
2016-09-18 20:30 | 228 | 226
2016-09-18 21:00 | 221 | 220
2016-09-18 21:30 | 215 | 214
2016-09-18 22:00 | 221 | 220
2016-09-18 22:30 | 224 | 223
2016-09-18 23:00 | 219 | 217
2016-09-18 23:30 | 209 | 209
2016-09-19 | 202 | 201
2016-09-19 00:30 | 195 | 194
2016-09-19 01:00 | 186 | 185
2016-09-19 01:30 | 181 | 181
2016-09-19 02:00 | 178 | 178
2016-09-19 02:30 | 177 | 177
2016-09-19 03:00 | 176 | 176
2016-09-19 03:30 | 171 | 170
2016-09-19 04:00 | 174 | 174
2016-09-19 04:30 | 175 | 175
2016-09-19 05:00 | 178 | 177
2016-09-19 05:30 | 185 | 185
2016-09-19 06:00 | 194 | 194
2016-09-19 06:30 | 211 | 211
2016-09-19 07:00 | 214 | 214
2016-09-19 07:30 | 243 | 242
2016-09-19 08:00 | 250 | 249
2016-09-19 08:30 | 254 | 253
2016-09-19 09:00 | 253 | 252
2016-09-19 09:30 | 253 | 252
2016-09-19 10:00 | 259 | 258
2016-09-19 10:30 | 267 | 266
2016-09-19 11:00 | 265 | 264
2016-09-19 11:30 | 262 | 261
2016-09-19 12:00 | 262 | 261
2016-09-19 12:30 | 267 | 266
2016-09-19 13:00 | 266 | 265
2016-09-19 13:30 | 261 | 260
2016-09-19 14:00 | 261 | 259
2016-09-19 14:30 | 261 | 259
2016-09-19 15:00 | 255 | 254
2016-09-19 15:30 | 251 | 250
2016-09-19 16:00 | 259 | 257
2016-09-19 16:30 | 266 | 264
2016-09-19 17:00 | 258 | 257
2016-09-19 17:30 | 259 | 258
2016-09-19 18:00 | 262 | 260
2016-09-19 18:30 | 282 | 281
2016-09-19 19:00 | 295 | 294
2016-09-19 19:30 | 300 | 298
2016-09-19 20:00 | 286 | 285
2016-09-19 20:30 | 276 | 275
2016-09-19 21:00 | 267 | 266
2016-09-19 21:30 | 257 | 256
2016-09-19 22:00 | 248 | 247
2016-09-19 22:30 | 230 | 230
2016-09-19 23:00 | 219 | 219
2016-09-19 23:30 | 211 | 210
2016-09-20 | 201 | 200
2016-09-20 00:30 | 192 | 192
2016-09-20 01:00 | 192 | 192
2016-09-20 01:30 | 192 | 191
2016-09-20 02:00 | 186 | 185
2016-09-20 02:30 | 182 | 182
2016-09-20 03:00 | 177 | 176
2016-09-20 03:30 | 173 | 173
2016-09-20 04:00 | 174 | 173
2016-09-20 04:30 | 176 | 175
2016-09-20 05:00 | 175 | 175
2016-09-20 05:30 | 181 | 181
2016-09-20 06:00 | 196 | 195
2016-09-20 06:30 | 211 | 210
2016-09-20 07:00 | 216 | 215
2016-09-20 07:30 | 236 | 235
2016-09-20 08:00 | 249 | 248
2016-09-20 08:30 | 268 | 266
2016-09-20 09:00 | 272 | 270
2016-09-20 09:30 | 273 | 272
2016-09-20 10:00 | 271 | 269
2016-09-20 10:30 | 270 | 269
2016-09-20 11:00 | 271 | 269
2016-09-20 11:30 | 264 | 263
2016-09-20 12:00 | 244 | 243
2016-09-20 12:30 | 237 | 236
2016-09-20 13:00 | 236 | 234
2016-09-20 13:30 | 238 | 237
2016-09-20 14:00 | 236 | 234
2016-09-20 14:30 | 225 | 224
2016-09-20 15:00 | 222 | 221
2016-09-20 15:30 | 214 | 212
2016-09-20 16:00 | 190 | 188
2016-09-20 16:30 | 177 | 175
2016-09-20 17:00 | 156 | 154
2016-09-20 17:30 | 166 | 164
2016-09-20 18:00 | 142 | 141
2016-09-20 18:30 | 143 | 141
2016-09-20 19:00 | 147 | 146
2016-09-20 19:30 | 153 | 151
2016-09-20 20:00 | 144 | 143
2016-09-20 20:30 | 148 | 147
2016-09-20 21:00 | 156 | 155
2016-09-20 21:30 | 171 | 170
2016-09-20 22:00 | 179 | 178
2016-09-20 22:30 | 124 | 122
2016-09-20 23:00 | 152 | 151
2016-09-20 23:30 | 146 | 145
2016-09-21 | 138 | 137
2016-09-21 00:30 | 131 | 130
2016-09-21 01:00 | 124 | 123
2016-09-21 01:30 | 117 | 116
2016-09-21 02:00 | 115 | 114
2016-09-21 02:30 | 112 | 111
2016-09-21 03:00 | 111 | 110
2016-09-21 03:30 | 110 | 108
2016-09-21 04:00 | 109 | 108
2016-09-21 04:30 | 109 | 107
2016-09-21 05:00 | 110 | 109
2016-09-21 05:30 | 116 | 115
2016-09-21 06:00 | 125 | 124
2016-09-21 06:30 | 139 | 138
2016-09-21 07:00 | 139 | 138
2016-09-21 07:30 | 156 | 155
2016-09-21 08:00 | 139 | 138
2016-09-21 08:30 | 140 | 138
2016-09-21 09:00 | 143 | 142
2016-09-21 09:30 | 132 | 131
2016-09-21 10:00 | 129 | 128
2016-09-21 10:30 | 128 | 127
2016-09-21 11:00 | 132 | 131
2016-09-21 11:30 | 139 | 138
2016-09-21 12:00 | 193 | 192
2016-09-21 12:30 | 193 | 192
2016-09-21 13:00 | 190 | 189
2016-09-21 13:30 | 195 | 194
2016-09-21 14:00 | 179 | 178
2016-09-21 14:30 | 139 | 138
2016-09-21 15:00 | 171 | 170
2016-09-21 15:30 | 150 | 149
2016-09-21 16:00 | 130 | 129
2016-09-21 16:30 | 135 | 133
2016-09-21 17:00 | 135 | 134
2016-09-21 17:30 | 186 | 185
2016-09-21 18:00 | 178 | 177
2016-09-21 18:30 | 153 | 152
2016-09-21 19:00 | 158 | 157
2016-09-21 19:30 | 156 | 155
2016-09-21 20:00 | 147 | 146
2016-09-21 20:30 | 150 | 150
2016-09-21 21:00 | 144 | 143
2016-09-21 21:30 | 140 | 139
2016-09-21 22:00 | 161 | 160
2016-09-21 22:30 | 126 | 125
2016-09-21 23:00 | 119 | 118
2016-09-21 23:30 | 105 | 104
2016-09-22 | 109 | 107
2016-09-22 00:30 | 136 | 135
2016-09-22 01:00 | 125 | 124
2016-09-22 01:30 | 126 | 125
2016-09-22 02:00 | 117 | 116
2016-09-22 02:30 | 117 | 116
2016-09-22 03:00 | 117 | 116
2016-09-22 03:30 | 116 | 116
2016-09-22 04:00 | 116 | 115
2016-09-22 04:30 | 115 | 114
2016-09-22 05:00 | 120 | 119
2016-09-22 05:30 | 125 | 124
2016-09-22 06:00 | 132 | 131
2016-09-22 06:30 | 94 | 92
2016-09-22 07:00 | 104 | 103
2016-09-22 07:30 | 164 | 163
2016-09-22 08:00 | 156 | 155
2016-09-22 08:30 | 162 | 161
2016-09-22 09:00 | 159 | 159
2016-09-22 09:30 | 189 | 188
2016-09-22 10:00 | 167 | 166
2016-09-22 10:30 | 180 | 178
2016-09-22 11:00 | 171 | 170
2016-09-22 11:30 | 158 | 156
2016-09-22 12:00 | 156 | 155
2016-09-22 12:30 | 157 | 156
2016-09-22 13:00 | 165 | 163
2016-09-22 13:30 | 195 | 194
2016-09-22 14:00 | 203 | 202
2016-09-22 14:30 | 194 | 192
2016-09-22 15:00 | 203 | 201
2016-09-22 15:30 | 208 | 207
2016-09-22 16:00 | 173 | 171
2016-09-22 16:30 | 163 | 161
2016-09-22 17:00 | 154 | 152
2016-09-22 17:30 | 159 | 157
2016-09-22 18:00 | 167 | 165
2016-09-22 18:30 | 162 | 159
2016-09-22 19:00 | 149 | 147
2016-09-22 19:30 | 179 | 177
2016-09-22 20:00 | 199 | 197
2016-09-22 20:30 | 166 | 165
2016-09-22 21:00 | 162 | 161
2016-09-22 21:30 | 159 | 157
2016-09-22 22:00 | 176 | 175
2016-09-22 22:30 | 135 | 133
2016-09-22 23:00 | 115 | 113
2016-09-22 23:30 | 158 | 157
2016-09-23 | 212 | 211
2016-09-23 00:30 | 204 | 203
2016-09-23 01:00 | 195 | 193
2016-09-23 01:30 | 189 | 188
2016-09-23 02:00 | 184 | 183
2016-09-23 02:30 | 183 | 182
2016-09-23 03:00 | 181 | 180
2016-09-23 03:30 | 178 | 177
2016-09-23 04:00 | 177 | 176
2016-09-23 04:30 | 182 | 181
2016-09-23 05:00 | 183 | 182
2016-09-23 05:30 | 188 | 187
2016-09-23 06:00 | 194 | 193
2016-09-23 06:30 | 203 | 202
2016-09-23 07:00 | 215 | 213
2016-09-23 07:30 | 230 | 228
2016-09-23 08:00 | 244 | 242
2016-09-23 08:30 | 249 | 247
2016-09-23 09:00 | 251 | 250
2016-09-23 09:30 | 256 | 254
2016-09-23 10:00 | 257 | 254
2016-09-23 10:30 | 254 | 251
2016-09-23 11:00 | 253 | 250
2016-09-23 11:30 | 256 | 253
2016-09-23 12:00 | 256 | 254
2016-09-23 12:30 | 257 | 254
2016-09-23 13:00 | 259 | 255
2016-09-23 13:30 | 258 | 255
2016-09-23 14:00 | 257 | 254
2016-09-23 14:30 | 256 | 252
2016-09-23 15:00 | 252 | 249
2016-09-23 15:30 | 250 | 246
2016-09-23 16:00 | 261 | 258
2016-09-23 16:30 | 265 | 262
2016-09-23 17:00 | 269 | 266
2016-09-23 17:30 | 272 | 268
2016-09-23 18:00 | 272 | 268
2016-09-23 18:30 | 273 | 269
2016-09-23 19:00 | 278 | 275
2016-09-23 19:30 | 287 | 283
2016-09-23 20:00 | 276 | 273
2016-09-23 20:30 | 279 | 276
2016-09-23 21:00 | 272 | 269
2016-09-23 21:30 | 264 | 260
2016-09-23 22:00 | 253 | 249
2016-09-23 22:30 | 246 | 241
2016-09-23 23:00 | 237 | 232
2016-09-23 23:30 | 225 | 220
2016-09-24 | 215 | 209
2016-09-24 00:30 | 209 | 203
2016-09-24 01:00 | 200 | 194
2016-09-24 01:30 | 195 | 189
2016-09-24 02:00 | 193 | 187
2016-09-24 02:30 | 188 | 182
2016-09-24 03:00 | 185 | 180
2016-09-24 03:30 | 182 | 178
2016-09-24 04:00 | 181 | 177
2016-09-24 04:30 | 182 | 177
2016-09-24 05:00 | 182 | 177
2016-09-24 05:30 | 187 | 183
2016-09-24 06:00 | 189 | 184
2016-09-24 06:30 | 187 | 182
2016-09-24 07:00 | 197 | 193
2016-09-24 07:30 | 207 | 204
2016-09-24 08:00 | 219 | 216
2016-09-24 08:30 | 239 | 236
2016-09-24 09:00 | 252 | 249
2016-09-24 09:30 | 251 | 248
2016-09-24 10:00 | 240 | 236
2016-09-24 10:30 | 234 | 230
2016-09-24 11:00 | 232 | 228
2016-09-24 11:30 | 231 | 228
2016-09-24 12:00 | 228 | 225
2016-09-24 12:30 | 231 | 228
2016-09-24 13:00 | 230 | 226
2016-09-24 13:30 | 230 | 226
2016-09-24 14:00 | 230 | 226
2016-09-24 14:30 | 221 | 217
2016-09-24 15:00 | 223 | 220
2016-09-24 15:30 | 231 | 228
2016-09-24 16:00 | 231 | 228
2016-09-24 16:30 | 238 | 235
2016-09-24 17:00 | 250 | 248
2016-09-24 17:30 | 259 | 257
2016-09-24 18:00 | 270 | 267
2016-09-24 18:30 | 271 | 268
2016-09-24 19:00 | 276 | 272
2016-09-24 19:30 | 286 | 282
2016-09-24 20:00 | 278 | 275
2016-09-24 20:30 | 271 | 267
2016-09-24 21:00 | 257 | 253
2016-09-24 21:30 | 252 | 248
2016-09-24 22:00 | 240 | 237
2016-09-24 22:30 | 232 | 228
2016-09-24 23:00 | 222 | 218
2016-09-24 23:30 | 210 | 205
2016-09-25 | 203 | 198
2016-09-25 00:30 | 199 | 194
2016-09-25 01:00 | 192 | 187
2016-09-25 01:30 | 189 | 184
2016-09-25 02:00 | 184 | 180
2016-09-25 02:30 | 179 | 176
2016-09-25 03:00 | 178 | 174
2016-09-25 03:30 | 177 | 174
2016-09-25 04:00 | 176 | 173
2016-09-25 04:30 | 179 | 176
2016-09-25 05:00 | 182 | 178
2016-09-25 05:30 | 181 | 177
2016-09-25 06:00 | 179 | 176
2016-09-25 06:30 | 180 | 176
2016-09-25 07:00 | 187 | 183
2016-09-25 07:30 | 195 | 192
2016-09-25 08:00 | 199 | 196
2016-09-25 08:30 | 202 | 199
2016-09-25 09:00 | 203 | 200
2016-09-25 09:30 | 209 | 206
2016-09-25 10:00 | 210 | 207
2016-09-25 10:30 | 213 | 210
2016-09-25 11:00 | 212 | 209
2016-09-25 11:30 | 214 | 211
2016-09-25 12:00 | 216 | 213
2016-09-25 12:30 | 219 | 215
2016-09-25 13:00 | 226 | 223
2016-09-25 13:30 | 228 | 224
2016-09-25 14:00 | 230 | 226
2016-09-25 14:30 | 220 | 216
2016-09-25 15:00 | 221 | 217
2016-09-25 15:30 | 230 | 226
2016-09-25 16:00 | 241 | 237
2016-09-25 16:30 | 247 | 244
2016-09-25 17:00 | 254 | 251
2016-09-25 17:30 | 260 | 257
2016-09-25 18:00 | 266 | 263
2016-09-25 18:30 | 275 | 272
2016-09-25 19:00 | 282 | 279
2016-09-25 19:30 | 285 | 282
2016-09-25 20:00 | 282 | 278
2016-09-25 20:30 | 294 | 290
2016-09-25 21:00 | 289 | 286
2016-09-25 21:30 | 270 | 267
2016-09-25 22:00 | 258 | 254
2016-09-25 22:30 | 244 | 240
2016-09-25 23:00 | 234 | 229
2016-09-25 23:30 | 227 | 222
2016-09-26 | 216 | 212
2016-09-26 00:30 | 210 | 206
2016-09-26 01:00 | 201 | 197
2016-09-26 01:30 | 195 | 190
2016-09-26 02:00 | 196 | 191
2016-09-26 02:30 | 194 | 189
2016-09-26 03:00 | 192 | 187
2016-09-26 03:30 | 193 | 188
2016-09-26 04:00 | 189 | 184
2016-09-26 04:30 | 188 | 182
2016-09-26 05:00 | 187 | 183
2016-09-26 05:30 | 195 | 191
2016-09-26 06:00 | 202 | 199
2016-09-26 06:30 | 216 | 212
2016-09-26 07:00 | 227 | 224
2016-09-26 07:30 | 241 | 238
2016-09-26 08:00 | 253 | 250
2016-09-26 08:30 | 262 | 259
2016-09-26 09:00 | 264 | 261
2016-09-26 09:30 | 265 | 262
2016-09-26 10:00 | 265 | 262
2016-09-26 10:30 | 265 | 262
2016-09-26 11:00 | 267 | 264
2016-09-26 11:30 | 271 | 268
2016-09-26 12:00 | 275 | 271
2016-09-26 12:30 | 284 | 281
2016-09-26 13:00 | 298 | 295
2016-09-26 13:30 | 303 | 300
2016-09-26 14:00 | 287 | 283
2016-09-26 14:30 | 286 | 282
2016-09-26 15:00 | 288 | 285
2016-09-26 15:30 | 292 | 288
2016-09-26 16:00 | 297 | 294
2016-09-26 16:30 | 299 | 296
2016-09-26 17:00 | 297 | 293
2016-09-26 17:30 | 305 | 302
2016-09-26 18:00 | 303 | 299
2016-09-26 18:30 | 318 | 315
2016-09-26 19:00 | 330 | 327
2016-09-26 19:30 | 335 | 332
2016-09-26 20:00 | 323 | 319
2016-09-26 20:30 | 310 | 305
2016-09-26 21:00 | 299 | 294
2016-09-26 21:30 | 293 | 289
2016-09-26 22:00 | 280 | 276
2016-09-26 22:30 | 265 | 260
2016-09-26 23:00 | 247 | 242
2016-09-26 23:30 | 235 | 232
2016-09-27 | 226 | 223
2016-09-27 00:30 | 220 | 217
2016-09-27 01:00 | 213 | 209
2016-09-27 01:30 | 208 | 203
2016-09-27 02:00 | 204 | 199
2016-09-27 02:30 | 201 | 196
2016-09-27 03:00 | 201 | 196
2016-09-27 03:30 | 200 | 195
2016-09-27 04:00 | 195 | 190
2016-09-27 04:30 | 194 | 188
2016-09-27 05:00 | 195 | 190
2016-09-27 05:30 | 204 | 199
2016-09-27 06:00 | 209 | 204
2016-09-27 06:30 | 212 | 208
2016-09-27 07:00 | 227 | 222
2016-09-27 07:30 | 254 | 249
2016-09-27 08:00 | 261 | 255
2016-09-27 08:30 | 269 | 265
2016-09-27 09:00 | 273 | 270
2016-09-27 09:30 | 278 | 274
2016-09-27 10:00 | 279 | 275
2016-09-27 10:30 | 276 | 273
2016-09-27 11:00 | 277 | 273
2016-09-27 11:30 | 286 | 283
2016-09-27 12:00 | 295 | 291
2016-09-27 12:30 | 294 | 289
2016-09-27 13:00 | 298 | 293
2016-09-27 13:30 | 302 | 298
2016-09-27 14:00 | 306 | 301
2016-09-27 14:30 | 291 | 286
2016-09-27 15:00 | 291 | 286
2016-09-27 15:30 | 295 | 290
2016-09-27 16:00 | 301 | 297
2016-09-27 16:30 | 308 | 304
2016-09-27 17:00 | 311 | 306
2016-09-27 17:30 | 309 | 304
2016-09-27 18:00 | 309 | 304
2016-09-27 18:30 | 314 | 309
2016-09-27 19:00 | 319 | 314
2016-09-27 19:30 | 336 | 332
2016-09-27 20:00 | 332 | 328
2016-09-27 20:30 | 317 | 312
2016-09-27 21:00 | 308 | 303
2016-09-27 21:30 | 293 | 287
2016-09-27 22:00 | 282 | 276
2016-09-27 22:30 | 261 | 256
2016-09-27 23:00 | 246 | 242
2016-09-27 23:30 | 233 | 228
2016-09-28 | 224 | 219
2016-09-28 00:30 | 216 | 211
2016-09-28 01:00 | 208 | 202
2016-09-28 01:30 | 203 | 197
2016-09-28 02:00 | 199 | 193
2016-09-28 02:30 | 200 | 194
2016-09-28 03:00 | 197 | 192
2016-09-28 03:30 | 198 | 193
2016-09-28 04:00 | 192 | 187
2016-09-28 04:30 | 195 | 190
2016-09-28 05:00 | 206 | 201
2016-09-28 05:30 | 213 | 208
2016-09-28 06:00 | 216 | 212
2016-09-28 06:30 | 226 | 222
2016-09-28 07:00 | 239 | 235
2016-09-28 07:30 | 256 | 252
2016-09-28 08:00 | 267 | 263
2016-09-28 08:30 | 274 | 270
2016-09-28 09:00 | 279 | 275
2016-09-28 09:30 | 281 | 276
2016-09-28 10:00 | 282 | 278
2016-09-28 10:30 | 281 | 277
2016-09-28 11:00 | 283 | 278
2016-09-28 11:30 | 281 | 276
2016-09-28 12:00 | 279 | 274
2016-09-28 12:30 | 280 | 275
2016-09-28 13:00 | 279 | 274
2016-09-28 13:30 | 283 | 278
2016-09-28 14:00 | 277 | 272
2016-09-28 14:30 | 278 | 273
2016-09-28 15:00 | 281 | 277
2016-09-28 15:30 | 286 | 282
2016-09-28 16:00 | 292 | 287
2016-09-28 16:30 | 297 | 292
2016-09-28 17:00 | 299 | 294
2016-09-28 17:30 | 295 | 290
2016-09-28 18:00 | 294 | 290
2016-09-28 18:30 | 321 | 317
2016-09-28 19:00 | 337 | 334
2016-09-28 19:30 | 332 | 328
2016-09-28 20:00 | 324 | 320
2016-09-28 20:30 | 317 | 312
2016-09-28 21:00 | 304 | 300
2016-09-28 21:30 | 296 | 290
2016-09-28 22:00 | 284 | 278
2016-09-28 22:30 | 252 | 246
2016-09-28 23:00 | 252 | 247
2016-09-28 23:30 | 245 | 241
2016-09-29 | 235 | 231
2016-09-29 00:30 | 223 | 219
2016-09-29 01:00 | 193 | 187
2016-09-29 01:30 | 184 | 178
2016-09-29 02:00 | 180 | 174
2016-09-29 02:30 | 175 | 169
2016-09-29 03:00 | 175 | 169
2016-09-29 03:30 | 180 | 174
2016-09-29 04:00 | 181 | 175
2016-09-29 04:30 | 170 | 164
2016-09-29 05:00 | 136 | 130
2016-09-29 05:30 | 145 | 140
2016-09-29 06:00 | 156 | 152
2016-09-29 06:30 | 159 | 156
2016-09-29 07:00 | 137 | 133
2016-09-29 07:30 | 153 | 149
2016-09-29 08:00 | 164 | 160
2016-09-29 08:30 | 177 | 173
2016-09-29 09:00 | 183 | 180
2016-09-29 09:30 | 177 | 174
2016-09-29 10:00 | 177 | 173
2016-09-29 10:30 | 176 | 173
2016-09-29 11:00 | 163 | 159
2016-09-29 11:30 | 159 | 155
2016-09-29 12:00 | 161 | 157
2016-09-29 12:30 | 163 | 159
2016-09-29 13:00 | 164 | 160
2016-09-29 13:30 | 168 | 164
2016-09-29 14:00 | 170 | 166
2016-09-29 14:30 | 159 | 153
2016-09-29 15:00 | 160 | 154
2016-09-29 15:30 | 161 | 155
2016-09-29 16:00 | 163 | 157
2016-09-29 16:30 | 164 | 158
2016-09-29 17:00 | 168 | 162
2016-09-29 17:30 | 168 | 162
2016-09-29 18:00 | 173 | 167
2016-09-29 18:30 | 198 | 194
2016-09-29 19:00 | 211 | 206
2016-09-29 19:30 | 207 | 203
2016-09-29 20:00 | 200 | 195
2016-09-29 20:30 | 190 | 185
2016-09-29 21:00 | 178 | 172
2016-09-29 21:30 | 156 | 151
2016-09-29 22:00 | 143 | 139
2016-09-29 22:30 | 126 | 122
2016-09-29 23:00 | 115 | 110
2016-09-29 23:30 | 106 | 101
2016-09-30 | 103 | 97
2016-09-30 00:30 | 134 | 131
2016-09-30 01:00 | 130 | 127
2016-09-30 01:30 | 127 | 124
2016-09-30 02:00 | 122 | 119
2016-09-30 02:30 | 120 | 117
2016-09-30 03:00 | 118 | 114
2016-09-30 03:30 | 124 | 120
2016-09-30 04:00 | 125 | 122
2016-09-30 04:30 | 124 | 121
2016-09-30 05:00 | 125 | 121
2016-09-30 05:30 | 122 | 118
2016-09-30 06:00 | 131 | 128
2016-09-30 06:30 | 145 | 142
2016-09-30 07:00 | 155 | 153
2016-09-30 07:30 | 175 | 173
2016-09-30 08:00 | 187 | 185
2016-09-30 08:30 | 192 | 190
2016-09-30 09:00 | 198 | 195
2016-09-30 09:30 | 203 | 201
2016-09-30 10:00 | 206 | 204
2016-09-30 10:30 | 206 | 203
2016-09-30 11:00 | 202 | 199
2016-09-30 11:30 | 199 | 197
2016-09-30 12:00 | 200 | 198
2016-09-30 12:30 | 204 | 202
2016-09-30 13:00 | 204 | 201
2016-09-30 13:30 | 203 | 201
2016-09-30 14:00 | 195 | 193
2016-09-30 14:30 | 193 | 191
2016-09-30 15:00 | 197 | 194
2016-09-30 15:30 | 205 | 203
2016-09-30 16:00 | 211 | 208
2016-09-30 16:30 | 171 | 168
2016-09-30 17:00 | 170 | 167
2016-09-30 17:30 | 175 | 172
2016-09-30 18:00 | 174 | 171
2016-09-30 18:30 | 181 | 178
2016-09-30 19:00 | 171 | 167
2016-09-30 19:30 | 188 | 185
2016-09-30 20:00 | 184 | 181
2016-09-30 20:30 | 174 | 170
2016-09-30 21:00 | 165 | 161
2016-09-30 21:30 | 155 | 151
2016-09-30 22:00 | 145 | 141
2016-09-30 22:30 | 131 | 127
2016-09-30 23:00 | 121 | 116
2016-09-30 23:30 | 112 | 107
2016-10-01 | 100 | 94
2016-10-01 00:30 | 126 | 122
2016-10-01 01:00 | 203 | 200
2016-10-01 01:30 | 203 | 200
2016-10-01 02:00 | 194 | 192
2016-10-01 02:30 | 191 | 188
2016-10-01 03:00 | 189 | 187
2016-10-01 03:30 | 188 | 185
2016-10-01 04:00 | 187 | 184
2016-10-01 04:30 | 187 | 184
2016-10-01 05:00 | 188 | 184
2016-10-01 05:30 | 190 | 187
2016-10-01 06:00 | 192 | 189
2016-10-01 06:30 | 195 | 192
2016-10-01 07:00 | 202 | 199
2016-10-01 07:30 | 214 | 212
2016-10-01 08:00 | 226 | 224
2016-10-01 08:30 | 238 | 236
2016-10-01 09:00 | 246 | 243
2016-10-01 09:30 | 242 | 240
2016-10-01 10:00 | 239 | 237
2016-10-01 10:30 | 239 | 236
2016-10-01 11:00 | 232 | 230
2016-10-01 11:30 | 225 | 222
2016-10-01 12:00 | 226 | 223
2016-10-01 12:30 | 218 | 216
2016-10-01 13:00 | 215 | 213
2016-10-01 13:30 | 217 | 214
2016-10-01 14:00 | 219 | 216
2016-10-01 14:30 | 224 | 222
2016-10-01 15:00 | 230 | 228
2016-10-01 15:30 | 234 | 232
2016-10-01 16:00 | 240 | 237
2016-10-01 16:30 | 241 | 239
2016-10-01 17:00 | 243 | 241
2016-10-01 17:30 | 244 | 241
2016-10-01 18:00 | 247 | 245
2016-10-01 18:30 | 256 | 254
2016-10-01 19:00 | 266 | 263
2016-10-01 19:30 | 262 | 259
2016-10-01 20:00 | 252 | 249
2016-10-01 20:30 | 240 | 237
2016-10-01 21:00 | 244 | 241
2016-10-01 21:30 | 243 | 239
2016-10-01 22:00 | 232 | 229
2016-10-01 22:30 | 225 | 222
2016-10-01 23:00 | 220 | 216
2016-10-01 23:30 | 209 | 205
2016-10-02 | 186 | 182
2016-10-02 00:30 | 192 | 189
2016-10-02 01:00 | 187 | 185
2016-10-02 01:30 | 182 | 180
2016-10-02 02:00 | 180 | 177
2016-10-02 02:30 | 177 | 174
2016-10-02 03:00 | 175 | 172
2016-10-02 03:30 | 171 | 168
2016-10-02 04:00 | 171 | 168
2016-10-02 04:30 | 171 | 168
2016-10-02 05:00 | 169 | 166
2016-10-02 05:30 | 171 | 168
2016-10-02 06:00 | 173 | 170
2016-10-02 06:30 | 174 | 171
2016-10-02 07:00 | 177 | 174
2016-10-02 07:30 | 186 | 183
2016-10-02 08:00 | 193 | 190
2016-10-02 08:30 | 203 | 201
2016-10-02 09:00 | 207 | 204
2016-10-02 09:30 | 214 | 211
2016-10-02 10:00 | 215 | 212
2016-10-02 10:30 | 218 | 215
2016-10-02 11:00 | 223 | 220
2016-10-02 11:30 | 219 | 216
2016-10-02 12:00 | 216 | 214
2016-10-02 12:30 | 211 | 208
2016-10-02 13:00 | 198 | 195
2016-10-02 13:30 | 195 | 193
2016-10-02 14:00 | 196 | 194
2016-10-02 14:30 | 202 | 200
2016-10-02 15:00 | 209 | 206
2016-10-02 15:30 | 213 | 211
2016-10-02 16:00 | 220 | 217
2016-10-02 16:30 | 227 | 225
2016-10-02 17:00 | 233 | 230
2016-10-02 17:30 | 244 | 241
2016-10-02 18:00 | 266 | 263
2016-10-02 18:30 | 276 | 273
2016-10-02 19:00 | 288 | 285
2016-10-02 19:30 | 285 | 282
2016-10-02 20:00 | 273 | 271
2016-10-02 20:30 | 260 | 257
2016-10-02 21:00 | 252 | 248
2016-10-02 21:30 | 247 | 243
2016-10-02 22:00 | 237 | 233
2016-10-02 22:30 | 225 | 221
2016-10-02 23:00 | 216 | 212
2016-10-02 23:30 | 206 | 202
2016-10-03 | 198 | 194
2016-10-03 00:30 | 193 | 189
2016-10-03 01:00 | 185 | 180
2016-10-03 01:30 | 181 | 176
2016-10-03 02:00 | 177 | 173
2016-10-03 02:30 | 172 | 168
2016-10-03 03:00 | 170 | 167
2016-10-03 03:30 | 170 | 167
2016-10-03 04:00 | 170 | 167
2016-10-03 04:30 | 171 | 169
2016-10-03 05:00 | 173 | 170
2016-10-03 05:30 | 173 | 170
2016-10-03 06:00 | 174 | 172
2016-10-03 06:30 | 177 | 174
2016-10-03 07:00 | 180 | 177
2016-10-03 07:30 | 183 | 181
2016-10-03 08:00 | 189 | 187
2016-10-03 08:30 | 198 | 195
2016-10-03 09:00 | 201 | 199
2016-10-03 09:30 | 208 | 205
2016-10-03 10:00 | 207 | 204
2016-10-03 10:30 | 206 | 203
2016-10-03 11:00 | 211 | 208
2016-10-03 11:30 | 212 | 209
2016-10-03 12:00 | 214 | 212
2016-10-03 12:30 | 216 | 213
2016-10-03 13:00 | 217 | 214
2016-10-03 13:30 | 212 | 209
2016-10-03 14:00 | 220 | 218
2016-10-03 14:30 | 222 | 219
2016-10-03 15:00 | 228 | 226
2016-10-03 15:30 | 238 | 235
2016-10-03 16:00 | 242 | 239
2016-10-03 16:30 | 246 | 243
2016-10-03 17:00 | 268 | 266
2016-10-03 17:30 | 280 | 278
2016-10-03 18:00 | 272 | 269
2016-10-03 18:30 | 278 | 274
2016-10-03 19:00 | 306 | 303
2016-10-03 19:30 | 308 | 306
2016-10-03 20:00 | 299 | 296
2016-10-03 20:30 | 274 | 270
2016-10-03 21:00 | 275 | 271
2016-10-03 21:30 | 264 | 260
2016-10-03 22:00 | 250 | 246
2016-10-03 22:30 | 220 | 216
2016-10-03 23:00 | 216 | 212
2016-10-03 23:30 | 210 | 206
2016-10-04 | 202 | 199
2016-10-04 00:30 | 197 | 194
2016-10-04 01:00 | 189 | 186
2016-10-04 01:30 | 186 | 183
2016-10-04 02:00 | 182 | 180
2016-10-04 02:30 | 179 | 177
2016-10-04 03:00 | 180 | 178
2016-10-04 03:30 | 182 | 179
2016-10-04 04:00 | 180 | 177
2016-10-04 04:30 | 184 | 181
2016-10-04 05:00 | 188 | 185
2016-10-04 05:30 | 192 | 190
2016-10-04 06:00 | 194 | 192
2016-10-04 06:30 | 209 | 206
2016-10-04 07:00 | 212 | 209
2016-10-04 07:30 | 245 | 243
2016-10-04 08:00 | 256 | 254
2016-10-04 08:30 | 260 | 258
2016-10-04 09:00 | 261 | 259
2016-10-04 09:30 | 265 | 263
2016-10-04 10:00 | 262 | 260
2016-10-04 10:30 | 253 | 251
2016-10-04 11:00 | 252 | 249
2016-10-04 11:30 | 250 | 248
2016-10-04 12:00 | 256 | 254
2016-10-04 12:30 | 259 | 257
2016-10-04 13:00 | 258 | 256
2016-10-04 13:30 | 248 | 245
2016-10-04 14:00 | 247 | 244
2016-10-04 14:30 | 251 | 249
2016-10-04 15:00 | 257 | 254
2016-10-04 15:30 | 260 | 257
2016-10-04 16:00 | 269 | 266
2016-10-04 16:30 | 281 | 278
2016-10-04 17:00 | 284 | 282
2016-10-04 17:30 | 281 | 279
2016-10-04 18:00 | 276 | 273
2016-10-04 18:30 | 285 | 282
2016-10-04 19:00 | 298 | 296
2016-10-04 19:30 | 295 | 292
2016-10-04 20:00 | 284 | 282
2016-10-04 20:30 | 273 | 270
2016-10-04 21:00 | 277 | 274
2016-10-04 21:30 | 272 | 269
2016-10-04 22:00 | 255 | 251
2016-10-04 22:30 | 240 | 236
2016-10-04 23:00 | 229 | 224
2016-10-04 23:30 | 218 | 215
2016-10-05 | 211 | 207
2016-10-05 00:30 | 211 | 207
2016-10-05 01:00 | 206 | 202
2016-10-05 01:30 | 200 | 195
2016-10-05 02:00 | 191 | 187
2016-10-05 02:30 | 183 | 180
2016-10-05 03:00 | 181 | 177
2016-10-05 03:30 | 174 | 170
2016-10-05 04:00 | 176 | 172
2016-10-05 04:30 | 172 | 168
2016-10-05 05:00 | 172 | 169
2016-10-05 05:30 | 181 | 178
2016-10-05 06:00 | 186 | 183
2016-10-05 06:30 | 206 | 203
2016-10-05 07:00 | 209 | 207
2016-10-05 07:30 | 239 | 237
2016-10-05 08:00 | 252 | 249
2016-10-05 08:30 | 256 | 254
2016-10-05 09:00 | 258 | 256
2016-10-05 09:30 | 265 | 263
2016-10-05 10:00 | 261 | 259
2016-10-05 10:30 | 258 | 255
2016-10-05 11:00 | 257 | 255
2016-10-05 11:30 | 253 | 252
2016-10-05 12:00 | 252 | 250
2016-10-05 12:30 | 255 | 253
2016-10-05 13:00 | 256 | 254
2016-10-05 13:30 | 243 | 241
2016-10-05 14:00 | 229 | 226
2016-10-05 14:30 | 229 | 226
2016-10-05 15:00 | 227 | 224
2016-10-05 15:30 | 223 | 220
2016-10-05 16:00 | 175 | 172
2016-10-05 16:30 | 143 | 139
2016-10-05 17:00 | 133 | 129
2016-10-05 17:30 | 148 | 144
2016-10-05 18:00 | 152 | 148
2016-10-05 18:30 | 162 | 159
2016-10-05 19:00 | 168 | 165
2016-10-05 19:30 | 164 | 161
2016-10-05 20:00 | 158 | 154
2016-10-05 20:30 | 168 | 165
2016-10-05 21:00 | 175 | 172
2016-10-05 21:30 | 170 | 167
2016-10-05 22:00 | 188 | 186
2016-10-05 22:30 | 128 | 124
2016-10-05 23:00 | 120 | 116
2016-10-05 23:30 | 102 | 98
2016-10-06 | 97 | 94
2016-10-06 00:30 | 98 | 95
2016-10-06 01:00 | 103 | 101
2016-10-06 01:30 | 166 | 164
2016-10-06 02:00 | 165 | 162
2016-10-06 02:30 | 162 | 160
2016-10-06 03:00 | 159 | 157
2016-10-06 03:30 | 159 | 156
2016-10-06 04:00 | 155 | 152
2016-10-06 04:30 | 155 | 152
2016-10-06 05:00 | 150 | 147
2016-10-06 05:30 | 138 | 134
2016-10-06 06:00 | 148 | 144
2016-10-06 06:30 | 166 | 162
2016-10-06 07:00 | 188 | 185
2016-10-06 07:30 | 216 | 214
2016-10-06 08:00 | 226 | 224
2016-10-06 08:30 | 230 | 228
2016-10-06 09:00 | 230 | 228
2016-10-06 09:30 | 218 | 216
2016-10-06 10:00 | 217 | 215
2016-10-06 10:30 | 218 | 216
2016-10-06 11:00 | 217 | 215
2016-10-06 11:30 | 219 | 217
2016-10-06 12:00 | 222 | 220
2016-10-06 12:30 | 213 | 211
2016-10-06 13:00 | 220 | 218
2016-10-06 13:30 | 215 | 212
2016-10-06 14:00 | 210 | 207
2016-10-06 14:30 | 218 | 216
2016-10-06 15:00 | 224 | 222
2016-10-06 15:30 | 221 | 218
2016-10-06 16:00 | 223 | 221
2016-10-06 16:30 | 226 | 224
2016-10-06 17:00 | 237 | 235
2016-10-06 17:30 | 236 | 234
2016-10-06 18:00 | 262 | 261
2016-10-06 18:30 | 288 | 286
2016-10-06 19:00 | 306 | 303
2016-10-06 19:30 | 305 | 302
2016-10-06 20:00 | 283 | 280
2016-10-06 20:30 | 273 | 270
2016-10-06 21:00 | 263 | 259
2016-10-06 21:30 | 245 | 242
2016-10-06 22:00 | 233 | 229
2016-10-06 22:30 | 215 | 211
2016-10-06 23:00 | 199 | 195
2016-10-06 23:30 | 187 | 183
2016-10-07 | 179 | 177
2016-10-07 00:30 | 174 | 171
2016-10-07 01:00 | 166 | 164
2016-10-07 01:30 | 161 | 158
2016-10-07 02:00 | 159 | 156
2016-10-07 02:30 | 154 | 152
2016-10-07 03:00 | 152 | 150
2016-10-07 03:30 | 151 | 148
2016-10-07 04:00 | 150 | 148
2016-10-07 04:30 | 156 | 153
2016-10-07 05:00 | 156 | 154
2016-10-07 05:30 | 164 | 162
2016-10-07 06:00 | 170 | 168
2016-10-07 06:30 | 187 | 185
2016-10-07 07:00 | 202 | 200
2016-10-07 07:30 | 217 | 215
2016-10-07 08:00 | 225 | 223
2016-10-07 08:30 | 229 | 227
2016-10-07 09:00 | 232 | 230
2016-10-07 09:30 | 231 | 229
2016-10-07 10:00 | 227 | 224
2016-10-07 10:30 | 224 | 221
2016-10-07 11:00 | 217 | 214
2016-10-07 11:30 | 217 | 214
2016-10-07 12:00 | 219 | 216
2016-10-07 12:30 | 220 | 217
2016-10-07 13:00 | 218 | 215
2016-10-07 13:30 | 207 | 204
2016-10-07 14:00 | 204 | 202
2016-10-07 14:30 | 207 | 205
2016-10-07 15:00 | 180 | 176
2016-10-07 15:30 | 132 | 128
2016-10-07 16:00 | 136 | 132
2016-10-07 16:30 | 144 | 141
2016-10-07 17:00 | 150 | 147
2016-10-07 17:30 | 156 | 153
2016-10-07 18:00 | 156 | 152
2016-10-07 18:30 | 165 | 162
2016-10-07 19:00 | 179 | 176
2016-10-07 19:30 | 170 | 167
2016-10-07 20:00 | 158 | 155
2016-10-07 20:30 | 162 | 159
2016-10-07 21:00 | 156 | 153
2016-10-07 21:30 | 145 | 142
2016-10-07 22:00 | 136 | 132
2016-10-07 22:30 | 123 | 118
2016-10-07 23:00 | 114 | 110
2016-10-07 23:30 | 105 | 100
2016-10-08 | 98 | 93
2016-10-08 00:30 | 129 | 125
2016-10-08 01:00 | 159 | 156
2016-10-08 01:30 | 164 | 161
2016-10-08 02:00 | 160 | 157
2016-10-08 02:30 | 146 | 143
2016-10-08 03:00 | 137 | 135
2016-10-08 03:30 | 140 | 139
2016-10-08 04:00 | 136 | 135
2016-10-08 04:30 | 128 | 125
2016-10-08 05:00 | 133 | 131
2016-10-08 05:30 | 142 | 140
2016-10-08 06:00 | 145 | 143
2016-10-08 06:30 | 146 | 144
2016-10-08 07:00 | 153 | 151
2016-10-08 07:30 | 164 | 163
2016-10-08 08:00 | 174 | 172
2016-10-08 08:30 | 184 | 182
2016-10-08 09:00 | 187 | 184
2016-10-08 09:30 | 192 | 190
2016-10-08 10:00 | 191 | 190
2016-10-08 10:30 | 188 | 186
2016-10-08 11:00 | 187 | 185
2016-10-08 11:30 | 185 | 183
2016-10-08 12:00 | 186 | 184
2016-10-08 12:30 | 184 | 182
2016-10-08 13:00 | 186 | 184
2016-10-08 13:30 | 184 | 182
2016-10-08 14:00 | 182 | 180
2016-10-08 14:30 | 182 | 180
2016-10-08 15:00 | 177 | 176
2016-10-08 15:30 | 181 | 180
2016-10-08 16:00 | 190 | 189
2016-10-08 16:30 | 199 | 197
2016-10-08 17:00 | 212 | 211
2016-10-08 17:30 | 220 | 219
2016-10-08 18:00 | 232 | 230
2016-10-08 18:30 | 243 | 241
2016-10-08 19:00 | 255 | 253
2016-10-08 19:30 | 252 | 251
2016-10-08 20:00 | 241 | 240
2016-10-08 20:30 | 244 | 242
2016-10-08 21:00 | 239 | 238
2016-10-08 21:30 | 229 | 227
2016-10-08 22:00 | 215 | 213
2016-10-08 22:30 | 203 | 201
2016-10-08 23:00 | 195 | 193
2016-10-08 23:30 | 186 | 184
2016-10-09 | 176 | 174
2016-10-09 00:30 | 174 | 172
2016-10-09 01:00 | 166 | 164
2016-10-09 01:30 | 156 | 154
2016-10-09 02:00 | 149 | 148
2016-10-09 02:30 | 148 | 146
2016-10-09 03:00 | 148 | 147
2016-10-09 03:30 | 148 | 146
2016-10-09 04:00 | 147 | 146
2016-10-09 04:30 | 146 | 145
2016-10-09 05:00 | 145 | 143
2016-10-09 05:30 | 148 | 146
2016-10-09 06:00 | 148 | 147
2016-10-09 06:30 | 149 | 147
2016-10-09 07:00 | 152 | 150
2016-10-09 07:30 | 158 | 156
2016-10-09 08:00 | 165 | 164
2016-10-09 08:30 | 172 | 170
2016-10-09 09:00 | 177 | 175
2016-10-09 09:30 | 181 | 180
2016-10-09 10:00 | 183 | 181
2016-10-09 10:30 | 184 | 182
2016-10-09 11:00 | 181 | 179
2016-10-09 11:30 | 181 | 179
2016-10-09 12:00 | 180 | 179
2016-10-09 12:30 | 181 | 179
2016-10-09 13:00 | 184 | 182
2016-10-09 13:30 | 180 | 178
2016-10-09 14:00 | 173 | 172
2016-10-09 14:30 | 174 | 172
2016-10-09 15:00 | 180 | 178
2016-10-09 15:30 | 188 | 187
2016-10-09 16:00 | 198 | 197
2016-10-09 16:30 | 209 | 207
2016-10-09 17:00 | 216 | 215
2016-10-09 17:30 | 228 | 226
2016-10-09 18:00 | 237 | 235
2016-10-09 18:30 | 263 | 262
2016-10-09 19:00 | 280 | 279
2016-10-09 19:30 | 279 | 277
2016-10-09 20:00 | 267 | 265
2016-10-09 20:30 | 253 | 251
2016-10-09 21:00 | 245 | 243
2016-10-09 21:30 | 233 | 231
2016-10-09 22:00 | 219 | 217
2016-10-09 22:30 | 203 | 201
2016-10-09 23:00 | 190 | 188
2016-10-09 23:30 | 181 | 180
2016-10-10 | 174 | 172
2016-10-10 00:30 | 164 | 162
2016-10-10 01:00 | 131 | 129
2016-10-10 01:30 | 122 | 120
2016-10-10 02:00 | 117 | 115
2016-10-10 02:30 | 118 | 116
2016-10-10 03:00 | 116 | 114
2016-10-10 03:30 | 117 | 115
2016-10-10 04:00 | 119 | 117
2016-10-10 04:30 | 111 | 109
2016-10-10 05:00 | 72 | 70
2016-10-10 05:30 | 75 | 73
2016-10-10 06:00 | 90 | 88
2016-10-10 06:30 | 102 | 100
2016-10-10 07:00 | 83 | 81
2016-10-10 07:30 | 126 | 124
2016-10-10 08:00 | 132 | 130
2016-10-10 08:30 | 151 | 150
2016-10-10 09:00 | 149 | 148
2016-10-10 09:30 | 183 | 182
2016-10-10 10:00 | 240 | 239
2016-10-10 10:30 | 236 | 235
2016-10-10 11:00 | 227 | 225
2016-10-10 11:30 | 232 | 230
2016-10-10 12:00 | 241 | 240
2016-10-10 12:30 | 237 | 235
2016-10-10 13:00 | 225 | 224
2016-10-10 13:30 | 226 | 224
2016-10-10 14:00 | 159 | 157
2016-10-10 14:30 | 177 | 175
2016-10-10 15:00 | 141 | 140
2016-10-10 15:30 | 146 | 145
2016-10-10 16:00 | 164 | 162
2016-10-10 16:30 | 176 | 174
2016-10-10 17:00 | 186 | 184
2016-10-10 17:30 | 187 | 185
2016-10-10 18:00 | 192 | 189
2016-10-10 18:30 | 205 | 203
2016-10-10 19:00 | 230 | 228
2016-10-10 19:30 | 223 | 221
2016-10-10 20:00 | 199 | 197
2016-10-10 20:30 | 206 | 204
2016-10-10 21:00 | 193 | 191
2016-10-10 21:30 | 170 | 168
2016-10-10 22:00 | 232 | 230
2016-10-10 22:30 | 143 | 141
2016-10-10 23:00 | 111 | 108
2016-10-10 23:30 | 103 | 99
2016-10-11 | 111 | 107
2016-10-11 00:30 | 174 | 171
2016-10-11 01:00 | 163 | 160
2016-10-11 01:30 | 153 | 151
2016-10-11 02:00 | 149 | 147
2016-10-11 02:30 | 149 | 146
2016-10-11 03:00 | 133 | 130
2016-10-11 03:30 | 134 | 131
2016-10-11 04:00 | 133 | 130
2016-10-11 04:30 | 131 | 129
2016-10-11 05:00 | 112 | 109
2016-10-11 05:30 | 64 | 59
2016-10-11 06:00 | 39 | 34
2016-10-11 06:30 | 43 | 38
2016-10-11 07:00 | 69 | 63
2016-10-11 07:30 | 107 | 104
2016-10-11 08:00 | 114 | 110
2016-10-11 08:30 | 136 | 133
2016-10-11 09:00 | 109 | 106
2016-10-11 09:30 | 100 | 96
2016-10-11 10:00 | 103 | 100
2016-10-11 10:30 | 162 | 160
2016-10-11 11:00 | 185 | 182
2016-10-11 11:30 | 187 | 184
2016-10-11 12:00 | 190 | 187
2016-10-11 12:30 | 196 | 194
2016-10-11 13:00 | 193 | 191
2016-10-11 13:30 | 179 | 177
2016-10-11 14:00 | 177 | 175
2016-10-11 14:30 | 186 | 184
2016-10-11 15:00 | 194 | 192
2016-10-11 15:30 | 197 | 195
2016-10-11 16:00 | 206 | 204
2016-10-11 16:30 | 218 | 216
2016-10-11 17:00 | 241 | 239
2016-10-11 17:30 | 236 | 234
2016-10-11 18:00 | 229 | 226
2016-10-11 18:30 | 210 | 207
2016-10-11 19:00 | 201 | 198
2016-10-11 19:30 | 195 | 192
2016-10-11 20:00 | 245 | 243
2016-10-11 20:30 | 314 | 313
2016-10-11 21:00 | 305 | 303
2016-10-11 21:30 | 297 | 296
2016-10-11 22:00 | 282 | 280
2016-10-11 22:30 | 211 | 208
2016-10-11 23:00 | 202 | 200
2016-10-11 23:30 | 195 | 192
2016-10-12 | 196 | 194
2016-10-12 00:30 | 193 | 191
2016-10-12 01:00 | 185 | 183
2016-10-12 01:30 | 173 | 171
2016-10-12 02:00 | 170 | 168
2016-10-12 02:30 | 164 | 161
2016-10-12 03:00 | 164 | 162
2016-10-12 03:30 | 162 | 160
2016-10-12 04:00 | 159 | 157
2016-10-12 04:30 | 160 | 157
2016-10-12 05:00 | 170 | 167
2016-10-12 05:30 | 187 | 185
2016-10-12 06:00 | 182 | 179
2016-10-12 06:30 | 198 | 196
2016-10-12 07:00 | 183 | 181
2016-10-12 07:30 | 225 | 223
2016-10-12 08:00 | 259 | 257
2016-10-12 08:30 | 255 | 254
2016-10-12 09:00 | 248 | 246
2016-10-12 09:30 | 251 | 250
2016-10-12 10:00 | 248 | 246
2016-10-12 10:30 | 247 | 246
2016-10-12 11:00 | 256 | 255
2016-10-12 11:30 | 264 | 262
2016-10-12 12:00 | 270 | 269
2016-10-12 12:30 | 283 | 282
2016-10-12 13:00 | 285 | 284
2016-10-12 13:30 | 265 | 263
2016-10-12 14:00 | 262 | 260
2016-10-12 14:30 | 263 | 262
2016-10-12 15:00 | 271 | 270
2016-10-12 15:30 | 268 | 266
2016-10-12 16:00 | 283 | 280
2016-10-12 16:30 | 292 | 290
2016-10-12 17:00 | 299 | 297
2016-10-12 17:30 | 293 | 291
2016-10-12 18:00 | 225 | 223
2016-10-12 18:30 | 211 | 208
2016-10-12 19:00 | 231 | 229
2016-10-12 19:30 | 237 | 235
2016-10-12 20:00 | 253 | 251
2016-10-12 20:30 | 261 | 259
2016-10-12 21:00 | 312 | 310
2016-10-12 21:30 | 294 | 292
2016-10-12 22:00 | 267 | 265
2016-10-12 22:30 | 240 | 239
2016-10-12 23:00 | 206 | 204
2016-10-12 23:30 | 190 | 189
2016-10-13 | 181 | 180
2016-10-13 00:30 | 177 | 176
2016-10-13 01:00 | 168 | 167
2016-10-13 01:30 | 160 | 159
2016-10-13 02:00 | 157 | 156
2016-10-13 02:30 | 157 | 156
2016-10-13 03:00 | 152 | 151
2016-10-13 03:30 | 151 | 151
2016-10-13 04:00 | 156 | 155
2016-10-13 04:30 | 165 | 164
2016-10-13 05:00 | 159 | 159
2016-10-13 05:30 | 156 | 156
2016-10-13 06:00 | 163 | 162
2016-10-13 06:30 | 191 | 191
2016-10-13 07:00 | 155 | 154
2016-10-13 07:30 | 223 | 223
2016-10-13 08:00 | 282 | 282
2016-10-13 08:30 | 285 | 285
2016-10-13 09:00 | 289 | 289
2016-10-13 09:30 | 277 | 277
2016-10-13 10:00 | 282 | 282
2016-10-13 10:30 | 302 | 302
2016-10-13 11:00 | 299 | 298
2016-10-13 11:30 | 299 | 298
2016-10-13 12:00 | 300 | 300
2016-10-13 12:30 | 302 | 302
2016-10-13 13:00 | 300 | 300
2016-10-13 13:30 | 286 | 285
2016-10-13 14:00 | 286 | 286
2016-10-13 14:30 | 306 | 306
2016-10-13 15:00 | 303 | 302
2016-10-13 15:30 | 294 | 293
2016-10-13 16:00 | 287 | 286
2016-10-13 16:30 | 283 | 281
2016-10-13 17:00 | 302 | 301
2016-10-13 17:30 | 240 | 239
2016-10-13 18:00 | 219 | 217
2016-10-13 18:30 | 231 | 230
2016-10-13 19:00 | 249 | 248
2016-10-13 19:30 | 245 | 245
2016-10-13 20:00 | 249 | 248
2016-10-13 20:30 | 238 | 237
2016-10-13 21:00 | 296 | 295
2016-10-13 21:30 | 293 | 292
2016-10-13 22:00 | 271 | 270
2016-10-13 22:30 | 212 | 211
2016-10-13 23:00 | 196 | 194
2016-10-13 23:30 | 179 | 178
2016-10-14 | 160 | 158
2016-10-14 00:30 | 156 | 154
2016-10-14 01:00 | 155 | 154
2016-10-14 01:30 | 155 | 155
2016-10-14 02:00 | 153 | 152
2016-10-14 02:30 | 145 | 145
2016-10-14 03:00 | 148 | 148
2016-10-14 03:30 | 150 | 150
2016-10-14 04:00 | 148 | 147
2016-10-14 04:30 | 154 | 153
2016-10-14 05:00 | 152 | 151
2016-10-14 05:30 | 143 | 143
2016-10-14 06:00 | 143 | 142
2016-10-14 06:30 | 139 | 138
2016-10-14 07:00 | 155 | 154
2016-10-14 07:30 | 213 | 213
2016-10-14 08:00 | 257 | 256
2016-10-14 08:30 | 258 | 258
2016-10-14 09:00 | 260 | 260
2016-10-14 09:30 | 268 | 267
2016-10-14 10:00 | 258 | 258
2016-10-14 10:30 | 302 | 301
2016-10-14 11:00 | 367 | 367
2016-10-14 11:30 | 379 | 378
2016-10-14 12:00 | 376 | 376
2016-10-14 12:30 | 390 | 389
2016-10-14 13:00 | 389 | 389
2016-10-14 13:30 | 374 | 373
2016-10-14 14:00 | 376 | 375
2016-10-14 14:30 | 386 | 386
2016-10-14 15:00 | 395 | 395
2016-10-14 15:30 | 392 | 391
2016-10-14 16:00 | 387 | 387
2016-10-14 16:30 | 386 | 385
2016-10-14 17:00 | 383 | 382
2016-10-14 17:30 | 381 | 380
2016-10-14 18:00 | 380 | 380
2016-10-14 18:30 | 403 | 403
2016-10-14 19:00 | 426 | 425
2016-10-14 19:30 | 425 | 425
2016-10-14 20:00 | 436 | 436
2016-10-14 20:30 | 415 | 415
2016-10-14 21:00 | 415 | 415
2016-10-14 21:30 | 404 | 403
2016-10-14 22:00 | 389 | 388
2016-10-14 22:30 | 323 | 323
2016-10-14 23:00 | 306 | 306
2016-10-14 23:30 | 303 | 303
2016-10-15 | 308 | 307
2016-10-15 00:30 | 311 | 310
2016-10-15 01:00 | 293 | 293
2016-10-15 01:30 | 289 | 289
2016-10-15 02:00 | 286 | 286
2016-10-15 02:30 | 283 | 283
2016-10-15 03:00 | 278 | 278
2016-10-15 03:30 | 275 | 274
2016-10-15 04:00 | 277 | 277
2016-10-15 04:30 | 289 | 288
2016-10-15 05:00 | 294 | 293
2016-10-15 05:30 | 298 | 298
2016-10-15 06:00 | 307 | 307
2016-10-15 06:30 | 321 | 321
2016-10-15 07:00 | 311 | 310
2016-10-15 07:30 | 337 | 337
2016-10-15 08:00 | 373 | 373
2016-10-15 08:30 | 391 | 390
2016-10-15 09:00 | 404 | 404
2016-10-15 09:30 | 401 | 401
2016-10-15 10:00 | 396 | 396
2016-10-15 10:30 | 393 | 392
2016-10-15 11:00 | 381 | 381
2016-10-15 11:30 | 382 | 382
2016-10-15 12:00 | 378 | 377
2016-10-15 12:30 | 381 | 381
2016-10-15 13:00 | 384 | 384
2016-10-15 13:30 | 370 | 370
2016-10-15 14:00 | 361 | 361
2016-10-15 14:30 | 358 | 358
2016-10-15 15:00 | 355 | 355
2016-10-15 15:30 | 361 | 361
2016-10-15 16:00 | 358 | 357
2016-10-15 16:30 | 369 | 368
2016-10-15 17:00 | 411 | 411
2016-10-15 17:30 | 440 | 439
2016-10-15 18:00 | 443 | 443
2016-10-15 18:30 | 443 | 443
2016-10-15 19:00 | 411 | 410
2016-10-15 19:30 | 415 | 415
2016-10-15 20:00 | 434 | 434
2016-10-15 20:30 | 437 | 437
2016-10-15 21:00 | 432 | 432
2016-10-15 21:30 | 420 | 419
2016-10-15 22:00 | 410 | 409
2016-10-15 22:30 | 386 | 386
2016-10-15 23:00 | 372 | 372
2016-10-15 23:30 | 354 | 354
2016-10-16 | 342 | 342
2016-10-16 00:30 | 330 | 329
2016-10-16 01:00 | 322 | 322
2016-10-16 01:30 | 317 | 317
2016-10-16 02:00 | 309 | 309
2016-10-16 02:30 | 305 | 304
2016-10-16 03:00 | 306 | 306
2016-10-16 03:30 | 297 | 297
2016-10-16 04:00 | 286 | 286
2016-10-16 04:30 | 283 | 283
2016-10-16 05:00 | 284 | 284
2016-10-16 05:30 | 296 | 296
2016-10-16 06:00 | 297 | 297
2016-10-16 06:30 | 305 | 304
2016-10-16 07:00 | 314 | 313
2016-10-16 07:30 | 323 | 323
2016-10-16 08:00 | 332 | 332
2016-10-16 08:30 | 366 | 366
2016-10-16 09:00 | 380 | 380
2016-10-16 09:30 | 372 | 372
2016-10-16 10:00 | 375 | 375
2016-10-16 10:30 | 378 | 378
2016-10-16 11:00 | 372 | 372
2016-10-16 11:30 | 367 | 366
2016-10-16 12:00 | 371 | 371
2016-10-16 12:30 | 360 | 359
2016-10-16 13:00 | 332 | 332
2016-10-16 13:30 | 330 | 330
2016-10-16 14:00 | 338 | 338
2016-10-16 14:30 | 347 | 346
2016-10-16 15:00 | 346 | 346
2016-10-16 15:30 | 358 | 357
2016-10-16 16:00 | 363 | 363
2016-10-16 16:30 | 366 | 365
2016-10-16 17:00 | 382 | 382
2016-10-16 17:30 | 394 | 394
2016-10-16 18:00 | 410 | 410
2016-10-16 18:30 | 396 | 396
2016-10-16 19:00 | 444 | 443
2016-10-16 19:30 | 456 | 455
2016-10-16 20:00 | 460 | 460
2016-10-16 20:30 | 439 | 439
2016-10-16 21:00 | 430 | 430
2016-10-16 21:30 | 412 | 411
2016-10-16 22:00 | 395 | 395
2016-10-16 22:30 | 373 | 372
2016-10-16 23:00 | 352 | 351
2016-10-16 23:30 | 336 | 335
2016-10-17 | 319 | 318
2016-10-17 00:30 | 311 | 311
2016-10-17 01:00 | 296 | 296
2016-10-17 01:30 | 284 | 284
2016-10-17 02:00 | 279 | 279
2016-10-17 02:30 | 276 | 275
2016-10-17 03:00 | 276 | 275
2016-10-17 03:30 | 272 | 271
2016-10-17 04:00 | 277 | 277
2016-10-17 04:30 | 281 | 280
2016-10-17 05:00 | 287 | 286
2016-10-17 05:30 | 296 | 295
2016-10-17 06:00 | 303 | 302
2016-10-17 06:30 | 324 | 323
2016-10-17 07:00 | 342 | 341
2016-10-17 07:30 | 374 | 374
2016-10-17 08:00 | 395 | 394
2016-10-17 08:30 | 407 | 407
2016-10-17 09:00 | 410 | 409
2016-10-17 09:30 | 412 | 411
2016-10-17 10:00 | 400 | 399
2016-10-17 10:30 | 388 | 386
2016-10-17 11:00 | 389 | 388
2016-10-17 11:30 | 392 | 390
2016-10-17 12:00 | 389 | 388
2016-10-17 12:30 | 402 | 401
2016-10-17 13:00 | 409 | 408
2016-10-17 13:30 | 384 | 383
2016-10-17 14:00 | 375 | 373
2016-10-17 14:30 | 389 | 388
2016-10-17 15:00 | 403 | 402
2016-10-17 15:30 | 409 | 408
2016-10-17 16:00 | 421 | 420
2016-10-17 16:30 | 432 | 431
2016-10-17 17:00 | 436 | 435
2016-10-17 17:30 | 430 | 429
2016-10-17 18:00 | 433 | 432
2016-10-17 18:30 | 447 | 446
2016-10-17 19:00 | 453 | 452
2016-10-17 19:30 | 473 | 472
2016-10-17 20:00 | 475 | 475
2016-10-17 20:30 | 453 | 452
2016-10-17 21:00 | 436 | 435
2016-10-17 21:30 | 419 | 418
2016-10-17 22:00 | 398 | 396
2016-10-17 22:30 | 353 | 352
2016-10-17 23:00 | 339 | 338
2016-10-17 23:30 | 319 | 318
2016-10-18 | 317 | 316
2016-10-18 00:30 | 303 | 303
2016-10-18 01:00 | 302 | 302
2016-10-18 01:30 | 295 | 294
2016-10-18 02:00 | 293 | 292
2016-10-18 02:30 | 288 | 288
2016-10-18 03:00 | 288 | 288
2016-10-18 03:30 | 286 | 286
2016-10-18 04:00 | 284 | 284
2016-10-18 04:30 | 286 | 286
2016-10-18 05:00 | 290 | 290
2016-10-18 05:30 | 296 | 295
2016-10-18 06:00 | 301 | 301
2016-10-18 06:30 | 331 | 331
2016-10-18 07:00 | 344 | 343
2016-10-18 07:30 | 381 | 381
2016-10-18 08:00 | 401 | 400
2016-10-18 08:30 | 409 | 408
2016-10-18 09:00 | 412 | 411
2016-10-18 09:30 | 409 | 409
2016-10-18 10:00 | 402 | 401
2016-10-18 10:30 | 404 | 403
2016-10-18 11:00 | 404 | 403
2016-10-18 11:30 | 410 | 409
2016-10-18 12:00 | 420 | 419
2016-10-18 12:30 | 419 | 418
2016-10-18 13:00 | 429 | 428
2016-10-18 13:30 | 419 | 418
2016-10-18 14:00 | 410 | 409
2016-10-18 14:30 | 416 | 414
2016-10-18 15:00 | 420 | 419
2016-10-18 15:30 | 423 | 422
2016-10-18 16:00 | 433 | 432
2016-10-18 16:30 | 448 | 446
2016-10-18 17:00 | 441 | 440
2016-10-18 17:30 | 435 | 433
2016-10-18 18:00 | 433 | 431
2016-10-18 18:30 | 438 | 437
2016-10-18 19:00 | 450 | 449
2016-10-18 19:30 | 443 | 442
2016-10-18 20:00 | 463 | 462
2016-10-18 20:30 | 452 | 451
2016-10-18 21:00 | 430 | 429
2016-10-18 21:30 | 426 | 424
2016-10-18 22:00 | 402 | 401
2016-10-18 22:30 | 345 | 344
2016-10-18 23:00 | 327 | 325
2016-10-18 23:30 | 318 | 316
2016-10-19 | 315 | 314
2016-10-19 00:30 | 316 | 315
2016-10-19 01:00 | 322 | 321
2016-10-19 01:30 | 322 | 321
2016-10-19 02:00 | 327 | 326
2016-10-19 02:30 | 322 | 321
2016-10-19 03:00 | 319 | 318
2016-10-19 03:30 | 321 | 320
2016-10-19 04:00 | 317 | 316
2016-10-19 04:30 | 308 | 307
2016-10-19 05:00 | 308 | 307
2016-10-19 05:30 | 299 | 297
2016-10-19 06:00 | 302 | 300
2016-10-19 06:30 | 328 | 327
2016-10-19 07:00 | 359 | 358
2016-10-19 07:30 | 418 | 417
2016-10-19 08:00 | 433 | 432
2016-10-19 08:30 | 451 | 451
2016-10-19 09:00 | 460 | 458
2016-10-19 09:30 | 470 | 468
2016-10-19 10:00 | 477 | 476
2016-10-19 10:30 | 479 | 478
2016-10-19 11:00 | 479 | 477
2016-10-19 11:30 | 471 | 469
2016-10-19 12:00 | 448 | 447
2016-10-19 12:30 | 432 | 431
2016-10-19 13:00 | 423 | 422
2016-10-19 13:30 | 406 | 404
2016-10-19 14:00 | 399 | 397
2016-10-19 14:30 | 415 | 413
2016-10-19 15:00 | 429 | 427
2016-10-19 15:30 | 430 | 428
2016-10-19 16:00 | 385 | 383
2016-10-19 16:30 | 376 | 374
2016-10-19 17:00 | 397 | 395
2016-10-19 17:30 | 397 | 396
2016-10-19 18:00 | 392 | 391
2016-10-19 18:30 | 386 | 385
2016-10-19 19:00 | 356 | 354
2016-10-19 19:30 | 357 | 356
2016-10-19 20:00 | 350 | 349
2016-10-19 20:30 | 358 | 357
2016-10-19 21:00 | 393 | 392
2016-10-19 21:30 | 382 | 381
2016-10-19 22:00 | 365 | 364
2016-10-19 22:30 | 264 | 262
2016-10-19 23:00 | 231 | 230
2016-10-19 23:30 | 231 | 230
2016-10-20 | 254 | 253
2016-10-20 00:30 | 224 | 223
2016-10-20 01:00 | 243 | 242
2016-10-20 01:30 | 242 | 241
2016-10-20 02:00 | 241 | 240
2016-10-20 02:30 | 238 | 237
2016-10-20 03:00 | 234 | 233
2016-10-20 03:30 | 226 | 225
2016-10-20 04:00 | 223 | 223
2016-10-20 04:30 | 228 | 227
2016-10-20 05:00 | 231 | 230
2016-10-20 05:30 | 239 | 238
2016-10-20 06:00 | 254 | 253
2016-10-20 06:30 | 280 | 280
2016-10-20 07:00 | 304 | 304
2016-10-20 07:30 | 326 | 326
2016-10-20 08:00 | 355 | 354
2016-10-20 08:30 | 303 | 301
2016-10-20 09:00 | 267 | 265
2016-10-20 09:30 | 271 | 268
2016-10-20 10:00 | 269 | 267
2016-10-20 10:30 | 263 | 261
2016-10-20 11:00 | 261 | 259
2016-10-20 11:30 | 265 | 263
2016-10-20 12:00 | 271 | 269
2016-10-20 12:30 | 275 | 273
2016-10-20 13:00 | 274 | 273
2016-10-20 13:30 | 258 | 256
2016-10-20 14:00 | 258 | 256
2016-10-20 14:30 | 267 | 265
2016-10-20 15:00 | 273 | 271
2016-10-20 15:30 | 266 | 264
2016-10-20 16:00 | 276 | 274
2016-10-20 16:30 | 235 | 232
2016-10-20 17:00 | 217 | 215
2016-10-20 17:30 | 223 | 221
2016-10-20 18:00 | 238 | 236
2016-10-20 18:30 | 225 | 224
2016-10-20 19:00 | 213 | 212
2016-10-20 19:30 | 226 | 225
2016-10-20 20:00 | 244 | 243
2016-10-20 20:30 | 247 | 247
2016-10-20 21:00 | 241 | 241
2016-10-20 21:30 | 219 | 218
2016-10-20 22:00 | 246 | 245
2016-10-20 22:30 | 156 | 156
2016-10-20 23:00 | 139 | 138
2016-10-20 23:30 | 125 | 125
2016-10-21 | 158 | 157
2016-10-21 00:30 | 177 | 177
2016-10-21 01:00 | 168 | 167
2016-10-21 01:30 | 163 | 162
2016-10-21 02:00 | 160 | 160
2016-10-21 02:30 | 154 | 154
2016-10-21 03:00 | 151 | 151
2016-10-21 03:30 | 152 | 151
2016-10-21 04:00 | 147 | 146
2016-10-21 04:30 | 147 | 146
2016-10-21 05:00 | 150 | 149
2016-10-21 05:30 | 158 | 157
2016-10-21 06:00 | 147 | 146
2016-10-21 06:30 | 165 | 164
2016-10-21 07:00 | 186 | 185
2016-10-21 07:30 | 226 | 226
2016-10-21 08:00 | 250 | 249
2016-10-21 08:30 | 235 | 234
2016-10-21 09:00 | 244 | 243
2016-10-21 09:30 | 245 | 244
2016-10-21 10:00 | 238 | 238
2016-10-21 10:30 | 239 | 239
2016-10-21 11:00 | 237 | 236
2016-10-21 11:30 | 236 | 235
2016-10-21 12:00 | 231 | 230
2016-10-21 12:30 | 236 | 235
2016-10-21 13:00 | 239 | 238
2016-10-21 13:30 | 240 | 240
2016-10-21 14:00 | 224 | 223
2016-10-21 14:30 | 222 | 221
2016-10-21 15:00 | 231 | 230
2016-10-21 15:30 | 233 | 232
2016-10-21 16:00 | 238 | 237
2016-10-21 16:30 | 245 | 244
2016-10-21 17:00 | 255 | 254
2016-10-21 17:30 | 254 | 253
2016-10-21 18:00 | 254 | 253
2016-10-21 18:30 | 258 | 257
2016-10-21 19:00 | 258 | 257
2016-10-21 19:30 | 205 | 204
2016-10-21 20:00 | 209 | 208
2016-10-21 20:30 | 203 | 202
2016-10-21 21:00 | 192 | 192
2016-10-21 21:30 | 174 | 173
2016-10-21 22:00 | 150 | 149
2016-10-21 22:30 | 143 | 142
2016-10-21 23:00 | 130 | 129
2016-10-21 23:30 | 113 | 111
2016-10-22 | 104 | 103
2016-10-22 00:30 | 142 | 141
2016-10-22 01:00 | 224 | 223
2016-10-22 01:30 | 239 | 239
2016-10-22 02:00 | 236 | 236
2016-10-22 02:30 | 236 | 236
2016-10-22 03:00 | 234 | 234
2016-10-22 03:30 | 234 | 234
2016-10-22 04:00 | 224 | 223
2016-10-22 04:30 | 223 | 223
2016-10-22 05:00 | 228 | 227
2016-10-22 05:30 | 232 | 232
2016-10-22 06:00 | 230 | 230
2016-10-22 06:30 | 228 | 227
2016-10-22 07:00 | 232 | 231
2016-10-22 07:30 | 242 | 241
2016-10-22 08:00 | 254 | 254
2016-10-22 08:30 | 266 | 266
2016-10-22 09:00 | 271 | 271
2016-10-22 09:30 | 277 | 277
2016-10-22 10:00 | 286 | 285
2016-10-22 10:30 | 287 | 287
2016-10-22 11:00 | 283 | 282
2016-10-22 11:30 | 284 | 284
2016-10-22 12:00 | 285 | 284
2016-10-22 12:30 | 284 | 284
2016-10-22 13:00 | 284 | 283
2016-10-22 13:30 | 284 | 283
2016-10-22 14:00 | 280 | 280
2016-10-22 14:30 | 281 | 281
2016-10-22 15:00 | 278 | 277
2016-10-22 15:30 | 292 | 291
2016-10-22 16:00 | 302 | 301
2016-10-22 16:30 | 309 | 308
2016-10-22 17:00 | 300 | 299
2016-10-22 17:30 | 322 | 321
2016-10-22 18:00 | 324 | 323
2016-10-22 18:30 | 330 | 329
2016-10-22 19:00 | 332 | 331
2016-10-22 19:30 | 330 | 329
2016-10-22 20:00 | 340 | 339
2016-10-22 20:30 | 341 | 340
2016-10-22 21:00 | 334 | 334
2016-10-22 21:30 | 322 | 321
2016-10-22 22:00 | 311 | 310
2016-10-22 22:30 | 294 | 293
2016-10-22 23:00 | 281 | 280
2016-10-22 23:30 | 269 | 268
2016-10-23 | 260 | 259
2016-10-23 00:30 | 255 | 254
2016-10-23 01:00 | 247 | 246
2016-10-23 01:30 | 245 | 244
2016-10-23 02:00 | 238 | 237
2016-10-23 02:30 | 236 | 235
2016-10-23 03:00 | 237 | 236
2016-10-23 03:30 | 233 | 232
2016-10-23 04:00 | 232 | 231
2016-10-23 04:30 | 229 | 228
2016-10-23 05:00 | 225 | 224
2016-10-23 05:30 | 226 | 224
2016-10-23 06:00 | 224 | 223
2016-10-23 06:30 | 231 | 230
2016-10-23 07:00 | 233 | 232
2016-10-23 07:30 | 242 | 241
2016-10-23 08:00 | 251 | 250
2016-10-23 08:30 | 260 | 259
2016-10-23 09:00 | 265 | 265
2016-10-23 09:30 | 270 | 269
2016-10-23 10:00 | 276 | 275
2016-10-23 10:30 | 280 | 280
2016-10-23 11:00 | 278 | 278
2016-10-23 11:30 | 281 | 280
2016-10-23 12:00 | 285 | 284
2016-10-23 12:30 | 284 | 284
2016-10-23 13:00 | 285 | 284
2016-10-23 13:30 | 281 | 280
2016-10-23 14:00 | 281 | 281
2016-10-23 14:30 | 289 | 288
2016-10-23 15:00 | 294 | 294
2016-10-23 15:30 | 301 | 301
2016-10-23 16:00 | 307 | 306
2016-10-23 16:30 | 307 | 306
2016-10-23 17:00 | 310 | 309
2016-10-23 17:30 | 317 | 317
2016-10-23 18:00 | 315 | 314
2016-10-23 18:30 | 320 | 320
2016-10-23 19:00 | 310 | 309
2016-10-23 19:30 | 317 | 316
2016-10-23 20:00 | 310 | 309
2016-10-23 20:30 | 313 | 312
2016-10-23 21:00 | 307 | 306
2016-10-23 21:30 | 320 | 319
2016-10-23 22:00 | 261 | 260
2016-10-23 22:30 | 235 | 234
2016-10-23 23:00 | 241 | 241
2016-10-23 23:30 | 254 | 253
2016-10-24 | 241 | 240
2016-10-24 00:30 | 239 | 238
2016-10-24 01:00 | 237 | 237
2016-10-24 01:30 | 239 | 238
2016-10-24 02:00 | 237 | 237
2016-10-24 02:30 | 236 | 235
2016-10-24 03:00 | 235 | 235
2016-10-24 03:30 | 233 | 232
2016-10-24 04:00 | 235 | 234
2016-10-24 04:30 | 235 | 235
2016-10-24 05:00 | 240 | 239
2016-10-24 05:30 | 237 | 237
2016-10-24 06:00 | 234 | 234
2016-10-24 06:30 | 238 | 238
2016-10-24 07:00 | 249 | 249
2016-10-24 07:30 | 292 | 292
2016-10-24 08:00 | 314 | 313
2016-10-24 08:30 | 323 | 322
2016-10-24 09:00 | 323 | 322
2016-10-24 09:30 | 323 | 322
2016-10-24 10:00 | 317 | 316
2016-10-24 10:30 | 308 | 307
2016-10-24 11:00 | 310 | 309
2016-10-24 11:30 | 307 | 306
2016-10-24 12:00 | 312 | 311
2016-10-24 12:30 | 320 | 319
2016-10-24 13:00 | 321 | 320
2016-10-24 13:30 | 308 | 307
2016-10-24 14:00 | 300 | 299
2016-10-24 14:30 | 307 | 306
2016-10-24 15:00 | 307 | 306
2016-10-24 15:30 | 318 | 317
2016-10-24 16:00 | 322 | 320
2016-10-24 16:30 | 323 | 322
2016-10-24 17:00 | 332 | 331
2016-10-24 17:30 | 337 | 336
2016-10-24 18:00 | 345 | 343
2016-10-24 18:30 | 355 | 354
2016-10-24 19:00 | 368 | 367
2016-10-24 19:30 | 367 | 366
2016-10-24 20:00 | 366 | 365
2016-10-24 20:30 | 362 | 361
2016-10-24 21:00 | 353 | 352
2016-10-24 21:30 | 339 | 338
2016-10-24 22:00 | 321 | 320
2016-10-24 22:30 | 289 | 288
2016-10-24 23:00 | 270 | 269
2016-10-24 23:30 | 257 | 256
2016-10-25 | 248 | 247
2016-10-25 00:30 | 260 | 260
2016-10-25 01:00 | 252 | 252
2016-10-25 01:30 | 250 | 249
2016-10-25 02:00 | 246 | 245
2016-10-25 02:30 | 238 | 238
2016-10-25 03:00 | 236 | 236
2016-10-25 03:30 | 237 | 236
2016-10-25 04:00 | 235 | 234
2016-10-25 04:30 | 234 | 233
2016-10-25 05:00 | 239 | 238
2016-10-25 05:30 | 246 | 245
2016-10-25 06:00 | 250 | 249
2016-10-25 06:30 | 278 | 277
2016-10-25 07:00 | 297 | 296
2016-10-25 07:30 | 309 | 309
2016-10-25 08:00 | 311 | 311
2016-10-25 08:30 | 312 | 312
2016-10-25 09:00 | 311 | 310
2016-10-25 09:30 | 304 | 304
2016-10-25 10:00 | 302 | 301
2016-10-25 10:30 | 299 | 298
2016-10-25 11:00 | 303 | 303
2016-10-25 11:30 | 306 | 306
2016-10-25 12:00 | 313 | 312
2016-10-25 12:30 | 314 | 312
2016-10-25 13:00 | 315 | 313
2016-10-25 13:30 | 303 | 301
2016-10-25 14:00 | 299 | 297
2016-10-25 14:30 | 307 | 305
2016-10-25 15:00 | 313 | 311
2016-10-25 15:30 | 294 | 293
2016-10-25 16:00 | 315 | 315
2016-10-25 16:30 | 349 | 348
2016-10-25 17:00 | 362 | 360
2016-10-25 17:30 | 366 | 364
2016-10-25 18:00 | 365 | 364
2016-10-25 18:30 | 364 | 363
2016-10-25 19:00 | 375 | 373
2016-10-25 19:30 | 378 | 376
2016-10-25 20:00 | 376 | 374
2016-10-25 20:30 | 362 | 361
2016-10-25 21:00 | 348 | 346
2016-10-25 21:30 | 330 | 329
2016-10-25 22:00 | 316 | 315
2016-10-25 22:30 | 298 | 296
2016-10-25 23:00 | 272 | 270
2016-10-25 23:30 | 259 | 258
2016-10-26 | 255 | 254
2016-10-26 00:30 | 242 | 241
2016-10-26 01:00 | 206 | 204
2016-10-26 01:30 | 196 | 195
2016-10-26 02:00 | 194 | 192
2016-10-26 02:30 | 192 | 191
2016-10-26 03:00 | 188 | 187
2016-10-26 03:30 | 189 | 187
2016-10-26 04:00 | 187 | 185
2016-10-26 04:30 | 181 | 180
2016-10-26 05:00 | 148 | 146
2016-10-26 05:30 | 133 | 131
2016-10-26 06:00 | 98 | 95
2016-10-26 06:30 | 110 | 109
2016-10-26 07:00 | 127 | 126
2016-10-26 07:30 | 206 | 205
2016-10-26 08:00 | 234 | 233
2016-10-26 08:30 | 228 | 226
2016-10-26 09:00 | 219 | 218
2016-10-26 09:30 | 222 | 221
2016-10-26 10:00 | 219 | 218
2016-10-26 10:30 | 219 | 218
2016-10-26 11:00 | 230 | 229
2016-10-26 11:30 | 234 | 233
2016-10-26 12:00 | 237 | 236
2016-10-26 12:30 | 245 | 245
2016-10-26 13:00 | 242 | 241
2016-10-26 13:30 | 237 | 236
2016-10-26 14:00 | 237 | 236
2016-10-26 14:30 | 245 | 244
2016-10-26 15:00 | 249 | 247
2016-10-26 15:30 | 256 | 255
2016-10-26 16:00 | 266 | 265
2016-10-26 16:30 | 282 | 281
2016-10-26 17:00 | 288 | 287
2016-10-26 17:30 | 289 | 288
2016-10-26 18:00 | 285 | 284
2016-10-26 18:30 | 297 | 296
2016-10-26 19:00 | 304 | 303
2016-10-26 19:30 | 300 | 299
2016-10-26 20:00 | 297 | 296
2016-10-26 20:30 | 287 | 286
2016-10-26 21:00 | 284 | 283
2016-10-26 21:30 | 279 | 278
2016-10-26 22:00 | 265 | 264
2016-10-26 22:30 | 209 | 207
2016-10-26 23:00 | 213 | 212
2016-10-26 23:30 | 211 | 210
2016-10-27 | 199 | 198
2016-10-27 00:30 | 191 | 190
2016-10-27 01:00 | 181 | 180
2016-10-27 01:30 | 176 | 175
2016-10-27 02:00 | 174 | 173
2016-10-27 02:30 | 171 | 170
2016-10-27 03:00 | 168 | 167
2016-10-27 03:30 | 167 | 166
2016-10-27 04:00 | 166 | 165
2016-10-27 04:30 | 166 | 165
2016-10-27 05:00 | 170 | 169
2016-10-27 05:30 | 180 | 179
2016-10-27 06:00 | 176 | 175
2016-10-27 06:30 | 197 | 196
2016-10-27 07:00 | 210 | 210
2016-10-27 07:30 | 239 | 238
2016-10-27 08:00 | 244 | 243
2016-10-27 08:30 | 240 | 238
2016-10-27 09:00 | 245 | 243
2016-10-27 09:30 | 245 | 243
2016-10-27 10:00 | 252 | 250
2016-10-27 10:30 | 253 | 251
2016-10-27 11:00 | 251 | 249
2016-10-27 11:30 | 252 | 251
2016-10-27 12:00 | 261 | 259
2016-10-27 12:30 | 266 | 265
2016-10-27 13:00 | 252 | 250
2016-10-27 13:30 | 248 | 247
2016-10-27 14:00 | 251 | 250
2016-10-27 14:30 | 257 | 255
2016-10-27 15:00 | 263 | 261
2016-10-27 15:30 | 270 | 268
2016-10-27 16:00 | 279 | 278
2016-10-27 16:30 | 301 | 299
2016-10-27 17:00 | 297 | 294
2016-10-27 17:30 | 306 | 304
2016-10-27 18:00 | 313 | 311
2016-10-27 18:30 | 315 | 313
2016-10-27 19:00 | 313 | 311
2016-10-27 19:30 | 319 | 318
2016-10-27 20:00 | 323 | 322
2016-10-27 20:30 | 314 | 312
2016-10-27 21:00 | 299 | 298
2016-10-27 21:30 | 280 | 278
2016-10-27 22:00 | 264 | 262
2016-10-27 22:30 | 218 | 215
2016-10-27 23:00 | 225 | 223
2016-10-27 23:30 | 217 | 215
2016-10-28 | 207 | 205
2016-10-28 00:30 | 194 | 192
2016-10-28 01:00 | 186 | 184
2016-10-28 01:30 | 180 | 179
2016-10-28 02:00 | 175 | 174
2016-10-28 02:30 | 172 | 171
2016-10-28 03:00 | 169 | 168
2016-10-28 03:30 | 171 | 170
2016-10-28 04:00 | 167 | 165
2016-10-28 04:30 | 170 | 169
2016-10-28 05:00 | 170 | 168
2016-10-28 05:30 | 169 | 168
2016-10-28 06:00 | 131 | 130
2016-10-28 06:30 | 145 | 143
2016-10-28 07:00 | 116 | 114
2016-10-28 07:30 | 188 | 187
2016-10-28 08:00 | 234 | 233
2016-10-28 08:30 | 225 | 223
2016-10-28 09:00 | 216 | 215
2016-10-28 09:30 | 229 | 227
2016-10-28 10:00 | 226 | 225
2016-10-28 10:30 | 262 | 261
2016-10-28 11:00 | 327 | 326
2016-10-28 11:30 | 331 | 329
2016-10-28 12:00 | 336 | 334
2016-10-28 12:30 | 335 | 332
2016-10-28 13:00 | 323 | 321
2016-10-28 13:30 | 314 | 311
2016-10-28 14:00 | 310 | 307
2016-10-28 14:30 | 323 | 321
2016-10-28 15:00 | 328 | 326
2016-10-28 15:30 | 321 | 319
2016-10-28 16:00 | 329 | 328
2016-10-28 16:30 | 348 | 346
2016-10-28 17:00 | 358 | 356
2016-10-28 17:30 | 347 | 345
2016-10-28 18:00 | 356 | 354
2016-10-28 18:30 | 373 | 371
2016-10-28 19:00 | 389 | 387
2016-10-28 19:30 | 388 | 386
2016-10-28 20:00 | 378 | 377
2016-10-28 20:30 | 366 | 365
2016-10-28 21:00 | 356 | 354
2016-10-28 21:30 | 346 | 344
2016-10-28 22:00 | 334 | 333
2016-10-28 22:30 | 293 | 291
2016-10-28 23:00 | 286 | 285
2016-10-28 23:30 | 288 | 286
2016-10-29 | 281 | 280
2016-10-29 00:30 | 272 | 270
2016-10-29 01:00 | 264 | 262
2016-10-29 01:30 | 258 | 256
2016-10-29 02:00 | 252 | 250
2016-10-29 02:30 | 248 | 246
2016-10-29 03:00 | 246 | 244
2016-10-29 03:30 | 245 | 243
2016-10-29 04:00 | 240 | 239
2016-10-29 04:30 | 238 | 236
2016-10-29 05:00 | 240 | 238
2016-10-29 05:30 | 244 | 242
2016-10-29 06:00 | 243 | 241
2016-10-29 06:30 | 249 | 247
2016-10-29 07:00 | 253 | 251
2016-10-29 07:30 | 262 | 260
2016-10-29 08:00 | 260 | 258
2016-10-29 08:30 | 263 | 261
2016-10-29 09:00 | 275 | 273
2016-10-29 09:30 | 281 | 280
2016-10-29 10:00 | 275 | 273
2016-10-29 10:30 | 260 | 258
2016-10-29 11:00 | 257 | 255
2016-10-29 11:30 | 254 | 252
2016-10-29 12:00 | 273 | 271
2016-10-29 12:30 | 278 | 276
2016-10-29 13:00 | 280 | 279
2016-10-29 13:30 | 273 | 272
2016-10-29 14:00 | 281 | 280
2016-10-29 14:30 | 288 | 287
2016-10-29 15:00 | 298 | 296
2016-10-29 15:30 | 305 | 303
2016-10-29 16:00 | 315 | 313
2016-10-29 16:30 | 320 | 318
2016-10-29 17:00 | 329 | 328
2016-10-29 17:30 | 332 | 330
2016-10-29 18:00 | 335 | 334
2016-10-29 18:30 | 339 | 338
2016-10-29 19:00 | 350 | 349
2016-10-29 19:30 | 367 | 365
2016-10-29 20:00 | 363 | 361
2016-10-29 20:30 | 356 | 354
2016-10-29 21:00 | 344 | 342
2016-10-29 21:30 | 333 | 331
2016-10-29 22:00 | 329 | 327
2016-10-29 22:30 | 301 | 299
2016-10-29 23:00 | 296 | 294
2016-10-29 23:30 | 285 | 283
2016-10-30 | 277 | 275
2016-10-30 00:30 | 269 | 267
2016-10-30 01:00 | 256 | 254
2016-10-30 01:30 | 255 | 253
2016-10-30 02:00 | 247 | 245
2016-10-30 02:30 | 244 | 242
2016-10-30 03:00 | 239 | 237
2016-10-30 03:30 | 240 | 238
2016-10-30 04:00 | 237 | 236
2016-10-30 04:30 | 239 | 237
2016-10-30 05:00 | 237 | 235
2016-10-30 05:30 | 235 | 233
2016-10-30 06:00 | 230 | 228
2016-10-30 06:30 | 231 | 230
2016-10-30 07:00 | 246 | 245
2016-10-30 07:30 | 259 | 257
2016-10-30 08:00 | 269 | 268
2016-10-30 08:30 | 279 | 278
2016-10-30 09:00 | 282 | 281
2016-10-30 09:30 | 268 | 266
2016-10-30 10:00 | 268 | 266
2016-10-30 10:30 | 289 | 288
2016-10-30 11:00 | 258 | 257
2016-10-30 11:30 | 219 | 218
2016-10-30 12:00 | 284 | 282
2016-10-30 12:30 | 289 | 287
2016-10-30 13:00 | 287 | 286
2016-10-30 13:30 | 276 | 275
2016-10-30 14:00 | 273 | 271
2016-10-30 14:30 | 280 | 278
2016-10-30 15:00 | 284 | 282
2016-10-30 15:30 | 291 | 289
2016-10-30 16:00 | 306 | 305
2016-10-30 16:30 | 320 | 319
2016-10-30 17:00 | 333 | 332
2016-10-30 17:30 | 341 | 339
2016-10-30 18:00 | 351 | 349
2016-10-30 18:30 | 362 | 360
2016-10-30 19:00 | 378 | 377
2016-10-30 19:30 | 398 | 396
2016-10-30 20:00 | 388 | 387
2016-10-30 20:30 | 371 | 370
2016-10-30 21:00 | 360 | 358
2016-10-30 21:30 | 346 | 344
2016-10-30 22:00 | 334 | 332
2016-10-30 22:30 | 312 | 310
2016-10-30 23:00 | 297 | 295
2016-10-30 23:30 | 282 | 281
2016-10-31 | 274 | 273
2016-10-31 00:30 | 264 | 262
2016-10-31 01:00 | 253 | 251
2016-10-31 01:30 | 249 | 248
2016-10-31 02:00 | 244 | 242
2016-10-31 02:30 | 241 | 239
2016-10-31 03:00 | 238 | 237
2016-10-31 03:30 | 239 | 237
2016-10-31 04:00 | 236 | 235
2016-10-31 04:30 | 238 | 237
2016-10-31 05:00 | 245 | 244
2016-10-31 05:30 | 254 | 253
2016-10-31 06:00 | 261 | 260
2016-10-31 06:30 | 279 | 278
2016-10-31 07:00 | 286 | 284
2016-10-31 07:30 | 313 | 312
2016-10-31 08:00 | 319 | 318
2016-10-31 08:30 | 321 | 319
2016-10-31 09:00 | 329 | 328
2016-10-31 09:30 | 319 | 318
2016-10-31 10:00 | 302 | 300
2016-10-31 10:30 | 296 | 294
2016-10-31 11:00 | 298 | 296
2016-10-31 11:30 | 300 | 298
2016-10-31 12:00 | 306 | 304
2016-10-31 12:30 | 311 | 309
2016-10-31 13:00 | 313 | 311
2016-10-31 13:30 | 308 | 306
2016-10-31 14:00 | 308 | 307
2016-10-31 14:30 | 312 | 310
2016-10-31 15:00 | 315 | 313
2016-10-31 15:30 | 318 | 316
2016-10-31 16:00 | 329 | 327
2016-10-31 16:30 | 354 | 353
2016-10-31 17:00 | 364 | 363
2016-10-31 17:30 | 366 | 365
2016-10-31 18:00 | 368 | 367
2016-10-31 18:30 | 372 | 371
2016-10-31 19:00 | 378 | 376
2016-10-31 19:30 | 379 | 378
2016-10-31 20:00 | 369 | 368
2016-10-31 20:30 | 352 | 350
2016-10-31 21:00 | 341 | 339
2016-10-31 21:30 | 330 | 328
2016-10-31 22:00 | 309 | 307
2016-10-31 22:30 | 263 | 261
2016-10-31 23:00 | 251 | 250
2016-10-31 23:30 | 245 | 243
2016-11-01 | 247 | 246
2016-11-01 00:30 | 240 | 239
2016-11-01 01:00 | 231 | 230
2016-11-01 01:30 | 222 | 221
2016-11-01 02:00 | 220 | 218
2016-11-01 02:30 | 230 | 228
2016-11-01 03:00 | 235 | 234
2016-11-01 03:30 | 229 | 228
2016-11-01 04:00 | 229 | 228
2016-11-01 04:30 | 227 | 226
2016-11-01 05:00 | 225 | 224
2016-11-01 05:30 | 233 | 232
2016-11-01 06:00 | 230 | 229
2016-11-01 06:30 | 253 | 252
2016-11-01 07:00 | 272 | 271
2016-11-01 07:30 | 285 | 284
2016-11-01 08:00 | 305 | 304
2016-11-01 08:30 | 282 | 280
2016-11-01 09:00 | 271 | 269
2016-11-01 09:30 | 266 | 264
2016-11-01 10:00 | 286 | 284
2016-11-01 10:30 | 294 | 293
2016-11-01 11:00 | 307 | 306
2016-11-01 11:30 | 310 | 309
2016-11-01 12:00 | 311 | 310
2016-11-01 12:30 | 312 | 312
2016-11-01 13:00 | 312 | 312
2016-11-01 13:30 | 309 | 308
2016-11-01 14:00 | 314 | 313
2016-11-01 14:30 | 328 | 327
2016-11-01 15:00 | 316 | 315
2016-11-01 15:30 | 307 | 306
2016-11-01 16:00 | 320 | 318
2016-11-01 16:30 | 328 | 326
2016-11-01 17:00 | 347 | 346
2016-11-01 17:30 | 353 | 352
2016-11-01 18:00 | 360 | 359
2016-11-01 18:30 | 368 | 367
2016-11-01 19:00 | 375 | 374
2016-11-01 19:30 | 378 | 377
2016-11-01 20:00 | 376 | 374
2016-11-01 20:30 | 363 | 362
2016-11-01 21:00 | 351 | 350
2016-11-01 21:30 | 335 | 334
2016-11-01 22:00 | 319 | 317
2016-11-01 22:30 | 296 | 294
2016-11-01 23:00 | 277 | 275
2016-11-01 23:30 | 266 | 264
2016-11-02 | 258 | 257
2016-11-02 00:30 | 250 | 249
2016-11-02 01:00 | 239 | 238
2016-11-02 01:30 | 235 | 234
2016-11-02 02:00 | 229 | 228
2016-11-02 02:30 | 224 | 223
2016-11-02 03:00 | 223 | 222
2016-11-02 03:30 | 223 | 221
2016-11-02 04:00 | 222 | 221
2016-11-02 04:30 | 222 | 221
2016-11-02 05:00 | 225 | 224
2016-11-02 05:30 | 233 | 232
2016-11-02 06:00 | 241 | 240
2016-11-02 06:30 | 267 | 266
2016-11-02 07:00 | 283 | 282
2016-11-02 07:30 | 297 | 297
2016-11-02 08:00 | 310 | 309
2016-11-02 08:30 | 313 | 313
2016-11-02 09:00 | 316 | 315
2016-11-02 09:30 | 317 | 316
2016-11-02 10:00 | 316 | 315
2016-11-02 10:30 | 318 | 317
2016-11-02 11:00 | 319 | 318
2016-11-02 11:30 | 315 | 314
2016-11-02 12:00 | 292 | 291
2016-11-02 12:30 | 293 | 291
2016-11-02 13:00 | 295 | 294
2016-11-02 13:30 | 291 | 290
2016-11-02 14:00 | 281 | 280
2016-11-02 14:30 | 289 | 288
2016-11-02 15:00 | 296 | 294
2016-11-02 15:30 | 262 | 260
2016-11-02 16:00 | 253 | 252
2016-11-02 16:30 | 253 | 251
2016-11-02 17:00 | 297 | 295
2016-11-02 17:30 | 296 | 294
2016-11-02 18:00 | 297 | 295
2016-11-02 18:30 | 307 | 306
2016-11-02 19:00 | 313 | 311
2016-11-02 19:30 | 286 | 284
2016-11-02 20:00 | 289 | 287
2016-11-02 20:30 | 290 | 288
2016-11-02 21:00 | 279 | 277
2016-11-02 21:30 | 260 | 259
2016-11-02 22:00 | 247 | 245
2016-11-02 22:30 | 228 | 226
2016-11-02 23:00 | 197 | 196
2016-11-02 23:30 | 189 | 188
2016-11-03 | 182 | 180
2016-11-03 00:30 | 179 | 178
2016-11-03 01:00 | 164 | 163
2016-11-03 01:30 | 160 | 159
2016-11-03 02:00 | 155 | 154
2016-11-03 02:30 | 153 | 151
2016-11-03 03:00 | 149 | 148
2016-11-03 03:30 | 147 | 146
2016-11-03 04:00 | 143 | 142
2016-11-03 04:30 | 140 | 139
2016-11-03 05:00 | 140 | 139
2016-11-03 05:30 | 148 | 147
2016-11-03 06:00 | 109 | 108
2016-11-03 06:30 | 120 | 119
2016-11-03 07:00 | 129 | 128
2016-11-03 07:30 | 154 | 154
2016-11-03 08:00 | 167 | 166
2016-11-03 08:30 | 173 | 171
2016-11-03 09:00 | 178 | 176
2016-11-03 09:30 | 179 | 178
2016-11-03 10:00 | 178 | 176
2016-11-03 10:30 | 231 | 230
2016-11-03 11:00 | 245 | 243
2016-11-03 11:30 | 245 | 243
2016-11-03 12:00 | 244 | 243
2016-11-03 12:30 | 250 | 248
2016-11-03 13:00 | 248 | 246
2016-11-03 13:30 | 248 | 248
2016-11-03 14:00 | 251 | 251
2016-11-03 14:30 | 255 | 255
2016-11-03 15:00 | 262 | 262
2016-11-03 15:30 | 263 | 263
2016-11-03 16:00 | 267 | 266
2016-11-03 16:30 | 237 | 236
2016-11-03 17:00 | 230 | 230
2016-11-03 17:30 | 229 | 228
2016-11-03 18:00 | 238 | 237
2016-11-03 18:30 | 244 | 244
2016-11-03 19:00 | 256 | 255
2016-11-03 19:30 | 228 | 227
2016-11-03 20:00 | 218 | 217
2016-11-03 20:30 | 225 | 225
2016-11-03 21:00 | 225 | 225
2016-11-03 21:30 | 210 | 210
2016-11-03 22:00 | 194 | 194
2016-11-03 22:30 | 173 | 172
2016-11-03 23:00 | 156 | 155
2016-11-03 23:30 | 187 | 187
2016-11-04 | 190 | 190
2016-11-04 00:30 | 180 | 179
2016-11-04 01:00 | 173 | 172
2016-11-04 01:30 | 166 | 165
2016-11-04 02:00 | 157 | 156
2016-11-04 02:30 | 155 | 155
2016-11-04 03:00 | 159 | 158
2016-11-04 03:30 | 158 | 157
2016-11-04 04:00 | 155 | 155
2016-11-04 04:30 | 155 | 155
2016-11-04 05:00 | 111 | 109
2016-11-04 05:30 | 110 | 109
2016-11-04 06:00 | 115 | 114
2016-11-04 06:30 | 136 | 135
2016-11-04 07:00 | 153 | 153
2016-11-04 07:30 | 169 | 169
2016-11-04 08:00 | 180 | 178
2016-11-04 08:30 | 189 | 187
2016-11-04 09:00 | 197 | 195
2016-11-04 09:30 | 195 | 193
2016-11-04 10:00 | 190 | 187
2016-11-04 10:30 | 189 | 186
2016-11-04 11:00 | 222 | 220
2016-11-04 11:30 | 281 | 279
2016-11-04 12:00 | 339 | 337
2016-11-04 12:30 | 340 | 338
2016-11-04 13:00 | 344 | 341
2016-11-04 13:30 | 339 | 335
2016-11-04 14:00 | 341 | 337
2016-11-04 14:30 | 346 | 343
2016-11-04 15:00 | 350 | 347
2016-11-04 15:30 | 329 | 326
2016-11-04 16:00 | 338 | 335
2016-11-04 16:30 | 342 | 340
2016-11-04 17:00 | 373 | 371
2016-11-04 17:30 | 374 | 371
2016-11-04 18:00 | 367 | 365
2016-11-04 18:30 | 372 | 369
2016-11-04 19:00 | 376 | 374
2016-11-04 19:30 | 375 | 372
2016-11-04 20:00 | 366 | 364
2016-11-04 20:30 | 358 | 356
2016-11-04 21:00 | 344 | 342
2016-11-04 21:30 | 329 | 327
2016-11-04 22:00 | 317 | 315
2016-11-04 22:30 | 302 | 300
2016-11-04 23:00 | 282 | 280
2016-11-04 23:30 | 275 | 273
2016-11-05 | 267 | 264
2016-11-05 00:30 | 255 | 252
2016-11-05 01:00 | 246 | 243
2016-11-05 01:30 | 244 | 241
2016-11-05 02:00 | 235 | 232
2016-11-05 02:30 | 232 | 230
2016-11-05 03:00 | 230 | 229
2016-11-05 03:30 | 234 | 232
2016-11-05 04:00 | 228 | 226
2016-11-05 04:30 | 228 | 226
2016-11-05 05:00 | 228 | 226
2016-11-05 05:30 | 228 | 226
2016-11-05 06:00 | 227 | 225
2016-11-05 06:30 | 231 | 229
2016-11-05 07:00 | 245 | 243
2016-11-05 07:30 | 257 | 255
2016-11-05 08:00 | 272 | 270
2016-11-05 08:30 | 282 | 281
2016-11-05 09:00 | 291 | 289
2016-11-05 09:30 | 307 | 305
2016-11-05 10:00 | 308 | 306
2016-11-05 10:30 | 304 | 302
2016-11-05 11:00 | 304 | 302
2016-11-05 11:30 | 309 | 307
2016-11-05 12:00 | 309 | 306
2016-11-05 12:30 | 313 | 311
2016-11-05 13:00 | 310 | 308
2016-11-05 13:30 | 302 | 300
2016-11-05 14:00 | 307 | 305
2016-11-05 14:30 | 312 | 310
2016-11-05 15:00 | 312 | 310
2016-11-05 15:30 | 321 | 318
2016-11-05 16:00 | 330 | 328
2016-11-05 16:30 | 345 | 343
2016-11-05 17:00 | 352 | 350
2016-11-05 17:30 | 331 | 328
2016-11-05 18:00 | 353 | 351
2016-11-05 18:30 | 360 | 358
2016-11-05 19:00 | 342 | 339
2016-11-05 19:30 | 350 | 347
2016-11-05 20:00 | 355 | 353
2016-11-05 20:30 | 346 | 343
2016-11-05 21:00 | 336 | 334
2016-11-05 21:30 | 330 | 327
2016-11-05 22:00 | 321 | 318
2016-11-05 22:30 | 305 | 303
2016-11-05 23:00 | 297 | 294
2016-11-05 23:30 | 285 | 283
2016-11-06 | 274 | 271
2016-11-06 00:30 | 266 | 263
2016-11-06 01:00 | 256 | 254
2016-11-06 01:30 | 251 | 249
2016-11-06 02:00 | 245 | 242
2016-11-06 02:30 | 243 | 240
2016-11-06 03:00 | 238 | 235
2016-11-06 03:30 | 233 | 230
2016-11-06 04:00 | 231 | 228
2016-11-06 04:30 | 231 | 229
2016-11-06 05:00 | 230 | 228
2016-11-06 05:30 | 228 | 226
2016-11-06 06:00 | 229 | 227
2016-11-06 06:30 | 227 | 225
2016-11-06 07:00 | 234 | 232
2016-11-06 07:30 | 245 | 244
2016-11-06 08:00 | 254 | 252
2016-11-06 08:30 | 261 | 259
2016-11-06 09:00 | 270 | 268
2016-11-06 09:30 | 280 | 278
2016-11-06 10:00 | 286 | 284
2016-11-06 10:30 | 294 | 291
2016-11-06 11:00 | 296 | 293
2016-11-06 11:30 | 296 | 294
2016-11-06 12:00 | 297 | 294
2016-11-06 12:30 | 307 | 305
2016-11-06 13:00 | 312 | 309
2016-11-06 13:30 | 303 | 300
2016-11-06 14:00 | 309 | 306
2016-11-06 14:30 | 320 | 317
2016-11-06 15:00 | 327 | 324
2016-11-06 15:30 | 332 | 330
2016-11-06 16:00 | 336 | 333
2016-11-06 16:30 | 350 | 347
2016-11-06 17:00 | 361 | 359
2016-11-06 17:30 | 370 | 368
2016-11-06 18:00 | 376 | 374
2016-11-06 18:30 | 377 | 375
2016-11-06 19:00 | 360 | 358
2016-11-06 19:30 | 360 | 358
2016-11-06 20:00 | 369 | 367
2016-11-06 20:30 | 365 | 363
2016-11-06 21:00 | 359 | 357
2016-11-06 21:30 | 343 | 340
2016-11-06 22:00 | 322 | 320
2016-11-06 22:30 | 302 | 300
2016-11-06 23:00 | 283 | 281
2016-11-06 23:30 | 271 | 270
2016-11-07 | 262 | 261
2016-11-07 00:30 | 253 | 252
2016-11-07 01:00 | 245 | 244
2016-11-07 01:30 | 236 | 235
2016-11-07 02:00 | 238 | 236
2016-11-07 02:30 | 238 | 237
2016-11-07 03:00 | 236 | 234
2016-11-07 03:30 | 234 | 232
2016-11-07 04:00 | 236 | 234
2016-11-07 04:30 | 227 | 226
2016-11-07 05:00 | 200 | 198
2016-11-07 05:30 | 201 | 199
2016-11-07 06:00 | 207 | 205
2016-11-07 06:30 | 227 | 226
2016-11-07 07:00 | 250 | 249
2016-11-07 07:30 | 265 | 264
2016-11-07 08:00 | 269 | 268
2016-11-07 08:30 | 234 | 233
2016-11-07 09:00 | 239 | 238
2016-11-07 09:30 | 242 | 241
2016-11-07 10:00 | 239 | 238
2016-11-07 10:30 | 247 | 245
2016-11-07 11:00 | 239 | 238
2016-11-07 11:30 | 243 | 242
2016-11-07 12:00 | 249 | 247
2016-11-07 12:30 | 252 | 250
2016-11-07 13:00 | 253 | 252
2016-11-07 13:30 | 243 | 241
2016-11-07 14:00 | 212 | 211
2016-11-07 14:30 | 239 | 238
2016-11-07 15:00 | 242 | 241
2016-11-07 15:30 | 215 | 213
2016-11-07 16:00 | 207 | 206
2016-11-07 16:30 | 218 | 216
2016-11-07 17:00 | 199 | 197
2016-11-07 17:30 | 261 | 259
2016-11-07 18:00 | 276 | 274
2016-11-07 18:30 | 294 | 292
2016-11-07 19:00 | 312 | 311
2016-11-07 19:30 | 295 | 293
2016-11-07 20:00 | 288 | 287
2016-11-07 20:30 | 266 | 265
2016-11-07 21:00 | 271 | 270
2016-11-07 21:30 | 251 | 249
2016-11-07 22:00 | 241 | 239
2016-11-07 22:30 | 172 | 170
2016-11-07 23:00 | 168 | 166
2016-11-07 23:30 | 177 | 175
2016-11-08 | 175 | 173
2016-11-08 00:30 | 168 | 167
2016-11-08 01:00 | 158 | 156
2016-11-08 01:30 | 155 | 153
2016-11-08 02:00 | 156 | 155
2016-11-08 02:30 | 155 | 154
2016-11-08 03:00 | 149 | 148
2016-11-08 03:30 | 148 | 147
2016-11-08 04:00 | 148 | 147
2016-11-08 04:30 | 148 | 147
2016-11-08 05:00 | 150 | 149
2016-11-08 05:30 | 142 | 141
2016-11-08 06:00 | 128 | 127
2016-11-08 06:30 | 155 | 154
2016-11-08 07:00 | 171 | 170
2016-11-08 07:30 | 207 | 206
2016-11-08 08:00 | 212 | 211
2016-11-08 08:30 | 213 | 213
2016-11-08 09:00 | 229 | 228
2016-11-08 09:30 | 217 | 216
2016-11-08 10:00 | 212 | 211
2016-11-08 10:30 | 216 | 215
2016-11-08 11:00 | 224 | 223
2016-11-08 11:30 | 226 | 225
2016-11-08 12:00 | 213 | 213
2016-11-08 12:30 | 219 | 218
2016-11-08 13:00 | 216 | 215
2016-11-08 13:30 | 211 | 210
2016-11-08 14:00 | 219 | 218
2016-11-08 14:30 | 219 | 218
2016-11-08 15:00 | 146 | 145
2016-11-08 15:30 | 80 | 79
2016-11-08 16:00 | 89 | 88
2016-11-08 16:30 | 116 | 115
2016-11-08 17:00 | 131 | 130
2016-11-08 17:30 | 122 | 121
2016-11-08 18:00 | 120 | 120
2016-11-08 18:30 | 233 | 232
2016-11-08 19:00 | 278 | 277
2016-11-08 19:30 | 292 | 291
2016-11-08 20:00 | 288 | 288
2016-11-08 20:30 | 277 | 276
2016-11-08 21:00 | 269 | 268
2016-11-08 21:30 | 290 | 289
2016-11-08 22:00 | 328 | 327
2016-11-08 22:30 | 311 | 310
2016-11-08 23:00 | 295 | 295
2016-11-08 23:30 | 281 | 281
2016-11-09 | 272 | 272
2016-11-09 00:30 | 258 | 258
2016-11-09 01:00 | 250 | 250
2016-11-09 01:30 | 244 | 243
2016-11-09 02:00 | 244 | 243
2016-11-09 02:30 | 240 | 240
2016-11-09 03:00 | 238 | 238
2016-11-09 03:30 | 241 | 240
2016-11-09 04:00 | 236 | 235
2016-11-09 04:30 | 239 | 238
2016-11-09 05:00 | 242 | 242
2016-11-09 05:30 | 238 | 238
2016-11-09 06:00 | 240 | 239
2016-11-09 06:30 | 241 | 240
2016-11-09 07:00 | 255 | 254
2016-11-09 07:30 | 295 | 294
2016-11-09 08:00 | 309 | 309
2016-11-09 08:30 | 313 | 313
2016-11-09 09:00 | 308 | 307
2016-11-09 09:30 | 322 | 321
2016-11-09 10:00 | 308 | 307
2016-11-09 10:30 | 272 | 272
2016-11-09 11:00 | 291 | 290
2016-11-09 11:30 | 312 | 312
2016-11-09 12:00 | 319 | 318
2016-11-09 12:30 | 286 | 285
2016-11-09 13:00 | 273 | 271
2016-11-09 13:30 | 271 | 269
2016-11-09 14:00 | 274 | 272
2016-11-09 14:30 | 270 | 268
2016-11-09 15:00 | 261 | 259
2016-11-09 15:30 | 259 | 257
2016-11-09 16:00 | 233 | 231
2016-11-09 16:30 | 273 | 272
2016-11-09 17:00 | 278 | 277
2016-11-09 17:30 | 295 | 294
2016-11-09 18:00 | 310 | 308
2016-11-09 18:30 | 307 | 306
2016-11-09 19:00 | 300 | 299
2016-11-09 19:30 | 303 | 302
2016-11-09 20:00 | 288 | 287
2016-11-09 20:30 | 281 | 280
2016-11-09 21:00 | 282 | 281
2016-11-09 21:30 | 310 | 309
2016-11-09 22:00 | 358 | 357
2016-11-09 22:30 | 326 | 325
2016-11-09 23:00 | 311 | 310
2016-11-09 23:30 | 308 | 307
2016-11-10 | 297 | 296
2016-11-10 00:30 | 277 | 277
2016-11-10 01:00 | 267 | 267
2016-11-10 01:30 | 259 | 258
2016-11-10 02:00 | 249 | 248
2016-11-10 02:30 | 245 | 245
2016-11-10 03:00 | 244 | 243
2016-11-10 03:30 | 243 | 242
2016-11-10 04:00 | 241 | 240
2016-11-10 04:30 | 244 | 244
2016-11-10 05:00 | 253 | 252
2016-11-10 05:30 | 245 | 245
2016-11-10 06:00 | 230 | 229
2016-11-10 06:30 | 235 | 232
2016-11-10 07:00 | 252 | 249
2016-11-10 07:30 | 262 | 259
2016-11-10 08:00 | 276 | 273
2016-11-10 08:30 | 286 | 283
2016-11-10 09:00 | 291 | 288
2016-11-10 09:30 | 278 | 274
2016-11-10 10:00 | 257 | 253
2016-11-10 10:30 | 254 | 251
2016-11-10 11:00 | 260 | 257
2016-11-10 11:30 | 242 | 238
2016-11-10 12:00 | 210 | 206
2016-11-10 12:30 | 224 | 220
2016-11-10 13:00 | 232 | 228
2016-11-10 13:30 | 243 | 240
2016-11-10 14:00 | 250 | 247
2016-11-10 14:30 | 246 | 243
2016-11-10 15:00 | 242 | 239
2016-11-10 15:30 | 208 | 205
2016-11-10 16:00 | 216 | 213
2016-11-10 16:30 | 219 | 216
2016-11-10 17:00 | 220 | 217
2016-11-10 17:30 | 216 | 213
2016-11-10 18:00 | 214 | 211
2016-11-10 18:30 | 262 | 259
2016-11-10 19:00 | 276 | 273
2016-11-10 19:30 | 246 | 242
2016-11-10 20:00 | 244 | 241
2016-11-10 20:30 | 245 | 241
2016-11-10 21:00 | 289 | 285
2016-11-10 21:30 | 281 | 278
2016-11-10 22:00 | 276 | 273
2016-11-10 22:30 | 245 | 241
2016-11-10 23:00 | 237 | 234
2016-11-10 23:30 | 235 | 232
2016-11-11 | 251 | 249
2016-11-11 00:30 | 287 | 285
2016-11-11 01:00 | 276 | 274
2016-11-11 01:30 | 267 | 265
2016-11-11 02:00 | 260 | 259
2016-11-11 02:30 | 257 | 255
2016-11-11 03:00 | 254 | 253
2016-11-11 03:30 | 255 | 254
2016-11-11 04:00 | 254 | 252
2016-11-11 04:30 | 253 | 252
2016-11-11 05:00 | 258 | 257
2016-11-11 05:30 | 263 | 262
2016-11-11 06:00 | 266 | 264
2016-11-11 06:30 | 286 | 285
2016-11-11 07:00 | 291 | 290
2016-11-11 07:30 | 314 | 312
2016-11-11 08:00 | 329 | 327
2016-11-11 08:30 | 330 | 328
2016-11-11 09:00 | 328 | 326
2016-11-11 09:30 | 335 | 333
2016-11-11 10:00 | 336 | 333
2016-11-11 10:30 | 340 | 337
2016-11-11 11:00 | 325 | 322
2016-11-11 11:30 | 351 | 348
2016-11-11 12:00 | 362 | 359
2016-11-11 12:30 | 369 | 366
2016-11-11 13:00 | 311 | 308
2016-11-11 13:30 | 276 | 273
2016-11-11 14:00 | 271 | 268
2016-11-11 14:30 | 260 | 255
2016-11-11 15:00 | 270 | 266
2016-11-11 15:30 | 282 | 279
2016-11-11 16:00 | 287 | 284
2016-11-11 16:30 | 302 | 299
2016-11-11 17:00 | 298 | 295
2016-11-11 17:30 | 341 | 338
2016-11-11 18:00 | 343 | 340
2016-11-11 18:30 | 336 | 333
2016-11-11 19:00 | 307 | 303
2016-11-11 19:30 | 309 | 306
2016-11-11 20:00 | 317 | 315
2016-11-11 20:30 | 311 | 308
2016-11-11 21:00 | 342 | 340
2016-11-11 21:30 | 294 | 291
2016-11-11 22:00 | 287 | 284
2016-11-11 22:30 | 311 | 309
2016-11-11 23:00 | 296 | 293
2016-11-11 23:30 | 287 | 284
2016-11-12 | 296 | 294
2016-11-12 00:30 | 295 | 293
2016-11-12 01:00 | 282 | 280
2016-11-12 01:30 | 275 | 273
2016-11-12 02:00 | 270 | 268
2016-11-12 02:30 | 265 | 263
2016-11-12 03:00 | 259 | 257
2016-11-12 03:30 | 259 | 257
2016-11-12 04:00 | 259 | 257
2016-11-12 04:30 | 261 | 260
2016-11-12 05:00 | 270 | 268
2016-11-12 05:30 | 274 | 272
2016-11-12 06:00 | 273 | 271
2016-11-12 06:30 | 278 | 276
2016-11-12 07:00 | 282 | 280
2016-11-12 07:30 | 301 | 299
2016-11-12 08:00 | 314 | 312
2016-11-12 08:30 | 329 | 327
2016-11-12 09:00 | 338 | 336
2016-11-12 09:30 | 343 | 340
2016-11-12 10:00 | 335 | 333
2016-11-12 10:30 | 348 | 345
2016-11-12 11:00 | 356 | 354
2016-11-12 11:30 | 346 | 344
2016-11-12 12:00 | 349 | 347
2016-11-12 12:30 | 361 | 359
2016-11-12 13:00 | 365 | 363
2016-11-12 13:30 | 339 | 336
2016-11-12 14:00 | 339 | 337
2016-11-12 14:30 | 339 | 336
2016-11-12 15:00 | 326 | 323
2016-11-12 15:30 | 347 | 344
2016-11-12 16:00 | 313 | 311
2016-11-12 16:30 | 326 | 323
2016-11-12 17:00 | 334 | 332
2016-11-12 17:30 | 297 | 295
2016-11-12 18:00 | 315 | 313
2016-11-12 18:30 | 343 | 341
2016-11-12 19:00 | 365 | 363
2016-11-12 19:30 | 364 | 362
2016-11-12 20:00 | 350 | 348
2016-11-12 20:30 | 336 | 334
2016-11-12 21:00 | 368 | 365
2016-11-12 21:30 | 359 | 356
2016-11-12 22:00 | 345 | 343
2016-11-12 22:30 | 334 | 331
2016-11-12 23:00 | 306 | 303
2016-11-12 23:30 | 308 | 306
2016-11-13 | 300 | 298
2016-11-13 00:30 | 293 | 291
2016-11-13 01:00 | 278 | 276
2016-11-13 01:30 | 267 | 265
2016-11-13 02:00 | 259 | 258
2016-11-13 02:30 | 254 | 253
2016-11-13 03:00 | 246 | 245
2016-11-13 03:30 | 244 | 242
2016-11-13 04:00 | 243 | 241
2016-11-13 04:30 | 241 | 240
2016-11-13 05:00 | 237 | 236
2016-11-13 05:30 | 236 | 234
2016-11-13 06:00 | 234 | 232
2016-11-13 06:30 | 239 | 237
2016-11-13 07:00 | 248 | 246
2016-11-13 07:30 | 257 | 256
2016-11-13 08:00 | 260 | 259
2016-11-13 08:30 | 274 | 272
2016-11-13 09:00 | 285 | 283
2016-11-13 09:30 | 299 | 298
2016-11-13 10:00 | 316 | 314
2016-11-13 10:30 | 327 | 324
2016-11-13 11:00 | 324 | 322
2016-11-13 11:30 | 298 | 295
2016-11-13 12:00 | 304 | 302
2016-11-13 12:30 | 309 | 307
2016-11-13 13:00 | 316 | 313
2016-11-13 13:30 | 313 | 311
2016-11-13 14:00 | 319 | 317
2016-11-13 14:30 | 297 | 294
2016-11-13 15:00 | 248 | 244
2016-11-13 15:30 | 243 | 240
2016-11-13 16:00 | 212 | 208
2016-11-13 16:30 | 210 | 208
2016-11-13 17:00 | 257 | 255
2016-11-13 17:30 | 258 | 256
2016-11-13 18:00 | 288 | 286
2016-11-13 18:30 | 294 | 292
2016-11-13 19:00 | 283 | 281
2016-11-13 19:30 | 290 | 289
2016-11-13 20:00 | 291 | 290
2016-11-13 20:30 | 285 | 283
2016-11-13 21:00 | 275 | 273
2016-11-13 21:30 | 257 | 255
2016-11-13 22:00 | 268 | 266
2016-11-13 22:30 | 289 | 287
2016-11-13 23:00 | 286 | 283
2016-11-13 23:30 | 271 | 269
2016-11-14 | 231 | 228
2016-11-14 00:30 | 239 | 237
2016-11-14 01:00 | 237 | 236
2016-11-14 01:30 | 228 | 227
2016-11-14 02:00 | 224 | 222
2016-11-14 02:30 | 222 | 221
2016-11-14 03:00 | 222 | 221
2016-11-14 03:30 | 223 | 221
2016-11-14 04:00 | 219 | 218
2016-11-14 04:30 | 220 | 218
2016-11-14 05:00 | 227 | 226
2016-11-14 05:30 | 230 | 229
2016-11-14 06:00 | 234 | 232
2016-11-14 06:30 | 241 | 240
2016-11-14 07:00 | 262 | 260
2016-11-14 07:30 | 297 | 296
2016-11-14 08:00 | 315 | 313
2016-11-14 08:30 | 320 | 319
2016-11-14 09:00 | 324 | 323
2016-11-14 09:30 | 315 | 313
2016-11-14 10:00 | 300 | 297
2016-11-14 10:30 | 304 | 302
2016-11-14 11:00 | 303 | 301
2016-11-14 11:30 | 284 | 281
2016-11-14 12:00 | 252 | 250
2016-11-14 12:30 | 235 | 232
2016-11-14 13:00 | 259 | 257
2016-11-14 13:30 | 259 | 256
2016-11-14 14:00 | 270 | 268
2016-11-14 14:30 | 272 | 269
2016-11-14 15:00 | 296 | 294
2016-11-14 15:30 | 292 | 290
2016-11-14 16:00 | 285 | 283
2016-11-14 16:30 | 272 | 270
2016-11-14 17:00 | 267 | 265
2016-11-14 17:30 | 305 | 303
2016-11-14 18:00 | 320 | 318
2016-11-14 18:30 | 343 | 341
2016-11-14 19:00 | 291 | 289
2016-11-14 19:30 | 315 | 312
2016-11-14 20:00 | 281 | 279
2016-11-14 20:30 | 250 | 247
2016-11-14 21:00 | 288 | 285
2016-11-14 21:30 | 272 | 270
2016-11-14 22:00 | 252 | 249
2016-11-14 22:30 | 150 | 146
2016-11-14 23:00 | 155 | 152
2016-11-14 23:30 | 173 | 170
2016-11-15 | 225 | 223
2016-11-15 00:30 | 250 | 248
2016-11-15 01:00 | 239 | 237
2016-11-15 01:30 | 235 | 233
2016-11-15 02:00 | 234 | 233
2016-11-15 02:30 | 235 | 233
2016-11-15 03:00 | 226 | 224
2016-11-15 03:30 | 221 | 219
2016-11-15 04:00 | 220 | 218
2016-11-15 04:30 | 219 | 217
2016-11-15 05:00 | 217 | 215
2016-11-15 05:30 | 224 | 222
2016-11-15 06:00 | 232 | 230
2016-11-15 06:30 | 250 | 248
2016-11-15 07:00 | 268 | 266
2016-11-15 07:30 | 274 | 272
2016-11-15 08:00 | 281 | 280
2016-11-15 08:30 | 286 | 285
2016-11-15 09:00 | 285 | 283
2016-11-15 09:30 | 291 | 289
2016-11-15 10:00 | 291 | 289
2016-11-15 10:30 | 296 | 294
2016-11-15 11:00 | 306 | 304
2016-11-15 11:30 | 299 | 297
2016-11-15 12:00 | 299 | 297
2016-11-15 12:30 | 306 | 304
2016-11-15 13:00 | 309 | 307
2016-11-15 13:30 | 288 | 286
2016-11-15 14:00 | 278 | 275
2016-11-15 14:30 | 279 | 275
2016-11-15 15:00 | 281 | 278
2016-11-15 15:30 | 286 | 283
2016-11-15 16:00 | 294 | 291
2016-11-15 16:30 | 305 | 302
2016-11-15 17:00 | 320 | 317
2016-11-15 17:30 | 343 | 341
2016-11-15 18:00 | 345 | 343
2016-11-15 18:30 | 361 | 359
2016-11-15 19:00 | 372 | 370
2016-11-15 19:30 | 354 | 352
2016-11-15 20:00 | 360 | 358
2016-11-15 20:30 | 356 | 354
2016-11-15 21:00 | 341 | 339
2016-11-15 21:30 | 326 | 324
2016-11-15 22:00 | 308 | 306
2016-11-15 22:30 | 277 | 275
2016-11-15 23:00 | 267 | 265
2016-11-15 23:30 | 255 | 253
2016-11-16 | 247 | 244
2016-11-16 00:30 | 241 | 239
2016-11-16 01:00 | 233 | 230
2016-11-16 01:30 | 230 | 228
2016-11-16 02:00 | 220 | 218
2016-11-16 02:30 | 215 | 212
2016-11-16 03:00 | 216 | 213
2016-11-16 03:30 | 211 | 208
2016-11-16 04:00 | 208 | 205
2016-11-16 04:30 | 207 | 204
2016-11-16 05:00 | 213 | 210
2016-11-16 05:30 | 218 | 215
2016-11-16 06:00 | 222 | 220
2016-11-16 06:30 | 253 | 252
2016-11-16 07:00 | 276 | 275
2016-11-16 07:30 | 287 | 285
2016-11-16 08:00 | 299 | 297
2016-11-16 08:30 | 308 | 306
2016-11-16 09:00 | 309 | 307
2016-11-16 09:30 | 310 | 308
2016-11-16 10:00 | 311 | 309
2016-11-16 10:30 | 313 | 311
2016-11-16 11:00 | 313 | 311
2016-11-16 11:30 | 310 | 308
2016-11-16 12:00 | 314 | 312
2016-11-16 12:30 | 322 | 319
2016-11-16 13:00 | 326 | 324
2016-11-16 13:30 | 325 | 323
2016-11-16 14:00 | 332 | 330
2016-11-16 14:30 | 336 | 333
2016-11-16 15:00 | 348 | 345
2016-11-16 15:30 | 346 | 343
2016-11-16 16:00 | 350 | 347
2016-11-16 16:30 | 354 | 352
2016-11-16 17:00 | 356 | 354
2016-11-16 17:30 | 357 | 355
2016-11-16 18:00 | 354 | 352
2016-11-16 18:30 | 360 | 358
2016-11-16 19:00 | 371 | 369
2016-11-16 19:30 | 379 | 377
2016-11-16 20:00 | 370 | 368
2016-11-16 20:30 | 358 | 356
2016-11-16 21:00 | 341 | 338
2016-11-16 21:30 | 330 | 328
2016-11-16 22:00 | 309 | 306
2016-11-16 22:30 | 291 | 288
2016-11-16 23:00 | 279 | 277
2016-11-16 23:30 | 266 | 264
2016-11-17 | 255 | 253
2016-11-17 00:30 | 250 | 248
2016-11-17 01:00 | 241 | 238
2016-11-17 01:30 | 233 | 230
2016-11-17 02:00 | 229 | 226
2016-11-17 02:30 | 224 | 221
2016-11-17 03:00 | 222 | 219
2016-11-17 03:30 | 222 | 219
2016-11-17 04:00 | 222 | 219
2016-11-17 04:30 | 227 | 224
2016-11-17 05:00 | 230 | 227
2016-11-17 05:30 | 237 | 234
2016-11-17 06:00 | 242 | 239
2016-11-17 06:30 | 262 | 260
2016-11-17 07:00 | 268 | 266
2016-11-17 07:30 | 297 | 295
2016-11-17 08:00 | 311 | 309
2016-11-17 08:30 | 313 | 311
2016-11-17 09:00 | 317 | 315
2016-11-17 09:30 | 317 | 314
2016-11-17 10:00 | 315 | 313
2016-11-17 10:30 | 315 | 313
2016-11-17 11:00 | 315 | 312
2016-11-17 11:30 | 311 | 309
2016-11-17 12:00 | 316 | 313
2016-11-17 12:30 | 321 | 319
2016-11-17 13:00 | 316 | 313
2016-11-17 13:30 | 311 | 308
2016-11-17 14:00 | 305 | 302
2016-11-17 14:30 | 313 | 310
2016-11-17 15:00 | 313 | 310
2016-11-17 15:30 | 323 | 320
2016-11-17 16:00 | 333 | 330
2016-11-17 16:30 | 346 | 343
2016-11-17 17:00 | 351 | 348
2016-11-17 17:30 | 348 | 345
2016-11-17 18:00 | 347 | 344
2016-11-17 18:30 | 350 | 347
2016-11-17 19:00 | 365 | 362
2016-11-17 19:30 | 368 | 366
2016-11-17 20:00 | 357 | 355
2016-11-17 20:30 | 348 | 345
2016-11-17 21:00 | 339 | 337
2016-11-17 21:30 | 325 | 322
2016-11-17 22:00 | 313 | 311
2016-11-17 22:30 | 298 | 295
2016-11-17 23:00 | 276 | 274
2016-11-17 23:30 | 265 | 263
2016-11-18 | 256 | 254
2016-11-18 00:30 | 249 | 247
2016-11-18 01:00 | 237 | 235
2016-11-18 01:30 | 230 | 227
2016-11-18 02:00 | 229 | 227
2016-11-18 02:30 | 221 | 218
2016-11-18 03:00 | 216 | 214
2016-11-18 03:30 | 212 | 210
2016-11-18 04:00 | 210 | 207
2016-11-18 04:30 | 210 | 208
2016-11-18 05:00 | 214 | 211
2016-11-18 05:30 | 217 | 215
2016-11-18 06:00 | 221 | 219
2016-11-18 06:30 | 244 | 242
2016-11-18 07:00 | 238 | 235
2016-11-18 07:30 | 271 | 269
2016-11-18 08:00 | 293 | 291
2016-11-18 08:30 | 317 | 316
2016-11-18 09:00 | 320 | 318
2016-11-18 09:30 | 308 | 306
2016-11-18 10:00 | 247 | 244
2016-11-18 10:30 | 242 | 239
2016-11-18 11:00 | 245 | 242
2016-11-18 11:30 | 247 | 245
2016-11-18 12:00 | 247 | 244
2016-11-18 12:30 | 246 | 243
2016-11-18 13:00 | 254 | 251
2016-11-18 13:30 | 216 | 214
2016-11-18 14:00 | 178 | 175
2016-11-18 14:30 | 147 | 145
2016-11-18 15:00 | 158 | 156
2016-11-18 15:30 | 147 | 146
2016-11-18 16:00 | 149 | 147
2016-11-18 16:30 | 171 | 170
2016-11-18 17:00 | 192 | 191
2016-11-18 17:30 | 249 | 247
2016-11-18 18:00 | 257 | 255
2016-11-18 18:30 | 265 | 263
2016-11-18 19:00 | 250 | 248
2016-11-18 19:30 | 252 | 250
2016-11-18 20:00 | 253 | 251
2016-11-18 20:30 | 254 | 252
2016-11-18 21:00 | 246 | 244
2016-11-18 21:30 | 257 | 256
2016-11-18 22:00 | 304 | 302
2016-11-18 22:30 | 280 | 279
2016-11-18 23:00 | 273 | 272
2016-11-18 23:30 | 262 | 261
2016-11-19 | 254 | 253
2016-11-19 00:30 | 247 | 246
2016-11-19 01:00 | 234 | 233
2016-11-19 01:30 | 230 | 229
2016-11-19 02:00 | 225 | 223
2016-11-19 02:30 | 218 | 217
2016-11-19 03:00 | 211 | 210
2016-11-19 03:30 | 211 | 210
2016-11-19 04:00 | 209 | 208
2016-11-19 04:30 | 204 | 202
2016-11-19 05:00 | 204 | 203
2016-11-19 05:30 | 205 | 204
2016-11-19 06:00 | 203 | 202
2016-11-19 06:30 | 210 | 209
2016-11-19 07:00 | 229 | 228
2016-11-19 07:30 | 234 | 234
2016-11-19 08:00 | 243 | 242
2016-11-19 08:30 | 253 | 252
2016-11-19 09:00 | 265 | 264
2016-11-19 09:30 | 270 | 269
2016-11-19 10:00 | 269 | 268
2016-11-19 10:30 | 275 | 274
2016-11-19 11:00 | 274 | 272
2016-11-19 11:30 | 268 | 266
2016-11-19 12:00 | 263 | 261
2016-11-19 12:30 | 271 | 270
2016-11-19 13:00 | 271 | 270
2016-11-19 13:30 | 269 | 268
2016-11-19 14:00 | 273 | 272
2016-11-19 14:30 | 281 | 280
2016-11-19 15:00 | 280 | 278
2016-11-19 15:30 | 286 | 285
2016-11-19 16:00 | 296 | 294
2016-11-19 16:30 | 302 | 301
2016-11-19 17:00 | 307 | 304
2016-11-19 17:30 | 313 | 310
2016-11-19 18:00 | 316 | 314
2016-11-19 18:30 | 320 | 318
2016-11-19 19:00 | 330 | 328
2016-11-19 19:30 | 334 | 332
2016-11-19 20:00 | 324 | 321
2016-11-19 20:30 | 318 | 316
2016-11-19 21:00 | 307 | 304
2016-11-19 21:30 | 295 | 292
2016-11-19 22:00 | 287 | 285
2016-11-19 22:30 | 280 | 278
2016-11-19 23:00 | 266 | 264
2016-11-19 23:30 | 258 | 256
2016-11-20 | 251 | 249
2016-11-20 00:30 | 245 | 243
2016-11-20 01:00 | 235 | 233
2016-11-20 01:30 | 230 | 228
2016-11-20 02:00 | 224 | 221
2016-11-20 02:30 | 214 | 212
2016-11-20 03:00 | 208 | 207
2016-11-20 03:30 | 207 | 206
2016-11-20 04:00 | 205 | 204
2016-11-20 04:30 | 203 | 202
2016-11-20 05:00 | 205 | 204
2016-11-20 05:30 | 204 | 203
2016-11-20 06:00 | 202 | 201
2016-11-20 06:30 | 208 | 207
2016-11-20 07:00 | 220 | 219
2016-11-20 07:30 | 226 | 225
2016-11-20 08:00 | 234 | 233
2016-11-20 08:30 | 243 | 242
2016-11-20 09:00 | 250 | 249
2016-11-20 09:30 | 258 | 257
2016-11-20 10:00 | 264 | 262
2016-11-20 10:30 | 267 | 265
2016-11-20 11:00 | 264 | 262
2016-11-20 11:30 | 263 | 262
2016-11-20 12:00 | 269 | 268
2016-11-20 12:30 | 268 | 267
2016-11-20 13:00 | 276 | 274
2016-11-20 13:30 | 276 | 275
2016-11-20 14:00 | 277 | 275
2016-11-20 14:30 | 282 | 281
2016-11-20 15:00 | 289 | 287
2016-11-20 15:30 | 298 | 297
2016-11-20 16:00 | 302 | 301
2016-11-20 16:30 | 306 | 305
2016-11-20 17:00 | 311 | 310
2016-11-20 17:30 | 319 | 318
2016-11-20 18:00 | 326 | 325
2016-11-20 18:30 | 335 | 334
2016-11-20 19:00 | 343 | 341
2016-11-20 19:30 | 344 | 342
2016-11-20 20:00 | 340 | 338
2016-11-20 20:30 | 321 | 319
2016-11-20 21:00 | 320 | 318
2016-11-20 21:30 | 310 | 308
2016-11-20 22:00 | 297 | 295
2016-11-20 22:30 | 283 | 282
2016-11-20 23:00 | 264 | 263
2016-11-20 23:30 | 255 | 253
2016-11-21 | 246 | 244
2016-11-21 00:30 | 243 | 241
2016-11-21 01:00 | 232 | 230
2016-11-21 01:30 | 226 | 226
2016-11-21 02:00 | 217 | 216
2016-11-21 02:30 | 212 | 211
2016-11-21 03:00 | 209 | 209
2016-11-21 03:30 | 209 | 209
2016-11-21 04:00 | 207 | 207
2016-11-21 04:30 | 203 | 203
2016-11-21 05:00 | 179 | 179
2016-11-21 05:30 | 184 | 184
2016-11-21 06:00 | 184 | 183
2016-11-21 06:30 | 204 | 204
2016-11-21 07:00 | 228 | 228
2016-11-21 07:30 | 249 | 248
2016-11-21 08:00 | 264 | 263
2016-11-21 08:30 | 249 | 248
2016-11-21 09:00 | 221 | 219
2016-11-21 09:30 | 231 | 229
2016-11-21 10:00 | 226 | 225
2016-11-21 10:30 | 229 | 227
2016-11-21 11:00 | 228 | 226
2016-11-21 11:30 | 229 | 228
2016-11-21 12:00 | 230 | 229
2016-11-21 12:30 | 232 | 231
2016-11-21 13:00 | 232 | 230
2016-11-21 13:30 | 228 | 226
2016-11-21 14:00 | 230 | 228
2016-11-21 14:30 | 226 | 224
2016-11-21 15:00 | 225 | 223
2016-11-21 15:30 | 226 | 224
2016-11-21 16:00 | 230 | 228
2016-11-21 16:30 | 248 | 247
2016-11-21 17:00 | 257 | 256
2016-11-21 17:30 | 261 | 260
2016-11-21 18:00 | 260 | 258
2016-11-21 18:30 | 263 | 262
2016-11-21 19:00 | 279 | 278
2016-11-21 19:30 | 283 | 281
2016-11-21 20:00 | 269 | 268
2016-11-21 20:30 | 259 | 257
2016-11-21 21:00 | 244 | 243
2016-11-21 21:30 | 225 | 223
2016-11-21 22:00 | 207 | 205
2016-11-21 22:30 | 195 | 193
2016-11-21 23:00 | 173 | 171
2016-11-21 23:30 | 164 | 163
2016-11-22 | 153 | 152
2016-11-22 00:30 | 153 | 152
2016-11-22 01:00 | 143 | 142
2016-11-22 01:30 | 136 | 135
2016-11-22 02:00 | 132 | 131
2016-11-22 02:30 | 127 | 126
2016-11-22 03:00 | 126 | 125
2016-11-22 03:30 | 130 | 129
2016-11-22 04:00 | 136 | 135
2016-11-22 04:30 | 140 | 139
2016-11-22 05:00 | 142 | 141
2016-11-22 05:30 | 150 | 149
2016-11-22 06:00 | 154 | 154
2016-11-22 06:30 | 173 | 172
2016-11-22 07:00 | 200 | 199
2016-11-22 07:30 | 217 | 216
2016-11-22 08:00 | 225 | 225
2016-11-22 08:30 | 231 | 230
2016-11-22 09:00 | 231 | 230
2016-11-22 09:30 | 235 | 234
2016-11-22 10:00 | 235 | 234
2016-11-22 10:30 | 236 | 235
2016-11-22 11:00 | 237 | 236
2016-11-22 11:30 | 229 | 228
2016-11-22 12:00 | 242 | 241
2016-11-22 12:30 | 246 | 245
2016-11-22 13:00 | 247 | 246
2016-11-22 13:30 | 261 | 260
2016-11-22 14:00 | 268 | 267
2016-11-22 14:30 | 272 | 271
2016-11-22 15:00 | 223 | 221
2016-11-22 15:30 | 222 | 221
2016-11-22 16:00 | 204 | 202
2016-11-22 16:30 | 208 | 206
2016-11-22 17:00 | 236 | 234
2016-11-22 17:30 | 250 | 249
2016-11-22 18:00 | 246 | 244
2016-11-22 18:30 | 247 | 246
2016-11-22 19:00 | 260 | 258
2016-11-22 19:30 | 266 | 264
2016-11-22 20:00 | 258 | 257
2016-11-22 20:30 | 248 | 246
2016-11-22 21:00 | 233 | 232
2016-11-22 21:30 | 257 | 256
2016-11-22 22:00 | 337 | 336
2016-11-22 22:30 | 325 | 324
2016-11-22 23:00 | 294 | 293
2016-11-22 23:30 | 290 | 289
2016-11-23 | 281 | 280
2016-11-23 00:30 | 271 | 270
2016-11-23 01:00 | 265 | 264
2016-11-23 01:30 | 261 | 260
2016-11-23 02:00 | 255 | 254
2016-11-23 02:30 | 250 | 249
2016-11-23 03:00 | 249 | 248
2016-11-23 03:30 | 250 | 249
2016-11-23 04:00 | 245 | 244
2016-11-23 04:30 | 244 | 244
2016-11-23 05:00 | 247 | 246
2016-11-23 05:30 | 254 | 253
2016-11-23 06:00 | 261 | 260
2016-11-23 06:30 | 284 | 283
2016-11-23 07:00 | 304 | 303
2016-11-23 07:30 | 321 | 320
2016-11-23 08:00 | 332 | 331
2016-11-23 08:30 | 345 | 343
2016-11-23 09:00 | 345 | 344
2016-11-23 09:30 | 330 | 329
2016-11-23 10:00 | 340 | 339
2016-11-23 10:30 | 311 | 310
2016-11-23 11:00 | 317 | 315
2016-11-23 11:30 | 336 | 335
2016-11-23 12:00 | 338 | 336
2016-11-23 12:30 | 344 | 343
2016-11-23 13:00 | 308 | 306
2016-11-23 13:30 | 318 | 316
2016-11-23 14:00 | 374 | 372
2016-11-23 14:30 | 379 | 377
2016-11-23 15:00 | 374 | 372
2016-11-23 15:30 | 373 | 372
2016-11-23 16:00 | 363 | 361
2016-11-23 16:30 | 346 | 344
2016-11-23 17:00 | 360 | 358
2016-11-23 17:30 | 362 | 361
2016-11-23 18:00 | 398 | 396
2016-11-23 18:30 | 404 | 402
2016-11-23 19:00 | 415 | 413
2016-11-23 19:30 | 422 | 420
2016-11-23 20:00 | 416 | 413
2016-11-23 20:30 | 404 | 402
2016-11-23 21:00 | 386 | 384
2016-11-23 21:30 | 374 | 371
2016-11-23 22:00 | 357 | 355
2016-11-23 22:30 | 335 | 333
2016-11-23 23:00 | 316 | 313
2016-11-23 23:30 | 301 | 300
2016-11-24 | 290 | 288
2016-11-24 00:30 | 282 | 281
2016-11-24 01:00 | 276 | 275
2016-11-24 01:30 | 270 | 268
2016-11-24 02:00 | 262 | 261
2016-11-24 02:30 | 254 | 253
2016-11-24 03:00 | 248 | 247
2016-11-24 03:30 | 248 | 246
2016-11-24 04:00 | 245 | 243
2016-11-24 04:30 | 245 | 244
2016-11-24 05:00 | 246 | 244
2016-11-24 05:30 | 251 | 249
2016-11-24 06:00 | 263 | 261
2016-11-24 06:30 | 285 | 283
2016-11-24 07:00 | 304 | 302
2016-11-24 07:30 | 327 | 326
2016-11-24 08:00 | 349 | 347
2016-11-24 08:30 | 357 | 355
2016-11-24 09:00 | 355 | 353
2016-11-24 09:30 | 352 | 349
2016-11-24 10:00 | 343 | 340
2016-11-24 10:30 | 333 | 329
2016-11-24 11:00 | 333 | 330
2016-11-24 11:30 | 335 | 332
2016-11-24 12:00 | 341 | 338
2016-11-24 12:30 | 349 | 344
2016-11-24 13:00 | 355 | 350
2016-11-24 13:30 | 334 | 328
2016-11-24 14:00 | 335 | 328
2016-11-24 14:30 | 337 | 331
2016-11-24 15:00 | 322 | 316
2016-11-24 15:30 | 257 | 253
2016-11-24 16:00 | 261 | 258
2016-11-24 16:30 | 271 | 268
2016-11-24 17:00 | 293 | 290
2016-11-24 17:30 | 314 | 312
2016-11-24 18:00 | 321 | 317
2016-11-24 18:30 | 324 | 320
2016-11-24 19:00 | 300 | 297
2016-11-24 19:30 | 304 | 302
2016-11-24 20:00 | 292 | 289
2016-11-24 20:30 | 326 | 323
2016-11-24 21:00 | 379 | 377
2016-11-24 21:30 | 376 | 374
2016-11-24 22:00 | 368 | 366
2016-11-24 22:30 | 340 | 337
2016-11-24 23:00 | 328 | 325
2016-11-24 23:30 | 313 | 310
2016-11-25 | 300 | 297
2016-11-25 00:30 | 287 | 284
2016-11-25 01:00 | 274 | 273
2016-11-25 01:30 | 273 | 272
2016-11-25 02:00 | 267 | 265
2016-11-25 02:30 | 262 | 261
2016-11-25 03:00 | 258 | 256
2016-11-25 03:30 | 254 | 252
2016-11-25 04:00 | 249 | 247
2016-11-25 04:30 | 250 | 249
2016-11-25 05:00 | 254 | 252
2016-11-25 05:30 | 260 | 258
2016-11-25 06:00 | 265 | 264
2016-11-25 06:30 | 287 | 286
2016-11-25 07:00 | 307 | 306
2016-11-25 07:30 | 324 | 323
2016-11-25 08:00 | 340 | 339
2016-11-25 08:30 | 347 | 346
2016-11-25 09:00 | 348 | 346
2016-11-25 09:30 | 350 | 348
2016-11-25 10:00 | 346 | 344
2016-11-25 10:30 | 338 | 336
2016-11-25 11:00 | 334 | 332
2016-11-25 11:30 | 334 | 332
2016-11-25 12:00 | 340 | 339
2016-11-25 12:30 | 342 | 340
2016-11-25 13:00 | 342 | 340
2016-11-25 13:30 | 357 | 355
2016-11-25 14:00 | 376 | 374
2016-11-25 14:30 | 384 | 381
2016-11-25 15:00 | 380 | 376
2016-11-25 15:30 | 382 | 379
2016-11-25 16:00 | 390 | 387
2016-11-25 16:30 | 395 | 392
2016-11-25 17:00 | 409 | 406
2016-11-25 17:30 | 383 | 380
2016-11-25 18:00 | 378 | 376
2016-11-25 18:30 | 378 | 375
2016-11-25 19:00 | 374 | 372
2016-11-25 19:30 | 380 | 378
2016-11-25 20:00 | 375 | 372
2016-11-25 20:30 | 363 | 361
2016-11-25 21:00 | 354 | 351
2016-11-25 21:30 | 335 | 332
2016-11-25 22:00 | 325 | 323
2016-11-25 22:30 | 313 | 310
2016-11-25 23:00 | 294 | 292
2016-11-25 23:30 | 278 | 277
2016-11-26 | 264 | 262
2016-11-26 00:30 | 257 | 255
2016-11-26 01:00 | 243 | 242
2016-11-26 01:30 | 239 | 238
2016-11-26 02:00 | 234 | 233
2016-11-26 02:30 | 227 | 225
2016-11-26 03:00 | 224 | 222
2016-11-26 03:30 | 223 | 221
2016-11-26 04:00 | 219 | 218
2016-11-26 04:30 | 216 | 214
2016-11-26 05:00 | 217 | 216
2016-11-26 05:30 | 219 | 218
2016-11-26 06:00 | 219 | 217
2016-11-26 06:30 | 228 | 226
2016-11-26 07:00 | 239 | 237
2016-11-26 07:30 | 256 | 254
2016-11-26 08:00 | 266 | 264
2016-11-26 08:30 | 279 | 278
2016-11-26 09:00 | 291 | 290
2016-11-26 09:30 | 301 | 300
2016-11-26 10:00 | 291 | 290
2016-11-26 10:30 | 289 | 288
2016-11-26 11:00 | 287 | 286
2016-11-26 11:30 | 286 | 286
2016-11-26 12:00 | 289 | 288
2016-11-26 12:30 | 292 | 291
2016-11-26 13:00 | 292 | 291
2016-11-26 13:30 | 297 | 296
2016-11-26 14:00 | 302 | 301
2016-11-26 14:30 | 308 | 308
2016-11-26 15:00 | 305 | 304
2016-11-26 15:30 | 311 | 310
2016-11-26 16:00 | 324 | 323
2016-11-26 16:30 | 329 | 329
2016-11-26 17:00 | 347 | 347
2016-11-26 17:30 | 350 | 350
2016-11-26 18:00 | 357 | 357
2016-11-26 18:30 | 361 | 361
2016-11-26 19:00 | 370 | 369
2016-11-26 19:30 | 373 | 373
2016-11-26 20:00 | 361 | 361
2016-11-26 20:30 | 349 | 349
2016-11-26 21:00 | 340 | 340
2016-11-26 21:30 | 332 | 331
2016-11-26 22:00 | 322 | 322
2016-11-26 22:30 | 306 | 306
2016-11-26 23:00 | 291 | 291
2016-11-26 23:30 | 274 | 273
2016-11-27 | 263 | 262
2016-11-27 00:30 | 254 | 253
2016-11-27 01:00 | 243 | 243
2016-11-27 01:30 | 234 | 234
2016-11-27 02:00 | 228 | 227
2016-11-27 02:30 | 222 | 222
2016-11-27 03:00 | 218 | 218
2016-11-27 03:30 | 217 | 216
2016-11-27 04:00 | 214 | 213
2016-11-27 04:30 | 214 | 213
2016-11-27 05:00 | 213 | 213
2016-11-27 05:30 | 212 | 212
2016-11-27 06:00 | 212 | 212
2016-11-27 06:30 | 220 | 220
2016-11-27 07:00 | 230 | 230
2016-11-27 07:30 | 241 | 240
2016-11-27 08:00 | 250 | 249
2016-11-27 08:30 | 261 | 261
2016-11-27 09:00 | 278 | 277
2016-11-27 09:30 | 285 | 285
2016-11-27 10:00 | 278 | 278
2016-11-27 10:30 | 280 | 280
2016-11-27 11:00 | 282 | 281
2016-11-27 11:30 | 281 | 281
2016-11-27 12:00 | 287 | 286
2016-11-27 12:30 | 297 | 297
2016-11-27 13:00 | 301 | 300
2016-11-27 13:30 | 305 | 304
2016-11-27 14:00 | 306 | 306
2016-11-27 14:30 | 308 | 308
2016-11-27 15:00 | 305 | 304
2016-11-27 15:30 | 311 | 311
2016-11-27 16:00 | 318 | 318
2016-11-27 16:30 | 324 | 324
2016-11-27 17:00 | 342 | 342
2016-11-27 17:30 | 351 | 350
2016-11-27 18:00 | 358 | 357
2016-11-27 18:30 | 360 | 359
2016-11-27 19:00 | 366 | 365
2016-11-27 19:30 | 374 | 373
2016-11-27 20:00 | 366 | 365
2016-11-27 20:30 | 355 | 353
2016-11-27 21:00 | 346 | 344
2016-11-27 21:30 | 331 | 329
2016-11-27 22:00 | 315 | 313
2016-11-27 22:30 | 295 | 294
2016-11-27 23:00 | 284 | 283
2016-11-27 23:30 | 270 | 268
2016-11-28 | 257 | 256
2016-11-28 00:30 | 251 | 249
2016-11-28 01:00 | 247 | 246
2016-11-28 01:30 | 238 | 237
2016-11-28 02:00 | 232 | 232
2016-11-28 02:30 | 230 | 230
2016-11-28 03:00 | 226 | 226
2016-11-28 03:30 | 218 | 217
2016-11-28 04:00 | 220 | 219
2016-11-28 04:30 | 223 | 222
2016-11-28 05:00 | 224 | 223
2016-11-28 05:30 | 231 | 230
2016-11-28 06:00 | 239 | 239
2016-11-28 06:30 | 264 | 263
2016-11-28 07:00 | 267 | 266
2016-11-28 07:30 | 298 | 298
2016-11-28 08:00 | 313 | 312
2016-11-28 08:30 | 325 | 324
2016-11-28 09:00 | 331 | 331
2016-11-28 09:30 | 325 | 324
2016-11-28 10:00 | 326 | 325
2016-11-28 10:30 | 330 | 330
2016-11-28 11:00 | 330 | 329
2016-11-28 11:30 | 331 | 330
2016-11-28 12:00 | 332 | 331
2016-11-28 12:30 | 339 | 338
2016-11-28 13:00 | 351 | 350
2016-11-28 13:30 | 354 | 354
2016-11-28 14:00 | 357 | 356
2016-11-28 14:30 | 361 | 360
2016-11-28 15:00 | 351 | 350
2016-11-28 15:30 | 344 | 344
2016-11-28 16:00 | 356 | 356
2016-11-28 16:30 | 352 | 351
2016-11-28 17:00 | 367 | 366
2016-11-28 17:30 | 371 | 371
2016-11-28 18:00 | 370 | 369
2016-11-28 18:30 | 374 | 373
2016-11-28 19:00 | 385 | 385
2016-11-28 19:30 | 381 | 381
2016-11-28 20:00 | 366 | 366
2016-11-28 20:30 | 360 | 359
2016-11-28 21:00 | 348 | 347
2016-11-28 21:30 | 345 | 344
2016-11-28 22:00 | 330 | 330
2016-11-28 22:30 | 311 | 310
2016-11-28 23:00 | 295 | 294
2016-11-28 23:30 | 278 | 277
2016-11-29 | 269 | 268
2016-11-29 00:30 | 262 | 260
2016-11-29 01:00 | 252 | 251
2016-11-29 01:30 | 247 | 245
2016-11-29 02:00 | 241 | 240
2016-11-29 02:30 | 236 | 235
2016-11-29 03:00 | 230 | 230
2016-11-29 03:30 | 230 | 230
2016-11-29 04:00 | 230 | 230
2016-11-29 04:30 | 230 | 230
2016-11-29 05:00 | 234 | 233
2016-11-29 05:30 | 242 | 242
2016-11-29 06:00 | 242 | 241
2016-11-29 06:30 | 261 | 260
2016-11-29 07:00 | 279 | 278
2016-11-29 07:30 | 297 | 296
2016-11-29 08:00 | 308 | 308
2016-11-29 08:30 | 320 | 320
2016-11-29 09:00 | 326 | 325
2016-11-29 09:30 | 343 | 342
2016-11-29 10:00 | 337 | 337
2016-11-29 10:30 | 320 | 320
2016-11-29 11:00 | 317 | 317
2016-11-29 11:30 | 323 | 323
2016-11-29 12:00 | 326 | 325
2016-11-29 12:30 | 313 | 312
2016-11-29 13:00 | 311 | 310
2016-11-29 13:30 | 313 | 313
2016-11-29 14:00 | 325 | 324
2016-11-29 14:30 | 338 | 338
2016-11-29 15:00 | 343 | 342
2016-11-29 15:30 | 352 | 350
2016-11-29 16:00 | 360 | 359
2016-11-29 16:30 | 375 | 374
2016-11-29 17:00 | 383 | 381
2016-11-29 17:30 | 382 | 381
2016-11-29 18:00 | 382 | 381
2016-11-29 18:30 | 382 | 381
2016-11-29 19:00 | 385 | 384
2016-11-29 19:30 | 390 | 389
2016-11-29 20:00 | 383 | 381
2016-11-29 20:30 | 376 | 374
2016-11-29 21:00 | 359 | 358
2016-11-29 21:30 | 344 | 342
2016-11-29 22:00 | 325 | 323
2016-11-29 22:30 | 294 | 292
2016-11-29 23:00 | 289 | 288
2016-11-29 23:30 | 274 | 273
2016-11-30 | 265 | 264
2016-11-30 00:30 | 256 | 255
2016-11-30 01:00 | 246 | 245
2016-11-30 01:30 | 242 | 240
2016-11-30 02:00 | 235 | 234
2016-11-30 02:30 | 234 | 233
2016-11-30 03:00 | 231 | 230
2016-11-30 03:30 | 229 | 228
2016-11-30 04:00 | 225 | 225
2016-11-30 04:30 | 222 | 222
2016-11-30 05:00 | 228 | 227
2016-11-30 05:30 | 227 | 226
2016-11-30 06:00 | 230 | 230
2016-11-30 06:30 | 253 | 252
2016-11-30 07:00 | 277 | 276
2016-11-30 07:30 | 293 | 293
2016-11-30 08:00 | 301 | 300
2016-11-30 08:30 | 309 | 308
2016-11-30 09:00 | 294 | 293
2016-11-30 09:30 | 294 | 292
2016-11-30 10:00 | 301 | 300
2016-11-30 10:30 | 315 | 314
2016-11-30 11:00 | 312 | 311
2016-11-30 11:30 | 309 | 307
2016-11-30 12:00 | 317 | 316
2016-11-30 12:30 | 314 | 313
2016-11-30 13:00 | 309 | 307
2016-11-30 13:30 | 291 | 287
2016-11-30 14:00 | 302 | 300
2016-11-30 14:30 | 320 | 318
2016-11-30 15:00 | 343 | 341
2016-11-30 15:30 | 320 | 317
2016-11-30 16:00 | 329 | 326
2016-11-30 16:30 | 313 | 311
2016-11-30 17:00 | 315 | 313
2016-11-30 17:30 | 316 | 313
2016-11-30 18:00 | 316 | 313
2016-11-30 18:30 | 317 | 314
2016-11-30 19:00 | 326 | 324
2016-11-30 19:30 | 337 | 335
2016-11-30 20:00 | 332 | 330
2016-11-30 20:30 | 364 | 362
2016-11-30 21:00 | 359 | 357
2016-11-30 21:30 | 346 | 344
2016-11-30 22:00 | 328 | 326
2016-11-30 22:30 | 304 | 302
2016-11-30 23:00 | 287 | 285
2016-11-30 23:30 | 274 | 272
2016-12-01 | 258 | 257
2016-12-01 00:30 | 252 | 251
2016-12-01 01:00 | 241 | 241
2016-12-01 01:30 | 237 | 236
2016-12-01 02:00 | 230 | 230
2016-12-01 02:30 | 228 | 227
2016-12-01 03:00 | 225 | 225
2016-12-01 03:30 | 221 | 220
2016-12-01 04:00 | 216 | 215
2016-12-01 04:30 | 216 | 215
2016-12-01 05:00 | 219 | 218
2016-12-01 05:30 | 234 | 233
2016-12-01 06:00 | 239 | 238
2016-12-01 06:30 | 259 | 258
2016-12-01 07:00 | 273 | 271
2016-12-01 07:30 | 298 | 296
2016-12-01 08:00 | 310 | 309
2016-12-01 08:30 | 318 | 317
2016-12-01 09:00 | 307 | 306
2016-12-01 09:30 | 277 | 275
2016-12-01 10:00 | 279 | 278
2016-12-01 10:30 | 281 | 279
2016-12-01 11:00 | 284 | 282
2016-12-01 11:30 | 290 | 288
2016-12-01 12:00 | 294 | 292
2016-12-01 12:30 | 301 | 298
2016-12-01 13:00 | 315 | 312
2016-12-01 13:30 | 295 | 292
2016-12-01 14:00 | 322 | 319
2016-12-01 14:30 | 315 | 312
2016-12-01 15:00 | 321 | 318
2016-12-01 15:30 | 339 | 337
2016-12-01 16:00 | 339 | 336
2016-12-01 16:30 | 324 | 321
2016-12-01 17:00 | 340 | 337
2016-12-01 17:30 | 358 | 356
2016-12-01 18:00 | 362 | 359
2016-12-01 18:30 | 350 | 347
2016-12-01 19:00 | 352 | 349
2016-12-01 19:30 | 362 | 359
2016-12-01 20:00 | 355 | 352
2016-12-01 20:30 | 340 | 338
2016-12-01 21:00 | 329 | 326
2016-12-01 21:30 | 355 | 353
2016-12-01 22:00 | 345 | 343
2016-12-01 22:30 | 330 | 327
2016-12-01 23:00 | 316 | 313
2016-12-01 23:30 | 298 | 296
2016-12-02 | 270 | 268
2016-12-02 00:30 | 258 | 255
2016-12-02 01:00 | 250 | 248
2016-12-02 01:30 | 247 | 245
2016-12-02 02:00 | 240 | 239
2016-12-02 02:30 | 237 | 236
2016-12-02 03:00 | 235 | 233
2016-12-02 03:30 | 229 | 228
2016-12-02 04:00 | 226 | 224
2016-12-02 04:30 | 226 | 224
2016-12-02 05:00 | 228 | 227
2016-12-02 05:30 | 233 | 231
2016-12-02 06:00 | 236 | 235
2016-12-02 06:30 | 256 | 255
2016-12-02 07:00 | 275 | 274
2016-12-02 07:30 | 288 | 287
2016-12-02 08:00 | 288 | 287
2016-12-02 08:30 | 275 | 273
2016-12-02 09:00 | 276 | 275
2016-12-02 09:30 | 287 | 286
2016-12-02 10:00 | 295 | 294
2016-12-02 10:30 | 304 | 303
2016-12-02 11:00 | 308 | 307
2016-12-02 11:30 | 305 | 303
2016-12-02 12:00 | 261 | 260
2016-12-02 12:30 | 275 | 274
2016-12-02 13:00 | 281 | 280
2016-12-02 13:30 | 287 | 286
2016-12-02 14:00 | 294 | 293
2016-12-02 14:30 | 302 | 301
2016-12-02 15:00 | 287 | 285
2016-12-02 15:30 | 286 | 284
2016-12-02 16:00 | 260 | 258
2016-12-02 16:30 | 248 | 246
2016-12-02 17:00 | 278 | 276
2016-12-02 17:30 | 296 | 293
2016-12-02 18:00 | 300 | 298
2016-12-02 18:30 | 292 | 290
2016-12-02 19:00 | 298 | 296
2016-12-02 19:30 | 311 | 310
2016-12-02 20:00 | 306 | 304
2016-12-02 20:30 | 295 | 293
2016-12-02 21:00 | 283 | 282
2016-12-02 21:30 | 272 | 270
2016-12-02 22:00 | 254 | 253
2016-12-02 22:30 | 205 | 203
2016-12-02 23:00 | 233 | 231
2016-12-02 23:30 | 238 | 236
2016-12-03 | 227 | 225
2016-12-03 00:30 | 214 | 212
2016-12-03 01:00 | 207 | 205
2016-12-03 01:30 | 188 | 186
2016-12-03 02:00 | 182 | 179
2016-12-03 02:30 | 176 | 174
2016-12-03 03:00 | 174 | 172
2016-12-03 03:30 | 173 | 171
2016-12-03 04:00 | 169 | 167
2016-12-03 04:30 | 164 | 162
2016-12-03 05:00 | 164 | 162
2016-12-03 05:30 | 166 | 164
2016-12-03 06:00 | 163 | 161
2016-12-03 06:30 | 170 | 167
2016-12-03 07:00 | 180 | 178
2016-12-03 07:30 | 192 | 190
2016-12-03 08:00 | 202 | 200
2016-12-03 08:30 | 218 | 217
2016-12-03 09:00 | 228 | 227
2016-12-03 09:30 | 223 | 221
2016-12-03 10:00 | 224 | 222
2016-12-03 10:30 | 227 | 225
2016-12-03 11:00 | 230 | 228
2016-12-03 11:30 | 230 | 229
2016-12-03 12:00 | 241 | 239
2016-12-03 12:30 | 250 | 248
2016-12-03 13:00 | 252 | 250
2016-12-03 13:30 | 255 | 253
2016-12-03 14:00 | 262 | 261
2016-12-03 14:30 | 268 | 267
2016-12-03 15:00 | 272 | 271
2016-12-03 15:30 | 278 | 277
2016-12-03 16:00 | 261 | 260
2016-12-03 16:30 | 265 | 264
2016-12-03 17:00 | 273 | 272
2016-12-03 17:30 | 285 | 283
2016-12-03 18:00 | 288 | 287
2016-12-03 18:30 | 287 | 285
2016-12-03 19:00 | 288 | 287
2016-12-03 19:30 | 296 | 294
2016-12-03 20:00 | 293 | 292
2016-12-03 20:30 | 299 | 297
2016-12-03 21:00 | 343 | 341
2016-12-03 21:30 | 381 | 381
2016-12-03 22:00 | 370 | 369
2016-12-03 22:30 | 352 | 351
2016-12-03 23:00 | 341 | 339
2016-12-03 23:30 | 330 | 328
2016-12-04 | 312 | 310
2016-12-04 00:30 | 297 | 295
2016-12-04 01:00 | 287 | 285
2016-12-04 01:30 | 279 | 277
2016-12-04 02:00 | 270 | 268
2016-12-04 02:30 | 264 | 263
2016-12-04 03:00 | 260 | 259
2016-12-04 03:30 | 260 | 259
2016-12-04 04:00 | 256 | 254
2016-12-04 04:30 | 257 | 256
2016-12-04 05:00 | 254 | 253
2016-12-04 05:30 | 253 | 251
2016-12-04 06:00 | 249 | 248
2016-12-04 06:30 | 255 | 253
2016-12-04 07:00 | 262 | 261
2016-12-04 07:30 | 269 | 268
2016-12-04 08:00 | 279 | 278
2016-12-04 08:30 | 294 | 293
2016-12-04 09:00 | 299 | 297
2016-12-04 09:30 | 293 | 292
2016-12-04 10:00 | 287 | 286
2016-12-04 10:30 | 292 | 290
2016-12-04 11:00 | 293 | 291
2016-12-04 11:30 | 295 | 294
2016-12-04 12:00 | 298 | 297
2016-12-04 12:30 | 301 | 299
2016-12-04 13:00 | 305 | 304
2016-12-04 13:30 | 299 | 298
2016-12-04 14:00 | 304 | 303
2016-12-04 14:30 | 312 | 311
2016-12-04 15:00 | 286 | 285
2016-12-04 15:30 | 279 | 277
2016-12-04 16:00 | 266 | 265
2016-12-04 16:30 | 281 | 279
2016-12-04 17:00 | 285 | 283
2016-12-04 17:30 | 217 | 215
2016-12-04 18:00 | 223 | 222
2016-12-04 18:30 | 230 | 229
2016-12-04 19:00 | 255 | 254
2016-12-04 19:30 | 289 | 288
2016-12-04 20:00 | 310 | 309
2016-12-04 20:30 | 327 | 326
2016-12-04 21:00 | 342 | 341
2016-12-04 21:30 | 327 | 326
2016-12-04 22:00 | 309 | 308
2016-12-04 22:30 | 281 | 280
2016-12-04 23:00 | 275 | 274
2016-12-04 23:30 | 255 | 253
2016-12-05 | 286 | 285
2016-12-05 00:30 | 285 | 284
2016-12-05 01:00 | 281 | 279
2016-12-05 01:30 | 270 | 268
2016-12-05 02:00 | 263 | 262
2016-12-05 02:30 | 258 | 257
2016-12-05 03:00 | 254 | 253
2016-12-05 03:30 | 255 | 254
2016-12-05 04:00 | 255 | 253
2016-12-05 04:30 | 261 | 259
2016-12-05 05:00 | 261 | 259
2016-12-05 05:30 | 266 | 265
2016-12-05 06:00 | 268 | 266
2016-12-05 06:30 | 284 | 282
2016-12-05 07:00 | 260 | 258
2016-12-05 07:30 | 301 | 300
2016-12-05 08:00 | 303 | 302
2016-12-05 08:30 | 295 | 294
2016-12-05 09:00 | 301 | 300
2016-12-05 09:30 | 304 | 302
2016-12-05 10:00 | 299 | 297
2016-12-05 10:30 | 279 | 277
2016-12-05 11:00 | 270 | 267
2016-12-05 11:30 | 211 | 209
2016-12-05 12:00 | 210 | 208
2016-12-05 12:30 | 209 | 207
2016-12-05 13:00 | 191 | 188
2016-12-05 13:30 | 214 | 212
2016-12-05 14:00 | 184 | 182
2016-12-05 14:30 | 178 | 176
2016-12-05 15:00 | 156 | 153
2016-12-05 15:30 | 151 | 148
2016-12-05 16:00 | 125 | 122
2016-12-05 16:30 | 144 | 142
2016-12-05 17:00 | 181 | 179
2016-12-05 17:30 | 190 | 189
2016-12-05 18:00 | 230 | 228
2016-12-05 18:30 | 245 | 243
2016-12-05 19:00 | 224 | 222
2016-12-05 19:30 | 233 | 231
2016-12-05 20:00 | 247 | 246
2016-12-05 20:30 | 256 | 254
2016-12-05 21:00 | 306 | 304
2016-12-05 21:30 | 304 | 303
2016-12-05 22:00 | 291 | 290
2016-12-05 22:30 | 255 | 253
2016-12-05 23:00 | 258 | 256
2016-12-05 23:30 | 241 | 239
2016-12-06 | 230 | 227
2016-12-06 00:30 | 218 | 216
2016-12-06 01:00 | 208 | 206
2016-12-06 01:30 | 202 | 199
2016-12-06 02:00 | 195 | 193
2016-12-06 02:30 | 193 | 191
2016-12-06 03:00 | 191 | 189
2016-12-06 03:30 | 186 | 185
2016-12-06 04:00 | 184 | 182
2016-12-06 04:30 | 190 | 189
2016-12-06 05:00 | 194 | 193
2016-12-06 05:30 | 203 | 202
2016-12-06 06:00 | 213 | 212
2016-12-06 06:30 | 237 | 236
2016-12-06 07:00 | 221 | 219
2016-12-06 07:30 | 262 | 260
2016-12-06 08:00 | 308 | 306
2016-12-06 08:30 | 335 | 334
2016-12-06 09:00 | 337 | 335
2016-12-06 09:30 | 329 | 328
2016-12-06 10:00 | 299 | 298
2016-12-06 10:30 | 265 | 264
2016-12-06 11:00 | 250 | 249
2016-12-06 11:30 | 321 | 319
2016-12-06 12:00 | 327 | 326
2016-12-06 12:30 | 332 | 330
2016-12-06 13:00 | 333 | 331
2016-12-06 13:30 | 287 | 286
2016-12-06 14:00 | 276 | 274
2016-12-06 14:30 | 280 | 278
2016-12-06 15:00 | 259 | 257
2016-12-06 15:30 | 256 | 254
2016-12-06 16:00 | 240 | 237
2016-12-06 16:30 | 242 | 240
2016-12-06 17:00 | 253 | 251
2016-12-06 17:30 | 255 | 253
2016-12-06 18:00 | 255 | 253
2016-12-06 18:30 | 238 | 236
2016-12-06 19:00 | 244 | 242
2016-12-06 19:30 | 270 | 268
2016-12-06 20:00 | 286 | 285
2016-12-06 20:30 | 308 | 307
2016-12-06 21:00 | 335 | 334
2016-12-06 21:30 | 317 | 315
2016-12-06 22:00 | 291 | 289
2016-12-06 22:30 | 259 | 257
2016-12-06 23:00 | 251 | 250
2016-12-06 23:30 | 309 | 308
2016-12-07 | 311 | 310
2016-12-07 00:30 | 300 | 299
2016-12-07 01:00 | 291 | 290
2016-12-07 01:30 | 274 | 274
2016-12-07 02:00 | 274 | 274
2016-12-07 02:30 | 271 | 271
2016-12-07 03:00 | 267 | 266
2016-12-07 03:30 | 264 | 263
2016-12-07 04:00 | 263 | 262
2016-12-07 04:30 | 263 | 262
2016-12-07 05:00 | 266 | 265
2016-12-07 05:30 | 276 | 276
2016-12-07 06:00 | 282 | 281
2016-12-07 06:30 | 298 | 298
2016-12-07 07:00 | 317 | 317
2016-12-07 07:30 | 337 | 336
2016-12-07 08:00 | 349 | 348
2016-12-07 08:30 | 355 | 354
2016-12-07 09:00 | 358 | 357
2016-12-07 09:30 | 355 | 354
2016-12-07 10:00 | 350 | 349
2016-12-07 10:30 | 349 | 348
2016-12-07 11:00 | 305 | 304
2016-12-07 11:30 | 306 | 305
2016-12-07 12:00 | 308 | 307
2016-12-07 12:30 | 316 | 315
2016-12-07 13:00 | 320 | 319
2016-12-07 13:30 | 329 | 328
2016-12-07 14:00 | 298 | 296
2016-12-07 14:30 | 287 | 286
2016-12-07 15:00 | 290 | 289
2016-12-07 15:30 | 302 | 301
2016-12-07 16:00 | 280 | 279
2016-12-07 16:30 | 266 | 265
2016-12-07 17:00 | 283 | 282
2016-12-07 17:30 | 315 | 314
2016-12-07 18:00 | 294 | 293
2016-12-07 18:30 | 326 | 325
2016-12-07 19:00 | 337 | 336
2016-12-07 19:30 | 321 | 320
2016-12-07 20:00 | 299 | 298
2016-12-07 20:30 | 322 | 321
2016-12-07 21:00 | 362 | 361
2016-12-07 21:30 | 353 | 352
2016-12-07 22:00 | 338 | 337
2016-12-07 22:30 | 320 | 319
2016-12-07 23:00 | 299 | 298
2016-12-07 23:30 | 329 | 328
2016-12-08 | 323 | 322
2016-12-08 00:30 | 310 | 309
2016-12-08 01:00 | 301 | 300
2016-12-08 01:30 | 300 | 300
2016-12-08 02:00 | 297 | 297
2016-12-08 02:30 | 292 | 291
2016-12-08 03:00 | 293 | 292
2016-12-08 03:30 | 292 | 291
2016-12-08 04:00 | 288 | 287
2016-12-08 04:30 | 291 | 290
2016-12-08 05:00 | 295 | 294
2016-12-08 05:30 | 301 | 300
2016-12-08 06:00 | 300 | 299
2016-12-08 06:30 | 314 | 314
2016-12-08 07:00 | 333 | 333
2016-12-08 07:30 | 357 | 356
2016-12-08 08:00 | 363 | 362
2016-12-08 08:30 | 362 | 362
2016-12-08 09:00 | 353 | 352
2016-12-08 09:30 | 342 | 341
2016-12-08 10:00 | 322 | 320
2016-12-08 10:30 | 294 | 292
2016-12-08 11:00 | 268 | 266
2016-12-08 11:30 | 286 | 284
2016-12-08 12:00 | 347 | 346
2016-12-08 12:30 | 358 | 357
2016-12-08 13:00 | 368 | 367
2016-12-08 13:30 | 355 | 354
2016-12-08 14:00 | 336 | 334
2016-12-08 14:30 | 347 | 345
2016-12-08 15:00 | 365 | 364
2016-12-08 15:30 | 371 | 369
2016-12-08 16:00 | 375 | 374
2016-12-08 16:30 | 400 | 398
2016-12-08 17:00 | 394 | 392
2016-12-08 17:30 | 399 | 398
2016-12-08 18:00 | 404 | 403
2016-12-08 18:30 | 409 | 408
2016-12-08 19:00 | 408 | 406
2016-12-08 19:30 | 410 | 409
2016-12-08 20:00 | 409 | 408
2016-12-08 20:30 | 415 | 414
2016-12-08 21:00 | 427 | 425
2016-12-08 21:30 | 407 | 406
2016-12-08 22:00 | 390 | 388
2016-12-08 22:30 | 373 | 371
2016-12-08 23:00 | 355 | 353
2016-12-08 23:30 | 340 | 339
2016-12-09 | 321 | 319
2016-12-09 00:30 | 308 | 307
2016-12-09 01:00 | 299 | 297
2016-12-09 01:30 | 290 | 288
2016-12-09 02:00 | 287 | 285
2016-12-09 02:30 | 287 | 285
2016-12-09 03:00 | 287 | 285
2016-12-09 03:30 | 284 | 282
2016-12-09 04:00 | 283 | 282
2016-12-09 04:30 | 281 | 280
2016-12-09 05:00 | 280 | 278
2016-12-09 05:30 | 288 | 286
2016-12-09 06:00 | 290 | 288
2016-12-09 06:30 | 304 | 303
2016-12-09 07:00 | 322 | 321
2016-12-09 07:30 | 348 | 346
2016-12-09 08:00 | 361 | 359
2016-12-09 08:30 | 375 | 373
2016-12-09 09:00 | 373 | 372
2016-12-09 09:30 | 362 | 360
2016-12-09 10:00 | 354 | 352
2016-12-09 10:30 | 355 | 353
2016-12-09 11:00 | 358 | 356
2016-12-09 11:30 | 362 | 360
2016-12-09 12:00 | 333 | 331
2016-12-09 12:30 | 312 | 310
2016-12-09 13:00 | 285 | 282
2016-12-09 13:30 | 308 | 306
2016-12-09 14:00 | 328 | 326
2016-12-09 14:30 | 334 | 332
2016-12-09 15:00 | 338 | 337
2016-12-09 15:30 | 344 | 342
2016-12-09 16:00 | 332 | 331
2016-12-09 16:30 | 337 | 335
2016-12-09 17:00 | 339 | 337
2016-12-09 17:30 | 342 | 340
2016-12-09 18:00 | 332 | 330
2016-12-09 18:30 | 324 | 323
2016-12-09 19:00 | 329 | 328
2016-12-09 19:30 | 332 | 330
2016-12-09 20:00 | 327 | 326
2016-12-09 20:30 | 334 | 333
2016-12-09 21:00 | 346 | 345
2016-12-09 21:30 | 334 | 333
2016-12-09 22:00 | 319 | 318
2016-12-09 22:30 | 305 | 303
2016-12-09 23:00 | 286 | 284
2016-12-09 23:30 | 272 | 271
2016-12-10 | 260 | 259
2016-12-10 00:30 | 294 | 294
2016-12-10 01:00 | 291 | 290
2016-12-10 01:30 | 285 | 284
2016-12-10 02:00 | 278 | 277
2016-12-10 02:30 | 274 | 273
2016-12-10 03:00 | 269 | 269
2016-12-10 03:30 | 267 | 266
2016-12-10 04:00 | 265 | 264
2016-12-10 04:30 | 264 | 263
2016-12-10 05:00 | 265 | 264
2016-12-10 05:30 | 269 | 268
2016-12-10 06:00 | 267 | 266
2016-12-10 06:30 | 269 | 269
2016-12-10 07:00 | 287 | 287
2016-12-10 07:30 | 311 | 310
2016-12-10 08:00 | 318 | 317
2016-12-10 08:30 | 328 | 327
2016-12-10 09:00 | 334 | 333
2016-12-10 09:30 | 329 | 329
2016-12-10 10:00 | 315 | 314
2016-12-10 10:30 | 311 | 310
2016-12-10 11:00 | 313 | 312
2016-12-10 11:30 | 318 | 317
2016-12-10 12:00 | 324 | 323
2016-12-10 12:30 | 324 | 323
2016-12-10 13:00 | 329 | 328
2016-12-10 13:30 | 335 | 334
2016-12-10 14:00 | 342 | 341
2016-12-10 14:30 | 345 | 344
2016-12-10 15:00 | 346 | 345
2016-12-10 15:30 | 349 | 348
2016-12-10 16:00 | 332 | 331
2016-12-10 16:30 | 340 | 339
2016-12-10 17:00 | 345 | 344
2016-12-10 17:30 | 344 | 343
2016-12-10 18:00 | 340 | 339
2016-12-10 18:30 | 341 | 340
2016-12-10 19:00 | 341 | 341
2016-12-10 19:30 | 350 | 349
2016-12-10 20:00 | 345 | 344
2016-12-10 20:30 | 354 | 353
2016-12-10 21:00 | 369 | 368
2016-12-10 21:30 | 361 | 360
2016-12-10 22:00 | 354 | 354
2016-12-10 22:30 | 339 | 339
2016-12-10 23:00 | 326 | 325
2016-12-10 23:30 | 314 | 314
2016-12-11 | 300 | 299
2016-12-11 00:30 | 295 | 294
2016-12-11 01:00 | 288 | 286
2016-12-11 01:30 | 286 | 284
2016-12-11 02:00 | 275 | 273
2016-12-11 02:30 | 271 | 270
2016-12-11 03:00 | 271 | 270
2016-12-11 03:30 | 267 | 265
2016-12-11 04:00 | 262 | 261
2016-12-11 04:30 | 260 | 258
2016-12-11 05:00 | 258 | 257
2016-12-11 05:30 | 261 | 259
2016-12-11 06:00 | 258 | 256
2016-12-11 06:30 | 258 | 256
2016-12-11 07:00 | 262 | 260
2016-12-11 07:30 | 274 | 273
2016-12-11 08:00 | 280 | 279
2016-12-11 08:30 | 286 | 284
2016-12-11 09:00 | 293 | 291
2016-12-11 09:30 | 292 | 291
2016-12-11 10:00 | 291 | 289
2016-12-11 10:30 | 294 | 292
2016-12-11 11:00 | 293 | 290
2016-12-11 11:30 | 293 | 290
2016-12-11 12:00 | 292 | 289
2016-12-11 12:30 | 295 | 292
2016-12-11 13:00 | 295 | 292
2016-12-11 13:30 | 280 | 277
2016-12-11 14:00 | 281 | 278
2016-12-11 14:30 | 279 | 276
2016-12-11 15:00 | 285 | 282
2016-12-11 15:30 | 294 | 291
2016-12-11 16:00 | 276 | 273
2016-12-11 16:30 | 285 | 283
2016-12-11 17:00 | 296 | 293
2016-12-11 17:30 | 306 | 304
2016-12-11 18:00 | 314 | 312
2016-12-11 18:30 | 320 | 317
2016-12-11 19:00 | 322 | 320
2016-12-11 19:30 | 327 | 325
2016-12-11 20:00 | 325 | 323
2016-12-11 20:30 | 338 | 336
2016-12-11 21:00 | 353 | 352
2016-12-11 21:30 | 345 | 343
2016-12-11 22:00 | 334 | 332
2016-12-11 22:30 | 319 | 317
2016-12-11 23:00 | 304 | 302
2016-12-11 23:30 | 293 | 290
2016-12-12 | 278 | 276
2016-12-12 00:30 | 264 | 262
2016-12-12 01:00 | 259 | 257
2016-12-12 01:30 | 256 | 254
2016-12-12 02:00 | 256 | 254
2016-12-12 02:30 | 246 | 244
2016-12-12 03:00 | 244 | 242
2016-12-12 03:30 | 243 | 240
2016-12-12 04:00 | 243 | 241
2016-12-12 04:30 | 243 | 240
2016-12-12 05:00 | 247 | 245
2016-12-12 05:30 | 255 | 253
2016-12-12 06:00 | 265 | 263
2016-12-12 06:30 | 276 | 274
2016-12-12 07:00 | 267 | 265
2016-12-12 07:30 | 280 | 278
2016-12-12 08:00 | 300 | 298
2016-12-12 08:30 | 313 | 311
2016-12-12 09:00 | 316 | 314
2016-12-12 09:30 | 307 | 305
2016-12-12 10:00 | 296 | 294
2016-12-12 10:30 | 280 | 278
2016-12-12 11:00 | 238 | 236
2016-12-12 11:30 | 248 | 245
2016-12-12 12:00 | 255 | 253
2016-12-12 12:30 | 249 | 246
2016-12-12 13:00 | 251 | 249
2016-12-12 13:30 | 239 | 236
2016-12-12 14:00 | 235 | 232
2016-12-12 14:30 | 231 | 228
2016-12-12 15:00 | 232 | 229
2016-12-12 15:30 | 195 | 192
2016-12-12 16:00 | 167 | 163
2016-12-12 16:30 | 183 | 181
2016-12-12 17:00 | 189 | 187
2016-12-12 17:30 | 187 | 185
2016-12-12 18:00 | 187 | 184
2016-12-12 18:30 | 191 | 188
2016-12-12 19:00 | 199 | 197
2016-12-12 19:30 | 214 | 211
2016-12-12 20:00 | 210 | 207
2016-12-12 20:30 | 219 | 216
2016-12-12 21:00 | 271 | 269
2016-12-12 21:30 | 273 | 271
2016-12-12 22:00 | 255 | 253
2016-12-12 22:30 | 237 | 235
2016-12-12 23:00 | 221 | 218
2016-12-12 23:30 | 210 | 208
2016-12-13 | 200 | 197
2016-12-13 00:30 | 188 | 186
2016-12-13 01:00 | 181 | 178
2016-12-13 01:30 | 176 | 174
2016-12-13 02:00 | 173 | 170
2016-12-13 02:30 | 174 | 172
2016-12-13 03:00 | 205 | 203
2016-12-13 03:30 | 206 | 205
2016-12-13 04:00 | 207 | 205
2016-12-13 04:30 | 207 | 205
2016-12-13 05:00 | 210 | 208
2016-12-13 05:30 | 215 | 213
2016-12-13 06:00 | 215 | 214
2016-12-13 06:30 | 232 | 229
2016-12-13 07:00 | 256 | 254
2016-12-13 07:30 | 276 | 274
2016-12-13 08:00 | 289 | 288
2016-12-13 08:30 | 295 | 293
2016-12-13 09:00 | 307 | 306
2016-12-13 09:30 | 302 | 300
2016-12-13 10:00 | 293 | 292
2016-12-13 10:30 | 293 | 292
2016-12-13 11:00 | 291 | 289
2016-12-13 11:30 | 290 | 288
2016-12-13 12:00 | 293 | 291
2016-12-13 12:30 | 296 | 294
2016-12-13 13:00 | 295 | 293
2016-12-13 13:30 | 300 | 298
2016-12-13 14:00 | 284 | 282
2016-12-13 14:30 | 278 | 275
2016-12-13 15:00 | 283 | 281
2016-12-13 15:30 | 286 | 284
2016-12-13 16:00 | 264 | 262
2016-12-13 16:30 | 270 | 268
2016-12-13 17:00 | 275 | 272
2016-12-13 17:30 | 272 | 270
2016-12-13 18:00 | 279 | 277
2016-12-13 18:30 | 284 | 282
2016-12-13 19:00 | 286 | 284
2016-12-13 19:30 | 264 | 262
2016-12-13 20:00 | 266 | 264
2016-12-13 20:30 | 274 | 272
2016-12-13 21:00 | 287 | 285
2016-12-13 21:30 | 273 | 270
2016-12-13 22:00 | 257 | 255
2016-12-13 22:30 | 184 | 182
2016-12-13 23:00 | 211 | 209
2016-12-13 23:30 | 210 | 207
2016-12-14 | 199 | 196
2016-12-14 00:30 | 186 | 184
2016-12-14 01:00 | 181 | 178
2016-12-14 01:30 | 176 | 174
2016-12-14 02:00 | 174 | 172
2016-12-14 02:30 | 172 | 170
2016-12-14 03:00 | 168 | 165
2016-12-14 03:30 | 166 | 163
2016-12-14 04:00 | 167 | 164
2016-12-14 04:30 | 168 | 165
2016-12-14 05:00 | 168 | 166
2016-12-14 05:30 | 178 | 176
2016-12-14 06:00 | 184 | 181
2016-12-14 06:30 | 207 | 205
2016-12-14 07:00 | 221 | 219
2016-12-14 07:30 | 241 | 239
2016-12-14 08:00 | 256 | 255
2016-12-14 08:30 | 261 | 259
2016-12-14 09:00 | 275 | 273
2016-12-14 09:30 | 265 | 264
2016-12-14 10:00 | 256 | 255
2016-12-14 10:30 | 254 | 252
2016-12-14 11:00 | 257 | 255
2016-12-14 11:30 | 265 | 263
2016-12-14 12:00 | 268 | 266
2016-12-14 12:30 | 256 | 254
2016-12-14 13:00 | 252 | 250
2016-12-14 13:30 | 264 | 262
2016-12-14 14:00 | 275 | 272
2016-12-14 14:30 | 277 | 274
2016-12-14 15:00 | 274 | 271
2016-12-14 15:30 | 274 | 271
2016-12-14 16:00 | 256 | 253
2016-12-14 16:30 | 234 | 230
2016-12-14 17:00 | 242 | 238
2016-12-14 17:30 | 236 | 232
2016-12-14 18:00 | 268 | 264
2016-12-14 18:30 | 272 | 269
2016-12-14 19:00 | 253 | 250
2016-12-14 19:30 | 263 | 260
2016-12-14 20:00 | 273 | 270
2016-12-14 20:30 | 282 | 279
2016-12-14 21:00 | 295 | 292
2016-12-14 21:30 | 284 | 281
2016-12-14 22:00 | 270 | 267
2016-12-14 22:30 | 248 | 244
2016-12-14 23:00 | 242 | 238
2016-12-14 23:30 | 223 | 218
2016-12-15 | 210 | 206
2016-12-15 00:30 | 199 | 196
2016-12-15 01:00 | 194 | 191
2016-12-15 01:30 | 191 | 188
2016-12-15 02:00 | 187 | 183
2016-12-15 02:30 | 184 | 181
2016-12-15 03:00 | 180 | 176
2016-12-15 03:30 | 183 | 180
2016-12-15 04:00 | 182 | 178
2016-12-15 04:30 | 182 | 179
2016-12-15 05:00 | 186 | 183
2016-12-15 05:30 | 192 | 189
2016-12-15 06:00 | 197 | 194
2016-12-15 06:30 | 219 | 216
2016-12-15 07:00 | 236 | 235
2016-12-15 07:30 | 256 | 254
2016-12-15 08:00 | 274 | 271
2016-12-15 08:30 | 278 | 276
2016-12-15 09:00 | 288 | 286
2016-12-15 09:30 | 278 | 276
2016-12-15 10:00 | 268 | 265
2016-12-15 10:30 | 272 | 270
2016-12-15 11:00 | 277 | 274
2016-12-15 11:30 | 279 | 276
2016-12-15 12:00 | 280 | 278
2016-12-15 12:30 | 221 | 217
2016-12-15 13:00 | 232 | 228
2016-12-15 13:30 | 237 | 234
2016-12-15 14:00 | 233 | 229
2016-12-15 14:30 | 236 | 232
2016-12-15 15:00 | 255 | 252
2016-12-15 15:30 | 234 | 230
2016-12-15 16:00 | 251 | 248
2016-12-15 16:30 | 261 | 258
2016-12-15 17:00 | 237 | 233
2016-12-15 17:30 | 231 | 227
2016-12-15 18:00 | 254 | 251
2016-12-15 18:30 | 280 | 277
2016-12-15 19:00 | 254 | 251
2016-12-15 19:30 | 245 | 242
2016-12-15 20:00 | 281 | 278
2016-12-15 20:30 | 263 | 260
2016-12-15 21:00 | 285 | 282
2016-12-15 21:30 | 292 | 289
2016-12-15 22:00 | 276 | 273
2016-12-15 22:30 | 256 | 253
2016-12-15 23:00 | 211 | 207
2016-12-15 23:30 | 189 | 185
2016-12-16 | 221 | 218
2016-12-16 00:30 | 212 | 209
2016-12-16 01:00 | 203 | 199
2016-12-16 01:30 | 197 | 194
2016-12-16 02:00 | 192 | 188
2016-12-16 02:30 | 190 | 187
2016-12-16 03:00 | 185 | 181
2016-12-16 03:30 | 183 | 179
2016-12-16 04:00 | 183 | 179
2016-12-16 04:30 | 182 | 178
2016-12-16 05:00 | 180 | 176
2016-12-16 05:30 | 182 | 178
2016-12-16 06:00 | 189 | 185
2016-12-16 06:30 | 170 | 166
2016-12-16 07:00 | 118 | 113
2016-12-16 07:30 | 145 | 142
2016-12-16 08:00 | 174 | 171
2016-12-16 08:30 | 170 | 167
2016-12-16 09:00 | 189 | 186
2016-12-16 09:30 | 195 | 192
2016-12-16 10:00 | 192 | 189
2016-12-16 10:30 | 195 | 192
2016-12-16 11:00 | 212 | 210
2016-12-16 11:30 | 220 | 216
2016-12-16 12:00 | 211 | 208
2016-12-16 12:30 | 201 | 197
2016-12-16 13:00 | 223 | 221
2016-12-16 13:30 | 238 | 235
2016-12-16 14:00 | 243 | 238
2016-12-16 14:30 | 234 | 229
2016-12-16 15:00 | 281 | 277
2016-12-16 15:30 | 306 | 303
2016-12-16 16:00 | 290 | 286
2016-12-16 16:30 | 260 | 256
2016-12-16 17:00 | 269 | 265
2016-12-16 17:30 | 279 | 275
2016-12-16 18:00 | 305 | 301
2016-12-16 18:30 | 302 | 299
2016-12-16 19:00 | 311 | 308
2016-12-16 19:30 | 323 | 320
2016-12-16 20:00 | 296 | 292
2016-12-16 20:30 | 271 | 267
2016-12-16 21:00 | 276 | 271
2016-12-16 21:30 | 275 | 271
2016-12-16 22:00 | 275 | 270
2016-12-16 22:30 | 250 | 246
2016-12-16 23:00 | 228 | 226
2016-12-16 23:30 | 245 | 243
2016-12-17 | 282 | 280
2016-12-17 00:30 | 300 | 298
2016-12-17 01:00 | 299 | 296
2016-12-17 01:30 | 291 | 288
2016-12-17 02:00 | 285 | 283
2016-12-17 02:30 | 282 | 279
2016-12-17 03:00 | 280 | 278
2016-12-17 03:30 | 276 | 273
2016-12-17 04:00 | 279 | 277
2016-12-17 04:30 | 277 | 274
2016-12-17 05:00 | 276 | 274
2016-12-17 05:30 | 277 | 274
2016-12-17 06:00 | 276 | 273
2016-12-17 06:30 | 281 | 279
2016-12-17 07:00 | 287 | 284
2016-12-17 07:30 | 304 | 302
2016-12-17 08:00 | 320 | 318
2016-12-17 08:30 | 332 | 330
2016-12-17 09:00 | 342 | 340
2016-12-17 09:30 | 343 | 342
2016-12-17 10:00 | 334 | 332
2016-12-17 10:30 | 334 | 332
2016-12-17 11:00 | 335 | 334
2016-12-17 11:30 | 336 | 334
2016-12-17 12:00 | 328 | 326
2016-12-17 12:30 | 327 | 324
2016-12-17 13:00 | 339 | 337
2016-12-17 13:30 | 303 | 300
2016-12-17 14:00 | 294 | 292
2016-12-17 14:30 | 295 | 293
2016-12-17 15:00 | 291 | 289
2016-12-17 15:30 | 294 | 292
2016-12-17 16:00 | 279 | 276
2016-12-17 16:30 | 247 | 244
2016-12-17 17:00 | 262 | 260
2016-12-17 17:30 | 278 | 276
2016-12-17 18:00 | 302 | 298
2016-12-17 18:30 | 314 | 309
2016-12-17 19:00 | 305 | 301
2016-12-17 19:30 | 314 | 310
2016-12-17 20:00 | 323 | 319
2016-12-17 20:30 | 311 | 307
2016-12-17 21:00 | 324 | 320
2016-12-17 21:30 | 326 | 322
2016-12-17 22:00 | 313 | 309
2016-12-17 22:30 | 259 | 255
2016-12-17 23:00 | 278 | 275
2016-12-17 23:30 | 251 | 248
2016-12-18 | 257 | 254
2016-12-18 00:30 | 253 | 250
2016-12-18 01:00 | 287 | 285
2016-12-18 01:30 | 290 | 287
2016-12-18 02:00 | 284 | 281
2016-12-18 02:30 | 279 | 276
2016-12-18 03:00 | 276 | 273
2016-12-18 03:30 | 275 | 272
2016-12-18 04:00 | 273 | 270
2016-12-18 04:30 | 276 | 273
2016-12-18 05:00 | 280 | 277
2016-12-18 05:30 | 286 | 283
2016-12-18 06:00 | 283 | 280
2016-12-18 06:30 | 279 | 276
2016-12-18 07:00 | 281 | 278
2016-12-18 07:30 | 288 | 285
2016-12-18 08:00 | 295 | 293
2016-12-18 08:30 | 304 | 301
2016-12-18 09:00 | 309 | 306
2016-12-18 09:30 | 286 | 282
2016-12-18 10:00 | 311 | 308
2016-12-18 10:30 | 313 | 309
2016-12-18 11:00 | 307 | 303
2016-12-18 11:30 | 286 | 281
2016-12-18 12:00 | 296 | 293
2016-12-18 12:30 | 296 | 293
2016-12-18 13:00 | 302 | 298
2016-12-18 13:30 | 303 | 299
2016-12-18 14:00 | 313 | 309
2016-12-18 14:30 | 312 | 308
2016-12-18 15:00 | 306 | 301
2016-12-18 15:30 | 306 | 302
2016-12-18 16:00 | 309 | 306
2016-12-18 16:30 | 337 | 333
2016-12-18 17:00 | 363 | 360
2016-12-18 17:30 | 373 | 370
2016-12-18 18:00 | 379 | 377
2016-12-18 18:30 | 380 | 378
2016-12-18 19:00 | 377 | 375
2016-12-18 19:30 | 382 | 379
2016-12-18 20:00 | 376 | 373
2016-12-18 20:30 | 379 | 377
2016-12-18 21:00 | 392 | 390
2016-12-18 21:30 | 395 | 392
2016-12-18 22:00 | 380 | 378
2016-12-18 22:30 | 335 | 331
2016-12-18 23:00 | 308 | 305
2016-12-18 23:30 | 321 | 318
2016-12-19 | 323 | 320
2016-12-19 00:30 | 317 | 314
2016-12-19 01:00 | 310 | 307
2016-12-19 01:30 | 301 | 298
2016-12-19 02:00 | 300 | 297
2016-12-19 02:30 | 294 | 291
2016-12-19 03:00 | 289 | 286
2016-12-19 03:30 | 288 | 285
2016-12-19 04:00 | 287 | 283
2016-12-19 04:30 | 283 | 279
2016-12-19 05:00 | 284 | 281
2016-12-19 05:30 | 292 | 288
2016-12-19 06:00 | 292 | 288
2016-12-19 06:30 | 309 | 306
2016-12-19 07:00 | 324 | 321
2016-12-19 07:30 | 351 | 349
2016-12-19 08:00 | 366 | 363
2016-12-19 08:30 | 377 | 374
2016-12-19 09:00 | 378 | 376
2016-12-19 09:30 | 370 | 367
2016-12-19 10:00 | 360 | 357
2016-12-19 10:30 | 361 | 358
2016-12-19 11:00 | 361 | 359
2016-12-19 11:30 | 364 | 361
2016-12-19 12:00 | 367 | 364
2016-12-19 12:30 | 372 | 369
2016-12-19 13:00 | 377 | 375
2016-12-19 13:30 | 379 | 376
2016-12-19 14:00 | 393 | 391
2016-12-19 14:30 | 397 | 394
2016-12-19 15:00 | 401 | 398
2016-12-19 15:30 | 408 | 405
2016-12-19 16:00 | 396 | 392
2016-12-19 16:30 | 419 | 415
2016-12-19 17:00 | 416 | 413
2016-12-19 17:30 | 424 | 421
2016-12-19 18:00 | 429 | 426
2016-12-19 18:30 | 436 | 433
2016-12-19 19:00 | 440 | 438
2016-12-19 19:30 | 448 | 446
2016-12-19 20:00 | 446 | 444
2016-12-19 20:30 | 436 | 433
2016-12-19 21:00 | 426 | 424
2016-12-19 21:30 | 411 | 409
2016-12-19 22:00 | 391 | 389
2016-12-19 22:30 | 342 | 340
2016-12-19 23:00 | 318 | 316
2016-12-19 23:30 | 332 | 331
2016-12-20 | 325 | 324
2016-12-20 00:30 | 316 | 315
2016-12-20 01:00 | 309 | 307
2016-12-20 01:30 | 297 | 296
2016-12-20 02:00 | 295 | 294
2016-12-20 02:30 | 290 | 288
2016-12-20 03:00 | 287 | 286
2016-12-20 03:30 | 287 | 286
2016-12-20 04:00 | 288 | 286
2016-12-20 04:30 | 286 | 284
2016-12-20 05:00 | 285 | 283
2016-12-20 05:30 | 281 | 278
2016-12-20 06:00 | 255 | 252
2016-12-20 06:30 | 246 | 243
2016-12-20 07:00 | 231 | 228
2016-12-20 07:30 | 252 | 250
2016-12-20 08:00 | 266 | 264
2016-12-20 08:30 | 272 | 270
2016-12-20 09:00 | 284 | 283
2016-12-20 09:30 | 275 | 273
2016-12-20 10:00 | 259 | 257
2016-12-20 10:30 | 213 | 210
2016-12-20 11:00 | 216 | 213
2016-12-20 11:30 | 223 | 220
2016-12-20 12:00 | 226 | 223
2016-12-20 12:30 | 233 | 229
2016-12-20 13:00 | 228 | 225
2016-12-20 13:30 | 229 | 226
2016-12-20 14:00 | 245 | 242
2016-12-20 14:30 | 253 | 250
2016-12-20 15:00 | 261 | 258
2016-12-20 15:30 | 220 | 217
2016-12-20 16:00 | 214 | 211
2016-12-20 16:30 | 222 | 219
2016-12-20 17:00 | 242 | 240
2016-12-20 17:30 | 241 | 238
2016-12-20 18:00 | 241 | 238
2016-12-20 18:30 | 247 | 243
2016-12-20 19:00 | 255 | 252
2016-12-20 19:30 | 276 | 274
2016-12-20 20:00 | 295 | 293
2016-12-20 20:30 | 289 | 287
2016-12-20 21:00 | 283 | 281
2016-12-20 21:30 | 296 | 294
2016-12-20 22:00 | 311 | 309
2016-12-20 22:30 | 273 | 270
2016-12-20 23:00 | 285 | 283
2016-12-20 23:30 | 268 | 265
2016-12-21 | 252 | 250
2016-12-21 00:30 | 245 | 242
2016-12-21 01:00 | 233 | 231
2016-12-21 01:30 | 225 | 223
2016-12-21 02:00 | 221 | 219
2016-12-21 02:30 | 217 | 215
2016-12-21 03:00 | 215 | 212
2016-12-21 03:30 | 210 | 207
2016-12-21 04:00 | 205 | 202
2016-12-21 04:30 | 204 | 202
2016-12-21 05:00 | 211 | 208
2016-12-21 05:30 | 221 | 219
2016-12-21 06:00 | 214 | 211
2016-12-21 06:30 | 212 | 208
2016-12-21 07:00 | 240 | 237
2016-12-21 07:30 | 260 | 258
2016-12-21 08:00 | 278 | 276
2016-12-21 08:30 | 291 | 288
2016-12-21 09:00 | 297 | 294
2016-12-21 09:30 | 289 | 286
2016-12-21 10:00 | 282 | 278
2016-12-21 10:30 | 288 | 283
2016-12-21 11:00 | 289 | 284
2016-12-21 11:30 | 288 | 282
2016-12-21 12:00 | 252 | 246
2016-12-21 12:30 | 247 | 241
2016-12-21 13:00 | 248 | 242
2016-12-21 13:30 | 247 | 241
2016-12-21 14:00 | 245 | 238
2016-12-21 14:30 | 247 | 242
2016-12-21 15:00 | 223 | 217
2016-12-21 15:30 | 227 | 222
2016-12-21 16:00 | 238 | 232
2016-12-21 16:30 | 243 | 238
2016-12-21 17:00 | 251 | 246
2016-12-21 17:30 | 271 | 266
2016-12-21 18:00 | 285 | 280
2016-12-21 18:30 | 295 | 291
2016-12-21 19:00 | 298 | 294
2016-12-21 19:30 | 307 | 304
2016-12-21 20:00 | 305 | 302
2016-12-21 20:30 | 304 | 300
2016-12-21 21:00 | 298 | 294
2016-12-21 21:30 | 328 | 324
2016-12-21 22:00 | 324 | 320
2016-12-21 22:30 | 290 | 285
2016-12-21 23:00 | 288 | 283
2016-12-21 23:30 | 268 | 263
2016-12-22 | 286 | 281
2016-12-22 00:30 | 328 | 324
2016-12-22 01:00 | 319 | 315
2016-12-22 01:30 | 308 | 303
2016-12-22 02:00 | 307 | 303
2016-12-22 02:30 | 303 | 299
2016-12-22 03:00 | 302 | 298
2016-12-22 03:30 | 298 | 293
2016-12-22 04:00 | 294 | 289
2016-12-22 04:30 | 289 | 284
2016-12-22 05:00 | 293 | 288
2016-12-22 05:30 | 295 | 290
2016-12-22 06:00 | 301 | 297
2016-12-22 06:30 | 317 | 313
2016-12-22 07:00 | 329 | 325
2016-12-22 07:30 | 356 | 352
2016-12-22 08:00 | 373 | 369
2016-12-22 08:30 | 383 | 380
2016-12-22 09:00 | 390 | 386
2016-12-22 09:30 | 380 | 377
2016-12-22 10:00 | 366 | 362
2016-12-22 10:30 | 370 | 366
2016-12-22 11:00 | 365 | 361
2016-12-22 11:30 | 369 | 365
2016-12-22 12:00 | 376 | 372
2016-12-22 12:30 | 379 | 375
2016-12-22 13:00 | 379 | 375
2016-12-22 13:30 | 346 | 341
2016-12-22 14:00 | 398 | 394
2016-12-22 14:30 | 404 | 400
2016-12-22 15:00 | 405 | 401
2016-12-22 15:30 | 414 | 410
2016-12-22 16:00 | 415 | 411
2016-12-22 16:30 | 438 | 435
2016-12-22 17:00 | 453 | 449
2016-12-22 17:30 | 454 | 450
2016-12-22 18:00 | 450 | 445
2016-12-22 18:30 | 451 | 447
2016-12-22 19:00 | 453 | 449
2016-12-22 19:30 | 459 | 455
2016-12-22 20:00 | 459 | 455
2016-12-22 20:30 | 449 | 445
2016-12-22 21:00 | 434 | 430
2016-12-22 21:30 | 418 | 414
2016-12-22 22:00 | 404 | 399
2016-12-22 22:30 | 379 | 374
2016-12-22 23:00 | 368 | 364
2016-12-22 23:30 | 356 | 352
2016-12-23 | 346 | 342
2016-12-23 00:30 | 336 | 332
2016-12-23 01:00 | 325 | 321
2016-12-23 01:30 | 321 | 316
2016-12-23 02:00 | 315 | 310
2016-12-23 02:30 | 307 | 302
2016-12-23 03:00 | 301 | 296
2016-12-23 03:30 | 299 | 295
2016-12-23 04:00 | 296 | 291
2016-12-23 04:30 | 297 | 292
2016-12-23 05:00 | 299 | 294
2016-12-23 05:30 | 306 | 301
2016-12-23 06:00 | 309 | 304
2016-12-23 06:30 | 323 | 319
2016-12-23 07:00 | 338 | 334
2016-12-23 07:30 | 350 | 347
2016-12-23 08:00 | 367 | 363
2016-12-23 08:30 | 378 | 374
2016-12-23 09:00 | 381 | 377
2016-12-23 09:30 | 373 | 369
2016-12-23 10:00 | 369 | 365
2016-12-23 10:30 | 368 | 364
2016-12-23 11:00 | 329 | 325
2016-12-23 11:30 | 311 | 307
2016-12-23 12:00 | 310 | 306
2016-12-23 12:30 | 314 | 309
2016-12-23 13:00 | 319 | 314
2016-12-23 13:30 | 323 | 319
2016-12-23 14:00 | 343 | 340
2016-12-23 14:30 | 342 | 338
2016-12-23 15:00 | 345 | 342
2016-12-23 15:30 | 349 | 346
2016-12-23 16:00 | 314 | 310
2016-12-23 16:30 | 315 | 311
2016-12-23 17:00 | 318 | 314
2016-12-23 17:30 | 315 | 311
2016-12-23 18:00 | 317 | 313
2016-12-23 18:30 | 318 | 314
2016-12-23 19:00 | 324 | 320
2016-12-23 19:30 | 333 | 329
2016-12-23 20:00 | 336 | 332
2016-12-23 20:30 | 331 | 327
2016-12-23 21:00 | 359 | 355
2016-12-23 21:30 | 357 | 354
2016-12-23 22:00 | 346 | 342
2016-12-23 22:30 | 303 | 299
2016-12-23 23:00 | 308 | 304
2016-12-23 23:30 | 347 | 343
2016-12-24 | 343 | 338
2016-12-24 00:30 | 335 | 330
2016-12-24 01:00 | 321 | 317
2016-12-24 01:30 | 316 | 311
2016-12-24 02:00 | 309 | 304
2016-12-24 02:30 | 300 | 298
2016-12-24 03:00 | 299 | 297
2016-12-24 03:30 | 300 | 298
2016-12-24 04:00 | 303 | 301
2016-12-24 04:30 | 299 | 297
2016-12-24 05:00 | 302 | 300
2016-12-24 05:30 | 304 | 302
2016-12-24 06:00 | 310 | 308
2016-12-24 06:30 | 315 | 313
2016-12-24 07:00 | 321 | 319
2016-12-24 07:30 | 330 | 327
2016-12-24 08:00 | 341 | 339
2016-12-24 08:30 | 350 | 347
2016-12-24 09:00 | 360 | 357
2016-12-24 09:30 | 324 | 321
2016-12-24 10:00 | 350 | 347
2016-12-24 10:30 | 355 | 353
2016-12-24 11:00 | 347 | 345
2016-12-24 11:30 | 359 | 357
2016-12-24 12:00 | 373 | 370
2016-12-24 12:30 | 375 | 372
2016-12-24 13:00 | 377 | 375
2016-12-24 13:30 | 384 | 382
2016-12-24 14:00 | 401 | 399
2016-12-24 14:30 | 403 | 401
2016-12-24 15:00 | 413 | 411
2016-12-24 15:30 | 423 | 421
2016-12-24 16:00 | 430 | 427
2016-12-24 16:30 | 429 | 427
2016-12-24 17:00 | 431 | 429
2016-12-24 17:30 | 433 | 430
2016-12-24 18:00 | 434 | 431
2016-12-24 18:30 | 435 | 433
2016-12-24 19:00 | 434 | 431
2016-12-24 19:30 | 438 | 436
2016-12-24 20:00 | 434 | 432
2016-12-24 20:30 | 429 | 426
2016-12-24 21:00 | 420 | 417
2016-12-24 21:30 | 410 | 408
2016-12-24 22:00 | 401 | 398
2016-12-24 22:30 | 393 | 390
2016-12-24 23:00 | 382 | 379
2016-12-24 23:30 | 365 | 362
2016-12-25 | 348 | 345
2016-12-25 00:30 | 341 | 339
2016-12-25 01:00 | 329 | 327
2016-12-25 01:30 | 321 | 320
2016-12-25 02:00 | 312 | 310
2016-12-25 02:30 | 307 | 305
2016-12-25 03:00 | 304 | 303
2016-12-25 03:30 | 304 | 302
2016-12-25 04:00 | 296 | 295
2016-12-25 04:30 | 292 | 292
2016-12-25 05:00 | 292 | 292
2016-12-25 05:30 | 292 | 292
2016-12-25 06:00 | 290 | 290
2016-12-25 06:30 | 293 | 292
2016-12-25 07:00 | 300 | 299
2016-12-25 07:30 | 311 | 311
2016-12-25 08:00 | 320 | 320
2016-12-25 08:30 | 326 | 326
2016-12-25 09:00 | 328 | 328
2016-12-25 09:30 | 323 | 323
2016-12-25 10:00 | 321 | 321
2016-12-25 10:30 | 324 | 323
2016-12-25 11:00 | 328 | 328
2016-12-25 11:30 | 327 | 326
2016-12-25 12:00 | 322 | 322
2016-12-25 12:30 | 321 | 321
2016-12-25 13:00 | 315 | 315
2016-12-25 13:30 | 308 | 308
2016-12-25 14:00 | 322 | 322
2016-12-25 14:30 | 318 | 317
2016-12-25 15:00 | 319 | 319
2016-12-25 15:30 | 322 | 322
2016-12-25 16:00 | 328 | 328
2016-12-25 16:30 | 352 | 352
2016-12-25 17:00 | 362 | 362
2016-12-25 17:30 | 365 | 365
2016-12-25 18:00 | 367 | 367
2016-12-25 18:30 | 374 | 374
2016-12-25 19:00 | 381 | 381
2016-12-25 19:30 | 390 | 390
2016-12-25 20:00 | 396 | 395
2016-12-25 20:30 | 390 | 390
2016-12-25 21:00 | 387 | 387
2016-12-25 21:30 | 383 | 383
2016-12-25 22:00 | 374 | 373
2016-12-25 22:30 | 362 | 362
2016-12-25 23:00 | 351 | 351
2016-12-25 23:30 | 341 | 341
2016-12-26 | 329 | 328
2016-12-26 00:30 | 326 | 325
2016-12-26 01:00 | 315 | 314
2016-12-26 01:30 | 306 | 305
2016-12-26 02:00 | 303 | 303
2016-12-26 02:30 | 299 | 298
2016-12-26 03:00 | 292 | 292
2016-12-26 03:30 | 292 | 291
2016-12-26 04:00 | 292 | 292
2016-12-26 04:30 | 292 | 291
2016-12-26 05:00 | 294 | 294
2016-12-26 05:30 | 297 | 297
2016-12-26 06:00 | 297 | 296
2016-12-26 06:30 | 302 | 302
2016-12-26 07:00 | 312 | 311
2016-12-26 07:30 | 320 | 320
2016-12-26 08:00 | 333 | 332
2016-12-26 08:30 | 339 | 339
2016-12-26 09:00 | 344 | 343
2016-12-26 09:30 | 339 | 338
2016-12-26 10:00 | 326 | 325
2016-12-26 10:30 | 330 | 329
2016-12-26 11:00 | 331 | 331
2016-12-26 11:30 | 332 | 332
2016-12-26 12:00 | 331 | 331
2016-12-26 12:30 | 337 | 337
2016-12-26 13:00 | 356 | 355
2016-12-26 13:30 | 355 | 355
2016-12-26 14:00 | 364 | 364
2016-12-26 14:30 | 371 | 371
2016-12-26 15:00 | 378 | 378
2016-12-26 15:30 | 392 | 392
2016-12-26 16:00 | 399 | 399
2016-12-26 16:30 | 420 | 420
2016-12-26 17:00 | 431 | 431
2016-12-26 17:30 | 436 | 436
2016-12-26 18:00 | 437 | 437
2016-12-26 18:30 | 438 | 438
2016-12-26 19:00 | 443 | 443
2016-12-26 19:30 | 452 | 451
2016-12-26 20:00 | 453 | 453
2016-12-26 20:30 | 446 | 446
2016-12-26 21:00 | 435 | 435
2016-12-26 21:30 | 423 | 423
2016-12-26 22:00 | 411 | 410
2016-12-26 22:30 | 394 | 393
2016-12-26 23:00 | 378 | 378
2016-12-26 23:30 | 363 | 363
2016-12-27 | 351 | 351
2016-12-27 00:30 | 343 | 342
2016-12-27 01:00 | 334 | 333
2016-12-27 01:30 | 326 | 326
2016-12-27 02:00 | 320 | 320
2016-12-27 02:30 | 314 | 313
2016-12-27 03:00 | 310 | 310
2016-12-27 03:30 | 306 | 306
2016-12-27 04:00 | 306 | 305
2016-12-27 04:30 | 306 | 305
2016-12-27 05:00 | 306 | 305
2016-12-27 05:30 | 308 | 308
2016-12-27 06:00 | 309 | 308
2016-12-27 06:30 | 314 | 314
2016-12-27 07:00 | 325 | 324
2016-12-27 07:30 | 334 | 333
2016-12-27 08:00 | 343 | 342
2016-12-27 08:30 | 350 | 350
2016-12-27 09:00 | 358 | 358
2016-12-27 09:30 | 350 | 349
2016-12-27 10:00 | 342 | 342
2016-12-27 10:30 | 342 | 341
2016-12-27 11:00 | 348 | 347
2016-12-27 11:30 | 353 | 353
2016-12-27 12:00 | 361 | 360
2016-12-27 12:30 | 369 | 368
2016-12-27 13:00 | 369 | 368
2016-12-27 13:30 | 360 | 359
2016-12-27 14:00 | 380 | 378
2016-12-27 14:30 | 388 | 386
2016-12-27 15:00 | 394 | 392
2016-12-27 15:30 | 394 | 393
2016-12-27 16:00 | 401 | 400
2016-12-27 16:30 | 416 | 415
2016-12-27 17:00 | 422 | 421
2016-12-27 17:30 | 431 | 430
2016-12-27 18:00 | 437 | 436
2016-12-27 18:30 | 438 | 438
2016-12-27 19:00 | 445 | 444
2016-12-27 19:30 | 446 | 446
2016-12-27 20:00 | 445 | 445
2016-12-27 20:30 | 443 | 442
2016-12-27 21:00 | 431 | 430
2016-12-27 21:30 | 419 | 418
2016-12-27 22:00 | 406 | 406
2016-12-27 22:30 | 387 | 386
2016-12-27 23:00 | 372 | 372
2016-12-27 23:30 | 362 | 362
2016-12-28 | 350 | 350
2016-12-28 00:30 | 344 | 343
2016-12-28 01:00 | 335 | 334
2016-12-28 01:30 | 329 | 328
2016-12-28 02:00 | 324 | 323
2016-12-28 02:30 | 320 | 319
2016-12-28 03:00 | 317 | 315
2016-12-28 03:30 | 315 | 313
2016-12-28 04:00 | 311 | 310
2016-12-28 04:30 | 311 | 310
2016-12-28 05:00 | 312 | 311
2016-12-28 05:30 | 314 | 313
2016-12-28 06:00 | 317 | 316
2016-12-28 06:30 | 329 | 327
2016-12-28 07:00 | 340 | 339
2016-12-28 07:30 | 354 | 353
2016-12-28 08:00 | 330 | 328
2016-12-28 08:30 | 323 | 321
2016-12-28 09:00 | 330 | 329
2016-12-28 09:30 | 320 | 319
2016-12-28 10:00 | 309 | 308
2016-12-28 10:30 | 303 | 301
2016-12-28 11:00 | 273 | 271
2016-12-28 11:30 | 278 | 276
2016-12-28 12:00 | 284 | 283
2016-12-28 12:30 | 287 | 286
2016-12-28 13:00 | 290 | 288
2016-12-28 13:30 | 296 | 295
2016-12-28 14:00 | 316 | 314
2016-12-28 14:30 | 322 | 321
2016-12-28 15:00 | 325 | 324
2016-12-28 15:30 | 332 | 330
2016-12-28 16:00 | 345 | 344
2016-12-28 16:30 | 352 | 350
2016-12-28 17:00 | 337 | 334
2016-12-28 17:30 | 321 | 318
2016-12-28 18:00 | 329 | 326
2016-12-28 18:30 | 344 | 341
2016-12-28 19:00 | 352 | 350
2016-12-28 19:30 | 360 | 358
2016-12-28 20:00 | 360 | 358
2016-12-28 20:30 | 353 | 351
2016-12-28 21:00 | 343 | 341
2016-12-28 21:30 | 330 | 327
2016-12-28 22:00 | 320 | 317
2016-12-28 22:30 | 332 | 329
2016-12-28 23:00 | 378 | 375
2016-12-28 23:30 | 366 | 364
2016-12-29 | 356 | 354
2016-12-29 00:30 | 349 | 346
2016-12-29 01:00 | 340 | 337
2016-12-29 01:30 | 332 | 330
2016-12-29 02:00 | 321 | 319
2016-12-29 02:30 | 316 | 314
2016-12-29 03:00 | 314 | 313
2016-12-29 03:30 | 313 | 311
2016-12-29 04:00 | 314 | 312
2016-12-29 04:30 | 312 | 310
2016-12-29 05:00 | 315 | 313
2016-12-29 05:30 | 321 | 320
2016-12-29 06:00 | 321 | 318
2016-12-29 06:30 | 322 | 320
2016-12-29 07:00 | 304 | 302
2016-12-29 07:30 | 315 | 313
2016-12-29 08:00 | 330 | 328
2016-12-29 08:30 | 345 | 343
2016-12-29 09:00 | 354 | 352
2016-12-29 09:30 | 351 | 349
2016-12-29 10:00 | 348 | 346
2016-12-29 10:30 | 321 | 319
2016-12-29 11:00 | 279 | 277
2016-12-29 11:30 | 248 | 245
2016-12-29 12:00 | 249 | 246
2016-12-29 12:30 | 256 | 253
2016-12-29 13:00 | 255 | 252
2016-12-29 13:30 | 252 | 249
2016-12-29 14:00 | 268 | 265
2016-12-29 14:30 | 275 | 272
2016-12-29 15:00 | 284 | 282
2016-12-29 15:30 | 284 | 282
2016-12-29 16:00 | 285 | 283
2016-12-29 16:30 | 294 | 291
2016-12-29 17:00 | 308 | 305
2016-12-29 17:30 | 317 | 315
2016-12-29 18:00 | 324 | 322
2016-12-29 18:30 | 322 | 320
2016-12-29 19:00 | 326 | 324
2016-12-29 19:30 | 330 | 328
2016-12-29 20:00 | 331 | 329
2016-12-29 20:30 | 323 | 321
2016-12-29 21:00 | 310 | 308
2016-12-29 21:30 | 337 | 335
2016-12-29 22:00 | 333 | 331
2016-12-29 22:30 | 275 | 272
2016-12-29 23:00 | 294 | 292
2016-12-29 23:30 | 293 | 290
2016-12-30 | 282 | 279
2016-12-30 00:30 | 274 | 271
2016-12-30 01:00 | 263 | 260
2016-12-30 01:30 | 253 | 251
2016-12-30 02:00 | 247 | 245
2016-12-30 02:30 | 242 | 239
2016-12-30 03:00 | 239 | 236
2016-12-30 03:30 | 235 | 232
2016-12-30 04:00 | 232 | 230
2016-12-30 04:30 | 231 | 229
2016-12-30 05:00 | 231 | 229
2016-12-30 05:30 | 235 | 233
2016-12-30 06:00 | 236 | 233
2016-12-30 06:30 | 246 | 244
2016-12-30 07:00 | 255 | 253
2016-12-30 07:30 | 267 | 266
2016-12-30 08:00 | 280 | 278
2016-12-30 08:30 | 292 | 290
2016-12-30 09:00 | 301 | 300
2016-12-30 09:30 | 291 | 290
2016-12-30 10:00 | 284 | 283
2016-12-30 10:30 | 261 | 260
2016-12-30 11:00 | 235 | 233
2016-12-30 11:30 | 237 | 236
2016-12-30 12:00 | 240 | 239
2016-12-30 12:30 | 244 | 243
2016-12-30 13:00 | 249 | 248
2016-12-30 13:30 | 263 | 261
2016-12-30 14:00 | 284 | 282
2016-12-30 14:30 | 290 | 288
2016-12-30 15:00 | 289 | 287
2016-12-30 15:30 | 298 | 296
2016-12-30 16:00 | 294 | 292
2016-12-30 16:30 | 276 | 274
2016-12-30 17:00 | 280 | 278
2016-12-30 17:30 | 304 | 302
2016-12-30 18:00 | 312 | 310
2016-12-30 18:30 | 316 | 314
2016-12-30 19:00 | 318 | 317
2016-12-30 19:30 | 332 | 331
2016-12-30 20:00 | 335 | 334
2016-12-30 20:30 | 324 | 323
2016-12-30 21:00 | 313 | 312
2016-12-30 21:30 | 299 | 297
2016-12-30 22:00 | 289 | 287
2016-12-30 22:30 | 260 | 258
2016-12-30 23:00 | 287 | 285
2016-12-30 23:30 | 296 | 294
2016-12-31 | 284 | 282
2016-12-31 00:30 | 277 | 274
2016-12-31 01:00 | 266 | 263
2016-12-31 01:30 | 255 | 253
2016-12-31 02:00 | 249 | 247
2016-12-31 02:30 | 247 | 244
2016-12-31 03:00 | 243 | 240
2016-12-31 03:30 | 241 | 238
2016-12-31 04:00 | 237 | 234
2016-12-31 04:30 | 237 | 235
2016-12-31 05:00 | 235 | 232
2016-12-31 05:30 | 236 | 234
2016-12-31 06:00 | 235 | 232
2016-12-31 06:30 | 237 | 235
2016-12-31 07:00 | 244 | 241
2016-12-31 07:30 | 254 | 251
2016-12-31 08:00 | 266 | 264
2016-12-31 08:30 | 279 | 277
2016-12-31 09:00 | 286 | 284
2016-12-31 09:30 | 281 | 280
2016-12-31 10:00 | 276 | 274
2016-12-31 10:30 | 283 | 281
2016-12-31 11:00 | 286 | 284
2016-12-31 11:30 | 265 | 263
2016-12-31 12:00 | 241 | 240
2016-12-31 12:30 | 247 | 245
2016-12-31 13:00 | 247 | 245
2016-12-31 13:30 | 270 | 269
2016-12-31 14:00 | 235 | 232
2016-12-31 14:30 | 251 | 248
2016-12-31 15:00 | 270 | 268
2016-12-31 15:30 | 283 | 281
2016-12-31 16:00 | 281 | 278
2016-12-31 16:30 | 264 | 262
2016-12-31 17:00 | 280 | 278
2016-12-31 17:30 | 277 | 274
2016-12-31 18:00 | 288 | 286
2016-12-31 18:30 | 293 | 291
2016-12-31 19:00 | 300 | 298
2016-12-31 19:30 | 296 | 294
2016-12-31 20:00 | 295 | 292
2016-12-31 20:30 | 292 | 289
2016-12-31 21:00 | 297 | 295
2016-12-31 21:30 | 283 | 280
2016-12-31 22:00 | 268 | 266
2016-12-31 22:30 | 259 | 256
2016-12-31 23:00 | 253 | 251
2016-12-31 23:30 | 281 | 279
2017-01-01 | 283 | 281
2017-01-01 00:30 | 206 | 203
2017-01-01 01:00 | 227 | 224
2017-01-01 01:30 | 261 | 259
2017-01-01 02:00 | 258 | 256
2017-01-01 02:30 | 249 | 247
2017-01-01 03:00 | 242 | 240
2017-01-01 03:30 | 237 | 235
2017-01-01 04:00 | 235 | 233
2017-01-01 04:30 | 234 | 231
2017-01-01 05:00 | 233 | 231
2017-01-01 05:30 | 232 | 230
2017-01-01 06:00 | 229 | 226
2017-01-01 06:30 | 226 | 224
2017-01-01 07:00 | 219 | 216
2017-01-01 07:30 | 197 | 194
2017-01-01 08:00 | 200 | 198
2017-01-01 08:30 | 209 | 207
2017-01-01 09:00 | 220 | 218
2017-01-01 09:30 | 227 | 224
2017-01-01 10:00 | 233 | 231
2017-01-01 10:30 | 230 | 228
2017-01-01 11:00 | 192 | 190
2017-01-01 11:30 | 181 | 178
2017-01-01 12:00 | 172 | 169
2017-01-01 12:30 | 174 | 171
2017-01-01 13:00 | 183 | 180
2017-01-01 13:30 | 189 | 187
2017-01-01 14:00 | 196 | 194
2017-01-01 14:30 | 200 | 198
2017-01-01 15:00 | 187 | 185
2017-01-01 15:30 | 201 | 200
2017-01-01 16:00 | 152 | 150
2017-01-01 16:30 | 141 | 139
2017-01-01 17:00 | 124 | 122
2017-01-01 17:30 | 122 | 120
2017-01-01 18:00 | 71 | 69
2017-01-01 18:30 | 119 | 118
2017-01-01 19:00 | 138 | 136
2017-01-01 19:30 | 178 | 176
2017-01-01 20:00 | 164 | 162
2017-01-01 20:30 | 170 | 168
2017-01-01 21:00 | 240 | 239
2017-01-01 21:30 | 265 | 264
2017-01-01 22:00 | 249 | 248
2017-01-01 22:30 | 223 | 222
2017-01-01 23:00 | 228 | 226
2017-01-01 23:30 | 257 | 255
2017-01-02 | 313 | 311
2017-01-02 00:30 | 361 | 360
2017-01-02 01:00 | 352 | 350
2017-01-02 01:30 | 344 | 342
2017-01-02 02:00 | 337 | 336
2017-01-02 02:30 | 333 | 331
2017-01-02 03:00 | 329 | 327
2017-01-02 03:30 | 327 | 325
2017-01-02 04:00 | 326 | 324
2017-01-02 04:30 | 325 | 323
2017-01-02 05:00 | 324 | 322
2017-01-02 05:30 | 326 | 325
2017-01-02 06:00 | 325 | 324
2017-01-02 06:30 | 329 | 328
2017-01-02 07:00 | 326 | 324
2017-01-02 07:30 | 307 | 305
2017-01-02 08:00 | 312 | 310
2017-01-02 08:30 | 320 | 318
2017-01-02 09:00 | 296 | 294
2017-01-02 09:30 | 262 | 260
2017-01-02 10:00 | 274 | 272
2017-01-02 10:30 | 275 | 273
2017-01-02 11:00 | 265 | 263
2017-01-02 11:30 | 261 | 259
2017-01-02 12:00 | 256 | 253
2017-01-02 12:30 | 290 | 288
2017-01-02 13:00 | 279 | 276
2017-01-02 13:30 | 274 | 273
2017-01-02 14:00 | 276 | 275
2017-01-02 14:30 | 288 | 286
2017-01-02 15:00 | 293 | 291
2017-01-02 15:30 | 286 | 284
2017-01-02 16:00 | 195 | 192
2017-01-02 16:30 | 188 | 187
2017-01-02 17:00 | 194 | 192
2017-01-02 17:30 | 211 | 209
2017-01-02 18:00 | 220 | 218
2017-01-02 18:30 | 259 | 257
2017-01-02 19:00 | 294 | 293
2017-01-02 19:30 | 300 | 299
2017-01-02 20:00 | 303 | 302
2017-01-02 20:30 | 329 | 327
2017-01-02 21:00 | 322 | 320
2017-01-02 21:30 | 310 | 308
2017-01-02 22:00 | 304 | 303
2017-01-02 22:30 | 314 | 312
2017-01-02 23:00 | 311 | 310
2017-01-02 23:30 | 275 | 273
2017-01-03 | 282 | 281
2017-01-03 00:30 | 279 | 278
2017-01-03 01:00 | 273 | 271
2017-01-03 01:30 | 269 | 267
2017-01-03 02:00 | 306 | 305
2017-01-03 02:30 | 310 | 308
2017-01-03 03:00 | 309 | 307
2017-01-03 03:30 | 308 | 306
2017-01-03 04:00 | 306 | 304
2017-01-03 04:30 | 305 | 303
2017-01-03 05:00 | 305 | 303
2017-01-03 05:30 | 309 | 307
2017-01-03 06:00 | 316 | 314
2017-01-03 06:30 | 292 | 290
2017-01-03 07:00 | 255 | 253
2017-01-03 07:30 | 257 | 255
2017-01-03 08:00 | 243 | 242
2017-01-03 08:30 | 248 | 246
2017-01-03 09:00 | 241 | 239
2017-01-03 09:30 | 259 | 258
2017-01-03 10:00 | 270 | 269
2017-01-03 10:30 | 271 | 270
2017-01-03 11:00 | 274 | 272
2017-01-03 11:30 | 280 | 279
2017-01-03 12:00 | 284 | 283
2017-01-03 12:30 | 256 | 253
2017-01-03 13:00 | 299 | 297
2017-01-03 13:30 | 298 | 296
2017-01-03 14:00 | 304 | 302
2017-01-03 14:30 | 308 | 307
2017-01-03 15:00 | 310 | 308
2017-01-03 15:30 | 309 | 308
2017-01-03 16:00 | 298 | 297
2017-01-03 16:30 | 307 | 305
2017-01-03 17:00 | 316 | 315
2017-01-03 17:30 | 324 | 323
2017-01-03 18:00 | 331 | 330
2017-01-03 18:30 | 356 | 355
2017-01-03 19:00 | 308 | 306
2017-01-03 19:30 | 304 | 302
2017-01-03 20:00 | 316 | 314
2017-01-03 20:30 | 317 | 315
2017-01-03 21:00 | 331 | 330
2017-01-03 21:30 | 378 | 377
2017-01-03 22:00 | 376 | 376
2017-01-03 22:30 | 392 | 392
2017-01-03 23:00 | 379 | 379
2017-01-03 23:30 | 361 | 360
2017-01-04 | 350 | 348
2017-01-04 00:30 | 343 | 341
2017-01-04 01:00 | 334 | 333
2017-01-04 01:30 | 329 | 327
2017-01-04 02:00 | 322 | 321
2017-01-04 02:30 | 318 | 317
2017-01-04 03:00 | 317 | 316
2017-01-04 03:30 | 314 | 313
2017-01-04 04:00 | 314 | 313
2017-01-04 04:30 | 313 | 312
2017-01-04 05:00 | 312 | 311
2017-01-04 05:30 | 316 | 315
2017-01-04 06:00 | 318 | 317
2017-01-04 06:30 | 322 | 321
2017-01-04 07:00 | 336 | 335
2017-01-04 07:30 | 324 | 323
2017-01-04 08:00 | 334 | 333
2017-01-04 08:30 | 347 | 346
2017-01-04 09:00 | 348 | 346
2017-01-04 09:30 | 353 | 351
2017-01-04 10:00 | 357 | 356
2017-01-04 10:30 | 370 | 369
2017-01-04 11:00 | 366 | 365
2017-01-04 11:30 | 356 | 355
2017-01-04 12:00 | 339 | 338
2017-01-04 12:30 | 327 | 326
2017-01-04 13:00 | 332 | 331
2017-01-04 13:30 | 340 | 339
2017-01-04 14:00 | 348 | 347
2017-01-04 14:30 | 354 | 353
2017-01-04 15:00 | 373 | 372
2017-01-04 15:30 | 367 | 366
2017-01-04 16:00 | 376 | 376
2017-01-04 16:30 | 368 | 367
2017-01-04 17:00 | 361 | 360
2017-01-04 17:30 | 367 | 366
2017-01-04 18:00 | 372 | 371
2017-01-04 18:30 | 373 | 372
2017-01-04 19:00 | 363 | 362
2017-01-04 19:30 | 368 | 367
2017-01-04 20:00 | 362 | 361
2017-01-04 20:30 | 351 | 350
2017-01-04 21:00 | 346 | 345
2017-01-04 21:30 | 345 | 344
2017-01-04 22:00 | 340 | 339
2017-01-04 22:30 | 359 | 358
2017-01-04 23:00 | 342 | 341
2017-01-04 23:30 | 294 | 293
2017-01-05 | 305 | 305
2017-01-05 00:30 | 306 | 305
2017-01-05 01:00 | 300 | 299
2017-01-05 01:30 | 292 | 292
2017-01-05 02:00 | 287 | 286
2017-01-05 02:30 | 281 | 280
2017-01-05 03:00 | 280 | 279
2017-01-05 03:30 | 277 | 277
2017-01-05 04:00 | 274 | 273
2017-01-05 04:30 | 273 | 272
2017-01-05 05:00 | 274 | 273
2017-01-05 05:30 | 279 | 278
2017-01-05 06:00 | 281 | 281
2017-01-05 06:30 | 291 | 290
2017-01-05 07:00 | 291 | 290
2017-01-05 07:30 | 286 | 286
2017-01-05 08:00 | 297 | 296
2017-01-05 08:30 | 292 | 291
2017-01-05 09:00 | 299 | 298
2017-01-05 09:30 | 303 | 302
2017-01-05 10:00 | 306 | 305
2017-01-05 10:30 | 303 | 302
2017-01-05 11:00 | 303 | 302
2017-01-05 11:30 | 309 | 308
2017-01-05 12:00 | 320 | 319
2017-01-05 12:30 | 320 | 319
2017-01-05 13:00 | 316 | 315
2017-01-05 13:30 | 312 | 311
2017-01-05 14:00 | 304 | 302
2017-01-05 14:30 | 321 | 320
2017-01-05 15:00 | 324 | 323
2017-01-05 15:30 | 328 | 327
2017-01-05 16:00 | 329 | 328
2017-01-05 16:30 | 313 | 312
2017-01-05 17:00 | 315 | 314
2017-01-05 17:30 | 315 | 314
2017-01-05 18:00 | 328 | 327
2017-01-05 18:30 | 360 | 359
2017-01-05 19:00 | 364 | 363
2017-01-05 19:30 | 364 | 363
2017-01-05 20:00 | 353 | 352
2017-01-05 20:30 | 334 | 333
2017-01-05 21:00 | 320 | 319
2017-01-05 21:30 | 305 | 304
2017-01-05 22:00 | 288 | 287
2017-01-05 22:30 | 240 | 239
2017-01-05 23:00 | 227 | 226
2017-01-05 23:30 | 236 | 235
2017-01-06 | 238 | 237
2017-01-06 00:30 | 228 | 227
2017-01-06 01:00 | 222 | 221
2017-01-06 01:30 | 214 | 213
2017-01-06 02:00 | 209 | 208
2017-01-06 02:30 | 207 | 205
2017-01-06 03:00 | 205 | 204
2017-01-06 03:30 | 203 | 202
2017-01-06 04:00 | 201 | 200
2017-01-06 04:30 | 201 | 200
2017-01-06 05:00 | 202 | 200
2017-01-06 05:30 | 204 | 203
2017-01-06 06:00 | 207 | 206
2017-01-06 06:30 | 220 | 219
2017-01-06 07:00 | 231 | 230
2017-01-06 07:30 | 249 | 248
2017-01-06 08:00 | 265 | 264
2017-01-06 08:30 | 281 | 281
2017-01-06 09:00 | 284 | 283
2017-01-06 09:30 | 280 | 279
2017-01-06 10:00 | 279 | 278
2017-01-06 10:30 | 296 | 295
2017-01-06 11:00 | 307 | 306
2017-01-06 11:30 | 248 | 247
2017-01-06 12:00 | 212 | 211
2017-01-06 12:30 | 208 | 207
2017-01-06 13:00 | 211 | 209
2017-01-06 13:30 | 227 | 225
2017-01-06 14:00 | 230 | 229
2017-01-06 14:30 | 234 | 233
2017-01-06 15:00 | 233 | 232
2017-01-06 15:30 | 211 | 209
2017-01-06 16:00 | 199 | 198
2017-01-06 16:30 | 200 | 198
2017-01-06 17:00 | 202 | 200
2017-01-06 17:30 | 212 | 211
2017-01-06 18:00 | 224 | 222
2017-01-06 18:30 | 228 | 226
2017-01-06 19:00 | 232 | 231
2017-01-06 19:30 | 258 | 257
2017-01-06 20:00 | 256 | 255
2017-01-06 20:30 | 222 | 221
2017-01-06 21:00 | 211 | 209
2017-01-06 21:30 | 188 | 186
2017-01-06 22:00 | 178 | 177
2017-01-06 22:30 | 172 | 171
2017-01-06 23:00 | 161 | 159
2017-01-06 23:30 | 148 | 147
2017-01-07 | 137 | 136
2017-01-07 00:30 | 190 | 189
2017-01-07 01:00 | 204 | 203
2017-01-07 01:30 | 199 | 198
2017-01-07 02:00 | 195 | 194
2017-01-07 02:30 | 190 | 189
2017-01-07 03:00 | 187 | 185
2017-01-07 03:30 | 184 | 182
2017-01-07 04:00 | 184 | 183
2017-01-07 04:30 | 187 | 186
2017-01-07 05:00 | 188 | 186
2017-01-07 05:30 | 190 | 188
2017-01-07 06:00 | 192 | 191
2017-01-07 06:30 | 195 | 193
2017-01-07 07:00 | 203 | 201
2017-01-07 07:30 | 214 | 212
2017-01-07 08:00 | 225 | 223
2017-01-07 08:30 | 239 | 238
2017-01-07 09:00 | 252 | 251
2017-01-07 09:30 | 218 | 217
2017-01-07 10:00 | 168 | 167
2017-01-07 10:30 | 170 | 169
2017-01-07 11:00 | 170 | 169
2017-01-07 11:30 | 180 | 179
2017-01-07 12:00 | 200 | 199
2017-01-07 12:30 | 228 | 227
2017-01-07 13:00 | 229 | 228
2017-01-07 13:30 | 238 | 237
2017-01-07 14:00 | 243 | 242
2017-01-07 14:30 | 245 | 244
2017-01-07 15:00 | 246 | 245
2017-01-07 15:30 | 251 | 250
2017-01-07 16:00 | 260 | 259
2017-01-07 16:30 | 267 | 266
2017-01-07 17:00 | 272 | 271
2017-01-07 17:30 | 267 | 266
2017-01-07 18:00 | 278 | 277
2017-01-07 18:30 | 284 | 283
2017-01-07 19:00 | 281 | 280
2017-01-07 19:30 | 328 | 328
2017-01-07 20:00 | 330 | 329
2017-01-07 20:30 | 312 | 311
2017-01-07 21:00 | 301 | 300
2017-01-07 21:30 | 290 | 289
2017-01-07 22:00 | 280 | 279
2017-01-07 22:30 | 265 | 264
2017-01-07 23:00 | 254 | 253
2017-01-07 23:30 | 239 | 238
2017-01-08 | 227 | 226
2017-01-08 00:30 | 219 | 218
2017-01-08 01:00 | 214 | 213
2017-01-08 01:30 | 205 | 204
2017-01-08 02:00 | 200 | 200
2017-01-08 02:30 | 195 | 194
2017-01-08 03:00 | 192 | 192
2017-01-08 03:30 | 191 | 190
2017-01-08 04:00 | 188 | 187
2017-01-08 04:30 | 186 | 185
2017-01-08 05:00 | 184 | 183
2017-01-08 05:30 | 186 | 185
2017-01-08 06:00 | 187 | 187
2017-01-08 06:30 | 187 | 187
2017-01-08 07:00 | 192 | 191
2017-01-08 07:30 | 199 | 199
2017-01-08 08:00 | 206 | 206
2017-01-08 08:30 | 216 | 215
2017-01-08 09:00 | 225 | 224
2017-01-08 09:30 | 237 | 237
2017-01-08 10:00 | 246 | 245
2017-01-08 10:30 | 250 | 248
2017-01-08 11:00 | 251 | 250
2017-01-08 11:30 | 254 | 253
2017-01-08 12:00 | 260 | 259
2017-01-08 12:30 | 262 | 261
2017-01-08 13:00 | 265 | 264
2017-01-08 13:30 | 273 | 272
2017-01-08 14:00 | 274 | 273
2017-01-08 14:30 | 276 | 275
2017-01-08 15:00 | 282 | 281
2017-01-08 15:30 | 294 | 293
2017-01-08 16:00 | 298 | 297
2017-01-08 16:30 | 293 | 292
2017-01-08 17:00 | 273 | 272
2017-01-08 17:30 | 281 | 279
2017-01-08 18:00 | 282 | 281
2017-01-08 18:30 | 312 | 311
2017-01-08 19:00 | 335 | 333
2017-01-08 19:30 | 340 | 338
2017-01-08 20:00 | 340 | 338
2017-01-08 20:30 | 332 | 330
2017-01-08 21:00 | 319 | 317
2017-01-08 21:30 | 297 | 295
2017-01-08 22:00 | 284 | 282
2017-01-08 22:30 | 267 | 265
2017-01-08 23:00 | 265 | 263
2017-01-08 23:30 | 252 | 250
2017-01-09 | 242 | 240
2017-01-09 00:30 | 232 | 231
2017-01-09 01:00 | 227 | 225
2017-01-09 01:30 | 221 | 219
2017-01-09 02:00 | 217 | 215
2017-01-09 02:30 | 211 | 209
2017-01-09 03:00 | 209 | 207
2017-01-09 03:30 | 210 | 207
2017-01-09 04:00 | 209 | 206
2017-01-09 04:30 | 199 | 196
2017-01-09 05:00 | 198 | 196
2017-01-09 05:30 | 205 | 202
2017-01-09 06:00 | 209 | 206
2017-01-09 06:30 | 233 | 231
2017-01-09 07:00 | 255 | 253
2017-01-09 07:30 | 320 | 318
2017-01-09 08:00 | 338 | 337
2017-01-09 08:30 | 352 | 351
2017-01-09 09:00 | 354 | 353
2017-01-09 09:30 | 293 | 291
2017-01-09 10:00 | 257 | 255
2017-01-09 10:30 | 261 | 259
2017-01-09 11:00 | 268 | 265
2017-01-09 11:30 | 266 | 264
2017-01-09 12:00 | 265 | 263
2017-01-09 12:30 | 260 | 258
2017-01-09 13:00 | 268 | 266
2017-01-09 13:30 | 275 | 273
2017-01-09 14:00 | 274 | 272
2017-01-09 14:30 | 271 | 269
2017-01-09 15:00 | 279 | 277
2017-01-09 15:30 | 287 | 285
2017-01-09 16:00 | 288 | 286
2017-01-09 16:30 | 292 | 290
2017-01-09 17:00 | 294 | 292
2017-01-09 17:30 | 298 | 296
2017-01-09 18:00 | 299 | 297
2017-01-09 18:30 | 297 | 295
2017-01-09 19:00 | 303 | 302
2017-01-09 19:30 | 308 | 306
2017-01-09 20:00 | 294 | 292
2017-01-09 20:30 | 244 | 241
2017-01-09 21:00 | 233 | 231
2017-01-09 21:30 | 215 | 213
2017-01-09 22:00 | 201 | 199
2017-01-09 22:30 | 185 | 183
2017-01-09 23:00 | 170 | 168
2017-01-09 23:30 | 194 | 192
2017-01-10 | 233 | 231
2017-01-10 00:30 | 227 | 225
2017-01-10 01:00 | 220 | 218
2017-01-10 01:30 | 216 | 214
2017-01-10 02:00 | 208 | 206
2017-01-10 02:30 | 205 | 203
2017-01-10 03:00 | 201 | 199
2017-01-10 03:30 | 199 | 198
2017-01-10 04:00 | 199 | 197
2017-01-10 04:30 | 247 | 245
2017-01-10 05:00 | 252 | 250
2017-01-10 05:30 | 259 | 258
2017-01-10 06:00 | 266 | 264
2017-01-10 06:30 | 258 | 256
2017-01-10 07:00 | 206 | 204
2017-01-10 07:30 | 223 | 222
2017-01-10 08:00 | 240 | 239
2017-01-10 08:30 | 263 | 261
2017-01-10 09:00 | 279 | 278
2017-01-10 09:30 | 278 | 276
2017-01-10 10:00 | 276 | 274
2017-01-10 10:30 | 237 | 235
2017-01-10 11:00 | 219 | 217
2017-01-10 11:30 | 216 | 213
2017-01-10 12:00 | 218 | 215
2017-01-10 12:30 | 211 | 209
2017-01-10 13:00 | 217 | 215
2017-01-10 13:30 | 209 | 207
2017-01-10 14:00 | 227 | 225
2017-01-10 14:30 | 211 | 209
2017-01-10 15:00 | 214 | 212
2017-01-10 15:30 | 211 | 209
2017-01-10 16:00 | 178 | 176
2017-01-10 16:30 | 92 | 90
2017-01-10 17:00 | 108 | 107
2017-01-10 17:30 | 117 | 115
2017-01-10 18:00 | 119 | 117
2017-01-10 18:30 | 121 | 119
2017-01-10 19:00 | 128 | 127
2017-01-10 19:30 | 136 | 134
2017-01-10 20:00 | 131 | 130
2017-01-10 20:30 | 226 | 225
2017-01-10 21:00 | 251 | 249
2017-01-10 21:30 | 235 | 234
2017-01-10 22:00 | 219 | 217
2017-01-10 22:30 | 189 | 187
2017-01-10 23:00 | 179 | 178
2017-01-10 23:30 | 168 | 167
2017-01-11 | 155 | 153
2017-01-11 00:30 | 146 | 144
2017-01-11 01:00 | 140 | 138
2017-01-11 01:30 | 135 | 133
2017-01-11 02:00 | 132 | 130
2017-01-11 02:30 | 129 | 127
2017-01-11 03:00 | 125 | 123
2017-01-11 03:30 | 121 | 120
2017-01-11 04:00 | 118 | 116
2017-01-11 04:30 | 118 | 116
2017-01-11 05:00 | 120 | 118
2017-01-11 05:30 | 124 | 122
2017-01-11 06:00 | 130 | 129
2017-01-11 06:30 | 145 | 144
2017-01-11 07:00 | 136 | 135
2017-01-11 07:30 | 169 | 168
2017-01-11 08:00 | 184 | 183
2017-01-11 08:30 | 154 | 153
2017-01-11 09:00 | 159 | 157
2017-01-11 09:30 | 158 | 157
2017-01-11 10:00 | 157 | 156
2017-01-11 10:30 | 162 | 160
2017-01-11 11:00 | 192 | 191
2017-01-11 11:30 | 181 | 179
2017-01-11 12:00 | 188 | 186
2017-01-11 12:30 | 177 | 175
2017-01-11 13:00 | 169 | 168
2017-01-11 13:30 | 133 | 131
2017-01-11 14:00 | 84 | 82
2017-01-11 14:30 | 26 | 21
2017-01-11 15:00 | 28 | 22
2017-01-11 15:30 | 69 | 58
2017-01-11 16:00 | 66 | 56
2017-01-11 16:30 | 15 | 10
2017-01-11 17:00 | 11 | 7
2017-01-11 17:30 | 70 | 63
2017-01-11 18:00 | 70 | 62
2017-01-11 18:30 | 15 | 13
2017-01-11 19:00 | 38 | 29
2017-01-11 19:30 | 37 | 26
2017-01-11 20:00 | 45 | 43
2017-01-11 20:30 | 79 | 78
2017-01-11 21:00 | 130 | 129
2017-01-11 21:30 | 164 | 163
2017-01-11 22:00 | 167 | 167
2017-01-11 22:30 | 71 | 68
2017-01-11 23:00 | 27 | 23
2017-01-11 23:30 | 97 | 97
2017-01-12 | 150 | 149
2017-01-12 00:30 | 150 | 149
2017-01-12 01:00 | 145 | 144
2017-01-12 01:30 | 138 | 138
2017-01-12 02:00 | 136 | 136
2017-01-12 02:30 | 132 | 131
2017-01-12 03:00 | 129 | 128
2017-01-12 03:30 | 128 | 127
2017-01-12 04:00 | 127 | 127
2017-01-12 04:30 | 128 | 127
2017-01-12 05:00 | 129 | 128
2017-01-12 05:30 | 134 | 134
2017-01-12 06:00 | 137 | 137
2017-01-12 06:30 | 154 | 153
2017-01-12 07:00 | 170 | 169
2017-01-12 07:30 | 191 | 190
2017-01-12 08:00 | 205 | 205
2017-01-12 08:30 | 216 | 215
2017-01-12 09:00 | 206 | 205
2017-01-12 09:30 | 226 | 225
2017-01-12 10:00 | 232 | 231
2017-01-12 10:30 | 225 | 223
2017-01-12 11:00 | 220 | 218
2017-01-12 11:30 | 220 | 218
2017-01-12 12:00 | 196 | 194
2017-01-12 12:30 | 154 | 152
2017-01-12 13:00 | 111 | 109
2017-01-12 13:30 | 59 | 56
2017-01-12 14:00 | 3 | 1
2017-01-12 14:30 | 43 | 36
2017-01-12 15:00 | 45 | 37
2017-01-12 15:30 | 53 | 44
2017-01-12 16:00 | 71 | 64
2017-01-12 16:30 | 78 | 70
2017-01-12 17:00 | 74 | 66
2017-01-12 17:30 | 83 | 75
2017-01-12 18:00 | 79 | 72
2017-01-12 18:30 | 45 | 39
2017-01-12 19:00 | 3 | 2
2017-01-12 19:30 | 4 | 2
2017-01-12 20:00 | 3 | 2
2017-01-12 20:30 | 18 | 15
2017-01-12 21:00 | 88 | 85
2017-01-12 21:30 | 114 | 113
2017-01-12 22:00 | 111 | 110
2017-01-12 22:30 | 55 | 51
2017-01-12 23:00 | 57 | 52
2017-01-12 23:30 | 103 | 101
2017-01-13 | 144 | 143
2017-01-13 00:30 | 149 | 148
2017-01-13 01:00 | 146 | 145
2017-01-13 01:30 | 141 | 140
2017-01-13 02:00 | 137 | 136
2017-01-13 02:30 | 133 | 132
2017-01-13 03:00 | 131 | 130
2017-01-13 03:30 | 130 | 129
2017-01-13 04:00 | 128 | 127
2017-01-13 04:30 | 127 | 126
2017-01-13 05:00 | 129 | 128
2017-01-13 05:30 | 138 | 137
2017-01-13 06:00 | 142 | 141
2017-01-13 06:30 | 156 | 155
2017-01-13 07:00 | 94 | 92
2017-01-13 07:30 | 151 | 150
2017-01-13 08:00 | 200 | 199
2017-01-13 08:30 | 216 | 216
2017-01-13 09:00 | 204 | 204
2017-01-13 09:30 | 199 | 198
2017-01-13 10:00 | 200 | 200
2017-01-13 10:30 | 189 | 189
2017-01-13 11:00 | 160 | 159
2017-01-13 11:30 | 152 | 152
2017-01-13 12:00 | 81 | 78
2017-01-13 12:30 | 74 | 69
2017-01-13 13:00 | 84 | 81
2017-01-13 13:30 | 50 | 43
2017-01-13 14:00 | 77 | 73
2017-01-13 14:30 | 60 | 53
2017-01-13 15:00 | 8 | 8
2017-01-13 15:30 | 21 | 19
2017-01-13 16:00 | 11 | 8
2017-01-13 16:30 | 46 | 37
2017-01-13 17:00 | 47 | 38
2017-01-13 17:30 | 47 | 38
2017-01-13 18:00 | 35 | 29
2017-01-13 18:30 | 41 | 32
2017-01-13 19:00 | 77 | 68
2017-01-13 19:30 | 64 | 56
2017-01-13 20:00 | 41 | 33
2017-01-13 20:30 | 18 | 14
2017-01-13 21:00 | 86 | 85
2017-01-13 21:30 | 165 | 164
2017-01-13 22:00 | 168 | 168
2017-01-13 22:30 | 60 | 57
2017-01-13 23:00 | 19 | 15
2017-01-13 23:30 | 67 | 65
2017-01-14 | 124 | 124
2017-01-14 00:30 | 112 | 110
2017-01-14 01:00 | 161 | 160
2017-01-14 01:30 | 224 | 223
2017-01-14 02:00 | 226 | 225
2017-01-14 02:30 | 223 | 223
2017-01-14 03:00 | 220 | 219
2017-01-14 03:30 | 217 | 216
2017-01-14 04:00 | 215 | 215
2017-01-14 04:30 | 212 | 212
2017-01-14 05:00 | 212 | 212
2017-01-14 05:30 | 213 | 213
2017-01-14 06:00 | 222 | 222
2017-01-14 06:30 | 216 | 216
2017-01-14 07:00 | 187 | 186
2017-01-14 07:30 | 190 | 189
2017-01-14 08:00 | 213 | 213
2017-01-14 08:30 | 231 | 231
2017-01-14 09:00 | 260 | 259
2017-01-14 09:30 | 264 | 263
2017-01-14 10:00 | 230 | 228
2017-01-14 10:30 | 204 | 202
2017-01-14 11:00 | 206 | 205
2017-01-14 11:30 | 185 | 183
2017-01-14 12:00 | 183 | 182
2017-01-14 12:30 | 169 | 167
2017-01-14 13:00 | 188 | 187
2017-01-14 13:30 | 195 | 194
2017-01-14 14:00 | 141 | 139
2017-01-14 14:30 | 129 | 127
2017-01-14 15:00 | 91 | 89
2017-01-14 15:30 | 25 | 23
2017-01-14 16:00 | 25 | 22
2017-01-14 16:30 | 11 | 8
2017-01-14 17:00 | 31 | 24
2017-01-14 17:30 | 32 | 28
2017-01-14 18:00 | 24 | 22
2017-01-14 18:30 | 17 | 13
2017-01-14 19:00 | 22 | 16
2017-01-14 19:30 | 16 | 11
2017-01-14 20:00 | 41 | 37
2017-01-14 20:30 | 55 | 53
2017-01-14 21:00 | 130 | 129
2017-01-14 21:30 | 168 | 167
2017-01-14 22:00 | 146 | 145
2017-01-14 22:30 | 83 | 82
2017-01-14 23:00 | 12 | 6
2017-01-14 23:30 | 73 | 72
2017-01-15 | 122 | 121
2017-01-15 00:30 | 202 | 201
2017-01-15 01:00 | 240 | 240
2017-01-15 01:30 | 237 | 236
2017-01-15 02:00 | 232 | 231
2017-01-15 02:30 | 230 | 229
2017-01-15 03:00 | 229 | 228
2017-01-15 03:30 | 241 | 240
2017-01-15 04:00 | 228 | 227
2017-01-15 04:30 | 227 | 226
2017-01-15 05:00 | 227 | 226
2017-01-15 05:30 | 230 | 230
2017-01-15 06:00 | 240 | 240
2017-01-15 06:30 | 232 | 231
2017-01-15 07:00 | 242 | 241
2017-01-15 07:30 | 242 | 241
2017-01-15 08:00 | 244 | 244
2017-01-15 08:30 | 255 | 255
2017-01-15 09:00 | 267 | 266
2017-01-15 09:30 | 284 | 283
2017-01-15 10:00 | 290 | 289
2017-01-15 10:30 | 257 | 256
2017-01-15 11:00 | 183 | 181
2017-01-15 11:30 | 179 | 177
2017-01-15 12:00 | 184 | 183
2017-01-15 12:30 | 174 | 173
2017-01-15 13:00 | 188 | 187
2017-01-15 13:30 | 142 | 141
2017-01-15 14:00 | 128 | 126
2017-01-15 14:30 | 105 | 104
2017-01-15 15:00 | 56 | 52
2017-01-15 15:30 | 60 | 56
2017-01-15 16:00 | 57 | 53
2017-01-15 16:30 | 59 | 55
2017-01-15 17:00 | 54 | 49
2017-01-15 17:30 | 58 | 54
2017-01-15 18:00 | 61 | 59
2017-01-15 18:30 | 65 | 62
2017-01-15 19:00 | 44 | 37
2017-01-15 19:30 | 58 | 56
2017-01-15 20:00 | 89 | 88
2017-01-15 20:30 | 167 | 166
2017-01-15 21:00 | 221 | 220
2017-01-15 21:30 | 251 | 250
2017-01-15 22:00 | 228 | 228
2017-01-15 22:30 | 170 | 168
2017-01-15 23:00 | 182 | 181
2017-01-15 23:30 | 181 | 179
2017-01-16 | 180 | 178
2017-01-16 00:30 | 192 | 190
2017-01-16 01:00 | 205 | 204
2017-01-16 01:30 | 202 | 201
2017-01-16 02:00 | 194 | 193
2017-01-16 02:30 | 192 | 191
2017-01-16 03:00 | 189 | 188
2017-01-16 03:30 | 187 | 186
2017-01-16 04:00 | 186 | 185
2017-01-16 04:30 | 186 | 185
2017-01-16 05:00 | 189 | 188
2017-01-16 05:30 | 193 | 193
2017-01-16 06:00 | 200 | 199
2017-01-16 06:30 | 195 | 194
2017-01-16 07:00 | 178 | 177
2017-01-16 07:30 | 209 | 208
2017-01-16 08:00 | 233 | 232
2017-01-16 08:30 | 266 | 265
2017-01-16 09:00 | 274 | 272
2017-01-16 09:30 | 272 | 271
2017-01-16 10:00 | 270 | 269
2017-01-16 10:30 | 275 | 274
2017-01-16 11:00 | 282 | 281
2017-01-16 11:30 | 286 | 285
2017-01-16 12:00 | 293 | 292
2017-01-16 12:30 | 292 | 291
2017-01-16 13:00 | 299 | 298
2017-01-16 13:30 | 302 | 301
2017-01-16 14:00 | 266 | 265
2017-01-16 14:30 | 241 | 240
2017-01-16 15:00 | 178 | 176
2017-01-16 15:30 | 149 | 148
2017-01-16 16:00 | 196 | 195
2017-01-16 16:30 | 192 | 190
2017-01-16 17:00 | 188 | 186
2017-01-16 17:30 | 245 | 244
2017-01-16 18:00 | 274 | 273
2017-01-16 18:30 | 279 | 278
2017-01-16 19:00 | 265 | 263
2017-01-16 19:30 | 298 | 296
2017-01-16 20:00 | 350 | 350
2017-01-16 20:30 | 349 | 349
2017-01-16 21:00 | 331 | 331
2017-01-16 21:30 | 312 | 311
2017-01-16 22:00 | 286 | 285
2017-01-16 22:30 | 250 | 248
2017-01-16 23:00 | 237 | 236
2017-01-16 23:30 | 239 | 238
2017-01-17 | 229 | 228
2017-01-17 00:30 | 229 | 227
2017-01-17 01:00 | 236 | 234
2017-01-17 01:30 | 232 | 231
2017-01-17 02:00 | 216 | 215
2017-01-17 02:30 | 210 | 209
2017-01-17 03:00 | 206 | 205
2017-01-17 03:30 | 204 | 203
2017-01-17 04:00 | 203 | 201
2017-01-17 04:30 | 203 | 202
2017-01-17 05:00 | 205 | 204
2017-01-17 05:30 | 209 | 208
2017-01-17 06:00 | 216 | 215
2017-01-17 06:30 | 202 | 200
2017-01-17 07:00 | 226 | 225
2017-01-17 07:30 | 255 | 254
2017-01-17 08:00 | 273 | 271
2017-01-17 08:30 | 283 | 282
2017-01-17 09:00 | 284 | 283
2017-01-17 09:30 | 279 | 277
2017-01-17 10:00 | 285 | 284
2017-01-17 10:30 | 290 | 289
2017-01-17 11:00 | 290 | 289
2017-01-17 11:30 | 294 | 293
2017-01-17 12:00 | 299 | 298
2017-01-17 12:30 | 297 | 296
2017-01-17 13:00 | 300 | 299
2017-01-17 13:30 | 305 | 304
2017-01-17 14:00 | 313 | 312
2017-01-17 14:30 | 275 | 273
2017-01-17 15:00 | 218 | 216
2017-01-17 15:30 | 172 | 170
2017-01-17 16:00 | 175 | 173
2017-01-17 16:30 | 122 | 120
2017-01-17 17:00 | 63 | 61
2017-01-17 17:30 | 61 | 58
2017-01-17 18:00 | 60 | 57
2017-01-17 18:30 | 84 | 81
2017-01-17 19:00 | 167 | 165
2017-01-17 19:30 | 216 | 215
2017-01-17 20:00 | 145 | 143
2017-01-17 20:30 | 175 | 173
2017-01-17 21:00 | 220 | 218
2017-01-17 21:30 | 214 | 212
2017-01-17 22:00 | 208 | 206
2017-01-17 22:30 | 162 | 160
2017-01-17 23:00 | 183 | 181
2017-01-17 23:30 | 190 | 188
2017-01-18 | 180 | 178
2017-01-18 00:30 | 227 | 225
2017-01-18 01:00 | 238 | 237
2017-01-18 01:30 | 231 | 229
2017-01-18 02:00 | 216 | 214
2017-01-18 02:30 | 210 | 209
2017-01-18 03:00 | 207 | 205
2017-01-18 03:30 | 206 | 204
2017-01-18 04:00 | 202 | 200
2017-01-18 04:30 | 203 | 201
2017-01-18 05:00 | 203 | 201
2017-01-18 05:30 | 208 | 206
2017-01-18 06:00 | 213 | 211
2017-01-18 06:30 | 231 | 228
2017-01-18 07:00 | 208 | 204
2017-01-18 07:30 | 232 | 229
2017-01-18 08:00 | 272 | 270
2017-01-18 08:30 | 277 | 275
2017-01-18 09:00 | 248 | 246
2017-01-18 09:30 | 231 | 229
2017-01-18 10:00 | 227 | 224
2017-01-18 10:30 | 224 | 221
2017-01-18 11:00 | 222 | 219
2017-01-18 11:30 | 233 | 230
2017-01-18 12:00 | 232 | 230
2017-01-18 12:30 | 233 | 230
2017-01-18 13:00 | 235 | 232
2017-01-18 13:30 | 252 | 250
2017-01-18 14:00 | 211 | 208
2017-01-18 14:30 | 195 | 192
2017-01-18 15:00 | 104 | 100
2017-01-18 15:30 | 39 | 33
2017-01-18 16:00 | 16 | 3
2017-01-18 16:30 | 47 | 36
2017-01-18 17:00 | 83 | 71
2017-01-18 17:30 | 104 | 95
2017-01-18 18:00 | 100 | 90
2017-01-18 18:30 | 75 | 63
2017-01-18 19:00 | 22 | 9
2017-01-18 19:30 | 18 | 4
2017-01-18 20:00 | 14 | 2
2017-01-18 20:30 | 84 | 81
2017-01-18 21:00 | 175 | 172
2017-01-18 21:30 | 182 | 180
2017-01-18 22:00 | 153 | 150
2017-01-18 22:30 | 90 | 88
2017-01-18 23:00 | 60 | 58
2017-01-18 23:30 | 115 | 113
2017-01-19 | 128 | 126
2017-01-19 00:30 | 164 | 162
2017-01-19 01:00 | 210 | 209
2017-01-19 01:30 | 205 | 204
2017-01-19 02:00 | 203 | 201
2017-01-19 02:30 | 201 | 200
2017-01-19 03:00 | 198 | 197
2017-01-19 03:30 | 196 | 195
2017-01-19 04:00 | 195 | 195
2017-01-19 04:30 | 196 | 195
2017-01-19 05:00 | 199 | 198
2017-01-19 05:30 | 205 | 205
2017-01-19 06:00 | 217 | 215
2017-01-19 06:30 | 234 | 231
2017-01-19 07:00 | 202 | 197
2017-01-19 07:30 | 261 | 258
2017-01-19 08:00 | 283 | 279
2017-01-19 08:30 | 287 | 284
2017-01-19 09:00 | 271 | 267
2017-01-19 09:30 | 239 | 234
2017-01-19 10:00 | 227 | 222
2017-01-19 10:30 | 230 | 225
2017-01-19 11:00 | 226 | 221
2017-01-19 11:30 | 197 | 190
2017-01-19 12:00 | 225 | 221
2017-01-19 12:30 | 237 | 233
2017-01-19 13:00 | 239 | 235
2017-01-19 13:30 | 233 | 229
2017-01-19 14:00 | 225 | 221
2017-01-19 14:30 | 223 | 219
2017-01-19 15:00 | 226 | 222
2017-01-19 15:30 | 222 | 218
2017-01-19 16:00 | 184 | 179
2017-01-19 16:30 | 187 | 183
2017-01-19 17:00 | 143 | 138
2017-01-19 17:30 | 175 | 170
2017-01-19 18:00 | 261 | 257
2017-01-19 18:30 | 263 | 259
2017-01-19 19:00 | 262 | 258
2017-01-19 19:30 | 269 | 265
2017-01-19 20:00 | 268 | 265
2017-01-19 20:30 | 258 | 254
2017-01-19 21:00 | 262 | 259
2017-01-19 21:30 | 244 | 241
2017-01-19 22:00 | 222 | 218
2017-01-19 22:30 | 177 | 172
2017-01-19 23:00 | 155 | 149
2017-01-19 23:30 | 155 | 148
2017-01-20 | 148 | 143
2017-01-20 00:30 | 206 | 202
2017-01-20 01:00 | 267 | 264
2017-01-20 01:30 | 257 | 253
2017-01-20 02:00 | 242 | 238
2017-01-20 02:30 | 232 | 228
2017-01-20 03:00 | 228 | 224
2017-01-20 03:30 | 225 | 221
2017-01-20 04:00 | 221 | 217
2017-01-20 04:30 | 222 | 218
2017-01-20 05:00 | 221 | 218
2017-01-20 05:30 | 228 | 225
2017-01-20 06:00 | 234 | 231
2017-01-20 06:30 | 249 | 246
2017-01-20 07:00 | 237 | 231
2017-01-20 07:30 | 259 | 255
2017-01-20 08:00 | 300 | 297
2017-01-20 08:30 | 329 | 326
2017-01-20 09:00 | 337 | 333
2017-01-20 09:30 | 325 | 322
2017-01-20 10:00 | 299 | 295
2017-01-20 10:30 | 296 | 292
2017-01-20 11:00 | 266 | 261
2017-01-20 11:30 | 314 | 310
2017-01-20 12:00 | 322 | 319
2017-01-20 12:30 | 299 | 295
2017-01-20 13:00 | 299 | 295
2017-01-20 13:30 | 277 | 273
2017-01-20 14:00 | 237 | 231
2017-01-20 14:30 | 182 | 177
2017-01-20 15:00 | 167 | 163
2017-01-20 15:30 | 112 | 106
2017-01-20 16:00 | 22 | 1
2017-01-20 16:30 | 40 | 33
2017-01-20 17:00 | 33 | 21
2017-01-20 17:30 | 60 | 47
2017-01-20 18:00 | 23 | 8
2017-01-20 18:30 | 23 | 14
2017-01-20 19:00 | 20 | 10
2017-01-20 19:30 | 19 | 10
2017-01-20 20:00 | 25 | 17
2017-01-20 20:30 | 21 | 12
2017-01-20 21:00 | 81 | 77
2017-01-20 21:30 | 164 | 161
2017-01-20 22:00 | 173 | 172
2017-01-20 22:30 | 47 | 44
2017-01-20 23:00 | 19 | 12
2017-01-20 23:30 | 25 | 21
2017-01-21 | 103 | 102
2017-01-21 00:30 | 132 | 131
2017-01-21 01:00 | 152 | 150
2017-01-21 01:30 | 161 | 160
2017-01-21 02:00 | 150 | 149
2017-01-21 02:30 | 145 | 144
2017-01-21 03:00 | 141 | 140
2017-01-21 03:30 | 140 | 138
2017-01-21 04:00 | 138 | 137
2017-01-21 04:30 | 139 | 138
2017-01-21 05:00 | 144 | 143
2017-01-21 05:30 | 144 | 143
2017-01-21 06:00 | 149 | 148
2017-01-21 06:30 | 145 | 144
2017-01-21 07:00 | 163 | 162
2017-01-21 07:30 | 168 | 167
2017-01-21 08:00 | 182 | 181
2017-01-21 08:30 | 199 | 198
2017-01-21 09:00 | 205 | 204
2017-01-21 09:30 | 191 | 189
2017-01-21 10:00 | 197 | 195
2017-01-21 10:30 | 197 | 195
2017-01-21 11:00 | 148 | 146
2017-01-21 11:30 | 198 | 196
2017-01-21 12:00 | 222 | 221
2017-01-21 12:30 | 235 | 233
2017-01-21 13:00 | 256 | 254
2017-01-21 13:30 | 262 | 261
2017-01-21 14:00 | 211 | 209
2017-01-21 14:30 | 233 | 231
2017-01-21 15:00 | 274 | 272
2017-01-21 15:30 | 283 | 282
2017-01-21 16:00 | 300 | 298
2017-01-21 16:30 | 304 | 302
2017-01-21 17:00 | 316 | 314
2017-01-21 17:30 | 323 | 322
2017-01-21 18:00 | 322 | 321
2017-01-21 18:30 | 322 | 321
2017-01-21 19:00 | 343 | 342
2017-01-21 19:30 | 383 | 382
2017-01-21 20:00 | 436 | 436
2017-01-21 20:30 | 426 | 426
2017-01-21 21:00 | 413 | 412
2017-01-21 21:30 | 399 | 397
2017-01-21 22:00 | 384 | 383
2017-01-21 22:30 | 354 | 351
2017-01-21 23:00 | 335 | 334
2017-01-21 23:30 | 320 | 318
2017-01-22 | 308 | 307
2017-01-22 00:30 | 313 | 313
2017-01-22 01:00 | 312 | 312
2017-01-22 01:30 | 297 | 297
2017-01-22 02:00 | 281 | 280
2017-01-22 02:30 | 273 | 273
2017-01-22 03:00 | 265 | 264
2017-01-22 03:30 | 242 | 241
2017-01-22 04:00 | 223 | 223
2017-01-22 04:30 | 219 | 218
2017-01-22 05:00 | 220 | 219
2017-01-22 05:30 | 218 | 217
2017-01-22 06:00 | 226 | 226
2017-01-22 06:30 | 221 | 220
2017-01-22 07:00 | 230 | 230
2017-01-22 07:30 | 232 | 231
2017-01-22 08:00 | 239 | 238
2017-01-22 08:30 | 250 | 249
2017-01-22 09:00 | 255 | 254
2017-01-22 09:30 | 265 | 264
2017-01-22 10:00 | 274 | 273
2017-01-22 10:30 | 280 | 279
2017-01-22 11:00 | 286 | 285
2017-01-22 11:30 | 292 | 291
2017-01-22 12:00 | 299 | 298
2017-01-22 12:30 | 306 | 305
2017-01-22 13:00 | 332 | 331
2017-01-22 13:30 | 343 | 342
2017-01-22 14:00 | 350 | 350
2017-01-22 14:30 | 357 | 357
2017-01-22 15:00 | 364 | 364
2017-01-22 15:30 | 382 | 382
2017-01-22 16:00 | 382 | 381
2017-01-22 16:30 | 385 | 384
2017-01-22 17:00 | 392 | 391
2017-01-22 17:30 | 386 | 385
2017-01-22 18:00 | 331 | 331
2017-01-22 18:30 | 335 | 334
2017-01-22 19:00 | 319 | 318
2017-01-22 19:30 | 291 | 290
2017-01-22 20:00 | 294 | 293
2017-01-22 20:30 | 318 | 317
2017-01-22 21:00 | 321 | 320
2017-01-22 21:30 | 317 | 316
2017-01-22 22:00 | 306 | 305
2017-01-22 22:30 | 264 | 263
2017-01-22 23:00 | 246 | 245
2017-01-22 23:30 | 243 | 242
2017-01-23 | 241 | 240
2017-01-23 00:30 | 255 | 254
2017-01-23 01:00 | 252 | 251
2017-01-23 01:30 | 244 | 243
2017-01-23 02:00 | 248 | 247
2017-01-23 02:30 | 268 | 267
2017-01-23 03:00 | 267 | 267
2017-01-23 03:30 | 251 | 250
2017-01-23 04:00 | 237 | 237
2017-01-23 04:30 | 235 | 234
2017-01-23 05:00 | 235 | 234
2017-01-23 05:30 | 239 | 238
2017-01-23 06:00 | 248 | 247
2017-01-23 06:30 | 268 | 267
2017-01-23 07:00 | 252 | 251
2017-01-23 07:30 | 309 | 308
2017-01-23 08:00 | 332 | 331
2017-01-23 08:30 | 340 | 339
2017-01-23 09:00 | 344 | 344
2017-01-23 09:30 | 352 | 351
2017-01-23 10:00 | 354 | 353
2017-01-23 10:30 | 359 | 358
2017-01-23 11:00 | 362 | 361
2017-01-23 11:30 | 366 | 365
2017-01-23 12:00 | 373 | 372
2017-01-23 12:30 | 374 | 373
2017-01-23 13:00 | 370 | 369
2017-01-23 13:30 | 376 | 375
2017-01-23 14:00 | 384 | 383
2017-01-23 14:30 | 389 | 388
2017-01-23 15:00 | 390 | 389
2017-01-23 15:30 | 395 | 394
2017-01-23 16:00 | 407 | 406
2017-01-23 16:30 | 366 | 365
2017-01-23 17:00 | 343 | 342
2017-01-23 17:30 | 365 | 364
2017-01-23 18:00 | 380 | 380
2017-01-23 18:30 | 390 | 390
2017-01-23 19:00 | 379 | 379
2017-01-23 19:30 | 405 | 404
2017-01-23 20:00 | 401 | 401
2017-01-23 20:30 | 417 | 416
2017-01-23 21:00 | 414 | 414
2017-01-23 21:30 | 392 | 391
2017-01-23 22:00 | 367 | 365
2017-01-23 22:30 | 308 | 307
2017-01-23 23:00 | 289 | 288
2017-01-23 23:30 | 283 | 282
2017-01-24 | 274 | 274
2017-01-24 00:30 | 275 | 274
2017-01-24 01:00 | 281 | 280
2017-01-24 01:30 | 268 | 267
2017-01-24 02:00 | 253 | 252
2017-01-24 02:30 | 246 | 245
2017-01-24 03:00 | 244 | 243
2017-01-24 03:30 | 241 | 241
2017-01-24 04:00 | 240 | 239
2017-01-24 04:30 | 237 | 236
2017-01-24 05:00 | 240 | 239
2017-01-24 05:30 | 245 | 244
2017-01-24 06:00 | 244 | 243
2017-01-24 06:30 | 243 | 243
2017-01-24 07:00 | 259 | 258
2017-01-24 07:30 | 343 | 342
2017-01-24 08:00 | 359 | 356
2017-01-24 08:30 | 356 | 353
2017-01-24 09:00 | 336 | 333
2017-01-24 09:30 | 336 | 332
2017-01-24 10:00 | 333 | 329
2017-01-24 10:30 | 331 | 327
2017-01-24 11:00 | 335 | 331
2017-01-24 11:30 | 341 | 337
2017-01-24 12:00 | 346 | 343
2017-01-24 12:30 | 320 | 316
2017-01-24 13:00 | 301 | 297
2017-01-24 13:30 | 242 | 237
2017-01-24 14:00 | 232 | 229
2017-01-24 14:30 | 210 | 207
2017-01-24 15:00 | 228 | 224
2017-01-24 15:30 | 234 | 231
2017-01-24 16:00 | 226 | 223
2017-01-24 16:30 | 173 | 170
2017-01-24 17:00 | 82 | 77
2017-01-24 17:30 | 108 | 106
2017-01-24 18:00 | 140 | 138
2017-01-24 18:30 | 168 | 166
2017-01-24 19:00 | 168 | 166
2017-01-24 19:30 | 174 | 172
2017-01-24 20:00 | 180 | 178
2017-01-24 20:30 | 210 | 208
2017-01-24 21:00 | 295 | 293
2017-01-24 21:30 | 298 | 296
2017-01-24 22:00 | 274 | 272
2017-01-24 22:30 | 211 | 207
2017-01-24 23:00 | 212 | 209
2017-01-24 23:30 | 211 | 208
2017-01-25 | 205 | 202
2017-01-25 00:30 | 222 | 219
2017-01-25 01:00 | 229 | 226
2017-01-25 01:30 | 216 | 213
2017-01-25 02:00 | 198 | 195
2017-01-25 02:30 | 191 | 188
2017-01-25 03:00 | 187 | 183
2017-01-25 03:30 | 185 | 182
2017-01-25 04:00 | 184 | 181
2017-01-25 04:30 | 184 | 180
2017-01-25 05:00 | 185 | 182
2017-01-25 05:30 | 191 | 187
2017-01-25 06:00 | 198 | 195
2017-01-25 06:30 | 197 | 193
2017-01-25 07:00 | 202 | 198
2017-01-25 07:30 | 236 | 233
2017-01-25 08:00 | 277 | 275
2017-01-25 08:30 | 282 | 280
2017-01-25 09:00 | 290 | 288
2017-01-25 09:30 | 299 | 297
2017-01-25 10:00 | 301 | 299
2017-01-25 10:30 | 302 | 300
2017-01-25 11:00 | 242 | 240
2017-01-25 11:30 | 228 | 225
2017-01-25 12:00 | 231 | 228
2017-01-25 12:30 | 238 | 235
2017-01-25 13:00 | 247 | 244
2017-01-25 13:30 | 250 | 247
2017-01-25 14:00 | 244 | 241
2017-01-25 14:30 | 265 | 262
2017-01-25 15:00 | 260 | 257
2017-01-25 15:30 | 257 | 254
2017-01-25 16:00 | 243 | 239
2017-01-25 16:30 | 184 | 180
2017-01-25 17:00 | 114 | 108
2017-01-25 17:30 | 85 | 79
2017-01-25 18:00 | 138 | 134
2017-01-25 18:30 | 197 | 194
2017-01-25 19:00 | 225 | 222
2017-01-25 19:30 | 211 | 208
2017-01-25 20:00 | 197 | 194
2017-01-25 20:30 | 195 | 193
2017-01-25 21:00 | 244 | 242
2017-01-25 21:30 | 240 | 239
2017-01-25 22:00 | 210 | 208
2017-01-25 22:30 | 179 | 177
2017-01-25 23:00 | 147 | 144
2017-01-25 23:30 | 198 | 196
2017-01-26 | 220 | 219
2017-01-26 00:30 | 245 | 243
2017-01-26 01:00 | 287 | 287
2017-01-26 01:30 | 281 | 280
2017-01-26 02:00 | 276 | 275
2017-01-26 02:30 | 274 | 273
2017-01-26 03:00 | 277 | 276
2017-01-26 03:30 | 266 | 265
2017-01-26 04:00 | 261 | 261
2017-01-26 04:30 | 260 | 259
2017-01-26 05:00 | 260 | 260
2017-01-26 05:30 | 259 | 258
2017-01-26 06:00 | 260 | 260
2017-01-26 06:30 | 267 | 266
2017-01-26 07:00 | 271 | 270
2017-01-26 07:30 | 283 | 282
2017-01-26 08:00 | 293 | 292
2017-01-26 08:30 | 303 | 302
2017-01-26 09:00 | 311 | 310
2017-01-26 09:30 | 315 | 314
2017-01-26 10:00 | 316 | 314
2017-01-26 10:30 | 315 | 313
2017-01-26 11:00 | 306 | 305
2017-01-26 11:30 | 301 | 299
2017-01-26 12:00 | 298 | 296
2017-01-26 12:30 | 295 | 294
2017-01-26 13:00 | 297 | 296
2017-01-26 13:30 | 299 | 298
2017-01-26 14:00 | 303 | 301
2017-01-26 14:30 | 305 | 304
2017-01-26 15:00 | 316 | 314
2017-01-26 15:30 | 291 | 289
2017-01-26 16:00 | 321 | 320
2017-01-26 16:30 | 281 | 279
2017-01-26 17:00 | 204 | 201
2017-01-26 17:30 | 218 | 216
2017-01-26 18:00 | 224 | 223
2017-01-26 18:30 | 250 | 249
2017-01-26 19:00 | 232 | 231
2017-01-26 19:30 | 260 | 259
2017-01-26 20:00 | 259 | 257
2017-01-26 20:30 | 261 | 260
2017-01-26 21:00 | 272 | 271
2017-01-26 21:30 | 257 | 256
2017-01-26 22:00 | 283 | 282
2017-01-26 22:30 | 221 | 220
2017-01-26 23:00 | 234 | 233
2017-01-26 23:30 | 239 | 238
2017-01-27 | 279 | 278
2017-01-27 00:30 | 265 | 264
2017-01-27 01:00 | 227 | 225
2017-01-27 01:30 | 260 | 259
2017-01-27 02:00 | 257 | 256
2017-01-27 02:30 | 257 | 256
2017-01-27 03:00 | 255 | 254
2017-01-27 03:30 | 254 | 253
2017-01-27 04:00 | 251 | 251
2017-01-27 04:30 | 250 | 249
2017-01-27 05:00 | 251 | 250
2017-01-27 05:30 | 257 | 256
2017-01-27 06:00 | 254 | 253
2017-01-27 06:30 | 246 | 245
2017-01-27 07:00 | 237 | 235
2017-01-27 07:30 | 263 | 262
2017-01-27 08:00 | 303 | 302
2017-01-27 08:30 | 308 | 305
2017-01-27 09:00 | 324 | 321
2017-01-27 09:30 | 316 | 313
2017-01-27 10:00 | 338 | 336
2017-01-27 10:30 | 332 | 329
2017-01-27 11:00 | 252 | 248
2017-01-27 11:30 | 245 | 241
2017-01-27 12:00 | 294 | 292
2017-01-27 12:30 | 304 | 302
2017-01-27 13:00 | 311 | 309
2017-01-27 13:30 | 312 | 310
2017-01-27 14:00 | 317 | 315
2017-01-27 14:30 | 324 | 322
2017-01-27 15:00 | 321 | 319
2017-01-27 15:30 | 297 | 295
2017-01-27 16:00 | 300 | 297
2017-01-27 16:30 | 281 | 278
2017-01-27 17:00 | 266 | 263
2017-01-27 17:30 | 326 | 323
2017-01-27 18:00 | 335 | 332
2017-01-27 18:30 | 354 | 352
2017-01-27 19:00 | 381 | 380
2017-01-27 19:30 | 395 | 394
2017-01-27 20:00 | 410 | 408
2017-01-27 20:30 | 414 | 413
2017-01-27 21:00 | 407 | 405
2017-01-27 21:30 | 386 | 383
2017-01-27 22:00 | 345 | 342
2017-01-27 22:30 | 283 | 280
2017-01-27 23:00 | 254 | 250
2017-01-27 23:30 | 275 | 272
2017-01-28 | 286 | 283
2017-01-28 00:30 | 297 | 295
2017-01-28 01:00 | 303 | 302
2017-01-28 01:30 | 295 | 293
2017-01-28 02:00 | 280 | 278
2017-01-28 02:30 | 270 | 268
2017-01-28 03:00 | 265 | 263
2017-01-28 03:30 | 263 | 261
2017-01-28 04:00 | 261 | 259
2017-01-28 04:30 | 260 | 258
2017-01-28 05:00 | 260 | 258
2017-01-28 05:30 | 257 | 255
2017-01-28 06:00 | 233 | 230
2017-01-28 06:30 | 221 | 218
2017-01-28 07:00 | 222 | 219
2017-01-28 07:30 | 257 | 256
2017-01-28 08:00 | 273 | 271
2017-01-28 08:30 | 287 | 286
2017-01-28 09:00 | 300 | 298
2017-01-28 09:30 | 310 | 309
2017-01-28 10:00 | 313 | 311
2017-01-28 10:30 | 312 | 310
2017-01-28 11:00 | 314 | 312
2017-01-28 11:30 | 320 | 318
2017-01-28 12:00 | 326 | 324
2017-01-28 12:30 | 330 | 328
2017-01-28 13:00 | 337 | 335
2017-01-28 13:30 | 340 | 338
2017-01-28 14:00 | 343 | 341
2017-01-28 14:30 | 327 | 324
2017-01-28 15:00 | 333 | 330
2017-01-28 15:30 | 345 | 343
2017-01-28 16:00 | 331 | 328
2017-01-28 16:30 | 339 | 335
2017-01-28 17:00 | 296 | 291
2017-01-28 17:30 | 304 | 300
2017-01-28 18:00 | 295 | 291
2017-01-28 18:30 | 305 | 301
2017-01-28 19:00 | 311 | 306
2017-01-28 19:30 | 359 | 356
2017-01-28 20:00 | 406 | 403
2017-01-28 20:30 | 397 | 393
2017-01-28 21:00 | 399 | 395
2017-01-28 21:30 | 393 | 389
2017-01-28 22:00 | 376 | 372
2017-01-28 22:30 | 322 | 318
2017-01-28 23:00 | 290 | 287
2017-01-28 23:30 | 303 | 300
2017-01-29 | 312 | 309
2017-01-29 00:30 | 302 | 300
2017-01-29 01:00 | 293 | 291
2017-01-29 01:30 | 285 | 283
2017-01-29 02:00 | 278 | 275
2017-01-29 02:30 | 274 | 272
2017-01-29 03:00 | 269 | 267
2017-01-29 03:30 | 266 | 264
2017-01-29 04:00 | 265 | 263
2017-01-29 04:30 | 262 | 259
2017-01-29 05:00 | 259 | 256
2017-01-29 05:30 | 262 | 259
2017-01-29 06:00 | 259 | 256
2017-01-29 06:30 | 257 | 254
2017-01-29 07:00 | 263 | 260
2017-01-29 07:30 | 274 | 271
2017-01-29 08:00 | 281 | 278
2017-01-29 08:30 | 293 | 290
2017-01-29 09:00 | 304 | 300
2017-01-29 09:30 | 311 | 308
2017-01-29 10:00 | 306 | 303
2017-01-29 10:30 | 304 | 301
2017-01-29 11:00 | 293 | 290
2017-01-29 11:30 | 255 | 251
2017-01-29 12:00 | 257 | 253
2017-01-29 12:30 | 270 | 266
2017-01-29 13:00 | 280 | 276
2017-01-29 13:30 | 280 | 276
2017-01-29 14:00 | 286 | 283
2017-01-29 14:30 | 282 | 279
2017-01-29 15:00 | 283 | 279
2017-01-29 15:30 | 310 | 307
2017-01-29 16:00 | 277 | 273
2017-01-29 16:30 | 192 | 187
2017-01-29 17:00 | 179 | 175
2017-01-29 17:30 | 173 | 170
2017-01-29 18:00 | 210 | 207
2017-01-29 18:30 | 238 | 235
2017-01-29 19:00 | 184 | 180
2017-01-29 19:30 | 148 | 144
2017-01-29 20:00 | 150 | 146
2017-01-29 20:30 | 187 | 184
2017-01-29 21:00 | 217 | 214
2017-01-29 21:30 | 330 | 327
2017-01-29 22:00 | 351 | 348
2017-01-29 22:30 | 304 | 300
2017-01-29 23:00 | 265 | 261
2017-01-29 23:30 | 280 | 277
2017-01-30 | 283 | 281
2017-01-30 00:30 | 285 | 282
2017-01-30 01:00 | 276 | 274
2017-01-30 01:30 | 268 | 265
2017-01-30 02:00 | 264 | 261
2017-01-30 02:30 | 260 | 258
2017-01-30 03:00 | 258 | 256
2017-01-30 03:30 | 255 | 253
2017-01-30 04:00 | 254 | 251
2017-01-30 04:30 | 252 | 249
2017-01-30 05:00 | 254 | 251
2017-01-30 05:30 | 262 | 260
2017-01-30 06:00 | 264 | 262
2017-01-30 06:30 | 224 | 221
2017-01-30 07:00 | 207 | 203
2017-01-30 07:30 | 251 | 249
2017-01-30 08:00 | 288 | 285
2017-01-30 08:30 | 303 | 300
2017-01-30 09:00 | 290 | 287
2017-01-30 09:30 | 298 | 294
2017-01-30 10:00 | 300 | 296
2017-01-30 10:30 | 305 | 302
2017-01-30 11:00 | 308 | 304
2017-01-30 11:30 | 301 | 297
2017-01-30 12:00 | 297 | 293
2017-01-30 12:30 | 303 | 299
2017-01-30 13:00 | 308 | 304
2017-01-30 13:30 | 279 | 274
2017-01-30 14:00 | 251 | 246
2017-01-30 14:30 | 164 | 159
2017-01-30 15:00 | 115 | 112
2017-01-30 15:30 | 49 | 45
2017-01-30 16:00 | 50 | 46
2017-01-30 16:30 | 64 | 60
2017-01-30 17:00 | 108 | 105
2017-01-30 17:30 | 134 | 131
2017-01-30 18:00 | 112 | 109
2017-01-30 18:30 | 95 | 92
2017-01-30 19:00 | 69 | 66
2017-01-30 19:30 | 70 | 67
2017-01-30 20:00 | 144 | 142
2017-01-30 20:30 | 158 | 155
2017-01-30 21:00 | 219 | 217
2017-01-30 21:30 | 246 | 244
2017-01-30 22:00 | 224 | 221
2017-01-30 22:30 | 146 | 142
2017-01-30 23:00 | 132 | 128
2017-01-30 23:30 | 191 | 188
2017-01-31 | 199 | 196
2017-01-31 00:30 | 197 | 194
2017-01-31 01:00 | 193 | 190
2017-01-31 01:30 | 183 | 180
2017-01-31 02:00 | 178 | 175
2017-01-31 02:30 | 177 | 174
2017-01-31 03:00 | 177 | 173
2017-01-31 03:30 | 175 | 172
2017-01-31 04:00 | 174 | 171
2017-01-31 04:30 | 175 | 172
2017-01-31 05:00 | 176 | 173
2017-01-31 05:30 | 182 | 180
2017-01-31 06:00 | 191 | 188
2017-01-31 06:30 | 185 | 182
2017-01-31 07:00 | 190 | 187
2017-01-31 07:30 | 233 | 231
2017-01-31 08:00 | 228 | 226
2017-01-31 08:30 | 241 | 238
2017-01-31 09:00 | 247 | 245
2017-01-31 09:30 | 239 | 237
2017-01-31 10:00 | 269 | 267
2017-01-31 10:30 | 276 | 273
2017-01-31 11:00 | 213 | 209
2017-01-31 11:30 | 231 | 228
2017-01-31 12:00 | 245 | 242
2017-01-31 12:30 | 263 | 260
2017-01-31 13:00 | 234 | 231
2017-01-31 13:30 | 222 | 219
2017-01-31 14:00 | 207 | 204
2017-01-31 14:30 | 175 | 171
2017-01-31 15:00 | 165 | 161
2017-01-31 15:30 | 73 | 67
2017-01-31 16:00 | 36 | 30
2017-01-31 16:30 | 43 | 38
2017-01-31 17:00 | 41 | 31
2017-01-31 17:30 | 70 | 60
2017-01-31 18:00 | 31 | 22
2017-01-31 18:30 | 50 | 39
2017-01-31 19:00 | 79 | 66
2017-01-31 19:30 | 82 | 71
2017-01-31 20:00 | 29 | 20
2017-01-31 20:30 | 23 | 15
2017-01-31 21:00 | 128 | 125
2017-01-31 21:30 | 213 | 211
2017-01-31 22:00 | 225 | 222
2017-01-31 22:30 | 151 | 148
2017-01-31 23:00 | 176 | 173
2017-01-31 23:30 | 141 | 137
2017-02-01 | 153 | 150
2017-02-01 00:30 | 178 | 176
2017-02-01 01:00 | 198 | 195
2017-02-01 01:30 | 216 | 213
2017-02-01 02:00 | 222 | 220
2017-02-01 02:30 | 214 | 212
2017-02-01 03:00 | 228 | 227
2017-02-01 03:30 | 236 | 235
2017-02-01 04:00 | 238 | 237
2017-02-01 04:30 | 239 | 238
2017-02-01 05:00 | 241 | 239
2017-02-01 05:30 | 251 | 250
2017-02-01 06:00 | 245 | 243
2017-02-01 06:30 | 248 | 246
2017-02-01 07:00 | 277 | 275
2017-02-01 07:30 | 306 | 304
2017-02-01 08:00 | 313 | 311
2017-02-01 08:30 | 334 | 333
2017-02-01 09:00 | 352 | 350
2017-02-01 09:30 | 363 | 362
2017-02-01 10:00 | 326 | 324
2017-02-01 10:30 | 307 | 305
2017-02-01 11:00 | 280 | 278
2017-02-01 11:30 | 257 | 254
2017-02-01 12:00 | 199 | 195
2017-02-01 12:30 | 208 | 204
2017-02-01 13:00 | 217 | 214
2017-02-01 13:30 | 202 | 199
2017-02-01 14:00 | 183 | 179
2017-02-01 14:30 | 143 | 139
2017-02-01 15:00 | 106 | 102
2017-02-01 15:30 | 55 | 52
2017-02-01 16:00 | 42 | 39
2017-02-01 16:30 | 32 | 26
2017-02-01 17:00 | 89 | 81
2017-02-01 17:30 | 59 | 50
2017-02-01 18:00 | 24 | 20
2017-02-01 18:30 | 18 | 13
2017-02-01 19:00 | 22 | 17
2017-02-01 19:30 | 43 | 40
2017-02-01 20:00 | 99 | 97
2017-02-01 20:30 | 108 | 106
2017-02-01 21:00 | 162 | 161
2017-02-01 21:30 | 179 | 178
2017-02-01 22:00 | 155 | 154
2017-02-01 22:30 | 86 | 83
2017-02-01 23:00 | 68 | 65
2017-02-01 23:30 | 82 | 79
2017-02-02 | 86 | 84
2017-02-02 00:30 | 152 | 150
2017-02-02 01:00 | 215 | 214
2017-02-02 01:30 | 218 | 217
2017-02-02 02:00 | 216 | 215
2017-02-02 02:30 | 215 | 214
2017-02-02 03:00 | 215 | 213
2017-02-02 03:30 | 215 | 213
2017-02-02 04:00 | 213 | 212
2017-02-02 04:30 | 205 | 204
2017-02-02 05:00 | 206 | 205
2017-02-02 05:30 | 214 | 213
2017-02-02 06:00 | 216 | 215
2017-02-02 06:30 | 215 | 213
2017-02-02 07:00 | 211 | 209
2017-02-02 07:30 | 248 | 246
2017-02-02 08:00 | 288 | 287
2017-02-02 08:30 | 299 | 298
2017-02-02 09:00 | 293 | 291
2017-02-02 09:30 | 299 | 298
2017-02-02 10:00 | 268 | 267
2017-02-02 10:30 | 272 | 270
2017-02-02 11:00 | 274 | 273
2017-02-02 11:30 | 257 | 255
2017-02-02 12:00 | 223 | 222
2017-02-02 12:30 | 233 | 231
2017-02-02 13:00 | 195 | 193
2017-02-02 13:30 | 99 | 97
2017-02-02 14:00 | 133 | 132
2017-02-02 14:30 | 119 | 117
2017-02-02 15:00 | 100 | 98
2017-02-02 15:30 | 49 | 46
2017-02-02 16:00 | 15 | 8
2017-02-02 16:30 | 38 | 30
2017-02-02 17:00 | 32 | 27
2017-02-02 17:30 | 73 | 63
2017-02-02 18:00 | 22 | 18
2017-02-02 18:30 | 9 | 4
2017-02-02 19:00 | 28 | 21
2017-02-02 19:30 | 50 | 42
2017-02-02 20:00 | 7 | 3
2017-02-02 20:30 | 91 | 90
2017-02-02 21:00 | 182 | 181
2017-02-02 21:30 | 222 | 221
2017-02-02 22:00 | 202 | 200
2017-02-02 22:30 | 88 | 86
2017-02-02 23:00 | 69 | 66
2017-02-02 23:30 | 78 | 76
2017-02-03 | 99 | 97
2017-02-03 00:30 | 167 | 166
2017-02-03 01:00 | 218 | 217
2017-02-03 01:30 | 208 | 207
2017-02-03 02:00 | 205 | 204
2017-02-03 02:30 | 205 | 204
2017-02-03 03:00 | 202 | 201
2017-02-03 03:30 | 204 | 204
2017-02-03 04:00 | 204 | 203
2017-02-03 04:30 | 207 | 206
2017-02-03 05:00 | 209 | 208
2017-02-03 05:30 | 213 | 212
2017-02-03 06:00 | 213 | 212
2017-02-03 06:30 | 216 | 214
2017-02-03 07:00 | 210 | 207
2017-02-03 07:30 | 254 | 252
2017-02-03 08:00 | 290 | 289
2017-02-03 08:30 | 301 | 299
2017-02-03 09:00 | 311 | 310
2017-02-03 09:30 | 288 | 286
2017-02-03 10:00 | 266 | 264
2017-02-03 10:30 | 267 | 265
2017-02-03 11:00 | 257 | 255
2017-02-03 11:30 | 206 | 204
2017-02-03 12:00 | 178 | 176
2017-02-03 12:30 | 190 | 189
2017-02-03 13:00 | 197 | 196
2017-02-03 13:30 | 205 | 204
2017-02-03 14:00 | 200 | 199
2017-02-03 14:30 | 176 | 175
2017-02-03 15:00 | 177 | 176
2017-02-03 15:30 | 184 | 182
2017-02-03 16:00 | 188 | 187
2017-02-03 16:30 | 156 | 154
2017-02-03 17:00 | 104 | 103
2017-02-03 17:30 | 154 | 153
2017-02-03 18:00 | 170 | 169
2017-02-03 18:30 | 185 | 184
2017-02-03 19:00 | 192 | 191
2017-02-03 19:30 | 204 | 203
2017-02-03 20:00 | 206 | 205
2017-02-03 20:30 | 187 | 186
2017-02-03 21:00 | 225 | 224
2017-02-03 21:30 | 245 | 244
2017-02-03 22:00 | 207 | 206
2017-02-03 22:30 | 152 | 151
2017-02-03 23:00 | 153 | 153
2017-02-03 23:30 | 220 | 219
2017-02-04 | 239 | 239
2017-02-04 00:30 | 231 | 230
2017-02-04 01:00 | 222 | 222
2017-02-04 01:30 | 214 | 214
2017-02-04 02:00 | 207 | 207
2017-02-04 02:30 | 202 | 201
2017-02-04 03:00 | 202 | 201
2017-02-04 03:30 | 200 | 199
2017-02-04 04:00 | 197 | 196
2017-02-04 04:30 | 195 | 195
2017-02-04 05:00 | 192 | 191
2017-02-04 05:30 | 194 | 193
2017-02-04 06:00 | 185 | 184
2017-02-04 06:30 | 175 | 174
2017-02-04 07:00 | 179 | 178
2017-02-04 07:30 | 210 | 210
2017-02-04 08:00 | 234 | 234
2017-02-04 08:30 | 248 | 248
2017-02-04 09:00 | 253 | 253
2017-02-04 09:30 | 259 | 259
2017-02-04 10:00 | 266 | 265
2017-02-04 10:30 | 272 | 272
2017-02-04 11:00 | 275 | 274
2017-02-04 11:30 | 271 | 270
2017-02-04 12:00 | 270 | 269
2017-02-04 12:30 | 261 | 260
2017-02-04 13:00 | 282 | 281
2017-02-04 13:30 | 261 | 260
2017-02-04 14:00 | 230 | 228
2017-02-04 14:30 | 225 | 224
2017-02-04 15:00 | 181 | 180
2017-02-04 15:30 | 183 | 182
2017-02-04 16:00 | 166 | 165
2017-02-04 16:30 | 118 | 116
2017-02-04 17:00 | 114 | 112
2017-02-04 17:30 | 140 | 138
2017-02-04 18:00 | 137 | 135
2017-02-04 18:30 | 165 | 163
2017-02-04 19:00 | 130 | 128
2017-02-04 19:30 | 170 | 169
2017-02-04 20:00 | 189 | 187
2017-02-04 20:30 | 208 | 206
2017-02-04 21:00 | 263 | 262
2017-02-04 21:30 | 289 | 288
2017-02-04 22:00 | 261 | 260
2017-02-04 22:30 | 176 | 174
2017-02-04 23:00 | 146 | 144
2017-02-04 23:30 | 170 | 169
2017-02-05 | 205 | 204
2017-02-05 00:30 | 223 | 222
2017-02-05 01:00 | 220 | 219
2017-02-05 01:30 | 210 | 210
2017-02-05 02:00 | 205 | 205
2017-02-05 02:30 | 202 | 201
2017-02-05 03:00 | 202 | 201
2017-02-05 03:30 | 202 | 201
2017-02-05 04:00 | 201 | 200
2017-02-05 04:30 | 201 | 200
2017-02-05 05:00 | 200 | 199
2017-02-05 05:30 | 200 | 199
2017-02-05 06:00 | 187 | 186
2017-02-05 06:30 | 176 | 175
2017-02-05 07:00 | 180 | 179
2017-02-05 07:30 | 210 | 209
2017-02-05 08:00 | 226 | 225
2017-02-05 08:30 | 241 | 240
2017-02-05 09:00 | 256 | 255
2017-02-05 09:30 | 267 | 266
2017-02-05 10:00 | 259 | 258
2017-02-05 10:30 | 259 | 258
2017-02-05 11:00 | 252 | 251
2017-02-05 11:30 | 254 | 253
2017-02-05 12:00 | 256 | 255
2017-02-05 12:30 | 254 | 253
2017-02-05 13:00 | 220 | 219
2017-02-05 13:30 | 200 | 198
2017-02-05 14:00 | 110 | 108
2017-02-05 14:30 | 91 | 89
2017-02-05 15:00 | 98 | 97
2017-02-05 15:30 | 111 | 110
2017-02-05 16:00 | 78 | 76
2017-02-05 16:30 | 68 | 66
2017-02-05 17:00 | 76 | 74
2017-02-05 17:30 | 71 | 69
2017-02-05 18:00 | 61 | 59
2017-02-05 18:30 | 59 | 56
2017-02-05 19:00 | 39 | 35
2017-02-05 19:30 | 37 | 34
2017-02-05 20:00 | 48 | 46
2017-02-05 20:30 | 83 | 81
2017-02-05 21:00 | 142 | 141
2017-02-05 21:30 | 240 | 239
2017-02-05 22:00 | 280 | 279
2017-02-05 22:30 | 230 | 228
2017-02-05 23:00 | 205 | 203
2017-02-05 23:30 | 198 | 196
2017-02-06 | 204 | 203
2017-02-06 00:30 | 209 | 208
2017-02-06 01:00 | 209 | 209
2017-02-06 01:30 | 201 | 200
2017-02-06 02:00 | 196 | 195
2017-02-06 02:30 | 195 | 195
2017-02-06 03:00 | 194 | 193
2017-02-06 03:30 | 193 | 192
2017-02-06 04:00 | 191 | 190
2017-02-06 04:30 | 191 | 190
2017-02-06 05:00 | 194 | 193
2017-02-06 05:30 | 201 | 200
2017-02-06 06:00 | 192 | 191
2017-02-06 06:30 | 191 | 190
2017-02-06 07:00 | 201 | 200
2017-02-06 07:30 | 236 | 235
2017-02-06 08:00 | 237 | 236
2017-02-06 08:30 | 240 | 240
2017-02-06 09:00 | 254 | 254
2017-02-06 09:30 | 244 | 243
2017-02-06 10:00 | 208 | 207
2017-02-06 10:30 | 198 | 196
2017-02-06 11:00 | 198 | 197
2017-02-06 11:30 | 203 | 202
2017-02-06 12:00 | 211 | 210
2017-02-06 12:30 | 213 | 212
2017-02-06 13:00 | 187 | 185
2017-02-06 13:30 | 104 | 103
2017-02-06 14:00 | 28 | 26
2017-02-06 14:30 | 15 | 12
2017-02-06 15:00 | 78 | 68
2017-02-06 15:30 | 86 | 76
2017-02-06 16:00 | 82 | 73
2017-02-06 16:30 | 96 | 87
2017-02-06 17:00 | 95 | 85
2017-02-06 17:30 | 67 | 58
2017-02-06 18:00 | 49 | 39
2017-02-06 18:30 | 26 | 22
2017-02-06 19:00 | 32 | 24
2017-02-06 19:30 | 21 | 18
2017-02-06 20:00 | 67 | 65
2017-02-06 20:30 | 133 | 132
2017-02-06 21:00 | 151 | 149
2017-02-06 21:30 | 174 | 173
2017-02-06 22:00 | 194 | 193
2017-02-06 22:30 | 86 | 84
2017-02-06 23:00 | 72 | 69
2017-02-06 23:30 | 125 | 124
2017-02-07 | 162 | 160
2017-02-07 00:30 | 178 | 177
2017-02-07 01:00 | 238 | 237
2017-02-07 01:30 | 234 | 233
2017-02-07 02:00 | 225 | 225
2017-02-07 02:30 | 218 | 217
2017-02-07 03:00 | 212 | 211
2017-02-07 03:30 | 208 | 207
2017-02-07 04:00 | 203 | 202
2017-02-07 04:30 | 204 | 203
2017-02-07 05:00 | 207 | 206
2017-02-07 05:30 | 214 | 213
2017-02-07 06:00 | 221 | 220
2017-02-07 06:30 | 216 | 214
2017-02-07 07:00 | 230 | 229
2017-02-07 07:30 | 255 | 254
2017-02-07 08:00 | 292 | 291
2017-02-07 08:30 | 297 | 296
2017-02-07 09:00 | 311 | 309
2017-02-07 09:30 | 292 | 290
2017-02-07 10:00 | 256 | 254
2017-02-07 10:30 | 258 | 256
2017-02-07 11:00 | 261 | 259
2017-02-07 11:30 | 240 | 238
2017-02-07 12:00 | 215 | 213
2017-02-07 12:30 | 221 | 219
2017-02-07 13:00 | 199 | 197
2017-02-07 13:30 | 160 | 158
2017-02-07 14:00 | 153 | 151
2017-02-07 14:30 | 49 | 47
2017-02-07 15:00 | 64 | 62
2017-02-07 15:30 | 60 | 58
2017-02-07 16:00 | 57 | 54
2017-02-07 16:30 | 13 | 2
2017-02-07 17:00 | 54 | 45
2017-02-07 17:30 | 62 | 52
2017-02-07 18:00 | 7 | 2
2017-02-07 18:30 | 103 | 102
2017-02-07 19:00 | 135 | 134
2017-02-07 19:30 | 138 | 137
2017-02-07 20:00 | 157 | 156
2017-02-07 20:30 | 208 | 207
2017-02-07 21:00 | 229 | 228
2017-02-07 21:30 | 213 | 211
2017-02-07 22:00 | 186 | 185
2017-02-07 22:30 | 131 | 129
2017-02-07 23:00 | 113 | 111
2017-02-07 23:30 | 152 | 150
2017-02-08 | 152 | 151
2017-02-08 00:30 | 175 | 174
2017-02-08 01:00 | 214 | 213
2017-02-08 01:30 | 211 | 210
2017-02-08 02:00 | 205 | 204
2017-02-08 02:30 | 201 | 201
2017-02-08 03:00 | 199 | 198
2017-02-08 03:30 | 200 | 199
2017-02-08 04:00 | 199 | 198
2017-02-08 04:30 | 201 | 200
2017-02-08 05:00 | 203 | 202
2017-02-08 05:30 | 213 | 212
2017-02-08 06:00 | 207 | 206
2017-02-08 06:30 | 187 | 186
2017-02-08 07:00 | 208 | 206
2017-02-08 07:30 | 270 | 269
2017-02-08 08:00 | 295 | 294
2017-02-08 08:30 | 292 | 290
2017-02-08 09:00 | 297 | 295
2017-02-08 09:30 | 272 | 271
2017-02-08 10:00 | 249 | 247
2017-02-08 10:30 | 263 | 261
2017-02-08 11:00 | 266 | 265
2017-02-08 11:30 | 242 | 240
2017-02-08 12:00 | 240 | 239
2017-02-08 12:30 | 246 | 245
2017-02-08 13:00 | 246 | 245
2017-02-08 13:30 | 238 | 237
2017-02-08 14:00 | 223 | 221
2017-02-08 14:30 | 218 | 216
2017-02-08 15:00 | 169 | 167
2017-02-08 15:30 | 143 | 141
2017-02-08 16:00 | 114 | 111
2017-02-08 16:30 | 115 | 113
2017-02-08 17:00 | 110 | 108
2017-02-08 17:30 | 119 | 117
2017-02-08 18:00 | 138 | 135
2017-02-08 18:30 | 186 | 184
2017-02-08 19:00 | 213 | 211
2017-02-08 19:30 | 230 | 228
2017-02-08 20:00 | 241 | 240
2017-02-08 20:30 | 240 | 238
2017-02-08 21:00 | 263 | 262
2017-02-08 21:30 | 252 | 251
2017-02-08 22:00 | 227 | 226
2017-02-08 22:30 | 157 | 156
2017-02-08 23:00 | 139 | 138
2017-02-08 23:30 | 150 | 149
2017-02-09 | 153 | 151
2017-02-09 00:30 | 186 | 185
2017-02-09 01:00 | 229 | 228
2017-02-09 01:30 | 221 | 220
2017-02-09 02:00 | 216 | 215
2017-02-09 02:30 | 211 | 210
2017-02-09 03:00 | 206 | 205
2017-02-09 03:30 | 206 | 205
2017-02-09 04:00 | 205 | 204
2017-02-09 04:30 | 203 | 202
2017-02-09 05:00 | 204 | 203
2017-02-09 05:30 | 214 | 213
2017-02-09 06:00 | 215 | 214
2017-02-09 06:30 | 193 | 191
2017-02-09 07:00 | 209 | 207
2017-02-09 07:30 | 266 | 264
2017-02-09 08:00 | 299 | 296
2017-02-09 08:30 | 299 | 296
2017-02-09 09:00 | 287 | 285
2017-02-09 09:30 | 248 | 246
2017-02-09 10:00 | 235 | 233
2017-02-09 10:30 | 236 | 233
2017-02-09 11:00 | 239 | 235
2017-02-09 11:30 | 202 | 198
2017-02-09 12:00 | 182 | 177
2017-02-09 12:30 | 188 | 183
2017-02-09 13:00 | 189 | 185
2017-02-09 13:30 | 195 | 190
2017-02-09 14:00 | 192 | 187
2017-02-09 14:30 | 158 | 153
2017-02-09 15:00 | 150 | 145
2017-02-09 15:30 | 143 | 138
2017-02-09 16:00 | 69 | 62
2017-02-09 16:30 | 50 | 42
2017-02-09 17:00 | 65 | 57
2017-02-09 17:30 | 122 | 117
2017-02-09 18:00 | 106 | 98
2017-02-09 18:30 | 84 | 77
2017-02-09 19:00 | 175 | 170
2017-02-09 19:30 | 132 | 126
2017-02-09 20:00 | 165 | 160
2017-02-09 20:30 | 169 | 164
2017-02-09 21:00 | 191 | 187
2017-02-09 21:30 | 252 | 249
2017-02-09 22:00 | 236 | 233
2017-02-09 22:30 | 132 | 128
2017-02-09 23:00 | 106 | 102
2017-02-09 23:30 | 140 | 137
2017-02-10 | 167 | 165
2017-02-10 00:30 | 197 | 195
2017-02-10 01:00 | 238 | 236
2017-02-10 01:30 | 233 | 231
2017-02-10 02:00 | 229 | 226
2017-02-10 02:30 | 226 | 223
2017-02-10 03:00 | 224 | 222
2017-02-10 03:30 | 224 | 221
2017-02-10 04:00 | 222 | 220
2017-02-10 04:30 | 222 | 219
2017-02-10 05:00 | 223 | 220
2017-02-10 05:30 | 230 | 227
2017-02-10 06:00 | 238 | 235
2017-02-10 06:30 | 204 | 200
2017-02-10 07:00 | 222 | 218
2017-02-10 07:30 | 282 | 279
2017-02-10 08:00 | 312 | 309
2017-02-10 08:30 | 277 | 274
2017-02-10 09:00 | 244 | 241
2017-02-10 09:30 | 246 | 243
2017-02-10 10:00 | 247 | 244
2017-02-10 10:30 | 214 | 211
2017-02-10 11:00 | 183 | 180
2017-02-10 11:30 | 182 | 179
2017-02-10 12:00 | 187 | 184
2017-02-10 12:30 | 187 | 184
2017-02-10 13:00 | 187 | 184
2017-02-10 13:30 | 157 | 153
2017-02-10 14:00 | 128 | 124
2017-02-10 14:30 | 34 | 29
2017-02-10 15:00 | 58 | 49
2017-02-10 15:30 | 92 | 81
2017-02-10 16:00 | 84 | 73
2017-02-10 16:30 | 73 | 63
2017-02-10 17:00 | 77 | 65
2017-02-10 17:30 | 26 | 16
2017-02-10 18:00 | 36 | 26
2017-02-10 18:30 | 19 | 11
2017-02-10 19:00 | 16 | 2
2017-02-10 19:30 | 22 | 15
2017-02-10 20:00 | 53 | 48
2017-02-10 20:30 | 92 | 88
2017-02-10 21:00 | 125 | 121
2017-02-10 21:30 | 105 | 101
2017-02-10 22:00 | 113 | 109
2017-02-10 22:30 | 66 | 62
2017-02-10 23:00 | 50 | 46
2017-02-10 23:30 | 91 | 88
2017-02-11 | 116 | 114
2017-02-11 00:30 | 170 | 168
2017-02-11 01:00 | 209 | 208
2017-02-11 01:30 | 209 | 207
2017-02-11 02:00 | 209 | 207
2017-02-11 02:30 | 209 | 207
2017-02-11 03:00 | 206 | 205
2017-02-11 03:30 | 205 | 204
2017-02-11 04:00 | 202 | 201
2017-02-11 04:30 | 202 | 201
2017-02-11 05:00 | 202 | 201
2017-02-11 05:30 | 206 | 204
2017-02-11 06:00 | 209 | 207
2017-02-11 06:30 | 185 | 182
2017-02-11 07:00 | 197 | 194
2017-02-11 07:30 | 227 | 225
2017-02-11 08:00 | 249 | 247
2017-02-11 08:30 | 247 | 246
2017-02-11 09:00 | 236 | 235
2017-02-11 09:30 | 238 | 237
2017-02-11 10:00 | 215 | 213
2017-02-11 10:30 | 174 | 172
2017-02-11 11:00 | 165 | 164
2017-02-11 11:30 | 166 | 165
2017-02-11 12:00 | 130 | 129
2017-02-11 12:30 | 104 | 103
2017-02-11 13:00 | 110 | 109
2017-02-11 13:30 | 117 | 116
2017-02-11 14:00 | 67 | 65
2017-02-11 14:30 | 37 | 34
2017-02-11 15:00 | 45 | 43
2017-02-11 15:30 | 30 | 25
2017-02-11 16:00 | 100 | 90
2017-02-11 16:30 | 94 | 84
2017-02-11 17:00 | 83 | 73
2017-02-11 17:30 | 57 | 46
2017-02-11 18:00 | 73 | 64
2017-02-11 18:30 | 51 | 43
2017-02-11 19:00 | 7 | 4
2017-02-11 19:30 | 28 | 24
2017-02-11 20:00 | 34 | 29
2017-02-11 20:30 | 119 | 117
2017-02-11 21:00 | 143 | 142
2017-02-11 21:30 | 151 | 150
2017-02-11 22:00 | 139 | 137
2017-02-11 22:30 | 114 | 112
2017-02-11 23:00 | 117 | 115
2017-02-11 23:30 | 128 | 126
2017-02-12 | 141 | 138
2017-02-12 00:30 | 165 | 164
2017-02-12 01:00 | 158 | 156
2017-02-12 01:30 | 147 | 145
2017-02-12 02:00 | 142 | 140
2017-02-12 02:30 | 138 | 136
2017-02-12 03:00 | 137 | 136
2017-02-12 03:30 | 135 | 133
2017-02-12 04:00 | 132 | 131
2017-02-12 04:30 | 129 | 128
2017-02-12 05:00 | 127 | 126
2017-02-12 05:30 | 130 | 129
2017-02-12 06:00 | 130 | 129
2017-02-12 06:30 | 132 | 130
2017-02-12 07:00 | 130 | 129
2017-02-12 07:30 | 144 | 143
2017-02-12 08:00 | 168 | 166
2017-02-12 08:30 | 182 | 181
2017-02-12 09:00 | 190 | 189
2017-02-12 09:30 | 178 | 177
2017-02-12 10:00 | 164 | 163
2017-02-12 10:30 | 177 | 175
2017-02-12 11:00 | 148 | 146
2017-02-12 11:30 | 117 | 115
2017-02-12 12:00 | 46 | 44
2017-02-12 12:30 | 9 | 6
2017-02-12 13:00 | 17 | 12
2017-02-12 13:30 | 92 | 83
2017-02-12 14:00 | 100 | 90
2017-02-12 14:30 | 104 | 97
2017-02-12 15:00 | 108 | 100
2017-02-12 15:30 | 102 | 92
2017-02-12 16:00 | 93 | 83
2017-02-12 16:30 | 82 | 74
2017-02-12 17:00 | 75 | 66
2017-02-12 17:30 | 66 | 54
2017-02-12 18:00 | 58 | 47
2017-02-12 18:30 | 78 | 70
2017-02-12 19:00 | 77 | 69
2017-02-12 19:30 | 65 | 54
2017-02-12 20:00 | 53 | 44
2017-02-12 20:30 | 18 | 11
2017-02-12 21:00 | 30 | 28
2017-02-12 21:30 | 109 | 108
2017-02-12 22:00 | 199 | 198
2017-02-12 22:30 | 85 | 83
2017-02-12 23:00 | 89 | 87
2017-02-12 23:30 | 162 | 160
2017-02-13 | 176 | 175
2017-02-13 00:30 | 174 | 172
2017-02-13 01:00 | 167 | 166
2017-02-13 01:30 | 159 | 158
2017-02-13 02:00 | 157 | 155
2017-02-13 02:30 | 153 | 152
2017-02-13 03:00 | 151 | 149
2017-02-13 03:30 | 149 | 148
2017-02-13 04:00 | 151 | 150
2017-02-13 04:30 | 149 | 148
2017-02-13 05:00 | 167 | 166
2017-02-13 05:30 | 179 | 178
2017-02-13 06:00 | 167 | 166
2017-02-13 06:30 | 172 | 171
2017-02-13 07:00 | 159 | 158
2017-02-13 07:30 | 181 | 180
2017-02-13 08:00 | 221 | 220
2017-02-13 08:30 | 197 | 196
2017-02-13 09:00 | 187 | 186
2017-02-13 09:30 | 184 | 182
2017-02-13 10:00 | 138 | 137
2017-02-13 10:30 | 115 | 113
2017-02-13 11:00 | 97 | 95
2017-02-13 11:30 | 80 | 79
2017-02-13 12:00 | 68 | 66
2017-02-13 12:30 | 45 | 41
2017-02-13 13:00 | 26 | 22
2017-02-13 13:30 | 33 | 27
2017-02-13 14:00 | 32 | 28
2017-02-13 14:30 | 43 | 39
2017-02-13 15:00 | 51 | 48
2017-02-13 15:30 | 63 | 60
2017-02-13 16:00 | 74 | 71
2017-02-13 16:30 | 76 | 73
2017-02-13 17:00 | 87 | 83
2017-02-13 17:30 | 107 | 104
2017-02-13 18:00 | 111 | 108
2017-02-13 18:30 | 119 | 116
2017-02-13 19:00 | 236 | 233
2017-02-13 19:30 | 275 | 273
2017-02-13 20:00 | 285 | 283
2017-02-13 20:30 | 283 | 281
2017-02-13 21:00 | 277 | 275
2017-02-13 21:30 | 305 | 303
2017-02-13 22:00 | 317 | 315
2017-02-13 22:30 | 240 | 237
2017-02-13 23:00 | 217 | 214
2017-02-13 23:30 | 220 | 217
2017-02-14 | 218 | 215
2017-02-14 00:30 | 271 | 268
2017-02-14 01:00 | 316 | 314
2017-02-14 01:30 | 309 | 307
2017-02-14 02:00 | 303 | 301
2017-02-14 02:30 | 295 | 294
2017-02-14 03:00 | 291 | 289
2017-02-14 03:30 | 287 | 285
2017-02-14 04:00 | 283 | 281
2017-02-14 04:30 | 280 | 278
2017-02-14 05:00 | 280 | 278
2017-02-14 05:30 | 288 | 286
2017-02-14 06:00 | 283 | 281
2017-02-14 06:30 | 278 | 276
2017-02-14 07:00 | 295 | 293
2017-02-14 07:30 | 332 | 330
2017-02-14 08:00 | 354 | 352
2017-02-14 08:30 | 368 | 365
2017-02-14 09:00 | 369 | 367
2017-02-14 09:30 | 383 | 381
2017-02-14 10:00 | 383 | 381
2017-02-14 10:30 | 387 | 385
2017-02-14 11:00 | 395 | 393
2017-02-14 11:30 | 402 | 400
2017-02-14 12:00 | 414 | 413
2017-02-14 12:30 | 420 | 419
2017-02-14 13:00 | 430 | 429
2017-02-14 13:30 | 424 | 423
2017-02-14 14:00 | 425 | 424
2017-02-14 14:30 | 429 | 429
2017-02-14 15:00 | 440 | 440
2017-02-14 15:30 | 454 | 453
2017-02-14 16:00 | 457 | 456
2017-02-14 16:30 | 425 | 423
2017-02-14 17:00 | 426 | 425
2017-02-14 17:30 | 423 | 422
2017-02-14 18:00 | 433 | 432
2017-02-14 18:30 | 453 | 452
2017-02-14 19:00 | 467 | 467
2017-02-14 19:30 | 490 | 489
2017-02-14 20:00 | 482 | 482
2017-02-14 20:30 | 464 | 463
2017-02-14 21:00 | 443 | 442
2017-02-14 21:30 | 430 | 429
2017-02-14 22:00 | 416 | 415
2017-02-14 22:30 | 397 | 396
2017-02-14 23:00 | 376 | 375
2017-02-14 23:30 | 370 | 369
2017-02-15 | 350 | 349
2017-02-15 00:30 | 337 | 336
2017-02-15 01:00 | 324 | 323
2017-02-15 01:30 | 316 | 315
2017-02-15 02:00 | 310 | 309
2017-02-15 02:30 | 305 | 304
2017-02-15 03:00 | 301 | 300
2017-02-15 03:30 | 299 | 298
2017-02-15 04:00 | 297 | 296
2017-02-15 04:30 | 296 | 295
2017-02-15 05:00 | 271 | 269
2017-02-15 05:30 | 270 | 269
2017-02-15 06:00 | 282 | 281
2017-02-15 06:30 | 283 | 282
2017-02-15 07:00 | 299 | 298
2017-02-15 07:30 | 332 | 331
2017-02-15 08:00 | 359 | 357
2017-02-15 08:30 | 364 | 362
2017-02-15 09:00 | 367 | 366
2017-02-15 09:30 | 373 | 371
2017-02-15 10:00 | 379 | 377
2017-02-15 10:30 | 379 | 377
2017-02-15 11:00 | 381 | 379
2017-02-15 11:30 | 390 | 388
2017-02-15 12:00 | 402 | 399
2017-02-15 12:30 | 408 | 405
2017-02-15 13:00 | 408 | 405
2017-02-15 13:30 | 408 | 406
2017-02-15 14:00 | 403 | 400
2017-02-15 14:30 | 395 | 392
2017-02-15 15:00 | 385 | 381
2017-02-15 15:30 | 385 | 381
2017-02-15 16:00 | 384 | 381
2017-02-15 16:30 | 391 | 388
2017-02-15 17:00 | 395 | 392
2017-02-15 17:30 | 396 | 393
2017-02-15 18:00 | 398 | 396
2017-02-15 18:30 | 405 | 402
2017-02-15 19:00 | 406 | 404
2017-02-15 19:30 | 410 | 408
2017-02-15 20:00 | 406 | 403
2017-02-15 20:30 | 389 | 387
2017-02-15 21:00 | 373 | 371
2017-02-15 21:30 | 359 | 356
2017-02-15 22:00 | 352 | 349
2017-02-15 22:30 | 347 | 344
2017-02-15 23:00 | 334 | 330
2017-02-15 23:30 | 314 | 312
2017-02-16 | 301 | 299
2017-02-16 00:30 | 289 | 287
2017-02-16 01:00 | 282 | 280
2017-02-16 01:30 | 276 | 274
2017-02-16 02:00 | 271 | 269
2017-02-16 02:30 | 268 | 266
2017-02-16 03:00 | 265 | 263
2017-02-16 03:30 | 264 | 262
2017-02-16 04:00 | 262 | 260
2017-02-16 04:30 | 269 | 267
2017-02-16 05:00 | 274 | 272
2017-02-16 05:30 | 281 | 279
2017-02-16 06:00 | 293 | 291
2017-02-16 06:30 | 311 | 310
2017-02-16 07:00 | 323 | 322
2017-02-16 07:30 | 318 | 316
2017-02-16 08:00 | 304 | 302
2017-02-16 08:30 | 308 | 306
2017-02-16 09:00 | 313 | 311
2017-02-16 09:30 | 319 | 317
2017-02-16 10:00 | 316 | 314
2017-02-16 10:30 | 316 | 314
2017-02-16 11:00 | 316 | 314
2017-02-16 11:30 | 279 | 276
2017-02-16 12:00 | 263 | 260
2017-02-16 12:30 | 270 | 268
2017-02-16 13:00 | 272 | 269
2017-02-16 13:30 | 218 | 215
2017-02-16 14:00 | 136 | 132
2017-02-16 14:30 | 58 | 54
2017-02-16 15:00 | 47 | 42
2017-02-16 15:30 | 49 | 46
2017-02-16 16:00 | 54 | 51
2017-02-16 16:30 | 51 | 48
2017-02-16 17:00 | 51 | 48
2017-02-16 17:30 | 61 | 58
2017-02-16 18:00 | 69 | 67
2017-02-16 18:30 | 73 | 71
2017-02-16 19:00 | 76 | 74
2017-02-16 19:30 | 74 | 72
2017-02-16 20:00 | 66 | 63
2017-02-16 20:30 | 93 | 92
2017-02-16 21:00 | 94 | 92
2017-02-16 21:30 | 71 | 69
2017-02-16 22:00 | 74 | 71
2017-02-16 22:30 | 57 | 55
2017-02-16 23:00 | 68 | 66
2017-02-16 23:30 | 106 | 104
2017-02-17 | 134 | 132
2017-02-17 00:30 | 206 | 205
2017-02-17 01:00 | 254 | 252
2017-02-17 01:30 | 250 | 248
2017-02-17 02:00 | 245 | 244
2017-02-17 02:30 | 242 | 241
2017-02-17 03:00 | 240 | 238
2017-02-17 03:30 | 240 | 238
2017-02-17 04:00 | 237 | 236
2017-02-17 04:30 | 239 | 238
2017-02-17 05:00 | 242 | 241
2017-02-17 05:30 | 251 | 249
2017-02-17 06:00 | 256 | 255
2017-02-17 06:30 | 262 | 261
2017-02-17 07:00 | 280 | 279
2017-02-17 07:30 | 292 | 291
2017-02-17 08:00 | 307 | 306
2017-02-17 08:30 | 297 | 295
2017-02-17 09:00 | 280 | 278
2017-02-17 09:30 | 282 | 280
2017-02-17 10:00 | 286 | 284
2017-02-17 10:30 | 255 | 253
2017-02-17 11:00 | 223 | 220
2017-02-17 11:30 | 234 | 231
2017-02-17 12:00 | 239 | 236
2017-02-17 12:30 | 242 | 240
2017-02-17 13:00 | 245 | 242
2017-02-17 13:30 | 254 | 252
2017-02-17 14:00 | 257 | 254
2017-02-17 14:30 | 233 | 230
2017-02-17 15:00 | 214 | 211
2017-02-17 15:30 | 191 | 188
2017-02-17 16:00 | 107 | 104
2017-02-17 16:30 | 104 | 102
2017-02-17 17:00 | 101 | 99
2017-02-17 17:30 | 106 | 104
2017-02-17 18:00 | 101 | 99
2017-02-17 18:30 | 103 | 101
2017-02-17 19:00 | 105 | 102
2017-02-17 19:30 | 108 | 105
2017-02-17 20:00 | 102 | 100
2017-02-17 20:30 | 91 | 88
2017-02-17 21:00 | 134 | 132
2017-02-17 21:30 | 144 | 142
2017-02-17 22:00 | 157 | 154
2017-02-17 22:30 | 163 | 161
2017-02-17 23:00 | 154 | 152
2017-02-17 23:30 | 193 | 191
2017-02-18 | 195 | 193
2017-02-18 00:30 | 185 | 183
2017-02-18 01:00 | 177 | 175
2017-02-18 01:30 | 172 | 170
2017-02-18 02:00 | 166 | 164
2017-02-18 02:30 | 163 | 161
2017-02-18 03:00 | 159 | 156
2017-02-18 03:30 | 157 | 155
2017-02-18 04:00 | 157 | 155
2017-02-18 04:30 | 157 | 154
2017-02-18 05:00 | 158 | 155
2017-02-18 05:30 | 159 | 157
2017-02-18 06:00 | 162 | 160
2017-02-18 06:30 | 166 | 163
2017-02-18 07:00 | 166 | 164
2017-02-18 07:30 | 167 | 164
2017-02-18 08:00 | 175 | 173
2017-02-18 08:30 | 191 | 189
2017-02-18 09:00 | 199 | 196
2017-02-18 09:30 | 207 | 205
2017-02-18 10:00 | 209 | 207
2017-02-18 10:30 | 208 | 207
2017-02-18 11:00 | 209 | 208
2017-02-18 11:30 | 208 | 207
2017-02-18 12:00 | 212 | 210
2017-02-18 12:30 | 179 | 177
2017-02-18 13:00 | 129 | 128
2017-02-18 13:30 | 46 | 43
2017-02-18 14:00 | 78 | 76
2017-02-18 14:30 | 86 | 84
2017-02-18 15:00 | 48 | 45
2017-02-18 15:30 | 105 | 103
2017-02-18 16:00 | 101 | 99
2017-02-18 16:30 | 78 | 76
2017-02-18 17:00 | 64 | 62
2017-02-18 17:30 | 123 | 121
2017-02-18 18:00 | 129 | 127
2017-02-18 18:30 | 156 | 155
2017-02-18 19:00 | 102 | 101
2017-02-18 19:30 | 85 | 83
2017-02-18 20:00 | 97 | 95
2017-02-18 20:30 | 167 | 165
2017-02-18 21:00 | 204 | 202
2017-02-18 21:30 | 230 | 229
2017-02-18 22:00 | 237 | 235
2017-02-18 22:30 | 195 | 193
2017-02-18 23:00 | 179 | 177
2017-02-18 23:30 | 203 | 201
2017-02-19 | 239 | 238
2017-02-19 00:30 | 281 | 280
2017-02-19 01:00 | 274 | 273
2017-02-19 01:30 | 267 | 265
2017-02-19 02:00 | 259 | 258
2017-02-19 02:30 | 255 | 254
2017-02-19 03:00 | 253 | 251
2017-02-19 03:30 | 250 | 248
2017-02-19 04:00 | 247 | 246
2017-02-19 04:30 | 246 | 245
2017-02-19 05:00 | 246 | 244
2017-02-19 05:30 | 247 | 246
2017-02-19 06:00 | 249 | 248
2017-02-19 06:30 | 248 | 247
2017-02-19 07:00 | 245 | 244
2017-02-19 07:30 | 242 | 240
2017-02-19 08:00 | 247 | 245
2017-02-19 08:30 | 262 | 260
2017-02-19 09:00 | 268 | 266
2017-02-19 09:30 | 277 | 276
2017-02-19 10:00 | 283 | 281
2017-02-19 10:30 | 284 | 283
2017-02-19 11:00 | 286 | 285
2017-02-19 11:30 | 294 | 293
2017-02-19 12:00 | 304 | 302
2017-02-19 12:30 | 312 | 310
2017-02-19 13:00 | 323 | 321
2017-02-19 13:30 | 332 | 330
2017-02-19 14:00 | 337 | 335
2017-02-19 14:30 | 321 | 319
2017-02-19 15:00 | 320 | 318
2017-02-19 15:30 | 333 | 332
2017-02-19 16:00 | 289 | 287
2017-02-19 16:30 | 276 | 274
2017-02-19 17:00 | 259 | 257
2017-02-19 17:30 | 247 | 245
2017-02-19 18:00 | 244 | 242
2017-02-19 18:30 | 277 | 275
2017-02-19 19:00 | 294 | 292
2017-02-19 19:30 | 295 | 293
2017-02-19 20:00 | 308 | 307
2017-02-19 20:30 | 306 | 304
2017-02-19 21:00 | 293 | 291
2017-02-19 21:30 | 290 | 289
2017-02-19 22:00 | 338 | 336
2017-02-19 22:30 | 328 | 326
2017-02-19 23:00 | 312 | 311
2017-02-19 23:30 | 300 | 298
2017-02-20 | 286 | 284
2017-02-20 00:30 | 273 | 272
2017-02-20 01:00 | 268 | 267
2017-02-20 01:30 | 263 | 262
2017-02-20 02:00 | 259 | 258
2017-02-20 02:30 | 256 | 255
2017-02-20 03:00 | 255 | 253
2017-02-20 03:30 | 252 | 251
2017-02-20 04:00 | 249 | 248
2017-02-20 04:30 | 251 | 250
2017-02-20 05:00 | 255 | 254
2017-02-20 05:30 | 261 | 259
2017-02-20 06:00 | 272 | 271
2017-02-20 06:30 | 292 | 291
2017-02-20 07:00 | 309 | 308
2017-02-20 07:30 | 313 | 312
2017-02-20 08:00 | 325 | 323
2017-02-20 08:30 | 333 | 332
2017-02-20 09:00 | 338 | 336
2017-02-20 09:30 | 340 | 338
2017-02-20 10:00 | 342 | 340
2017-02-20 10:30 | 340 | 338
2017-02-20 11:00 | 348 | 346
2017-02-20 11:30 | 357 | 355
2017-02-20 12:00 | 367 | 365
2017-02-20 12:30 | 369 | 366
2017-02-20 13:00 | 368 | 366
2017-02-20 13:30 | 340 | 338
2017-02-20 14:00 | 325 | 323
2017-02-20 14:30 | 323 | 321
2017-02-20 15:00 | 221 | 217
2017-02-20 15:30 | 198 | 195
2017-02-20 16:00 | 207 | 204
2017-02-20 16:30 | 184 | 182
2017-02-20 17:00 | 173 | 171
2017-02-20 17:30 | 176 | 173
2017-02-20 18:00 | 176 | 174
2017-02-20 18:30 | 175 | 173
2017-02-20 19:00 | 182 | 180
2017-02-20 19:30 | 190 | 188
2017-02-20 20:00 | 183 | 181
2017-02-20 20:30 | 167 | 164
2017-02-20 21:00 | 297 | 295
2017-02-20 21:30 | 339 | 337
2017-02-20 22:00 | 322 | 321
2017-02-20 22:30 | 353 | 352
2017-02-20 23:00 | 342 | 340
2017-02-20 23:30 | 320 | 318
2017-02-21 | 306 | 304
2017-02-21 00:30 | 296 | 295
2017-02-21 01:00 | 287 | 285
2017-02-21 01:30 | 278 | 277
2017-02-21 02:00 | 274 | 272
2017-02-21 02:30 | 272 | 271
2017-02-21 03:00 | 268 | 267
2017-02-21 03:30 | 266 | 264
2017-02-21 04:00 | 265 | 264
2017-02-21 04:30 | 265 | 263
2017-02-21 05:00 | 268 | 267
2017-02-21 05:30 | 274 | 273
2017-02-21 06:00 | 285 | 284
2017-02-21 06:30 | 256 | 255
2017-02-21 07:00 | 251 | 249
2017-02-21 07:30 | 283 | 282
2017-02-21 08:00 | 326 | 325
2017-02-21 08:30 | 298 | 295
2017-02-21 09:00 | 283 | 281
2017-02-21 09:30 | 279 | 276
2017-02-21 10:00 | 269 | 266
2017-02-21 10:30 | 268 | 264
2017-02-21 11:00 | 281 | 277
2017-02-21 11:30 | 280 | 277
2017-02-21 12:00 | 279 | 276
2017-02-21 12:30 | 284 | 282
2017-02-21 13:00 | 284 | 282
2017-02-21 13:30 | 294 | 292
2017-02-21 14:00 | 301 | 299
2017-02-21 14:30 | 302 | 299
2017-02-21 15:00 | 302 | 300
2017-02-21 15:30 | 308 | 306
2017-02-21 16:00 | 314 | 312
2017-02-21 16:30 | 301 | 299
2017-02-21 17:00 | 244 | 241
2017-02-21 17:30 | 243 | 241
2017-02-21 18:00 | 240 | 238
2017-02-21 18:30 | 245 | 243
2017-02-21 19:00 | 255 | 253
2017-02-21 19:30 | 274 | 272
2017-02-21 20:00 | 339 | 338
2017-02-21 20:30 | 357 | 355
2017-02-21 21:00 | 365 | 363
2017-02-21 21:30 | 360 | 358
2017-02-21 22:00 | 362 | 360
2017-02-21 22:30 | 351 | 349
2017-02-21 23:00 | 332 | 330
2017-02-21 23:30 | 314 | 312
2017-02-22 | 301 | 299
2017-02-22 00:30 | 290 | 288
2017-02-22 01:00 | 273 | 271
2017-02-22 01:30 | 269 | 267
2017-02-22 02:00 | 262 | 261
2017-02-22 02:30 | 259 | 258
2017-02-22 03:00 | 258 | 256
2017-02-22 03:30 | 256 | 254
2017-02-22 04:00 | 252 | 250
2017-02-22 04:30 | 252 | 251
2017-02-22 05:00 | 255 | 253
2017-02-22 05:30 | 263 | 262
2017-02-22 06:00 | 277 | 276
2017-02-22 06:30 | 295 | 294
2017-02-22 07:00 | 310 | 309
2017-02-22 07:30 | 337 | 336
2017-02-22 08:00 | 347 | 346
2017-02-22 08:30 | 323 | 322
2017-02-22 09:00 | 301 | 299
2017-02-22 09:30 | 295 | 294
2017-02-22 10:00 | 295 | 294
2017-02-22 10:30 | 300 | 299
2017-02-22 11:00 | 303 | 301
2017-02-22 11:30 | 309 | 307
2017-02-22 12:00 | 311 | 309
2017-02-22 12:30 | 277 | 274
2017-02-22 13:00 | 281 | 279
2017-02-22 13:30 | 283 | 280
2017-02-22 14:00 | 285 | 283
2017-02-22 14:30 | 281 | 279
2017-02-22 15:00 | 241 | 238
2017-02-22 15:30 | 235 | 233
2017-02-22 16:00 | 175 | 172
2017-02-22 16:30 | 197 | 194
2017-02-22 17:00 | 201 | 199
2017-02-22 17:30 | 204 | 202
2017-02-22 18:00 | 248 | 246
2017-02-22 18:30 | 256 | 254
2017-02-22 19:00 | 254 | 253
2017-02-22 19:30 | 242 | 241
2017-02-22 20:00 | 268 | 267
2017-02-22 20:30 | 327 | 326
2017-02-22 21:00 | 318 | 316
2017-02-22 21:30 | 301 | 299
2017-02-22 22:00 | 279 | 278
2017-02-22 22:30 | 266 | 265
2017-02-22 23:00 | 244 | 243
2017-02-22 23:30 | 226 | 225
2017-02-23 | 215 | 214
2017-02-23 00:30 | 206 | 205
2017-02-23 01:00 | 199 | 198
2017-02-23 01:30 | 193 | 191
2017-02-23 02:00 | 186 | 185
2017-02-23 02:30 | 182 | 180
2017-02-23 03:00 | 179 | 178
2017-02-23 03:30 | 178 | 176
2017-02-23 04:00 | 175 | 174
2017-02-23 04:30 | 174 | 172
2017-02-23 05:00 | 173 | 171
2017-02-23 05:30 | 157 | 155
2017-02-23 06:00 | 168 | 166
2017-02-23 06:30 | 190 | 189
2017-02-23 07:00 | 126 | 125
2017-02-23 07:30 | 171 | 169
2017-02-23 08:00 | 211 | 210
2017-02-23 08:30 | 223 | 222
2017-02-23 09:00 | 221 | 220
2017-02-23 09:30 | 226 | 225
2017-02-23 10:00 | 220 | 219
2017-02-23 10:30 | 161 | 159
2017-02-23 11:00 | 163 | 161
2017-02-23 11:30 | 203 | 201
2017-02-23 12:00 | 191 | 189
2017-02-23 12:30 | 199 | 198
2017-02-23 13:00 | 125 | 123
2017-02-23 13:30 | 89 | 87
2017-02-23 14:00 | 102 | 101
2017-02-23 14:30 | 96 | 94
2017-02-23 15:00 | 58 | 56
2017-02-23 15:30 | 59 | 56
2017-02-23 16:00 | 51 | 48
2017-02-23 16:30 | 24 | 21
2017-02-23 17:00 | 27 | 19
2017-02-23 17:30 | 6 | 2
2017-02-23 18:00 | 80 | 78
2017-02-23 18:30 | 133 | 132
2017-02-23 19:00 | 79 | 77
2017-02-23 19:30 | 66 | 64
2017-02-23 20:00 | 132 | 131
2017-02-23 20:30 | 257 | 256
2017-02-23 21:00 | 301 | 300
2017-02-23 21:30 | 266 | 265
2017-02-23 22:00 | 250 | 249
2017-02-23 22:30 | 251 | 250
2017-02-23 23:00 | 247 | 245
2017-02-23 23:30 | 234 | 233
2017-02-24 | 223 | 221
2017-02-24 00:30 | 214 | 213
2017-02-24 01:00 | 205 | 203
2017-02-24 01:30 | 198 | 196
2017-02-24 02:00 | 191 | 190
2017-02-24 02:30 | 189 | 188
2017-02-24 03:00 | 186 | 184
2017-02-24 03:30 | 185 | 184
2017-02-24 04:00 | 184 | 183
2017-02-24 04:30 | 184 | 182
2017-02-24 05:00 | 183 | 181
2017-02-24 05:30 | 192 | 190
2017-02-24 06:00 | 200 | 199
2017-02-24 06:30 | 179 | 177
2017-02-24 07:00 | 175 | 173
2017-02-24 07:30 | 186 | 185
2017-02-24 08:00 | 245 | 244
2017-02-24 08:30 | 243 | 241
2017-02-24 09:00 | 251 | 250
2017-02-24 09:30 | 253 | 251
2017-02-24 10:00 | 251 | 250
2017-02-24 10:30 | 203 | 201
2017-02-24 11:00 | 202 | 200
2017-02-24 11:30 | 226 | 224
2017-02-24 12:00 | 184 | 181
2017-02-24 12:30 | 159 | 156
2017-02-24 13:00 | 152 | 150
2017-02-24 13:30 | 150 | 147
2017-02-24 14:00 | 114 | 111
2017-02-24 14:30 | 111 | 109
2017-02-24 15:00 | 98 | 96
2017-02-24 15:30 | 73 | 71
2017-02-24 16:00 | 78 | 76
2017-02-24 16:30 | 15 | 10
2017-02-24 17:00 | 10 | 5
2017-02-24 17:30 | 9 | 4
2017-02-24 18:00 | 11 | 6
2017-02-24 18:30 | 52 | 49
2017-02-24 19:00 | 16 | 10
2017-02-24 19:30 | 24 | 16
2017-02-24 20:00 | 33 | 28
2017-02-24 20:30 | 80 | 78
2017-02-24 21:00 | 194 | 193
2017-02-24 21:30 | 206 | 205
2017-02-24 22:00 | 228 | 226
2017-02-24 22:30 | 251 | 249
2017-02-24 23:00 | 245 | 243
2017-02-24 23:30 | 267 | 265
2017-02-25 | 308 | 307
2017-02-25 00:30 | 303 | 302
2017-02-25 01:00 | 293 | 291
2017-02-25 01:30 | 284 | 283
2017-02-25 02:00 | 279 | 278
2017-02-25 02:30 | 274 | 272
2017-02-25 03:00 | 271 | 269
2017-02-25 03:30 | 268 | 267
2017-02-25 04:00 | 267 | 266
2017-02-25 04:30 | 262 | 261
2017-02-25 05:00 | 255 | 254
2017-02-25 05:30 | 263 | 262
2017-02-25 06:00 | 268 | 267
2017-02-25 06:30 | 275 | 274
2017-02-25 07:00 | 282 | 281
2017-02-25 07:30 | 296 | 295
2017-02-25 08:00 | 304 | 303
2017-02-25 08:30 | 298 | 297
2017-02-25 09:00 | 308 | 307
2017-02-25 09:30 | 316 | 315
2017-02-25 10:00 | 316 | 315
2017-02-25 10:30 | 314 | 312
2017-02-25 11:00 | 311 | 310
2017-02-25 11:30 | 317 | 316
2017-02-25 12:00 | 325 | 324
2017-02-25 12:30 | 327 | 326
2017-02-25 13:00 | 325 | 324
2017-02-25 13:30 | 312 | 310
2017-02-25 14:00 | 318 | 317
2017-02-25 14:30 | 317 | 316
2017-02-25 15:00 | 316 | 315
2017-02-25 15:30 | 320 | 319
2017-02-25 16:00 | 324 | 323
2017-02-25 16:30 | 322 | 321
2017-02-25 17:00 | 333 | 332
2017-02-25 17:30 | 331 | 330
2017-02-25 18:00 | 292 | 291
2017-02-25 18:30 | 267 | 265
2017-02-25 19:00 | 266 | 264
2017-02-25 19:30 | 269 | 268
2017-02-25 20:00 | 261 | 260
2017-02-25 20:30 | 251 | 250
2017-02-25 21:00 | 241 | 239
2017-02-25 21:30 | 229 | 227
2017-02-25 22:00 | 231 | 230
2017-02-25 22:30 | 237 | 235
2017-02-25 23:00 | 282 | 281
2017-02-25 23:30 | 285 | 284
2017-02-26 | 275 | 273
2017-02-26 00:30 | 267 | 266
2017-02-26 01:00 | 257 | 255
2017-02-26 01:30 | 251 | 250
2017-02-26 02:00 | 246 | 245
2017-02-26 02:30 | 243 | 242
2017-02-26 03:00 | 241 | 239
2017-02-26 03:30 | 241 | 239
2017-02-26 04:00 | 238 | 237
2017-02-26 04:30 | 239 | 238
2017-02-26 05:00 | 239 | 238
2017-02-26 05:30 | 240 | 238
2017-02-26 06:00 | 240 | 238
2017-02-26 06:30 | 241 | 240
2017-02-26 07:00 | 245 | 243
2017-02-26 07:30 | 255 | 253
2017-02-26 08:00 | 264 | 263
2017-02-26 08:30 | 271 | 270
2017-02-26 09:00 | 276 | 275
2017-02-26 09:30 | 283 | 282
2017-02-26 10:00 | 276 | 276
2017-02-26 10:30 | 272 | 271
2017-02-26 11:00 | 272 | 272
2017-02-26 11:30 | 277 | 276
2017-02-26 12:00 | 283 | 282
2017-02-26 12:30 | 287 | 287
2017-02-26 13:00 | 292 | 291
2017-02-26 13:30 | 297 | 296
2017-02-26 14:00 | 287 | 286
2017-02-26 14:30 | 286 | 285
2017-02-26 15:00 | 292 | 291
2017-02-26 15:30 | 301 | 300
2017-02-26 16:00 | 310 | 309
2017-02-26 16:30 | 317 | 316
2017-02-26 17:00 | 329 | 328
2017-02-26 17:30 | 336 | 335
2017-02-26 18:00 | 346 | 345
2017-02-26 18:30 | 352 | 351
2017-02-26 19:00 | 357 | 356
2017-02-26 19:30 | 370 | 369
2017-02-26 20:00 | 364 | 363
2017-02-26 20:30 | 350 | 349
2017-02-26 21:00 | 339 | 338
2017-02-26 21:30 | 324 | 322
2017-02-26 22:00 | 307 | 305
2017-02-26 22:30 | 304 | 303
2017-02-26 23:00 | 308 | 306
2017-02-26 23:30 | 299 | 298
2017-02-27 | 286 | 285
2017-02-27 00:30 | 278 | 276
2017-02-27 01:00 | 267 | 265
2017-02-27 01:30 | 263 | 261
2017-02-27 02:00 | 258 | 256
2017-02-27 02:30 | 254 | 252
2017-02-27 03:00 | 250 | 249
2017-02-27 03:30 | 248 | 247
2017-02-27 04:00 | 248 | 246
2017-02-27 04:30 | 248 | 246
2017-02-27 05:00 | 248 | 247
2017-02-27 05:30 | 256 | 255
2017-02-27 06:00 | 267 | 266
2017-02-27 06:30 | 287 | 287
2017-02-27 07:00 | 305 | 304
2017-02-27 07:30 | 313 | 312
2017-02-27 08:00 | 324 | 323
2017-02-27 08:30 | 330 | 329
2017-02-27 09:00 | 333 | 332
2017-02-27 09:30 | 335 | 334
2017-02-27 10:00 | 334 | 333
2017-02-27 10:30 | 334 | 333
2017-02-27 11:00 | 332 | 331
2017-02-27 11:30 | 321 | 320
2017-02-27 12:00 | 323 | 322
2017-02-27 12:30 | 334 | 333
2017-02-27 13:00 | 337 | 335
2017-02-27 13:30 | 340 | 339
2017-02-27 14:00 | 333 | 332
2017-02-27 14:30 | 340 | 338
2017-02-27 15:00 | 343 | 342
2017-02-27 15:30 | 348 | 347
2017-02-27 16:00 | 360 | 359
2017-02-27 16:30 | 364 | 363
2017-02-27 17:00 | 373 | 372
2017-02-27 17:30 | 375 | 374
2017-02-27 18:00 | 376 | 375
2017-02-27 18:30 | 376 | 375
2017-02-27 19:00 | 386 | 385
2017-02-27 19:30 | 391 | 390
2017-02-27 20:00 | 380 | 378
2017-02-27 20:30 | 363 | 362
2017-02-27 21:00 | 359 | 358
2017-02-27 21:30 | 360 | 358
2017-02-27 22:00 | 347 | 345
2017-02-27 22:30 | 323 | 322
2017-02-27 23:00 | 307 | 306
2017-02-27 23:30 | 294 | 292
2017-02-28 | 280 | 278
2017-02-28 00:30 | 271 | 269
2017-02-28 01:00 | 261 | 259
2017-02-28 01:30 | 255 | 254
2017-02-28 02:00 | 250 | 248
2017-02-28 02:30 | 247 | 246
2017-02-28 03:00 | 246 | 244
2017-02-28 03:30 | 242 | 240
2017-02-28 04:00 | 240 | 238
2017-02-28 04:30 | 239 | 238
2017-02-28 05:00 | 239 | 238
2017-02-28 05:30 | 247 | 245
2017-02-28 06:00 | 259 | 258
2017-02-28 06:30 | 277 | 277
2017-02-28 07:00 | 301 | 301
2017-02-28 07:30 | 324 | 323
2017-02-28 08:00 | 337 | 336
2017-02-28 08:30 | 340 | 339
2017-02-28 09:00 | 345 | 344
2017-02-28 09:30 | 347 | 346
2017-02-28 10:00 | 332 | 331
2017-02-28 10:30 | 331 | 329
2017-02-28 11:00 | 332 | 331
2017-02-28 11:30 | 333 | 332
2017-02-28 12:00 | 342 | 341
2017-02-28 12:30 | 350 | 349
2017-02-28 13:00 | 350 | 349
2017-02-28 13:30 | 347 | 346
2017-02-28 14:00 | 346 | 345
2017-02-28 14:30 | 340 | 339
2017-02-28 15:00 | 340 | 339
2017-02-28 15:30 | 342 | 341
2017-02-28 16:00 | 354 | 353
2017-02-28 16:30 | 359 | 358
2017-02-28 17:00 | 364 | 363
2017-02-28 17:30 | 368 | 367
2017-02-28 18:00 | 369 | 368
2017-02-28 18:30 | 373 | 372
2017-02-28 19:00 | 374 | 373
2017-02-28 19:30 | 403 | 402
2017-02-28 20:00 | 414 | 413
2017-02-28 20:30 | 403 | 403
2017-02-28 21:00 | 386 | 385
2017-02-28 21:30 | 373 | 373
2017-02-28 22:00 | 355 | 354
2017-02-28 22:30 | 330 | 329
2017-02-28 23:00 | 313 | 312
2017-02-28 23:30 | 296 | 295
2017-03-01 | 284 | 283
2017-03-01 00:30 | 275 | 273
2017-03-01 01:00 | 265 | 264
2017-03-01 01:30 | 259 | 258
2017-03-01 02:00 | 252 | 251
2017-03-01 02:30 | 249 | 248
2017-03-01 03:00 | 248 | 248
2017-03-01 03:30 | 246 | 245
2017-03-01 04:00 | 245 | 244
2017-03-01 04:30 | 245 | 244
2017-03-01 05:00 | 246 | 245
2017-03-01 05:30 | 253 | 252
2017-03-01 06:00 | 263 | 262
2017-03-01 06:30 | 282 | 281
2017-03-01 07:00 | 305 | 304
2017-03-01 07:30 | 327 | 326
2017-03-01 08:00 | 341 | 340
2017-03-01 08:30 | 349 | 348
2017-03-01 09:00 | 349 | 348
2017-03-01 09:30 | 332 | 331
2017-03-01 10:00 | 293 | 292
2017-03-01 10:30 | 295 | 293
2017-03-01 11:00 | 301 | 300
2017-03-01 11:30 | 295 | 294
2017-03-01 12:00 | 306 | 304
2017-03-01 12:30 | 307 | 306
2017-03-01 13:00 | 309 | 307
2017-03-01 13:30 | 256 | 254
2017-03-01 14:00 | 206 | 204
2017-03-01 14:30 | 200 | 199
2017-03-01 15:00 | 204 | 202
2017-03-01 15:30 | 207 | 205
2017-03-01 16:00 | 217 | 215
2017-03-01 16:30 | 219 | 217
2017-03-01 17:00 | 225 | 223
2017-03-01 17:30 | 235 | 233
2017-03-01 18:00 | 237 | 235
2017-03-01 18:30 | 250 | 248
2017-03-01 19:00 | 250 | 248
2017-03-01 19:30 | 287 | 286
2017-03-01 20:00 | 289 | 288
2017-03-01 20:30 | 322 | 321
2017-03-01 21:00 | 313 | 312
2017-03-01 21:30 | 296 | 295
2017-03-01 22:00 | 275 | 273
2017-03-01 22:30 | 252 | 251
2017-03-01 23:00 | 234 | 232
2017-03-01 23:30 | 217 | 216
2017-03-02 | 205 | 203
2017-03-02 00:30 | 196 | 195
2017-03-02 01:00 | 187 | 186
2017-03-02 01:30 | 179 | 177
2017-03-02 02:00 | 175 | 174
2017-03-02 02:30 | 170 | 168
2017-03-02 03:00 | 166 | 164
2017-03-02 03:30 | 162 | 161
2017-03-02 04:00 | 161 | 160
2017-03-02 04:30 | 163 | 162
2017-03-02 05:00 | 165 | 164
2017-03-02 05:30 | 171 | 170
2017-03-02 06:00 | 179 | 178
2017-03-02 06:30 | 198 | 197
2017-03-02 07:00 | 220 | 219
2017-03-02 07:30 | 243 | 242
2017-03-02 08:00 | 256 | 255
2017-03-02 08:30 | 264 | 263
2017-03-02 09:00 | 266 | 266
2017-03-02 09:30 | 267 | 267
2017-03-02 10:00 | 254 | 253
2017-03-02 10:30 | 244 | 243
2017-03-02 11:00 | 243 | 242
2017-03-02 11:30 | 244 | 243
2017-03-02 12:00 | 247 | 246
2017-03-02 12:30 | 252 | 251
2017-03-02 13:00 | 260 | 259
2017-03-02 13:30 | 210 | 209
2017-03-02 14:00 | 200 | 199
2017-03-02 14:30 | 204 | 203
2017-03-02 15:00 | 204 | 203
2017-03-02 15:30 | 208 | 207
2017-03-02 16:00 | 215 | 215
2017-03-02 16:30 | 220 | 219
2017-03-02 17:00 | 214 | 213
2017-03-02 17:30 | 214 | 214
2017-03-02 18:00 | 218 | 217
2017-03-02 18:30 | 230 | 229
2017-03-02 19:00 | 243 | 242
2017-03-02 19:30 | 265 | 264
2017-03-02 20:00 | 285 | 285
2017-03-02 20:30 | 326 | 326
2017-03-02 21:00 | 311 | 310
2017-03-02 21:30 | 292 | 291
2017-03-02 22:00 | 269 | 268
2017-03-02 22:30 | 251 | 249
2017-03-02 23:00 | 232 | 231
2017-03-02 23:30 | 215 | 214
2017-03-03 | 203 | 201
2017-03-03 00:30 | 196 | 195
2017-03-03 01:00 | 188 | 187
2017-03-03 01:30 | 180 | 179
2017-03-03 02:00 | 175 | 174
2017-03-03 02:30 | 169 | 168
2017-03-03 03:00 | 167 | 165
2017-03-03 03:30 | 163 | 161
2017-03-03 04:00 | 163 | 161
2017-03-03 04:30 | 166 | 165
2017-03-03 05:00 | 167 | 165
2017-03-03 05:30 | 175 | 173
2017-03-03 06:00 | 185 | 183
2017-03-03 06:30 | 180 | 179
2017-03-03 07:00 | 163 | 162
2017-03-03 07:30 | 193 | 192
2017-03-03 08:00 | 235 | 234
2017-03-03 08:30 | 215 | 214
2017-03-03 09:00 | 216 | 215
2017-03-03 09:30 | 220 | 219
2017-03-03 10:00 | 221 | 220
2017-03-03 10:30 | 226 | 225
2017-03-03 11:00 | 223 | 222
2017-03-03 11:30 | 225 | 224
2017-03-03 12:00 | 237 | 236
2017-03-03 12:30 | 215 | 214
2017-03-03 13:00 | 194 | 193
2017-03-03 13:30 | 190 | 189
2017-03-03 14:00 | 196 | 195
2017-03-03 14:30 | 184 | 182
2017-03-03 15:00 | 178 | 176
2017-03-03 15:30 | 171 | 170
2017-03-03 16:00 | 175 | 174
2017-03-03 16:30 | 185 | 183
2017-03-03 17:00 | 186 | 185
2017-03-03 17:30 | 181 | 179
2017-03-03 18:00 | 175 | 173
2017-03-03 18:30 | 206 | 205
2017-03-03 19:00 | 178 | 176
2017-03-03 19:30 | 205 | 204
2017-03-03 20:00 | 238 | 238
2017-03-03 20:30 | 250 | 249
2017-03-03 21:00 | 249 | 249
2017-03-03 21:30 | 242 | 241
2017-03-03 22:00 | 230 | 229
2017-03-03 22:30 | 215 | 215
2017-03-03 23:00 | 204 | 203
2017-03-03 23:30 | 193 | 193
2017-03-04 | 183 | 182
2017-03-04 00:30 | 178 | 177
2017-03-04 01:00 | 169 | 168
2017-03-04 01:30 | 162 | 161
2017-03-04 02:00 | 156 | 155
2017-03-04 02:30 | 155 | 154
2017-03-04 03:00 | 156 | 155
2017-03-04 03:30 | 155 | 154
2017-03-04 04:00 | 153 | 152
2017-03-04 04:30 | 153 | 152
2017-03-04 05:00 | 153 | 152
2017-03-04 05:30 | 156 | 155
2017-03-04 06:00 | 161 | 160
2017-03-04 06:30 | 167 | 167
2017-03-04 07:00 | 175 | 174
2017-03-04 07:30 | 187 | 186
2017-03-04 08:00 | 187 | 186
2017-03-04 08:30 | 160 | 159
2017-03-04 09:00 | 162 | 162
2017-03-04 09:30 | 170 | 169
2017-03-04 10:00 | 153 | 152
2017-03-04 10:30 | 150 | 150
2017-03-04 11:00 | 145 | 144
2017-03-04 11:30 | 139 | 138
2017-03-04 12:00 | 145 | 144
2017-03-04 12:30 | 156 | 156
2017-03-04 13:00 | 163 | 163
2017-03-04 13:30 | 167 | 167
2017-03-04 14:00 | 169 | 169
2017-03-04 14:30 | 165 | 165
2017-03-04 15:00 | 164 | 163
2017-03-04 15:30 | 158 | 157
2017-03-04 16:00 | 166 | 165
2017-03-04 16:30 | 163 | 162
2017-03-04 17:00 | 165 | 165
2017-03-04 17:30 | 169 | 169
2017-03-04 18:00 | 172 | 172
2017-03-04 18:30 | 176 | 176
2017-03-04 19:00 | 181 | 181
2017-03-04 19:30 | 198 | 197
2017-03-04 20:00 | 228 | 227
2017-03-04 20:30 | 217 | 216
2017-03-04 21:00 | 243 | 243
2017-03-04 21:30 | 245 | 245
2017-03-04 22:00 | 234 | 233
2017-03-04 22:30 | 212 | 211
2017-03-04 23:00 | 174 | 173
2017-03-04 23:30 | 195 | 194
2017-03-05 | 185 | 184
2017-03-05 00:30 | 178 | 177
2017-03-05 01:00 | 169 | 168
2017-03-05 01:30 | 162 | 161
2017-03-05 02:00 | 158 | 157
2017-03-05 02:30 | 154 | 153
2017-03-05 03:00 | 131 | 130
2017-03-05 03:30 | 110 | 109
2017-03-05 04:00 | 107 | 106
2017-03-05 04:30 | 107 | 106
2017-03-05 05:00 | 107 | 106
2017-03-05 05:30 | 107 | 106
2017-03-05 06:00 | 109 | 108
2017-03-05 06:30 | 113 | 112
2017-03-05 07:00 | 116 | 115
2017-03-05 07:30 | 126 | 125
2017-03-05 08:00 | 135 | 134
2017-03-05 08:30 | 152 | 151
2017-03-05 09:00 | 161 | 160
2017-03-05 09:30 | 166 | 165
2017-03-05 10:00 | 168 | 167
2017-03-05 10:30 | 173 | 172
2017-03-05 11:00 | 174 | 173
2017-03-05 11:30 | 177 | 177
2017-03-05 12:00 | 188 | 187
2017-03-05 12:30 | 187 | 186
2017-03-05 13:00 | 193 | 192
2017-03-05 13:30 | 199 | 198
2017-03-05 14:00 | 208 | 207
2017-03-05 14:30 | 205 | 204
2017-03-05 15:00 | 175 | 174
2017-03-05 15:30 | 196 | 195
2017-03-05 16:00 | 175 | 175
2017-03-05 16:30 | 152 | 151
2017-03-05 17:00 | 152 | 151
2017-03-05 17:30 | 97 | 96
2017-03-05 18:00 | 88 | 87
2017-03-05 18:30 | 88 | 86
2017-03-05 19:00 | 84 | 82
2017-03-05 19:30 | 130 | 129
2017-03-05 20:00 | 217 | 217
2017-03-05 20:30 | 261 | 260
2017-03-05 21:00 | 295 | 294
2017-03-05 21:30 | 278 | 278
2017-03-05 22:00 | 261 | 260
2017-03-05 22:30 | 239 | 239
2017-03-05 23:00 | 224 | 223
2017-03-05 23:30 | 209 | 208
2017-03-06 | 199 | 198
2017-03-06 00:30 | 192 | 191
2017-03-06 01:00 | 184 | 183
2017-03-06 01:30 | 179 | 178
2017-03-06 02:00 | 177 | 176
2017-03-06 02:30 | 175 | 174
2017-03-06 03:00 | 172 | 171
2017-03-06 03:30 | 171 | 171
2017-03-06 04:00 | 169 | 168
2017-03-06 04:30 | 170 | 169
2017-03-06 05:00 | 174 | 173
2017-03-06 05:30 | 179 | 179
2017-03-06 06:00 | 189 | 188
2017-03-06 06:30 | 198 | 197
2017-03-06 07:00 | 176 | 175
2017-03-06 07:30 | 225 | 224
2017-03-06 08:00 | 253 | 252
2017-03-06 08:30 | 262 | 261
2017-03-06 09:00 | 220 | 219
2017-03-06 09:30 | 220 | 219
2017-03-06 10:00 | 251 | 250
2017-03-06 10:30 | 274 | 273
2017-03-06 11:00 | 237 | 236
2017-03-06 11:30 | 222 | 221
2017-03-06 12:00 | 238 | 237
2017-03-06 12:30 | 242 | 241
2017-03-06 13:00 | 242 | 241
2017-03-06 13:30 | 242 | 241
2017-03-06 14:00 | 243 | 242
2017-03-06 14:30 | 249 | 248
2017-03-06 15:00 | 244 | 243
2017-03-06 15:30 | 245 | 244
2017-03-06 16:00 | 260 | 259
2017-03-06 16:30 | 269 | 268
2017-03-06 17:00 | 272 | 271
2017-03-06 17:30 | 266 | 265
2017-03-06 18:00 | 271 | 270
2017-03-06 18:30 | 276 | 275
2017-03-06 19:00 | 288 | 287
2017-03-06 19:30 | 307 | 306
2017-03-06 20:00 | 317 | 317
2017-03-06 20:30 | 339 | 338
2017-03-06 21:00 | 343 | 342
2017-03-06 21:30 | 322 | 321
2017-03-06 22:00 | 302 | 300
2017-03-06 22:30 | 275 | 274
2017-03-06 23:00 | 255 | 254
2017-03-06 23:30 | 238 | 237
2017-03-07 | 228 | 227
2017-03-07 00:30 | 222 | 220
2017-03-07 01:00 | 210 | 209
2017-03-07 01:30 | 205 | 204
2017-03-07 02:00 | 201 | 199
2017-03-07 02:30 | 197 | 195
2017-03-07 03:00 | 193 | 191
2017-03-07 03:30 | 190 | 188
2017-03-07 04:00 | 189 | 188
2017-03-07 04:30 | 188 | 187
2017-03-07 05:00 | 190 | 188
2017-03-07 05:30 | 197 | 195
2017-03-07 06:00 | 207 | 206
2017-03-07 06:30 | 190 | 188
2017-03-07 07:00 | 192 | 191
2017-03-07 07:30 | 214 | 213
2017-03-07 08:00 | 227 | 227
2017-03-07 08:30 | 238 | 237
2017-03-07 09:00 | 243 | 242
2017-03-07 09:30 | 247 | 246
2017-03-07 10:00 | 232 | 231
2017-03-07 10:30 | 231 | 230
2017-03-07 11:00 | 232 | 231
2017-03-07 11:30 | 236 | 235
2017-03-07 12:00 | 241 | 240
2017-03-07 12:30 | 248 | 247
2017-03-07 13:00 | 250 | 249
2017-03-07 13:30 | 257 | 256
2017-03-07 14:00 | 258 | 257
2017-03-07 14:30 | 251 | 250
2017-03-07 15:00 | 255 | 254
2017-03-07 15:30 | 258 | 257
2017-03-07 16:00 | 271 | 270
2017-03-07 16:30 | 279 | 278
2017-03-07 17:00 | 287 | 286
2017-03-07 17:30 | 288 | 288
2017-03-07 18:00 | 288 | 287
2017-03-07 18:30 | 303 | 302
2017-03-07 19:00 | 340 | 340
2017-03-07 19:30 | 347 | 346
2017-03-07 20:00 | 338 | 338
2017-03-07 20:30 | 328 | 327
2017-03-07 21:00 | 315 | 314
2017-03-07 21:30 | 291 | 290
2017-03-07 22:00 | 298 | 297
2017-03-07 22:30 | 247 | 246
2017-03-07 23:00 | 215 | 214
2017-03-07 23:30 | 198 | 197
2017-03-08 | 207 | 206
2017-03-08 00:30 | 226 | 226
2017-03-08 01:00 | 215 | 214
2017-03-08 01:30 | 207 | 206
2017-03-08 02:00 | 202 | 201
2017-03-08 02:30 | 196 | 195
2017-03-08 03:00 | 193 | 192
2017-03-08 03:30 | 191 | 190
2017-03-08 04:00 | 190 | 189
2017-03-08 04:30 | 189 | 188
2017-03-08 05:00 | 179 | 178
2017-03-08 05:30 | 170 | 169
2017-03-08 06:00 | 167 | 166
2017-03-08 06:30 | 124 | 123
2017-03-08 07:00 | 137 | 136
2017-03-08 07:30 | 165 | 165
2017-03-08 08:00 | 178 | 177
2017-03-08 08:30 | 197 | 197
2017-03-08 09:00 | 202 | 202
2017-03-08 09:30 | 202 | 202
2017-03-08 10:00 | 203 | 203
2017-03-08 10:30 | 209 | 208
2017-03-08 11:00 | 208 | 207
2017-03-08 11:30 | 201 | 200
2017-03-08 12:00 | 192 | 191
2017-03-08 12:30 | 194 | 193
2017-03-08 13:00 | 197 | 197
2017-03-08 13:30 | 206 | 205
2017-03-08 14:00 | 209 | 209
2017-03-08 14:30 | 212 | 211
2017-03-08 15:00 | 218 | 218
2017-03-08 15:30 | 211 | 210
2017-03-08 16:00 | 206 | 205
2017-03-08 16:30 | 213 | 212
2017-03-08 17:00 | 211 | 210
2017-03-08 17:30 | 207 | 206
2017-03-08 18:00 | 209 | 208
2017-03-08 18:30 | 217 | 216
2017-03-08 19:00 | 266 | 265
2017-03-08 19:30 | 299 | 298
2017-03-08 20:00 | 300 | 299
2017-03-08 20:30 | 285 | 284
2017-03-08 21:00 | 271 | 271
2017-03-08 21:30 | 256 | 255
2017-03-08 22:00 | 248 | 247
2017-03-08 22:30 | 216 | 215
2017-03-08 23:00 | 190 | 190
2017-03-08 23:30 | 216 | 215
2017-03-09 | 250 | 249
2017-03-09 00:30 | 294 | 293
2017-03-09 01:00 | 281 | 281
2017-03-09 01:30 | 275 | 275
2017-03-09 02:00 | 270 | 269
2017-03-09 02:30 | 266 | 265
2017-03-09 03:00 | 262 | 261
2017-03-09 03:30 | 260 | 259
2017-03-09 04:00 | 257 | 257
2017-03-09 04:30 | 258 | 257
2017-03-09 05:00 | 260 | 259
2017-03-09 05:30 | 266 | 265
2017-03-09 06:00 | 277 | 276
2017-03-09 06:30 | 300 | 299
2017-03-09 07:00 | 319 | 318
2017-03-09 07:30 | 343 | 343
2017-03-09 08:00 | 354 | 353
2017-03-09 08:30 | 371 | 371
2017-03-09 09:00 | 386 | 386
2017-03-09 09:30 | 398 | 397
2017-03-09 10:00 | 394 | 394
2017-03-09 10:30 | 398 | 398
2017-03-09 11:00 | 396 | 396
2017-03-09 11:30 | 335 | 334
2017-03-09 12:00 | 307 | 306
2017-03-09 12:30 | 300 | 300
2017-03-09 13:00 | 295 | 294
2017-03-09 13:30 | 301 | 300
2017-03-09 14:00 | 305 | 304
2017-03-09 14:30 | 300 | 299
2017-03-09 15:00 | 292 | 291
2017-03-09 15:30 | 286 | 285
2017-03-09 16:00 | 279 | 278
2017-03-09 16:30 | 261 | 260
2017-03-09 17:00 | 251 | 250
2017-03-09 17:30 | 248 | 247
2017-03-09 18:00 | 251 | 250
2017-03-09 18:30 | 257 | 256
2017-03-09 19:00 | 267 | 266
2017-03-09 19:30 | 285 | 284
2017-03-09 20:00 | 295 | 294
2017-03-09 20:30 | 287 | 286
2017-03-09 21:00 | 275 | 274
2017-03-09 21:30 | 258 | 257
2017-03-09 22:00 | 269 | 269
2017-03-09 22:30 | 221 | 220
2017-03-09 23:00 | 199 | 198
2017-03-09 23:30 | 184 | 183
2017-03-10 | 172 | 172
2017-03-10 00:30 | 240 | 239
2017-03-10 01:00 | 251 | 250
2017-03-10 01:30 | 244 | 243
2017-03-10 02:00 | 238 | 238
2017-03-10 02:30 | 233 | 232
2017-03-10 03:00 | 229 | 229
2017-03-10 03:30 | 228 | 228
2017-03-10 04:00 | 228 | 228
2017-03-10 04:30 | 227 | 227
2017-03-10 05:00 | 228 | 228
2017-03-10 05:30 | 237 | 236
2017-03-10 06:00 | 251 | 250
2017-03-10 06:30 | 270 | 269
2017-03-10 07:00 | 288 | 287
2017-03-10 07:30 | 268 | 267
2017-03-10 08:00 | 238 | 237
2017-03-10 08:30 | 229 | 228
2017-03-10 09:00 | 225 | 224
2017-03-10 09:30 | 224 | 222
2017-03-10 10:00 | 224 | 222
2017-03-10 10:30 | 225 | 224
2017-03-10 11:00 | 227 | 225
2017-03-10 11:30 | 224 | 223
2017-03-10 12:00 | 230 | 229
2017-03-10 12:30 | 233 | 232
2017-03-10 13:00 | 239 | 238
2017-03-10 13:30 | 240 | 239
2017-03-10 14:00 | 240 | 239
2017-03-10 14:30 | 240 | 239
2017-03-10 15:00 | 242 | 241
2017-03-10 15:30 | 245 | 244
2017-03-10 16:00 | 250 | 249
2017-03-10 16:30 | 246 | 245
2017-03-10 17:00 | 250 | 249
2017-03-10 17:30 | 246 | 245
2017-03-10 18:00 | 243 | 242
2017-03-10 18:30 | 244 | 242
2017-03-10 19:00 | 250 | 249
2017-03-10 19:30 | 256 | 254
2017-03-10 20:00 | 246 | 245
2017-03-10 20:30 | 233 | 232
2017-03-10 21:00 | 219 | 218
2017-03-10 21:30 | 205 | 204
2017-03-10 22:00 | 235 | 234
2017-03-10 22:30 | 218 | 216
2017-03-10 23:00 | 200 | 198
2017-03-10 23:30 | 190 | 188
2017-03-11 | 173 | 171
2017-03-11 00:30 | 236 | 235
2017-03-11 01:00 | 249 | 247
2017-03-11 01:30 | 242 | 240
2017-03-11 02:00 | 234 | 233
2017-03-11 02:30 | 231 | 230
2017-03-11 03:00 | 228 | 227
2017-03-11 03:30 | 225 | 224
2017-03-11 04:00 | 224 | 223
2017-03-11 04:30 | 222 | 221
2017-03-11 05:00 | 222 | 221
2017-03-11 05:30 | 224 | 222
2017-03-11 06:00 | 228 | 226
2017-03-11 06:30 | 231 | 229
2017-03-11 07:00 | 237 | 236
2017-03-11 07:30 | 250 | 249
2017-03-11 08:00 | 263 | 262
2017-03-11 08:30 | 275 | 274
2017-03-11 09:00 | 282 | 281
2017-03-11 09:30 | 241 | 240
2017-03-11 10:00 | 179 | 178
2017-03-11 10:30 | 173 | 172
2017-03-11 11:00 | 169 | 167
2017-03-11 11:30 | 170 | 169
2017-03-11 12:00 | 171 | 170
2017-03-11 12:30 | 172 | 171
2017-03-11 13:00 | 178 | 176
2017-03-11 13:30 | 181 | 179
2017-03-11 14:00 | 186 | 184
2017-03-11 14:30 | 176 | 174
2017-03-11 15:00 | 177 | 175
2017-03-11 15:30 | 184 | 182
2017-03-11 16:00 | 192 | 190
2017-03-11 16:30 | 201 | 199
2017-03-11 17:00 | 209 | 207
2017-03-11 17:30 | 215 | 213
2017-03-11 18:00 | 234 | 232
2017-03-11 18:30 | 256 | 255
2017-03-11 19:00 | 267 | 266
2017-03-11 19:30 | 351 | 350
2017-03-11 20:00 | 362 | 360
2017-03-11 20:30 | 348 | 347
2017-03-11 21:00 | 338 | 336
2017-03-11 21:30 | 326 | 324
2017-03-11 22:00 | 313 | 312
2017-03-11 22:30 | 299 | 297
2017-03-11 23:00 | 285 | 283
2017-03-11 23:30 | 272 | 271
2017-03-12 | 261 | 259
2017-03-12 00:30 | 252 | 250
2017-03-12 01:00 | 242 | 240
2017-03-12 01:30 | 235 | 233
2017-03-12 02:00 | 230 | 228
2017-03-12 02:30 | 225 | 223
2017-03-12 03:00 | 222 | 220
2017-03-12 03:30 | 221 | 219
2017-03-12 04:00 | 219 | 217
2017-03-12 04:30 | 219 | 217
2017-03-12 05:00 | 219 | 217
2017-03-12 05:30 | 219 | 217
2017-03-12 06:00 | 220 | 218
2017-03-12 06:30 | 222 | 221
2017-03-12 07:00 | 226 | 224
2017-03-12 07:30 | 234 | 233
2017-03-12 08:00 | 242 | 240
2017-03-12 08:30 | 250 | 248
2017-03-12 09:00 | 255 | 253
2017-03-12 09:30 | 264 | 262
2017-03-12 10:00 | 270 | 268
2017-03-12 10:30 | 273 | 271
2017-03-12 11:00 | 275 | 273
2017-03-12 11:30 | 276 | 274
2017-03-12 12:00 | 277 | 275
2017-03-12 12:30 | 272 | 270
2017-03-12 13:00 | 271 | 269
2017-03-12 13:30 | 274 | 272
2017-03-12 14:00 | 275 | 273
2017-03-12 14:30 | 274 | 272
2017-03-12 15:00 | 281 | 279
2017-03-12 15:30 | 290 | 288
2017-03-12 16:00 | 301 | 300
2017-03-12 16:30 | 305 | 303
2017-03-12 17:00 | 319 | 317
2017-03-12 17:30 | 326 | 325
2017-03-12 18:00 | 332 | 331
2017-03-12 18:30 | 345 | 344
2017-03-12 19:00 | 355 | 353
2017-03-12 19:30 | 378 | 377
2017-03-12 20:00 | 385 | 384
2017-03-12 20:30 | 375 | 374
2017-03-12 21:00 | 364 | 363
2017-03-12 21:30 | 346 | 344
2017-03-12 22:00 | 325 | 323
2017-03-12 22:30 | 308 | 306
2017-03-12 23:00 | 304 | 302
2017-03-12 23:30 | 289 | 288
2017-03-13 | 275 | 274
2017-03-13 00:30 | 267 | 266
2017-03-13 01:00 | 260 | 258
2017-03-13 01:30 | 254 | 252
2017-03-13 02:00 | 251 | 250
2017-03-13 02:30 | 255 | 254
2017-03-13 03:00 | 246 | 245
2017-03-13 03:30 | 239 | 238
2017-03-13 04:00 | 239 | 238
2017-03-13 04:30 | 232 | 231
2017-03-13 05:00 | 206 | 205
2017-03-13 05:30 | 209 | 208
2017-03-13 06:00 | 221 | 220
2017-03-13 06:30 | 240 | 240
2017-03-13 07:00 | 262 | 261
2017-03-13 07:30 | 285 | 284
2017-03-13 08:00 | 295 | 294
2017-03-13 08:30 | 301 | 299
2017-03-13 09:00 | 304 | 303
2017-03-13 09:30 | 252 | 250
2017-03-13 10:00 | 252 | 250
2017-03-13 10:30 | 254 | 252
2017-03-13 11:00 | 256 | 255
2017-03-13 11:30 | 256 | 254
2017-03-13 12:00 | 270 | 269
2017-03-13 12:30 | 287 | 286
2017-03-13 13:00 | 294 | 293
2017-03-13 13:30 | 283 | 281
2017-03-13 14:00 | 280 | 278
2017-03-13 14:30 | 288 | 287
2017-03-13 15:00 | 296 | 295
2017-03-13 15:30 | 302 | 301
2017-03-13 16:00 | 306 | 305
2017-03-13 16:30 | 304 | 302
2017-03-13 17:00 | 306 | 305
2017-03-13 17:30 | 305 | 303
2017-03-13 18:00 | 307 | 306
2017-03-13 18:30 | 328 | 327
2017-03-13 19:00 | 357 | 356
2017-03-13 19:30 | 366 | 365
2017-03-13 20:00 | 360 | 358
2017-03-13 20:30 | 344 | 343
2017-03-13 21:00 | 330 | 328
2017-03-13 21:30 | 307 | 306
2017-03-13 22:00 | 287 | 286
2017-03-13 22:30 | 264 | 263
2017-03-13 23:00 | 243 | 241
2017-03-13 23:30 | 226 | 224
2017-03-14 | 212 | 210
2017-03-14 00:30 | 205 | 204
2017-03-14 01:00 | 199 | 197
2017-03-14 01:30 | 192 | 191
2017-03-14 02:00 | 182 | 181
2017-03-14 02:30 | 194 | 193
2017-03-14 03:00 | 220 | 218
2017-03-14 03:30 | 201 | 199
2017-03-14 04:00 | 192 | 191
2017-03-14 04:30 | 176 | 175
2017-03-14 05:00 | 178 | 177
2017-03-14 05:30 | 183 | 182
2017-03-14 06:00 | 193 | 192
2017-03-14 06:30 | 210 | 209
2017-03-14 07:00 | 225 | 224
2017-03-14 07:30 | 248 | 247
2017-03-14 08:00 | 262 | 261
2017-03-14 08:30 | 269 | 268
2017-03-14 09:00 | 282 | 281
2017-03-14 09:30 | 288 | 287
2017-03-14 10:00 | 286 | 284
2017-03-14 10:30 | 289 | 287
2017-03-14 11:00 | 288 | 287
2017-03-14 11:30 | 290 | 288
2017-03-14 12:00 | 295 | 294
2017-03-14 12:30 | 301 | 300
2017-03-14 13:00 | 305 | 303
2017-03-14 13:30 | 299 | 298
2017-03-14 14:00 | 297 | 296
2017-03-14 14:30 | 299 | 297
2017-03-14 15:00 | 316 | 315
2017-03-14 15:30 | 327 | 325
2017-03-14 16:00 | 334 | 333
2017-03-14 16:30 | 339 | 338
2017-03-14 17:00 | 332 | 330
2017-03-14 17:30 | 315 | 314
2017-03-14 18:00 | 314 | 313
2017-03-14 18:30 | 318 | 317
2017-03-14 19:00 | 342 | 341
2017-03-14 19:30 | 365 | 364
2017-03-14 20:00 | 363 | 362
2017-03-14 20:30 | 351 | 350
2017-03-14 21:00 | 339 | 337
2017-03-14 21:30 | 320 | 319
2017-03-14 22:00 | 298 | 296
2017-03-14 22:30 | 273 | 271
2017-03-14 23:00 | 254 | 252
2017-03-14 23:30 | 235 | 234
2017-03-15 | 220 | 219
2017-03-15 00:30 | 280 | 279
2017-03-15 01:00 | 292 | 291
2017-03-15 01:30 | 286 | 285
2017-03-15 02:00 | 278 | 277
2017-03-15 02:30 | 276 | 275
2017-03-15 03:00 | 273 | 272
2017-03-15 03:30 | 269 | 267
2017-03-15 04:00 | 270 | 268
2017-03-15 04:30 | 271 | 270
2017-03-15 05:00 | 273 | 271
2017-03-15 05:30 | 281 | 280
2017-03-15 06:00 | 291 | 290
2017-03-15 06:30 | 306 | 305
2017-03-15 07:00 | 267 | 265
2017-03-15 07:30 | 254 | 252
2017-03-15 08:00 | 267 | 266
2017-03-15 08:30 | 275 | 274
2017-03-15 09:00 | 278 | 276
2017-03-15 09:30 | 277 | 275
2017-03-15 10:00 | 281 | 279
2017-03-15 10:30 | 284 | 283
2017-03-15 11:00 | 285 | 284
2017-03-15 11:30 | 273 | 271
2017-03-15 12:00 | 275 | 274
2017-03-15 12:30 | 281 | 280
2017-03-15 13:00 | 284 | 283
2017-03-15 13:30 | 288 | 287
2017-03-15 14:00 | 296 | 295
2017-03-15 14:30 | 310 | 308
2017-03-15 15:00 | 306 | 305
2017-03-15 15:30 | 310 | 308
2017-03-15 16:00 | 323 | 322
2017-03-15 16:30 | 307 | 305
2017-03-15 17:00 | 293 | 291
2017-03-15 17:30 | 291 | 288
2017-03-15 18:00 | 298 | 295
2017-03-15 18:30 | 314 | 311
2017-03-15 19:00 | 327 | 325
2017-03-15 19:30 | 337 | 335
2017-03-15 20:00 | 326 | 325
2017-03-15 20:30 | 295 | 293
2017-03-15 21:00 | 278 | 276
2017-03-15 21:30 | 256 | 254
2017-03-15 22:00 | 233 | 231
2017-03-15 22:30 | 209 | 207
2017-03-15 23:00 | 191 | 189
2017-03-15 23:30 | 175 | 173
2017-03-16 | 160 | 158
2017-03-16 00:30 | 223 | 222
2017-03-16 01:00 | 232 | 231
2017-03-16 01:30 | 224 | 223
2017-03-16 02:00 | 228 | 227
2017-03-16 02:30 | 236 | 235
2017-03-16 03:00 | 234 | 233
2017-03-16 03:30 | 233 | 232
2017-03-16 04:00 | 230 | 229
2017-03-16 04:30 | 229 | 228
2017-03-16 05:00 | 232 | 231
2017-03-16 05:30 | 252 | 251
2017-03-16 06:00 | 269 | 268
2017-03-16 06:30 | 292 | 290
2017-03-16 07:00 | 275 | 274
2017-03-16 07:30 | 241 | 240
2017-03-16 08:00 | 248 | 246
2017-03-16 08:30 | 259 | 258
2017-03-16 09:00 | 268 | 267
2017-03-16 09:30 | 272 | 270
2017-03-16 10:00 | 276 | 274
2017-03-16 10:30 | 279 | 277
2017-03-16 11:00 | 289 | 287
2017-03-16 11:30 | 301 | 299
2017-03-16 12:00 | 305 | 303
2017-03-16 12:30 | 308 | 306
2017-03-16 13:00 | 303 | 301
2017-03-16 13:30 | 291 | 289
2017-03-16 14:00 | 293 | 291
2017-03-16 14:30 | 298 | 297
2017-03-16 15:00 | 306 | 304
2017-03-16 15:30 | 272 | 270
2017-03-16 16:00 | 292 | 291
2017-03-16 16:30 | 293 | 291
2017-03-16 17:00 | 272 | 269
2017-03-16 17:30 | 271 | 268
2017-03-16 18:00 | 267 | 265
2017-03-16 18:30 | 277 | 276
2017-03-16 19:00 | 301 | 299
2017-03-16 19:30 | 341 | 340
2017-03-16 20:00 | 358 | 357
2017-03-16 20:30 | 350 | 349
2017-03-16 21:00 | 334 | 332
2017-03-16 21:30 | 310 | 308
2017-03-16 22:00 | 289 | 287
2017-03-16 22:30 | 271 | 269
2017-03-16 23:00 | 250 | 248
2017-03-16 23:30 | 232 | 230
2017-03-17 | 217 | 216
2017-03-17 00:30 | 276 | 275
2017-03-17 01:00 | 289 | 288
2017-03-17 01:30 | 284 | 283
2017-03-17 02:00 | 279 | 278
2017-03-17 02:30 | 273 | 272
2017-03-17 03:00 | 271 | 270
2017-03-17 03:30 | 268 | 267
2017-03-17 04:00 | 267 | 266
2017-03-17 04:30 | 265 | 264
2017-03-17 05:00 | 267 | 266
2017-03-17 05:30 | 274 | 273
2017-03-17 06:00 | 232 | 230
2017-03-17 06:30 | 208 | 207
2017-03-17 07:00 | 222 | 221
2017-03-17 07:30 | 247 | 246
2017-03-17 08:00 | 261 | 260
2017-03-17 08:30 | 273 | 272
2017-03-17 09:00 | 281 | 280
2017-03-17 09:30 | 287 | 286
2017-03-17 10:00 | 290 | 289
2017-03-17 10:30 | 292 | 291
2017-03-17 11:00 | 292 | 291
2017-03-17 11:30 | 294 | 293
2017-03-17 12:00 | 299 | 297
2017-03-17 12:30 | 289 | 287
2017-03-17 13:00 | 287 | 285
2017-03-17 13:30 | 293 | 291
2017-03-17 14:00 | 299 | 297
2017-03-17 14:30 | 310 | 309
2017-03-17 15:00 | 317 | 316
2017-03-17 15:30 | 324 | 322
2017-03-17 16:00 | 335 | 333
2017-03-17 16:30 | 346 | 344
2017-03-17 17:00 | 353 | 351
2017-03-17 17:30 | 349 | 348
2017-03-17 18:00 | 341 | 339
2017-03-17 18:30 | 338 | 336
2017-03-17 19:00 | 345 | 343
2017-03-17 19:30 | 365 | 363
2017-03-17 20:00 | 360 | 359
2017-03-17 20:30 | 349 | 347
2017-03-17 21:00 | 337 | 335
2017-03-17 21:30 | 323 | 321
2017-03-17 22:00 | 309 | 307
2017-03-17 22:30 | 288 | 286
2017-03-17 23:00 | 275 | 273
2017-03-17 23:30 | 257 | 256
2017-03-18 | 242 | 241
2017-03-18 00:30 | 301 | 300
2017-03-18 01:00 | 314 | 313
2017-03-18 01:30 | 309 | 308
2017-03-18 02:00 | 302 | 301
2017-03-18 02:30 | 297 | 296
2017-03-18 03:00 | 293 | 292
2017-03-18 03:30 | 289 | 288
2017-03-18 04:00 | 285 | 283
2017-03-18 04:30 | 281 | 280
2017-03-18 05:00 | 281 | 279
2017-03-18 05:30 | 279 | 278
2017-03-18 06:00 | 282 | 281
2017-03-18 06:30 | 288 | 287
2017-03-18 07:00 | 294 | 292
2017-03-18 07:30 | 309 | 308
2017-03-18 08:00 | 324 | 323
2017-03-18 08:30 | 338 | 336
2017-03-18 09:00 | 344 | 342
2017-03-18 09:30 | 290 | 288
2017-03-18 10:00 | 262 | 260
2017-03-18 10:30 | 269 | 267
2017-03-18 11:00 | 274 | 272
2017-03-18 11:30 | 283 | 281
2017-03-18 12:00 | 289 | 288
2017-03-18 12:30 | 286 | 284
2017-03-18 13:00 | 279 | 277
2017-03-18 13:30 | 257 | 255
2017-03-18 14:00 | 245 | 243
2017-03-18 14:30 | 249 | 247
2017-03-18 15:00 | 259 | 258
2017-03-18 15:30 | 275 | 273
2017-03-18 16:00 | 287 | 285
2017-03-18 16:30 | 285 | 284
2017-03-18 17:00 | 272 | 271
2017-03-18 17:30 | 278 | 277
2017-03-18 18:00 | 284 | 282
2017-03-18 18:30 | 289 | 288
2017-03-18 19:00 | 298 | 297
2017-03-18 19:30 | 299 | 297
2017-03-18 20:00 | 287 | 286
2017-03-18 20:30 | 290 | 289
2017-03-18 21:00 | 301 | 300
2017-03-18 21:30 | 293 | 292
2017-03-18 22:00 | 279 | 278
2017-03-18 22:30 | 333 | 332
2017-03-18 23:00 | 341 | 340
2017-03-18 23:30 | 328 | 327
2017-03-19 | 315 | 314
2017-03-19 00:30 | 305 | 304
2017-03-19 01:00 | 297 | 295
2017-03-19 01:30 | 289 | 287
2017-03-19 02:00 | 278 | 277
2017-03-19 02:30 | 275 | 274
2017-03-19 03:00 | 269 | 268
2017-03-19 03:30 | 262 | 261
2017-03-19 04:00 | 260 | 258
2017-03-19 04:30 | 256 | 255
2017-03-19 05:00 | 254 | 253
2017-03-19 05:30 | 255 | 254
2017-03-19 06:00 | 258 | 257
2017-03-19 06:30 | 259 | 258
2017-03-19 07:00 | 260 | 259
2017-03-19 07:30 | 269 | 267
2017-03-19 08:00 | 276 | 275
2017-03-19 08:30 | 289 | 288
2017-03-19 09:00 | 295 | 294
2017-03-19 09:30 | 299 | 298
2017-03-19 10:00 | 274 | 273
2017-03-19 10:30 | 294 | 293
2017-03-19 11:00 | 317 | 316
2017-03-19 11:30 | 320 | 319
2017-03-19 12:00 | 322 | 321
2017-03-19 12:30 | 332 | 331
2017-03-19 13:00 | 341 | 340
2017-03-19 13:30 | 340 | 338
2017-03-19 14:00 | 336 | 335
2017-03-19 14:30 | 344 | 343
2017-03-19 15:00 | 342 | 341
2017-03-19 15:30 | 323 | 322
2017-03-19 16:00 | 309 | 308
2017-03-19 16:30 | 335 | 335
2017-03-19 17:00 | 292 | 291
2017-03-19 17:30 | 285 | 283
2017-03-19 18:00 | 303 | 302
2017-03-19 18:30 | 315 | 314
2017-03-19 19:00 | 322 | 321
2017-03-19 19:30 | 349 | 348
2017-03-19 20:00 | 348 | 347
2017-03-19 20:30 | 338 | 337
2017-03-19 21:00 | 348 | 348
2017-03-19 21:30 | 342 | 342
2017-03-19 22:00 | 328 | 327
2017-03-19 22:30 | 312 | 311
2017-03-19 23:00 | 295 | 294
2017-03-19 23:30 | 284 | 283
2017-03-20 | 274 | 273
2017-03-20 00:30 | 265 | 264
2017-03-20 01:00 | 259 | 258
2017-03-20 01:30 | 253 | 252
2017-03-20 02:00 | 250 | 249
2017-03-20 02:30 | 247 | 246
2017-03-20 03:00 | 243 | 242
2017-03-20 03:30 | 240 | 238
2017-03-20 04:00 | 240 | 239
2017-03-20 04:30 | 239 | 238
2017-03-20 05:00 | 243 | 242
2017-03-20 05:30 | 252 | 251
2017-03-20 06:00 | 214 | 212
2017-03-20 06:30 | 185 | 184
2017-03-20 07:00 | 169 | 168
2017-03-20 07:30 | 210 | 210
2017-03-20 08:00 | 235 | 234
2017-03-20 08:30 | 210 | 209
2017-03-20 09:00 | 199 | 198
2017-03-20 09:30 | 204 | 203
2017-03-20 10:00 | 209 | 208
2017-03-20 10:30 | 204 | 203
2017-03-20 11:00 | 207 | 206
2017-03-20 11:30 | 210 | 209
2017-03-20 12:00 | 220 | 219
2017-03-20 12:30 | 228 | 227
2017-03-20 13:00 | 229 | 229
2017-03-20 13:30 | 224 | 223
2017-03-20 14:00 | 217 | 217
2017-03-20 14:30 | 226 | 225
2017-03-20 15:00 | 223 | 222
2017-03-20 15:30 | 210 | 209
2017-03-20 16:00 | 216 | 215
2017-03-20 16:30 | 226 | 225
2017-03-20 17:00 | 227 | 226
2017-03-20 17:30 | 231 | 230
2017-03-20 18:00 | 235 | 234
2017-03-20 18:30 | 246 | 245
2017-03-20 19:00 | 248 | 247
2017-03-20 19:30 | 258 | 258
2017-03-20 20:00 | 256 | 255
2017-03-20 20:30 | 242 | 241
2017-03-20 21:00 | 227 | 226
2017-03-20 21:30 | 213 | 212
2017-03-20 22:00 | 198 | 197
2017-03-20 22:30 | 177 | 176
2017-03-20 23:00 | 162 | 162
2017-03-20 23:30 | 148 | 147
2017-03-21 | 137 | 136
2017-03-21 00:30 | 207 | 206
2017-03-21 01:00 | 219 | 218
2017-03-21 01:30 | 212 | 211
2017-03-21 02:00 | 207 | 206
2017-03-21 02:30 | 205 | 205
2017-03-21 03:00 | 203 | 202
2017-03-21 03:30 | 201 | 200
2017-03-21 04:00 | 199 | 198
2017-03-21 04:30 | 215 | 214
2017-03-21 05:00 | 219 | 218
2017-03-21 05:30 | 239 | 238
2017-03-21 06:00 | 213 | 212
2017-03-21 06:30 | 193 | 192
2017-03-21 07:00 | 211 | 210
2017-03-21 07:30 | 205 | 204
2017-03-21 08:00 | 219 | 218
2017-03-21 08:30 | 222 | 221
2017-03-21 09:00 | 220 | 219
2017-03-21 09:30 | 227 | 226
2017-03-21 10:00 | 228 | 227
2017-03-21 10:30 | 231 | 230
2017-03-21 11:00 | 240 | 239
2017-03-21 11:30 | 251 | 250
2017-03-21 12:00 | 250 | 249
2017-03-21 12:30 | 244 | 243
2017-03-21 13:00 | 252 | 251
2017-03-21 13:30 | 252 | 251
2017-03-21 14:00 | 256 | 255
2017-03-21 14:30 | 266 | 265
2017-03-21 15:00 | 270 | 269
2017-03-21 15:30 | 273 | 272
2017-03-21 16:00 | 274 | 273
2017-03-21 16:30 | 280 | 278
2017-03-21 17:00 | 269 | 268
2017-03-21 17:30 | 262 | 260
2017-03-21 18:00 | 262 | 260
2017-03-21 18:30 | 267 | 266
2017-03-21 19:00 | 281 | 280
2017-03-21 19:30 | 279 | 277
2017-03-21 20:00 | 281 | 280
2017-03-21 20:30 | 271 | 270
2017-03-21 21:00 | 254 | 252
2017-03-21 21:30 | 312 | 311
2017-03-21 22:00 | 315 | 314
2017-03-21 22:30 | 311 | 310
2017-03-21 23:00 | 300 | 299
2017-03-21 23:30 | 284 | 283
2017-03-22 | 271 | 269
2017-03-22 00:30 | 263 | 261
2017-03-22 01:00 | 255 | 254
2017-03-22 01:30 | 249 | 248
2017-03-22 02:00 | 246 | 244
2017-03-22 02:30 | 244 | 243
2017-03-22 03:00 | 241 | 239
2017-03-22 03:30 | 238 | 237
2017-03-22 04:00 | 237 | 236
2017-03-22 04:30 | 238 | 236
2017-03-22 05:00 | 239 | 237
2017-03-22 05:30 | 247 | 246
2017-03-22 06:00 | 259 | 258
2017-03-22 06:30 | 279 | 279
2017-03-22 07:00 | 297 | 297
2017-03-22 07:30 | 298 | 297
2017-03-22 08:00 | 296 | 296
2017-03-22 08:30 | 300 | 298
2017-03-22 09:00 | 302 | 301
2017-03-22 09:30 | 262 | 261
2017-03-22 10:00 | 208 | 207
2017-03-22 10:30 | 211 | 210
2017-03-22 11:00 | 215 | 214
2017-03-22 11:30 | 220 | 219
2017-03-22 12:00 | 230 | 230
2017-03-22 12:30 | 235 | 235
2017-03-22 13:00 | 238 | 237
2017-03-22 13:30 | 248 | 247
2017-03-22 14:00 | 258 | 258
2017-03-22 14:30 | 266 | 266
2017-03-22 15:00 | 269 | 269
2017-03-22 15:30 | 269 | 269
2017-03-22 16:00 | 271 | 271
2017-03-22 16:30 | 284 | 284
2017-03-22 17:00 | 288 | 288
2017-03-22 17:30 | 283 | 283
2017-03-22 18:00 | 282 | 282
2017-03-22 18:30 | 283 | 283
2017-03-22 19:00 | 291 | 291
2017-03-22 19:30 | 289 | 288
2017-03-22 20:00 | 278 | 278
2017-03-22 20:30 | 268 | 267
2017-03-22 21:00 | 258 | 258
2017-03-22 21:30 | 247 | 247
2017-03-22 22:00 | 234 | 233
2017-03-22 22:30 | 211 | 211
2017-03-22 23:00 | 258 | 257
2017-03-22 23:30 | 272 | 272
2017-03-23 | 261 | 260
2017-03-23 00:30 | 252 | 251
2017-03-23 01:00 | 243 | 243
2017-03-23 01:30 | 237 | 237
2017-03-23 02:00 | 232 | 231
2017-03-23 02:30 | 228 | 227
2017-03-23 03:00 | 225 | 224
2017-03-23 03:30 | 225 | 224
2017-03-23 04:00 | 223 | 223
2017-03-23 04:30 | 224 | 223
2017-03-23 05:00 | 230 | 230
2017-03-23 05:30 | 234 | 234
2017-03-23 06:00 | 244 | 243
2017-03-23 06:30 | 265 | 265
2017-03-23 07:00 | 282 | 282
2017-03-23 07:30 | 299 | 298
2017-03-23 08:00 | 296 | 295
2017-03-23 08:30 | 303 | 302
2017-03-23 09:00 | 307 | 307
2017-03-23 09:30 | 265 | 265
2017-03-23 10:00 | 220 | 220
2017-03-23 10:30 | 217 | 216
2017-03-23 11:00 | 214 | 213
2017-03-23 11:30 | 217 | 217
2017-03-23 12:00 | 221 | 220
2017-03-23 12:30 | 230 | 230
2017-03-23 13:00 | 233 | 233
2017-03-23 13:30 | 232 | 232
2017-03-23 14:00 | 245 | 244
2017-03-23 14:30 | 259 | 259
2017-03-23 15:00 | 262 | 262
2017-03-23 15:30 | 263 | 263
2017-03-23 16:00 | 263 | 263
2017-03-23 16:30 | 262 | 262
2017-03-23 17:00 | 266 | 266
2017-03-23 17:30 | 267 | 267
2017-03-23 18:00 | 272 | 271
2017-03-23 18:30 | 279 | 278
2017-03-23 19:00 | 294 | 294
2017-03-23 19:30 | 295 | 295
2017-03-23 20:00 | 280 | 280
2017-03-23 20:30 | 270 | 269
2017-03-23 21:00 | 251 | 251
2017-03-23 21:30 | 232 | 231
2017-03-23 22:00 | 224 | 223
2017-03-23 22:30 | 204 | 204
2017-03-23 23:00 | 257 | 257
2017-03-23 23:30 | 263 | 263
2017-03-24 | 251 | 250
2017-03-24 00:30 | 258 | 258
2017-03-24 01:00 | 254 | 254
2017-03-24 01:30 | 248 | 248
2017-03-24 02:00 | 246 | 245
2017-03-24 02:30 | 242 | 241
2017-03-24 03:00 | 239 | 238
2017-03-24 03:30 | 237 | 236
2017-03-24 04:00 | 236 | 235
2017-03-24 04:30 | 213 | 213
2017-03-24 05:00 | 198 | 198
2017-03-24 05:30 | 203 | 202
2017-03-24 06:00 | 215 | 215
2017-03-24 06:30 | 234 | 233
2017-03-24 07:00 | 194 | 193
2017-03-24 07:30 | 182 | 182
2017-03-24 08:00 | 195 | 195
2017-03-24 08:30 | 203 | 202
2017-03-24 09:00 | 204 | 204
2017-03-24 09:30 | 211 | 211
2017-03-24 10:00 | 208 | 208
2017-03-24 10:30 | 208 | 208
2017-03-24 11:00 | 212 | 211
2017-03-24 11:30 | 212 | 212
2017-03-24 12:00 | 212 | 211
2017-03-24 12:30 | 212 | 211
2017-03-24 13:00 | 213 | 212
2017-03-24 13:30 | 214 | 214
2017-03-24 14:00 | 213 | 213
2017-03-24 14:30 | 216 | 215
2017-03-24 15:00 | 221 | 220
2017-03-24 15:30 | 219 | 219
2017-03-24 16:00 | 226 | 225
2017-03-24 16:30 | 225 | 225
2017-03-24 17:00 | 225 | 224
2017-03-24 17:30 | 221 | 220
2017-03-24 18:00 | 222 | 222
2017-03-24 18:30 | 227 | 226
2017-03-24 19:00 | 235 | 235
2017-03-24 19:30 | 233 | 233
2017-03-24 20:00 | 219 | 219
2017-03-24 20:30 | 202 | 201
2017-03-24 21:00 | 190 | 189
2017-03-24 21:30 | 252 | 252
2017-03-24 22:00 | 261 | 261
2017-03-24 22:30 | 247 | 246
2017-03-24 23:00 | 238 | 237
2017-03-24 23:30 | 228 | 227
2017-03-25 | 220 | 220
2017-03-25 00:30 | 210 | 209
2017-03-25 01:00 | 196 | 196
2017-03-25 01:30 | 192 | 191
2017-03-25 02:00 | 188 | 188
2017-03-25 02:30 | 186 | 185
2017-03-25 03:00 | 184 | 183
2017-03-25 03:30 | 182 | 181
2017-03-25 04:00 | 179 | 178
2017-03-25 04:30 | 178 | 178
2017-03-25 05:00 | 178 | 178
2017-03-25 05:30 | 181 | 181
2017-03-25 06:00 | 187 | 187
2017-03-25 06:30 | 217 | 216
2017-03-25 07:00 | 224 | 224
2017-03-25 07:30 | 237 | 237
2017-03-25 08:00 | 248 | 247
2017-03-25 08:30 | 258 | 258
2017-03-25 09:00 | 267 | 266
2017-03-25 09:30 | 269 | 269
2017-03-25 10:00 | 269 | 268
2017-03-25 10:30 | 271 | 271
2017-03-25 11:00 | 273 | 273
2017-03-25 11:30 | 220 | 219
2017-03-25 12:00 | 195 | 194
2017-03-25 12:30 | 198 | 197
2017-03-25 13:00 | 206 | 206
2017-03-25 13:30 | 212 | 212
2017-03-25 14:00 | 218 | 218
2017-03-25 14:30 | 225 | 225
2017-03-25 15:00 | 233 | 233
2017-03-25 15:30 | 242 | 242
2017-03-25 16:00 | 250 | 250
2017-03-25 16:30 | 259 | 259
2017-03-25 17:00 | 264 | 264
2017-03-25 17:30 | 262 | 261
2017-03-25 18:00 | 258 | 258
2017-03-25 18:30 | 256 | 256
2017-03-25 19:00 | 268 | 268
2017-03-25 19:30 | 343 | 343
2017-03-25 20:00 | 349 | 348
2017-03-25 20:30 | 336 | 335
2017-03-25 21:00 | 334 | 334
2017-03-25 21:30 | 329 | 328
2017-03-25 22:00 | 314 | 314
2017-03-25 22:30 | 298 | 297
2017-03-25 23:00 | 282 | 281
2017-03-25 23:30 | 268 | 268
2017-03-26 | 259 | 258
2017-03-26 00:30 | 255 | 254
2017-03-26 01:00 | 247 | 247
2017-03-26 01:30 | 239 | 239
2017-03-26 02:00 | 234 | 233
2017-03-26 02:30 | 229 | 229
2017-03-26 03:00 | 226 | 225
2017-03-26 03:30 | 222 | 221
2017-03-26 04:00 | 220 | 219
2017-03-26 04:30 | 218 | 217
2017-03-26 05:00 | 218 | 217
2017-03-26 05:30 | 217 | 216
2017-03-26 06:00 | 199 | 198
2017-03-26 06:30 | 200 | 200
2017-03-26 07:00 | 202 | 202
2017-03-26 07:30 | 210 | 210
2017-03-26 08:00 | 226 | 225
2017-03-26 08:30 | 235 | 234
2017-03-26 09:00 | 241 | 240
2017-03-26 09:30 | 248 | 247
2017-03-26 10:00 | 250 | 249
2017-03-26 10:30 | 254 | 253
2017-03-26 11:00 | 261 | 260
2017-03-26 11:30 | 268 | 267
2017-03-26 12:00 | 271 | 270
2017-03-26 12:30 | 277 | 276
2017-03-26 13:00 | 293 | 292
2017-03-26 13:30 | 296 | 295
2017-03-26 14:00 | 301 | 300
2017-03-26 14:30 | 303 | 302
2017-03-26 15:00 | 313 | 312
2017-03-26 15:30 | 325 | 324
2017-03-26 16:00 | 308 | 308
2017-03-26 16:30 | 309 | 308
2017-03-26 17:00 | 300 | 299
2017-03-26 17:30 | 272 | 271
2017-03-26 18:00 | 224 | 223
2017-03-26 18:30 | 233 | 232
2017-03-26 19:00 | 241 | 239
2017-03-26 19:30 | 253 | 252
2017-03-26 20:00 | 245 | 244
2017-03-26 20:30 | 251 | 250
2017-03-26 21:00 | 242 | 241
2017-03-26 21:30 | 227 | 226
2017-03-26 22:00 | 211 | 210
2017-03-26 22:30 | 206 | 205
2017-03-26 23:00 | 194 | 193
2017-03-26 23:30 | 177 | 176
2017-03-27 | 167 | 166
2017-03-27 00:30 | 167 | 166
2017-03-27 01:00 | 159 | 158
2017-03-27 01:30 | 153 | 152
2017-03-27 02:00 | 148 | 147
2017-03-27 02:30 | 144 | 143
2017-03-27 03:00 | 144 | 143
2017-03-27 03:30 | 143 | 142
2017-03-27 04:00 | 140 | 139
2017-03-27 04:30 | 132 | 131
2017-03-27 05:00 | 135 | 134
2017-03-27 05:30 | 140 | 139
2017-03-27 06:00 | 150 | 149
2017-03-27 06:30 | 168 | 167
2017-03-27 07:00 | 182 | 182
2017-03-27 07:30 | 196 | 196
2017-03-27 08:00 | 205 | 205
2017-03-27 08:30 | 206 | 205
2017-03-27 09:00 | 207 | 206
2017-03-27 09:30 | 216 | 215
2017-03-27 10:00 | 219 | 219
2017-03-27 10:30 | 218 | 218
2017-03-27 11:00 | 218 | 217
2017-03-27 11:30 | 226 | 225
2017-03-27 12:00 | 226 | 225
2017-03-27 12:30 | 217 | 217
2017-03-27 13:00 | 226 | 226
2017-03-27 13:30 | 214 | 213
2017-03-27 14:00 | 219 | 219
2017-03-27 14:30 | 223 | 222
2017-03-27 15:00 | 230 | 229
2017-03-27 15:30 | 231 | 230
2017-03-27 16:00 | 237 | 236
2017-03-27 16:30 | 240 | 239
2017-03-27 17:00 | 242 | 241
2017-03-27 17:30 | 244 | 243
2017-03-27 18:00 | 248 | 247
2017-03-27 18:30 | 251 | 251
2017-03-27 19:00 | 261 | 261
2017-03-27 19:30 | 258 | 257
2017-03-27 20:00 | 245 | 244
2017-03-27 20:30 | 236 | 236
2017-03-27 21:00 | 224 | 223
2017-03-27 21:30 | 202 | 201
2017-03-27 22:00 | 180 | 179
2017-03-27 22:30 | 160 | 159
2017-03-27 23:00 | 143 | 142
2017-03-27 23:30 | 128 | 127
2017-03-28 | 114 | 114
2017-03-28 00:30 | 106 | 105
2017-03-28 01:00 | 165 | 165
2017-03-28 01:30 | 181 | 180
2017-03-28 02:00 | 175 | 174
2017-03-28 02:30 | 171 | 171
2017-03-28 03:00 | 169 | 168
2017-03-28 03:30 | 166 | 166
2017-03-28 04:00 | 163 | 162
2017-03-28 04:30 | 161 | 161
2017-03-28 05:00 | 163 | 162
2017-03-28 05:30 | 166 | 166
2017-03-28 06:00 | 174 | 173
2017-03-28 06:30 | 189 | 188
2017-03-28 07:00 | 201 | 201
2017-03-28 07:30 | 220 | 219
2017-03-28 08:00 | 236 | 235
2017-03-28 08:30 | 247 | 247
2017-03-28 09:00 | 253 | 252
2017-03-28 09:30 | 257 | 256
2017-03-28 10:00 | 254 | 254
2017-03-28 10:30 | 257 | 256
2017-03-28 11:00 | 259 | 258
2017-03-28 11:30 | 261 | 261
2017-03-28 12:00 | 267 | 266
2017-03-28 12:30 | 209 | 208
2017-03-28 13:00 | 178 | 177
2017-03-28 13:30 | 182 | 181
2017-03-28 14:00 | 189 | 188
2017-03-28 14:30 | 195 | 194
2017-03-28 15:00 | 179 | 178
2017-03-28 15:30 | 172 | 172
2017-03-28 16:00 | 175 | 174
2017-03-28 16:30 | 157 | 157
2017-03-28 17:00 | 149 | 148
2017-03-28 17:30 | 152 | 152
2017-03-28 18:00 | 160 | 159
2017-03-28 18:30 | 167 | 166
2017-03-28 19:00 | 171 | 170
2017-03-28 19:30 | 170 | 169
2017-03-28 20:00 | 158 | 158
2017-03-28 20:30 | 161 | 161
2017-03-28 21:00 | 157 | 157
2017-03-28 21:30 | 155 | 154
2017-03-28 22:00 | 157 | 156
2017-03-28 22:30 | 154 | 153
2017-03-28 23:00 | 145 | 144
2017-03-28 23:30 | 159 | 158
2017-03-29 | 160 | 159
2017-03-29 00:30 | 154 | 153
2017-03-29 01:00 | 151 | 150
2017-03-29 01:30 | 154 | 153
2017-03-29 02:00 | 155 | 154
2017-03-29 02:30 | 151 | 150
2017-03-29 03:00 | 151 | 150
2017-03-29 03:30 | 151 | 150
2017-03-29 04:00 | 151 | 149
2017-03-29 04:30 | 178 | 178
2017-03-29 05:00 | 191 | 190
2017-03-29 05:30 | 196 | 195
2017-03-29 06:00 | 206 | 205
2017-03-29 06:30 | 229 | 229
2017-03-29 07:00 | 249 | 248
2017-03-29 07:30 | 269 | 268
2017-03-29 08:00 | 288 | 288
2017-03-29 08:30 | 299 | 299
2017-03-29 09:00 | 309 | 309
2017-03-29 09:30 | 317 | 317
2017-03-29 10:00 | 311 | 311
2017-03-29 10:30 | 279 | 278
2017-03-29 11:00 | 281 | 280
2017-03-29 11:30 | 282 | 281
2017-03-29 12:00 | 284 | 283
2017-03-29 12:30 | 296 | 296
2017-03-29 13:00 | 304 | 304
2017-03-29 13:30 | 297 | 297
2017-03-29 14:00 | 274 | 274
2017-03-29 14:30 | 285 | 285
2017-03-29 15:00 | 298 | 298
2017-03-29 15:30 | 297 | 296
2017-03-29 16:00 | 304 | 304
2017-03-29 16:30 | 306 | 306
2017-03-29 17:00 | 297 | 297
2017-03-29 17:30 | 304 | 304
2017-03-29 18:00 | 294 | 293
2017-03-29 18:30 | 293 | 293
2017-03-29 19:00 | 316 | 315
2017-03-29 19:30 | 357 | 357
2017-03-29 20:00 | 357 | 356
2017-03-29 20:30 | 347 | 347
2017-03-29 21:00 | 340 | 339
2017-03-29 21:30 | 323 | 322
2017-03-29 22:00 | 309 | 309
2017-03-29 22:30 | 364 | 364
2017-03-29 23:00 | 360 | 360
2017-03-29 23:30 | 341 | 341
2017-03-30 | 330 | 330
2017-03-30 00:30 | 315 | 315
2017-03-30 01:00 | 308 | 308
2017-03-30 01:30 | 299 | 299
2017-03-30 02:00 | 291 | 291
2017-03-30 02:30 | 286 | 285
2017-03-30 03:00 | 281 | 281
2017-03-30 03:30 | 279 | 279
2017-03-30 04:00 | 277 | 277
2017-03-30 04:30 | 268 | 268
2017-03-30 05:00 | 270 | 270
2017-03-30 05:30 | 275 | 275
2017-03-30 06:00 | 285 | 285
2017-03-30 06:30 | 246 | 246
2017-03-30 07:00 | 225 | 225
2017-03-30 07:30 | 249 | 249
2017-03-30 08:00 | 264 | 264
2017-03-30 08:30 | 280 | 280
2017-03-30 09:00 | 287 | 287
2017-03-30 09:30 | 293 | 293
2017-03-30 10:00 | 299 | 298
2017-03-30 10:30 | 299 | 298
2017-03-30 11:00 | 288 | 287
2017-03-30 11:30 | 242 | 241
2017-03-30 12:00 | 272 | 271
2017-03-30 12:30 | 273 | 272
2017-03-30 13:00 | 283 | 282
2017-03-30 13:30 | 298 | 297
2017-03-30 14:00 | 329 | 328
2017-03-30 14:30 | 340 | 340
2017-03-30 15:00 | 343 | 343
2017-03-30 15:30 | 341 | 340
2017-03-30 16:00 | 331 | 331
2017-03-30 16:30 | 324 | 323
2017-03-30 17:00 | 309 | 308
2017-03-30 17:30 | 310 | 309
2017-03-30 18:00 | 320 | 320
2017-03-30 18:30 | 330 | 329
2017-03-30 19:00 | 341 | 341
2017-03-30 19:30 | 339 | 338
2017-03-30 20:00 | 343 | 343
2017-03-30 20:30 | 352 | 351
2017-03-30 21:00 | 347 | 347
2017-03-30 21:30 | 322 | 322
2017-03-30 22:00 | 306 | 305
2017-03-30 22:30 | 275 | 274
2017-03-30 23:00 | 251 | 250
2017-03-30 23:30 | 232 | 231
2017-03-31 | 254 | 253
2017-03-31 00:30 | 290 | 289
2017-03-31 01:00 | 288 | 287
2017-03-31 01:30 | 282 | 281
2017-03-31 02:00 | 276 | 275
2017-03-31 02:30 | 280 | 279
2017-03-31 03:00 | 275 | 275
2017-03-31 03:30 | 274 | 273
2017-03-31 04:00 | 272 | 271
2017-03-31 04:30 | 265 | 264
2017-03-31 05:00 | 267 | 266
2017-03-31 05:30 | 273 | 272
2017-03-31 06:00 | 285 | 284
2017-03-31 06:30 | 241 | 240
2017-03-31 07:00 | 220 | 220
2017-03-31 07:30 | 245 | 244
2017-03-31 08:00 | 250 | 250
2017-03-31 08:30 | 254 | 253
2017-03-31 09:00 | 266 | 265
2017-03-31 09:30 | 267 | 266
2017-03-31 10:00 | 267 | 266
2017-03-31 10:30 | 268 | 267
2017-03-31 11:00 | 272 | 271
2017-03-31 11:30 | 297 | 296
2017-03-31 12:00 | 313 | 312
2017-03-31 12:30 | 302 | 301
2017-03-31 13:00 | 295 | 294
2017-03-31 13:30 | 289 | 288
2017-03-31 14:00 | 291 | 291
2017-03-31 14:30 | 298 | 297
2017-03-31 15:00 | 302 | 301
2017-03-31 15:30 | 306 | 305
2017-03-31 16:00 | 318 | 318
2017-03-31 16:30 | 317 | 316
2017-03-31 17:00 | 281 | 281
2017-03-31 17:30 | 278 | 278
2017-03-31 18:00 | 291 | 290
2017-03-31 18:30 | 286 | 285
2017-03-31 19:00 | 294 | 293
2017-03-31 19:30 | 290 | 289
2017-03-31 20:00 | 278 | 277
2017-03-31 20:30 | 263 | 262
2017-03-31 21:00 | 248 | 247
2017-03-31 21:30 | 249 | 248
2017-03-31 22:00 | 254 | 253
2017-03-31 22:30 | 247 | 247
2017-03-31 23:00 | 232 | 232
2017-03-31 23:30 | 217 | 217
2017-04-01 | 206 | 205
2017-04-01 00:30 | 266 | 266
2017-04-01 01:00 | 278 | 278
2017-04-01 01:30 | 270 | 269
2017-04-01 02:00 | 263 | 263
2017-04-01 02:30 | 259 | 258
2017-04-01 03:00 | 254 | 253
2017-04-01 03:30 | 250 | 250
2017-04-01 04:00 | 248 | 247
2017-04-01 04:30 | 246 | 246
2017-04-01 05:00 | 245 | 245
2017-04-01 05:30 | 246 | 245
2017-04-01 06:00 | 248 | 247
2017-04-01 06:30 | 253 | 252
2017-04-01 07:00 | 256 | 255
2017-04-01 07:30 | 267 | 266
2017-04-01 08:00 | 276 | 275
2017-04-01 08:30 | 286 | 286
2017-04-01 09:00 | 291 | 290
2017-04-01 09:30 | 294 | 294
2017-04-01 10:00 | 295 | 294
2017-04-01 10:30 | 296 | 296
2017-04-01 11:00 | 296 | 296
2017-04-01 11:30 | 297 | 296
2017-04-01 12:00 | 299 | 298
2017-04-01 12:30 | 301 | 301
2017-04-01 13:00 | 305 | 304
2017-04-01 13:30 | 310 | 310
2017-04-01 14:00 | 313 | 312
2017-04-01 14:30 | 305 | 305
2017-04-01 15:00 | 305 | 304
2017-04-01 15:30 | 309 | 308
2017-04-01 16:00 | 315 | 314
2017-04-01 16:30 | 316 | 316
2017-04-01 17:00 | 313 | 313
2017-04-01 17:30 | 317 | 317
2017-04-01 18:00 | 322 | 321
2017-04-01 18:30 | 326 | 326
2017-04-01 19:00 | 336 | 335
2017-04-01 19:30 | 335 | 335
2017-04-01 20:00 | 336 | 336
2017-04-01 20:30 | 344 | 344
2017-04-01 21:00 | 339 | 338
2017-04-01 21:30 | 329 | 329
2017-04-01 22:00 | 318 | 318
2017-04-01 22:30 | 304 | 303
2017-04-01 23:00 | 291 | 290
2017-04-01 23:30 | 279 | 278
2017-04-02 | 271 | 270
2017-04-02 00:30 | 262 | 261
2017-04-02 01:00 | 254 | 253
2017-04-02 01:30 | 246 | 245
2017-04-02 02:00 | 241 | 240
2017-04-02 02:30 | 237 | 236
2017-04-02 03:00 | 235 | 234
2017-04-02 03:30 | 232 | 231
2017-04-02 04:00 | 229 | 228
2017-04-02 04:30 | 228 | 227
2017-04-02 05:00 | 226 | 225
2017-04-02 05:30 | 228 | 227
2017-04-02 06:00 | 229 | 228
2017-04-02 06:30 | 230 | 230
2017-04-02 07:00 | 230 | 230
2017-04-02 07:30 | 239 | 238
2017-04-02 08:00 | 245 | 244
2017-04-02 08:30 | 252 | 251
2017-04-02 09:00 | 256 | 255
2017-04-02 09:30 | 259 | 258
2017-04-02 10:00 | 263 | 262
2017-04-02 10:30 | 269 | 269
2017-04-02 11:00 | 270 | 269
2017-04-02 11:30 | 273 | 272
2017-04-02 12:00 | 277 | 277
2017-04-02 12:30 | 280 | 280
2017-04-02 13:00 | 283 | 283
2017-04-02 13:30 | 291 | 291
2017-04-02 14:00 | 294 | 294
2017-04-02 14:30 | 285 | 284
2017-04-02 15:00 | 285 | 284
2017-04-02 15:30 | 297 | 296
2017-04-02 16:00 | 305 | 304
2017-04-02 16:30 | 308 | 307
2017-04-02 17:00 | 306 | 305
2017-04-02 17:30 | 316 | 316
2017-04-02 18:00 | 325 | 325
2017-04-02 18:30 | 337 | 337
2017-04-02 19:00 | 356 | 356
2017-04-02 19:30 | 358 | 357
2017-04-02 20:00 | 355 | 355
2017-04-02 20:30 | 361 | 361
2017-04-02 21:00 | 360 | 359
2017-04-02 21:30 | 344 | 343
2017-04-02 22:00 | 331 | 330
2017-04-02 22:30 | 313 | 312
2017-04-02 23:00 | 297 | 296
2017-04-02 23:30 | 282 | 281
2017-04-03 | 271 | 271
2017-04-03 00:30 | 263 | 262
2017-04-03 01:00 | 256 | 255
2017-04-03 01:30 | 252 | 251
2017-04-03 02:00 | 248 | 247
2017-04-03 02:30 | 245 | 245
2017-04-03 03:00 | 241 | 240
2017-04-03 03:30 | 239 | 238
2017-04-03 04:00 | 238 | 238
2017-04-03 04:30 | 228 | 227
2017-04-03 05:00 | 201 | 201
2017-04-03 05:30 | 202 | 201
2017-04-03 06:00 | 212 | 212
2017-04-03 06:30 | 232 | 231
2017-04-03 07:00 | 249 | 249
2017-04-03 07:30 | 260 | 259
2017-04-03 08:00 | 264 | 263
2017-04-03 08:30 | 229 | 228
2017-04-03 09:00 | 222 | 221
2017-04-03 09:30 | 225 | 224
2017-04-03 10:00 | 226 | 225
2017-04-03 10:30 | 227 | 226
2017-04-03 11:00 | 225 | 224
2017-04-03 11:30 | 226 | 225
2017-04-03 12:00 | 231 | 230
2017-04-03 12:30 | 236 | 235
2017-04-03 13:00 | 244 | 243
2017-04-03 13:30 | 252 | 251
2017-04-03 14:00 | 251 | 250
2017-04-03 14:30 | 251 | 250
2017-04-03 15:00 | 256 | 255
2017-04-03 15:30 | 223 | 222
2017-04-03 16:00 | 234 | 233
2017-04-03 16:30 | 223 | 222
2017-04-03 17:00 | 201 | 200
2017-04-03 17:30 | 199 | 198
2017-04-03 18:00 | 200 | 199
2017-04-03 18:30 | 205 | 204
2017-04-03 19:00 | 220 | 219
2017-04-03 19:30 | 213 | 212
2017-04-03 20:00 | 215 | 214
2017-04-03 20:30 | 215 | 214
2017-04-03 21:00 | 206 | 205
2017-04-03 21:30 | 238 | 237
2017-04-03 22:00 | 237 | 236
2017-04-03 22:30 | 227 | 225
2017-04-03 23:00 | 214 | 213
2017-04-03 23:30 | 200 | 199
2017-04-04 | 188 | 187
2017-04-04 00:30 | 179 | 178
2017-04-04 01:00 | 169 | 168
2017-04-04 01:30 | 163 | 162
2017-04-04 02:00 | 158 | 157
2017-04-04 02:30 | 155 | 154
2017-04-04 03:00 | 154 | 153
2017-04-04 03:30 | 151 | 150
2017-04-04 04:00 | 152 | 150
2017-04-04 04:30 | 153 | 152
2017-04-04 05:00 | 153 | 152
2017-04-04 05:30 | 160 | 159
2017-04-04 06:00 | 170 | 169
2017-04-04 06:30 | 181 | 180
2017-04-04 07:00 | 148 | 147
2017-04-04 07:30 | 162 | 161
2017-04-04 08:00 | 177 | 177
2017-04-04 08:30 | 231 | 230
2017-04-04 09:00 | 235 | 234
2017-04-04 09:30 | 224 | 223
2017-04-04 10:00 | 212 | 211
2017-04-04 10:30 | 208 | 207
2017-04-04 11:00 | 181 | 180
2017-04-04 11:30 | 184 | 183
2017-04-04 12:00 | 181 | 180
2017-04-04 12:30 | 182 | 181
2017-04-04 13:00 | 207 | 206
2017-04-04 13:30 | 196 | 195
2017-04-04 14:00 | 199 | 198
2017-04-04 14:30 | 191 | 190
2017-04-04 15:00 | 199 | 198
2017-04-04 15:30 | 212 | 211
2017-04-04 16:00 | 194 | 193
2017-04-04 16:30 | 186 | 185
2017-04-04 17:00 | 175 | 175
2017-04-04 17:30 | 175 | 174
2017-04-04 18:00 | 179 | 178
2017-04-04 18:30 | 185 | 184
2017-04-04 19:00 | 196 | 195
2017-04-04 19:30 | 192 | 191
2017-04-04 20:00 | 180 | 179
2017-04-04 20:30 | 176 | 175
2017-04-04 21:00 | 161 | 160
2017-04-04 21:30 | 167 | 166
2017-04-04 22:00 | 163 | 161
2017-04-04 22:30 | 158 | 157
2017-04-04 23:00 | 142 | 141
2017-04-04 23:30 | 126 | 125
2017-04-05 | 117 | 116
2017-04-05 00:30 | 153 | 153
2017-04-05 01:00 | 161 | 160
2017-04-05 01:30 | 157 | 156
2017-04-05 02:00 | 152 | 151
2017-04-05 02:30 | 148 | 147
2017-04-05 03:00 | 145 | 144
2017-04-05 03:30 | 145 | 144
2017-04-05 04:00 | 143 | 142
2017-04-05 04:30 | 147 | 146
2017-04-05 05:00 | 149 | 148
2017-04-05 05:30 | 155 | 154
2017-04-05 06:00 | 161 | 160
2017-04-05 06:30 | 149 | 148
2017-04-05 07:00 | 130 | 130
2017-04-05 07:30 | 146 | 146
2017-04-05 08:00 | 162 | 161
2017-04-05 08:30 | 169 | 168
2017-04-05 09:00 | 172 | 171
2017-04-05 09:30 | 162 | 161
2017-04-05 10:00 | 151 | 150
2017-04-05 10:30 | 148 | 147
2017-04-05 11:00 | 145 | 145
2017-04-05 11:30 | 143 | 142
2017-04-05 12:00 | 141 | 141
2017-04-05 12:30 | 143 | 143
2017-04-05 13:00 | 149 | 148
2017-04-05 13:30 | 150 | 149
2017-04-05 14:00 | 157 | 156
2017-04-05 14:30 | 160 | 159
2017-04-05 15:00 | 157 | 157
2017-04-05 15:30 | 169 | 169
2017-04-05 16:00 | 178 | 178
2017-04-05 16:30 | 179 | 178
2017-04-05 17:00 | 170 | 169
2017-04-05 17:30 | 166 | 166
2017-04-05 18:00 | 169 | 168
2017-04-05 18:30 | 179 | 178
2017-04-05 19:00 | 193 | 192
2017-04-05 19:30 | 190 | 189
2017-04-05 20:00 | 178 | 177
2017-04-05 20:30 | 164 | 163
2017-04-05 21:00 | 175 | 175
2017-04-05 21:30 | 181 | 180
2017-04-05 22:00 | 183 | 182
2017-04-05 22:30 | 128 | 127
2017-04-05 23:00 | 104 | 102
2017-04-05 23:30 | 93 | 91
2017-04-06 | 122 | 121
2017-04-06 00:30 | 133 | 132
2017-04-06 01:00 | 149 | 148
2017-04-06 01:30 | 149 | 148
2017-04-06 02:00 | 144 | 143
2017-04-06 02:30 | 141 | 140
2017-04-06 03:00 | 139 | 138
2017-04-06 03:30 | 137 | 136
2017-04-06 04:00 | 136 | 135
2017-04-06 04:30 | 139 | 138
2017-04-06 05:00 | 141 | 140
2017-04-06 05:30 | 147 | 146
2017-04-06 06:00 | 158 | 157
2017-04-06 06:30 | 166 | 165
2017-04-06 07:00 | 132 | 131
2017-04-06 07:30 | 156 | 156
2017-04-06 08:00 | 163 | 162
2017-04-06 08:30 | 222 | 220
2017-04-06 09:00 | 222 | 221
2017-04-06 09:30 | 209 | 208
2017-04-06 10:00 | 204 | 202
2017-04-06 10:30 | 206 | 204
2017-04-06 11:00 | 205 | 204
2017-04-06 11:30 | 199 | 198
2017-04-06 12:00 | 192 | 191
2017-04-06 12:30 | 188 | 187
2017-04-06 13:00 | 193 | 191
2017-04-06 13:30 | 199 | 198
2017-04-06 14:00 | 205 | 203
2017-04-06 14:30 | 207 | 205
2017-04-06 15:00 | 209 | 208
2017-04-06 15:30 | 164 | 162
2017-04-06 16:00 | 160 | 158
2017-04-06 16:30 | 165 | 164
2017-04-06 17:00 | 168 | 167
2017-04-06 17:30 | 171 | 169
2017-04-06 18:00 | 175 | 173
2017-04-06 18:30 | 185 | 183
2017-04-06 19:00 | 201 | 200
2017-04-06 19:30 | 193 | 192
2017-04-06 20:00 | 181 | 179
2017-04-06 20:30 | 167 | 165
2017-04-06 21:00 | 156 | 154
2017-04-06 21:30 | 179 | 177
2017-04-06 22:00 | 176 | 174
2017-04-06 22:30 | 172 | 170
2017-04-06 23:00 | 161 | 159
2017-04-06 23:30 | 147 | 146
2017-04-07 | 138 | 136
2017-04-07 00:30 | 128 | 126
2017-04-07 01:00 | 119 | 117
2017-04-07 01:30 | 115 | 112
2017-04-07 02:00 | 110 | 107
2017-04-07 02:30 | 120 | 118
2017-04-07 03:00 | 121 | 119
2017-04-07 03:30 | 119 | 117
2017-04-07 04:00 | 118 | 116
2017-04-07 04:30 | 118 | 116
2017-04-07 05:00 | 122 | 120
2017-04-07 05:30 | 128 | 126
2017-04-07 06:00 | 137 | 136
2017-04-07 06:30 | 147 | 145
2017-04-07 07:00 | 144 | 143
2017-04-07 07:30 | 180 | 179
2017-04-07 08:00 | 195 | 194
2017-04-07 08:30 | 204 | 203
2017-04-07 09:00 | 206 | 205
2017-04-07 09:30 | 209 | 208
2017-04-07 10:00 | 208 | 207
2017-04-07 10:30 | 208 | 207
2017-04-07 11:00 | 206 | 205
2017-04-07 11:30 | 204 | 203
2017-04-07 12:00 | 209 | 208
2017-04-07 12:30 | 210 | 209
2017-04-07 13:00 | 211 | 210
2017-04-07 13:30 | 218 | 217
2017-04-07 14:00 | 213 | 212
2017-04-07 14:30 | 213 | 212
2017-04-07 15:00 | 217 | 216
2017-04-07 15:30 | 223 | 222
2017-04-07 16:00 | 227 | 226
2017-04-07 16:30 | 220 | 219
2017-04-07 17:00 | 209 | 208
2017-04-07 17:30 | 207 | 206
2017-04-07 18:00 | 211 | 210
2017-04-07 18:30 | 215 | 214
2017-04-07 19:00 | 223 | 222
2017-04-07 19:30 | 218 | 218
2017-04-07 20:00 | 223 | 222
2017-04-07 20:30 | 218 | 217
2017-04-07 21:00 | 209 | 208
2017-04-07 21:30 | 198 | 197
2017-04-07 22:00 | 188 | 187
2017-04-07 22:30 | 201 | 200
2017-04-07 23:00 | 197 | 195
2017-04-07 23:30 | 183 | 181
2017-04-08 | 173 | 171
2017-04-08 00:30 | 197 | 196
2017-04-08 01:00 | 240 | 239
2017-04-08 01:30 | 237 | 235
2017-04-08 02:00 | 229 | 228
2017-04-08 02:30 | 225 | 224
2017-04-08 03:00 | 225 | 224
2017-04-08 03:30 | 228 | 227
2017-04-08 04:00 | 229 | 228
2017-04-08 04:30 | 228 | 227
2017-04-08 05:00 | 225 | 224
2017-04-08 05:30 | 227 | 225
2017-04-08 06:00 | 229 | 228
2017-04-08 06:30 | 237 | 236
2017-04-08 07:00 | 242 | 241
2017-04-08 07:30 | 255 | 254
2017-04-08 08:00 | 267 | 266
2017-04-08 08:30 | 261 | 260
2017-04-08 09:00 | 263 | 262
2017-04-08 09:30 | 270 | 269
2017-04-08 10:00 | 276 | 275
2017-04-08 10:30 | 271 | 269
2017-04-08 11:00 | 267 | 266
2017-04-08 11:30 | 268 | 266
2017-04-08 12:00 | 271 | 270
2017-04-08 12:30 | 273 | 272
2017-04-08 13:00 | 277 | 275
2017-04-08 13:30 | 278 | 276
2017-04-08 14:00 | 278 | 277
2017-04-08 14:30 | 280 | 279
2017-04-08 15:00 | 282 | 281
2017-04-08 15:30 | 289 | 288
2017-04-08 16:00 | 295 | 293
2017-04-08 16:30 | 293 | 292
2017-04-08 17:00 | 281 | 279
2017-04-08 17:30 | 289 | 288
2017-04-08 18:00 | 294 | 293
2017-04-08 18:30 | 301 | 299
2017-04-08 19:00 | 313 | 312
2017-04-08 19:30 | 308 | 307
2017-04-08 20:00 | 307 | 306
2017-04-08 20:30 | 315 | 313
2017-04-08 21:00 | 312 | 310
2017-04-08 21:30 | 302 | 300
2017-04-08 22:00 | 295 | 293
2017-04-08 22:30 | 289 | 287
2017-04-08 23:00 | 279 | 278
2017-04-08 23:30 | 268 | 267
2017-04-09 | 259 | 258
2017-04-09 00:30 | 248 | 247
2017-04-09 01:00 | 240 | 239
2017-04-09 01:30 | 233 | 232
2017-04-09 02:00 | 232 | 231
2017-04-09 02:30 | 237 | 236
2017-04-09 03:00 | 235 | 233
2017-04-09 03:30 | 232 | 231
2017-04-09 04:00 | 231 | 230
2017-04-09 04:30 | 231 | 230
2017-04-09 05:00 | 230 | 229
2017-04-09 05:30 | 231 | 230
2017-04-09 06:00 | 232 | 231
2017-04-09 06:30 | 234 | 232
2017-04-09 07:00 | 224 | 223
2017-04-09 07:30 | 232 | 230
2017-04-09 08:00 | 235 | 234
2017-04-09 08:30 | 243 | 243
2017-04-09 09:00 | 238 | 238
2017-04-09 09:30 | 245 | 245
2017-04-09 10:00 | 246 | 246
2017-04-09 10:30 | 245 | 245
2017-04-09 11:00 | 244 | 244
2017-04-09 11:30 | 243 | 243
2017-04-09 12:00 | 242 | 242
2017-04-09 12:30 | 242 | 242
2017-04-09 13:00 | 246 | 246
2017-04-09 13:30 | 251 | 251
2017-04-09 14:00 | 256 | 256
2017-04-09 14:30 | 263 | 263
2017-04-09 15:00 | 268 | 268
2017-04-09 15:30 | 277 | 276
2017-04-09 16:00 | 291 | 289
2017-04-09 16:30 | 292 | 290
2017-04-09 17:00 | 291 | 290
2017-04-09 17:30 | 301 | 299
2017-04-09 18:00 | 309 | 308
2017-04-09 18:30 | 325 | 324
2017-04-09 19:00 | 342 | 342
2017-04-09 19:30 | 338 | 336
2017-04-09 20:00 | 353 | 350
2017-04-09 20:30 | 349 | 347
2017-04-09 21:00 | 339 | 336
2017-04-09 21:30 | 328 | 324
2017-04-09 22:00 | 314 | 309
2017-04-09 22:30 | 301 | 293
2017-04-09 23:00 | 287 | 279
2017-04-09 23:30 | 271 | 265
2017-04-10 | 255 | 252
2017-04-10 00:30 | 246 | 245
2017-04-10 01:00 | 240 | 239
2017-04-10 01:30 | 234 | 232
2017-04-10 02:00 | 231 | 229
2017-04-10 02:30 | 227 | 224
2017-04-10 03:00 | 225 | 222
2017-04-10 03:30 | 224 | 221
2017-04-10 04:00 | 224 | 221
2017-04-10 04:30 | 214 | 212
2017-04-10 05:00 | 187 | 184
2017-04-10 05:30 | 188 | 185
2017-04-10 06:00 | 191 | 188
2017-04-10 06:30 | 192 | 189
2017-04-10 07:00 | 195 | 192
2017-04-10 07:30 | 219 | 217
2017-04-10 08:00 | 225 | 222
2017-04-10 08:30 | 197 | 194
2017-04-10 09:00 | 195 | 193
2017-04-10 09:30 | 167 | 165
2017-04-10 10:00 | 175 | 172
2017-04-10 10:30 | 195 | 192
2017-04-10 11:00 | 196 | 193
2017-04-10 11:30 | 195 | 191
2017-04-10 12:00 | 195 | 192
2017-04-10 12:30 | 201 | 198
2017-04-10 13:00 | 203 | 201
2017-04-10 13:30 | 210 | 208
2017-04-10 14:00 | 216 | 214
2017-04-10 14:30 | 223 | 221
2017-04-10 15:00 | 234 | 233
2017-04-10 15:30 | 239 | 237
2017-04-10 16:00 | 246 | 244
2017-04-10 16:30 | 247 | 245
2017-04-10 17:00 | 240 | 239
2017-04-10 17:30 | 242 | 240
2017-04-10 18:00 | 232 | 230
2017-04-10 18:30 | 198 | 195
2017-04-10 19:00 | 240 | 238
2017-04-10 19:30 | 262 | 261
2017-04-10 20:00 | 261 | 259
2017-04-10 20:30 | 267 | 265
2017-04-10 21:00 | 258 | 257
2017-04-10 21:30 | 245 | 243
2017-04-10 22:00 | 232 | 229
2017-04-10 22:30 | 221 | 217
2017-04-10 23:00 | 209 | 203
2017-04-10 23:30 | 187 | 187
2017-04-11 | 176 | 175
2017-04-11 00:30 | 166 | 165
2017-04-11 01:00 | 160 | 158
2017-04-11 01:30 | 156 | 155
2017-04-11 02:00 | 150 | 148
2017-04-11 02:30 | 147 | 145
2017-04-11 03:00 | 145 | 143
2017-04-11 03:30 | 143 | 142
2017-04-11 04:00 | 142 | 141
2017-04-11 04:30 | 143 | 142
2017-04-11 05:00 | 145 | 144
2017-04-11 05:30 | 153 | 152
2017-04-11 06:00 | 162 | 162
2017-04-11 06:30 | 178 | 177
2017-04-11 07:00 | 154 | 154
2017-04-11 07:30 | 202 | 201
2017-04-11 08:00 | 215 | 214
2017-04-11 08:30 | 222 | 221
2017-04-11 09:00 | 225 | 223
2017-04-11 09:30 | 224 | 222
2017-04-11 10:00 | 222 | 220
2017-04-11 10:30 | 224 | 222
2017-04-11 11:00 | 227 | 225
2017-04-11 11:30 | 232 | 231
2017-04-11 12:00 | 235 | 233
2017-04-11 12:30 | 238 | 237
2017-04-11 13:00 | 240 | 239
2017-04-11 13:30 | 244 | 243
2017-04-11 14:00 | 251 | 250
2017-04-11 14:30 | 244 | 243
2017-04-11 15:00 | 245 | 243
2017-04-11 15:30 | 254 | 252
2017-04-11 16:00 | 260 | 258
2017-04-11 16:30 | 236 | 234
2017-04-11 17:00 | 211 | 210
2017-04-11 17:30 | 209 | 207
2017-04-11 18:00 | 191 | 189
2017-04-11 18:30 | 166 | 164
2017-04-11 19:00 | 195 | 194
2017-04-11 19:30 | 245 | 244
2017-04-11 20:00 | 242 | 241
2017-04-11 20:30 | 233 | 232
2017-04-11 21:00 | 232 | 231
2017-04-11 21:30 | 230 | 229
2017-04-11 22:00 | 239 | 238
2017-04-11 22:30 | 226 | 225
2017-04-11 23:00 | 219 | 217
2017-04-11 23:30 | 203 | 202
2017-04-12 | 193 | 191
2017-04-12 00:30 | 217 | 215
2017-04-12 01:00 | 260 | 259
2017-04-12 01:30 | 254 | 253
2017-04-12 02:00 | 247 | 246
2017-04-12 02:30 | 244 | 243
2017-04-12 03:00 | 240 | 239
2017-04-12 03:30 | 239 | 238
2017-04-12 04:00 | 240 | 238
2017-04-12 04:30 | 240 | 239
2017-04-12 05:00 | 243 | 242
2017-04-12 05:30 | 249 | 248
2017-04-12 06:00 | 258 | 257
2017-04-12 06:30 | 252 | 251
2017-04-12 07:00 | 240 | 239
2017-04-12 07:30 | 258 | 257
2017-04-12 08:00 | 256 | 254
2017-04-12 08:30 | 208 | 207
2017-04-12 09:00 | 212 | 211
2017-04-12 09:30 | 217 | 216
2017-04-12 10:00 | 211 | 210
2017-04-12 10:30 | 199 | 197
2017-04-12 11:00 | 179 | 178
2017-04-12 11:30 | 157 | 155
2017-04-12 12:00 | 153 | 152
2017-04-12 12:30 | 153 | 152
2017-04-12 13:00 | 154 | 153
2017-04-12 13:30 | 157 | 156
2017-04-12 14:00 | 160 | 158
2017-04-12 14:30 | 161 | 160
2017-04-12 15:00 | 164 | 162
2017-04-12 15:30 | 173 | 172
2017-04-12 16:00 | 182 | 181
2017-04-12 16:30 | 182 | 180
2017-04-12 17:00 | 177 | 175
2017-04-12 17:30 | 174 | 173
2017-04-12 18:00 | 178 | 177
2017-04-12 18:30 | 188 | 187
2017-04-12 19:00 | 204 | 203
2017-04-12 19:30 | 199 | 198
2017-04-12 20:00 | 200 | 198
2017-04-12 20:30 | 207 | 205
2017-04-12 21:00 | 201 | 200
2017-04-12 21:30 | 189 | 187
2017-04-12 22:00 | 176 | 175
2017-04-12 22:30 | 171 | 170
2017-04-12 23:00 | 170 | 168
2017-04-12 23:30 | 161 | 160
2017-04-13 | 178 | 176
2017-04-13 00:30 | 174 | 173
2017-04-13 01:00 | 165 | 163
2017-04-13 01:30 | 160 | 158
2017-04-13 02:00 | 154 | 153
2017-04-13 02:30 | 150 | 149
2017-04-13 03:00 | 147 | 146
2017-04-13 03:30 | 146 | 145
2017-04-13 04:00 | 144 | 142
2017-04-13 04:30 | 144 | 143
2017-04-13 05:00 | 147 | 145
2017-04-13 05:30 | 153 | 152
2017-04-13 06:00 | 161 | 160
2017-04-13 06:30 | 131 | 129
2017-04-13 07:00 | 136 | 135
2017-04-13 07:30 | 146 | 145
2017-04-13 08:00 | 154 | 152
2017-04-13 08:30 | 159 | 158
2017-04-13 09:00 | 163 | 162
2017-04-13 09:30 | 163 | 162
2017-04-13 10:00 | 163 | 162
2017-04-13 10:30 | 163 | 162
2017-04-13 11:00 | 163 | 162
2017-04-13 11:30 | 163 | 162
2017-04-13 12:00 | 162 | 161
2017-04-13 12:30 | 168 | 167
2017-04-13 13:00 | 171 | 170
2017-04-13 13:30 | 175 | 174
2017-04-13 14:00 | 177 | 176
2017-04-13 14:30 | 170 | 169
2017-04-13 15:00 | 168 | 166
2017-04-13 15:30 | 171 | 170
2017-04-13 16:00 | 175 | 174
2017-04-13 16:30 | 178 | 177
2017-04-13 17:00 | 172 | 171
2017-04-13 17:30 | 171 | 170
2017-04-13 18:00 | 176 | 174
2017-04-13 18:30 | 186 | 185
2017-04-13 19:00 | 196 | 195
2017-04-13 19:30 | 189 | 188
2017-04-13 20:00 | 192 | 191
2017-04-13 20:30 | 202 | 201
2017-04-13 21:00 | 197 | 196
2017-04-13 21:30 | 181 | 180
2017-04-13 22:00 | 184 | 183
2017-04-13 22:30 | 163 | 162
2017-04-13 23:00 | 142 | 140
2017-04-13 23:30 | 130 | 129
2017-04-14 | 163 | 161
2017-04-14 00:30 | 197 | 196
2017-04-14 01:00 | 242 | 241
2017-04-14 01:30 | 236 | 235
2017-04-14 02:00 | 230 | 229
2017-04-14 02:30 | 228 | 227
2017-04-14 03:00 | 225 | 224
2017-04-14 03:30 | 222 | 220
2017-04-14 04:00 | 220 | 218
2017-04-14 04:30 | 228 | 226
2017-04-14 05:00 | 230 | 229
2017-04-14 05:30 | 233 | 232
2017-04-14 06:00 | 236 | 235
2017-04-14 06:30 | 219 | 217
2017-04-14 07:00 | 202 | 201
2017-04-14 07:30 | 210 | 208
2017-04-14 08:00 | 218 | 217
2017-04-14 08:30 | 200 | 199
2017-04-14 09:00 | 174 | 173
2017-04-14 09:30 | 180 | 179
2017-04-14 10:00 | 181 | 180
2017-04-14 10:30 | 181 | 180
2017-04-14 11:00 | 179 | 178
2017-04-14 11:30 | 178 | 177
2017-04-14 12:00 | 183 | 182
2017-04-14 12:30 | 189 | 188
2017-04-14 13:00 | 198 | 197
2017-04-14 13:30 | 199 | 198
2017-04-14 14:00 | 194 | 192
2017-04-14 14:30 | 178 | 177
2017-04-14 15:00 | 170 | 169
2017-04-14 15:30 | 168 | 167
2017-04-14 16:00 | 181 | 180
2017-04-14 16:30 | 181 | 180
2017-04-14 17:00 | 180 | 179
2017-04-14 17:30 | 188 | 186
2017-04-14 18:00 | 194 | 192
2017-04-14 18:30 | 202 | 201
2017-04-14 19:00 | 216 | 215
2017-04-14 19:30 | 212 | 211
2017-04-14 20:00 | 212 | 211
2017-04-14 20:30 | 222 | 221
2017-04-14 21:00 | 218 | 217
2017-04-14 21:30 | 211 | 210
2017-04-14 22:00 | 202 | 201
2017-04-14 22:30 | 194 | 193
2017-04-14 23:00 | 181 | 180
2017-04-14 23:30 | 189 | 187
2017-04-15 | 235 | 234
2017-04-15 00:30 | 242 | 241
2017-04-15 01:00 | 239 | 238
2017-04-15 01:30 | 233 | 232
2017-04-15 02:00 | 230 | 229
2017-04-15 02:30 | 226 | 224
2017-04-15 03:00 | 223 | 222
2017-04-15 03:30 | 222 | 220
2017-04-15 04:00 | 222 | 220
2017-04-15 04:30 | 219 | 218
2017-04-15 05:00 | 221 | 219
2017-04-15 05:30 | 222 | 221
2017-04-15 06:00 | 223 | 221
2017-04-15 06:30 | 228 | 227
2017-04-15 07:00 | 235 | 233
2017-04-15 07:30 | 248 | 247
2017-04-15 08:00 | 257 | 256
2017-04-15 08:30 | 265 | 264
2017-04-15 09:00 | 272 | 270
2017-04-15 09:30 | 273 | 272
2017-04-15 10:00 | 273 | 271
2017-04-15 10:30 | 270 | 269
2017-04-15 11:00 | 263 | 262
2017-04-15 11:30 | 258 | 257
2017-04-15 12:00 | 266 | 265
2017-04-15 12:30 | 267 | 266
2017-04-15 13:00 | 262 | 260
2017-04-15 13:30 | 262 | 261
2017-04-15 14:00 | 258 | 256
2017-04-15 14:30 | 249 | 248
2017-04-15 15:00 | 253 | 251
2017-04-15 15:30 | 263 | 261
2017-04-15 16:00 | 270 | 268
2017-04-15 16:30 | 274 | 273
2017-04-15 17:00 | 272 | 271
2017-04-15 17:30 | 281 | 280
2017-04-15 18:00 | 286 | 285
2017-04-15 18:30 | 299 | 298
2017-04-15 19:00 | 310 | 309
2017-04-15 19:30 | 301 | 300
2017-04-15 20:00 | 290 | 288
2017-04-15 20:30 | 291 | 290
2017-04-15 21:00 | 304 | 302
2017-04-15 21:30 | 300 | 298
2017-04-15 22:00 | 293 | 292
2017-04-15 22:30 | 282 | 280
2017-04-15 23:00 | 271 | 270
2017-04-15 23:30 | 262 | 260
2017-04-16 | 252 | 251
2017-04-16 00:30 | 245 | 244
2017-04-16 01:00 | 240 | 239
2017-04-16 01:30 | 233 | 232
2017-04-16 02:00 | 230 | 228
2017-04-16 02:30 | 226 | 224
2017-04-16 03:00 | 223 | 222
2017-04-16 03:30 | 222 | 221
2017-04-16 04:00 | 222 | 221
2017-04-16 04:30 | 222 | 221
2017-04-16 05:00 | 220 | 218
2017-04-16 05:30 | 221 | 219
2017-04-16 06:00 | 223 | 221
2017-04-16 06:30 | 225 | 224
2017-04-16 07:00 | 229 | 228
2017-04-16 07:30 | 239 | 237
2017-04-16 08:00 | 245 | 243
2017-04-16 08:30 | 251 | 250
2017-04-16 09:00 | 253 | 251
2017-04-16 09:30 | 256 | 255
2017-04-16 10:00 | 264 | 263
2017-04-16 10:30 | 267 | 266
2017-04-16 11:00 | 264 | 263
2017-04-16 11:30 | 264 | 262
2017-04-16 12:00 | 260 | 259
2017-04-16 12:30 | 261 | 259
2017-04-16 13:00 | 258 | 257
2017-04-16 13:30 | 263 | 262
2017-04-16 14:00 | 263 | 262
2017-04-16 14:30 | 248 | 246
2017-04-16 15:00 | 245 | 244
2017-04-16 15:30 | 253 | 252
2017-04-16 16:00 | 260 | 259
2017-04-16 16:30 | 264 | 263
2017-04-16 17:00 | 265 | 264
2017-04-16 17:30 | 274 | 273
2017-04-16 18:00 | 282 | 281
2017-04-16 18:30 | 292 | 291
2017-04-16 19:00 | 303 | 302
2017-04-16 19:30 | 296 | 295
2017-04-16 20:00 | 299 | 297
2017-04-16 20:30 | 310 | 309
2017-04-16 21:00 | 305 | 304
2017-04-16 21:30 | 296 | 295
2017-04-16 22:00 | 287 | 286
2017-04-16 22:30 | 275 | 273
2017-04-16 23:00 | 264 | 262
2017-04-16 23:30 | 252 | 251
2017-04-17 | 246 | 244
2017-04-17 00:30 | 238 | 236
2017-04-17 01:00 | 231 | 229
2017-04-17 01:30 | 226 | 225
2017-04-17 02:00 | 222 | 221
2017-04-17 02:30 | 220 | 219
2017-04-17 03:00 | 215 | 213
2017-04-17 03:30 | 215 | 213
2017-04-17 04:00 | 212 | 211
2017-04-17 04:30 | 213 | 212
2017-04-17 05:00 | 212 | 210
2017-04-17 05:30 | 215 | 214
2017-04-17 06:00 | 219 | 218
2017-04-17 06:30 | 225 | 224
2017-04-17 07:00 | 228 | 227
2017-04-17 07:30 | 239 | 238
2017-04-17 08:00 | 248 | 247
2017-04-17 08:30 | 256 | 255
2017-04-17 09:00 | 260 | 259
2017-04-17 09:30 | 265 | 264
2017-04-17 10:00 | 265 | 264
2017-04-17 10:30 | 268 | 267
2017-04-17 11:00 | 267 | 266
2017-04-17 11:30 | 266 | 265
2017-04-17 12:00 | 273 | 272
2017-04-17 12:30 | 276 | 275
2017-04-17 13:00 | 275 | 274
2017-04-17 13:30 | 270 | 269
2017-04-17 14:00 | 270 | 269
2017-04-17 14:30 | 260 | 259
2017-04-17 15:00 | 264 | 263
2017-04-17 15:30 | 272 | 271
2017-04-17 16:00 | 281 | 280
2017-04-17 16:30 | 285 | 284
2017-04-17 17:00 | 284 | 283
2017-04-17 17:30 | 297 | 296
2017-04-17 18:00 | 308 | 307
2017-04-17 18:30 | 325 | 324
2017-04-17 19:00 | 337 | 336
2017-04-17 19:30 | 331 | 329
2017-04-17 20:00 | 329 | 328
2017-04-17 20:30 | 335 | 334
2017-04-17 21:00 | 328 | 327
2017-04-17 21:30 | 318 | 316
2017-04-17 22:00 | 303 | 301
2017-04-17 22:30 | 288 | 286
2017-04-17 23:00 | 274 | 271
2017-04-17 23:30 | 262 | 260
2017-04-18 | 252 | 250
2017-04-18 00:30 | 244 | 242
2017-04-18 01:00 | 239 | 237
2017-04-18 01:30 | 233 | 231
2017-04-18 02:00 | 227 | 225
2017-04-18 02:30 | 225 | 223
2017-04-18 03:00 | 224 | 222
2017-04-18 03:30 | 222 | 221
2017-04-18 04:00 | 221 | 220
2017-04-18 04:30 | 224 | 223
2017-04-18 05:00 | 229 | 228
2017-04-18 05:30 | 237 | 236
2017-04-18 06:00 | 246 | 245
2017-04-18 06:30 | 268 | 267
2017-04-18 07:00 | 283 | 282
2017-04-18 07:30 | 306 | 305
2017-04-18 08:00 | 317 | 316
2017-04-18 08:30 | 316 | 315
2017-04-18 09:00 | 315 | 313
2017-04-18 09:30 | 314 | 313
2017-04-18 10:00 | 309 | 308
2017-04-18 10:30 | 309 | 307
2017-04-18 11:00 | 312 | 311
2017-04-18 11:30 | 308 | 307
2017-04-18 12:00 | 305 | 304
2017-04-18 12:30 | 313 | 312
2017-04-18 13:00 | 324 | 323
2017-04-18 13:30 | 325 | 324
2017-04-18 14:00 | 323 | 322
2017-04-18 14:30 | 313 | 312
2017-04-18 15:00 | 311 | 310
2017-04-18 15:30 | 314 | 312
2017-04-18 16:00 | 320 | 319
2017-04-18 16:30 | 323 | 321
2017-04-18 17:00 | 315 | 314
2017-04-18 17:30 | 315 | 314
2017-04-18 18:00 | 320 | 319
2017-04-18 18:30 | 333 | 332
2017-04-18 19:00 | 344 | 343
2017-04-18 19:30 | 336 | 335
2017-04-18 20:00 | 338 | 336
2017-04-18 20:30 | 346 | 345
2017-04-18 21:00 | 338 | 336
2017-04-18 21:30 | 321 | 319
2017-04-18 22:00 | 305 | 303
2017-04-18 22:30 | 295 | 293
2017-04-18 23:00 | 280 | 278
2017-04-18 23:30 | 268 | 266
2017-04-19 | 254 | 252
2017-04-19 00:30 | 246 | 244
2017-04-19 01:00 | 242 | 240
2017-04-19 01:30 | 235 | 233
2017-04-19 02:00 | 229 | 227
2017-04-19 02:30 | 224 | 222
2017-04-19 03:00 | 222 | 220
2017-04-19 03:30 | 220 | 218
2017-04-19 04:00 | 218 | 216
2017-04-19 04:30 | 197 | 195
2017-04-19 05:00 | 196 | 194
2017-04-19 05:30 | 188 | 186
2017-04-19 06:00 | 200 | 198
2017-04-19 06:30 | 217 | 215
2017-04-19 07:00 | 237 | 235
2017-04-19 07:30 | 262 | 260
2017-04-19 08:00 | 272 | 271
2017-04-19 08:30 | 275 | 274
2017-04-19 09:00 | 275 | 274
2017-04-19 09:30 | 281 | 280
2017-04-19 10:00 | 277 | 275
2017-04-19 10:30 | 266 | 264
2017-04-19 11:00 | 233 | 231
2017-04-19 11:30 | 231 | 228
2017-04-19 12:00 | 235 | 232
2017-04-19 12:30 | 227 | 225
2017-04-19 13:00 | 281 | 279
2017-04-19 13:30 | 286 | 284
2017-04-19 14:00 | 276 | 273
2017-04-19 14:30 | 225 | 222
2017-04-19 15:00 | 224 | 222
2017-04-19 15:30 | 226 | 224
2017-04-19 16:00 | 231 | 229
2017-04-19 16:30 | 230 | 228
2017-04-19 17:00 | 222 | 220
2017-04-19 17:30 | 209 | 207
2017-04-19 18:00 | 179 | 178
2017-04-19 18:30 | 192 | 191
2017-04-19 19:00 | 206 | 204
2017-04-19 19:30 | 210 | 208
2017-04-19 20:00 | 215 | 214
2017-04-19 20:30 | 233 | 231
2017-04-19 21:00 | 222 | 220
2017-04-19 21:30 | 218 | 217
2017-04-19 22:00 | 207 | 206
2017-04-19 22:30 | 190 | 188
2017-04-19 23:00 | 178 | 176
2017-04-19 23:30 | 165 | 164
2017-04-20 | 157 | 156
2017-04-20 00:30 | 152 | 151
2017-04-20 01:00 | 148 | 147
2017-04-20 01:30 | 144 | 143
2017-04-20 02:00 | 144 | 143
2017-04-20 02:30 | 141 | 140
2017-04-20 03:00 | 142 | 140
2017-04-20 03:30 | 142 | 140
2017-04-20 04:00 | 140 | 139
2017-04-20 04:30 | 141 | 139
2017-04-20 05:00 | 143 | 141
2017-04-20 05:30 | 152 | 150
2017-04-20 06:00 | 164 | 163
2017-04-20 06:30 | 184 | 182
2017-04-20 07:00 | 205 | 204
2017-04-20 07:30 | 232 | 231
2017-04-20 08:00 | 240 | 239
2017-04-20 08:30 | 243 | 242
2017-04-20 09:00 | 242 | 240
2017-04-20 09:30 | 240 | 239
2017-04-20 10:00 | 233 | 232
2017-04-20 10:30 | 244 | 242
2017-04-20 11:00 | 240 | 239
2017-04-20 11:30 | 235 | 234
2017-04-20 12:00 | 236 | 235
2017-04-20 12:30 | 242 | 240
2017-04-20 13:00 | 238 | 236
2017-04-20 13:30 | 239 | 237
2017-04-20 14:00 | 246 | 244
2017-04-20 14:30 | 238 | 237
2017-04-20 15:00 | 232 | 231
2017-04-20 15:30 | 235 | 233
2017-04-20 16:00 | 193 | 191
2017-04-20 16:30 | 181 | 180
2017-04-20 17:00 | 171 | 169
2017-04-20 17:30 | 170 | 168
2017-04-20 18:00 | 177 | 176
2017-04-20 18:30 | 194 | 193
2017-04-20 19:00 | 204 | 203
2017-04-20 19:30 | 210 | 209
2017-04-20 20:00 | 217 | 216
2017-04-20 20:30 | 212 | 211
2017-04-20 21:00 | 200 | 198
2017-04-20 21:30 | 225 | 224
2017-04-20 22:00 | 223 | 221
2017-04-20 22:30 | 208 | 206
2017-04-20 23:00 | 192 | 190
2017-04-20 23:30 | 179 | 178
2017-04-21 | 168 | 166
2017-04-21 00:30 | 161 | 159
2017-04-21 01:00 | 156 | 154
2017-04-21 01:30 | 151 | 149
2017-04-21 02:00 | 147 | 145
2017-04-21 02:30 | 142 | 139
2017-04-21 03:00 | 141 | 138
2017-04-21 03:30 | 141 | 138
2017-04-21 04:00 | 141 | 138
2017-04-21 04:30 | 143 | 140
2017-04-21 05:00 | 144 | 142
2017-04-21 05:30 | 153 | 151
2017-04-21 06:00 | 164 | 162
2017-04-21 06:30 | 189 | 187
2017-04-21 07:00 | 205 | 203
2017-04-21 07:30 | 230 | 229
2017-04-21 08:00 | 243 | 242
2017-04-21 08:30 | 247 | 245
2017-04-21 09:00 | 243 | 242
2017-04-21 09:30 | 240 | 238
2017-04-21 10:00 | 238 | 237
2017-04-21 10:30 | 236 | 235
2017-04-21 11:00 | 235 | 234
2017-04-21 11:30 | 233 | 231
2017-04-21 12:00 | 229 | 228
2017-04-21 12:30 | 232 | 230
2017-04-21 13:00 | 233 | 231
2017-04-21 13:30 | 235 | 233
2017-04-21 14:00 | 234 | 232
2017-04-21 14:30 | 223 | 222
2017-04-21 15:00 | 220 | 219
2017-04-21 15:30 | 216 | 215
2017-04-21 16:00 | 174 | 172
2017-04-21 16:30 | 164 | 162
2017-04-21 17:00 | 159 | 157
2017-04-21 17:30 | 162 | 160
2017-04-21 18:00 | 164 | 162
2017-04-21 18:30 | 175 | 173
2017-04-21 19:00 | 182 | 180
2017-04-21 19:30 | 176 | 174
2017-04-21 20:00 | 176 | 174
2017-04-21 20:30 | 185 | 183
2017-04-21 21:00 | 182 | 180
2017-04-21 21:30 | 215 | 213
2017-04-21 22:00 | 219 | 217
2017-04-21 22:30 | 206 | 204
2017-04-21 23:00 | 193 | 191
2017-04-21 23:30 | 182 | 180
2017-04-22 | 172 | 170
2017-04-22 00:30 | 197 | 195
2017-04-22 01:00 | 241 | 240
2017-04-22 01:30 | 235 | 234
2017-04-22 02:00 | 228 | 226
2017-04-22 02:30 | 224 | 222
2017-04-22 03:00 | 222 | 221
2017-04-22 03:30 | 222 | 221
2017-04-22 04:00 | 222 | 220
2017-04-22 04:30 | 219 | 218
2017-04-22 05:00 | 222 | 220
2017-04-22 05:30 | 223 | 221
2017-04-22 06:00 | 228 | 227
2017-04-22 06:30 | 267 | 265
2017-04-22 07:00 | 281 | 280
2017-04-22 07:30 | 286 | 285
2017-04-22 08:00 | 290 | 288
2017-04-22 08:30 | 293 | 292
2017-04-22 09:00 | 298 | 297
2017-04-22 09:30 | 299 | 297
2017-04-22 10:00 | 299 | 297
2017-04-22 10:30 | 295 | 293
2017-04-22 11:00 | 294 | 293
2017-04-22 11:30 | 289 | 287
2017-04-22 12:00 | 288 | 286
2017-04-22 12:30 | 287 | 285
2017-04-22 13:00 | 284 | 282
2017-04-22 13:30 | 283 | 281
2017-04-22 14:00 | 281 | 280
2017-04-22 14:30 | 268 | 267
2017-04-22 15:00 | 261 | 259
2017-04-22 15:30 | 268 | 266
2017-04-22 16:00 | 274 | 272
2017-04-22 16:30 | 277 | 276
2017-04-22 17:00 | 277 | 275
2017-04-22 17:30 | 283 | 281
2017-04-22 18:00 | 290 | 289
2017-04-22 18:30 | 303 | 301
2017-04-22 19:00 | 307 | 306
2017-04-22 19:30 | 297 | 295
2017-04-22 20:00 | 299 | 298
2017-04-22 20:30 | 307 | 306
2017-04-22 21:00 | 293 | 292
2017-04-22 21:30 | 286 | 285
2017-04-22 22:00 | 274 | 273
2017-04-22 22:30 | 266 | 264
2017-04-22 23:00 | 259 | 258
2017-04-22 23:30 | 251 | 250
2017-04-23 | 242 | 241
2017-04-23 00:30 | 235 | 233
2017-04-23 01:00 | 230 | 228
2017-04-23 01:30 | 224 | 222
2017-04-23 02:00 | 220 | 219
2017-04-23 02:30 | 216 | 214
2017-04-23 03:00 | 215 | 213
2017-04-23 03:30 | 213 | 211
2017-04-23 04:00 | 212 | 210
2017-04-23 04:30 | 212 | 210
2017-04-23 05:00 | 212 | 210
2017-04-23 05:30 | 215 | 214
2017-04-23 06:00 | 218 | 216
2017-04-23 06:30 | 223 | 221
2017-04-23 07:00 | 225 | 223
2017-04-23 07:30 | 230 | 229
2017-04-23 08:00 | 233 | 231
2017-04-23 08:30 | 241 | 240
2017-04-23 09:00 | 251 | 250
2017-04-23 09:30 | 263 | 262
2017-04-23 10:00 | 265 | 264
2017-04-23 10:30 | 264 | 263
2017-04-23 11:00 | 265 | 264
2017-04-23 11:30 | 258 | 256
2017-04-23 12:00 | 258 | 257
2017-04-23 12:30 | 259 | 258
2017-04-23 13:00 | 255 | 254
2017-04-23 13:30 | 260 | 259
2017-04-23 14:00 | 255 | 254
2017-04-23 14:30 | 243 | 241
2017-04-23 15:00 | 241 | 239
2017-04-23 15:30 | 259 | 258
2017-04-23 16:00 | 269 | 268
2017-04-23 16:30 | 273 | 272
2017-04-23 17:00 | 271 | 270
2017-04-23 17:30 | 282 | 280
2017-04-23 18:00 | 295 | 294
2017-04-23 18:30 | 317 | 316
2017-04-23 19:00 | 328 | 327
2017-04-23 19:30 | 330 | 329
2017-04-23 20:00 | 336 | 335
2017-04-23 20:30 | 329 | 328
2017-04-23 21:00 | 318 | 317
2017-04-23 21:30 | 305 | 304
2017-04-23 22:00 | 292 | 291
2017-04-23 22:30 | 276 | 274
2017-04-23 23:00 | 263 | 262
2017-04-23 23:30 | 251 | 249
2017-04-24 | 242 | 240
2017-04-24 00:30 | 234 | 232
2017-04-24 01:00 | 228 | 226
2017-04-24 01:30 | 223 | 221
2017-04-24 02:00 | 219 | 217
2017-04-24 02:30 | 218 | 216
2017-04-24 03:00 | 217 | 215
2017-04-24 03:30 | 219 | 217
2017-04-24 04:00 | 219 | 217
2017-04-24 04:30 | 219 | 217
2017-04-24 05:00 | 223 | 221
2017-04-24 05:30 | 230 | 228
2017-04-24 06:00 | 240 | 238
2017-04-24 06:30 | 259 | 258
2017-04-24 07:00 | 283 | 282
2017-04-24 07:30 | 307 | 306
2017-04-24 08:00 | 318 | 317
2017-04-24 08:30 | 321 | 320
2017-04-24 09:00 | 319 | 318
2017-04-24 09:30 | 318 | 316
2017-04-24 10:00 | 315 | 314
2017-04-24 10:30 | 315 | 313
2017-04-24 11:00 | 314 | 313
2017-04-24 11:30 | 316 | 315
2017-04-24 12:00 | 316 | 315
2017-04-24 12:30 | 318 | 317
2017-04-24 13:00 | 316 | 314
2017-04-24 13:30 | 316 | 314
2017-04-24 14:00 | 316 | 314
2017-04-24 14:30 | 310 | 309
2017-04-24 15:00 | 309 | 308
2017-04-24 15:30 | 313 | 311
2017-04-24 16:00 | 317 | 315
2017-04-24 16:30 | 318 | 317
2017-04-24 17:00 | 314 | 313
2017-04-24 17:30 | 314 | 312
2017-04-24 18:00 | 318 | 316
2017-04-24 18:30 | 336 | 335
2017-04-24 19:00 | 356 | 355
2017-04-24 19:30 | 365 | 364
2017-04-24 20:00 | 356 | 355
2017-04-24 20:30 | 340 | 339
2017-04-24 21:00 | 329 | 328
2017-04-24 21:30 | 316 | 316
2017-04-24 22:00 | 305 | 304
2017-04-24 22:30 | 289 | 288
2017-04-24 23:00 | 277 | 276
2017-04-24 23:30 | 265 | 263
2017-04-25 | 254 | 252
2017-04-25 00:30 | 245 | 243
2017-04-25 01:00 | 238 | 236
2017-04-25 01:30 | 231 | 229
2017-04-25 02:00 | 227 | 225
2017-04-25 02:30 | 225 | 224
2017-04-25 03:00 | 222 | 220
2017-04-25 03:30 | 219 | 217
2017-04-25 04:00 | 222 | 221
2017-04-25 04:30 | 223 | 221
2017-04-25 05:00 | 226 | 224
2017-04-25 05:30 | 226 | 224
2017-04-25 06:00 | 227 | 225
2017-04-25 06:30 | 234 | 232
2017-04-25 07:00 | 239 | 238
2017-04-25 07:30 | 247 | 245
2017-04-25 08:00 | 251 | 249
2017-04-25 08:30 | 257 | 255
2017-04-25 09:00 | 258 | 257
2017-04-25 09:30 | 258 | 257
2017-04-25 10:00 | 259 | 258
2017-04-25 10:30 | 259 | 258
2017-04-25 11:00 | 261 | 260
2017-04-25 11:30 | 258 | 256
2017-04-25 12:00 | 261 | 260
2017-04-25 12:30 | 262 | 261
2017-04-25 13:00 | 261 | 260
2017-04-25 13:30 | 268 | 267
2017-04-25 14:00 | 270 | 269
2017-04-25 14:30 | 258 | 257
2017-04-25 15:00 | 257 | 256
2017-04-25 15:30 | 264 | 263
2017-04-25 16:00 | 274 | 273
2017-04-25 16:30 | 283 | 282
2017-04-25 17:00 | 280 | 279
2017-04-25 17:30 | 290 | 288
2017-04-25 18:00 | 303 | 302
2017-04-25 18:30 | 325 | 324
2017-04-25 19:00 | 351 | 349
2017-04-25 19:30 | 360 | 359
2017-04-25 20:00 | 352 | 351
2017-04-25 20:30 | 338 | 337
2017-04-25 21:00 | 326 | 324
2017-04-25 21:30 | 315 | 314
2017-04-25 22:00 | 301 | 299
2017-04-25 22:30 | 286 | 284
2017-04-25 23:00 | 272 | 270
2017-04-25 23:30 | 262 | 260
2017-04-26 | 251 | 249
2017-04-26 00:30 | 244 | 242
2017-04-26 01:00 | 236 | 234
2017-04-26 01:30 | 232 | 230
2017-04-26 02:00 | 227 | 225
2017-04-26 02:30 | 224 | 222
2017-04-26 03:00 | 223 | 221
2017-04-26 03:30 | 220 | 218
2017-04-26 04:00 | 221 | 219
2017-04-26 04:30 | 223 | 221
2017-04-26 05:00 | 227 | 225
2017-04-26 05:30 | 234 | 233
2017-04-26 06:00 | 248 | 247
2017-04-26 06:30 | 270 | 269
2017-04-26 07:00 | 294 | 293
2017-04-26 07:30 | 315 | 314
2017-04-26 08:00 | 329 | 327
2017-04-26 08:30 | 326 | 325
2017-04-26 09:00 | 320 | 319
2017-04-26 09:30 | 320 | 318
2017-04-26 10:00 | 318 | 317
2017-04-26 10:30 | 308 | 307
2017-04-26 11:00 | 279 | 277
2017-04-26 11:30 | 278 | 276
2017-04-26 12:00 | 284 | 282
2017-04-26 12:30 | 285 | 283
2017-04-26 13:00 | 289 | 287
2017-04-26 13:30 | 289 | 287
2017-04-26 14:00 | 283 | 281
2017-04-26 14:30 | 238 | 236
2017-04-26 15:00 | 236 | 234
2017-04-26 15:30 | 235 | 233
2017-04-26 16:00 | 244 | 241
2017-04-26 16:30 | 234 | 232
2017-04-26 17:00 | 184 | 182
2017-04-26 17:30 | 179 | 177
2017-04-26 18:00 | 190 | 188
2017-04-26 18:30 | 205 | 203
2017-04-26 19:00 | 211 | 209
2017-04-26 19:30 | 208 | 206
2017-04-26 20:00 | 208 | 206
2017-04-26 20:30 | 208 | 206
2017-04-26 21:00 | 208 | 206
2017-04-26 21:30 | 193 | 191
2017-04-26 22:00 | 224 | 222
2017-04-26 22:30 | 215 | 213
2017-04-26 23:00 | 198 | 196
2017-04-26 23:30 | 185 | 183
2017-04-27 | 173 | 171
2017-04-27 00:30 | 164 | 162
2017-04-27 01:00 | 159 | 156
2017-04-27 01:30 | 154 | 152
2017-04-27 02:00 | 148 | 145
2017-04-27 02:30 | 147 | 145
2017-04-27 03:00 | 143 | 140
2017-04-27 03:30 | 145 | 142
2017-04-27 04:00 | 141 | 139
2017-04-27 04:30 | 145 | 143
2017-04-27 05:00 | 147 | 145
2017-04-27 05:30 | 156 | 154
2017-04-27 06:00 | 168 | 165
2017-04-27 06:30 | 182 | 180
2017-04-27 07:00 | 182 | 180
2017-04-27 07:30 | 223 | 221
2017-04-27 08:00 | 242 | 240
2017-04-27 08:30 | 240 | 239
2017-04-27 09:00 | 235 | 233
2017-04-27 09:30 | 231 | 229
2017-04-27 10:00 | 226 | 224
2017-04-27 10:30 | 224 | 223
2017-04-27 11:00 | 227 | 226
2017-04-27 11:30 | 225 | 223
2017-04-27 12:00 | 226 | 225
2017-04-27 12:30 | 230 | 229
2017-04-27 13:00 | 233 | 232
2017-04-27 13:30 | 237 | 236
2017-04-27 14:00 | 241 | 239
2017-04-27 14:30 | 236 | 235
2017-04-27 15:00 | 236 | 235
2017-04-27 15:30 | 242 | 241
2017-04-27 16:00 | 250 | 249
2017-04-27 16:30 | 214 | 212
2017-04-27 17:00 | 194 | 193
2017-04-27 17:30 | 188 | 186
2017-04-27 18:00 | 184 | 182
2017-04-27 18:30 | 170 | 168
2017-04-27 19:00 | 219 | 218
2017-04-27 19:30 | 241 | 240
2017-04-27 20:00 | 234 | 232
2017-04-27 20:30 | 221 | 219
2017-04-27 21:00 | 211 | 209
2017-04-27 21:30 | 245 | 244
2017-04-27 22:00 | 233 | 232
2017-04-27 22:30 | 217 | 216
2017-04-27 23:00 | 200 | 198
2017-04-27 23:30 | 185 | 183
2017-04-28 | 174 | 172
2017-04-28 00:30 | 195 | 193
2017-04-28 01:00 | 239 | 237
2017-04-28 01:30 | 237 | 236
2017-04-28 02:00 | 231 | 230
2017-04-28 02:30 | 227 | 226
2017-04-28 03:00 | 224 | 223
2017-04-28 03:30 | 222 | 221
2017-04-28 04:00 | 223 | 222
2017-04-28 04:30 | 220 | 220
2017-04-28 05:00 | 224 | 224
2017-04-28 05:30 | 232 | 232
2017-04-28 06:00 | 243 | 243
2017-04-28 06:30 | 262 | 261
2017-04-28 07:00 | 266 | 265
2017-04-28 07:30 | 297 | 296
2017-04-28 08:00 | 306 | 306
2017-04-28 08:30 | 302 | 302
2017-04-28 09:00 | 293 | 293
2017-04-28 09:30 | 288 | 287
2017-04-28 10:00 | 281 | 281
2017-04-28 10:30 | 276 | 275
2017-04-28 11:00 | 271 | 271
2017-04-28 11:30 | 269 | 268
2017-04-28 12:00 | 269 | 269
2017-04-28 12:30 | 269 | 269
2017-04-28 13:00 | 272 | 272
2017-04-28 13:30 | 278 | 277
2017-04-28 14:00 | 280 | 280
2017-04-28 14:30 | 271 | 270
2017-04-28 15:00 | 270 | 269
2017-04-28 15:30 | 273 | 272
2017-04-28 16:00 | 279 | 279
2017-04-28 16:30 | 290 | 289
2017-04-28 17:00 | 301 | 300
2017-04-28 17:30 | 304 | 303
2017-04-28 18:00 | 309 | 309
2017-04-28 18:30 | 321 | 321
2017-04-28 19:00 | 330 | 329
2017-04-28 19:30 | 320 | 320
2017-04-28 20:00 | 309 | 309
2017-04-28 20:30 | 314 | 313
2017-04-28 21:00 | 306 | 305
2017-04-28 21:30 | 296 | 295
2017-04-28 22:00 | 285 | 284
2017-04-28 22:30 | 272 | 272
2017-04-28 23:00 | 259 | 258
2017-04-28 23:30 | 244 | 244
2017-04-29 | 239 | 238
2017-04-29 00:30 | 229 | 228
2017-04-29 01:00 | 222 | 222
2017-04-29 01:30 | 216 | 216
2017-04-29 02:00 | 212 | 211
2017-04-29 02:30 | 208 | 207
2017-04-29 03:00 | 203 | 203
2017-04-29 03:30 | 203 | 203
2017-04-29 04:00 | 203 | 203
2017-04-29 04:30 | 203 | 203
2017-04-29 05:00 | 203 | 203
2017-04-29 05:30 | 208 | 208
2017-04-29 06:00 | 210 | 210
2017-04-29 06:30 | 217 | 217
2017-04-29 07:00 | 225 | 225
2017-04-29 07:30 | 240 | 239
2017-04-29 08:00 | 246 | 246
2017-04-29 08:30 | 253 | 252
2017-04-29 09:00 | 253 | 253
2017-04-29 09:30 | 253 | 252
2017-04-29 10:00 | 249 | 248
2017-04-29 10:30 | 243 | 243
2017-04-29 11:00 | 241 | 240
2017-04-29 11:30 | 235 | 235
2017-04-29 12:00 | 234 | 233
2017-04-29 12:30 | 232 | 232
2017-04-29 13:00 | 230 | 230
2017-04-29 13:30 | 230 | 230
2017-04-29 14:00 | 230 | 230
2017-04-29 14:30 | 221 | 220
2017-04-29 15:00 | 220 | 220
2017-04-29 15:30 | 227 | 226
2017-04-29 16:00 | 240 | 239
2017-04-29 16:30 | 251 | 251
2017-04-29 17:00 | 266 | 265
2017-04-29 17:30 | 279 | 278
2017-04-29 18:00 | 290 | 289
2017-04-29 18:30 | 306 | 305
2017-04-29 19:00 | 313 | 312
2017-04-29 19:30 | 303 | 302
2017-04-29 20:00 | 288 | 288
2017-04-29 20:30 | 293 | 292
2017-04-29 21:00 | 288 | 287
2017-04-29 21:30 | 277 | 277
2017-04-29 22:00 | 266 | 265
2017-04-29 22:30 | 255 | 255
2017-04-29 23:00 | 246 | 246
2017-04-29 23:30 | 236 | 235
2017-04-30 | 226 | 225
2017-04-30 00:30 | 220 | 220
2017-04-30 01:00 | 215 | 215
2017-04-30 01:30 | 212 | 211
2017-04-30 02:00 | 208 | 208
2017-04-30 02:30 | 204 | 204
2017-04-30 03:00 | 204 | 203
2017-04-30 03:30 | 203 | 203
2017-04-30 04:00 | 202 | 202
2017-04-30 04:30 | 204 | 204
2017-04-30 05:00 | 204 | 204
2017-04-30 05:30 | 206 | 205
2017-04-30 06:00 | 207 | 206
2017-04-30 06:30 | 214 | 213
2017-04-30 07:00 | 218 | 217
2017-04-30 07:30 | 225 | 224
2017-04-30 08:00 | 230 | 229
2017-04-30 08:30 | 237 | 236
2017-04-30 09:00 | 240 | 239
2017-04-30 09:30 | 241 | 241
2017-04-30 10:00 | 241 | 240
2017-04-30 10:30 | 240 | 239
2017-04-30 11:00 | 240 | 239
2017-04-30 11:30 | 238 | 238
2017-04-30 12:00 | 240 | 240
2017-04-30 12:30 | 244 | 243
2017-04-30 13:00 | 249 | 249
2017-04-30 13:30 | 256 | 255
2017-04-30 14:00 | 258 | 258
2017-04-30 14:30 | 248 | 247
2017-04-30 15:00 | 241 | 240
2017-04-30 15:30 | 248 | 247
2017-04-30 16:00 | 253 | 252
2017-04-30 16:30 | 260 | 259
2017-04-30 17:00 | 269 | 269
2017-04-30 17:30 | 282 | 281
2017-04-30 18:00 | 282 | 281
2017-04-30 18:30 | 289 | 288
2017-04-30 19:00 | 319 | 319
2017-04-30 19:30 | 311 | 311
2017-04-30 20:00 | 299 | 299
2017-04-30 20:30 | 302 | 302
2017-04-30 21:00 | 297 | 296
2017-04-30 21:30 | 288 | 288
2017-04-30 22:00 | 277 | 277
2017-04-30 22:30 | 268 | 267
2017-04-30 23:00 | 259 | 258
2017-04-30 23:30 | 249 | 248
2017-05-01 | 238 | 238
2017-05-01 00:30 | 233 | 232
2017-05-01 01:00 | 226 | 226
2017-05-01 01:30 | 221 | 220
2017-05-01 02:00 | 218 | 218
2017-05-01 02:30 | 216 | 215
2017-05-01 03:00 | 212 | 211
2017-05-01 03:30 | 212 | 211
2017-05-01 04:00 | 210 | 209
2017-05-01 04:30 | 211 | 210
2017-05-01 05:00 | 211 | 210
2017-05-01 05:30 | 216 | 215
2017-05-01 06:00 | 220 | 219
2017-05-01 06:30 | 229 | 228
2017-05-01 07:00 | 232 | 232
2017-05-01 07:30 | 243 | 242
2017-05-01 08:00 | 249 | 249
2017-05-01 08:30 | 256 | 256
2017-05-01 09:00 | 260 | 259
2017-05-01 09:30 | 264 | 263
2017-05-01 10:00 | 269 | 269
2017-05-01 10:30 | 271 | 271
2017-05-01 11:00 | 269 | 269
2017-05-01 11:30 | 263 | 263
2017-05-01 12:00 | 258 | 258
2017-05-01 12:30 | 256 | 256
2017-05-01 13:00 | 258 | 258
2017-05-01 13:30 | 263 | 262
2017-05-01 14:00 | 263 | 263
2017-05-01 14:30 | 253 | 252
2017-05-01 15:00 | 251 | 251
2017-05-01 15:30 | 258 | 257
2017-05-01 16:00 | 267 | 266
2017-05-01 16:30 | 279 | 279
2017-05-01 17:00 | 288 | 288
2017-05-01 17:30 | 302 | 302
2017-05-01 18:00 | 314 | 313
2017-05-01 18:30 | 340 | 340
2017-05-01 19:00 | 345 | 345
2017-05-01 19:30 | 333 | 333
2017-05-01 20:00 | 319 | 319
2017-05-01 20:30 | 323 | 323
2017-05-01 21:00 | 315 | 314
2017-05-01 21:30 | 303 | 303
2017-05-01 22:00 | 290 | 290
2017-05-01 22:30 | 275 | 275
2017-05-01 23:00 | 265 | 264
2017-05-01 23:30 | 251 | 250
2017-05-02 | 241 | 241
2017-05-02 00:30 | 236 | 236
2017-05-02 01:00 | 230 | 229
2017-05-02 01:30 | 224 | 223
2017-05-02 02:00 | 221 | 221
2017-05-02 02:30 | 221 | 220
2017-05-02 03:00 | 218 | 217
2017-05-02 03:30 | 216 | 216
2017-05-02 04:00 | 214 | 213
2017-05-02 04:30 | 215 | 214
2017-05-02 05:00 | 219 | 218
2017-05-02 05:30 | 229 | 229
2017-05-02 06:00 | 242 | 241
2017-05-02 06:30 | 264 | 264
2017-05-02 07:00 | 262 | 261
2017-05-02 07:30 | 300 | 299
2017-05-02 08:00 | 320 | 319
2017-05-02 08:30 | 320 | 318
2017-05-02 09:00 | 317 | 316
2017-05-02 09:30 | 315 | 313
2017-05-02 10:00 | 312 | 311
2017-05-02 10:30 | 314 | 312
2017-05-02 11:00 | 314 | 313
2017-05-02 11:30 | 317 | 315
2017-05-02 12:00 | 422 | 422
2017-05-02 12:30 | 429 | 428
2017-05-02 13:00 | 430 | 429
2017-05-02 13:30 | 430 | 429
2017-05-02 14:00 | 432 | 431
2017-05-02 14:30 | 424 | 423
2017-05-02 15:00 | 422 | 421
2017-05-02 15:30 | 426 | 425
2017-05-02 16:00 | 436 | 435
2017-05-02 16:30 | 445 | 444
2017-05-02 17:00 | 451 | 450
2017-05-02 17:30 | 455 | 454
2017-05-02 18:00 | 429 | 427
2017-05-02 18:30 | 443 | 442
2017-05-02 19:00 | 476 | 475
2017-05-02 19:30 | 482 | 481
2017-05-02 20:00 | 464 | 463
2017-05-02 20:30 | 468 | 467
2017-05-02 21:00 | 455 | 454
2017-05-02 21:30 | 436 | 435
2017-05-02 22:00 | 415 | 414
2017-05-02 22:30 | 394 | 393
2017-05-02 23:00 | 373 | 371
2017-05-02 23:30 | 351 | 350
2017-05-03 | 335 | 335
2017-05-03 00:30 | 327 | 326
2017-05-03 01:00 | 316 | 316
2017-05-03 01:30 | 310 | 309
2017-05-03 02:00 | 304 | 304
2017-05-03 02:30 | 302 | 302
2017-05-03 03:00 | 299 | 298
2017-05-03 03:30 | 299 | 298
2017-05-03 04:00 | 299 | 298
2017-05-03 04:30 | 302 | 301
2017-05-03 05:00 | 307 | 306
2017-05-03 05:30 | 322 | 321
2017-05-03 06:00 | 340 | 339
2017-05-03 06:30 | 370 | 369
2017-05-03 07:00 | 354 | 353
2017-05-03 07:30 | 397 | 396
2017-05-03 08:00 | 439 | 438
2017-05-03 08:30 | 439 | 438
2017-05-03 09:00 | 433 | 432
2017-05-03 09:30 | 431 | 430
2017-05-03 10:00 | 423 | 422
2017-05-03 10:30 | 420 | 419
2017-05-03 11:00 | 377 | 376
2017-05-03 11:30 | 367 | 365
2017-05-03 12:00 | 370 | 368
2017-05-03 12:30 | 368 | 367
2017-05-03 13:00 | 379 | 378
2017-05-03 13:30 | 378 | 377
2017-05-03 14:00 | 381 | 379
2017-05-03 14:30 | 316 | 314
2017-05-03 15:00 | 301 | 299
2017-05-03 15:30 | 307 | 305
2017-05-03 16:00 | 318 | 316
2017-05-03 16:30 | 328 | 326
2017-05-03 17:00 | 339 | 337
2017-05-03 17:30 | 363 | 361
2017-05-03 18:00 | 279 | 277
2017-05-03 18:30 | 327 | 325
2017-05-03 19:00 | 404 | 404
2017-05-03 19:30 | 398 | 397
2017-05-03 20:00 | 380 | 379
2017-05-03 20:30 | 361 | 360
2017-05-03 21:00 | 341 | 340
2017-05-03 21:30 | 325 | 324
2017-05-03 22:00 | 306 | 305
2017-05-03 22:30 | 280 | 279
2017-05-03 23:00 | 258 | 257
2017-05-03 23:30 | 239 | 237
2017-05-04 | 225 | 224
2017-05-04 00:30 | 214 | 212
2017-05-04 01:00 | 202 | 200
2017-05-04 01:30 | 191 | 191
2017-05-04 02:00 | 187 | 186
2017-05-04 02:30 | 184 | 183
2017-05-04 03:00 | 181 | 180
2017-05-04 03:30 | 182 | 181
2017-05-04 04:00 | 183 | 183
2017-05-04 04:30 | 185 | 185
2017-05-04 05:00 | 189 | 188
2017-05-04 05:30 | 202 | 201
2017-05-04 06:00 | 218 | 217
2017-05-04 06:30 | 247 | 247
2017-05-04 07:00 | 249 | 248
2017-05-04 07:30 | 301 | 300
2017-05-04 08:00 | 321 | 321
2017-05-04 08:30 | 329 | 328
2017-05-04 09:00 | 321 | 321
2017-05-04 09:30 | 312 | 311
2017-05-04 10:00 | 306 | 305
2017-05-04 10:30 | 289 | 288
2017-05-04 11:00 | 285 | 284
2017-05-04 11:30 | 290 | 289
2017-05-04 12:00 | 296 | 295
2017-05-04 12:30 | 290 | 289
2017-05-04 13:00 | 296 | 295
2017-05-04 13:30 | 299 | 298
2017-05-04 14:00 | 298 | 297
2017-05-04 14:30 | 301 | 300
2017-05-04 15:00 | 316 | 315
2017-05-04 15:30 | 313 | 312
2017-05-04 16:00 | 316 | 315
2017-05-04 16:30 | 324 | 323
2017-05-04 17:00 | 330 | 330
2017-05-04 17:30 | 358 | 357
2017-05-04 18:00 | 301 | 299
2017-05-04 18:30 | 282 | 280
2017-05-04 19:00 | 313 | 312
2017-05-04 19:30 | 388 | 387
2017-05-04 20:00 | 377 | 376
2017-05-04 20:30 | 360 | 359
2017-05-04 21:00 | 343 | 342
2017-05-04 21:30 | 322 | 320
2017-05-04 22:00 | 299 | 298
2017-05-04 22:30 | 272 | 271
2017-05-04 23:00 | 257 | 256
2017-05-04 23:30 | 237 | 235
2017-05-05 | 227 | 226
2017-05-05 00:30 | 255 | 254
2017-05-05 01:00 | 318 | 317
2017-05-05 01:30 | 312 | 311
2017-05-05 02:00 | 306 | 304
2017-05-05 02:30 | 300 | 298
2017-05-05 03:00 | 300 | 298
2017-05-05 03:30 | 299 | 297
2017-05-05 04:00 | 297 | 295
2017-05-05 04:30 | 300 | 298
2017-05-05 05:00 | 308 | 306
2017-05-05 05:30 | 318 | 316
2017-05-05 06:00 | 332 | 331
2017-05-05 06:30 | 362 | 361
2017-05-05 07:00 | 392 | 391
2017-05-05 07:30 | 429 | 428
2017-05-05 08:00 | 440 | 440
2017-05-05 08:30 | 448 | 447
2017-05-05 09:00 | 444 | 443
2017-05-05 09:30 | 321 | 320
2017-05-05 10:00 | 256 | 254
2017-05-05 10:30 | 252 | 250
2017-05-05 11:00 | 249 | 248
2017-05-05 11:30 | 254 | 252
2017-05-05 12:00 | 254 | 253
2017-05-05 12:30 | 250 | 248
2017-05-05 13:00 | 255 | 253
2017-05-05 13:30 | 253 | 251
2017-05-05 14:00 | 261 | 259
2017-05-05 14:30 | 249 | 247
2017-05-05 15:00 | 242 | 240
2017-05-05 15:30 | 237 | 235
2017-05-05 16:00 | 241 | 240
2017-05-05 16:30 | 243 | 241
2017-05-05 17:00 | 248 | 246
2017-05-05 17:30 | 252 | 250
2017-05-05 18:00 | 255 | 254
2017-05-05 18:30 | 265 | 264
2017-05-05 19:00 | 268 | 266
2017-05-05 19:30 | 262 | 260
2017-05-05 20:00 | 252 | 251
2017-05-05 20:30 | 258 | 257
2017-05-05 21:00 | 253 | 252
2017-05-05 21:30 | 245 | 244
2017-05-05 22:00 | 235 | 234
2017-05-05 22:30 | 225 | 224
2017-05-05 23:00 | 217 | 215
2017-05-05 23:30 | 208 | 207
2017-05-06 | 199 | 198
2017-05-06 00:30 | 193 | 191
2017-05-06 01:00 | 186 | 184
2017-05-06 01:30 | 181 | 180
2017-05-06 02:00 | 178 | 176
2017-05-06 02:30 | 176 | 174
2017-05-06 03:00 | 175 | 173
2017-05-06 03:30 | 173 | 171
2017-05-06 04:00 | 173 | 171
2017-05-06 04:30 | 173 | 171
2017-05-06 05:00 | 173 | 171
2017-05-06 05:30 | 177 | 174
2017-05-06 06:00 | 182 | 180
2017-05-06 06:30 | 188 | 186
2017-05-06 07:00 | 194 | 192
2017-05-06 07:30 | 204 | 202
2017-05-06 08:00 | 215 | 214
2017-05-06 08:30 | 225 | 224
2017-05-06 09:00 | 230 | 228
2017-05-06 09:30 | 230 | 229
2017-05-06 10:00 | 229 | 228
2017-05-06 10:30 | 229 | 228
2017-05-06 11:00 | 224 | 223
2017-05-06 11:30 | 226 | 225
2017-05-06 12:00 | 223 | 222
2017-05-06 12:30 | 221 | 220
2017-05-06 13:00 | 219 | 217
2017-05-06 13:30 | 217 | 215
2017-05-06 14:00 | 217 | 216
2017-05-06 14:30 | 205 | 204
2017-05-06 15:00 | 207 | 205
2017-05-06 15:30 | 213 | 211
2017-05-06 16:00 | 219 | 218
2017-05-06 16:30 | 225 | 224
2017-05-06 17:00 | 231 | 229
2017-05-06 17:30 | 239 | 238
2017-05-06 18:00 | 246 | 245
2017-05-06 18:30 | 257 | 255
2017-05-06 19:00 | 259 | 257
2017-05-06 19:30 | 250 | 249
2017-05-06 20:00 | 243 | 241
2017-05-06 20:30 | 246 | 244
2017-05-06 21:00 | 240 | 239
2017-05-06 21:30 | 232 | 230
2017-05-06 22:00 | 226 | 224
2017-05-06 22:30 | 216 | 214
2017-05-06 23:00 | 207 | 206
2017-05-06 23:30 | 198 | 197
2017-05-07 | 189 | 188
2017-05-07 00:30 | 185 | 184
2017-05-07 01:00 | 181 | 180
2017-05-07 01:30 | 178 | 177
2017-05-07 02:00 | 174 | 173
2017-05-07 02:30 | 173 | 172
2017-05-07 03:00 | 170 | 169
2017-05-07 03:30 | 170 | 169
2017-05-07 04:00 | 170 | 169
2017-05-07 04:30 | 169 | 168
2017-05-07 05:00 | 169 | 167
2017-05-07 05:30 | 170 | 169
2017-05-07 06:00 | 173 | 172
2017-05-07 06:30 | 178 | 177
2017-05-07 07:00 | 182 | 181
2017-05-07 07:30 | 189 | 188
2017-05-07 08:00 | 198 | 197
2017-05-07 08:30 | 207 | 206
2017-05-07 09:00 | 211 | 210
2017-05-07 09:30 | 218 | 217
2017-05-07 10:00 | 218 | 217
2017-05-07 10:30 | 223 | 221
2017-05-07 11:00 | 219 | 218
2017-05-07 11:30 | 212 | 211
2017-05-07 12:00 | 212 | 211
2017-05-07 12:30 | 214 | 212
2017-05-07 13:00 | 219 | 218
2017-05-07 13:30 | 220 | 218
2017-05-07 14:00 | 211 | 209
2017-05-07 14:30 | 203 | 201
2017-05-07 15:00 | 203 | 201
2017-05-07 15:30 | 209 | 208
2017-05-07 16:00 | 215 | 213
2017-05-07 16:30 | 220 | 218
2017-05-07 17:00 | 228 | 226
2017-05-07 17:30 | 238 | 236
2017-05-07 18:00 | 253 | 252
2017-05-07 18:30 | 266 | 265
2017-05-07 19:00 | 269 | 268
2017-05-07 19:30 | 259 | 258
2017-05-07 20:00 | 248 | 246
2017-05-07 20:30 | 251 | 249
2017-05-07 21:00 | 245 | 244
2017-05-07 21:30 | 238 | 236
2017-05-07 22:00 | 227 | 225
2017-05-07 22:30 | 214 | 213
2017-05-07 23:00 | 203 | 202
2017-05-07 23:30 | 194 | 193
2017-05-08 | 187 | 186
2017-05-08 00:30 | 181 | 180
2017-05-08 01:00 | 177 | 175
2017-05-08 01:30 | 173 | 171
2017-05-08 02:00 | 170 | 169
2017-05-08 02:30 | 168 | 166
2017-05-08 03:00 | 167 | 165
2017-05-08 03:30 | 166 | 164
2017-05-08 04:00 | 166 | 164
2017-05-08 04:30 | 167 | 165
2017-05-08 05:00 | 169 | 167
2017-05-08 05:30 | 177 | 175
2017-05-08 06:00 | 188 | 186
2017-05-08 06:30 | 205 | 204
2017-05-08 07:00 | 217 | 216
2017-05-08 07:30 | 237 | 236
2017-05-08 08:00 | 249 | 247
2017-05-08 08:30 | 248 | 247
2017-05-08 09:00 | 243 | 241
2017-05-08 09:30 | 238 | 237
2017-05-08 10:00 | 234 | 232
2017-05-08 10:30 | 232 | 230
2017-05-08 11:00 | 229 | 227
2017-05-08 11:30 | 229 | 227
2017-05-08 12:00 | 229 | 227
2017-05-08 12:30 | 229 | 227
2017-05-08 13:00 | 236 | 234
2017-05-08 13:30 | 238 | 236
2017-05-08 14:00 | 239 | 237
2017-05-08 14:30 | 232 | 231
2017-05-08 15:00 | 233 | 232
2017-05-08 15:30 | 236 | 234
2017-05-08 16:00 | 241 | 239
2017-05-08 16:30 | 246 | 244
2017-05-08 17:00 | 249 | 247
2017-05-08 17:30 | 232 | 230
2017-05-08 18:00 | 228 | 226
2017-05-08 18:30 | 238 | 236
2017-05-08 19:00 | 250 | 248
2017-05-08 19:30 | 259 | 258
2017-05-08 20:00 | 254 | 252
2017-05-08 20:30 | 256 | 254
2017-05-08 21:00 | 255 | 254
2017-05-08 21:30 | 249 | 248
2017-05-08 22:00 | 235 | 234
2017-05-08 22:30 | 199 | 197
2017-05-08 23:00 | 193 | 191
2017-05-08 23:30 | 189 | 187
2017-05-09 | 180 | 178
2017-05-09 00:30 | 180 | 178
2017-05-09 01:00 | 176 | 174
2017-05-09 01:30 | 171 | 169
2017-05-09 02:00 | 168 | 166
2017-05-09 02:30 | 166 | 164
2017-05-09 03:00 | 165 | 163
2017-05-09 03:30 | 164 | 163
2017-05-09 04:00 | 164 | 163
2017-05-09 04:30 | 166 | 165
2017-05-09 05:00 | 170 | 168
2017-05-09 05:30 | 175 | 173
2017-05-09 06:00 | 179 | 177
2017-05-09 06:30 | 196 | 194
2017-05-09 07:00 | 201 | 199
2017-05-09 07:30 | 216 | 214
2017-05-09 08:00 | 223 | 222
2017-05-09 08:30 | 223 | 222
2017-05-09 09:00 | 237 | 236
2017-05-09 09:30 | 247 | 245
2017-05-09 10:00 | 244 | 243
2017-05-09 10:30 | 241 | 240
2017-05-09 11:00 | 235 | 234
2017-05-09 11:30 | 234 | 233
2017-05-09 12:00 | 237 | 235
2017-05-09 12:30 | 238 | 236
2017-05-09 13:00 | 237 | 236
2017-05-09 13:30 | 242 | 241
2017-05-09 14:00 | 245 | 244
2017-05-09 14:30 | 242 | 241
2017-05-09 15:00 | 241 | 239
2017-05-09 15:30 | 245 | 244
2017-05-09 16:00 | 252 | 250
2017-05-09 16:30 | 256 | 255
2017-05-09 17:00 | 259 | 258
2017-05-09 17:30 | 262 | 260
2017-05-09 18:00 | 246 | 245
2017-05-09 18:30 | 265 | 263
2017-05-09 19:00 | 280 | 279
2017-05-09 19:30 | 276 | 275
2017-05-09 20:00 | 258 | 257
2017-05-09 20:30 | 265 | 263
2017-05-09 21:00 | 266 | 265
2017-05-09 21:30 | 255 | 254
2017-05-09 22:00 | 242 | 241
2017-05-09 22:30 | 209 | 207
2017-05-09 23:00 | 191 | 189
2017-05-09 23:30 | 203 | 202
2017-05-10 | 194 | 193
2017-05-10 00:30 | 188 | 187
2017-05-10 01:00 | 183 | 181
2017-05-10 01:30 | 179 | 177
2017-05-10 02:00 | 176 | 175
2017-05-10 02:30 | 173 | 171
2017-05-10 03:00 | 171 | 170
2017-05-10 03:30 | 173 | 171
2017-05-10 04:00 | 172 | 170
2017-05-10 04:30 | 172 | 170
2017-05-10 05:00 | 175 | 173
2017-05-10 05:30 | 183 | 181
2017-05-10 06:00 | 190 | 188
2017-05-10 06:30 | 185 | 183
2017-05-10 07:00 | 195 | 193
2017-05-10 07:30 | 218 | 217
2017-05-10 08:00 | 216 | 214
2017-05-10 08:30 | 216 | 215
2017-05-10 09:00 | 221 | 219
2017-05-10 09:30 | 226 | 224
2017-05-10 10:00 | 217 | 215
2017-05-10 10:30 | 216 | 214
2017-05-10 11:00 | 198 | 197
2017-05-10 11:30 | 203 | 201
2017-05-10 12:00 | 209 | 208
2017-05-10 12:30 | 212 | 211
2017-05-10 13:00 | 214 | 213
2017-05-10 13:30 | 217 | 216
2017-05-10 14:00 | 214 | 213
2017-05-10 14:30 | 182 | 181
2017-05-10 15:00 | 165 | 164
2017-05-10 15:30 | 171 | 170
2017-05-10 16:00 | 177 | 175
2017-05-10 16:30 | 182 | 181
2017-05-10 17:00 | 148 | 146
2017-05-10 17:30 | 131 | 130
2017-05-10 18:00 | 121 | 118
2017-05-10 18:30 | 133 | 131
2017-05-10 19:00 | 138 | 136
2017-05-10 19:30 | 154 | 153
2017-05-10 20:00 | 148 | 147
2017-05-10 20:30 | 139 | 138
2017-05-10 21:00 | 158 | 157
2017-05-10 21:30 | 151 | 150
2017-05-10 22:00 | 151 | 150
2017-05-10 22:30 | 115 | 113
2017-05-10 23:00 | 129 | 128
2017-05-10 23:30 | 130 | 128
2017-05-11 | 121 | 119
2017-05-11 00:30 | 115 | 113
2017-05-11 01:00 | 108 | 107
2017-05-11 01:30 | 107 | 105
2017-05-11 02:00 | 104 | 102
2017-05-11 02:30 | 101 | 99
2017-05-11 03:00 | 100 | 98
2017-05-11 03:30 | 99 | 97
2017-05-11 04:00 | 99 | 97
2017-05-11 04:30 | 101 | 99
2017-05-11 05:00 | 104 | 102
2017-05-11 05:30 | 110 | 108
2017-05-11 06:00 | 120 | 118
2017-05-11 06:30 | 139 | 137
2017-05-11 07:00 | 153 | 152
2017-05-11 07:30 | 173 | 172
2017-05-11 08:00 | 179 | 178
2017-05-11 08:30 | 177 | 176
2017-05-11 09:00 | 171 | 170
2017-05-11 09:30 | 164 | 163
2017-05-11 10:00 | 158 | 157
2017-05-11 10:30 | 155 | 154
2017-05-11 11:00 | 152 | 151
2017-05-11 11:30 | 152 | 151
2017-05-11 12:00 | 153 | 152
2017-05-11 12:30 | 152 | 151
2017-05-11 13:00 | 152 | 151
2017-05-11 13:30 | 156 | 155
2017-05-11 14:00 | 160 | 159
2017-05-11 14:30 | 154 | 153
2017-05-11 15:00 | 148 | 147
2017-05-11 15:30 | 152 | 151
2017-05-11 16:00 | 161 | 160
2017-05-11 16:30 | 166 | 165
2017-05-11 17:00 | 164 | 163
2017-05-11 17:30 | 140 | 139
2017-05-11 18:00 | 118 | 116
2017-05-11 18:30 | 130 | 129
2017-05-11 19:00 | 136 | 135
2017-05-11 19:30 | 128 | 127
2017-05-11 20:00 | 119 | 117
2017-05-11 20:30 | 123 | 121
2017-05-11 21:00 | 163 | 162
2017-05-11 21:30 | 157 | 155
2017-05-11 22:00 | 142 | 140
2017-05-11 22:30 | 130 | 128
2017-05-11 23:00 | 121 | 119
2017-05-11 23:30 | 117 | 115
2017-05-12 | 114 | 112
2017-05-12 00:30 | 137 | 136
2017-05-12 01:00 | 173 | 172
2017-05-12 01:30 | 169 | 168
2017-05-12 02:00 | 167 | 166
2017-05-12 02:30 | 167 | 166
2017-05-12 03:00 | 167 | 166
2017-05-12 03:30 | 164 | 163
2017-05-12 04:00 | 146 | 145
2017-05-12 04:30 | 141 | 139
2017-05-12 05:00 | 143 | 141
2017-05-12 05:30 | 150 | 148
2017-05-12 06:00 | 158 | 157
2017-05-12 06:30 | 175 | 173
2017-05-12 07:00 | 208 | 207
2017-05-12 07:30 | 224 | 223
2017-05-12 08:00 | 219 | 218
2017-05-12 08:30 | 230 | 229
2017-05-12 09:00 | 233 | 232
2017-05-12 09:30 | 225 | 224
2017-05-12 10:00 | 212 | 210
2017-05-12 10:30 | 209 | 207
2017-05-12 11:00 | 224 | 222
2017-05-12 11:30 | 236 | 235
2017-05-12 12:00 | 237 | 236
2017-05-12 12:30 | 241 | 239
2017-05-12 13:00 | 243 | 241
2017-05-12 13:30 | 231 | 229
2017-05-12 14:00 | 235 | 233
2017-05-12 14:30 | 205 | 203
2017-05-12 15:00 | 196 | 193
2017-05-12 15:30 | 197 | 194
2017-05-12 16:00 | 198 | 195
2017-05-12 16:30 | 205 | 202
2017-05-12 17:00 | 214 | 212
2017-05-12 17:30 | 218 | 216
2017-05-12 18:00 | 223 | 220
2017-05-12 18:30 | 233 | 231
2017-05-12 19:00 | 235 | 233
2017-05-12 19:30 | 237 | 235
2017-05-12 20:00 | 243 | 242
2017-05-12 20:30 | 247 | 245
2017-05-12 21:00 | 243 | 242
2017-05-12 21:30 | 234 | 233
2017-05-12 22:00 | 227 | 225
2017-05-12 22:30 | 198 | 196
2017-05-12 23:00 | 202 | 200
2017-05-12 23:30 | 200 | 198
2017-05-13 | 194 | 192
2017-05-13 00:30 | 188 | 187
2017-05-13 01:00 | 182 | 180
2017-05-13 01:30 | 177 | 175
2017-05-13 02:00 | 174 | 172
2017-05-13 02:30 | 172 | 170
2017-05-13 03:00 | 171 | 169
2017-05-13 03:30 | 168 | 166
2017-05-13 04:00 | 167 | 165
2017-05-13 04:30 | 170 | 167
2017-05-13 05:00 | 170 | 168
2017-05-13 05:30 | 173 | 171
2017-05-13 06:00 | 175 | 173
2017-05-13 06:30 | 184 | 182
2017-05-13 07:00 | 189 | 187
2017-05-13 07:30 | 198 | 196
2017-05-13 08:00 | 189 | 187
2017-05-13 08:30 | 199 | 197
2017-05-13 09:00 | 203 | 201
2017-05-13 09:30 | 201 | 199
2017-05-13 10:00 | 198 | 196
2017-05-13 10:30 | 197 | 195
2017-05-13 11:00 | 196 | 194
2017-05-13 11:30 | 193 | 191
2017-05-13 12:00 | 209 | 207
2017-05-13 12:30 | 217 | 216
2017-05-13 13:00 | 210 | 209
2017-05-13 13:30 | 206 | 205
2017-05-13 14:00 | 206 | 205
2017-05-13 14:30 | 197 | 195
2017-05-13 15:00 | 194 | 193
2017-05-13 15:30 | 201 | 200
2017-05-13 16:00 | 203 | 202
2017-05-13 16:30 | 215 | 214
2017-05-13 17:00 | 205 | 203
2017-05-13 17:30 | 205 | 203
2017-05-13 18:00 | 212 | 210
2017-05-13 18:30 | 225 | 224
2017-05-13 19:00 | 227 | 226
2017-05-13 19:30 | 236 | 235
2017-05-13 20:00 | 237 | 236
2017-05-13 20:30 | 241 | 240
2017-05-13 21:00 | 238 | 237
2017-05-13 21:30 | 231 | 229
2017-05-13 22:00 | 223 | 222
2017-05-13 22:30 | 214 | 212
2017-05-13 23:00 | 206 | 205
2017-05-13 23:30 | 198 | 197
2017-05-14 | 190 | 188
2017-05-14 00:30 | 183 | 182
2017-05-14 01:00 | 179 | 177
2017-05-14 01:30 | 174 | 173
2017-05-14 02:00 | 170 | 169
2017-05-14 02:30 | 168 | 166
2017-05-14 03:00 | 165 | 163
2017-05-14 03:30 | 165 | 163
2017-05-14 04:00 | 166 | 165
2017-05-14 04:30 | 166 | 165
2017-05-14 05:00 | 166 | 165
2017-05-14 05:30 | 167 | 165
2017-05-14 06:00 | 170 | 169
2017-05-14 06:30 | 175 | 174
2017-05-14 07:00 | 180 | 179
2017-05-14 07:30 | 187 | 186
2017-05-14 08:00 | 193 | 192
2017-05-14 08:30 | 196 | 195
2017-05-14 09:00 | 195 | 194
2017-05-14 09:30 | 208 | 207
2017-05-14 10:00 | 205 | 204
2017-05-14 10:30 | 210 | 209
2017-05-14 11:00 | 211 | 211
2017-05-14 11:30 | 208 | 207
2017-05-14 12:00 | 203 | 203
2017-05-14 12:30 | 199 | 198
2017-05-14 13:00 | 188 | 187
2017-05-14 13:30 | 196 | 196
2017-05-14 14:00 | 198 | 197
2017-05-14 14:30 | 192 | 192
2017-05-14 15:00 | 192 | 191
2017-05-14 15:30 | 198 | 197
2017-05-14 16:00 | 208 | 207
2017-05-14 16:30 | 215 | 215
2017-05-14 17:00 | 224 | 224
2017-05-14 17:30 | 234 | 234
2017-05-14 18:00 | 225 | 224
2017-05-14 18:30 | 257 | 256
2017-05-14 19:00 | 267 | 266
2017-05-14 19:30 | 259 | 258
2017-05-14 20:00 | 249 | 248
2017-05-14 20:30 | 250 | 249
2017-05-14 21:00 | 245 | 244
2017-05-14 21:30 | 239 | 238
2017-05-14 22:00 | 227 | 226
2017-05-14 22:30 | 217 | 216
2017-05-14 23:00 | 206 | 205
2017-05-14 23:30 | 195 | 194
2017-05-15 | 188 | 187
2017-05-15 00:30 | 183 | 182
2017-05-15 01:00 | 179 | 178
2017-05-15 01:30 | 175 | 174
2017-05-15 02:00 | 170 | 169
2017-05-15 02:30 | 169 | 168
2017-05-15 03:00 | 168 | 166
2017-05-15 03:30 | 169 | 167
2017-05-15 04:00 | 169 | 167
2017-05-15 04:30 | 170 | 169
2017-05-15 05:00 | 172 | 171
2017-05-15 05:30 | 178 | 177
2017-05-15 06:00 | 189 | 188
2017-05-15 06:30 | 207 | 206
2017-05-15 07:00 | 204 | 203
2017-05-15 07:30 | 231 | 230
2017-05-15 08:00 | 224 | 222
2017-05-15 08:30 | 240 | 239
2017-05-15 09:00 | 242 | 241
2017-05-15 09:30 | 233 | 232
2017-05-15 10:00 | 233 | 232
2017-05-15 10:30 | 234 | 233
2017-05-15 11:00 | 221 | 220
2017-05-15 11:30 | 223 | 222
2017-05-15 12:00 | 223 | 222
2017-05-15 12:30 | 233 | 233
2017-05-15 13:00 | 237 | 236
2017-05-15 13:30 | 223 | 222
2017-05-15 14:00 | 230 | 229
2017-05-15 14:30 | 210 | 209
2017-05-15 15:00 | 222 | 221
2017-05-15 15:30 | 215 | 213
2017-05-15 16:00 | 232 | 230
2017-05-15 16:30 | 227 | 226
2017-05-15 17:00 | 225 | 223
2017-05-15 17:30 | 228 | 226
2017-05-15 18:00 | 235 | 233
2017-05-15 18:30 | 250 | 249
2017-05-15 19:00 | 266 | 265
2017-05-15 19:30 | 279 | 278
2017-05-15 20:00 | 274 | 273
2017-05-15 20:30 | 262 | 261
2017-05-15 21:00 | 250 | 249
2017-05-15 21:30 | 243 | 242
2017-05-15 22:00 | 229 | 227
2017-05-15 22:30 | 194 | 193
2017-05-15 23:00 | 197 | 196
2017-05-15 23:30 | 193 | 192
2017-05-16 | 184 | 183
2017-05-16 00:30 | 179 | 178
2017-05-16 01:00 | 175 | 173
2017-05-16 01:30 | 170 | 169
2017-05-16 02:00 | 167 | 166
2017-05-16 02:30 | 166 | 165
2017-05-16 03:00 | 166 | 165
2017-05-16 03:30 | 165 | 164
2017-05-16 04:00 | 162 | 162
2017-05-16 04:30 | 165 | 164
2017-05-16 05:00 | 167 | 167
2017-05-16 05:30 | 175 | 174
2017-05-16 06:00 | 184 | 184
2017-05-16 06:30 | 188 | 187
2017-05-16 07:00 | 183 | 182
2017-05-16 07:30 | 209 | 208
2017-05-16 08:00 | 215 | 215
2017-05-16 08:30 | 233 | 232
2017-05-16 09:00 | 228 | 227
2017-05-16 09:30 | 174 | 148
2017-05-16 10:00 | 180 | 154
2017-05-16 10:30 | 178 | 152
2017-05-16 11:00 | 178 | 151
2017-05-16 11:30 | 177 | 150
2017-05-16 12:00 | 178 | 151
2017-05-16 12:30 | 178 | 152
2017-05-16 13:00 | 178 | 152
2017-05-16 13:30 | 180 | 154
2017-05-16 14:00 | 181 | 155
2017-05-16 14:30 | 190 | 184
2017-05-16 15:00 | 230 | 226
2017-05-16 15:30 | 235 | 231
2017-05-16 16:00 | 232 | 228
2017-05-16 16:30 | 240 | 236
2017-05-16 17:00 | 248 | 244
2017-05-16 17:30 | 258 | 254
2017-05-16 18:00 | 239 | 235
2017-05-16 18:30 | 261 | 259
2017-05-16 19:00 | 273 | 269
2017-05-16 19:30 | 279 | 276
2017-05-16 20:00 | 275 | 272
2017-05-16 20:30 | 248 | 243
2017-05-16 21:00 | 233 | 229
2017-05-16 21:30 | 222 | 217
2017-05-16 22:00 | 221 | 217
2017-05-16 22:30 | 201 | 196
2017-05-16 23:00 | 185 | 180
2017-05-16 23:30 | 173 | 170
2017-05-17 | 177 | 176
2017-05-17 00:30 | 176 | 175
2017-05-17 01:00 | 172 | 170
2017-05-17 01:30 | 168 | 166
2017-05-17 02:00 | 168 | 166
2017-05-17 02:30 | 166 | 165
2017-05-17 03:00 | 165 | 163
2017-05-17 03:30 | 165 | 163
2017-05-17 04:00 | 163 | 162
2017-05-17 04:30 | 166 | 164
2017-05-17 05:00 | 171 | 169
2017-05-17 05:30 | 161 | 159
2017-05-17 06:00 | 164 | 162
2017-05-17 06:30 | 182 | 180
2017-05-17 07:00 | 199 | 197
2017-05-17 07:30 | 226 | 224
2017-05-17 08:00 | 227 | 225
2017-05-17 08:30 | 245 | 242
2017-05-17 09:00 | 245 | 242
2017-05-17 09:30 | 254 | 252
2017-05-17 10:00 | 254 | 250
2017-05-17 10:30 | 254 | 250
2017-05-17 11:00 | 227 | 223
2017-05-17 11:30 | 225 | 222
2017-05-17 12:00 | 219 | 216
2017-05-17 12:30 | 229 | 226
2017-05-17 13:00 | 225 | 221
2017-05-17 13:30 | 239 | 236
2017-05-17 14:00 | 232 | 228
2017-05-17 14:30 | 222 | 217
2017-05-17 15:00 | 224 | 220
2017-05-17 15:30 | 223 | 219
2017-05-17 16:00 | 225 | 221
2017-05-17 16:30 | 228 | 224
2017-05-17 17:00 | 221 | 217
2017-05-17 17:30 | 225 | 222
2017-05-17 18:00 | 250 | 247
2017-05-17 18:30 | 264 | 262
2017-05-17 19:00 | 268 | 265
2017-05-17 19:30 | 258 | 256
2017-05-17 20:00 | 250 | 247
2017-05-17 20:30 | 241 | 238
2017-05-17 21:00 | 230 | 227
2017-05-17 21:30 | 224 | 221
2017-05-17 22:00 | 209 | 207
2017-05-17 22:30 | 198 | 196
2017-05-17 23:00 | 186 | 183
2017-05-17 23:30 | 178 | 175
2017-05-18 | 169 | 166
2017-05-18 00:30 | 163 | 160
2017-05-18 01:00 | 156 | 154
2017-05-18 01:30 | 154 | 151
2017-05-18 02:00 | 151 | 148
2017-05-18 02:30 | 163 | 161
2017-05-18 03:00 | 166 | 164
2017-05-18 03:30 | 166 | 164
2017-05-18 04:00 | 165 | 163
2017-05-18 04:30 | 166 | 164
2017-05-18 05:00 | 168 | 167
2017-05-18 05:30 | 174 | 172
2017-05-18 06:00 | 167 | 164
2017-05-18 06:30 | 175 | 173
2017-05-18 07:00 | 190 | 188
2017-05-18 07:30 | 208 | 206
2017-05-18 08:00 | 227 | 225
2017-05-18 08:30 | 229 | 226
2017-05-18 09:00 | 226 | 223
2017-05-18 09:30 | 233 | 231
2017-05-18 10:00 | 234 | 231
2017-05-18 10:30 | 235 | 232
2017-05-18 11:00 | 235 | 232
2017-05-18 11:30 | 235 | 232
2017-05-18 12:00 | 233 | 230
2017-05-18 12:30 | 233 | 230
2017-05-18 13:00 | 234 | 231
2017-05-18 13:30 | 233 | 230
2017-05-18 14:00 | 239 | 236
2017-05-18 14:30 | 233 | 230
2017-05-18 15:00 | 219 | 216
2017-05-18 15:30 | 219 | 215
2017-05-18 16:00 | 219 | 215
2017-05-18 16:30 | 213 | 210
2017-05-18 17:00 | 215 | 212
2017-05-18 17:30 | 219 | 216
2017-05-18 18:00 | 238 | 235
2017-05-18 18:30 | 254 | 251
2017-05-18 19:00 | 255 | 253
2017-05-18 19:30 | 246 | 244
2017-05-18 20:00 | 235 | 233
2017-05-18 20:30 | 244 | 242
2017-05-18 21:00 | 246 | 244
2017-05-18 21:30 | 239 | 236
2017-05-18 22:00 | 226 | 224
2017-05-18 22:30 | 215 | 213
2017-05-18 23:00 | 179 | 176
2017-05-18 23:30 | 170 | 167
2017-05-19 | 174 | 172
2017-05-19 00:30 | 181 | 179
2017-05-19 01:00 | 176 | 174
2017-05-19 01:30 | 172 | 170
2017-05-19 02:00 | 170 | 167
2017-05-19 02:30 | 168 | 166
2017-05-19 03:00 | 168 | 166
2017-05-19 03:30 | 167 | 165
2017-05-19 04:00 | 165 | 163
2017-05-19 04:30 | 167 | 164
2017-05-19 05:00 | 168 | 166
2017-05-19 05:30 | 171 | 169
2017-05-19 06:00 | 182 | 180
2017-05-19 06:30 | 185 | 183
2017-05-19 07:00 | 199 | 197
2017-05-19 07:30 | 233 | 231
2017-05-19 08:00 | 240 | 238
2017-05-19 08:30 | 245 | 243
2017-05-19 09:00 | 245 | 243
2017-05-19 09:30 | 241 | 239
2017-05-19 10:00 | 238 | 236
2017-05-19 10:30 | 234 | 231
2017-05-19 11:00 | 229 | 227
2017-05-19 11:30 | 189 | 187
2017-05-19 12:00 | 176 | 173
2017-05-19 12:30 | 176 | 174
2017-05-19 13:00 | 176 | 174
2017-05-19 13:30 | 203 | 201
2017-05-19 14:00 | 210 | 208
2017-05-19 14:30 | 198 | 196
2017-05-19 15:00 | 195 | 192
2017-05-19 15:30 | 193 | 191
2017-05-19 16:00 | 187 | 185
2017-05-19 16:30 | 191 | 189
2017-05-19 17:00 | 195 | 193
2017-05-19 17:30 | 199 | 197
2017-05-19 18:00 | 207 | 205
2017-05-19 18:30 | 218 | 216
2017-05-19 19:00 | 226 | 224
2017-05-19 19:30 | 224 | 222
2017-05-19 20:00 | 214 | 212
2017-05-19 20:30 | 218 | 216
2017-05-19 21:00 | 211 | 210
2017-05-19 21:30 | 201 | 199
2017-05-19 22:00 | 198 | 196
2017-05-19 22:30 | 178 | 176
2017-05-19 23:00 | 165 | 163
2017-05-19 23:30 | 157 | 154
2017-05-20 | 155 | 153
2017-05-20 00:30 | 154 | 152
2017-05-20 01:00 | 150 | 148
2017-05-20 01:30 | 152 | 150
2017-05-20 02:00 | 148 | 146
2017-05-20 02:30 | 147 | 145
2017-05-20 03:00 | 144 | 141
2017-05-20 03:30 | 144 | 141
2017-05-20 04:00 | 140 | 138
2017-05-20 04:30 | 127 | 124
2017-05-20 05:00 | 128 | 125
2017-05-20 05:30 | 130 | 128
2017-05-20 06:00 | 133 | 131
2017-05-20 06:30 | 140 | 138
2017-05-20 07:00 | 147 | 145
2017-05-20 07:30 | 157 | 155
2017-05-20 08:00 | 164 | 162
2017-05-20 08:30 | 178 | 176
2017-05-20 09:00 | 183 | 181
2017-05-20 09:30 | 184 | 182
2017-05-20 10:00 | 182 | 180
2017-05-20 10:30 | 179 | 177
2017-05-20 11:00 | 176 | 175
2017-05-20 11:30 | 171 | 170
2017-05-20 12:00 | 171 | 169
2017-05-20 12:30 | 169 | 167
2017-05-20 13:00 | 171 | 169
2017-05-20 13:30 | 169 | 167
2017-05-20 14:00 | 167 | 165
2017-05-20 14:30 | 161 | 159
2017-05-20 15:00 | 160 | 158
2017-05-20 15:30 | 165 | 163
2017-05-20 16:00 | 169 | 167
2017-05-20 16:30 | 178 | 176
2017-05-20 17:00 | 185 | 183
2017-05-20 17:30 | 191 | 189
2017-05-20 18:00 | 200 | 198
2017-05-20 18:30 | 214 | 213
2017-05-20 19:00 | 217 | 216
2017-05-20 19:30 | 209 | 207
2017-05-20 20:00 | 198 | 196
2017-05-20 20:30 | 202 | 200
2017-05-20 21:00 | 199 | 197
2017-05-20 21:30 | 191 | 189
2017-05-20 22:00 | 184 | 181
2017-05-20 22:30 | 174 | 172
2017-05-20 23:00 | 164 | 162
2017-05-20 23:30 | 157 | 154
2017-05-21 | 151 | 149
2017-05-21 00:30 | 146 | 143
2017-05-21 01:00 | 139 | 137
2017-05-21 01:30 | 134 | 132
2017-05-21 02:00 | 132 | 129
2017-05-21 02:30 | 129 | 126
2017-05-21 03:00 | 126 | 124
2017-05-21 03:30 | 126 | 124
2017-05-21 04:00 | 125 | 123
2017-05-21 04:30 | 126 | 124
2017-05-21 05:00 | 126 | 124
2017-05-21 05:30 | 128 | 126
2017-05-21 06:00 | 128 | 126
2017-05-21 06:30 | 135 | 134
2017-05-21 07:00 | 139 | 137
2017-05-21 07:30 | 146 | 144
2017-05-21 08:00 | 153 | 151
2017-05-21 08:30 | 160 | 158
2017-05-21 09:00 | 164 | 163
2017-05-21 09:30 | 167 | 165
2017-05-21 10:00 | 167 | 165
2017-05-21 10:30 | 170 | 168
2017-05-21 11:00 | 167 | 165
2017-05-21 11:30 | 165 | 163
2017-05-21 12:00 | 163 | 162
2017-05-21 12:30 | 165 | 164
2017-05-21 13:00 | 166 | 165
2017-05-21 13:30 | 163 | 162
2017-05-21 14:00 | 161 | 160
2017-05-21 14:30 | 156 | 154
2017-05-21 15:00 | 155 | 153
2017-05-21 15:30 | 158 | 156
2017-05-21 16:00 | 167 | 165
2017-05-21 16:30 | 175 | 174
2017-05-21 17:00 | 184 | 183
2017-05-21 17:30 | 194 | 193
2017-05-21 18:00 | 207 | 206
2017-05-21 18:30 | 224 | 223
2017-05-21 19:00 | 230 | 228
2017-05-21 19:30 | 219 | 218
2017-05-21 20:00 | 207 | 205
2017-05-21 20:30 | 207 | 206
2017-05-21 21:00 | 204 | 202
2017-05-21 21:30 | 195 | 193
2017-05-21 22:00 | 186 | 184
2017-05-21 22:30 | 174 | 172
2017-05-21 23:00 | 164 | 162
2017-05-21 23:30 | 156 | 153
2017-05-22 | 147 | 144
2017-05-22 00:30 | 142 | 139
2017-05-22 01:00 | 137 | 135
2017-05-22 01:30 | 134 | 132
2017-05-22 02:00 | 132 | 130
2017-05-22 02:30 | 129 | 127
2017-05-22 03:00 | 129 | 127
2017-05-22 03:30 | 129 | 127
2017-05-22 04:00 | 129 | 127
2017-05-22 04:30 | 132 | 130
2017-05-22 05:00 | 136 | 134
2017-05-22 05:30 | 141 | 139
2017-05-22 06:00 | 149 | 147
2017-05-22 06:30 | 168 | 166
2017-05-22 07:00 | 184 | 183
2017-05-22 07:30 | 204 | 203
2017-05-22 08:00 | 214 | 213
2017-05-22 08:30 | 214 | 213
2017-05-22 09:00 | 208 | 207
2017-05-22 09:30 | 204 | 203
2017-05-22 10:00 | 201 | 199
2017-05-22 10:30 | 199 | 198
2017-05-22 11:00 | 196 | 194
2017-05-22 11:30 | 195 | 194
2017-05-22 12:00 | 196 | 195
2017-05-22 12:30 | 201 | 200
2017-05-22 13:00 | 201 | 200
2017-05-22 13:30 | 204 | 203
2017-05-22 14:00 | 207 | 206
2017-05-22 14:30 | 203 | 202
2017-05-22 15:00 | 204 | 203
2017-05-22 15:30 | 209 | 207
2017-05-22 16:00 | 211 | 210
2017-05-22 16:30 | 218 | 217
2017-05-22 17:00 | 222 | 221
2017-05-22 17:30 | 226 | 224
2017-05-22 18:00 | 233 | 232
2017-05-22 18:30 | 246 | 245
2017-05-22 19:00 | 252 | 251
2017-05-22 19:30 | 243 | 242
2017-05-22 20:00 | 232 | 230
2017-05-22 20:30 | 232 | 231
2017-05-22 21:00 | 223 | 222
2017-05-22 21:30 | 216 | 215
2017-05-22 22:00 | 205 | 203
2017-05-22 22:30 | 190 | 188
2017-05-22 23:00 | 179 | 177
2017-05-22 23:30 | 170 | 168
2017-05-23 | 164 | 163
2017-05-23 00:30 | 162 | 160
2017-05-23 01:00 | 158 | 156
2017-05-23 01:30 | 157 | 156
2017-05-23 02:00 | 158 | 157
2017-05-23 02:30 | 157 | 155
2017-05-23 03:00 | 157 | 155
2017-05-23 03:30 | 157 | 155
2017-05-23 04:00 | 157 | 155
2017-05-23 04:30 | 159 | 157
2017-05-23 05:00 | 162 | 161
2017-05-23 05:30 | 171 | 170
2017-05-23 06:00 | 182 | 181
2017-05-23 06:30 | 202 | 201
2017-05-23 07:00 | 203 | 202
2017-05-23 07:30 | 234 | 233
2017-05-23 08:00 | 252 | 250
2017-05-23 08:30 | 256 | 255
2017-05-23 09:00 | 252 | 251
2017-05-23 09:30 | 246 | 245
2017-05-23 10:00 | 243 | 242
2017-05-23 10:30 | 235 | 233
2017-05-23 11:00 | 216 | 214
2017-05-23 11:30 | 206 | 205
2017-05-23 12:00 | 206 | 205
2017-05-23 12:30 | 205 | 203
2017-05-23 13:00 | 205 | 204
2017-05-23 13:30 | 208 | 206
2017-05-23 14:00 | 211 | 209
2017-05-23 14:30 | 187 | 185
2017-05-23 15:00 | 163 | 160
2017-05-23 15:30 | 171 | 168
2017-05-23 16:00 | 174 | 172
2017-05-23 16:30 | 177 | 175
2017-05-23 17:00 | 182 | 180
2017-05-23 17:30 | 156 | 153
2017-05-23 18:00 | 142 | 140
2017-05-23 18:30 | 156 | 154
2017-05-23 19:00 | 163 | 161
2017-05-23 19:30 | 187 | 186
2017-05-23 20:00 | 186 | 184
2017-05-23 20:30 | 187 | 185
2017-05-23 21:00 | 164 | 163
2017-05-23 21:30 | 170 | 168
2017-05-23 22:00 | 159 | 158
2017-05-23 22:30 | 147 | 145
2017-05-23 23:00 | 134 | 132
2017-05-23 23:30 | 122 | 119
2017-05-24 | 112 | 109
2017-05-24 00:30 | 106 | 103
2017-05-24 01:00 | 101 | 98
2017-05-24 01:30 | 98 | 96
2017-05-24 02:00 | 93 | 91
2017-05-24 02:30 | 90 | 88
2017-05-24 03:00 | 89 | 88
2017-05-24 03:30 | 89 | 88
2017-05-24 04:00 | 89 | 88
2017-05-24 04:30 | 89 | 88
2017-05-24 05:00 | 94 | 92
2017-05-24 05:30 | 102 | 100
2017-05-24 06:00 | 112 | 110
2017-05-24 06:30 | 130 | 129
2017-05-24 07:00 | 148 | 147
2017-05-24 07:30 | 168 | 167
2017-05-24 08:00 | 171 | 170
2017-05-24 08:30 | 168 | 167
2017-05-24 09:00 | 172 | 171
2017-05-24 09:30 | 167 | 166
2017-05-24 10:00 | 161 | 160
2017-05-24 10:30 | 158 | 157
2017-05-24 11:00 | 157 | 155
2017-05-24 11:30 | 153 | 151
2017-05-24 12:00 | 154 | 153
2017-05-24 12:30 | 156 | 154
2017-05-24 13:00 | 160 | 159
2017-05-24 13:30 | 162 | 161
2017-05-24 14:00 | 163 | 162
2017-05-24 14:30 | 156 | 155
2017-05-24 15:00 | 155 | 153
2017-05-24 15:30 | 156 | 154
2017-05-24 16:00 | 160 | 158
2017-05-24 16:30 | 166 | 165
2017-05-24 17:00 | 167 | 165
2017-05-24 17:30 | 155 | 153
2017-05-24 18:00 | 138 | 137
2017-05-24 18:30 | 182 | 181
2017-05-24 19:00 | 183 | 182
2017-05-24 19:30 | 200 | 199
2017-05-24 20:00 | 195 | 194
2017-05-24 20:30 | 184 | 183
2017-05-24 21:00 | 175 | 173
2017-05-24 21:30 | 165 | 164
2017-05-24 22:00 | 154 | 153
2017-05-24 22:30 | 126 | 124
2017-05-24 23:00 | 103 | 101
2017-05-24 23:30 | 107 | 104
2017-05-25 | 106 | 104
2017-05-25 00:30 | 124 | 122
2017-05-25 01:00 | 159 | 157
2017-05-25 01:30 | 158 | 156
2017-05-25 02:00 | 155 | 154
2017-05-25 02:30 | 153 | 152
2017-05-25 03:00 | 152 | 151
2017-05-25 03:30 | 153 | 151
2017-05-25 04:00 | 151 | 149
2017-05-25 04:30 | 152 | 151
2017-05-25 05:00 | 155 | 153
2017-05-25 05:30 | 160 | 158
2017-05-25 06:00 | 172 | 170
2017-05-25 06:30 | 173 | 172
2017-05-25 07:00 | 184 | 182
2017-05-25 07:30 | 201 | 199
2017-05-25 08:00 | 206 | 205
2017-05-25 08:30 | 219 | 218
2017-05-25 09:00 | 224 | 223
2017-05-25 09:30 | 218 | 217
2017-05-25 10:00 | 213 | 211
2017-05-25 10:30 | 209 | 208
2017-05-25 11:00 | 209 | 207
2017-05-25 11:30 | 206 | 205
2017-05-25 12:00 | 206 | 205
2017-05-25 12:30 | 206 | 205
2017-05-25 13:00 | 212 | 211
2017-05-25 13:30 | 217 | 215
2017-05-25 14:00 | 218 | 217
2017-05-25 14:30 | 209 | 207
2017-05-25 15:00 | 208 | 206
2017-05-25 15:30 | 212 | 211
2017-05-25 16:00 | 219 | 217
2017-05-25 16:30 | 226 | 224
2017-05-25 17:00 | 231 | 230
2017-05-25 17:30 | 217 | 215
2017-05-25 18:00 | 219 | 217
2017-05-25 18:30 | 235 | 232
2017-05-25 19:00 | 241 | 239
2017-05-25 19:30 | 245 | 242
2017-05-25 20:00 | 239 | 236
2017-05-25 20:30 | 230 | 228
2017-05-25 21:00 | 218 | 216
2017-05-25 21:30 | 206 | 204
2017-05-25 22:00 | 194 | 192
2017-05-25 22:30 | 180 | 177
2017-05-25 23:00 | 170 | 168
2017-05-25 23:30 | 159 | 157
2017-05-26 | 150 | 147
2017-05-26 00:30 | 145 | 143
2017-05-26 01:00 | 140 | 137
2017-05-26 01:30 | 136 | 133
2017-05-26 02:00 | 150 | 148
2017-05-26 02:30 | 151 | 149
2017-05-26 03:00 | 151 | 149
2017-05-26 03:30 | 148 | 147
2017-05-26 04:00 | 150 | 148
2017-05-26 04:30 | 152 | 150
2017-05-26 05:00 | 155 | 153
2017-05-26 05:30 | 159 | 158
2017-05-26 06:00 | 170 | 169
2017-05-26 06:30 | 172 | 170
2017-05-26 07:00 | 185 | 183
2017-05-26 07:30 | 201 | 200
2017-05-26 08:00 | 206 | 205
2017-05-26 08:30 | 221 | 220
2017-05-26 09:00 | 226 | 224
2017-05-26 09:30 | 222 | 221
2017-05-26 10:00 | 218 | 216
2017-05-26 10:30 | 218 | 216
2017-05-26 11:00 | 217 | 215
2017-05-26 11:30 | 217 | 215
2017-05-26 12:00 | 218 | 217
2017-05-26 12:30 | 223 | 221
2017-05-26 13:00 | 224 | 222
2017-05-26 13:30 | 221 | 219
2017-05-26 14:00 | 220 | 218
2017-05-26 14:30 | 214 | 212
2017-05-26 15:00 | 213 | 211
2017-05-26 15:30 | 214 | 212
2017-05-26 16:00 | 220 | 218
2017-05-26 16:30 | 226 | 224
2017-05-26 17:00 | 234 | 231
2017-05-26 17:30 | 216 | 214
2017-05-26 18:00 | 215 | 212
2017-05-26 18:30 | 245 | 243
2017-05-26 19:00 | 267 | 266
2017-05-26 19:30 | 265 | 264
2017-05-26 20:00 | 254 | 253
2017-05-26 20:30 | 248 | 247
2017-05-26 21:00 | 242 | 240
2017-05-26 21:30 | 232 | 230
2017-05-26 22:00 | 224 | 222
2017-05-26 22:30 | 214 | 212
2017-05-26 23:00 | 203 | 201
2017-05-26 23:30 | 193 | 191
2017-05-27 | 186 | 184
2017-05-27 00:30 | 178 | 175
2017-05-27 01:00 | 173 | 170
2017-05-27 01:30 | 168 | 165
2017-05-27 02:00 | 165 | 163
2017-05-27 02:30 | 164 | 161
2017-05-27 03:00 | 162 | 159
2017-05-27 03:30 | 161 | 158
2017-05-27 04:00 | 160 | 157
2017-05-27 04:30 | 161 | 158
2017-05-27 05:00 | 161 | 158
2017-05-27 05:30 | 164 | 161
2017-05-27 06:00 | 169 | 166
2017-05-27 06:30 | 179 | 176
2017-05-27 07:00 | 185 | 183
2017-05-27 07:30 | 196 | 193
2017-05-27 08:00 | 204 | 202
2017-05-27 08:30 | 215 | 213
2017-05-27 09:00 | 214 | 212
2017-05-27 09:30 | 214 | 212
2017-05-27 10:00 | 213 | 211
2017-05-27 10:30 | 209 | 207
2017-05-27 11:00 | 209 | 207
2017-05-27 11:30 | 206 | 203
2017-05-27 12:00 | 205 | 203
2017-05-27 12:30 | 201 | 199
2017-05-27 13:00 | 199 | 197
2017-05-27 13:30 | 199 | 197
2017-05-27 14:00 | 201 | 198
2017-05-27 14:30 | 194 | 192
2017-05-27 15:00 | 191 | 188
2017-05-27 15:30 | 196 | 194
2017-05-27 16:00 | 203 | 201
2017-05-27 16:30 | 213 | 211
2017-05-27 17:00 | 221 | 219
2017-05-27 17:30 | 228 | 226
2017-05-27 18:00 | 227 | 225
2017-05-27 18:30 | 224 | 222
2017-05-27 19:00 | 246 | 244
2017-05-27 19:30 | 242 | 240
2017-05-27 20:00 | 231 | 229
2017-05-27 20:30 | 236 | 234
2017-05-27 21:00 | 232 | 230
2017-05-27 21:30 | 226 | 224
2017-05-27 22:00 | 218 | 216
2017-05-27 22:30 | 211 | 209
2017-05-27 23:00 | 202 | 200
2017-05-27 23:30 | 194 | 192
2017-05-28 | 189 | 186
2017-05-28 00:30 | 184 | 181
2017-05-28 01:00 | 178 | 176
2017-05-28 01:30 | 175 | 172
2017-05-28 02:00 | 171 | 169
2017-05-28 02:30 | 170 | 167
2017-05-28 03:00 | 168 | 165
2017-05-28 03:30 | 166 | 163
2017-05-28 04:00 | 165 | 163
2017-05-28 04:30 | 165 | 163
2017-05-28 05:00 | 165 | 163
2017-05-28 05:30 | 166 | 164
2017-05-28 06:00 | 169 | 166
2017-05-28 06:30 | 175 | 172
2017-05-28 07:00 | 178 | 175
2017-05-28 07:30 | 184 | 182
2017-05-28 08:00 | 190 | 187
2017-05-28 08:30 | 197 | 195
2017-05-28 09:00 | 199 | 197
2017-05-28 09:30 | 204 | 202
2017-05-28 10:00 | 204 | 202
2017-05-28 10:30 | 207 | 204
2017-05-28 11:00 | 204 | 201
2017-05-28 11:30 | 202 | 199
2017-05-28 12:00 | 200 | 197
2017-05-28 12:30 | 199 | 197
2017-05-28 13:00 | 200 | 197
2017-05-28 13:30 | 200 | 197
2017-05-28 14:00 | 196 | 194
2017-05-28 14:30 | 189 | 186
2017-05-28 15:00 | 188 | 185
2017-05-28 15:30 | 194 | 192
2017-05-28 16:00 | 203 | 201
2017-05-28 16:30 | 210 | 208
2017-05-28 17:00 | 219 | 217
2017-05-28 17:30 | 231 | 230
2017-05-28 18:00 | 253 | 251
2017-05-28 18:30 | 271 | 270
2017-05-28 19:00 | 281 | 280
2017-05-28 19:30 | 272 | 271
2017-05-28 20:00 | 259 | 258
2017-05-28 20:30 | 249 | 248
2017-05-28 21:00 | 240 | 239
2017-05-28 21:30 | 231 | 229
2017-05-28 22:00 | 223 | 221
2017-05-28 22:30 | 211 | 208
2017-05-28 23:00 | 200 | 198
2017-05-28 23:30 | 190 | 188
2017-05-29 | 183 | 180
2017-05-29 00:30 | 179 | 176
2017-05-29 01:00 | 172 | 171
2017-05-29 01:30 | 168 | 166
2017-05-29 02:00 | 166 | 164
2017-05-29 02:30 | 165 | 164
2017-05-29 03:00 | 163 | 162
2017-05-29 03:30 | 163 | 162
2017-05-29 04:00 | 164 | 162
2017-05-29 04:30 | 166 | 164
2017-05-29 05:00 | 167 | 165
2017-05-29 05:30 | 173 | 171
2017-05-29 06:00 | 182 | 181
2017-05-29 06:30 | 201 | 200
2017-05-29 07:00 | 196 | 195
2017-05-29 07:30 | 232 | 231
2017-05-29 08:00 | 244 | 243
2017-05-29 08:30 | 242 | 241
2017-05-29 09:00 | 238 | 236
2017-05-29 09:30 | 237 | 235
2017-05-29 10:00 | 229 | 227
2017-05-29 10:30 | 232 | 230
2017-05-29 11:00 | 229 | 227
2017-05-29 11:30 | 231 | 228
2017-05-29 12:00 | 226 | 224
2017-05-29 12:30 | 228 | 226
2017-05-29 13:00 | 231 | 229
2017-05-29 13:30 | 235 | 233
2017-05-29 14:00 | 233 | 231
2017-05-29 14:30 | 222 | 220
2017-05-29 15:00 | 224 | 222
2017-05-29 15:30 | 227 | 225
2017-05-29 16:00 | 234 | 232
2017-05-29 16:30 | 242 | 240
2017-05-29 17:00 | 240 | 237
2017-05-29 17:30 | 230 | 227
2017-05-29 18:00 | 239 | 236
2017-05-29 18:30 | 255 | 253
2017-05-29 19:00 | 271 | 269
2017-05-29 19:30 | 273 | 271
2017-05-29 20:00 | 270 | 268
2017-05-29 20:30 | 256 | 255
2017-05-29 21:00 | 245 | 244
2017-05-29 21:30 | 233 | 232
2017-05-29 22:00 | 223 | 222
2017-05-29 22:30 | 210 | 208
2017-05-29 23:00 | 196 | 194
2017-05-29 23:30 | 186 | 185
2017-05-30 | 179 | 178
2017-05-30 00:30 | 173 | 172
2017-05-30 01:00 | 168 | 167
2017-05-30 01:30 | 164 | 163
2017-05-30 02:00 | 161 | 159
2017-05-30 02:30 | 160 | 158
2017-05-30 03:00 | 158 | 156
2017-05-30 03:30 | 151 | 149
2017-05-30 04:00 | 127 | 123
2017-05-30 04:30 | 149 | 147
2017-05-30 05:00 | 160 | 158
2017-05-30 05:30 | 170 | 168
2017-05-30 06:00 | 177 | 176
2017-05-30 06:30 | 184 | 183
2017-05-30 07:00 | 197 | 195
2017-05-30 07:30 | 215 | 214
2017-05-30 08:00 | 226 | 224
2017-05-30 08:30 | 225 | 224
2017-05-30 09:00 | 223 | 222
2017-05-30 09:30 | 217 | 214
2017-05-30 10:00 | 215 | 212
2017-05-30 10:30 | 217 | 215
2017-05-30 11:00 | 215 | 213
2017-05-30 11:30 | 211 | 209
2017-05-30 12:00 | 213 | 211
2017-05-30 12:30 | 216 | 213
2017-05-30 13:00 | 222 | 220
2017-05-30 13:30 | 227 | 224
2017-05-30 14:00 | 234 | 231
2017-05-30 14:30 | 229 | 226
2017-05-30 15:00 | 226 | 223
2017-05-30 15:30 | 226 | 224
2017-05-30 16:00 | 228 | 226
2017-05-30 16:30 | 232 | 230
2017-05-30 17:00 | 230 | 227
2017-05-30 17:30 | 222 | 221
2017-05-30 18:00 | 231 | 229
2017-05-30 18:30 | 260 | 259
2017-05-30 19:00 | 265 | 264
2017-05-30 19:30 | 267 | 266
2017-05-30 20:00 | 250 | 248
2017-05-30 20:30 | 235 | 233
2017-05-30 21:00 | 237 | 235
2017-05-30 21:30 | 233 | 231
2017-05-30 22:00 | 222 | 220
2017-05-30 22:30 | 208 | 206
2017-05-30 23:00 | 198 | 195
2017-05-30 23:30 | 186 | 184
2017-05-31 | 179 | 177
2017-05-31 00:30 | 170 | 168
2017-05-31 01:00 | 167 | 165
2017-05-31 01:30 | 165 | 163
2017-05-31 02:00 | 161 | 159
2017-05-31 02:30 | 158 | 156
2017-05-31 03:00 | 157 | 156
2017-05-31 03:30 | 158 | 156
2017-05-31 04:00 | 157 | 155
2017-05-31 04:30 | 159 | 157
2017-05-31 05:00 | 164 | 162
2017-05-31 05:30 | 170 | 168
2017-05-31 06:00 | 181 | 179
2017-05-31 06:30 | 187 | 185
2017-05-31 07:00 | 195 | 193
2017-05-31 07:30 | 212 | 211
2017-05-31 08:00 | 223 | 222
2017-05-31 08:30 | 237 | 234
2017-05-31 09:00 | 240 | 237
2017-05-31 09:30 | 235 | 232
2017-05-31 10:00 | 232 | 230
2017-05-31 10:30 | 226 | 223
2017-05-31 11:00 | 200 | 197
2017-05-31 11:30 | 196 | 193
2017-05-31 12:00 | 199 | 196
2017-05-31 12:30 | 206 | 204
2017-05-31 13:00 | 211 | 209
2017-05-31 13:30 | 214 | 212
2017-05-31 14:00 | 211 | 209
2017-05-31 14:30 | 177 | 174
2017-05-31 15:00 | 154 | 151
2017-05-31 15:30 | 162 | 159
2017-05-31 16:00 | 171 | 168
2017-05-31 16:30 | 165 | 162
2017-05-31 17:00 | 141 | 137
2017-05-31 17:30 | 107 | 100
2017-05-31 18:00 | 118 | 112
2017-05-31 18:30 | 129 | 124
2017-05-31 19:00 | 131 | 126
2017-05-31 19:30 | 133 | 128
2017-05-31 20:00 | 126 | 121
2017-05-31 20:30 | 115 | 109
2017-05-31 21:00 | 103 | 95
2017-05-31 21:30 | 97 | 89
2017-05-31 22:00 | 88 | 78
2017-05-31 22:30 | 79 | 67
2017-05-31 23:00 | 72 | 60
2017-05-31 23:30 | 55 | 48
2017-06-01 | 65 | 57
2017-06-01 00:30 | 103 | 99
2017-06-01 01:00 | 99 | 96
2017-06-01 01:30 | 96 | 92
2017-06-01 02:00 | 90 | 87
2017-06-01 02:30 | 89 | 87
2017-06-01 03:00 | 86 | 84
2017-06-01 03:30 | 86 | 84
2017-06-01 04:00 | 87 | 84
2017-06-01 04:30 | 87 | 85
2017-06-01 05:00 | 90 | 87
2017-06-01 05:30 | 95 | 93
2017-06-01 06:00 | 93 | 91
2017-06-01 06:30 | 103 | 101
2017-06-01 07:00 | 75 | 73
2017-06-01 07:30 | 86 | 84
2017-06-01 08:00 | 88 | 86
2017-06-01 08:30 | 104 | 102
2017-06-01 09:00 | 161 | 159
2017-06-01 09:30 | 166 | 164
2017-06-01 10:00 | 164 | 162
2017-06-01 10:30 | 160 | 158
2017-06-01 11:00 | 158 | 155
2017-06-01 11:30 | 156 | 154
2017-06-01 12:00 | 158 | 156
2017-06-01 12:30 | 156 | 154
2017-06-01 13:00 | 150 | 148
2017-06-01 13:30 | 153 | 151
2017-06-01 14:00 | 154 | 151
2017-06-01 14:30 | 143 | 140
2017-06-01 15:00 | 140 | 138
2017-06-01 15:30 | 145 | 142
2017-06-01 16:00 | 151 | 148
2017-06-01 16:30 | 150 | 148
2017-06-01 17:00 | 110 | 107
2017-06-01 17:30 | 113 | 110
2017-06-01 18:00 | 123 | 120
2017-06-01 18:30 | 131 | 128
2017-06-01 19:00 | 150 | 148
2017-06-01 19:30 | 151 | 149
2017-06-01 20:00 | 141 | 139
2017-06-01 20:30 | 131 | 129
2017-06-01 21:00 | 121 | 119
2017-06-01 21:30 | 109 | 107
2017-06-01 22:00 | 111 | 108
2017-06-01 22:30 | 92 | 89
2017-06-01 23:00 | 77 | 75
2017-06-01 23:30 | 67 | 64
2017-06-02 | 79 | 77
2017-06-02 00:30 | 95 | 94
2017-06-02 01:00 | 89 | 88
2017-06-02 01:30 | 84 | 83
2017-06-02 02:00 | 84 | 82
2017-06-02 02:30 | 84 | 82
2017-06-02 03:00 | 82 | 81
2017-06-02 03:30 | 82 | 80
2017-06-02 04:00 | 80 | 79
2017-06-02 04:30 | 83 | 82
2017-06-02 05:00 | 87 | 86
2017-06-02 05:30 | 95 | 93
2017-06-02 06:00 | 106 | 105
2017-06-02 06:30 | 125 | 124
2017-06-02 07:00 | 107 | 106
2017-06-02 07:30 | 121 | 120
2017-06-02 08:00 | 131 | 130
2017-06-02 08:30 | 136 | 135
2017-06-02 09:00 | 171 | 170
2017-06-02 09:30 | 178 | 177
2017-06-02 10:00 | 172 | 170
2017-06-02 10:30 | 163 | 160
2017-06-02 11:00 | 160 | 158
2017-06-02 11:30 | 160 | 158
2017-06-02 12:00 | 160 | 158
2017-06-02 12:30 | 161 | 159
2017-06-02 13:00 | 162 | 160
2017-06-02 13:30 | 163 | 161
2017-06-02 14:00 | 159 | 156
2017-06-02 14:30 | 150 | 147
2017-06-02 15:00 | 148 | 145
2017-06-02 15:30 | 150 | 147
2017-06-02 16:00 | 150 | 147
2017-06-02 16:30 | 151 | 148
2017-06-02 17:00 | 117 | 114
2017-06-02 17:30 | 99 | 95
2017-06-02 18:00 | 122 | 119
2017-06-02 18:30 | 133 | 130
2017-06-02 19:00 | 131 | 128
2017-06-02 19:30 | 129 | 126
2017-06-02 20:00 | 122 | 118
2017-06-02 20:30 | 107 | 103
2017-06-02 21:00 | 137 | 135
2017-06-02 21:30 | 150 | 147
2017-06-02 22:00 | 147 | 144
2017-06-02 22:30 | 108 | 104
2017-06-02 23:00 | 121 | 117
2017-06-02 23:30 | 117 | 113
2017-06-03 | 109 | 107
2017-06-03 00:30 | 126 | 124
2017-06-03 01:00 | 165 | 163
2017-06-03 01:30 | 160 | 158
2017-06-03 02:00 | 156 | 154
2017-06-03 02:30 | 152 | 150
2017-06-03 03:00 | 149 | 148
2017-06-03 03:30 | 150 | 149
2017-06-03 04:00 | 149 | 147
2017-06-03 04:30 | 149 | 147
2017-06-03 05:00 | 150 | 148
2017-06-03 05:30 | 155 | 153
2017-06-03 06:00 | 158 | 157
2017-06-03 06:30 | 159 | 157
2017-06-03 07:00 | 175 | 173
2017-06-03 07:30 | 186 | 184
2017-06-03 08:00 | 199 | 197
2017-06-03 08:30 | 211 | 210
2017-06-03 09:00 | 216 | 215
2017-06-03 09:30 | 218 | 217
2017-06-03 10:00 | 215 | 213
2017-06-03 10:30 | 207 | 206
2017-06-03 11:00 | 206 | 205
2017-06-03 11:30 | 208 | 207
2017-06-03 12:00 | 202 | 201
2017-06-03 12:30 | 196 | 195
2017-06-03 13:00 | 199 | 198
2017-06-03 13:30 | 198 | 197
2017-06-03 14:00 | 191 | 189
2017-06-03 14:30 | 188 | 187
2017-06-03 15:00 | 180 | 179
2017-06-03 15:30 | 182 | 180
2017-06-03 16:00 | 192 | 190
2017-06-03 16:30 | 197 | 196
2017-06-03 17:00 | 205 | 204
2017-06-03 17:30 | 215 | 214
2017-06-03 18:00 | 235 | 234
2017-06-03 18:30 | 234 | 232
2017-06-03 19:00 | 254 | 253
2017-06-03 19:30 | 247 | 245
2017-06-03 20:00 | 237 | 235
2017-06-03 20:30 | 226 | 224
2017-06-03 21:00 | 218 | 216
2017-06-03 21:30 | 211 | 209
2017-06-03 22:00 | 204 | 202
2017-06-03 22:30 | 195 | 192
2017-06-03 23:00 | 186 | 183
2017-06-03 23:30 | 178 | 175
2017-06-04 | 170 | 168
2017-06-04 00:30 | 164 | 163
2017-06-04 01:00 | 158 | 156
2017-06-04 01:30 | 155 | 153
2017-06-04 02:00 | 151 | 150
2017-06-04 02:30 | 150 | 148
2017-06-04 03:00 | 149 | 147
2017-06-04 03:30 | 147 | 146
2017-06-04 04:00 | 147 | 145
2017-06-04 04:30 | 147 | 145
2017-06-04 05:00 | 147 | 145
2017-06-04 05:30 | 149 | 147
2017-06-04 06:00 | 152 | 150
2017-06-04 06:30 | 156 | 154
2017-06-04 07:00 | 161 | 159
2017-06-04 07:30 | 170 | 168
2017-06-04 08:00 | 179 | 177
2017-06-04 08:30 | 185 | 183
2017-06-04 09:00 | 189 | 188
2017-06-04 09:30 | 192 | 191
2017-06-04 10:00 | 191 | 190
2017-06-04 10:30 | 190 | 189
2017-06-04 11:00 | 188 | 186
2017-06-04 11:30 | 185 | 184
2017-06-04 12:00 | 185 | 184
2017-06-04 12:30 | 183 | 182
2017-06-04 13:00 | 181 | 179
2017-06-04 13:30 | 181 | 180
2017-06-04 14:00 | 183 | 181
2017-06-04 14:30 | 172 | 170
2017-06-04 15:00 | 172 | 170
2017-06-04 15:30 | 179 | 178
2017-06-04 16:00 | 186 | 184
2017-06-04 16:30 | 193 | 192
2017-06-04 17:00 | 203 | 202
2017-06-04 17:30 | 218 | 217
2017-06-04 18:00 | 251 | 250
2017-06-04 18:30 | 269 | 268
2017-06-04 19:00 | 271 | 270
2017-06-04 19:30 | 261 | 260
2017-06-04 20:00 | 250 | 248
2017-06-04 20:30 | 238 | 237
2017-06-04 21:00 | 229 | 227
2017-06-04 21:30 | 221 | 219
2017-06-04 22:00 | 211 | 209
2017-06-04 22:30 | 198 | 196
2017-06-04 23:00 | 189 | 187
2017-06-04 23:30 | 178 | 176
2017-06-05 | 170 | 168
2017-06-05 00:30 | 165 | 163
2017-06-05 01:00 | 159 | 157
2017-06-05 01:30 | 155 | 153
2017-06-05 02:00 | 154 | 152
2017-06-05 02:30 | 152 | 150
2017-06-05 03:00 | 150 | 148
2017-06-05 03:30 | 149 | 147
2017-06-05 04:00 | 149 | 147
2017-06-05 04:30 | 153 | 151
2017-06-05 05:00 | 158 | 156
2017-06-05 05:30 | 165 | 163
2017-06-05 06:00 | 175 | 173
2017-06-05 06:30 | 183 | 181
2017-06-05 07:00 | 199 | 197
2017-06-05 07:30 | 219 | 218
2017-06-05 08:00 | 226 | 225
2017-06-05 08:30 | 234 | 233
2017-06-05 09:00 | 232 | 230
2017-06-05 09:30 | 228 | 226
2017-06-05 10:00 | 220 | 218
2017-06-05 10:30 | 219 | 217
2017-06-05 11:00 | 218 | 216
2017-06-05 11:30 | 215 | 213
2017-06-05 12:00 | 213 | 211
2017-06-05 12:30 | 213 | 211
2017-06-05 13:00 | 213 | 211
2017-06-05 13:30 | 213 | 212
2017-06-05 14:00 | 214 | 212
2017-06-05 14:30 | 209 | 207
2017-06-05 15:00 | 205 | 203
2017-06-05 15:30 | 208 | 206
2017-06-05 16:00 | 215 | 213
2017-06-05 16:30 | 215 | 214
2017-06-05 17:00 | 222 | 220
2017-06-05 17:30 | 219 | 217
2017-06-05 18:00 | 241 | 239
2017-06-05 18:30 | 262 | 260
2017-06-05 19:00 | 265 | 263
2017-06-05 19:30 | 255 | 253
2017-06-05 20:00 | 243 | 241
2017-06-05 20:30 | 232 | 230
2017-06-05 21:00 | 234 | 233
2017-06-05 21:30 | 229 | 226
2017-06-05 22:00 | 217 | 215
2017-06-05 22:30 | 200 | 199
2017-06-05 23:00 | 190 | 188
2017-06-05 23:30 | 180 | 178
2017-06-06 | 171 | 170
2017-06-06 00:30 | 166 | 164
2017-06-06 01:00 | 162 | 160
2017-06-06 01:30 | 158 | 155
2017-06-06 02:00 | 153 | 152
2017-06-06 02:30 | 152 | 151
2017-06-06 03:00 | 150 | 148
2017-06-06 03:30 | 151 | 150
2017-06-06 04:00 | 150 | 148
2017-06-06 04:30 | 150 | 148
2017-06-06 05:00 | 155 | 153
2017-06-06 05:30 | 160 | 159
2017-06-06 06:00 | 169 | 168
2017-06-06 06:30 | 177 | 175
2017-06-06 07:00 | 194 | 193
2017-06-06 07:30 | 209 | 208
2017-06-06 08:00 | 220 | 219
2017-06-06 08:30 | 233 | 231
2017-06-06 09:00 | 230 | 228
2017-06-06 09:30 | 222 | 220
2017-06-06 10:00 | 217 | 216
2017-06-06 10:30 | 208 | 207
2017-06-06 11:00 | 175 | 173
2017-06-06 11:30 | 164 | 163
2017-06-06 12:00 | 164 | 162
2017-06-06 12:30 | 164 | 162
2017-06-06 13:00 | 169 | 168
2017-06-06 13:30 | 174 | 172
2017-06-06 14:00 | 171 | 169
2017-06-06 14:30 | 135 | 133
2017-06-06 15:00 | 124 | 122
2017-06-06 15:30 | 129 | 127
2017-06-06 16:00 | 134 | 132
2017-06-06 16:30 | 123 | 121
2017-06-06 17:00 | 114 | 112
2017-06-06 17:30 | 108 | 106
2017-06-06 18:00 | 118 | 117
2017-06-06 18:30 | 136 | 135
2017-06-06 19:00 | 138 | 137
2017-06-06 19:30 | 137 | 136
2017-06-06 20:00 | 137 | 136
2017-06-06 20:30 | 128 | 127
2017-06-06 21:00 | 127 | 125
2017-06-06 21:30 | 142 | 141
2017-06-06 22:00 | 207 | 205
2017-06-06 22:30 | 206 | 204
2017-06-06 23:00 | 193 | 191
2017-06-06 23:30 | 182 | 180
2017-06-07 | 173 | 171
2017-06-07 00:30 | 166 | 164
2017-06-07 01:00 | 160 | 158
2017-06-07 01:30 | 155 | 154
2017-06-07 02:00 | 152 | 151
2017-06-07 02:30 | 150 | 149
2017-06-07 03:00 | 151 | 149
2017-06-07 03:30 | 150 | 149
2017-06-07 04:00 | 150 | 149
2017-06-07 04:30 | 154 | 152
2017-06-07 05:00 | 156 | 155
2017-06-07 05:30 | 164 | 162
2017-06-07 06:00 | 173 | 172
2017-06-07 06:30 | 182 | 181
2017-06-07 07:00 | 198 | 197
2017-06-07 07:30 | 220 | 219
2017-06-07 08:00 | 225 | 224
2017-06-07 08:30 | 235 | 234
2017-06-07 09:00 | 229 | 228
2017-06-07 09:30 | 221 | 219
2017-06-07 10:00 | 212 | 210
2017-06-07 10:30 | 206 | 204
2017-06-07 11:00 | 203 | 201
2017-06-07 11:30 | 199 | 196
2017-06-07 12:00 | 199 | 196
2017-06-07 12:30 | 200 | 197
2017-06-07 13:00 | 201 | 198
2017-06-07 13:30 | 202 | 199
2017-06-07 14:00 | 203 | 201
2017-06-07 14:30 | 196 | 194
2017-06-07 15:00 | 194 | 191
2017-06-07 15:30 | 197 | 194
2017-06-07 16:00 | 206 | 203
2017-06-07 16:30 | 213 | 210
2017-06-07 17:00 | 221 | 219
2017-06-07 17:30 | 217 | 214
2017-06-07 18:00 | 242 | 239
2017-06-07 18:30 | 262 | 260
2017-06-07 19:00 | 265 | 263
2017-06-07 19:30 | 257 | 255
2017-06-07 20:00 | 247 | 245
2017-06-07 20:30 | 239 | 236
2017-06-07 21:00 | 238 | 236
2017-06-07 21:30 | 229 | 228
2017-06-07 22:00 | 220 | 218
2017-06-07 22:30 | 206 | 204
2017-06-07 23:00 | 194 | 193
2017-06-07 23:30 | 183 | 181
2017-06-08 | 172 | 170
2017-06-08 00:30 | 167 | 165
2017-06-08 01:00 | 160 | 158
2017-06-08 01:30 | 155 | 154
2017-06-08 02:00 | 151 | 149
2017-06-08 02:30 | 150 | 149
2017-06-08 03:00 | 150 | 148
2017-06-08 03:30 | 150 | 148
2017-06-08 04:00 | 150 | 148
2017-06-08 04:30 | 152 | 150
2017-06-08 05:00 | 154 | 153
2017-06-08 05:30 | 162 | 161
2017-06-08 06:00 | 175 | 174
2017-06-08 06:30 | 185 | 183
2017-06-08 07:00 | 196 | 195
2017-06-08 07:30 | 222 | 220
2017-06-08 08:00 | 226 | 224
2017-06-08 08:30 | 228 | 227
2017-06-08 09:00 | 219 | 218
2017-06-08 09:30 | 214 | 212
2017-06-08 10:00 | 207 | 205
2017-06-08 10:30 | 202 | 200
2017-06-08 11:00 | 197 | 195
2017-06-08 11:30 | 196 | 194
2017-06-08 12:00 | 193 | 191
2017-06-08 12:30 | 192 | 190
2017-06-08 13:00 | 192 | 190
2017-06-08 13:30 | 193 | 192
2017-06-08 14:00 | 192 | 190
2017-06-08 14:30 | 185 | 183
2017-06-08 15:00 | 185 | 183
2017-06-08 15:30 | 193 | 191
2017-06-08 16:00 | 202 | 200
2017-06-08 16:30 | 211 | 209
2017-06-08 17:00 | 218 | 216
2017-06-08 17:30 | 220 | 218
2017-06-08 18:00 | 227 | 224
2017-06-08 18:30 | 245 | 243
2017-06-08 19:00 | 251 | 249
2017-06-08 19:30 | 258 | 256
2017-06-08 20:00 | 252 | 250
2017-06-08 20:30 | 243 | 241
2017-06-08 21:00 | 242 | 240
2017-06-08 21:30 | 232 | 230
2017-06-08 22:00 | 220 | 218
2017-06-08 22:30 | 208 | 206
2017-06-08 23:00 | 195 | 192
2017-06-08 23:30 | 182 | 180
2017-06-09 | 174 | 172
2017-06-09 00:30 | 166 | 164
2017-06-09 01:00 | 162 | 160
2017-06-09 01:30 | 157 | 155
2017-06-09 02:00 | 155 | 153
2017-06-09 02:30 | 150 | 149
2017-06-09 03:00 | 149 | 148
2017-06-09 03:30 | 148 | 147
2017-06-09 04:00 | 149 | 148
2017-06-09 04:30 | 151 | 150
2017-06-09 05:00 | 155 | 154
2017-06-09 05:30 | 162 | 161
2017-06-09 06:00 | 170 | 169
2017-06-09 06:30 | 178 | 177
2017-06-09 07:00 | 194 | 193
2017-06-09 07:30 | 213 | 212
2017-06-09 08:00 | 218 | 217
2017-06-09 08:30 | 220 | 219
2017-06-09 09:00 | 235 | 234
2017-06-09 09:30 | 195 | 194
2017-06-09 10:00 | 154 | 152
2017-06-09 10:30 | 168 | 167
2017-06-09 11:00 | 173 | 172
2017-06-09 11:30 | 174 | 173
2017-06-09 12:00 | 176 | 175
2017-06-09 12:30 | 175 | 173
2017-06-09 13:00 | 175 | 173
2017-06-09 13:30 | 180 | 179
2017-06-09 14:00 | 183 | 182
2017-06-09 14:30 | 176 | 175
2017-06-09 15:00 | 173 | 172
2017-06-09 15:30 | 171 | 169
2017-06-09 16:00 | 183 | 182
2017-06-09 16:30 | 195 | 194
2017-06-09 17:00 | 203 | 202
2017-06-09 17:30 | 209 | 208
2017-06-09 18:00 | 216 | 215
2017-06-09 18:30 | 230 | 229
2017-06-09 19:00 | 239 | 238
2017-06-09 19:30 | 252 | 251
2017-06-09 20:00 | 247 | 245
2017-06-09 20:30 | 237 | 236
2017-06-09 21:00 | 229 | 227
2017-06-09 21:30 | 220 | 219
2017-06-09 22:00 | 218 | 217
2017-06-09 22:30 | 237 | 236
2017-06-09 23:00 | 227 | 225
2017-06-09 23:30 | 217 | 215
2017-06-10 | 207 | 206
2017-06-10 00:30 | 202 | 201
2017-06-10 01:00 | 196 | 195
2017-06-10 01:30 | 192 | 191
2017-06-10 02:00 | 188 | 186
2017-06-10 02:30 | 187 | 185
2017-06-10 03:00 | 185 | 183
2017-06-10 03:30 | 184 | 182
2017-06-10 04:00 | 183 | 181
2017-06-10 04:30 | 183 | 181
2017-06-10 05:00 | 184 | 182
2017-06-10 05:30 | 186 | 184
2017-06-10 06:00 | 191 | 190
2017-06-10 06:30 | 196 | 195
2017-06-10 07:00 | 197 | 195
2017-06-10 07:30 | 182 | 180
2017-06-10 08:00 | 191 | 189
2017-06-10 08:30 | 204 | 202
2017-06-10 09:00 | 207 | 206
2017-06-10 09:30 | 211 | 209
2017-06-10 10:00 | 208 | 207
2017-06-10 10:30 | 204 | 203
2017-06-10 11:00 | 194 | 193
2017-06-10 11:30 | 188 | 187
2017-06-10 12:00 | 190 | 189
2017-06-10 12:30 | 189 | 187
2017-06-10 13:00 | 182 | 181
2017-06-10 13:30 | 181 | 179
2017-06-10 14:00 | 179 | 177
2017-06-10 14:30 | 169 | 167
2017-06-10 15:00 | 168 | 167
2017-06-10 15:30 | 174 | 172
2017-06-10 16:00 | 180 | 179
2017-06-10 16:30 | 192 | 190
2017-06-10 17:00 | 201 | 199
2017-06-10 17:30 | 211 | 210
2017-06-10 18:00 | 237 | 236
2017-06-10 18:30 | 251 | 250
2017-06-10 19:00 | 251 | 250
2017-06-10 19:30 | 243 | 242
2017-06-10 20:00 | 232 | 231
2017-06-10 20:30 | 223 | 222
2017-06-10 21:00 | 216 | 215
2017-06-10 21:30 | 210 | 208
2017-06-10 22:00 | 208 | 207
2017-06-10 22:30 | 227 | 226
2017-06-10 23:00 | 222 | 221
2017-06-10 23:30 | 213 | 212
2017-06-11 | 204 | 202
2017-06-11 00:30 | 199 | 197
2017-06-11 01:00 | 194 | 193
2017-06-11 01:30 | 190 | 189
2017-06-11 02:00 | 188 | 187
2017-06-11 02:30 | 188 | 186
2017-06-11 03:00 | 186 | 184
2017-06-11 03:30 | 185 | 183
2017-06-11 04:00 | 184 | 182
2017-06-11 04:30 | 185 | 183
2017-06-11 05:00 | 185 | 183
2017-06-11 05:30 | 183 | 181
2017-06-11 06:00 | 187 | 185
2017-06-11 06:30 | 192 | 190
2017-06-11 07:00 | 191 | 189
2017-06-11 07:30 | 172 | 170
2017-06-11 08:00 | 180 | 178
2017-06-11 08:30 | 190 | 189
2017-06-11 09:00 | 198 | 197
2017-06-11 09:30 | 206 | 204
2017-06-11 10:00 | 210 | 208
2017-06-11 10:30 | 210 | 208
2017-06-11 11:00 | 212 | 211
2017-06-11 11:30 | 214 | 213
2017-06-11 12:00 | 212 | 210
2017-06-11 12:30 | 212 | 210
2017-06-11 13:00 | 211 | 210
2017-06-11 13:30 | 208 | 207
2017-06-11 14:00 | 204 | 203
2017-06-11 14:30 | 193 | 191
2017-06-11 15:00 | 188 | 187
2017-06-11 15:30 | 191 | 190
2017-06-11 16:00 | 197 | 196
2017-06-11 16:30 | 205 | 204
2017-06-11 17:00 | 215 | 214
2017-06-11 17:30 | 227 | 226
2017-06-11 18:00 | 256 | 255
2017-06-11 18:30 | 270 | 269
2017-06-11 19:00 | 266 | 265
2017-06-11 19:30 | 257 | 256
2017-06-11 20:00 | 247 | 245
2017-06-11 20:30 | 237 | 235
2017-06-11 21:00 | 228 | 227
2017-06-11 21:30 | 220 | 219
2017-06-11 22:00 | 217 | 216
2017-06-11 22:30 | 231 | 230
2017-06-11 23:00 | 222 | 220
2017-06-11 23:30 | 213 | 211
2017-06-12 | 204 | 202
2017-06-12 00:30 | 198 | 196
2017-06-12 01:00 | 191 | 190
2017-06-12 01:30 | 189 | 188
2017-06-12 02:00 | 185 | 184
2017-06-12 02:30 | 183 | 182
2017-06-12 03:00 | 182 | 180
2017-06-12 03:30 | 182 | 181
2017-06-12 04:00 | 184 | 183
2017-06-12 04:30 | 185 | 184
2017-06-12 05:00 | 189 | 188
2017-06-12 05:30 | 196 | 195
2017-06-12 06:00 | 205 | 204
2017-06-12 06:30 | 226 | 224
2017-06-12 07:00 | 240 | 239
2017-06-12 07:30 | 236 | 235
2017-06-12 08:00 | 242 | 241
2017-06-12 08:30 | 238 | 236
2017-06-12 09:00 | 226 | 225
2017-06-12 09:30 | 217 | 216
2017-06-12 10:00 | 212 | 211
2017-06-12 10:30 | 206 | 205
2017-06-12 11:00 | 204 | 203
2017-06-12 11:30 | 200 | 199
2017-06-12 12:00 | 198 | 197
2017-06-12 12:30 | 198 | 197
2017-06-12 13:00 | 195 | 194
2017-06-12 13:30 | 197 | 196
2017-06-12 14:00 | 199 | 197
2017-06-12 14:30 | 192 | 190
2017-06-12 15:00 | 190 | 189
2017-06-12 15:30 | 194 | 193
2017-06-12 16:00 | 202 | 201
2017-06-12 16:30 | 211 | 210
2017-06-12 17:00 | 218 | 217
2017-06-12 17:30 | 217 | 216
2017-06-12 18:00 | 227 | 226
2017-06-12 18:30 | 246 | 245
2017-06-12 19:00 | 253 | 252
2017-06-12 19:30 | 266 | 265
2017-06-12 20:00 | 259 | 258
2017-06-12 20:30 | 251 | 250
2017-06-12 21:00 | 241 | 240
2017-06-12 21:30 | 230 | 228
2017-06-12 22:00 | 225 | 224
2017-06-12 22:30 | 239 | 237
2017-06-12 23:00 | 228 | 226
2017-06-12 23:30 | 216 | 215
2017-06-13 | 206 | 205
2017-06-13 00:30 | 200 | 199
2017-06-13 01:00 | 195 | 194
2017-06-13 01:30 | 190 | 189
2017-06-13 02:00 | 188 | 187
2017-06-13 02:30 | 188 | 187
2017-06-13 03:00 | 187 | 186
2017-06-13 03:30 | 185 | 184
2017-06-13 04:00 | 182 | 181
2017-06-13 04:30 | 168 | 167
2017-06-13 05:00 | 158 | 156
2017-06-13 05:30 | 162 | 161
2017-06-13 06:00 | 168 | 166
2017-06-13 06:30 | 161 | 160
2017-06-13 07:00 | 176 | 175
2017-06-13 07:30 | 195 | 194
2017-06-13 08:00 | 204 | 203
2017-06-13 08:30 | 175 | 174
2017-06-13 09:00 | 139 | 137
2017-06-13 09:30 | 106 | 105
2017-06-13 10:00 | 97 | 95
2017-06-13 10:30 | 89 | 87
2017-06-13 11:00 | 84 | 82
2017-06-13 11:30 | 81 | 79
2017-06-13 12:00 | 82 | 80
2017-06-13 12:30 | 81 | 79
2017-06-13 13:00 | 80 | 78
2017-06-13 13:30 | 84 | 82
2017-06-13 14:00 | 80 | 79
2017-06-13 14:30 | 73 | 71
2017-06-13 15:00 | 76 | 74
2017-06-13 15:30 | 79 | 78
2017-06-13 16:00 | 83 | 82
2017-06-13 16:30 | 100 | 99
2017-06-13 17:00 | 146 | 145
2017-06-13 17:30 | 133 | 132
2017-06-13 18:00 | 137 | 136
2017-06-13 18:30 | 155 | 154
2017-06-13 19:00 | 170 | 169
2017-06-13 19:30 | 200 | 199
2017-06-13 20:00 | 193 | 192
2017-06-13 20:30 | 177 | 176
2017-06-13 21:00 | 172 | 171
2017-06-13 21:30 | 164 | 163
2017-06-13 22:00 | 159 | 158
2017-06-13 22:30 | 172 | 171
2017-06-13 23:00 | 162 | 161
2017-06-13 23:30 | 150 | 149
2017-06-14 | 141 | 140
2017-06-14 00:30 | 135 | 134
2017-06-14 01:00 | 131 | 129
2017-06-14 01:30 | 127 | 125
2017-06-14 02:00 | 125 | 123
2017-06-14 02:30 | 123 | 121
2017-06-14 03:00 | 120 | 118
2017-06-14 03:30 | 117 | 115
2017-06-14 04:00 | 117 | 115
2017-06-14 04:30 | 119 | 118
2017-06-14 05:00 | 122 | 120
2017-06-14 05:30 | 128 | 126
2017-06-14 06:00 | 140 | 139
2017-06-14 06:30 | 161 | 160
2017-06-14 07:00 | 150 | 149
2017-06-14 07:30 | 159 | 158
2017-06-14 08:00 | 176 | 175
2017-06-14 08:30 | 177 | 176
2017-06-14 09:00 | 165 | 164
2017-06-14 09:30 | 160 | 159
2017-06-14 10:00 | 157 | 156
2017-06-14 10:30 | 151 | 150
2017-06-14 11:00 | 147 | 146
2017-06-14 11:30 | 143 | 141
2017-06-14 12:00 | 140 | 139
2017-06-14 12:30 | 145 | 144
2017-06-14 13:00 | 152 | 151
2017-06-14 13:30 | 157 | 155
2017-06-14 14:00 | 157 | 155
2017-06-14 14:30 | 145 | 144
2017-06-14 15:00 | 143 | 141
2017-06-14 15:30 | 145 | 144
2017-06-14 16:00 | 149 | 148
2017-06-14 16:30 | 154 | 153
2017-06-14 17:00 | 162 | 161
2017-06-14 17:30 | 157 | 156
2017-06-14 18:00 | 152 | 151
2017-06-14 18:30 | 168 | 167
2017-06-14 19:00 | 174 | 173
2017-06-14 19:30 | 203 | 202
2017-06-14 20:00 | 196 | 195
2017-06-14 20:30 | 167 | 166
2017-06-14 21:00 | 174 | 173
2017-06-14 21:30 | 165 | 163
2017-06-14 22:00 | 160 | 159
2017-06-14 22:30 | 171 | 170
2017-06-14 23:00 | 160 | 159
2017-06-14 23:30 | 150 | 149
2017-06-15 | 142 | 140
2017-06-15 00:30 | 161 | 160
2017-06-15 01:00 | 195 | 194
2017-06-15 01:30 | 193 | 192
2017-06-15 02:00 | 189 | 188
2017-06-15 02:30 | 185 | 184
2017-06-15 03:00 | 185 | 184
2017-06-15 03:30 | 185 | 183
2017-06-15 04:00 | 186 | 185
2017-06-15 04:30 | 187 | 186
2017-06-15 05:00 | 188 | 187
2017-06-15 05:30 | 195 | 193
2017-06-15 06:00 | 205 | 204
2017-06-15 06:30 | 223 | 222
2017-06-15 07:00 | 233 | 232
2017-06-15 07:30 | 234 | 233
2017-06-15 08:00 | 236 | 235
2017-06-15 08:30 | 233 | 231
2017-06-15 09:00 | 220 | 219
2017-06-15 09:30 | 217 | 216
2017-06-15 10:00 | 215 | 214
2017-06-15 10:30 | 209 | 207
2017-06-15 11:00 | 205 | 204
2017-06-15 11:30 | 203 | 202
2017-06-15 12:00 | 199 | 198
2017-06-15 12:30 | 198 | 197
2017-06-15 13:00 | 199 | 198
2017-06-15 13:30 | 202 | 201
2017-06-15 14:00 | 203 | 202
2017-06-15 14:30 | 198 | 196
2017-06-15 15:00 | 198 | 196
2017-06-15 15:30 | 200 | 198
2017-06-15 16:00 | 205 | 204
2017-06-15 16:30 | 213 | 212
2017-06-15 17:00 | 220 | 218
2017-06-15 17:30 | 226 | 225
2017-06-15 18:00 | 253 | 252
2017-06-15 18:30 | 275 | 274
2017-06-15 19:00 | 279 | 278
2017-06-15 19:30 | 270 | 269
2017-06-15 20:00 | 260 | 259
2017-06-15 20:30 | 253 | 251
2017-06-15 21:00 | 244 | 243
2017-06-15 21:30 | 232 | 231
2017-06-15 22:00 | 224 | 223
2017-06-15 22:30 | 241 | 239
2017-06-15 23:00 | 232 | 231
2017-06-15 23:30 | 221 | 219
2017-06-16 | 212 | 210
2017-06-16 00:30 | 203 | 201
2017-06-16 01:00 | 198 | 196
2017-06-16 01:30 | 197 | 195
2017-06-16 02:00 | 189 | 188
2017-06-16 02:30 | 188 | 187
2017-06-16 03:00 | 185 | 183
2017-06-16 03:30 | 186 | 184
2017-06-16 04:00 | 185 | 183
2017-06-16 04:30 | 185 | 183
2017-06-16 05:00 | 189 | 187
2017-06-16 05:30 | 196 | 195
2017-06-16 06:00 | 205 | 204
2017-06-16 06:30 | 224 | 222
2017-06-16 07:00 | 235 | 234
2017-06-16 07:30 | 227 | 226
2017-06-16 08:00 | 233 | 232
2017-06-16 08:30 | 234 | 233
2017-06-16 09:00 | 228 | 227
2017-06-16 09:30 | 222 | 221
2017-06-16 10:00 | 217 | 216
2017-06-16 10:30 | 211 | 210
2017-06-16 11:00 | 213 | 212
2017-06-16 11:30 | 211 | 210
2017-06-16 12:00 | 212 | 211
2017-06-16 12:30 | 211 | 210
2017-06-16 13:00 | 214 | 213
2017-06-16 13:30 | 214 | 213
2017-06-16 14:00 | 215 | 214
2017-06-16 14:30 | 201 | 199
2017-06-16 15:00 | 199 | 198
2017-06-16 15:30 | 200 | 199
2017-06-16 16:00 | 211 | 209
2017-06-16 16:30 | 219 | 218
2017-06-16 17:00 | 227 | 226
2017-06-16 17:30 | 232 | 230
2017-06-16 18:00 | 249 | 248
2017-06-16 18:30 | 263 | 261
2017-06-16 19:00 | 266 | 265
2017-06-16 19:30 | 258 | 257
2017-06-16 20:00 | 250 | 248
2017-06-16 20:30 | 241 | 240
2017-06-16 21:00 | 234 | 232
2017-06-16 21:30 | 230 | 228
2017-06-16 22:00 | 233 | 231
2017-06-16 22:30 | 241 | 239
2017-06-16 23:00 | 234 | 232
2017-06-16 23:30 | 223 | 222
2017-06-17 | 214 | 213
2017-06-17 00:30 | 207 | 205
2017-06-17 01:00 | 199 | 197
2017-06-17 01:30 | 196 | 194
2017-06-17 02:00 | 189 | 187
2017-06-17 02:30 | 190 | 188
2017-06-17 03:00 | 189 | 188
2017-06-17 03:30 | 189 | 188
2017-06-17 04:00 | 189 | 187
2017-06-17 04:30 | 187 | 185
2017-06-17 05:00 | 188 | 186
2017-06-17 05:30 | 190 | 188
2017-06-17 06:00 | 195 | 192
2017-06-17 06:30 | 203 | 201
2017-06-17 07:00 | 205 | 204
2017-06-17 07:30 | 192 | 190
2017-06-17 08:00 | 196 | 194
2017-06-17 08:30 | 206 | 205
2017-06-17 09:00 | 209 | 207
2017-06-17 09:30 | 213 | 212
2017-06-17 10:00 | 208 | 206
2017-06-17 10:30 | 208 | 206
2017-06-17 11:00 | 196 | 195
2017-06-17 11:30 | 189 | 187
2017-06-17 12:00 | 186 | 184
2017-06-17 12:30 | 184 | 183
2017-06-17 13:00 | 183 | 181
2017-06-17 13:30 | 181 | 179
2017-06-17 14:00 | 181 | 179
2017-06-17 14:30 | 172 | 171
2017-06-17 15:00 | 172 | 170
2017-06-17 15:30 | 175 | 173
2017-06-17 16:00 | 184 | 182
2017-06-17 16:30 | 190 | 189
2017-06-17 17:00 | 199 | 197
2017-06-17 17:30 | 207 | 206
2017-06-17 18:00 | 220 | 218
2017-06-17 18:30 | 234 | 232
2017-06-17 19:00 | 236 | 235
2017-06-17 19:30 | 239 | 237
2017-06-17 20:00 | 234 | 233
2017-06-17 20:30 | 224 | 223
2017-06-17 21:00 | 215 | 214
2017-06-17 21:30 | 202 | 200
2017-06-17 22:00 | 195 | 193
2017-06-17 22:30 | 195 | 193
2017-06-17 23:00 | 190 | 188
2017-06-17 23:30 | 187 | 185
2017-06-18 | 205 | 203
2017-06-18 00:30 | 200 | 199
2017-06-18 01:00 | 195 | 194
2017-06-18 01:30 | 185 | 184
2017-06-18 02:00 | 184 | 183
2017-06-18 02:30 | 181 | 180
2017-06-18 03:00 | 179 | 177
2017-06-18 03:30 | 179 | 178
2017-06-18 04:00 | 175 | 173
2017-06-18 04:30 | 156 | 154
2017-06-18 05:00 | 159 | 157
2017-06-18 05:30 | 174 | 173
2017-06-18 06:00 | 187 | 186
2017-06-18 06:30 | 194 | 193
2017-06-18 07:00 | 191 | 190
2017-06-18 07:30 | 174 | 172
2017-06-18 08:00 | 179 | 177
2017-06-18 08:30 | 184 | 183
2017-06-18 09:00 | 188 | 187
2017-06-18 09:30 | 189 | 188
2017-06-18 10:00 | 188 | 187
2017-06-18 10:30 | 189 | 187
2017-06-18 11:00 | 186 | 184
2017-06-18 11:30 | 187 | 185
2017-06-18 12:00 | 182 | 180
2017-06-18 12:30 | 179 | 177
2017-06-18 13:00 | 175 | 173
2017-06-18 13:30 | 174 | 172
2017-06-18 14:00 | 173 | 171
2017-06-18 14:30 | 166 | 164
2017-06-18 15:00 | 165 | 163
2017-06-18 15:30 | 170 | 169
2017-06-18 16:00 | 182 | 180
2017-06-18 16:30 | 196 | 194
2017-06-18 17:00 | 206 | 204
2017-06-18 17:30 | 220 | 219
2017-06-18 18:00 | 250 | 249
2017-06-18 18:30 | 265 | 263
2017-06-18 19:00 | 276 | 274
2017-06-18 19:30 | 264 | 262
2017-06-18 20:00 | 252 | 251
2017-06-18 20:30 | 239 | 237
2017-06-18 21:00 | 227 | 225
2017-06-18 21:30 | 216 | 214
2017-06-18 22:00 | 209 | 207
2017-06-18 22:30 | 198 | 196
2017-06-18 23:00 | 185 | 183
2017-06-18 23:30 | 177 | 176
2017-06-19 | 201 | 199
2017-06-19 00:30 | 198 | 196
2017-06-19 01:00 | 191 | 189
2017-06-19 01:30 | 186 | 184
2017-06-19 02:00 | 184 | 182
2017-06-19 02:30 | 181 | 180
2017-06-19 03:00 | 181 | 180
2017-06-19 03:30 | 181 | 180
2017-06-19 04:00 | 181 | 180
2017-06-19 04:30 | 177 | 175
2017-06-19 05:00 | 160 | 158
2017-06-19 05:30 | 161 | 160
2017-06-19 06:00 | 171 | 170
2017-06-19 06:30 | 164 | 162
2017-06-19 07:00 | 172 | 171
2017-06-19 07:30 | 192 | 191
2017-06-19 08:00 | 195 | 193
2017-06-19 08:30 | 161 | 160
2017-06-19 09:00 | 145 | 143
2017-06-19 09:30 | 159 | 157
2017-06-19 10:00 | 146 | 144
2017-06-19 10:30 | 142 | 141
2017-06-19 11:00 | 139 | 137
2017-06-19 11:30 | 138 | 136
2017-06-19 12:00 | 137 | 135
2017-06-19 12:30 | 137 | 135
2017-06-19 13:00 | 139 | 138
2017-06-19 13:30 | 138 | 136
2017-06-19 14:00 | 139 | 137
2017-06-19 14:30 | 133 | 132
2017-06-19 15:00 | 127 | 125
2017-06-19 15:30 | 87 | 85
2017-06-19 16:00 | 84 | 82
2017-06-19 16:30 | 92 | 90
2017-06-19 17:00 | 99 | 97
2017-06-19 17:30 | 106 | 105
2017-06-19 18:00 | 132 | 131
2017-06-19 18:30 | 156 | 154
2017-06-19 19:00 | 160 | 159
2017-06-19 19:30 | 145 | 143
2017-06-19 20:00 | 133 | 132
2017-06-19 20:30 | 122 | 121
2017-06-19 21:00 | 115 | 114
2017-06-19 21:30 | 110 | 108
2017-06-19 22:00 | 111 | 109
2017-06-19 22:30 | 96 | 94
2017-06-19 23:00 | 116 | 114
2017-06-19 23:30 | 115 | 114
2017-06-20 | 114 | 113
2017-06-20 00:30 | 121 | 120
2017-06-20 01:00 | 115 | 114
2017-06-20 01:30 | 111 | 109
2017-06-20 02:00 | 106 | 105
2017-06-20 02:30 | 106 | 105
2017-06-20 03:00 | 105 | 104
2017-06-20 03:30 | 106 | 105
2017-06-20 04:00 | 104 | 103
2017-06-20 04:30 | 106 | 105
2017-06-20 05:00 | 107 | 106
2017-06-20 05:30 | 113 | 112
2017-06-20 06:00 | 124 | 123
2017-06-20 06:30 | 144 | 143
2017-06-20 07:00 | 161 | 160
2017-06-20 07:30 | 161 | 160
2017-06-20 08:00 | 165 | 164
2017-06-20 08:30 | 161 | 160
2017-06-20 09:00 | 155 | 154
2017-06-20 09:30 | 149 | 148
2017-06-20 10:00 | 145 | 144
2017-06-20 10:30 | 146 | 145
2017-06-20 11:00 | 139 | 138
2017-06-20 11:30 | 140 | 139
2017-06-20 12:00 | 139 | 137
2017-06-20 12:30 | 141 | 140
2017-06-20 13:00 | 142 | 141
2017-06-20 13:30 | 138 | 136
2017-06-20 14:00 | 120 | 117
2017-06-20 14:30 | 104 | 102
2017-06-20 15:00 | 102 | 100
2017-06-20 15:30 | 63 | 61
2017-06-20 16:00 | 56 | 54
2017-06-20 16:30 | 58 | 56
2017-06-20 17:00 | 66 | 64
2017-06-20 17:30 | 73 | 70
2017-06-20 18:00 | 100 | 98
2017-06-20 18:30 | 120 | 119
2017-06-20 19:00 | 124 | 123
2017-06-20 19:30 | 117 | 115
2017-06-20 20:00 | 107 | 105
2017-06-20 20:30 | 96 | 94
2017-06-20 21:00 | 90 | 88
2017-06-20 21:30 | 86 | 84
2017-06-20 22:00 | 80 | 77
2017-06-20 22:30 | 84 | 82
2017-06-20 23:00 | 104 | 102
2017-06-20 23:30 | 172 | 170
2017-06-21 | 168 | 166
2017-06-21 00:30 | 162 | 160
2017-06-21 01:00 | 157 | 155
2017-06-21 01:30 | 153 | 150
2017-06-21 02:00 | 150 | 148
2017-06-21 02:30 | 137 | 134
2017-06-21 03:00 | 134 | 130
2017-06-21 03:30 | 130 | 127
2017-06-21 04:00 | 130 | 127
2017-06-21 04:30 | 140 | 138
2017-06-21 05:00 | 162 | 159
2017-06-21 05:30 | 181 | 179
2017-06-21 06:00 | 192 | 191
2017-06-21 06:30 | 212 | 211
2017-06-21 07:00 | 222 | 220
2017-06-21 07:30 | 222 | 221
2017-06-21 08:00 | 234 | 233
2017-06-21 08:30 | 236 | 235
2017-06-21 09:00 | 230 | 229
2017-06-21 09:30 | 225 | 224
2017-06-21 10:00 | 222 | 221
2017-06-21 10:30 | 218 | 217
2017-06-21 11:00 | 208 | 207
2017-06-21 11:30 | 208 | 207
2017-06-21 12:00 | 204 | 203
2017-06-21 12:30 | 202 | 201
2017-06-21 13:00 | 204 | 202
2017-06-21 13:30 | 204 | 203
2017-06-21 14:00 | 203 | 202
2017-06-21 14:30 | 193 | 192
2017-06-21 15:00 | 190 | 188
2017-06-21 15:30 | 192 | 190
2017-06-21 16:00 | 200 | 198
2017-06-21 16:30 | 207 | 206
2017-06-21 17:00 | 212 | 210
2017-06-21 17:30 | 219 | 218
2017-06-21 18:00 | 248 | 247
2017-06-21 18:30 | 268 | 266
2017-06-21 19:00 | 272 | 271
2017-06-21 19:30 | 260 | 259
2017-06-21 20:00 | 250 | 249
2017-06-21 20:30 | 235 | 233
2017-06-21 21:00 | 222 | 220
2017-06-21 21:30 | 214 | 213
2017-06-21 22:00 | 210 | 209
2017-06-21 22:30 | 223 | 222
2017-06-21 23:00 | 215 | 214
2017-06-21 23:30 | 210 | 208
2017-06-22 | 199 | 197
2017-06-22 00:30 | 191 | 189
2017-06-22 01:00 | 183 | 181
2017-06-22 01:30 | 177 | 175
2017-06-22 02:00 | 173 | 171
2017-06-22 02:30 | 172 | 170
2017-06-22 03:00 | 173 | 171
2017-06-22 03:30 | 171 | 169
2017-06-22 04:00 | 170 | 169
2017-06-22 04:30 | 173 | 171
2017-06-22 05:00 | 177 | 175
2017-06-22 05:30 | 187 | 186
2017-06-22 06:00 | 193 | 192
2017-06-22 06:30 | 211 | 210
2017-06-22 07:00 | 232 | 231
2017-06-22 07:30 | 224 | 223
2017-06-22 08:00 | 228 | 227
2017-06-22 08:30 | 226 | 224
2017-06-22 09:00 | 250 | 248
2017-06-22 09:30 | 247 | 244
2017-06-22 10:00 | 241 | 239
2017-06-22 10:30 | 237 | 234
2017-06-22 11:00 | 238 | 236
2017-06-22 11:30 | 241 | 238
2017-06-22 12:00 | 243 | 240
2017-06-22 12:30 | 244 | 241
2017-06-22 13:00 | 210 | 206
2017-06-22 13:30 | 203 | 201
2017-06-22 14:00 | 199 | 196
2017-06-22 14:30 | 188 | 185
2017-06-22 15:00 | 187 | 184
2017-06-22 15:30 | 192 | 189
2017-06-22 16:00 | 201 | 199
2017-06-22 16:30 | 209 | 207
2017-06-22 17:00 | 217 | 215
2017-06-22 17:30 | 223 | 220
2017-06-22 18:00 | 246 | 244
2017-06-22 18:30 | 265 | 263
2017-06-22 19:00 | 269 | 267
2017-06-22 19:30 | 267 | 265
2017-06-22 20:00 | 257 | 255
2017-06-22 20:30 | 247 | 244
2017-06-22 21:00 | 262 | 259
2017-06-22 21:30 | 251 | 248
2017-06-22 22:00 | 239 | 236
2017-06-22 22:30 | 228 | 225
2017-06-22 23:00 | 214 | 211
2017-06-22 23:30 | 205 | 202
2017-06-23 | 196 | 193
2017-06-23 00:30 | 188 | 185
2017-06-23 01:00 | 184 | 181
2017-06-23 01:30 | 179 | 176
2017-06-23 02:00 | 175 | 172
2017-06-23 02:30 | 174 | 171
2017-06-23 03:00 | 170 | 167
2017-06-23 03:30 | 171 | 167
2017-06-23 04:00 | 172 | 169
2017-06-23 04:30 | 174 | 171
2017-06-23 05:00 | 178 | 175
2017-06-23 05:30 | 184 | 181
2017-06-23 06:00 | 195 | 192
2017-06-23 06:30 | 215 | 213
2017-06-23 07:00 | 227 | 224
2017-06-23 07:30 | 218 | 216
2017-06-23 08:00 | 224 | 222
2017-06-23 08:30 | 227 | 224
2017-06-23 09:00 | 219 | 217
2017-06-23 09:30 | 210 | 207
2017-06-23 10:00 | 205 | 202
2017-06-23 10:30 | 194 | 192
2017-06-23 11:00 | 192 | 189
2017-06-23 11:30 | 192 | 189
2017-06-23 12:00 | 189 | 186
2017-06-23 12:30 | 188 | 186
2017-06-23 13:00 | 193 | 191
2017-06-23 13:30 | 198 | 195
2017-06-23 14:00 | 198 | 196
2017-06-23 14:30 | 187 | 184
2017-06-23 15:00 | 190 | 187
2017-06-23 15:30 | 191 | 188
2017-06-23 16:00 | 194 | 191
2017-06-23 16:30 | 197 | 194
2017-06-23 17:00 | 202 | 200
2017-06-23 17:30 | 209 | 206
2017-06-23 18:00 | 231 | 229
2017-06-23 18:30 | 245 | 243
2017-06-23 19:00 | 249 | 247
2017-06-23 19:30 | 244 | 242
2017-06-23 20:00 | 234 | 231
2017-06-23 20:30 | 225 | 223
2017-06-23 21:00 | 219 | 217
2017-06-23 21:30 | 210 | 207
2017-06-23 22:00 | 199 | 197
2017-06-23 22:30 | 191 | 188
2017-06-23 23:00 | 185 | 182
2017-06-23 23:30 | 174 | 171
2017-06-24 | 167 | 164
2017-06-24 00:30 | 181 | 178
2017-06-24 01:00 | 183 | 179
2017-06-24 01:30 | 180 | 177
2017-06-24 02:00 | 175 | 172
2017-06-24 02:30 | 174 | 171
2017-06-24 03:00 | 173 | 171
2017-06-24 03:30 | 171 | 168
2017-06-24 04:00 | 165 | 162
2017-06-24 04:30 | 166 | 163
2017-06-24 05:00 | 167 | 165
2017-06-24 05:30 | 173 | 171
2017-06-24 06:00 | 177 | 174
2017-06-24 06:30 | 183 | 181
2017-06-24 07:00 | 184 | 182
2017-06-24 07:30 | 170 | 167
2017-06-24 08:00 | 179 | 176
2017-06-24 08:30 | 190 | 188
2017-06-24 09:00 | 194 | 192
2017-06-24 09:30 | 194 | 192
2017-06-24 10:00 | 192 | 189
2017-06-24 10:30 | 194 | 191
2017-06-24 11:00 | 192 | 189
2017-06-24 11:30 | 187 | 184
2017-06-24 12:00 | 186 | 183
2017-06-24 12:30 | 187 | 184
2017-06-24 13:00 | 181 | 179
2017-06-24 13:30 | 180 | 178
2017-06-24 14:00 | 180 | 178
2017-06-24 14:30 | 171 | 169
2017-06-24 15:00 | 168 | 165
2017-06-24 15:30 | 168 | 165
2017-06-24 16:00 | 171 | 169
2017-06-24 16:30 | 177 | 175
2017-06-24 17:00 | 187 | 185
2017-06-24 17:30 | 199 | 197
2017-06-24 18:00 | 225 | 223
2017-06-24 18:30 | 241 | 239
2017-06-24 19:00 | 241 | 238
2017-06-24 19:30 | 230 | 227
2017-06-24 20:00 | 220 | 218
2017-06-24 20:30 | 211 | 209
2017-06-24 21:00 | 202 | 200
2017-06-24 21:30 | 195 | 192
2017-06-24 22:00 | 188 | 185
2017-06-24 22:30 | 189 | 186
2017-06-24 23:00 | 181 | 178
2017-06-24 23:30 | 174 | 171
2017-06-25 | 166 | 163
2017-06-25 00:30 | 176 | 173
2017-06-25 01:00 | 174 | 171
2017-06-25 01:30 | 170 | 167
2017-06-25 02:00 | 164 | 161
2017-06-25 02:30 | 162 | 159
2017-06-25 03:00 | 164 | 162
2017-06-25 03:30 | 162 | 159
2017-06-25 04:00 | 162 | 159
2017-06-25 04:30 | 162 | 159
2017-06-25 05:00 | 165 | 162
2017-06-25 05:30 | 168 | 165
2017-06-25 06:00 | 168 | 165
2017-06-25 06:30 | 170 | 168
2017-06-25 07:00 | 155 | 152
2017-06-25 07:30 | 150 | 147
2017-06-25 08:00 | 156 | 154
2017-06-25 08:30 | 168 | 165
2017-06-25 09:00 | 175 | 173
2017-06-25 09:30 | 180 | 178
2017-06-25 10:00 | 179 | 177
2017-06-25 10:30 | 177 | 175
2017-06-25 11:00 | 177 | 175
2017-06-25 11:30 | 176 | 173
2017-06-25 12:00 | 172 | 170
2017-06-25 12:30 | 172 | 170
2017-06-25 13:00 | 169 | 167
2017-06-25 13:30 | 169 | 166
2017-06-25 14:00 | 170 | 168
2017-06-25 14:30 | 159 | 157
2017-06-25 15:00 | 156 | 153
2017-06-25 15:30 | 161 | 158
2017-06-25 16:00 | 167 | 165
2017-06-25 16:30 | 176 | 174
2017-06-25 17:00 | 185 | 183
2017-06-25 17:30 | 194 | 192
2017-06-25 18:00 | 221 | 220
2017-06-25 18:30 | 243 | 242
2017-06-25 19:00 | 245 | 243
2017-06-25 19:30 | 236 | 235
2017-06-25 20:00 | 224 | 222
2017-06-25 20:30 | 215 | 213
2017-06-25 21:00 | 205 | 203
2017-06-25 21:30 | 197 | 195
2017-06-25 22:00 | 194 | 192
2017-06-25 22:30 | 210 | 208
2017-06-25 23:00 | 199 | 196
2017-06-25 23:30 | 190 | 188
2017-06-26 | 184 | 181
2017-06-26 00:30 | 178 | 176
2017-06-26 01:00 | 173 | 170
2017-06-26 01:30 | 168 | 166
2017-06-26 02:00 | 165 | 162
2017-06-26 02:30 | 162 | 159
2017-06-26 03:00 | 157 | 154
2017-06-26 03:30 | 156 | 153
2017-06-26 04:00 | 157 | 155
2017-06-26 04:30 | 159 | 156
2017-06-26 05:00 | 161 | 158
2017-06-26 05:30 | 169 | 166
2017-06-26 06:00 | 178 | 175
2017-06-26 06:30 | 182 | 180
2017-06-26 07:00 | 180 | 178
2017-06-26 07:30 | 175 | 173
2017-06-26 08:00 | 181 | 179
2017-06-26 08:30 | 182 | 181
2017-06-26 09:00 | 180 | 178
2017-06-26 09:30 | 178 | 176
2017-06-26 10:00 | 178 | 176
2017-06-26 10:30 | 176 | 174
2017-06-26 11:00 | 170 | 168
2017-06-26 11:30 | 165 | 163
2017-06-26 12:00 | 166 | 164
2017-06-26 12:30 | 167 | 165
2017-06-26 13:00 | 169 | 168
2017-06-26 13:30 | 171 | 169
2017-06-26 14:00 | 172 | 170
2017-06-26 14:30 | 164 | 162
2017-06-26 15:00 | 162 | 161
2017-06-26 15:30 | 170 | 168
2017-06-26 16:00 | 175 | 173
2017-06-26 16:30 | 177 | 175
2017-06-26 17:00 | 184 | 182
2017-06-26 17:30 | 192 | 190
2017-06-26 18:00 | 207 | 206
2017-06-26 18:30 | 219 | 217
2017-06-26 19:00 | 220 | 219
2017-06-26 19:30 | 212 | 210
2017-06-26 20:00 | 214 | 213
2017-06-26 20:30 | 206 | 204
2017-06-26 21:00 | 196 | 194
2017-06-26 21:30 | 184 | 183
2017-06-26 22:00 | 178 | 176
2017-06-26 22:30 | 181 | 179
2017-06-26 23:00 | 199 | 197
2017-06-26 23:30 | 188 | 186
2017-06-27 | 175 | 173
2017-06-27 00:30 | 167 | 165
2017-06-27 01:00 | 157 | 155
2017-06-27 01:30 | 153 | 151
2017-06-27 02:00 | 150 | 148
2017-06-27 02:30 | 148 | 146
2017-06-27 03:00 | 145 | 143
2017-06-27 03:30 | 148 | 145
2017-06-27 04:00 | 148 | 145
2017-06-27 04:30 | 139 | 137
2017-06-27 05:00 | 121 | 119
2017-06-27 05:30 | 122 | 120
2017-06-27 06:00 | 131 | 129
2017-06-27 06:30 | 150 | 147
2017-06-27 07:00 | 162 | 160
2017-06-27 07:30 | 146 | 144
2017-06-27 08:00 | 151 | 149
2017-06-27 08:30 | 120 | 119
2017-06-27 09:00 | 86 | 84
2017-06-27 09:30 | 105 | 104
2017-06-27 10:00 | 123 | 122
2017-06-27 10:30 | 121 | 120
2017-06-27 11:00 | 119 | 118
2017-06-27 11:30 | 119 | 118
2017-06-27 12:00 | 110 | 108
2017-06-27 12:30 | 117 | 115
2017-06-27 13:00 | 116 | 115
2017-06-27 13:30 | 121 | 119
2017-06-27 14:00 | 122 | 120
2017-06-27 14:30 | 111 | 110
2017-06-27 15:00 | 106 | 104
2017-06-27 15:30 | 104 | 102
2017-06-27 16:00 | 106 | 104
2017-06-27 16:30 | 113 | 111
2017-06-27 17:00 | 97 | 95
2017-06-27 17:30 | 99 | 97
2017-06-27 18:00 | 73 | 70
2017-06-27 18:30 | 91 | 89
2017-06-27 19:00 | 101 | 99
2017-06-27 19:30 | 119 | 117
2017-06-27 20:00 | 131 | 129
2017-06-27 20:30 | 128 | 126
2017-06-27 21:00 | 117 | 115
2017-06-27 21:30 | 108 | 106
2017-06-27 22:00 | 104 | 102
2017-06-27 22:30 | 121 | 119
2017-06-27 23:00 | 108 | 106
2017-06-27 23:30 | 109 | 107
2017-06-28 | 111 | 110
2017-06-28 00:30 | 106 | 104
2017-06-28 01:00 | 100 | 98
2017-06-28 01:30 | 86 | 84
2017-06-28 02:00 | 87 | 84
2017-06-28 02:30 | 90 | 88
2017-06-28 03:00 | 90 | 88
2017-06-28 03:30 | 91 | 88
2017-06-28 04:00 | 91 | 89
2017-06-28 04:30 | 100 | 98
2017-06-28 05:00 | 112 | 110
2017-06-28 05:30 | 121 | 119
2017-06-28 06:00 | 131 | 130
2017-06-28 06:30 | 140 | 139
2017-06-28 07:00 | 123 | 121
2017-06-28 07:30 | 94 | 92
2017-06-28 08:00 | 105 | 103
2017-06-28 08:30 | 95 | 93
2017-06-28 09:00 | 113 | 111
2017-06-28 09:30 | 125 | 123
2017-06-28 10:00 | 128 | 126
2017-06-28 10:30 | 121 | 120
2017-06-28 11:00 | 118 | 117
2017-06-28 11:30 | 115 | 114
2017-06-28 12:00 | 116 | 115
2017-06-28 12:30 | 118 | 117
2017-06-28 13:00 | 123 | 122
2017-06-28 13:30 | 129 | 128
2017-06-28 14:00 | 137 | 136
2017-06-28 14:30 | 131 | 130
2017-06-28 15:00 | 127 | 125
2017-06-28 15:30 | 132 | 131
2017-06-28 16:00 | 133 | 132
2017-06-28 16:30 | 122 | 120
2017-06-28 17:00 | 97 | 95
2017-06-28 17:30 | 68 | 66
2017-06-28 18:00 | 72 | 69
2017-06-28 18:30 | 84 | 81
2017-06-28 19:00 | 88 | 86
2017-06-28 19:30 | 86 | 84
2017-06-28 20:00 | 101 | 100
2017-06-28 20:30 | 112 | 110
2017-06-28 21:00 | 132 | 131
2017-06-28 21:30 | 129 | 127
2017-06-28 22:00 | 124 | 123
2017-06-28 22:30 | 146 | 144
2017-06-28 23:00 | 136 | 134
2017-06-28 23:30 | 128 | 126
2017-06-29 | 121 | 119
2017-06-29 00:30 | 138 | 136
2017-06-29 01:00 | 174 | 172
2017-06-29 01:30 | 172 | 171
2017-06-29 02:00 | 171 | 169
2017-06-29 02:30 | 167 | 165
2017-06-29 03:00 | 165 | 164
2017-06-29 03:30 | 165 | 163
2017-06-29 04:00 | 165 | 163
2017-06-29 04:30 | 163 | 161
2017-06-29 05:00 | 163 | 161
2017-06-29 05:30 | 171 | 170
2017-06-29 06:00 | 180 | 179
2017-06-29 06:30 | 192 | 190
2017-06-29 07:00 | 198 | 197
2017-06-29 07:30 | 183 | 182
2017-06-29 08:00 | 185 | 184
2017-06-29 08:30 | 200 | 199
2017-06-29 09:00 | 201 | 199
2017-06-29 09:30 | 202 | 200
2017-06-29 10:00 | 202 | 201
2017-06-29 10:30 | 198 | 196
2017-06-29 11:00 | 197 | 195
2017-06-29 11:30 | 193 | 191
2017-06-29 12:00 | 190 | 188
2017-06-29 12:30 | 193 | 191
2017-06-29 13:00 | 197 | 195
2017-06-29 13:30 | 196 | 194
2017-06-29 14:00 | 194 | 192
2017-06-29 14:30 | 186 | 184
2017-06-29 15:00 | 181 | 179
2017-06-29 15:30 | 184 | 182
2017-06-29 16:00 | 185 | 183
2017-06-29 16:30 | 190 | 188
2017-06-29 17:00 | 189 | 187
2017-06-29 17:30 | 182 | 180
2017-06-29 18:00 | 196 | 194
2017-06-29 18:30 | 209 | 207
2017-06-29 19:00 | 228 | 226
2017-06-29 19:30 | 227 | 226
2017-06-29 20:00 | 231 | 229
2017-06-29 20:30 | 224 | 222
2017-06-29 21:00 | 216 | 214
2017-06-29 21:30 | 204 | 202
2017-06-29 22:00 | 194 | 192
2017-06-29 22:30 | 179 | 176
2017-06-29 23:00 | 175 | 173
2017-06-29 23:30 | 197 | 195
2017-06-30 | 190 | 187
2017-06-30 00:30 | 184 | 182
2017-06-30 01:00 | 178 | 176
2017-06-30 01:30 | 172 | 171
2017-06-30 02:00 | 170 | 169
2017-06-30 02:30 | 170 | 168
2017-06-30 03:00 | 168 | 167
2017-06-30 03:30 | 167 | 166
2017-06-30 04:00 | 166 | 165
2017-06-30 04:30 | 167 | 166
2017-06-30 05:00 | 170 | 168
2017-06-30 05:30 | 175 | 174
2017-06-30 06:00 | 183 | 181
2017-06-30 06:30 | 201 | 200
2017-06-30 07:00 | 185 | 183
2017-06-30 07:30 | 172 | 170
2017-06-30 08:00 | 174 | 172
2017-06-30 08:30 | 185 | 183
2017-06-30 09:00 | 203 | 202
2017-06-30 09:30 | 205 | 204
2017-06-30 10:00 | 199 | 197
2017-06-30 10:30 | 194 | 192
2017-06-30 11:00 | 189 | 188
2017-06-30 11:30 | 195 | 193
2017-06-30 12:00 | 198 | 196
2017-06-30 12:30 | 198 | 196
2017-06-30 13:00 | 195 | 193
2017-06-30 13:30 | 192 | 190
2017-06-30 14:00 | 190 | 188
2017-06-30 14:30 | 181 | 180
2017-06-30 15:00 | 180 | 178
2017-06-30 15:30 | 186 | 184
2017-06-30 16:00 | 186 | 184
2017-06-30 16:30 | 188 | 186
2017-06-30 17:00 | 191 | 189
2017-06-30 17:30 | 196 | 194
2017-06-30 18:00 | 194 | 192
2017-06-30 18:30 | 198 | 196
2017-06-30 19:00 | 211 | 209
2017-06-30 19:30 | 207 | 205
2017-06-30 20:00 | 207 | 206
2017-06-30 20:30 | 205 | 204
2017-06-30 21:00 | 199 | 198
2017-06-30 21:30 | 187 | 186
2017-06-30 22:00 | 184 | 183
2017-06-30 22:30 | 207 | 206
2017-06-30 23:00 | 197 | 196
2017-06-30 23:30 | 186 | 185
2017-07-01 | 178 | 177
2017-07-01 00:30 | 172 | 171
2017-07-01 01:00 | 168 | 167
2017-07-01 01:30 | 163 | 162
2017-07-01 02:00 | 160 | 159
2017-07-01 02:30 | 157 | 156
2017-07-01 03:00 | 154 | 152
2017-07-01 03:30 | 153 | 152
2017-07-01 04:00 | 153 | 152
2017-07-01 04:30 | 153 | 152
2017-07-01 05:00 | 153 | 152
2017-07-01 05:30 | 156 | 155
2017-07-01 06:00 | 147 | 146
2017-07-01 06:30 | 151 | 150
2017-07-01 07:00 | 159 | 158
2017-07-01 07:30 | 154 | 153
2017-07-01 08:00 | 164 | 163
2017-07-01 08:30 | 179 | 178
2017-07-01 09:00 | 185 | 184
2017-07-01 09:30 | 184 | 183
2017-07-01 10:00 | 180 | 179
2017-07-01 10:30 | 178 | 177
2017-07-01 11:00 | 178 | 177
2017-07-01 11:30 | 172 | 171
2017-07-01 12:00 | 175 | 174
2017-07-01 12:30 | 178 | 177
2017-07-01 13:00 | 172 | 171
2017-07-01 13:30 | 168 | 167
2017-07-01 14:00 | 167 | 165
2017-07-01 14:30 | 154 | 153
2017-07-01 15:00 | 153 | 152
2017-07-01 15:30 | 157 | 156
2017-07-01 16:00 | 160 | 159
2017-07-01 16:30 | 166 | 165
2017-07-01 17:00 | 174 | 173
2017-07-01 17:30 | 185 | 184
2017-07-01 18:00 | 205 | 204
2017-07-01 18:30 | 210 | 209
2017-07-01 19:00 | 217 | 216
2017-07-01 19:30 | 217 | 216
2017-07-01 20:00 | 212 | 211
2017-07-01 20:30 | 191 | 190
2017-07-01 21:00 | 190 | 189
2017-07-01 21:30 | 184 | 183
2017-07-01 22:00 | 182 | 181
2017-07-01 22:30 | 200 | 199
2017-07-01 23:00 | 195 | 194
2017-07-01 23:30 | 187 | 187
2017-07-02 | 181 | 180
2017-07-02 00:30 | 174 | 173
2017-07-02 01:00 | 170 | 169
2017-07-02 01:30 | 167 | 166
2017-07-02 02:00 | 161 | 160
2017-07-02 02:30 | 158 | 156
2017-07-02 03:00 | 155 | 155
2017-07-02 03:30 | 157 | 156
2017-07-02 04:00 | 157 | 156
2017-07-02 04:30 | 157 | 156
2017-07-02 05:00 | 160 | 159
2017-07-02 05:30 | 161 | 160
2017-07-02 06:00 | 153 | 152
2017-07-02 06:30 | 145 | 144
2017-07-02 07:00 | 141 | 140
2017-07-02 07:30 | 150 | 149
2017-07-02 08:00 | 160 | 160
2017-07-02 08:30 | 175 | 174
2017-07-02 09:00 | 185 | 184
2017-07-02 09:30 | 192 | 192
2017-07-02 10:00 | 193 | 192
2017-07-02 10:30 | 188 | 187
2017-07-02 11:00 | 180 | 180
2017-07-02 11:30 | 150 | 149
2017-07-02 12:00 | 142 | 141
2017-07-02 12:30 | 142 | 141
2017-07-02 13:00 | 150 | 149
2017-07-02 13:30 | 151 | 150
2017-07-02 14:00 | 147 | 146
2017-07-02 14:30 | 148 | 147
2017-07-02 15:00 | 159 | 158
2017-07-02 15:30 | 158 | 157
2017-07-02 16:00 | 161 | 160
2017-07-02 16:30 | 169 | 168
2017-07-02 17:00 | 175 | 174
2017-07-02 17:30 | 198 | 197
2017-07-02 18:00 | 202 | 201
2017-07-02 18:30 | 217 | 217
2017-07-02 19:00 | 223 | 222
2017-07-02 19:30 | 219 | 218
2017-07-02 20:00 | 211 | 210
2017-07-02 20:30 | 198 | 196
2017-07-02 21:00 | 189 | 188
2017-07-02 21:30 | 188 | 186
2017-07-02 22:00 | 182 | 181
2017-07-02 22:30 | 169 | 167
2017-07-02 23:00 | 164 | 162
2017-07-02 23:30 | 183 | 181
2017-07-03 | 177 | 176
2017-07-03 00:30 | 173 | 171
2017-07-03 01:00 | 170 | 169
2017-07-03 01:30 | 167 | 166
2017-07-03 02:00 | 161 | 160
2017-07-03 02:30 | 159 | 158
2017-07-03 03:00 | 161 | 159
2017-07-03 03:30 | 162 | 160
2017-07-03 04:00 | 160 | 159
2017-07-03 04:30 | 162 | 161
2017-07-03 05:00 | 146 | 145
2017-07-03 05:30 | 127 | 126
2017-07-03 06:00 | 128 | 126
2017-07-03 06:30 | 143 | 142
2017-07-03 07:00 | 158 | 156
2017-07-03 07:30 | 172 | 171
2017-07-03 08:00 | 181 | 180
2017-07-03 08:30 | 174 | 173
2017-07-03 09:00 | 191 | 190
2017-07-03 09:30 | 187 | 186
2017-07-03 10:00 | 200 | 199
2017-07-03 10:30 | 200 | 199
2017-07-03 11:00 | 197 | 196
2017-07-03 11:30 | 187 | 186
2017-07-03 12:00 | 190 | 189
2017-07-03 12:30 | 184 | 183
2017-07-03 13:00 | 190 | 188
2017-07-03 13:30 | 191 | 190
2017-07-03 14:00 | 190 | 188
2017-07-03 14:30 | 181 | 180
2017-07-03 15:00 | 175 | 174
2017-07-03 15:30 | 179 | 177
2017-07-03 16:00 | 179 | 178
2017-07-03 16:30 | 183 | 182
2017-07-03 17:00 | 192 | 190
2017-07-03 17:30 | 200 | 199
2017-07-03 18:00 | 225 | 224
2017-07-03 18:30 | 245 | 244
2017-07-03 19:00 | 246 | 245
2017-07-03 19:30 | 237 | 236
2017-07-03 20:00 | 226 | 225
2017-07-03 20:30 | 215 | 213
2017-07-03 21:00 | 203 | 201
2017-07-03 21:30 | 193 | 191
2017-07-03 22:00 | 177 | 176
2017-07-03 22:30 | 163 | 162
2017-07-03 23:00 | 161 | 159
2017-07-03 23:30 | 186 | 184
2017-07-04 | 179 | 177
2017-07-04 00:30 | 172 | 170
2017-07-04 01:00 | 167 | 166
2017-07-04 01:30 | 163 | 161
2017-07-04 02:00 | 159 | 158
2017-07-04 02:30 | 161 | 159
2017-07-04 03:00 | 160 | 158
2017-07-04 03:30 | 158 | 156
2017-07-04 04:00 | 159 | 157
2017-07-04 04:30 | 161 | 160
2017-07-04 05:00 | 166 | 164
2017-07-04 05:30 | 171 | 169
2017-07-04 06:00 | 181 | 180
2017-07-04 06:30 | 191 | 190
2017-07-04 07:00 | 172 | 171
2017-07-04 07:30 | 184 | 183
2017-07-04 08:00 | 196 | 195
2017-07-04 08:30 | 201 | 200
2017-07-04 09:00 | 201 | 199
2017-07-04 09:30 | 202 | 201
2017-07-04 10:00 | 202 | 201
2017-07-04 10:30 | 188 | 187
2017-07-04 11:00 | 167 | 165
2017-07-04 11:30 | 161 | 160
2017-07-04 12:00 | 158 | 157
2017-07-04 12:30 | 156 | 155
2017-07-04 13:00 | 161 | 159
2017-07-04 13:30 | 163 | 161
2017-07-04 14:00 | 156 | 155
2017-07-04 14:30 | 118 | 116
2017-07-04 15:00 | 102 | 100
2017-07-04 15:30 | 114 | 112
2017-07-04 16:00 | 120 | 118
2017-07-04 16:30 | 124 | 123
2017-07-04 17:00 | 129 | 128
2017-07-04 17:30 | 98 | 96
2017-07-04 18:00 | 99 | 98
2017-07-04 18:30 | 117 | 116
2017-07-04 19:00 | 124 | 123
2017-07-04 19:30 | 115 | 113
2017-07-04 20:00 | 106 | 104
2017-07-04 20:30 | 131 | 129
2017-07-04 21:00 | 144 | 143
2017-07-04 21:30 | 140 | 138
2017-07-04 22:00 | 133 | 131
2017-07-04 22:30 | 148 | 147
2017-07-04 23:00 | 139 | 137
2017-07-04 23:30 | 126 | 124
2017-07-05 | 117 | 116
2017-07-05 00:30 | 111 | 110
2017-07-05 01:00 | 103 | 102
2017-07-05 01:30 | 99 | 98
2017-07-05 02:00 | 97 | 95
2017-07-05 02:30 | 94 | 92
2017-07-05 03:00 | 94 | 92
2017-07-05 03:30 | 93 | 91
2017-07-05 04:00 | 92 | 90
2017-07-05 04:30 | 93 | 91
2017-07-05 05:00 | 98 | 96
2017-07-05 05:30 | 107 | 105
2017-07-05 06:00 | 109 | 107
2017-07-05 06:30 | 81 | 79
2017-07-05 07:00 | 91 | 89
2017-07-05 07:30 | 101 | 100
2017-07-05 08:00 | 108 | 107
2017-07-05 08:30 | 114 | 112
2017-07-05 09:00 | 114 | 113
2017-07-05 09:30 | 112 | 110
2017-07-05 10:00 | 105 | 104
2017-07-05 10:30 | 104 | 102
2017-07-05 11:00 | 100 | 98
2017-07-05 11:30 | 98 | 96
2017-07-05 12:00 | 91 | 89
2017-07-05 12:30 | 89 | 88
2017-07-05 13:00 | 89 | 87
2017-07-05 13:30 | 88 | 87
2017-07-05 14:00 | 91 | 90
2017-07-05 14:30 | 95 | 94
2017-07-05 15:00 | 96 | 95
2017-07-05 15:30 | 101 | 99
2017-07-05 16:00 | 109 | 107
2017-07-05 16:30 | 116 | 115
2017-07-05 17:00 | 124 | 123
2017-07-05 17:30 | 89 | 88
2017-07-05 18:00 | 105 | 104
2017-07-05 18:30 | 121 | 120
2017-07-05 19:00 | 128 | 126
2017-07-05 19:30 | 119 | 118
2017-07-05 20:00 | 108 | 107
2017-07-05 20:30 | 97 | 95
2017-07-05 21:00 | 87 | 86
2017-07-05 21:30 | 114 | 113
2017-07-05 22:00 | 123 | 121
2017-07-05 22:30 | 147 | 146
2017-07-05 23:00 | 138 | 137
2017-07-05 23:30 | 137 | 136
2017-07-06 | 125 | 123
2017-07-06 00:30 | 141 | 140
2017-07-06 01:00 | 176 | 175
2017-07-06 01:30 | 171 | 170
2017-07-06 02:00 | 159 | 159
2017-07-06 02:30 | 154 | 153
2017-07-06 03:00 | 155 | 154
2017-07-06 03:30 | 157 | 156
2017-07-06 04:00 | 158 | 157
2017-07-06 04:30 | 162 | 161
2017-07-06 05:00 | 164 | 164
2017-07-06 05:30 | 176 | 175
2017-07-06 06:00 | 187 | 186
2017-07-06 06:30 | 205 | 204
2017-07-06 07:00 | 222 | 221
2017-07-06 07:30 | 211 | 210
2017-07-06 08:00 | 219 | 218
2017-07-06 08:30 | 225 | 224
2017-07-06 09:00 | 222 | 221
2017-07-06 09:30 | 215 | 214
2017-07-06 10:00 | 212 | 211
2017-07-06 10:30 | 206 | 205
2017-07-06 11:00 | 200 | 199
2017-07-06 11:30 | 196 | 195
2017-07-06 12:00 | 195 | 194
2017-07-06 12:30 | 188 | 187
2017-07-06 13:00 | 190 | 189
2017-07-06 13:30 | 191 | 190
2017-07-06 14:00 | 189 | 188
2017-07-06 14:30 | 180 | 179
2017-07-06 15:00 | 181 | 180
2017-07-06 15:30 | 186 | 184
2017-07-06 16:00 | 194 | 193
2017-07-06 16:30 | 189 | 188
2017-07-06 17:00 | 193 | 192
2017-07-06 17:30 | 197 | 196
2017-07-06 18:00 | 209 | 207
2017-07-06 18:30 | 224 | 223
2017-07-06 19:00 | 232 | 230
2017-07-06 19:30 | 228 | 227
2017-07-06 20:00 | 217 | 216
2017-07-06 20:30 | 209 | 207
2017-07-06 21:00 | 197 | 195
2017-07-06 21:30 | 185 | 184
2017-07-06 22:00 | 180 | 178
2017-07-06 22:30 | 205 | 203
2017-07-06 23:00 | 199 | 197
2017-07-06 23:30 | 193 | 191
2017-07-07 | 183 | 180
2017-07-07 00:30 | 175 | 172
2017-07-07 01:00 | 171 | 168
2017-07-07 01:30 | 161 | 158
2017-07-07 02:00 | 158 | 156
2017-07-07 02:30 | 156 | 155
2017-07-07 03:00 | 156 | 155
2017-07-07 03:30 | 156 | 155
2017-07-07 04:00 | 159 | 158
2017-07-07 04:30 | 160 | 159
2017-07-07 05:00 | 159 | 157
2017-07-07 05:30 | 166 | 164
2017-07-07 06:00 | 180 | 178
2017-07-07 06:30 | 196 | 195
2017-07-07 07:00 | 204 | 202
2017-07-07 07:30 | 191 | 190
2017-07-07 08:00 | 196 | 194
2017-07-07 08:30 | 199 | 198
2017-07-07 09:00 | 199 | 198
2017-07-07 09:30 | 198 | 197
2017-07-07 10:00 | 195 | 193
2017-07-07 10:30 | 193 | 192
2017-07-07 11:00 | 184 | 182
2017-07-07 11:30 | 175 | 172
2017-07-07 12:00 | 172 | 170
2017-07-07 12:30 | 168 | 166
2017-07-07 13:00 | 168 | 166
2017-07-07 13:30 | 168 | 165
2017-07-07 14:00 | 168 | 166
2017-07-07 14:30 | 156 | 154
2017-07-07 15:00 | 162 | 159
2017-07-07 15:30 | 169 | 166
2017-07-07 16:00 | 175 | 173
2017-07-07 16:30 | 183 | 181
2017-07-07 17:00 | 192 | 189
2017-07-07 17:30 | 198 | 196
2017-07-07 18:00 | 212 | 209
2017-07-07 18:30 | 227 | 225
2017-07-07 19:00 | 240 | 237
2017-07-07 19:30 | 232 | 229
2017-07-07 20:00 | 222 | 219
2017-07-07 20:30 | 209 | 206
2017-07-07 21:00 | 204 | 200
2017-07-07 21:30 | 197 | 193
2017-07-07 22:00 | 188 | 184
2017-07-07 22:30 | 173 | 169
2017-07-07 23:00 | 160 | 156
2017-07-07 23:30 | 161 | 157
2017-07-08 | 183 | 179
2017-07-08 00:30 | 179 | 175
2017-07-08 01:00 | 172 | 168
2017-07-08 01:30 | 167 | 163
2017-07-08 02:00 | 163 | 160
2017-07-08 02:30 | 162 | 159
2017-07-08 03:00 | 159 | 156
2017-07-08 03:30 | 159 | 155
2017-07-08 04:00 | 162 | 159
2017-07-08 04:30 | 167 | 163
2017-07-08 05:00 | 167 | 163
2017-07-08 05:30 | 170 | 167
2017-07-08 06:00 | 170 | 167
2017-07-08 06:30 | 176 | 174
2017-07-08 07:00 | 175 | 172
2017-07-08 07:30 | 160 | 156
2017-07-08 08:00 | 169 | 166
2017-07-08 08:30 | 174 | 170
2017-07-08 09:00 | 176 | 173
2017-07-08 09:30 | 179 | 176
2017-07-08 10:00 | 179 | 176
2017-07-08 10:30 | 175 | 171
2017-07-08 11:00 | 153 | 150
2017-07-08 11:30 | 144 | 140
2017-07-08 12:00 | 140 | 137
2017-07-08 12:30 | 135 | 132
2017-07-08 13:00 | 133 | 129
2017-07-08 13:30 | 131 | 127
2017-07-08 14:00 | 131 | 127
2017-07-08 14:30 | 133 | 129
2017-07-08 15:00 | 137 | 133
2017-07-08 15:30 | 145 | 142
2017-07-08 16:00 | 151 | 147
2017-07-08 16:30 | 158 | 155
2017-07-08 17:00 | 173 | 170
2017-07-08 17:30 | 183 | 180
2017-07-08 18:00 | 191 | 188
2017-07-08 18:30 | 207 | 205
2017-07-08 19:00 | 216 | 212
2017-07-08 19:30 | 216 | 213
2017-07-08 20:00 | 214 | 210
2017-07-08 20:30 | 211 | 207
2017-07-08 21:00 | 199 | 196
2017-07-08 21:30 | 190 | 186
2017-07-08 22:00 | 191 | 187
2017-07-08 22:30 | 203 | 199
2017-07-08 23:00 | 201 | 196
2017-07-08 23:30 | 189 | 184
2017-07-09 | 180 | 175
2017-07-09 00:30 | 173 | 168
2017-07-09 01:00 | 168 | 163
2017-07-09 01:30 | 164 | 161
2017-07-09 02:00 | 158 | 155
2017-07-09 02:30 | 156 | 153
2017-07-09 03:00 | 155 | 151
2017-07-09 03:30 | 155 | 152
2017-07-09 04:00 | 155 | 152
2017-07-09 04:30 | 146 | 142
2017-07-09 05:00 | 124 | 119
2017-07-09 05:30 | 122 | 117
2017-07-09 06:00 | 125 | 121
2017-07-09 06:30 | 125 | 121
2017-07-09 07:00 | 129 | 125
2017-07-09 07:30 | 138 | 134
2017-07-09 08:00 | 143 | 139
2017-07-09 08:30 | 150 | 146
2017-07-09 09:00 | 151 | 148
2017-07-09 09:30 | 158 | 155
2017-07-09 10:00 | 157 | 154
2017-07-09 10:30 | 156 | 153
2017-07-09 11:00 | 152 | 150
2017-07-09 11:30 | 150 | 147
2017-07-09 12:00 | 145 | 142
2017-07-09 12:30 | 144 | 141
2017-07-09 13:00 | 142 | 139
2017-07-09 13:30 | 143 | 140
2017-07-09 14:00 | 140 | 137
2017-07-09 14:30 | 133 | 129
2017-07-09 15:00 | 133 | 129
2017-07-09 15:30 | 139 | 136
2017-07-09 16:00 | 144 | 141
2017-07-09 16:30 | 152 | 149
2017-07-09 17:00 | 162 | 159
2017-07-09 17:30 | 169 | 166
2017-07-09 18:00 | 197 | 194
2017-07-09 18:30 | 215 | 212
2017-07-09 19:00 | 222 | 219
2017-07-09 19:30 | 215 | 212
2017-07-09 20:00 | 201 | 198
2017-07-09 20:30 | 189 | 185
2017-07-09 21:00 | 182 | 178
2017-07-09 21:30 | 174 | 170
2017-07-09 22:00 | 165 | 161
2017-07-09 22:30 | 162 | 157
2017-07-09 23:00 | 181 | 177
2017-07-09 23:30 | 174 | 170
2017-07-10 | 166 | 161
2017-07-10 00:30 | 159 | 154
2017-07-10 01:00 | 153 | 149
2017-07-10 01:30 | 147 | 144
2017-07-10 02:00 | 147 | 143
2017-07-10 02:30 | 146 | 143
2017-07-10 03:00 | 147 | 143
2017-07-10 03:30 | 146 | 143
2017-07-10 04:00 | 147 | 143
2017-07-10 04:30 | 149 | 146
2017-07-10 05:00 | 151 | 147
2017-07-10 05:30 | 158 | 155
2017-07-10 06:00 | 166 | 163
2017-07-10 06:30 | 180 | 177
2017-07-10 07:00 | 187 | 184
2017-07-10 07:30 | 193 | 191
2017-07-10 08:00 | 209 | 207
2017-07-10 08:30 | 213 | 210
2017-07-10 09:00 | 211 | 209
2017-07-10 09:30 | 203 | 200
2017-07-10 10:00 | 197 | 195
2017-07-10 10:30 | 190 | 187
2017-07-10 11:00 | 187 | 184
2017-07-10 11:30 | 181 | 177
2017-07-10 12:00 | 181 | 177
2017-07-10 12:30 | 180 | 177
2017-07-10 13:00 | 181 | 177
2017-07-10 13:30 | 181 | 177
2017-07-10 14:00 | 182 | 178
2017-07-10 14:30 | 171 | 167
2017-07-10 15:00 | 170 | 166
2017-07-10 15:30 | 176 | 172
2017-07-10 16:00 | 181 | 177
2017-07-10 16:30 | 190 | 186
2017-07-10 17:00 | 195 | 191
2017-07-10 17:30 | 203 | 199
2017-07-10 18:00 | 203 | 199
2017-07-10 18:30 | 219 | 215
2017-07-10 19:00 | 224 | 221
2017-07-10 19:30 | 227 | 224
2017-07-10 20:00 | 220 | 216
2017-07-10 20:30 | 209 | 206
2017-07-10 21:00 | 196 | 192
2017-07-10 21:30 | 181 | 177
2017-07-10 22:00 | 173 | 169
2017-07-10 22:30 | 169 | 164
2017-07-10 23:00 | 187 | 182
2017-07-10 23:30 | 182 | 177
2017-07-11 | 173 | 168
2017-07-11 00:30 | 165 | 161
2017-07-11 01:00 | 162 | 158
2017-07-11 01:30 | 160 | 156
2017-07-11 02:00 | 156 | 152
2017-07-11 02:30 | 151 | 148
2017-07-11 03:00 | 150 | 147
2017-07-11 03:30 | 150 | 147
2017-07-11 04:00 | 150 | 147
2017-07-11 04:30 | 152 | 149
2017-07-11 05:00 | 158 | 155
2017-07-11 05:30 | 169 | 166
2017-07-11 06:00 | 176 | 173
2017-07-11 06:30 | 193 | 190
2017-07-11 07:00 | 206 | 203
2017-07-11 07:30 | 196 | 193
2017-07-11 08:00 | 200 | 197
2017-07-11 08:30 | 201 | 198
2017-07-11 09:00 | 198 | 195
2017-07-11 09:30 | 196 | 193
2017-07-11 10:00 | 192 | 188
2017-07-11 10:30 | 189 | 186
2017-07-11 11:00 | 165 | 161
2017-07-11 11:30 | 160 | 155
2017-07-11 12:00 | 158 | 153
2017-07-11 12:30 | 154 | 150
2017-07-11 13:00 | 157 | 153
2017-07-11 13:30 | 161 | 157
2017-07-11 14:00 | 155 | 151
2017-07-11 14:30 | 118 | 112
2017-07-11 15:00 | 107 | 101
2017-07-11 15:30 | 115 | 111
2017-07-11 16:00 | 119 | 114
2017-07-11 16:30 | 124 | 119
2017-07-11 17:00 | 131 | 127
2017-07-11 17:30 | 122 | 117
2017-07-11 18:00 | 102 | 98
2017-07-11 18:30 | 132 | 129
2017-07-11 19:00 | 133 | 130
2017-07-11 19:30 | 128 | 125
2017-07-11 20:00 | 135 | 132
2017-07-11 20:30 | 135 | 132
2017-07-11 21:00 | 138 | 135
2017-07-11 21:30 | 124 | 121
2017-07-11 22:00 | 114 | 111
2017-07-11 22:30 | 109 | 105
2017-07-11 23:00 | 132 | 129
2017-07-11 23:30 | 127 | 123
2017-07-12 | 118 | 114
2017-07-12 00:30 | 110 | 107
2017-07-12 01:00 | 100 | 98
2017-07-12 01:30 | 100 | 98
2017-07-12 02:00 | 104 | 101
2017-07-12 02:30 | 100 | 97
2017-07-12 03:00 | 98 | 96
2017-07-12 03:30 | 95 | 92
2017-07-12 04:00 | 97 | 95
2017-07-12 04:30 | 98 | 95
2017-07-12 05:00 | 105 | 103
2017-07-12 05:30 | 114 | 112
2017-07-12 06:00 | 123 | 121
2017-07-12 06:30 | 138 | 137
2017-07-12 07:00 | 149 | 147
2017-07-12 07:30 | 136 | 134
2017-07-12 08:00 | 102 | 99
2017-07-12 08:30 | 104 | 101
2017-07-12 09:00 | 140 | 139
2017-07-12 09:30 | 137 | 136
2017-07-12 10:00 | 132 | 130
2017-07-12 10:30 | 127 | 125
2017-07-12 11:00 | 124 | 122
2017-07-12 11:30 | 123 | 121
2017-07-12 12:00 | 126 | 124
2017-07-12 12:30 | 121 | 119
2017-07-12 13:00 | 117 | 115
2017-07-12 13:30 | 120 | 118
2017-07-12 14:00 | 120 | 118
2017-07-12 14:30 | 112 | 110
2017-07-12 15:00 | 110 | 108
2017-07-12 15:30 | 113 | 111
2017-07-12 16:00 | 120 | 118
2017-07-12 16:30 | 122 | 120
2017-07-12 17:00 | 134 | 132
2017-07-12 17:30 | 116 | 114
2017-07-12 18:00 | 111 | 109
2017-07-12 18:30 | 128 | 126
2017-07-12 19:00 | 132 | 130
2017-07-12 19:30 | 123 | 122
2017-07-12 20:00 | 112 | 111
2017-07-12 20:30 | 103 | 101
2017-07-12 21:00 | 88 | 86
2017-07-12 21:30 | 114 | 112
2017-07-12 22:00 | 123 | 122
2017-07-12 22:30 | 108 | 106
2017-07-12 23:00 | 97 | 95
2017-07-12 23:30 | 125 | 123
2017-07-13 | 131 | 129
2017-07-13 00:30 | 150 | 149
2017-07-13 01:00 | 177 | 176
2017-07-13 01:30 | 175 | 173
2017-07-13 02:00 | 170 | 169
2017-07-13 02:30 | 169 | 167
2017-07-13 03:00 | 163 | 162
2017-07-13 03:30 | 162 | 160
2017-07-13 04:00 | 160 | 158
2017-07-13 04:30 | 159 | 157
2017-07-13 05:00 | 160 | 158
2017-07-13 05:30 | 169 | 167
2017-07-13 06:00 | 175 | 173
2017-07-13 06:30 | 191 | 189
2017-07-13 07:00 | 183 | 181
2017-07-13 07:30 | 193 | 191
2017-07-13 08:00 | 205 | 204
2017-07-13 08:30 | 207 | 205
2017-07-13 09:00 | 200 | 199
2017-07-13 09:30 | 194 | 193
2017-07-13 10:00 | 189 | 187
2017-07-13 10:30 | 190 | 188
2017-07-13 11:00 | 185 | 183
2017-07-13 11:30 | 180 | 178
2017-07-13 12:00 | 182 | 180
2017-07-13 12:30 | 188 | 187
2017-07-13 13:00 | 187 | 185
2017-07-13 13:30 | 184 | 182
2017-07-13 14:00 | 183 | 181
2017-07-13 14:30 | 177 | 175
2017-07-13 15:00 | 175 | 173
2017-07-13 15:30 | 176 | 174
2017-07-13 16:00 | 179 | 177
2017-07-13 16:30 | 185 | 183
2017-07-13 17:00 | 191 | 189
2017-07-13 17:30 | 198 | 196
2017-07-13 18:00 | 218 | 216
2017-07-13 18:30 | 235 | 233
2017-07-13 19:00 | 240 | 237
2017-07-13 19:30 | 233 | 231
2017-07-13 20:00 | 223 | 220
2017-07-13 20:30 | 213 | 211
2017-07-13 21:00 | 203 | 201
2017-07-13 21:30 | 190 | 188
2017-07-13 22:00 | 179 | 177
2017-07-13 22:30 | 175 | 172
2017-07-13 23:00 | 196 | 194
2017-07-13 23:30 | 189 | 186
2017-07-14 | 179 | 176
2017-07-14 00:30 | 175 | 172
2017-07-14 01:00 | 169 | 166
2017-07-14 01:30 | 162 | 159
2017-07-14 02:00 | 158 | 155
2017-07-14 02:30 | 156 | 154
2017-07-14 03:00 | 153 | 151
2017-07-14 03:30 | 154 | 151
2017-07-14 04:00 | 155 | 152
2017-07-14 04:30 | 155 | 153
2017-07-14 05:00 | 157 | 154
2017-07-14 05:30 | 164 | 161
2017-07-14 06:00 | 174 | 172
2017-07-14 06:30 | 190 | 188
2017-07-14 07:00 | 198 | 196
2017-07-14 07:30 | 192 | 190
2017-07-14 08:00 | 200 | 198
2017-07-14 08:30 | 203 | 201
2017-07-14 09:00 | 198 | 197
2017-07-14 09:30 | 194 | 192
2017-07-14 10:00 | 193 | 191
2017-07-14 10:30 | 186 | 184
2017-07-14 11:00 | 182 | 180
2017-07-14 11:30 | 178 | 176
2017-07-14 12:00 | 179 | 177
2017-07-14 12:30 | 179 | 177
2017-07-14 13:00 | 181 | 179
2017-07-14 13:30 | 184 | 182
2017-07-14 14:00 | 178 | 176
2017-07-14 14:30 | 171 | 169
2017-07-14 15:00 | 165 | 163
2017-07-14 15:30 | 169 | 167
2017-07-14 16:00 | 178 | 177
2017-07-14 16:30 | 185 | 183
2017-07-14 17:00 | 188 | 186
2017-07-14 17:30 | 192 | 190
2017-07-14 18:00 | 199 | 197
2017-07-14 18:30 | 213 | 211
2017-07-14 19:00 | 217 | 215
2017-07-14 19:30 | 211 | 209
2017-07-14 20:00 | 203 | 201
2017-07-14 20:30 | 207 | 205
2017-07-14 21:00 | 203 | 201
2017-07-14 21:30 | 194 | 192
2017-07-14 22:00 | 192 | 190
2017-07-14 22:30 | 211 | 209
2017-07-14 23:00 | 202 | 200
2017-07-14 23:30 | 194 | 191
2017-07-15 | 186 | 183
2017-07-15 00:30 | 182 | 179
2017-07-15 01:00 | 173 | 170
2017-07-15 01:30 | 168 | 165
2017-07-15 02:00 | 164 | 161
2017-07-15 02:30 | 160 | 157
2017-07-15 03:00 | 161 | 158
2017-07-15 03:30 | 161 | 158
2017-07-15 04:00 | 161 | 158
2017-07-15 04:30 | 157 | 154
2017-07-15 05:00 | 141 | 138
2017-07-15 05:30 | 132 | 130
2017-07-15 06:00 | 135 | 132
2017-07-15 06:30 | 143 | 140
2017-07-15 07:00 | 151 | 149
2017-07-15 07:30 | 164 | 161
2017-07-15 08:00 | 173 | 170
2017-07-15 08:30 | 181 | 179
2017-07-15 09:00 | 183 | 181
2017-07-15 09:30 | 188 | 186
2017-07-15 10:00 | 181 | 180
2017-07-15 10:30 | 180 | 178
2017-07-15 11:00 | 180 | 179
2017-07-15 11:30 | 178 | 176
2017-07-15 12:00 | 174 | 172
2017-07-15 12:30 | 171 | 169
2017-07-15 13:00 | 173 | 171
2017-07-15 13:30 | 171 | 169
2017-07-15 14:00 | 172 | 170
2017-07-15 14:30 | 154 | 152
2017-07-15 15:00 | 153 | 151
2017-07-15 15:30 | 155 | 153
2017-07-15 16:00 | 162 | 159
2017-07-15 16:30 | 171 | 169
2017-07-15 17:00 | 180 | 178
2017-07-15 17:30 | 180 | 178
2017-07-15 18:00 | 204 | 202
2017-07-15 18:30 | 219 | 217
2017-07-15 19:00 | 216 | 214
2017-07-15 19:30 | 190 | 187
2017-07-15 20:00 | 182 | 179
2017-07-15 20:30 | 172 | 169
2017-07-15 21:00 | 164 | 160
2017-07-15 21:30 | 159 | 156
2017-07-15 22:00 | 158 | 155
2017-07-15 22:30 | 181 | 178
2017-07-15 23:00 | 178 | 175
2017-07-15 23:30 | 171 | 168
2017-07-16 | 165 | 161
2017-07-16 00:30 | 157 | 154
2017-07-16 01:00 | 148 | 145
2017-07-16 01:30 | 147 | 145
2017-07-16 02:00 | 145 | 143
2017-07-16 02:30 | 143 | 141
2017-07-16 03:00 | 140 | 138
2017-07-16 03:30 | 137 | 135
2017-07-16 04:00 | 138 | 135
2017-07-16 04:30 | 140 | 138
2017-07-16 05:00 | 143 | 141
2017-07-16 05:30 | 146 | 144
2017-07-16 06:00 | 148 | 145
2017-07-16 06:30 | 151 | 149
2017-07-16 07:00 | 151 | 148
2017-07-16 07:30 | 130 | 128
2017-07-16 08:00 | 136 | 134
2017-07-16 08:30 | 143 | 140
2017-07-16 09:00 | 146 | 144
2017-07-16 09:30 | 148 | 146
2017-07-16 10:00 | 145 | 143
2017-07-16 10:30 | 144 | 142
2017-07-16 11:00 | 140 | 138
2017-07-16 11:30 | 136 | 134
2017-07-16 12:00 | 134 | 132
2017-07-16 12:30 | 133 | 131
2017-07-16 13:00 | 131 | 129
2017-07-16 13:30 | 131 | 129
2017-07-16 14:00 | 133 | 131
2017-07-16 14:30 | 123 | 121
2017-07-16 15:00 | 124 | 122
2017-07-16 15:30 | 127 | 125
2017-07-16 16:00 | 134 | 132
2017-07-16 16:30 | 143 | 141
2017-07-16 17:00 | 153 | 151
2017-07-16 17:30 | 160 | 159
2017-07-16 18:00 | 182 | 181
2017-07-16 18:30 | 208 | 206
2017-07-16 19:00 | 209 | 207
2017-07-16 19:30 | 185 | 182
2017-07-16 20:00 | 175 | 172
2017-07-16 20:30 | 161 | 158
2017-07-16 21:00 | 155 | 151
2017-07-16 21:30 | 141 | 137
2017-07-16 22:00 | 136 | 132
2017-07-16 22:30 | 156 | 153
2017-07-16 23:00 | 153 | 149
2017-07-16 23:30 | 145 | 141
2017-07-17 | 137 | 133
2017-07-17 00:30 | 128 | 125
2017-07-17 01:00 | 125 | 122
2017-07-17 01:30 | 123 | 119
2017-07-17 02:00 | 120 | 116
2017-07-17 02:30 | 120 | 116
2017-07-17 03:00 | 117 | 113
2017-07-17 03:30 | 116 | 112
2017-07-17 04:00 | 119 | 115
2017-07-17 04:30 | 131 | 127
2017-07-17 05:00 | 133 | 129
2017-07-17 05:30 | 134 | 130
2017-07-17 06:00 | 144 | 140
2017-07-17 06:30 | 163 | 160
2017-07-17 07:00 | 159 | 155
2017-07-17 07:30 | 148 | 145
2017-07-17 08:00 | 153 | 150
2017-07-17 08:30 | 147 | 144
2017-07-17 09:00 | 142 | 139
2017-07-17 09:30 | 131 | 129
2017-07-17 10:00 | 127 | 124
2017-07-17 10:30 | 123 | 121
2017-07-17 11:00 | 120 | 118
2017-07-17 11:30 | 117 | 114
2017-07-17 12:00 | 116 | 113
2017-07-17 12:30 | 119 | 116
2017-07-17 13:00 | 120 | 117
2017-07-17 13:30 | 120 | 117
2017-07-17 14:00 | 119 | 116
2017-07-17 14:30 | 113 | 110
2017-07-17 15:00 | 113 | 109
2017-07-17 15:30 | 116 | 113
2017-07-17 16:00 | 123 | 120
2017-07-17 16:30 | 129 | 126
2017-07-17 17:00 | 136 | 132
2017-07-17 17:30 | 138 | 135
2017-07-17 18:00 | 138 | 135
2017-07-17 18:30 | 155 | 152
2017-07-17 19:00 | 164 | 161
2017-07-17 19:30 | 170 | 168
2017-07-17 20:00 | 170 | 168
2017-07-17 20:30 | 163 | 161
2017-07-17 21:00 | 154 | 151
2017-07-17 21:30 | 144 | 141
2017-07-17 22:00 | 132 | 129
2017-07-17 22:30 | 135 | 132
2017-07-17 23:00 | 147 | 144
2017-07-17 23:30 | 140 | 137
2017-07-18 | 131 | 127
2017-07-18 00:30 | 125 | 121
2017-07-18 01:00 | 118 | 114
2017-07-18 01:30 | 114 | 110
2017-07-18 02:00 | 110 | 106
2017-07-18 02:30 | 110 | 105
2017-07-18 03:00 | 114 | 110
2017-07-18 03:30 | 110 | 106
2017-07-18 04:00 | 110 | 106
2017-07-18 04:30 | 112 | 108
2017-07-18 05:00 | 115 | 111
2017-07-18 05:30 | 115 | 111
2017-07-18 06:00 | 105 | 101
2017-07-18 06:30 | 112 | 108
2017-07-18 07:00 | 128 | 125
2017-07-18 07:30 | 147 | 144
2017-07-18 08:00 | 156 | 154
2017-07-18 08:30 | 151 | 149
2017-07-18 09:00 | 141 | 140
2017-07-18 09:30 | 135 | 134
2017-07-18 10:00 | 129 | 128
2017-07-18 10:30 | 128 | 127
2017-07-18 11:00 | 124 | 123
2017-07-18 11:30 | 123 | 122
2017-07-18 12:00 | 124 | 123
2017-07-18 12:30 | 120 | 119
2017-07-18 13:00 | 121 | 120
2017-07-18 13:30 | 123 | 122
2017-07-18 14:00 | 127 | 126
2017-07-18 14:30 | 123 | 122
2017-07-18 15:00 | 122 | 121
2017-07-18 15:30 | 124 | 123
2017-07-18 16:00 | 132 | 131
2017-07-18 16:30 | 137 | 136
2017-07-18 17:00 | 142 | 140
2017-07-18 17:30 | 150 | 149
2017-07-18 18:00 | 170 | 169
2017-07-18 18:30 | 189 | 188
2017-07-18 19:00 | 195 | 194
2017-07-18 19:30 | 189 | 188
2017-07-18 20:00 | 179 | 178
2017-07-18 20:30 | 166 | 165
2017-07-18 21:00 | 158 | 157
2017-07-18 21:30 | 149 | 148
2017-07-18 22:00 | 139 | 137
2017-07-18 22:30 | 144 | 143
2017-07-18 23:00 | 156 | 155
2017-07-18 23:30 | 145 | 144
2017-07-19 | 136 | 134
2017-07-19 00:30 | 131 | 130
2017-07-19 01:00 | 129 | 127
2017-07-19 01:30 | 126 | 124
2017-07-19 02:00 | 124 | 123
2017-07-19 02:30 | 121 | 120
2017-07-19 03:00 | 118 | 117
2017-07-19 03:30 | 118 | 116
2017-07-19 04:00 | 118 | 116
2017-07-19 04:30 | 119 | 117
2017-07-19 05:00 | 122 | 121
2017-07-19 05:30 | 129 | 127
2017-07-19 06:00 | 139 | 138
2017-07-19 06:30 | 140 | 139
2017-07-19 07:00 | 132 | 131
2017-07-19 07:30 | 150 | 149
2017-07-19 08:00 | 157 | 156
2017-07-19 08:30 | 153 | 152
2017-07-19 09:00 | 141 | 139
2017-07-19 09:30 | 132 | 130
2017-07-19 10:00 | 126 | 125
2017-07-19 10:30 | 121 | 120
2017-07-19 11:00 | 119 | 118
2017-07-19 11:30 | 119 | 118
2017-07-19 12:00 | 119 | 118
2017-07-19 12:30 | 119 | 118
2017-07-19 13:00 | 119 | 118
2017-07-19 13:30 | 122 | 120
2017-07-19 14:00 | 123 | 122
2017-07-19 14:30 | 118 | 116
2017-07-19 15:00 | 114 | 113
2017-07-19 15:30 | 118 | 117
2017-07-19 16:00 | 128 | 127
2017-07-19 16:30 | 134 | 133
2017-07-19 17:00 | 142 | 141
2017-07-19 17:30 | 144 | 143
2017-07-19 18:00 | 164 | 163
2017-07-19 18:30 | 181 | 180
2017-07-19 19:00 | 191 | 190
2017-07-19 19:30 | 183 | 182
2017-07-19 20:00 | 171 | 170
2017-07-19 20:30 | 161 | 159
2017-07-19 21:00 | 152 | 150
2017-07-19 21:30 | 141 | 140
2017-07-19 22:00 | 129 | 128
2017-07-19 22:30 | 130 | 129
2017-07-19 23:00 | 144 | 142
2017-07-19 23:30 | 134 | 132
2017-07-20 | 126 | 125
2017-07-20 00:30 | 119 | 117
2017-07-20 01:00 | 115 | 113
2017-07-20 01:30 | 111 | 109
2017-07-20 02:00 | 106 | 104
2017-07-20 02:30 | 108 | 106
2017-07-20 03:00 | 102 | 100
2017-07-20 03:30 | 100 | 98
2017-07-20 04:00 | 104 | 102
2017-07-20 04:30 | 108 | 106
2017-07-20 05:00 | 111 | 109
2017-07-20 05:30 | 114 | 112
2017-07-20 06:00 | 124 | 123
2017-07-20 06:30 | 112 | 111
2017-07-20 07:00 | 117 | 116
2017-07-20 07:30 | 133 | 132
2017-07-20 08:00 | 143 | 142
2017-07-20 08:30 | 136 | 135
2017-07-20 09:00 | 128 | 127
2017-07-20 09:30 | 121 | 120
2017-07-20 10:00 | 111 | 109
2017-07-20 10:30 | 99 | 98
2017-07-20 11:00 | 75 | 73
2017-07-20 11:30 | 66 | 64
2017-07-20 12:00 | 63 | 61
2017-07-20 12:30 | 62 | 61
2017-07-20 13:00 | 62 | 60
2017-07-20 13:30 | 69 | 67
2017-07-20 14:00 | 70 | 68
2017-07-20 14:30 | 58 | 55
2017-07-20 15:00 | 29 | 24
2017-07-20 15:30 | 15 | 11
2017-07-20 16:00 | 6 | 4
2017-07-20 16:30 | 4 | 3
2017-07-20 17:00 | 5 | 1
2017-07-20 17:30 | 6 | 3
2017-07-20 18:00 | 34 | 28
2017-07-20 18:30 | 54 | 51
2017-07-20 19:00 | 64 | 62
2017-07-20 19:30 | 60 | 57
2017-07-20 20:00 | 48 | 42
2017-07-20 20:30 | 40 | 33
2017-07-20 21:00 | 34 | 26
2017-07-20 21:30 | 13 | 11
2017-07-20 22:00 | 6 | 3
2017-07-20 22:30 | 9 | 7
2017-07-20 23:00 | 62 | 61
2017-07-20 23:30 | 69 | 68
2017-07-21 | 59 | 57
2017-07-21 00:30 | 53 | 49
2017-07-21 01:00 | 49 | 44
2017-07-21 01:30 | 48 | 42
2017-07-21 02:00 | 44 | 36
2017-07-21 02:30 | 44 | 36
2017-07-21 03:00 | 42 | 35
2017-07-21 03:30 | 41 | 34
2017-07-21 04:00 | 42 | 36
2017-07-21 04:30 | 45 | 38
2017-07-21 05:00 | 48 | 42
2017-07-21 05:30 | 50 | 44
2017-07-21 06:00 | 21 | 17
2017-07-21 06:30 | 1 | 1
2017-07-21 07:00 | 2 | 2
2017-07-21 07:30 | 3 | 2
2017-07-21 08:00 | 5 | 4
2017-07-21 08:30 | 6 | 4
2017-07-21 09:00 | 5 | 4
2017-07-21 09:30 | 0 | 0
2017-07-21 10:00 | 25 | 20
2017-07-21 10:30 | 41 | 34
2017-07-21 11:00 | 4 | 2
2017-07-21 11:30 | 6 | 5
2017-07-21 12:00 | 9 | 9
2017-07-21 12:30 | 10 | 9
2017-07-21 13:00 | 12 | 12
2017-07-21 13:30 | 15 | 14
2017-07-21 14:00 | 17 | 14
2017-07-21 14:30 | 34 | 24
2017-07-21 15:00 | 33 | 23
2017-07-21 15:30 | 26 | 20
2017-07-21 16:00 | 10 | 10
2017-07-21 16:30 | 7 | 7
2017-07-21 17:00 | 0 | 0
2017-07-21 17:30 | 1 | 1
2017-07-21 18:00 | 28 | 21
2017-07-21 18:30 | 44 | 36
2017-07-21 19:00 | 49 | 42
2017-07-21 19:30 | 43 | 35
2017-07-21 20:00 | 39 | 30
2017-07-21 20:30 | 31 | 21
2017-07-21 21:00 | 14 | 12
2017-07-21 21:30 | 8 | 6
2017-07-21 22:00 | 4 | 1
2017-07-21 22:30 | 7 | 4
2017-07-21 23:00 | 31 | 23
2017-07-21 23:30 | 17 | 12
2017-07-22 | 44 | 42
2017-07-22 00:30 | 77 | 75
2017-07-22 01:00 | 112 | 110
2017-07-22 01:30 | 109 | 106
2017-07-22 02:00 | 109 | 105
2017-07-22 02:30 | 106 | 103
2017-07-22 03:00 | 103 | 100
2017-07-22 03:30 | 103 | 100
2017-07-22 04:00 | 102 | 98
2017-07-22 04:30 | 102 | 99
2017-07-22 05:00 | 105 | 102
2017-07-22 05:30 | 111 | 108
2017-07-22 06:00 | 116 | 113
2017-07-22 06:30 | 122 | 119
2017-07-22 07:00 | 120 | 117
2017-07-22 07:30 | 105 | 101
2017-07-22 08:00 | 112 | 109
2017-07-22 08:30 | 126 | 123
2017-07-22 09:00 | 130 | 128
2017-07-22 09:30 | 126 | 123
2017-07-22 10:00 | 118 | 115
2017-07-22 10:30 | 110 | 107
2017-07-22 11:00 | 105 | 102
2017-07-22 11:30 | 102 | 99
2017-07-22 12:00 | 98 | 95
2017-07-22 12:30 | 94 | 91
2017-07-22 13:00 | 94 | 91
2017-07-22 13:30 | 93 | 90
2017-07-22 14:00 | 91 | 88
2017-07-22 14:30 | 85 | 82
2017-07-22 15:00 | 82 | 78
2017-07-22 15:30 | 87 | 84
2017-07-22 16:00 | 95 | 92
2017-07-22 16:30 | 105 | 103
2017-07-22 17:00 | 116 | 113
2017-07-22 17:30 | 127 | 124
2017-07-22 18:00 | 145 | 143
2017-07-22 18:30 | 157 | 155
2017-07-22 19:00 | 161 | 159
2017-07-22 19:30 | 157 | 156
2017-07-22 20:00 | 146 | 144
2017-07-22 20:30 | 140 | 137
2017-07-22 21:00 | 134 | 132
2017-07-22 21:30 | 124 | 122
2017-07-22 22:00 | 118 | 115
2017-07-22 22:30 | 107 | 103
2017-07-22 23:00 | 101 | 98
2017-07-22 23:30 | 94 | 90
2017-07-23 | 92 | 88
2017-07-23 00:30 | 113 | 110
2017-07-23 01:00 | 113 | 108
2017-07-23 01:30 | 109 | 104
2017-07-23 02:00 | 105 | 100
2017-07-23 02:30 | 102 | 96
2017-07-23 03:00 | 101 | 96
2017-07-23 03:30 | 100 | 96
2017-07-23 04:00 | 101 | 97
2017-07-23 04:30 | 102 | 98
2017-07-23 05:00 | 101 | 98
2017-07-23 05:30 | 105 | 101
2017-07-23 06:00 | 106 | 103
2017-07-23 06:30 | 110 | 107
2017-07-23 07:00 | 106 | 103
2017-07-23 07:30 | 90 | 87
2017-07-23 08:00 | 92 | 88
2017-07-23 08:30 | 101 | 98
2017-07-23 09:00 | 106 | 103
2017-07-23 09:30 | 106 | 103
2017-07-23 10:00 | 106 | 103
2017-07-23 10:30 | 104 | 101
2017-07-23 11:00 | 101 | 98
2017-07-23 11:30 | 98 | 95
2017-07-23 12:00 | 97 | 95
2017-07-23 12:30 | 95 | 93
2017-07-23 13:00 | 94 | 91
2017-07-23 13:30 | 94 | 91
2017-07-23 14:00 | 94 | 91
2017-07-23 14:30 | 87 | 84
2017-07-23 15:00 | 83 | 80
2017-07-23 15:30 | 89 | 86
2017-07-23 16:00 | 96 | 93
2017-07-23 16:30 | 104 | 101
2017-07-23 17:00 | 112 | 110
2017-07-23 17:30 | 133 | 130
2017-07-23 18:00 | 161 | 159
2017-07-23 18:30 | 185 | 184
2017-07-23 19:00 | 191 | 189
2017-07-23 19:30 | 183 | 181
2017-07-23 20:00 | 170 | 168
2017-07-23 20:30 | 159 | 157
2017-07-23 21:00 | 146 | 144
2017-07-23 21:30 | 134 | 132
2017-07-23 22:00 | 130 | 128
2017-07-23 22:30 | 146 | 143
2017-07-23 23:00 | 138 | 136
2017-07-23 23:30 | 130 | 127
2017-07-24 | 122 | 119
2017-07-24 00:30 | 117 | 113
2017-07-24 01:00 | 112 | 109
2017-07-24 01:30 | 110 | 107
2017-07-24 02:00 | 105 | 102
2017-07-24 02:30 | 105 | 102
2017-07-24 03:00 | 105 | 102
2017-07-24 03:30 | 105 | 102
2017-07-24 04:00 | 105 | 102
2017-07-24 04:30 | 106 | 103
2017-07-24 05:00 | 110 | 106
2017-07-24 05:30 | 115 | 112
2017-07-24 06:00 | 123 | 120
2017-07-24 06:30 | 109 | 106
2017-07-24 07:00 | 112 | 110
2017-07-24 07:30 | 131 | 129
2017-07-24 08:00 | 141 | 138
2017-07-24 08:30 | 139 | 137
2017-07-24 09:00 | 131 | 129
2017-07-24 09:30 | 127 | 125
2017-07-24 10:00 | 123 | 121
2017-07-24 10:30 | 121 | 118
2017-07-24 11:00 | 119 | 116
2017-07-24 11:30 | 116 | 113
2017-07-24 12:00 | 118 | 115
2017-07-24 12:30 | 118 | 115
2017-07-24 13:00 | 118 | 116
2017-07-24 13:30 | 123 | 120
2017-07-24 14:00 | 126 | 123
2017-07-24 14:30 | 117 | 114
2017-07-24 15:00 | 114 | 111
2017-07-24 15:30 | 118 | 115
2017-07-24 16:00 | 121 | 118
2017-07-24 16:30 | 126 | 123
2017-07-24 17:00 | 135 | 132
2017-07-24 17:30 | 142 | 139
2017-07-24 18:00 | 165 | 163
2017-07-24 18:30 | 184 | 181
2017-07-24 19:00 | 196 | 194
2017-07-24 19:30 | 190 | 188
2017-07-24 20:00 | 177 | 174
2017-07-24 20:30 | 165 | 162
2017-07-24 21:00 | 155 | 152
2017-07-24 21:30 | 142 | 139
2017-07-24 22:00 | 132 | 129
2017-07-24 22:30 | 134 | 131
2017-07-24 23:00 | 134 | 131
2017-07-24 23:30 | 120 | 116
2017-07-25 | 134 | 131
2017-07-25 00:30 | 129 | 126
2017-07-25 01:00 | 120 | 117
2017-07-25 01:30 | 113 | 109
2017-07-25 02:00 | 110 | 106
2017-07-25 02:30 | 110 | 106
2017-07-25 03:00 | 107 | 103
2017-07-25 03:30 | 107 | 103
2017-07-25 04:00 | 111 | 107
2017-07-25 04:30 | 114 | 110
2017-07-25 05:00 | 121 | 117
2017-07-25 05:30 | 130 | 127
2017-07-25 06:00 | 143 | 140
2017-07-25 06:30 | 133 | 130
2017-07-25 07:00 | 138 | 136
2017-07-25 07:30 | 156 | 154
2017-07-25 08:00 | 163 | 161
2017-07-25 08:30 | 163 | 161
2017-07-25 09:00 | 156 | 153
2017-07-25 09:30 | 149 | 147
2017-07-25 10:00 | 142 | 140
2017-07-25 10:30 | 139 | 136
2017-07-25 11:00 | 137 | 135
2017-07-25 11:30 | 138 | 136
2017-07-25 12:00 | 137 | 135
2017-07-25 12:30 | 133 | 131
2017-07-25 13:00 | 133 | 131
2017-07-25 13:30 | 137 | 135
2017-07-25 14:00 | 138 | 136
2017-07-25 14:30 | 133 | 131
2017-07-25 15:00 | 128 | 126
2017-07-25 15:30 | 133 | 131
2017-07-25 16:00 | 140 | 137
2017-07-25 16:30 | 146 | 144
2017-07-25 17:00 | 152 | 149
2017-07-25 17:30 | 159 | 157
2017-07-25 18:00 | 182 | 180
2017-07-25 18:30 | 202 | 200
2017-07-25 19:00 | 211 | 209
2017-07-25 19:30 | 204 | 202
2017-07-25 20:00 | 192 | 190
2017-07-25 20:30 | 183 | 180
2017-07-25 21:00 | 169 | 166
2017-07-25 21:30 | 155 | 152
2017-07-25 22:00 | 147 | 144
2017-07-25 22:30 | 152 | 149
2017-07-25 23:00 | 163 | 160
2017-07-25 23:30 | 150 | 147
2017-07-26 | 142 | 139
2017-07-26 00:30 | 135 | 132
2017-07-26 01:00 | 133 | 130
2017-07-26 01:30 | 128 | 126
2017-07-26 02:00 | 126 | 124
2017-07-26 02:30 | 121 | 118
2017-07-26 03:00 | 122 | 119
2017-07-26 03:30 | 119 | 116
2017-07-26 04:00 | 110 | 107
2017-07-26 04:30 | 108 | 105
2017-07-26 05:00 | 112 | 109
2017-07-26 05:30 | 120 | 118
2017-07-26 06:00 | 129 | 127
2017-07-26 06:30 | 117 | 115
2017-07-26 07:00 | 120 | 118
2017-07-26 07:30 | 137 | 135
2017-07-26 08:00 | 144 | 143
2017-07-26 08:30 | 143 | 141
2017-07-26 09:00 | 138 | 137
2017-07-26 09:30 | 132 | 130
2017-07-26 10:00 | 127 | 124
2017-07-26 10:30 | 124 | 122
2017-07-26 11:00 | 121 | 119
2017-07-26 11:30 | 117 | 115
2017-07-26 12:00 | 120 | 118
2017-07-26 12:30 | 121 | 119
2017-07-26 13:00 | 120 | 118
2017-07-26 13:30 | 121 | 119
2017-07-26 14:00 | 124 | 122
2017-07-26 14:30 | 109 | 107
2017-07-26 15:00 | 108 | 106
2017-07-26 15:30 | 112 | 109
2017-07-26 16:00 | 116 | 114
2017-07-26 16:30 | 122 | 120
2017-07-26 17:00 | 129 | 127
2017-07-26 17:30 | 138 | 135
2017-07-26 18:00 | 164 | 162
2017-07-26 18:30 | 182 | 180
2017-07-26 19:00 | 195 | 193
2017-07-26 19:30 | 189 | 187
2017-07-26 20:00 | 176 | 174
2017-07-26 20:30 | 167 | 165
2017-07-26 21:00 | 158 | 156
2017-07-26 21:30 | 146 | 144
2017-07-26 22:00 | 134 | 132
2017-07-26 22:30 | 127 | 125
2017-07-26 23:00 | 128 | 125
2017-07-26 23:30 | 113 | 110
2017-07-27 | 125 | 121
2017-07-27 00:30 | 120 | 116
2017-07-27 01:00 | 118 | 114
2017-07-27 01:30 | 112 | 108
2017-07-27 02:00 | 108 | 103
2017-07-27 02:30 | 108 | 104
2017-07-27 03:00 | 108 | 104
2017-07-27 03:30 | 107 | 103
2017-07-27 04:00 | 106 | 102
2017-07-27 04:30 | 108 | 104
2017-07-27 05:00 | 111 | 107
2017-07-27 05:30 | 118 | 115
2017-07-27 06:00 | 126 | 123
2017-07-27 06:30 | 114 | 111
2017-07-27 07:00 | 122 | 118
2017-07-27 07:30 | 143 | 140
2017-07-27 08:00 | 153 | 150
2017-07-27 08:30 | 154 | 150
2017-07-27 09:00 | 146 | 142
2017-07-27 09:30 | 141 | 137
2017-07-27 10:00 | 134 | 130
2017-07-27 10:30 | 131 | 126
2017-07-27 11:00 | 130 | 125
2017-07-27 11:30 | 128 | 123
2017-07-27 12:00 | 126 | 121
2017-07-27 12:30 | 124 | 120
2017-07-27 13:00 | 122 | 119
2017-07-27 13:30 | 120 | 117
2017-07-27 14:00 | 125 | 122
2017-07-27 14:30 | 115 | 112
2017-07-27 15:00 | 109 | 106
2017-07-27 15:30 | 109 | 105
2017-07-27 16:00 | 113 | 110
2017-07-27 16:30 | 121 | 118
2017-07-27 17:00 | 130 | 127
2017-07-27 17:30 | 137 | 134
2017-07-27 18:00 | 174 | 172
2017-07-27 18:30 | 204 | 202
2017-07-27 19:00 | 201 | 199
2017-07-27 19:30 | 189 | 187
2017-07-27 20:00 | 181 | 179
2017-07-27 20:30 | 172 | 169
2017-07-27 21:00 | 163 | 160
2017-07-27 21:30 | 152 | 149
2017-07-27 22:00 | 143 | 139
2017-07-27 22:30 | 150 | 146
2017-07-27 23:00 | 166 | 163
2017-07-27 23:30 | 166 | 163
2017-07-28 | 155 | 152
2017-07-28 00:30 | 154 | 151
2017-07-28 01:00 | 147 | 144
2017-07-28 01:30 | 143 | 140
2017-07-28 02:00 | 141 | 139
2017-07-28 02:30 | 139 | 137
2017-07-28 03:00 | 138 | 135
2017-07-28 03:30 | 139 | 137
2017-07-28 04:00 | 140 | 137
2017-07-28 04:30 | 139 | 137
2017-07-28 05:00 | 141 | 138
2017-07-28 05:30 | 147 | 145
2017-07-28 06:00 | 157 | 154
2017-07-28 06:30 | 143 | 141
2017-07-28 07:00 | 153 | 151
2017-07-28 07:30 | 171 | 169
2017-07-28 08:00 | 175 | 174
2017-07-28 08:30 | 180 | 178
2017-07-28 09:00 | 184 | 182
2017-07-28 09:30 | 181 | 179
2017-07-28 10:00 | 159 | 156
2017-07-28 10:30 | 140 | 136
2017-07-28 11:00 | 156 | 153
2017-07-28 11:30 | 158 | 155
2017-07-28 12:00 | 155 | 152
2017-07-28 12:30 | 156 | 152
2017-07-28 13:00 | 147 | 144
2017-07-28 13:30 | 149 | 146
2017-07-28 14:00 | 149 | 146
2017-07-28 14:30 | 139 | 136
2017-07-28 15:00 | 139 | 135
2017-07-28 15:30 | 142 | 139
2017-07-28 16:00 | 151 | 148
2017-07-28 16:30 | 160 | 157
2017-07-28 17:00 | 168 | 165
2017-07-28 17:30 | 172 | 169
2017-07-28 18:00 | 193 | 190
2017-07-28 18:30 | 187 | 184
2017-07-28 19:00 | 187 | 184
2017-07-28 19:30 | 184 | 180
2017-07-28 20:00 | 170 | 166
2017-07-28 20:30 | 159 | 157
2017-07-28 21:00 | 154 | 151
2017-07-28 21:30 | 145 | 141
2017-07-28 22:00 | 133 | 130
2017-07-28 22:30 | 142 | 139
2017-07-28 23:00 | 158 | 155
2017-07-28 23:30 | 148 | 145
2017-07-29 | 143 | 139
2017-07-29 00:30 | 157 | 154
2017-07-29 01:00 | 151 | 148
2017-07-29 01:30 | 148 | 145
2017-07-29 02:00 | 145 | 141
2017-07-29 02:30 | 142 | 139
2017-07-29 03:00 | 139 | 136
2017-07-29 03:30 | 139 | 135
2017-07-29 04:00 | 140 | 137
2017-07-29 04:30 | 141 | 138
2017-07-29 05:00 | 140 | 137
2017-07-29 05:30 | 143 | 139
2017-07-29 06:00 | 132 | 128
2017-07-29 06:30 | 135 | 131
2017-07-29 07:00 | 140 | 137
2017-07-29 07:30 | 137 | 134
2017-07-29 08:00 | 143 | 140
2017-07-29 08:30 | 153 | 150
2017-07-29 09:00 | 155 | 153
2017-07-29 09:30 | 156 | 154
2017-07-29 10:00 | 153 | 151
2017-07-29 10:30 | 150 | 148
2017-07-29 11:00 | 142 | 140
2017-07-29 11:30 | 142 | 139
2017-07-29 12:00 | 136 | 134
2017-07-29 12:30 | 133 | 131
2017-07-29 13:00 | 132 | 130
2017-07-29 13:30 | 131 | 129
2017-07-29 14:00 | 131 | 128
2017-07-29 14:30 | 121 | 118
2017-07-29 15:00 | 118 | 115
2017-07-29 15:30 | 124 | 121
2017-07-29 16:00 | 137 | 135
2017-07-29 16:30 | 146 | 143
2017-07-29 17:00 | 151 | 149
2017-07-29 17:30 | 160 | 158
2017-07-29 18:00 | 166 | 164
2017-07-29 18:30 | 188 | 186
2017-07-29 19:00 | 195 | 194
2017-07-29 19:30 | 175 | 172
2017-07-29 20:00 | 178 | 176
2017-07-29 20:30 | 178 | 177
2017-07-29 21:00 | 174 | 172
2017-07-29 21:30 | 166 | 164
2017-07-29 22:00 | 142 | 139
2017-07-29 22:30 | 165 | 162
2017-07-29 23:00 | 156 | 153
2017-07-29 23:30 | 142 | 139
2017-07-30 | 146 | 143
2017-07-30 00:30 | 152 | 149
2017-07-30 01:00 | 148 | 145
2017-07-30 01:30 | 145 | 142
2017-07-30 02:00 | 144 | 142
2017-07-30 02:30 | 142 | 139
2017-07-30 03:00 | 144 | 141
2017-07-30 03:30 | 142 | 139
2017-07-30 04:00 | 141 | 138
2017-07-30 04:30 | 142 | 139
2017-07-30 05:00 | 141 | 138
2017-07-30 05:30 | 138 | 135
2017-07-30 06:00 | 124 | 121
2017-07-30 06:30 | 118 | 115
2017-07-30 07:00 | 118 | 115
2017-07-30 07:30 | 126 | 124
2017-07-30 08:00 | 134 | 131
2017-07-30 08:30 | 144 | 141
2017-07-30 09:00 | 149 | 147
2017-07-30 09:30 | 155 | 152
2017-07-30 10:00 | 155 | 153
2017-07-30 10:30 | 155 | 153
2017-07-30 11:00 | 156 | 154
2017-07-30 11:30 | 154 | 152
2017-07-30 12:00 | 146 | 144
2017-07-30 12:30 | 141 | 139
2017-07-30 13:00 | 139 | 138
2017-07-30 13:30 | 142 | 140
2017-07-30 14:00 | 146 | 143
2017-07-30 14:30 | 131 | 128
2017-07-30 15:00 | 133 | 131
2017-07-30 15:30 | 137 | 135
2017-07-30 16:00 | 143 | 141
2017-07-30 16:30 | 154 | 152
2017-07-30 17:00 | 164 | 162
2017-07-30 17:30 | 175 | 173
2017-07-30 18:00 | 202 | 200
2017-07-30 18:30 | 218 | 216
2017-07-30 19:00 | 230 | 228
2017-07-30 19:30 | 227 | 225
2017-07-30 20:00 | 217 | 215
2017-07-30 20:30 | 207 | 205
2017-07-30 21:00 | 196 | 194
2017-07-30 21:30 | 185 | 184
2017-07-30 22:00 | 182 | 180
2017-07-30 22:30 | 194 | 192
2017-07-30 23:00 | 182 | 180
2017-07-30 23:30 | 173 | 170
2017-07-31 | 168 | 165
2017-07-31 00:30 | 164 | 161
2017-07-31 01:00 | 158 | 155
2017-07-31 01:30 | 155 | 153
2017-07-31 02:00 | 152 | 149
2017-07-31 02:30 | 148 | 145
2017-07-31 03:00 | 148 | 145
2017-07-31 03:30 | 148 | 145
2017-07-31 04:00 | 148 | 145
2017-07-31 04:30 | 151 | 148
2017-07-31 05:00 | 155 | 152
2017-07-31 05:30 | 165 | 163
2017-07-31 06:00 | 164 | 161
2017-07-31 06:30 | 162 | 159
2017-07-31 07:00 | 170 | 168
2017-07-31 07:30 | 190 | 188
2017-07-31 08:00 | 202 | 201
2017-07-31 08:30 | 203 | 201
2017-07-31 09:00 | 198 | 197
2017-07-31 09:30 | 198 | 196
2017-07-31 10:00 | 191 | 189
2017-07-31 10:30 | 183 | 181
2017-07-31 11:00 | 180 | 179
2017-07-31 11:30 | 178 | 177
2017-07-31 12:00 | 157 | 155
2017-07-31 12:30 | 155 | 154
2017-07-31 13:00 | 157 | 155
2017-07-31 13:30 | 154 | 153
2017-07-31 14:00 | 152 | 150
2017-07-31 14:30 | 144 | 141
2017-07-31 15:00 | 121 | 119
2017-07-31 15:30 | 97 | 95
2017-07-31 16:00 | 91 | 89
2017-07-31 16:30 | 91 | 90
2017-07-31 17:00 | 111 | 109
2017-07-31 17:30 | 110 | 108
2017-07-31 18:00 | 83 | 81
2017-07-31 18:30 | 90 | 88
2017-07-31 19:00 | 95 | 94
2017-07-31 19:30 | 90 | 88
2017-07-31 20:00 | 98 | 97
2017-07-31 20:30 | 93 | 91
2017-07-31 21:00 | 85 | 84
2017-07-31 21:30 | 75 | 74
2017-07-31 22:00 | 66 | 64
2017-07-31 22:30 | 53 | 47
2017-07-31 23:00 | 41 | 33
2017-07-31 23:30 | 64 | 62
2017-08-01 | 102 | 101
2017-08-01 00:30 | 109 | 108
2017-08-01 01:00 | 102 | 100
2017-08-01 01:30 | 98 | 97
2017-08-01 02:00 | 95 | 93
2017-08-01 02:30 | 94 | 93
2017-08-01 03:00 | 90 | 89
2017-08-01 03:30 | 90 | 89
2017-08-01 04:00 | 89 | 88
2017-08-01 04:30 | 90 | 89
2017-08-01 05:00 | 93 | 92
2017-08-01 05:30 | 97 | 96
2017-08-01 06:00 | 106 | 105
2017-08-01 06:30 | 49 | 45
2017-08-01 07:00 | 40 | 33
2017-08-01 07:30 | 57 | 54
2017-08-01 08:00 | 72 | 70
2017-08-01 08:30 | 85 | 84
2017-08-01 09:00 | 71 | 70
2017-08-01 09:30 | 88 | 87
2017-08-01 10:00 | 124 | 123
2017-08-01 10:30 | 119 | 118
2017-08-01 11:00 | 111 | 110
2017-08-01 11:30 | 104 | 103
2017-08-01 12:00 | 92 | 90
2017-08-01 12:30 | 65 | 64
2017-08-01 13:00 | 63 | 62
2017-08-01 13:30 | 71 | 69
2017-08-01 14:00 | 70 | 69
2017-08-01 14:30 | 85 | 84
2017-08-01 15:00 | 87 | 86
2017-08-01 15:30 | 92 | 90
2017-08-01 16:00 | 98 | 97
2017-08-01 16:30 | 67 | 65
2017-08-01 17:00 | 68 | 66
2017-08-01 17:30 | 70 | 69
2017-08-01 18:00 | 82 | 81
2017-08-01 18:30 | 93 | 91
2017-08-01 19:00 | 97 | 96
2017-08-01 19:30 | 117 | 116
2017-08-01 20:00 | 113 | 112
2017-08-01 20:30 | 105 | 103
2017-08-01 21:00 | 92 | 91
2017-08-01 21:30 | 81 | 79
2017-08-01 22:00 | 68 | 66
2017-08-01 22:30 | 65 | 63
2017-08-01 23:00 | 72 | 70
2017-08-01 23:30 | 63 | 62
2017-08-02 | 92 | 91
2017-08-02 00:30 | 125 | 124
2017-08-02 01:00 | 159 | 158
2017-08-02 01:30 | 158 | 156
2017-08-02 02:00 | 151 | 150
2017-08-02 02:30 | 148 | 147
2017-08-02 03:00 | 148 | 146
2017-08-02 03:30 | 148 | 147
2017-08-02 04:00 | 152 | 150
2017-08-02 04:30 | 151 | 150
2017-08-02 05:00 | 157 | 156
2017-08-02 05:30 | 158 | 156
2017-08-02 06:00 | 166 | 165
2017-08-02 06:30 | 153 | 151
2017-08-02 07:00 | 141 | 140
2017-08-02 07:30 | 182 | 180
2017-08-02 08:00 | 202 | 200
2017-08-02 08:30 | 202 | 200
2017-08-02 09:00 | 186 | 184
2017-08-02 09:30 | 182 | 180
2017-08-02 10:00 | 174 | 173
2017-08-02 10:30 | 167 | 165
2017-08-02 11:00 | 164 | 162
2017-08-02 11:30 | 161 | 160
2017-08-02 12:00 | 163 | 161
2017-08-02 12:30 | 162 | 160
2017-08-02 13:00 | 161 | 159
2017-08-02 13:30 | 165 | 164
2017-08-02 14:00 | 168 | 166
2017-08-02 14:30 | 160 | 158
2017-08-02 15:00 | 155 | 153
2017-08-02 15:30 | 161 | 159
2017-08-02 16:00 | 170 | 168
2017-08-02 16:30 | 177 | 175
2017-08-02 17:00 | 187 | 185
2017-08-02 17:30 | 170 | 168
2017-08-02 18:00 | 146 | 144
2017-08-02 18:30 | 154 | 152
2017-08-02 19:00 | 159 | 157
2017-08-02 19:30 | 152 | 150
2017-08-02 20:00 | 142 | 140
2017-08-02 20:30 | 133 | 132
2017-08-02 21:00 | 124 | 122
2017-08-02 21:30 | 115 | 114
2017-08-02 22:00 | 99 | 97
2017-08-02 22:30 | 103 | 101
2017-08-02 23:00 | 113 | 112
2017-08-02 23:30 | 106 | 105
2017-08-03 | 129 | 128
2017-08-03 00:30 | 170 | 168
2017-08-03 01:00 | 164 | 162
2017-08-03 01:30 | 160 | 158
2017-08-03 02:00 | 159 | 157
2017-08-03 02:30 | 158 | 157
2017-08-03 03:00 | 155 | 154
2017-08-03 03:30 | 158 | 157
2017-08-03 04:00 | 155 | 154
2017-08-03 04:30 | 158 | 156
2017-08-03 05:00 | 159 | 157
2017-08-03 05:30 | 167 | 166
2017-08-03 06:00 | 180 | 178
2017-08-03 06:30 | 169 | 168
2017-08-03 07:00 | 166 | 164
2017-08-03 07:30 | 175 | 174
2017-08-03 08:00 | 164 | 163
2017-08-03 08:30 | 163 | 162
2017-08-03 09:00 | 155 | 153
2017-08-03 09:30 | 146 | 145
2017-08-03 10:00 | 141 | 139
2017-08-03 10:30 | 138 | 137
2017-08-03 11:00 | 136 | 135
2017-08-03 11:30 | 137 | 136
2017-08-03 12:00 | 134 | 133
2017-08-03 12:30 | 154 | 153
2017-08-03 13:00 | 169 | 167
2017-08-03 13:30 | 177 | 175
2017-08-03 14:00 | 187 | 185
2017-08-03 14:30 | 182 | 180
2017-08-03 15:00 | 180 | 179
2017-08-03 15:30 | 183 | 182
2017-08-03 16:00 | 190 | 188
2017-08-03 16:30 | 198 | 196
2017-08-03 17:00 | 202 | 200
2017-08-03 17:30 | 166 | 164
2017-08-03 18:00 | 136 | 135
2017-08-03 18:30 | 161 | 160
2017-08-03 19:00 | 175 | 174
2017-08-03 19:30 | 172 | 170
2017-08-03 20:00 | 163 | 162
2017-08-03 20:30 | 151 | 149
2017-08-03 21:00 | 139 | 138
2017-08-03 21:30 | 131 | 129
2017-08-03 22:00 | 116 | 115
2017-08-03 22:30 | 120 | 119
2017-08-03 23:00 | 163 | 162
2017-08-03 23:30 | 196 | 195
2017-08-04 | 195 | 194
2017-08-04 00:30 | 195 | 193
2017-08-04 01:00 | 187 | 185
2017-08-04 01:30 | 179 | 177
2017-08-04 02:00 | 175 | 174
2017-08-04 02:30 | 175 | 173
2017-08-04 03:00 | 173 | 172
2017-08-04 03:30 | 171 | 170
2017-08-04 04:00 | 171 | 170
2017-08-04 04:30 | 169 | 168
2017-08-04 05:00 | 170 | 169
2017-08-04 05:30 | 178 | 177
2017-08-04 06:00 | 185 | 184
2017-08-04 06:30 | 172 | 171
2017-08-04 07:00 | 178 | 177
2017-08-04 07:30 | 197 | 196
2017-08-04 08:00 | 197 | 196
2017-08-04 08:30 | 132 | 131
2017-08-04 09:00 | 125 | 124
2017-08-04 09:30 | 120 | 119
2017-08-04 10:00 | 111 | 110
2017-08-04 10:30 | 112 | 111
2017-08-04 11:00 | 108 | 106
2017-08-04 11:30 | 103 | 101
2017-08-04 12:00 | 104 | 102
2017-08-04 12:30 | 108 | 107
2017-08-04 13:00 | 111 | 110
2017-08-04 13:30 | 114 | 113
2017-08-04 14:00 | 110 | 109
2017-08-04 14:30 | 100 | 99
2017-08-04 15:00 | 100 | 98
2017-08-04 15:30 | 102 | 100
2017-08-04 16:00 | 103 | 102
2017-08-04 16:30 | 105 | 104
2017-08-04 17:00 | 110 | 109
2017-08-04 17:30 | 116 | 114
2017-08-04 18:00 | 135 | 133
2017-08-04 18:30 | 148 | 146
2017-08-04 19:00 | 154 | 152
2017-08-04 19:30 | 146 | 144
2017-08-04 20:00 | 167 | 165
2017-08-04 20:30 | 201 | 199
2017-08-04 21:00 | 197 | 196
2017-08-04 21:30 | 189 | 188
2017-08-04 22:00 | 182 | 179
2017-08-04 22:30 | 188 | 186
2017-08-04 23:00 | 202 | 200
2017-08-04 23:30 | 194 | 191
2017-08-05 | 186 | 183
2017-08-05 00:30 | 176 | 174
2017-08-05 01:00 | 175 | 173
2017-08-05 01:30 | 177 | 175
2017-08-05 02:00 | 178 | 175
2017-08-05 02:30 | 170 | 167
2017-08-05 03:00 | 161 | 159
2017-08-05 03:30 | 159 | 156
2017-08-05 04:00 | 158 | 155
2017-08-05 04:30 | 156 | 154
2017-08-05 05:00 | 161 | 158
2017-08-05 05:30 | 161 | 158
2017-08-05 06:00 | 166 | 164
2017-08-05 06:30 | 145 | 143
2017-08-05 07:00 | 138 | 136
2017-08-05 07:30 | 152 | 149
2017-08-05 08:00 | 170 | 168
2017-08-05 08:30 | 181 | 178
2017-08-05 09:00 | 187 | 185
2017-08-05 09:30 | 187 | 185
2017-08-05 10:00 | 176 | 173
2017-08-05 10:30 | 174 | 171
2017-08-05 11:00 | 171 | 169
2017-08-05 11:30 | 123 | 121
2017-08-05 12:00 | 93 | 91
2017-08-05 12:30 | 89 | 87
2017-08-05 13:00 | 86 | 84
2017-08-05 13:30 | 87 | 84
2017-08-05 14:00 | 87 | 85
2017-08-05 14:30 | 80 | 77
2017-08-05 15:00 | 109 | 106
2017-08-05 15:30 | 84 | 81
2017-08-05 16:00 | 84 | 81
2017-08-05 16:30 | 89 | 86
2017-08-05 17:00 | 98 | 95
2017-08-05 17:30 | 107 | 105
2017-08-05 18:00 | 119 | 116
2017-08-05 18:30 | 128 | 125
2017-08-05 19:00 | 133 | 130
2017-08-05 19:30 | 184 | 182
2017-08-05 20:00 | 190 | 188
2017-08-05 20:30 | 181 | 178
2017-08-05 21:00 | 176 | 174
2017-08-05 21:30 | 168 | 166
2017-08-05 22:00 | 160 | 158
2017-08-05 22:30 | 181 | 178
2017-08-05 23:00 | 199 | 197
2017-08-05 23:30 | 194 | 191
2017-08-06 | 186 | 184
2017-08-06 00:30 | 180 | 178
2017-08-06 01:00 | 175 | 173
2017-08-06 01:30 | 171 | 168
2017-08-06 02:00 | 169 | 167
2017-08-06 02:30 | 163 | 161
2017-08-06 03:00 | 159 | 158
2017-08-06 03:30 | 160 | 158
2017-08-06 04:00 | 160 | 158
2017-08-06 04:30 | 160 | 158
2017-08-06 05:00 | 160 | 158
2017-08-06 05:30 | 163 | 161
2017-08-06 06:00 | 152 | 150
2017-08-06 06:30 | 137 | 135
2017-08-06 07:00 | 134 | 132
2017-08-06 07:30 | 143 | 141
2017-08-06 08:00 | 151 | 149
2017-08-06 08:30 | 166 | 164
2017-08-06 09:00 | 171 | 169
2017-08-06 09:30 | 169 | 168
2017-08-06 10:00 | 169 | 167
2017-08-06 10:30 | 171 | 170
2017-08-06 11:00 | 170 | 169
2017-08-06 11:30 | 169 | 168
2017-08-06 12:00 | 173 | 171
2017-08-06 12:30 | 169 | 167
2017-08-06 13:00 | 165 | 164
2017-08-06 13:30 | 161 | 160
2017-08-06 14:00 | 168 | 167
2017-08-06 14:30 | 157 | 156
2017-08-06 15:00 | 155 | 153
2017-08-06 15:30 | 160 | 159
2017-08-06 16:00 | 167 | 165
2017-08-06 16:30 | 168 | 167
2017-08-06 17:00 | 172 | 170
2017-08-06 17:30 | 183 | 182
2017-08-06 18:00 | 207 | 206
2017-08-06 18:30 | 226 | 225
2017-08-06 19:00 | 236 | 235
2017-08-06 19:30 | 229 | 228
2017-08-06 20:00 | 218 | 217
2017-08-06 20:30 | 209 | 208
2017-08-06 21:00 | 200 | 199
2017-08-06 21:30 | 189 | 187
2017-08-06 22:00 | 179 | 177
2017-08-06 22:30 | 185 | 184
2017-08-06 23:00 | 195 | 194
2017-08-06 23:30 | 188 | 187
2017-08-07 | 184 | 182
2017-08-07 00:30 | 179 | 177
2017-08-07 01:00 | 173 | 171
2017-08-07 01:30 | 169 | 167
2017-08-07 02:00 | 161 | 160
2017-08-07 02:30 | 149 | 147
2017-08-07 03:00 | 142 | 140
2017-08-07 03:30 | 141 | 139
2017-08-07 04:00 | 143 | 141
2017-08-07 04:30 | 161 | 159
2017-08-07 05:00 | 170 | 168
2017-08-07 05:30 | 177 | 175
2017-08-07 06:00 | 185 | 183
2017-08-07 06:30 | 176 | 174
2017-08-07 07:00 | 180 | 178
2017-08-07 07:30 | 204 | 202
2017-08-07 08:00 | 216 | 215
2017-08-07 08:30 | 211 | 210
2017-08-07 09:00 | 198 | 196
2017-08-07 09:30 | 190 | 188
2017-08-07 10:00 | 181 | 179
2017-08-07 10:30 | 179 | 177
2017-08-07 11:00 | 180 | 179
2017-08-07 11:30 | 191 | 189
2017-08-07 12:00 | 194 | 193
2017-08-07 12:30 | 196 | 194
2017-08-07 13:00 | 204 | 203
2017-08-07 13:30 | 208 | 207
2017-08-07 14:00 | 211 | 210
2017-08-07 14:30 | 194 | 192
2017-08-07 15:00 | 193 | 191
2017-08-07 15:30 | 198 | 196
2017-08-07 16:00 | 203 | 201
2017-08-07 16:30 | 206 | 204
2017-08-07 17:00 | 210 | 209
2017-08-07 17:30 | 208 | 206
2017-08-07 18:00 | 201 | 200
2017-08-07 18:30 | 205 | 203
2017-08-07 19:00 | 228 | 226
2017-08-07 19:30 | 223 | 220
2017-08-07 20:00 | 224 | 222
2017-08-07 20:30 | 234 | 232
2017-08-07 21:00 | 220 | 218
2017-08-07 21:30 | 208 | 206
2017-08-07 22:00 | 195 | 193
2017-08-07 22:30 | 203 | 201
2017-08-07 23:00 | 211 | 209
2017-08-07 23:30 | 200 | 198
2017-08-08 | 194 | 192
2017-08-08 00:30 | 186 | 184
2017-08-08 01:00 | 180 | 178
2017-08-08 01:30 | 175 | 173
2017-08-08 02:00 | 171 | 169
2017-08-08 02:30 | 167 | 165
2017-08-08 03:00 | 158 | 155
2017-08-08 03:30 | 157 | 155
2017-08-08 04:00 | 157 | 155
2017-08-08 04:30 | 154 | 152
2017-08-08 05:00 | 149 | 147
2017-08-08 05:30 | 154 | 152
2017-08-08 06:00 | 165 | 163
2017-08-08 06:30 | 189 | 187
2017-08-08 07:00 | 187 | 185
2017-08-08 07:30 | 223 | 222
2017-08-08 08:00 | 234 | 233
2017-08-08 08:30 | 248 | 248
2017-08-08 09:00 | 231 | 231
2017-08-08 09:30 | 225 | 224
2017-08-08 10:00 | 224 | 223
2017-08-08 10:30 | 228 | 227
2017-08-08 11:00 | 225 | 224
2017-08-08 11:30 | 223 | 222
2017-08-08 12:00 | 227 | 226
2017-08-08 12:30 | 225 | 224
2017-08-08 13:00 | 224 | 223
2017-08-08 13:30 | 226 | 224
2017-08-08 14:00 | 226 | 225
2017-08-08 14:30 | 219 | 217
2017-08-08 15:00 | 220 | 219
2017-08-08 15:30 | 201 | 200
2017-08-08 16:00 | 204 | 202
2017-08-08 16:30 | 227 | 226
2017-08-08 17:00 | 233 | 232
2017-08-08 17:30 | 234 | 233
2017-08-08 18:00 | 247 | 246
2017-08-08 18:30 | 257 | 256
2017-08-08 19:00 | 261 | 260
2017-08-08 19:30 | 250 | 249
2017-08-08 20:00 | 242 | 240
2017-08-08 20:30 | 229 | 228
2017-08-08 21:00 | 219 | 218
2017-08-08 21:30 | 225 | 224
2017-08-08 22:00 | 219 | 218
2017-08-08 22:30 | 212 | 210
2017-08-08 23:00 | 202 | 201
2017-08-08 23:30 | 191 | 189
2017-08-09 | 182 | 181
2017-08-09 00:30 | 177 | 176
2017-08-09 01:00 | 170 | 169
2017-08-09 01:30 | 166 | 165
2017-08-09 02:00 | 162 | 161
2017-08-09 02:30 | 160 | 159
2017-08-09 03:00 | 161 | 160
2017-08-09 03:30 | 161 | 160
2017-08-09 04:00 | 159 | 159
2017-08-09 04:30 | 161 | 160
2017-08-09 05:00 | 166 | 165
2017-08-09 05:30 | 174 | 173
2017-08-09 06:00 | 183 | 182
2017-08-09 06:30 | 201 | 200
2017-08-09 07:00 | 198 | 197
2017-08-09 07:30 | 230 | 230
2017-08-09 08:00 | 248 | 247
2017-08-09 08:30 | 251 | 250
2017-08-09 09:00 | 247 | 246
2017-08-09 09:30 | 244 | 243
2017-08-09 10:00 | 242 | 241
2017-08-09 10:30 | 237 | 236
2017-08-09 11:00 | 232 | 231
2017-08-09 11:30 | 233 | 231
2017-08-09 12:00 | 233 | 232
2017-08-09 12:30 | 223 | 222
2017-08-09 13:00 | 214 | 213
2017-08-09 13:30 | 212 | 211
2017-08-09 14:00 | 213 | 212
2017-08-09 14:30 | 209 | 208
2017-08-09 15:00 | 212 | 211
2017-08-09 15:30 | 217 | 216
2017-08-09 16:00 | 222 | 221
2017-08-09 16:30 | 231 | 230
2017-08-09 17:00 | 233 | 232
2017-08-09 17:30 | 241 | 240
2017-08-09 18:00 | 250 | 249
2017-08-09 18:30 | 264 | 262
2017-08-09 19:00 | 257 | 255
2017-08-09 19:30 | 254 | 252
2017-08-09 20:00 | 257 | 255
2017-08-09 20:30 | 250 | 248
2017-08-09 21:00 | 239 | 237
2017-08-09 21:30 | 228 | 226
2017-08-09 22:00 | 212 | 210
2017-08-09 22:30 | 205 | 203
2017-08-09 23:00 | 195 | 193
2017-08-09 23:30 | 184 | 182
2017-08-10 | 178 | 176
2017-08-10 00:30 | 173 | 171
2017-08-10 01:00 | 166 | 165
2017-08-10 01:30 | 159 | 158
2017-08-10 02:00 | 159 | 157
2017-08-10 02:30 | 156 | 154
2017-08-10 03:00 | 155 | 153
2017-08-10 03:30 | 159 | 157
2017-08-10 04:00 | 163 | 161
2017-08-10 04:30 | 165 | 164
2017-08-10 05:00 | 169 | 168
2017-08-10 05:30 | 180 | 179
2017-08-10 06:00 | 193 | 192
2017-08-10 06:30 | 213 | 211
2017-08-10 07:00 | 206 | 205
2017-08-10 07:30 | 243 | 241
2017-08-10 08:00 | 241 | 238
2017-08-10 08:30 | 240 | 237
2017-08-10 09:00 | 230 | 227
2017-08-10 09:30 | 230 | 227
2017-08-10 10:00 | 219 | 216
2017-08-10 10:30 | 213 | 211
2017-08-10 11:00 | 218 | 216
2017-08-10 11:30 | 217 | 214
2017-08-10 12:00 | 218 | 216
2017-08-10 12:30 | 221 | 219
2017-08-10 13:00 | 227 | 224
2017-08-10 13:30 | 230 | 227
2017-08-10 14:00 | 230 | 228
2017-08-10 14:30 | 224 | 222
2017-08-10 15:00 | 222 | 219
2017-08-10 15:30 | 226 | 223
2017-08-10 16:00 | 230 | 227
2017-08-10 16:30 | 235 | 232
2017-08-10 17:00 | 245 | 242
2017-08-10 17:30 | 245 | 242
2017-08-10 18:00 | 250 | 247
2017-08-10 18:30 | 262 | 259
2017-08-10 19:00 | 272 | 269
2017-08-10 19:30 | 267 | 264
2017-08-10 20:00 | 256 | 254
2017-08-10 20:30 | 246 | 243
2017-08-10 21:00 | 236 | 232
2017-08-10 21:30 | 221 | 218
2017-08-10 22:00 | 207 | 204
2017-08-10 22:30 | 208 | 204
2017-08-10 23:00 | 203 | 199
2017-08-10 23:30 | 194 | 190
2017-08-11 | 182 | 179
2017-08-11 00:30 | 173 | 170
2017-08-11 01:00 | 164 | 161
2017-08-11 01:30 | 161 | 158
2017-08-11 02:00 | 159 | 156
2017-08-11 02:30 | 159 | 156
2017-08-11 03:00 | 158 | 155
2017-08-11 03:30 | 158 | 155
2017-08-11 04:00 | 158 | 155
2017-08-11 04:30 | 158 | 155
2017-08-11 05:00 | 159 | 156
2017-08-11 05:30 | 162 | 159
2017-08-11 06:00 | 150 | 147
2017-08-11 06:30 | 166 | 163
2017-08-11 07:00 | 180 | 178
2017-08-11 07:30 | 192 | 189
2017-08-11 08:00 | 211 | 209
2017-08-11 08:30 | 222 | 219
2017-08-11 09:00 | 214 | 211
2017-08-11 09:30 | 220 | 217
2017-08-11 10:00 | 220 | 217
2017-08-11 10:30 | 214 | 211
2017-08-11 11:00 | 216 | 212
2017-08-11 11:30 | 206 | 203
2017-08-11 12:00 | 205 | 201
2017-08-11 12:30 | 202 | 198
2017-08-11 13:00 | 202 | 199
2017-08-11 13:30 | 202 | 198
2017-08-11 14:00 | 205 | 201
2017-08-11 14:30 | 197 | 193
2017-08-11 15:00 | 194 | 191
2017-08-11 15:30 | 199 | 195
2017-08-11 16:00 | 207 | 203
2017-08-11 16:30 | 218 | 214
2017-08-11 17:00 | 223 | 220
2017-08-11 17:30 | 229 | 226
2017-08-11 18:00 | 236 | 233
2017-08-11 18:30 | 245 | 242
2017-08-11 19:00 | 267 | 264
2017-08-11 19:30 | 263 | 261
2017-08-11 20:00 | 257 | 254
2017-08-11 20:30 | 247 | 244
2017-08-11 21:00 | 240 | 237
2017-08-11 21:30 | 229 | 226
2017-08-11 22:00 | 219 | 215
2017-08-11 22:30 | 211 | 207
2017-08-11 23:00 | 199 | 195
2017-08-11 23:30 | 188 | 185
2017-08-12 | 179 | 176
2017-08-12 00:30 | 174 | 172
2017-08-12 01:00 | 167 | 165
2017-08-12 01:30 | 163 | 161
2017-08-12 02:00 | 161 | 158
2017-08-12 02:30 | 160 | 157
2017-08-12 03:00 | 157 | 155
2017-08-12 03:30 | 155 | 152
2017-08-12 04:00 | 155 | 152
2017-08-12 04:30 | 155 | 152
2017-08-12 05:00 | 158 | 155
2017-08-12 05:30 | 161 | 158
2017-08-12 06:00 | 166 | 163
2017-08-12 06:30 | 170 | 168
2017-08-12 07:00 | 176 | 173
2017-08-12 07:30 | 187 | 185
2017-08-12 08:00 | 197 | 195
2017-08-12 08:30 | 203 | 201
2017-08-12 09:00 | 204 | 202
2017-08-12 09:30 | 150 | 147
2017-08-12 10:00 | 139 | 136
2017-08-12 10:30 | 179 | 177
2017-08-12 11:00 | 195 | 193
2017-08-12 11:30 | 189 | 187
2017-08-12 12:00 | 189 | 186
2017-08-12 12:30 | 189 | 186
2017-08-12 13:00 | 188 | 186
2017-08-12 13:30 | 186 | 183
2017-08-12 14:00 | 186 | 183
2017-08-12 14:30 | 175 | 172
2017-08-12 15:00 | 171 | 169
2017-08-12 15:30 | 176 | 174
2017-08-12 16:00 | 185 | 182
2017-08-12 16:30 | 195 | 192
2017-08-12 17:00 | 204 | 202
2017-08-12 17:30 | 217 | 214
2017-08-12 18:00 | 225 | 222
2017-08-12 18:30 | 239 | 236
2017-08-12 19:00 | 249 | 246
2017-08-12 19:30 | 245 | 242
2017-08-12 20:00 | 240 | 238
2017-08-12 20:30 | 232 | 229
2017-08-12 21:00 | 227 | 223
2017-08-12 21:30 | 216 | 213
2017-08-12 22:00 | 211 | 208
2017-08-12 22:30 | 209 | 205
2017-08-12 23:00 | 204 | 201
2017-08-12 23:30 | 192 | 188
2017-08-13 | 186 | 182
2017-08-13 00:30 | 180 | 177
2017-08-13 01:00 | 174 | 170
2017-08-13 01:30 | 170 | 167
2017-08-13 02:00 | 167 | 163
2017-08-13 02:30 | 169 | 166
2017-08-13 03:00 | 162 | 159
2017-08-13 03:30 | 161 | 158
2017-08-13 04:00 | 161 | 158
2017-08-13 04:30 | 161 | 159
2017-08-13 05:00 | 162 | 159
2017-08-13 05:30 | 164 | 161
2017-08-13 06:00 | 165 | 162
2017-08-13 06:30 | 167 | 164
2017-08-13 07:00 | 170 | 168
2017-08-13 07:30 | 174 | 172
2017-08-13 08:00 | 191 | 188
2017-08-13 08:30 | 204 | 202
2017-08-13 09:00 | 210 | 207
2017-08-13 09:30 | 210 | 207
2017-08-13 10:00 | 207 | 204
2017-08-13 10:30 | 199 | 197
2017-08-13 11:00 | 192 | 189
2017-08-13 11:30 | 189 | 187
2017-08-13 12:00 | 184 | 182
2017-08-13 12:30 | 180 | 178
2017-08-13 13:00 | 178 | 176
2017-08-13 13:30 | 180 | 178
2017-08-13 14:00 | 179 | 178
2017-08-13 14:30 | 169 | 168
2017-08-13 15:00 | 170 | 168
2017-08-13 15:30 | 176 | 174
2017-08-13 16:00 | 186 | 184
2017-08-13 16:30 | 195 | 194
2017-08-13 17:00 | 210 | 208
2017-08-13 17:30 | 220 | 218
2017-08-13 18:00 | 234 | 232
2017-08-13 18:30 | 247 | 245
2017-08-13 19:00 | 257 | 254
2017-08-13 19:30 | 251 | 248
2017-08-13 20:00 | 240 | 237
2017-08-13 20:30 | 241 | 239
2017-08-13 21:00 | 235 | 233
2017-08-13 21:30 | 225 | 223
2017-08-13 22:00 | 214 | 211
2017-08-13 22:30 | 202 | 199
2017-08-13 23:00 | 189 | 187
2017-08-13 23:30 | 179 | 177
2017-08-14 | 172 | 170
2017-08-14 00:30 | 167 | 165
2017-08-14 01:00 | 165 | 163
2017-08-14 01:30 | 164 | 162
2017-08-14 02:00 | 161 | 159
2017-08-14 02:30 | 159 | 157
2017-08-14 03:00 | 156 | 154
2017-08-14 03:30 | 155 | 153
2017-08-14 04:00 | 151 | 149
2017-08-14 04:30 | 152 | 150
2017-08-14 05:00 | 156 | 154
2017-08-14 05:30 | 167 | 165
2017-08-14 06:00 | 176 | 174
2017-08-14 06:30 | 190 | 188
2017-08-14 07:00 | 191 | 189
2017-08-14 07:30 | 206 | 204
2017-08-14 08:00 | 221 | 218
2017-08-14 08:30 | 217 | 214
2017-08-14 09:00 | 212 | 209
2017-08-14 09:30 | 205 | 202
2017-08-14 10:00 | 201 | 197
2017-08-14 10:30 | 202 | 199
2017-08-14 11:00 | 198 | 196
2017-08-14 11:30 | 196 | 194
2017-08-14 12:00 | 196 | 194
2017-08-14 12:30 | 197 | 195
2017-08-14 13:00 | 195 | 193
2017-08-14 13:30 | 194 | 191
2017-08-14 14:00 | 199 | 197
2017-08-14 14:30 | 207 | 204
2017-08-14 15:00 | 210 | 207
2017-08-14 15:30 | 213 | 211
2017-08-14 16:00 | 220 | 218
2017-08-14 16:30 | 224 | 222
2017-08-14 17:00 | 233 | 230
2017-08-14 17:30 | 243 | 241
2017-08-14 18:00 | 246 | 244
2017-08-14 18:30 | 267 | 265
2017-08-14 19:00 | 306 | 305
2017-08-14 19:30 | 301 | 299
2017-08-14 20:00 | 290 | 289
2017-08-14 20:30 | 278 | 277
2017-08-14 21:00 | 270 | 268
2017-08-14 21:30 | 257 | 255
2017-08-14 22:00 | 239 | 237
2017-08-14 22:30 | 224 | 222
2017-08-14 23:00 | 211 | 209
2017-08-14 23:30 | 202 | 200
2017-08-15 | 189 | 187
2017-08-15 00:30 | 181 | 180
2017-08-15 01:00 | 175 | 173
2017-08-15 01:30 | 169 | 168
2017-08-15 02:00 | 169 | 168
2017-08-15 02:30 | 168 | 166
2017-08-15 03:00 | 165 | 163
2017-08-15 03:30 | 165 | 163
2017-08-15 04:00 | 166 | 165
2017-08-15 04:30 | 168 | 166
2017-08-15 05:00 | 170 | 168
2017-08-15 05:30 | 177 | 176
2017-08-15 06:00 | 186 | 185
2017-08-15 06:30 | 205 | 204
2017-08-15 07:00 | 208 | 206
2017-08-15 07:30 | 241 | 240
2017-08-15 08:00 | 249 | 247
2017-08-15 08:30 | 234 | 232
2017-08-15 09:00 | 223 | 221
2017-08-15 09:30 | 221 | 219
2017-08-15 10:00 | 223 | 222
2017-08-15 10:30 | 220 | 219
2017-08-15 11:00 | 220 | 219
2017-08-15 11:30 | 212 | 210
2017-08-15 12:00 | 210 | 209
2017-08-15 12:30 | 207 | 206
2017-08-15 13:00 | 208 | 206
2017-08-15 13:30 | 211 | 209
2017-08-15 14:00 | 213 | 212
2017-08-15 14:30 | 211 | 209
2017-08-15 15:00 | 213 | 212
2017-08-15 15:30 | 217 | 215
2017-08-15 16:00 | 227 | 225
2017-08-15 16:30 | 235 | 233
2017-08-15 17:00 | 243 | 241
2017-08-15 17:30 | 247 | 246
2017-08-15 18:00 | 263 | 262
2017-08-15 18:30 | 282 | 280
2017-08-15 19:00 | 292 | 291
2017-08-15 19:30 | 286 | 284
2017-08-15 20:00 | 282 | 280
2017-08-15 20:30 | 275 | 273
2017-08-15 21:00 | 261 | 259
2017-08-15 21:30 | 246 | 244
2017-08-15 22:00 | 232 | 231
2017-08-15 22:30 | 215 | 213
2017-08-15 23:00 | 201 | 199
2017-08-15 23:30 | 193 | 192
2017-08-16 | 187 | 185
2017-08-16 00:30 | 185 | 183
2017-08-16 01:00 | 179 | 177
2017-08-16 01:30 | 175 | 173
2017-08-16 02:00 | 171 | 169
2017-08-16 02:30 | 169 | 167
2017-08-16 03:00 | 168 | 166
2017-08-16 03:30 | 170 | 167
2017-08-16 04:00 | 168 | 166
2017-08-16 04:30 | 171 | 169
2017-08-16 05:00 | 175 | 173
2017-08-16 05:30 | 180 | 178
2017-08-16 06:00 | 187 | 186
2017-08-16 06:30 | 208 | 206
2017-08-16 07:00 | 227 | 225
2017-08-16 07:30 | 245 | 244
2017-08-16 08:00 | 263 | 261
2017-08-16 08:30 | 262 | 261
2017-08-16 09:00 | 253 | 251
2017-08-16 09:30 | 246 | 244
2017-08-16 10:00 | 244 | 242
2017-08-16 10:30 | 242 | 240
2017-08-16 11:00 | 237 | 235
2017-08-16 11:30 | 236 | 234
2017-08-16 12:00 | 238 | 236
2017-08-16 12:30 | 233 | 231
2017-08-16 13:00 | 221 | 219
2017-08-16 13:30 | 218 | 216
2017-08-16 14:00 | 219 | 217
2017-08-16 14:30 | 215 | 213
2017-08-16 15:00 | 215 | 213
2017-08-16 15:30 | 219 | 217
2017-08-16 16:00 | 227 | 225
2017-08-16 16:30 | 234 | 232
2017-08-16 17:00 | 243 | 241
2017-08-16 17:30 | 249 | 247
2017-08-16 18:00 | 259 | 257
2017-08-16 18:30 | 262 | 259
2017-08-16 19:00 | 266 | 263
2017-08-16 19:30 | 277 | 275
2017-08-16 20:00 | 269 | 267
2017-08-16 20:30 | 258 | 256
2017-08-16 21:00 | 254 | 252
2017-08-16 21:30 | 243 | 241
2017-08-16 22:00 | 231 | 230
2017-08-16 22:30 | 229 | 228
2017-08-16 23:00 | 220 | 218
2017-08-16 23:30 | 205 | 203
2017-08-17 | 190 | 188
2017-08-17 00:30 | 179 | 177
2017-08-17 01:00 | 169 | 168
2017-08-17 01:30 | 171 | 170
2017-08-17 02:00 | 167 | 166
2017-08-17 02:30 | 163 | 162
2017-08-17 03:00 | 160 | 159
2017-08-17 03:30 | 164 | 162
2017-08-17 04:00 | 163 | 162
2017-08-17 04:30 | 164 | 163
2017-08-17 05:00 | 171 | 170
2017-08-17 05:30 | 176 | 175
2017-08-17 06:00 | 185 | 184
2017-08-17 06:30 | 208 | 206
2017-08-17 07:00 | 228 | 226
2017-08-17 07:30 | 245 | 242
2017-08-17 08:00 | 251 | 247
2017-08-17 08:30 | 246 | 243
2017-08-17 09:00 | 238 | 235
2017-08-17 09:30 | 236 | 233
2017-08-17 10:00 | 234 | 230
2017-08-17 10:30 | 234 | 230
2017-08-17 11:00 | 230 | 227
2017-08-17 11:30 | 233 | 229
2017-08-17 12:00 | 232 | 228
2017-08-17 12:30 | 229 | 226
2017-08-17 13:00 | 227 | 223
2017-08-17 13:30 | 229 | 226
2017-08-17 14:00 | 232 | 229
2017-08-17 14:30 | 224 | 220
2017-08-17 15:00 | 226 | 222
2017-08-17 15:30 | 227 | 224
2017-08-17 16:00 | 235 | 232
2017-08-17 16:30 | 241 | 238
2017-08-17 17:00 | 231 | 227
2017-08-17 17:30 | 233 | 228
2017-08-17 18:00 | 238 | 234
2017-08-17 18:30 | 258 | 254
2017-08-17 19:00 | 294 | 291
2017-08-17 19:30 | 292 | 289
2017-08-17 20:00 | 277 | 274
2017-08-17 20:30 | 266 | 263
2017-08-17 21:00 | 256 | 253
2017-08-17 21:30 | 238 | 234
2017-08-17 22:00 | 225 | 221
2017-08-17 22:30 | 222 | 218
2017-08-17 23:00 | 214 | 210
2017-08-17 23:30 | 203 | 200
2017-08-18 | 195 | 192
2017-08-18 00:30 | 187 | 186
2017-08-18 01:00 | 178 | 177
2017-08-18 01:30 | 173 | 172
2017-08-18 02:00 | 169 | 168
2017-08-18 02:30 | 167 | 166
2017-08-18 03:00 | 166 | 165
2017-08-18 03:30 | 167 | 166
2017-08-18 04:00 | 167 | 166
2017-08-18 04:30 | 167 | 165
2017-08-18 05:00 | 168 | 167
2017-08-18 05:30 | 178 | 177
2017-08-18 06:00 | 188 | 187
2017-08-18 06:30 | 206 | 205
2017-08-18 07:00 | 225 | 224
2017-08-18 07:30 | 240 | 239
2017-08-18 08:00 | 243 | 242
2017-08-18 08:30 | 240 | 239
2017-08-18 09:00 | 231 | 229
2017-08-18 09:30 | 223 | 221
2017-08-18 10:00 | 220 | 219
2017-08-18 10:30 | 219 | 217
2017-08-18 11:00 | 218 | 217
2017-08-18 11:30 | 215 | 213
2017-08-18 12:00 | 214 | 213
2017-08-18 12:30 | 213 | 212
2017-08-18 13:00 | 198 | 196
2017-08-18 13:30 | 187 | 185
2017-08-18 14:00 | 198 | 196
2017-08-18 14:30 | 191 | 188
2017-08-18 15:00 | 188 | 186
2017-08-18 15:30 | 189 | 187
2017-08-18 16:00 | 196 | 194
2017-08-18 16:30 | 204 | 202
2017-08-18 17:00 | 214 | 212
2017-08-18 17:30 | 228 | 226
2017-08-18 18:00 | 244 | 243
2017-08-18 18:30 | 242 | 240
2017-08-18 19:00 | 240 | 238
2017-08-18 19:30 | 232 | 230
2017-08-18 20:00 | 223 | 222
2017-08-18 20:30 | 218 | 216
2017-08-18 21:00 | 218 | 216
2017-08-18 21:30 | 206 | 203
2017-08-18 22:00 | 192 | 189
2017-08-18 22:30 | 211 | 208
2017-08-18 23:00 | 207 | 205
2017-08-18 23:30 | 197 | 195
2017-08-19 | 190 | 188
2017-08-19 00:30 | 185 | 184
2017-08-19 01:00 | 181 | 179
2017-08-19 01:30 | 172 | 171
2017-08-19 02:00 | 169 | 168
2017-08-19 02:30 | 167 | 166
2017-08-19 03:00 | 167 | 165
2017-08-19 03:30 | 166 | 165
2017-08-19 04:00 | 165 | 163
2017-08-19 04:30 | 164 | 163
2017-08-19 05:00 | 163 | 162
2017-08-19 05:30 | 164 | 163
2017-08-19 06:00 | 167 | 166
2017-08-19 06:30 | 152 | 151
2017-08-19 07:00 | 145 | 144
2017-08-19 07:30 | 162 | 161
2017-08-19 08:00 | 171 | 169
2017-08-19 08:30 | 174 | 173
2017-08-19 09:00 | 174 | 172
2017-08-19 09:30 | 174 | 172
2017-08-19 10:00 | 170 | 169
2017-08-19 10:30 | 166 | 164
2017-08-19 11:00 | 166 | 164
2017-08-19 11:30 | 164 | 163
2017-08-19 12:00 | 162 | 161
2017-08-19 12:30 | 162 | 161
2017-08-19 13:00 | 162 | 161
2017-08-19 13:30 | 162 | 161
2017-08-19 14:00 | 160 | 159
2017-08-19 14:30 | 154 | 152
2017-08-19 15:00 | 153 | 151
2017-08-19 15:30 | 158 | 156
2017-08-19 16:00 | 166 | 164
2017-08-19 16:30 | 174 | 173
2017-08-19 17:00 | 184 | 183
2017-08-19 17:30 | 191 | 190
2017-08-19 18:00 | 198 | 197
2017-08-19 18:30 | 209 | 208
2017-08-19 19:00 | 220 | 219
2017-08-19 19:30 | 215 | 214
2017-08-19 20:00 | 206 | 205
2017-08-19 20:30 | 198 | 196
2017-08-19 21:00 | 191 | 189
2017-08-19 21:30 | 183 | 181
2017-08-19 22:00 | 176 | 175
2017-08-19 22:30 | 185 | 184
2017-08-19 23:00 | 185 | 184
2017-08-19 23:30 | 174 | 172
2017-08-20 | 165 | 164
2017-08-20 00:30 | 170 | 169
2017-08-20 01:00 | 170 | 169
2017-08-20 01:30 | 169 | 168
2017-08-20 02:00 | 167 | 166
2017-08-20 02:30 | 165 | 163
2017-08-20 03:00 | 165 | 164
2017-08-20 03:30 | 164 | 163
2017-08-20 04:00 | 160 | 159
2017-08-20 04:30 | 159 | 158
2017-08-20 05:00 | 159 | 158
2017-08-20 05:30 | 160 | 158
2017-08-20 06:00 | 162 | 160
2017-08-20 06:30 | 144 | 142
2017-08-20 07:00 | 133 | 131
2017-08-20 07:30 | 140 | 138
2017-08-20 08:00 | 146 | 145
2017-08-20 08:30 | 151 | 150
2017-08-20 09:00 | 151 | 150
2017-08-20 09:30 | 150 | 149
2017-08-20 10:00 | 150 | 149
2017-08-20 10:30 | 151 | 150
2017-08-20 11:00 | 149 | 148
2017-08-20 11:30 | 146 | 145
2017-08-20 12:00 | 140 | 139
2017-08-20 12:30 | 140 | 139
2017-08-20 13:00 | 139 | 138
2017-08-20 13:30 | 132 | 131
2017-08-20 14:00 | 131 | 130
2017-08-20 14:30 | 127 | 126
2017-08-20 15:00 | 130 | 128
2017-08-20 15:30 | 133 | 132
2017-08-20 16:00 | 143 | 141
2017-08-20 16:30 | 154 | 153
2017-08-20 17:00 | 164 | 162
2017-08-20 17:30 | 176 | 175
2017-08-20 18:00 | 208 | 207
2017-08-20 18:30 | 227 | 225
2017-08-20 19:00 | 234 | 233
2017-08-20 19:30 | 230 | 229
2017-08-20 20:00 | 216 | 214
2017-08-20 20:30 | 194 | 192
2017-08-20 21:00 | 186 | 184
2017-08-20 21:30 | 179 | 177
2017-08-20 22:00 | 169 | 167
2017-08-20 22:30 | 187 | 186
2017-08-20 23:00 | 189 | 187
2017-08-20 23:30 | 184 | 182
2017-08-21 | 174 | 172
2017-08-21 00:30 | 170 | 168
2017-08-21 01:00 | 167 | 165
2017-08-21 01:30 | 162 | 159
2017-08-21 02:00 | 160 | 158
2017-08-21 02:30 | 156 | 154
2017-08-21 03:00 | 155 | 153
2017-08-21 03:30 | 154 | 153
2017-08-21 04:00 | 157 | 155
2017-08-21 04:30 | 157 | 156
2017-08-21 05:00 | 157 | 156
2017-08-21 05:30 | 165 | 164
2017-08-21 06:00 | 175 | 173
2017-08-21 06:30 | 168 | 166
2017-08-21 07:00 | 165 | 164
2017-08-21 07:30 | 182 | 181
2017-08-21 08:00 | 185 | 184
2017-08-21 08:30 | 186 | 184
2017-08-21 09:00 | 175 | 174
2017-08-21 09:30 | 177 | 176
2017-08-21 10:00 | 180 | 179
2017-08-21 10:30 | 177 | 176
2017-08-21 11:00 | 172 | 171
2017-08-21 11:30 | 167 | 165
2017-08-21 12:00 | 161 | 160
2017-08-21 12:30 | 162 | 161
2017-08-21 13:00 | 165 | 163
2017-08-21 13:30 | 164 | 162
2017-08-21 14:00 | 158 | 157
2017-08-21 14:30 | 162 | 160
2017-08-21 15:00 | 164 | 163
2017-08-21 15:30 | 164 | 163
2017-08-21 16:00 | 169 | 168
2017-08-21 16:30 | 181 | 180
2017-08-21 17:00 | 197 | 196
2017-08-21 17:30 | 210 | 208
2017-08-21 18:00 | 213 | 212
2017-08-21 18:30 | 227 | 226
2017-08-21 19:00 | 229 | 228
2017-08-21 19:30 | 230 | 229
2017-08-21 20:00 | 224 | 222
2017-08-21 20:30 | 214 | 213
2017-08-21 21:00 | 215 | 213
2017-08-21 21:30 | 210 | 208
2017-08-21 22:00 | 196 | 195
2017-08-21 22:30 | 195 | 194
2017-08-21 23:00 | 193 | 192
2017-08-21 23:30 | 186 | 185
2017-08-22 | 182 | 180
2017-08-22 00:30 | 177 | 176
2017-08-22 01:00 | 170 | 169
2017-08-22 01:30 | 165 | 164
2017-08-22 02:00 | 161 | 160
2017-08-22 02:30 | 161 | 159
2017-08-22 03:00 | 158 | 157
2017-08-22 03:30 | 158 | 157
2017-08-22 04:00 | 160 | 158
2017-08-22 04:30 | 158 | 156
2017-08-22 05:00 | 160 | 158
2017-08-22 05:30 | 170 | 169
2017-08-22 06:00 | 177 | 176
2017-08-22 06:30 | 176 | 175
2017-08-22 07:00 | 181 | 180
2017-08-22 07:30 | 204 | 203
2017-08-22 08:00 | 206 | 205
2017-08-22 08:30 | 202 | 200
2017-08-22 09:00 | 193 | 191
2017-08-22 09:30 | 182 | 181
2017-08-22 10:00 | 177 | 176
2017-08-22 10:30 | 175 | 173
2017-08-22 11:00 | 171 | 169
2017-08-22 11:30 | 171 | 169
2017-08-22 12:00 | 174 | 172
2017-08-22 12:30 | 173 | 172
2017-08-22 13:00 | 174 | 172
2017-08-22 13:30 | 176 | 175
2017-08-22 14:00 | 182 | 181
2017-08-22 14:30 | 175 | 174
2017-08-22 15:00 | 173 | 171
2017-08-22 15:30 | 176 | 175
2017-08-22 16:00 | 184 | 183
2017-08-22 16:30 | 193 | 192
2017-08-22 17:00 | 198 | 197
2017-08-22 17:30 | 208 | 207
2017-08-22 18:00 | 218 | 216
2017-08-22 18:30 | 226 | 225
2017-08-22 19:00 | 239 | 238
2017-08-22 19:30 | 236 | 235
2017-08-22 20:00 | 224 | 223
2017-08-22 20:30 | 229 | 228
2017-08-22 21:00 | 238 | 237
2017-08-22 21:30 | 228 | 227
2017-08-22 22:00 | 217 | 215
2017-08-22 22:30 | 220 | 219
2017-08-22 23:00 | 215 | 213
2017-08-22 23:30 | 201 | 199
2017-08-23 | 191 | 190
2017-08-23 00:30 | 185 | 184
2017-08-23 01:00 | 180 | 179
2017-08-23 01:30 | 175 | 174
2017-08-23 02:00 | 170 | 169
2017-08-23 02:30 | 168 | 166
2017-08-23 03:00 | 163 | 161
2017-08-23 03:30 | 162 | 161
2017-08-23 04:00 | 163 | 162
2017-08-23 04:30 | 164 | 163
2017-08-23 05:00 | 165 | 164
2017-08-23 05:30 | 170 | 169
2017-08-23 06:00 | 178 | 176
2017-08-23 06:30 | 165 | 163
2017-08-23 07:00 | 171 | 170
2017-08-23 07:30 | 187 | 186
2017-08-23 08:00 | 194 | 193
2017-08-23 08:30 | 187 | 186
2017-08-23 09:00 | 183 | 182
2017-08-23 09:30 | 177 | 175
2017-08-23 10:00 | 184 | 182
2017-08-23 10:30 | 187 | 185
2017-08-23 11:00 | 183 | 182
2017-08-23 11:30 | 181 | 180
2017-08-23 12:00 | 178 | 177
2017-08-23 12:30 | 177 | 176
2017-08-23 13:00 | 177 | 176
2017-08-23 13:30 | 179 | 178
2017-08-23 14:00 | 181 | 179
2017-08-23 14:30 | 176 | 174
2017-08-23 15:00 | 173 | 171
2017-08-23 15:30 | 174 | 173
2017-08-23 16:00 | 182 | 181
2017-08-23 16:30 | 192 | 191
2017-08-23 17:00 | 198 | 197
2017-08-23 17:30 | 205 | 203
2017-08-23 18:00 | 209 | 208
2017-08-23 18:30 | 225 | 223
2017-08-23 19:00 | 235 | 234
2017-08-23 19:30 | 230 | 229
2017-08-23 20:00 | 222 | 220
2017-08-23 20:30 | 225 | 223
2017-08-23 21:00 | 218 | 217
2017-08-23 21:30 | 208 | 207
2017-08-23 22:00 | 197 | 196
2017-08-23 22:30 | 184 | 182
2017-08-23 23:00 | 171 | 169
2017-08-23 23:30 | 172 | 170
2017-08-24 | 174 | 172
2017-08-24 00:30 | 181 | 179
2017-08-24 01:00 | 178 | 177
2017-08-24 01:30 | 172 | 170
2017-08-24 02:00 | 168 | 166
2017-08-24 02:30 | 165 | 164
2017-08-24 03:00 | 165 | 164
2017-08-24 03:30 | 165 | 164
2017-08-24 04:00 | 163 | 162
2017-08-24 04:30 | 167 | 165
2017-08-24 05:00 | 170 | 169
2017-08-24 05:30 | 183 | 181
2017-08-24 06:00 | 188 | 187
2017-08-24 06:30 | 176 | 175
2017-08-24 07:00 | 175 | 174
2017-08-24 07:30 | 196 | 195
2017-08-24 08:00 | 203 | 203
2017-08-24 08:30 | 198 | 197
2017-08-24 09:00 | 189 | 188
2017-08-24 09:30 | 185 | 184
2017-08-24 10:00 | 181 | 180
2017-08-24 10:30 | 177 | 176
2017-08-24 11:00 | 177 | 176
2017-08-24 11:30 | 176 | 175
2017-08-24 12:00 | 175 | 174
2017-08-24 12:30 | 174 | 173
2017-08-24 13:00 | 173 | 172
2017-08-24 13:30 | 173 | 172
2017-08-24 14:00 | 176 | 175
2017-08-24 14:30 | 183 | 181
2017-08-24 15:00 | 185 | 184
2017-08-24 15:30 | 187 | 186
2017-08-24 16:00 | 198 | 197
2017-08-24 16:30 | 204 | 203
2017-08-24 17:00 | 211 | 210
2017-08-24 17:30 | 216 | 215
2017-08-24 18:00 | 232 | 230
2017-08-24 18:30 | 248 | 247
2017-08-24 19:00 | 261 | 259
2017-08-24 19:30 | 268 | 266
2017-08-24 20:00 | 255 | 253
2017-08-24 20:30 | 252 | 251
2017-08-24 21:00 | 246 | 244
2017-08-24 21:30 | 235 | 233
2017-08-24 22:00 | 221 | 219
2017-08-24 22:30 | 211 | 209
2017-08-24 23:00 | 196 | 195
2017-08-24 23:30 | 186 | 185
2017-08-25 | 180 | 178
2017-08-25 00:30 | 191 | 190
2017-08-25 01:00 | 195 | 193
2017-08-25 01:30 | 192 | 190
2017-08-25 02:00 | 188 | 187
2017-08-25 02:30 | 185 | 183
2017-08-25 03:00 | 185 | 183
2017-08-25 03:30 | 184 | 182
2017-08-25 04:00 | 184 | 182
2017-08-25 04:30 | 184 | 182
2017-08-25 05:00 | 185 | 183
2017-08-25 05:30 | 170 | 169
2017-08-25 06:00 | 166 | 165
2017-08-25 06:30 | 182 | 180
2017-08-25 07:00 | 177 | 175
2017-08-25 07:30 | 210 | 209
2017-08-25 08:00 | 215 | 214
2017-08-25 08:30 | 214 | 214
2017-08-25 09:00 | 203 | 202
2017-08-25 09:30 | 196 | 195
2017-08-25 10:00 | 184 | 183
2017-08-25 10:30 | 177 | 176
2017-08-25 11:00 | 174 | 173
2017-08-25 11:30 | 174 | 173
2017-08-25 12:00 | 173 | 172
2017-08-25 12:30 | 173 | 172
2017-08-25 13:00 | 175 | 174
2017-08-25 13:30 | 176 | 175
2017-08-25 14:00 | 175 | 175
2017-08-25 14:30 | 167 | 166
2017-08-25 15:00 | 166 | 165
2017-08-25 15:30 | 171 | 170
2017-08-25 16:00 | 179 | 178
2017-08-25 16:30 | 186 | 185
2017-08-25 17:00 | 198 | 197
2017-08-25 17:30 | 203 | 201
2017-08-25 18:00 | 208 | 207
2017-08-25 18:30 | 215 | 214
2017-08-25 19:00 | 225 | 224
2017-08-25 19:30 | 237 | 236
2017-08-25 20:00 | 233 | 232
2017-08-25 20:30 | 224 | 222
2017-08-25 21:00 | 215 | 214
2017-08-25 21:30 | 206 | 204
2017-08-25 22:00 | 199 | 197
2017-08-25 22:30 | 185 | 183
2017-08-25 23:00 | 173 | 171
2017-08-25 23:30 | 165 | 163
2017-08-26 | 157 | 156
2017-08-26 00:30 | 168 | 167
2017-08-26 01:00 | 175 | 174
2017-08-26 01:30 | 173 | 172
2017-08-26 02:00 | 169 | 168
2017-08-26 02:30 | 168 | 167
2017-08-26 03:00 | 167 | 165
2017-08-26 03:30 | 166 | 165
2017-08-26 04:00 | 163 | 162
2017-08-26 04:30 | 166 | 165
2017-08-26 05:00 | 168 | 167
2017-08-26 05:30 | 170 | 168
2017-08-26 06:00 | 174 | 172
2017-08-26 06:30 | 161 | 160
2017-08-26 07:00 | 156 | 155
2017-08-26 07:30 | 164 | 162
2017-08-26 08:00 | 171 | 170
2017-08-26 08:30 | 177 | 175
2017-08-26 09:00 | 176 | 174
2017-08-26 09:30 | 174 | 172
2017-08-26 10:00 | 173 | 172
2017-08-26 10:30 | 170 | 169
2017-08-26 11:00 | 168 | 166
2017-08-26 11:30 | 171 | 170
2017-08-26 12:00 | 167 | 166
2017-08-26 12:30 | 165 | 163
2017-08-26 13:00 | 163 | 162
2017-08-26 13:30 | 161 | 160
2017-08-26 14:00 | 159 | 157
2017-08-26 14:30 | 148 | 146
2017-08-26 15:00 | 146 | 145
2017-08-26 15:30 | 149 | 147
2017-08-26 16:00 | 157 | 155
2017-08-26 16:30 | 165 | 164
2017-08-26 17:00 | 175 | 174
2017-08-26 17:30 | 182 | 180
2017-08-26 18:00 | 206 | 205
2017-08-26 18:30 | 217 | 216
2017-08-26 19:00 | 209 | 208
2017-08-26 19:30 | 204 | 202
2017-08-26 20:00 | 195 | 194
2017-08-26 20:30 | 188 | 187
2017-08-26 21:00 | 179 | 178
2017-08-26 21:30 | 170 | 169
2017-08-26 22:00 | 165 | 163
2017-08-26 22:30 | 185 | 183
2017-08-26 23:00 | 194 | 192
2017-08-26 23:30 | 188 | 186
2017-08-27 | 178 | 177
2017-08-27 00:30 | 172 | 170
2017-08-27 01:00 | 169 | 167
2017-08-27 01:30 | 164 | 162
2017-08-27 02:00 | 159 | 158
2017-08-27 02:30 | 158 | 156
2017-08-27 03:00 | 157 | 155
2017-08-27 03:30 | 154 | 153
2017-08-27 04:00 | 156 | 154
2017-08-27 04:30 | 156 | 155
2017-08-27 05:00 | 156 | 155
2017-08-27 05:30 | 159 | 158
2017-08-27 06:00 | 162 | 161
2017-08-27 06:30 | 150 | 148
2017-08-27 07:00 | 138 | 137
2017-08-27 07:30 | 147 | 145
2017-08-27 08:00 | 154 | 153
2017-08-27 08:30 | 159 | 157
2017-08-27 09:00 | 163 | 162
2017-08-27 09:30 | 164 | 162
2017-08-27 10:00 | 167 | 166
2017-08-27 10:30 | 167 | 166
2017-08-27 11:00 | 162 | 161
2017-08-27 11:30 | 158 | 157
2017-08-27 12:00 | 157 | 156
2017-08-27 12:30 | 156 | 155
2017-08-27 13:00 | 155 | 154
2017-08-27 13:30 | 150 | 149
2017-08-27 14:00 | 147 | 145
2017-08-27 14:30 | 135 | 133
2017-08-27 15:00 | 130 | 128
2017-08-27 15:30 | 136 | 134
2017-08-27 16:00 | 143 | 141
2017-08-27 16:30 | 152 | 151
2017-08-27 17:00 | 166 | 164
2017-08-27 17:30 | 184 | 183
2017-08-27 18:00 | 198 | 197
2017-08-27 18:30 | 220 | 219
2017-08-27 19:00 | 235 | 234
2017-08-27 19:30 | 227 | 226
2017-08-27 20:00 | 211 | 209
2017-08-27 20:30 | 172 | 170
2017-08-27 21:00 | 184 | 183
2017-08-27 21:30 | 187 | 185
2017-08-27 22:00 | 178 | 176
2017-08-27 22:30 | 185 | 184
2017-08-27 23:00 | 193 | 192
2017-08-27 23:30 | 186 | 185
2017-08-28 | 178 | 176
2017-08-28 00:30 | 176 | 174
2017-08-28 01:00 | 169 | 168
2017-08-28 01:30 | 164 | 163
2017-08-28 02:00 | 160 | 158
2017-08-28 02:30 | 160 | 158
2017-08-28 03:00 | 159 | 157
2017-08-28 03:30 | 156 | 155
2017-08-28 04:00 | 156 | 154
2017-08-28 04:30 | 156 | 155
2017-08-28 05:00 | 159 | 157
2017-08-28 05:30 | 166 | 164
2017-08-28 06:00 | 177 | 175
2017-08-28 06:30 | 169 | 167
2017-08-28 07:00 | 152 | 150
2017-08-28 07:30 | 176 | 174
2017-08-28 08:00 | 179 | 177
2017-08-28 08:30 | 178 | 177
2017-08-28 09:00 | 171 | 170
2017-08-28 09:30 | 176 | 176
2017-08-28 10:00 | 179 | 178
2017-08-28 10:30 | 179 | 178
2017-08-28 11:00 | 182 | 180
2017-08-28 11:30 | 182 | 179
2017-08-28 12:00 | 180 | 178
2017-08-28 12:30 | 184 | 181
2017-08-28 13:00 | 187 | 185
2017-08-28 13:30 | 190 | 187
2017-08-28 14:00 | 191 | 188
2017-08-28 14:30 | 182 | 179
2017-08-28 15:00 | 183 | 180
2017-08-28 15:30 | 181 | 179
2017-08-28 16:00 | 189 | 186
2017-08-28 16:30 | 192 | 190
2017-08-28 17:00 | 203 | 200
2017-08-28 17:30 | 216 | 213
2017-08-28 18:00 | 226 | 224
2017-08-28 18:30 | 218 | 215
2017-08-28 19:00 | 223 | 220
2017-08-28 19:30 | 209 | 205
2017-08-28 20:00 | 194 | 190
2017-08-28 20:30 | 194 | 190
2017-08-28 21:00 | 200 | 196
2017-08-28 21:30 | 203 | 200
2017-08-28 22:00 | 196 | 193
2017-08-28 22:30 | 198 | 195
2017-08-28 23:00 | 200 | 197
2017-08-28 23:30 | 190 | 187
2017-08-29 | 182 | 179
2017-08-29 00:30 | 176 | 172
2017-08-29 01:00 | 170 | 166
2017-08-29 01:30 | 167 | 164
2017-08-29 02:00 | 163 | 161
2017-08-29 02:30 | 160 | 158
2017-08-29 03:00 | 158 | 156
2017-08-29 03:30 | 158 | 156
2017-08-29 04:00 | 159 | 156
2017-08-29 04:30 | 162 | 160
2017-08-29 05:00 | 172 | 170
2017-08-29 05:30 | 179 | 177
2017-08-29 06:00 | 179 | 178
2017-08-29 06:30 | 175 | 173
2017-08-29 07:00 | 154 | 151
2017-08-29 07:30 | 167 | 165
2017-08-29 08:00 | 191 | 189
2017-08-29 08:30 | 194 | 192
2017-08-29 09:00 | 187 | 185
2017-08-29 09:30 | 194 | 192
2017-08-29 10:00 | 195 | 193
2017-08-29 10:30 | 197 | 195
2017-08-29 11:00 | 199 | 197
2017-08-29 11:30 | 197 | 196
2017-08-29 12:00 | 197 | 195
2017-08-29 12:30 | 198 | 196
2017-08-29 13:00 | 198 | 196
2017-08-29 13:30 | 201 | 199
2017-08-29 14:00 | 203 | 201
2017-08-29 14:30 | 191 | 189
2017-08-29 15:00 | 189 | 186
2017-08-29 15:30 | 194 | 191
2017-08-29 16:00 | 198 | 195
2017-08-29 16:30 | 203 | 201
2017-08-29 17:00 | 206 | 204
2017-08-29 17:30 | 211 | 209
2017-08-29 18:00 | 220 | 217
2017-08-29 18:30 | 215 | 212
2017-08-29 19:00 | 226 | 223
2017-08-29 19:30 | 227 | 224
2017-08-29 20:00 | 226 | 223
2017-08-29 20:30 | 217 | 215
2017-08-29 21:00 | 207 | 205
2017-08-29 21:30 | 213 | 211
2017-08-29 22:00 | 204 | 202
2017-08-29 22:30 | 189 | 186
2017-08-29 23:00 | 170 | 167
2017-08-29 23:30 | 159 | 156
2017-08-30 | 159 | 155
2017-08-30 00:30 | 158 | 155
2017-08-30 01:00 | 164 | 161
2017-08-30 01:30 | 162 | 159
2017-08-30 02:00 | 158 | 154
2017-08-30 02:30 | 152 | 148
2017-08-30 03:00 | 151 | 147
2017-08-30 03:30 | 151 | 148
2017-08-30 04:00 | 151 | 147
2017-08-30 04:30 | 154 | 150
2017-08-30 05:00 | 149 | 145
2017-08-30 05:30 | 153 | 149
2017-08-30 06:00 | 153 | 150
2017-08-30 06:30 | 164 | 161
2017-08-30 07:00 | 148 | 144
2017-08-30 07:30 | 166 | 164
2017-08-30 08:00 | 184 | 182
2017-08-30 08:30 | 183 | 181
2017-08-30 09:00 | 174 | 172
2017-08-30 09:30 | 179 | 177
2017-08-30 10:00 | 181 | 178
2017-08-30 10:30 | 179 | 176
2017-08-30 11:00 | 175 | 172
2017-08-30 11:30 | 172 | 169
2017-08-30 12:00 | 174 | 171
2017-08-30 12:30 | 169 | 166
2017-08-30 13:00 | 165 | 161
2017-08-30 13:30 | 174 | 171
2017-08-30 14:00 | 176 | 173
2017-08-30 14:30 | 148 | 144
2017-08-30 15:00 | 159 | 156
2017-08-30 15:30 | 166 | 163
2017-08-30 16:00 | 171 | 167
2017-08-30 16:30 | 178 | 174
2017-08-30 17:00 | 184 | 181
2017-08-30 17:30 | 195 | 192
2017-08-30 18:00 | 216 | 214
2017-08-30 18:30 | 214 | 212
2017-08-30 19:00 | 223 | 221
2017-08-30 19:30 | 219 | 216
2017-08-30 20:00 | 209 | 207
2017-08-30 20:30 | 210 | 208
2017-08-30 21:00 | 206 | 204
2017-08-30 21:30 | 197 | 194
2017-08-30 22:00 | 185 | 182
2017-08-30 22:30 | 192 | 189
2017-08-30 23:00 | 190 | 187
2017-08-30 23:30 | 180 | 177
2017-08-31 | 172 | 169
2017-08-31 00:30 | 167 | 164
2017-08-31 01:00 | 160 | 157
2017-08-31 01:30 | 157 | 154
2017-08-31 02:00 | 151 | 148
2017-08-31 02:30 | 151 | 147
2017-08-31 03:00 | 150 | 146
2017-08-31 03:30 | 150 | 147
2017-08-31 04:00 | 149 | 146
2017-08-31 04:30 | 151 | 148
2017-08-31 05:00 | 153 | 150
2017-08-31 05:30 | 157 | 154
2017-08-31 06:00 | 170 | 167
2017-08-31 06:30 | 186 | 184
2017-08-31 07:00 | 168 | 165
2017-08-31 07:30 | 176 | 173
2017-08-31 08:00 | 184 | 182
2017-08-31 08:30 | 181 | 179
2017-08-31 09:00 | 174 | 172
2017-08-31 09:30 | 196 | 194
2017-08-31 10:00 | 195 | 192
2017-08-31 10:30 | 173 | 170
2017-08-31 11:00 | 165 | 163
2017-08-31 11:30 | 161 | 160
2017-08-31 12:00 | 162 | 160
2017-08-31 12:30 | 171 | 166
2017-08-31 13:00 | 167 | 163
2017-08-31 13:30 | 165 | 162
2017-08-31 14:00 | 170 | 166
2017-08-31 14:30 | 163 | 160
2017-08-31 15:00 | 158 | 154
2017-08-31 15:30 | 161 | 158
2017-08-31 16:00 | 166 | 164
2017-08-31 16:30 | 173 | 171
2017-08-31 17:00 | 180 | 178
2017-08-31 17:30 | 187 | 185
2017-08-31 18:00 | 197 | 195
2017-08-31 18:30 | 211 | 207
2017-08-31 19:00 | 225 | 223
2017-08-31 19:30 | 243 | 241
2017-08-31 20:00 | 244 | 243
2017-08-31 20:30 | 238 | 236
2017-08-31 21:00 | 226 | 224
2017-08-31 21:30 | 222 | 219
2017-08-31 22:00 | 215 | 212
2017-08-31 22:30 | 221 | 218
2017-08-31 23:00 | 218 | 215
2017-08-31 23:30 | 212 | 209
2017-09-01 | 202 | 199
2017-09-01 00:30 | 197 | 193
2017-09-01 01:00 | 191 | 188
2017-09-01 01:30 | 185 | 182
2017-09-01 02:00 | 183 | 179
2017-09-01 02:30 | 179 | 176
2017-09-01 03:00 | 178 | 174
2017-09-01 03:30 | 176 | 173
2017-09-01 04:00 | 178 | 175
2017-09-01 04:30 | 180 | 177
2017-09-01 05:00 | 179 | 176
2017-09-01 05:30 | 185 | 182
2017-09-01 06:00 | 193 | 190
2017-09-01 06:30 | 209 | 206
2017-09-01 07:00 | 207 | 204
2017-09-01 07:30 | 214 | 211
2017-09-01 08:00 | 198 | 195
2017-09-01 08:30 | 194 | 191
2017-09-01 09:00 | 187 | 184
2017-09-01 09:30 | 190 | 184
2017-09-01 10:00 | 187 | 180
2017-09-01 10:30 | 180 | 174
2017-09-01 11:00 | 177 | 174
2017-09-01 11:30 | 177 | 175
2017-09-01 12:00 | 178 | 176
2017-09-01 12:30 | 199 | 196
2017-09-01 13:00 | 198 | 196
2017-09-01 13:30 | 188 | 186
2017-09-01 14:00 | 187 | 184
2017-09-01 14:30 | 152 | 149
2017-09-01 15:00 | 134 | 131
2017-09-01 15:30 | 132 | 129
2017-09-01 16:00 | 139 | 136
2017-09-01 16:30 | 149 | 146
2017-09-01 17:00 | 158 | 154
2017-09-01 17:30 | 166 | 161
2017-09-01 18:00 | 171 | 166
2017-09-01 18:30 | 177 | 174
2017-09-01 19:00 | 199 | 197
2017-09-01 19:30 | 232 | 229
2017-09-01 20:00 | 233 | 231
2017-09-01 20:30 | 229 | 226
2017-09-01 21:00 | 221 | 218
2017-09-01 21:30 | 213 | 210
2017-09-01 22:00 | 203 | 200
2017-09-01 22:30 | 209 | 207
2017-09-01 23:00 | 214 | 211
2017-09-01 23:30 | 205 | 203
2017-09-02 | 198 | 195
2017-09-02 00:30 | 196 | 193
2017-09-02 01:00 | 189 | 186
2017-09-02 01:30 | 186 | 183
2017-09-02 02:00 | 184 | 181
2017-09-02 02:30 | 179 | 175
2017-09-02 03:00 | 178 | 175
2017-09-02 03:30 | 177 | 173
2017-09-02 04:00 | 177 | 173
2017-09-02 04:30 | 174 | 171
2017-09-02 05:00 | 176 | 172
2017-09-02 05:30 | 177 | 173
2017-09-02 06:00 | 177 | 173
2017-09-02 06:30 | 183 | 179
2017-09-02 07:00 | 173 | 169
2017-09-02 07:30 | 176 | 173
2017-09-02 08:00 | 181 | 178
2017-09-02 08:30 | 188 | 185
2017-09-02 09:00 | 191 | 188
2017-09-02 09:30 | 185 | 182
2017-09-02 10:00 | 137 | 133
2017-09-02 10:30 | 112 | 109
2017-09-02 11:00 | 106 | 102
2017-09-02 11:30 | 103 | 100
2017-09-02 12:00 | 101 | 97
2017-09-02 12:30 | 100 | 95
2017-09-02 13:00 | 96 | 92
2017-09-02 13:30 | 96 | 92
2017-09-02 14:00 | 93 | 89
2017-09-02 14:30 | 91 | 87
2017-09-02 15:00 | 97 | 91
2017-09-02 15:30 | 104 | 98
2017-09-02 16:00 | 112 | 104
2017-09-02 16:30 | 117 | 110
2017-09-02 17:00 | 126 | 119
2017-09-02 17:30 | 133 | 127
2017-09-02 18:00 | 156 | 152
2017-09-02 18:30 | 180 | 177
2017-09-02 19:00 | 166 | 163
2017-09-02 19:30 | 224 | 222
2017-09-02 20:00 | 229 | 226
2017-09-02 20:30 | 221 | 218
2017-09-02 21:00 | 216 | 213
2017-09-02 21:30 | 209 | 206
2017-09-02 22:00 | 203 | 200
2017-09-02 22:30 | 207 | 204
2017-09-02 23:00 | 209 | 205
2017-09-02 23:30 | 200 | 197
2017-09-03 | 194 | 191
2017-09-03 00:30 | 191 | 187
2017-09-03 01:00 | 185 | 182
2017-09-03 01:30 | 179 | 175
2017-09-03 02:00 | 176 | 172
2017-09-03 02:30 | 172 | 168
2017-09-03 03:00 | 169 | 164
2017-09-03 03:30 | 170 | 165
2017-09-03 04:00 | 171 | 166
2017-09-03 04:30 | 169 | 164
2017-09-03 05:00 | 170 | 165
2017-09-03 05:30 | 168 | 163
2017-09-03 06:00 | 170 | 166
2017-09-03 06:30 | 175 | 171
2017-09-03 07:00 | 163 | 158
2017-09-03 07:30 | 163 | 158
2017-09-03 08:00 | 168 | 164
2017-09-03 08:30 | 173 | 169
2017-09-03 09:00 | 177 | 173
2017-09-03 09:30 | 177 | 173
2017-09-03 10:00 | 177 | 173
2017-09-03 10:30 | 177 | 173
2017-09-03 11:00 | 177 | 173
2017-09-03 11:30 | 174 | 170
2017-09-03 12:00 | 169 | 165
2017-09-03 12:30 | 169 | 165
2017-09-03 13:00 | 169 | 165
2017-09-03 13:30 | 168 | 164
2017-09-03 14:00 | 169 | 165
2017-09-03 14:30 | 162 | 158
2017-09-03 15:00 | 166 | 162
2017-09-03 15:30 | 172 | 168
2017-09-03 16:00 | 181 | 177
2017-09-03 16:30 | 185 | 182
2017-09-03 17:00 | 192 | 189
2017-09-03 17:30 | 205 | 202
2017-09-03 18:00 | 226 | 224
2017-09-03 18:30 | 241 | 238
2017-09-03 19:00 | 254 | 250
2017-09-03 19:30 | 249 | 245
2017-09-03 20:00 | 227 | 223
2017-09-03 20:30 | 218 | 214
2017-09-03 21:00 | 212 | 208
2017-09-03 21:30 | 202 | 199
2017-09-03 22:00 | 190 | 187
2017-09-03 22:30 | 191 | 188
2017-09-03 23:00 | 192 | 189
2017-09-03 23:30 | 183 | 180
2017-09-04 | 174 | 171
2017-09-04 00:30 | 171 | 168
2017-09-04 01:00 | 168 | 165
2017-09-04 01:30 | 164 | 160
2017-09-04 02:00 | 162 | 158
2017-09-04 02:30 | 159 | 155
2017-09-04 03:00 | 159 | 155
2017-09-04 03:30 | 161 | 157
2017-09-04 04:00 | 163 | 159
2017-09-04 04:30 | 163 | 159
2017-09-04 05:00 | 164 | 160
2017-09-04 05:30 | 170 | 166
2017-09-04 06:00 | 177 | 174
2017-09-04 06:30 | 195 | 192
2017-09-04 07:00 | 198 | 195
2017-09-04 07:30 | 204 | 202
2017-09-04 08:00 | 210 | 208
2017-09-04 08:30 | 211 | 207
2017-09-04 09:00 | 202 | 197
2017-09-04 09:30 | 199 | 195
2017-09-04 10:00 | 196 | 192
2017-09-04 10:30 | 193 | 188
2017-09-04 11:00 | 187 | 183
2017-09-04 11:30 | 185 | 181
2017-09-04 12:00 | 183 | 179
2017-09-04 12:30 | 184 | 180
2017-09-04 13:00 | 184 | 180
2017-09-04 13:30 | 185 | 181
2017-09-04 14:00 | 186 | 182
2017-09-04 14:30 | 182 | 178
2017-09-04 15:00 | 185 | 181
2017-09-04 15:30 | 190 | 186
2017-09-04 16:00 | 195 | 191
2017-09-04 16:30 | 203 | 199
2017-09-04 17:00 | 209 | 206
2017-09-04 17:30 | 220 | 216
2017-09-04 18:00 | 238 | 235
2017-09-04 18:30 | 251 | 248
2017-09-04 19:00 | 256 | 253
2017-09-04 19:30 | 258 | 256
2017-09-04 20:00 | 249 | 246
2017-09-04 20:30 | 237 | 234
2017-09-04 21:00 | 228 | 225
2017-09-04 21:30 | 218 | 214
2017-09-04 22:00 | 208 | 204
2017-09-04 22:30 | 209 | 205
2017-09-04 23:00 | 206 | 202
2017-09-04 23:30 | 197 | 193
2017-09-05 | 190 | 186
2017-09-05 00:30 | 183 | 179
2017-09-05 01:00 | 176 | 173
2017-09-05 01:30 | 175 | 171
2017-09-05 02:00 | 171 | 167
2017-09-05 02:30 | 167 | 163
2017-09-05 03:00 | 165 | 162
2017-09-05 03:30 | 169 | 165
2017-09-05 04:00 | 169 | 165
2017-09-05 04:30 | 171 | 167
2017-09-05 05:00 | 177 | 174
2017-09-05 05:30 | 184 | 181
2017-09-05 06:00 | 195 | 192
2017-09-05 06:30 | 209 | 206
2017-09-05 07:00 | 210 | 207
2017-09-05 07:30 | 217 | 214
2017-09-05 08:00 | 222 | 219
2017-09-05 08:30 | 217 | 214
2017-09-05 09:00 | 211 | 208
2017-09-05 09:30 | 207 | 203
2017-09-05 10:00 | 201 | 198
2017-09-05 10:30 | 197 | 194
2017-09-05 11:00 | 196 | 193
2017-09-05 11:30 | 193 | 190
2017-09-05 12:00 | 191 | 188
2017-09-05 12:30 | 195 | 192
2017-09-05 13:00 | 196 | 193
2017-09-05 13:30 | 200 | 198
2017-09-05 14:00 | 202 | 199
2017-09-05 14:30 | 197 | 194
2017-09-05 15:00 | 197 | 194
2017-09-05 15:30 | 202 | 199
2017-09-05 16:00 | 215 | 212
2017-09-05 16:30 | 223 | 220
2017-09-05 17:00 | 229 | 226
2017-09-05 17:30 | 243 | 240
2017-09-05 18:00 | 250 | 246
2017-09-05 18:30 | 261 | 258
2017-09-05 19:00 | 275 | 272
2017-09-05 19:30 | 273 | 270
2017-09-05 20:00 | 262 | 258
2017-09-05 20:30 | 251 | 248
2017-09-05 21:00 | 242 | 238
2017-09-05 21:30 | 233 | 228
2017-09-05 22:00 | 220 | 215
2017-09-05 22:30 | 220 | 216
2017-09-05 23:00 | 219 | 214
2017-09-05 23:30 | 207 | 204
2017-09-06 | 196 | 192
2017-09-06 00:30 | 185 | 181
2017-09-06 01:00 | 182 | 178
2017-09-06 01:30 | 177 | 173
2017-09-06 02:00 | 177 | 173
2017-09-06 02:30 | 175 | 171
2017-09-06 03:00 | 172 | 168
2017-09-06 03:30 | 169 | 166
2017-09-06 04:00 | 170 | 166
2017-09-06 04:30 | 177 | 173
2017-09-06 05:00 | 185 | 182
2017-09-06 05:30 | 197 | 193
2017-09-06 06:00 | 202 | 199
2017-09-06 06:30 | 215 | 212
2017-09-06 07:00 | 212 | 210
2017-09-06 07:30 | 214 | 211
2017-09-06 08:00 | 215 | 213
2017-09-06 08:30 | 208 | 206
2017-09-06 09:00 | 199 | 196
2017-09-06 09:30 | 191 | 190
2017-09-06 10:00 | 186 | 184
2017-09-06 10:30 | 185 | 183
2017-09-06 11:00 | 183 | 182
2017-09-06 11:30 | 180 | 178
2017-09-06 12:00 | 178 | 176
2017-09-06 12:30 | 179 | 177
2017-09-06 13:00 | 182 | 180
2017-09-06 13:30 | 186 | 184
2017-09-06 14:00 | 188 | 187
2017-09-06 14:30 | 176 | 174
2017-09-06 15:00 | 177 | 175
2017-09-06 15:30 | 186 | 184
2017-09-06 16:00 | 196 | 194
2017-09-06 16:30 | 207 | 205
2017-09-06 17:00 | 204 | 203
2017-09-06 17:30 | 191 | 189
2017-09-06 18:00 | 171 | 169
2017-09-06 18:30 | 181 | 179
2017-09-06 19:00 | 193 | 191
2017-09-06 19:30 | 189 | 187
2017-09-06 20:00 | 180 | 178
2017-09-06 20:30 | 168 | 166
2017-09-06 21:00 | 159 | 157
2017-09-06 21:30 | 150 | 148
2017-09-06 22:00 | 137 | 135
2017-09-06 22:30 | 137 | 135
2017-09-06 23:00 | 132 | 130
2017-09-06 23:30 | 124 | 122
2017-09-07 | 114 | 112
2017-09-07 00:30 | 172 | 170
2017-09-07 01:00 | 180 | 179
2017-09-07 01:30 | 183 | 181
2017-09-07 02:00 | 186 | 185
2017-09-07 02:30 | 186 | 184
2017-09-07 03:00 | 185 | 183
2017-09-07 03:30 | 184 | 181
2017-09-07 04:00 | 182 | 180
2017-09-07 04:30 | 183 | 180
2017-09-07 05:00 | 186 | 184
2017-09-07 05:30 | 192 | 190
2017-09-07 06:00 | 202 | 200
2017-09-07 06:30 | 213 | 211
2017-09-07 07:00 | 206 | 204
2017-09-07 07:30 | 213 | 211
2017-09-07 08:00 | 214 | 213
2017-09-07 08:30 | 213 | 211
2017-09-07 09:00 | 208 | 206
2017-09-07 09:30 | 214 | 212
2017-09-07 10:00 | 211 | 209
2017-09-07 10:30 | 207 | 205
2017-09-07 11:00 | 207 | 205
2017-09-07 11:30 | 204 | 202
2017-09-07 12:00 | 202 | 199
2017-09-07 12:30 | 199 | 197
2017-09-07 13:00 | 202 | 199
2017-09-07 13:30 | 205 | 202
2017-09-07 14:00 | 208 | 206
2017-09-07 14:30 | 201 | 199
2017-09-07 15:00 | 207 | 205
2017-09-07 15:30 | 212 | 210
2017-09-07 16:00 | 206 | 204
2017-09-07 16:30 | 172 | 169
2017-09-07 17:00 | 144 | 142
2017-09-07 17:30 | 157 | 155
2017-09-07 18:00 | 166 | 164
2017-09-07 18:30 | 179 | 177
2017-09-07 19:00 | 191 | 189
2017-09-07 19:30 | 190 | 189
2017-09-07 20:00 | 184 | 182
2017-09-07 20:30 | 169 | 167
2017-09-07 21:00 | 155 | 153
2017-09-07 21:30 | 143 | 141
2017-09-07 22:00 | 135 | 132
2017-09-07 22:30 | 134 | 132
2017-09-07 23:00 | 134 | 131
2017-09-07 23:30 | 121 | 119
2017-09-08 | 110 | 108
2017-09-08 00:30 | 167 | 165
2017-09-08 01:00 | 177 | 175
2017-09-08 01:30 | 173 | 172
2017-09-08 02:00 | 170 | 168
2017-09-08 02:30 | 166 | 164
2017-09-08 03:00 | 164 | 162
2017-09-08 03:30 | 163 | 161
2017-09-08 04:00 | 162 | 160
2017-09-08 04:30 | 163 | 161
2017-09-08 05:00 | 164 | 162
2017-09-08 05:30 | 170 | 168
2017-09-08 06:00 | 179 | 177
2017-09-08 06:30 | 195 | 193
2017-09-08 07:00 | 198 | 197
2017-09-08 07:30 | 204 | 203
2017-09-08 08:00 | 209 | 207
2017-09-08 08:30 | 208 | 207
2017-09-08 09:00 | 205 | 203
2017-09-08 09:30 | 198 | 196
2017-09-08 10:00 | 193 | 191
2017-09-08 10:30 | 194 | 193
2017-09-08 11:00 | 190 | 188
2017-09-08 11:30 | 183 | 181
2017-09-08 12:00 | 182 | 180
2017-09-08 12:30 | 184 | 183
2017-09-08 13:00 | 189 | 187
2017-09-08 13:30 | 190 | 189
2017-09-08 14:00 | 192 | 191
2017-09-08 14:30 | 194 | 192
2017-09-08 15:00 | 192 | 190
2017-09-08 15:30 | 195 | 193
2017-09-08 16:00 | 199 | 197
2017-09-08 16:30 | 206 | 205
2017-09-08 17:00 | 178 | 176
2017-09-08 17:30 | 147 | 145
2017-09-08 18:00 | 160 | 158
2017-09-08 18:30 | 167 | 166
2017-09-08 19:00 | 174 | 172
2017-09-08 19:30 | 163 | 161
2017-09-08 20:00 | 153 | 152
2017-09-08 20:30 | 144 | 142
2017-09-08 21:00 | 136 | 134
2017-09-08 21:30 | 127 | 126
2017-09-08 22:00 | 118 | 116
2017-09-08 22:30 | 122 | 120
2017-09-08 23:00 | 124 | 122
2017-09-08 23:30 | 114 | 112
2017-09-09 | 107 | 105
2017-09-09 00:30 | 165 | 163
2017-09-09 01:00 | 171 | 170
2017-09-09 01:30 | 166 | 164
2017-09-09 02:00 | 163 | 161
2017-09-09 02:30 | 160 | 158
2017-09-09 03:00 | 157 | 155
2017-09-09 03:30 | 157 | 155
2017-09-09 04:00 | 156 | 154
2017-09-09 04:30 | 157 | 155
2017-09-09 05:00 | 159 | 157
2017-09-09 05:30 | 163 | 161
2017-09-09 06:00 | 165 | 164
2017-09-09 06:30 | 173 | 171
2017-09-09 07:00 | 159 | 157
2017-09-09 07:30 | 159 | 158
2017-09-09 08:00 | 163 | 161
2017-09-09 08:30 | 168 | 167
2017-09-09 09:00 | 171 | 169
2017-09-09 09:30 | 170 | 168
2017-09-09 10:00 | 167 | 166
2017-09-09 10:30 | 168 | 167
2017-09-09 11:00 | 162 | 161
2017-09-09 11:30 | 160 | 158
2017-09-09 12:00 | 160 | 158
2017-09-09 12:30 | 158 | 157
2017-09-09 13:00 | 151 | 149
2017-09-09 13:30 | 150 | 148
2017-09-09 14:00 | 147 | 146
2017-09-09 14:30 | 148 | 147
2017-09-09 15:00 | 151 | 150
2017-09-09 15:30 | 160 | 159
2017-09-09 16:00 | 172 | 171
2017-09-09 16:30 | 180 | 179
2017-09-09 17:00 | 188 | 187
2017-09-09 17:30 | 198 | 197
2017-09-09 18:00 | 206 | 205
2017-09-09 18:30 | 220 | 219
2017-09-09 19:00 | 233 | 231
2017-09-09 19:30 | 226 | 225
2017-09-09 20:00 | 215 | 213
2017-09-09 20:30 | 210 | 208
2017-09-09 21:00 | 204 | 203
2017-09-09 21:30 | 195 | 194
2017-09-09 22:00 | 187 | 186
2017-09-09 22:30 | 192 | 191
2017-09-09 23:00 | 195 | 193
2017-09-09 23:30 | 188 | 186
2017-09-10 | 176 | 174
2017-09-10 00:30 | 171 | 170
2017-09-10 01:00 | 164 | 162
2017-09-10 01:30 | 161 | 159
2017-09-10 02:00 | 157 | 155
2017-09-10 02:30 | 155 | 153
2017-09-10 03:00 | 152 | 151
2017-09-10 03:30 | 150 | 148
2017-09-10 04:00 | 150 | 148
2017-09-10 04:30 | 150 | 148
2017-09-10 05:00 | 151 | 149
2017-09-10 05:30 | 153 | 152
2017-09-10 06:00 | 155 | 153
2017-09-10 06:30 | 157 | 155
2017-09-10 07:00 | 145 | 143
2017-09-10 07:30 | 142 | 139
2017-09-10 08:00 | 148 | 146
2017-09-10 08:30 | 153 | 151
2017-09-10 09:00 | 157 | 155
2017-09-10 09:30 | 159 | 158
2017-09-10 10:00 | 160 | 158
2017-09-10 10:30 | 157 | 155
2017-09-10 11:00 | 152 | 151
2017-09-10 11:30 | 149 | 147
2017-09-10 12:00 | 148 | 146
2017-09-10 12:30 | 145 | 143
2017-09-10 13:00 | 142 | 140
2017-09-10 13:30 | 139 | 138
2017-09-10 14:00 | 139 | 138
2017-09-10 14:30 | 136 | 134
2017-09-10 15:00 | 139 | 137
2017-09-10 15:30 | 146 | 145
2017-09-10 16:00 | 158 | 156
2017-09-10 16:30 | 169 | 167
2017-09-10 17:00 | 177 | 175
2017-09-10 17:30 | 207 | 206
2017-09-10 18:00 | 226 | 224
2017-09-10 18:30 | 236 | 235
2017-09-10 19:00 | 251 | 250
2017-09-10 19:30 | 247 | 246
2017-09-10 20:00 | 236 | 235
2017-09-10 20:30 | 221 | 219
2017-09-10 21:00 | 211 | 209
2017-09-10 21:30 | 203 | 201
2017-09-10 22:00 | 193 | 192
2017-09-10 22:30 | 191 | 189
2017-09-10 23:00 | 188 | 187
2017-09-10 23:30 | 183 | 181
2017-09-11 | 173 | 172
2017-09-11 00:30 | 170 | 168
2017-09-11 01:00 | 165 | 163
2017-09-11 01:30 | 163 | 161
2017-09-11 02:00 | 158 | 156
2017-09-11 02:30 | 157 | 155
2017-09-11 03:00 | 153 | 152
2017-09-11 03:30 | 153 | 151
2017-09-11 04:00 | 159 | 158
2017-09-11 04:30 | 162 | 160
2017-09-11 05:00 | 161 | 159
2017-09-11 05:30 | 167 | 165
2017-09-11 06:00 | 176 | 174
2017-09-11 06:30 | 191 | 189
2017-09-11 07:00 | 192 | 190
2017-09-11 07:30 | 198 | 197
2017-09-11 08:00 | 202 | 201
2017-09-11 08:30 | 201 | 199
2017-09-11 09:00 | 195 | 194
2017-09-11 09:30 | 193 | 192
2017-09-11 10:00 | 188 | 187
2017-09-11 10:30 | 184 | 183
2017-09-11 11:00 | 183 | 182
2017-09-11 11:30 | 187 | 185
2017-09-11 12:00 | 182 | 181
2017-09-11 12:30 | 178 | 177
2017-09-11 13:00 | 181 | 179
2017-09-11 13:30 | 187 | 185
2017-09-11 14:00 | 192 | 190
2017-09-11 14:30 | 189 | 188
2017-09-11 15:00 | 188 | 187
2017-09-11 15:30 | 189 | 188
2017-09-11 16:00 | 193 | 192
2017-09-11 16:30 | 161 | 160
2017-09-11 17:00 | 124 | 122
2017-09-11 17:30 | 126 | 124
2017-09-11 18:00 | 145 | 143
2017-09-11 18:30 | 160 | 159
2017-09-11 19:00 | 173 | 171
2017-09-11 19:30 | 231 | 229
2017-09-11 20:00 | 239 | 238
2017-09-11 20:30 | 230 | 229
2017-09-11 21:00 | 220 | 218
2017-09-11 21:30 | 211 | 209
2017-09-11 22:00 | 201 | 199
2017-09-11 22:30 | 204 | 202
2017-09-11 23:00 | 199 | 197
2017-09-11 23:30 | 189 | 188
2017-09-12 | 182 | 181
2017-09-12 00:30 | 177 | 175
2017-09-12 01:00 | 168 | 166
2017-09-12 01:30 | 165 | 163
2017-09-12 02:00 | 163 | 161
2017-09-12 02:30 | 158 | 157
2017-09-12 03:00 | 155 | 153
2017-09-12 03:30 | 157 | 155
2017-09-12 04:00 | 158 | 156
2017-09-12 04:30 | 158 | 156
2017-09-12 05:00 | 158 | 156
2017-09-12 05:30 | 167 | 165
2017-09-12 06:00 | 179 | 177
2017-09-12 06:30 | 194 | 193
2017-09-12 07:00 | 196 | 195
2017-09-12 07:30 | 205 | 204
2017-09-12 08:00 | 213 | 211
2017-09-12 08:30 | 211 | 210
2017-09-12 09:00 | 204 | 202
2017-09-12 09:30 | 205 | 203
2017-09-12 10:00 | 199 | 197
2017-09-12 10:30 | 195 | 194
2017-09-12 11:00 | 195 | 194
2017-09-12 11:30 | 196 | 195
2017-09-12 12:00 | 194 | 192
2017-09-12 12:30 | 192 | 190
2017-09-12 13:00 | 191 | 190
2017-09-12 13:30 | 193 | 191
2017-09-12 14:00 | 196 | 195
2017-09-12 14:30 | 192 | 191
2017-09-12 15:00 | 194 | 192
2017-09-12 15:30 | 197 | 195
2017-09-12 16:00 | 204 | 203
2017-09-12 16:30 | 210 | 208
2017-09-12 17:00 | 212 | 211
2017-09-12 17:30 | 225 | 223
2017-09-12 18:00 | 233 | 232
2017-09-12 18:30 | 246 | 245
2017-09-12 19:00 | 259 | 258
2017-09-12 19:30 | 255 | 253
2017-09-12 20:00 | 245 | 243
2017-09-12 20:30 | 234 | 232
2017-09-12 21:00 | 226 | 223
2017-09-12 21:30 | 215 | 213
2017-09-12 22:00 | 206 | 203
2017-09-12 22:30 | 206 | 204
2017-09-12 23:00 | 202 | 199
2017-09-12 23:30 | 195 | 192
2017-09-13 | 186 | 183
2017-09-13 00:30 | 181 | 178
2017-09-13 01:00 | 176 | 173
2017-09-13 01:30 | 173 | 170
2017-09-13 02:00 | 167 | 164
2017-09-13 02:30 | 166 | 163
2017-09-13 03:00 | 162 | 158
2017-09-13 03:30 | 164 | 161
2017-09-13 04:00 | 163 | 160
2017-09-13 04:30 | 162 | 160
2017-09-13 05:00 | 165 | 163
2017-09-13 05:30 | 173 | 170
2017-09-13 06:00 | 181 | 179
2017-09-13 06:30 | 199 | 197
2017-09-13 07:00 | 235 | 233
2017-09-13 07:30 | 245 | 242
2017-09-13 08:00 | 244 | 242
2017-09-13 08:30 | 241 | 239
2017-09-13 09:00 | 221 | 219
2017-09-13 09:30 | 212 | 209
2017-09-13 10:00 | 209 | 206
2017-09-13 10:30 | 207 | 205
2017-09-13 11:00 | 205 | 202
2017-09-13 11:30 | 201 | 198
2017-09-13 12:00 | 200 | 197
2017-09-13 12:30 | 200 | 198
2017-09-13 13:00 | 201 | 198
2017-09-13 13:30 | 202 | 199
2017-09-13 14:00 | 205 | 203
2017-09-13 14:30 | 208 | 206
2017-09-13 15:00 | 212 | 210
2017-09-13 15:30 | 219 | 217
2017-09-13 16:00 | 225 | 223
2017-09-13 16:30 | 227 | 226
2017-09-13 17:00 | 235 | 233
2017-09-13 17:30 | 242 | 240
2017-09-13 18:00 | 246 | 243
2017-09-13 18:30 | 265 | 263
2017-09-13 19:00 | 278 | 276
2017-09-13 19:30 | 274 | 271
2017-09-13 20:00 | 263 | 261
2017-09-13 20:30 | 254 | 251
2017-09-13 21:00 | 246 | 243
2017-09-13 21:30 | 234 | 231
2017-09-13 22:00 | 222 | 219
2017-09-13 22:30 | 222 | 220
2017-09-13 23:00 | 221 | 219
2017-09-13 23:30 | 209 | 207
2017-09-14 | 203 | 201
2017-09-14 00:30 | 195 | 194
2017-09-14 01:00 | 186 | 184
2017-09-14 01:30 | 182 | 181
2017-09-14 02:00 | 181 | 179
2017-09-14 02:30 | 179 | 177
2017-09-14 03:00 | 177 | 175
2017-09-14 03:30 | 178 | 177
2017-09-14 04:00 | 177 | 175
2017-09-14 04:30 | 177 | 175
2017-09-14 05:00 | 182 | 180
2017-09-14 05:30 | 189 | 187
2017-09-14 06:00 | 197 | 195
2017-09-14 06:30 | 214 | 211
2017-09-14 07:00 | 221 | 219
2017-09-14 07:30 | 217 | 216
2017-09-14 08:00 | 226 | 225
2017-09-14 08:30 | 226 | 224
2017-09-14 09:00 | 216 | 214
2017-09-14 09:30 | 205 | 203
2017-09-14 10:00 | 200 | 198
2017-09-14 10:30 | 195 | 193
2017-09-14 11:00 | 188 | 186
2017-09-14 11:30 | 188 | 187
2017-09-14 12:00 | 190 | 189
2017-09-14 12:30 | 179 | 177
2017-09-14 13:00 | 163 | 161
2017-09-14 13:30 | 164 | 163
2017-09-14 14:00 | 173 | 171
2017-09-14 14:30 | 183 | 182
2017-09-14 15:00 | 190 | 189
2017-09-14 15:30 | 202 | 200
2017-09-14 16:00 | 210 | 209
2017-09-14 16:30 | 227 | 226
2017-09-14 17:00 | 241 | 240
2017-09-14 17:30 | 224 | 223
2017-09-14 18:00 | 224 | 222
2017-09-14 18:30 | 201 | 200
2017-09-14 19:00 | 206 | 205
2017-09-14 19:30 | 198 | 197
2017-09-14 20:00 | 186 | 184
2017-09-14 20:30 | 175 | 173
2017-09-14 21:00 | 164 | 162
2017-09-14 21:30 | 152 | 150
2017-09-14 22:00 | 139 | 137
2017-09-14 22:30 | 142 | 140
2017-09-14 23:00 | 136 | 134
2017-09-14 23:30 | 126 | 124
2017-09-15 | 116 | 115
2017-09-15 00:30 | 172 | 171
2017-09-15 01:00 | 181 | 180
2017-09-15 01:30 | 177 | 175
2017-09-15 02:00 | 172 | 171
2017-09-15 02:30 | 169 | 167
2017-09-15 03:00 | 166 | 165
2017-09-15 03:30 | 167 | 165
2017-09-15 04:00 | 166 | 164
2017-09-15 04:30 | 164 | 162
2017-09-15 05:00 | 168 | 166
2017-09-15 05:30 | 175 | 174
2017-09-15 06:00 | 185 | 183
2017-09-15 06:30 | 204 | 202
2017-09-15 07:00 | 211 | 210
2017-09-15 07:30 | 215 | 214
2017-09-15 08:00 | 221 | 220
2017-09-15 08:30 | 226 | 224
2017-09-15 09:00 | 224 | 222
2017-09-15 09:30 | 221 | 220
2017-09-15 10:00 | 216 | 215
2017-09-15 10:30 | 213 | 211
2017-09-15 11:00 | 210 | 209
2017-09-15 11:30 | 209 | 208
2017-09-15 12:00 | 208 | 206
2017-09-15 12:30 | 189 | 187
2017-09-15 13:00 | 169 | 168
2017-09-15 13:30 | 169 | 168
2017-09-15 14:00 | 172 | 171
2017-09-15 14:30 | 175 | 174
2017-09-15 15:00 | 200 | 199
2017-09-15 15:30 | 187 | 186
2017-09-15 16:00 | 183 | 182
2017-09-15 16:30 | 186 | 185
2017-09-15 17:00 | 201 | 200
2017-09-15 17:30 | 219 | 218
2017-09-15 18:00 | 224 | 223
2017-09-15 18:30 | 230 | 229
2017-09-15 19:00 | 240 | 239
2017-09-15 19:30 | 237 | 236
2017-09-15 20:00 | 227 | 226
2017-09-15 20:30 | 217 | 215
2017-09-15 21:00 | 210 | 209
2017-09-15 21:30 | 204 | 202
2017-09-15 22:00 | 194 | 193
2017-09-15 22:30 | 199 | 197
2017-09-15 23:00 | 199 | 197
2017-09-15 23:30 | 192 | 190
2017-09-16 | 183 | 181
2017-09-16 00:30 | 176 | 175
2017-09-16 01:00 | 170 | 169
2017-09-16 01:30 | 165 | 164
2017-09-16 02:00 | 162 | 161
2017-09-16 02:30 | 160 | 158
2017-09-16 03:00 | 160 | 158
2017-09-16 03:30 | 161 | 159
2017-09-16 04:00 | 165 | 164
2017-09-16 04:30 | 164 | 163
2017-09-16 05:00 | 164 | 162
2017-09-16 05:30 | 164 | 163
2017-09-16 06:00 | 169 | 168
2017-09-16 06:30 | 175 | 174
2017-09-16 07:00 | 165 | 163
2017-09-16 07:30 | 169 | 168
2017-09-16 08:00 | 170 | 169
2017-09-16 08:30 | 179 | 178
2017-09-16 09:00 | 177 | 176
2017-09-16 09:30 | 177 | 176
2017-09-16 10:00 | 172 | 171
2017-09-16 10:30 | 168 | 167
2017-09-16 11:00 | 139 | 138
2017-09-16 11:30 | 122 | 120
2017-09-16 12:00 | 115 | 114
2017-09-16 12:30 | 113 | 112
2017-09-16 13:00 | 113 | 112
2017-09-16 13:30 | 113 | 112
2017-09-16 14:00 | 114 | 113
2017-09-16 14:30 | 128 | 126
2017-09-16 15:00 | 152 | 151
2017-09-16 15:30 | 153 | 152
2017-09-16 16:00 | 162 | 161
2017-09-16 16:30 | 175 | 174
2017-09-16 17:00 | 185 | 184
2017-09-16 17:30 | 196 | 195
2017-09-16 18:00 | 206 | 205
2017-09-16 18:30 | 217 | 216
2017-09-16 19:00 | 230 | 228
2017-09-16 19:30 | 235 | 234
2017-09-16 20:00 | 226 | 225
2017-09-16 20:30 | 215 | 214
2017-09-16 21:00 | 207 | 206
2017-09-16 21:30 | 199 | 197
2017-09-16 22:00 | 194 | 192
2017-09-16 22:30 | 199 | 197
2017-09-16 23:00 | 199 | 197
2017-09-16 23:30 | 192 | 189
2017-09-17 | 182 | 181
2017-09-17 00:30 | 175 | 173
2017-09-17 01:00 | 169 | 168
2017-09-17 01:30 | 166 | 164
2017-09-17 02:00 | 160 | 158
2017-09-17 02:30 | 157 | 156
2017-09-17 03:00 | 157 | 155
2017-09-17 03:30 | 158 | 156
2017-09-17 04:00 | 156 | 154
2017-09-17 04:30 | 157 | 155
2017-09-17 05:00 | 157 | 155
2017-09-17 05:30 | 157 | 155
2017-09-17 06:00 | 157 | 155
2017-09-17 06:30 | 159 | 157
2017-09-17 07:00 | 154 | 153
2017-09-17 07:30 | 145 | 143
2017-09-17 08:00 | 147 | 146
2017-09-17 08:30 | 150 | 149
2017-09-17 09:00 | 157 | 155
2017-09-17 09:30 | 162 | 160
2017-09-17 10:00 | 164 | 163
2017-09-17 10:30 | 161 | 160
2017-09-17 11:00 | 160 | 159
2017-09-17 11:30 | 161 | 160
2017-09-17 12:00 | 153 | 152
2017-09-17 12:30 | 152 | 150
2017-09-17 13:00 | 150 | 148
2017-09-17 13:30 | 152 | 150
2017-09-17 14:00 | 152 | 151
2017-09-17 14:30 | 157 | 155
2017-09-17 15:00 | 168 | 167
2017-09-17 15:30 | 169 | 168
2017-09-17 16:00 | 177 | 176
2017-09-17 16:30 | 188 | 186
2017-09-17 17:00 | 193 | 192
2017-09-17 17:30 | 204 | 203
2017-09-17 18:00 | 216 | 214
2017-09-17 18:30 | 231 | 229
2017-09-17 19:00 | 241 | 239
2017-09-17 19:30 | 234 | 233
2017-09-17 20:00 | 224 | 222
2017-09-17 20:30 | 215 | 213
2017-09-17 21:00 | 208 | 206
2017-09-17 21:30 | 201 | 199
2017-09-17 22:00 | 191 | 188
2017-09-17 22:30 | 192 | 190
2017-09-17 23:00 | 190 | 188
2017-09-17 23:30 | 184 | 182
2017-09-18 | 178 | 176
2017-09-18 00:30 | 172 | 170
2017-09-18 01:00 | 171 | 169
2017-09-18 01:30 | 169 | 166
2017-09-18 02:00 | 168 | 166
2017-09-18 02:30 | 164 | 161
2017-09-18 03:00 | 161 | 159
2017-09-18 03:30 | 160 | 158
2017-09-18 04:00 | 161 | 159
2017-09-18 04:30 | 161 | 159
2017-09-18 05:00 | 161 | 159
2017-09-18 05:30 | 168 | 166
2017-09-18 06:00 | 175 | 173
2017-09-18 06:30 | 187 | 185
2017-09-18 07:00 | 183 | 181
2017-09-18 07:30 | 187 | 185
2017-09-18 08:00 | 195 | 194
2017-09-18 08:30 | 205 | 204
2017-09-18 09:00 | 207 | 205
2017-09-18 09:30 | 202 | 200
2017-09-18 10:00 | 199 | 198
2017-09-18 10:30 | 188 | 186
2017-09-18 11:00 | 156 | 155
2017-09-18 11:30 | 152 | 151
2017-09-18 12:00 | 153 | 152
2017-09-18 12:30 | 155 | 154
2017-09-18 13:00 | 159 | 157
2017-09-18 13:30 | 165 | 163
2017-09-18 14:00 | 168 | 167
2017-09-18 14:30 | 185 | 184
2017-09-18 15:00 | 175 | 174
2017-09-18 15:30 | 170 | 168
2017-09-18 16:00 | 161 | 159
2017-09-18 16:30 | 163 | 161
2017-09-18 17:00 | 185 | 184
2017-09-18 17:30 | 217 | 216
2017-09-18 18:00 | 223 | 222
2017-09-18 18:30 | 201 | 199
2017-09-18 19:00 | 193 | 192
2017-09-18 19:30 | 175 | 174
2017-09-18 20:00 | 168 | 166
2017-09-18 20:30 | 217 | 215
2017-09-18 21:00 | 224 | 222
2017-09-18 21:30 | 214 | 211
2017-09-18 22:00 | 201 | 198
2017-09-18 22:30 | 204 | 201
2017-09-18 23:00 | 202 | 199
2017-09-18 23:30 | 195 | 193
2017-09-19 | 187 | 184
2017-09-19 00:30 | 186 | 184
2017-09-19 01:00 | 181 | 179
2017-09-19 01:30 | 180 | 178
2017-09-19 02:00 | 180 | 178
2017-09-19 02:30 | 179 | 176
2017-09-19 03:00 | 172 | 169
2017-09-19 03:30 | 172 | 169
2017-09-19 04:00 | 172 | 169
2017-09-19 04:30 | 174 | 171
2017-09-19 05:00 | 178 | 175
2017-09-19 05:30 | 185 | 182
2017-09-19 06:00 | 197 | 195
2017-09-19 06:30 | 210 | 208
2017-09-19 07:00 | 202 | 199
2017-09-19 07:30 | 213 | 210
2017-09-19 08:00 | 221 | 218
2017-09-19 08:30 | 228 | 226
2017-09-19 09:00 | 231 | 229
2017-09-19 09:30 | 237 | 235
2017-09-19 10:00 | 213 | 211
2017-09-19 10:30 | 169 | 166
2017-09-19 11:00 | 167 | 165
2017-09-19 11:30 | 180 | 178
2017-09-19 12:00 | 227 | 225
2017-09-19 12:30 | 226 | 224
2017-09-19 13:00 | 223 | 221
2017-09-19 13:30 | 223 | 220
2017-09-19 14:00 | 226 | 224
2017-09-19 14:30 | 231 | 229
2017-09-19 15:00 | 230 | 228
2017-09-19 15:30 | 220 | 218
2017-09-19 16:00 | 215 | 212
2017-09-19 16:30 | 190 | 187
2017-09-19 17:00 | 195 | 192
2017-09-19 17:30 | 198 | 196
2017-09-19 18:00 | 216 | 214
2017-09-19 18:30 | 234 | 232
2017-09-19 19:00 | 244 | 242
2017-09-19 19:30 | 238 | 236
2017-09-19 20:00 | 244 | 241
2017-09-19 20:30 | 255 | 252
2017-09-19 21:00 | 246 | 243
2017-09-19 21:30 | 237 | 234
2017-09-19 22:00 | 223 | 220
2017-09-19 22:30 | 225 | 222
2017-09-19 23:00 | 226 | 223
2017-09-19 23:30 | 219 | 217
2017-09-20 | 204 | 202
2017-09-20 00:30 | 197 | 194
2017-09-20 01:00 | 185 | 183
2017-09-20 01:30 | 182 | 179
2017-09-20 02:00 | 179 | 176
2017-09-20 02:30 | 176 | 173
2017-09-20 03:00 | 175 | 172
2017-09-20 03:30 | 174 | 172
2017-09-20 04:00 | 172 | 169
2017-09-20 04:30 | 172 | 170
2017-09-20 05:00 | 175 | 172
2017-09-20 05:30 | 178 | 176
2017-09-20 06:00 | 164 | 160
2017-09-20 06:30 | 161 | 158
2017-09-20 07:00 | 157 | 154
2017-09-20 07:30 | 161 | 158
2017-09-20 08:00 | 171 | 168
2017-09-20 08:30 | 171 | 169
2017-09-20 09:00 | 168 | 166
2017-09-20 09:30 | 163 | 161
2017-09-20 10:00 | 168 | 166
2017-09-20 10:30 | 169 | 166
2017-09-20 11:00 | 165 | 163
2017-09-20 11:30 | 160 | 158
2017-09-20 12:00 | 151 | 149
2017-09-20 12:30 | 125 | 122
2017-09-20 13:00 | 128 | 125
2017-09-20 13:30 | 130 | 127
2017-09-20 14:00 | 133 | 131
2017-09-20 14:30 | 138 | 136
2017-09-20 15:00 | 144 | 141
2017-09-20 15:30 | 148 | 145
2017-09-20 16:00 | 149 | 146
2017-09-20 16:30 | 152 | 150
2017-09-20 17:00 | 159 | 157
2017-09-20 17:30 | 163 | 161
2017-09-20 18:00 | 160 | 158
2017-09-20 18:30 | 170 | 167
2017-09-20 19:00 | 189 | 188
2017-09-20 19:30 | 197 | 195
2017-09-20 20:00 | 202 | 201
2017-09-20 20:30 | 225 | 224
2017-09-20 21:00 | 219 | 218
2017-09-20 21:30 | 208 | 207
2017-09-20 22:00 | 201 | 200
2017-09-20 22:30 | 206 | 205
2017-09-20 23:00 | 203 | 202
2017-09-20 23:30 | 195 | 193
2017-09-21 | 189 | 187
2017-09-21 00:30 | 183 | 182
2017-09-21 01:00 | 181 | 180
2017-09-21 01:30 | 178 | 176
2017-09-21 02:00 | 174 | 172
2017-09-21 02:30 | 171 | 169
2017-09-21 03:00 | 169 | 168
2017-09-21 03:30 | 166 | 164
2017-09-21 04:00 | 166 | 164
2017-09-21 04:30 | 164 | 162
2017-09-21 05:00 | 165 | 163
2017-09-21 05:30 | 168 | 166
2017-09-21 06:00 | 177 | 175
2017-09-21 06:30 | 195 | 193
2017-09-21 07:00 | 202 | 200
2017-09-21 07:30 | 187 | 186
2017-09-21 08:00 | 189 | 187
2017-09-21 08:30 | 183 | 181
2017-09-21 09:00 | 162 | 161
2017-09-21 09:30 | 181 | 180
2017-09-21 10:00 | 156 | 155
2017-09-21 10:30 | 151 | 150
2017-09-21 11:00 | 151 | 150
2017-09-21 11:30 | 148 | 147
2017-09-21 12:00 | 149 | 147
2017-09-21 12:30 | 150 | 149
2017-09-21 13:00 | 157 | 156
2017-09-21 13:30 | 180 | 179
2017-09-21 14:00 | 184 | 183
2017-09-21 14:30 | 185 | 184
2017-09-21 15:00 | 185 | 184
2017-09-21 15:30 | 190 | 189
2017-09-21 16:00 | 191 | 190
2017-09-21 16:30 | 202 | 201
2017-09-21 17:00 | 204 | 203
2017-09-21 17:30 | 192 | 190
2017-09-21 18:00 | 210 | 209
2017-09-21 18:30 | 226 | 225
2017-09-21 19:00 | 239 | 238
2017-09-21 19:30 | 244 | 243
2017-09-21 20:00 | 265 | 263
2017-09-21 20:30 | 255 | 253
2017-09-21 21:00 | 244 | 242
2017-09-21 21:30 | 231 | 229
2017-09-21 22:00 | 219 | 217
2017-09-21 22:30 | 229 | 227
2017-09-21 23:00 | 222 | 220
2017-09-21 23:30 | 211 | 210
2017-09-22 | 205 | 203
2017-09-22 00:30 | 198 | 196
2017-09-22 01:00 | 189 | 187
2017-09-22 01:30 | 185 | 183
2017-09-22 02:00 | 182 | 181
2017-09-22 02:30 | 181 | 179
2017-09-22 03:00 | 176 | 174
2017-09-22 03:30 | 175 | 173
2017-09-22 04:00 | 175 | 173
2017-09-22 04:30 | 177 | 175
2017-09-22 05:00 | 177 | 175
2017-09-22 05:30 | 182 | 180
2017-09-22 06:00 | 190 | 188
2017-09-22 06:30 | 200 | 198
2017-09-22 07:00 | 212 | 210
2017-09-22 07:30 | 201 | 200
2017-09-22 08:00 | 202 | 201
2017-09-22 08:30 | 226 | 225
2017-09-22 09:00 | 231 | 230
2017-09-22 09:30 | 239 | 237
2017-09-22 10:00 | 235 | 233
2017-09-22 10:30 | 219 | 217
2017-09-22 11:00 | 216 | 214
2017-09-22 11:30 | 211 | 209
2017-09-22 12:00 | 205 | 203
2017-09-22 12:30 | 202 | 200
2017-09-22 13:00 | 202 | 200
2017-09-22 13:30 | 209 | 207
2017-09-22 14:00 | 225 | 223
2017-09-22 14:30 | 234 | 232
2017-09-22 15:00 | 243 | 241
2017-09-22 15:30 | 240 | 238
2017-09-22 16:00 | 244 | 242
2017-09-22 16:30 | 249 | 247
2017-09-22 17:00 | 249 | 247
2017-09-22 17:30 | 235 | 233
2017-09-22 18:00 | 250 | 248
2017-09-22 18:30 | 256 | 254
2017-09-22 19:00 | 264 | 262
2017-09-22 19:30 | 264 | 262
2017-09-22 20:00 | 253 | 251
2017-09-22 20:30 | 242 | 240
2017-09-22 21:00 | 233 | 231
2017-09-22 21:30 | 223 | 221
2017-09-22 22:00 | 214 | 212
2017-09-22 22:30 | 230 | 228
2017-09-22 23:00 | 224 | 222
2017-09-22 23:30 | 215 | 213
2017-09-23 | 205 | 202
2017-09-23 00:30 | 200 | 197
2017-09-23 01:00 | 195 | 191
2017-09-23 01:30 | 189 | 185
2017-09-23 02:00 | 184 | 181
2017-09-23 02:30 | 182 | 179
2017-09-23 03:00 | 180 | 176
2017-09-23 03:30 | 179 | 175
2017-09-23 04:00 | 179 | 175
2017-09-23 04:30 | 179 | 175
2017-09-23 05:00 | 179 | 175
2017-09-23 05:30 | 184 | 180
2017-09-23 06:00 | 186 | 182
2017-09-23 06:30 | 192 | 189
2017-09-23 07:00 | 196 | 192
2017-09-23 07:30 | 203 | 200
2017-09-23 08:00 | 209 | 205
2017-09-23 08:30 | 216 | 213
2017-09-23 09:00 | 219 | 216
2017-09-23 09:30 | 218 | 215
2017-09-23 10:00 | 196 | 193
2017-09-23 10:30 | 169 | 165
2017-09-23 11:00 | 137 | 133
2017-09-23 11:30 | 120 | 116
2017-09-23 12:00 | 118 | 114
2017-09-23 12:30 | 120 | 115
2017-09-23 13:00 | 144 | 140
2017-09-23 13:30 | 153 | 150
2017-09-23 14:00 | 163 | 159
2017-09-23 14:30 | 168 | 165
2017-09-23 15:00 | 176 | 172
2017-09-23 15:30 | 184 | 181
2017-09-23 16:00 | 190 | 187
2017-09-23 16:30 | 197 | 194
2017-09-23 17:00 | 206 | 203
2017-09-23 17:30 | 216 | 214
2017-09-23 18:00 | 197 | 194
2017-09-23 18:30 | 192 | 190
2017-09-23 19:00 | 202 | 200
2017-09-23 19:30 | 267 | 265
2017-09-23 20:00 | 277 | 275
2017-09-23 20:30 | 263 | 260
2017-09-23 21:00 | 252 | 250
2017-09-23 21:30 | 242 | 239
2017-09-23 22:00 | 229 | 226
2017-09-23 22:30 | 222 | 219
2017-09-23 23:00 | 215 | 211
2017-09-23 23:30 | 204 | 200
2017-09-24 | 197 | 193
2017-09-24 00:30 | 191 | 187
2017-09-24 01:00 | 185 | 181
2017-09-24 01:30 | 178 | 174
2017-09-24 02:00 | 174 | 170
2017-09-24 02:30 | 171 | 167
2017-09-24 03:00 | 169 | 165
2017-09-24 03:30 | 168 | 164
2017-09-24 04:00 | 166 | 162
2017-09-24 04:30 | 166 | 162
2017-09-24 05:00 | 167 | 163
2017-09-24 05:30 | 167 | 163
2017-09-24 06:00 | 167 | 163
2017-09-24 06:30 | 169 | 165
2017-09-24 07:00 | 175 | 171
2017-09-24 07:30 | 180 | 176
2017-09-24 08:00 | 186 | 182
2017-09-24 08:30 | 190 | 186
2017-09-24 09:00 | 192 | 188
2017-09-24 09:30 | 195 | 192
2017-09-24 10:00 | 177 | 173
2017-09-24 10:30 | 170 | 166
2017-09-24 11:00 | 165 | 161
2017-09-24 11:30 | 164 | 160
2017-09-24 12:00 | 161 | 157
2017-09-24 12:30 | 160 | 156
2017-09-24 13:00 | 159 | 155
2017-09-24 13:30 | 174 | 171
2017-09-24 14:00 | 185 | 182
2017-09-24 14:30 | 190 | 187
2017-09-24 15:00 | 196 | 193
2017-09-24 15:30 | 203 | 200
2017-09-24 16:00 | 210 | 207
2017-09-24 16:30 | 221 | 219
2017-09-24 17:00 | 234 | 231
2017-09-24 17:30 | 243 | 241
2017-09-24 18:00 | 255 | 252
2017-09-24 18:30 | 266 | 263
2017-09-24 19:00 | 278 | 276
2017-09-24 19:30 | 274 | 272
2017-09-24 20:00 | 264 | 261
2017-09-24 20:30 | 256 | 253
2017-09-24 21:00 | 249 | 246
2017-09-24 21:30 | 241 | 237
2017-09-24 22:00 | 231 | 227
2017-09-24 22:30 | 221 | 217
2017-09-24 23:00 | 208 | 204
2017-09-24 23:30 | 199 | 195
2017-09-25 | 192 | 188
2017-09-25 00:30 | 187 | 184
2017-09-25 01:00 | 183 | 179
2017-09-25 01:30 | 180 | 177
2017-09-25 02:00 | 177 | 173
2017-09-25 02:30 | 173 | 169
2017-09-25 03:00 | 173 | 169
2017-09-25 03:30 | 173 | 169
2017-09-25 04:00 | 173 | 169
2017-09-25 04:30 | 173 | 169
2017-09-25 05:00 | 174 | 171
2017-09-25 05:30 | 180 | 176
2017-09-25 06:00 | 184 | 180
2017-09-25 06:30 | 195 | 191
2017-09-25 07:00 | 204 | 201
2017-09-25 07:30 | 199 | 195
2017-09-25 08:00 | 204 | 200
2017-09-25 08:30 | 208 | 205
2017-09-25 09:00 | 208 | 205
2017-09-25 09:30 | 207 | 204
2017-09-25 10:00 | 201 | 198
2017-09-25 10:30 | 197 | 194
2017-09-25 11:00 | 184 | 181
2017-09-25 11:30 | 159 | 156
2017-09-25 12:00 | 160 | 157
2017-09-25 12:30 | 161 | 158
2017-09-25 13:00 | 160 | 157
2017-09-25 13:30 | 162 | 159
2017-09-25 14:00 | 167 | 164
2017-09-25 14:30 | 172 | 169
2017-09-25 15:00 | 174 | 171
2017-09-25 15:30 | 147 | 143
2017-09-25 16:00 | 129 | 125
2017-09-25 16:30 | 134 | 131
2017-09-25 17:00 | 142 | 139
2017-09-25 17:30 | 146 | 143
2017-09-25 18:00 | 157 | 154
2017-09-25 18:30 | 172 | 169
2017-09-25 19:00 | 186 | 184
2017-09-25 19:30 | 182 | 179
2017-09-25 20:00 | 171 | 168
2017-09-25 20:30 | 157 | 154
2017-09-25 21:00 | 146 | 142
2017-09-25 21:30 | 212 | 209
2017-09-25 22:00 | 219 | 217
2017-09-25 22:30 | 211 | 208
2017-09-25 23:00 | 211 | 208
2017-09-25 23:30 | 203 | 199
2017-09-26 | 193 | 190
2017-09-26 00:30 | 188 | 185
2017-09-26 01:00 | 184 | 181
2017-09-26 01:30 | 181 | 178
2017-09-26 02:00 | 178 | 175
2017-09-26 02:30 | 177 | 174
2017-09-26 03:00 | 178 | 175
2017-09-26 03:30 | 179 | 176
2017-09-26 04:00 | 179 | 176
2017-09-26 04:30 | 180 | 177
2017-09-26 05:00 | 185 | 182
2017-09-26 05:30 | 188 | 185
2017-09-26 06:00 | 194 | 191
2017-09-26 06:30 | 207 | 205
2017-09-26 07:00 | 209 | 206
2017-09-26 07:30 | 200 | 197
2017-09-26 08:00 | 210 | 208
2017-09-26 08:30 | 227 | 224
2017-09-26 09:00 | 228 | 224
2017-09-26 09:30 | 222 | 219
2017-09-26 10:00 | 215 | 212
2017-09-26 10:30 | 189 | 185
2017-09-26 11:00 | 179 | 175
2017-09-26 11:30 | 176 | 172
2017-09-26 12:00 | 204 | 200
2017-09-26 12:30 | 211 | 208
2017-09-26 13:00 | 206 | 203
2017-09-26 13:30 | 172 | 168
2017-09-26 14:00 | 166 | 163
2017-09-26 14:30 | 169 | 166
2017-09-26 15:00 | 172 | 168
2017-09-26 15:30 | 180 | 177
2017-09-26 16:00 | 188 | 184
2017-09-26 16:30 | 186 | 183
2017-09-26 17:00 | 202 | 199
2017-09-26 17:30 | 198 | 195
2017-09-26 18:00 | 218 | 215
2017-09-26 18:30 | 194 | 192
2017-09-26 19:00 | 227 | 225
2017-09-26 19:30 | 222 | 219
2017-09-26 20:00 | 207 | 204
2017-09-26 20:30 | 192 | 189
2017-09-26 21:00 | 183 | 179
2017-09-26 21:30 | 173 | 169
2017-09-26 22:00 | 192 | 189
2017-09-26 22:30 | 184 | 181
2017-09-26 23:00 | 157 | 153
2017-09-26 23:30 | 211 | 207
2017-09-27 | 208 | 204
2017-09-27 00:30 | 203 | 200
2017-09-27 01:00 | 196 | 193
2017-09-27 01:30 | 192 | 189
2017-09-27 02:00 | 187 | 183
2017-09-27 02:30 | 180 | 176
2017-09-27 03:00 | 177 | 174
2017-09-27 03:30 | 175 | 172
2017-09-27 04:00 | 176 | 173
2017-09-27 04:30 | 178 | 175
2017-09-27 05:00 | 179 | 176
2017-09-27 05:30 | 186 | 183
2017-09-27 06:00 | 190 | 188
2017-09-27 06:30 | 200 | 197
2017-09-27 07:00 | 210 | 207
2017-09-27 07:30 | 205 | 202
2017-09-27 08:00 | 211 | 208
2017-09-27 08:30 | 219 | 216
2017-09-27 09:00 | 218 | 215
2017-09-27 09:30 | 195 | 192
2017-09-27 10:00 | 177 | 174
2017-09-27 10:30 | 179 | 176
2017-09-27 11:00 | 175 | 171
2017-09-27 11:30 | 180 | 177
2017-09-27 12:00 | 177 | 173
2017-09-27 12:30 | 178 | 174
2017-09-27 13:00 | 183 | 180
2017-09-27 13:30 | 182 | 178
2017-09-27 14:00 | 184 | 180
2017-09-27 14:30 | 192 | 189
2017-09-27 15:00 | 223 | 220
2017-09-27 15:30 | 225 | 221
2017-09-27 16:00 | 235 | 232
2017-09-27 16:30 | 232 | 229
2017-09-27 17:00 | 238 | 235
2017-09-27 17:30 | 256 | 253
2017-09-27 18:00 | 266 | 263
2017-09-27 18:30 | 274 | 271
2017-09-27 19:00 | 284 | 282
2017-09-27 19:30 | 280 | 278
2017-09-27 20:00 | 269 | 267
2017-09-27 20:30 | 258 | 256
2017-09-27 21:00 | 250 | 247
2017-09-27 21:30 | 241 | 238
2017-09-27 22:00 | 229 | 226
2017-09-27 22:30 | 231 | 228
2017-09-27 23:00 | 220 | 217
2017-09-27 23:30 | 209 | 206
2017-09-28 | 199 | 196
2017-09-28 00:30 | 194 | 192
2017-09-28 01:00 | 189 | 186
2017-09-28 01:30 | 185 | 182
2017-09-28 02:00 | 182 | 179
2017-09-28 02:30 | 178 | 175
2017-09-28 03:00 | 177 | 174
2017-09-28 03:30 | 174 | 171
2017-09-28 04:00 | 174 | 172
2017-09-28 04:30 | 180 | 177
2017-09-28 05:00 | 181 | 179
2017-09-28 05:30 | 186 | 183
2017-09-28 06:00 | 194 | 192
2017-09-28 06:30 | 208 | 205
2017-09-28 07:00 | 211 | 208
2017-09-28 07:30 | 201 | 198
2017-09-28 08:00 | 209 | 206
2017-09-28 08:30 | 215 | 213
2017-09-28 09:00 | 213 | 211
2017-09-28 09:30 | 208 | 206
2017-09-28 10:00 | 203 | 201
2017-09-28 10:30 | 201 | 199
2017-09-28 11:00 | 197 | 195
2017-09-28 11:30 | 199 | 196
2017-09-28 12:00 | 201 | 199
2017-09-28 12:30 | 206 | 204
2017-09-28 13:00 | 182 | 179
2017-09-28 13:30 | 162 | 160
2017-09-28 14:00 | 165 | 162
2017-09-28 14:30 | 192 | 190
2017-09-28 15:00 | 201 | 199
2017-09-28 15:30 | 193 | 191
2017-09-28 16:00 | 186 | 183
2017-09-28 16:30 | 152 | 150
2017-09-28 17:00 | 140 | 138
2017-09-28 17:30 | 164 | 162
2017-09-28 18:00 | 171 | 168
2017-09-28 18:30 | 147 | 145
2017-09-28 19:00 | 158 | 156
2017-09-28 19:30 | 216 | 214
2017-09-28 20:00 | 230 | 228
2017-09-28 20:30 | 219 | 217
2017-09-28 21:00 | 222 | 220
2017-09-28 21:30 | 213 | 211
2017-09-28 22:00 | 202 | 199
2017-09-28 22:30 | 188 | 185
2017-09-28 23:00 | 176 | 173
2017-09-28 23:30 | 204 | 201
2017-09-29 | 203 | 200
2017-09-29 00:30 | 197 | 194
2017-09-29 01:00 | 190 | 186
2017-09-29 01:30 | 186 | 183
2017-09-29 02:00 | 184 | 181
2017-09-29 02:30 | 179 | 176
2017-09-29 03:00 | 177 | 173
2017-09-29 03:30 | 176 | 172
2017-09-29 04:00 | 176 | 172
2017-09-29 04:30 | 176 | 172
2017-09-29 05:00 | 176 | 173
2017-09-29 05:30 | 182 | 179
2017-09-29 06:00 | 189 | 186
2017-09-29 06:30 | 200 | 197
2017-09-29 07:00 | 211 | 209
2017-09-29 07:30 | 223 | 220
2017-09-29 08:00 | 226 | 224
2017-09-29 08:30 | 232 | 230
2017-09-29 09:00 | 234 | 232
2017-09-29 09:30 | 191 | 189
2017-09-29 10:00 | 141 | 139
2017-09-29 10:30 | 189 | 187
2017-09-29 11:00 | 203 | 201
2017-09-29 11:30 | 200 | 198
2017-09-29 12:00 | 201 | 199
2017-09-29 12:30 | 201 | 198
2017-09-29 13:00 | 172 | 169
2017-09-29 13:30 | 179 | 176
2017-09-29 14:00 | 190 | 187
2017-09-29 14:30 | 194 | 191
2017-09-29 15:00 | 199 | 196
2017-09-29 15:30 | 193 | 190
2017-09-29 16:00 | 175 | 173
2017-09-29 16:30 | 171 | 169
2017-09-29 17:00 | 139 | 136
2017-09-29 17:30 | 166 | 163
2017-09-29 18:00 | 189 | 186
2017-09-29 18:30 | 197 | 194
2017-09-29 19:00 | 208 | 205
2017-09-29 19:30 | 215 | 213
2017-09-29 20:00 | 213 | 211
2017-09-29 20:30 | 218 | 216
2017-09-29 21:00 | 244 | 242
2017-09-29 21:30 | 243 | 241
2017-09-29 22:00 | 234 | 231
2017-09-29 22:30 | 223 | 221
2017-09-29 23:00 | 213 | 211
2017-09-29 23:30 | 217 | 214
2017-09-30 | 211 | 207
2017-09-30 00:30 | 203 | 200
2017-09-30 01:00 | 197 | 194
2017-09-30 01:30 | 190 | 187
2017-09-30 02:00 | 186 | 183
2017-09-30 02:30 | 186 | 183
2017-09-30 03:00 | 186 | 183
2017-09-30 03:30 | 189 | 186
2017-09-30 04:00 | 189 | 187
2017-09-30 04:30 | 188 | 185
2017-09-30 05:00 | 188 | 185
2017-09-30 05:30 | 189 | 186
2017-09-30 06:00 | 193 | 190
2017-09-30 06:30 | 197 | 194
2017-09-30 07:00 | 201 | 199
2017-09-30 07:30 | 207 | 204
2017-09-30 08:00 | 214 | 211
2017-09-30 08:30 | 222 | 220
2017-09-30 09:00 | 227 | 225
2017-09-30 09:30 | 229 | 227
2017-09-30 10:00 | 212 | 209
2017-09-30 10:30 | 200 | 197
2017-09-30 11:00 | 198 | 195
2017-09-30 11:30 | 196 | 193
2017-09-30 12:00 | 191 | 189
2017-09-30 12:30 | 194 | 192
2017-09-30 13:00 | 201 | 198
2017-09-30 13:30 | 221 | 219
2017-09-30 14:00 | 235 | 233
2017-09-30 14:30 | 235 | 233
2017-09-30 15:00 | 236 | 234
2017-09-30 15:30 | 244 | 242
2017-09-30 16:00 | 221 | 219
2017-09-30 16:30 | 215 | 213
2017-09-30 17:00 | 219 | 217
2017-09-30 17:30 | 224 | 221
2017-09-30 18:00 | 229 | 227
2017-09-30 18:30 | 214 | 212
2017-09-30 19:00 | 211 | 209
2017-09-30 19:30 | 231 | 229
2017-09-30 20:00 | 239 | 237
2017-09-30 20:30 | 263 | 261
2017-09-30 21:00 | 260 | 258
2017-09-30 21:30 | 254 | 252
2017-09-30 22:00 | 246 | 244
2017-09-30 22:30 | 238 | 235
2017-09-30 23:00 | 230 | 227
2017-09-30 23:30 | 222 | 219
2017-10-01 | 214 | 211
2017-10-01 00:30 | 210 | 207
2017-10-01 01:00 | 202 | 199
2017-10-01 01:30 | 195 | 193
2017-10-01 02:00 | 192 | 189
2017-10-01 02:30 | 192 | 189
2017-10-01 03:00 | 190 | 187
2017-10-01 03:30 | 188 | 185
2017-10-01 04:00 | 188 | 185
2017-10-01 04:30 | 188 | 185
2017-10-01 05:00 | 188 | 185
2017-10-01 05:30 | 189 | 186
2017-10-01 06:00 | 188 | 186
2017-10-01 06:30 | 191 | 189
2017-10-01 07:00 | 194 | 192
2017-10-01 07:30 | 200 | 197
2017-10-01 08:00 | 209 | 206
2017-10-01 08:30 | 228 | 226
2017-10-01 09:00 | 238 | 236
2017-10-01 09:30 | 241 | 238
2017-10-01 10:00 | 224 | 222
2017-10-01 10:30 | 214 | 211
2017-10-01 11:00 | 207 | 204
2017-10-01 11:30 | 204 | 201
2017-10-01 12:00 | 209 | 207
2017-10-01 12:30 | 211 | 208
2017-10-01 13:00 | 212 | 210
2017-10-01 13:30 | 228 | 225
2017-10-01 14:00 | 237 | 235
2017-10-01 14:30 | 241 | 239
2017-10-01 15:00 | 244 | 242
2017-10-01 15:30 | 249 | 247
2017-10-01 16:00 | 256 | 254
2017-10-01 16:30 | 208 | 205
2017-10-01 17:00 | 208 | 205
2017-10-01 17:30 | 215 | 212
2017-10-01 18:00 | 220 | 217
2017-10-01 18:30 | 220 | 218
2017-10-01 19:00 | 224 | 221
2017-10-01 19:30 | 254 | 251
2017-10-01 20:00 | 262 | 260
2017-10-01 20:30 | 265 | 263
2017-10-01 21:00 | 262 | 259
2017-10-01 21:30 | 257 | 254
2017-10-01 22:00 | 250 | 248
2017-10-01 22:30 | 240 | 237
2017-10-01 23:00 | 231 | 228
2017-10-01 23:30 | 220 | 216
2017-10-02 | 211 | 208
2017-10-02 00:30 | 206 | 203
2017-10-02 01:00 | 201 | 198
2017-10-02 01:30 | 197 | 193
2017-10-02 02:00 | 193 | 189
2017-10-02 02:30 | 190 | 187
2017-10-02 03:00 | 189 | 186
2017-10-02 03:30 | 188 | 184
2017-10-02 04:00 | 189 | 185
2017-10-02 04:30 | 187 | 183
2017-10-02 05:00 | 190 | 187
2017-10-02 05:30 | 193 | 190
2017-10-02 06:00 | 195 | 192
2017-10-02 06:30 | 197 | 194
2017-10-02 07:00 | 201 | 198
2017-10-02 07:30 | 208 | 206
2017-10-02 08:00 | 217 | 214
2017-10-02 08:30 | 223 | 220
2017-10-02 09:00 | 223 | 220
2017-10-02 09:30 | 228 | 225
2017-10-02 10:00 | 213 | 210
2017-10-02 10:30 | 200 | 197
2017-10-02 11:00 | 197 | 194
2017-10-02 11:30 | 200 | 197
2017-10-02 12:00 | 199 | 196
2017-10-02 12:30 | 199 | 196
2017-10-02 13:00 | 197 | 194
2017-10-02 13:30 | 217 | 214
2017-10-02 14:00 | 228 | 226
2017-10-02 14:30 | 227 | 224
2017-10-02 15:00 | 231 | 228
2017-10-02 15:30 | 230 | 228
2017-10-02 16:00 | 238 | 236
2017-10-02 16:30 | 248 | 246
2017-10-02 17:00 | 256 | 254
2017-10-02 17:30 | 263 | 261
2017-10-02 18:00 | 285 | 284
2017-10-02 18:30 | 298 | 296
2017-10-02 19:00 | 311 | 309
2017-10-02 19:30 | 301 | 299
2017-10-02 20:00 | 282 | 280
2017-10-02 20:30 | 270 | 268
2017-10-02 21:00 | 264 | 261
2017-10-02 21:30 | 259 | 256
2017-10-02 22:00 | 247 | 244
2017-10-02 22:30 | 233 | 231
2017-10-02 23:00 | 222 | 219
2017-10-02 23:30 | 214 | 211
2017-10-03 | 214 | 212
2017-10-03 00:30 | 210 | 207
2017-10-03 01:00 | 205 | 201
2017-10-03 01:30 | 199 | 195
2017-10-03 02:00 | 195 | 192
2017-10-03 02:30 | 195 | 192
2017-10-03 03:00 | 194 | 190
2017-10-03 03:30 | 184 | 181
2017-10-03 04:00 | 182 | 180
2017-10-03 04:30 | 188 | 185
2017-10-03 05:00 | 188 | 185
2017-10-03 05:30 | 194 | 191
2017-10-03 06:00 | 200 | 197
2017-10-03 06:30 | 217 | 215
2017-10-03 07:00 | 235 | 232
2017-10-03 07:30 | 255 | 253
2017-10-03 08:00 | 267 | 265
2017-10-03 08:30 | 266 | 264
2017-10-03 09:00 | 263 | 261
2017-10-03 09:30 | 262 | 260
2017-10-03 10:00 | 244 | 242
2017-10-03 10:30 | 235 | 232
2017-10-03 11:00 | 228 | 226
2017-10-03 11:30 | 228 | 226
2017-10-03 12:00 | 224 | 221
2017-10-03 12:30 | 225 | 223
2017-10-03 13:00 | 224 | 221
2017-10-03 13:30 | 241 | 239
2017-10-03 14:00 | 253 | 251
2017-10-03 14:30 | 265 | 263
2017-10-03 15:00 | 268 | 266
2017-10-03 15:30 | 233 | 230
2017-10-03 16:00 | 226 | 224
2017-10-03 16:30 | 216 | 214
2017-10-03 17:00 | 222 | 220
2017-10-03 17:30 | 210 | 207
2017-10-03 18:00 | 224 | 221
2017-10-03 18:30 | 239 | 236
2017-10-03 19:00 | 272 | 270
2017-10-03 19:30 | 278 | 276
2017-10-03 20:00 | 266 | 264
2017-10-03 20:30 | 236 | 234
2017-10-03 21:00 | 244 | 241
2017-10-03 21:30 | 270 | 268
2017-10-03 22:00 | 261 | 258
2017-10-03 22:30 | 248 | 245
2017-10-03 23:00 | 236 | 233
2017-10-03 23:30 | 226 | 223
2017-10-04 | 217 | 214
2017-10-04 00:30 | 210 | 207
2017-10-04 01:00 | 208 | 205
2017-10-04 01:30 | 205 | 202
2017-10-04 02:00 | 201 | 198
2017-10-04 02:30 | 200 | 197
2017-10-04 03:00 | 200 | 197
2017-10-04 03:30 | 196 | 193
2017-10-04 04:00 | 199 | 196
2017-10-04 04:30 | 197 | 194
2017-10-04 05:00 | 197 | 194
2017-10-04 05:30 | 208 | 206
2017-10-04 06:00 | 216 | 214
2017-10-04 06:30 | 229 | 227
2017-10-04 07:00 | 241 | 240
2017-10-04 07:30 | 260 | 258
2017-10-04 08:00 | 262 | 259
2017-10-04 08:30 | 280 | 278
2017-10-04 09:00 | 276 | 274
2017-10-04 09:30 | 267 | 264
2017-10-04 10:00 | 254 | 251
2017-10-04 10:30 | 242 | 239
2017-10-04 11:00 | 232 | 230
2017-10-04 11:30 | 246 | 243
2017-10-04 12:00 | 243 | 241
2017-10-04 12:30 | 241 | 238
2017-10-04 13:00 | 244 | 241
2017-10-04 13:30 | 260 | 258
2017-10-04 14:00 | 273 | 271
2017-10-04 14:30 | 277 | 273
2017-10-04 15:00 | 287 | 283
2017-10-04 15:30 | 285 | 281
2017-10-04 16:00 | 291 | 287
2017-10-04 16:30 | 296 | 292
2017-10-04 17:00 | 291 | 287
2017-10-04 17:30 | 309 | 305
2017-10-04 18:00 | 311 | 308
2017-10-04 18:30 | 320 | 317
2017-10-04 19:00 | 331 | 328
2017-10-04 19:30 | 336 | 333
2017-10-04 20:00 | 325 | 321
2017-10-04 20:30 | 313 | 310
2017-10-04 21:00 | 301 | 297
2017-10-04 21:30 | 288 | 284
2017-10-04 22:00 | 276 | 272
2017-10-04 22:30 | 260 | 256
2017-10-04 23:00 | 251 | 247
2017-10-04 23:30 | 236 | 233
2017-10-05 | 227 | 223
2017-10-05 00:30 | 221 | 217
2017-10-05 01:00 | 214 | 210
2017-10-05 01:30 | 208 | 204
2017-10-05 02:00 | 207 | 203
2017-10-05 02:30 | 207 | 204
2017-10-05 03:00 | 203 | 200
2017-10-05 03:30 | 201 | 197
2017-10-05 04:00 | 209 | 206
2017-10-05 04:30 | 209 | 205
2017-10-05 05:00 | 208 | 205
2017-10-05 05:30 | 217 | 214
2017-10-05 06:00 | 226 | 223
2017-10-05 06:30 | 240 | 238
2017-10-05 07:00 | 261 | 259
2017-10-05 07:30 | 278 | 276
2017-10-05 08:00 | 286 | 284
2017-10-05 08:30 | 292 | 290
2017-10-05 09:00 | 298 | 296
2017-10-05 09:30 | 298 | 297
2017-10-05 10:00 | 286 | 283
2017-10-05 10:30 | 274 | 272
2017-10-05 11:00 | 272 | 270
2017-10-05 11:30 | 270 | 268
2017-10-05 12:00 | 270 | 268
2017-10-05 12:30 | 272 | 270
2017-10-05 13:00 | 273 | 271
2017-10-05 13:30 | 282 | 279
2017-10-05 14:00 | 298 | 296
2017-10-05 14:30 | 304 | 301
2017-10-05 15:00 | 304 | 302
2017-10-05 15:30 | 294 | 292
2017-10-05 16:00 | 301 | 299
2017-10-05 16:30 | 305 | 303
2017-10-05 17:00 | 296 | 293
2017-10-05 17:30 | 273 | 271
2017-10-05 18:00 | 295 | 293
2017-10-05 18:30 | 280 | 277
2017-10-05 19:00 | 298 | 296
2017-10-05 19:30 | 346 | 344
2017-10-05 20:00 | 341 | 338
2017-10-05 20:30 | 326 | 323
2017-10-05 21:00 | 314 | 311
2017-10-05 21:30 | 301 | 299
2017-10-05 22:00 | 284 | 282
2017-10-05 22:30 | 270 | 267
2017-10-05 23:00 | 258 | 256
2017-10-05 23:30 | 246 | 243
2017-10-06 | 236 | 233
2017-10-06 00:30 | 230 | 228
2017-10-06 01:00 | 221 | 218
2017-10-06 01:30 | 210 | 208
2017-10-06 02:00 | 208 | 205
2017-10-06 02:30 | 204 | 201
2017-10-06 03:00 | 201 | 198
2017-10-06 03:30 | 200 | 197
2017-10-06 04:00 | 200 | 197
2017-10-06 04:30 | 202 | 199
2017-10-06 05:00 | 204 | 201
2017-10-06 05:30 | 212 | 210
2017-10-06 06:00 | 225 | 223
2017-10-06 06:30 | 239 | 236
2017-10-06 07:00 | 251 | 249
2017-10-06 07:30 | 268 | 266
2017-10-06 08:00 | 280 | 278
2017-10-06 08:30 | 282 | 279
2017-10-06 09:00 | 281 | 279
2017-10-06 09:30 | 279 | 277
2017-10-06 10:00 | 270 | 268
2017-10-06 10:30 | 259 | 257
2017-10-06 11:00 | 251 | 249
2017-10-06 11:30 | 249 | 247
2017-10-06 12:00 | 251 | 249
2017-10-06 12:30 | 252 | 249
2017-10-06 13:00 | 252 | 250
2017-10-06 13:30 | 258 | 256
2017-10-06 14:00 | 270 | 268
2017-10-06 14:30 | 276 | 274
2017-10-06 15:00 | 267 | 264
2017-10-06 15:30 | 249 | 247
2017-10-06 16:00 | 246 | 243
2017-10-06 16:30 | 223 | 222
2017-10-06 17:00 | 248 | 246
2017-10-06 17:30 | 241 | 239
2017-10-06 18:00 | 259 | 257
2017-10-06 18:30 | 260 | 258
2017-10-06 19:00 | 249 | 246
2017-10-06 19:30 | 257 | 255
2017-10-06 20:00 | 261 | 258
2017-10-06 20:30 | 264 | 261
2017-10-06 21:00 | 251 | 249
2017-10-06 21:30 | 240 | 237
2017-10-06 22:00 | 239 | 236
2017-10-06 22:30 | 247 | 245
2017-10-06 23:00 | 246 | 244
2017-10-06 23:30 | 233 | 231
2017-10-07 | 221 | 219
2017-10-07 00:30 | 214 | 212
2017-10-07 01:00 | 206 | 204
2017-10-07 01:30 | 199 | 197
2017-10-07 02:00 | 195 | 193
2017-10-07 02:30 | 197 | 194
2017-10-07 03:00 | 195 | 193
2017-10-07 03:30 | 189 | 187
2017-10-07 04:00 | 186 | 183
2017-10-07 04:30 | 184 | 181
2017-10-07 05:00 | 182 | 180
2017-10-07 05:30 | 186 | 184
2017-10-07 06:00 | 188 | 187
2017-10-07 06:30 | 191 | 190
2017-10-07 07:00 | 196 | 195
2017-10-07 07:30 | 205 | 204
2017-10-07 08:00 | 215 | 214
2017-10-07 08:30 | 225 | 223
2017-10-07 09:00 | 228 | 227
2017-10-07 09:30 | 233 | 232
2017-10-07 10:00 | 225 | 224
2017-10-07 10:30 | 214 | 213
2017-10-07 11:00 | 211 | 209
2017-10-07 11:30 | 207 | 205
2017-10-07 12:00 | 207 | 206
2017-10-07 12:30 | 204 | 203
2017-10-07 13:00 | 207 | 205
2017-10-07 13:30 | 212 | 211
2017-10-07 14:00 | 225 | 224
2017-10-07 14:30 | 230 | 229
2017-10-07 15:00 | 233 | 232
2017-10-07 15:30 | 242 | 241
2017-10-07 16:00 | 252 | 250
2017-10-07 16:30 | 258 | 257
2017-10-07 17:00 | 265 | 264
2017-10-07 17:30 | 271 | 270
2017-10-07 18:00 | 280 | 279
2017-10-07 18:30 | 287 | 286
2017-10-07 19:00 | 294 | 293
2017-10-07 19:30 | 292 | 291
2017-10-07 20:00 | 285 | 284
2017-10-07 20:30 | 271 | 270
2017-10-07 21:00 | 261 | 260
2017-10-07 21:30 | 254 | 253
2017-10-07 22:00 | 248 | 247
2017-10-07 22:30 | 235 | 235
2017-10-07 23:00 | 226 | 225
2017-10-07 23:30 | 219 | 218
2017-10-08 | 210 | 208
2017-10-08 00:30 | 202 | 201
2017-10-08 01:00 | 197 | 195
2017-10-08 01:30 | 190 | 189
2017-10-08 02:00 | 188 | 187
2017-10-08 02:30 | 186 | 185
2017-10-08 03:00 | 185 | 184
2017-10-08 03:30 | 181 | 180
2017-10-08 04:00 | 184 | 182
2017-10-08 04:30 | 181 | 180
2017-10-08 05:00 | 177 | 176
2017-10-08 05:30 | 179 | 178
2017-10-08 06:00 | 181 | 180
2017-10-08 06:30 | 184 | 183
2017-10-08 07:00 | 184 | 183
2017-10-08 07:30 | 190 | 189
2017-10-08 08:00 | 196 | 195
2017-10-08 08:30 | 204 | 203
2017-10-08 09:00 | 213 | 212
2017-10-08 09:30 | 215 | 214
2017-10-08 10:00 | 205 | 204
2017-10-08 10:30 | 201 | 200
2017-10-08 11:00 | 202 | 201
2017-10-08 11:30 | 201 | 200
2017-10-08 12:00 | 199 | 197
2017-10-08 12:30 | 200 | 199
2017-10-08 13:00 | 203 | 202
2017-10-08 13:30 | 213 | 212
2017-10-08 14:00 | 229 | 228
2017-10-08 14:30 | 236 | 234
2017-10-08 15:00 | 241 | 239
2017-10-08 15:30 | 244 | 242
2017-10-08 16:00 | 250 | 249
2017-10-08 16:30 | 258 | 256
2017-10-08 17:00 | 263 | 262
2017-10-08 17:30 | 238 | 237
2017-10-08 18:00 | 229 | 228
2017-10-08 18:30 | 241 | 240
2017-10-08 19:00 | 254 | 252
2017-10-08 19:30 | 276 | 275
2017-10-08 20:00 | 271 | 270
2017-10-08 20:30 | 266 | 265
2017-10-08 21:00 | 269 | 268
2017-10-08 21:30 | 260 | 258
2017-10-08 22:00 | 248 | 246
2017-10-08 22:30 | 236 | 235
2017-10-08 23:00 | 214 | 213
2017-10-08 23:30 | 199 | 197
2017-10-09 | 198 | 196
2017-10-09 00:30 | 201 | 199
2017-10-09 01:00 | 195 | 193
2017-10-09 01:30 | 188 | 186
2017-10-09 02:00 | 185 | 183
2017-10-09 02:30 | 183 | 181
2017-10-09 03:00 | 180 | 178
2017-10-09 03:30 | 179 | 178
2017-10-09 04:00 | 180 | 178
2017-10-09 04:30 | 180 | 178
2017-10-09 05:00 | 182 | 180
2017-10-09 05:30 | 189 | 187
2017-10-09 06:00 | 195 | 194
2017-10-09 06:30 | 211 | 209
2017-10-09 07:00 | 225 | 223
2017-10-09 07:30 | 234 | 233
2017-10-09 08:00 | 222 | 220
2017-10-09 08:30 | 224 | 222
2017-10-09 09:00 | 226 | 224
2017-10-09 09:30 | 221 | 219
2017-10-09 10:00 | 217 | 215
2017-10-09 10:30 | 215 | 214
2017-10-09 11:00 | 213 | 211
2017-10-09 11:30 | 210 | 208
2017-10-09 12:00 | 211 | 209
2017-10-09 12:30 | 212 | 210
2017-10-09 13:00 | 215 | 213
2017-10-09 13:30 | 216 | 214
2017-10-09 14:00 | 224 | 222
2017-10-09 14:30 | 238 | 236
2017-10-09 15:00 | 265 | 263
2017-10-09 15:30 | 259 | 257
2017-10-09 16:00 | 267 | 265
2017-10-09 16:30 | 271 | 270
2017-10-09 17:00 | 252 | 250
2017-10-09 17:30 | 244 | 243
2017-10-09 18:00 | 260 | 258
2017-10-09 18:30 | 263 | 261
2017-10-09 19:00 | 259 | 257
2017-10-09 19:30 | 270 | 268
2017-10-09 20:00 | 269 | 267
2017-10-09 20:30 | 260 | 258
2017-10-09 21:00 | 276 | 274
2017-10-09 21:30 | 272 | 270
2017-10-09 22:00 | 257 | 254
2017-10-09 22:30 | 239 | 237
2017-10-09 23:00 | 223 | 221
2017-10-09 23:30 | 215 | 213
2017-10-10 | 208 | 206
2017-10-10 00:30 | 201 | 199
2017-10-10 01:00 | 197 | 195
2017-10-10 01:30 | 193 | 191
2017-10-10 02:00 | 190 | 188
2017-10-10 02:30 | 187 | 186
2017-10-10 03:00 | 184 | 183
2017-10-10 03:30 | 184 | 183
2017-10-10 04:00 | 180 | 179
2017-10-10 04:30 | 179 | 178
2017-10-10 05:00 | 181 | 180
2017-10-10 05:30 | 185 | 184
2017-10-10 06:00 | 192 | 191
2017-10-10 06:30 | 212 | 211
2017-10-10 07:00 | 228 | 227
2017-10-10 07:30 | 232 | 231
2017-10-10 08:00 | 215 | 214
2017-10-10 08:30 | 216 | 215
2017-10-10 09:00 | 210 | 209
2017-10-10 09:30 | 208 | 207
2017-10-10 10:00 | 207 | 206
2017-10-10 10:30 | 206 | 205
2017-10-10 11:00 | 206 | 205
2017-10-10 11:30 | 200 | 199
2017-10-10 12:00 | 206 | 205
2017-10-10 12:30 | 209 | 208
2017-10-10 13:00 | 197 | 196
2017-10-10 13:30 | 212 | 211
2017-10-10 14:00 | 219 | 218
2017-10-10 14:30 | 232 | 231
2017-10-10 15:00 | 259 | 257
2017-10-10 15:30 | 256 | 255
2017-10-10 16:00 | 228 | 226
2017-10-10 16:30 | 231 | 230
2017-10-10 17:00 | 203 | 201
2017-10-10 17:30 | 173 | 171
2017-10-10 18:00 | 205 | 203
2017-10-10 18:30 | 222 | 221
2017-10-10 19:00 | 215 | 214
2017-10-10 19:30 | 224 | 223
2017-10-10 20:00 | 224 | 222
2017-10-10 20:30 | 217 | 216
2017-10-10 21:00 | 234 | 233
2017-10-10 21:30 | 230 | 229
2017-10-10 22:00 | 219 | 217
2017-10-10 22:30 | 196 | 194
2017-10-10 23:00 | 223 | 221
2017-10-10 23:30 | 217 | 215
2017-10-11 | 209 | 207
2017-10-11 00:30 | 202 | 201
2017-10-11 01:00 | 195 | 194
2017-10-11 01:30 | 191 | 190
2017-10-11 02:00 | 189 | 188
2017-10-11 02:30 | 188 | 187
2017-10-11 03:00 | 185 | 184
2017-10-11 03:30 | 184 | 183
2017-10-11 04:00 | 182 | 181
2017-10-11 04:30 | 181 | 180
2017-10-11 05:00 | 185 | 184
2017-10-11 05:30 | 190 | 189
2017-10-11 06:00 | 199 | 198
2017-10-11 06:30 | 216 | 215
2017-10-11 07:00 | 208 | 207
2017-10-11 07:30 | 193 | 191
2017-10-11 08:00 | 184 | 183
2017-10-11 08:30 | 204 | 203
2017-10-11 09:00 | 210 | 209
2017-10-11 09:30 | 209 | 208
2017-10-11 10:00 | 207 | 206
2017-10-11 10:30 | 205 | 205
2017-10-11 11:00 | 186 | 184
2017-10-11 11:30 | 184 | 183
2017-10-11 12:00 | 206 | 205
2017-10-11 12:30 | 212 | 211
2017-10-11 13:00 | 215 | 214
2017-10-11 13:30 | 217 | 216
2017-10-11 14:00 | 220 | 219
2017-10-11 14:30 | 226 | 224
2017-10-11 15:00 | 261 | 259
2017-10-11 15:30 | 267 | 265
2017-10-11 16:00 | 268 | 266
2017-10-11 16:30 | 282 | 281
2017-10-11 17:00 | 267 | 264
2017-10-11 17:30 | 255 | 252
2017-10-11 18:00 | 259 | 255
2017-10-11 18:30 | 272 | 268
2017-10-11 19:00 | 287 | 285
2017-10-11 19:30 | 302 | 299
2017-10-11 20:00 | 294 | 292
2017-10-11 20:30 | 282 | 280
2017-10-11 21:00 | 284 | 281
2017-10-11 21:30 | 277 | 275
2017-10-11 22:00 | 265 | 262
2017-10-11 22:30 | 249 | 246
2017-10-11 23:00 | 239 | 236
2017-10-11 23:30 | 226 | 224
2017-10-12 | 218 | 215
2017-10-12 00:30 | 213 | 210
2017-10-12 01:00 | 207 | 205
2017-10-12 01:30 | 203 | 201
2017-10-12 02:00 | 200 | 197
2017-10-12 02:30 | 197 | 194
2017-10-12 03:00 | 193 | 191
2017-10-12 03:30 | 191 | 188
2017-10-12 04:00 | 193 | 190
2017-10-12 04:30 | 194 | 191
2017-10-12 05:00 | 195 | 192
2017-10-12 05:30 | 202 | 200
2017-10-12 06:00 | 209 | 206
2017-10-12 06:30 | 222 | 220
2017-10-12 07:00 | 207 | 204
2017-10-12 07:30 | 202 | 199
2017-10-12 08:00 | 185 | 182
2017-10-12 08:30 | 185 | 182
2017-10-12 09:00 | 195 | 191
2017-10-12 09:30 | 199 | 196
2017-10-12 10:00 | 202 | 198
2017-10-12 10:30 | 192 | 189
2017-10-12 11:00 | 189 | 186
2017-10-12 11:30 | 198 | 195
2017-10-12 12:00 | 199 | 196
2017-10-12 12:30 | 211 | 208
2017-10-12 13:00 | 211 | 209
2017-10-12 13:30 | 212 | 210
2017-10-12 14:00 | 204 | 201
2017-10-12 14:30 | 216 | 213
2017-10-12 15:00 | 249 | 247
2017-10-12 15:30 | 251 | 249
2017-10-12 16:00 | 248 | 247
2017-10-12 16:30 | 247 | 245
2017-10-12 17:00 | 257 | 255
2017-10-12 17:30 | 252 | 251
2017-10-12 18:00 | 269 | 268
2017-10-12 18:30 | 287 | 286
2017-10-12 19:00 | 292 | 291
2017-10-12 19:30 | 296 | 294
2017-10-12 20:00 | 300 | 299
2017-10-12 20:30 | 301 | 300
2017-10-12 21:00 | 292 | 291
2017-10-12 21:30 | 277 | 276
2017-10-12 22:00 | 262 | 261
2017-10-12 22:30 | 238 | 236
2017-10-12 23:00 | 233 | 231
2017-10-12 23:30 | 220 | 218
2017-10-13 | 213 | 210
2017-10-13 00:30 | 207 | 205
2017-10-13 01:00 | 201 | 198
2017-10-13 01:30 | 195 | 193
2017-10-13 02:00 | 193 | 190
2017-10-13 02:30 | 189 | 187
2017-10-13 03:00 | 189 | 187
2017-10-13 03:30 | 189 | 187
2017-10-13 04:00 | 189 | 186
2017-10-13 04:30 | 190 | 188
2017-10-13 05:00 | 191 | 189
2017-10-13 05:30 | 196 | 194
2017-10-13 06:00 | 204 | 203
2017-10-13 06:30 | 218 | 217
2017-10-13 07:00 | 229 | 227
2017-10-13 07:30 | 215 | 213
2017-10-13 08:00 | 221 | 220
2017-10-13 08:30 | 224 | 223
2017-10-13 09:00 | 222 | 221
2017-10-13 09:30 | 224 | 222
2017-10-13 10:00 | 219 | 218
2017-10-13 10:30 | 217 | 215
2017-10-13 11:00 | 217 | 215
2017-10-13 11:30 | 218 | 216
2017-10-13 12:00 | 219 | 217
2017-10-13 12:30 | 219 | 217
2017-10-13 13:00 | 219 | 217
2017-10-13 13:30 | 221 | 219
2017-10-13 14:00 | 228 | 226
2017-10-13 14:30 | 254 | 252
2017-10-13 15:00 | 266 | 264
2017-10-13 15:30 | 262 | 261
2017-10-13 16:00 | 252 | 250
2017-10-13 16:30 | 259 | 257
2017-10-13 17:00 | 265 | 263
2017-10-13 17:30 | 267 | 266
2017-10-13 18:00 | 279 | 277
2017-10-13 18:30 | 286 | 284
2017-10-13 19:00 | 275 | 273
2017-10-13 19:30 | 280 | 279
2017-10-13 20:00 | 280 | 279
2017-10-13 20:30 | 270 | 268
2017-10-13 21:00 | 278 | 276
2017-10-13 21:30 | 271 | 269
2017-10-13 22:00 | 262 | 260
2017-10-13 22:30 | 250 | 248
2017-10-13 23:00 | 241 | 239
2017-10-13 23:30 | 229 | 226
2017-10-14 | 217 | 215
2017-10-14 00:30 | 213 | 210
2017-10-14 01:00 | 209 | 206
2017-10-14 01:30 | 200 | 198
2017-10-14 02:00 | 197 | 194
2017-10-14 02:30 | 197 | 194
2017-10-14 03:00 | 191 | 188
2017-10-14 03:30 | 188 | 186
2017-10-14 04:00 | 184 | 182
2017-10-14 04:30 | 185 | 182
2017-10-14 05:00 | 186 | 184
2017-10-14 05:30 | 187 | 185
2017-10-14 06:00 | 186 | 184
2017-10-14 06:30 | 193 | 191
2017-10-14 07:00 | 198 | 196
2017-10-14 07:30 | 208 | 206
2017-10-14 08:00 | 217 | 215
2017-10-14 08:30 | 227 | 225
2017-10-14 09:00 | 238 | 236
2017-10-14 09:30 | 242 | 240
2017-10-14 10:00 | 235 | 233
2017-10-14 10:30 | 224 | 223
2017-10-14 11:00 | 213 | 212
2017-10-14 11:30 | 215 | 214
2017-10-14 12:00 | 208 | 206
2017-10-14 12:30 | 206 | 204
2017-10-14 13:00 | 207 | 206
2017-10-14 13:30 | 213 | 212
2017-10-14 14:00 | 227 | 225
2017-10-14 14:30 | 234 | 233
2017-10-14 15:00 | 240 | 239
2017-10-14 15:30 | 241 | 239
2017-10-14 16:00 | 249 | 247
2017-10-14 16:30 | 259 | 257
2017-10-14 17:00 | 266 | 265
2017-10-14 17:30 | 272 | 270
2017-10-14 18:00 | 279 | 277
2017-10-14 18:30 | 287 | 285
2017-10-14 19:00 | 297 | 296
2017-10-14 19:30 | 296 | 295
2017-10-14 20:00 | 283 | 282
2017-10-14 20:30 | 273 | 272
2017-10-14 21:00 | 269 | 267
2017-10-14 21:30 | 263 | 261
2017-10-14 22:00 | 252 | 250
2017-10-14 22:30 | 244 | 242
2017-10-14 23:00 | 235 | 233
2017-10-14 23:30 | 224 | 222
2017-10-15 | 215 | 212
2017-10-15 00:30 | 207 | 204
2017-10-15 01:00 | 200 | 198
2017-10-15 01:30 | 197 | 195
2017-10-15 02:00 | 195 | 193
2017-10-15 02:30 | 191 | 189
2017-10-15 03:00 | 189 | 186
2017-10-15 03:30 | 188 | 185
2017-10-15 04:00 | 187 | 185
2017-10-15 04:30 | 187 | 184
2017-10-15 05:00 | 186 | 183
2017-10-15 05:30 | 190 | 187
2017-10-15 06:00 | 190 | 187
2017-10-15 06:30 | 189 | 187
2017-10-15 07:00 | 194 | 191
2017-10-15 07:30 | 201 | 199
2017-10-15 08:00 | 210 | 208
2017-10-15 08:30 | 216 | 214
2017-10-15 09:00 | 223 | 221
2017-10-15 09:30 | 229 | 227
2017-10-15 10:00 | 224 | 222
2017-10-15 10:30 | 216 | 214
2017-10-15 11:00 | 215 | 213
2017-10-15 11:30 | 213 | 211
2017-10-15 12:00 | 207 | 205
2017-10-15 12:30 | 205 | 202
2017-10-15 13:00 | 207 | 205
2017-10-15 13:30 | 214 | 212
2017-10-15 14:00 | 234 | 232
2017-10-15 14:30 | 249 | 247
2017-10-15 15:00 | 252 | 249
2017-10-15 15:30 | 255 | 253
2017-10-15 16:00 | 261 | 258
2017-10-15 16:30 | 267 | 265
2017-10-15 17:00 | 271 | 269
2017-10-15 17:30 | 278 | 276
2017-10-15 18:00 | 287 | 285
2017-10-15 18:30 | 296 | 295
2017-10-15 19:00 | 301 | 299
2017-10-15 19:30 | 296 | 294
2017-10-15 20:00 | 286 | 284
2017-10-15 20:30 | 276 | 275
2017-10-15 21:00 | 272 | 270
2017-10-15 21:30 | 262 | 260
2017-10-15 22:00 | 256 | 254
2017-10-15 22:30 | 243 | 241
2017-10-15 23:00 | 231 | 229
2017-10-15 23:30 | 215 | 213
2017-10-16 | 205 | 202
2017-10-16 00:30 | 198 | 196
2017-10-16 01:00 | 192 | 189
2017-10-16 01:30 | 191 | 188
2017-10-16 02:00 | 186 | 183
2017-10-16 02:30 | 184 | 182
2017-10-16 03:00 | 185 | 183
2017-10-16 03:30 | 187 | 185
2017-10-16 04:00 | 182 | 180
2017-10-16 04:30 | 182 | 180
2017-10-16 05:00 | 186 | 184
2017-10-16 05:30 | 190 | 188
2017-10-16 06:00 | 197 | 195
2017-10-16 06:30 | 210 | 208
2017-10-16 07:00 | 221 | 219
2017-10-16 07:30 | 240 | 238
2017-10-16 08:00 | 256 | 254
2017-10-16 08:30 | 267 | 265
2017-10-16 09:00 | 268 | 266
2017-10-16 09:30 | 268 | 266
2017-10-16 10:00 | 256 | 255
2017-10-16 10:30 | 246 | 244
2017-10-16 11:00 | 249 | 247
2017-10-16 11:30 | 250 | 248
2017-10-16 12:00 | 255 | 253
2017-10-16 12:30 | 250 | 248
2017-10-16 13:00 | 255 | 253
2017-10-16 13:30 | 252 | 251
2017-10-16 14:00 | 233 | 232
2017-10-16 14:30 | 217 | 215
2017-10-16 15:00 | 217 | 215
2017-10-16 15:30 | 211 | 209
2017-10-16 16:00 | 209 | 207
2017-10-16 16:30 | 208 | 206
2017-10-16 17:00 | 211 | 209
2017-10-16 17:30 | 213 | 211
2017-10-16 18:00 | 246 | 244
2017-10-16 18:30 | 255 | 253
2017-10-16 19:00 | 260 | 258
2017-10-16 19:30 | 288 | 286
2017-10-16 20:00 | 284 | 283
2017-10-16 20:30 | 272 | 270
2017-10-16 21:00 | 260 | 258
2017-10-16 21:30 | 248 | 246
2017-10-16 22:00 | 239 | 237
2017-10-16 22:30 | 224 | 222
2017-10-16 23:00 | 212 | 210
2017-10-16 23:30 | 202 | 200
2017-10-17 | 195 | 193
2017-10-17 00:30 | 193 | 191
2017-10-17 01:00 | 186 | 185
2017-10-17 01:30 | 184 | 182
2017-10-17 02:00 | 178 | 176
2017-10-17 02:30 | 178 | 176
2017-10-17 03:00 | 176 | 174
2017-10-17 03:30 | 175 | 173
2017-10-17 04:00 | 171 | 169
2017-10-17 04:30 | 177 | 175
2017-10-17 05:00 | 180 | 178
2017-10-17 05:30 | 188 | 186
2017-10-17 06:00 | 196 | 194
2017-10-17 06:30 | 214 | 212
2017-10-17 07:00 | 228 | 227
2017-10-17 07:30 | 246 | 245
2017-10-17 08:00 | 258 | 257
2017-10-17 08:30 | 243 | 242
2017-10-17 09:00 | 208 | 207
2017-10-17 09:30 | 228 | 227
2017-10-17 10:00 | 219 | 218
2017-10-17 10:30 | 205 | 203
2017-10-17 11:00 | 215 | 214
2017-10-17 11:30 | 212 | 211
2017-10-17 12:00 | 203 | 201
2017-10-17 12:30 | 203 | 202
2017-10-17 13:00 | 204 | 202
2017-10-17 13:30 | 211 | 210
2017-10-17 14:00 | 227 | 225
2017-10-17 14:30 | 229 | 227
2017-10-17 15:00 | 213 | 211
2017-10-17 15:30 | 200 | 198
2017-10-17 16:00 | 203 | 201
2017-10-17 16:30 | 205 | 203
2017-10-17 17:00 | 207 | 206
2017-10-17 17:30 | 215 | 214
2017-10-17 18:00 | 234 | 231
2017-10-17 18:30 | 248 | 247
2017-10-17 19:00 | 255 | 253
2017-10-17 19:30 | 247 | 246
2017-10-17 20:00 | 242 | 241
2017-10-17 20:30 | 262 | 261
2017-10-17 21:00 | 267 | 266
2017-10-17 21:30 | 256 | 255
2017-10-17 22:00 | 240 | 238
2017-10-17 22:30 | 226 | 224
2017-10-17 23:00 | 215 | 213
2017-10-17 23:30 | 205 | 202
2017-10-18 | 199 | 197
2017-10-18 00:30 | 196 | 194
2017-10-18 01:00 | 194 | 192
2017-10-18 01:30 | 190 | 188
2017-10-18 02:00 | 185 | 183
2017-10-18 02:30 | 184 | 182
2017-10-18 03:00 | 182 | 180
2017-10-18 03:30 | 182 | 180
2017-10-18 04:00 | 182 | 180
2017-10-18 04:30 | 185 | 183
2017-10-18 05:00 | 187 | 185
2017-10-18 05:30 | 194 | 192
2017-10-18 06:00 | 205 | 203
2017-10-18 06:30 | 222 | 220
2017-10-18 07:00 | 233 | 231
2017-10-18 07:30 | 247 | 245
2017-10-18 08:00 | 260 | 258
2017-10-18 08:30 | 271 | 270
2017-10-18 09:00 | 244 | 242
2017-10-18 09:30 | 229 | 227
2017-10-18 10:00 | 222 | 220
2017-10-18 10:30 | 205 | 203
2017-10-18 11:00 | 187 | 185
2017-10-18 11:30 | 230 | 228
2017-10-18 12:00 | 239 | 238
2017-10-18 12:30 | 242 | 240
2017-10-18 13:00 | 248 | 247
2017-10-18 13:30 | 258 | 256
2017-10-18 14:00 | 272 | 271
2017-10-18 14:30 | 248 | 246
2017-10-18 15:00 | 248 | 246
2017-10-18 15:30 | 227 | 225
2017-10-18 16:00 | 220 | 218
2017-10-18 16:30 | 221 | 219
2017-10-18 17:00 | 227 | 225
2017-10-18 17:30 | 229 | 228
2017-10-18 18:00 | 239 | 237
2017-10-18 18:30 | 252 | 251
2017-10-18 19:00 | 261 | 260
2017-10-18 19:30 | 273 | 272
2017-10-18 20:00 | 297 | 296
2017-10-18 20:30 | 308 | 306
2017-10-18 21:00 | 298 | 297
2017-10-18 21:30 | 287 | 286
2017-10-18 22:00 | 273 | 271
2017-10-18 22:30 | 259 | 257
2017-10-18 23:00 | 252 | 250
2017-10-18 23:30 | 242 | 240
2017-10-19 | 231 | 229
2017-10-19 00:30 | 224 | 222
2017-10-19 01:00 | 218 | 216
2017-10-19 01:30 | 214 | 212
2017-10-19 02:00 | 217 | 215
2017-10-19 02:30 | 219 | 218
2017-10-19 03:00 | 217 | 216
2017-10-19 03:30 | 196 | 194
2017-10-19 04:00 | 180 | 178
2017-10-19 04:30 | 183 | 181
2017-10-19 05:00 | 188 | 186
2017-10-19 05:30 | 192 | 190
2017-10-19 06:00 | 196 | 194
2017-10-19 06:30 | 217 | 215
2017-10-19 07:00 | 225 | 223
2017-10-19 07:30 | 239 | 237
2017-10-19 08:00 | 252 | 250
2017-10-19 08:30 | 239 | 237
2017-10-19 09:00 | 207 | 205
2017-10-19 09:30 | 209 | 208
2017-10-19 10:00 | 194 | 192
2017-10-19 10:30 | 171 | 169
2017-10-19 11:00 | 171 | 169
2017-10-19 11:30 | 170 | 169
2017-10-19 12:00 | 169 | 167
2017-10-19 12:30 | 145 | 142
2017-10-19 13:00 | 123 | 121
2017-10-19 13:30 | 118 | 116
2017-10-19 14:00 | 123 | 120
2017-10-19 14:30 | 124 | 122
2017-10-19 15:00 | 125 | 121
2017-10-19 15:30 | 122 | 115
2017-10-19 16:00 | 129 | 124
2017-10-19 16:30 | 132 | 126
2017-10-19 17:00 | 132 | 128
2017-10-19 17:30 | 130 | 126
2017-10-19 18:00 | 138 | 134
2017-10-19 18:30 | 174 | 170
2017-10-19 19:00 | 158 | 154
2017-10-19 19:30 | 175 | 172
2017-10-19 20:00 | 245 | 243
2017-10-19 20:30 | 275 | 274
2017-10-19 21:00 | 266 | 265
2017-10-19 21:30 | 254 | 252
2017-10-19 22:00 | 243 | 241
2017-10-19 22:30 | 228 | 225
2017-10-19 23:00 | 220 | 216
2017-10-19 23:30 | 211 | 207
2017-10-20 | 203 | 199
2017-10-20 00:30 | 194 | 192
2017-10-20 01:00 | 185 | 184
2017-10-20 01:30 | 180 | 179
2017-10-20 02:00 | 177 | 176
2017-10-20 02:30 | 177 | 176
2017-10-20 03:00 | 177 | 176
2017-10-20 03:30 | 177 | 176
2017-10-20 04:00 | 176 | 175
2017-10-20 04:30 | 180 | 179
2017-10-20 05:00 | 182 | 180
2017-10-20 05:30 | 189 | 188
2017-10-20 06:00 | 201 | 200
2017-10-20 06:30 | 221 | 221
2017-10-20 07:00 | 233 | 233
2017-10-20 07:30 | 251 | 250
2017-10-20 08:00 | 267 | 266
2017-10-20 08:30 | 270 | 268
2017-10-20 09:00 | 238 | 236
2017-10-20 09:30 | 223 | 221
2017-10-20 10:00 | 211 | 209
2017-10-20 10:30 | 197 | 193
2017-10-20 11:00 | 182 | 180
2017-10-20 11:30 | 183 | 182
2017-10-20 12:00 | 185 | 181
2017-10-20 12:30 | 189 | 188
2017-10-20 13:00 | 219 | 218
2017-10-20 13:30 | 235 | 234
2017-10-20 14:00 | 220 | 219
2017-10-20 14:30 | 172 | 170
2017-10-20 15:00 | 152 | 149
2017-10-20 15:30 | 169 | 167
2017-10-20 16:00 | 220 | 218
2017-10-20 16:30 | 266 | 265
2017-10-20 17:00 | 269 | 268
2017-10-20 17:30 | 267 | 265
2017-10-20 18:00 | 271 | 269
2017-10-20 18:30 | 274 | 272
2017-10-20 19:00 | 284 | 283
2017-10-20 19:30 | 282 | 280
2017-10-20 20:00 | 273 | 271
2017-10-20 20:30 | 261 | 259
2017-10-20 21:00 | 256 | 253
2017-10-20 21:30 | 246 | 242
2017-10-20 22:00 | 234 | 231
2017-10-20 22:30 | 223 | 221
2017-10-20 23:00 | 214 | 211
2017-10-20 23:30 | 204 | 201
2017-10-21 | 197 | 195
2017-10-21 00:30 | 188 | 187
2017-10-21 01:00 | 181 | 180
2017-10-21 01:30 | 178 | 177
2017-10-21 02:00 | 175 | 174
2017-10-21 02:30 | 173 | 172
2017-10-21 03:00 | 172 | 171
2017-10-21 03:30 | 170 | 169
2017-10-21 04:00 | 170 | 169
2017-10-21 04:30 | 170 | 169
2017-10-21 05:00 | 171 | 170
2017-10-21 05:30 | 172 | 171
2017-10-21 06:00 | 174 | 173
2017-10-21 06:30 | 182 | 181
2017-10-21 07:00 | 187 | 186
2017-10-21 07:30 | 196 | 196
2017-10-21 08:00 | 209 | 207
2017-10-21 08:30 | 213 | 212
2017-10-21 09:00 | 221 | 219
2017-10-21 09:30 | 222 | 221
2017-10-21 10:00 | 216 | 215
2017-10-21 10:30 | 212 | 211
2017-10-21 11:00 | 211 | 210
2017-10-21 11:30 | 210 | 209
2017-10-21 12:00 | 207 | 205
2017-10-21 12:30 | 203 | 202
2017-10-21 13:00 | 203 | 202
2017-10-21 13:30 | 215 | 214
2017-10-21 14:00 | 229 | 228
2017-10-21 14:30 | 231 | 230
2017-10-21 15:00 | 231 | 230
2017-10-21 15:30 | 235 | 235
2017-10-21 16:00 | 251 | 250
2017-10-21 16:30 | 259 | 258
2017-10-21 17:00 | 264 | 264
2017-10-21 17:30 | 270 | 269
2017-10-21 18:00 | 275 | 275
2017-10-21 18:30 | 283 | 282
2017-10-21 19:00 | 287 | 287
2017-10-21 19:30 | 282 | 282
2017-10-21 20:00 | 273 | 272
2017-10-21 20:30 | 265 | 265
2017-10-21 21:00 | 256 | 256
2017-10-21 21:30 | 259 | 258
2017-10-21 22:00 | 260 | 259
2017-10-21 22:30 | 250 | 249
2017-10-21 23:00 | 243 | 242
2017-10-21 23:30 | 236 | 234
2017-10-22 | 228 | 226
2017-10-22 00:30 | 224 | 221
2017-10-22 01:00 | 219 | 216
2017-10-22 01:30 | 214 | 212
2017-10-22 02:00 | 208 | 207
2017-10-22 02:30 | 206 | 205
2017-10-22 03:00 | 207 | 205
2017-10-22 03:30 | 204 | 203
2017-10-22 04:00 | 203 | 202
2017-10-22 04:30 | 202 | 201
2017-10-22 05:00 | 201 | 199
2017-10-22 05:30 | 202 | 201
2017-10-22 06:00 | 203 | 202
2017-10-22 06:30 | 208 | 207
2017-10-22 07:00 | 214 | 212
2017-10-22 07:30 | 219 | 218
2017-10-22 08:00 | 227 | 226
2017-10-22 08:30 | 236 | 235
2017-10-22 09:00 | 238 | 237
2017-10-22 09:30 | 243 | 242
2017-10-22 10:00 | 232 | 232
2017-10-22 10:30 | 226 | 226
2017-10-22 11:00 | 231 | 231
2017-10-22 11:30 | 234 | 234
2017-10-22 12:00 | 234 | 234
2017-10-22 12:30 | 234 | 233
2017-10-22 13:00 | 232 | 232
2017-10-22 13:30 | 239 | 239
2017-10-22 14:00 | 249 | 249
2017-10-22 14:30 | 246 | 246
2017-10-22 15:00 | 250 | 249
2017-10-22 15:30 | 254 | 253
2017-10-22 16:00 | 258 | 258
2017-10-22 16:30 | 265 | 264
2017-10-22 17:00 | 273 | 272
2017-10-22 17:30 | 280 | 279
2017-10-22 18:00 | 285 | 285
2017-10-22 18:30 | 287 | 287
2017-10-22 19:00 | 297 | 296
2017-10-22 19:30 | 294 | 294
2017-10-22 20:00 | 285 | 284
2017-10-22 20:30 | 271 | 271
2017-10-22 21:00 | 267 | 267
2017-10-22 21:30 | 249 | 249
2017-10-22 22:00 | 227 | 226
2017-10-22 22:30 | 214 | 213
2017-10-22 23:00 | 204 | 203
2017-10-22 23:30 | 195 | 194
2017-10-23 | 186 | 185
2017-10-23 00:30 | 209 | 208
2017-10-23 01:00 | 214 | 213
2017-10-23 01:30 | 211 | 210
2017-10-23 02:00 | 207 | 206
2017-10-23 02:30 | 204 | 204
2017-10-23 03:00 | 203 | 202
2017-10-23 03:30 | 203 | 202
2017-10-23 04:00 | 203 | 202
2017-10-23 04:30 | 204 | 203
2017-10-23 05:00 | 207 | 206
2017-10-23 05:30 | 215 | 214
2017-10-23 06:00 | 223 | 222
2017-10-23 06:30 | 241 | 240
2017-10-23 07:00 | 257 | 256
2017-10-23 07:30 | 274 | 273
2017-10-23 08:00 | 280 | 280
2017-10-23 08:30 | 276 | 276
2017-10-23 09:00 | 265 | 264
2017-10-23 09:30 | 256 | 255
2017-10-23 10:00 | 247 | 245
2017-10-23 10:30 | 240 | 239
2017-10-23 11:00 | 238 | 236
2017-10-23 11:30 | 238 | 237
2017-10-23 12:00 | 239 | 237
2017-10-23 12:30 | 242 | 241
2017-10-23 13:00 | 247 | 246
2017-10-23 13:30 | 256 | 255
2017-10-23 14:00 | 268 | 267
2017-10-23 14:30 | 269 | 268
2017-10-23 15:00 | 276 | 275
2017-10-23 15:30 | 282 | 281
2017-10-23 16:00 | 288 | 286
2017-10-23 16:30 | 294 | 293
2017-10-23 17:00 | 302 | 301
2017-10-23 17:30 | 297 | 295
2017-10-23 18:00 | 288 | 287
2017-10-23 18:30 | 294 | 293
2017-10-23 19:00 | 309 | 308
2017-10-23 19:30 | 309 | 307
2017-10-23 20:00 | 297 | 296
2017-10-23 20:30 | 283 | 282
2017-10-23 21:00 | 301 | 299
2017-10-23 21:30 | 295 | 293
2017-10-23 22:00 | 282 | 280
2017-10-23 22:30 | 265 | 264
2017-10-23 23:00 | 253 | 252
2017-10-23 23:30 | 242 | 241
2017-10-24 | 235 | 234
2017-10-24 00:30 | 228 | 227
2017-10-24 01:00 | 223 | 222
2017-10-24 01:30 | 217 | 216
2017-10-24 02:00 | 213 | 212
2017-10-24 02:30 | 212 | 211
2017-10-24 03:00 | 211 | 210
2017-10-24 03:30 | 210 | 209
2017-10-24 04:00 | 208 | 208
2017-10-24 04:30 | 212 | 211
2017-10-24 05:00 | 214 | 213
2017-10-24 05:30 | 222 | 221
2017-10-24 06:00 | 236 | 235
2017-10-24 06:30 | 256 | 255
2017-10-24 07:00 | 272 | 271
2017-10-24 07:30 | 289 | 288
2017-10-24 08:00 | 295 | 294
2017-10-24 08:30 | 298 | 296
2017-10-24 09:00 | 296 | 295
2017-10-24 09:30 | 295 | 294
2017-10-24 10:00 | 278 | 276
2017-10-24 10:30 | 267 | 264
2017-10-24 11:00 | 262 | 260
2017-10-24 11:30 | 263 | 260
2017-10-24 12:00 | 265 | 263
2017-10-24 12:30 | 267 | 265
2017-10-24 13:00 | 269 | 267
2017-10-24 13:30 | 277 | 275
2017-10-24 14:00 | 287 | 285
2017-10-24 14:30 | 289 | 288
2017-10-24 15:00 | 291 | 289
2017-10-24 15:30 | 280 | 278
2017-10-24 16:00 | 282 | 280
2017-10-24 16:30 | 288 | 286
2017-10-24 17:00 | 294 | 292
2017-10-24 17:30 | 297 | 295
2017-10-24 18:00 | 298 | 296
2017-10-24 18:30 | 300 | 298
2017-10-24 19:00 | 308 | 306
2017-10-24 19:30 | 306 | 304
2017-10-24 20:00 | 291 | 289
2017-10-24 20:30 | 277 | 274
2017-10-24 21:00 | 265 | 263
2017-10-24 21:30 | 255 | 253
2017-10-24 22:00 | 241 | 238
2017-10-24 22:30 | 239 | 237
2017-10-24 23:00 | 245 | 243
2017-10-24 23:30 | 240 | 238
2017-10-25 | 232 | 229
2017-10-25 00:30 | 225 | 222
2017-10-25 01:00 | 216 | 214
2017-10-25 01:30 | 211 | 209
2017-10-25 02:00 | 206 | 205
2017-10-25 02:30 | 206 | 205
2017-10-25 03:00 | 204 | 202
2017-10-25 03:30 | 203 | 202
2017-10-25 04:00 | 202 | 201
2017-10-25 04:30 | 202 | 201
2017-10-25 05:00 | 203 | 201
2017-10-25 05:30 | 208 | 207
2017-10-25 06:00 | 214 | 213
2017-10-25 06:30 | 230 | 228
2017-10-25 07:00 | 242 | 240
2017-10-25 07:30 | 257 | 255
2017-10-25 08:00 | 267 | 265
2017-10-25 08:30 | 270 | 269
2017-10-25 09:00 | 266 | 265
2017-10-25 09:30 | 265 | 263
2017-10-25 10:00 | 252 | 251
2017-10-25 10:30 | 242 | 241
2017-10-25 11:00 | 242 | 240
2017-10-25 11:30 | 243 | 241
2017-10-25 12:00 | 246 | 244
2017-10-25 12:30 | 246 | 244
2017-10-25 13:00 | 249 | 247
2017-10-25 13:30 | 257 | 255
2017-10-25 14:00 | 270 | 268
2017-10-25 14:30 | 276 | 274
2017-10-25 15:00 | 282 | 280
2017-10-25 15:30 | 286 | 284
2017-10-25 16:00 | 292 | 291
2017-10-25 16:30 | 300 | 298
2017-10-25 17:00 | 304 | 303
2017-10-25 17:30 | 294 | 292
2017-10-25 18:00 | 295 | 293
2017-10-25 18:30 | 300 | 298
2017-10-25 19:00 | 312 | 310
2017-10-25 19:30 | 313 | 311
2017-10-25 20:00 | 302 | 300
2017-10-25 20:30 | 289 | 287
2017-10-25 21:00 | 291 | 289
2017-10-25 21:30 | 280 | 278
2017-10-25 22:00 | 271 | 269
2017-10-25 22:30 | 259 | 257
2017-10-25 23:00 | 247 | 245
2017-10-25 23:30 | 236 | 234
2017-10-26 | 228 | 225
2017-10-26 00:30 | 218 | 216
2017-10-26 01:00 | 207 | 206
2017-10-26 01:30 | 202 | 200
2017-10-26 02:00 | 200 | 198
2017-10-26 02:30 | 195 | 193
2017-10-26 03:00 | 195 | 193
2017-10-26 03:30 | 195 | 194
2017-10-26 04:00 | 194 | 192
2017-10-26 04:30 | 195 | 194
2017-10-26 05:00 | 199 | 198
2017-10-26 05:30 | 205 | 203
2017-10-26 06:00 | 212 | 211
2017-10-26 06:30 | 232 | 230
2017-10-26 07:00 | 243 | 242
2017-10-26 07:30 | 255 | 254
2017-10-26 08:00 | 259 | 258
2017-10-26 08:30 | 258 | 257
2017-10-26 09:00 | 254 | 252
2017-10-26 09:30 | 256 | 254
2017-10-26 10:00 | 243 | 241
2017-10-26 10:30 | 235 | 233
2017-10-26 11:00 | 238 | 236
2017-10-26 11:30 | 240 | 238
2017-10-26 12:00 | 245 | 243
2017-10-26 12:30 | 237 | 235
2017-10-26 13:00 | 246 | 244
2017-10-26 13:30 | 233 | 231
2017-10-26 14:00 | 195 | 193
2017-10-26 14:30 | 196 | 194
2017-10-26 15:00 | 201 | 199
2017-10-26 15:30 | 211 | 209
2017-10-26 16:00 | 215 | 214
2017-10-26 16:30 | 223 | 222
2017-10-26 17:00 | 239 | 238
2017-10-26 17:30 | 244 | 243
2017-10-26 18:00 | 251 | 249
2017-10-26 18:30 | 257 | 256
2017-10-26 19:00 | 240 | 238
2017-10-26 19:30 | 210 | 207
2017-10-26 20:00 | 197 | 195
2017-10-26 20:30 | 185 | 182
2017-10-26 21:00 | 207 | 204
2017-10-26 21:30 | 216 | 213
2017-10-26 22:00 | 206 | 203
2017-10-26 22:30 | 192 | 189
2017-10-26 23:00 | 202 | 199
2017-10-26 23:30 | 237 | 234
2017-10-27 | 230 | 228
2017-10-27 00:30 | 220 | 219
2017-10-27 01:00 | 214 | 212
2017-10-27 01:30 | 210 | 208
2017-10-27 02:00 | 206 | 205
2017-10-27 02:30 | 206 | 204
2017-10-27 03:00 | 203 | 201
2017-10-27 03:30 | 203 | 201
2017-10-27 04:00 | 202 | 199
2017-10-27 04:30 | 200 | 197
2017-10-27 05:00 | 198 | 196
2017-10-27 05:30 | 204 | 202
2017-10-27 06:00 | 206 | 204
2017-10-27 06:30 | 221 | 219
2017-10-27 07:00 | 237 | 235
2017-10-27 07:30 | 247 | 245
2017-10-27 08:00 | 252 | 251
2017-10-27 08:30 | 250 | 249
2017-10-27 09:00 | 247 | 245
2017-10-27 09:30 | 245 | 244
2017-10-27 10:00 | 233 | 232
2017-10-27 10:30 | 226 | 224
2017-10-27 11:00 | 227 | 226
2017-10-27 11:30 | 229 | 228
2017-10-27 12:00 | 232 | 230
2017-10-27 12:30 | 235 | 233
2017-10-27 13:00 | 237 | 235
2017-10-27 13:30 | 246 | 244
2017-10-27 14:00 | 256 | 254
2017-10-27 14:30 | 261 | 259
2017-10-27 15:00 | 265 | 263
2017-10-27 15:30 | 259 | 257
2017-10-27 16:00 | 267 | 264
2017-10-27 16:30 | 276 | 274
2017-10-27 17:00 | 284 | 282
2017-10-27 17:30 | 285 | 283
2017-10-27 18:00 | 297 | 295
2017-10-27 18:30 | 302 | 300
2017-10-27 19:00 | 311 | 309
2017-10-27 19:30 | 307 | 305
2017-10-27 20:00 | 289 | 286
2017-10-27 20:30 | 279 | 276
2017-10-27 21:00 | 268 | 265
2017-10-27 21:30 | 261 | 258
2017-10-27 22:00 | 250 | 247
2017-10-27 22:30 | 238 | 235
2017-10-27 23:00 | 225 | 222
2017-10-27 23:30 | 216 | 213
2017-10-28 | 217 | 215
2017-10-28 00:30 | 215 | 212
2017-10-28 01:00 | 208 | 205
2017-10-28 01:30 | 204 | 201
2017-10-28 02:00 | 199 | 195
2017-10-28 02:30 | 197 | 194
2017-10-28 03:00 | 195 | 192
2017-10-28 03:30 | 194 | 192
2017-10-28 04:00 | 194 | 191
2017-10-28 04:30 | 193 | 190
2017-10-28 05:00 | 193 | 190
2017-10-28 05:30 | 194 | 191
2017-10-28 06:00 | 195 | 192
2017-10-28 06:30 | 199 | 196
2017-10-28 07:00 | 205 | 203
2017-10-28 07:30 | 213 | 211
2017-10-28 08:00 | 217 | 215
2017-10-28 08:30 | 224 | 222
2017-10-28 09:00 | 228 | 225
2017-10-28 09:30 | 228 | 226
2017-10-28 10:00 | 217 | 215
2017-10-28 10:30 | 210 | 207
2017-10-28 11:00 | 209 | 207
2017-10-28 11:30 | 212 | 210
2017-10-28 12:00 | 214 | 213
2017-10-28 12:30 | 217 | 215
2017-10-28 13:00 | 219 | 217
2017-10-28 13:30 | 230 | 228
2017-10-28 14:00 | 230 | 228
2017-10-28 14:30 | 235 | 233
2017-10-28 15:00 | 240 | 239
2017-10-28 15:30 | 247 | 246
2017-10-28 16:00 | 258 | 256
2017-10-28 16:30 | 267 | 265
2017-10-28 17:00 | 278 | 276
2017-10-28 17:30 | 286 | 284
2017-10-28 18:00 | 290 | 288
2017-10-28 18:30 | 292 | 289
2017-10-28 19:00 | 301 | 299
2017-10-28 19:30 | 310 | 308
2017-10-28 20:00 | 304 | 301
2017-10-28 20:30 | 296 | 293
2017-10-28 21:00 | 287 | 284
2017-10-28 21:30 | 276 | 273
2017-10-28 22:00 | 268 | 265
2017-10-28 22:30 | 256 | 253
2017-10-28 23:00 | 248 | 246
2017-10-28 23:30 | 240 | 238
2017-10-29 | 235 | 233
2017-10-29 00:30 | 228 | 225
2017-10-29 01:00 | 219 | 217
2017-10-29 01:30 | 213 | 211
2017-10-29 02:00 | 209 | 207
2017-10-29 02:30 | 206 | 203
2017-10-29 03:00 | 204 | 202
2017-10-29 03:30 | 201 | 198
2017-10-29 04:00 | 201 | 198
2017-10-29 04:30 | 201 | 198
2017-10-29 05:00 | 200 | 197
2017-10-29 05:30 | 201 | 198
2017-10-29 06:00 | 200 | 197
2017-10-29 06:30 | 203 | 200
2017-10-29 07:00 | 206 | 204
2017-10-29 07:30 | 213 | 210
2017-10-29 08:00 | 219 | 217
2017-10-29 08:30 | 224 | 222
2017-10-29 09:00 | 233 | 231
2017-10-29 09:30 | 238 | 237
2017-10-29 10:00 | 229 | 227
2017-10-29 10:30 | 223 | 221
2017-10-29 11:00 | 225 | 223
2017-10-29 11:30 | 228 | 226
2017-10-29 12:00 | 231 | 229
2017-10-29 12:30 | 231 | 229
2017-10-29 13:00 | 233 | 232
2017-10-29 13:30 | 242 | 240
2017-10-29 14:00 | 256 | 255
2017-10-29 14:30 | 263 | 261
2017-10-29 15:00 | 271 | 269
2017-10-29 15:30 | 275 | 273
2017-10-29 16:00 | 286 | 284
2017-10-29 16:30 | 293 | 290
2017-10-29 17:00 | 303 | 301
2017-10-29 17:30 | 314 | 312
2017-10-29 18:00 | 318 | 316
2017-10-29 18:30 | 319 | 317
2017-10-29 19:00 | 329 | 328
2017-10-29 19:30 | 331 | 330
2017-10-29 20:00 | 318 | 316
2017-10-29 20:30 | 312 | 311
2017-10-29 21:00 | 303 | 301
2017-10-29 21:30 | 293 | 292
2017-10-29 22:00 | 281 | 280
2017-10-29 22:30 | 267 | 266
2017-10-29 23:00 | 255 | 253
2017-10-29 23:30 | 243 | 241
2017-10-30 | 233 | 231
2017-10-30 00:30 | 227 | 225
2017-10-30 01:00 | 220 | 219
2017-10-30 01:30 | 217 | 215
2017-10-30 02:00 | 214 | 212
2017-10-30 02:30 | 211 | 209
2017-10-30 03:00 | 209 | 207
2017-10-30 03:30 | 208 | 206
2017-10-30 04:00 | 207 | 205
2017-10-30 04:30 | 207 | 205
2017-10-30 05:00 | 211 | 209
2017-10-30 05:30 | 215 | 213
2017-10-30 06:00 | 223 | 221
2017-10-30 06:30 | 241 | 240
2017-10-30 07:00 | 254 | 252
2017-10-30 07:30 | 272 | 270
2017-10-30 08:00 | 280 | 278
2017-10-30 08:30 | 282 | 280
2017-10-30 09:00 | 285 | 283
2017-10-30 09:30 | 289 | 287
2017-10-30 10:00 | 275 | 272
2017-10-30 10:30 | 266 | 264
2017-10-30 11:00 | 275 | 273
2017-10-30 11:30 | 279 | 276
2017-10-30 12:00 | 285 | 283
2017-10-30 12:30 | 291 | 288
2017-10-30 13:00 | 293 | 291
2017-10-30 13:30 | 306 | 304
2017-10-30 14:00 | 313 | 310
2017-10-30 14:30 | 316 | 313
2017-10-30 15:00 | 319 | 317
2017-10-30 15:30 | 312 | 309
2017-10-30 16:00 | 314 | 311
2017-10-30 16:30 | 311 | 309
2017-10-30 17:00 | 305 | 303
2017-10-30 17:30 | 303 | 300
2017-10-30 18:00 | 320 | 317
2017-10-30 18:30 | 331 | 328
2017-10-30 19:00 | 339 | 336
2017-10-30 19:30 | 333 | 331
2017-10-30 20:00 | 321 | 319
2017-10-30 20:30 | 305 | 302
2017-10-30 21:00 | 299 | 296
2017-10-30 21:30 | 298 | 296
2017-10-30 22:00 | 287 | 285
2017-10-30 22:30 | 275 | 272
2017-10-30 23:00 | 254 | 251
2017-10-30 23:30 | 241 | 238
2017-10-31 | 232 | 229
2017-10-31 00:30 | 226 | 223
2017-10-31 01:00 | 217 | 215
2017-10-31 01:30 | 214 | 212
2017-10-31 02:00 | 214 | 212
2017-10-31 02:30 | 213 | 211
2017-10-31 03:00 | 210 | 207
2017-10-31 03:30 | 208 | 205
2017-10-31 04:00 | 206 | 204
2017-10-31 04:30 | 209 | 207
2017-10-31 05:00 | 211 | 209
2017-10-31 05:30 | 220 | 217
2017-10-31 06:00 | 225 | 223
2017-10-31 06:30 | 242 | 240
2017-10-31 07:00 | 257 | 255
2017-10-31 07:30 | 275 | 273
2017-10-31 08:00 | 281 | 279
2017-10-31 08:30 | 288 | 286
2017-10-31 09:00 | 292 | 290
2017-10-31 09:30 | 291 | 290
2017-10-31 10:00 | 290 | 288
2017-10-31 10:30 | 293 | 291
2017-10-31 11:00 | 296 | 294
2017-10-31 11:30 | 298 | 297
2017-10-31 12:00 | 304 | 302
2017-10-31 12:30 | 304 | 301
2017-10-31 13:00 | 303 | 300
2017-10-31 13:30 | 307 | 304
2017-10-31 14:00 | 313 | 310
2017-10-31 14:30 | 318 | 316
2017-10-31 15:00 | 321 | 319
2017-10-31 15:30 | 317 | 315
2017-10-31 16:00 | 318 | 316
2017-10-31 16:30 | 321 | 319
2017-10-31 17:00 | 323 | 321
2017-10-31 17:30 | 325 | 323
2017-10-31 18:00 | 324 | 322
2017-10-31 18:30 | 325 | 323
2017-10-31 19:00 | 333 | 331
2017-10-31 19:30 | 337 | 336
2017-10-31 20:00 | 333 | 331
2017-10-31 20:30 | 339 | 337
2017-10-31 21:00 | 329 | 327
2017-10-31 21:30 | 325 | 322
2017-10-31 22:00 | 311 | 308
2017-10-31 22:30 | 297 | 294
2017-10-31 23:00 | 283 | 280
2017-10-31 23:30 | 272 | 270
2017-11-01 | 262 | 260
2017-11-01 00:30 | 255 | 253
2017-11-01 01:00 | 244 | 242
2017-11-01 01:30 | 238 | 235
2017-11-01 02:00 | 231 | 228
2017-11-01 02:30 | 230 | 227
2017-11-01 03:00 | 226 | 223
2017-11-01 03:30 | 225 | 222
2017-11-01 04:00 | 226 | 223
2017-11-01 04:30 | 227 | 224
2017-11-01 05:00 | 228 | 225
2017-11-01 05:30 | 233 | 230
2017-11-01 06:00 | 238 | 236
2017-11-01 06:30 | 259 | 257
2017-11-01 07:00 | 272 | 270
2017-11-01 07:30 | 286 | 284
2017-11-01 08:00 | 294 | 292
2017-11-01 08:30 | 304 | 302
2017-11-01 09:00 | 305 | 303
2017-11-01 09:30 | 305 | 303
2017-11-01 10:00 | 303 | 301
2017-11-01 10:30 | 299 | 297
2017-11-01 11:00 | 293 | 291
2017-11-01 11:30 | 291 | 289
2017-11-01 12:00 | 290 | 288
2017-11-01 12:30 | 292 | 290
2017-11-01 13:00 | 297 | 295
2017-11-01 13:30 | 302 | 299
2017-11-01 14:00 | 315 | 313
2017-11-01 14:30 | 316 | 314
2017-11-01 15:00 | 315 | 313
2017-11-01 15:30 | 306 | 304
2017-11-01 16:00 | 308 | 305
2017-11-01 16:30 | 310 | 308
2017-11-01 17:00 | 313 | 311
2017-11-01 17:30 | 315 | 313
2017-11-01 18:00 | 313 | 310
2017-11-01 18:30 | 334 | 332
2017-11-01 19:00 | 344 | 342
2017-11-01 19:30 | 342 | 340
2017-11-01 20:00 | 332 | 330
2017-11-01 20:30 | 323 | 321
2017-11-01 21:00 | 311 | 308
2017-11-01 21:30 | 296 | 293
2017-11-01 22:00 | 283 | 281
2017-11-01 22:30 | 270 | 268
2017-11-01 23:00 | 259 | 256
2017-11-01 23:30 | 246 | 243
2017-11-02 | 235 | 233
2017-11-02 00:30 | 228 | 226
2017-11-02 01:00 | 221 | 219
2017-11-02 01:30 | 219 | 216
2017-11-02 02:00 | 217 | 214
2017-11-02 02:30 | 219 | 216
2017-11-02 03:00 | 216 | 213
2017-11-02 03:30 | 215 | 212
2017-11-02 04:00 | 213 | 210
2017-11-02 04:30 | 211 | 207
2017-11-02 05:00 | 211 | 208
2017-11-02 05:30 | 217 | 214
2017-11-02 06:00 | 225 | 222
2017-11-02 06:30 | 242 | 239
2017-11-02 07:00 | 255 | 253
2017-11-02 07:30 | 274 | 272
2017-11-02 08:00 | 283 | 281
2017-11-02 08:30 | 286 | 284
2017-11-02 09:00 | 292 | 290
2017-11-02 09:30 | 292 | 290
2017-11-02 10:00 | 290 | 288
2017-11-02 10:30 | 289 | 287
2017-11-02 11:00 | 289 | 287
2017-11-02 11:30 | 285 | 283
2017-11-02 12:00 | 284 | 282
2017-11-02 12:30 | 291 | 289
2017-11-02 13:00 | 292 | 290
2017-11-02 13:30 | 293 | 290
2017-11-02 14:00 | 297 | 295
2017-11-02 14:30 | 305 | 302
2017-11-02 15:00 | 307 | 305
2017-11-02 15:30 | 301 | 299
2017-11-02 16:00 | 302 | 300
2017-11-02 16:30 | 308 | 305
2017-11-02 17:00 | 310 | 307
2017-11-02 17:30 | 309 | 307
2017-11-02 18:00 | 326 | 324
2017-11-02 18:30 | 333 | 331
2017-11-02 19:00 | 344 | 342
2017-11-02 19:30 | 347 | 345
2017-11-02 20:00 | 336 | 334
2017-11-02 20:30 | 325 | 323
2017-11-02 21:00 | 317 | 315
2017-11-02 21:30 | 299 | 296
2017-11-02 22:00 | 283 | 281
2017-11-02 22:30 | 265 | 262
2017-11-02 23:00 | 253 | 250
2017-11-02 23:30 | 242 | 239
2017-11-03 | 233 | 230
2017-11-03 00:30 | 227 | 223
2017-11-03 01:00 | 217 | 214
2017-11-03 01:30 | 211 | 208
2017-11-03 02:00 | 207 | 204
2017-11-03 02:30 | 207 | 203
2017-11-03 03:00 | 206 | 203
2017-11-03 03:30 | 205 | 202
2017-11-03 04:00 | 203 | 199
2017-11-03 04:30 | 203 | 199
2017-11-03 05:00 | 208 | 204
2017-11-03 05:30 | 211 | 208
2017-11-03 06:00 | 221 | 218
2017-11-03 06:30 | 241 | 239
2017-11-03 07:00 | 258 | 256
2017-11-03 07:30 | 273 | 271
2017-11-03 08:00 | 281 | 278
2017-11-03 08:30 | 285 | 282
2017-11-03 09:00 | 285 | 282
2017-11-03 09:30 | 287 | 284
2017-11-03 10:00 | 282 | 279
2017-11-03 10:30 | 280 | 277
2017-11-03 11:00 | 279 | 276
2017-11-03 11:30 | 282 | 280
2017-11-03 12:00 | 283 | 281
2017-11-03 12:30 | 284 | 281
2017-11-03 13:00 | 283 | 280
2017-11-03 13:30 | 283 | 281
2017-11-03 14:00 | 287 | 284
2017-11-03 14:30 | 293 | 290
2017-11-03 15:00 | 295 | 293
2017-11-03 15:30 | 286 | 284
2017-11-03 16:00 | 290 | 287
2017-11-03 16:30 | 297 | 294
2017-11-03 17:00 | 301 | 299
2017-11-03 17:30 | 301 | 298
2017-11-03 18:00 | 311 | 308
2017-11-03 18:30 | 314 | 312
2017-11-03 19:00 | 323 | 321
2017-11-03 19:30 | 322 | 320
2017-11-03 20:00 | 318 | 316
2017-11-03 20:30 | 309 | 306
2017-11-03 21:00 | 296 | 293
2017-11-03 21:30 | 288 | 285
2017-11-03 22:00 | 278 | 275
2017-11-03 22:30 | 264 | 262
2017-11-03 23:00 | 252 | 250
2017-11-03 23:30 | 243 | 240
2017-11-04 | 232 | 229
2017-11-04 00:30 | 225 | 221
2017-11-04 01:00 | 216 | 213
2017-11-04 01:30 | 208 | 205
2017-11-04 02:00 | 203 | 200
2017-11-04 02:30 | 202 | 199
2017-11-04 03:00 | 202 | 199
2017-11-04 03:30 | 199 | 196
2017-11-04 04:00 | 199 | 196
2017-11-04 04:30 | 199 | 196
2017-11-04 05:00 | 204 | 201
2017-11-04 05:30 | 207 | 205
2017-11-04 06:00 | 208 | 204
2017-11-04 06:30 | 212 | 209
2017-11-04 07:00 | 216 | 213
2017-11-04 07:30 | 226 | 223
2017-11-04 08:00 | 232 | 230
2017-11-04 08:30 | 242 | 239
2017-11-04 09:00 | 247 | 245
2017-11-04 09:30 | 251 | 249
2017-11-04 10:00 | 249 | 247
2017-11-04 10:30 | 248 | 246
2017-11-04 11:00 | 248 | 246
2017-11-04 11:30 | 246 | 244
2017-11-04 12:00 | 248 | 245
2017-11-04 12:30 | 241 | 239
2017-11-04 13:00 | 185 | 183
2017-11-04 13:30 | 177 | 175
2017-11-04 14:00 | 223 | 221
2017-11-04 14:30 | 250 | 248
2017-11-04 15:00 | 258 | 256
2017-11-04 15:30 | 266 | 264
2017-11-04 16:00 | 272 | 271
2017-11-04 16:30 | 278 | 276
2017-11-04 17:00 | 287 | 285
2017-11-04 17:30 | 294 | 292
2017-11-04 18:00 | 296 | 294
2017-11-04 18:30 | 291 | 289
2017-11-04 19:00 | 297 | 295
2017-11-04 19:30 | 300 | 297
2017-11-04 20:00 | 293 | 291
2017-11-04 20:30 | 280 | 277
2017-11-04 21:00 | 269 | 266
2017-11-04 21:30 | 272 | 269
2017-11-04 22:00 | 266 | 263
2017-11-04 22:30 | 254 | 251
2017-11-04 23:00 | 244 | 241
2017-11-04 23:30 | 235 | 233
2017-11-05 | 225 | 223
2017-11-05 00:30 | 219 | 217
2017-11-05 01:00 | 209 | 209
2017-11-05 01:30 | 202 | 202
2017-11-05 02:00 | 198 | 198
2017-11-05 02:30 | 198 | 197
2017-11-05 03:00 | 194 | 193
2017-11-05 03:30 | 190 | 190
2017-11-05 04:00 | 188 | 187
2017-11-05 04:30 | 188 | 188
2017-11-05 05:00 | 190 | 189
2017-11-05 05:30 | 194 | 193
2017-11-05 06:00 | 197 | 196
2017-11-05 06:30 | 200 | 199
2017-11-05 07:00 | 201 | 200
2017-11-05 07:30 | 206 | 205
2017-11-05 08:00 | 212 | 212
2017-11-05 08:30 | 217 | 217
2017-11-05 09:00 | 220 | 220
2017-11-05 09:30 | 225 | 224
2017-11-05 10:00 | 228 | 228
2017-11-05 10:30 | 231 | 231
2017-11-05 11:00 | 230 | 229
2017-11-05 11:30 | 230 | 230
2017-11-05 12:00 | 232 | 232
2017-11-05 12:30 | 234 | 233
2017-11-05 13:00 | 232 | 231
2017-11-05 13:30 | 236 | 235
2017-11-05 14:00 | 240 | 240
2017-11-05 14:30 | 246 | 245
2017-11-05 15:00 | 249 | 248
2017-11-05 15:30 | 253 | 253
2017-11-05 16:00 | 265 | 264
2017-11-05 16:30 | 275 | 275
2017-11-05 17:00 | 286 | 285
2017-11-05 17:30 | 297 | 296
2017-11-05 18:00 | 292 | 291
2017-11-05 18:30 | 291 | 291
2017-11-05 19:00 | 303 | 302
2017-11-05 19:30 | 308 | 307
2017-11-05 20:00 | 296 | 296
2017-11-05 20:30 | 296 | 296
2017-11-05 21:00 | 291 | 290
2017-11-05 21:30 | 280 | 279
2017-11-05 22:00 | 267 | 267
2017-11-05 22:30 | 254 | 253
2017-11-05 23:00 | 239 | 238
2017-11-05 23:30 | 229 | 229
2017-11-06 | 220 | 219
2017-11-06 00:30 | 212 | 211
2017-11-06 01:00 | 205 | 205
2017-11-06 01:30 | 203 | 202
2017-11-06 02:00 | 198 | 197
2017-11-06 02:30 | 198 | 197
2017-11-06 03:00 | 195 | 194
2017-11-06 03:30 | 198 | 197
2017-11-06 04:00 | 197 | 197
2017-11-06 04:30 | 198 | 197
2017-11-06 05:00 | 199 | 199
2017-11-06 05:30 | 207 | 206
2017-11-06 06:00 | 213 | 212
2017-11-06 06:30 | 229 | 229
2017-11-06 07:00 | 246 | 245
2017-11-06 07:30 | 260 | 259
2017-11-06 08:00 | 266 | 265
2017-11-06 08:30 | 273 | 271
2017-11-06 09:00 | 274 | 272
2017-11-06 09:30 | 274 | 273
2017-11-06 10:00 | 269 | 268
2017-11-06 10:30 | 267 | 266
2017-11-06 11:00 | 265 | 264
2017-11-06 11:30 | 264 | 263
2017-11-06 12:00 | 265 | 264
2017-11-06 12:30 | 266 | 264
2017-11-06 13:00 | 268 | 267
2017-11-06 13:30 | 270 | 269
2017-11-06 14:00 | 276 | 275
2017-11-06 14:30 | 282 | 280
2017-11-06 15:00 | 286 | 285
2017-11-06 15:30 | 281 | 280
2017-11-06 16:00 | 283 | 282
2017-11-06 16:30 | 289 | 287
2017-11-06 17:00 | 298 | 297
2017-11-06 17:30 | 298 | 297
2017-11-06 18:00 | 313 | 311
2017-11-06 18:30 | 322 | 321
2017-11-06 19:00 | 335 | 334
2017-11-06 19:30 | 336 | 334
2017-11-06 20:00 | 325 | 324
2017-11-06 20:30 | 314 | 312
2017-11-06 21:00 | 302 | 300
2017-11-06 21:30 | 290 | 289
2017-11-06 22:00 | 274 | 273
2017-11-06 22:30 | 258 | 256
2017-11-06 23:00 | 245 | 243
2017-11-06 23:30 | 235 | 233
2017-11-07 | 227 | 225
2017-11-07 00:30 | 222 | 220
2017-11-07 01:00 | 214 | 212
2017-11-07 01:30 | 209 | 207
2017-11-07 02:00 | 202 | 200
2017-11-07 02:30 | 199 | 198
2017-11-07 03:00 | 195 | 194
2017-11-07 03:30 | 197 | 196
2017-11-07 04:00 | 197 | 195
2017-11-07 04:30 | 198 | 196
2017-11-07 05:00 | 198 | 197
2017-11-07 05:30 | 205 | 203
2017-11-07 06:00 | 212 | 211
2017-11-07 06:30 | 229 | 228
2017-11-07 07:00 | 245 | 243
2017-11-07 07:30 | 258 | 257
2017-11-07 08:00 | 266 | 265
2017-11-07 08:30 | 271 | 269
2017-11-07 09:00 | 269 | 267
2017-11-07 09:30 | 270 | 268
2017-11-07 10:00 | 267 | 266
2017-11-07 10:30 | 269 | 267
2017-11-07 11:00 | 269 | 267
2017-11-07 11:30 | 277 | 276
2017-11-07 12:00 | 284 | 283
2017-11-07 12:30 | 285 | 283
2017-11-07 13:00 | 285 | 283
2017-11-07 13:30 | 285 | 283
2017-11-07 14:00 | 290 | 288
2017-11-07 14:30 | 298 | 296
2017-11-07 15:00 | 303 | 301
2017-11-07 15:30 | 295 | 293
2017-11-07 16:00 | 303 | 301
2017-11-07 16:30 | 311 | 309
2017-11-07 17:00 | 318 | 317
2017-11-07 17:30 | 321 | 320
2017-11-07 18:00 | 329 | 327
2017-11-07 18:30 | 333 | 332
2017-11-07 19:00 | 346 | 345
2017-11-07 19:30 | 347 | 346
2017-11-07 20:00 | 336 | 335
2017-11-07 20:30 | 326 | 324
2017-11-07 21:00 | 314 | 312
2017-11-07 21:30 | 297 | 295
2017-11-07 22:00 | 280 | 278
2017-11-07 22:30 | 266 | 264
2017-11-07 23:00 | 253 | 251
2017-11-07 23:30 | 243 | 241
2017-11-08 | 232 | 230
2017-11-08 00:30 | 226 | 224
2017-11-08 01:00 | 220 | 218
2017-11-08 01:30 | 213 | 211
2017-11-08 02:00 | 212 | 210
2017-11-08 02:30 | 209 | 207
2017-11-08 03:00 | 208 | 206
2017-11-08 03:30 | 207 | 205
2017-11-08 04:00 | 207 | 205
2017-11-08 04:30 | 207 | 205
2017-11-08 05:00 | 207 | 205
2017-11-08 05:30 | 212 | 210
2017-11-08 06:00 | 221 | 219
2017-11-08 06:30 | 239 | 237
2017-11-08 07:00 | 250 | 248
2017-11-08 07:30 | 264 | 262
2017-11-08 08:00 | 275 | 274
2017-11-08 08:30 | 281 | 280
2017-11-08 09:00 | 281 | 280
2017-11-08 09:30 | 281 | 279
2017-11-08 10:00 | 282 | 281
2017-11-08 10:30 | 283 | 282
2017-11-08 11:00 | 281 | 280
2017-11-08 11:30 | 282 | 280
2017-11-08 12:00 | 288 | 286
2017-11-08 12:30 | 296 | 294
2017-11-08 13:00 | 298 | 297
2017-11-08 13:30 | 299 | 297
2017-11-08 14:00 | 303 | 301
2017-11-08 14:30 | 310 | 309
2017-11-08 15:00 | 317 | 316
2017-11-08 15:30 | 318 | 317
2017-11-08 16:00 | 326 | 324
2017-11-08 16:30 | 336 | 335
2017-11-08 17:00 | 340 | 339
2017-11-08 17:30 | 338 | 337
2017-11-08 18:00 | 338 | 336
2017-11-08 18:30 | 340 | 338
2017-11-08 19:00 | 349 | 348
2017-11-08 19:30 | 350 | 348
2017-11-08 20:00 | 344 | 343
2017-11-08 20:30 | 332 | 331
2017-11-08 21:00 | 324 | 323
2017-11-08 21:30 | 311 | 309
2017-11-08 22:00 | 290 | 288
2017-11-08 22:30 | 275 | 274
2017-11-08 23:00 | 262 | 261
2017-11-08 23:30 | 249 | 247
2017-11-09 | 240 | 239
2017-11-09 00:30 | 233 | 231
2017-11-09 01:00 | 226 | 225
2017-11-09 01:30 | 222 | 220
2017-11-09 02:00 | 218 | 217
2017-11-09 02:30 | 217 | 215
2017-11-09 03:00 | 216 | 214
2017-11-09 03:30 | 214 | 212
2017-11-09 04:00 | 213 | 212
2017-11-09 04:30 | 215 | 213
2017-11-09 05:00 | 216 | 214
2017-11-09 05:30 | 221 | 219
2017-11-09 06:00 | 228 | 226
2017-11-09 06:30 | 244 | 242
2017-11-09 07:00 | 260 | 259
2017-11-09 07:30 | 277 | 276
2017-11-09 08:00 | 288 | 287
2017-11-09 08:30 | 292 | 290
2017-11-09 09:00 | 294 | 292
2017-11-09 09:30 | 292 | 291
2017-11-09 10:00 | 289 | 288
2017-11-09 10:30 | 289 | 288
2017-11-09 11:00 | 278 | 276
2017-11-09 11:30 | 283 | 281
2017-11-09 12:00 | 294 | 293
2017-11-09 12:30 | 297 | 296
2017-11-09 13:00 | 294 | 292
2017-11-09 13:30 | 295 | 294
2017-11-09 14:00 | 303 | 301
2017-11-09 14:30 | 303 | 302
2017-11-09 15:00 | 303 | 302
2017-11-09 15:30 | 296 | 294
2017-11-09 16:00 | 295 | 293
2017-11-09 16:30 | 287 | 285
2017-11-09 17:00 | 254 | 252
2017-11-09 17:30 | 248 | 246
2017-11-09 18:00 | 253 | 251
2017-11-09 18:30 | 260 | 258
2017-11-09 19:00 | 240 | 239
2017-11-09 19:30 | 228 | 226
2017-11-09 20:00 | 217 | 215
2017-11-09 20:30 | 216 | 215
2017-11-09 21:00 | 211 | 210
2017-11-09 21:30 | 196 | 195
2017-11-09 22:00 | 184 | 182
2017-11-09 22:30 | 169 | 168
2017-11-09 23:00 | 162 | 161
2017-11-09 23:30 | 152 | 150
2017-11-10 | 177 | 176
2017-11-10 00:30 | 208 | 207
2017-11-10 01:00 | 207 | 206
2017-11-10 01:30 | 204 | 202
2017-11-10 02:00 | 201 | 200
2017-11-10 02:30 | 196 | 195
2017-11-10 03:00 | 194 | 193
2017-11-10 03:30 | 190 | 189
2017-11-10 04:00 | 190 | 190
2017-11-10 04:30 | 190 | 189
2017-11-10 05:00 | 190 | 190
2017-11-10 05:30 | 197 | 196
2017-11-10 06:00 | 204 | 203
2017-11-10 06:30 | 221 | 220
2017-11-10 07:00 | 235 | 234
2017-11-10 07:30 | 237 | 236
2017-11-10 08:00 | 208 | 207
2017-11-10 08:30 | 198 | 197
2017-11-10 09:00 | 196 | 195
2017-11-10 09:30 | 194 | 193
2017-11-10 10:00 | 174 | 172
2017-11-10 10:30 | 158 | 156
2017-11-10 11:00 | 150 | 149
2017-11-10 11:30 | 148 | 146
2017-11-10 12:00 | 162 | 160
2017-11-10 12:30 | 156 | 155
2017-11-10 13:00 | 132 | 131
2017-11-10 13:30 | 134 | 133
2017-11-10 14:00 | 149 | 148
2017-11-10 14:30 | 155 | 154
2017-11-10 15:00 | 151 | 150
2017-11-10 15:30 | 139 | 138
2017-11-10 16:00 | 140 | 138
2017-11-10 16:30 | 143 | 141
2017-11-10 17:00 | 144 | 143
2017-11-10 17:30 | 144 | 143
2017-11-10 18:00 | 157 | 156
2017-11-10 18:30 | 167 | 166
2017-11-10 19:00 | 174 | 173
2017-11-10 19:30 | 174 | 173
2017-11-10 20:00 | 163 | 162
2017-11-10 20:30 | 144 | 143
2017-11-10 21:00 | 124 | 123
2017-11-10 21:30 | 119 | 117
2017-11-10 22:00 | 118 | 116
2017-11-10 22:30 | 116 | 114
2017-11-10 23:00 | 107 | 106
2017-11-10 23:30 | 98 | 97
2017-11-11 | 87 | 86
2017-11-11 00:30 | 114 | 113
2017-11-11 01:00 | 122 | 121
2017-11-11 01:30 | 117 | 116
2017-11-11 02:00 | 116 | 114
2017-11-11 02:30 | 112 | 110
2017-11-11 03:00 | 110 | 109
2017-11-11 03:30 | 109 | 108
2017-11-11 04:00 | 107 | 105
2017-11-11 04:30 | 109 | 107
2017-11-11 05:00 | 109 | 108
2017-11-11 05:30 | 113 | 111
2017-11-11 06:00 | 113 | 112
2017-11-11 06:30 | 118 | 117
2017-11-11 07:00 | 118 | 116
2017-11-11 07:30 | 118 | 117
2017-11-11 08:00 | 122 | 120
2017-11-11 08:30 | 132 | 131
2017-11-11 09:00 | 133 | 132
2017-11-11 09:30 | 136 | 135
2017-11-11 10:00 | 132 | 130
2017-11-11 10:30 | 136 | 135
2017-11-11 11:00 | 137 | 135
2017-11-11 11:30 | 131 | 130
2017-11-11 12:00 | 135 | 134
2017-11-11 12:30 | 138 | 136
2017-11-11 13:00 | 137 | 136
2017-11-11 13:30 | 142 | 141
2017-11-11 14:00 | 138 | 137
2017-11-11 14:30 | 139 | 138
2017-11-11 15:00 | 148 | 147
2017-11-11 15:30 | 150 | 149
2017-11-11 16:00 | 133 | 132
2017-11-11 16:30 | 136 | 135
2017-11-11 17:00 | 145 | 144
2017-11-11 17:30 | 147 | 146
2017-11-11 18:00 | 147 | 146
2017-11-11 18:30 | 154 | 153
2017-11-11 19:00 | 162 | 161
2017-11-11 19:30 | 184 | 183
2017-11-11 20:00 | 219 | 218
2017-11-11 20:30 | 234 | 233
2017-11-11 21:00 | 231 | 230
2017-11-11 21:30 | 225 | 224
2017-11-11 22:00 | 224 | 222
2017-11-11 22:30 | 214 | 212
2017-11-11 23:00 | 216 | 215
2017-11-11 23:30 | 209 | 207
2017-11-12 | 201 | 199
2017-11-12 00:30 | 193 | 191
2017-11-12 01:00 | 191 | 189
2017-11-12 01:30 | 190 | 188
2017-11-12 02:00 | 184 | 182
2017-11-12 02:30 | 183 | 181
2017-11-12 03:00 | 178 | 177
2017-11-12 03:30 | 177 | 176
2017-11-12 04:00 | 176 | 175
2017-11-12 04:30 | 176 | 174
2017-11-12 05:00 | 175 | 173
2017-11-12 05:30 | 177 | 175
2017-11-12 06:00 | 175 | 173
2017-11-12 06:30 | 175 | 173
2017-11-12 07:00 | 173 | 171
2017-11-12 07:30 | 167 | 165
2017-11-12 08:00 | 172 | 170
2017-11-12 08:30 | 176 | 175
2017-11-12 09:00 | 182 | 181
2017-11-12 09:30 | 196 | 195
2017-11-12 10:00 | 192 | 191
2017-11-12 10:30 | 186 | 185
2017-11-12 11:00 | 187 | 186
2017-11-12 11:30 | 189 | 189
2017-11-12 12:00 | 189 | 188
2017-11-12 12:30 | 182 | 181
2017-11-12 13:00 | 190 | 189
2017-11-12 13:30 | 194 | 193
2017-11-12 14:00 | 191 | 190
2017-11-12 14:30 | 197 | 196
2017-11-12 15:00 | 202 | 201
2017-11-12 15:30 | 195 | 193
2017-11-12 16:00 | 194 | 193
2017-11-12 16:30 | 201 | 199
2017-11-12 17:00 | 205 | 204
2017-11-12 17:30 | 214 | 213
2017-11-12 18:00 | 236 | 235
2017-11-12 18:30 | 244 | 243
2017-11-12 19:00 | 259 | 258
2017-11-12 19:30 | 260 | 259
2017-11-12 20:00 | 252 | 251
2017-11-12 20:30 | 248 | 248
2017-11-12 21:00 | 242 | 241
2017-11-12 21:30 | 234 | 233
2017-11-12 22:00 | 228 | 226
2017-11-12 22:30 | 221 | 220
2017-11-12 23:00 | 222 | 221
2017-11-12 23:30 | 210 | 209
2017-11-13 | 202 | 200
2017-11-13 00:30 | 199 | 197
2017-11-13 01:00 | 187 | 185
2017-11-13 01:30 | 177 | 176
2017-11-13 02:00 | 174 | 172
2017-11-13 02:30 | 173 | 172
2017-11-13 03:00 | 170 | 169
2017-11-13 03:30 | 169 | 168
2017-11-13 04:00 | 168 | 167
2017-11-13 04:30 | 170 | 169
2017-11-13 05:00 | 172 | 171
2017-11-13 05:30 | 177 | 176
2017-11-13 06:00 | 186 | 185
2017-11-13 06:30 | 202 | 201
2017-11-13 07:00 | 211 | 210
2017-11-13 07:30 | 217 | 216
2017-11-13 08:00 | 220 | 219
2017-11-13 08:30 | 225 | 224
2017-11-13 09:00 | 225 | 224
2017-11-13 09:30 | 223 | 222
2017-11-13 10:00 | 224 | 222
2017-11-13 10:30 | 226 | 225
2017-11-13 11:00 | 224 | 222
2017-11-13 11:30 | 221 | 220
2017-11-13 12:00 | 226 | 225
2017-11-13 12:30 | 228 | 227
2017-11-13 13:00 | 228 | 226
2017-11-13 13:30 | 230 | 229
2017-11-13 14:00 | 238 | 237
2017-11-13 14:30 | 242 | 241
2017-11-13 15:00 | 216 | 214
2017-11-13 15:30 | 198 | 196
2017-11-13 16:00 | 160 | 158
2017-11-13 16:30 | 159 | 157
2017-11-13 17:00 | 160 | 159
2017-11-13 17:30 | 169 | 166
2017-11-13 18:00 | 181 | 178
2017-11-13 18:30 | 191 | 189
2017-11-13 19:00 | 200 | 198
2017-11-13 19:30 | 196 | 194
2017-11-13 20:00 | 184 | 182
2017-11-13 20:30 | 180 | 178
2017-11-13 21:00 | 174 | 172
2017-11-13 21:30 | 165 | 163
2017-11-13 22:00 | 160 | 158
2017-11-13 22:30 | 150 | 148
2017-11-13 23:00 | 147 | 145
2017-11-13 23:30 | 137 | 135
2017-11-14 | 129 | 127
2017-11-14 00:30 | 182 | 180
2017-11-14 01:00 | 200 | 199
2017-11-14 01:30 | 194 | 193
2017-11-14 02:00 | 186 | 184
2017-11-14 02:30 | 182 | 181
2017-11-14 03:00 | 178 | 177
2017-11-14 03:30 | 178 | 176
2017-11-14 04:00 | 178 | 176
2017-11-14 04:30 | 182 | 181
2017-11-14 05:00 | 181 | 179
2017-11-14 05:30 | 188 | 187
2017-11-14 06:00 | 174 | 171
2017-11-14 06:30 | 164 | 161
2017-11-14 07:00 | 171 | 169
2017-11-14 07:30 | 179 | 177
2017-11-14 08:00 | 187 | 186
2017-11-14 08:30 | 200 | 199
2017-11-14 09:00 | 198 | 197
2017-11-14 09:30 | 199 | 198
2017-11-14 10:00 | 192 | 191
2017-11-14 10:30 | 193 | 192
2017-11-14 11:00 | 196 | 195
2017-11-14 11:30 | 176 | 175
2017-11-14 12:00 | 159 | 158
2017-11-14 12:30 | 160 | 159
2017-11-14 13:00 | 156 | 155
2017-11-14 13:30 | 157 | 155
2017-11-14 14:00 | 165 | 163
2017-11-14 14:30 | 157 | 156
2017-11-14 15:00 | 143 | 141
2017-11-14 15:30 | 136 | 135
2017-11-14 16:00 | 129 | 128
2017-11-14 16:30 | 133 | 132
2017-11-14 17:00 | 131 | 130
2017-11-14 17:30 | 132 | 131
2017-11-14 18:00 | 146 | 144
2017-11-14 18:30 | 150 | 149
2017-11-14 19:00 | 160 | 159
2017-11-14 19:30 | 161 | 160
2017-11-14 20:00 | 168 | 167
2017-11-14 20:30 | 179 | 178
2017-11-14 21:00 | 175 | 174
2017-11-14 21:30 | 168 | 167
2017-11-14 22:00 | 163 | 162
2017-11-14 22:30 | 151 | 150
2017-11-14 23:00 | 150 | 149
2017-11-14 23:30 | 141 | 140
2017-11-15 | 133 | 132
2017-11-15 00:30 | 131 | 130
2017-11-15 01:00 | 107 | 105
2017-11-15 01:30 | 118 | 116
2017-11-15 02:00 | 116 | 114
2017-11-15 02:30 | 114 | 113
2017-11-15 03:00 | 112 | 110
2017-11-15 03:30 | 117 | 115
2017-11-15 04:00 | 117 | 116
2017-11-15 04:30 | 114 | 113
2017-11-15 05:00 | 122 | 121
2017-11-15 05:30 | 128 | 126
2017-11-15 06:00 | 135 | 134
2017-11-15 06:30 | 151 | 150
2017-11-15 07:00 | 160 | 159
2017-11-15 07:30 | 167 | 166
2017-11-15 08:00 | 171 | 170
2017-11-15 08:30 | 175 | 174
2017-11-15 09:00 | 140 | 139
2017-11-15 09:30 | 132 | 131
2017-11-15 10:00 | 129 | 128
2017-11-15 10:30 | 129 | 128
2017-11-15 11:00 | 129 | 128
2017-11-15 11:30 | 139 | 138
2017-11-15 12:00 | 187 | 186
2017-11-15 12:30 | 206 | 205
2017-11-15 13:00 | 215 | 214
2017-11-15 13:30 | 209 | 208
2017-11-15 14:00 | 212 | 211
2017-11-15 14:30 | 213 | 212
2017-11-15 15:00 | 194 | 192
2017-11-15 15:30 | 191 | 189
2017-11-15 16:00 | 197 | 195
2017-11-15 16:30 | 200 | 198
2017-11-15 17:00 | 173 | 171
2017-11-15 17:30 | 160 | 158
2017-11-15 18:00 | 160 | 158
2017-11-15 18:30 | 163 | 161
2017-11-15 19:00 | 204 | 203
2017-11-15 19:30 | 217 | 215
2017-11-15 20:00 | 211 | 209
2017-11-15 20:30 | 210 | 208
2017-11-15 21:00 | 199 | 197
2017-11-15 21:30 | 190 | 188
2017-11-15 22:00 | 183 | 181
2017-11-15 22:30 | 169 | 166
2017-11-15 23:00 | 168 | 166
2017-11-15 23:30 | 158 | 156
2017-11-16 | 146 | 144
2017-11-16 00:30 | 140 | 138
2017-11-16 01:00 | 132 | 131
2017-11-16 01:30 | 127 | 126
2017-11-16 02:00 | 125 | 123
2017-11-16 02:30 | 121 | 120
2017-11-16 03:00 | 119 | 118
2017-11-16 03:30 | 118 | 117
2017-11-16 04:00 | 118 | 117
2017-11-16 04:30 | 121 | 119
2017-11-16 05:00 | 127 | 126
2017-11-16 05:30 | 135 | 134
2017-11-16 06:00 | 140 | 138
2017-11-16 06:30 | 155 | 154
2017-11-16 07:00 | 169 | 167
2017-11-16 07:30 | 179 | 177
2017-11-16 08:00 | 186 | 185
2017-11-16 08:30 | 184 | 183
2017-11-16 09:00 | 182 | 181
2017-11-16 09:30 | 148 | 146
2017-11-16 10:00 | 137 | 136
2017-11-16 10:30 | 136 | 134
2017-11-16 11:00 | 135 | 133
2017-11-16 11:30 | 141 | 140
2017-11-16 12:00 | 141 | 140
2017-11-16 12:30 | 141 | 140
2017-11-16 13:00 | 141 | 139
2017-11-16 13:30 | 144 | 142
2017-11-16 14:00 | 152 | 150
2017-11-16 14:30 | 191 | 190
2017-11-16 15:00 | 201 | 200
2017-11-16 15:30 | 217 | 216
2017-11-16 16:00 | 252 | 251
2017-11-16 16:30 | 257 | 255
2017-11-16 17:00 | 260 | 258
2017-11-16 17:30 | 263 | 261
2017-11-16 18:00 | 264 | 262
2017-11-16 18:30 | 274 | 271
2017-11-16 19:00 | 281 | 278
2017-11-16 19:30 | 282 | 279
2017-11-16 20:00 | 274 | 271
2017-11-16 20:30 | 288 | 285
2017-11-16 21:00 | 281 | 279
2017-11-16 21:30 | 269 | 267
2017-11-16 22:00 | 263 | 261
2017-11-16 22:30 | 248 | 246
2017-11-16 23:00 | 241 | 239
2017-11-16 23:30 | 229 | 226
2017-11-17 | 219 | 217
2017-11-17 00:30 | 207 | 205
2017-11-17 01:00 | 200 | 199
2017-11-17 01:30 | 196 | 194
2017-11-17 02:00 | 190 | 189
2017-11-17 02:30 | 188 | 187
2017-11-17 03:00 | 186 | 184
2017-11-17 03:30 | 187 | 185
2017-11-17 04:00 | 187 | 186
2017-11-17 04:30 | 188 | 187
2017-11-17 05:00 | 191 | 189
2017-11-17 05:30 | 195 | 193
2017-11-17 06:00 | 201 | 200
2017-11-17 06:30 | 216 | 215
2017-11-17 07:00 | 224 | 222
2017-11-17 07:30 | 227 | 226
2017-11-17 08:00 | 238 | 236
2017-11-17 08:30 | 241 | 239
2017-11-17 09:00 | 242 | 240
2017-11-17 09:30 | 246 | 244
2017-11-17 10:00 | 246 | 244
2017-11-17 10:30 | 237 | 235
2017-11-17 11:00 | 237 | 235
2017-11-17 11:30 | 236 | 234
2017-11-17 12:00 | 235 | 233
2017-11-17 12:30 | 238 | 237
2017-11-17 13:00 | 245 | 244
2017-11-17 13:30 | 246 | 244
2017-11-17 14:00 | 244 | 243
2017-11-17 14:30 | 250 | 248
2017-11-17 15:00 | 258 | 256
2017-11-17 15:30 | 260 | 258
2017-11-17 16:00 | 257 | 255
2017-11-17 16:30 | 271 | 269
2017-11-17 17:00 | 278 | 277
2017-11-17 17:30 | 275 | 273
2017-11-17 18:00 | 274 | 272
2017-11-17 18:30 | 274 | 272
2017-11-17 19:00 | 281 | 279
2017-11-17 19:30 | 283 | 281
2017-11-17 20:00 | 278 | 276
2017-11-17 20:30 | 277 | 275
2017-11-17 21:00 | 272 | 270
2017-11-17 21:30 | 262 | 260
2017-11-17 22:00 | 258 | 255
2017-11-17 22:30 | 246 | 244
2017-11-17 23:00 | 244 | 241
2017-11-17 23:30 | 236 | 234
2017-11-18 | 227 | 225
2017-11-18 00:30 | 221 | 218
2017-11-18 01:00 | 213 | 210
2017-11-18 01:30 | 207 | 206
2017-11-18 02:00 | 203 | 202
2017-11-18 02:30 | 199 | 198
2017-11-18 03:00 | 191 | 190
2017-11-18 03:30 | 187 | 186
2017-11-18 04:00 | 184 | 183
2017-11-18 04:30 | 183 | 182
2017-11-18 05:00 | 192 | 191
2017-11-18 05:30 | 194 | 193
2017-11-18 06:00 | 196 | 195
2017-11-18 06:30 | 202 | 201
2017-11-18 07:00 | 194 | 193
2017-11-18 07:30 | 187 | 186
2017-11-18 08:00 | 193 | 191
2017-11-18 08:30 | 200 | 199
2017-11-18 09:00 | 203 | 202
2017-11-18 09:30 | 207 | 206
2017-11-18 10:00 | 207 | 206
2017-11-18 10:30 | 210 | 209
2017-11-18 11:00 | 207 | 206
2017-11-18 11:30 | 206 | 205
2017-11-18 12:00 | 211 | 210
2017-11-18 12:30 | 209 | 208
2017-11-18 13:00 | 206 | 205
2017-11-18 13:30 | 207 | 206
2017-11-18 14:00 | 213 | 212
2017-11-18 14:30 | 219 | 218
2017-11-18 15:00 | 220 | 219
2017-11-18 15:30 | 220 | 219
2017-11-18 16:00 | 217 | 216
2017-11-18 16:30 | 230 | 229
2017-11-18 17:00 | 241 | 240
2017-11-18 17:30 | 247 | 246
2017-11-18 18:00 | 253 | 252
2017-11-18 18:30 | 254 | 254
2017-11-18 19:00 | 262 | 261
2017-11-18 19:30 | 268 | 267
2017-11-18 20:00 | 259 | 259
2017-11-18 20:30 | 256 | 256
2017-11-18 21:00 | 253 | 252
2017-11-18 21:30 | 245 | 244
2017-11-18 22:00 | 248 | 247
2017-11-18 22:30 | 238 | 238
2017-11-18 23:00 | 239 | 238
2017-11-18 23:30 | 234 | 233
2017-11-19 | 226 | 225
2017-11-19 00:30 | 220 | 219
2017-11-19 01:00 | 213 | 212
2017-11-19 01:30 | 210 | 209
2017-11-19 02:00 | 205 | 204
2017-11-19 02:30 | 202 | 201
2017-11-19 03:00 | 200 | 199
2017-11-19 03:30 | 200 | 199
2017-11-19 04:00 | 196 | 195
2017-11-19 04:30 | 196 | 195
2017-11-19 05:00 | 196 | 195
2017-11-19 05:30 | 196 | 195
2017-11-19 06:00 | 194 | 192
2017-11-19 06:30 | 195 | 194
2017-11-19 07:00 | 195 | 194
2017-11-19 07:30 | 190 | 189
2017-11-19 08:00 | 193 | 192
2017-11-19 08:30 | 200 | 199
2017-11-19 09:00 | 204 | 203
2017-11-19 09:30 | 206 | 205
2017-11-19 10:00 | 209 | 208
2017-11-19 10:30 | 213 | 212
2017-11-19 11:00 | 210 | 209
2017-11-19 11:30 | 211 | 210
2017-11-19 12:00 | 210 | 209
2017-11-19 12:30 | 208 | 207
2017-11-19 13:00 | 206 | 205
2017-11-19 13:30 | 204 | 203
2017-11-19 14:00 | 206 | 206
2017-11-19 14:30 | 212 | 211
2017-11-19 15:00 | 214 | 214
2017-11-19 15:30 | 224 | 223
2017-11-19 16:00 | 224 | 223
2017-11-19 16:30 | 240 | 239
2017-11-19 17:00 | 248 | 248
2017-11-19 17:30 | 255 | 254
2017-11-19 18:00 | 263 | 263
2017-11-19 18:30 | 272 | 271
2017-11-19 19:00 | 280 | 279
2017-11-19 19:30 | 284 | 284
2017-11-19 20:00 | 277 | 277
2017-11-19 20:30 | 273 | 273
2017-11-19 21:00 | 264 | 264
2017-11-19 21:30 | 255 | 255
2017-11-19 22:00 | 253 | 252
2017-11-19 22:30 | 238 | 237
2017-11-19 23:00 | 236 | 234
2017-11-19 23:30 | 228 | 227
2017-11-20 | 223 | 222
2017-11-20 00:30 | 217 | 217
2017-11-20 01:00 | 211 | 211
2017-11-20 01:30 | 209 | 208
2017-11-20 02:00 | 204 | 204
2017-11-20 02:30 | 200 | 199
2017-11-20 03:00 | 198 | 197
2017-11-20 03:30 | 198 | 197
2017-11-20 04:00 | 198 | 198
2017-11-20 04:30 | 199 | 198
2017-11-20 05:00 | 203 | 202
2017-11-20 05:30 | 210 | 209
2017-11-20 06:00 | 217 | 216
2017-11-20 06:30 | 234 | 233
2017-11-20 07:00 | 241 | 240
2017-11-20 07:30 | 247 | 247
2017-11-20 08:00 | 260 | 259
2017-11-20 08:30 | 259 | 258
2017-11-20 09:00 | 263 | 263
2017-11-20 09:30 | 263 | 263
2017-11-20 10:00 | 265 | 264
2017-11-20 10:30 | 261 | 260
2017-11-20 11:00 | 255 | 254
2017-11-20 11:30 | 253 | 252
2017-11-20 12:00 | 255 | 254
2017-11-20 12:30 | 251 | 250
2017-11-20 13:00 | 254 | 253
2017-11-20 13:30 | 254 | 253
2017-11-20 14:00 | 251 | 250
2017-11-20 14:30 | 259 | 258
2017-11-20 15:00 | 261 | 260
2017-11-20 15:30 | 261 | 260
2017-11-20 16:00 | 259 | 258
2017-11-20 16:30 | 261 | 260
2017-11-20 17:00 | 263 | 262
2017-11-20 17:30 | 263 | 262
2017-11-20 18:00 | 281 | 279
2017-11-20 18:30 | 288 | 286
2017-11-20 19:00 | 299 | 297
2017-11-20 19:30 | 300 | 298
2017-11-20 20:00 | 294 | 292
2017-11-20 20:30 | 281 | 279
2017-11-20 21:00 | 271 | 269
2017-11-20 21:30 | 260 | 258
2017-11-20 22:00 | 255 | 253
2017-11-20 22:30 | 243 | 241
2017-11-20 23:00 | 243 | 241
2017-11-20 23:30 | 237 | 235
2017-11-21 | 224 | 223
2017-11-21 00:30 | 217 | 216
2017-11-21 01:00 | 213 | 212
2017-11-21 01:30 | 209 | 208
2017-11-21 02:00 | 206 | 205
2017-11-21 02:30 | 203 | 202
2017-11-21 03:00 | 202 | 201
2017-11-21 03:30 | 199 | 198
2017-11-21 04:00 | 199 | 198
2017-11-21 04:30 | 203 | 201
2017-11-21 05:00 | 203 | 202
2017-11-21 05:30 | 212 | 211
2017-11-21 06:00 | 217 | 216
2017-11-21 06:30 | 232 | 231
2017-11-21 07:00 | 241 | 240
2017-11-21 07:30 | 258 | 257
2017-11-21 08:00 | 263 | 262
2017-11-21 08:30 | 271 | 270
2017-11-21 09:00 | 272 | 270
2017-11-21 09:30 | 268 | 267
2017-11-21 10:00 | 266 | 264
2017-11-21 10:30 | 265 | 264
2017-11-21 11:00 | 269 | 268
2017-11-21 11:30 | 257 | 255
2017-11-21 12:00 | 255 | 253
2017-11-21 12:30 | 250 | 248
2017-11-21 13:00 | 250 | 248
2017-11-21 13:30 | 254 | 252
2017-11-21 14:00 | 255 | 253
2017-11-21 14:30 | 255 | 254
2017-11-21 15:00 | 255 | 254
2017-11-21 15:30 | 253 | 251
2017-11-21 16:00 | 254 | 252
2017-11-21 16:30 | 258 | 256
2017-11-21 17:00 | 263 | 261
2017-11-21 17:30 | 261 | 259
2017-11-21 18:00 | 275 | 273
2017-11-21 18:30 | 285 | 284
2017-11-21 19:00 | 295 | 294
2017-11-21 19:30 | 290 | 288
2017-11-21 20:00 | 282 | 280
2017-11-21 20:30 | 275 | 273
2017-11-21 21:00 | 265 | 263
2017-11-21 21:30 | 255 | 253
2017-11-21 22:00 | 248 | 246
2017-11-21 22:30 | 240 | 238
2017-11-21 23:00 | 240 | 238
2017-11-21 23:30 | 233 | 231
2017-11-22 | 223 | 221
2017-11-22 00:30 | 216 | 214
2017-11-22 01:00 | 210 | 208
2017-11-22 01:30 | 204 | 202
2017-11-22 02:00 | 203 | 200
2017-11-22 02:30 | 200 | 198
2017-11-22 03:00 | 194 | 192
2017-11-22 03:30 | 194 | 192
2017-11-22 04:00 | 197 | 196
2017-11-22 04:30 | 197 | 195
2017-11-22 05:00 | 200 | 199
2017-11-22 05:30 | 201 | 200
2017-11-22 06:00 | 209 | 208
2017-11-22 06:30 | 220 | 219
2017-11-22 07:00 | 224 | 222
2017-11-22 07:30 | 241 | 240
2017-11-22 08:00 | 245 | 244
2017-11-22 08:30 | 247 | 245
2017-11-22 09:00 | 249 | 247
2017-11-22 09:30 | 251 | 249
2017-11-22 10:00 | 251 | 250
2017-11-22 10:30 | 251 | 249
2017-11-22 11:00 | 246 | 245
2017-11-22 11:30 | 251 | 249
2017-11-22 12:00 | 249 | 247
2017-11-22 12:30 | 247 | 246
2017-11-22 13:00 | 257 | 255
2017-11-22 13:30 | 263 | 261
2017-11-22 14:00 | 272 | 270
2017-11-22 14:30 | 273 | 271
2017-11-22 15:00 | 277 | 275
2017-11-22 15:30 | 275 | 273
2017-11-22 16:00 | 274 | 272
2017-11-22 16:30 | 278 | 276
2017-11-22 17:00 | 284 | 282
2017-11-22 17:30 | 286 | 284
2017-11-22 18:00 | 289 | 287
2017-11-22 18:30 | 294 | 292
2017-11-22 19:00 | 300 | 298
2017-11-22 19:30 | 298 | 296
2017-11-22 20:00 | 292 | 290
2017-11-22 20:30 | 281 | 279
2017-11-22 21:00 | 270 | 268
2017-11-22 21:30 | 261 | 259
2017-11-22 22:00 | 248 | 246
2017-11-22 22:30 | 231 | 229
2017-11-22 23:00 | 220 | 218
2017-11-22 23:30 | 210 | 208
2017-11-23 | 203 | 201
2017-11-23 00:30 | 196 | 194
2017-11-23 01:00 | 198 | 196
2017-11-23 01:30 | 207 | 206
2017-11-23 02:00 | 207 | 205
2017-11-23 02:30 | 205 | 203
2017-11-23 03:00 | 205 | 203
2017-11-23 03:30 | 204 | 203
2017-11-23 04:00 | 204 | 203
2017-11-23 04:30 | 204 | 203
2017-11-23 05:00 | 210 | 208
2017-11-23 05:30 | 217 | 216
2017-11-23 06:00 | 224 | 223
2017-11-23 06:30 | 239 | 237
2017-11-23 07:00 | 244 | 243
2017-11-23 07:30 | 251 | 250
2017-11-23 08:00 | 258 | 256
2017-11-23 08:30 | 262 | 261
2017-11-23 09:00 | 263 | 261
2017-11-23 09:30 | 260 | 259
2017-11-23 10:00 | 247 | 246
2017-11-23 10:30 | 244 | 242
2017-11-23 11:00 | 249 | 247
2017-11-23 11:30 | 245 | 243
2017-11-23 12:00 | 246 | 244
2017-11-23 12:30 | 248 | 246
2017-11-23 13:00 | 251 | 250
2017-11-23 13:30 | 246 | 245
2017-11-23 14:00 | 248 | 246
2017-11-23 14:30 | 261 | 259
2017-11-23 15:00 | 262 | 260
2017-11-23 15:30 | 252 | 251
2017-11-23 16:00 | 258 | 257
2017-11-23 16:30 | 266 | 265
2017-11-23 17:00 | 269 | 268
2017-11-23 17:30 | 270 | 268
2017-11-23 18:00 | 285 | 284
2017-11-23 18:30 | 292 | 290
2017-11-23 19:00 | 301 | 299
2017-11-23 19:30 | 302 | 301
2017-11-23 20:00 | 297 | 296
2017-11-23 20:30 | 288 | 287
2017-11-23 21:00 | 278 | 276
2017-11-23 21:30 | 267 | 265
2017-11-23 22:00 | 251 | 249
2017-11-23 22:30 | 256 | 253
2017-11-23 23:00 | 253 | 252
2017-11-23 23:30 | 241 | 240
2017-11-24 | 233 | 231
2017-11-24 00:30 | 225 | 223
2017-11-24 01:00 | 218 | 217
2017-11-24 01:30 | 213 | 212
2017-11-24 02:00 | 210 | 208
2017-11-24 02:30 | 208 | 207
2017-11-24 03:00 | 207 | 205
2017-11-24 03:30 | 206 | 204
2017-11-24 04:00 | 208 | 206
2017-11-24 04:30 | 209 | 207
2017-11-24 05:00 | 210 | 208
2017-11-24 05:30 | 213 | 211
2017-11-24 06:00 | 223 | 221
2017-11-24 06:30 | 239 | 237
2017-11-24 07:00 | 246 | 244
2017-11-24 07:30 | 254 | 253
2017-11-24 08:00 | 262 | 261
2017-11-24 08:30 | 263 | 262
2017-11-24 09:00 | 259 | 258
2017-11-24 09:30 | 257 | 255
2017-11-24 10:00 | 257 | 255
2017-11-24 10:30 | 258 | 257
2017-11-24 11:00 | 256 | 255
2017-11-24 11:30 | 256 | 255
2017-11-24 12:00 | 264 | 262
2017-11-24 12:30 | 267 | 266
2017-11-24 13:00 | 274 | 272
2017-11-24 13:30 | 275 | 274
2017-11-24 14:00 | 247 | 245
2017-11-24 14:30 | 208 | 206
2017-11-24 15:00 | 212 | 210
2017-11-24 15:30 | 208 | 206
2017-11-24 16:00 | 198 | 196
2017-11-24 16:30 | 198 | 195
2017-11-24 17:00 | 199 | 197
2017-11-24 17:30 | 202 | 199
2017-11-24 18:00 | 202 | 200
2017-11-24 18:30 | 202 | 199
2017-11-24 19:00 | 207 | 205
2017-11-24 19:30 | 206 | 204
2017-11-24 20:00 | 199 | 197
2017-11-24 20:30 | 212 | 210
2017-11-24 21:00 | 210 | 208
2017-11-24 21:30 | 200 | 198
2017-11-24 22:00 | 199 | 197
2017-11-24 22:30 | 189 | 187
2017-11-24 23:00 | 186 | 184
2017-11-24 23:30 | 176 | 173
2017-11-25 | 228 | 226
2017-11-25 00:30 | 232 | 231
2017-11-25 01:00 | 226 | 224
2017-11-25 01:30 | 220 | 219
2017-11-25 02:00 | 217 | 215
2017-11-25 02:30 | 215 | 213
2017-11-25 03:00 | 213 | 212
2017-11-25 03:30 | 211 | 210
2017-11-25 04:00 | 209 | 208
2017-11-25 04:30 | 208 | 206
2017-11-25 05:00 | 210 | 208
2017-11-25 05:30 | 210 | 208
2017-11-25 06:00 | 213 | 211
2017-11-25 06:30 | 217 | 215
2017-11-25 07:00 | 220 | 219
2017-11-25 07:30 | 217 | 215
2017-11-25 08:00 | 218 | 217
2017-11-25 08:30 | 227 | 226
2017-11-25 09:00 | 234 | 233
2017-11-25 09:30 | 238 | 237
2017-11-25 10:00 | 237 | 236
2017-11-25 10:30 | 235 | 234
2017-11-25 11:00 | 237 | 236
2017-11-25 11:30 | 233 | 232
2017-11-25 12:00 | 233 | 231
2017-11-25 12:30 | 230 | 229
2017-11-25 13:00 | 233 | 232
2017-11-25 13:30 | 241 | 240
2017-11-25 14:00 | 246 | 245
2017-11-25 14:30 | 251 | 249
2017-11-25 15:00 | 255 | 253
2017-11-25 15:30 | 249 | 247
2017-11-25 16:00 | 254 | 252
2017-11-25 16:30 | 262 | 260
2017-11-25 17:00 | 263 | 261
2017-11-25 17:30 | 269 | 267
2017-11-25 18:00 | 272 | 270
2017-11-25 18:30 | 272 | 271
2017-11-25 19:00 | 275 | 273
2017-11-25 19:30 | 289 | 287
2017-11-25 20:00 | 284 | 282
2017-11-25 20:30 | 274 | 272
2017-11-25 21:00 | 267 | 266
2017-11-25 21:30 | 267 | 266
2017-11-25 22:00 | 267 | 266
2017-11-25 22:30 | 256 | 254
2017-11-25 23:00 | 255 | 253
2017-11-25 23:30 | 245 | 244
2017-11-26 | 236 | 235
2017-11-26 00:30 | 228 | 226
2017-11-26 01:00 | 224 | 222
2017-11-26 01:30 | 219 | 217
2017-11-26 02:00 | 212 | 210
2017-11-26 02:30 | 207 | 205
2017-11-26 03:00 | 204 | 202
2017-11-26 03:30 | 204 | 202
2017-11-26 04:00 | 202 | 200
2017-11-26 04:30 | 200 | 198
2017-11-26 05:00 | 199 | 197
2017-11-26 05:30 | 201 | 199
2017-11-26 06:00 | 198 | 196
2017-11-26 06:30 | 202 | 200
2017-11-26 07:00 | 199 | 197
2017-11-26 07:30 | 194 | 192
2017-11-26 08:00 | 196 | 194
2017-11-26 08:30 | 202 | 201
2017-11-26 09:00 | 210 | 209
2017-11-26 09:30 | 212 | 211
2017-11-26 10:00 | 213 | 212
2017-11-26 10:30 | 217 | 215
2017-11-26 11:00 | 215 | 213
2017-11-26 11:30 | 217 | 215
2017-11-26 12:00 | 218 | 217
2017-11-26 12:30 | 227 | 225
2017-11-26 13:00 | 233 | 231
2017-11-26 13:30 | 235 | 233
2017-11-26 14:00 | 236 | 235
2017-11-26 14:30 | 245 | 243
2017-11-26 15:00 | 249 | 247
2017-11-26 15:30 | 246 | 245
2017-11-26 16:00 | 243 | 241
2017-11-26 16:30 | 247 | 246
2017-11-26 17:00 | 259 | 257
2017-11-26 17:30 | 269 | 268
2017-11-26 18:00 | 290 | 288
2017-11-26 18:30 | 296 | 294
2017-11-26 19:00 | 303 | 301
2017-11-26 19:30 | 309 | 307
2017-11-26 20:00 | 301 | 299
2017-11-26 20:30 | 265 | 262
2017-11-26 21:00 | 241 | 239
2017-11-26 21:30 | 248 | 246
2017-11-26 22:00 | 259 | 257
2017-11-26 22:30 | 254 | 253
2017-11-26 23:00 | 251 | 249
2017-11-26 23:30 | 244 | 242
2017-11-27 | 235 | 233
2017-11-27 00:30 | 228 | 226
2017-11-27 01:00 | 222 | 219
2017-11-27 01:30 | 217 | 215
2017-11-27 02:00 | 214 | 211
2017-11-27 02:30 | 214 | 211
2017-11-27 03:00 | 214 | 211
2017-11-27 03:30 | 214 | 212
2017-11-27 04:00 | 214 | 212
2017-11-27 04:30 | 201 | 198
2017-11-27 05:00 | 178 | 176
2017-11-27 05:30 | 180 | 178
2017-11-27 06:00 | 186 | 184
2017-11-27 06:30 | 199 | 197
2017-11-27 07:00 | 205 | 203
2017-11-27 07:30 | 199 | 196
2017-11-27 08:00 | 187 | 184
2017-11-27 08:30 | 194 | 192
2017-11-27 09:00 | 195 | 193
2017-11-27 09:30 | 199 | 197
2017-11-27 10:00 | 194 | 192
2017-11-27 10:30 | 201 | 199
2017-11-27 11:00 | 211 | 209
2017-11-27 11:30 | 212 | 209
2017-11-27 12:00 | 207 | 204
2017-11-27 12:30 | 207 | 205
2017-11-27 13:00 | 214 | 212
2017-11-27 13:30 | 217 | 215
2017-11-27 14:00 | 219 | 217
2017-11-27 14:30 | 207 | 205
2017-11-27 15:00 | 199 | 197
2017-11-27 15:30 | 171 | 169
2017-11-27 16:00 | 161 | 159
2017-11-27 16:30 | 164 | 162
2017-11-27 17:00 | 170 | 168
2017-11-27 17:30 | 175 | 172
2017-11-27 18:00 | 175 | 173
2017-11-27 18:30 | 178 | 176
2017-11-27 19:00 | 181 | 179
2017-11-27 19:30 | 185 | 183
2017-11-27 20:00 | 179 | 177
2017-11-27 20:30 | 188 | 186
2017-11-27 21:00 | 213 | 211
2017-11-27 21:30 | 212 | 209
2017-11-27 22:00 | 204 | 202
2017-11-27 22:30 | 189 | 186
2017-11-27 23:00 | 184 | 182
2017-11-27 23:30 | 175 | 172
2017-11-28 | 190 | 188
2017-11-28 00:30 | 226 | 224
2017-11-28 01:00 | 223 | 221
2017-11-28 01:30 | 217 | 215
2017-11-28 02:00 | 214 | 211
2017-11-28 02:30 | 212 | 210
2017-11-28 03:00 | 210 | 208
2017-11-28 03:30 | 209 | 207
2017-11-28 04:00 | 207 | 205
2017-11-28 04:30 | 209 | 206
2017-11-28 05:00 | 211 | 209
2017-11-28 05:30 | 218 | 216
2017-11-28 06:00 | 225 | 223
2017-11-28 06:30 | 241 | 239
2017-11-28 07:00 | 248 | 247
2017-11-28 07:30 | 252 | 251
2017-11-28 08:00 | 251 | 249
2017-11-28 08:30 | 254 | 252
2017-11-28 09:00 | 259 | 258
2017-11-28 09:30 | 259 | 257
2017-11-28 10:00 | 256 | 254
2017-11-28 10:30 | 256 | 254
2017-11-28 11:00 | 264 | 262
2017-11-28 11:30 | 263 | 261
2017-11-28 12:00 | 265 | 263
2017-11-28 12:30 | 267 | 265
2017-11-28 13:00 | 271 | 269
2017-11-28 13:30 | 298 | 296
2017-11-28 14:00 | 306 | 305
2017-11-28 14:30 | 304 | 303
2017-11-28 15:00 | 305 | 304
2017-11-28 15:30 | 298 | 296
2017-11-28 16:00 | 295 | 293
2017-11-28 16:30 | 298 | 297
2017-11-28 17:00 | 300 | 299
2017-11-28 17:30 | 299 | 297
2017-11-28 18:00 | 311 | 309
2017-11-28 18:30 | 317 | 316
2017-11-28 19:00 | 328 | 327
2017-11-28 19:30 | 332 | 330
2017-11-28 20:00 | 325 | 324
2017-11-28 20:30 | 316 | 314
2017-11-28 21:00 | 290 | 288
2017-11-28 21:30 | 265 | 263
2017-11-28 22:00 | 255 | 253
2017-11-28 22:30 | 256 | 254
2017-11-28 23:00 | 250 | 248
2017-11-28 23:30 | 240 | 238
2017-11-29 | 228 | 226
2017-11-29 00:30 | 221 | 218
2017-11-29 01:00 | 215 | 213
2017-11-29 01:30 | 213 | 211
2017-11-29 02:00 | 210 | 208
2017-11-29 02:30 | 208 | 205
2017-11-29 03:00 | 207 | 204
2017-11-29 03:30 | 204 | 201
2017-11-29 04:00 | 202 | 199
2017-11-29 04:30 | 203 | 200
2017-11-29 05:00 | 208 | 205
2017-11-29 05:30 | 213 | 211
2017-11-29 06:00 | 220 | 218
2017-11-29 06:30 | 239 | 237
2017-11-29 07:00 | 252 | 250
2017-11-29 07:30 | 270 | 268
2017-11-29 08:00 | 277 | 275
2017-11-29 08:30 | 284 | 282
2017-11-29 09:00 | 287 | 284
2017-11-29 09:30 | 290 | 287
2017-11-29 10:00 | 277 | 274
2017-11-29 10:30 | 270 | 267
2017-11-29 11:00 | 276 | 273
2017-11-29 11:30 | 278 | 275
2017-11-29 12:00 | 277 | 275
2017-11-29 12:30 | 274 | 271
2017-11-29 13:00 | 286 | 283
2017-11-29 13:30 | 283 | 280
2017-11-29 14:00 | 282 | 279
2017-11-29 14:30 | 286 | 283
2017-11-29 15:00 | 295 | 293
2017-11-29 15:30 | 297 | 294
2017-11-29 16:00 | 299 | 297
2017-11-29 16:30 | 293 | 291
2017-11-29 17:00 | 295 | 293
2017-11-29 17:30 | 310 | 308
2017-11-29 18:00 | 310 | 308
2017-11-29 18:30 | 314 | 311
2017-11-29 19:00 | 330 | 327
2017-11-29 19:30 | 337 | 334
2017-11-29 20:00 | 330 | 328
2017-11-29 20:30 | 317 | 314
2017-11-29 21:00 | 307 | 305
2017-11-29 21:30 | 292 | 289
2017-11-29 22:00 | 282 | 279
2017-11-29 22:30 | 274 | 272
2017-11-29 23:00 | 275 | 273
2017-11-29 23:30 | 269 | 267
2017-11-30 | 256 | 254
2017-11-30 00:30 | 248 | 246
2017-11-30 01:00 | 241 | 240
2017-11-30 01:30 | 237 | 235
2017-11-30 02:00 | 232 | 230
2017-11-30 02:30 | 231 | 229
2017-11-30 03:00 | 232 | 230
2017-11-30 03:30 | 224 | 222
2017-11-30 04:00 | 222 | 220
2017-11-30 04:30 | 221 | 219
2017-11-30 05:00 | 222 | 220
2017-11-30 05:30 | 228 | 226
2017-11-30 06:00 | 235 | 233
2017-11-30 06:30 | 251 | 249
2017-11-30 07:00 | 260 | 258
2017-11-30 07:30 | 263 | 261
2017-11-30 08:00 | 276 | 274
2017-11-30 08:30 | 286 | 284
2017-11-30 09:00 | 289 | 287
2017-11-30 09:30 | 294 | 292
2017-11-30 10:00 | 293 | 291
2017-11-30 10:30 | 292 | 289
2017-11-30 11:00 | 289 | 287
2017-11-30 11:30 | 293 | 290
2017-11-30 12:00 | 293 | 290
2017-11-30 12:30 | 296 | 293
2017-11-30 13:00 | 256 | 254
2017-11-30 13:30 | 225 | 223
2017-11-30 14:00 | 217 | 216
2017-11-30 14:30 | 222 | 220
2017-11-30 15:00 | 225 | 224
2017-11-30 15:30 | 224 | 223
2017-11-30 16:00 | 214 | 212
2017-11-30 16:30 | 221 | 220
2017-11-30 17:00 | 229 | 228
2017-11-30 17:30 | 231 | 230
2017-11-30 18:00 | 236 | 235
2017-11-30 18:30 | 241 | 240
2017-11-30 19:00 | 247 | 245
2017-11-30 19:30 | 262 | 260
2017-11-30 20:00 | 257 | 256
2017-11-30 20:30 | 258 | 256
2017-11-30 21:00 | 248 | 247
2017-11-30 21:30 | 233 | 232
2017-11-30 22:00 | 226 | 224
2017-11-30 22:30 | 213 | 211
2017-11-30 23:00 | 270 | 268
2017-11-30 23:30 | 277 | 275
2017-12-01 | 267 | 264
2017-12-01 00:30 | 256 | 254
2017-12-01 01:00 | 245 | 243
2017-12-01 01:30 | 240 | 238
2017-12-01 02:00 | 239 | 237
2017-12-01 02:30 | 237 | 235
2017-12-01 03:00 | 235 | 233
2017-12-01 03:30 | 234 | 232
2017-12-01 04:00 | 230 | 228
2017-12-01 04:30 | 229 | 227
2017-12-01 05:00 | 232 | 231
2017-12-01 05:30 | 239 | 237
2017-12-01 06:00 | 246 | 244
2017-12-01 06:30 | 264 | 262
2017-12-01 07:00 | 268 | 266
2017-12-01 07:30 | 275 | 273
2017-12-01 08:00 | 284 | 282
2017-12-01 08:30 | 277 | 275
2017-12-01 09:00 | 278 | 277
2017-12-01 09:30 | 290 | 288
2017-12-01 10:00 | 293 | 291
2017-12-01 10:30 | 291 | 290
2017-12-01 11:00 | 290 | 289
2017-12-01 11:30 | 288 | 286
2017-12-01 12:00 | 297 | 296
2017-12-01 12:30 | 294 | 293
2017-12-01 13:00 | 249 | 247
2017-12-01 13:30 | 227 | 225
2017-12-01 14:00 | 229 | 228
2017-12-01 14:30 | 227 | 226
2017-12-01 15:00 | 229 | 227
2017-12-01 15:30 | 219 | 217
2017-12-01 16:00 | 217 | 214
2017-12-01 16:30 | 228 | 226
2017-12-01 17:00 | 232 | 229
2017-12-01 17:30 | 229 | 226
2017-12-01 18:00 | 233 | 230
2017-12-01 18:30 | 234 | 232
2017-12-01 19:00 | 238 | 236
2017-12-01 19:30 | 243 | 240
2017-12-01 20:00 | 241 | 238
2017-12-01 20:30 | 241 | 238
2017-12-01 21:00 | 292 | 290
2017-12-01 21:30 | 305 | 304
2017-12-01 22:00 | 302 | 301
2017-12-01 22:30 | 290 | 289
2017-12-01 23:00 | 285 | 283
2017-12-01 23:30 | 274 | 272
2017-12-02 | 264 | 263
2017-12-02 00:30 | 257 | 255
2017-12-02 01:00 | 244 | 242
2017-12-02 01:30 | 239 | 237
2017-12-02 02:00 | 234 | 232
2017-12-02 02:30 | 230 | 228
2017-12-02 03:00 | 228 | 226
2017-12-02 03:30 | 226 | 224
2017-12-02 04:00 | 227 | 225
2017-12-02 04:30 | 226 | 225
2017-12-02 05:00 | 228 | 226
2017-12-02 05:30 | 232 | 230
2017-12-02 06:00 | 233 | 231
2017-12-02 06:30 | 240 | 238
2017-12-02 07:00 | 241 | 239
2017-12-02 07:30 | 238 | 236
2017-12-02 08:00 | 243 | 241
2017-12-02 08:30 | 251 | 249
2017-12-02 09:00 | 260 | 258
2017-12-02 09:30 | 266 | 265
2017-12-02 10:00 | 265 | 264
2017-12-02 10:30 | 271 | 269
2017-12-02 11:00 | 270 | 269
2017-12-02 11:30 | 270 | 269
2017-12-02 12:00 | 274 | 272
2017-12-02 12:30 | 274 | 273
2017-12-02 13:00 | 279 | 278
2017-12-02 13:30 | 284 | 283
2017-12-02 14:00 | 290 | 289
2017-12-02 14:30 | 292 | 290
2017-12-02 15:00 | 299 | 298
2017-12-02 15:30 | 304 | 303
2017-12-02 16:00 | 304 | 303
2017-12-02 16:30 | 301 | 300
2017-12-02 17:00 | 304 | 303
2017-12-02 17:30 | 316 | 315
2017-12-02 18:00 | 318 | 317
2017-12-02 18:30 | 319 | 318
2017-12-02 19:00 | 323 | 322
2017-12-02 19:30 | 329 | 328
2017-12-02 20:00 | 320 | 318
2017-12-02 20:30 | 322 | 321
2017-12-02 21:00 | 312 | 310
2017-12-02 21:30 | 303 | 302
2017-12-02 22:00 | 294 | 293
2017-12-02 22:30 | 284 | 283
2017-12-02 23:00 | 290 | 289
2017-12-02 23:30 | 276 | 275
2017-12-03 | 268 | 267
2017-12-03 00:30 | 257 | 256
2017-12-03 01:00 | 252 | 251
2017-12-03 01:30 | 246 | 245
2017-12-03 02:00 | 243 | 242
2017-12-03 02:30 | 236 | 235
2017-12-03 03:00 | 235 | 234
2017-12-03 03:30 | 234 | 232
2017-12-03 04:00 | 234 | 232
2017-12-03 04:30 | 232 | 231
2017-12-03 05:00 | 232 | 230
2017-12-03 05:30 | 233 | 232
2017-12-03 06:00 | 229 | 228
2017-12-03 06:30 | 232 | 231
2017-12-03 07:00 | 236 | 235
2017-12-03 07:30 | 229 | 228
2017-12-03 08:00 | 230 | 228
2017-12-03 08:30 | 237 | 236
2017-12-03 09:00 | 245 | 244
2017-12-03 09:30 | 250 | 249
2017-12-03 10:00 | 254 | 253
2017-12-03 10:30 | 256 | 255
2017-12-03 11:00 | 260 | 259
2017-12-03 11:30 | 265 | 264
2017-12-03 12:00 | 269 | 268
2017-12-03 12:30 | 274 | 273
2017-12-03 13:00 | 285 | 283
2017-12-03 13:30 | 297 | 296
2017-12-03 14:00 | 302 | 301
2017-12-03 14:30 | 310 | 309
2017-12-03 15:00 | 311 | 309
2017-12-03 15:30 | 313 | 312
2017-12-03 16:00 | 304 | 303
2017-12-03 16:30 | 305 | 304
2017-12-03 17:00 | 313 | 311
2017-12-03 17:30 | 317 | 316
2017-12-03 18:00 | 329 | 328
2017-12-03 18:30 | 337 | 336
2017-12-03 19:00 | 334 | 333
2017-12-03 19:30 | 343 | 342
2017-12-03 20:00 | 334 | 333
2017-12-03 20:30 | 338 | 336
2017-12-03 21:00 | 327 | 325
2017-12-03 21:30 | 313 | 312
2017-12-03 22:00 | 297 | 295
2017-12-03 22:30 | 288 | 286
2017-12-03 23:00 | 288 | 286
2017-12-03 23:30 | 271 | 269
2017-12-04 | 256 | 253
2017-12-04 00:30 | 246 | 244
2017-12-04 01:00 | 235 | 234
2017-12-04 01:30 | 227 | 226
2017-12-04 02:00 | 221 | 220
2017-12-04 02:30 | 216 | 215
2017-12-04 03:00 | 213 | 212
2017-12-04 03:30 | 211 | 210
2017-12-04 04:00 | 209 | 208
2017-12-04 04:30 | 210 | 209
2017-12-04 05:00 | 212 | 211
2017-12-04 05:30 | 218 | 218
2017-12-04 06:00 | 223 | 222
2017-12-04 06:30 | 235 | 234
2017-12-04 07:00 | 251 | 249
2017-12-04 07:30 | 260 | 258
2017-12-04 08:00 | 276 | 273
2017-12-04 08:30 | 285 | 282
2017-12-04 09:00 | 288 | 285
2017-12-04 09:30 | 290 | 288
2017-12-04 10:00 | 288 | 285
2017-12-04 10:30 | 284 | 280
2017-12-04 11:00 | 272 | 268
2017-12-04 11:30 | 267 | 262
2017-12-04 12:00 | 264 | 260
2017-12-04 12:30 | 263 | 259
2017-12-04 13:00 | 270 | 265
2017-12-04 13:30 | 278 | 274
2017-12-04 14:00 | 286 | 282
2017-12-04 14:30 | 290 | 286
2017-12-04 15:00 | 296 | 293
2017-12-04 15:30 | 297 | 293
2017-12-04 16:00 | 292 | 289
2017-12-04 16:30 | 302 | 298
2017-12-04 17:00 | 305 | 302
2017-12-04 17:30 | 306 | 303
2017-12-04 18:00 | 321 | 318
2017-12-04 18:30 | 335 | 332
2017-12-04 19:00 | 347 | 344
2017-12-04 19:30 | 350 | 347
2017-12-04 20:00 | 343 | 341
2017-12-04 20:30 | 326 | 323
2017-12-04 21:00 | 310 | 307
2017-12-04 21:30 | 289 | 286
2017-12-04 22:00 | 288 | 285
2017-12-04 22:30 | 270 | 266
2017-12-04 23:00 | 276 | 271
2017-12-04 23:30 | 264 | 260
2017-12-05 | 259 | 255
2017-12-05 00:30 | 260 | 256
2017-12-05 01:00 | 250 | 245
2017-12-05 01:30 | 244 | 240
2017-12-05 02:00 | 240 | 235
2017-12-05 02:30 | 235 | 231
2017-12-05 03:00 | 228 | 224
2017-12-05 03:30 | 224 | 219
2017-12-05 04:00 | 214 | 209
2017-12-05 04:30 | 213 | 208
2017-12-05 05:00 | 213 | 209
2017-12-05 05:30 | 215 | 211
2017-12-05 06:00 | 220 | 216
2017-12-05 06:30 | 223 | 219
2017-12-05 07:00 | 232 | 228
2017-12-05 07:30 | 243 | 239
2017-12-05 08:00 | 248 | 244
2017-12-05 08:30 | 252 | 248
2017-12-05 09:00 | 253 | 249
2017-12-05 09:30 | 256 | 252
2017-12-05 10:00 | 255 | 251
2017-12-05 10:30 | 254 | 250
2017-12-05 11:00 | 257 | 254
2017-12-05 11:30 | 268 | 264
2017-12-05 12:00 | 270 | 266
2017-12-05 12:30 | 273 | 270
2017-12-05 13:00 | 279 | 275
2017-12-05 13:30 | 287 | 283
2017-12-05 14:00 | 292 | 289
2017-12-05 14:30 | 312 | 309
2017-12-05 15:00 | 317 | 314
2017-12-05 15:30 | 307 | 305
2017-12-05 16:00 | 303 | 301
2017-12-05 16:30 | 307 | 305
2017-12-05 17:00 | 276 | 272
2017-12-05 17:30 | 289 | 285
2017-12-05 18:00 | 294 | 290
2017-12-05 18:30 | 303 | 299
2017-12-05 19:00 | 307 | 304
2017-12-05 19:30 | 313 | 310
2017-12-05 20:00 | 309 | 306
2017-12-05 20:30 | 328 | 325
2017-12-05 21:00 | 321 | 318
2017-12-05 21:30 | 315 | 312
2017-12-05 22:00 | 306 | 303
2017-12-05 22:30 | 290 | 286
2017-12-05 23:00 | 294 | 291
2017-12-05 23:30 | 283 | 281
2017-12-06 | 273 | 271
2017-12-06 00:30 | 263 | 260
2017-12-06 01:00 | 255 | 253
2017-12-06 01:30 | 253 | 251
2017-12-06 02:00 | 250 | 248
2017-12-06 02:30 | 247 | 244
2017-12-06 03:00 | 246 | 244
2017-12-06 03:30 | 246 | 243
2017-12-06 04:00 | 243 | 241
2017-12-06 04:30 | 240 | 237
2017-12-06 05:00 | 239 | 237
2017-12-06 05:30 | 244 | 242
2017-12-06 06:00 | 246 | 244
2017-12-06 06:30 | 252 | 250
2017-12-06 07:00 | 257 | 255
2017-12-06 07:30 | 263 | 261
2017-12-06 08:00 | 263 | 261
2017-12-06 08:30 | 272 | 270
2017-12-06 09:00 | 275 | 273
2017-12-06 09:30 | 275 | 273
2017-12-06 10:00 | 277 | 275
2017-12-06 10:30 | 279 | 277
2017-12-06 11:00 | 282 | 280
2017-12-06 11:30 | 285 | 283
2017-12-06 12:00 | 290 | 288
2017-12-06 12:30 | 295 | 293
2017-12-06 13:00 | 299 | 297
2017-12-06 13:30 | 303 | 301
2017-12-06 14:00 | 313 | 310
2017-12-06 14:30 | 318 | 316
2017-12-06 15:00 | 322 | 320
2017-12-06 15:30 | 319 | 316
2017-12-06 16:00 | 315 | 312
2017-12-06 16:30 | 320 | 317
2017-12-06 17:00 | 325 | 322
2017-12-06 17:30 | 328 | 326
2017-12-06 18:00 | 329 | 326
2017-12-06 18:30 | 331 | 328
2017-12-06 19:00 | 333 | 331
2017-12-06 19:30 | 342 | 340
2017-12-06 20:00 | 336 | 334
2017-12-06 20:30 | 336 | 334
2017-12-06 21:00 | 327 | 324
2017-12-06 21:30 | 321 | 318
2017-12-06 22:00 | 310 | 307
2017-12-06 22:30 | 291 | 288
2017-12-06 23:00 | 299 | 296
2017-12-06 23:30 | 288 | 284
2017-12-07 | 276 | 272
2017-12-07 00:30 | 268 | 265
2017-12-07 01:00 | 261 | 257
2017-12-07 01:30 | 255 | 252
2017-12-07 02:00 | 247 | 245
2017-12-07 02:30 | 244 | 241
2017-12-07 03:00 | 243 | 240
2017-12-07 03:30 | 242 | 239
2017-12-07 04:00 | 239 | 236
2017-12-07 04:30 | 240 | 237
2017-12-07 05:00 | 242 | 239
2017-12-07 05:30 | 247 | 244
2017-12-07 06:00 | 253 | 250
2017-12-07 06:30 | 258 | 256
2017-12-07 07:00 | 259 | 256
2017-12-07 07:30 | 262 | 260
2017-12-07 08:00 | 269 | 267
2017-12-07 08:30 | 270 | 268
2017-12-07 09:00 | 274 | 272
2017-12-07 09:30 | 270 | 268
2017-12-07 10:00 | 244 | 242
2017-12-07 10:30 | 238 | 237
2017-12-07 11:00 | 242 | 240
2017-12-07 11:30 | 244 | 242
2017-12-07 12:00 | 243 | 242
2017-12-07 12:30 | 231 | 229
2017-12-07 13:00 | 219 | 218
2017-12-07 13:30 | 225 | 224
2017-12-07 14:00 | 239 | 238
2017-12-07 14:30 | 241 | 240
2017-12-07 15:00 | 239 | 237
2017-12-07 15:30 | 235 | 234
2017-12-07 16:00 | 239 | 238
2017-12-07 16:30 | 241 | 240
2017-12-07 17:00 | 244 | 242
2017-12-07 17:30 | 251 | 250
2017-12-07 18:00 | 255 | 254
2017-12-07 18:30 | 256 | 255
2017-12-07 19:00 | 263 | 262
2017-12-07 19:30 | 270 | 268
2017-12-07 20:00 | 270 | 268
2017-12-07 20:30 | 270 | 268
2017-12-07 21:00 | 260 | 259
2017-12-07 21:30 | 255 | 254
2017-12-07 22:00 | 250 | 248
2017-12-07 22:30 | 233 | 231
2017-12-07 23:00 | 239 | 238
2017-12-07 23:30 | 230 | 228
2017-12-08 | 216 | 215
2017-12-08 00:30 | 209 | 208
2017-12-08 01:00 | 201 | 199
2017-12-08 01:30 | 195 | 194
2017-12-08 02:00 | 189 | 188
2017-12-08 02:30 | 188 | 187
2017-12-08 03:00 | 186 | 184
2017-12-08 03:30 | 184 | 182
2017-12-08 04:00 | 181 | 180
2017-12-08 04:30 | 183 | 181
2017-12-08 05:00 | 182 | 181
2017-12-08 05:30 | 188 | 186
2017-12-08 06:00 | 193 | 192
2017-12-08 06:30 | 196 | 195
2017-12-08 07:00 | 197 | 196
2017-12-08 07:30 | 201 | 199
2017-12-08 08:00 | 209 | 208
2017-12-08 08:30 | 213 | 212
2017-12-08 09:00 | 222 | 221
2017-12-08 09:30 | 224 | 223
2017-12-08 10:00 | 221 | 220
2017-12-08 10:30 | 220 | 219
2017-12-08 11:00 | 220 | 219
2017-12-08 11:30 | 221 | 219
2017-12-08 12:00 | 220 | 218
2017-12-08 12:30 | 224 | 222
2017-12-08 13:00 | 238 | 236
2017-12-08 13:30 | 248 | 246
2017-12-08 14:00 | 254 | 252
2017-12-08 14:30 | 261 | 260
2017-12-08 15:00 | 263 | 261
2017-12-08 15:30 | 254 | 252
2017-12-08 16:00 | 245 | 243
2017-12-08 16:30 | 251 | 249
2017-12-08 17:00 | 246 | 244
2017-12-08 17:30 | 243 | 241
2017-12-08 18:00 | 245 | 243
2017-12-08 18:30 | 242 | 240
2017-12-08 19:00 | 244 | 242
2017-12-08 19:30 | 248 | 247
2017-12-08 20:00 | 244 | 243
2017-12-08 20:30 | 270 | 268
2017-12-08 21:00 | 315 | 314
2017-12-08 21:30 | 309 | 308
2017-12-08 22:00 | 306 | 304
2017-12-08 22:30 | 294 | 292
2017-12-08 23:00 | 301 | 299
2017-12-08 23:30 | 293 | 291
2017-12-09 | 283 | 281
2017-12-09 00:30 | 269 | 267
2017-12-09 01:00 | 261 | 259
2017-12-09 01:30 | 255 | 254
2017-12-09 02:00 | 251 | 250
2017-12-09 02:30 | 245 | 244
2017-12-09 03:00 | 243 | 241
2017-12-09 03:30 | 241 | 240
2017-12-09 04:00 | 239 | 238
2017-12-09 04:30 | 235 | 234
2017-12-09 05:00 | 236 | 235
2017-12-09 05:30 | 238 | 237
2017-12-09 06:00 | 238 | 237
2017-12-09 06:30 | 232 | 231
2017-12-09 07:00 | 226 | 224
2017-12-09 07:30 | 221 | 220
2017-12-09 08:00 | 227 | 226
2017-12-09 08:30 | 238 | 237
2017-12-09 09:00 | 246 | 245
2017-12-09 09:30 | 250 | 248
2017-12-09 10:00 | 248 | 246
2017-12-09 10:30 | 247 | 246
2017-12-09 11:00 | 251 | 249
2017-12-09 11:30 | 247 | 245
2017-12-09 12:00 | 251 | 250
2017-12-09 12:30 | 255 | 253
2017-12-09 13:00 | 257 | 256
2017-12-09 13:30 | 258 | 257
2017-12-09 14:00 | 266 | 265
2017-12-09 14:30 | 272 | 271
2017-12-09 15:00 | 280 | 278
2017-12-09 15:30 | 282 | 281
2017-12-09 16:00 | 276 | 275
2017-12-09 16:30 | 286 | 285
2017-12-09 17:00 | 295 | 294
2017-12-09 17:30 | 300 | 298
2017-12-09 18:00 | 304 | 302
2017-12-09 18:30 | 302 | 300
2017-12-09 19:00 | 303 | 302
2017-12-09 19:30 | 311 | 309
2017-12-09 20:00 | 303 | 301
2017-12-09 20:30 | 308 | 307
2017-12-09 21:00 | 302 | 300
2017-12-09 21:30 | 291 | 289
2017-12-09 22:00 | 286 | 284
2017-12-09 22:30 | 275 | 273
2017-12-09 23:00 | 283 | 281
2017-12-09 23:30 | 276 | 274
2017-12-10 | 267 | 265
2017-12-10 00:30 | 258 | 256
2017-12-10 01:00 | 252 | 250
2017-12-10 01:30 | 247 | 246
2017-12-10 02:00 | 245 | 244
2017-12-10 02:30 | 241 | 240
2017-12-10 03:00 | 235 | 233
2017-12-10 03:30 | 233 | 232
2017-12-10 04:00 | 229 | 228
2017-12-10 04:30 | 230 | 228
2017-12-10 05:00 | 229 | 227
2017-12-10 05:30 | 231 | 229
2017-12-10 06:00 | 229 | 226
2017-12-10 06:30 | 218 | 216
2017-12-10 07:00 | 209 | 208
2017-12-10 07:30 | 207 | 205
2017-12-10 08:00 | 211 | 209
2017-12-10 08:30 | 216 | 214
2017-12-10 09:00 | 220 | 219
2017-12-10 09:30 | 227 | 225
2017-12-10 10:00 | 230 | 227
2017-12-10 10:30 | 234 | 232
2017-12-10 11:00 | 236 | 234
2017-12-10 11:30 | 239 | 237
2017-12-10 12:00 | 244 | 242
2017-12-10 12:30 | 245 | 243
2017-12-10 13:00 | 249 | 246
2017-12-10 13:30 | 254 | 252
2017-12-10 14:00 | 257 | 255
2017-12-10 14:30 | 260 | 258
2017-12-10 15:00 | 256 | 254
2017-12-10 15:30 | 262 | 260
2017-12-10 16:00 | 264 | 262
2017-12-10 16:30 | 268 | 267
2017-12-10 17:00 | 279 | 277
2017-12-10 17:30 | 288 | 286
2017-12-10 18:00 | 299 | 297
2017-12-10 18:30 | 301 | 299
2017-12-10 19:00 | 303 | 301
2017-12-10 19:30 | 309 | 306
2017-12-10 20:00 | 306 | 304
2017-12-10 20:30 | 316 | 314
2017-12-10 21:00 | 310 | 308
2017-12-10 21:30 | 299 | 297
2017-12-10 22:00 | 294 | 292
2017-12-10 22:30 | 280 | 278
2017-12-10 23:00 | 284 | 282
2017-12-10 23:30 | 274 | 272
2017-12-11 | 263 | 261
2017-12-11 00:30 | 255 | 252
2017-12-11 01:00 | 247 | 244
2017-12-11 01:30 | 242 | 240
2017-12-11 02:00 | 238 | 235
2017-12-11 02:30 | 235 | 233
2017-12-11 03:00 | 231 | 229
2017-12-11 03:30 | 229 | 227
2017-12-11 04:00 | 228 | 226
2017-12-11 04:30 | 229 | 226
2017-12-11 05:00 | 233 | 230
2017-12-11 05:30 | 237 | 235
2017-12-11 06:00 | 241 | 238
2017-12-11 06:30 | 241 | 239
2017-12-11 07:00 | 245 | 243
2017-12-11 07:30 | 250 | 248
2017-12-11 08:00 | 262 | 260
2017-12-11 08:30 | 265 | 263
2017-12-11 09:00 | 266 | 264
2017-12-11 09:30 | 260 | 258
2017-12-11 10:00 | 256 | 254
2017-12-11 10:30 | 257 | 255
2017-12-11 11:00 | 258 | 256
2017-12-11 11:30 | 261 | 259
2017-12-11 12:00 | 267 | 265
2017-12-11 12:30 | 270 | 268
2017-12-11 13:00 | 272 | 270
2017-12-11 13:30 | 281 | 279
2017-12-11 14:00 | 290 | 288
2017-12-11 14:30 | 293 | 292
2017-12-11 15:00 | 294 | 292
2017-12-11 15:30 | 290 | 288
2017-12-11 16:00 | 292 | 290
2017-12-11 16:30 | 298 | 296
2017-12-11 17:00 | 307 | 305
2017-12-11 17:30 | 305 | 303
2017-12-11 18:00 | 318 | 316
2017-12-11 18:30 | 325 | 323
2017-12-11 19:00 | 332 | 329
2017-12-11 19:30 | 332 | 329
2017-12-11 20:00 | 323 | 320
2017-12-11 20:30 | 311 | 308
2017-12-11 21:00 | 300 | 297
2017-12-11 21:30 | 288 | 285
2017-12-11 22:00 | 287 | 285
2017-12-11 22:30 | 270 | 267
2017-12-11 23:00 | 257 | 255
2017-12-11 23:30 | 246 | 244
2017-12-12 | 237 | 234
2017-12-12 00:30 | 248 | 246
2017-12-12 01:00 | 241 | 239
2017-12-12 01:30 | 236 | 234
2017-12-12 02:00 | 231 | 229
2017-12-12 02:30 | 229 | 227
2017-12-12 03:00 | 228 | 226
2017-12-12 03:30 | 227 | 225
2017-12-12 04:00 | 224 | 222
2017-12-12 04:30 | 224 | 222
2017-12-12 05:00 | 226 | 224
2017-12-12 05:30 | 231 | 230
2017-12-12 06:00 | 235 | 234
2017-12-12 06:30 | 249 | 248
2017-12-12 07:00 | 239 | 238
2017-12-12 07:30 | 231 | 230
2017-12-12 08:00 | 239 | 237
2017-12-12 08:30 | 247 | 244
2017-12-12 09:00 | 253 | 249
2017-12-12 09:30 | 255 | 252
2017-12-12 10:00 | 255 | 251
2017-12-12 10:30 | 254 | 251
2017-12-12 11:00 | 254 | 250
2017-12-12 11:30 | 257 | 254
2017-12-12 12:00 | 262 | 259
2017-12-12 12:30 | 264 | 260
2017-12-12 13:00 | 263 | 259
2017-12-12 13:30 | 265 | 262
2017-12-12 14:00 | 272 | 268
2017-12-12 14:30 | 278 | 274
2017-12-12 15:00 | 282 | 278
2017-12-12 15:30 | 278 | 274
2017-12-12 16:00 | 286 | 282
2017-12-12 16:30 | 290 | 287
2017-12-12 17:00 | 293 | 290
2017-12-12 17:30 | 290 | 288
2017-12-12 18:00 | 301 | 298
2017-12-12 18:30 | 308 | 306
2017-12-12 19:00 | 314 | 312
2017-12-12 19:30 | 322 | 320
2017-12-12 20:00 | 320 | 319
2017-12-12 20:30 | 309 | 307
2017-12-12 21:00 | 298 | 296
2017-12-12 21:30 | 287 | 285
2017-12-12 22:00 | 288 | 286
2017-12-12 22:30 | 275 | 273
2017-12-12 23:00 | 261 | 259
2017-12-12 23:30 | 250 | 248
2017-12-13 | 239 | 237
2017-12-13 00:30 | 247 | 246
2017-12-13 01:00 | 243 | 242
2017-12-13 01:30 | 237 | 236
2017-12-13 02:00 | 232 | 231
2017-12-13 02:30 | 228 | 227
2017-12-13 03:00 | 228 | 226
2017-12-13 03:30 | 228 | 226
2017-12-13 04:00 | 231 | 229
2017-12-13 04:30 | 232 | 230
2017-12-13 05:00 | 235 | 233
2017-12-13 05:30 | 238 | 236
2017-12-13 06:00 | 243 | 241
2017-12-13 06:30 | 257 | 255
2017-12-13 07:00 | 250 | 248
2017-12-13 07:30 | 240 | 238
2017-12-13 08:00 | 244 | 242
2017-12-13 08:30 | 250 | 249
2017-12-13 09:00 | 259 | 257
2017-12-13 09:30 | 251 | 250
2017-12-13 10:00 | 246 | 245
2017-12-13 10:30 | 248 | 246
2017-12-13 11:00 | 250 | 248
2017-12-13 11:30 | 253 | 251
2017-12-13 12:00 | 259 | 258
2017-12-13 12:30 | 257 | 255
2017-12-13 13:00 | 257 | 255
2017-12-13 13:30 | 261 | 260
2017-12-13 14:00 | 268 | 266
2017-12-13 14:30 | 274 | 273
2017-12-13 15:00 | 278 | 276
2017-12-13 15:30 | 282 | 280
2017-12-13 16:00 | 283 | 282
2017-12-13 16:30 | 282 | 281
2017-12-13 17:00 | 278 | 277
2017-12-13 17:30 | 287 | 286
2017-12-13 18:00 | 293 | 292
2017-12-13 18:30 | 299 | 298
2017-12-13 19:00 | 314 | 313
2017-12-13 19:30 | 320 | 319
2017-12-13 20:00 | 314 | 313
2017-12-13 20:30 | 303 | 302
2017-12-13 21:00 | 295 | 293
2017-12-13 21:30 | 284 | 283
2017-12-13 22:00 | 286 | 285
2017-12-13 22:30 | 291 | 289
2017-12-13 23:00 | 279 | 277
2017-12-13 23:30 | 268 | 266
2017-12-14 | 255 | 253
2017-12-14 00:30 | 247 | 245
2017-12-14 01:00 | 238 | 236
2017-12-14 01:30 | 232 | 230
2017-12-14 02:00 | 226 | 225
2017-12-14 02:30 | 230 | 228
2017-12-14 03:00 | 228 | 227
2017-12-14 03:30 | 228 | 227
2017-12-14 04:00 | 228 | 227
2017-12-14 04:30 | 230 | 229
2017-12-14 05:00 | 231 | 230
2017-12-14 05:30 | 234 | 233
2017-12-14 06:00 | 238 | 237
2017-12-14 06:30 | 248 | 247
2017-12-14 07:00 | 245 | 244
2017-12-14 07:30 | 237 | 236
2017-12-14 08:00 | 245 | 244
2017-12-14 08:30 | 246 | 245
2017-12-14 09:00 | 247 | 245
2017-12-14 09:30 | 247 | 246
2017-12-14 10:00 | 247 | 245
2017-12-14 10:30 | 250 | 249
2017-12-14 11:00 | 257 | 256
2017-12-14 11:30 | 267 | 266
2017-12-14 12:00 | 261 | 260
2017-12-14 12:30 | 261 | 260
2017-12-14 13:00 | 265 | 264
2017-12-14 13:30 | 271 | 269
2017-12-14 14:00 | 275 | 274
2017-12-14 14:30 | 280 | 279
2017-12-14 15:00 | 285 | 283
2017-12-14 15:30 | 278 | 277
2017-12-14 16:00 | 282 | 281
2017-12-14 16:30 | 290 | 289
2017-12-14 17:00 | 302 | 301
2017-12-14 17:30 | 309 | 308
2017-12-14 18:00 | 325 | 324
2017-12-14 18:30 | 332 | 331
2017-12-14 19:00 | 337 | 336
2017-12-14 19:30 | 344 | 344
2017-12-14 20:00 | 335 | 334
2017-12-14 20:30 | 324 | 323
2017-12-14 21:00 | 314 | 313
2017-12-14 21:30 | 300 | 298
2017-12-14 22:00 | 287 | 285
2017-12-14 22:30 | 283 | 282
2017-12-14 23:00 | 285 | 283
2017-12-14 23:30 | 271 | 270
2017-12-15 | 261 | 259
2017-12-15 00:30 | 253 | 252
2017-12-15 01:00 | 245 | 243
2017-12-15 01:30 | 239 | 238
2017-12-15 02:00 | 236 | 234
2017-12-15 02:30 | 231 | 230
2017-12-15 03:00 | 227 | 226
2017-12-15 03:30 | 225 | 224
2017-12-15 04:00 | 226 | 224
2017-12-15 04:30 | 226 | 225
2017-12-15 05:00 | 227 | 226
2017-12-15 05:30 | 223 | 221
2017-12-15 06:00 | 224 | 222
2017-12-15 06:30 | 235 | 233
2017-12-15 07:00 | 245 | 243
2017-12-15 07:30 | 251 | 250
2017-12-15 08:00 | 256 | 255
2017-12-15 08:30 | 255 | 254
2017-12-15 09:00 | 256 | 255
2017-12-15 09:30 | 257 | 256
2017-12-15 10:00 | 257 | 255
2017-12-15 10:30 | 258 | 257
2017-12-15 11:00 | 259 | 258
2017-12-15 11:30 | 260 | 258
2017-12-15 12:00 | 261 | 260
2017-12-15 12:30 | 261 | 260
2017-12-15 13:00 | 265 | 264
2017-12-15 13:30 | 270 | 268
2017-12-15 14:00 | 271 | 270
2017-12-15 14:30 | 269 | 268
2017-12-15 15:00 | 277 | 276
2017-12-15 15:30 | 277 | 276
2017-12-15 16:00 | 280 | 279
2017-12-15 16:30 | 291 | 290
2017-12-15 17:00 | 298 | 297
2017-12-15 17:30 | 293 | 292
2017-12-15 18:00 | 312 | 311
2017-12-15 18:30 | 314 | 313
2017-12-15 19:00 | 315 | 313
2017-12-15 19:30 | 320 | 319
2017-12-15 20:00 | 319 | 317
2017-12-15 20:30 | 310 | 309
2017-12-15 21:00 | 302 | 301
2017-12-15 21:30 | 291 | 290
2017-12-15 22:00 | 288 | 287
2017-12-15 22:30 | 303 | 301
2017-12-15 23:00 | 294 | 292
2017-12-15 23:30 | 281 | 279
2017-12-16 | 269 | 268
2017-12-16 00:30 | 260 | 258
2017-12-16 01:00 | 253 | 251
2017-12-16 01:30 | 247 | 245
2017-12-16 02:00 | 242 | 240
2017-12-16 02:30 | 240 | 238
2017-12-16 03:00 | 235 | 233
2017-12-16 03:30 | 232 | 230
2017-12-16 04:00 | 231 | 230
2017-12-16 04:30 | 229 | 228
2017-12-16 05:00 | 230 | 229
2017-12-16 05:30 | 231 | 229
2017-12-16 06:00 | 229 | 228
2017-12-16 06:30 | 232 | 230
2017-12-16 07:00 | 229 | 228
2017-12-16 07:30 | 226 | 225
2017-12-16 08:00 | 232 | 231
2017-12-16 08:30 | 239 | 238
2017-12-16 09:00 | 247 | 245
2017-12-16 09:30 | 255 | 254
2017-12-16 10:00 | 257 | 255
2017-12-16 10:30 | 260 | 258
2017-12-16 11:00 | 266 | 264
2017-12-16 11:30 | 267 | 265
2017-12-16 12:00 | 264 | 263
2017-12-16 12:30 | 262 | 260
2017-12-16 13:00 | 261 | 259
2017-12-16 13:30 | 264 | 263
2017-12-16 14:00 | 270 | 268
2017-12-16 14:30 | 265 | 263
2017-12-16 15:00 | 275 | 274
2017-12-16 15:30 | 277 | 275
2017-12-16 16:00 | 280 | 278
2017-12-16 16:30 | 290 | 289
2017-12-16 17:00 | 294 | 292
2017-12-16 17:30 | 303 | 302
2017-12-16 18:00 | 312 | 310
2017-12-16 18:30 | 317 | 316
2017-12-16 19:00 | 315 | 313
2017-12-16 19:30 | 316 | 315
2017-12-16 20:00 | 317 | 316
2017-12-16 20:30 | 312 | 311
2017-12-16 21:00 | 311 | 310
2017-12-16 21:30 | 312 | 311
2017-12-16 22:00 | 306 | 305
2017-12-16 22:30 | 303 | 301
2017-12-16 23:00 | 294 | 293
2017-12-16 23:30 | 283 | 282
2017-12-17 | 274 | 273
2017-12-17 00:30 | 266 | 264
2017-12-17 01:00 | 259 | 257
2017-12-17 01:30 | 251 | 249
2017-12-17 02:00 | 246 | 244
2017-12-17 02:30 | 245 | 243
2017-12-17 03:00 | 242 | 240
2017-12-17 03:30 | 240 | 238
2017-12-17 04:00 | 237 | 235
2017-12-17 04:30 | 233 | 231
2017-12-17 05:00 | 233 | 231
2017-12-17 05:30 | 235 | 233
2017-12-17 06:00 | 232 | 230
2017-12-17 06:30 | 233 | 231
2017-12-17 07:00 | 232 | 230
2017-12-17 07:30 | 224 | 222
2017-12-17 08:00 | 228 | 226
2017-12-17 08:30 | 235 | 233
2017-12-17 09:00 | 237 | 236
2017-12-17 09:30 | 245 | 243
2017-12-17 10:00 | 246 | 244
2017-12-17 10:30 | 244 | 243
2017-12-17 11:00 | 243 | 242
2017-12-17 11:30 | 246 | 245
2017-12-17 12:00 | 252 | 250
2017-12-17 12:30 | 251 | 249
2017-12-17 13:00 | 254 | 252
2017-12-17 13:30 | 262 | 260
2017-12-17 14:00 | 267 | 265
2017-12-17 14:30 | 270 | 268
2017-12-17 15:00 | 274 | 272
2017-12-17 15:30 | 279 | 277
2017-12-17 16:00 | 281 | 279
2017-12-17 16:30 | 282 | 280
2017-12-17 17:00 | 288 | 287
2017-12-17 17:30 | 291 | 290
2017-12-17 18:00 | 295 | 294
2017-12-17 18:30 | 299 | 298
2017-12-17 19:00 | 307 | 306
2017-12-17 19:30 | 314 | 313
2017-12-17 20:00 | 315 | 313
2017-12-17 20:30 | 308 | 306
2017-12-17 21:00 | 305 | 304
2017-12-17 21:30 | 305 | 304
2017-12-17 22:00 | 299 | 297
2017-12-17 22:30 | 294 | 293
2017-12-17 23:00 | 282 | 281
2017-12-17 23:30 | 272 | 270
2017-12-18 | 262 | 260
2017-12-18 00:30 | 253 | 252
2017-12-18 01:00 | 246 | 245
2017-12-18 01:30 | 242 | 241
2017-12-18 02:00 | 238 | 236
2017-12-18 02:30 | 235 | 233
2017-12-18 03:00 | 234 | 232
2017-12-18 03:30 | 231 | 230
2017-12-18 04:00 | 228 | 226
2017-12-18 04:30 | 229 | 228
2017-12-18 05:00 | 232 | 231
2017-12-18 05:30 | 236 | 234
2017-12-18 06:00 | 237 | 235
2017-12-18 06:30 | 249 | 248
2017-12-18 07:00 | 254 | 252
2017-12-18 07:30 | 259 | 258
2017-12-18 08:00 | 267 | 266
2017-12-18 08:30 | 277 | 276
2017-12-18 09:00 | 282 | 281
2017-12-18 09:30 | 283 | 282
2017-12-18 10:00 | 280 | 279
2017-12-18 10:30 | 282 | 280
2017-12-18 11:00 | 279 | 278
2017-12-18 11:30 | 284 | 283
2017-12-18 12:00 | 287 | 285
2017-12-18 12:30 | 291 | 289
2017-12-18 13:00 | 288 | 286
2017-12-18 13:30 | 294 | 293
2017-12-18 14:00 | 290 | 289
2017-12-18 14:30 | 297 | 296
2017-12-18 15:00 | 309 | 308
2017-12-18 15:30 | 308 | 306
2017-12-18 16:00 | 302 | 300
2017-12-18 16:30 | 296 | 294
2017-12-18 17:00 | 293 | 291
2017-12-18 17:30 | 296 | 295
2017-12-18 18:00 | 294 | 292
2017-12-18 18:30 | 312 | 311
2017-12-18 19:00 | 329 | 327
2017-12-18 19:30 | 334 | 334
2017-12-18 20:00 | 333 | 332
2017-12-18 20:30 | 324 | 323
2017-12-18 21:00 | 323 | 322
2017-12-18 21:30 | 322 | 321
2017-12-18 22:00 | 318 | 317
2017-12-18 22:30 | 309 | 308
2017-12-18 23:00 | 298 | 297
2017-12-18 23:30 | 287 | 286
2017-12-19 | 277 | 275
2017-12-19 00:30 | 269 | 268
2017-12-19 01:00 | 261 | 259
2017-12-19 01:30 | 256 | 254
2017-12-19 02:00 | 250 | 248
2017-12-19 02:30 | 245 | 244
2017-12-19 03:00 | 243 | 242
2017-12-19 03:30 | 240 | 238
2017-12-19 04:00 | 237 | 235
2017-12-19 04:30 | 237 | 235
2017-12-19 05:00 | 239 | 237
2017-12-19 05:30 | 242 | 240
2017-12-19 06:00 | 247 | 245
2017-12-19 06:30 | 255 | 254
2017-12-19 07:00 | 259 | 258
2017-12-19 07:30 | 263 | 262
2017-12-19 08:00 | 273 | 272
2017-12-19 08:30 | 274 | 273
2017-12-19 09:00 | 253 | 252
2017-12-19 09:30 | 247 | 245
2017-12-19 10:00 | 242 | 241
2017-12-19 10:30 | 242 | 241
2017-12-19 11:00 | 244 | 243
2017-12-19 11:30 | 242 | 241
2017-12-19 12:00 | 231 | 229
2017-12-19 12:30 | 214 | 213
2017-12-19 13:00 | 226 | 225
2017-12-19 13:30 | 231 | 230
2017-12-19 14:00 | 232 | 231
2017-12-19 14:30 | 240 | 239
2017-12-19 15:00 | 245 | 244
2017-12-19 15:30 | 186 | 184
2017-12-19 16:00 | 177 | 176
2017-12-19 16:30 | 218 | 216
2017-12-19 17:00 | 228 | 227
2017-12-19 17:30 | 233 | 232
2017-12-19 18:00 | 254 | 253
2017-12-19 18:30 | 260 | 259
2017-12-19 19:00 | 265 | 264
2017-12-19 19:30 | 272 | 271
2017-12-19 20:00 | 270 | 269
2017-12-19 20:30 | 261 | 260
2017-12-19 21:00 | 260 | 259
2017-12-19 21:30 | 259 | 258
2017-12-19 22:00 | 252 | 251
2017-12-19 22:30 | 245 | 244
2017-12-19 23:00 | 234 | 233
2017-12-19 23:30 | 220 | 218
2017-12-20 | 210 | 209
2017-12-20 00:30 | 204 | 203
2017-12-20 01:00 | 199 | 198
2017-12-20 01:30 | 186 | 184
2017-12-20 02:00 | 181 | 180
2017-12-20 02:30 | 179 | 178
2017-12-20 03:00 | 177 | 175
2017-12-20 03:30 | 175 | 173
2017-12-20 04:00 | 172 | 171
2017-12-20 04:30 | 172 | 171
2017-12-20 05:00 | 172 | 171
2017-12-20 05:30 | 175 | 174
2017-12-20 06:00 | 179 | 177
2017-12-20 06:30 | 192 | 191
2017-12-20 07:00 | 194 | 193
2017-12-20 07:30 | 200 | 199
2017-12-20 08:00 | 214 | 213
2017-12-20 08:30 | 222 | 221
2017-12-20 09:00 | 226 | 225
2017-12-20 09:30 | 225 | 224
2017-12-20 10:00 | 226 | 225
2017-12-20 10:30 | 227 | 226
2017-12-20 11:00 | 227 | 226
2017-12-20 11:30 | 228 | 227
2017-12-20 12:00 | 228 | 226
2017-12-20 12:30 | 230 | 228
2017-12-20 13:00 | 234 | 233
2017-12-20 13:30 | 227 | 226
2017-12-20 14:00 | 241 | 240
2017-12-20 14:30 | 244 | 243
2017-12-20 15:00 | 248 | 247
2017-12-20 15:30 | 257 | 256
2017-12-20 16:00 | 263 | 262
2017-12-20 16:30 | 260 | 259
2017-12-20 17:00 | 264 | 263
2017-12-20 17:30 | 268 | 266
2017-12-20 18:00 | 269 | 268
2017-12-20 18:30 | 269 | 268
2017-12-20 19:00 | 272 | 270
2017-12-20 19:30 | 280 | 279
2017-12-20 20:00 | 280 | 278
2017-12-20 20:30 | 270 | 269
2017-12-20 21:00 | 260 | 259
2017-12-20 21:30 | 281 | 280
2017-12-20 22:00 | 322 | 321
2017-12-20 22:30 | 318 | 317
2017-12-20 23:00 | 311 | 310
2017-12-20 23:30 | 300 | 299
2017-12-21 | 289 | 288
2017-12-21 00:30 | 279 | 278
2017-12-21 01:00 | 272 | 270
2017-12-21 01:30 | 266 | 264
2017-12-21 02:00 | 260 | 259
2017-12-21 02:30 | 258 | 256
2017-12-21 03:00 | 255 | 254
2017-12-21 03:30 | 254 | 253
2017-12-21 04:00 | 252 | 251
2017-12-21 04:30 | 252 | 251
2017-12-21 05:00 | 252 | 251
2017-12-21 05:30 | 256 | 255
2017-12-21 06:00 | 260 | 259
2017-12-21 06:30 | 271 | 270
2017-12-21 07:00 | 279 | 278
2017-12-21 07:30 | 280 | 279
2017-12-21 08:00 | 287 | 286
2017-12-21 08:30 | 292 | 291
2017-12-21 09:00 | 294 | 293
2017-12-21 09:30 | 297 | 297
2017-12-21 10:00 | 299 | 298
2017-12-21 10:30 | 302 | 302
2017-12-21 11:00 | 295 | 295
2017-12-21 11:30 | 292 | 292
2017-12-21 12:00 | 295 | 295
2017-12-21 12:30 | 305 | 305
2017-12-21 13:00 | 309 | 308
2017-12-21 13:30 | 311 | 310
2017-12-21 14:00 | 314 | 314
2017-12-21 14:30 | 321 | 320
2017-12-21 15:00 | 312 | 311
2017-12-21 15:30 | 304 | 304
2017-12-21 16:00 | 304 | 303
2017-12-21 16:30 | 302 | 301
2017-12-21 17:00 | 284 | 284
2017-12-21 17:30 | 290 | 289
2017-12-21 18:00 | 314 | 313
2017-12-21 18:30 | 329 | 329
2017-12-21 19:00 | 334 | 333
2017-12-21 19:30 | 338 | 337
2017-12-21 20:00 | 345 | 345
2017-12-21 20:30 | 340 | 340
2017-12-21 21:00 | 329 | 328
2017-12-21 21:30 | 335 | 335
2017-12-21 22:00 | 332 | 332
2017-12-21 22:30 | 326 | 326
2017-12-21 23:00 | 314 | 314
2017-12-21 23:30 | 301 | 301
2017-12-22 | 290 | 289
2017-12-22 00:30 | 280 | 279
2017-12-22 01:00 | 271 | 271
2017-12-22 01:30 | 266 | 265
2017-12-22 02:00 | 261 | 260
2017-12-22 02:30 | 257 | 256
2017-12-22 03:00 | 255 | 254
2017-12-22 03:30 | 252 | 251
2017-12-22 04:00 | 252 | 251
2017-12-22 04:30 | 252 | 251
2017-12-22 05:00 | 252 | 251
2017-12-22 05:30 | 252 | 251
2017-12-22 06:00 | 256 | 255
2017-12-22 06:30 | 265 | 265
2017-12-22 07:00 | 266 | 265
2017-12-22 07:30 | 268 | 267
2017-12-22 08:00 | 275 | 273
2017-12-22 08:30 | 284 | 282
2017-12-22 09:00 | 289 | 288
2017-12-22 09:30 | 292 | 290
2017-12-22 10:00 | 292 | 291
2017-12-22 10:30 | 294 | 293
2017-12-22 11:00 | 294 | 293
2017-12-22 11:30 | 290 | 288
2017-12-22 12:00 | 292 | 290
2017-12-22 12:30 | 293 | 291
2017-12-22 13:00 | 294 | 292
2017-12-22 13:30 | 297 | 295
2017-12-22 14:00 | 303 | 301
2017-12-22 14:30 | 307 | 305
2017-12-22 15:00 | 311 | 309
2017-12-22 15:30 | 309 | 308
2017-12-22 16:00 | 311 | 310
2017-12-22 16:30 | 301 | 299
2017-12-22 17:00 | 309 | 307
2017-12-22 17:30 | 318 | 317
2017-12-22 18:00 | 335 | 334
2017-12-22 18:30 | 339 | 338
2017-12-22 19:00 | 343 | 342
2017-12-22 19:30 | 346 | 345
2017-12-22 20:00 | 350 | 349
2017-12-22 20:30 | 345 | 344
2017-12-22 21:00 | 339 | 338
2017-12-22 21:30 | 337 | 335
2017-12-22 22:00 | 334 | 333
2017-12-22 22:30 | 330 | 329
2017-12-22 23:00 | 320 | 319
2017-12-22 23:30 | 309 | 307
2017-12-23 | 298 | 296
2017-12-23 00:30 | 289 | 288
2017-12-23 01:00 | 280 | 278
2017-12-23 01:30 | 274 | 272
2017-12-23 02:00 | 269 | 267
2017-12-23 02:30 | 265 | 263
2017-12-23 03:00 | 261 | 259
2017-12-23 03:30 | 259 | 257
2017-12-23 04:00 | 257 | 255
2017-12-23 04:30 | 256 | 255
2017-12-23 05:00 | 256 | 254
2017-12-23 05:30 | 255 | 253
2017-12-23 06:00 | 255 | 253
2017-12-23 06:30 | 256 | 254
2017-12-23 07:00 | 260 | 258
2017-12-23 07:30 | 267 | 265
2017-12-23 08:00 | 273 | 272
2017-12-23 08:30 | 279 | 278
2017-12-23 09:00 | 284 | 282
2017-12-23 09:30 | 286 | 284
2017-12-23 10:00 | 279 | 278
2017-12-23 10:30 | 267 | 265
2017-12-23 11:00 | 268 | 266
2017-12-23 11:30 | 270 | 268
2017-12-23 12:00 | 274 | 272
2017-12-23 12:30 | 272 | 270
2017-12-23 13:00 | 275 | 273
2017-12-23 13:30 | 287 | 285
2017-12-23 14:00 | 287 | 285
2017-12-23 14:30 | 294 | 292
2017-12-23 15:00 | 303 | 301
2017-12-23 15:30 | 306 | 304
2017-12-23 16:00 | 313 | 312
2017-12-23 16:30 | 307 | 304
2017-12-23 17:00 | 311 | 309
2017-12-23 17:30 | 318 | 316
2017-12-23 18:00 | 323 | 320
2017-12-23 18:30 | 325 | 323
2017-12-23 19:00 | 330 | 328
2017-12-23 19:30 | 335 | 333
2017-12-23 20:00 | 335 | 333
2017-12-23 20:30 | 329 | 327
2017-12-23 21:00 | 337 | 335
2017-12-23 21:30 | 331 | 329
2017-12-23 22:00 | 323 | 322
2017-12-23 22:30 | 316 | 314
2017-12-23 23:00 | 305 | 303
2017-12-23 23:30 | 295 | 293
2017-12-24 | 286 | 284
2017-12-24 00:30 | 278 | 276
2017-12-24 01:00 | 269 | 267
2017-12-24 01:30 | 263 | 261
2017-12-24 02:00 | 258 | 255
2017-12-24 02:30 | 253 | 251
2017-12-24 03:00 | 251 | 248
2017-12-24 03:30 | 248 | 246
2017-12-24 04:00 | 247 | 244
2017-12-24 04:30 | 248 | 245
2017-12-24 05:00 | 245 | 242
2017-12-24 05:30 | 245 | 242
2017-12-24 06:00 | 245 | 242
2017-12-24 06:30 | 245 | 242
2017-12-24 07:00 | 245 | 242
2017-12-24 07:30 | 251 | 249
2017-12-24 08:00 | 258 | 256
2017-12-24 08:30 | 266 | 264
2017-12-24 09:00 | 271 | 268
2017-12-24 09:30 | 276 | 274
2017-12-24 10:00 | 270 | 268
2017-12-24 10:30 | 261 | 259
2017-12-24 11:00 | 259 | 257
2017-12-24 11:30 | 260 | 258
2017-12-24 12:00 | 260 | 258
2017-12-24 12:30 | 265 | 263
2017-12-24 13:00 | 263 | 261
2017-12-24 13:30 | 270 | 267
2017-12-24 14:00 | 267 | 264
2017-12-24 14:30 | 281 | 279
2017-12-24 15:00 | 291 | 289
2017-12-24 15:30 | 302 | 300
2017-12-24 16:00 | 314 | 312
2017-12-24 16:30 | 325 | 322
2017-12-24 17:00 | 323 | 321
2017-12-24 17:30 | 333 | 331
2017-12-24 18:00 | 346 | 344
2017-12-24 18:30 | 350 | 348
2017-12-24 19:00 | 353 | 352
2017-12-24 19:30 | 358 | 356
2017-12-24 20:00 | 358 | 356
2017-12-24 20:30 | 350 | 349
2017-12-24 21:00 | 343 | 341
2017-12-24 21:30 | 334 | 332
2017-12-24 22:00 | 325 | 323
2017-12-24 22:30 | 317 | 315
2017-12-24 23:00 | 308 | 305
2017-12-24 23:30 | 296 | 294
2017-12-25 | 284 | 282
2017-12-25 00:30 | 275 | 273
2017-12-25 01:00 | 266 | 264
2017-12-25 01:30 | 260 | 257
2017-12-25 02:00 | 253 | 251
2017-12-25 02:30 | 250 | 248
2017-12-25 03:00 | 246 | 244
2017-12-25 03:30 | 243 | 241
2017-12-25 04:00 | 241 | 239
2017-12-25 04:30 | 240 | 238
2017-12-25 05:00 | 240 | 238
2017-12-25 05:30 | 239 | 237
2017-12-25 06:00 | 238 | 236
2017-12-25 06:30 | 241 | 239
2017-12-25 07:00 | 243 | 241
2017-12-25 07:30 | 250 | 248
2017-12-25 08:00 | 255 | 253
2017-12-25 08:30 | 258 | 256
2017-12-25 09:00 | 259 | 257
2017-12-25 09:30 | 260 | 258
2017-12-25 10:00 | 259 | 257
2017-12-25 10:30 | 251 | 249
2017-12-25 11:00 | 249 | 248
2017-12-25 11:30 | 247 | 245
2017-12-25 12:00 | 247 | 245
2017-12-25 12:30 | 246 | 244
2017-12-25 13:00 | 245 | 244
2017-12-25 13:30 | 251 | 250
2017-12-25 14:00 | 252 | 251
2017-12-25 14:30 | 255 | 253
2017-12-25 15:00 | 257 | 255
2017-12-25 15:30 | 255 | 254
2017-12-25 16:00 | 260 | 258
2017-12-25 16:30 | 271 | 269
2017-12-25 17:00 | 281 | 279
2017-12-25 17:30 | 289 | 287
2017-12-25 18:00 | 307 | 305
2017-12-25 18:30 | 313 | 311
2017-12-25 19:00 | 317 | 315
2017-12-25 19:30 | 322 | 320
2017-12-25 20:00 | 325 | 323
2017-12-25 20:30 | 322 | 320
2017-12-25 21:00 | 316 | 315
2017-12-25 21:30 | 312 | 310
2017-12-25 22:00 | 304 | 302
2017-12-25 22:30 | 300 | 298
2017-12-25 23:00 | 291 | 290
2017-12-25 23:30 | 279 | 278
2017-12-26 | 271 | 269
2017-12-26 00:30 | 264 | 262
2017-12-26 01:00 | 255 | 253
2017-12-26 01:30 | 251 | 250
2017-12-26 02:00 | 247 | 245
2017-12-26 02:30 | 244 | 242
2017-12-26 03:00 | 241 | 240
2017-12-26 03:30 | 240 | 239
2017-12-26 04:00 | 237 | 236
2017-12-26 04:30 | 236 | 235
2017-12-26 05:00 | 235 | 235
2017-12-26 05:30 | 236 | 235
2017-12-26 06:00 | 236 | 235
2017-12-26 06:30 | 237 | 236
2017-12-26 07:00 | 239 | 238
2017-12-26 07:30 | 246 | 245
2017-12-26 08:00 | 251 | 251
2017-12-26 08:30 | 254 | 253
2017-12-26 09:00 | 258 | 258
2017-12-26 09:30 | 261 | 260
2017-12-26 10:00 | 254 | 253
2017-12-26 10:30 | 245 | 244
2017-12-26 11:00 | 243 | 242
2017-12-26 11:30 | 243 | 242
2017-12-26 12:00 | 242 | 241
2017-12-26 12:30 | 243 | 242
2017-12-26 13:00 | 246 | 245
2017-12-26 13:30 | 262 | 261
2017-12-26 14:00 | 270 | 269
2017-12-26 14:30 | 274 | 274
2017-12-26 15:00 | 280 | 280
2017-12-26 15:30 | 280 | 280
2017-12-26 16:00 | 288 | 287
2017-12-26 16:30 | 299 | 297
2017-12-26 17:00 | 307 | 306
2017-12-26 17:30 | 315 | 313
2017-12-26 18:00 | 330 | 328
2017-12-26 18:30 | 336 | 335
2017-12-26 19:00 | 343 | 342
2017-12-26 19:30 | 350 | 349
2017-12-26 20:00 | 352 | 351
2017-12-26 20:30 | 345 | 344
2017-12-26 21:00 | 337 | 336
2017-12-26 21:30 | 330 | 329
2017-12-26 22:00 | 318 | 317
2017-12-26 22:30 | 310 | 309
2017-12-26 23:00 | 299 | 298
2017-12-26 23:30 | 288 | 287
2017-12-27 | 277 | 276
2017-12-27 00:30 | 270 | 270
2017-12-27 01:00 | 263 | 263
2017-12-27 01:30 | 258 | 258
2017-12-27 02:00 | 253 | 253
2017-12-27 02:30 | 252 | 251
2017-12-27 03:00 | 248 | 247
2017-12-27 03:30 | 246 | 245
2017-12-27 04:00 | 245 | 244
2017-12-27 04:30 | 245 | 244
2017-12-27 05:00 | 245 | 244
2017-12-27 05:30 | 247 | 247
2017-12-27 06:00 | 248 | 247
2017-12-27 06:30 | 253 | 252
2017-12-27 07:00 | 258 | 257
2017-12-27 07:30 | 269 | 268
2017-12-27 08:00 | 280 | 279
2017-12-27 08:30 | 287 | 286
2017-12-27 09:00 | 285 | 284
2017-12-27 09:30 | 285 | 284
2017-12-27 10:00 | 278 | 277
2017-12-27 10:30 | 270 | 269
2017-12-27 11:00 | 268 | 267
2017-12-27 11:30 | 270 | 269
2017-12-27 12:00 | 274 | 273
2017-12-27 12:30 | 279 | 279
2017-12-27 13:00 | 283 | 282
2017-12-27 13:30 | 297 | 297
2017-12-27 14:00 | 303 | 302
2017-12-27 14:30 | 309 | 308
2017-12-27 15:00 | 315 | 314
2017-12-27 15:30 | 323 | 322
2017-12-27 16:00 | 332 | 331
2017-12-27 16:30 | 337 | 336
2017-12-27 17:00 | 337 | 336
2017-12-27 17:30 | 352 | 352
2017-12-27 18:00 | 359 | 359
2017-12-27 18:30 | 363 | 362
2017-12-27 19:00 | 367 | 366
2017-12-27 19:30 | 373 | 372
2017-12-27 20:00 | 373 | 373
2017-12-27 20:30 | 365 | 364
2017-12-27 21:00 | 355 | 354
2017-12-27 21:30 | 345 | 345
2017-12-27 22:00 | 333 | 332
2017-12-27 22:30 | 324 | 323
2017-12-27 23:00 | 313 | 312
2017-12-27 23:30 | 302 | 301
2017-12-28 | 291 | 290
2017-12-28 00:30 | 284 | 283
2017-12-28 01:00 | 277 | 276
2017-12-28 01:30 | 272 | 271
2017-12-28 02:00 | 266 | 266
2017-12-28 02:30 | 262 | 261
2017-12-28 03:00 | 257 | 256
2017-12-28 03:30 | 256 | 256
2017-12-28 04:00 | 255 | 254
2017-12-28 04:30 | 254 | 254
2017-12-28 05:00 | 254 | 254
2017-12-28 05:30 | 258 | 257
2017-12-28 06:00 | 258 | 257
2017-12-28 06:30 | 264 | 263
2017-12-28 07:00 | 269 | 269
2017-12-28 07:30 | 279 | 278
2017-12-28 08:00 | 287 | 286
2017-12-28 08:30 | 294 | 293
2017-12-28 09:00 | 298 | 298
2017-12-28 09:30 | 299 | 298
2017-12-28 10:00 | 291 | 290
2017-12-28 10:30 | 290 | 290
2017-12-28 11:00 | 285 | 284
2017-12-28 11:30 | 280 | 280
2017-12-28 12:00 | 284 | 284
2017-12-28 12:30 | 285 | 285
2017-12-28 13:00 | 232 | 232
2017-12-28 13:30 | 210 | 209
2017-12-28 14:00 | 216 | 215
2017-12-28 14:30 | 234 | 234
2017-12-28 15:00 | 244 | 244
2017-12-28 15:30 | 243 | 242
2017-12-28 16:00 | 253 | 253
2017-12-28 16:30 | 266 | 266
2017-12-28 17:00 | 261 | 261
2017-12-28 17:30 | 260 | 259
2017-12-28 18:00 | 274 | 274
2017-12-28 18:30 | 294 | 293
2017-12-28 19:00 | 296 | 296
2017-12-28 19:30 | 304 | 304
2017-12-28 20:00 | 304 | 304
2017-12-28 20:30 | 353 | 353
2017-12-28 21:00 | 358 | 358
2017-12-28 21:30 | 358 | 358
2017-12-28 22:00 | 345 | 344
2017-12-28 22:30 | 321 | 321
2017-12-28 23:00 | 311 | 311
2017-12-28 23:30 | 305 | 305
2017-12-29 | 294 | 294
2017-12-29 00:30 | 286 | 285
2017-12-29 01:00 | 277 | 277
2017-12-29 01:30 | 272 | 272
2017-12-29 02:00 | 268 | 267
2017-12-29 02:30 | 264 | 264
2017-12-29 03:00 | 261 | 261
2017-12-29 03:30 | 259 | 258
2017-12-29 04:00 | 258 | 258
2017-12-29 04:30 | 258 | 258
2017-12-29 05:00 | 259 | 258
2017-12-29 05:30 | 262 | 262
2017-12-29 06:00 | 261 | 261
2017-12-29 06:30 | 265 | 264
2017-12-29 07:00 | 271 | 270
2017-12-29 07:30 | 278 | 278
2017-12-29 08:00 | 287 | 287
2017-12-29 08:30 | 287 | 287
2017-12-29 09:00 | 302 | 302
2017-12-29 09:30 | 292 | 291
2017-12-29 10:00 | 290 | 289
2017-12-29 10:30 | 281 | 280
2017-12-29 11:00 | 267 | 266
2017-12-29 11:30 | 277 | 276
2017-12-29 12:00 | 250 | 250
2017-12-29 12:30 | 210 | 210
2017-12-29 13:00 | 213 | 212
2017-12-29 13:30 | 226 | 226
2017-12-29 14:00 | 235 | 235
2017-12-29 14:30 | 237 | 237
2017-12-29 15:00 | 241 | 241
2017-12-29 15:30 | 242 | 242
2017-12-29 16:00 | 252 | 252
2017-12-29 16:30 | 263 | 262
2017-12-29 17:00 | 271 | 271
2017-12-29 17:30 | 279 | 278
2017-12-29 18:00 | 291 | 291
2017-12-29 18:30 | 293 | 293
2017-12-29 19:00 | 286 | 286
2017-12-29 19:30 | 285 | 285
2017-12-29 20:00 | 296 | 296
2017-12-29 20:30 | 356 | 356
2017-12-29 21:00 | 367 | 367
2017-12-29 21:30 | 358 | 358
2017-12-29 22:00 | 347 | 346
2017-12-29 22:30 | 333 | 333
2017-12-29 23:00 | 322 | 321
2017-12-29 23:30 | 310 | 310
2017-12-30 | 297 | 297
2017-12-30 00:30 | 289 | 289
2017-12-30 01:00 | 282 | 282
2017-12-30 01:30 | 274 | 273
2017-12-30 02:00 | 270 | 270
2017-12-30 02:30 | 265 | 265
2017-12-30 03:00 | 263 | 262
2017-12-30 03:30 | 261 | 260
2017-12-30 04:00 | 257 | 257
2017-12-30 04:30 | 256 | 255
2017-12-30 05:00 | 256 | 255
2017-12-30 05:30 | 256 | 255
2017-12-30 06:00 | 253 | 252
2017-12-30 06:30 | 255 | 255
2017-12-30 07:00 | 257 | 256
2017-12-30 07:30 | 263 | 263
2017-12-30 08:00 | 270 | 269
2017-12-30 08:30 | 275 | 275
2017-12-30 09:00 | 280 | 280
2017-12-30 09:30 | 283 | 283
2017-12-30 10:00 | 281 | 281
2017-12-30 10:30 | 274 | 274
2017-12-30 11:00 | 273 | 273
2017-12-30 11:30 | 276 | 275
2017-12-30 12:00 | 279 | 279
2017-12-30 12:30 | 282 | 282
2017-12-30 13:00 | 287 | 287
2017-12-30 13:30 | 300 | 299
2017-12-30 14:00 | 306 | 305
2017-12-30 14:30 | 313 | 313
2017-12-30 15:00 | 317 | 317
2017-12-30 15:30 | 323 | 322
2017-12-30 16:00 | 330 | 329
2017-12-30 16:30 | 341 | 341
2017-12-30 17:00 | 341 | 341
2017-12-30 17:30 | 343 | 342
2017-12-30 18:00 | 348 | 347
2017-12-30 18:30 | 366 | 365
2017-12-30 19:00 | 372 | 372
2017-12-30 19:30 | 379 | 378
2017-12-30 20:00 | 379 | 378
2017-12-30 20:30 | 377 | 376
2017-12-30 21:00 | 370 | 369
2017-12-30 21:30 | 360 | 359
2017-12-30 22:00 | 349 | 348
2017-12-30 22:30 | 335 | 334
2017-12-30 23:00 | 322 | 321
2017-12-30 23:30 | 309 | 308
2017-12-31 | 298 | 298
2017-12-31 00:30 | 291 | 290
2017-12-31 01:00 | 283 | 283
2017-12-31 01:30 | 276 | 276
2017-12-31 02:00 | 273 | 273
2017-12-31 02:30 | 269 | 269
2017-12-31 03:00 | 266 | 266
2017-12-31 03:30 | 263 | 263
2017-12-31 04:00 | 260 | 260
2017-12-31 04:30 | 259 | 258
2017-12-31 05:00 | 258 | 257
2017-12-31 05:30 | 258 | 257
2017-12-31 06:00 | 256 | 256
2017-12-31 06:30 | 256 | 255
2017-12-31 07:00 | 257 | 256
2017-12-31 07:30 | 260 | 260
2017-12-31 08:00 | 263 | 262
2017-12-31 08:30 | 269 | 268
2017-12-31 09:00 | 271 | 270
2017-12-31 09:30 | 275 | 274
2017-12-31 10:00 | 275 | 274
2017-12-31 10:30 | 264 | 264
2017-12-31 11:00 | 265 | 264
2017-12-31 11:30 | 266 | 266
2017-12-31 12:00 | 269 | 269
2017-12-31 12:30 | 275 | 275
2017-12-31 13:00 | 280 | 280
2017-12-31 13:30 | 294 | 294
2017-12-31 14:00 | 295 | 294
2017-12-31 14:30 | 306 | 305
2017-12-31 15:00 | 317 | 316
2017-12-31 15:30 | 324 | 324
2017-12-31 16:00 | 335 | 335
2017-12-31 16:30 | 345 | 344
2017-12-31 17:00 | 341 | 341
2017-12-31 17:30 | 347 | 346
2017-12-31 18:00 | 354 | 354
2017-12-31 18:30 | 355 | 354
2017-12-31 19:00 | 354 | 353
2017-12-31 19:30 | 353 | 352
2017-12-31 20:00 | 357 | 356
2017-12-31 20:30 | 354 | 354
2017-12-31 21:00 | 346 | 346
2017-12-31 21:30 | 335 | 335
2017-12-31 22:00 | 330 | 330
2017-12-31 22:30 | 323 | 323
2017-12-31 23:00 | 316 | 315
2017-12-31 23:30 | 308 | 308
2018-01-01 | 299 | 299
2018-01-01 00:30 | 291 | 290
2018-01-01 01:00 | 286 | 285
2018-01-01 01:30 | 283 | 282
2018-01-01 02:00 | 277 | 277
2018-01-01 02:30 | 272 | 272
2018-01-01 03:00 | 269 | 268
2018-01-01 03:30 | 267 | 266
2018-01-01 04:00 | 263 | 263
2018-01-01 04:30 | 263 | 263
2018-01-01 05:00 | 261 | 261
2018-01-01 05:30 | 261 | 261
2018-01-01 06:00 | 260 | 259
2018-01-01 06:30 | 261 | 260
2018-01-01 07:00 | 263 | 262
2018-01-01 07:30 | 267 | 266
2018-01-01 08:00 | 270 | 270
2018-01-01 08:30 | 274 | 273
2018-01-01 09:00 | 278 | 277
2018-01-01 09:30 | 283 | 282
2018-01-01 10:00 | 280 | 279
2018-01-01 10:30 | 275 | 275
2018-01-01 11:00 | 278 | 277
2018-01-01 11:30 | 285 | 284
2018-01-01 12:00 | 289 | 288
2018-01-01 12:30 | 293 | 293
2018-01-01 13:00 | 298 | 297
2018-01-01 13:30 | 311 | 311
2018-01-01 14:00 | 323 | 323
2018-01-01 14:30 | 332 | 331
2018-01-01 15:00 | 302 | 301
2018-01-01 15:30 | 263 | 263
2018-01-01 16:00 | 270 | 269
2018-01-01 16:30 | 269 | 268
2018-01-01 17:00 | 278 | 277
2018-01-01 17:30 | 287 | 286
2018-01-01 18:00 | 302 | 302
2018-01-01 18:30 | 310 | 309
2018-01-01 19:00 | 313 | 313
2018-01-01 19:30 | 321 | 321
2018-01-01 20:00 | 323 | 322
2018-01-01 20:30 | 325 | 324
2018-01-01 21:00 | 318 | 317
2018-01-01 21:30 | 367 | 366
2018-01-01 22:00 | 367 | 366
2018-01-01 22:30 | 351 | 351
2018-01-01 23:00 | 337 | 336
2018-01-01 23:30 | 323 | 322
2018-01-02 | 311 | 311
2018-01-02 00:30 | 303 | 303
2018-01-02 01:00 | 297 | 297
2018-01-02 01:30 | 291 | 291
2018-01-02 02:00 | 287 | 287
2018-01-02 02:30 | 285 | 284
2018-01-02 03:00 | 283 | 283
2018-01-02 03:30 | 281 | 280
2018-01-02 04:00 | 279 | 279
2018-01-02 04:30 | 277 | 277
2018-01-02 05:00 | 277 | 277
2018-01-02 05:30 | 280 | 280
2018-01-02 06:00 | 284 | 284
2018-01-02 06:30 | 291 | 290
2018-01-02 07:00 | 301 | 300
2018-01-02 07:30 | 316 | 316
2018-01-02 08:00 | 328 | 327
2018-01-02 08:30 | 341 | 340
2018-01-02 09:00 | 348 | 347
2018-01-02 09:30 | 347 | 345
2018-01-02 10:00 | 330 | 328
2018-01-02 10:30 | 324 | 323
2018-01-02 11:00 | 334 | 332
2018-01-02 11:30 | 333 | 332
2018-01-02 12:00 | 335 | 333
2018-01-02 12:30 | 341 | 340
2018-01-02 13:00 | 346 | 344
2018-01-02 13:30 | 354 | 353
2018-01-02 14:00 | 380 | 379
2018-01-02 14:30 | 387 | 386
2018-01-02 15:00 | 391 | 390
2018-01-02 15:30 | 383 | 381
2018-01-02 16:00 | 401 | 400
2018-01-02 16:30 | 395 | 394
2018-01-02 17:00 | 391 | 390
2018-01-02 17:30 | 389 | 388
2018-01-02 18:00 | 400 | 399
2018-01-02 18:30 | 399 | 398
2018-01-02 19:00 | 396 | 394
2018-01-02 19:30 | 393 | 392
2018-01-02 20:00 | 388 | 386
2018-01-02 20:30 | 387 | 386
2018-01-02 21:00 | 378 | 377
2018-01-02 21:30 | 365 | 364
2018-01-02 22:00 | 348 | 346
2018-01-02 22:30 | 332 | 331
2018-01-02 23:00 | 322 | 320
2018-01-02 23:30 | 310 | 309
2018-01-03 | 301 | 299
2018-01-03 00:30 | 291 | 289
2018-01-03 01:00 | 283 | 282
2018-01-03 01:30 | 278 | 277
2018-01-03 02:00 | 274 | 274
2018-01-03 02:30 | 273 | 272
2018-01-03 03:00 | 268 | 267
2018-01-03 03:30 | 266 | 265
2018-01-03 04:00 | 264 | 263
2018-01-03 04:30 | 263 | 262
2018-01-03 05:00 | 263 | 262
2018-01-03 05:30 | 266 | 265
2018-01-03 06:00 | 269 | 268
2018-01-03 06:30 | 277 | 276
2018-01-03 07:00 | 287 | 286
2018-01-03 07:30 | 298 | 297
2018-01-03 08:00 | 311 | 310
2018-01-03 08:30 | 318 | 317
2018-01-03 09:00 | 324 | 322
2018-01-03 09:30 | 330 | 329
2018-01-03 10:00 | 321 | 320
2018-01-03 10:30 | 305 | 303
2018-01-03 11:00 | 284 | 283
2018-01-03 11:30 | 287 | 286
2018-01-03 12:00 | 293 | 292
2018-01-03 12:30 | 295 | 294
2018-01-03 13:00 | 302 | 301
2018-01-03 13:30 | 311 | 310
2018-01-03 14:00 | 306 | 305
2018-01-03 14:30 | 320 | 318
2018-01-03 15:00 | 337 | 336
2018-01-03 15:30 | 339 | 338
2018-01-03 16:00 | 336 | 335
2018-01-03 16:30 | 335 | 334
2018-01-03 17:00 | 341 | 340
2018-01-03 17:30 | 346 | 345
2018-01-03 18:00 | 345 | 344
2018-01-03 18:30 | 353 | 351
2018-01-03 19:00 | 359 | 358
2018-01-03 19:30 | 360 | 359
2018-01-03 20:00 | 366 | 365
2018-01-03 20:30 | 352 | 351
2018-01-03 21:00 | 341 | 339
2018-01-03 21:30 | 324 | 323
2018-01-03 22:00 | 309 | 307
2018-01-03 22:30 | 290 | 288
2018-01-03 23:00 | 273 | 272
2018-01-03 23:30 | 259 | 258
2018-01-04 | 251 | 249
2018-01-04 00:30 | 242 | 240
2018-01-04 01:00 | 235 | 233
2018-01-04 01:30 | 230 | 228
2018-01-04 02:00 | 224 | 222
2018-01-04 02:30 | 219 | 217
2018-01-04 03:00 | 217 | 215
2018-01-04 03:30 | 216 | 213
2018-01-04 04:00 | 213 | 211
2018-01-04 04:30 | 212 | 210
2018-01-04 05:00 | 212 | 210
2018-01-04 05:30 | 212 | 210
2018-01-04 06:00 | 212 | 210
2018-01-04 06:30 | 219 | 217
2018-01-04 07:00 | 225 | 223
2018-01-04 07:30 | 240 | 239
2018-01-04 08:00 | 252 | 250
2018-01-04 08:30 | 259 | 257
2018-01-04 09:00 | 269 | 268
2018-01-04 09:30 | 276 | 274
2018-01-04 10:00 | 268 | 267
2018-01-04 10:30 | 270 | 269
2018-01-04 11:00 | 272 | 270
2018-01-04 11:30 | 275 | 274
2018-01-04 12:00 | 279 | 277
2018-01-04 12:30 | 283 | 281
2018-01-04 13:00 | 287 | 285
2018-01-04 13:30 | 308 | 307
2018-01-04 14:00 | 315 | 313
2018-01-04 14:30 | 333 | 330
2018-01-04 15:00 | 331 | 328
2018-01-04 15:30 | 335 | 332
2018-01-04 16:00 | 343 | 341
2018-01-04 16:30 | 344 | 341
2018-01-04 17:00 | 340 | 337
2018-01-04 17:30 | 332 | 329
2018-01-04 18:00 | 353 | 351
2018-01-04 18:30 | 358 | 356
2018-01-04 19:00 | 360 | 359
2018-01-04 19:30 | 360 | 359
2018-01-04 20:00 | 354 | 352
2018-01-04 20:30 | 343 | 342
2018-01-04 21:00 | 330 | 328
2018-01-04 21:30 | 312 | 310
2018-01-04 22:00 | 291 | 289
2018-01-04 22:30 | 275 | 273
2018-01-04 23:00 | 286 | 284
2018-01-04 23:30 | 319 | 316
2018-01-05 | 307 | 304
2018-01-05 00:30 | 298 | 294
2018-01-05 01:00 | 290 | 287
2018-01-05 01:30 | 282 | 279
2018-01-05 02:00 | 278 | 274
2018-01-05 02:30 | 275 | 271
2018-01-05 03:00 | 272 | 269
2018-01-05 03:30 | 266 | 264
2018-01-05 04:00 | 264 | 261
2018-01-05 04:30 | 263 | 261
2018-01-05 05:00 | 263 | 260
2018-01-05 05:30 | 263 | 260
2018-01-05 06:00 | 267 | 264
2018-01-05 06:30 | 275 | 273
2018-01-05 07:00 | 281 | 279
2018-01-05 07:30 | 289 | 287
2018-01-05 08:00 | 301 | 298
2018-01-05 08:30 | 311 | 308
2018-01-05 09:00 | 319 | 316
2018-01-05 09:30 | 322 | 319
2018-01-05 10:00 | 311 | 308
2018-01-05 10:30 | 313 | 310
2018-01-05 11:00 | 325 | 322
2018-01-05 11:30 | 328 | 326
2018-01-05 12:00 | 329 | 327
2018-01-05 12:30 | 329 | 327
2018-01-05 13:00 | 320 | 318
2018-01-05 13:30 | 333 | 330
2018-01-05 14:00 | 331 | 328
2018-01-05 14:30 | 334 | 331
2018-01-05 15:00 | 333 | 331
2018-01-05 15:30 | 325 | 322
2018-01-05 16:00 | 326 | 323
2018-01-05 16:30 | 323 | 320
2018-01-05 17:00 | 319 | 315
2018-01-05 17:30 | 324 | 321
2018-01-05 18:00 | 334 | 331
2018-01-05 18:30 | 336 | 333
2018-01-05 19:00 | 338 | 335
2018-01-05 19:30 | 344 | 340
2018-01-05 20:00 | 340 | 337
2018-01-05 20:30 | 333 | 330
2018-01-05 21:00 | 323 | 320
2018-01-05 21:30 | 316 | 313
2018-01-05 22:00 | 307 | 304
2018-01-05 22:30 | 294 | 291
2018-01-05 23:00 | 283 | 281
2018-01-05 23:30 | 275 | 272
2018-01-06 | 266 | 264
2018-01-06 00:30 | 258 | 256
2018-01-06 01:00 | 253 | 250
2018-01-06 01:30 | 249 | 246
2018-01-06 02:00 | 244 | 242
2018-01-06 02:30 | 243 | 240
2018-01-06 03:00 | 239 | 236
2018-01-06 03:30 | 237 | 234
2018-01-06 04:00 | 235 | 232
2018-01-06 04:30 | 232 | 229
2018-01-06 05:00 | 232 | 229
2018-01-06 05:30 | 234 | 231
2018-01-06 06:00 | 235 | 232
2018-01-06 06:30 | 237 | 234
2018-01-06 07:00 | 238 | 235
2018-01-06 07:30 | 245 | 242
2018-01-06 08:00 | 253 | 250
2018-01-06 08:30 | 259 | 256
2018-01-06 09:00 | 259 | 256
2018-01-06 09:30 | 263 | 260
2018-01-06 10:00 | 255 | 252
2018-01-06 10:30 | 247 | 245
2018-01-06 11:00 | 247 | 244
2018-01-06 11:30 | 250 | 247
2018-01-06 12:00 | 255 | 252
2018-01-06 12:30 | 256 | 253
2018-01-06 13:00 | 258 | 255
2018-01-06 13:30 | 276 | 274
2018-01-06 14:00 | 284 | 282
2018-01-06 14:30 | 289 | 287
2018-01-06 15:00 | 293 | 291
2018-01-06 15:30 | 301 | 298
2018-01-06 16:00 | 306 | 303
2018-01-06 16:30 | 315 | 312
2018-01-06 17:00 | 329 | 324
2018-01-06 17:30 | 331 | 326
2018-01-06 18:00 | 341 | 336
2018-01-06 18:30 | 347 | 342
2018-01-06 19:00 | 351 | 347
2018-01-06 19:30 | 356 | 352
2018-01-06 20:00 | 360 | 354
2018-01-06 20:30 | 354 | 347
2018-01-06 21:00 | 346 | 338
2018-01-06 21:30 | 335 | 327
2018-01-06 22:00 | 325 | 318
2018-01-06 22:30 | 314 | 306
2018-01-06 23:00 | 304 | 295
2018-01-06 23:30 | 289 | 284
2018-01-07 | 280 | 276
2018-01-07 00:30 | 272 | 268
2018-01-07 01:00 | 265 | 261
2018-01-07 01:30 | 259 | 254
2018-01-07 02:00 | 254 | 250
2018-01-07 02:30 | 250 | 246
2018-01-07 03:00 | 247 | 243
2018-01-07 03:30 | 246 | 242
2018-01-07 04:00 | 244 | 239
2018-01-07 04:30 | 243 | 238
2018-01-07 05:00 | 243 | 238
2018-01-07 05:30 | 243 | 238
2018-01-07 06:00 | 243 | 238
2018-01-07 06:30 | 243 | 238
2018-01-07 07:00 | 245 | 240
2018-01-07 07:30 | 251 | 246
2018-01-07 08:00 | 250 | 246
2018-01-07 08:30 | 257 | 253
2018-01-07 09:00 | 262 | 258
2018-01-07 09:30 | 272 | 267
2018-01-07 10:00 | 261 | 257
2018-01-07 10:30 | 256 | 251
2018-01-07 11:00 | 257 | 252
2018-01-07 11:30 | 258 | 254
2018-01-07 12:00 | 256 | 252
2018-01-07 12:30 | 259 | 255
2018-01-07 13:00 | 260 | 255
2018-01-07 13:30 | 277 | 272
2018-01-07 14:00 | 279 | 275
2018-01-07 14:30 | 287 | 283
2018-01-07 15:00 | 292 | 288
2018-01-07 15:30 | 287 | 283
2018-01-07 16:00 | 288 | 284
2018-01-07 16:30 | 293 | 288
2018-01-07 17:00 | 301 | 297
2018-01-07 17:30 | 309 | 305
2018-01-07 18:00 | 320 | 316
2018-01-07 18:30 | 327 | 324
2018-01-07 19:00 | 336 | 332
2018-01-07 19:30 | 343 | 340
2018-01-07 20:00 | 355 | 352
2018-01-07 20:30 | 353 | 350
2018-01-07 21:00 | 345 | 341
2018-01-07 21:30 | 334 | 331
2018-01-07 22:00 | 322 | 319
2018-01-07 22:30 | 307 | 304
2018-01-07 23:00 | 295 | 292
2018-01-07 23:30 | 286 | 282
2018-01-08 | 278 | 274
2018-01-08 00:30 | 271 | 267
2018-01-08 01:00 | 264 | 259
2018-01-08 01:30 | 258 | 253
2018-01-08 02:00 | 254 | 250
2018-01-08 02:30 | 249 | 246
2018-01-08 03:00 | 245 | 242
2018-01-08 03:30 | 243 | 239
2018-01-08 04:00 | 243 | 239
2018-01-08 04:30 | 243 | 240
2018-01-08 05:00 | 244 | 240
2018-01-08 05:30 | 247 | 243
2018-01-08 06:00 | 250 | 247
2018-01-08 06:30 | 261 | 258
2018-01-08 07:00 | 272 | 269
2018-01-08 07:30 | 289 | 286
2018-01-08 08:00 | 295 | 292
2018-01-08 08:30 | 304 | 300
2018-01-08 09:00 | 308 | 304
2018-01-08 09:30 | 311 | 307
2018-01-08 10:00 | 298 | 294
2018-01-08 10:30 | 294 | 289
2018-01-08 11:00 | 291 | 286
2018-01-08 11:30 | 296 | 291
2018-01-08 12:00 | 300 | 295
2018-01-08 12:30 | 304 | 299
2018-01-08 13:00 | 280 | 275
2018-01-08 13:30 | 270 | 265
2018-01-08 14:00 | 249 | 244
2018-01-08 14:30 | 257 | 251
2018-01-08 15:00 | 242 | 236
2018-01-08 15:30 | 246 | 240
2018-01-08 16:00 | 234 | 228
2018-01-08 16:30 | 236 | 230
2018-01-08 17:00 | 242 | 236
2018-01-08 17:30 | 252 | 246
2018-01-08 18:00 | 265 | 260
2018-01-08 18:30 | 308 | 304
2018-01-08 19:00 | 321 | 317
2018-01-08 19:30 | 326 | 323
2018-01-08 20:00 | 325 | 322
2018-01-08 20:30 | 350 | 346
2018-01-08 21:00 | 346 | 342
2018-01-08 21:30 | 333 | 329
2018-01-08 22:00 | 319 | 315
2018-01-08 22:30 | 304 | 300
2018-01-08 23:00 | 291 | 287
2018-01-08 23:30 | 282 | 277
2018-01-09 | 274 | 269
2018-01-09 00:30 | 267 | 262
2018-01-09 01:00 | 259 | 255
2018-01-09 01:30 | 251 | 247
2018-01-09 02:00 | 247 | 243
2018-01-09 02:30 | 246 | 242
2018-01-09 03:00 | 243 | 239
2018-01-09 03:30 | 242 | 238
2018-01-09 04:00 | 241 | 238
2018-01-09 04:30 | 241 | 237
2018-01-09 05:00 | 240 | 236
2018-01-09 05:30 | 243 | 240
2018-01-09 06:00 | 246 | 242
2018-01-09 06:30 | 255 | 252
2018-01-09 07:00 | 268 | 265
2018-01-09 07:30 | 283 | 280
2018-01-09 08:00 | 290 | 287
2018-01-09 08:30 | 303 | 299
2018-01-09 09:00 | 305 | 301
2018-01-09 09:30 | 307 | 303
2018-01-09 10:00 | 294 | 290
2018-01-09 10:30 | 288 | 284
2018-01-09 11:00 | 287 | 282
2018-01-09 11:30 | 288 | 283
2018-01-09 12:00 | 291 | 286
2018-01-09 12:30 | 296 | 292
2018-01-09 13:00 | 302 | 298
2018-01-09 13:30 | 327 | 323
2018-01-09 14:00 | 331 | 327
2018-01-09 14:30 | 333 | 330
2018-01-09 15:00 | 333 | 329
2018-01-09 15:30 | 325 | 322
2018-01-09 16:00 | 325 | 322
2018-01-09 16:30 | 333 | 329
2018-01-09 17:00 | 326 | 322
2018-01-09 17:30 | 328 | 324
2018-01-09 18:00 | 345 | 341
2018-01-09 18:30 | 362 | 359
2018-01-09 19:00 | 373 | 370
2018-01-09 19:30 | 381 | 378
2018-01-09 20:00 | 383 | 380
2018-01-09 20:30 | 374 | 371
2018-01-09 21:00 | 360 | 357
2018-01-09 21:30 | 346 | 343
2018-01-09 22:00 | 331 | 328
2018-01-09 22:30 | 315 | 312
2018-01-09 23:00 | 301 | 297
2018-01-09 23:30 | 290 | 286
2018-01-10 | 280 | 276
2018-01-10 00:30 | 272 | 268
2018-01-10 01:00 | 265 | 262
2018-01-10 01:30 | 261 | 257
2018-01-10 02:00 | 257 | 253
2018-01-10 02:30 | 254 | 250
2018-01-10 03:00 | 250 | 246
2018-01-10 03:30 | 249 | 245
2018-01-10 04:00 | 249 | 245
2018-01-10 04:30 | 247 | 243
2018-01-10 05:00 | 249 | 245
2018-01-10 05:30 | 253 | 249
2018-01-10 06:00 | 257 | 253
2018-01-10 06:30 | 265 | 261
2018-01-10 07:00 | 272 | 269
2018-01-10 07:30 | 287 | 284
2018-01-10 08:00 | 299 | 296
2018-01-10 08:30 | 308 | 305
2018-01-10 09:00 | 313 | 309
2018-01-10 09:30 | 314 | 310
2018-01-10 10:00 | 307 | 304
2018-01-10 10:30 | 301 | 297
2018-01-10 11:00 | 298 | 295
2018-01-10 11:30 | 297 | 293
2018-01-10 12:00 | 302 | 298
2018-01-10 12:30 | 306 | 303
2018-01-10 13:00 | 312 | 308
2018-01-10 13:30 | 315 | 311
2018-01-10 14:00 | 317 | 314
2018-01-10 14:30 | 326 | 322
2018-01-10 15:00 | 332 | 328
2018-01-10 15:30 | 334 | 331
2018-01-10 16:00 | 339 | 336
2018-01-10 16:30 | 346 | 343
2018-01-10 17:00 | 350 | 346
2018-01-10 17:30 | 352 | 349
2018-01-10 18:00 | 357 | 354
2018-01-10 18:30 | 359 | 356
2018-01-10 19:00 | 367 | 364
2018-01-10 19:30 | 376 | 374
2018-01-10 20:00 | 378 | 375
2018-01-10 20:30 | 375 | 373
2018-01-10 21:00 | 363 | 361
2018-01-10 21:30 | 351 | 348
2018-01-10 22:00 | 337 | 334
2018-01-10 22:30 | 322 | 318
2018-01-10 23:00 | 307 | 303
2018-01-10 23:30 | 295 | 291
2018-01-11 | 284 | 281
2018-01-11 00:30 | 277 | 273
2018-01-11 01:00 | 271 | 267
2018-01-11 01:30 | 266 | 262
2018-01-11 02:00 | 263 | 259
2018-01-11 02:30 | 260 | 256
2018-01-11 03:00 | 259 | 254
2018-01-11 03:30 | 257 | 253
2018-01-11 04:00 | 245 | 240
2018-01-11 04:30 | 230 | 225
2018-01-11 05:00 | 227 | 222
2018-01-11 05:30 | 223 | 219
2018-01-11 06:00 | 214 | 210
2018-01-11 06:30 | 224 | 220
2018-01-11 07:00 | 235 | 231
2018-01-11 07:30 | 247 | 244
2018-01-11 08:00 | 254 | 251
2018-01-11 08:30 | 268 | 265
2018-01-11 09:00 | 268 | 266
2018-01-11 09:30 | 264 | 261
2018-01-11 10:00 | 254 | 252
2018-01-11 10:30 | 247 | 244
2018-01-11 11:00 | 254 | 251
2018-01-11 11:30 | 259 | 256
2018-01-11 12:00 | 255 | 252
2018-01-11 12:30 | 250 | 246
2018-01-11 13:00 | 249 | 246
2018-01-11 13:30 | 265 | 261
2018-01-11 14:00 | 247 | 243
2018-01-11 14:30 | 234 | 231
2018-01-11 15:00 | 233 | 230
2018-01-11 15:30 | 225 | 221
2018-01-11 16:00 | 211 | 207
2018-01-11 16:30 | 235 | 231
2018-01-11 17:00 | 237 | 234
2018-01-11 17:30 | 239 | 235
2018-01-11 18:00 | 263 | 260
2018-01-11 18:30 | 277 | 274
2018-01-11 19:00 | 281 | 278
2018-01-11 19:30 | 291 | 288
2018-01-11 20:00 | 285 | 282
2018-01-11 20:30 | 319 | 316
2018-01-11 21:00 | 314 | 310
2018-01-11 21:30 | 299 | 295
2018-01-11 22:00 | 303 | 299
2018-01-11 22:30 | 295 | 291
2018-01-11 23:00 | 280 | 276
2018-01-11 23:30 | 272 | 268
2018-01-12 | 269 | 265
2018-01-12 00:30 | 263 | 259
2018-01-12 01:00 | 256 | 252
2018-01-12 01:30 | 253 | 249
2018-01-12 02:00 | 249 | 245
2018-01-12 02:30 | 246 | 242
2018-01-12 03:00 | 246 | 242
2018-01-12 03:30 | 246 | 242
2018-01-12 04:00 | 246 | 242
2018-01-12 04:30 | 246 | 242
2018-01-12 05:00 | 246 | 242
2018-01-12 05:30 | 254 | 251
2018-01-12 06:00 | 255 | 252
2018-01-12 06:30 | 268 | 264
2018-01-12 07:00 | 278 | 275
2018-01-12 07:30 | 287 | 284
2018-01-12 08:00 | 297 | 295
2018-01-12 08:30 | 290 | 286
2018-01-12 09:00 | 257 | 253
2018-01-12 09:30 | 265 | 261
2018-01-12 10:00 | 256 | 252
2018-01-12 10:30 | 252 | 248
2018-01-12 11:00 | 251 | 247
2018-01-12 11:30 | 245 | 240
2018-01-12 12:00 | 226 | 222
2018-01-12 12:30 | 229 | 224
2018-01-12 13:00 | 217 | 212
2018-01-12 13:30 | 229 | 224
2018-01-12 14:00 | 230 | 225
2018-01-12 14:30 | 224 | 218
2018-01-12 15:00 | 226 | 221
2018-01-12 15:30 | 218 | 214
2018-01-12 16:00 | 180 | 176
2018-01-12 16:30 | 149 | 145
2018-01-12 17:00 | 155 | 152
2018-01-12 17:30 | 149 | 146
2018-01-12 18:00 | 178 | 176
2018-01-12 18:30 | 241 | 239
2018-01-12 19:00 | 260 | 258
2018-01-12 19:30 | 280 | 279
2018-01-12 20:00 | 283 | 281
2018-01-12 20:30 | 283 | 282
2018-01-12 21:00 | 279 | 277
2018-01-12 21:30 | 268 | 267
2018-01-12 22:00 | 257 | 255
2018-01-12 22:30 | 229 | 228
2018-01-12 23:00 | 225 | 223
2018-01-12 23:30 | 218 | 216
2018-01-13 | 208 | 207
2018-01-13 00:30 | 200 | 199
2018-01-13 01:00 | 192 | 190
2018-01-13 01:30 | 187 | 185
2018-01-13 02:00 | 184 | 183
2018-01-13 02:30 | 180 | 178
2018-01-13 03:00 | 177 | 175
2018-01-13 03:30 | 174 | 172
2018-01-13 04:00 | 173 | 171
2018-01-13 04:30 | 172 | 170
2018-01-13 05:00 | 171 | 169
2018-01-13 05:30 | 170 | 168
2018-01-13 06:00 | 168 | 166
2018-01-13 06:30 | 172 | 170
2018-01-13 07:00 | 173 | 171
2018-01-13 07:30 | 176 | 174
2018-01-13 08:00 | 184 | 182
2018-01-13 08:30 | 192 | 191
2018-01-13 09:00 | 198 | 197
2018-01-13 09:30 | 204 | 202
2018-01-13 10:00 | 195 | 194
2018-01-13 10:30 | 189 | 188
2018-01-13 11:00 | 189 | 187
2018-01-13 11:30 | 191 | 190
2018-01-13 12:00 | 183 | 181
2018-01-13 12:30 | 172 | 171
2018-01-13 13:00 | 176 | 174
2018-01-13 13:30 | 206 | 204
2018-01-13 14:00 | 206 | 204
2018-01-13 14:30 | 198 | 196
2018-01-13 15:00 | 209 | 207
2018-01-13 15:30 | 218 | 216
2018-01-13 16:00 | 222 | 220
2018-01-13 16:30 | 183 | 180
2018-01-13 17:00 | 198 | 196
2018-01-13 17:30 | 213 | 211
2018-01-13 18:00 | 224 | 222
2018-01-13 18:30 | 233 | 231
2018-01-13 19:00 | 238 | 236
2018-01-13 19:30 | 285 | 283
2018-01-13 20:00 | 335 | 333
2018-01-13 20:30 | 328 | 326
2018-01-13 21:00 | 334 | 332
2018-01-13 21:30 | 334 | 331
2018-01-13 22:00 | 323 | 321
2018-01-13 22:30 | 309 | 306
2018-01-13 23:00 | 296 | 294
2018-01-13 23:30 | 286 | 283
2018-01-14 | 277 | 275
2018-01-14 00:30 | 268 | 266
2018-01-14 01:00 | 263 | 261
2018-01-14 01:30 | 259 | 257
2018-01-14 02:00 | 253 | 251
2018-01-14 02:30 | 250 | 248
2018-01-14 03:00 | 247 | 245
2018-01-14 03:30 | 247 | 245
2018-01-14 04:00 | 245 | 243
2018-01-14 04:30 | 244 | 242
2018-01-14 05:00 | 243 | 241
2018-01-14 05:30 | 243 | 241
2018-01-14 06:00 | 240 | 238
2018-01-14 06:30 | 240 | 238
2018-01-14 07:00 | 243 | 241
2018-01-14 07:30 | 247 | 245
2018-01-14 08:00 | 252 | 250
2018-01-14 08:30 | 256 | 254
2018-01-14 09:00 | 259 | 257
2018-01-14 09:30 | 261 | 258
2018-01-14 10:00 | 253 | 251
2018-01-14 10:30 | 248 | 246
2018-01-14 11:00 | 251 | 250
2018-01-14 11:30 | 257 | 256
2018-01-14 12:00 | 260 | 258
2018-01-14 12:30 | 271 | 269
2018-01-14 13:00 | 271 | 268
2018-01-14 13:30 | 280 | 278
2018-01-14 14:00 | 291 | 289
2018-01-14 14:30 | 278 | 276
2018-01-14 15:00 | 264 | 262
2018-01-14 15:30 | 239 | 238
2018-01-14 16:00 | 247 | 246
2018-01-14 16:30 | 248 | 246
2018-01-14 17:00 | 256 | 255
2018-01-14 17:30 | 266 | 265
2018-01-14 18:00 | 273 | 271
2018-01-14 18:30 | 312 | 311
2018-01-14 19:00 | 327 | 326
2018-01-14 19:30 | 334 | 332
2018-01-14 20:00 | 368 | 366
2018-01-14 20:30 | 377 | 375
2018-01-14 21:00 | 368 | 366
2018-01-14 21:30 | 354 | 351
2018-01-14 22:00 | 339 | 336
2018-01-14 22:30 | 321 | 318
2018-01-14 23:00 | 307 | 304
2018-01-14 23:30 | 297 | 294
2018-01-15 | 286 | 283
2018-01-15 00:30 | 276 | 273
2018-01-15 01:00 | 270 | 267
2018-01-15 01:30 | 263 | 261
2018-01-15 02:00 | 260 | 257
2018-01-15 02:30 | 256 | 254
2018-01-15 03:00 | 256 | 254
2018-01-15 03:30 | 255 | 252
2018-01-15 04:00 | 254 | 252
2018-01-15 04:30 | 255 | 252
2018-01-15 05:00 | 257 | 254
2018-01-15 05:30 | 260 | 257
2018-01-15 06:00 | 265 | 263
2018-01-15 06:30 | 278 | 275
2018-01-15 07:00 | 293 | 291
2018-01-15 07:30 | 308 | 307
2018-01-15 08:00 | 321 | 319
2018-01-15 08:30 | 334 | 331
2018-01-15 09:00 | 343 | 340
2018-01-15 09:30 | 341 | 338
2018-01-15 10:00 | 334 | 331
2018-01-15 10:30 | 326 | 322
2018-01-15 11:00 | 326 | 323
2018-01-15 11:30 | 329 | 325
2018-01-15 12:00 | 338 | 335
2018-01-15 12:30 | 353 | 349
2018-01-15 13:00 | 360 | 355
2018-01-15 13:30 | 371 | 366
2018-01-15 14:00 | 378 | 374
2018-01-15 14:30 | 390 | 386
2018-01-15 15:00 | 400 | 396
2018-01-15 15:30 | 403 | 399
2018-01-15 16:00 | 385 | 381
2018-01-15 16:30 | 376 | 371
2018-01-15 17:00 | 367 | 362
2018-01-15 17:30 | 358 | 353
2018-01-15 18:00 | 368 | 364
2018-01-15 18:30 | 374 | 369
2018-01-15 19:00 | 377 | 373
2018-01-15 19:30 | 379 | 374
2018-01-15 20:00 | 378 | 373
2018-01-15 20:30 | 368 | 363
2018-01-15 21:00 | 360 | 355
2018-01-15 21:30 | 341 | 336
2018-01-15 22:00 | 310 | 307
2018-01-15 22:30 | 287 | 285
2018-01-15 23:00 | 273 | 270
2018-01-15 23:30 | 262 | 259
2018-01-16 | 253 | 250
2018-01-16 00:30 | 246 | 244
2018-01-16 01:00 | 238 | 236
2018-01-16 01:30 | 232 | 230
2018-01-16 02:00 | 229 | 228
2018-01-16 02:30 | 226 | 224
2018-01-16 03:00 | 218 | 216
2018-01-16 03:30 | 216 | 214
2018-01-16 04:00 | 239 | 237
2018-01-16 04:30 | 239 | 238
2018-01-16 05:00 | 242 | 241
2018-01-16 05:30 | 244 | 242
2018-01-16 06:00 | 252 | 250
2018-01-16 06:30 | 261 | 259
2018-01-16 07:00 | 270 | 269
2018-01-16 07:30 | 277 | 276
2018-01-16 08:00 | 294 | 293
2018-01-16 08:30 | 301 | 300
2018-01-16 09:00 | 300 | 299
2018-01-16 09:30 | 305 | 304
2018-01-16 10:00 | 298 | 297
2018-01-16 10:30 | 289 | 288
2018-01-16 11:00 | 284 | 282
2018-01-16 11:30 | 282 | 281
2018-01-16 12:00 | 287 | 285
2018-01-16 12:30 | 296 | 295
2018-01-16 13:00 | 292 | 291
2018-01-16 13:30 | 294 | 292
2018-01-16 14:00 | 285 | 284
2018-01-16 14:30 | 285 | 284
2018-01-16 15:00 | 287 | 285
2018-01-16 15:30 | 297 | 295
2018-01-16 16:00 | 305 | 304
2018-01-16 16:30 | 316 | 315
2018-01-16 17:00 | 319 | 318
2018-01-16 17:30 | 312 | 310
2018-01-16 18:00 | 331 | 329
2018-01-16 18:30 | 341 | 339
2018-01-16 19:00 | 346 | 344
2018-01-16 19:30 | 350 | 348
2018-01-16 20:00 | 351 | 349
2018-01-16 20:30 | 353 | 351
2018-01-16 21:00 | 343 | 341
2018-01-16 21:30 | 331 | 328
2018-01-16 22:00 | 321 | 319
2018-01-16 22:30 | 305 | 302
2018-01-16 23:00 | 290 | 287
2018-01-16 23:30 | 279 | 276
2018-01-17 | 271 | 269
2018-01-17 00:30 | 263 | 261
2018-01-17 01:00 | 255 | 252
2018-01-17 01:30 | 252 | 249
2018-01-17 02:00 | 249 | 246
2018-01-17 02:30 | 247 | 244
2018-01-17 03:00 | 247 | 244
2018-01-17 03:30 | 247 | 244
2018-01-17 04:00 | 247 | 244
2018-01-17 04:30 | 244 | 241
2018-01-17 05:00 | 244 | 241
2018-01-17 05:30 | 248 | 246
2018-01-17 06:00 | 253 | 250
2018-01-17 06:30 | 266 | 263
2018-01-17 07:00 | 278 | 275
2018-01-17 07:30 | 294 | 293
2018-01-17 08:00 | 305 | 303
2018-01-17 08:30 | 310 | 309
2018-01-17 09:00 | 306 | 304
2018-01-17 09:30 | 298 | 296
2018-01-17 10:00 | 260 | 258
2018-01-17 10:30 | 246 | 244
2018-01-17 11:00 | 240 | 238
2018-01-17 11:30 | 239 | 236
2018-01-17 12:00 | 244 | 242
2018-01-17 12:30 | 243 | 241
2018-01-17 13:00 | 245 | 243
2018-01-17 13:30 | 263 | 261
2018-01-17 14:00 | 255 | 252
2018-01-17 14:30 | 260 | 258
2018-01-17 15:00 | 263 | 260
2018-01-17 15:30 | 267 | 265
2018-01-17 16:00 | 272 | 270
2018-01-17 16:30 | 275 | 272
2018-01-17 17:00 | 275 | 272
2018-01-17 17:30 | 273 | 270
2018-01-17 18:00 | 276 | 273
2018-01-17 18:30 | 278 | 275
2018-01-17 19:00 | 286 | 284
2018-01-17 19:30 | 293 | 290
2018-01-17 20:00 | 293 | 291
2018-01-17 20:30 | 292 | 290
2018-01-17 21:00 | 288 | 286
2018-01-17 21:30 | 281 | 278
2018-01-17 22:00 | 267 | 264
2018-01-17 22:30 | 256 | 254
2018-01-17 23:00 | 255 | 253
2018-01-17 23:30 | 248 | 245
2018-01-18 | 241 | 238
2018-01-18 00:30 | 234 | 232
2018-01-18 01:00 | 227 | 225
2018-01-18 01:30 | 223 | 220
2018-01-18 02:00 | 220 | 218
2018-01-18 02:30 | 218 | 216
2018-01-18 03:00 | 218 | 215
2018-01-18 03:30 | 227 | 225
2018-01-18 04:00 | 229 | 227
2018-01-18 04:30 | 229 | 227
2018-01-18 05:00 | 231 | 229
2018-01-18 05:30 | 234 | 232
2018-01-18 06:00 | 231 | 229
2018-01-18 06:30 | 243 | 241
2018-01-18 07:00 | 255 | 253
2018-01-18 07:30 | 268 | 266
2018-01-18 08:00 | 277 | 276
2018-01-18 08:30 | 291 | 289
2018-01-18 09:00 | 291 | 289
2018-01-18 09:30 | 287 | 285
2018-01-18 10:00 | 283 | 281
2018-01-18 10:30 | 274 | 272
2018-01-18 11:00 | 269 | 267
2018-01-18 11:30 | 260 | 258
2018-01-18 12:00 | 266 | 265
2018-01-18 12:30 | 260 | 258
2018-01-18 13:00 | 265 | 264
2018-01-18 13:30 | 288 | 286
2018-01-18 14:00 | 280 | 278
2018-01-18 14:30 | 281 | 278
2018-01-18 15:00 | 271 | 269
2018-01-18 15:30 | 283 | 281
2018-01-18 16:00 | 266 | 263
2018-01-18 16:30 | 247 | 244
2018-01-18 17:00 | 245 | 241
2018-01-18 17:30 | 244 | 241
2018-01-18 18:00 | 266 | 263
2018-01-18 18:30 | 276 | 274
2018-01-18 19:00 | 280 | 277
2018-01-18 19:30 | 281 | 279
2018-01-18 20:00 | 278 | 276
2018-01-18 20:30 | 268 | 265
2018-01-18 21:00 | 258 | 255
2018-01-18 21:30 | 302 | 300
2018-01-18 22:00 | 296 | 294
2018-01-18 22:30 | 279 | 276
2018-01-18 23:00 | 261 | 258
2018-01-18 23:30 | 248 | 246
2018-01-19 | 242 | 240
2018-01-19 00:30 | 235 | 233
2018-01-19 01:00 | 229 | 227
2018-01-19 01:30 | 226 | 225
2018-01-19 02:00 | 222 | 220
2018-01-19 02:30 | 220 | 218
2018-01-19 03:00 | 227 | 225
2018-01-19 03:30 | 228 | 226
2018-01-19 04:00 | 225 | 223
2018-01-19 04:30 | 225 | 223
2018-01-19 05:00 | 228 | 226
2018-01-19 05:30 | 231 | 229
2018-01-19 06:00 | 236 | 234
2018-01-19 06:30 | 249 | 246
2018-01-19 07:00 | 235 | 232
2018-01-19 07:30 | 231 | 228
2018-01-19 08:00 | 240 | 238
2018-01-19 08:30 | 237 | 235
2018-01-19 09:00 | 217 | 215
2018-01-19 09:30 | 215 | 213
2018-01-19 10:00 | 195 | 191
2018-01-19 10:30 | 193 | 190
2018-01-19 11:00 | 189 | 186
2018-01-19 11:30 | 182 | 179
2018-01-19 12:00 | 160 | 157
2018-01-19 12:30 | 163 | 160
2018-01-19 13:00 | 164 | 161
2018-01-19 13:30 | 145 | 141
2018-01-19 14:00 | 135 | 132
2018-01-19 14:30 | 140 | 137
2018-01-19 15:00 | 139 | 136
2018-01-19 15:30 | 139 | 136
2018-01-19 16:00 | 132 | 129
2018-01-19 16:30 | 138 | 135
2018-01-19 17:00 | 146 | 143
2018-01-19 17:30 | 145 | 142
2018-01-19 18:00 | 147 | 144
2018-01-19 18:30 | 149 | 146
2018-01-19 19:00 | 159 | 157
2018-01-19 19:30 | 166 | 164
2018-01-19 20:00 | 167 | 165
2018-01-19 20:30 | 170 | 167
2018-01-19 21:00 | 162 | 160
2018-01-19 21:30 | 153 | 151
2018-01-19 22:00 | 143 | 140
2018-01-19 22:30 | 175 | 173
2018-01-19 23:00 | 218 | 216
2018-01-19 23:30 | 225 | 223
2018-01-20 | 215 | 212
2018-01-20 00:30 | 210 | 208
2018-01-20 01:00 | 205 | 203
2018-01-20 01:30 | 197 | 194
2018-01-20 02:00 | 192 | 189
2018-01-20 02:30 | 191 | 188
2018-01-20 03:00 | 188 | 185
2018-01-20 03:30 | 185 | 182
2018-01-20 04:00 | 183 | 180
2018-01-20 04:30 | 197 | 194
2018-01-20 05:00 | 204 | 202
2018-01-20 05:30 | 205 | 203
2018-01-20 06:00 | 206 | 204
2018-01-20 06:30 | 208 | 206
2018-01-20 07:00 | 209 | 206
2018-01-20 07:30 | 209 | 207
2018-01-20 08:00 | 218 | 215
2018-01-20 08:30 | 227 | 225
2018-01-20 09:00 | 230 | 228
2018-01-20 09:30 | 231 | 229
2018-01-20 10:00 | 232 | 230
2018-01-20 10:30 | 225 | 223
2018-01-20 11:00 | 225 | 222
2018-01-20 11:30 | 225 | 223
2018-01-20 12:00 | 225 | 222
2018-01-20 12:30 | 227 | 225
2018-01-20 13:00 | 222 | 220
2018-01-20 13:30 | 228 | 226
2018-01-20 14:00 | 229 | 227
2018-01-20 14:30 | 233 | 231
2018-01-20 15:00 | 237 | 235
2018-01-20 15:30 | 240 | 238
2018-01-20 16:00 | 246 | 244
2018-01-20 16:30 | 252 | 250
2018-01-20 17:00 | 262 | 260
2018-01-20 17:30 | 274 | 272
2018-01-20 18:00 | 282 | 280
2018-01-20 18:30 | 286 | 285
2018-01-20 19:00 | 290 | 288
2018-01-20 19:30 | 295 | 293
2018-01-20 20:00 | 293 | 291
2018-01-20 20:30 | 295 | 292
2018-01-20 21:00 | 290 | 287
2018-01-20 21:30 | 282 | 279
2018-01-20 22:00 | 275 | 272
2018-01-20 22:30 | 264 | 261
2018-01-20 23:00 | 252 | 250
2018-01-20 23:30 | 243 | 240
2018-01-21 | 235 | 232
2018-01-21 00:30 | 240 | 237
2018-01-21 01:00 | 240 | 237
2018-01-21 01:30 | 234 | 231
2018-01-21 02:00 | 232 | 229
2018-01-21 02:30 | 229 | 226
2018-01-21 03:00 | 225 | 222
2018-01-21 03:30 | 225 | 222
2018-01-21 04:00 | 222 | 219
2018-01-21 04:30 | 221 | 219
2018-01-21 05:00 | 222 | 219
2018-01-21 05:30 | 225 | 222
2018-01-21 06:00 | 217 | 215
2018-01-21 06:30 | 212 | 209
2018-01-21 07:00 | 218 | 215
2018-01-21 07:30 | 223 | 220
2018-01-21 08:00 | 228 | 225
2018-01-21 08:30 | 233 | 231
2018-01-21 09:00 | 235 | 232
2018-01-21 09:30 | 236 | 233
2018-01-21 10:00 | 233 | 230
2018-01-21 10:30 | 216 | 213
2018-01-21 11:00 | 218 | 215
2018-01-21 11:30 | 219 | 217
2018-01-21 12:00 | 220 | 217
2018-01-21 12:30 | 218 | 215
2018-01-21 13:00 | 217 | 215
2018-01-21 13:30 | 232 | 230
2018-01-21 14:00 | 237 | 235
2018-01-21 14:30 | 241 | 238
2018-01-21 15:00 | 245 | 243
2018-01-21 15:30 | 255 | 253
2018-01-21 16:00 | 261 | 259
2018-01-21 16:30 | 264 | 262
2018-01-21 17:00 | 267 | 265
2018-01-21 17:30 | 274 | 272
2018-01-21 18:00 | 284 | 282
2018-01-21 18:30 | 294 | 291
2018-01-21 19:00 | 300 | 298
2018-01-21 19:30 | 308 | 306
2018-01-21 20:00 | 312 | 310
2018-01-21 20:30 | 317 | 314
2018-01-21 21:00 | 306 | 304
2018-01-21 21:30 | 298 | 295
2018-01-21 22:00 | 295 | 292
2018-01-21 22:30 | 286 | 282
2018-01-21 23:00 | 273 | 270
2018-01-21 23:30 | 262 | 259
2018-01-22 | 255 | 252
2018-01-22 00:30 | 249 | 246
2018-01-22 01:00 | 247 | 243
2018-01-22 01:30 | 243 | 239
2018-01-22 02:00 | 238 | 234
2018-01-22 02:30 | 236 | 233
2018-01-22 03:00 | 233 | 230
2018-01-22 03:30 | 233 | 230
2018-01-22 04:00 | 233 | 230
2018-01-22 04:30 | 234 | 231
2018-01-22 05:00 | 236 | 233
2018-01-22 05:30 | 225 | 222
2018-01-22 06:00 | 209 | 206
2018-01-22 06:30 | 224 | 221
2018-01-22 07:00 | 241 | 238
2018-01-22 07:30 | 259 | 257
2018-01-22 08:00 | 264 | 262
2018-01-22 08:30 | 246 | 244
2018-01-22 09:00 | 227 | 225
2018-01-22 09:30 | 234 | 231
2018-01-22 10:00 | 218 | 215
2018-01-22 10:30 | 213 | 210
2018-01-22 11:00 | 221 | 218
2018-01-22 11:30 | 216 | 214
2018-01-22 12:00 | 216 | 213
2018-01-22 12:30 | 217 | 214
2018-01-22 13:00 | 212 | 209
2018-01-22 13:30 | 211 | 208
2018-01-22 14:00 | 210 | 207
2018-01-22 14:30 | 215 | 211
2018-01-22 15:00 | 218 | 215
2018-01-22 15:30 | 218 | 215
2018-01-22 16:00 | 205 | 201
2018-01-22 16:30 | 218 | 215
2018-01-22 17:00 | 228 | 225
2018-01-22 17:30 | 237 | 234
2018-01-22 18:00 | 241 | 238
2018-01-22 18:30 | 246 | 243
2018-01-22 19:00 | 254 | 252
2018-01-22 19:30 | 261 | 258
2018-01-22 20:00 | 265 | 262
2018-01-22 20:30 | 276 | 274
2018-01-22 21:00 | 272 | 269
2018-01-22 21:30 | 261 | 259
2018-01-22 22:00 | 247 | 244
2018-01-22 22:30 | 231 | 228
2018-01-22 23:00 | 219 | 215
2018-01-22 23:30 | 208 | 205
2018-01-23 | 199 | 196
2018-01-23 00:30 | 193 | 190
2018-01-23 01:00 | 184 | 182
2018-01-23 01:30 | 181 | 178
2018-01-23 02:00 | 176 | 174
2018-01-23 02:30 | 173 | 171
2018-01-23 03:00 | 171 | 169
2018-01-23 03:30 | 170 | 169
2018-01-23 04:00 | 170 | 169
2018-01-23 04:30 | 171 | 170
2018-01-23 05:00 | 174 | 172
2018-01-23 05:30 | 179 | 177
2018-01-23 06:00 | 185 | 184
2018-01-23 06:30 | 204 | 202
2018-01-23 07:00 | 217 | 214
2018-01-23 07:30 | 234 | 230
2018-01-23 08:00 | 237 | 234
2018-01-23 08:30 | 241 | 238
2018-01-23 09:00 | 244 | 241
2018-01-23 09:30 | 245 | 242
2018-01-23 10:00 | 231 | 229
2018-01-23 10:30 | 220 | 218
2018-01-23 11:00 | 228 | 225
2018-01-23 11:30 | 228 | 224
2018-01-23 12:00 | 223 | 219
2018-01-23 12:30 | 232 | 228
2018-01-23 13:00 | 234 | 230
2018-01-23 13:30 | 245 | 241
2018-01-23 14:00 | 254 | 250
2018-01-23 14:30 | 258 | 255
2018-01-23 15:00 | 260 | 256
2018-01-23 15:30 | 253 | 249
2018-01-23 16:00 | 210 | 205
2018-01-23 16:30 | 208 | 203
2018-01-23 17:00 | 215 | 209
2018-01-23 17:30 | 214 | 209
2018-01-23 18:00 | 216 | 211
2018-01-23 18:30 | 222 | 217
2018-01-23 19:00 | 234 | 230
2018-01-23 19:30 | 250 | 248
2018-01-23 20:00 | 285 | 282
2018-01-23 20:30 | 285 | 282
2018-01-23 21:00 | 274 | 271
2018-01-23 21:30 | 261 | 258
2018-01-23 22:00 | 246 | 244
2018-01-23 22:30 | 231 | 228
2018-01-23 23:00 | 219 | 216
2018-01-23 23:30 | 209 | 205
2018-01-24 | 200 | 198
2018-01-24 00:30 | 192 | 191
2018-01-24 01:00 | 187 | 186
2018-01-24 01:30 | 184 | 182
2018-01-24 02:00 | 178 | 177
2018-01-24 02:30 | 177 | 176
2018-01-24 03:00 | 177 | 176
2018-01-24 03:30 | 177 | 176
2018-01-24 04:00 | 176 | 175
2018-01-24 04:30 | 176 | 175
2018-01-24 05:00 | 176 | 175
2018-01-24 05:30 | 181 | 180
2018-01-24 06:00 | 189 | 188
2018-01-24 06:30 | 205 | 203
2018-01-24 07:00 | 219 | 218
2018-01-24 07:30 | 233 | 232
2018-01-24 08:00 | 235 | 234
2018-01-24 08:30 | 237 | 236
2018-01-24 09:00 | 239 | 238
2018-01-24 09:30 | 241 | 239
2018-01-24 10:00 | 232 | 230
2018-01-24 10:30 | 228 | 226
2018-01-24 11:00 | 229 | 228
2018-01-24 11:30 | 231 | 229
2018-01-24 12:00 | 234 | 233
2018-01-24 12:30 | 239 | 237
2018-01-24 13:00 | 225 | 224
2018-01-24 13:30 | 207 | 205
2018-01-24 14:00 | 206 | 204
2018-01-24 14:30 | 208 | 206
2018-01-24 15:00 | 206 | 204
2018-01-24 15:30 | 180 | 178
2018-01-24 16:00 | 180 | 178
2018-01-24 16:30 | 185 | 183
2018-01-24 17:00 | 194 | 192
2018-01-24 17:30 | 211 | 209
2018-01-24 18:00 | 214 | 212
2018-01-24 18:30 | 222 | 221
2018-01-24 19:00 | 232 | 230
2018-01-24 19:30 | 235 | 233
2018-01-24 20:00 | 264 | 263
2018-01-24 20:30 | 252 | 250
2018-01-24 21:00 | 239 | 238
2018-01-24 21:30 | 222 | 220
2018-01-24 22:00 | 211 | 209
2018-01-24 22:30 | 194 | 192
2018-01-24 23:00 | 182 | 180
2018-01-24 23:30 | 198 | 197
2018-01-25 | 231 | 230
2018-01-25 00:30 | 251 | 250
2018-01-25 01:00 | 254 | 252
2018-01-25 01:30 | 249 | 247
2018-01-25 02:00 | 245 | 244
2018-01-25 02:30 | 243 | 242
2018-01-25 03:00 | 242 | 240
2018-01-25 03:30 | 242 | 240
2018-01-25 04:00 | 242 | 240
2018-01-25 04:30 | 242 | 240
2018-01-25 05:00 | 243 | 242
2018-01-25 05:30 | 248 | 247
2018-01-25 06:00 | 240 | 239
2018-01-25 06:30 | 251 | 250
2018-01-25 07:00 | 252 | 250
2018-01-25 07:30 | 251 | 249
2018-01-25 08:00 | 257 | 256
2018-01-25 08:30 | 260 | 258
2018-01-25 09:00 | 260 | 258
2018-01-25 09:30 | 259 | 258
2018-01-25 10:00 | 259 | 257
2018-01-25 10:30 | 252 | 250
2018-01-25 11:00 | 259 | 257
2018-01-25 11:30 | 255 | 253
2018-01-25 12:00 | 247 | 245
2018-01-25 12:30 | 255 | 254
2018-01-25 13:00 | 268 | 267
2018-01-25 13:30 | 269 | 267
2018-01-25 14:00 | 272 | 270
2018-01-25 14:30 | 269 | 267
2018-01-25 15:00 | 261 | 259
2018-01-25 15:30 | 245 | 243
2018-01-25 16:00 | 244 | 242
2018-01-25 16:30 | 244 | 242
2018-01-25 17:00 | 256 | 254
2018-01-25 17:30 | 261 | 260
2018-01-25 18:00 | 271 | 269
2018-01-25 18:30 | 272 | 270
2018-01-25 19:00 | 275 | 274
2018-01-25 19:30 | 302 | 301
2018-01-25 20:00 | 303 | 302
2018-01-25 20:30 | 292 | 291
2018-01-25 21:00 | 283 | 282
2018-01-25 21:30 | 271 | 269
2018-01-25 22:00 | 261 | 259
2018-01-25 22:30 | 263 | 261
2018-01-25 23:00 | 254 | 252
2018-01-25 23:30 | 244 | 242
2018-01-26 | 233 | 231
2018-01-26 00:30 | 227 | 225
2018-01-26 01:00 | 222 | 220
2018-01-26 01:30 | 215 | 214
2018-01-26 02:00 | 210 | 209
2018-01-26 02:30 | 209 | 207
2018-01-26 03:00 | 206 | 205
2018-01-26 03:30 | 205 | 203
2018-01-26 04:00 | 203 | 201
2018-01-26 04:30 | 194 | 193
2018-01-26 05:00 | 197 | 196
2018-01-26 05:30 | 200 | 199
2018-01-26 06:00 | 201 | 200
2018-01-26 06:30 | 208 | 206
2018-01-26 07:00 | 212 | 210
2018-01-26 07:30 | 206 | 205
2018-01-26 08:00 | 209 | 208
2018-01-26 08:30 | 217 | 216
2018-01-26 09:00 | 222 | 220
2018-01-26 09:30 | 223 | 222
2018-01-26 10:00 | 222 | 221
2018-01-26 10:30 | 228 | 227
2018-01-26 11:00 | 216 | 214
2018-01-26 11:30 | 208 | 206
2018-01-26 12:00 | 195 | 193
2018-01-26 12:30 | 187 | 186
2018-01-26 13:00 | 197 | 196
2018-01-26 13:30 | 197 | 196
2018-01-26 14:00 | 189 | 187
2018-01-26 14:30 | 194 | 193
2018-01-26 15:00 | 202 | 201
2018-01-26 15:30 | 208 | 207
2018-01-26 16:00 | 212 | 211
2018-01-26 16:30 | 216 | 214
2018-01-26 17:00 | 224 | 222
2018-01-26 17:30 | 227 | 225
2018-01-26 18:00 | 231 | 230
2018-01-26 18:30 | 237 | 235
2018-01-26 19:00 | 244 | 243
2018-01-26 19:30 | 278 | 277
2018-01-26 20:00 | 278 | 277
2018-01-26 20:30 | 273 | 271
2018-01-26 21:00 | 266 | 264
2018-01-26 21:30 | 258 | 257
2018-01-26 22:00 | 250 | 249
2018-01-26 22:30 | 247 | 246
2018-01-26 23:00 | 240 | 238
2018-01-26 23:30 | 230 | 228
2018-01-27 | 222 | 220
2018-01-27 00:30 | 214 | 213
2018-01-27 01:00 | 210 | 208
2018-01-27 01:30 | 204 | 203
2018-01-27 02:00 | 198 | 196
2018-01-27 02:30 | 197 | 195
2018-01-27 03:00 | 193 | 191
2018-01-27 03:30 | 193 | 191
2018-01-27 04:00 | 191 | 189
2018-01-27 04:30 | 190 | 188
2018-01-27 05:00 | 190 | 188
2018-01-27 05:30 | 190 | 188
2018-01-27 06:00 | 192 | 190
2018-01-27 06:30 | 194 | 192
2018-01-27 07:00 | 195 | 193
2018-01-27 07:30 | 190 | 188
2018-01-27 08:00 | 192 | 190
2018-01-27 08:30 | 205 | 203
2018-01-27 09:00 | 212 | 210
2018-01-27 09:30 | 218 | 215
2018-01-27 10:00 | 216 | 214
2018-01-27 10:30 | 215 | 212
2018-01-27 11:00 | 213 | 210
2018-01-27 11:30 | 214 | 211
2018-01-27 12:00 | 213 | 211
2018-01-27 12:30 | 216 | 213
2018-01-27 13:00 | 216 | 214
2018-01-27 13:30 | 213 | 210
2018-01-27 14:00 | 214 | 211
2018-01-27 14:30 | 220 | 217
2018-01-27 15:00 | 224 | 221
2018-01-27 15:30 | 210 | 208
2018-01-27 16:00 | 219 | 217
2018-01-27 16:30 | 225 | 223
2018-01-27 17:00 | 231 | 229
2018-01-27 17:30 | 243 | 241
2018-01-27 18:00 | 251 | 249
2018-01-27 18:30 | 282 | 280
2018-01-27 19:00 | 288 | 286
2018-01-27 19:30 | 297 | 295
2018-01-27 20:00 | 300 | 298
2018-01-27 20:30 | 303 | 301
2018-01-27 21:00 | 301 | 300
2018-01-27 21:30 | 293 | 291
2018-01-27 22:00 | 282 | 279
2018-01-27 22:30 | 270 | 267
2018-01-27 23:00 | 260 | 257
2018-01-27 23:30 | 247 | 243
2018-01-28 | 236 | 233
2018-01-28 00:30 | 228 | 224
2018-01-28 01:00 | 222 | 218
2018-01-28 01:30 | 214 | 211
2018-01-28 02:00 | 207 | 205
2018-01-28 02:30 | 205 | 203
2018-01-28 03:00 | 203 | 202
2018-01-28 03:30 | 203 | 201
2018-01-28 04:00 | 201 | 199
2018-01-28 04:30 | 199 | 197
2018-01-28 05:00 | 199 | 197
2018-01-28 05:30 | 199 | 197
2018-01-28 06:00 | 198 | 196
2018-01-28 06:30 | 199 | 197
2018-01-28 07:00 | 198 | 196
2018-01-28 07:30 | 183 | 181
2018-01-28 08:00 | 185 | 183
2018-01-28 08:30 | 190 | 188
2018-01-28 09:00 | 194 | 192
2018-01-28 09:30 | 213 | 211
2018-01-28 10:00 | 222 | 220
2018-01-28 10:30 | 228 | 226
2018-01-28 11:00 | 228 | 226
2018-01-28 11:30 | 232 | 230
2018-01-28 12:00 | 237 | 234
2018-01-28 12:30 | 233 | 231
2018-01-28 13:00 | 236 | 234
2018-01-28 13:30 | 237 | 235
2018-01-28 14:00 | 242 | 240
2018-01-28 14:30 | 234 | 231
2018-01-28 15:00 | 241 | 238
2018-01-28 15:30 | 226 | 221
2018-01-28 16:00 | 220 | 216
2018-01-28 16:30 | 228 | 225
2018-01-28 17:00 | 245 | 241
2018-01-28 17:30 | 254 | 251
2018-01-28 18:00 | 278 | 275
2018-01-28 18:30 | 290 | 287
2018-01-28 19:00 | 299 | 295
2018-01-28 19:30 | 334 | 330
2018-01-28 20:00 | 338 | 334
2018-01-28 20:30 | 328 | 324
2018-01-28 21:00 | 318 | 314
2018-01-28 21:30 | 304 | 299
2018-01-28 22:00 | 288 | 284
2018-01-28 22:30 | 292 | 288
2018-01-28 23:00 | 280 | 277
2018-01-28 23:30 | 268 | 264
2018-01-29 | 255 | 251
2018-01-29 00:30 | 250 | 246
2018-01-29 01:00 | 246 | 242
2018-01-29 01:30 | 239 | 235
2018-01-29 02:00 | 235 | 231
2018-01-29 02:30 | 233 | 229
2018-01-29 03:00 | 230 | 226
2018-01-29 03:30 | 229 | 225
2018-01-29 04:00 | 228 | 223
2018-01-29 04:30 | 230 | 225
2018-01-29 05:00 | 230 | 226
2018-01-29 05:30 | 237 | 233
2018-01-29 06:00 | 244 | 240
2018-01-29 06:30 | 259 | 254
2018-01-29 07:00 | 271 | 266
2018-01-29 07:30 | 269 | 264
2018-01-29 08:00 | 277 | 273
2018-01-29 08:30 | 261 | 256
2018-01-29 09:00 | 246 | 241
2018-01-29 09:30 | 242 | 237
2018-01-29 10:00 | 243 | 238
2018-01-29 10:30 | 243 | 238
2018-01-29 11:00 | 246 | 241
2018-01-29 11:30 | 231 | 227
2018-01-29 12:00 | 214 | 209
2018-01-29 12:30 | 219 | 214
2018-01-29 13:00 | 225 | 220
2018-01-29 13:30 | 224 | 220
2018-01-29 14:00 | 231 | 227
2018-01-29 14:30 | 237 | 233
2018-01-29 15:00 | 237 | 233
2018-01-29 15:30 | 221 | 216
2018-01-29 16:00 | 227 | 223
2018-01-29 16:30 | 239 | 234
2018-01-29 17:00 | 249 | 245
2018-01-29 17:30 | 255 | 251
2018-01-29 18:00 | 257 | 253
2018-01-29 18:30 | 263 | 259
2018-01-29 19:00 | 273 | 269
2018-01-29 19:30 | 296 | 293
2018-01-29 20:00 | 297 | 293
2018-01-29 20:30 | 286 | 282
2018-01-29 21:00 | 274 | 270
2018-01-29 21:30 | 259 | 254
2018-01-29 22:00 | 244 | 239
2018-01-29 22:30 | 239 | 234
2018-01-29 23:00 | 224 | 220
2018-01-29 23:30 | 211 | 208
2018-01-30 | 200 | 197
2018-01-30 00:30 | 192 | 189
2018-01-30 01:00 | 185 | 181
2018-01-30 01:30 | 181 | 177
2018-01-30 02:00 | 176 | 173
2018-01-30 02:30 | 172 | 169
2018-01-30 03:00 | 168 | 165
2018-01-30 03:30 | 167 | 164
2018-01-30 04:00 | 165 | 162
2018-01-30 04:30 | 165 | 162
2018-01-30 05:00 | 168 | 165
2018-01-30 05:30 | 172 | 168
2018-01-30 06:00 | 181 | 177
2018-01-30 06:30 | 197 | 193
2018-01-30 07:00 | 209 | 205
2018-01-30 07:30 | 207 | 203
2018-01-30 08:00 | 213 | 209
2018-01-30 08:30 | 208 | 203
2018-01-30 09:00 | 209 | 205
2018-01-30 09:30 | 208 | 204
2018-01-30 10:00 | 204 | 201
2018-01-30 10:30 | 206 | 202
2018-01-30 11:00 | 201 | 197
2018-01-30 11:30 | 202 | 199
2018-01-30 12:00 | 207 | 204
2018-01-30 12:30 | 218 | 215
2018-01-30 13:00 | 226 | 222
2018-01-30 13:30 | 228 | 225
2018-01-30 14:00 | 221 | 219
2018-01-30 14:30 | 229 | 227
2018-01-30 15:00 | 214 | 211
2018-01-30 15:30 | 191 | 188
2018-01-30 16:00 | 194 | 191
2018-01-30 16:30 | 211 | 208
2018-01-30 17:00 | 239 | 237
2018-01-30 17:30 | 253 | 251
2018-01-30 18:00 | 254 | 252
2018-01-30 18:30 | 259 | 257
2018-01-30 19:00 | 257 | 255
2018-01-30 19:30 | 274 | 272
2018-01-30 20:00 | 273 | 271
2018-01-30 20:30 | 276 | 273
2018-01-30 21:00 | 268 | 265
2018-01-30 21:30 | 251 | 249
2018-01-30 22:00 | 236 | 234
2018-01-30 22:30 | 234 | 231
2018-01-30 23:00 | 222 | 220
2018-01-30 23:30 | 215 | 212
2018-01-31 | 203 | 202
2018-01-31 00:30 | 204 | 203
2018-01-31 01:00 | 199 | 198
2018-01-31 01:30 | 192 | 191
2018-01-31 02:00 | 189 | 188
2018-01-31 02:30 | 187 | 186
2018-01-31 03:00 | 184 | 183
2018-01-31 03:30 | 184 | 183
2018-01-31 04:00 | 182 | 181
2018-01-31 04:30 | 182 | 181
2018-01-31 05:00 | 183 | 182
2018-01-31 05:30 | 188 | 187
2018-01-31 06:00 | 194 | 194
2018-01-31 06:30 | 209 | 209
2018-01-31 07:00 | 222 | 221
2018-01-31 07:30 | 210 | 209
2018-01-31 08:00 | 211 | 211
2018-01-31 08:30 | 197 | 196
2018-01-31 09:00 | 193 | 192
2018-01-31 09:30 | 195 | 194
2018-01-31 10:00 | 195 | 194
2018-01-31 10:30 | 200 | 199
2018-01-31 11:00 | 200 | 198
2018-01-31 11:30 | 202 | 201
2018-01-31 12:00 | 195 | 194
2018-01-31 12:30 | 197 | 196
2018-01-31 13:00 | 200 | 199
2018-01-31 13:30 | 208 | 207
2018-01-31 14:00 | 214 | 213
2018-01-31 14:30 | 232 | 231
2018-01-31 15:00 | 239 | 238
2018-01-31 15:30 | 220 | 220
2018-01-31 16:00 | 226 | 226
2018-01-31 16:30 | 240 | 239
2018-01-31 17:00 | 245 | 243
2018-01-31 17:30 | 253 | 252
2018-01-31 18:00 | 261 | 260
2018-01-31 18:30 | 263 | 262
2018-01-31 19:00 | 273 | 272
2018-01-31 19:30 | 277 | 276
2018-01-31 20:00 | 276 | 275
2018-01-31 20:30 | 271 | 270
2018-01-31 21:00 | 259 | 257
2018-01-31 21:30 | 244 | 243
2018-01-31 22:00 | 228 | 226
2018-01-31 22:30 | 236 | 235
2018-01-31 23:00 | 250 | 248
2018-01-31 23:30 | 295 | 294
2018-02-01 | 287 | 286
2018-02-01 00:30 | 282 | 281
2018-02-01 01:00 | 273 | 271
2018-02-01 01:30 | 265 | 263
2018-02-01 02:00 | 259 | 257
2018-02-01 02:30 | 256 | 254
2018-02-01 03:00 | 253 | 251
2018-02-01 03:30 | 250 | 249
2018-02-01 04:00 | 248 | 246
2018-02-01 04:30 | 247 | 246
2018-02-01 05:00 | 248 | 247
2018-02-01 05:30 | 254 | 253
2018-02-01 06:00 | 261 | 260
2018-02-01 06:30 | 276 | 275
2018-02-01 07:00 | 286 | 285
2018-02-01 07:30 | 271 | 270
2018-02-01 08:00 | 272 | 271
2018-02-01 08:30 | 267 | 266
2018-02-01 09:00 | 264 | 263
2018-02-01 09:30 | 270 | 268
2018-02-01 10:00 | 267 | 266
2018-02-01 10:30 | 268 | 266
2018-02-01 11:00 | 268 | 266
2018-02-01 11:30 | 272 | 270
2018-02-01 12:00 | 276 | 274
2018-02-01 12:30 | 271 | 270
2018-02-01 13:00 | 265 | 263
2018-02-01 13:30 | 256 | 254
2018-02-01 14:00 | 258 | 257
2018-02-01 14:30 | 259 | 258
2018-02-01 15:00 | 264 | 263
2018-02-01 15:30 | 270 | 268
2018-02-01 16:00 | 287 | 285
2018-02-01 16:30 | 293 | 291
2018-02-01 17:00 | 299 | 298
2018-02-01 17:30 | 300 | 299
2018-02-01 18:00 | 315 | 314
2018-02-01 18:30 | 322 | 320
2018-02-01 19:00 | 330 | 328
2018-02-01 19:30 | 350 | 349
2018-02-01 20:00 | 352 | 351
2018-02-01 20:30 | 345 | 344
2018-02-01 21:00 | 333 | 332
2018-02-01 21:30 | 313 | 312
2018-02-01 22:00 | 300 | 299
2018-02-01 22:30 | 318 | 317
2018-02-01 23:00 | 310 | 309
2018-02-01 23:30 | 296 | 295
2018-02-02 | 285 | 284
2018-02-02 00:30 | 279 | 278
2018-02-02 01:00 | 273 | 272
2018-02-02 01:30 | 267 | 265
2018-02-02 02:00 | 261 | 260
2018-02-02 02:30 | 258 | 257
2018-02-02 03:00 | 256 | 254
2018-02-02 03:30 | 254 | 253
2018-02-02 04:00 | 254 | 253
2018-02-02 04:30 | 254 | 253
2018-02-02 05:00 | 254 | 253
2018-02-02 05:30 | 258 | 257
2018-02-02 06:00 | 265 | 264
2018-02-02 06:30 | 281 | 280
2018-02-02 07:00 | 284 | 283
2018-02-02 07:30 | 261 | 261
2018-02-02 08:00 | 266 | 265
2018-02-02 08:30 | 267 | 266
2018-02-02 09:00 | 260 | 259
2018-02-02 09:30 | 258 | 257
2018-02-02 10:00 | 255 | 254
2018-02-02 10:30 | 258 | 257
2018-02-02 11:00 | 270 | 269
2018-02-02 11:30 | 283 | 282
2018-02-02 12:00 | 284 | 283
2018-02-02 12:30 | 289 | 288
2018-02-02 13:00 | 295 | 294
2018-02-02 13:30 | 299 | 298
2018-02-02 14:00 | 301 | 299
2018-02-02 14:30 | 292 | 290
2018-02-02 15:00 | 288 | 286
2018-02-02 15:30 | 290 | 289
2018-02-02 16:00 | 302 | 300
2018-02-02 16:30 | 305 | 303
2018-02-02 17:00 | 299 | 297
2018-02-02 17:30 | 300 | 299
2018-02-02 18:00 | 301 | 300
2018-02-02 18:30 | 308 | 306
2018-02-02 19:00 | 315 | 313
2018-02-02 19:30 | 322 | 320
2018-02-02 20:00 | 322 | 320
2018-02-02 20:30 | 317 | 315
2018-02-02 21:00 | 317 | 316
2018-02-02 21:30 | 318 | 317
2018-02-02 22:00 | 314 | 313
2018-02-02 22:30 | 327 | 325
2018-02-02 23:00 | 314 | 313
2018-02-02 23:30 | 300 | 298
2018-02-03 | 290 | 288
2018-02-03 00:30 | 285 | 283
2018-02-03 01:00 | 277 | 275
2018-02-03 01:30 | 270 | 268
2018-02-03 02:00 | 264 | 263
2018-02-03 02:30 | 261 | 259
2018-02-03 03:00 | 259 | 258
2018-02-03 03:30 | 256 | 255
2018-02-03 04:00 | 256 | 254
2018-02-03 04:30 | 253 | 251
2018-02-03 05:00 | 252 | 251
2018-02-03 05:30 | 252 | 251
2018-02-03 06:00 | 255 | 254
2018-02-03 06:30 | 257 | 255
2018-02-03 07:00 | 254 | 252
2018-02-03 07:30 | 241 | 240
2018-02-03 08:00 | 262 | 261
2018-02-03 08:30 | 271 | 270
2018-02-03 09:00 | 276 | 274
2018-02-03 09:30 | 275 | 274
2018-02-03 10:00 | 264 | 263
2018-02-03 10:30 | 263 | 261
2018-02-03 11:00 | 263 | 262
2018-02-03 11:30 | 262 | 261
2018-02-03 12:00 | 250 | 248
2018-02-03 12:30 | 251 | 249
2018-02-03 13:00 | 251 | 250
2018-02-03 13:30 | 252 | 250
2018-02-03 14:00 | 259 | 257
2018-02-03 14:30 | 273 | 272
2018-02-03 15:00 | 282 | 281
2018-02-03 15:30 | 288 | 287
2018-02-03 16:00 | 303 | 302
2018-02-03 16:30 | 304 | 302
2018-02-03 17:00 | 310 | 309
2018-02-03 17:30 | 319 | 317
2018-02-03 18:00 | 322 | 321
2018-02-03 18:30 | 327 | 325
2018-02-03 19:00 | 328 | 326
2018-02-03 19:30 | 331 | 329
2018-02-03 20:00 | 329 | 328
2018-02-03 20:30 | 336 | 334
2018-02-03 21:00 | 329 | 328
2018-02-03 21:30 | 319 | 317
2018-02-03 22:00 | 315 | 314
2018-02-03 22:30 | 330 | 329
2018-02-03 23:00 | 321 | 320
2018-02-03 23:30 | 311 | 309
2018-02-04 | 301 | 299
2018-02-04 00:30 | 293 | 291
2018-02-04 01:00 | 285 | 283
2018-02-04 01:30 | 280 | 278
2018-02-04 02:00 | 277 | 275
2018-02-04 02:30 | 273 | 271
2018-02-04 03:00 | 269 | 267
2018-02-04 03:30 | 266 | 264
2018-02-04 04:00 | 264 | 262
2018-02-04 04:30 | 261 | 260
2018-02-04 05:00 | 261 | 259
2018-02-04 05:30 | 258 | 256
2018-02-04 06:00 | 258 | 256
2018-02-04 06:30 | 258 | 256
2018-02-04 07:00 | 250 | 249
2018-02-04 07:30 | 238 | 236
2018-02-04 08:00 | 235 | 233
2018-02-04 08:30 | 230 | 229
2018-02-04 09:00 | 228 | 226
2018-02-04 09:30 | 232 | 230
2018-02-04 10:00 | 231 | 230
2018-02-04 10:30 | 235 | 234
2018-02-04 11:00 | 233 | 232
2018-02-04 11:30 | 229 | 227
2018-02-04 12:00 | 228 | 227
2018-02-04 12:30 | 227 | 225
2018-02-04 13:00 | 230 | 229
2018-02-04 13:30 | 233 | 232
2018-02-04 14:00 | 242 | 240
2018-02-04 14:30 | 248 | 247
2018-02-04 15:00 | 245 | 244
2018-02-04 15:30 | 255 | 253
2018-02-04 16:00 | 280 | 278
2018-02-04 16:30 | 300 | 298
2018-02-04 17:00 | 306 | 304
2018-02-04 17:30 | 311 | 309
2018-02-04 18:00 | 319 | 317
2018-02-04 18:30 | 322 | 320
2018-02-04 19:00 | 323 | 322
2018-02-04 19:30 | 322 | 320
2018-02-04 20:00 | 315 | 313
2018-02-04 20:30 | 308 | 306
2018-02-04 21:00 | 297 | 295
2018-02-04 21:30 | 285 | 283
2018-02-04 22:00 | 275 | 273
2018-02-04 22:30 | 285 | 283
2018-02-04 23:00 | 276 | 274
2018-02-04 23:30 | 264 | 262
2018-02-05 | 254 | 252
2018-02-05 00:30 | 250 | 248
2018-02-05 01:00 | 245 | 243
2018-02-05 01:30 | 241 | 239
2018-02-05 02:00 | 238 | 236
2018-02-05 02:30 | 235 | 233
2018-02-05 03:00 | 233 | 231
2018-02-05 03:30 | 231 | 229
2018-02-05 04:00 | 229 | 228
2018-02-05 04:30 | 230 | 229
2018-02-05 05:00 | 231 | 230
2018-02-05 05:30 | 235 | 233
2018-02-05 06:00 | 246 | 244
2018-02-05 06:30 | 262 | 261
2018-02-05 07:00 | 270 | 269
2018-02-05 07:30 | 263 | 261
2018-02-05 08:00 | 267 | 265
2018-02-05 08:30 | 269 | 267
2018-02-05 09:00 | 266 | 264
2018-02-05 09:30 | 262 | 261
2018-02-05 10:00 | 260 | 258
2018-02-05 10:30 | 256 | 254
2018-02-05 11:00 | 250 | 247
2018-02-05 11:30 | 245 | 243
2018-02-05 12:00 | 242 | 240
2018-02-05 12:30 | 246 | 244
2018-02-05 13:00 | 247 | 245
2018-02-05 13:30 | 239 | 236
2018-02-05 14:00 | 248 | 246
2018-02-05 14:30 | 234 | 232
2018-02-05 15:00 | 230 | 227
2018-02-05 15:30 | 228 | 225
2018-02-05 16:00 | 231 | 228
2018-02-05 16:30 | 240 | 237
2018-02-05 17:00 | 242 | 239
2018-02-05 17:30 | 251 | 248
2018-02-05 18:00 | 257 | 255
2018-02-05 18:30 | 264 | 262
2018-02-05 19:00 | 271 | 269
2018-02-05 19:30 | 271 | 268
2018-02-05 20:00 | 265 | 263
2018-02-05 20:30 | 258 | 256
2018-02-05 21:00 | 246 | 243
2018-02-05 21:30 | 236 | 233
2018-02-05 22:00 | 228 | 226
2018-02-05 22:30 | 221 | 218
2018-02-05 23:00 | 217 | 214
2018-02-05 23:30 | 209 | 207
2018-02-06 | 202 | 199
2018-02-06 00:30 | 196 | 193
2018-02-06 01:00 | 191 | 189
2018-02-06 01:30 | 187 | 185
2018-02-06 02:00 | 188 | 186
2018-02-06 02:30 | 186 | 183
2018-02-06 03:00 | 184 | 182
2018-02-06 03:30 | 184 | 182
2018-02-06 04:00 | 180 | 177
2018-02-06 04:30 | 179 | 177
2018-02-06 05:00 | 183 | 181
2018-02-06 05:30 | 189 | 187
2018-02-06 06:00 | 197 | 195
2018-02-06 06:30 | 216 | 214
2018-02-06 07:00 | 228 | 225
2018-02-06 07:30 | 226 | 224
2018-02-06 08:00 | 231 | 228
2018-02-06 08:30 | 231 | 229
2018-02-06 09:00 | 226 | 223
2018-02-06 09:30 | 222 | 219
2018-02-06 10:00 | 216 | 213
2018-02-06 10:30 | 217 | 214
2018-02-06 11:00 | 216 | 213
2018-02-06 11:30 | 206 | 203
2018-02-06 12:00 | 204 | 201
2018-02-06 12:30 | 210 | 207
2018-02-06 13:00 | 211 | 208
2018-02-06 13:30 | 210 | 207
2018-02-06 14:00 | 210 | 207
2018-02-06 14:30 | 207 | 204
2018-02-06 15:00 | 204 | 201
2018-02-06 15:30 | 204 | 201
2018-02-06 16:00 | 211 | 208
2018-02-06 16:30 | 215 | 212
2018-02-06 17:00 | 220 | 217
2018-02-06 17:30 | 227 | 223
2018-02-06 18:00 | 234 | 231
2018-02-06 18:30 | 241 | 237
2018-02-06 19:00 | 247 | 243
2018-02-06 19:30 | 250 | 247
2018-02-06 20:00 | 248 | 245
2018-02-06 20:30 | 243 | 240
2018-02-06 21:00 | 233 | 230
2018-02-06 21:30 | 224 | 221
2018-02-06 22:00 | 210 | 208
2018-02-06 22:30 | 193 | 190
2018-02-06 23:00 | 183 | 180
2018-02-06 23:30 | 172 | 169
2018-02-07 | 162 | 160
2018-02-07 00:30 | 157 | 155
2018-02-07 01:00 | 152 | 150
2018-02-07 01:30 | 154 | 152
2018-02-07 02:00 | 153 | 150
2018-02-07 02:30 | 151 | 148
2018-02-07 03:00 | 148 | 145
2018-02-07 03:30 | 149 | 147
2018-02-07 04:00 | 147 | 145
2018-02-07 04:30 | 147 | 145
2018-02-07 05:00 | 149 | 146
2018-02-07 05:30 | 156 | 154
2018-02-07 06:00 | 164 | 161
2018-02-07 06:30 | 180 | 178
2018-02-07 07:00 | 192 | 191
2018-02-07 07:30 | 194 | 192
2018-02-07 08:00 | 192 | 191
2018-02-07 08:30 | 202 | 200
2018-02-07 09:00 | 207 | 205
2018-02-07 09:30 | 206 | 203
2018-02-07 10:00 | 204 | 202
2018-02-07 10:30 | 199 | 197
2018-02-07 11:00 | 198 | 195
2018-02-07 11:30 | 197 | 194
2018-02-07 12:00 | 196 | 194
2018-02-07 12:30 | 203 | 202
2018-02-07 13:00 | 208 | 206
2018-02-07 13:30 | 203 | 202
2018-02-07 14:00 | 207 | 205
2018-02-07 14:30 | 203 | 201
2018-02-07 15:00 | 204 | 202
2018-02-07 15:30 | 205 | 203
2018-02-07 16:00 | 214 | 211
2018-02-07 16:30 | 215 | 213
2018-02-07 17:00 | 222 | 220
2018-02-07 17:30 | 228 | 226
2018-02-07 18:00 | 236 | 234
2018-02-07 18:30 | 237 | 235
2018-02-07 19:00 | 247 | 245
2018-02-07 19:30 | 256 | 254
2018-02-07 20:00 | 257 | 254
2018-02-07 20:30 | 251 | 249
2018-02-07 21:00 | 242 | 239
2018-02-07 21:30 | 232 | 230
2018-02-07 22:00 | 219 | 216
2018-02-07 22:30 | 206 | 203
2018-02-07 23:00 | 193 | 190
2018-02-07 23:30 | 183 | 180
2018-02-08 | 174 | 171
2018-02-08 00:30 | 170 | 167
2018-02-08 01:00 | 163 | 160
2018-02-08 01:30 | 158 | 156
2018-02-08 02:00 | 153 | 151
2018-02-08 02:30 | 150 | 148
2018-02-08 03:00 | 150 | 148
2018-02-08 03:30 | 150 | 147
2018-02-08 04:00 | 151 | 148
2018-02-08 04:30 | 151 | 148
2018-02-08 05:00 | 151 | 148
2018-02-08 05:30 | 158 | 156
2018-02-08 06:00 | 164 | 162
2018-02-08 06:30 | 179 | 177
2018-02-08 07:00 | 189 | 187
2018-02-08 07:30 | 192 | 190
2018-02-08 08:00 | 196 | 194
2018-02-08 08:30 | 183 | 181
2018-02-08 09:00 | 157 | 155
2018-02-08 09:30 | 152 | 151
2018-02-08 10:00 | 141 | 139
2018-02-08 10:30 | 144 | 142
2018-02-08 11:00 | 149 | 147
2018-02-08 11:30 | 144 | 142
2018-02-08 12:00 | 132 | 131
2018-02-08 12:30 | 114 | 112
2018-02-08 13:00 | 122 | 120
2018-02-08 13:30 | 131 | 129
2018-02-08 14:00 | 135 | 134
2018-02-08 14:30 | 132 | 130
2018-02-08 15:00 | 130 | 128
2018-02-08 15:30 | 114 | 112
2018-02-08 16:00 | 93 | 90
2018-02-08 16:30 | 107 | 105
2018-02-08 17:00 | 119 | 117
2018-02-08 17:30 | 127 | 125
2018-02-08 18:00 | 132 | 131
2018-02-08 18:30 | 147 | 145
2018-02-08 19:00 | 160 | 158
2018-02-08 19:30 | 174 | 172
2018-02-08 20:00 | 172 | 170
2018-02-08 20:30 | 161 | 159
2018-02-08 21:00 | 151 | 149
2018-02-08 21:30 | 159 | 157
2018-02-08 22:00 | 191 | 190
2018-02-08 22:30 | 186 | 185
2018-02-08 23:00 | 176 | 174
2018-02-08 23:30 | 165 | 163
2018-02-09 | 157 | 154
2018-02-09 00:30 | 169 | 168
2018-02-09 01:00 | 164 | 162
2018-02-09 01:30 | 159 | 158
2018-02-09 02:00 | 157 | 155
2018-02-09 02:30 | 153 | 152
2018-02-09 03:00 | 152 | 151
2018-02-09 03:30 | 152 | 150
2018-02-09 04:00 | 150 | 149
2018-02-09 04:30 | 152 | 151
2018-02-09 05:00 | 154 | 152
2018-02-09 05:30 | 158 | 157
2018-02-09 06:00 | 161 | 160
2018-02-09 06:30 | 174 | 173
2018-02-09 07:00 | 171 | 170
2018-02-09 07:30 | 163 | 162
2018-02-09 08:00 | 167 | 166
2018-02-09 08:30 | 169 | 168
2018-02-09 09:00 | 168 | 167
2018-02-09 09:30 | 163 | 162
2018-02-09 10:00 | 163 | 162
2018-02-09 10:30 | 160 | 159
2018-02-09 11:00 | 165 | 163
2018-02-09 11:30 | 182 | 181
2018-02-09 12:00 | 185 | 184
2018-02-09 12:30 | 191 | 190
2018-02-09 13:00 | 191 | 189
2018-02-09 13:30 | 187 | 186
2018-02-09 14:00 | 194 | 193
2018-02-09 14:30 | 192 | 191
2018-02-09 15:00 | 181 | 179
2018-02-09 15:30 | 193 | 192
2018-02-09 16:00 | 198 | 196
2018-02-09 16:30 | 203 | 201
2018-02-09 17:00 | 202 | 200
2018-02-09 17:30 | 209 | 208
2018-02-09 18:00 | 212 | 210
2018-02-09 18:30 | 218 | 216
2018-02-09 19:00 | 224 | 222
2018-02-09 19:30 | 240 | 239
2018-02-09 20:00 | 242 | 240
2018-02-09 20:30 | 254 | 253
2018-02-09 21:00 | 251 | 250
2018-02-09 21:30 | 242 | 240
2018-02-09 22:00 | 230 | 229
2018-02-09 22:30 | 218 | 217
2018-02-09 23:00 | 208 | 207
2018-02-09 23:30 | 200 | 198
2018-02-10 | 190 | 189
2018-02-10 00:30 | 183 | 182
2018-02-10 01:00 | 179 | 177
2018-02-10 01:30 | 176 | 174
2018-02-10 02:00 | 171 | 169
2018-02-10 02:30 | 168 | 166
2018-02-10 03:00 | 165 | 163
2018-02-10 03:30 | 164 | 163
2018-02-10 04:00 | 163 | 161
2018-02-10 04:30 | 158 | 156
2018-02-10 05:00 | 150 | 148
2018-02-10 05:30 | 153 | 151
2018-02-10 06:00 | 154 | 152
2018-02-10 06:30 | 155 | 153
2018-02-10 07:00 | 159 | 157
2018-02-10 07:30 | 156 | 155
2018-02-10 08:00 | 160 | 159
2018-02-10 08:30 | 166 | 164
2018-02-10 09:00 | 172 | 171
2018-02-10 09:30 | 174 | 173
2018-02-10 10:00 | 173 | 172
2018-02-10 10:30 | 176 | 175
2018-02-10 11:00 | 174 | 173
2018-02-10 11:30 | 173 | 172
2018-02-10 12:00 | 172 | 170
2018-02-10 12:30 | 171 | 170
2018-02-10 13:00 | 173 | 172
2018-02-10 13:30 | 175 | 174
2018-02-10 14:00 | 177 | 176
2018-02-10 14:30 | 176 | 175
2018-02-10 15:00 | 179 | 178
2018-02-10 15:30 | 191 | 189
2018-02-10 16:00 | 205 | 204
2018-02-10 16:30 | 208 | 207
2018-02-10 17:00 | 216 | 215
2018-02-10 17:30 | 223 | 222
2018-02-10 18:00 | 237 | 235
2018-02-10 18:30 | 247 | 246
2018-02-10 19:00 | 256 | 255
2018-02-10 19:30 | 264 | 263
2018-02-10 20:00 | 264 | 262
2018-02-10 20:30 | 263 | 262
2018-02-10 21:00 | 254 | 253
2018-02-10 21:30 | 245 | 244
2018-02-10 22:00 | 236 | 235
2018-02-10 22:30 | 223 | 221
2018-02-10 23:00 | 214 | 212
2018-02-10 23:30 | 203 | 202
2018-02-11 | 196 | 194
2018-02-11 00:30 | 190 | 189
2018-02-11 01:00 | 183 | 182
2018-02-11 01:30 | 177 | 176
2018-02-11 02:00 | 173 | 173
2018-02-11 02:30 | 182 | 181
2018-02-11 03:00 | 184 | 184
2018-02-11 03:30 | 182 | 181
2018-02-11 04:00 | 180 | 179
2018-02-11 04:30 | 178 | 178
2018-02-11 05:00 | 178 | 178
2018-02-11 05:30 | 179 | 179
2018-02-11 06:00 | 180 | 179
2018-02-11 06:30 | 180 | 179
2018-02-11 07:00 | 179 | 178
2018-02-11 07:30 | 175 | 174
2018-02-11 08:00 | 167 | 166
2018-02-11 08:30 | 162 | 162
2018-02-11 09:00 | 156 | 155
2018-02-11 09:30 | 158 | 157
2018-02-11 10:00 | 161 | 160
2018-02-11 10:30 | 163 | 162
2018-02-11 11:00 | 162 | 161
2018-02-11 11:30 | 163 | 163
2018-02-11 12:00 | 166 | 165
2018-02-11 12:30 | 170 | 170
2018-02-11 13:00 | 173 | 172
2018-02-11 13:30 | 176 | 175
2018-02-11 14:00 | 178 | 178
2018-02-11 14:30 | 185 | 184
2018-02-11 15:00 | 189 | 189
2018-02-11 15:30 | 197 | 196
2018-02-11 16:00 | 205 | 204
2018-02-11 16:30 | 213 | 212
2018-02-11 17:00 | 191 | 190
2018-02-11 17:30 | 163 | 162
2018-02-11 18:00 | 173 | 173
2018-02-11 18:30 | 212 | 211
2018-02-11 19:00 | 234 | 233
2018-02-11 19:30 | 245 | 244
2018-02-11 20:00 | 243 | 242
2018-02-11 20:30 | 248 | 247
2018-02-11 21:00 | 247 | 247
2018-02-11 21:30 | 245 | 244
2018-02-11 22:00 | 229 | 228
2018-02-11 22:30 | 223 | 222
2018-02-11 23:00 | 229 | 228
2018-02-11 23:30 | 222 | 221
2018-02-12 | 214 | 213
2018-02-12 00:30 | 189 | 188
2018-02-12 01:00 | 161 | 160
2018-02-12 01:30 | 157 | 157
2018-02-12 02:00 | 154 | 153
2018-02-12 02:30 | 150 | 149
2018-02-12 03:00 | 149 | 148
2018-02-12 03:30 | 137 | 137
2018-02-12 04:00 | 116 | 115
2018-02-12 04:30 | 117 | 116
2018-02-12 05:00 | 120 | 119
2018-02-12 05:30 | 124 | 123
2018-02-12 06:00 | 131 | 130
2018-02-12 06:30 | 146 | 146
2018-02-12 07:00 | 158 | 157
2018-02-12 07:30 | 168 | 167
2018-02-12 08:00 | 170 | 168
2018-02-12 08:30 | 170 | 168
2018-02-12 09:00 | 167 | 165
2018-02-12 09:30 | 167 | 165
2018-02-12 10:00 | 164 | 162
2018-02-12 10:30 | 162 | 160
2018-02-12 11:00 | 168 | 166
2018-02-12 11:30 | 169 | 167
2018-02-12 12:00 | 174 | 172
2018-02-12 12:30 | 180 | 178
2018-02-12 13:00 | 184 | 181
2018-02-12 13:30 | 186 | 183
2018-02-12 14:00 | 190 | 187
2018-02-12 14:30 | 182 | 179
2018-02-12 15:00 | 150 | 147
2018-02-12 15:30 | 149 | 146
2018-02-12 16:00 | 186 | 183
2018-02-12 16:30 | 187 | 184
2018-02-12 17:00 | 153 | 149
2018-02-12 17:30 | 151 | 148
2018-02-12 18:00 | 163 | 161
2018-02-12 18:30 | 185 | 183
2018-02-12 19:00 | 185 | 183
2018-02-12 19:30 | 203 | 200
2018-02-12 20:00 | 250 | 248
2018-02-12 20:30 | 267 | 264
2018-02-12 21:00 | 256 | 253
2018-02-12 21:30 | 247 | 244
2018-02-12 22:00 | 231 | 228
2018-02-12 22:30 | 252 | 249
2018-02-12 23:00 | 241 | 239
2018-02-12 23:30 | 242 | 240
2018-02-13 | 236 | 233
2018-02-13 00:30 | 230 | 227
2018-02-13 01:00 | 222 | 219
2018-02-13 01:30 | 217 | 215
2018-02-13 02:00 | 213 | 212
2018-02-13 02:30 | 211 | 210
2018-02-13 03:00 | 207 | 206
2018-02-13 03:30 | 207 | 206
2018-02-13 04:00 | 204 | 203
2018-02-13 04:30 | 204 | 203
2018-02-13 05:00 | 205 | 204
2018-02-13 05:30 | 211 | 210
2018-02-13 06:00 | 217 | 216
2018-02-13 06:30 | 231 | 230
2018-02-13 07:00 | 242 | 241
2018-02-13 07:30 | 248 | 247
2018-02-13 08:00 | 252 | 251
2018-02-13 08:30 | 235 | 234
2018-02-13 09:00 | 226 | 225
2018-02-13 09:30 | 214 | 213
2018-02-13 10:00 | 201 | 199
2018-02-13 10:30 | 213 | 212
2018-02-13 11:00 | 202 | 201
2018-02-13 11:30 | 189 | 188
2018-02-13 12:00 | 192 | 191
2018-02-13 12:30 | 200 | 199
2018-02-13 13:00 | 204 | 203
2018-02-13 13:30 | 208 | 207
2018-02-13 14:00 | 214 | 213
2018-02-13 14:30 | 238 | 237
2018-02-13 15:00 | 262 | 261
2018-02-13 15:30 | 233 | 232
2018-02-13 16:00 | 212 | 210
2018-02-13 16:30 | 152 | 150
2018-02-13 17:00 | 146 | 144
2018-02-13 17:30 | 112 | 111
2018-02-13 18:00 | 115 | 114
2018-02-13 18:30 | 136 | 135
2018-02-13 19:00 | 145 | 144
2018-02-13 19:30 | 139 | 138
2018-02-13 20:00 | 182 | 181
2018-02-13 20:30 | 236 | 235
2018-02-13 21:00 | 258 | 258
2018-02-13 21:30 | 257 | 256
2018-02-13 22:00 | 239 | 238
2018-02-13 22:30 | 277 | 276
2018-02-13 23:00 | 279 | 278
2018-02-13 23:30 | 264 | 263
2018-02-14 | 253 | 252
2018-02-14 00:30 | 244 | 243
2018-02-14 01:00 | 237 | 236
2018-02-14 01:30 | 231 | 230
2018-02-14 02:00 | 226 | 225
2018-02-14 02:30 | 222 | 221
2018-02-14 03:00 | 218 | 217
2018-02-14 03:30 | 217 | 216
2018-02-14 04:00 | 215 | 215
2018-02-14 04:30 | 216 | 215
2018-02-14 05:00 | 216 | 215
2018-02-14 05:30 | 224 | 224
2018-02-14 06:00 | 232 | 231
2018-02-14 06:30 | 248 | 247
2018-02-14 07:00 | 258 | 257
2018-02-14 07:30 | 221 | 220
2018-02-14 08:00 | 202 | 202
2018-02-14 08:30 | 206 | 205
2018-02-14 09:00 | 212 | 212
2018-02-14 09:30 | 209 | 208
2018-02-14 10:00 | 189 | 188
2018-02-14 10:30 | 175 | 174
2018-02-14 11:00 | 185 | 184
2018-02-14 11:30 | 191 | 190
2018-02-14 12:00 | 197 | 196
2018-02-14 12:30 | 197 | 196
2018-02-14 13:00 | 194 | 193
2018-02-14 13:30 | 201 | 200
2018-02-14 14:00 | 209 | 208
2018-02-14 14:30 | 214 | 213
2018-02-14 15:00 | 209 | 208
2018-02-14 15:30 | 163 | 162
2018-02-14 16:00 | 119 | 118
2018-02-14 16:30 | 75 | 74
2018-02-14 17:00 | 57 | 54
2018-02-14 17:30 | 51 | 47
2018-02-14 18:00 | 55 | 52
2018-02-14 18:30 | 80 | 78
2018-02-14 19:00 | 91 | 89
2018-02-14 19:30 | 66 | 64
2018-02-14 20:00 | 114 | 113
2018-02-14 20:30 | 158 | 157
2018-02-14 21:00 | 215 | 215
2018-02-14 21:30 | 231 | 230
2018-02-14 22:00 | 216 | 215
2018-02-14 22:30 | 204 | 202
2018-02-14 23:00 | 188 | 186
2018-02-14 23:30 | 174 | 173
2018-02-15 | 162 | 160
2018-02-15 00:30 | 162 | 160
2018-02-15 01:00 | 156 | 154
2018-02-15 01:30 | 150 | 148
2018-02-15 02:00 | 145 | 143
2018-02-15 02:30 | 140 | 138
2018-02-15 03:00 | 138 | 135
2018-02-15 03:30 | 136 | 134
2018-02-15 04:00 | 135 | 133
2018-02-15 04:30 | 145 | 143
2018-02-15 05:00 | 158 | 156
2018-02-15 05:30 | 164 | 162
2018-02-15 06:00 | 171 | 169
2018-02-15 06:30 | 183 | 182
2018-02-15 07:00 | 194 | 192
2018-02-15 07:30 | 189 | 187
2018-02-15 08:00 | 192 | 191
2018-02-15 08:30 | 194 | 193
2018-02-15 09:00 | 195 | 194
2018-02-15 09:30 | 201 | 199
2018-02-15 10:00 | 201 | 200
2018-02-15 10:30 | 201 | 199
2018-02-15 11:00 | 188 | 186
2018-02-15 11:30 | 201 | 200
2018-02-15 12:00 | 203 | 201
2018-02-15 12:30 | 195 | 194
2018-02-15 13:00 | 190 | 189
2018-02-15 13:30 | 194 | 193
2018-02-15 14:00 | 213 | 212
2018-02-15 14:30 | 201 | 200
2018-02-15 15:00 | 194 | 193
2018-02-15 15:30 | 156 | 155
2018-02-15 16:00 | 99 | 98
2018-02-15 16:30 | 100 | 98
2018-02-15 17:00 | 90 | 88
2018-02-15 17:30 | 84 | 82
2018-02-15 18:00 | 164 | 163
2018-02-15 18:30 | 170 | 169
2018-02-15 19:00 | 184 | 183
2018-02-15 19:30 | 207 | 206
2018-02-15 20:00 | 232 | 231
2018-02-15 20:30 | 261 | 260
2018-02-15 21:00 | 307 | 306
2018-02-15 21:30 | 296 | 295
2018-02-15 22:00 | 279 | 277
2018-02-15 22:30 | 260 | 258
2018-02-15 23:00 | 266 | 264
2018-02-15 23:30 | 289 | 287
2018-02-16 | 275 | 273
2018-02-16 00:30 | 263 | 261
2018-02-16 01:00 | 253 | 251
2018-02-16 01:30 | 249 | 247
2018-02-16 02:00 | 246 | 243
2018-02-16 02:30 | 243 | 240
2018-02-16 03:00 | 240 | 238
2018-02-16 03:30 | 237 | 234
2018-02-16 04:00 | 233 | 231
2018-02-16 04:30 | 231 | 229
2018-02-16 05:00 | 233 | 231
2018-02-16 05:30 | 236 | 233
2018-02-16 06:00 | 242 | 239
2018-02-16 06:30 | 254 | 252
2018-02-16 07:00 | 268 | 266
2018-02-16 07:30 | 270 | 268
2018-02-16 08:00 | 280 | 278
2018-02-16 08:30 | 285 | 283
2018-02-16 09:00 | 283 | 281
2018-02-16 09:30 | 280 | 279
2018-02-16 10:00 | 278 | 276
2018-02-16 10:30 | 281 | 279
2018-02-16 11:00 | 280 | 278
2018-02-16 11:30 | 283 | 281
2018-02-16 12:00 | 292 | 290
2018-02-16 12:30 | 296 | 294
2018-02-16 13:00 | 303 | 301
2018-02-16 13:30 | 306 | 304
2018-02-16 14:00 | 302 | 300
2018-02-16 14:30 | 277 | 275
2018-02-16 15:00 | 254 | 251
2018-02-16 15:30 | 218 | 215
2018-02-16 16:00 | 225 | 223
2018-02-16 16:30 | 226 | 224
2018-02-16 17:00 | 231 | 230
2018-02-16 17:30 | 250 | 248
2018-02-16 18:00 | 273 | 271
2018-02-16 18:30 | 312 | 311
2018-02-16 19:00 | 322 | 321
2018-02-16 19:30 | 329 | 328
2018-02-16 20:00 | 325 | 324
2018-02-16 20:30 | 328 | 326
2018-02-16 21:00 | 355 | 353
2018-02-16 21:30 | 343 | 341
2018-02-16 22:00 | 329 | 327
2018-02-16 22:30 | 312 | 309
2018-02-16 23:00 | 297 | 295
2018-02-16 23:30 | 283 | 281
2018-02-17 | 269 | 267
2018-02-17 00:30 | 260 | 258
2018-02-17 01:00 | 260 | 258
2018-02-17 01:30 | 250 | 247
2018-02-17 02:00 | 239 | 237
2018-02-17 02:30 | 234 | 232
2018-02-17 03:00 | 231 | 229
2018-02-17 03:30 | 228 | 226
2018-02-17 04:00 | 223 | 221
2018-02-17 04:30 | 221 | 218
2018-02-17 05:00 | 220 | 217
2018-02-17 05:30 | 219 | 217
2018-02-17 06:00 | 220 | 218
2018-02-17 06:30 | 222 | 220
2018-02-17 07:00 | 222 | 220
2018-02-17 07:30 | 214 | 211
2018-02-17 08:00 | 217 | 215
2018-02-17 08:30 | 234 | 231
2018-02-17 09:00 | 242 | 239
2018-02-17 09:30 | 239 | 237
2018-02-17 10:00 | 232 | 230
2018-02-17 10:30 | 223 | 221
2018-02-17 11:00 | 221 | 219
2018-02-17 11:30 | 219 | 217
2018-02-17 12:00 | 222 | 220
2018-02-17 12:30 | 227 | 225
2018-02-17 13:00 | 231 | 229
2018-02-17 13:30 | 236 | 234
2018-02-17 14:00 | 247 | 246
2018-02-17 14:30 | 257 | 255
2018-02-17 15:00 | 257 | 255
2018-02-17 15:30 | 259 | 257
2018-02-17 16:00 | 279 | 277
2018-02-17 16:30 | 286 | 285
2018-02-17 17:00 | 294 | 292
2018-02-17 17:30 | 298 | 296
2018-02-17 18:00 | 303 | 301
2018-02-17 18:30 | 322 | 320
2018-02-17 19:00 | 332 | 331
2018-02-17 19:30 | 326 | 325
2018-02-17 20:00 | 254 | 253
2018-02-17 20:30 | 314 | 312
2018-02-17 21:00 | 318 | 315
2018-02-17 21:30 | 318 | 315
2018-02-17 22:00 | 307 | 305
2018-02-17 22:30 | 293 | 290
2018-02-17 23:00 | 277 | 275
2018-02-17 23:30 | 260 | 257
2018-02-18 | 247 | 244
2018-02-18 00:30 | 237 | 234
2018-02-18 01:00 | 229 | 226
2018-02-18 01:30 | 222 | 219
2018-02-18 02:00 | 217 | 214
2018-02-18 02:30 | 214 | 212
2018-02-18 03:00 | 212 | 210
2018-02-18 03:30 | 208 | 206
2018-02-18 04:00 | 207 | 205
2018-02-18 04:30 | 201 | 199
2018-02-18 05:00 | 184 | 182
2018-02-18 05:30 | 174 | 172
2018-02-18 06:00 | 172 | 169
2018-02-18 06:30 | 170 | 167
2018-02-18 07:00 | 169 | 166
2018-02-18 07:30 | 161 | 158
2018-02-18 08:00 | 159 | 157
2018-02-18 08:30 | 168 | 166
2018-02-18 09:00 | 164 | 162
2018-02-18 09:30 | 163 | 161
2018-02-18 10:00 | 169 | 167
2018-02-18 10:30 | 191 | 188
2018-02-18 11:00 | 195 | 193
2018-02-18 11:30 | 202 | 199
2018-02-18 12:00 | 209 | 206
2018-02-18 12:30 | 217 | 214
2018-02-18 13:00 | 224 | 222
2018-02-18 13:30 | 231 | 229
2018-02-18 14:00 | 236 | 234
2018-02-18 14:30 | 244 | 241
2018-02-18 15:00 | 252 | 249
2018-02-18 15:30 | 260 | 257
2018-02-18 16:00 | 274 | 271
2018-02-18 16:30 | 281 | 278
2018-02-18 17:00 | 295 | 292
2018-02-18 17:30 | 306 | 304
2018-02-18 18:00 | 310 | 308
2018-02-18 18:30 | 334 | 332
2018-02-18 19:00 | 345 | 343
2018-02-18 19:30 | 353 | 350
2018-02-18 20:00 | 348 | 346
2018-02-18 20:30 | 335 | 333
2018-02-18 21:00 | 322 | 320
2018-02-18 21:30 | 292 | 290
2018-02-18 22:00 | 274 | 271
2018-02-18 22:30 | 253 | 250
2018-02-18 23:00 | 238 | 236
2018-02-18 23:30 | 227 | 224
2018-02-19 | 218 | 215
2018-02-19 00:30 | 209 | 206
2018-02-19 01:00 | 199 | 197
2018-02-19 01:30 | 195 | 193
2018-02-19 02:00 | 192 | 190
2018-02-19 02:30 | 190 | 188
2018-02-19 03:00 | 186 | 184
2018-02-19 03:30 | 183 | 181
2018-02-19 04:00 | 182 | 180
2018-02-19 04:30 | 196 | 194
2018-02-19 05:00 | 201 | 199
2018-02-19 05:30 | 205 | 204
2018-02-19 06:00 | 214 | 212
2018-02-19 06:30 | 229 | 226
2018-02-19 07:00 | 238 | 236
2018-02-19 07:30 | 236 | 234
2018-02-19 08:00 | 241 | 239
2018-02-19 08:30 | 229 | 227
2018-02-19 09:00 | 204 | 202
2018-02-19 09:30 | 205 | 203
2018-02-19 10:00 | 201 | 198
2018-02-19 10:30 | 203 | 200
2018-02-19 11:00 | 201 | 199
2018-02-19 11:30 | 196 | 193
2018-02-19 12:00 | 180 | 177
2018-02-19 12:30 | 188 | 185
2018-02-19 13:00 | 193 | 190
2018-02-19 13:30 | 200 | 197
2018-02-19 14:00 | 203 | 200
2018-02-19 14:30 | 216 | 213
2018-02-19 15:00 | 222 | 220
2018-02-19 15:30 | 223 | 220
2018-02-19 16:00 | 203 | 201
2018-02-19 16:30 | 207 | 205
2018-02-19 17:00 | 214 | 212
2018-02-19 17:30 | 219 | 216
2018-02-19 18:00 | 228 | 225
2018-02-19 18:30 | 262 | 259
2018-02-19 19:00 | 242 | 239
2018-02-19 19:30 | 245 | 242
2018-02-19 20:00 | 247 | 244
2018-02-19 20:30 | 258 | 255
2018-02-19 21:00 | 246 | 243
2018-02-19 21:30 | 229 | 227
2018-02-19 22:00 | 209 | 207
2018-02-19 22:30 | 202 | 200
2018-02-19 23:00 | 193 | 191
2018-02-19 23:30 | 180 | 177
2018-02-20 | 170 | 167
2018-02-20 00:30 | 165 | 162
2018-02-20 01:00 | 158 | 155
2018-02-20 01:30 | 152 | 149
2018-02-20 02:00 | 148 | 146
2018-02-20 02:30 | 144 | 142
2018-02-20 03:00 | 139 | 138
2018-02-20 03:30 | 137 | 136
2018-02-20 04:00 | 137 | 136
2018-02-20 04:30 | 137 | 136
2018-02-20 05:00 | 139 | 137
2018-02-20 05:30 | 146 | 145
2018-02-20 06:00 | 155 | 153
2018-02-20 06:30 | 164 | 163
2018-02-20 07:00 | 179 | 178
2018-02-20 07:30 | 210 | 209
2018-02-20 08:00 | 221 | 221
2018-02-20 08:30 | 228 | 228
2018-02-20 09:00 | 211 | 209
2018-02-20 09:30 | 195 | 193
2018-02-20 10:00 | 202 | 200
2018-02-20 10:30 | 214 | 212
2018-02-20 11:00 | 213 | 211
2018-02-20 11:30 | 205 | 203
2018-02-20 12:00 | 202 | 200
2018-02-20 12:30 | 195 | 193
2018-02-20 13:00 | 199 | 197
2018-02-20 13:30 | 210 | 208
2018-02-20 14:00 | 215 | 214
2018-02-20 14:30 | 214 | 213
2018-02-20 15:00 | 214 | 213
2018-02-20 15:30 | 222 | 220
2018-02-20 16:00 | 229 | 228
2018-02-20 16:30 | 223 | 221
2018-02-20 17:00 | 201 | 200
2018-02-20 17:30 | 221 | 220
2018-02-20 18:00 | 233 | 231
2018-02-20 18:30 | 240 | 239
2018-02-20 19:00 | 249 | 247
2018-02-20 19:30 | 257 | 255
2018-02-20 20:00 | 259 | 258
2018-02-20 20:30 | 245 | 244
2018-02-20 21:00 | 230 | 229
2018-02-20 21:30 | 232 | 231
2018-02-20 22:00 | 225 | 223
2018-02-20 22:30 | 179 | 177
2018-02-20 23:00 | 184 | 182
2018-02-20 23:30 | 221 | 220
2018-02-21 | 212 | 211
2018-02-21 00:30 | 211 | 210
2018-02-21 01:00 | 208 | 207
2018-02-21 01:30 | 203 | 202
2018-02-21 02:00 | 200 | 199
2018-02-21 02:30 | 195 | 195
2018-02-21 03:00 | 195 | 195
2018-02-21 03:30 | 195 | 194
2018-02-21 04:00 | 194 | 193
2018-02-21 04:30 | 194 | 193
2018-02-21 05:00 | 197 | 196
2018-02-21 05:30 | 201 | 201
2018-02-21 06:00 | 209 | 208
2018-02-21 06:30 | 223 | 222
2018-02-21 07:00 | 237 | 236
2018-02-21 07:30 | 252 | 252
2018-02-21 08:00 | 261 | 260
2018-02-21 08:30 | 262 | 260
2018-02-21 09:00 | 256 | 255
2018-02-21 09:30 | 256 | 256
2018-02-21 10:00 | 256 | 255
2018-02-21 10:30 | 249 | 248
2018-02-21 11:00 | 250 | 249
2018-02-21 11:30 | 252 | 251
2018-02-21 12:00 | 241 | 240
2018-02-21 12:30 | 236 | 235
2018-02-21 13:00 | 241 | 240
2018-02-21 13:30 | 235 | 234
2018-02-21 14:00 | 250 | 249
2018-02-21 14:30 | 243 | 242
2018-02-21 15:00 | 233 | 232
2018-02-21 15:30 | 235 | 234
2018-02-21 16:00 | 250 | 248
2018-02-21 16:30 | 261 | 259
2018-02-21 17:00 | 263 | 262
2018-02-21 17:30 | 260 | 258
2018-02-21 18:00 | 264 | 262
2018-02-21 18:30 | 248 | 246
2018-02-21 19:00 | 240 | 239
2018-02-21 19:30 | 279 | 279
2018-02-21 20:00 | 289 | 289
2018-02-21 20:30 | 279 | 279
2018-02-21 21:00 | 270 | 270
2018-02-21 21:30 | 271 | 271
2018-02-21 22:00 | 262 | 261
2018-02-21 22:30 | 246 | 245
2018-02-21 23:00 | 237 | 236
2018-02-21 23:30 | 227 | 226
2018-02-22 | 217 | 216
2018-02-22 00:30 | 214 | 213
2018-02-22 01:00 | 208 | 207
2018-02-22 01:30 | 201 | 200
2018-02-22 02:00 | 196 | 195
2018-02-22 02:30 | 196 | 194
2018-02-22 03:00 | 191 | 190
2018-02-22 03:30 | 191 | 190
2018-02-22 04:00 | 191 | 189
2018-02-22 04:30 | 191 | 190
2018-02-22 05:00 | 195 | 194
2018-02-22 05:30 | 199 | 198
2018-02-22 06:00 | 208 | 206
2018-02-22 06:30 | 224 | 223
2018-02-22 07:00 | 238 | 237
2018-02-22 07:30 | 246 | 246
2018-02-22 08:00 | 255 | 254
2018-02-22 08:30 | 254 | 253
2018-02-22 09:00 | 253 | 252
2018-02-22 09:30 | 249 | 248
2018-02-22 10:00 | 246 | 244
2018-02-22 10:30 | 247 | 246
2018-02-22 11:00 | 242 | 241
2018-02-22 11:30 | 241 | 240
2018-02-22 12:00 | 234 | 233
2018-02-22 12:30 | 231 | 230
2018-02-22 13:00 | 242 | 241
2018-02-22 13:30 | 247 | 246
2018-02-22 14:00 | 251 | 250
2018-02-22 14:30 | 254 | 253
2018-02-22 15:00 | 248 | 247
2018-02-22 15:30 | 247 | 246
2018-02-22 16:00 | 251 | 250
2018-02-22 16:30 | 246 | 245
2018-02-22 17:00 | 254 | 253
2018-02-22 17:30 | 257 | 255
2018-02-22 18:00 | 263 | 261
2018-02-22 18:30 | 270 | 268
2018-02-22 19:00 | 279 | 277
2018-02-22 19:30 | 295 | 294
2018-02-22 20:00 | 291 | 290
2018-02-22 20:30 | 292 | 291
2018-02-22 21:00 | 286 | 284
2018-02-22 21:30 | 290 | 289
2018-02-22 22:00 | 280 | 278
2018-02-22 22:30 | 249 | 248
2018-02-22 23:00 | 227 | 225
2018-02-22 23:30 | 198 | 195
2018-02-23 | 187 | 185
2018-02-23 00:30 | 180 | 178
2018-02-23 01:00 | 174 | 172
2018-02-23 01:30 | 167 | 165
2018-02-23 02:00 | 157 | 155
2018-02-23 02:30 | 158 | 156
2018-02-23 03:00 | 155 | 154
2018-02-23 03:30 | 156 | 155
2018-02-23 04:00 | 155 | 154
2018-02-23 04:30 | 153 | 151
2018-02-23 05:00 | 157 | 155
2018-02-23 05:30 | 164 | 162
2018-02-23 06:00 | 172 | 171
2018-02-23 06:30 | 190 | 189
2018-02-23 07:00 | 205 | 203
2018-02-23 07:30 | 220 | 218
2018-02-23 08:00 | 226 | 225
2018-02-23 08:30 | 232 | 231
2018-02-23 09:00 | 227 | 226
2018-02-23 09:30 | 237 | 235
2018-02-23 10:00 | 244 | 243
2018-02-23 10:30 | 244 | 243
2018-02-23 11:00 | 243 | 242
2018-02-23 11:30 | 223 | 222
2018-02-23 12:00 | 215 | 214
2018-02-23 12:30 | 220 | 219
2018-02-23 13:00 | 219 | 218
2018-02-23 13:30 | 217 | 215
2018-02-23 14:00 | 216 | 214
2018-02-23 14:30 | 215 | 214
2018-02-23 15:00 | 224 | 223
2018-02-23 15:30 | 230 | 228
2018-02-23 16:00 | 232 | 231
2018-02-23 16:30 | 244 | 243
2018-02-23 17:00 | 251 | 250
2018-02-23 17:30 | 260 | 258
2018-02-23 18:00 | 255 | 253
2018-02-23 18:30 | 263 | 261
2018-02-23 19:00 | 269 | 268
2018-02-23 19:30 | 269 | 267
2018-02-23 20:00 | 261 | 259
2018-02-23 20:30 | 247 | 245
2018-02-23 21:00 | 234 | 232
2018-02-23 21:30 | 226 | 224
2018-02-23 22:00 | 214 | 212
2018-02-23 22:30 | 204 | 202
2018-02-23 23:00 | 196 | 194
2018-02-23 23:30 | 187 | 185
2018-02-24 | 178 | 176
2018-02-24 00:30 | 172 | 169
2018-02-24 01:00 | 162 | 161
2018-02-24 01:30 | 158 | 156
2018-02-24 02:00 | 153 | 152
2018-02-24 02:30 | 150 | 149
2018-02-24 03:00 | 149 | 147
2018-02-24 03:30 | 149 | 147
2018-02-24 04:00 | 146 | 145
2018-02-24 04:30 | 145 | 144
2018-02-24 05:00 | 146 | 145
2018-02-24 05:30 | 151 | 149
2018-02-24 06:00 | 165 | 164
2018-02-24 06:30 | 175 | 174
2018-02-24 07:00 | 179 | 178
2018-02-24 07:30 | 189 | 188
2018-02-24 08:00 | 198 | 197
2018-02-24 08:30 | 205 | 204
2018-02-24 09:00 | 209 | 209
2018-02-24 09:30 | 229 | 228
2018-02-24 10:00 | 228 | 227
2018-02-24 10:30 | 231 | 230
2018-02-24 11:00 | 233 | 231
2018-02-24 11:30 | 229 | 228
2018-02-24 12:00 | 219 | 218
2018-02-24 12:30 | 213 | 211
2018-02-24 13:00 | 214 | 212
2018-02-24 13:30 | 220 | 218
2018-02-24 14:00 | 227 | 225
2018-02-24 14:30 | 231 | 229
2018-02-24 15:00 | 233 | 232
2018-02-24 15:30 | 242 | 241
2018-02-24 16:00 | 250 | 249
2018-02-24 16:30 | 250 | 249
2018-02-24 17:00 | 246 | 245
2018-02-24 17:30 | 245 | 244
2018-02-24 18:00 | 261 | 260
2018-02-24 18:30 | 265 | 263
2018-02-24 19:00 | 258 | 256
2018-02-24 19:30 | 258 | 256
2018-02-24 20:00 | 259 | 257
2018-02-24 20:30 | 247 | 245
2018-02-24 21:00 | 244 | 241
2018-02-24 21:30 | 240 | 238
2018-02-24 22:00 | 234 | 232
2018-02-24 22:30 | 234 | 231
2018-02-24 23:00 | 233 | 231
2018-02-24 23:30 | 225 | 223
2018-02-25 | 218 | 216
2018-02-25 00:30 | 212 | 210
2018-02-25 01:00 | 208 | 205
2018-02-25 01:30 | 203 | 201
2018-02-25 02:00 | 200 | 198
2018-02-25 02:30 | 195 | 194
2018-02-25 03:00 | 192 | 191
2018-02-25 03:30 | 190 | 189
2018-02-25 04:00 | 190 | 188
2018-02-25 04:30 | 188 | 187
2018-02-25 05:00 | 188 | 187
2018-02-25 05:30 | 196 | 195
2018-02-25 06:00 | 207 | 206
2018-02-25 06:30 | 208 | 207
2018-02-25 07:00 | 212 | 211
2018-02-25 07:30 | 201 | 199
2018-02-25 08:00 | 193 | 191
2018-02-25 08:30 | 192 | 191
2018-02-25 09:00 | 196 | 195
2018-02-25 09:30 | 203 | 201
2018-02-25 10:00 | 195 | 193
2018-02-25 10:30 | 193 | 191
2018-02-25 11:00 | 194 | 191
2018-02-25 11:30 | 201 | 199
2018-02-25 12:00 | 211 | 209
2018-02-25 12:30 | 212 | 210
2018-02-25 13:00 | 228 | 226
2018-02-25 13:30 | 245 | 244
2018-02-25 14:00 | 246 | 245
2018-02-25 14:30 | 239 | 237
2018-02-25 15:00 | 239 | 238
2018-02-25 15:30 | 244 | 242
2018-02-25 16:00 | 241 | 240
2018-02-25 16:30 | 236 | 234
2018-02-25 17:00 | 239 | 238
2018-02-25 17:30 | 244 | 243
2018-02-25 18:00 | 254 | 252
2018-02-25 18:30 | 254 | 252
2018-02-25 19:00 | 256 | 254
2018-02-25 19:30 | 260 | 258
2018-02-25 20:00 | 254 | 252
2018-02-25 20:30 | 245 | 243
2018-02-25 21:00 | 237 | 235
2018-02-25 21:30 | 228 | 227
2018-02-25 22:00 | 217 | 215
2018-02-25 22:30 | 205 | 202
2018-02-25 23:00 | 193 | 191
2018-02-25 23:30 | 184 | 182
2018-02-26 | 177 | 175
2018-02-26 00:30 | 173 | 171
2018-02-26 01:00 | 168 | 166
2018-02-26 01:30 | 164 | 162
2018-02-26 02:00 | 161 | 159
2018-02-26 02:30 | 159 | 157
2018-02-26 03:00 | 158 | 156
2018-02-26 03:30 | 158 | 156
2018-02-26 04:00 | 156 | 155
2018-02-26 04:30 | 156 | 155
2018-02-26 05:00 | 157 | 155
2018-02-26 05:30 | 165 | 163
2018-02-26 06:00 | 175 | 173
2018-02-26 06:30 | 188 | 187
2018-02-26 07:00 | 202 | 201
2018-02-26 07:30 | 222 | 221
2018-02-26 08:00 | 233 | 231
2018-02-26 08:30 | 234 | 231
2018-02-26 09:00 | 234 | 232
2018-02-26 09:30 | 234 | 231
2018-02-26 10:00 | 234 | 231
2018-02-26 10:30 | 232 | 230
2018-02-26 11:00 | 234 | 232
2018-02-26 11:30 | 240 | 238
2018-02-26 12:00 | 246 | 244
2018-02-26 12:30 | 261 | 259
2018-02-26 13:00 | 259 | 257
2018-02-26 13:30 | 264 | 262
2018-02-26 14:00 | 281 | 279
2018-02-26 14:30 | 255 | 253
2018-02-26 15:00 | 256 | 254
2018-02-26 15:30 | 270 | 269
2018-02-26 16:00 | 274 | 272
2018-02-26 16:30 | 268 | 266
2018-02-26 17:00 | 272 | 270
2018-02-26 17:30 | 269 | 266
2018-02-26 18:00 | 286 | 283
2018-02-26 18:30 | 292 | 290
2018-02-26 19:00 | 303 | 301
2018-02-26 19:30 | 307 | 305
2018-02-26 20:00 | 299 | 297
2018-02-26 20:30 | 290 | 287
2018-02-26 21:00 | 274 | 271
2018-02-26 21:30 | 258 | 254
2018-02-26 22:00 | 243 | 239
2018-02-26 22:30 | 227 | 224
2018-02-26 23:00 | 214 | 211
2018-02-26 23:30 | 201 | 198
2018-02-27 | 192 | 189
2018-02-27 00:30 | 185 | 182
2018-02-27 01:00 | 179 | 176
2018-02-27 01:30 | 182 | 179
2018-02-27 02:00 | 180 | 177
2018-02-27 02:30 | 178 | 175
2018-02-27 03:00 | 175 | 173
2018-02-27 03:30 | 173 | 171
2018-02-27 04:00 | 171 | 169
2018-02-27 04:30 | 172 | 170
2018-02-27 05:00 | 173 | 171
2018-02-27 05:30 | 182 | 180
2018-02-27 06:00 | 189 | 187
2018-02-27 06:30 | 203 | 201
2018-02-27 07:00 | 220 | 218
2018-02-27 07:30 | 225 | 223
2018-02-27 08:00 | 234 | 232
2018-02-27 08:30 | 237 | 235
2018-02-27 09:00 | 233 | 231
2018-02-27 09:30 | 237 | 234
2018-02-27 10:00 | 234 | 232
2018-02-27 10:30 | 234 | 232
2018-02-27 11:00 | 233 | 230
2018-02-27 11:30 | 232 | 229
2018-02-27 12:00 | 235 | 232
2018-02-27 12:30 | 236 | 233
2018-02-27 13:00 | 242 | 239
2018-02-27 13:30 | 259 | 257
2018-02-27 14:00 | 271 | 269
2018-02-27 14:30 | 280 | 277
2018-02-27 15:00 | 274 | 272
2018-02-27 15:30 | 265 | 262
2018-02-27 16:00 | 262 | 259
2018-02-27 16:30 | 264 | 261
2018-02-27 17:00 | 277 | 274
2018-02-27 17:30 | 288 | 286
2018-02-27 18:00 | 291 | 289
2018-02-27 18:30 | 299 | 296
2018-02-27 19:00 | 306 | 304
2018-02-27 19:30 | 308 | 306
2018-02-27 20:00 | 302 | 300
2018-02-27 20:30 | 290 | 288
2018-02-27 21:00 | 278 | 275
2018-02-27 21:30 | 259 | 257
2018-02-27 22:00 | 240 | 237
2018-02-27 22:30 | 228 | 225
2018-02-27 23:00 | 219 | 215
2018-02-27 23:30 | 214 | 211
2018-02-28 | 203 | 201
2018-02-28 00:30 | 199 | 198
2018-02-28 01:00 | 191 | 189
2018-02-28 01:30 | 186 | 184
2018-02-28 02:00 | 182 | 180
2018-02-28 02:30 | 182 | 180
2018-02-28 03:00 | 182 | 180
2018-02-28 03:30 | 180 | 177
2018-02-28 04:00 | 177 | 175
2018-02-28 04:30 | 188 | 186
2018-02-28 05:00 | 193 | 191
2018-02-28 05:30 | 199 | 197
2018-02-28 06:00 | 207 | 205
2018-02-28 06:30 | 227 | 225
2018-02-28 07:00 | 243 | 242
2018-02-28 07:30 | 261 | 260
2018-02-28 08:00 | 270 | 269
2018-02-28 08:30 | 272 | 271
2018-02-28 09:00 | 267 | 265
2018-02-28 09:30 | 268 | 266
2018-02-28 10:00 | 272 | 270
2018-02-28 10:30 | 272 | 270
2018-02-28 11:00 | 265 | 263
2018-02-28 11:30 | 253 | 251
2018-02-28 12:00 | 253 | 251
2018-02-28 12:30 | 259 | 257
2018-02-28 13:00 | 261 | 260
2018-02-28 13:30 | 246 | 244
2018-02-28 14:00 | 262 | 260
2018-02-28 14:30 | 275 | 273
2018-02-28 15:00 | 278 | 276
2018-02-28 15:30 | 272 | 269
2018-02-28 16:00 | 268 | 266
2018-02-28 16:30 | 258 | 256
2018-02-28 17:00 | 258 | 255
2018-02-28 17:30 | 258 | 255
2018-02-28 18:00 | 264 | 261
2018-02-28 18:30 | 269 | 267
2018-02-28 19:00 | 277 | 274
2018-02-28 19:30 | 277 | 274
2018-02-28 20:00 | 270 | 267
2018-02-28 20:30 | 258 | 256
2018-02-28 21:00 | 248 | 245
2018-02-28 21:30 | 245 | 242
2018-02-28 22:00 | 234 | 232
2018-02-28 22:30 | 219 | 216
2018-02-28 23:00 | 208 | 205
2018-02-28 23:30 | 198 | 195
2018-03-01 | 191 | 188
2018-03-01 00:30 | 185 | 182
2018-03-01 01:00 | 181 | 178
2018-03-01 01:30 | 179 | 176
2018-03-01 02:00 | 176 | 173
2018-03-01 02:30 | 175 | 172
2018-03-01 03:00 | 172 | 169
2018-03-01 03:30 | 172 | 169
2018-03-01 04:00 | 172 | 169
2018-03-01 04:30 | 172 | 169
2018-03-01 05:00 | 173 | 170
2018-03-01 05:30 | 180 | 178
2018-03-01 06:00 | 189 | 187
2018-03-01 06:30 | 207 | 205
2018-03-01 07:00 | 224 | 222
2018-03-01 07:30 | 244 | 243
2018-03-01 08:00 | 253 | 252
2018-03-01 08:30 | 255 | 254
2018-03-01 09:00 | 242 | 240
2018-03-01 09:30 | 223 | 221
2018-03-01 10:00 | 209 | 207
2018-03-01 10:30 | 208 | 206
2018-03-01 11:00 | 206 | 204
2018-03-01 11:30 | 193 | 190
2018-03-01 12:00 | 180 | 177
2018-03-01 12:30 | 178 | 175
2018-03-01 13:00 | 139 | 136
2018-03-01 13:30 | 131 | 128
2018-03-01 14:00 | 131 | 128
2018-03-01 14:30 | 145 | 143
2018-03-01 15:00 | 147 | 145
2018-03-01 15:30 | 146 | 143
2018-03-01 16:00 | 155 | 153
2018-03-01 16:30 | 159 | 157
2018-03-01 17:00 | 163 | 161
2018-03-01 17:30 | 164 | 162
2018-03-01 18:00 | 170 | 168
2018-03-01 18:30 | 180 | 177
2018-03-01 19:00 | 190 | 187
2018-03-01 19:30 | 194 | 191
2018-03-01 20:00 | 185 | 183
2018-03-01 20:30 | 175 | 173
2018-03-01 21:00 | 196 | 194
2018-03-01 21:30 | 215 | 213
2018-03-01 22:00 | 243 | 241
2018-03-01 22:30 | 230 | 227
2018-03-01 23:00 | 218 | 215
2018-03-01 23:30 | 204 | 202
2018-03-02 | 195 | 193
2018-03-02 00:30 | 188 | 186
2018-03-02 01:00 | 183 | 181
2018-03-02 01:30 | 179 | 176
2018-03-02 02:00 | 175 | 172
2018-03-02 02:30 | 169 | 167
2018-03-02 03:00 | 166 | 164
2018-03-02 03:30 | 165 | 163
2018-03-02 04:00 | 164 | 162
2018-03-02 04:30 | 165 | 162
2018-03-02 05:00 | 166 | 164
2018-03-02 05:30 | 171 | 169
2018-03-02 06:00 | 178 | 176
2018-03-02 06:30 | 195 | 194
2018-03-02 07:00 | 209 | 207
2018-03-02 07:30 | 226 | 224
2018-03-02 08:00 | 231 | 229
2018-03-02 08:30 | 223 | 222
2018-03-02 09:00 | 234 | 232
2018-03-02 09:30 | 243 | 241
2018-03-02 10:00 | 245 | 243
2018-03-02 10:30 | 241 | 239
2018-03-02 11:00 | 245 | 243
2018-03-02 11:30 | 247 | 245
2018-03-02 12:00 | 243 | 241
2018-03-02 12:30 | 242 | 240
2018-03-02 13:00 | 242 | 240
2018-03-02 13:30 | 247 | 245
2018-03-02 14:00 | 252 | 250
2018-03-02 14:30 | 253 | 251
2018-03-02 15:00 | 246 | 245
2018-03-02 15:30 | 252 | 250
2018-03-02 16:00 | 262 | 261
2018-03-02 16:30 | 278 | 276
2018-03-02 17:00 | 285 | 283
2018-03-02 17:30 | 284 | 282
2018-03-02 18:00 | 286 | 284
2018-03-02 18:30 | 287 | 285
2018-03-02 19:00 | 295 | 293
2018-03-02 19:30 | 299 | 297
2018-03-02 20:00 | 293 | 292
2018-03-02 20:30 | 294 | 292
2018-03-02 21:00 | 287 | 285
2018-03-02 21:30 | 276 | 274
2018-03-02 22:00 | 264 | 262
2018-03-02 22:30 | 247 | 245
2018-03-02 23:00 | 235 | 233
2018-03-02 23:30 | 224 | 222
2018-03-03 | 215 | 213
2018-03-03 00:30 | 206 | 205
2018-03-03 01:00 | 200 | 198
2018-03-03 01:30 | 195 | 193
2018-03-03 02:00 | 192 | 190
2018-03-03 02:30 | 189 | 187
2018-03-03 03:00 | 187 | 185
2018-03-03 03:30 | 185 | 183
2018-03-03 04:00 | 184 | 182
2018-03-03 04:30 | 183 | 181
2018-03-03 05:00 | 184 | 182
2018-03-03 05:30 | 185 | 183
2018-03-03 06:00 | 187 | 185
2018-03-03 06:30 | 193 | 191
2018-03-03 07:00 | 198 | 196
2018-03-03 07:30 | 203 | 201
2018-03-03 08:00 | 208 | 207
2018-03-03 08:30 | 215 | 214
2018-03-03 09:00 | 220 | 218
2018-03-03 09:30 | 223 | 221
2018-03-03 10:00 | 220 | 218
2018-03-03 10:30 | 198 | 196
2018-03-03 11:00 | 196 | 194
2018-03-03 11:30 | 190 | 188
2018-03-03 12:00 | 203 | 201
2018-03-03 12:30 | 219 | 216
2018-03-03 13:00 | 220 | 218
2018-03-03 13:30 | 222 | 220
2018-03-03 14:00 | 220 | 217
2018-03-03 14:30 | 223 | 220
2018-03-03 15:00 | 225 | 222
2018-03-03 15:30 | 232 | 229
2018-03-03 16:00 | 240 | 238
2018-03-03 16:30 | 247 | 245
2018-03-03 17:00 | 250 | 248
2018-03-03 17:30 | 265 | 263
2018-03-03 18:00 | 274 | 272
2018-03-03 18:30 | 278 | 276
2018-03-03 19:00 | 285 | 283
2018-03-03 19:30 | 289 | 288
2018-03-03 20:00 | 281 | 280
2018-03-03 20:30 | 271 | 269
2018-03-03 21:00 | 261 | 259
2018-03-03 21:30 | 252 | 250
2018-03-03 22:00 | 243 | 240
2018-03-03 22:30 | 231 | 228
2018-03-03 23:00 | 217 | 215
2018-03-03 23:30 | 209 | 207
2018-03-04 | 199 | 196
2018-03-04 00:30 | 192 | 190
2018-03-04 01:00 | 186 | 184
2018-03-04 01:30 | 182 | 179
2018-03-04 02:00 | 178 | 175
2018-03-04 02:30 | 176 | 173
2018-03-04 03:00 | 173 | 170
2018-03-04 03:30 | 170 | 167
2018-03-04 04:00 | 168 | 165
2018-03-04 04:30 | 169 | 166
2018-03-04 05:00 | 169 | 166
2018-03-04 05:30 | 169 | 166
2018-03-04 06:00 | 171 | 168
2018-03-04 06:30 | 172 | 170
2018-03-04 07:00 | 176 | 174
2018-03-04 07:30 | 189 | 187
2018-03-04 08:00 | 196 | 194
2018-03-04 08:30 | 197 | 195
2018-03-04 09:00 | 192 | 190
2018-03-04 09:30 | 195 | 193
2018-03-04 10:00 | 211 | 210
2018-03-04 10:30 | 222 | 220
2018-03-04 11:00 | 222 | 221
2018-03-04 11:30 | 218 | 216
2018-03-04 12:00 | 226 | 225
2018-03-04 12:30 | 227 | 225
2018-03-04 13:00 | 223 | 221
2018-03-04 13:30 | 225 | 224
2018-03-04 14:00 | 234 | 232
2018-03-04 14:30 | 233 | 231
2018-03-04 15:00 | 232 | 229
2018-03-04 15:30 | 228 | 226
2018-03-04 16:00 | 239 | 237
2018-03-04 16:30 | 244 | 242
2018-03-04 17:00 | 252 | 250
2018-03-04 17:30 | 268 | 266
2018-03-04 18:00 | 270 | 268
2018-03-04 18:30 | 283 | 281
2018-03-04 19:00 | 286 | 284
2018-03-04 19:30 | 288 | 287
2018-03-04 20:00 | 281 | 279
2018-03-04 20:30 | 279 | 277
2018-03-04 21:00 | 273 | 271
2018-03-04 21:30 | 258 | 256
2018-03-04 22:00 | 247 | 245
2018-03-04 22:30 | 232 | 229
2018-03-04 23:00 | 220 | 217
2018-03-04 23:30 | 209 | 207
2018-03-05 | 202 | 199
2018-03-05 00:30 | 196 | 194
2018-03-05 01:00 | 190 | 187
2018-03-05 01:30 | 198 | 195
2018-03-05 02:00 | 200 | 198
2018-03-05 02:30 | 198 | 196
2018-03-05 03:00 | 196 | 194
2018-03-05 03:30 | 194 | 192
2018-03-05 04:00 | 194 | 192
2018-03-05 04:30 | 194 | 192
2018-03-05 05:00 | 195 | 193
2018-03-05 05:30 | 203 | 201
2018-03-05 06:00 | 210 | 208
2018-03-05 06:30 | 215 | 213
2018-03-05 07:00 | 228 | 227
2018-03-05 07:30 | 247 | 246
2018-03-05 08:00 | 253 | 251
2018-03-05 08:30 | 252 | 250
2018-03-05 09:00 | 236 | 234
2018-03-05 09:30 | 208 | 206
2018-03-05 10:00 | 203 | 201
2018-03-05 10:30 | 210 | 208
2018-03-05 11:00 | 205 | 204
2018-03-05 11:30 | 215 | 214
2018-03-05 12:00 | 216 | 214
2018-03-05 12:30 | 212 | 210
2018-03-05 13:00 | 213 | 212
2018-03-05 13:30 | 222 | 221
2018-03-05 14:00 | 249 | 247
2018-03-05 14:30 | 233 | 232
2018-03-05 15:00 | 232 | 230
2018-03-05 15:30 | 222 | 220
2018-03-05 16:00 | 195 | 193
2018-03-05 16:30 | 195 | 193
2018-03-05 17:00 | 195 | 193
2018-03-05 17:30 | 194 | 192
2018-03-05 18:00 | 194 | 192
2018-03-05 18:30 | 203 | 201
2018-03-05 19:00 | 215 | 213
2018-03-05 19:30 | 215 | 213
2018-03-05 20:00 | 206 | 204
2018-03-05 20:30 | 195 | 193
2018-03-05 21:00 | 181 | 179
2018-03-05 21:30 | 167 | 165
2018-03-05 22:00 | 155 | 152
2018-03-05 22:30 | 147 | 146
2018-03-05 23:00 | 171 | 169
2018-03-05 23:30 | 191 | 189
2018-03-06 | 223 | 222
2018-03-06 00:30 | 219 | 218
2018-03-06 01:00 | 214 | 212
2018-03-06 01:30 | 209 | 207
2018-03-06 02:00 | 204 | 201
2018-03-06 02:30 | 203 | 201
2018-03-06 03:00 | 203 | 201
2018-03-06 03:30 | 201 | 199
2018-03-06 04:00 | 199 | 197
2018-03-06 04:30 | 200 | 198
2018-03-06 05:00 | 206 | 204
2018-03-06 05:30 | 211 | 209
2018-03-06 06:00 | 217 | 215
2018-03-06 06:30 | 203 | 201
2018-03-06 07:00 | 194 | 193
2018-03-06 07:30 | 207 | 206
2018-03-06 08:00 | 210 | 208
2018-03-06 08:30 | 176 | 174
2018-03-06 09:00 | 176 | 174
2018-03-06 09:30 | 176 | 174
2018-03-06 10:00 | 178 | 176
2018-03-06 10:30 | 173 | 171
2018-03-06 11:00 | 168 | 166
2018-03-06 11:30 | 168 | 166
2018-03-06 12:00 | 173 | 171
2018-03-06 12:30 | 199 | 197
2018-03-06 13:00 | 203 | 202
2018-03-06 13:30 | 202 | 201
2018-03-06 14:00 | 198 | 197
2018-03-06 14:30 | 202 | 200
2018-03-06 15:00 | 168 | 166
2018-03-06 15:30 | 164 | 163
2018-03-06 16:00 | 173 | 172
2018-03-06 16:30 | 182 | 181
2018-03-06 17:00 | 192 | 190
2018-03-06 17:30 | 194 | 193
2018-03-06 18:00 | 204 | 202
2018-03-06 18:30 | 208 | 207
2018-03-06 19:00 | 218 | 216
2018-03-06 19:30 | 221 | 219
2018-03-06 20:00 | 214 | 212
2018-03-06 20:30 | 203 | 201
2018-03-06 21:00 | 191 | 189
2018-03-06 21:30 | 211 | 210
2018-03-06 22:00 | 227 | 225
2018-03-06 22:30 | 259 | 258
2018-03-06 23:00 | 250 | 249
2018-03-06 23:30 | 239 | 238
2018-03-07 | 230 | 228
2018-03-07 00:30 | 224 | 223
2018-03-07 01:00 | 217 | 215
2018-03-07 01:30 | 213 | 211
2018-03-07 02:00 | 209 | 207
2018-03-07 02:30 | 208 | 207
2018-03-07 03:00 | 206 | 205
2018-03-07 03:30 | 201 | 200
2018-03-07 04:00 | 192 | 191
2018-03-07 04:30 | 182 | 181
2018-03-07 05:00 | 184 | 183
2018-03-07 05:30 | 188 | 186
2018-03-07 06:00 | 168 | 166
2018-03-07 06:30 | 173 | 171
2018-03-07 07:00 | 186 | 184
2018-03-07 07:30 | 214 | 213
2018-03-07 08:00 | 220 | 218
2018-03-07 08:30 | 199 | 198
2018-03-07 09:00 | 191 | 190
2018-03-07 09:30 | 186 | 185
2018-03-07 10:00 | 182 | 181
2018-03-07 10:30 | 188 | 186
2018-03-07 11:00 | 181 | 179
2018-03-07 11:30 | 178 | 176
2018-03-07 12:00 | 179 | 177
2018-03-07 12:30 | 183 | 181
2018-03-07 13:00 | 177 | 176
2018-03-07 13:30 | 176 | 174
2018-03-07 14:00 | 183 | 182
2018-03-07 14:30 | 203 | 202
2018-03-07 15:00 | 205 | 204
2018-03-07 15:30 | 205 | 203
2018-03-07 16:00 | 201 | 199
2018-03-07 16:30 | 201 | 199
2018-03-07 17:00 | 204 | 202
2018-03-07 17:30 | 209 | 208
2018-03-07 18:00 | 211 | 209
2018-03-07 18:30 | 222 | 221
2018-03-07 19:00 | 236 | 234
2018-03-07 19:30 | 239 | 237
2018-03-07 20:00 | 232 | 230
2018-03-07 20:30 | 232 | 230
2018-03-07 21:00 | 232 | 230
2018-03-07 21:30 | 238 | 236
2018-03-07 22:00 | 238 | 237
2018-03-07 22:30 | 224 | 223
2018-03-07 23:00 | 214 | 212
2018-03-07 23:30 | 203 | 201
2018-03-08 | 196 | 195
2018-03-08 00:30 | 195 | 193
2018-03-08 01:00 | 190 | 188
2018-03-08 01:30 | 189 | 188
2018-03-08 02:00 | 187 | 186
2018-03-08 02:30 | 187 | 185
2018-03-08 03:00 | 185 | 183
2018-03-08 03:30 | 181 | 180
2018-03-08 04:00 | 182 | 181
2018-03-08 04:30 | 185 | 184
2018-03-08 05:00 | 155 | 154
2018-03-08 05:30 | 145 | 144
2018-03-08 06:00 | 172 | 171
2018-03-08 06:30 | 202 | 201
2018-03-08 07:00 | 219 | 218
2018-03-08 07:30 | 245 | 244
2018-03-08 08:00 | 264 | 262
2018-03-08 08:30 | 270 | 268
2018-03-08 09:00 | 273 | 272
2018-03-08 09:30 | 282 | 281
2018-03-08 10:00 | 274 | 272
2018-03-08 10:30 | 256 | 254
2018-03-08 11:00 | 252 | 250
2018-03-08 11:30 | 244 | 242
2018-03-08 12:00 | 245 | 243
2018-03-08 12:30 | 233 | 231
2018-03-08 13:00 | 201 | 198
2018-03-08 13:30 | 172 | 169
2018-03-08 14:00 | 170 | 168
2018-03-08 14:30 | 168 | 165
2018-03-08 15:00 | 169 | 166
2018-03-08 15:30 | 171 | 169
2018-03-08 16:00 | 170 | 167
2018-03-08 16:30 | 181 | 178
2018-03-08 17:00 | 184 | 182
2018-03-08 17:30 | 185 | 183
2018-03-08 18:00 | 189 | 187
2018-03-08 18:30 | 195 | 193
2018-03-08 19:00 | 203 | 201
2018-03-08 19:30 | 200 | 199
2018-03-08 20:00 | 193 | 192
2018-03-08 20:30 | 185 | 183
2018-03-08 21:00 | 176 | 174
2018-03-08 21:30 | 164 | 162
2018-03-08 22:00 | 153 | 151
2018-03-08 22:30 | 138 | 136
2018-03-08 23:00 | 160 | 159
2018-03-08 23:30 | 161 | 159
2018-03-09 | 152 | 151
2018-03-09 00:30 | 147 | 145
2018-03-09 01:00 | 140 | 138
2018-03-09 01:30 | 135 | 134
2018-03-09 02:00 | 132 | 131
2018-03-09 02:30 | 131 | 129
2018-03-09 03:00 | 128 | 126
2018-03-09 03:30 | 127 | 125
2018-03-09 04:00 | 129 | 127
2018-03-09 04:30 | 129 | 127
2018-03-09 05:00 | 133 | 132
2018-03-09 05:30 | 141 | 140
2018-03-09 06:00 | 151 | 150
2018-03-09 06:30 | 169 | 168
2018-03-09 07:00 | 181 | 180
2018-03-09 07:30 | 198 | 197
2018-03-09 08:00 | 211 | 210
2018-03-09 08:30 | 213 | 211
2018-03-09 09:00 | 174 | 173
2018-03-09 09:30 | 163 | 162
2018-03-09 10:00 | 161 | 159
2018-03-09 10:30 | 159 | 157
2018-03-09 11:00 | 148 | 147
2018-03-09 11:30 | 141 | 140
2018-03-09 12:00 | 145 | 143
2018-03-09 12:30 | 148 | 146
2018-03-09 13:00 | 149 | 148
2018-03-09 13:30 | 150 | 148
2018-03-09 14:00 | 151 | 149
2018-03-09 14:30 | 154 | 152
2018-03-09 15:00 | 151 | 149
2018-03-09 15:30 | 151 | 149
2018-03-09 16:00 | 156 | 155
2018-03-09 16:30 | 161 | 160
2018-03-09 17:00 | 168 | 167
2018-03-09 17:30 | 174 | 173
2018-03-09 18:00 | 173 | 171
2018-03-09 18:30 | 173 | 171
2018-03-09 19:00 | 177 | 175
2018-03-09 19:30 | 176 | 175
2018-03-09 20:00 | 166 | 165
2018-03-09 20:30 | 158 | 157
2018-03-09 21:00 | 184 | 183
2018-03-09 21:30 | 209 | 208
2018-03-09 22:00 | 246 | 244
2018-03-09 22:30 | 238 | 236
2018-03-09 23:00 | 227 | 226
2018-03-09 23:30 | 215 | 214
2018-03-10 | 210 | 208
2018-03-10 00:30 | 203 | 201
2018-03-10 01:00 | 197 | 195
2018-03-10 01:30 | 191 | 189
2018-03-10 02:00 | 188 | 186
2018-03-10 02:30 | 186 | 184
2018-03-10 03:00 | 185 | 183
2018-03-10 03:30 | 186 | 183
2018-03-10 04:00 | 186 | 184
2018-03-10 04:30 | 187 | 185
2018-03-10 05:00 | 189 | 187
2018-03-10 05:30 | 190 | 188
2018-03-10 06:00 | 192 | 190
2018-03-10 06:30 | 198 | 196
2018-03-10 07:00 | 201 | 199
2018-03-10 07:30 | 209 | 207
2018-03-10 08:00 | 213 | 211
2018-03-10 08:30 | 212 | 210
2018-03-10 09:00 | 215 | 214
2018-03-10 09:30 | 219 | 217
2018-03-10 10:00 | 218 | 216
2018-03-10 10:30 | 216 | 214
2018-03-10 11:00 | 213 | 211
2018-03-10 11:30 | 210 | 208
2018-03-10 12:00 | 208 | 207
2018-03-10 12:30 | 208 | 207
2018-03-10 13:00 | 206 | 204
2018-03-10 13:30 | 206 | 205
2018-03-10 14:00 | 209 | 207
2018-03-10 14:30 | 219 | 218
2018-03-10 15:00 | 226 | 224
2018-03-10 15:30 | 232 | 231
2018-03-10 16:00 | 239 | 238
2018-03-10 16:30 | 245 | 243
2018-03-10 17:00 | 253 | 252
2018-03-10 17:30 | 261 | 259
2018-03-10 18:00 | 270 | 269
2018-03-10 18:30 | 276 | 275
2018-03-10 19:00 | 281 | 279
2018-03-10 19:30 | 282 | 281
2018-03-10 20:00 | 275 | 273
2018-03-10 20:30 | 265 | 263
2018-03-10 21:00 | 257 | 255
2018-03-10 21:30 | 252 | 251
2018-03-10 22:00 | 246 | 244
2018-03-10 22:30 | 239 | 237
2018-03-10 23:00 | 228 | 227
2018-03-10 23:30 | 217 | 216
2018-03-11 | 213 | 211
2018-03-11 00:30 | 206 | 204
2018-03-11 01:00 | 200 | 198
2018-03-11 01:30 | 196 | 193
2018-03-11 02:00 | 191 | 189
2018-03-11 02:30 | 189 | 186
2018-03-11 03:00 | 187 | 185
2018-03-11 03:30 | 185 | 183
2018-03-11 04:00 | 185 | 183
2018-03-11 04:30 | 186 | 185
2018-03-11 05:00 | 186 | 184
2018-03-11 05:30 | 186 | 185
2018-03-11 06:00 | 188 | 187
2018-03-11 06:30 | 190 | 189
2018-03-11 07:00 | 194 | 193
2018-03-11 07:30 | 196 | 195
2018-03-11 08:00 | 199 | 197
2018-03-11 08:30 | 199 | 198
2018-03-11 09:00 | 199 | 198
2018-03-11 09:30 | 199 | 198
2018-03-11 10:00 | 202 | 200
2018-03-11 10:30 | 206 | 204
2018-03-11 11:00 | 200 | 197
2018-03-11 11:30 | 195 | 193
2018-03-11 12:00 | 201 | 199
2018-03-11 12:30 | 198 | 197
2018-03-11 13:00 | 192 | 190
2018-03-11 13:30 | 190 | 188
2018-03-11 14:00 | 190 | 188
2018-03-11 14:30 | 193 | 192
2018-03-11 15:00 | 202 | 200
2018-03-11 15:30 | 203 | 201
2018-03-11 16:00 | 215 | 213
2018-03-11 16:30 | 221 | 219
2018-03-11 17:00 | 230 | 228
2018-03-11 17:30 | 240 | 238
2018-03-11 18:00 | 251 | 249
2018-03-11 18:30 | 261 | 259
2018-03-11 19:00 | 269 | 268
2018-03-11 19:30 | 274 | 273
2018-03-11 20:00 | 266 | 265
2018-03-11 20:30 | 256 | 255
2018-03-11 21:00 | 249 | 248
2018-03-11 21:30 | 240 | 239
2018-03-11 22:00 | 228 | 227
2018-03-11 22:30 | 215 | 213
2018-03-11 23:00 | 204 | 202
2018-03-11 23:30 | 195 | 193
2018-03-12 | 188 | 186
2018-03-12 00:30 | 181 | 179
2018-03-12 01:00 | 177 | 174
2018-03-12 01:30 | 171 | 168
2018-03-12 02:00 | 169 | 167
2018-03-12 02:30 | 166 | 164
2018-03-12 03:00 | 165 | 162
2018-03-12 03:30 | 164 | 161
2018-03-12 04:00 | 161 | 159
2018-03-12 04:30 | 161 | 159
2018-03-12 05:00 | 164 | 162
2018-03-12 05:30 | 171 | 169
2018-03-12 06:00 | 179 | 177
2018-03-12 06:30 | 194 | 193
2018-03-12 07:00 | 211 | 210
2018-03-12 07:30 | 219 | 218
2018-03-12 08:00 | 215 | 213
2018-03-12 08:30 | 213 | 211
2018-03-12 09:00 | 210 | 208
2018-03-12 09:30 | 207 | 206
2018-03-12 10:00 | 202 | 201
2018-03-12 10:30 | 200 | 198
2018-03-12 11:00 | 202 | 200
2018-03-12 11:30 | 209 | 208
2018-03-12 12:00 | 210 | 208
2018-03-12 12:30 | 214 | 213
2018-03-12 13:00 | 213 | 211
2018-03-12 13:30 | 214 | 212
2018-03-12 14:00 | 224 | 222
2018-03-12 14:30 | 228 | 227
2018-03-12 15:00 | 212 | 211
2018-03-12 15:30 | 221 | 219
2018-03-12 16:00 | 228 | 226
2018-03-12 16:30 | 231 | 230
2018-03-12 17:00 | 240 | 238
2018-03-12 17:30 | 251 | 249
2018-03-12 18:00 | 262 | 261
2018-03-12 18:30 | 269 | 267
2018-03-12 19:00 | 267 | 265
2018-03-12 19:30 | 271 | 270
2018-03-12 20:00 | 262 | 261
2018-03-12 20:30 | 250 | 248
2018-03-12 21:00 | 239 | 237
2018-03-12 21:30 | 225 | 223
2018-03-12 22:00 | 213 | 211
2018-03-12 22:30 | 197 | 195
2018-03-12 23:00 | 185 | 183
2018-03-12 23:30 | 174 | 172
2018-03-13 | 166 | 165
2018-03-13 00:30 | 161 | 159
2018-03-13 01:00 | 156 | 154
2018-03-13 01:30 | 150 | 148
2018-03-13 02:00 | 147 | 145
2018-03-13 02:30 | 146 | 143
2018-03-13 03:00 | 142 | 139
2018-03-13 03:30 | 140 | 138
2018-03-13 04:00 | 137 | 135
2018-03-13 04:30 | 138 | 136
2018-03-13 05:00 | 140 | 139
2018-03-13 05:30 | 146 | 145
2018-03-13 06:00 | 154 | 153
2018-03-13 06:30 | 170 | 169
2018-03-13 07:00 | 184 | 183
2018-03-13 07:30 | 190 | 189
2018-03-13 08:00 | 189 | 187
2018-03-13 08:30 | 185 | 184
2018-03-13 09:00 | 180 | 178
2018-03-13 09:30 | 180 | 179
2018-03-13 10:00 | 178 | 177
2018-03-13 10:30 | 174 | 173
2018-03-13 11:00 | 175 | 174
2018-03-13 11:30 | 178 | 177
2018-03-13 12:00 | 185 | 184
2018-03-13 12:30 | 189 | 187
2018-03-13 13:00 | 185 | 183
2018-03-13 13:30 | 185 | 184
2018-03-13 14:00 | 193 | 192
2018-03-13 14:30 | 195 | 194
2018-03-13 15:00 | 196 | 195
2018-03-13 15:30 | 198 | 197
2018-03-13 16:00 | 202 | 201
2018-03-13 16:30 | 207 | 206
2018-03-13 17:00 | 220 | 218
2018-03-13 17:30 | 226 | 225
2018-03-13 18:00 | 239 | 237
2018-03-13 18:30 | 256 | 255
2018-03-13 19:00 | 269 | 268
2018-03-13 19:30 | 278 | 276
2018-03-13 20:00 | 271 | 269
2018-03-13 20:30 | 258 | 256
2018-03-13 21:00 | 246 | 245
2018-03-13 21:30 | 234 | 232
2018-03-13 22:00 | 220 | 218
2018-03-13 22:30 | 205 | 203
2018-03-13 23:00 | 192 | 190
2018-03-13 23:30 | 181 | 179
2018-03-14 | 170 | 168
2018-03-14 00:30 | 163 | 161
2018-03-14 01:00 | 158 | 156
2018-03-14 01:30 | 153 | 151
2018-03-14 02:00 | 150 | 148
2018-03-14 02:30 | 146 | 145
2018-03-14 03:00 | 146 | 145
2018-03-14 03:30 | 145 | 143
2018-03-14 04:00 | 142 | 140
2018-03-14 04:30 | 143 | 142
2018-03-14 05:00 | 147 | 145
2018-03-14 05:30 | 153 | 152
2018-03-14 06:00 | 163 | 161
2018-03-14 06:30 | 179 | 178
2018-03-14 07:00 | 192 | 191
2018-03-14 07:30 | 200 | 199
2018-03-14 08:00 | 198 | 197
2018-03-14 08:30 | 194 | 193
2018-03-14 09:00 | 191 | 190
2018-03-14 09:30 | 187 | 185
2018-03-14 10:00 | 180 | 178
2018-03-14 10:30 | 185 | 183
2018-03-14 11:00 | 184 | 182
2018-03-14 11:30 | 186 | 184
2018-03-14 12:00 | 180 | 179
2018-03-14 12:30 | 186 | 185
2018-03-14 13:00 | 190 | 188
2018-03-14 13:30 | 190 | 189
2018-03-14 14:00 | 191 | 189
2018-03-14 14:30 | 195 | 194
2018-03-14 15:00 | 201 | 200
2018-03-14 15:30 | 210 | 208
2018-03-14 16:00 | 220 | 218
2018-03-14 16:30 | 229 | 227
2018-03-14 17:00 | 238 | 237
2018-03-14 17:30 | 257 | 256
2018-03-14 18:00 | 266 | 265
2018-03-14 18:30 | 264 | 262
2018-03-14 19:00 | 278 | 277
2018-03-14 19:30 | 283 | 281
2018-03-14 20:00 | 277 | 275
2018-03-14 20:30 | 265 | 264
2018-03-14 21:00 | 256 | 254
2018-03-14 21:30 | 245 | 243
2018-03-14 22:00 | 229 | 228
2018-03-14 22:30 | 213 | 212
2018-03-14 23:00 | 199 | 197
2018-03-14 23:30 | 188 | 187
2018-03-15 | 180 | 178
2018-03-15 00:30 | 172 | 170
2018-03-15 01:00 | 166 | 164
2018-03-15 01:30 | 162 | 160
2018-03-15 02:00 | 158 | 156
2018-03-15 02:30 | 156 | 154
2018-03-15 03:00 | 155 | 153
2018-03-15 03:30 | 155 | 152
2018-03-15 04:00 | 154 | 152
2018-03-15 04:30 | 141 | 139
2018-03-15 05:00 | 118 | 116
2018-03-15 05:30 | 123 | 121
2018-03-15 06:00 | 132 | 130
2018-03-15 06:30 | 149 | 147
2018-03-15 07:00 | 158 | 156
2018-03-15 07:30 | 148 | 146
2018-03-15 08:00 | 123 | 121
2018-03-15 08:30 | 121 | 119
2018-03-15 09:00 | 137 | 136
2018-03-15 09:30 | 142 | 141
2018-03-15 10:00 | 136 | 135
2018-03-15 10:30 | 133 | 132
2018-03-15 11:00 | 127 | 126
2018-03-15 11:30 | 124 | 123
2018-03-15 12:00 | 126 | 124
2018-03-15 12:30 | 128 | 127
2018-03-15 13:00 | 102 | 100
2018-03-15 13:30 | 92 | 90
2018-03-15 14:00 | 97 | 96
2018-03-15 14:30 | 102 | 100
2018-03-15 15:00 | 105 | 103
2018-03-15 15:30 | 103 | 101
2018-03-15 16:00 | 114 | 112
2018-03-15 16:30 | 128 | 126
2018-03-15 17:00 | 168 | 166
2018-03-15 17:30 | 191 | 189
2018-03-15 18:00 | 188 | 186
2018-03-15 18:30 | 160 | 158
2018-03-15 19:00 | 166 | 164
2018-03-15 19:30 | 174 | 171
2018-03-15 20:00 | 166 | 163
2018-03-15 20:30 | 154 | 151
2018-03-15 21:00 | 153 | 151
2018-03-15 21:30 | 191 | 190
2018-03-15 22:00 | 219 | 218
2018-03-15 22:30 | 205 | 204
2018-03-15 23:00 | 194 | 193
2018-03-15 23:30 | 187 | 185
2018-03-16 | 177 | 175
2018-03-16 00:30 | 170 | 168
2018-03-16 01:00 | 164 | 162
2018-03-16 01:30 | 158 | 156
2018-03-16 02:00 | 154 | 153
2018-03-16 02:30 | 146 | 145
2018-03-16 03:00 | 142 | 141
2018-03-16 03:30 | 141 | 140
2018-03-16 04:00 | 141 | 139
2018-03-16 04:30 | 140 | 139
2018-03-16 05:00 | 142 | 141
2018-03-16 05:30 | 154 | 153
2018-03-16 06:00 | 156 | 154
2018-03-16 06:30 | 168 | 167
2018-03-16 07:00 | 182 | 181
2018-03-16 07:30 | 188 | 187
2018-03-16 08:00 | 186 | 185
2018-03-16 08:30 | 181 | 180
2018-03-16 09:00 | 179 | 178
2018-03-16 09:30 | 177 | 175
2018-03-16 10:00 | 176 | 175
2018-03-16 10:30 | 177 | 176
2018-03-16 11:00 | 176 | 175
2018-03-16 11:30 | 178 | 177
2018-03-16 12:00 | 184 | 182
2018-03-16 12:30 | 187 | 185
2018-03-16 13:00 | 188 | 186
2018-03-16 13:30 | 194 | 192
2018-03-16 14:00 | 198 | 196
2018-03-16 14:30 | 203 | 202
2018-03-16 15:00 | 208 | 207
2018-03-16 15:30 | 214 | 212
2018-03-16 16:00 | 221 | 219
2018-03-16 16:30 | 230 | 229
2018-03-16 17:00 | 240 | 238
2018-03-16 17:30 | 245 | 243
2018-03-16 18:00 | 256 | 255
2018-03-16 18:30 | 267 | 266
2018-03-16 19:00 | 276 | 274
2018-03-16 19:30 | 281 | 280
2018-03-16 20:00 | 272 | 270
2018-03-16 20:30 | 262 | 261
2018-03-16 21:00 | 251 | 250
2018-03-16 21:30 | 243 | 241
2018-03-16 22:00 | 234 | 232
2018-03-16 22:30 | 215 | 214
2018-03-16 23:00 | 205 | 203
2018-03-16 23:30 | 195 | 192
2018-03-17 | 185 | 183
2018-03-17 00:30 | 189 | 187
2018-03-17 01:00 | 186 | 185
2018-03-17 01:30 | 180 | 179
2018-03-17 02:00 | 176 | 175
2018-03-17 02:30 | 174 | 173
2018-03-17 03:00 | 171 | 170
2018-03-17 03:30 | 168 | 167
2018-03-17 04:00 | 167 | 166
2018-03-17 04:30 | 167 | 165
2018-03-17 05:00 | 168 | 167
2018-03-17 05:30 | 168 | 167
2018-03-17 06:00 | 171 | 170
2018-03-17 06:30 | 176 | 174
2018-03-17 07:00 | 179 | 178
2018-03-17 07:30 | 179 | 178
2018-03-17 08:00 | 177 | 176
2018-03-17 08:30 | 178 | 177
2018-03-17 09:00 | 180 | 179
2018-03-17 09:30 | 180 | 179
2018-03-17 10:00 | 175 | 174
2018-03-17 10:30 | 172 | 171
2018-03-17 11:00 | 171 | 170
2018-03-17 11:30 | 169 | 168
2018-03-17 12:00 | 173 | 172
2018-03-17 12:30 | 177 | 176
2018-03-17 13:00 | 171 | 170
2018-03-17 13:30 | 164 | 163
2018-03-17 14:00 | 171 | 170
2018-03-17 14:30 | 175 | 174
2018-03-17 15:00 | 179 | 177
2018-03-17 15:30 | 189 | 188
2018-03-17 16:00 | 199 | 198
2018-03-17 16:30 | 207 | 206
2018-03-17 17:00 | 219 | 218
2018-03-17 17:30 | 235 | 234
2018-03-17 18:00 | 243 | 242
2018-03-17 18:30 | 258 | 257
2018-03-17 19:00 | 267 | 266
2018-03-17 19:30 | 270 | 269
2018-03-17 20:00 | 261 | 261
2018-03-17 20:30 | 252 | 251
2018-03-17 21:00 | 243 | 242
2018-03-17 21:30 | 235 | 235
2018-03-17 22:00 | 227 | 226
2018-03-17 22:30 | 226 | 225
2018-03-17 23:00 | 223 | 222
2018-03-17 23:30 | 214 | 213
2018-03-18 | 205 | 205
2018-03-18 00:30 | 198 | 197
2018-03-18 01:00 | 193 | 192
2018-03-18 01:30 | 186 | 185
2018-03-18 02:00 | 183 | 182
2018-03-18 02:30 | 182 | 181
2018-03-18 03:00 | 179 | 178
2018-03-18 03:30 | 178 | 177
2018-03-18 04:00 | 176 | 174
2018-03-18 04:30 | 176 | 174
2018-03-18 05:00 | 173 | 172
2018-03-18 05:30 | 174 | 172
2018-03-18 06:00 | 175 | 174
2018-03-18 06:30 | 177 | 176
2018-03-18 07:00 | 177 | 176
2018-03-18 07:30 | 177 | 176
2018-03-18 08:00 | 174 | 173
2018-03-18 08:30 | 177 | 176
2018-03-18 09:00 | 184 | 184
2018-03-18 09:30 | 191 | 191
2018-03-18 10:00 | 194 | 194
2018-03-18 10:30 | 195 | 194
2018-03-18 11:00 | 193 | 192
2018-03-18 11:30 | 193 | 192
2018-03-18 12:00 | 199 | 198
2018-03-18 12:30 | 200 | 200
2018-03-18 13:00 | 204 | 203
2018-03-18 13:30 | 195 | 195
2018-03-18 14:00 | 202 | 202
2018-03-18 14:30 | 201 | 201
2018-03-18 15:00 | 206 | 205
2018-03-18 15:30 | 212 | 211
2018-03-18 16:00 | 215 | 214
2018-03-18 16:30 | 227 | 226
2018-03-18 17:00 | 230 | 230
2018-03-18 17:30 | 243 | 242
2018-03-18 18:00 | 257 | 257
2018-03-18 18:30 | 273 | 273
2018-03-18 19:00 | 286 | 285
2018-03-18 19:30 | 299 | 298
2018-03-18 20:00 | 293 | 292
2018-03-18 20:30 | 279 | 278
2018-03-18 21:00 | 270 | 269
2018-03-18 21:30 | 259 | 258
2018-03-18 22:00 | 242 | 241
2018-03-18 22:30 | 228 | 227
2018-03-18 23:00 | 215 | 215
2018-03-18 23:30 | 207 | 206
2018-03-19 | 198 | 197
2018-03-19 00:30 | 191 | 190
2018-03-19 01:00 | 186 | 185
2018-03-19 01:30 | 180 | 179
2018-03-19 02:00 | 178 | 177
2018-03-19 02:30 | 176 | 175
2018-03-19 03:00 | 173 | 172
2018-03-19 03:30 | 171 | 170
2018-03-19 04:00 | 171 | 170
2018-03-19 04:30 | 171 | 170
2018-03-19 05:00 | 173 | 172
2018-03-19 05:30 | 180 | 179
2018-03-19 06:00 | 189 | 189
2018-03-19 06:30 | 204 | 204
2018-03-19 07:00 | 222 | 222
2018-03-19 07:30 | 235 | 234
2018-03-19 08:00 | 233 | 231
2018-03-19 08:30 | 221 | 219
2018-03-19 09:00 | 191 | 190
2018-03-19 09:30 | 191 | 189
2018-03-19 10:00 | 190 | 189
2018-03-19 10:30 | 191 | 190
2018-03-19 11:00 | 188 | 187
2018-03-19 11:30 | 180 | 179
2018-03-19 12:00 | 161 | 159
2018-03-19 12:30 | 130 | 129
2018-03-19 13:00 | 133 | 132
2018-03-19 13:30 | 139 | 138
2018-03-19 14:00 | 139 | 138
2018-03-19 14:30 | 141 | 140
2018-03-19 15:00 | 143 | 141
2018-03-19 15:30 | 144 | 143
2018-03-19 16:00 | 143 | 142
2018-03-19 16:30 | 141 | 139
2018-03-19 17:00 | 147 | 146
2018-03-19 17:30 | 150 | 149
2018-03-19 18:00 | 158 | 156
2018-03-19 18:30 | 175 | 173
2018-03-19 19:00 | 186 | 185
2018-03-19 19:30 | 188 | 186
2018-03-19 20:00 | 178 | 177
2018-03-19 20:30 | 167 | 166
2018-03-19 21:00 | 154 | 153
2018-03-19 21:30 | 141 | 139
2018-03-19 22:00 | 128 | 126
2018-03-19 22:30 | 125 | 123
2018-03-19 23:00 | 150 | 148
2018-03-19 23:30 | 150 | 148
2018-03-20 | 140 | 138
2018-03-20 00:30 | 131 | 129
2018-03-20 01:00 | 125 | 124
2018-03-20 01:30 | 122 | 120
2018-03-20 02:00 | 118 | 117
2018-03-20 02:30 | 117 | 115
2018-03-20 03:00 | 113 | 111
2018-03-20 03:30 | 111 | 109
2018-03-20 04:00 | 107 | 106
2018-03-20 04:30 | 111 | 109
2018-03-20 05:00 | 111 | 109
2018-03-20 05:30 | 116 | 115
2018-03-20 06:00 | 124 | 123
2018-03-20 06:30 | 104 | 103
2018-03-20 07:00 | 113 | 112
2018-03-20 07:30 | 124 | 123
2018-03-20 08:00 | 130 | 130
2018-03-20 08:30 | 125 | 124
2018-03-20 09:00 | 122 | 121
2018-03-20 09:30 | 117 | 116
2018-03-20 10:00 | 119 | 118
2018-03-20 10:30 | 120 | 119
2018-03-20 11:00 | 118 | 117
2018-03-20 11:30 | 119 | 118
2018-03-20 12:00 | 119 | 118
2018-03-20 12:30 | 122 | 121
2018-03-20 13:00 | 123 | 122
2018-03-20 13:30 | 124 | 123
2018-03-20 14:00 | 129 | 128
2018-03-20 14:30 | 136 | 135
2018-03-20 15:00 | 140 | 139
2018-03-20 15:30 | 146 | 145
2018-03-20 16:00 | 156 | 155
2018-03-20 16:30 | 162 | 161
2018-03-20 17:00 | 174 | 173
2018-03-20 17:30 | 175 | 174
2018-03-20 18:00 | 180 | 179
2018-03-20 18:30 | 195 | 194
2018-03-20 19:00 | 213 | 212
2018-03-20 19:30 | 217 | 216
2018-03-20 20:00 | 210 | 209
2018-03-20 20:30 | 197 | 196
2018-03-20 21:00 | 183 | 182
2018-03-20 21:30 | 170 | 169
2018-03-20 22:00 | 159 | 158
2018-03-20 22:30 | 174 | 172
2018-03-20 23:00 | 190 | 189
2018-03-20 23:30 | 222 | 221
2018-03-21 | 213 | 213
2018-03-21 00:30 | 206 | 205
2018-03-21 01:00 | 198 | 197
2018-03-21 01:30 | 192 | 190
2018-03-21 02:00 | 188 | 187
2018-03-21 02:30 | 187 | 185
2018-03-21 03:00 | 184 | 183
2018-03-21 03:30 | 184 | 183
2018-03-21 04:00 | 184 | 183
2018-03-21 04:30 | 184 | 183
2018-03-21 05:00 | 185 | 183
2018-03-21 05:30 | 192 | 191
2018-03-21 06:00 | 200 | 199
2018-03-21 06:30 | 218 | 217
2018-03-21 07:00 | 232 | 231
2018-03-21 07:30 | 242 | 241
2018-03-21 08:00 | 242 | 241
2018-03-21 08:30 | 242 | 241
2018-03-21 09:00 | 240 | 239
2018-03-21 09:30 | 248 | 247
2018-03-21 10:00 | 246 | 245
2018-03-21 10:30 | 240 | 239
2018-03-21 11:00 | 245 | 244
2018-03-21 11:30 | 242 | 241
2018-03-21 12:00 | 241 | 239
2018-03-21 12:30 | 247 | 246
2018-03-21 13:00 | 248 | 246
2018-03-21 13:30 | 241 | 240
2018-03-21 14:00 | 246 | 245
2018-03-21 14:30 | 251 | 250
2018-03-21 15:00 | 262 | 261
2018-03-21 15:30 | 265 | 264
2018-03-21 16:00 | 277 | 276
2018-03-21 16:30 | 268 | 267
2018-03-21 17:00 | 262 | 260
2018-03-21 17:30 | 266 | 265
2018-03-21 18:00 | 273 | 272
2018-03-21 18:30 | 285 | 283
2018-03-21 19:00 | 295 | 294
2018-03-21 19:30 | 291 | 290
2018-03-21 20:00 | 279 | 278
2018-03-21 20:30 | 265 | 263
2018-03-21 21:00 | 255 | 254
2018-03-21 21:30 | 258 | 257
2018-03-21 22:00 | 254 | 253
2018-03-21 22:30 | 238 | 236
2018-03-21 23:00 | 223 | 222
2018-03-21 23:30 | 212 | 211
2018-03-22 | 204 | 203
2018-03-22 00:30 | 198 | 196
2018-03-22 01:00 | 191 | 190
2018-03-22 01:30 | 184 | 182
2018-03-22 02:00 | 179 | 178
2018-03-22 02:30 | 175 | 173
2018-03-22 03:00 | 175 | 174
2018-03-22 03:30 | 173 | 172
2018-03-22 04:00 | 172 | 171
2018-03-22 04:30 | 173 | 172
2018-03-22 05:00 | 175 | 175
2018-03-22 05:30 | 181 | 180
2018-03-22 06:00 | 190 | 189
2018-03-22 06:30 | 209 | 208
2018-03-22 07:00 | 224 | 223
2018-03-22 07:30 | 237 | 236
2018-03-22 08:00 | 247 | 245
2018-03-22 08:30 | 250 | 249
2018-03-22 09:00 | 241 | 239
2018-03-22 09:30 | 231 | 229
2018-03-22 10:00 | 226 | 225
2018-03-22 10:30 | 227 | 225
2018-03-22 11:00 | 228 | 227
2018-03-22 11:30 | 223 | 222
2018-03-22 12:00 | 229 | 228
2018-03-22 12:30 | 230 | 229
2018-03-22 13:00 | 235 | 233
2018-03-22 13:30 | 240 | 238
2018-03-22 14:00 | 237 | 235
2018-03-22 14:30 | 237 | 236
2018-03-22 15:00 | 247 | 246
2018-03-22 15:30 | 243 | 242
2018-03-22 16:00 | 251 | 249
2018-03-22 16:30 | 253 | 251
2018-03-22 17:00 | 247 | 245
2018-03-22 17:30 | 242 | 240
2018-03-22 18:00 | 271 | 270
2018-03-22 18:30 | 285 | 284
2018-03-22 19:00 | 297 | 296
2018-03-22 19:30 | 296 | 294
2018-03-22 20:00 | 284 | 283
2018-03-22 20:30 | 279 | 277
2018-03-22 21:00 | 265 | 263
2018-03-22 21:30 | 254 | 252
2018-03-22 22:00 | 240 | 239
2018-03-22 22:30 | 227 | 226
2018-03-22 23:00 | 214 | 213
2018-03-22 23:30 | 205 | 204
2018-03-23 | 197 | 196
2018-03-23 00:30 | 191 | 189
2018-03-23 01:00 | 186 | 184
2018-03-23 01:30 | 181 | 179
2018-03-23 02:00 | 177 | 176
2018-03-23 02:30 | 174 | 173
2018-03-23 03:00 | 173 | 172
2018-03-23 03:30 | 173 | 172
2018-03-23 04:00 | 170 | 169
2018-03-23 04:30 | 173 | 172
2018-03-23 05:00 | 175 | 174
2018-03-23 05:30 | 181 | 180
2018-03-23 06:00 | 189 | 188
2018-03-23 06:30 | 207 | 206
2018-03-23 07:00 | 221 | 220
2018-03-23 07:30 | 236 | 235
2018-03-23 08:00 | 251 | 250
2018-03-23 08:30 | 261 | 260
2018-03-23 09:00 | 260 | 259
2018-03-23 09:30 | 261 | 260
2018-03-23 10:00 | 255 | 254
2018-03-23 10:30 | 245 | 245
2018-03-23 11:00 | 255 | 254
2018-03-23 11:30 | 255 | 254
2018-03-23 12:00 | 239 | 238
2018-03-23 12:30 | 220 | 219
2018-03-23 13:00 | 223 | 222
2018-03-23 13:30 | 220 | 219
2018-03-23 14:00 | 221 | 220
2018-03-23 14:30 | 216 | 215
2018-03-23 15:00 | 219 | 217
2018-03-23 15:30 | 226 | 225
2018-03-23 16:00 | 234 | 232
2018-03-23 16:30 | 239 | 238
2018-03-23 17:00 | 242 | 241
2018-03-23 17:30 | 242 | 241
2018-03-23 18:00 | 246 | 244
2018-03-23 18:30 | 250 | 249
2018-03-23 19:00 | 255 | 254
2018-03-23 19:30 | 255 | 253
2018-03-23 20:00 | 246 | 244
2018-03-23 20:30 | 237 | 236
2018-03-23 21:00 | 228 | 227
2018-03-23 21:30 | 221 | 220
2018-03-23 22:00 | 214 | 213
2018-03-23 22:30 | 213 | 212
2018-03-23 23:00 | 209 | 208
2018-03-23 23:30 | 199 | 198
2018-03-24 | 191 | 190
2018-03-24 00:30 | 184 | 183
2018-03-24 01:00 | 180 | 178
2018-03-24 01:30 | 176 | 175
2018-03-24 02:00 | 173 | 171
2018-03-24 02:30 | 170 | 168
2018-03-24 03:00 | 166 | 165
2018-03-24 03:30 | 165 | 163
2018-03-24 04:00 | 164 | 162
2018-03-24 04:30 | 166 | 164
2018-03-24 05:00 | 166 | 164
2018-03-24 05:30 | 169 | 167
2018-03-24 06:00 | 171 | 170
2018-03-24 06:30 | 179 | 177
2018-03-24 07:00 | 185 | 183
2018-03-24 07:30 | 196 | 195
2018-03-24 08:00 | 204 | 202
2018-03-24 08:30 | 211 | 210
2018-03-24 09:00 | 216 | 215
2018-03-24 09:30 | 213 | 212
2018-03-24 10:00 | 216 | 215
2018-03-24 10:30 | 220 | 219
2018-03-24 11:00 | 216 | 215
2018-03-24 11:30 | 216 | 215
2018-03-24 12:00 | 223 | 222
2018-03-24 12:30 | 224 | 223
2018-03-24 13:00 | 223 | 222
2018-03-24 13:30 | 225 | 224
2018-03-24 14:00 | 220 | 219
2018-03-24 14:30 | 211 | 210
2018-03-24 15:00 | 214 | 213
2018-03-24 15:30 | 215 | 214
2018-03-24 16:00 | 211 | 210
2018-03-24 16:30 | 216 | 214
2018-03-24 17:00 | 224 | 222
2018-03-24 17:30 | 232 | 231
2018-03-24 18:00 | 239 | 238
2018-03-24 18:30 | 245 | 244
2018-03-24 19:00 | 247 | 246
2018-03-24 19:30 | 242 | 241
2018-03-24 20:00 | 233 | 231
2018-03-24 20:30 | 221 | 220
2018-03-24 21:00 | 215 | 214
2018-03-24 21:30 | 207 | 205
2018-03-24 22:00 | 199 | 197
2018-03-24 22:30 | 187 | 186
2018-03-24 23:00 | 179 | 177
2018-03-24 23:30 | 170 | 168
2018-03-25 | 163 | 160
2018-03-25 00:30 | 158 | 155
2018-03-25 01:00 | 152 | 149
2018-03-25 01:30 | 150 | 147
2018-03-25 02:00 | 147 | 144
2018-03-25 02:30 | 142 | 141
2018-03-25 03:00 | 142 | 141
2018-03-25 03:30 | 142 | 141
2018-03-25 04:00 | 140 | 139
2018-03-25 04:30 | 140 | 139
2018-03-25 05:00 | 140 | 138
2018-03-25 05:30 | 141 | 140
2018-03-25 06:00 | 143 | 142
2018-03-25 06:30 | 146 | 145
2018-03-25 07:00 | 150 | 149
2018-03-25 07:30 | 159 | 157
2018-03-25 08:00 | 168 | 167
2018-03-25 08:30 | 180 | 178
2018-03-25 09:00 | 185 | 184
2018-03-25 09:30 | 190 | 189
2018-03-25 10:00 | 189 | 188
2018-03-25 10:30 | 193 | 192
2018-03-25 11:00 | 196 | 195
2018-03-25 11:30 | 192 | 192
2018-03-25 12:00 | 194 | 193
2018-03-25 12:30 | 199 | 197
2018-03-25 13:00 | 201 | 200
2018-03-25 13:30 | 191 | 190
2018-03-25 14:00 | 197 | 196
2018-03-25 14:30 | 195 | 193
2018-03-25 15:00 | 201 | 200
2018-03-25 15:30 | 201 | 200
2018-03-25 16:00 | 198 | 197
2018-03-25 16:30 | 208 | 206
2018-03-25 17:00 | 215 | 214
2018-03-25 17:30 | 220 | 218
2018-03-25 18:00 | 233 | 232
2018-03-25 18:30 | 243 | 242
2018-03-25 19:00 | 252 | 251
2018-03-25 19:30 | 246 | 245
2018-03-25 20:00 | 238 | 237
2018-03-25 20:30 | 229 | 227
2018-03-25 21:00 | 219 | 218
2018-03-25 21:30 | 223 | 221
2018-03-25 22:00 | 215 | 213
2018-03-25 22:30 | 203 | 201
2018-03-25 23:00 | 189 | 187
2018-03-25 23:30 | 180 | 179
2018-03-26 | 174 | 172
2018-03-26 00:30 | 172 | 170
2018-03-26 01:00 | 167 | 165
2018-03-26 01:30 | 163 | 161
2018-03-26 02:00 | 161 | 159
2018-03-26 02:30 | 161 | 159
2018-03-26 03:00 | 158 | 156
2018-03-26 03:30 | 158 | 156
2018-03-26 04:00 | 159 | 157
2018-03-26 04:30 | 160 | 158
2018-03-26 05:00 | 163 | 161
2018-03-26 05:30 | 169 | 166
2018-03-26 06:00 | 180 | 178
2018-03-26 06:30 | 198 | 196
2018-03-26 07:00 | 217 | 216
2018-03-26 07:30 | 238 | 237
2018-03-26 08:00 | 248 | 247
2018-03-26 08:30 | 251 | 249
2018-03-26 09:00 | 245 | 244
2018-03-26 09:30 | 248 | 246
2018-03-26 10:00 | 250 | 248
2018-03-26 10:30 | 248 | 247
2018-03-26 11:00 | 246 | 245
2018-03-26 11:30 | 244 | 242
2018-03-26 12:00 | 241 | 240
2018-03-26 12:30 | 247 | 245
2018-03-26 13:00 | 249 | 248
2018-03-26 13:30 | 248 | 246
2018-03-26 14:00 | 246 | 245
2018-03-26 14:30 | 249 | 247
2018-03-26 15:00 | 251 | 250
2018-03-26 15:30 | 255 | 254
2018-03-26 16:00 | 259 | 258
2018-03-26 16:30 | 261 | 260
2018-03-26 17:00 | 264 | 262
2018-03-26 17:30 | 262 | 260
2018-03-26 18:00 | 267 | 265
2018-03-26 18:30 | 276 | 274
2018-03-26 19:00 | 282 | 280
2018-03-26 19:30 | 275 | 274
2018-03-26 20:00 | 264 | 262
2018-03-26 20:30 | 255 | 253
2018-03-26 21:00 | 243 | 241
2018-03-26 21:30 | 231 | 229
2018-03-26 22:00 | 220 | 218
2018-03-26 22:30 | 208 | 207
2018-03-26 23:00 | 196 | 194
2018-03-26 23:30 | 188 | 186
2018-03-27 | 186 | 184
2018-03-27 00:30 | 184 | 182
2018-03-27 01:00 | 180 | 178
2018-03-27 01:30 | 176 | 174
2018-03-27 02:00 | 172 | 170
2018-03-27 02:30 | 168 | 166
2018-03-27 03:00 | 168 | 166
2018-03-27 03:30 | 171 | 170
2018-03-27 04:00 | 177 | 176
2018-03-27 04:30 | 177 | 175
2018-03-27 05:00 | 179 | 177
2018-03-27 05:30 | 185 | 184
2018-03-27 06:00 | 193 | 192
2018-03-27 06:30 | 212 | 211
2018-03-27 07:00 | 229 | 228
2018-03-27 07:30 | 249 | 248
2018-03-27 08:00 | 258 | 257
2018-03-27 08:30 | 262 | 261
2018-03-27 09:00 | 265 | 264
2018-03-27 09:30 | 267 | 266
2018-03-27 10:00 | 262 | 261
2018-03-27 10:30 | 253 | 252
2018-03-27 11:00 | 249 | 248
2018-03-27 11:30 | 246 | 245
2018-03-27 12:00 | 228 | 227
2018-03-27 12:30 | 192 | 191
2018-03-27 13:00 | 188 | 186
2018-03-27 13:30 | 188 | 187
2018-03-27 14:00 | 235 | 234
2018-03-27 14:30 | 251 | 250
2018-03-27 15:00 | 250 | 249
2018-03-27 15:30 | 260 | 258
2018-03-27 16:00 | 269 | 268
2018-03-27 16:30 | 272 | 271
2018-03-27 17:00 | 265 | 264
2018-03-27 17:30 | 267 | 265
2018-03-27 18:00 | 272 | 270
2018-03-27 18:30 | 281 | 279
2018-03-27 19:00 | 293 | 291
2018-03-27 19:30 | 290 | 289
2018-03-27 20:00 | 281 | 280
2018-03-27 20:30 | 273 | 272
2018-03-27 21:00 | 263 | 261
2018-03-27 21:30 | 250 | 248
2018-03-27 22:00 | 235 | 234
2018-03-27 22:30 | 219 | 218
2018-03-27 23:00 | 206 | 205
2018-03-27 23:30 | 199 | 198
2018-03-28 | 192 | 191
2018-03-28 00:30 | 184 | 184
2018-03-28 01:00 | 176 | 175
2018-03-28 01:30 | 173 | 173
2018-03-28 02:00 | 170 | 170
2018-03-28 02:30 | 167 | 166
2018-03-28 03:00 | 166 | 165
2018-03-28 03:30 | 164 | 163
2018-03-28 04:00 | 164 | 163
2018-03-28 04:30 | 167 | 166
2018-03-28 05:00 | 172 | 171
2018-03-28 05:30 | 179 | 178
2018-03-28 06:00 | 188 | 188
2018-03-28 06:30 | 208 | 207
2018-03-28 07:00 | 221 | 220
2018-03-28 07:30 | 238 | 237
2018-03-28 08:00 | 244 | 243
2018-03-28 08:30 | 247 | 247
2018-03-28 09:00 | 220 | 219
2018-03-28 09:30 | 180 | 180
2018-03-28 10:00 | 178 | 177
2018-03-28 10:30 | 189 | 189
2018-03-28 11:00 | 174 | 173
2018-03-28 11:30 | 172 | 171
2018-03-28 12:00 | 179 | 178
2018-03-28 12:30 | 188 | 187
2018-03-28 13:00 | 196 | 196
2018-03-28 13:30 | 208 | 207
2018-03-28 14:00 | 194 | 193
2018-03-28 14:30 | 181 | 180
2018-03-28 15:00 | 154 | 152
2018-03-28 15:30 | 157 | 155
2018-03-28 16:00 | 162 | 161
2018-03-28 16:30 | 162 | 161
2018-03-28 17:00 | 167 | 166
2018-03-28 17:30 | 166 | 165
2018-03-28 18:00 | 169 | 168
2018-03-28 18:30 | 178 | 177
2018-03-28 19:00 | 193 | 192
2018-03-28 19:30 | 193 | 192
2018-03-28 20:00 | 184 | 182
2018-03-28 20:30 | 173 | 172
2018-03-28 21:00 | 164 | 162
2018-03-28 21:30 | 152 | 151
2018-03-28 22:00 | 137 | 136
2018-03-28 22:30 | 121 | 119
2018-03-28 23:00 | 142 | 141
2018-03-28 23:30 | 141 | 140
2018-03-29 | 129 | 128
2018-03-29 00:30 | 121 | 120
2018-03-29 01:00 | 114 | 113
2018-03-29 01:30 | 109 | 108
2018-03-29 02:00 | 104 | 103
2018-03-29 02:30 | 103 | 102
2018-03-29 03:00 | 101 | 99
2018-03-29 03:30 | 99 | 97
2018-03-29 04:00 | 99 | 97
2018-03-29 04:30 | 100 | 99
2018-03-29 05:00 | 101 | 100
2018-03-29 05:30 | 108 | 107
2018-03-29 06:00 | 131 | 130
2018-03-29 06:30 | 149 | 148
2018-03-29 07:00 | 160 | 159
2018-03-29 07:30 | 165 | 164
2018-03-29 08:00 | 164 | 163
2018-03-29 08:30 | 162 | 161
2018-03-29 09:00 | 155 | 154
2018-03-29 09:30 | 105 | 104
2018-03-29 10:00 | 99 | 98
2018-03-29 10:30 | 87 | 86
2018-03-29 11:00 | 115 | 114
2018-03-29 11:30 | 123 | 122
2018-03-29 12:00 | 127 | 126
2018-03-29 12:30 | 123 | 122
2018-03-29 13:00 | 96 | 95
2018-03-29 13:30 | 84 | 82
2018-03-29 14:00 | 82 | 80
2018-03-29 14:30 | 56 | 53
2018-03-29 15:00 | 64 | 63
2018-03-29 15:30 | 82 | 81
2018-03-29 16:00 | 96 | 95
2018-03-29 16:30 | 127 | 126
2018-03-29 17:00 | 136 | 135
2018-03-29 17:30 | 142 | 141
2018-03-29 18:00 | 155 | 153
2018-03-29 18:30 | 160 | 158
2018-03-29 19:00 | 172 | 170
2018-03-29 19:30 | 170 | 169
2018-03-29 20:00 | 162 | 160
2018-03-29 20:30 | 182 | 181
2018-03-29 21:00 | 182 | 181
2018-03-29 21:30 | 168 | 166
2018-03-29 22:00 | 156 | 155
2018-03-29 22:30 | 142 | 140
2018-03-29 23:00 | 154 | 153
2018-03-29 23:30 | 184 | 183
2018-03-30 | 177 | 175
2018-03-30 00:30 | 168 | 166
2018-03-30 01:00 | 161 | 159
2018-03-30 01:30 | 155 | 153
2018-03-30 02:00 | 150 | 148
2018-03-30 02:30 | 146 | 143
2018-03-30 03:00 | 142 | 140
2018-03-30 03:30 | 139 | 137
2018-03-30 04:00 | 138 | 137
2018-03-30 04:30 | 138 | 136
2018-03-30 05:00 | 138 | 136
2018-03-30 05:30 | 139 | 138
2018-03-30 06:00 | 141 | 140
2018-03-30 06:30 | 148 | 146
2018-03-30 07:00 | 148 | 146
2018-03-30 07:30 | 146 | 144
2018-03-30 08:00 | 142 | 140
2018-03-30 08:30 | 139 | 138
2018-03-30 09:00 | 152 | 151
2018-03-30 09:30 | 157 | 156
2018-03-30 10:00 | 155 | 154
2018-03-30 10:30 | 150 | 149
2018-03-30 11:00 | 138 | 137
2018-03-30 11:30 | 138 | 137
2018-03-30 12:00 | 144 | 143
2018-03-30 12:30 | 150 | 149
2018-03-30 13:00 | 154 | 153
2018-03-30 13:30 | 157 | 156
2018-03-30 14:00 | 163 | 162
2018-03-30 14:30 | 171 | 170
2018-03-30 15:00 | 179 | 178
2018-03-30 15:30 | 192 | 191
2018-03-30 16:00 | 202 | 200
2018-03-30 16:30 | 214 | 213
2018-03-30 17:00 | 224 | 223
2018-03-30 17:30 | 238 | 236
2018-03-30 18:00 | 252 | 251
2018-03-30 18:30 | 263 | 261
2018-03-30 19:00 | 272 | 271
2018-03-30 19:30 | 275 | 274
2018-03-30 20:00 | 264 | 263
2018-03-30 20:30 | 254 | 253
2018-03-30 21:00 | 244 | 242
2018-03-30 21:30 | 234 | 232
2018-03-30 22:00 | 225 | 223
2018-03-30 22:30 | 211 | 210
2018-03-30 23:00 | 202 | 200
2018-03-30 23:30 | 192 | 190
2018-03-31 | 181 | 180
2018-03-31 00:30 | 173 | 172
2018-03-31 01:00 | 167 | 166
2018-03-31 01:30 | 162 | 161
2018-03-31 02:00 | 158 | 157
2018-03-31 02:30 | 155 | 154
2018-03-31 03:00 | 152 | 151
2018-03-31 03:30 | 149 | 148
2018-03-31 04:00 | 149 | 148
2018-03-31 04:30 | 150 | 149
2018-03-31 05:00 | 149 | 147
2018-03-31 05:30 | 152 | 151
2018-03-31 06:00 | 153 | 152
2018-03-31 06:30 | 156 | 155
2018-03-31 07:00 | 159 | 158
2018-03-31 07:30 | 161 | 160
2018-03-31 08:00 | 158 | 157
2018-03-31 08:30 | 157 | 156
2018-03-31 09:00 | 158 | 157
2018-03-31 09:30 | 159 | 158
2018-03-31 10:00 | 164 | 163
2018-03-31 10:30 | 164 | 162
2018-03-31 11:00 | 163 | 162
2018-03-31 11:30 | 165 | 164
2018-03-31 12:00 | 167 | 165
2018-03-31 12:30 | 171 | 170
2018-03-31 13:00 | 175 | 173
2018-03-31 13:30 | 175 | 174
2018-03-31 14:00 | 187 | 186
2018-03-31 14:30 | 194 | 193
2018-03-31 15:00 | 196 | 195
2018-03-31 15:30 | 192 | 191
2018-03-31 16:00 | 202 | 201
2018-03-31 16:30 | 207 | 206
2018-03-31 17:00 | 217 | 216
2018-03-31 17:30 | 232 | 231
2018-03-31 18:00 | 242 | 241
2018-03-31 18:30 | 251 | 250
2018-03-31 19:00 | 257 | 256
2018-03-31 19:30 | 257 | 256
2018-03-31 20:00 | 249 | 247
2018-03-31 20:30 | 239 | 237
2018-03-31 21:00 | 231 | 230
2018-03-31 21:30 | 222 | 220
2018-03-31 22:00 | 214 | 212
2018-03-31 22:30 | 202 | 200
2018-03-31 23:00 | 195 | 193
2018-03-31 23:30 | 186 | 184
2018-04-01 | 177 | 175
2018-04-01 00:30 | 172 | 170
2018-04-01 01:00 | 164 | 162
2018-04-01 01:30 | 159 | 157
2018-04-01 02:00 | 157 | 155
2018-04-01 02:30 | 153 | 151
2018-04-01 03:00 | 150 | 148
2018-04-01 03:30 | 150 | 148
2018-04-01 04:00 | 146 | 145
2018-04-01 04:30 | 146 | 145
2018-04-01 05:00 | 146 | 145
2018-04-01 05:30 | 147 | 146
2018-04-01 06:00 | 148 | 147
2018-04-01 06:30 | 152 | 151
2018-04-01 07:00 | 155 | 154
2018-04-01 07:30 | 156 | 155
2018-04-01 08:00 | 156 | 155
2018-04-01 08:30 | 169 | 167
2018-04-01 09:00 | 177 | 176
2018-04-01 09:30 | 167 | 166
2018-04-01 10:00 | 173 | 172
2018-04-01 10:30 | 173 | 172
2018-04-01 11:00 | 164 | 162
2018-04-01 11:30 | 159 | 157
2018-04-01 12:00 | 166 | 164
2018-04-01 12:30 | 167 | 166
2018-04-01 13:00 | 174 | 172
2018-04-01 13:30 | 176 | 175
2018-04-01 14:00 | 171 | 170
2018-04-01 14:30 | 169 | 168
2018-04-01 15:00 | 185 | 183
2018-04-01 15:30 | 190 | 188
2018-04-01 16:00 | 193 | 191
2018-04-01 16:30 | 191 | 190
2018-04-01 17:00 | 204 | 203
2018-04-01 17:30 | 207 | 205
2018-04-01 18:00 | 223 | 222
2018-04-01 18:30 | 238 | 237
2018-04-01 19:00 | 248 | 246
2018-04-01 19:30 | 247 | 245
2018-04-01 20:00 | 239 | 238
2018-04-01 20:30 | 230 | 229
2018-04-01 21:00 | 219 | 218
2018-04-01 21:30 | 213 | 212
2018-04-01 22:00 | 205 | 204
2018-04-01 22:30 | 197 | 195
2018-04-01 23:00 | 189 | 188
2018-04-01 23:30 | 177 | 176
2018-04-02 | 167 | 165
2018-04-02 00:30 | 163 | 162
2018-04-02 01:00 | 159 | 157
2018-04-02 01:30 | 155 | 154
2018-04-02 02:00 | 150 | 149
2018-04-02 02:30 | 147 | 146
2018-04-02 03:00 | 146 | 144
2018-04-02 03:30 | 143 | 142
2018-04-02 04:00 | 144 | 143
2018-04-02 04:30 | 143 | 142
2018-04-02 05:00 | 143 | 142
2018-04-02 05:30 | 145 | 144
2018-04-02 06:00 | 147 | 146
2018-04-02 06:30 | 155 | 153
2018-04-02 07:00 | 156 | 155
2018-04-02 07:30 | 159 | 158
2018-04-02 08:00 | 162 | 160
2018-04-02 08:30 | 159 | 157
2018-04-02 09:00 | 163 | 161
2018-04-02 09:30 | 170 | 168
2018-04-02 10:00 | 173 | 172
2018-04-02 10:30 | 167 | 166
2018-04-02 11:00 | 162 | 161
2018-04-02 11:30 | 177 | 175
2018-04-02 12:00 | 183 | 182
2018-04-02 12:30 | 183 | 182
2018-04-02 13:00 | 180 | 179
2018-04-02 13:30 | 176 | 175
2018-04-02 14:00 | 174 | 172
2018-04-02 14:30 | 178 | 177
2018-04-02 15:00 | 182 | 181
2018-04-02 15:30 | 191 | 190
2018-04-02 16:00 | 200 | 199
2018-04-02 16:30 | 214 | 212
2018-04-02 17:00 | 214 | 213
2018-04-02 17:30 | 229 | 228
2018-04-02 18:00 | 243 | 241
2018-04-02 18:30 | 253 | 252
2018-04-02 19:00 | 264 | 263
2018-04-02 19:30 | 257 | 256
2018-04-02 20:00 | 247 | 245
2018-04-02 20:30 | 237 | 235
2018-04-02 21:00 | 229 | 228
2018-04-02 21:30 | 218 | 217
2018-04-02 22:00 | 209 | 207
2018-04-02 22:30 | 196 | 195
2018-04-02 23:00 | 187 | 185
2018-04-02 23:30 | 177 | 175
2018-04-03 | 170 | 168
2018-04-03 00:30 | 163 | 161
2018-04-03 01:00 | 157 | 155
2018-04-03 01:30 | 150 | 148
2018-04-03 02:00 | 150 | 148
2018-04-03 02:30 | 150 | 148
2018-04-03 03:00 | 146 | 145
2018-04-03 03:30 | 146 | 145
2018-04-03 04:00 | 146 | 145
2018-04-03 04:30 | 146 | 145
2018-04-03 05:00 | 146 | 145
2018-04-03 05:30 | 154 | 152
2018-04-03 06:00 | 160 | 159
2018-04-03 06:30 | 176 | 175
2018-04-03 07:00 | 187 | 186
2018-04-03 07:30 | 198 | 197
2018-04-03 08:00 | 199 | 198
2018-04-03 08:30 | 198 | 197
2018-04-03 09:00 | 195 | 193
2018-04-03 09:30 | 193 | 191
2018-04-03 10:00 | 191 | 189
2018-04-03 10:30 | 189 | 188
2018-04-03 11:00 | 195 | 193
2018-04-03 11:30 | 192 | 190
2018-04-03 12:00 | 194 | 192
2018-04-03 12:30 | 193 | 192
2018-04-03 13:00 | 196 | 194
2018-04-03 13:30 | 205 | 203
2018-04-03 14:00 | 209 | 207
2018-04-03 14:30 | 213 | 211
2018-04-03 15:00 | 216 | 214
2018-04-03 15:30 | 215 | 214
2018-04-03 16:00 | 220 | 219
2018-04-03 16:30 | 224 | 223
2018-04-03 17:00 | 234 | 233
2018-04-03 17:30 | 243 | 242
2018-04-03 18:00 | 253 | 252
2018-04-03 18:30 | 265 | 264
2018-04-03 19:00 | 275 | 274
2018-04-03 19:30 | 272 | 271
2018-04-03 20:00 | 258 | 257
2018-04-03 20:30 | 248 | 247
2018-04-03 21:00 | 239 | 238
2018-04-03 21:30 | 229 | 227
2018-04-03 22:00 | 217 | 216
2018-04-03 22:30 | 203 | 202
2018-04-03 23:00 | 191 | 190
2018-04-03 23:30 | 179 | 178
2018-04-04 | 169 | 168
2018-04-04 00:30 | 162 | 161
2018-04-04 01:00 | 157 | 156
2018-04-04 01:30 | 153 | 152
2018-04-04 02:00 | 148 | 147
2018-04-04 02:30 | 146 | 145
2018-04-04 03:00 | 145 | 143
2018-04-04 03:30 | 142 | 141
2018-04-04 04:00 | 140 | 139
2018-04-04 04:30 | 139 | 138
2018-04-04 05:00 | 140 | 139
2018-04-04 05:30 | 146 | 145
2018-04-04 06:00 | 154 | 153
2018-04-04 06:30 | 168 | 167
2018-04-04 07:00 | 179 | 178
2018-04-04 07:30 | 193 | 192
2018-04-04 08:00 | 194 | 193
2018-04-04 08:30 | 189 | 188
2018-04-04 09:00 | 188 | 187
2018-04-04 09:30 | 187 | 186
2018-04-04 10:00 | 179 | 179
2018-04-04 10:30 | 160 | 159
2018-04-04 11:00 | 135 | 134
2018-04-04 11:30 | 130 | 129
2018-04-04 12:00 | 129 | 128
2018-04-04 12:30 | 129 | 129
2018-04-04 13:00 | 133 | 132
2018-04-04 13:30 | 133 | 132
2018-04-04 14:00 | 124 | 123
2018-04-04 14:30 | 131 | 130
2018-04-04 15:00 | 140 | 139
2018-04-04 15:30 | 144 | 143
2018-04-04 16:00 | 149 | 148
2018-04-04 16:30 | 160 | 159
2018-04-04 17:00 | 119 | 118
2018-04-04 17:30 | 118 | 117
2018-04-04 18:00 | 130 | 129
2018-04-04 18:30 | 143 | 142
2018-04-04 19:00 | 154 | 153
2018-04-04 19:30 | 150 | 149
2018-04-04 20:00 | 142 | 141
2018-04-04 20:30 | 130 | 129
2018-04-04 21:00 | 120 | 119
2018-04-04 21:30 | 111 | 110
2018-04-04 22:00 | 100 | 99
2018-04-04 22:30 | 86 | 85
2018-04-04 23:00 | 108 | 107
2018-04-04 23:30 | 109 | 108
2018-04-05 | 101 | 100
2018-04-05 00:30 | 95 | 93
2018-04-05 01:00 | 88 | 86
2018-04-05 01:30 | 83 | 82
2018-04-05 02:00 | 78 | 77
2018-04-05 02:30 | 74 | 73
2018-04-05 03:00 | 73 | 71
2018-04-05 03:30 | 72 | 70
2018-04-05 04:00 | 72 | 70
2018-04-05 04:30 | 73 | 71
2018-04-05 05:00 | 75 | 73
2018-04-05 05:30 | 80 | 79
2018-04-05 06:00 | 85 | 84
2018-04-05 06:30 | 103 | 102
2018-04-05 07:00 | 112 | 111
2018-04-05 07:30 | 120 | 119
2018-04-05 08:00 | 123 | 122
2018-04-05 08:30 | 134 | 133
2018-04-05 09:00 | 133 | 132
2018-04-05 09:30 | 126 | 125
2018-04-05 10:00 | 119 | 118
2018-04-05 10:30 | 115 | 114
2018-04-05 11:00 | 115 | 114
2018-04-05 11:30 | 113 | 112
2018-04-05 12:00 | 117 | 116
2018-04-05 12:30 | 120 | 119
2018-04-05 13:00 | 126 | 125
2018-04-05 13:30 | 127 | 127
2018-04-05 14:00 | 131 | 131
2018-04-05 14:30 | 135 | 134
2018-04-05 15:00 | 139 | 139
2018-04-05 15:30 | 145 | 144
2018-04-05 16:00 | 149 | 148
2018-04-05 16:30 | 156 | 156
2018-04-05 17:00 | 125 | 125
2018-04-05 17:30 | 127 | 127
2018-04-05 18:00 | 143 | 142
2018-04-05 18:30 | 159 | 158
2018-04-05 19:00 | 169 | 168
2018-04-05 19:30 | 166 | 166
2018-04-05 20:00 | 157 | 157
2018-04-05 20:30 | 147 | 146
2018-04-05 21:00 | 137 | 136
2018-04-05 21:30 | 124 | 123
2018-04-05 22:00 | 112 | 111
2018-04-05 22:30 | 98 | 96
2018-04-05 23:00 | 86 | 85
2018-04-05 23:30 | 107 | 106
2018-04-06 | 108 | 107
2018-04-06 00:30 | 127 | 125
2018-04-06 01:00 | 163 | 162
2018-04-06 01:30 | 160 | 159
2018-04-06 02:00 | 156 | 155
2018-04-06 02:30 | 153 | 152
2018-04-06 03:00 | 153 | 152
2018-04-06 03:30 | 154 | 153
2018-04-06 04:00 | 153 | 152
2018-04-06 04:30 | 152 | 151
2018-04-06 05:00 | 153 | 152
2018-04-06 05:30 | 160 | 159
2018-04-06 06:00 | 168 | 167
2018-04-06 06:30 | 180 | 179
2018-04-06 07:00 | 190 | 189
2018-04-06 07:30 | 198 | 198
2018-04-06 08:00 | 203 | 203
2018-04-06 08:30 | 194 | 193
2018-04-06 09:00 | 198 | 197
2018-04-06 09:30 | 198 | 197
2018-04-06 10:00 | 191 | 190
2018-04-06 10:30 | 190 | 188
2018-04-06 11:00 | 188 | 186
2018-04-06 11:30 | 198 | 196
2018-04-06 12:00 | 200 | 198
2018-04-06 12:30 | 203 | 201
2018-04-06 13:00 | 209 | 208
2018-04-06 13:30 | 215 | 214
2018-04-06 14:00 | 209 | 208
2018-04-06 14:30 | 202 | 201
2018-04-06 15:00 | 212 | 211
2018-04-06 15:30 | 223 | 222
2018-04-06 16:00 | 215 | 213
2018-04-06 16:30 | 239 | 238
2018-04-06 17:00 | 248 | 247
2018-04-06 17:30 | 250 | 249
2018-04-06 18:00 | 252 | 251
2018-04-06 18:30 | 259 | 258
2018-04-06 19:00 | 268 | 267
2018-04-06 19:30 | 266 | 265
2018-04-06 20:00 | 256 | 255
2018-04-06 20:30 | 245 | 244
2018-04-06 21:00 | 235 | 234
2018-04-06 21:30 | 226 | 225
2018-04-06 22:00 | 220 | 219
2018-04-06 22:30 | 209 | 208
2018-04-06 23:00 | 199 | 198
2018-04-06 23:30 | 189 | 188
2018-04-07 | 180 | 178
2018-04-07 00:30 | 174 | 173
2018-04-07 01:00 | 168 | 167
2018-04-07 01:30 | 161 | 159
2018-04-07 02:00 | 159 | 156
2018-04-07 02:30 | 155 | 153
2018-04-07 03:00 | 151 | 149
2018-04-07 03:30 | 151 | 148
2018-04-07 04:00 | 151 | 148
2018-04-07 04:30 | 160 | 158
2018-04-07 05:00 | 166 | 164
2018-04-07 05:30 | 167 | 164
2018-04-07 06:00 | 171 | 169
2018-04-07 06:30 | 175 | 173
2018-04-07 07:00 | 181 | 179
2018-04-07 07:30 | 189 | 187
2018-04-07 08:00 | 189 | 187
2018-04-07 08:30 | 192 | 190
2018-04-07 09:00 | 194 | 193
2018-04-07 09:30 | 185 | 183
2018-04-07 10:00 | 183 | 181
2018-04-07 10:30 | 167 | 165
2018-04-07 11:00 | 171 | 169
2018-04-07 11:30 | 166 | 164
2018-04-07 12:00 | 168 | 166
2018-04-07 12:30 | 169 | 168
2018-04-07 13:00 | 172 | 171
2018-04-07 13:30 | 179 | 177
2018-04-07 14:00 | 177 | 175
2018-04-07 14:30 | 180 | 178
2018-04-07 15:00 | 186 | 185
2018-04-07 15:30 | 196 | 195
2018-04-07 16:00 | 200 | 198
2018-04-07 16:30 | 204 | 203
2018-04-07 17:00 | 214 | 213
2018-04-07 17:30 | 226 | 224
2018-04-07 18:00 | 240 | 239
2018-04-07 18:30 | 257 | 256
2018-04-07 19:00 | 264 | 262
2018-04-07 19:30 | 258 | 257
2018-04-07 20:00 | 249 | 248
2018-04-07 20:30 | 239 | 238
2018-04-07 21:00 | 229 | 228
2018-04-07 21:30 | 223 | 221
2018-04-07 22:00 | 216 | 214
2018-04-07 22:30 | 203 | 202
2018-04-07 23:00 | 195 | 194
2018-04-07 23:30 | 186 | 184
2018-04-08 | 179 | 178
2018-04-08 00:30 | 172 | 171
2018-04-08 01:00 | 165 | 163
2018-04-08 01:30 | 159 | 157
2018-04-08 02:00 | 155 | 154
2018-04-08 02:30 | 152 | 151
2018-04-08 03:00 | 149 | 148
2018-04-08 03:30 | 149 | 148
2018-04-08 04:00 | 149 | 148
2018-04-08 04:30 | 149 | 148
2018-04-08 05:00 | 149 | 148
2018-04-08 05:30 | 147 | 146
2018-04-08 06:00 | 150 | 148
2018-04-08 06:30 | 156 | 154
2018-04-08 07:00 | 157 | 156
2018-04-08 07:30 | 157 | 156
2018-04-08 08:00 | 156 | 155
2018-04-08 08:30 | 165 | 164
2018-04-08 09:00 | 163 | 162
2018-04-08 09:30 | 169 | 168
2018-04-08 10:00 | 167 | 166
2018-04-08 10:30 | 166 | 165
2018-04-08 11:00 | 164 | 163
2018-04-08 11:30 | 164 | 163
2018-04-08 12:00 | 168 | 167
2018-04-08 12:30 | 161 | 160
2018-04-08 13:00 | 168 | 167
2018-04-08 13:30 | 171 | 171
2018-04-08 14:00 | 179 | 178
2018-04-08 14:30 | 189 | 188
2018-04-08 15:00 | 194 | 193
2018-04-08 15:30 | 204 | 203
2018-04-08 16:00 | 207 | 206
2018-04-08 16:30 | 212 | 211
2018-04-08 17:00 | 231 | 230
2018-04-08 17:30 | 239 | 238
2018-04-08 18:00 | 256 | 255
2018-04-08 18:30 | 270 | 269
2018-04-08 19:00 | 283 | 282
2018-04-08 19:30 | 280 | 279
2018-04-08 20:00 | 266 | 265
2018-04-08 20:30 | 255 | 254
2018-04-08 21:00 | 247 | 246
2018-04-08 21:30 | 239 | 237
2018-04-08 22:00 | 226 | 225
2018-04-08 22:30 | 222 | 221
2018-04-08 23:00 | 214 | 213
2018-04-08 23:30 | 204 | 203
2018-04-09 | 197 | 196
2018-04-09 00:30 | 190 | 189
2018-04-09 01:00 | 184 | 182
2018-04-09 01:30 | 180 | 178
2018-04-09 02:00 | 178 | 176
2018-04-09 02:30 | 175 | 173
2018-04-09 03:00 | 173 | 172
2018-04-09 03:30 | 171 | 169
2018-04-09 04:00 | 169 | 167
2018-04-09 04:30 | 170 | 168
2018-04-09 05:00 | 172 | 170
2018-04-09 05:30 | 177 | 176
2018-04-09 06:00 | 185 | 184
2018-04-09 06:30 | 200 | 198
2018-04-09 07:00 | 216 | 215
2018-04-09 07:30 | 229 | 228
2018-04-09 08:00 | 238 | 237
2018-04-09 08:30 | 239 | 238
2018-04-09 09:00 | 234 | 233
2018-04-09 09:30 | 222 | 221
2018-04-09 10:00 | 207 | 206
2018-04-09 10:30 | 204 | 203
2018-04-09 11:00 | 203 | 203
2018-04-09 11:30 | 203 | 203
2018-04-09 12:00 | 203 | 202
2018-04-09 12:30 | 206 | 205
2018-04-09 13:00 | 210 | 210
2018-04-09 13:30 | 212 | 211
2018-04-09 14:00 | 218 | 218
2018-04-09 14:30 | 225 | 224
2018-04-09 15:00 | 229 | 229
2018-04-09 15:30 | 233 | 233
2018-04-09 16:00 | 237 | 236
2018-04-09 16:30 | 242 | 242
2018-04-09 17:00 | 246 | 246
2018-04-09 17:30 | 248 | 248
2018-04-09 18:00 | 263 | 262
2018-04-09 18:30 | 274 | 273
2018-04-09 19:00 | 284 | 284
2018-04-09 19:30 | 280 | 279
2018-04-09 20:00 | 268 | 268
2018-04-09 20:30 | 259 | 258
2018-04-09 21:00 | 251 | 249
2018-04-09 21:30 | 239 | 237
2018-04-09 22:00 | 229 | 228
2018-04-09 22:30 | 224 | 223
2018-04-09 23:00 | 217 | 216
2018-04-09 23:30 | 206 | 205
2018-04-10 | 196 | 195
2018-04-10 00:30 | 188 | 187
2018-04-10 01:00 | 180 | 180
2018-04-10 01:30 | 176 | 176
2018-04-10 02:00 | 172 | 172
2018-04-10 02:30 | 168 | 167
2018-04-10 03:00 | 167 | 166
2018-04-10 03:30 | 163 | 163
2018-04-10 04:00 | 163 | 163
2018-04-10 04:30 | 163 | 163
2018-04-10 05:00 | 165 | 164
2018-04-10 05:30 | 170 | 169
2018-04-10 06:00 | 177 | 177
2018-04-10 06:30 | 193 | 192
2018-04-10 07:00 | 205 | 204
2018-04-10 07:30 | 213 | 212
2018-04-10 08:00 | 210 | 210
2018-04-10 08:30 | 208 | 208
2018-04-10 09:00 | 207 | 206
2018-04-10 09:30 | 212 | 212
2018-04-10 10:00 | 216 | 216
2018-04-10 10:30 | 215 | 214
2018-04-10 11:00 | 215 | 214
2018-04-10 11:30 | 214 | 213
2018-04-10 12:00 | 215 | 214
2018-04-10 12:30 | 215 | 214
2018-04-10 13:00 | 216 | 214
2018-04-10 13:30 | 222 | 220
2018-04-10 14:00 | 228 | 227
2018-04-10 14:30 | 228 | 226
2018-04-10 15:00 | 223 | 221
2018-04-10 15:30 | 228 | 226
2018-04-10 16:00 | 235 | 233
2018-04-10 16:30 | 243 | 241
2018-04-10 17:00 | 252 | 250
2018-04-10 17:30 | 255 | 253
2018-04-10 18:00 | 260 | 258
2018-04-10 18:30 | 267 | 266
2018-04-10 19:00 | 278 | 277
2018-04-10 19:30 | 273 | 272
2018-04-10 20:00 | 260 | 259
2018-04-10 20:30 | 252 | 250
2018-04-10 21:00 | 242 | 240
2018-04-10 21:30 | 230 | 228
2018-04-10 22:00 | 218 | 216
2018-04-10 22:30 | 215 | 214
2018-04-10 23:00 | 209 | 207
2018-04-10 23:30 | 197 | 195
2018-04-11 | 187 | 185
2018-04-11 00:30 | 180 | 178
2018-04-11 01:00 | 171 | 168
2018-04-11 01:30 | 167 | 166
2018-04-11 02:00 | 164 | 162
2018-04-11 02:30 | 162 | 160
2018-04-11 03:00 | 159 | 158
2018-04-11 03:30 | 157 | 155
2018-04-11 04:00 | 156 | 155
2018-04-11 04:30 | 157 | 155
2018-04-11 05:00 | 159 | 157
2018-04-11 05:30 | 164 | 163
2018-04-11 06:00 | 172 | 170
2018-04-11 06:30 | 186 | 185
2018-04-11 07:00 | 197 | 196
2018-04-11 07:30 | 210 | 209
2018-04-11 08:00 | 203 | 201
2018-04-11 08:30 | 184 | 183
2018-04-11 09:00 | 180 | 179
2018-04-11 09:30 | 177 | 176
2018-04-11 10:00 | 178 | 177
2018-04-11 10:30 | 167 | 166
2018-04-11 11:00 | 159 | 158
2018-04-11 11:30 | 137 | 135
2018-04-11 12:00 | 123 | 122
2018-04-11 12:30 | 128 | 127
2018-04-11 13:00 | 130 | 128
2018-04-11 13:30 | 128 | 127
2018-04-11 14:00 | 130 | 128
2018-04-11 14:30 | 133 | 132
2018-04-11 15:00 | 130 | 129
2018-04-11 15:30 | 139 | 139
2018-04-11 16:00 | 140 | 139
2018-04-11 16:30 | 114 | 113
2018-04-11 17:00 | 106 | 105
2018-04-11 17:30 | 113 | 112
2018-04-11 18:00 | 123 | 122
2018-04-11 18:30 | 133 | 132
2018-04-11 19:00 | 144 | 143
2018-04-11 19:30 | 143 | 141
2018-04-11 20:00 | 131 | 130
2018-04-11 20:30 | 123 | 122
2018-04-11 21:00 | 115 | 114
2018-04-11 21:30 | 107 | 106
2018-04-11 22:00 | 131 | 130
2018-04-11 22:30 | 139 | 138
2018-04-11 23:00 | 131 | 129
2018-04-11 23:30 | 121 | 120
2018-04-12 | 113 | 111
2018-04-12 00:30 | 106 | 104
2018-04-12 01:00 | 99 | 97
2018-04-12 01:30 | 96 | 94
2018-04-12 02:00 | 92 | 90
2018-04-12 02:30 | 91 | 89
2018-04-12 03:00 | 90 | 88
2018-04-12 03:30 | 89 | 87
2018-04-12 04:00 | 89 | 87
2018-04-12 04:30 | 90 | 88
2018-04-12 05:00 | 93 | 90
2018-04-12 05:30 | 99 | 97
2018-04-12 06:00 | 106 | 105
2018-04-12 06:30 | 118 | 117
2018-04-12 07:00 | 131 | 130
2018-04-12 07:30 | 139 | 138
2018-04-12 08:00 | 136 | 135
2018-04-12 08:30 | 147 | 146
2018-04-12 09:00 | 150 | 149
2018-04-12 09:30 | 144 | 143
2018-04-12 10:00 | 137 | 136
2018-04-12 10:30 | 142 | 141
2018-04-12 11:00 | 144 | 143
2018-04-12 11:30 | 137 | 136
2018-04-12 12:00 | 132 | 130
2018-04-12 12:30 | 138 | 137
2018-04-12 13:00 | 135 | 134
2018-04-12 13:30 | 132 | 131
2018-04-12 14:00 | 137 | 135
2018-04-12 14:30 | 134 | 133
2018-04-12 15:00 | 130 | 129
2018-04-12 15:30 | 118 | 117
2018-04-12 16:00 | 141 | 140
2018-04-12 16:30 | 110 | 109
2018-04-12 17:00 | 119 | 118
2018-04-12 17:30 | 129 | 128
2018-04-12 18:00 | 140 | 139
2018-04-12 18:30 | 152 | 151
2018-04-12 19:00 | 163 | 162
2018-04-12 19:30 | 159 | 158
2018-04-12 20:00 | 157 | 156
2018-04-12 20:30 | 155 | 154
2018-04-12 21:00 | 146 | 145
2018-04-12 21:30 | 135 | 134
2018-04-12 22:00 | 157 | 156
2018-04-12 22:30 | 152 | 151
2018-04-12 23:00 | 143 | 141
2018-04-12 23:30 | 156 | 154
2018-04-13 | 191 | 190
2018-04-13 00:30 | 184 | 183
2018-04-13 01:00 | 173 | 171
2018-04-13 01:30 | 157 | 155
2018-04-13 02:00 | 154 | 151
2018-04-13 02:30 | 149 | 147
2018-04-13 03:00 | 147 | 145
2018-04-13 03:30 | 146 | 145
2018-04-13 04:00 | 143 | 141
2018-04-13 04:30 | 136 | 134
2018-04-13 05:00 | 134 | 132
2018-04-13 05:30 | 139 | 137
2018-04-13 06:00 | 145 | 143
2018-04-13 06:30 | 160 | 159
2018-04-13 07:00 | 171 | 169
2018-04-13 07:30 | 184 | 183
2018-04-13 08:00 | 196 | 195
2018-04-13 08:30 | 212 | 211
2018-04-13 09:00 | 210 | 208
2018-04-13 09:30 | 213 | 212
2018-04-13 10:00 | 213 | 212
2018-04-13 10:30 | 206 | 205
2018-04-13 11:00 | 203 | 201
2018-04-13 11:30 | 198 | 197
2018-04-13 12:00 | 200 | 199
2018-04-13 12:30 | 199 | 197
2018-04-13 13:00 | 202 | 200
2018-04-13 13:30 | 202 | 200
2018-04-13 14:00 | 209 | 207
2018-04-13 14:30 | 216 | 215
2018-04-13 15:00 | 221 | 220
2018-04-13 15:30 | 195 | 194
2018-04-13 16:00 | 156 | 154
2018-04-13 16:30 | 154 | 153
2018-04-13 17:00 | 162 | 160
2018-04-13 17:30 | 172 | 171
2018-04-13 18:00 | 182 | 180
2018-04-13 18:30 | 191 | 190
2018-04-13 19:00 | 200 | 198
2018-04-13 19:30 | 196 | 194
2018-04-13 20:00 | 186 | 184
2018-04-13 20:30 | 176 | 174
2018-04-13 21:00 | 169 | 167
2018-04-13 21:30 | 160 | 158
2018-04-13 22:00 | 149 | 147
2018-04-13 22:30 | 140 | 138
2018-04-13 23:00 | 160 | 158
2018-04-13 23:30 | 190 | 189
2018-04-14 | 187 | 186
2018-04-14 00:30 | 179 | 178
2018-04-14 01:00 | 174 | 173
2018-04-14 01:30 | 169 | 168
2018-04-14 02:00 | 166 | 164
2018-04-14 02:30 | 164 | 162
2018-04-14 03:00 | 161 | 159
2018-04-14 03:30 | 160 | 159
2018-04-14 04:00 | 157 | 155
2018-04-14 04:30 | 157 | 155
2018-04-14 05:00 | 158 | 156
2018-04-14 05:30 | 161 | 159
2018-04-14 06:00 | 163 | 161
2018-04-14 06:30 | 171 | 170
2018-04-14 07:00 | 175 | 174
2018-04-14 07:30 | 183 | 182
2018-04-14 08:00 | 185 | 184
2018-04-14 08:30 | 190 | 189
2018-04-14 09:00 | 194 | 193
2018-04-14 09:30 | 193 | 192
2018-04-14 10:00 | 187 | 186
2018-04-14 10:30 | 190 | 189
2018-04-14 11:00 | 191 | 190
2018-04-14 11:30 | 192 | 190
2018-04-14 12:00 | 188 | 187
2018-04-14 12:30 | 194 | 193
2018-04-14 13:00 | 190 | 189
2018-04-14 13:30 | 187 | 186
2018-04-14 14:00 | 189 | 188
2018-04-14 14:30 | 184 | 182
2018-04-14 15:00 | 176 | 175
2018-04-14 15:30 | 178 | 177
2018-04-14 16:00 | 187 | 185
2018-04-14 16:30 | 194 | 193
2018-04-14 17:00 | 202 | 201
2018-04-14 17:30 | 216 | 215
2018-04-14 18:00 | 231 | 230
2018-04-14 18:30 | 242 | 241
2018-04-14 19:00 | 249 | 248
2018-04-14 19:30 | 243 | 242
2018-04-14 20:00 | 232 | 231
2018-04-14 20:30 | 224 | 222
2018-04-14 21:00 | 217 | 215
2018-04-14 21:30 | 210 | 208
2018-04-14 22:00 | 209 | 207
2018-04-14 22:30 | 189 | 187
2018-04-14 23:00 | 182 | 181
2018-04-14 23:30 | 174 | 172
2018-04-15 | 177 | 176
2018-04-15 00:30 | 184 | 183
2018-04-15 01:00 | 182 | 181
2018-04-15 01:30 | 179 | 178
2018-04-15 02:00 | 175 | 174
2018-04-15 02:30 | 174 | 173
2018-04-15 03:00 | 174 | 172
2018-04-15 03:30 | 172 | 170
2018-04-15 04:00 | 169 | 167
2018-04-15 04:30 | 170 | 168
2018-04-15 05:00 | 169 | 167
2018-04-15 05:30 | 170 | 169
2018-04-15 06:00 | 171 | 170
2018-04-15 06:30 | 176 | 174
2018-04-15 07:00 | 177 | 176
2018-04-15 07:30 | 173 | 171
2018-04-15 08:00 | 160 | 159
2018-04-15 08:30 | 157 | 155
2018-04-15 09:00 | 155 | 154
2018-04-15 09:30 | 155 | 154
2018-04-15 10:00 | 156 | 155
2018-04-15 10:30 | 156 | 155
2018-04-15 11:00 | 159 | 158
2018-04-15 11:30 | 157 | 156
2018-04-15 12:00 | 161 | 160
2018-04-15 12:30 | 164 | 163
2018-04-15 13:00 | 171 | 170
2018-04-15 13:30 | 172 | 172
2018-04-15 14:00 | 172 | 171
2018-04-15 14:30 | 179 | 178
2018-04-15 15:00 | 185 | 184
2018-04-15 15:30 | 195 | 194
2018-04-15 16:00 | 202 | 201
2018-04-15 16:30 | 209 | 208
2018-04-15 17:00 | 220 | 219
2018-04-15 17:30 | 239 | 238
2018-04-15 18:00 | 258 | 257
2018-04-15 18:30 | 273 | 272
2018-04-15 19:00 | 284 | 283
2018-04-15 19:30 | 280 | 279
2018-04-15 20:00 | 269 | 267
2018-04-15 20:30 | 256 | 254
2018-04-15 21:00 | 247 | 245
2018-04-15 21:30 | 238 | 236
2018-04-15 22:00 | 228 | 225
2018-04-15 22:30 | 212 | 211
2018-04-15 23:00 | 202 | 200
2018-04-15 23:30 | 193 | 192
2018-04-16 | 186 | 185
2018-04-16 00:30 | 180 | 178
2018-04-16 01:00 | 175 | 173
2018-04-16 01:30 | 169 | 168
2018-04-16 02:00 | 164 | 163
2018-04-16 02:30 | 163 | 162
2018-04-16 03:00 | 160 | 159
2018-04-16 03:30 | 161 | 160
2018-04-16 04:00 | 161 | 160
2018-04-16 04:30 | 147 | 145
2018-04-16 05:00 | 126 | 124
2018-04-16 05:30 | 128 | 127
2018-04-16 06:00 | 139 | 137
2018-04-16 06:30 | 156 | 155
2018-04-16 07:00 | 170 | 169
2018-04-16 07:30 | 174 | 173
2018-04-16 08:00 | 151 | 150
2018-04-16 08:30 | 155 | 154
2018-04-16 09:00 | 166 | 165
2018-04-16 09:30 | 161 | 160
2018-04-16 10:00 | 155 | 153
2018-04-16 10:30 | 120 | 119
2018-04-16 11:00 | 112 | 110
2018-04-16 11:30 | 114 | 113
2018-04-16 12:00 | 110 | 109
2018-04-16 12:30 | 109 | 108
2018-04-16 13:00 | 105 | 103
2018-04-16 13:30 | 106 | 104
2018-04-16 14:00 | 110 | 109
2018-04-16 14:30 | 112 | 111
2018-04-16 15:00 | 122 | 121
2018-04-16 15:30 | 130 | 129
2018-04-16 16:00 | 136 | 134
2018-04-16 16:30 | 149 | 148
2018-04-16 17:00 | 151 | 149
2018-04-16 17:30 | 157 | 156
2018-04-16 18:00 | 169 | 167
2018-04-16 18:30 | 180 | 179
2018-04-16 19:00 | 187 | 186
2018-04-16 19:30 | 179 | 178
2018-04-16 20:00 | 168 | 166
2018-04-16 20:30 | 159 | 157
2018-04-16 21:00 | 145 | 143
2018-04-16 21:30 | 166 | 164
2018-04-16 22:00 | 165 | 164
2018-04-16 22:30 | 152 | 150
2018-04-16 23:00 | 138 | 137
2018-04-16 23:30 | 128 | 127
2018-04-17 | 144 | 142
2018-04-17 00:30 | 182 | 180
2018-04-17 01:00 | 177 | 176
2018-04-17 01:30 | 175 | 174
2018-04-17 02:00 | 172 | 170
2018-04-17 02:30 | 170 | 168
2018-04-17 03:00 | 165 | 164
2018-04-17 03:30 | 164 | 162
2018-04-17 04:00 | 163 | 162
2018-04-17 04:30 | 166 | 165
2018-04-17 05:00 | 167 | 165
2018-04-17 05:30 | 173 | 172
2018-04-17 06:00 | 181 | 180
2018-04-17 06:30 | 199 | 198
2018-04-17 07:00 | 216 | 216
2018-04-17 07:30 | 228 | 227
2018-04-17 08:00 | 233 | 232
2018-04-17 08:30 | 229 | 228
2018-04-17 09:00 | 225 | 224
2018-04-17 09:30 | 221 | 220
2018-04-17 10:00 | 224 | 223
2018-04-17 10:30 | 217 | 216
2018-04-17 11:00 | 216 | 215
2018-04-17 11:30 | 213 | 212
2018-04-17 12:00 | 216 | 215
2018-04-17 12:30 | 217 | 216
2018-04-17 13:00 | 216 | 215
2018-04-17 13:30 | 212 | 212
2018-04-17 14:00 | 167 | 166
2018-04-17 14:30 | 147 | 146
2018-04-17 15:00 | 155 | 155
2018-04-17 15:30 | 160 | 159
2018-04-17 16:00 | 167 | 167
2018-04-17 16:30 | 183 | 182
2018-04-17 17:00 | 186 | 185
2018-04-17 17:30 | 196 | 195
2018-04-17 18:00 | 207 | 207
2018-04-17 18:30 | 222 | 221
2018-04-17 19:00 | 233 | 232
2018-04-17 19:30 | 227 | 226
2018-04-17 20:00 | 217 | 216
2018-04-17 20:30 | 203 | 202
2018-04-17 21:00 | 188 | 187
2018-04-17 21:30 | 178 | 177
2018-04-17 22:00 | 167 | 166
2018-04-17 22:30 | 150 | 149
2018-04-17 23:00 | 165 | 164
2018-04-17 23:30 | 196 | 195
2018-04-18 | 191 | 191
2018-04-18 00:30 | 182 | 182
2018-04-18 01:00 | 180 | 179
2018-04-18 01:30 | 175 | 174
2018-04-18 02:00 | 172 | 171
2018-04-18 02:30 | 168 | 167
2018-04-18 03:00 | 165 | 164
2018-04-18 03:30 | 165 | 164
2018-04-18 04:00 | 163 | 163
2018-04-18 04:30 | 165 | 164
2018-04-18 05:00 | 168 | 167
2018-04-18 05:30 | 173 | 172
2018-04-18 06:00 | 179 | 179
2018-04-18 06:30 | 197 | 196
2018-04-18 07:00 | 212 | 211
2018-04-18 07:30 | 229 | 229
2018-04-18 08:00 | 234 | 234
2018-04-18 08:30 | 231 | 231
2018-04-18 09:00 | 226 | 226
2018-04-18 09:30 | 216 | 216
2018-04-18 10:00 | 213 | 213
2018-04-18 10:30 | 211 | 210
2018-04-18 11:00 | 204 | 204
2018-04-18 11:30 | 201 | 200
2018-04-18 12:00 | 200 | 200
2018-04-18 12:30 | 201 | 201
2018-04-18 13:00 | 207 | 206
2018-04-18 13:30 | 209 | 209
2018-04-18 14:00 | 208 | 208
2018-04-18 14:30 | 212 | 211
2018-04-18 15:00 | 216 | 215
2018-04-18 15:30 | 222 | 221
2018-04-18 16:00 | 233 | 233
2018-04-18 16:30 | 198 | 197
2018-04-18 17:00 | 182 | 181
2018-04-18 17:30 | 181 | 181
2018-04-18 18:00 | 194 | 193
2018-04-18 18:30 | 208 | 207
2018-04-18 19:00 | 218 | 217
2018-04-18 19:30 | 212 | 211
2018-04-18 20:00 | 200 | 199
2018-04-18 20:30 | 186 | 185
2018-04-18 21:00 | 176 | 174
2018-04-18 21:30 | 166 | 165
2018-04-18 22:00 | 154 | 153
2018-04-18 22:30 | 138 | 137
2018-04-18 23:00 | 157 | 157
2018-04-18 23:30 | 188 | 187
2018-04-19 | 183 | 182
2018-04-19 00:30 | 177 | 176
2018-04-19 01:00 | 170 | 170
2018-04-19 01:30 | 165 | 165
2018-04-19 02:00 | 162 | 162
2018-04-19 02:30 | 159 | 158
2018-04-19 03:00 | 158 | 157
2018-04-19 03:30 | 157 | 156
2018-04-19 04:00 | 156 | 155
2018-04-19 04:30 | 156 | 155
2018-04-19 05:00 | 157 | 156
2018-04-19 05:30 | 163 | 163
2018-04-19 06:00 | 171 | 170
2018-04-19 06:30 | 188 | 188
2018-04-19 07:00 | 202 | 201
2018-04-19 07:30 | 214 | 213
2018-04-19 08:00 | 213 | 213
2018-04-19 08:30 | 211 | 211
2018-04-19 09:00 | 219 | 218
2018-04-19 09:30 | 212 | 211
2018-04-19 10:00 | 199 | 199
2018-04-19 10:30 | 199 | 198
2018-04-19 11:00 | 194 | 194
2018-04-19 11:30 | 195 | 195
2018-04-19 12:00 | 195 | 194
2018-04-19 12:30 | 202 | 201
2018-04-19 13:00 | 203 | 203
2018-04-19 13:30 | 205 | 205
2018-04-19 14:00 | 181 | 180
2018-04-19 14:30 | 140 | 139
2018-04-19 15:00 | 142 | 142
2018-04-19 15:30 | 145 | 144
2018-04-19 16:00 | 149 | 149
2018-04-19 16:30 | 158 | 157
2018-04-19 17:00 | 167 | 166
2018-04-19 17:30 | 170 | 169
2018-04-19 18:00 | 183 | 183
2018-04-19 18:30 | 198 | 198
2018-04-19 19:00 | 212 | 211
2018-04-19 19:30 | 204 | 204
2018-04-19 20:00 | 194 | 193
2018-04-19 20:30 | 182 | 181
2018-04-19 21:00 | 172 | 172
2018-04-19 21:30 | 159 | 158
2018-04-19 22:00 | 146 | 145
2018-04-19 22:30 | 138 | 137
2018-04-19 23:00 | 165 | 165
2018-04-19 23:30 | 196 | 196
2018-04-20 | 193 | 192
2018-04-20 00:30 | 187 | 186
2018-04-20 01:00 | 181 | 180
2018-04-20 01:30 | 175 | 175
2018-04-20 02:00 | 173 | 172
2018-04-20 02:30 | 171 | 171
2018-04-20 03:00 | 171 | 170
2018-04-20 03:30 | 171 | 170
2018-04-20 04:00 | 170 | 169
2018-04-20 04:30 | 171 | 170
2018-04-20 05:00 | 174 | 173
2018-04-20 05:30 | 180 | 180
2018-04-20 06:00 | 190 | 189
2018-04-20 06:30 | 207 | 206
2018-04-20 07:00 | 222 | 221
2018-04-20 07:30 | 229 | 227
2018-04-20 08:00 | 225 | 223
2018-04-20 08:30 | 216 | 214
2018-04-20 09:00 | 210 | 208
2018-04-20 09:30 | 206 | 204
2018-04-20 10:00 | 201 | 200
2018-04-20 10:30 | 198 | 197
2018-04-20 11:00 | 196 | 195
2018-04-20 11:30 | 197 | 196
2018-04-20 12:00 | 200 | 199
2018-04-20 12:30 | 203 | 202
2018-04-20 13:00 | 206 | 204
2018-04-20 13:30 | 206 | 205
2018-04-20 14:00 | 210 | 208
2018-04-20 14:30 | 177 | 176
2018-04-20 15:00 | 144 | 143
2018-04-20 15:30 | 151 | 149
2018-04-20 16:00 | 153 | 152
2018-04-20 16:30 | 154 | 152
2018-04-20 17:00 | 163 | 161
2018-04-20 17:30 | 173 | 171
2018-04-20 18:00 | 183 | 181
2018-04-20 18:30 | 194 | 192
2018-04-20 19:00 | 202 | 200
2018-04-20 19:30 | 198 | 196
2018-04-20 20:00 | 188 | 186
2018-04-20 20:30 | 178 | 176
2018-04-20 21:00 | 170 | 168
2018-04-20 21:30 | 161 | 159
2018-04-20 22:00 | 150 | 148
2018-04-20 22:30 | 139 | 137
2018-04-20 23:00 | 161 | 159
2018-04-20 23:30 | 189 | 187
2018-04-21 | 187 | 185
2018-04-21 00:30 | 180 | 177
2018-04-21 01:00 | 173 | 172
2018-04-21 01:30 | 169 | 167
2018-04-21 02:00 | 165 | 163
2018-04-21 02:30 | 163 | 161
2018-04-21 03:00 | 159 | 156
2018-04-21 03:30 | 157 | 155
2018-04-21 04:00 | 155 | 154
2018-04-21 04:30 | 155 | 153
2018-04-21 05:00 | 157 | 155
2018-04-21 05:30 | 158 | 156
2018-04-21 06:00 | 162 | 160
2018-04-21 06:30 | 169 | 168
2018-04-21 07:00 | 171 | 170
2018-04-21 07:30 | 175 | 173
2018-04-21 08:00 | 177 | 176
2018-04-21 08:30 | 174 | 172
2018-04-21 09:00 | 173 | 172
2018-04-21 09:30 | 167 | 166
2018-04-21 10:00 | 162 | 161
2018-04-21 10:30 | 159 | 158
2018-04-21 11:00 | 156 | 155
2018-04-21 11:30 | 156 | 153
2018-04-21 12:00 | 157 | 155
2018-04-21 12:30 | 157 | 155
2018-04-21 13:00 | 157 | 155
2018-04-21 13:30 | 157 | 155
2018-04-21 14:00 | 162 | 160
2018-04-21 14:30 | 167 | 165
2018-04-21 15:00 | 176 | 174
2018-04-21 15:30 | 181 | 179
2018-04-21 16:00 | 193 | 191
2018-04-21 16:30 | 200 | 199
2018-04-21 17:00 | 212 | 210
2018-04-21 17:30 | 228 | 226
2018-04-21 18:00 | 244 | 242
2018-04-21 18:30 | 256 | 255
2018-04-21 19:00 | 263 | 262
2018-04-21 19:30 | 256 | 255
2018-04-21 20:00 | 248 | 247
2018-04-21 20:30 | 238 | 236
2018-04-21 21:00 | 230 | 229
2018-04-21 21:30 | 220 | 218
2018-04-21 22:00 | 211 | 210
2018-04-21 22:30 | 214 | 212
2018-04-21 23:00 | 211 | 209
2018-04-21 23:30 | 203 | 201
2018-04-22 | 194 | 192
2018-04-22 00:30 | 188 | 186
2018-04-22 01:00 | 180 | 179
2018-04-22 01:30 | 177 | 175
2018-04-22 02:00 | 173 | 171
2018-04-22 02:30 | 169 | 167
2018-04-22 03:00 | 166 | 164
2018-04-22 03:30 | 165 | 163
2018-04-22 04:00 | 163 | 162
2018-04-22 04:30 | 163 | 162
2018-04-22 05:00 | 163 | 162
2018-04-22 05:30 | 166 | 164
2018-04-22 06:00 | 168 | 166
2018-04-22 06:30 | 173 | 171
2018-04-22 07:00 | 173 | 172
2018-04-22 07:30 | 172 | 170
2018-04-22 08:00 | 155 | 153
2018-04-22 08:30 | 150 | 148
2018-04-22 09:00 | 150 | 148
2018-04-22 09:30 | 150 | 149
2018-04-22 10:00 | 149 | 147
2018-04-22 10:30 | 147 | 146
2018-04-22 11:00 | 148 | 147
2018-04-22 11:30 | 149 | 147
2018-04-22 12:00 | 145 | 143
2018-04-22 12:30 | 147 | 146
2018-04-22 13:00 | 151 | 150
2018-04-22 13:30 | 153 | 152
2018-04-22 14:00 | 161 | 160
2018-04-22 14:30 | 160 | 159
2018-04-22 15:00 | 170 | 169
2018-04-22 15:30 | 184 | 183
2018-04-22 16:00 | 189 | 188
2018-04-22 16:30 | 194 | 192
2018-04-22 17:00 | 214 | 213
2018-04-22 17:30 | 232 | 231
2018-04-22 18:00 | 252 | 250
2018-04-22 18:30 | 269 | 268
2018-04-22 19:00 | 277 | 277
2018-04-22 19:30 | 269 | 269
2018-04-22 20:00 | 257 | 256
2018-04-22 20:30 | 245 | 244
2018-04-22 21:00 | 236 | 235
2018-04-22 21:30 | 227 | 225
2018-04-22 22:00 | 215 | 213
2018-04-22 22:30 | 201 | 199
2018-04-22 23:00 | 188 | 187
2018-04-22 23:30 | 178 | 177
2018-04-23 | 173 | 171
2018-04-23 00:30 | 179 | 178
2018-04-23 01:00 | 178 | 177
2018-04-23 01:30 | 172 | 171
2018-04-23 02:00 | 172 | 170
2018-04-23 02:30 | 169 | 167
2018-04-23 03:00 | 168 | 166
2018-04-23 03:30 | 167 | 165
2018-04-23 04:00 | 167 | 165
2018-04-23 04:30 | 168 | 166
2018-04-23 05:00 | 172 | 170
2018-04-23 05:30 | 178 | 176
2018-04-23 06:00 | 187 | 186
2018-04-23 06:30 | 205 | 204
2018-04-23 07:00 | 222 | 221
2018-04-23 07:30 | 242 | 241
2018-04-23 08:00 | 228 | 227
2018-04-23 08:30 | 216 | 214
2018-04-23 09:00 | 211 | 209
2018-04-23 09:30 | 208 | 207
2018-04-23 10:00 | 205 | 203
2018-04-23 10:30 | 201 | 199
2018-04-23 11:00 | 199 | 198
2018-04-23 11:30 | 201 | 199
2018-04-23 12:00 | 206 | 205
2018-04-23 12:30 | 205 | 203
2018-04-23 13:00 | 208 | 205
2018-04-23 13:30 | 214 | 212
2018-04-23 14:00 | 213 | 211
2018-04-23 14:30 | 218 | 216
2018-04-23 15:00 | 218 | 217
2018-04-23 15:30 | 218 | 217
2018-04-23 16:00 | 228 | 227
2018-04-23 16:30 | 232 | 231
2018-04-23 17:00 | 250 | 248
2018-04-23 17:30 | 261 | 259
2018-04-23 18:00 | 273 | 271
2018-04-23 18:30 | 290 | 289
2018-04-23 19:00 | 300 | 298
2018-04-23 19:30 | 291 | 289
2018-04-23 20:00 | 281 | 279
2018-04-23 20:30 | 267 | 265
2018-04-23 21:00 | 255 | 253
2018-04-23 21:30 | 245 | 243
2018-04-23 22:00 | 236 | 234
2018-04-23 22:30 | 230 | 228
2018-04-23 23:00 | 223 | 221
2018-04-23 23:30 | 212 | 210
2018-04-24 | 204 | 202
2018-04-24 00:30 | 197 | 195
2018-04-24 01:00 | 192 | 191
2018-04-24 01:30 | 188 | 186
2018-04-24 02:00 | 183 | 181
2018-04-24 02:30 | 180 | 178
2018-04-24 03:00 | 181 | 179
2018-04-24 03:30 | 179 | 178
2018-04-24 04:00 | 180 | 178
2018-04-24 04:30 | 181 | 179
2018-04-24 05:00 | 182 | 180
2018-04-24 05:30 | 190 | 188
2018-04-24 06:00 | 198 | 197
2018-04-24 06:30 | 215 | 214
2018-04-24 07:00 | 218 | 217
2018-04-24 07:30 | 235 | 233
2018-04-24 08:00 | 234 | 232
2018-04-24 08:30 | 231 | 229
2018-04-24 09:00 | 220 | 218
2018-04-24 09:30 | 212 | 209
2018-04-24 10:00 | 205 | 202
2018-04-24 10:30 | 203 | 201
2018-04-24 11:00 | 199 | 196
2018-04-24 11:30 | 198 | 196
2018-04-24 12:00 | 202 | 199
2018-04-24 12:30 | 203 | 200
2018-04-24 13:00 | 200 | 197
2018-04-24 13:30 | 197 | 195
2018-04-24 14:00 | 202 | 199
2018-04-24 14:30 | 210 | 207
2018-04-24 15:00 | 213 | 210
2018-04-24 15:30 | 217 | 214
2018-04-24 16:00 | 222 | 219
2018-04-24 16:30 | 220 | 217
2018-04-24 17:00 | 229 | 226
2018-04-24 17:30 | 241 | 238
2018-04-24 18:00 | 255 | 252
2018-04-24 18:30 | 268 | 265
2018-04-24 19:00 | 280 | 278
2018-04-24 19:30 | 274 | 271
2018-04-24 20:00 | 263 | 260
2018-04-24 20:30 | 251 | 248
2018-04-24 21:00 | 241 | 238
2018-04-24 21:30 | 230 | 227
2018-04-24 22:00 | 220 | 217
2018-04-24 22:30 | 221 | 218
2018-04-24 23:00 | 214 | 211
2018-04-24 23:30 | 202 | 199
2018-04-25 | 192 | 189
2018-04-25 00:30 | 187 | 184
2018-04-25 01:00 | 181 | 178
2018-04-25 01:30 | 178 | 175
2018-04-25 02:00 | 173 | 170
2018-04-25 02:30 | 169 | 166
2018-04-25 03:00 | 166 | 164
2018-04-25 03:30 | 165 | 163
2018-04-25 04:00 | 126 | 121
2018-04-25 04:30 | 124 | 119
2018-04-25 05:00 | 134 | 130
2018-04-25 05:30 | 145 | 141
2018-04-25 06:00 | 150 | 146
2018-04-25 06:30 | 154 | 151
2018-04-25 07:00 | 157 | 153
2018-04-25 07:30 | 155 | 152
2018-04-25 08:00 | 138 | 135
2018-04-25 08:30 | 134 | 131
2018-04-25 09:00 | 123 | 121
2018-04-25 09:30 | 120 | 117
2018-04-25 10:00 | 99 | 95
2018-04-25 10:30 | 76 | 70
2018-04-25 11:00 | 82 | 77
2018-04-25 11:30 | 96 | 93
2018-04-25 12:00 | 109 | 107
2018-04-25 12:30 | 124 | 122
2018-04-25 13:00 | 134 | 132
2018-04-25 13:30 | 137 | 135
2018-04-25 14:00 | 139 | 137
2018-04-25 14:30 | 144 | 142
2018-04-25 15:00 | 148 | 146
2018-04-25 15:30 | 159 | 157
2018-04-25 16:00 | 168 | 166
2018-04-25 16:30 | 181 | 179
2018-04-25 17:00 | 198 | 196
2018-04-25 17:30 | 221 | 219
2018-04-25 18:00 | 240 | 239
2018-04-25 18:30 | 259 | 257
2018-04-25 19:00 | 267 | 265
2018-04-25 19:30 | 259 | 257
2018-04-25 20:00 | 247 | 245
2018-04-25 20:30 | 237 | 235
2018-04-25 21:00 | 220 | 217
2018-04-25 21:30 | 197 | 194
2018-04-25 22:00 | 186 | 183
2018-04-25 22:30 | 184 | 181
2018-04-25 23:00 | 174 | 171
2018-04-25 23:30 | 150 | 146
2018-04-26 | 142 | 138
2018-04-26 00:30 | 139 | 135
2018-04-26 01:00 | 134 | 129
2018-04-26 01:30 | 131 | 126
2018-04-26 02:00 | 126 | 122
2018-04-26 02:30 | 126 | 121
2018-04-26 03:00 | 125 | 120
2018-04-26 03:30 | 124 | 119
2018-04-26 04:00 | 124 | 119
2018-04-26 04:30 | 124 | 119
2018-04-26 05:00 | 127 | 123
2018-04-26 05:30 | 133 | 129
2018-04-26 06:00 | 143 | 139
2018-04-26 06:30 | 159 | 156
2018-04-26 07:00 | 176 | 172
2018-04-26 07:30 | 179 | 176
2018-04-26 08:00 | 164 | 161
2018-04-26 08:30 | 137 | 134
2018-04-26 09:00 | 103 | 101
2018-04-26 09:30 | 95 | 93
2018-04-26 10:00 | 91 | 89
2018-04-26 10:30 | 90 | 87
2018-04-26 11:00 | 87 | 85
2018-04-26 11:30 | 73 | 70
2018-04-26 12:00 | 53 | 50
2018-04-26 12:30 | 30 | 25
2018-04-26 13:00 | 26 | 19
2018-04-26 13:30 | 29 | 24
2018-04-26 14:00 | 31 | 26
2018-04-26 14:30 | 35 | 31
2018-04-26 15:00 | 42 | 39
2018-04-26 15:30 | 50 | 47
2018-04-26 16:00 | 55 | 53
2018-04-26 16:30 | 66 | 64
2018-04-26 17:00 | 77 | 75
2018-04-26 17:30 | 91 | 89
2018-04-26 18:00 | 108 | 106
2018-04-26 18:30 | 121 | 119
2018-04-26 19:00 | 131 | 129
2018-04-26 19:30 | 126 | 124
2018-04-26 20:00 | 114 | 112
2018-04-26 20:30 | 100 | 98
2018-04-26 21:00 | 85 | 83
2018-04-26 21:30 | 72 | 69
2018-04-26 22:00 | 58 | 55
2018-04-26 22:30 | 60 | 58
2018-04-26 23:00 | 86 | 84
2018-04-26 23:30 | 86 | 84
2018-04-27 | 76 | 73
2018-04-27 00:30 | 70 | 68
2018-04-27 01:00 | 64 | 61
2018-04-27 01:30 | 60 | 57
2018-04-27 02:00 | 56 | 54
2018-04-27 02:30 | 55 | 52
2018-04-27 03:00 | 53 | 50
2018-04-27 03:30 | 48 | 45
2018-04-27 04:00 | 49 | 45
2018-04-27 04:30 | 53 | 50
2018-04-27 05:00 | 54 | 52
2018-04-27 05:30 | 61 | 59
2018-04-27 06:00 | 71 | 69
2018-04-27 06:30 | 88 | 87
2018-04-27 07:00 | 101 | 99
2018-04-27 07:30 | 107 | 106
2018-04-27 08:00 | 95 | 93
2018-04-27 08:30 | 78 | 76
2018-04-27 09:00 | 64 | 62
2018-04-27 09:30 | 61 | 59
2018-04-27 10:00 | 57 | 54
2018-04-27 10:30 | 56 | 54
2018-04-27 11:00 | 54 | 51
2018-04-27 11:30 | 51 | 48
2018-04-27 12:00 | 52 | 49
2018-04-27 12:30 | 55 | 52
2018-04-27 13:00 | 56 | 54
2018-04-27 13:30 | 58 | 55
2018-04-27 14:00 | 64 | 62
2018-04-27 14:30 | 72 | 70
2018-04-27 15:00 | 79 | 78
2018-04-27 15:30 | 83 | 81
2018-04-27 16:00 | 57 | 55
2018-04-27 16:30 | 59 | 57
2018-04-27 17:00 | 70 | 69
2018-04-27 17:30 | 84 | 83
2018-04-27 18:00 | 95 | 94
2018-04-27 18:30 | 108 | 107
2018-04-27 19:00 | 113 | 112
2018-04-27 19:30 | 106 | 105
2018-04-27 20:00 | 99 | 98
2018-04-27 20:30 | 91 | 90
2018-04-27 21:00 | 91 | 90
2018-04-27 21:30 | 88 | 86
2018-04-27 22:00 | 76 | 75
2018-04-27 22:30 | 78 | 76
2018-04-27 23:00 | 105 | 103
2018-04-27 23:30 | 128 | 127
2018-04-28 | 164 | 162
2018-04-28 00:30 | 159 | 157
2018-04-28 01:00 | 153 | 151
2018-04-28 01:30 | 148 | 146
2018-04-28 02:00 | 144 | 142
2018-04-28 02:30 | 143 | 140
2018-04-28 03:00 | 140 | 138
2018-04-28 03:30 | 139 | 137
2018-04-28 04:00 | 137 | 135
2018-04-28 04:30 | 139 | 136
2018-04-28 05:00 | 140 | 138
2018-04-28 05:30 | 141 | 139
2018-04-28 06:00 | 144 | 142
2018-04-28 06:30 | 152 | 150
2018-04-28 07:00 | 155 | 153
2018-04-28 07:30 | 157 | 156
2018-04-28 08:00 | 146 | 144
2018-04-28 08:30 | 137 | 135
2018-04-28 09:00 | 136 | 134
2018-04-28 09:30 | 133 | 131
2018-04-28 10:00 | 127 | 126
2018-04-28 10:30 | 117 | 115
2018-04-28 11:00 | 110 | 108
2018-04-28 11:30 | 107 | 104
2018-04-28 12:00 | 105 | 103
2018-04-28 12:30 | 99 | 96
2018-04-28 13:00 | 101 | 99
2018-04-28 13:30 | 115 | 113
2018-04-28 14:00 | 114 | 112
2018-04-28 14:30 | 120 | 118
2018-04-28 15:00 | 122 | 120
2018-04-28 15:30 | 132 | 131
2018-04-28 16:00 | 155 | 154
2018-04-28 16:30 | 164 | 162
2018-04-28 17:00 | 182 | 181
2018-04-28 17:30 | 206 | 205
2018-04-28 18:00 | 221 | 219
2018-04-28 18:30 | 235 | 234
2018-04-28 19:00 | 240 | 239
2018-04-28 19:30 | 231 | 229
2018-04-28 20:00 | 221 | 219
2018-04-28 20:30 | 212 | 211
2018-04-28 21:00 | 205 | 203
2018-04-28 21:30 | 199 | 197
2018-04-28 22:00 | 191 | 189
2018-04-28 22:30 | 193 | 191
2018-04-28 23:00 | 190 | 188
2018-04-28 23:30 | 181 | 180
2018-04-29 | 175 | 173
2018-04-29 00:30 | 169 | 168
2018-04-29 01:00 | 163 | 161
2018-04-29 01:30 | 157 | 155
2018-04-29 02:00 | 153 | 152
2018-04-29 02:30 | 151 | 149
2018-04-29 03:00 | 149 | 147
2018-04-29 03:30 | 148 | 146
2018-04-29 04:00 | 146 | 144
2018-04-29 04:30 | 146 | 144
2018-04-29 05:00 | 148 | 146
2018-04-29 05:30 | 150 | 148
2018-04-29 06:00 | 152 | 150
2018-04-29 06:30 | 156 | 155
2018-04-29 07:00 | 157 | 155
2018-04-29 07:30 | 155 | 153
2018-04-29 08:00 | 138 | 136
2018-04-29 08:30 | 136 | 134
2018-04-29 09:00 | 131 | 130
2018-04-29 09:30 | 142 | 140
2018-04-29 10:00 | 135 | 134
2018-04-29 10:30 | 131 | 130
2018-04-29 11:00 | 126 | 125
2018-04-29 11:30 | 126 | 125
2018-04-29 12:00 | 129 | 127
2018-04-29 12:30 | 133 | 131
2018-04-29 13:00 | 133 | 132
2018-04-29 13:30 | 140 | 139
2018-04-29 14:00 | 129 | 127
2018-04-29 14:30 | 132 | 131
2018-04-29 15:00 | 140 | 138
2018-04-29 15:30 | 153 | 151
2018-04-29 16:00 | 163 | 161
2018-04-29 16:30 | 180 | 179
2018-04-29 17:00 | 198 | 197
2018-04-29 17:30 | 222 | 221
2018-04-29 18:00 | 240 | 239
2018-04-29 18:30 | 258 | 257
2018-04-29 19:00 | 261 | 260
2018-04-29 19:30 | 251 | 249
2018-04-29 20:00 | 238 | 236
2018-04-29 20:30 | 228 | 226
2018-04-29 21:00 | 220 | 218
2018-04-29 21:30 | 212 | 210
2018-04-29 22:00 | 199 | 197
2018-04-29 22:30 | 197 | 195
2018-04-29 23:00 | 192 | 191
2018-04-29 23:30 | 183 | 182
2018-04-30 | 176 | 175
2018-04-30 00:30 | 173 | 172
2018-04-30 01:00 | 168 | 167
2018-04-30 01:30 | 164 | 163
2018-04-30 02:00 | 161 | 160
2018-04-30 02:30 | 159 | 158
2018-04-30 03:00 | 159 | 158
2018-04-30 03:30 | 159 | 158
2018-04-30 04:00 | 159 | 158
2018-04-30 04:30 | 159 | 158
2018-04-30 05:00 | 162 | 161
2018-04-30 05:30 | 169 | 168
2018-04-30 06:00 | 179 | 177
2018-04-30 06:30 | 200 | 198
2018-04-30 07:00 | 215 | 213
2018-04-30 07:30 | 224 | 222
2018-04-30 08:00 | 209 | 207
2018-04-30 08:30 | 190 | 187
2018-04-30 09:00 | 182 | 180
2018-04-30 09:30 | 180 | 177
2018-04-30 10:00 | 146 | 143
2018-04-30 10:30 | 138 | 134
2018-04-30 11:00 | 142 | 138
2018-04-30 11:30 | 134 | 130
2018-04-30 12:00 | 131 | 129
2018-04-30 12:30 | 135 | 133
2018-04-30 13:00 | 135 | 133
2018-04-30 13:30 | 140 | 138
2018-04-30 14:00 | 136 | 133
2018-04-30 14:30 | 147 | 144
2018-04-30 15:00 | 175 | 173
2018-04-30 15:30 | 184 | 183
2018-04-30 16:00 | 191 | 189
2018-04-30 16:30 | 209 | 206
2018-04-30 17:00 | 219 | 216
2018-04-30 17:30 | 231 | 228
2018-04-30 18:00 | 237 | 234
2018-04-30 18:30 | 259 | 256
2018-04-30 19:00 | 263 | 261
2018-04-30 19:30 | 253 | 251
2018-04-30 20:00 | 251 | 249
2018-04-30 20:30 | 244 | 241
2018-04-30 21:00 | 234 | 231
2018-04-30 21:30 | 224 | 221
2018-04-30 22:00 | 213 | 210
2018-04-30 22:30 | 211 | 208
2018-04-30 23:00 | 202 | 200
2018-04-30 23:30 | 191 | 189
2018-05-01 | 184 | 182
2018-05-01 00:30 | 178 | 177
2018-05-01 01:00 | 172 | 171
2018-05-01 01:30 | 169 | 168
2018-05-01 02:00 | 165 | 164
2018-05-01 02:30 | 163 | 162
2018-05-01 03:00 | 160 | 159
2018-05-01 03:30 | 159 | 158
2018-05-01 04:00 | 159 | 158
2018-05-01 04:30 | 160 | 159
2018-05-01 05:00 | 164 | 163
2018-05-01 05:30 | 170 | 169
2018-05-01 06:00 | 182 | 181
2018-05-01 06:30 | 200 | 198
2018-05-01 07:00 | 204 | 202
2018-05-01 07:30 | 210 | 208
2018-05-01 08:00 | 204 | 201
2018-05-01 08:30 | 189 | 185
2018-05-01 09:00 | 172 | 168
2018-05-01 09:30 | 178 | 174
2018-05-01 10:00 | 178 | 174
2018-05-01 10:30 | 169 | 164
2018-05-01 11:00 | 162 | 157
2018-05-01 11:30 | 169 | 164
2018-05-01 12:00 | 174 | 169
2018-05-01 12:30 | 175 | 170
2018-05-01 13:00 | 177 | 172
2018-05-01 13:30 | 167 | 163
2018-05-01 14:00 | 181 | 177
2018-05-01 14:30 | 202 | 199
2018-05-01 15:00 | 207 | 204
2018-05-01 15:30 | 195 | 191
2018-05-01 16:00 | 193 | 189
2018-05-01 16:30 | 196 | 191
2018-05-01 17:00 | 211 | 205
2018-05-01 17:30 | 226 | 222
2018-05-01 18:00 | 239 | 234
2018-05-01 18:30 | 255 | 251
2018-05-01 19:00 | 260 | 256
2018-05-01 19:30 | 250 | 246
2018-05-01 20:00 | 239 | 235
2018-05-01 20:30 | 229 | 225
2018-05-01 21:00 | 218 | 214
2018-05-01 21:30 | 216 | 213
2018-05-01 22:00 | 209 | 205
2018-05-01 22:30 | 209 | 205
2018-05-01 23:00 | 198 | 196
2018-05-01 23:30 | 188 | 186
2018-05-02 | 181 | 179
2018-05-02 00:30 | 176 | 174
2018-05-02 01:00 | 169 | 168
2018-05-02 01:30 | 167 | 165
2018-05-02 02:00 | 162 | 160
2018-05-02 02:30 | 159 | 158
2018-05-02 03:00 | 159 | 158
2018-05-02 03:30 | 159 | 158
2018-05-02 04:00 | 158 | 156
2018-05-02 04:30 | 159 | 158
2018-05-02 05:00 | 159 | 158
2018-05-02 05:30 | 154 | 153
2018-05-02 06:00 | 161 | 160
2018-05-02 06:30 | 184 | 183
2018-05-02 07:00 | 194 | 193
2018-05-02 07:30 | 208 | 207
2018-05-02 08:00 | 225 | 223
2018-05-02 08:30 | 222 | 220
2018-05-02 09:00 | 210 | 208
2018-05-02 09:30 | 197 | 195
2018-05-02 10:00 | 191 | 188
2018-05-02 10:30 | 178 | 176
2018-05-02 11:00 | 179 | 176
2018-05-02 11:30 | 173 | 171
2018-05-02 12:00 | 180 | 178
2018-05-02 12:30 | 187 | 184
2018-05-02 13:00 | 189 | 186
2018-05-02 13:30 | 187 | 185
2018-05-02 14:00 | 202 | 200
2018-05-02 14:30 | 205 | 203
2018-05-02 15:00 | 201 | 199
2018-05-02 15:30 | 197 | 194
2018-05-02 16:00 | 199 | 196
2018-05-02 16:30 | 211 | 209
2018-05-02 17:00 | 213 | 211
2018-05-02 17:30 | 224 | 221
2018-05-02 18:00 | 237 | 235
2018-05-02 18:30 | 250 | 248
2018-05-02 19:00 | 255 | 253
2018-05-02 19:30 | 248 | 247
2018-05-02 20:00 | 238 | 236
2018-05-02 20:30 | 226 | 224
2018-05-02 21:00 | 216 | 213
2018-05-02 21:30 | 205 | 203
2018-05-02 22:00 | 194 | 192
2018-05-02 22:30 | 180 | 178
2018-05-02 23:00 | 169 | 166
2018-05-02 23:30 | 161 | 158
2018-05-03 | 153 | 150
2018-05-03 00:30 | 153 | 150
2018-05-03 01:00 | 165 | 162
2018-05-03 01:30 | 160 | 158
2018-05-03 02:00 | 136 | 135
2018-05-03 02:30 | 137 | 136
2018-05-03 03:00 | 133 | 131
2018-05-03 03:30 | 137 | 135
2018-05-03 04:00 | 141 | 139
2018-05-03 04:30 | 120 | 118
2018-05-03 05:00 | 98 | 97
2018-05-03 05:30 | 103 | 102
2018-05-03 06:00 | 119 | 117
2018-05-03 06:30 | 145 | 143
2018-05-03 07:00 | 161 | 160
2018-05-03 07:30 | 175 | 174
2018-05-03 08:00 | 165 | 164
2018-05-03 08:30 | 124 | 123
2018-05-03 09:00 | 119 | 118
2018-05-03 09:30 | 105 | 103
2018-05-03 10:00 | 99 | 98
2018-05-03 10:30 | 94 | 93
2018-05-03 11:00 | 109 | 108
2018-05-03 11:30 | 102 | 101
2018-05-03 12:00 | 87 | 85
2018-05-03 12:30 | 81 | 79
2018-05-03 13:00 | 78 | 76
2018-05-03 13:30 | 79 | 77
2018-05-03 14:00 | 83 | 81
2018-05-03 14:30 | 82 | 79
2018-05-03 15:00 | 86 | 84
2018-05-03 15:30 | 103 | 102
2018-05-03 16:00 | 114 | 114
2018-05-03 16:30 | 125 | 125
2018-05-03 17:00 | 136 | 136
2018-05-03 17:30 | 142 | 141
2018-05-03 18:00 | 151 | 150
2018-05-03 18:30 | 166 | 165
2018-05-03 19:00 | 173 | 172
2018-05-03 19:30 | 166 | 165
2018-05-03 20:00 | 157 | 157
2018-05-03 20:30 | 147 | 146
2018-05-03 21:00 | 170 | 169
2018-05-03 21:30 | 193 | 192
2018-05-03 22:00 | 223 | 222
2018-05-03 22:30 | 210 | 209
2018-05-03 23:00 | 200 | 199
2018-05-03 23:30 | 187 | 186
2018-05-04 | 179 | 178
2018-05-04 00:30 | 174 | 173
2018-05-04 01:00 | 168 | 167
2018-05-04 01:30 | 165 | 165
2018-05-04 02:00 | 162 | 161
2018-05-04 02:30 | 159 | 158
2018-05-04 03:00 | 156 | 155
2018-05-04 03:30 | 155 | 155
2018-05-04 04:00 | 157 | 156
2018-05-04 04:30 | 158 | 157
2018-05-04 05:00 | 162 | 161
2018-05-04 05:30 | 169 | 168
2018-05-04 06:00 | 178 | 177
2018-05-04 06:30 | 192 | 191
2018-05-04 07:00 | 209 | 208
2018-05-04 07:30 | 218 | 217
2018-05-04 08:00 | 215 | 214
2018-05-04 08:30 | 202 | 202
2018-05-04 09:00 | 186 | 186
2018-05-04 09:30 | 176 | 175
2018-05-04 10:00 | 175 | 174
2018-05-04 10:30 | 167 | 167
2018-05-04 11:00 | 165 | 165
2018-05-04 11:30 | 166 | 165
2018-05-04 12:00 | 170 | 169
2018-05-04 12:30 | 166 | 165
2018-05-04 13:00 | 177 | 176
2018-05-04 13:30 | 180 | 179
2018-05-04 14:00 | 182 | 181
2018-05-04 14:30 | 181 | 180
2018-05-04 15:00 | 182 | 181
2018-05-04 15:30 | 179 | 178
2018-05-04 16:00 | 190 | 189
2018-05-04 16:30 | 202 | 201
2018-05-04 17:00 | 215 | 214
2018-05-04 17:30 | 227 | 226
2018-05-04 18:00 | 239 | 238
2018-05-04 18:30 | 249 | 248
2018-05-04 19:00 | 253 | 253
2018-05-04 19:30 | 247 | 246
2018-05-04 20:00 | 238 | 237
2018-05-04 20:30 | 230 | 229
2018-05-04 21:00 | 220 | 219
2018-05-04 21:30 | 226 | 225
2018-05-04 22:00 | 220 | 219
2018-05-04 22:30 | 211 | 210
2018-05-04 23:00 | 200 | 199
2018-05-04 23:30 | 187 | 186
2018-05-05 | 177 | 176
2018-05-05 00:30 | 175 | 174
2018-05-05 01:00 | 170 | 169
2018-05-05 01:30 | 165 | 164
2018-05-05 02:00 | 162 | 161
2018-05-05 02:30 | 160 | 158
2018-05-05 03:00 | 157 | 156
2018-05-05 03:30 | 156 | 154
2018-05-05 04:00 | 157 | 155
2018-05-05 04:30 | 157 | 155
2018-05-05 05:00 | 157 | 156
2018-05-05 05:30 | 161 | 160
2018-05-05 06:00 | 166 | 165
2018-05-05 06:30 | 171 | 169
2018-05-05 07:00 | 174 | 172
2018-05-05 07:30 | 175 | 174
2018-05-05 08:00 | 173 | 171
2018-05-05 08:30 | 167 | 166
2018-05-05 09:00 | 154 | 153
2018-05-05 09:30 | 145 | 143
2018-05-05 10:00 | 139 | 138
2018-05-05 10:30 | 137 | 136
2018-05-05 11:00 | 131 | 129
2018-05-05 11:30 | 133 | 131
2018-05-05 12:00 | 129 | 127
2018-05-05 12:30 | 130 | 129
2018-05-05 13:00 | 128 | 126
2018-05-05 13:30 | 131 | 129
2018-05-05 14:00 | 132 | 130
2018-05-05 14:30 | 137 | 135
2018-05-05 15:00 | 143 | 141
2018-05-05 15:30 | 150 | 148
2018-05-05 16:00 | 167 | 165
2018-05-05 16:30 | 181 | 179
2018-05-05 17:00 | 187 | 185
2018-05-05 17:30 | 196 | 194
2018-05-05 18:00 | 211 | 209
2018-05-05 18:30 | 225 | 224
2018-05-05 19:00 | 229 | 227
2018-05-05 19:30 | 221 | 219
2018-05-05 20:00 | 211 | 209
2018-05-05 20:30 | 202 | 200
2018-05-05 21:00 | 203 | 201
2018-05-05 21:30 | 201 | 198
2018-05-05 22:00 | 194 | 191
2018-05-05 22:30 | 195 | 192
2018-05-05 23:00 | 191 | 188
2018-05-05 23:30 | 181 | 180
2018-05-06 | 177 | 175
2018-05-06 00:30 | 173 | 171
2018-05-06 01:00 | 168 | 166
2018-05-06 01:30 | 163 | 162
2018-05-06 02:00 | 161 | 159
2018-05-06 02:30 | 158 | 157
2018-05-06 03:00 | 156 | 155
2018-05-06 03:30 | 154 | 153
2018-05-06 04:00 | 154 | 152
2018-05-06 04:30 | 154 | 152
2018-05-06 05:00 | 154 | 152
2018-05-06 05:30 | 156 | 155
2018-05-06 06:00 | 157 | 155
2018-05-06 06:30 | 159 | 158
2018-05-06 07:00 | 163 | 161
2018-05-06 07:30 | 165 | 163
2018-05-06 08:00 | 159 | 157
2018-05-06 08:30 | 156 | 154
2018-05-06 09:00 | 155 | 153
2018-05-06 09:30 | 149 | 147
2018-05-06 10:00 | 135 | 133
2018-05-06 10:30 | 130 | 128
2018-05-06 11:00 | 129 | 127
2018-05-06 11:30 | 126 | 124
2018-05-06 12:00 | 128 | 126
2018-05-06 12:30 | 125 | 123
2018-05-06 13:00 | 127 | 125
2018-05-06 13:30 | 131 | 129
2018-05-06 14:00 | 135 | 133
2018-05-06 14:30 | 141 | 139
2018-05-06 15:00 | 141 | 139
2018-05-06 15:30 | 152 | 150
2018-05-06 16:00 | 159 | 157
2018-05-06 16:30 | 169 | 168
2018-05-06 17:00 | 182 | 180
2018-05-06 17:30 | 203 | 202
2018-05-06 18:00 | 215 | 214
2018-05-06 18:30 | 232 | 231
2018-05-06 19:00 | 236 | 235
2018-05-06 19:30 | 229 | 227
2018-05-06 20:00 | 219 | 217
2018-05-06 20:30 | 209 | 207
2018-05-06 21:00 | 202 | 200
2018-05-06 21:30 | 210 | 208
2018-05-06 22:00 | 205 | 203
2018-05-06 22:30 | 199 | 196
2018-05-06 23:00 | 189 | 187
2018-05-06 23:30 | 182 | 179
2018-05-07 | 175 | 173
2018-05-07 00:30 | 172 | 169
2018-05-07 01:00 | 168 | 165
2018-05-07 01:30 | 161 | 159
2018-05-07 02:00 | 159 | 157
2018-05-07 02:30 | 157 | 155
2018-05-07 03:00 | 157 | 155
2018-05-07 03:30 | 157 | 155
2018-05-07 04:00 | 154 | 152
2018-05-07 04:30 | 157 | 155
2018-05-07 05:00 | 157 | 155
2018-05-07 05:30 | 157 | 155
2018-05-07 06:00 | 159 | 157
2018-05-07 06:30 | 164 | 162
2018-05-07 07:00 | 168 | 167
2018-05-07 07:30 | 171 | 169
2018-05-07 08:00 | 164 | 162
2018-05-07 08:30 | 159 | 157
2018-05-07 09:00 | 155 | 153
2018-05-07 09:30 | 150 | 148
2018-05-07 10:00 | 140 | 139
2018-05-07 10:30 | 137 | 135
2018-05-07 11:00 | 132 | 130
2018-05-07 11:30 | 130 | 129
2018-05-07 12:00 | 135 | 134
2018-05-07 12:30 | 137 | 136
2018-05-07 13:00 | 139 | 137
2018-05-07 13:30 | 143 | 142
2018-05-07 14:00 | 148 | 147
2018-05-07 14:30 | 143 | 142
2018-05-07 15:00 | 151 | 150
2018-05-07 15:30 | 158 | 157
2018-05-07 16:00 | 170 | 168
2018-05-07 16:30 | 181 | 180
2018-05-07 17:00 | 186 | 185
2018-05-07 17:30 | 205 | 203
2018-05-07 18:00 | 226 | 224
2018-05-07 18:30 | 244 | 242
2018-05-07 19:00 | 247 | 246
2018-05-07 19:30 | 248 | 246
2018-05-07 20:00 | 240 | 239
2018-05-07 20:30 | 229 | 227
2018-05-07 21:00 | 218 | 217
2018-05-07 21:30 | 209 | 207
2018-05-07 22:00 | 199 | 197
2018-05-07 22:30 | 188 | 186
2018-05-07 23:00 | 178 | 176
2018-05-07 23:30 | 181 | 179
2018-05-08 | 176 | 174
2018-05-08 00:30 | 172 | 171
2018-05-08 01:00 | 168 | 167
2018-05-08 01:30 | 164 | 162
2018-05-08 02:00 | 162 | 160
2018-05-08 02:30 | 160 | 158
2018-05-08 03:00 | 159 | 157
2018-05-08 03:30 | 156 | 155
2018-05-08 04:00 | 158 | 156
2018-05-08 04:30 | 159 | 158
2018-05-08 05:00 | 161 | 159
2018-05-08 05:30 | 168 | 167
2018-05-08 06:00 | 177 | 176
2018-05-08 06:30 | 196 | 195
2018-05-08 07:00 | 214 | 213
2018-05-08 07:30 | 228 | 226
2018-05-08 08:00 | 231 | 230
2018-05-08 08:30 | 224 | 223
2018-05-08 09:00 | 209 | 208
2018-05-08 09:30 | 204 | 203
2018-05-08 10:00 | 198 | 196
2018-05-08 10:30 | 191 | 189
2018-05-08 11:00 | 188 | 187
2018-05-08 11:30 | 188 | 187
2018-05-08 12:00 | 185 | 184
2018-05-08 12:30 | 185 | 184
2018-05-08 13:00 | 192 | 191
2018-05-08 13:30 | 198 | 196
2018-05-08 14:00 | 196 | 194
2018-05-08 14:30 | 198 | 196
2018-05-08 15:00 | 199 | 198
2018-05-08 15:30 | 202 | 201
2018-05-08 16:00 | 209 | 207
2018-05-08 16:30 | 221 | 220
2018-05-08 17:00 | 237 | 235
2018-05-08 17:30 | 238 | 236
2018-05-08 18:00 | 221 | 219
2018-05-08 18:30 | 257 | 255
2018-05-08 19:00 | 269 | 268
2018-05-08 19:30 | 260 | 258
2018-05-08 20:00 | 247 | 245
2018-05-08 20:30 | 237 | 235
2018-05-08 21:00 | 225 | 223
2018-05-08 21:30 | 214 | 212
2018-05-08 22:00 | 204 | 201
2018-05-08 22:30 | 190 | 187
2018-05-08 23:00 | 173 | 172
2018-05-08 23:30 | 161 | 160
2018-05-09 | 177 | 176
2018-05-09 00:30 | 178 | 177
2018-05-09 01:00 | 173 | 172
2018-05-09 01:30 | 169 | 167
2018-05-09 02:00 | 167 | 165
2018-05-09 02:30 | 163 | 162
2018-05-09 03:00 | 160 | 158
2018-05-09 03:30 | 160 | 158
2018-05-09 04:00 | 160 | 158
2018-05-09 04:30 | 163 | 161
2018-05-09 05:00 | 168 | 166
2018-05-09 05:30 | 173 | 171
2018-05-09 06:00 | 183 | 181
2018-05-09 06:30 | 197 | 195
2018-05-09 07:00 | 213 | 212
2018-05-09 07:30 | 229 | 228
2018-05-09 08:00 | 232 | 231
2018-05-09 08:30 | 231 | 229
2018-05-09 09:00 | 222 | 220
2018-05-09 09:30 | 204 | 202
2018-05-09 10:00 | 189 | 186
2018-05-09 10:30 | 187 | 183
2018-05-09 11:00 | 172 | 168
2018-05-09 11:30 | 168 | 163
2018-05-09 12:00 | 165 | 162
2018-05-09 12:30 | 184 | 181
2018-05-09 13:00 | 194 | 191
2018-05-09 13:30 | 195 | 193
2018-05-09 14:00 | 190 | 188
2018-05-09 14:30 | 201 | 199
2018-05-09 15:00 | 208 | 206
2018-05-09 15:30 | 225 | 223
2018-05-09 16:00 | 227 | 225
2018-05-09 16:30 | 234 | 232
2018-05-09 17:00 | 240 | 238
2018-05-09 17:30 | 260 | 258
2018-05-09 18:00 | 269 | 267
2018-05-09 18:30 | 286 | 284
2018-05-09 19:00 | 292 | 290
2018-05-09 19:30 | 283 | 280
2018-05-09 20:00 | 272 | 269
2018-05-09 20:30 | 260 | 257
2018-05-09 21:00 | 249 | 246
2018-05-09 21:30 | 237 | 235
2018-05-09 22:00 | 223 | 221
2018-05-09 22:30 | 220 | 218
2018-05-09 23:00 | 211 | 209
2018-05-09 23:30 | 201 | 199
2018-05-10 | 189 | 188
2018-05-10 00:30 | 184 | 182
2018-05-10 01:00 | 179 | 177
2018-05-10 01:30 | 174 | 172
2018-05-10 02:00 | 171 | 170
2018-05-10 02:30 | 168 | 167
2018-05-10 03:00 | 166 | 165
2018-05-10 03:30 | 167 | 165
2018-05-10 04:00 | 166 | 165
2018-05-10 04:30 | 170 | 168
2018-05-10 05:00 | 171 | 170
2018-05-10 05:30 | 177 | 176
2018-05-10 06:00 | 186 | 185
2018-05-10 06:30 | 205 | 204
2018-05-10 07:00 | 220 | 219
2018-05-10 07:30 | 232 | 231
2018-05-10 08:00 | 226 | 225
2018-05-10 08:30 | 218 | 216
2018-05-10 09:00 | 203 | 202
2018-05-10 09:30 | 196 | 195
2018-05-10 10:00 | 195 | 194
2018-05-10 10:30 | 192 | 191
2018-05-10 11:00 | 187 | 186
2018-05-10 11:30 | 188 | 187
2018-05-10 12:00 | 188 | 187
2018-05-10 12:30 | 201 | 200
2018-05-10 13:00 | 200 | 199
2018-05-10 13:30 | 199 | 197
2018-05-10 14:00 | 188 | 187
2018-05-10 14:30 | 190 | 189
2018-05-10 15:00 | 198 | 197
2018-05-10 15:30 | 204 | 203
2018-05-10 16:00 | 217 | 216
2018-05-10 16:30 | 225 | 224
2018-05-10 17:00 | 251 | 250
2018-05-10 17:30 | 261 | 259
2018-05-10 18:00 | 270 | 268
2018-05-10 18:30 | 273 | 272
2018-05-10 19:00 | 280 | 278
2018-05-10 19:30 | 270 | 269
2018-05-10 20:00 | 261 | 260
2018-05-10 20:30 | 250 | 248
2018-05-10 21:00 | 248 | 247
2018-05-10 21:30 | 255 | 254
2018-05-10 22:00 | 245 | 243
2018-05-10 22:30 | 231 | 230
2018-05-10 23:00 | 219 | 217
2018-05-10 23:30 | 204 | 202
2018-05-11 | 193 | 191
2018-05-11 00:30 | 186 | 184
2018-05-11 01:00 | 181 | 179
2018-05-11 01:30 | 176 | 175
2018-05-11 02:00 | 174 | 173
2018-05-11 02:30 | 173 | 172
2018-05-11 03:00 | 170 | 169
2018-05-11 03:30 | 171 | 170
2018-05-11 04:00 | 170 | 169
2018-05-11 04:30 | 158 | 157
2018-05-11 05:00 | 137 | 136
2018-05-11 05:30 | 140 | 138
2018-05-11 06:00 | 149 | 147
2018-05-11 06:30 | 168 | 166
2018-05-11 07:00 | 184 | 183
2018-05-11 07:30 | 192 | 191
2018-05-11 08:00 | 167 | 165
2018-05-11 08:30 | 119 | 116
2018-05-11 09:00 | 109 | 107
2018-05-11 09:30 | 101 | 99
2018-05-11 10:00 | 122 | 120
2018-05-11 10:30 | 128 | 125
2018-05-11 11:00 | 131 | 128
2018-05-11 11:30 | 131 | 128
2018-05-11 12:00 | 125 | 122
2018-05-11 12:30 | 113 | 110
2018-05-11 13:00 | 118 | 115
2018-05-11 13:30 | 117 | 114
2018-05-11 14:00 | 135 | 132
2018-05-11 14:30 | 142 | 140
2018-05-11 15:00 | 147 | 144
2018-05-11 15:30 | 145 | 142
2018-05-11 16:00 | 119 | 116
2018-05-11 16:30 | 120 | 118
2018-05-11 17:00 | 131 | 128
2018-05-11 17:30 | 136 | 134
2018-05-11 18:00 | 135 | 133
2018-05-11 18:30 | 146 | 144
2018-05-11 19:00 | 148 | 145
2018-05-11 19:30 | 139 | 137
2018-05-11 20:00 | 133 | 131
2018-05-11 20:30 | 123 | 121
2018-05-11 21:00 | 114 | 112
2018-05-11 21:30 | 104 | 102
2018-05-11 22:00 | 107 | 104
2018-05-11 22:30 | 111 | 109
2018-05-11 23:00 | 103 | 101
2018-05-11 23:30 | 125 | 123
2018-05-12 | 148 | 146
2018-05-12 00:30 | 184 | 183
2018-05-12 01:00 | 176 | 175
2018-05-12 01:30 | 172 | 170
2018-05-12 02:00 | 168 | 166
2018-05-12 02:30 | 165 | 165
2018-05-12 03:00 | 161 | 160
2018-05-12 03:30 | 159 | 158
2018-05-12 04:00 | 158 | 157
2018-05-12 04:30 | 158 | 158
2018-05-12 05:00 | 159 | 158
2018-05-12 05:30 | 163 | 163
2018-05-12 06:00 | 169 | 169
2018-05-12 06:30 | 178 | 177
2018-05-12 07:00 | 179 | 178
2018-05-12 07:30 | 180 | 179
2018-05-12 08:00 | 176 | 175
2018-05-12 08:30 | 166 | 165
2018-05-12 09:00 | 159 | 158
2018-05-12 09:30 | 155 | 154
2018-05-12 10:00 | 146 | 145
2018-05-12 10:30 | 128 | 127
2018-05-12 11:00 | 120 | 118
2018-05-12 11:30 | 115 | 113
2018-05-12 12:00 | 115 | 113
2018-05-12 12:30 | 112 | 110
2018-05-12 13:00 | 116 | 114
2018-05-12 13:30 | 117 | 115
2018-05-12 14:00 | 123 | 121
2018-05-12 14:30 | 128 | 126
2018-05-12 15:00 | 136 | 134
2018-05-12 15:30 | 148 | 146
2018-05-12 16:00 | 163 | 161
2018-05-12 16:30 | 178 | 176
2018-05-12 17:00 | 196 | 194
2018-05-12 17:30 | 211 | 209
2018-05-12 18:00 | 228 | 226
2018-05-12 18:30 | 240 | 239
2018-05-12 19:00 | 242 | 241
2018-05-12 19:30 | 233 | 231
2018-05-12 20:00 | 224 | 222
2018-05-12 20:30 | 190 | 187
2018-05-12 21:00 | 182 | 180
2018-05-12 21:30 | 176 | 173
2018-05-12 22:00 | 178 | 175
2018-05-12 22:30 | 173 | 171
2018-05-12 23:00 | 166 | 164
2018-05-12 23:30 | 157 | 155
2018-05-13 | 150 | 148
2018-05-13 00:30 | 146 | 144
2018-05-13 01:00 | 142 | 140
2018-05-13 01:30 | 154 | 152
2018-05-13 02:00 | 150 | 148
2018-05-13 02:30 | 149 | 147
2018-05-13 03:00 | 146 | 145
2018-05-13 03:30 | 146 | 145
2018-05-13 04:00 | 145 | 144
2018-05-13 04:30 | 145 | 144
2018-05-13 05:00 | 146 | 145
2018-05-13 05:30 | 149 | 148
2018-05-13 06:00 | 151 | 150
2018-05-13 06:30 | 157 | 156
2018-05-13 07:00 | 166 | 165
2018-05-13 07:30 | 169 | 168
2018-05-13 08:00 | 190 | 190
2018-05-13 08:30 | 162 | 161
2018-05-13 09:00 | 154 | 153
2018-05-13 09:30 | 149 | 148
2018-05-13 10:00 | 144 | 143
2018-05-13 10:30 | 138 | 137
2018-05-13 11:00 | 134 | 133
2018-05-13 11:30 | 132 | 131
2018-05-13 12:00 | 127 | 125
2018-05-13 12:30 | 129 | 128
2018-05-13 13:00 | 147 | 146
2018-05-13 13:30 | 154 | 152
2018-05-13 14:00 | 122 | 120
2018-05-13 14:30 | 107 | 106
2018-05-13 15:00 | 111 | 110
2018-05-13 15:30 | 119 | 118
2018-05-13 16:00 | 140 | 139
2018-05-13 16:30 | 158 | 156
2018-05-13 17:00 | 171 | 170
2018-05-13 17:30 | 176 | 174
2018-05-13 18:00 | 195 | 194
2018-05-13 18:30 | 214 | 213
2018-05-13 19:00 | 214 | 213
2018-05-13 19:30 | 206 | 204
2018-05-13 20:00 | 198 | 196
2018-05-13 20:30 | 198 | 196
2018-05-13 21:00 | 195 | 192
2018-05-13 21:30 | 197 | 194
2018-05-13 22:00 | 191 | 189
2018-05-13 22:30 | 180 | 178
2018-05-13 23:00 | 168 | 166
2018-05-13 23:30 | 162 | 159
2018-05-14 | 152 | 150
2018-05-14 00:30 | 149 | 147
2018-05-14 01:00 | 144 | 143
2018-05-14 01:30 | 141 | 140
2018-05-14 02:00 | 138 | 137
2018-05-14 02:30 | 137 | 136
2018-05-14 03:00 | 137 | 136
2018-05-14 03:30 | 134 | 133
2018-05-14 04:00 | 134 | 133
2018-05-14 04:30 | 137 | 135
2018-05-14 05:00 | 141 | 140
2018-05-14 05:30 | 148 | 147
2018-05-14 06:00 | 158 | 157
2018-05-14 06:30 | 176 | 175
2018-05-14 07:00 | 192 | 191
2018-05-14 07:30 | 200 | 199
2018-05-14 08:00 | 191 | 190
2018-05-14 08:30 | 173 | 172
2018-05-14 09:00 | 156 | 154
2018-05-14 09:30 | 147 | 146
2018-05-14 10:00 | 139 | 138
2018-05-14 10:30 | 122 | 121
2018-05-14 11:00 | 96 | 94
2018-05-14 11:30 | 92 | 90
2018-05-14 12:00 | 93 | 91
2018-05-14 12:30 | 92 | 91
2018-05-14 13:00 | 96 | 95
2018-05-14 13:30 | 86 | 84
2018-05-14 14:00 | 57 | 55
2018-05-14 14:30 | 30 | 24
2018-05-14 15:00 | 29 | 24
2018-05-14 15:30 | 33 | 29
2018-05-14 16:00 | 46 | 44
2018-05-14 16:30 | 57 | 55
2018-05-14 17:00 | 54 | 52
2018-05-14 17:30 | 91 | 89
2018-05-14 18:00 | 112 | 110
2018-05-14 18:30 | 130 | 128
2018-05-14 19:00 | 134 | 132
2018-05-14 19:30 | 124 | 123
2018-05-14 20:00 | 112 | 110
2018-05-14 20:30 | 99 | 98
2018-05-14 21:00 | 97 | 95
2018-05-14 21:30 | 91 | 90
2018-05-14 22:00 | 92 | 91
2018-05-14 22:30 | 84 | 82
2018-05-14 23:00 | 107 | 106
2018-05-14 23:30 | 108 | 106
2018-05-15 | 102 | 100
2018-05-15 00:30 | 98 | 96
2018-05-15 01:00 | 92 | 90
2018-05-15 01:30 | 90 | 88
2018-05-15 02:00 | 87 | 85
2018-05-15 02:30 | 85 | 83
2018-05-15 03:00 | 83 | 81
2018-05-15 03:30 | 82 | 80
2018-05-15 04:00 | 81 | 80
2018-05-15 04:30 | 83 | 81
2018-05-15 05:00 | 86 | 84
2018-05-15 05:30 | 94 | 92
2018-05-15 06:00 | 102 | 100
2018-05-15 06:30 | 83 | 81
2018-05-15 07:00 | 89 | 88
2018-05-15 07:30 | 98 | 97
2018-05-15 08:00 | 93 | 92
2018-05-15 08:30 | 82 | 81
2018-05-15 09:00 | 106 | 105
2018-05-15 09:30 | 109 | 108
2018-05-15 10:00 | 91 | 90
2018-05-15 10:30 | 79 | 78
2018-05-15 11:00 | 76 | 75
2018-05-15 11:30 | 76 | 74
2018-05-15 12:00 | 75 | 73
2018-05-15 12:30 | 75 | 73
2018-05-15 13:00 | 78 | 76
2018-05-15 13:30 | 79 | 78
2018-05-15 14:00 | 74 | 72
2018-05-15 14:30 | 39 | 33
2018-05-15 15:00 | 36 | 29
2018-05-15 15:30 | 41 | 36
2018-05-15 16:00 | 50 | 48
2018-05-15 16:30 | 62 | 60
2018-05-15 17:00 | 74 | 72
2018-05-15 17:30 | 94 | 93
2018-05-15 18:00 | 105 | 104
2018-05-15 18:30 | 106 | 104
2018-05-15 19:00 | 128 | 127
2018-05-15 19:30 | 126 | 125
2018-05-15 20:00 | 124 | 123
2018-05-15 20:30 | 117 | 116
2018-05-15 21:00 | 155 | 154
2018-05-15 21:30 | 113 | 112
2018-05-15 22:00 | 99 | 98
2018-05-15 22:30 | 85 | 83
2018-05-15 23:00 | 67 | 65
2018-05-15 23:30 | 50 | 48
2018-05-16 | 57 | 55
2018-05-16 00:30 | 51 | 49
2018-05-16 01:00 | 83 | 81
2018-05-16 01:30 | 111 | 109
2018-05-16 02:00 | 155 | 153
2018-05-16 02:30 | 153 | 151
2018-05-16 03:00 | 150 | 148
2018-05-16 03:30 | 150 | 148
2018-05-16 04:00 | 150 | 148
2018-05-16 04:30 | 151 | 150
2018-05-16 05:00 | 156 | 154
2018-05-16 05:30 | 163 | 162
2018-05-16 06:00 | 173 | 172
2018-05-16 06:30 | 192 | 190
2018-05-16 07:00 | 210 | 209
2018-05-16 07:30 | 223 | 221
2018-05-16 08:00 | 205 | 204
2018-05-16 08:30 | 188 | 187
2018-05-16 09:00 | 185 | 184
2018-05-16 09:30 | 178 | 177
2018-05-16 10:00 | 177 | 176
2018-05-16 10:30 | 173 | 171
2018-05-16 11:00 | 163 | 162
2018-05-16 11:30 | 161 | 160
2018-05-16 12:00 | 161 | 160
2018-05-16 12:30 | 165 | 164
2018-05-16 13:00 | 166 | 164
2018-05-16 13:30 | 167 | 166
2018-05-16 14:00 | 164 | 163
2018-05-16 14:30 | 168 | 166
2018-05-16 15:00 | 177 | 176
2018-05-16 15:30 | 183 | 182
2018-05-16 16:00 | 198 | 197
2018-05-16 16:30 | 200 | 198
2018-05-16 17:00 | 201 | 200
2018-05-16 17:30 | 215 | 213
2018-05-16 18:00 | 231 | 229
2018-05-16 18:30 | 244 | 243
2018-05-16 19:00 | 247 | 246
2018-05-16 19:30 | 247 | 246
2018-05-16 20:00 | 241 | 239
2018-05-16 20:30 | 243 | 242
2018-05-16 21:00 | 238 | 237
2018-05-16 21:30 | 228 | 227
2018-05-16 22:00 | 215 | 213
2018-05-16 22:30 | 200 | 199
2018-05-16 23:00 | 190 | 188
2018-05-16 23:30 | 182 | 181
2018-05-17 | 174 | 172
2018-05-17 00:30 | 169 | 168
2018-05-17 01:00 | 163 | 161
2018-05-17 01:30 | 149 | 147
2018-05-17 02:00 | 117 | 114
2018-05-17 02:30 | 117 | 114
2018-05-17 03:00 | 134 | 132
2018-05-17 03:30 | 146 | 144
2018-05-17 04:00 | 151 | 149
2018-05-17 04:30 | 155 | 153
2018-05-17 05:00 | 159 | 157
2018-05-17 05:30 | 168 | 166
2018-05-17 06:00 | 177 | 176
2018-05-17 06:30 | 194 | 193
2018-05-17 07:00 | 214 | 213
2018-05-17 07:30 | 234 | 232
2018-05-17 08:00 | 243 | 242
2018-05-17 08:30 | 239 | 238
2018-05-17 09:00 | 229 | 227
2018-05-17 09:30 | 220 | 218
2018-05-17 10:00 | 215 | 214
2018-05-17 10:30 | 204 | 202
2018-05-17 11:00 | 200 | 198
2018-05-17 11:30 | 197 | 195
2018-05-17 12:00 | 199 | 197
2018-05-17 12:30 | 201 | 199
2018-05-17 13:00 | 195 | 193
2018-05-17 13:30 | 196 | 194
2018-05-17 14:00 | 196 | 194
2018-05-17 14:30 | 196 | 194
2018-05-17 15:00 | 197 | 195
2018-05-17 15:30 | 208 | 206
2018-05-17 16:00 | 210 | 208
2018-05-17 16:30 | 206 | 204
2018-05-17 17:00 | 208 | 206
2018-05-17 17:30 | 222 | 220
2018-05-17 18:00 | 238 | 237
2018-05-17 18:30 | 250 | 249
2018-05-17 19:00 | 254 | 253
2018-05-17 19:30 | 257 | 256
2018-05-17 20:00 | 252 | 250
2018-05-17 20:30 | 253 | 252
2018-05-17 21:00 | 247 | 245
2018-05-17 21:30 | 233 | 231
2018-05-17 22:00 | 220 | 218
2018-05-17 22:30 | 208 | 206
2018-05-17 23:00 | 195 | 192
2018-05-17 23:30 | 171 | 168
2018-05-18 | 175 | 173
2018-05-18 00:30 | 172 | 170
2018-05-18 01:00 | 166 | 164
2018-05-18 01:30 | 163 | 161
2018-05-18 02:00 | 160 | 159
2018-05-18 02:30 | 157 | 156
2018-05-18 03:00 | 157 | 155
2018-05-18 03:30 | 157 | 155
2018-05-18 04:00 | 157 | 155
2018-05-18 04:30 | 157 | 155
2018-05-18 05:00 | 160 | 158
2018-05-18 05:30 | 169 | 168
2018-05-18 06:00 | 181 | 179
2018-05-18 06:30 | 198 | 195
2018-05-18 07:00 | 208 | 205
2018-05-18 07:30 | 225 | 223
2018-05-18 08:00 | 228 | 226
2018-05-18 08:30 | 208 | 205
2018-05-18 09:00 | 203 | 201
2018-05-18 09:30 | 190 | 188
2018-05-18 10:00 | 182 | 180
2018-05-18 10:30 | 172 | 169
2018-05-18 11:00 | 170 | 167
2018-05-18 11:30 | 165 | 162
2018-05-18 12:00 | 166 | 164
2018-05-18 12:30 | 173 | 170
2018-05-18 13:00 | 173 | 170
2018-05-18 13:30 | 178 | 175
2018-05-18 14:00 | 171 | 169
2018-05-18 14:30 | 170 | 167
2018-05-18 15:00 | 172 | 170
2018-05-18 15:30 | 183 | 180
2018-05-18 16:00 | 187 | 185
2018-05-18 16:30 | 177 | 174
2018-05-18 17:00 | 164 | 160
2018-05-18 17:30 | 200 | 197
2018-05-18 18:00 | 223 | 221
2018-05-18 18:30 | 233 | 231
2018-05-18 19:00 | 235 | 233
2018-05-18 19:30 | 229 | 226
2018-05-18 20:00 | 219 | 217
2018-05-18 20:30 | 223 | 221
2018-05-18 21:00 | 230 | 228
2018-05-18 21:30 | 227 | 225
2018-05-18 22:00 | 217 | 214
2018-05-18 22:30 | 208 | 205
2018-05-18 23:00 | 199 | 196
2018-05-18 23:30 | 188 | 185
2018-05-19 | 182 | 179
2018-05-19 00:30 | 175 | 172
2018-05-19 01:00 | 171 | 168
2018-05-19 01:30 | 167 | 164
2018-05-19 02:00 | 162 | 159
2018-05-19 02:30 | 159 | 157
2018-05-19 03:00 | 159 | 157
2018-05-19 03:30 | 157 | 154
2018-05-19 04:00 | 157 | 154
2018-05-19 04:30 | 157 | 154
2018-05-19 05:00 | 159 | 156
2018-05-19 05:30 | 162 | 159
2018-05-19 06:00 | 166 | 163
2018-05-19 06:30 | 173 | 170
2018-05-19 07:00 | 178 | 175
2018-05-19 07:30 | 184 | 182
2018-05-19 08:00 | 181 | 178
2018-05-19 08:30 | 179 | 177
2018-05-19 09:00 | 177 | 176
2018-05-19 09:30 | 178 | 176
2018-05-19 10:00 | 174 | 173
2018-05-19 10:30 | 167 | 165
2018-05-19 11:00 | 162 | 160
2018-05-19 11:30 | 155 | 153
2018-05-19 12:00 | 159 | 158
2018-05-19 12:30 | 163 | 162
2018-05-19 13:00 | 165 | 163
2018-05-19 13:30 | 160 | 158
2018-05-19 14:00 | 164 | 163
2018-05-19 14:30 | 168 | 167
2018-05-19 15:00 | 172 | 171
2018-05-19 15:30 | 177 | 175
2018-05-19 16:00 | 187 | 185
2018-05-19 16:30 | 195 | 194
2018-05-19 17:00 | 209 | 207
2018-05-19 17:30 | 223 | 222
2018-05-19 18:00 | 235 | 233
2018-05-19 18:30 | 243 | 241
2018-05-19 19:00 | 241 | 240
2018-05-19 19:30 | 232 | 230
2018-05-19 20:00 | 223 | 222
2018-05-19 20:30 | 215 | 213
2018-05-19 21:00 | 206 | 204
2018-05-19 21:30 | 197 | 195
2018-05-19 22:00 | 191 | 190
2018-05-19 22:30 | 186 | 185
2018-05-19 23:00 | 181 | 179
2018-05-19 23:30 | 185 | 183
2018-05-20 | 181 | 179
2018-05-20 00:30 | 173 | 171
2018-05-20 01:00 | 165 | 164
2018-05-20 01:30 | 161 | 159
2018-05-20 02:00 | 157 | 156
2018-05-20 02:30 | 154 | 153
2018-05-20 03:00 | 154 | 153
2018-05-20 03:30 | 153 | 152
2018-05-20 04:00 | 152 | 151
2018-05-20 04:30 | 152 | 151
2018-05-20 05:00 | 155 | 154
2018-05-20 05:30 | 155 | 155
2018-05-20 06:00 | 158 | 157
2018-05-20 06:30 | 165 | 164
2018-05-20 07:00 | 166 | 165
2018-05-20 07:30 | 172 | 171
2018-05-20 08:00 | 177 | 176
2018-05-20 08:30 | 177 | 175
2018-05-20 09:00 | 175 | 173
2018-05-20 09:30 | 172 | 170
2018-05-20 10:00 | 168 | 166
2018-05-20 10:30 | 164 | 162
2018-05-20 11:00 | 167 | 165
2018-05-20 11:30 | 153 | 151
2018-05-20 12:00 | 147 | 145
2018-05-20 12:30 | 148 | 146
2018-05-20 13:00 | 148 | 146
2018-05-20 13:30 | 149 | 148
2018-05-20 14:00 | 145 | 144
2018-05-20 14:30 | 158 | 157
2018-05-20 15:00 | 163 | 161
2018-05-20 15:30 | 165 | 163
2018-05-20 16:00 | 179 | 178
2018-05-20 16:30 | 181 | 180
2018-05-20 17:00 | 184 | 183
2018-05-20 17:30 | 203 | 202
2018-05-20 18:00 | 228 | 227
2018-05-20 18:30 | 243 | 241
2018-05-20 19:00 | 245 | 243
2018-05-20 19:30 | 235 | 234
2018-05-20 20:00 | 227 | 225
2018-05-20 20:30 | 225 | 223
2018-05-20 21:00 | 219 | 216
2018-05-20 21:30 | 218 | 217
2018-05-20 22:00 | 213 | 211
2018-05-20 22:30 | 201 | 200
2018-05-20 23:00 | 192 | 191
2018-05-20 23:30 | 182 | 180
2018-05-21 | 173 | 172
2018-05-21 00:30 | 155 | 152
2018-05-21 01:00 | 165 | 163
2018-05-21 01:30 | 162 | 160
2018-05-21 02:00 | 160 | 158
2018-05-21 02:30 | 158 | 156
2018-05-21 03:00 | 158 | 155
2018-05-21 03:30 | 157 | 155
2018-05-21 04:00 | 157 | 155
2018-05-21 04:30 | 160 | 158
2018-05-21 05:00 | 163 | 161
2018-05-21 05:30 | 171 | 169
2018-05-21 06:00 | 180 | 178
2018-05-21 06:30 | 197 | 196
2018-05-21 07:00 | 215 | 213
2018-05-21 07:30 | 229 | 228
2018-05-21 08:00 | 229 | 227
2018-05-21 08:30 | 214 | 213
2018-05-21 09:00 | 201 | 199
2018-05-21 09:30 | 190 | 188
2018-05-21 10:00 | 184 | 182
2018-05-21 10:30 | 182 | 180
2018-05-21 11:00 | 182 | 180
2018-05-21 11:30 | 176 | 174
2018-05-21 12:00 | 175 | 172
2018-05-21 12:30 | 172 | 170
2018-05-21 13:00 | 173 | 170
2018-05-21 13:30 | 175 | 173
2018-05-21 14:00 | 177 | 175
2018-05-21 14:30 | 173 | 171
2018-05-21 15:00 | 178 | 176
2018-05-21 15:30 | 183 | 181
2018-05-21 16:00 | 197 | 195
2018-05-21 16:30 | 204 | 202
2018-05-21 17:00 | 210 | 208
2018-05-21 17:30 | 196 | 193
2018-05-21 18:00 | 201 | 200
2018-05-21 18:30 | 197 | 194
2018-05-21 19:00 | 213 | 211
2018-05-21 19:30 | 246 | 245
2018-05-21 20:00 | 242 | 240
2018-05-21 20:30 | 240 | 238
2018-05-21 21:00 | 232 | 230
2018-05-21 21:30 | 222 | 219
2018-05-21 22:00 | 209 | 207
2018-05-21 22:30 | 207 | 205
2018-05-21 23:00 | 200 | 198
2018-05-21 23:30 | 188 | 187
2018-05-22 | 180 | 178
2018-05-22 00:30 | 173 | 172
2018-05-22 01:00 | 168 | 167
2018-05-22 01:30 | 165 | 164
2018-05-22 02:00 | 161 | 160
2018-05-22 02:30 | 158 | 156
2018-05-22 03:00 | 157 | 155
2018-05-22 03:30 | 158 | 156
2018-05-22 04:00 | 158 | 156
2018-05-22 04:30 | 160 | 158
2018-05-22 05:00 | 164 | 162
2018-05-22 05:30 | 172 | 170
2018-05-22 06:00 | 181 | 179
2018-05-22 06:30 | 201 | 200
2018-05-22 07:00 | 204 | 202
2018-05-22 07:30 | 230 | 228
2018-05-22 08:00 | 228 | 227
2018-05-22 08:30 | 212 | 211
2018-05-22 09:00 | 199 | 197
2018-05-22 09:30 | 188 | 187
2018-05-22 10:00 | 178 | 177
2018-05-22 10:30 | 126 | 111
2018-05-22 11:00 | 154 | 148
2018-05-22 11:30 | 129 | 125
2018-05-22 12:00 | 161 | 157
2018-05-22 12:30 | 160 | 156
2018-05-22 13:00 | 163 | 159
2018-05-22 13:30 | 145 | 141
2018-05-22 14:00 | 150 | 147
2018-05-22 14:30 | 151 | 148
2018-05-22 15:00 | 157 | 154
2018-05-22 15:30 | 166 | 163
2018-05-22 16:00 | 177 | 174
2018-05-22 16:30 | 190 | 188
2018-05-22 17:00 | 207 | 204
2018-05-22 17:30 | 228 | 225
2018-05-22 18:00 | 238 | 235
2018-05-22 18:30 | 254 | 251
2018-05-22 19:00 | 256 | 254
2018-05-22 19:30 | 248 | 245
2018-05-22 20:00 | 237 | 234
2018-05-22 20:30 | 235 | 232
2018-05-22 21:00 | 239 | 236
2018-05-22 21:30 | 232 | 229
2018-05-22 22:00 | 217 | 215
2018-05-22 22:30 | 202 | 201
2018-05-22 23:00 | 190 | 189
2018-05-22 23:30 | 182 | 182
2018-05-23 | 174 | 174
2018-05-23 00:30 | 168 | 167
2018-05-23 01:00 | 164 | 164
2018-05-23 01:30 | 161 | 160
2018-05-23 02:00 | 157 | 156
2018-05-23 02:30 | 156 | 155
2018-05-23 03:00 | 155 | 154
2018-05-23 03:30 | 155 | 154
2018-05-23 04:00 | 155 | 155
2018-05-23 04:30 | 157 | 157
2018-05-23 05:00 | 161 | 160
2018-05-23 05:30 | 169 | 169
2018-05-23 06:00 | 179 | 178
2018-05-23 06:30 | 199 | 198
2018-05-23 07:00 | 187 | 185
2018-05-23 07:30 | 225 | 224
2018-05-23 08:00 | 215 | 214
2018-05-23 08:30 | 194 | 193
2018-05-23 09:00 | 179 | 178
2018-05-23 09:30 | 171 | 169
2018-05-23 10:00 | 159 | 158
2018-05-23 10:30 | 156 | 155
2018-05-23 11:00 | 154 | 152
2018-05-23 11:30 | 151 | 149
2018-05-23 12:00 | 150 | 148
2018-05-23 12:30 | 150 | 147
2018-05-23 13:00 | 149 | 147
2018-05-23 13:30 | 153 | 151
2018-05-23 14:00 | 155 | 153
2018-05-23 14:30 | 149 | 147
2018-05-23 15:00 | 150 | 148
2018-05-23 15:30 | 162 | 160
2018-05-23 16:00 | 176 | 173
2018-05-23 16:30 | 192 | 190
2018-05-23 17:00 | 209 | 207
2018-05-23 17:30 | 227 | 225
2018-05-23 18:00 | 246 | 244
2018-05-23 18:30 | 262 | 260
2018-05-23 19:00 | 265 | 263
2018-05-23 19:30 | 256 | 254
2018-05-23 20:00 | 247 | 245
2018-05-23 20:30 | 237 | 235
2018-05-23 21:00 | 226 | 224
2018-05-23 21:30 | 215 | 213
2018-05-23 22:00 | 203 | 201
2018-05-23 22:30 | 202 | 200
2018-05-23 23:00 | 194 | 193
2018-05-23 23:30 | 185 | 184
2018-05-24 | 176 | 175
2018-05-24 00:30 | 170 | 170
2018-05-24 01:00 | 165 | 164
2018-05-24 01:30 | 160 | 160
2018-05-24 02:00 | 158 | 157
2018-05-24 02:30 | 154 | 153
2018-05-24 03:00 | 141 | 140
2018-05-24 03:30 | 154 | 153
2018-05-24 04:00 | 154 | 154
2018-05-24 04:30 | 157 | 157
2018-05-24 05:00 | 162 | 162
2018-05-24 05:30 | 169 | 168
2018-05-24 06:00 | 180 | 179
2018-05-24 06:30 | 199 | 198
2018-05-24 07:00 | 200 | 198
2018-05-24 07:30 | 229 | 227
2018-05-24 08:00 | 228 | 227
2018-05-24 08:30 | 215 | 213
2018-05-24 09:00 | 201 | 200
2018-05-24 09:30 | 200 | 199
2018-05-24 10:00 | 185 | 184
2018-05-24 10:30 | 184 | 183
2018-05-24 11:00 | 180 | 178
2018-05-24 11:30 | 180 | 179
2018-05-24 12:00 | 178 | 177
2018-05-24 12:30 | 188 | 186
2018-05-24 13:00 | 184 | 183
2018-05-24 13:30 | 178 | 176
2018-05-24 14:00 | 173 | 172
2018-05-24 14:30 | 183 | 181
2018-05-24 15:00 | 191 | 190
2018-05-24 15:30 | 198 | 196
2018-05-24 16:00 | 211 | 209
2018-05-24 16:30 | 218 | 216
2018-05-24 17:00 | 227 | 226
2018-05-24 17:30 | 236 | 234
2018-05-24 18:00 | 251 | 249
2018-05-24 18:30 | 264 | 263
2018-05-24 19:00 | 270 | 268
2018-05-24 19:30 | 262 | 260
2018-05-24 20:00 | 252 | 251
2018-05-24 20:30 | 241 | 239
2018-05-24 21:00 | 229 | 227
2018-05-24 21:30 | 217 | 215
2018-05-24 22:00 | 203 | 201
2018-05-24 22:30 | 191 | 189
2018-05-24 23:00 | 180 | 178
2018-05-24 23:30 | 171 | 169
2018-05-25 | 164 | 161
2018-05-25 00:30 | 169 | 166
2018-05-25 01:00 | 168 | 166
2018-05-25 01:30 | 164 | 161
2018-05-25 02:00 | 161 | 158
2018-05-25 02:30 | 159 | 156
2018-05-25 03:00 | 160 | 158
2018-05-25 03:30 | 158 | 156
2018-05-25 04:00 | 156 | 155
2018-05-25 04:30 | 158 | 156
2018-05-25 05:00 | 161 | 159
2018-05-25 05:30 | 168 | 167
2018-05-25 06:00 | 178 | 177
2018-05-25 06:30 | 197 | 196
2018-05-25 07:00 | 215 | 214
2018-05-25 07:30 | 233 | 232
2018-05-25 08:00 | 232 | 231
2018-05-25 08:30 | 228 | 227
2018-05-25 09:00 | 220 | 218
2018-05-25 09:30 | 217 | 215
2018-05-25 10:00 | 198 | 196
2018-05-25 10:30 | 191 | 190
2018-05-25 11:00 | 180 | 179
2018-05-25 11:30 | 181 | 180
2018-05-25 12:00 | 189 | 187
2018-05-25 12:30 | 185 | 183
2018-05-25 13:00 | 189 | 187
2018-05-25 13:30 | 195 | 193
2018-05-25 14:00 | 192 | 191
2018-05-25 14:30 | 192 | 190
2018-05-25 15:00 | 184 | 182
2018-05-25 15:30 | 185 | 183
2018-05-25 16:00 | 194 | 193
2018-05-25 16:30 | 200 | 198
2018-05-25 17:00 | 212 | 210
2018-05-25 17:30 | 222 | 220
2018-05-25 18:00 | 223 | 221
2018-05-25 18:30 | 244 | 242
2018-05-25 19:00 | 244 | 242
2018-05-25 19:30 | 235 | 233
2018-05-25 20:00 | 224 | 223
2018-05-25 20:30 | 224 | 222
2018-05-25 21:00 | 219 | 217
2018-05-25 21:30 | 212 | 210
2018-05-25 22:00 | 204 | 202
2018-05-25 22:30 | 206 | 204
2018-05-25 23:00 | 200 | 198
2018-05-25 23:30 | 191 | 189
2018-05-26 | 183 | 182
2018-05-26 00:30 | 177 | 176
2018-05-26 01:00 | 171 | 170
2018-05-26 01:30 | 168 | 166
2018-05-26 02:00 | 163 | 162
2018-05-26 02:30 | 160 | 158
2018-05-26 03:00 | 158 | 156
2018-05-26 03:30 | 156 | 155
2018-05-26 04:00 | 156 | 154
2018-05-26 04:30 | 156 | 154
2018-05-26 05:00 | 157 | 156
2018-05-26 05:30 | 160 | 158
2018-05-26 06:00 | 164 | 162
2018-05-26 06:30 | 170 | 169
2018-05-26 07:00 | 178 | 176
2018-05-26 07:30 | 188 | 186
2018-05-26 08:00 | 192 | 191
2018-05-26 08:30 | 195 | 193
2018-05-26 09:00 | 193 | 191
2018-05-26 09:30 | 184 | 183
2018-05-26 10:00 | 209 | 208
2018-05-26 10:30 | 203 | 202
2018-05-26 11:00 | 161 | 159
2018-05-26 11:30 | 158 | 156
2018-05-26 12:00 | 156 | 155
2018-05-26 12:30 | 156 | 155
2018-05-26 13:00 | 165 | 164
2018-05-26 13:30 | 159 | 158
2018-05-26 14:00 | 144 | 143
2018-05-26 14:30 | 139 | 138
2018-05-26 15:00 | 143 | 141
2018-05-26 15:30 | 153 | 152
2018-05-26 16:00 | 161 | 160
2018-05-26 16:30 | 179 | 178
2018-05-26 17:00 | 196 | 195
2018-05-26 17:30 | 213 | 212
2018-05-26 18:00 | 228 | 227
2018-05-26 18:30 | 240 | 239
2018-05-26 19:00 | 240 | 239
2018-05-26 19:30 | 243 | 242
2018-05-26 20:00 | 240 | 239
2018-05-26 20:30 | 230 | 229
2018-05-26 21:00 | 222 | 220
2018-05-26 21:30 | 215 | 214
2018-05-26 22:00 | 206 | 205
2018-05-26 22:30 | 199 | 197
2018-05-26 23:00 | 190 | 189
2018-05-26 23:30 | 182 | 180
2018-05-27 | 176 | 174
2018-05-27 00:30 | 171 | 169
2018-05-27 01:00 | 165 | 163
2018-05-27 01:30 | 161 | 159
2018-05-27 02:00 | 157 | 155
2018-05-27 02:30 | 157 | 155
2018-05-27 03:00 | 154 | 152
2018-05-27 03:30 | 153 | 151
2018-05-27 04:00 | 139 | 137
2018-05-27 04:30 | 149 | 147
2018-05-27 05:00 | 153 | 151
2018-05-27 05:30 | 154 | 152
2018-05-27 06:00 | 156 | 155
2018-05-27 06:30 | 161 | 159
2018-05-27 07:00 | 165 | 164
2018-05-27 07:30 | 170 | 168
2018-05-27 08:00 | 153 | 151
2018-05-27 08:30 | 143 | 141
2018-05-27 09:00 | 147 | 146
2018-05-27 09:30 | 149 | 148
2018-05-27 10:00 | 145 | 143
2018-05-27 10:30 | 146 | 145
2018-05-27 11:00 | 142 | 141
2018-05-27 11:30 | 146 | 145
2018-05-27 12:00 | 145 | 144
2018-05-27 12:30 | 142 | 140
2018-05-27 13:00 | 137 | 136
2018-05-27 13:30 | 139 | 138
2018-05-27 14:00 | 143 | 142
2018-05-27 14:30 | 140 | 138
2018-05-27 15:00 | 142 | 140
2018-05-27 15:30 | 153 | 152
2018-05-27 16:00 | 174 | 173
2018-05-27 16:30 | 181 | 180
2018-05-27 17:00 | 207 | 206
2018-05-27 17:30 | 235 | 234
2018-05-27 18:00 | 256 | 255
2018-05-27 18:30 | 270 | 268
2018-05-27 19:00 | 260 | 258
2018-05-27 19:30 | 249 | 248
2018-05-27 20:00 | 239 | 237
2018-05-27 20:30 | 229 | 228
2018-05-27 21:00 | 219 | 217
2018-05-27 21:30 | 209 | 207
2018-05-27 22:00 | 199 | 197
2018-05-27 22:30 | 198 | 196
2018-05-27 23:00 | 191 | 189
2018-05-27 23:30 | 184 | 182
2018-05-28 | 176 | 174
2018-05-28 00:30 | 171 | 170
2018-05-28 01:00 | 167 | 165
2018-05-28 01:30 | 163 | 162
2018-05-28 02:00 | 161 | 159
2018-05-28 02:30 | 159 | 157
2018-05-28 03:00 | 157 | 155
2018-05-28 03:30 | 156 | 155
2018-05-28 04:00 | 156 | 155
2018-05-28 04:30 | 156 | 155
2018-05-28 05:00 | 160 | 158
2018-05-28 05:30 | 168 | 166
2018-05-28 06:00 | 177 | 176
2018-05-28 06:30 | 199 | 198
2018-05-28 07:00 | 217 | 216
2018-05-28 07:30 | 235 | 233
2018-05-28 08:00 | 238 | 235
2018-05-28 08:30 | 223 | 221
2018-05-28 09:00 | 220 | 217
2018-05-28 09:30 | 211 | 208
2018-05-28 10:00 | 205 | 203
2018-05-28 10:30 | 197 | 195
2018-05-28 11:00 | 175 | 173
2018-05-28 11:30 | 147 | 144
2018-05-28 12:00 | 151 | 148
2018-05-28 12:30 | 155 | 152
2018-05-28 13:00 | 155 | 152
2018-05-28 13:30 | 143 | 140
2018-05-28 14:00 | 123 | 119
2018-05-28 14:30 | 107 | 103
2018-05-28 15:00 | 77 | 72
2018-05-28 15:30 | 84 | 80
2018-05-28 16:00 | 94 | 90
2018-05-28 16:30 | 100 | 97
2018-05-28 17:00 | 103 | 99
2018-05-28 17:30 | 100 | 95
2018-05-28 18:00 | 122 | 118
2018-05-28 18:30 | 136 | 132
2018-05-28 19:00 | 140 | 137
2018-05-28 19:30 | 130 | 127
2018-05-28 20:00 | 121 | 117
2018-05-28 20:30 | 110 | 105
2018-05-28 21:00 | 111 | 106
2018-05-28 21:30 | 118 | 114
2018-05-28 22:00 | 109 | 105
2018-05-28 22:30 | 96 | 93
2018-05-28 23:00 | 119 | 116
2018-05-28 23:30 | 144 | 141
2018-05-29 | 178 | 175
2018-05-29 00:30 | 173 | 171
2018-05-29 01:00 | 169 | 166
2018-05-29 01:30 | 166 | 163
2018-05-29 02:00 | 164 | 161
2018-05-29 02:30 | 160 | 157
2018-05-29 03:00 | 159 | 156
2018-05-29 03:30 | 159 | 156
2018-05-29 04:00 | 159 | 155
2018-05-29 04:30 | 161 | 157
2018-05-29 05:00 | 165 | 162
2018-05-29 05:30 | 174 | 171
2018-05-29 06:00 | 181 | 178
2018-05-29 06:30 | 184 | 181
2018-05-29 07:00 | 184 | 181
2018-05-29 07:30 | 201 | 199
2018-05-29 08:00 | 213 | 210
2018-05-29 08:30 | 217 | 215
2018-05-29 09:00 | 206 | 203
2018-05-29 09:30 | 201 | 198
2018-05-29 10:00 | 200 | 197
2018-05-29 10:30 | 202 | 199
2018-05-29 11:00 | 197 | 195
2018-05-29 11:30 | 196 | 193
2018-05-29 12:00 | 192 | 189
2018-05-29 12:30 | 192 | 190
2018-05-29 13:00 | 197 | 195
2018-05-29 13:30 | 196 | 193
2018-05-29 14:00 | 188 | 185
2018-05-29 14:30 | 180 | 177
2018-05-29 15:00 | 173 | 170
2018-05-29 15:30 | 178 | 175
2018-05-29 16:00 | 191 | 189
2018-05-29 16:30 | 207 | 204
2018-05-29 17:00 | 222 | 219
2018-05-29 17:30 | 242 | 239
2018-05-29 18:00 | 224 | 221
2018-05-29 18:30 | 247 | 244
2018-05-29 19:00 | 254 | 251
2018-05-29 19:30 | 268 | 266
2018-05-29 20:00 | 269 | 267
2018-05-29 20:30 | 258 | 255
2018-05-29 21:00 | 248 | 246
2018-05-29 21:30 | 238 | 235
2018-05-29 22:00 | 227 | 224
2018-05-29 22:30 | 214 | 211
2018-05-29 23:00 | 202 | 199
2018-05-29 23:30 | 190 | 187
2018-05-30 | 181 | 178
2018-05-30 00:30 | 174 | 171
2018-05-30 01:00 | 168 | 165
2018-05-30 01:30 | 164 | 160
2018-05-30 02:00 | 162 | 158
2018-05-30 02:30 | 161 | 157
2018-05-30 03:00 | 160 | 156
2018-05-30 03:30 | 151 | 147
2018-05-30 04:00 | 153 | 150
2018-05-30 04:30 | 158 | 155
2018-05-30 05:00 | 159 | 157
2018-05-30 05:30 | 165 | 163
2018-05-30 06:00 | 178 | 176
2018-05-30 06:30 | 199 | 197
2018-05-30 07:00 | 214 | 212
2018-05-30 07:30 | 230 | 227
2018-05-30 08:00 | 222 | 220
2018-05-30 08:30 | 203 | 201
2018-05-30 09:00 | 188 | 185
2018-05-30 09:30 | 177 | 175
2018-05-30 10:00 | 165 | 163
2018-05-30 10:30 | 158 | 156
2018-05-30 11:00 | 151 | 149
2018-05-30 11:30 | 150 | 147
2018-05-30 12:00 | 140 | 138
2018-05-30 12:30 | 127 | 124
2018-05-30 13:00 | 128 | 125
2018-05-30 13:30 | 130 | 127
2018-05-30 14:00 | 125 | 122
2018-05-30 14:30 | 128 | 125
2018-05-30 15:00 | 156 | 153
2018-05-30 15:30 | 155 | 153
2018-05-30 16:00 | 171 | 169
2018-05-30 16:30 | 188 | 186
2018-05-30 17:00 | 211 | 209
2018-05-30 17:30 | 229 | 227
2018-05-30 18:00 | 250 | 247
2018-05-30 18:30 | 265 | 263
2018-05-30 19:00 | 269 | 267
2018-05-30 19:30 | 264 | 261
2018-05-30 20:00 | 251 | 249
2018-05-30 20:30 | 239 | 236
2018-05-30 21:00 | 229 | 226
2018-05-30 21:30 | 220 | 217
2018-05-30 22:00 | 208 | 206
2018-05-30 22:30 | 205 | 203
2018-05-30 23:00 | 196 | 193
2018-05-30 23:30 | 187 | 185
2018-05-31 | 179 | 176
2018-05-31 00:30 | 172 | 169
2018-05-31 01:00 | 167 | 163
2018-05-31 01:30 | 162 | 159
2018-05-31 02:00 | 158 | 155
2018-05-31 02:30 | 155 | 152
2018-05-31 03:00 | 155 | 152
2018-05-31 03:30 | 155 | 152
2018-05-31 04:00 | 155 | 152
2018-05-31 04:30 | 158 | 154
2018-05-31 05:00 | 160 | 157
2018-05-31 05:30 | 168 | 164
2018-05-31 06:00 | 179 | 176
2018-05-31 06:30 | 200 | 197
2018-05-31 07:00 | 211 | 209
2018-05-31 07:30 | 210 | 207
2018-05-31 08:00 | 199 | 196
2018-05-31 08:30 | 191 | 188
2018-05-31 09:00 | 180 | 176
2018-05-31 09:30 | 170 | 167
2018-05-31 10:00 | 158 | 155
2018-05-31 10:30 | 153 | 150
2018-05-31 11:00 | 146 | 143
2018-05-31 11:30 | 144 | 141
2018-05-31 12:00 | 144 | 141
2018-05-31 12:30 | 143 | 140
2018-05-31 13:00 | 141 | 138
2018-05-31 13:30 | 146 | 143
2018-05-31 14:00 | 150 | 147
2018-05-31 14:30 | 128 | 125
2018-05-31 15:00 | 112 | 108
2018-05-31 15:30 | 125 | 121
2018-05-31 16:00 | 133 | 130
2018-05-31 16:30 | 142 | 139
2018-05-31 17:00 | 152 | 149
2018-05-31 17:30 | 146 | 142
2018-05-31 18:00 | 121 | 117
2018-05-31 18:30 | 133 | 130
2018-05-31 19:00 | 138 | 135
2018-05-31 19:30 | 131 | 128
2018-05-31 20:00 | 130 | 127
2018-05-31 20:30 | 132 | 128
2018-05-31 21:00 | 135 | 132
2018-05-31 21:30 | 159 | 156
2018-05-31 22:00 | 156 | 152
2018-05-31 22:30 | 143 | 139
2018-05-31 23:00 | 132 | 129
2018-05-31 23:30 | 122 | 118
2018-06-01 | 114 | 110
2018-06-01 00:30 | 109 | 105
2018-06-01 01:00 | 103 | 99
2018-06-01 01:30 | 120 | 117
2018-06-01 02:00 | 158 | 155
2018-06-01 02:30 | 159 | 156
2018-06-01 03:00 | 158 | 155
2018-06-01 03:30 | 156 | 153
2018-06-01 04:00 | 157 | 155
2018-06-01 04:30 | 160 | 158
2018-06-01 05:00 | 162 | 159
2018-06-01 05:30 | 155 | 152
2018-06-01 06:00 | 162 | 160
2018-06-01 06:30 | 176 | 173
2018-06-01 07:00 | 180 | 178
2018-06-01 07:30 | 191 | 189
2018-06-01 08:00 | 193 | 191
2018-06-01 08:30 | 192 | 189
2018-06-01 09:00 | 177 | 174
2018-06-01 09:30 | 163 | 160
2018-06-01 10:00 | 149 | 147
2018-06-01 10:30 | 140 | 137
2018-06-01 11:00 | 133 | 130
2018-06-01 11:30 | 129 | 126
2018-06-01 12:00 | 127 | 124
2018-06-01 12:30 | 125 | 122
2018-06-01 13:00 | 122 | 119
2018-06-01 13:30 | 121 | 118
2018-06-01 14:00 | 118 | 115
2018-06-01 14:30 | 121 | 118
2018-06-01 15:00 | 127 | 123
2018-06-01 15:30 | 135 | 131
2018-06-01 16:00 | 146 | 143
2018-06-01 16:30 | 165 | 163
2018-06-01 17:00 | 190 | 187
2018-06-01 17:30 | 206 | 203
2018-06-01 18:00 | 211 | 208
2018-06-01 18:30 | 227 | 224
2018-06-01 19:00 | 230 | 228
2018-06-01 19:30 | 223 | 221
2018-06-01 20:00 | 214 | 212
2018-06-01 20:30 | 205 | 202
2018-06-01 21:00 | 198 | 196
2018-06-01 21:30 | 189 | 187
2018-06-01 22:00 | 180 | 177
2018-06-01 22:30 | 167 | 165
2018-06-01 23:00 | 170 | 168
2018-06-01 23:30 | 178 | 176
2018-06-02 | 174 | 171
2018-06-02 00:30 | 167 | 165
2018-06-02 01:00 | 160 | 157
2018-06-02 01:30 | 157 | 154
2018-06-02 02:00 | 154 | 151
2018-06-02 02:30 | 152 | 149
2018-06-02 03:00 | 150 | 147
2018-06-02 03:30 | 150 | 147
2018-06-02 04:00 | 149 | 146
2018-06-02 04:30 | 150 | 146
2018-06-02 05:00 | 152 | 149
2018-06-02 05:30 | 157 | 154
2018-06-02 06:00 | 161 | 158
2018-06-02 06:30 | 167 | 164
2018-06-02 07:00 | 170 | 167
2018-06-02 07:30 | 163 | 160
2018-06-02 08:00 | 152 | 149
2018-06-02 08:30 | 129 | 126
2018-06-02 09:00 | 131 | 128
2018-06-02 09:30 | 122 | 119
2018-06-02 10:00 | 115 | 112
2018-06-02 10:30 | 109 | 106
2018-06-02 11:00 | 105 | 101
2018-06-02 11:30 | 100 | 97
2018-06-02 12:00 | 97 | 94
2018-06-02 12:30 | 94 | 90
2018-06-02 13:00 | 93 | 90
2018-06-02 13:30 | 94 | 92
2018-06-02 14:00 | 96 | 93
2018-06-02 14:30 | 99 | 97
2018-06-02 15:00 | 107 | 105
2018-06-02 15:30 | 116 | 113
2018-06-02 16:00 | 130 | 127
2018-06-02 16:30 | 147 | 145
2018-06-02 17:00 | 176 | 174
2018-06-02 17:30 | 202 | 199
2018-06-02 18:00 | 209 | 207
2018-06-02 18:30 | 225 | 222
2018-06-02 19:00 | 224 | 222
2018-06-02 19:30 | 216 | 213
2018-06-02 20:00 | 205 | 202
2018-06-02 20:30 | 197 | 194
2018-06-02 21:00 | 189 | 186
2018-06-02 21:30 | 182 | 179
2018-06-02 22:00 | 176 | 173
2018-06-02 22:30 | 191 | 188
2018-06-02 23:00 | 189 | 186
2018-06-02 23:30 | 182 | 179
2018-06-03 | 174 | 170
2018-06-03 00:30 | 167 | 164
2018-06-03 01:00 | 162 | 159
2018-06-03 01:30 | 159 | 155
2018-06-03 02:00 | 158 | 155
2018-06-03 02:30 | 155 | 152
2018-06-03 03:00 | 153 | 150
2018-06-03 03:30 | 152 | 148
2018-06-03 04:00 | 152 | 148
2018-06-03 04:30 | 152 | 148
2018-06-03 05:00 | 154 | 150
2018-06-03 05:30 | 156 | 153
2018-06-03 06:00 | 158 | 155
2018-06-03 06:30 | 163 | 160
2018-06-03 07:00 | 163 | 160
2018-06-03 07:30 | 153 | 149
2018-06-03 08:00 | 139 | 136
2018-06-03 08:30 | 126 | 123
2018-06-03 09:00 | 119 | 115
2018-06-03 09:30 | 112 | 108
2018-06-03 10:00 | 107 | 103
2018-06-03 10:30 | 103 | 99
2018-06-03 11:00 | 98 | 94
2018-06-03 11:30 | 92 | 88
2018-06-03 12:00 | 92 | 88
2018-06-03 12:30 | 91 | 87
2018-06-03 13:00 | 89 | 85
2018-06-03 13:30 | 89 | 85
2018-06-03 14:00 | 84 | 79
2018-06-03 14:30 | 79 | 75
2018-06-03 15:00 | 82 | 78
2018-06-03 15:30 | 93 | 89
2018-06-03 16:00 | 107 | 104
2018-06-03 16:30 | 130 | 127
2018-06-03 17:00 | 157 | 154
2018-06-03 17:30 | 191 | 188
2018-06-03 18:00 | 215 | 213
2018-06-03 18:30 | 234 | 231
2018-06-03 19:00 | 238 | 236
2018-06-03 19:30 | 230 | 227
2018-06-03 20:00 | 219 | 216
2018-06-03 20:30 | 202 | 198
2018-06-03 21:00 | 189 | 185
2018-06-03 21:30 | 187 | 184
2018-06-03 22:00 | 178 | 175
2018-06-03 22:30 | 191 | 188
2018-06-03 23:00 | 185 | 182
2018-06-03 23:30 | 177 | 173
2018-06-04 | 170 | 167
2018-06-04 00:30 | 165 | 161
2018-06-04 01:00 | 160 | 157
2018-06-04 01:30 | 157 | 153
2018-06-04 02:00 | 156 | 152
2018-06-04 02:30 | 153 | 150
2018-06-04 03:00 | 152 | 149
2018-06-04 03:30 | 151 | 148
2018-06-04 04:00 | 152 | 148
2018-06-04 04:30 | 155 | 151
2018-06-04 05:00 | 160 | 157
2018-06-04 05:30 | 156 | 153
2018-06-04 06:00 | 142 | 139
2018-06-04 06:30 | 157 | 154
2018-06-04 07:00 | 171 | 168
2018-06-04 07:30 | 171 | 168
2018-06-04 08:00 | 159 | 156
2018-06-04 08:30 | 131 | 125
2018-06-04 09:00 | 89 | 80
2018-06-04 09:30 | 27 | 18
2018-06-04 10:00 | 19 | 9
2018-06-04 10:30 | 18 | 7
2018-06-04 11:00 | 17 | 3
2018-06-04 11:30 | 17 | 2
2018-06-04 12:00 | 19 | 2
2018-06-04 12:30 | 20 | 2
2018-06-04 13:00 | 18 | 2
2018-06-04 13:30 | 18 | 2
2018-06-04 14:00 | 19 | 8
2018-06-04 14:30 | 44 | 35
2018-06-04 15:00 | 49 | 42
2018-06-04 15:30 | 56 | 51
2018-06-04 16:00 | 72 | 65
2018-06-04 16:30 | 86 | 81
2018-06-04 17:00 | 111 | 106
2018-06-04 17:30 | 100 | 95
2018-06-04 18:00 | 96 | 90
2018-06-04 18:30 | 124 | 120
2018-06-04 19:00 | 141 | 136
2018-06-04 19:30 | 132 | 128
2018-06-04 20:00 | 121 | 117
2018-06-04 20:30 | 109 | 104
2018-06-04 21:00 | 132 | 128
2018-06-04 21:30 | 132 | 128
2018-06-04 22:00 | 122 | 117
2018-06-04 22:30 | 130 | 125
2018-06-04 23:00 | 149 | 144
2018-06-04 23:30 | 183 | 179
2018-06-05 | 178 | 173
2018-06-05 00:30 | 171 | 165
2018-06-05 01:00 | 165 | 160
2018-06-05 01:30 | 163 | 158
2018-06-05 02:00 | 161 | 157
2018-06-05 02:30 | 159 | 155
2018-06-05 03:00 | 158 | 153
2018-06-05 03:30 | 158 | 154
2018-06-05 04:00 | 158 | 154
2018-06-05 04:30 | 158 | 154
2018-06-05 05:00 | 161 | 157
2018-06-05 05:30 | 170 | 166
2018-06-05 06:00 | 182 | 178
2018-06-05 06:30 | 200 | 196
2018-06-05 07:00 | 211 | 207
2018-06-05 07:30 | 207 | 203
2018-06-05 08:00 | 192 | 188
2018-06-05 08:30 | 172 | 168
2018-06-05 09:00 | 150 | 145
2018-06-05 09:30 | 133 | 128
2018-06-05 10:00 | 124 | 119
2018-06-05 10:30 | 119 | 114
2018-06-05 11:00 | 113 | 110
2018-06-05 11:30 | 112 | 109
2018-06-05 12:00 | 110 | 107
2018-06-05 12:30 | 108 | 106
2018-06-05 13:00 | 106 | 105
2018-06-05 13:30 | 107 | 106
2018-06-05 14:00 | 107 | 106
2018-06-05 14:30 | 86 | 85
2018-06-05 15:00 | 74 | 72
2018-06-05 15:30 | 74 | 73
2018-06-05 16:00 | 87 | 86
2018-06-05 16:30 | 89 | 88
2018-06-05 17:00 | 66 | 64
2018-06-05 17:30 | 46 | 43
2018-06-05 18:00 | 90 | 88
2018-06-05 18:30 | 107 | 105
2018-06-05 19:00 | 97 | 95
2018-06-05 19:30 | 94 | 92
2018-06-05 20:00 | 84 | 82
2018-06-05 20:30 | 132 | 131
2018-06-05 21:00 | 139 | 138
2018-06-05 21:30 | 131 | 130
2018-06-05 22:00 | 118 | 117
2018-06-05 22:30 | 119 | 118
2018-06-05 23:00 | 122 | 120
2018-06-05 23:30 | 115 | 114
2018-06-06 | 106 | 105
2018-06-06 00:30 | 100 | 98
2018-06-06 01:00 | 95 | 93
2018-06-06 01:30 | 91 | 89
2018-06-06 02:00 | 89 | 87
2018-06-06 02:30 | 87 | 85
2018-06-06 03:00 | 85 | 83
2018-06-06 03:30 | 83 | 82
2018-06-06 04:00 | 85 | 83
2018-06-06 04:30 | 86 | 84
2018-06-06 05:00 | 92 | 91
2018-06-06 05:30 | 100 | 98
2018-06-06 06:00 | 109 | 108
2018-06-06 06:30 | 89 | 88
2018-06-06 07:00 | 85 | 84
2018-06-06 07:30 | 96 | 94
2018-06-06 08:00 | 58 | 56
2018-06-06 08:30 | 46 | 43
2018-06-06 09:00 | 42 | 37
2018-06-06 09:30 | 25 | 19
2018-06-06 10:00 | 8 | 8
2018-06-06 10:30 | 45 | 40
2018-06-06 11:00 | 56 | 51
2018-06-06 11:30 | 57 | 52
2018-06-06 12:00 | 57 | 52
2018-06-06 12:30 | 57 | 51
2018-06-06 13:00 | 54 | 48
2018-06-06 13:30 | 55 | 50
2018-06-06 14:00 | 50 | 45
2018-06-06 14:30 | 52 | 45
2018-06-06 15:00 | 7 | 6
2018-06-06 15:30 | 6 | 5
2018-06-06 16:00 | 23 | 18
2018-06-06 16:30 | 42 | 37
2018-06-06 17:00 | 67 | 64
2018-06-06 17:30 | 87 | 86
2018-06-06 18:00 | 109 | 108
2018-06-06 18:30 | 127 | 126
2018-06-06 19:00 | 130 | 129
2018-06-06 19:30 | 124 | 123
2018-06-06 20:00 | 113 | 112
2018-06-06 20:30 | 100 | 99
2018-06-06 21:00 | 86 | 85
2018-06-06 21:30 | 79 | 78
2018-06-06 22:00 | 92 | 91
2018-06-06 22:30 | 110 | 108
2018-06-06 23:00 | 148 | 147
2018-06-06 23:30 | 183 | 182
2018-06-07 | 178 | 177
2018-06-07 00:30 | 171 | 170
2018-06-07 01:00 | 163 | 162
2018-06-07 01:30 | 160 | 159
2018-06-07 02:00 | 157 | 155
2018-06-07 02:30 | 156 | 155
2018-06-07 03:00 | 153 | 152
2018-06-07 03:30 | 153 | 152
2018-06-07 04:00 | 154 | 153
2018-06-07 04:30 | 157 | 155
2018-06-07 05:00 | 160 | 159
2018-06-07 05:30 | 168 | 167
2018-06-07 06:00 | 176 | 175
2018-06-07 06:30 | 195 | 194
2018-06-07 07:00 | 208 | 207
2018-06-07 07:30 | 209 | 208
2018-06-07 08:00 | 199 | 198
2018-06-07 08:30 | 175 | 174
2018-06-07 09:00 | 157 | 157
2018-06-07 09:30 | 147 | 146
2018-06-07 10:00 | 135 | 133
2018-06-07 10:30 | 125 | 123
2018-06-07 11:00 | 128 | 127
2018-06-07 11:30 | 124 | 123
2018-06-07 12:00 | 123 | 121
2018-06-07 12:30 | 120 | 119
2018-06-07 13:00 | 120 | 118
2018-06-07 13:30 | 124 | 122
2018-06-07 14:00 | 117 | 115
2018-06-07 14:30 | 108 | 106
2018-06-07 15:00 | 115 | 113
2018-06-07 15:30 | 120 | 119
2018-06-07 16:00 | 135 | 133
2018-06-07 16:30 | 150 | 148
2018-06-07 17:00 | 166 | 165
2018-06-07 17:30 | 124 | 121
2018-06-07 18:00 | 98 | 95
2018-06-07 18:30 | 115 | 113
2018-06-07 19:00 | 117 | 115
2018-06-07 19:30 | 116 | 114
2018-06-07 20:00 | 118 | 116
2018-06-07 20:30 | 126 | 124
2018-06-07 21:00 | 124 | 123
2018-06-07 21:30 | 114 | 112
2018-06-07 22:00 | 101 | 98
2018-06-07 22:30 | 133 | 131
2018-06-07 23:00 | 177 | 175
2018-06-07 23:30 | 176 | 173
2018-06-08 | 167 | 164
2018-06-08 00:30 | 162 | 160
2018-06-08 01:00 | 158 | 155
2018-06-08 01:30 | 154 | 152
2018-06-08 02:00 | 152 | 150
2018-06-08 02:30 | 149 | 147
2018-06-08 03:00 | 146 | 144
2018-06-08 03:30 | 147 | 145
2018-06-08 04:00 | 147 | 145
2018-06-08 04:30 | 149 | 147
2018-06-08 05:00 | 154 | 152
2018-06-08 05:30 | 161 | 159
2018-06-08 06:00 | 170 | 168
2018-06-08 06:30 | 185 | 183
2018-06-08 07:00 | 201 | 199
2018-06-08 07:30 | 202 | 200
2018-06-08 08:00 | 193 | 192
2018-06-08 08:30 | 173 | 172
2018-06-08 09:00 | 157 | 155
2018-06-08 09:30 | 147 | 146
2018-06-08 10:00 | 137 | 136
2018-06-08 10:30 | 140 | 139
2018-06-08 11:00 | 133 | 132
2018-06-08 11:30 | 132 | 130
2018-06-08 12:00 | 133 | 131
2018-06-08 12:30 | 125 | 123
2018-06-08 13:00 | 126 | 125
2018-06-08 13:30 | 129 | 127
2018-06-08 14:00 | 126 | 124
2018-06-08 14:30 | 79 | 77
2018-06-08 15:00 | 47 | 44
2018-06-08 15:30 | 53 | 51
2018-06-08 16:00 | 58 | 56
2018-06-08 16:30 | 79 | 77
2018-06-08 17:00 | 96 | 94
2018-06-08 17:30 | 99 | 97
2018-06-08 18:00 | 104 | 102
2018-06-08 18:30 | 118 | 116
2018-06-08 19:00 | 120 | 118
2018-06-08 19:30 | 132 | 130
2018-06-08 20:00 | 132 | 131
2018-06-08 20:30 | 124 | 122
2018-06-08 21:00 | 118 | 116
2018-06-08 21:30 | 111 | 109
2018-06-08 22:00 | 100 | 98
2018-06-08 22:30 | 96 | 94
2018-06-08 23:00 | 149 | 147
2018-06-08 23:30 | 170 | 168
2018-06-09 | 166 | 164
2018-06-09 00:30 | 171 | 169
2018-06-09 01:00 | 168 | 166
2018-06-09 01:30 | 165 | 163
2018-06-09 02:00 | 162 | 160
2018-06-09 02:30 | 158 | 156
2018-06-09 03:00 | 158 | 156
2018-06-09 03:30 | 157 | 155
2018-06-09 04:00 | 158 | 155
2018-06-09 04:30 | 159 | 157
2018-06-09 05:00 | 160 | 158
2018-06-09 05:30 | 165 | 163
2018-06-09 06:00 | 168 | 166
2018-06-09 06:30 | 174 | 172
2018-06-09 07:00 | 178 | 177
2018-06-09 07:30 | 174 | 172
2018-06-09 08:00 | 166 | 164
2018-06-09 08:30 | 161 | 159
2018-06-09 09:00 | 164 | 162
2018-06-09 09:30 | 154 | 152
2018-06-09 10:00 | 153 | 152
2018-06-09 10:30 | 146 | 145
2018-06-09 11:00 | 139 | 137
2018-06-09 11:30 | 128 | 126
2018-06-09 12:00 | 127 | 125
2018-06-09 12:30 | 121 | 120
2018-06-09 13:00 | 136 | 134
2018-06-09 13:30 | 142 | 141
2018-06-09 14:00 | 141 | 139
2018-06-09 14:30 | 131 | 130
2018-06-09 15:00 | 135 | 133
2018-06-09 15:30 | 146 | 144
2018-06-09 16:00 | 156 | 154
2018-06-09 16:30 | 174 | 173
2018-06-09 17:00 | 146 | 144
2018-06-09 17:30 | 130 | 129
2018-06-09 18:00 | 144 | 143
2018-06-09 18:30 | 154 | 153
2018-06-09 19:00 | 153 | 152
2018-06-09 19:30 | 144 | 143
2018-06-09 20:00 | 134 | 133
2018-06-09 20:30 | 124 | 123
2018-06-09 21:00 | 119 | 118
2018-06-09 21:30 | 110 | 109
2018-06-09 22:00 | 104 | 103
2018-06-09 22:30 | 106 | 105
2018-06-09 23:00 | 114 | 113
2018-06-09 23:30 | 110 | 109
2018-06-10 | 163 | 162
2018-06-10 00:30 | 158 | 157
2018-06-10 01:00 | 166 | 165
2018-06-10 01:30 | 161 | 160
2018-06-10 02:00 | 159 | 157
2018-06-10 02:30 | 157 | 156
2018-06-10 03:00 | 156 | 155
2018-06-10 03:30 | 153 | 152
2018-06-10 04:00 | 153 | 152
2018-06-10 04:30 | 153 | 152
2018-06-10 05:00 | 153 | 152
2018-06-10 05:30 | 157 | 155
2018-06-10 06:00 | 161 | 159
2018-06-10 06:30 | 166 | 164
2018-06-10 07:00 | 166 | 165
2018-06-10 07:30 | 160 | 158
2018-06-10 08:00 | 155 | 154
2018-06-10 08:30 | 150 | 148
2018-06-10 09:00 | 146 | 145
2018-06-10 09:30 | 146 | 144
2018-06-10 10:00 | 133 | 132
2018-06-10 10:30 | 130 | 129
2018-06-10 11:00 | 126 | 125
2018-06-10 11:30 | 128 | 127
2018-06-10 12:00 | 127 | 126
2018-06-10 12:30 | 124 | 123
2018-06-10 13:00 | 119 | 118
2018-06-10 13:30 | 116 | 114
2018-06-10 14:00 | 110 | 108
2018-06-10 14:30 | 103 | 102
2018-06-10 15:00 | 111 | 110
2018-06-10 15:30 | 114 | 113
2018-06-10 16:00 | 123 | 122
2018-06-10 16:30 | 143 | 142
2018-06-10 17:00 | 169 | 168
2018-06-10 17:30 | 197 | 196
2018-06-10 18:00 | 220 | 219
2018-06-10 18:30 | 239 | 238
2018-06-10 19:00 | 246 | 245
2018-06-10 19:30 | 238 | 237
2018-06-10 20:00 | 228 | 227
2018-06-10 20:30 | 217 | 215
2018-06-10 21:00 | 207 | 205
2018-06-10 21:30 | 197 | 195
2018-06-10 22:00 | 187 | 185
2018-06-10 22:30 | 186 | 183
2018-06-10 23:00 | 192 | 190
2018-06-10 23:30 | 186 | 183
2018-06-11 | 178 | 176
2018-06-11 00:30 | 174 | 172
2018-06-11 01:00 | 165 | 163
2018-06-11 01:30 | 163 | 161
2018-06-11 02:00 | 157 | 155
2018-06-11 02:30 | 156 | 154
2018-06-11 03:00 | 155 | 153
2018-06-11 03:30 | 154 | 152
2018-06-11 04:00 | 154 | 152
2018-06-11 04:30 | 157 | 155
2018-06-11 05:00 | 160 | 158
2018-06-11 05:30 | 170 | 168
2018-06-11 06:00 | 177 | 176
2018-06-11 06:30 | 197 | 195
2018-06-11 07:00 | 212 | 210
2018-06-11 07:30 | 213 | 212
2018-06-11 08:00 | 209 | 208
2018-06-11 08:30 | 182 | 181
2018-06-11 09:00 | 163 | 162
2018-06-11 09:30 | 157 | 156
2018-06-11 10:00 | 144 | 143
2018-06-11 10:30 | 141 | 139
2018-06-11 11:00 | 139 | 138
2018-06-11 11:30 | 136 | 134
2018-06-11 12:00 | 135 | 134
2018-06-11 12:30 | 131 | 130
2018-06-11 13:00 | 128 | 127
2018-06-11 13:30 | 131 | 130
2018-06-11 14:00 | 129 | 128
2018-06-11 14:30 | 122 | 121
2018-06-11 15:00 | 129 | 128
2018-06-11 15:30 | 135 | 134
2018-06-11 16:00 | 150 | 149
2018-06-11 16:30 | 169 | 168
2018-06-11 17:00 | 193 | 191
2018-06-11 17:30 | 216 | 215
2018-06-11 18:00 | 236 | 234
2018-06-11 18:30 | 253 | 252
2018-06-11 19:00 | 258 | 257
2018-06-11 19:30 | 250 | 249
2018-06-11 20:00 | 239 | 238
2018-06-11 20:30 | 228 | 227
2018-06-11 21:00 | 218 | 217
2018-06-11 21:30 | 206 | 204
2018-06-11 22:00 | 194 | 192
2018-06-11 22:30 | 191 | 189
2018-06-11 23:00 | 195 | 192
2018-06-11 23:30 | 189 | 187
2018-06-12 | 179 | 177
2018-06-12 00:30 | 173 | 171
2018-06-12 01:00 | 169 | 167
2018-06-12 01:30 | 166 | 164
2018-06-12 02:00 | 161 | 160
2018-06-12 02:30 | 160 | 158
2018-06-12 03:00 | 157 | 156
2018-06-12 03:30 | 157 | 155
2018-06-12 04:00 | 155 | 153
2018-06-12 04:30 | 151 | 149
2018-06-12 05:00 | 156 | 154
2018-06-12 05:30 | 167 | 166
2018-06-12 06:00 | 179 | 177
2018-06-12 06:30 | 200 | 199
2018-06-12 07:00 | 213 | 212
2018-06-12 07:30 | 217 | 216
2018-06-12 08:00 | 208 | 207
2018-06-12 08:30 | 189 | 188
2018-06-12 09:00 | 168 | 167
2018-06-12 09:30 | 156 | 155
2018-06-12 10:00 | 145 | 143
2018-06-12 10:30 | 143 | 142
2018-06-12 11:00 | 141 | 139
2018-06-12 11:30 | 139 | 138
2018-06-12 12:00 | 140 | 139
2018-06-12 12:30 | 140 | 139
2018-06-12 13:00 | 139 | 138
2018-06-12 13:30 | 116 | 115
2018-06-12 14:00 | 116 | 115
2018-06-12 14:30 | 116 | 115
2018-06-12 15:00 | 142 | 141
2018-06-12 15:30 | 151 | 150
2018-06-12 16:00 | 165 | 164
2018-06-12 16:30 | 171 | 170
2018-06-12 17:00 | 193 | 193
2018-06-12 17:30 | 217 | 216
2018-06-12 18:00 | 239 | 237
2018-06-12 18:30 | 261 | 260
2018-06-12 19:00 | 264 | 262
2018-06-12 19:30 | 254 | 253
2018-06-12 20:00 | 244 | 243
2018-06-12 20:30 | 232 | 230
2018-06-12 21:00 | 217 | 215
2018-06-12 21:30 | 185 | 183
2018-06-12 22:00 | 192 | 191
2018-06-12 22:30 | 192 | 191
2018-06-12 23:00 | 198 | 197
2018-06-12 23:30 | 191 | 190
2018-06-13 | 179 | 178
2018-06-13 00:30 | 172 | 172
2018-06-13 01:00 | 167 | 166
2018-06-13 01:30 | 165 | 165
2018-06-13 02:00 | 161 | 160
2018-06-13 02:30 | 159 | 158
2018-06-13 03:00 | 158 | 157
2018-06-13 03:30 | 159 | 158
2018-06-13 04:00 | 160 | 159
2018-06-13 04:30 | 162 | 161
2018-06-13 05:00 | 163 | 162
2018-06-13 05:30 | 169 | 168
2018-06-13 06:00 | 178 | 178
2018-06-13 06:30 | 201 | 199
2018-06-13 07:00 | 214 | 212
2018-06-13 07:30 | 220 | 218
2018-06-13 08:00 | 218 | 217
2018-06-13 08:30 | 192 | 190
2018-06-13 09:00 | 175 | 173
2018-06-13 09:30 | 157 | 155
2018-06-13 10:00 | 150 | 148
2018-06-13 10:30 | 145 | 144
2018-06-13 11:00 | 136 | 135
2018-06-13 11:30 | 131 | 130
2018-06-13 12:00 | 133 | 132
2018-06-13 12:30 | 128 | 127
2018-06-13 13:00 | 132 | 131
2018-06-13 13:30 | 133 | 132
2018-06-13 14:00 | 127 | 126
2018-06-13 14:30 | 126 | 124
2018-06-13 15:00 | 124 | 123
2018-06-13 15:30 | 130 | 129
2018-06-13 16:00 | 143 | 142
2018-06-13 16:30 | 161 | 160
2018-06-13 17:00 | 185 | 184
2018-06-13 17:30 | 208 | 207
2018-06-13 18:00 | 226 | 225
2018-06-13 18:30 | 240 | 239
2018-06-13 19:00 | 244 | 243
2018-06-13 19:30 | 235 | 234
2018-06-13 20:00 | 224 | 224
2018-06-13 20:30 | 211 | 210
2018-06-13 21:00 | 201 | 200
2018-06-13 21:30 | 190 | 189
2018-06-13 22:00 | 183 | 181
2018-06-13 22:30 | 179 | 178
2018-06-13 23:00 | 184 | 182
2018-06-13 23:30 | 180 | 179
2018-06-14 | 169 | 169
2018-06-14 00:30 | 163 | 162
2018-06-14 01:00 | 157 | 156
2018-06-14 01:30 | 152 | 151
2018-06-14 02:00 | 148 | 148
2018-06-14 02:30 | 144 | 144
2018-06-14 03:00 | 143 | 142
2018-06-14 03:30 | 146 | 145
2018-06-14 04:00 | 144 | 143
2018-06-14 04:30 | 141 | 141
2018-06-14 05:00 | 146 | 145
2018-06-14 05:30 | 143 | 142
2018-06-14 06:00 | 137 | 136
2018-06-14 06:30 | 145 | 142
2018-06-14 07:00 | 164 | 162
2018-06-14 07:30 | 176 | 174
2018-06-14 08:00 | 173 | 171
2018-06-14 08:30 | 156 | 154
2018-06-14 09:00 | 140 | 138
2018-06-14 09:30 | 126 | 124
2018-06-14 10:00 | 118 | 115
2018-06-14 10:30 | 119 | 116
2018-06-14 11:00 | 98 | 95
2018-06-14 11:30 | 101 | 98
2018-06-14 12:00 | 100 | 97
2018-06-14 12:30 | 101 | 97
2018-06-14 13:00 | 87 | 84
2018-06-14 13:30 | 85 | 81
2018-06-14 14:00 | 90 | 87
2018-06-14 14:30 | 98 | 94
2018-06-14 15:00 | 101 | 97
2018-06-14 15:30 | 106 | 102
2018-06-14 16:00 | 114 | 111
2018-06-14 16:30 | 119 | 116
2018-06-14 17:00 | 139 | 136
2018-06-14 17:30 | 156 | 153
2018-06-14 18:00 | 177 | 174
2018-06-14 18:30 | 193 | 191
2018-06-14 19:00 | 198 | 196
2018-06-14 19:30 | 189 | 186
2018-06-14 20:00 | 189 | 186
2018-06-14 20:30 | 197 | 195
2018-06-14 21:00 | 193 | 191
2018-06-14 21:30 | 187 | 185
2018-06-14 22:00 | 182 | 180
2018-06-14 22:30 | 180 | 178
2018-06-14 23:00 | 185 | 183
2018-06-14 23:30 | 183 | 181
2018-06-15 | 175 | 173
2018-06-15 00:30 | 162 | 160
2018-06-15 01:00 | 152 | 149
2018-06-15 01:30 | 159 | 157
2018-06-15 02:00 | 158 | 155
2018-06-15 02:30 | 157 | 154
2018-06-15 03:00 | 154 | 151
2018-06-15 03:30 | 154 | 151
2018-06-15 04:00 | 155 | 152
2018-06-15 04:30 | 157 | 154
2018-06-15 05:00 | 162 | 160
2018-06-15 05:30 | 169 | 167
2018-06-15 06:00 | 176 | 174
2018-06-15 06:30 | 194 | 192
2018-06-15 07:00 | 214 | 212
2018-06-15 07:30 | 227 | 225
2018-06-15 08:00 | 209 | 206
2018-06-15 08:30 | 185 | 183
2018-06-15 09:00 | 170 | 168
2018-06-15 09:30 | 151 | 149
2018-06-15 10:00 | 138 | 136
2018-06-15 10:30 | 129 | 126
2018-06-15 11:00 | 124 | 121
2018-06-15 11:30 | 120 | 118
2018-06-15 12:00 | 122 | 120
2018-06-15 12:30 | 126 | 124
2018-06-15 13:00 | 111 | 109
2018-06-15 13:30 | 117 | 115
2018-06-15 14:00 | 124 | 122
2018-06-15 14:30 | 138 | 136
2018-06-15 15:00 | 139 | 137
2018-06-15 15:30 | 140 | 138
2018-06-15 16:00 | 148 | 146
2018-06-15 16:30 | 155 | 152
2018-06-15 17:00 | 175 | 173
2018-06-15 17:30 | 198 | 197
2018-06-15 18:00 | 218 | 216
2018-06-15 18:30 | 229 | 226
2018-06-15 19:00 | 231 | 228
2018-06-15 19:30 | 221 | 218
2018-06-15 20:00 | 227 | 224
2018-06-15 20:30 | 223 | 220
2018-06-15 21:00 | 218 | 215
2018-06-15 21:30 | 210 | 206
2018-06-15 22:00 | 196 | 193
2018-06-15 22:30 | 187 | 184
2018-06-15 23:00 | 188 | 185
2018-06-15 23:30 | 180 | 177
2018-06-16 | 173 | 169
2018-06-16 00:30 | 165 | 162
2018-06-16 01:00 | 162 | 160
2018-06-16 01:30 | 158 | 155
2018-06-16 02:00 | 154 | 152
2018-06-16 02:30 | 151 | 149
2018-06-16 03:00 | 151 | 148
2018-06-16 03:30 | 152 | 150
2018-06-16 04:00 | 149 | 147
2018-06-16 04:30 | 151 | 150
2018-06-16 05:00 | 156 | 155
2018-06-16 05:30 | 154 | 153
2018-06-16 06:00 | 156 | 155
2018-06-16 06:30 | 165 | 163
2018-06-16 07:00 | 168 | 167
2018-06-16 07:30 | 165 | 164
2018-06-16 08:00 | 170 | 169
2018-06-16 08:30 | 174 | 173
2018-06-16 09:00 | 161 | 160
2018-06-16 09:30 | 146 | 144
2018-06-16 10:00 | 157 | 156
2018-06-16 10:30 | 145 | 144
2018-06-16 11:00 | 129 | 127
2018-06-16 11:30 | 123 | 122
2018-06-16 12:00 | 118 | 117
2018-06-16 12:30 | 114 | 113
2018-06-16 13:00 | 103 | 101
2018-06-16 13:30 | 116 | 115
2018-06-16 14:00 | 124 | 123
2018-06-16 14:30 | 115 | 114
2018-06-16 15:00 | 110 | 109
2018-06-16 15:30 | 115 | 113
2018-06-16 16:00 | 129 | 127
2018-06-16 16:30 | 136 | 135
2018-06-16 17:00 | 160 | 159
2018-06-16 17:30 | 189 | 188
2018-06-16 18:00 | 204 | 202
2018-06-16 18:30 | 211 | 209
2018-06-16 19:00 | 210 | 209
2018-06-16 19:30 | 201 | 199
2018-06-16 20:00 | 194 | 192
2018-06-16 20:30 | 180 | 178
2018-06-16 21:00 | 173 | 171
2018-06-16 21:30 | 166 | 164
2018-06-16 22:00 | 158 | 155
2018-06-16 22:30 | 160 | 157
2018-06-16 23:00 | 163 | 161
2018-06-16 23:30 | 161 | 159
2018-06-17 | 151 | 149
2018-06-17 00:30 | 146 | 144
2018-06-17 01:00 | 140 | 138
2018-06-17 01:30 | 138 | 137
2018-06-17 02:00 | 138 | 136
2018-06-17 02:30 | 135 | 133
2018-06-17 03:00 | 131 | 129
2018-06-17 03:30 | 129 | 127
2018-06-17 04:00 | 127 | 125
2018-06-17 04:30 | 131 | 129
2018-06-17 05:00 | 131 | 129
2018-06-17 05:30 | 132 | 130
2018-06-17 06:00 | 137 | 135
2018-06-17 06:30 | 142 | 141
2018-06-17 07:00 | 143 | 141
2018-06-17 07:30 | 136 | 134
2018-06-17 08:00 | 137 | 136
2018-06-17 08:30 | 143 | 141
2018-06-17 09:00 | 139 | 138
2018-06-17 09:30 | 137 | 136
2018-06-17 10:00 | 132 | 131
2018-06-17 10:30 | 123 | 122
2018-06-17 11:00 | 109 | 108
2018-06-17 11:30 | 108 | 106
2018-06-17 12:00 | 106 | 104
2018-06-17 12:30 | 100 | 99
2018-06-17 13:00 | 93 | 91
2018-06-17 13:30 | 98 | 97
2018-06-17 14:00 | 99 | 98
2018-06-17 14:30 | 105 | 104
2018-06-17 15:00 | 108 | 106
2018-06-17 15:30 | 119 | 118
2018-06-17 16:00 | 126 | 124
2018-06-17 16:30 | 141 | 139
2018-06-17 17:00 | 155 | 154
2018-06-17 17:30 | 193 | 192
2018-06-17 18:00 | 215 | 214
2018-06-17 18:30 | 231 | 229
2018-06-17 19:00 | 219 | 217
2018-06-17 19:30 | 220 | 218
2018-06-17 20:00 | 209 | 208
2018-06-17 20:30 | 199 | 197
2018-06-17 21:00 | 188 | 186
2018-06-17 21:30 | 191 | 189
2018-06-17 22:00 | 186 | 185
2018-06-17 22:30 | 174 | 172
2018-06-17 23:00 | 173 | 171
2018-06-17 23:30 | 166 | 164
2018-06-18 | 160 | 158
2018-06-18 00:30 | 154 | 152
2018-06-18 01:00 | 145 | 143
2018-06-18 01:30 | 144 | 142
2018-06-18 02:00 | 146 | 144
2018-06-18 02:30 | 145 | 143
2018-06-18 03:00 | 144 | 142
2018-06-18 03:30 | 143 | 141
2018-06-18 04:00 | 144 | 142
2018-06-18 04:30 | 147 | 145
2018-06-18 05:00 | 149 | 147
2018-06-18 05:30 | 159 | 157
2018-06-18 06:00 | 166 | 165
2018-06-18 06:30 | 169 | 168
2018-06-18 07:00 | 153 | 152
2018-06-18 07:30 | 155 | 154
2018-06-18 08:00 | 87 | 85
2018-06-18 08:30 | 80 | 79
2018-06-18 09:00 | 133 | 132
2018-06-18 09:30 | 131 | 130
2018-06-18 10:00 | 122 | 121
2018-06-18 10:30 | 113 | 111
2018-06-18 11:00 | 107 | 106
2018-06-18 11:30 | 101 | 99
2018-06-18 12:00 | 96 | 94
2018-06-18 12:30 | 98 | 96
2018-06-18 13:00 | 101 | 99
2018-06-18 13:30 | 101 | 100
2018-06-18 14:00 | 106 | 105
2018-06-18 14:30 | 108 | 107
2018-06-18 15:00 | 113 | 112
2018-06-18 15:30 | 119 | 118
2018-06-18 16:00 | 131 | 130
2018-06-18 16:30 | 143 | 142
2018-06-18 17:00 | 168 | 167
2018-06-18 17:30 | 197 | 196
2018-06-18 18:00 | 213 | 211
2018-06-18 18:30 | 217 | 214
2018-06-18 19:00 | 234 | 232
2018-06-18 19:30 | 239 | 237
2018-06-18 20:00 | 226 | 224
2018-06-18 20:30 | 217 | 215
2018-06-18 21:00 | 200 | 198
2018-06-18 21:30 | 190 | 188
2018-06-18 22:00 | 175 | 174
2018-06-18 22:30 | 173 | 171
2018-06-18 23:00 | 179 | 177
2018-06-18 23:30 | 171 | 169
2018-06-19 | 160 | 159
2018-06-19 00:30 | 155 | 154
2018-06-19 01:00 | 148 | 146
2018-06-19 01:30 | 144 | 142
2018-06-19 02:00 | 144 | 142
2018-06-19 02:30 | 143 | 141
2018-06-19 03:00 | 140 | 138
2018-06-19 03:30 | 140 | 139
2018-06-19 04:00 | 139 | 138
2018-06-19 04:30 | 142 | 140
2018-06-19 05:00 | 146 | 144
2018-06-19 05:30 | 149 | 148
2018-06-19 06:00 | 156 | 154
2018-06-19 06:30 | 179 | 178
2018-06-19 07:00 | 134 | 133
2018-06-19 07:30 | 138 | 137
2018-06-19 08:00 | 169 | 168
2018-06-19 08:30 | 156 | 155
2018-06-19 09:00 | 133 | 132
2018-06-19 09:30 | 122 | 121
2018-06-19 10:00 | 109 | 107
2018-06-19 10:30 | 100 | 99
2018-06-19 11:00 | 95 | 93
2018-06-19 11:30 | 96 | 95
2018-06-19 12:00 | 91 | 90
2018-06-19 12:30 | 90 | 88
2018-06-19 13:00 | 90 | 88
2018-06-19 13:30 | 93 | 91
2018-06-19 14:00 | 92 | 90
2018-06-19 14:30 | 86 | 84
2018-06-19 15:00 | 94 | 92
2018-06-19 15:30 | 102 | 100
2018-06-19 16:00 | 114 | 112
2018-06-19 16:30 | 123 | 121
2018-06-19 17:00 | 152 | 151
2018-06-19 17:30 | 191 | 190
2018-06-19 18:00 | 190 | 187
2018-06-19 18:30 | 197 | 195
2018-06-19 19:00 | 227 | 225
2018-06-19 19:30 | 223 | 222
2018-06-19 20:00 | 219 | 217
2018-06-19 20:30 | 207 | 206
2018-06-19 21:00 | 194 | 192
2018-06-19 21:30 | 197 | 195
2018-06-19 22:00 | 188 | 186
2018-06-19 22:30 | 175 | 173
2018-06-19 23:00 | 170 | 168
2018-06-19 23:30 | 163 | 160
2018-06-20 | 151 | 150
2018-06-20 00:30 | 145 | 144
2018-06-20 01:00 | 141 | 140
2018-06-20 01:30 | 138 | 137
2018-06-20 02:00 | 136 | 135
2018-06-20 02:30 | 134 | 133
2018-06-20 03:00 | 133 | 132
2018-06-20 03:30 | 132 | 131
2018-06-20 04:00 | 132 | 131
2018-06-20 04:30 | 137 | 136
2018-06-20 05:00 | 138 | 138
2018-06-20 05:30 | 149 | 148
2018-06-20 06:00 | 162 | 161
2018-06-20 06:30 | 179 | 179
2018-06-20 07:00 | 194 | 194
2018-06-20 07:30 | 199 | 198
2018-06-20 08:00 | 185 | 184
2018-06-20 08:30 | 152 | 152
2018-06-20 09:00 | 134 | 133
2018-06-20 09:30 | 124 | 123
2018-06-20 10:00 | 111 | 109
2018-06-20 10:30 | 100 | 98
2018-06-20 11:00 | 94 | 92
2018-06-20 11:30 | 91 | 88
2018-06-20 12:00 | 89 | 87
2018-06-20 12:30 | 91 | 89
2018-06-20 13:00 | 88 | 86
2018-06-20 13:30 | 86 | 84
2018-06-20 14:00 | 85 | 83
2018-06-20 14:30 | 82 | 79
2018-06-20 15:00 | 87 | 85
2018-06-20 15:30 | 90 | 88
2018-06-20 16:00 | 103 | 102
2018-06-20 16:30 | 120 | 119
2018-06-20 17:00 | 146 | 145
2018-06-20 17:30 | 178 | 178
2018-06-20 18:00 | 205 | 205
2018-06-20 18:30 | 225 | 224
2018-06-20 19:00 | 233 | 232
2018-06-20 19:30 | 226 | 225
2018-06-20 20:00 | 215 | 214
2018-06-20 20:30 | 192 | 191
2018-06-20 21:00 | 184 | 183
2018-06-20 21:30 | 183 | 182
2018-06-20 22:00 | 180 | 179
2018-06-20 22:30 | 179 | 178
2018-06-20 23:00 | 172 | 171
2018-06-20 23:30 | 161 | 160
2018-06-21 | 151 | 150
2018-06-21 00:30 | 147 | 146
2018-06-21 01:00 | 142 | 141
2018-06-21 01:30 | 137 | 136
2018-06-21 02:00 | 134 | 133
2018-06-21 02:30 | 132 | 131
2018-06-21 03:00 | 131 | 129
2018-06-21 03:30 | 133 | 132
2018-06-21 04:00 | 136 | 135
2018-06-21 04:30 | 138 | 137
2018-06-21 05:00 | 139 | 138
2018-06-21 05:30 | 147 | 146
2018-06-21 06:00 | 160 | 160
2018-06-21 06:30 | 180 | 179
2018-06-21 07:00 | 177 | 177
2018-06-21 07:30 | 187 | 187
2018-06-21 08:00 | 161 | 160
2018-06-21 08:30 | 112 | 111
2018-06-21 09:00 | 91 | 89
2018-06-21 09:30 | 81 | 78
2018-06-21 10:00 | 72 | 68
2018-06-21 10:30 | 61 | 54
2018-06-21 11:00 | 42 | 37
2018-06-21 11:30 | 16 | 12
2018-06-21 12:00 | 31 | 23
2018-06-21 12:30 | 27 | 20
2018-06-21 13:00 | 20 | 17
2018-06-21 13:30 | 31 | 23
2018-06-21 14:00 | 38 | 30
2018-06-21 14:30 | 38 | 30
2018-06-21 15:00 | 37 | 27
2018-06-21 15:30 | 18 | 15
2018-06-21 16:00 | 3 | 3
2018-06-21 16:30 | 1 | 1
2018-06-21 17:00 | 23 | 20
2018-06-21 17:30 | 62 | 56
2018-06-21 18:00 | 86 | 84
2018-06-21 18:30 | 106 | 105
2018-06-21 19:00 | 112 | 110
2018-06-21 19:30 | 102 | 101
2018-06-21 20:00 | 93 | 91
2018-06-21 20:30 | 84 | 82
2018-06-21 21:00 | 73 | 69
2018-06-21 21:30 | 61 | 55
2018-06-21 22:00 | 47 | 41
2018-06-21 22:30 | 45 | 41
2018-06-21 23:00 | 60 | 53
2018-06-21 23:30 | 47 | 42
2018-06-22 | 38 | 34
2018-06-22 00:30 | 70 | 66
2018-06-22 01:00 | 95 | 93
2018-06-22 01:30 | 133 | 132
2018-06-22 02:00 | 133 | 132
2018-06-22 02:30 | 130 | 129
2018-06-22 03:00 | 130 | 129
2018-06-22 03:30 | 130 | 129
2018-06-22 04:00 | 130 | 129
2018-06-22 04:30 | 135 | 134
2018-06-22 05:00 | 137 | 137
2018-06-22 05:30 | 129 | 128
2018-06-22 06:00 | 153 | 152
2018-06-22 06:30 | 171 | 171
2018-06-22 07:00 | 187 | 187
2018-06-22 07:30 | 197 | 197
2018-06-22 08:00 | 191 | 190
2018-06-22 08:30 | 167 | 166
2018-06-22 09:00 | 155 | 154
2018-06-22 09:30 | 147 | 146
2018-06-22 10:00 | 133 | 132
2018-06-22 10:30 | 126 | 125
2018-06-22 11:00 | 121 | 120
2018-06-22 11:30 | 111 | 109
2018-06-22 12:00 | 111 | 109
2018-06-22 12:30 | 106 | 104
2018-06-22 13:00 | 107 | 105
2018-06-22 13:30 | 108 | 106
2018-06-22 14:00 | 104 | 102
2018-06-22 14:30 | 101 | 99
2018-06-22 15:00 | 105 | 103
2018-06-22 15:30 | 114 | 113
2018-06-22 16:00 | 120 | 119
2018-06-22 16:30 | 128 | 127
2018-06-22 17:00 | 150 | 149
2018-06-22 17:30 | 179 | 178
2018-06-22 18:00 | 197 | 197
2018-06-22 18:30 | 208 | 208
2018-06-22 19:00 | 209 | 208
2018-06-22 19:30 | 201 | 201
2018-06-22 20:00 | 193 | 192
2018-06-22 20:30 | 184 | 183
2018-06-22 21:00 | 175 | 174
2018-06-22 21:30 | 166 | 165
2018-06-22 22:00 | 159 | 159
2018-06-22 22:30 | 161 | 160
2018-06-22 23:00 | 169 | 169
2018-06-22 23:30 | 161 | 160
2018-06-23 | 154 | 153
2018-06-23 00:30 | 149 | 148
2018-06-23 01:00 | 143 | 142
2018-06-23 01:30 | 137 | 136
2018-06-23 02:00 | 132 | 131
2018-06-23 02:30 | 129 | 128
2018-06-23 03:00 | 127 | 126
2018-06-23 03:30 | 127 | 126
2018-06-23 04:00 | 128 | 126
2018-06-23 04:30 | 129 | 128
2018-06-23 05:00 | 131 | 130
2018-06-23 05:30 | 140 | 139
2018-06-23 06:00 | 143 | 142
2018-06-23 06:30 | 150 | 150
2018-06-23 07:00 | 156 | 155
2018-06-23 07:30 | 149 | 149
2018-06-23 08:00 | 145 | 144
2018-06-23 08:30 | 139 | 138
2018-06-23 09:00 | 145 | 144
2018-06-23 09:30 | 142 | 141
2018-06-23 10:00 | 137 | 136
2018-06-23 10:30 | 125 | 125
2018-06-23 11:00 | 121 | 120
2018-06-23 11:30 | 109 | 108
2018-06-23 12:00 | 103 | 102
2018-06-23 12:30 | 105 | 104
2018-06-23 13:00 | 106 | 105
2018-06-23 13:30 | 112 | 111
2018-06-23 14:00 | 99 | 98
2018-06-23 14:30 | 90 | 89
2018-06-23 15:00 | 86 | 84
2018-06-23 15:30 | 114 | 113
2018-06-23 16:00 | 127 | 126
2018-06-23 16:30 | 140 | 139
2018-06-23 17:00 | 163 | 162
2018-06-23 17:30 | 179 | 178
2018-06-23 18:00 | 200 | 200
2018-06-23 18:30 | 213 | 212
2018-06-23 19:00 | 212 | 211
2018-06-23 19:30 | 200 | 200
2018-06-23 20:00 | 195 | 194
2018-06-23 20:30 | 181 | 180
2018-06-23 21:00 | 160 | 160
2018-06-23 21:30 | 151 | 150
2018-06-23 22:00 | 144 | 144
2018-06-23 22:30 | 147 | 146
2018-06-23 23:00 | 153 | 152
2018-06-23 23:30 | 152 | 151
2018-06-24 | 141 | 140
2018-06-24 00:30 | 139 | 138
2018-06-24 01:00 | 136 | 135
2018-06-24 01:30 | 131 | 129
2018-06-24 02:00 | 128 | 127
2018-06-24 02:30 | 127 | 126
2018-06-24 03:00 | 127 | 126
2018-06-24 03:30 | 127 | 126
2018-06-24 04:00 | 129 | 128
2018-06-24 04:30 | 126 | 125
2018-06-24 05:00 | 125 | 124
2018-06-24 05:30 | 129 | 128
2018-06-24 06:00 | 136 | 135
2018-06-24 06:30 | 141 | 140
2018-06-24 07:00 | 142 | 141
2018-06-24 07:30 | 132 | 131
2018-06-24 08:00 | 139 | 138
2018-06-24 08:30 | 139 | 138
2018-06-24 09:00 | 129 | 128
2018-06-24 09:30 | 125 | 124
2018-06-24 10:00 | 118 | 117
2018-06-24 10:30 | 117 | 115
2018-06-24 11:00 | 114 | 113
2018-06-24 11:30 | 105 | 104
2018-06-24 12:00 | 105 | 104
2018-06-24 12:30 | 108 | 107
2018-06-24 13:00 | 109 | 108
2018-06-24 13:30 | 111 | 110
2018-06-24 14:00 | 104 | 103
2018-06-24 14:30 | 98 | 97
2018-06-24 15:00 | 102 | 101
2018-06-24 15:30 | 105 | 104
2018-06-24 16:00 | 121 | 120
2018-06-24 16:30 | 139 | 138
2018-06-24 17:00 | 156 | 155
2018-06-24 17:30 | 178 | 177
2018-06-24 18:00 | 194 | 193
2018-06-24 18:30 | 211 | 210
2018-06-24 19:00 | 215 | 214
2018-06-24 19:30 | 206 | 205
2018-06-24 20:00 | 193 | 191
2018-06-24 20:30 | 167 | 166
2018-06-24 21:00 | 168 | 167
2018-06-24 21:30 | 158 | 157
2018-06-24 22:00 | 148 | 147
2018-06-24 22:30 | 153 | 152
2018-06-24 23:00 | 160 | 159
2018-06-24 23:30 | 144 | 143
2018-06-25 | 141 | 140
2018-06-25 00:30 | 138 | 136
2018-06-25 01:00 | 132 | 130
2018-06-25 01:30 | 129 | 128
2018-06-25 02:00 | 125 | 124
2018-06-25 02:30 | 122 | 121
2018-06-25 03:00 | 121 | 120
2018-06-25 03:30 | 121 | 120
2018-06-25 04:00 | 123 | 121
2018-06-25 04:30 | 125 | 123
2018-06-25 05:00 | 128 | 127
2018-06-25 05:30 | 134 | 133
2018-06-25 06:00 | 142 | 141
2018-06-25 06:30 | 160 | 159
2018-06-25 07:00 | 170 | 169
2018-06-25 07:30 | 176 | 176
2018-06-25 08:00 | 186 | 186
2018-06-25 08:30 | 187 | 186
2018-06-25 09:00 | 184 | 183
2018-06-25 09:30 | 170 | 169
2018-06-25 10:00 | 153 | 152
2018-06-25 10:30 | 148 | 147
2018-06-25 11:00 | 142 | 141
2018-06-25 11:30 | 134 | 133
2018-06-25 12:00 | 126 | 126
2018-06-25 12:30 | 137 | 136
2018-06-25 13:00 | 137 | 136
2018-06-25 13:30 | 142 | 141
2018-06-25 14:00 | 140 | 139
2018-06-25 14:30 | 131 | 130
2018-06-25 15:00 | 134 | 133
2018-06-25 15:30 | 152 | 151
2018-06-25 16:00 | 169 | 168
2018-06-25 16:30 | 180 | 179
2018-06-25 17:00 | 190 | 189
2018-06-25 17:30 | 205 | 204
2018-06-25 18:00 | 196 | 195
2018-06-25 18:30 | 191 | 190
2018-06-25 19:00 | 192 | 190
2018-06-25 19:30 | 191 | 190
2018-06-25 20:00 | 190 | 189
2018-06-25 20:30 | 190 | 190
2018-06-25 21:00 | 180 | 179
2018-06-25 21:30 | 169 | 168
2018-06-25 22:00 | 155 | 154
2018-06-25 22:30 | 150 | 150
2018-06-25 23:00 | 157 | 156
2018-06-25 23:30 | 151 | 150
2018-06-26 | 141 | 140
2018-06-26 00:30 | 135 | 134
2018-06-26 01:00 | 131 | 130
2018-06-26 01:30 | 128 | 126
2018-06-26 02:00 | 123 | 122
2018-06-26 02:30 | 122 | 121
2018-06-26 03:00 | 124 | 123
2018-06-26 03:30 | 130 | 129
2018-06-26 04:00 | 135 | 133
2018-06-26 04:30 | 136 | 135
2018-06-26 05:00 | 137 | 136
2018-06-26 05:30 | 142 | 141
2018-06-26 06:00 | 150 | 149
2018-06-26 06:30 | 173 | 172
2018-06-26 07:00 | 187 | 186
2018-06-26 07:30 | 198 | 197
2018-06-26 08:00 | 207 | 207
2018-06-26 08:30 | 205 | 205
2018-06-26 09:00 | 190 | 189
2018-06-26 09:30 | 186 | 185
2018-06-26 10:00 | 183 | 182
2018-06-26 10:30 | 183 | 182
2018-06-26 11:00 | 175 | 174
2018-06-26 11:30 | 161 | 160
2018-06-26 12:00 | 142 | 141
2018-06-26 12:30 | 124 | 123
2018-06-26 13:00 | 124 | 123
2018-06-26 13:30 | 121 | 120
2018-06-26 14:00 | 137 | 136
2018-06-26 14:30 | 138 | 137
2018-06-26 15:00 | 140 | 139
2018-06-26 15:30 | 156 | 155
2018-06-26 16:00 | 166 | 165
2018-06-26 16:30 | 178 | 177
2018-06-26 17:00 | 187 | 186
2018-06-26 17:30 | 204 | 203
2018-06-26 18:00 | 222 | 221
2018-06-26 18:30 | 238 | 237
2018-06-26 19:00 | 241 | 240
2018-06-26 19:30 | 234 | 233
2018-06-26 20:00 | 220 | 219
2018-06-26 20:30 | 208 | 207
2018-06-26 21:00 | 198 | 197
2018-06-26 21:30 | 196 | 195
2018-06-26 22:00 | 184 | 183
2018-06-26 22:30 | 179 | 178
2018-06-26 23:00 | 184 | 183
2018-06-26 23:30 | 176 | 175
2018-06-27 | 167 | 166
2018-06-27 00:30 | 156 | 155
2018-06-27 01:00 | 155 | 154
2018-06-27 01:30 | 151 | 150
2018-06-27 02:00 | 147 | 146
2018-06-27 02:30 | 145 | 144
2018-06-27 03:00 | 139 | 138
2018-06-27 03:30 | 136 | 135
2018-06-27 04:00 | 138 | 137
2018-06-27 04:30 | 125 | 124
2018-06-27 05:00 | 102 | 100
2018-06-27 05:30 | 106 | 105
2018-06-27 06:00 | 119 | 118
2018-06-27 06:30 | 134 | 133
2018-06-27 07:00 | 147 | 146
2018-06-27 07:30 | 135 | 134
2018-06-27 08:00 | 121 | 120
2018-06-27 08:30 | 85 | 83
2018-06-27 09:00 | 67 | 66
2018-06-27 09:30 | 56 | 52
2018-06-27 10:00 | 44 | 39
2018-06-27 10:30 | 46 | 39
2018-06-27 11:00 | 44 | 37
2018-06-27 11:30 | 38 | 32
2018-06-27 12:00 | 34 | 25
2018-06-27 12:30 | 39 | 31
2018-06-27 13:00 | 44 | 39
2018-06-27 13:30 | 41 | 36
2018-06-27 14:00 | 42 | 36
2018-06-27 14:30 | 46 | 42
2018-06-27 15:00 | 41 | 35
2018-06-27 15:30 | 39 | 34
2018-06-27 16:00 | 52 | 47
2018-06-27 16:30 | 57 | 54
2018-06-27 17:00 | 59 | 57
2018-06-27 17:30 | 76 | 75
2018-06-27 18:00 | 89 | 88
2018-06-27 18:30 | 109 | 108
2018-06-27 19:00 | 113 | 112
2018-06-27 19:30 | 106 | 105
2018-06-27 20:00 | 97 | 96
2018-06-27 20:30 | 84 | 82
2018-06-27 21:00 | 82 | 80
2018-06-27 21:30 | 66 | 64
2018-06-27 22:00 | 77 | 75
2018-06-27 22:30 | 77 | 75
2018-06-27 23:00 | 81 | 80
2018-06-27 23:30 | 75 | 74
2018-06-28 | 67 | 64
2018-06-28 00:30 | 93 | 92
2018-06-28 01:00 | 123 | 122
2018-06-28 01:30 | 162 | 161
2018-06-28 02:00 | 162 | 161
2018-06-28 02:30 | 154 | 153
2018-06-28 03:00 | 144 | 143
2018-06-28 03:30 | 141 | 140
2018-06-28 04:00 | 136 | 134
2018-06-28 04:30 | 136 | 135
2018-06-28 05:00 | 139 | 138
2018-06-28 05:30 | 146 | 145
2018-06-28 06:00 | 156 | 155
2018-06-28 06:30 | 175 | 174
2018-06-28 07:00 | 188 | 188
2018-06-28 07:30 | 193 | 193
2018-06-28 08:00 | 196 | 196
2018-06-28 08:30 | 182 | 181
2018-06-28 09:00 | 169 | 168
2018-06-28 09:30 | 182 | 181
2018-06-28 10:00 | 176 | 175
2018-06-28 10:30 | 172 | 172
2018-06-28 11:00 | 172 | 171
2018-06-28 11:30 | 168 | 167
2018-06-28 12:00 | 162 | 161
2018-06-28 12:30 | 158 | 157
2018-06-28 13:00 | 151 | 151
2018-06-28 13:30 | 156 | 156
2018-06-28 14:00 | 152 | 151
2018-06-28 14:30 | 153 | 153
2018-06-28 15:00 | 162 | 161
2018-06-28 15:30 | 167 | 167
2018-06-28 16:00 | 175 | 175
2018-06-28 16:30 | 179 | 179
2018-06-28 17:00 | 185 | 185
2018-06-28 17:30 | 208 | 207
2018-06-28 18:00 | 222 | 222
2018-06-28 18:30 | 241 | 240
2018-06-28 19:00 | 244 | 243
2018-06-28 19:30 | 231 | 230
2018-06-28 20:00 | 223 | 222
2018-06-28 20:30 | 211 | 210
2018-06-28 21:00 | 201 | 200
2018-06-28 21:30 | 185 | 184
2018-06-28 22:00 | 173 | 172
2018-06-28 22:30 | 173 | 172
2018-06-28 23:00 | 178 | 177
2018-06-28 23:30 | 170 | 168
2018-06-29 | 161 | 160
2018-06-29 00:30 | 153 | 152
2018-06-29 01:00 | 148 | 146
2018-06-29 01:30 | 144 | 143
2018-06-29 02:00 | 143 | 142
2018-06-29 02:30 | 141 | 140
2018-06-29 03:00 | 138 | 137
2018-06-29 03:30 | 137 | 136
2018-06-29 04:00 | 136 | 135
2018-06-29 04:30 | 137 | 136
2018-06-29 05:00 | 138 | 137
2018-06-29 05:30 | 146 | 145
2018-06-29 06:00 | 154 | 153
2018-06-29 06:30 | 171 | 170
2018-06-29 07:00 | 189 | 188
2018-06-29 07:30 | 180 | 179
2018-06-29 08:00 | 191 | 190
2018-06-29 08:30 | 188 | 187
2018-06-29 09:00 | 178 | 178
2018-06-29 09:30 | 168 | 167
2018-06-29 10:00 | 164 | 163
2018-06-29 10:30 | 159 | 158
2018-06-29 11:00 | 151 | 150
2018-06-29 11:30 | 144 | 143
2018-06-29 12:00 | 139 | 138
2018-06-29 12:30 | 136 | 135
2018-06-29 13:00 | 132 | 132
2018-06-29 13:30 | 126 | 125
2018-06-29 14:00 | 117 | 116
2018-06-29 14:30 | 115 | 114
2018-06-29 15:00 | 118 | 117
2018-06-29 15:30 | 130 | 129
2018-06-29 16:00 | 134 | 133
2018-06-29 16:30 | 149 | 148
2018-06-29 17:00 | 164 | 163
2018-06-29 17:30 | 186 | 185
2018-06-29 18:00 | 202 | 201
2018-06-29 18:30 | 218 | 218
2018-06-29 19:00 | 221 | 220
2018-06-29 19:30 | 211 | 210
2018-06-29 20:00 | 201 | 201
2018-06-29 20:30 | 192 | 191
2018-06-29 21:00 | 183 | 182
2018-06-29 21:30 | 175 | 174
2018-06-29 22:00 | 166 | 166
2018-06-29 22:30 | 157 | 156
2018-06-29 23:00 | 146 | 145
2018-06-29 23:30 | 151 | 150
2018-06-30 | 161 | 160
2018-06-30 00:30 | 158 | 157
2018-06-30 01:00 | 155 | 154
2018-06-30 01:30 | 151 | 150
2018-06-30 02:00 | 144 | 143
2018-06-30 02:30 | 142 | 141
2018-06-30 03:00 | 141 | 140
2018-06-30 03:30 | 139 | 138
2018-06-30 04:00 | 138 | 137
2018-06-30 04:30 | 139 | 138
2018-06-30 05:00 | 139 | 138
2018-06-30 05:30 | 142 | 141
2018-06-30 06:00 | 144 | 143
2018-06-30 06:30 | 153 | 152
2018-06-30 07:00 | 157 | 156
2018-06-30 07:30 | 154 | 153
2018-06-30 08:00 | 149 | 148
2018-06-30 08:30 | 145 | 144
2018-06-30 09:00 | 148 | 147
2018-06-30 09:30 | 146 | 146
2018-06-30 10:00 | 145 | 144
2018-06-30 10:30 | 143 | 142
2018-06-30 11:00 | 136 | 135
2018-06-30 11:30 | 133 | 132
2018-06-30 12:00 | 129 | 128
2018-06-30 12:30 | 125 | 124
2018-06-30 13:00 | 122 | 121
2018-06-30 13:30 | 119 | 118
2018-06-30 14:00 | 115 | 114
2018-06-30 14:30 | 109 | 108
2018-06-30 15:00 | 112 | 111
2018-06-30 15:30 | 128 | 127
2018-06-30 16:00 | 139 | 138
2018-06-30 16:30 | 145 | 145
2018-06-30 17:00 | 169 | 168
2018-06-30 17:30 | 183 | 182
2018-06-30 18:00 | 196 | 196
2018-06-30 18:30 | 203 | 203
2018-06-30 19:00 | 198 | 198
2018-06-30 19:30 | 195 | 195
2018-06-30 20:00 | 187 | 187
2018-06-30 20:30 | 179 | 178
2018-06-30 21:00 | 173 | 172
2018-06-30 21:30 | 163 | 162
2018-06-30 22:00 | 158 | 157
2018-06-30 22:30 | 160 | 159
2018-06-30 23:00 | 165 | 164
2018-06-30 23:30 | 161 | 160
2018-07-01 | 156 | 155
2018-07-01 00:30 | 151 | 151
2018-07-01 01:00 | 148 | 147
2018-07-01 01:30 | 142 | 141
2018-07-01 02:00 | 137 | 136
2018-07-01 02:30 | 135 | 134
2018-07-01 03:00 | 133 | 132
2018-07-01 03:30 | 135 | 134
2018-07-01 04:00 | 138 | 137
2018-07-01 04:30 | 136 | 135
2018-07-01 05:00 | 137 | 136
2018-07-01 05:30 | 140 | 139
2018-07-01 06:00 | 142 | 141
2018-07-01 06:30 | 130 | 129
2018-07-01 07:00 | 136 | 136
2018-07-01 07:30 | 138 | 137
2018-07-01 08:00 | 133 | 132
2018-07-01 08:30 | 134 | 133
2018-07-01 09:00 | 130 | 130
2018-07-01 09:30 | 131 | 130
2018-07-01 10:00 | 129 | 128
2018-07-01 10:30 | 117 | 116
2018-07-01 11:00 | 111 | 110
2018-07-01 11:30 | 109 | 109
2018-07-01 12:00 | 108 | 107
2018-07-01 12:30 | 114 | 113
2018-07-01 13:00 | 112 | 111
2018-07-01 13:30 | 115 | 114
2018-07-01 14:00 | 112 | 111
2018-07-01 14:30 | 116 | 115
2018-07-01 15:00 | 134 | 133
2018-07-01 15:30 | 149 | 148
2018-07-01 16:00 | 156 | 155
2018-07-01 16:30 | 148 | 147
2018-07-01 17:00 | 167 | 166
2018-07-01 17:30 | 175 | 175
2018-07-01 18:00 | 195 | 195
2018-07-01 18:30 | 206 | 206
2018-07-01 19:00 | 211 | 211
2018-07-01 19:30 | 202 | 202
2018-07-01 20:00 | 193 | 192
2018-07-01 20:30 | 188 | 187
2018-07-01 21:00 | 180 | 180
2018-07-01 21:30 | 173 | 173
2018-07-01 22:00 | 166 | 165
2018-07-01 22:30 | 180 | 179
2018-07-01 23:00 | 178 | 177
2018-07-01 23:30 | 167 | 167
2018-07-02 | 157 | 156
2018-07-02 00:30 | 150 | 149
2018-07-02 01:00 | 146 | 146
2018-07-02 01:30 | 143 | 143
2018-07-02 02:00 | 140 | 139
2018-07-02 02:30 | 139 | 138
2018-07-02 03:00 | 137 | 136
2018-07-02 03:30 | 140 | 139
2018-07-02 04:00 | 142 | 141
2018-07-02 04:30 | 136 | 135
2018-07-02 05:00 | 141 | 140
2018-07-02 05:30 | 149 | 148
2018-07-02 06:00 | 136 | 135
2018-07-02 06:30 | 134 | 133
2018-07-02 07:00 | 148 | 147
2018-07-02 07:30 | 162 | 162
2018-07-02 08:00 | 167 | 166
2018-07-02 08:30 | 169 | 168
2018-07-02 09:00 | 175 | 174
2018-07-02 09:30 | 164 | 163
2018-07-02 10:00 | 151 | 150
2018-07-02 10:30 | 147 | 146
2018-07-02 11:00 | 148 | 148
2018-07-02 11:30 | 134 | 133
2018-07-02 12:00 | 127 | 127
2018-07-02 12:30 | 132 | 132
2018-07-02 13:00 | 139 | 138
2018-07-02 13:30 | 134 | 133
2018-07-02 14:00 | 136 | 135
2018-07-02 14:30 | 130 | 130
2018-07-02 15:00 | 143 | 142
2018-07-02 15:30 | 152 | 151
2018-07-02 16:00 | 158 | 157
2018-07-02 16:30 | 124 | 123
2018-07-02 17:00 | 100 | 99
2018-07-02 17:30 | 116 | 115
2018-07-02 18:00 | 134 | 133
2018-07-02 18:30 | 150 | 149
2018-07-02 19:00 | 153 | 152
2018-07-02 19:30 | 143 | 142
2018-07-02 20:00 | 139 | 138
2018-07-02 20:30 | 127 | 126
2018-07-02 21:00 | 181 | 180
2018-07-02 21:30 | 196 | 196
2018-07-02 22:00 | 189 | 188
2018-07-02 22:30 | 195 | 194
2018-07-02 23:00 | 189 | 188
2018-07-02 23:30 | 185 | 185
2018-07-03 | 180 | 180
2018-07-03 00:30 | 171 | 171
2018-07-03 01:00 | 165 | 164
2018-07-03 01:30 | 160 | 159
2018-07-03 02:00 | 158 | 157
2018-07-03 02:30 | 155 | 154
2018-07-03 03:00 | 153 | 152
2018-07-03 03:30 | 154 | 153
2018-07-03 04:00 | 154 | 153
2018-07-03 04:30 | 156 | 155
2018-07-03 05:00 | 156 | 156
2018-07-03 05:30 | 163 | 162
2018-07-03 06:00 | 170 | 169
2018-07-03 06:30 | 171 | 170
2018-07-03 07:00 | 183 | 182
2018-07-03 07:30 | 181 | 180
2018-07-03 08:00 | 170 | 169
2018-07-03 08:30 | 157 | 156
2018-07-03 09:00 | 151 | 150
2018-07-03 09:30 | 152 | 151
2018-07-03 10:00 | 143 | 141
2018-07-03 10:30 | 136 | 135
2018-07-03 11:00 | 133 | 132
2018-07-03 11:30 | 143 | 142
2018-07-03 12:00 | 132 | 131
2018-07-03 12:30 | 125 | 123
2018-07-03 13:00 | 128 | 128
2018-07-03 13:30 | 136 | 135
2018-07-03 14:00 | 145 | 144
2018-07-03 14:30 | 145 | 145
2018-07-03 15:00 | 150 | 150
2018-07-03 15:30 | 155 | 155
2018-07-03 16:00 | 159 | 158
2018-07-03 16:30 | 125 | 124
2018-07-03 17:00 | 101 | 100
2018-07-03 17:30 | 126 | 125
2018-07-03 18:00 | 148 | 147
2018-07-03 18:30 | 166 | 165
2018-07-03 19:00 | 172 | 172
2018-07-03 19:30 | 158 | 157
2018-07-03 20:00 | 147 | 146
2018-07-03 20:30 | 138 | 136
2018-07-03 21:00 | 185 | 184
2018-07-03 21:30 | 213 | 212
2018-07-03 22:00 | 210 | 209
2018-07-03 22:30 | 201 | 200
2018-07-03 23:00 | 199 | 198
2018-07-03 23:30 | 191 | 190
2018-07-04 | 182 | 181
2018-07-04 00:30 | 169 | 167
2018-07-04 01:00 | 159 | 158
2018-07-04 01:30 | 152 | 150
2018-07-04 02:00 | 146 | 144
2018-07-04 02:30 | 144 | 143
2018-07-04 03:00 | 142 | 140
2018-07-04 03:30 | 139 | 138
2018-07-04 04:00 | 143 | 141
2018-07-04 04:30 | 145 | 144
2018-07-04 05:00 | 149 | 147
2018-07-04 05:30 | 154 | 152
2018-07-04 06:00 | 162 | 161
2018-07-04 06:30 | 174 | 172
2018-07-04 07:00 | 173 | 172
2018-07-04 07:30 | 182 | 181
2018-07-04 08:00 | 170 | 169
2018-07-04 08:30 | 126 | 125
2018-07-04 09:00 | 128 | 126
2018-07-04 09:30 | 142 | 141
2018-07-04 10:00 | 131 | 130
2018-07-04 10:30 | 125 | 124
2018-07-04 11:00 | 133 | 132
2018-07-04 11:30 | 133 | 132
2018-07-04 12:00 | 126 | 125
2018-07-04 12:30 | 123 | 122
2018-07-04 13:00 | 118 | 117
2018-07-04 13:30 | 114 | 113
2018-07-04 14:00 | 111 | 109
2018-07-04 14:30 | 117 | 115
2018-07-04 15:00 | 124 | 123
2018-07-04 15:30 | 130 | 129
2018-07-04 16:00 | 138 | 137
2018-07-04 16:30 | 146 | 145
2018-07-04 17:00 | 127 | 126
2018-07-04 17:30 | 113 | 112
2018-07-04 18:00 | 126 | 125
2018-07-04 18:30 | 146 | 145
2018-07-04 19:00 | 154 | 153
2018-07-04 19:30 | 147 | 146
2018-07-04 20:00 | 140 | 139
2018-07-04 20:30 | 134 | 132
2018-07-04 21:00 | 121 | 120
2018-07-04 21:30 | 173 | 172
2018-07-04 22:00 | 179 | 178
2018-07-04 22:30 | 167 | 166
2018-07-04 23:00 | 153 | 152
2018-07-04 23:30 | 146 | 145
2018-07-05 | 126 | 124
2018-07-05 00:30 | 131 | 129
2018-07-05 01:00 | 125 | 123
2018-07-05 01:30 | 119 | 117
2018-07-05 02:00 | 135 | 134
2018-07-05 02:30 | 140 | 139
2018-07-05 03:00 | 143 | 141
2018-07-05 03:30 | 145 | 143
2018-07-05 04:00 | 144 | 143
2018-07-05 04:30 | 145 | 143
2018-07-05 05:00 | 149 | 148
2018-07-05 05:30 | 156 | 154
2018-07-05 06:00 | 163 | 162
2018-07-05 06:30 | 174 | 173
2018-07-05 07:00 | 177 | 176
2018-07-05 07:30 | 183 | 182
2018-07-05 08:00 | 172 | 171
2018-07-05 08:30 | 154 | 153
2018-07-05 09:00 | 142 | 141
2018-07-05 09:30 | 125 | 124
2018-07-05 10:00 | 114 | 113
2018-07-05 10:30 | 104 | 103
2018-07-05 11:00 | 117 | 116
2018-07-05 11:30 | 124 | 123
2018-07-05 12:00 | 120 | 119
2018-07-05 12:30 | 117 | 115
2018-07-05 13:00 | 115 | 114
2018-07-05 13:30 | 106 | 105
2018-07-05 14:00 | 98 | 97
2018-07-05 14:30 | 96 | 94
2018-07-05 15:00 | 99 | 98
2018-07-05 15:30 | 108 | 107
2018-07-05 16:00 | 114 | 112
2018-07-05 16:30 | 121 | 120
2018-07-05 17:00 | 141 | 140
2018-07-05 17:30 | 178 | 177
2018-07-05 18:00 | 202 | 201
2018-07-05 18:30 | 221 | 220
2018-07-05 19:00 | 231 | 230
2018-07-05 19:30 | 226 | 225
2018-07-05 20:00 | 229 | 228
2018-07-05 20:30 | 232 | 231
2018-07-05 21:00 | 228 | 227
2018-07-05 21:30 | 216 | 214
2018-07-05 22:00 | 202 | 200
2018-07-05 22:30 | 188 | 186
2018-07-05 23:00 | 176 | 174
2018-07-05 23:30 | 164 | 163
2018-07-06 | 156 | 154
2018-07-06 00:30 | 150 | 148
2018-07-06 01:00 | 145 | 143
2018-07-06 01:30 | 139 | 137
2018-07-06 02:00 | 135 | 133
2018-07-06 02:30 | 132 | 131
2018-07-06 03:00 | 131 | 130
2018-07-06 03:30 | 131 | 130
2018-07-06 04:00 | 132 | 131
2018-07-06 04:30 | 137 | 136
2018-07-06 05:00 | 141 | 140
2018-07-06 05:30 | 144 | 143
2018-07-06 06:00 | 154 | 153
2018-07-06 06:30 | 167 | 166
2018-07-06 07:00 | 165 | 164
2018-07-06 07:30 | 161 | 160
2018-07-06 08:00 | 155 | 154
2018-07-06 08:30 | 144 | 143
2018-07-06 09:00 | 132 | 131
2018-07-06 09:30 | 122 | 122
2018-07-06 10:00 | 126 | 125
2018-07-06 10:30 | 120 | 119
2018-07-06 11:00 | 113 | 112
2018-07-06 11:30 | 111 | 110
2018-07-06 12:00 | 106 | 105
2018-07-06 12:30 | 121 | 120
2018-07-06 13:00 | 118 | 117
2018-07-06 13:30 | 115 | 114
2018-07-06 14:00 | 109 | 108
2018-07-06 14:30 | 107 | 106
2018-07-06 15:00 | 105 | 105
2018-07-06 15:30 | 122 | 121
2018-07-06 16:00 | 126 | 125
2018-07-06 16:30 | 133 | 132
2018-07-06 17:00 | 153 | 152
2018-07-06 17:30 | 176 | 175
2018-07-06 18:00 | 188 | 187
2018-07-06 18:30 | 202 | 201
2018-07-06 19:00 | 209 | 208
2018-07-06 19:30 | 201 | 201
2018-07-06 20:00 | 196 | 196
2018-07-06 20:30 | 199 | 198
2018-07-06 21:00 | 194 | 193
2018-07-06 21:30 | 197 | 197
2018-07-06 22:00 | 191 | 190
2018-07-06 22:30 | 181 | 180
2018-07-06 23:00 | 172 | 170
2018-07-06 23:30 | 161 | 160
2018-07-07 | 153 | 152
2018-07-07 00:30 | 145 | 144
2018-07-07 01:00 | 139 | 137
2018-07-07 01:30 | 135 | 134
2018-07-07 02:00 | 131 | 129
2018-07-07 02:30 | 128 | 127
2018-07-07 03:00 | 129 | 127
2018-07-07 03:30 | 128 | 127
2018-07-07 04:00 | 128 | 126
2018-07-07 04:30 | 130 | 129
2018-07-07 05:00 | 132 | 130
2018-07-07 05:30 | 134 | 133
2018-07-07 06:00 | 137 | 135
2018-07-07 06:30 | 143 | 142
2018-07-07 07:00 | 131 | 130
2018-07-07 07:30 | 96 | 95
2018-07-07 08:00 | 100 | 98
2018-07-07 08:30 | 125 | 124
2018-07-07 09:00 | 125 | 124
2018-07-07 09:30 | 131 | 131
2018-07-07 10:00 | 130 | 129
2018-07-07 10:30 | 123 | 122
2018-07-07 11:00 | 117 | 116
2018-07-07 11:30 | 113 | 112
2018-07-07 12:00 | 112 | 111
2018-07-07 12:30 | 104 | 103
2018-07-07 13:00 | 101 | 100
2018-07-07 13:30 | 102 | 101
2018-07-07 14:00 | 108 | 107
2018-07-07 14:30 | 112 | 111
2018-07-07 15:00 | 113 | 112
2018-07-07 15:30 | 127 | 126
2018-07-07 16:00 | 130 | 129
2018-07-07 16:30 | 152 | 151
2018-07-07 17:00 | 158 | 157
2018-07-07 17:30 | 179 | 178
2018-07-07 18:00 | 189 | 188
2018-07-07 18:30 | 204 | 203
2018-07-07 19:00 | 204 | 203
2018-07-07 19:30 | 196 | 195
2018-07-07 20:00 | 195 | 194
2018-07-07 20:30 | 191 | 190
2018-07-07 21:00 | 184 | 183
2018-07-07 21:30 | 178 | 177
2018-07-07 22:00 | 177 | 176
2018-07-07 22:30 | 160 | 159
2018-07-07 23:00 | 158 | 156
2018-07-07 23:30 | 153 | 152
2018-07-08 | 153 | 151
2018-07-08 00:30 | 150 | 149
2018-07-08 01:00 | 146 | 145
2018-07-08 01:30 | 141 | 140
2018-07-08 02:00 | 138 | 136
2018-07-08 02:30 | 134 | 133
2018-07-08 03:00 | 129 | 128
2018-07-08 03:30 | 128 | 127
2018-07-08 04:00 | 127 | 126
2018-07-08 04:30 | 126 | 125
2018-07-08 05:00 | 125 | 124
2018-07-08 05:30 | 127 | 126
2018-07-08 06:00 | 128 | 127
2018-07-08 06:30 | 125 | 124
2018-07-08 07:00 | 110 | 109
2018-07-08 07:30 | 113 | 112
2018-07-08 08:00 | 106 | 105
2018-07-08 08:30 | 95 | 93
2018-07-08 09:00 | 91 | 89
2018-07-08 09:30 | 100 | 99
2018-07-08 10:00 | 100 | 99
2018-07-08 10:30 | 97 | 96
2018-07-08 11:00 | 95 | 94
2018-07-08 11:30 | 89 | 88
2018-07-08 12:00 | 81 | 78
2018-07-08 12:30 | 73 | 69
2018-07-08 13:00 | 77 | 74
2018-07-08 13:30 | 84 | 82
2018-07-08 14:00 | 80 | 76
2018-07-08 14:30 | 80 | 77
2018-07-08 15:00 | 82 | 79
2018-07-08 15:30 | 89 | 88
2018-07-08 16:00 | 97 | 95
2018-07-08 16:30 | 111 | 110
2018-07-08 17:00 | 137 | 136
2018-07-08 17:30 | 176 | 175
2018-07-08 18:00 | 207 | 207
2018-07-08 18:30 | 226 | 226
2018-07-08 19:00 | 230 | 229
2018-07-08 19:30 | 220 | 220
2018-07-08 20:00 | 208 | 207
2018-07-08 20:30 | 195 | 194
2018-07-08 21:00 | 189 | 188
2018-07-08 21:30 | 177 | 176
2018-07-08 22:00 | 167 | 166
2018-07-08 22:30 | 161 | 161
2018-07-08 23:00 | 159 | 158
2018-07-08 23:30 | 152 | 151
2018-07-09 | 145 | 145
2018-07-09 00:30 | 136 | 135
2018-07-09 01:00 | 130 | 129
2018-07-09 01:30 | 127 | 126
2018-07-09 02:00 | 125 | 124
2018-07-09 02:30 | 125 | 124
2018-07-09 03:00 | 123 | 122
2018-07-09 03:30 | 125 | 124
2018-07-09 04:00 | 126 | 125
2018-07-09 04:30 | 127 | 126
2018-07-09 05:00 | 130 | 129
2018-07-09 05:30 | 136 | 135
2018-07-09 06:00 | 142 | 141
2018-07-09 06:30 | 146 | 145
2018-07-09 07:00 | 153 | 152
2018-07-09 07:30 | 152 | 151
2018-07-09 08:00 | 134 | 133
2018-07-09 08:30 | 121 | 120
2018-07-09 09:00 | 99 | 98
2018-07-09 09:30 | 105 | 104
2018-07-09 10:00 | 104 | 103
2018-07-09 10:30 | 100 | 99
2018-07-09 11:00 | 94 | 93
2018-07-09 11:30 | 87 | 85
2018-07-09 12:00 | 83 | 81
2018-07-09 12:30 | 70 | 67
2018-07-09 13:00 | 43 | 36
2018-07-09 13:30 | 39 | 33
2018-07-09 14:00 | 44 | 36
2018-07-09 14:30 | 55 | 49
2018-07-09 15:00 | 58 | 53
2018-07-09 15:30 | 52 | 45
2018-07-09 16:00 | 42 | 34
2018-07-09 16:30 | 39 | 31
2018-07-09 17:00 | 34 | 27
2018-07-09 17:30 | 61 | 58
2018-07-09 18:00 | 81 | 80
2018-07-09 18:30 | 98 | 97
2018-07-09 19:00 | 105 | 104
2018-07-09 19:30 | 99 | 98
2018-07-09 20:00 | 87 | 86
2018-07-09 20:30 | 88 | 87
2018-07-09 21:00 | 82 | 81
2018-07-09 21:30 | 77 | 76
2018-07-09 22:00 | 75 | 73
2018-07-09 22:30 | 65 | 62
2018-07-09 23:00 | 53 | 47
2018-07-09 23:30 | 44 | 36
2018-07-10 | 69 | 67
2018-07-10 00:30 | 96 | 94
2018-07-10 01:00 | 135 | 134
2018-07-10 01:30 | 131 | 130
2018-07-10 02:00 | 127 | 126
2018-07-10 02:30 | 125 | 124
2018-07-10 03:00 | 125 | 124
2018-07-10 03:30 | 125 | 124
2018-07-10 04:00 | 125 | 124
2018-07-10 04:30 | 127 | 126
2018-07-10 05:00 | 135 | 134
2018-07-10 05:30 | 141 | 140
2018-07-10 06:00 | 152 | 151
2018-07-10 06:30 | 164 | 163
2018-07-10 07:00 | 161 | 160
2018-07-10 07:30 | 159 | 158
2018-07-10 08:00 | 143 | 143
2018-07-10 08:30 | 128 | 127
2018-07-10 09:00 | 120 | 119
2018-07-10 09:30 | 121 | 121
2018-07-10 10:00 | 117 | 116
2018-07-10 10:30 | 107 | 106
2018-07-10 11:00 | 98 | 97
2018-07-10 11:30 | 100 | 99
2018-07-10 12:00 | 93 | 92
2018-07-10 12:30 | 93 | 92
2018-07-10 13:00 | 92 | 90
2018-07-10 13:30 | 93 | 92
2018-07-10 14:00 | 93 | 92
2018-07-10 14:30 | 96 | 95
2018-07-10 15:00 | 101 | 100
2018-07-10 15:30 | 110 | 109
2018-07-10 16:00 | 120 | 119
2018-07-10 16:30 | 132 | 132
2018-07-10 17:00 | 154 | 154
2018-07-10 17:30 | 188 | 188
2018-07-10 18:00 | 209 | 208
2018-07-10 18:30 | 216 | 215
2018-07-10 19:00 | 231 | 231
2018-07-10 19:30 | 226 | 226
2018-07-10 20:00 | 216 | 216
2018-07-10 20:30 | 203 | 202
2018-07-10 21:00 | 185 | 184
2018-07-10 21:30 | 186 | 185
2018-07-10 22:00 | 174 | 173
2018-07-10 22:30 | 171 | 170
2018-07-10 23:00 | 163 | 162
2018-07-10 23:30 | 154 | 153
2018-07-11 | 148 | 147
2018-07-11 00:30 | 140 | 139
2018-07-11 01:00 | 136 | 135
2018-07-11 01:30 | 128 | 127
2018-07-11 02:00 | 128 | 127
2018-07-11 02:30 | 128 | 127
2018-07-11 03:00 | 128 | 127
2018-07-11 03:30 | 124 | 123
2018-07-11 04:00 | 124 | 123
2018-07-11 04:30 | 126 | 126
2018-07-11 05:00 | 130 | 129
2018-07-11 05:30 | 136 | 135
2018-07-11 06:00 | 146 | 145
2018-07-11 06:30 | 158 | 157
2018-07-11 07:00 | 165 | 164
2018-07-11 07:30 | 168 | 167
2018-07-11 08:00 | 154 | 154
2018-07-11 08:30 | 138 | 138
2018-07-11 09:00 | 132 | 131
2018-07-11 09:30 | 122 | 121
2018-07-11 10:00 | 112 | 111
2018-07-11 10:30 | 117 | 117
2018-07-11 11:00 | 115 | 115
2018-07-11 11:30 | 94 | 93
2018-07-11 12:00 | 96 | 94
2018-07-11 12:30 | 94 | 93
2018-07-11 13:00 | 96 | 94
2018-07-11 13:30 | 99 | 98
2018-07-11 14:00 | 97 | 96
2018-07-11 14:30 | 91 | 89
2018-07-11 15:00 | 102 | 101
2018-07-11 15:30 | 104 | 103
2018-07-11 16:00 | 115 | 114
2018-07-11 16:30 | 131 | 130
2018-07-11 17:00 | 151 | 151
2018-07-11 17:30 | 144 | 143
2018-07-11 18:00 | 134 | 133
2018-07-11 18:30 | 152 | 151
2018-07-11 19:00 | 158 | 158
2018-07-11 19:30 | 150 | 149
2018-07-11 20:00 | 140 | 140
2018-07-11 20:30 | 128 | 127
2018-07-11 21:00 | 115 | 114
2018-07-11 21:30 | 141 | 140
2018-07-11 22:00 | 171 | 170
2018-07-11 22:30 | 164 | 163
2018-07-11 23:00 | 157 | 156
2018-07-11 23:30 | 147 | 146
2018-07-12 | 140 | 139
2018-07-12 00:30 | 147 | 146
2018-07-12 01:00 | 143 | 142
2018-07-12 01:30 | 138 | 137
2018-07-12 02:00 | 133 | 133
2018-07-12 02:30 | 131 | 130
2018-07-12 03:00 | 130 | 129
2018-07-12 03:30 | 132 | 131
2018-07-12 04:00 | 133 | 132
2018-07-12 04:30 | 134 | 133
2018-07-12 05:00 | 138 | 137
2018-07-12 05:30 | 145 | 144
2018-07-12 06:00 | 153 | 152
2018-07-12 06:30 | 163 | 162
2018-07-12 07:00 | 155 | 154
2018-07-12 07:30 | 172 | 171
2018-07-12 08:00 | 166 | 165
2018-07-12 08:30 | 154 | 154
2018-07-12 09:00 | 141 | 141
2018-07-12 09:30 | 120 | 120
2018-07-12 10:00 | 101 | 100
2018-07-12 10:30 | 96 | 95
2018-07-12 11:00 | 89 | 88
2018-07-12 11:30 | 87 | 86
2018-07-12 12:00 | 84 | 83
2018-07-12 12:30 | 69 | 66
2018-07-12 13:00 | 44 | 38
2018-07-12 13:30 | 47 | 42
2018-07-12 14:00 | 52 | 48
2018-07-12 14:30 | 48 | 44
2018-07-12 15:00 | 45 | 43
2018-07-12 15:30 | 40 | 34
2018-07-12 16:00 | 38 | 33
2018-07-12 16:30 | 54 | 52
2018-07-12 17:00 | 85 | 84
2018-07-12 17:30 | 97 | 95
2018-07-12 18:00 | 97 | 95
2018-07-12 18:30 | 113 | 112
2018-07-12 19:00 | 122 | 121
2018-07-12 19:30 | 114 | 113
2018-07-12 20:00 | 104 | 102
2018-07-12 20:30 | 93 | 92
2018-07-12 21:00 | 84 | 82
2018-07-12 21:30 | 71 | 69
2018-07-12 22:00 | 59 | 57
2018-07-12 22:30 | 47 | 44
2018-07-12 23:00 | 36 | 31
2018-07-12 23:30 | 40 | 36
2018-07-13 | 39 | 34
2018-07-13 00:30 | 65 | 63
2018-07-13 01:00 | 87 | 86
2018-07-13 01:30 | 129 | 128
2018-07-13 02:00 | 132 | 130
2018-07-13 02:30 | 132 | 130
2018-07-13 03:00 | 128 | 126
2018-07-13 03:30 | 131 | 129
2018-07-13 04:00 | 127 | 126
2018-07-13 04:30 | 128 | 126
2018-07-13 05:00 | 135 | 134
2018-07-13 05:30 | 142 | 140
2018-07-13 06:00 | 148 | 147
2018-07-13 06:30 | 159 | 158
2018-07-13 07:00 | 157 | 156
2018-07-13 07:30 | 163 | 162
2018-07-13 08:00 | 148 | 147
2018-07-13 08:30 | 127 | 126
2018-07-13 09:00 | 111 | 110
2018-07-13 09:30 | 96 | 94
2018-07-13 10:00 | 84 | 83
2018-07-13 10:30 | 81 | 80
2018-07-13 11:00 | 70 | 69
2018-07-13 11:30 | 56 | 52
2018-07-13 12:00 | 65 | 63
2018-07-13 12:30 | 66 | 63
2018-07-13 13:00 | 66 | 63
2018-07-13 13:30 | 65 | 61
2018-07-13 14:00 | 37 | 30
2018-07-13 14:30 | 51 | 45
2018-07-13 15:00 | 68 | 66
2018-07-13 15:30 | 81 | 79
2018-07-13 16:00 | 97 | 95
2018-07-13 16:30 | 119 | 118
2018-07-13 17:00 | 112 | 111
2018-07-13 17:30 | 100 | 99
2018-07-13 18:00 | 97 | 96
2018-07-13 18:30 | 101 | 99
2018-07-13 19:00 | 106 | 105
2018-07-13 19:30 | 118 | 117
2018-07-13 20:00 | 129 | 128
2018-07-13 20:30 | 123 | 122
2018-07-13 21:00 | 101 | 100
2018-07-13 21:30 | 100 | 99
2018-07-13 22:00 | 92 | 90
2018-07-13 22:30 | 82 | 81
2018-07-13 23:00 | 64 | 62
2018-07-13 23:30 | 106 | 105
2018-07-14 | 140 | 140
2018-07-14 00:30 | 142 | 142
2018-07-14 01:00 | 138 | 137
2018-07-14 01:30 | 134 | 133
2018-07-14 02:00 | 131 | 130
2018-07-14 02:30 | 128 | 127
2018-07-14 03:00 | 127 | 126
2018-07-14 03:30 | 125 | 124
2018-07-14 04:00 | 128 | 127
2018-07-14 04:30 | 127 | 126
2018-07-14 05:00 | 129 | 128
2018-07-14 05:30 | 134 | 133
2018-07-14 06:00 | 136 | 135
2018-07-14 06:30 | 140 | 139
2018-07-14 07:00 | 137 | 136
2018-07-14 07:30 | 139 | 138
2018-07-14 08:00 | 124 | 123
2018-07-14 08:30 | 106 | 105
2018-07-14 09:00 | 92 | 91
2018-07-14 09:30 | 83 | 82
2018-07-14 10:00 | 73 | 71
2018-07-14 10:30 | 64 | 62
2018-07-14 11:00 | 59 | 56
2018-07-14 11:30 | 55 | 51
2018-07-14 12:00 | 52 | 47
2018-07-14 12:30 | 48 | 42
2018-07-14 13:00 | 47 | 39
2018-07-14 13:30 | 48 | 40
2018-07-14 14:00 | 47 | 40
2018-07-14 14:30 | 50 | 45
2018-07-14 15:00 | 51 | 48
2018-07-14 15:30 | 60 | 57
2018-07-14 16:00 | 79 | 77
2018-07-14 16:30 | 99 | 97
2018-07-14 17:00 | 126 | 125
2018-07-14 17:30 | 163 | 162
2018-07-14 18:00 | 191 | 190
2018-07-14 18:30 | 208 | 207
2018-07-14 19:00 | 210 | 209
2018-07-14 19:30 | 206 | 205
2018-07-14 20:00 | 201 | 200
2018-07-14 20:30 | 187 | 186
2018-07-14 21:00 | 181 | 180
2018-07-14 21:30 | 173 | 171
2018-07-14 22:00 | 167 | 165
2018-07-14 22:30 | 159 | 158
2018-07-14 23:00 | 152 | 151
2018-07-14 23:30 | 154 | 153
2018-07-15 | 150 | 150
2018-07-15 00:30 | 145 | 144
2018-07-15 01:00 | 141 | 140
2018-07-15 01:30 | 136 | 135
2018-07-15 02:00 | 131 | 130
2018-07-15 02:30 | 128 | 127
2018-07-15 03:00 | 125 | 124
2018-07-15 03:30 | 124 | 123
2018-07-15 04:00 | 123 | 122
2018-07-15 04:30 | 119 | 118
2018-07-15 05:00 | 123 | 121
2018-07-15 05:30 | 124 | 123
2018-07-15 06:00 | 115 | 114
2018-07-15 06:30 | 131 | 130
2018-07-15 07:00 | 124 | 123
2018-07-15 07:30 | 124 | 123
2018-07-15 08:00 | 103 | 101
2018-07-15 08:30 | 92 | 91
2018-07-15 09:00 | 81 | 79
2018-07-15 09:30 | 70 | 68
2018-07-15 10:00 | 42 | 39
2018-07-15 10:30 | 22 | 18
2018-07-15 11:00 | 18 | 12
2018-07-15 11:30 | 10 | 6
2018-07-15 12:00 | 13 | 6
2018-07-15 12:30 | 16 | 9
2018-07-15 13:00 | 16 | 8
2018-07-15 13:30 | 14 | 6
2018-07-15 14:00 | 29 | 24
2018-07-15 14:30 | 48 | 45
2018-07-15 15:00 | 58 | 56
2018-07-15 15:30 | 71 | 69
2018-07-15 16:00 | 90 | 88
2018-07-15 16:30 | 112 | 110
2018-07-15 17:00 | 134 | 132
2018-07-15 17:30 | 172 | 170
2018-07-15 18:00 | 202 | 201
2018-07-15 18:30 | 199 | 197
2018-07-15 19:00 | 211 | 209
2018-07-15 19:30 | 216 | 215
2018-07-15 20:00 | 203 | 202
2018-07-15 20:30 | 195 | 194
2018-07-15 21:00 | 185 | 184
2018-07-15 21:30 | 177 | 175
2018-07-15 22:00 | 167 | 166
2018-07-15 22:30 | 155 | 154
2018-07-15 23:00 | 143 | 141
2018-07-15 23:30 | 144 | 142
2018-07-16 | 142 | 140
2018-07-16 00:30 | 141 | 139
2018-07-16 01:00 | 136 | 135
2018-07-16 01:30 | 131 | 130
2018-07-16 02:00 | 129 | 127
2018-07-16 02:30 | 128 | 127
2018-07-16 03:00 | 127 | 126
2018-07-16 03:30 | 125 | 124
2018-07-16 04:00 | 125 | 124
2018-07-16 04:30 | 124 | 123
2018-07-16 05:00 | 129 | 127
2018-07-16 05:30 | 140 | 139
2018-07-16 06:00 | 149 | 148
2018-07-16 06:30 | 160 | 159
2018-07-16 07:00 | 164 | 163
2018-07-16 07:30 | 179 | 178
2018-07-16 08:00 | 160 | 159
2018-07-16 08:30 | 138 | 137
2018-07-16 09:00 | 112 | 110
2018-07-16 09:30 | 94 | 93
2018-07-16 10:00 | 64 | 60
2018-07-16 10:30 | 42 | 35
2018-07-16 11:00 | 39 | 32
2018-07-16 11:30 | 36 | 30
2018-07-16 12:00 | 37 | 31
2018-07-16 12:30 | 24 | 19
2018-07-16 13:00 | 1 | 1
2018-07-16 13:30 | 0 | 0
2018-07-16 14:00 | 3 | 2
2018-07-16 14:30 | 26 | 21
2018-07-16 15:00 | 54 | 49
2018-07-16 15:30 | 68 | 65
2018-07-16 16:00 | 59 | 54
2018-07-16 16:30 | 37 | 27
2018-07-16 17:00 | 51 | 45
2018-07-16 17:30 | 77 | 75
2018-07-16 18:00 | 103 | 102
2018-07-16 18:30 | 121 | 120
2018-07-16 19:00 | 128 | 127
2018-07-16 19:30 | 122 | 121
2018-07-16 20:00 | 113 | 112
2018-07-16 20:30 | 98 | 97
2018-07-16 21:00 | 89 | 88
2018-07-16 21:30 | 80 | 78
2018-07-16 22:00 | 66 | 64
2018-07-16 22:30 | 53 | 49
2018-07-16 23:00 | 44 | 36
2018-07-16 23:30 | 46 | 40
2018-07-17 | 76 | 75
2018-07-17 00:30 | 102 | 100
2018-07-17 01:00 | 143 | 142
2018-07-17 01:30 | 142 | 140
2018-07-17 02:00 | 139 | 138
2018-07-17 02:30 | 129 | 127
2018-07-17 03:00 | 135 | 134
2018-07-17 03:30 | 135 | 134
2018-07-17 04:00 | 136 | 134
2018-07-17 04:30 | 137 | 136
2018-07-17 05:00 | 138 | 137
2018-07-17 05:30 | 147 | 145
2018-07-17 06:00 | 160 | 159
2018-07-17 06:30 | 175 | 174
2018-07-17 07:00 | 183 | 182
2018-07-17 07:30 | 187 | 186
2018-07-17 08:00 | 171 | 171
2018-07-17 08:30 | 142 | 141
2018-07-17 09:00 | 117 | 116
2018-07-17 09:30 | 93 | 92
2018-07-17 10:00 | 86 | 85
2018-07-17 10:30 | 81 | 80
2018-07-17 11:00 | 74 | 72
2018-07-17 11:30 | 77 | 75
2018-07-17 12:00 | 75 | 73
2018-07-17 12:30 | 77 | 76
2018-07-17 13:00 | 86 | 84
2018-07-17 13:30 | 81 | 79
2018-07-17 14:00 | 83 | 81
2018-07-17 14:30 | 101 | 100
2018-07-17 15:00 | 102 | 100
2018-07-17 15:30 | 104 | 103
2018-07-17 16:00 | 120 | 119
2018-07-17 16:30 | 145 | 144
2018-07-17 17:00 | 162 | 161
2018-07-17 17:30 | 176 | 175
2018-07-17 18:00 | 204 | 203
2018-07-17 18:30 | 228 | 227
2018-07-17 19:00 | 231 | 230
2018-07-17 19:30 | 230 | 229
2018-07-17 20:00 | 220 | 219
2018-07-17 20:30 | 206 | 205
2018-07-17 21:00 | 195 | 194
2018-07-17 21:30 | 196 | 195
2018-07-17 22:00 | 189 | 188
2018-07-17 22:30 | 172 | 170
2018-07-17 23:00 | 157 | 155
2018-07-17 23:30 | 160 | 159
2018-07-18 | 157 | 156
2018-07-18 00:30 | 149 | 148
2018-07-18 01:00 | 144 | 142
2018-07-18 01:30 | 140 | 139
2018-07-18 02:00 | 137 | 136
2018-07-18 02:30 | 136 | 135
2018-07-18 03:00 | 134 | 132
2018-07-18 03:30 | 132 | 130
2018-07-18 04:00 | 130 | 129
2018-07-18 04:30 | 132 | 130
2018-07-18 05:00 | 133 | 132
2018-07-18 05:30 | 141 | 139
2018-07-18 06:00 | 150 | 148
2018-07-18 06:30 | 144 | 143
2018-07-18 07:00 | 153 | 151
2018-07-18 07:30 | 159 | 158
2018-07-18 08:00 | 156 | 155
2018-07-18 08:30 | 138 | 137
2018-07-18 09:00 | 124 | 122
2018-07-18 09:30 | 145 | 144
2018-07-18 10:00 | 153 | 152
2018-07-18 10:30 | 138 | 137
2018-07-18 11:00 | 119 | 118
2018-07-18 11:30 | 94 | 93
2018-07-18 12:00 | 92 | 91
2018-07-18 12:30 | 91 | 90
2018-07-18 13:00 | 94 | 93
2018-07-18 13:30 | 92 | 91
2018-07-18 14:00 | 94 | 92
2018-07-18 14:30 | 102 | 101
2018-07-18 15:00 | 105 | 104
2018-07-18 15:30 | 105 | 104
2018-07-18 16:00 | 121 | 120
2018-07-18 16:30 | 115 | 114
2018-07-18 17:00 | 128 | 127
2018-07-18 17:30 | 101 | 100
2018-07-18 18:00 | 115 | 114
2018-07-18 18:30 | 131 | 130
2018-07-18 19:00 | 140 | 139
2018-07-18 19:30 | 134 | 133
2018-07-18 20:00 | 125 | 124
2018-07-18 20:30 | 132 | 131
2018-07-18 21:00 | 125 | 124
2018-07-18 21:30 | 114 | 113
2018-07-18 22:00 | 101 | 100
2018-07-18 22:30 | 118 | 117
2018-07-18 23:00 | 110 | 109
2018-07-18 23:30 | 146 | 145
2018-07-19 | 145 | 144
2018-07-19 00:30 | 140 | 139
2018-07-19 01:00 | 134 | 133
2018-07-19 01:30 | 127 | 126
2018-07-19 02:00 | 126 | 125
2018-07-19 02:30 | 125 | 124
2018-07-19 03:00 | 122 | 121
2018-07-19 03:30 | 121 | 120
2018-07-19 04:00 | 123 | 121
2018-07-19 04:30 | 127 | 126
2018-07-19 05:00 | 133 | 132
2018-07-19 05:30 | 143 | 142
2018-07-19 06:00 | 153 | 152
2018-07-19 06:30 | 154 | 153
2018-07-19 07:00 | 150 | 148
2018-07-19 07:30 | 156 | 155
2018-07-19 08:00 | 147 | 146
2018-07-19 08:30 | 122 | 121
2018-07-19 09:00 | 145 | 144
2018-07-19 09:30 | 144 | 143
2018-07-19 10:00 | 146 | 145
2018-07-19 10:30 | 131 | 130
2018-07-19 11:00 | 106 | 105
2018-07-19 11:30 | 103 | 102
2018-07-19 12:00 | 101 | 100
2018-07-19 12:30 | 100 | 99
2018-07-19 13:00 | 96 | 94
2018-07-19 13:30 | 95 | 93
2018-07-19 14:00 | 106 | 105
2018-07-19 14:30 | 110 | 109
2018-07-19 15:00 | 113 | 111
2018-07-19 15:30 | 121 | 119
2018-07-19 16:00 | 128 | 126
2018-07-19 16:30 | 122 | 121
2018-07-19 17:00 | 124 | 123
2018-07-19 17:30 | 96 | 94
2018-07-19 18:00 | 109 | 107
2018-07-19 18:30 | 122 | 120
2018-07-19 19:00 | 131 | 129
2018-07-19 19:30 | 126 | 123
2018-07-19 20:00 | 118 | 116
2018-07-19 20:30 | 103 | 101
2018-07-19 21:00 | 92 | 90
2018-07-19 21:30 | 84 | 83
2018-07-19 22:00 | 71 | 70
2018-07-19 22:30 | 93 | 92
2018-07-19 23:00 | 106 | 105
2018-07-19 23:30 | 147 | 146
2018-07-20 | 145 | 145
2018-07-20 00:30 | 141 | 140
2018-07-20 01:00 | 132 | 131
2018-07-20 01:30 | 127 | 126
2018-07-20 02:00 | 126 | 125
2018-07-20 02:30 | 122 | 121
2018-07-20 03:00 | 120 | 119
2018-07-20 03:30 | 123 | 122
2018-07-20 04:00 | 126 | 125
2018-07-20 04:30 | 125 | 124
2018-07-20 05:00 | 127 | 126
2018-07-20 05:30 | 119 | 118
2018-07-20 06:00 | 135 | 134
2018-07-20 06:30 | 137 | 136
2018-07-20 07:00 | 131 | 130
2018-07-20 07:30 | 130 | 129
2018-07-20 08:00 | 113 | 111
2018-07-20 08:30 | 94 | 92
2018-07-20 09:00 | 82 | 80
2018-07-20 09:30 | 96 | 94
2018-07-20 10:00 | 94 | 92
2018-07-20 10:30 | 87 | 85
2018-07-20 11:00 | 74 | 71
2018-07-20 11:30 | 70 | 68
2018-07-20 12:00 | 62 | 57
2018-07-20 12:30 | 58 | 51
2018-07-20 13:00 | 64 | 61
2018-07-20 13:30 | 70 | 68
2018-07-20 14:00 | 72 | 70
2018-07-20 14:30 | 93 | 91
2018-07-20 15:00 | 110 | 109
2018-07-20 15:30 | 123 | 122
2018-07-20 16:00 | 138 | 137
2018-07-20 16:30 | 134 | 133
2018-07-20 17:00 | 135 | 134
2018-07-20 17:30 | 93 | 92
2018-07-20 18:00 | 99 | 98
2018-07-20 18:30 | 112 | 111
2018-07-20 19:00 | 116 | 115
2018-07-20 19:30 | 110 | 109
2018-07-20 20:00 | 102 | 101
2018-07-20 20:30 | 92 | 90
2018-07-20 21:00 | 85 | 84
2018-07-20 21:30 | 97 | 96
2018-07-20 22:00 | 95 | 93
2018-07-20 22:30 | 124 | 123
2018-07-20 23:00 | 119 | 118
2018-07-20 23:30 | 153 | 153
2018-07-21 | 154 | 154
2018-07-21 00:30 | 146 | 145
2018-07-21 01:00 | 141 | 141
2018-07-21 01:30 | 136 | 135
2018-07-21 02:00 | 132 | 131
2018-07-21 02:30 | 130 | 129
2018-07-21 03:00 | 129 | 128
2018-07-21 03:30 | 128 | 127
2018-07-21 04:00 | 130 | 129
2018-07-21 04:30 | 130 | 129
2018-07-21 05:00 | 130 | 129
2018-07-21 05:30 | 133 | 132
2018-07-21 06:00 | 136 | 135
2018-07-21 06:30 | 119 | 118
2018-07-21 07:00 | 107 | 105
2018-07-21 07:30 | 103 | 102
2018-07-21 08:00 | 82 | 81
2018-07-21 08:30 | 67 | 64
2018-07-21 09:00 | 73 | 69
2018-07-21 09:30 | 66 | 60
2018-07-21 10:00 | 57 | 49
2018-07-21 10:30 | 51 | 43
2018-07-21 11:00 | 39 | 35
2018-07-21 11:30 | 36 | 29
2018-07-21 12:00 | 35 | 28
2018-07-21 12:30 | 36 | 28
2018-07-21 13:00 | 34 | 26
2018-07-21 13:30 | 30 | 23
2018-07-21 14:00 | 30 | 25
2018-07-21 14:30 | 34 | 32
2018-07-21 15:00 | 51 | 43
2018-07-21 15:30 | 58 | 52
2018-07-21 16:00 | 72 | 69
2018-07-21 16:30 | 93 | 92
2018-07-21 17:00 | 122 | 121
2018-07-21 17:30 | 155 | 155
2018-07-21 18:00 | 181 | 181
2018-07-21 18:30 | 180 | 179
2018-07-21 19:00 | 180 | 178
2018-07-21 19:30 | 171 | 170
2018-07-21 20:00 | 163 | 162
2018-07-21 20:30 | 153 | 152
2018-07-21 21:00 | 148 | 147
2018-07-21 21:30 | 141 | 140
2018-07-21 22:00 | 136 | 136
2018-07-21 22:30 | 128 | 127
2018-07-21 23:00 | 117 | 116
2018-07-21 23:30 | 121 | 120
2018-07-22 | 138 | 137
2018-07-22 00:30 | 137 | 136
2018-07-22 01:00 | 131 | 131
2018-07-22 01:30 | 129 | 128
2018-07-22 02:00 | 125 | 124
2018-07-22 02:30 | 123 | 122
2018-07-22 03:00 | 120 | 119
2018-07-22 03:30 | 114 | 113
2018-07-22 04:00 | 120 | 119
2018-07-22 04:30 | 120 | 119
2018-07-22 05:00 | 120 | 119
2018-07-22 05:30 | 124 | 123
2018-07-22 06:00 | 124 | 123
2018-07-22 06:30 | 106 | 105
2018-07-22 07:00 | 94 | 93
2018-07-22 07:30 | 96 | 95
2018-07-22 08:00 | 87 | 85
2018-07-22 08:30 | 91 | 90
2018-07-22 09:00 | 91 | 90
2018-07-22 09:30 | 73 | 70
2018-07-22 10:00 | 65 | 58
2018-07-22 10:30 | 64 | 56
2018-07-22 11:00 | 60 | 52
2018-07-22 11:30 | 56 | 48
2018-07-22 12:00 | 51 | 44
2018-07-22 12:30 | 43 | 40
2018-07-22 13:00 | 56 | 48
2018-07-22 13:30 | 57 | 49
2018-07-22 14:00 | 59 | 51
2018-07-22 14:30 | 59 | 51
2018-07-22 15:00 | 71 | 66
2018-07-22 15:30 | 76 | 72
2018-07-22 16:00 | 89 | 86
2018-07-22 16:30 | 109 | 107
2018-07-22 17:00 | 137 | 136
2018-07-22 17:30 | 143 | 142
2018-07-22 18:00 | 164 | 164
2018-07-22 18:30 | 177 | 177
2018-07-22 19:00 | 190 | 189
2018-07-22 19:30 | 183 | 182
2018-07-22 20:00 | 173 | 173
2018-07-22 20:30 | 163 | 162
2018-07-22 21:00 | 156 | 155
2018-07-22 21:30 | 160 | 159
2018-07-22 22:00 | 159 | 159
2018-07-22 22:30 | 160 | 160
2018-07-22 23:00 | 154 | 153
2018-07-22 23:30 | 145 | 144
2018-07-23 | 137 | 136
2018-07-23 00:30 | 130 | 129
2018-07-23 01:00 | 125 | 124
2018-07-23 01:30 | 122 | 120
2018-07-23 02:00 | 120 | 119
2018-07-23 02:30 | 121 | 119
2018-07-23 03:00 | 121 | 120
2018-07-23 03:30 | 121 | 120
2018-07-23 04:00 | 121 | 120
2018-07-23 04:30 | 124 | 123
2018-07-23 05:00 | 126 | 125
2018-07-23 05:30 | 130 | 129
2018-07-23 06:00 | 140 | 139
2018-07-23 06:30 | 131 | 130
2018-07-23 07:00 | 137 | 136
2018-07-23 07:30 | 146 | 145
2018-07-23 08:00 | 136 | 136
2018-07-23 08:30 | 139 | 138
2018-07-23 09:00 | 121 | 121
2018-07-23 09:30 | 102 | 101
2018-07-23 10:00 | 92 | 91
2018-07-23 10:30 | 90 | 89
2018-07-23 11:00 | 85 | 83
2018-07-23 11:30 | 84 | 82
2018-07-23 12:00 | 81 | 79
2018-07-23 12:30 | 87 | 85
2018-07-23 13:00 | 89 | 87
2018-07-23 13:30 | 96 | 94
2018-07-23 14:00 | 89 | 87
2018-07-23 14:30 | 91 | 90
2018-07-23 15:00 | 98 | 97
2018-07-23 15:30 | 113 | 112
2018-07-23 16:00 | 138 | 138
2018-07-23 16:30 | 157 | 156
2018-07-23 17:00 | 168 | 167
2018-07-23 17:30 | 164 | 163
2018-07-23 18:00 | 189 | 188
2018-07-23 18:30 | 209 | 209
2018-07-23 19:00 | 217 | 217
2018-07-23 19:30 | 209 | 208
2018-07-23 20:00 | 197 | 197
2018-07-23 20:30 | 184 | 184
2018-07-23 21:00 | 176 | 175
2018-07-23 21:30 | 163 | 162
2018-07-23 22:00 | 153 | 152
2018-07-23 22:30 | 153 | 153
2018-07-23 23:00 | 159 | 158
2018-07-23 23:30 | 158 | 157
2018-07-24 | 144 | 143
2018-07-24 00:30 | 137 | 137
2018-07-24 01:00 | 138 | 137
2018-07-24 01:30 | 137 | 136
2018-07-24 02:00 | 134 | 133
2018-07-24 02:30 | 133 | 133
2018-07-24 03:00 | 132 | 131
2018-07-24 03:30 | 131 | 130
2018-07-24 04:00 | 130 | 130
2018-07-24 04:30 | 133 | 132
2018-07-24 05:00 | 136 | 135
2018-07-24 05:30 | 142 | 142
2018-07-24 06:00 | 154 | 153
2018-07-24 06:30 | 146 | 145
2018-07-24 07:00 | 152 | 151
2018-07-24 07:30 | 158 | 157
2018-07-24 08:00 | 145 | 145
2018-07-24 08:30 | 125 | 124
2018-07-24 09:00 | 128 | 127
2018-07-24 09:30 | 112 | 111
2018-07-24 10:00 | 105 | 104
2018-07-24 10:30 | 102 | 100
2018-07-24 11:00 | 102 | 100
2018-07-24 11:30 | 108 | 106
2018-07-24 12:00 | 98 | 96
2018-07-24 12:30 | 91 | 88
2018-07-24 13:00 | 96 | 94
2018-07-24 13:30 | 98 | 96
2018-07-24 14:00 | 98 | 96
2018-07-24 14:30 | 108 | 106
2018-07-24 15:00 | 127 | 126
2018-07-24 15:30 | 137 | 136
2018-07-24 16:00 | 130 | 129
2018-07-24 16:30 | 153 | 152
2018-07-24 17:00 | 174 | 174
2018-07-24 17:30 | 172 | 172
2018-07-24 18:00 | 190 | 189
2018-07-24 18:30 | 209 | 208
2018-07-24 19:00 | 219 | 219
2018-07-24 19:30 | 215 | 215
2018-07-24 20:00 | 202 | 201
2018-07-24 20:30 | 203 | 202
2018-07-24 21:00 | 191 | 191
2018-07-24 21:30 | 200 | 199
2018-07-24 22:00 | 197 | 196
2018-07-24 22:30 | 182 | 181
2018-07-24 23:00 | 168 | 167
2018-07-24 23:30 | 153 | 152
2018-07-25 | 143 | 142
2018-07-25 00:30 | 137 | 137
2018-07-25 01:00 | 132 | 132
2018-07-25 01:30 | 130 | 129
2018-07-25 02:00 | 128 | 127
2018-07-25 02:30 | 126 | 125
2018-07-25 03:00 | 125 | 124
2018-07-25 03:30 | 124 | 123
2018-07-25 04:00 | 129 | 128
2018-07-25 04:30 | 136 | 135
2018-07-25 05:00 | 136 | 135
2018-07-25 05:30 | 142 | 142
2018-07-25 06:00 | 150 | 149
2018-07-25 06:30 | 140 | 139
2018-07-25 07:00 | 146 | 145
2018-07-25 07:30 | 159 | 158
2018-07-25 08:00 | 149 | 149
2018-07-25 08:30 | 128 | 128
2018-07-25 09:00 | 134 | 133
2018-07-25 09:30 | 121 | 120
2018-07-25 10:00 | 110 | 110
2018-07-25 10:30 | 97 | 96
2018-07-25 11:00 | 99 | 98
2018-07-25 11:30 | 99 | 98
2018-07-25 12:00 | 93 | 92
2018-07-25 12:30 | 90 | 89
2018-07-25 13:00 | 96 | 95
2018-07-25 13:30 | 109 | 108
2018-07-25 14:00 | 108 | 107
2018-07-25 14:30 | 113 | 113
2018-07-25 15:00 | 106 | 105
2018-07-25 15:30 | 127 | 126
2018-07-25 16:00 | 127 | 127
2018-07-25 16:30 | 116 | 115
2018-07-25 17:00 | 115 | 114
2018-07-25 17:30 | 109 | 108
2018-07-25 18:00 | 118 | 117
2018-07-25 18:30 | 131 | 130
2018-07-25 19:00 | 133 | 132
2018-07-25 19:30 | 120 | 119
2018-07-25 20:00 | 111 | 110
2018-07-25 20:30 | 101 | 100
2018-07-25 21:00 | 90 | 89
2018-07-25 21:30 | 96 | 95
2018-07-25 22:00 | 94 | 92
2018-07-25 22:30 | 82 | 80
2018-07-25 23:00 | 130 | 129
2018-07-25 23:30 | 148 | 147
2018-07-26 | 142 | 142
2018-07-26 00:30 | 137 | 136
2018-07-26 01:00 | 136 | 135
2018-07-26 01:30 | 136 | 135
2018-07-26 02:00 | 134 | 133
2018-07-26 02:30 | 134 | 133
2018-07-26 03:00 | 127 | 127
2018-07-26 03:30 | 124 | 123
2018-07-26 04:00 | 122 | 121
2018-07-26 04:30 | 126 | 125
2018-07-26 05:00 | 128 | 127
2018-07-26 05:30 | 134 | 133
2018-07-26 06:00 | 144 | 144
2018-07-26 06:30 | 161 | 161
2018-07-26 07:00 | 169 | 168
2018-07-26 07:30 | 157 | 157
2018-07-26 08:00 | 147 | 146
2018-07-26 08:30 | 128 | 128
2018-07-26 09:00 | 110 | 109
2018-07-26 09:30 | 107 | 106
2018-07-26 10:00 | 95 | 93
2018-07-26 10:30 | 87 | 84
2018-07-26 11:00 | 83 | 79
2018-07-26 11:30 | 81 | 77
2018-07-26 12:00 | 74 | 68
2018-07-26 12:30 | 71 | 64
2018-07-26 13:00 | 72 | 65
2018-07-26 13:30 | 77 | 72
2018-07-26 14:00 | 84 | 80
2018-07-26 14:30 | 92 | 89
2018-07-26 15:00 | 103 | 100
2018-07-26 15:30 | 104 | 102
2018-07-26 16:00 | 112 | 110
2018-07-26 16:30 | 130 | 129
2018-07-26 17:00 | 126 | 125
2018-07-26 17:30 | 123 | 122
2018-07-26 18:00 | 117 | 116
2018-07-26 18:30 | 137 | 136
2018-07-26 19:00 | 143 | 143
2018-07-26 19:30 | 134 | 133
2018-07-26 20:00 | 125 | 124
2018-07-26 20:30 | 129 | 128
2018-07-26 21:00 | 129 | 128
2018-07-26 21:30 | 150 | 149
2018-07-26 22:00 | 139 | 138
2018-07-26 22:30 | 128 | 127
2018-07-26 23:00 | 148 | 147
2018-07-26 23:30 | 154 | 154
2018-07-27 | 146 | 145
2018-07-27 00:30 | 142 | 141
2018-07-27 01:00 | 136 | 135
2018-07-27 01:30 | 130 | 129
2018-07-27 02:00 | 138 | 137
2018-07-27 02:30 | 140 | 139
2018-07-27 03:00 | 119 | 118
2018-07-27 03:30 | 136 | 135
2018-07-27 04:00 | 133 | 132
2018-07-27 04:30 | 138 | 138
2018-07-27 05:00 | 137 | 136
2018-07-27 05:30 | 136 | 136
2018-07-27 06:00 | 145 | 145
2018-07-27 06:30 | 145 | 144
2018-07-27 07:00 | 145 | 144
2018-07-27 07:30 | 157 | 156
2018-07-27 08:00 | 160 | 159
2018-07-27 08:30 | 148 | 148
2018-07-27 09:00 | 125 | 124
2018-07-27 09:30 | 103 | 102
2018-07-27 10:00 | 86 | 84
2018-07-27 10:30 | 83 | 80
2018-07-27 11:00 | 81 | 78
2018-07-27 11:30 | 74 | 71
2018-07-27 12:00 | 71 | 66
2018-07-27 12:30 | 62 | 54
2018-07-27 13:00 | 59 | 49
2018-07-27 13:30 | 57 | 48
2018-07-27 14:00 | 64 | 57
2018-07-27 14:30 | 85 | 82
2018-07-27 15:00 | 83 | 79
2018-07-27 15:30 | 80 | 76
2018-07-27 16:00 | 102 | 101
2018-07-27 16:30 | 111 | 110
2018-07-27 17:00 | 121 | 120
2018-07-27 17:30 | 140 | 139
2018-07-27 18:00 | 131 | 131
2018-07-27 18:30 | 138 | 137
2018-07-27 19:00 | 149 | 149
2018-07-27 19:30 | 145 | 144
2018-07-27 20:00 | 133 | 132
2018-07-27 20:30 | 124 | 123
2018-07-27 21:00 | 115 | 114
2018-07-27 21:30 | 109 | 108
2018-07-27 22:00 | 95 | 94
2018-07-27 22:30 | 116 | 115
2018-07-27 23:00 | 146 | 145
2018-07-27 23:30 | 153 | 152
2018-07-28 | 147 | 146
2018-07-28 00:30 | 141 | 140
2018-07-28 01:00 | 135 | 134
2018-07-28 01:30 | 130 | 129
2018-07-28 02:00 | 127 | 126
2018-07-28 02:30 | 125 | 124
2018-07-28 03:00 | 125 | 124
2018-07-28 03:30 | 124 | 123
2018-07-28 04:00 | 123 | 122
2018-07-28 04:30 | 137 | 136
2018-07-28 05:00 | 135 | 134
2018-07-28 05:30 | 138 | 137
2018-07-28 06:00 | 127 | 126
2018-07-28 06:30 | 127 | 126
2018-07-28 07:00 | 123 | 122
2018-07-28 07:30 | 126 | 125
2018-07-28 08:00 | 116 | 115
2018-07-28 08:30 | 95 | 94
2018-07-28 09:00 | 83 | 80
2018-07-28 09:30 | 72 | 67
2018-07-28 10:00 | 79 | 75
2018-07-28 10:30 | 74 | 69
2018-07-28 11:00 | 71 | 65
2018-07-28 11:30 | 66 | 59
2018-07-28 12:00 | 56 | 47
2018-07-28 12:30 | 41 | 39
2018-07-28 13:00 | 54 | 45
2018-07-28 13:30 | 53 | 44
2018-07-28 14:00 | 48 | 42
2018-07-28 14:30 | 46 | 41
2018-07-28 15:00 | 57 | 49
2018-07-28 15:30 | 64 | 58
2018-07-28 16:00 | 79 | 76
2018-07-28 16:30 | 81 | 78
2018-07-28 17:00 | 110 | 109
2018-07-28 17:30 | 150 | 150
2018-07-28 18:00 | 177 | 177
2018-07-28 18:30 | 194 | 194
2018-07-28 19:00 | 200 | 200
2018-07-28 19:30 | 192 | 192
2018-07-28 20:00 | 183 | 183
2018-07-28 20:30 | 173 | 172
2018-07-28 21:00 | 162 | 162
2018-07-28 21:30 | 156 | 155
2018-07-28 22:00 | 150 | 150
2018-07-28 22:30 | 156 | 156
2018-07-28 23:00 | 148 | 147
2018-07-28 23:30 | 154 | 153
2018-07-29 | 150 | 150
2018-07-29 00:30 | 144 | 143
2018-07-29 01:00 | 138 | 138
2018-07-29 01:30 | 137 | 136
2018-07-29 02:00 | 131 | 130
2018-07-29 02:30 | 130 | 130
2018-07-29 03:00 | 132 | 131
2018-07-29 03:30 | 135 | 135
2018-07-29 04:00 | 128 | 127
2018-07-29 04:30 | 127 | 126
2018-07-29 05:00 | 129 | 128
2018-07-29 05:30 | 134 | 133
2018-07-29 06:00 | 118 | 117
2018-07-29 06:30 | 120 | 119
2018-07-29 07:00 | 114 | 113
2018-07-29 07:30 | 110 | 109
2018-07-29 08:00 | 90 | 89
2018-07-29 08:30 | 76 | 73
2018-07-29 09:00 | 70 | 66
2018-07-29 09:30 | 61 | 54
2018-07-29 10:00 | 71 | 67
2018-07-29 10:30 | 68 | 64
2018-07-29 11:00 | 58 | 55
2018-07-29 11:30 | 55 | 51
2018-07-29 12:00 | 47 | 41
2018-07-29 12:30 | 46 | 40
2018-07-29 13:00 | 48 | 45
2018-07-29 13:30 | 49 | 46
2018-07-29 14:00 | 47 | 44
2018-07-29 14:30 | 58 | 56
2018-07-29 15:00 | 66 | 64
2018-07-29 15:30 | 81 | 79
2018-07-29 16:00 | 100 | 98
2018-07-29 16:30 | 103 | 102
2018-07-29 17:00 | 134 | 133
2018-07-29 17:30 | 176 | 175
2018-07-29 18:00 | 208 | 207
2018-07-29 18:30 | 230 | 229
2018-07-29 19:00 | 240 | 238
2018-07-29 19:30 | 229 | 228
2018-07-29 20:00 | 220 | 219
2018-07-29 20:30 | 213 | 212
2018-07-29 21:00 | 200 | 198
2018-07-29 21:30 | 189 | 188
2018-07-29 22:00 | 179 | 177
2018-07-29 22:30 | 183 | 181
2018-07-29 23:00 | 171 | 169
2018-07-29 23:30 | 160 | 159
2018-07-30 | 154 | 153
2018-07-30 00:30 | 148 | 146
2018-07-30 01:00 | 143 | 141
2018-07-30 01:30 | 129 | 128
2018-07-30 02:00 | 135 | 134
2018-07-30 02:30 | 135 | 134
2018-07-30 03:00 | 135 | 134
2018-07-30 03:30 | 135 | 134
2018-07-30 04:00 | 134 | 133
2018-07-30 04:30 | 135 | 134
2018-07-30 05:00 | 138 | 137
2018-07-30 05:30 | 144 | 143
2018-07-30 06:00 | 137 | 136
2018-07-30 06:30 | 148 | 147
2018-07-30 07:00 | 153 | 152
2018-07-30 07:30 | 161 | 160
2018-07-30 08:00 | 144 | 143
2018-07-30 08:30 | 117 | 116
2018-07-30 09:00 | 95 | 94
2018-07-30 09:30 | 74 | 73
2018-07-30 10:00 | 74 | 73
2018-07-30 10:30 | 64 | 62
2018-07-30 11:00 | 52 | 46
2018-07-30 11:30 | 35 | 25
2018-07-30 12:00 | 35 | 30
2018-07-30 12:30 | 41 | 37
2018-07-30 13:00 | 37 | 33
2018-07-30 13:30 | 41 | 35
2018-07-30 14:00 | 49 | 44
2018-07-30 14:30 | 97 | 96
2018-07-30 15:00 | 119 | 119
2018-07-30 15:30 | 137 | 136
2018-07-30 16:00 | 175 | 174
2018-07-30 16:30 | 180 | 179
2018-07-30 17:00 | 234 | 233
2018-07-30 17:30 | 297 | 297
2018-07-30 18:00 | 363 | 362
2018-07-30 18:30 | 395 | 394
2018-07-30 19:00 | 401 | 401
2018-07-30 19:30 | 377 | 377
2018-07-30 20:00 | 357 | 356
2018-07-30 20:30 | 341 | 341
2018-07-30 21:00 | 322 | 321
2018-07-30 21:30 | 303 | 302
2018-07-30 22:00 | 286 | 286
2018-07-30 22:30 | 289 | 289
2018-07-30 23:00 | 269 | 268
2018-07-30 23:30 | 272 | 271
2018-07-31 | 257 | 256
2018-07-31 00:30 | 254 | 254
2018-07-31 01:00 | 244 | 243
2018-07-31 01:30 | 237 | 236
2018-07-31 02:00 | 221 | 220
2018-07-31 02:30 | 219 | 219
2018-07-31 03:00 | 217 | 217
2018-07-31 03:30 | 217 | 216
2018-07-31 04:00 | 218 | 217
2018-07-31 04:30 | 225 | 224
2018-07-31 05:00 | 232 | 232
2018-07-31 05:30 | 241 | 241
2018-07-31 06:00 | 239 | 238
2018-07-31 06:30 | 263 | 263
2018-07-31 07:00 | 278 | 277
2018-07-31 07:30 | 281 | 281
2018-07-31 08:00 | 239 | 238
2018-07-31 08:30 | 182 | 182
2018-07-31 09:00 | 146 | 146
2018-07-31 09:30 | 118 | 117
2018-07-31 10:00 | 126 | 126
2018-07-31 10:30 | 115 | 114
2018-07-31 11:00 | 62 | 58
2018-07-31 11:30 | 57 | 51
2018-07-31 12:00 | 61 | 55
2018-07-31 12:30 | 62 | 58
2018-07-31 13:00 | 51 | 47
2018-07-31 13:30 | 77 | 76
2018-07-31 14:00 | 93 | 91
2018-07-31 14:30 | 100 | 99
2018-07-31 15:00 | 135 | 134
2018-07-31 15:30 | 150 | 148
2018-07-31 16:00 | 180 | 179
2018-07-31 16:30 | 184 | 183
2018-07-31 17:00 | 232 | 232
2018-07-31 17:30 | 303 | 303
2018-07-31 18:00 | 353 | 352
2018-07-31 18:30 | 384 | 383
2018-07-31 19:00 | 396 | 395
2018-07-31 19:30 | 385 | 385
2018-07-31 20:00 | 366 | 365
2018-07-31 20:30 | 348 | 347
2018-07-31 21:00 | 326 | 325
2018-07-31 21:30 | 272 | 270
2018-07-31 22:00 | 280 | 279
2018-07-31 22:30 | 290 | 289
2018-07-31 23:00 | 271 | 270
2018-07-31 23:30 | 271 | 270
2018-08-01 | 255 | 254
2018-08-01 00:30 | 244 | 243
2018-08-01 01:00 | 230 | 229
2018-08-01 01:30 | 226 | 225
2018-08-01 02:00 | 226 | 225
2018-08-01 02:30 | 196 | 195
2018-08-01 03:00 | 177 | 176
2018-08-01 03:30 | 149 | 148
2018-08-01 04:00 | 152 | 151
2018-08-01 04:30 | 162 | 162
2018-08-01 05:00 | 161 | 160
2018-08-01 05:30 | 170 | 169
2018-08-01 06:00 | 140 | 140
2018-08-01 06:30 | 129 | 128
2018-08-01 07:00 | 139 | 138
2018-08-01 07:30 | 92 | 91
2018-08-01 08:00 | 51 | 46
2018-08-01 08:30 | 8 | 6
2018-08-01 09:00 | 60 | 51
2018-08-01 09:30 | 85 | 75
2018-08-01 10:00 | 76 | 69
2018-08-01 10:30 | 18 | 16
2018-08-01 11:00 | 0 | 0
2018-08-01 11:30 | 1 | 0
2018-08-01 12:00 | 0 | 0
2018-08-01 12:30 | 2 | 2
2018-08-01 13:00 | 1 | 0
2018-08-01 13:30 | 4 | 3
2018-08-01 14:00 | 0 | 0
2018-08-01 14:30 | 6 | 5
2018-08-01 15:00 | 6 | 6
2018-08-01 15:30 | 16 | 13
2018-08-01 16:00 | 32 | 25
2018-08-01 16:30 | 66 | 60
2018-08-01 17:00 | 8 | 7
2018-08-01 17:30 | 74 | 71
2018-08-01 18:00 | 138 | 137
2018-08-01 18:30 | 177 | 177
2018-08-01 19:00 | 155 | 155
2018-08-01 19:30 | 153 | 152
2018-08-01 20:00 | 150 | 149
2018-08-01 20:30 | 132 | 131
2018-08-01 21:00 | 118 | 117
2018-08-01 21:30 | 101 | 100
2018-08-01 22:00 | 107 | 106
2018-08-01 22:30 | 110 | 109
2018-08-01 23:00 | 91 | 90
2018-08-01 23:30 | 73 | 71
2018-08-02 | 120 | 119
2018-08-02 00:30 | 171 | 170
2018-08-02 01:00 | 232 | 231
2018-08-02 01:30 | 229 | 228
2018-08-02 02:00 | 234 | 234
2018-08-02 02:30 | 229 | 228
2018-08-02 03:00 | 228 | 228
2018-08-02 03:30 | 227 | 226
2018-08-02 04:00 | 227 | 226
2018-08-02 04:30 | 235 | 234
2018-08-02 05:00 | 243 | 242
2018-08-02 05:30 | 252 | 251
2018-08-02 06:00 | 241 | 241
2018-08-02 06:30 | 263 | 263
2018-08-02 07:00 | 277 | 277
2018-08-02 07:30 | 274 | 273
2018-08-02 08:00 | 260 | 260
2018-08-02 08:30 | 203 | 203
2018-08-02 09:00 | 175 | 175
2018-08-02 09:30 | 148 | 148
2018-08-02 10:00 | 154 | 154
2018-08-02 10:30 | 141 | 140
2018-08-02 11:00 | 142 | 141
2018-08-02 11:30 | 137 | 136
2018-08-02 12:00 | 132 | 130
2018-08-02 12:30 | 132 | 130
2018-08-02 13:00 | 130 | 128
2018-08-02 13:30 | 132 | 130
2018-08-02 14:00 | 136 | 134
2018-08-02 14:30 | 145 | 143
2018-08-02 15:00 | 150 | 149
2018-08-02 15:30 | 162 | 161
2018-08-02 16:00 | 181 | 180
2018-08-02 16:30 | 190 | 190
2018-08-02 17:00 | 234 | 234
2018-08-02 17:30 | 297 | 297
2018-08-02 18:00 | 352 | 351
2018-08-02 18:30 | 380 | 380
2018-08-02 19:00 | 378 | 378
2018-08-02 19:30 | 372 | 372
2018-08-02 20:00 | 358 | 357
2018-08-02 20:30 | 343 | 343
2018-08-02 21:00 | 324 | 324
2018-08-02 21:30 | 299 | 299
2018-08-02 22:00 | 281 | 280
2018-08-02 22:30 | 312 | 312
2018-08-02 23:00 | 300 | 300
2018-08-02 23:30 | 278 | 278
2018-08-03 | 266 | 265
2018-08-03 00:30 | 254 | 253
2018-08-03 01:00 | 240 | 240
2018-08-03 01:30 | 232 | 232
2018-08-03 02:00 | 231 | 231
2018-08-03 02:30 | 229 | 229
2018-08-03 03:00 | 222 | 222
2018-08-03 03:30 | 220 | 220
2018-08-03 04:00 | 221 | 221
2018-08-03 04:30 | 221 | 220
2018-08-03 05:00 | 226 | 226
2018-08-03 05:30 | 236 | 236
2018-08-03 06:00 | 224 | 224
2018-08-03 06:30 | 249 | 249
2018-08-03 07:00 | 261 | 261
2018-08-03 07:30 | 264 | 264
2018-08-03 08:00 | 234 | 233
2018-08-03 08:30 | 179 | 179
2018-08-03 09:00 | 147 | 146
2018-08-03 09:30 | 120 | 119
2018-08-03 10:00 | 143 | 142
2018-08-03 10:30 | 129 | 127
2018-08-03 11:00 | 128 | 126
2018-08-03 11:30 | 127 | 125
2018-08-03 12:00 | 147 | 146
2018-08-03 12:30 | 131 | 130
2018-08-03 13:00 | 134 | 132
2018-08-03 13:30 | 133 | 131
2018-08-03 14:00 | 155 | 154
2018-08-03 14:30 | 159 | 158
2018-08-03 15:00 | 159 | 158
2018-08-03 15:30 | 159 | 158
2018-08-03 16:00 | 183 | 182
2018-08-03 16:30 | 193 | 192
2018-08-03 17:00 | 232 | 232
2018-08-03 17:30 | 184 | 183
2018-08-03 18:00 | 201 | 201
2018-08-03 18:30 | 219 | 219
2018-08-03 19:00 | 220 | 219
2018-08-03 19:30 | 208 | 208
2018-08-03 20:00 | 197 | 196
2018-08-03 20:30 | 182 | 182
2018-08-03 21:00 | 172 | 171
2018-08-03 21:30 | 172 | 172
2018-08-03 22:00 | 163 | 162
2018-08-03 22:30 | 175 | 175
2018-08-03 23:00 | 171 | 170
2018-08-03 23:30 | 173 | 172
2018-08-04 | 167 | 166
2018-08-04 00:30 | 161 | 161
2018-08-04 01:00 | 148 | 148
2018-08-04 01:30 | 144 | 144
2018-08-04 02:00 | 142 | 141
2018-08-04 02:30 | 141 | 140
2018-08-04 03:00 | 138 | 137
2018-08-04 03:30 | 137 | 136
2018-08-04 04:00 | 137 | 136
2018-08-04 04:30 | 132 | 131
2018-08-04 05:00 | 134 | 133
2018-08-04 05:30 | 141 | 140
2018-08-04 06:00 | 125 | 124
2018-08-04 06:30 | 130 | 129
2018-08-04 07:00 | 127 | 126
2018-08-04 07:30 | 136 | 135
2018-08-04 08:00 | 124 | 123
2018-08-04 08:30 | 110 | 109
2018-08-04 09:00 | 99 | 97
2018-08-04 09:30 | 93 | 90
2018-08-04 10:00 | 95 | 93
2018-08-04 10:30 | 84 | 81
2018-08-04 11:00 | 73 | 68
2018-08-04 11:30 | 72 | 66
2018-08-04 12:00 | 68 | 61
2018-08-04 12:30 | 63 | 56
2018-08-04 13:00 | 61 | 53
2018-08-04 13:30 | 64 | 56
2018-08-04 14:00 | 60 | 51
2018-08-04 14:30 | 64 | 57
2018-08-04 15:00 | 62 | 55
2018-08-04 15:30 | 70 | 65
2018-08-04 16:00 | 87 | 84
2018-08-04 16:30 | 90 | 87
2018-08-04 17:00 | 117 | 116
2018-08-04 17:30 | 155 | 154
2018-08-04 18:00 | 181 | 180
2018-08-04 18:30 | 198 | 198
2018-08-04 19:00 | 206 | 205
2018-08-04 19:30 | 200 | 200
2018-08-04 20:00 | 188 | 187
2018-08-04 20:30 | 180 | 179
2018-08-04 21:00 | 183 | 182
2018-08-04 21:30 | 180 | 178
2018-08-04 22:00 | 171 | 170
2018-08-04 22:30 | 178 | 177
2018-08-04 23:00 | 172 | 171
2018-08-04 23:30 | 170 | 169
2018-08-05 | 165 | 164
2018-08-05 00:30 | 159 | 158
2018-08-05 01:00 | 150 | 149
2018-08-05 01:30 | 146 | 146
2018-08-05 02:00 | 146 | 145
2018-08-05 02:30 | 143 | 142
2018-08-05 03:00 | 139 | 138
2018-08-05 03:30 | 138 | 138
2018-08-05 04:00 | 138 | 138
2018-08-05 04:30 | 126 | 125
2018-08-05 05:00 | 138 | 137
2018-08-05 05:30 | 141 | 140
2018-08-05 06:00 | 135 | 135
2018-08-05 06:30 | 140 | 139
2018-08-05 07:00 | 127 | 126
2018-08-05 07:30 | 122 | 121
2018-08-05 08:00 | 105 | 104
2018-08-05 08:30 | 88 | 87
2018-08-05 09:00 | 74 | 72
2018-08-05 09:30 | 71 | 69
2018-08-05 10:00 | 74 | 72
2018-08-05 10:30 | 70 | 67
2018-08-05 11:00 | 59 | 53
2018-08-05 11:30 | 58 | 52
2018-08-05 12:00 | 58 | 52
2018-08-05 12:30 | 52 | 43
2018-08-05 13:00 | 50 | 42
2018-08-05 13:30 | 54 | 47
2018-08-05 14:00 | 60 | 55
2018-08-05 14:30 | 58 | 53
2018-08-05 15:00 | 57 | 51
2018-08-05 15:30 | 69 | 65
2018-08-05 16:00 | 93 | 92
2018-08-05 16:30 | 87 | 86
2018-08-05 17:00 | 112 | 111
2018-08-05 17:30 | 159 | 158
2018-08-05 18:00 | 196 | 195
2018-08-05 18:30 | 220 | 220
2018-08-05 19:00 | 210 | 209
2018-08-05 19:30 | 199 | 198
2018-08-05 20:00 | 203 | 202
2018-08-05 20:30 | 194 | 194
2018-08-05 21:00 | 184 | 184
2018-08-05 21:30 | 175 | 174
2018-08-05 22:00 | 158 | 157
2018-08-05 22:30 | 163 | 162
2018-08-05 23:00 | 154 | 153
2018-08-05 23:30 | 156 | 155
2018-08-06 | 154 | 153
2018-08-06 00:30 | 148 | 147
2018-08-06 01:00 | 142 | 142
2018-08-06 01:30 | 139 | 138
2018-08-06 02:00 | 139 | 138
2018-08-06 02:30 | 137 | 136
2018-08-06 03:00 | 130 | 129
2018-08-06 03:30 | 132 | 131
2018-08-06 04:00 | 136 | 136
2018-08-06 04:30 | 142 | 142
2018-08-06 05:00 | 138 | 138
2018-08-06 05:30 | 145 | 145
2018-08-06 06:00 | 139 | 138
2018-08-06 06:30 | 151 | 150
2018-08-06 07:00 | 156 | 156
2018-08-06 07:30 | 165 | 164
2018-08-06 08:00 | 149 | 148
2018-08-06 08:30 | 122 | 121
2018-08-06 09:00 | 107 | 106
2018-08-06 09:30 | 93 | 92
2018-08-06 10:00 | 102 | 101
2018-08-06 10:30 | 94 | 93
2018-08-06 11:00 | 83 | 80
2018-08-06 11:30 | 78 | 75
2018-08-06 12:00 | 75 | 71
2018-08-06 12:30 | 77 | 75
2018-08-06 13:00 | 77 | 75
2018-08-06 13:30 | 79 | 76
2018-08-06 14:00 | 91 | 90
2018-08-06 14:30 | 96 | 94
2018-08-06 15:00 | 108 | 107
2018-08-06 15:30 | 142 | 141
2018-08-06 16:00 | 137 | 136
2018-08-06 16:30 | 132 | 131
2018-08-06 17:00 | 125 | 125
2018-08-06 17:30 | 134 | 134
2018-08-06 18:00 | 138 | 138
2018-08-06 18:30 | 154 | 154
2018-08-06 19:00 | 142 | 142
2018-08-06 19:30 | 141 | 140
2018-08-06 20:00 | 141 | 140
2018-08-06 20:30 | 133 | 132
2018-08-06 21:00 | 124 | 123
2018-08-06 21:30 | 142 | 142
2018-08-06 22:00 | 147 | 147
2018-08-06 22:30 | 124 | 123
2018-08-06 23:00 | 173 | 172
2018-08-06 23:30 | 170 | 169
2018-08-07 | 161 | 160
2018-08-07 00:30 | 155 | 154
2018-08-07 01:00 | 151 | 150
2018-08-07 01:30 | 146 | 145
2018-08-07 02:00 | 145 | 144
2018-08-07 02:30 | 144 | 143
2018-08-07 03:00 | 148 | 147
2018-08-07 03:30 | 149 | 148
2018-08-07 04:00 | 152 | 151
2018-08-07 04:30 | 157 | 156
2018-08-07 05:00 | 162 | 161
2018-08-07 05:30 | 170 | 170
2018-08-07 06:00 | 161 | 160
2018-08-07 06:30 | 175 | 174
2018-08-07 07:00 | 186 | 185
2018-08-07 07:30 | 197 | 196
2018-08-07 08:00 | 202 | 201
2018-08-07 08:30 | 194 | 194
2018-08-07 09:00 | 185 | 185
2018-08-07 09:30 | 159 | 159
2018-08-07 10:00 | 185 | 185
2018-08-07 10:30 | 172 | 171
2018-08-07 11:00 | 157 | 157
2018-08-07 11:30 | 158 | 157
2018-08-07 12:00 | 156 | 156
2018-08-07 12:30 | 149 | 149
2018-08-07 13:00 | 155 | 154
2018-08-07 13:30 | 139 | 138
2018-08-07 14:00 | 137 | 136
2018-08-07 14:30 | 136 | 135
2018-08-07 15:00 | 147 | 147
2018-08-07 15:30 | 163 | 163
2018-08-07 16:00 | 181 | 180
2018-08-07 16:30 | 174 | 173
2018-08-07 17:00 | 154 | 154
2018-08-07 17:30 | 138 | 137
2018-08-07 18:00 | 139 | 138
2018-08-07 18:30 | 154 | 154
2018-08-07 19:00 | 164 | 164
2018-08-07 19:30 | 153 | 153
2018-08-07 20:00 | 138 | 137
2018-08-07 20:30 | 124 | 124
2018-08-07 21:00 | 113 | 112
2018-08-07 21:30 | 102 | 101
2018-08-07 22:00 | 122 | 122
2018-08-07 22:30 | 125 | 124
2018-08-07 23:00 | 148 | 148
2018-08-07 23:30 | 150 | 150
2018-08-08 | 147 | 147
2018-08-08 00:30 | 146 | 145
2018-08-08 01:00 | 140 | 139
2018-08-08 01:30 | 135 | 134
2018-08-08 02:00 | 122 | 121
2018-08-08 02:30 | 131 | 130
2018-08-08 03:00 | 128 | 127
2018-08-08 03:30 | 128 | 127
2018-08-08 04:00 | 128 | 128
2018-08-08 04:30 | 132 | 131
2018-08-08 05:00 | 135 | 134
2018-08-08 05:30 | 140 | 139
2018-08-08 06:00 | 110 | 109
2018-08-08 06:30 | 83 | 79
2018-08-08 07:00 | 60 | 54
2018-08-08 07:30 | 49 | 43
2018-08-08 08:00 | 48 | 43
2018-08-08 08:30 | 41 | 35
2018-08-08 09:00 | 14 | 12
2018-08-08 09:30 | 46 | 40
2018-08-08 10:00 | 60 | 54
2018-08-08 10:30 | 86 | 84
2018-08-08 11:00 | 85 | 82
2018-08-08 11:30 | 82 | 79
2018-08-08 12:00 | 82 | 80
2018-08-08 12:30 | 82 | 80
2018-08-08 13:00 | 80 | 77
2018-08-08 13:30 | 79 | 75
2018-08-08 14:00 | 76 | 72
2018-08-08 14:30 | 78 | 74
2018-08-08 15:00 | 84 | 81
2018-08-08 15:30 | 93 | 91
2018-08-08 16:00 | 105 | 103
2018-08-08 16:30 | 107 | 105
2018-08-08 17:00 | 100 | 99
2018-08-08 17:30 | 97 | 96
2018-08-08 18:00 | 113 | 112
2018-08-08 18:30 | 121 | 120
2018-08-08 19:00 | 122 | 121
2018-08-08 19:30 | 129 | 128
2018-08-08 20:00 | 111 | 110
2018-08-08 20:30 | 96 | 95
2018-08-08 21:00 | 105 | 104
2018-08-08 21:30 | 111 | 110
2018-08-08 22:00 | 121 | 121
2018-08-08 22:30 | 144 | 144
2018-08-08 23:00 | 165 | 164
2018-08-08 23:30 | 161 | 160
2018-08-09 | 153 | 152
2018-08-09 00:30 | 148 | 147
2018-08-09 01:00 | 141 | 140
2018-08-09 01:30 | 137 | 137
2018-08-09 02:00 | 134 | 133
2018-08-09 02:30 | 130 | 129
2018-08-09 03:00 | 129 | 128
2018-08-09 03:30 | 128 | 127
2018-08-09 04:00 | 129 | 128
2018-08-09 04:30 | 130 | 129
2018-08-09 05:00 | 135 | 134
2018-08-09 05:30 | 143 | 143
2018-08-09 06:00 | 137 | 136
2018-08-09 06:30 | 152 | 151
2018-08-09 07:00 | 141 | 140
2018-08-09 07:30 | 133 | 132
2018-08-09 08:00 | 117 | 116
2018-08-09 08:30 | 107 | 106
2018-08-09 09:00 | 84 | 82
2018-08-09 09:30 | 72 | 68
2018-08-09 10:00 | 78 | 75
2018-08-09 10:30 | 71 | 67
2018-08-09 11:00 | 66 | 60
2018-08-09 11:30 | 65 | 59
2018-08-09 12:00 | 70 | 65
2018-08-09 12:30 | 70 | 64
2018-08-09 13:00 | 71 | 66
2018-08-09 13:30 | 75 | 71
2018-08-09 14:00 | 72 | 68
2018-08-09 14:30 | 75 | 71
2018-08-09 15:00 | 75 | 71
2018-08-09 15:30 | 86 | 84
2018-08-09 16:00 | 96 | 94
2018-08-09 16:30 | 70 | 65
2018-08-09 17:00 | 78 | 75
2018-08-09 17:30 | 83 | 81
2018-08-09 18:00 | 113 | 112
2018-08-09 18:30 | 134 | 133
2018-08-09 19:00 | 142 | 142
2018-08-09 19:30 | 140 | 140
2018-08-09 20:00 | 132 | 131
2018-08-09 20:30 | 119 | 118
2018-08-09 21:00 | 110 | 109
2018-08-09 21:30 | 116 | 115
2018-08-09 22:00 | 121 | 120
2018-08-09 22:30 | 118 | 117
2018-08-09 23:00 | 123 | 122
2018-08-09 23:30 | 120 | 119
2018-08-10 | 112 | 111
2018-08-10 00:30 | 108 | 107
2018-08-10 01:00 | 136 | 136
2018-08-10 01:30 | 138 | 137
2018-08-10 02:00 | 135 | 134
2018-08-10 02:30 | 134 | 133
2018-08-10 03:00 | 133 | 133
2018-08-10 03:30 | 133 | 132
2018-08-10 04:00 | 131 | 130
2018-08-10 04:30 | 133 | 132
2018-08-10 05:00 | 138 | 137
2018-08-10 05:30 | 143 | 142
2018-08-10 06:00 | 135 | 134
2018-08-10 06:30 | 108 | 106
2018-08-10 07:00 | 47 | 41
2018-08-10 07:30 | 51 | 44
2018-08-10 08:00 | 38 | 34
2018-08-10 08:30 | 44 | 39
2018-08-10 09:00 | 38 | 33
2018-08-10 09:30 | 12 | 12
2018-08-10 10:00 | 65 | 61
2018-08-10 10:30 | 27 | 21
2018-08-10 11:00 | 12 | 11
2018-08-10 11:30 | 25 | 21
2018-08-10 12:00 | 22 | 18
2018-08-10 12:30 | 15 | 14
2018-08-10 13:00 | 26 | 21
2018-08-10 13:30 | 50 | 44
2018-08-10 14:00 | 55 | 47
2018-08-10 14:30 | 67 | 62
2018-08-10 15:00 | 79 | 76
2018-08-10 15:30 | 102 | 101
2018-08-10 16:00 | 116 | 115
2018-08-10 16:30 | 119 | 118
2018-08-10 17:00 | 134 | 134
2018-08-10 17:30 | 162 | 161
2018-08-10 18:00 | 186 | 185
2018-08-10 18:30 | 200 | 200
2018-08-10 19:00 | 210 | 210
2018-08-10 19:30 | 204 | 204
2018-08-10 20:00 | 195 | 195
2018-08-10 20:30 | 184 | 183
2018-08-10 21:00 | 175 | 174
2018-08-10 21:30 | 182 | 181
2018-08-10 22:00 | 178 | 177
2018-08-10 22:30 | 184 | 183
2018-08-10 23:00 | 176 | 175
2018-08-10 23:30 | 162 | 161
2018-08-11 | 153 | 152
2018-08-11 00:30 | 152 | 151
2018-08-11 01:00 | 145 | 144
2018-08-11 01:30 | 144 | 143
2018-08-11 02:00 | 139 | 138
2018-08-11 02:30 | 138 | 137
2018-08-11 03:00 | 135 | 134
2018-08-11 03:30 | 132 | 132
2018-08-11 04:00 | 131 | 131
2018-08-11 04:30 | 134 | 133
2018-08-11 05:00 | 136 | 135
2018-08-11 05:30 | 137 | 136
2018-08-11 06:00 | 127 | 127
2018-08-11 06:30 | 129 | 128
2018-08-11 07:00 | 123 | 122
2018-08-11 07:30 | 121 | 120
2018-08-11 08:00 | 102 | 101
2018-08-11 08:30 | 89 | 88
2018-08-11 09:00 | 92 | 90
2018-08-11 09:30 | 88 | 87
2018-08-11 10:00 | 87 | 85
2018-08-11 10:30 | 70 | 68
2018-08-11 11:00 | 63 | 59
2018-08-11 11:30 | 19 | 16
2018-08-11 12:00 | 6 | 5
2018-08-11 12:30 | 38 | 32
2018-08-11 13:00 | 55 | 46
2018-08-11 13:30 | 56 | 48
2018-08-11 14:00 | 52 | 43
2018-08-11 14:30 | 53 | 44
2018-08-11 15:00 | 57 | 49
2018-08-11 15:30 | 61 | 56
2018-08-11 16:00 | 70 | 67
2018-08-11 16:30 | 83 | 81
2018-08-11 17:00 | 110 | 110
2018-08-11 17:30 | 147 | 146
2018-08-11 18:00 | 179 | 178
2018-08-11 18:30 | 199 | 199
2018-08-11 19:00 | 205 | 205
2018-08-11 19:30 | 201 | 200
2018-08-11 20:00 | 193 | 192
2018-08-11 20:30 | 186 | 185
2018-08-11 21:00 | 180 | 179
2018-08-11 21:30 | 184 | 183
2018-08-11 22:00 | 177 | 177
2018-08-11 22:30 | 181 | 180
2018-08-11 23:00 | 174 | 173
2018-08-11 23:30 | 162 | 161
2018-08-12 | 158 | 157
2018-08-12 00:30 | 154 | 154
2018-08-12 01:00 | 147 | 146
2018-08-12 01:30 | 140 | 139
2018-08-12 02:00 | 138 | 137
2018-08-12 02:30 | 135 | 134
2018-08-12 03:00 | 132 | 131
2018-08-12 03:30 | 132 | 131
2018-08-12 04:00 | 132 | 131
2018-08-12 04:30 | 132 | 131
2018-08-12 05:00 | 132 | 131
2018-08-12 05:30 | 132 | 131
2018-08-12 06:00 | 118 | 117
2018-08-12 06:30 | 120 | 119
2018-08-12 07:00 | 114 | 113
2018-08-12 07:30 | 104 | 103
2018-08-12 08:00 | 81 | 79
2018-08-12 08:30 | 67 | 64
2018-08-12 09:00 | 59 | 53
2018-08-12 09:30 | 51 | 42
2018-08-12 10:00 | 67 | 64
2018-08-12 10:30 | 69 | 65
2018-08-12 11:00 | 57 | 48
2018-08-12 11:30 | 46 | 39
2018-08-12 12:00 | 36 | 34
2018-08-12 12:30 | 33 | 33
2018-08-12 13:00 | 32 | 31
2018-08-12 13:30 | 34 | 31
2018-08-12 14:00 | 39 | 35
2018-08-12 14:30 | 45 | 39
2018-08-12 15:00 | 55 | 47
2018-08-12 15:30 | 69 | 65
2018-08-12 16:00 | 89 | 88
2018-08-12 16:30 | 92 | 91
2018-08-12 17:00 | 106 | 105
2018-08-12 17:30 | 140 | 139
2018-08-12 18:00 | 177 | 177
2018-08-12 18:30 | 204 | 204
2018-08-12 19:00 | 215 | 214
2018-08-12 19:30 | 211 | 210
2018-08-12 20:00 | 202 | 201
2018-08-12 20:30 | 189 | 188
2018-08-12 21:00 | 182 | 181
2018-08-12 21:30 | 186 | 185
2018-08-12 22:00 | 180 | 179
2018-08-12 22:30 | 181 | 180
2018-08-12 23:00 | 174 | 173
2018-08-12 23:30 | 165 | 164
2018-08-13 | 158 | 157
2018-08-13 00:30 | 155 | 154
2018-08-13 01:00 | 147 | 146
2018-08-13 01:30 | 145 | 144
2018-08-13 02:00 | 137 | 136
2018-08-13 02:30 | 136 | 135
2018-08-13 03:00 | 132 | 131
2018-08-13 03:30 | 130 | 129
2018-08-13 04:00 | 130 | 129
2018-08-13 04:30 | 131 | 130
2018-08-13 05:00 | 134 | 133
2018-08-13 05:30 | 142 | 141
2018-08-13 06:00 | 133 | 133
2018-08-13 06:30 | 147 | 146
2018-08-13 07:00 | 154 | 153
2018-08-13 07:30 | 157 | 156
2018-08-13 08:00 | 136 | 136
2018-08-13 08:30 | 104 | 102
2018-08-13 09:00 | 83 | 80
2018-08-13 09:30 | 71 | 66
2018-08-13 10:00 | 77 | 72
2018-08-13 10:30 | 75 | 69
2018-08-13 11:00 | 69 | 62
2018-08-13 11:30 | 63 | 58
2018-08-13 12:00 | 59 | 53
2018-08-13 12:30 | 59 | 54
2018-08-13 13:00 | 61 | 56
2018-08-13 13:30 | 61 | 57
2018-08-13 14:00 | 67 | 63
2018-08-13 14:30 | 71 | 68
2018-08-13 15:00 | 76 | 73
2018-08-13 15:30 | 81 | 78
2018-08-13 16:00 | 98 | 96
2018-08-13 16:30 | 98 | 97
2018-08-13 17:00 | 121 | 120
2018-08-13 17:30 | 154 | 153
2018-08-13 18:00 | 177 | 176
2018-08-13 18:30 | 198 | 198
2018-08-13 19:00 | 204 | 203
2018-08-13 19:30 | 207 | 206
2018-08-13 20:00 | 197 | 196
2018-08-13 20:30 | 184 | 183
2018-08-13 21:00 | 183 | 182
2018-08-13 21:30 | 188 | 187
2018-08-13 22:00 | 177 | 177
2018-08-13 22:30 | 181 | 180
2018-08-13 23:00 | 168 | 167
2018-08-13 23:30 | 157 | 156
2018-08-14 | 154 | 152
2018-08-14 00:30 | 150 | 149
2018-08-14 01:00 | 143 | 142
2018-08-14 01:30 | 140 | 139
2018-08-14 02:00 | 130 | 129
2018-08-14 02:30 | 131 | 130
2018-08-14 03:00 | 134 | 133
2018-08-14 03:30 | 135 | 134
2018-08-14 04:00 | 135 | 134
2018-08-14 04:30 | 133 | 132
2018-08-14 05:00 | 136 | 135
2018-08-14 05:30 | 143 | 142
2018-08-14 06:00 | 137 | 137
2018-08-14 06:30 | 149 | 148
2018-08-14 07:00 | 158 | 157
2018-08-14 07:30 | 165 | 164
2018-08-14 08:00 | 140 | 139
2018-08-14 08:30 | 109 | 108
2018-08-14 09:00 | 103 | 101
2018-08-14 09:30 | 93 | 91
2018-08-14 10:00 | 95 | 94
2018-08-14 10:30 | 89 | 87
2018-08-14 11:00 | 82 | 80
2018-08-14 11:30 | 81 | 79
2018-08-14 12:00 | 78 | 75
2018-08-14 12:30 | 75 | 72
2018-08-14 13:00 | 75 | 72
2018-08-14 13:30 | 80 | 77
2018-08-14 14:00 | 81 | 78
2018-08-14 14:30 | 86 | 83
2018-08-14 15:00 | 90 | 87
2018-08-14 15:30 | 103 | 101
2018-08-14 16:00 | 125 | 124
2018-08-14 16:30 | 115 | 113
2018-08-14 17:00 | 128 | 127
2018-08-14 17:30 | 166 | 165
2018-08-14 18:00 | 202 | 202
2018-08-14 18:30 | 223 | 223
2018-08-14 19:00 | 240 | 240
2018-08-14 19:30 | 238 | 237
2018-08-14 20:00 | 221 | 221
2018-08-14 20:30 | 211 | 211
2018-08-14 21:00 | 200 | 200
2018-08-14 21:30 | 189 | 188
2018-08-14 22:00 | 177 | 176
2018-08-14 22:30 | 181 | 180
2018-08-14 23:00 | 182 | 181
2018-08-14 23:30 | 173 | 172
2018-08-15 | 160 | 159
2018-08-15 00:30 | 151 | 149
2018-08-15 01:00 | 143 | 142
2018-08-15 01:30 | 141 | 140
2018-08-15 02:00 | 139 | 138
2018-08-15 02:30 | 136 | 135
2018-08-15 03:00 | 137 | 136
2018-08-15 03:30 | 134 | 133
2018-08-15 04:00 | 132 | 131
2018-08-15 04:30 | 134 | 133
2018-08-15 05:00 | 143 | 142
2018-08-15 05:30 | 148 | 147
2018-08-15 06:00 | 140 | 139
2018-08-15 06:30 | 158 | 157
2018-08-15 07:00 | 161 | 160
2018-08-15 07:30 | 179 | 179
2018-08-15 08:00 | 171 | 170
2018-08-15 08:30 | 154 | 154
2018-08-15 09:00 | 117 | 116
2018-08-15 09:30 | 103 | 102
2018-08-15 10:00 | 111 | 110
2018-08-15 10:30 | 94 | 93
2018-08-15 11:00 | 87 | 85
2018-08-15 11:30 | 75 | 73
2018-08-15 12:00 | 81 | 79
2018-08-15 12:30 | 75 | 73
2018-08-15 13:00 | 73 | 70
2018-08-15 13:30 | 78 | 75
2018-08-15 14:00 | 75 | 72
2018-08-15 14:30 | 81 | 79
2018-08-15 15:00 | 81 | 79
2018-08-15 15:30 | 88 | 86
2018-08-15 16:00 | 93 | 92
2018-08-15 16:30 | 96 | 95
2018-08-15 17:00 | 124 | 123
2018-08-15 17:30 | 164 | 163
2018-08-15 18:00 | 171 | 171
2018-08-15 18:30 | 189 | 189
2018-08-15 19:00 | 203 | 202
2018-08-15 19:30 | 195 | 194
2018-08-15 20:00 | 188 | 187
2018-08-15 20:30 | 177 | 176
2018-08-15 21:00 | 183 | 182
2018-08-15 21:30 | 189 | 189
2018-08-15 22:00 | 185 | 184
2018-08-15 22:30 | 185 | 184
2018-08-15 23:00 | 173 | 172
2018-08-15 23:30 | 162 | 161
2018-08-16 | 153 | 152
2018-08-16 00:30 | 151 | 150
2018-08-16 01:00 | 143 | 142
2018-08-16 01:30 | 139 | 139
2018-08-16 02:00 | 136 | 135
2018-08-16 02:30 | 134 | 133
2018-08-16 03:00 | 135 | 134
2018-08-16 03:30 | 135 | 134
2018-08-16 04:00 | 137 | 137
2018-08-16 04:30 | 139 | 139
2018-08-16 05:00 | 143 | 143
2018-08-16 05:30 | 154 | 153
2018-08-16 06:00 | 146 | 146
2018-08-16 06:30 | 143 | 142
2018-08-16 07:00 | 146 | 145
2018-08-16 07:30 | 150 | 150
2018-08-16 08:00 | 135 | 134
2018-08-16 08:30 | 123 | 122
2018-08-16 09:00 | 103 | 102
2018-08-16 09:30 | 86 | 84
2018-08-16 10:00 | 88 | 85
2018-08-16 10:30 | 83 | 79
2018-08-16 11:00 | 98 | 93
2018-08-16 11:30 | 89 | 81
2018-08-16 12:00 | 77 | 65
2018-08-16 12:30 | 50 | 40
2018-08-16 13:00 | 59 | 47
2018-08-16 13:30 | 55 | 46
2018-08-16 14:00 | 60 | 50
2018-08-16 14:30 | 72 | 58
2018-08-16 15:00 | 49 | 43
2018-08-16 15:30 | 41 | 26
2018-08-16 16:00 | 23 | 7
2018-08-16 16:30 | 9 | 1
2018-08-16 17:00 | 25 | 21
2018-08-16 17:30 | 62 | 60
2018-08-16 18:00 | 71 | 70
2018-08-16 18:30 | 88 | 87
2018-08-16 19:00 | 101 | 100
2018-08-16 19:30 | 94 | 92
2018-08-16 20:00 | 82 | 80
2018-08-16 20:30 | 72 | 68
2018-08-16 21:00 | 79 | 77
2018-08-16 21:30 | 109 | 107
2018-08-16 22:00 | 111 | 110
2018-08-16 22:30 | 99 | 97
2018-08-16 23:00 | 136 | 135
2018-08-16 23:30 | 165 | 164
2018-08-17 | 158 | 158
2018-08-17 00:30 | 144 | 143
2018-08-17 01:00 | 145 | 144
2018-08-17 01:30 | 144 | 143
2018-08-17 02:00 | 139 | 138
2018-08-17 02:30 | 139 | 138
2018-08-17 03:00 | 138 | 137
2018-08-17 03:30 | 137 | 137
2018-08-17 04:00 | 135 | 135
2018-08-17 04:30 | 135 | 134
2018-08-17 05:00 | 139 | 138
2018-08-17 05:30 | 145 | 144
2018-08-17 06:00 | 137 | 136
2018-08-17 06:30 | 132 | 132
2018-08-17 07:00 | 135 | 134
2018-08-17 07:30 | 131 | 130
2018-08-17 08:00 | 111 | 110
2018-08-17 08:30 | 103 | 101
2018-08-17 09:00 | 88 | 86
2018-08-17 09:30 | 75 | 72
2018-08-17 10:00 | 96 | 95
2018-08-17 10:30 | 93 | 91
2018-08-17 11:00 | 89 | 87
2018-08-17 11:30 | 86 | 83
2018-08-17 12:00 | 86 | 83
2018-08-17 12:30 | 87 | 85
2018-08-17 13:00 | 87 | 84
2018-08-17 13:30 | 85 | 82
2018-08-17 14:00 | 79 | 76
2018-08-17 14:30 | 78 | 75
2018-08-17 15:00 | 80 | 77
2018-08-17 15:30 | 83 | 80
2018-08-17 16:00 | 94 | 92
2018-08-17 16:30 | 98 | 97
2018-08-17 17:00 | 128 | 127
2018-08-17 17:30 | 144 | 144
2018-08-17 18:00 | 172 | 172
2018-08-17 18:30 | 177 | 176
2018-08-17 19:00 | 184 | 183
2018-08-17 19:30 | 179 | 179
2018-08-17 20:00 | 171 | 171
2018-08-17 20:30 | 172 | 171
2018-08-17 21:00 | 163 | 162
2018-08-17 21:30 | 170 | 169
2018-08-17 22:00 | 166 | 165
2018-08-17 22:30 | 168 | 167
2018-08-17 23:00 | 161 | 160
2018-08-17 23:30 | 152 | 151
2018-08-18 | 143 | 142
2018-08-18 00:30 | 150 | 149
2018-08-18 01:00 | 144 | 143
2018-08-18 01:30 | 144 | 144
2018-08-18 02:00 | 144 | 143
2018-08-18 02:30 | 144 | 143
2018-08-18 03:00 | 137 | 136
2018-08-18 03:30 | 131 | 130
2018-08-18 04:00 | 128 | 127
2018-08-18 04:30 | 130 | 129
2018-08-18 05:00 | 131 | 130
2018-08-18 05:30 | 133 | 132
2018-08-18 06:00 | 122 | 121
2018-08-18 06:30 | 104 | 103
2018-08-18 07:00 | 97 | 95
2018-08-18 07:30 | 91 | 90
2018-08-18 08:00 | 67 | 64
2018-08-18 08:30 | 61 | 57
2018-08-18 09:00 | 51 | 43
2018-08-18 09:30 | 42 | 37
2018-08-18 10:00 | 72 | 70
2018-08-18 10:30 | 72 | 69
2018-08-18 11:00 | 68 | 65
2018-08-18 11:30 | 65 | 61
2018-08-18 12:00 | 60 | 55
2018-08-18 12:30 | 61 | 56
2018-08-18 13:00 | 62 | 57
2018-08-18 13:30 | 59 | 54
2018-08-18 14:00 | 46 | 38
2018-08-18 14:30 | 53 | 44
2018-08-18 15:00 | 59 | 54
2018-08-18 15:30 | 63 | 59
2018-08-18 16:00 | 67 | 64
2018-08-18 16:30 | 78 | 76
2018-08-18 17:00 | 111 | 110
2018-08-18 17:30 | 134 | 134
2018-08-18 18:00 | 166 | 165
2018-08-18 18:30 | 171 | 170
2018-08-18 19:00 | 175 | 174
2018-08-18 19:30 | 170 | 169
2018-08-18 20:00 | 159 | 159
2018-08-18 20:30 | 159 | 158
2018-08-18 21:00 | 153 | 153
2018-08-18 21:30 | 158 | 158
2018-08-18 22:00 | 154 | 153
2018-08-18 22:30 | 162 | 161
2018-08-18 23:00 | 154 | 153
2018-08-18 23:30 | 145 | 144
2018-08-19 | 140 | 139
2018-08-19 00:30 | 151 | 151
2018-08-19 01:00 | 144 | 143
2018-08-19 01:30 | 138 | 137
2018-08-19 02:00 | 136 | 136
2018-08-19 02:30 | 133 | 132
2018-08-19 03:00 | 128 | 127
2018-08-19 03:30 | 128 | 127
2018-08-19 04:00 | 128 | 127
2018-08-19 04:30 | 128 | 127
2018-08-19 05:00 | 126 | 125
2018-08-19 05:30 | 132 | 131
2018-08-19 06:00 | 117 | 116
2018-08-19 06:30 | 99 | 98
2018-08-19 07:00 | 83 | 81
2018-08-19 07:30 | 71 | 69
2018-08-19 08:00 | 46 | 40
2018-08-19 08:30 | 41 | 34
2018-08-19 09:00 | 35 | 26
2018-08-19 09:30 | 27 | 19
2018-08-19 10:00 | 56 | 51
2018-08-19 10:30 | 60 | 55
2018-08-19 11:00 | 57 | 50
2018-08-19 11:30 | 55 | 46
2018-08-19 12:00 | 54 | 45
2018-08-19 12:30 | 52 | 44
2018-08-19 13:00 | 48 | 41
2018-08-19 13:30 | 47 | 40
2018-08-19 14:00 | 35 | 32
2018-08-19 14:30 | 39 | 35
2018-08-19 15:00 | 49 | 42
2018-08-19 15:30 | 60 | 55
2018-08-19 16:00 | 76 | 74
2018-08-19 16:30 | 83 | 82
2018-08-19 17:00 | 111 | 110
2018-08-19 17:30 | 135 | 135
2018-08-19 18:00 | 169 | 168
2018-08-19 18:30 | 181 | 180
2018-08-19 19:00 | 191 | 190
2018-08-19 19:30 | 184 | 183
2018-08-19 20:00 | 174 | 173
2018-08-19 20:30 | 172 | 172
2018-08-19 21:00 | 164 | 163
2018-08-19 21:30 | 166 | 165
2018-08-19 22:00 | 162 | 162
2018-08-19 22:30 | 161 | 161
2018-08-19 23:00 | 151 | 150
2018-08-19 23:30 | 141 | 141
2018-08-20 | 134 | 133
2018-08-20 00:30 | 131 | 130
2018-08-20 01:00 | 132 | 131
2018-08-20 01:30 | 132 | 131
2018-08-20 02:00 | 128 | 127
2018-08-20 02:30 | 122 | 121
2018-08-20 03:00 | 118 | 117
2018-08-20 03:30 | 126 | 125
2018-08-20 04:00 | 126 | 125
2018-08-20 04:30 | 129 | 128
2018-08-20 05:00 | 135 | 134
2018-08-20 05:30 | 139 | 138
2018-08-20 06:00 | 130 | 130
2018-08-20 06:30 | 122 | 121
2018-08-20 07:00 | 122 | 122
2018-08-20 07:30 | 120 | 119
2018-08-20 08:00 | 95 | 94
2018-08-20 08:30 | 123 | 122
2018-08-20 09:00 | 96 | 94
2018-08-20 09:30 | 99 | 99
2018-08-20 10:00 | 128 | 127
2018-08-20 10:30 | 121 | 120
2018-08-20 11:00 | 111 | 111
2018-08-20 11:30 | 106 | 105
2018-08-20 12:00 | 99 | 98
2018-08-20 12:30 | 103 | 102
2018-08-20 13:00 | 100 | 99
2018-08-20 13:30 | 100 | 99
2018-08-20 14:00 | 82 | 80
2018-08-20 14:30 | 88 | 86
2018-08-20 15:00 | 100 | 100
2018-08-20 15:30 | 115 | 114
2018-08-20 16:00 | 143 | 143
2018-08-20 16:30 | 148 | 148
2018-08-20 17:00 | 192 | 191
2018-08-20 17:30 | 222 | 222
2018-08-20 18:00 | 276 | 275
2018-08-20 18:30 | 312 | 312
2018-08-20 19:00 | 332 | 332
2018-08-20 19:30 | 321 | 320
2018-08-20 20:00 | 306 | 305
2018-08-20 20:30 | 281 | 280
2018-08-20 21:00 | 284 | 283
2018-08-20 21:30 | 305 | 305
2018-08-20 22:00 | 287 | 286
2018-08-20 22:30 | 293 | 292
2018-08-20 23:00 | 271 | 271
2018-08-20 23:30 | 228 | 227
2018-08-21 | 212 | 212
2018-08-21 00:30 | 209 | 208
2018-08-21 01:00 | 203 | 203
2018-08-21 01:30 | 181 | 180
2018-08-21 02:00 | 167 | 167
2018-08-21 02:30 | 154 | 154
2018-08-21 03:00 | 155 | 154
2018-08-21 03:30 | 159 | 158
2018-08-21 04:00 | 155 | 155
2018-08-21 04:30 | 146 | 145
2018-08-21 05:00 | 146 | 145
2018-08-21 05:30 | 158 | 157
2018-08-21 06:00 | 166 | 165
2018-08-21 06:30 | 202 | 202
2018-08-21 07:00 | 227 | 226
2018-08-21 07:30 | 110 | 109
2018-08-21 08:00 | 42 | 36
2018-08-21 08:30 | 3 | 3
2018-08-21 09:00 | 43 | 34
2018-08-21 09:30 | 39 | 36
2018-08-21 10:00 | 80 | 78
2018-08-21 10:30 | 75 | 73
2018-08-21 11:00 | 69 | 66
2018-08-21 11:30 | 86 | 85
2018-08-21 12:00 | 68 | 64
2018-08-21 12:30 | 68 | 66
2018-08-21 13:00 | 66 | 63
2018-08-21 13:30 | 63 | 59
2018-08-21 14:00 | 49 | 43
2018-08-21 14:30 | 47 | 41
2018-08-21 15:00 | 55 | 50
2018-08-21 15:30 | 69 | 67
2018-08-21 16:00 | 97 | 96
2018-08-21 16:30 | 95 | 94
2018-08-21 17:00 | 135 | 135
2018-08-21 17:30 | 196 | 195
2018-08-21 18:00 | 248 | 247
2018-08-21 18:30 | 290 | 290
2018-08-21 19:00 | 312 | 312
2018-08-21 19:30 | 258 | 257
2018-08-21 20:00 | 145 | 145
2018-08-21 20:30 | 122 | 121
2018-08-21 21:00 | 107 | 107
2018-08-21 21:30 | 199 | 198
2018-08-21 22:00 | 206 | 206
2018-08-21 22:30 | 231 | 230
2018-08-21 23:00 | 216 | 215
2018-08-21 23:30 | 191 | 190
2018-08-22 | 174 | 173
2018-08-22 00:30 | 170 | 169
2018-08-22 01:00 | 160 | 159
2018-08-22 01:30 | 154 | 154
2018-08-22 02:00 | 151 | 150
2018-08-22 02:30 | 152 | 151
2018-08-22 03:00 | 149 | 148
2018-08-22 03:30 | 150 | 149
2018-08-22 04:00 | 152 | 151
2018-08-22 04:30 | 156 | 155
2018-08-22 05:00 | 159 | 158
2018-08-22 05:30 | 166 | 165
2018-08-22 06:00 | 161 | 160
2018-08-22 06:30 | 194 | 193
2018-08-22 07:00 | 221 | 220
2018-08-22 07:30 | 242 | 242
2018-08-22 08:00 | 220 | 220
2018-08-22 08:30 | 182 | 181
2018-08-22 09:00 | 157 | 156
2018-08-22 09:30 | 135 | 134
2018-08-22 10:00 | 109 | 108
2018-08-22 10:30 | 76 | 73
2018-08-22 11:00 | 73 | 70
2018-08-22 11:30 | 67 | 60
2018-08-22 12:00 | 65 | 59
2018-08-22 12:30 | 63 | 57
2018-08-22 13:00 | 63 | 56
2018-08-22 13:30 | 71 | 68
2018-08-22 14:00 | 62 | 56
2018-08-22 14:30 | 66 | 62
2018-08-22 15:00 | 75 | 72
2018-08-22 15:30 | 89 | 88
2018-08-22 16:00 | 107 | 106
2018-08-22 16:30 | 112 | 111
2018-08-22 17:00 | 139 | 138
2018-08-22 17:30 | 168 | 168
2018-08-22 18:00 | 171 | 171
2018-08-22 18:30 | 199 | 199
2018-08-22 19:00 | 230 | 230
2018-08-22 19:30 | 240 | 240
2018-08-22 20:00 | 222 | 221
2018-08-22 20:30 | 202 | 201
2018-08-22 21:00 | 184 | 184
2018-08-22 21:30 | 223 | 223
2018-08-22 22:00 | 267 | 266
2018-08-22 22:30 | 304 | 303
2018-08-22 23:00 | 299 | 299
2018-08-22 23:30 | 276 | 275
2018-08-23 | 259 | 259
2018-08-23 00:30 | 259 | 259
2018-08-23 01:00 | 252 | 252
2018-08-23 01:30 | 246 | 246
2018-08-23 02:00 | 241 | 240
2018-08-23 02:30 | 230 | 229
2018-08-23 03:00 | 231 | 231
2018-08-23 03:30 | 226 | 226
2018-08-23 04:00 | 227 | 226
2018-08-23 04:30 | 232 | 232
2018-08-23 05:00 | 240 | 239
2018-08-23 05:30 | 254 | 254
2018-08-23 06:00 | 241 | 241
2018-08-23 06:30 | 275 | 275
2018-08-23 07:00 | 308 | 307
2018-08-23 07:30 | 321 | 320
2018-08-23 08:00 | 302 | 302
2018-08-23 08:30 | 259 | 258
2018-08-23 09:00 | 213 | 213
2018-08-23 09:30 | 187 | 187
2018-08-23 10:00 | 192 | 192
2018-08-23 10:30 | 179 | 179
2018-08-23 11:00 | 168 | 168
2018-08-23 11:30 | 161 | 161
2018-08-23 12:00 | 148 | 148
2018-08-23 12:30 | 146 | 145
2018-08-23 13:00 | 146 | 146
2018-08-23 13:30 | 140 | 139
2018-08-23 14:00 | 122 | 121
2018-08-23 14:30 | 124 | 123
2018-08-23 15:00 | 127 | 127
2018-08-23 15:30 | 131 | 130
2018-08-23 16:00 | 137 | 136
2018-08-23 16:30 | 144 | 144
2018-08-23 17:00 | 168 | 167
2018-08-23 17:30 | 109 | 107
2018-08-23 18:00 | 122 | 120
2018-08-23 18:30 | 116 | 114
2018-08-23 19:00 | 134 | 133
2018-08-23 19:30 | 140 | 139
2018-08-23 20:00 | 131 | 129
2018-08-23 20:30 | 117 | 116
2018-08-23 21:00 | 103 | 101
2018-08-23 21:30 | 134 | 134
2018-08-23 22:00 | 161 | 160
2018-08-23 22:30 | 180 | 179
2018-08-23 23:00 | 174 | 173
2018-08-23 23:30 | 164 | 163
2018-08-24 | 154 | 153
2018-08-24 00:30 | 153 | 152
2018-08-24 01:00 | 148 | 147
2018-08-24 01:30 | 142 | 141
2018-08-24 02:00 | 138 | 137
2018-08-24 02:30 | 137 | 136
2018-08-24 03:00 | 135 | 134
2018-08-24 03:30 | 137 | 136
2018-08-24 04:00 | 137 | 136
2018-08-24 04:30 | 138 | 137
2018-08-24 05:00 | 143 | 142
2018-08-24 05:30 | 146 | 145
2018-08-24 06:00 | 135 | 134
2018-08-24 06:30 | 147 | 147
2018-08-24 07:00 | 167 | 167
2018-08-24 07:30 | 170 | 169
2018-08-24 08:00 | 147 | 146
2018-08-24 08:30 | 118 | 118
2018-08-24 09:00 | 99 | 98
2018-08-24 09:30 | 93 | 92
2018-08-24 10:00 | 101 | 99
2018-08-24 10:30 | 91 | 90
2018-08-24 11:00 | 85 | 84
2018-08-24 11:30 | 82 | 80
2018-08-24 12:00 | 80 | 78
2018-08-24 12:30 | 82 | 80
2018-08-24 13:00 | 79 | 77
2018-08-24 13:30 | 77 | 75
2018-08-24 14:00 | 70 | 68
2018-08-24 14:30 | 77 | 75
2018-08-24 15:00 | 84 | 83
2018-08-24 15:30 | 80 | 78
2018-08-24 16:00 | 104 | 103
2018-08-24 16:30 | 117 | 116
2018-08-24 17:00 | 139 | 138
2018-08-24 17:30 | 159 | 159
2018-08-24 18:00 | 168 | 167
2018-08-24 18:30 | 174 | 173
2018-08-24 19:00 | 183 | 182
2018-08-24 19:30 | 179 | 178
2018-08-24 20:00 | 170 | 169
2018-08-24 20:30 | 161 | 160
2018-08-24 21:00 | 158 | 157
2018-08-24 21:30 | 155 | 154
2018-08-24 22:00 | 141 | 140
2018-08-24 22:30 | 144 | 143
2018-08-24 23:00 | 138 | 138
2018-08-24 23:30 | 130 | 129
2018-08-25 | 127 | 127
2018-08-25 00:30 | 135 | 134
2018-08-25 01:00 | 133 | 131
2018-08-25 01:30 | 127 | 126
2018-08-25 02:00 | 125 | 124
2018-08-25 02:30 | 126 | 125
2018-08-25 03:00 | 127 | 126
2018-08-25 03:30 | 124 | 123
2018-08-25 04:00 | 124 | 123
2018-08-25 04:30 | 124 | 123
2018-08-25 05:00 | 127 | 126
2018-08-25 05:30 | 130 | 129
2018-08-25 06:00 | 115 | 114
2018-08-25 06:30 | 108 | 107
2018-08-25 07:00 | 116 | 115
2018-08-25 07:30 | 111 | 110
2018-08-25 08:00 | 90 | 89
2018-08-25 08:30 | 102 | 101
2018-08-25 09:00 | 86 | 84
2018-08-25 09:30 | 85 | 83
2018-08-25 10:00 | 112 | 111
2018-08-25 10:30 | 112 | 111
2018-08-25 11:00 | 102 | 101
2018-08-25 11:30 | 97 | 95
2018-08-25 12:00 | 102 | 101
2018-08-25 12:30 | 99 | 98
2018-08-25 13:00 | 80 | 78
2018-08-25 13:30 | 100 | 99
2018-08-25 14:00 | 96 | 94
2018-08-25 14:30 | 93 | 91
2018-08-25 15:00 | 99 | 98
2018-08-25 15:30 | 106 | 105
2018-08-25 16:00 | 104 | 103
2018-08-25 16:30 | 104 | 103
2018-08-25 17:00 | 130 | 129
2018-08-25 17:30 | 154 | 153
2018-08-25 18:00 | 121 | 120
2018-08-25 18:30 | 97 | 96
2018-08-25 19:00 | 98 | 97
2018-08-25 19:30 | 117 | 116
2018-08-25 20:00 | 120 | 119
2018-08-25 20:30 | 110 | 109
2018-08-25 21:00 | 112 | 111
2018-08-25 21:30 | 163 | 163
2018-08-25 22:00 | 174 | 173
2018-08-25 22:30 | 183 | 182
2018-08-25 23:00 | 174 | 173
2018-08-25 23:30 | 163 | 162
2018-08-26 | 160 | 159
2018-08-26 00:30 | 172 | 171
2018-08-26 01:00 | 168 | 168
2018-08-26 01:30 | 165 | 164
2018-08-26 02:00 | 162 | 161
2018-08-26 02:30 | 158 | 157
2018-08-26 03:00 | 158 | 157
2018-08-26 03:30 | 157 | 156
2018-08-26 04:00 | 156 | 155
2018-08-26 04:30 | 158 | 157
2018-08-26 05:00 | 159 | 158
2018-08-26 05:30 | 162 | 161
2018-08-26 06:00 | 146 | 145
2018-08-26 06:30 | 139 | 138
2018-08-26 07:00 | 136 | 135
2018-08-26 07:30 | 126 | 125
2018-08-26 08:00 | 114 | 113
2018-08-26 08:30 | 99 | 98
2018-08-26 09:00 | 94 | 93
2018-08-26 09:30 | 90 | 89
2018-08-26 10:00 | 111 | 110
2018-08-26 10:30 | 109 | 108
2018-08-26 11:00 | 110 | 109
2018-08-26 11:30 | 100 | 99
2018-08-26 12:00 | 104 | 103
2018-08-26 12:30 | 88 | 86
2018-08-26 13:00 | 86 | 84
2018-08-26 13:30 | 90 | 89
2018-08-26 14:00 | 93 | 92
2018-08-26 14:30 | 96 | 95
2018-08-26 15:00 | 103 | 102
2018-08-26 15:30 | 84 | 83
2018-08-26 16:00 | 92 | 91
2018-08-26 16:30 | 94 | 93
2018-08-26 17:00 | 125 | 124
2018-08-26 17:30 | 159 | 159
2018-08-26 18:00 | 181 | 181
2018-08-26 18:30 | 198 | 198
2018-08-26 19:00 | 199 | 198
2018-08-26 19:30 | 202 | 201
2018-08-26 20:00 | 200 | 200
2018-08-26 20:30 | 192 | 191
2018-08-26 21:00 | 186 | 185
2018-08-26 21:30 | 177 | 177
2018-08-26 22:00 | 167 | 167
2018-08-26 22:30 | 181 | 180
2018-08-26 23:00 | 178 | 177
2018-08-26 23:30 | 168 | 167
2018-08-27 | 160 | 159
2018-08-27 00:30 | 160 | 159
2018-08-27 01:00 | 152 | 151
2018-08-27 01:30 | 145 | 144
2018-08-27 02:00 | 143 | 142
2018-08-27 02:30 | 139 | 138
2018-08-27 03:00 | 135 | 134
2018-08-27 03:30 | 138 | 138
2018-08-27 04:00 | 143 | 142
2018-08-27 04:30 | 142 | 142
2018-08-27 05:00 | 143 | 143
2018-08-27 05:30 | 152 | 152
2018-08-27 06:00 | 145 | 144
2018-08-27 06:30 | 151 | 150
2018-08-27 07:00 | 161 | 160
2018-08-27 07:30 | 152 | 151
2018-08-27 08:00 | 124 | 123
2018-08-27 08:30 | 98 | 97
2018-08-27 09:00 | 79 | 77
2018-08-27 09:30 | 64 | 61
2018-08-27 10:00 | 70 | 68
2018-08-27 10:30 | 66 | 63
2018-08-27 11:00 | 63 | 60
2018-08-27 11:30 | 65 | 61
2018-08-27 12:00 | 65 | 62
2018-08-27 12:30 | 66 | 63
2018-08-27 13:00 | 71 | 69
2018-08-27 13:30 | 73 | 71
2018-08-27 14:00 | 67 | 64
2018-08-27 14:30 | 68 | 66
2018-08-27 15:00 | 74 | 72
2018-08-27 15:30 | 84 | 83
2018-08-27 16:00 | 95 | 94
2018-08-27 16:30 | 96 | 94
2018-08-27 17:00 | 120 | 119
2018-08-27 17:30 | 150 | 149
2018-08-27 18:00 | 99 | 98
2018-08-27 18:30 | 82 | 81
2018-08-27 19:00 | 96 | 94
2018-08-27 19:30 | 103 | 102
2018-08-27 20:00 | 106 | 105
2018-08-27 20:30 | 94 | 93
2018-08-27 21:00 | 100 | 98
2018-08-27 21:30 | 162 | 162
2018-08-27 22:00 | 157 | 156
2018-08-27 22:30 | 172 | 171
2018-08-27 23:00 | 171 | 169
2018-08-27 23:30 | 158 | 157
2018-08-28 | 148 | 147
2018-08-28 00:30 | 149 | 148
2018-08-28 01:00 | 142 | 141
2018-08-28 01:30 | 139 | 137
2018-08-28 02:00 | 133 | 132
2018-08-28 02:30 | 132 | 130
2018-08-28 03:00 | 132 | 130
2018-08-28 03:30 | 132 | 130
2018-08-28 04:00 | 132 | 130
2018-08-28 04:30 | 132 | 130
2018-08-28 05:00 | 135 | 134
2018-08-28 05:30 | 141 | 140
2018-08-28 06:00 | 136 | 135
2018-08-28 06:30 | 135 | 134
2018-08-28 07:00 | 137 | 136
2018-08-28 07:30 | 129 | 128
2018-08-28 08:00 | 106 | 105
2018-08-28 08:30 | 97 | 96
2018-08-28 09:00 | 80 | 79
2018-08-28 09:30 | 79 | 78
2018-08-28 10:00 | 90 | 89
2018-08-28 10:30 | 87 | 86
2018-08-28 11:00 | 87 | 86
2018-08-28 11:30 | 87 | 86
2018-08-28 12:00 | 87 | 85
2018-08-28 12:30 | 87 | 85
2018-08-28 13:00 | 84 | 83
2018-08-28 13:30 | 82 | 81
2018-08-28 14:00 | 75 | 73
2018-08-28 14:30 | 77 | 76
2018-08-28 15:00 | 88 | 87
2018-08-28 15:30 | 95 | 94
2018-08-28 16:00 | 110 | 109
2018-08-28 16:30 | 113 | 112
2018-08-28 17:00 | 126 | 125
2018-08-28 17:30 | 122 | 121
2018-08-28 18:00 | 95 | 93
2018-08-28 18:30 | 110 | 108
2018-08-28 19:00 | 106 | 105
2018-08-28 19:30 | 110 | 108
2018-08-28 20:00 | 102 | 101
2018-08-28 20:30 | 98 | 97
2018-08-28 21:00 | 86 | 84
2018-08-28 21:30 | 92 | 91
2018-08-28 22:00 | 87 | 85
2018-08-28 22:30 | 99 | 98
2018-08-28 23:00 | 150 | 149
2018-08-28 23:30 | 158 | 156
2018-08-29 | 150 | 148
2018-08-29 00:30 | 151 | 149
2018-08-29 01:00 | 144 | 143
2018-08-29 01:30 | 138 | 137
2018-08-29 02:00 | 136 | 135
2018-08-29 02:30 | 134 | 133
2018-08-29 03:00 | 132 | 131
2018-08-29 03:30 | 132 | 131
2018-08-29 04:00 | 130 | 129
2018-08-29 04:30 | 133 | 131
2018-08-29 05:00 | 134 | 133
2018-08-29 05:30 | 143 | 142
2018-08-29 06:00 | 136 | 135
2018-08-29 06:30 | 123 | 121
2018-08-29 07:00 | 118 | 116
2018-08-29 07:30 | 100 | 99
2018-08-29 08:00 | 76 | 75
2018-08-29 08:30 | 78 | 76
2018-08-29 09:00 | 71 | 69
2018-08-29 09:30 | 72 | 69
2018-08-29 10:00 | 86 | 85
2018-08-29 10:30 | 86 | 85
2018-08-29 11:00 | 84 | 83
2018-08-29 11:30 | 86 | 84
2018-08-29 12:00 | 85 | 83
2018-08-29 12:30 | 85 | 83
2018-08-29 13:00 | 89 | 88
2018-08-29 13:30 | 88 | 86
2018-08-29 14:00 | 82 | 80
2018-08-29 14:30 | 82 | 80
2018-08-29 15:00 | 91 | 90
2018-08-29 15:30 | 102 | 101
2018-08-29 16:00 | 108 | 106
2018-08-29 16:30 | 102 | 101
2018-08-29 17:00 | 128 | 127
2018-08-29 17:30 | 156 | 155
2018-08-29 18:00 | 174 | 173
2018-08-29 18:30 | 194 | 193
2018-08-29 19:00 | 207 | 206
2018-08-29 19:30 | 188 | 187
2018-08-29 20:00 | 173 | 172
2018-08-29 20:30 | 167 | 166
2018-08-29 21:00 | 164 | 163
2018-08-29 21:30 | 153 | 152
2018-08-29 22:00 | 151 | 150
2018-08-29 22:30 | 162 | 161
2018-08-29 23:00 | 151 | 150
2018-08-29 23:30 | 152 | 151
2018-08-30 | 148 | 146
2018-08-30 00:30 | 146 | 145
2018-08-30 01:00 | 134 | 132
2018-08-30 01:30 | 129 | 128
2018-08-30 02:00 | 125 | 124
2018-08-30 02:30 | 121 | 119
2018-08-30 03:00 | 118 | 116
2018-08-30 03:30 | 117 | 116
2018-08-30 04:00 | 127 | 126
2018-08-30 04:30 | 133 | 132
2018-08-30 05:00 | 134 | 133
2018-08-30 05:30 | 139 | 137
2018-08-30 06:00 | 118 | 116
2018-08-30 06:30 | 134 | 133
2018-08-30 07:00 | 128 | 127
2018-08-30 07:30 | 111 | 109
2018-08-30 08:00 | 96 | 94
2018-08-30 08:30 | 90 | 88
2018-08-30 09:00 | 80 | 78
2018-08-30 09:30 | 85 | 84
2018-08-30 10:00 | 124 | 123
2018-08-30 10:30 | 113 | 112
2018-08-30 11:00 | 110 | 109
2018-08-30 11:30 | 99 | 97
2018-08-30 12:00 | 91 | 90
2018-08-30 12:30 | 92 | 91
2018-08-30 13:00 | 93 | 92
2018-08-30 13:30 | 93 | 91
2018-08-30 14:00 | 94 | 93
2018-08-30 14:30 | 92 | 91
2018-08-30 15:00 | 91 | 89
2018-08-30 15:30 | 91 | 90
2018-08-30 16:00 | 107 | 106
2018-08-30 16:30 | 109 | 107
2018-08-30 17:00 | 128 | 128
2018-08-30 17:30 | 150 | 149
2018-08-30 18:00 | 173 | 172
2018-08-30 18:30 | 192 | 191
2018-08-30 19:00 | 197 | 196
2018-08-30 19:30 | 186 | 185
2018-08-30 20:00 | 178 | 177
2018-08-30 20:30 | 163 | 161
2018-08-30 21:00 | 162 | 161
2018-08-30 21:30 | 158 | 157
2018-08-30 22:00 | 151 | 150
2018-08-30 22:30 | 168 | 167
2018-08-30 23:00 | 162 | 160
2018-08-30 23:30 | 154 | 152
2018-08-31 | 147 | 146
2018-08-31 00:30 | 143 | 142
2018-08-31 01:00 | 127 | 126
2018-08-31 01:30 | 127 | 125
2018-08-31 02:00 | 125 | 123
2018-08-31 02:30 | 126 | 125
2018-08-31 03:00 | 128 | 126
2018-08-31 03:30 | 127 | 126
2018-08-31 04:00 | 123 | 122
2018-08-31 04:30 | 128 | 126
2018-08-31 05:00 | 135 | 134
2018-08-31 05:30 | 143 | 142
2018-08-31 06:00 | 135 | 134
2018-08-31 06:30 | 129 | 128
2018-08-31 07:00 | 142 | 141
2018-08-31 07:30 | 135 | 133
2018-08-31 08:00 | 126 | 125
2018-08-31 08:30 | 113 | 112
2018-08-31 09:00 | 97 | 96
2018-08-31 09:30 | 80 | 79
2018-08-31 10:00 | 93 | 92
2018-08-31 10:30 | 89 | 88
2018-08-31 11:00 | 81 | 80
2018-08-31 11:30 | 80 | 79
2018-08-31 12:00 | 78 | 76
2018-08-31 12:30 | 82 | 80
2018-08-31 13:00 | 79 | 78
2018-08-31 13:30 | 79 | 77
2018-08-31 14:00 | 76 | 75
2018-08-31 14:30 | 74 | 73
2018-08-31 15:00 | 71 | 70
2018-08-31 15:30 | 78 | 76
2018-08-31 16:00 | 94 | 93
2018-08-31 16:30 | 96 | 95
2018-08-31 17:00 | 117 | 116
2018-08-31 17:30 | 141 | 140
2018-08-31 18:00 | 166 | 165
2018-08-31 18:30 | 177 | 176
2018-08-31 19:00 | 183 | 182
2018-08-31 19:30 | 190 | 188
2018-08-31 20:00 | 182 | 180
2018-08-31 20:30 | 172 | 171
2018-08-31 21:00 | 164 | 163
2018-08-31 21:30 | 158 | 156
2018-08-31 22:00 | 150 | 148
2018-08-31 22:30 | 160 | 159
2018-08-31 23:00 | 155 | 154
2018-08-31 23:30 | 152 | 150
2018-09-01 | 144 | 143
2018-09-01 00:30 | 154 | 153
2018-09-01 01:00 | 150 | 149
2018-09-01 01:30 | 145 | 144
2018-09-01 02:00 | 139 | 138
2018-09-01 02:30 | 138 | 137
2018-09-01 03:00 | 138 | 137
2018-09-01 03:30 | 137 | 135
2018-09-01 04:00 | 136 | 135
2018-09-01 04:30 | 138 | 137
2018-09-01 05:00 | 141 | 139
2018-09-01 05:30 | 144 | 142
2018-09-01 06:00 | 132 | 130
2018-09-01 06:30 | 133 | 132
2018-09-01 07:00 | 138 | 137
2018-09-01 07:30 | 131 | 130
2018-09-01 08:00 | 115 | 114
2018-09-01 08:30 | 79 | 77
2018-09-01 09:00 | 76 | 74
2018-09-01 09:30 | 69 | 67
2018-09-01 10:00 | 78 | 76
2018-09-01 10:30 | 76 | 75
2018-09-01 11:00 | 71 | 69
2018-09-01 11:30 | 67 | 65
2018-09-01 12:00 | 66 | 64
2018-09-01 12:30 | 66 | 64
2018-09-01 13:00 | 65 | 62
2018-09-01 13:30 | 62 | 59
2018-09-01 14:00 | 57 | 53
2018-09-01 14:30 | 57 | 54
2018-09-01 15:00 | 67 | 65
2018-09-01 15:30 | 81 | 79
2018-09-01 16:00 | 97 | 96
2018-09-01 16:30 | 98 | 97
2018-09-01 17:00 | 117 | 116
2018-09-01 17:30 | 139 | 138
2018-09-01 18:00 | 166 | 165
2018-09-01 18:30 | 182 | 181
2018-09-01 19:00 | 185 | 183
2018-09-01 19:30 | 185 | 184
2018-09-01 20:00 | 179 | 177
2018-09-01 20:30 | 170 | 168
2018-09-01 21:00 | 162 | 160
2018-09-01 21:30 | 151 | 149
2018-09-01 22:00 | 145 | 143
2018-09-01 22:30 | 162 | 160
2018-09-01 23:00 | 163 | 161
2018-09-01 23:30 | 154 | 152
2018-09-02 | 157 | 155
2018-09-02 00:30 | 159 | 158
2018-09-02 01:00 | 145 | 143
2018-09-02 01:30 | 143 | 141
2018-09-02 02:00 | 143 | 141
2018-09-02 02:30 | 141 | 139
2018-09-02 03:00 | 139 | 138
2018-09-02 03:30 | 138 | 137
2018-09-02 04:00 | 138 | 136
2018-09-02 04:30 | 135 | 134
2018-09-02 05:00 | 139 | 137
2018-09-02 05:30 | 143 | 141
2018-09-02 06:00 | 126 | 124
2018-09-02 06:30 | 129 | 128
2018-09-02 07:00 | 128 | 126
2018-09-02 07:30 | 113 | 111
2018-09-02 08:00 | 96 | 94
2018-09-02 08:30 | 80 | 78
2018-09-02 09:00 | 65 | 63
2018-09-02 09:30 | 59 | 56
2018-09-02 10:00 | 71 | 69
2018-09-02 10:30 | 69 | 67
2018-09-02 11:00 | 63 | 61
2018-09-02 11:30 | 62 | 60
2018-09-02 12:00 | 61 | 58
2018-09-02 12:30 | 62 | 60
2018-09-02 13:00 | 61 | 58
2018-09-02 13:30 | 61 | 57
2018-09-02 14:00 | 54 | 50
2018-09-02 14:30 | 56 | 52
2018-09-02 15:00 | 63 | 60
2018-09-02 15:30 | 69 | 67
2018-09-02 16:00 | 83 | 82
2018-09-02 16:30 | 86 | 85
2018-09-02 17:00 | 107 | 106
2018-09-02 17:30 | 132 | 131
2018-09-02 18:00 | 160 | 159
2018-09-02 18:30 | 161 | 159
2018-09-02 19:00 | 167 | 165
2018-09-02 19:30 | 171 | 169
2018-09-02 20:00 | 168 | 166
2018-09-02 20:30 | 165 | 164
2018-09-02 21:00 | 165 | 164
2018-09-02 21:30 | 154 | 153
2018-09-02 22:00 | 141 | 140
2018-09-02 22:30 | 154 | 152
2018-09-02 23:00 | 150 | 149
2018-09-02 23:30 | 152 | 151
2018-09-03 | 148 | 147
2018-09-03 00:30 | 149 | 148
2018-09-03 01:00 | 144 | 143
2018-09-03 01:30 | 144 | 143
2018-09-03 02:00 | 140 | 139
2018-09-03 02:30 | 137 | 136
2018-09-03 03:00 | 139 | 138
2018-09-03 03:30 | 137 | 136
2018-09-03 04:00 | 138 | 136
2018-09-03 04:30 | 137 | 136
2018-09-03 05:00 | 142 | 141
2018-09-03 05:30 | 146 | 144
2018-09-03 06:00 | 135 | 133
2018-09-03 06:30 | 137 | 135
2018-09-03 07:00 | 135 | 134
2018-09-03 07:30 | 118 | 117
2018-09-03 08:00 | 74 | 73
2018-09-03 08:30 | 66 | 64
2018-09-03 09:00 | 55 | 50
2018-09-03 09:30 | 48 | 42
2018-09-03 10:00 | 60 | 57
2018-09-03 10:30 | 62 | 59
2018-09-03 11:00 | 53 | 49
2018-09-03 11:30 | 55 | 51
2018-09-03 12:00 | 61 | 58
2018-09-03 12:30 | 65 | 63
2018-09-03 13:00 | 67 | 65
2018-09-03 13:30 | 69 | 66
2018-09-03 14:00 | 71 | 69
2018-09-03 14:30 | 81 | 79
2018-09-03 15:00 | 86 | 85
2018-09-03 15:30 | 92 | 91
2018-09-03 16:00 | 104 | 104
2018-09-03 16:30 | 76 | 75
2018-09-03 17:00 | 86 | 84
2018-09-03 17:30 | 74 | 73
2018-09-03 18:00 | 68 | 67
2018-09-03 18:30 | 103 | 102
2018-09-03 19:00 | 115 | 114
2018-09-03 19:30 | 109 | 108
2018-09-03 20:00 | 115 | 114
2018-09-03 20:30 | 101 | 100
2018-09-03 21:00 | 101 | 100
2018-09-03 21:30 | 95 | 94
2018-09-03 22:00 | 84 | 83
2018-09-03 22:30 | 110 | 109
2018-09-03 23:00 | 141 | 140
2018-09-03 23:30 | 172 | 171
2018-09-04 | 169 | 168
2018-09-04 00:30 | 170 | 169
2018-09-04 01:00 | 165 | 164
2018-09-04 01:30 | 161 | 160
2018-09-04 02:00 | 157 | 156
2018-09-04 02:30 | 157 | 156
2018-09-04 03:00 | 155 | 154
2018-09-04 03:30 | 154 | 153
2018-09-04 04:00 | 154 | 154
2018-09-04 04:30 | 158 | 158
2018-09-04 05:00 | 158 | 157
2018-09-04 05:30 | 166 | 166
2018-09-04 06:00 | 162 | 161
2018-09-04 06:30 | 177 | 176
2018-09-04 07:00 | 154 | 153
2018-09-04 07:30 | 155 | 155
2018-09-04 08:00 | 137 | 136
2018-09-04 08:30 | 127 | 126
2018-09-04 09:00 | 114 | 113
2018-09-04 09:30 | 110 | 109
2018-09-04 10:00 | 102 | 101
2018-09-04 10:30 | 99 | 98
2018-09-04 11:00 | 106 | 105
2018-09-04 11:30 | 101 | 100
2018-09-04 12:00 | 101 | 100
2018-09-04 12:30 | 106 | 105
2018-09-04 13:00 | 109 | 108
2018-09-04 13:30 | 114 | 113
2018-09-04 14:00 | 113 | 112
2018-09-04 14:30 | 109 | 108
2018-09-04 15:00 | 123 | 122
2018-09-04 15:30 | 124 | 123
2018-09-04 16:00 | 112 | 111
2018-09-04 16:30 | 117 | 116
2018-09-04 17:00 | 144 | 143
2018-09-04 17:30 | 147 | 146
2018-09-04 18:00 | 113 | 112
2018-09-04 18:30 | 116 | 115
2018-09-04 19:00 | 120 | 119
2018-09-04 19:30 | 131 | 130
2018-09-04 20:00 | 154 | 153
2018-09-04 20:30 | 174 | 173
2018-09-04 21:00 | 164 | 163
2018-09-04 21:30 | 150 | 150
2018-09-04 22:00 | 140 | 139
2018-09-04 22:30 | 137 | 136
2018-09-04 23:00 | 182 | 181
2018-09-04 23:30 | 183 | 182
2018-09-05 | 175 | 174
2018-09-05 00:30 | 172 | 171
2018-09-05 01:00 | 165 | 164
2018-09-05 01:30 | 161 | 160
2018-09-05 02:00 | 158 | 157
2018-09-05 02:30 | 158 | 157
2018-09-05 03:00 | 157 | 156
2018-09-05 03:30 | 156 | 156
2018-09-05 04:00 | 156 | 155
2018-09-05 04:30 | 159 | 158
2018-09-05 05:00 | 163 | 163
2018-09-05 05:30 | 170 | 169
2018-09-05 06:00 | 169 | 168
2018-09-05 06:30 | 182 | 181
2018-09-05 07:00 | 165 | 164
2018-09-05 07:30 | 151 | 150
2018-09-05 08:00 | 131 | 131
2018-09-05 08:30 | 108 | 107
2018-09-05 09:00 | 112 | 111
2018-09-05 09:30 | 109 | 108
2018-09-05 10:00 | 117 | 117
2018-09-05 10:30 | 127 | 126
2018-09-05 11:00 | 113 | 112
2018-09-05 11:30 | 110 | 109
2018-09-05 12:00 | 102 | 101
2018-09-05 12:30 | 104 | 103
2018-09-05 13:00 | 106 | 105
2018-09-05 13:30 | 102 | 101
2018-09-05 14:00 | 97 | 96
2018-09-05 14:30 | 97 | 96
2018-09-05 15:00 | 104 | 103
2018-09-05 15:30 | 114 | 113
2018-09-05 16:00 | 118 | 117
2018-09-05 16:30 | 121 | 120
2018-09-05 17:00 | 161 | 160
2018-09-05 17:30 | 170 | 169
2018-09-05 18:00 | 156 | 155
2018-09-05 18:30 | 176 | 175
2018-09-05 19:00 | 197 | 196
2018-09-05 19:30 | 193 | 192
2018-09-05 20:00 | 187 | 186
2018-09-05 20:30 | 186 | 185
2018-09-05 21:00 | 188 | 187
2018-09-05 21:30 | 190 | 189
2018-09-05 22:00 | 187 | 186
2018-09-05 22:30 | 203 | 202
2018-09-05 23:00 | 194 | 193
2018-09-05 23:30 | 177 | 176
2018-09-06 | 168 | 167
2018-09-06 00:30 | 166 | 165
2018-09-06 01:00 | 160 | 159
2018-09-06 01:30 | 157 | 156
2018-09-06 02:00 | 152 | 151
2018-09-06 02:30 | 147 | 146
2018-09-06 03:00 | 143 | 142
2018-09-06 03:30 | 144 | 143
2018-09-06 04:00 | 146 | 145
2018-09-06 04:30 | 147 | 146
2018-09-06 05:00 | 153 | 152
2018-09-06 05:30 | 165 | 165
2018-09-06 06:00 | 156 | 155
2018-09-06 06:30 | 159 | 158
2018-09-06 07:00 | 137 | 136
2018-09-06 07:30 | 125 | 124
2018-09-06 08:00 | 117 | 116
2018-09-06 08:30 | 107 | 106
2018-09-06 09:00 | 115 | 114
2018-09-06 09:30 | 112 | 111
2018-09-06 10:00 | 109 | 109
2018-09-06 10:30 | 111 | 111
2018-09-06 11:00 | 114 | 113
2018-09-06 11:30 | 108 | 107
2018-09-06 12:00 | 112 | 111
2018-09-06 12:30 | 136 | 135
2018-09-06 13:00 | 136 | 136
2018-09-06 13:30 | 151 | 151
2018-09-06 14:00 | 140 | 140
2018-09-06 14:30 | 135 | 134
2018-09-06 15:00 | 135 | 135
2018-09-06 15:30 | 135 | 134
2018-09-06 16:00 | 153 | 153
2018-09-06 16:30 | 140 | 139
2018-09-06 17:00 | 148 | 147
2018-09-06 17:30 | 169 | 168
2018-09-06 18:00 | 197 | 197
2018-09-06 18:30 | 219 | 219
2018-09-06 19:00 | 207 | 206
2018-09-06 19:30 | 206 | 205
2018-09-06 20:00 | 201 | 201
2018-09-06 20:30 | 196 | 195
2018-09-06 21:00 | 178 | 177
2018-09-06 21:30 | 194 | 193
2018-09-06 22:00 | 187 | 186
2018-09-06 22:30 | 208 | 207
2018-09-06 23:00 | 205 | 204
2018-09-06 23:30 | 195 | 194
2018-09-07 | 187 | 186
2018-09-07 00:30 | 187 | 186
2018-09-07 01:00 | 179 | 178
2018-09-07 01:30 | 174 | 174
2018-09-07 02:00 | 171 | 170
2018-09-07 02:30 | 166 | 165
2018-09-07 03:00 | 164 | 163
2018-09-07 03:30 | 163 | 162
2018-09-07 04:00 | 162 | 161
2018-09-07 04:30 | 162 | 161
2018-09-07 05:00 | 170 | 169
2018-09-07 05:30 | 175 | 174
2018-09-07 06:00 | 171 | 170
2018-09-07 06:30 | 180 | 179
2018-09-07 07:00 | 159 | 158
2018-09-07 07:30 | 146 | 145
2018-09-07 08:00 | 137 | 136
2018-09-07 08:30 | 137 | 136
2018-09-07 09:00 | 118 | 118
2018-09-07 09:30 | 88 | 86
2018-09-07 10:00 | 82 | 80
2018-09-07 10:30 | 86 | 84
2018-09-07 11:00 | 87 | 85
2018-09-07 11:30 | 88 | 86
2018-09-07 12:00 | 89 | 87
2018-09-07 12:30 | 88 | 86
2018-09-07 13:00 | 87 | 85
2018-09-07 13:30 | 89 | 87
2018-09-07 14:00 | 85 | 84
2018-09-07 14:30 | 90 | 88
2018-09-07 15:00 | 98 | 97
2018-09-07 15:30 | 113 | 112
2018-09-07 16:00 | 124 | 124
2018-09-07 16:30 | 134 | 133
2018-09-07 17:00 | 158 | 157
2018-09-07 17:30 | 195 | 195
2018-09-07 18:00 | 212 | 211
2018-09-07 18:30 | 203 | 202
2018-09-07 19:00 | 210 | 209
2018-09-07 19:30 | 219 | 217
2018-09-07 20:00 | 211 | 210
2018-09-07 20:30 | 205 | 204
2018-09-07 21:00 | 205 | 204
2018-09-07 21:30 | 194 | 193
2018-09-07 22:00 | 179 | 178
2018-09-07 22:30 | 190 | 189
2018-09-07 23:00 | 190 | 189
2018-09-07 23:30 | 180 | 180
2018-09-08 | 172 | 171
2018-09-08 00:30 | 164 | 163
2018-09-08 01:00 | 156 | 156
2018-09-08 01:30 | 156 | 156
2018-09-08 02:00 | 152 | 151
2018-09-08 02:30 | 147 | 146
2018-09-08 03:00 | 140 | 140
2018-09-08 03:30 | 135 | 134
2018-09-08 04:00 | 129 | 127
2018-09-08 04:30 | 126 | 125
2018-09-08 05:00 | 126 | 125
2018-09-08 05:30 | 133 | 132
2018-09-08 06:00 | 125 | 124
2018-09-08 06:30 | 126 | 125
2018-09-08 07:00 | 127 | 126
2018-09-08 07:30 | 114 | 113
2018-09-08 08:00 | 97 | 96
2018-09-08 08:30 | 89 | 87
2018-09-08 09:00 | 89 | 87
2018-09-08 09:30 | 78 | 77
2018-09-08 10:00 | 75 | 73
2018-09-08 10:30 | 84 | 82
2018-09-08 11:00 | 83 | 82
2018-09-08 11:30 | 87 | 85
2018-09-08 12:00 | 84 | 82
2018-09-08 12:30 | 86 | 84
2018-09-08 13:00 | 81 | 79
2018-09-08 13:30 | 81 | 79
2018-09-08 14:00 | 67 | 64
2018-09-08 14:30 | 64 | 60
2018-09-08 15:00 | 71 | 68
2018-09-08 15:30 | 80 | 78
2018-09-08 16:00 | 100 | 99
2018-09-08 16:30 | 106 | 105
2018-09-08 17:00 | 127 | 126
2018-09-08 17:30 | 162 | 161
2018-09-08 18:00 | 186 | 185
2018-09-08 18:30 | 216 | 215
2018-09-08 19:00 | 232 | 231
2018-09-08 19:30 | 220 | 220
2018-09-08 20:00 | 210 | 210
2018-09-08 20:30 | 195 | 194
2018-09-08 21:00 | 188 | 187
2018-09-08 21:30 | 181 | 180
2018-09-08 22:00 | 177 | 176
2018-09-08 22:30 | 195 | 194
2018-09-08 23:00 | 192 | 191
2018-09-08 23:30 | 182 | 181
2018-09-09 | 178 | 176
2018-09-09 00:30 | 176 | 175
2018-09-09 01:00 | 168 | 167
2018-09-09 01:30 | 163 | 161
2018-09-09 02:00 | 161 | 160
2018-09-09 02:30 | 157 | 156
2018-09-09 03:00 | 156 | 155
2018-09-09 03:30 | 158 | 157
2018-09-09 04:00 | 157 | 156
2018-09-09 04:30 | 158 | 157
2018-09-09 05:00 | 155 | 154
2018-09-09 05:30 | 152 | 151
2018-09-09 06:00 | 141 | 139
2018-09-09 06:30 | 145 | 144
2018-09-09 07:00 | 144 | 143
2018-09-09 07:30 | 115 | 114
2018-09-09 08:00 | 85 | 84
2018-09-09 08:30 | 72 | 69
2018-09-09 09:00 | 61 | 56
2018-09-09 09:30 | 57 | 51
2018-09-09 10:00 | 54 | 46
2018-09-09 10:30 | 53 | 46
2018-09-09 11:00 | 47 | 39
2018-09-09 11:30 | 49 | 41
2018-09-09 12:00 | 53 | 46
2018-09-09 12:30 | 55 | 50
2018-09-09 13:00 | 55 | 49
2018-09-09 13:30 | 56 | 51
2018-09-09 14:00 | 54 | 49
2018-09-09 14:30 | 55 | 50
2018-09-09 15:00 | 62 | 59
2018-09-09 15:30 | 69 | 67
2018-09-09 16:00 | 85 | 83
2018-09-09 16:30 | 111 | 110
2018-09-09 17:00 | 130 | 129
2018-09-09 17:30 | 167 | 166
2018-09-09 18:00 | 200 | 199
2018-09-09 18:30 | 195 | 194
2018-09-09 19:00 | 192 | 191
2018-09-09 19:30 | 203 | 202
2018-09-09 20:00 | 172 | 171
2018-09-09 20:30 | 167 | 166
2018-09-09 21:00 | 175 | 174
2018-09-09 21:30 | 169 | 169
2018-09-09 22:00 | 162 | 161
2018-09-09 22:30 | 168 | 167
2018-09-09 23:00 | 160 | 159
2018-09-09 23:30 | 152 | 151
2018-09-10 | 147 | 146
2018-09-10 00:30 | 145 | 144
2018-09-10 01:00 | 138 | 137
2018-09-10 01:30 | 135 | 134
2018-09-10 02:00 | 131 | 130
2018-09-10 02:30 | 130 | 129
2018-09-10 03:00 | 128 | 127
2018-09-10 03:30 | 128 | 127
2018-09-10 04:00 | 129 | 128
2018-09-10 04:30 | 130 | 129
2018-09-10 05:00 | 131 | 130
2018-09-10 05:30 | 138 | 137
2018-09-10 06:00 | 132 | 131
2018-09-10 06:30 | 146 | 145
2018-09-10 07:00 | 141 | 140
2018-09-10 07:30 | 136 | 135
2018-09-10 08:00 | 117 | 116
2018-09-10 08:30 | 98 | 97
2018-09-10 09:00 | 83 | 81
2018-09-10 09:30 | 74 | 71
2018-09-10 10:00 | 69 | 66
2018-09-10 10:30 | 66 | 61
2018-09-10 11:00 | 63 | 58
2018-09-10 11:30 | 65 | 60
2018-09-10 12:00 | 65 | 60
2018-09-10 12:30 | 64 | 60
2018-09-10 13:00 | 64 | 60
2018-09-10 13:30 | 67 | 64
2018-09-10 14:00 | 63 | 58
2018-09-10 14:30 | 60 | 55
2018-09-10 15:00 | 62 | 58
2018-09-10 15:30 | 71 | 68
2018-09-10 16:00 | 80 | 78
2018-09-10 16:30 | 87 | 86
2018-09-10 17:00 | 129 | 128
2018-09-10 17:30 | 178 | 178
2018-09-10 18:00 | 207 | 206
2018-09-10 18:30 | 186 | 185
2018-09-10 19:00 | 172 | 170
2018-09-10 19:30 | 195 | 194
2018-09-10 20:00 | 196 | 196
2018-09-10 20:30 | 185 | 185
2018-09-10 21:00 | 175 | 174
2018-09-10 21:30 | 163 | 162
2018-09-10 22:00 | 151 | 150
2018-09-10 22:30 | 164 | 164
2018-09-10 23:00 | 156 | 155
2018-09-10 23:30 | 147 | 147
2018-09-11 | 138 | 138
2018-09-11 00:30 | 137 | 136
2018-09-11 01:00 | 130 | 129
2018-09-11 01:30 | 127 | 125
2018-09-11 02:00 | 118 | 117
2018-09-11 02:30 | 114 | 113
2018-09-11 03:00 | 116 | 115
2018-09-11 03:30 | 116 | 115
2018-09-11 04:00 | 117 | 116
2018-09-11 04:30 | 120 | 119
2018-09-11 05:00 | 125 | 124
2018-09-11 05:30 | 132 | 131
2018-09-11 06:00 | 128 | 127
2018-09-11 06:30 | 143 | 142
2018-09-11 07:00 | 137 | 136
2018-09-11 07:30 | 126 | 125
2018-09-11 08:00 | 110 | 109
2018-09-11 08:30 | 109 | 109
2018-09-11 09:00 | 91 | 90
2018-09-11 09:30 | 83 | 81
2018-09-11 10:00 | 90 | 88
2018-09-11 10:30 | 89 | 87
2018-09-11 11:00 | 74 | 72
2018-09-11 11:30 | 63 | 58
2018-09-11 12:00 | 64 | 60
2018-09-11 12:30 | 62 | 57
2018-09-11 13:00 | 76 | 74
2018-09-11 13:30 | 80 | 78
2018-09-11 14:00 | 73 | 71
2018-09-11 14:30 | 78 | 77
2018-09-11 15:00 | 79 | 77
2018-09-11 15:30 | 73 | 71
2018-09-11 16:00 | 79 | 78
2018-09-11 16:30 | 94 | 93
2018-09-11 17:00 | 120 | 119
2018-09-11 17:30 | 136 | 135
2018-09-11 18:00 | 166 | 165
2018-09-11 18:30 | 199 | 198
2018-09-11 19:00 | 213 | 213
2018-09-11 19:30 | 213 | 212
2018-09-11 20:00 | 205 | 204
2018-09-11 20:30 | 204 | 203
2018-09-11 21:00 | 200 | 199
2018-09-11 21:30 | 189 | 188
2018-09-11 22:00 | 178 | 177
2018-09-11 22:30 | 177 | 175
2018-09-11 23:00 | 162 | 162
2018-09-11 23:30 | 154 | 153
2018-09-12 | 146 | 145
2018-09-12 00:30 | 144 | 143
2018-09-12 01:00 | 137 | 136
2018-09-12 01:30 | 133 | 132
2018-09-12 02:00 | 99 | 97
2018-09-12 02:30 | 91 | 89
2018-09-12 03:00 | 91 | 89
2018-09-12 03:30 | 96 | 94
2018-09-12 04:00 | 117 | 115
2018-09-12 04:30 | 129 | 128
2018-09-12 05:00 | 130 | 129
2018-09-12 05:30 | 139 | 138
2018-09-12 06:00 | 138 | 137
2018-09-12 06:30 | 147 | 146
2018-09-12 07:00 | 150 | 150
2018-09-12 07:30 | 156 | 155
2018-09-12 08:00 | 146 | 145
2018-09-12 08:30 | 136 | 135
2018-09-12 09:00 | 132 | 131
2018-09-12 09:30 | 111 | 110
2018-09-12 10:00 | 100 | 99
2018-09-12 10:30 | 100 | 99
2018-09-12 11:00 | 94 | 93
2018-09-12 11:30 | 77 | 76
2018-09-12 12:00 | 81 | 80
2018-09-12 12:30 | 83 | 82
2018-09-12 13:00 | 95 | 95
2018-09-12 13:30 | 117 | 116
2018-09-12 14:00 | 107 | 105
2018-09-12 14:30 | 96 | 95
2018-09-12 15:00 | 102 | 101
2018-09-12 15:30 | 116 | 115
2018-09-12 16:00 | 124 | 123
2018-09-12 16:30 | 139 | 138
2018-09-12 17:00 | 160 | 159
2018-09-12 17:30 | 175 | 174
2018-09-12 18:00 | 199 | 198
2018-09-12 18:30 | 215 | 215
2018-09-12 19:00 | 221 | 221
2018-09-12 19:30 | 215 | 214
2018-09-12 20:00 | 208 | 208
2018-09-12 20:30 | 210 | 210
2018-09-12 21:00 | 206 | 205
2018-09-12 21:30 | 197 | 196
2018-09-12 22:00 | 183 | 182
2018-09-12 22:30 | 180 | 178
2018-09-12 23:00 | 173 | 171
2018-09-12 23:30 | 164 | 163
2018-09-13 | 155 | 154
2018-09-13 00:30 | 150 | 149
2018-09-13 01:00 | 142 | 141
2018-09-13 01:30 | 140 | 138
2018-09-13 02:00 | 137 | 136
2018-09-13 02:30 | 134 | 132
2018-09-13 03:00 | 135 | 134
2018-09-13 03:30 | 132 | 131
2018-09-13 04:00 | 135 | 135
2018-09-13 04:30 | 139 | 138
2018-09-13 05:00 | 144 | 143
2018-09-13 05:30 | 154 | 154
2018-09-13 06:00 | 149 | 149
2018-09-13 06:30 | 160 | 160
2018-09-13 07:00 | 157 | 156
2018-09-13 07:30 | 158 | 157
2018-09-13 08:00 | 138 | 137
2018-09-13 08:30 | 120 | 119
2018-09-13 09:00 | 118 | 118
2018-09-13 09:30 | 111 | 111
2018-09-13 10:00 | 108 | 107
2018-09-13 10:30 | 97 | 96
2018-09-13 11:00 | 103 | 102
2018-09-13 11:30 | 100 | 99
2018-09-13 12:00 | 76 | 74
2018-09-13 12:30 | 85 | 84
2018-09-13 13:00 | 90 | 89
2018-09-13 13:30 | 98 | 97
2018-09-13 14:00 | 88 | 87
2018-09-13 14:30 | 76 | 75
2018-09-13 15:00 | 88 | 87
2018-09-13 15:30 | 96 | 94
2018-09-13 16:00 | 107 | 106
2018-09-13 16:30 | 109 | 108
2018-09-13 17:00 | 132 | 131
2018-09-13 17:30 | 162 | 161
2018-09-13 18:00 | 193 | 192
2018-09-13 18:30 | 211 | 210
2018-09-13 19:00 | 224 | 223
2018-09-13 19:30 | 221 | 219
2018-09-13 20:00 | 208 | 207
2018-09-13 20:30 | 202 | 201
2018-09-13 21:00 | 201 | 200
2018-09-13 21:30 | 191 | 189
2018-09-13 22:00 | 178 | 177
2018-09-13 22:30 | 174 | 173
2018-09-13 23:00 | 164 | 163
2018-09-13 23:30 | 155 | 154
2018-09-14 | 147 | 146
2018-09-14 00:30 | 145 | 144
2018-09-14 01:00 | 142 | 140
2018-09-14 01:30 | 137 | 136
2018-09-14 02:00 | 131 | 130
2018-09-14 02:30 | 130 | 129
2018-09-14 03:00 | 133 | 132
2018-09-14 03:30 | 129 | 128
2018-09-14 04:00 | 129 | 128
2018-09-14 04:30 | 133 | 132
2018-09-14 05:00 | 136 | 135
2018-09-14 05:30 | 140 | 139
2018-09-14 06:00 | 133 | 132
2018-09-14 06:30 | 143 | 142
2018-09-14 07:00 | 133 | 132
2018-09-14 07:30 | 117 | 116
2018-09-14 08:00 | 96 | 95
2018-09-14 08:30 | 80 | 78
2018-09-14 09:00 | 73 | 70
2018-09-14 09:30 | 65 | 60
2018-09-14 10:00 | 36 | 30
2018-09-14 10:30 | 11 | 11
2018-09-14 11:00 | 8 | 7
2018-09-14 11:30 | 1 | 1
2018-09-14 12:00 | 5 | 5
2018-09-14 12:30 | 19 | 15
2018-09-14 13:00 | 33 | 25
2018-09-14 13:30 | 34 | 31
2018-09-14 14:00 | 35 | 27
2018-09-14 14:30 | 35 | 29
2018-09-14 15:00 | 42 | 37
2018-09-14 15:30 | 60 | 54
2018-09-14 16:00 | 82 | 80
2018-09-14 16:30 | 98 | 97
2018-09-14 17:00 | 119 | 118
2018-09-14 17:30 | 153 | 153
2018-09-14 18:00 | 183 | 182
2018-09-14 18:30 | 198 | 197
2018-09-14 19:00 | 204 | 204
2018-09-14 19:30 | 200 | 200
2018-09-14 20:00 | 163 | 162
2018-09-14 20:30 | 151 | 150
2018-09-14 21:00 | 148 | 147
2018-09-14 21:30 | 143 | 142
2018-09-14 22:00 | 138 | 137
2018-09-14 22:30 | 142 | 141
2018-09-14 23:00 | 133 | 132
2018-09-14 23:30 | 123 | 121
2018-09-15 | 112 | 111
2018-09-15 00:30 | 111 | 110
2018-09-15 01:00 | 103 | 102
2018-09-15 01:30 | 109 | 107
2018-09-15 02:00 | 123 | 121
2018-09-15 02:30 | 129 | 128
2018-09-15 03:00 | 127 | 126
2018-09-15 03:30 | 127 | 125
2018-09-15 04:00 | 129 | 128
2018-09-15 04:30 | 129 | 128
2018-09-15 05:00 | 127 | 126
2018-09-15 05:30 | 133 | 132
2018-09-15 06:00 | 140 | 139
2018-09-15 06:30 | 135 | 134
2018-09-15 07:00 | 113 | 112
2018-09-15 07:30 | 107 | 106
2018-09-15 08:00 | 91 | 90
2018-09-15 08:30 | 77 | 75
2018-09-15 09:00 | 75 | 72
2018-09-15 09:30 | 77 | 75
2018-09-15 10:00 | 61 | 57
2018-09-15 10:30 | 70 | 67
2018-09-15 11:00 | 78 | 76
2018-09-15 11:30 | 62 | 58
2018-09-15 12:00 | 52 | 44
2018-09-15 12:30 | 51 | 43
2018-09-15 13:00 | 51 | 44
2018-09-15 13:30 | 48 | 40
2018-09-15 14:00 | 48 | 40
2018-09-15 14:30 | 50 | 41
2018-09-15 15:00 | 57 | 52
2018-09-15 15:30 | 71 | 69
2018-09-15 16:00 | 81 | 79
2018-09-15 16:30 | 98 | 97
2018-09-15 17:00 | 123 | 122
2018-09-15 17:30 | 156 | 156
2018-09-15 18:00 | 188 | 187
2018-09-15 18:30 | 206 | 206
2018-09-15 19:00 | 209 | 208
2018-09-15 19:30 | 209 | 208
2018-09-15 20:00 | 208 | 208
2018-09-15 20:30 | 205 | 204
2018-09-15 21:00 | 203 | 202
2018-09-15 21:30 | 193 | 192
2018-09-15 22:00 | 185 | 184
2018-09-15 22:30 | 177 | 177
2018-09-15 23:00 | 188 | 188
2018-09-15 23:30 | 171 | 170
2018-09-16 | 167 | 166
2018-09-16 00:30 | 171 | 170
2018-09-16 01:00 | 160 | 159
2018-09-16 01:30 | 157 | 156
2018-09-16 02:00 | 155 | 154
2018-09-16 02:30 | 157 | 156
2018-09-16 03:00 | 155 | 154
2018-09-16 03:30 | 152 | 151
2018-09-16 04:00 | 153 | 152
2018-09-16 04:30 | 155 | 154
2018-09-16 05:00 | 155 | 154
2018-09-16 05:30 | 157 | 156
2018-09-16 06:00 | 158 | 157
2018-09-16 06:30 | 158 | 157
2018-09-16 07:00 | 141 | 140
2018-09-16 07:30 | 115 | 113
2018-09-16 08:00 | 84 | 83
2018-09-16 08:30 | 68 | 66
2018-09-16 09:00 | 73 | 71
2018-09-16 09:30 | 59 | 56
2018-09-16 10:00 | 49 | 43
2018-09-16 10:30 | 38 | 30
2018-09-16 11:00 | 24 | 18
2018-09-16 11:30 | 21 | 16
2018-09-16 12:00 | 15 | 13
2018-09-16 12:30 | 15 | 13
2018-09-16 13:00 | 9 | 8
2018-09-16 13:30 | 10 | 9
2018-09-16 14:00 | 8 | 7
2018-09-16 14:30 | 18 | 14
2018-09-16 15:00 | 37 | 28
2018-09-16 15:30 | 45 | 38
2018-09-16 16:00 | 66 | 64
2018-09-16 16:30 | 97 | 96
2018-09-16 17:00 | 125 | 124
2018-09-16 17:30 | 147 | 146
2018-09-16 18:00 | 184 | 183
2018-09-16 18:30 | 210 | 209
2018-09-16 19:00 | 244 | 243
2018-09-16 19:30 | 241 | 241
2018-09-16 20:00 | 236 | 236
2018-09-16 20:30 | 244 | 243
2018-09-16 21:00 | 248 | 247
2018-09-16 21:30 | 241 | 240
2018-09-16 22:00 | 233 | 232
2018-09-16 22:30 | 220 | 219
2018-09-16 23:00 | 210 | 208
2018-09-16 23:30 | 205 | 204
2018-09-17 | 201 | 199
2018-09-17 00:30 | 200 | 199
2018-09-17 01:00 | 194 | 193
2018-09-17 01:30 | 192 | 190
2018-09-17 02:00 | 188 | 187
2018-09-17 02:30 | 188 | 187
2018-09-17 03:00 | 187 | 186
2018-09-17 03:30 | 184 | 183
2018-09-17 04:00 | 184 | 183
2018-09-17 04:30 | 188 | 187
2018-09-17 05:00 | 186 | 185
2018-09-17 05:30 | 188 | 187
2018-09-17 06:00 | 197 | 196
2018-09-17 06:30 | 208 | 207
2018-09-17 07:00 | 195 | 194
2018-09-17 07:30 | 182 | 182
2018-09-17 08:00 | 156 | 155
2018-09-17 08:30 | 128 | 127
2018-09-17 09:00 | 122 | 121
2018-09-17 09:30 | 103 | 102
2018-09-17 10:00 | 83 | 81
2018-09-17 10:30 | 40 | 35
2018-09-17 11:00 | 61 | 58
2018-09-17 11:30 | 60 | 57
2018-09-17 12:00 | 57 | 53
2018-09-17 12:30 | 50 | 46
2018-09-17 13:00 | 49 | 42
2018-09-17 13:30 | 40 | 36
2018-09-17 14:00 | 56 | 50
2018-09-17 14:30 | 66 | 63
2018-09-17 15:00 | 82 | 80
2018-09-17 15:30 | 92 | 91
2018-09-17 16:00 | 115 | 114
2018-09-17 16:30 | 133 | 133
2018-09-17 17:00 | 162 | 162
2018-09-17 17:30 | 195 | 194
2018-09-17 18:00 | 226 | 225
2018-09-17 18:30 | 240 | 239
2018-09-17 19:00 | 250 | 249
2018-09-17 19:30 | 242 | 241
2018-09-17 20:00 | 237 | 236
2018-09-17 20:30 | 243 | 242
2018-09-17 21:00 | 239 | 238
2018-09-17 21:30 | 228 | 227
2018-09-17 22:00 | 215 | 214
2018-09-17 22:30 | 201 | 200
2018-09-17 23:00 | 189 | 188
2018-09-17 23:30 | 178 | 177
2018-09-18 | 168 | 166
2018-09-18 00:30 | 164 | 163
2018-09-18 01:00 | 157 | 156
2018-09-18 01:30 | 154 | 153
2018-09-18 02:00 | 154 | 153
2018-09-18 02:30 | 153 | 152
2018-09-18 03:00 | 154 | 153
2018-09-18 03:30 | 153 | 152
2018-09-18 04:00 | 155 | 153
2018-09-18 04:30 | 154 | 153
2018-09-18 05:00 | 158 | 157
2018-09-18 05:30 | 156 | 155
2018-09-18 06:00 | 165 | 164
2018-09-18 06:30 | 176 | 175
2018-09-18 07:00 | 169 | 168
2018-09-18 07:30 | 169 | 168
2018-09-18 08:00 | 168 | 167
2018-09-18 08:30 | 157 | 157
2018-09-18 09:00 | 161 | 160
2018-09-18 09:30 | 134 | 132
2018-09-18 10:00 | 116 | 114
2018-09-18 10:30 | 103 | 102
2018-09-18 11:00 | 109 | 108
2018-09-18 11:30 | 98 | 97
2018-09-18 12:00 | 99 | 98
2018-09-18 12:30 | 93 | 92
2018-09-18 13:00 | 109 | 107
2018-09-18 13:30 | 105 | 104
2018-09-18 14:00 | 115 | 113
2018-09-18 14:30 | 82 | 81
2018-09-18 15:00 | 90 | 89
2018-09-18 15:30 | 98 | 97
2018-09-18 16:00 | 118 | 117
2018-09-18 16:30 | 129 | 128
2018-09-18 17:00 | 152 | 151
2018-09-18 17:30 | 180 | 179
2018-09-18 18:00 | 217 | 217
2018-09-18 18:30 | 238 | 238
2018-09-18 19:00 | 227 | 227
2018-09-18 19:30 | 223 | 223
2018-09-18 20:00 | 234 | 234
2018-09-18 20:30 | 253 | 253
2018-09-18 21:00 | 243 | 242
2018-09-18 21:30 | 229 | 229
2018-09-18 22:00 | 210 | 210
2018-09-18 22:30 | 189 | 188
2018-09-18 23:00 | 179 | 179
2018-09-18 23:30 | 169 | 169
2018-09-19 | 160 | 160
2018-09-19 00:30 | 157 | 156
2018-09-19 01:00 | 152 | 151
2018-09-19 01:30 | 147 | 146
2018-09-19 02:00 | 139 | 138
2018-09-19 02:30 | 137 | 137
2018-09-19 03:00 | 134 | 134
2018-09-19 03:30 | 134 | 134
2018-09-19 04:00 | 134 | 133
2018-09-19 04:30 | 133 | 133
2018-09-19 05:00 | 135 | 135
2018-09-19 05:30 | 142 | 141
2018-09-19 06:00 | 151 | 150
2018-09-19 06:30 | 162 | 162
2018-09-19 07:00 | 148 | 147
2018-09-19 07:30 | 141 | 140
2018-09-19 08:00 | 121 | 119
2018-09-19 08:30 | 99 | 96
2018-09-19 09:00 | 99 | 96
2018-09-19 09:30 | 100 | 96
2018-09-19 10:00 | 61 | 53
2018-09-19 10:30 | 71 | 65
2018-09-19 11:00 | 67 | 59
2018-09-19 11:30 | 39 | 36
2018-09-19 12:00 | 41 | 36
2018-09-19 12:30 | 38 | 34
2018-09-19 13:00 | 55 | 48
2018-09-19 13:30 | 65 | 60
2018-09-19 14:00 | 65 | 60
2018-09-19 14:30 | 62 | 57
2018-09-19 15:00 | 62 | 56
2018-09-19 15:30 | 64 | 59
2018-09-19 16:00 | 88 | 87
2018-09-19 16:30 | 106 | 106
2018-09-19 17:00 | 135 | 134
2018-09-19 17:30 | 123 | 123
2018-09-19 18:00 | 112 | 112
2018-09-19 18:30 | 136 | 136
2018-09-19 19:00 | 155 | 155
2018-09-19 19:30 | 158 | 157
2018-09-19 20:00 | 151 | 150
2018-09-19 20:30 | 142 | 141
2018-09-19 21:00 | 134 | 134
2018-09-19 21:30 | 126 | 125
2018-09-19 22:00 | 110 | 110
2018-09-19 22:30 | 104 | 104
2018-09-19 23:00 | 98 | 97
2018-09-19 23:30 | 87 | 86
2018-09-20 | 79 | 77
2018-09-20 00:30 | 109 | 108
2018-09-20 01:00 | 144 | 144
2018-09-20 01:30 | 140 | 140
2018-09-20 02:00 | 136 | 135
2018-09-20 02:30 | 135 | 134
2018-09-20 03:00 | 134 | 134
2018-09-20 03:30 | 136 | 135
2018-09-20 04:00 | 134 | 133
2018-09-20 04:30 | 137 | 136
2018-09-20 05:00 | 138 | 138
2018-09-20 05:30 | 145 | 144
2018-09-20 06:00 | 155 | 154
2018-09-20 06:30 | 166 | 165
2018-09-20 07:00 | 140 | 139
2018-09-20 07:30 | 125 | 124
2018-09-20 08:00 | 99 | 98
2018-09-20 08:30 | 89 | 88
2018-09-20 09:00 | 90 | 89
2018-09-20 09:30 | 71 | 69
2018-09-20 10:00 | 54 | 50
2018-09-20 10:30 | 29 | 21
2018-09-20 11:00 | 22 | 16
2018-09-20 11:30 | 52 | 46
2018-09-20 12:00 | 10 | 9
2018-09-20 12:30 | 33 | 30
2018-09-20 13:00 | 7 | 7
2018-09-20 13:30 | 6 | 5
2018-09-20 14:00 | 7 | 6
2018-09-20 14:30 | 50 | 42
2018-09-20 15:00 | 59 | 54
2018-09-20 15:30 | 75 | 72
2018-09-20 16:00 | 95 | 93
2018-09-20 16:30 | 117 | 116
2018-09-20 17:00 | 155 | 155
2018-09-20 17:30 | 166 | 165
2018-09-20 18:00 | 149 | 148
2018-09-20 18:30 | 128 | 127
2018-09-20 19:00 | 150 | 149
2018-09-20 19:30 | 151 | 150
2018-09-20 20:00 | 146 | 145
2018-09-20 20:30 | 155 | 155
2018-09-20 21:00 | 152 | 151
2018-09-20 21:30 | 141 | 140
2018-09-20 22:00 | 129 | 128
2018-09-20 22:30 | 114 | 113
2018-09-20 23:00 | 134 | 133
2018-09-20 23:30 | 164 | 163
2018-09-21 | 160 | 159
2018-09-21 00:30 | 157 | 156
2018-09-21 01:00 | 149 | 148
2018-09-21 01:30 | 148 | 147
2018-09-21 02:00 | 152 | 151
2018-09-21 02:30 | 157 | 156
2018-09-21 03:00 | 156 | 155
2018-09-21 03:30 | 155 | 154
2018-09-21 04:00 | 154 | 153
2018-09-21 04:30 | 151 | 150
2018-09-21 05:00 | 158 | 157
2018-09-21 05:30 | 160 | 159
2018-09-21 06:00 | 160 | 159
2018-09-21 06:30 | 167 | 167
2018-09-21 07:00 | 144 | 144
2018-09-21 07:30 | 120 | 120
2018-09-21 08:00 | 95 | 94
2018-09-21 08:30 | 82 | 80
2018-09-21 09:00 | 85 | 83
2018-09-21 09:30 | 85 | 83
2018-09-21 10:00 | 75 | 72
2018-09-21 10:30 | 78 | 74
2018-09-21 11:00 | 84 | 80
2018-09-21 11:30 | 60 | 53
2018-09-21 12:00 | 61 | 55
2018-09-21 12:30 | 44 | 40
2018-09-21 13:00 | 49 | 42
2018-09-21 13:30 | 57 | 49
2018-09-21 14:00 | 35 | 34
2018-09-21 14:30 | 41 | 37
2018-09-21 15:00 | 62 | 55
2018-09-21 15:30 | 78 | 73
2018-09-21 16:00 | 105 | 103
2018-09-21 16:30 | 121 | 119
2018-09-21 17:00 | 137 | 136
2018-09-21 17:30 | 122 | 122
2018-09-21 18:00 | 130 | 130
2018-09-21 18:30 | 137 | 137
2018-09-21 19:00 | 147 | 146
2018-09-21 19:30 | 147 | 146
2018-09-21 20:00 | 137 | 136
2018-09-21 20:30 | 137 | 137
2018-09-21 21:00 | 136 | 135
2018-09-21 21:30 | 130 | 129
2018-09-21 22:00 | 121 | 120
2018-09-21 22:30 | 107 | 106
2018-09-21 23:00 | 104 | 103
2018-09-21 23:30 | 115 | 114
2018-09-22 | 117 | 116
2018-09-22 00:30 | 150 | 149
2018-09-22 01:00 | 149 | 148
2018-09-22 01:30 | 144 | 144
2018-09-22 02:00 | 140 | 140
2018-09-22 02:30 | 138 | 137
2018-09-22 03:00 | 139 | 138
2018-09-22 03:30 | 136 | 135
2018-09-22 04:00 | 133 | 132
2018-09-22 04:30 | 139 | 139
2018-09-22 05:00 | 141 | 140
2018-09-22 05:30 | 145 | 145
2018-09-22 06:00 | 147 | 146
2018-09-22 06:30 | 144 | 144
2018-09-22 07:00 | 122 | 121
2018-09-22 07:30 | 93 | 92
2018-09-22 08:00 | 71 | 67
2018-09-22 08:30 | 65 | 59
2018-09-22 09:00 | 72 | 68
2018-09-22 09:30 | 67 | 62
2018-09-22 10:00 | 57 | 50
2018-09-22 10:30 | 52 | 47
2018-09-22 11:00 | 54 | 49
2018-09-22 11:30 | 68 | 63
2018-09-22 12:00 | 53 | 46
2018-09-22 12:30 | 54 | 46
2018-09-22 13:00 | 45 | 38
2018-09-22 13:30 | 35 | 27
2018-09-22 14:00 | 27 | 23
2018-09-22 14:30 | 36 | 28
2018-09-22 15:00 | 50 | 43
2018-09-22 15:30 | 53 | 47
2018-09-22 16:00 | 61 | 55
2018-09-22 16:30 | 84 | 82
2018-09-22 17:00 | 118 | 117
2018-09-22 17:30 | 155 | 154
2018-09-22 18:00 | 190 | 189
2018-09-22 18:30 | 218 | 218
2018-09-22 19:00 | 232 | 231
2018-09-22 19:30 | 228 | 227
2018-09-22 20:00 | 219 | 218
2018-09-22 20:30 | 218 | 217
2018-09-22 21:00 | 220 | 219
2018-09-22 21:30 | 216 | 215
2018-09-22 22:00 | 199 | 198
2018-09-22 22:30 | 191 | 191
2018-09-22 23:00 | 182 | 182
2018-09-22 23:30 | 174 | 173
2018-09-23 | 162 | 161
2018-09-23 00:30 | 168 | 167
2018-09-23 01:00 | 164 | 163
2018-09-23 01:30 | 151 | 150
2018-09-23 02:00 | 140 | 139
2018-09-23 02:30 | 147 | 146
2018-09-23 03:00 | 144 | 143
2018-09-23 03:30 | 147 | 146
2018-09-23 04:00 | 146 | 145
2018-09-23 04:30 | 138 | 137
2018-09-23 05:00 | 134 | 132
2018-09-23 05:30 | 141 | 140
2018-09-23 06:00 | 148 | 147
2018-09-23 06:30 | 137 | 136
2018-09-23 07:00 | 103 | 101
2018-09-23 07:30 | 70 | 67
2018-09-23 08:00 | 52 | 48
2018-09-23 08:30 | 42 | 35
2018-09-23 09:00 | 51 | 47
2018-09-23 09:30 | 33 | 24
2018-09-23 10:00 | 24 | 16
2018-09-23 10:30 | 29 | 22
2018-09-23 11:00 | 25 | 20
2018-09-23 11:30 | 30 | 23
2018-09-23 12:00 | 18 | 13
2018-09-23 12:30 | 16 | 12
2018-09-23 13:00 | 14 | 9
2018-09-23 13:30 | 30 | 23
2018-09-23 14:00 | 28 | 22
2018-09-23 14:30 | 27 | 21
2018-09-23 15:00 | 32 | 26
2018-09-23 15:30 | 44 | 37
2018-09-23 16:00 | 55 | 51
2018-09-23 16:30 | 74 | 72
2018-09-23 17:00 | 101 | 99
2018-09-23 17:30 | 157 | 156
2018-09-23 18:00 | 207 | 207
2018-09-23 18:30 | 226 | 226
2018-09-23 19:00 | 245 | 244
2018-09-23 19:30 | 241 | 241
2018-09-23 20:00 | 226 | 226
2018-09-23 20:30 | 227 | 226
2018-09-23 21:00 | 227 | 226
2018-09-23 21:30 | 212 | 211
2018-09-23 22:00 | 207 | 206
2018-09-23 22:30 | 196 | 195
2018-09-23 23:00 | 177 | 176
2018-09-23 23:30 | 172 | 171
2018-09-24 | 162 | 160
2018-09-24 00:30 | 162 | 161
2018-09-24 01:00 | 149 | 148
2018-09-24 01:30 | 144 | 143
2018-09-24 02:00 | 138 | 137
2018-09-24 02:30 | 143 | 142
2018-09-24 03:00 | 145 | 144
2018-09-24 03:30 | 146 | 145
2018-09-24 04:00 | 145 | 144
2018-09-24 04:30 | 146 | 145
2018-09-24 05:00 | 149 | 148
2018-09-24 05:30 | 153 | 152
2018-09-24 06:00 | 156 | 155
2018-09-24 06:30 | 163 | 162
2018-09-24 07:00 | 139 | 138
2018-09-24 07:30 | 108 | 106
2018-09-24 08:00 | 78 | 77
2018-09-24 08:30 | 67 | 64
2018-09-24 09:00 | 70 | 68
2018-09-24 09:30 | 79 | 78
2018-09-24 10:00 | 67 | 63
2018-09-24 10:30 | 65 | 59
2018-09-24 11:00 | 62 | 54
2018-09-24 11:30 | 61 | 54
2018-09-24 12:00 | 63 | 57
2018-09-24 12:30 | 64 | 58
2018-09-24 13:00 | 76 | 74
2018-09-24 13:30 | 70 | 67
2018-09-24 14:00 | 61 | 56
2018-09-24 14:30 | 62 | 56
2018-09-24 15:00 | 61 | 56
2018-09-24 15:30 | 73 | 70
2018-09-24 16:00 | 87 | 86
2018-09-24 16:30 | 122 | 121
2018-09-24 17:00 | 172 | 172
2018-09-24 17:30 | 173 | 173
2018-09-24 18:00 | 160 | 159
2018-09-24 18:30 | 172 | 171
2018-09-24 19:00 | 188 | 188
2018-09-24 19:30 | 187 | 186
2018-09-24 20:00 | 180 | 180
2018-09-24 20:30 | 173 | 172
2018-09-24 21:00 | 172 | 171
2018-09-24 21:30 | 166 | 165
2018-09-24 22:00 | 151 | 150
2018-09-24 22:30 | 138 | 137
2018-09-24 23:00 | 139 | 138
2018-09-24 23:30 | 171 | 171
2018-09-25 | 169 | 168
2018-09-25 00:30 | 165 | 164
2018-09-25 01:00 | 161 | 160
2018-09-25 01:30 | 155 | 154
2018-09-25 02:00 | 151 | 150
2018-09-25 02:30 | 152 | 151
2018-09-25 03:00 | 148 | 147
2018-09-25 03:30 | 149 | 148
2018-09-25 04:00 | 149 | 148
2018-09-25 04:30 | 149 | 148
2018-09-25 05:00 | 152 | 152
2018-09-25 05:30 | 159 | 158
2018-09-25 06:00 | 165 | 164
2018-09-25 06:30 | 177 | 176
2018-09-25 07:00 | 162 | 162
2018-09-25 07:30 | 133 | 132
2018-09-25 08:00 | 109 | 108
2018-09-25 08:30 | 95 | 94
2018-09-25 09:00 | 111 | 109
2018-09-25 09:30 | 115 | 113
2018-09-25 10:00 | 100 | 98
2018-09-25 10:30 | 86 | 84
2018-09-25 11:00 | 99 | 97
2018-09-25 11:30 | 96 | 95
2018-09-25 12:00 | 89 | 88
2018-09-25 12:30 | 89 | 87
2018-09-25 13:00 | 84 | 82
2018-09-25 13:30 | 79 | 78
2018-09-25 14:00 | 74 | 72
2018-09-25 14:30 | 88 | 87
2018-09-25 15:00 | 81 | 79
2018-09-25 15:30 | 90 | 89
2018-09-25 16:00 | 117 | 115
2018-09-25 16:30 | 130 | 129
2018-09-25 17:00 | 153 | 152
2018-09-25 17:30 | 177 | 176
2018-09-25 18:00 | 208 | 207
2018-09-25 18:30 | 231 | 230
2018-09-25 19:00 | 240 | 239
2018-09-25 19:30 | 241 | 240
2018-09-25 20:00 | 231 | 229
2018-09-25 20:30 | 231 | 229
2018-09-25 21:00 | 225 | 224
2018-09-25 21:30 | 218 | 216
2018-09-25 22:00 | 210 | 208
2018-09-25 22:30 | 193 | 191
2018-09-25 23:00 | 181 | 179
2018-09-25 23:30 | 171 | 170
2018-09-26 | 162 | 161
2018-09-26 00:30 | 159 | 158
2018-09-26 01:00 | 153 | 152
2018-09-26 01:30 | 155 | 154
2018-09-26 02:00 | 147 | 146
2018-09-26 02:30 | 148 | 146
2018-09-26 03:00 | 144 | 142
2018-09-26 03:30 | 146 | 145
2018-09-26 04:00 | 149 | 148
2018-09-26 04:30 | 143 | 142
2018-09-26 05:00 | 143 | 142
2018-09-26 05:30 | 152 | 150
2018-09-26 06:00 | 158 | 157
2018-09-26 06:30 | 166 | 165
2018-09-26 07:00 | 149 | 148
2018-09-26 07:30 | 125 | 123
2018-09-26 08:00 | 105 | 104
2018-09-26 08:30 | 88 | 87
2018-09-26 09:00 | 85 | 84
2018-09-26 09:30 | 83 | 82
2018-09-26 10:00 | 72 | 70
2018-09-26 10:30 | 70 | 68
2018-09-26 11:00 | 65 | 62
2018-09-26 11:30 | 52 | 46
2018-09-26 12:00 | 55 | 50
2018-09-26 12:30 | 60 | 55
2018-09-26 13:00 | 67 | 63
2018-09-26 13:30 | 77 | 75
2018-09-26 14:00 | 63 | 59
2018-09-26 14:30 | 70 | 67
2018-09-26 15:00 | 69 | 66
2018-09-26 15:30 | 95 | 94
2018-09-26 16:00 | 114 | 113
2018-09-26 16:30 | 119 | 118
2018-09-26 17:00 | 108 | 107
2018-09-26 17:30 | 95 | 94
2018-09-26 18:00 | 131 | 131
2018-09-26 18:30 | 142 | 141
2018-09-26 19:00 | 163 | 162
2018-09-26 19:30 | 158 | 157
2018-09-26 20:00 | 151 | 150
2018-09-26 20:30 | 142 | 141
2018-09-26 21:00 | 138 | 137
2018-09-26 21:30 | 127 | 126
2018-09-26 22:00 | 119 | 118
2018-09-26 22:30 | 130 | 129
2018-09-26 23:00 | 167 | 166
2018-09-26 23:30 | 169 | 168
2018-09-27 | 165 | 164
2018-09-27 00:30 | 172 | 171
2018-09-27 01:00 | 173 | 172
2018-09-27 01:30 | 172 | 171
2018-09-27 02:00 | 168 | 167
2018-09-27 02:30 | 164 | 163
2018-09-27 03:00 | 160 | 159
2018-09-27 03:30 | 162 | 161
2018-09-27 04:00 | 163 | 162
2018-09-27 04:30 | 164 | 163
2018-09-27 05:00 | 167 | 165
2018-09-27 05:30 | 174 | 173
2018-09-27 06:00 | 179 | 178
2018-09-27 06:30 | 182 | 181
2018-09-27 07:00 | 162 | 161
2018-09-27 07:30 | 137 | 136
2018-09-27 08:00 | 117 | 116
2018-09-27 08:30 | 108 | 108
2018-09-27 09:00 | 123 | 122
2018-09-27 09:30 | 109 | 108
2018-09-27 10:00 | 103 | 102
2018-09-27 10:30 | 86 | 84
2018-09-27 11:00 | 71 | 69
2018-09-27 11:30 | 68 | 65
2018-09-27 12:00 | 66 | 63
2018-09-27 12:30 | 61 | 57
2018-09-27 13:00 | 56 | 50
2018-09-27 13:30 | 47 | 40
2018-09-27 14:00 | 38 | 33
2018-09-27 14:30 | 47 | 40
2018-09-27 15:00 | 66 | 60
2018-09-27 15:30 | 83 | 80
2018-09-27 16:00 | 111 | 110
2018-09-27 16:30 | 127 | 126
2018-09-27 17:00 | 130 | 129
2018-09-27 17:30 | 160 | 160
2018-09-27 18:00 | 166 | 165
2018-09-27 18:30 | 177 | 176
2018-09-27 19:00 | 172 | 171
2018-09-27 19:30 | 172 | 172
2018-09-27 20:00 | 168 | 167
2018-09-27 20:30 | 173 | 172
2018-09-27 21:00 | 169 | 169
2018-09-27 21:30 | 159 | 158
2018-09-27 22:00 | 150 | 149
2018-09-27 22:30 | 164 | 164
2018-09-27 23:00 | 186 | 185
2018-09-27 23:30 | 173 | 173
2018-09-28 | 160 | 160
2018-09-28 00:30 | 159 | 158
2018-09-28 01:00 | 150 | 149
2018-09-28 01:30 | 145 | 144
2018-09-28 02:00 | 143 | 142
2018-09-28 02:30 | 140 | 139
2018-09-28 03:00 | 139 | 138
2018-09-28 03:30 | 138 | 138
2018-09-28 04:00 | 143 | 142
2018-09-28 04:30 | 149 | 148
2018-09-28 05:00 | 148 | 148
2018-09-28 05:30 | 149 | 149
2018-09-28 06:00 | 157 | 157
2018-09-28 06:30 | 167 | 166
2018-09-28 07:00 | 145 | 144
2018-09-28 07:30 | 115 | 114
2018-09-28 08:00 | 115 | 114
2018-09-28 08:30 | 105 | 104
2018-09-28 09:00 | 97 | 96
2018-09-28 09:30 | 88 | 86
2018-09-28 10:00 | 70 | 64
2018-09-28 10:30 | 45 | 41
2018-09-28 11:00 | 58 | 52
2018-09-28 11:30 | 53 | 46
2018-09-28 12:00 | 48 | 43
2018-09-28 12:30 | 40 | 38
2018-09-28 13:00 | 41 | 39
2018-09-28 13:30 | 48 | 41
2018-09-28 14:00 | 49 | 43
2018-09-28 14:30 | 53 | 44
2018-09-28 15:00 | 73 | 69
2018-09-28 15:30 | 74 | 70
2018-09-28 16:00 | 85 | 82
2018-09-28 16:30 | 106 | 105
2018-09-28 17:00 | 129 | 128
2018-09-28 17:30 | 167 | 166
2018-09-28 18:00 | 197 | 196
2018-09-28 18:30 | 219 | 218
2018-09-28 19:00 | 235 | 235
2018-09-28 19:30 | 245 | 245
2018-09-28 20:00 | 214 | 214
2018-09-28 20:30 | 232 | 232
2018-09-28 21:00 | 230 | 230
2018-09-28 21:30 | 219 | 218
2018-09-28 22:00 | 206 | 206
2018-09-28 22:30 | 198 | 198
2018-09-28 23:00 | 191 | 190
2018-09-28 23:30 | 184 | 183
2018-09-29 | 172 | 171
2018-09-29 00:30 | 170 | 170
2018-09-29 01:00 | 163 | 162
2018-09-29 01:30 | 160 | 159
2018-09-29 02:00 | 155 | 155
2018-09-29 02:30 | 152 | 151
2018-09-29 03:00 | 146 | 145
2018-09-29 03:30 | 138 | 138
2018-09-29 04:00 | 137 | 136
2018-09-29 04:30 | 140 | 139
2018-09-29 05:00 | 142 | 141
2018-09-29 05:30 | 148 | 147
2018-09-29 06:00 | 147 | 146
2018-09-29 06:30 | 142 | 141
2018-09-29 07:00 | 111 | 110
2018-09-29 07:30 | 82 | 80
2018-09-29 08:00 | 63 | 57
2018-09-29 08:30 | 56 | 48
2018-09-29 09:00 | 71 | 67
2018-09-29 09:30 | 56 | 49
2018-09-29 10:00 | 39 | 35
2018-09-29 10:30 | 31 | 27
2018-09-29 11:00 | 17 | 15
2018-09-29 11:30 | 12 | 12
2018-09-29 12:00 | 13 | 12
2018-09-29 12:30 | 9 | 9
2018-09-29 13:00 | 8 | 8
2018-09-29 13:30 | 13 | 12
2018-09-29 14:00 | 14 | 13
2018-09-29 14:30 | 34 | 29
2018-09-29 15:00 | 38 | 35
2018-09-29 15:30 | 58 | 51
2018-09-29 16:00 | 71 | 68
2018-09-29 16:30 | 93 | 92
2018-09-29 17:00 | 122 | 121
2018-09-29 17:30 | 162 | 161
2018-09-29 18:00 | 194 | 193
2018-09-29 18:30 | 209 | 209
2018-09-29 19:00 | 231 | 230
2018-09-29 19:30 | 228 | 228
2018-09-29 20:00 | 219 | 218
2018-09-29 20:30 | 226 | 226
2018-09-29 21:00 | 218 | 218
2018-09-29 21:30 | 207 | 206
2018-09-29 22:00 | 199 | 198
2018-09-29 22:30 | 190 | 189
2018-09-29 23:00 | 183 | 182
2018-09-29 23:30 | 175 | 174
2018-09-30 | 167 | 167
2018-09-30 00:30 | 166 | 166
2018-09-30 01:00 | 161 | 160
2018-09-30 01:30 | 159 | 158
2018-09-30 02:00 | 153 | 153
2018-09-30 02:30 | 147 | 146
2018-09-30 03:00 | 141 | 140
2018-09-30 03:30 | 143 | 142
2018-09-30 04:00 | 141 | 140
2018-09-30 04:30 | 139 | 138
2018-09-30 05:00 | 144 | 144
2018-09-30 05:30 | 144 | 143
2018-09-30 06:00 | 144 | 143
2018-09-30 06:30 | 136 | 135
2018-09-30 07:00 | 102 | 101
2018-09-30 07:30 | 76 | 74
2018-09-30 08:00 | 57 | 50
2018-09-30 08:30 | 51 | 42
2018-09-30 09:00 | 61 | 56
2018-09-30 09:30 | 48 | 43
2018-09-30 10:00 | 27 | 23
2018-09-30 10:30 | 8 | 8
2018-09-30 11:00 | 8 | 7
2018-09-30 11:30 | 7 | 7
2018-09-30 12:00 | 7 | 7
2018-09-30 12:30 | 6 | 6
2018-09-30 13:00 | 5 | 5
2018-09-30 13:30 | 7 | 7
2018-09-30 14:00 | 9 | 8
2018-09-30 14:30 | 14 | 13
2018-09-30 15:00 | 37 | 29
2018-09-30 15:30 | 48 | 42
2018-09-30 16:00 | 66 | 60
2018-09-30 16:30 | 93 | 91
2018-09-30 17:00 | 130 | 130
2018-09-30 17:30 | 174 | 174
2018-09-30 18:00 | 206 | 206
2018-09-30 18:30 | 229 | 228
2018-09-30 19:00 | 240 | 240
2018-09-30 19:30 | 235 | 234
2018-09-30 20:00 | 221 | 221
2018-09-30 20:30 | 233 | 232
2018-09-30 21:00 | 228 | 227
2018-09-30 21:30 | 215 | 214
2018-09-30 22:00 | 206 | 205
2018-09-30 22:30 | 190 | 189
2018-09-30 23:00 | 183 | 182
2018-09-30 23:30 | 175 | 175
2018-10-01 | 161 | 160
2018-10-01 00:30 | 157 | 156
2018-10-01 01:00 | 150 | 150
2018-10-01 01:30 | 149 | 149
2018-10-01 02:00 | 146 | 145
2018-10-01 02:30 | 147 | 146
2018-10-01 03:00 | 145 | 144
2018-10-01 03:30 | 144 | 143
2018-10-01 04:00 | 142 | 141
2018-10-01 04:30 | 143 | 142
2018-10-01 05:00 | 145 | 144
2018-10-01 05:30 | 145 | 144
2018-10-01 06:00 | 147 | 147
2018-10-01 06:30 | 151 | 150
2018-10-01 07:00 | 150 | 150
2018-10-01 07:30 | 121 | 120
2018-10-01 08:00 | 109 | 108
2018-10-01 08:30 | 94 | 92
2018-10-01 09:00 | 101 | 99
2018-10-01 09:30 | 89 | 87
2018-10-01 10:00 | 68 | 64
2018-10-01 10:30 | 75 | 72
2018-10-01 11:00 | 68 | 63
2018-10-01 11:30 | 55 | 49
2018-10-01 12:00 | 51 | 45
2018-10-01 12:30 | 47 | 43
2018-10-01 13:00 | 25 | 19
2018-10-01 13:30 | 12 | 11
2018-10-01 14:00 | 17 | 16
2018-10-01 14:30 | 34 | 29
2018-10-01 15:00 | 42 | 37
2018-10-01 15:30 | 61 | 54
2018-10-01 16:00 | 82 | 80
2018-10-01 16:30 | 104 | 102
2018-10-01 17:00 | 132 | 131
2018-10-01 17:30 | 172 | 171
2018-10-01 18:00 | 221 | 220
2018-10-01 18:30 | 224 | 223
2018-10-01 19:00 | 229 | 228
2018-10-01 19:30 | 237 | 237
2018-10-01 20:00 | 225 | 224
2018-10-01 20:30 | 228 | 227
2018-10-01 21:00 | 219 | 218
2018-10-01 21:30 | 213 | 213
2018-10-01 22:00 | 212 | 212
2018-10-01 22:30 | 193 | 193
2018-10-01 23:00 | 185 | 184
2018-10-01 23:30 | 183 | 182
2018-10-02 | 180 | 180
2018-10-02 00:30 | 170 | 169
2018-10-02 01:00 | 165 | 164
2018-10-02 01:30 | 157 | 156
2018-10-02 02:00 | 156 | 155
2018-10-02 02:30 | 152 | 151
2018-10-02 03:00 | 153 | 152
2018-10-02 03:30 | 145 | 144
2018-10-02 04:00 | 143 | 142
2018-10-02 04:30 | 143 | 143
2018-10-02 05:00 | 145 | 144
2018-10-02 05:30 | 150 | 149
2018-10-02 06:00 | 156 | 156
2018-10-02 06:30 | 165 | 165
2018-10-02 07:00 | 151 | 151
2018-10-02 07:30 | 131 | 131
2018-10-02 08:00 | 115 | 114
2018-10-02 08:30 | 112 | 111
2018-10-02 09:00 | 106 | 104
2018-10-02 09:30 | 109 | 108
2018-10-02 10:00 | 112 | 111
2018-10-02 10:30 | 91 | 88
2018-10-02 11:00 | 98 | 96
2018-10-02 11:30 | 82 | 79
2018-10-02 12:00 | 71 | 67
2018-10-02 12:30 | 56 | 47
2018-10-02 13:00 | 51 | 46
2018-10-02 13:30 | 48 | 44
2018-10-02 14:00 | 54 | 49
2018-10-02 14:30 | 72 | 67
2018-10-02 15:00 | 56 | 48
2018-10-02 15:30 | 69 | 65
2018-10-02 16:00 | 80 | 77
2018-10-02 16:30 | 91 | 89
2018-10-02 17:00 | 101 | 99
2018-10-02 17:30 | 96 | 95
2018-10-02 18:00 | 114 | 113
2018-10-02 18:30 | 139 | 138
2018-10-02 19:00 | 152 | 151
2018-10-02 19:30 | 152 | 151
2018-10-02 20:00 | 146 | 145
2018-10-02 20:30 | 130 | 130
2018-10-02 21:00 | 127 | 126
2018-10-02 21:30 | 186 | 185
2018-10-02 22:00 | 194 | 193
2018-10-02 22:30 | 181 | 181
2018-10-02 23:00 | 170 | 170
2018-10-02 23:30 | 161 | 160
2018-10-03 | 159 | 158
2018-10-03 00:30 | 158 | 157
2018-10-03 01:00 | 151 | 150
2018-10-03 01:30 | 144 | 144
2018-10-03 02:00 | 139 | 138
2018-10-03 02:30 | 134 | 133
2018-10-03 03:00 | 134 | 133
2018-10-03 03:30 | 137 | 136
2018-10-03 04:00 | 132 | 131
2018-10-03 04:30 | 137 | 137
2018-10-03 05:00 | 139 | 138
2018-10-03 05:30 | 149 | 148
2018-10-03 06:00 | 159 | 158
2018-10-03 06:30 | 165 | 164
2018-10-03 07:00 | 151 | 150
2018-10-03 07:30 | 124 | 124
2018-10-03 08:00 | 100 | 99
2018-10-03 08:30 | 94 | 92
2018-10-03 09:00 | 82 | 80
2018-10-03 09:30 | 75 | 71
2018-10-03 10:00 | 71 | 66
2018-10-03 10:30 | 77 | 73
2018-10-03 11:00 | 73 | 69
2018-10-03 11:30 | 77 | 74
2018-10-03 12:00 | 98 | 97
2018-10-03 12:30 | 78 | 75
2018-10-03 13:00 | 68 | 62
2018-10-03 13:30 | 62 | 55
2018-10-03 14:00 | 65 | 59
2018-10-03 14:30 | 84 | 82
2018-10-03 15:00 | 77 | 74
2018-10-03 15:30 | 84 | 81
2018-10-03 16:00 | 113 | 112
2018-10-03 16:30 | 152 | 151
2018-10-03 17:00 | 142 | 141
2018-10-03 17:30 | 114 | 113
2018-10-03 18:00 | 137 | 136
2018-10-03 18:30 | 155 | 154
2018-10-03 19:00 | 161 | 161
2018-10-03 19:30 | 164 | 163
2018-10-03 20:00 | 150 | 149
2018-10-03 20:30 | 136 | 135
2018-10-03 21:00 | 137 | 136
2018-10-03 21:30 | 160 | 159
2018-10-03 22:00 | 159 | 158
2018-10-03 22:30 | 108 | 107
2018-10-03 23:00 | 85 | 83
2018-10-03 23:30 | 80 | 78
2018-10-04 | 152 | 151
2018-10-04 00:30 | 168 | 167
2018-10-04 01:00 | 164 | 164
2018-10-04 01:30 | 160 | 160
2018-10-04 02:00 | 159 | 159
2018-10-04 02:30 | 162 | 161
2018-10-04 03:00 | 164 | 163
2018-10-04 03:30 | 169 | 168
2018-10-04 04:00 | 163 | 163
2018-10-04 04:30 | 163 | 163
2018-10-04 05:00 | 155 | 154
2018-10-04 05:30 | 157 | 156
2018-10-04 06:00 | 163 | 162
2018-10-04 06:30 | 167 | 167
2018-10-04 07:00 | 135 | 134
2018-10-04 07:30 | 112 | 111
2018-10-04 08:00 | 101 | 100
2018-10-04 08:30 | 90 | 88
2018-10-04 09:00 | 84 | 82
2018-10-04 09:30 | 79 | 76
2018-10-04 10:00 | 74 | 71
2018-10-04 10:30 | 75 | 72
2018-10-04 11:00 | 70 | 65
2018-10-04 11:30 | 65 | 59
2018-10-04 12:00 | 65 | 60
2018-10-04 12:30 | 63 | 57
2018-10-04 13:00 | 61 | 53
2018-10-04 13:30 | 46 | 42
2018-10-04 14:00 | 60 | 54
2018-10-04 14:30 | 80 | 77
2018-10-04 15:00 | 93 | 91
2018-10-04 15:30 | 119 | 118
2018-10-04 16:00 | 129 | 128
2018-10-04 16:30 | 136 | 135
2018-10-04 17:00 | 162 | 161
2018-10-04 17:30 | 151 | 150
2018-10-04 18:00 | 157 | 156
2018-10-04 18:30 | 166 | 165
2018-10-04 19:00 | 176 | 175
2018-10-04 19:30 | 170 | 170
2018-10-04 20:00 | 156 | 155
2018-10-04 20:30 | 155 | 154
2018-10-04 21:00 | 150 | 149
2018-10-04 21:30 | 212 | 211
2018-10-04 22:00 | 229 | 228
2018-10-04 22:30 | 214 | 213
2018-10-04 23:00 | 204 | 203
2018-10-04 23:30 | 192 | 192
2018-10-05 | 186 | 185
2018-10-05 00:30 | 195 | 194
2018-10-05 01:00 | 182 | 181
2018-10-05 01:30 | 181 | 180
2018-10-05 02:00 | 178 | 178
2018-10-05 02:30 | 178 | 178
2018-10-05 03:00 | 170 | 169
2018-10-05 03:30 | 167 | 167
2018-10-05 04:00 | 163 | 162
2018-10-05 04:30 | 163 | 162
2018-10-05 05:00 | 170 | 169
2018-10-05 05:30 | 178 | 177
2018-10-05 06:00 | 186 | 186
2018-10-05 06:30 | 187 | 187
2018-10-05 07:00 | 175 | 175
2018-10-05 07:30 | 156 | 155
2018-10-05 08:00 | 138 | 137
2018-10-05 08:30 | 127 | 126
2018-10-05 09:00 | 136 | 135
2018-10-05 09:30 | 135 | 134
2018-10-05 10:00 | 102 | 101
2018-10-05 10:30 | 85 | 83
2018-10-05 11:00 | 78 | 75
2018-10-05 11:30 | 69 | 64
2018-10-05 12:00 | 63 | 60
2018-10-05 12:30 | 37 | 31
2018-10-05 13:00 | 76 | 73
2018-10-05 13:30 | 69 | 65
2018-10-05 14:00 | 63 | 57
2018-10-05 14:30 | 74 | 70
2018-10-05 15:00 | 88 | 86
2018-10-05 15:30 | 100 | 99
2018-10-05 16:00 | 109 | 108
2018-10-05 16:30 | 140 | 139
2018-10-05 17:00 | 167 | 167
2018-10-05 17:30 | 184 | 184
2018-10-05 18:00 | 220 | 220
2018-10-05 18:30 | 240 | 240
2018-10-05 19:00 | 241 | 241
2018-10-05 19:30 | 244 | 244
2018-10-05 20:00 | 243 | 243
2018-10-05 20:30 | 234 | 233
2018-10-05 21:00 | 229 | 229
2018-10-05 21:30 | 251 | 251
2018-10-05 22:00 | 249 | 249
2018-10-05 22:30 | 216 | 216
2018-10-05 23:00 | 215 | 214
2018-10-05 23:30 | 201 | 200
2018-10-06 | 198 | 197
2018-10-06 00:30 | 199 | 199
2018-10-06 01:00 | 190 | 189
2018-10-06 01:30 | 187 | 187
2018-10-06 02:00 | 183 | 183
2018-10-06 02:30 | 182 | 181
2018-10-06 03:00 | 178 | 177
2018-10-06 03:30 | 177 | 176
2018-10-06 04:00 | 177 | 176
2018-10-06 04:30 | 177 | 177
2018-10-06 05:00 | 179 | 178
2018-10-06 05:30 | 183 | 183
2018-10-06 06:00 | 186 | 185
2018-10-06 06:30 | 182 | 181
2018-10-06 07:00 | 168 | 168
2018-10-06 07:30 | 151 | 151
2018-10-06 08:00 | 132 | 131
2018-10-06 08:30 | 126 | 125
2018-10-06 09:00 | 111 | 109
2018-10-06 09:30 | 112 | 111
2018-10-06 10:00 | 95 | 93
2018-10-06 10:30 | 83 | 80
2018-10-06 11:00 | 74 | 69
2018-10-06 11:30 | 64 | 56
2018-10-06 12:00 | 63 | 56
2018-10-06 12:30 | 62 | 54
2018-10-06 13:00 | 61 | 53
2018-10-06 13:30 | 50 | 45
2018-10-06 14:00 | 56 | 49
2018-10-06 14:30 | 68 | 63
2018-10-06 15:00 | 79 | 75
2018-10-06 15:30 | 83 | 79
2018-10-06 16:00 | 104 | 102
2018-10-06 16:30 | 128 | 127
2018-10-06 17:00 | 152 | 151
2018-10-06 17:30 | 166 | 165
2018-10-06 18:00 | 219 | 218
2018-10-06 18:30 | 246 | 246
2018-10-06 19:00 | 258 | 258
2018-10-06 19:30 | 255 | 254
2018-10-06 20:00 | 247 | 246
2018-10-06 20:30 | 239 | 239
2018-10-06 21:00 | 235 | 235
2018-10-06 21:30 | 246 | 245
2018-10-06 22:00 | 237 | 237
2018-10-06 22:30 | 209 | 209
2018-10-06 23:00 | 212 | 212
2018-10-06 23:30 | 209 | 208
2018-10-07 | 203 | 203
2018-10-07 00:30 | 201 | 200
2018-10-07 01:00 | 191 | 191
2018-10-07 01:30 | 187 | 186
2018-10-07 02:00 | 187 | 187
2018-10-07 02:30 | 187 | 187
2018-10-07 03:00 | 190 | 190
2018-10-07 03:30 | 189 | 188
2018-10-07 04:00 | 183 | 183
2018-10-07 04:30 | 177 | 176
2018-10-07 05:00 | 177 | 176
2018-10-07 05:30 | 181 | 180
2018-10-07 06:00 | 182 | 182
2018-10-07 06:30 | 180 | 180
2018-10-07 07:00 | 160 | 160
2018-10-07 07:30 | 133 | 132
2018-10-07 08:00 | 131 | 130
2018-10-07 08:30 | 126 | 126
2018-10-07 09:00 | 119 | 118
2018-10-07 09:30 | 95 | 93
2018-10-07 10:00 | 81 | 77
2018-10-07 10:30 | 83 | 81
2018-10-07 11:00 | 77 | 73
2018-10-07 11:30 | 65 | 59
2018-10-07 12:00 | 41 | 38
2018-10-07 12:30 | 38 | 35
2018-10-07 13:00 | 34 | 33
2018-10-07 13:30 | 38 | 36
2018-10-07 14:00 | 57 | 49
2018-10-07 14:30 | 63 | 57
2018-10-07 15:00 | 69 | 64
2018-10-07 15:30 | 79 | 75
2018-10-07 16:00 | 95 | 93
2018-10-07 16:30 | 118 | 117
2018-10-07 17:00 | 145 | 144
2018-10-07 17:30 | 160 | 159
2018-10-07 18:00 | 200 | 200
2018-10-07 18:30 | 221 | 220
2018-10-07 19:00 | 226 | 226
2018-10-07 19:30 | 236 | 235
2018-10-07 20:00 | 247 | 247
2018-10-07 20:30 | 242 | 241
2018-10-07 21:00 | 236 | 236
2018-10-07 21:30 | 244 | 243
2018-10-07 22:00 | 233 | 232
2018-10-07 22:30 | 219 | 218
2018-10-07 23:00 | 202 | 202
2018-10-07 23:30 | 195 | 194
2018-10-08 | 187 | 187
2018-10-08 00:30 | 189 | 189
2018-10-08 01:00 | 182 | 182
2018-10-08 01:30 | 178 | 177
2018-10-08 02:00 | 174 | 173
2018-10-08 02:30 | 175 | 174
2018-10-08 03:00 | 175 | 174
2018-10-08 03:30 | 176 | 175
2018-10-08 04:00 | 172 | 171
2018-10-08 04:30 | 170 | 169
2018-10-08 05:00 | 178 | 177
2018-10-08 05:30 | 184 | 184
2018-10-08 06:00 | 194 | 194
2018-10-08 06:30 | 202 | 201
2018-10-08 07:00 | 190 | 190
2018-10-08 07:30 | 170 | 169
2018-10-08 08:00 | 152 | 152
2018-10-08 08:30 | 140 | 140
2018-10-08 09:00 | 132 | 130
2018-10-08 09:30 | 122 | 121
2018-10-08 10:00 | 104 | 102
2018-10-08 10:30 | 96 | 94
2018-10-08 11:00 | 90 | 88
2018-10-08 11:30 | 78 | 74
2018-10-08 12:00 | 55 | 47
2018-10-08 12:30 | 51 | 43
2018-10-08 13:00 | 42 | 38
2018-10-08 13:30 | 35 | 30
2018-10-08 14:00 | 39 | 37
2018-10-08 14:30 | 59 | 51
2018-10-08 15:00 | 61 | 54
2018-10-08 15:30 | 58 | 49
2018-10-08 16:00 | 52 | 46
2018-10-08 16:30 | 42 | 38
2018-10-08 17:00 | 75 | 71
2018-10-08 17:30 | 76 | 74
2018-10-08 18:00 | 122 | 121
2018-10-08 18:30 | 148 | 147
2018-10-08 19:00 | 160 | 159
2018-10-08 19:30 | 174 | 173
2018-10-08 20:00 | 164 | 163
2018-10-08 20:30 | 179 | 178
2018-10-08 21:00 | 169 | 168
2018-10-08 21:30 | 172 | 171
2018-10-08 22:00 | 161 | 160
2018-10-08 22:30 | 142 | 141
2018-10-08 23:00 | 134 | 133
2018-10-08 23:30 | 123 | 122
2018-10-09 | 113 | 112
2018-10-09 00:30 | 114 | 112
2018-10-09 01:00 | 109 | 107
2018-10-09 01:30 | 113 | 112
2018-10-09 02:00 | 114 | 113
2018-10-09 02:30 | 113 | 112
2018-10-09 03:00 | 105 | 104
2018-10-09 03:30 | 105 | 104
2018-10-09 04:00 | 106 | 104
2018-10-09 04:30 | 108 | 107
2018-10-09 05:00 | 111 | 110
2018-10-09 05:30 | 119 | 118
2018-10-09 06:00 | 125 | 124
2018-10-09 06:30 | 126 | 125
2018-10-09 07:00 | 81 | 78
2018-10-09 07:30 | 90 | 88
2018-10-09 08:00 | 91 | 89
2018-10-09 08:30 | 89 | 85
2018-10-09 09:00 | 64 | 56
2018-10-09 09:30 | 22 | 20
2018-10-09 10:00 | 27 | 21
2018-10-09 10:30 | 37 | 29
2018-10-09 11:00 | 33 | 25
2018-10-09 11:30 | 26 | 19
2018-10-09 12:00 | 32 | 24
2018-10-09 12:30 | 28 | 19
2018-10-09 13:00 | 27 | 20
2018-10-09 13:30 | 9 | 8
2018-10-09 14:00 | 31 | 24
2018-10-09 14:30 | 44 | 40
2018-10-09 15:00 | 48 | 42
2018-10-09 15:30 | 64 | 59
2018-10-09 16:00 | 81 | 79
2018-10-09 16:30 | 118 | 117
2018-10-09 17:00 | 133 | 133
2018-10-09 17:30 | 155 | 154
2018-10-09 18:00 | 167 | 166
2018-10-09 18:30 | 143 | 143
2018-10-09 19:00 | 167 | 167
2018-10-09 19:30 | 175 | 175
2018-10-09 20:00 | 195 | 195
2018-10-09 20:30 | 178 | 177
2018-10-09 21:00 | 169 | 169
2018-10-09 21:30 | 178 | 178
2018-10-09 22:00 | 169 | 168
2018-10-09 22:30 | 154 | 153
2018-10-09 23:00 | 143 | 142
2018-10-09 23:30 | 130 | 129
2018-10-10 | 125 | 124
2018-10-10 00:30 | 123 | 122
2018-10-10 01:00 | 114 | 113
2018-10-10 01:30 | 109 | 108
2018-10-10 02:00 | 108 | 107
2018-10-10 02:30 | 111 | 110
2018-10-10 03:00 | 110 | 108
2018-10-10 03:30 | 106 | 105
2018-10-10 04:00 | 107 | 106
2018-10-10 04:30 | 112 | 111
2018-10-10 05:00 | 116 | 115
2018-10-10 05:30 | 126 | 125
2018-10-10 06:00 | 135 | 135
2018-10-10 06:30 | 142 | 141
2018-10-10 07:00 | 102 | 101
2018-10-10 07:30 | 74 | 70
2018-10-10 08:00 | 60 | 51
2018-10-10 08:30 | 44 | 38
2018-10-10 09:00 | 38 | 29
2018-10-10 09:30 | 10 | 9
2018-10-10 10:00 | 1 | 1
2018-10-10 10:30 | 1 | 1
2018-10-10 11:00 | 4 | 3
2018-10-10 11:30 | 2 | 2
2018-10-10 12:00 | 2 | 2
2018-10-10 12:30 | 4 | 4
2018-10-10 13:00 | 4 | 4
2018-10-10 13:30 | 1 | 1
2018-10-10 14:00 | 0 | 0
2018-10-10 14:30 | 1 | 0
2018-10-10 15:00 | 4 | 4
2018-10-10 15:30 | 18 | 14
2018-10-10 16:00 | 67 | 64
2018-10-10 16:30 | 98 | 97
2018-10-10 17:00 | 130 | 129
2018-10-10 17:30 | 161 | 160
2018-10-10 18:00 | 161 | 160
2018-10-10 18:30 | 171 | 170
2018-10-10 19:00 | 167 | 166
2018-10-10 19:30 | 183 | 182
2018-10-10 20:00 | 178 | 178
2018-10-10 20:30 | 165 | 164
2018-10-10 21:00 | 177 | 177
2018-10-10 21:30 | 181 | 181
2018-10-10 22:00 | 173 | 172
2018-10-10 22:30 | 184 | 183
2018-10-10 23:00 | 214 | 214
2018-10-10 23:30 | 209 | 209
2018-10-11 | 199 | 199
2018-10-11 00:30 | 195 | 195
2018-10-11 01:00 | 192 | 191
2018-10-11 01:30 | 194 | 194
2018-10-11 02:00 | 193 | 193
2018-10-11 02:30 | 194 | 194
2018-10-11 03:00 | 191 | 191
2018-10-11 03:30 | 192 | 191
2018-10-11 04:00 | 193 | 192
2018-10-11 04:30 | 196 | 196
2018-10-11 05:00 | 198 | 197
2018-10-11 05:30 | 204 | 203
2018-10-11 06:00 | 208 | 208
2018-10-11 06:30 | 202 | 201
2018-10-11 07:00 | 177 | 176
2018-10-11 07:30 | 186 | 186
2018-10-11 08:00 | 184 | 184
2018-10-11 08:30 | 177 | 176
2018-10-11 09:00 | 153 | 152
2018-10-11 09:30 | 131 | 130
2018-10-11 10:00 | 110 | 109
2018-10-11 10:30 | 104 | 102
2018-10-11 11:00 | 100 | 99
2018-10-11 11:30 | 99 | 97
2018-10-11 12:00 | 102 | 101
2018-10-11 12:30 | 106 | 105
2018-10-11 13:00 | 101 | 99
2018-10-11 13:30 | 106 | 105
2018-10-11 14:00 | 114 | 113
2018-10-11 14:30 | 115 | 114
2018-10-11 15:00 | 115 | 114
2018-10-11 15:30 | 130 | 130
2018-10-11 16:00 | 160 | 159
2018-10-11 16:30 | 180 | 180
2018-10-11 17:00 | 182 | 182
2018-10-11 17:30 | 205 | 205
2018-10-11 18:00 | 242 | 241
2018-10-11 18:30 | 271 | 270
2018-10-11 19:00 | 283 | 282
2018-10-11 19:30 | 294 | 294
2018-10-11 20:00 | 283 | 283
2018-10-11 20:30 | 270 | 269
2018-10-11 21:00 | 263 | 262
2018-10-11 21:30 | 267 | 267
2018-10-11 22:00 | 261 | 260
2018-10-11 22:30 | 252 | 252
2018-10-11 23:00 | 239 | 238
2018-10-11 23:30 | 227 | 227
2018-10-12 | 215 | 214
2018-10-12 00:30 | 215 | 215
2018-10-12 01:00 | 207 | 206
2018-10-12 01:30 | 209 | 209
2018-10-12 02:00 | 204 | 204
2018-10-12 02:30 | 202 | 202
2018-10-12 03:00 | 197 | 196
2018-10-12 03:30 | 193 | 193
2018-10-12 04:00 | 183 | 183
2018-10-12 04:30 | 194 | 194
2018-10-12 05:00 | 198 | 198
2018-10-12 05:30 | 203 | 202
2018-10-12 06:00 | 207 | 207
2018-10-12 06:30 | 215 | 215
2018-10-12 07:00 | 203 | 203
2018-10-12 07:30 | 191 | 190
2018-10-12 08:00 | 181 | 180
2018-10-12 08:30 | 172 | 172
2018-10-12 09:00 | 153 | 153
2018-10-12 09:30 | 136 | 136
2018-10-12 10:00 | 118 | 117
2018-10-12 10:30 | 117 | 117
2018-10-12 11:00 | 129 | 128
2018-10-12 11:30 | 121 | 120
2018-10-12 12:00 | 115 | 114
2018-10-12 12:30 | 113 | 112
2018-10-12 13:00 | 120 | 119
2018-10-12 13:30 | 119 | 118
2018-10-12 14:00 | 105 | 104
2018-10-12 14:30 | 122 | 121
2018-10-12 15:00 | 122 | 121
2018-10-12 15:30 | 137 | 137
2018-10-12 16:00 | 149 | 148
2018-10-12 16:30 | 176 | 175
2018-10-12 17:00 | 179 | 178
2018-10-12 17:30 | 213 | 212
2018-10-12 18:00 | 224 | 223
2018-10-12 18:30 | 237 | 236
2018-10-12 19:00 | 248 | 247
2018-10-12 19:30 | 255 | 255
2018-10-12 20:00 | 253 | 253
2018-10-12 20:30 | 254 | 253
2018-10-12 21:00 | 237 | 236
2018-10-12 21:30 | 223 | 222
2018-10-12 22:00 | 227 | 226
2018-10-12 22:30 | 206 | 205
2018-10-12 23:00 | 199 | 198
2018-10-12 23:30 | 194 | 193
2018-10-13 | 211 | 210
2018-10-13 00:30 | 217 | 216
2018-10-13 01:00 | 199 | 198
2018-10-13 01:30 | 203 | 202
2018-10-13 02:00 | 203 | 202
2018-10-13 02:30 | 193 | 192
2018-10-13 03:00 | 189 | 188
2018-10-13 03:30 | 190 | 189
2018-10-13 04:00 | 189 | 188
2018-10-13 04:30 | 193 | 192
2018-10-13 05:00 | 195 | 194
2018-10-13 05:30 | 200 | 199
2018-10-13 06:00 | 200 | 200
2018-10-13 06:30 | 205 | 204
2018-10-13 07:00 | 199 | 198
2018-10-13 07:30 | 200 | 199
2018-10-13 08:00 | 177 | 176
2018-10-13 08:30 | 148 | 147
2018-10-13 09:00 | 151 | 150
2018-10-13 09:30 | 169 | 168
2018-10-13 10:00 | 191 | 190
2018-10-13 10:30 | 167 | 167
2018-10-13 11:00 | 150 | 149
2018-10-13 11:30 | 152 | 151
2018-10-13 12:00 | 158 | 157
2018-10-13 12:30 | 160 | 159
2018-10-13 13:00 | 139 | 138
2018-10-13 13:30 | 160 | 159
2018-10-13 14:00 | 166 | 165
2018-10-13 14:30 | 161 | 160
2018-10-13 15:00 | 177 | 177
2018-10-13 15:30 | 188 | 187
2018-10-13 16:00 | 210 | 209
2018-10-13 16:30 | 208 | 208
2018-10-13 17:00 | 209 | 209
2018-10-13 17:30 | 203 | 202
2018-10-13 18:00 | 219 | 218
2018-10-13 18:30 | 239 | 238
2018-10-13 19:00 | 243 | 243
2018-10-13 19:30 | 246 | 246
2018-10-13 20:00 | 238 | 237
2018-10-13 20:30 | 243 | 243
2018-10-13 21:00 | 236 | 236
2018-10-13 21:30 | 232 | 231
2018-10-13 22:00 | 216 | 215
2018-10-13 22:30 | 207 | 206
2018-10-13 23:00 | 199 | 199
2018-10-13 23:30 | 196 | 195
2018-10-14 | 188 | 187
2018-10-14 00:30 | 187 | 187
2018-10-14 01:00 | 184 | 183
2018-10-14 01:30 | 183 | 182
2018-10-14 02:00 | 176 | 175
2018-10-14 02:30 | 174 | 173
2018-10-14 03:00 | 177 | 176
2018-10-14 03:30 | 182 | 181
2018-10-14 04:00 | 179 | 178
2018-10-14 04:30 | 178 | 177
2018-10-14 05:00 | 183 | 182
2018-10-14 05:30 | 186 | 185
2018-10-14 06:00 | 181 | 180
2018-10-14 06:30 | 178 | 177
2018-10-14 07:00 | 168 | 167
2018-10-14 07:30 | 159 | 158
2018-10-14 08:00 | 168 | 167
2018-10-14 08:30 | 158 | 157
2018-10-14 09:00 | 135 | 134
2018-10-14 09:30 | 116 | 115
2018-10-14 10:00 | 115 | 114
2018-10-14 10:30 | 104 | 103
2018-10-14 11:00 | 94 | 92
2018-10-14 11:30 | 94 | 93
2018-10-14 12:00 | 91 | 90
2018-10-14 12:30 | 85 | 83
2018-10-14 13:00 | 82 | 80
2018-10-14 13:30 | 68 | 66
2018-10-14 14:00 | 58 | 53
2018-10-14 14:30 | 70 | 67
2018-10-14 15:00 | 95 | 94
2018-10-14 15:30 | 112 | 111
2018-10-14 16:00 | 127 | 126
2018-10-14 16:30 | 136 | 135
2018-10-14 17:00 | 147 | 147
2018-10-14 17:30 | 168 | 167
2018-10-14 18:00 | 195 | 195
2018-10-14 18:30 | 227 | 226
2018-10-14 19:00 | 245 | 244
2018-10-14 19:30 | 259 | 259
2018-10-14 20:00 | 253 | 253
2018-10-14 20:30 | 237 | 237
2018-10-14 21:00 | 235 | 234
2018-10-14 21:30 | 234 | 234
2018-10-14 22:00 | 225 | 225
2018-10-14 22:30 | 215 | 214
2018-10-14 23:00 | 203 | 203
2018-10-14 23:30 | 189 | 188
2018-10-15 | 185 | 184
2018-10-15 00:30 | 185 | 184
2018-10-15 01:00 | 174 | 173
2018-10-15 01:30 | 166 | 165
2018-10-15 02:00 | 159 | 158
2018-10-15 02:30 | 162 | 161
2018-10-15 03:00 | 159 | 158
2018-10-15 03:30 | 163 | 162
2018-10-15 04:00 | 164 | 164
2018-10-15 04:30 | 171 | 170
2018-10-15 05:00 | 178 | 177
2018-10-15 05:30 | 179 | 178
2018-10-15 06:00 | 187 | 186
2018-10-15 06:30 | 198 | 198
2018-10-15 07:00 | 185 | 184
2018-10-15 07:30 | 198 | 198
2018-10-15 08:00 | 195 | 194
2018-10-15 08:30 | 194 | 194
2018-10-15 09:00 | 188 | 187
2018-10-15 09:30 | 180 | 179
2018-10-15 10:00 | 169 | 169
2018-10-15 10:30 | 158 | 158
2018-10-15 11:00 | 145 | 145
2018-10-15 11:30 | 139 | 139
2018-10-15 12:00 | 131 | 130
2018-10-15 12:30 | 120 | 119
2018-10-15 13:00 | 115 | 114
2018-10-15 13:30 | 119 | 118
2018-10-15 14:00 | 130 | 130
2018-10-15 14:30 | 137 | 136
2018-10-15 15:00 | 150 | 149
2018-10-15 15:30 | 159 | 158
2018-10-15 16:00 | 183 | 182
2018-10-15 16:30 | 195 | 194
2018-10-15 17:00 | 201 | 201
2018-10-15 17:30 | 224 | 223
2018-10-15 18:00 | 249 | 248
2018-10-15 18:30 | 259 | 258
2018-10-15 19:00 | 273 | 273
2018-10-15 19:30 | 284 | 283
2018-10-15 20:00 | 273 | 273
2018-10-15 20:30 | 266 | 265
2018-10-15 21:00 | 263 | 263
2018-10-15 21:30 | 255 | 254
2018-10-15 22:00 | 239 | 239
2018-10-15 22:30 | 226 | 225
2018-10-15 23:00 | 212 | 211
2018-10-15 23:30 | 209 | 209
2018-10-16 | 200 | 199
2018-10-16 00:30 | 194 | 194
2018-10-16 01:00 | 191 | 190
2018-10-16 01:30 | 191 | 190
2018-10-16 02:00 | 191 | 190
2018-10-16 02:30 | 189 | 188
2018-10-16 03:00 | 186 | 186
2018-10-16 03:30 | 186 | 186
2018-10-16 04:00 | 188 | 188
2018-10-16 04:30 | 190 | 189
2018-10-16 05:00 | 192 | 192
2018-10-16 05:30 | 196 | 195
2018-10-16 06:00 | 205 | 204
2018-10-16 06:30 | 214 | 213
2018-10-16 07:00 | 212 | 211
2018-10-16 07:30 | 210 | 210
2018-10-16 08:00 | 208 | 207
2018-10-16 08:30 | 196 | 195
2018-10-16 09:00 | 175 | 174
2018-10-16 09:30 | 158 | 158
2018-10-16 10:00 | 125 | 124
2018-10-16 10:30 | 124 | 123
2018-10-16 11:00 | 119 | 118
2018-10-16 11:30 | 118 | 117
2018-10-16 12:00 | 116 | 115
2018-10-16 12:30 | 129 | 128
2018-10-16 13:00 | 128 | 127
2018-10-16 13:30 | 128 | 127
2018-10-16 14:00 | 126 | 125
2018-10-16 14:30 | 142 | 141
2018-10-16 15:00 | 164 | 164
2018-10-16 15:30 | 204 | 203
2018-10-16 16:00 | 197 | 196
2018-10-16 16:30 | 237 | 236
2018-10-16 17:00 | 259 | 259
2018-10-16 17:30 | 253 | 252
2018-10-16 18:00 | 262 | 261
2018-10-16 18:30 | 269 | 268
2018-10-16 19:00 | 287 | 286
2018-10-16 19:30 | 307 | 306
2018-10-16 20:00 | 301 | 301
2018-10-16 20:30 | 286 | 285
2018-10-16 21:00 | 270 | 269
2018-10-16 21:30 | 273 | 273
2018-10-16 22:00 | 261 | 260
2018-10-16 22:30 | 247 | 246
2018-10-16 23:00 | 236 | 235
2018-10-16 23:30 | 225 | 225
2018-10-17 | 218 | 217
2018-10-17 00:30 | 211 | 210
2018-10-17 01:00 | 210 | 209
2018-10-17 01:30 | 207 | 206
2018-10-17 02:00 | 201 | 200
2018-10-17 02:30 | 197 | 196
2018-10-17 03:00 | 195 | 194
2018-10-17 03:30 | 195 | 194
2018-10-17 04:00 | 195 | 194
2018-10-17 04:30 | 195 | 194
2018-10-17 05:00 | 195 | 194
2018-10-17 05:30 | 204 | 203
2018-10-17 06:00 | 211 | 210
2018-10-17 06:30 | 209 | 208
2018-10-17 07:00 | 209 | 208
2018-10-17 07:30 | 220 | 219
2018-10-17 08:00 | 209 | 209
2018-10-17 08:30 | 173 | 172
2018-10-17 09:00 | 140 | 139
2018-10-17 09:30 | 120 | 119
2018-10-17 10:00 | 130 | 129
2018-10-17 10:30 | 109 | 108
2018-10-17 11:00 | 114 | 113
2018-10-17 11:30 | 119 | 118
2018-10-17 12:00 | 115 | 114
2018-10-17 12:30 | 126 | 125
2018-10-17 13:00 | 125 | 124
2018-10-17 13:30 | 130 | 128
2018-10-17 14:00 | 123 | 122
2018-10-17 14:30 | 129 | 128
2018-10-17 15:00 | 141 | 140
2018-10-17 15:30 | 157 | 156
2018-10-17 16:00 | 156 | 155
2018-10-17 16:30 | 178 | 177
2018-10-17 17:00 | 202 | 201
2018-10-17 17:30 | 224 | 223
2018-10-17 18:00 | 248 | 248
2018-10-17 18:30 | 268 | 267
2018-10-17 19:00 | 272 | 271
2018-10-17 19:30 | 298 | 296
2018-10-17 20:00 | 297 | 295
2018-10-17 20:30 | 284 | 283
2018-10-17 21:00 | 278 | 277
2018-10-17 21:30 | 267 | 265
2018-10-17 22:00 | 262 | 260
2018-10-17 22:30 | 244 | 243
2018-10-17 23:00 | 218 | 216
2018-10-17 23:30 | 207 | 206
2018-10-18 | 202 | 201
2018-10-18 00:30 | 193 | 192
2018-10-18 01:00 | 185 | 184
2018-10-18 01:30 | 187 | 187
2018-10-18 02:00 | 191 | 191
2018-10-18 02:30 | 193 | 193
2018-10-18 03:00 | 187 | 187
2018-10-18 03:30 | 189 | 189
2018-10-18 04:00 | 190 | 189
2018-10-18 04:30 | 188 | 187
2018-10-18 05:00 | 184 | 184
2018-10-18 05:30 | 175 | 174
2018-10-18 06:00 | 165 | 165
2018-10-18 06:30 | 168 | 167
2018-10-18 07:00 | 179 | 178
2018-10-18 07:30 | 177 | 177
2018-10-18 08:00 | 169 | 169
2018-10-18 08:30 | 168 | 167
2018-10-18 09:00 | 151 | 150
2018-10-18 09:30 | 145 | 143
2018-10-18 10:00 | 123 | 122
2018-10-18 10:30 | 122 | 121
2018-10-18 11:00 | 97 | 96
2018-10-18 11:30 | 80 | 79
2018-10-18 12:00 | 101 | 100
2018-10-18 12:30 | 103 | 102
2018-10-18 13:00 | 100 | 98
2018-10-18 13:30 | 83 | 81
2018-10-18 14:00 | 82 | 80
2018-10-18 14:30 | 100 | 99
2018-10-18 15:00 | 105 | 104
2018-10-18 15:30 | 122 | 121
2018-10-18 16:00 | 157 | 156
2018-10-18 16:30 | 178 | 177
2018-10-18 17:00 | 198 | 197
2018-10-18 17:30 | 208 | 207
2018-10-18 18:00 | 216 | 215
2018-10-18 18:30 | 235 | 235
2018-10-18 19:00 | 248 | 247
2018-10-18 19:30 | 264 | 263
2018-10-18 20:00 | 261 | 260
2018-10-18 20:30 | 258 | 258
2018-10-18 21:00 | 270 | 269
2018-10-18 21:30 | 261 | 261
2018-10-18 22:00 | 251 | 251
2018-10-18 22:30 | 233 | 232
2018-10-18 23:00 | 211 | 211
2018-10-18 23:30 | 197 | 196
2018-10-19 | 190 | 189
2018-10-19 00:30 | 180 | 179
2018-10-19 01:00 | 185 | 184
2018-10-19 01:30 | 197 | 197
2018-10-19 02:00 | 196 | 196
2018-10-19 02:30 | 190 | 190
2018-10-19 03:00 | 185 | 185
2018-10-19 03:30 | 185 | 184
2018-10-19 04:00 | 180 | 180
2018-10-19 04:30 | 181 | 181
2018-10-19 05:00 | 181 | 180
2018-10-19 05:30 | 176 | 176
2018-10-19 06:00 | 173 | 172
2018-10-19 06:30 | 164 | 163
2018-10-19 07:00 | 163 | 162
2018-10-19 07:30 | 141 | 140
2018-10-19 08:00 | 152 | 152
2018-10-19 08:30 | 136 | 135
2018-10-19 09:00 | 138 | 137
2018-10-19 09:30 | 138 | 138
2018-10-19 10:00 | 122 | 121
2018-10-19 10:30 | 125 | 124
2018-10-19 11:00 | 128 | 127
2018-10-19 11:30 | 124 | 123
2018-10-19 12:00 | 119 | 118
2018-10-19 12:30 | 111 | 110
2018-10-19 13:00 | 102 | 101
2018-10-19 13:30 | 104 | 103
2018-10-19 14:00 | 113 | 112
2018-10-19 14:30 | 114 | 113
2018-10-19 15:00 | 115 | 114
2018-10-19 15:30 | 127 | 126
2018-10-19 16:00 | 140 | 139
2018-10-19 16:30 | 160 | 159
2018-10-19 17:00 | 169 | 169
2018-10-19 17:30 | 170 | 169
2018-10-19 18:00 | 179 | 178
2018-10-19 18:30 | 184 | 184
2018-10-19 19:00 | 204 | 203
2018-10-19 19:30 | 222 | 221
2018-10-19 20:00 | 219 | 218
2018-10-19 20:30 | 210 | 209
2018-10-19 21:00 | 209 | 208
2018-10-19 21:30 | 207 | 206
2018-10-19 22:00 | 190 | 190
2018-10-19 22:30 | 176 | 176
2018-10-19 23:00 | 171 | 170
2018-10-19 23:30 | 170 | 169
2018-10-20 | 163 | 162
2018-10-20 00:30 | 162 | 161
2018-10-20 01:00 | 148 | 147
2018-10-20 01:30 | 144 | 143
2018-10-20 02:00 | 146 | 145
2018-10-20 02:30 | 144 | 143
2018-10-20 03:00 | 137 | 137
2018-10-20 03:30 | 139 | 139
2018-10-20 04:00 | 136 | 135
2018-10-20 04:30 | 143 | 142
2018-10-20 05:00 | 147 | 146
2018-10-20 05:30 | 148 | 147
2018-10-20 06:00 | 138 | 137
2018-10-20 06:30 | 129 | 128
2018-10-20 07:00 | 116 | 115
2018-10-20 07:30 | 106 | 105
2018-10-20 08:00 | 102 | 101
2018-10-20 08:30 | 101 | 100
2018-10-20 09:00 | 108 | 107
2018-10-20 09:30 | 122 | 121
2018-10-20 10:00 | 108 | 107
2018-10-20 10:30 | 93 | 92
2018-10-20 11:00 | 97 | 95
2018-10-20 11:30 | 87 | 85
2018-10-20 12:00 | 90 | 89
2018-10-20 12:30 | 89 | 87
2018-10-20 13:00 | 80 | 77
2018-10-20 13:30 | 81 | 79
2018-10-20 14:00 | 93 | 91
2018-10-20 14:30 | 91 | 89
2018-10-20 15:00 | 87 | 86
2018-10-20 15:30 | 106 | 105
2018-10-20 16:00 | 128 | 127
2018-10-20 16:30 | 146 | 146
2018-10-20 17:00 | 144 | 143
2018-10-20 17:30 | 179 | 178
2018-10-20 18:00 | 231 | 230
2018-10-20 18:30 | 244 | 243
2018-10-20 19:00 | 252 | 251
2018-10-20 19:30 | 261 | 260
2018-10-20 20:00 | 260 | 260
2018-10-20 20:30 | 253 | 252
2018-10-20 21:00 | 240 | 239
2018-10-20 21:30 | 229 | 228
2018-10-20 22:00 | 217 | 216
2018-10-20 22:30 | 209 | 208
2018-10-20 23:00 | 194 | 193
2018-10-20 23:30 | 184 | 183
2018-10-21 | 177 | 176
2018-10-21 00:30 | 175 | 174
2018-10-21 01:00 | 163 | 162
2018-10-21 01:30 | 153 | 152
2018-10-21 02:00 | 163 | 162
2018-10-21 02:30 | 161 | 160
2018-10-21 03:00 | 163 | 162
2018-10-21 03:30 | 163 | 162
2018-10-21 04:00 | 158 | 157
2018-10-21 04:30 | 168 | 167
2018-10-21 05:00 | 179 | 178
2018-10-21 05:30 | 176 | 175
2018-10-21 06:00 | 167 | 166
2018-10-21 06:30 | 162 | 161
2018-10-21 07:00 | 141 | 139
2018-10-21 07:30 | 126 | 125
2018-10-21 08:00 | 121 | 120
2018-10-21 08:30 | 123 | 122
2018-10-21 09:00 | 120 | 119
2018-10-21 09:30 | 118 | 117
2018-10-21 10:00 | 105 | 104
2018-10-21 10:30 | 107 | 106
2018-10-21 11:00 | 91 | 90
2018-10-21 11:30 | 86 | 85
2018-10-21 12:00 | 82 | 81
2018-10-21 12:30 | 81 | 80
2018-10-21 13:00 | 82 | 81
2018-10-21 13:30 | 82 | 81
2018-10-21 14:00 | 86 | 84
2018-10-21 14:30 | 95 | 94
2018-10-21 15:00 | 103 | 102
2018-10-21 15:30 | 118 | 117
2018-10-21 16:00 | 122 | 121
2018-10-21 16:30 | 154 | 154
2018-10-21 17:00 | 180 | 179
2018-10-21 17:30 | 214 | 214
2018-10-21 18:00 | 242 | 242
2018-10-21 18:30 | 278 | 277
2018-10-21 19:00 | 291 | 291
2018-10-21 19:30 | 287 | 286
2018-10-21 20:00 | 270 | 269
2018-10-21 20:30 | 263 | 262
2018-10-21 21:00 | 262 | 260
2018-10-21 21:30 | 258 | 257
2018-10-21 22:00 | 250 | 248
2018-10-21 22:30 | 237 | 236
2018-10-21 23:00 | 227 | 225
2018-10-21 23:30 | 222 | 220
2018-10-22 | 219 | 218
2018-10-22 00:30 | 214 | 212
2018-10-22 01:00 | 205 | 203
2018-10-22 01:30 | 196 | 194
2018-10-22 02:00 | 196 | 194
2018-10-22 02:30 | 190 | 189
2018-10-22 03:00 | 194 | 193
2018-10-22 03:30 | 197 | 195
2018-10-22 04:00 | 196 | 195
2018-10-22 04:30 | 200 | 199
2018-10-22 05:00 | 204 | 203
2018-10-22 05:30 | 206 | 205
2018-10-22 06:00 | 215 | 214
2018-10-22 06:30 | 222 | 221
2018-10-22 07:00 | 216 | 215
2018-10-22 07:30 | 205 | 204
2018-10-22 08:00 | 185 | 184
2018-10-22 08:30 | 169 | 168
2018-10-22 09:00 | 170 | 169
2018-10-22 09:30 | 140 | 139
2018-10-22 10:00 | 128 | 127
2018-10-22 10:30 | 128 | 127
2018-10-22 11:00 | 122 | 121
2018-10-22 11:30 | 122 | 120
2018-10-22 12:00 | 123 | 122
2018-10-22 12:30 | 128 | 127
2018-10-22 13:00 | 140 | 139
2018-10-22 13:30 | 130 | 129
2018-10-22 14:00 | 145 | 144
2018-10-22 14:30 | 153 | 152
2018-10-22 15:00 | 149 | 148
2018-10-22 15:30 | 156 | 155
2018-10-22 16:00 | 174 | 173
2018-10-22 16:30 | 198 | 196
2018-10-22 17:00 | 216 | 215
2018-10-22 17:30 | 244 | 244
2018-10-22 18:00 | 280 | 279
2018-10-22 18:30 | 280 | 279
2018-10-22 19:00 | 276 | 274
2018-10-22 19:30 | 289 | 288
2018-10-22 20:00 | 301 | 300
2018-10-22 20:30 | 292 | 291
2018-10-22 21:00 | 285 | 284
2018-10-22 21:30 | 282 | 281
2018-10-22 22:00 | 275 | 274
2018-10-22 22:30 | 253 | 252
2018-10-22 23:00 | 234 | 234
2018-10-22 23:30 | 224 | 223
2018-10-23 | 215 | 214
2018-10-23 00:30 | 207 | 206
2018-10-23 01:00 | 197 | 197
2018-10-23 01:30 | 188 | 187
2018-10-23 02:00 | 180 | 179
2018-10-23 02:30 | 184 | 183
2018-10-23 03:00 | 187 | 186
2018-10-23 03:30 | 195 | 195
2018-10-23 04:00 | 194 | 193
2018-10-23 04:30 | 195 | 195
2018-10-23 05:00 | 198 | 197
2018-10-23 05:30 | 206 | 205
2018-10-23 06:00 | 215 | 214
2018-10-23 06:30 | 212 | 212
2018-10-23 07:00 | 171 | 171
2018-10-23 07:30 | 134 | 133
2018-10-23 08:00 | 155 | 154
2018-10-23 08:30 | 172 | 171
2018-10-23 09:00 | 157 | 156
2018-10-23 09:30 | 153 | 152
2018-10-23 10:00 | 148 | 146
2018-10-23 10:30 | 221 | 221
2018-10-23 11:00 | 239 | 239
2018-10-23 11:30 | 217 | 216
2018-10-23 12:00 | 174 | 173
2018-10-23 12:30 | 176 | 175
2018-10-23 13:00 | 161 | 160
2018-10-23 13:30 | 134 | 133
2018-10-23 14:00 | 162 | 161
2018-10-23 14:30 | 182 | 182
2018-10-23 15:00 | 203 | 203
2018-10-23 15:30 | 201 | 200
2018-10-23 16:00 | 200 | 199
2018-10-23 16:30 | 265 | 264
2018-10-23 17:00 | 239 | 239
2018-10-23 17:30 | 289 | 289
2018-10-23 18:00 | 341 | 341
2018-10-23 18:30 | 352 | 352
2018-10-23 19:00 | 295 | 294
2018-10-23 19:30 | 316 | 316
2018-10-23 20:00 | 349 | 349
2018-10-23 20:30 | 350 | 350
2018-10-23 21:00 | 331 | 331
2018-10-23 21:30 | 332 | 332
2018-10-23 22:00 | 319 | 319
2018-10-23 22:30 | 279 | 278
2018-10-23 23:00 | 250 | 250
2018-10-23 23:30 | 235 | 235
2018-10-24 | 232 | 232
2018-10-24 00:30 | 234 | 234
2018-10-24 01:00 | 221 | 220
2018-10-24 01:30 | 202 | 202
2018-10-24 02:00 | 197 | 196
2018-10-24 02:30 | 198 | 197
2018-10-24 03:00 | 207 | 207
2018-10-24 03:30 | 202 | 201
2018-10-24 04:00 | 199 | 199
2018-10-24 04:30 | 182 | 181
2018-10-24 05:00 | 205 | 205
2018-10-24 05:30 | 227 | 227
2018-10-24 06:00 | 211 | 210
2018-10-24 06:30 | 159 | 158
2018-10-24 07:00 | 135 | 133
2018-10-24 07:30 | 116 | 114
2018-10-24 08:00 | 107 | 104
2018-10-24 08:30 | 117 | 114
2018-10-24 09:00 | 101 | 98
2018-10-24 09:30 | 132 | 131
2018-10-24 10:00 | 117 | 115
2018-10-24 10:30 | 106 | 104
2018-10-24 11:00 | 101 | 99
2018-10-24 11:30 | 102 | 100
2018-10-24 12:00 | 107 | 105
2018-10-24 12:30 | 105 | 103
2018-10-24 13:00 | 113 | 112
2018-10-24 13:30 | 130 | 128
2018-10-24 14:00 | 135 | 134
2018-10-24 14:30 | 150 | 149
2018-10-24 15:00 | 158 | 157
2018-10-24 15:30 | 139 | 138
2018-10-24 16:00 | 171 | 170
2018-10-24 16:30 | 230 | 230
2018-10-24 17:00 | 220 | 220
2018-10-24 17:30 | 223 | 223
2018-10-24 18:00 | 280 | 280
2018-10-24 18:30 | 358 | 358
2018-10-24 19:00 | 314 | 313
2018-10-24 19:30 | 366 | 366
2018-10-24 20:00 | 346 | 346
2018-10-24 20:30 | 314 | 314
2018-10-24 21:00 | 293 | 292
2018-10-24 21:30 | 295 | 295
2018-10-24 22:00 | 273 | 273
2018-10-24 22:30 | 242 | 241
2018-10-24 23:00 | 218 | 218
2018-10-24 23:30 | 224 | 224
2018-10-25 | 259 | 259
2018-10-25 00:30 | 264 | 264
2018-10-25 01:00 | 247 | 246
2018-10-25 01:30 | 232 | 232
2018-10-25 02:00 | 233 | 233
2018-10-25 02:30 | 251 | 251
2018-10-25 03:00 | 252 | 252
2018-10-25 03:30 | 259 | 259
2018-10-25 04:00 | 267 | 267
2018-10-25 04:30 | 274 | 274
2018-10-25 05:00 | 302 | 301
2018-10-25 05:30 | 314 | 313
2018-10-25 06:00 | 288 | 287
2018-10-25 06:30 | 286 | 286
2018-10-25 07:00 | 258 | 258
2018-10-25 07:30 | 213 | 212
2018-10-25 08:00 | 211 | 211
2018-10-25 08:30 | 211 | 211
2018-10-25 09:00 | 188 | 188
2018-10-25 09:30 | 155 | 154
2018-10-25 10:00 | 129 | 128
2018-10-25 10:30 | 118 | 116
2018-10-25 11:00 | 105 | 102
2018-10-25 11:30 | 131 | 129
2018-10-25 12:00 | 86 | 82
2018-10-25 12:30 | 87 | 83
2018-10-25 13:00 | 93 | 89
2018-10-25 13:30 | 98 | 95
2018-10-25 14:00 | 120 | 119
2018-10-25 14:30 | 125 | 124
2018-10-25 15:00 | 143 | 142
2018-10-25 15:30 | 178 | 177
2018-10-25 16:00 | 192 | 192
2018-10-25 16:30 | 256 | 255
2018-10-25 17:00 | 276 | 276
2018-10-25 17:30 | 317 | 317
2018-10-25 18:00 | 384 | 384
2018-10-25 18:30 | 448 | 448
2018-10-25 19:00 | 481 | 481
2018-10-25 19:30 | 490 | 490
2018-10-25 20:00 | 487 | 487
2018-10-25 20:30 | 466 | 466
2018-10-25 21:00 | 477 | 477
2018-10-25 21:30 | 444 | 444
2018-10-25 22:00 | 426 | 425
2018-10-25 22:30 | 386 | 386
2018-10-25 23:00 | 359 | 358
2018-10-25 23:30 | 334 | 334
2018-10-26 | 301 | 301
2018-10-26 00:30 | 295 | 295
2018-10-26 01:00 | 277 | 277
2018-10-26 01:30 | 277 | 277
2018-10-26 02:00 | 264 | 264
2018-10-26 02:30 | 264 | 264
2018-10-26 03:00 | 264 | 264
2018-10-26 03:30 | 288 | 288
2018-10-26 04:00 | 293 | 292
2018-10-26 04:30 | 289 | 289
2018-10-26 05:00 | 292 | 292
2018-10-26 05:30 | 308 | 307
2018-10-26 06:00 | 299 | 299
2018-10-26 06:30 | 282 | 282
2018-10-26 07:00 | 254 | 254
2018-10-26 07:30 | 227 | 226
2018-10-26 08:00 | 210 | 209
2018-10-26 08:30 | 203 | 202
2018-10-26 09:00 | 192 | 191
2018-10-26 09:30 | 172 | 171
2018-10-26 10:00 | 93 | 92
2018-10-26 10:30 | 77 | 74
2018-10-26 11:00 | 76 | 72
2018-10-26 11:30 | 77 | 73
2018-10-26 12:00 | 84 | 81
2018-10-26 12:30 | 85 | 82
2018-10-26 13:00 | 85 | 82
2018-10-26 13:30 | 82 | 79
2018-10-26 14:00 | 85 | 83
2018-10-26 14:30 | 93 | 91
2018-10-26 15:00 | 103 | 101
2018-10-26 15:30 | 110 | 108
2018-10-26 16:00 | 113 | 112
2018-10-26 16:30 | 121 | 120
2018-10-26 17:00 | 158 | 158
2018-10-26 17:30 | 171 | 170
2018-10-26 18:00 | 212 | 211
2018-10-26 18:30 | 234 | 233
2018-10-26 19:00 | 258 | 258
2018-10-26 19:30 | 279 | 279
2018-10-26 20:00 | 282 | 281
2018-10-26 20:30 | 273 | 272
2018-10-26 21:00 | 265 | 265
2018-10-26 21:30 | 263 | 262
2018-10-26 22:00 | 258 | 258
2018-10-26 22:30 | 246 | 246
2018-10-26 23:00 | 232 | 232
2018-10-26 23:30 | 217 | 217
2018-10-27 | 210 | 210
2018-10-27 00:30 | 210 | 210
2018-10-27 01:00 | 199 | 199
2018-10-27 01:30 | 191 | 191
2018-10-27 02:00 | 188 | 188
2018-10-27 02:30 | 186 | 185
2018-10-27 03:00 | 187 | 186
2018-10-27 03:30 | 186 | 186
2018-10-27 04:00 | 183 | 183
2018-10-27 04:30 | 184 | 184
2018-10-27 05:00 | 186 | 186
2018-10-27 05:30 | 190 | 190
2018-10-27 06:00 | 187 | 187
2018-10-27 06:30 | 175 | 174
2018-10-27 07:00 | 139 | 138
2018-10-27 07:30 | 111 | 110
2018-10-27 08:00 | 101 | 98
2018-10-27 08:30 | 92 | 89
2018-10-27 09:00 | 85 | 82
2018-10-27 09:30 | 75 | 70
2018-10-27 10:00 | 60 | 51
2018-10-27 10:30 | 42 | 39
2018-10-27 11:00 | 46 | 40
2018-10-27 11:30 | 50 | 41
2018-10-27 12:00 | 51 | 43
2018-10-27 12:30 | 55 | 46
2018-10-27 13:00 | 59 | 50
2018-10-27 13:30 | 64 | 57
2018-10-27 14:00 | 64 | 58
2018-10-27 14:30 | 73 | 67
2018-10-27 15:00 | 82 | 79
2018-10-27 15:30 | 100 | 99
2018-10-27 16:00 | 119 | 118
2018-10-27 16:30 | 149 | 148
2018-10-27 17:00 | 162 | 161
2018-10-27 17:30 | 206 | 205
2018-10-27 18:00 | 246 | 246
2018-10-27 18:30 | 262 | 262
2018-10-27 19:00 | 269 | 269
2018-10-27 19:30 | 266 | 265
2018-10-27 20:00 | 255 | 255
2018-10-27 20:30 | 241 | 241
2018-10-27 21:00 | 227 | 226
2018-10-27 21:30 | 231 | 231
2018-10-27 22:00 | 223 | 223
2018-10-27 22:30 | 210 | 210
2018-10-27 23:00 | 212 | 211
2018-10-27 23:30 | 204 | 204
2018-10-28 | 193 | 192
2018-10-28 00:30 | 196 | 195
2018-10-28 01:00 | 189 | 189
2018-10-28 01:30 | 185 | 185
2018-10-28 02:00 | 184 | 184
2018-10-28 02:30 | 181 | 181
2018-10-28 03:00 | 178 | 177
2018-10-28 03:30 | 168 | 167
2018-10-28 04:00 | 166 | 166
2018-10-28 04:30 | 165 | 165
2018-10-28 05:00 | 165 | 165
2018-10-28 05:30 | 179 | 179
2018-10-28 06:00 | 185 | 184
2018-10-28 06:30 | 171 | 170
2018-10-28 07:00 | 132 | 131
2018-10-28 07:30 | 104 | 102
2018-10-28 08:00 | 92 | 89
2018-10-28 08:30 | 84 | 80
2018-10-28 09:00 | 82 | 77
2018-10-28 09:30 | 77 | 72
2018-10-28 10:00 | 69 | 62
2018-10-28 10:30 | 71 | 64
2018-10-28 11:00 | 77 | 71
2018-10-28 11:30 | 77 | 72
2018-10-28 12:00 | 81 | 77
2018-10-28 12:30 | 81 | 77
2018-10-28 13:00 | 88 | 84
2018-10-28 13:30 | 85 | 81
2018-10-28 14:00 | 93 | 90
2018-10-28 14:30 | 92 | 89
2018-10-28 15:00 | 90 | 86
2018-10-28 15:30 | 103 | 100
2018-10-28 16:00 | 123 | 122
2018-10-28 16:30 | 158 | 157
2018-10-28 17:00 | 196 | 195
2018-10-28 17:30 | 222 | 222
2018-10-28 18:00 | 270 | 270
2018-10-28 18:30 | 294 | 294
2018-10-28 19:00 | 304 | 303
2018-10-28 19:30 | 304 | 303
2018-10-28 20:00 | 301 | 300
2018-10-28 20:30 | 289 | 289
2018-10-28 21:00 | 286 | 286
2018-10-28 21:30 | 288 | 288
2018-10-28 22:00 | 270 | 270
2018-10-28 22:30 | 262 | 261
2018-10-28 23:00 | 254 | 253
2018-10-28 23:30 | 246 | 246
2018-10-29 | 239 | 239
2018-10-29 00:30 | 239 | 239
2018-10-29 01:00 | 230 | 230
2018-10-29 01:30 | 225 | 224
2018-10-29 02:00 | 214 | 214
2018-10-29 02:30 | 211 | 211
2018-10-29 03:00 | 214 | 214
2018-10-29 03:30 | 212 | 212
2018-10-29 04:00 | 209 | 208
2018-10-29 04:30 | 212 | 212
2018-10-29 05:00 | 213 | 212
2018-10-29 05:30 | 219 | 219
2018-10-29 06:00 | 221 | 221
2018-10-29 06:30 | 224 | 224
2018-10-29 07:00 | 205 | 204
2018-10-29 07:30 | 180 | 180
2018-10-29 08:00 | 163 | 162
2018-10-29 08:30 | 165 | 164
2018-10-29 09:00 | 150 | 149
2018-10-29 09:30 | 135 | 134
2018-10-29 10:00 | 133 | 132
2018-10-29 10:30 | 132 | 131
2018-10-29 11:00 | 134 | 133
2018-10-29 11:30 | 140 | 139
2018-10-29 12:00 | 144 | 143
2018-10-29 12:30 | 150 | 149
2018-10-29 13:00 | 153 | 152
2018-10-29 13:30 | 151 | 150
2018-10-29 14:00 | 146 | 145
2018-10-29 14:30 | 152 | 151
2018-10-29 15:00 | 155 | 154
2018-10-29 15:30 | 166 | 166
2018-10-29 16:00 | 184 | 184
2018-10-29 16:30 | 229 | 229
2018-10-29 17:00 | 267 | 266
2018-10-29 17:30 | 276 | 276
2018-10-29 18:00 | 299 | 299
2018-10-29 18:30 | 315 | 315
2018-10-29 19:00 | 327 | 326
2018-10-29 19:30 | 328 | 328
2018-10-29 20:00 | 316 | 315
2018-10-29 20:30 | 309 | 309
2018-10-29 21:00 | 301 | 301
2018-10-29 21:30 | 291 | 291
2018-10-29 22:00 | 276 | 276
2018-10-29 22:30 | 265 | 265
2018-10-29 23:00 | 254 | 253
2018-10-29 23:30 | 241 | 240
2018-10-30 | 232 | 232
2018-10-30 00:30 | 231 | 231
2018-10-30 01:00 | 218 | 218
2018-10-30 01:30 | 213 | 213
2018-10-30 02:00 | 209 | 209
2018-10-30 02:30 | 205 | 205
2018-10-30 03:00 | 196 | 196
2018-10-30 03:30 | 192 | 192
2018-10-30 04:00 | 194 | 194
2018-10-30 04:30 | 207 | 207
2018-10-30 05:00 | 208 | 208
2018-10-30 05:30 | 216 | 216
2018-10-30 06:00 | 223 | 223
2018-10-30 06:30 | 231 | 231
2018-10-30 07:00 | 201 | 200
2018-10-30 07:30 | 202 | 202
2018-10-30 08:00 | 205 | 204
2018-10-30 08:30 | 201 | 200
2018-10-30 09:00 | 205 | 205
2018-10-30 09:30 | 185 | 184
2018-10-30 10:00 | 162 | 161
2018-10-30 10:30 | 144 | 143
2018-10-30 11:00 | 146 | 145
2018-10-30 11:30 | 146 | 145
2018-10-30 12:00 | 140 | 139
2018-10-30 12:30 | 147 | 146
2018-10-30 13:00 | 144 | 143
2018-10-30 13:30 | 136 | 135
2018-10-30 14:00 | 144 | 143
2018-10-30 14:30 | 155 | 154
2018-10-30 15:00 | 164 | 163
2018-10-30 15:30 | 176 | 175
2018-10-30 16:00 | 227 | 227
2018-10-30 16:30 | 273 | 273
2018-10-30 17:00 | 291 | 291
2018-10-30 17:30 | 302 | 302
2018-10-30 18:00 | 306 | 306
2018-10-30 18:30 | 311 | 311
2018-10-30 19:00 | 312 | 312
2018-10-30 19:30 | 321 | 321
2018-10-30 20:00 | 321 | 321
2018-10-30 20:30 | 312 | 312
2018-10-30 21:00 | 304 | 304
2018-10-30 21:30 | 301 | 301
2018-10-30 22:00 | 290 | 290
2018-10-30 22:30 | 272 | 272
2018-10-30 23:00 | 257 | 256
2018-10-30 23:30 | 246 | 245
2018-10-31 | 241 | 241
2018-10-31 00:30 | 243 | 243
2018-10-31 01:00 | 232 | 231
2018-10-31 01:30 | 225 | 225
2018-10-31 02:00 | 220 | 220
2018-10-31 02:30 | 216 | 216
2018-10-31 03:00 | 214 | 213
2018-10-31 03:30 | 213 | 213
2018-10-31 04:00 | 212 | 211
2018-10-31 04:30 | 209 | 209
2018-10-31 05:00 | 209 | 209
2018-10-31 05:30 | 215 | 215
2018-10-31 06:00 | 216 | 216
2018-10-31 06:30 | 207 | 206
2018-10-31 07:00 | 196 | 196
2018-10-31 07:30 | 190 | 190
2018-10-31 08:00 | 178 | 177
2018-10-31 08:30 | 169 | 169
2018-10-31 09:00 | 129 | 128
2018-10-31 09:30 | 140 | 139
2018-10-31 10:00 | 131 | 129
2018-10-31 10:30 | 130 | 129
2018-10-31 11:00 | 128 | 127
2018-10-31 11:30 | 134 | 133
2018-10-31 12:00 | 124 | 122
2018-10-31 12:30 | 129 | 128
2018-10-31 13:00 | 137 | 136
2018-10-31 13:30 | 132 | 131
2018-10-31 14:00 | 142 | 141
2018-10-31 14:30 | 147 | 147
2018-10-31 15:00 | 162 | 161
2018-10-31 15:30 | 184 | 183
2018-10-31 16:00 | 175 | 174
2018-10-31 16:30 | 185 | 184
2018-10-31 17:00 | 169 | 168
2018-10-31 17:30 | 192 | 191
2018-10-31 18:00 | 227 | 227
2018-10-31 18:30 | 238 | 238
2018-10-31 19:00 | 250 | 250
2018-10-31 19:30 | 251 | 250
2018-10-31 20:00 | 272 | 272
2018-10-31 20:30 | 284 | 284
2018-10-31 21:00 | 309 | 309
2018-10-31 21:30 | 304 | 303
2018-10-31 22:00 | 280 | 280
2018-10-31 22:30 | 276 | 276
2018-10-31 23:00 | 258 | 258
2018-10-31 23:30 | 247 | 247
2018-11-01 | 239 | 239
2018-11-01 00:30 | 240 | 240
2018-11-01 01:00 | 228 | 227
2018-11-01 01:30 | 218 | 218
2018-11-01 02:00 | 212 | 212
2018-11-01 02:30 | 208 | 208
2018-11-01 03:00 | 208 | 207
2018-11-01 03:30 | 208 | 207
2018-11-01 04:00 | 208 | 207
2018-11-01 04:30 | 208 | 208
2018-11-01 05:00 | 208 | 208
2018-11-01 05:30 | 214 | 213
2018-11-01 06:00 | 215 | 215
2018-11-01 06:30 | 212 | 212
2018-11-01 07:00 | 194 | 194
2018-11-01 07:30 | 185 | 184
2018-11-01 08:00 | 200 | 199
2018-11-01 08:30 | 172 | 171
2018-11-01 09:00 | 151 | 151
2018-11-01 09:30 | 134 | 133
2018-11-01 10:00 | 129 | 127
2018-11-01 10:30 | 113 | 112
2018-11-01 11:00 | 106 | 104
2018-11-01 11:30 | 104 | 103
2018-11-01 12:00 | 78 | 73
2018-11-01 12:30 | 76 | 71
2018-11-01 13:00 | 94 | 91
2018-11-01 13:30 | 92 | 90
2018-11-01 14:00 | 90 | 87
2018-11-01 14:30 | 115 | 114
2018-11-01 15:00 | 102 | 100
2018-11-01 15:30 | 93 | 91
2018-11-01 16:00 | 102 | 101
2018-11-01 16:30 | 85 | 81
2018-11-01 17:00 | 103 | 102
2018-11-01 17:30 | 116 | 115
2018-11-01 18:00 | 141 | 140
2018-11-01 18:30 | 156 | 156
2018-11-01 19:00 | 165 | 164
2018-11-01 19:30 | 169 | 168
2018-11-01 20:00 | 175 | 174
2018-11-01 20:30 | 204 | 203
2018-11-01 21:00 | 221 | 221
2018-11-01 21:30 | 269 | 269
2018-11-01 22:00 | 284 | 284
2018-11-01 22:30 | 263 | 263
2018-11-01 23:00 | 252 | 252
2018-11-01 23:30 | 246 | 246
2018-11-02 | 208 | 207
2018-11-02 00:30 | 201 | 201
2018-11-02 01:00 | 190 | 190
2018-11-02 01:30 | 182 | 182
2018-11-02 02:00 | 180 | 180
2018-11-02 02:30 | 182 | 182
2018-11-02 03:00 | 175 | 175
2018-11-02 03:30 | 168 | 168
2018-11-02 04:00 | 201 | 201
2018-11-02 04:30 | 195 | 195
2018-11-02 05:00 | 175 | 174
2018-11-02 05:30 | 192 | 192
2018-11-02 06:00 | 181 | 180
2018-11-02 06:30 | 178 | 177
2018-11-02 07:00 | 164 | 163
2018-11-02 07:30 | 140 | 139
2018-11-02 08:00 | 120 | 119
2018-11-02 08:30 | 116 | 115
2018-11-02 09:00 | 117 | 116
2018-11-02 09:30 | 127 | 126
2018-11-02 10:00 | 122 | 120
2018-11-02 10:30 | 106 | 104
2018-11-02 11:00 | 82 | 77
2018-11-02 11:30 | 67 | 59
2018-11-02 12:00 | 72 | 66
2018-11-02 12:30 | 64 | 55
2018-11-02 13:00 | 62 | 55
2018-11-02 13:30 | 49 | 43
2018-11-02 14:00 | 60 | 53
2018-11-02 14:30 | 62 | 53
2018-11-02 15:00 | 32 | 28
2018-11-02 15:30 | 17 | 15
2018-11-02 16:00 | 4 | 1
2018-11-02 16:30 | 5 | 4
2018-11-02 17:00 | 31 | 26
2018-11-02 17:30 | 45 | 41
2018-11-02 18:00 | 80 | 77
2018-11-02 18:30 | 133 | 132
2018-11-02 19:00 | 111 | 109
2018-11-02 19:30 | 125 | 124
2018-11-02 20:00 | 154 | 153
2018-11-02 20:30 | 156 | 156
2018-11-02 21:00 | 161 | 160
2018-11-02 21:30 | 188 | 187
2018-11-02 22:00 | 224 | 224
2018-11-02 22:30 | 213 | 213
2018-11-02 23:00 | 203 | 203
2018-11-02 23:30 | 188 | 188
2018-11-03 | 175 | 175
2018-11-03 00:30 | 185 | 184
2018-11-03 01:00 | 175 | 175
2018-11-03 01:30 | 175 | 174
2018-11-03 02:00 | 160 | 160
2018-11-03 02:30 | 155 | 154
2018-11-03 03:00 | 154 | 154
2018-11-03 03:30 | 145 | 144
2018-11-03 04:00 | 145 | 144
2018-11-03 04:30 | 144 | 143
2018-11-03 05:00 | 140 | 139
2018-11-03 05:30 | 140 | 139
2018-11-03 06:00 | 137 | 136
2018-11-03 06:30 | 120 | 118
2018-11-03 07:00 | 95 | 92
2018-11-03 07:30 | 84 | 80
2018-11-03 08:00 | 83 | 79
2018-11-03 08:30 | 64 | 56
2018-11-03 09:00 | 56 | 47
2018-11-03 09:30 | 65 | 57
2018-11-03 10:00 | 91 | 88
2018-11-03 10:30 | 78 | 73
2018-11-03 11:00 | 79 | 74
2018-11-03 11:30 | 83 | 79
2018-11-03 12:00 | 82 | 78
2018-11-03 12:30 | 75 | 69
2018-11-03 13:00 | 75 | 69
2018-11-03 13:30 | 84 | 80
2018-11-03 14:00 | 100 | 97
2018-11-03 14:30 | 106 | 104
2018-11-03 15:00 | 110 | 108
2018-11-03 15:30 | 108 | 106
2018-11-03 16:00 | 91 | 88
2018-11-03 16:30 | 104 | 102
2018-11-03 17:00 | 129 | 128
2018-11-03 17:30 | 157 | 156
2018-11-03 18:00 | 192 | 192
2018-11-03 18:30 | 206 | 206
2018-11-03 19:00 | 225 | 225
2018-11-03 19:30 | 223 | 223
2018-11-03 20:00 | 217 | 216
2018-11-03 20:30 | 210 | 209
2018-11-03 21:00 | 218 | 217
2018-11-03 21:30 | 211 | 211
2018-11-03 22:00 | 209 | 208
2018-11-03 22:30 | 196 | 195
2018-11-03 23:00 | 192 | 192
2018-11-03 23:30 | 196 | 195
2018-11-04 | 190 | 189
2018-11-04 00:30 | 193 | 193
2018-11-04 01:00 | 186 | 185
2018-11-04 01:30 | 186 | 185
2018-11-04 02:00 | 188 | 188
2018-11-04 02:30 | 181 | 180
2018-11-04 03:00 | 175 | 175
2018-11-04 03:30 | 178 | 177
2018-11-04 04:00 | 172 | 172
2018-11-04 04:30 | 172 | 171
2018-11-04 05:00 | 174 | 174
2018-11-04 05:30 | 176 | 175
2018-11-04 06:00 | 172 | 172
2018-11-04 06:30 | 153 | 152
2018-11-04 07:00 | 123 | 121
2018-11-04 07:30 | 91 | 88
2018-11-04 08:00 | 89 | 85
2018-11-04 08:30 | 96 | 93
2018-11-04 09:00 | 96 | 93
2018-11-04 09:30 | 93 | 89
2018-11-04 10:00 | 90 | 86
2018-11-04 10:30 | 88 | 84
2018-11-04 11:00 | 70 | 63
2018-11-04 11:30 | 72 | 65
2018-11-04 12:00 | 77 | 72
2018-11-04 12:30 | 71 | 64
2018-11-04 13:00 | 75 | 69
2018-11-04 13:30 | 85 | 81
2018-11-04 14:00 | 93 | 89
2018-11-04 14:30 | 106 | 103
2018-11-04 15:00 | 111 | 109
2018-11-04 15:30 | 116 | 114
2018-11-04 16:00 | 139 | 138
2018-11-04 16:30 | 133 | 132
2018-11-04 17:00 | 156 | 155
2018-11-04 17:30 | 169 | 168
2018-11-04 18:00 | 212 | 212
2018-11-04 18:30 | 241 | 241
2018-11-04 19:00 | 250 | 249
2018-11-04 19:30 | 238 | 238
2018-11-04 20:00 | 228 | 228
2018-11-04 20:30 | 238 | 238
2018-11-04 21:00 | 237 | 237
2018-11-04 21:30 | 246 | 246
2018-11-04 22:00 | 232 | 232
2018-11-04 22:30 | 218 | 218
2018-11-04 23:00 | 201 | 200
2018-11-04 23:30 | 192 | 191
2018-11-05 | 183 | 183
2018-11-05 00:30 | 196 | 196
2018-11-05 01:00 | 185 | 185
2018-11-05 01:30 | 182 | 182
2018-11-05 02:00 | 177 | 176
2018-11-05 02:30 | 178 | 177
2018-11-05 03:00 | 171 | 171
2018-11-05 03:30 | 168 | 167
2018-11-05 04:00 | 168 | 167
2018-11-05 04:30 | 174 | 173
2018-11-05 05:00 | 180 | 179
2018-11-05 05:30 | 189 | 189
2018-11-05 06:00 | 184 | 183
2018-11-05 06:30 | 175 | 174
2018-11-05 07:00 | 151 | 150
2018-11-05 07:30 | 146 | 145
2018-11-05 08:00 | 150 | 150
2018-11-05 08:30 | 132 | 131
2018-11-05 09:00 | 133 | 132
2018-11-05 09:30 | 124 | 123
2018-11-05 10:00 | 116 | 114
2018-11-05 10:30 | 111 | 110
2018-11-05 11:00 | 114 | 112
2018-11-05 11:30 | 117 | 115
2018-11-05 12:00 | 118 | 116
2018-11-05 12:30 | 119 | 117
2018-11-05 13:00 | 124 | 123
2018-11-05 13:30 | 127 | 126
2018-11-05 14:00 | 117 | 116
2018-11-05 14:30 | 128 | 127
2018-11-05 15:00 | 129 | 128
2018-11-05 15:30 | 107 | 105
2018-11-05 16:00 | 101 | 98
2018-11-05 16:30 | 85 | 81
2018-11-05 17:00 | 105 | 102
2018-11-05 17:30 | 131 | 130
2018-11-05 18:00 | 154 | 153
2018-11-05 18:30 | 174 | 173
2018-11-05 19:00 | 181 | 181
2018-11-05 19:30 | 178 | 178
2018-11-05 20:00 | 182 | 181
2018-11-05 20:30 | 169 | 169
2018-11-05 21:00 | 186 | 185
2018-11-05 21:30 | 187 | 187
2018-11-05 22:00 | 198 | 197
2018-11-05 22:30 | 217 | 217
2018-11-05 23:00 | 208 | 207
2018-11-05 23:30 | 190 | 190
2018-11-06 | 180 | 179
2018-11-06 00:30 | 178 | 177
2018-11-06 01:00 | 128 | 127
2018-11-06 01:30 | 120 | 118
2018-11-06 02:00 | 121 | 120
2018-11-06 02:30 | 118 | 116
2018-11-06 03:00 | 111 | 110
2018-11-06 03:30 | 111 | 110
2018-11-06 04:00 | 108 | 106
2018-11-06 04:30 | 105 | 104
2018-11-06 05:00 | 112 | 111
2018-11-06 05:30 | 124 | 123
2018-11-06 06:00 | 123 | 122
2018-11-06 06:30 | 119 | 117
2018-11-06 07:00 | 89 | 86
2018-11-06 07:30 | 104 | 102
2018-11-06 08:00 | 113 | 112
2018-11-06 08:30 | 103 | 102
2018-11-06 09:00 | 92 | 90
2018-11-06 09:30 | 95 | 92
2018-11-06 10:00 | 108 | 107
2018-11-06 10:30 | 113 | 112
2018-11-06 11:00 | 104 | 103
2018-11-06 11:30 | 86 | 83
2018-11-06 12:00 | 49 | 45
2018-11-06 12:30 | 37 | 36
2018-11-06 13:00 | 39 | 37
2018-11-06 13:30 | 38 | 36
2018-11-06 14:00 | 46 | 42
2018-11-06 14:30 | 47 | 41
2018-11-06 15:00 | 10 | 9
2018-11-06 15:30 | 12 | 11
2018-11-06 16:00 | 8 | 7
2018-11-06 16:30 | 3 | 2
2018-11-06 17:00 | 12 | 10
2018-11-06 17:30 | 51 | 44
2018-11-06 18:00 | 92 | 89
2018-11-06 18:30 | 107 | 106
2018-11-06 19:00 | 120 | 119
2018-11-06 19:30 | 127 | 126
2018-11-06 20:00 | 117 | 116
2018-11-06 20:30 | 121 | 120
2018-11-06 21:00 | 133 | 132
2018-11-06 21:30 | 138 | 138
2018-11-06 22:00 | 164 | 164
2018-11-06 22:30 | 146 | 145
2018-11-06 23:00 | 171 | 171
2018-11-06 23:30 | 168 | 167
2018-11-07 | 173 | 172
2018-11-07 00:30 | 218 | 217
2018-11-07 01:00 | 204 | 203
2018-11-07 01:30 | 186 | 185
2018-11-07 02:00 | 183 | 183
2018-11-07 02:30 | 179 | 178
2018-11-07 03:00 | 174 | 173
2018-11-07 03:30 | 171 | 170
2018-11-07 04:00 | 174 | 173
2018-11-07 04:30 | 185 | 184
2018-11-07 05:00 | 187 | 186
2018-11-07 05:30 | 200 | 199
2018-11-07 06:00 | 212 | 212
2018-11-07 06:30 | 195 | 195
2018-11-07 07:00 | 150 | 149
2018-11-07 07:30 | 154 | 153
2018-11-07 08:00 | 163 | 162
2018-11-07 08:30 | 154 | 152
2018-11-07 09:00 | 119 | 116
2018-11-07 09:30 | 92 | 86
2018-11-07 10:00 | 70 | 59
2018-11-07 10:30 | 64 | 52
2018-11-07 11:00 | 58 | 49
2018-11-07 11:30 | 25 | 20
2018-11-07 12:00 | 37 | 21
2018-11-07 12:30 | 37 | 25
2018-11-07 13:00 | 25 | 17
2018-11-07 13:30 | 55 | 44
2018-11-07 14:00 | 56 | 46
2018-11-07 14:30 | 26 | 21
2018-11-07 15:00 | 66 | 55
2018-11-07 15:30 | 63 | 52
2018-11-07 16:00 | 39 | 25
2018-11-07 16:30 | 41 | 34
2018-11-07 17:00 | 63 | 55
2018-11-07 17:30 | 108 | 105
2018-11-07 18:00 | 136 | 134
2018-11-07 18:30 | 157 | 155
2018-11-07 19:00 | 164 | 162
2018-11-07 19:30 | 170 | 168
2018-11-07 20:00 | 187 | 186
2018-11-07 20:30 | 227 | 227
2018-11-07 21:00 | 230 | 229
2018-11-07 21:30 | 228 | 228
2018-11-07 22:00 | 236 | 235
2018-11-07 22:30 | 262 | 262
2018-11-07 23:00 | 254 | 254
2018-11-07 23:30 | 238 | 238
2018-11-08 | 234 | 233
2018-11-08 00:30 | 241 | 240
2018-11-08 01:00 | 232 | 232
2018-11-08 01:30 | 224 | 224
2018-11-08 02:00 | 216 | 216
2018-11-08 02:30 | 214 | 213
2018-11-08 03:00 | 215 | 215
2018-11-08 03:30 | 212 | 212
2018-11-08 04:00 | 211 | 210
2018-11-08 04:30 | 210 | 210
2018-11-08 05:00 | 209 | 209
2018-11-08 05:30 | 211 | 211
2018-11-08 06:00 | 199 | 198
2018-11-08 06:30 | 195 | 195
2018-11-08 07:00 | 171 | 170
2018-11-08 07:30 | 165 | 164
2018-11-08 08:00 | 165 | 163
2018-11-08 08:30 | 158 | 156
2018-11-08 09:00 | 159 | 157
2018-11-08 09:30 | 163 | 161
2018-11-08 10:00 | 142 | 138
2018-11-08 10:30 | 122 | 120
2018-11-08 11:00 | 117 | 115
2018-11-08 11:30 | 126 | 123
2018-11-08 12:00 | 125 | 124
2018-11-08 12:30 | 70 | 68
2018-11-08 13:00 | 69 | 60
2018-11-08 13:30 | 75 | 64
2018-11-08 14:00 | 114 | 110
2018-11-08 14:30 | 154 | 152
2018-11-08 15:00 | 159 | 157
2018-11-08 15:30 | 175 | 173
2018-11-08 16:00 | 184 | 183
2018-11-08 16:30 | 199 | 198
2018-11-08 17:00 | 227 | 227
2018-11-08 17:30 | 248 | 248
2018-11-08 18:00 | 264 | 264
2018-11-08 18:30 | 270 | 270
2018-11-08 19:00 | 276 | 276
2018-11-08 19:30 | 273 | 273
2018-11-08 20:00 | 265 | 264
2018-11-08 20:30 | 273 | 272
2018-11-08 21:00 | 278 | 278
2018-11-08 21:30 | 270 | 269
2018-11-08 22:00 | 251 | 250
2018-11-08 22:30 | 232 | 231
2018-11-08 23:00 | 219 | 219
2018-11-08 23:30 | 236 | 236
2018-11-09 | 230 | 229
2018-11-09 00:30 | 226 | 226
2018-11-09 01:00 | 222 | 222
2018-11-09 01:30 | 220 | 220
2018-11-09 02:00 | 212 | 212
2018-11-09 02:30 | 202 | 202
2018-11-09 03:00 | 201 | 200
2018-11-09 03:30 | 196 | 196
2018-11-09 04:00 | 203 | 203
2018-11-09 04:30 | 206 | 205
2018-11-09 05:00 | 211 | 210
2018-11-09 05:30 | 212 | 212
2018-11-09 06:00 | 220 | 219
2018-11-09 06:30 | 220 | 220
2018-11-09 07:00 | 214 | 213
2018-11-09 07:30 | 233 | 232
2018-11-09 08:00 | 235 | 235
2018-11-09 08:30 | 221 | 220
2018-11-09 09:00 | 210 | 209
2018-11-09 09:30 | 221 | 220
2018-11-09 10:00 | 182 | 181
2018-11-09 10:30 | 181 | 180
2018-11-09 11:00 | 164 | 162
2018-11-09 11:30 | 165 | 163
2018-11-09 12:00 | 157 | 156
2018-11-09 12:30 | 153 | 151
2018-11-09 13:00 | 147 | 144
2018-11-09 13:30 | 151 | 149
2018-11-09 14:00 | 162 | 160
2018-11-09 14:30 | 148 | 146
2018-11-09 15:00 | 133 | 130
2018-11-09 15:30 | 143 | 142
2018-11-09 16:00 | 147 | 145
2018-11-09 16:30 | 150 | 149
2018-11-09 17:00 | 181 | 180
2018-11-09 17:30 | 208 | 207
2018-11-09 18:00 | 234 | 233
2018-11-09 18:30 | 229 | 228
2018-11-09 19:00 | 240 | 240
2018-11-09 19:30 | 240 | 239
2018-11-09 20:00 | 227 | 226
2018-11-09 20:30 | 233 | 233
2018-11-09 21:00 | 255 | 255
2018-11-09 21:30 | 255 | 254
2018-11-09 22:00 | 240 | 240
2018-11-09 22:30 | 226 | 226
2018-11-09 23:00 | 214 | 214
2018-11-09 23:30 | 191 | 190
2018-11-10 | 183 | 182
2018-11-10 00:30 | 181 | 180
2018-11-10 01:00 | 188 | 188
2018-11-10 01:30 | 188 | 187
2018-11-10 02:00 | 171 | 171
2018-11-10 02:30 | 175 | 174
2018-11-10 03:00 | 188 | 187
2018-11-10 03:30 | 191 | 191
2018-11-10 04:00 | 177 | 176
2018-11-10 04:30 | 181 | 180
2018-11-10 05:00 | 180 | 180
2018-11-10 05:30 | 183 | 182
2018-11-10 06:00 | 187 | 186
2018-11-10 06:30 | 175 | 174
2018-11-10 07:00 | 154 | 153
2018-11-10 07:30 | 153 | 152
2018-11-10 08:00 | 132 | 131
2018-11-10 08:30 | 126 | 124
2018-11-10 09:00 | 111 | 109
2018-11-10 09:30 | 116 | 114
2018-11-10 10:00 | 129 | 127
2018-11-10 10:30 | 118 | 116
2018-11-10 11:00 | 116 | 114
2018-11-10 11:30 | 105 | 102
2018-11-10 12:00 | 114 | 112
2018-11-10 12:30 | 111 | 109
2018-11-10 13:00 | 107 | 104
2018-11-10 13:30 | 111 | 108
2018-11-10 14:00 | 112 | 110
2018-11-10 14:30 | 122 | 120
2018-11-10 15:00 | 127 | 126
2018-11-10 15:30 | 128 | 127
2018-11-10 16:00 | 111 | 108
2018-11-10 16:30 | 142 | 140
2018-11-10 17:00 | 156 | 155
2018-11-10 17:30 | 197 | 196
2018-11-10 18:00 | 215 | 215
2018-11-10 18:30 | 215 | 215
2018-11-10 19:00 | 231 | 231
2018-11-10 19:30 | 237 | 236
2018-11-10 20:00 | 236 | 235
2018-11-10 20:30 | 241 | 240
2018-11-10 21:00 | 254 | 253
2018-11-10 21:30 | 241 | 241
2018-11-10 22:00 | 232 | 232
2018-11-10 22:30 | 218 | 217
2018-11-10 23:00 | 199 | 199
2018-11-10 23:30 | 203 | 202
2018-11-11 | 189 | 189
2018-11-11 00:30 | 189 | 189
2018-11-11 01:00 | 177 | 177
2018-11-11 01:30 | 176 | 176
2018-11-11 02:00 | 178 | 177
2018-11-11 02:30 | 176 | 176
2018-11-11 03:00 | 186 | 185
2018-11-11 03:30 | 190 | 189
2018-11-11 04:00 | 189 | 188
2018-11-11 04:30 | 195 | 195
2018-11-11 05:00 | 195 | 195
2018-11-11 05:30 | 192 | 192
2018-11-11 06:00 | 181 | 180
2018-11-11 06:30 | 165 | 165
2018-11-11 07:00 | 150 | 149
2018-11-11 07:30 | 116 | 116
2018-11-11 08:00 | 127 | 126
2018-11-11 08:30 | 124 | 124
2018-11-11 09:00 | 95 | 94
2018-11-11 09:30 | 88 | 86
2018-11-11 10:00 | 86 | 84
2018-11-11 10:30 | 74 | 72
2018-11-11 11:00 | 68 | 65
2018-11-11 11:30 | 83 | 81
2018-11-11 12:00 | 98 | 97
2018-11-11 12:30 | 89 | 88
2018-11-11 13:00 | 84 | 83
2018-11-11 13:30 | 79 | 76
2018-11-11 14:00 | 92 | 91
2018-11-11 14:30 | 58 | 53
2018-11-11 15:00 | 56 | 50
2018-11-11 15:30 | 68 | 64
2018-11-11 16:00 | 69 | 66
2018-11-11 16:30 | 75 | 72
2018-11-11 17:00 | 110 | 109
2018-11-11 17:30 | 148 | 147
2018-11-11 18:00 | 158 | 157
2018-11-11 18:30 | 172 | 171
2018-11-11 19:00 | 168 | 168
2018-11-11 19:30 | 193 | 193
2018-11-11 20:00 | 190 | 190
2018-11-11 20:30 | 195 | 195
2018-11-11 21:00 | 211 | 210
2018-11-11 21:30 | 216 | 216
2018-11-11 22:00 | 206 | 206
2018-11-11 22:30 | 191 | 191
2018-11-11 23:00 | 178 | 178
2018-11-11 23:30 | 171 | 171
2018-11-12 | 162 | 161
2018-11-12 00:30 | 169 | 169
2018-11-12 01:00 | 154 | 153
2018-11-12 01:30 | 148 | 148
2018-11-12 02:00 | 149 | 149
2018-11-12 02:30 | 140 | 139
2018-11-12 03:00 | 137 | 136
2018-11-12 03:30 | 135 | 134
2018-11-12 04:00 | 134 | 133
2018-11-12 04:30 | 137 | 136
2018-11-12 05:00 | 151 | 151
2018-11-12 05:30 | 162 | 162
2018-11-12 06:00 | 177 | 177
2018-11-12 06:30 | 172 | 171
2018-11-12 07:00 | 143 | 143
2018-11-12 07:30 | 142 | 141
2018-11-12 08:00 | 130 | 129
2018-11-12 08:30 | 117 | 116
2018-11-12 09:00 | 114 | 113
2018-11-12 09:30 | 126 | 125
2018-11-12 10:00 | 115 | 114
2018-11-12 10:30 | 110 | 108
2018-11-12 11:00 | 104 | 102
2018-11-12 11:30 | 104 | 102
2018-11-12 12:00 | 112 | 111
2018-11-12 12:30 | 110 | 108
2018-11-12 13:00 | 111 | 109
2018-11-12 13:30 | 106 | 104
2018-11-12 14:00 | 112 | 110
2018-11-12 14:30 | 127 | 126
2018-11-12 15:00 | 120 | 118
2018-11-12 15:30 | 127 | 126
2018-11-12 16:00 | 102 | 99
2018-11-12 16:30 | 82 | 78
2018-11-12 17:00 | 94 | 91
2018-11-12 17:30 | 104 | 102
2018-11-12 18:00 | 143 | 142
2018-11-12 18:30 | 169 | 168
2018-11-12 19:00 | 186 | 186
2018-11-12 19:30 | 188 | 188
2018-11-12 20:00 | 178 | 178
2018-11-12 20:30 | 192 | 192
2018-11-12 21:00 | 206 | 206
2018-11-12 21:30 | 227 | 227
2018-11-12 22:00 | 217 | 216
2018-11-12 22:30 | 201 | 200
2018-11-12 23:00 | 188 | 188
2018-11-12 23:30 | 175 | 175
2018-11-13 | 169 | 168
2018-11-13 00:30 | 173 | 172
2018-11-13 01:00 | 164 | 163
2018-11-13 01:30 | 157 | 156
2018-11-13 02:00 | 152 | 152
2018-11-13 02:30 | 149 | 149
2018-11-13 03:00 | 152 | 151
2018-11-13 03:30 | 154 | 153
2018-11-13 04:00 | 150 | 149
2018-11-13 04:30 | 152 | 152
2018-11-13 05:00 | 161 | 160
2018-11-13 05:30 | 164 | 163
2018-11-13 06:00 | 159 | 158
2018-11-13 06:30 | 148 | 147
2018-11-13 07:00 | 121 | 120
2018-11-13 07:30 | 105 | 103
2018-11-13 08:00 | 98 | 96
2018-11-13 08:30 | 89 | 85
2018-11-13 09:00 | 86 | 82
2018-11-13 09:30 | 80 | 76
2018-11-13 10:00 | 77 | 72
2018-11-13 10:30 | 56 | 48
2018-11-13 11:00 | 59 | 52
2018-11-13 11:30 | 68 | 61
2018-11-13 12:00 | 69 | 63
2018-11-13 12:30 | 72 | 67
2018-11-13 13:00 | 80 | 75
2018-11-13 13:30 | 81 | 77
2018-11-13 14:00 | 89 | 86
2018-11-13 14:30 | 104 | 102
2018-11-13 15:00 | 112 | 110
2018-11-13 15:30 | 122 | 120
2018-11-13 16:00 | 122 | 120
2018-11-13 16:30 | 137 | 136
2018-11-13 17:00 | 162 | 162
2018-11-13 17:30 | 182 | 181
2018-11-13 18:00 | 223 | 222
2018-11-13 18:30 | 239 | 239
2018-11-13 19:00 | 237 | 237
2018-11-13 19:30 | 232 | 232
2018-11-13 20:00 | 223 | 223
2018-11-13 20:30 | 220 | 219
2018-11-13 21:00 | 233 | 233
2018-11-13 21:30 | 248 | 248
2018-11-13 22:00 | 238 | 238
2018-11-13 22:30 | 222 | 221
2018-11-13 23:00 | 207 | 207
2018-11-13 23:30 | 195 | 194
2018-11-14 | 189 | 188
2018-11-14 00:30 | 193 | 193
2018-11-14 01:00 | 197 | 196
2018-11-14 01:30 | 195 | 195
2018-11-14 02:00 | 179 | 178
2018-11-14 02:30 | 183 | 182
2018-11-14 03:00 | 187 | 187
2018-11-14 03:30 | 181 | 181
2018-11-14 04:00 | 180 | 179
2018-11-14 04:30 | 183 | 182
2018-11-14 05:00 | 186 | 185
2018-11-14 05:30 | 189 | 189
2018-11-14 06:00 | 169 | 169
2018-11-14 06:30 | 147 | 146
2018-11-14 07:00 | 123 | 122
2018-11-14 07:30 | 126 | 126
2018-11-14 08:00 | 124 | 123
2018-11-14 08:30 | 111 | 110
2018-11-14 09:00 | 113 | 112
2018-11-14 09:30 | 104 | 103
2018-11-14 10:00 | 107 | 106
2018-11-14 10:30 | 94 | 93
2018-11-14 11:00 | 93 | 91
2018-11-14 11:30 | 104 | 103
2018-11-14 12:00 | 106 | 105
2018-11-14 12:30 | 111 | 110
2018-11-14 13:00 | 110 | 109
2018-11-14 13:30 | 114 | 113
2018-11-14 14:00 | 124 | 123
2018-11-14 14:30 | 142 | 141
2018-11-14 15:00 | 154 | 153
2018-11-14 15:30 | 131 | 130
2018-11-14 16:00 | 101 | 99
2018-11-14 16:30 | 70 | 65
2018-11-14 17:00 | 73 | 69
2018-11-14 17:30 | 90 | 89
2018-11-14 18:00 | 133 | 132
2018-11-14 18:30 | 137 | 136
2018-11-14 19:00 | 138 | 137
2018-11-14 19:30 | 158 | 158
2018-11-14 20:00 | 148 | 147
2018-11-14 20:30 | 151 | 150
2018-11-14 21:00 | 175 | 174
2018-11-14 21:30 | 175 | 174
2018-11-14 22:00 | 166 | 165
2018-11-14 22:30 | 180 | 180
2018-11-14 23:00 | 202 | 201
2018-11-14 23:30 | 198 | 197
2018-11-15 | 189 | 189
2018-11-15 00:30 | 189 | 188
2018-11-15 01:00 | 176 | 176
2018-11-15 01:30 | 168 | 168
2018-11-15 02:00 | 165 | 164
2018-11-15 02:30 | 162 | 162
2018-11-15 03:00 | 160 | 159
2018-11-15 03:30 | 162 | 161
2018-11-15 04:00 | 175 | 175
2018-11-15 04:30 | 174 | 174
2018-11-15 05:00 | 173 | 173
2018-11-15 05:30 | 180 | 179
2018-11-15 06:00 | 182 | 182
2018-11-15 06:30 | 174 | 173
2018-11-15 07:00 | 155 | 154
2018-11-15 07:30 | 157 | 156
2018-11-15 08:00 | 147 | 146
2018-11-15 08:30 | 135 | 134
2018-11-15 09:00 | 132 | 131
2018-11-15 09:30 | 132 | 130
2018-11-15 10:00 | 117 | 115
2018-11-15 10:30 | 102 | 99
2018-11-15 11:00 | 113 | 112
2018-11-15 11:30 | 112 | 111
2018-11-15 12:00 | 111 | 109
2018-11-15 12:30 | 103 | 102
2018-11-15 13:00 | 102 | 100
2018-11-15 13:30 | 99 | 98
2018-11-15 14:00 | 103 | 101
2018-11-15 14:30 | 110 | 109
2018-11-15 15:00 | 122 | 121
2018-11-15 15:30 | 127 | 126
2018-11-15 16:00 | 129 | 128
2018-11-15 16:30 | 131 | 130
2018-11-15 17:00 | 155 | 154
2018-11-15 17:30 | 185 | 184
2018-11-15 18:00 | 226 | 225
2018-11-15 18:30 | 249 | 249
2018-11-15 19:00 | 269 | 269
2018-11-15 19:30 | 287 | 286
2018-11-15 20:00 | 278 | 278
2018-11-15 20:30 | 266 | 266
2018-11-15 21:00 | 280 | 279
2018-11-15 21:30 | 276 | 276
2018-11-15 22:00 | 259 | 259
2018-11-15 22:30 | 244 | 243
2018-11-15 23:00 | 228 | 228
2018-11-15 23:30 | 216 | 215
2018-11-16 | 207 | 207
2018-11-16 00:30 | 214 | 214
2018-11-16 01:00 | 190 | 190
2018-11-16 01:30 | 177 | 177
2018-11-16 02:00 | 179 | 178
2018-11-16 02:30 | 173 | 173
2018-11-16 03:00 | 173 | 172
2018-11-16 03:30 | 171 | 170
2018-11-16 04:00 | 172 | 171
2018-11-16 04:30 | 174 | 174
2018-11-16 05:00 | 169 | 169
2018-11-16 05:30 | 175 | 174
2018-11-16 06:00 | 171 | 170
2018-11-16 06:30 | 161 | 160
2018-11-16 07:00 | 144 | 143
2018-11-16 07:30 | 128 | 127
2018-11-16 08:00 | 116 | 115
2018-11-16 08:30 | 120 | 119
2018-11-16 09:00 | 121 | 119
2018-11-16 09:30 | 102 | 98
2018-11-16 10:00 | 58 | 52
2018-11-16 10:30 | 66 | 58
2018-11-16 11:00 | 67 | 59
2018-11-16 11:30 | 68 | 60
2018-11-16 12:00 | 67 | 58
2018-11-16 12:30 | 72 | 63
2018-11-16 13:00 | 77 | 70
2018-11-16 13:30 | 76 | 71
2018-11-16 14:00 | 75 | 69
2018-11-16 14:30 | 79 | 74
2018-11-16 15:00 | 88 | 84
2018-11-16 15:30 | 99 | 96
2018-11-16 16:00 | 98 | 95
2018-11-16 16:30 | 101 | 99
2018-11-16 17:00 | 123 | 122
2018-11-16 17:30 | 157 | 156
2018-11-16 18:00 | 199 | 199
2018-11-16 18:30 | 236 | 235
2018-11-16 19:00 | 248 | 247
2018-11-16 19:30 | 266 | 265
2018-11-16 20:00 | 252 | 252
2018-11-16 20:30 | 238 | 237
2018-11-16 21:00 | 242 | 241
2018-11-16 21:30 | 240 | 239
2018-11-16 22:00 | 223 | 222
2018-11-16 22:30 | 210 | 210
2018-11-16 23:00 | 196 | 195
2018-11-16 23:30 | 188 | 188
2018-11-17 | 185 | 185
2018-11-17 00:30 | 189 | 189
2018-11-17 01:00 | 179 | 178
2018-11-17 01:30 | 168 | 167
2018-11-17 02:00 | 156 | 156
2018-11-17 02:30 | 154 | 153
2018-11-17 03:00 | 150 | 149
2018-11-17 03:30 | 147 | 146
2018-11-17 04:00 | 146 | 145
2018-11-17 04:30 | 156 | 156
2018-11-17 05:00 | 170 | 169
2018-11-17 05:30 | 184 | 183
2018-11-17 06:00 | 191 | 190
2018-11-17 06:30 | 166 | 165
2018-11-17 07:00 | 120 | 119
2018-11-17 07:30 | 95 | 92
2018-11-17 08:00 | 76 | 72
2018-11-17 08:30 | 96 | 93
2018-11-17 09:00 | 87 | 84
2018-11-17 09:30 | 77 | 72
2018-11-17 10:00 | 62 | 53
2018-11-17 10:30 | 42 | 39
2018-11-17 11:00 | 50 | 45
2018-11-17 11:30 | 55 | 47
2018-11-17 12:00 | 45 | 39
2018-11-17 12:30 | 34 | 32
2018-11-17 13:00 | 29 | 22
2018-11-17 13:30 | 19 | 16
2018-11-17 14:00 | 40 | 35
2018-11-17 14:30 | 61 | 54
2018-11-17 15:00 | 73 | 68
2018-11-17 15:30 | 90 | 88
2018-11-17 16:00 | 114 | 113
2018-11-17 16:30 | 118 | 117
2018-11-17 17:00 | 146 | 145
2018-11-17 17:30 | 191 | 191
2018-11-17 18:00 | 239 | 238
2018-11-17 18:30 | 262 | 262
2018-11-17 19:00 | 273 | 273
2018-11-17 19:30 | 280 | 279
2018-11-17 20:00 | 274 | 274
2018-11-17 20:30 | 264 | 263
2018-11-17 21:00 | 269 | 268
2018-11-17 21:30 | 274 | 274
2018-11-17 22:00 | 271 | 270
2018-11-17 22:30 | 256 | 255
2018-11-17 23:00 | 247 | 247
2018-11-17 23:30 | 236 | 236
2018-11-18 | 229 | 229
2018-11-18 00:30 | 232 | 232
2018-11-18 01:00 | 222 | 221
2018-11-18 01:30 | 224 | 224
2018-11-18 02:00 | 219 | 219
2018-11-18 02:30 | 207 | 206
2018-11-18 03:00 | 200 | 199
2018-11-18 03:30 | 199 | 198
2018-11-18 04:00 | 198 | 197
2018-11-18 04:30 | 197 | 197
2018-11-18 05:00 | 200 | 199
2018-11-18 05:30 | 200 | 199
2018-11-18 06:00 | 192 | 191
2018-11-18 06:30 | 165 | 165
2018-11-18 07:00 | 139 | 139
2018-11-18 07:30 | 116 | 115
2018-11-18 08:00 | 102 | 100
2018-11-18 08:30 | 96 | 94
2018-11-18 09:00 | 96 | 94
2018-11-18 09:30 | 90 | 88
2018-11-18 10:00 | 85 | 83
2018-11-18 10:30 | 60 | 54
2018-11-18 11:00 | 53 | 47
2018-11-18 11:30 | 58 | 52
2018-11-18 12:00 | 64 | 57
2018-11-18 12:30 | 54 | 48
2018-11-18 13:00 | 70 | 66
2018-11-18 13:30 | 84 | 82
2018-11-18 14:00 | 84 | 82
2018-11-18 14:30 | 88 | 86
2018-11-18 15:00 | 83 | 81
2018-11-18 15:30 | 96 | 95
2018-11-18 16:00 | 92 | 89
2018-11-18 16:30 | 113 | 111
2018-11-18 17:00 | 167 | 166
2018-11-18 17:30 | 209 | 209
2018-11-18 18:00 | 246 | 245
2018-11-18 18:30 | 257 | 257
2018-11-18 19:00 | 279 | 279
2018-11-18 19:30 | 283 | 283
2018-11-18 20:00 | 279 | 279
2018-11-18 20:30 | 274 | 274
2018-11-18 21:00 | 282 | 281
2018-11-18 21:30 | 275 | 275
2018-11-18 22:00 | 261 | 261
2018-11-18 22:30 | 246 | 245
2018-11-18 23:00 | 223 | 222
2018-11-18 23:30 | 207 | 206
2018-11-19 | 199 | 198
2018-11-19 00:30 | 199 | 198
2018-11-19 01:00 | 192 | 191
2018-11-19 01:30 | 178 | 177
2018-11-19 02:00 | 172 | 171
2018-11-19 02:30 | 165 | 164
2018-11-19 03:00 | 166 | 166
2018-11-19 03:30 | 165 | 164
2018-11-19 04:00 | 159 | 158
2018-11-19 04:30 | 155 | 155
2018-11-19 05:00 | 157 | 156
2018-11-19 05:30 | 160 | 159
2018-11-19 06:00 | 159 | 158
2018-11-19 06:30 | 159 | 158
2018-11-19 07:00 | 155 | 154
2018-11-19 07:30 | 153 | 152
2018-11-19 08:00 | 192 | 191
2018-11-19 08:30 | 164 | 163
2018-11-19 09:00 | 151 | 150
2018-11-19 09:30 | 162 | 162
2018-11-19 10:00 | 126 | 125
2018-11-19 10:30 | 133 | 132
2018-11-19 11:00 | 112 | 111
2018-11-19 11:30 | 142 | 142
2018-11-19 12:00 | 113 | 112
2018-11-19 12:30 | 112 | 111
2018-11-19 13:00 | 119 | 119
2018-11-19 13:30 | 128 | 128
2018-11-19 14:00 | 134 | 133
2018-11-19 14:30 | 158 | 157
2018-11-19 15:00 | 178 | 177
2018-11-19 15:30 | 172 | 172
2018-11-19 16:00 | 162 | 161
2018-11-19 16:30 | 154 | 154
2018-11-19 17:00 | 145 | 144
2018-11-19 17:30 | 133 | 133
2018-11-19 18:00 | 152 | 151
2018-11-19 18:30 | 170 | 170
2018-11-19 19:00 | 183 | 182
2018-11-19 19:30 | 208 | 207
2018-11-19 20:00 | 235 | 234
2018-11-19 20:30 | 234 | 234
2018-11-19 21:00 | 248 | 247
2018-11-19 21:30 | 290 | 289
2018-11-19 22:00 | 281 | 280
2018-11-19 22:30 | 257 | 257
2018-11-19 23:00 | 248 | 247
2018-11-19 23:30 | 234 | 233
2018-11-20 | 221 | 220
2018-11-20 00:30 | 223 | 223
2018-11-20 01:00 | 207 | 206
2018-11-20 01:30 | 195 | 194
2018-11-20 02:00 | 189 | 188
2018-11-20 02:30 | 193 | 192
2018-11-20 03:00 | 189 | 188
2018-11-20 03:30 | 181 | 180
2018-11-20 04:00 | 177 | 176
2018-11-20 04:30 | 184 | 183
2018-11-20 05:00 | 184 | 183
2018-11-20 05:30 | 195 | 195
2018-11-20 06:00 | 205 | 204
2018-11-20 06:30 | 204 | 203
2018-11-20 07:00 | 171 | 170
2018-11-20 07:30 | 186 | 185
2018-11-20 08:00 | 173 | 173
2018-11-20 08:30 | 149 | 148
2018-11-20 09:00 | 167 | 167
2018-11-20 09:30 | 191 | 190
2018-11-20 10:00 | 192 | 191
2018-11-20 10:30 | 164 | 163
2018-11-20 11:00 | 163 | 162
2018-11-20 11:30 | 166 | 165
2018-11-20 12:00 | 163 | 163
2018-11-20 12:30 | 159 | 158
2018-11-20 13:00 | 163 | 162
2018-11-20 13:30 | 166 | 165
2018-11-20 14:00 | 176 | 175
2018-11-20 14:30 | 157 | 156
2018-11-20 15:00 | 162 | 162
2018-11-20 15:30 | 166 | 166
2018-11-20 16:00 | 164 | 163
2018-11-20 16:30 | 158 | 158
2018-11-20 17:00 | 182 | 182
2018-11-20 17:30 | 209 | 208
2018-11-20 18:00 | 234 | 233
2018-11-20 18:30 | 256 | 255
2018-11-20 19:00 | 249 | 248
2018-11-20 19:30 | 276 | 276
2018-11-20 20:00 | 281 | 280
2018-11-20 20:30 | 273 | 272
2018-11-20 21:00 | 277 | 276
2018-11-20 21:30 | 279 | 278
2018-11-20 22:00 | 279 | 278
2018-11-20 22:30 | 265 | 264
2018-11-20 23:00 | 251 | 250
2018-11-20 23:30 | 241 | 240
2018-11-21 | 230 | 229
2018-11-21 00:30 | 244 | 243
2018-11-21 01:00 | 232 | 231
2018-11-21 01:30 | 230 | 229
2018-11-21 02:00 | 227 | 226
2018-11-21 02:30 | 224 | 223
2018-11-21 03:00 | 220 | 219
2018-11-21 03:30 | 215 | 214
2018-11-21 04:00 | 217 | 216
2018-11-21 04:30 | 220 | 219
2018-11-21 05:00 | 225 | 224
2018-11-21 05:30 | 235 | 234
2018-11-21 06:00 | 234 | 233
2018-11-21 06:30 | 229 | 228
2018-11-21 07:00 | 213 | 212
2018-11-21 07:30 | 190 | 189
2018-11-21 08:00 | 176 | 175
2018-11-21 08:30 | 178 | 178
2018-11-21 09:00 | 182 | 181
2018-11-21 09:30 | 167 | 167
2018-11-21 10:00 | 155 | 154
2018-11-21 10:30 | 141 | 141
2018-11-21 11:00 | 134 | 133
2018-11-21 11:30 | 133 | 132
2018-11-21 12:00 | 132 | 131
2018-11-21 12:30 | 135 | 135
2018-11-21 13:00 | 134 | 133
2018-11-21 13:30 | 129 | 129
2018-11-21 14:00 | 139 | 138
2018-11-21 14:30 | 137 | 137
2018-11-21 15:00 | 126 | 125
2018-11-21 15:30 | 91 | 89
2018-11-21 16:00 | 109 | 108
2018-11-21 16:30 | 116 | 115
2018-11-21 17:00 | 112 | 111
2018-11-21 17:30 | 138 | 137
2018-11-21 18:00 | 166 | 166
2018-11-21 18:30 | 180 | 180
2018-11-21 19:00 | 177 | 176
2018-11-21 19:30 | 211 | 210
2018-11-21 20:00 | 216 | 215
2018-11-21 20:30 | 225 | 224
2018-11-21 21:00 | 248 | 247
2018-11-21 21:30 | 261 | 260
2018-11-21 22:00 | 251 | 250
2018-11-21 22:30 | 253 | 252
2018-11-21 23:00 | 245 | 244
2018-11-21 23:30 | 268 | 267
2018-11-22 | 266 | 265
2018-11-22 00:30 | 268 | 267
2018-11-22 01:00 | 256 | 255
2018-11-22 01:30 | 246 | 245
2018-11-22 02:00 | 240 | 239
2018-11-22 02:30 | 237 | 236
2018-11-22 03:00 | 238 | 237
2018-11-22 03:30 | 240 | 239
2018-11-22 04:00 | 239 | 238
2018-11-22 04:30 | 239 | 238
2018-11-22 05:00 | 242 | 241
2018-11-22 05:30 | 249 | 249
2018-11-22 06:00 | 254 | 253
2018-11-22 06:30 | 263 | 262
2018-11-22 07:00 | 263 | 262
2018-11-22 07:30 | 246 | 246
2018-11-22 08:00 | 232 | 231
2018-11-22 08:30 | 215 | 215
2018-11-22 09:00 | 168 | 167
2018-11-22 09:30 | 187 | 187
2018-11-22 10:00 | 187 | 187
2018-11-22 10:30 | 181 | 180
2018-11-22 11:00 | 170 | 170
2018-11-22 11:30 | 170 | 170
2018-11-22 12:00 | 176 | 176
2018-11-22 12:30 | 191 | 190
2018-11-22 13:00 | 227 | 226
2018-11-22 13:30 | 196 | 195
2018-11-22 14:00 | 205 | 204
2018-11-22 14:30 | 209 | 208
2018-11-22 15:00 | 202 | 201
2018-11-22 15:30 | 219 | 219
2018-11-22 16:00 | 242 | 241
2018-11-22 16:30 | 256 | 254
2018-11-22 17:00 | 243 | 241
2018-11-22 17:30 | 206 | 203
2018-11-22 18:00 | 207 | 205
2018-11-22 18:30 | 204 | 202
2018-11-22 19:00 | 198 | 197
2018-11-22 19:30 | 206 | 204
2018-11-22 20:00 | 221 | 219
2018-11-22 20:30 | 212 | 210
2018-11-22 21:00 | 238 | 236
2018-11-22 21:30 | 250 | 248
2018-11-22 22:00 | 267 | 265
2018-11-22 22:30 | 272 | 271
2018-11-22 23:00 | 294 | 293
2018-11-22 23:30 | 291 | 288
2018-11-23 | 284 | 281
2018-11-23 00:30 | 283 | 281
2018-11-23 01:00 | 270 | 267
2018-11-23 01:30 | 261 | 259
2018-11-23 02:00 | 259 | 257
2018-11-23 02:30 | 258 | 257
2018-11-23 03:00 | 252 | 251
2018-11-23 03:30 | 251 | 249
2018-11-23 04:00 | 245 | 243
2018-11-23 04:30 | 244 | 242
2018-11-23 05:00 | 248 | 247
2018-11-23 05:30 | 253 | 251
2018-11-23 06:00 | 254 | 252
2018-11-23 06:30 | 262 | 261
2018-11-23 07:00 | 263 | 262
2018-11-23 07:30 | 254 | 253
2018-11-23 08:00 | 250 | 249
2018-11-23 08:30 | 252 | 250
2018-11-23 09:00 | 229 | 228
2018-11-23 09:30 | 225 | 224
2018-11-23 10:00 | 171 | 170
2018-11-23 10:30 | 169 | 167
2018-11-23 11:00 | 157 | 155
2018-11-23 11:30 | 116 | 114
2018-11-23 12:00 | 116 | 115
2018-11-23 12:30 | 112 | 111
2018-11-23 13:00 | 114 | 113
2018-11-23 13:30 | 160 | 159
2018-11-23 14:00 | 177 | 176
2018-11-23 14:30 | 188 | 188
2018-11-23 15:00 | 195 | 195
2018-11-23 15:30 | 215 | 215
2018-11-23 16:00 | 206 | 205
2018-11-23 16:30 | 208 | 207
2018-11-23 17:00 | 231 | 230
2018-11-23 17:30 | 239 | 238
2018-11-23 18:00 | 281 | 280
2018-11-23 18:30 | 301 | 299
2018-11-23 19:00 | 320 | 318
2018-11-23 19:30 | 316 | 313
2018-11-23 20:00 | 316 | 314
2018-11-23 20:30 | 323 | 321
2018-11-23 21:00 | 337 | 335
2018-11-23 21:30 | 340 | 338
2018-11-23 22:00 | 328 | 326
2018-11-23 22:30 | 317 | 315
2018-11-23 23:00 | 302 | 301
2018-11-23 23:30 | 290 | 289
2018-11-24 | 279 | 278
2018-11-24 00:30 | 279 | 278
2018-11-24 01:00 | 267 | 266
2018-11-24 01:30 | 259 | 258
2018-11-24 02:00 | 253 | 252
2018-11-24 02:30 | 250 | 249
2018-11-24 03:00 | 249 | 247
2018-11-24 03:30 | 247 | 245
2018-11-24 04:00 | 245 | 244
2018-11-24 04:30 | 245 | 244
2018-11-24 05:00 | 242 | 241
2018-11-24 05:30 | 242 | 241
2018-11-24 06:00 | 237 | 235
2018-11-24 06:30 | 221 | 220
2018-11-24 07:00 | 197 | 196
2018-11-24 07:30 | 170 | 169
2018-11-24 08:00 | 151 | 150
2018-11-24 08:30 | 149 | 147
2018-11-24 09:00 | 155 | 154
2018-11-24 09:30 | 155 | 154
2018-11-24 10:00 | 137 | 136
2018-11-24 10:30 | 129 | 128
2018-11-24 11:00 | 130 | 129
2018-11-24 11:30 | 126 | 125
2018-11-24 12:00 | 137 | 136
2018-11-24 12:30 | 147 | 146
2018-11-24 13:00 | 154 | 153
2018-11-24 13:30 | 156 | 155
2018-11-24 14:00 | 158 | 157
2018-11-24 14:30 | 165 | 164
2018-11-24 15:00 | 163 | 162
2018-11-24 15:30 | 163 | 162
2018-11-24 16:00 | 181 | 180
2018-11-24 16:30 | 220 | 220
2018-11-24 17:00 | 259 | 258
2018-11-24 17:30 | 283 | 282
2018-11-24 18:00 | 323 | 322
2018-11-24 18:30 | 350 | 348
2018-11-24 19:00 | 362 | 361
2018-11-24 19:30 | 374 | 373
2018-11-24 20:00 | 368 | 367
2018-11-24 20:30 | 351 | 349
2018-11-24 21:00 | 328 | 326
2018-11-24 21:30 | 318 | 316
2018-11-24 22:00 | 306 | 304
2018-11-24 22:30 | 302 | 301
2018-11-24 23:00 | 302 | 300
2018-11-24 23:30 | 292 | 290
2018-11-25 | 284 | 282
2018-11-25 00:30 | 275 | 273
2018-11-25 01:00 | 253 | 251
2018-11-25 01:30 | 245 | 243
2018-11-25 02:00 | 241 | 239
2018-11-25 02:30 | 236 | 234
2018-11-25 03:00 | 234 | 233
2018-11-25 03:30 | 230 | 228
2018-11-25 04:00 | 226 | 225
2018-11-25 04:30 | 242 | 241
2018-11-25 05:00 | 244 | 242
2018-11-25 05:30 | 237 | 235
2018-11-25 06:00 | 223 | 222
2018-11-25 06:30 | 204 | 202
2018-11-25 07:00 | 177 | 175
2018-11-25 07:30 | 151 | 149
2018-11-25 08:00 | 141 | 139
2018-11-25 08:30 | 134 | 132
2018-11-25 09:00 | 115 | 114
2018-11-25 09:30 | 115 | 114
2018-11-25 10:00 | 120 | 119
2018-11-25 10:30 | 124 | 123
2018-11-25 11:00 | 135 | 133
2018-11-25 11:30 | 139 | 138
2018-11-25 12:00 | 140 | 139
2018-11-25 12:30 | 145 | 144
2018-11-25 13:00 | 155 | 154
2018-11-25 13:30 | 159 | 158
2018-11-25 14:00 | 175 | 175
2018-11-25 14:30 | 180 | 179
2018-11-25 15:00 | 197 | 197
2018-11-25 15:30 | 217 | 216
2018-11-25 16:00 | 229 | 228
2018-11-25 16:30 | 235 | 234
2018-11-25 17:00 | 253 | 252
2018-11-25 17:30 | 300 | 298
2018-11-25 18:00 | 338 | 337
2018-11-25 18:30 | 348 | 347
2018-11-25 19:00 | 365 | 362
2018-11-25 19:30 | 383 | 380
2018-11-25 20:00 | 393 | 391
2018-11-25 20:30 | 406 | 405
2018-11-25 21:00 | 399 | 398
2018-11-25 21:30 | 383 | 382
2018-11-25 22:00 | 363 | 361
2018-11-25 22:30 | 338 | 336
2018-11-25 23:00 | 323 | 321
2018-11-25 23:30 | 308 | 306
2018-11-26 | 296 | 294
2018-11-26 00:30 | 288 | 286
2018-11-26 01:00 | 279 | 277
2018-11-26 01:30 | 269 | 267
2018-11-26 02:00 | 263 | 261
2018-11-26 02:30 | 248 | 246
2018-11-26 03:00 | 230 | 228
2018-11-26 03:30 | 220 | 217
2018-11-26 04:00 | 209 | 207
2018-11-26 04:30 | 219 | 216
2018-11-26 05:00 | 222 | 220
2018-11-26 05:30 | 225 | 223
2018-11-26 06:00 | 225 | 223
2018-11-26 06:30 | 221 | 220
2018-11-26 07:00 | 194 | 193
2018-11-26 07:30 | 178 | 177
2018-11-26 08:00 | 157 | 155
2018-11-26 08:30 | 165 | 164
2018-11-26 09:00 | 162 | 161
2018-11-26 09:30 | 158 | 157
2018-11-26 10:00 | 148 | 147
2018-11-26 10:30 | 152 | 151
2018-11-26 11:00 | 170 | 169
2018-11-26 11:30 | 187 | 186
2018-11-26 12:00 | 192 | 190
2018-11-26 12:30 | 202 | 201
2018-11-26 13:00 | 224 | 223
2018-11-26 13:30 | 227 | 225
2018-11-26 14:00 | 242 | 241
2018-11-26 14:30 | 264 | 263
2018-11-26 15:00 | 271 | 270
2018-11-26 15:30 | 277 | 276
2018-11-26 16:00 | 257 | 255
2018-11-26 16:30 | 202 | 200
2018-11-26 17:00 | 227 | 225
2018-11-26 17:30 | 250 | 248
2018-11-26 18:00 | 261 | 259
2018-11-26 18:30 | 290 | 288
2018-11-26 19:00 | 294 | 292
2018-11-26 19:30 | 307 | 305
2018-11-26 20:00 | 286 | 284
2018-11-26 20:30 | 306 | 304
2018-11-26 21:00 | 323 | 321
2018-11-26 21:30 | 366 | 366
2018-11-26 22:00 | 390 | 389
2018-11-26 22:30 | 368 | 367
2018-11-26 23:00 | 330 | 328
2018-11-26 23:30 | 313 | 311
2018-11-27 | 301 | 299
2018-11-27 00:30 | 288 | 286
2018-11-27 01:00 | 274 | 272
2018-11-27 01:30 | 266 | 264
2018-11-27 02:00 | 264 | 262
2018-11-27 02:30 | 261 | 259
2018-11-27 03:00 | 249 | 247
2018-11-27 03:30 | 240 | 237
2018-11-27 04:00 | 230 | 227
2018-11-27 04:30 | 233 | 230
2018-11-27 05:00 | 236 | 233
2018-11-27 05:30 | 248 | 246
2018-11-27 06:00 | 250 | 248
2018-11-27 06:30 | 248 | 245
2018-11-27 07:00 | 239 | 237
2018-11-27 07:30 | 224 | 223
2018-11-27 08:00 | 252 | 250
2018-11-27 08:30 | 246 | 244
2018-11-27 09:00 | 246 | 245
2018-11-27 09:30 | 240 | 238
2018-11-27 10:00 | 237 | 236
2018-11-27 10:30 | 225 | 222
2018-11-27 11:00 | 224 | 221
2018-11-27 11:30 | 227 | 224
2018-11-27 12:00 | 256 | 254
2018-11-27 12:30 | 285 | 283
2018-11-27 13:00 | 260 | 258
2018-11-27 13:30 | 266 | 263
2018-11-27 14:00 | 262 | 260
2018-11-27 14:30 | 265 | 262
2018-11-27 15:00 | 255 | 252
2018-11-27 15:30 | 316 | 314
2018-11-27 16:00 | 317 | 314
2018-11-27 16:30 | 318 | 315
2018-11-27 17:00 | 334 | 332
2018-11-27 17:30 | 361 | 358
2018-11-27 18:00 | 371 | 369
2018-11-27 18:30 | 377 | 375
2018-11-27 19:00 | 382 | 381
2018-11-27 19:30 | 382 | 380
2018-11-27 20:00 | 366 | 364
2018-11-27 20:30 | 338 | 335
2018-11-27 21:00 | 360 | 358
2018-11-27 21:30 | 377 | 376
2018-11-27 22:00 | 353 | 352
2018-11-27 22:30 | 347 | 345
2018-11-27 23:00 | 339 | 336
2018-11-27 23:30 | 306 | 304
2018-11-28 | 289 | 286
2018-11-28 00:30 | 280 | 277
2018-11-28 01:00 | 271 | 268
2018-11-28 01:30 | 270 | 269
2018-11-28 02:00 | 264 | 264
2018-11-28 02:30 | 262 | 261
2018-11-28 03:00 | 259 | 258
2018-11-28 03:30 | 257 | 256
2018-11-28 04:00 | 256 | 255
2018-11-28 04:30 | 254 | 254
2018-11-28 05:00 | 251 | 250
2018-11-28 05:30 | 253 | 253
2018-11-28 06:00 | 264 | 263
2018-11-28 06:30 | 261 | 260
2018-11-28 07:00 | 250 | 250
2018-11-28 07:30 | 236 | 236
2018-11-28 08:00 | 208 | 208
2018-11-28 08:30 | 195 | 194
2018-11-28 09:00 | 257 | 257
2018-11-28 09:30 | 359 | 358
2018-11-28 10:00 | 338 | 338
2018-11-28 10:30 | 358 | 358
2018-11-28 11:00 | 382 | 381
2018-11-28 11:30 | 380 | 379
2018-11-28 12:00 | 420 | 419
2018-11-28 12:30 | 425 | 424
2018-11-28 13:00 | 401 | 400
2018-11-28 13:30 | 418 | 417
2018-11-28 14:00 | 420 | 420
2018-11-28 14:30 | 428 | 428
2018-11-28 15:00 | 488 | 488
2018-11-28 15:30 | 467 | 467
2018-11-28 16:00 | 476 | 476
2018-11-28 16:30 | 320 | 318
2018-11-28 17:00 | 273 | 272
2018-11-28 17:30 | 277 | 276
2018-11-28 18:00 | 281 | 280
2018-11-28 18:30 | 288 | 287
2018-11-28 19:00 | 303 | 303
2018-11-28 19:30 | 313 | 312
2018-11-28 20:00 | 305 | 304
2018-11-28 20:30 | 316 | 315
2018-11-28 21:00 | 343 | 341
2018-11-28 21:30 | 366 | 365
2018-11-28 22:00 | 360 | 359
2018-11-28 22:30 | 339 | 339
2018-11-28 23:00 | 313 | 312
2018-11-28 23:30 | 287 | 287
2018-11-29 | 270 | 269
2018-11-29 00:30 | 254 | 254
2018-11-29 01:00 | 252 | 252
2018-11-29 01:30 | 246 | 245
2018-11-29 02:00 | 245 | 244
2018-11-29 02:30 | 242 | 242
2018-11-29 03:00 | 228 | 227
2018-11-29 03:30 | 228 | 227
2018-11-29 04:00 | 234 | 233
2018-11-29 04:30 | 238 | 237
2018-11-29 05:00 | 244 | 243
2018-11-29 05:30 | 245 | 244
2018-11-29 06:00 | 244 | 243
2018-11-29 06:30 | 241 | 241
2018-11-29 07:00 | 226 | 225
2018-11-29 07:30 | 220 | 220
2018-11-29 08:00 | 198 | 197
2018-11-29 08:30 | 182 | 181
2018-11-29 09:00 | 185 | 184
2018-11-29 09:30 | 218 | 217
2018-11-29 10:00 | 225 | 224
2018-11-29 10:30 | 239 | 238
2018-11-29 11:00 | 245 | 245
2018-11-29 11:30 | 260 | 259
2018-11-29 12:00 | 272 | 271
2018-11-29 12:30 | 284 | 283
2018-11-29 13:00 | 290 | 290
2018-11-29 13:30 | 347 | 346
2018-11-29 14:00 | 365 | 364
2018-11-29 14:30 | 371 | 371
2018-11-29 15:00 | 378 | 378
2018-11-29 15:30 | 412 | 412
2018-11-29 16:00 | 266 | 265
2018-11-29 16:30 | 267 | 266
2018-11-29 17:00 | 270 | 269
2018-11-29 17:30 | 311 | 310
2018-11-29 18:00 | 327 | 327
2018-11-29 18:30 | 341 | 340
2018-11-29 19:00 | 351 | 350
2018-11-29 19:30 | 337 | 336
2018-11-29 20:00 | 329 | 328
2018-11-29 20:30 | 325 | 324
2018-11-29 21:00 | 331 | 331
2018-11-29 21:30 | 344 | 343
2018-11-29 22:00 | 359 | 358
2018-11-29 22:30 | 342 | 341
2018-11-29 23:00 | 324 | 323
2018-11-29 23:30 | 308 | 307
2018-11-30 | 297 | 296
2018-11-30 00:30 | 289 | 287
2018-11-30 01:00 | 279 | 278
2018-11-30 01:30 | 274 | 273
2018-11-30 02:00 | 268 | 267
2018-11-30 02:30 | 264 | 262
2018-11-30 03:00 | 258 | 256
2018-11-30 03:30 | 255 | 254
2018-11-30 04:00 | 252 | 251
2018-11-30 04:30 | 250 | 249
2018-11-30 05:00 | 249 | 248
2018-11-30 05:30 | 255 | 254
2018-11-30 06:00 | 254 | 253
2018-11-30 06:30 | 238 | 237
2018-11-30 07:00 | 211 | 210
2018-11-30 07:30 | 184 | 183
2018-11-30 08:00 | 158 | 158
2018-11-30 08:30 | 155 | 154
2018-11-30 09:00 | 146 | 146
2018-11-30 09:30 | 163 | 162
2018-11-30 10:00 | 169 | 168
2018-11-30 10:30 | 162 | 161
2018-11-30 11:00 | 164 | 164
2018-11-30 11:30 | 170 | 169
2018-11-30 12:00 | 178 | 178
2018-11-30 12:30 | 306 | 305
2018-11-30 13:00 | 211 | 210
2018-11-30 13:30 | 202 | 201
2018-11-30 14:00 | 209 | 208
2018-11-30 14:30 | 219 | 218
2018-11-30 15:00 | 228 | 227
2018-11-30 15:30 | 234 | 234
2018-11-30 16:00 | 234 | 233
2018-11-30 16:30 | 257 | 256
2018-11-30 17:00 | 277 | 277
2018-11-30 17:30 | 303 | 302
2018-11-30 18:00 | 337 | 336
2018-11-30 18:30 | 362 | 361
2018-11-30 19:00 | 350 | 349
2018-11-30 19:30 | 369 | 368
2018-11-30 20:00 | 372 | 371
2018-11-30 20:30 | 368 | 367
2018-11-30 21:00 | 366 | 365
2018-11-30 21:30 | 349 | 349
2018-11-30 22:00 | 338 | 337
2018-11-30 22:30 | 323 | 322
2018-11-30 23:00 | 311 | 309
2018-11-30 23:30 | 298 | 297
2018-12-01 | 289 | 288
2018-12-01 00:30 | 291 | 290
2018-12-01 01:00 | 282 | 281
2018-12-01 01:30 | 275 | 274
2018-12-01 02:00 | 267 | 267
2018-12-01 02:30 | 263 | 262
2018-12-01 03:00 | 261 | 260
2018-12-01 03:30 | 258 | 257
2018-12-01 04:00 | 256 | 255
2018-12-01 04:30 | 255 | 254
2018-12-01 05:00 | 252 | 251
2018-12-01 05:30 | 249 | 248
2018-12-01 06:00 | 241 | 240
2018-12-01 06:30 | 226 | 225
2018-12-01 07:00 | 199 | 199
2018-12-01 07:30 | 175 | 174
2018-12-01 08:00 | 163 | 162
2018-12-01 08:30 | 223 | 222
2018-12-01 09:00 | 283 | 282
2018-12-01 09:30 | 260 | 259
2018-12-01 10:00 | 255 | 254
2018-12-01 10:30 | 249 | 248
2018-12-01 11:00 | 249 | 248
2018-12-01 11:30 | 251 | 251
2018-12-01 12:00 | 265 | 265
2018-12-01 12:30 | 276 | 276
2018-12-01 13:00 | 293 | 293
2018-12-01 13:30 | 299 | 299
2018-12-01 14:00 | 325 | 324
2018-12-01 14:30 | 337 | 337
2018-12-01 15:00 | 351 | 351
2018-12-01 15:30 | 228 | 227
2018-12-01 16:00 | 230 | 229
2018-12-01 16:30 | 256 | 254
2018-12-01 17:00 | 278 | 277
2018-12-01 17:30 | 301 | 300
2018-12-01 18:00 | 332 | 331
2018-12-01 18:30 | 365 | 364
2018-12-01 19:00 | 376 | 376
2018-12-01 19:30 | 380 | 380
2018-12-01 20:00 | 383 | 382
2018-12-01 20:30 | 383 | 383
2018-12-01 21:00 | 365 | 365
2018-12-01 21:30 | 346 | 345
2018-12-01 22:00 | 332 | 332
2018-12-01 22:30 | 300 | 300
2018-12-01 23:00 | 223 | 221
2018-12-01 23:30 | 211 | 210
2018-12-02 | 216 | 214
2018-12-02 00:30 | 221 | 220
2018-12-02 01:00 | 212 | 211
2018-12-02 01:30 | 204 | 203
2018-12-02 02:00 | 199 | 198
2018-12-02 02:30 | 190 | 188
2018-12-02 03:00 | 182 | 181
2018-12-02 03:30 | 182 | 180
2018-12-02 04:00 | 183 | 181
2018-12-02 04:30 | 185 | 183
2018-12-02 05:00 | 188 | 187
2018-12-02 05:30 | 188 | 187
2018-12-02 06:00 | 183 | 182
2018-12-02 06:30 | 169 | 168
2018-12-02 07:00 | 144 | 143
2018-12-02 07:30 | 200 | 199
2018-12-02 08:00 | 180 | 180
2018-12-02 08:30 | 194 | 193
2018-12-02 09:00 | 194 | 193
2018-12-02 09:30 | 195 | 194
2018-12-02 10:00 | 181 | 180
2018-12-02 10:30 | 183 | 183
2018-12-02 11:00 | 253 | 252
2018-12-02 11:30 | 267 | 266
2018-12-02 12:00 | 282 | 281
2018-12-02 12:30 | 286 | 286
2018-12-02 13:00 | 291 | 291
2018-12-02 13:30 | 298 | 297
2018-12-02 14:00 | 306 | 305
2018-12-02 14:30 | 331 | 331
2018-12-02 15:00 | 332 | 332
2018-12-02 15:30 | 348 | 348
2018-12-02 16:00 | 280 | 280
2018-12-02 16:30 | 166 | 164
2018-12-02 17:00 | 187 | 186
2018-12-02 17:30 | 231 | 230
2018-12-02 18:00 | 271 | 270
2018-12-02 18:30 | 295 | 294
2018-12-02 19:00 | 291 | 290
2018-12-02 19:30 | 280 | 279
2018-12-02 20:00 | 272 | 271
2018-12-02 20:30 | 265 | 264
2018-12-02 21:00 | 285 | 284
2018-12-02 21:30 | 322 | 320
2018-12-02 22:00 | 347 | 346
2018-12-02 22:30 | 335 | 333
2018-12-02 23:00 | 319 | 317
2018-12-02 23:30 | 303 | 300
2018-12-03 | 294 | 292
2018-12-03 00:30 | 288 | 287
2018-12-03 01:00 | 280 | 278
2018-12-03 01:30 | 264 | 262
2018-12-03 02:00 | 238 | 236
2018-12-03 02:30 | 232 | 230
2018-12-03 03:00 | 227 | 225
2018-12-03 03:30 | 225 | 223
2018-12-03 04:00 | 225 | 223
2018-12-03 04:30 | 222 | 220
2018-12-03 05:00 | 209 | 207
2018-12-03 05:30 | 189 | 186
2018-12-03 06:00 | 193 | 190
2018-12-03 06:30 | 202 | 200
2018-12-03 07:00 | 184 | 182
2018-12-03 07:30 | 283 | 282
2018-12-03 08:00 | 266 | 266
2018-12-03 08:30 | 272 | 272
2018-12-03 09:00 | 243 | 242
2018-12-03 09:30 | 217 | 217
2018-12-03 10:00 | 195 | 194
2018-12-03 10:30 | 175 | 175
2018-12-03 11:00 | 180 | 179
2018-12-03 11:30 | 188 | 187
2018-12-03 12:00 | 205 | 204
2018-12-03 12:30 | 225 | 223
2018-12-03 13:00 | 227 | 226
2018-12-03 13:30 | 223 | 222
2018-12-03 14:00 | 248 | 247
2018-12-03 14:30 | 253 | 252
2018-12-03 15:00 | 185 | 184
2018-12-03 15:30 | 259 | 257
2018-12-03 16:00 | 189 | 186
2018-12-03 16:30 | 226 | 224
2018-12-03 17:00 | 283 | 281
2018-12-03 17:30 | 318 | 316
2018-12-03 18:00 | 325 | 323
2018-12-03 18:30 | 336 | 335
2018-12-03 19:00 | 369 | 368
2018-12-03 19:30 | 355 | 354
2018-12-03 20:00 | 311 | 309
2018-12-03 20:30 | 289 | 288
2018-12-03 21:00 | 273 | 271
2018-12-03 21:30 | 258 | 257
2018-12-03 22:00 | 247 | 246
2018-12-03 22:30 | 226 | 224
2018-12-03 23:00 | 206 | 204
2018-12-03 23:30 | 195 | 193
2018-12-04 | 216 | 214
2018-12-04 00:30 | 224 | 223
2018-12-04 01:00 | 195 | 193
2018-12-04 01:30 | 187 | 185
2018-12-04 02:00 | 164 | 163
2018-12-04 02:30 | 186 | 185
2018-12-04 03:00 | 183 | 181
2018-12-04 03:30 | 177 | 175
2018-12-04 04:00 | 178 | 176
2018-12-04 04:30 | 189 | 188
2018-12-04 05:00 | 195 | 194
2018-12-04 05:30 | 207 | 206
2018-12-04 06:00 | 195 | 193
2018-12-04 06:30 | 164 | 163
2018-12-04 07:00 | 142 | 141
2018-12-04 07:30 | 199 | 198
2018-12-04 08:00 | 185 | 185
2018-12-04 08:30 | 173 | 173
2018-12-04 09:00 | 161 | 161
2018-12-04 09:30 | 152 | 151
2018-12-04 10:00 | 124 | 123
2018-12-04 10:30 | 158 | 157
2018-12-04 11:00 | 181 | 180
2018-12-04 11:30 | 186 | 186
2018-12-04 12:00 | 200 | 199
2018-12-04 12:30 | 209 | 209
2018-12-04 13:00 | 220 | 219
2018-12-04 13:30 | 233 | 233
2018-12-04 14:00 | 259 | 258
2018-12-04 14:30 | 225 | 225
2018-12-04 15:00 | 255 | 255
2018-12-04 15:30 | 212 | 212
2018-12-04 16:00 | 212 | 211
2018-12-04 16:30 | 234 | 233
2018-12-04 17:00 | 261 | 260
2018-12-04 17:30 | 308 | 308
2018-12-04 18:00 | 309 | 308
2018-12-04 18:30 | 315 | 314
2018-12-04 19:00 | 332 | 332
2018-12-04 19:30 | 334 | 334
2018-12-04 20:00 | 350 | 349
2018-12-04 20:30 | 359 | 358
2018-12-04 21:00 | 345 | 344
2018-12-04 21:30 | 320 | 319
2018-12-04 22:00 | 304 | 304
2018-12-04 22:30 | 314 | 314
2018-12-04 23:00 | 308 | 307
2018-12-04 23:30 | 288 | 287
2018-12-05 | 280 | 279
2018-12-05 00:30 | 287 | 287
2018-12-05 01:00 | 281 | 280
2018-12-05 01:30 | 276 | 276
2018-12-05 02:00 | 275 | 275
2018-12-05 02:30 | 276 | 275
2018-12-05 03:00 | 271 | 271
2018-12-05 03:30 | 268 | 267
2018-12-05 04:00 | 260 | 259
2018-12-05 04:30 | 262 | 261
2018-12-05 05:00 | 263 | 262
2018-12-05 05:30 | 271 | 271
2018-12-05 06:00 | 276 | 275
2018-12-05 06:30 | 275 | 274
2018-12-05 07:00 | 264 | 263
2018-12-05 07:30 | 252 | 251
2018-12-05 08:00 | 230 | 230
2018-12-05 08:30 | 363 | 363
2018-12-05 09:00 | 376 | 376
2018-12-05 09:30 | 363 | 363
2018-12-05 10:00 | 322 | 321
2018-12-05 10:30 | 302 | 302
2018-12-05 11:00 | 298 | 298
2018-12-05 11:30 | 312 | 312
2018-12-05 12:00 | 329 | 328
2018-12-05 12:30 | 334 | 333
2018-12-05 13:00 | 345 | 345
2018-12-05 13:30 | 337 | 336
2018-12-05 14:00 | 322 | 322
2018-12-05 14:30 | 277 | 276
2018-12-05 15:00 | 306 | 305
2018-12-05 15:30 | 259 | 258
2018-12-05 16:00 | 222 | 221
2018-12-05 16:30 | 234 | 233
2018-12-05 17:00 | 244 | 243
2018-12-05 17:30 | 274 | 273
2018-12-05 18:00 | 307 | 306
2018-12-05 18:30 | 309 | 308
2018-12-05 19:00 | 339 | 338
2018-12-05 19:30 | 356 | 355
2018-12-05 20:00 | 322 | 320
2018-12-05 20:30 | 298 | 296
2018-12-05 21:00 | 298 | 296
2018-12-05 21:30 | 291 | 290
2018-12-05 22:00 | 271 | 270
2018-12-05 22:30 | 261 | 259
2018-12-05 23:00 | 249 | 248
2018-12-05 23:30 | 233 | 232
2018-12-06 | 227 | 226
2018-12-06 00:30 | 227 | 226
2018-12-06 01:00 | 210 | 209
2018-12-06 01:30 | 211 | 210
2018-12-06 02:00 | 222 | 220
2018-12-06 02:30 | 227 | 226
2018-12-06 03:00 | 217 | 216
2018-12-06 03:30 | 223 | 222
2018-12-06 04:00 | 228 | 227
2018-12-06 04:30 | 231 | 230
2018-12-06 05:00 | 233 | 232
2018-12-06 05:30 | 241 | 240
2018-12-06 06:00 | 208 | 207
2018-12-06 06:30 | 225 | 224
2018-12-06 07:00 | 213 | 212
2018-12-06 07:30 | 395 | 395
2018-12-06 08:00 | 424 | 424
2018-12-06 08:30 | 425 | 425
2018-12-06 09:00 | 411 | 410
2018-12-06 09:30 | 362 | 361
2018-12-06 10:00 | 290 | 289
2018-12-06 10:30 | 255 | 254
2018-12-06 11:00 | 222 | 221
2018-12-06 11:30 | 226 | 225
2018-12-06 12:00 | 248 | 247
2018-12-06 12:30 | 279 | 278
2018-12-06 13:00 | 292 | 291
2018-12-06 13:30 | 277 | 276
2018-12-06 14:00 | 296 | 295
2018-12-06 14:30 | 310 | 310
2018-12-06 15:00 | 346 | 345
2018-12-06 15:30 | 283 | 282
2018-12-06 16:00 | 248 | 246
2018-12-06 16:30 | 259 | 258
2018-12-06 17:00 | 266 | 265
2018-12-06 17:30 | 275 | 273
2018-12-06 18:00 | 266 | 265
2018-12-06 18:30 | 250 | 248
2018-12-06 19:00 | 252 | 250
2018-12-06 19:30 | 271 | 270
2018-12-06 20:00 | 270 | 269
2018-12-06 20:30 | 261 | 259
2018-12-06 21:00 | 255 | 253
2018-12-06 21:30 | 271 | 270
2018-12-06 22:00 | 265 | 264
2018-12-06 22:30 | 270 | 269
2018-12-06 23:00 | 252 | 251
2018-12-06 23:30 | 240 | 238
2018-12-07 | 230 | 228
2018-12-07 00:30 | 226 | 225
2018-12-07 01:00 | 206 | 205
2018-12-07 01:30 | 198 | 198
2018-12-07 02:00 | 191 | 190
2018-12-07 02:30 | 186 | 186
2018-12-07 03:00 | 191 | 190
2018-12-07 03:30 | 197 | 197
2018-12-07 04:00 | 196 | 196
2018-12-07 04:30 | 198 | 197
2018-12-07 05:00 | 208 | 208
2018-12-07 05:30 | 222 | 222
2018-12-07 06:00 | 218 | 217
2018-12-07 06:30 | 213 | 212
2018-12-07 07:00 | 225 | 224
2018-12-07 07:30 | 240 | 240
2018-12-07 08:00 | 243 | 243
2018-12-07 08:30 | 233 | 233
2018-12-07 09:00 | 229 | 228
2018-12-07 09:30 | 195 | 194
2018-12-07 10:00 | 190 | 189
2018-12-07 10:30 | 176 | 175
2018-12-07 11:00 | 151 | 151
2018-12-07 11:30 | 171 | 170
2018-12-07 12:00 | 171 | 170
2018-12-07 12:30 | 153 | 153
2018-12-07 13:00 | 161 | 161
2018-12-07 13:30 | 194 | 193
2018-12-07 14:00 | 207 | 206
2018-12-07 14:30 | 204 | 203
2018-12-07 15:00 | 203 | 203
2018-12-07 15:30 | 201 | 201
2018-12-07 16:00 | 211 | 210
2018-12-07 16:30 | 209 | 208
2018-12-07 17:00 | 206 | 205
2018-12-07 17:30 | 211 | 211
2018-12-07 18:00 | 192 | 192
2018-12-07 18:30 | 195 | 194
2018-12-07 19:00 | 202 | 202
2018-12-07 19:30 | 209 | 208
2018-12-07 20:00 | 207 | 206
2018-12-07 20:30 | 196 | 195
2018-12-07 21:00 | 203 | 203
2018-12-07 21:30 | 210 | 209
2018-12-07 22:00 | 214 | 213
2018-12-07 22:30 | 214 | 213
2018-12-07 23:00 | 220 | 220
2018-12-07 23:30 | 228 | 227
2018-12-08 | 218 | 218
2018-12-08 00:30 | 233 | 233
2018-12-08 01:00 | 220 | 219
2018-12-08 01:30 | 199 | 198
2018-12-08 02:00 | 197 | 196
2018-12-08 02:30 | 197 | 196
2018-12-08 03:00 | 202 | 201
2018-12-08 03:30 | 199 | 198
2018-12-08 04:00 | 202 | 201
2018-12-08 04:30 | 190 | 189
2018-12-08 05:00 | 193 | 192
2018-12-08 05:30 | 192 | 191
2018-12-08 06:00 | 197 | 196
2018-12-08 06:30 | 180 | 179
2018-12-08 07:00 | 172 | 171
2018-12-08 07:30 | 166 | 165
2018-12-08 08:00 | 163 | 162
2018-12-08 08:30 | 174 | 173
2018-12-08 09:00 | 158 | 157
2018-12-08 09:30 | 141 | 140
2018-12-08 10:00 | 123 | 122
2018-12-08 10:30 | 112 | 111
2018-12-08 11:00 | 96 | 95
2018-12-08 11:30 | 98 | 97
2018-12-08 12:00 | 110 | 109
2018-12-08 12:30 | 110 | 110
2018-12-08 13:00 | 119 | 118
2018-12-08 13:30 | 132 | 131
2018-12-08 14:00 | 152 | 152
2018-12-08 14:30 | 171 | 171
2018-12-08 15:00 | 197 | 196
2018-12-08 15:30 | 214 | 213
2018-12-08 16:00 | 208 | 207
2018-12-08 16:30 | 216 | 215
2018-12-08 17:00 | 226 | 225
2018-12-08 17:30 | 247 | 246
2018-12-08 18:00 | 266 | 266
2018-12-08 18:30 | 284 | 284
2018-12-08 19:00 | 291 | 290
2018-12-08 19:30 | 293 | 292
2018-12-08 20:00 | 283 | 282
2018-12-08 20:30 | 278 | 277
2018-12-08 21:00 | 257 | 257
2018-12-08 21:30 | 256 | 255
2018-12-08 22:00 | 234 | 233
2018-12-08 22:30 | 223 | 222
2018-12-08 23:00 | 219 | 218
2018-12-08 23:30 | 214 | 214
2018-12-09 | 231 | 230
2018-12-09 00:30 | 243 | 242
2018-12-09 01:00 | 226 | 225
2018-12-09 01:30 | 214 | 213
2018-12-09 02:00 | 212 | 211
2018-12-09 02:30 | 208 | 207
2018-12-09 03:00 | 208 | 207
2018-12-09 03:30 | 204 | 203
2018-12-09 04:00 | 213 | 212
2018-12-09 04:30 | 212 | 211
2018-12-09 05:00 | 220 | 219
2018-12-09 05:30 | 223 | 222
2018-12-09 06:00 | 221 | 220
2018-12-09 06:30 | 219 | 218
2018-12-09 07:00 | 216 | 215
2018-12-09 07:30 | 210 | 209
2018-12-09 08:00 | 221 | 220
2018-12-09 08:30 | 203 | 202
2018-12-09 09:00 | 208 | 207
2018-12-09 09:30 | 202 | 201
2018-12-09 10:00 | 164 | 163
2018-12-09 10:30 | 147 | 146
2018-12-09 11:00 | 157 | 156
2018-12-09 11:30 | 180 | 180
2018-12-09 12:00 | 169 | 168
2018-12-09 12:30 | 169 | 168
2018-12-09 13:00 | 180 | 179
2018-12-09 13:30 | 153 | 152
2018-12-09 14:00 | 160 | 159
2018-12-09 14:30 | 175 | 174
2018-12-09 15:00 | 178 | 177
2018-12-09 15:30 | 189 | 188
2018-12-09 16:00 | 203 | 202
2018-12-09 16:30 | 215 | 214
2018-12-09 17:00 | 217 | 216
2018-12-09 17:30 | 223 | 222
2018-12-09 18:00 | 239 | 238
2018-12-09 18:30 | 232 | 232
2018-12-09 19:00 | 234 | 233
2018-12-09 19:30 | 230 | 229
2018-12-09 20:00 | 202 | 202
2018-12-09 20:30 | 216 | 215
2018-12-09 21:00 | 223 | 222
2018-12-09 21:30 | 212 | 211
2018-12-09 22:00 | 199 | 199
2018-12-09 22:30 | 180 | 179
2018-12-09 23:00 | 155 | 154
2018-12-09 23:30 | 130 | 129
2018-12-10 | 114 | 113
2018-12-10 00:30 | 121 | 120
2018-12-10 01:00 | 108 | 107
2018-12-10 01:30 | 105 | 104
2018-12-10 02:00 | 98 | 96
2018-12-10 02:30 | 98 | 97
2018-12-10 03:00 | 99 | 98
2018-12-10 03:30 | 100 | 99
2018-12-10 04:00 | 94 | 92
2018-12-10 04:30 | 86 | 84
2018-12-10 05:00 | 85 | 83
2018-12-10 05:30 | 92 | 91
2018-12-10 06:00 | 101 | 100
2018-12-10 06:30 | 114 | 113
2018-12-10 07:00 | 100 | 99
2018-12-10 07:30 | 139 | 138
2018-12-10 08:00 | 148 | 147
2018-12-10 08:30 | 132 | 132
2018-12-10 09:00 | 125 | 125
2018-12-10 09:30 | 107 | 106
2018-12-10 10:00 | 70 | 67
2018-12-10 10:30 | 82 | 80
2018-12-10 11:00 | 76 | 74
2018-12-10 11:30 | 96 | 95
2018-12-10 12:00 | 97 | 96
2018-12-10 12:30 | 97 | 96
2018-12-10 13:00 | 87 | 86
2018-12-10 13:30 | 101 | 100
2018-12-10 14:00 | 117 | 116
2018-12-10 14:30 | 112 | 111
2018-12-10 15:00 | 106 | 105
2018-12-10 15:30 | 124 | 124
2018-12-10 16:00 | 135 | 134
2018-12-10 16:30 | 144 | 143
2018-12-10 17:00 | 151 | 151
2018-12-10 17:30 | 156 | 155
2018-12-10 18:00 | 167 | 166
2018-12-10 18:30 | 183 | 182
2018-12-10 19:00 | 201 | 201
2018-12-10 19:30 | 187 | 186
2018-12-10 20:00 | 191 | 191
2018-12-10 20:30 | 185 | 184
2018-12-10 21:00 | 186 | 185
2018-12-10 21:30 | 175 | 174
2018-12-10 22:00 | 172 | 171
2018-12-10 22:30 | 170 | 169
2018-12-10 23:00 | 164 | 163
2018-12-10 23:30 | 156 | 155
2018-12-11 | 154 | 154
2018-12-11 00:30 | 158 | 157
2018-12-11 01:00 | 137 | 136
2018-12-11 01:30 | 117 | 116
2018-12-11 02:00 | 116 | 115
2018-12-11 02:30 | 113 | 112
2018-12-11 03:00 | 114 | 113
2018-12-11 03:30 | 117 | 116
2018-12-11 04:00 | 117 | 116
2018-12-11 04:30 | 122 | 121
2018-12-11 05:00 | 121 | 120
2018-12-11 05:30 | 134 | 133
2018-12-11 06:00 | 145 | 144
2018-12-11 06:30 | 155 | 154
2018-12-11 07:00 | 163 | 162
2018-12-11 07:30 | 155 | 155
2018-12-11 08:00 | 159 | 158
2018-12-11 08:30 | 205 | 204
2018-12-11 09:00 | 210 | 209
2018-12-11 09:30 | 240 | 240
2018-12-11 10:00 | 244 | 243
2018-12-11 10:30 | 238 | 237
2018-12-11 11:00 | 230 | 230
2018-12-11 11:30 | 220 | 220
2018-12-11 12:00 | 242 | 242
2018-12-11 12:30 | 196 | 195
2018-12-11 13:00 | 159 | 158
2018-12-11 13:30 | 146 | 145
2018-12-11 14:00 | 187 | 187
2018-12-11 14:30 | 191 | 191
2018-12-11 15:00 | 197 | 197
2018-12-11 15:30 | 254 | 254
2018-12-11 16:00 | 289 | 288
2018-12-11 16:30 | 185 | 184
2018-12-11 17:00 | 91 | 90
2018-12-11 17:30 | 137 | 136
2018-12-11 18:00 | 130 | 129
2018-12-11 18:30 | 158 | 157
2018-12-11 19:00 | 174 | 173
2018-12-11 19:30 | 186 | 185
2018-12-11 20:00 | 183 | 182
2018-12-11 20:30 | 173 | 172
2018-12-11 21:00 | 189 | 188
2018-12-11 21:30 | 219 | 218
2018-12-11 22:00 | 211 | 210
2018-12-11 22:30 | 199 | 197
2018-12-11 23:00 | 191 | 190
2018-12-11 23:30 | 182 | 182
2018-12-12 | 179 | 179
2018-12-12 00:30 | 179 | 178
2018-12-12 01:00 | 161 | 160
2018-12-12 01:30 | 158 | 157
2018-12-12 02:00 | 153 | 153
2018-12-12 02:30 | 145 | 144
2018-12-12 03:00 | 146 | 146
2018-12-12 03:30 | 154 | 153
2018-12-12 04:00 | 150 | 149
2018-12-12 04:30 | 150 | 150
2018-12-12 05:00 | 152 | 151
2018-12-12 05:30 | 153 | 152
2018-12-12 06:00 | 157 | 156
2018-12-12 06:30 | 170 | 169
2018-12-12 07:00 | 147 | 146
2018-12-12 07:30 | 150 | 149
2018-12-12 08:00 | 157 | 157
2018-12-12 08:30 | 153 | 152
2018-12-12 09:00 | 157 | 156
2018-12-12 09:30 | 137 | 137
2018-12-12 10:00 | 132 | 131
2018-12-12 10:30 | 117 | 116
2018-12-12 11:00 | 112 | 112
2018-12-12 11:30 | 114 | 113
2018-12-12 12:00 | 113 | 112
2018-12-12 12:30 | 117 | 116
2018-12-12 13:00 | 112 | 111
2018-12-12 13:30 | 108 | 107
2018-12-12 14:00 | 102 | 101
2018-12-12 14:30 | 118 | 117
2018-12-12 15:00 | 80 | 78
2018-12-12 15:30 | 88 | 87
2018-12-12 16:00 | 117 | 116
2018-12-12 16:30 | 135 | 134
2018-12-12 17:00 | 132 | 131
2018-12-12 17:30 | 164 | 164
2018-12-12 18:00 | 182 | 182
2018-12-12 18:30 | 183 | 183
2018-12-12 19:00 | 199 | 199
2018-12-12 19:30 | 209 | 208
2018-12-12 20:00 | 208 | 207
2018-12-12 20:30 | 230 | 230
2018-12-12 21:00 | 262 | 262
2018-12-12 21:30 | 259 | 258
2018-12-12 22:00 | 242 | 241
2018-12-12 22:30 | 240 | 240
2018-12-12 23:00 | 233 | 233
2018-12-12 23:30 | 221 | 221
2018-12-13 | 214 | 213
2018-12-13 00:30 | 215 | 215
2018-12-13 01:00 | 201 | 200
2018-12-13 01:30 | 194 | 193
2018-12-13 02:00 | 190 | 189
2018-12-13 02:30 | 187 | 187
2018-12-13 03:00 | 184 | 183
2018-12-13 03:30 | 183 | 182
2018-12-13 04:00 | 180 | 179
2018-12-13 04:30 | 179 | 178
2018-12-13 05:00 | 176 | 175
2018-12-13 05:30 | 167 | 166
2018-12-13 06:00 | 160 | 159
2018-12-13 06:30 | 156 | 155
2018-12-13 07:00 | 140 | 139
2018-12-13 07:30 | 150 | 149
2018-12-13 08:00 | 128 | 127
2018-12-13 08:30 | 133 | 132
2018-12-13 09:00 | 126 | 125
2018-12-13 09:30 | 98 | 97
2018-12-13 10:00 | 114 | 113
2018-12-13 10:30 | 116 | 115
2018-12-13 11:00 | 109 | 108
2018-12-13 11:30 | 93 | 92
2018-12-13 12:00 | 98 | 97
2018-12-13 12:30 | 103 | 101
2018-12-13 13:00 | 109 | 108
2018-12-13 13:30 | 105 | 104
2018-12-13 14:00 | 110 | 109
2018-12-13 14:30 | 90 | 88
2018-12-13 15:00 | 94 | 92
2018-12-13 15:30 | 127 | 126
2018-12-13 16:00 | 148 | 148
2018-12-13 16:30 | 169 | 169
2018-12-13 17:00 | 187 | 187
2018-12-13 17:30 | 221 | 220
2018-12-13 18:00 | 214 | 214
2018-12-13 18:30 | 218 | 218
2018-12-13 19:00 | 212 | 212
2018-12-13 19:30 | 208 | 208
2018-12-13 20:00 | 195 | 194
2018-12-13 20:30 | 211 | 211
2018-12-13 21:00 | 239 | 238
2018-12-13 21:30 | 234 | 234
2018-12-13 22:00 | 221 | 221
2018-12-13 22:30 | 207 | 206
2018-12-13 23:00 | 197 | 196
2018-12-13 23:30 | 198 | 196
2018-12-14 | 167 | 165
2018-12-14 00:30 | 166 | 164
2018-12-14 01:00 | 144 | 142
2018-12-14 01:30 | 133 | 131
2018-12-14 02:00 | 144 | 142
2018-12-14 02:30 | 151 | 149
2018-12-14 03:00 | 171 | 170
2018-12-14 03:30 | 183 | 182
2018-12-14 04:00 | 187 | 186
2018-12-14 04:30 | 186 | 185
2018-12-14 05:00 | 187 | 186
2018-12-14 05:30 | 195 | 194
2018-12-14 06:00 | 198 | 197
2018-12-14 06:30 | 194 | 193
2018-12-14 07:00 | 192 | 191
2018-12-14 07:30 | 173 | 172
2018-12-14 08:00 | 169 | 168
2018-12-14 08:30 | 154 | 153
2018-12-14 09:00 | 112 | 110
2018-12-14 09:30 | 112 | 111
2018-12-14 10:00 | 119 | 118
2018-12-14 10:30 | 107 | 106
2018-12-14 11:00 | 101 | 100
2018-12-14 11:30 | 112 | 111
2018-12-14 12:00 | 127 | 126
2018-12-14 12:30 | 97 | 96
2018-12-14 13:00 | 113 | 112
2018-12-14 13:30 | 116 | 115
2018-12-14 14:00 | 135 | 135
2018-12-14 14:30 | 180 | 180
2018-12-14 15:00 | 201 | 201
2018-12-14 15:30 | 221 | 220
2018-12-14 16:00 | 193 | 192
2018-12-14 16:30 | 183 | 183
2018-12-14 17:00 | 218 | 217
2018-12-14 17:30 | 224 | 224
2018-12-14 18:00 | 237 | 237
2018-12-14 18:30 | 238 | 238
2018-12-14 19:00 | 241 | 241
2018-12-14 19:30 | 243 | 242
2018-12-14 20:00 | 228 | 227
2018-12-14 20:30 | 244 | 244
2018-12-14 21:00 | 271 | 271
2018-12-14 21:30 | 269 | 269
2018-12-14 22:00 | 256 | 256
2018-12-14 22:30 | 241 | 240
2018-12-14 23:00 | 231 | 230
2018-12-14 23:30 | 224 | 223
2018-12-15 | 217 | 216
2018-12-15 00:30 | 217 | 216
2018-12-15 01:00 | 203 | 203
2018-12-15 01:30 | 208 | 207
2018-12-15 02:00 | 211 | 210
2018-12-15 02:30 | 208 | 207
2018-12-15 03:00 | 204 | 203
2018-12-15 03:30 | 200 | 200
2018-12-15 04:00 | 198 | 197
2018-12-15 04:30 | 189 | 188
2018-12-15 05:00 | 192 | 191
2018-12-15 05:30 | 196 | 196
2018-12-15 06:00 | 198 | 197
2018-12-15 06:30 | 203 | 202
2018-12-15 07:00 | 199 | 198
2018-12-15 07:30 | 190 | 190
2018-12-15 08:00 | 195 | 194
2018-12-15 08:30 | 184 | 183
2018-12-15 09:00 | 184 | 183
2018-12-15 09:30 | 184 | 184
2018-12-15 10:00 | 169 | 168
2018-12-15 10:30 | 183 | 182
2018-12-15 11:00 | 157 | 156
2018-12-15 11:30 | 184 | 184
2018-12-15 12:00 | 169 | 168
2018-12-15 12:30 | 175 | 175
2018-12-15 13:00 | 176 | 175
2018-12-15 13:30 | 194 | 193
2018-12-15 14:00 | 195 | 195
2018-12-15 14:30 | 207 | 207
2018-12-15 15:00 | 206 | 206
2018-12-15 15:30 | 201 | 200
2018-12-15 16:00 | 232 | 231
2018-12-15 16:30 | 246 | 245
2018-12-15 17:00 | 241 | 241
2018-12-15 17:30 | 249 | 248
2018-12-15 18:00 | 259 | 259
2018-12-15 18:30 | 273 | 272
2018-12-15 19:00 | 282 | 281
2018-12-15 19:30 | 275 | 275
2018-12-15 20:00 | 266 | 266
2018-12-15 20:30 | 244 | 244
2018-12-15 21:00 | 232 | 231
2018-12-15 21:30 | 224 | 223
2018-12-15 22:00 | 214 | 213
2018-12-15 22:30 | 206 | 205
2018-12-15 23:00 | 194 | 193
2018-12-15 23:30 | 174 | 173
2018-12-16 | 161 | 160
2018-12-16 00:30 | 172 | 171
2018-12-16 01:00 | 153 | 152
2018-12-16 01:30 | 144 | 143
2018-12-16 02:00 | 141 | 140
2018-12-16 02:30 | 141 | 140
2018-12-16 03:00 | 138 | 137
2018-12-16 03:30 | 142 | 141
2018-12-16 04:00 | 127 | 126
2018-12-16 04:30 | 132 | 131
2018-12-16 05:00 | 133 | 132
2018-12-16 05:30 | 121 | 120
2018-12-16 06:00 | 127 | 127
2018-12-16 06:30 | 144 | 144
2018-12-16 07:00 | 152 | 151
2018-12-16 07:30 | 164 | 163
2018-12-16 08:00 | 171 | 170
2018-12-16 08:30 | 177 | 177
2018-12-16 09:00 | 176 | 176
2018-12-16 09:30 | 168 | 168
2018-12-16 10:00 | 153 | 153
2018-12-16 10:30 | 138 | 137
2018-12-16 11:00 | 119 | 118
2018-12-16 11:30 | 105 | 103
2018-12-16 12:00 | 88 | 87
2018-12-16 12:30 | 93 | 92
2018-12-16 13:00 | 101 | 101
2018-12-16 13:30 | 95 | 94
2018-12-16 14:00 | 101 | 100
2018-12-16 14:30 | 109 | 109
2018-12-16 15:00 | 126 | 125
2018-12-16 15:30 | 123 | 123
2018-12-16 16:00 | 149 | 149
2018-12-16 16:30 | 177 | 176
2018-12-16 17:00 | 192 | 192
2018-12-16 17:30 | 218 | 217
2018-12-16 18:00 | 239 | 239
2018-12-16 18:30 | 257 | 256
2018-12-16 19:00 | 267 | 266
2018-12-16 19:30 | 272 | 272
2018-12-16 20:00 | 268 | 268
2018-12-16 20:30 | 258 | 257
2018-12-16 21:00 | 245 | 244
2018-12-16 21:30 | 233 | 233
2018-12-16 22:00 | 222 | 222
2018-12-16 22:30 | 213 | 212
2018-12-16 23:00 | 196 | 195
2018-12-16 23:30 | 182 | 181
2018-12-17 | 173 | 172
2018-12-17 00:30 | 176 | 175
2018-12-17 01:00 | 160 | 159
2018-12-17 01:30 | 160 | 159
2018-12-17 02:00 | 159 | 159
2018-12-17 02:30 | 157 | 156
2018-12-17 03:00 | 154 | 153
2018-12-17 03:30 | 153 | 153
2018-12-17 04:00 | 151 | 151
2018-12-17 04:30 | 150 | 150
2018-12-17 05:00 | 155 | 155
2018-12-17 05:30 | 154 | 154
2018-12-17 06:00 | 153 | 153
2018-12-17 06:30 | 159 | 159
2018-12-17 07:00 | 162 | 161
2018-12-17 07:30 | 161 | 160
2018-12-17 08:00 | 159 | 158
2018-12-17 08:30 | 157 | 157
2018-12-17 09:00 | 147 | 146
2018-12-17 09:30 | 134 | 133
2018-12-17 10:00 | 132 | 131
2018-12-17 10:30 | 136 | 135
2018-12-17 11:00 | 137 | 137
2018-12-17 11:30 | 138 | 137
2018-12-17 12:00 | 137 | 136
2018-12-17 12:30 | 133 | 132
2018-12-17 13:00 | 137 | 136
2018-12-17 13:30 | 144 | 144
2018-12-17 14:00 | 151 | 150
2018-12-17 14:30 | 159 | 159
2018-12-17 15:00 | 172 | 171
2018-12-17 15:30 | 185 | 184
2018-12-17 16:00 | 201 | 201
2018-12-17 16:30 | 220 | 220
2018-12-17 17:00 | 237 | 236
2018-12-17 17:30 | 252 | 252
2018-12-17 18:00 | 278 | 278
2018-12-17 18:30 | 294 | 293
2018-12-17 19:00 | 310 | 309
2018-12-17 19:30 | 316 | 315
2018-12-17 20:00 | 318 | 318
2018-12-17 20:30 | 315 | 314
2018-12-17 21:00 | 299 | 299
2018-12-17 21:30 | 284 | 283
2018-12-17 22:00 | 268 | 266
2018-12-17 22:30 | 248 | 247
2018-12-17 23:00 | 232 | 231
2018-12-17 23:30 | 216 | 215
2018-12-18 | 206 | 205
2018-12-18 00:30 | 205 | 205
2018-12-18 01:00 | 190 | 190
2018-12-18 01:30 | 194 | 193
2018-12-18 02:00 | 193 | 192
2018-12-18 02:30 | 190 | 189
2018-12-18 03:00 | 188 | 188
2018-12-18 03:30 | 186 | 185
2018-12-18 04:00 | 184 | 183
2018-12-18 04:30 | 179 | 178
2018-12-18 05:00 | 174 | 173
2018-12-18 05:30 | 178 | 177
2018-12-18 06:00 | 182 | 182
2018-12-18 06:30 | 183 | 182
2018-12-18 07:00 | 173 | 173
2018-12-18 07:30 | 167 | 166
2018-12-18 08:00 | 159 | 159
2018-12-18 08:30 | 148 | 147
2018-12-18 09:00 | 144 | 143
2018-12-18 09:30 | 144 | 144
2018-12-18 10:00 | 142 | 142
2018-12-18 10:30 | 145 | 145
2018-12-18 11:00 | 158 | 157
2018-12-18 11:30 | 168 | 168
2018-12-18 12:00 | 177 | 177
2018-12-18 12:30 | 190 | 190
2018-12-18 13:00 | 212 | 212
2018-12-18 13:30 | 219 | 219
2018-12-18 14:00 | 234 | 234
2018-12-18 14:30 | 243 | 243
2018-12-18 15:00 | 262 | 262
2018-12-18 15:30 | 256 | 255
2018-12-18 16:00 | 262 | 261
2018-12-18 16:30 | 276 | 275
2018-12-18 17:00 | 286 | 285
2018-12-18 17:30 | 311 | 310
2018-12-18 18:00 | 331 | 330
2018-12-18 18:30 | 335 | 334
2018-12-18 19:00 | 339 | 338
2018-12-18 19:30 | 347 | 346
2018-12-18 20:00 | 348 | 347
2018-12-18 20:30 | 350 | 350
2018-12-18 21:00 | 344 | 343
2018-12-18 21:30 | 327 | 326
2018-12-18 22:00 | 309 | 308
2018-12-18 22:30 | 287 | 287
2018-12-18 23:00 | 267 | 266
2018-12-18 23:30 | 269 | 269
2018-12-19 | 257 | 256
2018-12-19 00:30 | 252 | 251
2018-12-19 01:00 | 247 | 246
2018-12-19 01:30 | 235 | 234
2018-12-19 02:00 | 228 | 227
2018-12-19 02:30 | 224 | 223
2018-12-19 03:00 | 221 | 221
2018-12-19 03:30 | 218 | 218
2018-12-19 04:00 | 217 | 216
2018-12-19 04:30 | 217 | 216
2018-12-19 05:00 | 218 | 217
2018-12-19 05:30 | 221 | 220
2018-12-19 06:00 | 223 | 223
2018-12-19 06:30 | 213 | 212
2018-12-19 07:00 | 205 | 204
2018-12-19 07:30 | 202 | 201
2018-12-19 08:00 | 186 | 186
2018-12-19 08:30 | 178 | 177
2018-12-19 09:00 | 175 | 174
2018-12-19 09:30 | 165 | 164
2018-12-19 10:00 | 172 | 171
2018-12-19 10:30 | 170 | 170
2018-12-19 11:00 | 178 | 177
2018-12-19 11:30 | 163 | 163
2018-12-19 12:00 | 170 | 169
2018-12-19 12:30 | 183 | 182
2018-12-19 13:00 | 185 | 184
2018-12-19 13:30 | 187 | 187
2018-12-19 14:00 | 201 | 201
2018-12-19 14:30 | 206 | 206
2018-12-19 15:00 | 206 | 206
2018-12-19 15:30 | 215 | 215
2018-12-19 16:00 | 243 | 243
2018-12-19 16:30 | 267 | 267
2018-12-19 17:00 | 277 | 277
2018-12-19 17:30 | 291 | 291
2018-12-19 18:00 | 320 | 320
2018-12-19 18:30 | 334 | 333
2018-12-19 19:00 | 323 | 323
2018-12-19 19:30 | 317 | 317
2018-12-19 20:00 | 331 | 331
2018-12-19 20:30 | 333 | 333
2018-12-19 21:00 | 323 | 323
2018-12-19 21:30 | 320 | 319
2018-12-19 22:00 | 307 | 307
2018-12-19 22:30 | 293 | 293
2018-12-19 23:00 | 274 | 274
2018-12-19 23:30 | 263 | 262
2018-12-20 | 251 | 250
2018-12-20 00:30 | 238 | 238
2018-12-20 01:00 | 224 | 224
2018-12-20 01:30 | 227 | 227
2018-12-20 02:00 | 214 | 214
2018-12-20 02:30 | 213 | 213
2018-12-20 03:00 | 217 | 217
2018-12-20 03:30 | 216 | 215
2018-12-20 04:00 | 213 | 213
2018-12-20 04:30 | 217 | 217
2018-12-20 05:00 | 220 | 220
2018-12-20 05:30 | 225 | 224
2018-12-20 06:00 | 229 | 229
2018-12-20 06:30 | 230 | 229
2018-12-20 07:00 | 224 | 224
2018-12-20 07:30 | 220 | 219
2018-12-20 08:00 | 217 | 216
2018-12-20 08:30 | 205 | 204
2018-12-20 09:00 | 198 | 198
2018-12-20 09:30 | 199 | 198
2018-12-20 10:00 | 153 | 152
2018-12-20 10:30 | 140 | 139
2018-12-20 11:00 | 130 | 129
2018-12-20 11:30 | 140 | 139
2018-12-20 12:00 | 157 | 155
2018-12-20 12:30 | 165 | 164
2018-12-20 13:00 | 171 | 170
2018-12-20 13:30 | 170 | 169
2018-12-20 14:00 | 159 | 158
2018-12-20 14:30 | 146 | 144
2018-12-20 15:00 | 108 | 105
2018-12-20 15:30 | 86 | 81
2018-12-20 16:00 | 119 | 117
2018-12-20 16:30 | 142 | 141
2018-12-20 17:00 | 150 | 149
2018-12-20 17:30 | 180 | 179
2018-12-20 18:00 | 211 | 210
2018-12-20 18:30 | 242 | 241
2018-12-20 19:00 | 227 | 226
2018-12-20 19:30 | 214 | 214
2018-12-20 20:00 | 227 | 227
2018-12-20 20:30 | 270 | 269
2018-12-20 21:00 | 266 | 266
2018-12-20 21:30 | 233 | 233
2018-12-20 22:00 | 216 | 216
2018-12-20 22:30 | 193 | 193
2018-12-20 23:00 | 187 | 186
2018-12-20 23:30 | 178 | 177
2018-12-21 | 173 | 172
2018-12-21 00:30 | 172 | 171
2018-12-21 01:00 | 158 | 157
2018-12-21 01:30 | 158 | 157
2018-12-21 02:00 | 159 | 158
2018-12-21 02:30 | 158 | 157
2018-12-21 03:00 | 151 | 150
2018-12-21 03:30 | 150 | 149
2018-12-21 04:00 | 149 | 147
2018-12-21 04:30 | 148 | 147
2018-12-21 05:00 | 150 | 148
2018-12-21 05:30 | 152 | 151
2018-12-21 06:00 | 157 | 156
2018-12-21 06:30 | 157 | 155
2018-12-21 07:00 | 152 | 151
2018-12-21 07:30 | 135 | 133
2018-12-21 08:00 | 125 | 122
2018-12-21 08:30 | 120 | 117
2018-12-21 09:00 | 113 | 109
2018-12-21 09:30 | 103 | 100
2018-12-21 10:00 | 103 | 101
2018-12-21 10:30 | 107 | 105
2018-12-21 11:00 | 121 | 120
2018-12-21 11:30 | 138 | 137
2018-12-21 12:00 | 137 | 136
2018-12-21 12:30 | 142 | 142
2018-12-21 13:00 | 131 | 130
2018-12-21 13:30 | 123 | 122
2018-12-21 14:00 | 128 | 127
2018-12-21 14:30 | 134 | 133
2018-12-21 15:00 | 139 | 138
2018-12-21 15:30 | 145 | 144
2018-12-21 16:00 | 161 | 161
2018-12-21 16:30 | 157 | 156
2018-12-21 17:00 | 169 | 168
2018-12-21 17:30 | 186 | 185
2018-12-21 18:00 | 215 | 215
2018-12-21 18:30 | 226 | 225
2018-12-21 19:00 | 239 | 239
2018-12-21 19:30 | 242 | 241
2018-12-21 20:00 | 241 | 240
2018-12-21 20:30 | 256 | 255
2018-12-21 21:00 | 256 | 255
2018-12-21 21:30 | 255 | 255
2018-12-21 22:00 | 245 | 245
2018-12-21 22:30 | 231 | 230
2018-12-21 23:00 | 216 | 215
2018-12-21 23:30 | 224 | 223
2018-12-22 | 262 | 261
2018-12-22 00:30 | 264 | 264
2018-12-22 01:00 | 253 | 252
2018-12-22 01:30 | 243 | 243
2018-12-22 02:00 | 239 | 238
2018-12-22 02:30 | 233 | 232
2018-12-22 03:00 | 230 | 229
2018-12-22 03:30 | 227 | 227
2018-12-22 04:00 | 225 | 224
2018-12-22 04:30 | 224 | 223
2018-12-22 05:00 | 223 | 222
2018-12-22 05:30 | 224 | 223
2018-12-22 06:00 | 220 | 219
2018-12-22 06:30 | 210 | 209
2018-12-22 07:00 | 188 | 187
2018-12-22 07:30 | 184 | 184
2018-12-22 08:00 | 196 | 195
2018-12-22 08:30 | 179 | 178
2018-12-22 09:00 | 173 | 172
2018-12-22 09:30 | 152 | 151
2018-12-22 10:00 | 164 | 163
2018-12-22 10:30 | 184 | 184
2018-12-22 11:00 | 188 | 187
2018-12-22 11:30 | 170 | 169
2018-12-22 12:00 | 154 | 153
2018-12-22 12:30 | 204 | 204
2018-12-22 13:00 | 199 | 199
2018-12-22 13:30 | 197 | 196
2018-12-22 14:00 | 161 | 161
2018-12-22 14:30 | 162 | 162
2018-12-22 15:00 | 149 | 148
2018-12-22 15:30 | 144 | 143
2018-12-22 16:00 | 159 | 158
2018-12-22 16:30 | 142 | 141
2018-12-22 17:00 | 177 | 177
2018-12-22 17:30 | 219 | 219
2018-12-22 18:00 | 275 | 275
2018-12-22 18:30 | 309 | 308
2018-12-22 19:00 | 317 | 316
2018-12-22 19:30 | 308 | 307
2018-12-22 20:00 | 314 | 313
2018-12-22 20:30 | 327 | 327
2018-12-22 21:00 | 326 | 326
2018-12-22 21:30 | 317 | 317
2018-12-22 22:00 | 307 | 306
2018-12-22 22:30 | 293 | 292
2018-12-22 23:00 | 281 | 281
2018-12-22 23:30 | 270 | 270
2018-12-23 | 261 | 260
2018-12-23 00:30 | 260 | 260
2018-12-23 01:00 | 248 | 247
2018-12-23 01:30 | 238 | 238
2018-12-23 02:00 | 233 | 232
2018-12-23 02:30 | 230 | 230
2018-12-23 03:00 | 225 | 225
2018-12-23 03:30 | 222 | 222
2018-12-23 04:00 | 219 | 219
2018-12-23 04:30 | 219 | 219
2018-12-23 05:00 | 216 | 216
2018-12-23 05:30 | 219 | 218
2018-12-23 06:00 | 216 | 216
2018-12-23 06:30 | 206 | 206
2018-12-23 07:00 | 181 | 180
2018-12-23 07:30 | 169 | 169
2018-12-23 08:00 | 143 | 143
2018-12-23 08:30 | 139 | 138
2018-12-23 09:00 | 150 | 150
2018-12-23 09:30 | 141 | 141
2018-12-23 10:00 | 115 | 115
2018-12-23 10:30 | 125 | 124
2018-12-23 11:00 | 129 | 129
2018-12-23 11:30 | 121 | 120
2018-12-23 12:00 | 133 | 132
2018-12-23 12:30 | 138 | 137
2018-12-23 13:00 | 154 | 153
2018-12-23 13:30 | 147 | 146
2018-12-23 14:00 | 145 | 145
2018-12-23 14:30 | 136 | 136
2018-12-23 15:00 | 144 | 144
2018-12-23 15:30 | 154 | 153
2018-12-23 16:00 | 170 | 170
2018-12-23 16:30 | 215 | 215
2018-12-23 17:00 | 227 | 226
2018-12-23 17:30 | 259 | 258
2018-12-23 18:00 | 266 | 265
2018-12-23 18:30 | 279 | 279
2018-12-23 19:00 | 289 | 288
2018-12-23 19:30 | 294 | 294
2018-12-23 20:00 | 276 | 275
2018-12-23 20:30 | 264 | 264
2018-12-23 21:00 | 266 | 265
2018-12-23 21:30 | 262 | 261
2018-12-23 22:00 | 252 | 251
2018-12-23 22:30 | 253 | 252
2018-12-23 23:00 | 238 | 237
2018-12-23 23:30 | 222 | 222
2018-12-24 | 222 | 222
2018-12-24 00:30 | 226 | 226
2018-12-24 01:00 | 220 | 220
2018-12-24 01:30 | 217 | 216
2018-12-24 02:00 | 209 | 208
2018-12-24 02:30 | 178 | 178
2018-12-24 03:00 | 168 | 167
2018-12-24 03:30 | 171 | 170
2018-12-24 04:00 | 155 | 154
2018-12-24 04:30 | 135 | 135
2018-12-24 05:00 | 124 | 123
2018-12-24 05:30 | 124 | 123
2018-12-24 06:00 | 124 | 123
2018-12-24 06:30 | 127 | 126
2018-12-24 07:00 | 135 | 134
2018-12-24 07:30 | 131 | 130
2018-12-24 08:00 | 129 | 128
2018-12-24 08:30 | 124 | 124
2018-12-24 09:00 | 121 | 120
2018-12-24 09:30 | 130 | 129
2018-12-24 10:00 | 102 | 101
2018-12-24 10:30 | 80 | 79
2018-12-24 11:00 | 114 | 113
2018-12-24 11:30 | 103 | 102
2018-12-24 12:00 | 102 | 101
2018-12-24 12:30 | 93 | 91
2018-12-24 13:00 | 94 | 93
2018-12-24 13:30 | 111 | 110
2018-12-24 14:00 | 122 | 121
2018-12-24 14:30 | 108 | 107
2018-12-24 15:00 | 101 | 100
2018-12-24 15:30 | 76 | 75
2018-12-24 16:00 | 86 | 85
2018-12-24 16:30 | 105 | 104
2018-12-24 17:00 | 114 | 113
2018-12-24 17:30 | 129 | 128
2018-12-24 18:00 | 146 | 145
2018-12-24 18:30 | 159 | 158
2018-12-24 19:00 | 171 | 171
2018-12-24 19:30 | 173 | 172
2018-12-24 20:00 | 168 | 167
2018-12-24 20:30 | 160 | 159
2018-12-24 21:00 | 157 | 156
2018-12-24 21:30 | 156 | 155
2018-12-24 22:00 | 150 | 149
2018-12-24 22:30 | 146 | 145
2018-12-24 23:00 | 143 | 143
2018-12-24 23:30 | 134 | 133
2018-12-25 | 122 | 121
2018-12-25 00:30 | 135 | 134
2018-12-25 01:00 | 117 | 115
2018-12-25 01:30 | 103 | 102
2018-12-25 02:00 | 95 | 93
2018-12-25 02:30 | 93 | 91
2018-12-25 03:00 | 90 | 89
2018-12-25 03:30 | 90 | 88
2018-12-25 04:00 | 90 | 89
2018-12-25 04:30 | 96 | 95
2018-12-25 05:00 | 102 | 101
2018-12-25 05:30 | 97 | 96
2018-12-25 06:00 | 94 | 93
2018-12-25 06:30 | 84 | 82
2018-12-25 07:00 | 52 | 46
2018-12-25 07:30 | 49 | 42
2018-12-25 08:00 | 10 | 8
2018-12-25 08:30 | 25 | 20
2018-12-25 09:00 | 34 | 26
2018-12-25 09:30 | 5 | 4
2018-12-25 10:00 | 1 | 0
2018-12-25 10:30 | 6 | 5
2018-12-25 11:00 | 15 | 13
2018-12-25 11:30 | 3 | 2
2018-12-25 12:00 | 9 | 8
2018-12-25 12:30 | 5 | 5
2018-12-25 13:00 | 12 | 11
2018-12-25 13:30 | 10 | 9
2018-12-25 14:00 | 6 | 6
2018-12-25 14:30 | 5 | 4
2018-12-25 15:00 | 40 | 33
2018-12-25 15:30 | 60 | 54
2018-12-25 16:00 | 70 | 66
2018-12-25 16:30 | 85 | 84
2018-12-25 17:00 | 107 | 106
2018-12-25 17:30 | 135 | 134
2018-12-25 18:00 | 132 | 132
2018-12-25 18:30 | 165 | 164
2018-12-25 19:00 | 178 | 177
2018-12-25 19:30 | 185 | 184
2018-12-25 20:00 | 176 | 175
2018-12-25 20:30 | 172 | 171
2018-12-25 21:00 | 178 | 177
2018-12-25 21:30 | 162 | 160
2018-12-25 22:00 | 143 | 142
2018-12-25 22:30 | 142 | 140
2018-12-25 23:00 | 130 | 128
2018-12-25 23:30 | 122 | 121
2018-12-26 | 119 | 118
2018-12-26 00:30 | 130 | 130
2018-12-26 01:00 | 123 | 122
2018-12-26 01:30 | 111 | 110
2018-12-26 02:00 | 109 | 108
2018-12-26 02:30 | 100 | 99
2018-12-26 03:00 | 96 | 95
2018-12-26 03:30 | 90 | 89
2018-12-26 04:00 | 96 | 94
2018-12-26 04:30 | 96 | 95
2018-12-26 05:00 | 110 | 109
2018-12-26 05:30 | 99 | 98
2018-12-26 06:00 | 94 | 92
2018-12-26 06:30 | 95 | 94
2018-12-26 07:00 | 62 | 57
2018-12-26 07:30 | 40 | 34
2018-12-26 08:00 | 32 | 29
2018-12-26 08:30 | 13 | 12
2018-12-26 09:00 | 2 | 2
2018-12-26 09:30 | 6 | 6
2018-12-26 10:00 | 18 | 17
2018-12-26 10:30 | 21 | 17
2018-12-26 11:00 | 34 | 31
2018-12-26 11:30 | 38 | 34
2018-12-26 12:00 | 24 | 20
2018-12-26 12:30 | 46 | 41
2018-12-26 13:00 | 61 | 54
2018-12-26 13:30 | 37 | 33
2018-12-26 14:00 | 42 | 38
2018-12-26 14:30 | 65 | 59
2018-12-26 15:00 | 59 | 55
2018-12-26 15:30 | 59 | 55
2018-12-26 16:00 | 76 | 74
2018-12-26 16:30 | 86 | 84
2018-12-26 17:00 | 116 | 115
2018-12-26 17:30 | 144 | 143
2018-12-26 18:00 | 175 | 175
2018-12-26 18:30 | 212 | 211
2018-12-26 19:00 | 220 | 219
2018-12-26 19:30 | 233 | 232
2018-12-26 20:00 | 215 | 214
2018-12-26 20:30 | 197 | 196
2018-12-26 21:00 | 183 | 182
2018-12-26 21:30 | 164 | 163
2018-12-26 22:00 | 170 | 169
2018-12-26 22:30 | 168 | 167
2018-12-26 23:00 | 158 | 158
2018-12-26 23:30 | 153 | 152
2018-12-27 | 141 | 140
2018-12-27 00:30 | 147 | 146
2018-12-27 01:00 | 141 | 141
2018-12-27 01:30 | 132 | 132
2018-12-27 02:00 | 138 | 137
2018-12-27 02:30 | 154 | 154
2018-12-27 03:00 | 140 | 139
2018-12-27 03:30 | 131 | 130
2018-12-27 04:00 | 135 | 134
2018-12-27 04:30 | 128 | 128
2018-12-27 05:00 | 119 | 118
2018-12-27 05:30 | 120 | 119
2018-12-27 06:00 | 119 | 118
2018-12-27 06:30 | 123 | 122
2018-12-27 07:00 | 108 | 107
2018-12-27 07:30 | 86 | 85
2018-12-27 08:00 | 60 | 54
2018-12-27 08:30 | 64 | 59
2018-12-27 09:00 | 59 | 53
2018-12-27 09:30 | 65 | 61
2018-12-27 10:00 | 74 | 72
2018-12-27 10:30 | 62 | 58
2018-12-27 11:00 | 44 | 37
2018-12-27 11:30 | 37 | 33
2018-12-27 12:00 | 43 | 38
2018-12-27 12:30 | 54 | 51
2018-12-27 13:00 | 44 | 37
2018-12-27 13:30 | 25 | 20
2018-12-27 14:00 | 10 | 8
2018-12-27 14:30 | 31 | 24
2018-12-27 15:00 | 34 | 26
2018-12-27 15:30 | 59 | 54
2018-12-27 16:00 | 74 | 72
2018-12-27 16:30 | 80 | 78
2018-12-27 17:00 | 117 | 116
2018-12-27 17:30 | 159 | 159
2018-12-27 18:00 | 170 | 169
2018-12-27 18:30 | 181 | 180
2018-12-27 19:00 | 191 | 190
2018-12-27 19:30 | 199 | 198
2018-12-27 20:00 | 201 | 200
2018-12-27 20:30 | 195 | 195
2018-12-27 21:00 | 189 | 188
2018-12-27 21:30 | 177 | 177
2018-12-27 22:00 | 167 | 166
2018-12-27 22:30 | 159 | 158
2018-12-27 23:00 | 154 | 153
2018-12-27 23:30 | 144 | 142
2018-12-28 | 136 | 135
2018-12-28 00:30 | 135 | 134
2018-12-28 01:00 | 122 | 121
2018-12-28 01:30 | 114 | 113
2018-12-28 02:00 | 109 | 107
2018-12-28 02:30 | 105 | 104
2018-12-28 03:00 | 106 | 104
2018-12-28 03:30 | 107 | 106
2018-12-28 04:00 | 110 | 109
2018-12-28 04:30 | 111 | 110
2018-12-28 05:00 | 113 | 112
2018-12-28 05:30 | 113 | 112
2018-12-28 06:00 | 115 | 114
2018-12-28 06:30 | 103 | 101
2018-12-28 07:00 | 75 | 72
2018-12-28 07:30 | 50 | 43
2018-12-28 08:00 | 16 | 13
2018-12-28 08:30 | 0 | 0
2018-12-28 09:00 | 1 | 1
2018-12-28 09:30 | 10 | 9
2018-12-28 10:00 | 7 | 7
2018-12-28 10:30 | 6 | 5
2018-12-28 11:00 | 8 | 7
2018-12-28 11:30 | 27 | 22
2018-12-28 12:00 | 31 | 27
2018-12-28 12:30 | 39 | 33
2018-12-28 13:00 | 33 | 28
2018-12-28 13:30 | 27 | 23
2018-12-28 14:00 | 38 | 32
2018-12-28 14:30 | 20 | 18
2018-12-28 15:00 | 10 | 9
2018-12-28 15:30 | 5 | 4
2018-12-28 16:00 | 11 | 10
2018-12-28 16:30 | 12 | 10
2018-12-28 17:00 | 19 | 15
2018-12-28 17:30 | 53 | 49
2018-12-28 18:00 | 92 | 91
2018-12-28 18:30 | 118 | 118
2018-12-28 19:00 | 134 | 133
2018-12-28 19:30 | 138 | 137
2018-12-28 20:00 | 159 | 159
2018-12-28 20:30 | 166 | 165
2018-12-28 21:00 | 154 | 154
2018-12-28 21:30 | 172 | 172
2018-12-28 22:00 | 156 | 156
2018-12-28 22:30 | 133 | 132
2018-12-28 23:00 | 152 | 151
2018-12-28 23:30 | 147 | 146
2018-12-29 | 148 | 148
2018-12-29 00:30 | 147 | 147
2018-12-29 01:00 | 131 | 130
2018-12-29 01:30 | 123 | 122
2018-12-29 02:00 | 117 | 116
2018-12-29 02:30 | 113 | 111
2018-12-29 03:00 | 112 | 111
2018-12-29 03:30 | 114 | 113
2018-12-29 04:00 | 109 | 108
2018-12-29 04:30 | 113 | 112
2018-12-29 05:00 | 113 | 112
2018-12-29 05:30 | 115 | 114
2018-12-29 06:00 | 110 | 109
2018-12-29 06:30 | 99 | 97
2018-12-29 07:00 | 88 | 84
2018-12-29 07:30 | 87 | 84
2018-12-29 08:00 | 69 | 63
2018-12-29 08:30 | 87 | 84
2018-12-29 09:00 | 68 | 63
2018-12-29 09:30 | 36 | 31
2018-12-29 10:00 | 59 | 53
2018-12-29 10:30 | 39 | 33
2018-12-29 11:00 | 59 | 53
2018-12-29 11:30 | 61 | 54
2018-12-29 12:00 | 69 | 62
2018-12-29 12:30 | 22 | 19
2018-12-29 13:00 | 38 | 32
2018-12-29 13:30 | 28 | 25
2018-12-29 14:00 | 40 | 35
2018-12-29 14:30 | 59 | 51
2018-12-29 15:00 | 59 | 54
2018-12-29 15:30 | 68 | 62
2018-12-29 16:00 | 76 | 71
2018-12-29 16:30 | 99 | 97
2018-12-29 17:00 | 143 | 142
2018-12-29 17:30 | 161 | 160
2018-12-29 18:00 | 171 | 171
2018-12-29 18:30 | 186 | 186
2018-12-29 19:00 | 212 | 211
2018-12-29 19:30 | 211 | 210
2018-12-29 20:00 | 207 | 207
2018-12-29 20:30 | 203 | 202
2018-12-29 21:00 | 203 | 202
2018-12-29 21:30 | 181 | 180
2018-12-29 22:00 | 174 | 173
2018-12-29 22:30 | 169 | 168
2018-12-29 23:00 | 147 | 146
2018-12-29 23:30 | 145 | 144
2018-12-30 | 126 | 125
2018-12-30 00:30 | 125 | 124
2018-12-30 01:00 | 116 | 114
2018-12-30 01:30 | 112 | 111
2018-12-30 02:00 | 117 | 116
2018-12-30 02:30 | 124 | 123
2018-12-30 03:00 | 111 | 110
2018-12-30 03:30 | 112 | 110
2018-12-30 04:00 | 112 | 111
2018-12-30 04:30 | 115 | 114
2018-12-30 05:00 | 115 | 114
2018-12-30 05:30 | 113 | 112
2018-12-30 06:00 | 115 | 114
2018-12-30 06:30 | 102 | 101
2018-12-30 07:00 | 96 | 94
2018-12-30 07:30 | 81 | 79
2018-12-30 08:00 | 71 | 68
2018-12-30 08:30 | 64 | 61
2018-12-30 09:00 | 67 | 64
2018-12-30 09:30 | 59 | 55
2018-12-30 10:00 | 41 | 36
2018-12-30 10:30 | 40 | 34
2018-12-30 11:00 | 28 | 23
2018-12-30 11:30 | 13 | 11
2018-12-30 12:00 | 6 | 5
2018-12-30 12:30 | 2 | 2
2018-12-30 13:00 | 2 | 2
2018-12-30 13:30 | 6 | 6
2018-12-30 14:00 | 1 | 1
2018-12-30 14:30 | 2 | 2
2018-12-30 15:00 | 2 | 2
2018-12-30 15:30 | 30 | 23
2018-12-30 16:00 | 43 | 36
2018-12-30 16:30 | 52 | 46
2018-12-30 17:00 | 65 | 62
2018-12-30 17:30 | 66 | 63
2018-12-30 18:00 | 73 | 71
2018-12-30 18:30 | 100 | 100
2018-12-30 19:00 | 118 | 118
2018-12-30 19:30 | 143 | 142
2018-12-30 20:00 | 131 | 131
2018-12-30 20:30 | 190 | 189
2018-12-30 21:00 | 193 | 192
2018-12-30 21:30 | 183 | 182
2018-12-30 22:00 | 173 | 172
2018-12-30 22:30 | 165 | 164
2018-12-30 23:00 | 158 | 157
2018-12-30 23:30 | 148 | 147
2018-12-31 | 145 | 144
2018-12-31 00:30 | 145 | 144
2018-12-31 01:00 | 132 | 130
2018-12-31 01:30 | 127 | 125
2018-12-31 02:00 | 117 | 115
2018-12-31 02:30 | 117 | 115
2018-12-31 03:00 | 118 | 116
2018-12-31 03:30 | 105 | 104
2018-12-31 04:00 | 107 | 106
2018-12-31 04:30 | 110 | 109
2018-12-31 05:00 | 108 | 107
2018-12-31 05:30 | 109 | 108
2018-12-31 06:00 | 112 | 111
2018-12-31 06:30 | 106 | 105
2018-12-31 07:00 | 98 | 96
2018-12-31 07:30 | 81 | 79
2018-12-31 08:00 | 80 | 78
2018-12-31 08:30 | 87 | 85
2018-12-31 09:00 | 89 | 88
2018-12-31 09:30 | 68 | 65
2018-12-31 10:00 | 58 | 52
2018-12-31 10:30 | 62 | 57
2018-12-31 11:00 | 33 | 30
2018-12-31 11:30 | 4 | 3
2018-12-31 12:00 | 6 | 5
2018-12-31 12:30 | 3 | 3
2018-12-31 13:00 | 2 | 2
2018-12-31 13:30 | 1 | 1
2018-12-31 14:00 | 2 | 2
2018-12-31 14:30 | 6 | 6
2018-12-31 15:00 | 1 | 1
2018-12-31 15:30 | 47 | 42
2018-12-31 16:00 | 62 | 58
2018-12-31 16:30 | 63 | 58
2018-12-31 17:00 | 95 | 93
2018-12-31 17:30 | 126 | 126
2018-12-31 18:00 | 147 | 146
2018-12-31 18:30 | 173 | 172
2018-12-31 19:00 | 179 | 178
2018-12-31 19:30 | 179 | 179
2018-12-31 20:00 | 177 | 176
2018-12-31 20:30 | 169 | 169
2018-12-31 21:00 | 168 | 167
2018-12-31 21:30 | 154 | 153
2018-12-31 22:00 | 148 | 148
2018-12-31 22:30 | 142 | 141
2018-12-31 23:00 | 138 | 137
2018-12-31 23:30 | 133 | 132
2019-01-01 | 135 | 134
2019-01-01 00:30 | 140 | 139
2019-01-01 01:00 | 124 | 123
2019-01-01 01:30 | 114 | 112
2019-01-01 02:00 | 106 | 105
2019-01-01 02:30 | 99 | 97
2019-01-01 03:00 | 90 | 88
2019-01-01 03:30 | 89 | 87
2019-01-01 04:00 | 86 | 84
2019-01-01 04:30 | 85 | 83
2019-01-01 05:00 | 86 | 85
2019-01-01 05:30 | 90 | 89
2019-01-01 06:00 | 90 | 88
2019-01-01 06:30 | 73 | 69
2019-01-01 07:00 | 43 | 38
2019-01-01 07:30 | 6 | 5
2019-01-01 08:00 | 7 | 5
2019-01-01 08:30 | 6 | 5
2019-01-01 09:00 | 13 | 10
2019-01-01 09:30 | 37 | 29
2019-01-01 10:00 | 9 | 8
2019-01-01 10:30 | 12 | 10
2019-01-01 11:00 | 8 | 6
2019-01-01 11:30 | 10 | 9
2019-01-01 12:00 | 10 | 8
2019-01-01 12:30 | 28 | 22
2019-01-01 13:00 | 15 | 11
2019-01-01 13:30 | 21 | 16
2019-01-01 14:00 | 4 | 2
2019-01-01 14:30 | 2 | 0
2019-01-01 15:00 | 6 | 6
2019-01-01 15:30 | 1 | 0
2019-01-01 16:00 | 7 | 6
2019-01-01 16:30 | 32 | 26
2019-01-01 17:00 | 72 | 70
2019-01-01 17:30 | 128 | 127
2019-01-01 18:00 | 149 | 148
2019-01-01 18:30 | 180 | 179
2019-01-01 19:00 | 201 | 200
2019-01-01 19:30 | 215 | 214
2019-01-01 20:00 | 207 | 206
2019-01-01 20:30 | 197 | 196
2019-01-01 21:00 | 185 | 184
2019-01-01 21:30 | 168 | 167
2019-01-01 22:00 | 157 | 156
2019-01-01 22:30 | 146 | 144
2019-01-01 23:00 | 138 | 137
2019-01-01 23:30 | 133 | 132
2019-01-02 | 127 | 125
2019-01-02 00:30 | 135 | 134
2019-01-02 01:00 | 121 | 120
2019-01-02 01:30 | 114 | 112
2019-01-02 02:00 | 112 | 111
2019-01-02 02:30 | 106 | 104
2019-01-02 03:00 | 102 | 100
2019-01-02 03:30 | 107 | 106
2019-01-02 04:00 | 110 | 109
2019-01-02 04:30 | 115 | 114
2019-01-02 05:00 | 111 | 109
2019-01-02 05:30 | 108 | 107
2019-01-02 06:00 | 105 | 103
2019-01-02 06:30 | 112 | 110
2019-01-02 07:00 | 80 | 78
2019-01-02 07:30 | 58 | 55
2019-01-02 08:00 | 36 | 28
2019-01-02 08:30 | 26 | 19
2019-01-02 09:00 | 10 | 8
2019-01-02 09:30 | 4 | 2
2019-01-02 10:00 | 10 | 7
2019-01-02 10:30 | 8 | 5
2019-01-02 11:00 | 20 | 16
2019-01-02 11:30 | 17 | 14
2019-01-02 12:00 | 4 | 1
2019-01-02 12:30 | 34 | 28
2019-01-02 13:00 | 63 | 53
2019-01-02 13:30 | 79 | 69
2019-01-02 14:00 | 66 | 58
2019-01-02 14:30 | 35 | 29
2019-01-02 15:00 | 35 | 27
2019-01-02 15:30 | 22 | 16
2019-01-02 16:00 | 15 | 11
2019-01-02 16:30 | 50 | 47
2019-01-02 17:00 | 29 | 21
2019-01-02 17:30 | 68 | 66
2019-01-02 18:00 | 108 | 107
2019-01-02 18:30 | 133 | 132
2019-01-02 19:00 | 160 | 159
2019-01-02 19:30 | 198 | 197
2019-01-02 20:00 | 187 | 186
2019-01-02 20:30 | 174 | 173
2019-01-02 21:00 | 200 | 199
2019-01-02 21:30 | 192 | 191
2019-01-02 22:00 | 216 | 215
2019-01-02 22:30 | 208 | 207
2019-01-02 23:00 | 188 | 187
2019-01-02 23:30 | 170 | 168
2019-01-03 | 151 | 149
2019-01-03 00:30 | 157 | 156
2019-01-03 01:00 | 153 | 152
2019-01-03 01:30 | 135 | 134
2019-01-03 02:00 | 107 | 105
2019-01-03 02:30 | 102 | 100
2019-01-03 03:00 | 111 | 109
2019-01-03 03:30 | 112 | 111
2019-01-03 04:00 | 114 | 112
2019-01-03 04:30 | 117 | 116
2019-01-03 05:00 | 116 | 115
2019-01-03 05:30 | 130 | 129
2019-01-03 06:00 | 139 | 138
2019-01-03 06:30 | 142 | 141
2019-01-03 07:00 | 118 | 117
2019-01-03 07:30 | 94 | 93
2019-01-03 08:00 | 70 | 67
2019-01-03 08:30 | 55 | 52
2019-01-03 09:00 | 50 | 44
2019-01-03 09:30 | 42 | 35
2019-01-03 10:00 | 40 | 32
2019-01-03 10:30 | 38 | 30
2019-01-03 11:00 | 37 | 29
2019-01-03 11:30 | 41 | 33
2019-01-03 12:00 | 46 | 41
2019-01-03 12:30 | 63 | 61
2019-01-03 13:00 | 59 | 56
2019-01-03 13:30 | 62 | 59
2019-01-03 14:00 | 60 | 57
2019-01-03 14:30 | 49 | 43
2019-01-03 15:00 | 63 | 60
2019-01-03 15:30 | 80 | 79
2019-01-03 16:00 | 88 | 86
2019-01-03 16:30 | 114 | 113
2019-01-03 17:00 | 137 | 137
2019-01-03 17:30 | 177 | 176
2019-01-03 18:00 | 197 | 196
2019-01-03 18:30 | 232 | 231
2019-01-03 19:00 | 242 | 241
2019-01-03 19:30 | 250 | 249
2019-01-03 20:00 | 245 | 245
2019-01-03 20:30 | 237 | 236
2019-01-03 21:00 | 222 | 221
2019-01-03 21:30 | 204 | 203
2019-01-03 22:00 | 190 | 189
2019-01-03 22:30 | 173 | 172
2019-01-03 23:00 | 165 | 164
2019-01-03 23:30 | 160 | 159
2019-01-04 | 165 | 164
2019-01-04 00:30 | 170 | 169
2019-01-04 01:00 | 156 | 155
2019-01-04 01:30 | 157 | 156
2019-01-04 02:00 | 160 | 159
2019-01-04 02:30 | 157 | 156
2019-01-04 03:00 | 153 | 152
2019-01-04 03:30 | 151 | 150
2019-01-04 04:00 | 148 | 147
2019-01-04 04:30 | 161 | 160
2019-01-04 05:00 | 164 | 164
2019-01-04 05:30 | 152 | 151
2019-01-04 06:00 | 151 | 150
2019-01-04 06:30 | 153 | 152
2019-01-04 07:00 | 132 | 131
2019-01-04 07:30 | 108 | 107
2019-01-04 08:00 | 85 | 83
2019-01-04 08:30 | 78 | 74
2019-01-04 09:00 | 98 | 96
2019-01-04 09:30 | 86 | 84
2019-01-04 10:00 | 80 | 76
2019-01-04 10:30 | 89 | 87
2019-01-04 11:00 | 85 | 83
2019-01-04 11:30 | 90 | 88
2019-01-04 12:00 | 100 | 98
2019-01-04 12:30 | 75 | 72
2019-01-04 13:00 | 52 | 45
2019-01-04 13:30 | 20 | 17
2019-01-04 14:00 | 39 | 31
2019-01-04 14:30 | 39 | 31
2019-01-04 15:00 | 28 | 24
2019-01-04 15:30 | 8 | 7
2019-01-04 16:00 | 28 | 23
2019-01-04 16:30 | 62 | 57
2019-01-04 17:00 | 74 | 71
2019-01-04 17:30 | 90 | 88
2019-01-04 18:00 | 134 | 133
2019-01-04 18:30 | 167 | 167
2019-01-04 19:00 | 172 | 172
2019-01-04 19:30 | 167 | 166
2019-01-04 20:00 | 176 | 175
2019-01-04 20:30 | 194 | 193
2019-01-04 21:00 | 220 | 219
2019-01-04 21:30 | 212 | 211
2019-01-04 22:00 | 193 | 192
2019-01-04 22:30 | 180 | 180
2019-01-04 23:00 | 171 | 170
2019-01-04 23:30 | 161 | 160
2019-01-05 | 157 | 156
2019-01-05 00:30 | 168 | 167
2019-01-05 01:00 | 160 | 159
2019-01-05 01:30 | 161 | 160
2019-01-05 02:00 | 160 | 159
2019-01-05 02:30 | 156 | 156
2019-01-05 03:00 | 153 | 153
2019-01-05 03:30 | 151 | 150
2019-01-05 04:00 | 146 | 145
2019-01-05 04:30 | 148 | 147
2019-01-05 05:00 | 156 | 155
2019-01-05 05:30 | 163 | 162
2019-01-05 06:00 | 164 | 164
2019-01-05 06:30 | 153 | 152
2019-01-05 07:00 | 133 | 133
2019-01-05 07:30 | 108 | 108
2019-01-05 08:00 | 89 | 87
2019-01-05 08:30 | 74 | 72
2019-01-05 09:00 | 67 | 63
2019-01-05 09:30 | 66 | 62
2019-01-05 10:00 | 79 | 77
2019-01-05 10:30 | 61 | 58
2019-01-05 11:00 | 64 | 60
2019-01-05 11:30 | 84 | 82
2019-01-05 12:00 | 89 | 88
2019-01-05 12:30 | 82 | 80
2019-01-05 13:00 | 67 | 62
2019-01-05 13:30 | 55 | 49
2019-01-05 14:00 | 89 | 87
2019-01-05 14:30 | 79 | 77
2019-01-05 15:00 | 83 | 82
2019-01-05 15:30 | 70 | 67
2019-01-05 16:00 | 83 | 81
2019-01-05 16:30 | 102 | 101
2019-01-05 17:00 | 120 | 119
2019-01-05 17:30 | 153 | 152
2019-01-05 18:00 | 197 | 196
2019-01-05 18:30 | 222 | 221
2019-01-05 19:00 | 237 | 236
2019-01-05 19:30 | 237 | 236
2019-01-05 20:00 | 243 | 242
2019-01-05 20:30 | 241 | 240
2019-01-05 21:00 | 226 | 225
2019-01-05 21:30 | 211 | 210
2019-01-05 22:00 | 201 | 201
2019-01-05 22:30 | 204 | 203
2019-01-05 23:00 | 200 | 199
2019-01-05 23:30 | 187 | 186
2019-01-06 | 172 | 171
2019-01-06 00:30 | 163 | 162
2019-01-06 01:00 | 162 | 161
2019-01-06 01:30 | 168 | 167
2019-01-06 02:00 | 167 | 166
2019-01-06 02:30 | 180 | 178
2019-01-06 03:00 | 198 | 197
2019-01-06 03:30 | 204 | 203
2019-01-06 04:00 | 202 | 201
2019-01-06 04:30 | 202 | 201
2019-01-06 05:00 | 202 | 201
2019-01-06 05:30 | 205 | 204
2019-01-06 06:00 | 201 | 199
2019-01-06 06:30 | 182 | 181
2019-01-06 07:00 | 153 | 151
2019-01-06 07:30 | 107 | 105
2019-01-06 08:00 | 72 | 70
2019-01-06 08:30 | 58 | 55
2019-01-06 09:00 | 62 | 59
2019-01-06 09:30 | 46 | 40
2019-01-06 10:00 | 42 | 34
2019-01-06 10:30 | 37 | 30
2019-01-06 11:00 | 43 | 35
2019-01-06 11:30 | 39 | 32
2019-01-06 12:00 | 58 | 53
2019-01-06 12:30 | 44 | 37
2019-01-06 13:00 | 49 | 43
2019-01-06 13:30 | 68 | 66
2019-01-06 14:00 | 54 | 51
2019-01-06 14:30 | 53 | 49
2019-01-06 15:00 | 60 | 57
2019-01-06 15:30 | 84 | 82
2019-01-06 16:00 | 101 | 100
2019-01-06 16:30 | 116 | 115
2019-01-06 17:00 | 147 | 146
2019-01-06 17:30 | 191 | 190
2019-01-06 18:00 | 227 | 226
2019-01-06 18:30 | 262 | 261
2019-01-06 19:00 | 277 | 275
2019-01-06 19:30 | 285 | 283
2019-01-06 20:00 | 296 | 295
2019-01-06 20:30 | 299 | 297
2019-01-06 21:00 | 285 | 283
2019-01-06 21:30 | 272 | 270
2019-01-06 22:00 | 261 | 259
2019-01-06 22:30 | 241 | 240
2019-01-06 23:00 | 224 | 223
2019-01-06 23:30 | 217 | 215
2019-01-07 | 213 | 212
2019-01-07 00:30 | 211 | 210
2019-01-07 01:00 | 202 | 200
2019-01-07 01:30 | 196 | 194
2019-01-07 02:00 | 193 | 192
2019-01-07 02:30 | 191 | 190
2019-01-07 03:00 | 188 | 187
2019-01-07 03:30 | 188 | 187
2019-01-07 04:00 | 186 | 185
2019-01-07 04:30 | 188 | 186
2019-01-07 05:00 | 186 | 184
2019-01-07 05:30 | 191 | 189
2019-01-07 06:00 | 194 | 193
2019-01-07 06:30 | 186 | 185
2019-01-07 07:00 | 176 | 175
2019-01-07 07:30 | 147 | 146
2019-01-07 08:00 | 129 | 128
2019-01-07 08:30 | 106 | 105
2019-01-07 09:00 | 108 | 107
2019-01-07 09:30 | 96 | 94
2019-01-07 10:00 | 74 | 73
2019-01-07 10:30 | 84 | 83
2019-01-07 11:00 | 91 | 90
2019-01-07 11:30 | 89 | 88
2019-01-07 12:00 | 92 | 91
2019-01-07 12:30 | 116 | 115
2019-01-07 13:00 | 94 | 93
2019-01-07 13:30 | 93 | 91
2019-01-07 14:00 | 108 | 107
2019-01-07 14:30 | 122 | 121
2019-01-07 15:00 | 119 | 118
2019-01-07 15:30 | 120 | 119
2019-01-07 16:00 | 128 | 127
2019-01-07 16:30 | 174 | 173
2019-01-07 17:00 | 180 | 179
2019-01-07 17:30 | 158 | 157
2019-01-07 18:00 | 167 | 166
2019-01-07 18:30 | 187 | 186
2019-01-07 19:00 | 201 | 200
2019-01-07 19:30 | 209 | 208
2019-01-07 20:00 | 213 | 212
2019-01-07 20:30 | 204 | 203
2019-01-07 21:00 | 223 | 222
2019-01-07 21:30 | 259 | 258
2019-01-07 22:00 | 253 | 252
2019-01-07 22:30 | 247 | 246
2019-01-07 23:00 | 243 | 242
2019-01-07 23:30 | 244 | 243
2019-01-08 | 239 | 239
2019-01-08 00:30 | 240 | 239
2019-01-08 01:00 | 225 | 224
2019-01-08 01:30 | 215 | 214
2019-01-08 02:00 | 211 | 210
2019-01-08 02:30 | 209 | 208
2019-01-08 03:00 | 207 | 206
2019-01-08 03:30 | 203 | 202
2019-01-08 04:00 | 201 | 200
2019-01-08 04:30 | 203 | 202
2019-01-08 05:00 | 204 | 203
2019-01-08 05:30 | 210 | 209
2019-01-08 06:00 | 212 | 211
2019-01-08 06:30 | 216 | 215
2019-01-08 07:00 | 199 | 198
2019-01-08 07:30 | 174 | 173
2019-01-08 08:00 | 138 | 137
2019-01-08 08:30 | 118 | 117
2019-01-08 09:00 | 92 | 90
2019-01-08 09:30 | 81 | 80
2019-01-08 10:00 | 64 | 62
2019-01-08 10:30 | 72 | 70
2019-01-08 11:00 | 84 | 83
2019-01-08 11:30 | 90 | 89
2019-01-08 12:00 | 93 | 92
2019-01-08 12:30 | 103 | 102
2019-01-08 13:00 | 119 | 118
2019-01-08 13:30 | 113 | 112
2019-01-08 14:00 | 107 | 106
2019-01-08 14:30 | 111 | 110
2019-01-08 15:00 | 99 | 98
2019-01-08 15:30 | 75 | 73
2019-01-08 16:00 | 96 | 95
2019-01-08 16:30 | 100 | 99
2019-01-08 17:00 | 121 | 120
2019-01-08 17:30 | 135 | 134
2019-01-08 18:00 | 173 | 172
2019-01-08 18:30 | 201 | 200
2019-01-08 19:00 | 220 | 219
2019-01-08 19:30 | 228 | 227
2019-01-08 20:00 | 225 | 224
2019-01-08 20:30 | 215 | 214
2019-01-08 21:00 | 205 | 204
2019-01-08 21:30 | 236 | 235
2019-01-08 22:00 | 271 | 271
2019-01-08 22:30 | 274 | 273
2019-01-08 23:00 | 260 | 259
2019-01-08 23:30 | 249 | 247
2019-01-09 | 234 | 232
2019-01-09 00:30 | 234 | 233
2019-01-09 01:00 | 217 | 215
2019-01-09 01:30 | 214 | 213
2019-01-09 02:00 | 212 | 210
2019-01-09 02:30 | 208 | 206
2019-01-09 03:00 | 206 | 204
2019-01-09 03:30 | 209 | 207
2019-01-09 04:00 | 203 | 202
2019-01-09 04:30 | 198 | 197
2019-01-09 05:00 | 200 | 199
2019-01-09 05:30 | 205 | 204
2019-01-09 06:00 | 206 | 205
2019-01-09 06:30 | 205 | 204
2019-01-09 07:00 | 202 | 201
2019-01-09 07:30 | 200 | 199
2019-01-09 08:00 | 168 | 167
2019-01-09 08:30 | 144 | 143
2019-01-09 09:00 | 116 | 115
2019-01-09 09:30 | 107 | 106
2019-01-09 10:00 | 76 | 75
2019-01-09 10:30 | 79 | 77
2019-01-09 11:00 | 83 | 82
2019-01-09 11:30 | 93 | 92
2019-01-09 12:00 | 99 | 98
2019-01-09 12:30 | 126 | 125
2019-01-09 13:00 | 117 | 116
2019-01-09 13:30 | 160 | 159
2019-01-09 14:00 | 152 | 151
2019-01-09 14:30 | 150 | 149
2019-01-09 15:00 | 129 | 128
2019-01-09 15:30 | 130 | 128
2019-01-09 16:00 | 157 | 155
2019-01-09 16:30 | 163 | 162
2019-01-09 17:00 | 164 | 162
2019-01-09 17:30 | 171 | 170
2019-01-09 18:00 | 192 | 191
2019-01-09 18:30 | 204 | 203
2019-01-09 19:00 | 215 | 214
2019-01-09 19:30 | 236 | 235
2019-01-09 20:00 | 254 | 253
2019-01-09 20:30 | 247 | 245
2019-01-09 21:00 | 245 | 243
2019-01-09 21:30 | 272 | 271
2019-01-09 22:00 | 277 | 275
2019-01-09 22:30 | 262 | 260
2019-01-09 23:00 | 251 | 250
2019-01-09 23:30 | 238 | 237
2019-01-10 | 232 | 231
2019-01-10 00:30 | 230 | 229
2019-01-10 01:00 | 219 | 218
2019-01-10 01:30 | 214 | 213
2019-01-10 02:00 | 207 | 205
2019-01-10 02:30 | 201 | 200
2019-01-10 03:00 | 197 | 196
2019-01-10 03:30 | 188 | 187
2019-01-10 04:00 | 183 | 181
2019-01-10 04:30 | 180 | 179
2019-01-10 05:00 | 181 | 179
2019-01-10 05:30 | 187 | 186
2019-01-10 06:00 | 189 | 188
2019-01-10 06:30 | 194 | 193
2019-01-10 07:00 | 187 | 186
2019-01-10 07:30 | 205 | 204
2019-01-10 08:00 | 219 | 218
2019-01-10 08:30 | 221 | 220
2019-01-10 09:00 | 219 | 218
2019-01-10 09:30 | 215 | 214
2019-01-10 10:00 | 210 | 209
2019-01-10 10:30 | 207 | 206
2019-01-10 11:00 | 206 | 205
2019-01-10 11:30 | 199 | 197
2019-01-10 12:00 | 201 | 200
2019-01-10 12:30 | 202 | 200
2019-01-10 13:00 | 193 | 192
2019-01-10 13:30 | 208 | 206
2019-01-10 14:00 | 203 | 202
2019-01-10 14:30 | 211 | 210
2019-01-10 15:00 | 204 | 203
2019-01-10 15:30 | 202 | 200
2019-01-10 16:00 | 209 | 207
2019-01-10 16:30 | 188 | 187
2019-01-10 17:00 | 197 | 196
2019-01-10 17:30 | 200 | 198
2019-01-10 18:00 | 219 | 217
2019-01-10 18:30 | 232 | 230
2019-01-10 19:00 | 242 | 240
2019-01-10 19:30 | 242 | 239
2019-01-10 20:00 | 246 | 244
2019-01-10 20:30 | 253 | 251
2019-01-10 21:00 | 242 | 239
2019-01-10 21:30 | 233 | 231
2019-01-10 22:00 | 222 | 220
2019-01-10 22:30 | 193 | 191
2019-01-10 23:00 | 190 | 187
2019-01-10 23:30 | 187 | 184
2019-01-11 | 177 | 175
2019-01-11 00:30 | 191 | 189
2019-01-11 01:00 | 182 | 181
2019-01-11 01:30 | 174 | 173
2019-01-11 02:00 | 170 | 169
2019-01-11 02:30 | 166 | 164
2019-01-11 03:00 | 161 | 159
2019-01-11 03:30 | 158 | 157
2019-01-11 04:00 | 155 | 154
2019-01-11 04:30 | 155 | 153
2019-01-11 05:00 | 145 | 144
2019-01-11 05:30 | 144 | 143
2019-01-11 06:00 | 150 | 148
2019-01-11 06:30 | 160 | 159
2019-01-11 07:00 | 159 | 157
2019-01-11 07:30 | 156 | 155
2019-01-11 08:00 | 154 | 153
2019-01-11 08:30 | 154 | 153
2019-01-11 09:00 | 148 | 147
2019-01-11 09:30 | 151 | 150
2019-01-11 10:00 | 120 | 119
2019-01-11 10:30 | 105 | 104
2019-01-11 11:00 | 88 | 86
2019-01-11 11:30 | 88 | 86
2019-01-11 12:00 | 95 | 93
2019-01-11 12:30 | 95 | 93
2019-01-11 13:00 | 103 | 101
2019-01-11 13:30 | 65 | 63
2019-01-11 14:00 | 59 | 57
2019-01-11 14:30 | 44 | 41
2019-01-11 15:00 | 28 | 20
2019-01-11 15:30 | 35 | 29
2019-01-11 16:00 | 39 | 36
2019-01-11 16:30 | 66 | 64
2019-01-11 17:00 | 103 | 102
2019-01-11 17:30 | 109 | 107
2019-01-11 18:00 | 116 | 114
2019-01-11 18:30 | 136 | 134
2019-01-11 19:00 | 144 | 142
2019-01-11 19:30 | 162 | 161
2019-01-11 20:00 | 179 | 178
2019-01-11 20:30 | 176 | 174
2019-01-11 21:00 | 150 | 148
2019-01-11 21:30 | 134 | 132
2019-01-11 22:00 | 174 | 172
2019-01-11 22:30 | 190 | 189
2019-01-11 23:00 | 183 | 181
2019-01-11 23:30 | 165 | 163
2019-01-12 | 163 | 161
2019-01-12 00:30 | 171 | 169
2019-01-12 01:00 | 162 | 160
2019-01-12 01:30 | 150 | 148
2019-01-12 02:00 | 141 | 139
2019-01-12 02:30 | 142 | 140
2019-01-12 03:00 | 149 | 147
2019-01-12 03:30 | 150 | 148
2019-01-12 04:00 | 145 | 143
2019-01-12 04:30 | 130 | 128
2019-01-12 05:00 | 126 | 124
2019-01-12 05:30 | 125 | 123
2019-01-12 06:00 | 123 | 120
2019-01-12 06:30 | 111 | 109
2019-01-12 07:00 | 89 | 86
2019-01-12 07:30 | 64 | 62
2019-01-12 08:00 | 49 | 46
2019-01-12 08:30 | 31 | 25
2019-01-12 09:00 | 34 | 29
2019-01-12 09:30 | 32 | 27
2019-01-12 10:00 | 37 | 33
2019-01-12 10:30 | 19 | 14
2019-01-12 11:00 | 29 | 25
2019-01-12 11:30 | 27 | 23
2019-01-12 12:00 | 35 | 30
2019-01-12 12:30 | 43 | 37
2019-01-12 13:00 | 44 | 39
2019-01-12 13:30 | 23 | 18
2019-01-12 14:00 | 38 | 33
2019-01-12 14:30 | 49 | 45
2019-01-12 15:00 | 43 | 40
2019-01-12 15:30 | 41 | 34
2019-01-12 16:00 | 37 | 29
2019-01-12 16:30 | 51 | 48
2019-01-12 17:00 | 60 | 58
2019-01-12 17:30 | 99 | 97
2019-01-12 18:00 | 85 | 83
2019-01-12 18:30 | 93 | 91
2019-01-12 19:00 | 101 | 99
2019-01-12 19:30 | 113 | 112
2019-01-12 20:00 | 103 | 102
2019-01-12 20:30 | 101 | 100
2019-01-12 21:00 | 148 | 147
2019-01-12 21:30 | 183 | 182
2019-01-12 22:00 | 176 | 175
2019-01-12 22:30 | 163 | 162
2019-01-12 23:00 | 157 | 156
2019-01-12 23:30 | 149 | 148
2019-01-13 | 144 | 143
2019-01-13 00:30 | 140 | 139
2019-01-13 01:00 | 135 | 134
2019-01-13 01:30 | 129 | 128
2019-01-13 02:00 | 120 | 118
2019-01-13 02:30 | 122 | 121
2019-01-13 03:00 | 125 | 124
2019-01-13 03:30 | 117 | 116
2019-01-13 04:00 | 119 | 118
2019-01-13 04:30 | 146 | 145
2019-01-13 05:00 | 141 | 140
2019-01-13 05:30 | 119 | 118
2019-01-13 06:00 | 113 | 111
2019-01-13 06:30 | 106 | 105
2019-01-13 07:00 | 79 | 77
2019-01-13 07:30 | 55 | 50
2019-01-13 08:00 | 27 | 21
2019-01-13 08:30 | 7 | 3
2019-01-13 09:00 | 16 | 12
2019-01-13 09:30 | 25 | 18
2019-01-13 10:00 | 34 | 23
2019-01-13 10:30 | 11 | 8
2019-01-13 11:00 | 4 | 3
2019-01-13 11:30 | 11 | 8
2019-01-13 12:00 | 38 | 31
2019-01-13 12:30 | 37 | 31
2019-01-13 13:00 | 22 | 16
2019-01-13 13:30 | 47 | 43
2019-01-13 14:00 | 55 | 51
2019-01-13 14:30 | 95 | 94
2019-01-13 15:00 | 93 | 92
2019-01-13 15:30 | 96 | 95
2019-01-13 16:00 | 116 | 115
2019-01-13 16:30 | 100 | 98
2019-01-13 17:00 | 133 | 132
2019-01-13 17:30 | 163 | 162
2019-01-13 18:00 | 198 | 197
2019-01-13 18:30 | 200 | 199
2019-01-13 19:00 | 213 | 212
2019-01-13 19:30 | 227 | 226
2019-01-13 20:00 | 224 | 223
2019-01-13 20:30 | 218 | 216
2019-01-13 21:00 | 218 | 217
2019-01-13 21:30 | 207 | 206
2019-01-13 22:00 | 193 | 192
2019-01-13 22:30 | 185 | 184
2019-01-13 23:00 | 173 | 171
2019-01-13 23:30 | 165 | 164
2019-01-14 | 154 | 152
2019-01-14 00:30 | 150 | 149
2019-01-14 01:00 | 144 | 143
2019-01-14 01:30 | 141 | 140
2019-01-14 02:00 | 131 | 130
2019-01-14 02:30 | 125 | 124
2019-01-14 03:00 | 123 | 121
2019-01-14 03:30 | 136 | 135
2019-01-14 04:00 | 133 | 131
2019-01-14 04:30 | 121 | 120
2019-01-14 05:00 | 126 | 125
2019-01-14 05:30 | 127 | 125
2019-01-14 06:00 | 127 | 125
2019-01-14 06:30 | 131 | 130
2019-01-14 07:00 | 133 | 132
2019-01-14 07:30 | 136 | 135
2019-01-14 08:00 | 128 | 126
2019-01-14 08:30 | 94 | 93
2019-01-14 09:00 | 85 | 83
2019-01-14 09:30 | 100 | 99
2019-01-14 10:00 | 95 | 94
2019-01-14 10:30 | 105 | 104
2019-01-14 11:00 | 113 | 112
2019-01-14 11:30 | 103 | 102
2019-01-14 12:00 | 126 | 125
2019-01-14 12:30 | 114 | 113
2019-01-14 13:00 | 95 | 94
2019-01-14 13:30 | 125 | 125
2019-01-14 14:00 | 145 | 144
2019-01-14 14:30 | 93 | 92
2019-01-14 15:00 | 109 | 108
2019-01-14 15:30 | 84 | 82
2019-01-14 16:00 | 72 | 70
2019-01-14 16:30 | 63 | 60
2019-01-14 17:00 | 69 | 67
2019-01-14 17:30 | 100 | 98
2019-01-14 18:00 | 124 | 123
2019-01-14 18:30 | 128 | 127
2019-01-14 19:00 | 141 | 140
2019-01-14 19:30 | 146 | 145
2019-01-14 20:00 | 133 | 132
2019-01-14 20:30 | 144 | 142
2019-01-14 21:00 | 132 | 131
2019-01-14 21:30 | 154 | 152
2019-01-14 22:00 | 164 | 163
2019-01-14 22:30 | 162 | 161
2019-01-14 23:00 | 187 | 186
2019-01-14 23:30 | 180 | 179
2019-01-15 | 156 | 155
2019-01-15 00:30 | 137 | 136
2019-01-15 01:00 | 133 | 133
2019-01-15 01:30 | 148 | 147
2019-01-15 02:00 | 142 | 141
2019-01-15 02:30 | 144 | 143
2019-01-15 03:00 | 138 | 137
2019-01-15 03:30 | 141 | 140
2019-01-15 04:00 | 136 | 135
2019-01-15 04:30 | 139 | 138
2019-01-15 05:00 | 145 | 144
2019-01-15 05:30 | 148 | 148
2019-01-15 06:00 | 147 | 146
2019-01-15 06:30 | 158 | 157
2019-01-15 07:00 | 158 | 158
2019-01-15 07:30 | 162 | 161
2019-01-15 08:00 | 152 | 152
2019-01-15 08:30 | 167 | 167
2019-01-15 09:00 | 149 | 148
2019-01-15 09:30 | 141 | 140
2019-01-15 10:00 | 112 | 110
2019-01-15 10:30 | 94 | 92
2019-01-15 11:00 | 95 | 92
2019-01-15 11:30 | 109 | 108
2019-01-15 12:00 | 75 | 73
2019-01-15 12:30 | 104 | 103
2019-01-15 13:00 | 85 | 84
2019-01-15 13:30 | 78 | 76
2019-01-15 14:00 | 90 | 89
2019-01-15 14:30 | 83 | 81
2019-01-15 15:00 | 85 | 83
2019-01-15 15:30 | 56 | 52
2019-01-15 16:00 | 92 | 90
2019-01-15 16:30 | 87 | 85
2019-01-15 17:00 | 103 | 102
2019-01-15 17:30 | 131 | 131
2019-01-15 18:00 | 146 | 146
2019-01-15 18:30 | 177 | 176
2019-01-15 19:00 | 196 | 195
2019-01-15 19:30 | 199 | 198
2019-01-15 20:00 | 180 | 179
2019-01-15 20:30 | 171 | 170
2019-01-15 21:00 | 174 | 173
2019-01-15 21:30 | 180 | 179
2019-01-15 22:00 | 170 | 170
2019-01-15 22:30 | 157 | 156
2019-01-15 23:00 | 128 | 127
2019-01-15 23:30 | 119 | 118
2019-01-16 | 129 | 129
2019-01-16 00:30 | 149 | 149
2019-01-16 01:00 | 148 | 147
2019-01-16 01:30 | 118 | 117
2019-01-16 02:00 | 120 | 119
2019-01-16 02:30 | 115 | 114
2019-01-16 03:00 | 130 | 129
2019-01-16 03:30 | 115 | 114
2019-01-16 04:00 | 106 | 104
2019-01-16 04:30 | 99 | 98
2019-01-16 05:00 | 102 | 101
2019-01-16 05:30 | 121 | 120
2019-01-16 06:00 | 115 | 114
2019-01-16 06:30 | 109 | 108
2019-01-16 07:00 | 69 | 66
2019-01-16 07:30 | 53 | 48
2019-01-16 08:00 | 36 | 32
2019-01-16 08:30 | 21 | 18
2019-01-16 09:00 | 10 | 9
2019-01-16 09:30 | 12 | 10
2019-01-16 10:00 | 37 | 32
2019-01-16 10:30 | 25 | 21
2019-01-16 11:00 | 27 | 21
2019-01-16 11:30 | 19 | 16
2019-01-16 12:00 | 43 | 37
2019-01-16 12:30 | 44 | 38
2019-01-16 13:00 | 45 | 39
2019-01-16 13:30 | 56 | 52
2019-01-16 14:00 | 56 | 50
2019-01-16 14:30 | 16 | 13
2019-01-16 15:00 | 9 | 9
2019-01-16 15:30 | 7 | 7
2019-01-16 16:00 | 7 | 7
2019-01-16 16:30 | 1 | 1
2019-01-16 17:00 | 11 | 9
2019-01-16 17:30 | 23 | 18
2019-01-16 18:00 | 56 | 51
2019-01-16 18:30 | 92 | 90
2019-01-16 19:00 | 97 | 96
2019-01-16 19:30 | 93 | 92
2019-01-16 20:00 | 83 | 81
2019-01-16 20:30 | 72 | 70
2019-01-16 21:00 | 113 | 112
2019-01-16 21:30 | 134 | 133
2019-01-16 22:00 | 140 | 139
2019-01-16 22:30 | 139 | 138
2019-01-16 23:00 | 130 | 129
2019-01-16 23:30 | 104 | 103
2019-01-17 | 93 | 92
2019-01-17 00:30 | 95 | 94
2019-01-17 01:00 | 84 | 83
2019-01-17 01:30 | 86 | 84
2019-01-17 02:00 | 93 | 92
2019-01-17 02:30 | 121 | 120
2019-01-17 03:00 | 130 | 129
2019-01-17 03:30 | 129 | 128
2019-01-17 04:00 | 128 | 128
2019-01-17 04:30 | 117 | 116
2019-01-17 05:00 | 93 | 92
2019-01-17 05:30 | 82 | 80
2019-01-17 06:00 | 81 | 78
2019-01-17 06:30 | 97 | 96
2019-01-17 07:00 | 71 | 69
2019-01-17 07:30 | 58 | 54
2019-01-17 08:00 | 42 | 36
2019-01-17 08:30 | 31 | 27
2019-01-17 09:00 | 3 | 3
2019-01-17 09:30 | 19 | 17
2019-01-17 10:00 | 9 | 8
2019-01-17 10:30 | 12 | 11
2019-01-17 11:00 | 20 | 17
2019-01-17 11:30 | 42 | 37
2019-01-17 12:00 | 55 | 49
2019-01-17 12:30 | 44 | 38
2019-01-17 13:00 | 14 | 13
2019-01-17 13:30 | 3 | 3
2019-01-17 14:00 | 13 | 11
2019-01-17 14:30 | 7 | 6
2019-01-17 15:00 | 3 | 1
2019-01-17 15:30 | 1 | 0
2019-01-17 16:00 | 1 | 0
2019-01-17 16:30 | 13 | 12
2019-01-17 17:00 | 60 | 56
2019-01-17 17:30 | 69 | 66
2019-01-17 18:00 | 98 | 97
2019-01-17 18:30 | 122 | 121
2019-01-17 19:00 | 137 | 136
2019-01-17 19:30 | 134 | 133
2019-01-17 20:00 | 126 | 125
2019-01-17 20:30 | 109 | 108
2019-01-17 21:00 | 108 | 107
2019-01-17 21:30 | 153 | 152
2019-01-17 22:00 | 156 | 155
2019-01-17 22:30 | 143 | 142
2019-01-17 23:00 | 127 | 126
2019-01-17 23:30 | 124 | 123
2019-01-18 | 117 | 116
2019-01-18 00:30 | 124 | 123
2019-01-18 01:00 | 122 | 121
2019-01-18 01:30 | 121 | 120
2019-01-18 02:00 | 112 | 110
2019-01-18 02:30 | 109 | 107
2019-01-18 03:00 | 106 | 105
2019-01-18 03:30 | 104 | 103
2019-01-18 04:00 | 101 | 100
2019-01-18 04:30 | 110 | 108
2019-01-18 05:00 | 110 | 108
2019-01-18 05:30 | 114 | 113
2019-01-18 06:00 | 103 | 102
2019-01-18 06:30 | 113 | 113
2019-01-18 07:00 | 109 | 108
2019-01-18 07:30 | 114 | 112
2019-01-18 08:00 | 110 | 109
2019-01-18 08:30 | 74 | 71
2019-01-18 09:00 | 87 | 85
2019-01-18 09:30 | 106 | 105
2019-01-18 10:00 | 95 | 94
2019-01-18 10:30 | 86 | 85
2019-01-18 11:00 | 112 | 111
2019-01-18 11:30 | 107 | 106
2019-01-18 12:00 | 117 | 117
2019-01-18 12:30 | 125 | 125
2019-01-18 13:00 | 149 | 148
2019-01-18 13:30 | 119 | 118
2019-01-18 14:00 | 107 | 106
2019-01-18 14:30 | 67 | 64
2019-01-18 15:00 | 75 | 73
2019-01-18 15:30 | 74 | 72
2019-01-18 16:00 | 75 | 73
2019-01-18 16:30 | 89 | 87
2019-01-18 17:00 | 127 | 126
2019-01-18 17:30 | 136 | 135
2019-01-18 18:00 | 119 | 118
2019-01-18 18:30 | 126 | 125
2019-01-18 19:00 | 150 | 149
2019-01-18 19:30 | 163 | 163
2019-01-18 20:00 | 155 | 155
2019-01-18 20:30 | 159 | 158
2019-01-18 21:00 | 153 | 153
2019-01-18 21:30 | 198 | 197
2019-01-18 22:00 | 202 | 202
2019-01-18 22:30 | 183 | 182
2019-01-18 23:00 | 176 | 175
2019-01-18 23:30 | 164 | 163
2019-01-19 | 167 | 166
2019-01-19 00:30 | 178 | 178
2019-01-19 01:00 | 173 | 172
2019-01-19 01:30 | 164 | 164
2019-01-19 02:00 | 157 | 156
2019-01-19 02:30 | 159 | 158
2019-01-19 03:00 | 155 | 154
2019-01-19 03:30 | 153 | 152
2019-01-19 04:00 | 157 | 156
2019-01-19 04:30 | 164 | 163
2019-01-19 05:00 | 159 | 159
2019-01-19 05:30 | 157 | 156
2019-01-19 06:00 | 153 | 152
2019-01-19 06:30 | 153 | 153
2019-01-19 07:00 | 143 | 143
2019-01-19 07:30 | 122 | 121
2019-01-19 08:00 | 99 | 98
2019-01-19 08:30 | 74 | 71
2019-01-19 09:00 | 43 | 39
2019-01-19 09:30 | 21 | 18
2019-01-19 10:00 | 7 | 7
2019-01-19 10:30 | 1 | 0
2019-01-19 11:00 | 5 | 4
2019-01-19 11:30 | 26 | 22
2019-01-19 12:00 | 10 | 9
2019-01-19 12:30 | 15 | 13
2019-01-19 13:00 | 32 | 29
2019-01-19 13:30 | 53 | 48
2019-01-19 14:00 | 41 | 38
2019-01-19 14:30 | 44 | 39
2019-01-19 15:00 | 66 | 61
2019-01-19 15:30 | 70 | 67
2019-01-19 16:00 | 80 | 77
2019-01-19 16:30 | 112 | 111
2019-01-19 17:00 | 138 | 137
2019-01-19 17:30 | 156 | 155
2019-01-19 18:00 | 172 | 172
2019-01-19 18:30 | 197 | 197
2019-01-19 19:00 | 210 | 210
2019-01-19 19:30 | 213 | 212
2019-01-19 20:00 | 211 | 211
2019-01-19 20:30 | 191 | 191
2019-01-19 21:00 | 170 | 170
2019-01-19 21:30 | 149 | 149
2019-01-19 22:00 | 139 | 139
2019-01-19 22:30 | 130 | 129
2019-01-19 23:00 | 125 | 124
2019-01-19 23:30 | 127 | 126
2019-01-20 | 117 | 116
2019-01-20 00:30 | 121 | 120
2019-01-20 01:00 | 110 | 109
2019-01-20 01:30 | 108 | 107
2019-01-20 02:00 | 90 | 89
2019-01-20 02:30 | 83 | 81
2019-01-20 03:00 | 74 | 71
2019-01-20 03:30 | 72 | 69
2019-01-20 04:00 | 73 | 70
2019-01-20 04:30 | 81 | 79
2019-01-20 05:00 | 88 | 86
2019-01-20 05:30 | 88 | 86
2019-01-20 06:00 | 85 | 83
2019-01-20 06:30 | 81 | 79
2019-01-20 07:00 | 72 | 68
2019-01-20 07:30 | 78 | 76
2019-01-20 08:00 | 78 | 75
2019-01-20 08:30 | 85 | 82
2019-01-20 09:00 | 82 | 80
2019-01-20 09:30 | 77 | 75
2019-01-20 10:00 | 62 | 57
2019-01-20 10:30 | 29 | 25
2019-01-20 11:00 | 22 | 18
2019-01-20 11:30 | 19 | 17
2019-01-20 12:00 | 13 | 11
2019-01-20 12:30 | 3 | 3
2019-01-20 13:00 | 2 | 2
2019-01-20 13:30 | 2 | 1
2019-01-20 14:00 | 13 | 10
2019-01-20 14:30 | 1 | 1
2019-01-20 15:00 | 3 | 2
2019-01-20 15:30 | 29 | 23
2019-01-20 16:00 | 50 | 43
2019-01-20 16:30 | 69 | 66
2019-01-20 17:00 | 106 | 105
2019-01-20 17:30 | 128 | 127
2019-01-20 18:00 | 159 | 159
2019-01-20 18:30 | 187 | 187
2019-01-20 19:00 | 205 | 204
2019-01-20 19:30 | 211 | 210
2019-01-20 20:00 | 207 | 206
2019-01-20 20:30 | 217 | 216
2019-01-20 21:00 | 213 | 213
2019-01-20 21:30 | 198 | 198
2019-01-20 22:00 | 182 | 182
2019-01-20 22:30 | 153 | 153
2019-01-20 23:00 | 143 | 142
2019-01-20 23:30 | 127 | 126
2019-01-21 | 127 | 126
2019-01-21 00:30 | 138 | 138
2019-01-21 01:00 | 138 | 137
2019-01-21 01:30 | 133 | 132
2019-01-21 02:00 | 134 | 133
2019-01-21 02:30 | 126 | 125
2019-01-21 03:00 | 123 | 122
2019-01-21 03:30 | 116 | 115
2019-01-21 04:00 | 114 | 112
2019-01-21 04:30 | 117 | 115
2019-01-21 05:00 | 114 | 112
2019-01-21 05:30 | 124 | 122
2019-01-21 06:00 | 126 | 125
2019-01-21 06:30 | 122 | 121
2019-01-21 07:00 | 115 | 114
2019-01-21 07:30 | 96 | 94
2019-01-21 08:00 | 88 | 86
2019-01-21 08:30 | 68 | 63
2019-01-21 09:00 | 39 | 37
2019-01-21 09:30 | 46 | 41
2019-01-21 10:00 | 64 | 59
2019-01-21 10:30 | 76 | 73
2019-01-21 11:00 | 86 | 83
2019-01-21 11:30 | 91 | 89
2019-01-21 12:00 | 99 | 97
2019-01-21 12:30 | 78 | 75
2019-01-21 13:00 | 44 | 39
2019-01-21 13:30 | 4 | 1
2019-01-21 14:00 | 27 | 21
2019-01-21 14:30 | 16 | 12
2019-01-21 15:00 | 15 | 12
2019-01-21 15:30 | 14 | 12
2019-01-21 16:00 | 3 | 3
2019-01-21 16:30 | 29 | 27
2019-01-21 17:00 | 57 | 53
2019-01-21 17:30 | 47 | 42
2019-01-21 18:00 | 66 | 61
2019-01-21 18:30 | 105 | 104
2019-01-21 19:00 | 122 | 121
2019-01-21 19:30 | 133 | 133
2019-01-21 20:00 | 132 | 131
2019-01-21 20:30 | 122 | 121
2019-01-21 21:00 | 135 | 134
2019-01-21 21:30 | 160 | 160
2019-01-21 22:00 | 162 | 161
2019-01-21 22:30 | 150 | 149
2019-01-21 23:00 | 157 | 156
2019-01-21 23:30 | 170 | 169
2019-01-22 | 153 | 152
2019-01-22 00:30 | 159 | 158
2019-01-22 01:00 | 157 | 156
2019-01-22 01:30 | 153 | 152
2019-01-22 02:00 | 149 | 148
2019-01-22 02:30 | 135 | 134
2019-01-22 03:00 | 121 | 120
2019-01-22 03:30 | 105 | 104
2019-01-22 04:00 | 99 | 97
2019-01-22 04:30 | 101 | 100
2019-01-22 05:00 | 107 | 106
2019-01-22 05:30 | 103 | 102
2019-01-22 06:00 | 98 | 96
2019-01-22 06:30 | 100 | 98
2019-01-22 07:00 | 116 | 115
2019-01-22 07:30 | 124 | 123
2019-01-22 08:00 | 98 | 97
2019-01-22 08:30 | 69 | 65
2019-01-22 09:00 | 65 | 60
2019-01-22 09:30 | 54 | 47
2019-01-22 10:00 | 40 | 36
2019-01-22 10:30 | 45 | 39
2019-01-22 11:00 | 68 | 64
2019-01-22 11:30 | 89 | 87
2019-01-22 12:00 | 73 | 70
2019-01-22 12:30 | 89 | 87
2019-01-22 13:00 | 105 | 104
2019-01-22 13:30 | 87 | 86
2019-01-22 14:00 | 69 | 66
2019-01-22 14:30 | 53 | 48
2019-01-22 15:00 | 66 | 64
2019-01-22 15:30 | 76 | 74
2019-01-22 16:00 | 69 | 66
2019-01-22 16:30 | 32 | 29
2019-01-22 17:00 | 33 | 32
2019-01-22 17:30 | 78 | 76
2019-01-22 18:00 | 104 | 103
2019-01-22 18:30 | 122 | 122
2019-01-22 19:00 | 139 | 138
2019-01-22 19:30 | 156 | 156
2019-01-22 20:00 | 170 | 170
2019-01-22 20:30 | 147 | 146
2019-01-22 21:00 | 148 | 147
2019-01-22 21:30 | 153 | 152
2019-01-22 22:00 | 175 | 174
2019-01-22 22:30 | 175 | 174
2019-01-22 23:00 | 162 | 161
2019-01-22 23:30 | 143 | 142
2019-01-23 | 139 | 138
2019-01-23 00:30 | 137 | 136
2019-01-23 01:00 | 120 | 119
2019-01-23 01:30 | 111 | 110
2019-01-23 02:00 | 107 | 105
2019-01-23 02:30 | 109 | 108
2019-01-23 03:00 | 120 | 119
2019-01-23 03:30 | 143 | 142
2019-01-23 04:00 | 153 | 152
2019-01-23 04:30 | 148 | 147
2019-01-23 05:00 | 151 | 150
2019-01-23 05:30 | 158 | 158
2019-01-23 06:00 | 160 | 159
2019-01-23 06:30 | 175 | 175
2019-01-23 07:00 | 163 | 162
2019-01-23 07:30 | 149 | 148
2019-01-23 08:00 | 131 | 131
2019-01-23 08:30 | 112 | 111
2019-01-23 09:00 | 115 | 114
2019-01-23 09:30 | 106 | 105
2019-01-23 10:00 | 87 | 85
2019-01-23 10:30 | 66 | 63
2019-01-23 11:00 | 30 | 25
2019-01-23 11:30 | 20 | 17
2019-01-23 12:00 | 12 | 9
2019-01-23 12:30 | 31 | 26
2019-01-23 13:00 | 3 | 3
2019-01-23 13:30 | 23 | 19
2019-01-23 14:00 | 22 | 17
2019-01-23 14:30 | 15 | 13
2019-01-23 15:00 | 6 | 5
2019-01-23 15:30 | 9 | 9
2019-01-23 16:00 | 68 | 65
2019-01-23 16:30 | 65 | 62
2019-01-23 17:00 | 73 | 71
2019-01-23 17:30 | 73 | 70
2019-01-23 18:00 | 87 | 86
2019-01-23 18:30 | 94 | 92
2019-01-23 19:00 | 118 | 117
2019-01-23 19:30 | 119 | 118
2019-01-23 20:00 | 123 | 123
2019-01-23 20:30 | 116 | 115
2019-01-23 21:00 | 119 | 118
2019-01-23 21:30 | 106 | 105
2019-01-23 22:00 | 99 | 98
2019-01-23 22:30 | 126 | 125
2019-01-23 23:00 | 133 | 132
2019-01-23 23:30 | 125 | 125
2019-01-24 | 153 | 152
2019-01-24 00:30 | 162 | 161
2019-01-24 01:00 | 166 | 166
2019-01-24 01:30 | 158 | 157
2019-01-24 02:00 | 150 | 149
2019-01-24 02:30 | 147 | 147
2019-01-24 03:00 | 131 | 130
2019-01-24 03:30 | 126 | 125
2019-01-24 04:00 | 144 | 143
2019-01-24 04:30 | 139 | 139
2019-01-24 05:00 | 134 | 133
2019-01-24 05:30 | 141 | 141
2019-01-24 06:00 | 151 | 150
2019-01-24 06:30 | 166 | 165
2019-01-24 07:00 | 156 | 155
2019-01-24 07:30 | 174 | 173
2019-01-24 08:00 | 138 | 137
2019-01-24 08:30 | 108 | 107
2019-01-24 09:00 | 82 | 80
2019-01-24 09:30 | 99 | 98
2019-01-24 10:00 | 53 | 47
2019-01-24 10:30 | 21 | 16
2019-01-24 11:00 | 2 | 2
2019-01-24 11:30 | 10 | 9
2019-01-24 12:00 | 16 | 13
2019-01-24 12:30 | 8 | 8
2019-01-24 13:00 | 3 | 1
2019-01-24 13:30 | 32 | 25
2019-01-24 14:00 | 5 | 4
2019-01-24 14:30 | 17 | 14
2019-01-24 15:00 | 33 | 25
2019-01-24 15:30 | 86 | 84
2019-01-24 16:00 | 58 | 54
2019-01-24 16:30 | 54 | 48
2019-01-24 17:00 | 81 | 79
2019-01-24 17:30 | 77 | 75
2019-01-24 18:00 | 92 | 91
2019-01-24 18:30 | 120 | 119
2019-01-24 19:00 | 121 | 120
2019-01-24 19:30 | 125 | 124
2019-01-24 20:00 | 137 | 137
2019-01-24 20:30 | 122 | 121
2019-01-24 21:00 | 106 | 105
2019-01-24 21:30 | 97 | 96
2019-01-24 22:00 | 119 | 119
2019-01-24 22:30 | 129 | 128
2019-01-24 23:00 | 118 | 117
2019-01-24 23:30 | 135 | 134
2019-01-25 | 179 | 178
2019-01-25 00:30 | 186 | 186
2019-01-25 01:00 | 166 | 166
2019-01-25 01:30 | 156 | 155
2019-01-25 02:00 | 146 | 145
2019-01-25 02:30 | 138 | 137
2019-01-25 03:00 | 124 | 123
2019-01-25 03:30 | 123 | 122
2019-01-25 04:00 | 127 | 126
2019-01-25 04:30 | 133 | 132
2019-01-25 05:00 | 127 | 126
2019-01-25 05:30 | 125 | 124
2019-01-25 06:00 | 133 | 132
2019-01-25 06:30 | 154 | 154
2019-01-25 07:00 | 144 | 143
2019-01-25 07:30 | 143 | 142
2019-01-25 08:00 | 146 | 145
2019-01-25 08:30 | 114 | 113
2019-01-25 09:00 | 97 | 95
2019-01-25 09:30 | 100 | 98
2019-01-25 10:00 | 84 | 82
2019-01-25 10:30 | 68 | 63
2019-01-25 11:00 | 47 | 41
2019-01-25 11:30 | 40 | 33
2019-01-25 12:00 | 19 | 16
2019-01-25 12:30 | 15 | 12
2019-01-25 13:00 | 34 | 31
2019-01-25 13:30 | 38 | 33
2019-01-25 14:00 | 38 | 32
2019-01-25 14:30 | 4 | 4
2019-01-25 15:00 | 21 | 17
2019-01-25 15:30 | 2 | 2
2019-01-25 16:00 | 12 | 10
2019-01-25 16:30 | 7 | 6
2019-01-25 17:00 | 19 | 16
2019-01-25 17:30 | 43 | 35
2019-01-25 18:00 | 64 | 60
2019-01-25 18:30 | 60 | 54
2019-01-25 19:00 | 56 | 50
2019-01-25 19:30 | 47 | 39
2019-01-25 20:00 | 53 | 45
2019-01-25 20:30 | 57 | 49
2019-01-25 21:00 | 56 | 48
2019-01-25 21:30 | 40 | 37
2019-01-25 22:00 | 40 | 34
2019-01-25 22:30 | 68 | 63
2019-01-25 23:00 | 61 | 54
2019-01-25 23:30 | 56 | 48
2019-01-26 | 81 | 78
2019-01-26 00:30 | 134 | 133
2019-01-26 01:00 | 125 | 124
2019-01-26 01:30 | 109 | 107
2019-01-26 02:00 | 102 | 101
2019-01-26 02:30 | 103 | 102
2019-01-26 03:00 | 106 | 105
2019-01-26 03:30 | 114 | 113
2019-01-26 04:00 | 122 | 121
2019-01-26 04:30 | 113 | 112
2019-01-26 05:00 | 113 | 111
2019-01-26 05:30 | 122 | 121
2019-01-26 06:00 | 112 | 110
2019-01-26 06:30 | 110 | 109
2019-01-26 07:00 | 103 | 102
2019-01-26 07:30 | 93 | 91
2019-01-26 08:00 | 98 | 96
2019-01-26 08:30 | 94 | 92
2019-01-26 09:00 | 87 | 84
2019-01-26 09:30 | 107 | 106
2019-01-26 10:00 | 106 | 104
2019-01-26 10:30 | 60 | 55
2019-01-26 11:00 | 81 | 78
2019-01-26 11:30 | 77 | 74
2019-01-26 12:00 | 53 | 49
2019-01-26 12:30 | 28 | 22
2019-01-26 13:00 | 54 | 48
2019-01-26 13:30 | 85 | 83
2019-01-26 14:00 | 89 | 86
2019-01-26 14:30 | 77 | 74
2019-01-26 15:00 | 86 | 84
2019-01-26 15:30 | 101 | 99
2019-01-26 16:00 | 111 | 110
2019-01-26 16:30 | 106 | 105
2019-01-26 17:00 | 106 | 105
2019-01-26 17:30 | 110 | 109
2019-01-26 18:00 | 119 | 118
2019-01-26 18:30 | 125 | 124
2019-01-26 19:00 | 125 | 124
2019-01-26 19:30 | 127 | 126
2019-01-26 20:00 | 131 | 130
2019-01-26 20:30 | 121 | 119
2019-01-26 21:00 | 119 | 118
2019-01-26 21:30 | 123 | 122
2019-01-26 22:00 | 119 | 118
2019-01-26 22:30 | 119 | 118
2019-01-26 23:00 | 113 | 111
2019-01-26 23:30 | 134 | 133
2019-01-27 | 139 | 138
2019-01-27 00:30 | 161 | 160
2019-01-27 01:00 | 96 | 94
2019-01-27 01:30 | 87 | 84
2019-01-27 02:00 | 84 | 81
2019-01-27 02:30 | 85 | 81
2019-01-27 03:00 | 91 | 88
2019-01-27 03:30 | 82 | 79
2019-01-27 04:00 | 86 | 83
2019-01-27 04:30 | 81 | 78
2019-01-27 05:00 | 80 | 77
2019-01-27 05:30 | 87 | 85
2019-01-27 06:00 | 100 | 98
2019-01-27 06:30 | 102 | 100
2019-01-27 07:00 | 94 | 92
2019-01-27 07:30 | 84 | 81
2019-01-27 08:00 | 92 | 89
2019-01-27 08:30 | 95 | 93
2019-01-27 09:00 | 102 | 100
2019-01-27 09:30 | 97 | 95
2019-01-27 10:00 | 87 | 84
2019-01-27 10:30 | 84 | 82
2019-01-27 11:00 | 79 | 76
2019-01-27 11:30 | 81 | 77
2019-01-27 12:00 | 93 | 90
2019-01-27 12:30 | 58 | 52
2019-01-27 13:00 | 64 | 58
2019-01-27 13:30 | 78 | 74
2019-01-27 14:00 | 107 | 106
2019-01-27 14:30 | 115 | 113
2019-01-27 15:00 | 131 | 130
2019-01-27 15:30 | 130 | 129
2019-01-27 16:00 | 141 | 141
2019-01-27 16:30 | 135 | 134
2019-01-27 17:00 | 132 | 131
2019-01-27 17:30 | 148 | 147
2019-01-27 18:00 | 179 | 179
2019-01-27 18:30 | 188 | 187
2019-01-27 19:00 | 199 | 198
2019-01-27 19:30 | 203 | 203
2019-01-27 20:00 | 198 | 198
2019-01-27 20:30 | 184 | 183
2019-01-27 21:00 | 189 | 188
2019-01-27 21:30 | 192 | 192
2019-01-27 22:00 | 193 | 193
2019-01-27 22:30 | 182 | 181
2019-01-27 23:00 | 155 | 154
2019-01-27 23:30 | 160 | 159
2019-01-28 | 165 | 165
2019-01-28 00:30 | 176 | 175
2019-01-28 01:00 | 168 | 167
2019-01-28 01:30 | 164 | 164
2019-01-28 02:00 | 160 | 160
2019-01-28 02:30 | 160 | 159
2019-01-28 03:00 | 149 | 149
2019-01-28 03:30 | 145 | 144
2019-01-28 04:00 | 144 | 143
2019-01-28 04:30 | 151 | 150
2019-01-28 05:00 | 152 | 151
2019-01-28 05:30 | 154 | 154
2019-01-28 06:00 | 156 | 156
2019-01-28 06:30 | 164 | 164
2019-01-28 07:00 | 169 | 168
2019-01-28 07:30 | 175 | 174
2019-01-28 08:00 | 182 | 182
2019-01-28 08:30 | 185 | 184
2019-01-28 09:00 | 190 | 189
2019-01-28 09:30 | 192 | 192
2019-01-28 10:00 | 194 | 193
2019-01-28 10:30 | 194 | 194
2019-01-28 11:00 | 183 | 183
2019-01-28 11:30 | 188 | 187
2019-01-28 12:00 | 193 | 193
2019-01-28 12:30 | 201 | 201
2019-01-28 13:00 | 199 | 199
2019-01-28 13:30 | 185 | 184
2019-01-28 14:00 | 183 | 182
2019-01-28 14:30 | 177 | 176
2019-01-28 15:00 | 170 | 169
2019-01-28 15:30 | 169 | 169
2019-01-28 16:00 | 166 | 165
2019-01-28 16:30 | 171 | 170
2019-01-28 17:00 | 176 | 176
2019-01-28 17:30 | 183 | 182
2019-01-28 18:00 | 191 | 191
2019-01-28 18:30 | 202 | 201
2019-01-28 19:00 | 217 | 217
2019-01-28 19:30 | 226 | 225
2019-01-28 20:00 | 228 | 228
2019-01-28 20:30 | 220 | 220
2019-01-28 21:00 | 207 | 206
2019-01-28 21:30 | 197 | 197
2019-01-28 22:00 | 185 | 185
2019-01-28 22:30 | 176 | 175
2019-01-28 23:00 | 183 | 183
2019-01-28 23:30 | 173 | 173
2019-01-29 | 168 | 167
2019-01-29 00:30 | 166 | 166
2019-01-29 01:00 | 161 | 160
2019-01-29 01:30 | 160 | 159
2019-01-29 02:00 | 154 | 153
2019-01-29 02:30 | 150 | 149
2019-01-29 03:00 | 145 | 145
2019-01-29 03:30 | 142 | 141
2019-01-29 04:00 | 142 | 141
2019-01-29 04:30 | 149 | 148
2019-01-29 05:00 | 142 | 141
2019-01-29 05:30 | 141 | 140
2019-01-29 06:00 | 158 | 157
2019-01-29 06:30 | 172 | 172
2019-01-29 07:00 | 166 | 165
2019-01-29 07:30 | 188 | 188
2019-01-29 08:00 | 194 | 193
2019-01-29 08:30 | 214 | 214
2019-01-29 09:00 | 221 | 220
2019-01-29 09:30 | 225 | 224
2019-01-29 10:00 | 220 | 219
2019-01-29 10:30 | 212 | 212
2019-01-29 11:00 | 209 | 209
2019-01-29 11:30 | 183 | 183
2019-01-29 12:00 | 163 | 162
2019-01-29 12:30 | 173 | 173
2019-01-29 13:00 | 197 | 196
2019-01-29 13:30 | 214 | 213
2019-01-29 14:00 | 219 | 218
2019-01-29 14:30 | 215 | 215
2019-01-29 15:00 | 215 | 215
2019-01-29 15:30 | 202 | 202
2019-01-29 16:00 | 193 | 192
2019-01-29 16:30 | 183 | 183
2019-01-29 17:00 | 110 | 108
2019-01-29 17:30 | 111 | 109
2019-01-29 18:00 | 125 | 124
2019-01-29 18:30 | 131 | 130
2019-01-29 19:00 | 133 | 132
2019-01-29 19:30 | 146 | 145
2019-01-29 20:00 | 147 | 146
2019-01-29 20:30 | 141 | 140
2019-01-29 21:00 | 130 | 129
2019-01-29 21:30 | 181 | 180
2019-01-29 22:00 | 202 | 201
2019-01-29 22:30 | 191 | 191
2019-01-29 23:00 | 175 | 174
2019-01-29 23:30 | 173 | 173
2019-01-30 | 172 | 172
2019-01-30 00:30 | 174 | 174
2019-01-30 01:00 | 159 | 158
2019-01-30 01:30 | 150 | 149
2019-01-30 02:00 | 140 | 139
2019-01-30 02:30 | 143 | 142
2019-01-30 03:00 | 145 | 144
2019-01-30 03:30 | 147 | 146
2019-01-30 04:00 | 151 | 150
2019-01-30 04:30 | 154 | 153
2019-01-30 05:00 | 155 | 154
2019-01-30 05:30 | 162 | 161
2019-01-30 06:00 | 168 | 167
2019-01-30 06:30 | 178 | 177
2019-01-30 07:00 | 190 | 189
2019-01-30 07:30 | 218 | 218
2019-01-30 08:00 | 225 | 225
2019-01-30 08:30 | 231 | 231
2019-01-30 09:00 | 235 | 234
2019-01-30 09:30 | 239 | 239
2019-01-30 10:00 | 236 | 236
2019-01-30 10:30 | 232 | 232
2019-01-30 11:00 | 228 | 228
2019-01-30 11:30 | 221 | 221
2019-01-30 12:00 | 217 | 217
2019-01-30 12:30 | 215 | 214
2019-01-30 13:00 | 210 | 210
2019-01-30 13:30 | 202 | 201
2019-01-30 14:00 | 195 | 194
2019-01-30 14:30 | 189 | 189
2019-01-30 15:00 | 156 | 156
2019-01-30 15:30 | 117 | 116
2019-01-30 16:00 | 121 | 121
2019-01-30 16:30 | 129 | 128
2019-01-30 17:00 | 141 | 140
2019-01-30 17:30 | 143 | 142
2019-01-30 18:00 | 176 | 175
2019-01-30 18:30 | 196 | 195
2019-01-30 19:00 | 195 | 195
2019-01-30 19:30 | 177 | 177
2019-01-30 20:00 | 202 | 202
2019-01-30 20:30 | 224 | 223
2019-01-30 21:00 | 237 | 236
2019-01-30 21:30 | 229 | 229
2019-01-30 22:00 | 214 | 214
2019-01-30 22:30 | 198 | 197
2019-01-30 23:00 | 186 | 185
2019-01-30 23:30 | 168 | 168
2019-01-31 | 165 | 164
2019-01-31 00:30 | 166 | 166
2019-01-31 01:00 | 160 | 159
2019-01-31 01:30 | 158 | 157
2019-01-31 02:00 | 162 | 161
2019-01-31 02:30 | 158 | 157
2019-01-31 03:00 | 152 | 151
2019-01-31 03:30 | 153 | 153
2019-01-31 04:00 | 153 | 152
2019-01-31 04:30 | 156 | 155
2019-01-31 05:00 | 160 | 159
2019-01-31 05:30 | 167 | 166
2019-01-31 06:00 | 174 | 173
2019-01-31 06:30 | 182 | 181
2019-01-31 07:00 | 179 | 179
2019-01-31 07:30 | 203 | 202
2019-01-31 08:00 | 222 | 221
2019-01-31 08:30 | 230 | 229
2019-01-31 09:00 | 238 | 238
2019-01-31 09:30 | 238 | 238
2019-01-31 10:00 | 230 | 230
2019-01-31 10:30 | 222 | 222
2019-01-31 11:00 | 220 | 220
2019-01-31 11:30 | 212 | 211
2019-01-31 12:00 | 215 | 215
2019-01-31 12:30 | 211 | 211
2019-01-31 13:00 | 206 | 205
2019-01-31 13:30 | 162 | 161
2019-01-31 14:00 | 126 | 125
2019-01-31 14:30 | 126 | 125
2019-01-31 15:00 | 113 | 111
2019-01-31 15:30 | 100 | 99
2019-01-31 16:00 | 110 | 109
2019-01-31 16:30 | 101 | 100
2019-01-31 17:00 | 103 | 102
2019-01-31 17:30 | 111 | 110
2019-01-31 18:00 | 128 | 127
2019-01-31 18:30 | 151 | 150
2019-01-31 19:00 | 184 | 184
2019-01-31 19:30 | 198 | 198
2019-01-31 20:00 | 191 | 191
2019-01-31 20:30 | 242 | 242
2019-01-31 21:00 | 253 | 253
2019-01-31 21:30 | 243 | 243
2019-01-31 22:00 | 232 | 232
2019-01-31 22:30 | 220 | 220
2019-01-31 23:00 | 209 | 209
2019-01-31 23:30 | 199 | 198
2019-02-01 | 191 | 191
2019-02-01 00:30 | 193 | 193
2019-02-01 01:00 | 181 | 181
2019-02-01 01:30 | 174 | 173
2019-02-01 02:00 | 166 | 166
2019-02-01 02:30 | 165 | 164
2019-02-01 03:00 | 164 | 163
2019-02-01 03:30 | 157 | 156
2019-02-01 04:00 | 145 | 145
2019-02-01 04:30 | 147 | 146
2019-02-01 05:00 | 148 | 147
2019-02-01 05:30 | 155 | 154
2019-02-01 06:00 | 163 | 163
2019-02-01 06:30 | 179 | 179
2019-02-01 07:00 | 187 | 186
2019-02-01 07:30 | 200 | 200
2019-02-01 08:00 | 215 | 214
2019-02-01 08:30 | 222 | 221
2019-02-01 09:00 | 213 | 213
2019-02-01 09:30 | 216 | 216
2019-02-01 10:00 | 222 | 221
2019-02-01 10:30 | 222 | 221
2019-02-01 11:00 | 210 | 210
2019-02-01 11:30 | 190 | 189
2019-02-01 12:00 | 186 | 185
2019-02-01 12:30 | 184 | 184
2019-02-01 13:00 | 192 | 191
2019-02-01 13:30 | 205 | 205
2019-02-01 14:00 | 209 | 209
2019-02-01 14:30 | 222 | 222
2019-02-01 15:00 | 220 | 220
2019-02-01 15:30 | 209 | 209
2019-02-01 16:00 | 212 | 212
2019-02-01 16:30 | 207 | 206
2019-02-01 17:00 | 206 | 206
2019-02-01 17:30 | 223 | 223
2019-02-01 18:00 | 233 | 233
2019-02-01 18:30 | 238 | 238
2019-02-01 19:00 | 244 | 244
2019-02-01 19:30 | 247 | 247
2019-02-01 20:00 | 237 | 237
2019-02-01 20:30 | 229 | 229
2019-02-01 21:00 | 223 | 223
2019-02-01 21:30 | 217 | 217
2019-02-01 22:00 | 210 | 209
2019-02-01 22:30 | 200 | 199
2019-02-01 23:00 | 191 | 190
2019-02-01 23:30 | 181 | 181
2019-02-02 | 174 | 173
2019-02-02 00:30 | 175 | 175
2019-02-02 01:00 | 159 | 159
2019-02-02 01:30 | 107 | 106
2019-02-02 02:00 | 104 | 103
2019-02-02 02:30 | 97 | 96
2019-02-02 03:00 | 95 | 94
2019-02-02 03:30 | 98 | 96
2019-02-02 04:00 | 97 | 96
2019-02-02 04:30 | 91 | 90
2019-02-02 05:00 | 106 | 105
2019-02-02 05:30 | 123 | 122
2019-02-02 06:00 | 128 | 127
2019-02-02 06:30 | 138 | 137
2019-02-02 07:00 | 143 | 143
2019-02-02 07:30 | 150 | 149
2019-02-02 08:00 | 158 | 158
2019-02-02 08:30 | 164 | 164
2019-02-02 09:00 | 172 | 171
2019-02-02 09:30 | 175 | 174
2019-02-02 10:00 | 177 | 176
2019-02-02 10:30 | 173 | 172
2019-02-02 11:00 | 161 | 160
2019-02-02 11:30 | 171 | 170
2019-02-02 12:00 | 191 | 190
2019-02-02 12:30 | 185 | 184
2019-02-02 13:00 | 186 | 185
2019-02-02 13:30 | 189 | 188
2019-02-02 14:00 | 178 | 177
2019-02-02 14:30 | 165 | 165
2019-02-02 15:00 | 173 | 172
2019-02-02 15:30 | 187 | 187
2019-02-02 16:00 | 199 | 199
2019-02-02 16:30 | 191 | 190
2019-02-02 17:00 | 182 | 181
2019-02-02 17:30 | 185 | 184
2019-02-02 18:00 | 194 | 194
2019-02-02 18:30 | 208 | 208
2019-02-02 19:00 | 208 | 208
2019-02-02 19:30 | 208 | 208
2019-02-02 20:00 | 212 | 211
2019-02-02 20:30 | 199 | 198
2019-02-02 21:00 | 193 | 192
2019-02-02 21:30 | 182 | 181
2019-02-02 22:00 | 172 | 172
2019-02-02 22:30 | 167 | 167
2019-02-02 23:00 | 156 | 156
2019-02-02 23:30 | 145 | 144
2019-02-03 | 140 | 140
2019-02-03 00:30 | 144 | 143
2019-02-03 01:00 | 130 | 130
2019-02-03 01:30 | 123 | 122
2019-02-03 02:00 | 122 | 121
2019-02-03 02:30 | 119 | 118
2019-02-03 03:00 | 120 | 119
2019-02-03 03:30 | 116 | 115
2019-02-03 04:00 | 113 | 113
2019-02-03 04:30 | 114 | 113
2019-02-03 05:00 | 117 | 116
2019-02-03 05:30 | 118 | 117
2019-02-03 06:00 | 118 | 117
2019-02-03 06:30 | 124 | 123
2019-02-03 07:00 | 127 | 126
2019-02-03 07:30 | 132 | 131
2019-02-03 08:00 | 141 | 141
2019-02-03 08:30 | 150 | 150
2019-02-03 09:00 | 154 | 153
2019-02-03 09:30 | 155 | 155
2019-02-03 10:00 | 158 | 158
2019-02-03 10:30 | 162 | 162
2019-02-03 11:00 | 170 | 170
2019-02-03 11:30 | 165 | 164
2019-02-03 12:00 | 164 | 164
2019-02-03 12:30 | 148 | 147
2019-02-03 13:00 | 148 | 147
2019-02-03 13:30 | 153 | 152
2019-02-03 14:00 | 152 | 151
2019-02-03 14:30 | 142 | 141
2019-02-03 15:00 | 140 | 140
2019-02-03 15:30 | 168 | 167
2019-02-03 16:00 | 174 | 173
2019-02-03 16:30 | 187 | 187
2019-02-03 17:00 | 205 | 205
2019-02-03 17:30 | 210 | 210
2019-02-03 18:00 | 223 | 222
2019-02-03 18:30 | 223 | 222
2019-02-03 19:00 | 214 | 213
2019-02-03 19:30 | 213 | 212
2019-02-03 20:00 | 192 | 192
2019-02-03 20:30 | 180 | 180
2019-02-03 21:00 | 171 | 170
2019-02-03 21:30 | 156 | 155
2019-02-03 22:00 | 143 | 142
2019-02-03 22:30 | 134 | 133
2019-02-03 23:00 | 128 | 127
2019-02-03 23:30 | 118 | 117
2019-02-04 | 115 | 114
2019-02-04 00:30 | 120 | 119
2019-02-04 01:00 | 98 | 97
2019-02-04 01:30 | 96 | 94
2019-02-04 02:00 | 96 | 94
2019-02-04 02:30 | 97 | 95
2019-02-04 03:00 | 94 | 92
2019-02-04 03:30 | 83 | 81
2019-02-04 04:00 | 81 | 79
2019-02-04 04:30 | 82 | 80
2019-02-04 05:00 | 83 | 82
2019-02-04 05:30 | 85 | 83
2019-02-04 06:00 | 96 | 94
2019-02-04 06:30 | 109 | 107
2019-02-04 07:00 | 126 | 124
2019-02-04 07:30 | 137 | 136
2019-02-04 08:00 | 145 | 144
2019-02-04 08:30 | 147 | 146
2019-02-04 09:00 | 139 | 138
2019-02-04 09:30 | 140 | 139
2019-02-04 10:00 | 134 | 133
2019-02-04 10:30 | 127 | 127
2019-02-04 11:00 | 127 | 127
2019-02-04 11:30 | 129 | 129
2019-02-04 12:00 | 122 | 122
2019-02-04 12:30 | 92 | 90
2019-02-04 13:00 | 84 | 83
2019-02-04 13:30 | 59 | 54
2019-02-04 14:00 | 75 | 72
2019-02-04 14:30 | 62 | 56
2019-02-04 15:00 | 83 | 81
2019-02-04 15:30 | 89 | 87
2019-02-04 16:00 | 89 | 87
2019-02-04 16:30 | 93 | 91
2019-02-04 17:00 | 94 | 93
2019-02-04 17:30 | 106 | 105
2019-02-04 18:00 | 114 | 114
2019-02-04 18:30 | 115 | 114
2019-02-04 19:00 | 122 | 122
2019-02-04 19:30 | 125 | 124
2019-02-04 20:00 | 117 | 117
2019-02-04 20:30 | 104 | 103
2019-02-04 21:00 | 113 | 112
2019-02-04 21:30 | 123 | 122
2019-02-04 22:00 | 113 | 112
2019-02-04 22:30 | 129 | 128
2019-02-04 23:00 | 126 | 125
2019-02-04 23:30 | 117 | 116
2019-02-05 | 112 | 111
2019-02-05 00:30 | 121 | 120
2019-02-05 01:00 | 107 | 106
2019-02-05 01:30 | 99 | 98
2019-02-05 02:00 | 89 | 88
2019-02-05 02:30 | 93 | 91
2019-02-05 03:00 | 93 | 92
2019-02-05 03:30 | 80 | 78
2019-02-05 04:00 | 80 | 78
2019-02-05 04:30 | 83 | 81
2019-02-05 05:00 | 90 | 89
2019-02-05 05:30 | 93 | 92
2019-02-05 06:00 | 105 | 104
2019-02-05 06:30 | 121 | 120
2019-02-05 07:00 | 131 | 130
2019-02-05 07:30 | 147 | 146
2019-02-05 08:00 | 153 | 152
2019-02-05 08:30 | 143 | 142
2019-02-05 09:00 | 131 | 130
2019-02-05 09:30 | 121 | 120
2019-02-05 10:00 | 109 | 108
2019-02-05 10:30 | 103 | 102
2019-02-05 11:00 | 105 | 104
2019-02-05 11:30 | 101 | 100
2019-02-05 12:00 | 103 | 102
2019-02-05 12:30 | 106 | 105
2019-02-05 13:00 | 87 | 84
2019-02-05 13:30 | 96 | 94
2019-02-05 14:00 | 108 | 107
2019-02-05 14:30 | 115 | 114
2019-02-05 15:00 | 147 | 146
2019-02-05 15:30 | 175 | 174
2019-02-05 16:00 | 203 | 202
2019-02-05 16:30 | 200 | 199
2019-02-05 17:00 | 227 | 227
2019-02-05 17:30 | 235 | 235
2019-02-05 18:00 | 243 | 242
2019-02-05 18:30 | 225 | 224
2019-02-05 19:00 | 236 | 236
2019-02-05 19:30 | 241 | 241
2019-02-05 20:00 | 233 | 233
2019-02-05 20:30 | 222 | 221
2019-02-05 21:00 | 215 | 215
2019-02-05 21:30 | 195 | 194
2019-02-05 22:00 | 189 | 188
2019-02-05 22:30 | 182 | 181
2019-02-05 23:00 | 173 | 172
2019-02-05 23:30 | 157 | 157
2019-02-06 | 150 | 149
2019-02-06 00:30 | 158 | 157
2019-02-06 01:00 | 150 | 149
2019-02-06 01:30 | 139 | 139
2019-02-06 02:00 | 135 | 134
2019-02-06 02:30 | 128 | 127
2019-02-06 03:00 | 124 | 123
2019-02-06 03:30 | 123 | 122
2019-02-06 04:00 | 126 | 125
2019-02-06 04:30 | 128 | 127
2019-02-06 05:00 | 124 | 123
2019-02-06 05:30 | 125 | 123
2019-02-06 06:00 | 130 | 129
2019-02-06 06:30 | 149 | 148
2019-02-06 07:00 | 169 | 168
2019-02-06 07:30 | 188 | 187
2019-02-06 08:00 | 198 | 198
2019-02-06 08:30 | 202 | 202
2019-02-06 09:00 | 197 | 196
2019-02-06 09:30 | 192 | 192
2019-02-06 10:00 | 185 | 184
2019-02-06 10:30 | 168 | 167
2019-02-06 11:00 | 155 | 154
2019-02-06 11:30 | 140 | 139
2019-02-06 12:00 | 118 | 117
2019-02-06 12:30 | 113 | 112
2019-02-06 13:00 | 110 | 109
2019-02-06 13:30 | 106 | 105
2019-02-06 14:00 | 111 | 110
2019-02-06 14:30 | 99 | 98
2019-02-06 15:00 | 98 | 97
2019-02-06 15:30 | 78 | 76
2019-02-06 16:00 | 55 | 49
2019-02-06 16:30 | 69 | 65
2019-02-06 17:00 | 105 | 104
2019-02-06 17:30 | 127 | 126
2019-02-06 18:00 | 139 | 138
2019-02-06 18:30 | 134 | 133
2019-02-06 19:00 | 145 | 145
2019-02-06 19:30 | 140 | 139
2019-02-06 20:00 | 144 | 143
2019-02-06 20:30 | 147 | 146
2019-02-06 21:00 | 177 | 176
2019-02-06 21:30 | 171 | 170
2019-02-06 22:00 | 161 | 160
2019-02-06 22:30 | 163 | 162
2019-02-06 23:00 | 154 | 154
2019-02-06 23:30 | 155 | 155
2019-02-07 | 148 | 147
2019-02-07 00:30 | 151 | 150
2019-02-07 01:00 | 142 | 142
2019-02-07 01:30 | 136 | 135
2019-02-07 02:00 | 126 | 125
2019-02-07 02:30 | 124 | 123
2019-02-07 03:00 | 124 | 123
2019-02-07 03:30 | 116 | 115
2019-02-07 04:00 | 108 | 107
2019-02-07 04:30 | 110 | 109
2019-02-07 05:00 | 113 | 112
2019-02-07 05:30 | 123 | 122
2019-02-07 06:00 | 128 | 127
2019-02-07 06:30 | 152 | 151
2019-02-07 07:00 | 167 | 167
2019-02-07 07:30 | 186 | 185
2019-02-07 08:00 | 192 | 192
2019-02-07 08:30 | 191 | 190
2019-02-07 09:00 | 179 | 178
2019-02-07 09:30 | 172 | 172
2019-02-07 10:00 | 174 | 173
2019-02-07 10:30 | 157 | 157
2019-02-07 11:00 | 159 | 159
2019-02-07 11:30 | 176 | 176
2019-02-07 12:00 | 170 | 169
2019-02-07 12:30 | 187 | 186
2019-02-07 13:00 | 193 | 193
2019-02-07 13:30 | 171 | 171
2019-02-07 14:00 | 162 | 161
2019-02-07 14:30 | 161 | 160
2019-02-07 15:00 | 132 | 130
2019-02-07 15:30 | 128 | 125
2019-02-07 16:00 | 146 | 145
2019-02-07 16:30 | 155 | 154
2019-02-07 17:00 | 154 | 153
2019-02-07 17:30 | 157 | 156
2019-02-07 18:00 | 165 | 164
2019-02-07 18:30 | 176 | 176
2019-02-07 19:00 | 182 | 181
2019-02-07 19:30 | 187 | 186
2019-02-07 20:00 | 184 | 183
2019-02-07 20:30 | 176 | 175
2019-02-07 21:00 | 188 | 187
2019-02-07 21:30 | 170 | 169
2019-02-07 22:00 | 167 | 166
2019-02-07 22:30 | 185 | 184
2019-02-07 23:00 | 178 | 178
2019-02-07 23:30 | 168 | 168
2019-02-08 | 163 | 162
2019-02-08 00:30 | 168 | 168
2019-02-08 01:00 | 161 | 160
2019-02-08 01:30 | 158 | 157
2019-02-08 02:00 | 153 | 153
2019-02-08 02:30 | 153 | 152
2019-02-08 03:00 | 149 | 149
2019-02-08 03:30 | 148 | 147
2019-02-08 04:00 | 148 | 147
2019-02-08 04:30 | 148 | 147
2019-02-08 05:00 | 152 | 151
2019-02-08 05:30 | 158 | 157
2019-02-08 06:00 | 166 | 165
2019-02-08 06:30 | 178 | 177
2019-02-08 07:00 | 188 | 188
2019-02-08 07:30 | 200 | 199
2019-02-08 08:00 | 201 | 201
2019-02-08 08:30 | 197 | 196
2019-02-08 09:00 | 189 | 188
2019-02-08 09:30 | 178 | 177
2019-02-08 10:00 | 157 | 157
2019-02-08 10:30 | 127 | 126
2019-02-08 11:00 | 124 | 121
2019-02-08 11:30 | 142 | 139
2019-02-08 12:00 | 137 | 134
2019-02-08 12:30 | 145 | 142
2019-02-08 13:00 | 157 | 154
2019-02-08 13:30 | 161 | 160
2019-02-08 14:00 | 186 | 184
2019-02-08 14:30 | 204 | 203
2019-02-08 15:00 | 197 | 195
2019-02-08 15:30 | 212 | 211
2019-02-08 16:00 | 205 | 203
2019-02-08 16:30 | 211 | 211
2019-02-08 17:00 | 220 | 219
2019-02-08 17:30 | 225 | 224
2019-02-08 18:00 | 235 | 234
2019-02-08 18:30 | 245 | 244
2019-02-08 19:00 | 247 | 247
2019-02-08 19:30 | 255 | 253
2019-02-08 20:00 | 251 | 250
2019-02-08 20:30 | 243 | 242
2019-02-08 21:00 | 231 | 231
2019-02-08 21:30 | 217 | 217
2019-02-08 22:00 | 208 | 208
2019-02-08 22:30 | 195 | 195
2019-02-08 23:00 | 181 | 181
2019-02-08 23:30 | 172 | 172
2019-02-09 | 160 | 160
2019-02-09 00:30 | 160 | 159
2019-02-09 01:00 | 143 | 142
2019-02-09 01:30 | 135 | 135
2019-02-09 02:00 | 136 | 135
2019-02-09 02:30 | 137 | 136
2019-02-09 03:00 | 143 | 142
2019-02-09 03:30 | 149 | 148
2019-02-09 04:00 | 149 | 149
2019-02-09 04:30 | 149 | 148
2019-02-09 05:00 | 144 | 143
2019-02-09 05:30 | 144 | 143
2019-02-09 06:00 | 146 | 146
2019-02-09 06:30 | 149 | 148
2019-02-09 07:00 | 143 | 143
2019-02-09 07:30 | 150 | 149
2019-02-09 08:00 | 152 | 151
2019-02-09 08:30 | 135 | 134
2019-02-09 09:00 | 139 | 138
2019-02-09 09:30 | 128 | 128
2019-02-09 10:00 | 125 | 124
2019-02-09 10:30 | 111 | 110
2019-02-09 11:00 | 100 | 99
2019-02-09 11:30 | 111 | 110
2019-02-09 12:00 | 111 | 110
2019-02-09 12:30 | 109 | 107
2019-02-09 13:00 | 101 | 99
2019-02-09 13:30 | 99 | 98
2019-02-09 14:00 | 105 | 103
2019-02-09 14:30 | 102 | 101
2019-02-09 15:00 | 110 | 110
2019-02-09 15:30 | 121 | 120
2019-02-09 16:00 | 132 | 131
2019-02-09 16:30 | 152 | 151
2019-02-09 17:00 | 164 | 164
2019-02-09 17:30 | 193 | 193
2019-02-09 18:00 | 222 | 222
2019-02-09 18:30 | 236 | 236
2019-02-09 19:00 | 260 | 259
2019-02-09 19:30 | 259 | 258
2019-02-09 20:00 | 257 | 256
2019-02-09 20:30 | 246 | 246
2019-02-09 21:00 | 241 | 241
2019-02-09 21:30 | 234 | 233
2019-02-09 22:00 | 231 | 230
2019-02-09 22:30 | 216 | 215
2019-02-09 23:00 | 206 | 206
2019-02-09 23:30 | 190 | 190
2019-02-10 | 175 | 175
2019-02-10 00:30 | 175 | 174
2019-02-10 01:00 | 164 | 163
2019-02-10 01:30 | 157 | 157
2019-02-10 02:00 | 152 | 152
2019-02-10 02:30 | 148 | 147
2019-02-10 03:00 | 141 | 141
2019-02-10 03:30 | 136 | 135
2019-02-10 04:00 | 129 | 128
2019-02-10 04:30 | 130 | 130
2019-02-10 05:00 | 137 | 136
2019-02-10 05:30 | 134 | 133
2019-02-10 06:00 | 134 | 133
2019-02-10 06:30 | 123 | 123
2019-02-10 07:00 | 105 | 104
2019-02-10 07:30 | 89 | 88
2019-02-10 08:00 | 73 | 70
2019-02-10 08:30 | 68 | 63
2019-02-10 09:00 | 61 | 55
2019-02-10 09:30 | 65 | 60
2019-02-10 10:00 | 71 | 67
2019-02-10 10:30 | 75 | 71
2019-02-10 11:00 | 74 | 71
2019-02-10 11:30 | 76 | 73
2019-02-10 12:00 | 81 | 78
2019-02-10 12:30 | 82 | 80
2019-02-10 13:00 | 92 | 90
2019-02-10 13:30 | 97 | 96
2019-02-10 14:00 | 106 | 104
2019-02-10 14:30 | 117 | 116
2019-02-10 15:00 | 130 | 129
2019-02-10 15:30 | 157 | 156
2019-02-10 16:00 | 178 | 178
2019-02-10 16:30 | 168 | 168
2019-02-10 17:00 | 220 | 219
2019-02-10 17:30 | 262 | 262
2019-02-10 18:00 | 270 | 269
2019-02-10 18:30 | 268 | 268
2019-02-10 19:00 | 292 | 292
2019-02-10 19:30 | 289 | 289
2019-02-10 20:00 | 282 | 282
2019-02-10 20:30 | 282 | 281
2019-02-10 21:00 | 270 | 270
2019-02-10 21:30 | 258 | 257
2019-02-10 22:00 | 245 | 244
2019-02-10 22:30 | 227 | 227
2019-02-10 23:00 | 212 | 212
2019-02-10 23:30 | 195 | 194
2019-02-11 | 182 | 182
2019-02-11 00:30 | 175 | 174
2019-02-11 01:00 | 157 | 156
2019-02-11 01:30 | 145 | 144
2019-02-11 02:00 | 137 | 136
2019-02-11 02:30 | 133 | 132
2019-02-11 03:00 | 130 | 128
2019-02-11 03:30 | 132 | 131
2019-02-11 04:00 | 133 | 132
2019-02-11 04:30 | 136 | 135
2019-02-11 05:00 | 139 | 138
2019-02-11 05:30 | 147 | 146
2019-02-11 06:00 | 158 | 157
2019-02-11 06:30 | 173 | 172
2019-02-11 07:00 | 169 | 169
2019-02-11 07:30 | 155 | 155
2019-02-11 08:00 | 146 | 145
2019-02-11 08:30 | 137 | 136
2019-02-11 09:00 | 136 | 135
2019-02-11 09:30 | 133 | 132
2019-02-11 10:00 | 126 | 125
2019-02-11 10:30 | 110 | 109
2019-02-11 11:00 | 76 | 72
2019-02-11 11:30 | 65 | 57
2019-02-11 12:00 | 71 | 66
2019-02-11 12:30 | 76 | 72
2019-02-11 13:00 | 79 | 76
2019-02-11 13:30 | 85 | 82
2019-02-11 14:00 | 83 | 79
2019-02-11 14:30 | 76 | 72
2019-02-11 15:00 | 88 | 85
2019-02-11 15:30 | 100 | 99
2019-02-11 16:00 | 118 | 117
2019-02-11 16:30 | 142 | 141
2019-02-11 17:00 | 157 | 156
2019-02-11 17:30 | 182 | 181
2019-02-11 18:00 | 201 | 201
2019-02-11 18:30 | 211 | 210
2019-02-11 19:00 | 230 | 230
2019-02-11 19:30 | 236 | 236
2019-02-11 20:00 | 241 | 241
2019-02-11 20:30 | 248 | 248
2019-02-11 21:00 | 241 | 240
2019-02-11 21:30 | 227 | 226
2019-02-11 22:00 | 221 | 221
2019-02-11 22:30 | 182 | 182
2019-02-11 23:00 | 161 | 161
2019-02-11 23:30 | 200 | 200
2019-02-12 | 209 | 208
2019-02-12 00:30 | 206 | 206
2019-02-12 01:00 | 196 | 196
2019-02-12 01:30 | 188 | 188
2019-02-12 02:00 | 183 | 182
2019-02-12 02:30 | 177 | 177
2019-02-12 03:00 | 167 | 166
2019-02-12 03:30 | 153 | 153
2019-02-12 04:00 | 142 | 142
2019-02-12 04:30 | 140 | 140
2019-02-12 05:00 | 140 | 139
2019-02-12 05:30 | 149 | 148
2019-02-12 06:00 | 155 | 155
2019-02-12 06:30 | 160 | 160
2019-02-12 07:00 | 158 | 157
2019-02-12 07:30 | 178 | 177
2019-02-12 08:00 | 176 | 176
2019-02-12 08:30 | 141 | 139
2019-02-12 09:00 | 139 | 138
2019-02-12 09:30 | 138 | 137
2019-02-12 10:00 | 130 | 129
2019-02-12 10:30 | 123 | 121
2019-02-12 11:00 | 115 | 113
2019-02-12 11:30 | 115 | 113
2019-02-12 12:00 | 117 | 115
2019-02-12 12:30 | 129 | 128
2019-02-12 13:00 | 131 | 129
2019-02-12 13:30 | 103 | 101
2019-02-12 14:00 | 118 | 117
2019-02-12 14:30 | 123 | 121
2019-02-12 15:00 | 124 | 122
2019-02-12 15:30 | 114 | 113
2019-02-12 16:00 | 98 | 96
2019-02-12 16:30 | 91 | 88
2019-02-12 17:00 | 92 | 90
2019-02-12 17:30 | 115 | 114
2019-02-12 18:00 | 141 | 141
2019-02-12 18:30 | 176 | 175
2019-02-12 19:00 | 176 | 176
2019-02-12 19:30 | 186 | 185
2019-02-12 20:00 | 210 | 210
2019-02-12 20:30 | 214 | 213
2019-02-12 21:00 | 214 | 214
2019-02-12 21:30 | 210 | 209
2019-02-12 22:00 | 197 | 196
2019-02-12 22:30 | 177 | 177
2019-02-12 23:00 | 159 | 158
2019-02-12 23:30 | 143 | 142
2019-02-13 | 132 | 131
2019-02-13 00:30 | 130 | 129
2019-02-13 01:00 | 117 | 116
2019-02-13 01:30 | 111 | 110
2019-02-13 02:00 | 105 | 103
2019-02-13 02:30 | 100 | 98
2019-02-13 03:00 | 96 | 94
2019-02-13 03:30 | 88 | 86
2019-02-13 04:00 | 87 | 84
2019-02-13 04:30 | 86 | 83
2019-02-13 05:00 | 82 | 80
2019-02-13 05:30 | 87 | 84
2019-02-13 06:00 | 91 | 89
2019-02-13 06:30 | 88 | 85
2019-02-13 07:00 | 94 | 92
2019-02-13 07:30 | 93 | 90
2019-02-13 08:00 | 73 | 67
2019-02-13 08:30 | 57 | 48
2019-02-13 09:00 | 41 | 39
2019-02-13 09:30 | 38 | 37
2019-02-13 10:00 | 34 | 34
2019-02-13 10:30 | 35 | 35
2019-02-13 11:00 | 38 | 36
2019-02-13 11:30 | 49 | 42
2019-02-13 12:00 | 49 | 42
2019-02-13 12:30 | 63 | 55
2019-02-13 13:00 | 62 | 53
2019-02-13 13:30 | 68 | 61
2019-02-13 14:00 | 75 | 70
2019-02-13 14:30 | 80 | 76
2019-02-13 15:00 | 85 | 82
2019-02-13 15:30 | 82 | 78
2019-02-13 16:00 | 73 | 68
2019-02-13 16:30 | 70 | 66
2019-02-13 17:00 | 3 | 2
2019-02-13 17:30 | 22 | 21
2019-02-13 18:00 | 59 | 50
2019-02-13 18:30 | 78 | 74
2019-02-13 19:00 | 91 | 88
2019-02-13 19:30 | 99 | 97
2019-02-13 20:00 | 105 | 103
2019-02-13 20:30 | 81 | 77
2019-02-13 21:00 | 73 | 67
2019-02-13 21:30 | 109 | 107
2019-02-13 22:00 | 69 | 62
2019-02-13 22:30 | 131 | 130
2019-02-13 23:00 | 154 | 153
2019-02-13 23:30 | 138 | 138
2019-02-14 | 127 | 126
2019-02-14 00:30 | 135 | 134
2019-02-14 01:00 | 122 | 120
2019-02-14 01:30 | 114 | 112
2019-02-14 02:00 | 110 | 108
2019-02-14 02:30 | 104 | 102
2019-02-14 03:00 | 101 | 99
2019-02-14 03:30 | 100 | 98
2019-02-14 04:00 | 94 | 92
2019-02-14 04:30 | 93 | 90
2019-02-14 05:00 | 93 | 91
2019-02-14 05:30 | 96 | 93
2019-02-14 06:00 | 69 | 63
2019-02-14 06:30 | 72 | 66
2019-02-14 07:00 | 75 | 70
2019-02-14 07:30 | 72 | 66
2019-02-14 08:00 | 97 | 95
2019-02-14 08:30 | 84 | 80
2019-02-14 09:00 | 80 | 75
2019-02-14 09:30 | 75 | 69
2019-02-14 10:00 | 70 | 63
2019-02-14 10:30 | 58 | 51
2019-02-14 11:00 | 34 | 27
2019-02-14 11:30 | 36 | 28
2019-02-14 12:00 | 40 | 37
2019-02-14 12:30 | 58 | 48
2019-02-14 13:00 | 67 | 60
2019-02-14 13:30 | 73 | 67
2019-02-14 14:00 | 82 | 77
2019-02-14 14:30 | 101 | 99
2019-02-14 15:00 | 112 | 110
2019-02-14 15:30 | 122 | 120
2019-02-14 16:00 | 134 | 133
2019-02-14 16:30 | 158 | 157
2019-02-14 17:00 | 189 | 188
2019-02-14 17:30 | 206 | 205
2019-02-14 18:00 | 227 | 227
2019-02-14 18:30 | 239 | 238
2019-02-14 19:00 | 244 | 244
2019-02-14 19:30 | 241 | 241
2019-02-14 20:00 | 241 | 241
2019-02-14 20:30 | 234 | 234
2019-02-14 21:00 | 231 | 231
2019-02-14 21:30 | 212 | 211
2019-02-14 22:00 | 200 | 200
2019-02-14 22:30 | 170 | 169
2019-02-14 23:00 | 172 | 172
2019-02-14 23:30 | 190 | 189
2019-02-15 | 221 | 221
2019-02-15 00:30 | 213 | 213
2019-02-15 01:00 | 206 | 206
2019-02-15 01:30 | 200 | 199
2019-02-15 02:00 | 195 | 194
2019-02-15 02:30 | 189 | 189
2019-02-15 03:00 | 184 | 184
2019-02-15 03:30 | 184 | 184
2019-02-15 04:00 | 169 | 168
2019-02-15 04:30 | 142 | 142
2019-02-15 05:00 | 130 | 129
2019-02-15 05:30 | 153 | 153
2019-02-15 06:00 | 180 | 180
2019-02-15 06:30 | 193 | 192
2019-02-15 07:00 | 196 | 196
2019-02-15 07:30 | 195 | 195
2019-02-15 08:00 | 180 | 180
2019-02-15 08:30 | 160 | 159
2019-02-15 09:00 | 155 | 154
2019-02-15 09:30 | 140 | 139
2019-02-15 10:00 | 113 | 112
2019-02-15 10:30 | 106 | 105
2019-02-15 11:00 | 102 | 101
2019-02-15 11:30 | 104 | 102
2019-02-15 12:00 | 106 | 105
2019-02-15 12:30 | 110 | 108
2019-02-15 13:00 | 116 | 115
2019-02-15 13:30 | 124 | 123
2019-02-15 14:00 | 134 | 134
2019-02-15 14:30 | 159 | 159
2019-02-15 15:00 | 170 | 170
2019-02-15 15:30 | 175 | 174
2019-02-15 16:00 | 206 | 205
2019-02-15 16:30 | 192 | 192
2019-02-15 17:00 | 214 | 214
2019-02-15 17:30 | 229 | 229
2019-02-15 18:00 | 256 | 255
2019-02-15 18:30 | 268 | 268
2019-02-15 19:00 | 273 | 273
2019-02-15 19:30 | 285 | 285
2019-02-15 20:00 | 282 | 282
2019-02-15 20:30 | 271 | 270
2019-02-15 21:00 | 254 | 253
2019-02-15 21:30 | 250 | 249
2019-02-15 22:00 | 238 | 237
2019-02-15 22:30 | 225 | 225
2019-02-15 23:00 | 216 | 215
2019-02-15 23:30 | 204 | 204
2019-02-16 | 190 | 189
2019-02-16 00:30 | 192 | 191
2019-02-16 01:00 | 176 | 175
2019-02-16 01:30 | 172 | 171
2019-02-16 02:00 | 175 | 175
2019-02-16 02:30 | 169 | 168
2019-02-16 03:00 | 153 | 152
2019-02-16 03:30 | 139 | 138
2019-02-16 04:00 | 127 | 126
2019-02-16 04:30 | 120 | 119
2019-02-16 05:00 | 116 | 115
2019-02-16 05:30 | 123 | 122
2019-02-16 06:00 | 123 | 122
2019-02-16 06:30 | 113 | 112
2019-02-16 07:00 | 104 | 103
2019-02-16 07:30 | 104 | 103
2019-02-16 08:00 | 90 | 88
2019-02-16 08:30 | 80 | 78
2019-02-16 09:00 | 76 | 74
2019-02-16 09:30 | 79 | 77
2019-02-16 10:00 | 83 | 82
2019-02-16 10:30 | 87 | 85
2019-02-16 11:00 | 76 | 74
2019-02-16 11:30 | 81 | 80
2019-02-16 12:00 | 91 | 90
2019-02-16 12:30 | 94 | 93
2019-02-16 13:00 | 92 | 91
2019-02-16 13:30 | 98 | 96
2019-02-16 14:00 | 98 | 97
2019-02-16 14:30 | 100 | 99
2019-02-16 15:00 | 119 | 118
2019-02-16 15:30 | 126 | 125
2019-02-16 16:00 | 143 | 142
2019-02-16 16:30 | 141 | 140
2019-02-16 17:00 | 166 | 165
2019-02-16 17:30 | 184 | 184
2019-02-16 18:00 | 217 | 217
2019-02-16 18:30 | 244 | 243
2019-02-16 19:00 | 257 | 256
2019-02-16 19:30 | 262 | 262
2019-02-16 20:00 | 258 | 257
2019-02-16 20:30 | 240 | 239
2019-02-16 21:00 | 236 | 235
2019-02-16 21:30 | 244 | 244
2019-02-16 22:00 | 243 | 243
2019-02-16 22:30 | 224 | 224
2019-02-16 23:00 | 211 | 210
2019-02-16 23:30 | 205 | 204
2019-02-17 | 197 | 197
2019-02-17 00:30 | 197 | 197
2019-02-17 01:00 | 182 | 181
2019-02-17 01:30 | 171 | 171
2019-02-17 02:00 | 165 | 164
2019-02-17 02:30 | 158 | 157
2019-02-17 03:00 | 157 | 157
2019-02-17 03:30 | 156 | 156
2019-02-17 04:00 | 161 | 160
2019-02-17 04:30 | 164 | 163
2019-02-17 05:00 | 161 | 161
2019-02-17 05:30 | 162 | 161
2019-02-17 06:00 | 165 | 164
2019-02-17 06:30 | 160 | 160
2019-02-17 07:00 | 157 | 157
2019-02-17 07:30 | 155 | 154
2019-02-17 08:00 | 145 | 144
2019-02-17 08:30 | 114 | 113
2019-02-17 09:00 | 105 | 103
2019-02-17 09:30 | 107 | 106
2019-02-17 10:00 | 97 | 95
2019-02-17 10:30 | 105 | 104
2019-02-17 11:00 | 114 | 113
2019-02-17 11:30 | 108 | 107
2019-02-17 12:00 | 104 | 103
2019-02-17 12:30 | 142 | 141
2019-02-17 13:00 | 134 | 133
2019-02-17 13:30 | 161 | 160
2019-02-17 14:00 | 145 | 144
2019-02-17 14:30 | 157 | 156
2019-02-17 15:00 | 147 | 146
2019-02-17 15:30 | 150 | 149
2019-02-17 16:00 | 193 | 192
2019-02-17 16:30 | 173 | 172
2019-02-17 17:00 | 163 | 162
2019-02-17 17:30 | 215 | 215
2019-02-17 18:00 | 240 | 239
2019-02-17 18:30 | 254 | 254
2019-02-17 19:00 | 265 | 264
2019-02-17 19:30 | 270 | 269
2019-02-17 20:00 | 265 | 265
2019-02-17 20:30 | 259 | 259
2019-02-17 21:00 | 262 | 262
2019-02-17 21:30 | 250 | 250
2019-02-17 22:00 | 232 | 231
2019-02-17 22:30 | 220 | 219
2019-02-17 23:00 | 205 | 205
2019-02-17 23:30 | 194 | 194
2019-02-18 | 190 | 190
2019-02-18 00:30 | 197 | 197
2019-02-18 01:00 | 184 | 183
2019-02-18 01:30 | 177 | 176
2019-02-18 02:00 | 174 | 173
2019-02-18 02:30 | 170 | 169
2019-02-18 03:00 | 167 | 166
2019-02-18 03:30 | 166 | 165
2019-02-18 04:00 | 163 | 163
2019-02-18 04:30 | 166 | 165
2019-02-18 05:00 | 168 | 168
2019-02-18 05:30 | 174 | 174
2019-02-18 06:00 | 180 | 179
2019-02-18 06:30 | 189 | 188
2019-02-18 07:00 | 196 | 196
2019-02-18 07:30 | 194 | 194
2019-02-18 08:00 | 180 | 179
2019-02-18 08:30 | 161 | 160
2019-02-18 09:00 | 139 | 139
2019-02-18 09:30 | 136 | 135
2019-02-18 10:00 | 121 | 120
2019-02-18 10:30 | 126 | 126
2019-02-18 11:00 | 130 | 129
2019-02-18 11:30 | 120 | 119
2019-02-18 12:00 | 115 | 114
2019-02-18 12:30 | 121 | 120
2019-02-18 13:00 | 131 | 130
2019-02-18 13:30 | 140 | 139
2019-02-18 14:00 | 164 | 164
2019-02-18 14:30 | 163 | 162
2019-02-18 15:00 | 168 | 167
2019-02-18 15:30 | 165 | 164
2019-02-18 16:00 | 171 | 170
2019-02-18 16:30 | 194 | 194
2019-02-18 17:00 | 224 | 224
2019-02-18 17:30 | 243 | 242
2019-02-18 18:00 | 262 | 262
2019-02-18 18:30 | 284 | 284
2019-02-18 19:00 | 298 | 298
2019-02-18 19:30 | 306 | 306
2019-02-18 20:00 | 301 | 300
2019-02-18 20:30 | 287 | 286
2019-02-18 21:00 | 274 | 273
2019-02-18 21:30 | 277 | 276
2019-02-18 22:00 | 260 | 259
2019-02-18 22:30 | 241 | 240
2019-02-18 23:00 | 225 | 224
2019-02-18 23:30 | 213 | 212
2019-02-19 | 203 | 202
2019-02-19 00:30 | 206 | 205
2019-02-19 01:00 | 194 | 194
2019-02-19 01:30 | 185 | 184
2019-02-19 02:00 | 183 | 182
2019-02-19 02:30 | 178 | 177
2019-02-19 03:00 | 175 | 174
2019-02-19 03:30 | 171 | 171
2019-02-19 04:00 | 166 | 166
2019-02-19 04:30 | 161 | 160
2019-02-19 05:00 | 157 | 156
2019-02-19 05:30 | 145 | 144
2019-02-19 06:00 | 137 | 136
2019-02-19 06:30 | 143 | 142
2019-02-19 07:00 | 151 | 150
2019-02-19 07:30 | 138 | 137
2019-02-19 08:00 | 128 | 127
2019-02-19 08:30 | 116 | 115
2019-02-19 09:00 | 114 | 113
2019-02-19 09:30 | 103 | 102
2019-02-19 10:00 | 97 | 96
2019-02-19 10:30 | 95 | 94
2019-02-19 11:00 | 93 | 91
2019-02-19 11:30 | 93 | 92
2019-02-19 12:00 | 93 | 92
2019-02-19 12:30 | 101 | 99
2019-02-19 13:00 | 114 | 113
2019-02-19 13:30 | 119 | 118
2019-02-19 14:00 | 128 | 127
2019-02-19 14:30 | 131 | 130
2019-02-19 15:00 | 131 | 130
2019-02-19 15:30 | 127 | 126
2019-02-19 16:00 | 141 | 141
2019-02-19 16:30 | 171 | 171
2019-02-19 17:00 | 192 | 191
2019-02-19 17:30 | 217 | 216
2019-02-19 18:00 | 245 | 244
2019-02-19 18:30 | 265 | 264
2019-02-19 19:00 | 269 | 269
2019-02-19 19:30 | 285 | 285
2019-02-19 20:00 | 287 | 286
2019-02-19 20:30 | 298 | 298
2019-02-19 21:00 | 283 | 283
2019-02-19 21:30 | 277 | 276
2019-02-19 22:00 | 257 | 257
2019-02-19 22:30 | 242 | 241
2019-02-19 23:00 | 230 | 229
2019-02-19 23:30 | 218 | 217
2019-02-20 | 204 | 203
2019-02-20 00:30 | 201 | 200
2019-02-20 01:00 | 190 | 189
2019-02-20 01:30 | 180 | 179
2019-02-20 02:00 | 180 | 179
2019-02-20 02:30 | 170 | 169
2019-02-20 03:00 | 164 | 163
2019-02-20 03:30 | 164 | 163
2019-02-20 04:00 | 163 | 162
2019-02-20 04:30 | 163 | 162
2019-02-20 05:00 | 166 | 165
2019-02-20 05:30 | 173 | 172
2019-02-20 06:00 | 180 | 179
2019-02-20 06:30 | 160 | 159
2019-02-20 07:00 | 152 | 150
2019-02-20 07:30 | 118 | 117
2019-02-20 08:00 | 98 | 97
2019-02-20 08:30 | 81 | 80
2019-02-20 09:00 | 65 | 62
2019-02-20 09:30 | 51 | 45
2019-02-20 10:00 | 45 | 38
2019-02-20 10:30 | 34 | 32
2019-02-20 11:00 | 37 | 31
2019-02-20 11:30 | 40 | 33
2019-02-20 12:00 | 42 | 36
2019-02-20 12:30 | 55 | 48
2019-02-20 13:00 | 63 | 59
2019-02-20 13:30 | 69 | 66
2019-02-20 14:00 | 79 | 76
2019-02-20 14:30 | 92 | 90
2019-02-20 15:00 | 99 | 98
2019-02-20 15:30 | 99 | 98
2019-02-20 16:00 | 121 | 121
2019-02-20 16:30 | 133 | 132
2019-02-20 17:00 | 161 | 160
2019-02-20 17:30 | 190 | 189
2019-02-20 18:00 | 224 | 223
2019-02-20 18:30 | 248 | 247
2019-02-20 19:00 | 264 | 263
2019-02-20 19:30 | 261 | 260
2019-02-20 20:00 | 253 | 252
2019-02-20 20:30 | 245 | 244
2019-02-20 21:00 | 267 | 266
2019-02-20 21:30 | 290 | 290
2019-02-20 22:00 | 320 | 320
2019-02-20 22:30 | 299 | 298
2019-02-20 23:00 | 268 | 267
2019-02-20 23:30 | 246 | 245
2019-02-21 | 228 | 227
2019-02-21 00:30 | 215 | 214
2019-02-21 01:00 | 210 | 209
2019-02-21 01:30 | 203 | 202
2019-02-21 02:00 | 197 | 197
2019-02-21 02:30 | 194 | 193
2019-02-21 03:00 | 191 | 190
2019-02-21 03:30 | 186 | 185
2019-02-21 04:00 | 180 | 179
2019-02-21 04:30 | 179 | 178
2019-02-21 05:00 | 183 | 183
2019-02-21 05:30 | 185 | 184
2019-02-21 06:00 | 191 | 190
2019-02-21 06:30 | 197 | 196
2019-02-21 07:00 | 200 | 199
2019-02-21 07:30 | 182 | 181
2019-02-21 08:00 | 154 | 153
2019-02-21 08:30 | 132 | 131
2019-02-21 09:00 | 114 | 113
2019-02-21 09:30 | 93 | 92
2019-02-21 10:00 | 66 | 63
2019-02-21 10:30 | 65 | 62
2019-02-21 11:00 | 74 | 72
2019-02-21 11:30 | 85 | 84
2019-02-21 12:00 | 99 | 98
2019-02-21 12:30 | 104 | 103
2019-02-21 13:00 | 91 | 90
2019-02-21 13:30 | 82 | 81
2019-02-21 14:00 | 56 | 51
2019-02-21 14:30 | 59 | 53
2019-02-21 15:00 | 67 | 63
2019-02-21 15:30 | 72 | 70
2019-02-21 16:00 | 91 | 90
2019-02-21 16:30 | 88 | 87
2019-02-21 17:00 | 117 | 116
2019-02-21 17:30 | 148 | 147
2019-02-21 18:00 | 186 | 185
2019-02-21 18:30 | 211 | 210
2019-02-21 19:00 | 234 | 233
2019-02-21 19:30 | 244 | 243
2019-02-21 20:00 | 242 | 240
2019-02-21 20:30 | 232 | 231
2019-02-21 21:00 | 218 | 217
2019-02-21 21:30 | 251 | 249
2019-02-21 22:00 | 268 | 266
2019-02-21 22:30 | 306 | 305
2019-02-21 23:00 | 279 | 277
2019-02-21 23:30 | 256 | 254
2019-02-22 | 237 | 235
2019-02-22 00:30 | 217 | 216
2019-02-22 01:00 | 203 | 201
2019-02-22 01:30 | 191 | 189
2019-02-22 02:00 | 190 | 189
2019-02-22 02:30 | 191 | 189
2019-02-22 03:00 | 187 | 186
2019-02-22 03:30 | 182 | 181
2019-02-22 04:00 | 175 | 174
2019-02-22 04:30 | 173 | 172
2019-02-22 05:00 | 175 | 173
2019-02-22 05:30 | 184 | 182
2019-02-22 06:00 | 198 | 196
2019-02-22 06:30 | 210 | 209
2019-02-22 07:00 | 213 | 211
2019-02-22 07:30 | 197 | 195
2019-02-22 08:00 | 171 | 170
2019-02-22 08:30 | 158 | 157
2019-02-22 09:00 | 160 | 159
2019-02-22 09:30 | 170 | 169
2019-02-22 10:00 | 165 | 164
2019-02-22 10:30 | 144 | 143
2019-02-22 11:00 | 142 | 142
2019-02-22 11:30 | 158 | 157
2019-02-22 12:00 | 165 | 164
2019-02-22 12:30 | 170 | 170
2019-02-22 13:00 | 170 | 169
2019-02-22 13:30 | 171 | 170
2019-02-22 14:00 | 176 | 176
2019-02-22 14:30 | 178 | 178
2019-02-22 15:00 | 211 | 210
2019-02-22 15:30 | 179 | 178
2019-02-22 16:00 | 181 | 180
2019-02-22 16:30 | 200 | 200
2019-02-22 17:00 | 216 | 215
2019-02-22 17:30 | 234 | 234
2019-02-22 18:00 | 259 | 259
2019-02-22 18:30 | 262 | 261
2019-02-22 19:00 | 248 | 247
2019-02-22 19:30 | 262 | 261
2019-02-22 20:00 | 276 | 275
2019-02-22 20:30 | 271 | 271
2019-02-22 21:00 | 264 | 263
2019-02-22 21:30 | 246 | 245
2019-02-22 22:00 | 222 | 222
2019-02-22 22:30 | 235 | 234
2019-02-22 23:00 | 232 | 231
2019-02-22 23:30 | 215 | 214
2019-02-23 | 208 | 207
2019-02-23 00:30 | 208 | 207
2019-02-23 01:00 | 194 | 193
2019-02-23 01:30 | 189 | 188
2019-02-23 02:00 | 183 | 182
2019-02-23 02:30 | 176 | 175
2019-02-23 03:00 | 172 | 171
2019-02-23 03:30 | 168 | 167
2019-02-23 04:00 | 174 | 173
2019-02-23 04:30 | 182 | 180
2019-02-23 05:00 | 182 | 180
2019-02-23 05:30 | 182 | 180
2019-02-23 06:00 | 178 | 177
2019-02-23 06:30 | 181 | 180
2019-02-23 07:00 | 181 | 180
2019-02-23 07:30 | 161 | 160
2019-02-23 08:00 | 147 | 146
2019-02-23 08:30 | 148 | 147
2019-02-23 09:00 | 156 | 155
2019-02-23 09:30 | 159 | 158
2019-02-23 10:00 | 147 | 146
2019-02-23 10:30 | 146 | 145
2019-02-23 11:00 | 126 | 125
2019-02-23 11:30 | 141 | 140
2019-02-23 12:00 | 140 | 139
2019-02-23 12:30 | 126 | 125
2019-02-23 13:00 | 121 | 120
2019-02-23 13:30 | 135 | 134
2019-02-23 14:00 | 154 | 153
2019-02-23 14:30 | 181 | 180
2019-02-23 15:00 | 182 | 182
2019-02-23 15:30 | 204 | 204
2019-02-23 16:00 | 213 | 212
2019-02-23 16:30 | 212 | 212
2019-02-23 17:00 | 227 | 226
2019-02-23 17:30 | 241 | 240
2019-02-23 18:00 | 261 | 261
2019-02-23 18:30 | 259 | 259
2019-02-23 19:00 | 249 | 249
2019-02-23 19:30 | 235 | 234
2019-02-23 20:00 | 218 | 217
2019-02-23 20:30 | 215 | 214
2019-02-23 21:00 | 217 | 216
2019-02-23 21:30 | 204 | 203
2019-02-23 22:00 | 192 | 191
2019-02-23 22:30 | 173 | 172
2019-02-23 23:00 | 163 | 162
2019-02-23 23:30 | 155 | 155
2019-02-24 | 149 | 148
2019-02-24 00:30 | 151 | 150
2019-02-24 01:00 | 138 | 138
2019-02-24 01:30 | 136 | 135
2019-02-24 02:00 | 144 | 143
2019-02-24 02:30 | 146 | 145
2019-02-24 03:00 | 135 | 134
2019-02-24 03:30 | 135 | 134
2019-02-24 04:00 | 128 | 126
2019-02-24 04:30 | 130 | 129
2019-02-24 05:00 | 127 | 125
2019-02-24 05:30 | 128 | 127
2019-02-24 06:00 | 123 | 121
2019-02-24 06:30 | 125 | 123
2019-02-24 07:00 | 137 | 136
2019-02-24 07:30 | 136 | 135
2019-02-24 08:00 | 128 | 127
2019-02-24 08:30 | 134 | 134
2019-02-24 09:00 | 143 | 143
2019-02-24 09:30 | 133 | 133
2019-02-24 10:00 | 118 | 117
2019-02-24 10:30 | 102 | 101
2019-02-24 11:00 | 99 | 98
2019-02-24 11:30 | 89 | 87
2019-02-24 12:00 | 83 | 81
2019-02-24 12:30 | 93 | 92
2019-02-24 13:00 | 96 | 94
2019-02-24 13:30 | 95 | 94
2019-02-24 14:00 | 83 | 81
2019-02-24 14:30 | 99 | 98
2019-02-24 15:00 | 128 | 127
2019-02-24 15:30 | 140 | 139
2019-02-24 16:00 | 145 | 145
2019-02-24 16:30 | 151 | 151
2019-02-24 17:00 | 154 | 154
2019-02-24 17:30 | 164 | 163
2019-02-24 18:00 | 173 | 172
2019-02-24 18:30 | 191 | 190
2019-02-24 19:00 | 188 | 188
2019-02-24 19:30 | 188 | 187
2019-02-24 20:00 | 187 | 187
2019-02-24 20:30 | 172 | 171
2019-02-24 21:00 | 171 | 170
2019-02-24 21:30 | 169 | 169
2019-02-24 22:00 | 160 | 159
2019-02-24 22:30 | 154 | 153
2019-02-24 23:00 | 150 | 150
2019-02-24 23:30 | 146 | 145
2019-02-25 | 120 | 119
2019-02-25 00:30 | 125 | 124
2019-02-25 01:00 | 105 | 104
2019-02-25 01:30 | 94 | 92
2019-02-25 02:00 | 94 | 92
2019-02-25 02:30 | 81 | 78
2019-02-25 03:00 | 74 | 71
2019-02-25 03:30 | 82 | 79
2019-02-25 04:00 | 82 | 80
2019-02-25 04:30 | 101 | 99
2019-02-25 05:00 | 108 | 107
2019-02-25 05:30 | 120 | 119
2019-02-25 06:00 | 132 | 131
2019-02-25 06:30 | 132 | 131
2019-02-25 07:00 | 143 | 143
2019-02-25 07:30 | 147 | 146
2019-02-25 08:00 | 121 | 120
2019-02-25 08:30 | 121 | 120
2019-02-25 09:00 | 78 | 75
2019-02-25 09:30 | 70 | 66
2019-02-25 10:00 | 55 | 49
2019-02-25 10:30 | 35 | 32
2019-02-25 11:00 | 24 | 20
2019-02-25 11:30 | 32 | 27
2019-02-25 12:00 | 36 | 30
2019-02-25 12:30 | 56 | 49
2019-02-25 13:00 | 82 | 79
2019-02-25 13:30 | 99 | 97
2019-02-25 14:00 | 109 | 108
2019-02-25 14:30 | 104 | 103
2019-02-25 15:00 | 86 | 83
2019-02-25 15:30 | 129 | 129
2019-02-25 16:00 | 135 | 134
2019-02-25 16:30 | 95 | 93
2019-02-25 17:00 | 122 | 121
2019-02-25 17:30 | 142 | 141
2019-02-25 18:00 | 167 | 166
2019-02-25 18:30 | 181 | 180
2019-02-25 19:00 | 198 | 198
2019-02-25 19:30 | 199 | 199
2019-02-25 20:00 | 170 | 169
2019-02-25 20:30 | 154 | 153
2019-02-25 21:00 | 148 | 147
2019-02-25 21:30 | 157 | 157
2019-02-25 22:00 | 141 | 140
2019-02-25 22:30 | 131 | 130
2019-02-25 23:00 | 116 | 115
2019-02-25 23:30 | 106 | 105
2019-02-26 | 101 | 100
2019-02-26 00:30 | 109 | 108
2019-02-26 01:00 | 103 | 102
2019-02-26 01:30 | 91 | 90
2019-02-26 02:00 | 87 | 85
2019-02-26 02:30 | 82 | 80
2019-02-26 03:00 | 80 | 79
2019-02-26 03:30 | 81 | 80
2019-02-26 04:00 | 81 | 79
2019-02-26 04:30 | 82 | 80
2019-02-26 05:00 | 87 | 85
2019-02-26 05:30 | 94 | 93
2019-02-26 06:00 | 99 | 98
2019-02-26 06:30 | 106 | 105
2019-02-26 07:00 | 108 | 107
2019-02-26 07:30 | 90 | 89
2019-02-26 08:00 | 70 | 66
2019-02-26 08:30 | 43 | 39
2019-02-26 09:00 | 32 | 25
2019-02-26 09:30 | 19 | 15
2019-02-26 10:00 | 33 | 26
2019-02-26 10:30 | 9 | 8
2019-02-26 11:00 | 13 | 10
2019-02-26 11:30 | 27 | 22
2019-02-26 12:00 | 47 | 41
2019-02-26 12:30 | 42 | 34
2019-02-26 13:00 | 61 | 56
2019-02-26 13:30 | 67 | 63
2019-02-26 14:00 | 82 | 80
2019-02-26 14:30 | 84 | 82
2019-02-26 15:00 | 85 | 82
2019-02-26 15:30 | 90 | 88
2019-02-26 16:00 | 94 | 92
2019-02-26 16:30 | 114 | 113
2019-02-26 17:00 | 135 | 135
2019-02-26 17:30 | 133 | 132
2019-02-26 18:00 | 169 | 168
2019-02-26 18:30 | 175 | 174
2019-02-26 19:00 | 186 | 186
2019-02-26 19:30 | 192 | 191
2019-02-26 20:00 | 188 | 187
2019-02-26 20:30 | 182 | 181
2019-02-26 21:00 | 174 | 173
2019-02-26 21:30 | 167 | 167
2019-02-26 22:00 | 154 | 153
2019-02-26 22:30 | 141 | 140
2019-02-26 23:00 | 123 | 122
2019-02-26 23:30 | 110 | 109
2019-02-27 | 103 | 102
2019-02-27 00:30 | 111 | 109
2019-02-27 01:00 | 101 | 100
2019-02-27 01:30 | 92 | 91
2019-02-27 02:00 | 87 | 85
2019-02-27 02:30 | 82 | 80
2019-02-27 03:00 | 87 | 86
2019-02-27 03:30 | 91 | 90
2019-02-27 04:00 | 88 | 86
2019-02-27 04:30 | 92 | 90
2019-02-27 05:00 | 104 | 103
2019-02-27 05:30 | 108 | 106
2019-02-27 06:00 | 111 | 109
2019-02-27 06:30 | 119 | 118
2019-02-27 07:00 | 131 | 130
2019-02-27 07:30 | 111 | 109
2019-02-27 08:00 | 82 | 79
2019-02-27 08:30 | 64 | 57
2019-02-27 09:00 | 54 | 46
2019-02-27 09:30 | 43 | 38
2019-02-27 10:00 | 49 | 44
2019-02-27 10:30 | 58 | 50
2019-02-27 11:00 | 57 | 49
2019-02-27 11:30 | 74 | 70
2019-02-27 12:00 | 80 | 77
2019-02-27 12:30 | 93 | 91
2019-02-27 13:00 | 93 | 90
2019-02-27 13:30 | 135 | 134
2019-02-27 14:00 | 108 | 107
2019-02-27 14:30 | 91 | 89
2019-02-27 15:00 | 92 | 90
2019-02-27 15:30 | 97 | 96
2019-02-27 16:00 | 110 | 109
2019-02-27 16:30 | 147 | 146
2019-02-27 17:00 | 115 | 114
2019-02-27 17:30 | 146 | 145
2019-02-27 18:00 | 173 | 172
2019-02-27 18:30 | 200 | 199
2019-02-27 19:00 | 209 | 208
2019-02-27 19:30 | 214 | 213
2019-02-27 20:00 | 197 | 196
2019-02-27 20:30 | 198 | 197
2019-02-27 21:00 | 195 | 194
2019-02-27 21:30 | 189 | 188
2019-02-27 22:00 | 175 | 174
2019-02-27 22:30 | 148 | 147
2019-02-27 23:00 | 144 | 143
2019-02-27 23:30 | 122 | 121
2019-02-28 | 106 | 104
2019-02-28 00:30 | 121 | 119
2019-02-28 01:00 | 110 | 108
2019-02-28 01:30 | 93 | 92
2019-02-28 02:00 | 86 | 84
2019-02-28 02:30 | 81 | 79
2019-02-28 03:00 | 82 | 80
2019-02-28 03:30 | 87 | 85
2019-02-28 04:00 | 95 | 94
2019-02-28 04:30 | 99 | 97
2019-02-28 05:00 | 104 | 102
2019-02-28 05:30 | 110 | 109
2019-02-28 06:00 | 123 | 122
2019-02-28 06:30 | 146 | 145
2019-02-28 07:00 | 142 | 142
2019-02-28 07:30 | 133 | 132
2019-02-28 08:00 | 99 | 97
2019-02-28 08:30 | 91 | 89
2019-02-28 09:00 | 59 | 53
2019-02-28 09:30 | 42 | 38
2019-02-28 10:00 | 29 | 21
2019-02-28 10:30 | 8 | 7
2019-02-28 11:00 | 28 | 23
2019-02-28 11:30 | 54 | 47
2019-02-28 12:00 | 37 | 35
2019-02-28 12:30 | 41 | 36
2019-02-28 13:00 | 25 | 22
2019-02-28 13:30 | 24 | 21
2019-02-28 14:00 | 44 | 40
2019-02-28 14:30 | 58 | 52
2019-02-28 15:00 | 35 | 30
2019-02-28 15:30 | 0 | 0
2019-02-28 16:00 | 3 | 3
2019-02-28 16:30 | 18 | 16
2019-02-28 17:00 | 21 | 17
2019-02-28 17:30 | 64 | 60
2019-02-28 18:00 | 96 | 95
2019-02-28 18:30 | 139 | 138
2019-02-28 19:00 | 163 | 162
2019-02-28 19:30 | 157 | 156
2019-02-28 20:00 | 158 | 157
2019-02-28 20:30 | 159 | 158
2019-02-28 21:00 | 142 | 140
2019-02-28 21:30 | 130 | 129
2019-02-28 22:00 | 109 | 107
2019-02-28 22:30 | 151 | 149
2019-02-28 23:00 | 162 | 161
2019-02-28 23:30 | 149 | 147
2019-03-01 | 143 | 142

## 18. Historic line rating
|  | 2016 Winter | 2016/17 Summer | 2017 Winter | 2017/18 Summer | 2018 Winter | 2018/19 Summer
PQ Rating (MVA) |  | 1486 | 1303 | 1486 | 1292 | 1483 | 1292
Feeders | 8857 | 918 | 807 | 918 | 811 | 921 | 811
| 8858 | 568 | 496 | 568 | 481 | 562 | 481

## 21. Annual constraint duration
Financial year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Annual constrain duration (hours)

## 22. Constraint dur. (peak day)
Financial year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Annual constrain duration (peak day, hours)